## Test Conditions
DESIREE-FIRE Intermediate Scale Test 12 - Circuit Simulator Data Only
Test Date: | 2009-11-23
DCSim DAQ Start Time | 15:07
DCSim Time for Synchronization | 15:08
Heat Source Synchronization | 0:01 | hour:minutes:seconds
Heat Source DAQ Start Time | 15:08
Fire Time | 15:57
Offset | 0:50 | hour:minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 3026 | seconds
Heat Source Offset | 0:50 | hour:minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 2991 | seconds
Heat Source Stop Time | 17:02
Test Duration | 1:05 | hour:minutes:seconds
| 3894 | seconds
CT500 turns | 2 | 1 or 2 | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 turns | 5 | 1 or 5
Pre-Test Baseline: | Gathered | Gathered or Not Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit Number | Cable Type |  | Cable TC Channel | Air TC Channel
SOV 1 | EPR/CPE, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 5, 6, and 7 represents the air temperature 3', 5', and 7' down the cable tray located in D-Position. These are labeled as "D-Position - 3'", "D-Position - Middle", " D-Position - 7'", respectively.
SOV 2 | EPR/CPE, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 1 which is defined as "B Position - Middle" in the Temperature Data File respresents the temperature in the center of the cable tray.
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | SOV-1_CT500 | SOV-1_CT35_1_P | SOV-1_CT35_2_S1 | SOV-1_CT35_3_G | SOV-1_CT35_4_S2 | SOV-1_CT35_5_N | SOV-2_CT500 | SOV-2_CT35_1_P | SOV-2_CT35_2_S1 | SOV-2_CT35_3_G | SOV-2_CT35_4_S2 | SOV-2_CT35_5_N | SOV-1_VT7_1_R | SOV-1_VT7_2_SP | SOV-1_VT7_3_S | SOV-1_VTU_1_P | SOV-1_VTU_2_S1 | SOV-1_VTU_3_G | SOV-1_VTU_4_N | SOV-2_VT7_1_R | SOV-2_VT7_2_SP | SOV-2_VT7_3_S | SOV-2_VTU_1_P | SOV-2_VTU_2_S1 | SOV-2_VTU_3_G | SOV-2_VTU_4_N | {SOV1} V(N) - V(Batt -) | {SOV1} V(P) - V(Batt +) | {SOV1} V(R) - V(Batt -) | {SOV1} V(S) - V(Batt -) | {SOV1} V(S) - V(N) | {SOV1} V(S1) - V(Batt +) | {SOV1} V(G) - V(Batt +) | {SOV2} V(N) - V(Batt -) | {SOV2} V(P) - V(Batt +) | {SOV2} V(R) - V(Batt -) | {SOV2} V(S) - V(Batt -) | {SOV2} V(S) - V(N) | {SOV2} V(S1) - V(Batt +) | {SOV2} V(G) - V(Batt +) | {SOV1} V(P) - V(Batt -) | {SOV1} V(S1) - V(Batt -) | {SOV1} V(G) - V(Batt -) | {SOV1} V(SP) - V(Batt -) | {SOV1} V(N) - V(Batt +) | {SOV2} V(P) - V(Batt -) | {SOV2} V(S1) - V(Batt -) | {SOV1} V(G) - V(Batt -) | {SOV2} V(SP) - V(Batt -) | {SOV2} V(N) - V(Batt +)
-1.3438 | 122.3145 | -62.2742 | 59.7427 | 1.4211e-13 | -0.021186 | -0.0036602 | 0.067075 | -0.0040766 | 0.060941 | -0.0054937 | 0.00057035 | -0.0016878 | -0.0027988 | 0.016713 | -0.0085312 | -62.2833 | 0.001407 | -62.241 | 59.6582 | 59.3799 | 59.4074 | -62.2174 | -62.2602 | 0.082776 | -62.3543 | 59.4767 | 59.5905 | 59.5983 | -62.3399 | 0.056791 | -0.084578 | -0.009171 | 0.033193 | -0.023598 | -0.36288 | -0.33534 | -0.065737 | -0.26599 | 0.013921 | -0.080107 | -0.01437 | -0.15225 | -0.14447 | 121.9323 | 121.654 | 121.6816 | 62.2756 | -121.9601 | 121.7509 | 121.8647 | 121.8724 | 62.3569 | -122.0826
0.40625 | 122.2366 | -62.265 | 59.8068 | 1.4211e-13 | -0.021399 | -0.003233 | 0.066648 | -0.0040766 | 0.060514 | -0.0054937 | 0.00078395 | -0.0014742 | -0.0023714 | 0.0165 | -0.0083176 | -62.2879 | -0.012329 | -62.2456 | 59.6582 | 59.3753 | 59.4028 | -62.2128 | -62.2602 | 0.078197 | -62.368 | 59.4676 | 59.5996 | 59.6212 | -62.3353 | 0.052215 | -0.14867 | -0.022904 | 0.01946 | -0.032755 | -0.43155 | -0.40401 | -0.070314 | -0.33923 | 0.004766 | -0.103 | -0.032684 | -0.20718 | -0.18567 | 121.9232 | 121.6403 | 121.6678 | 62.2527 | -122.0196 | 121.7326 | 121.8647 | 121.8862 | 62.3432 | -122.1422
2.1406 | 122.2366 | -62.2833 | 59.8114 | 1.4211e-13 | -0.021186 | -0.0030192 | 0.067075 | -0.003863 | 0.0603 | 0.0021363 | 0.00099775 | -0.0019016 | -0.0027988 | 0.0165 | -0.0085312 | -62.2879 | -0.003172 | -62.241 | 59.6536 | 59.3707 | 59.4028 | -62.2174 | -62.2511 | 0.082776 | -62.3589 | 59.4722 | 59.5951 | 59.6074 | -62.3308 | 0.065946 | -0.15782 | -0.004594 | 0.042348 | -0.023598 | -0.44071 | -0.40858 | -0.047425 | -0.33923 | 0.032233 | -0.075531 | -0.028106 | -0.21634 | -0.20398 | 121.9369 | 121.654 | 121.6861 | 62.2802 | -122.0288 | 121.7555 | 121.8784 | 121.8907 | 62.3661 | -122.1422
3.875 | 122.3419 | -62.265 | 59.7427 | 1.4211e-13 | -0.021827 | -0.003233 | 0.066434 | -0.0040766 | 0.0603 | -0.0054937 | 0.00057035 | -0.0016878 | -0.0023714 | 0.0165 | -0.0083176 | -62.2879 | -0.003172 | -62.2364 | 59.6582 | 59.3753 | 59.4074 | -62.2174 | -62.2557 | 0.082776 | -62.368 | 59.4767 | 59.6088 | 59.6074 | -62.3399 | 0.047636 | -0.084578 | -0.022904 | 0.028617 | -0.019019 | -0.36746 | -0.33534 | -0.074892 | -0.26599 | 0.009345 | -0.103 | -0.028106 | -0.13394 | -0.13532 | 121.9232 | 121.6403 | 121.6724 | 62.2618 | -121.9601 | 121.7418 | 121.8738 | 121.8724 | 62.3478 | -122.0826
5.5781 | 122.1817 | -62.2559 | 59.8022 | 1.4211e-13 | -0.021186 | -0.003233 | 0.066648 | -0.0040766 | 0.0603 | 0.0021363 | 0.00057035 | -0.0016878 | -0.002585 | 0.016713 | -0.0085312 | -62.2925 | 0.005985 | -62.2456 | 59.6536 | 59.3799 | 59.412 | -62.222 | -62.2511 | 0.078197 | -62.368 | 59.4722 | 59.5951 | 59.5937 | -62.3308 | 0.033901 | -0.14866 | -0.036639 | 0.010304 | -0.023597 | -0.42239 | -0.39027 | -0.074891 | -0.33008 | 0.004767 | -0.11215 | -0.037263 | -0.20718 | -0.20856 | 121.9094 | 121.6357 | 121.6678 | 62.2618 | -122.0242 | 121.728 | 121.8509 | 121.8495 | 62.3341 | -122.133
7.3281 | 122.2137 | -62.265 | 59.8068 | 1.4211e-13 | -0.021613 | -0.003233 | 0.066434 | -0.003863 | 0.060086 | -0.013124 | 0.00078395 | -0.0016878 | -0.002585 | 0.016713 | -0.0087448 | -62.2833 | 0.001407 | -62.2364 | 59.6582 | 59.3753 | 59.412 | -62.2174 | -62.2511 | 0.087354 | -62.368 | 59.4767 | 59.5951 | 59.6074 | -62.3353 | 0.047636 | -0.14867 | -0.018326 | 0.028617 | -0.019019 | -0.43155 | -0.39485 | -0.070314 | -0.33008 | 0.013923 | -0.103 | -0.032684 | -0.21176 | -0.1994 | 121.9232 | 121.6403 | 121.677 | 62.2664 | -122.0242 | 121.7418 | 121.8601 | 121.8724 | 62.3524 | -122.1422
9.0156 | 122.1909 | -62.2833 | 59.8022 | 1.4211e-13 | -0.021613 | -0.003233 | 0.066861 | -0.0042904 | 0.0603 | 0.0021363 | 0.00078395 | -0.0016878 | -0.002585 | 0.0165 | -0.0085312 | -62.2925 | 0.001407 | -62.241 | 59.649 | 59.3753 | 59.4028 | -62.222 | -62.2511 | 0.082776 | -62.3543 | 59.4767 | 59.5951 | 59.5845 | -62.3399 | 0.061367 | -0.15324 | -0.009173 | 0.042348 | -0.019019 | -0.42697 | -0.39943 | -0.056582 | -0.3255 | 0.032233 | -0.070952 | -0.01437 | -0.20718 | -0.21772 | 121.9323 | 121.6586 | 121.6861 | 62.2847 | -122.0242 | 121.7601 | 121.8784 | 121.8679 | 62.3661 | -122.1422
10.75 | 122.2733 | -62.2696 | 59.7473 | 1.4211e-13 | -0.021613 | -0.003233 | 0.066434 | -0.003863 | 0.060086 | 0.0021363 | 0.00057035 | -0.0016878 | -0.0030124 | 0.016713 | -0.0083176 | -62.2925 | -0.003172 | -62.2272 | 59.6582 | 59.389 | 59.412 | -62.222 | -62.2465 | 0.078197 | -62.3589 | 59.4767 | 59.5996 | 59.612 | -62.3399 | 0.047634 | -0.089155 | -0.022906 | 0.04235 | -0.005284 | -0.3583 | -0.33534 | -0.070315 | -0.27057 | 0.023079 | -0.089264 | -0.018949 | -0.14767 | -0.13532 | 121.9278 | 121.6586 | 121.6816 | 62.2664 | -121.9693 | 121.7463 | 121.8692 | 121.8816 | 62.3478 | -122.0872
12.4844 | 122.2137 | -62.2925 | 59.8022 | 1.4211e-13 | -0.021399 | -0.0034466 | 0.066648 | -0.003863 | 0.060086 | -0.013124 | 0.00035675 | -0.0019016 | -0.002585 | 0.016286 | -0.0081038 | -62.2879 | 0.001407 | -62.241 | 59.6582 | 59.3799 | 59.412 | -62.2174 | -62.2511 | 0.082776 | -62.3634 | 59.4813 | 59.5996 | 59.6257 | -62.3445 | 0.075101 | -0.14409 | 0.004561 | 0.051503 | -0.023598 | -0.42239 | -0.39027 | -0.052006 | -0.32092 | 0.041388 | -0.070955 | -0.018949 | -0.20261 | -0.17651 | 121.9506 | 121.6723 | 121.7045 | 62.2939 | -122.0196 | 121.7738 | 121.8921 | 121.9182 | 62.3753 | -122.1467
14.2344 | 122.2092 | -62.3016 | 59.8206 | 1.4211e-13 | -0.021613 | -0.0034466 | 0.066861 | -0.0040766 | 0.060086 | 0.0097668 | 0.00035675 | -0.0016878 | -0.0023714 | 0.0165 | -0.0085312 | -62.2925 | 0.001407 | -62.241 | 59.649 | 59.3799 | 59.4028 | -62.2082 | -62.2511 | 0.073618 | -62.3589 | 59.4813 | 59.5951 | 59.6212 | -62.3445 | 0.093415 | -0.17155 | 0.009138 | 0.060659 | -0.032756 | -0.44071 | -0.41774 | -0.04285 | -0.33923 | 0.050544 | -0.05722 | -0.01437 | -0.2255 | -0.1994 | 121.9506 | 121.6815 | 121.7045 | 62.303 | -122.0288 | 121.783 | 121.8967 | 121.9228 | 62.3753 | -122.165
16 | 122.1909 | -62.3291 | 59.7885 | 1.4211e-13 | -0.021613 | -0.0034466 | 0.066648 | -0.0040766 | 0.060086 | 0.0021363 | 0.00057035 | -0.0016878 | -0.002585 | 0.016713 | -0.0083176 | -62.2879 | -0.003172 | -62.241 | 59.6536 | 59.3753 | 59.3982 | -62.2082 | -62.2648 | 0.082776 | -62.3634 | 59.4767 | 59.5996 | 59.5983 | -62.3445 | 0.12088 | -0.13493 | 0.041183 | 0.088125 | -0.032756 | -0.41324 | -0.39027 | -0.015384 | -0.31177 | 0.064274 | -0.034333 | -0.018949 | -0.18887 | -0.19025 | 121.9827 | 121.7044 | 121.7273 | 62.3259 | -121.9967 | 121.8058 | 121.9287 | 121.9274 | 62.4119 | -122.133
17.6875 | 122.2549 | -62.3245 | 59.7702 | 1.4211e-13 | -0.021827 | -0.0034466 | 0.066648 | -0.0040766 | 0.060086 | 0.0021363 | 0.00035675 | -0.0016878 | -0.0027988 | 0.016286 | -0.0083176 | -62.2879 | 0.001407 | -62.2364 | 59.6582 | 59.3844 | 59.4074 | -62.2174 | -62.2557 | 0.073618 | -62.3589 | 59.4813 | 59.5996 | 59.6166 | -62.3399 | 0.10714 | -0.11204 | 0.036605 | 0.088126 | -0.019019 | -0.38577 | -0.36281 | -0.015383 | -0.28888 | 0.068854 | -0.034332 | -0.018949 | -0.17056 | -0.15363 | 121.9827 | 121.709 | 121.7319 | 62.3259 | -121.9876 | 121.8058 | 121.9242 | 121.9411 | 62.3981 | -122.1101
19.4219 | 122.2137 | -62.3154 | 59.7656 | 1.4211e-13 | -0.021613 | -0.0034466 | 0.066648 | -0.0040766 | 0.060086 | -0.0054937 | 0.00078395 | -0.0012606 | -0.0027988 | 0.016713 | -0.0085312 | -62.2833 | 0.001407 | -62.2364 | 59.6582 | 59.3799 | 59.4074 | -62.2174 | -62.2557 | 0.078197 | -62.3634 | 59.4722 | 59.5996 | 59.5937 | -62.3445 | 0.09799 | -0.10747 | 0.032028 | 0.078971 | -0.019019 | -0.38577 | -0.35823 | -0.029117 | -0.29346 | 0.059699 | -0.048066 | -0.018949 | -0.16598 | -0.17194 | 121.9735 | 121.6952 | 121.7228 | 62.3168 | -121.983 | 121.7875 | 121.915 | 121.9091 | 62.3936 | -122.1101
21.1562 | 122.2549 | -62.2787 | 59.7839 | 1.4211e-13 | -0.021613 | -0.003233 | 0.066648 | -0.0040766 | 0.060086 | -0.0054937 | 0.00057035 | -0.0012606 | -0.002585 | 0.017141 | -0.0083176 | -62.2879 | -0.003172 | -62.2456 | 59.6582 | 59.3753 | 59.4074 | -62.2128 | -62.2465 | 0.078197 | -62.3634 | 59.4767 | 59.6088 | 59.5983 | -62.3308 | 0.065948 | -0.12578 | -0.009171 | 0.033193 | -0.032755 | -0.40866 | -0.37654 | -0.052002 | -0.30719 | 0.032235 | -0.084687 | -0.032685 | -0.17514 | -0.18567 | 121.9369 | 121.654 | 121.6861 | 62.2756 | -121.9967 | 121.7555 | 121.8875 | 121.877 | 62.3569 | -122.1147
22.8906 | 122.2229 | -62.3108 | 59.7977 | 1.4211e-13 | -0.021613 | -0.0034466 | 0.066861 | -0.0042904 | 0.060086 | 0.0021363 | 0.00057035 | -0.0021152 | -0.0027988 | 0.016927 | -0.0083176 | -62.2879 | -0.003172 | -62.2364 | 59.6536 | 59.3844 | 59.4074 | -62.2174 | -62.2557 | 0.078197 | -62.3589 | 59.4767 | 59.5951 | 59.6212 | -62.3399 | 0.093412 | -0.14409 | 0.022872 | 0.074393 | -0.019019 | -0.41324 | -0.39027 | -0.029116 | -0.32092 | 0.055121 | -0.048065 | -0.018949 | -0.20261 | -0.17651 | 121.9644 | 121.6952 | 121.7182 | 62.3076 | -122.015 | 121.7875 | 121.9059 | 121.9319 | 62.389 | -122.1376
24.5625 | 122.3282 | -62.2559 | 59.7931 | 1.4211e-13 | -0.021827 | -0.003233 | 0.066861 | -0.0040766 | 0.060086 | 0.0021363 | 0.00057035 | -0.0019016 | -0.0023714 | 0.016713 | -0.0085312 | -62.2879 | 0.001407 | -62.241 | 59.6536 | 59.3799 | 59.4074 | -62.2174 | -62.2602 | 0.082776 | -62.3543 | 59.4767 | 59.5951 | 59.6257 | -62.3399 | 0.03848 | -0.13951 | -0.03206 | 0.014882 | -0.023598 | -0.41324 | -0.38569 | -0.084048 | -0.31634 | -0.00439 | -0.098418 | -0.01437 | -0.19803 | -0.16736 | 121.9094 | 121.6357 | 121.6633 | 62.2573 | -122.0105 | 121.7326 | 121.8509 | 121.8816 | 62.3386 | -122.133
26.25 | 122.3099 | -62.2742 | 59.7794 | 1.4211e-13 | -0.02204 | -0.003233 | 0.066861 | -0.0042904 | 0.0603 | -0.0054937 | 0.00057035 | -0.0019016 | -0.002585 | 0.016713 | -0.0083176 | -62.2925 | 0.001407 | -62.2364 | 59.649 | 59.3844 | 59.412 | -62.2128 | -62.2511 | 0.091933 | -62.3543 | 59.4767 | 59.5905 | 59.612 | -62.3353 | 0.06137 | -0.13036 | -0.018328 | 0.037772 | -0.023598 | -0.39493 | -0.36738 | -0.061159 | -0.30261 | 0.023078 | -0.080107 | -0.018948 | -0.18888 | -0.16736 | 121.9232 | 121.6586 | 121.6861 | 62.2756 | -121.9922 | 121.7509 | 121.8647 | 121.8862 | 62.3661 | -122.1147
27.9844 | 122.3282 | -62.2559 | 59.8022 | 1.4211e-13 | -0.02204 | -0.003233 | 0.066648 | -0.003863 | 0.060086 | 0.0021363 | 0.00057035 | -0.0019016 | -0.0027988 | 0.016713 | -0.0085312 | -62.2833 | 0.001407 | -62.2318 | 59.6536 | 59.3753 | 59.4028 | -62.222 | -62.2557 | 0.078197 | -62.3634 | 59.4722 | 59.6042 | 59.5799 | -62.3308 | 0.033901 | -0.14866 | -0.027482 | 0.024039 | -0.009862 | -0.42697 | -0.39943 | -0.074891 | -0.33008 | 0.000189 | -0.10758 | -0.032685 | -0.19803 | -0.2223 | 121.9094 | 121.6311 | 121.6587 | 62.2573 | -122.0242 | 121.728 | 121.8601 | 121.8358 | 62.3341 | -122.133
29.7188 | 122.3053 | -62.2925 | 59.7198 | 1.4211e-13 | -0.021827 | -0.003233 | 0.066648 | -0.0042904 | 0.060086 | -0.0054937 | 0.00035675 | -0.0016878 | -0.002585 | 0.016713 | -0.0085312 | -62.2833 | 0.005985 | -62.2364 | 59.6582 | 59.3799 | 59.4074 | -62.222 | -62.2511 | 0.087354 | -62.3634 | 59.4722 | 59.5951 | 59.6074 | -62.3353 | 0.070522 | -0.06169 | 0.009139 | 0.056082 | -0.01444 | -0.34 | -0.31245 | -0.042849 | -0.24768 | 0.041388 | -0.070955 | -0.028106 | -0.12479 | -0.11243 | 121.9506 | 121.6723 | 121.6999 | 62.2985 | -121.9418 | 121.7646 | 121.8875 | 121.8999 | 62.3798 | -122.0552
31.4688 | 122.2183 | -62.2925 | 59.8206 | 1.4211e-13 | -0.021827 | -0.0034466 | 0.066648 | -0.003863 | 0.0603 | -0.013124 | 0.00035675 | -0.0016878 | -0.0030124 | 0.016713 | -0.0085312 | -62.2925 | 0.005985 | -62.2364 | 59.6582 | 59.3844 | 59.4074 | -62.222 | -62.2465 | 0.087354 | -62.3589 | 59.4767 | 59.5996 | 59.612 | -62.3308 | 0.070522 | -0.1624 | -1.8e-05 | 0.056082 | -0.01444 | -0.43613 | -0.41316 | -0.03827 | -0.34381 | 0.045967 | -0.066376 | -0.028106 | -0.22092 | -0.20856 | 121.9506 | 121.6769 | 121.6999 | 62.2985 | -122.0425 | 121.7692 | 121.8921 | 121.9045 | 62.3798 | -122.1513
33.1406 | 122.2549 | -62.2925 | 59.7794 | 1.4211e-13 | -0.02204 | -0.003233 | 0.066861 | -0.0040766 | 0.060086 | -0.013124 | 0.00057035 | -0.0016878 | -0.002585 | 0.016713 | -0.0085312 | -62.2879 | -0.003172 | -62.241 | 59.6536 | 59.389 | 59.4074 | -62.222 | -62.2511 | 0.082776 | -62.3589 | 59.4813 | 59.6042 | 59.6212 | -62.3353 | 0.070522 | -0.12578 | 0.004561 | 0.051503 | -0.019019 | -0.39035 | -0.37196 | -0.042849 | -0.29803 | 0.041388 | -0.066376 | -0.023527 | -0.17514 | -0.1582 | 121.9461 | 121.6815 | 121.6999 | 62.2893 | -122.0013 | 121.7738 | 121.8967 | 121.9136 | 62.3753 | -122.1147
34.875 | 122.3053 | -62.2879 | 59.729 | 1.4211e-13 | -0.021827 | -0.003233 | 0.067075 | -0.004504 | 0.0603 | -0.0054937 | 0.00035675 | -0.0019016 | -0.002585 | 0.0165 | -0.0081038 | -62.2879 | -0.003172 | -62.2456 | 59.6536 | 59.3799 | 59.4074 | -62.2174 | -62.2557 | 0.082776 | -62.368 | 59.4859 | 59.6042 | 59.5983 | -62.3353 | 0.070524 | -0.075423 | -1.6e-05 | 0.042348 | -0.028176 | -0.34915 | -0.32161 | -0.047426 | -0.2431 | 0.032233 | -0.08011 | -0.032684 | -0.12479 | -0.13074 | 121.9415 | 121.6678 | 121.6953 | 62.2847 | -121.9464 | 121.7738 | 121.8921 | 121.8862 | 62.3707 | -122.0643
36.5625 | 122.2458 | -62.2833 | 59.7885 | 1.4211e-13 | -0.02204 | -0.0034466 | 0.066434 | -0.0042904 | 0.0603 | -0.013124 | 0.00057035 | -0.0014742 | -0.003226 | 0.016927 | -0.0083176 | -62.2879 | 0.005985 | -62.2318 | 59.6536 | 59.3799 | 59.4028 | -62.2174 | -62.2648 | 0.087354 | -62.3543 | 59.4813 | 59.5905 | 59.5891 | -62.3445 | 0.065946 | -0.13493 | -0.004594 | 0.051505 | -0.014441 | -0.40866 | -0.38569 | -0.061161 | -0.30719 | 0.018497 | -0.070952 | -0.009791 | -0.19803 | -0.19941 | 121.9369 | 121.6632 | 121.6861 | 62.2893 | -122.0059 | 121.7647 | 121.8738 | 121.8724 | 62.3707 | -122.133
38.3125 | 122.2549 | -62.2559 | 59.8297 | 1.4211e-13 | -0.022254 | -0.0034466 | 0.066861 | -0.004504 | 0.060086 | -0.0054937 | 0.00057035 | -0.0016878 | -0.0030124 | 0.016713 | -0.0087448 | -62.2879 | -0.003172 | -62.2456 | 59.6536 | 59.3753 | 59.4074 | -62.2174 | -62.2511 | 0.082776 | -62.3589 | 59.4767 | 59.5905 | 59.5891 | -62.3399 | 0.03848 | -0.17613 | -0.03206 | 0.010304 | -0.028176 | -0.45444 | -0.42231 | -0.084048 | -0.35296 | 0.004767 | -0.103 | -0.018949 | -0.23923 | -0.24061 | 121.9094 | 121.6311 | 121.6633 | 62.2527 | -122.0471 | 121.7326 | 121.8463 | 121.845 | 62.3386 | -122.1696
40.0625 | 122.2504 | -62.2833 | 59.8114 | 1.4211e-13 | -0.021827 | -0.0030192 | 0.066648 | -0.004504 | 0.060086 | -0.0054937 | 0.00057035 | -0.0014742 | -0.0027988 | 0.017141 | -0.0085312 | -62.2879 | 0.005985 | -62.2364 | 59.6536 | 59.3753 | 59.412 | -62.2174 | -62.2557 | 0.078197 | -62.3589 | 59.4813 | 59.5951 | 59.5937 | -62.3353 | 0.065946 | -0.15782 | -0.004594 | 0.046927 | -0.019019 | -0.43613 | -0.39942 | -0.052004 | -0.33007 | 0.027655 | -0.075531 | -0.023527 | -0.21634 | -0.21772 | 121.9369 | 121.6586 | 121.6953 | 62.2893 | -122.0288 | 121.7647 | 121.8784 | 121.877 | 62.3615 | -122.1467
41.8125 | 122.2275 | -62.2559 | 59.8526 | 1.4211e-13 | -0.02204 | -0.0034466 | 0.066434 | -0.0040766 | 0.0603 | -0.013124 | 0.00078395 | -0.0016878 | -0.002585 | 0.017141 | -0.0085312 | -62.2879 | 0.001407 | -62.2456 | 59.6582 | 59.3799 | 59.4028 | -62.222 | -62.2557 | 0.087354 | -62.368 | 59.4813 | 59.5951 | 59.6028 | -62.3308 | 0.033901 | -0.19444 | -0.03206 | 0.010304 | -0.023597 | -0.47275 | -0.44978 | -0.074891 | -0.37127 | 0.000189 | -0.11215 | -0.037263 | -0.25754 | -0.24976 | 121.914 | 121.6357 | 121.6587 | 62.2573 | -122.0746 | 121.7372 | 121.8509 | 121.8587 | 62.3432 | -122.1834
43.4844 | 122.2 | -62.3062 | 59.8022 | 1.4211e-13 | -0.02204 | -0.0030192 | 0.066861 | -0.004504 | 0.060086 | 0.0021363 | 0.00057035 | -0.0021152 | -0.0027988 | 0.017354 | -0.0083176 | -62.2879 | 0.005985 | -62.2364 | 59.6582 | 59.3844 | 59.4074 | -62.2128 | -62.2511 | 0.078197 | -62.3543 | 59.4813 | 59.5996 | 59.6303 | -62.3353 | 0.093413 | -0.14409 | 0.018294 | 0.069815 | -0.023598 | -0.41781 | -0.39485 | -0.029116 | -0.32092 | 0.055121 | -0.048064 | -0.018948 | -0.20261 | -0.17193 | 121.9644 | 121.6906 | 121.7136 | 62.3122 | -122.015 | 121.7875 | 121.9059 | 121.9365 | 62.3844 | -122.1376
45.2344 | 122.3099 | -62.265 | 59.761 | 1.4211e-13 | -0.021827 | -0.0030192 | 0.066434 | -0.004504 | 0.060086 | -0.013124 | 0.00057035 | -0.0016878 | -0.0027988 | 0.016927 | -0.0087448 | -62.2833 | -0.003172 | -62.241 | 59.6582 | 59.3844 | 59.4074 | -62.2265 | -62.2557 | 0.082776 | -62.3589 | 59.4722 | 59.5951 | 59.6257 | -62.3308 | 0.038478 | -0.10289 | -0.018326 | 0.024038 | -0.01444 | -0.37662 | -0.35365 | -0.065735 | -0.28888 | 0.009345 | -0.093841 | -0.028106 | -0.16599 | -0.13531 | 121.9232 | 121.6494 | 121.6724 | 62.2618 | -121.9876 | 121.7372 | 121.8601 | 121.8907 | 62.3478 | -122.0918
46.9844 | 122.319 | -62.2467 | 59.7656 | 1.4211e-13 | -0.022254 | -0.0034466 | 0.066861 | -0.004504 | 0.060086 | -0.0054937 | 0.00078395 | -0.0016878 | -0.002585 | 0.016713 | -0.0085312 | -62.2879 | 0.005985 | -62.2456 | 59.6536 | 59.3844 | 59.4074 | -62.2265 | -62.2557 | 0.078197 | -62.3589 | 59.4859 | 59.5996 | 59.612 | -62.3399 | 0.020167 | -0.11204 | -0.041215 | 0.001149 | -0.019018 | -0.38119 | -0.35823 | -0.093203 | -0.27972 | -0.008966 | -0.11215 | -0.018949 | -0.16598 | -0.15363 | 121.9003 | 121.6311 | 121.6541 | 62.2527 | -121.9922 | 121.7326 | 121.8463 | 121.8587 | 62.3249 | -122.1055
48.6562 | 122.3465 | -62.2833 | 59.7382 | 1.4211e-13 | -0.022254 | -0.0034466 | 0.066861 | -0.0047176 | 0.060086 | -0.013124 | 0.00057035 | -0.0019016 | -0.002585 | 0.016927 | -0.0085312 | -62.2879 | 0.005985 | -62.2364 | 59.6536 | 59.3844 | 59.4166 | -62.222 | -62.2557 | 0.073618 | -62.3589 | 59.4813 | 59.5951 | 59.6257 | -62.3399 | 0.061367 | -0.084578 | -0.004594 | 0.046927 | -0.01444 | -0.35373 | -0.32161 | -0.056582 | -0.25683 | 0.027655 | -0.075531 | -0.018949 | -0.1431 | -0.11243 | 121.9369 | 121.6678 | 121.6999 | 62.2893 | -121.9601 | 121.7647 | 121.8784 | 121.9091 | 62.3569 | -122.0781
50.3438 | 122.2504 | -62.265 | 59.816 | 1.4211e-13 | -0.022468 | -0.003233 | 0.066434 | -0.0047176 | 0.059873 | -0.0054937 | 0.00057035 | -0.0019016 | -0.0030124 | 0.016927 | -0.0083176 | -62.2971 | -0.003172 | -62.241 | 59.6536 | 59.3799 | 59.4166 | -62.222 | -62.2511 | 0.082776 | -62.3589 | 59.4722 | 59.5996 | 59.6257 | -62.3399 | 0.043057 | -0.1624 | -0.032061 | 0.024038 | -0.019019 | -0.43613 | -0.39943 | -0.074892 | -0.34381 | 0.013923 | -0.093841 | -0.018949 | -0.21634 | -0.19024 | 121.9186 | 121.6449 | 121.6816 | 62.2618 | -122.0379 | 121.7372 | 121.8647 | 121.8907 | 62.3478 | -122.1559
52.0938 | 122.2961 | -62.2833 | 59.7656 | 1.4211e-13 | -0.022254 | -0.0030192 | 0.067075 | -0.0042904 | 0.060514 | 0.0021363 | 0.00035675 | -0.0016878 | -0.002585 | 0.017141 | -0.0089584 | -62.2971 | 0.001407 | -62.2364 | 59.6582 | 59.3799 | 59.412 | -62.2174 | -62.2602 | 0.087354 | -62.3634 | 59.4813 | 59.5996 | 59.6257 | -62.3308 | 0.065946 | -0.10747 | -0.013751 | 0.046927 | -0.019019 | -0.38577 | -0.35365 | -0.047425 | -0.2843 | 0.023076 | -0.08011 | -0.032685 | -0.16598 | -0.13989 | 121.9415 | 121.6632 | 121.6953 | 62.2847 | -121.983 | 121.7647 | 121.883 | 121.9091 | 62.3707 | -122.0964
53.8281 | 122.3145 | -62.2879 | 59.7427 | 1.4211e-13 | -0.02204 | -0.0034466 | 0.066434 | -0.004504 | 0.0603 | 0.0097668 | 0.00035675 | -0.0016878 | -0.0027988 | 0.017141 | -0.0085312 | -62.2879 | 0.001407 | -62.241 | 59.6536 | 59.389 | 59.412 | -62.2174 | -62.2557 | 0.078197 | -62.3589 | 59.4813 | 59.5951 | 59.5845 | -62.3399 | 0.070524 | -0.089156 | -1.6e-05 | 0.046926 | -0.023598 | -0.35373 | -0.33076 | -0.052004 | -0.26141 | 0.032233 | -0.070953 | -0.018949 | -0.14768 | -0.15821 | 121.9415 | 121.6769 | 121.6999 | 62.2893 | -121.9601 | 121.7692 | 121.883 | 121.8724 | 62.3661 | -122.0826
55.5 | 122.2412 | -62.2787 | 59.7839 | 1.4211e-13 | -0.022254 | -0.0034466 | 0.066648 | -0.004504 | 0.060086 | -0.0054937 | 0.00078395 | -0.0016878 | -0.002585 | 0.016927 | -0.0087448 | -62.2833 | 0.005985 | -62.241 | 59.6536 | 59.3799 | 59.412 | -62.222 | -62.2511 | 0.087354 | -62.3589 | 59.4767 | 59.5951 | 59.6257 | -62.3445 | 0.05679 | -0.13035 | -0.004593 | 0.037771 | -0.019019 | -0.40408 | -0.37196 | -0.065738 | -0.30719 | 0.027656 | -0.080108 | -0.01437 | -0.18887 | -0.1582 | 121.9323 | 121.6586 | 121.6907 | 62.2847 | -122.0059 | 121.7555 | 121.8738 | 121.9045 | 62.3661 | -122.1284
57.2344 | 122.3282 | -62.2833 | 59.7427 | 1.4211e-13 | -0.02204 | -0.0030192 | 0.06622 | -0.0042904 | 0.060727 | -0.0054937 | 0.00035675 | -0.0016878 | -0.002585 | 0.016927 | -0.0085312 | -62.2833 | -0.003172 | -62.2501 | 59.6582 | 59.3799 | 59.4074 | -62.2265 | -62.2602 | 0.078197 | -62.3543 | 59.4813 | 59.5996 | 59.5983 | -62.3399 | 0.056788 | -0.084578 | -1.6e-05 | 0.033192 | -0.023596 | -0.36288 | -0.33534 | -0.056582 | -0.26141 | 0.023076 | -0.070952 | -0.01437 | -0.1431 | -0.14447 | 121.9415 | 121.6632 | 121.6907 | 62.2802 | -121.9693 | 121.7647 | 121.883 | 121.8816 | 62.3615 | -122.0826
58.9844 | 122.3419 | -62.2742 | 59.7382 | 1.4211e-13 | -0.022468 | -0.0034466 | 0.066434 | -0.0040766 | 0.0603 | -0.013124 | 0.00014315 | -0.0019016 | -0.0023714 | 0.017141 | -0.0087448 | -62.2788 | 0.001407 | -62.241 | 59.6582 | 59.3844 | 59.412 | -62.2128 | -62.2511 | 0.078197 | -62.3589 | 59.4813 | 59.5996 | 59.6303 | -62.3399 | 0.06137 | -0.08 | -0.004593 | 0.033193 | -0.028177 | -0.35373 | -0.32618 | -0.065737 | -0.25683 | 0.023078 | -0.084686 | -0.018949 | -0.13852 | -0.10785 | 121.9323 | 121.6586 | 121.6861 | 62.2756 | -121.951 | 121.7555 | 121.8738 | 121.9045 | 62.3524 | -122.0781
60.6719 | 122.2504 | -62.3016 | 59.8022 | 1.4211e-13 | -0.022468 | -0.003233 | 0.066648 | -0.0042904 | 0.060086 | -0.0054937 | 0.00014315 | -0.0014742 | -0.002585 | 0.016713 | -0.0083176 | -62.2925 | 0.001407 | -62.241 | 59.6536 | 59.3799 | 59.4166 | -62.222 | -62.2557 | 0.082776 | -62.3589 | 59.4722 | 59.5996 | 59.6212 | -62.3353 | 0.079678 | -0.14866 | 0.009138 | 0.060659 | -0.019019 | -0.42239 | -0.38569 | -0.033693 | -0.33008 | 0.045966 | -0.05722 | -0.023527 | -0.20261 | -0.18109 | 121.9552 | 121.6815 | 121.7182 | 62.303 | -122.0242 | 121.7738 | 121.9013 | 121.9228 | 62.3844 | -122.1376
62.4219 | 122.2046 | -62.3016 | 59.7931 | 1.4211e-13 | -0.022254 | -0.003233 | 0.066434 | -0.0042904 | 0.060086 | 0.0021363 | 0.00057035 | -0.0014742 | -0.003226 | 0.016927 | -0.0087448 | -62.2788 | -0.003172 | -62.2456 | 59.6536 | 59.3844 | 59.412 | -62.222 | -62.2557 | 0.082776 | -62.3589 | 59.4767 | 59.5951 | 59.6212 | -62.3399 | 0.079678 | -0.13951 | 0.022873 | 0.056081 | -0.023597 | -0.40866 | -0.38111 | -0.038271 | -0.31634 | 0.045966 | -0.05722 | -0.018949 | -0.19803 | -0.17194 | 121.9552 | 121.6861 | 121.7136 | 62.2985 | -122.015 | 121.7784 | 121.8967 | 121.9228 | 62.3844 | -122.133
64.1562 | 122.3145 | -62.2696 | 59.7748 | 1.4211e-13 | -0.022468 | -0.003233 | 0.067075 | -0.0047176 | 0.060086 | -0.0054937 | 0.00078395 | -0.0019016 | -0.0027988 | 0.016927 | -0.0085312 | -62.2879 | 0.005985 | -62.2318 | 59.6536 | 59.3844 | 59.4074 | -62.222 | -62.2465 | 0.091933 | -62.3634 | 59.4813 | 59.6088 | 59.6166 | -62.3353 | 0.047634 | -0.1212 | -0.018327 | 0.037772 | -0.009862 | -0.39035 | -0.36738 | -0.065737 | -0.29345 | 0.023079 | -0.093843 | -0.028106 | -0.16598 | -0.1582 | 121.9232 | 121.654 | 121.677 | 62.2756 | -121.9967 | 121.7509 | 121.8784 | 121.8862 | 62.3615 | -122.1101
65.8438 | 122.3373 | -62.265 | 59.7107 | 1.4211e-13 | -0.022681 | -0.0036602 | 0.066648 | -0.0040766 | 0.059873 | 0.0021363 | 0.00014315 | -0.0014742 | -0.0027988 | 0.017141 | -0.0085312 | -62.2833 | -0.003172 | -62.241 | 59.6582 | 59.3844 | 59.4074 | -62.222 | -62.2557 | 0.082776 | -62.3543 | 59.4813 | 59.6042 | 59.6257 | -62.3399 | 0.043057 | -0.052534 | -0.018326 | 0.024038 | -0.019019 | -0.32626 | -0.3033 | -0.074892 | -0.22937 | 0.009345 | -0.089262 | -0.01437 | -0.10647 | -0.084959 | 121.9232 | 121.6494 | 121.6724 | 62.2618 | -121.9327 | 121.7463 | 121.8692 | 121.8907 | 62.3478 | -122.0506
67.5781 | 122.3145 | -62.2742 | 59.7519 | 1.4211e-13 | -0.022468 | -0.0034466 | 0.066434 | -0.0042904 | 0.059873 | 0.0021363 | 0.00099775 | -0.0021152 | -0.002585 | 0.016927 | -0.0089584 | -62.2788 | 0.001407 | -62.2318 | 59.6536 | 59.3799 | 59.4166 | -62.2265 | -62.2511 | 0.082776 | -62.3589 | 59.4813 | 59.6042 | 59.612 | -62.3399 | 0.047633 | -0.098311 | -0.004593 | 0.04235 | -0.005283 | -0.37204 | -0.33534 | -0.065737 | -0.27057 | 0.023078 | -0.084686 | -0.018949 | -0.14767 | -0.13989 | 121.9278 | 121.654 | 121.6907 | 62.2756 | -121.9784 | 121.7555 | 121.8784 | 121.8862 | 62.3569 | -122.0918
69.25 | 122.2549 | -62.2787 | 59.8297 | 1.4211e-13 | -0.022681 | -0.0034466 | 0.066434 | -0.0042904 | 0.059873 | 0.0097668 | 0.00078395 | -0.0016878 | -0.0027988 | 0.017141 | -0.0087448 | -62.2833 | -0.003172 | -62.2364 | 59.6536 | 59.3799 | 59.412 | -62.2174 | -62.2557 | 0.073618 | -62.3634 | 59.4767 | 59.5996 | 59.6395 | -62.3445 | 0.061369 | -0.17613 | -0.004593 | 0.04235 | -0.019019 | -0.44986 | -0.41774 | -0.065738 | -0.35296 | 0.023078 | -0.084687 | -0.018949 | -0.23007 | -0.19024 | 121.9323 | 121.6586 | 121.6907 | 62.2756 | -122.0471 | 121.7555 | 121.8784 | 121.9182 | 62.3524 | -122.1742
71 | 122.3053 | -62.2787 | 59.7519 | 1.4211e-13 | -0.022681 | -0.0034466 | 0.066434 | -0.0047176 | 0.059873 | -0.013124 | 0.00035675 | -0.0019016 | -0.0027988 | 0.017141 | -0.0085312 | -62.2833 | -0.003172 | -62.241 | 59.649 | 59.3844 | 59.4166 | -62.2128 | -62.2557 | 0.082776 | -62.3589 | 59.4813 | 59.5951 | 59.5937 | -62.3399 | 0.065948 | -0.10289 | -0.004593 | 0.037771 | -0.028177 | -0.36746 | -0.33534 | -0.061159 | -0.27057 | 0.023078 | -0.080108 | -0.018949 | -0.15683 | -0.15821 | 121.9278 | 121.6632 | 121.6953 | 62.2756 | -121.9647 | 121.7601 | 121.8738 | 121.8724 | 62.3615 | -122.0918
72.6875 | 122.3785 | -62.2375 | 59.7656 | 1.4211e-13 | -0.022468 | -0.0034466 | 0.066861 | -0.004504 | 0.059659 | 0.0021363 | 0.00078395 | -0.0019016 | -0.0027988 | 0.016927 | -0.0085312 | -62.2925 | -0.003172 | -62.2364 | 59.6582 | 59.3799 | 59.4074 | -62.2174 | -62.2557 | 0.073618 | -62.3589 | 59.4813 | 59.5951 | 59.6257 | -62.3399 | 0.02017 | -0.10747 | -0.054949 | 0.001151 | -0.019019 | -0.38577 | -0.35823 | -0.10236 | -0.2843 | -0.018121 | -0.12131 | -0.018949 | -0.17056 | -0.13989 | 121.8957 | 121.6174 | 121.6449 | 62.2344 | -121.983 | 121.7189 | 121.8326 | 121.8633 | 62.3112 | -122.1055
74.4375 | 122.3602 | -62.2559 | 59.7794 | 1.4211e-13 | -0.022895 | -0.003233 | 0.06622 | -0.0047176 | 0.059873 | 0.0021363 | 0.00057035 | -0.0016878 | -0.0030124 | 0.017141 | -0.0087448 | -62.2879 | 0.001407 | -62.241 | 59.6582 | 59.3844 | 59.412 | -62.2082 | -62.2557 | 0.082776 | -62.3589 | 59.4767 | 59.6042 | 59.6349 | -62.3308 | 0.047638 | -0.1212 | -0.03206 | 0.014882 | -0.032756 | -0.39493 | -0.36738 | -0.074891 | -0.30261 | 0.000189 | -0.103 | -0.028106 | -0.17514 | -0.14447 | 121.914 | 121.6403 | 121.6678 | 62.2573 | -121.9876 | 121.7326 | 121.8601 | 121.8907 | 62.3386 | -122.1101
76.125 | 122.2961 | -62.2833 | 59.7519 | 1.4211e-13 | -0.022895 | -0.003233 | 0.066648 | -0.004504 | 0.059659 | -0.0054937 | 0.00057035 | -0.0016878 | -0.002585 | 0.016927 | -0.0087448 | -62.2833 | 0.001407 | -62.2318 | 59.6627 | 59.3844 | 59.4074 | -62.2265 | -62.2511 | 0.087354 | -62.3634 | 59.4813 | 59.5951 | 59.6257 | -62.3399 | 0.056788 | -0.089154 | -1.6e-05 | 0.051505 | -0.005283 | -0.36746 | -0.34449 | -0.056582 | -0.27057 | 0.032233 | -0.08011 | -0.023528 | -0.15683 | -0.12616 | 121.9461 | 121.6678 | 121.6907 | 62.2847 | -121.9784 | 121.7647 | 121.8784 | 121.9091 | 62.3707 | -122.0918
77.8438 | 122.2229 | -62.265 | 59.8297 | 1.4211e-13 | -0.022468 | -0.0034466 | 0.066861 | -0.0042904 | 0.059659 | -0.0054937 | 0.00057035 | -0.0014742 | -0.0030124 | 0.017354 | -0.0087448 | -62.2925 | 0.010564 | -62.2364 | 59.6536 | 59.389 | 59.4074 | -62.2265 | -62.2511 | 0.087354 | -62.3634 | 59.4767 | 59.5996 | 59.5937 | -62.3491 | 0.038478 | -0.17613 | -0.027483 | 0.028617 | -0.009861 | -0.4407 | -0.42231 | -0.08405 | -0.35296 | 0.013923 | -0.09842 | -0.01437 | -0.23007 | -0.23603 | 121.9186 | 121.654 | 121.6724 | 62.2756 | -122.0562 | 121.7418 | 121.8647 | 121.8587 | 62.3524 | -122.1788
79.5156 | 122.2961 | -62.2879 | 59.729 | 1.4211e-13 | -0.022681 | -0.0030192 | 0.066648 | -0.0047176 | 0.059873 | -0.0054937 | 0.00078395 | -0.0016878 | -0.0027988 | 0.017141 | -0.0087448 | -62.2833 | -0.003172 | -62.2501 | 59.6536 | 59.389 | 59.412 | -62.222 | -62.2511 | 0.082776 | -62.3634 | 59.4722 | 59.6042 | 59.6349 | -62.3399 | 0.065945 | -0.075423 | 0.004562 | 0.03777 | -0.028175 | -0.33999 | -0.31703 | -0.052004 | -0.25684 | 0.036811 | -0.075532 | -0.023528 | -0.12479 | -0.094113 | 121.9415 | 121.6769 | 121.6999 | 62.2847 | -121.951 | 121.7601 | 121.8921 | 121.9228 | 62.3707 | -122.0689
81.2656 | 122.2 | -62.2696 | 59.8526 | 1.4211e-13 | -0.023322 | -0.003233 | 0.066648 | -0.004504 | 0.059873 | -0.013124 | 0.00078395 | -0.0019016 | -0.0027988 | 0.017141 | -0.0085312 | -62.2833 | 0.001407 | -62.2501 | 59.6536 | 59.3844 | 59.4211 | -62.222 | -62.2557 | 0.082776 | -62.3634 | 59.4813 | 59.5996 | 59.6028 | -62.3491 | 0.047634 | -0.19902 | -0.013749 | 0.019459 | -0.028175 | -0.46817 | -0.43147 | -0.079473 | -0.37127 | 0.013922 | -0.093843 | -0.01437 | -0.25296 | -0.24976 | 121.9232 | 121.654 | 121.6907 | 62.271 | -122.0746 | 121.7509 | 121.8692 | 121.8724 | 62.3524 | -122.2017
83 | 122.2412 | -62.2559 | 59.7931 | 1.4211e-13 | -0.022681 | -0.0030192 | 0.066434 | -0.004504 | 0.059659 | -0.0054937 | 0.00057035 | -0.0014742 | -0.0027988 | 0.017568 | -0.0091722 | -62.2833 | 0.005985 | -62.241 | 59.649 | 59.3844 | 59.4074 | -62.2082 | -62.2557 | 0.078197 | -62.3589 | 59.4813 | 59.5951 | 59.5662 | -62.3353 | 0.047638 | -0.14409 | -0.027482 | 0.014882 | -0.032756 | -0.40866 | -0.38569 | -0.07947 | -0.31176 | 0.000189 | -0.103 | -0.023527 | -0.19803 | -0.22688 | 121.9049 | 121.6403 | 121.6633 | 62.2618 | -122.0013 | 121.7372 | 121.8509 | 121.8221 | 62.3341 | -122.1284
84.6719 | 122.3236 | -62.2604 | 59.7427 | 1.4211e-13 | -0.022895 | -0.0030192 | 0.066434 | -0.004504 | 0.059873 | 0.0097668 | 0.00035675 | -0.0016878 | -0.0023714 | 0.017354 | -0.0087448 | -62.2925 | -0.007751 | -62.2456 | 59.6536 | 59.3844 | 59.412 | -62.222 | -62.2511 | 0.087354 | -62.3543 | 59.4905 | 59.5951 | 59.6166 | -62.3491 | 0.038479 | -0.089156 | -0.032061 | 0.014882 | -0.023597 | -0.35831 | -0.33076 | -0.088628 | -0.25225 | 0.009345 | -0.09384 | -0.005212 | -0.14768 | -0.12616 | 121.914 | 121.6449 | 121.6724 | 62.2527 | -121.9647 | 121.7509 | 121.8555 | 121.877 | 62.3478 | -122.0918
86.4062 | 122.3145 | -62.2604 | 59.7794 | 1.4211e-13 | -0.022681 | -0.0030192 | 0.066861 | -0.004504 | 0.059873 | 0.0021363 | 0.00035675 | -0.0019016 | -0.002585 | 0.017141 | -0.0085312 | -62.2879 | -0.003172 | -62.2501 | 59.6582 | 59.3799 | 59.412 | -62.2174 | -62.2557 | 0.091933 | -62.368 | 59.4813 | 59.6042 | 59.6303 | -62.3399 | 0.043058 | -0.1212 | -0.027482 | 0.010304 | -0.032754 | -0.39951 | -0.36738 | -0.07947 | -0.29803 | 0.004767 | -0.10758 | -0.028106 | -0.17514 | -0.14905 | 121.9186 | 121.6403 | 121.6724 | 62.2573 | -121.9967 | 121.7418 | 121.8647 | 121.8907 | 62.3524 | -122.1193
88.1562 | 122.2504 | -62.2742 | 59.8251 | 1.4211e-13 | -0.022895 | -0.0030192 | 0.066648 | -0.0047176 | 0.059873 | -0.0054937 | 0.00099775 | -0.0019016 | -0.002585 | 0.017141 | -0.0083176 | -62.2879 | 0.001407 | -62.241 | 59.6536 | 59.3753 | 59.412 | -62.2174 | -62.2557 | 0.082776 | -62.368 | 59.4859 | 59.5996 | 59.6257 | -62.3399 | 0.056791 | -0.17155 | -0.013749 | 0.033193 | -0.023598 | -0.44986 | -0.41316 | -0.065737 | -0.33923 | 0.0185 | -0.093843 | -0.028106 | -0.22549 | -0.1994 | 121.9278 | 121.6494 | 121.6861 | 62.2756 | -122.0425 | 121.7601 | 121.8738 | 121.8999 | 62.3569 | -122.165
89.9062 | 122.2412 | -62.2742 | 59.8022 | 1.4211e-13 | -0.022895 | -0.0036602 | 0.066648 | -0.0047176 | 0.059873 | -0.013124 | 0.00078395 | -0.0016878 | -0.0027988 | 0.017354 | -0.0089584 | -62.2879 | 0.001407 | -62.241 | 59.6582 | 59.3844 | 59.412 | -62.2128 | -62.2602 | 0.082776 | -62.3634 | 59.4813 | 59.5996 | 59.6212 | -62.3491 | 0.06137 | -0.14409 | -0.013749 | 0.033193 | -0.028177 | -0.41781 | -0.39027 | -0.074895 | -0.32092 | 0.013921 | -0.089265 | -0.01437 | -0.20261 | -0.18109 | 121.9323 | 121.6586 | 121.6861 | 62.2756 | -122.015 | 121.7555 | 121.8738 | 121.8953 | 62.3569 | -122.1513
91.5938 | 122.3419 | -62.2513 | 59.7565 | 1.4211e-13 | -0.022468 | -0.0036602 | 0.066434 | -0.004504 | 0.059873 | -0.0054937 | 0.00035675 | -0.0014742 | -0.002585 | 0.017141 | -0.0085312 | -62.2879 | -0.003172 | -62.2364 | 59.6582 | 59.3844 | 59.4166 | -62.222 | -62.2557 | 0.082776 | -62.3589 | 59.4767 | 59.5996 | 59.612 | -62.3491 | 0.029324 | -0.098311 | -0.036637 | 0.014884 | -0.01444 | -0.37204 | -0.33992 | -0.097783 | -0.27972 | -0.004388 | -0.10757 | -0.009791 | -0.15683 | -0.14447 | 121.9094 | 121.6357 | 121.6678 | 62.2481 | -121.9784 | 121.728 | 121.8509 | 121.8633 | 62.3341 | -122.1055
93.3438 | 122.3373 | -62.2284 | 59.7565 | 1.4211e-13 | -0.023109 | -0.003233 | 0.066434 | -0.0047176 | 0.059873 | -0.0054937 | 0.00099775 | -0.0019016 | -0.0027988 | 0.017568 | -0.0087448 | -62.2879 | -0.003172 | -62.241 | 59.6536 | 59.3799 | 59.4166 | -62.2265 | -62.2557 | 0.078197 | -62.3589 | 59.4813 | 59.6088 | 59.6212 | -62.3445 | 0.001857 | -0.10289 | -0.059525 | -0.012583 | -0.01444 | -0.37662 | -0.33992 | -0.11609 | -0.27514 | -0.027276 | -0.13046 | -0.01437 | -0.14767 | -0.13531 | 121.882 | 121.6082 | 121.6449 | 62.2252 | -121.983 | 121.7097 | 121.8372 | 121.8495 | 62.3066 | -122.101
95.0781 | 122.2092 | -62.3154 | 59.7794 | 1.4211e-13 | -0.022895 | -0.0030192 | 0.066648 | -0.0047176 | 0.059659 | -0.0054937 | 0.00057035 | -0.0019016 | -0.0027988 | 0.017354 | -0.0087448 | -62.2879 | 0.001407 | -62.241 | 59.6582 | 59.389 | 59.412 | -62.222 | -62.2511 | 0.087354 | -62.3589 | 59.4859 | 59.6088 | 59.6257 | -62.3445 | 0.093411 | -0.1212 | 0.02745 | 0.074392 | -0.019019 | -0.39035 | -0.36738 | -0.029117 | -0.29345 | 0.064277 | -0.043487 | -0.01437 | -0.17056 | -0.15362 | 121.9735 | 121.7044 | 121.7273 | 62.3168 | -122.0013 | 121.8013 | 121.9242 | 121.9411 | 62.4027 | -122.1238
96.7656 | 122.2 | -62.2879 | 59.7931 | 1.4211e-13 | -0.022895 | -0.0030192 | 0.066007 | -0.0049314 | 0.059873 | 0.0021363 | 0.00057035 | -0.0016878 | -0.0027988 | 0.017141 | -0.0085312 | -62.2925 | -0.003172 | -62.241 | 59.6536 | 59.389 | 59.4166 | -62.222 | -62.2511 | 0.087354 | -62.3726 | 59.4767 | 59.6042 | 59.6303 | -62.3536 | 0.065945 | -0.13951 | -0.004595 | 0.046926 | -0.019019 | -0.40408 | -0.37654 | -0.065741 | -0.31634 | 0.036811 | -0.084689 | -0.018948 | -0.18887 | -0.16278 | 121.9415 | 121.6769 | 121.7045 | 62.2847 | -122.015 | 121.7647 | 121.8921 | 121.9182 | 62.3753 | -122.1467
98.5156 | 122.2824 | -62.2742 | 59.7702 | 1.4211e-13 | -0.023109 | -0.0034466 | 0.066648 | -0.004504 | 0.059445 | 0.0021363 | 0.00078395 | -0.0014742 | -0.0027988 | 0.017354 | -0.0085312 | -62.2833 | 0.005985 | -62.241 | 59.6582 | 59.3844 | 59.4257 | -62.2265 | -62.2557 | 0.091933 | -62.3543 | 59.4859 | 59.5996 | 59.6257 | -62.3491 | 0.047633 | -0.11204 | -0.009171 | 0.033193 | -0.01444 | -0.38577 | -0.34449 | -0.074895 | -0.2843 | 0.0185 | -0.080107 | -0.005212 | -0.17056 | -0.14447 | 121.9323 | 121.6586 | 121.6999 | 62.2802 | -121.9967 | 121.7601 | 121.8738 | 121.8999 | 62.3661 | -122.1193
100.2031 | 122.2549 | -62.2604 | 59.8206 | 1.4211e-13 | -0.022895 | -0.003233 | 0.06622 | -0.0047176 | 0.059873 | -0.0054937 | 0.00035675 | -0.0016878 | -0.0030124 | 0.017354 | -0.0089584 | -62.2879 | 0.005985 | -62.2456 | 59.6444 | 59.3844 | 59.4074 | -62.2174 | -62.2648 | 0.082776 | -62.3589 | 59.4859 | 59.5996 | 59.6257 | -62.3399 | 0.043058 | -0.17613 | -0.027482 | 0.014882 | -0.028176 | -0.43613 | -0.41316 | -0.07947 | -0.33465 | -0.004391 | -0.098419 | -0.018949 | -0.22092 | -0.19482 | 121.9049 | 121.6449 | 121.6678 | 62.2664 | -122.0379 | 121.7463 | 121.8601 | 121.8862 | 62.3432 | -122.1605
101.9531 | 122.2916 | -62.2925 | 59.7702 | 1.4211e-13 | -0.023322 | -0.003233 | 0.066861 | -0.0049314 | 0.059659 | -0.013124 | 0.00057035 | -0.0016878 | -0.0030124 | 0.017141 | -0.0083176 | -62.2788 | 0.005985 | -62.241 | 59.649 | 59.389 | 59.4257 | -62.222 | -62.2557 | 0.087354 | -62.3589 | 59.4859 | 59.6088 | 59.6166 | -62.3491 | 0.070522 | -0.1212 | 0.013717 | 0.051503 | -0.019019 | -0.38119 | -0.34449 | -0.056585 | -0.2843 | 0.03681 | -0.066376 | -0.009791 | -0.16141 | -0.15363 | 121.9415 | 121.6815 | 121.7182 | 62.2985 | -121.9922 | 121.7784 | 121.9013 | 121.9091 | 62.3798 | -122.1193
103.625 | 122.2275 | -62.2742 | 59.8343 | 1.4211e-13 | -0.023109 | -0.0034466 | 0.066648 | -0.0047176 | 0.059445 | -0.0054937 | 0.00035675 | -0.0019016 | -0.0027988 | 0.017354 | -0.0087448 | -62.2925 | -0.003172 | -62.241 | 59.649 | 59.3936 | 59.4028 | -62.2174 | -62.2511 | 0.082776 | -62.3589 | 59.4905 | 59.6042 | 59.6257 | -62.3353 | 0.056791 | -0.18529 | -0.018328 | 0.033193 | -0.023598 | -0.4407 | -0.43147 | -0.061159 | -0.34381 | 0.023078 | -0.084686 | -0.023527 | -0.23007 | -0.20856 | 121.9232 | 121.6678 | 121.677 | 62.271 | -122.0517 | 121.7647 | 121.8784 | 121.8999 | 62.3569 | -122.1696
105.3125 | 122.3328 | -62.2833 | 59.7336 | 1.4211e-13 | -0.023109 | -0.003233 | 0.066861 | -0.0042904 | 0.059873 | -0.0054937 | 0.00078395 | -0.0021152 | -0.0030124 | 0.017354 | -0.0089584 | -62.2788 | 0.001407 | -62.2364 | 59.6582 | 59.3982 | 59.412 | -62.2174 | -62.2236 | 0.087354 | -62.3634 | 59.4859 | 59.6042 | 59.6395 | -62.3399 | 0.065946 | -0.075423 | 0.004562 | 0.046927 | -0.019019 | -0.33541 | -0.32161 | -0.056582 | -0.24768 | 0.059706 | -0.08011 | -0.023528 | -0.12936 | -0.094112 | 121.9415 | 121.6815 | 121.6953 | 62.2847 | -121.951 | 121.7692 | 121.8875 | 121.9228 | 62.3707 | -122.0735
107.0625 | 122.2824 | -62.2604 | 59.7382 | 1.4211e-13 | -0.023109 | -0.003233 | 0.066434 | -0.0049314 | 0.060086 | -0.0054937 | 0.00057035 | -0.0016878 | -0.0030124 | 0.017782 | -0.0087448 | -62.2879 | -0.012329 | -62.2456 | 59.6536 | 59.3844 | 59.4166 | -62.222 | -62.2374 | 0.087354 | -62.3589 | 59.4859 | 59.5996 | 59.6074 | -62.3445 | 0.038479 | -0.084578 | -0.027482 | 0.014882 | -0.023597 | -0.35373 | -0.32161 | -0.084049 | -0.25225 | 0.023082 | -0.098419 | -0.01437 | -0.13852 | -0.13074 | 121.914 | 121.6449 | 121.677 | 62.2481 | -121.9601 | 121.7463 | 121.8601 | 121.8679 | 62.3478 | -122.0826
108.8125 | 122.3694 | -62.2467 | 59.7427 | 1.4211e-13 | -0.023109 | -0.0034466 | 0.066648 | -0.0042904 | 0.059659 | -0.0054937 | 0.00035675 | -0.0019016 | -0.0027988 | 0.017354 | -0.0089584 | -62.2879 | -0.003172 | -62.241 | 59.6536 | 59.3753 | 59.4211 | -62.2174 | -62.2374 | 0.091933 | -62.3589 | 59.4813 | 59.5996 | 59.6212 | -62.3445 | 0.029325 | -0.089156 | -0.041215 | 0.005727 | -0.023598 | -0.36746 | -0.3216 | -0.097782 | -0.26141 | 0.009349 | -0.11215 | -0.01437 | -0.1431 | -0.12158 | 121.9003 | 121.622 | 121.6678 | 62.2435 | -121.9601 | 121.728 | 121.8463 | 121.8679 | 62.3386 | -122.0872
110.5156 | 122.3053 | -62.2742 | 59.7473 | 1.4211e-13 | -0.023109 | -0.0036602 | 0.066434 | -0.0049314 | 0.059873 | 0.0097668 | 0.00035675 | -0.0021152 | -0.0030124 | 0.017354 | -0.0087448 | -62.2925 | -0.007751 | -62.241 | 59.6536 | 59.389 | 59.4211 | -62.2265 | -62.2328 | 0.082776 | -62.3589 | 59.4859 | 59.6042 | 59.6028 | -62.3399 | 0.047633 | -0.093733 | -0.018328 | 0.033193 | -0.01444 | -0.3583 | -0.32618 | -0.065737 | -0.26141 | 0.041393 | -0.084686 | -0.018949 | -0.1431 | -0.14447 | 121.9278 | 121.6632 | 121.6953 | 62.2664 | -121.9739 | 121.7601 | 121.8784 | 121.877 | 62.3569 | -122.0872
112.2031 | 122.3373 | -62.2833 | 59.697 | 1.4211e-13 | -0.023322 | -0.0036602 | 0.066648 | -0.004504 | 0.059873 | -0.0054937 | 0.00078395 | -0.0019016 | -0.0027988 | 0.017354 | -0.0089584 | -62.2833 | 0.005985 | -62.241 | 59.6582 | 59.389 | 59.4211 | -62.222 | -62.2328 | 0.073618 | -62.3543 | 59.4767 | 59.6088 | 59.6166 | -62.3491 | 0.061367 | -0.038801 | -1.6e-05 | 0.042348 | -0.019019 | -0.30795 | -0.27583 | -0.06574 | -0.22021 | 0.050548 | -0.070952 | -0.005212 | -0.088163 | -0.080383 | 121.9415 | 121.6723 | 121.7045 | 62.2893 | -121.9189 | 121.7601 | 121.8921 | 121.8999 | 62.3569 | -122.046
113.9375 | 122.3053 | -62.2971 | 59.7473 | 1.4211e-13 | -0.023109 | -0.0036602 | 0.066434 | -0.0047176 | 0.059659 | 0.0021363 | 0.00057035 | -0.0019016 | -0.0027988 | 0.017568 | -0.0089584 | -62.2925 | -0.003172 | -62.2364 | 59.6536 | 59.3844 | 59.4211 | -62.222 | -62.2282 | 0.087354 | -62.3589 | 59.4813 | 59.6042 | 59.6212 | -62.3445 | 0.0751 | -0.093733 | 0.00456 | 0.06066 | -0.01444 | -0.36288 | -0.32618 | -0.047428 | -0.26599 | 0.06886 | -0.061798 | -0.01437 | -0.1431 | -0.12616 | 121.9506 | 121.6815 | 121.7182 | 62.2939 | -121.9693 | 121.7784 | 121.9013 | 121.9182 | 62.3844 | -122.0918
115.6719 | 122.2824 | -62.2742 | 59.7702 | 1.4211e-13 | -0.023536 | -0.003233 | 0.06622 | -0.004504 | 0.059659 | 0.0021363 | 0.00014315 | -0.0021152 | -0.0030124 | 0.017354 | -0.0089584 | -62.2925 | -0.007751 | -62.241 | 59.6582 | 59.3844 | 59.4166 | -62.222 | -62.2282 | 0.082776 | -62.3634 | 59.4859 | 59.5996 | 59.6212 | -62.3445 | 0.052212 | -0.11204 | -0.018328 | 0.033193 | -0.019019 | -0.38577 | -0.35365 | -0.070316 | -0.2843 | 0.045972 | -0.089265 | -0.018949 | -0.17056 | -0.14905 | 121.9323 | 121.6586 | 121.6907 | 62.2664 | -121.9922 | 121.7601 | 121.8738 | 121.8953 | 62.3569 | -122.1147
117.3594 | 122.2412 | -62.2971 | 59.7656 | 1.4211e-13 | -0.023322 | -0.0036602 | 0.066434 | -0.0049314 | 0.059659 | -0.0054937 | 0.00057035 | -0.0016878 | -0.0030124 | 0.017568 | -0.0087448 | -62.2879 | 0.001407 | -62.241 | 59.6627 | 59.3982 | 59.4211 | -62.2265 | -62.2328 | 0.082776 | -62.3543 | 59.4767 | 59.5951 | 59.6257 | -62.3582 | 0.070521 | -0.10289 | 0.009139 | 0.056081 | -0.01444 | -0.36746 | -0.34449 | -0.061165 | -0.28888 | 0.064281 | -0.057219 | 0.003946 | -0.17056 | -0.13989 | 121.9598 | 121.6952 | 121.7182 | 62.2985 | -121.9922 | 121.7738 | 121.8921 | 121.9228 | 62.3798 | -122.1238
119.1094 | 122.2458 | -62.2742 | 59.7977 | 1.4211e-13 | -0.02375 | -0.0034466 | 0.066648 | -0.004504 | 0.059232 | -0.0054937 | 0.00078395 | -0.0019016 | -0.002585 | 0.017568 | -0.0085312 | -62.2833 | -0.007751 | -62.2456 | 59.6536 | 59.389 | 59.4211 | -62.2174 | -62.2282 | 0.082776 | -62.3589 | 59.4767 | 59.6042 | 59.6257 | -62.3445 | 0.056791 | -0.14409 | -0.009171 | 0.028615 | -0.028176 | -0.40866 | -0.37654 | -0.070316 | -0.32092 | 0.045972 | -0.084686 | -0.01437 | -0.19345 | -0.17193 | 121.9278 | 121.6632 | 121.6953 | 62.2664 | -122.015 | 121.7509 | 121.8784 | 121.8999 | 62.3569 | -122.1422
120.7969 | 122.2641 | -62.2467 | 59.8297 | 1.4211e-13 | -0.023536 | -0.0034466 | 0.066434 | -0.0047176 | 0.059873 | -0.0054937 | 0.00057035 | -0.0012606 | -0.002585 | 0.017782 | -0.0087448 | -62.2879 | -0.003172 | -62.2456 | 59.6582 | 59.3844 | 59.4211 | -62.222 | -62.2328 | 0.087354 | -62.3726 | 59.4859 | 59.6042 | 59.6074 | -62.3445 | 0.024746 | -0.17155 | -0.041215 | 0.001149 | -0.023597 | -0.44528 | -0.40858 | -0.097782 | -0.34381 | 0.013927 | -0.12589 | -0.028106 | -0.22549 | -0.22229 | 121.9049 | 121.6311 | 121.6678 | 62.2435 | -122.0517 | 121.7326 | 121.8509 | 121.8541 | 62.3341 | -122.1742
122.7031 | 122.2504 | -62.2467 | 59.8251 | 1.4211e-13 | -0.023109 | -0.0034466 | 0.066434 | -0.0049314 | 0.059659 | -0.0054937 | 0.00057035 | -0.0014742 | -0.0027988 | 0.017568 | -0.0085312 | -62.2833 | -0.007751 | -62.2456 | 59.6582 | 59.3844 | 59.4166 | -62.222 | -62.2236 | 0.082776 | -62.3589 | 59.4813 | 59.6042 | 59.6257 | -62.3399 | 0.024746 | -0.16698 | -0.036637 | 0.001149 | -0.023597 | -0.4407 | -0.40858 | -0.093203 | -0.34381 | 0.023085 | -0.11215 | -0.018949 | -0.22092 | -0.1994 | 121.9049 | 121.6311 | 121.6633 | 62.239 | -122.0471 | 121.728 | 121.8509 | 121.8724 | 62.3295 | -122.165
124.4688 | 122.2504 | -62.2833 | 59.7931 | 1.4211e-13 | -0.023109 | -0.0036602 | 0.06622 | -0.0049314 | 0.059232 | -0.0054937 | 0.00035675 | -0.0016878 | -0.003226 | 0.017568 | -0.0089584 | -62.2925 | -0.003172 | -62.2456 | 59.6582 | 59.389 | 59.4211 | -62.222 | -62.2328 | 0.091933 | -62.368 | 59.4905 | 59.6042 | 59.6212 | -62.3491 | 0.061367 | -0.13493 | -0.009173 | 0.03777 | -0.023597 | -0.40408 | -0.37196 | -0.06574 | -0.30261 | 0.050548 | -0.084688 | -0.018948 | -0.18887 | -0.17194 | 121.9415 | 121.6723 | 121.7045 | 62.2802 | -122.015 | 121.7738 | 121.8875 | 121.9045 | 62.3753 | -122.1422
126.1562 | 122.2961 | -62.2971 | 59.7656 | 1.4211e-13 | -0.02375 | -0.0036602 | 0.066434 | -0.0047176 | 0.059659 | -0.0054937 | 0.00057035 | -0.0019016 | -0.002585 | 0.017782 | -0.0089584 | -62.2925 | -0.007751 | -62.2456 | 59.6582 | 59.3844 | 59.412 | -62.2265 | -62.2374 | 0.087354 | -62.3497 | 59.4767 | 59.5996 | 59.612 | -62.3445 | 0.070521 | -0.10747 | 0.00456 | 0.051503 | -0.019018 | -0.38119 | -0.35365 | -0.047428 | -0.28888 | 0.059703 | -0.052641 | -0.005213 | -0.16598 | -0.15363 | 121.9552 | 121.6815 | 121.709 | 62.2893 | -121.9922 | 121.7738 | 121.8967 | 121.9091 | 62.3844 | -122.1101
127.8906 | 122.3282 | -62.2467 | 59.7702 | 1.4211e-13 | -0.023322 | -0.003233 | 0.066434 | -0.0047176 | 0.059445 | -0.0054937 | 0.00014315 | -0.0019016 | -0.002585 | 0.017354 | -0.0085312 | -62.2879 | -0.003172 | -62.241 | 59.6627 | 59.389 | 59.4166 | -62.222 | -62.2236 | 0.082776 | -62.3634 | 59.4859 | 59.6088 | 59.6028 | -62.3536 | 0.024746 | -0.10747 | -0.041215 | 0.005727 | -0.019019 | -0.38119 | -0.35365 | -0.10694 | -0.2843 | 0.023085 | -0.11673 | -0.009791 | -0.16141 | -0.16736 | 121.9094 | 121.6357 | 121.6633 | 62.2435 | -121.9922 | 121.7326 | 121.8555 | 121.8495 | 62.3295 | -122.1238
129.625 | 122.2183 | -62.2238 | 59.8068 | 1.4211e-13 | -0.023536 | -0.0034466 | 0.066648 | -0.0047176 | 0.059873 | -0.0054937 | 0.00057035 | -0.0019016 | -0.0027988 | 0.017782 | -0.0085312 | -62.2925 | -0.007751 | -62.241 | 59.6536 | 59.3844 | 59.4211 | -62.222 | -62.2236 | 0.087354 | -62.368 | 59.4767 | 59.6042 | 59.6257 | -62.3491 | 0.001858 | -0.15324 | -0.068682 | -0.017161 | -0.019019 | -0.42239 | -0.38569 | -0.12525 | -0.33008 | 0.000197 | -0.1442 | -0.018948 | -0.20261 | -0.18109 | 121.8774 | 121.6082 | 121.6449 | 62.2161 | -122.0288 | 121.7006 | 121.828 | 121.8495 | 62.3112 | -122.1559
131.3125 | 122.3328 | -62.2971 | 59.7336 | 1.4211e-13 | -0.02375 | -0.0034466 | 0.066434 | -0.0049314 | 0.059445 | -0.013124 | 0.00057035 | -0.0019016 | -0.0023714 | 0.017782 | -0.0087448 | -62.2879 | 0.001407 | -62.241 | 59.6582 | 59.389 | 59.4166 | -62.2265 | -62.2328 | 0.087354 | -62.3589 | 59.4859 | 59.6042 | 59.6257 | -62.3491 | 0.070521 | -0.075423 | 0.009139 | 0.056081 | -0.01444 | -0.34457 | -0.31703 | -0.052007 | -0.24768 | 0.064281 | -0.061798 | -0.009791 | -0.12936 | -0.10785 | 121.9552 | 121.6861 | 121.7136 | 62.2985 | -121.9601 | 121.783 | 121.9013 | 121.9228 | 62.3844 | -122.0826
133.0625 | 122.3145 | -62.2971 | 59.7427 | 1.4211e-13 | -0.023536 | -0.0034466 | 0.06622 | -0.0047176 | 0.059873 | -0.0054937 | 0.00078395 | -0.0016878 | -0.003226 | 0.017354 | -0.0085312 | -62.2833 | -0.003172 | -62.2456 | 59.6582 | 59.389 | 59.4211 | -62.2311 | -62.2328 | 0.087354 | -62.3589 | 59.4859 | 59.6088 | 59.6028 | -62.3399 | 0.065942 | -0.084578 | 0.013717 | 0.051503 | -0.014439 | -0.35373 | -0.3216 | -0.042849 | -0.25683 | 0.064281 | -0.061798 | -0.018949 | -0.13394 | -0.1399 | 121.9552 | 121.6861 | 121.7182 | 62.2939 | -121.9739 | 121.783 | 121.9059 | 121.8999 | 62.3844 | -122.0826
134.75 | 122.3557 | -62.2467 | 59.7427 | 1.4211e-13 | -0.023322 | -0.0034466 | 0.06622 | -0.0047176 | 0.059873 | -0.013124 | 0.00078395 | -0.0019016 | -0.0027988 | 0.017568 | -0.0089584 | -62.2742 | 0.001407 | -62.2364 | 59.6536 | 59.3844 | 59.4166 | -62.2311 | -62.2236 | 0.082776 | -62.3634 | 59.4813 | 59.6042 | 59.6349 | -62.3399 | 0.015588 | -0.089156 | -0.02748 | 0.010306 | -0.005282 | -0.35831 | -0.32618 | -0.093203 | -0.26141 | 0.023085 | -0.11673 | -0.023528 | -0.13852 | -0.10785 | 121.9003 | 121.6311 | 121.6633 | 62.2481 | -121.9739 | 121.728 | 121.8509 | 121.8816 | 62.3295 | -122.0826
136.5 | 122.2549 | -62.2925 | 59.8251 | 1.4211e-13 | -0.02375 | -0.003874 | 0.066434 | -0.0047176 | 0.059445 | -0.0054937 | 0.00057035 | -0.0014742 | -0.0030124 | 0.017996 | -0.0087448 | -62.2879 | 0.005985 | -62.2364 | 59.6536 | 59.3844 | 59.4166 | -62.2174 | -62.2328 | 0.078197 | -62.3589 | 59.4859 | 59.6042 | 59.6028 | -62.3445 | 0.075101 | -0.17155 | 0.004561 | 0.056082 | -0.019019 | -0.4407 | -0.40858 | -0.052006 | -0.33923 | 0.059703 | -0.066376 | -0.01437 | -0.22092 | -0.22229 | 121.9461 | 121.6769 | 121.709 | 62.2985 | -122.0425 | 121.7784 | 121.8967 | 121.8953 | 62.3707 | -122.1696
138.1875 | 122.3602 | -62.2559 | 59.7565 | 1.4211e-13 | -0.023963 | -0.0036602 | 0.06622 | -0.0047176 | 0.059445 | -0.013124 | 0.00078395 | -0.0019016 | -0.0027988 | 0.017568 | -0.0087448 | -62.2833 | 0.001407 | -62.2272 | 59.6582 | 59.3799 | 59.4166 | -62.222 | -62.2236 | 0.082776 | -62.3634 | 59.4813 | 59.6042 | 59.6303 | -62.3491 | 0.033901 | -0.098311 | -0.027482 | 0.028617 | -0.005284 | -0.37662 | -0.33992 | -0.093206 | -0.27514 | 0.03224 | -0.10758 | -0.01437 | -0.15225 | -0.12616 | 121.914 | 121.6357 | 121.6724 | 62.2573 | -121.9784 | 121.7372 | 121.8601 | 121.8862 | 62.3386 | -122.1055
139.9219 | 122.3557 | -62.2375 | 59.7885 | 1.4211e-13 | -0.023963 | -0.003233 | 0.06622 | -0.004504 | 0.059445 | -0.0054937 | 0.00035675 | -0.0016878 | -0.0027988 | 0.017568 | -0.0087448 | -62.2833 | 0.001407 | -62.2364 | 59.6673 | 59.3753 | 59.4211 | -62.2265 | -62.2328 | 0.082776 | -62.3634 | 59.4859 | 59.6134 | 59.6303 | -62.3491 | 0.011012 | -0.1212 | -0.045792 | 0.001151 | -0.009861 | -0.41324 | -0.36738 | -0.11152 | -0.30261 | 0.004772 | -0.12589 | -0.01437 | -0.17514 | -0.1582 | 121.9049 | 121.6128 | 121.6587 | 62.239 | -122.0151 | 121.7235 | 121.8509 | 121.8679 | 62.3203 | -122.1376
141.6562 | 122.2504 | -62.2559 | 59.8251 | 1.4211e-13 | -0.023536 | -0.003233 | 0.066648 | -0.0049314 | 0.059445 | 0.0021363 | 0.00078395 | -0.0019016 | -0.0023714 | 0.017568 | -0.0089584 | -62.2833 | -0.003172 | -62.2272 | 59.6582 | 59.389 | 59.4211 | -62.2174 | -62.2282 | 0.087354 | -62.3589 | 59.4813 | 59.6088 | 59.612 | -62.3491 | 0.03848 | -0.16698 | -0.027482 | 0.028617 | -0.009863 | -0.43612 | -0.404 | -0.093206 | -0.34381 | 0.027661 | -0.103 | -0.009791 | -0.21634 | -0.21314 | 121.914 | 121.6449 | 121.677 | 62.2527 | -122.0425 | 121.7372 | 121.8647 | 121.8679 | 62.3432 | -122.1742
143.3438 | 122.2229 | -62.3154 | 59.7519 | 1.4211e-13 | -0.023536 | -0.0034466 | 0.06622 | -0.004504 | 0.059232 | 0.0021363 | 0.00078395 | -0.0016878 | -0.0023714 | 0.017568 | -0.0087448 | -62.2833 | 0.001407 | -62.2364 | 59.6627 | 59.3936 | 59.4211 | -62.222 | -62.2374 | 0.091933 | -62.3589 | 59.4767 | 59.6042 | 59.5937 | -62.3536 | 0.093411 | -0.089154 | 0.032028 | 0.078971 | -0.01444 | -0.3583 | -0.33076 | -0.038275 | -0.27514 | 0.078014 | -0.043487 | -0.005212 | -0.14767 | -0.15821 | 121.9781 | 121.709 | 121.7365 | 62.3168 | -121.9738 | 121.7921 | 121.9196 | 121.9091 | 62.4073 | -122.1055
145.1094 | 122.2504 | -62.2925 | 59.7931 | 1.4211e-13 | -0.023963 | -0.0036602 | 0.066434 | -0.0049314 | 0.059018 | -0.013124 | 0.00057035 | -0.0019016 | -0.0023714 | 0.017568 | -0.0087448 | -62.2879 | -0.003172 | -62.2318 | 59.6627 | 59.3936 | 59.4257 | -62.2174 | -62.2282 | 0.087354 | -62.368 | 59.4722 | 59.5996 | 59.6303 | -62.3536 | 0.075101 | -0.13035 | 0.004561 | 0.06066 | -0.014441 | -0.3995 | -0.36738 | -0.061164 | -0.32092 | 0.064282 | -0.075533 | -0.014369 | -0.19345 | -0.16278 | 121.9552 | 121.6861 | 121.7182 | 62.2893 | -122.0105 | 121.7646 | 121.8921 | 121.9228 | 62.3798 | -122.1467
146.7969 | 122.2321 | -62.2604 | 59.8206 | 1.4211e-13 | -0.02375 | -0.0036602 | 0.066648 | -0.0049314 | 0.059232 | -0.0054937 | 0.00057035 | -0.0016878 | -0.0027988 | 0.017568 | -0.0085312 | -62.2879 | 0.001407 | -62.2272 | 59.6536 | 59.389 | 59.4257 | -62.2174 | -62.2282 | 0.082776 | -62.368 | 59.4859 | 59.5996 | 59.6212 | -62.3445 | 0.043058 | -0.16698 | -0.027482 | 0.033195 | -0.009863 | -0.43155 | -0.39485 | -0.084049 | -0.33465 | 0.032239 | -0.10758 | -0.023527 | -0.22092 | -0.1994 | 121.914 | 121.6494 | 121.6861 | 62.2618 | -122.0379 | 121.7463 | 121.8601 | 121.8816 | 62.3432 | -122.165
148.5312 | 122.3602 | -62.2742 | 59.7931 | 1.4211e-13 | -0.02375 | -0.0036602 | 0.066648 | -0.0049314 | 0.059445 | 0.0021363 | 0.00057035 | -0.0019016 | -0.0030124 | 0.017782 | -0.0089584 | -62.2833 | 0.001407 | -62.2318 | 59.6627 | 59.389 | 59.4211 | -62.222 | -62.2328 | 0.087354 | -62.3589 | 59.4767 | 59.6042 | 59.612 | -62.3445 | 0.052212 | -0.13035 | -0.009171 | 0.04235 | -0.009862 | -0.40408 | -0.37196 | -0.070316 | -0.31634 | 0.041393 | -0.084686 | -0.01437 | -0.18887 | -0.18109 | 121.9369 | 121.6632 | 121.6953 | 62.2756 | -122.015 | 121.7509 | 121.8784 | 121.8862 | 62.3615 | -122.1376
150.2188 | 122.2458 | -62.2833 | 59.7839 | 1.4211e-13 | -0.023963 | -0.003874 | 0.066434 | -0.0049314 | 0.059659 | -0.0054937 | 0.00035675 | -0.0019016 | -0.002585 | 0.017996 | -0.0089584 | -62.2879 | 0.001407 | -62.2318 | 59.6582 | 59.389 | 59.4166 | -62.2265 | -62.2374 | 0.082776 | -62.3589 | 59.4767 | 59.6042 | 59.6257 | -62.3491 | 0.056788 | -0.12578 | -0.004594 | 0.051505 | -0.005283 | -0.39493 | -0.36738 | -0.06574 | -0.30719 | 0.04597 | -0.075531 | -0.009791 | -0.17972 | -0.1582 | 121.9415 | 121.6723 | 121.6999 | 62.2847 | -122.0105 | 121.7601 | 121.8875 | 121.9091 | 62.3661 | -122.133
151.9531 | 122.3465 | -62.2833 | 59.7153 | 1.4211e-13 | -0.023536 | -0.0034466 | 0.066434 | -0.0049314 | 0.059659 | 0.0021363 | 0.00057035 | -0.0016878 | -0.003226 | 0.018209 | -0.0085312 | -62.2879 | 0.005985 | -62.2318 | 59.6582 | 59.3982 | 59.4257 | -62.222 | -62.2236 | 0.087354 | -62.3634 | 59.4813 | 59.6042 | 59.6303 | -62.3491 | 0.061367 | -0.057112 | -0.004594 | 0.051505 | -0.009862 | -0.3171 | -0.28956 | -0.06574 | -0.23394 | 0.059706 | -0.08011 | -0.01437 | -0.11105 | -0.084958 | 121.9415 | 121.6815 | 121.709 | 62.2893 | -121.9372 | 121.7647 | 121.8875 | 121.9136 | 62.3707 | -122.0643
153.6875 | 122.3007 | -62.2833 | 59.761 | 1.4211e-13 | -0.024177 | -0.0036602 | 0.066648 | -0.004504 | 0.059659 | 0.0097668 | 0.00035675 | -0.0019016 | -0.0027988 | 0.017782 | -0.0089584 | -62.2833 | 0.005985 | -62.2318 | 59.6582 | 59.389 | 59.4303 | -62.222 | -62.2328 | 0.082776 | -62.3589 | 59.4813 | 59.6042 | 59.612 | -62.3491 | 0.061367 | -0.10289 | -1.6e-05 | 0.051505 | -0.009862 | -0.37204 | -0.33076 | -0.06574 | -0.27972 | 0.050548 | -0.075531 | -0.009791 | -0.15683 | -0.14905 | 121.9415 | 121.6723 | 121.7136 | 62.2893 | -121.983 | 121.7647 | 121.8875 | 121.8953 | 62.3661 | -122.1101
155.375 | 122.2321 | -62.2742 | 59.8343 | 1.4211e-13 | -0.02375 | -0.003874 | 0.066648 | -0.0047176 | 0.059445 | -0.020755 | 0.00078395 | -0.0019016 | -0.002585 | 0.017782 | -0.0085312 | -62.2879 | 0.001407 | -62.2272 | 59.6582 | 59.389 | 59.4257 | -62.222 | -62.2282 | 0.082776 | -62.3589 | 59.4813 | 59.6042 | 59.5937 | -62.3536 | 0.052212 | -0.17613 | -0.013749 | 0.046928 | -0.005284 | -0.44528 | -0.40858 | -0.079474 | -0.35296 | 0.045972 | -0.084686 | -0.005212 | -0.23007 | -0.24061 | 121.9323 | 121.6632 | 121.6999 | 62.2756 | -122.0562 | 121.7555 | 121.8784 | 121.8679 | 62.3569 | -122.1879
157.125 | 122.3373 | -62.265 | 59.7382 | 1.4211e-13 | -0.02375 | -0.003233 | 0.066434 | -0.0049314 | 0.059445 | -0.0054937 | 0.00057035 | -0.0021152 | -0.002585 | 0.017568 | -0.0087448 | -62.2879 | -0.003172 | -62.2318 | 59.6582 | 59.3844 | 59.4303 | -62.2265 | -62.2282 | 0.087354 | -62.3589 | 59.4859 | 59.6088 | 59.6349 | -62.3582 | 0.038478 | -0.08 | -0.022904 | 0.033195 | -0.005283 | -0.35373 | -0.30787 | -0.093208 | -0.25225 | 0.036817 | -0.093841 | -0.000633 | -0.12936 | -0.10327 | 121.9232 | 121.6494 | 121.6953 | 62.2618 | -121.9647 | 121.7509 | 121.8738 | 121.8999 | 62.3524 | -122.0964
158.7969 | 122.2183 | -62.2833 | 59.8206 | 1.4211e-13 | -0.023963 | -0.0034466 | 0.066007 | -0.004504 | 0.059232 | -0.0054937 | 0.00057035 | -0.0019016 | -0.0027988 | 0.018209 | -0.0089584 | -62.2833 | 0.005985 | -62.2318 | 59.6536 | 59.3844 | 59.4303 | -62.2265 | -62.2282 | 0.087354 | -62.3634 | 59.4722 | 59.6042 | 59.6349 | -62.3536 | 0.056788 | -0.16698 | -1.6e-05 | 0.051505 | -0.005283 | -0.43613 | -0.39027 | -0.070319 | -0.34839 | 0.055127 | -0.08011 | -0.009791 | -0.21634 | -0.18567 | 121.9369 | 121.6678 | 121.7136 | 62.2893 | -122.0471 | 121.7555 | 121.8875 | 121.9182 | 62.3707 | -122.1742
160.5469 | 122.2916 | -62.2833 | 59.7565 | 1.4211e-13 | -0.02375 | -0.0034466 | 0.066434 | -0.005145 | 0.059873 | 0.0021363 | 0.00035675 | -0.0016878 | -0.0027988 | 0.017568 | -0.0087448 | -62.2879 | 0.001407 | -62.2364 | 59.6627 | 59.3936 | 59.4257 | -62.2311 | -62.2328 | 0.087354 | -62.3589 | 59.4905 | 59.6088 | 59.6395 | -62.3536 | 0.052209 | -0.093732 | -0.004594 | 0.046927 | -0.005282 | -0.36288 | -0.33076 | -0.070319 | -0.26599 | 0.050548 | -0.075531 | -0.005212 | -0.14767 | -0.117 | 121.9461 | 121.6769 | 121.709 | 62.2847 | -121.9876 | 121.7738 | 121.8921 | 121.9228 | 62.3707 | -122.1101
162.2969 | 122.2549 | -62.2467 | 59.8297 | 1.4211e-13 | -0.023963 | -0.0036602 | 0.066648 | -0.005145 | 0.059659 | 0.0097668 | 0.00078395 | -0.0014742 | -0.0027988 | 0.017782 | -0.0087448 | -62.2833 | -0.003172 | -62.2318 | 59.6582 | 59.389 | 59.4257 | -62.222 | -62.2328 | 0.091933 | -62.368 | 59.4859 | 59.6042 | 59.6349 | -62.3445 | 0.024746 | -0.17155 | -0.036637 | 0.014884 | -0.009862 | -0.4407 | -0.404 | -0.097782 | -0.34381 | 0.013927 | -0.12131 | -0.023527 | -0.22549 | -0.19482 | 121.9049 | 121.6357 | 121.6724 | 62.2435 | -122.0517 | 121.7326 | 121.8509 | 121.8816 | 62.3386 | -122.1742
164.0312 | 122.2595 | -62.2879 | 59.8206 | 1.4211e-13 | -0.024177 | -0.0036602 | 0.066434 | -0.0047176 | 0.059659 | 0.0097668 | 0.00014315 | -0.0016878 | -0.0030124 | 0.017782 | -0.0085312 | -62.2925 | 0.005985 | -62.2318 | 59.6536 | 59.3982 | 59.4211 | -62.2174 | -62.2328 | 0.087354 | -62.3634 | 59.4813 | 59.6042 | 59.6349 | -62.3536 | 0.070524 | -0.16698 | -0.004595 | 0.056083 | -0.014441 | -0.42239 | -0.39942 | -0.065741 | -0.33923 | 0.055126 | -0.075532 | -0.009791 | -0.21634 | -0.18567 | 121.9415 | 121.6861 | 121.709 | 62.2939 | -122.0379 | 121.7692 | 121.8921 | 121.9228 | 62.3753 | -122.1742
165.7031 | 122.2961 | -62.3016 | 59.7565 | 1.4211e-13 | -0.02375 | -0.0036602 | 0.066434 | -0.0049314 | 0.059232 | 0.0021363 | 0.00035675 | -0.0021152 | -0.0030124 | 0.018209 | -0.0087448 | -62.2925 | 0.005985 | -62.2272 | 59.6582 | 59.3936 | 59.4257 | -62.2265 | -62.2328 | 0.082776 | -62.3634 | 59.4859 | 59.6134 | 59.6349 | -62.3536 | 0.075099 | -0.098311 | 0.009138 | 0.074394 | -0.000705 | -0.36288 | -0.33076 | -0.052008 | -0.27056 | 0.068859 | -0.061799 | -0.009791 | -0.1431 | -0.12158 | 121.9598 | 121.6952 | 121.7273 | 62.3076 | -121.983 | 121.7875 | 121.915 | 121.9365 | 62.3844 | -122.1101
167.4531 | 122.3145 | -62.2421 | 59.7931 | 1.4211e-13 | -0.024177 | -0.0036602 | 0.066007 | -0.0049314 | 0.059445 | -0.0054937 | 0.00057035 | -0.0021152 | -0.002585 | 0.017782 | -0.0085312 | -62.2925 | -0.003172 | -62.241 | 59.6627 | 59.389 | 59.4211 | -62.222 | -62.2328 | 0.078197 | -62.3634 | 59.4813 | 59.6088 | 59.6257 | -62.3536 | 0.020168 | -0.13035 | -0.050372 | 0.001149 | -0.019019 | -0.40408 | -0.37196 | -0.11152 | -0.31176 | 0.009349 | -0.12131 | -0.009791 | -0.18429 | -0.16736 | 121.9049 | 121.6311 | 121.6633 | 62.239 | -122.015 | 121.7235 | 121.8509 | 121.8679 | 62.3203 | -122.1467
169.2031 | 122.2046 | -62.2696 | 59.8297 | 1.4211e-13 | -0.02375 | -0.003874 | 0.066434 | -0.0049314 | 0.059018 | -0.0054937 | 0.00078395 | -0.0016878 | -0.002585 | 0.017996 | -0.0089584 | -62.2879 | 0.001407 | -62.241 | 59.6536 | 59.3936 | 59.4257 | -62.2174 | -62.2282 | 0.078197 | -62.3726 | 59.4859 | 59.6088 | 59.644 | -62.3445 | 0.052213 | -0.17613 | -0.018327 | 0.028615 | -0.023598 | -0.43612 | -0.404 | -0.074894 | -0.34381 | 0.041394 | -0.103 | -0.028106 | -0.22091 | -0.18566 | 121.9232 | 121.6632 | 121.6953 | 62.271 | -122.0471 | 121.7555 | 121.8784 | 121.9136 | 62.3478 | -122.1742
170.8906 | 122.3099 | -62.265 | 59.7931 | 1.4211e-13 | -0.024177 | -0.003874 | 0.066648 | -0.0049314 | 0.059232 | -0.0054937 | 0.00057035 | -0.0021152 | -0.0027988 | 0.017996 | -0.0087448 | -62.2925 | 0.005985 | -62.241 | 59.6582 | 59.3982 | 59.4303 | -62.2265 | -62.2282 | 0.082776 | -62.3634 | 59.4767 | 59.6134 | 59.6349 | -62.3491 | 0.038478 | -0.13493 | -0.027483 | 0.024038 | -0.01444 | -0.39492 | -0.3628 | -0.08405 | -0.31634 | 0.036817 | -0.09842 | -0.01437 | -0.17972 | -0.1582 | 121.9232 | 121.6632 | 121.6953 | 62.271 | -122.0196 | 121.7418 | 121.8784 | 121.8999 | 62.3478 | -122.1422
172.6406 | 122.2824 | -62.2787 | 59.761 | 1.4211e-13 | -0.024177 | -0.003874 | 0.066434 | -0.004504 | 0.059445 | -0.0054937 | 0.00057035 | -0.0019016 | -0.002585 | 0.017782 | -0.0089584 | -62.2833 | 0.005985 | -62.2364 | 59.6582 | 59.3982 | 59.4257 | -62.2265 | -62.2282 | 0.087354 | -62.368 | 59.4859 | 59.6134 | 59.5891 | -62.3536 | 0.052211 | -0.10289 | -0.004593 | 0.04235 | -0.009861 | -0.36288 | -0.33534 | -0.074896 | -0.27514 | 0.05055 | -0.089265 | -0.014369 | -0.14767 | -0.17194 | 121.9369 | 121.6769 | 121.7045 | 62.2847 | -121.9876 | 121.7647 | 121.8921 | 121.8679 | 62.3661 | -122.1147
174.375 | 122.3511 | -62.2513 | 59.7565 | 1.4211e-13 | -0.024177 | -0.0034466 | 0.066434 | -0.005145 | 0.059232 | -0.0054937 | 0.00078395 | -0.0012606 | -0.0030124 | 0.017996 | -0.0087448 | -62.2833 | 0.005985 | -62.241 | 59.6627 | 59.389 | 59.4257 | -62.222 | -62.2328 | 0.087354 | -62.3589 | 59.4859 | 59.6088 | 59.6303 | -62.3491 | 0.029324 | -0.093732 | -0.032059 | 0.010305 | -0.019019 | -0.36746 | -0.33076 | -0.097783 | -0.27056 | 0.018505 | -0.10757 | -0.009791 | -0.14767 | -0.12616 | 121.914 | 121.6403 | 121.677 | 62.2573 | -121.9784 | 121.7372 | 121.8601 | 121.8816 | 62.3386 | -122.1055
176.1094 | 122.3236 | -62.2421 | 59.7702 | 1.4211e-13 | -0.023963 | -0.0036602 | 0.06622 | -0.0049314 | 0.059018 | 0.0097668 | 0.00035675 | -0.0016878 | -0.0030124 | 0.017996 | -0.0087448 | -62.2833 | 0.005985 | -62.2364 | 59.6582 | 59.3982 | 59.4257 | -62.2265 | -62.2374 | 0.082776 | -62.3634 | 59.4813 | 59.6088 | 59.6349 | -62.3491 | 0.015589 | -0.11204 | -0.041215 | 0.005728 | -0.009861 | -0.37204 | -0.34449 | -0.10694 | -0.28888 | 0.004771 | -0.12131 | -0.01437 | -0.16141 | -0.13531 | 121.9003 | 121.6403 | 121.6678 | 62.2481 | -121.9967 | 121.7235 | 121.8509 | 121.877 | 62.3249 | -122.1193
177.8594 | 122.2092 | -62.3199 | 59.8022 | 1.4211e-13 | -0.024391 | -0.0034466 | 0.066434 | -0.005145 | 0.059018 | -0.013124 | 0.00057035 | -0.0019016 | -0.0030124 | 0.018209 | -0.0089584 | -62.2833 | 0.005985 | -62.2318 | 59.6673 | 59.3936 | 59.4303 | -62.2265 | -62.2282 | 0.091933 | -62.3634 | 59.4859 | 59.5996 | 59.6257 | -62.3536 | 0.093409 | -0.13493 | 0.036605 | 0.088126 | -0.005283 | -0.40866 | -0.37196 | -0.033698 | -0.31634 | 0.091748 | -0.043489 | -0.009791 | -0.20261 | -0.17651 | 121.9873 | 121.7135 | 121.7502 | 62.3259 | -122.0288 | 121.8059 | 121.9196 | 121.9457 | 62.4119 | -122.1559
179.5469 | 122.3007 | -62.2604 | 59.7748 | 1.4211e-13 | -0.02375 | -0.0034466 | 0.06622 | -0.0053586 | 0.059232 | 0.0021363 | 0.00057035 | -0.0019016 | -0.0027988 | 0.017996 | -0.0089584 | -62.2833 | 0.005985 | -62.241 | 59.6582 | 59.3936 | 59.4349 | -62.2311 | -62.2282 | 0.087354 | -62.3589 | 59.4813 | 59.5996 | 59.6028 | -62.3491 | 0.029321 | -0.11662 | -0.022904 | 0.01946 | -0.009861 | -0.38119 | -0.33991 | -0.088628 | -0.29345 | 0.032239 | -0.098419 | -0.009791 | -0.17514 | -0.17194 | 121.9186 | 121.654 | 121.6953 | 62.2664 | -122.0059 | 121.7418 | 121.8601 | 121.8633 | 62.3478 | -122.1238
181.2969 | 122.2961 | -62.2833 | 59.7153 | 1.4211e-13 | -0.024391 | -0.0034466 | 0.066648 | -0.0047176 | 0.059232 | -0.013124 | 0.00057035 | -0.0019016 | -0.0027988 | 0.017996 | -0.0089584 | -62.2879 | -0.007751 | -62.2364 | 59.6627 | 59.3982 | 59.4257 | -62.2357 | -62.2328 | 0.091933 | -62.3634 | 59.4813 | 59.6088 | 59.6349 | -62.3536 | 0.04763 | -0.052533 | -0.004594 | 0.046927 | -0.000703 | -0.3171 | -0.28956 | -0.070319 | -0.23394 | 0.050548 | -0.08011 | -0.009791 | -0.10647 | -0.08038 | 121.9461 | 121.6815 | 121.709 | 62.2756 | -121.951 | 121.7647 | 121.8921 | 121.9182 | 62.3753 | -122.0689
183.0469 | 122.2916 | -62.2833 | 59.729 | 1.4211e-13 | -0.024177 | -0.003874 | 0.066434 | -0.0047176 | 0.059232 | 0.0097668 | 0.00057035 | -0.0019016 | -0.002585 | 0.018209 | -0.0089584 | -62.2925 | 0.005985 | -62.2318 | 59.6582 | 59.3936 | 59.4303 | -62.2311 | -62.2374 | 0.082776 | -62.3589 | 59.4859 | 59.6088 | 59.6395 | -62.3582 | 0.052209 | -0.070845 | -0.009173 | 0.051505 | -0.000704 | -0.33542 | -0.29871 | -0.074898 | -0.2431 | 0.04597 | -0.075531 | -0.000633 | -0.12021 | -0.089534 | 121.9415 | 121.6769 | 121.7136 | 62.2893 | -121.9601 | 121.7692 | 121.8921 | 121.9228 | 62.3661 | -122.0872
184.7344 | 122.3373 | -62.2375 | 59.7885 | 1.4211e-13 | -0.024177 | -0.003874 | 0.066434 | -0.0047176 | 0.059659 | -0.0054937 | 0.00078395 | -0.0019016 | -0.0027988 | 0.018209 | -0.0089584 | -62.2879 | 0.010564 | -62.241 | 59.6582 | 59.389 | 59.4303 | -62.222 | -62.2282 | 0.087354 | -62.3634 | 59.4767 | 59.6088 | 59.6303 | -62.3491 | 0.015591 | -0.13035 | -0.05037 | -0.003428 | -0.019019 | -0.3995 | -0.35822 | -0.11152 | -0.31177 | 0.009351 | -0.12589 | -0.01437 | -0.17972 | -0.1582 | 121.8957 | 121.6266 | 121.6678 | 62.2481 | -122.0105 | 121.7143 | 121.8463 | 121.8679 | 62.3249 | -122.1376
186.4844 | 122.3648 | -62.2696 | 59.7427 | 1.4211e-13 | -0.024177 | -0.003874 | 0.06622 | -0.004504 | 0.059445 | -0.0054937 | 0.00078395 | -0.0016878 | -0.0027988 | 0.017782 | -0.0089584 | -62.2833 | 0.005985 | -62.2318 | 59.6627 | 59.3982 | 59.4394 | -62.2311 | -62.2282 | 0.091933 | -62.3589 | 59.4905 | 59.6042 | 59.6395 | -62.3582 | 0.038476 | -0.079999 | -0.013749 | 0.037772 | -0.000704 | -0.34457 | -0.30329 | -0.088631 | -0.25225 | 0.041394 | -0.089264 | -0.000633 | -0.13852 | -0.10327 | 121.9323 | 121.6678 | 121.709 | 62.2756 | -121.9739 | 121.7601 | 121.8738 | 121.9091 | 62.3615 | -122.101
188.2344 | 122.3373 | -62.265 | 59.7702 | 1.4211e-13 | -0.024177 | -0.003874 | 0.06622 | -0.004504 | 0.059018 | 0.0021363 | 0.00035675 | -0.0019016 | -0.0030124 | 0.017996 | -0.0091722 | -62.2833 | 0.005985 | -62.2318 | 59.6627 | 59.3936 | 59.4394 | -62.2311 | -62.2328 | 0.087354 | -62.3634 | 59.4813 | 59.6088 | 59.6212 | -62.3582 | 0.033899 | -0.10747 | -0.018326 | 0.033195 | -0.000704 | -0.37661 | -0.33076 | -0.093208 | -0.28888 | 0.032238 | -0.09842 | -0.005212 | -0.16141 | -0.14905 | 121.9278 | 121.6586 | 121.7045 | 62.271 | -122.0013 | 121.7463 | 121.8738 | 121.8862 | 62.3524 | -122.1284
189.9844 | 122.2183 | -62.265 | 59.7977 | 1.4211e-13 | -0.024177 | -0.0036602 | 0.06622 | -0.0047176 | 0.059232 | -0.0054937 | 0.00035675 | -0.0016878 | -0.0027988 | 0.017996 | -0.0089584 | -62.2833 | 0.010564 | -62.2318 | 59.6582 | 59.389 | 59.4303 | -62.222 | -62.1778 | 0.091933 | -62.3589 | 59.4859 | 59.6042 | 59.6349 | -62.3491 | 0.043057 | -0.13951 | -0.018326 | 0.033195 | -0.009862 | -0.40866 | -0.36738 | -0.08405 | -0.31176 | 0.087183 | -0.093841 | -0.009791 | -0.19345 | -0.16278 | 121.9232 | 121.654 | 121.6953 | 62.2756 | -122.0196 | 121.7509 | 121.8692 | 121.8999 | 62.3569 | -122.1467
191.6719 | 122.3602 | -62.2467 | 59.7473 | 1.4211e-13 | -0.024391 | -0.0036602 | 0.066434 | -0.0049314 | 0.059445 | -0.0054937 | 0.00057035 | -0.0016878 | -0.0027988 | 0.017996 | -0.0089584 | -62.2788 | 0.005985 | -62.2364 | 59.6536 | 59.3982 | 59.4303 | -62.2311 | -62.1229 | 0.078197 | -62.3589 | 59.4813 | 59.6042 | 59.6166 | -62.3582 | 0.015588 | -0.093733 | -0.032059 | 0.010306 | -0.005282 | -0.34915 | -0.31702 | -0.11152 | -0.26599 | 0.12382 | -0.11215 | -0.000633 | -0.1431 | -0.13074 | 121.9003 | 121.6449 | 121.677 | 62.2527 | -121.9784 | 121.728 | 121.8509 | 121.8633 | 62.3249 | -122.1055
193.4062 | 122.2092 | -62.2787 | 59.8297 | 1.4211e-13 | -0.024177 | -0.003874 | 0.06622 | -0.0047176 | 0.059232 | -0.013124 | 0.00078395 | -0.0016878 | -0.002585 | 0.017996 | -0.0089584 | -62.2833 | 0.005985 | -62.2456 | 59.6673 | 59.389 | 59.4303 | -62.222 | -62.0542 | 0.082776 | -62.3634 | 59.4859 | 59.6134 | 59.612 | -62.3491 | 0.05679 | -0.1624 | -0.004593 | 0.033193 | -0.023597 | -0.4407 | -0.39942 | -0.070317 | -0.34381 | 0.22454 | -0.084687 | -0.01437 | -0.21634 | -0.21771 | 121.9461 | 121.6678 | 121.709 | 62.2847 | -122.0517 | 121.7647 | 121.8921 | 121.8907 | 62.3615 | -122.1788
195.0781 | 122.2137 | -62.2879 | 59.7885 | 1.4211e-13 | -0.024604 | -0.003233 | 0.066434 | -0.004504 | 0.059232 | -0.0054937 | 0.00035675 | -0.0014742 | -0.002585 | 0.017782 | -0.0087448 | -62.2925 | 0.010564 | -62.2364 | 59.6627 | 59.3936 | 59.4257 | -62.2311 | -62.1504 | 0.082776 | -62.3589 | 59.4813 | 59.6088 | 59.6395 | -62.3536 | 0.056787 | -0.12578 | -0.004595 | 0.051505 | -0.005282 | -0.39492 | -0.3628 | -0.065741 | -0.30719 | 0.13754 | -0.070953 | -0.005212 | -0.17972 | -0.14904 | 121.9506 | 121.6815 | 121.7136 | 62.2985 | -122.0196 | 121.7692 | 121.8967 | 121.9274 | 62.3707 | -122.1422
196.8125 | 122.2229 | -62.2742 | 59.7931 | 1.4211e-13 | -0.024818 | -0.0040876 | 0.06622 | -0.0047176 | 0.059232 | -0.0054937 | 0.00035675 | -0.0021152 | -0.0030124 | 0.018423 | -0.0091722 | -62.2879 | 0.005985 | -62.2227 | 59.6536 | 59.3936 | 59.4303 | -62.2311 | -62.2419 | 0.087354 | -62.3634 | 59.4813 | 59.6088 | 59.6074 | -62.3536 | 0.043054 | -0.13951 | -0.013749 | 0.051506 | 0.008452 | -0.3995 | -0.3628 | -0.079474 | -0.31176 | 0.032236 | -0.089265 | -0.009791 | -0.18429 | -0.18567 | 121.9278 | 121.6678 | 121.7045 | 62.2802 | -122.0242 | 121.7555 | 121.883 | 121.8816 | 62.3615 | -122.1467
198.5 | 122.2046 | -62.2787 | 59.8206 | 1.4211e-13 | -0.024391 | -0.0036602 | 0.066861 | -0.0047176 | 0.059232 | 0.0021363 | 0.00078395 | -0.0016878 | -0.0027988 | 0.018423 | -0.0089584 | -62.2925 | 0.010564 | -62.2272 | 59.6582 | 59.389 | 59.4303 | -62.2265 | -62.0908 | 0.082776 | -62.3589 | 59.4767 | 59.6134 | 59.6303 | -62.3536 | 0.052211 | -0.1624 | -0.01375 | 0.051506 | -0.000705 | -0.43155 | -0.39027 | -0.074896 | -0.34381 | 0.18791 | -0.080108 | -0.005212 | -0.20718 | -0.19024 | 121.9369 | 121.6678 | 121.709 | 62.2893 | -122.0471 | 121.7555 | 121.8921 | 121.9091 | 62.3615 | -122.1742
200.25 | 122.3282 | -62.2787 | 59.7244 | 1.4211e-13 | -0.024177 | -0.0034466 | 0.066434 | -0.004504 | 0.059445 | 0.0097668 | 0.00057035 | -0.0016878 | -0.0027988 | 0.018423 | -0.0089584 | -62.2833 | 0.010564 | -62.2318 | 59.6627 | 59.4027 | 59.4257 | -62.2265 | -62.0863 | 0.087354 | -62.3634 | 59.4859 | 59.6134 | 59.5937 | -62.3536 | 0.052211 | -0.061688 | -0.004593 | 0.046928 | -0.005283 | -0.32168 | -0.29872 | -0.074896 | -0.23852 | 0.19249 | -0.084687 | -0.009791 | -0.11105 | -0.13074 | 121.9415 | 121.6815 | 121.7045 | 62.2893 | -121.951 | 121.7647 | 121.8921 | 121.8724 | 62.3661 | -122.0781
202 | 122.3282 | -62.2742 | 59.7382 | 1.4211e-13 | -0.024604 | -0.0034466 | 0.066007 | -0.0049314 | 0.059018 | -0.0054937 | 0.00035675 | -0.0016878 | -0.003226 | 0.017782 | -0.0091722 | -62.2879 | 0.010564 | -62.2364 | 59.6627 | 59.3982 | 59.4303 | -62.2265 | -62.132 | 0.087354 | -62.3589 | 59.4859 | 59.618 | 59.6349 | -62.3536 | 0.047633 | -0.075421 | -0.013749 | 0.037772 | -0.009861 | -0.33999 | -0.30787 | -0.079474 | -0.25225 | 0.14213 | -0.084686 | -0.005212 | -0.12021 | -0.10327 | 121.9369 | 121.6723 | 121.7045 | 62.2847 | -121.9647 | 121.7601 | 121.8921 | 121.9091 | 62.3615 | -122.0918
203.6875 | 122.2595 | -62.265 | 59.8068 | 1.4211e-13 | -0.024604 | -0.0036602 | 0.066434 | -0.004504 | 0.059232 | -0.013124 | 0.00078395 | -0.0016878 | -0.0027988 | 0.018209 | -0.0093858 | -62.2879 | 0.010564 | -62.2318 | 59.6673 | 59.3936 | 59.4349 | -62.2311 | -62.0771 | 0.078197 | -62.3634 | 59.4813 | 59.6042 | 59.644 | -62.3536 | 0.033899 | -0.13951 | -0.022904 | 0.033195 | -0.000704 | -0.41324 | -0.37195 | -0.088629 | -0.3255 | 0.18791 | -0.09842 | -0.009791 | -0.20261 | -0.16278 | 121.9323 | 121.6586 | 121.6999 | 62.2756 | -122.0379 | 121.7463 | 121.8692 | 121.9091 | 62.3432 | -122.1605
205.4375 | 122.3373 | -62.2787 | 59.7244 | 1.4211e-13 | -0.024391 | -0.0036602 | 0.066434 | -0.0049314 | 0.059232 | 0.0097668 | 0.00035675 | -0.0016878 | -0.0027988 | 0.018423 | -0.0091722 | -62.2833 | 0.005985 | -62.2318 | 59.6627 | 59.3982 | 59.4303 | -62.2311 | -62.1 | 0.082776 | -62.368 | 59.4813 | 59.618 | 59.6257 | -62.3582 | 0.047632 | -0.061688 | -0.004593 | 0.046928 | -0.000704 | -0.32626 | -0.29414 | -0.079475 | -0.2431 | 0.17875 | -0.089265 | -0.00979 | -0.10647 | -0.098692 | 121.9415 | 121.6769 | 121.709 | 62.2847 | -121.9555 | 121.7601 | 121.8967 | 121.9045 | 62.3615 | -122.0826
207.1094 | 122.3145 | -62.2559 | 59.7565 | 1.4211e-13 | -0.024818 | -0.0036602 | 0.06622 | -0.0047176 | 0.059445 | -0.0054937 | 0.00078395 | -0.0014742 | -0.003226 | 0.018209 | -0.0089584 | -62.2879 | 0.005985 | -62.2364 | 59.6673 | 59.4027 | 59.4303 | -62.2265 | -62.219 | 0.087354 | -62.3589 | 59.4859 | 59.6088 | 59.644 | -62.3491 | 0.029322 | -0.089154 | -0.03206 | 0.019461 | -0.009861 | -0.35372 | -0.32618 | -0.093206 | -0.27056 | 0.036818 | -0.103 | -0.009791 | -0.14767 | -0.11242 | 121.9232 | 121.6586 | 121.6861 | 62.2618 | -121.983 | 121.7418 | 121.8647 | 121.8999 | 62.3432 | -122.1055
208.8594 | 122.319 | -62.2787 | 59.7473 | 1.4211e-13 | -0.024818 | -0.003874 | 0.066434 | -0.004504 | 0.059232 | -0.013124 | 0.00057035 | -0.0016878 | -0.0030124 | 0.018423 | -0.0093858 | -62.2833 | 0.010564 | -62.241 | 59.6582 | 59.3982 | 59.4349 | -62.2311 | -61.8161 | 0.091933 | -62.3634 | 59.4767 | 59.6134 | 59.6349 | -62.3582 | 0.047632 | -0.089155 | -0.004593 | 0.037771 | -0.009861 | -0.34915 | -0.31245 | -0.079475 | -0.27057 | 0.46263 | -0.084687 | -0.005212 | -0.13394 | -0.11242 | 121.9369 | 121.6769 | 121.7136 | 62.2893 | -121.9784 | 121.7555 | 121.8921 | 121.9136 | 62.3707 | -122.1055
210.625 | 122.2275 | -62.3108 | 59.7931 | 1.4211e-13 | -0.024391 | -0.0040876 | 0.066434 | -0.0042904 | 0.059018 | -0.0054937 | 0.00035675 | -0.0014742 | -0.0027988 | 0.018209 | -0.0091722 | -62.2971 | 0.015142 | -62.241 | 59.6582 | 59.4027 | 59.4257 | -62.2311 | -61.6925 | 0.087354 | -62.3634 | 59.4859 | 59.6042 | 59.6349 | -62.3536 | 0.079675 | -0.13493 | 0.013715 | 0.069814 | -0.009861 | -0.39034 | -0.36738 | -0.042853 | -0.30719 | 0.6183 | -0.052644 | -0.009791 | -0.18887 | -0.1582 | 121.969 | 121.7135 | 121.7365 | 62.3259 | -122.0242 | 121.7967 | 121.915 | 121.9457 | 62.3981 | -122.1467
212.3125 | 122.2092 | -62.2742 | 59.8389 | 1.4211e-13 | -0.024604 | -0.0036602 | 0.066434 | -0.004504 | 0.059018 | -0.0054937 | 0.00078395 | -0.0016878 | -0.0030124 | 0.018423 | -0.0091722 | -62.2925 | 0.001407 | -62.2364 | 59.6673 | 59.389 | 59.4257 | -62.222 | -62.2374 | 0.082776 | -62.3634 | 59.4859 | 59.6134 | 59.6303 | -62.3536 | 0.052212 | -0.17155 | -0.018328 | 0.037772 | -0.01444 | -0.44986 | -0.41316 | -0.079474 | -0.35296 | 0.036815 | -0.089265 | -0.009791 | -0.22549 | -0.20855 | 121.9415 | 121.6632 | 121.6999 | 62.2756 | -122.0608 | 121.7601 | 121.8875 | 121.9045 | 62.3569 | -122.1925
214.0469 | 122.2412 | -62.2604 | 59.8389 | 1.4211e-13 | -0.025032 | -0.003874 | 0.06622 | -0.004504 | 0.059018 | -0.0054937 | 0.00078395 | -0.0016878 | -0.0027988 | 0.018209 | -0.0089584 | -62.2833 | 0.005985 | -62.2456 | 59.6582 | 59.3982 | 59.4257 | -62.2265 | -62.2328 | 0.082776 | -62.3589 | 59.4859 | 59.6134 | 59.6212 | -62.3536 | 0.0339 | -0.18071 | -0.022904 | 0.014882 | -0.019018 | -0.4407 | -0.41316 | -0.093207 | -0.35296 | 0.02766 | -0.098419 | -0.005212 | -0.22549 | -0.21771 | 121.9186 | 121.6586 | 121.6861 | 62.2664 | -122.0654 | 121.7463 | 121.8738 | 121.8816 | 62.3432 | -122.1925
215.7812 | 122.3419 | -62.265 | 59.7748 | 1.4211e-13 | -0.025032 | -0.003874 | 0.066434 | -0.0047176 | 0.059232 | -0.0054937 | 0.00078395 | -0.0019016 | -0.0030124 | 0.018209 | -0.0089584 | -62.2788 | -0.003172 | -62.2501 | 59.6582 | 59.4027 | 59.4257 | -62.2265 | -62.2465 | 0.082776 | -62.3634 | 59.4905 | 59.618 | 59.6395 | -62.3582 | 0.038478 | -0.11662 | -0.013748 | 0.014882 | -0.023596 | -0.37203 | -0.34907 | -0.093208 | -0.2843 | 0.018502 | -0.09842 | -0.005212 | -0.15683 | -0.13531 | 121.9232 | 121.6678 | 121.6907 | 62.2618 | -122.0013 | 121.7555 | 121.883 | 121.9045 | 62.3478 | -122.133
217.5469 | 122.3328 | -62.2971 | 59.7382 | 1.4211e-13 | -0.024818 | -0.0036602 | 0.06622 | -0.0049314 | 0.058804 | -0.013124 | 0.00078395 | -0.0016878 | -0.0027988 | 0.017996 | -0.0089584 | -62.2833 | 0.015142 | -62.2456 | 59.6627 | 59.3982 | 59.4349 | -62.2265 | -61.9352 | 0.082776 | -62.3589 | 59.4859 | 59.618 | 59.6257 | -62.3536 | 0.070521 | -0.075421 | 0.013717 | 0.051503 | -0.019018 | -0.33999 | -0.30329 | -0.056586 | -0.25225 | 0.3619 | -0.061798 | -0.005212 | -0.12021 | -0.11243 | 121.9598 | 121.6952 | 121.7319 | 62.3122 | -121.9647 | 121.783 | 121.915 | 121.9228 | 62.3798 | -122.0918
219.2344 | 122.2321 | -62.2879 | 59.8022 | 1.4211e-13 | -0.024818 | -0.003874 | 0.06622 | -0.0047176 | 0.059018 | 0.0097668 | 0.00057035 | -0.0019016 | -0.003226 | 0.018209 | -0.0093858 | -62.2833 | 0.001407 | -62.2593 | 59.6582 | 59.3936 | 59.4303 | -62.2265 | -61.8711 | 0.087354 | -62.3634 | 59.4767 | 59.6088 | 59.6257 | -62.3582 | 0.061366 | -0.14409 | 0.004562 | 0.028613 | -0.032753 | -0.40866 | -0.37196 | -0.07032 | -0.3255 | 0.41684 | -0.075532 | -0.005212 | -0.19345 | -0.17651 | 121.9461 | 121.6815 | 121.7182 | 62.2893 | -122.0288 | 121.7647 | 121.8967 | 121.9136 | 62.3753 | -122.1605
220.9844 | 122.3419 | -62.2559 | 59.761 | 1.4211e-13 | -0.024818 | -0.003874 | 0.06622 | -0.0049314 | 0.059018 | -0.0054937 | 0.00035675 | -0.0019016 | -0.003226 | 0.018209 | -0.0089584 | -62.2833 | 0.005985 | -62.2547 | 59.6582 | 59.389 | 59.4211 | -62.2265 | -61.9168 | 0.082776 | -62.3589 | 59.4813 | 59.6134 | 59.6028 | -62.3536 | 0.029322 | -0.10289 | -0.027482 | 0.001147 | -0.028175 | -0.37204 | -0.33991 | -0.097785 | -0.27972 | 0.33901 | -0.103 | -0.005212 | -0.14767 | -0.15821 | 121.914 | 121.6449 | 121.677 | 62.2618 | -121.9876 | 121.7372 | 121.8692 | 121.8587 | 62.3386 | -122.1147
222.75 | 122.3053 | -62.2833 | 59.7565 | 1.4211e-13 | -0.024818 | -0.0036602 | 0.066648 | -0.0047176 | 0.059018 | -0.0054937 | 0.00035675 | -0.0014742 | -0.0030124 | 0.018209 | -0.0089584 | -62.2879 | 0.001407 | -62.2547 | 59.6627 | 59.3982 | 59.4349 | -62.2265 | -61.7841 | 0.087354 | -62.3589 | 59.4813 | 59.618 | 59.612 | -62.3582 | 0.056788 | -0.093732 | -0.004594 | 0.028613 | -0.028175 | -0.3583 | -0.3216 | -0.074898 | -0.27514 | 0.49926 | -0.075531 | -0.000633 | -0.13852 | -0.14447 | 121.9461 | 121.6815 | 121.7182 | 62.2847 | -121.983 | 121.7647 | 121.9013 | 121.8953 | 62.3707 | -122.1147
224.4375 | 122.2458 | -62.2604 | 59.8022 | 1.4211e-13 | -0.025032 | -0.0040876 | 0.066434 | -0.0047176 | 0.059018 | 0.0021363 | 0.00057035 | -0.0016878 | -0.0027988 | 0.017996 | -0.0089584 | -62.2879 | 0.001407 | -62.2456 | 59.6582 | 59.3936 | 59.4257 | -62.2311 | -61.7932 | 0.087354 | -62.3634 | 59.4859 | 59.6134 | 59.6349 | -62.3628 | 0.029321 | -0.14409 | -0.027482 | 0.014882 | -0.014439 | -0.40866 | -0.37653 | -0.10236 | -0.31634 | 0.46722 | -0.103 | -0.000633 | -0.18887 | -0.16735 | 121.9186 | 121.654 | 121.6861 | 62.2618 | -122.0334 | 121.7463 | 121.8738 | 121.8953 | 62.3478 | -122.165
226.1875 | 122.319 | -62.2833 | 59.7519 | 1.4211e-13 | -0.024818 | -0.003874 | 0.06622 | -0.004504 | 0.058804 | -0.0054937 | 0.00099775 | -0.0016878 | -0.0027988 | 0.018637 | -0.0091722 | -62.2788 | -0.003172 | -62.2501 | 59.6582 | 59.3982 | 59.4303 | -62.2357 | -61.807 | 0.082776 | -62.3726 | 59.4859 | 59.6225 | 59.6349 | -62.3582 | 0.04763 | -0.093733 | 0.004562 | 0.033192 | -0.014438 | -0.35372 | -0.3216 | -0.074898 | -0.26599 | 0.47637 | -0.089267 | -0.014369 | -0.12936 | -0.117 | 121.9415 | 121.6815 | 121.7136 | 62.2802 | -121.9876 | 121.7692 | 121.9059 | 121.9182 | 62.3661 | -122.1101
227.8594 | 122.2183 | -62.2833 | 59.8343 | 1.4211e-13 | -0.025245 | -0.0040876 | 0.066648 | -0.004504 | 0.059232 | -0.013124 | 0.00078395 | -0.0014742 | -0.0030124 | 0.018637 | -0.0089584 | -62.2879 | -0.003172 | -62.2501 | 59.6582 | 59.3982 | 59.4211 | -62.222 | -61.8253 | 0.091933 | -62.3634 | 59.4859 | 59.6134 | 59.5754 | -62.3582 | 0.061367 | -0.17613 | -0.004594 | 0.033192 | -0.028175 | -0.43612 | -0.41316 | -0.074898 | -0.34839 | 0.45805 | -0.08011 | -0.005212 | -0.22092 | -0.25892 | 121.9415 | 121.6815 | 121.7045 | 62.2802 | -122.0562 | 121.7692 | 121.8967 | 121.8587 | 62.3753 | -122.1925
229.5938 | 122.2458 | -62.2787 | 59.8206 | 1.4211e-13 | -0.025245 | -0.0036602 | 0.066861 | -0.0049314 | 0.059232 | -0.0054937 | 0.00078395 | -0.0019016 | -0.003226 | 0.018209 | -0.0089584 | -62.2879 | 0.005985 | -62.2593 | 59.6582 | 59.3982 | 59.4349 | -62.2265 | -61.807 | 0.082776 | -62.3589 | 59.4813 | 59.618 | 59.6257 | -62.3582 | 0.052211 | -0.1624 | -0.009171 | 0.019458 | -0.032753 | -0.42239 | -0.38569 | -0.079475 | -0.33923 | 0.47179 | -0.080108 | -0.000633 | -0.2026 | -0.19482 | 121.9369 | 121.6769 | 121.7136 | 62.2847 | -122.0471 | 121.7601 | 121.8967 | 121.9045 | 62.3615 | -122.1788
231.3281 | 122.2092 | -62.2925 | 59.8389 | 1.4211e-13 | -0.025032 | -0.003874 | 0.066648 | -0.004504 | 0.058591 | 0.0021363 | 0.00099775 | -0.0016878 | -0.0030124 | 0.018423 | -0.0089584 | -62.2925 | 0.001407 | -62.2547 | 59.6582 | 59.3982 | 59.4303 | -62.2265 | -61.7932 | 0.082776 | -62.3589 | 59.4859 | 59.6088 | 59.6212 | -62.3582 | 0.065943 | -0.18071 | -1.8e-05 | 0.037768 | -0.028175 | -0.4407 | -0.40858 | -0.065743 | -0.35296 | 0.49926 | -0.066376 | -0.000633 | -0.23007 | -0.21771 | 121.9506 | 121.6906 | 121.7228 | 62.2939 | -122.0654 | 121.7784 | 121.9013 | 121.9136 | 62.3753 | -122.1971
233.0625 | 122.2687 | -62.2742 | 59.7839 | 1.4211e-13 | -0.025032 | -0.0040876 | 0.066434 | -0.005145 | 0.058804 | 0.0021363 | 0.00057035 | -0.0019016 | -0.0030124 | 0.018423 | -0.0091722 | -62.2879 | 0.001407 | -62.2501 | 59.6582 | 59.3982 | 59.4394 | -62.2265 | -61.7886 | 0.087354 | -62.3634 | 59.4859 | 59.6088 | 59.6257 | -62.3582 | 0.047633 | -0.12578 | -0.013749 | 0.024037 | -0.023596 | -0.38577 | -0.34449 | -0.084053 | -0.29803 | 0.48553 | -0.089265 | -0.005212 | -0.17514 | -0.1582 | 121.9323 | 121.6723 | 121.7136 | 62.2756 | -122.0105 | 121.7601 | 121.883 | 121.8999 | 62.3615 | -122.1422
234.7969 | 122.2733 | -62.2696 | 59.8206 | 1.4211e-13 | -0.025245 | -0.0036602 | 0.066434 | -0.0042904 | 0.059018 | 0.0021363 | 0.00057035 | -0.0019016 | -0.0030124 | 0.018637 | -0.0089584 | -62.2833 | 0.001407 | -62.2501 | 59.6582 | 59.389 | 59.4257 | -62.2357 | -61.7932 | 0.087354 | -62.3543 | 59.4859 | 59.6134 | 59.5937 | -62.3582 | 0.033897 | -0.1624 | -0.013749 | 0.019459 | -0.014438 | -0.43155 | -0.39485 | -0.088631 | -0.33465 | 0.47637 | -0.084685 | 0.003946 | -0.20718 | -0.22687 | 121.9278 | 121.6586 | 121.6953 | 62.271 | -122.0563 | 121.7555 | 121.883 | 121.8633 | 62.3569 | -122.1788
236.5312 | 122.3282 | -62.2971 | 59.7382 | 1.4211e-13 | -0.025032 | -0.0036602 | 0.06622 | -0.0042904 | 0.059232 | -0.0054937 | 0.00057035 | -0.0019016 | -0.002585 | 0.018637 | -0.0091722 | -62.2879 | 0.001407 | -62.2593 | 59.6627 | 59.4027 | 59.4349 | -62.2311 | -61.7932 | 0.082776 | -62.3634 | 59.4905 | 59.6134 | 59.6349 | -62.3674 | 0.065942 | -0.075421 | 0.009139 | 0.037768 | -0.028174 | -0.33541 | -0.30329 | -0.070322 | -0.24768 | 0.50384 | -0.066377 | 0.003945 | -0.12478 | -0.10327 | 121.9598 | 121.6998 | 121.7319 | 62.2985 | -121.9693 | 121.7875 | 121.9104 | 121.9319 | 62.3798 | -122.1055
238.2188 | 122.2046 | -62.2925 | 59.7885 | 1.4211e-13 | -0.025459 | -0.003874 | 0.066648 | -0.004504 | 0.059018 | -0.0054937 | 0.00035675 | -0.0016878 | -0.0027988 | 0.018637 | -0.0091722 | -62.2879 | 0.001407 | -62.2547 | 59.6536 | 59.3982 | 59.4303 | -62.2265 | -61.7474 | 0.082776 | -62.368 | 59.4859 | 59.6134 | 59.6349 | -62.3628 | 0.065943 | -0.13493 | 0.004561 | 0.037768 | -0.028175 | -0.39035 | -0.35822 | -0.070322 | -0.30261 | 0.54505 | -0.075533 | -0.005211 | -0.17514 | -0.15362 | 121.9461 | 121.6906 | 121.7228 | 62.2939 | -122.0151 | 121.7784 | 121.9059 | 121.9274 | 62.3753 | -122.1513
239.9531 | 122.2366 | -62.2742 | 59.8206 | 1.4211e-13 | -0.025245 | -0.0036602 | 0.06622 | -0.0049314 | 0.058804 | 0.0021363 | 0.00057035 | -0.0016878 | -0.003226 | 0.018423 | -0.0087448 | -62.2833 | -0.003172 | -62.2593 | 59.6627 | 59.4027 | 59.4257 | -62.2357 | -61.7429 | 0.087354 | -62.3589 | 59.4859 | 59.6134 | 59.6395 | -62.3536 | 0.038475 | -0.15782 | -0.009171 | 0.01488 | -0.023595 | -0.41781 | -0.39485 | -0.079474 | -0.33465 | 0.53131 | -0.084686 | -0.005212 | -0.20718 | -0.18109 | 121.9369 | 121.6769 | 121.6999 | 62.271 | -122.0563 | 121.7601 | 121.8875 | 121.9136 | 62.3615 | -122.1742
241.7031 | 122.3419 | -62.265 | 59.7382 | 1.4211e-13 | -0.025245 | -0.003874 | 0.066648 | -0.004504 | 0.059018 | 0.0021363 | 0.00078395 | -0.0016878 | -0.003226 | 0.018637 | -0.0091722 | -62.2833 | 0.005985 | -62.2639 | 59.6582 | 59.3936 | 59.4349 | -62.2357 | -61.7245 | 0.087354 | -62.3589 | 59.4859 | 59.6134 | 59.6349 | -62.3628 | 0.02932 | -0.08 | -0.018326 | 0.001147 | -0.028173 | -0.34457 | -0.30329 | -0.097787 | -0.25225 | 0.54048 | -0.093841 | 0.003946 | -0.12478 | -0.10327 | 121.9232 | 121.6586 | 121.6999 | 62.271 | -121.9739 | 121.7509 | 121.8784 | 121.8999 | 62.3524 | -122.101
243.3906 | 122.2046 | -62.3245 | 59.8022 | 1.4211e-13 | -0.025245 | -0.003874 | 0.06622 | -0.0047176 | 0.058804 | -0.0054937 | 0.00057035 | -0.0019016 | -0.0034396 | 0.018637 | -0.0091722 | -62.2879 | -0.003172 | -62.2547 | 59.6536 | 59.3936 | 59.4303 | -62.2311 | -61.7795 | 0.082776 | -62.3589 | 59.4905 | 59.618 | 59.6395 | -62.3582 | 0.093408 | -0.14866 | 0.036605 | 0.069812 | -0.023596 | -0.40866 | -0.37196 | -0.033699 | -0.31176 | 0.54504 | -0.034332 | -0.000633 | -0.18429 | -0.16278 | 121.9781 | 121.7181 | 121.7548 | 62.3214 | -122.0334 | 121.815 | 121.9425 | 121.964 | 62.4073 | -122.1605
245.1406 | 122.2366 | -62.2833 | 59.816 | 1.4211e-13 | -0.025459 | -0.0040876 | 0.066648 | -0.004504 | 0.059018 | 0.0097668 | 0.00099775 | -0.0019016 | -0.0030124 | 0.018423 | -0.0091722 | -62.2833 | 0.005985 | -62.2593 | 59.6582 | 59.4027 | 59.4257 | -62.2311 | -61.7978 | 0.091933 | -62.368 | 59.4859 | 59.6088 | 59.6212 | -62.3674 | 0.052209 | -0.15782 | -1.6e-05 | 0.024035 | -0.028174 | -0.41323 | -0.39027 | -0.084055 | -0.33007 | 0.48553 | -0.084688 | -0.000633 | -0.20718 | -0.19482 | 121.9415 | 121.6861 | 121.709 | 62.2893 | -122.0471 | 121.7692 | 121.8921 | 121.9045 | 62.3753 | -122.1834
246.8906 | 122.2504 | -62.2787 | 59.7839 | 1.4211e-13 | -0.025459 | -0.003874 | 0.06622 | -0.004504 | 0.058804 | -0.0054937 | 0.00078395 | -0.0021152 | -0.0027988 | 0.018423 | -0.0093858 | -62.2879 | -0.003172 | -62.2547 | 59.6582 | 59.389 | 59.4349 | -62.222 | -61.6696 | 0.082776 | -62.3589 | 59.4859 | 59.618 | 59.6303 | -62.3582 | 0.05679 | -0.12578 | -0.009171 | 0.024036 | -0.032754 | -0.39493 | -0.34907 | -0.079475 | -0.29803 | 0.60915 | -0.080108 | -0.000633 | -0.16598 | -0.15362 | 121.9369 | 121.6678 | 121.7136 | 62.2756 | -122.0059 | 121.7647 | 121.8967 | 121.9091 | 62.3615 | -122.1422
248.6406 | 122.319 | -62.2742 | 59.7931 | 1.4211e-13 | -0.025459 | -0.0036602 | 0.06622 | -0.004504 | 0.058804 | 0.0021363 | 0.00057035 | -0.0016878 | -0.002585 | 0.018423 | -0.0091722 | -62.2833 | 0.010564 | -62.2547 | 59.6627 | 59.3982 | 59.4303 | -62.2311 | -61.6742 | 0.087354 | -62.368 | 59.4813 | 59.6088 | 59.6303 | -62.3582 | 0.043054 | -0.13035 | -0.009171 | 0.019458 | -0.023596 | -0.39492 | -0.3628 | -0.084053 | -0.31176 | 0.6 | -0.093843 | -0.00979 | -0.18429 | -0.16278 | 121.9369 | 121.6723 | 121.7045 | 62.2847 | -122.0242 | 121.7555 | 121.883 | 121.9045 | 62.3615 | -122.1513
250.3281 | 122.3373 | -62.265 | 59.7427 | 1.4211e-13 | -0.025245 | -0.003874 | 0.06622 | -0.0049314 | 0.058804 | -0.013124 | 0.00057035 | -0.0019016 | -0.0027988 | 0.018423 | -0.0093858 | -62.2788 | 0.010564 | -62.2501 | 59.6627 | 59.4027 | 59.4349 | -62.2357 | -61.6788 | 0.082776 | -62.3543 | 59.4859 | 59.618 | 59.6349 | -62.3582 | 0.02932 | -0.079999 | -0.013748 | 0.014882 | -0.014438 | -0.33999 | -0.30787 | -0.093208 | -0.25683 | 0.58626 | -0.089262 | 0.003946 | -0.12478 | -0.10785 | 121.9278 | 121.6678 | 121.6999 | 62.2756 | -121.9784 | 121.7509 | 121.883 | 121.8999 | 62.3478 | -122.101
252.0781 | 122.3648 | -62.2604 | 59.7656 | 1.4211e-13 | -0.025245 | -0.003874 | 0.066434 | -0.005145 | 0.058804 | 0.0021363 | 0.00099775 | -0.0021152 | -0.0027988 | 0.018637 | -0.0089584 | -62.2833 | 0.001407 | -62.2501 | 59.6582 | 59.3982 | 59.4349 | -62.2265 | -61.7016 | 0.082776 | -62.3589 | 59.4905 | 59.6134 | 59.6303 | -62.3582 | 0.0339 | -0.10747 | -0.022904 | 0.010304 | -0.023596 | -0.36746 | -0.33076 | -0.097786 | -0.27514 | 0.55879 | -0.098419 | -0.000633 | -0.15225 | -0.13531 | 121.9186 | 121.6586 | 121.6953 | 62.2618 | -121.9922 | 121.7509 | 121.8738 | 121.8907 | 62.3432 | -122.1238
253.7656 | 122.2229 | -62.3154 | 59.7839 | 1.4211e-13 | -0.025459 | -0.0036602 | 0.066434 | -0.0047176 | 0.058591 | -0.013124 | 0.00057035 | -0.0014742 | -0.003226 | 0.018423 | -0.0091722 | -62.2879 | 0.005985 | -62.2593 | 59.6536 | 59.3982 | 59.444 | -62.2357 | -61.6055 | 0.087354 | -62.368 | 59.4859 | 59.6134 | 59.6395 | -62.3674 | 0.079674 | -0.13035 | 0.02745 | 0.056079 | -0.023595 | -0.38577 | -0.33991 | -0.052011 | -0.29803 | 0.70988 | -0.052644 | -0.000633 | -0.17056 | -0.14447 | 121.969 | 121.7135 | 121.7594 | 62.3214 | -122.0196 | 121.8013 | 121.9287 | 121.9548 | 62.4027 | -122.1513
255.5 | 122.3145 | -62.2971 | 59.7473 | 1.4211e-13 | -0.025673 | -0.0036602 | 0.06622 | -0.0047176 | 0.059018 | -0.0054937 | 0.00035675 | -0.0019016 | -0.0030124 | 0.018423 | -0.0093858 | -62.2788 | -0.003172 | -62.2593 | 59.6582 | 59.4027 | 59.4349 | -62.2357 | -61.8573 | 0.087354 | -62.3543 | 59.4905 | 59.6225 | 59.6349 | -62.3582 | 0.061363 | -0.089155 | 0.018295 | 0.037768 | -0.023595 | -0.34457 | -0.31245 | -0.061165 | -0.25683 | 0.43973 | -0.057219 | 0.003946 | -0.12478 | -0.11242 | 121.9552 | 121.6998 | 121.7319 | 62.2939 | -121.983 | 121.7875 | 121.9196 | 121.9319 | 62.3844 | -122.1055
257.1719 | 122.3419 | -62.2559 | 59.7656 | 1.4211e-13 | -0.025673 | -0.0036602 | 0.066434 | -0.0049314 | 0.059018 | 0.0021363 | 0.00078395 | -0.0016878 | -0.0027988 | 0.018423 | -0.0089584 | -62.2833 | -0.003172 | -62.2547 | 59.6582 | 59.4073 | 59.4303 | -62.2403 | -61.8573 | 0.082776 | -62.3589 | 59.4859 | 59.618 | 59.6303 | -62.3674 | 0.015585 | -0.10747 | -0.027482 | 0.001147 | -0.014438 | -0.3583 | -0.33534 | -0.11152 | -0.27972 | 0.39854 | -0.103 | 0.008524 | -0.14767 | -0.13531 | 121.914 | 121.6632 | 121.6861 | 62.2527 | -122.0059 | 121.7418 | 121.8738 | 121.8862 | 62.3386 | -122.133
258.9062 | 122.2366 | -62.2879 | 59.8206 | 1.4211e-13 | -0.025886 | -0.0036602 | 0.066434 | -0.004504 | 0.059018 | -0.0054937 | 0.00078395 | -0.0016878 | -0.002585 | 0.01885 | -0.0091722 | -62.2879 | 0.001407 | -62.2593 | 59.6582 | 59.3982 | 59.444 | -62.2265 | -61.6925 | 0.091933 | -62.368 | 59.4905 | 59.6271 | 59.6303 | -62.3674 | 0.061366 | -0.1624 | -1.6e-05 | 0.028613 | -0.032753 | -0.42239 | -0.37653 | -0.079477 | -0.33007 | 0.59541 | -0.08011 | -0.000633 | -0.19345 | -0.19024 | 121.9461 | 121.6861 | 121.7319 | 62.2893 | -122.0471 | 121.7784 | 121.915 | 121.9182 | 62.3798 | -122.1879
260.6562 | 122.3145 | -62.2787 | 59.7198 | 1.4211e-13 | -0.025886 | -0.0036602 | 0.066434 | -0.005145 | 0.058804 | -0.0054937 | 0.00035675 | -0.0016878 | -0.003226 | 0.018637 | -0.0089584 | -62.2879 | 0.010564 | -62.2547 | 59.6627 | 59.3936 | 59.4394 | -62.2357 | -61.8619 | 0.082776 | -62.3634 | 59.4951 | 59.6134 | 59.6395 | -62.3582 | 0.043053 | -0.057111 | -0.009171 | 0.024036 | -0.019017 | -0.32626 | -0.2804 | -0.079475 | -0.22479 | 0.41685 | -0.084687 | -0.005212 | -0.10647 | -0.080379 | 121.9415 | 121.6723 | 121.7182 | 62.2893 | -121.9555 | 121.7738 | 121.8921 | 121.9182 | 62.3615 | -122.0781
262.3438 | 122.2046 | -62.3154 | 59.7977 | 1.4211e-13 | -0.025673 | -0.003874 | 0.066434 | -0.0047176 | 0.059018 | 0.0021363 | 0.00057035 | -0.0014742 | -0.003226 | 0.019064 | -0.0091722 | -62.2833 | 0.010564 | -62.2684 | 59.6673 | 59.4073 | 59.4349 | -62.2357 | -61.9077 | 0.082776 | -62.368 | 59.4859 | 59.618 | 59.6303 | -62.3628 | 0.079674 | -0.13035 | 0.032028 | 0.046923 | -0.032751 | -0.39034 | -0.3628 | -0.047433 | -0.31176 | 0.40768 | -0.052644 | -0.005211 | -0.17971 | -0.16736 | 121.9827 | 121.7227 | 121.7502 | 62.3259 | -122.0334 | 121.8013 | 121.9333 | 121.9457 | 62.3981 | -122.1605
264.0312 | 122.3511 | -62.2787 | 59.7656 | 1.4211e-13 | -0.025886 | -0.0040876 | 0.066648 | -0.0047176 | 0.059232 | 0.0021363 | 0.00057035 | -0.0016878 | -0.003226 | 0.018637 | -0.0093858 | -62.2833 | 0.005985 | -62.2593 | 59.6627 | 59.4027 | 59.4349 | -62.2357 | -61.9443 | 0.091933 | -62.3589 | 59.4905 | 59.6225 | 59.6349 | -62.3582 | 0.043053 | -0.10289 | -0.004593 | 0.019458 | -0.023595 | -0.36288 | -0.33076 | -0.079475 | -0.27514 | 0.33443 | -0.080108 | -0.000633 | -0.14309 | -0.13073 | 121.9415 | 121.6815 | 121.7136 | 62.2847 | -122.0013 | 121.7692 | 121.9013 | 121.9136 | 62.3707 | -122.1238
265.7812 | 122.3373 | -62.2513 | 59.7656 | 1.4211e-13 | -0.025673 | -0.003874 | 0.066434 | -0.0049314 | 0.058804 | -0.013124 | 0.00099775 | -0.0016878 | -0.0027988 | 0.018637 | -0.0093858 | -62.2879 | 0.005985 | -62.2547 | 59.6673 | 59.4027 | 59.444 | -62.2403 | -62.1 | 0.091933 | -62.3589 | 59.4859 | 59.618 | 59.644 | -62.3628 | 0.011008 | -0.098309 | -0.036637 | -0.00343 | -0.014438 | -0.36288 | -0.3216 | -0.11152 | -0.27972 | 0.15129 | -0.10757 | 0.003946 | -0.14767 | -0.12158 | 121.9186 | 121.654 | 121.6953 | 62.2573 | -122.0059 | 121.7372 | 121.8692 | 121.8953 | 62.3432 | -122.1284
267.5312 | 122.2183 | -62.3062 | 59.7931 | 1.4211e-13 | -0.025673 | -0.0036602 | 0.066434 | -0.005145 | 0.058591 | -0.0054937 | 0.00078395 | -0.0014742 | -0.0030124 | 0.018637 | -0.0093858 | -62.2788 | 0.001407 | -62.2501 | 59.6582 | 59.4073 | 59.4349 | -62.2357 | -62.1 | 0.087354 | -62.3543 | 59.4905 | 59.618 | 59.644 | -62.3628 | 0.070518 | -0.13493 | 0.02745 | 0.05608 | -0.014438 | -0.38576 | -0.35822 | -0.056589 | -0.30261 | 0.20622 | -0.048064 | 0.008525 | -0.17514 | -0.14904 | 121.9644 | 121.7135 | 121.7411 | 62.3076 | -122.0288 | 121.7967 | 121.9242 | 121.9503 | 62.3936 | -122.1559
269.2188 | 122.2321 | -62.2787 | 59.8389 | 1.4211e-13 | -0.025886 | -0.003874 | 0.06622 | -0.0049314 | 0.058804 | 0.0097668 | 0.00078395 | -0.0016878 | -0.003226 | 0.018423 | -0.0089584 | -62.2788 | 0.001407 | -62.2547 | 59.6627 | 59.4027 | 59.4349 | -62.2265 | -62.1046 | 0.082776 | -62.3589 | 59.4859 | 59.618 | 59.6349 | -62.3628 | 0.052211 | -0.17613 | -1.5e-05 | 0.024036 | -0.028175 | -0.43612 | -0.404 | -0.084054 | -0.35296 | 0.17417 | -0.080108 | 0.003946 | -0.22091 | -0.20398 | 121.9415 | 121.6815 | 121.7136 | 62.2802 | -122.0654 | 121.7647 | 121.8967 | 121.9136 | 62.3615 | -122.2017
270.9531 | 122.3007 | -62.2787 | 59.7794 | 1.4211e-13 | -0.025459 | -0.0040876 | 0.06622 | -0.0047176 | 0.058804 | 0.0021363 | 0.00078395 | -0.0016878 | -0.003226 | 0.018209 | -0.0095994 | -62.2833 | 0.010564 | -62.2547 | 59.6627 | 59.4073 | 59.4349 | -62.2357 | -62.0863 | 0.082776 | -62.3634 | 59.4859 | 59.618 | 59.6395 | -62.3582 | 0.043053 | -0.11662 | -0.004593 | 0.024036 | -0.019017 | -0.37203 | -0.34449 | -0.079475 | -0.29345 | 0.19249 | -0.084687 | -0.005212 | -0.1614 | -0.13989 | 121.9415 | 121.6861 | 121.7136 | 62.2893 | -122.0151 | 121.7647 | 121.8967 | 121.9182 | 62.3615 | -122.1376
272.7031 | 122.2412 | -62.2787 | 59.8297 | 1.4211e-13 | -0.026314 | -0.003874 | 0.066434 | -0.004504 | 0.058591 | 0.0097668 | 0.00099775 | -0.0016878 | -0.003226 | 0.019064 | -0.0091722 | -62.2925 | 0.010564 | -62.2639 | 59.6627 | 59.3936 | 59.4303 | -62.2311 | -62.0954 | 0.087354 | -62.3634 | 59.4905 | 59.6134 | 59.6395 | -62.3582 | 0.047632 | -0.16697 | -0.01375 | 0.01488 | -0.032752 | -0.43612 | -0.39942 | -0.079475 | -0.33923 | 0.18333 | -0.084687 | -0.005212 | -0.21634 | -0.19024 | 121.9415 | 121.6723 | 121.709 | 62.2893 | -122.0608 | 121.7692 | 121.8921 | 121.9182 | 62.3661 | -122.1879
274.4531 | 122.3099 | -62.2787 | 59.7382 | 1.4211e-13 | -0.025886 | -0.0040876 | 0.066007 | -0.0047176 | 0.058804 | 0.0021363 | 0.00078395 | -0.0014742 | -0.003226 | 0.019278 | -0.0091722 | -62.2788 | 0.005985 | -62.2593 | 59.6627 | 59.4027 | 59.4349 | -62.2403 | -62.1412 | 0.087354 | -62.3543 | 59.4859 | 59.6134 | 59.6395 | -62.3674 | 0.038474 | -0.075421 | -1.5e-05 | 0.019458 | -0.019016 | -0.33541 | -0.30329 | -0.088632 | -0.25225 | 0.13755 | -0.075529 | 0.013103 | -0.12478 | -0.098689 | 121.9415 | 121.6815 | 121.7136 | 62.2847 | -121.9784 | 121.7647 | 121.8921 | 121.9182 | 62.3661 | -122.1055
276.1875 | 122.2504 | -62.3108 | 59.7473 | 1.4211e-13 | -0.025886 | -0.003874 | 0.066648 | -0.0047176 | 0.058591 | -0.0054937 | 0.00078395 | -0.0019016 | -0.0030124 | 0.018637 | -0.0093858 | -62.2833 | -0.003172 | -62.2547 | 59.6627 | 59.4027 | 59.4349 | -62.2265 | -62.1504 | 0.091933 | -62.3589 | 59.4996 | 59.618 | 59.6395 | -62.3582 | 0.084254 | -0.084576 | 0.02745 | 0.056079 | -0.028175 | -0.34457 | -0.31245 | -0.047432 | -0.24767 | 0.16043 | -0.048065 | -0.000633 | -0.12936 | -0.10784 | 121.9735 | 121.7135 | 121.7457 | 62.3076 | -121.9739 | 121.8104 | 121.9287 | 121.9503 | 62.4027 | -122.1055
277.875 | 122.2641 | -62.2925 | 59.7702 | 1.4211e-13 | -0.025459 | -0.0043014 | 0.066434 | -0.0047176 | 0.058804 | -0.013124 | 0.00078395 | -0.0019016 | -0.0030124 | 0.01885 | -0.0093858 | -62.2833 | 0.001407 | -62.2684 | 59.6627 | 59.4119 | 59.444 | -62.2311 | -62.1458 | 0.078197 | -62.3634 | 59.4996 | 59.6134 | 59.6395 | -62.3628 | 0.061364 | -0.10747 | 0.009139 | 0.024034 | -0.03733 | -0.3583 | -0.32618 | -0.070322 | -0.27056 | 0.1467 | -0.070955 | -0.000633 | -0.15683 | -0.13073 | 121.9552 | 121.7044 | 121.7365 | 62.2939 | -122.0013 | 121.7921 | 121.9059 | 121.932 | 62.3707 | -122.133
279.625 | 122.3602 | -62.2604 | 59.7382 | 1.4211e-13 | -0.025886 | -0.003874 | 0.066434 | -0.0049314 | 0.058591 | 0.0021363 | 0.00078395 | -0.0019016 | -0.0030124 | 0.01885 | -0.0087448 | -62.2788 | 0.001407 | -62.2501 | 59.6673 | 59.4073 | 59.444 | -62.2357 | -62.1549 | 0.078197 | -62.3589 | 59.5042 | 59.618 | 59.612 | -62.3628 | 0.024742 | -0.070843 | -0.018326 | 0.010304 | -0.014438 | -0.33083 | -0.29413 | -0.10236 | -0.23394 | 0.1055 | -0.098419 | 0.003946 | -0.12021 | -0.12616 | 121.9278 | 121.6678 | 121.7045 | 62.2618 | -121.9739 | 121.7647 | 121.8784 | 121.8724 | 62.3386 | -122.101
281.375 | 122.3785 | -62.2238 | 59.7748 | 1.4211e-13 | -0.025886 | -0.0040876 | 0.066648 | -0.0049314 | 0.058591 | -0.013124 | 0.00035675 | -0.0019016 | -0.0034396 | 0.01885 | -0.0091722 | -62.2971 | -0.003172 | -62.2593 | 59.6719 | 59.3982 | 59.4394 | -62.2311 | -62.0267 | 0.087354 | -62.3634 | 59.5088 | 59.6134 | 59.6349 | -62.3628 | -0.0073 | -0.10289 | -0.07326 | -0.035474 | -0.028174 | -0.37661 | -0.33533 | -0.13899 | -0.26598 | 0.19708 | -0.13962 | -0.000633 | -0.16141 | -0.13989 | 121.8957 | 121.622 | 121.6633 | 62.2206 | -122.0059 | 121.7326 | 121.8372 | 121.8587 | 62.3112 | -122.1376
283.1094 | 122.3282 | -62.3062 | 59.7244 | 1.4211e-13 | -0.025886 | -0.0040876 | 0.06622 | -0.005145 | 0.058804 | 0.0021363 | 0.00057035 | -0.0019016 | -0.0030124 | 0.01885 | -0.0089584 | -62.2833 | 0.005985 | -62.2639 | 59.6673 | 59.4073 | 59.4532 | -62.2311 | -61.9947 | 0.087354 | -62.3589 | 59.4996 | 59.6088 | 59.6349 | -62.3582 | 0.075097 | -0.05711 | 0.022872 | 0.042345 | -0.032752 | -0.3171 | -0.27124 | -0.05201 | -0.22479 | 0.31153 | -0.052643 | -0.000633 | -0.11563 | -0.089535 | 121.9735 | 121.7135 | 121.7594 | 62.3122 | -121.9555 | 121.8059 | 121.915 | 121.9411 | 62.3936 | -122.0826
284.8594 | 122.2458 | -62.3062 | 59.7977 | 1.4211e-13 | -0.025673 | -0.003874 | 0.06622 | -0.0049314 | 0.059018 | 0.0021363 | 0.0012114 | -0.0019016 | -0.0027988 | 0.018637 | -0.0093858 | -62.2833 | 0.001407 | -62.2547 | 59.6627 | 59.4119 | 59.444 | -62.2357 | -62.0725 | 0.087354 | -62.3543 | 59.4951 | 59.6134 | 59.644 | -62.3628 | 0.070518 | -0.13493 | 0.022872 | 0.051501 | -0.019017 | -0.38576 | -0.35364 | -0.056589 | -0.30261 | 0.23369 | -0.048064 | 0.008525 | -0.18429 | -0.15362 | 121.969 | 121.7181 | 121.7502 | 62.3076 | -122.0334 | 121.8013 | 121.9196 | 121.9503 | 62.3936 | -122.1605
286.5469 | 122.3099 | -62.2925 | 59.7336 | 1.4211e-13 | -0.026314 | -0.0036602 | 0.066007 | -0.0049314 | 0.059018 | -0.013124 | 0.00035675 | -0.0019016 | -0.0030124 | 0.019278 | -0.0091722 | -62.2788 | 0.010564 | -62.2593 | 59.6673 | 59.4027 | 59.4349 | -62.2311 | -62.1275 | 0.082776 | -62.3634 | 59.5042 | 59.6134 | 59.6349 | -62.3582 | 0.061364 | -0.066266 | 0.013717 | 0.03319 | -0.028174 | -0.33084 | -0.29871 | -0.065743 | -0.22936 | 0.16501 | -0.070955 | -0.005212 | -0.12021 | -0.098691 | 121.9598 | 121.6952 | 121.7273 | 62.303 | -121.9647 | 121.7967 | 121.9059 | 121.9274 | 62.3753 | -122.0918
288.2969 | 122.2778 | -62.265 | 59.7794 | 1.4211e-13 | -0.0261 | -0.0043014 | 0.06622 | -0.0047176 | 0.058804 | -0.0054937 | 0.00057035 | -0.0016878 | -0.0030124 | 0.01885 | -0.0093858 | -62.2788 | 0.001407 | -62.2593 | 59.6673 | 59.4027 | 59.4486 | -62.2311 | -62.2511 | 0.091933 | -62.3589 | 59.5042 | 59.618 | 59.644 | -62.3628 | 0.033899 | -0.11204 | -0.013748 | 0.005725 | -0.028174 | -0.37661 | -0.33075 | -0.097787 | -0.27514 | 0.013923 | -0.093841 | 0.003946 | -0.1614 | -0.13531 | 121.9323 | 121.6678 | 121.7136 | 62.2664 | -122.0105 | 121.7692 | 121.883 | 121.9091 | 62.3569 | -122.1422
290.0625 | 122.3557 | -62.2787 | 59.7748 | 1.4211e-13 | -0.025673 | -0.0040876 | 0.066007 | -0.0049314 | 0.058804 | 0.0021363 | 0.00078395 | -0.0019016 | -0.0030124 | 0.019064 | -0.0091722 | -62.2879 | 0.010564 | -62.2639 | 59.6582 | 59.4027 | 59.444 | -62.2265 | -62.2557 | 0.091933 | -62.3634 | 59.5042 | 59.6225 | 59.6395 | -62.3628 | 0.052211 | -0.11662 | -0.009171 | 0.01488 | -0.037331 | -0.37203 | -0.33075 | -0.084054 | -0.27056 | 0.023078 | -0.084687 | -0.000633 | -0.15225 | -0.13531 | 121.9369 | 121.6815 | 121.7228 | 62.2893 | -122.0013 | 121.783 | 121.9013 | 121.9182 | 62.3707 | -122.1376
291.75 | 122.2137 | -62.2787 | 59.8434 | 1.4211e-13 | -0.0261 | -0.003874 | 0.06622 | -0.0049314 | 0.058804 | 0.0021363 | 0.00078395 | -0.0019016 | -0.003226 | 0.01885 | -0.0093858 | -62.2879 | 0.001407 | -62.2593 | 59.6719 | 59.4027 | 59.4394 | -62.2265 | -62.2602 | 0.091933 | -62.3634 | 59.5042 | 59.6134 | 59.6395 | -62.3582 | 0.052211 | -0.17155 | -0.009171 | 0.019458 | -0.032753 | -0.4407 | -0.404 | -0.079475 | -0.33923 | 0.018499 | -0.084687 | -0.005212 | -0.23007 | -0.20397 | 121.9506 | 121.6815 | 121.7182 | 62.2802 | -122.07 | 121.783 | 121.8921 | 121.9182 | 62.3707 | -122.2017
293.5 | 122.2092 | -62.2879 | 59.8389 | 1.4211e-13 | -0.025886 | -0.004515 | 0.066007 | -0.004504 | 0.058591 | -0.0054937 | 0.00078395 | -0.0019016 | -0.003226 | 0.01885 | -0.0093858 | -62.2925 | 0.005985 | -62.2501 | 59.6673 | 59.3982 | 59.444 | -62.2357 | -62.2557 | 0.087354 | -62.368 | 59.5042 | 59.6225 | 59.6303 | -62.3765 | 0.052208 | -0.17155 | -0.004595 | 0.03777 | -0.014438 | -0.4407 | -0.39484 | -0.088635 | -0.33465 | 0.032233 | -0.08011 | 0.008525 | -0.21633 | -0.20855 | 121.9552 | 121.6861 | 121.7319 | 62.2939 | -122.0746 | 121.7921 | 121.9104 | 121.9182 | 62.3753 | -122.2154
295.25 | 122.3465 | -62.2787 | 59.761 | 1.4211e-13 | -0.025886 | -0.0040876 | 0.066007 | -0.0049314 | 0.058591 | -0.0054937 | 0.00035675 | -0.0019016 | -0.003226 | 0.01885 | -0.0095994 | -62.2879 | 0.001407 | -62.2547 | 59.6627 | 59.4027 | 59.4349 | -62.2357 | -62.2602 | 0.087354 | -62.3589 | 59.5088 | 59.6271 | 59.644 | -62.3628 | 0.043053 | -0.098309 | -0.009171 | 0.024036 | -0.019017 | -0.3583 | -0.32618 | -0.084054 | -0.25225 | 0.018499 | -0.080108 | 0.003946 | -0.13394 | -0.117 | 121.9415 | 121.6815 | 121.7136 | 62.2802 | -121.9967 | 121.7875 | 121.9059 | 121.9228 | 62.3661 | -122.1238
296.9219 | 122.2916 | -62.2879 | 59.7656 | 1.4211e-13 | -0.026314 | -0.0043014 | 0.06622 | -0.005145 | 0.059018 | 0.0021363 | 0.00057035 | -0.0021152 | -0.0030124 | 0.019278 | -0.0091722 | -62.2833 | 0.005985 | -62.2547 | 59.6627 | 59.4119 | 59.4486 | -62.2311 | -62.2557 | 0.096512 | -62.3543 | 59.4996 | 59.6134 | 59.644 | -62.3628 | 0.056787 | -0.10289 | 0.004562 | 0.033191 | -0.023596 | -0.35372 | -0.31702 | -0.074899 | -0.26599 | 0.032233 | -0.066374 | 0.008525 | -0.15225 | -0.12158 | 121.9506 | 121.6998 | 121.7365 | 62.2939 | -121.9967 | 121.7875 | 121.9013 | 121.932 | 62.3844 | -122.1284
298.6719 | 122.2183 | -62.2833 | 59.816 | 1.4211e-13 | -0.025673 | -0.0040876 | 0.06622 | -0.0047176 | 0.058804 | -0.013124 | 0.00099775 | -0.0016878 | -0.0030124 | 0.019278 | -0.0093858 | -62.2879 | 0.005985 | -62.2639 | 59.6719 | 59.4027 | 59.4486 | -62.2265 | -62.2602 | 0.078197 | -62.3589 | 59.5088 | 59.6134 | 59.6395 | -62.3674 | 0.056788 | -0.14408 | -0.004594 | 0.019457 | -0.037331 | -0.41323 | -0.36737 | -0.084055 | -0.30718 | 0.023076 | -0.075531 | 0.008524 | -0.2026 | -0.17651 | 121.9552 | 121.6861 | 121.7319 | 62.2893 | -122.0425 | 121.7921 | 121.8967 | 121.9228 | 62.3615 | -122.1834
300.4062 | 122.3648 | -62.2742 | 59.7748 | 1.4211e-13 | -0.0261 | -0.0036602 | 0.06622 | -0.005145 | 0.059018 | -0.0054937 | 0.00057035 | -0.0019016 | -0.003226 | 0.01885 | -0.0093858 | -62.2833 | -0.003172 | -62.2593 | 59.6673 | 59.3982 | 59.4486 | -62.2449 | -62.2557 | 0.091933 | -62.3543 | 59.4951 | 59.618 | 59.644 | -62.3674 | 0.029317 | -0.10746 | -0.009171 | 0.01488 | -0.014437 | -0.37661 | -0.32618 | -0.09321 | -0.27972 | 0.0185 | -0.080107 | 0.013103 | -0.15683 | -0.13073 | 121.9415 | 121.6723 | 121.7228 | 62.271 | -122.0196 | 121.7692 | 121.8921 | 121.9182 | 62.3661 | -122.1422
302.1406 | 122.3007 | -62.2833 | 59.7748 | 1.4211e-13 | -0.025886 | -0.003874 | 0.066007 | -0.0047176 | 0.058591 | -0.013124 | 0.00035675 | -0.0016878 | -0.0030124 | 0.019278 | -0.0093858 | -62.2833 | 0.010564 | -62.2593 | 59.6582 | 59.4073 | 59.444 | -62.2311 | -62.2602 | 0.087354 | -62.3589 | 59.4996 | 59.618 | 59.6532 | -62.3628 | 0.052209 | -0.11662 | -1.6e-05 | 0.024035 | -0.028174 | -0.36745 | -0.33075 | -0.079477 | -0.27514 | 0.023076 | -0.075531 | 0.003946 | -0.15683 | -0.12157 | 121.9415 | 121.6907 | 121.7274 | 62.2939 | -122.0059 | 121.783 | 121.9013 | 121.9365 | 62.3707 | -122.1376
303.8281 | 122.3373 | -62.2787 | 59.7382 | 1.4211e-13 | -0.0261 | -0.0040876 | 0.066007 | -0.005145 | 0.058804 | -0.013124 | 0.00057035 | -0.0019016 | -0.0030124 | 0.019064 | -0.0095994 | -62.2788 | 0.005985 | -62.2547 | 59.6673 | 59.4027 | 59.444 | -62.2265 | -62.2602 | 0.082776 | -62.3589 | 59.5088 | 59.6225 | 59.644 | -62.3628 | 0.052211 | -0.070843 | -1.5e-05 | 0.024036 | -0.028175 | -0.33541 | -0.29413 | -0.084054 | -0.22936 | 0.018499 | -0.080108 | 0.003946 | -0.11563 | -0.094111 | 121.9461 | 121.6815 | 121.7228 | 62.2847 | -121.9647 | 121.7875 | 121.9013 | 121.9228 | 62.3615 | -122.101
305.5781 | 122.2778 | -62.2879 | 59.7473 | 1.4211e-13 | -0.026314 | -0.003874 | 0.06622 | -0.0049314 | 0.058591 | 0.0021363 | 0.00057035 | -0.0016878 | -0.0030124 | 0.019278 | -0.0091722 | -62.2833 | 0.005985 | -62.2593 | 59.6673 | 59.4073 | 59.444 | -62.2403 | -62.2648 | 0.087354 | -62.3543 | 59.5088 | 59.618 | 59.6486 | -62.3628 | 0.047629 | -0.079998 | 0.004562 | 0.028613 | -0.019016 | -0.33999 | -0.30329 | -0.074899 | -0.23852 | 0.023075 | -0.066374 | 0.008525 | -0.12936 | -0.098687 | 121.9552 | 121.6952 | 121.7319 | 62.2939 | -121.9876 | 121.7967 | 121.9059 | 121.9365 | 62.3753 | -122.1101
307.2656 | 122.2641 | -62.2971 | 59.761 | 1.4211e-13 | -0.025886 | -0.004515 | 0.06622 | -0.0049314 | 0.058591 | 0.0021363 | 0.00078395 | -0.0014742 | -0.0027988 | 0.01885 | -0.0091722 | -62.2788 | 0.010564 | -62.2593 | 59.6627 | 59.4073 | 59.444 | -62.2357 | -62.2602 | 0.091933 | -62.3589 | 59.5134 | 59.618 | 59.6486 | -62.3674 | 0.061363 | -0.098309 | 0.018295 | 0.037768 | -0.023595 | -0.35372 | -0.31702 | -0.070322 | -0.24767 | 0.036809 | -0.061798 | 0.008524 | -0.14309 | -0.11242 | 121.9598 | 121.7044 | 121.7411 | 62.3076 | -121.9967 | 121.8104 | 121.915 | 121.9457 | 62.389 | -122.1284
309 | 122.2687 | -62.2879 | 59.7748 | 1.4211e-13 | -0.025886 | -0.0040876 | 0.066007 | -0.005145 | 0.058591 | 0.0021363 | 0.00057035 | -0.0019016 | -0.003226 | 0.019064 | -0.0091722 | -62.2833 | 0.010564 | -62.2593 | 59.6719 | 59.3982 | 59.4394 | -62.2357 | -62.2602 | 0.082776 | -62.3634 | 59.5042 | 59.6134 | 59.644 | -62.372 | 0.052208 | -0.10289 | 0.004562 | 0.028613 | -0.023595 | -0.37661 | -0.33533 | -0.084056 | -0.27056 | 0.027654 | -0.075532 | 0.008524 | -0.16141 | -0.13073 | 121.9598 | 121.6861 | 121.7274 | 62.2985 | -122.0105 | 121.7921 | 121.9013 | 121.932 | 62.3707 | -122.1467
310.75 | 122.2366 | -62.2879 | 59.7977 | 1.4211e-13 | -0.026314 | -0.0040876 | 0.066007 | -0.004504 | 0.058804 | -0.013124 | 0.00099775 | -0.0016878 | -0.003226 | 0.019278 | -0.0091722 | -62.2833 | 0.005985 | -62.2639 | 59.6627 | 59.4073 | 59.444 | -62.2357 | -62.2511 | 0.087354 | -62.368 | 59.4996 | 59.6134 | 59.644 | -62.3628 | 0.052208 | -0.13493 | 0.004562 | 0.024035 | -0.028173 | -0.39034 | -0.35364 | -0.074899 | -0.29803 | 0.036811 | -0.08011 | -0.005211 | -0.18429 | -0.15362 | 121.9506 | 121.6952 | 121.7319 | 62.2939 | -122.0334 | 121.7875 | 121.9013 | 121.932 | 62.3753 | -122.1605
312.5 | 122.3053 | -62.2925 | 59.761 | 1.4211e-13 | -0.0261 | -0.0040876 | 0.066007 | -0.0047176 | 0.058591 | -0.020755 | 0.00057035 | -0.0016878 | -0.0030124 | 0.019064 | -0.0093858 | -62.2879 | 0.015142 | -62.2593 | 59.6582 | 59.4073 | 59.444 | -62.2357 | -62.2602 | 0.082776 | -62.3543 | 59.4996 | 59.618 | 59.6486 | -62.3674 | 0.056785 | -0.10289 | 0.004561 | 0.03319 | -0.023595 | -0.35372 | -0.31702 | -0.0749 | -0.26141 | 0.032231 | -0.061797 | 0.013103 | -0.14309 | -0.11242 | 121.9506 | 121.6998 | 121.7365 | 62.3076 | -121.9967 | 121.7921 | 121.9104 | 121.9411 | 62.3753 | -122.1284
314.1875 | 122.3465 | -62.2925 | 59.7519 | 1.4211e-13 | -0.026314 | -0.003874 | 0.06622 | -0.0049314 | 0.058591 | -0.013124 | 0.00099775 | -0.0016878 | -0.0030124 | 0.019278 | -0.0091722 | -62.2879 | 0.015142 | -62.2547 | 59.6627 | 59.4073 | 59.4486 | -62.2357 | -62.2557 | 0.087354 | -62.3543 | 59.5042 | 59.6134 | 59.644 | -62.3628 | 0.056785 | -0.089154 | 0.004561 | 0.037768 | -0.019017 | -0.34457 | -0.30329 | -0.070322 | -0.24767 | 0.03681 | -0.061797 | 0.008525 | -0.13852 | -0.10784 | 121.9552 | 121.6998 | 121.7411 | 62.3076 | -121.9876 | 121.7967 | 121.9059 | 121.9365 | 62.3798 | -122.1147
315.9219 | 122.2046 | -62.2833 | 59.816 | 1.4211e-13 | -0.026314 | -0.0043014 | 0.065793 | -0.005145 | 0.058591 | -0.0054937 | 0.00035675 | -0.0019016 | -0.0030124 | 0.019278 | -0.0091722 | -62.2925 | 0.019721 | -62.2593 | 59.6627 | 59.4027 | 59.4486 | -62.2357 | -62.2557 | 0.078197 | -62.3589 | 59.5042 | 59.618 | 59.6486 | -62.372 | 0.04763 | -0.15324 | -0.009173 | 0.024035 | -0.023595 | -0.41323 | -0.36737 | -0.088634 | -0.31176 | 0.027655 | -0.075531 | 0.013103 | -0.19803 | -0.16735 | 121.9461 | 121.6861 | 121.7319 | 62.303 | -122.0517 | 121.7875 | 121.9013 | 121.932 | 62.3615 | -122.1879
317.5938 | 122.319 | -62.2971 | 59.729 | 1.4211e-13 | -0.026314 | -0.0040876 | 0.06622 | -0.0047176 | 0.058591 | 0.0021363 | 0.00057035 | -0.0019016 | -0.003226 | 0.019064 | -0.0095994 | -62.2833 | 0.019721 | -62.2501 | 59.6765 | 59.4073 | 59.4486 | -62.2265 | -62.2602 | 0.087354 | -62.3589 | 59.5042 | 59.618 | 59.644 | -62.3628 | 0.070521 | -0.052531 | 0.013717 | 0.046925 | -0.023596 | -0.32168 | -0.2804 | -0.065744 | -0.22479 | 0.036809 | -0.061798 | 0.003946 | -0.11105 | -0.084956 | 121.9735 | 121.7044 | 121.7457 | 62.3168 | -121.9555 | 121.8013 | 121.915 | 121.9411 | 62.3844 | -122.0918
319.2812 | 122.3053 | -62.2925 | 59.7519 | 1.4211e-13 | -0.026314 | -0.0040876 | 0.06622 | -0.0049314 | 0.058804 | 0.0021363 | 0.00099775 | -0.0023288 | -0.0030124 | 0.019278 | -0.0093858 | -62.2879 | 0.015142 | -62.2547 | 59.6582 | 59.4027 | 59.4532 | -62.2311 | -62.2557 | 0.091933 | -62.3497 | 59.5042 | 59.6134 | 59.644 | -62.3674 | 0.061364 | -0.093733 | 0.004561 | 0.037768 | -0.023596 | -0.34915 | -0.29871 | -0.0749 | -0.24767 | 0.03681 | -0.057219 | 0.017681 | -0.13852 | -0.10784 | 121.9506 | 121.6952 | 121.7457 | 62.3076 | -121.983 | 121.7967 | 121.9059 | 121.9365 | 62.3844 | -122.1193
321 | 122.2687 | -62.2696 | 59.8114 | 1.4211e-13 | -0.026527 | -0.003874 | 0.066007 | -0.0049314 | 0.058377 | -0.0054937 | 0.00057035 | -0.0019016 | -0.003226 | 0.019491 | -0.0093858 | -62.2879 | 0.010564 | -62.2593 | 59.6627 | 59.4027 | 59.444 | -62.222 | -62.2511 | 0.082776 | -62.3543 | 59.5088 | 59.6225 | 59.6303 | -62.3582 | 0.047634 | -0.14866 | -0.018327 | 0.010302 | -0.037332 | -0.40865 | -0.36737 | -0.088631 | -0.3026 | 0.0185 | -0.084685 | 0.003946 | -0.18887 | -0.18109 | 121.9323 | 121.6723 | 121.7136 | 62.2802 | -122.0334 | 121.7784 | 121.8921 | 121.8999 | 62.3524 | -122.1696
322.75 | 122.287 | -62.2787 | 59.7565 | 1.4211e-13 | -0.026314 | -0.0040876 | 0.066007 | -0.0049314 | 0.058591 | 0.0097668 | 0.00057035 | -0.0016878 | -0.003226 | 0.019064 | -0.0095994 | -62.2788 | 0.010564 | -62.2593 | 59.6673 | 59.4119 | 59.4486 | -62.2311 | -62.2511 | 0.087354 | -62.3543 | 59.5042 | 59.6225 | 59.6395 | -62.372 | 0.047632 | -0.089154 | -1.5e-05 | 0.019458 | -0.028174 | -0.34457 | -0.30787 | -0.093211 | -0.25225 | 0.027656 | -0.075529 | 0.017682 | -0.13394 | -0.117 | 121.9461 | 121.6907 | 121.7274 | 62.2893 | -121.9876 | 121.783 | 121.9013 | 121.9182 | 62.3661 | -122.1284
324.4844 | 122.374 | -62.2559 | 59.7931 | 1.4211e-13 | -0.026955 | -0.0040876 | 0.06622 | -0.0047176 | 0.058591 | 0.0021363 | 0.00057035 | -0.0016878 | -0.0027988 | 0.019491 | -0.0091722 | -62.2833 | 0.010564 | -62.2593 | 59.6582 | 59.4073 | 59.444 | -62.2311 | -62.2648 | 0.096512 | -62.3543 | 59.4996 | 59.6271 | 59.644 | -62.3674 | 0.024743 | -0.13493 | -0.027482 | -0.003431 | -0.028174 | -0.38576 | -0.34906 | -0.11152 | -0.29345 | -0.008969 | -0.098418 | 0.013103 | -0.16598 | -0.14904 | 121.914 | 121.6632 | 121.6999 | 62.2664 | -122.0242 | 121.7555 | 121.883 | 121.8999 | 62.3524 | -122.1605
326.2188 | 122.3602 | -62.2467 | 59.7839 | 1.4211e-13 | -0.026314 | -0.003874 | 0.066007 | -0.0047176 | 0.058591 | 0.0021363 | 0.00099775 | -0.0016878 | -0.0030124 | 0.019491 | -0.0095994 | -62.2833 | 0.005985 | -62.2456 | 59.6673 | 59.4073 | 59.444 | -62.2311 | -62.2511 | 0.091933 | -62.3497 | 59.5088 | 59.6225 | 59.6395 | -62.3674 | 0.015588 | -0.11662 | -0.036637 | 0.001149 | -0.014439 | -0.37661 | -0.33991 | -0.12068 | -0.27514 | -0.004388 | -0.10299 | 0.017681 | -0.1614 | -0.14447 | 121.914 | 121.654 | 121.6907 | 62.2527 | -122.0151 | 121.7555 | 121.8692 | 121.8862 | 62.3386 | -122.1513
327.9531 | 122.319 | -62.2879 | 59.7382 | 1.4211e-13 | -0.026314 | -0.0040876 | 0.06622 | -0.0049314 | 0.058377 | 0.0021363 | 0.00057035 | -0.0016878 | -0.0034396 | 0.019064 | -0.0095994 | -62.2788 | 0.005985 | -62.2593 | 59.6673 | 59.4073 | 59.4532 | -62.2311 | -62.2602 | 0.087354 | -62.3497 | 59.5042 | 59.6225 | 59.644 | -62.3628 | 0.056787 | -0.070843 | 0.00914 | 0.028613 | -0.028174 | -0.33083 | -0.28498 | -0.074899 | -0.23394 | 0.027654 | -0.061796 | 0.013103 | -0.11563 | -0.094111 | 121.9552 | 121.6952 | 121.7411 | 62.2939 | -121.9693 | 121.7921 | 121.9104 | 121.932 | 62.3753 | -122.101
329.6406 | 122.2183 | -62.3016 | 59.7977 | 1.4211e-13 | -0.026527 | -0.0040876 | 0.065793 | -0.0047176 | 0.058591 | 0.0021363 | 0.00057035 | -0.0019016 | -0.0030124 | 0.019491 | -0.0091722 | -62.2833 | 0.010564 | -62.2593 | 59.6627 | 59.3982 | 59.4532 | -62.2265 | -62.2557 | 0.087354 | -62.3497 | 59.4996 | 59.6271 | 59.6349 | -62.3674 | 0.075099 | -0.13493 | 0.018295 | 0.042346 | -0.032753 | -0.3995 | -0.34448 | -0.065744 | -0.29803 | 0.045966 | -0.048063 | 0.017681 | -0.17056 | -0.16278 | 121.9644 | 121.6998 | 121.7548 | 62.3122 | -122.0242 | 121.8013 | 121.9287 | 121.9365 | 62.389 | -122.165
331.375 | 122.1954 | -62.2833 | 59.8068 | 1.4211e-13 | -0.026314 | -0.003874 | 0.066007 | -0.005145 | 0.058591 | -0.013124 | 0.00057035 | -0.0016878 | -0.0030124 | 0.019491 | -0.0095994 | -62.2879 | 0.001407 | -62.2684 | 59.6719 | 59.4073 | 59.444 | -62.2357 | -62.2511 | 0.087354 | -62.3543 | 59.5088 | 59.6225 | 59.644 | -62.3765 | 0.04763 | -0.13493 | -0.004594 | 0.014879 | -0.032751 | -0.3995 | -0.3628 | -0.093213 | -0.29803 | 0.032233 | -0.070952 | 0.022261 | -0.18429 | -0.16278 | 121.9552 | 121.6907 | 121.7274 | 62.2847 | -122.0425 | 121.7921 | 121.9059 | 121.9274 | 62.3707 | -122.1834
333.0469 | 122.287 | -62.2604 | 59.7794 | 1.4211e-13 | -0.026314 | -0.003874 | 0.066434 | -0.0049314 | 0.058591 | 0.0021363 | 0.00057035 | -0.0021152 | -0.003226 | 0.019278 | -0.0095994 | -62.2742 | 0.010564 | -62.2593 | 59.6673 | 59.4073 | 59.4486 | -62.2357 | -62.2557 | 0.082776 | -62.3543 | 59.5088 | 59.618 | 59.6532 | -62.372 | 0.024742 | -0.11204 | -0.013747 | 0.001147 | -0.023595 | -0.37203 | -0.33075 | -0.11152 | -0.27056 | 0.004767 | -0.09384 | 0.017682 | -0.1614 | -0.12615 | 121.9278 | 121.6678 | 121.709 | 62.271 | -122.0151 | 121.7692 | 121.8784 | 121.9136 | 62.3432 | -122.1513
334.8125 | 122.2961 | -62.2879 | 59.7702 | 1.4211e-13 | -0.026527 | -0.003874 | 0.06622 | -0.0049314 | 0.058591 | -0.0054937 | 0.00035675 | -0.0016878 | -0.003226 | 0.019278 | -0.0095994 | -62.2833 | 0.010564 | -62.2639 | 59.6719 | 59.4073 | 59.444 | -62.2311 | -62.2557 | 0.082776 | -62.3589 | 59.5088 | 59.6225 | 59.6486 | -62.3674 | 0.056787 | -0.098309 | 0.004562 | 0.024035 | -0.032752 | -0.36288 | -0.32618 | -0.079477 | -0.26141 | 0.032233 | -0.070953 | 0.008524 | -0.14767 | -0.12158 | 121.9598 | 121.6952 | 121.7319 | 62.2985 | -122.0013 | 121.7967 | 121.9104 | 121.9365 | 62.3707 | -122.1376
336.4844 | 122.1954 | -62.2833 | 59.8251 | 1.4211e-13 | -0.026955 | -0.003874 | 0.06622 | -0.0047176 | 0.058377 | -0.0054937 | 0.00057035 | -0.0016878 | -0.0030124 | 0.019064 | -0.0095994 | -62.2925 | 0.005985 | -62.2593 | 59.6673 | 59.4073 | 59.4532 | -62.2357 | -62.2557 | 0.087354 | -62.3543 | 59.5088 | 59.6225 | 59.6395 | -62.372 | 0.04763 | -0.15782 | -0.009173 | 0.024035 | -0.023595 | -0.41781 | -0.37195 | -0.088634 | -0.31634 | 0.027655 | -0.070952 | 0.017682 | -0.2026 | -0.18566 | 121.9506 | 121.6907 | 121.7365 | 62.2893 | -122.0608 | 121.7921 | 121.9059 | 121.9228 | 62.3707 | -122.1971
338.1719 | 122.2092 | -62.3108 | 59.7839 | 1.4211e-13 | -0.026741 | -0.0040876 | 0.066007 | -0.0049314 | 0.058163 | 0.0021363 | 0.00057035 | -0.0019016 | -0.003226 | 0.019278 | -0.0095994 | -62.2833 | 0.019721 | -62.2639 | 59.6673 | 59.4027 | 59.4486 | -62.2357 | -62.2557 | 0.087354 | -62.3543 | 59.5042 | 59.6225 | 59.6395 | -62.3674 | 0.075096 | -0.11662 | 0.02745 | 0.046923 | -0.028173 | -0.38119 | -0.33533 | -0.056589 | -0.27972 | 0.055121 | -0.043486 | 0.013103 | -0.1614 | -0.14447 | 121.9781 | 121.7135 | 121.7594 | 62.3305 | -122.0196 | 121.815 | 121.9333 | 121.9503 | 62.3981 | -122.1513
339.9219 | 122.3236 | -62.2742 | 59.7153 | 1.4211e-13 | -0.026741 | -0.0043014 | 0.066007 | -0.0049314 | 0.058804 | 0.0021363 | 0.00035675 | -0.0021152 | -0.003226 | 0.019491 | -0.0095994 | -62.2788 | 0.010564 | -62.2547 | 59.6719 | 59.4073 | 59.4532 | -62.2357 | -62.2557 | 0.091933 | -62.3589 | 59.5042 | 59.6225 | 59.6395 | -62.3628 | 0.038475 | -0.043377 | -0.004593 | 0.019458 | -0.019017 | -0.30795 | -0.26209 | -0.088632 | -0.21105 | 0.0185 | -0.084686 | 0.003946 | -0.092738 | -0.075801 | 121.9461 | 121.6815 | 121.7274 | 62.2847 | -121.951 | 121.7784 | 121.8967 | 121.9136 | 62.3661 | -122.0781
341.6719 | 122.2229 | -62.2742 | 59.7885 | 1.4211e-13 | -0.026955 | -0.003874 | 0.066007 | -0.005145 | 0.058163 | -0.0054937 | 0.00078395 | -0.0021152 | -0.003226 | 0.019278 | -0.0091722 | -62.2879 | 0.005985 | -62.2547 | 59.6627 | 59.4073 | 59.4486 | -62.2357 | -62.2511 | 0.087354 | -62.3543 | 59.5042 | 59.6134 | 59.6395 | -62.372 | 0.038475 | -0.12578 | -0.013749 | 0.019458 | -0.019017 | -0.38119 | -0.33991 | -0.097789 | -0.28429 | 0.023078 | -0.080107 | 0.017682 | -0.17514 | -0.14904 | 121.9369 | 121.6815 | 121.7228 | 62.2802 | -122.0242 | 121.7784 | 121.8875 | 121.9136 | 62.3615 | -122.1605
343.4062 | 122.2183 | -62.3062 | 59.7931 | 1.4211e-13 | -0.026955 | -0.0043014 | 0.06622 | -0.005145 | 0.058163 | -0.0054937 | 0.00057035 | -0.0021152 | -0.0034396 | 0.019278 | -0.0095994 | -62.2833 | 0.015142 | -62.2639 | 59.6673 | 59.4027 | 59.4486 | -62.2403 | -62.2557 | 0.087354 | -62.3543 | 59.4996 | 59.6225 | 59.6166 | -62.372 | 0.065939 | -0.12577 | 0.022872 | 0.042345 | -0.023594 | -0.39034 | -0.34449 | -0.065746 | -0.29345 | 0.050543 | -0.048064 | 0.017682 | -0.17056 | -0.17651 | 121.9735 | 121.709 | 121.7548 | 62.3214 | -122.0334 | 121.8059 | 121.9287 | 121.9228 | 62.3936 | -122.165
345.1562 | 122.2 | -62.3108 | 59.816 | 1.4211e-13 | -0.026527 | -0.0043014 | 0.066007 | -0.0049314 | 0.058163 | 0.017397 | 0.00057035 | -0.0021152 | -0.003226 | 0.019491 | -0.0093858 | -62.2879 | 0.010564 | -62.2593 | 59.6627 | 59.4119 | 59.4486 | -62.2357 | -62.2557 | 0.087354 | -62.3589 | 59.5088 | 59.618 | 59.6395 | -62.3674 | 0.075096 | -0.15324 | 0.022872 | 0.051501 | -0.023595 | -0.40407 | -0.36737 | -0.056589 | -0.30718 | 0.055121 | -0.048065 | 0.008524 | -0.19803 | -0.17651 | 121.9735 | 121.7227 | 121.7594 | 62.3214 | -122.0517 | 121.8196 | 121.9287 | 121.9503 | 62.3981 | -122.1834
346.8438 | 122.3328 | -62.2742 | 59.7244 | 1.4211e-13 | -0.026527 | -0.003874 | 0.06622 | -0.0047176 | 0.058377 | -0.0054937 | 0.00057035 | -0.0016878 | -0.003226 | 0.019278 | -0.0093858 | -62.2833 | 0.015142 | -62.2593 | 59.6719 | 59.4073 | 59.4486 | -62.2357 | -62.2602 | 0.082776 | -62.3543 | 59.5134 | 59.6271 | 59.6349 | -62.3674 | 0.038475 | -0.052532 | -0.009171 | 0.01488 | -0.023595 | -0.3171 | -0.27582 | -0.09321 | -0.21105 | 0.013921 | -0.080107 | 0.013103 | -0.097315 | -0.089535 | 121.9461 | 121.6815 | 121.7228 | 62.2893 | -121.9601 | 121.7875 | 121.9013 | 121.9091 | 62.3569 | -122.0918
348.5781 | 122.3419 | -62.2833 | 59.7473 | 1.4211e-13 | -0.026527 | -0.0036602 | 0.066007 | -0.0049314 | 0.058591 | -0.0054937 | 0.00078395 | -0.0023288 | -0.003226 | 0.019705 | -0.0091722 | -62.2879 | 0.010564 | -62.2593 | 59.6719 | 59.4119 | 59.4486 | -62.2357 | -62.2557 | 0.087354 | -62.3589 | 59.5088 | 59.618 | 59.6395 | -62.372 | 0.04763 | -0.07542 | -0.004594 | 0.024035 | -0.023595 | -0.33541 | -0.29871 | -0.088634 | -0.23852 | 0.027655 | -0.075531 | 0.013103 | -0.12936 | -0.10784 | 121.9552 | 121.6952 | 121.7319 | 62.2939 | -121.983 | 121.7921 | 121.9013 | 121.9228 | 62.3707 | -122.1193
350.3281 | 122.3099 | -62.2559 | 59.7794 | 1.4211e-13 | -0.026741 | -0.0043014 | 0.066007 | -0.0049314 | 0.058591 | -0.0054937 | 0.00057035 | -0.0019016 | -0.0030124 | 0.019491 | -0.0095994 | -62.2833 | 0.010564 | -62.2547 | 59.6673 | 59.4073 | 59.4532 | -62.2311 | -62.2602 | 0.091933 | -62.3543 | 59.5042 | 59.618 | 59.644 | -62.3628 | 0.024743 | -0.11204 | -0.027482 | 0.001147 | -0.023596 | -0.37203 | -0.32617 | -0.10694 | -0.27514 | -0.00439 | -0.098418 | 0.008525 | -0.1614 | -0.13531 | 121.9232 | 121.6632 | 121.709 | 62.2664 | -122.0105 | 121.7601 | 121.8738 | 121.8999 | 62.3478 | -122.1422
352.0781 | 122.3145 | -62.2833 | 59.7244 | 1.4211e-13 | -0.026741 | -0.0040876 | 0.065579 | -0.005145 | 0.058377 | -0.0054937 | 0.00035675 | -0.0021152 | -0.0030124 | 0.019705 | -0.0091722 | -62.2879 | 0.005985 | -62.2639 | 59.6719 | 59.4119 | 59.444 | -62.2311 | -62.2557 | 0.082776 | -62.3543 | 59.5042 | 59.6225 | 59.644 | -62.3674 | 0.052209 | -0.052532 | -0.004594 | 0.019457 | -0.032752 | -0.31252 | -0.2804 | -0.084055 | -0.22021 | 0.027655 | -0.070952 | 0.013103 | -0.10189 | -0.080378 | 121.9552 | 121.6952 | 121.7274 | 62.2893 | -121.9555 | 121.7875 | 121.9059 | 121.9274 | 62.3661 | -122.0918
353.7656 | 122.2183 | -62.265 | 59.8297 | 1.4211e-13 | -0.026955 | -0.0040876 | 0.066007 | -0.0049314 | 0.058591 | -0.0054937 | 0.00057035 | -0.0021152 | -0.003226 | 0.019705 | -0.0093858 | -62.2833 | 0.010564 | -62.2639 | 59.6673 | 59.4027 | 59.444 | -62.2357 | -62.2557 | 0.096512 | -62.3497 | 59.4996 | 59.6271 | 59.644 | -62.372 | 0.02932 | -0.1624 | -0.018326 | 0.001147 | -0.028173 | -0.42697 | -0.38569 | -0.10694 | -0.33007 | 0.009345 | -0.084684 | 0.02226 | -0.2026 | -0.18566 | 121.9323 | 121.6678 | 121.709 | 62.2756 | -122.0654 | 121.7647 | 121.8921 | 121.9091 | 62.3615 | -122.2017
355.5156 | 122.3465 | -62.2421 | 59.7748 | 1.4211e-13 | -0.027168 | -0.0040876 | 0.066007 | -0.0049314 | 0.058377 | -0.013124 | 0.00057035 | -0.0021152 | -0.003226 | 0.019278 | -0.0098132 | -62.2833 | 0.015142 | -62.2501 | 59.6627 | 59.4119 | 59.4532 | -62.2311 | -62.2511 | 0.091933 | -62.3497 | 59.5042 | 59.6317 | 59.6395 | -62.3765 | 0.01101 | -0.11204 | -0.041215 | -0.008007 | -0.019017 | -0.36288 | -0.3216 | -0.13441 | -0.27056 | -0.008966 | -0.10757 | 0.026839 | -0.14309 | -0.13531 | 121.9049 | 121.654 | 121.6953 | 62.2573 | -122.0059 | 121.7463 | 121.8738 | 121.8816 | 62.3341 | -122.1513
357.2031 | 122.2504 | -62.2787 | 59.8434 | 1.4211e-13 | -0.026955 | -0.003874 | 0.065793 | -0.005145 | 0.058377 | 0.0097668 | 0.00078395 | -0.0019016 | -0.003226 | 0.019919 | -0.0093858 | -62.2788 | 0.010564 | -62.2593 | 59.6582 | 59.4027 | 59.4532 | -62.2403 | -62.2557 | 0.087354 | -62.3589 | 59.5088 | 59.6317 | 59.6395 | -62.3765 | 0.038474 | -0.18529 | -1.5e-05 | 0.019458 | -0.019016 | -0.4407 | -0.39026 | -0.09779 | -0.33465 | 0.023078 | -0.080108 | 0.017682 | -0.21176 | -0.20397 | 121.9369 | 121.6815 | 121.7319 | 62.2893 | -122.0837 | 121.7875 | 121.9104 | 121.9182 | 62.3661 | -122.22
358.9375 | 122.2046 | -62.265 | 59.8297 | 1.4211e-13 | -0.026527 | -0.004515 | 0.066007 | -0.0049314 | 0.058804 | 0.0021363 | 0.00078395 | -0.0021152 | -0.0030124 | 0.019278 | -0.0095994 | -62.2833 | 0.005985 | -62.2547 | 59.6673 | 59.4027 | 59.4486 | -62.2357 | -62.2602 | 0.096512 | -62.3543 | 59.5088 | 59.6317 | 59.644 | -62.372 | 0.02932 | -0.1624 | -0.018326 | 0.010303 | -0.019017 | -0.42697 | -0.38111 | -0.10694 | -0.32091 | 0.004766 | -0.089262 | 0.017682 | -0.19802 | -0.18566 | 121.9323 | 121.6678 | 121.7136 | 62.271 | -122.0654 | 121.7738 | 121.8967 | 121.9091 | 62.3615 | -122.2017
360.6875 | 122.3007 | -62.2696 | 59.7565 | 1.4211e-13 | -0.026741 | -0.0040876 | 0.066007 | -0.0047176 | 0.058377 | -0.0054937 | 0.00057035 | -0.0019016 | -0.0030124 | 0.019705 | -0.0093858 | -62.2788 | 0.015142 | -62.2684 | 59.6719 | 59.4073 | 59.4532 | -62.2357 | -62.2557 | 0.082776 | -62.3497 | 59.5042 | 59.6225 | 59.644 | -62.3765 | 0.033897 | -0.084576 | -0.009171 | 0.001146 | -0.032751 | -0.34914 | -0.30329 | -0.10695 | -0.25225 | 0.013922 | -0.080107 | 0.026839 | -0.13394 | -0.11242 | 121.9415 | 121.6769 | 121.7228 | 62.2847 | -121.9922 | 121.7738 | 121.8921 | 121.9136 | 62.3524 | -122.133
362.3594 | 122.2137 | -62.3199 | 59.7885 | 1.4211e-13 | -0.026955 | -0.0043014 | 0.065793 | -0.005145 | 0.058591 | -0.0054937 | 0.00057035 | -0.0021152 | -0.0027988 | 0.019491 | -0.0095994 | -62.2833 | 0.010564 | -62.2547 | 59.6719 | 59.4211 | 59.4486 | -62.2403 | -62.2602 | 0.091933 | -62.3543 | 59.4996 | 59.6271 | 59.6395 | -62.3674 | 0.079672 | -0.11662 | 0.036605 | 0.065234 | -0.014438 | -0.36745 | -0.33991 | -0.047434 | -0.28887 | 0.059697 | -0.034331 | 0.013103 | -0.1614 | -0.14904 | 121.9918 | 121.741 | 121.7686 | 62.3305 | -122.0288 | 121.8196 | 121.9471 | 121.9594 | 62.4119 | -122.1559
364.1094 | 122.2 | -62.3016 | 59.816 | 1.4211e-13 | -0.026955 | -0.0040876 | 0.065793 | -0.0049314 | 0.058377 | -0.0054937 | 0.00099775 | -0.0016878 | -0.0027988 | 0.019491 | -0.0095994 | -62.2925 | 0.010564 | -62.2593 | 59.6673 | 59.4119 | 59.4486 | -62.2449 | -62.2557 | 0.087354 | -62.3543 | 59.5134 | 59.6317 | 59.644 | -62.3674 | 0.056783 | -0.14866 | 0.009138 | 0.042346 | -0.014437 | -0.40407 | -0.36737 | -0.065744 | -0.3026 | 0.045966 | -0.052641 | 0.013103 | -0.18429 | -0.17193 | 121.969 | 121.7135 | 121.7502 | 62.3122 | -122.0608 | 121.815 | 121.9333 | 121.9457 | 62.389 | -122.1834
365.7969 | 122.2595 | -62.2879 | 59.8022 | 1.4211e-13 | -0.026955 | -0.0040876 | 0.065793 | -0.0049314 | 0.058377 | -0.013124 | 0.00057035 | -0.0021152 | -0.003226 | 0.019919 | -0.0091722 | -62.2788 | 0.010564 | -62.2593 | 59.6719 | 59.4073 | 59.4486 | -62.2357 | -62.2602 | 0.087354 | -62.3634 | 59.5088 | 59.6225 | 59.6395 | -62.3765 | 0.052208 | -0.13035 | 0.00914 | 0.028613 | -0.023595 | -0.39492 | -0.35364 | -0.088635 | -0.29345 | 0.027654 | -0.075532 | 0.013103 | -0.17971 | -0.16278 | 121.9598 | 121.6952 | 121.7365 | 62.2985 | -122.0379 | 121.7967 | 121.9104 | 121.9274 | 62.3753 | -122.1788
367.5312 | 122.2046 | -62.2971 | 59.8068 | 1.4211e-13 | -0.026955 | -0.0043014 | 0.066007 | -0.005145 | 0.058591 | 0.0021363 | 0.00057035 | -0.0019016 | -0.0027988 | 0.019705 | -0.0093858 | -62.2788 | 0.010564 | -62.2501 | 59.6627 | 59.4119 | 59.4486 | -62.2357 | -62.2602 | 0.091933 | -62.3543 | 59.5134 | 59.6317 | 59.644 | -62.3811 | 0.061363 | -0.14409 | 0.018295 | 0.046925 | -0.014438 | -0.39492 | -0.35822 | -0.084059 | -0.29345 | 0.036809 | -0.057219 | 0.02684 | -0.17513 | -0.16278 | 121.9598 | 121.709 | 121.7457 | 62.3076 | -122.0425 | 121.8104 | 121.9287 | 121.9411 | 62.389 | -122.1879
369.2656 | 122.2137 | -62.2787 | 59.816 | 1.4211e-13 | -0.026955 | -0.003874 | 0.065793 | -0.005145 | 0.058163 | 0.0021363 | 0.00078395 | -0.0019016 | -0.0027988 | 0.019491 | -0.0093858 | -62.2833 | 0.015142 | -62.2547 | 59.6673 | 59.4165 | 59.4578 | -62.2449 | -62.2557 | 0.087354 | -62.3497 | 59.5042 | 59.6317 | 59.644 | -62.3765 | 0.033895 | -0.14866 | -0.004593 | 0.024036 | -0.009859 | -0.3995 | -0.35822 | -0.09779 | -0.31176 | 0.023078 | -0.070951 | 0.026839 | -0.18429 | -0.17193 | 121.9461 | 121.6952 | 121.7365 | 62.2939 | -122.0608 | 121.783 | 121.9104 | 121.9228 | 62.3661 | -122.1925
371 | 122.3328 | -62.2879 | 59.7473 | 1.4211e-13 | -0.026955 | -0.003874 | 0.065579 | -0.0049314 | 0.058804 | -0.013124 | 0.00057035 | -0.0019016 | -0.0030124 | 0.019491 | -0.0095994 | -62.2879 | 0.010564 | -62.2593 | 59.6673 | 59.4073 | 59.4486 | -62.2403 | -62.2602 | 0.087354 | -62.3543 | 59.4996 | 59.6271 | 59.6166 | -62.372 | 0.047629 | -0.079998 | -1.6e-05 | 0.028613 | -0.019016 | -0.33999 | -0.29871 | -0.084056 | -0.24767 | 0.027654 | -0.066374 | 0.017682 | -0.1202 | -0.13074 | 121.9552 | 121.6952 | 121.7365 | 62.2985 | -121.9876 | 121.7875 | 121.915 | 121.9045 | 62.3753 | -122.1193
372.6875 | 122.2275 | -62.2879 | 59.8297 | 1.4211e-13 | -0.027168 | -0.0040876 | 0.066007 | -0.0049314 | 0.058163 | -0.0054937 | 0.00099775 | -0.0016878 | -0.0030124 | 0.019705 | -0.0093858 | -62.2879 | 0.010564 | -62.2547 | 59.6673 | 59.4073 | 59.4486 | -62.2357 | -62.2557 | 0.096512 | -62.3451 | 59.5088 | 59.618 | 59.6395 | -62.3765 | 0.052208 | -0.1624 | -1.6e-05 | 0.033191 | -0.019017 | -0.42239 | -0.38111 | -0.088635 | -0.32091 | 0.032233 | -0.057217 | 0.031418 | -0.21176 | -0.19024 | 121.9552 | 121.6952 | 121.7365 | 62.2985 | -122.0654 | 121.7967 | 121.9059 | 121.9274 | 62.3844 | -122.2062
374.4375 | 122.2412 | -62.2925 | 59.7748 | 1.4211e-13 | -0.027168 | -0.003874 | 0.066007 | -0.0049314 | 0.05795 | -0.0054937 | 0.00078395 | -0.0016878 | -0.0034396 | 0.019919 | -0.0095994 | -62.2879 | 0.001407 | -62.2547 | 59.6627 | 59.4119 | 59.4486 | -62.2403 | -62.2557 | 0.091933 | -62.3497 | 59.5088 | 59.6225 | 59.6395 | -62.372 | 0.052206 | -0.11204 | 0.004561 | 0.037768 | -0.014438 | -0.36288 | -0.32618 | -0.079479 | -0.26598 | 0.03681 | -0.057219 | 0.02226 | -0.15225 | -0.13531 | 121.9552 | 121.7044 | 121.7411 | 62.2939 | -122.0151 | 121.8013 | 121.915 | 121.932 | 62.3844 | -122.1467
376.1875 | 122.287 | -62.2971 | 59.7519 | 1.4211e-13 | -0.026955 | -0.003874 | 0.066007 | -0.005145 | 0.058377 | -0.0054937 | 0.00078395 | -0.0019016 | -0.0034396 | 0.019705 | -0.01024 | -62.2833 | 0.010564 | -62.2456 | 59.6719 | 59.4119 | 59.4532 | -62.2403 | -62.2602 | 0.087354 | -62.3497 | 59.5042 | 59.6271 | 59.6395 | -62.372 | 0.056784 | -0.079998 | 0.013717 | 0.051503 | -0.005281 | -0.33999 | -0.29871 | -0.074901 | -0.24767 | 0.036809 | -0.052641 | 0.02226 | -0.12478 | -0.11242 | 121.969 | 121.709 | 121.7502 | 62.3076 | -121.9922 | 121.8013 | 121.9242 | 121.9365 | 62.3844 | -122.1239
377.8594 | 122.3053 | -62.2833 | 59.761 | 1.4211e-13 | -0.027382 | -0.003874 | 0.066007 | -0.0049314 | 0.058377 | -0.0054937 | 0.00078395 | -0.0019016 | -0.003226 | 0.019705 | -0.010027 | -62.2925 | 0.005985 | -62.2456 | 59.6719 | 59.4165 | 59.4623 | -62.2357 | -62.2648 | 0.091933 | -62.3543 | 59.5042 | 59.6225 | 59.644 | -62.3765 | 0.04763 | -0.089153 | -0.009173 | 0.03777 | -0.00986 | -0.34456 | -0.29871 | -0.093213 | -0.25683 | 0.018497 | -0.070952 | 0.022261 | -0.13851 | -0.117 | 121.9552 | 121.6998 | 121.7457 | 62.2893 | -121.9967 | 121.7875 | 121.9059 | 121.9274 | 62.3753 | -122.1376
379.6094 | 122.2229 | -62.2833 | 59.8297 | 1.4211e-13 | -0.027168 | -0.0043014 | 0.066007 | -0.005145 | 0.058377 | 0.0021363 | 0.00078395 | -0.0019016 | -0.0030124 | 0.019705 | -0.0095994 | -62.2925 | 0.005985 | -62.2456 | 59.6719 | 59.4073 | 59.4532 | -62.2357 | -62.2557 | 0.091933 | -62.3634 | 59.5042 | 59.6271 | 59.6395 | -62.3765 | 0.04763 | -0.15782 | -0.009173 | 0.03777 | -0.00986 | -0.42239 | -0.37653 | -0.093213 | -0.32549 | 0.027655 | -0.08011 | 0.013103 | -0.2026 | -0.19024 | 121.9552 | 121.6907 | 121.7365 | 62.2893 | -122.0654 | 121.7875 | 121.9104 | 121.9228 | 62.3753 | -122.2062
381.3594 | 122.2961 | -62.2833 | 59.7473 | 1.4211e-13 | -0.026955 | -0.003874 | 0.065793 | -0.005145 | 0.05795 | -0.0054937 | 0.00057035 | -0.0021152 | -0.003226 | 0.019705 | -0.0098132 | -62.2879 | 0.010564 | -62.2547 | 59.6627 | 59.4165 | 59.4578 | -62.2449 | -62.2648 | 0.082776 | -62.3543 | 59.5042 | 59.6225 | 59.6212 | -62.3765 | 0.038472 | -0.084576 | -0.004594 | 0.028613 | -0.009859 | -0.33083 | -0.28955 | -0.093213 | -0.2431 | 0.018497 | -0.070952 | 0.022261 | -0.12478 | -0.12616 | 121.9461 | 121.6998 | 121.7411 | 62.2939 | -121.9922 | 121.7875 | 121.9059 | 121.9045 | 62.3661 | -122.1239
383.1094 | 122.2046 | -62.3062 | 59.8022 | 1.4211e-13 | -0.027382 | -0.0043014 | 0.066007 | -0.0049314 | 0.058591 | 0.0021363 | 0.00035675 | -0.0023288 | -0.0030124 | 0.019919 | -0.0093858 | -62.2879 | 0.015142 | -62.2501 | 59.6811 | 59.4165 | 59.4578 | -62.2357 | -62.2602 | 0.087354 | -62.3543 | 59.5042 | 59.6271 | 59.6395 | -62.3765 | 0.070518 | -0.1212 | 0.018294 | 0.05608 | -0.014438 | -0.38576 | -0.34448 | -0.070325 | -0.29803 | 0.045964 | -0.048064 | 0.022261 | -0.17513 | -0.16278 | 121.9873 | 121.7227 | 121.764 | 62.3214 | -122.0379 | 121.8104 | 121.9333 | 121.9457 | 62.3936 | -122.1788
384.8125 | 122.3282 | -62.2604 | 59.7748 | 1.4211e-13 | -0.026741 | -0.003874 | 0.066007 | -0.005145 | 0.058377 | 0.0021363 | 0.00078395 | -0.0021152 | -0.003226 | 0.019705 | -0.0095994 | -62.2833 | 0.019721 | -62.2501 | 59.6673 | 59.4073 | 59.4532 | -62.2357 | -62.2557 | 0.087354 | -62.3543 | 59.5042 | 59.6225 | 59.644 | -62.372 | 0.024742 | -0.10746 | -0.022904 | 0.010304 | -0.014438 | -0.36745 | -0.3216 | -0.11152 | -0.27056 | 0.004767 | -0.09384 | 0.017682 | -0.15225 | -0.13073 | 121.9278 | 121.6678 | 121.7136 | 62.2802 | -122.0105 | 121.7647 | 121.883 | 121.9045 | 62.3478 | -122.1467
386.5625 | 122.2916 | -62.2742 | 59.7656 | 1.4211e-13 | -0.027382 | -0.0040876 | 0.066007 | -0.005145 | 0.058163 | 0.0021363 | 0.00035675 | -0.0021152 | -0.0034396 | 0.019919 | -0.0095994 | -62.2925 | 0.015142 | -62.2501 | 59.6673 | 59.4165 | 59.4578 | -62.2357 | -62.2557 | 0.087354 | -62.3589 | 59.5042 | 59.6271 | 59.6486 | -62.372 | 0.038475 | -0.098309 | -0.018328 | 0.024037 | -0.014438 | -0.34914 | -0.30786 | -0.097789 | -0.26141 | 0.0185 | -0.084686 | 0.013103 | -0.13851 | -0.117 | 121.9415 | 121.6907 | 121.7319 | 62.2893 | -122.0013 | 121.7784 | 121.9013 | 121.9228 | 62.3615 | -122.1376
388.3125 | 122.3969 | -62.2787 | 59.761 | 1.4211e-13 | -0.027382 | -0.0040876 | 0.065793 | -0.005145 | 0.058163 | -0.013124 | 0.00057035 | -0.0019016 | -0.0034396 | 0.019278 | -0.0095994 | -62.2833 | 0.015142 | -62.2456 | 59.6673 | 59.4073 | 59.4532 | -62.2357 | -62.2557 | 0.091933 | -62.3497 | 59.5134 | 59.6317 | 59.6486 | -62.3765 | 0.043053 | -0.093731 | -0.004593 | 0.033193 | -0.00986 | -0.35372 | -0.30786 | -0.09779 | -0.24767 | 0.023078 | -0.070951 | 0.026839 | -0.12936 | -0.11242 | 121.9461 | 121.6861 | 121.7319 | 62.2939 | -121.9967 | 121.7921 | 121.9104 | 121.9274 | 62.3707 | -122.1376
390.0625 | 122.2229 | -62.2787 | 59.816 | 1.4211e-13 | -0.027382 | -0.0040876 | 0.06622 | -0.005145 | 0.058377 | -0.013124 | 0.00057035 | -0.0019016 | -0.0030124 | 0.019705 | -0.0098132 | -62.2879 | 0.010564 | -62.2456 | 59.6673 | 59.4119 | 59.4532 | -62.2357 | -62.2557 | 0.082776 | -62.3543 | 59.5042 | 59.6317 | 59.644 | -62.3811 | 0.043053 | -0.14866 | -0.009171 | 0.033193 | -0.00986 | -0.40407 | -0.3628 | -0.10237 | -0.31176 | 0.023078 | -0.075529 | 0.02684 | -0.18429 | -0.17193 | 121.9461 | 121.6907 | 121.7319 | 62.2893 | -122.0517 | 121.783 | 121.9104 | 121.9228 | 62.3615 | -122.1971
391.7344 | 122.3053 | -62.2787 | 59.7656 | 1.4211e-13 | -0.027596 | -0.0043014 | 0.066007 | -0.0053586 | 0.058163 | -0.013124 | 0.00057035 | -0.0021152 | -0.003226 | 0.019919 | -0.010027 | -62.2833 | 0.005985 | -62.2593 | 59.6719 | 59.4119 | 59.4578 | -62.2357 | -62.2557 | 0.087354 | -62.3497 | 59.5042 | 59.6317 | 59.644 | -62.3674 | 0.043053 | -0.093731 | -0.004593 | 0.019458 | -0.023595 | -0.35372 | -0.30786 | -0.088632 | -0.26141 | 0.023078 | -0.070951 | 0.017681 | -0.13394 | -0.12158 | 121.9506 | 121.6907 | 121.7365 | 62.2847 | -122.0013 | 121.783 | 121.9104 | 121.9228 | 62.3661 | -122.133
393.4688 | 122.3282 | -62.2742 | 59.7656 | 1.4211e-13 | -0.027168 | -0.0040876 | 0.065793 | -0.005145 | 0.058163 | 0.0021363 | 0.00035675 | -0.0021152 | -0.003226 | 0.019705 | -0.0098132 | -62.2925 | 0.005985 | -62.2547 | 59.6673 | 59.4165 | 59.4532 | -62.2403 | -62.2602 | 0.091933 | -62.3543 | 59.5042 | 59.618 | 59.6166 | -62.372 | 0.033896 | -0.098309 | -0.018328 | 0.019458 | -0.014438 | -0.34914 | -0.31244 | -0.097789 | -0.26141 | 0.013921 | -0.080107 | 0.017682 | -0.14767 | -0.14905 | 121.9415 | 121.6907 | 121.7274 | 62.2802 | -122.0059 | 121.7784 | 121.8921 | 121.8907 | 62.3661 | -122.1376
395.1562 | 122.2687 | -62.2742 | 59.7977 | 1.4211e-13 | -0.027168 | -0.0043014 | 0.066007 | -0.0049314 | 0.058377 | -0.0054937 | 0.00035675 | -0.0019016 | -0.003226 | 0.019919 | -0.0095994 | -62.2833 | 0.001407 | -62.2547 | 59.6765 | 59.4119 | 59.4532 | -62.2311 | -62.2557 | 0.087354 | -62.3589 | 59.5042 | 59.6271 | 59.6395 | -62.372 | 0.043054 | -0.1212 | -0.009171 | 0.019458 | -0.023596 | -0.38576 | -0.34448 | -0.097789 | -0.29345 | 0.0185 | -0.084686 | 0.013103 | -0.17056 | -0.1582 | 121.9506 | 121.6861 | 121.7274 | 62.2756 | -122.0288 | 121.7784 | 121.9013 | 121.9136 | 62.3615 | -122.1696
396.8906 | 122.2092 | -62.2833 | 59.8251 | 1.4211e-13 | -0.027382 | -0.0043014 | 0.065793 | -0.005145 | 0.05795 | 0.0097668 | 0.00078395 | -0.0019016 | -0.003226 | 0.019705 | -0.010027 | -62.2788 | 0.010564 | -62.2501 | 59.6627 | 59.4119 | 59.4532 | -62.2311 | -62.2648 | 0.087354 | -62.3543 | 59.5134 | 59.6317 | 59.6349 | -62.3811 | 0.052209 | -0.1624 | 0.004562 | 0.033192 | -0.019017 | -0.41323 | -0.37195 | -0.097792 | -0.31176 | 0.018497 | -0.070952 | 0.02684 | -0.19344 | -0.19024 | 121.9461 | 121.6952 | 121.7365 | 62.2939 | -122.0563 | 121.7967 | 121.915 | 121.9182 | 62.3707 | -122.2063
398.625 | 122.2275 | -62.2833 | 59.8343 | 1.4211e-13 | -0.02781 | -0.0043014 | 0.065793 | -0.0047176 | 0.058163 | -0.0054937 | 0.00057035 | -0.0021152 | -0.003226 | 0.019705 | -0.0095994 | -62.2788 | 0.010564 | -62.2456 | 59.6673 | 59.4073 | 59.4578 | -62.2403 | -62.2557 | 0.087354 | -62.3497 | 59.5134 | 59.6271 | 59.644 | -62.3765 | 0.043051 | -0.16697 | 0.004562 | 0.03777 | -0.005281 | -0.42696 | -0.37653 | -0.093213 | -0.32091 | 0.027655 | -0.066374 | 0.026839 | -0.20718 | -0.19024 | 121.9506 | 121.6907 | 121.7411 | 62.2939 | -122.0746 | 121.7967 | 121.9104 | 121.9274 | 62.3707 | -122.2108
400.3281 | 122.3419 | -62.265 | 59.7839 | 1.4211e-13 | -0.027382 | -0.0043014 | 0.06622 | -0.005145 | 0.058163 | -0.0054937 | 0.00057035 | -0.0019016 | -0.0034396 | 0.019705 | -0.010027 | -62.2879 | 0.005985 | -62.2501 | 59.6673 | 59.4073 | 59.4532 | -62.2403 | -62.2557 | 0.091933 | -62.3543 | 59.4996 | 59.6271 | 59.6532 | -62.3811 | 0.024741 | -0.11662 | -0.022904 | 0.014882 | -0.009859 | -0.37661 | -0.33075 | -0.1161 | -0.2843 | 0.009345 | -0.089262 | 0.02684 | -0.15682 | -0.13073 | 121.9323 | 121.6723 | 121.7182 | 62.271 | -122.0242 | 121.7647 | 121.8921 | 121.9182 | 62.3569 | -122.1651
402.0625 | 122.2961 | -62.2787 | 59.7748 | 1.4211e-13 | -0.027596 | -0.004515 | 0.066007 | -0.0053586 | 0.058377 | -0.0054937 | 0.00078395 | -0.0016878 | -0.003226 | 0.020132 | -0.01024 | -62.2833 | 0.010564 | -62.2547 | 59.6765 | 59.4119 | 59.4578 | -62.2403 | -62.2557 | 0.082776 | -62.3543 | 59.5042 | 59.6225 | 59.6486 | -62.372 | 0.038474 | -0.098307 | -0.004593 | 0.024036 | -0.014438 | -0.36288 | -0.31702 | -0.093211 | -0.27056 | 0.023078 | -0.075529 | 0.017682 | -0.15225 | -0.12615 | 121.9552 | 121.6907 | 121.7365 | 62.2893 | -122.0151 | 121.783 | 121.9013 | 121.9274 | 62.3615 | -122.1467
403.8125 | 122.2733 | -62.3016 | 59.7656 | 1.4211e-13 | -0.027382 | -0.003874 | 0.06622 | -0.005145 | 0.058377 | -0.0054937 | 0.00057035 | -0.0016878 | -0.0030124 | 0.019919 | -0.0098132 | -62.2788 | 0.010564 | -62.2547 | 59.6719 | 59.4165 | 59.4532 | -62.2449 | -62.2557 | 0.087354 | -62.3589 | 59.5088 | 59.6271 | 59.6486 | -62.3811 | 0.056783 | -0.093731 | 0.022873 | 0.046924 | -0.009859 | -0.34914 | -0.31244 | -0.079481 | -0.25683 | 0.045966 | -0.05722 | 0.022261 | -0.13851 | -0.117 | 121.9735 | 121.7181 | 121.7548 | 62.3122 | -122.0105 | 121.8104 | 121.9287 | 121.9503 | 62.389 | -122.1467
405.5 | 122.2549 | -62.2879 | 59.7885 | 1.4211e-13 | -0.027596 | -0.0040876 | 0.06622 | -0.005145 | 0.05795 | -0.0054937 | 0.00057035 | -0.0019016 | -0.0027988 | 0.019705 | -0.0098132 | -62.2879 | 0.005985 | -62.2456 | 59.6627 | 59.4119 | 59.4578 | -62.2357 | -62.2557 | 0.087354 | -62.3589 | 59.5088 | 59.6317 | 59.644 | -62.3765 | 0.052208 | -0.12578 | -1.6e-05 | 0.042348 | -0.00986 | -0.37661 | -0.33075 | -0.088635 | -0.27972 | 0.032233 | -0.070953 | 0.017682 | -0.15682 | -0.14447 | 121.9506 | 121.6998 | 121.7457 | 62.2939 | -122.0242 | 121.7967 | 121.9196 | 121.932 | 62.3753 | -122.1651
407.2344 | 122.2916 | -62.2833 | 59.7565 | 1.4211e-13 | -0.027596 | -0.004515 | 0.065793 | -0.0047176 | 0.058377 | -0.013124 | 0.00078395 | -0.0019016 | -0.0030124 | 0.019919 | -0.0095994 | -62.2833 | 0.010564 | -62.2501 | 59.6719 | 59.4165 | 59.4669 | -62.2449 | -62.2511 | 0.091933 | -62.3589 | 59.5042 | 59.6271 | 59.644 | -62.372 | 0.038472 | -0.084576 | -1.6e-05 | 0.033192 | -0.00528 | -0.33999 | -0.28955 | -0.088634 | -0.25225 | 0.032233 | -0.075531 | 0.013103 | -0.12936 | -0.11242 | 121.9552 | 121.6998 | 121.7502 | 62.2939 | -122.0013 | 121.7875 | 121.9104 | 121.9274 | 62.3753 | -122.1284
408.9062 | 122.2961 | -62.2971 | 59.7473 | 1.4211e-13 | -0.027596 | -0.004515 | 0.066007 | -0.0049314 | 0.05795 | 0.0021363 | 0.00078395 | -0.0016878 | -0.003226 | 0.019705 | -0.010027 | -62.2879 | 0.010564 | -62.2501 | 59.6719 | 59.4073 | 59.4532 | -62.2449 | -62.2557 | 0.087354 | -62.3543 | 59.5134 | 59.6271 | 59.6257 | -62.3765 | 0.052205 | -0.07542 | 0.009139 | 0.046925 | -0.00528 | -0.33999 | -0.29413 | -0.07948 | -0.23394 | 0.041388 | -0.057219 | 0.022261 | -0.1202 | -0.12158 | 121.969 | 121.7044 | 121.7502 | 62.3076 | -121.9922 | 121.8104 | 121.9242 | 121.9228 | 62.3844 | -122.1239
410.6562 | 122.3373 | -62.2879 | 59.7153 | 1.4211e-13 | -0.027596 | -0.0040876 | 0.065793 | -0.005145 | 0.058163 | -0.020755 | 0.00035675 | -0.0019016 | -0.0034396 | 0.019705 | -0.01024 | -62.2833 | 0.010564 | -62.2456 | 59.6673 | 59.4119 | 59.4669 | -62.2403 | -62.2557 | 0.082776 | -62.3543 | 59.5042 | 59.6271 | 59.6395 | -62.3765 | 0.047629 | -0.047955 | 0.004562 | 0.042348 | -0.005281 | -0.30337 | -0.24835 | -0.088635 | -0.21105 | 0.032233 | -0.066374 | 0.022261 | -0.08816 | -0.075801 | 121.9552 | 121.6998 | 121.7548 | 62.2985 | -121.9555 | 121.7921 | 121.915 | 121.9274 | 62.3707 | -122.0918
412.3438 | 122.2137 | -62.3108 | 59.7885 | 1.4211e-13 | -0.027596 | -0.0040876 | 0.065793 | -0.0049314 | 0.058377 | 0.0021363 | 0.00057035 | -0.0021152 | -0.003226 | 0.020132 | -0.0098132 | -62.2879 | 0.010564 | -62.2593 | 59.6673 | 59.4073 | 59.4623 | -62.2403 | -62.2557 | 0.087354 | -62.3589 | 59.5088 | 59.6271 | 59.644 | -62.3811 | 0.070517 | -0.1212 | 0.022872 | 0.051501 | -0.019016 | -0.38119 | -0.32617 | -0.070326 | -0.27972 | 0.055121 | -0.048065 | 0.022261 | -0.1614 | -0.14447 | 121.9781 | 121.7181 | 121.7731 | 62.3214 | -122.0288 | 121.8196 | 121.9379 | 121.9548 | 62.3981 | -122.1696
414.0938 | 122.2595 | -62.2742 | 59.7977 | 1.4211e-13 | -0.02781 | -0.004515 | 0.065793 | -0.0053586 | 0.05795 | -0.0054937 | 0.00057035 | -0.0019016 | -0.003226 | 0.019705 | -0.010027 | -62.2879 | 0.001407 | -62.2547 | 59.6765 | 59.4165 | 59.4578 | -62.2449 | -62.2602 | 0.087354 | -62.3589 | 59.5088 | 59.6271 | 59.6395 | -62.3765 | 0.029317 | -0.1212 | -0.013749 | 0.019458 | -0.009859 | -0.38118 | -0.33991 | -0.10237 | -0.28887 | 0.013921 | -0.084686 | 0.017682 | -0.17056 | -0.1582 | 121.9506 | 121.6907 | 121.7319 | 62.2756 | -122.0425 | 121.783 | 121.9013 | 121.9136 | 62.3615 | -122.1742
415.7969 | 122.319 | -62.2559 | 59.7931 | 1.4211e-13 | -0.02781 | -0.0043014 | 0.065793 | -0.0049314 | 0.058163 | -0.013124 | 0.00078395 | -0.0016878 | -0.0036534 | 0.020132 | -0.01024 | -62.2879 | 0.019721 | -62.2501 | 59.6673 | 59.4119 | 59.4578 | -62.2357 | -62.2511 | 0.082776 | -62.3589 | 59.5134 | 59.6225 | 59.6532 | -62.3811 | 0.020164 | -0.12577 | -0.03206 | 0.005726 | -0.014438 | -0.38119 | -0.33533 | -0.12526 | -0.27971 | 0.004767 | -0.103 | 0.022261 | -0.17056 | -0.13988 | 121.9232 | 121.6678 | 121.7136 | 62.2756 | -122.0288 | 121.7692 | 121.8784 | 121.9091 | 62.3386 | -122.1742
417.4688 | 122.2229 | -62.3108 | 59.7931 | 1.4211e-13 | -0.02781 | -0.0043014 | 0.065579 | -0.0053586 | 0.05795 | -0.0054937 | 0.00057035 | -0.0019016 | -0.0034396 | 0.020132 | -0.010027 | -62.2925 | 0.019721 | -62.2547 | 59.6719 | 59.4119 | 59.4623 | -62.2403 | -62.2602 | 0.082776 | -62.3543 | 59.5134 | 59.6271 | 59.6486 | -62.3765 | 0.070517 | -0.1212 | 0.018293 | 0.056079 | -0.014438 | -0.38119 | -0.33075 | -0.065747 | -0.27971 | 0.050542 | -0.043486 | 0.022261 | -0.16598 | -0.14446 | 121.9827 | 121.7227 | 121.7731 | 62.3305 | -122.0334 | 121.8242 | 121.9379 | 121.9594 | 62.3936 | -122.1696
419.2031 | 122.2778 | -62.3062 | 59.7748 | 1.4211e-13 | -0.027596 | -0.0047286 | 0.065793 | -0.005145 | 0.058163 | 0.0021363 | 0.00099775 | -0.0021152 | -0.0034396 | 0.020132 | -0.010027 | -62.2925 | 0.005985 | -62.2547 | 59.6673 | 59.4211 | 59.4623 | -62.2403 | -62.2557 | 0.087354 | -62.3497 | 59.518 | 59.6271 | 59.644 | -62.3811 | 0.065939 | -0.10746 | 0.013715 | 0.051501 | -0.014438 | -0.35372 | -0.31244 | -0.074904 | -0.25683 | 0.050543 | -0.043486 | 0.031418 | -0.14767 | -0.13073 | 121.9735 | 121.7273 | 121.7686 | 62.3122 | -122.0151 | 121.8242 | 121.9333 | 121.9503 | 62.3936 | -122.1559
420.8906 | 122.2504 | -62.2833 | 59.7931 | 1.4211e-13 | -0.028237 | -0.0043014 | 0.066007 | -0.0053586 | 0.05795 | 0.0021363 | 0.00057035 | -0.0019016 | -0.0030124 | 0.020132 | -0.01024 | -62.2925 | 0.010564 | -62.2547 | 59.6765 | 59.4165 | 59.4578 | -62.2311 | -62.2511 | 0.082776 | -62.3497 | 59.5088 | 59.6317 | 59.6486 | -62.372 | 0.052209 | -0.11662 | -0.009173 | 0.028613 | -0.023596 | -0.37661 | -0.33533 | -0.088634 | -0.28429 | 0.032233 | -0.066374 | 0.02226 | -0.1614 | -0.14446 | 121.9598 | 121.6998 | 121.7411 | 62.2939 | -122.0242 | 121.7921 | 121.915 | 121.932 | 62.3661 | -122.165
422.6562 | 122.2321 | -62.3016 | 59.8572 | 1.4211e-13 | -0.027596 | -0.004515 | 0.066007 | -0.005145 | 0.057736 | 0.0021363 | 0.00035675 | -0.0021152 | -0.0030124 | 0.020132 | -0.0098132 | -62.2925 | 0.005985 | -62.2547 | 59.6673 | 59.4119 | 59.4623 | -62.2403 | -62.2511 | 0.082776 | -62.3543 | 59.4996 | 59.6271 | 59.644 | -62.372 | 0.061362 | -0.18986 | 0.009138 | 0.046924 | -0.014438 | -0.44527 | -0.39484 | -0.070323 | -0.35754 | 0.050544 | -0.052641 | 0.017682 | -0.23007 | -0.21313 | 121.969 | 121.7135 | 121.764 | 62.3076 | -122.0975 | 121.8013 | 121.9287 | 121.9457 | 62.3844 | -122.2291
424.3438 | 122.2961 | -62.2833 | 59.7382 | 1.4211e-13 | -0.028237 | -0.0043014 | 0.066007 | -0.005145 | 0.058163 | -0.013124 | 0.00057035 | -0.0016878 | -0.0034396 | 0.020132 | -0.010027 | -62.2879 | 0.015142 | -62.2593 | 59.6765 | 59.4211 | 59.4578 | -62.2449 | -62.2557 | 0.078197 | -62.3543 | 59.5088 | 59.6271 | 59.6486 | -62.3765 | 0.038472 | -0.061686 | -0.004594 | 0.024035 | -0.014437 | -0.3171 | -0.2804 | -0.093213 | -0.22936 | 0.027655 | -0.070952 | 0.022261 | -0.11105 | -0.089532 | 121.9598 | 121.7044 | 121.7411 | 62.2985 | -121.983 | 121.7921 | 121.9104 | 121.932 | 62.3615 | -122.1147
426.0781 | 122.2366 | -62.2742 | 59.8343 | 1.4211e-13 | -0.02781 | -0.004515 | 0.065793 | -0.0049314 | 0.05795 | 0.0021363 | 0.00057035 | -0.0019016 | -0.0034396 | 0.019919 | -0.010027 | -62.2879 | 0.015142 | -62.2593 | 59.6627 | 59.4073 | 59.4623 | -62.2403 | -62.2511 | 0.091933 | -62.368 | 59.5088 | 59.618 | 59.644 | -62.3765 | 0.033896 | -0.17155 | -0.013749 | 0.01488 | -0.019016 | -0.42696 | -0.37195 | -0.10237 | -0.32549 | 0.023078 | -0.093843 | 0.008525 | -0.21634 | -0.19024 | 121.9369 | 121.6815 | 121.7365 | 62.2893 | -122.0746 | 121.783 | 121.8921 | 121.9182 | 62.3661 | -122.2108
427.8281 | 122.2458 | -62.2925 | 59.8343 | 1.4211e-13 | -0.027596 | -0.0043014 | 0.065793 | -0.005145 | 0.05795 | -0.020755 | 0.00057035 | -0.0021152 | -0.003226 | 0.019919 | -0.0098132 | -62.2879 | 0.019721 | -62.2456 | 59.6719 | 59.4211 | 59.4623 | -62.2357 | -62.2511 | 0.087354 | -62.3589 | 59.5042 | 59.6317 | 59.6486 | -62.372 | 0.056785 | -0.1624 | 0.004561 | 0.046925 | -0.00986 | -0.41323 | -0.37195 | -0.079479 | -0.33007 | 0.041388 | -0.066376 | 0.013103 | -0.2026 | -0.18566 | 121.9644 | 121.7135 | 121.7548 | 62.3122 | -122.07 | 121.7967 | 121.9242 | 121.9411 | 62.3798 | -122.2062
429.5156 | 122.3373 | -62.2696 | 59.7153 | 1.4211e-13 | -0.028023 | -0.004515 | 0.065793 | -0.005145 | 0.05795 | -0.0054937 | 0.00057035 | -0.0019016 | -0.0030124 | 0.020132 | -0.01024 | -62.2833 | 0.019721 | -62.2593 | 59.6673 | 59.4165 | 59.4669 | -62.2449 | -62.1458 | 0.087354 | -62.3497 | 59.5134 | 59.6317 | 59.644 | -62.3903 | 0.024739 | -0.047955 | -0.013749 | 0.010302 | -0.014437 | -0.29879 | -0.24835 | -0.12068 | -0.2019 | 0.12381 | -0.080107 | 0.040575 | -0.083581 | -0.071223 | 121.9369 | 121.6861 | 121.7365 | 62.2893 | -121.9601 | 121.783 | 121.9013 | 121.9136 | 62.3569 | -122.1055
431.2812 | 122.2961 | -62.3062 | 59.7336 | 1.4211e-13 | -0.027596 | -0.0043014 | 0.065366 | -0.0049314 | 0.058163 | -0.0054937 | 0.00035675 | -0.0019016 | -0.003226 | 0.019919 | -0.01024 | -62.2833 | 0.015142 | -62.2639 | 59.6765 | 59.4211 | 59.4669 | -62.2403 | -62.2282 | 0.087354 | -62.3543 | 59.5134 | 59.6317 | 59.644 | -62.3765 | 0.065939 | -0.057109 | 0.022872 | 0.042345 | -0.023594 | -0.31252 | -0.26666 | -0.070325 | -0.22021 | 0.078015 | -0.048064 | 0.022261 | -0.10189 | -0.089534 | 121.9827 | 121.7273 | 121.7731 | 62.3214 | -121.9739 | 121.8196 | 121.9379 | 121.9503 | 62.3936 | -122.1101
433.0312 | 122.2733 | -62.2787 | 59.816 | 1.4211e-13 | -0.028023 | -0.0043014 | 0.065579 | -0.0053586 | 0.057736 | -0.0054937 | 0.00057035 | -0.0016878 | -0.0030124 | 0.020346 | -0.0098132 | -62.2879 | 0.010564 | -62.2501 | 59.6719 | 59.4165 | 59.4486 | -62.2403 | -62.2511 | 0.087354 | -62.3543 | 59.5134 | 59.6271 | 59.6486 | -62.3765 | 0.038474 | -0.14408 | -0.009171 | 0.028615 | -0.009859 | -0.3995 | -0.36737 | -0.09779 | -0.3026 | 0.027656 | -0.075529 | 0.022261 | -0.18887 | -0.16735 | 121.9506 | 121.6952 | 121.7274 | 62.2893 | -122.0563 | 121.7921 | 121.9059 | 121.9274 | 62.3661 | -122.1925
434.7188 | 122.287 | -62.2742 | 59.8068 | 1.4211e-13 | -0.028023 | -0.004515 | 0.065793 | -0.0053586 | 0.058163 | 0.0021363 | 0.00035675 | -0.0019016 | -0.0030124 | 0.020132 | -0.010027 | -62.2925 | 0.010564 | -62.2547 | 59.6673 | 59.4119 | 59.4578 | -62.2357 | -62.2465 | 0.091933 | -62.3589 | 59.5042 | 59.6271 | 59.6349 | -62.3857 | 0.038475 | -0.13951 | -0.018328 | 0.019458 | -0.019017 | -0.39492 | -0.34906 | -0.11153 | -0.3026 | 0.027657 | -0.084686 | 0.02684 | -0.17971 | -0.17193 | 121.9415 | 121.6861 | 121.7319 | 62.2847 | -122.0425 | 121.7784 | 121.9013 | 121.9091 | 62.3661 | -122.1925
436.4531 | 122.2641 | -62.2696 | 59.8297 | 1.4211e-13 | -0.028023 | -0.0040876 | 0.065793 | -0.0049314 | 0.057736 | 0.017397 | 0.00057035 | -0.0021152 | -0.0034396 | 0.020132 | -0.01024 | -62.2879 | 0.005985 | -62.2547 | 59.6719 | 59.4073 | 59.4578 | -62.2449 | -62.2557 | 0.082776 | -62.3589 | 59.5088 | 59.6271 | 59.6486 | -62.3811 | 0.024739 | -0.15782 | -0.018327 | 0.01488 | -0.009859 | -0.42239 | -0.37195 | -0.11153 | -0.32091 | 0.013922 | -0.089264 | 0.022261 | -0.2026 | -0.18109 | 121.9415 | 121.6769 | 121.7274 | 62.2756 | -122.0746 | 121.7784 | 121.8967 | 121.9182 | 62.3524 | -122.2108
438.125 | 122.287 | -62.2833 | 59.7748 | 1.4211e-13 | -0.02781 | -0.004515 | 0.066007 | -0.0053586 | 0.058163 | 0.0097668 | 0.00057035 | -0.0021152 | -0.003226 | 0.020346 | -0.01024 | -62.2879 | 0.015142 | -62.2547 | 59.6719 | 59.4211 | 59.4669 | -62.2449 | -62.2557 | 0.087354 | -62.3589 | 59.5088 | 59.6317 | 59.644 | -62.3765 | 0.038472 | -0.10289 | -0.004594 | 0.028613 | -0.009859 | -0.35372 | -0.30786 | -0.093213 | -0.26598 | 0.027655 | -0.075531 | 0.017682 | -0.14309 | -0.13073 | 121.9552 | 121.7044 | 121.7502 | 62.2985 | -122.0196 | 121.7921 | 121.915 | 121.9274 | 62.3707 | -122.1513
439.875 | 122.2321 | -62.2787 | 59.7931 | 1.4211e-13 | -0.02781 | -0.004515 | 0.065793 | -0.0049314 | 0.058377 | 0.0097668 | 0.00078395 | -0.0019016 | -0.003226 | 0.020346 | -0.0098132 | -62.2925 | 0.005985 | -62.2593 | 59.6673 | 59.4119 | 59.4623 | -62.2449 | -61.7108 | 0.087354 | -62.3589 | 59.5088 | 59.618 | 59.6532 | -62.3811 | 0.033895 | -0.12577 | -0.01375 | 0.019458 | -0.014437 | -0.38119 | -0.33075 | -0.10237 | -0.28429 | 0.56794 | -0.080108 | 0.022261 | -0.17514 | -0.13988 | 121.9461 | 121.6907 | 121.7411 | 62.2847 | -122.0379 | 121.7875 | 121.8967 | 121.932 | 62.3661 | -122.1742
441.6094 | 122.3099 | -62.2879 | 59.7656 | 1.4211e-13 | -0.027596 | -0.0043014 | 0.065579 | -0.0053586 | 0.05795 | 0.0097668 | 0.00035675 | -0.0019016 | -0.0036534 | 0.020346 | -0.010027 | -62.2833 | 0.019721 | -62.2593 | 59.6673 | 59.4256 | 59.4623 | -62.2449 | -62.1916 | 0.082776 | -62.3589 | 59.5088 | 59.6271 | 59.6532 | -62.3811 | 0.04305 | -0.098309 | 0.004562 | 0.028613 | -0.014437 | -0.33998 | -0.30329 | -0.093214 | -0.25683 | 0.096335 | -0.070953 | 0.022261 | -0.13851 | -0.11242 | 121.9552 | 121.7135 | 121.7502 | 62.3076 | -122.0105 | 121.7967 | 121.915 | 121.9411 | 62.3707 | -122.1467
443.2812 | 122.2595 | -62.2787 | 59.816 | 1.4211e-13 | -0.028023 | -0.003874 | 0.065579 | -0.0049314 | 0.057736 | -0.013124 | 0.00035675 | -0.0016878 | -0.0034396 | 0.020346 | -0.010454 | -62.2879 | 0.015142 | -62.2547 | 59.6673 | 59.4119 | 59.4623 | -62.2357 | -62.0359 | 0.091933 | -62.3543 | 59.5088 | 59.6271 | 59.6486 | -62.3811 | 0.043053 | -0.14866 | -0.009171 | 0.024036 | -0.019017 | -0.40407 | -0.35364 | -0.10237 | -0.30718 | 0.24286 | -0.075529 | 0.02684 | -0.18887 | -0.16735 | 121.9461 | 121.6907 | 121.7411 | 62.2939 | -122.0517 | 121.7875 | 121.9059 | 121.9274 | 62.3707 | -122.1971
445.0312 | 122.2046 | -62.2833 | 59.8434 | 1.4211e-13 | -0.02781 | -0.0043014 | 0.065579 | -0.0053586 | 0.058163 | -0.0054937 | 0.00014315 | -0.0019016 | -0.003226 | 0.020346 | -0.010027 | -62.2879 | 0.005985 | -62.2547 | 59.6673 | 59.4211 | 59.4623 | -62.2403 | -62.0405 | 0.091933 | -62.3589 | 59.5088 | 59.6363 | 59.6532 | -62.3811 | 0.043051 | -0.17613 | -0.004594 | 0.028613 | -0.014438 | -0.42238 | -0.38111 | -0.097792 | -0.33465 | 0.24285 | -0.075531 | 0.022261 | -0.20718 | -0.19024 | 121.9506 | 121.7044 | 121.7457 | 62.2893 | -122.0837 | 121.7921 | 121.9196 | 121.9365 | 62.3753 | -122.2246
446.7188 | 122.2733 | -62.265 | 59.8068 | 1.4211e-13 | -0.028023 | -0.004515 | 0.065793 | -0.0053586 | 0.057736 | -0.0054937 | 0.00057035 | -0.0021152 | -0.003226 | 0.020132 | -0.010454 | -62.2879 | 0.015142 | -62.2593 | 59.6719 | 59.4211 | 59.4669 | -62.2357 | -62.2419 | 0.078197 | -62.3589 | 59.5042 | 59.6408 | 59.6395 | -62.3765 | 0.02932 | -0.13493 | -0.022904 | 0.005725 | -0.023595 | -0.38576 | -0.33991 | -0.11152 | -0.3026 | 0.023081 | -0.093841 | 0.017682 | -0.16598 | -0.16735 | 121.9369 | 121.6861 | 121.7319 | 62.2802 | -122.0425 | 121.7692 | 121.9059 | 121.9045 | 62.3432 | -122.1834
448.4531 | 122.2961 | -62.2696 | 59.7473 | 1.4211e-13 | -0.028023 | -0.0040876 | 0.065793 | -0.005145 | 0.058163 | 0.0021363 | 0.00014315 | -0.0021152 | -0.003226 | 0.020346 | -0.010027 | -62.2833 | 0.015142 | -62.2639 | 59.6719 | 59.4211 | 59.4669 | -62.2449 | -62.2419 | 0.087354 | -62.3543 | 59.5088 | 59.6225 | 59.6532 | -62.372 | 0.024739 | -0.07542 | -0.013749 | 0.005724 | -0.019015 | -0.32625 | -0.2804 | -0.10237 | -0.23852 | 0.027658 | -0.084685 | 0.017682 | -0.12478 | -0.094108 | 121.9415 | 121.6907 | 121.7365 | 62.2847 | -121.9922 | 121.7784 | 121.8921 | 121.9228 | 62.3569 | -122.1193
450.2031 | 122.2321 | -62.2971 | 59.8022 | 1.4211e-13 | -0.028023 | -0.004515 | 0.065793 | -0.0053586 | 0.057736 | 0.0021363 | 0.00057035 | -0.0021152 | -0.003226 | 0.02056 | -0.01024 | -62.2925 | 0.005985 | -62.2547 | 59.6719 | 59.4211 | 59.4578 | -62.2403 | -61.8894 | 0.082776 | -62.3543 | 59.5134 | 59.6317 | 59.6395 | -62.3811 | 0.056784 | -0.13035 | 0.00456 | 0.042346 | -0.014438 | -0.38118 | -0.34448 | -0.084059 | -0.28887 | 0.40769 | -0.057219 | 0.02684 | -0.17056 | -0.16278 | 121.969 | 121.7181 | 121.7548 | 62.303 | -122.0425 | 121.8104 | 121.9287 | 121.9365 | 62.3798 | -122.1834
451.8906 | 122.3419 | -62.2559 | 59.7794 | 1.4211e-13 | -0.028237 | -0.0040876 | 0.065579 | -0.0049314 | 0.05795 | -0.013124 | 0.00057035 | -0.0019016 | -0.0030124 | 0.02056 | -0.01024 | -62.2925 | 0.019721 | -62.2547 | 59.6719 | 59.4073 | 59.4578 | -62.2403 | -62.219 | 0.091933 | -62.3589 | 59.5088 | 59.6317 | 59.6395 | -62.3811 | 0.015585 | -0.10746 | -0.036639 | 0.001147 | -0.014438 | -0.37203 | -0.3216 | -0.12526 | -0.27056 | 0.036818 | -0.103 | 0.022261 | -0.14767 | -0.13989 | 121.9278 | 121.6632 | 121.7136 | 62.2756 | -122.0196 | 121.7647 | 121.8875 | 121.8953 | 62.3478 | -122.1605
453.6406 | 122.2778 | -62.2925 | 59.7931 | 1.4211e-13 | -0.028451 | -0.0049424 | 0.065793 | -0.0049314 | 0.057736 | -0.013124 | 0.00057035 | -0.0019016 | -0.0034396 | 0.020346 | -0.01024 | -62.2879 | 0.015142 | -62.2547 | 59.6765 | 59.4119 | 59.4623 | -62.2357 | -62.1137 | 0.078197 | -62.3543 | 59.5088 | 59.6225 | 59.6486 | -62.3674 | 0.056785 | -0.11662 | 0.004561 | 0.037768 | -0.019017 | -0.38119 | -0.33075 | -0.0749 | -0.28429 | 0.17875 | -0.061797 | 0.013103 | -0.17056 | -0.14446 | 121.969 | 121.7044 | 121.7548 | 62.3076 | -122.0288 | 121.8013 | 121.915 | 121.9411 | 62.3707 | -122.1605
455.375 | 122.2092 | -62.3062 | 59.8022 | 1.4211e-13 | -0.028664 | -0.003874 | 0.065793 | -0.0049314 | 0.057736 | 0.0021363 | 0.00035675 | -0.0021152 | -0.0034396 | 0.020346 | -0.010454 | -62.2879 | 0.019721 | -62.2501 | 59.6673 | 59.4165 | 59.4715 | -62.2357 | -62.219 | 0.073618 | -62.3543 | 59.5088 | 59.6317 | 59.6395 | -62.3857 | 0.070518 | -0.13493 | 0.018294 | 0.05608 | -0.014438 | -0.38576 | -0.33075 | -0.079483 | -0.29345 | 0.087172 | -0.048064 | 0.031419 | -0.17056 | -0.16278 | 121.9735 | 121.7227 | 121.7777 | 62.3259 | -122.0379 | 121.815 | 121.9379 | 121.9457 | 62.3798 | -122.1879
457.1094 | 122.3099 | -62.2833 | 59.7565 | 1.4211e-13 | -0.028237 | -0.0043014 | 0.066007 | -0.0053586 | 0.057736 | -0.0054937 | 0.00057035 | -0.0021152 | -0.0034396 | 0.02056 | -0.010454 | -62.2879 | 0.010564 | -62.2593 | 59.6765 | 59.4256 | 59.4669 | -62.2403 | -62.2282 | 0.082776 | -62.3543 | 59.5088 | 59.6317 | 59.644 | -62.3857 | 0.043051 | -0.079997 | -0.004594 | 0.024035 | -0.019016 | -0.33083 | -0.28955 | -0.10237 | -0.24767 | 0.055127 | -0.070952 | 0.031419 | -0.12478 | -0.11242 | 121.9598 | 121.709 | 121.7502 | 62.2939 | -121.9967 | 121.7921 | 121.915 | 121.9274 | 62.3661 | -122.1422
458.8438 | 122.3053 | -62.2467 | 59.7473 | 1.4211e-13 | -0.028023 | -0.0043014 | 0.06622 | -0.0055724 | 0.058163 | -0.0054937 | 0.00014315 | -0.0019016 | -0.003226 | 0.02056 | -0.01024 | -62.2925 | 0.019721 | -62.2501 | 59.6811 | 59.4211 | 59.4669 | -62.2449 | -62.2419 | 0.091933 | -62.3634 | 59.5042 | 59.6271 | 59.644 | -62.3811 | 0.001851 | -0.066263 | -0.045794 | -0.003429 | -0.00528 | -0.32625 | -0.2804 | -0.13441 | -0.2431 | 0.00477 | -0.11673 | 0.017682 | -0.1202 | -0.10327 | 121.9278 | 121.6678 | 121.7136 | 62.2664 | -121.9922 | 121.7509 | 121.8738 | 121.8908 | 62.3386 | -122.1284
460.5156 | 122.2366 | -62.265 | 59.816 | 1.4211e-13 | -0.028451 | -0.0047286 | 0.065793 | -0.005145 | 0.05795 | -0.0054937 | 0.00057035 | -0.0021152 | -0.003226 | 0.020773 | -0.010027 | -62.2879 | 0.019721 | -62.2501 | 59.6673 | 59.4119 | 59.4623 | -62.2403 | -62.2374 | 0.082776 | -62.3543 | 59.5088 | 59.6317 | 59.644 | -62.3811 | 0.024741 | -0.14866 | -0.022904 | 0.014882 | -0.009859 | -0.40407 | -0.35364 | -0.1161 | -0.30718 | 0.02766 | -0.089262 | 0.02684 | -0.18429 | -0.17193 | 121.9323 | 121.6769 | 121.7274 | 62.2847 | -122.0563 | 121.7738 | 121.8967 | 121.9091 | 62.3478 | -122.1971
462.2656 | 122.3145 | -62.2787 | 59.7473 | 1.4211e-13 | -0.028237 | -0.0043014 | 0.065793 | -0.005145 | 0.05795 | -0.0054937 | 0.00035675 | -0.0019016 | -0.0034396 | 0.020132 | -0.01024 | -62.2879 | 0.019721 | -62.2547 | 59.6673 | 59.4256 | 59.4623 | -62.2357 | -62.2374 | 0.078197 | -62.3589 | 59.5134 | 59.6271 | 59.6486 | -62.3811 | 0.043053 | -0.079998 | -0.009171 | 0.024036 | -0.019017 | -0.32167 | -0.28497 | -0.10237 | -0.23394 | 0.041393 | -0.080108 | 0.022261 | -0.1202 | -0.098687 | 121.9461 | 121.7044 | 121.7411 | 62.2985 | -121.983 | 121.7921 | 121.9059 | 121.9274 | 62.3569 | -122.1284
464.0156 | 122.2641 | -62.2742 | 59.8022 | 1.4211e-13 | -0.02781 | -0.0043014 | 0.065793 | -0.005145 | 0.057736 | -0.0054937 | 0.00035675 | -0.0019016 | -0.003226 | 0.020132 | -0.010027 | -62.3017 | 0.015142 | -62.2547 | 59.6719 | 59.4119 | 59.4669 | -62.2403 | -62.2374 | 0.087354 | -62.3543 | 59.5088 | 59.6317 | 59.6395 | -62.3857 | 0.033896 | -0.13035 | -0.027484 | 0.019458 | -0.014438 | -0.39034 | -0.33533 | -0.11153 | -0.29345 | 0.036815 | -0.080107 | 0.031419 | -0.17056 | -0.16278 | 121.9461 | 121.6861 | 121.7411 | 62.2893 | -122.0425 | 121.783 | 121.9059 | 121.9136 | 62.3615 | -122.1879
465.7656 | 122.3099 | -62.2696 | 59.7839 | 1.4211e-13 | -0.028237 | -0.004515 | 0.06622 | -0.005145 | 0.057736 | -0.0054937 | 0.00078395 | -0.0021152 | -0.0030124 | 0.020346 | -0.0098132 | -62.2879 | 0.010564 | -62.2456 | 59.6765 | 59.4165 | 59.4578 | -62.2357 | -62.2557 | 0.091933 | -62.3589 | 59.518 | 59.6317 | 59.6486 | -62.3811 | 0.033897 | -0.10746 | -0.018327 | 0.024037 | -0.00986 | -0.36745 | -0.32617 | -0.11153 | -0.26598 | 0.013922 | -0.089264 | 0.022261 | -0.15225 | -0.13531 | 121.9461 | 121.6861 | 121.7274 | 62.2802 | -122.0196 | 121.7875 | 121.9013 | 121.9182 | 62.3615 | -122.1651
467.4531 | 122.2321 | -62.2833 | 59.8022 | 1.4211e-13 | -0.028237 | -0.0043014 | 0.065793 | -0.0053586 | 0.05795 | 0.0097668 | 0.00035675 | -0.0019016 | -0.003226 | 0.020132 | -0.01024 | -62.2925 | 0.010564 | -62.2639 | 59.6765 | 59.4302 | 59.4669 | -62.2449 | -62.2557 | 0.082776 | -62.3543 | 59.5042 | 59.6225 | 59.6486 | -62.372 | 0.038472 | -0.12577 | -0.009173 | 0.019457 | -0.019015 | -0.37202 | -0.33533 | -0.088634 | -0.29803 | 0.027655 | -0.070952 | 0.017682 | -0.17971 | -0.15362 | 121.9598 | 121.7135 | 121.7502 | 62.2939 | -122.0471 | 121.7875 | 121.9059 | 121.932 | 62.3661 | -122.1742
469.1875 | 122.287 | -62.2513 | 59.8068 | 1.4211e-13 | -0.028237 | -0.0040876 | 0.065793 | -0.0053586 | 0.058163 | 0.0097668 | 0.00057035 | -0.0021152 | -0.0034396 | 0.02056 | -0.010027 | -62.2925 | 0.015142 | -62.2547 | 59.6719 | 59.4165 | 59.4715 | -62.2494 | -62.2511 | 0.082776 | -62.3543 | 59.5088 | 59.6317 | 59.6486 | -62.3857 | 0.001851 | -0.13493 | -0.041216 | -0.00343 | -0.005281 | -0.39034 | -0.33533 | -0.13441 | -0.29803 | 0.00019 | -0.10299 | 0.031419 | -0.17513 | -0.1582 | 121.9232 | 121.6678 | 121.7228 | 62.2664 | -122.0563 | 121.7601 | 121.883 | 121.8999 | 62.3341 | -122.1925
470.875 | 122.3602 | -62.2604 | 59.761 | 1.4211e-13 | -0.028451 | -0.0047286 | 0.065579 | -0.0053586 | 0.058163 | -0.0054937 | 0.00035675 | -0.0019016 | -0.0030124 | 0.02056 | -0.010027 | -62.2879 | 0.010564 | -62.2547 | 59.6719 | 59.4211 | 59.4715 | -62.2403 | -62.2557 | 0.091933 | -62.3589 | 59.5042 | 59.6454 | 59.612 | -62.3811 | 0.020163 | -0.089153 | -0.027482 | 0.005725 | -0.014438 | -0.33998 | -0.28955 | -0.12068 | -0.25683 | 0.004767 | -0.098419 | 0.022261 | -0.11562 | -0.14905 | 121.9323 | 121.6815 | 121.7319 | 62.271 | -122.0013 | 121.7647 | 121.9059 | 121.8724 | 62.3524 | -122.1422
472.625 | 122.3557 | -62.2696 | 59.7427 | 1.4211e-13 | -0.028237 | -0.004515 | 0.065579 | -0.005145 | 0.05795 | 0.0021363 | 0.00035675 | -0.0019016 | -0.003226 | 0.020346 | -0.01024 | -62.2833 | 0.010564 | -62.2593 | 59.6765 | 59.4119 | 59.4715 | -62.2403 | -62.2557 | 0.082776 | -62.3589 | 59.5088 | 59.6363 | 59.6486 | -62.3765 | 0.029318 | -0.066264 | -0.013749 | 0.010302 | -0.019016 | -0.33083 | -0.27124 | -0.10695 | -0.23394 | 0.013922 | -0.089264 | 0.017682 | -0.10647 | -0.09411 | 121.9461 | 121.6815 | 121.7411 | 62.2802 | -121.983 | 121.7784 | 121.9059 | 121.9182 | 62.3524 | -122.1193
474.3594 | 122.3099 | -62.2833 | 59.7702 | 1.4211e-13 | -0.028451 | -0.0043014 | 0.065579 | -0.0053586 | 0.05795 | -0.0054937 | 0.00035675 | -0.0021152 | -0.003226 | 0.02056 | -0.010027 | -62.2833 | 0.015142 | -62.2593 | 59.6719 | 59.4165 | 59.4715 | -62.2494 | -62.2557 | 0.078197 | -62.3543 | 59.5088 | 59.6408 | 59.6578 | -62.3811 | 0.033894 | -0.098309 | -1.6e-05 | 0.024035 | -0.009859 | -0.35372 | -0.29871 | -0.097792 | -0.26141 | 0.027655 | -0.070952 | 0.02684 | -0.12936 | -0.11242 | 121.9552 | 121.6998 | 121.7548 | 62.2985 | -122.0196 | 121.7921 | 121.9242 | 121.9411 | 62.3615 | -122.1513
476.0938 | 122.3511 | -62.2879 | 59.7382 | 1.4211e-13 | -0.028451 | -0.0047286 | 0.065793 | -0.0053586 | 0.057736 | -0.0054937 | 0.00035675 | -0.0021152 | -0.003226 | 0.020346 | -0.0098132 | -62.2879 | 0.015142 | -62.2547 | 59.6673 | 59.4165 | 59.4715 | -62.2403 | -62.2557 | 0.082776 | -62.3543 | 59.518 | 59.65 | 59.6578 | -62.3811 | 0.047629 | -0.070843 | -1.6e-05 | 0.033191 | -0.014438 | -0.32168 | -0.26666 | -0.093214 | -0.2202 | 0.032233 | -0.066374 | 0.02684 | -0.088155 | -0.080375 | 121.9552 | 121.7044 | 121.7594 | 62.303 | -121.9784 | 121.8059 | 121.9379 | 121.9457 | 62.3707 | -122.1193
477.7656 | 122.2321 | -62.2696 | 59.8251 | 1.4211e-13 | -0.028664 | -0.0040876 | 0.066007 | -0.005145 | 0.057736 | 0.0021363 | 0.00014315 | -0.0016878 | -0.003226 | 0.02056 | -0.010454 | -62.2925 | 0.019721 | -62.2456 | 59.6719 | 59.4256 | 59.4669 | -62.2449 | -62.2511 | 0.087354 | -62.3543 | 59.518 | 59.6363 | 59.6532 | -62.3811 | 0.024739 | -0.15324 | -0.022906 | 0.024037 | -0.000702 | -0.39949 | -0.35822 | -0.11153 | -0.30718 | 0.0185 | -0.084685 | 0.02684 | -0.18887 | -0.17193 | 121.9415 | 121.6952 | 121.7365 | 62.2893 | -122.07 | 121.7875 | 121.9059 | 121.9228 | 62.3569 | -122.2063
479.5156 | 122.2366 | -62.2787 | 59.816 | 1.4211e-13 | -0.028451 | -0.004515 | 0.065793 | -0.0055724 | 0.057522 | -0.0054937 | 0.00014315 | -0.0019016 | -0.0034396 | 0.020346 | -0.01024 | -62.2971 | 0.005985 | -62.2547 | 59.6719 | 59.4211 | 59.4715 | -62.2449 | -62.2511 | 0.087354 | -62.3589 | 59.5088 | 59.6408 | 59.6486 | -62.3811 | 0.033895 | -0.14408 | -0.018328 | 0.024036 | -0.009859 | -0.39492 | -0.34448 | -0.10237 | -0.30718 | 0.027656 | -0.080108 | 0.022261 | -0.17513 | -0.16735 | 121.9506 | 121.6998 | 121.7502 | 62.2847 | -122.0608 | 121.7875 | 121.9196 | 121.9274 | 62.3661 | -122.1971
481.2031 | 122.3419 | -62.2833 | 59.7427 | 1.4211e-13 | -0.028664 | -0.004515 | 0.065793 | -0.0053586 | 0.057736 | -0.013124 | 0.00035675 | -0.0019016 | -0.0030124 | 0.02056 | -0.01024 | -62.2833 | 0.015142 | -62.2547 | 59.6673 | 59.4256 | 59.4715 | -62.2494 | -62.2602 | 0.082776 | -62.3543 | 59.5088 | 59.6317 | 59.6532 | -62.3765 | 0.033894 | -0.075421 | -1.6e-05 | 0.028613 | -0.005281 | -0.31709 | -0.27124 | -0.093213 | -0.23394 | 0.023076 | -0.070952 | 0.022261 | -0.11105 | -0.089531 | 121.9506 | 121.709 | 121.7548 | 62.2985 | -121.9922 | 121.7921 | 121.915 | 121.9365 | 62.3661 | -122.1193
482.9531 | 122.2275 | -62.3016 | 59.8434 | 1.4211e-13 | -0.028451 | -0.0047286 | 0.065579 | -0.005145 | 0.057736 | -0.0054937 | 0.00057035 | -0.0016878 | -0.0034396 | 0.020773 | -0.0098132 | -62.2879 | 0.010564 | -62.2593 | 59.6673 | 59.4211 | 59.4715 | -62.2403 | -62.2511 | 0.082776 | -62.3543 | 59.5134 | 59.6363 | 59.6532 | -62.3811 | 0.061362 | -0.17613 | 0.013717 | 0.042346 | -0.019016 | -0.42238 | -0.37195 | -0.079481 | -0.33007 | 0.050544 | -0.052641 | 0.02684 | -0.20718 | -0.19024 | 121.969 | 121.7227 | 121.7731 | 62.3122 | -122.0837 | 121.815 | 121.9379 | 121.9548 | 62.3844 | -122.2246
484.6406 | 122.3511 | -62.2604 | 59.7473 | 1.4211e-13 | -0.028451 | -0.0043014 | 0.06622 | -0.0055724 | 0.058163 | -0.0054937 | 0.00035675 | -0.0021152 | -0.0034396 | 0.020773 | -0.01024 | -62.2879 | 0.015142 | -62.2501 | 59.6765 | 59.4211 | 59.4761 | -62.2449 | -62.2557 | 0.078197 | -62.3497 | 59.5042 | 59.6363 | 59.6532 | -62.3811 | 0.015584 | -0.070841 | -0.027482 | 0.010304 | -0.00528 | -0.32625 | -0.27124 | -0.12068 | -0.2431 | 0.004767 | -0.089262 | 0.031418 | -0.11105 | -0.094108 | 121.9369 | 121.6815 | 121.7365 | 62.2756 | -121.9922 | 121.7647 | 121.8967 | 121.9136 | 62.3386 | -122.1284
486.3906 | 122.2595 | -62.2696 | 59.8206 | 1.4211e-13 | -0.028664 | -0.0043014 | 0.065579 | -0.0055724 | 0.057522 | -0.0054937 | 0.00035675 | -0.0016878 | -0.0034396 | 0.02056 | -0.01024 | -62.2879 | 0.010564 | -62.2547 | 59.6719 | 59.4165 | 59.4669 | -62.2449 | -62.2511 | 0.082776 | -62.3589 | 59.5134 | 59.6363 | 59.6486 | -62.3811 | 0.024739 | -0.14866 | -0.018327 | 0.01488 | -0.009859 | -0.40407 | -0.35364 | -0.11153 | -0.30718 | 0.0185 | -0.089264 | 0.022261 | -0.18429 | -0.17193 | 121.9415 | 121.6861 | 121.7365 | 62.2802 | -122.0654 | 121.783 | 121.9059 | 121.9182 | 62.3524 | -122.2017
488.125 | 122.2687 | -62.2742 | 59.8114 | 1.4211e-13 | -0.028451 | -0.004515 | 0.066007 | -0.0055724 | 0.057736 | -0.013124 | 0.00057035 | -0.0021152 | -0.0036534 | 0.02056 | -0.010668 | -62.2925 | 0.015142 | -62.2639 | 59.6765 | 59.4165 | 59.4715 | -62.2449 | -62.2557 | 0.078197 | -62.3543 | 59.5134 | 59.6363 | 59.644 | -62.3811 | 0.029317 | -0.13493 | -0.018328 | 0.010302 | -0.019015 | -0.39492 | -0.3399 | -0.10695 | -0.29802 | 0.0185 | -0.080107 | 0.02684 | -0.17513 | -0.16735 | 121.9506 | 121.6907 | 121.7457 | 62.2893 | -122.0563 | 121.7875 | 121.9104 | 121.9182 | 62.3524 | -122.1925
489.8125 | 122.2137 | -62.2787 | 59.8343 | 1.4211e-13 | -0.028451 | -0.004515 | 0.065793 | -0.0055724 | 0.05795 | 0.0021363 | 0.00057035 | -0.0021152 | -0.003226 | 0.02056 | -0.01024 | -62.2833 | 0.015142 | -62.2547 | 59.6765 | 59.4165 | 59.4715 | -62.2449 | -62.2602 | 0.091933 | -62.3589 | 59.5042 | 59.6317 | 59.6532 | -62.3765 | 0.033895 | -0.15782 | -0.004593 | 0.024036 | -0.009859 | -0.41781 | -0.36279 | -0.09779 | -0.33007 | 0.018499 | -0.080108 | 0.017682 | -0.2026 | -0.18108 | 121.9552 | 121.6952 | 121.7502 | 62.2939 | -122.0791 | 121.783 | 121.9104 | 121.932 | 62.3707 | -122.2108
491.5625 | 122.2824 | -62.2833 | 59.7885 | 1.4211e-13 | -0.028878 | -0.0043014 | 0.065366 | -0.005145 | 0.057522 | -0.0054937 | 0.00099775 | -0.0023288 | -0.003226 | 0.020773 | -0.010454 | -62.2833 | 0.019721 | -62.2547 | 59.6765 | 59.4165 | 59.4715 | -62.2403 | -62.2511 | 0.087354 | -62.3451 | 59.5088 | 59.6408 | 59.6578 | -62.3811 | 0.043051 | -0.11204 | -1.6e-05 | 0.028613 | -0.014438 | -0.37203 | -0.31702 | -0.097792 | -0.27972 | 0.032233 | -0.061795 | 0.035997 | -0.14767 | -0.13073 | 121.9598 | 121.6998 | 121.7548 | 62.303 | -122.0288 | 121.7921 | 121.9242 | 121.9411 | 62.3707 | -122.1696
493.2969 | 122.2961 | -62.2879 | 59.7839 | 1.4211e-13 | -0.028664 | -0.004515 | 0.065793 | -0.0055724 | 0.057522 | -0.0054937 | 0.00057035 | -0.0021152 | -0.003226 | 0.020773 | -0.010027 | -62.2833 | 0.015142 | -62.2593 | 59.6719 | 59.4211 | 59.4715 | -62.2494 | -62.2602 | 0.082776 | -62.3543 | 59.5134 | 59.6454 | 59.6532 | -62.3811 | 0.038472 | -0.11204 | 0.004562 | 0.028613 | -0.009859 | -0.36287 | -0.31244 | -0.093214 | -0.27056 | 0.027654 | -0.066374 | 0.02684 | -0.13851 | -0.13073 | 121.9598 | 121.709 | 121.7594 | 62.303 | -122.0334 | 121.8013 | 121.9333 | 121.9411 | 62.3707 | -122.1651
495.0469 | 122.2458 | -62.265 | 59.8297 | 1.4211e-13 | -0.028878 | -0.004515 | 0.065793 | -0.0053586 | 0.057309 | -0.0054937 | 0.00057035 | -0.0021152 | -0.0034396 | 0.020773 | -0.01024 | -62.2879 | 0.010564 | -62.2547 | 59.6719 | 59.4073 | 59.4623 | -62.2403 | -62.2648 | 0.091933 | -62.3589 | 59.5088 | 59.6408 | 59.6395 | -62.3857 | 0.024741 | -0.15782 | -0.022904 | 0.010303 | -0.014438 | -0.42239 | -0.36737 | -0.12068 | -0.32091 | 0.000187 | -0.093841 | 0.02684 | -0.18886 | -0.19024 | 121.9369 | 121.6723 | 121.7274 | 62.2756 | -122.07 | 121.7738 | 121.9059 | 121.9045 | 62.3569 | -122.2154
496.7969 | 122.287 | -62.2787 | 59.7565 | 1.4211e-13 | -0.029092 | -0.0047286 | 0.065793 | -0.005786 | 0.057522 | -0.013124 | 0.00035675 | -0.0021152 | -0.0034396 | 0.02056 | -0.010027 | -62.2879 | 0.010564 | -62.2593 | 59.6811 | 59.4211 | 59.4761 | -62.2494 | -62.2557 | 0.087354 | -62.3543 | 59.5134 | 59.6363 | 59.6212 | -62.3811 | 0.029317 | -0.075419 | -0.009171 | 0.019458 | -0.009859 | -0.33541 | -0.28039 | -0.10237 | -0.24309 | 0.023078 | -0.075529 | 0.02684 | -0.1202 | -0.13531 | 121.9598 | 121.6998 | 121.7548 | 62.2893 | -122.0059 | 121.7921 | 121.915 | 121.8999 | 62.3661 | -122.1376
498.4688 | 122.2366 | -62.2467 | 59.8389 | 1.4211e-13 | -0.028664 | -0.0047286 | 0.065579 | -0.0053586 | 0.05795 | 0.0097668 | 0.00014315 | -0.0021152 | -0.003226 | 0.02056 | -0.0098132 | -62.2879 | 0.019721 | -62.2501 | 59.6765 | 59.4211 | 59.4715 | -62.2449 | -62.2557 | 0.087354 | -62.3497 | 59.5088 | 59.6363 | 59.644 | -62.3811 | 0.001851 | -0.16239 | -0.041215 | -0.003429 | -0.00528 | -0.4178 | -0.36737 | -0.13441 | -0.33007 | -0.008966 | -0.10299 | 0.031418 | -0.2026 | -0.19482 | 121.9232 | 121.6678 | 121.7182 | 62.2664 | -122.0837 | 121.7555 | 121.883 | 121.8908 | 62.3341 | -122.22
500.2031 | 122.2595 | -62.2604 | 59.7885 | 1.4211e-13 | -0.028664 | -0.0043014 | 0.065793 | -0.0055724 | 0.057522 | -0.020755 | 0.00035675 | -0.0019016 | -0.0030124 | 0.020773 | -0.01024 | -62.2879 | 0.010564 | -62.2547 | 59.6719 | 59.4165 | 59.4669 | -62.2494 | -62.2557 | 0.087354 | -62.3589 | 59.5088 | 59.6363 | 59.6532 | -62.372 | 0.011006 | -0.11662 | -0.027482 | 0.005725 | -0.005281 | -0.37203 | -0.32159 | -0.11152 | -0.27972 | 0.004767 | -0.098419 | 0.013103 | -0.15225 | -0.13531 | 121.9323 | 121.6769 | 121.7274 | 62.271 | -122.0379 | 121.7692 | 121.8967 | 121.9136 | 62.3478 | -122.1605
501.9375 | 122.3373 | -62.2971 | 59.7519 | 1.4211e-13 | -0.029092 | -0.0040876 | 0.065793 | -0.005786 | 0.057522 | -0.013124 | 0.00014315 | -0.0023288 | -0.0034396 | 0.020987 | -0.01024 | -62.2879 | 0.005985 | -62.2547 | 59.6719 | 59.4256 | 59.4669 | -62.2449 | -62.2602 | 0.087354 | -62.3543 | 59.5134 | 59.6408 | 59.6578 | -62.3765 | 0.052205 | -0.079998 | 0.009139 | 0.042346 | -0.009859 | -0.32625 | -0.28497 | -0.07948 | -0.23852 | 0.036809 | -0.057219 | 0.022261 | -0.11104 | -0.094108 | 121.969 | 121.7227 | 121.764 | 62.303 | -121.9967 | 121.8104 | 121.9379 | 121.9548 | 62.3844 | -122.1284
503.625 | 122.3236 | -62.2696 | 59.7885 | 1.4211e-13 | -0.028451 | -0.0047286 | 0.065579 | -0.0053586 | 0.057522 | 0.0021363 | 0.00014315 | -0.0021152 | -0.003226 | 0.02056 | -0.01024 | -62.2833 | 0.005985 | -62.2547 | 59.6719 | 59.4256 | 59.4715 | -62.2403 | -62.2602 | 0.096512 | -62.3543 | 59.5088 | 59.6363 | 59.6532 | -62.3811 | 0.029318 | -0.11662 | -0.013749 | 0.01488 | -0.014438 | -0.36287 | -0.31702 | -0.11153 | -0.27972 | 0.009343 | -0.084685 | 0.02684 | -0.15225 | -0.13531 | 121.9415 | 121.6952 | 121.7411 | 62.2756 | -122.0288 | 121.7784 | 121.9059 | 121.9228 | 62.3661 | -122.1696
505.375 | 122.3602 | -62.2559 | 59.7702 | 1.4211e-13 | -0.028664 | -0.0047286 | 0.065793 | -0.0053586 | 0.057736 | -0.0054937 | 0.00035675 | -0.0021152 | -0.0036534 | 0.020773 | -0.010027 | -62.2788 | 0.015142 | -62.2547 | 59.6765 | 59.4211 | 59.4669 | -62.2449 | -62.2511 | 0.082776 | -62.3589 | 59.5134 | 59.6408 | 59.6532 | -62.3811 | 0.011006 | -0.09373 | -0.022904 | 0.001147 | -0.009859 | -0.34914 | -0.30328 | -0.12526 | -0.25683 | 0.004767 | -0.103 | 0.022261 | -0.12936 | -0.117 | 121.9323 | 121.6769 | 121.7228 | 62.271 | -122.0151 | 121.7692 | 121.8967 | 121.9091 | 62.3386 | -122.1513
507.125 | 122.3511 | -62.2742 | 59.7244 | 1.4211e-13 | -0.028878 | -0.004515 | 0.066007 | -0.0055724 | 0.057736 | -0.0054937 | 0.00035675 | -0.0021152 | -0.0036534 | 0.020987 | -0.01024 | -62.2879 | 0.010564 | -62.2593 | 59.6719 | 59.4256 | 59.4669 | -62.254 | -62.2602 | 0.087354 | -62.3497 | 59.5088 | 59.6454 | 59.6532 | -62.3765 | 0.02016 | -0.052532 | -0.013749 | 0.01488 | -0.00528 | -0.29878 | -0.25751 | -0.10237 | -0.21563 | 0.013921 | -0.075529 | 0.026839 | -0.079 | -0.07122 | 121.9461 | 121.6998 | 121.7411 | 62.2847 | -121.9784 | 121.783 | 121.9196 | 121.9274 | 62.3615 | -122.101
508.7969 | 122.2961 | -62.2742 | 59.7565 | 1.4211e-13 | -0.028878 | -0.0043014 | 0.065793 | -0.005145 | 0.05795 | -0.0054937 | 0.00035675 | -0.0019016 | -0.0034396 | 0.020346 | -0.01024 | -62.2879 | 0.019721 | -62.2593 | 59.6811 | 59.4256 | 59.4761 | -62.254 | -62.2602 | 0.091933 | -62.3589 | 59.5088 | 59.6363 | 59.6532 | -62.3765 | 0.02016 | -0.075419 | -0.013749 | 0.01488 | -0.00528 | -0.33083 | -0.28039 | -0.10237 | -0.24767 | 0.013921 | -0.084686 | 0.017682 | -0.1202 | -0.10326 | 121.9552 | 121.6998 | 121.7502 | 62.2939 | -122.0105 | 121.783 | 121.9104 | 121.9274 | 62.3661 | -122.133
510.5312 | 122.3373 | -62.2559 | 59.7931 | 1.4211e-13 | -0.029092 | -0.0049424 | 0.065366 | -0.0053586 | 0.057522 | -0.0054937 | 0.00035675 | -0.0016878 | -0.0030124 | 0.020773 | -0.01024 | -62.2925 | 0.010564 | -62.2593 | 59.6765 | 59.4211 | 59.4669 | -62.2449 | -62.2602 | 0.082776 | -62.3497 | 59.5088 | 59.6317 | 59.6578 | -62.3857 | 0.011006 | -0.11662 | -0.036639 | -0.003431 | -0.014437 | -0.37203 | -0.32617 | -0.12984 | -0.28429 | -0.00439 | -0.09384 | 0.035997 | -0.1614 | -0.13531 | 121.9323 | 121.6769 | 121.7228 | 62.2664 | -122.0379 | 121.7647 | 121.8875 | 121.9136 | 62.3386 | -122.1788
512.2812 | 122.3007 | -62.2925 | 59.7656 | 1.4211e-13 | -0.028878 | -0.004515 | 0.065793 | -0.0055724 | 0.05795 | 0.0021363 | 0.00035675 | -0.0016878 | -0.0034396 | 0.020987 | -0.010027 | -62.2833 | 0.015142 | -62.2547 | 59.6765 | 59.4302 | 59.4715 | -62.2494 | -62.2602 | 0.082776 | -62.3497 | 59.5134 | 59.6317 | 59.6578 | -62.3857 | 0.043049 | -0.089152 | 0.009139 | 0.037768 | -0.005281 | -0.3354 | -0.29413 | -0.093216 | -0.25225 | 0.032231 | -0.057219 | 0.035997 | -0.13394 | -0.10784 | 121.969 | 121.7227 | 121.764 | 62.3076 | -122.0151 | 121.8059 | 121.9242 | 121.9503 | 62.3753 | -122.1513
514.0156 | 122.3328 | -62.2513 | 59.7748 | 1.4211e-13 | -0.028878 | -0.004515 | 0.066007 | -0.005786 | 0.057736 | -0.0054937 | 0.00035675 | -0.0016878 | -0.0034396 | 0.020773 | -0.01024 | -62.2879 | 0.015142 | -62.2501 | 59.6719 | 59.4165 | 59.4807 | -62.2449 | -62.2557 | 0.091933 | -62.3543 | 59.5088 | 59.6317 | 59.6532 | -62.3811 | 0.006429 | -0.10289 | -0.036637 | 0.001149 | -0.00528 | -0.3583 | -0.29413 | -0.12983 | -0.26598 | -0.004388 | -0.10299 | 0.02684 | -0.14309 | -0.12157 | 121.9232 | 121.6678 | 121.7319 | 62.2664 | -122.0196 | 121.7601 | 121.883 | 121.9045 | 62.3432 | -122.1559
515.6875 | 122.2595 | -62.2833 | 59.816 | 1.4211e-13 | -0.028878 | -0.0049424 | 0.065793 | -0.0053586 | 0.057736 | -0.0054937 | 0.00057035 | -0.0014742 | -0.003226 | 0.021414 | -0.010454 | -62.2925 | 0.015142 | -62.2593 | 59.6765 | 59.4211 | 59.4715 | -62.254 | -62.2602 | 0.087354 | -62.3634 | 59.5134 | 59.6317 | 59.6486 | -62.3765 | 0.029315 | -0.13951 | -0.009173 | 0.024035 | -0.00528 | -0.39492 | -0.34448 | -0.093213 | -0.3026 | 0.023076 | -0.08011 | 0.013103 | -0.18429 | -0.16735 | 121.9598 | 121.7044 | 121.7548 | 62.2985 | -122.07 | 121.7967 | 121.915 | 121.932 | 62.3707 | -122.1925
517.4375 | 122.2595 | -62.2696 | 59.8068 | 1.4211e-13 | -0.028878 | -0.004515 | 0.065579 | -0.0053586 | 0.057736 | 0.0021363 | 0.00078395 | -0.0023288 | -0.0036534 | 0.020987 | -0.010027 | -62.2879 | 0.010564 | -62.2593 | 59.6765 | 59.4256 | 59.4715 | -62.2449 | -62.2557 | 0.087354 | -62.3634 | 59.5134 | 59.6408 | 59.6532 | -62.3765 | 0.024739 | -0.13035 | -0.018327 | 0.010302 | -0.014437 | -0.38118 | -0.33533 | -0.10695 | -0.29345 | 0.013922 | -0.093843 | 0.013103 | -0.16598 | -0.15362 | 121.9461 | 121.6952 | 121.7411 | 62.2802 | -122.0517 | 121.783 | 121.9104 | 121.9228 | 62.3569 | -122.1834
519.1719 | 122.2733 | -62.2971 | 59.7748 | 1.4211e-13 | -0.029092 | -0.0047286 | 0.066007 | -0.0055724 | 0.05795 | -0.0054937 | 0.00057035 | -0.0021152 | -0.003226 | 0.02056 | -0.01024 | -62.2833 | 0.015142 | -62.2547 | 59.6719 | 59.4256 | 59.4715 | -62.2494 | -62.2557 | 0.087354 | -62.3543 | 59.5042 | 59.6317 | 59.6578 | -62.3765 | 0.047627 | -0.10289 | 0.013717 | 0.042346 | -0.005281 | -0.34914 | -0.30328 | -0.07948 | -0.27056 | 0.041388 | -0.057219 | 0.022261 | -0.14309 | -0.117 | 121.969 | 121.7227 | 121.7686 | 62.3122 | -122.0242 | 121.8013 | 121.9287 | 121.9548 | 62.3844 | -122.1513
520.8594 | 122.2046 | -62.2833 | 59.8434 | 1.4211e-13 | -0.028878 | -0.004515 | 0.065579 | -0.0053586 | 0.057522 | 0.0021363 | 0.00035675 | -0.0019016 | -0.0027988 | 0.020987 | -0.010454 | -62.2879 | 0.010564 | -62.2639 | 59.6719 | 59.4211 | 59.4761 | -62.2449 | -62.2557 | 0.082776 | -62.3543 | 59.5134 | 59.6271 | 59.6486 | -62.3811 | 0.038472 | -0.17155 | -0.004594 | 0.019457 | -0.019015 | -0.42238 | -0.36737 | -0.097792 | -0.33007 | 0.027655 | -0.070952 | 0.02684 | -0.21633 | -0.19482 | 121.9552 | 121.7044 | 121.7594 | 62.2939 | -122.0883 | 121.7967 | 121.9104 | 121.932 | 62.3661 | -122.2246
522.625 | 122.2137 | -62.2971 | 59.8022 | 1.4211e-13 | -0.029305 | -0.004515 | 0.065793 | -0.005786 | 0.057309 | -0.0054937 | 0.00078395 | -0.0021152 | -0.003226 | 0.020987 | -0.010027 | -62.2925 | 0.005985 | -62.2593 | 59.6719 | 59.4256 | 59.4715 | -62.2403 | -62.2511 | 0.082776 | -62.3634 | 59.5088 | 59.6363 | 59.6532 | -62.3811 | 0.056784 | -0.13035 | 0.00456 | 0.037768 | -0.019016 | -0.3766 | -0.33075 | -0.084059 | -0.29345 | 0.045966 | -0.066377 | 0.017682 | -0.16598 | -0.14904 | 121.969 | 121.7227 | 121.7686 | 62.303 | -122.0425 | 121.8059 | 121.9333 | 121.9503 | 62.3798 | -122.1834
524.3594 | 122.2366 | -62.3062 | 59.8114 | 1.4211e-13 | -0.029092 | -0.0043014 | 0.065793 | -0.0055724 | 0.057522 | -0.0054937 | 0.00078395 | -0.0023288 | -0.003226 | 0.020987 | -0.01024 | -62.2879 | 0.010564 | -62.2593 | 59.6765 | 59.4256 | 59.4761 | -62.2449 | -62.2602 | 0.087354 | -62.3589 | 59.5134 | 59.6317 | 59.6486 | -62.3857 | 0.06136 | -0.13493 | 0.018294 | 0.046923 | -0.014437 | -0.38576 | -0.33532 | -0.079483 | -0.29802 | 0.045964 | -0.052643 | 0.02684 | -0.17971 | -0.16277 | 121.9827 | 121.7319 | 121.7823 | 62.3168 | -122.0563 | 121.8196 | 121.9379 | 121.9548 | 62.3936 | -122.1971
526.1094 | 122.2916 | -62.2879 | 59.7656 | 1.4211e-13 | -0.029092 | -0.0047286 | 0.065793 | -0.0055724 | 0.057522 | -0.0054937 | 0.00035675 | -0.0016878 | -0.0034396 | 0.020987 | -0.010454 | -62.2925 | 0.005985 | -62.2593 | 59.6811 | 59.4256 | 59.4761 | -62.2449 | -62.2557 | 0.091933 | -62.3497 | 59.5134 | 59.6317 | 59.6486 | -62.3903 | 0.04305 | -0.084574 | -0.004595 | 0.028613 | -0.014437 | -0.33998 | -0.28955 | -0.10237 | -0.25225 | 0.032233 | -0.061796 | 0.040575 | -0.13394 | -0.117 | 121.969 | 121.7135 | 121.764 | 62.2939 | -122.0105 | 121.8013 | 121.9196 | 121.9365 | 62.3798 | -122.1559
527.8594 | 122.2321 | -62.3108 | 59.8022 | 1.4211e-13 | -0.028878 | -0.0047286 | 0.065793 | -0.0055724 | 0.057522 | -0.0054937 | 0.00057035 | -0.0019016 | -0.003226 | 0.020773 | -0.010027 | -62.2925 | 0.010564 | -62.2547 | 59.6765 | 59.4302 | 59.4715 | -62.2494 | -62.2511 | 0.082776 | -62.3497 | 59.518 | 59.6317 | 59.6624 | -62.3857 | 0.06136 | -0.12577 | 0.018293 | 0.056079 | -0.005281 | -0.37202 | -0.33075 | -0.074905 | -0.28429 | 0.059699 | -0.038908 | 0.035997 | -0.17056 | -0.13988 | 121.9873 | 121.741 | 121.7823 | 62.3214 | -122.0517 | 121.8287 | 121.9425 | 121.9732 | 62.3936 | -122.1879
529.5469 | 122.2321 | -62.2742 | 59.8389 | 1.4211e-13 | -0.029092 | -0.004515 | 0.065793 | -0.0055724 | 0.057736 | -0.0054937 | 0.00035675 | -0.0019016 | -0.0034396 | 0.02056 | -0.01024 | -62.2833 | 0.005985 | -62.2547 | 59.6765 | 59.4256 | 59.4761 | -62.2494 | -62.2602 | 0.091933 | -62.3543 | 59.5088 | 59.6408 | 59.6532 | -62.3903 | 0.024739 | -0.16239 | -0.009171 | 0.019458 | -0.005281 | -0.41322 | -0.36279 | -0.1161 | -0.33007 | 0.013921 | -0.080107 | 0.035997 | -0.19802 | -0.18566 | 121.9506 | 121.6998 | 121.7502 | 62.2802 | -122.0883 | 121.783 | 121.915 | 121.9274 | 62.3661 | -122.2291
531.2812 | 122.3465 | -62.2604 | 59.7702 | 1.4211e-13 | -0.029305 | -0.0047286 | 0.065793 | -0.0053586 | 0.057095 | 0.0021363 | 0.00014315 | -0.0019016 | -0.0034396 | 0.020987 | -0.01024 | -62.2833 | 0.010564 | -62.2547 | 59.6719 | 59.4211 | 59.4807 | -62.2449 | -62.2465 | 0.082776 | -62.3543 | 59.5042 | 59.6408 | 59.6486 | -62.3857 | 0.015584 | -0.098309 | -0.022904 | 0.005725 | -0.009859 | -0.34914 | -0.28955 | -0.12526 | -0.26598 | 0.013924 | -0.09384 | 0.031419 | -0.12936 | -0.12158 | 121.9323 | 121.6815 | 121.7411 | 62.271 | -122.0151 | 121.7647 | 121.9013 | 121.9091 | 62.3432 | -122.1559
533.0312 | 122.2549 | -62.2696 | 59.8022 | 1.4211e-13 | -0.028878 | -0.0043014 | 0.065366 | -0.0055724 | 0.05795 | -0.0054937 | 0.00014315 | -0.0019016 | -0.0034396 | 0.020987 | -0.01024 | -62.2879 | 0.010564 | -62.2547 | 59.6719 | 59.4256 | 59.4715 | -62.2449 | -62.2602 | 0.082776 | -62.3589 | 59.5134 | 59.6317 | 59.6486 | -62.3903 | 0.024739 | -0.13035 | -0.018327 | 0.01488 | -0.009859 | -0.3766 | -0.33075 | -0.12068 | -0.28887 | 0.009343 | -0.089264 | 0.031418 | -0.17056 | -0.15362 | 121.9415 | 121.6952 | 121.7411 | 62.2802 | -122.0471 | 121.783 | 121.9013 | 121.9182 | 62.3524 | -122.1925
534.7188 | 122.374 | -62.265 | 59.7794 | 1.4211e-13 | -0.029092 | -0.004515 | 0.065793 | -0.0055724 | 0.057095 | 0.0021363 | 0.00078395 | -0.0019016 | -0.0034396 | 0.020987 | -0.010668 | -62.2879 | 0.010564 | -62.2547 | 59.6765 | 59.4256 | 59.4761 | -62.2449 | -62.2602 | 0.082776 | -62.3543 | 59.5134 | 59.6363 | 59.6486 | -62.3903 | 0.020162 | -0.10289 | -0.022904 | 0.010303 | -0.009859 | -0.35372 | -0.30328 | -0.12526 | -0.26598 | 0.004766 | -0.089262 | 0.035997 | -0.14309 | -0.13073 | 121.9415 | 121.6907 | 121.7411 | 62.2756 | -122.0242 | 121.7784 | 121.9013 | 121.9136 | 62.3478 | -122.1696
536.4531 | 122.2549 | -62.2696 | 59.8343 | 1.4211e-13 | -0.029092 | -0.0047286 | 0.066007 | -0.0053586 | 0.057309 | -0.0054937 | 0.00057035 | -0.0021152 | -0.0036534 | 0.020773 | -0.01024 | -62.2925 | 0.005985 | -62.2684 | 59.6719 | 59.4211 | 59.4761 | -62.2494 | -62.2511 | 0.082776 | -62.3589 | 59.5225 | 59.65 | 59.6578 | -62.3811 | 0.020161 | -0.1624 | -0.022906 | 0.001146 | -0.019015 | -0.41323 | -0.35821 | -0.11153 | -0.31176 | 0.0185 | -0.089264 | 0.022261 | -0.18429 | -0.17651 | 121.9415 | 121.6907 | 121.7457 | 62.2756 | -122.0837 | 121.7921 | 121.9196 | 121.9274 | 62.3524 | -122.2154
538.2031 | 122.2595 | -62.2604 | 59.8572 | 1.4211e-13 | -0.029305 | -0.0047286 | 0.065579 | -0.005786 | 0.057309 | -0.0054937 | 0.00014315 | -0.0021152 | -0.003226 | 0.021201 | -0.010027 | -62.2833 | 0.005985 | -62.2593 | 59.6719 | 59.4211 | 59.4761 | -62.2494 | -62.2602 | 0.091933 | -62.3543 | 59.5271 | 59.6363 | 59.6578 | -62.3857 | 0.011006 | -0.18528 | -0.022904 | 0.001147 | -0.009859 | -0.43612 | -0.3811 | -0.12526 | -0.33007 | 0.000188 | -0.09384 | 0.031419 | -0.22091 | -0.19939 | 121.9323 | 121.6815 | 121.7365 | 62.2664 | -122.1066 | 121.7875 | 121.8967 | 121.9182 | 62.3524 | -122.2429
539.8906 | 122.3602 | -62.2879 | 59.729 | 1.4211e-13 | -0.029305 | -0.004515 | 0.065793 | -0.005786 | 0.057309 | 0.0021363 | 0.00057035 | -0.0021152 | -0.0034396 | 0.021201 | -0.010454 | -62.2879 | 0.015142 | -62.2593 | 59.6765 | 59.4348 | 59.4715 | -62.2449 | -62.2602 | 0.082776 | -62.3589 | 59.518 | 59.6408 | 59.6486 | -62.3857 | 0.04305 | -0.052531 | -1.6e-05 | 0.028613 | -0.014437 | -0.2942 | -0.25751 | -0.097793 | -0.21105 | 0.027654 | -0.070953 | 0.02684 | -0.088157 | -0.080377 | 121.9644 | 121.7227 | 121.7594 | 62.303 | -121.9739 | 121.8059 | 121.9287 | 121.9365 | 62.3707 | -122.1147
541.6406 | 122.2366 | -62.2971 | 59.8618 | 1.4211e-13 | -0.029305 | -0.0049424 | 0.065793 | -0.005786 | 0.057522 | -0.0054937 | 0.00035675 | -0.0023288 | -0.0034396 | 0.020987 | -0.010027 | -62.2879 | 0.010564 | -62.2547 | 59.6765 | 59.4211 | 59.4761 | -62.2494 | -62.2557 | 0.087354 | -62.3543 | 59.5134 | 59.6408 | 59.6486 | -62.3903 | 0.047627 | -0.18528 | 0.009139 | 0.042346 | -0.005281 | -0.44069 | -0.38568 | -0.093216 | -0.34838 | 0.041388 | -0.057219 | 0.035997 | -0.22091 | -0.21313 | 121.9735 | 121.7181 | 121.7731 | 62.3076 | -122.1112 | 121.8104 | 121.9379 | 121.9457 | 62.3844 | -122.252
543.375 | 122.2549 | -62.2971 | 59.8022 | 1.4211e-13 | -0.029092 | -0.0049424 | 0.065152 | -0.0062134 | 0.057309 | -0.0054937 | 0.00035675 | -0.0019016 | -0.0036534 | 0.020987 | -0.010027 | -62.2833 | 0.010564 | -62.2593 | 59.6765 | 59.4211 | 59.4807 | -62.254 | -62.2511 | 0.082776 | -62.3497 | 59.5088 | 59.6408 | 59.6532 | -62.3811 | 0.043048 | -0.12577 | 0.013717 | 0.037768 | -0.00528 | -0.38118 | -0.32159 | -0.084059 | -0.29345 | 0.045966 | -0.052641 | 0.031418 | -0.1614 | -0.14904 | 121.9735 | 121.7181 | 121.7777 | 62.3076 | -122.0563 | 121.8059 | 121.9379 | 121.9503 | 62.3798 | -122.1834
545.125 | 122.2961 | -62.2879 | 59.7931 | 1.4211e-13 | -0.029305 | -0.0047286 | 0.066007 | -0.005786 | 0.057309 | 0.0021363 | 0.00057035 | -0.0016878 | -0.0034396 | 0.021201 | -0.01024 | -62.2925 | 0.015142 | -62.2593 | 59.6719 | 59.4256 | 59.4761 | -62.2449 | -62.2557 | 0.087354 | -62.3589 | 59.5134 | 59.6408 | 59.6578 | -62.3903 | 0.04305 | -0.1212 | -0.004595 | 0.028613 | -0.014437 | -0.36745 | -0.31701 | -0.10237 | -0.27971 | 0.032233 | -0.070953 | 0.031418 | -0.15224 | -0.13531 | 121.9598 | 121.7135 | 121.764 | 62.303 | -122.0379 | 121.8013 | 121.9287 | 121.9457 | 62.3753 | -122.1834
546.8125 | 122.2137 | -62.3199 | 59.7931 | 1.4211e-13 | -0.029092 | -0.004515 | 0.066007 | -0.005786 | 0.057522 | -0.0054937 | 0.00057035 | -0.0019016 | -0.0034396 | 0.020987 | -0.01024 | -62.2879 | 0.010564 | -62.2639 | 59.6765 | 59.4302 | 59.4761 | -62.2494 | -62.2602 | 0.087354 | -62.3543 | 59.5134 | 59.6408 | 59.6578 | -62.3857 | 0.070515 | -0.11662 | 0.032027 | 0.056078 | -0.014437 | -0.36287 | -0.31701 | -0.06575 | -0.27971 | 0.059697 | -0.034331 | 0.031419 | -0.15224 | -0.13531 | 121.9964 | 121.7502 | 121.796 | 62.3305 | -122.0425 | 121.8333 | 121.9608 | 121.9777 | 62.4073 | -122.1788
548.5469 | 122.287 | -62.2879 | 59.7656 | 1.4211e-13 | -0.029733 | -0.004515 | 0.065579 | -0.0055724 | 0.057309 | -0.013124 | 0.00078395 | -0.0021152 | -0.0034396 | 0.021414 | -0.010027 | -62.2833 | 0.005985 | -62.2593 | 59.6765 | 59.4302 | 59.4715 | -62.2449 | -62.2557 | 0.087354 | -62.3543 | 59.5134 | 59.6408 | 59.6578 | -62.3903 | 0.04305 | -0.089152 | 0.004562 | 0.028613 | -0.014437 | -0.3354 | -0.29413 | -0.10237 | -0.25225 | 0.032233 | -0.066374 | 0.035997 | -0.12478 | -0.10784 | 121.9644 | 121.7181 | 121.7594 | 62.2939 | -122.0105 | 121.8013 | 121.9287 | 121.9457 | 62.3753 | -122.1559
550.2188 | 122.3236 | -62.2559 | 59.7885 | 1.4211e-13 | -0.029519 | -0.0047286 | 0.065579 | -0.0059996 | 0.057522 | -0.0054937 | 0.00035675 | -0.0021152 | -0.0034396 | 0.020987 | -0.01024 | -62.2925 | 0.010564 | -62.2593 | 59.6765 | 59.4256 | 59.4761 | -62.2494 | -62.2602 | 0.087354 | -62.3543 | 59.5134 | 59.6408 | 59.6486 | -62.3811 | 0.006428 | -0.11204 | -0.036639 | -0.003431 | -0.009859 | -0.36287 | -0.31244 | -0.12526 | -0.27514 | -0.00439 | -0.098418 | 0.02684 | -0.14767 | -0.13989 | 121.9323 | 121.6815 | 121.7319 | 62.2664 | -122.0379 | 121.7692 | 121.8967 | 121.9045 | 62.3432 | -122.1696
551.9844 | 122.3373 | -62.2559 | 59.7839 | 1.4211e-13 | -0.029733 | -0.0049424 | 0.065793 | -0.0055724 | 0.057522 | -0.0054937 | 0.00057035 | -0.0023288 | -0.0034396 | 0.020987 | -0.01024 | -62.2879 | 0.015142 | -62.2639 | 59.6719 | 59.4211 | 59.4715 | -62.254 | -62.2557 | 0.087354 | -62.3451 | 59.5134 | 59.6363 | 59.6578 | -62.3857 | 0.001849 | -0.11204 | -0.03206 | -0.008009 | -0.009858 | -0.36287 | -0.31244 | -0.12984 | -0.27056 | 0.000189 | -0.089261 | 0.040576 | -0.14767 | -0.12615 | 121.9278 | 121.6769 | 121.7274 | 62.271 | -122.0379 | 121.7692 | 121.8921 | 121.9136 | 62.3432 | -122.1696
553.7188 | 122.3373 | -62.265 | 59.7931 | 1.4211e-13 | -0.029092 | -0.0047286 | 0.065579 | -0.0053586 | 0.057309 | -0.013124 | 0.00057035 | -0.0021152 | -0.0034396 | 0.020987 | -0.01024 | -62.2925 | 0.015142 | -62.2593 | 59.6719 | 59.4256 | 59.4807 | -62.2586 | -62.2602 | 0.087354 | -62.3589 | 59.5134 | 59.6408 | 59.6486 | -62.3857 | 0.006426 | -0.1212 | -0.027483 | 0.005725 | -0.000701 | -0.36745 | -0.31244 | -0.12068 | -0.27971 | 0.004766 | -0.093841 | 0.02684 | -0.15224 | -0.14446 | 121.9369 | 121.6907 | 121.7457 | 62.2802 | -122.0517 | 121.7784 | 121.9059 | 121.9136 | 62.3524 | -122.1788
555.4688 | 122.3557 | -62.2284 | 59.761 | 1.4211e-13 | -0.029305 | -0.004515 | 0.065793 | -0.0055724 | 0.057309 | 0.0021363 | 0.00057035 | -0.0019016 | -0.0030124 | 0.021201 | -0.010454 | -62.2879 | 0.010564 | -62.2593 | 59.6811 | 59.4211 | 59.4807 | -62.2494 | -62.2602 | 0.087354 | -62.3589 | 59.5088 | 59.6363 | 59.6303 | -62.3811 | -0.021037 | -0.079996 | -0.059525 | -0.030896 | -0.009859 | -0.33998 | -0.28039 | -0.15272 | -0.25225 | -0.031855 | -0.13046 | 0.022261 | -0.12478 | -0.13073 | 121.9094 | 121.6495 | 121.709 | 62.239 | -122.0105 | 121.7372 | 121.8647 | 121.8587 | 62.3157 | -122.1422
557.2344 | 122.3694 | -62.2604 | 59.7748 | 1.4211e-13 | -0.029519 | -0.004515 | 0.066007 | -0.0055724 | 0.057522 | -0.0054937 | 0.00057035 | -0.0019016 | -0.003226 | 0.021414 | -0.010454 | -62.2833 | 0.010564 | -62.2593 | 59.6811 | 59.4256 | 59.4715 | -62.2449 | -62.2557 | 0.091933 | -62.3589 | 59.5134 | 59.6408 | 59.6669 | -62.3857 | 0.015584 | -0.093729 | -0.022904 | 0.001147 | -0.014437 | -0.34914 | -0.30328 | -0.12526 | -0.2614 | 0.004767 | -0.098419 | 0.02684 | -0.13393 | -0.10784 | 121.9415 | 121.6861 | 121.7319 | 62.271 | -122.0196 | 121.7738 | 121.9013 | 121.9274 | 62.3524 | -122.1605
558.9062 | 122.2229 | -62.2787 | 59.8434 | 1.4211e-13 | -0.029519 | -0.0047286 | 0.065579 | -0.0055724 | 0.057522 | -0.0054937 | 0.00057035 | -0.0023288 | -0.0034396 | 0.020987 | -0.010454 | -62.2925 | 0.010564 | -62.2547 | 59.6765 | 59.4302 | 59.4807 | -62.2449 | -62.2602 | 0.091933 | -62.3589 | 59.5134 | 59.6408 | 59.6486 | -62.3949 | 0.033895 | -0.16697 | -0.01375 | 0.024036 | -0.009859 | -0.41322 | -0.36279 | -0.1161 | -0.33007 | 0.018499 | -0.080108 | 0.035997 | -0.2026 | -0.19482 | 121.9552 | 121.709 | 121.7594 | 62.2893 | -122.0883 | 121.7921 | 121.9196 | 121.9274 | 62.3707 | -122.2383
560.6562 | 122.3053 | -62.2742 | 59.7702 | 1.4211e-13 | -0.029519 | -0.0047286 | 0.065793 | -0.0055724 | 0.057309 | 0.0097668 | 0.00057035 | -0.0021152 | -0.0034396 | 0.021201 | -0.010027 | -62.2879 | 0.015142 | -62.2593 | 59.6765 | 59.4302 | 59.4807 | -62.2494 | -62.2602 | 0.091933 | -62.3589 | 59.5225 | 59.6363 | 59.6532 | -62.3857 | 0.024739 | -0.09373 | -0.013749 | 0.01488 | -0.009859 | -0.33998 | -0.28955 | -0.11153 | -0.24767 | 0.013921 | -0.084686 | 0.02684 | -0.13394 | -0.117 | 121.9506 | 121.7044 | 121.7548 | 62.2893 | -122.0196 | 121.7967 | 121.9104 | 121.9274 | 62.3661 | -122.1559
562.4062 | 122.3145 | -62.2742 | 59.7519 | 1.4211e-13 | -0.029519 | -0.004515 | 0.065793 | -0.0059996 | 0.057522 | -0.013124 | 0.00035675 | -0.0016878 | -0.0034396 | 0.020987 | -0.010454 | -62.2879 | 0.001407 | -62.2547 | 59.6811 | 59.4256 | 59.4761 | -62.2449 | -62.2557 | 0.091933 | -62.3497 | 59.5134 | 59.6363 | 59.6532 | -62.3949 | 0.029317 | -0.070841 | -0.013749 | 0.019458 | -0.009859 | -0.32625 | -0.27582 | -0.12068 | -0.23852 | 0.0185 | -0.075529 | 0.045154 | -0.11562 | -0.098686 | 121.9552 | 121.6998 | 121.7502 | 62.2756 | -121.9967 | 121.7875 | 121.9104 | 121.9274 | 62.3661 | -122.1467
564.1406 | 122.3236 | -62.2421 | 59.8068 | 1.4211e-13 | -0.029519 | -0.0047286 | 0.065579 | -0.0059996 | 0.057736 | -0.0054937 | 0.00057035 | -0.0021152 | -0.003226 | 0.021201 | -0.01024 | -62.2879 | 0.015142 | -62.2593 | 59.6719 | 59.4256 | 59.4852 | -62.2494 | -62.2602 | 0.087354 | -62.3497 | 59.5225 | 59.6271 | 59.6624 | -62.3811 | -0.007305 | -0.13493 | -0.045793 | -0.017164 | -0.009859 | -0.38118 | -0.32159 | -0.13899 | -0.28429 | -0.018123 | -0.10757 | 0.031418 | -0.17971 | -0.14446 | 121.914 | 121.6678 | 121.7274 | 62.2573 | -122.0563 | 121.7647 | 121.8692 | 121.9045 | 62.3295 | -122.1879
565.8125 | 122.2595 | -62.2559 | 59.7931 | 1.4211e-13 | -0.029519 | -0.004515 | 0.066007 | -0.0053586 | 0.057522 | -0.013124 | 0.00078395 | -0.0023288 | -0.0036534 | 0.021201 | -0.01024 | -62.2879 | 0.019721 | -62.2547 | 59.6765 | 59.4348 | 59.4761 | -62.2449 | -62.2602 | 0.087354 | -62.3589 | 59.5134 | 59.6454 | 59.6578 | -62.3903 | 0.011006 | -0.11662 | -0.03206 | 0.001147 | -0.009859 | -0.35829 | -0.31701 | -0.13441 | -0.27971 | -0.00439 | -0.103 | 0.031418 | -0.14766 | -0.13531 | 121.9323 | 121.6907 | 121.7319 | 62.2756 | -122.0379 | 121.7692 | 121.9013 | 121.9136 | 62.3432 | -122.1834
567.5781 | 122.3511 | -62.2879 | 59.7656 | 1.4211e-13 | -0.029519 | -0.004515 | 0.065579 | -0.0055724 | 0.057736 | 0.0097668 | 0.00035675 | -0.0019016 | -0.003226 | 0.021201 | -0.010454 | -62.2833 | 0.015142 | -62.2639 | 59.6765 | 59.4256 | 59.4715 | -62.2494 | -62.2602 | 0.087354 | -62.3634 | 59.5134 | 59.6317 | 59.6578 | -62.3811 | 0.038472 | -0.089152 | 0.004562 | 0.024035 | -0.014437 | -0.33998 | -0.29413 | -0.093214 | -0.25225 | 0.027654 | -0.075532 | 0.017682 | -0.13394 | -0.10784 | 121.9644 | 121.7135 | 121.7594 | 62.303 | -122.0151 | 121.8013 | 121.9196 | 121.9457 | 62.3753 | -122.1467
569.2656 | 122.2137 | -62.2833 | 59.7839 | 1.4211e-13 | -0.029946 | -0.004515 | 0.065366 | -0.005786 | 0.057522 | -0.0054937 | 0.00078395 | -0.0019016 | -0.0034396 | 0.021414 | -0.01024 | -62.2879 | 0.005985 | -62.2593 | 59.6765 | 59.4302 | 59.4761 | -62.2494 | -62.2511 | 0.091933 | -62.3589 | 59.518 | 59.6408 | 59.6669 | -62.3857 | 0.033894 | -0.10746 | -0.004594 | 0.024035 | -0.009859 | -0.35371 | -0.30786 | -0.10237 | -0.26598 | 0.032233 | -0.075531 | 0.02684 | -0.14309 | -0.11699 | 121.9598 | 121.7135 | 121.7594 | 62.2893 | -122.0334 | 121.8013 | 121.9242 | 121.9503 | 62.3753 | -122.1696
571.0156 | 122.3373 | -62.2696 | 59.7839 | 1.4211e-13 | -0.029946 | -0.0047286 | 0.065579 | -0.005786 | 0.057522 | -0.0054937 | 0.00078395 | -0.0023288 | -0.0036534 | 0.021201 | -0.010454 | -62.2925 | 0.010564 | -62.2639 | 59.6765 | 59.4211 | 59.4852 | -62.2494 | -62.2557 | 0.087354 | -62.3451 | 59.5225 | 59.6408 | 59.6486 | -62.3903 | 0.020161 | -0.10746 | -0.022906 | 0.005724 | -0.014437 | -0.36287 | -0.2987 | -0.12068 | -0.2614 | 0.013922 | -0.075528 | 0.045154 | -0.14309 | -0.13531 | 121.9461 | 121.6907 | 121.7548 | 62.2802 | -122.0334 | 121.7921 | 121.9104 | 121.9182 | 62.3569 | -122.1742
572.7656 | 122.2137 | -62.2925 | 59.8251 | 1.4211e-13 | -0.029733 | -0.005156 | 0.065579 | -0.0059996 | 0.057095 | 0.0021363 | 0.00078395 | -0.0023288 | -0.0034396 | 0.021414 | -0.01024 | -62.2925 | 0.010564 | -62.2639 | 59.6719 | 59.4348 | 59.4852 | -62.2449 | -62.2557 | 0.091933 | -62.3589 | 59.5225 | 59.6408 | 59.6578 | -62.3903 | 0.047627 | -0.15324 | -1.8e-05 | 0.028612 | -0.019015 | -0.39033 | -0.3399 | -0.097794 | -0.3026 | 0.03681 | -0.066376 | 0.031418 | -0.18429 | -0.16735 | 121.9644 | 121.7273 | 121.7777 | 62.303 | -122.07 | 121.815 | 121.9333 | 121.9503 | 62.3844 | -122.2154
574.5156 | 122.2183 | -62.3062 | 59.7885 | 1.4211e-13 | -0.029733 | -0.0047286 | 0.065793 | -0.005786 | 0.057095 | -0.0054937 | 0.00057035 | -0.0021152 | -0.0034396 | 0.021414 | -0.010454 | -62.2925 | 0.010564 | -62.2547 | 59.6811 | 59.4256 | 59.4807 | -62.254 | -62.2557 | 0.087354 | -62.3543 | 59.5134 | 59.6408 | 59.6578 | -62.3857 | 0.052203 | -0.10746 | 0.013715 | 0.051501 | -0.000702 | -0.36287 | -0.30786 | -0.079483 | -0.27514 | 0.050543 | -0.048064 | 0.031419 | -0.14767 | -0.13073 | 121.9873 | 121.7319 | 121.7869 | 62.3168 | -122.0425 | 121.8196 | 121.9471 | 121.964 | 62.3936 | -122.1742
576.2031 | 122.2412 | -62.2971 | 59.8114 | 1.4211e-13 | -0.03016 | -0.004515 | 0.065793 | -0.0059996 | 0.057522 | -0.0054937 | 0.00035675 | -0.0021152 | -0.0036534 | 0.021414 | -0.010668 | -62.2879 | 0.015142 | -62.2593 | 59.6765 | 59.4302 | 59.4715 | -62.2494 | -62.2557 | 0.087354 | -62.3543 | 59.518 | 59.6363 | 59.6532 | -62.3811 | 0.047627 | -0.13493 | 0.009139 | 0.037768 | -0.009859 | -0.38118 | -0.3399 | -0.084059 | -0.29345 | 0.041388 | -0.057219 | 0.02684 | -0.17513 | -0.15819 | 121.9735 | 121.7273 | 121.7686 | 62.3122 | -122.0608 | 121.815 | 121.9333 | 121.9503 | 62.3844 | -122.1925
577.9688 | 122.2275 | -62.2787 | 59.8251 | 1.4211e-13 | -0.029733 | -0.0047286 | 0.066007 | -0.0055724 | 0.057309 | -0.0054937 | 0.00014315 | -0.0021152 | -0.003226 | 0.021414 | -0.010454 | -62.2879 | 0.015142 | -62.2639 | 59.6765 | 59.4302 | 59.4807 | -62.2494 | -62.2557 | 0.082776 | -62.3589 | 59.5134 | 59.6317 | 59.6578 | -62.3903 | 0.029317 | -0.14866 | -0.009171 | 0.01488 | -0.014437 | -0.39491 | -0.34448 | -0.11153 | -0.31176 | 0.023078 | -0.080108 | 0.031418 | -0.19344 | -0.16735 | 121.9552 | 121.709 | 121.7594 | 62.2939 | -122.0746 | 121.7921 | 121.9104 | 121.9365 | 62.3615 | -122.2154
579.6562 | 122.3694 | -62.2559 | 59.7565 | 1.4211e-13 | -0.029733 | -0.0049424 | 0.065579 | -0.0059996 | 0.057522 | 0.0021363 | 0.00078395 | -0.0021152 | -0.0034396 | 0.021414 | -0.010668 | -62.2925 | 0.015142 | -62.2593 | 59.6811 | 59.4348 | 59.4852 | -62.254 | -62.2557 | 0.091933 | -62.3543 | 59.5134 | 59.6454 | 59.6532 | -62.3903 | 0.001849 | -0.075419 | -0.036639 | -0.003431 | -0.00528 | -0.32167 | -0.27124 | -0.13441 | -0.24309 | 0.000189 | -0.098418 | 0.035997 | -0.11104 | -0.10326 | 121.9369 | 121.6907 | 121.7411 | 62.271 | -122.0105 | 121.7692 | 121.9013 | 121.9091 | 62.3478 | -122.1467
581.3906 | 122.2366 | -62.2879 | 59.8343 | 1.4211e-13 | -0.029946 | -0.0049424 | 0.065579 | -0.005786 | 0.057522 | 0.0021363 | 0.00057035 | -0.0021152 | -0.003226 | 0.021414 | -0.010454 | -62.2833 | 0.015142 | -62.2593 | 59.6811 | 59.4302 | 59.4852 | -62.2449 | -62.2648 | 0.087354 | -62.3543 | 59.518 | 59.6363 | 59.6532 | -62.3903 | 0.04305 | -0.15324 | 0.004562 | 0.028613 | -0.014437 | -0.40407 | -0.34906 | -0.10237 | -0.31634 | 0.023075 | -0.066374 | 0.035997 | -0.19802 | -0.18108 | 121.969 | 121.7181 | 121.7731 | 62.303 | -122.0791 | 121.8059 | 121.9242 | 121.9411 | 62.3753 | -122.2246
583.1406 | 122.2 | -62.3199 | 59.8114 | 1.4211e-13 | -0.030374 | -0.004515 | 0.065579 | -0.005786 | 0.057736 | -0.013124 | 0.00057035 | -0.0019016 | -0.003226 | 0.021628 | -0.01024 | -62.2925 | 0.010564 | -62.2593 | 59.6811 | 59.4302 | 59.4852 | -62.254 | -62.2602 | 0.091933 | -62.3589 | 59.5225 | 59.6363 | 59.6532 | -62.3949 | 0.065936 | -0.13035 | 0.027448 | 0.060656 | -0.00528 | -0.38118 | -0.32617 | -0.074907 | -0.28887 | 0.059697 | -0.03891 | 0.035997 | -0.17513 | -0.15819 | 122.001 | 121.7502 | 121.8052 | 62.3305 | -122.0654 | 121.8425 | 121.9562 | 121.9732 | 62.4119 | -122.2063
584.8281 | 122.2229 | -62.2604 | 59.8526 | 1.4211e-13 | -0.029733 | -0.005156 | 0.065579 | -0.0059996 | 0.057522 | -0.0054937 | 0.00057035 | -0.0019016 | -0.0034396 | 0.021201 | -0.010668 | -62.2879 | 0.010564 | -62.2593 | 59.6811 | 59.4256 | 59.4807 | -62.2494 | -62.2602 | 0.087354 | -62.3589 | 59.518 | 59.6408 | 59.6532 | -62.3949 | 0.011006 | -0.17155 | -0.027482 | 0.001147 | -0.009859 | -0.42696 | -0.37195 | -0.13442 | -0.33465 | 0.000188 | -0.098419 | 0.035997 | -0.21175 | -0.19939 | 121.9415 | 121.6861 | 121.7411 | 62.271 | -122.102 | 121.7784 | 121.9013 | 121.9136 | 62.3478 | -122.2475
586.5625 | 122.2229 | -62.2696 | 59.8343 | 1.4211e-13 | -0.03016 | -0.0049424 | 0.065579 | -0.005786 | 0.057095 | -0.013124 | 0.00035675 | -0.0021152 | -0.003226 | 0.020987 | -0.01024 | -62.2925 | 0.005985 | -62.2547 | 59.6856 | 59.4302 | 59.4807 | -62.2449 | -62.2648 | 0.096512 | -62.3589 | 59.5225 | 59.6408 | 59.6578 | -62.3949 | 0.024739 | -0.14866 | -0.022906 | 0.01488 | -0.009859 | -0.40407 | -0.35364 | -0.12526 | -0.31176 | 0.004764 | -0.089264 | 0.035997 | -0.19344 | -0.17651 | 121.9552 | 121.6998 | 121.7502 | 62.2756 | -122.0791 | 121.7921 | 121.9104 | 121.9274 | 62.3661 | -122.2291
588.25 | 122.2092 | -62.3062 | 59.8022 | 1.4211e-13 | -0.030587 | -0.0047286 | 0.065793 | -0.0059996 | 0.057309 | -0.0054937 | 0.00035675 | -0.0021152 | -0.0034396 | 0.021201 | -0.010454 | -62.2925 | 0.005985 | -62.273 | 59.6811 | 59.4302 | 59.4852 | -62.2494 | -62.2602 | 0.087354 | -62.3589 | 59.5134 | 59.6454 | 59.6532 | -62.3903 | 0.056782 | -0.1212 | 0.013715 | 0.033188 | -0.023594 | -0.37202 | -0.31701 | -0.084061 | -0.28887 | 0.045964 | -0.052643 | 0.031418 | -0.15682 | -0.14904 | 121.9873 | 121.7364 | 121.7914 | 62.3122 | -122.0517 | 121.8196 | 121.9516 | 121.9594 | 62.3936 | -122.1925
590 | 122.1954 | -62.3062 | 59.8068 | 1.4211e-13 | -0.03016 | -0.005156 | 0.065793 | -0.0059996 | 0.057522 | -0.0054937 | 0.00057035 | -0.0021152 | -0.0034396 | 0.021414 | -0.010454 | -62.2833 | 0.005985 | -62.2639 | 59.6811 | 59.4256 | 59.4807 | -62.254 | -62.2648 | 0.091933 | -62.3543 | 59.5225 | 59.6408 | 59.6578 | -62.3857 | 0.052203 | -0.12577 | 0.022872 | 0.042345 | -0.009858 | -0.38118 | -0.32617 | -0.079483 | -0.28429 | 0.041385 | -0.048064 | 0.031419 | -0.16598 | -0.14904 | 121.9873 | 121.7319 | 121.7869 | 62.3122 | -122.0608 | 121.8287 | 121.9471 | 121.964 | 62.3981 | -122.1925
591.7344 | 122.3328 | -62.265 | 59.7382 | 1.4211e-13 | -0.03016 | -0.004515 | 0.065579 | -0.0055724 | 0.057309 | -0.013124 | 0.00035675 | -0.0016878 | -0.0030124 | 0.021414 | -0.010454 | -62.2971 | 0.010564 | -62.2639 | 59.6811 | 59.4394 | 59.4807 | -62.2449 | -62.2602 | 0.091933 | -62.3589 | 59.5225 | 59.6408 | 59.6624 | -62.3949 | 0.020162 | -0.057108 | -0.032061 | 0.001147 | -0.019015 | -0.29878 | -0.2575 | -0.12984 | -0.21563 | 0.004766 | -0.093841 | 0.035997 | -0.097312 | -0.075796 | 121.9461 | 121.7044 | 121.7457 | 62.2756 | -121.983 | 121.7875 | 121.9059 | 121.9274 | 62.3569 | -122.133
593.4844 | 122.3557 | -62.2925 | 59.7382 | 1.4211e-13 | -0.029946 | -0.0047286 | 0.065793 | -0.005786 | 0.057309 | -0.013124 | 0.00035675 | -0.0021152 | -0.003226 | 0.021842 | -0.010454 | -62.2879 | -0.003172 | -62.2639 | 59.6811 | 59.4348 | 59.4761 | -62.2494 | -62.2602 | 0.082776 | -62.3543 | 59.5134 | 59.6408 | 59.6624 | -62.3903 | 0.043049 | -0.057108 | 0.004561 | 0.028612 | -0.014437 | -0.30336 | -0.26208 | -0.097794 | -0.22478 | 0.032231 | -0.061797 | 0.035997 | -0.097312 | -0.075796 | 121.9735 | 121.7273 | 121.7686 | 62.2893 | -121.9876 | 121.8059 | 121.9333 | 121.9548 | 62.3753 | -122.1284
595.1562 | 122.3099 | -62.2833 | 59.7519 | 1.4211e-13 | -0.03016 | -0.004515 | 0.065579 | -0.005786 | 0.056881 | 0.0021363 | 0.00057035 | -0.0019016 | -0.0034396 | 0.021628 | -0.01024 | -62.2925 | 0.005985 | -62.2593 | 59.6811 | 59.4348 | 59.4807 | -62.2494 | -62.2557 | 0.082776 | -62.3497 | 59.5271 | 59.6454 | 59.6578 | -62.3903 | 0.033894 | -0.070841 | -0.009173 | 0.024035 | -0.009859 | -0.31709 | -0.27124 | -0.10695 | -0.22478 | 0.027655 | -0.066374 | 0.040575 | -0.10647 | -0.094108 | 121.9644 | 121.7181 | 121.764 | 62.2893 | -122.0013 | 121.8104 | 121.9288 | 121.9411 | 62.3661 | -122.1422
596.8906 | 122.2961 | -62.2742 | 59.7748 | 1.4211e-13 | -0.029946 | -0.0049424 | 0.065579 | -0.005786 | 0.057309 | -0.013124 | 0.00057035 | -0.0019016 | -0.003226 | 0.021414 | -0.01024 | -62.2925 | 0.005985 | -62.2593 | 59.6765 | 59.4211 | 59.4852 | -62.2494 | -62.2557 | 0.091933 | -62.3589 | 59.5134 | 59.6363 | 59.6578 | -62.3949 | 0.024739 | -0.098307 | -0.018328 | 0.01488 | -0.009859 | -0.35372 | -0.28955 | -0.12068 | -0.2614 | 0.0185 | -0.084686 | 0.035997 | -0.13851 | -0.117 | 121.9506 | 121.6952 | 121.7594 | 62.2802 | -122.0242 | 121.7875 | 121.9104 | 121.932 | 62.3661 | -122.1696
598.6406 | 122.2183 | -62.3016 | 59.8114 | 1.4211e-13 | -0.029946 | -0.005156 | 0.065579 | -0.005786 | 0.057309 | -0.0054937 | 0.00057035 | -0.0016878 | -0.0036534 | 0.021414 | -0.010668 | -62.2879 | 0.001407 | -62.2593 | 59.6811 | 59.4302 | 59.4807 | -62.2449 | -62.2557 | 0.078197 | -62.3589 | 59.518 | 59.6363 | 59.6303 | -62.3903 | 0.056783 | -0.13035 | 0.013717 | 0.042346 | -0.014437 | -0.38118 | -0.33075 | -0.088638 | -0.29345 | 0.045966 | -0.05722 | 0.031418 | -0.17513 | -0.18109 | 121.9827 | 121.7319 | 121.7823 | 62.303 | -122.0563 | 121.8196 | 121.9379 | 121.9319 | 62.3798 | -122.2017
600.3906 | 122.2183 | -62.2833 | 59.8434 | 1.4211e-13 | -0.029519 | -0.0049424 | 0.065793 | -0.0059996 | 0.057095 | -0.013124 | 0.00057035 | -0.0021152 | -0.0034396 | 0.021628 | -0.010881 | -62.2925 | 0.010564 | -62.2639 | 59.6719 | 59.4302 | 59.4807 | -62.254 | -62.2557 | 0.082776 | -62.3589 | 59.5271 | 59.6363 | 59.6486 | -62.3857 | 0.029315 | -0.17155 | -0.009173 | 0.019457 | -0.009858 | -0.41322 | -0.36279 | -0.10237 | -0.31633 | 0.027655 | -0.075531 | 0.02684 | -0.20718 | -0.19482 | 121.9552 | 121.7135 | 121.764 | 62.2939 | -122.0975 | 121.8104 | 121.9196 | 121.932 | 62.3661 | -122.2291
602.1406 | 122.2321 | -62.3108 | 59.7702 | 1.4211e-13 | -0.030374 | -0.0049424 | 0.065579 | -0.0059996 | 0.056881 | 0.0097668 | 0.00035675 | -0.0019016 | -0.0036534 | 0.021628 | -0.010454 | -62.2925 | 0.001407 | -62.2593 | 59.6811 | 59.4302 | 59.4761 | -62.2494 | -62.2557 | 0.087354 | -62.368 | 59.518 | 59.6408 | 59.6395 | -62.3949 | 0.06136 | -0.089152 | 0.018293 | 0.051501 | -0.009859 | -0.33998 | -0.29413 | -0.084062 | -0.25225 | 0.055121 | -0.057222 | 0.02684 | -0.12936 | -0.13073 | 121.9918 | 121.741 | 121.7869 | 62.3122 | -122.0196 | 121.8287 | 121.9516 | 121.9503 | 62.3981 | -122.1651
603.9062 | 122.2275 | -62.3108 | 59.7931 | 1.4211e-13 | -0.03016 | -0.0049424 | 0.065579 | -0.0059996 | 0.057309 | 0.0021363 | 0.00035675 | -0.0021152 | -0.0034396 | 0.021628 | -0.01024 | -62.2925 | 0.010564 | -62.2684 | 59.6765 | 59.4394 | 59.4898 | -62.2449 | -62.2602 | 0.082776 | -62.3543 | 59.5134 | 59.6408 | 59.6532 | -62.3857 | 0.065938 | -0.11662 | 0.018293 | 0.042345 | -0.023593 | -0.35371 | -0.30328 | -0.074905 | -0.27971 | 0.050542 | -0.043486 | 0.031419 | -0.15224 | -0.13988 | 121.9873 | 121.7502 | 121.8006 | 62.3214 | -122.0379 | 121.8242 | 121.9516 | 121.964 | 62.3936 | -122.1788
605.6562 | 122.3145 | -62.2879 | 59.7519 | 1.4211e-13 | -0.029946 | -0.0049424 | 0.065579 | -0.005786 | 0.057522 | 0.0021363 | 0.00035675 | -0.0023288 | -0.003226 | 0.021414 | -0.010454 | -62.2925 | 0.010564 | -62.2593 | 59.6856 | 59.4302 | 59.4852 | -62.2586 | -62.2511 | 0.087354 | -62.3543 | 59.5134 | 59.6408 | 59.6532 | -62.404 | 0.029314 | -0.066262 | -0.004595 | 0.028613 | -0.000701 | -0.32167 | -0.26666 | -0.11611 | -0.23852 | 0.036811 | -0.066374 | 0.049734 | -0.11104 | -0.098686 | 121.9735 | 121.7181 | 121.7731 | 62.2985 | -122.0105 | 121.8013 | 121.9287 | 121.9411 | 62.3753 | -122.1559
607.3281 | 122.2687 | -62.2879 | 59.8618 | 1.4211e-13 | -0.03016 | -0.0047286 | 0.065366 | -0.005786 | 0.057095 | 0.0021363 | 0.00035675 | -0.0019016 | -0.0034396 | 0.021414 | -0.010668 | -62.2971 | 0.010564 | -62.2547 | 59.6765 | 59.4302 | 59.4852 | -62.2494 | -62.2602 | 0.087354 | -62.3543 | 59.518 | 59.6408 | 59.6578 | -62.3994 | 0.038472 | -0.18528 | -0.009173 | 0.033191 | -0.005281 | -0.43153 | -0.37652 | -0.11153 | -0.3438 | 0.027654 | -0.066374 | 0.045155 | -0.22091 | -0.20397 | 121.9644 | 121.7181 | 121.7731 | 62.2985 | -122.1112 | 121.8059 | 121.9287 | 121.9457 | 62.3753 | -122.2612
609.0781 | 122.2733 | -62.2696 | 59.8297 | 1.4211e-13 | -0.030587 | -0.005156 | 0.065579 | -0.0059996 | 0.056881 | -0.0054937 | 0.00057035 | -0.0021152 | -0.003226 | 0.021628 | -0.010027 | -62.2833 | 0.010564 | -62.2639 | 59.6765 | 59.4256 | 59.4852 | -62.254 | -62.2648 | 0.087354 | -62.3543 | 59.5225 | 59.6454 | 59.6532 | -62.3857 | 0.015582 | -0.15324 | -0.013749 | 0.005724 | -0.009858 | -0.40407 | -0.34448 | -0.1161 | -0.30718 | 0.004764 | -0.084685 | 0.031419 | -0.18429 | -0.17651 | 121.9461 | 121.6952 | 121.7548 | 62.2802 | -122.0837 | 121.7921 | 121.915 | 121.9228 | 62.3569 | -122.2154
610.75 | 122.2137 | -62.3016 | 59.8206 | 1.4211e-13 | -0.030587 | -0.0049424 | 0.065579 | -0.005786 | 0.057095 | 0.0021363 | 0.00057035 | -0.0016878 | -0.0030124 | 0.021628 | -0.01024 | -62.2879 | 0.010564 | -62.2593 | 59.6811 | 59.4348 | 59.4807 | -62.254 | -62.2557 | 0.087354 | -62.3634 | 59.518 | 59.6363 | 59.6624 | -62.3857 | 0.047626 | -0.13951 | 0.013717 | 0.042346 | -0.00528 | -0.38576 | -0.3399 | -0.08406 | -0.3026 | 0.045966 | -0.061799 | 0.022261 | -0.18429 | -0.15819 | 121.9827 | 121.7364 | 121.7823 | 62.3122 | -122.0746 | 121.8196 | 121.9379 | 121.964 | 62.389 | -122.2063
612.5 | 122.3602 | -62.2742 | 59.7748 | 1.4211e-13 | -0.030374 | -0.005156 | 0.065366 | -0.0055724 | 0.056668 | 0.0097668 | 0.00035675 | -0.0019016 | -0.0034396 | 0.021842 | -0.01024 | -62.2879 | 0.010564 | -62.2593 | 59.6811 | 59.4302 | 59.4852 | -62.2586 | -62.2511 | 0.082776 | -62.3589 | 59.5134 | 59.6408 | 59.6578 | -62.3949 | 0.015581 | -0.093729 | -0.013749 | 0.01488 | -0.000701 | -0.34456 | -0.28955 | -0.12068 | -0.2614 | 0.023078 | -0.084686 | 0.035997 | -0.13393 | -0.117 | 121.9552 | 121.7044 | 121.7594 | 62.2847 | -122.0334 | 121.7875 | 121.915 | 121.932 | 62.3569 | -122.1696
614.25 | 122.2366 | -62.3108 | 59.7885 | 1.4211e-13 | -0.03016 | -0.005156 | 0.065366 | -0.005786 | 0.057095 | -0.013124 | 0.00078395 | -0.0021152 | -0.0036534 | 0.021842 | -0.010668 | -62.2879 | 0.010564 | -62.2593 | 59.6856 | 59.444 | 59.4852 | -62.2494 | -62.2511 | 0.087354 | -62.3543 | 59.518 | 59.6408 | 59.6624 | -62.3903 | 0.06136 | -0.10288 | 0.022872 | 0.051501 | -0.009859 | -0.34456 | -0.30328 | -0.079483 | -0.27056 | 0.059699 | -0.043486 | 0.035997 | -0.14767 | -0.12615 | 121.9964 | 121.7547 | 121.796 | 62.3214 | -122.0379 | 121.8287 | 121.9516 | 121.9732 | 62.3981 | -122.1788
616 | 122.3511 | -62.2696 | 59.7702 | 1.4211e-13 | -0.03016 | -0.0049424 | 0.065579 | -0.0055724 | 0.057095 | -0.013124 | 0.00099775 | -0.0019016 | -0.003867 | 0.021842 | -0.010668 | -62.2833 | 0.005985 | -62.2639 | 59.6811 | 59.4348 | 59.4852 | -62.254 | -62.2557 | 0.087354 | -62.3634 | 59.518 | 59.65 | 59.6578 | -62.3949 | 0.015582 | -0.089152 | -0.013749 | 0.005724 | -0.009858 | -0.3354 | -0.28497 | -0.12526 | -0.25225 | 0.013922 | -0.093843 | 0.031418 | -0.1202 | -0.11242 | 121.9506 | 121.7044 | 121.7548 | 62.2756 | -122.0242 | 121.7875 | 121.9196 | 121.9274 | 62.3569 | -122.1651
617.6875 | 122.2733 | -62.2925 | 59.8526 | 1.4211e-13 | -0.029733 | -0.0047286 | 0.065579 | -0.005786 | 0.057095 | -0.0054937 | 0.00035675 | -0.0016878 | -0.0036534 | 0.021842 | -0.010454 | -62.2788 | 0.001407 | -62.2639 | 59.6765 | 59.4302 | 59.4852 | -62.254 | -62.2557 | 0.091933 | -62.3543 | 59.518 | 59.6363 | 59.6532 | -62.3903 | 0.03847 | -0.17613 | 0.013717 | 0.028612 | -0.009858 | -0.42238 | -0.36737 | -0.097794 | -0.33465 | 0.03681 | -0.061797 | 0.035997 | -0.21633 | -0.19939 | 121.969 | 121.7227 | 121.7777 | 62.2939 | -122.1066 | 121.8104 | 121.9287 | 121.9457 | 62.3844 | -122.2429
619.4531 | 122.3511 | -62.2467 | 59.761 | 1.4211e-13 | -0.03016 | -0.005156 | 0.065366 | -0.0059996 | 0.057095 | -0.0054937 | 0.00035675 | -0.0021152 | -0.0036534 | 0.021628 | -0.010668 | -62.2833 | 0.010564 | -62.2593 | 59.6811 | 59.4302 | 59.4852 | -62.254 | -62.2648 | 0.091933 | -62.3543 | 59.518 | 59.6317 | 59.6624 | -62.3949 | -0.007306 | -0.079996 | -0.036637 | -0.012586 | -0.00528 | -0.33083 | -0.27581 | -0.14815 | -0.24309 | -0.018124 | -0.10757 | 0.040576 | -0.12936 | -0.098684 | 121.9278 | 121.6769 | 121.7319 | 62.2573 | -122.0151 | 121.7647 | 121.8784 | 121.9091 | 62.3386 | -122.1559
621.1406 | 122.2824 | -62.2604 | 59.8114 | 1.4211e-13 | -0.030587 | -0.005156 | 0.065579 | -0.005786 | 0.057095 | -0.0054937 | 0.00078395 | -0.0021152 | -0.0034396 | 0.021414 | -0.01024 | -62.2833 | 0.005985 | -62.2684 | 59.6719 | 59.4394 | 59.4807 | -62.2494 | -62.2557 | 0.091933 | -62.3497 | 59.5225 | 59.6454 | 59.6486 | -62.3949 | 0.011006 | -0.13951 | -0.022904 | -0.008009 | -0.019015 | -0.37202 | -0.33075 | -0.13442 | -0.28887 | 0.004767 | -0.089262 | 0.045154 | -0.16597 | -0.16277 | 121.9323 | 121.6998 | 121.7411 | 62.2664 | -122.0608 | 121.783 | 121.9059 | 121.9091 | 62.3524 | -122.2063
622.8906 | 122.2229 | -62.2925 | 59.7977 | 1.4211e-13 | -0.030374 | -0.0047286 | 0.065579 | -0.0053586 | 0.056881 | -0.0054937 | 0.00057035 | -0.0021152 | -0.0036534 | 0.021842 | -0.010454 | -62.2879 | 0.010564 | -62.2639 | 59.6765 | 59.4302 | 59.4761 | -62.2494 | -62.2602 | 0.078197 | -62.3589 | 59.518 | 59.6454 | 59.6578 | -62.3994 | 0.043049 | -0.1212 | 0.004561 | 0.028612 | -0.014437 | -0.36745 | -0.32159 | -0.10695 | -0.27971 | 0.032231 | -0.066376 | 0.040576 | -0.15224 | -0.13988 | 121.969 | 121.7227 | 121.7686 | 62.303 | -122.0471 | 121.8104 | 121.9379 | 121.9503 | 62.3707 | -122.1971
624.6406 | 122.3511 | -62.265 | 59.7839 | 1.4211e-13 | -0.030374 | -0.0049424 | 0.066007 | -0.0055724 | 0.057095 | -0.0054937 | 0.00035675 | -0.0016878 | -0.0034396 | 0.021414 | -0.01024 | -62.2925 | 0.019721 | -62.2593 | 59.6811 | 59.4302 | 59.4898 | -62.254 | -62.2602 | 0.087354 | -62.3497 | 59.5225 | 59.6454 | 59.6532 | -62.3903 | 0.011005 | -0.10289 | -0.027483 | 0.005725 | -0.00528 | -0.35371 | -0.29412 | -0.12526 | -0.2614 | 0.004766 | -0.084684 | 0.040575 | -0.13851 | -0.13073 | 121.9461 | 121.6952 | 121.7548 | 62.2847 | -122.0379 | 121.7875 | 121.9104 | 121.9182 | 62.3524 | -122.1742
626.3594 | 122.2137 | -62.2879 | 59.8297 | 1.4211e-13 | -0.030374 | -0.0047286 | 0.065366 | -0.005786 | 0.056881 | 0.0021363 | 0.00078395 | -0.0021152 | -0.0034396 | 0.021842 | -0.010881 | -62.2833 | 0.001407 | -62.2639 | 59.6811 | 59.4302 | 59.4852 | -62.2586 | -62.2511 | 0.087354 | -62.3543 | 59.518 | 59.6454 | 59.6578 | -62.3903 | 0.029314 | -0.14866 | 0.004562 | 0.024035 | -0.005279 | -0.39949 | -0.34448 | -0.10237 | -0.31176 | 0.036811 | -0.066374 | 0.035997 | -0.18429 | -0.17193 | 121.969 | 121.7181 | 121.7731 | 62.2893 | -122.0883 | 121.8059 | 121.9333 | 121.9457 | 62.3753 | -122.22
628.0625 | 122.3648 | -62.2559 | 59.761 | 1.4211e-13 | -0.030587 | -0.0049424 | 0.065793 | -0.0059996 | 0.057095 | 0.0021363 | 0.00057035 | -0.0019016 | -0.0036534 | 0.021628 | -0.010454 | -62.2879 | 0.010564 | -62.2593 | 59.6811 | 59.4256 | 59.4852 | -62.2494 | -62.2511 | 0.082776 | -62.3589 | 59.5225 | 59.6454 | 59.6532 | -62.3903 | 0.006428 | -0.079996 | -0.03206 | -0.003431 | -0.009859 | -0.3354 | -0.27581 | -0.13441 | -0.23851 | 0.004767 | -0.103 | 0.031418 | -0.11562 | -0.10784 | 121.9369 | 121.6815 | 121.7411 | 62.2664 | -122.0105 | 121.7784 | 121.9013 | 121.9091 | 62.3386 | -122.1513
629.7969 | 122.2733 | -62.2787 | 59.816 | 1.4211e-13 | -0.030374 | -0.005156 | 0.065366 | -0.0055724 | 0.056881 | -0.0054937 | 0.00078395 | -0.0019016 | -0.0036534 | 0.021842 | -0.010668 | -62.2925 | 0.001407 | -62.2639 | 59.6811 | 59.4256 | 59.4852 | -62.2586 | -62.2602 | 0.087354 | -62.3543 | 59.5225 | 59.6454 | 59.6624 | -62.404 | 0.020159 | -0.13493 | -0.01375 | 0.01488 | -0.005279 | -0.39034 | -0.33075 | -0.12526 | -0.29345 | 0.018499 | -0.075529 | 0.049734 | -0.17055 | -0.15362 | 121.9598 | 121.7044 | 121.764 | 62.2802 | -122.0746 | 121.8013 | 121.9242 | 121.9411 | 62.3661 | -122.22
631.5312 | 122.3328 | -62.265 | 59.7702 | 1.4211e-13 | -0.030374 | -0.0043014 | 0.065366 | -0.0062134 | 0.056881 | -0.013124 | 0.00035675 | -0.0019016 | -0.003226 | 0.021842 | -0.010454 | -62.2879 | 0.001407 | -62.2639 | 59.6811 | 59.4302 | 59.4852 | -62.254 | -62.2602 | 0.073618 | -62.3543 | 59.5225 | 59.65 | 59.6624 | -62.3994 | 0.011005 | -0.089152 | -0.022904 | 0.001147 | -0.009858 | -0.33998 | -0.28497 | -0.13442 | -0.24767 | 0.004766 | -0.089262 | 0.045155 | -0.1202 | -0.10784 | 121.9461 | 121.6952 | 121.7502 | 62.2664 | -122.0242 | 121.7875 | 121.915 | 121.9274 | 62.3386 | -122.1696
633.2812 | 122.2275 | -62.2925 | 59.8022 | 1.4211e-13 | -0.030587 | -0.0049424 | 0.065366 | -0.005786 | 0.056881 | 0.0021363 | 0.00035675 | -0.0019016 | -0.0034396 | 0.022055 | -0.010454 | -62.2879 | 0.010564 | -62.2639 | 59.6811 | 59.4348 | 59.4898 | -62.254 | -62.2602 | 0.06904 | -62.3634 | 59.5271 | 59.6408 | 59.6578 | -62.3994 | 0.03847 | -0.1212 | 0.004561 | 0.028612 | -0.009858 | -0.36745 | -0.31243 | -0.10695 | -0.27513 | 0.032231 | -0.070955 | 0.035997 | -0.1614 | -0.14446 | 121.9735 | 121.7273 | 121.7823 | 62.303 | -122.0563 | 121.8196 | 121.9333 | 121.9503 | 62.3615 | -122.2017
635.0469 | 122.2366 | -62.3108 | 59.816 | 1.4211e-13 | -0.030587 | -0.0047286 | 0.065579 | -0.005786 | 0.056454 | -0.0054937 | 0.00057035 | -0.0021152 | -0.0034396 | 0.022055 | -0.010454 | -62.2879 | 0.001407 | -62.2639 | 59.6765 | 59.4394 | 59.4852 | -62.254 | -62.2557 | 0.082776 | -62.3543 | 59.5225 | 59.65 | 59.6669 | -62.3903 | 0.056781 | -0.13951 | 0.022872 | 0.046923 | -0.009858 | -0.3766 | -0.33075 | -0.079483 | -0.29345 | 0.055121 | -0.043486 | 0.035997 | -0.16597 | -0.14904 | 121.9873 | 121.7502 | 121.796 | 62.3122 | -122.07 | 121.8333 | 121.9608 | 121.9777 | 62.3936 | -122.2063
636.7969 | 122.3465 | -62.2604 | 59.7336 | 1.4211e-13 | -0.030587 | -0.0047286 | 0.065579 | -0.0059996 | 0.056881 | -0.0054937 | 0.00014315 | -0.0016878 | -0.0036534 | 0.022055 | -0.010454 | -62.2879 | 0.005985 | -62.2547 | 59.6811 | 59.4348 | 59.4852 | -62.254 | -62.2557 | 0.073618 | -62.3589 | 59.518 | 59.65 | 59.6578 | -62.3994 | 0.006427 | -0.052531 | -0.027482 | 0.005725 | -0.000702 | -0.29878 | -0.24835 | -0.13899 | -0.21563 | 0.004767 | -0.098419 | 0.040576 | -0.083578 | -0.075798 | 121.9415 | 121.6952 | 121.7457 | 62.2664 | -121.9876 | 121.7784 | 121.9104 | 121.9182 | 62.3341 | -122.133
638.4844 | 122.2229 | -62.2879 | 59.8022 | 1.4211e-13 | -0.031015 | -0.0047286 | 0.065579 | -0.005786 | 0.056881 | -0.013124 | 0.00014315 | -0.0019016 | -0.0034396 | 0.021842 | -0.010454 | -62.2925 | 0.005985 | -62.2547 | 59.6811 | 59.4394 | 59.4852 | -62.2586 | -62.2602 | 0.082776 | -62.3589 | 59.518 | 59.65 | 59.6669 | -62.3994 | 0.029314 | -0.1212 | -0.004595 | 0.033191 | 0.003877 | -0.36287 | -0.31701 | -0.11153 | -0.28429 | 0.027654 | -0.070953 | 0.040576 | -0.15224 | -0.1353 | 121.969 | 121.7273 | 121.7731 | 62.2939 | -122.0608 | 121.8059 | 121.9379 | 121.9548 | 62.3707 | -122.2017
640.2188 | 122.2778 | -62.2787 | 59.8343 | 1.4211e-13 | -0.030587 | -0.005156 | 0.065366 | -0.0059996 | 0.056668 | -0.0054937 | 0.00057035 | -0.0019016 | -0.0036534 | 0.021842 | -0.010668 | -62.2833 | 0.005985 | -62.2547 | 59.6811 | 59.4302 | 59.4852 | -62.2632 | -62.2557 | 0.082776 | -62.3589 | 59.5134 | 59.6317 | 59.6715 | -62.3949 | 0.01558 | -0.15324 | -0.004593 | 0.024036 | 0.008456 | -0.40407 | -0.34906 | -0.1161 | -0.32091 | 0.023078 | -0.080108 | 0.035997 | -0.2026 | -0.16277 | 121.9598 | 121.709 | 121.764 | 62.2847 | -122.0975 | 121.7921 | 121.9104 | 121.9503 | 62.3615 | -122.2291
641.9531 | 122.2046 | -62.3108 | 59.8068 | 1.4211e-13 | -0.031015 | -0.0049424 | 0.065793 | -0.005786 | 0.057095 | -0.020755 | 0.00014315 | -0.0019016 | -0.0034396 | 0.022269 | -0.010027 | -62.2833 | 0.001407 | -62.2593 | 59.6811 | 59.4348 | 59.4898 | -62.254 | -62.2602 | 0.073618 | -62.3543 | 59.5271 | 59.6454 | 59.6624 | -62.3949 | 0.056781 | -0.12577 | 0.02745 | 0.051501 | -0.00528 | -0.37202 | -0.31701 | -0.084062 | -0.27971 | 0.050542 | -0.043486 | 0.040576 | -0.1614 | -0.14446 | 121.9918 | 121.7456 | 121.8006 | 62.3122 | -122.0608 | 121.8379 | 121.9562 | 121.9732 | 62.3844 | -122.2017
643.7031 | 122.3648 | -62.2604 | 59.7519 | 1.4211e-13 | -0.030801 | -0.0047286 | 0.065793 | -0.0062134 | 0.057095 | -0.0054937 | 0.00035675 | -0.0019016 | -0.0034396 | 0.021842 | -0.010668 | -62.2925 | 0.010564 | -62.2593 | 59.6811 | 59.4348 | 59.4898 | -62.2494 | -62.2557 | 0.073618 | -62.3589 | 59.5225 | 59.6408 | 59.6578 | -62.3903 | 0.011006 | -0.070841 | -0.032061 | 0.001147 | -0.009859 | -0.31709 | -0.26208 | -0.12984 | -0.22936 | 0.004767 | -0.098419 | 0.031418 | -0.11104 | -0.094108 | 121.9415 | 121.6952 | 121.7502 | 62.271 | -122.0013 | 121.783 | 121.9013 | 121.9182 | 62.3341 | -122.1422
645.3906 | 122.2275 | -62.3016 | 59.8251 | 1.4211e-13 | -0.031015 | -0.005156 | 0.065366 | -0.005786 | 0.056668 | -0.0054937 | 0.00057035 | -0.0021152 | -0.0034396 | 0.022269 | -0.010454 | -62.2879 | 0.005985 | -62.2639 | 59.6811 | 59.4348 | 59.4807 | -62.254 | -62.2602 | 0.078197 | -62.3589 | 59.5271 | 59.6408 | 59.6578 | -62.3949 | 0.047626 | -0.14408 | 0.013717 | 0.037768 | -0.009858 | -0.39033 | -0.34448 | -0.093217 | -0.29802 | 0.041387 | -0.05722 | 0.035997 | -0.18429 | -0.16735 | 121.9827 | 121.7364 | 121.7823 | 62.3076 | -122.0791 | 121.8287 | 121.9425 | 121.9594 | 62.3798 | -122.22
647.1406 | 122.1909 | -62.3154 | 59.816 | 1.4211e-13 | -0.030801 | -0.0049424 | 0.065366 | -0.0059996 | 0.056881 | -0.0054937 | 0.00035675 | -0.0023288 | -0.0034396 | 0.021842 | -0.010454 | -62.2925 | 0.005985 | -62.2684 | 59.6902 | 59.4348 | 59.4944 | -62.254 | -62.2648 | 0.078197 | -62.3634 | 59.518 | 59.6408 | 59.644 | -62.3811 | 0.061359 | -0.12577 | 0.022871 | 0.046923 | -0.014436 | -0.38118 | -0.32159 | -0.065748 | -0.29802 | 0.050541 | -0.048066 | 0.017682 | -0.17513 | -0.17193 | 122.0056 | 121.7502 | 121.8098 | 62.3214 | -122.07 | 121.8333 | 121.9562 | 121.9594 | 62.3936 | -122.1971
648.8438 | 122.2183 | -62.2879 | 59.8389 | 1.4211e-13 | -0.030587 | -0.0049424 | 0.065152 | -0.0055724 | 0.056881 | -0.013124 | 0.00057035 | -0.0021152 | -0.0034396 | 0.021842 | -0.010454 | -62.2971 | 0.010564 | -62.2639 | 59.6811 | 59.4302 | 59.4944 | -62.2586 | -62.2602 | 0.082776 | -62.3589 | 59.5225 | 59.6408 | 59.6532 | -62.3949 | 0.029314 | -0.15782 | -0.009173 | 0.024035 | -0.005279 | -0.40865 | -0.34448 | -0.10695 | -0.31633 | 0.027654 | -0.070953 | 0.035997 | -0.19802 | -0.18566 | 121.969 | 121.7181 | 121.7823 | 62.2985 | -122.0975 | 121.8104 | 121.9287 | 121.9411 | 62.3707 | -122.2337
650.5781 | 122.2595 | -62.2833 | 59.8572 | 1.4211e-13 | -0.030587 | -0.005156 | 0.066007 | -0.005786 | 0.057095 | -0.020755 | 0.00035675 | -0.0019016 | -0.0034396 | 0.022269 | -0.010668 | -62.2879 | 0.001407 | -62.2593 | 59.6856 | 59.4302 | 59.4898 | -62.254 | -62.2557 | 0.073618 | -62.3543 | 59.518 | 59.6454 | 59.6578 | -62.3994 | 0.029315 | -0.17155 | -0.004594 | 0.024035 | -0.00528 | -0.42696 | -0.36737 | -0.11611 | -0.33922 | 0.027655 | -0.070952 | 0.045155 | -0.21175 | -0.19939 | 121.969 | 121.7135 | 121.7731 | 62.2847 | -122.1112 | 121.8013 | 121.9288 | 121.9411 | 62.3569 | -122.2566
652.25 | 122.3602 | -62.2696 | 59.7427 | 1.4211e-13 | -0.030801 | -0.0049424 | 0.065366 | -0.0059996 | 0.056668 | -0.0054937 | 0.00014315 | -0.0019016 | -0.0034396 | 0.022055 | -0.010454 | -62.2879 | 0.010564 | -62.2593 | 59.6811 | 59.4623 | 59.4898 | -62.254 | -62.2602 | 0.073618 | -62.3589 | 59.5134 | 59.6454 | 59.6578 | -62.404 | 0.015582 | -0.061686 | -0.018327 | 0.010302 | -0.00528 | -0.28046 | -0.25292 | -0.13442 | -0.22936 | 0.009343 | -0.089264 | 0.045155 | -0.097311 | -0.084953 | 121.9506 | 121.7319 | 121.7594 | 62.2802 | -121.9967 | 121.783 | 121.915 | 121.9274 | 62.3432 | -122.1467
654 | 122.2275 | -62.3016 | 59.7977 | 1.4211e-13 | -0.031015 | -0.005156 | 0.065579 | -0.0055724 | 0.056668 | -0.013124 | 0.00035675 | -0.0016878 | -0.0034396 | 0.022055 | -0.01024 | -62.2879 | 0.010564 | -62.2684 | 59.6856 | 59.4348 | 59.4852 | -62.2586 | -62.2557 | 0.078197 | -62.3634 | 59.5225 | 59.6454 | 59.6578 | -62.3949 | 0.043047 | -0.11204 | 0.013717 | 0.03319 | -0.009857 | -0.36287 | -0.31244 | -0.093217 | -0.27513 | 0.045966 | -0.061799 | 0.031418 | -0.15224 | -0.13988 | 121.9873 | 121.7364 | 121.7869 | 62.3122 | -122.0563 | 121.8242 | 121.9471 | 121.9594 | 62.3798 | -122.1925
655.7344 | 122.2 | -62.3154 | 59.7931 | 1.4211e-13 | -0.030801 | -0.0049424 | 0.065579 | -0.005786 | 0.056668 | -0.0054937 | 0.00057035 | -0.0019016 | -0.0034396 | 0.021628 | -0.010454 | -62.2879 | 0.015142 | -62.2593 | 59.6856 | 59.4394 | 59.4898 | -62.2586 | -62.2602 | 0.087354 | -62.3589 | 59.518 | 59.6454 | 59.6578 | -62.3949 | 0.05678 | -0.10746 | 0.02745 | 0.056079 | -0.000701 | -0.35371 | -0.30328 | -0.079484 | -0.27514 | 0.05512 | -0.043487 | 0.035997 | -0.14766 | -0.13531 | 122.001 | 121.7547 | 121.8052 | 62.3305 | -122.0517 | 121.8333 | 121.9608 | 121.9732 | 62.4027 | -122.1879
657.4375 | 122.3328 | -62.2833 | 59.7565 | 1.4211e-13 | -0.030801 | -0.0049424 | 0.065579 | -0.0059996 | 0.057095 | -0.013124 | 0.00035675 | -0.0021152 | -0.0036534 | 0.021842 | -0.010454 | -62.2833 | 0.010564 | -62.2639 | 59.6856 | 59.4348 | 59.4898 | -62.254 | -62.2602 | 0.082776 | -62.3589 | 59.518 | 59.6408 | 59.6486 | -62.404 | 0.029315 | -0.07084 | -1.6e-05 | 0.019457 | -0.009858 | -0.32167 | -0.26666 | -0.12069 | -0.23852 | 0.023076 | -0.075531 | 0.045155 | -0.11562 | -0.10784 | 121.969 | 121.7181 | 121.7731 | 62.2939 | -122.0105 | 121.8013 | 121.9242 | 121.932 | 62.3661 | -122.1605
659.1875 | 122.3236 | -62.2559 | 59.7931 | 1.4211e-13 | -0.030801 | -0.0049424 | 0.065366 | -0.0055724 | 0.056668 | -0.028385 | 0.00035675 | -0.0023288 | -0.0036534 | 0.022055 | -0.010881 | -62.2925 | 0.010564 | -62.2684 | 59.6811 | 59.4394 | 59.4898 | -62.2494 | -62.2557 | 0.073618 | -62.3589 | 59.518 | 59.6454 | 59.6486 | -62.3994 | 0.006428 | -0.11204 | -0.036639 | -0.012587 | -0.019015 | -0.35371 | -0.30328 | -0.14357 | -0.27514 | 0.000189 | -0.103 | 0.040576 | -0.14766 | -0.14446 | 121.9369 | 121.6952 | 121.7457 | 62.2664 | -122.0425 | 121.7738 | 121.9013 | 121.9045 | 62.3295 | -122.1925
660.875 | 122.3145 | -62.2971 | 59.729 | 1.4211e-13 | -0.030587 | -0.005156 | 0.065579 | -0.0062134 | 0.057309 | -0.0054937 | 0.00057035 | -0.0023288 | -0.0036534 | 0.022055 | -0.010454 | -62.2833 | 0.010564 | -62.2639 | 59.6811 | 59.4531 | 59.4944 | -62.254 | -62.2557 | 0.078197 | -62.3589 | 59.518 | 59.6454 | 59.6624 | -62.3949 | 0.043048 | -0.047953 | 0.013717 | 0.03319 | -0.009858 | -0.27589 | -0.23461 | -0.097795 | -0.21105 | 0.041388 | -0.061798 | 0.035997 | -0.083578 | -0.066641 | 121.9781 | 121.7502 | 121.7914 | 62.3076 | -121.983 | 121.815 | 121.9425 | 121.9594 | 62.3753 | -122.1239
662.625 | 122.3282 | -62.2925 | 59.761 | 1.4211e-13 | -0.030801 | -0.0049424 | 0.065152 | -0.0059996 | 0.056454 | -0.0054937 | 0.00057035 | -0.0021152 | -0.003226 | 0.022055 | -0.010668 | -62.2971 | 0.015142 | -62.2684 | 59.6856 | 59.4348 | 59.4944 | -62.2632 | -62.2557 | 0.078197 | -62.3589 | 59.5225 | 59.6408 | 59.6624 | -62.3994 | 0.029312 | -0.075417 | -0.004596 | 0.024034 | -0.005278 | -0.32625 | -0.26666 | -0.10695 | -0.23851 | 0.03681 | -0.066376 | 0.040576 | -0.1202 | -0.098684 | 121.9781 | 121.7273 | 121.7869 | 62.3076 | -122.0242 | 121.815 | 121.9333 | 121.9548 | 62.3707 | -122.1605
664.3281 | 122.3648 | -62.2879 | 59.7382 | 1.4211e-13 | -0.031442 | -0.005156 | 0.065366 | -0.005786 | 0.057095 | -0.013124 | 0.00057035 | -0.0023288 | -0.003226 | 0.022055 | -0.010881 | -62.2879 | 0.005985 | -62.2593 | 59.6856 | 59.444 | 59.4898 | -62.254 | -62.2648 | 0.078197 | -62.3497 | 59.5134 | 59.6408 | 59.6578 | -62.3949 | 0.033893 | -0.052529 | -1.6e-05 | 0.028613 | -0.00528 | -0.2942 | -0.24835 | -0.10695 | -0.22478 | 0.023075 | -0.061796 | 0.045154 | -0.097312 | -0.080375 | 121.9735 | 121.7319 | 121.7777 | 62.2939 | -121.9922 | 121.8013 | 121.9287 | 121.9457 | 62.3661 | -122.133
666.0625 | 122.2229 | -62.2879 | 59.8114 | 1.4211e-13 | -0.030801 | -0.0047286 | 0.065579 | -0.0059996 | 0.056881 | 0.0021363 | 0.00014315 | -0.0021152 | -0.0036534 | 0.022483 | -0.010668 | -62.2879 | 0.010564 | -62.2684 | 59.6811 | 59.4394 | 59.4944 | -62.2586 | -62.2602 | 0.078197 | -62.3589 | 59.5271 | 59.6454 | 59.6624 | -62.404 | 0.029314 | -0.13035 | -1.6e-05 | 0.019457 | -0.009857 | -0.37202 | -0.31701 | -0.11611 | -0.28429 | 0.027654 | -0.070953 | 0.045155 | -0.16597 | -0.14904 | 121.969 | 121.7273 | 121.7823 | 62.2985 | -122.07 | 121.815 | 121.9333 | 121.9503 | 62.3661 | -122.2154
667.8125 | 122.2046 | -62.3062 | 59.8068 | 1.4211e-13 | -0.031015 | -0.0049424 | 0.065579 | -0.0059996 | 0.057095 | 0.0021363 | 0.00035675 | -0.0021152 | -0.0036534 | 0.022269 | -0.010668 | -62.2879 | 0.005985 | -62.2639 | 59.6765 | 59.444 | 59.4898 | -62.2586 | -62.2648 | 0.078197 | -62.3497 | 59.518 | 59.6454 | 59.6578 | -62.404 | 0.047624 | -0.13035 | 0.018294 | 0.042345 | -0.005279 | -0.36287 | -0.31701 | -0.097798 | -0.28887 | 0.041385 | -0.043486 | 0.054312 | -0.1614 | -0.14904 | 121.9827 | 121.7502 | 121.796 | 62.3122 | -122.0654 | 121.8242 | 121.9516 | 121.964 | 62.3844 | -122.2108
669.5 | 122.2412 | -62.2742 | 59.7931 | 1.4211e-13 | -0.031442 | -0.0049424 | 0.065366 | -0.0059996 | 0.057095 | -0.0054937 | 0.00057035 | -0.0019016 | -0.003226 | 0.022483 | -0.010668 | -62.2879 | 0.010564 | -62.2593 | 59.6902 | 59.4394 | 59.4898 | -62.2586 | -62.2557 | 0.078197 | -62.3589 | 59.518 | 59.6408 | 59.6532 | -62.3949 | 0.015581 | -0.10288 | -0.013749 | 0.01488 | -0.000701 | -0.35371 | -0.30328 | -0.12068 | -0.27514 | 0.0185 | -0.084686 | 0.035997 | -0.15224 | -0.13988 | 121.9644 | 121.7135 | 121.764 | 62.2847 | -122.0517 | 121.7921 | 121.915 | 121.9274 | 62.3524 | -122.1879
671.1719 | 122.3328 | -62.3062 | 59.7336 | 1.4211e-13 | -0.031442 | -0.005156 | 0.065152 | -0.005786 | 0.056881 | 0.0021363 | 0.00035675 | -0.0023288 | -0.003226 | 0.022055 | -0.010881 | -62.2833 | 0.005985 | -62.2593 | 59.6902 | 59.4394 | 59.4898 | -62.2449 | -62.2602 | 0.082776 | -62.3543 | 59.5225 | 59.6408 | 59.6624 | -62.404 | 0.06136 | -0.043374 | 0.022872 | 0.046923 | -0.014437 | -0.2942 | -0.24377 | -0.097798 | -0.21105 | 0.045964 | -0.048064 | 0.049734 | -0.092735 | -0.071219 | 121.9964 | 121.7456 | 121.796 | 62.3122 | -121.9784 | 121.8287 | 121.9471 | 121.9686 | 62.389 | -122.1376
672.9219 | 122.3511 | -62.2421 | 59.7748 | 1.4211e-13 | -0.031442 | -0.004515 | 0.065152 | -0.0062134 | 0.056668 | -0.0054937 | 0.00035675 | -0.0021152 | -0.0034396 | 0.022055 | -0.010668 | -62.2879 | 0.010564 | -62.2639 | 59.6902 | 59.4394 | 59.4944 | -62.254 | -62.2511 | 0.082776 | -62.3589 | 59.5271 | 59.6454 | 59.6578 | -62.3994 | -0.011884 | -0.084572 | -0.045793 | -0.021742 | -0.009858 | -0.3354 | -0.28039 | -0.15731 | -0.24767 | -0.008966 | -0.11673 | 0.040576 | -0.12935 | -0.117 | 121.9323 | 121.6815 | 121.7365 | 62.2527 | -122.0288 | 121.7692 | 121.8876 | 121.8999 | 62.3249 | -122.1742
674.6094 | 122.2824 | -62.2787 | 59.8251 | 1.4211e-13 | -0.031228 | -0.0049424 | 0.065579 | -0.0059996 | 0.056668 | -0.0054937 | 0.00057035 | -0.0021152 | -0.0034396 | 0.022696 | -0.010668 | -62.2971 | 0.010564 | -62.2593 | 59.6948 | 59.4394 | 59.4944 | -62.2586 | -62.2557 | 0.087354 | -62.3543 | 59.518 | 59.6454 | 59.6624 | -62.3994 | 0.020159 | -0.13035 | -0.018328 | 0.019458 | -0.000701 | -0.38576 | -0.33074 | -0.12068 | -0.30718 | 0.023078 | -0.075529 | 0.045155 | -0.17971 | -0.16277 | 121.9735 | 121.7181 | 121.7731 | 62.2893 | -122.0837 | 121.7967 | 121.9242 | 121.9411 | 62.3661 | -122.2246
676.3438 | 122.319 | -62.2787 | 59.761 | 1.4211e-13 | -0.031656 | -0.005156 | 0.065793 | -0.005786 | 0.056668 | -0.013124 | 0.00078395 | -0.0023288 | -0.0036534 | 0.022269 | -0.011095 | -62.2925 | 0.010564 | -62.2639 | 59.6811 | 59.4348 | 59.4898 | -62.254 | -62.2511 | 0.078197 | -62.3497 | 59.518 | 59.65 | 59.6578 | -62.404 | 0.024738 | -0.079996 | -0.01375 | 0.01488 | -0.009858 | -0.32625 | -0.27123 | -0.12526 | -0.24309 | 0.027656 | -0.070951 | 0.054312 | -0.11104 | -0.10326 | 121.9598 | 121.7135 | 121.7686 | 62.2893 | -122.0151 | 121.7967 | 121.9288 | 121.9365 | 62.3569 | -122.1651
678.0781 | 122.2275 | -62.2925 | 59.8251 | 1.4211e-13 | -0.031442 | -0.0053696 | 0.065366 | -0.005786 | 0.056668 | -0.0054937 | 0.00057035 | -0.0021152 | -0.0036534 | 0.022483 | -0.010668 | -62.2925 | 0.010564 | -62.2593 | 59.6856 | 59.4394 | 59.4898 | -62.2494 | -62.2557 | 0.082776 | -62.3634 | 59.5271 | 59.6454 | 59.6624 | -62.404 | 0.043049 | -0.1395 | -1.8e-05 | 0.03319 | -0.009859 | -0.38576 | -0.33532 | -0.11153 | -0.29802 | 0.03681 | -0.070955 | 0.040576 | -0.17971 | -0.16277 | 121.9781 | 121.7319 | 121.7823 | 62.303 | -122.0746 | 121.8196 | 121.9379 | 121.9548 | 62.3753 | -122.2291
679.7656 | 122.2092 | -62.2971 | 59.8114 | 1.4211e-13 | -0.031228 | -0.005156 | 0.065579 | -0.0059996 | 0.056668 | 0.0097668 | 0.00014315 | -0.0021152 | -0.0036534 | 0.022269 | -0.010454 | -62.2879 | 0.005985 | -62.2684 | 59.6856 | 59.444 | 59.5035 | -62.2586 | -62.2557 | 0.082776 | -62.3634 | 59.5225 | 59.6408 | 59.6624 | -62.404 | 0.038469 | -0.12577 | 0.009139 | 0.028612 | -0.009857 | -0.36744 | -0.30785 | -0.10695 | -0.28887 | 0.041388 | -0.066377 | 0.040576 | -0.17055 | -0.14904 | 121.9827 | 121.741 | 121.8006 | 62.303 | -122.07 | 121.8196 | 121.9379 | 121.9594 | 62.3798 | -122.2154
681.5 | 122.2183 | -62.3016 | 59.8114 | 1.4211e-13 | -0.031228 | -0.0049424 | 0.065793 | -0.005786 | 0.056668 | -0.013124 | 0.00057035 | -0.0021152 | -0.003867 | 0.022696 | -0.010668 | -62.2879 | 0.010564 | -62.2593 | 59.6856 | 59.4394 | 59.4944 | -62.254 | -62.2602 | 0.082776 | -62.3589 | 59.5271 | 59.65 | 59.6532 | -62.3994 | 0.047626 | -0.12577 | 0.013717 | 0.042346 | -0.00528 | -0.37202 | -0.31701 | -0.097796 | -0.28429 | 0.041387 | -0.05722 | 0.040576 | -0.1614 | -0.15819 | 121.9873 | 121.741 | 121.796 | 62.3122 | -122.0654 | 121.8287 | 121.9516 | 121.9548 | 62.3844 | -122.2108
683.2344 | 122.3053 | -62.2879 | 59.7473 | 1.4211e-13 | -0.031442 | -0.0049424 | 0.065579 | -0.0059996 | 0.056454 | -0.013124 | 0.00035675 | -0.0021152 | -0.0036534 | 0.022269 | -0.010668 | -62.2925 | 0.015142 | -62.2639 | 59.6856 | 59.4531 | 59.4944 | -62.2586 | -62.2511 | 0.087354 | -62.3543 | 59.518 | 59.6454 | 59.6669 | -62.3994 | 0.029314 | -0.061684 | -0.004595 | 0.024035 | -0.005279 | -0.2942 | -0.25292 | -0.11153 | -0.22936 | 0.036811 | -0.066374 | 0.045155 | -0.10189 | -0.080373 | 121.9735 | 121.741 | 121.7823 | 62.303 | -122.0059 | 121.8059 | 121.9333 | 121.9548 | 62.3753 | -122.1467
684.9844 | 122.2229 | -62.2833 | 59.8114 | 1.4211e-13 | -0.031442 | -0.005156 | 0.065579 | -0.0059996 | 0.056881 | -0.013124 | 0.00057035 | -0.0019016 | -0.0036534 | 0.022269 | -0.010881 | -62.2879 | 0.005985 | -62.2593 | 59.6856 | 59.4394 | 59.4944 | -62.2586 | -62.2602 | 0.078197 | -62.3543 | 59.518 | 59.6454 | 59.6624 | -62.4086 | 0.024736 | -0.12577 | -0.004594 | 0.024035 | -0.000701 | -0.37202 | -0.31701 | -0.12526 | -0.29345 | 0.023076 | -0.070952 | 0.054313 | -0.16597 | -0.14904 | 121.969 | 121.7227 | 121.7777 | 62.2893 | -122.07 | 121.8013 | 121.9288 | 121.9457 | 62.3615 | -122.22
686.7188 | 122.2733 | -62.2696 | 59.8251 | 1.4211e-13 | -0.031442 | -0.0049424 | 0.065366 | -0.0059996 | 0.056881 | 0.0021363 | 0.00035675 | -0.0023288 | -0.003226 | 0.022269 | -0.010881 | -62.2879 | 0.001407 | -62.2593 | 59.6856 | 59.4348 | 59.499 | -62.254 | -62.2602 | 0.078197 | -62.3589 | 59.518 | 59.6454 | 59.6578 | -62.4086 | 0.015582 | -0.1395 | -0.018327 | 0.010302 | -0.00528 | -0.39033 | -0.32616 | -0.139 | -0.30718 | 0.009343 | -0.089264 | 0.049734 | -0.17971 | -0.16735 | 121.9552 | 121.7044 | 121.7686 | 62.271 | -122.0791 | 121.7875 | 121.915 | 121.9274 | 62.3478 | -122.2337
688.4062 | 122.2961 | -62.3016 | 59.7931 | 1.4211e-13 | -0.031442 | -0.0049424 | 0.065579 | -0.0062134 | 0.056668 | 0.0097668 | -7.0448e-05 | -0.0021152 | -0.0034396 | 0.022269 | -0.010881 | -62.2879 | 0.005985 | -62.2684 | 59.6856 | 59.4394 | 59.4898 | -62.2586 | -62.2602 | 0.082776 | -62.3543 | 59.5225 | 59.6454 | 59.6624 | -62.3949 | 0.043047 | -0.10746 | 0.013717 | 0.03319 | -0.009857 | -0.35371 | -0.30328 | -0.093217 | -0.27056 | 0.041387 | -0.052641 | 0.040576 | -0.14766 | -0.13073 | 121.9873 | 121.741 | 121.7914 | 62.3076 | -122.0517 | 121.8242 | 121.9471 | 121.964 | 62.3844 | -122.1879
690.1562 | 122.3145 | -62.2513 | 59.816 | 1.4211e-13 | -0.031228 | -0.0049424 | 0.065366 | -0.0062134 | 0.056668 | -0.0054937 | 0.00057035 | -0.0019016 | -0.003867 | 0.022696 | -0.010454 | -62.2879 | 0.005985 | -62.2684 | 59.6811 | 59.4394 | 59.4944 | -62.254 | -62.2648 | 0.082776 | -62.3589 | 59.5225 | 59.6454 | 59.6624 | -62.404 | -0.002728 | -0.13493 | -0.036637 | -0.017164 | -0.014436 | -0.3766 | -0.32159 | -0.15273 | -0.29345 | -0.013546 | -0.10757 | 0.045155 | -0.17055 | -0.15362 | 121.9323 | 121.6907 | 121.7457 | 62.2573 | -122.07 | 121.7738 | 121.8967 | 121.9136 | 62.3341 | -122.22
691.8906 | 122.3373 | -62.2696 | 59.8114 | 1.4211e-13 | -0.031228 | -0.0047286 | 0.065579 | -0.0059996 | 0.056881 | -0.0054937 | 0.00057035 | -0.0016878 | -0.0034396 | 0.022269 | -0.010881 | -62.2833 | 0.010564 | -62.2684 | 59.6856 | 59.444 | 59.499 | -62.254 | -62.2602 | 0.082776 | -62.3589 | 59.5225 | 59.6592 | 59.6669 | -62.404 | 0.015582 | -0.12577 | -0.013749 | 0.001146 | -0.014436 | -0.36744 | -0.31243 | -0.13442 | -0.28887 | 0.009343 | -0.089264 | 0.045155 | -0.15224 | -0.14446 | 121.9552 | 121.7135 | 121.7686 | 62.2802 | -122.0654 | 121.7921 | 121.9288 | 121.9365 | 62.3524 | -122.2154
693.5781 | 122.2183 | -62.2833 | 59.7839 | 1.4211e-13 | -0.031442 | -0.005156 | 0.065579 | -0.0059996 | 0.056881 | -0.0054937 | 0.00035675 | -0.0021152 | -0.0036534 | 0.022269 | -0.010668 | -62.2833 | 0.005985 | -62.2639 | 59.6902 | 59.444 | 59.499 | -62.254 | -62.2557 | 0.073618 | -62.3589 | 59.518 | 59.6454 | 59.6578 | -62.404 | 0.029315 | -0.093728 | -1.6e-05 | 0.019457 | -0.009858 | -0.33998 | -0.28497 | -0.12069 | -0.26598 | 0.027655 | -0.075531 | 0.045155 | -0.13851 | -0.12615 | 121.9735 | 121.7273 | 121.7823 | 62.2893 | -122.0379 | 121.8013 | 121.9288 | 121.9411 | 62.3569 | -122.1879
695.3281 | 122.2137 | -62.2879 | 59.8297 | 1.4211e-13 | -0.031656 | -0.005156 | 0.065579 | -0.0059996 | 0.056668 | -0.0054937 | 0.00057035 | -0.0021152 | -0.003226 | 0.022483 | -0.010881 | -62.2925 | 0.010564 | -62.273 | 59.6902 | 59.4394 | 59.5035 | -62.2586 | -62.2602 | 0.082776 | -62.3634 | 59.518 | 59.65 | 59.6669 | -62.4086 | 0.029314 | -0.1395 | -0.004595 | 0.014878 | -0.014436 | -0.39033 | -0.32616 | -0.12069 | -0.31176 | 0.027654 | -0.075532 | 0.045155 | -0.17971 | -0.16277 | 121.9781 | 121.7273 | 121.7915 | 62.2985 | -122.0883 | 121.8059 | 121.9379 | 121.9548 | 62.3707 | -122.2383
697.0625 | 122.2504 | -62.2879 | 59.8389 | 1.4211e-13 | -0.031656 | -0.0053696 | 0.065366 | -0.0062134 | 0.056668 | -0.013124 | 0.00014315 | -0.0021152 | -0.0036534 | 0.022269 | -0.010668 | -62.2833 | 0.010564 | -62.2684 | 59.6902 | 59.4485 | 59.499 | -62.2586 | -62.2648 | 0.087354 | -62.3589 | 59.518 | 59.6454 | 59.6578 | -62.4086 | 0.029314 | -0.14866 | 0.004562 | 0.019457 | -0.009857 | -0.39033 | -0.3399 | -0.12069 | -0.32091 | 0.023075 | -0.070953 | 0.049734 | -0.19344 | -0.18108 | 121.9781 | 121.7364 | 121.7869 | 62.2985 | -122.0975 | 121.8059 | 121.9333 | 121.9457 | 62.3753 | -122.2475
698.7344 | 122.3145 | -62.3062 | 59.7336 | 1.4211e-13 | -0.031442 | -0.0049424 | 0.065579 | -0.0062134 | 0.056454 | -0.0054937 | 0.00035675 | -0.0019016 | -0.0034396 | 0.022483 | -0.011095 | -62.2833 | 0.010564 | -62.2684 | 59.6902 | 59.4485 | 59.499 | -62.2632 | -62.2602 | 0.082776 | -62.3543 | 59.5271 | 59.6546 | 59.6624 | -62.4086 | 0.043045 | -0.043374 | 0.022872 | 0.037767 | -0.005278 | -0.28505 | -0.23461 | -0.10238 | -0.20647 | 0.045964 | -0.048064 | 0.054313 | -0.078999 | -0.071219 | 121.9964 | 121.7547 | 121.8052 | 62.3168 | -121.9967 | 121.8333 | 121.9608 | 121.9686 | 62.389 | -122.1422
700.4844 | 122.3373 | -62.2375 | 59.8022 | 1.4211e-13 | -0.031656 | -0.0053696 | 0.064938 | -0.005786 | 0.056454 | -0.0054937 | 0.00057035 | -0.0023288 | -0.003867 | 0.022055 | -0.010668 | -62.2879 | 0.005985 | -62.2547 | 59.6856 | 59.4394 | 59.4944 | -62.2494 | -62.2557 | 0.082776 | -62.3589 | 59.518 | 59.6454 | 59.6532 | -62.4086 | -0.011882 | -0.11662 | -0.05037 | -0.017163 | -0.005281 | -0.36287 | -0.30786 | -0.17104 | -0.28429 | -0.018121 | -0.12131 | 0.049734 | -0.15682 | -0.14904 | 121.9232 | 121.6769 | 121.7319 | 62.2435 | -122.0517 | 121.7555 | 121.883 | 121.8908 | 62.3203 | -122.2108
702.2344 | 122.2778 | -62.2833 | 59.8297 | 1.4211e-13 | -0.031869 | -0.0053696 | 0.065793 | -0.0055724 | 0.056881 | 0.0021363 | 0.00035675 | -0.0019016 | -0.0034396 | 0.022696 | -0.011095 | -62.2925 | 0.010564 | -62.2639 | 59.6902 | 59.444 | 59.4944 | -62.2586 | -62.2694 | 0.078197 | -62.3634 | 59.5271 | 59.6454 | 59.6624 | -62.3994 | 0.024736 | -0.1395 | -0.009173 | 0.019457 | -0.005279 | -0.38576 | -0.33532 | -0.11611 | -0.3026 | 0.013919 | -0.08011 | 0.035997 | -0.18429 | -0.16735 | 121.9735 | 121.7273 | 121.7777 | 62.2939 | -122.0883 | 121.8104 | 121.9288 | 121.9457 | 62.3615 | -122.2291
703.9844 | 122.2641 | -62.2559 | 59.8251 | 1.4211e-13 | -0.031442 | -0.0049424 | 0.065366 | -0.0062134 | 0.056668 | -0.0054937 | 0.00035675 | -0.0025424 | -0.0036534 | 0.022483 | -0.010668 | -62.2879 | 0.001407 | -62.2684 | 59.6811 | 59.4485 | 59.499 | -62.2632 | -62.2602 | 0.073618 | -62.3589 | 59.5271 | 59.6454 | 59.6624 | -62.4132 | -0.007309 | -0.14408 | -0.03206 | -0.012587 | -0.005278 | -0.3766 | -0.32616 | -0.15731 | -0.29802 | -0.00439 | -0.103 | 0.054313 | -0.17971 | -0.16277 | 121.9369 | 121.7044 | 121.7548 | 62.2573 | -122.0883 | 121.783 | 121.9013 | 121.9182 | 62.3295 | -122.2383
705.6719 | 122.3648 | -62.2467 | 59.7656 | 1.4211e-13 | -0.031656 | -0.005156 | 0.065579 | -0.0062134 | 0.056454 | -0.0054937 | 0.00014315 | -0.0023288 | -0.0034396 | 0.022055 | -0.010668 | -62.2833 | 0.010564 | -62.2684 | 59.6856 | 59.4394 | 59.4898 | -62.2586 | -62.2648 | 0.087354 | -62.3589 | 59.518 | 59.6408 | 59.6624 | -62.404 | -0.011885 | -0.079995 | -0.036637 | -0.021742 | -0.009857 | -0.32625 | -0.27581 | -0.15731 | -0.24767 | -0.018124 | -0.11215 | 0.045155 | -0.12478 | -0.10326 | 121.9323 | 121.6861 | 121.7365 | 62.2573 | -122.0242 | 121.7647 | 121.8876 | 121.9091 | 62.3341 | -122.1696
707.4062 | 122.2275 | -62.2971 | 59.8434 | 1.4211e-13 | -0.031869 | -0.0053696 | 0.065366 | -0.0055724 | 0.057095 | 0.0021363 | 0.00014315 | -0.0025424 | -0.0036534 | 0.022696 | -0.010881 | -62.2879 | 0.010564 | -62.2684 | 59.6902 | 59.4394 | 59.499 | -62.2494 | -62.2557 | 0.082776 | -62.3634 | 59.518 | 59.6454 | 59.6624 | -62.4086 | 0.047627 | -0.15324 | 0.009139 | 0.028612 | -0.019015 | -0.40407 | -0.34448 | -0.11153 | -0.32549 | 0.041388 | -0.066377 | 0.045155 | -0.19802 | -0.18108 | 121.9873 | 121.7364 | 121.796 | 62.3076 | -122.0929 | 121.815 | 121.9425 | 121.9594 | 62.3798 | -122.252
709.1562 | 122.2412 | -62.3062 | 59.8068 | 1.4211e-13 | -0.031442 | -0.0053696 | 0.065579 | -0.0059996 | 0.056454 | -0.0054937 | 0.00035675 | -0.0021152 | -0.0034396 | 0.022696 | -0.011309 | -62.2925 | 0.010564 | -62.2639 | 59.6856 | 59.444 | 59.499 | -62.254 | -62.2602 | 0.087354 | -62.3634 | 59.518 | 59.65 | 59.6669 | -62.404 | 0.052203 | -0.12119 | 0.013715 | 0.042345 | -0.009858 | -0.36287 | -0.30785 | -0.097798 | -0.28887 | 0.045964 | -0.057222 | 0.040576 | -0.15682 | -0.13988 | 121.9918 | 121.7502 | 121.8052 | 62.3168 | -122.0608 | 121.8242 | 121.9562 | 121.9732 | 62.3936 | -122.2108
710.9062 | 122.3373 | -62.2467 | 59.8068 | 1.4211e-13 | -0.031656 | -0.0053696 | 0.065366 | -0.0055724 | 0.05624 | 0.0021363 | 0.00035675 | -0.0023288 | -0.0036534 | 0.022483 | -0.011095 | -62.2879 | 0.010564 | -62.2684 | 59.6811 | 59.4394 | 59.499 | -62.2586 | -62.2602 | 0.087354 | -62.3543 | 59.5225 | 59.6454 | 59.6624 | -62.404 | -0.011885 | -0.12577 | -0.041215 | -0.021742 | -0.009857 | -0.36745 | -0.30785 | -0.15731 | -0.28429 | -0.013545 | -0.10757 | 0.049734 | -0.1614 | -0.14446 | 121.9278 | 121.6861 | 121.7457 | 62.2573 | -122.0654 | 121.7692 | 121.8921 | 121.9091 | 62.3341 | -122.2108
712.5938 | 122.2229 | -62.2742 | 59.8389 | 1.4211e-13 | -0.032083 | -0.005156 | 0.065793 | -0.005786 | 0.056668 | -0.0054937 | 0.00035675 | -0.0019016 | -0.003867 | 0.022483 | -0.010668 | -62.2879 | 0.019721 | -62.2639 | 59.6856 | 59.444 | 59.499 | -62.2586 | -62.2648 | 0.078197 | -62.3589 | 59.5225 | 59.6454 | 59.6578 | -62.3994 | 0.015581 | -0.15324 | -0.013749 | 0.010302 | -0.005279 | -0.39491 | -0.3399 | -0.12526 | -0.31633 | 0.009342 | -0.084686 | 0.040576 | -0.19344 | -0.18108 | 121.9598 | 121.7181 | 121.7731 | 62.2939 | -122.0975 | 121.7967 | 121.9196 | 121.932 | 62.3524 | -122.2383
714.3281 | 122.2321 | -62.2833 | 59.8618 | 1.4211e-13 | -0.031442 | -0.0049424 | 0.065366 | -0.005786 | 0.056881 | -0.0054937 | 0.00035675 | -0.0021152 | -0.003867 | 0.022269 | -0.010881 | -62.2879 | 0.019721 | -62.2822 | 59.6948 | 59.4623 | 59.4944 | -62.2586 | -62.2648 | 0.082776 | -62.368 | 59.5225 | 59.6454 | 59.6578 | -62.4086 | 0.024736 | -0.16697 | -0.004594 | 0.001144 | -0.023592 | -0.39948 | -0.36736 | -0.12526 | -0.33922 | 0.018497 | -0.084688 | 0.040577 | -0.21633 | -0.20397 | 121.9781 | 121.7456 | 121.7777 | 62.303 | -122.1203 | 121.8059 | 121.9288 | 121.9411 | 62.3661 | -122.2703
716.0781 | 122.319 | -62.2925 | 59.7885 | 1.4211e-13 | -0.032083 | -0.005156 | 0.065579 | -0.0053586 | 0.056668 | -0.0054937 | 0.00078395 | -0.0023288 | -0.0036534 | 0.022696 | -0.010881 | -62.2833 | 0.005985 | -62.2639 | 59.6902 | 59.444 | 59.499 | -62.2632 | -62.2557 | 0.087354 | -62.3589 | 59.5225 | 59.65 | 59.6532 | -62.4086 | 0.029312 | -0.098305 | 0.009139 | 0.028612 | -0.0007 | -0.34456 | -0.28954 | -0.11611 | -0.26598 | 0.03681 | -0.066376 | 0.049734 | -0.13851 | -0.13531 | 121.9827 | 121.7364 | 121.7914 | 62.2985 | -122.0517 | 121.815 | 121.9425 | 121.9457 | 62.3798 | -122.1971
717.7656 | 122.2595 | -62.2879 | 59.8022 | 1.4211e-13 | -0.031656 | -0.0049424 | 0.065579 | -0.0062134 | 0.056454 | -0.013124 | 0.00035675 | -0.0021152 | -0.0034396 | 0.022696 | -0.010881 | -62.3017 | 0.001407 | -62.2639 | 59.6902 | 59.4394 | 59.499 | -62.2632 | -62.2648 | 0.078197 | -62.3543 | 59.5225 | 59.65 | 59.6578 | -62.3994 | 0.024735 | -0.11204 | -0.013751 | 0.024035 | -0.0007 | -0.36287 | -0.30328 | -0.11153 | -0.27971 | 0.023075 | -0.066374 | 0.045155 | -0.15224 | -0.14446 | 121.9781 | 121.7273 | 121.7869 | 62.2893 | -122.0654 | 121.8104 | 121.9379 | 121.9457 | 62.3661 | -122.2017
719.5 | 122.374 | -62.2787 | 59.7794 | 1.4211e-13 | -0.031656 | -0.0049424 | 0.065579 | -0.0059996 | 0.056881 | -0.0054937 | 0.00014315 | -0.0019016 | -0.0034396 | 0.022696 | -0.011309 | -62.2879 | 0.015142 | -62.2639 | 59.6902 | 59.444 | 59.4944 | -62.2677 | -62.2602 | 0.082776 | -62.3634 | 59.5271 | 59.6546 | 59.6669 | -62.4086 | 0.011001 | -0.08915 | -0.009171 | 0.01488 | 0.003879 | -0.3354 | -0.28497 | -0.12984 | -0.25225 | 0.018499 | -0.084687 | 0.045155 | -0.12477 | -0.11242 | 121.969 | 121.7227 | 121.7731 | 62.2939 | -122.0471 | 121.8059 | 121.9333 | 121.9457 | 62.3615 | -122.1879
721.2344 | 122.3465 | -62.2696 | 59.7565 | 1.4211e-13 | -0.031442 | -0.0047286 | 0.065579 | -0.0062134 | 0.056454 | -0.013124 | 0.00035675 | -0.0023288 | -0.0034396 | 0.022696 | -0.010454 | -62.2879 | 0.010564 | -62.2639 | 59.6902 | 59.4669 | 59.5035 | -62.2586 | -62.2557 | 0.087354 | -62.3543 | 59.5225 | 59.6546 | 59.6669 | -62.404 | 0.011003 | -0.066262 | -0.018327 | 0.005724 | -0.005279 | -0.28962 | -0.25292 | -0.13442 | -0.23394 | 0.013922 | -0.084685 | 0.049734 | -0.10189 | -0.089529 | 121.9598 | 121.7364 | 121.7731 | 62.2802 | -122.0151 | 121.7921 | 121.9242 | 121.9365 | 62.3569 | -122.1605
722.9844 | 122.3511 | -62.2696 | 59.7748 | 1.4211e-13 | -0.031869 | -0.005156 | 0.065152 | -0.0059996 | 0.056454 | 0.0021363 | 0.00014315 | -0.0021152 | -0.0034396 | 0.022696 | -0.010668 | -62.2879 | 0.015142 | -62.2593 | 59.6902 | 59.4485 | 59.499 | -62.254 | -62.2602 | 0.087354 | -62.3543 | 59.5225 | 59.65 | 59.6578 | -62.4086 | 0.015582 | -0.084572 | -0.018327 | 0.010302 | -0.00528 | -0.32624 | -0.27581 | -0.139 | -0.25225 | 0.009343 | -0.084685 | 0.054313 | -0.12478 | -0.117 | 121.9598 | 121.7181 | 121.7686 | 62.2847 | -122.0288 | 121.7921 | 121.9196 | 121.9274 | 62.3569 | -122.1834
724.6719 | 122.3694 | -62.2559 | 59.7794 | 1.4211e-13 | -0.032083 | -0.005156 | 0.065366 | -0.0062134 | 0.056454 | -0.020755 | 0.00035675 | -0.0021152 | -0.0036534 | 0.022269 | -0.011095 | -62.2879 | 0.010564 | -62.2639 | 59.6902 | 59.444 | 59.499 | -62.254 | -62.2602 | 0.087354 | -62.3589 | 59.5225 | 59.65 | 59.6624 | -62.4086 | 0.001849 | -0.08915 | -0.03206 | -0.008009 | -0.009858 | -0.3354 | -0.28039 | -0.15273 | -0.25682 | -0.00439 | -0.103 | 0.049734 | -0.12935 | -0.117 | 121.9461 | 121.6998 | 121.7548 | 62.2664 | -122.0334 | 121.7784 | 121.9059 | 121.9182 | 62.3432 | -122.1879
726.4062 | 122.2961 | -62.2559 | 59.8251 | 1.4211e-13 | -0.032083 | -0.005156 | 0.065152 | -0.006427 | 0.056668 | -0.0054937 | 0.00035675 | -0.0019016 | -0.0034396 | 0.022483 | -0.010881 | -62.2879 | 0.010564 | -62.2639 | 59.6902 | 59.444 | 59.5035 | -62.2586 | -62.2557 | 0.082776 | -62.3634 | 59.5225 | 59.6546 | 59.6578 | -62.3949 | -0.00273 | -0.13493 | -0.03206 | -0.008009 | -0.005279 | -0.38118 | -0.32159 | -0.13899 | -0.3026 | 0.000189 | -0.10758 | 0.031418 | -0.17055 | -0.16735 | 121.9461 | 121.6998 | 121.7594 | 62.2664 | -122.0837 | 121.7784 | 121.9104 | 121.9136 | 62.3386 | -122.22
728.1406 | 122.2778 | -62.2833 | 59.816 | 1.4211e-13 | -0.032297 | -0.0053696 | 0.065579 | -0.0062134 | 0.056881 | 0.0021363 | 0.00035675 | -0.0021152 | -0.0034396 | 0.022696 | -0.010881 | -62.2879 | 0.010564 | -62.2639 | 59.6902 | 59.4531 | 59.4944 | -62.2632 | -62.2648 | 0.087354 | -62.368 | 59.518 | 59.6546 | 59.6578 | -62.3949 | 0.020157 | -0.12577 | -0.004594 | 0.019457 | -0.0007 | -0.36286 | -0.32159 | -0.11153 | -0.29802 | 0.018497 | -0.084688 | 0.02684 | -0.1614 | -0.15819 | 121.9735 | 121.7364 | 121.7777 | 62.2939 | -122.0791 | 121.8013 | 121.9379 | 121.9411 | 62.3707 | -122.2108
729.8281 | 122.2321 | -62.2879 | 59.8251 | 1.4211e-13 | -0.031656 | -0.0049424 | 0.065366 | -0.0062134 | 0.056454 | -0.0054937 | 0.00014315 | -0.0021152 | -0.0034396 | 0.02291 | -0.010881 | -62.2833 | 0.001407 | -62.2639 | 59.6902 | 59.444 | 59.5035 | -62.2586 | -62.2648 | 0.082776 | -62.3589 | 59.518 | 59.6454 | 59.6578 | -62.404 | 0.029314 | -0.13493 | 0.004562 | 0.024035 | -0.005279 | -0.38118 | -0.32159 | -0.11611 | -0.30718 | 0.023075 | -0.070953 | 0.045155 | -0.17971 | -0.16735 | 121.9781 | 121.7319 | 121.7915 | 62.2893 | -122.0837 | 121.8059 | 121.9333 | 121.9457 | 62.3707 | -122.2291
731.5625 | 122.3373 | -62.2971 | 59.7244 | 1.4211e-13 | -0.031869 | -0.005156 | 0.065366 | -0.0059996 | 0.057095 | 0.0097668 | 0.00035675 | -0.0021152 | -0.0030124 | 0.022483 | -0.011095 | -62.2879 | 0.005985 | -62.2593 | 59.6811 | 59.4531 | 59.499 | -62.2632 | -62.2602 | 0.087354 | -62.3543 | 59.5225 | 59.65 | 59.6669 | -62.404 | 0.03389 | -0.043375 | 0.009139 | 0.037768 | 0.003878 | -0.27131 | -0.22546 | -0.10695 | -0.20189 | 0.036809 | -0.057219 | 0.049734 | -0.074422 | -0.057485 | 121.9781 | 121.7502 | 121.796 | 62.303 | -121.9876 | 121.8196 | 121.9471 | 121.964 | 62.3844 | -122.1284
733.3125 | 122.3465 | -62.2742 | 59.761 | 1.4211e-13 | -0.032297 | -0.0053696 | 0.065152 | -0.005786 | 0.056454 | -0.0054937 | 0.00057035 | -0.0019016 | -0.0034396 | 0.02291 | -0.010881 | -62.2925 | 0.005985 | -62.2639 | 59.6856 | 59.4485 | 59.499 | -62.2632 | -62.2648 | 0.087354 | -62.3634 | 59.5225 | 59.65 | 59.6624 | -62.3994 | 0.011002 | -0.075417 | -0.018328 | 0.010302 | -0.0007 | -0.31251 | -0.26208 | -0.12526 | -0.23851 | 0.009342 | -0.089265 | 0.035997 | -0.11104 | -0.098684 | 121.9598 | 121.7227 | 121.7731 | 62.2802 | -122.0242 | 121.7967 | 121.9242 | 121.9365 | 62.3615 | -122.1605
735.0625 | 122.3328 | -62.2879 | 59.7473 | 1.4211e-13 | -0.031869 | -0.005156 | 0.065579 | -0.006427 | 0.056668 | -0.013124 | 0.00014315 | -0.0019016 | -0.0036534 | 0.022696 | -0.011309 | -62.2879 | 0.010564 | -62.2684 | 59.6948 | 59.4485 | 59.499 | -62.2586 | -62.2694 | 0.087354 | -62.3543 | 59.5134 | 59.65 | 59.6669 | -62.404 | 0.029314 | -0.052528 | -1.6e-05 | 0.019457 | -0.009857 | -0.29878 | -0.24835 | -0.11611 | -0.23394 | 0.018497 | -0.066374 | 0.049734 | -0.09731 | -0.080373 | 121.9827 | 121.7364 | 121.7869 | 62.2985 | -122.0059 | 121.8013 | 121.9379 | 121.9548 | 62.3753 | -122.1513
736.75 | 122.3465 | -62.2742 | 59.7794 | 1.4211e-13 | -0.032083 | -0.005156 | 0.065366 | -0.0059996 | 0.056668 | -0.0054937 | 0.00035675 | -0.0021152 | -0.0040806 | 0.022483 | -0.010881 | -62.2879 | 0.010564 | -62.2593 | 59.6811 | 59.444 | 59.499 | -62.2632 | -62.2648 | 0.087354 | -62.3634 | 59.5042 | 59.6546 | 59.6624 | -62.404 | 0.011002 | -0.098307 | -0.013749 | 0.01488 | 0.003878 | -0.3354 | -0.28039 | -0.12984 | -0.27514 | 0.009342 | -0.089265 | 0.040576 | -0.12477 | -0.117 | 121.9552 | 121.7181 | 121.7731 | 62.2847 | -122.0425 | 121.7784 | 121.9288 | 121.9365 | 62.3615 | -122.1834
738.4844 | 122.3099 | -62.2833 | 59.7794 | 1.4211e-13 | -0.032083 | -0.005156 | 0.065579 | -0.0062134 | 0.056454 | -0.0054937 | 0.00014315 | -0.0019016 | -0.0036534 | 0.022696 | -0.010881 | -62.2833 | 0.005985 | -62.2639 | 59.6948 | 59.4485 | 59.5035 | -62.2586 | -62.2557 | 0.078197 | -62.3589 | 59.5134 | 59.65 | 59.6624 | -62.4086 | 0.024736 | -0.084572 | -1.6e-05 | 0.019457 | -0.005279 | -0.33082 | -0.27581 | -0.12526 | -0.26598 | 0.027655 | -0.075531 | 0.049734 | -0.12935 | -0.117 | 121.9781 | 121.7319 | 121.7869 | 62.2893 | -122.0379 | 121.7967 | 121.9333 | 121.9457 | 62.3615 | -122.1879
740.2344 | 122.3282 | -62.3199 | 59.7473 | 1.4211e-13 | -0.032297 | -0.0049424 | 0.065579 | -0.006427 | 0.056454 | -0.020755 | 0.00014315 | -0.0019016 | -0.0034396 | 0.022483 | -0.011309 | -62.2925 | 0.010564 | -62.273 | 59.6902 | 59.4485 | 59.5035 | -62.2586 | -62.2694 | 0.087354 | -62.3589 | 59.518 | 59.65 | 59.6669 | -62.404 | 0.061357 | -0.057106 | 0.027448 | 0.046921 | -0.014436 | -0.29878 | -0.24377 | -0.084065 | -0.22936 | 0.05054 | -0.03891 | 0.045155 | -0.09731 | -0.080373 | 122.0102 | 121.7685 | 121.8235 | 62.3305 | -122.0059 | 121.8379 | 121.97 | 121.9869 | 62.4073 | -122.1513
741.9688 | 122.319 | -62.3199 | 59.761 | 1.4211e-13 | -0.032297 | -0.0053696 | 0.065579 | -0.0062134 | 0.056454 | -0.0054937 | 0.00014315 | -0.0019016 | -0.0036534 | 0.022269 | -0.011522 | -62.2925 | 0.001407 | -62.2639 | 59.6948 | 59.4577 | 59.499 | -62.2586 | -62.2694 | 0.091933 | -62.3543 | 59.5134 | 59.65 | 59.6624 | -62.4086 | 0.061357 | -0.066261 | 0.027448 | 0.056078 | -0.005279 | -0.30335 | -0.26208 | -0.088644 | -0.24767 | 0.05054 | -0.034331 | 0.054313 | -0.11104 | -0.098684 | 122.0147 | 121.7776 | 121.8189 | 62.3214 | -122.0196 | 121.8333 | 121.97 | 121.9823 | 62.4119 | -122.1696
743.6406 | 122.2458 | -62.265 | 59.8206 | 1.4211e-13 | -0.032083 | -0.005156 | 0.065366 | -0.0059996 | 0.056881 | 0.0021363 | 0.00014315 | -0.0021152 | -0.0034396 | 0.022696 | -0.011095 | -62.2925 | 0.005985 | -62.2684 | 59.6811 | 59.444 | 59.4944 | -62.2586 | -62.2694 | 0.082776 | -62.3634 | 59.5088 | 59.6592 | 59.6624 | -62.4086 | 0.006426 | -0.13951 | -0.027483 | -0.003431 | -0.009857 | -0.3766 | -0.32617 | -0.14357 | -0.31176 | -0.004391 | -0.09842 | 0.045155 | -0.16139 | -0.15819 | 121.9461 | 121.709 | 121.7594 | 62.271 | -122.0791 | 121.7738 | 121.9242 | 121.9274 | 62.3478 | -122.2291
745.3906 | 122.2183 | -62.2833 | 59.8251 | 1.4211e-13 | -0.03251 | -0.0049424 | 0.065579 | -0.0062134 | 0.056668 | -0.0054937 | 0.00057035 | -0.0021152 | -0.0034396 | 0.022696 | -0.011309 | -62.2879 | 0.015142 | -62.2684 | 59.6811 | 59.4531 | 59.4944 | -62.254 | -62.2648 | 0.082776 | -62.3589 | 59.518 | 59.6546 | 59.6624 | -62.4086 | 0.029315 | -0.14408 | -0.004594 | 0.014879 | -0.014436 | -0.37202 | -0.33074 | -0.12526 | -0.30718 | 0.018497 | -0.075531 | 0.049734 | -0.17055 | -0.16277 | 121.9644 | 121.7364 | 121.7777 | 62.2985 | -122.0791 | 121.8013 | 121.9379 | 121.9457 | 62.3661 | -122.2337
747.0625 | 122.2687 | -62.2787 | 59.816 | 1.4211e-13 | -0.032297 | -0.005156 | 0.065579 | -0.0062134 | 0.056454 | -0.028385 | 0.00057035 | -0.0021152 | -0.0036534 | 0.022696 | -0.011309 | -62.2971 | 0.010564 | -62.273 | 59.6856 | 59.444 | 59.5035 | -62.2494 | -62.2694 | 0.091933 | -62.3634 | 59.5134 | 59.6546 | 59.6624 | -62.3994 | 0.029317 | -0.13035 | -0.018328 | 0.005723 | -0.023594 | -0.37202 | -0.31243 | -0.12068 | -0.3026 | 0.009342 | -0.084687 | 0.035997 | -0.1614 | -0.15362 | 121.9644 | 121.7227 | 121.7823 | 62.2893 | -122.0654 | 121.7921 | 121.9333 | 121.9411 | 62.3707 | -122.2154
748.7969 | 122.2733 | -62.2559 | 59.7977 | 1.4211e-13 | -0.032724 | -0.005156 | 0.065366 | -0.006427 | 0.056668 | -0.0054937 | 0.00057035 | -0.0021152 | -0.0034396 | 0.02291 | -0.010881 | -62.2833 | 0.005985 | -62.2684 | 59.6902 | 59.4531 | 59.499 | -62.254 | -62.2602 | 0.082776 | -62.3543 | 59.5271 | 59.65 | 59.6624 | -62.4086 | 0.001849 | -0.10746 | -0.027482 | -0.012587 | -0.014436 | -0.34455 | -0.2987 | -0.15273 | -0.27056 | -0.00439 | -0.098418 | 0.054313 | -0.14766 | -0.13531 | 121.9461 | 121.709 | 121.7548 | 62.2618 | -122.0517 | 121.783 | 121.9059 | 121.9182 | 62.3386 | -122.2063
750.5469 | 122.3465 | -62.2925 | 59.7473 | 1.4211e-13 | -0.032083 | -0.005156 | 0.065152 | -0.0062134 | 0.05624 | -0.020755 | 0.00014315 | -0.0019016 | -0.003867 | 0.022696 | -0.011309 | -62.2879 | 0.005985 | -62.273 | 59.6856 | 59.4485 | 59.5035 | -62.254 | -62.2557 | 0.091933 | -62.3543 | 59.518 | 59.6592 | 59.6624 | -62.404 | 0.03847 | -0.061684 | 0.004561 | 0.019455 | -0.019015 | -0.29878 | -0.24377 | -0.11153 | -0.22936 | 0.03681 | -0.061797 | 0.049734 | -0.088152 | -0.084951 | 121.9781 | 121.741 | 121.796 | 62.2985 | -122.0013 | 121.8104 | 121.9516 | 121.9548 | 62.3844 | -122.1513
752.2969 | 122.2549 | -62.2696 | 59.8114 | 1.4211e-13 | -0.032297 | -0.0049424 | 0.065152 | -0.006427 | 0.05624 | -0.0054937 | 0.00014315 | -0.0025424 | -0.003867 | 0.02291 | -0.010881 | -62.2971 | 0.015142 | -62.2639 | 59.6902 | 59.4531 | 59.499 | -62.2586 | -62.2602 | 0.087354 | -62.3589 | 59.5134 | 59.6592 | 59.6578 | -62.3949 | 0.011003 | -0.12119 | -0.027484 | 0.005724 | -0.005279 | -0.35829 | -0.31243 | -0.12526 | -0.29802 | 0.009343 | -0.089264 | 0.035997 | -0.15224 | -0.15362 | 121.9598 | 121.7227 | 121.7686 | 62.2847 | -122.07 | 121.783 | 121.9288 | 121.9274 | 62.3569 | -122.2063
753.9688 | 122.3145 | -62.2925 | 59.7839 | 1.4211e-13 | -0.03251 | -0.005156 | 0.065579 | -0.0062134 | 0.056454 | -0.0054937 | 0.00057035 | -0.0023288 | -0.0036534 | 0.023124 | -0.011309 | -62.2925 | 0.005985 | -62.273 | 59.6948 | 59.4531 | 59.499 | -62.2586 | -62.2602 | 0.087354 | -62.3543 | 59.5225 | 59.6546 | 59.6669 | -62.404 | 0.033891 | -0.08915 | -1.8e-05 | 0.019455 | -0.014436 | -0.33082 | -0.28497 | -0.11153 | -0.2614 | 0.032231 | -0.061797 | 0.049734 | -0.12935 | -0.11699 | 121.9873 | 121.7456 | 121.7914 | 62.2985 | -122.0425 | 121.815 | 121.9471 | 121.9594 | 62.3798 | -122.1879
755.7188 | 122.3511 | -62.2513 | 59.761 | 1.4211e-13 | -0.032724 | -0.0049424 | 0.065152 | -0.0059996 | 0.056454 | -0.013124 | 0.00057035 | -0.0019016 | -0.0034396 | 0.023337 | -0.011309 | -62.2879 | 0.019721 | -62.2684 | 59.6948 | 59.444 | 59.5035 | -62.254 | -62.2648 | 0.087354 | -62.3543 | 59.5088 | 59.65 | 59.6624 | -62.404 | -0.002728 | -0.066261 | -0.036637 | -0.017164 | -0.014436 | -0.31709 | -0.2575 | -0.15273 | -0.25225 | -0.013546 | -0.10299 | 0.049734 | -0.11104 | -0.098684 | 121.9461 | 121.6952 | 121.7548 | 62.271 | -122.0151 | 121.7601 | 121.9013 | 121.9136 | 62.3386 | -122.1651
757.4688 | 122.2092 | -62.2833 | 59.8389 | 1.4211e-13 | -0.03251 | -0.005156 | 0.065152 | -0.0062134 | 0.056454 | -0.0054937 | 0.00035675 | -0.0023288 | -0.0036534 | 0.02291 | -0.011309 | -62.2925 | 0.010564 | -62.2684 | 59.6994 | 59.444 | 59.5035 | -62.2586 | -62.2602 | 0.082776 | -62.3634 | 59.5134 | 59.6546 | 59.6669 | -62.3994 | 0.024736 | -0.1395 | -0.009173 | 0.014879 | -0.009857 | -0.39491 | -0.33532 | -0.11611 | -0.32549 | 0.023076 | -0.08011 | 0.035997 | -0.18428 | -0.17193 | 121.9827 | 121.7273 | 121.7869 | 62.2939 | -122.0975 | 121.7967 | 121.9379 | 121.9503 | 62.3661 | -122.2383
759.2188 | 122.3465 | -62.2375 | 59.7565 | 1.4211e-13 | -0.032297 | -0.005156 | 0.065579 | -0.0062134 | 0.056668 | -0.013124 | 0.00014315 | -0.0021152 | -0.0034396 | 0.022696 | -0.011095 | -62.2879 | 0.015142 | -62.2639 | 59.6902 | 59.4577 | 59.5081 | -62.2586 | -62.2602 | 0.087354 | -62.3543 | 59.5088 | 59.6546 | 59.6624 | -62.3994 | -0.02104 | -0.066262 | -0.05037 | -0.026319 | -0.005279 | -0.29878 | -0.24834 | -0.16188 | -0.24767 | -0.0227 | -0.11673 | 0.045155 | -0.10189 | -0.094107 | 121.9278 | 121.6952 | 121.7457 | 62.2527 | -122.0151 | 121.7463 | 121.8921 | 121.8999 | 62.3249 | -122.1559
760.9688 | 122.3511 | -62.265 | 59.7794 | 1.4211e-13 | -0.03251 | -0.005156 | 0.065366 | -0.0066406 | 0.056454 | 0.0021363 | 0.00035675 | -0.0023288 | -0.0034396 | 0.023124 | -0.011522 | -62.2879 | 0.010564 | -62.273 | 59.6994 | 59.4531 | 59.499 | -62.2494 | -62.2602 | 0.082776 | -62.3589 | 59.518 | 59.6592 | 59.6578 | -62.4086 | 0.015584 | -0.079993 | -0.022904 | -0.00801 | -0.023594 | -0.32624 | -0.28039 | -0.14357 | -0.2614 | 0.004766 | -0.093841 | 0.049734 | -0.1202 | -0.12157 | 121.9644 | 121.7181 | 121.764 | 62.2756 | -122.0288 | 121.783 | 121.9242 | 121.9228 | 62.3478 | -122.1879
762.6562 | 122.2183 | -62.3154 | 59.816 | 1.4211e-13 | -0.032724 | -0.0053696 | 0.064938 | -0.0062134 | 0.056027 | 0.0021363 | 0.00057035 | -0.0021152 | -0.0040806 | 0.023124 | -0.011095 | -62.3017 | 0.001407 | -62.2639 | 59.6856 | 59.4485 | 59.499 | -62.2586 | -62.2602 | 0.091933 | -62.3543 | 59.518 | 59.6592 | 59.6624 | -62.4086 | 0.05678 | -0.13035 | 0.013715 | 0.051501 | -0.005279 | -0.36744 | -0.31701 | -0.093221 | -0.29802 | 0.05512 | -0.038908 | 0.054313 | -0.15682 | -0.15362 | 122.001 | 121.7639 | 121.8143 | 62.3168 | -122.0746 | 121.8333 | 121.9745 | 121.9777 | 62.4073 | -122.2246
764.3906 | 122.2229 | -62.3062 | 59.8297 | 1.4211e-13 | -0.03251 | -0.005156 | 0.065366 | -0.0066406 | 0.05624 | 0.0021363 | 0.00057035 | -0.0023288 | -0.0034396 | 0.022696 | -0.011309 | -62.2879 | 0.001407 | -62.273 | 59.6902 | 59.444 | 59.5035 | -62.254 | -62.2557 | 0.082776 | -62.3589 | 59.5134 | 59.6546 | 59.6349 | -62.4086 | 0.052203 | -0.1395 | 0.018294 | 0.033188 | -0.019015 | -0.38576 | -0.32616 | -0.10238 | -0.31634 | 0.050543 | -0.052643 | 0.049734 | -0.17513 | -0.19482 | 121.9964 | 121.7502 | 121.8098 | 62.3076 | -122.0837 | 121.8196 | 121.9608 | 121.9411 | 62.389 | -122.2383
766.1406 | 122.3053 | -62.3016 | 59.7748 | 1.4211e-13 | -0.03251 | -0.0049424 | 0.065366 | -0.0062134 | 0.056668 | 0.0021363 | 0.00035675 | -0.0023288 | -0.0040806 | 0.022696 | -0.010881 | -62.2971 | 0.015142 | -62.2684 | 59.6902 | 59.4531 | 59.5035 | -62.2586 | -62.2602 | 0.087354 | -62.3543 | 59.518 | 59.6546 | 59.6761 | -62.3994 | 0.043047 | -0.084572 | 0.00456 | 0.03319 | -0.009857 | -0.32167 | -0.27123 | -0.097796 | -0.25683 | 0.041387 | -0.052641 | 0.045155 | -0.1202 | -0.098681 | 121.9918 | 121.7548 | 121.8052 | 62.3168 | -122.0334 | 121.8196 | 121.9562 | 121.9777 | 62.389 | -122.1742
767.8125 | 122.2321 | -62.2925 | 59.7839 | 1.4211e-13 | -0.032724 | -0.005156 | 0.065366 | -0.0062134 | 0.05624 | -0.013124 | 0.00035675 | -0.0021152 | -0.0036534 | 0.023124 | -0.011095 | -62.2925 | 0.001407 | -62.273 | 59.6856 | 59.444 | 59.5035 | -62.254 | -62.2648 | 0.082776 | -62.3589 | 59.518 | 59.6546 | 59.6669 | -62.3994 | 0.03847 | -0.098306 | -1.8e-05 | 0.019455 | -0.019015 | -0.33998 | -0.28039 | -0.10695 | -0.26598 | 0.027652 | -0.066376 | 0.040576 | -0.12935 | -0.11699 | 121.9781 | 121.7364 | 121.796 | 62.2939 | -122.0379 | 121.8104 | 121.9471 | 121.9594 | 62.3753 | -122.1834
769.5625 | 122.3145 | -62.2879 | 59.7519 | 1.4211e-13 | -0.032938 | -0.0053696 | 0.065366 | -0.006427 | 0.056454 | -0.0054937 | 0.00035675 | -0.0023288 | -0.0034396 | 0.02291 | -0.011309 | -62.2879 | 0.010564 | -62.2684 | 59.6948 | 59.4531 | 59.5081 | -62.2586 | -62.2602 | 0.082776 | -62.3589 | 59.518 | 59.65 | 59.6715 | -62.404 | 0.029314 | -0.057106 | -1.6e-05 | 0.019457 | -0.009857 | -0.29878 | -0.24377 | -0.11611 | -0.23394 | 0.027654 | -0.070953 | 0.045155 | -0.10189 | -0.080372 | 121.9827 | 121.741 | 121.796 | 62.2985 | -122.0105 | 121.8059 | 121.9379 | 121.9594 | 62.3707 | -122.1559
771.2656 | 122.3053 | -62.2787 | 59.7198 | 1.4211e-13 | -0.032938 | -0.0053696 | 0.065366 | -0.006427 | 0.05624 | -0.0054937 | 0.00035675 | -0.0021152 | -0.0036534 | 0.023124 | -0.011309 | -62.2925 | 0.010564 | -62.2684 | 59.6902 | 59.4577 | 59.5127 | -62.2494 | -62.2648 | 0.082776 | -62.3634 | 59.5134 | 59.6683 | 59.6715 | -62.3994 | 0.029317 | -0.029641 | -0.01375 | 0.010302 | -0.019015 | -0.26216 | -0.20714 | -0.12068 | -0.20647 | 0.01392 | -0.084687 | 0.035997 | -0.05153 | -0.048329 | 121.969 | 121.7364 | 121.7915 | 62.2893 | -121.9693 | 121.7921 | 121.9471 | 121.9503 | 62.3615 | -122.1193
773 | 122.3511 | -62.2925 | 59.7427 | 1.4211e-13 | -0.032297 | -0.0053696 | 0.065152 | -0.006427 | 0.056454 | -0.0054937 | 0.00035675 | -0.0023288 | -0.0036534 | 0.022696 | -0.011095 | -62.2879 | 0.005985 | -62.2639 | 59.6994 | 59.4577 | 59.5081 | -62.2632 | -62.2648 | 0.091933 | -62.3543 | 59.5134 | 59.6683 | 59.6624 | -62.404 | 0.029312 | -0.043372 | 0.004561 | 0.028612 | -0.0007 | -0.28504 | -0.23461 | -0.11153 | -0.22936 | 0.027652 | -0.061797 | 0.049734 | -0.074418 | -0.080374 | 121.9918 | 121.7502 | 121.8006 | 62.2985 | -122.0059 | 121.8059 | 121.9608 | 121.9548 | 62.3844 | -122.1467
774.75 | 122.3145 | -62.2971 | 59.7702 | 1.4211e-13 | -0.032724 | -0.0049424 | 0.065366 | -0.006427 | 0.05624 | 0.0021363 | 0.00035675 | -0.0023288 | -0.003867 | 0.023124 | -0.011095 | -62.2833 | 0.010564 | -62.2684 | 59.6948 | 59.444 | 59.5081 | -62.2632 | -62.2694 | 0.087354 | -62.3543 | 59.5134 | 59.6637 | 59.6624 | -62.404 | 0.03389 | -0.075417 | 0.013717 | 0.028612 | -0.005278 | -0.32625 | -0.26208 | -0.10695 | -0.25683 | 0.027652 | -0.057219 | 0.049734 | -0.10646 | -0.10784 | 121.9918 | 121.741 | 121.8052 | 62.3076 | -122.0334 | 121.8104 | 121.9608 | 121.9594 | 62.3844 | -122.1742
776.4375 | 122.2366 | -62.3062 | 59.7839 | 1.4211e-13 | -0.032724 | -0.005156 | 0.065366 | -0.0062134 | 0.05624 | -0.0054937 | 0.00035675 | -0.0019016 | -0.0036534 | 0.023124 | -0.011095 | -62.2879 | 0.005985 | -62.2684 | 59.6948 | 59.4531 | 59.5127 | -62.2586 | -62.2602 | 0.082776 | -62.3589 | 59.5088 | 59.6546 | 59.6624 | -62.404 | 0.047624 | -0.08915 | 0.018294 | 0.037767 | -0.009857 | -0.33082 | -0.27123 | -0.097798 | -0.27514 | 0.045964 | -0.052643 | 0.045155 | -0.12935 | -0.12157 | 122.001 | 121.7593 | 121.8189 | 62.3122 | -122.0425 | 121.815 | 121.9608 | 121.9686 | 62.389 | -122.1879
778.1875 | 122.374 | -62.265 | 59.7748 | 1.4211e-13 | -0.03251 | -0.0055834 | 0.065579 | -0.0062134 | 0.05624 | -0.0054937 | 0.00035675 | -0.0021152 | -0.0036534 | 0.02291 | -0.011522 | -62.2925 | 0.015142 | -62.273 | 59.6948 | 59.4577 | 59.5035 | -62.254 | -62.2694 | 0.087354 | -62.3589 | 59.5134 | 59.6546 | 59.6624 | -62.404 | 0.011005 | -0.079994 | -0.027483 | -0.00801 | -0.019015 | -0.31709 | -0.27123 | -0.139 | -0.2614 | -0.004391 | -0.093841 | 0.045155 | -0.1202 | -0.11242 | 121.9598 | 121.7227 | 121.7686 | 62.2802 | -122.0288 | 121.7784 | 121.9196 | 121.9274 | 62.3524 | -122.1788
779.875 | 122.2961 | -62.2604 | 59.7656 | 1.4211e-13 | -0.03251 | -0.0049424 | 0.065152 | -0.0066406 | 0.05624 | -0.013124 | 0.00035675 | -0.0019016 | -0.0040806 | 0.02291 | -0.011095 | -62.2925 | 0.010564 | -62.2684 | 59.6902 | 59.4531 | 59.5081 | -62.2586 | -62.2602 | 0.087354 | -62.3589 | 59.518 | 59.6592 | 59.6669 | -62.3994 | 0.001848 | -0.075417 | -0.032061 | -0.008009 | -0.009857 | -0.31251 | -0.2575 | -0.13899 | -0.24767 | 0.000188 | -0.098419 | 0.040576 | -0.10646 | -0.098684 | 121.9506 | 121.7136 | 121.7686 | 62.271 | -122.0242 | 121.7784 | 121.9196 | 121.9274 | 62.3478 | -122.1651
781.6094 | 122.3511 | -62.2787 | 59.7382 | 1.4211e-13 | -0.032724 | -0.005156 | 0.065366 | -0.0062134 | 0.056454 | -0.020755 | 0.00014315 | -0.0021152 | -0.003867 | 0.023124 | -0.011309 | -62.2925 | 0.010564 | -62.273 | 59.6902 | 59.4577 | 59.5035 | -62.2632 | -62.2602 | 0.087354 | -62.3589 | 59.518 | 59.6546 | 59.6578 | -62.3994 | 0.01558 | -0.047951 | -0.01375 | 0.005723 | -0.009857 | -0.28047 | -0.23461 | -0.12068 | -0.2202 | 0.018499 | -0.080108 | 0.040576 | -0.083576 | -0.080375 | 121.969 | 121.7364 | 121.7823 | 62.2893 | -122.0013 | 121.7967 | 121.9333 | 121.9365 | 62.3661 | -122.1376
783.3594 | 122.3373 | -62.2833 | 59.7519 | 1.4211e-13 | -0.032724 | -0.0049424 | 0.065366 | -0.006427 | 0.05624 | 0.0021363 | 0.00035675 | -0.0019016 | -0.0036534 | 0.02291 | -0.011522 | -62.2879 | 0.010564 | -62.2639 | 59.6902 | 59.4531 | 59.5127 | -62.254 | -62.2557 | 0.087354 | -62.3589 | 59.5134 | 59.6546 | 59.6669 | -62.404 | 0.029315 | -0.061684 | -0.004594 | 0.019457 | -0.009858 | -0.29878 | -0.23919 | -0.12069 | -0.23852 | 0.027655 | -0.075531 | 0.045155 | -0.097309 | -0.084951 | 121.9735 | 121.7364 | 121.796 | 62.2939 | -122.0059 | 121.7967 | 121.9379 | 121.9503 | 62.3707 | -122.1559
785.125 | 122.2687 | -62.3108 | 59.8022 | 1.4211e-13 | -0.032724 | -0.005156 | 0.065366 | -0.006427 | 0.05624 | -0.0054937 | 0.00014315 | -0.0016878 | -0.0036534 | 0.023337 | -0.011095 | -62.2925 | 0.010564 | -62.2684 | 59.6948 | 59.4531 | 59.5127 | -62.2586 | -62.2602 | 0.087354 | -62.3589 | 59.518 | 59.6637 | 59.6624 | -62.4086 | 0.052202 | -0.10746 | 0.018293 | 0.042345 | -0.009857 | -0.34913 | -0.28954 | -0.097799 | -0.28429 | 0.050542 | -0.048065 | 0.049734 | -0.13851 | -0.13988 | 122.0056 | 121.7639 | 121.8235 | 62.3214 | -122.0608 | 121.8287 | 121.9745 | 121.9732 | 62.3981 | -122.2108
786.875 | 122.2321 | -62.2833 | 59.7931 | 1.4211e-13 | -0.033151 | -0.005156 | 0.065366 | -0.0062134 | 0.05624 | 0.0021363 | 0.00035675 | -0.0021152 | -0.0036534 | 0.023337 | -0.010881 | -62.3017 | 0.010564 | -62.2684 | 59.6994 | 59.4485 | 59.5127 | -62.2586 | -62.2557 | 0.091933 | -62.3589 | 59.5134 | 59.6546 | 59.6624 | -62.3994 | 0.024736 | -0.093726 | -0.018329 | 0.014879 | -0.009857 | -0.34455 | -0.28039 | -0.11611 | -0.27971 | 0.027655 | -0.075531 | 0.040576 | -0.13851 | -0.13073 | 121.9827 | 121.7319 | 121.796 | 62.2939 | -122.0517 | 121.7967 | 121.9379 | 121.9457 | 62.3753 | -122.1925
788.5625 | 122.3099 | -62.2742 | 59.7656 | 1.4211e-13 | -0.032938 | -0.005156 | 0.065793 | -0.0066406 | 0.056454 | -0.013124 | 0.00035675 | -0.0019016 | -0.003867 | 0.023337 | -0.011095 | -62.2925 | 0.010564 | -62.273 | 59.7039 | 59.4623 | 59.5081 | -62.254 | -62.2648 | 0.087354 | -62.3634 | 59.5225 | 59.6592 | 59.6669 | -62.404 | 0.02016 | -0.061682 | -0.018328 | 0.001145 | -0.019015 | -0.30335 | -0.2575 | -0.12984 | -0.24309 | 0.009342 | -0.089265 | 0.040576 | -0.10646 | -0.098684 | 121.9781 | 121.7364 | 121.7823 | 62.2847 | -122.0196 | 121.7967 | 121.9333 | 121.9411 | 62.3615 | -122.1696
790.3281 | 122.3053 | -62.2787 | 59.7885 | 1.4211e-13 | -0.03251 | -0.0053696 | 0.065579 | -0.0062134 | 0.05624 | -0.013124 | 0.00014315 | -0.0021152 | -0.0036534 | 0.023124 | -0.011095 | -62.2879 | 0.010564 | -62.273 | 59.6994 | 59.4531 | 59.5127 | -62.254 | -62.2602 | 0.082776 | -62.3497 | 59.5134 | 59.6592 | 59.6578 | -62.404 | 0.024738 | -0.089148 | -0.009171 | 0.005723 | -0.019015 | -0.3354 | -0.27581 | -0.12526 | -0.27514 | 0.018499 | -0.070951 | 0.054312 | -0.12935 | -0.13073 | 121.9781 | 121.7319 | 121.7915 | 62.2893 | -122.0425 | 121.7921 | 121.9379 | 121.9365 | 62.3615 | -122.1925
792.0156 | 122.3099 | -62.2787 | 59.7656 | 1.4211e-13 | -0.032938 | -0.005156 | 0.065793 | -0.0062134 | 0.056027 | -0.0054937 | 0.00014315 | -0.0023288 | -0.0036534 | 0.023337 | -0.011309 | -62.2879 | 0.010564 | -62.2639 | 59.6948 | 59.4577 | 59.5173 | -62.2677 | -62.2648 | 0.087354 | -62.3589 | 59.5134 | 59.6592 | 59.6669 | -62.3994 | 0.011001 | -0.070839 | -0.009171 | 0.01488 | 0.003879 | -0.30793 | -0.24834 | -0.12068 | -0.25225 | 0.01392 | -0.080108 | 0.040576 | -0.10646 | -0.098684 | 121.9735 | 121.7364 | 121.796 | 62.2893 | -122.0334 | 121.7921 | 121.9379 | 121.9457 | 62.3661 | -122.1651
793.7656 | 122.2504 | -62.2742 | 59.7931 | 1.4211e-13 | -0.032938 | -0.0053696 | 0.065152 | -0.0059996 | 0.056027 | 0.0097668 | 0.00035675 | -0.0021152 | -0.0034396 | 0.023337 | -0.011095 | -62.2833 | 0.005985 | -62.2684 | 59.6811 | 59.4577 | 59.5081 | -62.254 | -62.2602 | 0.087354 | -62.3589 | 59.5134 | 59.6592 | 59.6669 | -62.3994 | 0.02016 | -0.11204 | -0.009171 | 0.005724 | -0.014436 | -0.3354 | -0.28496 | -0.12526 | -0.27971 | 0.013921 | -0.084686 | 0.040576 | -0.13393 | -0.12615 | 121.9552 | 121.7319 | 121.7823 | 62.2802 | -122.0471 | 121.7875 | 121.9333 | 121.9411 | 62.3615 | -122.1925
795.5156 | 122.2366 | -62.3062 | 59.8434 | 1.4211e-13 | -0.032938 | -0.005156 | 0.065152 | -0.006427 | 0.055813 | 0.0021363 | 0.00014315 | -0.0021152 | -0.0034396 | 0.023124 | -0.011095 | -62.2879 | 0.010564 | -62.2684 | 59.6948 | 59.4577 | 59.5127 | -62.2586 | -62.2648 | 0.087354 | -62.3589 | 59.5225 | 59.6637 | 59.6624 | -62.404 | 0.047624 | -0.14866 | 0.018294 | 0.037767 | -0.009857 | -0.38575 | -0.33074 | -0.097798 | -0.32091 | 0.041385 | -0.052643 | 0.045155 | -0.17971 | -0.18108 | 122.001 | 121.7639 | 121.8189 | 62.3168 | -122.102 | 121.8287 | 121.97 | 121.9686 | 62.3936 | -122.2475
797.2031 | 122.3099 | -62.2787 | 59.7702 | 1.4211e-13 | -0.033151 | -0.005156 | 0.065579 | -0.006427 | 0.055813 | -0.0054937 | 0.00014315 | -0.0021152 | -0.0036534 | 0.023124 | -0.011522 | -62.2833 | 0.005985 | -62.2639 | 59.6994 | 59.4623 | 59.5127 | -62.2586 | -62.2557 | 0.087354 | -62.3634 | 59.518 | 59.6637 | 59.6624 | -62.3994 | 0.020159 | -0.070838 | -0.004593 | 0.01488 | -0.005279 | -0.30793 | -0.2575 | -0.12068 | -0.25225 | 0.023078 | -0.084687 | 0.035997 | -0.10646 | -0.10784 | 121.9781 | 121.741 | 121.7915 | 62.2847 | -122.0288 | 121.7967 | 121.9425 | 121.9411 | 62.3661 | -122.1696
798.9531 | 122.3557 | -62.2513 | 59.7931 | 1.4211e-13 | -0.032938 | -0.005156 | 0.065366 | -0.0062134 | 0.056454 | 0.0021363 | 0.00057035 | -0.0019016 | -0.0034396 | 0.023765 | -0.011309 | -62.2879 | 0.005985 | -62.2639 | 59.6994 | 59.4623 | 59.5127 | -62.254 | -62.2648 | 0.091933 | -62.3543 | 59.518 | 59.6592 | 59.6669 | -62.4086 | -0.002728 | -0.093726 | -0.036637 | -0.012586 | -0.009858 | -0.33082 | -0.28039 | -0.15731 | -0.27514 | -0.013546 | -0.10299 | 0.054313 | -0.13393 | -0.12615 | 121.9506 | 121.7136 | 121.764 | 62.2573 | -122.0471 | 121.7692 | 121.9104 | 121.9182 | 62.3432 | -122.2017
800.6406 | 122.3099 | -62.3016 | 59.7382 | 1.4211e-13 | -0.033151 | -0.005156 | 0.065579 | -0.006427 | 0.05624 | 0.0021363 | 0.00035675 | -0.0021152 | -0.003867 | 0.023551 | -0.011522 | -62.2879 | 0.010564 | -62.273 | 59.7039 | 59.4531 | 59.5081 | -62.2632 | -62.2602 | 0.091933 | -62.3634 | 59.5225 | 59.6546 | 59.6761 | -62.4086 | 0.038468 | -0.034216 | 0.013717 | 0.028611 | -0.009857 | -0.28504 | -0.23003 | -0.10695 | -0.21563 | 0.041387 | -0.061799 | 0.045155 | -0.083576 | -0.06206 | 122.0056 | 121.7548 | 121.8098 | 62.3122 | -122.0013 | 121.8242 | 121.9562 | 121.9777 | 62.3936 | -122.1467
802.3281 | 122.2824 | -62.2742 | 59.8206 | 1.4211e-13 | -0.033151 | -0.0049424 | 0.065366 | -0.0062134 | 0.05624 | -0.013124 | 0.00035675 | -0.0021152 | -0.0036534 | 0.023551 | -0.011736 | -62.2879 | 0.010564 | -62.2776 | 59.6948 | 59.4577 | 59.5173 | -62.2586 | -62.2694 | 0.087354 | -62.3543 | 59.518 | 59.6637 | 59.6715 | -62.404 | 0.015581 | -0.12577 | -0.013749 | -0.003433 | -0.019014 | -0.36286 | -0.30327 | -0.12984 | -0.3026 | 0.004764 | -0.080107 | 0.049734 | -0.15682 | -0.14904 | 121.969 | 121.7319 | 121.7915 | 62.2847 | -122.0791 | 121.7921 | 121.9379 | 121.9457 | 62.3615 | -122.2246
804.0781 | 122.2366 | -62.2833 | 59.8389 | 1.4211e-13 | -0.032938 | -0.005156 | 0.065366 | -0.006427 | 0.056027 | -0.0054937 | 0.00035675 | -0.0021152 | -0.003867 | 0.023337 | -0.011309 | -62.2879 | 0.010564 | -62.2639 | 59.6994 | 59.4577 | 59.5081 | -62.2632 | -62.2648 | 0.087354 | -62.3497 | 59.5225 | 59.6592 | 59.6669 | -62.404 | 0.020157 | -0.1395 | -0.004594 | 0.019457 | -0.0007 | -0.38117 | -0.33074 | -0.12069 | -0.31633 | 0.018497 | -0.066374 | 0.054312 | -0.1797 | -0.17193 | 121.9827 | 121.741 | 121.7915 | 62.2939 | -122.102 | 121.8059 | 121.9425 | 121.9503 | 62.3707 | -122.2429
805.8438 | 122.2275 | -62.2971 | 59.8389 | 1.4211e-13 | -0.033151 | -0.0053696 | 0.065793 | -0.006427 | 0.056454 | -0.0054937 | 0.00035675 | -0.0021152 | -0.0034396 | 0.023124 | -0.011095 | -62.2879 | 0.005985 | -62.273 | 59.6948 | 59.4531 | 59.5173 | -62.2677 | -62.2602 | 0.087354 | -62.3543 | 59.5225 | 59.6683 | 59.6715 | -62.404 | 0.029311 | -0.14408 | 0.009139 | 0.024033 | -0.005278 | -0.38575 | -0.32158 | -0.10695 | -0.31633 | 0.036809 | -0.057219 | 0.049734 | -0.17055 | -0.16735 | 121.9918 | 121.7502 | 121.8143 | 62.303 | -122.1066 | 121.8196 | 121.9654 | 121.9686 | 62.3844 | -122.2429
807.5938 | 122.287 | -62.2833 | 59.8206 | 1.4211e-13 | -0.033365 | -0.0053696 | 0.065366 | -0.0062134 | 0.05624 | -0.0054937 | 0.00014315 | -0.0021152 | -0.003867 | 0.023551 | -0.011309 | -62.2925 | 0.010564 | -62.2684 | 59.6948 | 59.476 | 59.5127 | -62.2586 | -62.2602 | 0.091933 | -62.3543 | 59.518 | 59.6729 | 59.6761 | -62.404 | 0.024736 | -0.12577 | -0.009173 | 0.014879 | -0.009857 | -0.34455 | -0.30785 | -0.12069 | -0.3026 | 0.023076 | -0.070952 | 0.049734 | -0.14766 | -0.14446 | 121.9781 | 121.7593 | 121.796 | 62.2939 | -122.0791 | 121.8013 | 121.9562 | 121.9594 | 62.3753 | -122.2246
809.2812 | 122.3557 | -62.2559 | 59.7656 | 1.4211e-13 | -0.033579 | -0.0053696 | 0.065366 | -0.006427 | 0.056454 | -0.013124 | 0.00035675 | -0.0023288 | -0.003226 | 0.023124 | -0.011309 | -62.2879 | 0.019721 | -62.2639 | 59.6994 | 59.4577 | 59.5127 | -62.2632 | -62.2557 | 0.087354 | -62.3589 | 59.5271 | 59.6775 | 59.6303 | -62.4086 | -0.007309 | -0.06626 | -0.03206 | -0.008009 | -0.0007 | -0.30793 | -0.25292 | -0.15273 | -0.23851 | 0.000189 | -0.103 | 0.049734 | -0.088149 | -0.13531 | 121.9552 | 121.7136 | 121.7686 | 62.2756 | -122.0288 | 121.783 | 121.9333 | 121.8862 | 62.3432 | -122.1742
811.0156 | 122.3419 | -62.2696 | 59.8022 | 1.4211e-13 | -0.033151 | -0.0053696 | 0.066007 | -0.0066406 | 0.056454 | 0.0021363 | 0.00014315 | -0.0023288 | -0.0036534 | 0.023337 | -0.011095 | -62.2879 | 0.015142 | -62.2684 | 59.6994 | 59.4531 | 59.5173 | -62.2586 | -62.2602 | 0.091933 | -62.3589 | 59.5225 | 59.6729 | 59.6715 | -62.404 | 0.011003 | -0.10288 | -0.018327 | 0.001146 | -0.009857 | -0.34913 | -0.28496 | -0.13442 | -0.27971 | 0.009343 | -0.089264 | 0.045155 | -0.12935 | -0.13073 | 121.969 | 121.7227 | 121.7869 | 62.2847 | -122.0608 | 121.7921 | 121.9425 | 121.9411 | 62.3615 | -122.2063
812.75 | 122.3007 | -62.2696 | 59.7748 | 1.4211e-13 | -0.033579 | -0.0053696 | 0.065366 | -0.0062134 | 0.056454 | -0.0054937 | 0.00035675 | -0.0021152 | -0.0036534 | 0.023337 | -0.011095 | -62.2833 | 0.005985 | -62.273 | 59.6994 | 59.476 | 59.5173 | -62.254 | -62.2648 | 0.087354 | -62.3543 | 59.5225 | 59.6729 | 59.6761 | -62.404 | 0.015582 | -0.075415 | -0.013749 | -0.003433 | -0.019015 | -0.29877 | -0.2575 | -0.13442 | -0.25225 | 0.004764 | -0.084685 | 0.049734 | -0.10188 | -0.098681 | 121.969 | 121.7456 | 121.7869 | 62.2756 | -122.0288 | 121.7921 | 121.9425 | 121.9457 | 62.3569 | -122.1788
814.4844 | 122.2046 | -62.2971 | 59.816 | 1.4211e-13 | -0.033365 | -0.0053696 | 0.064938 | -0.006427 | 0.05624 | -0.013124 | 0.00035675 | -0.0016878 | -0.0036534 | 0.023551 | -0.011522 | -62.2879 | 0.015142 | -62.2684 | 59.6948 | 59.4714 | 59.5173 | -62.2586 | -62.2557 | 0.087354 | -62.3543 | 59.518 | 59.6683 | 59.6669 | -62.3994 | 0.038469 | -0.12119 | 0.009139 | 0.028612 | -0.009857 | -0.34455 | -0.2987 | -0.10237 | -0.29802 | 0.041388 | -0.057219 | 0.045155 | -0.14766 | -0.14904 | 121.9918 | 121.7685 | 121.8143 | 62.3122 | -122.0746 | 121.815 | 121.9654 | 121.964 | 62.3844 | -122.2154
816.1719 | 122.2366 | -62.2833 | 59.8434 | 1.4211e-13 | -0.033365 | -0.0055834 | 0.065366 | -0.0059996 | 0.056454 | -0.0054937 | 0.00014315 | -0.0019016 | -0.0034396 | 0.02291 | -0.010881 | -62.2925 | 0.005985 | -62.2684 | 59.6994 | 59.4623 | 59.5173 | -62.254 | -62.2557 | 0.091933 | -62.3497 | 59.5225 | 59.6729 | 59.6715 | -62.404 | 0.029315 | -0.14408 | -0.009173 | 0.014879 | -0.014436 | -0.38117 | -0.32616 | -0.12069 | -0.32091 | 0.027655 | -0.066374 | 0.054312 | -0.17055 | -0.17193 | 121.9827 | 121.7456 | 121.8006 | 62.2893 | -122.0975 | 121.8059 | 121.9562 | 121.9548 | 62.3753 | -122.2475
817.9219 | 122.3648 | -62.2421 | 59.7839 | 1.4211e-13 | -0.033151 | -0.005156 | 0.065152 | -0.0066406 | 0.056027 | -0.0054937 | 0.00014315 | -0.0021152 | -0.0036534 | 0.023765 | -0.011309 | -62.2879 | 0.019721 | -62.2639 | 59.6994 | 59.4852 | 59.5127 | -62.2586 | -62.2648 | 0.091933 | -62.3543 | 59.5271 | 59.6637 | 59.6669 | -62.3994 | -0.016463 | -0.084571 | -0.045793 | -0.021742 | -0.005279 | -0.29877 | -0.27123 | -0.15731 | -0.25682 | -0.022702 | -0.11215 | 0.045155 | -0.1202 | -0.11699 | 121.9415 | 121.7273 | 121.7548 | 62.2618 | -122.0425 | 121.7692 | 121.9059 | 121.9091 | 62.3341 | -122.1834
819.6719 | 122.2733 | -62.265 | 59.8206 | 1.4211e-13 | -0.033365 | -0.005156 | 0.064938 | -0.006427 | 0.056027 | -0.0054937 | 0.00035675 | -0.0023288 | -0.0034396 | 0.023337 | -0.011309 | -62.2879 | 0.010564 | -62.2684 | 59.6948 | 59.476 | 59.5127 | -62.2586 | -62.2511 | 0.091933 | -62.3497 | 59.5225 | 59.6683 | 59.6715 | -62.404 | 0.006426 | -0.12577 | -0.022904 | -0.003431 | -0.009857 | -0.34455 | -0.30785 | -0.139 | -0.29802 | 0.013923 | -0.084684 | 0.054312 | -0.15224 | -0.14904 | 121.9598 | 121.741 | 121.7777 | 62.2756 | -122.0791 | 121.7875 | 121.9333 | 121.9365 | 62.3569 | -122.2246
821.3594 | 122.3694 | -62.2467 | 59.7885 | 1.4211e-13 | -0.033365 | -0.005156 | 0.065366 | -0.0066406 | 0.055813 | 0.0021363 | 0.00035675 | -0.0019016 | -0.003867 | 0.023551 | -0.011522 | -62.2833 | 0.019721 | -62.2684 | 59.7039 | 59.4943 | 59.5127 | -62.2494 | -62.2557 | 0.091933 | -62.3589 | 59.5225 | 59.6683 | 59.6761 | -62.404 | -0.002727 | -0.08457 | -0.036637 | -0.021742 | -0.019015 | -0.29419 | -0.27581 | -0.15731 | -0.26598 | -0.008966 | -0.11215 | 0.045155 | -0.12019 | -0.11241 | 121.9506 | 121.741 | 121.7594 | 62.2664 | -122.0379 | 121.7692 | 121.915 | 121.9228 | 62.3386 | -122.1925
823.1094 | 122.3145 | -62.2696 | 59.8206 | 1.4211e-13 | -0.033365 | -0.005156 | 0.065366 | -0.006427 | 0.05624 | -0.0054937 | 0.00035675 | -0.0023288 | -0.003867 | 0.023337 | -0.011522 | -62.2879 | 0.005985 | -62.2639 | 59.6948 | 59.4669 | 59.5127 | -62.2586 | -62.2602 | 0.087354 | -62.3543 | 59.5271 | 59.6775 | 59.6669 | -62.4132 | 0.011003 | -0.12577 | -0.018327 | 0.005724 | -0.005279 | -0.3537 | -0.30785 | -0.14358 | -0.29345 | 0.009343 | -0.084685 | 0.058892 | -0.14308 | -0.15362 | 121.9644 | 121.7364 | 121.7823 | 62.2756 | -122.0791 | 121.7967 | 121.9471 | 121.9365 | 62.3569 | -122.2337
824.8594 | 122.3648 | -62.2787 | 59.7702 | 1.4211e-13 | -0.033365 | -0.0053696 | 0.065579 | -0.0062134 | 0.056027 | -0.013124 | 0.00035675 | -0.0021152 | -0.0036534 | 0.023551 | -0.011095 | -62.2833 | 0.005985 | -62.2684 | 59.7039 | 59.4623 | 59.5173 | -62.254 | -62.2511 | 0.091933 | -62.3543 | 59.5225 | 59.6637 | 59.6761 | -62.3994 | 0.024738 | -0.06626 | -0.004593 | 0.010302 | -0.014436 | -0.30793 | -0.25292 | -0.12068 | -0.24767 | 0.027656 | -0.075529 | 0.045155 | -0.10646 | -0.094104 | 121.9827 | 121.741 | 121.796 | 62.2847 | -122.0242 | 121.8013 | 121.9425 | 121.9548 | 62.3707 | -122.1696
826.6094 | 122.3099 | -62.2513 | 59.816 | 1.4211e-13 | -0.033365 | -0.005156 | 0.065366 | -0.0068542 | 0.05624 | 0.0021363 | 0.00078395 | -0.0021152 | -0.0036534 | 0.023337 | -0.011736 | -62.2833 | 0.010564 | -62.2639 | 59.6994 | 59.4623 | 59.5219 | -62.2586 | -62.2557 | 0.087354 | -62.3589 | 59.5271 | 59.6683 | 59.6715 | -62.3994 | -0.007307 | -0.11661 | -0.032059 | -0.012586 | -0.005279 | -0.35371 | -0.29412 | -0.14815 | -0.28887 | -0.004388 | -0.10757 | 0.040576 | -0.14766 | -0.14446 | 121.9506 | 121.7136 | 121.7731 | 62.2618 | -122.0746 | 121.7784 | 121.9196 | 121.9228 | 62.3386 | -122.2154
828.2969 | 122.3465 | -62.2742 | 59.7427 | 1.4211e-13 | -0.033579 | -0.0053696 | 0.065579 | -0.006427 | 0.056027 | -0.013124 | 0.00035675 | -0.0025424 | -0.003867 | 0.023551 | -0.011309 | -62.2833 | 0.019721 | -62.2684 | 59.7085 | 59.4714 | 59.5127 | -62.254 | -62.2557 | 0.091933 | -62.3543 | 59.5225 | 59.6683 | 59.6807 | -62.3903 | 0.02016 | -0.034215 | -0.009171 | 0.005724 | -0.014436 | -0.27131 | -0.23003 | -0.1161 | -0.2202 | 0.0185 | -0.080107 | 0.035997 | -0.074418 | -0.06206 | 121.9827 | 121.7456 | 121.7869 | 62.2939 | -121.9967 | 121.7967 | 121.9425 | 121.9548 | 62.3661 | -122.133
830.0625 | 122.2275 | -62.2787 | 59.848 | 1.4211e-13 | -0.033579 | -0.0053696 | 0.065366 | -0.0062134 | 0.056027 | -0.0054937 | 0.00035675 | -0.0025424 | -0.003867 | 0.023551 | -0.011309 | -62.2833 | 0.010564 | -62.2593 | 59.7039 | 59.476 | 59.5219 | -62.2586 | -62.2511 | 0.082776 | -62.3497 | 59.5271 | 59.6683 | 59.6715 | -62.404 | 0.020159 | -0.14408 | -0.004593 | 0.019458 | -0.000701 | -0.37201 | -0.32616 | -0.12526 | -0.32091 | 0.027656 | -0.070951 | 0.054312 | -0.1797 | -0.1765 | 121.9827 | 121.7548 | 121.8006 | 62.2893 | -122.1066 | 121.8059 | 121.9471 | 121.9503 | 62.3615 | -122.252
831.8125 | 122.319 | -62.2696 | 59.7702 | 1.4211e-13 | -0.033365 | -0.0053696 | 0.065579 | -0.006427 | 0.056454 | 0.0097668 | 0.00035675 | -0.0023288 | -0.003867 | 0.023337 | -0.011309 | -62.2788 | 0.010564 | -62.2639 | 59.7039 | 59.4943 | 59.5219 | -62.2632 | -62.2511 | 0.087354 | -62.3497 | 59.5225 | 59.6683 | 59.6807 | -62.404 | 0.006424 | -0.06626 | -0.009171 | 0.005724 | -0.0007 | -0.27588 | -0.24834 | -0.13442 | -0.24767 | 0.0185 | -0.080107 | 0.054312 | -0.10188 | -0.089526 | 121.9735 | 121.7639 | 121.7915 | 62.2802 | -122.0334 | 121.7921 | 121.9379 | 121.9503 | 62.3569 | -122.1742
833.4844 | 122.2504 | -62.2787 | 59.848 | 1.4211e-13 | -0.033579 | -0.0055834 | 0.065366 | -0.0066406 | 0.05624 | 0.0021363 | 0.00035675 | -0.0023288 | -0.0040806 | 0.023337 | -0.011522 | -62.2742 | 0.010564 | -62.2593 | 59.7131 | 59.4989 | 59.5264 | -62.2494 | -62.2511 | 0.087354 | -62.3497 | 59.5271 | 59.6683 | 59.6807 | -62.3994 | 0.029317 | -0.13492 | 0.004564 | 0.019458 | -0.009859 | -0.34912 | -0.32158 | -0.12068 | -0.32091 | 0.027656 | -0.070951 | 0.049733 | -0.1797 | -0.16734 | 121.9918 | 121.7777 | 121.8052 | 62.2893 | -122.0975 | 121.8059 | 121.9471 | 121.9594 | 62.3661 | -122.2475
835.1562 | 122.3648 | -62.2559 | 59.7519 | 1.4211e-13 | -0.033579 | -0.0053696 | 0.065152 | -0.0068542 | 0.055813 | 0.0021363 | 0.00035675 | -0.0019016 | -0.003867 | 0.023337 | -0.011095 | -62.2742 | 0.015142 | -62.2639 | 59.7085 | 59.4897 | 59.5219 | -62.2494 | -62.2511 | 0.087354 | -62.3543 | 59.5225 | 59.6775 | 59.6761 | -62.3949 | 0.006428 | -0.04337 | -0.018325 | -0.008009 | -0.014437 | -0.26214 | -0.23003 | -0.13899 | -0.22936 | 0.004767 | -0.098418 | 0.040576 | -0.074416 | -0.075793 | 121.9644 | 121.7456 | 121.7777 | 62.271 | -122.0013 | 121.7784 | 121.9333 | 121.932 | 62.3432 | -122.1467
836.8438 | 122.2961 | -62.2604 | 59.7702 | 1.4211e-13 | -0.033579 | -0.005156 | 0.065366 | -0.0062134 | 0.056027 | -0.013124 | 0.00035675 | -0.0021152 | -0.0040806 | 0.023765 | -0.011309 | -62.2788 | 0.015142 | -62.2684 | 59.7085 | 59.4714 | 59.531 | -62.2494 | -62.2557 | 0.091933 | -62.3497 | 59.5317 | 59.6683 | 59.6807 | -62.3994 | 0.011006 | -0.061681 | -0.018326 | -0.008009 | -0.019015 | -0.29877 | -0.23918 | -0.13899 | -0.23851 | 0.004767 | -0.089262 | 0.049733 | -0.10188 | -0.089526 | 121.969 | 121.7319 | 121.7915 | 62.2756 | -122.0196 | 121.7921 | 121.9288 | 121.9411 | 62.3524 | -122.1696
838.5312 | 122.2641 | -62.2696 | 59.8389 | 1.4211e-13 | -0.033579 | -0.0053696 | 0.065152 | -0.0062134 | 0.056027 | -0.0054937 | 0.00014315 | -0.0021152 | -0.0036534 | 0.023765 | -0.011522 | -62.2788 | 0.015142 | -62.2639 | 59.7039 | 59.4714 | 59.5264 | -62.2449 | -62.2465 | 0.10109 | -62.3451 | 59.5225 | 59.6775 | 59.6761 | -62.3994 | 0.024739 | -0.13492 | -0.009171 | 0.005724 | -0.019015 | -0.36744 | -0.31243 | -0.12984 | -0.31633 | 0.023079 | -0.075528 | 0.054312 | -0.16139 | -0.16277 | 121.9735 | 121.741 | 121.796 | 62.2847 | -122.0837 | 121.7921 | 121.9471 | 121.9457 | 62.3707 | -122.2383
840.2344 | 122.2229 | -62.2971 | 59.8389 | 1.4211e-13 | -0.033792 | -0.0055834 | 0.065152 | -0.0062134 | 0.05624 | -0.0054937 | 0.00035675 | -0.0023288 | -0.003226 | 0.023765 | -0.011095 | -62.2833 | 0.005985 | -62.2639 | 59.7131 | 59.4897 | 59.531 | -62.254 | -62.2511 | 0.091933 | -62.3405 | 59.5363 | 59.6866 | 59.6761 | -62.3994 | 0.043048 | -0.12577 | 0.013717 | 0.03319 | -0.009858 | -0.34912 | -0.30785 | -0.10237 | -0.3026 | 0.045966 | -0.043483 | 0.058891 | -0.15223 | -0.16277 | 122.0102 | 121.7868 | 121.8281 | 62.303 | -122.0929 | 121.8333 | 121.9837 | 121.9732 | 62.389 | -122.2383
841.9844 | 122.2321 | -62.265 | 59.8801 | 1.4211e-13 | -0.033151 | -0.0053696 | 0.065152 | -0.0066406 | 0.055813 | 0.0021363 | 0.00035675 | -0.0019016 | -0.003867 | 0.023337 | -0.011095 | -62.2788 | 0.015142 | -62.2639 | 59.7085 | 59.4669 | 59.531 | -62.2449 | -62.2511 | 0.087354 | -62.3497 | 59.5317 | 59.6775 | 59.6853 | -62.404 | 0.020162 | -0.17154 | -0.013748 | 0.001147 | -0.019015 | -0.41321 | -0.34905 | -0.139 | -0.34838 | 0.013923 | -0.084684 | 0.054312 | -0.20259 | -0.19481 | 121.9735 | 121.7319 | 121.796 | 62.2802 | -122.1249 | 121.7967 | 121.9425 | 121.9503 | 62.3524 | -122.2841
843.7344 | 122.2229 | -62.2833 | 59.8022 | 1.4211e-13 | -0.033792 | -0.0053696 | 0.065579 | -0.006427 | 0.05624 | -0.013124 | 0.00035675 | -0.0019016 | -0.0034396 | 0.023337 | -0.011309 | -62.2742 | 0.010564 | -62.2593 | 59.7085 | 59.476 | 59.5264 | -62.2449 | -62.2465 | 0.087354 | -62.3543 | 59.5317 | 59.6866 | 59.6853 | -62.3903 | 0.038472 | -0.093724 | 0.009141 | 0.024035 | -0.014437 | -0.32624 | -0.2758 | -0.10695 | -0.27056 | 0.036812 | -0.070952 | 0.035997 | -0.11561 | -0.11699 | 121.9918 | 121.7593 | 121.8098 | 62.2939 | -122.0471 | 121.815 | 121.97 | 121.9686 | 62.3707 | -122.1925
845.4219 | 122.3236 | -62.2467 | 59.8068 | 1.4211e-13 | -0.033365 | -0.0055834 | 0.065366 | -0.0066406 | 0.056027 | -0.013124 | 0.00035675 | -0.0021152 | -0.003867 | 0.023765 | -0.011309 | -62.2788 | 0.010564 | -62.2547 | 59.7131 | 59.476 | 59.5264 | -62.254 | -62.2465 | 0.082776 | -62.3497 | 59.5317 | 59.6912 | 59.6761 | -62.3903 | -0.007306 | -0.093724 | -0.032059 | -0.008008 | -0.000702 | -0.33081 | -0.28038 | -0.14357 | -0.27513 | 0.000191 | -0.10299 | 0.040575 | -0.11561 | -0.13072 | 121.9598 | 121.7227 | 121.7731 | 62.2573 | -122.0608 | 121.7784 | 121.9379 | 121.9228 | 62.3295 | -122.1971
847.1562 | 122.2183 | -62.2925 | 59.8022 | 1.4211e-13 | -0.033792 | -0.0053696 | 0.064938 | -0.0062134 | 0.056027 | -0.020755 | 0.00035675 | -0.0023288 | -0.0034396 | 0.023765 | -0.011522 | -62.2788 | 0.001407 | -62.2593 | 59.7131 | 59.4989 | 59.531 | -62.2494 | -62.2465 | 0.087354 | -62.3451 | 59.5408 | 59.6912 | 59.6761 | -62.3949 | 0.043049 | -0.089146 | 0.013717 | 0.03319 | -0.009859 | -0.30334 | -0.27123 | -0.10237 | -0.2614 | 0.045967 | -0.05264 | 0.049733 | -0.11103 | -0.12615 | 122.0056 | 121.7914 | 121.8235 | 62.2939 | -122.0517 | 121.8333 | 121.9837 | 121.9686 | 62.3798 | -122.1971
848.9062 | 122.374 | -62.2375 | 59.7794 | 1.4211e-13 | -0.033792 | -0.0049424 | 0.065152 | -0.006427 | 0.056027 | -0.0054937 | 0.00057035 | -0.0021152 | -0.003867 | 0.023124 | -0.011522 | -62.2788 | 0.010564 | -62.2547 | 59.7131 | 59.4714 | 59.531 | -62.2494 | -62.2419 | 0.091933 | -62.3405 | 59.5408 | 59.6775 | 59.6853 | -62.3949 | -0.011882 | -0.066258 | -0.041214 | -0.017163 | -0.005281 | -0.30793 | -0.24834 | -0.1573 | -0.23851 | -0.004385 | -0.10299 | 0.054312 | -0.10188 | -0.094102 | 121.9506 | 121.709 | 121.7686 | 62.2481 | -122.0288 | 121.7784 | 121.915 | 121.9228 | 62.3295 | -122.1742
850.6562 | 122.2412 | -62.2604 | 59.8343 | 1.4211e-13 | -0.033792 | -0.005156 | 0.065152 | -0.0062134 | 0.056027 | -0.0054937 | 0.00035675 | -0.0025424 | -0.003867 | 0.023551 | -0.011522 | -62.2742 | 0.015142 | -62.2547 | 59.7085 | 59.4989 | 59.531 | -62.2449 | -62.2465 | 0.087354 | -62.3405 | 59.5363 | 59.6821 | 59.6761 | -62.3949 | 0.015584 | -0.12577 | -0.013747 | 0.005725 | -0.009859 | -0.33539 | -0.30327 | -0.13442 | -0.29802 | 0.013924 | -0.080104 | 0.054312 | -0.15224 | -0.15819 | 121.969 | 121.7593 | 121.7915 | 62.2756 | -122.0791 | 121.7967 | 121.9425 | 121.9365 | 62.3478 | -122.2291
852.3438 | 122.3557 | -62.2559 | 59.7565 | 1.4211e-13 | -0.033792 | -0.0053696 | 0.065152 | -0.006427 | 0.05624 | -0.0054937 | 0.00035675 | -0.0021152 | -0.003867 | 0.023551 | -0.011309 | -62.2696 | 0.015142 | -62.2593 | 59.7131 | 59.4943 | 59.5356 | -62.2494 | -62.2465 | 0.096512 | -62.3451 | 59.5408 | 59.6912 | 59.6853 | -62.3903 | 0.006428 | -0.04337 | -0.013747 | -0.003431 | -0.009859 | -0.26214 | -0.22087 | -0.13441 | -0.21562 | 0.009346 | -0.089261 | 0.045154 | -0.065258 | -0.071214 | 121.969 | 121.7502 | 121.7915 | 62.271 | -122.0059 | 121.7967 | 121.9471 | 121.9411 | 62.3524 | -122.1467
854.0938 | 122.3145 | -62.2559 | 59.7748 | 1.4211e-13 | -0.034006 | -0.0053696 | 0.065152 | -0.0066406 | 0.055813 | -0.0054937 | 0.00014315 | -0.0023288 | -0.003867 | 0.023765 | -0.011309 | -62.2742 | 0.015142 | -62.2593 | 59.7223 | 59.4806 | 59.531 | -62.2357 | -62.2328 | 0.096512 | -62.3451 | 59.5363 | 59.6821 | 59.6624 | -62.3949 | 0.020164 | -0.052523 | -0.018325 | -0.003431 | -0.023595 | -0.29419 | -0.24376 | -0.13899 | -0.23851 | 0.023082 | -0.089261 | 0.049733 | -0.092725 | -0.11242 | 121.9781 | 121.7364 | 121.7869 | 62.271 | -122.0105 | 121.7921 | 121.9379 | 121.9182 | 62.3524 | -122.1696
855.8438 | 122.3282 | -62.2192 | 59.816 | 1.4211e-13 | -0.034006 | -0.005156 | 0.065579 | -0.0062134 | 0.056027 | -0.0054937 | 0.00035675 | -0.0021152 | -0.003867 | 0.023765 | -0.011522 | -62.2696 | 0.010564 | -62.2547 | 59.7177 | 59.4989 | 59.531 | -62.254 | -62.2511 | 0.091933 | -62.3405 | 59.5363 | 59.6912 | 59.6807 | -62.3903 | -0.034772 | -0.098301 | -0.050368 | -0.035474 | -0.000702 | -0.31707 | -0.28496 | -0.17104 | -0.27971 | -0.031854 | -0.1213 | 0.049733 | -0.12477 | -0.1353 | 121.9369 | 121.7181 | 121.7503 | 62.2298 | -122.07 | 121.7555 | 121.9104 | 121.8999 | 62.3112 | -122.2063
857.5938 | 122.2824 | -62.265 | 59.8068 | 1.4211e-13 | -0.033365 | -0.0053696 | 0.065366 | -0.006427 | 0.055813 | -0.013124 | 0.00014315 | -0.0021152 | -0.0040806 | 0.023551 | -0.011522 | -62.2696 | 0.015142 | -62.2547 | 59.7131 | 59.4806 | 59.5402 | -62.2357 | -62.2465 | 0.087354 | -62.3314 | 59.5408 | 59.6958 | 59.6898 | -62.3857 | 0.02932 | -0.093724 | -0.004591 | 0.010303 | -0.019017 | -0.32623 | -0.26665 | -0.12068 | -0.26598 | 0.018502 | -0.066369 | 0.054312 | -0.11103 | -0.11699 | 121.9781 | 121.7456 | 121.8052 | 62.2802 | -122.0425 | 121.8059 | 121.9608 | 121.9548 | 62.3524 | -122.1925
859.2656 | 122.3236 | -62.2696 | 59.7839 | 1.4211e-13 | -0.033579 | -0.005156 | 0.065366 | -0.0066406 | 0.056027 | 0.0021363 | 0.00035675 | -0.0019016 | -0.0036534 | 0.023551 | -0.011736 | -62.2696 | 0.015142 | -62.2456 | 59.7268 | 59.4989 | 59.5448 | -62.2494 | -62.2419 | 0.091933 | -62.3405 | 59.5363 | 59.6866 | 59.6807 | -62.3903 | 0.020161 | -0.057101 | -1.4e-05 | 0.024037 | 0.003876 | -0.28503 | -0.23918 | -0.12068 | -0.24767 | 0.027658 | -0.070949 | 0.049733 | -0.097303 | -0.10326 | 121.9964 | 121.7685 | 121.8143 | 62.2847 | -122.0334 | 121.8059 | 121.9562 | 121.9503 | 62.3615 | -122.1742
861.0156 | 122.2229 | -62.2559 | 59.8618 | 1.4211e-13 | -0.033579 | -0.0053696 | 0.065366 | -0.006427 | 0.05624 | -0.020755 | 0.00035675 | -0.0023288 | -0.0034396 | 0.023551 | -0.011522 | -62.265 | 0.010564 | -62.241 | 59.7223 | 59.4806 | 59.5356 | -62.2449 | -62.2374 | 0.091933 | -62.3268 | 59.5408 | 59.6866 | 59.6944 | -62.3903 | 0.011006 | -0.1395 | -0.009168 | 0.014882 | 0.003876 | -0.38117 | -0.32616 | -0.13441 | -0.32091 | 0.018504 | -0.070946 | 0.063469 | -0.17512 | -0.16734 | 121.9781 | 121.7364 | 121.7915 | 62.2664 | -122.1066 | 121.7967 | 121.9425 | 121.9503 | 62.3478 | -122.252
862.7656 | 122.2916 | -62.2467 | 59.848 | 1.4211e-13 | -0.034006 | -0.0055834 | 0.065366 | -0.0066406 | 0.05624 | 0.0021363 | -7.0448e-05 | -0.0021152 | -0.003867 | 0.023765 | -0.011522 | -62.2604 | 0.015142 | -62.2501 | 59.7131 | 59.5035 | 59.5402 | -62.2357 | -62.2419 | 0.087354 | -62.3314 | 59.5363 | 59.6912 | 59.6944 | -62.3903 | 0.011009 | -0.13492 | -0.013745 | -0.003429 | -0.014438 | -0.34454 | -0.30785 | -0.14357 | -0.31175 | 0.00477 | -0.08468 | 0.05889 | -0.15681 | -0.15361 | 121.9598 | 121.7502 | 121.7869 | 62.2618 | -122.0837 | 121.783 | 121.9379 | 121.9411 | 62.3341 | -122.2383
864.4531 | 122.2321 | -62.3016 | 59.8297 | 1.4211e-13 | -0.033792 | -0.0053696 | 0.065152 | -0.0066406 | 0.055813 | -0.013124 | 0.00035675 | -0.0025424 | -0.003867 | 0.023551 | -0.011522 | -62.265 | 0.005985 | -62.2364 | 59.736 | 59.5035 | 59.5493 | -62.2449 | -62.2374 | 0.091933 | -62.3314 | 59.55 | 59.6866 | 59.7036 | -62.3857 | 0.056783 | -0.09372 | 0.036609 | 0.065238 | 0.008455 | -0.32623 | -0.28038 | -0.08406 | -0.27971 | 0.064281 | -0.029748 | 0.054312 | -0.14308 | -0.12614 | 122.0376 | 121.8051 | 121.851 | 62.3076 | -122.0746 | 121.8516 | 121.9883 | 122.0052 | 62.3936 | -122.2154
866.2031 | 122.2687 | -62.2513 | 59.8389 | 1.4211e-13 | -0.033792 | -0.0055834 | 0.065152 | -0.0062134 | 0.055813 | -0.013124 | 0.00035675 | -0.0021152 | -0.003867 | 0.023765 | -0.011522 | -62.265 | 0.015142 | -62.241 | 59.7314 | 59.5081 | 59.5402 | -62.2357 | -62.2374 | 0.096512 | -62.3314 | 59.5454 | 59.6958 | 59.6944 | -62.3857 | 0.015587 | -0.10745 | -0.013745 | 0.010305 | -0.005282 | -0.3308 | -0.29869 | -0.13441 | -0.29344 | 0.013927 | -0.080102 | 0.054312 | -0.14308 | -0.14445 | 121.9827 | 121.7593 | 121.7915 | 62.2664 | -122.0746 | 121.7967 | 121.9471 | 121.9457 | 62.3478 | -122.2246
867.9531 | 122.3145 | -62.2787 | 59.7748 | 1.4211e-13 | -0.033579 | -0.005156 | 0.065152 | -0.006427 | 0.056027 | 0.0021363 | 0.00035675 | -0.0019016 | -0.003867 | 0.023551 | -0.011309 | -62.265 | 0.010564 | -62.2501 | 59.7268 | 59.5081 | 59.5402 | -62.2357 | -62.2374 | 0.087354 | -62.336 | 59.5408 | 59.6912 | 59.7036 | -62.3857 | 0.043053 | -0.047945 | 0.013721 | 0.028615 | -0.014438 | -0.26672 | -0.2346 | -0.10695 | -0.23393 | 0.041393 | -0.057215 | 0.049733 | -0.083568 | -0.07121 | 122.0056 | 121.7868 | 121.8189 | 62.2893 | -122.0105 | 121.8196 | 121.97 | 121.9823 | 62.3661 | -122.1605
869.6406 | 122.287 | -62.2421 | 59.8434 | 1.4211e-13 | -0.034006 | -0.0053696 | 0.065366 | -0.006427 | 0.056027 | -0.0054937 | 0.00035675 | -0.0019016 | -0.0040806 | 0.023978 | -0.011309 | -62.2604 | 0.015142 | -62.2456 | 59.7314 | 59.4989 | 59.5493 | -62.2311 | -62.2374 | 0.087354 | -62.3314 | 59.5592 | 59.7004 | 59.6944 | -62.3811 | 0.01101 | -0.11203 | -0.018323 | -0.003429 | -0.014439 | -0.34454 | -0.29411 | -0.13899 | -0.28428 | 0.004771 | -0.089258 | 0.049733 | -0.14308 | -0.14903 | 121.9735 | 121.741 | 121.7915 | 62.2573 | -122.0746 | 121.8013 | 121.9425 | 121.9365 | 62.3295 | -122.2246
871.3281 | 122.2687 | -62.2467 | 59.8663 | 1.4211e-13 | -0.034006 | -0.0053696 | 0.065579 | -0.0062134 | 0.05624 | 0.0097668 | 0.00057035 | -0.0021152 | -0.0040806 | 0.023765 | -0.011522 | -62.265 | 0.005985 | -62.2364 | 59.7223 | 59.4943 | 59.5402 | -62.2357 | -62.2282 | 0.087354 | -62.3314 | 59.5546 | 59.7004 | 59.7036 | -62.3811 | 0.011009 | -0.14408 | -0.018323 | 0.010306 | -0.000703 | -0.37201 | -0.32616 | -0.13441 | -0.31175 | 0.018506 | -0.08468 | 0.049733 | -0.16596 | -0.16276 | 121.969 | 121.741 | 121.7869 | 62.2527 | -122.102 | 121.8013 | 121.9471 | 121.9503 | 62.3341 | -122.2475
873.0625 | 122.319 | -62.2421 | 59.8022 | 1.4211e-13 | -0.034006 | -0.0055834 | 0.065366 | -0.0066406 | 0.056027 | -0.0054937 | 0.00035675 | -0.0023288 | -0.003867 | 0.023765 | -0.011309 | -62.2559 | 0.010564 | -62.2364 | 59.736 | 59.5447 | 59.5493 | -62.2357 | -62.2282 | 0.087354 | -62.3222 | 59.5592 | 59.6958 | 59.699 | -62.3765 | 0.006431 | -0.066254 | -0.013745 | 0.005728 | -0.000703 | -0.25755 | -0.25291 | -0.13441 | -0.24308 | 0.013928 | -0.0801 | 0.054312 | -0.10646 | -0.10325 | 121.9781 | 121.7868 | 121.7915 | 62.2527 | -122.0379 | 121.8013 | 121.9379 | 121.9411 | 62.3295 | -122.1788
874.8125 | 122.2595 | -62.2696 | 59.8572 | 1.4211e-13 | -0.03422 | -0.0055834 | 0.065366 | -0.006427 | 0.055813 | 0.0097668 | 0.00035675 | -0.0016878 | -0.0040806 | 0.023765 | -0.011736 | -62.2467 | 0.010564 | -62.2318 | 59.7314 | 59.4943 | 59.5631 | -62.222 | -62.2282 | 0.082776 | -62.3176 | 59.5546 | 59.7049 | 59.7036 | -62.3765 | 0.047634 | -0.12576 | 0.022878 | 0.037772 | -0.009862 | -0.36285 | -0.29411 | -0.10695 | -0.3026 | 0.041394 | -0.048056 | 0.05889 | -0.15223 | -0.15361 | 122.001 | 121.7639 | 121.8327 | 62.2802 | -122.0791 | 121.8242 | 121.9745 | 121.9732 | 62.3524 | -122.2337
876.5781 | 122.2321 | -62.2604 | 59.8389 | 1.4211e-13 | -0.034006 | -0.0053696 | 0.065152 | -0.006427 | 0.05624 | 0.0021363 | 0.00035675 | -0.0023288 | -0.003867 | 0.023765 | -0.011522 | -62.2559 | 0.010564 | -62.2272 | 59.7268 | 59.5401 | 59.5631 | -62.222 | -62.219 | 0.096512 | -62.3176 | 59.5637 | 59.7004 | 59.7081 | -62.3765 | 0.038479 | -0.11203 | 0.004566 | 0.033195 | -0.005284 | -0.29875 | -0.2758 | -0.1161 | -0.27513 | 0.041396 | -0.057211 | 0.05889 | -0.1385 | -0.13072 | 121.9873 | 121.8006 | 121.8235 | 62.271 | -122.0608 | 121.8242 | 121.9608 | 121.9686 | 62.3569 | -122.2154
878.2656 | 122.2366 | -62.2421 | 59.8984 | 1.4211e-13 | -0.034006 | -0.0053696 | 0.064938 | -0.006427 | 0.055813 | -0.0054937 | 0.00014315 | -0.0023288 | -0.003867 | 0.023551 | -0.011736 | -62.2513 | 0.015142 | -62.2364 | 59.736 | 59.5218 | 59.5585 | -62.2174 | -62.2236 | 0.096512 | -62.3176 | 59.5592 | 59.7049 | 59.7127 | -62.3765 | 0.024747 | -0.16238 | -0.009166 | 0.005728 | -0.019019 | -0.37658 | -0.33989 | -0.13441 | -0.33921 | 0.018507 | -0.075522 | 0.05889 | -0.19343 | -0.18565 | 121.9781 | 121.7639 | 121.8006 | 62.2573 | -122.1158 | 121.8013 | 121.9471 | 121.9549 | 62.3386 | -122.2749
880.0156 | 122.319 | -62.233 | 59.7748 | 1.4211e-13 | -0.033792 | -0.005797 | 0.065152 | -0.0059996 | 0.05624 | 0.0021363 | 0.00014315 | -0.0021152 | -0.003867 | 0.023765 | -0.011736 | -62.2513 | 0.015142 | -62.2272 | 59.7451 | 59.5264 | 59.5631 | -62.222 | -62.2236 | 0.091933 | -62.3131 | 59.5637 | 59.7095 | 59.7173 | -62.3628 | 0.011013 | -0.029631 | -0.018321 | 0.005729 | -0.005284 | -0.2484 | -0.21171 | -0.12983 | -0.21104 | 0.009352 | -0.080098 | 0.049733 | -0.065254 | -0.057474 | 121.9781 | 121.7593 | 121.796 | 62.2481 | -121.9967 | 121.7967 | 121.9425 | 121.9503 | 62.3249 | -122.1376
881.7031 | 122.2137 | -62.233 | 59.8618 | 1.4211e-13 | -0.034006 | -0.0053696 | 0.065152 | -0.0062134 | 0.055599 | 0.0021363 | 0.00035675 | -0.0023288 | -0.003867 | 0.023765 | -0.011736 | -62.2421 | 0.015142 | -62.2227 | 59.736 | 59.5126 | 59.5676 | -62.2128 | -62.2099 | 0.096512 | -62.3131 | 59.5683 | 59.7141 | 59.7173 | -62.3582 | 0.020171 | -0.12576 | -0.009164 | 0.010307 | -0.009864 | -0.34911 | -0.29411 | -0.12525 | -0.29344 | 0.023088 | -0.080098 | 0.045154 | -0.14765 | -0.14445 | 121.969 | 121.7456 | 121.8006 | 62.2481 | -122.0746 | 121.8013 | 121.9471 | 121.9503 | 62.3295 | -122.22
883.3906 | 122.2504 | -62.2192 | 59.8938 | 1.4211e-13 | -0.034433 | -0.005797 | 0.065366 | -0.0066406 | 0.055813 | 0.0021363 | 0.00057035 | -0.0021152 | -0.0036534 | 0.023765 | -0.011736 | -62.2421 | 0.010564 | -62.2227 | 59.7543 | 59.5401 | 59.5722 | -62.2082 | -62.2099 | 0.091933 | -62.3131 | 59.5683 | 59.7233 | 59.7265 | -62.3628 | 0.011017 | -0.13949 | -0.022897 | -0.003426 | -0.014443 | -0.35368 | -0.32157 | -0.14356 | -0.32548 | 0.009355 | -0.093831 | 0.049733 | -0.17054 | -0.16734 | 121.9735 | 121.7594 | 121.7915 | 62.2298 | -122.102 | 121.7876 | 121.9425 | 121.9457 | 62.3112 | -122.2566
885.125 | 122.2229 | -62.2284 | 59.9121 | 1.4211e-13 | -0.034006 | -0.005156 | 0.064938 | -0.0066406 | 0.056027 | -0.0054937 | 0.00035675 | -0.0021152 | -0.0036534 | 0.023765 | -0.011309 | -62.2376 | 0.015142 | -62.2181 | 59.7543 | 59.5539 | 59.5722 | -62.2082 | -62.2053 | 0.087354 | -62.3131 | 59.5683 | 59.7233 | 59.7265 | -62.3582 | 0.020173 | -0.1578 | -0.009163 | 0.010309 | -0.009864 | -0.35826 | -0.33988 | -0.12983 | -0.34379 | 0.02309 | -0.084675 | 0.045154 | -0.18885 | -0.18565 | 121.9827 | 121.7822 | 121.8006 | 62.2435 | -122.1203 | 121.7967 | 121.9517 | 121.9549 | 62.3157 | -122.2703
886.8125 | 122.3419 | -62.2147 | 59.8618 | 1.4211e-13 | -0.03422 | -0.0055834 | 0.065152 | -0.006427 | 0.056027 | -0.0054937 | 0.00057035 | -0.0021152 | -0.0036534 | 0.023765 | -0.011522 | -62.2238 | 0.019721 | -62.2089 | 59.7589 | 59.531 | 59.5722 | -62.2082 | -62.2099 | 0.087354 | -62.3085 | 59.5775 | 59.7324 | 59.7356 | -62.3536 | 0.00644 | -0.10287 | -0.009161 | 0.005732 | -0.000708 | -0.3308 | -0.28953 | -0.13898 | -0.28428 | 0.004778 | -0.093829 | 0.045154 | -0.12934 | -0.12613 | 121.9735 | 121.7456 | 121.7869 | 62.2344 | -122.07 | 121.7921 | 121.9471 | 121.9503 | 62.302 | -122.2154
888.5 | 122.2778 | -62.1964 | 59.8938 | 1.4211e-13 | -0.03422 | -0.0053696 | 0.064938 | -0.0062134 | 0.055599 | -0.0054937 | -7.0448e-05 | -0.0021152 | -0.003867 | 0.023765 | -0.012163 | -62.2284 | 0.010564 | -62.2135 | 59.7543 | 59.5951 | 59.5814 | -62.2128 | -62.1961 | 0.091933 | -62.2993 | 59.5821 | 59.7416 | 59.7356 | -62.3536 | -0.01645 | -0.13949 | -0.03205 | -0.017157 | -0.000707 | -0.29874 | -0.31242 | -0.15729 | -0.31175 | 0.000203 | -0.10298 | 0.054311 | -0.15222 | -0.15818 | 121.9507 | 121.7914 | 121.7777 | 62.2069 | -122.1066 | 121.7784 | 121.9379 | 121.932 | 62.2883 | -122.2474
890.1875 | 122.2458 | -62.2375 | 59.903 | 1.4211e-13 | -0.03422 | -0.0053696 | 0.065152 | -0.0066406 | 0.056027 | -0.0054937 | 0.00035675 | -0.0019016 | -0.003867 | 0.023978 | -0.01195 | -62.2238 | 0.010564 | -62.1998 | 59.7589 | 59.563 | 59.5951 | -62.1991 | -62.2007 | 0.096512 | -62.2948 | 59.5866 | 59.7416 | 59.731 | -62.3491 | 0.038486 | -0.14407 | 0.013727 | 0.037777 | -0.000709 | -0.33995 | -0.30783 | -0.11152 | -0.31632 | 0.036823 | -0.057205 | 0.054311 | -0.16138 | -0.17191 | 121.9964 | 121.8006 | 121.8327 | 62.2481 | -122.102 | 121.8242 | 121.9791 | 121.9686 | 62.3341 | -122.252
891.9375 | 122.2366 | -62.2055 | 59.903 | 1.4211e-13 | -0.034433 | -0.005797 | 0.064938 | -0.006427 | 0.055813 | 0.0021363 | -7.0448e-05 | -0.0021152 | -0.0036534 | 0.023551 | -0.011736 | -62.2238 | 0.005985 | -62.2044 | 59.7726 | 59.5859 | 59.5951 | -62.1945 | -62.1961 | 0.087354 | -62.281 | 59.5866 | 59.7462 | 59.7402 | -62.3399 | 0.011021 | -0.13034 | -0.018317 | 0.001154 | -0.009867 | -0.31705 | -0.30783 | -0.1344 | -0.31632 | 0.009358 | -0.075513 | 0.058889 | -0.1568 | -0.16276 | 121.9781 | 121.7914 | 121.8006 | 62.2115 | -122.0974 | 121.7921 | 121.9517 | 121.9457 | 62.2929 | -122.2429
893.6094 | 122.319 | -62.2055 | 59.8297 | 1.4211e-13 | -0.03422 | -0.0053696 | 0.065366 | -0.0068542 | 0.055599 | 0.0021363 | 0.00035675 | -0.0019016 | -0.003867 | 0.023765 | -0.011736 | -62.2147 | 0.010564 | -62.1906 | 59.7818 | 59.5767 | 59.5951 | -62.1945 | -62.1824 | 0.091933 | -62.2856 | 59.5912 | 59.7553 | 59.7539 | -62.3353 | 0.011021 | -0.047936 | -0.00916 | 0.014889 | 0.003868 | -0.25297 | -0.23459 | -0.12982 | -0.2385 | 0.023094 | -0.080092 | 0.049732 | -0.0744 | -0.075777 | 121.9873 | 121.7823 | 121.8006 | 62.2161 | -122.0242 | 121.7967 | 121.9608 | 121.9594 | 62.2974 | -122.165
895.3125 | 122.3282 | -62.2147 | 59.8572 | 1.4211e-13 | -0.03422 | -0.0053696 | 0.065152 | -0.0068542 | 0.056027 | 0.0021363 | 0.00057035 | -0.0019016 | -0.0034396 | 0.024192 | -0.011309 | -62.2055 | 0.015142 | -62.1906 | 59.7818 | 59.6042 | 59.6089 | -62.1807 | -62.187 | 0.096512 | -62.2856 | 59.6049 | 59.7507 | 59.7539 | -62.3399 | 0.033913 | -0.075402 | 0.009153 | 0.024045 | -0.009868 | -0.25296 | -0.24832 | -0.12525 | -0.25223 | 0.027671 | -0.070936 | 0.05431 | -0.10644 | -0.10324 | 121.9964 | 121.8189 | 121.8235 | 62.2298 | -122.0379 | 121.8196 | 121.9654 | 121.9686 | 62.3112 | -122.1971
897.0625 | 122.2733 | -62.2147 | 59.9075 | 1.4211e-13 | -0.034647 | -0.0055834 | 0.064725 | -0.0066406 | 0.055813 | 0.0021363 | 0.00035675 | -0.0021152 | -0.003867 | 0.023978 | -0.011736 | -62.2055 | 0.015142 | -62.186 | 59.7864 | 59.5676 | 59.6134 | -62.1762 | -62.1778 | 0.10109 | -62.2673 | 59.6095 | 59.7553 | 59.7585 | -62.3262 | 0.038492 | -0.12118 | 0.009153 | 0.028624 | -0.009868 | -0.33994 | -0.2941 | -0.11151 | -0.29801 | 0.036829 | -0.052621 | 0.058889 | -0.15222 | -0.14902 | 122.001 | 121.7822 | 121.8281 | 62.2298 | -122.0837 | 121.8242 | 121.97 | 121.9732 | 62.3158 | -122.2337
898.75 | 122.2687 | -62.178 | 59.935 | 1.4211e-13 | -0.034433 | -0.005797 | 0.065152 | -0.0068542 | 0.055813 | -0.013124 | 0.00014315 | -0.0021152 | -0.0036534 | 0.023978 | -0.012163 | -62.2055 | 0.015142 | -62.186 | 59.8001 | 59.5767 | 59.6134 | -62.1762 | -62.1778 | 0.087354 | -62.2673 | 59.6141 | 59.7645 | 59.7585 | -62.3262 | 0.001871 | -0.13491 | -0.027468 | -0.007997 | -0.009868 | -0.35825 | -0.32156 | -0.14813 | -0.3209 | 0.000208 | -0.089242 | 0.058889 | -0.17053 | -0.17648 | 121.9781 | 121.7548 | 121.7915 | 62.1932 | -122.1112 | 121.7921 | 121.9425 | 121.9366 | 62.2654 | -122.2612
900.4375 | 122.3602 | -62.2055 | 59.8343 | 1.4211e-13 | -0.03422 | -0.0055834 | 0.065152 | -0.0066406 | 0.05624 | -0.0054937 | -7.0448e-05 | -0.0021152 | -0.003867 | 0.023978 | -0.011522 | -62.1964 | 0.015142 | -62.1723 | 59.7955 | 59.6088 | 59.6226 | -62.1762 | -62.1733 | 0.082776 | -62.2673 | 59.6049 | 59.7645 | 59.7677 | -62.317 | 0.029336 | -0.038779 | 0.009153 | 0.033202 | 0.003866 | -0.22549 | -0.2117 | -0.11151 | -0.22935 | 0.032252 | -0.061777 | 0.049731 | -0.069821 | -0.066619 | 122.001 | 121.8143 | 121.8281 | 62.2206 | -122.0105 | 121.8105 | 121.97 | 121.9732 | 62.2883 | -122.1513
902.2031 | 122.2778 | -62.1918 | 59.9213 | 1.4211e-13 | -0.034433 | -0.0055834 | 0.065366 | -0.006427 | 0.056027 | -0.013124 | 0.00057035 | -0.0021152 | -0.0040806 | 0.023978 | -0.011736 | -62.1964 | 0.019721 | -62.1631 | 59.7909 | 59.5859 | 59.6272 | -62.1624 | -62.1549 | 0.091933 | -62.2581 | 59.6187 | 59.7736 | 59.7768 | -62.317 | 0.02934 | -0.13033 | -0.00458 | 0.028626 | -0.000714 | -0.33536 | -0.29409 | -0.12524 | -0.30258 | 0.036833 | -0.066352 | 0.058889 | -0.14764 | -0.14444 | 121.9827 | 121.7777 | 121.8189 | 62.2115 | -122.0837 | 121.8105 | 121.9654 | 121.9686 | 62.2837 | -122.2383
903.9375 | 122.287 | -62.178 | 59.9167 | 1.4211e-13 | -0.034647 | -0.0053696 | 0.064725 | -0.006427 | 0.055813 | 0.0021363 | 0.00035675 | -0.0021152 | -0.0036534 | 0.023551 | -0.011522 | -62.1918 | 0.010564 | -62.1631 | 59.8092 | 59.5813 | 59.6272 | -62.1533 | -62.1549 | 0.087354 | -62.2535 | 59.6324 | 59.7782 | 59.7768 | -62.3079 | 0.024766 | -0.10744 | -0.013733 | 0.014894 | -0.009872 | -0.33536 | -0.28952 | -0.12982 | -0.28427 | 0.023101 | -0.075506 | 0.05431 | -0.13848 | -0.13986 | 121.9873 | 121.7594 | 121.8052 | 62.1886 | -122.07 | 121.8105 | 121.9562 | 121.9549 | 62.2654 | -122.2245
905.6719 | 122.2549 | -62.1872 | 59.9487 | 1.4211e-13 | -0.034647 | -0.0049424 | 0.065152 | -0.0066406 | 0.055813 | -0.013124 | 0.00035675 | -0.0021152 | -0.003867 | 0.023978 | -0.01195 | -62.1735 | 0.019721 | -62.1586 | 59.8047 | 59.5859 | 59.6409 | -62.1487 | -62.1504 | 0.091933 | -62.249 | 59.637 | 59.7874 | 59.7814 | -62.3033 | 0.0385 | -0.14406 | 0.013735 | 0.028627 | -0.009873 | -0.36283 | -0.30782 | -0.11608 | -0.31173 | 0.036835 | -0.061772 | 0.05431 | -0.16137 | -0.16732 | 121.9919 | 121.7731 | 121.8281 | 62.2069 | -122.0974 | 121.8242 | 121.9746 | 121.9686 | 62.2791 | -122.252
907.3594 | 122.2137 | -62.2101 | 59.9258 | 1.4211e-13 | -0.034433 | -0.0055834 | 0.064725 | -0.0068542 | 0.055599 | 0.0021363 | 0.00035675 | -0.0023288 | -0.003867 | 0.024192 | -0.01195 | -62.178 | 0.010564 | -62.1494 | 59.8184 | 59.6134 | 59.6455 | -62.1487 | -62.1458 | 0.087354 | -62.249 | 59.637 | 59.7919 | 59.786 | -62.2895 | 0.061388 | -0.10744 | 0.032045 | 0.060672 | -0.000716 | -0.31246 | -0.28036 | -0.079457 | -0.28885 | 0.064302 | -0.038884 | 0.040573 | -0.1339 | -0.13986 | 122.0285 | 121.8235 | 121.8556 | 62.2206 | -122.0745 | 121.8471 | 122.002 | 121.9961 | 62.2974 | -122.2154
909.0938 | 122.287 | -62.1368 | 59.935 | 1.4211e-13 | -0.034433 | -0.0055834 | 0.064938 | -0.0066406 | 0.055813 | -0.013124 | 0.00014315 | -0.0016878 | -0.003867 | 0.024192 | -0.011522 | -62.1735 | 0.015142 | -62.1494 | 59.8138 | 59.6225 | 59.6501 | -62.1533 | -62.1458 | 0.087354 | -62.2444 | 59.6462 | 59.7828 | 59.7997 | -62.2941 | -0.016433 | -0.12117 | -0.036619 | -0.01257 | 0.003863 | -0.31246 | -0.28493 | -0.15728 | -0.28885 | -0.00894 | -0.10755 | 0.049731 | -0.15221 | -0.13528 | 121.9507 | 121.7594 | 121.7869 | 62.152 | -122.0883 | 121.783 | 121.9196 | 121.9366 | 62.2242 | -122.2291
910.8438 | 122.3373 | -62.1552 | 59.8892 | 1.4211e-13 | -0.034433 | -0.0055834 | 0.065152 | -0.0068542 | 0.056027 | -0.013124 | 0.00014315 | -0.0019016 | -0.003867 | 0.024192 | -0.011736 | -62.1643 | 0.019721 | -62.1448 | 59.823 | 59.6042 | 59.6501 | -62.135 | -62.1366 | 0.096512 | -62.2352 | 59.6553 | 59.8057 | 59.7997 | -62.285 | 0.020193 | -0.06624 | -0.009152 | 0.010318 | -0.009875 | -0.285 | -0.23916 | -0.12981 | -0.23391 | 0.018527 | -0.08008 | 0.049731 | -0.083544 | -0.0895 | 121.9781 | 121.7594 | 121.8052 | 62.1749 | -122.0242 | 121.8105 | 121.9608 | 121.9549 | 62.2517 | -122.1742
912.6094 | 122.3282 | -62.1643 | 59.9213 | 1.4211e-13 | -0.034647 | -0.005797 | 0.065152 | -0.0066406 | 0.055599 | 0.0021363 | 0.00035675 | -0.0023288 | -0.0036534 | 0.023765 | -0.011736 | -62.1506 | 0.010564 | -62.1311 | 59.8367 | 59.6271 | 59.6638 | -62.1258 | -62.1275 | 0.096512 | -62.2169 | 59.669 | 59.8103 | 59.8043 | -62.2758 | 0.038506 | -0.084549 | 0.013739 | 0.033209 | -0.005297 | -0.29415 | -0.25747 | -0.1115 | -0.25222 | 0.036841 | -0.052609 | 0.058888 | -0.11101 | -0.11697 | 122.001 | 121.7914 | 121.8281 | 62.1749 | -122.0471 | 121.8334 | 121.9746 | 121.9686 | 62.2608 | -122.1971
914.3125 | 122.2778 | -62.1323 | 59.9808 | 1.4211e-13 | -0.034647 | -0.0055834 | 0.064938 | -0.006427 | 0.056027 | -0.0054937 | 0.00057035 | -0.0021152 | -0.003867 | 0.024192 | -0.011736 | -62.1506 | 0.019721 | -62.1265 | 59.8459 | 59.6134 | 59.6592 | -62.1212 | -62.1183 | 0.091933 | -62.2123 | 59.6645 | 59.8194 | 59.8135 | -62.2666 | 0.011041 | -0.1349 | -0.018305 | 0.005743 | -0.005298 | -0.3674 | -0.32155 | -0.13438 | -0.31631 | 0.013954 | -0.080074 | 0.054309 | -0.16136 | -0.16732 | 121.9781 | 121.7456 | 121.7915 | 62.152 | -122.102 | 121.7967 | 121.9517 | 121.9457 | 62.2242 | -122.2474
916.0625 | 122.3145 | -62.1094 | 59.9579 | 1.4211e-13 | -0.034861 | -0.0055834 | 0.064938 | -0.006427 | 0.05624 | -0.0054937 | 0.00057035 | -0.0023288 | -0.0040806 | 0.024406 | -0.011522 | -62.1414 | 0.015142 | -62.1174 | 59.8505 | 59.6546 | 59.673 | -62.1121 | -62.1137 | 0.082776 | -62.2078 | 59.6736 | 59.824 | 59.8226 | -62.2575 | -0.002689 | -0.10743 | -0.032036 | -0.007988 | -0.005299 | -0.3033 | -0.28493 | -0.14811 | -0.28426 | -0.004355 | -0.098384 | 0.04973 | -0.1339 | -0.13527 | 121.9598 | 121.764 | 121.7823 | 62.1245 | -122.07 | 121.783 | 121.9334 | 121.932 | 62.1922 | -122.2154
917.8281 | 122.3785 | -62.1094 | 59.935 | 1.4211e-13 | -0.034433 | -0.0055834 | 0.064725 | -0.0068542 | 0.056027 | 0.0021363 | 0.00035675 | -0.0021152 | -0.0036534 | 0.023765 | -0.011736 | -62.1368 | 0.019721 | -62.1174 | 59.8596 | 59.6454 | 59.6821 | -62.1121 | -62.1092 | 0.091933 | -62.2032 | 59.6782 | 59.8377 | 59.8272 | -62.2575 | -0.002689 | -0.07539 | -0.027458 | -0.007988 | -0.005299 | -0.28957 | -0.25288 | -0.14811 | -0.2568 | 0.000223 | -0.093805 | 0.054309 | -0.097271 | -0.1078 | 121.969 | 121.7548 | 121.7915 | 62.1291 | -122.0471 | 121.7876 | 121.9471 | 121.9366 | 62.2013 | -122.1925
919.5781 | 122.2275 | -62.1231 | 60.0357 | 1.4211e-13 | -0.034861 | -0.0055834 | 0.065152 | -0.0066406 | 0.055813 | 0.0021363 | 0.00035675 | -0.0021152 | -0.003867 | 0.023765 | -0.01195 | -62.1277 | 0.005985 | -62.1036 | 59.8596 | 59.6683 | 59.6913 | -62.1029 | -62.0908 | 0.10109 | -62.1986 | 59.6874 | 59.8423 | 59.8409 | -62.2483 | 0.020202 | -0.1761 | -0.004568 | 0.01948 | -0.000722 | -0.36738 | -0.34444 | -0.12522 | -0.34835 | 0.032271 | -0.075493 | 0.04973 | -0.1934 | -0.19478 | 121.9827 | 121.7914 | 121.8144 | 62.1291 | -122.1386 | 121.8105 | 121.9654 | 121.964 | 62.2242 | -122.284
921.25 | 122.319 | -62.1185 | 59.9442 | 1.4211e-13 | -0.034647 | -0.0055834 | 0.064725 | -0.0066406 | 0.05624 | -0.0054937 | 0.00057035 | -0.0023288 | -0.003867 | 0.023978 | -0.01195 | -62.1231 | 0.019721 | -62.099 | 59.8779 | 59.6775 | 59.7004 | -62.0937 | -62.0954 | 0.10109 | -62.1849 | 59.6919 | 59.8377 | 59.8364 | -62.2438 | 0.024782 | -0.066231 | -0.004567 | 0.01948 | -0.005302 | -0.26667 | -0.24372 | -0.12522 | -0.25222 | 0.023115 | -0.066335 | 0.058887 | -0.10643 | -0.1078 | 121.9965 | 121.796 | 121.819 | 62.1383 | -122.0379 | 121.8105 | 121.9563 | 121.9549 | 62.2196 | -122.1879
923 | 122.2549 | -62.1185 | 60.0082 | 1.4211e-13 | -0.034861 | -0.0060108 | 0.065152 | -0.006427 | 0.055813 | 0.0021363 | 0.00035675 | -0.0023288 | -0.0036534 | 0.024406 | -0.011522 | -62.1139 | 0.015142 | -62.0945 | 59.8779 | 59.6409 | 59.705 | -62.0846 | -62.0863 | 0.087354 | -62.1757 | 59.6965 | 59.8515 | 59.8501 | -62.2346 | 0.03394 | -0.13032 | 0.004589 | 0.024058 | -0.009882 | -0.36739 | -0.30323 | -0.11606 | -0.31173 | 0.032272 | -0.057178 | 0.058887 | -0.15678 | -0.15815 | 121.9965 | 121.7594 | 121.8235 | 62.1337 | -122.0928 | 121.815 | 121.97 | 121.9686 | 62.2059 | -122.2428
924.75 | 122.3099 | -62.114 | 59.9808 | 1.4211e-13 | -0.034433 | -0.0049424 | 0.064938 | -0.0066406 | 0.056027 | 0.0021363 | 0.00035675 | -0.0019016 | -0.003867 | 0.023978 | -0.011522 | -62.1139 | 0.015142 | -62.0899 | 59.8917 | 59.6866 | 59.7142 | -62.0754 | -62.0817 | 0.091933 | -62.1757 | 59.7103 | 59.8515 | 59.8592 | -62.23 | 0.038521 | -0.089117 | 1.2e-05 | 0.024059 | -0.014462 | -0.29413 | -0.26661 | -0.11606 | -0.27052 | 0.032274 | -0.061755 | 0.054308 | -0.12931 | -0.12153 | 122.0056 | 121.8006 | 121.8281 | 62.1291 | -122.0562 | 121.8242 | 121.9654 | 121.9732 | 62.2059 | -122.2108
926.4375 | 122.2458 | -62.0911 | 60.022 | 1.4211e-13 | -0.034647 | -0.0053696 | 0.064511 | -0.0068542 | 0.055813 | -0.013124 | 0.00014315 | -0.0023288 | -0.003867 | 0.024406 | -0.011522 | -62.0956 | 0.010564 | -62.0762 | 59.9008 | 59.6821 | 59.7187 | -62.0754 | -62.0588 | 0.087354 | -62.1666 | 59.7194 | 59.8606 | 59.8638 | -62.2209 | 0.015632 | -0.12116 | -0.004563 | 0.014905 | -0.000727 | -0.33991 | -0.30323 | -0.12979 | -0.30257 | 0.032278 | -0.075486 | 0.054308 | -0.16135 | -0.15815 | 121.9919 | 121.7731 | 121.8098 | 62.1016 | -122.0974 | 121.8105 | 121.9517 | 121.9549 | 62.1784 | -122.2428
928.1875 | 122.2916 | -62.0819 | 60.0082 | 1.4211e-13 | -0.034647 | -0.005797 | 0.065152 | -0.0068542 | 0.055813 | -0.0054937 | 0.00014315 | -0.0023288 | -0.0040806 | 0.023978 | -0.011095 | -62.0865 | 0.010564 | -62.0716 | 59.9008 | 59.6775 | 59.7371 | -62.0571 | -62.0542 | 0.087354 | -62.1528 | 59.7377 | 59.8789 | 59.8776 | -62.2071 | 0.024792 | -0.10743 | -0.004561 | 0.010329 | -0.014463 | -0.33076 | -0.27118 | -0.12521 | -0.27052 | 0.027702 | -0.070905 | 0.054308 | -0.12931 | -0.13068 | 121.9827 | 121.7594 | 121.819 | 62.0925 | -122.0654 | 121.8196 | 121.9608 | 121.9595 | 62.1693 | -122.2154
929.9375 | 122.3511 | -62.0407 | 59.9487 | 1.4211e-13 | -0.034861 | -0.0053696 | 0.064938 | -0.0068542 | 0.055813 | -0.013124 | 0.00014315 | -0.0023288 | -0.0040806 | 0.023978 | -0.011736 | -62.0773 | 0.015142 | -62.0624 | 59.9191 | 59.7462 | 59.7416 | -62.048 | -62.0405 | 0.091933 | -62.1391 | 59.7423 | 59.8881 | 59.9004 | -62.198 | -0.007249 | -0.029603 | -0.036603 | -0.021714 | -0.014465 | -0.20256 | -0.20709 | -0.15725 | -0.20643 | 0.000239 | -0.098368 | 0.058886 | -0.060638 | -0.04828 | 121.9598 | 121.7869 | 121.7823 | 62.0559 | -121.9967 | 121.783 | 121.9288 | 121.9412 | 62.1326 | -122.1467
931.6875 | 122.287 | -62.0453 | 60.0632 | 1.4211e-13 | -0.035074 | -0.005797 | 0.064938 | -0.0068542 | 0.056027 | -0.0054937 | 0.00035675 | -0.0023288 | -0.0040806 | 0.023978 | -0.01195 | -62.0636 | 0.010564 | -62.0395 | 59.9283 | 59.7004 | 59.7508 | -62.0342 | -62.0313 | 0.091933 | -62.1253 | 59.756 | 59.8972 | 59.8959 | -62.198 | 0.011066 | -0.13489 | -0.01829 | 0.005756 | -0.00531 | -0.36279 | -0.31238 | -0.15268 | -0.30713 | 0.013975 | -0.080054 | 0.072622 | -0.16592 | -0.1673 | 121.9736 | 121.7457 | 121.7961 | 62.0559 | -122.0974 | 121.8013 | 121.9425 | 121.9412 | 62.1372 | -122.2611
933.375 | 122.319 | -62.0132 | 60.0494 | 1.4211e-13 | -0.035074 | -0.005797 | 0.065152 | -0.0066406 | 0.055386 | 0.0097668 | 0.00035675 | -0.0023288 | -0.0042942 | 0.024406 | -0.011736 | -62.0453 | 0.010564 | -62.0304 | 59.9374 | 59.737 | 59.7645 | -62.0159 | -62.0267 | 0.091933 | -62.1208 | 59.7743 | 59.9201 | 59.9233 | -62.1705 | -0.002661 | -0.112 | -0.03202 | -0.017131 | -0.01447 | -0.31243 | -0.28491 | -0.15725 | -0.27509 | -0.01349 | -0.10752 | 0.049728 | -0.1293 | -0.12609 | 121.9507 | 121.7503 | 121.7778 | 62.0238 | -122.0653 | 121.7876 | 121.9334 | 121.9366 | 62.1052 | -122.2199
935.1094 | 122.2458 | -62.0224 | 60.0952 | 1.4211e-13 | -0.034647 | -0.005797 | 0.064725 | -0.0068542 | 0.055813 | -0.020755 | 0.00014315 | -0.0021152 | -0.0040806 | 0.024406 | -0.01195 | -62.0453 | 0.015142 | -62.0166 | 59.9558 | 59.7462 | 59.7828 | -62.0067 | -62.0084 | 0.091933 | -62.107 | 59.7835 | 59.9385 | 59.9279 | -62.1568 | 0.015652 | -0.13946 | -0.022865 | 0.005759 | -0.009893 | -0.34905 | -0.31237 | -0.13435 | -0.31171 | 0.01398 | -0.084627 | 0.049728 | -0.15676 | -0.16729 | 121.9782 | 121.7686 | 121.8052 | 62.0375 | -122.102 | 121.8059 | 121.9609 | 121.9503 | 62.1143 | -122.252
936.7812 | 122.2092 | -62.0407 | 60.1044 | 1.4211e-13 | -0.034861 | -0.0055834 | 0.064938 | -0.006427 | 0.055599 | -0.0054937 | 0.00014315 | -0.0023288 | -0.003867 | 0.023978 | -0.011522 | -62.0086 | 0.0243 | -61.9892 | 59.9832 | 59.7828 | 59.8149 | -61.9793 | -61.9764 | 0.087354 | -62.0796 | 59.811 | 59.9568 | 59.9462 | -62.1293 | 0.061435 | -0.12115 | 0.032072 | 0.051539 | -0.009896 | -0.32157 | -0.28948 | -0.088572 | -0.29339 | 0.064341 | -0.038845 | 0.049727 | -0.1476 | -0.15813 | 122.0239 | 121.8235 | 121.8556 | 62.065 | -122.0836 | 121.8517 | 121.9975 | 121.9869 | 62.1281 | -122.2337
938.5312 | 122.2641 | -61.9858 | 60.141 | 1.4211e-13 | -0.035288 | -0.0055834 | 0.064938 | -0.0066406 | 0.055813 | 0.0021363 | 0.00014315 | -0.0023288 | -0.0040806 | 0.023978 | -0.01195 | -61.9949 | 0.015142 | -61.9754 | 60.0061 | 59.824 | 59.8286 | -61.961 | -61.9672 | 0.096512 | -62.0658 | 59.8247 | 59.9659 | 59.9737 | -62.1247 | 0.02482 | -0.13487 | -0.009123 | 0.010343 | -0.014477 | -0.31698 | -0.31236 | -0.13892 | -0.31628 | 0.018567 | -0.08004 | 0.058884 | -0.17506 | -0.16728 | 121.9919 | 121.8098 | 121.8144 | 62.0009 | -122.102 | 121.8105 | 121.9517 | 121.9595 | 62.0823 | -122.2657
940.2188 | 122.3373 | -61.9583 | 60.0815 | 1.4211e-13 | -0.034861 | -0.0053696 | 0.064938 | -0.006427 | 0.055599 | -0.0054937 | 0.00057035 | -0.0021152 | -0.0036534 | 0.024192 | -0.011736 | -61.9857 | 0.019721 | -61.9663 | 60.0061 | 59.7874 | 59.8332 | -61.961 | -61.9581 | 0.096512 | -62.0567 | 59.8293 | 59.9751 | 59.9783 | -62.1155 | -0.002646 | -0.075365 | -0.027433 | -0.007967 | -0.005321 | -0.29411 | -0.24827 | -0.15723 | -0.25219 | 0.000259 | -0.098348 | 0.058884 | -0.1064 | -0.1032 | 121.9644 | 121.7457 | 121.7915 | 61.978 | -122.0424 | 121.7876 | 121.9334 | 121.9366 | 62.0548 | -122.197
941.9688 | 122.3511 | -61.94 | 60.1044 | 1.4211e-13 | -0.034861 | -0.0055834 | 0.064938 | -0.0068542 | 0.055599 | -0.013124 | -0.00028425 | -0.0021152 | -0.0040806 | 0.024192 | -0.011736 | -61.972 | 0.015142 | -61.9571 | 60.0199 | 59.8057 | 59.8424 | -61.9381 | -61.9489 | 0.091933 | -62.0475 | 59.843 | 59.9888 | 59.992 | -62.1018 | 0.001937 | -0.084518 | -0.032009 | -0.017121 | -0.019058 | -0.29868 | -0.26201 | -0.16181 | -0.26134 | -0.008895 | -0.1075 | 0.054305 | -0.11555 | -0.11235 | 121.9599 | 121.7457 | 121.7824 | 61.9551 | -122.0424 | 121.783 | 121.9288 | 121.932 | 62.0319 | -122.2062
943.7188 | 122.3419 | -61.9217 | 60.0952 | 1.4211e-13 | -0.034861 | -0.0053696 | 0.064725 | -0.0068542 | 0.056027 | -0.0054937 | 0.00035675 | -0.0023288 | -0.0034396 | 0.024406 | -0.011522 | -61.9583 | 0.015142 | -61.9297 | 60.0519 | 59.8835 | 59.8698 | -61.9243 | -61.926 | 0.091933 | -62.0246 | 59.8659 | 60.0117 | 60.0195 | -62.0743 | -0.002636 | -0.043314 | -0.036583 | -0.007962 | -0.005326 | -0.21168 | -0.22538 | -0.15264 | -0.2293 | -0.004311 | -0.10292 | 0.049726 | -0.083501 | -0.075721 | 121.9736 | 121.8052 | 121.7915 | 61.9368 | -122.0195 | 121.7876 | 121.9334 | 121.9412 | 62.0136 | -122.1696
945.4219 | 122.3557 | -61.8759 | 60.1456 | 1.4211e-13 | -0.035074 | -0.0053696 | 0.064938 | -0.0066406 | 0.055813 | 0.0097668 | -7.0448e-05 | -0.0021152 | -0.003867 | 0.024619 | -0.01195 | -61.9354 | 0.015142 | -61.9205 | 60.0565 | 59.8469 | 59.8836 | -61.9106 | -61.9123 | 0.096512 | -62.0109 | 59.8797 | 60.0254 | 60.0287 | -62.0652 | -0.034675 | -0.08909 | -0.059467 | -0.044581 | -0.009906 | -0.29867 | -0.262 | -0.18926 | -0.26591 | -0.036351 | -0.13496 | 0.054304 | -0.12012 | -0.11692 | 121.9324 | 121.7228 | 121.7595 | 61.8911 | -122.0562 | 121.7556 | 121.9014 | 121.9046 | 61.9724 | -122.2107
947.1719 | 122.2733 | -61.9171 | 60.2005 | 1.4211e-13 | -0.034861 | -0.005797 | 0.064938 | -0.0066406 | 0.055599 | -0.028385 | 0.00057035 | -0.0023288 | -0.003867 | 0.024406 | -0.011736 | -61.9216 | 0.019721 | -61.8976 | 60.0839 | 59.8744 | 59.8927 | -61.8877 | -61.8894 | 0.091933 | -61.9926 | 59.9025 | 60.0483 | 60.047 | -62.0423 | 0.029418 | -0.11655 | -0.004534 | 0.019508 | -0.00991 | -0.32612 | -0.30777 | -0.12517 | -0.29795 | 0.027741 | -0.075445 | 0.049725 | -0.15216 | -0.15353 | 122.0011 | 121.7915 | 121.8098 | 61.9368 | -122.0882 | 121.8197 | 121.9655 | 121.9641 | 62.009 | -122.2428
948.9062 | 122.3373 | -61.8576 | 60.173 | 1.4211e-13 | -0.035288 | -0.0055834 | 0.064938 | -0.0068542 | 0.055599 | 0.0021363 | 0.00035675 | -0.0019016 | -0.0036534 | 0.024619 | -0.01195 | -61.9033 | 0.019721 | -61.8793 | 60.1023 | 59.8744 | 59.9156 | -61.874 | -61.8756 | 0.087354 | -61.9742 | 59.9209 | 60.0667 | 60.0653 | -62.0285 | -0.016355 | -0.070772 | -0.04573 | -0.021688 | -0.005333 | -0.29866 | -0.25741 | -0.17094 | -0.25217 | -0.018032 | -0.11664 | 0.054304 | -0.10638 | -0.10775 | 121.9599 | 121.732 | 121.7732 | 61.8773 | -122.047 | 121.7785 | 121.9243 | 121.9229 | 61.945 | -122.2016
950.6562 | 122.2778 | -61.8759 | 60.2463 | 1.4211e-13 | -0.034861 | -0.005797 | 0.064938 | -0.0066406 | 0.055386 | -0.0054937 | 0.00057035 | -0.0021152 | -0.003867 | 0.024406 | -0.012163 | -61.8896 | 0.0243 | -61.8656 | 60.116 | 59.8744 | 59.9339 | -61.8511 | -61.8527 | 0.091933 | -61.9559 | 59.9392 | 60.0758 | 60.0744 | -62.0194 | 0.024851 | -0.13028 | -0.013684 | 0.010358 | -0.014493 | -0.3719 | -0.31234 | -0.14347 | -0.3071 | 0.023172 | -0.080014 | 0.06346 | -0.17046 | -0.17184 | 121.9919 | 121.7503 | 121.8099 | 61.9002 | -122.0973 | 121.8151 | 121.9517 | 121.9504 | 61.9678 | -122.2657
952.3438 | 122.2275 | -61.8713 | 60.2737 | 1.4211e-13 | -0.034861 | -0.005797 | 0.064938 | -0.0068542 | 0.055813 | 0.0021363 | 0.00078395 | -0.0021152 | -0.003867 | 0.024192 | -0.011522 | -61.8576 | 0.010564 | -61.8427 | 60.1343 | 59.9339 | 59.9614 | -61.8327 | -61.839 | 0.10109 | -61.9376 | 59.9575 | 60.0987 | 60.1019 | -61.9873 | 0.038589 | -0.13943 | 0.013787 | 0.028672 | -0.009917 | -0.33984 | -0.31234 | -0.116 | -0.31625 | 0.03233 | -0.066277 | 0.049724 | -0.17504 | -0.17183 | 122.0057 | 121.8052 | 121.8327 | 61.8819 | -122.1065 | 121.8288 | 121.97 | 121.9732 | 61.9724 | -122.2611
954.0938 | 122.3465 | -61.821 | 60.2234 | 1.4211e-13 | -0.035074 | -0.0053696 | 0.065366 | -0.0068542 | 0.055813 | -0.0054937 | 0.00014315 | -0.0021152 | -0.003867 | 0.024192 | -0.011736 | -61.8301 | 0.019721 | -61.8198 | 60.1572 | 59.9385 | 59.9889 | -61.8053 | -61.807 | 0.096512 | -61.9056 | 59.985 | 60.1262 | 60.1248 | -61.9553 | 0.015708 | -0.066185 | -0.009097 | 0.001209 | -0.014499 | -0.28491 | -0.23451 | -0.1343 | -0.23843 | 0.014027 | -0.08458 | 0.049723 | -0.09721 | -0.098587 | 121.9782 | 121.7595 | 121.8099 | 61.8407 | -122.0287 | 121.8059 | 121.9472 | 121.9458 | 61.9175 | -122.1787
955.8438 | 122.2641 | -61.821 | 60.2829 | 1.4211e-13 | -0.035288 | -0.0055834 | 0.064725 | -0.007068 | 0.055386 | -0.013124 | 0.00035675 | -0.0023288 | -0.003867 | 0.024406 | -0.011522 | -61.8118 | 0.010564 | -61.7923 | 60.1801 | 59.9934 | 60.0164 | -61.787 | -61.7841 | 0.091933 | -61.8827 | 60.0033 | 60.1537 | 60.1569 | -61.937 | 0.034024 | -0.1028 | 0.009217 | 0.028679 | -0.005345 | -0.28947 | -0.26655 | -0.11599 | -0.27962 | 0.036921 | -0.061686 | 0.054302 | -0.12925 | -0.12605 | 122.0011 | 121.8144 | 121.8373 | 61.8315 | -122.0699 | 121.8243 | 121.9746 | 121.9778 | 61.9129 | -122.2199
957.5938 | 122.2733 | -61.8027 | 60.2966 | 1.4211e-13 | -0.035502 | -0.0055834 | 0.065152 | -0.0068542 | 0.055599 | -0.0054937 | 0.00057035 | -0.0023288 | -0.0036534 | 0.024192 | -0.01195 | -61.7843 | 0.019721 | -61.7648 | 60.2167 | 59.998 | 60.0301 | -61.7549 | -61.752 | 0.087354 | -61.8598 | 60.0262 | 60.1811 | 60.1843 | -61.9187 | 0.047765 | -0.079908 | 0.018376 | 0.037837 | -0.009928 | -0.29862 | -0.26654 | -0.11598 | -0.27046 | 0.050661 | -0.057104 | 0.058879 | -0.11551 | -0.11231 | 122.0194 | 121.8007 | 121.8328 | 61.8224 | -122.0515 | 121.8288 | 121.9838 | 121.987 | 61.89 | -122.2153
959.2656 | 122.4014 | -61.7294 | 60.3653 | 1.4211e-13 | -0.035074 | -0.0060108 | 0.064725 | -0.0066406 | 0.055599 | -0.0054937 | 0.00014315 | -0.0021152 | -0.003867 | 0.024192 | -0.011736 | -61.7522 | 0.010564 | -61.7328 | 60.2488 | 60.0484 | 60.0713 | -61.7274 | -61.7291 | 0.091933 | -61.8277 | 60.0628 | 60.2132 | 60.2118 | -61.8774 | 0.001997 | -0.11652 | -0.022817 | -0.003357 | -0.005354 | -0.31692 | -0.294 | -0.14802 | -0.3025 | 0.000312 | -0.098295 | 0.049721 | -0.15212 | -0.1535 | 121.9782 | 121.7778 | 121.8007 | 61.74 | -122.0927 | 121.7922 | 121.9426 | 121.9412 | 61.8214 | -122.2427
961 | 122.3282 | -61.7111 | 60.3241 | 1.4211e-13 | -0.035288 | -0.0055834 | 0.064511 | -0.0066406 | 0.055813 | -0.020755 | 0.00035675 | -0.0023288 | -0.0036534 | 0.024406 | -0.012163 | -61.7385 | 0.0243 | -61.7191 | 60.2579 | 60.085 | 60.0896 | -61.7091 | -61.72 | 0.087354 | -61.8048 | 60.0811 | 60.2269 | 60.2347 | -61.8683 | 0.002003 | -0.066169 | -0.027392 | -0.007932 | -0.009935 | -0.23909 | -0.23449 | -0.15717 | -0.24299 | -0.00884 | -0.093711 | 0.063457 | -0.097189 | -0.089409 | 121.969 | 121.7961 | 121.8007 | 61.7354 | -122.0332 | 121.7922 | 121.938 | 121.9458 | 61.7985 | -122.1924
962.7344 | 122.2733 | -61.702 | 60.4294 | 1.4211e-13 | -0.035074 | -0.0055834 | 0.064938 | -0.0062134 | 0.055599 | -0.013124 | 0.00014315 | -0.0023288 | -0.003867 | 0.024406 | -0.01195 | -61.7019 | 0.015142 | -61.6778 | 60.29 | 60.1079 | 60.1217 | -61.6679 | -61.6696 | 0.082776 | -61.7774 | 60.1177 | 60.2773 | 60.2713 | -61.8271 | 0.034057 | -0.1394 | 7.9e-05 | 0.024117 | -0.00994 | -0.32148 | -0.30772 | -0.12512 | -0.31164 | 0.03237 | -0.075395 | 0.04972 | -0.15211 | -0.15806 | 121.9919 | 121.8099 | 121.8236 | 61.7171 | -122.0973 | 121.8197 | 121.9792 | 121.9733 | 61.7847 | -122.2565
964.4219 | 122.3328 | -61.6882 | 60.3882 | 1.4211e-13 | -0.034861 | -0.0062244 | 0.064725 | -0.0068542 | 0.055599 | -0.0054937 | 0.00035675 | -0.0021152 | -0.0040806 | 0.024192 | -0.01195 | -61.6836 | 0.019721 | -61.6595 | 60.3174 | 60.0942 | 60.1446 | -61.6542 | -61.6604 | 0.096512 | -61.7545 | 60.1361 | 60.2956 | 60.2942 | -61.8179 | 0.034061 | -0.070737 | 0.00466 | 0.028697 | -0.005364 | -0.29402 | -0.24363 | -0.12969 | -0.25213 | 0.027794 | -0.066234 | 0.063456 | -0.092597 | -0.093974 | 122.0057 | 121.7824 | 121.8328 | 61.708 | -122.0424 | 121.8243 | 121.9838 | 121.9824 | 61.7847 | -122.2061
966.1719 | 122.2412 | -61.6425 | 60.5026 | 1.4211e-13 | -0.035288 | -0.0055834 | 0.064297 | -0.0068542 | 0.055599 | -0.0054937 | 0.00014315 | -0.0019016 | -0.0040806 | 0.024406 | -0.01195 | -61.6561 | 0.015142 | -61.6321 | 60.3495 | 60.1766 | 60.1674 | -61.6221 | -61.6284 | 0.091933 | -61.727 | 60.1727 | 60.3276 | 60.3171 | -61.7721 | 0.020337 | -0.15313 | -0.013646 | 0.010391 | -0.009946 | -0.32604 | -0.33518 | -0.12968 | -0.32995 | 0.014069 | -0.084538 | 0.04514 | -0.17499 | -0.18552 | 121.992 | 121.819 | 121.8099 | 61.6576 | -122.1247 | 121.8151 | 121.9701 | 121.9596 | 61.7344 | -122.2748
967.9219 | 122.3099 | -61.6425 | 60.4523 | 1.4211e-13 | -0.035288 | -0.005797 | 0.064938 | -0.0066406 | 0.055172 | 0.0021363 | 0.00035675 | -0.0023288 | -0.0040806 | 0.024619 | -0.011736 | -61.6241 | 0.015142 | -61.6092 | 60.377 | 60.2041 | 60.2041 | -61.5992 | -61.5963 | 0.10109 | -61.6858 | 60.191 | 60.346 | 60.34 | -61.7447 | 0.043232 | -0.075305 | 0.018403 | 0.033282 | -0.00995 | -0.24821 | -0.2482 | -0.1022 | -0.26128 | 0.04612 | -0.04333 | 0.058875 | -0.10632 | -0.11228 | 122.0194 | 121.8465 | 121.8465 | 61.6576 | -122.0515 | 121.8334 | 121.9884 | 121.9825 | 61.7435 | -122.1969
969.6719 | 122.2412 | -61.5646 | 60.5759 | 1.4211e-13 | -0.035288 | -0.0060108 | 0.065152 | -0.0066406 | 0.055599 | -0.013124 | 0.00057035 | -0.0023288 | -0.0036534 | 0.024406 | -0.01195 | -61.5966 | 0.019721 | -61.568 | 60.4044 | 60.2636 | 60.2361 | -61.5718 | -61.5597 | 0.087354 | -61.6675 | 60.223 | 60.3826 | 60.3766 | -61.7172 | -0.007115 | -0.17143 | -0.031947 | -0.003334 | 0.003781 | -0.31228 | -0.33974 | -0.15255 | -0.35283 | 0.00493 | -0.10283 | 0.049717 | -0.19329 | -0.19924 | 121.9691 | 121.8282 | 121.8008 | 61.5844 | -122.1476 | 121.7877 | 121.9472 | 121.9413 | 61.652 | -122.2931
971.3438 | 122.3145 | -61.5646 | 60.4889 | 1.4211e-13 | -0.035288 | -0.005797 | 0.064938 | -0.006427 | 0.055599 | 0.0097668 | 0.00078395 | -0.0023288 | -0.0040806 | 0.024406 | -0.011736 | -61.5645 | 0.0243 | -61.5451 | 60.4365 | 60.2407 | 60.2636 | -61.5397 | -61.5414 | 0.091933 | -61.6354 | 60.2505 | 60.4055 | 60.4133 | -61.6851 | 0.024938 | -0.052407 | 0.000102 | 0.019558 | -0.00538 | -0.2482 | -0.2253 | -0.1205 | -0.23838 | 0.023244 | -0.070784 | 0.049717 | -0.083418 | -0.075638 | 122.0011 | 121.8053 | 121.8282 | 61.5889 | -122.0286 | 121.8151 | 121.9701 | 121.9779 | 61.6566 | -122.174
973.0938 | 122.3282 | -61.5189 | 60.5347 | 1.4211e-13 | -0.035502 | -0.0055834 | 0.064938 | -0.006427 | 0.055599 | -0.013124 | 0.00014315 | -0.0021152 | -0.0040806 | 0.024406 | -0.01195 | -61.5325 | 0.0243 | -61.5085 | 60.4731 | 60.3002 | 60.2956 | -61.5076 | -61.5093 | 0.087354 | -61.5988 | 60.2871 | 60.4421 | 60.4453 | -61.6531 | 0.011214 | -0.061556 | -0.013625 | 0.010408 | -0.000806 | -0.23445 | -0.23902 | -0.13423 | -0.24753 | 0.009519 | -0.07993 | 0.054295 | -0.092565 | -0.089364 | 121.992 | 121.8191 | 121.8145 | 61.5432 | -122.0423 | 121.806 | 121.961 | 121.9642 | 61.6062 | -122.1878
974.8438 | 122.3465 | -61.4182 | 60.6262 | 1.4211e-13 | -0.035288 | -0.0055834 | 0.064511 | -0.0068542 | 0.055386 | -0.0054937 | 0.00035675 | -0.0021152 | -0.003867 | 0.024406 | -0.01195 | -61.4867 | 0.0243 | -61.4581 | 60.5235 | 60.346 | 60.346 | -61.4527 | -61.4498 | 0.091933 | -61.5438 | 60.3467 | 60.4925 | 60.4911 | -61.6027 | -0.034547 | -0.10275 | -0.068549 | -0.039939 | -0.005392 | -0.28021 | -0.28021 | -0.18457 | -0.27956 | -0.031665 | -0.12569 | 0.058872 | -0.13375 | -0.13513 | 121.9416 | 121.7642 | 121.7642 | 61.4425 | -122.0789 | 121.7648 | 121.9106 | 121.9092 | 61.5101 | -122.2289
976.5938 | 122.3236 | -61.3861 | 60.64 | 1.4211e-13 | -0.035288 | -0.0055834 | 0.064725 | -0.007068 | 0.055599 | 0.0097668 | 0.00035675 | -0.0021152 | -0.0040806 | 0.024406 | -0.01195 | -61.4089 | 0.0243 | -61.3894 | 60.5876 | 60.4193 | 60.4193 | -61.3794 | -61.3857 | 0.091933 | -61.4797 | 60.4153 | 60.5611 | 60.5598 | -61.5203 | 0.006672 | -0.052382 | -0.022761 | -0.003309 | -0.009981 | -0.22069 | -0.22069 | -0.13419 | -0.22462 | 0.000393 | -0.093636 | 0.040555 | -0.078808 | -0.080185 | 121.9737 | 121.8054 | 121.8054 | 61.4104 | -122.0194 | 121.8014 | 121.9473 | 121.9459 | 61.478 | -122.1603
978.2812 | 122.3557 | -61.3174 | 60.6995 | 1.4211e-13 | -0.035502 | -0.0055834 | 0.064725 | -0.0066406 | 0.055599 | -0.0054937 | 0.00057035 | -0.0023288 | -0.0040806 | 0.024619 | -0.011736 | -61.331 | 0.0243 | -61.3162 | 60.67 | 60.4742 | 60.4925 | -61.3108 | -61.3033 | 0.096512 | -61.4065 | 60.4886 | 60.6436 | 60.6422 | -61.4562 | 0.006692 | -0.02948 | -0.013592 | 0.00128 | -0.005412 | -0.22525 | -0.20694 | -0.13875 | -0.21087 | 0.014145 | -0.08904 | 0.049712 | -0.055902 | -0.057279 | 121.9874 | 121.7917 | 121.81 | 61.3417 | -122.0102 | 121.806 | 121.961 | 121.9596 | 61.414 | -122.1557
980.0312 | 122.2687 | -61.2946 | 60.7819 | 1.4211e-13 | -0.035715 | -0.0055834 | 0.064938 | -0.007068 | 0.055386 | -0.013124 | 0.00014315 | -0.0023288 | -0.0042942 | 0.024406 | -0.01195 | -61.331 | 0.019721 | -61.3024 | 60.6791 | 60.5017 | 60.5108 | -61.2924 | -61.3033 | 0.096512 | -61.3927 | 60.5023 | 60.6527 | 60.6422 | -61.447 | 0.00212 | -0.10272 | -0.03648 | -0.007873 | -0.009993 | -0.28017 | -0.27102 | -0.15248 | -0.27953 | -0.008743 | -0.098192 | 0.05429 | -0.12914 | -0.13968 | 121.9737 | 121.7962 | 121.8054 | 61.3143 | -122.0743 | 121.7969 | 121.9473 | 121.9367 | 61.3911 | -122.2289
981.7812 | 122.3373 | -61.3129 | 60.7727 | 1.4211e-13 | -0.035715 | -0.0055834 | 0.064511 | -0.0066406 | 0.055599 | -0.013124 | 0.00057035 | -0.0021152 | -0.0036534 | 0.025047 | -0.012163 | -61.3081 | 0.015142 | -61.2887 | 60.702 | 60.4925 | 60.5292 | -61.2741 | -61.2758 | 0.096512 | -61.3744 | 60.5161 | 60.671 | 60.6651 | -61.4287 | 0.038745 | -0.070673 | 0.004722 | 0.024172 | -0.014573 | -0.28017 | -0.24355 | -0.11586 | -0.25664 | 0.03704 | -0.061567 | 0.05429 | -0.10167 | -0.10763 | 122.0149 | 121.8054 | 121.842 | 61.328 | -122.0468 | 121.8289 | 121.9839 | 121.9779 | 61.4094 | -122.2014
983.5312 | 122.3145 | -61.2442 | 60.8047 | 1.4211e-13 | -0.035288 | -0.005797 | 0.064725 | -0.007068 | 0.055386 | -0.0054937 | 0.00014315 | -0.0021152 | -0.0040806 | 0.024406 | -0.011736 | -61.2486 | 0.015142 | -61.2338 | 60.7524 | 60.5704 | 60.5749 | -61.2329 | -61.2346 | 0.096512 | -61.3195 | 60.5664 | 60.726 | 60.7154 | -61.3738 | 0.011292 | -0.052355 | -0.004423 | 0.010447 | -0.000845 | -0.23438 | -0.22981 | -0.12957 | -0.23832 | 0.009584 | -0.075287 | 0.054288 | -0.078773 | -0.089308 | 121.9966 | 121.8146 | 121.8191 | 61.2593 | -122.0377 | 121.8106 | 121.9702 | 121.9596 | 61.3407 | -122.1785
985.2031 | 122.2733 | -61.171 | 60.9787 | 1.4211e-13 | -0.035502 | -0.0055834 | 0.064938 | -0.007068 | 0.055813 | -0.020755 | 0.00014315 | -0.0021152 | -0.0036534 | 0.024833 | -0.012163 | -61.1799 | 0.015142 | -61.1605 | 60.8256 | 60.6253 | 60.6482 | -61.1413 | -61.1568 | 0.087354 | -61.2462 | 60.6534 | 60.8038 | 60.7841 | -61.2914 | 0.029627 | -0.15305 | -0.00899 | 0.010456 | -0.019171 | -0.35338 | -0.3305 | -0.1204 | -0.32528 | 0.014179 | -0.075271 | 0.045128 | -0.17489 | -0.19458 | 121.9966 | 121.7963 | 121.8192 | 61.1861 | -122.12 | 121.8244 | 121.9748 | 121.9551 | 61.2583 | -122.2701
986.9531 | 122.2275 | -61.0931 | 60.9924 | 1.4211e-13 | -0.035288 | -0.0055834 | 0.064511 | -0.006427 | 0.055386 | 0.0021363 | 0.00035675 | -0.0023288 | -0.0040806 | 0.024619 | -0.01195 | -61.1479 | 0.019721 | -61.1285 | 60.8577 | 60.6345 | 60.6848 | -61.1139 | -61.1339 | 0.096512 | -61.2188 | 60.6626 | 60.8359 | 60.8207 | -61.273 | -0.020718 | -0.13473 | -0.054761 | -0.035315 | -0.014597 | -0.35795 | -0.30761 | -0.1799 | -0.32985 | -0.040746 | -0.12562 | 0.054286 | -0.15657 | -0.17168 | 121.9508 | 121.7276 | 121.778 | 61.1129 | -122.1063 | 121.7557 | 121.929 | 121.9139 | 61.1897 | -122.2655
988.7031 | 122.2824 | -61.1069 | 60.965 | 1.4211e-13 | -0.035288 | -0.0055834 | 0.064511 | -0.007068 | 0.055599 | 0.0021363 | 0.00078395 | -0.0021152 | -0.003867 | 0.024406 | -0.01195 | -61.125 | 0.010564 | -61.1056 | 60.876 | 60.7169 | 60.7123 | -61.091 | -61.0927 | 0.087354 | -61.1867 | 60.7084 | 60.8633 | 60.8574 | -61.2456 | 0.015909 | -0.088956 | -0.018136 | 0.00131 | -0.014599 | -0.24807 | -0.25267 | -0.1387 | -0.2566 | 0.014195 | -0.079833 | 0.058864 | -0.10163 | -0.10759 | 121.9829 | 121.8238 | 121.8192 | 61.1174 | -122.0559 | 121.8152 | 121.9702 | 121.9643 | 61.1942 | -122.2105
990.4688 | 122.287 | -61.0291 | 61.0794 | 1.4211e-13 | -0.035502 | -0.0055834 | 0.064938 | -0.0066406 | 0.055386 | -0.0054937 | 0.00035675 | -0.0023288 | -0.003867 | 0.024192 | -0.012377 | -61.0518 | 0.010564 | -61.0277 | 60.9493 | 60.7902 | 60.781 | -61.0223 | -61.0286 | 0.091933 | -61.1226 | 60.7679 | 60.9274 | 60.9261 | -61.1723 | 0.006773 | -0.13014 | -0.022702 | 0.001321 | -0.005452 | -0.28925 | -0.29843 | -0.14326 | -0.31152 | 0.000477 | -0.093551 | 0.049705 | -0.15197 | -0.15335 | 121.9783 | 121.8192 | 121.81 | 61.0396 | -122.1017 | 121.7969 | 121.9565 | 121.9551 | 61.121 | -122.2517
992.1562 | 122.2366 | -61.0016 | 61.1435 | 1.4211e-13 | -0.035715 | -0.005797 | 0.064725 | -0.0066406 | 0.055386 | -0.013124 | 0.00057035 | -0.0021152 | -0.003867 | 0.024406 | -0.01195 | -61.0014 | 0.019721 | -60.9819 | 60.995 | 60.7856 | 60.8268 | -60.9719 | -60.9691 | 0.091933 | -61.0814 | 60.8228 | 60.9778 | 60.9673 | -61.1174 | 0.029675 | -0.14844 | 0.000195 | 0.019637 | -0.010038 | -0.35791 | -0.31673 | -0.11578 | -0.32067 | 0.032534 | -0.079809 | 0.035967 | -0.16569 | -0.17623 | 121.9966 | 121.7872 | 121.8284 | 61.0213 | -122.1154 | 121.8244 | 121.9794 | 121.9689 | 61.0935 | -122.2609
993.9062 | 122.3236 | -60.9558 | 61.1023 | 1.4211e-13 | -0.035715 | -0.0060108 | 0.064725 | -0.007068 | 0.055599 | -0.0054937 | 0.00035675 | -0.0023288 | -0.0040806 | 0.024406 | -0.012377 | -60.9602 | 0.015142 | -60.9499 | 61.0408 | 60.8634 | 60.868 | -60.9307 | -60.9416 | 0.096512 | -61.0448 | 60.864 | 61.0098 | 61.0176 | -61.0807 | 0.02511 | -0.061463 | -0.004376 | 0.005909 | -0.019201 | -0.23887 | -0.23432 | -0.12492 | -0.23826 | 0.01423 | -0.088955 | 0.035967 | -0.092446 | -0.084666 | 121.9966 | 121.8192 | 121.8238 | 60.971 | -122.033 | 121.8198 | 121.9657 | 121.9734 | 61.0523 | -122.183
995.5938 | 122.2321 | -60.9238 | 61.1847 | 1.4211e-13 | -0.035929 | -0.0055834 | 0.064938 | -0.0066406 | 0.055599 | -0.0054937 | 0.00057035 | -0.0023288 | -0.0040806 | 0.024833 | -0.012163 | -60.9281 | 0.019721 | -60.9087 | 61.0775 | 60.9092 | 60.9046 | -60.8986 | -60.905 | 0.091933 | -60.999 | 60.8961 | 61.0511 | 61.0451 | -61.0487 | 0.025118 | -0.10723 | -0.004371 | 0.01507 | -0.010048 | -0.27548 | -0.28009 | -0.12491 | -0.28861 | 0.018816 | -0.075212 | 0.049702 | -0.13363 | -0.13959 | 122.0012 | 121.833 | 121.8284 | 60.9435 | -122.0833 | 121.8198 | 121.9748 | 121.9689 | 61.0157 | -122.2334
997.2656 | 122.2916 | -60.8276 | 61.2854 | 1.4211e-13 | -0.035502 | -0.0055834 | 0.064725 | -0.0068542 | 0.055386 | -0.0054937 | 0.00057035 | -0.0019016 | -0.0040806 | 0.024619 | -0.01195 | -60.8411 | 0.010564 | -60.8171 | 61.169 | 60.9825 | 60.9916 | -60.8116 | -60.8134 | 0.096512 | -60.912 | 60.9831 | 61.1335 | 61.1321 | -60.9571 | 0.015988 | -0.11637 | -0.013512 | 0.010505 | -0.005483 | -0.30292 | -0.29381 | -0.12947 | -0.30233 | 0.01426 | -0.084347 | 0.045121 | -0.15193 | -0.15331 | 121.9967 | 121.8101 | 121.8192 | 60.8382 | -122.097 | 121.8107 | 121.9611 | 121.9597 | 60.9241 | -122.2425
999.0312 | 122.2778 | -60.7773 | 61.3678 | 1.4211e-13 | -0.035715 | -0.005797 | 0.064725 | -0.0068542 | 0.055386 | -0.013124 | 0.00057035 | -0.0021152 | -0.0040806 | 0.024833 | -0.01195 | -60.7771 | 0.0243 | -60.753 | 61.2331 | 61.0237 | 61.0557 | -60.743 | -60.7493 | 0.091933 | -60.8433 | 61.0563 | 61.2022 | 61.2054 | -60.8976 | 0.034318 | -0.13467 | 0.000232 | 0.024247 | -0.010071 | -0.34411 | -0.3121 | -0.1203 | -0.31147 | 0.028008 | -0.06602 | 0.054277 | -0.16565 | -0.16245 | 122.0104 | 121.801 | 121.833 | 60.8016 | -122.1108 | 121.8336 | 121.9794 | 121.9826 | 60.8692 | -122.2654
1000.7188 | 122.3145 | -60.7178 | 61.377 | 1.4211e-13 | -0.035502 | -0.005797 | 0.064511 | -0.007068 | 0.055599 | 0.0021363 | 0.00035675 | -0.0019016 | -0.0034396 | 0.024833 | -0.012163 | -60.7267 | 0.028878 | -60.7073 | 61.2835 | 61.1244 | 61.1198 | -60.6926 | -60.6989 | 0.096512 | -60.7975 | 61.1067 | 61.2525 | 61.2511 | -60.8426 | 0.025176 | -0.093466 | -0.008916 | 0.01052 | -0.014656 | -0.25253 | -0.25716 | -0.12486 | -0.27026 | 0.018864 | -0.079743 | 0.045118 | -0.12444 | -0.12582 | 122.0013 | 121.8422 | 121.8376 | 60.7467 | -122.0695 | 121.8245 | 121.9703 | 121.9689 | 60.8143 | -122.2196
1002.4062 | 122.3419 | -60.6262 | 61.409 | 1.4211e-13 | -0.035715 | -0.005797 | 0.064725 | -0.007068 | 0.055172 | -0.0054937 | 0.00035675 | -0.0021152 | -0.003867 | 0.024619 | -0.012377 | -60.6672 | 0.028878 | -60.6477 | 61.343 | 61.1611 | 61.1702 | -60.6239 | -60.6348 | 0.091933 | -60.738 | 61.1708 | 61.3258 | 61.3152 | -60.7831 | 0.002308 | -0.065991 | -0.040949 | -0.021514 | -0.023822 | -0.24794 | -0.23884 | -0.15689 | -0.23821 | -0.008586 | -0.11177 | 0.045117 | -0.083224 | -0.093759 | 121.9692 | 121.7873 | 121.7964 | 60.6551 | -122.0329 | 121.797 | 121.952 | 121.9415 | 60.7182 | -122.1921
1004.1562 | 122.2137 | -60.5301 | 61.5967 | 1.4211e-13 | -0.035502 | -0.005797 | 0.064725 | -0.0066406 | 0.055172 | -0.0054937 | 0.00035675 | -0.0021152 | -0.003867 | 0.024619 | -0.012163 | -60.571 | 0.015142 | -60.5333 | 61.4392 | 61.2526 | 61.2709 | -60.5369 | -60.5341 | 0.091933 | -60.6373 | 61.2715 | 61.4128 | 61.4114 | -60.687 | -0.006824 | -0.15753 | -0.040934 | -0.003188 | 0.003636 | -0.34405 | -0.32579 | -0.15686 | -0.32516 | -0.003985 | -0.10717 | 0.049693 | -0.18391 | -0.18529 | 121.9692 | 121.7827 | 121.801 | 60.5452 | -122.1336 | 121.8016 | 121.9429 | 121.9415 | 60.622 | -122.2836
1005.9062 | 122.3373 | -60.4385 | 61.5967 | 1.4211e-13 | -0.035929 | -0.0060108 | 0.065152 | -0.0066406 | 0.055386 | 0.0097668 | 0.00057035 | -0.0021152 | -0.003867 | 0.024619 | -0.01195 | -60.4566 | 0.015142 | -60.4417 | 61.5536 | 61.4037 | 61.3762 | -60.4179 | -60.4333 | 0.091933 | -60.532 | 61.3814 | 61.5272 | 61.5259 | -60.5816 | 0.020676 | -0.043068 | -0.018026 | -0.003175 | -0.023851 | -0.19294 | -0.22048 | -0.1431 | -0.21528 | 0.005194 | -0.093413 | 0.049691 | -0.069449 | -0.070826 | 121.9922 | 121.8423 | 121.8147 | 60.4537 | -122.0145 | 121.8199 | 121.9658 | 121.9644 | 60.5305 | -122.1783
1007.6562 | 122.2137 | -60.347 | 61.7569 | 1.4211e-13 | -0.035929 | -0.0055834 | 0.064725 | -0.0068542 | 0.055172 | -0.013124 | 0.00057035 | -0.0019016 | -0.0042942 | 0.025047 | -0.01195 | -60.3467 | 0.015142 | -60.3273 | 61.6635 | 61.5274 | 61.4907 | -60.308 | -60.3189 | 0.087354 | -60.4175 | 61.4821 | 61.6371 | 61.6266 | -60.458 | 0.039018 | -0.093404 | 0.000302 | 0.01973 | -0.019288 | -0.22953 | -0.26624 | -0.11103 | -0.27477 | 0.028109 | -0.070498 | 0.040531 | -0.11978 | -0.13031 | 122.0105 | 121.8744 | 121.8376 | 60.3621 | -122.0649 | 121.8291 | 121.9841 | 121.9736 | 60.4343 | -122.2149
1009.3438 | 122.2458 | -60.26 | 61.8576 | 1.4211e-13 | -0.035715 | -0.0055834 | 0.064725 | -0.0066406 | 0.055386 | 0.0097668 | 0.00014315 | -0.0021152 | -0.0034396 | 0.024406 | -0.01195 | -60.2826 | 0.019721 | -60.2586 | 61.7322 | 61.5823 | 61.5548 | -60.2439 | -60.2548 | 0.091933 | -60.3488 | 61.5508 | 61.7012 | 61.6998 | -60.3893 | 0.016147 | -0.12544 | -0.022575 | 0.001429 | -0.014718 | -0.27529 | -0.30284 | -0.12932 | -0.3068 | 0.005236 | -0.088792 | 0.040529 | -0.15639 | -0.15776 | 121.9922 | 121.8423 | 121.8148 | 60.2797 | -122.1015 | 121.8108 | 121.9612 | 121.9599 | 60.3519 | -122.2469
1011.0938 | 122.3785 | -60.1273 | 61.9263 | 1.4211e-13 | -0.035715 | -0.005797 | 0.064725 | -0.0068542 | 0.055172 | -0.0054937 | 0.00078395 | -0.0023288 | -0.0040806 | 0.024833 | -0.01195 | -60.1956 | 0.019721 | -60.1808 | 61.8146 | 61.6464 | 61.6463 | -60.1569 | -60.1678 | 0.096512 | -60.2572 | 61.6378 | 61.7974 | 61.7868 | -60.3115 | -0.029605 | -0.11169 | -0.068338 | -0.053493 | -0.023888 | -0.27985 | -0.27994 | -0.18423 | -0.28847 | -0.040521 | -0.12997 | 0.054263 | -0.1289 | -0.13944 | 121.9418 | 121.7737 | 121.7736 | 60.147 | -122.0831 | 121.7651 | 121.9246 | 121.9141 | 60.2238 | -122.2378
1012.8438 | 122.374 | -60.054 | 61.9766 | 1.4211e-13 | -0.036143 | -0.0060108 | 0.064725 | -0.0068542 | 0.055172 | -0.020755 | 0.00035675 | -0.0021152 | -0.0036534 | 0.025047 | -0.012163 | -60.0857 | 0.015142 | -60.0617 | 61.929 | 61.7426 | 61.7562 | -60.0424 | -60.0533 | 0.087354 | -60.1519 | 61.7431 | 61.9027 | 61.8921 | -60.2016 | 0.011626 | -0.047584 | -0.031699 | -0.007699 | -0.019325 | -0.23405 | -0.2204 | -0.14758 | -0.23352 | 0.000705 | -0.097902 | 0.049682 | -0.073947 | -0.084482 | 121.9831 | 121.7966 | 121.8102 | 60.0692 | -122.019 | 121.7971 | 121.9567 | 121.9462 | 60.1414 | -122.1782
1014.5781 | 122.3557 | -59.9716 | 62.0956 | 1.4211e-13 | -0.035715 | -0.005797 | 0.064511 | -0.0068542 | 0.055386 | -0.013124 | 0.00035675 | -0.0023288 | -0.003867 | 0.024833 | -0.01195 | -60.0033 | 0.019721 | -59.9793 | 62.0069 | 61.8433 | 61.8432 | -59.96 | -59.9617 | 0.087354 | -60.0649 | 61.8301 | 61.9942 | 61.9837 | -60.1192 | 0.01165 | -0.08877 | -0.031685 | -0.007687 | -0.019337 | -0.25233 | -0.25243 | -0.14756 | -0.26555 | 0.009882 | -0.093303 | 0.054259 | -0.10139 | -0.11193 | 121.9785 | 121.8149 | 121.8148 | 59.9913 | -122.0556 | 121.8017 | 121.9659 | 121.9553 | 60.059 | -122.2148
1016.2656 | 122.3648 | -59.8434 | 62.1918 | 1.4211e-13 | -0.035715 | -0.0055834 | 0.064725 | -0.007068 | 0.055386 | -0.0054937 | 0.00014315 | -0.0021152 | -0.003867 | 0.024619 | -0.012377 | -59.8705 | 0.0243 | -59.8648 | 62.1442 | 62.0082 | 61.9623 | -59.8455 | -59.8564 | 0.087354 | -59.9459 | 61.9446 | 62.1133 | 62.1028 | -59.991 | -0.002051 | -0.047548 | -0.027086 | -0.021404 | -0.019353 | -0.18362 | -0.22951 | -0.14753 | -0.24722 | -0.012981 | -0.10243 | 0.045098 | -0.07848 | -0.089014 | 121.9877 | 121.8516 | 121.8057 | 59.8677 | -122.0373 | 121.788 | 121.9567 | 121.9462 | 59.9308 | -122.1827
1018.0312 | 122.3236 | -59.8022 | 62.2559 | 1.4211e-13 | -0.035929 | -0.005797 | 0.064725 | -0.0066406 | 0.055172 | -0.013124 | 0.00035675 | -0.0021152 | -0.003867 | 0.024619 | -0.012163 | -59.811 | 0.028878 | -59.7916 | 62.2083 | 62.0219 | 62.0309 | -59.7768 | -59.7786 | 0.082776 | -59.8772 | 62.0315 | 62.182 | 62.176 | -59.9223 | 0.025434 | -0.047538 | -0.008765 | 0.010649 | -0.014785 | -0.23397 | -0.22492 | -0.12005 | -0.22431 | 0.023658 | -0.074949 | 0.045097 | -0.073888 | -0.079843 | 122.0106 | 121.8241 | 121.8332 | 59.8311 | -122.0327 | 121.8338 | 121.9842 | 121.9783 | 59.885 | -122.1782
1019.7812 | 122.2504 | -59.761 | 62.3749 | 1.4211e-13 | -0.035715 | -0.005797 | 0.064725 | -0.007068 | 0.055386 | 0.0021363 | 0.00014315 | -0.0021152 | -0.003867 | 0.024833 | -0.01195 | -59.779 | 0.019721 | -59.755 | 62.2404 | 62.0494 | 62.0584 | -59.7402 | -59.7511 | 0.078197 | -59.8543 | 62.059 | 62.214 | 62.2035 | -59.8948 | 0.020866 | -0.13451 | -0.017916 | 0.006077 | -0.014789 | -0.32551 | -0.31647 | -0.13377 | -0.31586 | 0.009931 | -0.093255 | 0.040517 | -0.16086 | -0.17139 | 122.0014 | 121.8104 | 121.8195 | 59.7808 | -122.1151 | 121.8201 | 121.9751 | 121.9645 | 59.8392 | -122.2697
1021.4688 | 122.3557 | -59.6237 | 62.4115 | 1.4211e-13 | -0.036356 | -0.0055834 | 0.065152 | -0.0072816 | 0.055386 | 0.0097668 | 0.00014315 | -0.0021152 | -0.003867 | 0.024619 | -0.012163 | -59.6599 | 0.015142 | -59.6451 | 62.3548 | 62.2279 | 62.1912 | -59.6303 | -59.6412 | 0.087354 | -59.7353 | 62.1689 | 62.3331 | 62.3225 | -59.7712 | -0.006569 | -0.056669 | -0.036207 | -0.021374 | -0.014805 | -0.18355 | -0.22031 | -0.14747 | -0.2426 | -0.017509 | -0.11154 | 0.035936 | -0.078434 | -0.088968 | 121.9785 | 121.8517 | 121.8149 | 59.6389 | -122.0418 | 121.7926 | 121.9568 | 121.9462 | 59.7111 | -122.1827
1023.2188 | 122.3694 | -59.5047 | 62.5031 | 1.4211e-13 | -0.035502 | -0.0053696 | 0.064938 | -0.007068 | 0.055172 | -0.0054937 | 0.00035675 | -0.0021152 | -0.003867 | 0.025047 | -0.012163 | -59.5546 | 0.0243 | -59.5261 | 62.4784 | 62.2966 | 62.3057 | -59.5021 | -59.5176 | 0.087354 | -59.6208 | 62.2879 | 62.4475 | 62.4416 | -59.6476 | 0.002623 | -0.024606 | -0.049922 | -0.021356 | -0.023979 | -0.20642 | -0.1974 | -0.14286 | -0.21511 | -0.012902 | -0.11609 | 0.026775 | -0.055522 | -0.061477 | 121.9831 | 121.8013 | 121.8104 | 59.529 | -122.0051 | 121.7926 | 121.9522 | 121.9463 | 59.5921 | -122.1506
1024.9688 | 122.2366 | -59.4086 | 62.7228 | 1.4211e-13 | -0.035929 | -0.0053696 | 0.064938 | -0.0068542 | 0.055386 | -0.013124 | 0.00057035 | -0.0019016 | -0.003867 | 0.025474 | -0.012163 | -59.4081 | 0.015142 | -59.3841 | 62.6158 | 62.4798 | 62.443 | -59.3556 | -59.3802 | 0.082776 | -59.4834 | 62.4345 | 62.6032 | 62.5698 | -59.5148 | 0.053018 | -0.10698 | 0.000456 | 0.024439 | -0.028579 | -0.24299 | -0.27977 | -0.10621 | -0.28832 | 0.028329 | -0.074857 | 0.031351 | -0.11957 | -0.153 | 122.0244 | 121.8884 | 121.8516 | 59.4237 | -122.0783 | 121.843 | 122.0118 | 121.9783 | 59.4913 | -122.2376
1026.7031 | 122.3465 | -59.3262 | 62.7228 | 1.4211e-13 | -0.035929 | -0.0055834 | 0.065152 | -0.0068542 | 0.055386 | -0.0054937 | 0.00035675 | -0.0021152 | -0.003867 | 0.024619 | -0.01195 | -59.3532 | 0.0243 | -59.3429 | 62.657 | 62.5073 | 62.4888 | -59.3189 | -59.3345 | 0.087354 | -59.4331 | 62.4665 | 62.6307 | 62.6247 | -59.4781 | 0.007252 | -0.065775 | -0.027001 | -0.016753 | -0.024005 | -0.21552 | -0.23398 | -0.15198 | -0.25627 | -0.008281 | -0.10689 | 0.045087 | -0.092103 | -0.098059 | 121.9832 | 121.8334 | 121.815 | 59.3505 | -122.0417 | 121.7927 | 121.9568 | 121.9509 | 59.4135 | -122.2009
1028.3906 | 122.3053 | -59.2941 | 62.796 | 1.4211e-13 | -0.035929 | -0.0055834 | 0.064938 | -0.0068542 | 0.055599 | -0.0054937 | -7.0448e-05 | -0.0019016 | -0.003867 | 0.02526 | -0.012377 | -59.3028 | 0.019721 | -59.2834 | 62.7165 | 62.6034 | 62.5392 | -59.2594 | -59.2841 | 0.087354 | -59.3781 | 62.5306 | 62.6948 | 62.6888 | -59.4232 | 0.034734 | -0.079499 | -0.008682 | 0.01072 | -0.024014 | -0.19261 | -0.25686 | -0.12907 | -0.26542 | 0.01004 | -0.083988 | 0.045085 | -0.10125 | -0.1072 | 122.0106 | 121.8975 | 121.8333 | 59.3138 | -122.0554 | 121.8247 | 121.9889 | 121.9829 | 59.3815 | -122.2192
1030.125 | 122.2275 | -59.2072 | 62.9288 | 1.4211e-13 | -0.036143 | -0.0055834 | 0.064725 | -0.0068542 | 0.055386 | -0.013124 | 0.00057035 | -0.0021152 | -0.004508 | 0.02526 | -0.012163 | -59.2204 | 0.015142 | -59.1964 | 62.8035 | 62.6355 | 62.6262 | -59.1678 | -59.1925 | 0.082776 | -59.2865 | 62.6222 | 62.7772 | 62.7712 | -59.327 | 0.039338 | -0.12526 | -0.013246 | 0.010733 | -0.028605 | -0.2933 | -0.30262 | -0.11989 | -0.3066 | 0.01464 | -0.079389 | 0.040504 | -0.15158 | -0.15754 | 122.0107 | 121.8426 | 121.8333 | 59.2223 | -122.0966 | 121.8293 | 121.9843 | 121.9784 | 59.2899 | -122.2558
1031.875 | 122.2321 | -59.0744 | 63.0295 | 1.4211e-13 | -0.036143 | -0.0055834 | 0.064938 | -0.007068 | 0.055172 | 0.0021363 | 0.00035675 | -0.0021152 | -0.0042942 | 0.025047 | -0.012377 | -59.1105 | 0.019721 | -59.082 | 62.918 | 62.7545 | 62.7406 | -59.0533 | -59.0735 | 0.082776 | -59.1767 | 62.7321 | 62.8962 | 62.8811 | -59.2172 | 0.02106 | -0.11151 | -0.036116 | -0.007561 | -0.028621 | -0.27496 | -0.28886 | -0.14275 | -0.29742 | 0.000935 | -0.10225 | 0.040501 | -0.13325 | -0.14836 | 121.9924 | 121.8289 | 121.815 | 59.0941 | -122.0828 | 121.8065 | 121.9706 | 121.9555 | 59.1572 | -122.2466
1033.5625 | 122.2412 | -59.024 | 63.1302 | 1.4211e-13 | -0.035929 | -0.0055834 | 0.064938 | -0.0066406 | 0.054958 | 0.0021363 | 0.00014315 | -0.0019016 | -0.0036534 | 0.024833 | -0.012163 | -59.0464 | 0.019721 | -59.0316 | 62.9775 | 62.8507 | 62.7956 | -59.003 | -59.0094 | 0.082776 | -59.1171 | 62.787 | 62.9512 | 62.9406 | -59.1531 | 0.021074 | -0.1527 | -0.022373 | -0.007554 | -0.028628 | -0.27951 | -0.33462 | -0.129 | -0.34319 | 0.014683 | -0.093082 | 0.035921 | -0.17901 | -0.18955 | 122.0015 | 121.8747 | 121.8196 | 59.0438 | -122.1332 | 121.811 | 121.9752 | 121.9647 | 59.1068 | -122.2832
1035.25 | 122.3328 | -58.9645 | 63.0798 | 1.4211e-13 | -0.035929 | -0.0053696 | 0.064725 | -0.007068 | 0.055386 | 0.0021363 | 0.00035675 | -0.0021152 | -0.0042942 | 0.025047 | -0.012377 | -59.0098 | 0.015142 | -58.9767 | 63.0279 | 62.8919 | 62.8459 | -58.9572 | -58.9727 | 0.087354 | -59.0713 | 62.8328 | 62.9878 | 62.9956 | -59.1073 | 0.007354 | -0.051981 | -0.045255 | -0.012124 | -0.019478 | -0.18795 | -0.23391 | -0.14272 | -0.24705 | -0.008196 | -0.1068 | 0.035921 | -0.092028 | -0.084249 | 121.9924 | 121.8564 | 121.8105 | 58.9797 | -122.037 | 121.7973 | 121.9523 | 121.9601 | 59.0519 | -122.1871
1037 | 122.3511 | -58.8821 | 63.1622 | 1.4211e-13 | -0.035929 | -0.0053696 | 0.064511 | -0.0068542 | 0.055386 | 0.0021363 | 0.00014315 | -0.0023288 | -0.003867 | 0.024833 | -0.012377 | -58.8953 | 0.015142 | -58.8805 | 63.124 | 62.988 | 62.9467 | -58.8564 | -58.8812 | 0.082776 | -58.9798 | 62.9335 | 63.0885 | 63.0872 | -59.0157 | 0.025693 | -0.038232 | -0.013193 | 0.001622 | -0.024071 | -0.17419 | -0.21557 | -0.13355 | -0.22872 | 0.00098 | -0.097627 | 0.035918 | -0.073696 | -0.075073 | 122.0061 | 121.8702 | 121.8288 | 58.8973 | -122.0187 | 121.8157 | 121.9707 | 121.9693 | 58.9649 | -122.1779
1038.75 | 122.2275 | -58.7769 | 63.3179 | 1.4211e-13 | -0.035929 | -0.0060108 | 0.064725 | -0.0066406 | 0.055172 | -0.0054937 | 0.00014315 | -0.0019016 | -0.003867 | 0.025474 | -0.012163 | -58.8038 | 0.019721 | -58.7798 | 63.2201 | 63.1163 | 63.052 | -58.7557 | -58.7759 | 0.087354 | -58.8653 | 63.0388 | 63.1938 | 63.197 | -58.9104 | 0.021143 | -0.097726 | -0.026911 | -0.002942 | -0.024085 | -0.20162 | -0.26591 | -0.13352 | -0.27905 | 0.001004 | -0.088445 | 0.045073 | -0.12403 | -0.12083 | 121.997 | 121.8931 | 121.8288 | 58.7966 | -122.0736 | 121.8157 | 121.9707 | 121.9739 | 58.8642 | -122.2282
1040.4531 | 122.2321 | -58.6899 | 63.4369 | 1.4211e-13 | -0.035929 | -0.0060108 | 0.064938 | -0.0068542 | 0.055386 | -0.0054937 | 0.00035675 | -0.0023288 | -0.0036534 | 0.02526 | -0.012591 | -58.7122 | 0.019721 | -58.6882 | 63.3254 | 63.1895 | 63.1527 | -58.6596 | -58.6797 | 0.087354 | -58.7783 | 63.135 | 63.29 | 63.284 | -58.8142 | 0.030325 | -0.11144 | -0.022318 | 0.001649 | -0.028676 | -0.24737 | -0.2842 | -0.12434 | -0.30192 | 0.010182 | -0.088425 | 0.035913 | -0.1469 | -0.15285 | 122.0153 | 121.8794 | 121.8426 | 58.7096 | -122.0964 | 121.8248 | 121.9799 | 121.9739 | 58.7772 | -122.2511
1042.2031 | 122.3511 | -58.6487 | 63.4048 | 1.4211e-13 | -0.036356 | -0.0053696 | 0.064938 | -0.007068 | 0.055386 | -0.013124 | -7.0448e-05 | -0.0023288 | -0.0040806 | 0.024833 | -0.012591 | -58.671 | 0.0243 | -58.6424 | 63.3667 | 63.2536 | 63.1847 | -58.6229 | -58.6339 | 0.096512 | -58.7325 | 63.1762 | 63.3404 | 63.3298 | -58.7776 | 0.025759 | -0.038193 | -0.022311 | 0.006234 | -0.019525 | -0.15122 | -0.2201 | -0.12891 | -0.22867 | 0.014771 | -0.083836 | 0.04507 | -0.064488 | -0.075023 | 122.0153 | 121.9023 | 121.8334 | 58.673 | -122.0278 | 121.8249 | 121.989 | 121.9785 | 58.7452 | -122.1824
1043.9531 | 122.2916 | -58.6029 | 63.5056 | 1.4211e-13 | -0.036356 | -0.005797 | 0.064725 | -0.007068 | 0.055172 | -0.0054937 | 0.00014315 | -0.0021152 | -0.003867 | 0.025047 | -0.012591 | -58.6435 | 0.019721 | -58.6241 | 63.3895 | 63.2628 | 63.2122 | -58.5909 | -58.611 | 0.087354 | -58.7096 | 63.1945 | 63.3587 | 63.3481 | -58.7501 | 0.012034 | -0.11601 | -0.040618 | -0.02123 | -0.033264 | -0.24277 | -0.29334 | -0.14721 | -0.31107 | -0.008112 | -0.10672 | 0.040491 | -0.14688 | -0.15742 | 121.9924 | 121.8657 | 121.8151 | 58.6226 | -122.0964 | 121.7974 | 121.9616 | 121.951 | 58.6903 | -122.2557
1045.6406 | 122.3648 | -58.5434 | 63.5193 | 1.4211e-13 | -0.036143 | -0.0053696 | 0.064511 | -0.0068542 | 0.055172 | -0.0054937 | 0.00035675 | -0.0021152 | -0.0040806 | 0.02526 | -0.01195 | -58.584 | 0.015142 | -58.5646 | 63.4399 | 63.3086 | 63.2672 | -58.5359 | -58.5561 | 0.091933 | -58.6593 | 63.2586 | 63.409 | 63.4031 | -58.6952 | 0.007472 | -0.079379 | -0.040608 | -0.021221 | -0.028693 | -0.21072 | -0.25213 | -0.15177 | -0.2607 | -0.012677 | -0.11586 | 0.03591 | -0.11025 | -0.11621 | 121.9833 | 121.852 | 121.8106 | 58.5585 | -122.0552 | 121.802 | 121.9524 | 121.9465 | 58.6353 | -122.2145
1047.3281 | 122.3419 | -58.493 | 63.5193 | 1.4211e-13 | -0.036143 | -0.0060108 | 0.064725 | -0.007068 | 0.055599 | 0.0021363 | 0.00035675 | -0.0023288 | -0.0040806 | 0.025474 | -0.012377 | -58.5382 | 0.019721 | -58.5188 | 63.4994 | 63.3681 | 63.3129 | -58.4901 | -58.5103 | 0.091933 | -58.6089 | 63.2952 | 63.4594 | 63.458 | -58.6494 | 0.002908 | -0.01986 | -0.045178 | -0.025793 | -0.028701 | -0.15119 | -0.20634 | -0.15634 | -0.22407 | -0.017244 | -0.11585 | 0.040488 | -0.059885 | -0.061263 | 121.9925 | 121.8611 | 121.806 | 58.5128 | -122.0094 | 121.7883 | 121.9524 | 121.9511 | 58.585 | -122.1687
1049.0781 | 122.2321 | -58.429 | 63.6841 | 1.4211e-13 | -0.03657 | -0.005797 | 0.064725 | -0.0068542 | 0.055386 | 0.0021363 | -7.0448e-05 | -0.0023288 | -0.0040806 | 0.025047 | -0.012591 | -58.4512 | 0.019721 | -58.4318 | 63.5818 | 63.4368 | 63.4091 | -58.4031 | -58.4187 | 0.087354 | -58.5219 | 63.4005 | 63.551 | 63.545 | -58.5532 | 0.02582 | -0.10224 | -0.022275 | -0.002892 | -0.028712 | -0.2473 | -0.27499 | -0.12427 | -0.28356 | 0.010244 | -0.092942 | 0.031329 | -0.13311 | -0.13906 | 122.0108 | 121.8657 | 121.8381 | 58.4487 | -122.0872 | 121.8295 | 121.9799 | 121.974 | 58.5163 | -122.2373
1050.7656 | 122.3785 | -58.2962 | 63.7619 | 1.4211e-13 | -0.036143 | -0.0055834 | 0.064511 | -0.0072816 | 0.055386 | -0.013124 | 0.00014315 | -0.0021152 | -0.0042942 | 0.025047 | -0.012591 | -58.378 | 0.033457 | -58.3449 | 63.6597 | 63.5421 | 63.4824 | -58.3253 | -58.3317 | 0.087354 | -58.4441 | 63.4784 | 63.6288 | 63.6229 | -58.4845 | -0.029089 | -0.10223 | -0.081772 | -0.048656 | -0.019567 | -0.21981 | -0.27955 | -0.18834 | -0.28355 | -0.035512 | -0.14785 | 0.040484 | -0.13309 | -0.13905 | 121.9559 | 121.8383 | 121.7786 | 58.3297 | -122.0872 | 121.7746 | 121.925 | 121.9191 | 58.3836 | -122.2464
1052.5156 | 122.2321 | -58.2367 | 63.9084 | 1.4211e-13 | -0.036356 | -0.0055834 | 0.064511 | -0.0068542 | 0.054958 | 0.0021363 | 0.00035675 | -0.0021152 | -0.003867 | 0.02526 | -0.012591 | -58.2773 | 0.0243 | -58.2533 | 63.7558 | 63.6428 | 63.5831 | -58.2246 | -58.2401 | 0.091933 | -58.3479 | 63.5745 | 63.7295 | 63.7236 | -58.3747 | 0.012137 | -0.15257 | -0.040558 | -0.0166 | -0.028737 | -0.26555 | -0.3253 | -0.13796 | -0.33389 | -0.003448 | -0.11121 | 0.026746 | -0.17885 | -0.1848 | 121.9925 | 121.8795 | 121.8198 | 58.261 | -122.1329 | 121.8112 | 121.9662 | 121.9603 | 58.3286 | -122.283
1054.2031 | 122.2275 | -58.2092 | 63.9542 | 1.4211e-13 | -0.03657 | -0.005797 | 0.064938 | -0.007068 | 0.055172 | -0.0054937 | 0.00035675 | -0.0023288 | -0.0040806 | 0.02526 | -0.012591 | -58.2452 | 0.0243 | -58.2121 | 63.7879 | 63.6749 | 63.6197 | -58.1833 | -58.2081 | 0.091933 | -58.3021 | 63.6065 | 63.7753 | 63.7648 | -58.3426 | 0.025883 | -0.1663 | -0.035974 | -0.002861 | -0.028744 | -0.27928 | -0.33445 | -0.13337 | -0.34761 | 0.001138 | -0.09289 | 0.040481 | -0.17884 | -0.18937 | 121.9971 | 121.8841 | 121.8289 | 58.2335 | -122.1375 | 121.8158 | 121.9846 | 121.974 | 58.3012 | -122.2968
1055.9531 | 122.2778 | -58.1635 | 63.9542 | 1.4211e-13 | -0.036143 | -0.0060108 | 0.064938 | -0.0066406 | 0.055386 | -0.0054937 | 0.00035675 | -0.0021152 | -0.0042942 | 0.025047 | -0.012377 | -58.1903 | 0.019721 | -58.1663 | 63.8382 | 63.7161 | 63.6563 | -58.1421 | -58.1715 | 0.091933 | -58.2609 | 63.6432 | 63.812 | 63.8014 | -58.2968 | 0.021316 | -0.11594 | -0.02681 | -0.002855 | -0.024171 | -0.23807 | -0.29782 | -0.13336 | -0.31099 | -0.008009 | -0.097459 | 0.035901 | -0.14221 | -0.15274 | 122.0017 | 121.8795 | 121.8198 | 58.1832 | -122.0963 | 121.8066 | 121.9754 | 121.9649 | 58.2554 | -122.251
1057.6562 | 122.2641 | -58.0582 | 64.064 | 1.4211e-13 | -0.036143 | -0.0055834 | 0.064511 | -0.007068 | 0.054958 | 0.0021363 | 0.00035675 | -0.0023288 | -0.003867 | 0.025047 | -0.012163 | -58.0987 | 0.028878 | -58.0747 | 63.9435 | 63.8077 | 63.7571 | -58.0506 | -58.0707 | 0.091933 | -58.1648 | 63.7485 | 63.9035 | 63.9021 | -58.2052 | 0.007609 | -0.1205 | -0.040527 | -0.016574 | -0.024183 | -0.25635 | -0.30696 | -0.14707 | -0.31554 | -0.012562 | -0.10659 | 0.040478 | -0.1605 | -0.16188 | 122.0017 | 121.8658 | 121.8152 | 58.087 | -122.1146 | 121.8067 | 121.9617 | 121.9603 | 58.1501 | -122.2693
1059.4062 | 122.2824 | -58.0032 | 64.1052 | 1.4211e-13 | -0.03657 | -0.005797 | 0.064938 | -0.0068542 | 0.055386 | -0.0054937 | 0.00035675 | -0.0023288 | -0.003867 | 0.02526 | -0.012377 | -58.0346 | 0.019721 | -58.0061 | 63.9985 | 63.8901 | 63.8257 | -57.9773 | -58.0066 | 0.087354 | -58.1007 | 63.8172 | 63.9768 | 63.9525 | -58.1274 | 0.02594 | -0.10675 | -0.031362 | -0.002832 | -0.028772 | -0.21513 | -0.27948 | -0.12416 | -0.28806 | -0.003393 | -0.097421 | 0.02674 | -0.12844 | -0.15271 | 122.0017 | 121.8933 | 121.829 | 58.023 | -122.0825 | 121.8204 | 121.98 | 121.9557 | 58.0906 | -122.2326
1061.0938 | 122.2641 | -57.8796 | 64.2334 | 1.4211e-13 | -0.036356 | -0.0055834 | 0.064725 | -0.0066406 | 0.055172 | 0.0021363 | 0.00014315 | -0.0025424 | -0.0040806 | 0.025047 | -0.012377 | -57.8972 | 0.019721 | -57.8641 | 64.1496 | 64.0366 | 63.9723 | -57.8353 | -57.8601 | 0.096512 | -57.9587 | 63.9591 | 64.1233 | 64.1128 | -57.9946 | 0.044291 | -0.08384 | -0.017606 | 0.015498 | -0.028793 | -0.19678 | -0.26113 | -0.11497 | -0.2743 | 0.01953 | -0.079077 | 0.035894 | -0.1101 | -0.12063 | 122.0292 | 121.9163 | 121.8519 | 57.8994 | -122.0687 | 121.8387 | 122.0029 | 121.9924 | 57.9762 | -122.228
1062.8438 | 122.374 | -57.7057 | 64.3341 | 1.4211e-13 | -0.03657 | -0.005797 | 0.064725 | -0.007068 | 0.055172 | -0.0054937 | 0.00014315 | -0.0021152 | -0.0040806 | 0.025047 | -0.012377 | -57.7462 | 0.0243 | -57.7131 | 64.3006 | 64.1969 | 64.1142 | -57.6888 | -57.7044 | 0.091933 | -57.803 | 64.101 | 64.2607 | 64.2593 | -57.8435 | 0.016865 | -0.033461 | -0.040471 | -0.007369 | -0.024234 | -0.13723 | -0.21991 | -0.13782 | -0.23308 | 0.001255 | -0.097352 | 0.040469 | -0.073449 | -0.074826 | 122.0063 | 121.9026 | 121.8199 | 57.73 | -122.0229 | 121.8067 | 121.9663 | 121.965 | 57.7976 | -122.1776
1064.5312 | 122.2504 | -57.6187 | 64.5401 | 1.4211e-13 | -0.036356 | -0.005797 | 0.064938 | -0.006427 | 0.055172 | -0.013124 | 0.00057035 | -0.0019016 | -0.003867 | 0.025047 | -0.012591 | -57.6271 | 0.028878 | -57.5986 | 64.4151 | 64.3022 | 64.2287 | -57.5652 | -57.5991 | 0.082776 | -57.6932 | 64.2292 | 64.3843 | 64.3829 | -57.7245 | 0.053521 | -0.125 | -0.008407 | 0.020113 | -0.033408 | -0.2379 | -0.31143 | -0.10575 | -0.31087 | 0.019591 | -0.074438 | 0.031309 | -0.15582 | -0.1572 | 122.0338 | 121.9209 | 121.8474 | 57.6476 | -122.1053 | 121.8479 | 122.003 | 122.0016 | 57.7015 | -122.2646
1066.2188 | 122.3328 | -57.5317 | 64.5355 | 1.4211e-13 | -0.036356 | -0.0055834 | 0.065152 | -0.007068 | 0.055172 | -0.013124 | 0.00035675 | -0.0021152 | -0.0040806 | 0.02526 | -0.012591 | -57.5768 | 0.028878 | -57.5574 | 64.4609 | 64.3434 | 64.279 | -57.524 | -57.5533 | 0.091933 | -57.6474 | 64.2613 | 64.4301 | 64.4287 | -57.6787 | 0.007757 | -0.074634 | -0.04502 | -0.025658 | -0.033415 | -0.19212 | -0.25649 | -0.14693 | -0.27425 | -0.021597 | -0.11563 | 0.031308 | -0.10546 | -0.10683 | 121.9926 | 121.8751 | 121.8108 | 57.5606 | -122.0595 | 121.793 | 121.9618 | 121.9604 | 57.6237 | -122.2142
1067.9688 | 122.3877 | -57.4493 | 64.595 | 1.4211e-13 | -0.03657 | -0.005797 | 0.064725 | -0.0068542 | 0.055172 | -0.0054937 | 0.00014315 | -0.0021152 | -0.0040806 | 0.025474 | -0.012591 | -57.531 | 0.028878 | -57.507 | 64.5113 | 64.3938 | 64.3202 | -57.4782 | -57.503 | 0.091933 | -57.5924 | 64.3208 | 64.485 | 64.4699 | -57.6283 | -0.028851 | -0.083782 | -0.081633 | -0.057694 | -0.028843 | -0.20126 | -0.27479 | -0.17896 | -0.27424 | -0.053628 | -0.14308 | 0.035886 | -0.11002 | -0.12514 | 121.9606 | 121.8431 | 121.7696 | 57.4782 | -122.0732 | 121.7701 | 121.9343 | 121.9192 | 57.5413 | -122.2233
1069.7344 | 122.3465 | -57.3441 | 64.7141 | 1.4211e-13 | -0.03657 | -0.005797 | 0.065152 | -0.0066406 | 0.055172 | 0.0021363 | 0.00035675 | -0.0021152 | -0.0040806 | 0.02526 | -0.012163 | -57.3982 | 0.0243 | -57.3788 | 64.6349 | 64.522 | 64.4576 | -57.35 | -57.3748 | 0.087354 | -57.4734 | 64.449 | 64.6178 | 64.6027 | -57.5001 | -0.005927 | -0.079183 | -0.054146 | -0.034788 | -0.028861 | -0.19206 | -0.25645 | -0.15604 | -0.26506 | -0.030711 | -0.12932 | 0.026725 | -0.096262 | -0.11137 | 121.9789 | 121.866 | 121.8017 | 57.3684 | -122.064 | 121.793 | 121.9618 | 121.9467 | 57.4314 | -122.2141
1071.4062 | 122.3602 | -57.28 | 64.7873 | 1.4211e-13 | -0.03657 | -0.0062244 | 0.064725 | -0.0068542 | 0.054958 | -0.013124 | 0.00035675 | -0.0023288 | -0.0042942 | 0.025474 | -0.012377 | -57.3066 | 0.033457 | -57.2873 | 64.7356 | 64.6181 | 64.5537 | -57.2492 | -57.2649 | 0.087354 | -57.3726 | 64.5497 | 64.7002 | 64.6988 | -57.3994 | 0.030722 | -0.051701 | -0.026665 | -0.007309 | -0.038031 | -0.16915 | -0.23355 | -0.1194 | -0.23757 | 0.015091 | -0.092673 | 0.026723 | -0.087089 | -0.088466 | 122.0156 | 121.8981 | 121.8337 | 57.3134 | -122.0365 | 121.8297 | 121.9802 | 121.9788 | 57.3673 | -122.1867
1073.0938 | 122.2458 | -57.2021 | 64.9521 | 1.4211e-13 | -0.036784 | -0.005797 | 0.064938 | -0.007068 | 0.054958 | 0.0021363 | 0.00035675 | -0.0019016 | -0.0040806 | 0.02526 | -0.012377 | -57.2151 | 0.0243 | -57.1957 | 64.8226 | 64.7235 | 64.6499 | -57.1622 | -57.187 | 0.087354 | -57.2811 | 64.6413 | 64.8009 | 64.7904 | -57.3124 | 0.039902 | -0.12951 | -0.012918 | 0.006436 | -0.033466 | -0.22863 | -0.30219 | -0.11022 | -0.3108 | 0.01511 | -0.078919 | 0.031299 | -0.15116 | -0.16169 | 122.0247 | 121.9256 | 121.852 | 57.2264 | -122.1143 | 121.8434 | 122.0031 | 121.9925 | 57.2895 | -122.2645
1074.8438 | 122.2549 | -57.0648 | 65.062 | 1.4211e-13 | -0.03657 | -0.005797 | 0.064938 | -0.007068 | 0.054958 | -0.013124 | 0.00035675 | -0.0021152 | -0.003867 | 0.025047 | -0.01195 | -57.1052 | 0.028878 | -57.0767 | 64.9416 | 64.8059 | 64.7644 | -57.0386 | -57.068 | 0.087354 | -57.1666 | 64.7512 | 64.9154 | 64.9003 | -57.1887 | 0.026204 | -0.12033 | -0.040365 | -0.011857 | -0.038061 | -0.25607 | -0.29759 | -0.12392 | -0.31078 | -0.003173 | -0.10178 | 0.022139 | -0.14655 | -0.16167 | 122.0064 | 121.8707 | 121.8292 | 57.0937 | -122.1006 | 121.816 | 121.9802 | 121.9651 | 57.1522 | -122.2507
1076.5938 | 122.2549 | -56.987 | 65.1169 | 1.4211e-13 | -0.036784 | -0.0055834 | 0.064938 | -0.0068542 | 0.055386 | -0.013124 | 0.00057035 | -0.0016878 | -0.0042942 | 0.02526 | -0.012377 | -57.0502 | 0.028878 | -57.0126 | 65.0011 | 64.8929 | 64.833 | -56.9791 | -57.0039 | 0.087354 | -57.1071 | 64.8199 | 64.9795 | 64.9644 | -57.1338 | 0.007911 | -0.11574 | -0.063244 | -0.02558 | -0.033491 | -0.224 | -0.28384 | -0.14679 | -0.29703 | -0.01689 | -0.12008 | 0.026716 | -0.13738 | -0.1525 | 121.9881 | 121.8799 | 121.82 | 57.0159 | -122.096 | 121.8069 | 121.9665 | 121.9514 | 57.0744 | -122.2507
1078.2812 | 122.3007 | -56.9687 | 65.1581 | 1.4211e-13 | -0.036997 | -0.0062244 | 0.064725 | -0.0068542 | 0.055386 | -0.0054937 | 0.00035675 | -0.0027562 | -0.003867 | 0.02526 | -0.012163 | -57.0319 | 0.028878 | -57.008 | 65.0057 | 64.9066 | 64.833 | -56.9699 | -57.0085 | 0.091933 | -57.1025 | 64.8199 | 64.9841 | 64.969 | -57.1292 | -0.001242 | -0.15236 | -0.063241 | -0.039313 | -0.038071 | -0.25147 | -0.32504 | -0.16052 | -0.33823 | -0.03978 | -0.13381 | 0.026716 | -0.174 | -0.18912 | 121.9744 | 121.8753 | 121.8017 | 56.9976 | -122.128 | 121.7885 | 121.9528 | 121.9377 | 57.0606 | -122.2873
1080.0312 | 122.3145 | -56.9366 | 65.1443 | 1.4211e-13 | -0.03657 | -0.0060108 | 0.064725 | -0.007068 | 0.055172 | -0.0054937 | 0.00014315 | -0.0025424 | -0.003226 | 0.02526 | -0.012377 | -56.9953 | 0.033457 | -56.9714 | 65.0561 | 64.9158 | 64.8697 | -56.9333 | -56.9581 | 0.082776 | -57.0567 | 64.8702 | 65.0253 | 65.0147 | -57.088 | 0.003346 | -0.088269 | -0.058657 | -0.03473 | -0.038076 | -0.22858 | -0.27468 | -0.15136 | -0.27413 | -0.021457 | -0.12006 | 0.031294 | -0.11906 | -0.1296 | 121.9927 | 121.8524 | 121.8063 | 56.9701 | -122.0776 | 121.8069 | 121.9619 | 121.9514 | 57.0194 | -122.2324
1081.7031 | 122.2733 | -56.9458 | 65.1672 | 1.4211e-13 | -0.036784 | -0.005797 | 0.064725 | -0.007068 | 0.054958 | 0.0021363 | 0.00014315 | -0.0023288 | -0.0030124 | 0.025688 | -0.012377 | -56.9678 | 0.028878 | -56.9439 | 65.0835 | 64.9661 | 64.8971 | -56.9058 | -56.9352 | 0.082776 | -57.0292 | 64.8931 | 65.0482 | 65.0285 | -57.0651 | 0.039974 | -0.083687 | -0.022032 | 0.001895 | -0.038079 | -0.2011 | -0.27009 | -0.11931 | -0.27413 | 0.010592 | -0.083437 | 0.035872 | -0.11906 | -0.13875 | 122.0294 | 121.9119 | 121.8429 | 56.9747 | -122.0731 | 121.8389 | 121.994 | 121.9743 | 57.0286 | -122.2323
1083.3906 | 122.3557 | -56.6711 | 65.3595 | 1.4211e-13 | -0.036784 | -0.005797 | 0.064725 | -0.0068542 | 0.054958 | -0.020755 | 0.00035675 | -0.0025424 | -0.0036534 | 0.02526 | -0.012591 | -56.7526 | 0.033457 | -56.7333 | 65.2942 | 65.1722 | 65.1078 | -56.7044 | -56.7246 | 0.082776 | -56.8186 | 65.1037 | 65.2634 | 65.2528 | -56.8453 | -0.033211 | -0.065342 | -0.081505 | -0.062162 | -0.028951 | -0.18731 | -0.25174 | -0.17418 | -0.25578 | -0.053446 | -0.14747 | 0.02671 | -0.096126 | -0.10666 | 121.9653 | 121.8433 | 121.7789 | 56.7046 | -122.0639 | 121.7749 | 121.9345 | 121.924 | 56.7539 | -122.2048
1085.0938 | 122.3602 | -56.6666 | 65.3549 | 1.4211e-13 | -0.03657 | -0.005797 | 0.065152 | -0.0072816 | 0.055172 | -0.013124 | 0.00035675 | -0.0023288 | -0.0030124 | 0.025474 | -0.012377 | -56.7343 | 0.033457 | -56.7058 | 65.317 | 65.2088 | 65.1307 | -56.6723 | -56.6971 | 0.091933 | -56.8095 | 65.122 | 65.2817 | 65.2757 | -56.827 | -0.005736 | -0.037872 | -0.06777 | -0.039271 | -0.033535 | -0.1461 | -0.22427 | -0.16045 | -0.23289 | -0.030552 | -0.1429 | 0.017552 | -0.073234 | -0.079189 | 121.9836 | 121.8754 | 121.7972 | 56.7 | -122.0272 | 121.7886 | 121.9483 | 121.9423 | 56.7585 | -122.1819
1086.8438 | 122.2458 | -56.543 | 65.5701 | 1.4211e-13 | -0.036997 | -0.0055834 | 0.065152 | -0.0066406 | 0.055172 | -0.013124 | 0.00057035 | -0.0023288 | -0.003226 | 0.025474 | -0.012591 | -56.5924 | 0.0243 | -56.5639 | 65.4636 | 65.3553 | 65.2909 | -56.5212 | -56.5506 | 0.087354 | -56.6538 | 65.2731 | 65.4374 | 65.4314 | -56.6713 | 0.021772 | -0.10651 | -0.049436 | -0.02094 | -0.042712 | -0.21472 | -0.27917 | -0.12836 | -0.29695 | -0.007629 | -0.11082 | 0.017548 | -0.13271 | -0.13867 | 122.0065 | 121.8983 | 121.8339 | 56.5673 | -122.0913 | 121.8161 | 121.9803 | 121.9744 | 56.6303 | -122.2414
1088.5312 | 122.3373 | -56.3553 | 65.7211 | 1.4211e-13 | -0.036997 | -0.005797 | 0.064725 | -0.007068 | 0.055172 | -0.013124 | 0.00014315 | -0.0023288 | -0.003226 | 0.02526 | -0.012804 | -56.4001 | 0.0243 | -56.3808 | 65.6604 | 65.5431 | 65.474 | -56.338 | -56.3629 | 0.087354 | -56.4661 | 65.4608 | 65.6205 | 65.6191 | -56.4882 | 0.017246 | -0.060704 | -0.044827 | -0.025492 | -0.042738 | -0.17804 | -0.24708 | -0.13289 | -0.26029 | -0.007585 | -0.11077 | 0.022123 | -0.10063 | -0.10201 | 122.0157 | 121.8984 | 121.8293 | 56.3796 | -122.0592 | 121.8161 | 121.9758 | 121.9744 | 56.4426 | -122.2093
1090.2188 | 122.2687 | -56.3004 | 65.8493 | 1.4211e-13 | -0.03657 | -0.005797 | 0.064938 | -0.0072816 | 0.055386 | -0.020755 | 0.00014315 | -0.0019016 | -0.003226 | 0.02526 | -0.012804 | -56.3269 | 0.028878 | -56.2984 | 65.7337 | 65.6255 | 65.5427 | -56.2602 | -56.2896 | 0.091933 | -56.3836 | 65.5341 | 65.6983 | 65.6924 | -56.4195 | 0.040156 | -0.11562 | -0.026504 | 0.001985 | -0.038171 | -0.2238 | -0.30658 | -0.11914 | -0.31521 | 0.010743 | -0.083286 | 0.035857 | -0.15097 | -0.15692 | 122.034 | 121.9259 | 121.8431 | 56.3292 | -122.1095 | 121.8345 | 121.9987 | 121.9927 | 56.3923 | -122.2688
1091.9688 | 122.3145 | -56.1813 | 65.918 | 1.4211e-13 | -0.036784 | -0.005797 | 0.064725 | -0.0068542 | 0.054958 | -0.013124 | 0.00014315 | -0.0023288 | -0.0030124 | 0.025474 | -0.012377 | -56.2124 | 0.028878 | -56.1839 | 65.8436 | 65.7171 | 65.6663 | -56.1503 | -56.1751 | 0.091933 | -56.2738 | 65.6577 | 65.8128 | 65.8114 | -56.3004 | 0.031031 | -0.074408 | -0.031064 | -0.002577 | -0.033608 | -0.20088 | -0.25162 | -0.11911 | -0.26025 | 0.006191 | -0.092416 | 0.026697 | -0.10517 | -0.10654 | 122.0249 | 121.8984 | 121.8477 | 56.2102 | -122.0683 | 121.8391 | 121.9941 | 121.9928 | 56.2733 | -122.2184
1093.6562 | 122.2366 | -56.0211 | 66.1285 | 1.4211e-13 | -0.037211 | -0.0060108 | 0.065152 | -0.007068 | 0.055172 | 0.0021363 | 0.00014315 | -0.0021152 | -0.0036534 | 0.025474 | -0.012591 | -56.043 | 0.028878 | -56.0237 | 66.013 | 65.8957 | 65.8312 | -55.9763 | -56.0149 | 0.087354 | -56.1135 | 65.8225 | 65.9868 | 65.9763 | -56.131 | 0.044813 | -0.11558 | -0.02188 | -0.002554 | -0.047367 | -0.23288 | -0.29736 | -0.10991 | -0.306 | 0.006229 | -0.092378 | 0.017535 | -0.14175 | -0.15228 | 122.0341 | 121.9168 | 121.8523 | 56.05 | -122.1048 | 121.8437 | 122.0079 | 121.9974 | 56.1085 | -122.2596
1095.3438 | 122.3511 | -55.9113 | 66.1514 | 1.4211e-13 | -0.037211 | -0.005797 | 0.064938 | -0.0068542 | 0.054958 | -0.0054937 | 0.00057035 | -0.0019016 | -0.003226 | 0.025474 | -0.012377 | -55.9469 | 0.028878 | -55.923 | 66.1091 | 65.9918 | 65.9273 | -55.8756 | -55.905 | 0.087354 | -56.0173 | 65.9187 | 66.0829 | 66.077 | -56.0349 | 0.035686 | -0.04232 | -0.035597 | -0.011695 | -0.047381 | -0.15961 | -0.2241 | -0.12362 | -0.23274 | 0.006255 | -0.10609 | 0.017533 | -0.068487 | -0.074443 | 122.0204 | 121.9031 | 121.8386 | 55.9401 | -122.027 | 121.8299 | 121.9942 | 121.9882 | 55.9986 | -122.1863
1097.0938 | 122.3785 | -55.806 | 66.2476 | 1.4211e-13 | -0.037211 | -0.0060108 | 0.064938 | -0.0072816 | 0.055386 | -0.0054937 | 0.00014315 | -0.0025424 | -0.003226 | 0.02526 | -0.012377 | -55.8599 | 0.033457 | -55.8451 | 66.2007 | 66.088 | 66.0189 | -55.7931 | -55.8317 | 0.087354 | -55.9258 | 66.0011 | 66.1654 | 66.164 | -55.9479 | 0.012821 | -0.046883 | -0.053894 | -0.03915 | -0.051971 | -0.15958 | -0.22866 | -0.14191 | -0.24646 | -0.025771 | -0.1198 | 0.02211 | -0.082203 | -0.083581 | 122.0066 | 121.8939 | 121.8249 | 55.8394 | -122.0407 | 121.8071 | 121.9713 | 121.9699 | 55.8933 | -122.1954
1098.8281 | 122.319 | -55.5405 | 66.5451 | 1.4211e-13 | -0.037211 | -0.005797 | 0.064938 | -0.007068 | 0.054745 | -0.020755 | 0.00035675 | -0.0021152 | -0.003226 | 0.025688 | -0.012591 | -55.5897 | 0.033457 | -55.5658 | 66.4662 | 66.3536 | 66.2845 | -55.523 | -55.557 | 0.096512 | -55.651 | 66.2758 | 66.4401 | 66.4387 | -55.6731 | 0.017475 | -0.078883 | -0.049272 | -0.025378 | -0.042853 | -0.19155 | -0.26065 | -0.13268 | -0.26929 | -0.016552 | -0.11058 | 0.022104 | -0.10503 | -0.10641 | 122.0067 | 121.894 | 121.8249 | 55.5739 | -122.0681 | 121.8163 | 121.9805 | 121.9792 | 55.637 | -122.2183
1100.5938 | 122.3923 | -55.1743 | 66.8701 | 1.4211e-13 | -0.037425 | -0.0062244 | 0.064725 | -0.007068 | 0.055172 | -0.0054937 | 0.00014315 | -0.0021152 | -0.0030124 | 0.025474 | -0.012591 | -55.2693 | 0.042614 | -55.2454 | 66.7913 | 66.6878 | 66.6141 | -55.1887 | -55.2411 | 0.087354 | -55.3397 | 66.5963 | 66.7606 | 66.7592 | -55.3481 | -0.014475 | -0.078829 | -0.094996 | -0.071109 | -0.056634 | -0.1823 | -0.256 | -0.1738 | -0.27381 | -0.066832 | -0.16544 | 0.00836 | -0.10954 | -0.11092 | 121.9655 | 121.8621 | 121.7884 | 55.2169 | -122.0588 | 121.7706 | 121.9348 | 121.9335 | 55.2616 | -122.2182
1102.2812 | 122.2412 | -55.0369 | 67.1082 | 1.4211e-13 | -0.036784 | -0.0062244 | 0.064725 | -0.0068542 | 0.055172 | 0.0021363 | 0.00014315 | -0.0019016 | -0.0034396 | 0.025474 | -0.012804 | -55.0632 | 0.033457 | -55.0485 | 67.0065 | 66.8847 | 66.8247 | -54.9918 | -55.0305 | 0.096512 | -55.1337 | 66.8115 | 66.9712 | 66.9744 | -55.142 | 0.04509 | -0.10168 | -0.026297 | -0.011572 | -0.056662 | -0.22344 | -0.28342 | -0.10508 | -0.29666 | 0.00646 | -0.096726 | 0.008355 | -0.13696 | -0.13376 | 122.0434 | 121.9216 | 121.8617 | 55.0704 | -122.1 | 121.8484 | 122.0081 | 122.0113 | 55.1334 | -122.2502
1104.0312 | 122.3328 | -54.9179 | 67.1356 | 1.4211e-13 | -0.037211 | -0.005797 | 0.064725 | -0.0072816 | 0.055172 | -0.013124 | 0.00035675 | -0.0021152 | -0.003226 | 0.025474 | -0.012804 | -54.9854 | 0.038035 | -54.9569 | 67.0797 | 66.9626 | 66.898 | -54.9094 | -54.948 | 0.091933 | -55.0558 | 66.8848 | 67.049 | 67.0339 | -55.0687 | 0.008493 | -0.055894 | -0.067483 | -0.039024 | -0.047517 | -0.17307 | -0.23763 | -0.15084 | -0.25087 | -0.030141 | -0.13791 | 0.012932 | -0.086594 | -0.10171 | 121.9976 | 121.8805 | 121.8159 | 54.9559 | -122.045 | 121.8027 | 121.9669 | 121.9518 | 55.0098 | -122.2044
1105.7812 | 122.2458 | -54.9316 | 67.1997 | 1.4211e-13 | -0.037425 | -0.0060108 | 0.064725 | -0.007068 | 0.054745 | -0.0054937 | 0.00035675 | -0.0023288 | -0.003226 | 0.02526 | -0.012377 | -54.9717 | 0.0243 | -54.9432 | 67.0935 | 66.99 | 66.9071 | -54.8957 | -54.9389 | 0.096512 | -55.0375 | 66.8985 | 67.0765 | 67.0568 | -55.0504 | 0.035962 | -0.10625 | -0.040015 | -0.011557 | -0.047519 | -0.20968 | -0.29256 | -0.11879 | -0.30122 | -0.007251 | -0.10586 | 0.012931 | -0.12321 | -0.1429 | 122.0251 | 121.9217 | 121.8388 | 54.9559 | -122.0954 | 121.8301 | 122.0081 | 121.9884 | 55.0282 | -122.2501
1107.4844 | 122.2549 | -54.9545 | 67.1768 | 1.4211e-13 | -0.037425 | -0.0060108 | 0.064725 | -0.007068 | 0.055172 | -0.0054937 | 0.00057035 | -0.0025424 | -0.0030124 | 0.026115 | -0.012591 | -55.022 | 0.038035 | -54.9936 | 67.0477 | 66.9351 | 66.8705 | -54.9415 | -54.9893 | 0.091933 | -55.0787 | 66.8573 | 67.0124 | 67.0019 | -55.1008 | 0.013061 | -0.12914 | -0.067489 | -0.03903 | -0.052091 | -0.24174 | -0.3063 | -0.14627 | -0.31954 | -0.034729 | -0.12418 | 0.02209 | -0.16442 | -0.17496 | 122.0022 | 121.8896 | 121.825 | 54.9926 | -122.1183 | 121.8118 | 121.9669 | 121.9564 | 55.0465 | -122.2776
1109.2188 | 122.2641 | -54.8218 | 67.2958 | 1.4211e-13 | -0.037211 | -0.0055834 | 0.064725 | -0.0068542 | 0.055172 | 0.0021363 | 0.00014315 | -0.0019016 | -0.003226 | 0.02526 | -0.012804 | -54.8984 | 0.028878 | -54.8699 | 67.1713 | 67.0587 | 66.9941 | -54.8178 | -54.8702 | 0.091933 | -54.9597 | 66.9763 | 67.1452 | 67.1301 | -54.9726 | 0.00394 | -0.12454 | -0.076624 | -0.048168 | -0.052108 | -0.23713 | -0.3017 | -0.15081 | -0.31951 | -0.048434 | -0.13788 | 0.01293 | -0.15066 | -0.16577 | 121.9931 | 121.8805 | 121.8159 | 54.8507 | -122.1137 | 121.7981 | 121.967 | 121.9518 | 54.9137 | -122.2684
1110.9688 | 122.2458 | -54.7943 | 67.3416 | 1.4211e-13 | -0.037425 | -0.005797 | 0.064511 | -0.007068 | 0.054958 | -0.0054937 | 0.00035675 | -0.0023288 | -0.0036534 | 0.025474 | -0.012591 | -54.8297 | 0.028878 | -54.7967 | 67.2445 | 67.1228 | 67.0628 | -54.7492 | -54.797 | 0.091933 | -54.8864 | 67.045 | 67.2093 | 67.2033 | -54.8993 | 0.045159 | -0.097066 | -0.035413 | -0.002381 | -0.04754 | -0.2188 | -0.27879 | -0.10502 | -0.29661 | -0.00264 | -0.09209 | 0.012928 | -0.13234 | -0.13829 | 122.0389 | 121.9171 | 121.8571 | 54.8232 | -122.0908 | 121.8393 | 122.0036 | 121.9976 | 54.8862 | -122.2409
1112.6719 | 122.287 | -54.6295 | 67.4515 | 1.4211e-13 | -0.037425 | -0.0062244 | 0.064938 | -0.0066406 | 0.054958 | -0.013124 | 0.00035675 | -0.0023288 | -0.003226 | 0.025688 | -0.012377 | -54.7198 | 0.033457 | -54.6914 | 67.359 | 67.2464 | 67.1636 | -54.6347 | -54.6779 | 0.091933 | -54.7857 | 67.1549 | 67.3237 | 67.3132 | -54.794 | -0.005163 | -0.092469 | -0.090327 | -0.061875 | -0.056712 | -0.20503 | -0.28793 | -0.1645 | -0.29659 | -0.048388 | -0.15615 | 0.008347 | -0.12774 | -0.13827 | 121.9885 | 121.876 | 121.7931 | 54.663 | -122.0862 | 121.7844 | 121.9533 | 121.9427 | 54.7214 | -122.2455
1114.4375 | 122.2778 | -54.4373 | 67.6941 | 1.4211e-13 | -0.037425 | -0.005797 | 0.064725 | -0.0072816 | 0.054531 | -0.013124 | 0.00035675 | -0.0021152 | -0.0030124 | 0.025901 | -0.012163 | -54.5321 | 0.042614 | -54.5128 | 67.5467 | 67.4342 | 67.3559 | -54.4469 | -54.4948 | 0.10109 | -54.6025 | 67.3426 | 67.5115 | 67.5009 | -54.6109 | -0.009688 | -0.14737 | -0.094874 | -0.075583 | -0.065895 | -0.25991 | -0.33824 | -0.17361 | -0.35149 | -0.057501 | -0.16527 | 0.008342 | -0.18263 | -0.19316 | 121.984 | 121.8714 | 121.7931 | 54.4799 | -122.141 | 121.7799 | 121.9487 | 121.9382 | 54.5383 | -122.305
1116.125 | 122.3236 | -54.2084 | 67.8772 | 1.4211e-13 | -0.037852 | -0.0060108 | 0.064725 | -0.0072816 | 0.054958 | -0.0054937 | 0.00057035 | -0.0021152 | -0.0034396 | 0.025474 | -0.012804 | -54.2803 | 0.038035 | -54.2656 | 67.7802 | 67.6677 | 67.5985 | -54.2043 | -54.2567 | 0.087354 | -54.3553 | 67.5853 | 67.7587 | 67.7436 | -54.3682 | 0.004113 | -0.096978 | -0.071945 | -0.057238 | -0.061351 | -0.20949 | -0.27868 | -0.15981 | -0.29193 | -0.04829 | -0.1469 | 0.012916 | -0.11849 | -0.1336 | 121.9886 | 121.8761 | 121.8069 | 54.2464 | -122.0815 | 121.7936 | 121.9671 | 121.952 | 54.2957 | -122.2454
1117.875 | 122.2916 | -53.9474 | 68.1702 | 1.4211e-13 | -0.037638 | -0.0060108 | 0.065152 | -0.0068542 | 0.054958 | 0.0021363 | 0.00014315 | -0.0021152 | -0.0030124 | 0.025901 | -0.012377 | -54.0148 | 0.028878 | -53.9818 | 68.0641 | 67.9516 | 67.8732 | -53.9295 | -53.9682 | 0.096512 | -54.076 | 67.8646 | 68.0334 | 68.0229 | -54.0797 | 0.017923 | -0.10609 | -0.067323 | -0.03431 | -0.052233 | -0.21857 | -0.29693 | -0.13227 | -0.30561 | -0.020756 | -0.12852 | 0.003751 | -0.13674 | -0.14727 | 122.0115 | 121.899 | 121.8207 | 53.9763 | -122.0997 | 121.812 | 121.9809 | 121.9703 | 54.044 | -122.2499
1119.625 | 122.2366 | -53.7643 | 68.3578 | 1.4211e-13 | -0.037638 | -0.0062244 | 0.064725 | -0.0072816 | 0.054531 | -0.013124 | 0.00035675 | -0.0019016 | -0.003226 | 0.025901 | -0.012804 | -53.8362 | 0.033457 | -53.7986 | 68.2472 | 68.1348 | 68.0655 | -53.7418 | -53.7988 | 0.096512 | -53.8974 | 68.0477 | 68.212 | 68.2015 | -53.9011 | 0.022553 | -0.11063 | -0.071872 | -0.034284 | -0.056837 | -0.22309 | -0.29232 | -0.1368 | -0.31016 | -0.03445 | -0.13306 | 0.003747 | -0.14586 | -0.15639 | 122.0116 | 121.8991 | 121.8299 | 53.7978 | -122.0996 | 121.812 | 121.9763 | 121.9658 | 53.8609 | -122.259
1121.3125 | 122.3602 | -53.5263 | 68.5043 | 1.4211e-13 | -0.037852 | -0.0062244 | 0.065152 | -0.0072816 | 0.054958 | -0.0054937 | 0.00078395 | -0.0019016 | -0.003226 | 0.025474 | -0.012377 | -53.6302 | 0.042614 | -53.5972 | 68.4532 | 68.3408 | 68.2624 | -53.5541 | -53.5973 | 0.10109 | -53.7051 | 68.2446 | 68.4272 | 68.4075 | -53.7043 | -0.027748 | -0.051091 | -0.10388 | -0.070877 | -0.043129 | -0.16353 | -0.24192 | -0.17795 | -0.25977 | -0.071024 | -0.17879 | -0.000836 | -0.077148 | -0.096839 | 121.9795 | 121.8671 | 121.7887 | 53.5689 | -122.0584 | 121.7709 | 121.9535 | 121.9338 | 53.6274 | -122.2086
1123.0625 | 122.3557 | -53.1876 | 68.8522 | 1.4211e-13 | -0.037425 | -0.0060108 | 0.064938 | -0.007068 | 0.054958 | -0.020755 | 0.00057035 | -0.0021152 | -0.0034396 | 0.025474 | -0.012804 | -53.328 | 0.038035 | -53.2904 | 68.7646 | 68.6522 | 68.56 | -53.2381 | -53.2906 | 0.091933 | -53.3937 | 68.5696 | 68.7294 | 68.7234 | -53.3792 | -0.050547 | -0.087661 | -0.14045 | -0.10288 | -0.05233 | -0.20006 | -0.29221 | -0.1916 | -0.2826 | -0.10299 | -0.20618 | -0.01458 | -0.12286 | -0.12882 | 121.9521 | 121.8397 | 121.7476 | 53.2256 | -122.0903 | 121.7572 | 121.9169 | 121.911 | 53.2795 | -122.2314
1124.8125 | 122.2458 | -52.9678 | 69.1727 | 1.4211e-13 | -0.037638 | -0.0060108 | 0.064511 | -0.0072816 | 0.054958 | -0.013124 | 0.00035675 | -0.0021152 | -0.0027988 | 0.025688 | -0.012591 | -53.0304 | 0.042614 | -53.002 | 69.0576 | 68.9498 | 68.8714 | -52.9359 | -52.9929 | 0.096512 | -53.0961 | 68.8581 | 69.0224 | 69.0164 | -53.0999 | 0.031935 | -0.11508 | -0.062585 | -0.034173 | -0.066108 | -0.22286 | -0.3013 | -0.13202 | -0.31458 | -0.025106 | -0.12829 | 0.003728 | -0.15026 | -0.15622 | 122.0254 | 121.9176 | 121.8392 | 53.0104 | -122.1086 | 121.8259 | 121.9902 | 121.9843 | 53.0643 | -122.2725
1126.5 | 122.3877 | -52.6794 | 69.3741 | 1.4211e-13 | -0.037638 | -0.0060108 | 0.064938 | -0.0066406 | 0.054958 | -0.013124 | 0.00057035 | -0.0021152 | -0.0034396 | 0.025474 | -0.012804 | -52.7786 | 0.042614 | -52.7548 | 69.3094 | 69.1971 | 69.1186 | -52.6978 | -52.7457 | 0.096512 | -52.8489 | 69.1053 | 69.2742 | 69.2637 | -52.8434 | -0.018352 | -0.064683 | -0.099165 | -0.075336 | -0.056984 | -0.17702 | -0.25547 | -0.164 | -0.26876 | -0.066247 | -0.16943 | -0.005435 | -0.099857 | -0.11039 | 121.9888 | 121.8765 | 121.7981 | 52.7221 | -122.0719 | 121.7848 | 121.9537 | 121.9431 | 52.776 | -122.2175
1128.1875 | 122.2504 | -52.4048 | 69.7357 | 1.4211e-13 | -0.037852 | -0.0060108 | 0.064938 | -0.007068 | 0.054958 | -0.013124 | 0.00057035 | -0.0019016 | -0.0034396 | 0.025474 | -0.012591 | -52.4856 | 0.047193 | -52.4435 | 69.6207 | 69.4993 | 69.4208 | -52.3864 | -52.4435 | 0.091933 | -52.5421 | 69.4075 | 69.581 | 69.5705 | -52.5367 | 0.018357 | -0.11499 | -0.080806 | -0.038671 | -0.057028 | -0.23644 | -0.31492 | -0.13188 | -0.32821 | -0.03871 | -0.13732 | -0.005442 | -0.15472 | -0.16526 | 122.0255 | 121.9041 | 121.8256 | 52.452 | -122.1221 | 121.8123 | 121.9858 | 121.9752 | 52.4967 | -122.2724
1129.9531 | 122.2412 | -52.0157 | 70.1202 | 1.4211e-13 | -0.037425 | -0.0060108 | 0.064938 | -0.0074952 | 0.054958 | -0.013124 | 0.00035675 | -0.0021152 | -0.003226 | 0.025688 | -0.013018 | -52.0919 | 0.042614 | -52.0497 | 70.0145 | 69.8976 | 69.8146 | -51.9881 | -52.0497 | 0.096512 | -52.1438 | 69.8058 | 69.9748 | 69.9642 | -52.1383 | 0.027624 | -0.10577 | -0.076164 | -0.034038 | -0.061662 | -0.2226 | -0.30568 | -0.12262 | -0.31441 | -0.03404 | -0.12807 | -0.005451 | -0.14549 | -0.15602 | 122.0302 | 121.9133 | 121.8302 | 52.0583 | -122.1083 | 121.8215 | 121.9904 | 121.9799 | 52.1122 | -122.2585
1131.7031 | 122.2778 | -51.5533 | 70.546 | 1.4211e-13 | -0.037638 | -0.0060108 | 0.064725 | -0.007068 | 0.054958 | -0.020755 | 0.00035675 | -0.0021152 | -0.0030124 | 0.025474 | -0.012591 | -51.6798 | 0.042614 | -51.6514 | 70.4082 | 70.3097 | 70.2221 | -51.5897 | -51.6468 | 0.10567 | -51.7454 | 70.2087 | 70.3777 | 70.3717 | -51.7354 | -0.03635 | -0.13774 | -0.12645 | -0.098069 | -0.061719 | -0.23621 | -0.3239 | -0.18202 | -0.33722 | -0.093455 | -0.19206 | -0.01004 | -0.16829 | -0.17424 | 121.9616 | 121.8631 | 121.7754 | 51.596 | -122.1357 | 121.7621 | 121.931 | 121.9251 | 51.659 | -122.2813
1133.3906 | 122.319 | -51.3657 | 70.7108 | 1.4211e-13 | -0.037852 | -0.005797 | 0.064725 | -0.0072816 | 0.054958 | -0.020755 | 0.00014315 | -0.0021152 | -0.0036534 | 0.02526 | -0.012591 | -51.4463 | 0.038035 | -51.4088 | 70.6554 | 70.5433 | 70.4601 | -51.3424 | -51.4087 | 0.10109 | -51.5119 | 70.4514 | 70.6203 | 70.6098 | -51.4973 | 0.023229 | -0.055307 | -0.080635 | -0.043103 | -0.066332 | -0.16748 | -0.25061 | -0.13161 | -0.25935 | -0.043045 | -0.14623 | -0.014624 | -0.090418 | -0.10095 | 122.0211 | 121.9089 | 121.8258 | 51.4037 | -122.0532 | 121.8171 | 121.986 | 121.9755 | 51.4668 | -122.208
1135.1406 | 122.3419 | -51.0223 | 71.0083 | 1.4211e-13 | -0.037638 | -0.005797 | 0.064725 | -0.007068 | 0.054958 | -0.0054937 | 0.00035675 | -0.0021152 | -0.0030124 | 0.025688 | -0.012591 | -51.1395 | 0.051771 | -51.1112 | 70.9576 | 70.8409 | 70.7578 | -51.0402 | -51.1019 | 0.10567 | -51.2097 | 70.7536 | 70.9225 | 70.912 | -51.1951 | -0.017885 | -0.050681 | -0.11721 | -0.088838 | -0.070953 | -0.1674 | -0.25055 | -0.17273 | -0.25472 | -0.079594 | -0.18736 | -0.014632 | -0.085777 | -0.096312 | 121.98 | 121.8632 | 121.7801 | 51.0741 | -122.0485 | 121.7759 | 121.9449 | 121.9343 | 51.128 | -122.2034
1136.8906 | 122.3511 | -50.6653 | 71.4203 | 1.4211e-13 | -0.037425 | -0.0062244 | 0.064938 | -0.0068542 | 0.054958 | -0.0054937 | 0.00035675 | -0.0021152 | -0.003226 | 0.025474 | -0.012804 | -50.7687 | 0.042614 | -50.7358 | 71.3285 | 71.221 | 71.1424 | -50.6785 | -50.7356 | 0.11483 | -50.8388 | 71.1199 | 71.2934 | 71.2874 | -50.8196 | -0.013206 | -0.091818 | -0.10341 | -0.070475 | -0.057269 | -0.19934 | -0.27793 | -0.15432 | -0.30043 | -0.070353 | -0.17354 | -0.019219 | -0.1269 | -0.13285 | 121.9938 | 121.8862 | 121.8076 | 50.7079 | -122.0988 | 121.7851 | 121.9587 | 121.9527 | 50.7801 | -122.2399
1138.6406 | 122.3099 | -50.267 | 71.8094 | 1.4211e-13 | -0.038066 | -0.005797 | 0.064938 | -0.007068 | 0.054958 | -0.0054937 | 0.00035675 | -0.0021152 | -0.0030124 | 0.025688 | -0.012591 | -50.3933 | 0.038035 | -50.3558 | 71.7131 | 71.601 | 71.5178 | -50.2893 | -50.3556 | 0.10567 | -50.4542 | 71.509 | 71.6734 | 71.672 | -50.4396 | -0.022252 | -0.096333 | -0.12624 | -0.088731 | -0.066479 | -0.20839 | -0.29159 | -0.17253 | -0.30035 | -0.088574 | -0.18718 | -0.014648 | -0.13597 | -0.13735 | 121.9801 | 121.868 | 121.7848 | 50.3051 | -122.0987 | 121.7761 | 121.9404 | 121.9391 | 50.3727 | -122.2489
1140.3281 | 122.2458 | -49.9466 | 72.1893 | 1.4211e-13 | -0.037638 | -0.0060108 | 0.064938 | -0.007068 | 0.054958 | -0.013124 | 0.00057035 | -0.0023288 | -0.0030124 | 0.025688 | -0.013018 | -50.0728 | 0.047193 | -50.0261 | 72.0381 | 71.9307 | 71.8475 | -49.9504 | -50.0305 | 0.10567 | -50.1291 | 71.8387 | 72.0168 | 71.9971 | -50.1053 | -0.003846 | -0.15121 | -0.12619 | -0.07953 | -0.075684 | -0.25865 | -0.34187 | -0.15871 | -0.35065 | -0.083921 | -0.18253 | -0.023814 | -0.17252 | -0.19221 | 121.9847 | 121.8773 | 121.7941 | 49.9938 | -122.1398 | 121.7853 | 121.9634 | 121.9437 | 50.0523 | -122.2946
1142.0625 | 122.2275 | -49.5163 | 72.6196 | 1.4211e-13 | -0.038066 | -0.0060108 | 0.064938 | -0.007068 | 0.054958 | 0.0021363 | 0.00057035 | -0.0016878 | -0.003226 | 0.025688 | -0.012804 | -49.6241 | 0.051771 | -49.5775 | 72.4868 | 72.3886 | 72.3053 | -49.5109 | -49.5772 | 0.10567 | -49.685 | 72.2828 | 72.4518 | 72.455 | -49.6657 | 0.005433 | -0.13283 | -0.1078 | -0.061157 | -0.06659 | -0.23105 | -0.31431 | -0.14945 | -0.33683 | -0.060927 | -0.16869 | -0.019246 | -0.16785 | -0.16465 | 122.0031 | 121.9049 | 121.8216 | 49.5681 | -122.1305 | 121.7991 | 121.9681 | 121.9713 | 49.622 | -122.2854
1143.8125 | 122.319 | -48.9441 | 73.114 | 1.4211e-13 | -0.038066 | -0.0060108 | 0.064938 | -0.007068 | 0.054958 | 0.0021363 | 0.00057035 | -0.0021152 | -0.003226 | 0.025688 | -0.012804 | -49.0518 | 0.047193 | -49.0189 | 73.0591 | 72.9472 | 72.8593 | -48.9522 | -49.0186 | 0.11025 | -49.1264 | 72.8505 | 73.0287 | 73.0136 | -49.098 | -0.008143 | -0.054913 | -0.10771 | -0.074811 | -0.066668 | -0.16681 | -0.25468 | -0.15388 | -0.26348 | -0.074528 | -0.18229 | -0.028417 | -0.085333 | -0.10045 | 122.0032 | 121.8913 | 121.8034 | 48.9913 | -122.0662 | 121.7946 | 121.9728 | 121.9577 | 49.0543 | -122.212
1145.5625 | 122.2412 | -48.4955 | 73.6816 | 1.4211e-13 | -0.038279 | -0.0062244 | 0.064725 | -0.007068 | 0.054958 | -0.0054937 | 0.00057035 | -0.0019016 | -0.0030124 | 0.025688 | -0.012804 | -48.6031 | 0.05635 | -48.5611 | 73.5215 | 73.4097 | 73.3126 | -48.4806 | -48.5653 | 0.11483 | -48.6685 | 73.313 | 73.4911 | 73.476 | -48.6355 | 0.014878 | -0.16012 | -0.10764 | -0.065592 | -0.08047 | -0.27196 | -0.36903 | -0.14003 | -0.36868 | -0.069845 | -0.17303 | -0.033006 | -0.19052 | -0.20563 | 122.017 | 121.9052 | 121.8081 | 48.5518 | -122.1622 | 121.8084 | 121.9866 | 121.9715 | 48.6103 | -122.3171
1147.25 | 122.2321 | -47.9462 | 74.231 | 1.4211e-13 | -0.038066 | -0.0062244 | 0.064938 | -0.0072816 | 0.054958 | -0.0054937 | 0.00014315 | -0.0021152 | -0.003226 | 0.025688 | -0.013445 | -48.0629 | 0.047193 | -48.0254 | 74.0618 | 73.9591 | 73.8666 | -47.9449 | -48.025 | 0.1194 | -48.1282 | 73.8486 | 74.0222 | 74.0117 | -48.0906 | 0.001296 | -0.16919 | -0.1167 | -0.079249 | -0.080545 | -0.27181 | -0.36433 | -0.14446 | -0.38231 | -0.078873 | -0.18206 | -0.037598 | -0.20872 | -0.21925 | 122.0079 | 121.9053 | 121.8128 | 47.9934 | -122.1758 | 121.7948 | 121.9684 | 121.9579 | 48.0656 | -122.3216
1148.9844 | 122.2275 | -47.4289 | 74.7162 | 1.4211e-13 | -0.038279 | -0.0062244 | 0.064938 | -0.007068 | 0.054958 | 0.0021363 | 0.00035675 | -0.0019016 | -0.0034396 | 0.025688 | -0.012804 | -47.518 | 0.051771 | -47.476 | 74.6249 | 74.504 | 74.4161 | -47.3817 | -47.4756 | 0.11025 | -47.5742 | 74.4026 | 74.5808 | 74.5703 | -47.5366 | 0.047231 | -0.091278 | -0.089146 | -0.047128 | -0.094359 | -0.21215 | -0.30013 | -0.1077 | -0.31355 | -0.046701 | -0.14531 | -0.037611 | -0.13536 | -0.14589 | 122.0538 | 121.9329 | 121.8449 | 47.4807 | -122.0979 | 121.8315 | 122.0097 | 121.9992 | 47.5391 | -122.2528
1150.7344 | 122.2733 | -46.7743 | 75.3616 | 1.4211e-13 | -0.038066 | -0.0060108 | 0.064938 | -0.0072816 | 0.054745 | -0.0054937 | 0.00035675 | -0.0019016 | -0.0030124 | 0.025901 | -0.012804 | -46.8679 | 0.05635 | -46.8305 | 75.2796 | 75.1542 | 75.0708 | -46.736 | -46.83 | 0.1194 | -46.9332 | 75.0574 | 75.2401 | 75.2205 | -46.8864 | 0.038257 | -0.082014 | -0.093617 | -0.056192 | -0.094449 | -0.20739 | -0.29084 | -0.11211 | -0.30427 | -0.055705 | -0.15889 | -0.046784 | -0.12149 | -0.14118 | 122.0539 | 121.9285 | 121.8451 | 46.8306 | -122.0977 | 121.8317 | 122.0144 | 121.9947 | 46.8937 | -122.248
1152.4219 | 122.3602 | -46.1288 | 75.9247 | 1.4211e-13 | -0.038279 | -0.0060108 | 0.064511 | -0.0074952 | 0.054531 | 0.0021363 | 0.00035675 | -0.0019016 | -0.003226 | 0.025688 | -0.013018 | -46.3093 | 0.05635 | -46.2811 | 75.8382 | 75.7175 | 75.6248 | -46.1728 | -46.2714 | 0.1194 | -46.37 | 75.6205 | 75.7942 | 75.7928 | -46.3232 | -0.043982 | -0.086501 | -0.1805 | -0.15225 | -0.10826 | -0.20723 | -0.29988 | -0.19436 | -0.30416 | -0.14255 | -0.24116 | -0.046796 | -0.13053 | -0.1319 | 121.967 | 121.8463 | 121.7537 | 46.1852 | -122.0975 | 121.7494 | 121.923 | 121.9216 | 46.2482 | -122.2479
1154.1094 | 122.2321 | -45.5978 | 76.5335 | 1.4211e-13 | -0.038066 | -0.0060108 | 0.064938 | -0.0074952 | 0.054745 | -0.0054937 | 0.00035675 | -0.0021152 | -0.003226 | 0.026115 | -0.012804 | -45.7325 | 0.060928 | -45.6905 | 76.4196 | 76.3036 | 76.2063 | -45.5867 | -45.6853 | 0.12398 | -45.7977 | 76.1974 | 76.3802 | 76.3605 | -45.7371 | 0.011114 | -0.11387 | -0.13463 | -0.092654 | -0.10377 | -0.22995 | -0.32722 | -0.13928 | -0.3361 | -0.08748 | -0.19982 | -0.060547 | -0.15329 | -0.17298 | 122.0175 | 121.9014 | 121.8041 | 45.6588 | -122.1202 | 121.7953 | 121.9781 | 121.9584 | 45.7218 | -122.2706
1155.8594 | 122.3465 | -44.8883 | 77.1927 | 1.4211e-13 | -0.038493 | -0.0060108 | 0.064938 | -0.0074952 | 0.054958 | -0.0054937 | 0.00014315 | -0.0016878 | -0.003226 | 0.026115 | -0.013232 | -45.0411 | 0.05635 | -45.0083 | 77.1156 | 76.9904 | 76.9022 | -44.9045 | -45.0031 | 0.12856 | -45.1154 | 76.8979 | 77.067 | 77.0656 | -45.0503 | -0.016159 | -0.077136 | -0.15283 | -0.12002 | -0.10386 | -0.20229 | -0.29045 | -0.16199 | -0.29477 | -0.11479 | -0.22713 | -0.065141 | -0.12568 | -0.12706 | 122.0039 | 121.8787 | 121.7905 | 44.9447 | -122.0972 | 121.7862 | 121.9553 | 121.9539 | 45.0169 | -122.243
1157.6094 | 122.3373 | -44.101 | 78.0304 | 1.4211e-13 | -0.038066 | -0.005797 | 0.064938 | -0.007068 | 0.054531 | -0.0054937 | 0.00057035 | -0.0019016 | -0.0030124 | 0.025901 | -0.013445 | -44.2903 | 0.065507 | -44.2529 | 77.8664 | 77.7413 | 77.6577 | -44.1444 | -44.2522 | 0.12398 | -44.3599 | 77.6488 | 77.8271 | 77.8119 | -44.2948 | -0.043412 | -0.16399 | -0.18933 | -0.15196 | -0.10855 | -0.28906 | -0.37269 | -0.19384 | -0.3816 | -0.15123 | -0.259 | -0.065159 | -0.20334 | -0.21845 | 121.9674 | 121.8423 | 121.7587 | 44.1665 | -122.1748 | 121.7497 | 121.928 | 121.9129 | 44.2249 | -122.3252
1159.2969 | 122.3236 | -43.309 | 78.7811 | 1.4211e-13 | -0.038066 | -0.0060108 | 0.064938 | -0.007068 | 0.054745 | -0.0054937 | 0.00035675 | -0.0019016 | -0.0034396 | 0.025688 | -0.013018 | -43.4479 | 0.065507 | -43.4014 | 78.7271 | 78.6022 | 78.5093 | -43.2881 | -43.396 | 0.12856 | -43.5083 | 78.505 | 78.6833 | 78.6727 | -43.4431 | 0.020916 | -0.053983 | -0.13883 | -0.092331 | -0.11325 | -0.17895 | -0.2718 | -0.13411 | -0.27615 | -0.086943 | -0.19929 | -0.065179 | -0.097873 | -0.10841 | 122.0362 | 121.9112 | 121.8183 | 43.3745 | -122.0692 | 121.814 | 121.9923 | 121.9817 | 43.4376 | -122.2243
1161.0625 | 122.3557 | -42.2928 | 79.7745 | 1.4211e-13 | -0.038279 | -0.0062244 | 0.065366 | -0.0074952 | 0.054958 | -0.013124 | 0.00014315 | -0.0021152 | -0.003226 | 0.026115 | -0.013232 | -42.4269 | 0.070086 | -42.3896 | 79.7435 | 79.6233 | 79.5166 | -42.2716 | -42.3886 | 0.13772 | -42.5101 | 79.5122 | 79.7089 | 79.68 | -42.4221 | 0.021202 | -0.030928 | -0.13409 | -0.096766 | -0.11797 | -0.1512 | -0.25786 | -0.12927 | -0.26223 | -0.095862 | -0.21736 | -0.088096 | -0.065613 | -0.094462 | 122.0363 | 121.9161 | 121.8094 | 42.3629 | -122.0461 | 121.805 | 122.0016 | 121.9728 | 42.4305 | -122.1965
1162.8125 | 122.319 | -41.2582 | 80.8411 | 1.4211e-13 | -0.038279 | -0.006438 | 0.064725 | -0.007068 | 0.054531 | -0.0054937 | 0.00035675 | -0.0019016 | -0.0030124 | 0.025474 | -0.013018 | -41.47 | 0.074664 | -41.4281 | 80.7187 | 80.5894 | 80.4919 | -41.3009 | -41.418 | 0.13772 | -41.5395 | 80.4783 | 80.6749 | 80.669 | -41.4513 | -0.042612 | -0.12232 | -0.21175 | -0.16987 | -0.12726 | -0.25163 | -0.3492 | -0.1931 | -0.36276 | -0.15972 | -0.28122 | -0.088119 | -0.16612 | -0.17207 | 121.977 | 121.8477 | 121.7501 | 41.3329 | -122.1419 | 121.7365 | 121.9332 | 121.9272 | 41.396 | -122.2924
1164.5781 | 122.2092 | -40.2832 | 81.8802 | 1.4211e-13 | -0.038493 | -0.0055834 | 0.064938 | -0.007068 | 0.054745 | 0.0021363 | 0.00057035 | -0.0019016 | -0.0030124 | 0.025474 | -0.013232 | -40.449 | 0.079243 | -40.4026 | 81.7489 | 81.6197 | 81.5175 | -40.2752 | -40.4015 | 0.13314 | -40.5184 | 81.5085 | 81.7006 | 81.6854 | -40.4211 | 0.00803 | -0.13131 | -0.16581 | -0.11938 | -0.12741 | -0.2605 | -0.36272 | -0.13791 | -0.37172 | -0.11829 | -0.23521 | -0.0973 | -0.17963 | -0.19475 | 122.0321 | 121.9029 | 121.8007 | 40.3624 | -122.1554 | 121.7917 | 121.9838 | 121.9686 | 40.4163 | -122.3013
1166.2656 | 122.2504 | -39.3036 | 82.8598 | 1.4211e-13 | -0.038493 | -0.0062244 | 0.065152 | -0.0072816 | 0.054745 | -0.0054937 | 0.00057035 | -0.0016878 | -0.003226 | 0.025688 | -0.013018 | -39.5013 | 0.083821 | -39.4595 | 82.6966 | 82.5675 | 82.4698 | -39.3182 | -39.4491 | 0.15146 | -39.566 | 82.4654 | 82.6621 | 82.6469 | -39.4687 | -0.014588 | -0.1632 | -0.19769 | -0.15586 | -0.14128 | -0.29228 | -0.38998 | -0.16513 | -0.39443 | -0.14553 | -0.26245 | -0.097322 | -0.19774 | -0.21285 | 122.0002 | 121.8711 | 121.7734 | 39.3874 | -122.178 | 121.769 | 121.9656 | 121.9505 | 39.455 | -122.3285
1168.0156 | 122.2778 | -38.1775 | 83.9905 | 1.4211e-13 | -0.038493 | -0.0060108 | 0.064938 | -0.007709 | 0.054531 | -0.013124 | 0.00014315 | -0.0021152 | -0.0030124 | 0.025901 | -0.013232 | -38.3704 | 0.079243 | -38.3424 | 83.832 | 83.7031 | 83.6053 | -38.1918 | -38.3228 | 0.15146 | -38.4443 | 83.5963 | 83.7884 | 83.7687 | -38.3332 | -0.014272 | -0.15843 | -0.19293 | -0.16486 | -0.15059 | -0.28738 | -0.38517 | -0.15568 | -0.39422 | -0.14526 | -0.26676 | -0.11109 | -0.20208 | -0.22177 | 122.0095 | 121.8806 | 121.7828 | 38.2567 | -122.1822 | 121.7738 | 121.9659 | 121.9462 | 38.3289 | -122.3236
1169.75 | 122.2183 | -37.0743 | 85.1074 | 1.4211e-13 | -0.038707 | -0.0060108 | 0.064511 | -0.0072816 | 0.054531 | -0.013124 | 0.00035675 | -0.0016878 | -0.003226 | 0.026115 | -0.013018 | -37.267 | 0.083821 | -37.2344 | 84.9446 | 84.8112 | 84.7088 | -37.0791 | -37.2147 | 0.15604 | -37.3408 | 84.7134 | 84.9102 | 84.8813 | -37.2297 | -0.004803 | -0.16283 | -0.19275 | -0.16013 | -0.15533 | -0.29622 | -0.39867 | -0.15539 | -0.39401 | -0.14043 | -0.2665 | -0.11111 | -0.19727 | -0.22612 | 122.0189 | 121.8855 | 121.783 | 37.1581 | -122.1865 | 121.7877 | 121.9844 | 121.9556 | 37.2303 | -122.3371
1171.4531 | 122.2275 | -35.9573 | 86.2244 | 1.4211e-13 | -0.038279 | -0.0060108 | 0.065366 | -0.0074952 | 0.054531 | -0.013124 | 0.00057035 | -0.0019016 | -0.003226 | 0.026115 | -0.013445 | -36.1636 | 0.079243 | -36.1402 | 86.0526 | 85.9239 | 85.8168 | -35.9801 | -36.1204 | 0.15146 | -36.2511 | 85.8168 | 86.0182 | 85.9893 | -36.1216 | -0.022805 | -0.1718 | -0.2063 | -0.18286 | -0.16006 | -0.30049 | -0.40759 | -0.16426 | -0.40754 | -0.16306 | -0.29372 | -0.12945 | -0.20619 | -0.23504 | 122.0099 | 121.8812 | 121.7741 | 36.0366 | -122.2045 | 121.7742 | 121.9755 | 121.9467 | 36.1088 | -122.346
1173.1875 | 122.3236 | -34.8816 | 87.2406 | 1.4211e-13 | -0.038707 | -0.0062244 | 0.064938 | -0.0074952 | 0.054531 | -0.013124 | -7.0448e-05 | -0.0023288 | -0.003226 | 0.025901 | -0.013232 | -35.0877 | 0.083821 | -35.0506 | 87.1376 | 86.9953 | 86.8882 | -34.9041 | -35.049 | 0.15604 | -35.1613 | 86.8928 | 87.0941 | 87.0745 | -35.0456 | -0.022502 | -0.10296 | -0.20613 | -0.16898 | -0.14648 | -0.24526 | -0.35243 | -0.16399 | -0.34782 | -0.16738 | -0.27973 | -0.11574 | -0.14645 | -0.16615 | 122.0192 | 121.8769 | 121.7698 | 34.9654 | -122.1447 | 121.7744 | 121.9757 | 121.956 | 35.0376 | -122.2862
1174.9219 | 122.3557 | -29.6402 | 92.5003 | 1.4211e-13 | -0.038493 | -0.005797 | 0.064938 | -0.0074952 | 0.054745 | 0.0021363 | 0.00057035 | -0.0019016 | -0.0030124 | 0.026115 | -0.013232 | -32.8901 | 0.19371 | -32.8805 | 89.3215 | 89.1841 | 89.063 | -32.6696 | -32.8283 | 0.26592 | -32.9544 | 89.1042 | 89.2919 | 89.2951 | -32.8111 | -3.0294 | -3.1788 | -3.2499 | -3.2403 | -0.21089 | -3.3162 | -3.4373 | -3.1709 | -3.3961 | -3.1881 | -3.3142 | -0.14327 | -3.2084 | -3.2052 | 118.9617 | 118.8243 | 118.7032 | 29.8339 | -125.1699 | 118.7444 | 118.9321 | 118.9353 | 29.9061 | -125.3114
1176.7031 | 122.1909 | -20.6772 | 101.5778 | 1.4211e-13 | -0.038707 | -0.0060108 | 0.064938 | -0.0072816 | 0.054531 | -0.0054937 | 0.00057035 | -0.0019016 | -0.0027988 | 0.026329 | -0.013445 | -20.8993 | 0.1525 | -20.9083 | 101.3673 | 101.2037 | 101.0681 | -20.7003 | -20.8504 | 0.24303 | -21.0085 | 101.0907 | 101.3061 | 101.2864 | -20.778 | -0.023085 | -0.21049 | -0.22211 | -0.23107 | -0.20799 | -0.37401 | -0.50966 | -0.1008 | -0.48707 | -0.17321 | -0.33134 | -0.23054 | -0.27163 | -0.29132 | 122.0445 | 121.8809 | 121.7453 | 20.8297 | -122.278 | 121.7679 | 121.9833 | 121.9636 | 20.9202 | -122.3557
1178.3906 | 122.3419 | -19.0521 | 103.1021 | 1.4211e-13 | -0.038707 | -0.0060108 | 0.065152 | -0.0072816 | 0.054531 | 0.0021363 | 0.00078395 | -0.0016878 | -0.0030124 | 0.025688 | -0.013659 | -19.3152 | 0.14334 | -19.3288 | 102.9422 | 102.7697 | 102.6431 | -19.1205 | -19.2753 | 0.23387 | -19.4289 | 102.6611 | 102.8903 | 102.8477 | -19.2029 | -0.068417 | -0.15987 | -0.26305 | -0.27663 | -0.20821 | -0.33237 | -0.45897 | -0.15075 | -0.441 | -0.2232 | -0.37675 | -0.226 | -0.21179 | -0.25437 | 121.9944 | 121.8219 | 121.6953 | 19.1955 | -122.2227 | 121.7132 | 121.9425 | 121.8999 | 19.286 | -122.305
1180.1406 | 122.3099 | -17.8711 | 104.2648 | 1.4211e-13 | -0.038493 | -0.0060108 | 0.064938 | -0.0072816 | 0.054531 | -0.0054937 | 0.00035675 | -0.0019016 | -0.0030124 | 0.025901 | -0.013659 | -18.0927 | 0.13876 | -18.1201 | 104.1738 | 103.9923 | 103.8565 | -17.9209 | -18.0574 | 0.22929 | -18.2109 | 103.8698 | 104.0991 | 104.0611 | -17.9941 | -0.049769 | -0.091008 | -0.22165 | -0.24899 | -0.19922 | -0.27252 | -0.40836 | -0.12297 | -0.39499 | -0.18629 | -0.33984 | -0.21687 | -0.16575 | -0.20376 | 122.0449 | 121.8634 | 121.7276 | 18.0099 | -122.1857 | 121.7409 | 121.9702 | 121.9322 | 18.1004 | -122.2589
1181.875 | 122.3099 | -17.0151 | 105.162 | 1.4211e-13 | -0.038493 | -0.0060108 | 0.065366 | -0.0072816 | 0.054531 | -0.0054937 | 0.00057035 | -0.0019016 | -0.0030124 | 0.025901 | -0.013659 | -17.2183 | 0.13876 | -17.2411 | 105.0437 | 104.8715 | 104.731 | -17.0417 | -17.1783 | 0.22472 | -17.3318 | 104.7489 | 104.9782 | 104.9539 | -17.1195 | -0.026633 | -0.11833 | -0.20319 | -0.22598 | -0.19935 | -0.29058 | -0.43107 | -0.10443 | -0.41314 | -0.1632 | -0.31675 | -0.21231 | -0.18388 | -0.20815 | 122.0588 | 121.8865 | 121.7461 | 17.1538 | -122.2038 | 121.764 | 121.9932 | 121.969 | 17.2398 | -122.2816
1183.625 | 122.319 | -16.3925 | 105.7571 | 1.4211e-13 | -0.038707 | -0.0060108 | 0.064938 | -0.0074952 | 0.054531 | -0.0054937 | 0.00078395 | -0.0019016 | -0.003226 | 0.026115 | -0.013018 | -16.5498 | 0.12961 | -16.5772 | 105.6984 | 105.5354 | 105.3995 | -16.3778 | -16.5144 | 0.21556 | -16.6679 | 105.4128 | 105.6466 | 105.6086 | -16.4647 | 0.014752 | -0.058713 | -0.15731 | -0.18469 | -0.19944 | -0.22173 | -0.35768 | -0.072221 | -0.34435 | -0.12184 | -0.27539 | -0.20317 | -0.1105 | -0.1485 | 122.0909 | 121.9279 | 121.792 | 16.5221 | -122.1349 | 121.8053 | 122.0392 | 122.0012 | 16.6081 | -122.2219
1185.3594 | 122.3236 | -15.9485 | 106.2286 | 1.4211e-13 | -0.038921 | -0.005797 | 0.064725 | -0.0079226 | 0.054317 | -0.0054937 | 0.00035675 | -0.0014742 | -0.0027988 | 0.026115 | -0.013445 | -16.1011 | 0.13419 | -16.1285 | 106.1563 | 105.9887 | 105.8527 | -15.9428 | -16.0611 | 0.22472 | -16.2192 | 105.8569 | 106.0953 | 106.0665 | -16.0069 | 0.005718 | -0.072372 | -0.15266 | -0.18005 | -0.18577 | -0.23991 | -0.3759 | -0.05837 | -0.37173 | -0.11258 | -0.27071 | -0.21234 | -0.13329 | -0.16214 | 122.1048 | 121.9372 | 121.8012 | 16.0827 | -122.1714 | 121.8054 | 122.0438 | 122.015 | 16.1732 | -122.2355
1187.0469 | 122.374 | -15.3534 | 106.8054 | 1.4211e-13 | -0.038707 | -0.0060108 | 0.064938 | -0.007068 | 0.054317 | -0.0054937 | 0.00057035 | -0.0016878 | -0.0030124 | 0.025688 | -0.013445 | -15.4739 | 0.13419 | -15.5013 | 106.7698 | 106.5977 | 106.4571 | -15.3246 | -15.4338 | 0.22014 | -15.6011 | 106.4704 | 106.7043 | 106.6755 | -15.3933 | 0.028781 | -0.03565 | -0.12051 | -0.14792 | -0.1767 | -0.2077 | -0.3483 | -0.039901 | -0.335 | -0.080389 | -0.24768 | -0.20778 | -0.10112 | -0.12997 | 122.1232 | 121.9511 | 121.8105 | 15.4876 | -122.13 | 121.8238 | 122.0577 | 122.0288 | 15.5735 | -122.1987
1188.7812 | 122.2504 | -14.9414 | 107.2952 | 1.4211e-13 | -0.038921 | -0.0060108 | 0.065366 | -0.007709 | 0.054317 | -0.0054937 | 0.00035675 | -0.0019016 | -0.0027988 | 0.025901 | -0.013232 | -15.0161 | 0.12503 | -15.0526 | 107.223 | 107.0465 | 106.9104 | -14.8667 | -14.9759 | 0.22014 | -15.1478 | 106.9237 | 107.1622 | 107.1196 | -14.9354 | 0.074686 | -0.072196 | -0.074659 | -0.11123 | -0.18592 | -0.24877 | -0.38483 | 0.005993 | -0.37153 | -0.034506 | -0.20637 | -0.21237 | -0.13306 | -0.17565 | 122.1644 | 121.9879 | 121.8518 | 15.0664 | -122.1619 | 121.8651 | 122.1036 | 122.061 | 15.1615 | -122.2306
1190.5312 | 122.2412 | -14.534 | 107.6935 | 1.4211e-13 | -0.038921 | -0.0062244 | 0.065152 | -0.0074952 | 0.054531 | -0.0054937 | 0.00057035 | -0.0019016 | -0.003226 | 0.025688 | -0.013659 | -14.6406 | 0.12961 | -14.6635 | 107.6122 | 107.4357 | 107.2996 | -14.4821 | -14.5913 | 0.21556 | -14.754 | 107.3174 | 107.5468 | 107.4996 | -14.5462 | 0.051906 | -0.081287 | -0.10664 | -0.12949 | -0.18139 | -0.25782 | -0.3939 | -0.012217 | -0.37604 | -0.057304 | -0.22001 | -0.2078 | -0.14672 | -0.19388 | 122.1462 | 121.9697 | 121.8336 | 14.6636 | -122.1756 | 121.8514 | 122.0808 | 122.0336 | 14.7496 | -122.2397
1192.2188 | 122.3557 | -14.1449 | 108.0231 | 1.4211e-13 | -0.038707 | -0.005797 | 0.065152 | -0.0072816 | 0.054317 | -0.0054937 | 0.00099775 | -0.0019016 | -0.003226 | 0.025688 | -0.013659 | -14.2789 | 0.12503 | -14.311 | 107.9647 | 107.7882 | 107.6521 | -14.1387 | -14.2387 | 0.22014 | -14.4014 | 107.6563 | 107.8993 | 107.8613 | -14.2028 | 0.006226 | -0.058341 | -0.13405 | -0.16606 | -0.17229 | -0.23483 | -0.37094 | -0.057905 | -0.36682 | -0.093843 | -0.25655 | -0.19865 | -0.12375 | -0.16176 | 122.1096 | 121.9331 | 121.797 | 14.2699 | -122.1617 | 121.8011 | 122.0442 | 122.0062 | 14.365 | -122.2259
1193.9688 | 122.3648 | -13.8977 | 108.2428 | 1.4211e-13 | -0.038707 | -0.0062244 | 0.064938 | -0.007709 | 0.054317 | -0.020755 | 0.00035675 | -0.0019016 | -0.0030124 | 0.025901 | -0.013873 | -13.9997 | 0.12045 | -14.0363 | 108.244 | 108.063 | 107.9268 | -13.8594 | -13.964 | 0.22014 | -14.1267 | 107.9447 | 108.1786 | 108.136 | -13.9281 | 0.038348 | 0.001213 | -0.10196 | -0.13856 | -0.1769 | -0.17982 | -0.31595 | -0.030368 | -0.2981 | -0.066312 | -0.22902 | -0.19865 | -0.064186 | -0.10677 | 122.1417 | 121.9607 | 121.8246 | 14.0182 | -122.1022 | 121.8424 | 122.0763 | 122.0337 | 14.1178 | -122.1709
1195.7344 | 122.3419 | -13.4583 | 108.6868 | 1.4211e-13 | -0.038707 | -0.0055834 | 0.065152 | -0.0074952 | 0.054104 | -0.0054937 | 0.00057035 | -0.0019016 | -0.0027988 | 0.026329 | -0.013445 | -13.5922 | 0.13419 | -13.6334 | 108.6423 | 108.4705 | 108.3252 | -13.461 | -13.5519 | 0.22014 | -13.7238 | 108.343 | 108.577 | 108.5435 | -13.5297 | -0.002738 | -0.044498 | -0.13393 | -0.17512 | -0.17238 | -0.21633 | -0.36164 | -0.071464 | -0.3438 | -0.093682 | -0.26555 | -0.19408 | -0.10988 | -0.14331 | 122.1006 | 121.9288 | 121.7834 | 13.5924 | -122.1478 | 121.8013 | 122.0352 | 122.0018 | 13.6784 | -122.2165
1197.4062 | 122.3053 | -13.3667 | 108.7784 | 1.4211e-13 | -0.039134 | -0.005797 | 0.064938 | -0.007709 | 0.054531 | -0.013124 | 0.00057035 | -0.0016878 | -0.0030124 | 0.026115 | -0.013659 | -13.464 | 0.13419 | -13.5006 | 108.7797 | 108.6033 | 108.4625 | -13.3374 | -13.4237 | 0.22929 | -13.5864 | 108.4758 | 108.7097 | 108.6626 | -13.4015 | 0.029339 | 0.001302 | -0.097292 | -0.1339 | -0.16324 | -0.17509 | -0.31584 | -0.03481 | -0.30258 | -0.057031 | -0.21974 | -0.18493 | -0.068651 | -0.11581 | 122.1464 | 121.97 | 121.8292 | 13.5009 | -122.1157 | 121.8425 | 122.0764 | 122.0293 | 13.596 | -122.1799
1199.1562 | 122.3694 | -13.0142 | 109.1629 | 1.4211e-13 | -0.038921 | -0.0062244 | 0.065152 | -0.0074952 | 0.054317 | -0.0054937 | 0.00099775 | -0.0019016 | -0.0030124 | 0.026115 | -0.013445 | -13.1069 | 0.12961 | -13.1481 | 109.1185 | 108.9421 | 108.8014 | -12.9802 | -13.0757 | 0.22472 | -13.2339 | 108.8238 | 109.0531 | 109.0197 | -13.0489 | 0.034018 | -0.04442 | -0.092656 | -0.13385 | -0.16787 | -0.22077 | -0.36154 | -0.034719 | -0.33913 | -0.061527 | -0.21966 | -0.18494 | -0.10978 | -0.1432 | 122.1327 | 121.9564 | 121.8156 | 13.1438 | -122.1431 | 121.838 | 122.0673 | 122.0339 | 13.2389 | -122.2118
1200.8438 | 122.3053 | -12.6663 | 109.4925 | 1.4211e-13 | -0.038921 | -0.0060108 | 0.065366 | -0.0072816 | 0.054104 | 0.0021363 | 0.00099775 | -0.0021152 | -0.0027988 | 0.026115 | -0.013445 | -12.7452 | 0.12961 | -12.7864 | 109.4756 | 109.313 | 109.1676 | -12.623 | -12.7095 | 0.22472 | -12.8722 | 109.1717 | 109.4286 | 109.3814 | -12.6918 | 0.043274 | -0.016895 | -0.078863 | -0.12007 | -0.16334 | -0.17947 | -0.32484 | -0.025472 | -0.32076 | -0.04313 | -0.20584 | -0.18037 | -0.063922 | -0.11109 | 122.1419 | 121.9793 | 121.834 | 12.7959 | -122.1155 | 121.8381 | 122.0949 | 122.0477 | 12.891 | -122.1843
1202.5781 | 122.3373 | -12.2681 | 109.8679 | 1.4211e-13 | -0.038921 | -0.0060108 | 0.065152 | -0.007709 | 0.054317 | -0.020755 | 0.00057035 | -0.0019016 | -0.0030124 | 0.026115 | -0.013659 | -12.3926 | 0.12503 | -12.4339 | 109.8373 | 109.6702 | 109.5202 | -12.2796 | -12.3615 | 0.22929 | -12.5242 | 109.5197 | 109.7674 | 109.7248 | -12.3438 | -0.011562 | -0.030569 | -0.12458 | -0.1658 | -0.15423 | -0.19768 | -0.34766 | -0.075737 | -0.34816 | -0.093403 | -0.25611 | -0.18037 | -0.10047 | -0.14306 | 122.1054 | 121.9382 | 121.7883 | 12.3931 | -122.1475 | 121.7878 | 122.0355 | 121.9929 | 12.4974 | -122.2117
1204.25 | 122.2733 | -11.9247 | 110.2844 | 1.4211e-13 | -0.038921 | -0.005797 | 0.064938 | -0.007709 | 0.054317 | -0.0054937 | 0.00057035 | -0.0016878 | -0.0030124 | 0.026115 | -0.013445 | -11.9898 | 0.12503 | -12.031 | 110.2173 | 110.0594 | 109.914 | -11.8858 | -11.9677 | 0.22472 | -12.1258 | 109.9226 | 110.1657 | 110.1231 | -11.9454 | 0.038904 | -0.067128 | -0.065006 | -0.10623 | -0.14513 | -0.22504 | -0.37046 | -0.020701 | -0.36182 | -0.042956 | -0.20109 | -0.18039 | -0.1187 | -0.16128 | 122.142 | 121.9841 | 121.8387 | 12.0498 | -122.1703 | 121.8474 | 122.0905 | 122.0479 | 12.1495 | -122.2299
1206.0156 | 122.3145 | -11.5356 | 110.6873 | 1.4211e-13 | -0.039348 | -0.0055834 | 0.065152 | -0.0074952 | 0.054531 | -0.0054937 | 0.00057035 | -0.0019016 | -0.0027988 | 0.026542 | -0.013445 | -11.5914 | 0.12961 | -11.6235 | 110.6385 | 110.4578 | 110.3123 | -11.4692 | -11.5556 | 0.22472 | -11.7092 | 110.3301 | 110.5732 | 110.5169 | -11.5517 | 0.066487 | -0.048748 | -0.055786 | -0.087862 | -0.15435 | -0.2295 | -0.37496 | -0.016022 | -0.35716 | -0.019971 | -0.17352 | -0.1575 | -0.11404 | -0.17036 | 122.1742 | 121.9934 | 121.8479 | 11.6653 | -122.1564 | 121.8657 | 122.1089 | 122.0525 | 11.7604 | -122.2389
1207.7031 | 122.2504 | -11.2244 | 111.0352 | 1.4211e-13 | -0.039134 | -0.005797 | 0.065152 | -0.007709 | 0.054104 | -0.0054937 | 0.00057035 | -0.0016878 | -0.0027988 | 0.026329 | -0.013445 | -11.2435 | 0.12961 | -11.2847 | 110.9727 | 110.7874 | 110.6511 | -11.1486 | -11.2031 | 0.22929 | -11.3749 | 110.6643 | 110.912 | 110.8557 | -11.2037 | 0.075731 | -0.062426 | -0.019108 | -0.060349 | -0.13608 | -0.24772 | -0.38404 | 0.020688 | -0.37083 | 0.02131 | -0.15056 | -0.17124 | -0.12312 | -0.17944 | 122.1971 | 122.0118 | 121.8755 | 11.354 | -122.1838 | 121.8887 | 122.1364 | 122.0801 | 11.4537 | -122.2388
1209.3906 | 122.2366 | -10.7941 | 111.438 | 1.4211e-13 | -0.039348 | -0.0062244 | 0.064938 | -0.007709 | 0.05389 | -0.013124 | 0.00057035 | -0.0016878 | -0.002585 | 0.026329 | -0.013659 | -10.8406 | 0.12961 | -10.8727 | 111.371 | 111.1904 | 111.0495 | -10.7411 | -10.8001 | 0.22929 | -10.9583 | 111.0672 | 111.315 | 111.2632 | -10.8053 | 0.052958 | -0.066938 | -0.046508 | -0.078602 | -0.13156 | -0.2476 | -0.38853 | -0.011253 | -0.37076 | -0.006062 | -0.16419 | -0.15294 | -0.12303 | -0.17478 | 122.1651 | 121.9845 | 121.8435 | 10.9237 | -122.1791 | 121.8613 | 122.109 | 122.0573 | 11.0234 | -122.2433
1211.1406 | 122.3145 | -10.5469 | 111.6531 | 1.4211e-13 | -0.039134 | -0.0060108 | 0.065366 | -0.007709 | 0.054317 | -0.0054937 | 0.00035675 | -0.0019016 | -0.0027988 | 0.026115 | -0.013659 | -10.5888 | 0.13419 | -10.63 | 111.6183 | 111.4422 | 111.3013 | -10.503 | -10.5529 | 0.22929 | -10.7156 | 111.3145 | 111.5576 | 111.5105 | -10.5718 | 0.04387 | -0.034854 | -0.041889 | -0.083145 | -0.12702 | -0.21091 | -0.35186 | -0.024925 | -0.33867 | -0.006004 | -0.16871 | -0.14379 | -0.095516 | -0.14268 | 122.1652 | 121.9891 | 121.8482 | 10.6811 | -122.1561 | 121.8613 | 122.1045 | 122.0573 | 10.7762 | -122.2249
1212.8906 | 122.3465 | -10.2722 | 111.9003 | 1.4211e-13 | -0.039348 | -0.005797 | 0.065152 | -0.0074952 | 0.054104 | -0.013124 | 0.00078395 | -0.0016878 | -0.0030124 | 0.026329 | -0.013873 | -10.3049 | 0.12961 | -10.3462 | 111.8976 | 111.7215 | 111.5806 | -10.2191 | -10.269 | 0.22929 | -10.4363 | 111.5892 | 111.8369 | 111.7898 | -10.2833 | 0.053105 | -0.002765 | -0.032687 | -0.07395 | -0.12705 | -0.17879 | -0.31976 | -0.011118 | -0.31115 | 0.003218 | -0.16407 | -0.15295 | -0.063414 | -0.11058 | 122.1698 | 121.9938 | 121.8528 | 10.4018 | -122.1194 | 121.8614 | 122.1091 | 122.062 | 10.5015 | -122.1837
1214.6406 | 122.3465 | -9.9609 | 112.2345 | 1.4211e-13 | -0.039348 | -0.0062244 | 0.064938 | -0.0074952 | 0.054104 | 0.0021363 | 0.00014315 | -0.0014742 | -0.0027988 | 0.025901 | -0.013232 | -10.0073 | 0.13419 | -10.0532 | 112.1997 | 112.01 | 111.8782 | -9.9306 | -9.9714 | 0.22472 | -10.1387 | 111.8776 | 112.1299 | 112.0874 | -9.9857 | 0.030297 | -0.034759 | -0.046371 | -0.09222 | -0.12252 | -0.22449 | -0.35632 | -0.024775 | -0.35687 | -0.010445 | -0.17773 | -0.15296 | -0.10455 | -0.14714 | 122.1607 | 121.9709 | 121.8391 | 10.0951 | -122.1651 | 121.8386 | 122.0909 | 122.0483 | 10.1857 | -122.2202
1216.3438 | 122.3099 | -9.6817 | 112.5 | 1.4211e-13 | -0.039134 | -0.005797 | 0.065152 | -0.0074952 | 0.05389 | 0.0021363 | 0.00057035 | -0.0021152 | -0.003226 | 0.026115 | -0.013445 | -9.7234 | 0.13419 | -9.7647 | 112.4744 | 112.3076 | 112.1529 | -9.6376 | -9.6829 | 0.23387 | -9.8411 | 112.1615 | 112.4138 | 112.3667 | -9.7064 | 0.044113 | -0.025558 | -0.041746 | -0.083023 | -0.12714 | -0.19236 | -0.3471 | -0.024702 | -0.33851 | -0.001222 | -0.15935 | -0.13465 | -0.08618 | -0.13334 | 122.1561 | 121.9893 | 121.8346 | 9.8159 | -122.1376 | 121.8432 | 122.0955 | 122.0484 | 9.9156 | -122.2064
1218.0938 | 122.3145 | -9.4254 | 112.7655 | 1.4211e-13 | -0.039134 | -0.005797 | 0.065366 | -0.007068 | 0.054317 | -0.0054937 | 0.00057035 | -0.0019016 | -0.0030124 | 0.025901 | -0.013659 | -9.4533 | 0.12961 | -9.4992 | 112.7354 | 112.5641 | 112.4185 | -9.3812 | -9.4128 | 0.22472 | -9.5755 | 112.4316 | 112.6794 | 112.6368 | -9.4408 | 0.044185 | -0.030093 | -0.027969 | -0.073831 | -0.11802 | -0.20144 | -0.34705 | -0.015478 | -0.33388 | 0.012574 | -0.15013 | -0.13466 | -0.086124 | -0.12871 | 122.1608 | 121.9894 | 121.8438 | 9.555 | -122.1467 | 121.857 | 122.1047 | 122.0621 | 9.6501 | -122.2063
1219.8438 | 122.3053 | -41.3452 | 80.9463 | 1.4211e-13 | -0.039989 | -0.0062244 | 0.064938 | -0.0072816 | 0.054531 | 0.0021363 | 0.00057035 | -0.0019016 | -0.0030124 | 0.026115 | -0.013232 | -36.713 | -0.30994 | -36.5934 | 85.6817 | 85.4614 | 85.5329 | -36.6395 | -36.7294 | -0.25147 | -36.8371 | 85.2903 | 85.5741 | 85.4216 | -36.7077 | 4.7057 | 4.7354 | 4.6322 | 4.7518 | 0.046058 | 4.5151 | 4.5866 | 4.6375 | 4.344 | 4.6159 | 4.5081 | -0.12944 | 4.6277 | 4.4752 | 127.0269 | 126.8066 | 126.8781 | 41.0353 | -117.5859 | 126.6355 | 126.9193 | 126.7668 | 41.0937 | -117.654
1221.5312 | 121.9894 | -29.4846 | 92.2943 | 1.4211e-13 | -0.039562 | -0.006438 | 0.064725 | -0.007068 | 0.054317 | 0.0021363 | 0.00057035 | -0.0019016 | -0.0027988 | 0.025901 | -0.013445 | -23.715 | -0.067272 | -23.7468 | 98.3364 | 98.1496 | 98.0645 | -23.5942 | -23.7396 | 0.023253 | -23.8473 | 97.9682 | 98.2064 | 98.1913 | -23.6855 | 5.8904 | 6.0421 | 5.7696 | 5.7378 | -0.15264 | 5.8553 | 5.7702 | 5.799 | 5.6738 | 5.745 | 5.6372 | -0.16179 | 5.9121 | 5.897 | 127.8209 | 127.6342 | 127.5491 | 29.4173 | -115.8885 | 127.4527 | 127.691 | 127.6759 | 29.5078 | -115.9798
1223.2812 | 122.1588 | -0.49896 | 121.8384 | 1.4211e-13 | -0.039562 | -0.005797 | 0.064725 | -0.0072816 | 0.054317 | -0.013124 | 0.00078395 | -0.0016878 | -0.0027988 | 0.026115 | -0.013659 | -0.53462 | 0.22118 | -0.57612 | 121.5488 | 121.3556 | 121.1911 | -0.58505 | -0.51177 | 0.33918 | -0.6058 | 121.2086 | 121.484 | 121.4277 | -0.66324 | -0.086093 | -0.28957 | -0.035662 | -0.077154 | 0.008939 | -0.48278 | -0.64732 | -0.16428 | -0.62978 | -0.012806 | -0.10683 | 0.057444 | -0.35435 | -0.41067 | 122.0478 | 121.8546 | 121.69 | 0.72014 | -122.4234 | 121.7076 | 121.983 | 121.9267 | 0.83815 | -122.5016
1225.0312 | 122.1542 | -5.2917 | 116.748 | 1.4211e-13 | -0.039348 | -0.0062244 | 0.065152 | -0.0072816 | 0.054104 | -0.013124 | 0.00099775 | -0.0019016 | -0.002585 | 0.026542 | -0.013659 | -5.5892 | 0.23949 | -5.7084 | 116.302 | 116.1631 | 115.9165 | -5.5486 | -5.5712 | 0.3575 | -5.6836 | 116.0212 | 116.2186 | 116.2951 | -5.6725 | -0.25686 | -0.44607 | -0.29742 | -0.41662 | -0.15976 | -0.58495 | -0.83154 | -0.38072 | -0.72688 | -0.27949 | -0.39184 | -0.01112 | -0.52941 | -0.45295 | 121.5937 | 121.4548 | 121.2083 | 5.5312 | -122.2967 | 121.3129 | 121.5104 | 121.5868 | 5.6492 | -122.4205
1226.7969 | 122.1634 | -121.2158 | 0.73242 | 1.4211e-13 | -0.040416 | -0.0068654 | 0.064084 | -0.007068 | 0.055172 | -0.0054937 | -0.00028425 | -0.0027562 | -0.0047216 | 0.026329 | -0.012377 | -120.8135 | -0.43814 | -120.962 | 0.69768 | 0.69636 | 0.77381 | -121.2443 | -120.8998 | -0.48498 | -121.0076 | 0.61561 | 0.71423 | 0.74491 | -121.3654 | -0.028475 | -0.034742 | 0.40237 | 0.25382 | 0.28229 | -0.036066 | 0.041391 | -0.14962 | -0.11681 | 0.31603 | 0.20827 | 0.35789 | -0.018189 | 0.012484 | 121.9135 | 121.9122 | 121.9896 | 120.7777 | -121.9767 | 121.8314 | 121.9301 | 121.9607 | 120.7308 | -122.0979
1228.5625 | 122.2824 | -120.9778 | 0.97046 | 1.4211e-13 | -0.040203 | -0.0068654 | 0.064084 | -0.0074952 | 0.054958 | 0.0021363 | 0.00014315 | -0.0027562 | -0.0047216 | 0.026542 | -0.012591 | -120.699 | -0.30536 | -120.8475 | 0.89913 | 0.89325 | 0.95696 | -121.1252 | -120.7807 | -0.34762 | -120.8885 | 0.80333 | 0.90195 | 0.94179 | -121.2372 | -0.14746 | -0.07133 | 0.27879 | 0.13024 | 0.2777 | -0.07721 | -0.013502 | -0.25945 | -0.16713 | 0.19704 | 0.089279 | 0.34873 | -0.068504 | -0.028673 | 121.8769 | 121.871 | 121.9347 | 120.6724 | -122.0957 | 121.7811 | 121.8797 | 121.9196 | 120.6302 | -122.2077
1230.25 | 122.2 | -120.932 | 1.1719 | 1.4211e-13 | -0.04063 | -0.0070792 | 0.064297 | -0.0072816 | 0.054958 | -0.0054937 | -7.0448e-05 | -0.0023288 | -0.0047216 | 0.026115 | -0.012377 | -120.5159 | -0.23668 | -120.6782 | 1.0914 | 1.0993 | 1.163 | -120.9512 | -120.6022 | -0.28352 | -120.7054 | 1.0048 | 1.1126 | 1.1432 | -121.0587 | -0.019237 | -0.080453 | 0.41615 | 0.25386 | 0.27309 | -0.072574 | -0.008881 | -0.12665 | -0.16709 | 0.32984 | 0.22665 | 0.3533 | -0.059304 | -0.028631 | 122.0234 | 122.0313 | 122.095 | 120.6953 | -122.1231 | 121.9368 | 122.0446 | 122.0753 | 120.6485 | -122.2305
1232 | 122.3053 | -121.0373 | 1.0208 | 1.4211e-13 | -0.04063 | -0.0068654 | 0.064084 | -0.0072816 | 0.055172 | -0.013124 | -0.00049785 | -0.0027562 | -0.004508 | 0.026542 | -0.012591 | -120.6257 | -0.21379 | -120.7835 | 0.99985 | 1.0031 | 1.0668 | -121.0657 | -120.7166 | -0.26521 | -120.8198 | 0.91779 | 1.0118 | 1.0471 | -121.1823 | -0.028425 | -0.020959 | 0.41155 | 0.25384 | 0.28227 | -0.01767 | 0.046031 | -0.145 | -0.10302 | 0.32065 | 0.21747 | 0.36246 | -0.008971 | 0.02628 | 122.0371 | 122.0404 | 122.1041 | 120.8235 | -122.0865 | 121.9551 | 122.0491 | 122.0844 | 120.7721 | -122.2031
1233.75 | 122.2229 | -121.0693 | 1.0712 | 1.4211e-13 | -0.04063 | -0.0068654 | 0.064084 | -0.0072816 | 0.054958 | 0.0021363 | -7.0448e-05 | -0.0029698 | -0.0049352 | 0.026542 | -0.012804 | -120.6441 | -0.19547 | -120.8018 | 0.98612 | 0.99399 | 1.0531 | -121.0795 | -120.7304 | -0.23773 | -120.8336 | 0.90406 | 1.0073 | 1.0425 | -121.1914 | -0.010118 | -0.085048 | 0.42529 | 0.26757 | 0.27769 | -0.077181 | -0.018059 | -0.12211 | -0.16711 | 0.33896 | 0.23578 | 0.35788 | -0.063904 | -0.028652 | 122.0555 | 122.0633 | 122.1224 | 120.8739 | -122.1506 | 121.9734 | 122.0766 | 122.1119 | 120.8316 | -122.2626
1235.4375 | 122.2366 | -120.8633 | 1.2817 | 1.4211e-13 | -0.040416 | -0.0070792 | 0.064297 | -0.0074952 | 0.055172 | -0.0054937 | -0.00028425 | -0.0025424 | -0.0047216 | 0.026542 | -0.012591 | -120.4014 | -0.18174 | -120.5637 | 1.2288 | 1.2367 | 1.2912 | -120.7681 | -120.4923 | -0.22858 | -120.6046 | 1.1513 | 1.2408 | 1.2806 | -120.9671 | 0.095255 | -0.052965 | 0.46195 | 0.29965 | 0.20439 | -0.045069 | 0.009457 | -0.10374 | -0.13044 | 0.37106 | 0.25872 | 0.36246 | -0.040966 | -0.001136 | 122.0921 | 122.1 | 122.1545 | 120.6816 | -122.0498 | 122.0146 | 122.1041 | 122.1439 | 120.6348 | -122.2488
1237.1875 | 122.3328 | -121.0236 | 1.0757 | 1.4211e-13 | -0.040416 | -0.0068654 | 0.064297 | -0.007068 | 0.055172 | -0.013124 | -0.00049785 | -0.0025424 | -0.0047216 | 0.026756 | -0.012591 | -120.5983 | -0.16342 | -120.7651 | 1.0411 | 1.0489 | 1.0989 | -120.9696 | -120.6983 | -0.21942 | -120.8015 | 0.94527 | 1.0485 | 1.0929 | -121.164 | 0.054 | -0.034686 | 0.42529 | 0.25842 | 0.20442 | -0.026812 | 0.023149 | -0.14041 | -0.13048 | 0.32524 | 0.22205 | 0.36246 | -0.027274 | 0.017134 | 122.0646 | 122.0725 | 122.1225 | 120.8601 | -122.0453 | 121.9688 | 122.072 | 122.1164 | 120.8041 | -122.2397
1238.9219 | 122.2412 | -120.5246 | 1.6022 | 1.4211e-13 | -0.04063 | -0.0066518 | 0.064084 | -0.0074952 | 0.055599 | -0.0054937 | 0.00014315 | -0.0025424 | -0.0047216 | 0.026756 | -0.012591 | -120.2961 | -0.14511 | -120.4675 | 1.3295 | 1.3374 | 1.3965 | -120.6674 | -120.387 | -0.2011 | -120.5039 | 1.2612 | 1.3507 | 1.3996 | -120.8572 | -0.14275 | -0.27268 | 0.2285 | 0.057048 | 0.1998 | -0.26477 | -0.20567 | -0.33259 | -0.34099 | 0.13763 | 0.020704 | 0.3533 | -0.25152 | -0.20253 | 121.8541 | 121.862 | 121.9211 | 120.3795 | -122.2695 | 121.7858 | 121.8753 | 121.9242 | 120.3235 | -122.4594
1240.6719 | 122.1909 | -120.6116 | 1.5335 | 1.4211e-13 | -0.040416 | -0.0070792 | 0.064084 | -0.007068 | 0.055172 | -0.0054937 | -0.00028425 | -0.0027562 | -0.0047216 | 0.026756 | -0.012591 | -120.1816 | -0.14969 | -120.3485 | 1.4623 | 1.461 | 1.5155 | -120.5529 | -120.2771 | -0.20568 | -120.394 | 1.3711 | 1.4743 | 1.5187 | -120.7473 | 0.058694 | -0.071237 | 0.42994 | 0.26306 | 0.20437 | -0.072472 | -0.017961 | -0.13573 | -0.16244 | 0.33449 | 0.21757 | 0.3533 | -0.059227 | -0.014819 | 122.0738 | 122.0726 | 122.1271 | 120.4619 | -122.0864 | 121.9826 | 122.0859 | 122.1303 | 120.4059 | -122.2808
1242.3594 | 122.2504 | -120.7901 | 1.3367 | 1.4211e-13 | -0.041057 | -0.0066518 | 0.064084 | -0.0074952 | 0.055172 | 0.0021363 | -7.0448e-05 | -0.0025424 | -0.0047216 | 0.026115 | -0.012804 | -120.3739 | -0.14511 | -120.5362 | 1.27 | 1.2687 | 1.3324 | -120.7498 | -120.4648 | -0.2011 | -120.5726 | 1.1879 | 1.2866 | 1.3264 | -120.9396 | 0.040329 | -0.066691 | 0.41617 | 0.25388 | 0.21355 | -0.067949 | -0.004267 | -0.14951 | -0.14875 | 0.32529 | 0.21753 | 0.36704 | -0.050112 | -0.010282 | 122.0601 | 122.0588 | 122.1225 | 120.645 | -122.0864 | 121.978 | 122.0767 | 122.1165 | 120.589 | -122.2763
1244.1094 | 122.2504 | -120.9915 | 1.1444 | 1.4211e-13 | -0.040844 | -0.0072928 | 0.064084 | -0.007068 | 0.055172 | -0.013124 | -7.0448e-05 | -0.0025424 | -0.0047216 | 0.026756 | -0.012591 | -120.5845 | -0.14511 | -120.7422 | 1.0731 | 1.081 | 1.1355 | -120.9467 | -120.6709 | -0.19653 | -120.7786 | 0.98647 | 1.0943 | 1.1249 | -121.1457 | 0.044851 | -0.071301 | 0.40698 | 0.24927 | 0.20442 | -0.063424 | -0.008886 | -0.15414 | -0.15794 | 0.32067 | 0.2129 | 0.36704 | -0.050152 | -0.019479 | 122.0646 | 122.0725 | 122.127 | 120.8464 | -122.0911 | 121.978 | 122.0858 | 122.1164 | 120.795 | -122.2901
1245.8438 | 122.3328 | -121.0602 | 0.99335 | 1.4211e-13 | -0.041057 | -0.0072928 | 0.064084 | -0.007709 | 0.055172 | -0.013124 | -0.00028425 | -0.0023288 | -0.0047216 | 0.026756 | -0.012377 | -120.6853 | -0.13595 | -120.8567 | 0.96323 | 0.96651 | 1.0211 | -121.0611 | -120.7807 | -0.19653 | -120.8931 | 0.88117 | 0.97979 | 1.0196 | -121.2647 | -0.000957 | -0.03012 | 0.37493 | 0.20348 | 0.20444 | -0.026835 | 0.027711 | -0.20453 | -0.11218 | 0.27944 | 0.1671 | 0.37162 | -0.013555 | 0.026275 | 122.0234 | 122.0267 | 122.0812 | 120.9242 | -122.0545 | 121.9413 | 122.04 | 122.0798 | 120.8637 | -122.2581
1247.5938 | 122.3145 | -121.138 | 0.93842 | 1.4211e-13 | -0.04063 | -0.0070792 | 0.064084 | -0.0072816 | 0.054958 | 0.0021363 | -7.0448e-05 | -0.0027562 | -0.0047216 | 0.026756 | -0.012804 | -120.7402 | -0.13137 | -120.9116 | 0.91744 | 0.91156 | 0.96611 | -121.1252 | -120.8403 | -0.20568 | -120.9434 | 0.81707 | 0.92485 | 0.96468 | -121.3059 | 0.012757 | -0.020973 | 0.3978 | 0.22636 | 0.2136 | -0.026851 | 0.027698 | -0.16791 | -0.12135 | 0.29774 | 0.19455 | 0.36247 | -0.013568 | 0.026263 | 122.0554 | 122.0496 | 122.1041 | 121.0066 | -122.0637 | 121.9551 | 122.0628 | 122.1027 | 120.9323 | -122.2443
1249.2812 | 122.2 | -121.2296 | 0.91095 | 1.4211e-13 | -0.040844 | -0.0070792 | 0.064297 | -0.007709 | 0.055172 | 0.0021363 | -0.00049785 | -0.0029698 | -0.004508 | 0.02697 | -0.012591 | -120.8089 | -0.13595 | -120.9803 | 0.83961 | 0.84288 | 0.89743 | -121.1848 | -120.9089 | -0.2011 | -121.0167 | 0.76213 | 0.86075 | 0.896 | -121.3838 | 0.044784 | -0.07134 | 0.42068 | 0.24924 | 0.20445 | -0.068069 | -0.013515 | -0.1542 | -0.14882 | 0.32061 | 0.21285 | 0.36705 | -0.050202 | -0.01495 | 122.0692 | 122.0724 | 122.127 | 121.0936 | -122.0957 | 121.9917 | 122.0903 | 122.1256 | 121.0284 | -122.2947
1251.0312 | 122.1863 | -121.2387 | 0.90637 | 1.4211e-13 | -0.040844 | -0.0070792 | 0.06387 | -0.0072816 | 0.055386 | -0.0054937 | -0.00028425 | -0.0029698 | -0.0051488 | 0.026756 | -0.012377 | -120.8272 | -0.12679 | -120.9895 | 0.83045 | 0.82914 | 0.8837 | -121.2077 | -120.9227 | -0.2011 | -121.0304 | 0.74381 | 0.83786 | 0.88226 | -121.4021 | 0.031044 | -0.075918 | 0.41152 | 0.24923 | 0.21819 | -0.077228 | -0.022672 | -0.16336 | -0.16256 | 0.31603 | 0.20826 | 0.37163 | -0.068517 | -0.024108 | 122.0692 | 122.0679 | 122.1224 | 121.1119 | -122.114 | 121.9825 | 122.0766 | 122.121 | 121.0376 | -122.3084
1252.7969 | 122.2733 | -121.2067 | 0.90179 | 1.4211e-13 | -0.040844 | -0.0066518 | 0.064297 | -0.0074952 | 0.055599 | -0.013124 | -0.00028425 | -0.0025424 | -0.0047216 | 0.026756 | -0.012591 | -120.8135 | -0.12679 | -120.9849 | 0.84419 | 0.85204 | 0.90659 | -121.1985 | -120.9044 | -0.19653 | -121.0076 | 0.75297 | 0.85617 | 0.89142 | -121.3792 | 0.008159 | -0.057605 | 0.39321 | 0.22177 | 0.21361 | -0.049755 | 0.004799 | -0.17251 | -0.14883 | 0.3023 | 0.19911 | 0.37162 | -0.045625 | -0.010373 | 122.0509 | 122.0587 | 122.1133 | 121.0799 | -122.1003 | 121.9596 | 122.0628 | 122.0981 | 121.0101 | -122.281
1254.5625 | 122.3236 | -121.2204 | 0.82398 | 1.4211e-13 | -0.040844 | -0.0068654 | 0.064084 | -0.0074952 | 0.054745 | -0.0054937 | -0.00071145 | -0.0029698 | -0.0047216 | 0.02697 | -0.012377 | -120.8455 | -0.12222 | -121.0169 | 0.80298 | 0.79709 | 0.86081 | -121.2306 | -120.9502 | -0.19653 | -121.0533 | 0.71634 | 0.81496 | 0.84564 | -121.425 | -0.01016 | -0.020992 | 0.3749 | 0.20346 | 0.21362 | -0.026883 | 0.036832 | -0.20457 | -0.10764 | 0.27025 | 0.16706 | 0.37163 | -0.009013 | 0.02166 | 122.0234 | 122.0175 | 122.0812 | 121.0982 | -122.0545 | 121.9367 | 122.0354 | 122.066 | 121.0239 | -122.2489
1256.2656 | 122.3236 | -121.2524 | 0.82855 | 1.4211e-13 | -0.040844 | -0.0070792 | 0.064084 | -0.0074952 | 0.055386 | 0.0021363 | -7.0448e-05 | -0.0027562 | -0.0049352 | 0.026756 | -0.012591 | -120.873 | -0.12222 | -121.0444 | 0.77551 | 0.78336 | 0.83791 | -121.258 | -120.9685 | -0.18737 | -121.0808 | 0.67971 | 0.79207 | 0.82732 | -121.4524 | -0.005591 | -0.053039 | 0.37947 | 0.20803 | 0.21362 | -0.045197 | 0.009362 | -0.2 | -0.14884 | 0.28397 | 0.17163 | 0.37163 | -0.036483 | -0.001231 | 122.028 | 122.0358 | 122.0904 | 121.1302 | -122.0866 | 121.9322 | 122.0445 | 122.0798 | 121.0651 | -122.281
1258.0156 | 122.2046 | -121.2524 | 0.90637 | 1.4211e-13 | -0.040844 | -0.0070792 | 0.064084 | -0.0074952 | 0.055599 | 0.0021363 | -7.0448e-05 | -0.0027562 | -0.0047216 | 0.02697 | -0.012804 | -120.8363 | -0.12679 | -121.0078 | 0.81214 | 0.81541 | 0.86996 | -121.2214 | -120.941 | -0.19653 | -121.0442 | 0.72092 | 0.8287 | 0.86395 | -121.4158 | 0.03104 | -0.094232 | 0.4161 | 0.24466 | 0.21362 | -0.090964 | -0.036408 | -0.16337 | -0.18545 | 0.31145 | 0.20826 | 0.37163 | -0.077674 | -0.042423 | 122.0646 | 122.0678 | 122.1224 | 121.1256 | -122.1278 | 121.9734 | 122.0811 | 122.1164 | 121.0559 | -122.3222
1259.7656 | 122.3373 | -121.2616 | 0.7782 | 1.4211e-13 | -0.041057 | -0.0066518 | 0.064511 | -0.007709 | 0.055172 | -0.013124 | -0.00049785 | -0.0027562 | -0.0049352 | 0.026542 | -0.012804 | -120.8959 | -0.11764 | -121.0673 | 0.7572 | 0.75588 | 0.8196 | -121.2855 | -120.9959 | -0.19653 | -121.1083 | 0.67056 | 0.76002 | 0.79985 | -121.4799 | -0.023909 | -0.020999 | 0.36574 | 0.19429 | 0.2182 | -0.022316 | 0.041401 | -0.21831 | -0.10764 | 0.26566 | 0.15331 | 0.37163 | -0.018179 | 0.021651 | 122.0188 | 122.0175 | 122.0812 | 121.144 | -122.0637 | 121.9322 | 122.0216 | 122.0614 | 121.0651 | -122.2581
1261.4688 | 122.1909 | -121.3211 | 0.8606 | 1.4211e-13 | -0.041271 | -0.0068654 | 0.064084 | -0.0072816 | 0.054958 | 0.0021363 | -0.00049785 | -0.0025424 | -0.0051488 | 0.026756 | -0.012591 | -120.8821 | -0.11764 | -121.0627 | 0.76178 | 0.76962 | 0.82418 | -121.2626 | -120.9822 | -0.2011 | -121.0854 | 0.68429 | 0.77375 | 0.82274 | -121.4662 | 0.058495 | -0.098818 | 0.43898 | 0.25838 | 0.19989 | -0.090978 | -0.036418 | -0.14507 | -0.17631 | 0.3389 | 0.23572 | 0.38078 | -0.086841 | -0.037854 | 122.0829 | 122.0907 | 122.1453 | 121.2035 | -122.1232 | 122.0054 | 122.0949 | 122.1438 | 121.12 | -122.3268
1263.2031 | 122.2641 | -121.3257 | 0.76446 | 1.4211e-13 | -0.041057 | -0.0068654 | 0.064297 | -0.007709 | 0.055172 | -0.0054937 | -7.0448e-05 | -0.0025424 | -0.0047216 | 0.027183 | -0.012591 | -120.9279 | -0.11306 | -121.0994 | 0.72057 | 0.71467 | 0.77839 | -121.2992 | -121.0234 | -0.18737 | -121.1403 | 0.64308 | 0.73255 | 0.77238 | -121.512 | 0.026442 | -0.043893 | 0.39777 | 0.22633 | 0.19989 | -0.049794 | 0.013927 | -0.18628 | -0.12138 | 0.30227 | 0.18535 | 0.37163 | -0.031918 | 0.007912 | 122.0463 | 122.0404 | 122.1041 | 121.2126 | -122.0637 | 121.9688 | 122.0582 | 122.0981 | 121.1383 | -122.2764
1264.9531 | 122.3328 | -121.2936 | 0.75531 | 1.4211e-13 | -0.041057 | -0.0072928 | 0.064084 | -0.0072816 | 0.055172 | -0.0054937 | -0.00049785 | -0.0027562 | -0.0047216 | 0.02697 | -0.012591 | -120.9279 | -0.11764 | -121.1039 | 0.71599 | 0.71925 | 0.76924 | -121.3084 | -121.0326 | -0.19653 | -121.1449 | 0.63393 | 0.72797 | 0.77696 | -121.512 | -0.01476 | -0.039316 | 0.36573 | 0.18971 | 0.20447 | -0.03606 | 0.013925 | -0.21832 | -0.12138 | 0.26107 | 0.14873 | 0.36705 | -0.027342 | 0.021646 | 122.0096 | 122.0129 | 122.0629 | 121.176 | -122.0637 | 121.9276 | 122.0216 | 122.0706 | 121.0971 | -122.2673
1266.6406 | 122.3465 | -121.3165 | 0.76904 | 1.4211e-13 | -0.041271 | -0.0070792 | 0.064084 | -0.0074952 | 0.054958 | -0.0054937 | -7.0448e-05 | -0.0023288 | -0.003867 | 0.027183 | -0.012591 | -120.9233 | -0.10848 | -121.0948 | 0.72973 | 0.72841 | 0.77381 | -121.3084 | -121.0188 | -0.19653 | -121.1312 | 0.63393 | 0.7417 | 0.78153 | -121.5074 | 0.008128 | -0.039314 | 0.3932 | 0.22176 | 0.21363 | -0.040635 | 0.00477 | -0.19085 | -0.13512 | 0.2977 | 0.18535 | 0.37621 | -0.027339 | 0.012491 | 122.0463 | 122.0449 | 122.0903 | 121.208 | -122.0774 | 121.9505 | 122.0582 | 122.0981 | 121.12 | -122.2764
1268.3281 | 122.2733 | -121.2753 | 0.82398 | 1.4211e-13 | -0.041271 | -0.0068654 | 0.064084 | -0.007709 | 0.055172 | -0.013124 | -0.00028425 | -0.0027562 | -0.003867 | 0.026542 | -0.012377 | -120.8959 | -0.11764 | -121.0673 | 0.75262 | 0.76046 | 0.80586 | -121.2855 | -121.0005 | -0.19653 | -121.0945 | 0.66598 | 0.76918 | 0.80901 | -121.4845 | -0.010176 | -0.071354 | 0.37947 | 0.20803 | 0.2182 | -0.063515 | -0.018112 | -0.20916 | -0.158 | 0.27481 | 0.18078 | 0.38994 | -0.054799 | -0.014969 | 122.028 | 122.0358 | 122.0812 | 121.1577 | -122.1095 | 121.9413 | 122.0445 | 122.0843 | 121.0788 | -122.3085
1270.0781 | 122.2412 | -121.225 | 0.86975 | 1.4211e-13 | -0.041485 | -0.0068654 | 0.064084 | -0.0074952 | 0.055172 | -0.013124 | -0.00028425 | -0.0027562 | -0.003867 | 0.02697 | -0.012804 | -120.8226 | -0.11306 | -120.9941 | 0.83045 | 0.82456 | 0.8837 | -121.2077 | -120.9227 | -0.19653 | -121.035 | 0.73923 | 0.84243 | 0.87311 | -121.4066 | 0.017312 | -0.039297 | 0.40237 | 0.23092 | 0.21361 | -0.045186 | 0.013949 | -0.18167 | -0.13052 | 0.3023 | 0.18995 | 0.37163 | -0.027317 | 0.003356 | 122.0554 | 122.0495 | 122.1087 | 121.1119 | -122.0774 | 121.9642 | 122.0674 | 122.0981 | 121.0284 | -122.2764
1271.8438 | 122.2687 | -121.1197 | 0.99335 | 1.4211e-13 | -0.041485 | -0.0068654 | 0.063656 | -0.0072816 | 0.054958 | -0.0054937 | -0.00028425 | -0.0025424 | -0.0036534 | 0.027183 | -0.012804 | -120.7127 | -0.11306 | -120.8796 | 0.94034 | 0.93446 | 0.99359 | -121.0978 | -120.8082 | -0.2011 | -120.9206 | 0.85369 | 0.9569 | 0.99215 | -121.2876 | 0.02192 | -0.053012 | 0.40696 | 0.2401 | 0.21818 | -0.058887 | 0.000239 | -0.16791 | -0.13965 | 0.31148 | 0.19914 | 0.36705 | -0.036448 | -0.001197 | 122.06 | 122.0542 | 122.1133 | 121.0066 | -122.0911 | 121.9734 | 122.0766 | 122.1118 | 120.9186 | -122.2809
1273.5938 | 122.3236 | -120.9091 | 1.149 | 1.4211e-13 | -0.041485 | -0.0072928 | 0.064084 | -0.0072816 | 0.055386 | -0.0054937 | -0.00049785 | -0.0029698 | -0.0040806 | 0.02697 | -0.012591 | -120.5159 | -0.11306 | -120.6873 | 1.128 | 1.1314 | 1.1859 | -120.8963 | -120.6205 | -0.19653 | -120.7145 | 1.0506 | 1.1492 | 1.1753 | -121.0999 | 0.012822 | -0.020938 | 0.39326 | 0.22181 | 0.20899 | -0.017634 | 0.0369 | -0.19075 | -0.098416 | 0.28863 | 0.19461 | 0.38536 | 0.000213 | 0.026307 | 122.0372 | 122.0405 | 122.095 | 120.7961 | -122.0453 | 121.9597 | 122.0583 | 122.0844 | 120.7126 | -122.2489
1275.2812 | 122.2458 | -121.0144 | 1.1078 | 1.4211e-13 | -0.041485 | -0.0068654 | 0.064297 | -0.007709 | 0.054958 | -0.0054937 | -0.00028425 | -0.0029698 | -0.0040806 | 0.027183 | -0.012591 | -120.6257 | -0.11764 | -120.7972 | 1.0227 | 1.0169 | 1.0714 | -121.0108 | -120.7258 | -0.2011 | -120.8244 | 0.93153 | 1.0347 | 1.07 | -121.196 | 0.003634 | -0.085042 | 0.38867 | 0.21722 | 0.21358 | -0.090908 | -0.036366 | -0.18162 | -0.17626 | 0.28861 | 0.19 | 0.37162 | -0.073053 | -0.037802 | 122.0371 | 122.0313 | 122.0858 | 120.8968 | -122.1186 | 121.9459 | 122.0491 | 122.0844 | 120.8133 | -122.3038
1277.0156 | 122.2778 | -120.9915 | 1.0574 | 1.4211e-13 | -0.041912 | -0.0070792 | 0.064084 | -0.007709 | 0.055386 | -0.0054937 | -0.00049785 | -0.0027562 | -0.0040806 | 0.026756 | -0.012804 | -120.6212 | -0.11764 | -120.7972 | 1.0182 | 1.0215 | 1.0806 | -121.0153 | -120.7212 | -0.2011 | -120.8336 | 0.94069 | 1.0439 | 1.07 | -121.2098 | -0.023833 | -0.039266 | 0.37036 | 0.19433 | 0.21816 | -0.035975 | 0.023145 | -0.21824 | -0.11675 | 0.2703 | 0.15796 | 0.3762 | -0.013542 | 0.012552 | 122.0097 | 122.013 | 122.0721 | 120.8739 | -122.0728 | 121.9322 | 122.0354 | 122.0615 | 120.7904 | -122.2672
1278.7656 | 122.3236 | -119.5908 | 2.4948 | 1.4211e-13 | -0.041485 | -0.0068654 | 0.063656 | -0.007709 | 0.054958 | -0.013124 | -7.0448e-05 | -0.0029698 | -0.0036534 | 0.026756 | -0.012804 | -119.1423 | -0.1039 | -119.3092 | 2.4558 | 2.4867 | 2.5412 | -119.5226 | -119.2423 | -0.2011 | -119.3455 | 2.4104 | 2.5136 | 2.5443 | -119.7216 | 0.068139 | -0.039031 | 0.44842 | 0.28151 | 0.21338 | -0.008097 | 0.046342 | -0.13089 | -0.084428 | 0.34847 | 0.24528 | 0.37617 | 0.018811 | 0.049484 | 122.0465 | 122.0775 | 122.1319 | 119.4869 | -122.0174 | 122.0011 | 122.1044 | 122.1351 | 119.3897 | -122.2165
1280.4531 | 122.2137 | -119.4717 | 2.6047 | 1.4211e-13 | -0.041485 | -0.0068654 | 0.06387 | -0.007709 | 0.055172 | 0.0021363 | -0.00049785 | -0.0025424 | -0.003867 | 0.02697 | -0.012591 | -118.95 | -0.1039 | -119.1673 | 2.6069 | 2.6424 | 2.6922 | -119.3715 | -119.0958 | -0.2011 | -119.199 | 2.5615 | 2.6647 | 2.7 | -119.5705 | 0.10023 | 0.002193 | 0.52169 | 0.30442 | 0.2042 | 0.037723 | 0.087573 | -0.098803 | -0.043201 | 0.37597 | 0.27278 | 0.37158 | 0.060042 | 0.095294 | 122.0786 | 122.1141 | 122.164 | 119.3678 | -121.9762 | 122.0332 | 122.1365 | 122.1717 | 119.2706 | -122.1752
1282.2188 | 122.2275 | -119.6823 | 2.4307 | 1.4211e-13 | -0.041698 | -0.0068654 | 0.064297 | -0.0074952 | 0.054958 | -0.0054937 | -0.00028425 | -0.0025424 | -0.0040806 | 0.02697 | -0.012591 | -119.2385 | -0.1039 | -119.4466 | 2.3184 | 2.3585 | 2.4038 | -119.6554 | -119.3751 | -0.20568 | -119.4828 | 2.2776 | 2.3763 | 2.4115 | -119.8636 | 0.026904 | -0.11229 | 0.44383 | 0.23572 | 0.20882 | -0.07222 | -0.026929 | -0.18128 | -0.15312 | 0.30724 | 0.19947 | 0.38075 | -0.05446 | -0.019208 | 122.0007 | 122.0408 | 122.0861 | 119.5784 | -122.0861 | 121.9599 | 122.0586 | 122.0938 | 119.4766 | -122.2943
1283.9688 | 122.3145 | -120.5658 | 1.474 | 1.4211e-13 | -0.041485 | -0.0075064 | 0.064297 | -0.0074952 | 0.054958 | -0.0054937 | -0.00028425 | -0.0025424 | -0.0040806 | 0.026756 | -0.013018 | -120.1496 | -0.11764 | -120.3622 | 1.3936 | 1.4427 | 1.4972 | -120.5849 | -120.3046 | -0.2011 | -120.4123 | 1.3482 | 1.456 | 1.505 | -120.7885 | -0.019134 | -0.080404 | 0.41621 | 0.20355 | 0.22268 | -0.031279 | 0.023233 | -0.22271 | -0.12583 | 0.26124 | 0.15348 | 0.37619 | -0.018033 | 0.030955 | 121.9594 | 122.0085 | 122.063 | 120.4482 | -122.0589 | 121.914 | 122.0218 | 122.0708 | 120.3647 | -122.2625
1285.7188 | 122.2092 | -120.7214 | 1.4236 | 1.4211e-13 | -0.041485 | -0.0068654 | 0.064084 | -0.0074952 | 0.054745 | 0.0021363 | -0.00049785 | -0.0027562 | -0.0040806 | 0.027183 | -0.013018 | -120.2595 | -0.11306 | -120.4767 | 1.2929 | 1.3466 | 1.3919 | -120.6811 | -120.4053 | -0.224 | -120.5085 | 1.252 | 1.3507 | 1.3951 | -120.8892 | 0.040348 | -0.13077 | 0.46197 | 0.24473 | 0.20438 | -0.077082 | -0.031721 | -0.16781 | -0.17162 | 0.31615 | 0.21296 | 0.38077 | -0.072987 | -0.028578 | 122.0143 | 122.068 | 122.1134 | 120.6084 | -122.1047 | 121.9735 | 122.0721 | 122.1165 | 120.4974 | -122.3129
1287.4062 | 122.2137 | -120.7123 | 1.4328 | 1.4211e-13 | -0.041485 | -0.0066518 | 0.064297 | -0.0072816 | 0.054958 | -0.013124 | -0.00049785 | -0.0027562 | -0.0040806 | 0.02697 | -0.013018 | -120.2457 | -0.10848 | -120.4767 | 1.2929 | 1.3374 | 1.3965 | -120.6811 | -120.3961 | -0.21484 | -120.5039 | 1.2612 | 1.3598 | 1.3996 | -120.8938 | 0.031192 | -0.13993 | 0.46655 | 0.23558 | 0.20438 | -0.095395 | -0.036297 | -0.18154 | -0.17162 | 0.31615 | 0.20839 | 0.38993 | -0.072984 | -0.033154 | 122.0052 | 122.0497 | 122.1088 | 120.6038 | -122.1139 | 121.9735 | 122.0721 | 122.1119 | 120.4974 | -122.3266
1289.1562 | 122.2366 | -120.7031 | 1.442 | 1.4211e-13 | -0.041912 | -0.0070792 | 0.064297 | -0.007709 | 0.054958 | -0.0054937 | -0.00028425 | -0.0025424 | -0.0040806 | 0.026756 | -0.012804 | -120.2549 | -0.1039 | -120.4675 | 1.2883 | 1.3374 | 1.3873 | -120.6857 | -120.4053 | -0.21484 | -120.5039 | 1.2612 | 1.3552 | 1.3951 | -120.8984 | 0.017459 | -0.15366 | 0.44824 | 0.23558 | 0.21812 | -0.10455 | -0.05461 | -0.19528 | -0.18077 | 0.29784 | 0.19923 | 0.39451 | -0.086719 | -0.046889 | 121.9914 | 122.0405 | 122.0905 | 120.5992 | -122.1276 | 121.9643 | 122.0584 | 122.0982 | 120.4883 | -122.3404
1290.9062 | 122.2549 | -120.7306 | 1.3687 | 1.4211e-13 | -0.042126 | -0.0068654 | 0.064084 | -0.007709 | 0.054958 | -0.0054937 | -0.00028425 | -0.0029698 | -0.003867 | 0.027183 | -0.012804 | -120.2915 | -0.11306 | -120.5225 | 1.2562 | 1.2962 | 1.3507 | -120.7223 | -120.4419 | -0.21942 | -120.5405 | 1.2246 | 1.3049 | 1.3539 | -120.9396 | 0.008293 | -0.11247 | 0.43908 | 0.2081 | 0.19981 | -0.072518 | -0.017996 | -0.20902 | -0.14416 | 0.28868 | 0.19007 | 0.39909 | -0.063841 | -0.014853 | 121.9868 | 122.0268 | 122.0813 | 120.6175 | -122.091 | 121.9551 | 122.0355 | 122.0845 | 120.5112 | -122.3083
1292.5938 | 122.2504 | -120.6802 | 1.4191 | 1.4211e-13 | -0.041912 | -0.0075064 | 0.064297 | -0.0074952 | 0.054958 | 0.0021363 | -7.0448e-05 | -0.0027562 | -0.003867 | 0.02697 | -0.013018 | -120.2366 | -0.099323 | -120.4584 | 1.3158 | 1.3603 | 1.4102 | -120.6628 | -120.3824 | -0.21484 | -120.4902 | 1.2749 | 1.3736 | 1.4134 | -120.8663 | 0.017465 | -0.1033 | 0.44366 | 0.22185 | 0.20438 | -0.058767 | -0.008828 | -0.18611 | -0.14415 | 0.29785 | 0.19008 | 0.37619 | -0.045516 | -0.005685 | 121.996 | 122.0405 | 122.0905 | 120.5809 | -122.0818 | 121.9552 | 122.0538 | 122.0936 | 120.4654 | -122.2854
1294.2812 | 122.2504 | -120.5704 | 1.5564 | 1.4211e-13 | -0.041912 | -0.0072928 | 0.064084 | -0.007709 | 0.055172 | -0.0054937 | 0.00014315 | -0.0025424 | -0.0034396 | 0.02697 | -0.012591 | -120.1999 | -0.1039 | -120.4218 | 1.3432 | 1.3924 | 1.4469 | -120.6353 | -120.3458 | -0.224 | -120.4489 | 1.307 | 1.3964 | 1.4409 | -120.8343 | -0.064924 | -0.21316 | 0.37043 | 0.14861 | 0.21353 | -0.16404 | -0.10953 | -0.26392 | -0.24943 | 0.22461 | 0.12143 | 0.38535 | -0.15995 | -0.11554 | 121.9136 | 121.9627 | 122.0172 | 120.4665 | -122.1917 | 121.8773 | 121.9668 | 122.0112 | 120.3464 | -122.3907
1296.0312 | 122.2641 | -119.5038 | 2.5772 | 1.4211e-13 | -0.042126 | -0.0072928 | 0.064084 | -0.0079226 | 0.055172 | -0.0054937 | -0.00028425 | -0.0025424 | -0.0042942 | 0.027183 | -0.012377 | -119.0554 | -0.1039 | -119.2589 | 2.5061 | 2.5417 | 2.5961 | -119.4768 | -119.1919 | -0.21484 | -119.2951 | 2.4653 | 2.5503 | 2.5992 | -119.6759 | 0.026954 | -0.071065 | 0.44843 | 0.2449 | 0.21795 | -0.035547 | 0.018888 | -0.17207 | -0.11188 | 0.31186 | 0.20867 | 0.38074 | -0.026957 | 0.022031 | 122.0099 | 122.0454 | 122.0999 | 119.3999 | -122.054 | 121.9691 | 122.054 | 122.103 | 119.2889 | -122.2531
1297.7969 | 122.3328 | -119.7418 | 2.3117 | 1.4211e-13 | -0.041485 | -0.0072928 | 0.06387 | -0.007709 | 0.055172 | -0.013124 | -0.00049785 | -0.0025424 | -0.0034396 | 0.02697 | -0.012804 | -119.3117 | -0.10848 | -119.5198 | 2.2498 | 2.2852 | 2.3397 | -119.7424 | -119.4621 | -0.224 | -119.5561 | 2.1952 | 2.2939 | 2.3337 | -119.9368 | -0.000587 | -0.061953 | 0.43008 | 0.22198 | 0.22256 | -0.026465 | 0.027988 | -0.19503 | -0.11651 | 0.27975 | 0.18572 | 0.38075 | -0.017856 | 0.021974 | 121.9916 | 122.0271 | 122.0815 | 119.6333 | -122.0541 | 121.937 | 122.0357 | 122.0755 | 119.5178 | -122.2486
1299.5469 | 122.1909 | -117.2516 | 4.866 | 1.4211e-13 | -0.041912 | -0.0070792 | 0.064084 | -0.0079226 | 0.054958 | -0.0054937 | -0.00028425 | -0.0025424 | -0.003867 | 0.02697 | -0.012804 | -116.7982 | -0.085587 | -117.0064 | 4.7633 | 4.7945 | 4.8442 | -117.2057 | -116.9346 | -0.19653 | -117.0378 | 4.7088 | 4.8075 | 4.8519 | -117.4048 | 0.045903 | -0.10274 | 0.45338 | 0.24522 | 0.19931 | -0.071535 | -0.021837 | -0.15318 | -0.15724 | 0.31696 | 0.21378 | 0.36695 | -0.058525 | -0.014116 | 122.0149 | 122.0461 | 122.0958 | 117.166 | -122.0717 | 121.9604 | 122.0591 | 122.1035 | 117.0551 | -122.2708
1301.2188 | 122.2687 | -117.1555 | 4.9484 | 1.4211e-13 | -0.042126 | -0.0072928 | 0.064297 | -0.0074952 | 0.054958 | -0.0054937 | -0.00028425 | -0.0027562 | -0.0040806 | 0.027183 | -0.012591 | -116.7662 | -0.085587 | -116.9606 | 4.7999 | 4.8403 | 4.8808 | -117.1599 | -116.8843 | -0.2011 | -116.992 | 4.7592 | 4.8441 | 4.8977 | -117.3636 | -0.004438 | -0.14851 | 0.3893 | 0.19487 | 0.19931 | -0.10814 | -0.067605 | -0.2081 | -0.18927 | 0.2712 | 0.16343 | 0.37153 | -0.10429 | -0.050727 | 121.9554 | 121.9957 | 122.0363 | 117.0699 | -122.1083 | 121.9146 | 121.9996 | 122.0532 | 116.9544 | -122.312
1302.9688 | 122.3099 | -116.716 | 5.3192 | 1.4211e-13 | -0.042126 | -0.0070792 | 0.063656 | -0.0074952 | 0.055172 | -0.013124 | -0.00028425 | -0.0029698 | -0.0040806 | 0.02697 | -0.013018 | -116.2488 | -0.094744 | -116.4524 | 5.3539 | 5.3394 | 5.3936 | -116.7341 | -116.3806 | -0.21026 | -116.4884 | 5.2536 | 5.3569 | 5.4059 | -116.8507 | -0.018052 | 0.034687 | 0.4672 | 0.26361 | 0.28166 | 0.020171 | 0.074409 | -0.13472 | -0.065585 | 0.3354 | 0.22764 | 0.36236 | 0.037722 | 0.086709 | 122.0699 | 122.0554 | 122.1096 | 116.6213 | -122.0533 | 121.9696 | 122.0729 | 122.1219 | 116.5057 | -122.1699
1304.7188 | 122.319 | -115.6082 | 6.4362 | 1.4211e-13 | -0.041912 | -0.0072928 | 0.063656 | -0.007709 | 0.054745 | -0.013124 | -0.00028425 | -0.0029698 | -0.0036534 | 0.02697 | -0.013018 | -115.2095 | -0.090166 | -115.404 | 6.3657 | 6.4017 | 6.4375 | -115.5985 | -115.3367 | -0.2011 | -115.4353 | 6.3158 | 6.4009 | 6.4544 | -115.793 | 0.009734 | -0.070432 | 0.39871 | 0.20425 | 0.19451 | -0.034462 | 0.001387 | -0.1848 | -0.12032 | 0.27156 | 0.17295 | 0.35776 | -0.0353 | 0.018266 | 121.9739 | 122.0099 | 122.0458 | 115.518 | -122.0346 | 121.9241 | 122.0091 | 122.0626 | 115.4071 | -122.2292
1306.4219 | 122.2 | -116.2766 | 5.8411 | 1.4211e-13 | -0.041698 | -0.0070792 | 0.06387 | -0.0081362 | 0.054958 | -0.0054937 | -0.00049785 | -0.0027562 | -0.003867 | 0.027611 | -0.012804 | -115.8367 | -0.094744 | -116.0404 | 5.7293 | 5.7606 | 5.8149 | -116.235 | -115.9731 | -0.21026 | -116.0717 | 5.6703 | 5.7782 | 5.8226 | -116.4386 | 0.041598 | -0.11174 | 0.43981 | 0.2362 | 0.1946 | -0.080418 | -0.026209 | -0.16208 | -0.17079 | 0.30346 | 0.20485 | 0.36693 | -0.062897 | -0.018488 | 122.0059 | 122.0372 | 122.0914 | 116.1818 | -122.076 | 121.9468 | 122.0547 | 122.0991 | 116.0663 | -122.2797
1308.1719 | 122.287 | -116.5237 | 5.5206 | 1.4211e-13 | -0.041912 | -0.0072928 | 0.06387 | -0.0074952 | 0.054958 | -0.0054937 | -0.00028425 | -0.0025424 | -0.003867 | 0.027183 | -0.013018 | -116.1481 | -0.094744 | -116.3471 | 5.4134 | 5.4539 | 5.4989 | -116.5509 | -116.2707 | -0.21484 | -116.3739 | 5.3772 | 5.476 | 5.5158 | -116.7408 | -0.027155 | -0.10721 | 0.37567 | 0.17665 | 0.2038 | -0.066772 | -0.021699 | -0.21709 | -0.14338 | 0.25303 | 0.14985 | 0.36694 | -0.044651 | -0.004821 | 121.9372 | 121.9776 | 122.0227 | 116.429 | -122.0715 | 121.901 | 121.9997 | 122.0396 | 116.3089 | -122.2615
1309.9219 | 122.2733 | -116.7297 | 5.3467 | 1.4211e-13 | -0.041912 | -0.0070792 | 0.06387 | -0.0079226 | 0.055172 | -0.0054937 | -0.00049785 | -0.0025424 | -0.003867 | 0.027183 | -0.013018 | -116.3175 | -0.094744 | -116.5302 | 5.2394 | 5.2753 | 5.3158 | -116.7295 | -116.4539 | -0.21484 | -116.5479 | 5.1941 | 5.2883 | 5.3372 | -116.9148 | 0.00026 | -0.10724 | 0.41226 | 0.19951 | 0.19925 | -0.0714 | -0.030893 | -0.18509 | -0.15257 | 0.27588 | 0.18185 | 0.36694 | -0.058423 | -0.009436 | 121.9692 | 122.005 | 122.0455 | 116.635 | -122.0762 | 121.9238 | 122.018 | 122.067 | 116.5149 | -122.2615
1311.6875 | 122.2321 | -117.2653 | 4.8706 | 1.4211e-13 | -0.042126 | -0.0075064 | 0.064084 | -0.0079226 | 0.054745 | 0.0021363 | -0.00028425 | -0.0025424 | -0.0042942 | 0.02697 | -0.013018 | -116.7982 | -0.1039 | -117.0109 | 4.7587 | 4.7991 | 4.8442 | -117.2011 | -116.9346 | -0.22858 | -117.0378 | 4.7134 | 4.8212 | 4.8565 | -117.3956 | 0.064215 | -0.1119 | 0.46712 | 0.25437 | 0.19016 | -0.071533 | -0.026414 | -0.13029 | -0.15724 | 0.3307 | 0.22751 | 0.3578 | -0.049366 | -0.014114 | 122.024 | 122.0644 | 122.1095 | 117.1614 | -122.0717 | 121.9787 | 122.0866 | 122.1218 | 117.0367 | -122.2662
1313.4375 | 122.2458 | -116.9586 | 5.1407 | 1.4211e-13 | -0.042126 | -0.0072928 | 0.064297 | -0.0074952 | 0.054958 | -0.0054937 | -0.00028425 | -0.0023288 | -0.0040806 | 0.027183 | -0.013018 | -116.5784 | -0.094744 | -116.7866 | 4.9831 | 5.028 | 5.0777 | -116.9722 | -116.7011 | -0.224 | -116.8135 | 4.9423 | 5.041 | 5.0854 | -117.1667 | -0.013541 | -0.15763 | 0.38018 | 0.17201 | 0.18555 | -0.11267 | -0.062987 | -0.20805 | -0.19839 | 0.25751 | 0.14517 | 0.35321 | -0.099674 | -0.055265 | 121.9417 | 121.9866 | 122.0363 | 116.8639 | -122.1128 | 121.9009 | 121.9996 | 122.044 | 116.7346 | -122.3074
1315.125 | 122.3236 | -116.3177 | 5.6946 | 1.4211e-13 | -0.041912 | -0.0072928 | 0.06387 | -0.0081362 | 0.054958 | 0.0021363 | -0.00049785 | -0.0023288 | -0.0042942 | 0.02697 | -0.013018 | -115.9466 | -0.090166 | -116.1411 | 5.6194 | 5.6599 | 5.7004 | -116.3448 | -116.0692 | -0.224 | -116.177 | 5.5604 | 5.6729 | 5.7173 | -116.5348 | -0.027097 | -0.075133 | 0.37112 | 0.17668 | 0.20377 | -0.03467 | 0.005809 | -0.21704 | -0.13419 | 0.2485 | 0.14074 | 0.35778 | -0.021721 | 0.022688 | 121.9372 | 121.9777 | 122.0181 | 116.2276 | -122.0394 | 121.8781 | 121.9906 | 122.035 | 116.0938 | -122.2294
1316.875 | 122.2092 | -116.3406 | 5.8182 | 1.4211e-13 | -0.042339 | -0.0070792 | 0.06387 | -0.0079226 | 0.054958 | 0.0021363 | -7.0448e-05 | -0.0027562 | -0.003867 | 0.02697 | -0.013018 | -115.9192 | -0.090166 | -116.1182 | 5.6423 | 5.6828 | 5.7233 | -116.3265 | -116.0464 | -0.21942 | -116.145 | 5.597 | 5.6912 | 5.7402 | -116.5119 | 0.014107 | -0.17584 | 0.42148 | 0.22245 | 0.20835 | -0.13537 | -0.094894 | -0.17126 | -0.22116 | 0.29428 | 0.19568 | 0.36693 | -0.127 | -0.078015 | 121.983 | 122.0234 | 122.0639 | 116.2505 | -122.1447 | 121.9377 | 122.0318 | 122.0808 | 116.1212 | -122.3301
1318.5469 | 122.3007 | -116.4047 | 5.6396 | 1.4211e-13 | -0.042126 | -0.0072928 | 0.06387 | -0.0081362 | 0.054958 | 0.0021363 | -0.00049785 | -0.0027562 | -0.003867 | 0.027397 | -0.013232 | -115.997 | -0.094744 | -116.2006 | 5.5645 | 5.605 | 5.6454 | -116.3906 | -116.1196 | -0.22858 | -116.2228 | 5.5283 | 5.6271 | 5.6669 | -116.5852 | 0.014089 | -0.075141 | 0.40774 | 0.20413 | 0.19004 | -0.034685 | 0.005798 | -0.18043 | -0.11131 | 0.28511 | 0.18193 | 0.36236 | -0.012575 | 0.027255 | 121.9692 | 122.0097 | 122.0502 | 116.31 | -122.0303 | 121.9331 | 122.0318 | 122.0716 | 116.1761 | -122.2248
1320.2344 | 122.2733 | -118.8858 | 3.241 | 1.4211e-13 | -0.042339 | -0.0070792 | 0.064084 | -0.007709 | 0.054745 | 0.0021363 | -7.0448e-05 | -0.0025424 | -0.0036534 | 0.027397 | -0.013018 | -118.1992 | -0.13595 | -118.389 | 3.4218 | 3.4071 | 3.466 | -118.6114 | -118.3494 | -0.27894 | -118.4481 | 3.3215 | 3.4202 | 3.4554 | -118.7967 | 0.27439 | 0.18085 | 0.68661 | 0.49679 | 0.2224 | 0.16611 | 0.22506 | 0.08908 | 0.080537 | 0.53636 | 0.43775 | 0.34867 | 0.17922 | 0.21447 | 122.3076 | 122.2929 | 122.3518 | 118.7499 | -121.8524 | 122.2073 | 122.306 | 122.3412 | 118.6069 | -122.0377
1321.9844 | 122.3648 | -119.6411 | 2.4216 | 1.4211e-13 | -0.041912 | -0.0077202 | 0.064084 | -0.0074952 | 0.054958 | -0.0054937 | -0.00049785 | -0.0025424 | -0.003867 | 0.027397 | -0.013018 | -119.1881 | -0.11306 | -119.4008 | 2.4146 | 2.4135 | 2.4679 | -119.605 | -119.3201 | -0.26063 | -119.4279 | 2.328 | 2.4266 | 2.4665 | -119.7995 | 0.036073 | -0.006994 | 0.45299 | 0.2403 | 0.20423 | -0.008118 | 0.046326 | -0.15837 | -0.093599 | 0.32098 | 0.21322 | 0.37159 | 0.00506 | 0.04489 | 122.0557 | 122.0546 | 122.109 | 119.5281 | -122.0266 | 121.9691 | 122.0677 | 122.1076 | 119.3805 | -122.2211
1323.7344 | 122.2412 | -119.9341 | 2.179 | 1.4211e-13 | -0.042339 | -0.0072928 | 0.064084 | -0.007709 | 0.054958 | -0.0054937 | -0.00049785 | -0.0027562 | -0.0036534 | 0.027397 | -0.012804 | -119.4949 | -0.10848 | -119.7213 | 2.1078 | 2.1021 | 2.152 | -119.9256 | -119.6361 | -0.26063 | -119.7484 | 2.0121 | 2.1244 | 2.1551 | -120.1108 | 0.008517 | -0.071131 | 0.43921 | 0.21279 | 0.20428 | -0.07687 | -0.026983 | -0.17676 | -0.1669 | 0.29802 | 0.18568 | 0.36244 | -0.054513 | -0.02384 | 122.0419 | 122.0362 | 122.0861 | 119.8256 | -122.1045 | 121.9461 | 122.0585 | 122.0892 | 119.6735 | -122.2898
1325.4062 | 122.2046 | -119.9936 | 2.1881 | 1.4211e-13 | -0.042553 | -0.0070792 | 0.064084 | -0.0072816 | 0.054745 | 0.0021363 | -0.00028425 | -0.0025424 | -0.0040806 | 0.027824 | -0.012804 | -119.5315 | -0.10848 | -119.7533 | 2.062 | 2.0563 | 2.1108 | -119.9714 | -119.6818 | -0.26063 | -119.7896 | 1.98 | 2.0741 | 2.1231 | -120.1566 | 0.022237 | -0.12607 | 0.46209 | 0.24025 | 0.21802 | -0.13181 | -0.077345 | -0.16304 | -0.2081 | 0.31174 | 0.20398 | 0.36702 | -0.11403 | -0.065045 | 122.0556 | 122.0499 | 122.1044 | 119.8851 | -122.1595 | 121.9736 | 122.0677 | 122.1167 | 119.733 | -122.3447
1327.1562 | 122.3419 | -119.7418 | 2.3254 | 1.4211e-13 | -0.042339 | -0.0072928 | 0.064084 | -0.007709 | 0.054745 | -0.0054937 | -7.0448e-05 | -0.0029698 | -0.0040806 | 0.027397 | -0.012804 | -119.3163 | -0.1039 | -119.5336 | 2.291 | 2.2898 | 2.3351 | -119.7378 | -119.4575 | -0.26521 | -119.5515 | 2.2089 | 2.3076 | 2.3428 | -119.9323 | 0.003992 | -0.03448 | 0.4255 | 0.20824 | 0.20425 | -0.035618 | 0.009678 | -0.19045 | -0.11651 | 0.28433 | 0.1903 | 0.38075 | -0.017853 | 0.017399 | 122.0328 | 122.0316 | 122.0769 | 119.6379 | -122.0633 | 121.9508 | 122.0494 | 122.0847 | 119.4766 | -122.2577
1328.9062 | 122.1863 | -120.1172 | 2.0325 | 1.4211e-13 | -0.042339 | -0.0070792 | 0.063656 | -0.0079226 | 0.055172 | -0.020755 | -0.00049785 | -0.0025424 | -0.003867 | 0.027397 | -0.013018 | -119.6002 | -0.10848 | -119.822 | 1.9659 | 2.0105 | 2.065 | -120.0171 | -119.7322 | -0.26521 | -119.84 | 1.9251 | 2.0237 | 2.0635 | -120.2162 | 0.10004 | -0.066577 | 0.51701 | 0.29518 | 0.19513 | -0.021964 | 0.032508 | -0.09897 | -0.10741 | 0.38497 | 0.27721 | 0.37618 | -0.008758 | 0.031072 | 122.0831 | 122.1277 | 122.1822 | 120.0087 | -122.0496 | 122.0422 | 122.1409 | 122.1807 | 119.852 | -122.2486
1330.5938 | 122.2137 | -120.2591 | 1.9089 | 1.4211e-13 | -0.042339 | -0.0070792 | 0.064084 | -0.0079226 | 0.055172 | -0.0054937 | -0.00049785 | -0.0027562 | -0.003867 | 0.027397 | -0.012804 | -119.797 | -0.11306 | -120.0143 | 1.769 | 1.8136 | 1.8589 | -120.2278 | -119.9337 | -0.26978 | -120.046 | 1.7236 | 1.8177 | 1.8621 | -120.4176 | 0.03132 | -0.13985 | 0.46205 | 0.2448 | 0.21348 | -0.095262 | -0.049933 | -0.15853 | -0.18527 | 0.32542 | 0.21307 | 0.3716 | -0.091199 | -0.04679 | 122.0281 | 122.0727 | 122.118 | 120.146 | -122.1366 | 121.9827 | 122.0768 | 122.1212 | 119.9893 | -122.3265
1332.2812 | 122.2504 | -120.2087 | 1.8997 | 1.4211e-13 | -0.042553 | -0.0075064 | 0.064084 | -0.0079226 | 0.055172 | -0.0054937 | -7.0448e-05 | -0.0027562 | -0.0040806 | 0.027183 | -0.013018 | -119.7787 | -0.11306 | -119.996 | 1.7782 | 1.8319 | 1.8773 | -120.2003 | -119.9199 | -0.26521 | -120.0185 | 1.7419 | 1.8451 | 1.885 | -120.4039 | 0.00844 | -0.12154 | 0.43 | 0.21275 | 0.20431 | -0.06779 | -0.022463 | -0.19515 | -0.1578 | 0.2888 | 0.19019 | 0.38534 | -0.054571 | -0.014741 | 121.9869 | 122.0407 | 122.086 | 120.0957 | -122.1 | 121.9507 | 122.0539 | 122.0937 | 119.9435 | -122.3036
1334.0312 | 122.3328 | -120.0577 | 2.0279 | 1.4211e-13 | -0.042553 | -0.0072928 | 0.06387 | -0.0081362 | 0.055172 | -0.013124 | -0.00049785 | -0.0025424 | -0.0042942 | 0.027397 | -0.013018 | -119.765 | -0.099323 | -119.9868 | 1.7873 | 1.8411 | 1.891 | -120.1911 | -119.9062 | -0.26063 | -120.0094 | 1.7557 | 1.8497 | 1.8941 | -120.3902 | -0.13347 | -0.24056 | 0.29268 | 0.070849 | 0.20431 | -0.18681 | -0.1369 | -0.33247 | -0.27223 | 0.15147 | 0.048286 | 0.38076 | -0.17817 | -0.13376 | 121.845 | 121.8988 | 121.9487 | 119.9584 | -122.219 | 121.8133 | 121.9074 | 121.9518 | 119.7971 | -122.418
1335.7188 | 122.2778 | -120.1401 | 1.9455 | 1.4211e-13 | -0.042553 | -0.0072928 | 0.06387 | -0.007709 | 0.055386 | -0.013124 | -0.00028425 | -0.0023288 | -0.0040806 | 0.027611 | -0.013018 | -119.797 | -0.099323 | -120.0235 | 1.7644 | 1.8045 | 1.8544 | -120.2232 | -119.9383 | -0.26521 | -120.0414 | 1.7282 | 1.8268 | 1.8712 | -120.413 | -0.083119 | -0.18105 | 0.34303 | 0.11662 | 0.19974 | -0.14104 | -0.091133 | -0.27297 | -0.21731 | 0.20182 | 0.098633 | 0.3716 | -0.11866 | -0.074254 | 121.9045 | 121.9445 | 121.9944 | 120.0408 | -122.1687 | 121.8683 | 121.9669 | 122.0113 | 119.8749 | -122.3585
1337.4062 | 122.3282 | -120.163 | 1.8906 | 1.4211e-13 | -0.042767 | -0.0072928 | 0.06387 | -0.007709 | 0.054958 | -0.0054937 | -0.00028425 | -0.0025424 | -0.0042942 | 0.027397 | -0.013018 | -119.7742 | -0.1039 | -119.9823 | 1.7919 | 1.8411 | 1.8818 | -120.1957 | -119.9108 | -0.27894 | -120.014 | 1.7557 | 1.8543 | 1.8896 | -120.3947 | -0.032758 | -0.098649 | 0.38881 | 0.18071 | 0.21347 | -0.049477 | -0.008729 | -0.23177 | -0.1349 | 0.25218 | 0.14899 | 0.38076 | -0.036259 | -0.001008 | 121.9549 | 122.0041 | 122.0448 | 120.0591 | -122.0863 | 121.9186 | 122.0173 | 122.0525 | 119.884 | -122.2853
1339.1562 | 122.2275 | -120.1584 | 1.9867 | 1.4211e-13 | -0.042767 | -0.0072928 | 0.064084 | -0.0079226 | 0.055172 | 0.0021363 | -7.0448e-05 | -0.0025424 | -0.0042942 | 0.027611 | -0.012804 | -119.7192 | -0.11306 | -119.9456 | 1.8423 | 1.8823 | 1.9414 | -120.1499 | -119.8604 | -0.27894 | -119.9636 | 1.806 | 1.9047 | 1.9353 | -120.3489 | 0.008454 | -0.14442 | 0.43917 | 0.21276 | 0.20431 | -0.1044 | -0.045337 | -0.19056 | -0.18067 | 0.29797 | 0.19478 | 0.38534 | -0.082025 | -0.051352 | 122.0007 | 122.0407 | 122.0997 | 120.0453 | -122.1366 | 121.9644 | 122.0631 | 122.0937 | 119.8794 | -122.3356
1340.9062 | 122.168 | -120.1447 | 2.0142 | 1.4211e-13 | -0.04298 | -0.0072928 | 0.064084 | -0.007709 | 0.054958 | -0.0054937 | 0.00014315 | -0.0029698 | -0.0040806 | 0.027611 | -0.013232 | -119.6414 | -0.11764 | -119.8678 | 1.9247 | 1.9693 | 2.01 | -120.0767 | -119.7826 | -0.2881 | -119.8858 | 1.8747 | 1.9779 | 2.0178 | -120.2665 | 0.067983 | -0.089472 | 0.50327 | 0.27686 | 0.20888 | -0.044863 | -0.004124 | -0.12187 | -0.13946 | 0.36207 | 0.25889 | 0.38076 | -0.036233 | 0.003597 | 122.0693 | 122.114 | 122.1547 | 120.027 | -122.0908 | 122.0194 | 122.1226 | 122.1624 | 119.8566 | -122.2807
1342.6719 | 122.2916 | -120.1309 | 1.9547 | 1.4211e-13 | -0.042767 | -0.0070792 | 0.063443 | -0.0081362 | 0.055172 | -0.013124 | -0.00049785 | -0.0027562 | -0.0042942 | 0.027397 | -0.013018 | -119.7146 | -0.10848 | -119.9227 | 1.856 | 1.896 | 1.9414 | -120.1316 | -119.8467 | -0.27894 | -119.959 | 1.8106 | 1.923 | 1.9491 | -120.3398 | -0.000697 | -0.098638 | 0.41628 | 0.20819 | 0.20888 | -0.058617 | -0.013294 | -0.20887 | -0.14405 | 0.28424 | 0.17189 | 0.38076 | -0.031667 | -0.005573 | 121.9869 | 122.027 | 122.0723 | 120.0224 | -122.0863 | 121.9415 | 122.0539 | 122.08 | 119.852 | -122.2944
1344.4219 | 122.3328 | -120.2042 | 1.8723 | 1.4211e-13 | -0.042339 | -0.0072928 | 0.064084 | -0.0081362 | 0.055172 | -0.013124 | -0.00028425 | -0.0027562 | -0.0040806 | 0.027611 | -0.013232 | -119.7787 | -0.10848 | -119.996 | 1.7782 | 1.8274 | 1.8773 | -120.2095 | -119.9199 | -0.29268 | -120.0231 | 1.7373 | 1.8451 | 1.885 | -120.4039 | -0.005295 | -0.094073 | 0.42543 | 0.20818 | 0.21347 | -0.044903 | 0.005003 | -0.19973 | -0.13491 | 0.28422 | 0.18103 | 0.38076 | -0.027105 | 0.012725 | 121.9823 | 122.0315 | 122.0814 | 120.0957 | -122.0817 | 121.9415 | 122.0493 | 122.0891 | 119.9115 | -122.2761
1346.1094 | 122.3145 | -119.9158 | 2.1561 | 1.4211e-13 | -0.042553 | -0.0072928 | 0.06387 | -0.0079226 | 0.054958 | -0.0054937 | -0.00028425 | -0.0027562 | -0.003867 | 0.027397 | -0.012591 | -119.5223 | -0.1039 | -119.7442 | 2.0483 | 2.0883 | 2.1245 | -119.953 | -119.659 | -0.29268 | -119.7621 | 2.0075 | 2.1061 | 2.1414 | -120.1429 | -0.037268 | -0.10776 | 0.39343 | 0.17159 | 0.20886 | -0.067718 | -0.031566 | -0.22712 | -0.14859 | 0.25682 | 0.15363 | 0.38075 | -0.049939 | -0.014688 | 121.9641 | 122.0041 | 122.0403 | 119.8119 | -122.1091 | 121.9232 | 122.0219 | 122.0572 | 119.6231 | -122.299
1347.8125 | 122.2733 | -118.7988 | 3.3279 | 1.4211e-13 | -0.042553 | -0.0075064 | 0.064084 | -0.0081362 | 0.054745 | -0.0054937 | -7.0448e-05 | -0.0027562 | -0.0040806 | 0.027397 | -0.013232 | -118.158 | -0.1039 | -118.3661 | 3.4172 | 3.4574 | 3.5027 | -118.561 | -118.2899 | -0.2881 | -118.3931 | 3.3719 | 3.4706 | 3.5058 | -118.7693 | 0.23778 | 0.089301 | 0.64084 | 0.43271 | 0.19493 | 0.1295 | 0.17472 | 0.029577 | 0.043926 | 0.50891 | 0.40572 | 0.37614 | 0.14261 | 0.17786 | 122.2161 | 122.2563 | 122.3015 | 118.6949 | -121.889 | 122.1707 | 122.2694 | 122.3046 | 118.5107 | -122.0972
1349.5625 | 122.3282 | -119.0414 | 3.0121 | 1.4211e-13 | -0.042553 | -0.0075064 | 0.06387 | -0.0081362 | 0.054745 | -0.013124 | 0.00014315 | -0.0025424 | -0.0040806 | 0.027824 | -0.013232 | -118.6662 | -0.1039 | -118.8926 | 2.8953 | 2.9309 | 2.9807 | -119.0876 | -118.8165 | -0.2881 | -118.9105 | 2.8545 | 2.9577 | 2.993 | -119.2867 | -0.046179 | -0.11678 | 0.37526 | 0.14882 | 0.195 | -0.081214 | -0.031385 | -0.24521 | -0.15759 | 0.22497 | 0.13094 | 0.37616 | -0.054337 | -0.019086 | 121.9368 | 121.9723 | 122.0221 | 118.9375 | -122.0997 | 121.8959 | 121.9992 | 122.0344 | 118.7533 | -122.2987
1351.25 | 122.2183 | -118.6615 | 3.4836 | 1.4211e-13 | -0.04298 | -0.0068654 | 0.063443 | -0.0081362 | 0.054958 | -0.020755 | -0.00049785 | -0.0025424 | -0.0040806 | 0.027611 | -0.013018 | -118.1992 | -0.1039 | -118.4119 | 3.3623 | 3.4025 | 3.4569 | -118.6206 | -118.3311 | -0.2881 | -118.4435 | 3.3261 | 3.4202 | 3.4738 | -118.8196 | 0.040927 | -0.12128 | 0.46231 | 0.2496 | 0.20867 | -0.081082 | -0.026708 | -0.15812 | -0.1575 | 0.33037 | 0.21803 | 0.37615 | -0.063395 | -0.009829 | 122.0238 | 122.064 | 122.1184 | 118.5576 | -122.1042 | 121.9876 | 122.0817 | 122.1353 | 118.3734 | -122.3032
1353 | 122.319 | -118.8171 | 3.2867 | 1.4211e-13 | -0.043194 | -0.0075064 | 0.064084 | -0.0081362 | 0.054958 | 0.0021363 | -0.00049785 | -0.0027562 | -0.0040806 | 0.027397 | -0.013018 | -118.3823 | -0.099323 | -118.595 | 3.1975 | 3.2331 | 3.2783 | -118.7946 | -118.5189 | -0.30184 | -118.6129 | 3.1475 | 3.2462 | 3.2906 | -118.989 | 0.022568 | -0.089263 | 0.43481 | 0.22211 | 0.19954 | -0.053663 | -0.008434 | -0.1719 | -0.13922 | 0.29828 | 0.20425 | 0.37615 | -0.040543 | 0.003866 | 122.0146 | 122.0502 | 122.0954 | 118.7178 | -122.0813 | 121.9647 | 122.0633 | 122.1077 | 118.5153 | -122.2758
1354.75 | 122.3236 | -118.5013 | 3.5706 | 1.4211e-13 | -0.04298 | -0.0070792 | 0.063656 | -0.0079226 | 0.054745 | -0.0054937 | -7.0448e-05 | -0.0027562 | -0.004508 | 0.027611 | -0.013018 | -118.0527 | -0.10848 | -118.2746 | 3.518 | 3.5399 | 3.5897 | -118.474 | -118.1983 | -0.30641 | -118.2924 | 3.4634 | 3.5621 | 3.6111 | -118.6823 | 0.027236 | -0.05259 | 0.4486 | 0.22673 | 0.19949 | -0.030689 | 0.019097 | -0.18097 | -0.10712 | 0.30294 | 0.20891 | 0.38988 | -0.008434 | 0.040554 | 122.0192 | 122.0412 | 122.0909 | 118.3928 | -122.0446 | 121.9647 | 122.0634 | 122.1124 | 118.1949 | -122.2528
1356.4375 | 122.2 | -118.4738 | 3.653 | 1.4211e-13 | -0.04298 | -0.0075064 | 0.063656 | -0.0081362 | 0.054745 | -0.013124 | -0.00028425 | -0.0027562 | -0.0042942 | 0.027397 | -0.013232 | -118.0573 | -0.099323 | -118.2791 | 3.5042 | 3.5444 | 3.5851 | -118.4786 | -118.2029 | -0.30641 | -118.297 | 3.4634 | 3.553 | 3.602 | -118.6777 | -0.004809 | -0.14872 | 0.41655 | 0.19468 | 0.19949 | -0.10851 | -0.067879 | -0.20386 | -0.18952 | 0.27089 | 0.17686 | 0.38072 | -0.099988 | -0.051 | 121.978 | 122.0183 | 122.0589 | 118.3745 | -122.1316 | 121.9373 | 122.0268 | 122.0758 | 118.1674 | -122.3306
1358.1875 | 122.1863 | -118.0618 | 4.0833 | 1.4211e-13 | -0.042767 | -0.0075064 | 0.06387 | -0.0079226 | 0.054745 | -0.0054937 | -0.00028425 | -0.0027562 | -0.0040806 | 0.027611 | -0.013232 | -117.5811 | -0.10848 | -117.7847 | 3.9941 | 4.0252 | 4.075 | -117.9841 | -117.7084 | -0.30184 | -117.8162 | 3.9396 | 4.052 | 4.0827 | -118.1923 | 0.077728 | -0.089132 | 0.48072 | 0.27715 | 0.19942 | -0.058018 | -0.008266 | -0.13049 | -0.14365 | 0.3534 | 0.24564 | 0.37613 | -0.031218 | -0.000545 | 122.0559 | 122.0871 | 122.1368 | 117.9533 | -122.0674 | 122.0014 | 122.1139 | 122.1445 | 117.76 | -122.2756
1359.9375 | 122.2092 | -118.0344 | 4.0833 | 1.4211e-13 | -0.04298 | -0.0072928 | 0.06387 | -0.0081362 | 0.054745 | -0.013124 | -0.00049785 | -0.0025424 | -0.0042942 | 0.027611 | -0.013018 | -117.5948 | -0.099323 | -117.8167 | 3.9666 | 4.0115 | 4.0475 | -118.0207 | -117.7359 | -0.30641 | -117.8437 | 3.9259 | 4.02 | 4.069 | -118.2198 | 0.013631 | -0.1166 | 0.43952 | 0.21764 | 0.20401 | -0.071755 | -0.035738 | -0.18543 | -0.15739 | 0.29846 | 0.1907 | 0.37613 | -0.063268 | -0.014281 | 122.001 | 122.0459 | 122.0819 | 117.935 | -122.104 | 121.9602 | 122.0543 | 122.1033 | 117.7279 | -122.303
1361.7031 | 122.2137 | -117.4255 | 4.7287 | 1.4211e-13 | -0.043194 | -0.0075064 | 0.064084 | -0.0079226 | 0.054745 | -0.013124 | -0.00028425 | -0.0027562 | -0.0040806 | 0.027824 | -0.013232 | -116.9676 | -0.099323 | -117.1712 | 4.603 | 4.6434 | 4.6839 | -117.3751 | -117.104 | -0.30641 | -117.2072 | 4.5485 | 4.6564 | 4.6962 | -117.5788 | 0.050433 | -0.12565 | 0.45793 | 0.25435 | 0.20392 | -0.085311 | -0.044759 | -0.15322 | -0.18016 | 0.3215 | 0.21832 | 0.37154 | -0.07229 | -0.032459 | 122.0286 | 122.0689 | 122.1095 | 117.3262 | -122.1038 | 121.9741 | 122.0819 | 122.1218 | 117.1191 | -122.3075
1363.4062 | 122.2321 | -116.5283 | 5.6122 | 1.4211e-13 | -0.04298 | -0.0072928 | 0.06387 | -0.0081362 | 0.054531 | -0.013124 | -0.00071145 | -0.0025424 | -0.0040806 | 0.027611 | -0.013018 | -116.1435 | -0.094744 | -116.3471 | 5.4226 | 5.4676 | 5.5035 | -116.5463 | -116.2707 | -0.29726 | -116.3693 | 5.3864 | 5.4851 | 5.525 | -116.7454 | -0.017999 | -0.18961 | 0.38482 | 0.18122 | 0.19922 | -0.14459 | -0.10867 | -0.21709 | -0.22578 | 0.25761 | 0.159 | 0.37609 | -0.12705 | -0.087216 | 121.9509 | 121.9959 | 122.0318 | 116.4336 | -122.1585 | 121.9147 | 122.0135 | 122.0533 | 116.2311 | -122.3576
1365.1562 | 122.2137 | -113.681 | 8.4824 | 1.4211e-13 | -0.043408 | -0.0072928 | 0.06387 | -0.0081362 | 0.054531 | 0.0021363 | -0.00028425 | -0.0027562 | -0.003867 | 0.027397 | -0.013018 | -113.1859 | -0.081008 | -113.33 | 8.4443 | 8.2928 | 8.5162 | -113.5196 | -113.3037 | -0.29268 | -113.3611 | 8.3853 | 8.4841 | 8.3088 | -113.7188 | 0.16138 | -0.038048 | 0.49517 | 0.35102 | 0.18964 | -0.18957 | 0.033869 | -0.037785 | -0.097041 | 0.37732 | 0.31993 | 0.35771 | 0.00176 | -0.1736 | 122.1253 | 121.9738 | 122.1973 | 113.6 | -122.002 | 122.0663 | 122.1652 | 121.9898 | 113.3884 | -122.2012
1366.9062 | 122.319 | -114.4226 | 7.6263 | 1.4211e-13 | -0.043408 | -0.0070792 | 0.06387 | -0.0079226 | 0.054531 | -0.0054937 | -0.00028425 | -0.0027562 | -0.0040806 | 0.027824 | -0.013232 | -114.0558 | -0.094744 | -114.2045 | 7.5607 | 7.4091 | 7.6417 | -114.408 | -114.1874 | -0.30184 | -114.2402 | 7.5154 | 7.6142 | 7.4297 | -114.6117 | 0.014646 | -0.065659 | 0.36686 | 0.21815 | 0.2035 | -0.21728 | 0.015374 | -0.18908 | -0.11094 | 0.23521 | 0.18239 | 0.37147 | -0.012156 | -0.19668 | 121.9833 | 121.8317 | 122.0643 | 114.3279 | -122.0343 | 121.938 | 122.0368 | 121.8523 | 114.1208 | -122.238
1368.5938 | 122.2504 | -114.9261 | 7.196 | 1.4211e-13 | -0.04298 | -0.0070792 | 0.063443 | -0.0081362 | 0.054958 | -0.0054937 | -0.00028425 | -0.0025424 | -0.0042942 | 0.028038 | -0.013232 | -114.5502 | -0.099323 | -114.6943 | 7.08 | 6.942 | 7.1518 | -114.8933 | -114.6773 | -0.31099 | -114.721 | 7.0255 | 7.1334 | 6.9626 | -115.1016 | 0.03282 | -0.11609 | 0.37593 | 0.23181 | 0.19899 | -0.25404 | -0.044239 | -0.17547 | -0.17054 | 0.24883 | 0.20516 | 0.38064 | -0.062612 | -0.2334 | 122.0061 | 121.8682 | 122.078 | 114.8268 | -122.0894 | 121.9517 | 122.0596 | 121.8888 | 114.6152 | -122.2977
1370.2812 | 122.2 | -113.6078 | 8.5098 | 1.4211e-13 | -0.04298 | -0.0072928 | 0.06387 | -0.0081362 | 0.054531 | -0.013124 | 0.00014315 | -0.0025424 | -0.0040806 | 0.027611 | -0.013018 | -113.4239 | -0.07643 | -113.5772 | 8.1879 | 8.0593 | 8.2736 | -113.7669 | -113.5464 | -0.2881 | -113.6038 | 8.1472 | 8.2415 | 8.0752 | -113.9798 | -0.15912 | -0.3219 | 0.18385 | 0.030552 | 0.18967 | -0.45056 | -0.23626 | -0.37202 | -0.36259 | 0.06141 | 0.004011 | 0.37603 | -0.26837 | -0.43458 | 121.7957 | 121.6671 | 121.8814 | 113.5314 | -122.2767 | 121.755 | 121.8492 | 121.683 | 113.3197 | -122.4896
1372.0156 | 122.2366 | -113.7817 | 8.3313 | 1.4211e-13 | -0.043194 | -0.0072928 | 0.06387 | -0.0079226 | 0.054958 | -0.0054937 | -0.00049785 | -0.0027562 | -0.003867 | 0.027824 | -0.013232 | -113.4148 | -0.094744 | -113.5772 | 8.1971 | 8.0501 | 8.269 | -113.7715 | -113.5601 | -0.30641 | -113.6038 | 8.1564 | 8.246 | 8.0752 | -113.9707 | 0.010248 | -0.13422 | 0.36696 | 0.2045 | 0.19425 | -0.28119 | -0.062314 | -0.18891 | -0.1749 | 0.22162 | 0.17796 | 0.36687 | -0.085265 | -0.25605 | 121.9788 | 121.8318 | 122.0507 | 113.687 | -122.1028 | 121.9381 | 122.0278 | 121.857 | 113.4753 | -122.3019
1373.7656 | 122.2504 | -113.1821 | 8.9172 | 1.4211e-13 | -0.043194 | -0.0075064 | 0.064084 | -0.0079226 | 0.054531 | 0.0021363 | -0.00028425 | -0.0025424 | -0.0042942 | 0.027824 | -0.013232 | -112.9661 | -0.081008 | -113.124 | 8.6641 | 8.508 | 8.7223 | -113.3136 | -113.0885 | -0.29726 | -113.1413 | 8.6005 | 8.7039 | 8.5285 | -113.5128 | -0.13153 | -0.25316 | 0.21597 | 0.058081 | 0.18961 | -0.40924 | -0.19497 | -0.3307 | -0.31673 | 0.093561 | 0.040741 | 0.37144 | -0.21334 | -0.38871 | 121.8461 | 121.6901 | 121.9043 | 113.1011 | -122.2308 | 121.7826 | 121.886 | 121.7106 | 112.8848 | -122.43
1375.4375 | 122.3053 | -112.9211 | 9.1644 | 1.4211e-13 | -0.04298 | -0.0068654 | 0.06387 | -0.0081362 | 0.054531 | -0.013124 | -7.0448e-05 | -0.0027562 | -0.0040806 | 0.027824 | -0.013018 | -112.5952 | -0.085587 | -112.7348 | 9.0395 | 8.9018 | 9.1114 | -112.9244 | -112.7131 | -0.30641 | -112.7613 | 8.9897 | 9.0977 | 8.9223 | -113.1327 | -0.003246 | -0.12493 | 0.3259 | 0.18631 | 0.18956 | -0.26264 | -0.052981 | -0.21158 | -0.17475 | 0.20809 | 0.15985 | 0.37143 | -0.066775 | -0.24214 | 121.9606 | 121.8229 | 122.0326 | 112.8356 | -122.0888 | 121.9108 | 122.0188 | 121.8434 | 112.6147 | -122.2972
1377.1875 | 122.2229 | -112.1567 | 9.9609 | 1.4211e-13 | -0.043408 | -0.0077202 | 0.064084 | -0.0081362 | 0.054531 | -0.0054937 | -0.00028425 | -0.0025424 | -0.003867 | 0.028038 | -0.013018 | -111.8032 | -0.07643 | -111.9382 | 9.8361 | 9.6894 | 9.9127 | -112.1277 | -111.9118 | -0.29726 | -111.9554 | 9.7863 | 9.8852 | 9.7098 | -112.336 | 0.02902 | -0.12479 | 0.35349 | 0.21847 | 0.18945 | -0.27157 | -0.048233 | -0.17933 | -0.1746 | 0.2449 | 0.20124 | 0.38057 | -0.075763 | -0.25113 | 121.9928 | 121.846 | 122.0694 | 112.0802 | -122.0886 | 121.943 | 122.0419 | 121.8665 | 111.8594 | -122.2969
1378.875 | 122.2092 | -111.2412 | 10.881 | 1.4211e-13 | -0.043194 | -0.0072928 | 0.06387 | -0.0079226 | 0.054531 | -0.0054937 | -7.0448e-05 | -0.0027562 | -0.0040806 | 0.028252 | -0.013232 | -110.8829 | -0.081008 | -111.0226 | 10.7656 | 10.6189 | 10.8193 | -111.2119 | -110.996 | -0.29726 | -111.0443 | 10.702 | 10.8009 | 10.6255 | -111.4111 | 0.029278 | -0.11549 | 0.35822 | 0.21859 | 0.18932 | -0.26216 | -0.061775 | -0.16994 | -0.179 | 0.24511 | 0.19687 | 0.36681 | -0.080148 | -0.25551 | 122.0067 | 121.86 | 122.0604 | 111.1601 | -122.0929 | 121.9432 | 122.042 | 121.8667 | 110.9439 | -122.2921
1380.625 | 122.319 | -111.026 | 10.9817 | 1.4211e-13 | -0.043621 | -0.0075064 | 0.063656 | -0.007709 | 0.054745 | -0.0054937 | -7.0448e-05 | -0.0025424 | -0.003867 | 0.027611 | -0.013445 | -110.7318 | -0.085587 | -110.8761 | 10.9029 | 10.77 | 10.9704 | -111.0608 | -110.8495 | -0.29726 | -110.8886 | 10.8485 | 10.952 | 10.7904 | -111.26 | -0.034766 | -0.078843 | 0.29416 | 0.14995 | 0.18472 | -0.21176 | -0.011389 | -0.23399 | -0.1332 | 0.17648 | 0.1374 | 0.37139 | -0.029762 | -0.19139 | 121.9289 | 121.796 | 121.9964 | 110.9404 | -122.0425 | 121.8746 | 121.978 | 121.8164 | 110.7287 | -122.2417
1382.3125 | 122.2046 | -111.676 | 10.4553 | 1.4211e-13 | -0.043408 | -0.0075064 | 0.063656 | -0.0079226 | 0.054531 | -0.0054937 | -7.0448e-05 | -0.0029698 | -0.0040806 | 0.028038 | -0.013018 | -111.3087 | -0.090166 | -111.4483 | 10.3306 | 10.1839 | 10.3935 | -111.6286 | -111.4173 | -0.31557 | -111.4655 | 10.2717 | 10.3751 | 10.2089 | -111.8323 | 0.047471 | -0.12471 | 0.36731 | 0.22769 | 0.18022 | -0.27144 | -0.061865 | -0.15632 | -0.18366 | 0.25875 | 0.21051 | 0.36682 | -0.080238 | -0.24645 | 122.0066 | 121.8599 | 122.0695 | 111.5859 | -122.0839 | 121.9477 | 122.0511 | 121.8849 | 111.3605 | -122.2877
1384.0625 | 122.2 | -111.5753 | 10.5606 | 1.4211e-13 | -0.043621 | -0.0077202 | 0.06387 | -0.007709 | 0.054745 | -0.013124 | -0.00028425 | -0.0029698 | -0.0040806 | 0.027611 | -0.013232 | -111.2034 | -0.090166 | -111.343 | 10.4359 | 10.2984 | 10.5033 | -111.5187 | -111.3074 | -0.32015 | -111.3511 | 10.3953 | 10.485 | 10.3188 | -111.7179 | 0.056657 | -0.1247 | 0.3719 | 0.23228 | 0.17562 | -0.26225 | -0.057265 | -0.14256 | -0.16533 | 0.26793 | 0.22427 | 0.36682 | -0.075638 | -0.24184 | 122.0112 | 121.8737 | 122.0787 | 111.4852 | -122.0793 | 121.9706 | 122.0603 | 121.8941 | 111.2552 | -122.2785
1385.75 | 122.3099 | -111.5524 | 10.4919 | 1.4211e-13 | -0.043408 | -0.0070792 | 0.064297 | -0.00835 | 0.054958 | -0.0054937 | -7.0448e-05 | -0.0025424 | -0.0042942 | 0.027611 | -0.013232 | -111.2126 | -0.094744 | -111.3476 | 10.4359 | 10.2846 | 10.4942 | -111.5324 | -111.3303 | -0.31099 | -111.3694 | 10.377 | 10.4804 | 10.305 | -111.7362 | 0.020033 | -0.056032 | 0.33986 | 0.20482 | 0.18478 | -0.20732 | 0.002243 | -0.18376 | -0.11498 | 0.22215 | 0.18306 | 0.36682 | -0.011551 | -0.18691 | 121.9883 | 121.8371 | 122.0466 | 111.4577 | -122.0243 | 121.9294 | 122.0328 | 121.8575 | 111.2414 | -122.2281
1387.5 | 122.2137 | -111.9507 | 10.144 | 1.4211e-13 | -0.043621 | -0.0075064 | 0.06387 | -0.0081362 | 0.054745 | -0.013124 | -0.00028425 | -0.0031834 | -0.0040806 | 0.027824 | -0.013018 | -111.6292 | -0.085587 | -111.778 | 10.0101 | 9.8634 | 10.0775 | -111.9674 | -111.7424 | -0.32473 | -111.7906 | 9.9557 | 10.0546 | 9.8792 | -112.1712 | -0.01671 | -0.13392 | 0.32148 | 0.17271 | 0.18942 | -0.28068 | -0.06651 | -0.22049 | -0.1883 | 0.20832 | 0.16008 | 0.38057 | -0.089461 | -0.26483 | 121.9608 | 121.814 | 122.0282 | 111.8651 | -122.1114 | 121.9064 | 122.0053 | 121.8299 | 111.626 | -122.3152
1389.1875 | 122.3053 | -111.5982 | 10.4645 | 1.4211e-13 | -0.043408 | -0.0072928 | 0.063656 | -0.0081362 | 0.054531 | -0.0054937 | -0.00028425 | -0.0023288 | -0.0040806 | 0.027824 | -0.013018 | -111.2996 | -0.085587 | -111.4392 | 10.3443 | 10.1976 | 10.4026 | -111.6331 | -111.4035 | -0.33389 | -111.4564 | 10.29 | 10.3842 | 10.2135 | -111.8369 | -0.034927 | -0.12013 | 0.29865 | 0.15903 | 0.19395 | -0.26685 | -0.061864 | -0.23871 | -0.1745 | 0.19466 | 0.14184 | 0.38056 | -0.080237 | -0.25102 | 121.9426 | 121.7958 | 122.0008 | 111.5126 | -122.0976 | 121.8882 | 121.9824 | 121.8117 | 111.2643 | -122.3014
1390.9375 | 122.2412 | -111.1221 | 10.9863 | 1.4211e-13 | -0.043835 | -0.0072928 | 0.063656 | -0.0079226 | 0.054958 | -0.0054937 | -0.00071145 | -0.0027562 | -0.0042942 | 0.028038 | -0.013232 | -110.7364 | -0.090166 | -110.8761 | 10.9075 | 10.7517 | 10.9704 | -111.0608 | -110.8404 | -0.33389 | -110.9023 | 10.844 | 10.9474 | 10.7858 | -111.26 | 0.061364 | -0.078843 | 0.38571 | 0.24608 | 0.18472 | -0.23465 | -0.015967 | -0.13786 | -0.14236 | 0.28177 | 0.21979 | 0.35765 | -0.038919 | -0.20055 | 122.0296 | 121.8738 | 122.0925 | 111.032 | -122.0471 | 121.9661 | 122.0695 | 121.9079 | 110.7882 | -122.2463
1392.625 | 122.3373 | -111.5387 | 10.524 | 1.4211e-13 | -0.043835 | -0.0072928 | 0.06387 | -0.0079226 | 0.054531 | 0.0021363 | -0.00028425 | -0.0025424 | -0.0040806 | 0.027611 | -0.013445 | -111.2172 | -0.094744 | -111.3522 | 10.4268 | 10.2892 | 10.4896 | -111.5416 | -111.3211 | -0.34304 | -111.3785 | 10.3724 | 10.4758 | 10.305 | -111.7499 | -0.002858 | -0.097232 | 0.32155 | 0.1865 | 0.18936 | -0.23479 | -0.034379 | -0.21123 | -0.1516 | 0.21757 | 0.16017 | 0.3714 | -0.048174 | -0.21896 | 121.9655 | 121.8279 | 122.0283 | 111.444 | -122.0655 | 121.9111 | 122.0145 | 121.8437 | 111.1957 | -122.2739
1394.3125 | 122.2916 | -111.8317 | 10.2127 | 1.4211e-13 | -0.043835 | -0.0072928 | 0.06387 | -0.0081362 | 0.054745 | 0.0021363 | 0.00014315 | -0.0025424 | -0.0040806 | 0.028038 | -0.013232 | -111.4873 | -0.099323 | -111.636 | 10.1521 | 10.0007 | 10.2057 | -111.8346 | -111.6096 | -0.35678 | -111.6716 | 10.0885 | 10.1874 | 10.0212 | -112.0292 | -0.00294 | -0.060657 | 0.34439 | 0.19562 | 0.19856 | -0.21198 | -0.006974 | -0.19757 | -0.12419 | 0.22208 | 0.1601 | 0.35767 | -0.025347 | -0.19155 | 121.9837 | 121.8324 | 122.0374 | 111.7323 | -122.0473 | 121.9202 | 122.019 | 121.8528 | 111.4749 | -122.2419
1396.0469 | 122.3465 | -112.2849 | 9.7641 | 1.4211e-13 | -0.043621 | -0.0072928 | 0.06387 | -0.00835 | 0.054745 | -0.0054937 | -7.0448e-05 | -0.0027562 | -0.003867 | 0.027611 | -0.013232 | -111.9588 | -0.099323 | -112.0985 | 9.6805 | 9.5383 | 9.7479 | -112.2833 | -112.0675 | -0.3522 | -112.1203 | 9.6352 | 9.7295 | 9.5587 | -112.4871 | 0.001511 | -0.083622 | 0.326 | 0.1864 | 0.18489 | -0.22584 | -0.016225 | -0.20226 | -0.12885 | 0.2174 | 0.16458 | 0.36684 | -0.034598 | -0.20538 | 121.9653 | 121.8231 | 122.0327 | 112.1855 | -122.0474 | 121.9201 | 122.0144 | 121.8436 | 111.9326 | -122.2512
1397.7969 | 122.3602 | -112.4817 | 9.5673 | 1.4211e-13 | -0.043835 | -0.0072928 | 0.063656 | -0.0079226 | 0.054531 | -0.0054937 | -0.00028425 | -0.0027562 | -0.0042942 | 0.027611 | -0.013018 | -112.1603 | -0.094744 | -112.2953 | 9.4836 | 9.3276 | 9.5464 | -112.4985 | -112.2781 | -0.36136 | -112.3355 | 9.4246 | 9.5235 | 9.3527 | -112.7023 | -0.01686 | -0.083654 | 0.32139 | 0.18637 | 0.20323 | -0.23963 | -0.020845 | -0.22063 | -0.14262 | 0.20361 | 0.14621 | 0.36684 | -0.043797 | -0.21458 | 121.9653 | 121.8093 | 122.0281 | 112.3869 | -122.0658 | 121.9063 | 122.0052 | 121.8344 | 112.1203 | -122.2696
1399.5469 | 122.2916 | -113.0768 | 9.0088 | 1.4211e-13 | -0.043408 | -0.0072928 | 0.063656 | -0.007709 | 0.054317 | -0.0054937 | -0.00028425 | -0.0029698 | -0.0040806 | 0.027824 | -0.013232 | -112.7967 | -0.1039 | -112.9454 | 8.8381 | 8.6912 | 8.9054 | -113.1396 | -112.9054 | -0.36594 | -112.9719 | 8.7836 | 8.887 | 8.7208 | -113.3571 | -0.062817 | -0.17074 | 0.28009 | 0.13135 | 0.19416 | -0.31763 | -0.10338 | -0.28031 | -0.22514 | 0.17142 | 0.10487 | 0.38517 | -0.12175 | -0.28796 | 121.9148 | 121.7679 | 121.9822 | 112.9729 | -122.1484 | 121.8604 | 121.9638 | 121.7976 | 112.7108 | -122.3659
1401.2188 | 122.3419 | -113.8641 | 8.1482 | 1.4211e-13 | -0.043621 | -0.0072928 | 0.063656 | -0.00835 | 0.054745 | -0.020755 | -0.00049785 | -0.0025424 | -0.0040806 | 0.028038 | -0.013232 | -113.5384 | -0.10848 | -113.6871 | 8.0872 | 7.9494 | 8.1637 | -113.8951 | -113.6608 | -0.3751 | -113.7228 | 8.0374 | 8.1407 | 7.9654 | -114.0897 | -0.030985 | -0.060995 | 0.32574 | 0.17702 | 0.20801 | -0.19882 | 0.015485 | -0.22556 | -0.11084 | 0.20329 | 0.14131 | 0.36688 | -0.007467 | -0.18283 | 121.9513 | 121.8135 | 122.0278 | 113.7557 | -122.0433 | 121.9015 | 122.0049 | 121.8295 | 113.489 | -122.2379
1402.9688 | 122.3328 | -114.0015 | 8.0383 | 1.4211e-13 | -0.044049 | -0.0072928 | 0.063443 | -0.0079226 | 0.054745 | -0.0054937 | -7.0448e-05 | -0.0025424 | -0.0036534 | 0.027824 | -0.013445 | -113.7169 | -0.1039 | -113.8748 | 7.9178 | 7.7662 | 7.9851 | -114.0645 | -113.8394 | -0.38425 | -113.8922 | 7.8542 | 7.9576 | 7.7914 | -114.2729 | -0.063077 | -0.12053 | 0.28451 | 0.12664 | 0.18972 | -0.27212 | -0.053218 | -0.27139 | -0.18412 | 0.16205 | 0.10923 | 0.38062 | -0.080748 | -0.24695 | 121.9193 | 121.7677 | 121.9866 | 113.8976 | -122.1029 | 121.8557 | 121.959 | 121.7928 | 113.6172 | -122.3112
1404.6562 | 122.2183 | -113.974 | 8.1802 | 1.4211e-13 | -0.044049 | -0.0072928 | 0.06387 | -0.00835 | 0.054531 | -0.0054937 | -7.0448e-05 | -0.0027562 | -0.003867 | 0.028252 | -0.013232 | -113.6712 | -0.1039 | -113.8245 | 7.959 | 7.8257 | 8.0263 | -114.0188 | -113.7936 | -0.38883 | -113.8419 | 7.9092 | 8.0125 | 7.8372 | -114.2271 | -0.044753 | -0.22123 | 0.30283 | 0.14954 | 0.19429 | -0.3545 | -0.15392 | -0.25306 | -0.27108 | 0.18037 | 0.13213 | 0.38519 | -0.16771 | -0.34308 | 121.933 | 121.7997 | 122.0003 | 113.8701 | -122.199 | 121.8832 | 121.9865 | 121.8112 | 113.5852 | -122.4073
1406.3906 | 122.2916 | -114.4455 | 7.6401 | 1.4211e-13 | -0.044262 | -0.0075064 | 0.06387 | -0.00835 | 0.054531 | -0.013124 | -0.00028425 | -0.0027562 | -0.0040806 | 0.028038 | -0.013445 | -114.1794 | -0.099323 | -114.3464 | 7.4462 | 7.2992 | 7.5181 | -114.5362 | -114.3064 | -0.39799 | -114.3593 | 7.3918 | 7.4951 | 7.3244 | -114.7399 | -0.090675 | -0.19385 | 0.26613 | 0.099108 | 0.18978 | -0.34091 | -0.12198 | -0.29439 | -0.24829 | 0.13905 | 0.086232 | 0.38063 | -0.14493 | -0.31572 | 121.8917 | 121.7447 | 121.9636 | 114.3462 | -122.1762 | 121.8373 | 121.9406 | 121.7699 | 114.0475 | -122.38
1408.0938 | 122.3648 | -114.9857 | 7.077 | 1.4211e-13 | -0.044049 | -0.0075064 | 0.063656 | -0.0079226 | 0.054745 | -0.0054937 | -0.00028425 | -0.0027562 | -0.0042942 | 0.028252 | -0.013018 | -114.6006 | -0.1039 | -114.7584 | 7.0387 | 6.8962 | 7.106 | -114.9437 | -114.7231 | -0.40257 | -114.7805 | 6.9889 | 7.0785 | 6.9031 | -115.1657 | 0.041962 | -0.038278 | 0.38508 | 0.22722 | 0.18526 | -0.18081 | 0.028994 | -0.18006 | -0.088147 | 0.26255 | 0.20515 | 0.38522 | 0.001464 | -0.1739 | 122.0244 | 121.8819 | 122.0917 | 114.8818 | -122.0207 | 121.9745 | 122.0641 | 121.8888 | 114.5831 | -122.2427
1409.8438 | 122.2321 | -114.8529 | 7.3013 | 1.4211e-13 | -0.044262 | -0.0075064 | 0.06387 | -0.0079226 | 0.054317 | -0.0054937 | 0.00014315 | -0.0025424 | -0.0040806 | 0.028679 | -0.013018 | -114.4129 | -0.10848 | -114.5753 | 7.2127 | 7.084 | 7.2937 | -114.7605 | -114.5308 | -0.40257 | -114.5928 | 7.1674 | 7.2708 | 7.0954 | -114.9688 | 0.092367 | -0.088605 | 0.44004 | 0.2776 | 0.18524 | -0.21738 | -0.007588 | -0.11593 | -0.13389 | 0.3221 | 0.26013 | 0.37605 | -0.03054 | -0.2059 | 122.0656 | 121.9369 | 122.1466 | 114.7444 | -122.0619 | 122.0203 | 122.1237 | 121.9483 | 114.4503 | -122.2702
1411.5469 | 122.2458 | -115.2603 | 6.8756 | 1.4211e-13 | -0.044262 | -0.0077202 | 0.06387 | -0.0081362 | 0.054745 | 0.0021363 | -0.00028425 | -0.0025424 | -0.0042942 | 0.028252 | -0.013018 | -114.8982 | -0.10848 | -115.0606 | 6.7274 | 6.5803 | 6.8084 | -115.2596 | -115.0161 | -0.4163 | -115.0735 | 6.6821 | 6.7809 | 6.5964 | -115.4588 | 0.000674 | -0.14819 | 0.36214 | 0.19972 | 0.19904 | -0.29534 | -0.067199 | -0.19845 | -0.19349 | 0.24417 | 0.18677 | 0.38522 | -0.094729 | -0.27925 | 121.9877 | 121.8406 | 122.0687 | 115.1518 | -122.1353 | 121.9424 | 122.0412 | 121.8567 | 114.844 | -122.3344
1413.2344 | 122.2183 | -115.2649 | 6.8756 | 1.4211e-13 | -0.044262 | -0.0077202 | 0.06387 | -0.0081362 | 0.054317 | -0.0054937 | -0.00028425 | -0.0025424 | -0.0040806 | 0.028679 | -0.013445 | -114.8753 | -0.1039 | -115.0377 | 6.7503 | 6.6032 | 6.8221 | -115.2367 | -115.007 | -0.41173 | -115.0598 | 6.7096 | 6.8038 | 6.6238 | -115.4404 | 0.028147 | -0.1253 | 0.38961 | 0.22719 | 0.19904 | -0.27244 | -0.053463 | -0.17556 | -0.16602 | 0.25791 | 0.20509 | 0.38064 | -0.071836 | -0.25178 | 122.0152 | 121.8681 | 122.087 | 115.161 | -122.1124 | 121.9745 | 122.0687 | 121.8887 | 114.8532 | -122.3161
1414.9688 | 122.2275 | -115.3198 | 6.8207 | 1.4211e-13 | -0.044476 | -0.0075064 | 0.063656 | -0.0079226 | 0.054531 | 0.0021363 | -0.00028425 | -0.0025424 | -0.003867 | 0.028252 | -0.013232 | -114.9714 | -0.1039 | -115.1293 | 6.6679 | 6.5299 | 6.7397 | -115.3237 | -115.0802 | -0.42088 | -115.1468 | 6.6134 | 6.7122 | 6.5368 | -115.532 | -0.003922 | -0.15278 | 0.3484 | 0.19055 | 0.19447 | -0.29077 | -0.080947 | -0.2122 | -0.20724 | 0.23958 | 0.17302 | 0.38523 | -0.10848 | -0.28384 | 121.9877 | 121.8497 | 122.0596 | 115.2159 | -122.1444 | 121.9333 | 122.032 | 121.8567 | 114.8989 | -122.3527
1416.7188 | 122.2961 | -115.567 | 6.514 | 1.4211e-13 | -0.044049 | -0.0077202 | 0.064084 | -0.0081362 | 0.054745 | 0.0021363 | -0.00049785 | -0.0029698 | -0.0042942 | 0.028038 | -0.013445 | -115.2232 | -0.11306 | -115.3811 | 6.4161 | 6.2735 | 6.4879 | -115.5756 | -115.3367 | -0.43004 | -115.3986 | 6.3662 | 6.465 | 6.2896 | -115.7839 | -0.00857 | -0.09789 | 0.34378 | 0.18594 | 0.19451 | -0.24049 | -0.026068 | -0.21684 | -0.14777 | 0.23036 | 0.16839 | 0.38523 | -0.04902 | -0.22438 | 121.9831 | 121.8405 | 122.0549 | 115.454 | -122.0896 | 121.9332 | 122.032 | 121.8566 | 115.137 | -122.2978
1418.4062 | 122.319 | -115.6769 | 6.3629 | 1.4211e-13 | -0.044262 | -0.0079338 | 0.06387 | -0.0079226 | 0.054531 | 0.0097668 | -0.00028425 | -0.0027562 | -0.003867 | 0.028252 | -0.013232 | -115.356 | -0.1039 | -115.5093 | 6.2787 | 6.1407 | 6.3689 | -115.7084 | -115.4694 | -0.44378 | -115.5223 | 6.2334 | 6.3413 | 6.1614 | -115.9121 | -0.031496 | -0.08418 | 0.32087 | 0.16761 | 0.19911 | -0.22222 | 0.00595 | -0.23519 | -0.12949 | 0.20744 | 0.15462 | 0.38981 | -0.02158 | -0.20152 | 121.9556 | 121.8176 | 122.0457 | 115.573 | -122.0713 | 121.9103 | 122.0182 | 121.8383 | 115.2331 | -122.275
1420.1562 | 122.3145 | -115.5716 | 6.4957 | 1.4211e-13 | -0.044476 | -0.0077202 | 0.063656 | -0.00835 | 0.054317 | -0.0054937 | -7.0448e-05 | -0.0027562 | -0.004508 | 0.027824 | -0.013445 | -115.1912 | -0.1039 | -115.3536 | 6.4344 | 6.2964 | 6.5108 | -115.5527 | -115.3183 | -0.4392 | -115.3803 | 6.3799 | 6.4787 | 6.3125 | -115.7564 | 0.018902 | -0.061267 | 0.3804 | 0.21798 | 0.19908 | -0.19929 | 0.015135 | -0.18479 | -0.11573 | 0.25326 | 0.19128 | 0.37607 | -0.016974 | -0.18318 | 122.006 | 121.868 | 122.0824 | 115.4677 | -122.0484 | 121.9515 | 122.0503 | 121.8841 | 115.1324 | -122.2521
1421.8594 | 122.3282 | -115.4022 | 6.6833 | 1.4211e-13 | -0.04469 | -0.0077202 | 0.063656 | -0.0081362 | 0.054531 | -0.0054937 | -0.00028425 | -0.0025424 | -0.003867 | 0.028038 | -0.013445 | -115.0538 | -0.10848 | -115.2208 | 6.5809 | 6.4429 | 6.6436 | -115.4107 | -115.1764 | -0.44378 | -115.2292 | 6.5265 | 6.6252 | 6.459 | -115.6236 | -0.008523 | -0.10244 | 0.34838 | 0.18138 | 0.18991 | -0.24044 | -0.039768 | -0.22138 | -0.1569 | 0.22582 | 0.173 | 0.39438 | -0.058141 | -0.22435 | 121.9831 | 121.8451 | 122.0458 | 115.2937 | -122.0941 | 121.9287 | 122.0274 | 121.8612 | 114.9584 | -122.307
1423.6094 | 122.2137 | -115.3564 | 6.8069 | 1.4211e-13 | -0.044476 | -0.0077202 | 0.063656 | -0.0081362 | 0.054104 | -0.013124 | -0.00049785 | -0.0025424 | -0.003867 | 0.028038 | -0.013018 | -114.9943 | -0.10848 | -115.1567 | 6.6313 | 6.4933 | 6.7077 | -115.3512 | -115.1215 | -0.45293 | -115.1789 | 6.5814 | 6.6756 | 6.5048 | -115.5641 | 0.005226 | -0.17568 | 0.36212 | 0.1997 | 0.19448 | -0.31367 | -0.099264 | -0.20763 | -0.22555 | 0.23499 | 0.17759 | 0.38523 | -0.13137 | -0.30216 | 121.9877 | 121.8497 | 122.0641 | 115.248 | -122.1582 | 121.9378 | 122.032 | 121.8612 | 114.9035 | -122.371
1425.2969 | 122.374 | -115.2878 | 6.7657 | 1.4211e-13 | -0.044262 | -0.0077202 | 0.063656 | -0.0081362 | 0.054745 | -0.013124 | -0.00028425 | -0.0025424 | -0.0040806 | 0.028465 | -0.013018 | -114.9577 | -0.1039 | -115.1155 | 6.6725 | 6.5345 | 6.7535 | -115.3054 | -115.0802 | -0.44836 | -115.1376 | 6.6318 | 6.7305 | 6.546 | -115.5229 | -0.017649 | -0.09327 | 0.33009 | 0.17224 | 0.18989 | -0.23126 | -0.012279 | -0.23509 | -0.13399 | 0.20753 | 0.15014 | 0.38522 | -0.035231 | -0.21975 | 121.9603 | 121.8223 | 122.0412 | 115.1839 | -122.0712 | 121.9195 | 122.0183 | 121.8338 | 114.8394 | -122.2886
1427.0625 | 122.2641 | -115.4526 | 6.665 | 1.4211e-13 | -0.044476 | -0.0075064 | 0.063656 | -0.0079226 | 0.054531 | -0.013124 | -7.0448e-05 | -0.0027562 | -0.0042942 | 0.028252 | -0.013445 | -115.1042 | -0.10848 | -115.2575 | 6.5351 | 6.388 | 6.6161 | -115.4565 | -115.2222 | -0.45751 | -115.2796 | 6.4898 | 6.5886 | 6.4041 | -115.6694 | -0.003959 | -0.12991 | 0.34837 | 0.19511 | 0.19907 | -0.27708 | -0.048929 | -0.21682 | -0.17522 | 0.23039 | 0.17299 | 0.38981 | -0.076459 | -0.26098 | 121.9877 | 121.8405 | 122.0687 | 115.3441 | -122.1216 | 121.9424 | 122.0412 | 121.8566 | 114.9951 | -122.3344
1428.75 | 122.3602 | -115.9195 | 6.134 | 1.4211e-13 | -0.044262 | -0.0075064 | 0.063656 | -0.0079226 | 0.054958 | -0.013124 | -0.00028425 | -0.0027562 | -0.0040806 | 0.028252 | -0.013232 | -115.5483 | -0.11306 | -115.7107 | 6.0819 | 5.9438 | 6.1628 | -115.9053 | -115.6755 | -0.47125 | -115.7375 | 6.0366 | 6.1353 | 5.9599 | -116.1181 | 0.014226 | -0.052168 | 0.37119 | 0.20878 | 0.19455 | -0.19023 | 0.028795 | -0.19862 | -0.097481 | 0.24402 | 0.18204 | 0.38066 | 0.001265 | -0.1741 | 122.0014 | 121.8633 | 122.0823 | 115.8064 | -122.0393 | 121.956 | 122.0548 | 121.8794 | 115.4482 | -122.2521
1430.4375 | 122.3511 | -116.1667 | 5.8594 | 1.4211e-13 | -0.044476 | -0.0072928 | 0.063656 | -0.0081362 | 0.054745 | 0.0021363 | -0.00071145 | -0.0027562 | -0.0040806 | 0.028252 | -0.013232 | -115.8413 | -0.12222 | -116.0129 | 5.798 | 5.6599 | 5.8744 | -116.2075 | -115.9685 | -0.47125 | -116.0168 | 5.7481 | 5.8514 | 5.6669 | -116.4112 | -0.040791 | -0.061371 | 0.32536 | 0.1538 | 0.1946 | -0.19947 | 0.015001 | -0.24447 | -0.11127 | 0.19817 | 0.14993 | 0.3944 | -0.00795 | -0.19247 | 121.9647 | 121.8266 | 122.0411 | 116.0445 | -122.0669 | 121.9148 | 122.0181 | 121.8336 | 115.6954 | -122.2705
1432.1875 | 122.3419 | -116.2125 | 5.8411 | 1.4211e-13 | -0.044262 | -0.0077202 | 0.063443 | -0.00835 | 0.054531 | -0.013124 | -7.0448e-05 | -0.0027562 | -0.0042942 | 0.028038 | -0.013232 | -115.8871 | -0.11764 | -116.0632 | 5.7476 | 5.605 | 5.8286 | -116.2441 | -116.0097 | -0.47583 | -116.0625 | 5.6932 | 5.7919 | 5.6165 | -116.4615 | -0.031647 | -0.093422 | 0.32536 | 0.14922 | 0.18087 | -0.2361 | -0.012474 | -0.24906 | -0.1479 | 0.20274 | 0.14992 | 0.39898 | -0.049161 | -0.22452 | 121.9601 | 121.8174 | 122.0411 | 116.0948 | -122.0852 | 121.9056 | 122.0044 | 121.829 | 115.7366 | -122.3026
1433.9375 | 122.1954 | -116.153 | 5.9967 | 1.4211e-13 | -0.044903 | -0.0079338 | 0.063656 | -0.0081362 | 0.054745 | -0.0054937 | -0.00028425 | -0.0029698 | -0.0040806 | 0.028038 | -0.013018 | -115.8184 | -0.11306 | -115.99 | 5.8209 | 5.6782 | 5.8973 | -116.1754 | -115.9365 | -0.48956 | -115.9984 | 5.7664 | 5.8789 | 5.6898 | -116.3883 | -0.022472 | -0.17581 | 0.33452 | 0.16296 | 0.18544 | -0.31848 | -0.099435 | -0.23531 | -0.23028 | 0.21649 | 0.15451 | 0.38982 | -0.11781 | -0.30691 | 121.9738 | 121.8312 | 122.0502 | 116.0399 | -122.1721 | 121.9194 | 122.0318 | 121.8427 | 115.6634 | -122.385
1435.6875 | 122.3465 | -116.4871 | 5.5847 | 1.4211e-13 | -0.04469 | -0.0075064 | 0.064084 | -0.0079226 | 0.054531 | -0.0054937 | -0.00028425 | -0.0027562 | -0.004508 | 0.028038 | -0.013018 | -116.1435 | -0.12222 | -116.3105 | 5.4913 | 5.3531 | 5.5768 | -116.496 | -116.2524 | -0.48956 | -116.3144 | 5.4505 | 5.5447 | 5.3739 | -116.7042 | -0.008829 | -0.093465 | 0.34363 | 0.17665 | 0.18548 | -0.2316 | -0.00795 | -0.21708 | -0.13421 | 0.23473 | 0.17275 | 0.38983 | -0.040059 | -0.21084 | 121.9784 | 121.8402 | 122.0639 | 116.3649 | -122.0807 | 121.9376 | 122.0318 | 121.861 | 115.9976 | -122.2889
1437.375 | 122.2687 | -116.5558 | 5.5618 | 1.4211e-13 | -0.04469 | -0.0075064 | 0.06387 | -0.0081362 | 0.054317 | 0.0021363 | -0.00028425 | -0.0029698 | -0.0040806 | 0.028679 | -0.013445 | -116.2488 | -0.11306 | -116.4203 | 5.386 | 5.257 | 5.4715 | -116.6104 | -116.376 | -0.49414 | -116.4197 | 5.3315 | 5.4394 | 5.2594 | -116.8233 | -0.054638 | -0.17588 | 0.30699 | 0.13544 | 0.19007 | -0.30487 | -0.09037 | -0.26747 | -0.23036 | 0.17977 | 0.1361 | 0.40357 | -0.12248 | -0.30242 | 121.9417 | 121.8127 | 122.0272 | 116.4427 | -122.1723 | 121.8872 | 121.9951 | 121.8152 | 116.0616 | -122.3851
1439.125 | 122.2275 | -116.5375 | 5.6259 | 1.4211e-13 | -0.044903 | -0.0077202 | 0.063443 | -0.0081362 | 0.054317 | -0.013124 | -7.0448e-05 | -0.0027562 | -0.0042942 | 0.028465 | -0.013445 | -116.171 | -0.11764 | -116.3425 | 5.4592 | 5.3211 | 5.5401 | -116.5372 | -116.2982 | -0.5033 | -116.351 | 5.4139 | 5.5126 | 5.3235 | -116.7454 | 0.000315 | -0.16671 | 0.36651 | 0.19496 | 0.19464 | -0.30485 | -0.085778 | -0.20794 | -0.21204 | 0.23929 | 0.18647 | 0.39441 | -0.11331 | -0.30241 | 121.9967 | 121.8585 | 122.0776 | 116.4198 | -122.1631 | 121.9514 | 122.0501 | 121.861 | 116.0342 | -122.3713
1440.875 | 122.2595 | -116.5192 | 5.5893 | 1.4211e-13 | -0.044476 | -0.0072928 | 0.063443 | -0.00835 | 0.054531 | -0.0054937 | -0.00028425 | -0.0025424 | -0.0042942 | 0.028465 | -0.013659 | -116.1664 | -0.11764 | -116.3379 | 5.4729 | 5.3256 | 5.5447 | -116.528 | -116.2936 | -0.50788 | -116.3464 | 5.4139 | 5.5218 | 5.3464 | -116.7454 | -0.008838 | -0.11635 | 0.35278 | 0.18122 | 0.19006 | -0.26365 | -0.044577 | -0.22625 | -0.17542 | 0.22556 | 0.17274 | 0.39899 | -0.067529 | -0.24289 | 121.9921 | 121.8448 | 122.0639 | 116.4015 | -122.1173 | 121.933 | 122.0409 | 121.8656 | 116.0113 | -122.3347
1442.625 | 122.2321 | -116.6931 | 5.4428 | 1.4211e-13 | -0.044262 | -0.0077202 | 0.063656 | -0.007709 | 0.054317 | -0.0054937 | -0.00028425 | -0.0027562 | -0.0040806 | 0.028252 | -0.013232 | -116.3266 | -0.11764 | -116.5028 | 5.3081 | 5.17 | 5.3799 | -116.6928 | -116.4539 | -0.51704 | -116.5113 | 5.2582 | 5.3615 | 5.1724 | -116.9057 | 0.000271 | -0.13469 | 0.36648 | 0.19036 | 0.19009 | -0.27284 | -0.062923 | -0.21256 | -0.1846 | 0.23926 | 0.18186 | 0.39441 | -0.081296 | -0.2704 | 122.0012 | 121.8631 | 122.073 | 116.5755 | -122.1357 | 121.9513 | 122.0546 | 121.8655 | 116.1761 | -122.3485
1444.3125 | 122.2366 | -116.9083 | 5.2597 | 1.4211e-13 | -0.044476 | -0.0079338 | 0.06387 | -0.0081362 | 0.054531 | -0.0054937 | -0.00028425 | -0.0027562 | -0.003867 | 0.028252 | -0.013018 | -116.4777 | -0.12222 | -116.6493 | 5.1479 | 5.0143 | 5.238 | -116.8439 | -116.6095 | -0.52619 | -116.6578 | 5.1071 | 5.2058 | 5.0259 | -117.0614 | 0.064315 | -0.11183 | 0.43055 | 0.259 | 0.19469 | -0.24542 | -0.021754 | -0.15309 | -0.15259 | 0.29873 | 0.25049 | 0.40358 | -0.053863 | -0.23381 | 122.0561 | 121.9225 | 122.1462 | 116.786 | -122.1037 | 122.0154 | 122.1141 | 121.9342 | 116.3821 | -122.3211
1446 | 122.3511 | -116.9952 | 5.0583 | 1.4211e-13 | -0.044903 | -0.0079338 | 0.063443 | -0.0081362 | 0.054317 | 0.0021363 | -0.00028425 | -0.0025424 | -0.0042942 | 0.028252 | -0.013232 | -116.6609 | -0.11764 | -116.8461 | 4.9693 | 4.822 | 5.0456 | -117.0317 | -116.7835 | -0.53077 | -116.8409 | 4.9194 | 5.0227 | 4.8473 | -117.2445 | -0.036446 | -0.088973 | 0.33438 | 0.14911 | 0.18556 | -0.23632 | -0.01264 | -0.24927 | -0.13889 | 0.21171 | 0.15431 | 0.40358 | -0.035591 | -0.21096 | 121.9646 | 121.8172 | 122.0409 | 116.8776 | -122.09 | 121.9146 | 122.0179 | 121.8426 | 116.4645 | -122.3028
1447.75 | 122.3373 | -117.16 | 4.8706 | 1.4211e-13 | -0.044903 | -0.0077202 | 0.063656 | -0.0079226 | 0.054317 | -0.013124 | -0.00028425 | -0.0025424 | -0.0042942 | 0.028465 | -0.013659 | -116.8531 | -0.11764 | -117.0384 | 4.7724 | 4.6434 | 4.8625 | -117.2194 | -116.9758 | -0.53535 | -117.0378 | 4.7271 | 4.8396 | 4.6505 | -117.4322 | -0.059387 | -0.098159 | 0.30689 | 0.12162 | 0.181 | -0.22722 | -0.0081 | -0.2722 | -0.1435 | 0.1842 | 0.12223 | 0.39443 | -0.031051 | -0.22015 | 121.9325 | 121.8034 | 122.0225 | 117.0424 | -122.09 | 121.8871 | 121.9996 | 121.8105 | 116.6247 | -122.3028
1449.4531 | 122.3419 | -117.2882 | 4.7974 | 1.4211e-13 | -0.044903 | -0.0079338 | 0.063443 | -0.0079226 | 0.054317 | -0.013124 | -7.0448e-05 | -0.0025424 | -0.0042942 | 0.028252 | -0.013018 | -116.9493 | -0.12679 | -117.13 | 4.6809 | 4.5427 | 4.7572 | -117.3202 | -117.0766 | -0.53535 | -117.134 | 4.6264 | 4.7342 | 4.5497 | -117.5375 | -0.031949 | -0.11648 | 0.33892 | 0.15823 | 0.19017 | -0.25471 | -0.040166 | -0.24934 | -0.17099 | 0.21165 | 0.15425 | 0.40359 | -0.063117 | -0.24764 | 121.9691 | 121.8309 | 122.0454 | 117.1614 | -122.1175 | 121.9146 | 122.0225 | 121.8379 | 116.7529 | -122.3349
1451.1875 | 122.3145 | -117.3523 | 4.7287 | 1.4211e-13 | -0.045117 | -0.0077202 | 0.063656 | -0.00835 | 0.054317 | -0.0054937 | -7.0448e-05 | -0.0025424 | -0.0040806 | 0.028465 | -0.013232 | -116.9951 | -0.13137 | -117.1666 | 4.6397 | 4.506 | 4.7206 | -117.3568 | -117.1178 | -0.54909 | -117.1706 | 4.5897 | 4.6885 | 4.5177 | -117.5696 | -0.004493 | -0.089027 | 0.35722 | 0.18569 | 0.19018 | -0.22268 | -0.008131 | -0.2173 | -0.13895 | 0.23452 | 0.1817 | 0.39901 | -0.040239 | -0.21102 | 121.992 | 121.8583 | 122.0729 | 117.2209 | -122.0855 | 121.942 | 122.0408 | 121.87 | 116.8032 | -122.2983
1452.9375 | 122.2046 | -117.572 | 4.5639 | 1.4211e-13 | -0.044903 | -0.0077202 | 0.063443 | -0.0081362 | 0.054531 | -0.0054937 | -0.00028425 | -0.0025424 | -0.0042942 | 0.028679 | -0.013445 | -117.1828 | -0.12222 | -117.3497 | 4.4565 | 4.3137 | 4.5466 | -117.5445 | -117.3009 | -0.55366 | -117.3583 | 4.4203 | 4.5145 | 4.3254 | -117.7573 | 0.027497 | -0.10737 | 0.38923 | 0.22228 | 0.19478 | -0.2502 | -0.017322 | -0.18531 | -0.14356 | 0.2711 | 0.2137 | 0.39901 | -0.049431 | -0.23853 | 122.0286 | 121.8857 | 122.1186 | 117.4498 | -122.1084 | 121.9924 | 122.0865 | 121.8974 | 117.0184 | -122.3212
1454.6875 | 122.3511 | -117.6315 | 4.4174 | 1.4211e-13 | -0.044903 | -0.0075064 | 0.06387 | -0.00835 | 0.054104 | -0.013124 | -7.0448e-05 | -0.0027562 | -0.004508 | 0.028679 | -0.013659 | -117.2698 | -0.11306 | -117.455 | 4.365 | 4.2221 | 4.4413 | -117.6498 | -117.3925 | -0.57198 | -117.4545 | 4.315 | 4.4137 | 4.2384 | -117.8581 | -0.018309 | -0.05245 | 0.36175 | 0.17649 | 0.1948 | -0.19529 | 0.023855 | -0.22653 | -0.10238 | 0.23904 | 0.17706 | 0.40359 | -0.003675 | -0.17904 | 121.9965 | 121.8537 | 122.0728 | 117.5185 | -122.0673 | 121.9466 | 122.0453 | 121.8699 | 117.0596 | -122.2755
1456.375 | 122.2687 | -117.746 | 4.3991 | 1.4211e-13 | -0.044903 | -0.0077202 | 0.06387 | -0.0081362 | 0.054317 | 0.0021363 | -0.00028425 | -0.0029698 | -0.0040806 | 0.028252 | -0.013445 | -117.3797 | -0.12222 | -117.5558 | 4.2642 | 4.1214 | 4.3451 | -117.7368 | -117.4932 | -0.5674 | -117.5369 | 4.2235 | 4.3176 | 4.1376 | -117.9588 | 0.009133 | -0.13486 | 0.36631 | 0.19021 | 0.18108 | -0.27772 | -0.053986 | -0.21283 | -0.17564 | 0.25275 | 0.20908 | 0.42191 | -0.081516 | -0.26146 | 122.0102 | 121.8674 | 122.0911 | 117.6238 | -122.1359 | 121.9694 | 122.0636 | 121.8836 | 117.1786 | -122.3579
1458.125 | 122.3511 | -117.8192 | 4.2526 | 1.4211e-13 | -0.045331 | -0.0079338 | 0.063443 | -0.0085636 | 0.054531 | 0.0021363 | -0.00028425 | -0.0027562 | -0.004508 | 0.028679 | -0.013232 | -117.4529 | -0.12679 | -117.6336 | 4.1773 | 4.0435 | 4.2627 | -117.8238 | -117.5802 | -0.57198 | -117.633 | 4.1365 | 4.2352 | 4.0598 | -118.0458 | -0.004625 | -0.07537 | 0.3663 | 0.18562 | 0.19025 | -0.20908 | 0.010083 | -0.22658 | -0.11615 | 0.23899 | 0.18617 | 0.41276 | -0.017447 | -0.19281 | 121.9965 | 121.8628 | 122.0819 | 117.6924 | -122.0765 | 121.9557 | 122.0544 | 121.879 | 117.2472 | -122.2984
1459.875 | 122.3465 | -117.9611 | 4.1107 | 1.4211e-13 | -0.045117 | -0.0079338 | 0.063656 | -0.0081362 | 0.054531 | -0.0054937 | -0.00028425 | -0.0029698 | -0.0042942 | 0.028465 | -0.013445 | -117.5903 | -0.13137 | -117.7664 | 4.0445 | 3.9108 | 4.1299 | -117.9658 | -117.7176 | -0.58114 | -117.7796 | 3.9945 | 4.0932 | 3.927 | -118.1832 | -0.004664 | -0.066236 | 0.37086 | 0.19476 | 0.19942 | -0.19996 | 0.019211 | -0.22204 | -0.11618 | 0.24354 | 0.18156 | 0.4036 | -0.017477 | -0.18368 | 122.0056 | 121.8719 | 122.0911 | 117.8297 | -122.0765 | 121.9557 | 122.0544 | 121.8882 | 117.38 | -122.2939
1461.625 | 122.3419 | -118.6295 | 3.4332 | 1.4211e-13 | -0.045331 | -0.0077202 | 0.063656 | -0.0081362 | 0.054531 | -0.013124 | -0.00028425 | -0.0023288 | -0.0040806 | 0.028679 | -0.013445 | -118.2908 | -0.13137 | -118.4806 | 3.344 | 3.2193 | 3.434 | -118.6664 | -118.4181 | -0.59945 | -118.4755 | 3.294 | 3.4019 | 3.2265 | -118.8929 | -0.036905 | -0.089239 | 0.3387 | 0.14888 | 0.18579 | -0.21389 | 0.000753 | -0.26342 | -0.13919 | 0.21133 | 0.15393 | 0.41736 | -0.031356 | -0.20672 | 121.9734 | 121.8488 | 122.0634 | 118.4981 | -122.0996 | 121.9235 | 122.0313 | 121.856 | 118.03 | -122.3261
1463.2969 | 122.2687 | -118.7485 | 3.3783 | 1.4211e-13 | -0.045331 | -0.0079338 | 0.06387 | -0.0081362 | 0.054104 | 0.0021363 | -0.00028425 | -0.0027562 | -0.004508 | 0.028465 | -0.013445 | -118.3869 | -0.12679 | -118.563 | 3.2524 | 3.114 | 3.3424 | -118.7625 | -118.5097 | -0.60403 | -118.5763 | 3.207 | 3.3057 | 3.1258 | -118.9845 | -0.014044 | -0.12588 | 0.36157 | 0.18549 | 0.19953 | -0.26427 | -0.035887 | -0.23598 | -0.17125 | 0.23877 | 0.17222 | 0.4082 | -0.072574 | -0.25252 | 122.0009 | 121.8625 | 122.0909 | 118.6217 | -122.1408 | 121.9555 | 122.0542 | 121.8743 | 118.1444 | -122.3628
1465.0469 | 122.2321 | -118.8812 | 3.3234 | 1.4211e-13 | -0.045117 | -0.0077202 | 0.063656 | -0.00835 | 0.054104 | -0.013124 | -0.00028425 | -0.0027562 | -0.0040806 | 0.028252 | -0.013445 | -118.4647 | -0.12679 | -118.6454 | 3.1746 | 3.0316 | 3.2692 | -118.8358 | -118.583 | -0.60861 | -118.6449 | 3.1292 | 3.2279 | 3.0434 | -119.0623 | 0.045445 | -0.14878 | 0.41649 | 0.23583 | 0.19039 | -0.29176 | -0.054212 | -0.18107 | -0.19416 | 0.29827 | 0.23629 | 0.41736 | -0.095479 | -0.28 | 122.0558 | 121.9128 | 122.1504 | 118.7544 | -122.1591 | 122.0104 | 122.1091 | 121.9246 | 118.2726 | -122.3857
1466.7969 | 122.3373 | -118.8126 | 3.2501 | 1.4211e-13 | -0.045544 | -0.0077202 | 0.063656 | -0.0081362 | 0.054104 | 0.0021363 | -0.00092505 | -0.0027562 | -0.0040806 | 0.028465 | -0.013232 | -118.5105 | -0.12679 | -118.6912 | 3.1288 | 2.9904 | 3.2096 | -118.8861 | -118.6379 | -0.62235 | -118.6907 | 3.0788 | 3.1775 | 3.0022 | -119.1127 | -0.073588 | -0.12132 | 0.30204 | 0.12139 | 0.19497 | -0.25972 | -0.040492 | -0.3001 | -0.17128 | 0.17466 | 0.12184 | 0.42194 | -0.072601 | -0.24797 | 121.9414 | 121.803 | 122.0222 | 118.6858 | -122.1363 | 121.8914 | 121.9901 | 121.8147 | 118.1902 | -122.3628
1468.5625 | 122.2641 | -118.8904 | 3.2501 | 1.4211e-13 | -0.044903 | -0.0081476 | 0.063443 | -0.00835 | 0.054317 | -0.0054937 | -0.00049785 | -0.0027562 | -0.0042942 | 0.028679 | -0.013445 | -118.4876 | -0.12222 | -118.6591 | 3.1563 | 3.0133 | 3.2371 | -118.8587 | -118.615 | -0.62692 | -118.6633 | 3.1063 | 3.205 | 3.0205 | -119.0943 | 0.031705 | -0.093847 | 0.40275 | 0.23125 | 0.19955 | -0.23683 | -0.013021 | -0.20397 | -0.14381 | 0.27537 | 0.22713 | 0.4311 | -0.04513 | -0.22965 | 122.0467 | 121.9037 | 122.1275 | 118.7682 | -122.1088 | 121.9967 | 122.0954 | 121.9109 | 118.2635 | -122.3445
1470.25 | 122.3145 | -118.8858 | 3.2318 | 1.4211e-13 | -0.045331 | -0.0077202 | 0.064084 | -0.0079226 | 0.054104 | -0.013124 | -0.00049785 | -0.0027562 | -0.004508 | 0.028679 | -0.013445 | -118.4693 | -0.12679 | -118.6591 | 3.17 | 3.0179 | 3.2508 | -118.8495 | -118.6013 | -0.62235 | -118.6587 | 3.1246 | 3.2187 | 3.0388 | -119.0806 | 0.036285 | -0.061802 | 0.41649 | 0.22668 | 0.19039 | -0.21394 | 0.019025 | -0.19481 | -0.10718 | 0.28453 | 0.22713 | 0.42194 | -0.013084 | -0.19303 | 122.0558 | 121.9037 | 122.1366 | 118.759 | -122.0813 | 122.0104 | 122.1045 | 121.9246 | 118.2635 | -122.3124
1472.0312 | 122.2412 | -118.9133 | 3.2547 | 1.4211e-13 | -0.045117 | -0.0077202 | 0.063656 | -0.00835 | 0.054104 | 0.0097668 | -0.00049785 | -0.0025424 | -0.004508 | 0.028679 | -0.013232 | -118.4968 | -0.13137 | -118.682 | 3.138 | 2.9996 | 3.2188 | -118.877 | -118.6242 | -0.64066 | -118.677 | 3.088 | 3.1867 | 3.0067 | -119.1218 | 0.036278 | -0.11674 | 0.41648 | 0.23125 | 0.19497 | -0.25515 | -0.035913 | -0.20855 | -0.1667 | 0.2891 | 0.23628 | 0.44483 | -0.068022 | -0.24797 | 122.0512 | 121.9128 | 122.1321 | 118.7819 | -122.1317 | 122.0013 | 122.0999 | 121.92 | 118.2726 | -122.3765
1473.7812 | 122.2595 | -118.8995 | 3.2593 | 1.4211e-13 | -0.045331 | -0.0079338 | 0.064084 | -0.0081362 | 0.054317 | -0.013124 | -0.00028425 | -0.0027562 | -0.0042942 | 0.028679 | -0.013445 | -118.4876 | -0.12679 | -118.6729 | 3.1563 | 3.0133 | 3.2371 | -118.8633 | -118.6196 | -0.64066 | -118.6724 | 3.1063 | 3.2096 | 3.0159 | -119.0943 | 0.036281 | -0.103 | 0.41191 | 0.22667 | 0.19039 | -0.24599 | -0.022176 | -0.19481 | -0.15296 | 0.27995 | 0.22713 | 0.42194 | -0.049706 | -0.24338 | 122.0558 | 121.9128 | 122.1366 | 118.7727 | -122.1225 | 122.0059 | 122.1091 | 121.9154 | 118.2589 | -122.3536
1475.4688 | 122.2549 | -118.9682 | 3.1677 | 1.4211e-13 | -0.045331 | -0.0081476 | 0.063443 | -0.00835 | 0.054317 | -0.013124 | -7.0448e-05 | -0.0025424 | -0.0042942 | 0.028679 | -0.013445 | -118.5746 | -0.12679 | -118.7599 | 3.0647 | 2.9263 | 3.1593 | -118.9503 | -118.702 | -0.64524 | -118.7548 | 3.0193 | 3.118 | 2.9289 | -119.1951 | 0.017947 | -0.10302 | 0.39358 | 0.20835 | 0.1904 | -0.24143 | -0.00846 | -0.22688 | -0.1484 | 0.2662 | 0.21338 | 0.44026 | -0.049726 | -0.23883 | 122.0329 | 121.8945 | 122.1275 | 118.8414 | -122.118 | 121.9875 | 122.0862 | 121.8971 | 118.323 | -122.3628
1477.2188 | 122.3236 | -118.9682 | 3.1265 | 1.4211e-13 | -0.045758 | -0.0077202 | 0.063656 | -0.0081362 | 0.054317 | 0.0021363 | -0.00049785 | -0.0029698 | -0.004508 | 0.028893 | -0.013232 | -118.6204 | -0.12679 | -118.8011 | 3.0143 | 2.8759 | 3.1089 | -119.0006 | -118.7478 | -0.64066 | -118.8098 | 2.969 | 3.0676 | 2.8877 | -119.2409 | -0.032421 | -0.11218 | 0.3478 | 0.16715 | 0.19957 | -0.2506 | -0.017626 | -0.27267 | -0.15757 | 0.22041 | 0.15843 | 0.4311 | -0.058892 | -0.23883 | 121.9825 | 121.8441 | 122.0771 | 118.8414 | -122.1271 | 121.9372 | 122.0358 | 121.8559 | 118.3275 | -122.3674
1478.9844 | 122.2961 | -119.0781 | 3.0304 | 1.4211e-13 | -0.045331 | -0.0081476 | 0.063656 | -0.00835 | 0.054531 | 0.0021363 | -0.00071145 | -0.0029698 | -0.0042942 | 0.028679 | -0.013232 | -118.6891 | -0.13137 | -118.8743 | 2.9502 | 2.8164 | 3.0448 | -119.0739 | -118.8119 | -0.6544 | -118.8693 | 2.9094 | 3.0081 | 2.8282 | -119.3004 | 0.004179 | -0.080149 | 0.38898 | 0.20376 | 0.19958 | -0.214 | 0.014404 | -0.22233 | -0.12096 | 0.26617 | 0.20877 | 0.4311 | -0.022283 | -0.20223 | 122.0283 | 121.8945 | 122.1229 | 118.9467 | -122.1043 | 121.9875 | 122.0862 | 121.9062 | 118.4237 | -122.3308
1480.6719 | 122.2458 | -119.3024 | 2.8519 | 1.4211e-13 | -0.045544 | -0.0079338 | 0.063229 | -0.0081362 | 0.054317 | 0.0021363 | -0.00028425 | -0.0027562 | -0.0042942 | 0.028465 | -0.013659 | -118.8997 | -0.12679 | -119.0803 | 2.7488 | 2.6058 | 2.8296 | -119.2799 | -119.0225 | -0.65897 | -119.0845 | 2.6942 | 2.8021 | 2.6176 | -119.5248 | 0.022431 | -0.10307 | 0.40268 | 0.22204 | 0.19961 | -0.2461 | -0.022262 | -0.22239 | -0.15762 | 0.27985 | 0.21788 | 0.44026 | -0.049793 | -0.23431 | 122.0512 | 121.9081 | 122.132 | 119.1756 | -122.1318 | 121.9966 | 122.1044 | 121.9199 | 118.6434 | -122.3766
1482.3438 | 122.3557 | -119.3756 | 2.7145 | 1.4211e-13 | -0.045758 | -0.0079338 | 0.06387 | -0.0079226 | 0.054104 | -0.0054937 | -0.00028425 | -0.0023288 | -0.0040806 | 0.028679 | -0.013232 | -119.0141 | -0.13595 | -119.1994 | 2.6206 | 2.4867 | 2.7106 | -119.3944 | -119.1416 | -0.67271 | -119.2081 | 2.5752 | 2.6785 | 2.4985 | -119.6392 | -0.0188 | -0.093936 | 0.36146 | 0.17624 | 0.19504 | -0.22782 | -0.003977 | -0.26362 | -0.13933 | 0.23405 | 0.16749 | 0.43111 | -0.036086 | -0.21603 | 121.9962 | 121.8623 | 122.0862 | 119.2397 | -122.1089 | 121.9508 | 122.0541 | 121.8741 | 118.7029 | -122.3538
1484.0938 | 122.3053 | -119.4855 | 2.623 | 1.4211e-13 | -0.045758 | -0.0079338 | 0.063443 | -0.0085636 | 0.054104 | -0.013124 | -0.00049785 | -0.0027562 | -0.0040806 | 0.028679 | -0.013232 | -119.1011 | -0.13137 | -119.2955 | 2.5245 | 2.3997 | 2.6236 | -119.4906 | -119.2331 | -0.67729 | -119.2997 | 2.4836 | 2.5869 | 2.4115 | -119.7354 | -0.005093 | -0.098529 | 0.38434 | 0.18997 | 0.19506 | -0.22327 | 0.000583 | -0.24991 | -0.13935 | 0.25234 | 0.18578 | 0.43569 | -0.036105 | -0.21147 | 122.0099 | 121.8852 | 122.109 | 119.3541 | -122.1136 | 121.9691 | 122.0724 | 121.897 | 118.8082 | -122.3584
1485.7656 | 122.2778 | -119.5404 | 2.6093 | 1.4211e-13 | -0.045758 | -0.0081476 | 0.063443 | -0.00835 | 0.05389 | 0.0021363 | -0.00028425 | -0.0027562 | -0.0042942 | 0.028679 | -0.013232 | -119.179 | -0.13595 | -119.3596 | 2.4604 | 2.331 | 2.5595 | -119.5593 | -119.3064 | -0.68645 | -119.3638 | 2.4195 | 2.5182 | 2.3383 | -119.7995 | -0.018846 | -0.14889 | 0.36144 | 0.1808 | 0.19965 | -0.27822 | -0.049785 | -0.25908 | -0.18971 | 0.23401 | 0.17661 | 0.43569 | -0.091051 | -0.27099 | 122.0008 | 121.8714 | 122.0999 | 119.4045 | -122.1685 | 121.9599 | 122.0586 | 121.8787 | 118.854 | -122.4087
1487.4531 | 122.2687 | -119.7235 | 2.417 | 1.4211e-13 | -0.045544 | -0.0079338 | 0.063656 | -0.00835 | 0.05389 | 0.0021363 | -7.0448e-05 | -0.0025424 | -0.004508 | 0.028679 | -0.013445 | -119.3346 | -0.13137 | -119.5198 | 2.3047 | 2.1753 | 2.3946 | -119.7149 | -119.4621 | -0.69561 | -119.5195 | 2.273 | 2.3671 | 2.1826 | -119.9643 | 0.008577 | -0.1123 | 0.38888 | 0.20367 | 0.19509 | -0.24164 | -0.022354 | -0.24081 | -0.14396 | 0.26144 | 0.20404 | 0.44485 | -0.049884 | -0.23441 | 122.0282 | 121.8989 | 122.1181 | 119.5921 | -122.1319 | 121.9965 | 122.0906 | 121.9061 | 119.0279 | -122.3813
1489.1406 | 122.3648 | -119.751 | 2.3346 | 1.4211e-13 | -0.045544 | -0.0079338 | 0.063443 | -0.0085636 | 0.054104 | 0.0021363 | -7.0448e-05 | -0.0029698 | -0.0042942 | 0.029107 | -0.013232 | -119.3942 | -0.12222 | -119.5748 | 2.236 | 2.1021 | 2.3305 | -119.779 | -119.5216 | -0.69561 | -119.5836 | 2.1998 | 2.303 | 2.1276 | -120.033 | -0.028062 | -0.098576 | 0.35683 | 0.17619 | 0.20426 | -0.23251 | -0.004057 | -0.28203 | -0.13482 | 0.22938 | 0.16741 | 0.44943 | -0.031587 | -0.20695 | 121.987 | 121.8531 | 122.0815 | 119.6288 | -122.1136 | 121.9507 | 122.054 | 121.8786 | 119.0554 | -122.3676
1490.8906 | 122.2275 | -119.8746 | 2.3163 | 1.4211e-13 | -0.045758 | -0.0077202 | 0.063443 | -0.00835 | 0.054317 | -0.0054937 | -0.00049785 | -0.0027562 | -0.0042942 | 0.028893 | -0.013445 | -119.4537 | -0.13137 | -119.648 | 2.1719 | 2.038 | 2.2664 | -119.8431 | -119.5949 | -0.71392 | -119.6568 | 2.1311 | 2.2298 | 2.0406 | -120.0925 | 0.031429 | -0.14436 | 0.4209 | 0.22654 | 0.19511 | -0.2783 | -0.049846 | -0.21796 | -0.18519 | 0.27972 | 0.21774 | 0.4357 | -0.086534 | -0.27563 | 122.0465 | 121.9126 | 122.141 | 119.7432 | -122.1594 | 122.0057 | 122.1043 | 121.9152 | 119.1607 | -122.4088
1492.6406 | 122.3511 | -119.8837 | 2.211 | 1.4211e-13 | -0.045544 | -0.0077202 | 0.063443 | -0.0085636 | 0.054317 | -0.0054937 | -0.00028425 | -0.0029698 | -0.004508 | 0.028893 | -0.013232 | -119.5178 | -0.13137 | -119.7167 | 2.1216 | 1.983 | 2.2069 | -119.9027 | -119.6498 | -0.7185 | -119.7072 | 2.0762 | 2.1794 | 1.9994 | -120.1475 | -0.018942 | -0.08944 | 0.36596 | 0.16702 | 0.18596 | -0.22797 | -0.004083 | -0.26375 | -0.13485 | 0.23393 | 0.17653 | 0.44028 | -0.031614 | -0.21156 | 122.0053 | 121.8668 | 122.0906 | 119.7524 | -122.1137 | 121.9599 | 122.0631 | 121.8832 | 119.1652 | -122.3585
1494.3281 | 122.3236 | -119.9707 | 2.1423 | 1.4211e-13 | -0.045544 | -0.0077202 | 0.06387 | -0.0085636 | 0.054104 | -0.013124 | -0.00028425 | -0.0029698 | -0.004508 | 0.028893 | -0.013659 | -119.6048 | -0.13595 | -119.79 | 2.0391 | 1.9006 | 2.1291 | -119.9805 | -119.7276 | -0.7185 | -119.7896 | 2.0121 | 2.1061 | 1.9079 | -120.2391 | -0.009809 | -0.10319 | 0.36595 | 0.18074 | 0.19055 | -0.24172 | -0.013255 | -0.26835 | -0.13028 | 0.24307 | 0.18109 | 0.44944 | -0.036206 | -0.23446 | 122.0099 | 121.8713 | 122.0998 | 119.8348 | -122.1228 | 121.9828 | 122.0768 | 121.8786 | 119.2522 | -122.3814
1496.0781 | 122.2961 | -120.0256 | 2.0737 | 1.4211e-13 | -0.045758 | -0.0079338 | 0.063656 | -0.0081362 | 0.054317 | -0.0054937 | -0.00049785 | -0.0025424 | -0.0040806 | 0.028679 | -0.013445 | -119.6414 | -0.13595 | -119.8403 | 1.9888 | 1.8594 | 2.0879 | -120.04 | -119.7688 | -0.73223 | -119.8354 | 1.9571 | 2.0466 | 1.8667 | -120.2757 | -0.014403 | -0.084883 | 0.38425 | 0.18531 | 0.19971 | -0.21427 | 0.014203 | -0.25005 | -0.11656 | 0.25679 | 0.19023 | 0.44028 | -0.027063 | -0.20701 | 122.0144 | 121.885 | 122.1135 | 119.8897 | -122.1137 | 121.9827 | 122.0722 | 121.8923 | 119.2934 | -122.3494
1497.8125 | 122.2549 | -120.108 | 2.0737 | 1.4211e-13 | -0.045758 | -0.0079338 | 0.06387 | -0.0081362 | 0.054104 | 0.0097668 | -0.00028425 | -0.0029698 | -0.0042942 | 0.028893 | -0.013445 | -119.6917 | -0.13137 | -119.8907 | 1.9384 | 1.8045 | 2.0421 | -120.0812 | -119.8238 | -0.74139 | -119.8766 | 1.9159 | 1.9962 | 1.8117 | -120.3306 | 0.026784 | -0.13525 | 0.41629 | 0.21735 | 0.19056 | -0.26921 | -0.031583 | -0.2226 | -0.15776 | 0.28424 | 0.23142 | 0.45402 | -0.077428 | -0.26195 | 122.0465 | 121.9125 | 122.1501 | 119.9767 | -122.1549 | 122.0239 | 122.1043 | 121.9198 | 119.3666 | -122.4043
1499.5781 | 122.3236 | -120.1218 | 1.9867 | 1.4211e-13 | -0.046185 | -0.0079338 | 0.063229 | -0.00835 | 0.054531 | 0.0021363 | -0.00049785 | -0.0029698 | -0.004508 | 0.029107 | -0.013659 | -119.7421 | -0.14053 | -119.9319 | 1.8926 | 1.7678 | 1.9871 | -120.1225 | -119.8742 | -0.75055 | -119.9316 | 1.861 | 1.955 | 1.7751 | -120.3718 | -0.000694 | -0.094054 | 0.37966 | 0.18988 | 0.19057 | -0.21887 | 0.000449 | -0.25007 | -0.12573 | 0.24761 | 0.19021 | 0.44028 | -0.03166 | -0.2116 | 122.0144 | 121.8896 | 122.1089 | 119.9812 | -122.1092 | 121.9827 | 122.0768 | 121.8969 | 119.3712 | -122.3585
1501.2656 | 122.2641 | -120.1584 | 1.9958 | 1.4211e-13 | -0.045972 | -0.0079338 | 0.063656 | -0.00835 | 0.054104 | -0.0054937 | -0.00049785 | -0.0029698 | -0.004508 | 0.028679 | -0.013445 | -119.7696 | -0.13595 | -119.9548 | 1.8743 | 1.7404 | 1.9597 | -120.1499 | -119.897 | -0.75513 | -119.959 | 1.8426 | 1.9276 | 1.7476 | -120.3947 | 0.008454 | -0.12152 | 0.38881 | 0.2036 | 0.19515 | -0.2555 | -0.036179 | -0.23635 | -0.1532 | 0.26134 | 0.19936 | 0.4357 | -0.068288 | -0.24823 | 122.0327 | 121.8987 | 122.1181 | 120.0224 | -122.1458 | 122.001 | 122.0859 | 121.906 | 119.4033 | -122.3906
1503.0312 | 122.2504 | -120.2087 | 1.9501 | 1.4211e-13 | -0.046185 | -0.0081476 | 0.063443 | -0.00835 | 0.054317 | -0.0054937 | -0.00049785 | -0.0025424 | -0.0042942 | 0.029107 | -0.013232 | -119.8291 | -0.13595 | -120.0189 | 1.8011 | 1.6762 | 1.9047 | -120.214 | -119.9612 | -0.76429 | -120.0185 | 1.7831 | 1.868 | 1.6881 | -120.468 | -0.005297 | -0.149 | 0.37964 | 0.18986 | 0.19516 | -0.27383 | -0.045345 | -0.25925 | -0.16694 | 0.24759 | 0.19019 | 0.44944 | -0.082032 | -0.26197 | 122.0098 | 121.885 | 122.1135 | 120.0728 | -122.1641 | 121.9919 | 122.0768 | 121.8968 | 119.4445 | -122.4181
1504.7812 | 122.2641 | -120.2545 | 1.886 | 1.4211e-13 | -0.045972 | -0.0079338 | 0.063656 | -0.0085636 | 0.054317 | 0.0021363 | -0.00049785 | -0.0021152 | -0.0042942 | 0.029107 | -0.013873 | -119.8795 | -0.14053 | -120.0601 | 1.7599 | 1.6305 | 1.8589 | -120.2598 | -120.0024 | -0.77802 | -120.0689 | 1.7328 | 1.8223 | 1.6377 | -120.5 | -0.005309 | -0.12612 | 0.37506 | 0.19444 | 0.19974 | -0.25553 | -0.027044 | -0.24553 | -0.15322 | 0.25216 | 0.1856 | 0.43113 | -0.063732 | -0.24825 | 122.0144 | 121.885 | 122.1135 | 120.114 | -122.1458 | 121.9873 | 122.0768 | 121.8923 | 119.4765 | -122.386
1506.4688 | 122.2092 | -120.3186 | 1.8539 | 1.4211e-13 | -0.046185 | -0.0081476 | 0.063656 | -0.0081362 | 0.054104 | -0.013124 | -0.00049785 | -0.0025424 | -0.0042942 | 0.029107 | -0.013018 | -119.9207 | -0.13137 | -120.1104 | 1.7095 | 1.5892 | 1.8086 | -120.3148 | -120.0481 | -0.79176 | -120.1101 | 1.6916 | 1.781 | 1.6011 | -120.555 | 0.00383 | -0.14444 | 0.39794 | 0.20816 | 0.20433 | -0.2647 | -0.045366 | -0.23639 | -0.16238 | 0.27046 | 0.20848 | 0.44487 | -0.072896 | -0.25284 | 122.0281 | 121.9078 | 122.1272 | 120.1872 | -122.1687 | 122.0102 | 122.0997 | 121.9197 | 119.5268 | -122.4089
1508.2188 | 122.3602 | -120.3369 | 1.7624 | 1.4211e-13 | -0.046185 | -0.0079338 | 0.063443 | -0.00835 | 0.054104 | -0.0054937 | -7.0448e-05 | -0.0029698 | -0.0042942 | 0.028679 | -0.013232 | -119.9619 | -0.14053 | -120.1654 | 1.6683 | 1.5435 | 1.7628 | -120.356 | -120.0939 | -0.79176 | -120.1468 | 1.6504 | 1.7307 | 1.5599 | -120.5962 | -0.01907 | -0.094091 | 0.37504 | 0.17153 | 0.1906 | -0.21893 | 0.000401 | -0.25929 | -0.11204 | 0.24298 | 0.19016 | 0.44945 | -0.031708 | -0.20249 | 122.0052 | 121.8804 | 122.0997 | 120.1964 | -122.1184 | 121.9873 | 122.0676 | 121.8968 | 119.5452 | -122.3586
1509.9688 | 122.3465 | -120.3369 | 1.7303 | 1.4211e-13 | -0.046185 | -0.0079338 | 0.063656 | -0.00835 | 0.054104 | -0.0054937 | 0.00014315 | -0.0029698 | -0.0042942 | 0.028893 | -0.013659 | -119.9939 | -0.14053 | -120.1883 | 1.65 | 1.516 | 1.7353 | -120.388 | -120.1168 | -0.80092 | -120.1834 | 1.6183 | 1.7078 | 1.5278 | -120.6237 | -0.051122 | -0.080362 | 0.34299 | 0.14864 | 0.19976 | -0.21436 | 0.004973 | -0.28676 | -0.11204 | 0.22009 | 0.15353 | 0.44029 | -0.022558 | -0.2025 | 121.9869 | 121.8529 | 122.0722 | 120.1964 | -122.1184 | 121.9552 | 122.0447 | 121.8648 | 119.536 | -122.354
1511.7188 | 122.2275 | -120.4147 | 1.7532 | 1.4211e-13 | -0.046185 | -0.0079338 | 0.063443 | -0.0081362 | 0.054531 | -0.0054937 | -0.00028425 | -0.0027562 | -0.0042942 | 0.028893 | -0.013659 | -120.0214 | -0.14053 | -120.2203 | 1.6134 | 1.4839 | 1.7078 | -120.4201 | -120.1535 | -0.81007 | -120.2246 | 1.5908 | 1.6666 | 1.4958 | -120.6557 | -0.005355 | -0.13988 | 0.39334 | 0.19441 | 0.19977 | -0.2693 | -0.045387 | -0.24099 | -0.1624 | 0.26128 | 0.19014 | 0.43113 | -0.086653 | -0.25744 | 122.0281 | 121.8987 | 122.1226 | 120.2742 | -122.1733 | 122.0056 | 122.0813 | 121.9105 | 119.6047 | -122.409
1513.4062 | 122.2183 | -120.4834 | 1.7166 | 1.4211e-13 | -0.046399 | -0.0077202 | 0.063443 | -0.00835 | 0.054104 | 0.0021363 | -7.0448e-05 | -0.0025424 | -0.004508 | 0.02932 | -0.013659 | -120.0672 | -0.14511 | -120.2478 | 1.5722 | 1.4427 | 1.6621 | -120.4476 | -120.1947 | -0.82381 | -120.2658 | 1.5588 | 1.6345 | 1.45 | -120.7015 | 0.035836 | -0.14446 | 0.41622 | 0.23561 | 0.19977 | -0.27389 | -0.054552 | -0.21811 | -0.15783 | 0.28873 | 0.2176 | 0.43571 | -0.082082 | -0.2666 | 122.0555 | 121.9261 | 122.1455 | 120.3383 | -122.1642 | 122.0422 | 122.1179 | 121.9334 | 119.6596 | -122.4181
1515.1562 | 122.3145 | -120.4422 | 1.6571 | 1.4211e-13 | -0.046613 | -0.0079338 | 0.063656 | -0.0087772 | 0.054531 | 0.0021363 | -7.0448e-05 | -0.0029698 | -0.004508 | 0.02932 | -0.013445 | -120.0901 | -0.13595 | -120.2844 | 1.5538 | 1.4152 | 1.6437 | -120.4888 | -120.2176 | -0.82839 | -120.275 | 1.5176 | 1.6162 | 1.4225 | -120.7336 | -0.046573 | -0.10326 | 0.35213 | 0.15778 | 0.20436 | -0.24186 | -0.013356 | -0.29136 | -0.13953 | 0.22464 | 0.16724 | 0.45861 | -0.040887 | -0.23456 | 121.996 | 121.8574 | 122.0859 | 120.3062 | -122.1459 | 121.9598 | 122.0584 | 121.8647 | 119.6138 | -122.3907
1516.9219 | 122.3053 | -120.5063 | 1.6434 | 1.4211e-13 | -0.046399 | -0.0077202 | 0.063229 | -0.0081362 | 0.054317 | -0.0054937 | -0.00071145 | -0.0027562 | -0.004508 | 0.029107 | -0.013659 | -120.1084 | -0.14511 | -120.3119 | 1.5309 | 1.3969 | 1.6163 | -120.5208 | -120.245 | -0.84212 | -120.3024 | 1.4993 | 1.5842 | 1.4042 | -120.7427 | -0.014538 | -0.11242 | 0.39791 | 0.1944 | 0.20894 | -0.24644 | -0.027096 | -0.23643 | -0.14411 | 0.26126 | 0.20386 | 0.44029 | -0.059205 | -0.23915 | 122.0372 | 121.9032 | 122.1226 | 120.3612 | -122.1642 | 122.0055 | 122.0905 | 121.9105 | 119.6642 | -122.3861
1518.6719 | 122.287 | -120.5063 | 1.6067 | 1.4211e-13 | -0.046399 | -0.0081476 | 0.06387 | -0.0081362 | 0.054104 | -0.0054937 | -0.00028425 | -0.0023288 | -0.0042942 | 0.029107 | -0.013659 | -120.1313 | -0.14511 | -120.3256 | 1.5126 | 1.3695 | 1.6117 | -120.5208 | -120.2633 | -0.85586 | -120.3207 | 1.4809 | 1.5659 | 1.3859 | -120.7656 | -0.014538 | -0.094117 | 0.37502 | 0.18067 | 0.1952 | -0.23729 | 0.004947 | -0.25933 | -0.1258 | 0.24294 | 0.18554 | 0.44487 | -0.040897 | -0.22084 | 122.0189 | 121.8757 | 122.118 | 120.3612 | -122.1276 | 121.9872 | 122.0721 | 121.8922 | 119.6504 | -122.3724
1520.3594 | 122.2412 | -120.5795 | 1.6159 | 1.4211e-13 | -0.046185 | -0.0079338 | 0.063656 | -0.00835 | 0.05389 | -0.0054937 | -7.0448e-05 | -0.0027562 | -0.0042942 | 0.02932 | -0.013659 | -120.1496 | -0.14511 | -120.3531 | 1.4806 | 1.3466 | 1.5705 | -120.5483 | -120.2908 | -0.85586 | -120.3574 | 1.4581 | 1.5384 | 1.3539 | -120.7931 | 0.03123 | -0.13532 | 0.42994 | 0.22644 | 0.19521 | -0.26934 | -0.045416 | -0.21356 | -0.15785 | 0.28871 | 0.22216 | 0.43571 | -0.077525 | -0.26205 | 122.0601 | 121.9261 | 122.15 | 120.4344 | -122.1642 | 122.0376 | 122.1179 | 121.9334 | 119.7237 | -122.409
1522.125 | 122.2092 | -120.5841 | 1.5656 | 1.4211e-13 | -0.046613 | -0.0079338 | 0.063229 | -0.0085636 | 0.054104 | -0.013124 | -7.0448e-05 | -0.0025424 | -0.0040806 | 0.02932 | -0.013873 | -120.1862 | -0.14511 | -120.3851 | 1.4485 | 1.3191 | 1.5476 | -120.5804 | -120.3183 | -0.86502 | -120.3803 | 1.4168 | 1.5063 | 1.331 | -120.8206 | 0.003755 | -0.11702 | 0.39789 | 0.19897 | 0.19521 | -0.24646 | -0.017955 | -0.23645 | -0.1487 | 0.26582 | 0.20384 | 0.44029 | -0.059221 | -0.23459 | 122.0326 | 121.9032 | 122.1317 | 120.439 | -122.1459 | 122.001 | 122.0904 | 121.9151 | 119.7191 | -122.3861
1523.875 | 122.3099 | -120.6024 | 1.5518 | 1.4211e-13 | -0.046613 | -0.0079338 | 0.06387 | -0.0087772 | 0.054317 | -0.0054937 | -0.00028425 | -0.0027562 | -0.0042942 | 0.029107 | -0.014086 | -120.1999 | -0.14511 | -120.3851 | 1.444 | 1.3054 | 1.5384 | -120.5941 | -120.3229 | -0.87418 | -120.3848 | 1.426 | 1.5063 | 1.3172 | -120.8389 | 0.008329 | -0.10786 | 0.40247 | 0.21728 | 0.20895 | -0.24647 | -0.013379 | -0.23646 | -0.12581 | 0.27955 | 0.21757 | 0.45403 | -0.045488 | -0.23459 | 122.0464 | 121.9078 | 122.1409 | 120.4573 | -122.1459 | 122.0284 | 122.1087 | 121.9196 | 119.7282 | -122.3907
1525.5625 | 122.3419 | -120.5978 | 1.5152 | 1.4211e-13 | -0.046826 | -0.0079338 | 0.063656 | -0.00835 | 0.054531 | -0.020755 | -0.00028425 | -0.0027562 | -0.0042942 | 0.02932 | -0.013659 | -120.2183 | -0.14053 | -120.408 | 1.4119 | 1.287 | 1.511 | -120.6124 | -120.3503 | -0.88333 | -120.4077 | 1.3894 | 1.4743 | 1.2898 | -120.8526 | -0.014565 | -0.10329 | 0.37958 | 0.18981 | 0.20437 | -0.22816 | -0.00423 | -0.25477 | -0.12582 | 0.2475 | 0.1901 | 0.44487 | -0.040917 | -0.22544 | 122.0097 | 121.8849 | 122.1088 | 120.4573 | -122.1276 | 121.9872 | 122.0721 | 121.8876 | 119.7145 | -122.3678
1527.25 | 122.3373 | -120.5933 | 1.5106 | 1.4211e-13 | -0.046399 | -0.0079338 | 0.063656 | -0.00835 | 0.054317 | -0.013124 | -0.00028425 | -0.0029698 | -0.004508 | 0.02932 | -0.013445 | -120.2274 | -0.14969 | -120.4263 | 1.3982 | 1.2825 | 1.5018 | -120.6307 | -120.3549 | -0.89707 | -120.4306 | 1.3711 | 1.4651 | 1.2852 | -120.8755 | -0.037457 | -0.11245 | 0.36584 | 0.16692 | 0.20437 | -0.22816 | -0.008809 | -0.28224 | -0.13956 | 0.23834 | 0.16263 | 0.44487 | -0.045496 | -0.22544 | 121.9914 | 121.8757 | 122.0951 | 120.4436 | -122.1413 | 121.9643 | 122.0584 | 121.8784 | 119.6962 | -122.3861
1529 | 122.3419 | -120.607 | 1.4969 | 1.4211e-13 | -0.046826 | -0.0081476 | 0.06387 | -0.00835 | 0.054104 | 0.0021363 | -7.0448e-05 | -0.0025424 | -0.004508 | 0.029107 | -0.013873 | -120.232 | -0.14511 | -120.4309 | 1.4028 | 1.2687 | 1.4972 | -120.6261 | -120.3595 | -0.90165 | -120.4306 | 1.3756 | 1.4605 | 1.276 | -120.8709 | -0.019145 | -0.094135 | 0.375 | 0.17607 | 0.19522 | -0.22817 | 0.000345 | -0.26393 | -0.12124 | 0.2475 | 0.17636 | 0.4403 | -0.036342 | -0.22086 | 122.0097 | 121.8757 | 122.1042 | 120.4619 | -122.123 | 121.9826 | 122.0675 | 121.883 | 119.7053 | -122.3678
1530.75 | 122.2549 | -120.6573 | 1.5106 | 1.4211e-13 | -0.046185 | -0.0081476 | 0.063656 | -0.00835 | 0.054104 | -0.0054937 | -0.00028425 | -0.0029698 | -0.0042942 | 0.02932 | -0.013659 | -120.2457 | -0.14511 | -120.4309 | 1.3799 | 1.255 | 1.4881 | -120.6399 | -120.3366 | -0.92454 | -120.4352 | 1.3711 | 1.4468 | 1.2623 | -120.8801 | 0.017472 | -0.13076 | 0.41162 | 0.22643 | 0.20896 | -0.25564 | -0.022545 | -0.22274 | -0.13956 | 0.32074 | 0.22214 | 0.44487 | -0.063811 | -0.24833 | 122.0372 | 121.9123 | 122.1454 | 120.5122 | -122.1505 | 122.0284 | 122.1042 | 121.9196 | 119.7328 | -122.3907
1532.4375 | 122.3465 | -120.6024 | 1.4694 | 1.4211e-13 | -0.046826 | -0.0079338 | 0.063443 | -0.00835 | 0.054317 | -0.0054937 | -0.00049785 | -0.0027562 | -0.004508 | 0.029534 | -0.013445 | -120.2549 | -0.14511 | -120.4538 | 1.3844 | 1.2504 | 1.4698 | -120.649 | -120.3824 | -0.9337 | -120.4444 | 1.3528 | 1.4422 | 1.2623 | -120.8984 | -0.046618 | -0.084982 | 0.34753 | 0.1486 | 0.19522 | -0.21902 | 0.00034 | -0.29598 | -0.11667 | 0.22003 | 0.15805 | 0.45403 | -0.027191 | -0.20713 | 121.9869 | 121.8528 | 122.0722 | 120.4573 | -122.1185 | 121.9552 | 122.0446 | 121.8647 | 119.6687 | -122.3678
1534.2031 | 122.2687 | -120.607 | 1.5152 | 1.4211e-13 | -0.046826 | -0.0079338 | 0.063443 | -0.0081362 | 0.054104 | -0.020755 | -7.0448e-05 | -0.0027562 | -0.0040806 | 0.029107 | -0.013445 | -120.2549 | -0.15427 | -120.4355 | 1.3753 | 1.255 | 1.4835 | -120.6399 | -120.3778 | -0.94743 | -120.4444 | 1.3619 | 1.4422 | 1.2714 | -120.8847 | -0.032882 | -0.13992 | 0.35211 | 0.17149 | 0.20438 | -0.26021 | -0.031701 | -0.27767 | -0.15329 | 0.22918 | 0.16263 | 0.4403 | -0.072968 | -0.24375 | 121.9823 | 121.862 | 122.0905 | 120.4527 | -122.1551 | 121.9689 | 122.0492 | 121.8784 | 119.6596 | -122.3999
1535.8906 | 122.2595 | -120.6757 | 1.4923 | 1.4211e-13 | -0.046826 | -0.0079338 | 0.063443 | -0.00835 | 0.05389 | 0.0021363 | -0.00092505 | -0.0031834 | -0.0042942 | 0.029534 | -0.013445 | -120.2595 | -0.14511 | -120.4584 | 1.3753 | 1.2367 | 1.4743 | -120.6536 | -120.3366 | -0.96117 | -120.4581 | 1.3482 | 1.4422 | 1.2486 | -120.9121 | 0.022045 | -0.11703 | 0.41619 | 0.21727 | 0.19522 | -0.25564 | -0.017971 | -0.23648 | -0.14414 | 0.33905 | 0.21755 | 0.45403 | -0.05008 | -0.24376 | 122.0509 | 121.9123 | 122.15 | 120.5305 | -122.1459 | 122.0238 | 122.1179 | 121.9242 | 119.7145 | -122.4044
1537.6406 | 122.2961 | -120.6665 | 1.4465 | 1.4211e-13 | -0.046613 | -0.0077202 | 0.063229 | -0.0085636 | 0.054317 | -0.013124 | -0.00049785 | -0.0025424 | -0.004508 | 0.029534 | -0.013659 | -120.2869 | -0.14511 | -120.4813 | 1.3524 | 1.2184 | 1.4377 | -120.6857 | -120.4099 | -0.97491 | -120.4764 | 1.3207 | 1.4056 | 1.2302 | -120.9305 | -0.019162 | -0.094143 | 0.37957 | 0.18522 | 0.20438 | -0.22818 | -0.008823 | -0.26395 | -0.12583 | 0.25664 | 0.19008 | 0.45403 | -0.040931 | -0.2163 | 122.0189 | 121.8849 | 122.1042 | 120.5214 | -122.1322 | 121.9872 | 122.0721 | 121.8967 | 119.6916 | -122.377
1539.3281 | 122.2229 | -120.7214 | 1.4648 | 1.4211e-13 | -0.04704 | -0.0083612 | 0.063443 | -0.00835 | 0.054104 | -0.0054937 | -0.00049785 | -0.0025424 | -0.0042942 | 0.029534 | -0.014086 | -120.3007 | -0.15884 | -120.495 | 1.3341 | 1.2092 | 1.4377 | -120.6902 | -120.2908 | -0.97949 | -120.4856 | 1.307 | 1.401 | 1.2211 | -120.9442 | 0.031191 | -0.13077 | 0.42076 | 0.22642 | 0.19523 | -0.25565 | -0.027134 | -0.22275 | -0.15788 | 0.43062 | 0.23586 | 0.45861 | -0.063821 | -0.24376 | 122.0555 | 121.9306 | 122.1591 | 120.5626 | -122.1551 | 122.0284 | 122.1225 | 121.9425 | 119.742 | -122.409
1541.0938 | 122.3465 | -120.6436 | 1.4465 | 1.4211e-13 | -0.046826 | -0.0081476 | 0.063443 | -0.0087772 | 0.053463 | -0.013124 | -0.00049785 | -0.0029698 | -0.004508 | 0.029534 | -0.013873 | -120.3007 | -0.15427 | -120.4996 | 1.3432 | 1.2184 | 1.4423 | -120.6902 | -120.4144 | -0.98406 | -120.4856 | 1.3115 | 1.3964 | 1.2257 | -120.935 | -0.046629 | -0.1033 | 0.34294 | 0.14402 | 0.19065 | -0.22818 | -0.004244 | -0.29142 | -0.13499 | 0.22917 | 0.15804 | 0.44945 | -0.050089 | -0.22087 | 121.9868 | 121.862 | 122.0859 | 120.4893 | -122.1368 | 121.9552 | 122.0401 | 121.8693 | 119.6596 | -122.3816
1542.8438 | 122.2733 | -120.7169 | 1.4557 | 1.4211e-13 | -0.047254 | -0.0081476 | 0.063443 | -0.0085636 | 0.054104 | 0.0021363 | -0.00049785 | -0.0025424 | -0.0040806 | 0.02932 | -0.013445 | -120.2915 | -0.15427 | -120.4996 | 1.3387 | 1.2092 | 1.4331 | -120.6948 | -120.4236 | -1.0024 | -120.4856 | 1.3161 | 1.4056 | 1.2211 | -120.9396 | 0.022034 | -0.11703 | 0.42534 | 0.21726 | 0.19523 | -0.24649 | -0.022556 | -0.22275 | -0.13957 | 0.29326 | 0.23128 | 0.45403 | -0.050086 | -0.23461 | 122.0555 | 121.9261 | 122.15 | 120.5626 | -122.1505 | 122.033 | 122.1225 | 121.9379 | 119.7145 | -122.3953
1544.5312 | 122.2549 | -120.7123 | 1.4465 | 1.4211e-13 | -0.046826 | -0.0077202 | 0.063443 | -0.0085636 | 0.053676 | -0.0054937 | -7.0448e-05 | -0.0025424 | -0.0036534 | 0.029534 | -0.013873 | -120.3236 | -0.14969 | -120.5133 | 1.3203 | 1.1955 | 1.424 | -120.7086 | -120.4419 | -1.0161 | -120.5085 | 1.2978 | 1.3781 | 1.2073 | -120.9579 | 0.003719 | -0.12619 | 0.38872 | 0.19895 | 0.19523 | -0.25108 | -0.022558 | -0.24564 | -0.14872 | 0.27037 | 0.20381 | 0.44945 | -0.068403 | -0.23919 | 122.0326 | 121.9077 | 122.1363 | 120.5626 | -122.1551 | 122.0101 | 122.0904 | 121.9196 | 119.6962 | -122.4045
1546.2188 | 122.3557 | -120.6528 | 1.4282 | 1.4211e-13 | -0.046613 | -0.0081476 | 0.063443 | -0.00835 | 0.05389 | -0.013124 | -0.00049785 | -0.0029698 | -0.004508 | 0.029107 | -0.013445 | -120.3098 | -0.15427 | -120.5042 | 1.3203 | 1.2 | 1.424 | -120.7086 | -120.4419 | -1.0299 | -120.5039 | 1.2978 | 1.3873 | 1.2028 | -120.9579 | -0.05579 | -0.10788 | 0.34294 | 0.1486 | 0.20439 | -0.22819 | -0.004248 | -0.30515 | -0.13041 | 0.21086 | 0.14888 | 0.45403 | -0.040936 | -0.22546 | 121.9731 | 121.8528 | 122.0767 | 120.4985 | -122.1368 | 121.9506 | 122.0401 | 121.8555 | 119.6229 | -122.3861
1547.9688 | 122.2366 | -120.7489 | 1.4374 | 1.4211e-13 | -0.046399 | -0.0079338 | 0.063443 | -0.00835 | 0.054317 | -0.013124 | -0.00028425 | -0.0027562 | -0.0047216 | 0.02932 | -0.013873 | -120.3419 | -0.14969 | -120.5271 | 1.302 | 1.1726 | 1.4057 | -120.7269 | -120.4648 | -1.039 | -120.5268 | 1.2749 | 1.3644 | 1.1799 | -120.9854 | 0.022024 | -0.13535 | 0.40702 | 0.22183 | 0.19981 | -0.26481 | -0.031718 | -0.2365 | -0.16246 | 0.28409 | 0.22212 | 0.45861 | -0.072984 | -0.25751 | 122.0509 | 121.9215 | 122.1546 | 120.5992 | -122.1643 | 122.0238 | 122.1133 | 121.9288 | 119.7099 | -122.4228
1549.6562 | 122.2778 | -120.7123 | 1.4236 | 1.4211e-13 | -0.046399 | -0.0081476 | 0.063656 | -0.00835 | 0.053676 | 0.0021363 | -0.00028425 | -0.0027562 | -0.0042942 | 0.028893 | -0.013873 | -120.3465 | -0.15884 | -120.5454 | 1.2974 | 1.1588 | 1.3965 | -120.736 | -120.4694 | -1.0482 | -120.5359 | 1.2749 | 1.3507 | 1.1707 | -120.99 | -0.023755 | -0.1262 | 0.36582 | 0.1669 | 0.19066 | -0.26482 | -0.027142 | -0.2777 | -0.14873 | 0.24289 | 0.17634 | 0.45403 | -0.072987 | -0.25293 | 122.0097 | 121.8711 | 122.1088 | 120.5534 | -122.1597 | 121.9872 | 122.0629 | 121.883 | 119.6641 | -122.4136
1551.3438 | 122.2961 | -120.7306 | 1.3687 | 1.4211e-13 | -0.047254 | -0.0079338 | 0.063656 | -0.0087772 | 0.054531 | -0.013124 | -0.00028425 | -0.0025424 | -0.0042942 | 0.029748 | -0.013873 | -120.3602 | -0.15884 | -120.5591 | 1.2791 | 1.1497 | 1.369 | -120.7635 | -120.4923 | -1.0573 | -120.5497 | 1.252 | 1.3278 | 1.1524 | -121.0129 | -0.032917 | -0.089577 | 0.3704 | 0.17148 | 0.20439 | -0.21904 | 0.000318 | -0.28228 | -0.11669 | 0.23831 | 0.18091 | 0.46319 | -0.040948 | -0.21631 | 122.0097 | 121.8803 | 122.0996 | 120.5717 | -122.1322 | 121.9826 | 122.0584 | 121.883 | 119.6733 | -122.3816
1553.0938 | 122.2824 | -120.7626 | 1.3687 | 1.4211e-13 | -0.047467 | -0.0079338 | 0.063656 | -0.0085636 | 0.054104 | -0.0054937 | -0.00049785 | -0.0027562 | -0.0042942 | 0.029107 | -0.013873 | -120.3739 | -0.15427 | -120.5637 | 1.27 | 1.1405 | 1.3645 | -120.7727 | -120.4923 | -1.0711 | -120.5634 | 1.2429 | 1.3278 | 1.1524 | -121.0174 | -0.010032 | -0.098734 | 0.38871 | 0.19894 | 0.20897 | -0.2282 | -0.00426 | -0.25482 | -0.12585 | 0.27035 | 0.19922 | 0.45403 | -0.040948 | -0.21631 | 122.0326 | 121.9031 | 122.1271 | 120.6084 | -122.1414 | 122.0055 | 122.0904 | 121.915 | 119.6916 | -122.3862
1554.8594 | 122.3602 | -120.7718 | 1.3504 | 1.4211e-13 | -0.046826 | -0.0081476 | 0.063443 | -0.0087772 | 0.054317 | -0.0054937 | -0.00049785 | -0.0027562 | -0.0042942 | 0.02932 | -0.013873 | -120.3877 | -0.15884 | -120.582 | 1.2562 | 1.1222 | 1.3507 | -120.7864 | -120.506 | -1.0894 | -120.5817 | 1.2291 | 1.3095 | 1.1387 | -121.0358 | -0.014613 | -0.094159 | 0.38413 | 0.18978 | 0.2044 | -0.22821 | 0.000314 | -0.26398 | -0.12127 | 0.26577 | 0.19006 | 0.45403 | -0.040952 | -0.21174 | 122.028 | 121.894 | 122.1225 | 120.6129 | -122.1368 | 122.0009 | 122.0812 | 121.9105 | 119.6824 | -122.3862
1556.6094 | 122.3511 | -120.7626 | 1.3184 | 1.4211e-13 | -0.047254 | -0.0077202 | 0.063656 | -0.0087772 | 0.05389 | -0.013124 | -7.0448e-05 | -0.0029698 | -0.0042942 | 0.02932 | -0.013873 | -120.3968 | -0.15884 | -120.6003 | 1.2334 | 1.1085 | 1.3278 | -120.8001 | -120.5106 | -1.1031 | -120.5909 | 1.2108 | 1.2957 | 1.1112 | -121.0587 | -0.037506 | -0.085007 | 0.36582 | 0.16232 | 0.19982 | -0.2099 | 0.009465 | -0.29603 | -0.10754 | 0.25204 | 0.17175 | 0.46777 | -0.022644 | -0.20717 | 121.996 | 121.8711 | 122.0905 | 120.6038 | -122.1185 | 121.9735 | 122.0583 | 121.8738 | 119.6595 | -122.377
1558.2969 | 122.2229 | -120.8496 | 1.355 | 1.4211e-13 | -0.047254 | -0.0075064 | 0.06387 | -0.0087772 | 0.05389 | 0.0021363 | -0.00049785 | -0.0027562 | -0.004508 | 0.029534 | -0.013445 | -120.4151 | -0.15427 | -120.6186 | 1.2196 | 1.0856 | 1.3095 | -120.8185 | -120.4969 | -1.1168 | -120.6092 | 1.1925 | 1.2682 | 1.0929 | -121.0724 | 0.031154 | -0.13536 | 0.43448 | 0.23098 | 0.19982 | -0.26942 | -0.04547 | -0.22279 | -0.16248 | 0.35275 | 0.24041 | 0.46319 | -0.086736 | -0.2621 | 122.0692 | 121.9352 | 122.1591 | 120.6953 | -122.1734 | 122.0421 | 122.1179 | 121.9425 | 119.7328 | -122.4274
1560.0469 | 122.2733 | -120.726 | 1.442 | 1.4211e-13 | -0.047467 | -0.0079338 | 0.063656 | -0.00835 | 0.05389 | -0.0054937 | -0.00028425 | -0.0029698 | -0.004508 | 0.02932 | -0.013659 | -120.319 | -0.14969 | -120.5179 | 1.3203 | 1.1955 | 1.424 | -120.7131 | -120.4328 | -1.126 | -120.5085 | 1.3024 | 1.3873 | 1.2073 | -120.9579 | 0.012873 | -0.12162 | 0.40703 | 0.2081 | 0.19523 | -0.2465 | -0.017981 | -0.23191 | -0.13957 | 0.29325 | 0.21754 | 0.44945 | -0.054669 | -0.23461 | 122.0464 | 121.9215 | 122.15 | 120.5763 | -122.1551 | 122.0284 | 122.1133 | 121.9334 | 119.6 | -122.3999
1561.8125 | 122.2229 | -120.6848 | 1.506 | 1.4211e-13 | -0.047467 | -0.0081476 | 0.063443 | -0.00835 | 0.054317 | -0.020755 | -0.00028425 | -0.0027562 | -0.0049352 | 0.02932 | -0.013659 | -120.264 | -0.15884 | -120.4584 | 1.3799 | 1.2412 | 1.4698 | -120.6582 | -120.3824 | -1.1443 | -120.4581 | 1.3436 | 1.4285 | 1.2623 | -120.9121 | 0.026621 | -0.12618 | 0.42077 | 0.22642 | 0.1998 | -0.26479 | -0.036281 | -0.22732 | -0.16245 | 0.30242 | 0.22671 | 0.45403 | -0.077547 | -0.24375 | 122.0647 | 121.9261 | 122.1546 | 120.526 | -122.1642 | 122.0284 | 122.1133 | 121.9471 | 119.5405 | -122.4182
1563.5 | 122.2275 | -120.6573 | 1.5015 | 1.4211e-13 | -0.047467 | -0.0079338 | 0.063443 | -0.0085636 | 0.054104 | -0.013124 | -0.00071145 | -0.0027562 | -0.004508 | 0.029534 | -0.013873 | -120.2549 | -0.16342 | -120.4447 | 1.389 | 1.2504 | 1.4835 | -120.6536 | -120.3687 | -1.1535 | -120.4489 | 1.3573 | 1.4377 | 1.2714 | -120.903 | 0.003735 | -0.11245 | 0.40246 | 0.21269 | 0.20896 | -0.25106 | -0.017968 | -0.24563 | -0.14414 | 0.28869 | 0.2084 | 0.45403 | -0.063813 | -0.23002 | 122.0464 | 121.9078 | 122.1408 | 120.4939 | -122.1551 | 122.0147 | 122.095 | 121.9288 | 119.5039 | -122.4044
1565.1719 | 122.3053 | -120.8267 | 1.3046 | 1.4211e-13 | -0.047681 | -0.0081476 | 0.063229 | -0.0085636 | 0.05389 | -0.020755 | -0.00049785 | -0.0029698 | -0.004508 | 0.029961 | -0.014086 | -120.4334 | -0.15884 | -120.6369 | 1.2059 | 1.0672 | 1.3004 | -120.8368 | -120.5564 | -1.1718 | -120.6321 | 1.1696 | 1.2591 | 1.0837 | -121.0907 | -0.01005 | -0.098745 | 0.39328 | 0.18978 | 0.19983 | -0.23738 | -0.004274 | -0.26399 | -0.13502 | 0.27034 | 0.19463 | 0.45861 | -0.04554 | -0.2209 | 122.0326 | 121.894 | 122.1271 | 120.6679 | -122.1414 | 121.9963 | 122.0858 | 121.9104 | 119.6549 | -122.3953
1566.9219 | 122.2229 | -120.6528 | 1.5152 | 1.4211e-13 | -0.047681 | -0.0083612 | 0.063443 | -0.0085636 | 0.05389 | -0.013124 | -0.00071145 | -0.0029698 | -0.004508 | 0.02932 | -0.013873 | -120.2503 | -0.15884 | -120.4355 | 1.3982 | 1.255 | 1.4835 | -120.6445 | -120.3732 | -1.1809 | -120.4444 | 1.3711 | 1.456 | 1.2669 | -120.903 | 0.008315 | -0.11702 | 0.40246 | 0.21727 | 0.20896 | -0.26021 | -0.031701 | -0.25021 | -0.14413 | 0.27954 | 0.2084 | 0.45861 | -0.059232 | -0.24833 | 122.0509 | 121.9078 | 122.1363 | 120.4939 | -122.1597 | 122.0238 | 122.1087 | 121.9196 | 119.4718 | -122.4182
1568.6875 | 122.3053 | -120.5887 | 1.4694 | 1.4211e-13 | -0.047467 | -0.0083612 | 0.063656 | -0.0087772 | 0.05389 | -0.0054937 | -0.00049785 | -0.0027562 | -0.0042942 | 0.029534 | -0.013659 | -120.2457 | -0.16342 | -120.4401 | 1.3936 | 1.2687 | 1.4927 | -120.6353 | -120.2267 | -1.1993 | -120.4261 | 1.3665 | 1.456 | 1.2714 | -120.8938 | -0.046614 | -0.075826 | 0.34295 | 0.14861 | 0.19522 | -0.2007 | 0.023233 | -0.30514 | -0.10293 | 0.36197 | 0.16263 | 0.46777 | -0.013455 | -0.19798 | 121.9823 | 121.8574 | 122.0813 | 120.4253 | -122.1047 | 121.9552 | 122.0447 | 121.8601 | 119.3894 | -122.3632
1570.4531 | 122.3053 | -120.6207 | 1.4786 | 1.4211e-13 | -0.047254 | -0.0081476 | 0.063229 | -0.00835 | 0.05389 | 0.0021363 | -0.00049785 | -0.0031834 | -0.0047216 | 0.029748 | -0.013873 | -120.2412 | -0.16342 | -120.4492 | 1.3982 | 1.255 | 1.4881 | -120.6445 | -120.3641 | -1.213 | -120.4306 | 1.3665 | 1.456 | 1.2714 | -120.8938 | -0.023728 | -0.080403 | 0.37958 | 0.17149 | 0.19522 | -0.22359 | 0.009498 | -0.27309 | -0.11209 | 0.25665 | 0.19009 | 0.46319 | -0.022611 | -0.20713 | 122.0189 | 121.8757 | 122.1088 | 120.4573 | -122.123 | 121.9872 | 122.0767 | 121.8922 | 119.4077 | -122.3724
1572.1406 | 122.2046 | -120.694 | 1.4877 | 1.4211e-13 | -0.047254 | -0.0083612 | 0.063015 | -0.0085636 | 0.05389 | -0.013124 | -0.00028425 | -0.0029698 | -0.004508 | 0.029534 | -0.013873 | -120.2686 | -0.15884 | -120.463 | 1.3707 | 1.2412 | 1.4606 | -120.6674 | -120.3824 | -1.2313 | -120.4627 | 1.3482 | 1.4239 | 1.244 | -120.9259 | 0.026619 | -0.11703 | 0.42535 | 0.231 | 0.20438 | -0.24648 | -0.027128 | -0.2319 | -0.13956 | 0.31158 | 0.23129 | 0.46319 | -0.063816 | -0.24376 | 122.0647 | 121.9352 | 122.1546 | 120.5351 | -122.1551 | 122.0421 | 122.1179 | 121.9379 | 119.4627 | -122.4136
1573.8281 | 122.2641 | -120.726 | 1.4374 | 1.4211e-13 | -0.047681 | -0.0081476 | 0.063443 | -0.0085636 | 0.054104 | -0.0054937 | -0.00049785 | -0.0027562 | -0.004508 | 0.029534 | -0.013873 | -120.3281 | -0.17258 | -120.5225 | 1.3203 | 1.1817 | 1.4194 | -120.7131 | -120.4419 | -1.2405 | -120.5131 | 1.2841 | 1.3736 | 1.2028 | -120.9808 | 0.012873 | -0.11704 | 0.39787 | 0.20352 | 0.19065 | -0.25566 | -0.017982 | -0.25481 | -0.1533 | 0.2841 | 0.21296 | 0.46777 | -0.063827 | -0.23461 | 122.0464 | 121.9077 | 122.1454 | 120.5534 | -122.1505 | 122.0101 | 122.0996 | 121.9288 | 119.4855 | -122.4182
1575.5938 | 122.2321 | -120.7123 | 1.474 | 1.4211e-13 | -0.047895 | -0.0081476 | 0.063656 | -0.00835 | 0.05389 | -0.0054937 | -0.00028425 | -0.0029698 | -0.0040806 | 0.029748 | -0.013873 | -120.3007 | -0.168 | -120.5088 | 1.3341 | 1.1955 | 1.424 | -120.704 | -120.3778 | -1.2634 | -120.4902 | 1.307 | 1.3919 | 1.2073 | -120.9579 | 0.008298 | -0.13992 | 0.41161 | 0.20353 | 0.19523 | -0.27854 | -0.050024 | -0.24564 | -0.16703 | 0.33447 | 0.22212 | 0.46777 | -0.082133 | -0.26665 | 122.0464 | 121.9077 | 122.1363 | 120.5443 | -122.178 | 122.0192 | 122.1041 | 121.9196 | 119.4489 | -122.4319
1577.2812 | 122.3465 | -120.8038 | 1.268 | 1.4211e-13 | -0.047467 | -0.0083612 | 0.063656 | -0.00835 | 0.054317 | -0.020755 | -0.00049785 | -0.0029698 | -0.004508 | 0.029534 | -0.013873 | -120.4426 | -0.16342 | -120.6369 | 1.1784 | 1.0444 | 1.2729 | -120.8414 | -120.561 | -1.2817 | -120.6367 | 1.1513 | 1.2316 | 1.0517 | -121.1044 | -0.037517 | -0.089594 | 0.36123 | 0.16689 | 0.20441 | -0.22365 | 0.004876 | -0.30061 | -0.11671 | 0.24287 | 0.16716 | 0.46777 | -0.03639 | -0.21633 | 121.9822 | 121.8482 | 122.0767 | 120.6404 | -122.1094 | 121.9551 | 122.0354 | 121.8555 | 119.5222 | -122.3725
1579.0312 | 122.1954 | -120.7214 | 1.2405 | 1.4211e-13 | -0.047681 | -0.0081476 | 0.063443 | -0.0081362 | 0.054104 | -0.013124 | -0.00049785 | -0.0027562 | -0.004508 | 0.029534 | -0.013659 | -120.406 | -0.15884 | -120.5957 | 1.0823 | 0.96193 | 1.1813 | -120.8001 | -120.5014 | -1.3 | -120.5955 | 1.0597 | 1.1492 | 0.97384 | -121.0587 | -0.078704 | -0.15827 | 0.31546 | 0.12569 | 0.2044 | -0.27861 | -0.059231 | -0.33722 | -0.18081 | 0.22 | 0.12597 | 0.46319 | -0.09134 | -0.2667 | 121.8037 | 121.6834 | 121.9027 | 120.5626 | -122.0407 | 121.7812 | 121.8706 | 121.6953 | 119.4214 | -122.2992
1580.7344 | 122.1588 | -120.9549 | 1.1627 | 1.4211e-13 | -0.048108 | -0.0083612 | 0.063443 | -0.0087772 | 0.05389 | 0.0021363 | -7.0448e-05 | -0.0025424 | -0.004508 | 0.029961 | -0.013659 | -120.5387 | -0.17716 | -120.7377 | 1.0502 | 0.9253 | 1.1447 | -120.9329 | -120.6571 | -1.3092 | -120.7328 | 1.0277 | 1.108 | 0.93721 | -121.2006 | 0.021967 | -0.1125 | 0.41615 | 0.21723 | 0.19526 | -0.23742 | -0.01804 | -0.24571 | -0.13504 | 0.29778 | 0.22207 | 0.46777 | -0.054727 | -0.22551 | 122.0051 | 121.8802 | 122.0996 | 120.7777 | -122.0956 | 121.9826 | 122.0629 | 121.8921 | 119.6457 | -122.3633
1582.4219 | 122.2733 | -120.5658 | 1.5244 | 1.4211e-13 | -0.048108 | -0.0081476 | 0.063656 | -0.0085636 | 0.053676 | 0.0021363 | -0.00049785 | -0.0027562 | -0.004508 | 0.02932 | -0.013873 | -120.1862 | -0.17258 | -120.3897 | 1.4211 | 1.2779 | 1.5064 | -120.5895 | -120.3137 | -1.3275 | -120.3757 | 1.394 | 1.4789 | 1.2852 | -120.848 | -0.023713 | -0.10329 | 0.37958 | 0.17608 | 0.19979 | -0.24647 | -0.017963 | -0.28224 | -0.1304 | 0.25209 | 0.19011 | 0.47235 | -0.045494 | -0.23917 | 121.9869 | 121.8437 | 122.0722 | 120.3932 | -122.1139 | 121.9598 | 122.0447 | 121.851 | 119.2383 | -122.3724
1584.1719 | 122.1909 | -120.6894 | 1.4832 | 1.4211e-13 | -0.048108 | -0.0083612 | 0.063229 | -0.00835 | 0.053676 | -0.0054937 | -0.00049785 | -0.0025424 | -0.0040806 | 0.029961 | -0.013873 | -120.2732 | -0.17258 | -120.4675 | 1.3341 | 1.2046 | 1.4331 | -120.6765 | -120.387 | -1.3412 | -120.4535 | 1.2978 | 1.3964 | 1.2119 | -120.9488 | 0.012883 | -0.14908 | 0.41619 | 0.22184 | 0.20896 | -0.27854 | -0.050022 | -0.25938 | -0.18535 | 0.30242 | 0.23587 | 0.49524 | -0.08671 | -0.27123 | 122.0235 | 121.894 | 122.1225 | 120.5168 | -122.1597 | 121.9872 | 122.0858 | 121.9013 | 119.3482 | -122.4319
1585.9219 | 122.2321 | -120.282 | 1.8677 | 1.4211e-13 | -0.047895 | -0.0083612 | 0.063656 | -0.0085636 | 0.053463 | -0.020755 | -0.00028425 | -0.0027562 | -0.0040806 | 0.029534 | -0.013873 | -119.8749 | -0.168 | -120.083 | 1.7278 | 1.5984 | 1.8223 | -120.2736 | -119.952 | -1.3458 | -120.0735 | 1.7007 | 1.7994 | 1.6057 | -120.5413 | 0.008419 | -0.13986 | 0.4071 | 0.19901 | 0.19059 | -0.26927 | -0.045363 | -0.25927 | -0.16696 | 0.32999 | 0.20849 | 0.46776 | -0.068315 | -0.26199 | 122.0098 | 121.8804 | 122.1043 | 120.114 | -122.1412 | 121.9827 | 122.0813 | 121.8877 | 118.9362 | -122.4089
1587.6719 | 122.2092 | -120.2637 | 1.8768 | 1.4211e-13 | -0.047895 | -0.0081476 | 0.063229 | -0.00835 | 0.05389 | -0.0054937 | -0.00028425 | -0.0031834 | -0.004508 | 0.029961 | -0.014086 | -119.8703 | -0.17716 | -120.0555 | 1.7461 | 1.6167 | 1.8544 | -120.2552 | -119.9886 | -1.3595 | -120.0506 | 1.7328 | 1.8177 | 1.6286 | -120.5229 | 0.008424 | -0.1307 | 0.39337 | 0.20817 | 0.19974 | -0.26011 | -0.022468 | -0.25927 | -0.14406 | 0.27505 | 0.21307 | 0.47234 | -0.059155 | -0.24825 | 122.0098 | 121.8804 | 122.118 | 120.0865 | -122.1321 | 121.9964 | 122.0813 | 121.8922 | 118.9042 | -122.3998
1589.4219 | 122.3236 | -120.4697 | 1.593 | 1.4211e-13 | -0.047681 | -0.0085748 | 0.063443 | -0.0085636 | 0.05389 | -0.0054937 | -0.00071145 | -0.0029698 | -0.004508 | 0.029748 | -0.013873 | -120.0489 | -0.18174 | -120.2386 | 1.5722 | 1.4381 | 1.6529 | -120.443 | -120.1672 | -1.3916 | -120.2383 | 1.5405 | 1.6345 | 1.4454 | -120.7061 | 0.026683 | -0.020866 | 0.42081 | 0.23103 | 0.20435 | -0.15488 | 0.059887 | -0.23642 | -0.052548 | 0.30247 | 0.23134 | 0.46776 | 0.041514 | -0.14759 | 122.0418 | 121.9078 | 122.1226 | 120.2879 | -122.036 | 122.0101 | 122.1042 | 121.9151 | 119.0781 | -122.2991
1591.1094 | 122.2778 | -120.4926 | 1.5701 | 1.4211e-13 | -0.048108 | -0.0081476 | 0.063443 | -0.0087772 | 0.05389 | -0.0054937 | -0.00028425 | -0.0027562 | -0.0042942 | 0.029961 | -0.013873 | -120.1313 | -0.17258 | -120.3302 | 1.476 | 1.342 | 1.5659 | -120.5346 | -120.2588 | -1.4053 | -120.3299 | 1.4352 | 1.543 | 1.3584 | -120.8022 | -0.042008 | -0.094123 | 0.36128 | 0.16235 | 0.20436 | -0.22815 | -0.004218 | -0.30969 | -0.13497 | 0.23379 | 0.16265 | 0.47234 | -0.027169 | -0.21169 | 121.9686 | 121.8345 | 122.0585 | 120.32 | -122.1047 | 121.9277 | 122.0355 | 121.851 | 119.0872 | -122.3724
1592.8594 | 122.3557 | -120.6436 | 1.4053 | 1.4211e-13 | -0.047895 | -0.0077202 | 0.063443 | -0.00835 | 0.053676 | 0.0021363 | 0.00014315 | -0.0027562 | -0.0047216 | 0.029748 | -0.0143 | -120.2824 | -0.168 | -120.4767 | 1.3158 | 1.1909 | 1.4194 | -120.6811 | -120.4236 | -1.4282 | -120.481 | 1.2932 | 1.3827 | 1.1982 | -120.9533 | -0.037472 | -0.089571 | 0.36126 | 0.16691 | 0.20438 | -0.21446 | 0.014062 | -0.30973 | -0.1121 | 0.22002 | 0.16262 | 0.47235 | -0.022625 | -0.20715 | 121.9594 | 121.8345 | 122.063 | 120.4756 | -122.0864 | 121.9368 | 122.0263 | 121.8418 | 119.2154 | -122.3587
1594.5625 | 122.2641 | -120.6665 | 1.4465 | 1.4211e-13 | -0.047895 | -0.0083612 | 0.063229 | -0.0085636 | 0.05389 | -0.013124 | -0.00028425 | -0.0027562 | -0.004508 | 0.029961 | -0.014086 | -120.2778 | -0.17716 | -120.463 | 1.3341 | 1.2184 | 1.4377 | -120.6674 | -120.3915 | -1.4419 | -120.4581 | 1.3161 | 1.4056 | 1.2211 | -120.9396 | -0.000847 | -0.11246 | 0.38872 | 0.20353 | 0.20438 | -0.22818 | -0.008823 | -0.27311 | -0.13041 | 0.27496 | 0.2084 | 0.4815 | -0.040931 | -0.22545 | 122.0006 | 121.8849 | 122.1042 | 120.4893 | -122.1139 | 121.9826 | 122.0721 | 121.8876 | 119.2246 | -122.3861
1596.25 | 122.2366 | -120.6573 | 1.4694 | 1.4211e-13 | -0.048108 | -0.0081476 | 0.063229 | -0.008991 | 0.053676 | -0.013124 | -0.00049785 | -0.0029698 | -0.0047216 | 0.029961 | -0.014086 | -120.2549 | -0.18174 | -120.463 | 1.3478 | 1.2229 | 1.4469 | -120.649 | -120.3778 | -1.4511 | -120.4489 | 1.3253 | 1.4193 | 1.2348 | -120.9167 | 0.008314 | -0.12161 | 0.40246 | 0.19438 | 0.18606 | -0.24649 | -0.022553 | -0.25937 | -0.14414 | 0.27954 | 0.2084 | 0.46777 | -0.050084 | -0.23461 | 122.0052 | 121.8803 | 122.1042 | 120.4756 | -122.1185 | 121.9826 | 122.0767 | 121.8922 | 119.2063 | -122.3861
1598.0156 | 122.3145 | -120.7169 | 1.3504 | 1.4211e-13 | -0.048322 | -0.0081476 | 0.063015 | -0.0085636 | 0.05389 | 0.0021363 | -0.00028425 | -0.0027562 | -0.0042942 | 0.030175 | -0.014086 | -120.3373 | -0.17258 | -120.5362 | 1.2791 | 1.1451 | 1.3645 | -120.736 | -120.4602 | -1.474 | -120.5222 | 1.2474 | 1.3369 | 1.157 | -120.9991 | -0.019177 | -0.071267 | 0.37956 | 0.18063 | 0.19981 | -0.20531 | 0.01405 | -0.28228 | -0.10296 | 0.25663 | 0.19465 | 0.47693 | -0.01348 | -0.19342 | 121.996 | 121.8619 | 122.0813 | 120.5443 | -122.0864 | 121.9643 | 122.0538 | 121.8738 | 119.2429 | -122.3495
1599.7656 | 122.1863 | -120.5612 | 1.5839 | 1.4211e-13 | -0.048108 | -0.0081476 | 0.063443 | -0.0085636 | 0.053676 | -0.013124 | -0.00028425 | -0.0027562 | -0.004508 | 0.029961 | -0.013873 | -120.1587 | -0.18174 | -120.3577 | 1.4531 | 1.3145 | 1.543 | -120.562 | -120.2725 | -1.4923 | -120.3482 | 1.4214 | 1.5109 | 1.3264 | -120.8206 | -0.000818 | -0.13075 | 0.40248 | 0.20355 | 0.20437 | -0.26935 | -0.040844 | -0.25934 | -0.16243 | 0.28871 | 0.213 | 0.47235 | -0.072952 | -0.25747 | 122.0143 | 121.8757 | 122.1042 | 120.3795 | -122.1459 | 121.9826 | 122.0721 | 121.8876 | 119.0689 | -122.4044
1601.4531 | 122.2275 | -120.401 | 1.6937 | 1.4211e-13 | -0.047895 | -0.0085748 | 0.063229 | -0.0087772 | 0.053463 | -0.0054937 | -0.00049785 | -0.0027562 | -0.0047216 | 0.029534 | -0.013873 | -120.0168 | -0.17716 | -120.2295 | 1.5813 | 1.4519 | 1.6666 | -120.4292 | -120.1489 | -1.506 | -120.2109 | 1.545 | 1.63 | 1.4592 | -120.6924 | -0.028246 | -0.11242 | 0.38419 | 0.17152 | 0.19977 | -0.24185 | -0.027085 | -0.29135 | -0.14868 | 0.25212 | 0.19015 | 0.4815 | -0.063773 | -0.23456 | 121.9823 | 121.8529 | 122.0676 | 120.2238 | -122.123 | 121.946 | 122.031 | 121.8602 | 118.895 | -122.3861
1603.1875 | 122.287 | -120.8084 | 1.2909 | 1.4211e-13 | -0.048108 | -0.0083612 | 0.063656 | -0.0087772 | 0.05389 | 0.0021363 | -0.00049785 | -0.0027562 | -0.004508 | 0.030175 | -0.0143 | -120.4151 | -0.18632 | -120.6141 | 1.1967 | 1.0672 | 1.2912 | -120.8093 | -120.5472 | -1.5381 | -120.6046 | 1.165 | 1.2454 | 1.0791 | -121.077 | -0.000886 | -0.094169 | 0.39328 | 0.19436 | 0.19524 | -0.22365 | 0.000301 | -0.26856 | -0.12586 | 0.26119 | 0.20379 | 0.47235 | -0.045543 | -0.21175 | 122.0051 | 121.8757 | 122.0996 | 120.6221 | -122.1002 | 121.9734 | 122.0538 | 121.8876 | 119.2703 | -122.3679
1604.9375 | 122.2366 | -120.8176 | 1.2955 | 1.4211e-13 | -0.048322 | -0.0085748 | 0.063443 | -0.0087772 | 0.053676 | 0.0021363 | -0.00071145 | -0.0031834 | -0.004508 | 0.029961 | -0.013873 | -120.4334 | -0.1909 | -120.6232 | 1.183 | 1.0581 | 1.2866 | -120.8139 | -120.5472 | -1.5518 | -120.6138 | 1.1605 | 1.2499 | 1.0654 | -121.0907 | 0.00369 | -0.11248 | 0.38412 | 0.19436 | 0.19067 | -0.23738 | -0.008854 | -0.27314 | -0.13502 | 0.27034 | 0.20378 | 0.47693 | -0.045542 | -0.23006 | 122.0006 | 121.8757 | 122.1042 | 120.6267 | -122.1093 | 121.978 | 122.0675 | 121.883 | 119.2657 | -122.3862
1606.7031 | 122.1954 | -120.7718 | 1.3504 | 1.4211e-13 | -0.048322 | -0.0081476 | 0.063443 | -0.0087772 | 0.053463 | 0.0021363 | -0.00028425 | -0.0029698 | -0.004508 | 0.029961 | -0.013659 | -120.3693 | -0.18632 | -120.5683 | 1.2334 | 1.1039 | 1.337 | -120.7818 | -120.4923 | -1.5747 | -120.5588 | 1.2062 | 1.3003 | 1.1204 | -121.0358 | -0.010034 | -0.11705 | 0.40244 | 0.20352 | 0.21355 | -0.24652 | -0.013422 | -0.26398 | -0.14416 | 0.27951 | 0.21295 | 0.47693 | -0.050109 | -0.23005 | 122.0051 | 121.8757 | 122.1088 | 120.5855 | -122.1322 | 121.978 | 122.0721 | 121.8921 | 119.1971 | -122.3862
1608.375 | 122.2092 | -120.7809 | 1.3229 | 1.4211e-13 | -0.048536 | -0.0081476 | 0.063229 | -0.0085636 | 0.053676 | 0.0021363 | -0.00028425 | -0.0029698 | -0.0042942 | 0.029748 | -0.013659 | -120.3465 | -0.18174 | -120.5454 | 1.2105 | 1.0764 | 1.3141 | -120.7635 | -120.4694 | -1.5793 | -120.5359 | 1.1833 | 1.2682 | 1.0929 | -121.0083 | 0.017437 | -0.11248 | 0.43449 | 0.23557 | 0.21813 | -0.24653 | -0.008849 | -0.22735 | -0.13959 | 0.31156 | 0.245 | 0.47235 | -0.054693 | -0.23006 | 121.9914 | 121.8574 | 122.095 | 120.5992 | -122.0864 | 121.9643 | 122.0492 | 121.8738 | 119.2016 | -122.3312
1610.125 | 122.1542 | -120.7169 | 1.3824 | 1.4211e-13 | -0.048536 | -0.0083612 | 0.063443 | -0.00835 | 0.05389 | -0.0054937 | -7.0448e-05 | -0.0029698 | -0.004508 | 0.030389 | -0.014086 | -120.3144 | -0.1909 | -120.5225 | 1.2746 | 1.1268 | 1.3599 | -120.7131 | -120.4373 | -1.6068 | -120.4993 | 1.2337 | 1.3278 | 1.1432 | -120.9854 | 0.003718 | -0.10789 | 0.40245 | 0.19437 | 0.19065 | -0.25567 | -0.022572 | -0.26854 | -0.14874 | 0.27952 | 0.21754 | 0.48608 | -0.054681 | -0.2392 | 121.9914 | 121.8436 | 122.0767 | 120.526 | -122.0956 | 121.9506 | 122.0446 | 121.8601 | 119.1101 | -122.3678
1611.8906 | 122.1909 | -120.6848 | 1.3962 | 1.4211e-13 | -0.048322 | -0.0083612 | 0.063656 | -0.0087772 | 0.053676 | -0.0054937 | -0.00028425 | -0.0027562 | -0.004508 | 0.030175 | -0.0143 | -120.2961 | -0.18632 | -120.495 | 1.27 | 1.1497 | 1.3736 | -120.6994 | -120.4236 | -1.6297 | -120.4947 | 1.252 | 1.3415 | 1.1616 | -120.9625 | -0.014589 | -0.1262 | 0.38872 | 0.1898 | 0.20439 | -0.24651 | -0.022569 | -0.27769 | -0.14416 | 0.26121 | 0.19008 | 0.46777 | -0.054678 | -0.23462 | 121.9548 | 121.8345 | 122.0584 | 120.4985 | -122.0956 | 121.9368 | 122.0263 | 121.8464 | 119.0552 | -122.3587
1613.6406 | 122.1771 | -120.5475 | 1.5106 | 1.4211e-13 | -0.048536 | -0.0083612 | 0.063443 | -0.0087772 | 0.053676 | 0.0097668 | -0.00049785 | -0.0025424 | -0.0047216 | 0.029961 | -0.013873 | -120.2503 | -0.19547 | -120.4492 | 1.302 | 1.1726 | 1.4011 | -120.6445 | -120.3641 | -1.6434 | -120.4398 | 1.2749 | 1.3598 | 1.1845 | -120.9076 | -0.096971 | -0.20859 | 0.29717 | 0.098249 | 0.19522 | -0.33806 | -0.10954 | -0.36007 | -0.2357 | 0.18341 | 0.10769 | 0.46777 | -0.1508 | -0.32617 | 121.8495 | 121.72 | 121.9486 | 120.352 | -122.1551 | 121.8224 | 121.9073 | 121.7319 | 118.9041 | -122.4182
1615.3281 | 122.1954 | -120.6345 | 1.4465 | 1.4211e-13 | -0.048536 | -0.0083612 | 0.063229 | -0.0087772 | 0.053676 | -0.0054937 | -0.00028425 | -0.0027562 | -0.0040806 | 0.029748 | -0.013873 | -120.2412 | -0.19547 | -120.4492 | 1.3295 | 1.1817 | 1.4194 | -120.6399 | -120.3595 | -1.6617 | -120.4352 | 1.2841 | 1.3781 | 1.1982 | -120.9076 | -0.005417 | -0.11704 | 0.39331 | 0.18522 | 0.19064 | -0.26481 | -0.027137 | -0.2731 | -0.16246 | 0.27496 | 0.19925 | 0.47235 | -0.068403 | -0.24835 | 121.964 | 121.8162 | 122.0539 | 120.439 | -122.0864 | 121.9185 | 122.0126 | 121.8326 | 118.9727 | -122.3541
1617.0938 | 122.168 | -120.5978 | 1.4786 | 1.4211e-13 | -0.048536 | -0.0083612 | 0.063443 | -0.008991 | 0.053676 | -0.0054937 | -0.00028425 | -0.0029698 | -0.0047216 | 0.029748 | -0.013873 | -120.1999 | -0.1909 | -120.408 | 1.3615 | 1.2184 | 1.4514 | -120.6124 | -120.3229 | -1.68 | -120.394 | 1.3299 | 1.4102 | 1.2257 | -120.8709 | -0.014565 | -0.11703 | 0.39789 | 0.18981 | 0.20437 | -0.26022 | -0.027131 | -0.27309 | -0.14872 | 0.27497 | 0.20384 | 0.47693 | -0.068397 | -0.25292 | 121.9594 | 121.8162 | 122.0493 | 120.4069 | -122.091 | 121.9277 | 122.008 | 121.8235 | 118.9178 | -122.3495
1618.8438 | 122.1725 | -120.5795 | 1.4923 | 1.4211e-13 | -0.048322 | -0.0083612 | 0.063015 | -0.00835 | 0.05389 | -0.0054937 | -0.00028425 | -0.0025424 | -0.004508 | 0.030175 | -0.014086 | -120.1999 | -0.19547 | -120.4035 | 1.357 | 1.2138 | 1.4514 | -120.6032 | -120.3183 | -1.7029 | -120.3848 | 1.3207 | 1.4148 | 1.2302 | -120.8709 | -0.023717 | -0.13534 | 0.37958 | 0.17608 | 0.19979 | -0.27854 | -0.040864 | -0.2914 | -0.17161 | 0.26124 | 0.19468 | 0.48608 | -0.077551 | -0.26207 | 121.9365 | 121.7933 | 122.031 | 120.3841 | -122.0956 | 121.9002 | 121.9943 | 121.8098 | 118.8766 | -122.3632
1620.5312 | 122.1634 | -120.5704 | 1.5472 | 1.4211e-13 | -0.048322 | -0.0081476 | 0.063443 | -0.0085636 | 0.053676 | -0.013124 | -7.0448e-05 | -0.0025424 | -0.0047216 | 0.029961 | -0.014086 | -120.1313 | -0.20005 | -120.3394 | 1.4256 | 1.3008 | 1.5201 | -120.5391 | -120.2588 | -1.7304 | -120.3253 | 1.4077 | 1.4926 | 1.3081 | -120.8022 | 0.031233 | -0.1216 | 0.4391 | 0.23102 | 0.19978 | -0.24647 | -0.027116 | -0.23187 | -0.13955 | 0.31161 | 0.24505 | 0.47692 | -0.054646 | -0.23917 | 121.996 | 121.8711 | 122.0905 | 120.3703 | -122.0864 | 121.9781 | 122.063 | 121.8784 | 118.84 | -122.3495
1622.2188 | 122.1909 | -120.5521 | 1.4969 | 1.4211e-13 | -0.048536 | -0.0085748 | 0.063229 | -0.0087772 | 0.053463 | -0.020755 | -0.00071145 | -0.0025424 | -0.004508 | 0.029961 | -0.013873 | -120.1404 | -0.1909 | -120.3485 | 1.4256 | 1.287 | 1.5155 | -120.562 | -120.2725 | -1.7487 | -120.3391 | 1.3985 | 1.4789 | 1.3081 | -120.816 | -0.009973 | -0.071243 | 0.41164 | 0.20355 | 0.21352 | -0.20985 | 0.01866 | -0.26392 | -0.098351 | 0.27956 | 0.213 | 0.47692 | -0.018028 | -0.18881 | 121.9777 | 121.8391 | 122.0676 | 120.3612 | -122.0589 | 121.9506 | 122.0309 | 121.8601 | 118.8034 | -122.3129
1623.9688 | 122.1268 | -120.5063 | 1.5793 | 1.4211e-13 | -0.048536 | -0.0081476 | 0.063229 | -0.0085636 | 0.05389 | -0.0054937 | -0.00028425 | -0.0025424 | -0.004508 | 0.029961 | -0.014086 | -120.1084 | -0.20463 | -120.3165 | 1.4623 | 1.342 | 1.5522 | -120.5071 | -120.2313 | -1.7624 | -120.2979 | 1.4352 | 1.5201 | 1.3447 | -120.7839 | -0.000801 | -0.11701 | 0.39791 | 0.18982 | 0.19062 | -0.2373 | -0.027109 | -0.27764 | -0.14412 | 0.27499 | 0.20844 | 0.48608 | -0.059218 | -0.23458 | 121.9686 | 121.8483 | 122.0585 | 120.3017 | -122.0864 | 121.9415 | 122.0264 | 121.851 | 118.7438 | -122.3632
1625.7188 | 122.2046 | -120.3461 | 1.712 | 1.4211e-13 | -0.048749 | -0.0083612 | 0.063015 | -0.008991 | 0.05389 | 0.0097668 | -0.00028425 | -0.0027562 | -0.0047216 | 0.030175 | -0.013659 | -119.9756 | -0.19547 | -120.1883 | 1.5996 | 1.4702 | 1.6987 | -120.3743 | -120.0985 | -1.7762 | -120.1696 | 1.5679 | 1.6528 | 1.4683 | -120.6557 | -0.028231 | -0.11241 | 0.37046 | 0.15779 | 0.18603 | -0.24184 | -0.013345 | -0.30965 | -0.1441 | 0.24756 | 0.17642 | 0.48608 | -0.05919 | -0.24371 | 121.9457 | 121.8163 | 122.0448 | 120.1506 | -122.0863 | 121.914 | 121.9989 | 121.8144 | 118.5699 | -122.3678
1627.4062 | 122.3007 | -120.3278 | 1.7075 | 1.4211e-13 | -0.048749 | -0.0083612 | 0.063015 | -0.0085636 | 0.05389 | -0.013124 | -0.00028425 | -0.0023288 | -0.004508 | 0.030175 | -0.014086 | -119.9619 | -0.20005 | -120.1654 | 1.6179 | 1.4794 | 1.7033 | -120.3606 | -120.0802 | -1.8082 | -120.1513 | 1.5863 | 1.6757 | 1.4775 | -120.6328 | -0.032804 | -0.089522 | 0.36589 | 0.16238 | 0.19518 | -0.22811 | -0.004189 | -0.30507 | -0.1212 | 0.24756 | 0.17643 | 0.4815 | -0.031719 | -0.22998 | 121.9457 | 121.8071 | 122.031 | 120.1277 | -122.068 | 121.914 | 122.0035 | 121.8052 | 118.5195 | -122.3403
1629.1562 | 122.0947 | -120.4788 | 1.6067 | 1.4211e-13 | -0.048749 | -0.0083612 | 0.063015 | -0.0085636 | 0.05389 | -0.0054937 | -0.00071145 | -0.0029698 | -0.0040806 | 0.030389 | -0.0143 | -120.058 | -0.20005 | -120.2707 | 1.4897 | 1.3603 | 1.5751 | -120.4705 | -120.1809 | -1.8311 | -120.2521 | 1.4535 | 1.5475 | 1.3539 | -120.729 | 0.008364 | -0.11701 | 0.4208 | 0.20814 | 0.19977 | -0.24645 | -0.031681 | -0.25016 | -0.15327 | 0.29789 | 0.22676 | 0.47692 | -0.059212 | -0.25289 | 121.9686 | 121.8391 | 122.0539 | 120.2788 | -122.0772 | 121.9323 | 122.0264 | 121.8327 | 118.6477 | -122.3357
1630.8594 | 122.1039 | -120.4651 | 1.5701 | 1.4211e-13 | -0.048536 | -0.0081476 | 0.063443 | -0.008991 | 0.053676 | -0.0054937 | -0.00028425 | -0.0023288 | -0.004508 | 0.030175 | -0.013873 | -120.0534 | -0.20463 | -120.2661 | 1.4531 | 1.3191 | 1.5613 | -120.475 | -120.1718 | -1.8494 | -120.2566 | 1.426 | 1.5155 | 1.3218 | -120.7336 | -0.009948 | -0.11702 | 0.41165 | 0.19898 | 0.20893 | -0.25104 | -0.008796 | -0.26848 | -0.14412 | 0.29332 | 0.20845 | 0.47692 | -0.054641 | -0.24832 | 121.9182 | 121.7842 | 122.0264 | 120.2605 | -122.0452 | 121.8911 | 121.9806 | 121.7869 | 118.6156 | -122.3037
1632.5469 | 122.168 | -120.4742 | 1.6479 | 1.4211e-13 | -0.048749 | -0.0083612 | 0.063015 | -0.0085636 | 0.05389 | -0.013124 | -0.00028425 | -0.0023288 | -0.004508 | 0.030175 | -0.013873 | -120.0443 | -0.20921 | -120.2432 | 1.5126 | 1.3878 | 1.6163 | -120.4476 | -120.1626 | -1.8723 | -120.2292 | 1.4901 | 1.575 | 1.3951 | -120.7107 | 0.026681 | -0.13532 | 0.42996 | 0.23103 | 0.20435 | -0.26018 | -0.031673 | -0.23643 | -0.15784 | 0.31163 | 0.24507 | 0.4815 | -0.072939 | -0.25288 | 121.9869 | 121.862 | 122.0905 | 120.265 | -122.0955 | 121.9643 | 122.0493 | 121.8693 | 118.6019 | -122.3586
1634.2344 | 122.1039 | -120.4971 | 1.5518 | 1.4211e-13 | -0.048963 | -0.0085748 | 0.062801 | -0.008991 | 0.05389 | -0.0054937 | -7.0448e-05 | -0.0029698 | -0.004508 | 0.030175 | -0.014086 | -120.1587 | -0.20463 | -120.3668 | 1.389 | 1.2596 | 1.4789 | -120.5758 | -120.2725 | -1.8952 | -120.3436 | 1.3573 | 1.4514 | 1.2714 | -120.8343 | -0.078641 | -0.1628 | 0.33839 | 0.1303 | 0.20895 | -0.29226 | -0.072901 | -0.33717 | -0.19449 | 0.22463 | 0.15349 | 0.49066 | -0.10043 | -0.28037 | 121.8861 | 121.7567 | 121.976 | 120.2925 | -122.1276 | 121.8545 | 121.9485 | 121.7686 | 118.6019 | -122.3861
1635.9844 | 122.1863 | -120.4559 | 1.4923 | 1.4211e-13 | -0.048749 | -0.0087886 | 0.063443 | -0.0085636 | 0.053676 | 0.0097668 | -0.00028425 | -0.0031834 | -0.0049352 | 0.030389 | -0.013873 | -120.1038 | -0.20463 | -120.3027 | 1.3707 | 1.2458 | 1.4652 | -120.5117 | -120.2267 | -1.9135 | -120.2979 | 1.3436 | 1.4285 | 1.2577 | -120.7748 | -0.055734 | -0.12161 | 0.35213 | 0.1532 | 0.20894 | -0.24648 | -0.027128 | -0.31884 | -0.14872 | 0.22922 | 0.15808 | 0.47692 | -0.063815 | -0.2346 | 121.8266 | 121.7018 | 121.9211 | 120.2513 | -122.004 | 121.7995 | 121.8844 | 121.7136 | 118.5424 | -122.2671
1637.7344 | 120.6665 | -119.0506 | 1.5839 | 1.4211e-13 | -0.048749 | -0.0085748 | 0.062374 | -0.0085636 | 0.053035 | -0.013124 | -0.00028425 | -0.0025424 | -0.0049352 | 0.030389 | -0.013873 | -118.8493 | -0.20005 | -119.0483 | 1.4668 | 1.3374 | 1.5613 | -119.2433 | -118.963 | -1.9044 | -119.0341 | 1.4352 | 1.5155 | 1.3447 | -119.5019 | -0.19271 | -0.11701 | 0.20127 | 0.002316 | 0.19502 | -0.24646 | -0.022529 | -0.45126 | -0.1487 | 0.087606 | 0.016471 | 0.46773 | -0.068374 | -0.23916 | 120.5174 | 120.388 | 120.6119 | 118.8505 | -120.8272 | 120.4858 | 120.5661 | 120.3953 | 117.1462 | -121.0857
1639.4219 | 121.9391 | -111.8866 | 10.0204 | 1.4211e-13 | -0.048963 | -0.0083612 | 0.063015 | -0.0085636 | 0.053249 | -0.0054937 | -0.00028425 | -0.0027562 | -0.0042942 | 0.030389 | -0.013873 | -111.6338 | -0.13595 | -111.8146 | 9.7446 | 9.6024 | 9.812 | -111.9811 | -111.7241 | -1.7075 | -111.7952 | 9.7085 | 9.7982 | 9.6274 | -112.1712 | -0.094534 | -0.27587 | 0.25281 | 0.071999 | 0.16653 | -0.41808 | -0.20847 | -0.28458 | -0.31194 | 0.16254 | 0.091411 | 0.37599 | -0.22227 | -0.39305 | 121.6312 | 121.489 | 121.6986 | 111.7506 | -122.0016 | 121.5951 | 121.6848 | 121.514 | 110.1791 | -122.1916
1641.1719 | 121.9437 | -111.2686 | 10.6247 | 1.4211e-13 | -0.048963 | -0.0083612 | 0.062801 | -0.008991 | 0.053676 | -0.0054937 | -0.00028425 | -0.0027562 | -0.0042942 | 0.030389 | -0.013873 | -110.9196 | -0.14969 | -111.0912 | 10.4863 | 10.3396 | 10.5491 | -111.2577 | -111.0144 | -1.7396 | -111.0717 | 10.4319 | 10.5308 | 10.3508 | -111.4569 | 0.010955 | -0.13842 | 0.34906 | 0.17739 | 0.16643 | -0.28512 | -0.075565 | -0.18826 | -0.19279 | 0.25426 | 0.19687 | 0.38513 | -0.093939 | -0.27388 | 121.7549 | 121.6082 | 121.8177 | 111.1189 | -121.8824 | 121.7005 | 121.7994 | 121.6194 | 109.5291 | -122.0816
1642.8594 | 122.0581 | -108.934 | 12.8586 | 1.4211e-13 | -0.049177 | -0.0085748 | 0.062801 | -0.0087772 | 0.053463 | 0.0021363 | -7.0448e-05 | -0.0029698 | -0.004508 | 0.030389 | -0.0143 | -108.6853 | -0.13137 | -108.8891 | 12.7114 | 12.5649 | 12.7698 | -109.0186 | -108.7616 | -1.68 | -108.8328 | 12.6616 | 12.7605 | 12.5898 | -109.2041 | -0.084546 | -0.14721 | 0.24872 | 0.044944 | 0.12949 | -0.29365 | -0.08883 | -0.27008 | -0.19695 | 0.17239 | 0.10126 | 0.37134 | -0.098046 | -0.26883 | 121.6454 | 121.4989 | 121.7038 | 108.8026 | -121.8771 | 121.5957 | 121.6946 | 121.5238 | 107.254 | -122.0627
1644.625 | 121.8658 | -115.535 | 6.2714 | 1.4211e-13 | -0.049177 | -0.0085748 | 0.063443 | -0.0085636 | 0.053249 | -0.0054937 | -0.00028425 | -0.0029698 | -0.0042942 | 0.030389 | -0.013873 | -114.7013 | -0.24584 | -114.8637 | 6.6587 | 6.4887 | 6.7352 | -115.0627 | -114.7781 | -1.9547 | -114.8812 | 6.5906 | 6.6847 | 6.4911 | -115.2527 | 0.47223 | 0.38738 | 0.83367 | 0.67124 | 0.19901 | 0.21733 | 0.46379 | 0.28225 | 0.31919 | 0.75692 | 0.65374 | 0.37148 | 0.41337 | 0.21969 | 122.1937 | 122.0237 | 122.2701 | 115.2891 | -121.3341 | 122.1255 | 122.2197 | 122.026 | 113.5802 | -121.5241
1646.3281 | 121.8384 | -117.2058 | 4.4678 | 1.4211e-13 | -0.048749 | -0.0085748 | 0.063015 | -0.008991 | 0.053249 | 0.0021363 | -0.00049785 | -0.0027562 | -0.0042942 | 0.030389 | -0.014086 | -116.9035 | -0.21837 | -117.0934 | 4.3192 | 4.1809 | 4.4138 | -117.2789 | -116.9667 | -1.9868 | -117.0744 | 4.2876 | 4.3725 | 4.2063 | -117.478 | -0.073136 | -0.14859 | 0.3023 | 0.11245 | 0.18559 | -0.28686 | -0.053971 | -0.27221 | -0.18021 | 0.23914 | 0.13137 | 0.40359 | -0.095237 | -0.26144 | 121.525 | 121.3867 | 121.6196 | 116.9874 | -121.7467 | 121.4934 | 121.5783 | 121.4121 | 115.219 | -121.9458
1648.0781 | 121.701 | -116.1804 | 5.452 | 1.4211e-13 | -0.049177 | -0.0085748 | 0.062588 | -0.008991 | 0.053463 | -0.013124 | -0.00049785 | -0.0027562 | -0.0042942 | 0.030816 | -0.014086 | -115.9283 | -0.1909 | -116.1228 | 5.2028 | 5.0647 | 5.2837 | -116.2991 | -115.9914 | -1.9639 | -116.0946 | 5.1666 | 5.2608 | 5.0717 | -116.5668 | -0.11864 | -0.24915 | 0.25211 | 0.05766 | 0.1763 | -0.38732 | -0.16823 | -0.38642 | -0.28533 | 0.18901 | 0.085825 | 0.47224 | -0.19118 | -0.38028 | 121.3832 | 121.2451 | 121.4642 | 115.9895 | -121.751 | 121.3471 | 121.4412 | 121.2521 | 114.2165 | -122.0188
1649.7656 | 121.701 | -115.773 | 5.69 | 1.4211e-13 | -0.049177 | -0.0085748 | 0.062801 | -0.0087772 | 0.053035 | -0.013124 | -0.00028425 | -0.0027562 | -0.004508 | 0.030602 | -0.014086 | -115.3926 | -0.19547 | -115.5825 | 5.6103 | 5.463 | 5.6821 | -115.7725 | -115.4465 | -1.9822 | -115.5589 | 5.5604 | 5.6591 | 5.4792 | -116.0265 | 0.00053 | -0.079711 | 0.38037 | 0.19049 | 0.18996 | -0.22699 | -0.007927 | -0.25353 | -0.12961 | 0.32647 | 0.21412 | 0.46765 | -0.030879 | -0.21082 | 121.3833 | 121.236 | 121.4551 | 115.5775 | -121.4625 | 121.3334 | 121.4321 | 121.2522 | 113.7908 | -121.7165
1651.4688 | 121.6232 | -117.2974 | 4.248 | 1.4211e-13 | -0.04939 | -0.0085748 | 0.063015 | -0.0087772 | 0.053249 | -0.013124 | -0.00028425 | -0.0029698 | -0.004508 | 0.030602 | -0.0143 | -117.137 | -0.20921 | -117.336 | 3.8934 | 3.7597 | 3.988 | -117.5766 | -117.2093 | -2.0463 | -117.308 | 3.8618 | 3.9513 | 3.7668 | -117.7848 | -0.27921 | -0.35465 | 0.16036 | -0.038642 | 0.24057 | -0.48839 | -0.26005 | -0.48744 | -0.38628 | 0.088017 | -0.01059 | 0.47685 | -0.29674 | -0.48126 | 121.1908 | 121.057 | 121.2854 | 117.0882 | -121.8246 | 121.1591 | 121.2487 | 121.0641 | 115.251 | -122.0329
1653.2188 | 121.4584 | -114.4775 | 6.7154 | 1.4211e-13 | -0.049177 | -0.0083612 | 0.062588 | -0.008991 | 0.053463 | 0.0021363 | -7.0448e-05 | -0.0023288 | -0.004508 | 0.030389 | -0.014086 | -114.3717 | -0.17716 | -114.5616 | 6.4069 | 6.2643 | 6.4742 | -114.7514 | -114.4346 | -1.9776 | -114.5333 | 6.3708 | 6.4604 | 6.2804 | -115.0009 | -0.27384 | -0.30846 | 0.10588 | -0.084028 | 0.18981 | -0.45106 | -0.24122 | -0.52335 | -0.34461 | 0.042891 | -0.055716 | 0.46763 | -0.25501 | -0.43496 | 120.8845 | 120.7419 | 120.9517 | 114.3004 | -121.4668 | 120.8483 | 120.9379 | 120.758 | 112.4999 | -121.7163
1654.9688 | 121.5683 | -117.6956 | 3.6163 | 1.4211e-13 | -0.049177 | -0.0085748 | 0.06216 | -0.0087772 | 0.053249 | 0.0021363 | -0.00071145 | -0.0031834 | -0.0042942 | 0.030389 | -0.0143 | -116.7158 | -0.23668 | -116.8965 | 4.1361 | 3.9794 | 4.2261 | -117.1324 | -116.7881 | -2.1196 | -116.8867 | 4.0907 | 4.194 | 4.0003 | -117.3544 | 0.5632 | 0.51972 | 0.97982 | 0.79913 | 0.23593 | 0.36311 | 0.60975 | 0.34122 | 0.47436 | 0.90751 | 0.80891 | 0.46768 | 0.57764 | 0.38396 | 121.8317 | 121.6751 | 121.9217 | 117.4589 | -120.7488 | 121.7863 | 121.8896 | 121.6959 | 115.576 | -120.9707
1656.7344 | 121.3303 | -116.3361 | 4.9759 | 1.4211e-13 | -0.049177 | -0.0085748 | 0.062588 | -0.00835 | 0.053035 | -0.020755 | -0.00028425 | -0.0027562 | -0.0042942 | 0.030389 | -0.014086 | -116.0473 | -0.20463 | -116.2418 | 4.7496 | 4.6159 | 4.8259 | -116.4364 | -116.1059 | -2.0967 | -116.2182 | 4.7134 | 4.8029 | 4.6276 | -116.6859 | -0.10036 | -0.22634 | 0.28871 | 0.094264 | 0.19463 | -0.35998 | -0.15001 | -0.34983 | -0.26252 | 0.23018 | 0.11784 | 0.46767 | -0.17297 | -0.34833 | 121.0856 | 120.952 | 121.1619 | 116.1314 | -121.4123 | 121.0494 | 121.139 | 120.9636 | 114.2394 | -121.6618
1658.4844 | 121.2387 | -114.4867 | 6.5643 | 1.4211e-13 | -0.049177 | -0.0085748 | 0.062374 | -0.008991 | 0.052822 | 0.0021363 | -0.00028425 | -0.0027562 | -0.004508 | 0.030175 | -0.014086 | -114.1611 | -0.19547 | -114.3418 | 6.4298 | 6.2872 | 6.5062 | -114.5408 | -114.2286 | -2.0646 | -114.3226 | 6.3845 | 6.4787 | 6.3033 | -114.7857 | -0.054056 | -0.13451 | 0.32564 | 0.14489 | 0.19894 | -0.27711 | -0.058108 | -0.29899 | -0.17981 | 0.25809 | 0.16406 | 0.46305 | -0.085638 | -0.261 | 120.9165 | 120.7739 | 120.9929 | 114.2912 | -121.1051 | 120.8712 | 120.9654 | 120.79 | 112.4221 | -121.35
1660.1719 | 121.0327 | -113.6856 | 7.251 | 1.4211e-13 | -0.04939 | -0.0087886 | 0.062374 | -0.008991 | 0.052608 | -0.013124 | -7.0448e-05 | -0.0027562 | -0.0047216 | 0.030602 | -0.014086 | -113.6666 | -0.18174 | -113.8519 | 6.7595 | 6.6215 | 6.8405 | -114.0645 | -113.7295 | -2.0555 | -113.8281 | 6.7279 | 6.8175 | 6.633 | -114.2957 | -0.37893 | -0.49151 | 0.01902 | -0.16633 | 0.21261 | -0.62949 | -0.41052 | -0.61014 | -0.52307 | -0.043918 | -0.14253 | 0.46761 | -0.43347 | -0.61799 | 120.4451 | 120.3071 | 120.5261 | 113.5039 | -121.3155 | 120.4135 | 120.5031 | 120.3186 | 111.6301 | -121.5467
1661.9219 | 121.1334 | -115.5075 | 5.4245 | 1.4211e-13 | -0.04939 | -0.0085748 | 0.06216 | -0.0087772 | 0.053035 | -0.013124 | -7.0448e-05 | -0.0027562 | -0.004508 | 0.030389 | -0.0143 | -115.2416 | -0.21379 | -115.4269 | 5.2257 | 5.083 | 5.3112 | -115.6901 | -115.3138 | -2.1608 | -115.4124 | 5.1804 | 5.2837 | 5.0946 | -115.8709 | -0.18255 | -0.19879 | 0.26595 | 0.080645 | 0.2632 | -0.34154 | -0.11329 | -0.36335 | -0.24413 | 0.19375 | 0.09514 | 0.45849 | -0.14082 | -0.32992 | 120.7332 | 120.5905 | 120.8187 | 115.2937 | -121.1146 | 120.6879 | 120.7912 | 120.6021 | 113.3467 | -121.2954
1663.6094 | 121.2891 | -118.8995 | 2.3483 | 1.4211e-13 | -0.049604 | -0.0085748 | 0.062588 | -0.0087772 | 0.053035 | -0.020755 | -0.00049785 | -0.0031834 | -0.0042942 | 0.030602 | -0.014086 | -119.3163 | -0.21379 | -119.529 | 1.4485 | 1.3374 | 1.5568 | -119.7928 | -119.3888 | -2.2798 | -119.492 | 1.4306 | 1.5201 | 1.3493 | -119.9781 | -0.89324 | -0.89979 | -0.41678 | -0.62946 | 0.26378 | -1.0109 | -0.79157 | -1.0785 | -0.91774 | -0.48928 | -0.59246 | 0.48606 | -0.82826 | -0.99905 | 120.3481 | 120.2369 | 120.4563 | 118.6857 | -122.1411 | 120.3301 | 120.4196 | 120.2488 | 116.6197 | -122.3264
1665.2969 | 121.2067 | -117.4393 | 3.7125 | 1.4211e-13 | -0.049604 | -0.0081476 | 0.062374 | -0.0087772 | 0.052822 | -0.0054937 | -0.00028425 | -0.0027562 | -0.0042942 | 0.030602 | -0.014086 | -117.3018 | -0.21379 | -117.4962 | 3.344 | 3.2193 | 3.4386 | -117.7048 | -117.3604 | -2.2569 | -117.4728 | 3.3307 | 3.411 | 3.2311 | -117.9451 | -0.26552 | -0.36847 | 0.13744 | -0.056975 | 0.20854 | -0.49312 | -0.2739 | -0.50579 | -0.3818 | 0.078827 | -0.033517 | 0.47228 | -0.30143 | -0.48138 | 120.7833 | 120.6586 | 120.8778 | 117.2255 | -121.4172 | 120.7699 | 120.8503 | 120.6704 | 115.1823 | -121.6575
1667.0469 | 121.1929 | -116.7709 | 4.1748 | 1.4211e-13 | -0.04939 | -0.0083612 | 0.062588 | -0.008991 | 0.052822 | -0.013124 | -0.00071145 | -0.0027562 | -0.004508 | 0.030389 | -0.0143 | -116.3633 | -0.21837 | -116.5577 | 4.1406 | 4.0023 | 4.2307 | -116.789 | -116.4355 | -2.2707 | -116.5342 | 4.1044 | 4.2031 | 4.0049 | -117.0064 | -0.018067 | -0.034177 | 0.40768 | 0.21324 | 0.2313 | -0.17247 | 0.055853 | -0.23547 | -0.070378 | 0.33539 | 0.23678 | 0.47226 | 0.028323 | -0.16993 | 120.9116 | 120.7733 | 121.0016 | 116.5526 | -120.9638 | 120.8754 | 120.9741 | 120.7758 | 114.5003 | -121.1812
1668.7969 | 121.4447 | -119.7784 | 1.5106 | 1.4211e-13 | -0.049818 | -0.0083612 | 0.062374 | -0.0087772 | 0.053035 | -0.013124 | -0.00049785 | -0.0023288 | -0.0047216 | 0.030602 | -0.0143 | -119.5819 | -0.24126 | -119.79 | 1.2471 | 1.113 | 1.3416 | -120.0171 | -119.6498 | -2.3851 | -119.7667 | 1.22 | 1.3049 | 1.1295 | -120.2345 | -0.2387 | -0.26353 | 0.19658 | -0.011521 | 0.22718 | -0.39758 | -0.16906 | -0.45603 | -0.29065 | 0.12864 | 0.011722 | 0.46775 | -0.20575 | -0.38111 | 121.0255 | 120.8915 | 121.12 | 119.5372 | -121.5278 | 120.9984 | 121.0833 | 120.9079 | 117.3933 | -121.7451
1670.5469 | 121.4127 | -119.1147 | 2.1561 | 1.4211e-13 | -0.04939 | -0.0085748 | 0.062588 | -0.0085636 | 0.053035 | -0.013124 | -7.0448e-05 | -0.0029698 | -0.0047216 | 0.03103 | -0.014086 | -118.8447 | -0.2321 | -119.0391 | 1.9338 | 1.8045 | 2.0284 | -119.2845 | -118.9035 | -2.3851 | -119.0204 | 1.9159 | 2.01 | 1.8209 | -119.4973 | -0.16983 | -0.22222 | 0.26994 | 0.07556 | 0.24539 | -0.35161 | -0.12772 | -0.3826 | -0.24016 | 0.21122 | 0.094294 | 0.47689 | -0.14609 | -0.33519 | 121.0485 | 120.9191 | 121.143 | 118.8826 | -121.4406 | 121.0306 | 121.1247 | 120.9356 | 116.7295 | -121.6533
1672.2344 | 121.2616 | -119.4214 | 1.8402 | 1.4211e-13 | -0.049604 | -0.0083612 | 0.062588 | -0.0085636 | 0.052822 | -0.013124 | -7.0448e-05 | -0.0027562 | -0.004508 | 0.030602 | -0.014513 | -118.8035 | -0.25042 | -118.9979 | 1.9247 | 1.777 | 2.0238 | -119.2754 | -118.8897 | -2.4355 | -118.9929 | 1.8747 | 1.9825 | 1.7842 | -119.4561 | 0.14603 | 0.084478 | 0.61785 | 0.42347 | 0.27744 | -0.063228 | 0.18356 | -0.034686 | 0.03449 | 0.53166 | 0.42847 | 0.46316 | 0.1423 | -0.055962 | 121.3461 | 121.1984 | 121.4452 | 119.171 | -121.1156 | 121.2961 | 121.4039 | 121.2056 | 116.9859 | -121.2963
1673.9219 | 121.2936 | -118.0756 | 3.0441 | 1.4211e-13 | -0.04939 | -0.0087886 | 0.06216 | -0.0085636 | 0.053035 | -0.0054937 | -0.00071145 | -0.0027562 | -0.0040806 | 0.030602 | -0.014086 | -117.9108 | -0.21837 | -118.1052 | 2.7488 | 2.6195 | 2.8342 | -118.3458 | -117.974 | -2.4172 | -118.0909 | 2.7309 | 2.8158 | 2.6267 | -118.5678 | -0.27027 | -0.29533 | 0.16481 | -0.029594 | 0.24068 | -0.42462 | -0.20994 | -0.49222 | -0.31325 | 0.10157 | -0.01535 | 0.47687 | -0.22832 | -0.41742 | 120.8244 | 120.6951 | 120.9097 | 117.8572 | -121.39 | 120.8064 | 120.8914 | 120.7023 | 115.6584 | -121.6119
1675.6719 | 121.1609 | -118.2861 | 2.8519 | 1.4211e-13 | -0.050245 | -0.0085748 | 0.062588 | -0.0087772 | 0.052608 | -0.0054937 | -0.00028425 | -0.0029698 | -0.004508 | 0.03103 | -0.013873 | -117.9108 | -0.24126 | -118.1097 | 2.7259 | 2.5783 | 2.8204 | -118.3367 | -117.9786 | -2.4493 | -118.0909 | 2.6851 | 2.7792 | 2.5992 | -118.5632 | -0.050545 | -0.12596 | 0.37538 | 0.1764 | 0.22694 | -0.27357 | -0.03142 | -0.27707 | -0.16677 | 0.30756 | 0.19522 | 0.47229 | -0.072686 | -0.25263 | 121.012 | 120.8644 | 121.1066 | 118.0449 | -121.1885 | 120.9712 | 121.0653 | 120.8854 | 115.8369 | -121.4151
1677.4375 | 121.2479 | -118.6844 | 2.536 | 1.4211e-13 | -0.049818 | -0.0083612 | 0.062801 | -0.0092046 | 0.052822 | -0.013124 | -0.00028425 | -0.0025424 | -0.004508 | 0.03103 | -0.0143 | -118.3732 | -0.22752 | -118.5767 | 2.323 | 2.1891 | 2.4084 | -118.7991 | -118.4364 | -2.4859 | -118.5579 | 2.2868 | 2.3808 | 2.1917 | -119.0257 | -0.11476 | -0.213 | 0.31122 | 0.10767 | 0.22243 | -0.34693 | -0.12764 | -0.34128 | -0.24925 | 0.24795 | 0.12645 | 0.46772 | -0.15517 | -0.34427 | 121.0074 | 120.8735 | 121.0928 | 118.4569 | -121.3352 | 120.9712 | 121.0652 | 120.8761 | 116.1985 | -121.5617
1679.125 | 121.1609 | -117.6956 | 3.3188 | 1.4211e-13 | -0.049604 | -0.0083612 | 0.062374 | -0.008991 | 0.052608 | -0.0054937 | -0.00049785 | -0.0027562 | -0.0042942 | 0.030816 | -0.0143 | -117.2148 | -0.22752 | -117.4093 | 3.3394 | 3.2056 | 3.4294 | -117.6498 | -117.278 | -2.4813 | -117.3858 | 3.3078 | 3.4019 | 3.2082 | -117.8581 | 0.045778 | 0.020623 | 0.48078 | 0.28636 | 0.24058 | -0.11318 | 0.11062 | -0.16245 | -0.011018 | 0.41759 | 0.30983 | 0.47227 | 0.083085 | -0.11059 | 121.035 | 120.9012 | 121.125 | 117.4681 | -120.9686 | 121.0034 | 121.0975 | 120.9038 | 115.2143 | -121.1769
1680.875 | 121.2204 | -118.103 | 3.0121 | 1.4211e-13 | -0.050245 | -0.0085748 | 0.062588 | -0.008991 | 0.052394 | 0.0021363 | -7.0448e-05 | -0.0027562 | -0.004508 | 0.030816 | -0.0143 | -118.2679 | -0.22295 | -118.476 | 2.3322 | 2.2074 | 2.4267 | -118.7167 | -118.3357 | -2.5271 | -118.4481 | 2.3097 | 2.3992 | 2.2101 | -118.9158 | -0.6137 | -0.67992 | -0.16484 | -0.37297 | 0.24073 | -0.80468 | -0.5854 | -0.81275 | -0.70243 | -0.23268 | -0.34503 | 0.46772 | -0.61293 | -0.80203 | 120.4352 | 120.3104 | 120.5297 | 117.8801 | -121.7288 | 120.4127 | 120.5022 | 120.3131 | 115.5759 | -121.9279
1682.5781 | 121.106 | -116.1484 | 4.6692 | 1.4211e-13 | -0.049604 | -0.0090022 | 0.06216 | -0.008991 | 0.052822 | -0.0054937 | -0.00028425 | -0.0031834 | -0.0042942 | 0.031243 | -0.0143 | -116.3999 | -0.20921 | -116.6081 | 4.0216 | 3.8924 | 4.1116 | -116.8211 | -116.463 | -2.4859 | -116.5708 | 3.9991 | 4.0887 | 3.9133 | -117.043 | -0.67268 | -0.6476 | -0.25151 | -0.45968 | 0.213 | -0.77674 | -0.55757 | -0.89466 | -0.67007 | -0.31464 | -0.4224 | 0.47226 | -0.58053 | -0.75589 | 120.17 | 120.0408 | 120.26 | 115.9392 | -121.4902 | 120.1475 | 120.237 | 120.0617 | 113.6625 | -121.7122
1684.2656 | 120.9183 | -115.6448 | 5.1041 | 1.4211e-13 | -0.050032 | -0.0085748 | 0.061947 | -0.008991 | 0.052822 | -0.0054937 | -0.00071145 | -0.0029698 | -0.0047216 | 0.030389 | -0.014086 | -115.5163 | -0.21837 | -115.7107 | 4.7816 | 4.6571 | 4.8808 | -115.9465 | -115.5656 | -2.5042 | -115.6871 | 4.7546 | 4.8533 | 4.6642 | -116.1456 | -0.30164 | -0.32246 | 0.12858 | -0.065879 | 0.23577 | -0.44694 | -0.22325 | -0.50075 | -0.34949 | 0.079247 | -0.042254 | 0.4585 | -0.25078 | -0.43988 | 120.4264 | 120.302 | 120.5257 | 115.4265 | -121.0505 | 120.3994 | 120.4981 | 120.309 | 113.1406 | -121.2497
1685.9531 | 120.8221 | -114.4592 | 6.0745 | 1.4211e-13 | -0.050032 | -0.0083612 | 0.061947 | -0.008991 | 0.052394 | -0.0054937 | -0.00049785 | -0.0027562 | -0.004508 | 0.03103 | -0.014513 | -114.4541 | -0.20921 | -114.6623 | 5.6881 | 5.5638 | 5.7691 | -114.8659 | -114.5079 | -2.4996 | -114.6248 | 5.6611 | 5.7415 | 5.5799 | -115.0833 | -0.40662 | -0.3864 | 0.005158 | -0.20306 | 0.20356 | -0.51077 | -0.30546 | -0.62407 | -0.41341 | -0.048678 | -0.1656 | 0.45847 | -0.33299 | -0.49461 | 120.1474 | 120.023 | 120.2283 | 114.25 | -120.9404 | 120.1203 | 120.2008 | 120.0391 | 111.9596 | -121.1578
1687.6406 | 120.5704 | -113.4247 | 7.0816 | 1.4211e-13 | -0.050245 | -0.0087886 | 0.062374 | -0.0087772 | 0.052608 | 0.0021363 | -0.00028425 | -0.0029698 | -0.0042942 | 0.030602 | -0.014086 | -113.4239 | -0.22295 | -113.6047 | 6.5946 | 6.4658 | 6.6848 | -113.8448 | -113.4685 | -2.5042 | -113.5946 | 6.5631 | 6.6618 | 6.4727 | -114.0393 | -0.42007 | -0.48696 | 0.00075 | -0.18002 | 0.24005 | -0.6158 | -0.39681 | -0.61465 | -0.51852 | -0.043857 | -0.16994 | 0.44471 | -0.41977 | -0.60887 | 120.0193 | 119.8905 | 120.1095 | 113.2017 | -120.9264 | 119.9878 | 120.0865 | 119.8974 | 110.9205 | -121.1209
1689.3438 | 120.4559 | -113.681 | 6.6971 | 1.4211e-13 | -0.050459 | -0.0087886 | 0.06216 | -0.008991 | 0.052394 | -0.020755 | -0.00028425 | -0.0027562 | -0.004508 | 0.030389 | -0.014513 | -112.7875 | -0.24126 | -112.9592 | 7.1486 | 7.0061 | 7.2251 | -113.2037 | -112.8413 | -2.5317 | -112.949 | 7.0988 | 7.193 | 7.0267 | -113.3983 | 0.47733 | 0.45155 | 0.89349 | 0.72186 | 0.24453 | 0.30903 | 0.52798 | 0.28273 | 0.40168 | 0.83977 | 0.73201 | 0.44928 | 0.49587 | 0.32967 | 120.8297 | 120.6871 | 120.9061 | 113.4398 | -119.9008 | 120.7798 | 120.874 | 120.7078 | 111.1494 | -120.0954
1691.0938 | 120.7947 | -115.9653 | 4.5822 | 1.4211e-13 | -0.050032 | -0.0083612 | 0.061947 | -0.0087772 | 0.052608 | -0.013124 | -0.00071145 | -0.0025424 | -0.0042942 | 0.030816 | -0.0143 | -116.3541 | -0.24126 | -116.5623 | 3.8705 | 3.7322 | 3.9514 | -116.8027 | -116.3943 | -2.669 | -116.5296 | 3.8343 | 3.9193 | 3.7485 | -117.0018 | -0.83747 | -0.71171 | -0.38883 | -0.597 | 0.24046 | -0.85003 | -0.63085 | -1.0366 | -0.74792 | -0.42906 | -0.5643 | 0.47226 | -0.66296 | -0.83374 | 119.8358 | 119.6975 | 119.9166 | 115.724 | -121.385 | 119.7996 | 119.8845 | 119.7137 | 113.2962 | -121.584
1692.8594 | 120.5933 | -115.0314 | 5.4932 | 1.4211e-13 | -0.050032 | -0.0087886 | 0.061947 | -0.0087772 | 0.052394 | -0.0054937 | -7.0448e-05 | -0.0027562 | -0.004508 | 0.031243 | -0.0143 | -114.6555 | -0.23668 | -114.8454 | 5.3676 | 5.2432 | 5.4669 | -115.0902 | -114.6956 | -2.6599 | -114.8126 | 5.3406 | 5.4348 | 5.2503 | -115.2756 | -0.058788 | -0.12553 | 0.37591 | 0.18601 | 0.2448 | -0.24994 | -0.026283 | -0.24418 | -0.15254 | 0.3358 | 0.21888 | 0.46306 | -0.058392 | -0.24291 | 120.3991 | 120.2747 | 120.4983 | 114.7948 | -120.5834 | 120.3721 | 120.4662 | 120.2817 | 112.3716 | -120.7688
1694.5625 | 120.6573 | -114.798 | 5.6259 | 1.4211e-13 | -0.050245 | -0.0085748 | 0.06216 | -0.0087772 | 0.052608 | -0.0054937 | -0.00049785 | -0.0027562 | -0.004508 | 0.031243 | -0.014513 | -115.0447 | -0.2321 | -115.2254 | 4.9876 | 4.8494 | 5.0731 | -115.4932 | -115.0986 | -2.7057 | -115.1972 | 4.9514 | 5.0456 | 4.8656 | -115.6648 | -0.69519 | -0.63829 | -0.24671 | -0.42744 | 0.26775 | -0.77648 | -0.55279 | -0.86684 | -0.67447 | -0.30059 | -0.39919 | 0.46764 | -0.58033 | -0.76027 | 119.7856 | 119.6474 | 119.8711 | 114.5659 | -121.1191 | 119.7494 | 119.8436 | 119.6636 | 112.0923 | -121.2907
1696.25 | 120.4102 | -113.7772 | 6.5781 | 1.4211e-13 | -0.050245 | -0.0085748 | 0.061947 | -0.0092046 | 0.052181 | -0.0054937 | -0.00028425 | -0.0027562 | -0.004508 | 0.03103 | -0.014513 | -113.3736 | -0.23668 | -113.5589 | 6.471 | 6.333 | 6.552 | -113.7761 | -113.4273 | -2.6782 | -113.5305 | 6.4349 | 6.5291 | 6.34 | -113.9844 | 0.001092 | -0.10704 | 0.40359 | 0.21824 | 0.21715 | -0.24505 | -0.026054 | -0.20723 | -0.14318 | 0.34983 | 0.24664 | 0.45387 | -0.049006 | -0.23811 | 120.2482 | 120.1102 | 120.3292 | 113.5405 | -120.3541 | 120.212 | 120.3062 | 120.1171 | 111.099 | -120.5625
1698 | 120.5933 | -116.4413 | 4.0878 | 1.4211e-13 | -0.050032 | -0.0087886 | 0.061733 | -0.0087772 | 0.052181 | 0.0021363 | -0.00049785 | -0.0027562 | -0.004508 | 0.03103 | -0.014086 | -115.9237 | -0.27789 | -116.109 | 4.0857 | 3.9382 | 4.1803 | -116.3769 | -115.9914 | -2.843 | -116.1038 | 4.0449 | 4.1344 | 3.9545 | -116.5531 | 0.064447 | -0.002143 | 0.51761 | 0.33232 | 0.26787 | -0.1496 | 0.092463 | -0.11176 | -0.042924 | 0.44994 | 0.33759 | 0.44935 | 0.046619 | -0.13332 | 120.527 | 120.3796 | 120.6216 | 116.1635 | -120.4647 | 120.4863 | 120.5758 | 120.3959 | 113.5983 | -120.6409
1699.6875 | 120.3094 | -113.1363 | 7.1365 | 1.4211e-13 | -0.050245 | -0.0085748 | 0.061947 | -0.008991 | 0.052608 | -0.013124 | -0.00028425 | -0.0027562 | -0.004508 | 0.03103 | -0.014086 | -112.9753 | -0.23668 | -113.1652 | 6.7915 | 6.6444 | 6.8725 | -113.3777 | -113.029 | -2.7331 | -113.1367 | 6.76 | 6.845 | 6.6605 | -113.5998 | -0.24141 | -0.34502 | 0.16104 | -0.028899 | 0.21251 | -0.49216 | -0.26402 | -0.46347 | -0.37658 | 0.10731 | -0.000456 | 0.46302 | -0.29156 | -0.47608 | 119.9278 | 119.7807 | 120.0088 | 112.8996 | -120.5142 | 119.8962 | 119.9813 | 119.7968 | 110.4032 | -120.7363
1701.3906 | 120.8038 | -120.6253 | 0.10986 | 1.4211e-13 | -0.050245 | -0.0087886 | 0.061947 | -0.0092046 | 0.052394 | -0.0054937 | -0.00028425 | -0.0027562 | -0.004508 | 0.030816 | -0.014086 | -119.9756 | -0.34199 | -120.1562 | 0.27647 | 0.23846 | 0.32511 | -120.443 | -120.0481 | -3.0994 | -120.1651 | 0.1715 | 0.27011 | 0.28247 | -120.6191 | 0.18232 | 0.16661 | 0.6497 | 0.46908 | 0.28676 | 0.1286 | 0.21525 | 0.006212 | 0.061636 | 0.57716 | 0.46024 | 0.45403 | 0.16025 | 0.1726 | 120.9018 | 120.8638 | 120.9504 | 120.2833 | -120.5528 | 120.7968 | 120.8954 | 120.9078 | 117.5259 | -120.729
1703.0781 | 121.1563 | -120.8313 | 0.082397 | 1.4211e-13 | -0.050459 | -0.0085748 | 0.06216 | -0.008991 | 0.052608 | -0.013124 | -0.00028425 | -0.0027562 | -0.004508 | 0.030816 | -0.0143 | -120.4655 | -0.2962 | -120.6736 | 0.042971 | 0.046148 | 0.09618 | -120.8734 | -120.5106 | -3.104 | -120.6458 | -0.029954 | 0.054914 | 0.094744 | -121.1182 | -0.042103 | -0.039426 | 0.3658 | 0.15773 | 0.19983 | -0.036249 | 0.013783 | -0.28688 | -0.11235 | 0.3207 | 0.18547 | 0.47235 | -0.027483 | 0.012347 | 120.8743 | 120.8774 | 120.9275 | 120.5351 | -120.9558 | 120.8013 | 120.8862 | 120.926 | 117.7273 | -121.2006
1704.7656 | 121.1151 | -120.9457 | 0.10986 | 1.4211e-13 | -0.050459 | -0.0087886 | 0.062588 | -0.0085636 | 0.052822 | -0.0054937 | 0.00014315 | -0.0025424 | -0.0049352 | 0.031243 | -0.014086 | -120.5387 | -0.28704 | -120.7514 | 0.047549 | 0.03699 | 0.09618 | -120.9512 | -120.6067 | -3.1361 | -120.7237 | -0.034533 | 0.059493 | 0.090166 | -121.2052 | -0.005504 | -0.062314 | 0.40699 | 0.19434 | 0.19984 | -0.072873 | -0.013683 | -0.25944 | -0.1444 | 0.33899 | 0.22207 | 0.48151 | -0.05037 | -0.019697 | 120.9933 | 120.9827 | 121.0419 | 120.6587 | -121.0611 | 120.9112 | 121.0052 | 121.0359 | 117.8097 | -121.315
1706.4531 | 121.2616 | -120.9595 | 0.059509 | 1.4211e-13 | -0.050459 | -0.0090022 | 0.062588 | -0.0087772 | 0.052822 | 0.0021363 | -0.00028425 | -0.0027562 | -0.0047216 | 0.03103 | -0.014086 | -120.5845 | -0.29162 | -120.788 | 0.042971 | 0.03699 | 0.10992 | -120.9925 | -120.6571 | -3.1727 | -120.7649 | -0.039111 | 0.050335 | 0.094744 | -121.251 | -0.032981 | -0.016538 | 0.37494 | 0.17145 | 0.20443 | -0.022519 | 0.050407 | -0.2915 | -0.09862 | 0.30236 | 0.19459 | 0.48609 | -0.009174 | 0.035235 | 121.0024 | 120.9965 | 121.0694 | 120.6678 | -121.052 | 120.9204 | 121.0098 | 121.0542 | 117.7868 | -121.3105
1708.2031 | 121.1792 | -121.019 | 0.11444 | 1.4211e-13 | -0.050673 | -0.0085748 | 0.061947 | -0.0087772 | 0.052608 | -0.013124 | -0.00028425 | -0.0025424 | -0.004508 | 0.03103 | -0.0143 | -120.6212 | -0.2962 | -120.8338 | 0.042971 | 0.03699 | 0.09618 | -121.0291 | -120.6983 | -3.2231 | -120.8061 | -0.039111 | 0.045757 | 0.090166 | -121.2784 | -0.010104 | -0.07147 | 0.39782 | 0.18517 | 0.19528 | -0.077451 | -0.018261 | -0.25946 | -0.15355 | 0.32066 | 0.21289 | 0.47235 | -0.068684 | -0.024275 | 121.062 | 121.056 | 121.1152 | 120.7228 | -121.1435 | 120.9799 | 121.0647 | 121.1091 | 117.7959 | -121.3929
1709.9531 | 121.3531 | -121.0144 | 0.082397 | 1.4211e-13 | -0.050673 | -0.0083612 | 0.062588 | -0.0087772 | 0.052181 | -0.0054937 | -0.00049785 | -0.0027562 | -0.0049352 | 0.030602 | -0.014086 | -120.6486 | -0.29162 | -120.8704 | 0.042971 | 0.03699 | 0.10076 | -121.0657 | -120.7166 | -3.2597 | -120.829 | -0.034533 | 0.054914 | 0.085587 | -121.3151 | -0.051313 | -0.039426 | 0.36577 | 0.14397 | 0.19528 | -0.045407 | 0.018362 | -0.30067 | -0.11693 | 0.29777 | 0.18542 | 0.48609 | -0.027483 | 0.00319 | 121.0574 | 121.0514 | 121.1152 | 120.7228 | -121.1481 | 120.9799 | 121.0693 | 121.1 | 117.7547 | -121.3975
1711.6406 | 121.3531 | -121.0327 | 0.068665 | 1.4211e-13 | -0.050459 | -0.0090022 | 0.062588 | -0.008991 | 0.052608 | -0.0054937 | -0.00049785 | -0.0025424 | -0.004508 | 0.030816 | -0.014513 | -120.6715 | -0.29162 | -120.8979 | 0.042971 | 0.03699 | 0.09618 | -121.0886 | -120.7533 | -3.31 | -120.861 | -0.034533 | 0.050335 | 0.090166 | -121.3471 | -0.055897 | -0.025694 | 0.36119 | 0.13481 | 0.1907 | -0.031675 | 0.027515 | -0.31441 | -0.1032 | 0.27945 | 0.17168 | 0.48609 | -0.01833 | 0.021501 | 121.0757 | 121.0697 | 121.1289 | 120.7411 | -121.1573 | 120.9982 | 121.0831 | 121.1229 | 117.7227 | -121.4158
1713.3281 | 121.2662 | -121.1426 | 0.10986 | 1.4211e-13 | -0.050459 | -0.0087886 | 0.062588 | -0.0087772 | 0.052608 | 0.0021363 | -0.00049785 | -0.0029698 | -0.0042942 | 0.031243 | -0.014513 | -120.7127 | -0.29162 | -120.9162 | 0.042971 | 0.03699 | 0.09618 | -121.1115 | -120.7807 | -3.3513 | -120.8931 | -0.039111 | 0.050335 | 0.081008 | -121.3609 | 0.031072 | -0.066892 | 0.42985 | 0.22636 | 0.19529 | -0.072873 | -0.013683 | -0.21828 | -0.14897 | 0.36184 | 0.24949 | 0.46778 | -0.059528 | -0.028855 | 121.1855 | 121.1796 | 121.2388 | 120.851 | -121.2214 | 121.1035 | 121.1929 | 121.2236 | 117.7913 | -121.4707
1715.0156 | 121.4264 | -121.0876 | 0.054932 | 1.4211e-13 | -0.050886 | -0.0087886 | 0.062374 | -0.009632 | 0.052822 | -0.0054937 | -7.0448e-05 | -0.0027562 | -0.004508 | 0.031457 | -0.0143 | -120.731 | -0.30078 | -120.9437 | 0.038393 | 0.03699 | 0.10076 | -121.1481 | -120.7899 | -3.3925 | -120.9068 | -0.039111 | 0.059493 | 0.085587 | -121.4021 | -0.060492 | -0.016539 | 0.35661 | 0.14396 | 0.20445 | -0.017942 | 0.045827 | -0.31442 | -0.094043 | 0.29775 | 0.18083 | 0.49525 | 0.004561 | 0.030655 | 121.126 | 121.1246 | 121.1884 | 120.7869 | -121.2031 | 121.0485 | 121.1471 | 121.1732 | 117.6952 | -121.457
1716.7812 | 121.4401 | -121.1472 | 0.068665 | 1.4211e-13 | -0.050459 | -0.0085748 | 0.062588 | -0.0092046 | 0.052608 | 0.0021363 | -0.00049785 | -0.0029698 | -0.0042942 | 0.031243 | -0.0143 | -120.7448 | -0.2962 | -120.9666 | 0.042971 | 0.03699 | 0.09618 | -121.1665 | -120.7395 | -3.4337 | -120.9297 | -0.039111 | 0.059493 | 0.085587 | -121.4158 | -0.019298 | -0.025694 | 0.40238 | 0.18057 | 0.19987 | -0.031675 | 0.027515 | -0.26865 | -0.10778 | 0.40762 | 0.21744 | 0.48609 | -0.009172 | 0.016922 | 121.1901 | 121.1841 | 121.2433 | 120.851 | -121.2351 | 121.108 | 121.2066 | 121.2327 | 117.7135 | -121.4845
1718.4688 | 121.3257 | -121.1884 | 0.1236 | 1.4211e-13 | -0.050673 | -0.0087886 | 0.062588 | -0.0092046 | 0.052608 | -0.013124 | -0.00028425 | -0.0031834 | -0.0042942 | 0.031457 | -0.014513 | -120.7677 | -0.30078 | -120.9849 | 0.033814 | 0.03699 | 0.10076 | -121.1802 | -120.8494 | -3.4383 | -120.9526 | -0.025376 | 0.054914 | 0.090166 | -121.4341 | 0.008164 | -0.089782 | 0.42069 | 0.20346 | 0.1953 | -0.086606 | -0.022837 | -0.24577 | -0.14897 | 0.33893 | 0.23575 | 0.48152 | -0.068682 | -0.03343 | 121.2222 | 121.2253 | 121.2891 | 120.8876 | -121.3038 | 121.163 | 121.2433 | 121.2785 | 117.7501 | -121.5577
1720.2188 | 121.3623 | -121.1929 | 0.11902 | 1.4211e-13 | -0.050673 | -0.0087886 | 0.062588 | -0.0087772 | 0.052608 | -0.013124 | -0.00049785 | -0.0027562 | -0.004508 | 0.031243 | -0.0143 | -120.786 | -0.30536 | -120.9986 | 0.042971 | 0.041569 | 0.09618 | -121.2031 | -120.8632 | -3.484 | -120.9755 | -0.029954 | 0.059493 | 0.090166 | -121.4524 | -0.010153 | -0.076048 | 0.40695 | 0.1943 | 0.20446 | -0.07745 | -0.022839 | -0.25951 | -0.14897 | 0.32978 | 0.21743 | 0.47694 | -0.059526 | -0.028853 | 121.2359 | 121.2345 | 121.2891 | 120.8876 | -121.3221 | 121.163 | 121.2524 | 121.2831 | 117.7089 | -121.5715
1721.9688 | 121.4401 | -121.2341 | 0.09613 | 1.4211e-13 | -0.050886 | -0.0085748 | 0.062374 | -0.0087772 | 0.053035 | -0.020755 | -7.0448e-05 | -0.0029698 | -0.0047216 | 0.031243 | -0.0143 | -120.8135 | -0.30536 | -121.0307 | 0.038393 | 0.046148 | 0.10534 | -121.2214 | -120.8769 | -3.5252 | -120.9984 | -0.039111 | 0.050335 | 0.085587 | -121.4753 | 0.01273 | -0.057737 | 0.42068 | 0.20345 | 0.19072 | -0.049982 | 0.009207 | -0.2412 | -0.13524 | 0.35724 | 0.23574 | 0.47694 | -0.045795 | -0.010543 | 121.2725 | 121.2803 | 121.3395 | 120.9288 | -121.3175 | 121.195 | 121.2845 | 121.3197 | 117.7089 | -121.5715
1723.6562 | 121.5042 | -121.225 | 0.064087 | 1.4211e-13 | -0.050886 | -0.0085748 | 0.062588 | -0.008991 | 0.052822 | -0.013124 | -0.00028425 | -0.0029698 | -0.0049352 | 0.031457 | -0.014513 | -120.818 | -0.30078 | -121.0444 | 0.038393 | 0.041569 | 0.10076 | -121.2443 | -120.8906 | -3.5756 | -121.0121 | -0.04369 | 0.054914 | 0.090166 | -121.4891 | -0.019319 | -0.025694 | 0.40695 | 0.18056 | 0.19988 | -0.022518 | 0.036672 | -0.26409 | -0.10778 | 0.33435 | 0.21285 | 0.47694 | -0.009173 | 0.026079 | 121.2634 | 121.2665 | 121.3257 | 120.9242 | -121.3084 | 121.1813 | 121.2799 | 121.3151 | 117.6494 | -121.5532
1725.3438 | 121.4905 | -121.225 | 0.07782 | 1.4211e-13 | -0.050886 | -0.0087886 | 0.062374 | -0.0092046 | 0.052608 | -0.0054937 | -0.00028425 | -0.0029698 | -0.0047216 | 0.031243 | -0.014513 | -120.8409 | -0.30994 | -121.0627 | 0.042971 | 0.03699 | 0.09618 | -121.2535 | -120.9135 | -3.6031 | -121.0259 | -0.039111 | 0.045757 | 0.094744 | -121.5028 | -0.028477 | -0.034849 | 0.38405 | 0.16225 | 0.19073 | -0.04083 | 0.01836 | -0.27783 | -0.11693 | 0.31145 | 0.19911 | 0.47694 | -0.032063 | 0.016924 | 121.2679 | 121.262 | 121.3212 | 120.915 | -121.3313 | 121.1859 | 121.2707 | 121.3197 | 117.6219 | -121.5806
1727.0938 | 121.5546 | -121.2433 | 0.082397 | 1.4211e-13 | -0.0511 | -0.0090022 | 0.06216 | -0.008991 | 0.052608 | -0.0054937 | -0.00049785 | -0.0029698 | -0.0047216 | 0.03103 | -0.0143 | -120.8547 | -0.31452 | -121.081 | 0.038393 | 0.032411 | 0.10076 | -121.2763 | -120.9273 | -3.6443 | -121.0442 | -0.039111 | 0.059493 | 0.094744 | -121.5257 | -0.033062 | -0.044004 | 0.38863 | 0.16225 | 0.19531 | -0.049986 | 0.018362 | -0.28241 | -0.12151 | 0.31603 | 0.19911 | 0.48152 | -0.022904 | 0.012347 | 121.2817 | 121.2757 | 121.344 | 120.9288 | -121.3587 | 121.2042 | 121.3028 | 121.338 | 117.599 | -121.6081
1728.7812 | 121.4584 | -121.2845 | 0.10529 | 1.4211e-13 | -0.050886 | -0.0083612 | 0.062588 | -0.0092046 | 0.052608 | -0.013124 | -0.00049785 | -0.0029698 | -0.0049352 | 0.031457 | -0.014513 | -120.8684 | -0.31452 | -121.0948 | 0.047549 | 0.03699 | 0.09618 | -121.2855 | -120.9089 | -3.6992 | -121.0488 | -0.029954 | 0.045757 | 0.094744 | -121.5349 | -0.001021 | -0.057737 | 0.41609 | 0.18971 | 0.19073 | -0.068296 | -0.009106 | -0.25037 | -0.13524 | 0.37554 | 0.23573 | 0.4861 | -0.059529 | -0.010542 | 121.332 | 121.3215 | 121.3807 | 120.97 | -121.3908 | 121.2545 | 121.3302 | 121.3792 | 117.5852 | -121.6401
1730.4688 | 121.4905 | -121.2891 | 0.10986 | 1.4211e-13 | -0.0511 | -0.0090022 | 0.062801 | -0.0092046 | 0.052394 | -0.0054937 | -0.00028425 | -0.0029698 | -0.004508 | 0.031457 | -0.0143 | -120.8913 | -0.3191 | -121.1039 | 0.042971 | 0.041569 | 0.10076 | -121.3038 | -120.8723 | -3.7359 | -121.0671 | -0.029954 | 0.054914 | 0.085587 | -121.5532 | -0.014759 | -0.066892 | 0.39778 | 0.18513 | 0.19989 | -0.068294 | -0.009104 | -0.26411 | -0.13982 | 0.41675 | 0.22199 | 0.4861 | -0.054949 | -0.024276 | 121.332 | 121.3306 | 121.3898 | 120.97 | -121.4137 | 121.2591 | 121.344 | 121.3746 | 117.5532 | -121.663
1732.2344 | 121.582 | -121.2708 | 0.073242 | 1.4211e-13 | -0.0511 | -0.0087886 | 0.062588 | -0.0087772 | 0.052608 | -0.013124 | -0.00049785 | -0.0029698 | -0.0047216 | 0.031457 | -0.014513 | -120.8959 | -0.32367 | -121.1222 | 0.038393 | 0.03699 | 0.09618 | -121.3176 | -120.8952 | -3.7862 | -121.0854 | -0.034533 | 0.064071 | 0.085587 | -121.5623 | -0.046806 | -0.034849 | 0.37489 | 0.14851 | 0.19532 | -0.036252 | 0.022938 | -0.29158 | -0.10778 | 0.37555 | 0.18536 | 0.47694 | -0.009171 | 0.012345 | 121.3091 | 121.3077 | 121.3669 | 120.9471 | -121.3908 | 121.2362 | 121.3348 | 121.3563 | 117.4845 | -121.6356
1733.9844 | 121.5591 | -121.2936 | 0.09613 | 1.4211e-13 | -0.0511 | -0.0087886 | 0.062801 | -0.008991 | 0.052608 | -0.013124 | -7.0448e-05 | -0.0025424 | -0.0049352 | 0.031457 | -0.0143 | -120.9096 | -0.3191 | -121.1406 | 0.033814 | 0.03699 | 0.091601 | -121.3267 | -120.8494 | -3.832 | -121.0991 | -0.029954 | 0.045757 | 0.094744 | -121.5761 | -0.033076 | -0.062316 | 0.38404 | 0.15308 | 0.18616 | -0.05914 | -0.004529 | -0.28243 | -0.12608 | 0.44422 | 0.19451 | 0.47694 | -0.050373 | -0.001386 | 121.3275 | 121.3306 | 121.3852 | 120.9745 | -121.4228 | 121.2637 | 121.3394 | 121.3884 | 117.4616 | -121.6722
1735.7344 | 121.5271 | -121.3623 | 0.10529 | 1.4211e-13 | -0.051527 | -0.0092158 | 0.06216 | -0.008991 | 0.053035 | 0.0021363 | 0.00014315 | -0.0027562 | -0.0047216 | 0.031243 | -0.0143 | -120.9279 | -0.32367 | -121.1589 | 0.038393 | 0.041569 | 0.09618 | -121.345 | -120.9868 | -3.8824 | -121.1129 | -0.025376 | 0.050335 | 0.094744 | -121.5944 | 0.017273 | -0.066893 | 0.43439 | 0.20344 | 0.18616 | -0.063717 | -0.009106 | -0.23208 | -0.13066 | 0.37552 | 0.24944 | 0.48152 | -0.054951 | -0.010542 | 121.4007 | 121.4039 | 121.4585 | 121.0386 | -121.4503 | 121.3369 | 121.4126 | 121.457 | 117.4799 | -121.6997
1737.4375 | 121.5088 | -121.344 | 0.11444 | 1.4211e-13 | -0.0511 | -0.0085748 | 0.062801 | -0.0094182 | 0.052822 | -0.0054937 | -0.00049785 | -0.0031834 | -0.0047216 | 0.031457 | -0.014086 | -120.9462 | -0.32367 | -121.168 | 0.042971 | 0.03699 | 0.09618 | -121.3633 | -121.0051 | -3.9419 | -121.1174 | -0.039111 | 0.059493 | 0.085587 | -121.6035 | -0.019353 | -0.07147 | 0.39777 | 0.17597 | 0.19532 | -0.077451 | -0.018261 | -0.25954 | -0.15355 | 0.3389 | 0.22655 | 0.4861 | -0.054948 | -0.028854 | 121.387 | 121.381 | 121.4402 | 121.0203 | -121.4778 | 121.3049 | 121.4035 | 121.4296 | 117.4021 | -121.718
1739.1875 | 121.6324 | -121.3257 | 0.09613 | 1.4211e-13 | -0.050673 | -0.0090022 | 0.062374 | -0.008991 | 0.052608 | 0.0021363 | -0.00049785 | -0.0029698 | -0.004508 | 0.031671 | -0.013873 | -120.9508 | -0.33283 | -121.1726 | 0.038393 | 0.03699 | 0.09618 | -121.3725 | -121.0143 | -3.9877 | -121.1358 | -0.039111 | 0.054914 | 0.090166 | -121.6219 | -0.046821 | -0.057737 | 0.37488 | 0.15308 | 0.1999 | -0.05914 | 5e-05 | -0.29617 | -0.13524 | 0.31143 | 0.18993 | 0.4861 | -0.041216 | -0.005964 | 121.3641 | 121.3627 | 121.4219 | 120.9929 | -121.4686 | 121.2866 | 121.3806 | 121.4158 | 117.338 | -121.718
1740.875 | 121.6415 | -121.3394 | 0.073242 | 1.4211e-13 | -0.0511 | -0.0085748 | 0.062801 | -0.0094182 | 0.052822 | -0.013124 | -0.00028425 | -0.0031834 | -0.004508 | 0.031457 | -0.0143 | -120.9554 | -0.32825 | -121.1863 | 0.038393 | 0.041569 | 0.10076 | -121.3862 | -121.0143 | -4.0243 | -121.1449 | -0.039111 | 0.054914 | 0.090166 | -121.6219 | -0.046825 | -0.034849 | 0.38404 | 0.15308 | 0.1999 | -0.031673 | 0.027517 | -0.28244 | -0.11235 | 0.32516 | 0.1945 | 0.47694 | -0.018328 | 0.016924 | 121.3778 | 121.381 | 121.4402 | 121.0112 | -121.4595 | 121.3003 | 121.3943 | 121.4296 | 117.3151 | -121.6951
1742.625 | 121.5408 | -121.376 | 0.10529 | 1.4211e-13 | -0.051314 | -0.0090022 | 0.062588 | -0.0092046 | 0.052822 | -0.020755 | -0.00049785 | -0.0031834 | -0.0042942 | 0.031671 | -0.014513 | -120.9737 | -0.33741 | -121.2001 | 0.047549 | 0.046148 | 0.10076 | -121.3908 | -121.028 | -4.0747 | -121.1586 | -0.034533 | 0.045757 | 0.094744 | -121.6447 | -0.014783 | -0.057737 | 0.40234 | 0.17596 | 0.19075 | -0.059138 | -0.004527 | -0.26871 | -0.13982 | 0.34805 | 0.21739 | 0.4861 | -0.059529 | -0.010542 | 121.4236 | 121.4222 | 121.4768 | 121.0386 | -121.4961 | 121.3415 | 121.4218 | 121.4708 | 117.3013 | -121.75
1744.3594 | 121.7056 | -121.3715 | 0.09613 | 1.4211e-13 | -0.051314 | -0.0083612 | 0.06216 | -0.0092046 | 0.052822 | -0.013124 | -0.00049785 | -0.0027562 | -0.0047216 | 0.031457 | -0.0143 | -120.9829 | -0.32825 | -121.2138 | 0.038393 | 0.041569 | 0.09618 | -121.4 | -121.0371 | -4.1388 | -121.1632 | -0.039111 | 0.050335 | 0.085587 | -121.6539 | -0.028519 | -0.057737 | 0.38861 | 0.15765 | 0.18617 | -0.054561 | 5e-05 | -0.28244 | -0.13524 | 0.33431 | 0.20823 | 0.49068 | -0.045795 | -0.010543 | 121.4099 | 121.413 | 121.4676 | 121.0432 | -121.4961 | 121.3323 | 121.4218 | 121.457 | 117.2327 | -121.75
1746.0625 | 121.6507 | -121.3852 | 0.086975 | 1.4211e-13 | -0.0511 | -0.0085748 | 0.062588 | -0.0092046 | 0.052822 | -0.013124 | -0.00028425 | -0.0027562 | -0.0047216 | 0.031671 | -0.014513 | -120.9874 | -0.34199 | -121.2184 | 0.038393 | 0.050727 | 0.10076 | -121.4229 | -121.0463 | -4.1754 | -121.177 | -0.034533 | 0.059493 | 0.094744 | -121.6676 | -0.03768 | -0.048582 | 0.39776 | 0.16681 | 0.20449 | -0.036248 | 0.013784 | -0.28245 | -0.12151 | 0.33889 | 0.20823 | 0.49068 | -0.027482 | 0.007769 | 121.4236 | 121.4359 | 121.486 | 121.0432 | -121.5098 | 121.3507 | 121.4447 | 121.4799 | 117.2098 | -121.7546
1747.8125 | 121.6553 | -121.3943 | 0.07782 | 1.4211e-13 | -0.051314 | -0.0087886 | 0.062801 | -0.0094182 | 0.052608 | -0.020755 | -0.00028425 | -0.0027562 | -0.0047216 | 0.03103 | -0.0143 | -121.0057 | -0.33741 | -121.2321 | 0.038393 | 0.041569 | 0.10534 | -121.4275 | -121.0097 | -4.2349 | -121.1907 | -0.034533 | 0.045757 | 0.085587 | -121.6676 | -0.033104 | -0.039427 | 0.3886 | 0.16223 | 0.19533 | -0.036251 | 0.027517 | -0.27329 | -0.11235 | 0.38467 | 0.20365 | 0.47694 | -0.032063 | 0.007767 | 121.4327 | 121.4359 | 121.4997 | 121.0569 | -121.5053 | 121.3598 | 121.4401 | 121.4799 | 117.1594 | -121.7455
1749.5 | 121.7148 | -121.3852 | 0.082397 | 1.4211e-13 | -0.051527 | -0.0085748 | 0.062374 | -0.0092046 | 0.052608 | -0.0054937 | -0.00028425 | -0.0029698 | -0.0049352 | 0.031457 | -0.0143 | -121.0103 | -0.34199 | -121.2367 | 0.038393 | 0.041569 | 0.09618 | -121.4366 | -121.0326 | -4.2807 | -121.1999 | -0.039111 | 0.050335 | 0.085587 | -121.6814 | -0.051417 | -0.044004 | 0.37487 | 0.14849 | 0.19991 | -0.040828 | 0.013783 | -0.29618 | -0.12151 | 0.35262 | 0.18534 | 0.48152 | -0.032062 | 0.00319 | 121.4236 | 121.4268 | 121.4814 | 121.0432 | -121.519 | 121.3461 | 121.4355 | 121.4708 | 117.1045 | -121.7638
1751.1875 | 121.5866 | -121.4447 | 0.10529 | 1.4211e-13 | -0.051314 | -0.0087886 | 0.062374 | -0.0092046 | 0.052822 | -0.013124 | -0.00049785 | -0.0029698 | -0.004508 | 0.031243 | -0.014513 | -121.0286 | -0.34657 | -121.2504 | 0.047549 | 0.032411 | 0.091601 | -121.432 | -120.9776 | -4.3311 | -121.209 | -0.029954 | 0.045757 | 0.090166 | -121.686 | 0.012671 | -0.057737 | 0.41607 | 0.19427 | 0.1816 | -0.072875 | -0.013685 | -0.24125 | -0.13524 | 0.46708 | 0.23569 | 0.47694 | -0.059529 | -0.01512 | 121.4923 | 121.4771 | 121.5363 | 121.0981 | -121.5373 | 121.4147 | 121.4905 | 121.5349 | 117.1136 | -121.7912
1752.9531 | 121.7102 | -121.4218 | 0.082397 | 1.4211e-13 | -0.051527 | -0.0085748 | 0.062374 | -0.0094182 | 0.052608 | -0.0054937 | -0.00028425 | -0.0025424 | -0.0047216 | 0.031243 | -0.0143 | -121.0286 | -0.34657 | -121.2504 | 0.038393 | 0.03699 | 0.10076 | -121.4549 | -121.0555 | -4.386 | -121.2182 | -0.034533 | 0.054914 | 0.085587 | -121.6951 | -0.033112 | -0.044004 | 0.39318 | 0.17138 | 0.20449 | -0.045407 | 0.018362 | -0.2733 | -0.11693 | 0.36635 | 0.20364 | 0.47694 | -0.027483 | 0.00319 | 121.4602 | 121.4588 | 121.5226 | 121.0752 | -121.5373 | 121.3873 | 121.4767 | 121.5074 | 117.0358 | -121.7775
1754.7031 | 121.6553 | -121.463 | 0.10986 | 1.4211e-13 | -0.051527 | -0.0085748 | 0.062374 | -0.008991 | 0.053035 | -0.013124 | -7.0448e-05 | -0.0027562 | -0.0047216 | 0.031457 | -0.014727 | -121.0424 | -0.35115 | -121.2687 | 0.042971 | 0.03699 | 0.091601 | -121.4549 | -121.06 | -4.4318 | -121.2182 | -0.034533 | 0.050335 | 0.094744 | -121.6997 | 0.008087 | -0.066892 | 0.42064 | 0.19427 | 0.18618 | -0.072873 | -0.018262 | -0.23668 | -0.1444 | 0.40297 | 0.24484 | 0.48152 | -0.059528 | -0.015119 | 121.506 | 121.5 | 121.5546 | 121.1119 | -121.5648 | 121.4285 | 121.5133 | 121.5578 | 117.0312 | -121.8096
1756.3906 | 121.6599 | -121.463 | 0.11444 | 1.4211e-13 | -0.0511 | -0.0092158 | 0.062588 | -0.0092046 | 0.052608 | -0.020755 | -7.0448e-05 | -0.0029698 | -0.0049352 | 0.031671 | -0.014727 | -121.0057 | -0.35572 | -121.2733 | 0.042971 | 0.046148 | 0.10534 | -121.4687 | -121.0646 | -4.4914 | -121.2319 | -0.039111 | 0.050335 | 0.094744 | -121.7226 | -0.00565 | -0.07147 | 0.45727 | 0.18969 | 0.19534 | -0.068293 | -0.009104 | -0.25957 | -0.15355 | 0.39839 | 0.23111 | 0.49068 | -0.064106 | -0.019697 | 121.506 | 121.5092 | 121.5684 | 121.1073 | -121.5831 | 121.4239 | 121.5133 | 121.5578 | 116.9717 | -121.837
1758.1406 | 121.7056 | -121.4493 | 0.09613 | 1.4211e-13 | -0.051741 | -0.0087886 | 0.062801 | -0.0087772 | 0.052608 | -0.0054937 | -7.0448e-05 | -0.0031834 | -0.004508 | 0.031671 | -0.0143 | -121.0057 | -0.35115 | -121.2871 | 0.042971 | 0.03699 | 0.10076 | -121.4778 | -121.0692 | -4.5463 | -121.2411 | -0.034533 | 0.050335 | 0.085587 | -121.7272 | -0.02854 | -0.053159 | 0.44354 | 0.16222 | 0.19076 | -0.05914 | 0.004629 | -0.27789 | -0.13066 | 0.38008 | 0.20821 | 0.4861 | -0.045795 | -0.010543 | 121.4923 | 121.4863 | 121.55 | 121.0981 | -121.5739 | 121.4147 | 121.4996 | 121.5349 | 116.903 | -121.8233
1759.8281 | 121.669 | -121.463 | 0.09613 | 1.4211e-13 | -0.051314 | -0.0087886 | 0.062588 | -0.008991 | 0.053249 | -0.0054937 | -7.0448e-05 | -0.0029698 | -0.0047216 | 0.031671 | -0.014513 | -121.0195 | -0.3603 | -121.2962 | 0.042971 | 0.03699 | 0.091601 | -121.4916 | -121.0829 | -4.6104 | -121.2502 | -0.039111 | 0.050335 | 0.090166 | -121.7409 | -0.028544 | -0.053159 | 0.44353 | 0.1668 | 0.19534 | -0.05914 | -0.004529 | -0.27789 | -0.13524 | 0.38008 | 0.21279 | 0.49068 | -0.045795 | -0.005964 | 121.506 | 121.5 | 121.5546 | 121.1027 | -121.5877 | 121.4239 | 121.5133 | 121.5532 | 116.8526 | -121.837
1761.5156 | 121.6599 | -121.4905 | 0.1236 | 1.4211e-13 | -0.051741 | -0.0090022 | 0.062588 | -0.0092046 | 0.052394 | -0.0054937 | -0.00049785 | -0.0031834 | -0.0047216 | 0.031671 | -0.014086 | -121.0241 | -0.35572 | -121.3008 | 0.042971 | 0.041569 | 0.10076 | -121.5007 | -121.0921 | -4.6608 | -121.2548 | -0.034533 | 0.045757 | 0.090166 | -121.7546 | -0.010236 | -0.080625 | 0.46642 | 0.18968 | 0.19992 | -0.082027 | -0.022837 | -0.26416 | -0.15813 | 0.39839 | 0.23568 | 0.49984 | -0.077839 | -0.03343 | 121.5334 | 121.532 | 121.5912 | 121.1348 | -121.6243 | 121.4559 | 121.5362 | 121.5806 | 116.8297 | -121.8782
1763.2188 | 121.6507 | -121.4996 | 0.10986 | 1.4211e-13 | -0.051955 | -0.0087886 | 0.062801 | -0.0094182 | 0.052822 | -0.013124 | -7.0448e-05 | -0.0029698 | -0.004508 | 0.031671 | -0.0143 | -121.0378 | -0.36488 | -121.3145 | 0.042971 | 0.041569 | 0.09618 | -121.4961 | -121.0967 | -4.7249 | -121.264 | -0.034533 | 0.045757 | 0.094744 | -121.7501 | 0.003498 | -0.066892 | 0.46184 | 0.1851 | 0.18161 | -0.068294 | -0.013683 | -0.25043 | -0.1444 | 0.40296 | 0.23568 | 0.4861 | -0.064106 | -0.015119 | 121.5426 | 121.5412 | 121.5958 | 121.1348 | -121.606 | 121.4651 | 121.5454 | 121.5944 | 116.7748 | -121.8599
1764.9688 | 121.7606 | -121.4859 | 0.09613 | 1.4211e-13 | -0.051527 | -0.0085748 | 0.062374 | -0.008991 | 0.053035 | -0.013124 | -0.00049785 | -0.0029698 | -0.0047216 | 0.032098 | -0.014727 | -121.0424 | -0.36946 | -121.3145 | 0.038393 | 0.032411 | 0.09618 | -121.5145 | -121.1012 | -4.7752 | -121.2731 | -0.034533 | 0.050335 | 0.085587 | -121.7592 | -0.028551 | -0.057737 | 0.44353 | 0.17137 | 0.19992 | -0.063719 | 5e-05 | -0.27332 | -0.13066 | 0.38465 | 0.21278 | 0.4861 | -0.045795 | -0.010543 | 121.5243 | 121.5183 | 121.5821 | 121.1164 | -121.6106 | 121.4514 | 121.5362 | 121.5715 | 116.7107 | -121.8553
1766.7188 | 121.669 | -121.5271 | 0.12817 | 1.4211e-13 | -0.051741 | -0.0087886 | 0.062374 | -0.0092046 | 0.053035 | 0.0097668 | -0.00028425 | -0.0029698 | -0.0047216 | 0.031671 | -0.014941 | -121.0469 | -0.37404 | -121.3283 | 0.047549 | 0.03699 | 0.10076 | -121.5099 | -121.1012 | -4.8302 | -121.2869 | -0.034533 | 0.050335 | 0.094744 | -121.7684 | 0.017227 | -0.080625 | 0.48015 | 0.19884 | 0.18161 | -0.091184 | -0.027415 | -0.24128 | -0.16271 | 0.42585 | 0.24025 | 0.48152 | -0.077839 | -0.03343 | 121.5746 | 121.5641 | 121.6279 | 121.1531 | -121.638 | 121.4926 | 121.5774 | 121.6218 | 116.6969 | -121.8966
1768.4062 | 121.7239 | -121.5134 | 0.11902 | 1.4211e-13 | -0.051741 | -0.0087886 | 0.062588 | -0.0092046 | 0.052608 | 0.0021363 | -0.00028425 | -0.0029698 | -0.0047216 | 0.031884 | -0.014727 | -121.0698 | -0.36946 | -121.3328 | 0.038393 | 0.041569 | 0.09618 | -121.5282 | -121.1379 | -4.8851 | -121.2914 | -0.039111 | 0.054914 | 0.090166 | -121.773 | -0.014822 | -0.080626 | 0.44353 | 0.18052 | 0.19535 | -0.07745 | -0.022839 | -0.25959 | -0.15813 | 0.37549 | 0.22194 | 0.48152 | -0.064105 | -0.028853 | 121.5518 | 121.5549 | 121.6095 | 121.1439 | -121.6472 | 121.4743 | 121.5683 | 121.6035 | 116.6282 | -121.892
1770.1562 | 121.6782 | -121.5546 | 0.12817 | 1.4211e-13 | -0.051741 | -0.0087886 | 0.062374 | -0.008991 | 0.053035 | -0.0054937 | -0.00028425 | -0.0025424 | -0.004508 | 0.031884 | -0.0143 | -121.0698 | -0.37404 | -121.342 | 0.047549 | 0.046148 | 0.10534 | -121.5373 | -121.1425 | -4.9309 | -121.296 | -0.04369 | 0.054914 | 0.094744 | -121.7913 | 0.017219 | -0.080625 | 0.48472 | 0.21256 | 0.19535 | -0.082026 | -0.022837 | -0.23671 | -0.17186 | 0.41211 | 0.25856 | 0.49526 | -0.07326 | -0.03343 | 121.6021 | 121.6007 | 121.6599 | 121.1805 | -121.6655 | 121.5109 | 121.6095 | 121.6493 | 116.6237 | -121.9194
1771.9219 | 121.7331 | -121.5408 | 0.11444 | 1.4211e-13 | -0.051741 | -0.0092158 | 0.062588 | -0.0094182 | 0.053035 | -0.013124 | -7.0448e-05 | -0.0029698 | -0.0047216 | 0.031671 | -0.014727 | -121.0698 | -0.37862 | -121.3512 | 0.047549 | 0.041569 | 0.09618 | -121.5328 | -121.1379 | -4.9904 | -121.3006 | -0.034533 | 0.045757 | 0.090166 | -121.7913 | 0.008065 | -0.066892 | 0.47099 | 0.18968 | 0.18161 | -0.072872 | -0.018261 | -0.25044 | -0.14897 | 0.40295 | 0.24025 | 0.49068 | -0.068684 | -0.024275 | 121.5884 | 121.5824 | 121.637 | 121.1622 | -121.6472 | 121.5063 | 121.5866 | 121.631 | 116.5504 | -121.9057
1773.6875 | 121.7102 | -121.5912 | 0.11902 | 1.4211e-13 | -0.051955 | -0.0087886 | 0.062588 | -0.0092046 | 0.053035 | -0.013124 | -0.00028425 | -0.0031834 | -0.004508 | 0.031884 | -0.014727 | -121.079 | -0.37404 | -121.3603 | 0.042971 | 0.03699 | 0.091601 | -121.5465 | -121.1562 | -5.0545 | -121.3143 | -0.039111 | 0.054914 | 0.094744 | -121.8004 | 0.044683 | -0.076048 | 0.51219 | 0.23087 | 0.18619 | -0.082029 | -0.027418 | -0.20924 | -0.15813 | 0.43499 | 0.27686 | 0.4861 | -0.064105 | -0.024275 | 121.6342 | 121.6282 | 121.6828 | 121.2171 | -121.6655 | 121.5521 | 121.6461 | 121.6859 | 116.5367 | -121.9194
1775.375 | 121.843 | -121.5179 | 0.082397 | 1.4211e-13 | -0.051527 | -0.0090022 | 0.062588 | -0.008991 | 0.052822 | -0.0054937 | -7.0448e-05 | -0.0027562 | -0.0051488 | 0.031884 | -0.014727 | -121.0882 | -0.38777 | -121.3695 | 0.047549 | 0.041569 | 0.10534 | -121.5557 | -121.1974 | -5.1141 | -121.3189 | -0.039111 | 0.041178 | 0.085587 | -121.8142 | -0.037718 | -0.034848 | 0.42979 | 0.14847 | 0.18619 | -0.040828 | 0.02294 | -0.29622 | -0.12151 | 0.32054 | 0.19904 | 0.49526 | -0.041219 | 0.00319 | 121.5655 | 121.5595 | 121.6233 | 121.1302 | -121.6381 | 121.4788 | 121.5591 | 121.6035 | 116.4039 | -121.8966
1777.125 | 121.843 | -121.5225 | 0.082397 | 1.4211e-13 | -0.051741 | -0.0090022 | 0.062801 | -0.0094182 | 0.052822 | -0.0054937 | -0.00028425 | -0.0025424 | -0.004508 | 0.031671 | -0.014513 | -121.0882 | -0.3832 | -121.3603 | 0.047549 | 0.03699 | 0.09618 | -121.5648 | -121.2066 | -5.1782 | -121.3189 | -0.039111 | 0.050335 | 0.085587 | -121.8279 | -0.042298 | -0.034848 | 0.43437 | 0.16221 | 0.20451 | -0.045407 | 0.013783 | -0.30538 | -0.12151 | 0.31596 | 0.20362 | 0.509 | -0.032062 | 0.00319 | 121.5701 | 121.5595 | 121.6187 | 121.1393 | -121.6472 | 121.4834 | 121.5729 | 121.6081 | 116.3444 | -121.9103
1778.875 | 121.8521 | -121.5271 | 0.059509 | 1.4211e-13 | -0.051741 | -0.0087886 | 0.062374 | -0.0094182 | 0.052822 | -0.013124 | -0.00028425 | -0.0023288 | -0.0049352 | 0.031884 | -0.014727 | -121.1019 | -0.39235 | -121.3786 | 0.038393 | 0.03699 | 0.10076 | -121.5694 | -121.2066 | -5.2377 | -121.3326 | -0.034533 | 0.050335 | 0.090166 | -121.8233 | -0.042299 | -0.021116 | 0.42521 | 0.14847 | 0.19077 | -0.022519 | 0.04125 | -0.29622 | -0.094042 | 0.32054 | 0.19446 | 0.49068 | -0.009174 | 0.030657 | 121.5655 | 121.5641 | 121.6279 | 121.1347 | -121.6289 | 121.4926 | 121.5774 | 121.6173 | 116.2894 | -121.8828
1780.625 | 121.7651 | -121.5683 | 0.09613 | 1.4211e-13 | -0.051741 | -0.0087886 | 0.062588 | -0.0092046 | 0.052822 | 0.0021363 | -0.00028425 | -0.0027562 | -0.0047216 | 0.032098 | -0.014727 | -121.1065 | -0.39693 | -121.3924 | 0.042971 | 0.046148 | 0.10534 | -121.574 | -121.2203 | -5.3064 | -121.3372 | -0.039111 | 0.050335 | 0.090166 | -121.8279 | -0.00568 | -0.053159 | 0.46183 | 0.17594 | 0.18162 | -0.049982 | 0.009207 | -0.2596 | -0.13524 | 0.348 | 0.23108 | 0.49068 | -0.045795 | -0.005964 | 121.6113 | 121.6144 | 121.6736 | 121.1714 | -121.6701 | 121.5292 | 121.6186 | 121.6585 | 116.2619 | -121.924
1782.3281 | 121.7606 | -121.5866 | 0.10071 | 1.4211e-13 | -0.051955 | -0.0087886 | 0.062588 | -0.009632 | 0.052608 | -0.013124 | -7.0448e-05 | -0.0027562 | -0.0047216 | 0.031671 | -0.014513 | -121.1156 | -0.38777 | -121.3878 | 0.042971 | 0.041569 | 0.091601 | -121.5923 | -121.2203 | -5.3522 | -121.3418 | -0.039111 | 0.050335 | 0.094744 | -121.8371 | -0.005685 | -0.057737 | 0.47098 | 0.19883 | 0.20451 | -0.059139 | -0.009107 | -0.25045 | -0.13982 | 0.36631 | 0.24481 | 0.49526 | -0.050373 | -0.005964 | 121.6296 | 121.6282 | 121.6782 | 121.1988 | -121.693 | 121.5475 | 121.6369 | 121.6814 | 116.2345 | -121.9378
1784.0938 | 121.8155 | -121.5958 | 0.086975 | 1.4211e-13 | -0.051955 | -0.0087886 | 0.062374 | -0.0092046 | 0.052822 | -0.0054937 | -0.00028425 | -0.0027562 | -0.0047216 | 0.031884 | -0.014727 | -121.1294 | -0.39235 | -121.3969 | 0.038393 | 0.046148 | 0.091601 | -121.5969 | -121.2295 | -5.4208 | -121.351 | -0.039111 | 0.050335 | 0.094744 | -121.8416 | -0.001108 | -0.048582 | 0.4664 | 0.19882 | 0.19993 | -0.040827 | 0.004626 | -0.24587 | -0.12609 | 0.36631 | 0.24481 | 0.49068 | -0.03664 | 0.007769 | 121.6342 | 121.6419 | 121.6874 | 121.2034 | -121.6838 | 121.5567 | 121.6461 | 121.6905 | 116.1749 | -121.9286
1785.8438 | 121.7377 | -121.6003 | 0.10986 | 1.4211e-13 | -0.051955 | -0.0087886 | 0.062801 | -0.0092046 | 0.052822 | -0.0054937 | -0.00028425 | -0.0027562 | -0.0049352 | 0.032098 | -0.014941 | -121.1248 | -0.39235 | -121.4015 | 0.038393 | 0.041569 | 0.10534 | -121.5923 | -121.2386 | -5.4804 | -121.351 | -0.04369 | 0.059493 | 0.090166 | -121.86 | 0.008048 | -0.07147 | 0.47556 | 0.19882 | 0.19078 | -0.068294 | -0.004526 | -0.25961 | -0.15355 | 0.36173 | 0.24939 | 0.509 | -0.05037 | -0.019697 | 121.6387 | 121.6419 | 121.7057 | 121.208 | -121.7022 | 121.5567 | 121.6598 | 121.6905 | 116.12 | -121.9698
1787.6094 | 121.7514 | -121.5958 | 0.10529 | 1.4211e-13 | -0.052168 | -0.0090022 | 0.06216 | -0.0094182 | 0.052822 | -0.013124 | -7.0448e-05 | -0.0029698 | -0.004508 | 0.031884 | -0.014727 | -121.1339 | -0.39693 | -121.4061 | 0.042971 | 0.041569 | 0.10076 | -121.6015 | -121.2386 | -5.549 | -121.3555 | -0.029954 | 0.050335 | 0.085587 | -121.86 | -0.005687 | -0.062315 | 0.46183 | 0.18967 | 0.19535 | -0.063717 | -0.004527 | -0.26419 | -0.13524 | 0.35715 | 0.24023 | 0.50442 | -0.054951 | -0.019699 | 121.6387 | 121.6373 | 121.6965 | 121.1988 | -121.7067 | 121.5658 | 121.6461 | 121.6814 | 116.0467 | -121.9652
1789.3125 | 121.7926 | -121.6049 | 0.11902 | 1.4211e-13 | -0.051955 | -0.0087886 | 0.062588 | -0.0092046 | 0.052608 | -0.020755 | -7.0448e-05 | -0.0029698 | -0.004508 | 0.032098 | -0.015154 | -121.1431 | -0.41067 | -121.4107 | 0.042971 | 0.041569 | 0.10076 | -121.6152 | -121.2386 | -5.6086 | -121.3601 | -0.039111 | 0.054914 | 0.094744 | -121.86 | -0.010269 | -0.076048 | 0.46182 | 0.19424 | 0.20451 | -0.07745 | -0.01826 | -0.25503 | -0.15813 | 0.36631 | 0.24481 | 0.49984 | -0.064105 | -0.024275 | 121.6479 | 121.6465 | 121.7057 | 121.1943 | -121.7342 | 121.5658 | 121.6598 | 121.6997 | 115.9964 | -121.979
1791.0625 | 121.907 | -121.5775 | 0.086975 | 1.4211e-13 | -0.051955 | -0.0083612 | 0.062801 | -0.009632 | 0.052822 | -0.020755 | -0.00049785 | -0.0025424 | -0.0051488 | 0.032098 | -0.014513 | -121.1523 | -0.41525 | -121.4244 | 0.038393 | 0.041569 | 0.10534 | -121.6198 | -121.2523 | -5.691 | -121.3693 | -0.039111 | 0.050335 | 0.090166 | -121.8783 | -0.042313 | -0.048582 | 0.4252 | 0.15305 | 0.19536 | -0.045406 | 0.018362 | -0.30081 | -0.12609 | 0.32511 | 0.20819 | 0.509 | -0.03664 | 0.003191 | 121.6158 | 121.619 | 121.6828 | 121.1622 | -121.7067 | 121.5383 | 121.6278 | 121.6676 | 115.8865 | -121.9652
1792.75 | 121.8063 | -121.6141 | 0.086975 | 1.4211e-13 | -0.052382 | -0.0087886 | 0.062801 | -0.0092046 | 0.052822 | -0.0054937 | -7.0448e-05 | -0.0027562 | -0.0049352 | 0.031884 | -0.014941 | -121.1568 | -0.41067 | -121.4244 | 0.038393 | 0.03699 | 0.10076 | -121.6335 | -121.2615 | -5.7597 | -121.3738 | -0.034533 | 0.059493 | 0.085587 | -121.8783 | -0.019429 | -0.048582 | 0.45725 | 0.18967 | 0.2091 | -0.049985 | 0.013784 | -0.26419 | -0.12151 | 0.35257 | 0.24023 | 0.50442 | -0.027482 | -0.001388 | 121.6525 | 121.6511 | 121.7148 | 121.2034 | -121.7205 | 121.5795 | 121.6736 | 121.6997 | 115.8544 | -121.9652
1794.4531 | 121.9116 | -121.5866 | 0.068665 | 1.4211e-13 | -0.052168 | -0.0087886 | 0.062374 | -0.009632 | 0.053035 | -0.0054937 | -7.0448e-05 | -0.0027562 | -0.0049352 | 0.031884 | -0.0143 | -121.1614 | -0.41983 | -121.4336 | 0.042971 | 0.046148 | 0.09618 | -121.6243 | -121.2615 | -5.8192 | -121.3784 | -0.039111 | 0.054914 | 0.094744 | -121.892 | -0.037737 | -0.025694 | 0.4252 | 0.15304 | 0.19078 | -0.022517 | 0.027515 | -0.3054 | -0.10778 | 0.3251 | 0.20818 | 0.51358 | -0.013751 | 0.026079 | 121.6296 | 121.6328 | 121.6828 | 121.1668 | -121.693 | 121.5475 | 121.6415 | 121.6814 | 115.7674 | -121.9607
1796.2031 | 121.843 | -121.6095 | 0.07782 | 1.4211e-13 | -0.051955 | -0.0090022 | 0.062588 | -0.0092046 | 0.052608 | -0.013124 | -7.0448e-05 | -0.0027562 | -0.0049352 | 0.032098 | -0.014727 | -121.166 | -0.41525 | -121.4427 | 0.042971 | 0.03699 | 0.10076 | -121.6381 | -121.2707 | -5.9016 | -121.383 | -0.034533 | 0.054914 | 0.094744 | -121.9012 | -0.028586 | -0.034849 | 0.44351 | 0.16678 | 0.19536 | -0.04083 | 0.022939 | -0.29166 | -0.11235 | 0.33884 | 0.22649 | 0.51816 | -0.022906 | 0.016924 | 121.6525 | 121.6465 | 121.7103 | 121.1943 | -121.7159 | 121.575 | 121.6644 | 121.7042 | 115.7079 | -121.979
1797.9688 | 121.907 | -121.5958 | 0.068665 | 1.4211e-13 | -0.052168 | -0.0090022 | 0.062801 | -0.0094182 | 0.052822 | -0.0054937 | -0.00028425 | -0.0029698 | -0.0049352 | 0.031671 | -0.014727 | -121.1706 | -0.42898 | -121.4427 | 0.033814 | 0.046148 | 0.10076 | -121.6472 | -121.2798 | -5.9886 | -121.3876 | -0.039111 | 0.054914 | 0.085587 | -121.8966 | -0.051477 | -0.034851 | 0.4252 | 0.15304 | 0.20452 | -0.022517 | 0.032094 | -0.30082 | -0.10778 | 0.31594 | 0.20818 | 0.509 | -0.013751 | 0.016922 | 121.6296 | 121.6419 | 121.6965 | 121.1668 | -121.7159 | 121.5567 | 121.6507 | 121.6814 | 115.6072 | -121.9652
1799.7188 | 121.9116 | -121.582 | 0.082397 | 1.4211e-13 | -0.052382 | -0.0087886 | 0.062588 | -0.0094182 | 0.052394 | -0.0054937 | -0.00028425 | -0.0029698 | -0.0047216 | 0.032098 | -0.014727 | -121.1797 | -0.4244 | -121.4519 | 0.038393 | 0.03699 | 0.10534 | -121.6472 | -121.2798 | -6.0619 | -121.3922 | -0.029954 | 0.054914 | 0.085587 | -121.9103 | -0.06521 | -0.044004 | 0.40231 | 0.13015 | 0.19536 | -0.045407 | 0.02294 | -0.32829 | -0.11235 | 0.30221 | 0.18987 | 0.51816 | -0.027483 | 0.00319 | 121.6204 | 121.619 | 121.6874 | 121.1576 | -121.7296 | 121.5521 | 121.6369 | 121.6676 | 115.5202 | -121.9927
1801.4531 | 121.7651 | -121.6644 | 0.10529 | 1.4211e-13 | -0.052809 | -0.0090022 | 0.062801 | -0.0092046 | 0.052608 | -0.0054937 | -7.0448e-05 | -0.0029698 | -0.0047216 | 0.031884 | -0.014513 | -121.1889 | -0.42898 | -121.4565 | 0.042971 | 0.046148 | 0.09618 | -121.6472 | -121.2844 | -6.1397 | -121.4059 | -0.034533 | 0.050335 | 0.090166 | -121.9103 | 0.017188 | -0.062315 | 0.47555 | 0.20797 | 0.19078 | -0.059138 | -0.009106 | -0.24589 | -0.13982 | 0.38003 | 0.25853 | 0.50442 | -0.054951 | -0.01512 | 121.7074 | 121.7106 | 121.7606 | 121.2354 | -121.7525 | 121.6299 | 121.7148 | 121.7546 | 115.5247 | -122.0156
1803.1406 | 121.9254 | -121.6049 | 0.068665 | 1.4211e-13 | -0.052382 | -0.0087886 | 0.062588 | -0.009632 | 0.053249 | -0.013124 | -0.00028425 | -0.0027562 | -0.0047216 | 0.031884 | -0.014727 | -121.1843 | -0.42898 | -121.4565 | 0.042971 | 0.046148 | 0.10076 | -121.6518 | -121.289 | -6.2175 | -121.4105 | -0.039111 | 0.054914 | 0.085587 | -121.9241 | -0.046901 | -0.025694 | 0.42062 | 0.14846 | 0.19536 | -0.022517 | 0.032094 | -0.31914 | -0.10778 | 0.31594 | 0.19444 | 0.51358 | -0.013751 | 0.016922 | 121.6479 | 121.6511 | 121.7057 | 121.1759 | -121.7205 | 121.5658 | 121.6598 | 121.6905 | 115.3874 | -121.9927
1804.8906 | 121.8887 | -121.6461 | 0.082397 | 1.4211e-13 | -0.052168 | -0.0087886 | 0.062588 | -0.009632 | 0.052822 | 0.0021363 | -7.0448e-05 | -0.0027562 | -0.0049352 | 0.031884 | -0.014941 | -121.1889 | -0.44272 | -121.4656 | 0.042971 | 0.046148 | 0.10076 | -121.6564 | -121.289 | -6.3183 | -121.4151 | -0.04369 | 0.045757 | 0.099323 | -121.9241 | -0.01028 | -0.039426 | 0.45724 | 0.1805 | 0.19078 | -0.036249 | 0.018362 | -0.27794 | -0.12609 | 0.35714 | 0.23106 | 0.509 | -0.03664 | 0.016926 | 121.6891 | 121.6923 | 121.7469 | 121.2034 | -121.7388 | 121.6024 | 121.6919 | 121.7454 | 115.3279 | -122.0065
1806.6406 | 121.7972 | -121.6782 | 0.11444 | 1.4211e-13 | -0.052596 | -0.0090022 | 0.06216 | -0.0094182 | 0.053035 | -0.013124 | -0.00049785 | -0.0027562 | -0.0047216 | 0.032312 | -0.014941 | -121.1889 | -0.44272 | -121.4748 | 0.042971 | 0.041569 | 0.10534 | -121.6656 | -121.2981 | -6.4053 | -121.4105 | -0.034533 | 0.054914 | 0.085587 | -121.9378 | 0.012606 | -0.07147 | 0.48928 | 0.20339 | 0.19079 | -0.072872 | -0.009104 | -0.25963 | -0.14897 | 0.38003 | 0.26769 | 0.52732 | -0.059527 | -0.028854 | 121.7211 | 121.7197 | 121.7835 | 121.2354 | -121.78 | 121.6436 | 121.7331 | 121.7637 | 115.2729 | -122.0522
1808.3906 | 121.8063 | -121.6827 | 0.11902 | 1.4211e-13 | -0.052382 | -0.0092158 | 0.062588 | -0.009632 | 0.052608 | -0.013124 | -0.00028425 | -0.0031834 | -0.0047216 | 0.032098 | -0.014727 | -121.2026 | -0.44272 | -121.4839 | 0.038393 | 0.03699 | 0.09618 | -121.6747 | -121.3073 | -6.4877 | -121.4105 | -0.029954 | 0.045757 | 0.094744 | -121.9332 | 0.008025 | -0.080626 | 0.48013 | 0.19881 | 0.19079 | -0.082029 | -0.022839 | -0.25047 | -0.14897 | 0.37545 | 0.27226 | 0.52274 | -0.073262 | -0.024275 | 121.7211 | 121.7197 | 121.7789 | 121.24 | -121.7937 | 121.6528 | 121.7285 | 121.7775 | 115.1951 | -122.0522
1810.0781 | 121.9391 | -121.6141 | 0.073242 | 1.4211e-13 | -0.052809 | -0.0092158 | 0.062588 | -0.0094182 | 0.052822 | -0.013124 | -7.0448e-05 | -0.0029698 | -0.0047216 | 0.032312 | -0.014513 | -121.2072 | -0.4473 | -121.4839 | 0.042971 | 0.041569 | 0.10076 | -121.6793 | -121.3073 | -6.5747 | -121.4196 | -0.039111 | 0.054914 | 0.090166 | -121.9424 | -0.065218 | -0.030271 | 0.40688 | 0.13015 | 0.19537 | -0.031673 | 0.027517 | -0.3283 | -0.11235 | 0.30678 | 0.19444 | 0.52274 | -0.018328 | 0.016924 | 121.657 | 121.6556 | 121.7148 | 121.1668 | -121.7525 | 121.575 | 121.669 | 121.7042 | 115.0394 | -122.0156
1811.8281 | 121.8796 | -121.637 | 0.10529 | 1.4211e-13 | -0.052382 | -0.0090022 | 0.062588 | -0.0094182 | 0.052822 | -0.013124 | -7.0448e-05 | -0.0029698 | -0.004508 | 0.032098 | -0.014727 | -121.2072 | -0.44272 | -121.4839 | 0.047549 | 0.046148 | 0.10076 | -121.6793 | -121.3119 | -6.68 | -121.4196 | -0.034533 | 0.041178 | 0.094744 | -121.947 | -0.04233 | -0.057737 | 0.42977 | 0.15304 | 0.19537 | -0.059138 | -0.004527 | -0.30999 | -0.13982 | 0.32509 | 0.21733 | 0.52732 | -0.064108 | -0.010542 | 121.6845 | 121.6831 | 121.7377 | 121.1942 | -121.7846 | 121.6024 | 121.6781 | 121.7317 | 114.957 | -122.0522
1813.5938 | 121.8246 | -121.6827 | 0.11902 | 1.4211e-13 | -0.052596 | -0.0090022 | 0.062588 | -0.0092046 | 0.052608 | 0.0021363 | -0.00028425 | -0.0027562 | -0.0047216 | 0.032098 | -0.014727 | -121.2118 | -0.4473 | -121.4977 | 0.038393 | 0.03699 | 0.10076 | -121.6793 | -121.3119 | -6.7807 | -121.4334 | -0.04369 | 0.054914 | 0.090166 | -121.947 | 0.003446 | -0.080626 | 0.47097 | 0.18508 | 0.18163 | -0.082029 | -0.01826 | -0.26421 | -0.16271 | 0.37087 | 0.24937 | 0.51358 | -0.064105 | -0.028853 | 121.7211 | 121.7197 | 121.7835 | 121.2354 | -121.7983 | 121.639 | 121.7377 | 121.7729 | 114.902 | -122.066
1815.2812 | 121.8475 | -121.6827 | 0.086975 | 1.4211e-13 | -0.052809 | -0.0087886 | 0.062374 | -0.0092046 | 0.052608 | 0.0021363 | -7.0448e-05 | -0.0029698 | -0.0047216 | 0.032525 | -0.014513 | -121.2163 | -0.45645 | -121.4931 | 0.038393 | 0.046148 | 0.10076 | -121.6976 | -121.3164 | -6.8677 | -121.4334 | -0.029954 | 0.059493 | 0.090166 | -121.9653 | -0.01487 | -0.048582 | 0.46639 | 0.18966 | 0.20453 | -0.040827 | 0.013784 | -0.28253 | -0.11693 | 0.36629 | 0.24937 | 0.53189 | -0.027482 | 0.003191 | 121.7211 | 121.7289 | 121.7835 | 121.2263 | -121.7846 | 121.6528 | 121.7422 | 121.7729 | 114.815 | -122.0522
1817.0312 | 121.9254 | -121.6827 | 0.091553 | 1.4211e-13 | -0.052809 | -0.0092158 | 0.062801 | -0.009632 | 0.052822 | -0.0054937 | -0.00028425 | -0.0027562 | -0.0051488 | 0.032312 | -0.014727 | -121.2255 | -0.46561 | -121.4977 | 0.042971 | 0.046148 | 0.10534 | -121.7022 | -121.3119 | -6.9639 | -121.4334 | -0.034533 | 0.054914 | 0.094744 | -121.9698 | -0.019449 | -0.048582 | 0.45723 | 0.18508 | 0.20453 | -0.045405 | 0.013784 | -0.2871 | -0.12609 | 0.37087 | 0.24937 | 0.53647 | -0.036639 | 0.003191 | 121.7257 | 121.7289 | 121.7881 | 121.2171 | -121.7937 | 121.6482 | 121.7377 | 121.7775 | 114.7189 | -122.0614
1818.7812 | 121.8842 | -121.6599 | 0.09613 | 1.4211e-13 | -0.052809 | -0.0090022 | 0.063015 | -0.0092046 | 0.052394 | 0.0021363 | -0.00028425 | -0.0025424 | -0.004508 | 0.032525 | -0.0143 | -121.2347 | -0.47019 | -121.5022 | 0.042971 | 0.03699 | 0.10992 | -121.693 | -121.321 | -7.06 | -121.4425 | -0.029954 | 0.050335 | 0.094744 | -121.9744 | -0.033179 | -0.053159 | 0.42519 | 0.15761 | 0.19079 | -0.05914 | 0.013786 | -0.31457 | -0.12608 | 0.33882 | 0.21732 | 0.5319 | -0.045795 | -0.001386 | 121.7028 | 121.6968 | 121.7698 | 121.1897 | -121.7892 | 121.6299 | 121.7102 | 121.7546 | 114.5998 | -122.0706
1820.5312 | 121.9757 | -121.6507 | 0.07782 | 1.4211e-13 | -0.052809 | -0.0092158 | 0.062588 | -0.0094182 | 0.052822 | -0.0054937 | -0.00049785 | -0.0029698 | -0.004508 | 0.032312 | -0.014513 | -121.2209 | -0.46103 | -121.5114 | 0.042971 | 0.046148 | 0.10534 | -121.6976 | -121.3256 | -7.1516 | -121.4425 | -0.04369 | 0.054914 | 0.094744 | -121.9744 | -0.046913 | -0.034849 | 0.42977 | 0.1393 | 0.18621 | -0.031672 | 0.027517 | -0.32373 | -0.12151 | 0.32509 | 0.20817 | 0.5319 | -0.022906 | 0.016924 | 121.6937 | 121.6968 | 121.756 | 121.1897 | -121.7754 | 121.607 | 121.7056 | 121.7454 | 114.4991 | -122.0522
1822.2188 | 121.9345 | -121.6644 | 0.082397 | 1.4211e-13 | -0.052809 | -0.0090022 | 0.062801 | -0.008991 | 0.052608 | 0.0021363 | -7.0448e-05 | -0.0027562 | -0.0049352 | 0.032525 | -0.014513 | -121.2347 | -0.46561 | -121.516 | 0.038393 | 0.041569 | 0.10076 | -121.7113 | -121.3256 | -7.2523 | -121.4517 | -0.029954 | 0.054914 | 0.090166 | -121.9836 | -0.046917 | -0.044004 | 0.42977 | 0.14845 | 0.19537 | -0.040828 | 0.018362 | -0.31915 | -0.11235 | 0.33882 | 0.21274 | 0.5319 | -0.027483 | 0.007769 | 121.7028 | 121.706 | 121.7652 | 121.1988 | -121.7937 | 121.6345 | 121.7193 | 121.7546 | 114.4121 | -122.066
1823.9688 | 122.0078 | -121.669 | 0.082397 | 1.4211e-13 | -0.053023 | -0.0092158 | 0.062801 | -0.0094182 | 0.052181 | -0.0054937 | -0.00028425 | -0.0029698 | -0.0049352 | 0.032525 | -0.014727 | -121.2347 | -0.47019 | -121.516 | 0.042971 | 0.041569 | 0.10076 | -121.7159 | -121.3256 | -7.3668 | -121.4563 | -0.039111 | 0.064071 | 0.090166 | -121.979 | -0.046918 | -0.039426 | 0.43434 | 0.15303 | 0.19995 | -0.040828 | 0.018362 | -0.31 | -0.12151 | 0.3434 | 0.21274 | 0.52274 | -0.018326 | 0.007769 | 121.712 | 121.7106 | 121.7698 | 121.1988 | -121.7983 | 121.6299 | 121.7331 | 121.7592 | 114.3022 | -122.0614
1825.7188 | 121.9025 | -121.6873 | 0.09613 | 1.4211e-13 | -0.052809 | -0.0090022 | 0.062374 | -0.0098456 | 0.052608 | -0.0054937 | -0.00028425 | -0.0029698 | -0.0047216 | 0.032525 | -0.014727 | -121.2392 | -0.47935 | -121.516 | 0.042971 | 0.046148 | 0.09618 | -121.7159 | -121.3302 | -7.4629 | -121.4563 | -0.034533 | 0.054914 | 0.090166 | -121.9836 | -0.028607 | -0.053159 | 0.44808 | 0.17134 | 0.19995 | -0.049982 | 5e-05 | -0.29626 | -0.13066 | 0.35713 | 0.23105 | 0.52732 | -0.041216 | -0.005964 | 121.7303 | 121.7335 | 121.7835 | 121.208 | -121.8121 | 121.6528 | 121.7422 | 121.7775 | 114.2244 | -122.0797
1827.4062 | 121.8613 | -121.7102 | 0.1236 | 1.4211e-13 | -0.052809 | -0.0090022 | 0.062588 | -0.008991 | 0.052608 | -0.013124 | -7.0448e-05 | -0.0029698 | -0.0053626 | 0.032739 | -0.014727 | -121.2392 | -0.47477 | -121.5251 | 0.042971 | 0.041569 | 0.10076 | -121.7251 | -121.3393 | -7.5682 | -121.4517 | -0.039111 | 0.059493 | 0.090166 | -122.0019 | -0.014877 | -0.080625 | 0.47096 | 0.18507 | 0.19995 | -0.082027 | -0.022837 | -0.29169 | -0.16271 | 0.37086 | 0.25852 | 0.55021 | -0.064103 | -0.03343 | 121.7532 | 121.7518 | 121.811 | 121.2354 | -121.8487 | 121.6711 | 121.7697 | 121.8004 | 114.142 | -122.1255
1829.1562 | 121.9757 | -121.6736 | 0.068665 | 1.4211e-13 | -0.053023 | -0.0092158 | 0.062801 | -0.0094182 | 0.053249 | -0.013124 | -0.00028425 | -0.0029698 | -0.0049352 | 0.032312 | -0.014513 | -121.253 | -0.4885 | -121.5343 | 0.047549 | 0.046148 | 0.10534 | -121.7251 | -121.3393 | -7.6781 | -121.4654 | -0.039111 | 0.050335 | 0.094744 | -121.9973 | -0.051498 | -0.021116 | 0.42061 | 0.1393 | 0.19079 | -0.022517 | 0.036672 | -0.32373 | -0.10778 | 0.33424 | 0.20816 | 0.53189 | -0.01833 | 0.026079 | 121.7211 | 121.7197 | 121.7789 | 121.1851 | -121.7937 | 121.6345 | 121.7239 | 121.7683 | 113.9954 | -122.066
1830.8438 | 122.0078 | -121.6919 | 0.082397 | 1.4211e-13 | -0.052809 | -0.0094296 | 0.062801 | -0.0098456 | 0.052608 | 0.0021363 | -0.00049785 | -0.0027562 | -0.0047216 | 0.032312 | -0.014513 | -121.253 | -0.4885 | -121.5389 | 0.042971 | 0.046148 | 0.10076 | -121.7297 | -121.3348 | -7.788 | -121.4608 | -0.04369 | 0.054914 | 0.099323 | -121.9973 | -0.037766 | -0.039426 | 0.43892 | 0.15303 | 0.19079 | -0.036249 | 0.018362 | -0.30542 | -0.12609 | 0.35713 | 0.23105 | 0.53647 | -0.027483 | 0.016926 | 121.7349 | 121.738 | 121.7927 | 121.2034 | -121.8121 | 121.6482 | 121.7468 | 121.7912 | 113.9039 | -122.0797
1832.5938 | 121.994 | -121.6965 | 0.073242 | 1.4211e-13 | -0.052809 | -0.0092158 | 0.062374 | -0.0094182 | 0.052608 | -0.0054937 | -0.00028425 | -0.0025424 | -0.0049352 | 0.032312 | -0.014941 | -121.2667 | -0.49308 | -121.5389 | 0.047549 | 0.046148 | 0.10076 | -121.7342 | -121.3439 | -7.8979 | -121.4654 | -0.029954 | 0.045757 | 0.090166 | -122.0065 | -0.037768 | -0.025693 | 0.42976 | 0.15761 | 0.19537 | -0.027094 | 0.027517 | -0.31 | -0.1032 | 0.35255 | 0.23105 | 0.54105 | -0.027485 | 0.016924 | 121.744 | 121.7426 | 121.7972 | 121.2034 | -121.8075 | 121.6665 | 121.7422 | 121.7866 | 113.7986 | -122.0797
1834.3594 | 121.8521 | -121.7194 | 0.10986 | 1.4211e-13 | -0.05345 | -0.0092158 | 0.062374 | -0.0094182 | 0.052608 | -0.013124 | -7.0448e-05 | -0.0033972 | -0.0049352 | 0.032739 | -0.014513 | -121.2667 | -0.49766 | -121.5434 | 0.033814 | 0.041569 | 0.10076 | -121.7388 | -121.3393 | -8.0124 | -121.47 | -0.034533 | 0.050335 | 0.094744 | -122.0111 | -0.019459 | -0.076049 | 0.45265 | 0.17591 | 0.19537 | -0.068294 | -0.009104 | -0.29169 | -0.1444 | 0.38002 | 0.24936 | 0.54105 | -0.059528 | -0.015119 | 121.7532 | 121.7609 | 121.8201 | 121.2217 | -121.8487 | 121.6848 | 121.7697 | 121.8141 | 113.707 | -122.1209
1836.0469 | 121.8887 | -121.7422 | 0.1236 | 1.4211e-13 | -0.052596 | -0.0087886 | 0.062374 | -0.0094182 | 0.053035 | -0.013124 | -7.0448e-05 | -0.0029698 | -0.0047216 | 0.032525 | -0.014727 | -121.2667 | -0.49308 | -121.548 | 0.042971 | 0.046148 | 0.10534 | -121.7434 | -121.3302 | -8.1314 | -121.4746 | -0.039111 | 0.059493 | 0.094744 | -122.0248 | -0.001149 | -0.080625 | 0.47554 | 0.19423 | 0.19537 | -0.077448 | -0.018259 | -0.28254 | -0.16271 | 0.41206 | 0.26767 | 0.55021 | -0.064103 | -0.028852 | 121.7852 | 121.7884 | 121.8476 | 121.2492 | -121.867 | 121.7031 | 121.8017 | 121.837 | 113.6108 | -122.1484
1837.7969 | 121.9574 | -121.7468 | 0.068665 | 1.4211e-13 | -0.053237 | -0.0094296 | 0.062588 | -0.009632 | 0.053035 | -0.013124 | -0.00028425 | -0.0029698 | -0.0053626 | 0.032525 | -0.014727 | -121.2713 | -0.50224 | -121.5526 | 0.038393 | 0.041569 | 0.10992 | -121.748 | -121.3485 | -8.2459 | -121.4792 | -0.034533 | 0.054914 | 0.090166 | -122.0202 | -0.001151 | -0.030272 | 0.47554 | 0.19423 | 0.19538 | -0.027096 | 0.041251 | -0.27339 | -0.1032 | 0.39833 | 0.26767 | 0.54105 | -0.013751 | 0.021501 | 121.7852 | 121.7884 | 121.8567 | 121.2446 | -121.8166 | 121.7123 | 121.8017 | 121.837 | 113.5009 | -122.0889
1839.5625 | 121.8887 | -121.756 | 0.15106 | 1.4211e-13 | -0.053237 | -0.0092158 | 0.06216 | -0.0098456 | 0.052394 | 0.0021363 | -0.00028425 | -0.0027562 | -0.0049352 | 0.032312 | -0.014727 | -121.2759 | -0.50682 | -121.548 | 0.042971 | 0.046148 | 0.10534 | -121.7434 | -121.3485 | -8.3604 | -121.4837 | -0.034533 | 0.050335 | 0.090166 | -122.0248 | 0.012583 | -0.10809 | 0.48011 | 0.20796 | 0.19537 | -0.10491 | -0.045725 | -0.26881 | -0.1856 | 0.40748 | 0.27225 | 0.54105 | -0.10073 | -0.060896 | 121.799 | 121.8021 | 121.8613 | 121.2492 | -121.8945 | 121.7214 | 121.8063 | 121.8461 | 113.3956 | -122.1759
1841.25 | 122.0078 | -121.7239 | 0.082397 | 1.4211e-13 | -0.053237 | -0.0092158 | 0.062588 | -0.0094182 | 0.053035 | -0.013124 | -0.00028425 | -0.0031834 | -0.0047216 | 0.032739 | -0.014941 | -121.2804 | -0.51598 | -121.5618 | 0.038393 | 0.046148 | 0.10076 | -121.7526 | -121.3531 | -8.4748 | -121.4792 | -0.034533 | 0.054914 | 0.094744 | -122.0202 | -0.028618 | -0.044004 | 0.44349 | 0.16218 | 0.1908 | -0.036249 | 0.018362 | -0.29627 | -0.11693 | 0.37086 | 0.24478 | 0.54105 | -0.027483 | 0.012347 | 121.7623 | 121.7701 | 121.8247 | 121.208 | -121.835 | 121.6894 | 121.7789 | 121.8187 | 113.2491 | -122.1026
1843 | 121.9666 | -121.7468 | 0.091553 | 1.4211e-13 | -0.053237 | -0.0092158 | 0.062588 | -0.0094182 | 0.052394 | -0.013124 | -7.0448e-05 | -0.0029698 | -0.0047216 | 0.032312 | -0.014513 | -121.2804 | -0.51598 | -121.5618 | 0.052128 | 0.046148 | 0.10076 | -121.7617 | -121.3622 | -8.5939 | -121.4883 | -0.034533 | 0.064071 | 0.085587 | -122.0294 | -0.014888 | -0.039425 | 0.46638 | 0.18507 | 0.19996 | -0.045405 | 0.009206 | -0.28254 | -0.12609 | 0.38459 | 0.25851 | 0.54105 | -0.027482 | -0.005966 | 121.799 | 121.793 | 121.8476 | 121.2309 | -121.8533 | 121.7123 | 121.8109 | 121.8324 | 113.1529 | -122.1209
1844.75 | 121.9116 | -121.7697 | 0.10529 | 1.4211e-13 | -0.052809 | -0.0090022 | 0.062588 | -0.009632 | 0.052822 | -0.0054937 | -0.00028425 | -0.0025424 | -0.0047216 | 0.032525 | -0.014727 | -121.285 | -0.52055 | -121.5709 | 0.038393 | 0.041569 | 0.10076 | -121.7571 | -121.3531 | -8.7129 | -121.4883 | -0.034533 | 0.054914 | 0.094744 | -122.0294 | 0.012579 | -0.066893 | 0.48469 | 0.1988 | 0.18622 | -0.063717 | -0.004527 | -0.25965 | -0.13982 | 0.41664 | 0.2814 | 0.54105 | -0.050372 | -0.010542 | 121.8081 | 121.8113 | 121.8705 | 121.2492 | -121.8624 | 121.7352 | 121.8246 | 121.8645 | 113.0568 | -122.1347
1846.4531 | 121.9162 | -121.7972 | 0.10529 | 1.4211e-13 | -0.053023 | -0.0092158 | 0.062588 | -0.0094182 | 0.052394 | 0.0021363 | 0.00014315 | -0.0027562 | -0.0047216 | 0.032312 | -0.014941 | -121.2896 | -0.52971 | -121.5663 | 0.052128 | 0.03699 | 0.10076 | -121.7663 | -121.3531 | -8.8411 | -121.4837 | -0.04369 | 0.050335 | 0.094744 | -122.0339 | 0.030887 | -0.053158 | 0.50758 | 0.23084 | 0.19996 | -0.068296 | -0.004527 | -0.23677 | -0.14898 | 0.4441 | 0.31344 | 0.55021 | -0.054951 | -0.010542 | 121.8493 | 121.8342 | 121.8979 | 121.2675 | -121.8716 | 121.7535 | 121.8475 | 121.8919 | 112.9561 | -122.1392
1848.2031 | 121.8933 | -121.7514 | 0.10986 | 1.4211e-13 | -0.053237 | -0.0092158 | 0.062374 | -0.0094182 | 0.052608 | -0.013124 | 0.00035675 | -0.0029698 | -0.0049352 | 0.032739 | -0.014513 | -121.285 | -0.52971 | -121.5663 | 0.038393 | 0.046148 | 0.10992 | -121.7663 | -119.8284 | -8.9739 | -121.4929 | -0.025376 | 0.041178 | 0.094744 | -122.0431 | -0.014889 | -0.07147 | 0.46638 | 0.18507 | 0.19996 | -0.063715 | 5.3e-05 | -0.2917 | -0.13524 | 1.923 | 0.25851 | 0.55021 | -0.068685 | -0.015119 | 121.7898 | 121.7976 | 121.8613 | 121.2217 | -121.8762 | 121.726 | 121.7926 | 121.8461 | 112.7775 | -122.153
1849.9531 | 121.9528 | -121.7789 | 0.10529 | 1.4211e-13 | -0.053237 | -0.0094296 | 0.062801 | -0.009632 | 0.052608 | -0.0054937 | -7.0448e-05 | -0.0025424 | -0.0047216 | 0.032953 | -0.014727 | -121.2988 | -0.53429 | -121.5801 | 0.038393 | 0.041569 | 0.10076 | -121.7617 | -119.8101 | -9.0884 | -121.4975 | -0.034533 | 0.050335 | 0.094744 | -122.0431 | 0.017156 | -0.066893 | 0.48011 | 0.1988 | 0.18164 | -0.063717 | -0.004527 | -0.26423 | -0.13982 | 1.9688 | 0.2814 | 0.54563 | -0.054951 | -0.010542 | 121.8173 | 121.8204 | 121.8796 | 121.2446 | -121.867 | 121.7443 | 121.8292 | 121.8736 | 112.6905 | -122.1484
1851.7031 | 121.9849 | -121.7239 | 0.10071 | 1.4211e-13 | -0.053023 | -0.0090022 | 0.062588 | -0.0098456 | 0.052608 | -0.013124 | -0.00028425 | -0.0027562 | -0.0049352 | 0.032525 | -0.014513 | -121.3033 | -0.53887 | -121.5801 | 0.038393 | 0.046148 | 0.10076 | -121.78 | -119.7688 | -9.2212 | -121.4975 | -0.04369 | 0.050335 | 0.090166 | -122.0477 | -0.056091 | -0.062315 | 0.4206 | 0.14387 | 0.19996 | -0.05456 | 5.1e-05 | -0.32375 | -0.1444 | 1.9551 | 0.22647 | 0.55021 | -0.050373 | -0.010542 | 121.7623 | 121.7701 | 121.8247 | 121.1851 | -121.8807 | 121.6802 | 121.7743 | 121.8141 | 112.5028 | -122.1484
1853.3906 | 121.994 | -121.756 | 0.086975 | 1.4211e-13 | -0.05345 | -0.0092158 | 0.062588 | -0.009632 | 0.052608 | -0.0054937 | -0.00028425 | -0.0029698 | -0.0051488 | 0.032312 | -0.014727 | -121.3079 | -0.53429 | -121.5846 | 0.042971 | 0.046148 | 0.10534 | -121.7755 | -118.8714 | -9.3539 | -121.5021 | -0.034533 | 0.054914 | 0.090166 | -122.0477 | -0.01947 | -0.044004 | 0.44806 | 0.17133 | 0.1908 | -0.040827 | 0.018362 | -0.2917 | -0.12151 | 2.8846 | 0.25393 | 0.54563 | -0.032061 | 0.003191 | 121.799 | 121.8021 | 121.8613 | 121.2217 | -121.8624 | 121.7214 | 121.8109 | 121.8461 | 112.402 | -122.1347
1855.1406 | 121.994 | -121.7651 | 0.09613 | 1.4211e-13 | -0.053237 | -0.0092158 | 0.062801 | -0.009632 | 0.052822 | -0.013124 | -0.00049785 | -0.0029698 | -0.0049352 | 0.032525 | -0.014941 | -121.3033 | -0.53887 | -121.5984 | 0.038393 | 0.041569 | 0.10992 | -121.7846 | -118.8852 | -9.4867 | -121.5066 | -0.034533 | 0.054914 | 0.090166 | -122.0523 | -0.019471 | -0.057737 | 0.4618 | 0.16675 | 0.18622 | -0.054561 | 0.013786 | -0.28713 | -0.13066 | 2.88 | 0.25851 | 0.54563 | -0.041216 | -0.005964 | 121.8035 | 121.8067 | 121.8751 | 121.2263 | -121.8807 | 121.7306 | 121.8201 | 121.8553 | 112.2784 | -122.1484
1856.9062 | 121.9803 | -121.7377 | 0.086975 | 1.4211e-13 | -0.05345 | -0.0092158 | 0.062588 | -0.0098456 | 0.052822 | 0.0021363 | -0.00049785 | -0.0027562 | -0.0051488 | 0.032739 | -0.014941 | -121.3125 | -0.54803 | -121.5938 | 0.038393 | 0.041569 | 0.10076 | -121.7846 | -119.8238 | -9.6332 | -121.5066 | -0.034533 | 0.050335 | 0.094744 | -122.0523 | -0.046937 | -0.048582 | 0.42518 | 0.14387 | 0.1908 | -0.045406 | 0.013784 | -0.31459 | -0.12151 | 1.9139 | 0.23104 | 0.54563 | -0.03664 | 0.007769 | 121.7761 | 121.7792 | 121.8384 | 121.1896 | -121.8716 | 121.7031 | 121.788 | 121.8324 | 112.1044 | -122.1392
1858.6094 | 122.0032 | -121.7422 | 0.091553 | 1.4211e-13 | -0.053664 | -0.0090022 | 0.062374 | -0.010059 | 0.052822 | -0.0054937 | -0.00028425 | -0.0025424 | -0.0049352 | 0.032525 | -0.014727 | -121.3079 | -0.5526 | -121.5984 | 0.042971 | 0.046148 | 0.10534 | -121.7938 | -120.4373 | -9.7706 | -121.5066 | -0.034533 | 0.054914 | 0.090166 | -122.0568 | -0.051517 | -0.048582 | 0.43433 | 0.14387 | 0.19538 | -0.045405 | 0.013784 | -0.31459 | -0.12609 | 1.3049 | 0.23562 | 0.55021 | -0.036639 | -0.001387 | 121.7852 | 121.7884 | 121.8476 | 121.1896 | -121.8853 | 121.7077 | 121.7972 | 121.8324 | 111.9716 | -122.1484
1860.2969 | 122.0261 | -121.7331 | 0.059509 | 1.4211e-13 | -0.053237 | -0.0094296 | 0.062801 | -0.009632 | 0.052822 | -0.028385 | -0.00028425 | -0.0027562 | -0.0051488 | 0.032739 | -0.014513 | -121.3125 | -0.55718 | -121.5984 | 0.042971 | 0.03699 | 0.10534 | -121.7892 | -121.1837 | -9.908 | -121.5066 | -0.029954 | 0.050335 | 0.085587 | -122.066 | -0.056094 | -0.016538 | 0.4206 | 0.13471 | 0.1908 | -0.022519 | 0.045828 | -0.33291 | -0.089463 | 0.54943 | 0.22646 | 0.55937 | -0.009174 | 0.026078 | 121.7761 | 121.7701 | 121.8384 | 121.1759 | -121.8487 | 121.7031 | 121.7834 | 121.8187 | 111.8251 | -122.1255
1862.0469 | 122.0032 | -121.7651 | 0.082397 | 1.4211e-13 | -0.05345 | -0.0092158 | 0.062374 | -0.009632 | 0.052822 | -0.0054937 | -0.00071145 | -0.0025424 | -0.0049352 | 0.032739 | -0.014513 | -121.3171 | -0.56176 | -121.603 | 0.047549 | 0.03699 | 0.10534 | -121.8029 | -120.2176 | -10.0591 | -121.5066 | -0.034533 | 0.050335 | 0.090166 | -122.066 | -0.037787 | -0.034848 | 0.44806 | 0.16217 | 0.19996 | -0.045407 | 0.02294 | -0.30086 | -0.11693 | 1.5476 | 0.25851 | 0.55937 | -0.032062 | 0.007769 | 121.8127 | 121.8021 | 121.8705 | 121.2034 | -121.8853 | 121.7306 | 121.8155 | 121.8553 | 111.7061 | -122.1484
1863.7969 | 122.0627 | -121.7422 | 0.059509 | 1.4211e-13 | -0.053878 | -0.0096432 | 0.062588 | -0.009632 | 0.052822 | 0.0021363 | -7.0448e-05 | -0.0027562 | -0.0047216 | 0.032739 | -0.014727 | -121.3171 | -0.56634 | -121.603 | 0.047549 | 0.041569 | 0.10534 | -121.7983 | -120.1992 | -10.2102 | -121.5158 | -0.034533 | 0.050335 | 0.085587 | -122.066 | -0.056096 | -0.01196 | 0.42517 | 0.13929 | 0.19538 | -0.01794 | 0.045828 | -0.32375 | -0.094042 | 1.543 | 0.22646 | 0.55021 | -0.009174 | 0.026078 | 121.7898 | 121.7838 | 121.8476 | 121.1759 | -121.8579 | 121.7077 | 121.7926 | 121.8278 | 111.5321 | -122.1255
1865.4844 | 121.9528 | -121.756 | 0.10986 | 1.4211e-13 | -0.053878 | -0.0090022 | 0.062588 | -0.009632 | 0.052608 | -0.013124 | -0.00028425 | -0.0029698 | -0.0051488 | 0.032953 | -0.014727 | -121.3217 | -0.5755 | -121.6121 | 0.047549 | 0.041569 | 0.10534 | -121.8029 | -120.3687 | -10.3658 | -121.5158 | -0.034533 | 0.054914 | 0.094744 | -122.066 | -0.046943 | -0.062314 | 0.43433 | 0.14386 | 0.1908 | -0.068294 | -0.004526 | -0.31002 | -0.1444 | 1.3873 | 0.24019 | 0.55021 | -0.054949 | -0.015119 | 121.8035 | 121.7976 | 121.8613 | 121.1805 | -121.9128 | 121.7214 | 121.8109 | 121.8507 | 111.3901 | -122.1759
1867.1875 | 121.9574 | -121.788 | 0.10071 | 1.4211e-13 | -0.053023 | -0.0094296 | 0.062588 | -0.0094182 | 0.052822 | -0.013124 | -0.00028425 | -0.0027562 | -0.0047216 | 0.033166 | -0.014727 | -121.3262 | -0.5755 | -121.6213 | 0.038393 | 0.03699 | 0.10534 | -121.8075 | -121.3668 | -10.5078 | -121.5112 | -0.020797 | 0.054914 | 0.099323 | -122.0797 | -0.019478 | -0.062315 | 0.46179 | 0.16675 | 0.18623 | -0.063718 | 0.004629 | -0.29171 | -0.12151 | 0.42121 | 0.27682 | 0.56853 | -0.045794 | -0.001385 | 121.8264 | 121.825 | 121.8934 | 121.2125 | -121.9082 | 121.7672 | 121.8429 | 121.8873 | 111.2802 | -122.1804
1868.9531 | 122.0261 | -121.756 | 0.064087 | 1.4211e-13 | -0.054091 | -0.0094296 | 0.062588 | -0.0098456 | 0.052822 | -0.013124 | -7.0448e-05 | -0.0029698 | -0.0047216 | 0.032739 | -0.015154 | -121.3308 | -0.58466 | -121.6213 | 0.047549 | 0.046148 | 0.10992 | -121.8121 | -121.2752 | -10.6772 | -121.5158 | -0.048268 | 0.059493 | 0.094744 | -122.0752 | -0.056101 | -0.016538 | 0.42517 | 0.13471 | 0.19081 | -0.017939 | 0.045829 | -0.31918 | -0.11236 | 0.48074 | 0.24019 | 0.55937 | -0.004594 | 0.030657 | 121.8035 | 121.8021 | 121.8659 | 121.1713 | -121.8762 | 121.7077 | 121.8155 | 121.8507 | 111.0788 | -122.1392
1870.625 | 121.9528 | -121.8109 | 0.11444 | 1.4211e-13 | -0.053878 | -0.0092158 | 0.062588 | -0.0094182 | 0.052822 | -0.013124 | -7.0448e-05 | -0.0027562 | -0.0049352 | 0.032953 | -0.014727 | -121.3308 | -0.58466 | -121.6213 | 0.047549 | 0.03699 | 0.10534 | -121.8121 | -121.376 | -10.842 | -121.5204 | -0.025376 | 0.054914 | 0.090166 | -122.0843 | -0.001169 | -0.066892 | 0.4801 | 0.18964 | 0.19081 | -0.077451 | -0.009104 | -0.2734 | -0.13982 | 0.43494 | 0.29055 | 0.56395 | -0.059527 | -0.024275 | 121.8585 | 121.8479 | 121.9163 | 121.2263 | -121.9265 | 121.7855 | 121.8658 | 121.9011 | 110.9689 | -122.1988
1872.375 | 121.9299 | -121.8292 | 0.13733 | 1.4211e-13 | -0.053664 | -0.0094296 | 0.062801 | -0.0098456 | 0.052608 | -0.0054937 | -0.00028425 | -0.0027562 | -0.0049352 | 0.032739 | -0.014941 | -121.3354 | -0.58466 | -121.6259 | 0.047549 | 0.041569 | 0.10534 | -121.8167 | -121.3622 | -11.0069 | -121.5158 | -0.029954 | 0.050335 | 0.094744 | -122.0797 | 0.012563 | -0.08978 | 0.49384 | 0.20337 | 0.19081 | -0.09576 | -0.031992 | -0.25051 | -0.16728 | 0.46699 | 0.31344 | 0.56395 | -0.086994 | -0.042585 | 121.8768 | 121.8708 | 121.9346 | 121.2446 | -121.954 | 121.7993 | 121.8796 | 121.924 | 110.8224 | -122.2171
1874.0781 | 121.9574 | -121.8109 | 0.091553 | 1.4211e-13 | -0.054091 | -0.0094296 | 0.062588 | -0.0098456 | 0.053249 | -0.013124 | -0.00028425 | -0.0025424 | -0.0049352 | 0.03338 | -0.014941 | -121.3354 | -0.59381 | -121.6259 | 0.033814 | 0.046148 | 0.10534 | -121.8167 | -121.3485 | -11.1946 | -121.5204 | -0.039111 | 0.050335 | 0.081008 | -122.0889 | -0.005748 | -0.057739 | 0.47553 | 0.18506 | 0.19081 | -0.045405 | 0.013784 | -0.27798 | -0.13066 | 0.46241 | 0.29055 | 0.56853 | -0.041218 | -0.010545 | 121.8447 | 121.8571 | 121.9163 | 121.2171 | -121.9082 | 121.7718 | 121.8612 | 121.8919 | 110.6163 | -122.1804
1875.8281 | 121.994 | -121.7926 | 0.10986 | 1.4211e-13 | -0.053878 | -0.0094296 | 0.062801 | -0.009632 | 0.052822 | -0.013124 | -7.0448e-05 | -0.0031834 | -0.0049352 | 0.032953 | -0.014513 | -121.34 | -0.59839 | -121.6213 | 0.042971 | 0.046148 | 0.10534 | -121.8167 | -121.3806 | -11.3548 | -121.5158 | -0.029954 | 0.050335 | 0.090166 | -122.0843 | -0.024058 | -0.066892 | 0.45264 | 0.17133 | 0.19539 | -0.063715 | -0.004526 | -0.29171 | -0.13982 | 0.41205 | 0.27682 | 0.56853 | -0.059528 | -0.019697 | 121.8356 | 121.8388 | 121.8979 | 121.1942 | -121.9265 | 121.7626 | 121.8429 | 121.8828 | 110.4378 | -122.1942
1877.5156 | 121.962 | -121.843 | 0.12817 | 1.4211e-13 | -0.053878 | -0.0096432 | 0.062588 | -0.009632 | 0.052822 | -0.020755 | -7.0448e-05 | -0.0029698 | -0.0049352 | 0.032739 | -0.015154 | -121.3354 | -0.59839 | -121.635 | 0.038393 | 0.041569 | 0.10534 | -121.8258 | -121.376 | -11.5288 | -121.5249 | -0.034533 | 0.054914 | 0.090166 | -122.0889 | 0.017138 | -0.089781 | 0.50757 | 0.20795 | 0.19081 | -0.086605 | -0.022837 | -0.24594 | -0.16271 | 0.46698 | 0.31801 | 0.56395 | -0.07326 | -0.038008 | 121.8813 | 121.8845 | 121.9483 | 121.2446 | -121.954 | 121.8084 | 121.8979 | 121.9331 | 110.3141 | -122.2171
1879.2812 | 122.1085 | -121.7606 | 0.068665 | 1.4211e-13 | -0.053664 | -0.0094296 | 0.062588 | -0.009632 | 0.052394 | 0.0021363 | -0.00028425 | -0.0029698 | -0.0051488 | 0.032953 | -0.014941 | -121.3491 | -0.60297 | -121.635 | 0.042971 | 0.041569 | 0.10534 | -121.8304 | -121.3989 | -11.6982 | -121.5249 | -0.034533 | 0.054914 | 0.085587 | -122.0889 | -0.069839 | -0.025694 | 0.41144 | 0.12555 | 0.19539 | -0.027096 | 0.036672 | -0.32833 | -0.1032 | 0.36169 | 0.23561 | 0.56395 | -0.013751 | 0.016922 | 121.8035 | 121.8021 | 121.8659 | 121.1576 | -121.8991 | 121.726 | 121.8155 | 121.8461 | 110.0623 | -122.1576
1881.0312 | 122.0444 | -121.7972 | 0.086975 | 1.4211e-13 | -0.054305 | -0.0094296 | 0.062588 | -0.009632 | 0.052608 | -0.013124 | -0.00028425 | -0.0031834 | -0.0049352 | 0.033166 | -0.015154 | -121.3583 | -0.61213 | -121.635 | 0.042971 | 0.041569 | 0.10992 | -121.8304 | -121.3943 | -11.8951 | -121.5204 | -0.034533 | 0.059493 | 0.090166 | -122.0935 | -0.033218 | -0.044004 | 0.4389 | 0.16217 | 0.19539 | -0.045406 | 0.022941 | -0.29629 | -0.12151 | 0.40289 | 0.27681 | 0.57311 | -0.027482 | 0.003191 | 121.8402 | 121.8387 | 121.9071 | 121.1851 | -121.9174 | 121.7626 | 121.8567 | 121.8873 | 109.9021 | -122.1804
1882.7656 | 122.0581 | -121.8246 | 0.10986 | 1.4211e-13 | -0.054091 | -0.009857 | 0.062588 | -0.0094182 | 0.052608 | -0.0054937 | -0.00028425 | -0.0027562 | -0.0051488 | 0.03338 | -0.014727 | -121.3491 | -0.61213 | -121.6442 | 0.047549 | 0.046148 | 0.10534 | -121.8396 | -121.3989 | -12.0737 | -121.5249 | -0.039111 | 0.050335 | 0.090166 | -122.0935 | -0.014909 | -0.062314 | 0.47552 | 0.18048 | 0.19539 | -0.063715 | -0.004526 | -0.26883 | -0.14897 | 0.42578 | 0.2997 | 0.56853 | -0.059528 | -0.019697 | 121.8722 | 121.8708 | 121.93 | 121.2125 | -121.9494 | 121.7855 | 121.875 | 121.9148 | 109.7509 | -122.2033
1884.4688 | 121.9437 | -121.8475 | 0.11444 | 1.4211e-13 | -0.053878 | -0.0092158 | 0.062801 | -0.0094182 | 0.052608 | -0.0054937 | 0.00014315 | -0.0031834 | -0.0053626 | 0.033166 | -0.015368 | -121.3537 | -0.6167 | -121.6304 | 0.047549 | 0.046148 | 0.10534 | -121.8304 | -121.3943 | -12.2706 | -121.5295 | -0.039111 | 0.054914 | 0.090166 | -122.0981 | 0.017136 | -0.066892 | 0.49383 | 0.2171 | 0.19997 | -0.068293 | -0.009104 | -0.25052 | -0.15355 | 0.45325 | 0.31801 | 0.56853 | -0.059527 | -0.024275 | 121.8951 | 121.8937 | 121.9529 | 121.2308 | -121.9448 | 121.8084 | 121.9024 | 121.9377 | 109.577 | -122.2125
1886.2188 | 122.0627 | -121.7789 | 0.082397 | 1.4211e-13 | -0.054091 | -0.0096432 | 0.062588 | -0.009632 | 0.052394 | -0.013124 | -7.0448e-05 | -0.0027562 | -0.0053626 | 0.033166 | -0.014941 | -121.3629 | -0.62586 | -121.6442 | 0.042971 | 0.041569 | 0.10076 | -121.8396 | -121.3989 | -12.4629 | -121.5295 | -0.039111 | 0.054914 | 0.090166 | -122.0981 | -0.060685 | -0.039426 | 0.41601 | 0.1347 | 0.19539 | -0.040828 | 0.018362 | -0.31918 | -0.12151 | 0.38 | 0.24935 | 0.56853 | -0.027483 | 0.007769 | 121.8218 | 121.8204 | 121.8796 | 121.153 | -121.922 | 121.7398 | 121.8338 | 121.869 | 109.316 | -122.1804
1887.9688 | 121.9711 | -121.843 | 0.10071 | 1.4211e-13 | -0.053878 | -0.0090022 | 0.062588 | -0.0094182 | 0.052181 | -0.0054937 | -0.00071145 | -0.0029698 | -0.0053626 | 0.033166 | -0.014941 | -121.3537 | -0.62128 | -121.6396 | 0.038393 | 0.041569 | 0.10534 | -121.835 | -121.3989 | -12.6277 | -121.5295 | -0.029954 | 0.059493 | 0.085587 | -122.1026 | 0.00798 | -0.062315 | 0.48926 | 0.20337 | 0.19539 | -0.059139 | 0.004629 | -0.25967 | -0.13066 | 0.44409 | 0.31343 | 0.5731 | -0.041215 | -0.015121 | 121.8813 | 121.8845 | 121.9483 | 121.2217 | -121.9357 | 121.813 | 121.9025 | 121.9285 | 109.2152 | -122.2033
1889.7344 | 122.0169 | -121.8155 | 0.09613 | 1.4211e-13 | -0.054091 | -0.0094296 | 0.062588 | -0.0098456 | 0.052608 | -0.0054937 | -0.00071145 | -0.0027562 | -0.0049352 | 0.033166 | -0.015154 | -121.3674 | -0.63502 | -121.6533 | 0.033814 | 0.046148 | 0.10534 | -121.835 | -121.3943 | -12.8292 | -121.5341 | -0.029954 | 0.059493 | 0.090166 | -122.0981 | -0.019486 | -0.062316 | 0.44805 | 0.16217 | 0.18165 | -0.049982 | 0.009207 | -0.28256 | -0.12608 | 0.4212 | 0.28139 | 0.56395 | -0.036637 | -0.005964 | 121.8493 | 121.8616 | 121.9208 | 121.1805 | -121.9311 | 121.7855 | 121.875 | 121.9057 | 108.9863 | -122.1942
1891.5 | 121.9757 | -121.8704 | 0.11902 | 1.4211e-13 | -0.054091 | -0.0092158 | 0.062801 | -0.0098456 | 0.053035 | -0.020755 | -0.00071145 | -0.0029698 | -0.0051488 | 0.033166 | -0.014941 | -121.3629 | -0.63044 | -121.6533 | 0.038393 | 0.041569 | 0.10992 | -121.8441 | -121.4034 | -13.0352 | -121.5341 | -0.039111 | 0.059493 | 0.090166 | -122.1072 | 0.026288 | -0.080626 | 0.50756 | 0.2171 | 0.19081 | -0.07745 | -0.009103 | -0.23679 | -0.15813 | 0.46698 | 0.33632 | 0.57311 | -0.059526 | -0.028853 | 121.9088 | 121.912 | 121.9803 | 121.24 | -121.9632 | 121.8313 | 121.9299 | 121.9606 | 108.8352 | -122.2262
1893.1875 | 122.0673 | -121.8201 | 0.082397 | 1.4211e-13 | -0.053664 | -0.0090022 | 0.062588 | -0.0098456 | 0.052394 | 0.0021363 | -0.00028425 | -0.0027562 | -0.0049352 | 0.032953 | -0.015154 | -121.3674 | -0.6396 | -121.6533 | 0.042971 | 0.050727 | 0.10076 | -121.8533 | -121.0738 | -13.2504 | -121.5341 | -0.034533 | 0.054914 | 0.094744 | -122.1164 | -0.033224 | -0.039426 | 0.45263 | 0.16675 | 0.19997 | -0.03167 | 0.018362 | -0.2963 | -0.11693 | 0.74629 | 0.28597 | 0.58226 | -0.027483 | 0.012347 | 121.863 | 121.8708 | 121.9208 | 121.1805 | -121.9357 | 121.7855 | 121.875 | 121.9148 | 108.5696 | -122.1988
1894.9375 | 122.1039 | -121.788 | 0.068665 | 1.4211e-13 | -0.054091 | -0.0092158 | 0.062588 | -0.0094182 | 0.052822 | -0.0054937 | -7.0448e-05 | -0.0029698 | -0.0049352 | 0.033166 | -0.014941 | -121.3629 | -0.64418 | -121.6579 | 0.042971 | 0.041569 | 0.10534 | -121.8487 | -121.1837 | -13.461 | -121.5249 | -0.034533 | 0.059493 | 0.090166 | -122.1164 | -0.060688 | -0.025694 | 0.42517 | 0.13012 | 0.19081 | -0.027096 | 0.036672 | -0.32834 | -0.1032 | 0.60436 | 0.26308 | 0.59142 | -0.009172 | 0.021501 | 121.831 | 121.8296 | 121.8934 | 121.1438 | -121.9174 | 121.7535 | 121.8475 | 121.8782 | 108.327 | -122.185
1896.6875 | 122.0306 | -121.843 | 0.09613 | 1.4211e-13 | -0.054519 | -0.0087886 | 0.062588 | -0.010059 | 0.052822 | -0.0054937 | -7.0448e-05 | -0.0025424 | -0.0047216 | 0.033166 | -0.014941 | -121.3674 | -0.65791 | -121.6625 | 0.038393 | 0.041569 | 0.10992 | -121.8441 | -121.3851 | -13.6991 | -121.5387 | -0.025376 | 0.050335 | 0.099323 | -122.1164 | -0.001177 | -0.057737 | 0.47552 | 0.18048 | 0.18165 | -0.054561 | 0.013786 | -0.27341 | -0.12151 | 0.45783 | 0.30428 | 0.57769 | -0.045795 | 0.003193 | 121.8813 | 121.8845 | 121.9529 | 121.185 | -121.9403 | 121.8176 | 121.8933 | 121.9423 | 108.1438 | -122.2125
1898.3906 | 122.1176 | -121.8109 | 0.07782 | 1.4211e-13 | -0.054305 | -0.0096432 | 0.062801 | -0.010059 | 0.052822 | -0.0054937 | -0.00028425 | -0.0031834 | -0.0047216 | 0.03338 | -0.015154 | -121.3766 | -0.64875 | -121.6625 | 0.038393 | 0.041569 | 0.11449 | -121.8533 | -120.7395 | -13.9372 | -121.5341 | -0.034533 | 0.059493 | 0.090166 | -122.1164 | -0.042379 | -0.039427 | 0.43432 | 0.14843 | 0.19081 | -0.036251 | 0.036674 | -0.30545 | -0.11235 | 1.0714 | 0.27681 | 0.58226 | -0.018327 | 0.012346 | 121.8493 | 121.8525 | 121.9254 | 121.1622 | -121.9311 | 121.7764 | 121.8704 | 121.9011 | 107.8737 | -122.1942
1900.1562 | 122.1176 | -121.788 | 0.068665 | 1.4211e-13 | -0.054305 | -0.0094296 | 0.062588 | -0.0098456 | 0.052822 | -0.0054937 | -0.00028425 | -0.0029698 | -0.0049352 | 0.03338 | -0.015154 | -121.3812 | -0.66707 | -121.6671 | 0.042971 | 0.041569 | 0.10076 | -121.8579 | -121.289 | -14.1845 | -121.5295 | -0.034533 | 0.054914 | 0.090166 | -122.1209 | -0.069846 | -0.025694 | 0.40685 | 0.12097 | 0.19081 | -0.027096 | 0.032094 | -0.33292 | -0.1032 | 0.49905 | 0.2585 | 0.59142 | -0.013751 | 0.021501 | 121.831 | 121.8296 | 121.8888 | 121.121 | -121.9265 | 121.7535 | 121.8429 | 121.8782 | 107.6035 | -122.1896
1901.9219 | 122.1222 | -121.8201 | 0.064087 | 1.4211e-13 | -0.054519 | -0.0094296 | 0.06216 | -0.0094182 | 0.052822 | -0.013124 | -0.00049785 | -0.0029698 | -0.0049352 | 0.03338 | -0.014941 | -121.3766 | -0.66707 | -121.6671 | 0.042971 | 0.046148 | 0.10534 | -121.8533 | -121.3989 | -14.45 | -121.5341 | -0.034533 | 0.054914 | 0.094744 | -122.1164 | -0.033224 | -0.021116 | 0.44348 | 0.15301 | 0.18623 | -0.017939 | 0.04125 | -0.2963 | -0.09862 | 0.4212 | 0.28597 | 0.58226 | -0.009173 | 0.030657 | 121.863 | 121.8662 | 121.9254 | 121.153 | -121.9174 | 121.7855 | 121.875 | 121.9148 | 107.37 | -122.1805
1903.6094 | 122.0123 | -121.8384 | 0.1236 | 1.4211e-13 | -0.054091 | -0.0096432 | 0.062588 | -0.0094182 | 0.052394 | -0.0054937 | -7.0448e-05 | -0.0027562 | -0.0049352 | 0.03338 | -0.014727 | -121.3812 | -0.66707 | -121.6716 | 0.047549 | 0.046148 | 0.11449 | -121.8579 | -121.3851 | -14.7065 | -121.5341 | -0.029954 | 0.059493 | 0.094744 | -122.1255 | -0.019492 | -0.076047 | 0.45721 | 0.16674 | 0.18623 | -0.077448 | -0.009102 | -0.28714 | -0.15355 | 0.45325 | 0.30428 | 0.59142 | -0.064103 | -0.028852 | 121.8859 | 121.8845 | 121.9529 | 121.1713 | -121.9815 | 121.8084 | 121.8979 | 121.9331 | 107.1319 | -122.2491
1905.2969 | 122.1497 | -121.8201 | 0.073242 | 1.4211e-13 | -0.054946 | -0.0094296 | 0.062374 | -0.0098456 | 0.052822 | -0.0054937 | -0.00028425 | -0.0031834 | -0.0053626 | 0.033594 | -0.014727 | -121.3812 | -0.67165 | -121.6716 | 0.042971 | 0.041569 | 0.10992 | -121.8716 | -121.3897 | -14.9812 | -121.5341 | -0.029954 | 0.050335 | 0.094744 | -122.1255 | -0.05154 | -0.030271 | 0.4389 | 0.14843 | 0.19997 | -0.031673 | 0.036674 | -0.30546 | -0.1032 | 0.43036 | 0.28597 | 0.59142 | -0.022907 | 0.021502 | 121.863 | 121.8616 | 121.93 | 121.1484 | -121.9448 | 121.7901 | 121.8704 | 121.9148 | 106.8389 | -122.1988
1907.0469 | 121.9986 | -121.8521 | 0.11902 | 1.4211e-13 | -0.054091 | -0.0094296 | 0.062588 | -0.0098456 | 0.052608 | 0.0021363 | -0.00049785 | -0.0029698 | -0.0053626 | 0.03338 | -0.014513 | -121.3903 | -0.68538 | -121.6671 | 0.042971 | 0.041569 | 0.10992 | -121.8716 | -121.2981 | -15.2696 | -121.5341 | -0.034533 | 0.054914 | 0.090166 | -122.1301 | -0.019496 | -0.076048 | 0.46178 | 0.18505 | 0.20455 | -0.07745 | -0.009103 | -0.27799 | -0.15355 | 0.55398 | 0.31801 | 0.596 | -0.064105 | -0.028853 | 121.8951 | 121.8937 | 121.962 | 121.1667 | -121.9906 | 121.8176 | 121.907 | 121.9423 | 106.5825 | -122.2491
1908.8125 | 122.0718 | -121.8201 | 0.082397 | 1.4211e-13 | -0.054519 | -0.0092158 | 0.062374 | -0.009632 | 0.052822 | -0.013124 | -0.00049785 | -0.0025424 | -0.0053626 | 0.033166 | -0.014941 | -121.3858 | -0.68538 | -121.6762 | 0.047549 | 0.03699 | 0.10534 | -121.8762 | -121.376 | -15.581 | -121.5341 | -0.029954 | 0.054914 | 0.090166 | -122.1301 | -0.056119 | -0.034848 | 0.43432 | 0.14385 | 0.19997 | -0.045407 | 0.02294 | -0.31003 | -0.11235 | 0.4441 | 0.28597 | 0.596 | -0.027483 | 0.007769 | 121.8676 | 121.8571 | 121.9254 | 121.1347 | -121.9586 | 121.7901 | 121.875 | 121.9102 | 106.2391 | -122.2125
1910.5625 | 122.0901 | -121.843 | 0.086975 | 1.4211e-13 | -0.054305 | -0.0094296 | 0.062588 | -0.0098456 | 0.053035 | -0.0054937 | -0.00028425 | -0.0025424 | -0.0051488 | 0.03338 | -0.014941 | -121.3903 | -0.69454 | -121.6762 | 0.047549 | 0.046148 | 0.10992 | -121.8762 | -121.3714 | -15.8878 | -121.5341 | -0.034533 | 0.059493 | 0.090166 | -122.1347 | -0.03323 | -0.039426 | 0.45263 | 0.16674 | 0.19997 | -0.040827 | 0.022941 | -0.29172 | -0.12151 | 0.47156 | 0.30885 | 0.60058 | -0.027482 | 0.003191 | 121.8905 | 121.8891 | 121.9529 | 121.1484 | -121.9632 | 121.8084 | 121.9025 | 121.9331 | 105.9552 | -122.2217
1912.25 | 122.081 | -121.8246 | 0.073242 | 1.4211e-13 | -0.054305 | -0.0094296 | 0.062374 | -0.010059 | 0.052822 | 0.0021363 | -0.00028425 | -0.0031834 | -0.0051488 | 0.03338 | -0.014941 | -121.3903 | -0.68996 | -121.6854 | 0.038393 | 0.041569 | 0.10992 | -121.8762 | -121.3943 | -16.1991 | -121.5341 | -0.034533 | 0.059493 | 0.094744 | -122.1301 | -0.051541 | -0.034849 | 0.43432 | 0.13927 | 0.19082 | -0.031673 | 0.036674 | -0.30546 | -0.10778 | 0.43036 | 0.29054 | 0.596 | -0.013749 | 0.021502 | 121.863 | 121.8662 | 121.9346 | 121.1347 | -121.9494 | 121.7901 | 121.8841 | 121.9194 | 105.6255 | -122.2033
1914 | 122.1359 | -121.8246 | 0.068665 | 1.4211e-13 | -0.054732 | -0.0094296 | 0.062374 | -0.0098456 | 0.052608 | -0.013124 | -0.00049785 | -0.0029698 | -0.0055762 | 0.033594 | -0.015154 | -121.3858 | -0.7037 | -121.6808 | 0.042971 | 0.041569 | 0.10534 | -121.8762 | -121.3851 | -16.5288 | -121.5295 | -0.029954 | 0.054914 | 0.090166 | -122.1347 | -0.051541 | -0.025694 | 0.4389 | 0.14385 | 0.19539 | -0.027096 | 0.036672 | -0.31003 | -0.098619 | 0.43952 | 0.29512 | 0.60516 | -0.013751 | 0.021501 | 121.8676 | 121.8662 | 121.93 | 121.1209 | -121.9449 | 121.7947 | 121.8796 | 121.9148 | 105.2959 | -122.2033
1915.75 | 122.0673 | -121.8658 | 0.10986 | 1.4211e-13 | -0.054519 | -0.0096432 | 0.062588 | -0.0094182 | 0.052608 | -0.0054937 | -7.0448e-05 | -0.0029698 | -0.0049352 | 0.033594 | -0.015154 | -121.3995 | -0.70828 | -121.6899 | 0.038393 | 0.046148 | 0.10992 | -121.8762 | -120.9273 | -16.8768 | -121.5341 | -0.034533 | 0.059493 | 0.090166 | -122.1393 | -0.010342 | -0.07147 | 0.46636 | 0.17589 | 0.18624 | -0.063715 | 5.3e-05 | -0.27341 | -0.1444 | 0.93859 | 0.33174 | 0.60516 | -0.05037 | -0.019697 | 121.9042 | 121.912 | 121.9758 | 121.1576 | -121.9861 | 121.8313 | 121.9253 | 121.956 | 104.9891 | -122.2491
1917.4375 | 122.0398 | -121.875 | 0.10071 | 1.4211e-13 | -0.054946 | -0.0096432 | 0.062801 | -0.010059 | 0.052394 | 0.0021363 | -0.00028425 | -0.0027562 | -0.0049352 | 0.033807 | -0.014941 | -121.3995 | -0.71743 | -121.6854 | 0.042971 | 0.041569 | 0.10534 | -121.8853 | -120.9914 | -17.1973 | -121.5387 | -0.029954 | 0.059493 | 0.090166 | -122.1484 | -0.010345 | -0.057737 | 0.47552 | 0.18963 | 0.19997 | -0.059139 | 0.004629 | -0.27342 | -0.13066 | 0.88364 | 0.33632 | 0.60974 | -0.041215 | -0.010542 | 121.918 | 121.9166 | 121.9803 | 121.1576 | -121.9861 | 121.845 | 121.9345 | 121.9652 | 104.6777 | -122.2491
1919.1875 | 122.0947 | -121.8704 | 0.082397 | 1.4211e-13 | -0.054732 | -0.0090022 | 0.062374 | -0.0098456 | 0.052608 | 0.0021363 | -0.00049785 | -0.0029698 | -0.0053626 | 0.033594 | -0.014941 | -121.3995 | -0.71743 | -121.6899 | 0.042971 | 0.050727 | 0.11449 | -121.8853 | -120.9868 | -17.5407 | -121.5341 | -0.029954 | 0.050335 | 0.094744 | -122.1438 | -0.014923 | -0.039426 | 0.47094 | 0.18047 | 0.1954 | -0.03167 | 0.032097 | -0.27342 | -0.11235 | 0.88364 | 0.33632 | 0.60974 | -0.032062 | 0.012347 | 121.9134 | 121.9211 | 121.9849 | 121.153 | -121.9677 | 121.8405 | 121.9208 | 121.9652 | 104.3297 | -122.2262
1920.9375 | 122.0535 | -121.8567 | 0.10529 | 1.4211e-13 | -0.054946 | -0.0092158 | 0.06216 | -0.009632 | 0.052608 | -0.013124 | 0.00014315 | -0.0029698 | -0.0049352 | 0.03338 | -0.014941 | -121.4086 | -0.73117 | -121.6945 | 0.042971 | 0.046148 | 0.10534 | -121.8762 | -120.9868 | -17.8703 | -121.5341 | -0.039111 | 0.054914 | 0.090166 | -122.1438 | -0.019498 | -0.062315 | 0.44805 | 0.16216 | 0.18166 | -0.059138 | 5.1e-05 | -0.28715 | -0.1444 | 0.86991 | 0.32259 | 0.60974 | -0.050372 | -0.01512 | 121.8997 | 121.9028 | 121.962 | 121.1255 | -121.9815 | 121.8176 | 121.9116 | 121.9469 | 103.9863 | -122.2491
1922.625 | 122.1268 | -121.8796 | 0.086975 | 1.4211e-13 | -0.054732 | -0.0094296 | 0.062588 | -0.009632 | 0.052608 | -0.0054937 | -7.0448e-05 | -0.0029698 | -0.0049352 | 0.03338 | -0.014941 | -121.4086 | -0.73117 | -121.6945 | 0.042971 | 0.041569 | 0.10992 | -121.8899 | -120.9639 | -18.2137 | -121.5295 | -0.029954 | 0.050335 | 0.090166 | -122.153 | -0.010346 | -0.044004 | 0.47094 | 0.18505 | 0.1954 | -0.045406 | 0.022941 | -0.27342 | -0.11693 | 0.91569 | 0.35005 | 0.62347 | -0.03664 | 0.003191 | 121.9225 | 121.9211 | 121.9895 | 121.1484 | -121.9769 | 121.8496 | 121.9299 | 121.9697 | 103.6658 | -122.24
1924.3125 | 122.0352 | -121.8521 | 0.11902 | 1.4211e-13 | -0.054946 | -0.009857 | 0.062374 | -0.0098456 | 0.052608 | -0.013124 | -7.0448e-05 | -0.0025424 | -0.0051488 | 0.034021 | -0.014727 | -121.4132 | -0.74033 | -121.6945 | 0.042971 | 0.032411 | 0.10076 | -121.8853 | -120.7762 | -18.5388 | -121.5341 | -0.034533 | 0.059493 | 0.094744 | -122.153 | -0.033233 | -0.076048 | 0.43889 | 0.15758 | 0.19082 | -0.086608 | -0.01826 | -0.30088 | -0.15355 | 1.076 | 0.31801 | 0.61889 | -0.059526 | -0.024275 | 121.8951 | 121.8845 | 121.9529 | 121.1118 | -122.0044 | 121.8176 | 121.9116 | 121.9469 | 103.3133 | -122.272
1926.0625 | 122.1542 | -121.8384 | 0.082397 | 1.4211e-13 | -0.05516 | -0.0096432 | 0.062588 | -0.010059 | 0.052394 | -0.013124 | -0.00028425 | -0.0029698 | -0.0049352 | 0.03338 | -0.014727 | -121.4178 | -0.74491 | -121.7037 | 0.047549 | 0.046148 | 0.10534 | -121.8899 | -121.0738 | -18.983 | -121.5249 | -0.029954 | 0.054914 | 0.094744 | -122.1622 | -0.051545 | -0.034848 | 0.42058 | 0.1347 | 0.18624 | -0.036249 | 0.02294 | -0.32377 | -0.11235 | 0.7646 | 0.31343 | 0.63721 | -0.027483 | 0.012347 | 121.8859 | 121.8845 | 121.9437 | 121.0935 | -121.9723 | 121.8084 | 121.8933 | 121.9331 | 102.8554 | -122.2446
1927.8125 | 122.0718 | -121.8842 | 0.091553 | 1.4211e-13 | -0.05516 | -0.0094296 | 0.062588 | -0.009632 | 0.052394 | -0.0054937 | -0.00049785 | -0.0029698 | -0.0049352 | 0.03338 | -0.015368 | -121.4178 | -0.74948 | -121.7037 | 0.047549 | 0.041569 | 0.10534 | -121.8991 | -121.1196 | -19.3538 | -121.5249 | -0.029954 | 0.064071 | 0.094744 | -122.153 | -0.014926 | -0.044004 | 0.46636 | 0.18047 | 0.1954 | -0.049984 | 0.013784 | -0.26884 | -0.12151 | 0.76459 | 0.35921 | 0.62805 | -0.027482 | 0.003191 | 121.9317 | 121.9257 | 121.9895 | 121.1347 | -121.9906 | 121.8542 | 121.9482 | 121.9789 | 102.5303 | -122.2445
1929.5781 | 122.1588 | -121.843 | 0.082397 | 1.4211e-13 | -0.054946 | -0.0096432 | 0.062374 | -0.0098456 | 0.052608 | -0.013124 | -0.00028425 | -0.0029698 | -0.0047216 | 0.033807 | -0.014941 | -121.4178 | -0.75864 | -121.7128 | 0.042971 | 0.055306 | 0.10534 | -121.8945 | -121.1745 | -19.743 | -121.5249 | -0.039111 | 0.064071 | 0.099323 | -122.1667 | -0.051546 | -0.039426 | 0.42516 | 0.13012 | 0.18166 | -0.027091 | 0.02294 | -0.32378 | -0.12151 | 0.66845 | 0.31801 | 0.64179 | -0.018326 | 0.016926 | 121.8859 | 121.8983 | 121.9483 | 121.0843 | -121.9769 | 121.8038 | 121.907 | 121.9423 | 102.0999 | -122.2491
1931.2656 | 122.1359 | -121.8567 | 0.073242 | 1.4211e-13 | -0.054732 | -0.0094296 | 0.062374 | -0.0098456 | 0.052822 | -0.013124 | -0.00028425 | -0.0029698 | -0.0049352 | 0.033594 | -0.015154 | -121.4224 | -0.75864 | -121.7083 | 0.042971 | 0.041569 | 0.10076 | -121.8991 | -120.6571 | -20.146 | -121.5249 | -0.039111 | 0.054914 | 0.099323 | -122.1622 | -0.042392 | -0.030271 | 0.43431 | 0.14843 | 0.19082 | -0.031673 | 0.027517 | -0.30546 | -0.11235 | 1.1996 | 0.33174 | 0.63721 | -0.018328 | 0.026081 | 121.8997 | 121.8983 | 121.9574 | 121.098 | -121.9723 | 121.8176 | 121.9116 | 121.956 | 101.7107 | -122.2354
1933.0312 | 122.1634 | -121.8475 | 0.082397 | 1.4211e-13 | -0.05516 | -0.0094296 | 0.062374 | -0.009632 | 0.052608 | -0.0054937 | -0.00028425 | -0.0031834 | -0.0049352 | 0.033807 | -0.014941 | -121.4224 | -0.75864 | -121.7083 | 0.047549 | 0.046148 | 0.10992 | -121.9082 | -120.8998 | -20.5168 | -121.5204 | -0.034533 | 0.054914 | 0.094744 | -122.1622 | -0.060705 | -0.034848 | 0.42516 | 0.13927 | 0.19998 | -0.036249 | 0.027519 | -0.31462 | -0.11693 | 0.94775 | 0.32717 | 0.64179 | -0.027483 | 0.012347 | 121.8951 | 121.8937 | 121.9574 | 121.0889 | -121.9906 | 121.813 | 121.9024 | 121.9423 | 101.3307 | -122.2446
1934.7969 | 122.0535 | -121.875 | 0.086975 | 1.4211e-13 | -0.054519 | -0.0094296 | 0.062374 | -0.0098456 | 0.052394 | -0.0054937 | -7.0448e-05 | -0.0025424 | -0.0051488 | 0.033807 | -0.014941 | -121.4224 | -0.7678 | -121.7083 | 0.042971 | 0.046148 | 0.11449 | -121.8991 | -120.7075 | -20.9015 | -121.5204 | -0.04369 | 0.050335 | 0.099323 | -122.1667 | -0.024081 | -0.044004 | 0.45262 | 0.16674 | 0.19082 | -0.040827 | 0.027519 | -0.29173 | -0.13067 | 1.1675 | 0.35463 | 0.64637 | -0.03664 | 0.012348 | 121.918 | 121.9211 | 121.9895 | 121.1072 | -121.9861 | 121.8313 | 121.9253 | 121.9743 | 100.9735 | -122.2537
1936.4844 | 122.0352 | -121.907 | 0.10529 | 1.4211e-13 | -0.054946 | -0.0094296 | 0.062801 | -0.010059 | 0.052394 | -0.013124 | -7.0448e-05 | -0.0027562 | -0.0049352 | 0.033594 | -0.015154 | -121.4178 | -0.78153 | -121.7128 | 0.038393 | 0.041569 | 0.10992 | -121.9037 | -120.7075 | -21.2723 | -121.5249 | -0.029954 | 0.054914 | 0.094744 | -122.1713 | 0.003383 | -0.066893 | 0.48924 | 0.1942 | 0.19082 | -0.063717 | 0.00463 | -0.26427 | -0.13524 | 1.1996 | 0.3821 | 0.64637 | -0.050372 | -0.010542 | 121.9454 | 121.9486 | 122.017 | 121.1255 | -122.0089 | 121.8771 | 121.962 | 122.0018 | 100.6347 | -122.2766
1938.25 | 122.168 | -121.8567 | 0.082397 | 1.4211e-13 | -0.05516 | -0.0094296 | 0.062801 | -0.010059 | 0.052181 | -0.0054937 | -0.00049785 | -0.0027562 | -0.0053626 | 0.033594 | -0.015154 | -121.4224 | -0.77696 | -121.722 | 0.047549 | 0.046148 | 0.10992 | -121.9128 | -120.735 | -21.6569 | -121.5158 | -0.025376 | 0.054914 | 0.094744 | -122.1622 | -0.056129 | -0.034848 | 0.43431 | 0.13469 | 0.19082 | -0.036249 | 0.027519 | -0.30546 | -0.10777 | 1.1217 | 0.3409 | 0.64637 | -0.027483 | 0.012347 | 121.9042 | 121.9028 | 121.9666 | 121.0797 | -121.9952 | 121.8313 | 121.9116 | 121.9514 | 100.1997 | -122.2446
1940.0156 | 122.0352 | -121.8704 | 0.10071 | 1.4211e-13 | -0.05516 | -0.0094296 | 0.062588 | -0.009632 | 0.052822 | -0.0054937 | -0.00028425 | -0.0029698 | -0.0049352 | 0.033807 | -0.015154 | -121.427 | -0.78153 | -121.722 | 0.052128 | 0.046148 | 0.10534 | -121.9082 | -120.8998 | -22.0828 | -121.5158 | -0.029954 | 0.059493 | 0.090166 | -122.1759 | -0.037817 | -0.04858 | 0.44347 | 0.14842 | 0.18624 | -0.05456 | 0.004629 | -0.30547 | -0.13066 | 0.97064 | 0.35464 | 0.6601 | -0.041215 | -0.010542 | 121.9226 | 121.9166 | 121.9758 | 121.0889 | -122.0089 | 121.8405 | 121.9299 | 121.9606 | 99.7877 | -122.2766
1941.7031 | 122.1909 | -121.8521 | 0.073242 | 1.4211e-13 | -0.054732 | -0.0094296 | 0.062588 | -0.010059 | 0.052608 | -0.020755 | -0.00049785 | -0.0029698 | -0.0049352 | 0.033594 | -0.015154 | -121.4315 | -0.79527 | -121.7174 | 0.038393 | 0.046148 | 0.10992 | -121.9128 | -120.8311 | -22.4445 | -121.5158 | -0.039111 | 0.050335 | 0.1039 | -122.1759 | -0.060706 | -0.034849 | 0.42058 | 0.13469 | 0.1954 | -0.027094 | 0.036674 | -0.32378 | -0.11235 | 1.021 | 0.33633 | 0.6601 | -0.022907 | 0.030659 | 121.8905 | 121.8983 | 121.962 | 121.0568 | -121.9861 | 121.813 | 121.9024 | 121.956 | 99.4076 | -122.2491
1943.4062 | 122.1771 | -121.8658 | 0.086975 | 1.4211e-13 | -0.05516 | -0.0094296 | 0.062374 | -0.009632 | 0.052822 | 0.0021363 | -0.00049785 | -0.0036108 | -0.0051488 | 0.034235 | -0.015154 | -121.4178 | -0.80901 | -121.722 | 0.047549 | 0.041569 | 0.10992 | -121.9128 | -120.7304 | -22.8199 | -121.5158 | -0.034533 | 0.059493 | 0.090166 | -122.1667 | -0.046973 | -0.039426 | 0.44805 | 0.14385 | 0.19082 | -0.045406 | 0.022941 | -0.30089 | -0.12151 | 1.1355 | 0.35006 | 0.65095 | -0.027482 | 0.003191 | 121.9134 | 121.9074 | 121.9758 | 121.0568 | -121.9998 | 121.8313 | 121.9253 | 121.956 | 99.0459 | -122.2537
1945.1562 | 122.1405 | -121.8704 | 0.086975 | 1.4211e-13 | -0.05516 | -0.0092158 | 0.062374 | -0.009632 | 0.052608 | -0.0054937 | -0.00049785 | -0.0033972 | -0.0049352 | 0.034021 | -0.015154 | -121.4315 | -0.80901 | -121.7266 | 0.042971 | 0.046148 | 0.10992 | -121.9174 | -120.6754 | -23.232 | -121.5158 | -0.029954 | 0.059493 | 0.094744 | -122.1805 | -0.046975 | -0.044004 | 0.43889 | 0.14385 | 0.19082 | -0.040827 | 0.022941 | -0.31005 | -0.11693 | 1.195 | 0.35464 | 0.66468 | -0.027482 | 0.007769 | 121.9134 | 121.9166 | 121.9803 | 121.0614 | -122.0044 | 121.8405 | 121.9299 | 121.9652 | 98.6384 | -122.2674
1946.8438 | 122.0215 | -121.907 | 0.11902 | 1.4211e-13 | -0.055373 | -0.0092158 | 0.062588 | -0.0094182 | 0.052608 | -0.013124 | -7.0448e-05 | -0.0036108 | -0.0049352 | 0.033807 | -0.015154 | -121.4361 | -0.81816 | -121.722 | 0.047549 | 0.046148 | 0.10992 | -121.9174 | -121.3439 | -23.5571 | -121.5066 | -0.034533 | 0.064071 | 0.094744 | -122.1759 | -0.010354 | -0.07147 | 0.47093 | 0.18505 | 0.1954 | -0.072871 | -0.009103 | -0.26885 | -0.15355 | 0.56312 | 0.40041 | 0.66926 | -0.054948 | -0.024275 | 121.9546 | 121.9532 | 122.017 | 121.0889 | -122.0364 | 121.8725 | 121.9711 | 122.0018 | 98.3499 | -122.2949
1948.6094 | 122.1909 | -121.8613 | 0.082397 | 1.4211e-13 | -0.05516 | -0.0096432 | 0.06216 | -0.010059 | 0.052822 | -0.013124 | -0.00049785 | -0.0033972 | -0.0049352 | 0.033807 | -0.014941 | -121.4315 | -0.81816 | -121.7266 | 0.047549 | 0.055306 | 0.10992 | -121.9174 | -121.3622 | -23.9463 | -121.5158 | -0.034533 | 0.054914 | 0.099323 | -122.1896 | -0.05613 | -0.034848 | 0.42973 | 0.13469 | 0.19082 | -0.027091 | 0.027519 | -0.32836 | -0.11693 | 0.49903 | 0.34548 | 0.67384 | -0.027483 | 0.016926 | 121.9088 | 121.9166 | 121.9712 | 121.0431 | -121.9998 | 121.8267 | 121.9162 | 121.9606 | 97.915 | -122.272
1950.2969 | 122.0901 | -121.8979 | 0.1236 | 1.4211e-13 | -0.05516 | -0.0092158 | 0.062801 | -0.010059 | 0.052394 | -0.013124 | -0.00028425 | -0.0033972 | -0.0049352 | 0.034021 | -0.014941 | -121.4315 | -0.82732 | -121.7266 | 0.047549 | 0.041569 | 0.10534 | -121.922 | -121.3577 | -24.308 | -121.5021 | -0.029954 | 0.059493 | 0.099323 | -122.1805 | -0.024088 | -0.076047 | 0.46635 | 0.17131 | 0.1954 | -0.082027 | -0.018259 | -0.28258 | -0.15355 | 0.54023 | 0.39584 | 0.67842 | -0.064103 | -0.024273 | 121.9454 | 121.9395 | 122.0032 | 121.0706 | -122.0456 | 121.8679 | 121.9574 | 121.9972 | 97.5899 | -122.3041
1952.0625 | 122.0581 | -121.9025 | 0.1236 | 1.4211e-13 | -0.055373 | -0.0094296 | 0.062588 | -0.0098456 | 0.052608 | -0.0054937 | -0.00028425 | -0.0031834 | -0.0051488 | 0.034021 | -0.015582 | -121.4361 | -0.8319 | -121.7312 | 0.042971 | 0.046148 | 0.10534 | -121.922 | -121.3577 | -24.6743 | -121.5112 | -0.039111 | 0.054914 | 0.094744 | -122.185 | -0.01951 | -0.080625 | 0.46635 | 0.17131 | 0.19082 | -0.077448 | -0.018259 | -0.28258 | -0.16271 | 0.54481 | 0.39126 | 0.67384 | -0.068682 | -0.028852 | 121.9454 | 121.9486 | 122.0078 | 121.0706 | -122.0456 | 121.8634 | 121.9574 | 121.9972 | 97.2282 | -122.3086
1953.75 | 122.0901 | -121.9025 | 0.11444 | 1.4211e-13 | -0.055373 | -0.0096432 | 0.062374 | -0.0098456 | 0.052608 | -0.0054937 | -7.0448e-05 | -0.0036108 | -0.0051488 | 0.034021 | -0.014941 | -121.4361 | -0.84106 | -121.7357 | 0.042971 | 0.041569 | 0.11907 | -121.9174 | -121.3439 | -25.0727 | -121.5066 | -0.039111 | 0.059493 | 0.090166 | -122.1805 | -0.014931 | -0.07147 | 0.46635 | 0.16673 | 0.18166 | -0.072872 | 0.004632 | -0.278 | -0.15355 | 0.55855 | 0.39584 | 0.67384 | -0.054948 | -0.024275 | 121.9454 | 121.944 | 122.0215 | 121.0614 | -122.0318 | 121.8634 | 121.962 | 121.9926 | 96.8298 | -122.2949
1955.5 | 122.0947 | -121.8979 | 0.10529 | 1.4211e-13 | -0.055801 | -0.009857 | 0.062588 | -0.010059 | 0.052608 | -0.0054937 | -0.00028425 | -0.0036108 | -0.0051488 | 0.034021 | -0.014941 | -121.4407 | -0.85479 | -121.7403 | 0.047549 | 0.041569 | 0.10534 | -121.9266 | -121.3439 | -25.2238 | -121.5066 | -0.029954 | 0.050335 | 0.094744 | -122.1896 | -0.028667 | -0.057737 | 0.4572 | 0.15758 | 0.18624 | -0.063717 | 5.1e-05 | -0.29174 | -0.13524 | 0.55397 | 0.39126 | 0.683 | -0.054951 | -0.010542 | 121.9454 | 121.9395 | 122.0032 | 121.0431 | -122.0318 | 121.8679 | 121.9482 | 121.9926 | 96.6741 | -122.2949
1957.1875 | 122.1909 | -121.8796 | 0.10071 | 1.4211e-13 | -0.055587 | -0.0096432 | 0.062801 | -0.0098456 | 0.052394 | -0.0054937 | -0.00028425 | -0.0038244 | -0.0049352 | 0.034235 | -0.015154 | -121.4407 | -0.84564 | -121.7403 | 0.047549 | 0.046148 | 0.10992 | -121.9311 | -121.3348 | -25.4435 | -121.5112 | -0.034533 | 0.054914 | 0.099323 | -122.1896 | -0.051556 | -0.053159 | 0.43889 | 0.13927 | 0.19082 | -0.05456 | 0.009208 | -0.31005 | -0.13524 | 0.54481 | 0.36837 | 0.67842 | -0.045794 | -0.001385 | 121.9271 | 121.9257 | 121.9895 | 121.0339 | -122.0318 | 121.845 | 121.9345 | 121.9789 | 96.436 | -122.2903
1958.9375 | 122.2092 | -121.8842 | 0.086975 | 1.4211e-13 | -0.055373 | -0.0094296 | 0.062588 | -0.0098456 | 0.052822 | -0.013124 | -0.00028425 | -0.0033972 | -0.0051488 | 0.034235 | -0.015154 | -121.4453 | -0.85479 | -121.7403 | 0.047549 | 0.046148 | 0.10992 | -121.9311 | -121.321 | -25.8648 | -121.5021 | -0.034533 | 0.054914 | 0.094744 | -122.1988 | -0.046979 | -0.039426 | 0.43889 | 0.14384 | 0.19082 | -0.040827 | 0.022941 | -0.31463 | -0.12151 | 0.56313 | 0.3821 | 0.69673 | -0.032061 | 0.007769 | 121.9317 | 121.9303 | 121.9941 | 121.0294 | -122.0181 | 121.8496 | 121.9391 | 121.9789 | 96.0194 | -122.2858
1960.6406 | 122.0718 | -121.9299 | 0.11902 | 1.4211e-13 | -0.055587 | -0.0094296 | 0.062374 | -0.009632 | 0.052394 | -0.013124 | -0.00028425 | -0.0031834 | -0.0049352 | 0.034235 | -0.014941 | -121.4498 | -0.86853 | -121.7357 | 0.042971 | 0.046148 | 0.10992 | -121.9357 | -121.321 | -26.199 | -121.5021 | -0.025376 | 0.059493 | 0.099323 | -122.1896 | -0.005781 | -0.076048 | 0.48008 | 0.1942 | 0.19998 | -0.072871 | -0.009103 | -0.2597 | -0.14439 | 0.6089 | 0.42788 | 0.68758 | -0.059526 | -0.019696 | 121.9729 | 121.9761 | 122.0398 | 121.0614 | -122.0547 | 121.9046 | 121.9894 | 122.0293 | 95.7309 | -122.3086
1962.4062 | 122.0993 | -121.8979 | 0.11444 | 1.4211e-13 | -0.055587 | -0.009857 | 0.062588 | -0.009632 | 0.052822 | -0.013124 | 0.00014315 | -0.0036108 | -0.0051488 | 0.034235 | -0.014941 | -121.4498 | -0.86853 | -121.7403 | 0.038393 | 0.046148 | 0.10992 | -121.9266 | -121.321 | -26.6065 | -121.5021 | -0.029954 | 0.059493 | 0.099323 | -122.1988 | -0.028667 | -0.076048 | 0.44804 | 0.15758 | 0.18624 | -0.068293 | -0.004525 | -0.3009 | -0.14439 | 0.57686 | 0.39584 | 0.69673 | -0.054948 | -0.015118 | 121.9363 | 121.944 | 122.0078 | 121.0294 | -122.041 | 121.8679 | 121.9574 | 121.9972 | 95.2914 | -122.3132
1964.1406 | 122.1405 | -121.8979 | 0.09613 | 1.4211e-13 | -0.055587 | -0.0094296 | 0.062588 | -0.0098456 | 0.052608 | -0.013124 | -0.00049785 | -0.0031834 | -0.0049352 | 0.034021 | -0.015154 | -121.4498 | -0.87769 | -121.7403 | 0.047549 | 0.046148 | 0.10992 | -121.9311 | -121.3164 | -26.982 | -121.4929 | -0.039111 | 0.050335 | 0.099323 | -122.1896 | -0.033246 | -0.048581 | 0.44804 | 0.15758 | 0.19082 | -0.049982 | 0.013786 | -0.29174 | -0.13524 | 0.58144 | 0.40499 | 0.69673 | -0.045795 | 0.003193 | 121.9454 | 121.944 | 122.0078 | 121.0202 | -122.0273 | 121.8588 | 121.9482 | 121.9972 | 94.9159 | -122.2858
1965.8281 | 122.2046 | -121.9025 | 0.09613 | 1.4211e-13 | -0.055373 | -0.0096432 | 0.062588 | -0.010059 | 0.052822 | -0.013124 | -7.0448e-05 | -0.0038244 | -0.0051488 | 0.034021 | -0.015368 | -121.4498 | -0.88684 | -121.7449 | 0.042971 | 0.041569 | 0.11449 | -121.9311 | -121.3073 | -27.3071 | -121.4929 | -0.029954 | 0.054914 | 0.090166 | -122.2034 | -0.028668 | -0.053159 | 0.45262 | 0.15758 | 0.18624 | -0.054561 | 0.018364 | -0.3009 | -0.12608 | 0.59517 | 0.40957 | 0.71047 | -0.041216 | -0.005964 | 121.9454 | 121.944 | 122.017 | 121.0156 | -122.0273 | 121.8725 | 121.9574 | 121.9926 | 94.5954 | -122.2995
1967.5781 | 122.1222 | -121.9208 | 0.091553 | 1.4211e-13 | -0.055801 | -0.010071 | 0.062588 | -0.009632 | 0.052394 | -0.013124 | -0.00028425 | -0.0036108 | -0.0049352 | 0.034235 | -0.014941 | -121.4544 | -0.88684 | -121.7403 | 0.047549 | 0.046148 | 0.11449 | -121.9449 | -121.3073 | -27.6459 | -121.4975 | -0.025376 | 0.054914 | 0.094744 | -122.1988 | -0.024095 | -0.044004 | 0.46635 | 0.18046 | 0.20456 | -0.045405 | 0.022941 | -0.27801 | -0.11693 | 0.61348 | 0.4233 | 0.70131 | -0.036639 | 0.003191 | 121.9683 | 121.9669 | 122.0353 | 121.0339 | -122.0364 | 121.8954 | 121.9757 | 122.0155 | 94.2749 | -122.2903
1969.2812 | 122.081 | -121.9345 | 0.10986 | 1.4211e-13 | -0.055801 | -0.0096432 | 0.062801 | -0.010059 | 0.052608 | -0.013124 | -0.00049785 | -0.0033972 | -0.0049352 | 0.034235 | -0.015154 | -121.4453 | -0.90058 | -121.754 | 0.042971 | 0.055306 | 0.10534 | -121.9449 | -121.3027 | -28.0488 | -121.4883 | -0.039111 | 0.054914 | 0.090166 | -122.1988 | -0.010362 | -0.066892 | 0.48924 | 0.18046 | 0.19083 | -0.054557 | -0.004526 | -0.26428 | -0.14897 | 0.6318 | 0.44619 | 0.71047 | -0.054949 | -0.019697 | 121.9775 | 121.9898 | 122.0398 | 121.0339 | -122.0547 | 121.8954 | 121.9894 | 122.0247 | 93.8857 | -122.3086
1971.0312 | 122.1954 | -121.8979 | 0.082397 | 1.4211e-13 | -0.055801 | -0.0096432 | 0.062588 | -0.0098456 | 0.052608 | -0.0054937 | -0.00028425 | -0.0033972 | -0.0053626 | 0.034021 | -0.014941 | -121.4544 | -0.90516 | -121.7449 | 0.047549 | 0.046148 | 0.11449 | -121.9403 | -121.2798 | -28.4609 | -121.4792 | -0.039111 | 0.054914 | 0.094744 | -122.1988 | -0.042404 | -0.034848 | 0.44346 | 0.153 | 0.1954 | -0.036249 | 0.032097 | -0.3009 | -0.12151 | 0.61807 | 0.41873 | 0.71963 | -0.027483 | 0.012347 | 121.9454 | 121.944 | 122.0124 | 120.9927 | -122.0227 | 121.8588 | 121.9528 | 121.9926 | 93.437 | -122.2812
1972.7656 | 122.113 | -121.9345 | 0.11902 | 1.4211e-13 | -0.055587 | -0.0094296 | 0.062588 | -0.010059 | 0.052394 | -0.020755 | -0.00049785 | -0.0033972 | -0.0051488 | 0.034235 | -0.014941 | -121.4636 | -0.91431 | -121.754 | 0.047549 | 0.050727 | 0.11449 | -121.9403 | -121.289 | -28.786 | -121.4883 | -0.034533 | 0.054914 | 0.099323 | -122.2034 | -0.005783 | -0.07147 | 0.47093 | 0.18046 | 0.18625 | -0.068292 | -0.004525 | -0.26885 | -0.15355 | 0.64553 | 0.44619 | 0.71505 | -0.064105 | -0.019696 | 121.9821 | 121.9852 | 122.049 | 121.0202 | -122.0593 | 121.9 | 121.9894 | 122.0338 | 93.1485 | -122.3224
1974.5312 | 122.1954 | -121.875 | 0.086975 | 1.4211e-13 | -0.055587 | -0.0094296 | 0.062801 | -0.0098456 | 0.052394 | 0.0021363 | -0.00028425 | -0.0031834 | -0.0047216 | 0.034235 | -0.015154 | -121.4636 | -0.92347 | -121.7586 | 0.047549 | 0.046148 | 0.11449 | -121.9403 | -121.289 | -29.1523 | -121.4792 | -0.039111 | 0.054914 | 0.094744 | -122.2079 | -0.065292 | -0.039426 | 0.41142 | 0.11638 | 0.18167 | -0.040827 | 0.027519 | -0.33294 | -0.12609 | 0.58602 | 0.39584 | 0.72878 | -0.032061 | 0.007769 | 121.9225 | 121.9211 | 121.9895 | 120.9515 | -122.0273 | 121.8359 | 121.9299 | 121.9697 | 92.7227 | -122.2949
1976.2344 | 122.1817 | -121.8887 | 0.091553 | 1.4211e-13 | -0.055801 | -0.0096432 | 0.062588 | -0.0098456 | 0.052394 | -0.0054937 | -0.00028425 | -0.0036108 | -0.0051488 | 0.034448 | -0.015154 | -121.4544 | -0.92805 | -121.7586 | 0.047549 | 0.046148 | 0.11907 | -121.9403 | -121.2798 | -29.5827 | -121.4746 | -0.034533 | 0.064071 | 0.099323 | -122.1988 | -0.051559 | -0.044004 | 0.43431 | 0.13011 | 0.18167 | -0.045405 | 0.02752 | -0.31005 | -0.12609 | 0.60891 | 0.41415 | 0.72421 | -0.027482 | 0.00777 | 121.9363 | 121.9349 | 122.0078 | 120.9607 | -122.0318 | 121.8542 | 121.9528 | 121.9881 | 92.306 | -122.2903
1977.9844 | 122.1268 | -121.9254 | 0.11902 | 1.4211e-13 | -0.055801 | -0.0096432 | 0.062588 | -0.010059 | 0.052394 | -0.013124 | -0.00028425 | -0.0031834 | -0.0049352 | 0.034448 | -0.014941 | -121.459 | -0.94179 | -121.7586 | 0.047549 | 0.055306 | 0.10992 | -121.9494 | -121.2798 | -30.036 | -121.4792 | -0.029954 | 0.054914 | 0.090166 | -122.2079 | -0.024096 | -0.07147 | 0.46635 | 0.16673 | 0.19083 | -0.063713 | -0.009103 | -0.28259 | -0.14897 | 0.64553 | 0.4462 | 0.72878 | -0.064105 | -0.028853 | 121.9729 | 121.9807 | 122.0353 | 120.9836 | -122.0685 | 121.8954 | 121.9803 | 122.0155 | 91.8894 | -122.327
1979.7344 | 122.0718 | -121.9345 | 0.10986 | 1.4211e-13 | -0.056228 | -0.0096432 | 0.062374 | -0.010487 | 0.052608 | -0.020755 | -0.00071145 | -0.0038244 | -0.0049352 | 0.034448 | -0.014941 | -121.459 | -0.93721 | -121.7586 | 0.047549 | 0.046148 | 0.10992 | -121.9449 | -121.2707 | -30.3748 | -121.4746 | -0.039111 | 0.054914 | 0.094744 | -122.2125 | -0.010362 | -0.062314 | 0.47551 | 0.17589 | 0.18625 | -0.063715 | 5.3e-05 | -0.27801 | -0.14897 | 0.66385 | 0.45993 | 0.73794 | -0.054949 | -0.015119 | 121.9821 | 121.9807 | 122.0444 | 120.9973 | -122.0547 | 121.8954 | 121.9894 | 122.0293 | 91.5597 | -122.3224
1981.4844 | 122.2092 | -121.9208 | 0.073242 | 1.4211e-13 | -0.056228 | -0.009857 | 0.062374 | -0.0098456 | 0.052822 | -0.0054937 | -0.00049785 | -0.0033972 | -0.0049352 | 0.034662 | -0.014941 | -121.459 | -0.94636 | -121.7724 | 0.056706 | 0.046148 | 0.11449 | -121.9494 | -121.2707 | -30.8327 | -121.4608 | -0.034533 | 0.059493 | 0.090166 | -122.2125 | -0.028674 | -0.016536 | 0.46177 | 0.14842 | 0.17709 | -0.027094 | 0.041252 | -0.29174 | -0.10778 | 0.65011 | 0.45993 | 0.75168 | -0.013749 | 0.016924 | 121.9775 | 121.9669 | 122.0353 | 120.9744 | -122.0227 | 121.8862 | 121.9803 | 122.0109 | 91.0881 | -122.2858
1983.2344 | 122.113 | -121.9299 | 0.10071 | 1.4211e-13 | -0.056228 | -0.0094296 | 0.062801 | -0.010273 | 0.052394 | -0.0054937 | -0.00049785 | -0.0033972 | -0.0051488 | 0.034448 | -0.014941 | -121.4636 | -0.95094 | -121.7586 | 0.047549 | 0.046148 | 0.11449 | -121.954 | -121.2661 | -31.1486 | -121.47 | -0.029954 | 0.045757 | 0.099323 | -122.2079 | -0.024097 | -0.053159 | 0.46635 | 0.17131 | 0.19541 | -0.05456 | 0.013786 | -0.27801 | -0.13066 | 0.66385 | 0.45993 | 0.73794 | -0.054951 | -0.001385 | 121.9775 | 121.9761 | 122.0444 | 120.979 | -122.0547 | 121.9 | 121.9757 | 122.0293 | 90.7813 | -122.3087
1984.9844 | 122.113 | -121.9391 | 0.10529 | 1.4211e-13 | -0.056228 | -0.0096432 | 0.062374 | -0.009632 | 0.052608 | -0.013124 | -0.00028425 | -0.0033972 | -0.0049352 | 0.034662 | -0.014941 | -121.4682 | -0.95552 | -121.7678 | 0.047549 | 0.055306 | 0.10534 | -121.9494 | -121.2615 | -31.5149 | -121.4654 | -0.029954 | 0.059493 | 0.099323 | -122.2079 | -0.010363 | -0.057737 | 0.47093 | 0.17131 | 0.18167 | -0.04998 | 5.1e-05 | -0.26886 | -0.13524 | 0.67758 | 0.47366 | 0.74252 | -0.045793 | -0.005963 | 121.9866 | 121.9944 | 122.0444 | 120.9836 | -122.0547 | 121.9091 | 121.9986 | 122.0384 | 90.4242 | -122.3132
1986.6719 | 122.1313 | -121.9345 | 0.10071 | 1.4211e-13 | -0.056014 | -0.0096432 | 0.06216 | -0.0098456 | 0.052608 | -0.013124 | -7.0448e-05 | -0.0029698 | -0.0049352 | 0.034876 | -0.015154 | -121.4727 | -0.96468 | -121.7586 | 0.047549 | 0.041569 | 0.10534 | -121.9632 | -121.2569 | -31.8675 | -121.4654 | -0.029954 | 0.059493 | 0.094744 | -122.2171 | -0.028677 | -0.053159 | 0.46177 | 0.17589 | 0.20456 | -0.059139 | 0.004629 | -0.28259 | -0.13066 | 0.67758 | 0.46909 | 0.75168 | -0.041215 | -0.005964 | 121.9821 | 121.9761 | 122.0398 | 120.9698 | -122.0639 | 121.9046 | 121.994 | 122.0293 | 90.067 | -122.3178
1988.4219 | 122.1359 | -121.9208 | 0.10986 | 1.4211e-13 | -0.056228 | -0.0096432 | 0.062588 | -0.010059 | 0.052181 | -0.013124 | -7.0448e-05 | -0.0031834 | -0.0053626 | 0.034662 | -0.015582 | -121.4727 | -0.97384 | -121.7632 | 0.056706 | 0.050727 | 0.11449 | -121.9586 | -121.2523 | -32.2704 | -121.4608 | -0.034533 | 0.059493 | 0.090166 | -122.2171 | -0.037831 | -0.053157 | 0.44804 | 0.15757 | 0.1954 | -0.059136 | 0.004631 | -0.29632 | -0.1444 | 0.66843 | 0.45993 | 0.75626 | -0.05037 | -0.019697 | 121.9775 | 121.9715 | 122.0353 | 120.9469 | -122.0685 | 121.8862 | 121.9803 | 122.0109 | 89.6504 | -122.327
1990.125 | 122.1085 | -121.9666 | 0.11902 | 1.4211e-13 | -0.056228 | -0.009857 | 0.062801 | -0.010273 | 0.052822 | -0.0054937 | -0.00028425 | -0.0036108 | -0.0047216 | 0.034662 | -0.015154 | -121.4636 | -0.98299 | -121.7724 | 0.052128 | 0.046148 | 0.11449 | -121.9632 | -121.2523 | -32.7054 | -121.4563 | -0.025376 | 0.059493 | 0.094744 | -122.2171 | 0.003367 | -0.066891 | 0.50297 | 0.19419 | 0.19083 | -0.072871 | -0.004525 | -0.25055 | -0.14439 | 0.71421 | 0.51029 | 0.76084 | -0.059526 | -0.024275 | 122.0187 | 122.0127 | 122.081 | 120.9836 | -122.0822 | 121.9412 | 122.026 | 122.0613 | 89.2612 | -122.3361
1991.875 | 122.1863 | -121.907 | 0.09613 | 1.4211e-13 | -0.056228 | -0.009857 | 0.062374 | -0.009632 | 0.052394 | -0.0054937 | -0.00028425 | -0.0036108 | -0.0049352 | 0.034448 | -0.014941 | -121.4727 | -0.99215 | -121.7724 | 0.052128 | 0.050727 | 0.11449 | -121.9586 | -121.2432 | -33.0854 | -121.4563 | -0.034533 | 0.059493 | 0.090166 | -122.2125 | -0.051564 | -0.044002 | 0.4343 | 0.13468 | 0.18625 | -0.045403 | 0.018364 | -0.30548 | -0.13066 | 0.66385 | 0.45078 | 0.75626 | -0.036637 | -0.005964 | 121.9592 | 121.9578 | 122.0215 | 120.9149 | -122.0547 | 121.8725 | 121.9665 | 121.9972 | 88.8216 | -122.3087
1993.625 | 122.1542 | -121.9345 | 0.086975 | 1.4211e-13 | -0.056014 | -0.0096432 | 0.062374 | -0.0098456 | 0.052822 | -0.013124 | -7.0448e-05 | -0.0031834 | -0.0051488 | 0.034448 | -0.014941 | -121.4682 | -0.99673 | -121.7678 | 0.052128 | 0.046148 | 0.10534 | -121.9586 | -121.2386 | -33.5295 | -121.4425 | -0.034533 | 0.059493 | 0.099323 | -122.2171 | -0.024098 | -0.034847 | 0.46635 | 0.16673 | 0.19083 | -0.040827 | 0.018362 | -0.28259 | -0.12151 | 0.6959 | 0.49198 | 0.77457 | -0.027482 | 0.012348 | 121.9866 | 121.9807 | 122.0398 | 120.9378 | -122.0456 | 121.9 | 121.994 | 122.0338 | 88.405 | -122.3041
1995.375 | 122.2137 | -121.907 | 0.086975 | 1.4211e-13 | -0.056442 | -0.010071 | 0.062588 | -0.0098456 | 0.052394 | -0.0054937 | -0.00071145 | -0.0031834 | -0.0051488 | 0.034662 | -0.014941 | -121.4727 | -1.0013 | -121.7769 | 0.052128 | 0.050727 | 0.11449 | -121.9586 | -121.234 | -34.0332 | -121.4379 | -0.029954 | 0.064071 | 0.099323 | -122.2263 | -0.051564 | -0.034847 | 0.4343 | 0.13011 | 0.18167 | -0.036248 | 0.027519 | -0.31921 | -0.11693 | 0.67301 | 0.46909 | 0.78831 | -0.022904 | 0.012348 | 121.9592 | 121.9578 | 122.0215 | 120.9057 | -122.0456 | 121.8771 | 121.9711 | 122.0064 | 87.8739 | -122.3132
1997.125 | 122.1085 | -121.9528 | 0.10529 | 1.4211e-13 | -0.056014 | -0.009857 | 0.062801 | -0.0098456 | 0.052608 | -0.020755 | -0.00028425 | -0.0036108 | -0.0049352 | 0.034876 | -0.015368 | -121.4773 | -1.0059 | -121.7769 | 0.042971 | 0.050727 | 0.10534 | -121.9632 | -121.234 | -34.5231 | -121.4425 | -0.039111 | 0.059493 | 0.094744 | -122.2263 | -0.010366 | -0.062315 | 0.4755 | 0.17588 | 0.18625 | -0.054559 | 5.1e-05 | -0.27344 | -0.1444 | 0.71879 | 0.51029 | 0.78373 | -0.045793 | -0.010542 | 121.9958 | 122.0035 | 122.0582 | 120.9469 | -122.0685 | 121.9137 | 122.0123 | 122.0476 | 87.4297 | -122.3315
1998.8125 | 122.1497 | -121.9299 | 0.09613 | 1.4211e-13 | -0.056228 | -0.0096432 | 0.062588 | -0.009632 | 0.052608 | -0.0054937 | -7.0448e-05 | -0.0031834 | -0.0051488 | 0.034662 | -0.015154 | -121.4773 | -1.0196 | -121.7724 | 0.047549 | 0.050727 | 0.11907 | -121.9586 | -121.2295 | -34.8574 | -121.4379 | -0.029954 | 0.064071 | 0.090166 | -122.2263 | -0.028675 | -0.048581 | 0.45261 | 0.15757 | 0.18625 | -0.045403 | 0.022943 | -0.29633 | -0.12608 | 0.70048 | 0.49198 | 0.78831 | -0.032059 | -0.005964 | 121.9775 | 121.9807 | 122.049 | 120.9103 | -122.0547 | 121.9 | 121.994 | 122.0201 | 87.0726 | -122.3224
2000.5781 | 122.2229 | -121.9025 | 0.086975 | 1.4211e-13 | -0.056228 | -0.0096432 | 0.062374 | -0.009632 | 0.052608 | -0.0054937 | -0.00049785 | -0.0033972 | -0.0049352 | 0.034662 | -0.014941 | -121.4727 | -1.0196 | -121.7815 | 0.047549 | 0.041569 | 0.11449 | -121.9723 | -121.2249 | -35.3015 | -121.4334 | -0.034533 | 0.054914 | 0.094744 | -122.2263 | -0.069878 | -0.039426 | 0.42973 | 0.12095 | 0.19083 | -0.045406 | 0.027519 | -0.32379 | -0.12151 | 0.67759 | 0.4691 | 0.79289 | -0.032061 | 0.007769 | 121.95 | 121.944 | 122.017 | 120.8828 | -122.0593 | 121.8679 | 121.9574 | 121.9972 | 86.601 | -122.3132
2002.2812 | 122.1863 | -121.9482 | 0.10071 | 1.4211e-13 | -0.055801 | -0.0094296 | 0.063015 | -0.0098456 | 0.053035 | -0.020755 | -0.00049785 | -0.0036108 | -0.0053626 | 0.034448 | -0.014727 | -121.4773 | -1.0334 | -121.7815 | 0.047549 | 0.055306 | 0.11449 | -121.9723 | -121.2157 | -35.7731 | -121.4288 | -0.029954 | 0.054914 | 0.090166 | -122.2217 | -0.024102 | -0.053159 | 0.47092 | 0.16673 | 0.19083 | -0.045402 | 0.013786 | -0.27344 | -0.13066 | 0.73252 | 0.51945 | 0.79289 | -0.045794 | -0.010542 | 121.9958 | 122.0035 | 122.0627 | 120.9149 | -122.0731 | 121.9183 | 122.0032 | 122.0384 | 86.1751 | -122.3224
2004.0312 | 122.1405 | -121.9574 | 0.11444 | 1.4211e-13 | -0.056014 | -0.0096432 | 0.062588 | -0.0098456 | 0.052394 | -0.013124 | -0.00028425 | -0.0036108 | -0.0047216 | 0.034876 | -0.014941 | -121.4819 | -1.0379 | -121.7724 | 0.042971 | 0.050727 | 0.10992 | -121.9723 | -121.2066 | -36.4553 | -121.4288 | -0.029954 | 0.06865 | 0.094744 | -122.2308 | -0.014947 | -0.07147 | 0.4755 | 0.18504 | 0.19999 | -0.063714 | -0.004525 | -0.27344 | -0.14439 | 0.75084 | 0.5286 | 0.80204 | -0.045791 | -0.019697 | 122.0004 | 122.0081 | 122.0673 | 120.9195 | -122.0868 | 121.9274 | 122.026 | 122.0521 | 85.5021 | -122.3453
2005.7812 | 122.2321 | -121.9345 | 0.073242 | 1.4211e-13 | -0.056014 | -0.009857 | 0.062374 | -0.010273 | 0.052822 | -0.013124 | -0.00028425 | -0.0033972 | -0.0051488 | 0.035089 | -0.015154 | -121.4819 | -1.0471 | -121.7861 | 0.042971 | 0.046148 | 0.11449 | -121.9678 | -121.2203 | -36.8216 | -121.4242 | -0.034533 | 0.059493 | 0.094744 | -122.2308 | -0.033256 | -0.030271 | 0.45261 | 0.14842 | 0.18167 | -0.027094 | 0.041252 | -0.29633 | -0.10778 | 0.71421 | 0.5103 | 0.80662 | -0.013749 | 0.021502 | 121.9775 | 121.9807 | 122.049 | 120.8874 | -122.041 | 121.9 | 121.994 | 122.0293 | 85.1129 | -122.3041
2007.5312 | 122.1268 | -121.9299 | 0.10986 | 1.4211e-13 | -0.056014 | -0.0096432 | 0.062801 | -0.010059 | 0.053035 | -0.0054937 | 0.00014315 | -0.0033972 | -0.0051488 | 0.034876 | -0.015154 | -121.4819 | -1.0563 | -121.7815 | 0.047549 | 0.046148 | 0.11449 | -121.9678 | -121.202 | -37.2658 | -121.4151 | -0.034533 | 0.06865 | 0.094744 | -122.24 | -0.037833 | -0.062314 | 0.44804 | 0.14842 | 0.18625 | -0.063715 | 0.004631 | -0.31006 | -0.1444 | 0.72795 | 0.51488 | 0.82494 | -0.041213 | -0.015119 | 121.9775 | 121.9761 | 122.0444 | 120.8737 | -122.0776 | 121.8954 | 121.9986 | 122.0247 | 84.6642 | -122.3499
2009.2812 | 122.1497 | -121.962 | 0.10529 | 1.4211e-13 | -0.056655 | -0.009857 | 0.063015 | -0.0098456 | 0.052608 | -0.013124 | -7.0448e-05 | -0.0033972 | -0.0051488 | 0.034876 | -0.015154 | -121.4865 | -1.07 | -121.7815 | 0.042971 | 0.050727 | 0.11449 | -121.9769 | -121.2066 | -37.9205 | -121.4105 | -0.029954 | 0.064071 | 0.099323 | -122.2354 | -0.014948 | -0.062315 | 0.4755 | 0.18046 | 0.19541 | -0.054559 | 0.009208 | -0.27344 | -0.13524 | 0.75541 | 0.5515 | 0.82494 | -0.041215 | -0.005963 | 122.0049 | 122.0127 | 122.0765 | 120.892 | -122.0822 | 121.932 | 122.026 | 122.0613 | 84.0415 | -122.3407
2011.0312 | 122.2321 | -121.9116 | 0.086975 | 1.4211e-13 | -0.056228 | -0.010071 | 0.062588 | -0.010059 | 0.052822 | -0.0054937 | -0.00028425 | -0.0036108 | -0.0053626 | 0.034448 | -0.015154 | -121.4865 | -1.0654 | -121.7861 | 0.047549 | 0.050727 | 0.10992 | -121.9815 | -121.1974 | -38.3372 | -121.4059 | -0.025376 | 0.054914 | 0.094744 | -122.2308 | -0.069881 | -0.039426 | 0.42515 | 0.12553 | 0.19541 | -0.036248 | 0.022941 | -0.31921 | -0.11235 | 0.71422 | 0.50572 | 0.82494 | -0.032061 | 0.007769 | 121.9592 | 121.9623 | 122.0215 | 120.8462 | -122.0685 | 121.8862 | 121.9665 | 122.0064 | 83.5744 | -122.3178
2012.7812 | 122.1588 | -121.9482 | 0.10986 | 1.4211e-13 | -0.056655 | -0.0096432 | 0.062801 | -0.010059 | 0.052822 | -0.013124 | -7.0448e-05 | -0.0031834 | -0.0051488 | 0.034876 | -0.014941 | -121.4911 | -1.0791 | -121.7815 | 0.052128 | 0.046148 | 0.10992 | -121.9815 | -121.2066 | -38.8317 | -121.4013 | -0.034533 | 0.059493 | 0.094744 | -122.2446 | -0.03326 | -0.057735 | 0.45719 | 0.16673 | 0.19999 | -0.063715 | 5.3e-05 | -0.29633 | -0.1444 | 0.74168 | 0.54692 | 0.84325 | -0.05037 | -0.015119 | 122.0004 | 121.9944 | 122.0582 | 120.8691 | -122.0914 | 121.9137 | 122.0077 | 122.043 | 83.1166 | -122.3544
2014.4688 | 122.1405 | -121.9666 | 0.11902 | 1.4211e-13 | -0.056228 | -0.009857 | 0.062588 | -0.009632 | 0.052822 | -0.020755 | -0.00028425 | -0.0033972 | -0.0049352 | 0.035089 | -0.014941 | -121.4911 | -1.0837 | -121.7861 | 0.052128 | 0.046148 | 0.11907 | -121.9678 | -121.1928 | -39.2575 | -121.4013 | -0.034533 | 0.064071 | 0.094744 | -122.2354 | -0.001212 | -0.066891 | 0.4755 | 0.18046 | 0.18167 | -0.072871 | 5.4e-05 | -0.26886 | -0.15355 | 0.77373 | 0.56523 | 0.8341 | -0.054948 | -0.024275 | 122.0187 | 122.0127 | 122.0856 | 120.8828 | -122.0868 | 121.932 | 122.0306 | 122.0613 | 82.7091 | -122.3544
2016.2188 | 122.1954 | -121.9391 | 0.09613 | 1.4211e-13 | -0.056655 | -0.0096432 | 0.06216 | -0.009632 | 0.052822 | 0.0021363 | -7.0448e-05 | -0.0031834 | -0.0049352 | 0.034662 | -0.015368 | -121.4865 | -1.0975 | -121.7907 | 0.052128 | 0.046148 | 0.10992 | -121.9861 | -121.1882 | -39.8436 | -121.3922 | -0.025376 | 0.054914 | 0.094744 | -122.2446 | -0.046994 | -0.044002 | 0.45261 | 0.14841 | 0.19541 | -0.049982 | 0.013786 | -0.30549 | -0.12151 | 0.75084 | 0.54693 | 0.85241 | -0.041216 | -0.001386 | 121.9912 | 121.9852 | 122.049 | 120.8416 | -122.0822 | 121.9137 | 121.994 | 122.0338 | 82.0955 | -122.3407
2017.9844 | 122.1359 | -121.9711 | 0.10986 | 1.4211e-13 | -0.056442 | -0.0096432 | 0.062801 | -0.010059 | 0.052822 | -0.0054937 | -0.00028425 | -0.0031834 | -0.0051488 | 0.035089 | -0.015154 | -121.4865 | -1.102 | -121.7861 | 0.047549 | 0.046148 | 0.12365 | -121.9769 | -121.1791 | -40.2511 | -121.3922 | -0.029954 | 0.054914 | 0.090166 | -122.2492 | -0.005793 | -0.062314 | 0.48466 | 0.18504 | 0.19083 | -0.063715 | 0.013789 | -0.27802 | -0.13982 | 0.79204 | 0.57897 | 0.85699 | -0.054949 | -0.019697 | 122.0187 | 122.0173 | 122.0948 | 120.8691 | -122.0868 | 121.9412 | 122.026 | 122.0613 | 81.7201 | -122.359
2019.6719 | 122.0993 | -121.9574 | 0.11902 | 1.4211e-13 | -0.056869 | -0.009857 | 0.062588 | -0.0098456 | 0.052822 | 0.0021363 | 0.00014315 | -0.0031834 | -0.0049352 | 0.035089 | -0.015368 | -121.4911 | -1.1066 | -121.7861 | 0.052128 | 0.055306 | 0.11449 | -121.9815 | -121.1745 | -40.4342 | -121.3784 | -0.034533 | 0.059493 | 0.094744 | -122.24 | -0.024105 | -0.066891 | 0.46634 | 0.1713 | 0.19541 | -0.063713 | -0.004525 | -0.2826 | -0.15355 | 0.78289 | 0.57897 | 0.86157 | -0.059526 | -0.024275 | 122.0095 | 122.0127 | 122.0719 | 120.8508 | -122.1005 | 121.9229 | 122.0169 | 122.0521 | 81.5232 | -122.359
2021.4219 | 122.0901 | -121.9803 | 0.1236 | 1.4211e-13 | -0.056442 | -0.0096432 | 0.062801 | -0.0098456 | 0.052608 | -0.0054937 | -0.00028425 | -0.0036108 | -0.0051488 | 0.034876 | -0.015368 | -121.4911 | -1.1204 | -121.7952 | 0.042971 | 0.050727 | 0.11449 | -121.9815 | -121.1699 | -41.0203 | -121.3784 | -0.039111 | 0.059493 | 0.1039 | -122.2446 | -0.001216 | -0.080625 | 0.48923 | 0.18504 | 0.18625 | -0.072869 | -0.009102 | -0.26429 | -0.16271 | 0.81036 | 0.60186 | 0.86615 | -0.064103 | -0.019695 | 122.0233 | 122.031 | 122.0948 | 120.8599 | -122.1051 | 121.9412 | 122.0398 | 122.0842 | 80.96 | -122.3682
2023.1719 | 122.2 | -121.9528 | 0.091553 | 1.4211e-13 | -0.056442 | -0.0096432 | 0.062588 | -0.0098456 | 0.052608 | -0.013124 | -0.00028425 | -0.0033972 | -0.0051488 | 0.034662 | -0.015154 | -121.4911 | -1.1249 | -121.7952 | 0.056706 | 0.050727 | 0.11449 | -121.9815 | -121.1654 | -41.2859 | -121.3693 | -0.034533 | 0.059493 | 0.094744 | -122.2446 | -0.028682 | -0.034847 | 0.46177 | 0.15757 | 0.18625 | -0.040826 | 0.022941 | -0.29175 | -0.12609 | 0.78747 | 0.58355 | 0.8753 | -0.03206 | 0.003191 | 122.0095 | 122.0035 | 122.0673 | 120.8279 | -122.0731 | 121.9183 | 122.0123 | 122.0476 | 80.667 | -122.3361
2024.8594 | 122.1085 | -121.9757 | 0.10071 | 1.4211e-13 | -0.056655 | -0.009857 | 0.062374 | -0.010273 | 0.052608 | -0.013124 | -0.00049785 | -0.0036108 | -0.0049352 | 0.034876 | -0.015154 | -121.4911 | -1.1341 | -121.7952 | 0.047549 | 0.041569 | 0.11449 | -121.9815 | -121.1516 | -41.6888 | -121.3601 | -0.029954 | 0.054914 | 0.094744 | -122.2446 | -0.005794 | -0.053159 | 0.48466 | 0.18046 | 0.18625 | -0.059139 | 0.013786 | -0.26887 | -0.13066 | 0.82409 | 0.6156 | 0.88446 | -0.045794 | -0.005964 | 122.0233 | 122.0173 | 122.0902 | 120.8416 | -122.0822 | 121.9458 | 122.0306 | 122.0705 | 80.2869 | -122.3453
2026.6094 | 122.1817 | -121.9574 | 0.082397 | 1.4211e-13 | -0.056655 | -0.009857 | 0.062588 | -0.010273 | 0.053035 | -0.0054937 | -0.00049785 | -0.0036108 | -0.0055762 | 0.035089 | -0.014941 | -121.4956 | -1.1478 | -121.7952 | 0.052128 | 0.046148 | 0.10992 | -121.9769 | -121.1425 | -41.9681 | -121.3647 | -0.029954 | 0.059493 | 0.094744 | -122.2583 | -0.019526 | -0.030269 | 0.46177 | 0.16215 | 0.18167 | -0.036249 | 0.027519 | -0.30091 | -0.11235 | 0.81494 | 0.59271 | 0.89362 | -0.022904 | 0.012347 | 122.0095 | 122.0035 | 122.0673 | 120.8096 | -122.0593 | 121.9274 | 122.0169 | 122.0521 | 79.9893 | -122.3407
2028.2969 | 122.1588 | -121.962 | 0.10529 | 1.4211e-13 | -0.056869 | -0.0096432 | 0.062374 | -0.010059 | 0.052608 | 0.0021363 | -0.00071145 | -0.0033972 | -0.0051488 | 0.035089 | -0.014941 | -121.4956 | -1.1524 | -121.7952 | 0.047549 | 0.055306 | 0.11449 | -121.9907 | -121.1425 | -42.371 | -121.3464 | -0.029954 | 0.06865 | 0.090166 | -122.2537 | -0.028685 | -0.057737 | 0.46634 | 0.16672 | 0.19541 | -0.04998 | 0.009208 | -0.29176 | -0.13524 | 0.81952 | 0.6156 | 0.90736 | -0.036636 | -0.01512 | 122.0095 | 122.0173 | 122.0765 | 120.8096 | -122.0959 | 121.932 | 122.0306 | 122.0521 | 79.591 | -122.359
2030.0469 | 122.2366 | -121.9162 | 0.091553 | 1.4211e-13 | -0.056869 | -0.0096432 | 0.062801 | -0.010059 | 0.052608 | -0.020755 | -0.00028425 | -0.0033972 | -0.0053626 | 0.034876 | -0.015154 | -121.5002 | -1.1661 | -121.8044 | 0.047549 | 0.050727 | 0.10992 | -121.9861 | -121.1287 | -42.8701 | -121.351 | -0.025376 | 0.064071 | 0.090166 | -122.2537 | -0.069882 | -0.044004 | 0.41599 | 0.11179 | 0.18167 | -0.040826 | 0.018363 | -0.33753 | -0.11693 | 0.78748 | 0.56525 | 0.90278 | -0.027482 | -0.001387 | 121.9637 | 121.9669 | 122.0261 | 120.7501 | -122.0776 | 121.8908 | 121.9803 | 122.0064 | 79.0461 | -122.3453
2031.7969 | 122.1405 | -121.9574 | 0.091553 | 1.4211e-13 | -0.056869 | -0.0096432 | 0.062374 | -0.010059 | 0.052608 | -0.020755 | -0.00028425 | -0.0033972 | -0.0051488 | 0.035089 | -0.015154 | -121.5002 | -1.1707 | -121.8044 | 0.052128 | 0.041569 | 0.10992 | -121.9861 | -121.1241 | -43.186 | -121.3418 | -0.034533 | 0.059493 | 0.094744 | -122.2583 | -0.028684 | -0.039425 | 0.45719 | 0.15299 | 0.18167 | -0.049984 | 0.018363 | -0.30091 | -0.12609 | 0.83325 | 0.6156 | 0.91651 | -0.03206 | 0.003191 | 122.0095 | 121.999 | 122.0673 | 120.7867 | -122.0776 | 121.9229 | 122.0169 | 122.0521 | 78.7714 | -122.3499
2033.5312 | 122.2046 | -121.9666 | 0.07782 | 1.4211e-13 | -0.056655 | -0.009857 | 0.062588 | -0.009632 | 0.052608 | -0.013124 | -0.00028425 | -0.0033972 | -0.0053626 | 0.035303 | -0.015368 | -121.5048 | -1.1799 | -121.7998 | 0.056706 | 0.046148 | 0.11907 | -121.9952 | -121.1241 | -43.6393 | -121.3372 | -0.034533 | 0.064071 | 0.094744 | -122.2537 | -0.028686 | -0.021114 | 0.46176 | 0.16672 | 0.19541 | -0.031672 | 0.041253 | -0.28718 | -0.11235 | 0.84241 | 0.62934 | 0.91651 | -0.013749 | 0.016924 | 122.0233 | 122.0127 | 122.0856 | 120.7867 | -122.0731 | 121.932 | 122.0306 | 122.0613 | 78.3272 | -122.3316
2035.2656 | 122.1909 | -121.9574 | 0.073242 | 1.4211e-13 | -0.056655 | -0.0096432 | 0.062588 | -0.0098456 | 0.052822 | -0.0054937 | 0.00035675 | -0.0036108 | -0.0049352 | 0.035089 | -0.014941 | -121.5002 | -1.1845 | -121.8044 | 0.047549 | 0.046148 | 0.10992 | -121.9952 | -121.1104 | -44.2941 | -121.3281 | -0.029954 | 0.064071 | 0.094744 | -122.2583 | -0.037842 | -0.025693 | 0.45719 | 0.15299 | 0.19083 | -0.027094 | 0.036674 | -0.30091 | -0.1032 | 0.84699 | 0.62934 | 0.93025 | -0.009171 | 0.021502 | 122.0049 | 122.0035 | 122.0673 | 120.7729 | -122.0685 | 121.9274 | 122.0215 | 122.0521 | 77.6633 | -122.3316
2037.0469 | 122.2778 | -121.9299 | 0.086975 | 1.4211e-13 | -0.056655 | -0.0096432 | 0.062801 | -0.0098456 | 0.052608 | -0.013124 | -7.0448e-05 | -0.0033972 | -0.0049352 | 0.035303 | -0.014941 | -121.5002 | -1.1982 | -121.7861 | 0.052128 | 0.046148 | 0.11907 | -121.9952 | -121.0967 | -44.6146 | -121.3326 | -0.034533 | 0.064071 | 0.090166 | -122.2629 | -0.065307 | -0.034847 | 0.42972 | 0.14384 | 0.20915 | -0.040827 | 0.032098 | -0.33296 | -0.12151 | 0.83326 | 0.59729 | 0.93025 | -0.022904 | 0.003191 | 121.9821 | 121.9761 | 122.049 | 120.7317 | -122.0822 | 121.8954 | 121.994 | 122.0201 | 77.3153 | -122.3499
2038.7344 | 122.1405 | -121.9803 | 0.09613 | 1.4211e-13 | -0.056869 | -0.0096432 | 0.062588 | -0.010273 | 0.052822 | -0.020755 | 0.00014315 | -0.0029698 | -0.0053626 | 0.035089 | -0.014941 | -121.5002 | -1.2073 | -121.7998 | 0.052128 | 0.055306 | 0.11449 | -121.9907 | -121.1058 | -44.9946 | -121.3143 | -0.029954 | 0.064071 | 0.090166 | -122.2629 | -0.010374 | -0.044002 | 0.48008 | 0.18046 | 0.19083 | -0.040824 | 0.018364 | -0.2826 | -0.12608 | 0.87446 | 0.66596 | 0.94856 | -0.032059 | -0.005964 | 122.0324 | 122.0356 | 122.0948 | 120.7729 | -122.0868 | 121.9503 | 122.0444 | 122.0705 | 76.9857 | -122.359
2040.4844 | 122.2458 | -121.9437 | 0.082397 | 1.4211e-13 | -0.056869 | -0.009857 | 0.062374 | -0.0098456 | 0.052608 | -0.0054937 | -0.00028425 | -0.0031834 | -0.0051488 | 0.035303 | -0.014941 | -121.5048 | -1.2119 | -121.809 | 0.052128 | 0.041569 | 0.11907 | -122.0044 | -121.0875 | -45.4433 | -121.3143 | -0.025376 | 0.064071 | 0.094744 | -122.2675 | -0.060732 | -0.030269 | 0.43888 | 0.13468 | 0.19541 | -0.040828 | 0.036676 | -0.3238 | -0.10777 | 0.85615 | 0.62934 | 0.95314 | -0.018326 | 0.012347 | 121.9958 | 121.9852 | 122.0627 | 120.7317 | -122.0868 | 121.9183 | 122.0077 | 122.0384 | 76.5003 | -122.3499
2042.2344 | 122.1085 | -121.9849 | 0.10986 | 1.4211e-13 | -0.057083 | -0.009857 | 0.063015 | -0.0098456 | 0.052394 | -0.020755 | -7.0448e-05 | -0.0033972 | -0.0051488 | 0.035303 | -0.014727 | -121.5002 | -1.2302 | -121.7952 | 0.056706 | 0.055306 | 0.11907 | -121.9952 | -121.0784 | -45.8737 | -121.3006 | -0.034533 | 0.064071 | 0.099323 | -122.2675 | -0.010376 | -0.053157 | 0.48465 | 0.18961 | 0.19999 | -0.054557 | 0.00921 | -0.2826 | -0.1444 | 0.90651 | 0.68427 | 0.96688 | -0.045792 | -0.01054 | 122.0416 | 122.0402 | 122.1039 | 120.7546 | -122.1051 | 121.9503 | 122.0489 | 122.0842 | 76.1111 | -122.3773
2044 | 122.1176 | -121.994 | 0.10529 | 1.4211e-13 | -0.056869 | -0.009857 | 0.062588 | -0.010059 | 0.052822 | 0.0021363 | -7.0448e-05 | -0.0033972 | -0.0049352 | 0.035517 | -0.014727 | -121.5048 | -1.2348 | -121.8044 | 0.047549 | 0.050727 | 0.11449 | -121.9998 | -121.06 | -46.2858 | -121.2914 | -0.025376 | 0.064071 | 0.090166 | -122.2583 | -0.005799 | -0.057737 | 0.48923 | 0.18961 | 0.19541 | -0.054559 | 0.009208 | -0.26429 | -0.13066 | 0.93398 | 0.70259 | 0.96688 | -0.041215 | -0.01512 | 122.0416 | 122.0447 | 122.1085 | 120.7592 | -122.1051 | 121.9686 | 122.0581 | 122.0842 | 75.7082 | -122.3636
2045.75 | 122.1176 | -121.9986 | 0.11902 | 1.4211e-13 | -0.057083 | -0.009857 | 0.062374 | -0.0098456 | 0.052394 | 0.0097668 | -0.00049785 | -0.0036108 | -0.0051488 | 0.035303 | -0.014727 | -121.5048 | -1.244 | -121.809 | 0.047549 | 0.046148 | 0.11907 | -121.9952 | -121.0509 | -46.7666 | -121.2869 | -0.029954 | 0.064071 | 0.099323 | -122.2675 | 0.003357 | -0.07147 | 0.49381 | 0.18961 | 0.18625 | -0.072871 | 5.4e-05 | -0.26887 | -0.14897 | 0.94771 | 0.71174 | 0.98062 | -0.054948 | -0.019696 | 122.0461 | 122.0447 | 122.1177 | 120.7546 | -122.1143 | 121.9686 | 122.0627 | 122.0979 | 75.232 | -122.3865
2047.4531 | 122.1817 | -121.9757 | 0.10986 | 1.4211e-13 | -0.056869 | -0.009857 | 0.063015 | -0.010273 | 0.052608 | -0.013124 | -0.00028425 | -0.0033972 | -0.0051488 | 0.035517 | -0.015154 | -121.5002 | -1.2486 | -121.8044 | 0.052128 | 0.046148 | 0.11449 | -121.9998 | -121.0463 | -47.1741 | -121.2777 | -0.034533 | 0.064071 | 0.094744 | -122.2675 | -0.02411 | -0.057735 | 0.4755 | 0.1713 | 0.19541 | -0.063715 | 0.004631 | -0.29176 | -0.1444 | 0.9294 | 0.69801 | 0.98977 | -0.045792 | -0.015119 | 122.0278 | 122.0219 | 122.0902 | 120.7272 | -122.1097 | 121.9412 | 122.0398 | 122.0705 | 74.8016 | -122.3773
2049.2031 | 122.1268 | -121.9986 | 0.10986 | 1.4211e-13 | -0.057296 | -0.010071 | 0.062374 | -0.010273 | 0.052608 | -0.0054937 | -0.00028425 | -0.0036108 | -0.0051488 | 0.035303 | -0.014727 | -121.5139 | -1.2623 | -121.809 | 0.052128 | 0.055306 | 0.11449 | -122.0044 | -121.028 | -47.6045 | -121.2731 | -0.034533 | 0.064071 | 0.099323 | -122.2766 | -0.005801 | -0.057735 | 0.48465 | 0.18961 | 0.19541 | -0.054557 | 0.004631 | -0.27803 | -0.1444 | 0.97061 | 0.72548 | 1.0035 | -0.045792 | -0.01054 | 122.0507 | 122.0539 | 122.1131 | 120.7363 | -122.1143 | 121.9641 | 122.0627 | 122.0979 | 74.3941 | -122.3865
2050.9062 | 122.2275 | -121.9666 | 0.09613 | 1.4211e-13 | -0.056869 | -0.009857 | 0.062374 | -0.010059 | 0.052608 | -0.013124 | 0.00014315 | -0.0033972 | -0.0051488 | 0.035517 | -0.015154 | -121.5139 | -1.2669 | -121.8044 | 0.047549 | 0.055306 | 0.11907 | -122.0044 | -121.028 | -48.044 | -121.264 | -0.034533 | 0.06865 | 0.099323 | -122.2629 | -0.037844 | -0.048581 | 0.45261 | 0.16215 | 0.19999 | -0.040824 | 0.022943 | -0.29633 | -0.13066 | 0.93856 | 0.7026 | 0.99893 | -0.02748 | 0.003193 | 122.0141 | 122.0219 | 122.0856 | 120.6997 | -122.1005 | 121.932 | 122.0352 | 122.0659 | 73.9225 | -122.359
2052.6562 | 122.2961 | -121.9528 | 0.091553 | 1.4211e-13 | -0.057083 | -0.010071 | 0.062374 | -0.010273 | 0.052394 | -0.0054937 | -0.00028425 | -0.0031834 | -0.0049352 | 0.035303 | -0.015154 | -121.5094 | -1.2852 | -121.8136 | 0.052128 | 0.050727 | 0.11907 | -122.0044 | -121.0188 | -48.4607 | -121.2594 | -0.034533 | 0.073228 | 0.090166 | -122.2766 | -0.051577 | -0.039425 | 0.44345 | 0.13926 | 0.19083 | -0.040826 | 0.02752 | -0.3238 | -0.12609 | 0.93399 | 0.69344 | 1.0172 | -0.018325 | -0.001387 | 122.0049 | 122.0035 | 122.0719 | 120.6676 | -122.096 | 121.9183 | 122.026 | 122.043 | 73.4921 | -122.3682
2054.4062 | 122.1268 | -122.0032 | 0.10529 | 1.4211e-13 | -0.057296 | -0.010071 | 0.062588 | -0.010059 | 0.052608 | -0.020755 | -7.0448e-05 | -0.0033972 | -0.0049352 | 0.03573 | -0.014941 | -121.5139 | -1.2943 | -121.8136 | 0.047549 | 0.059885 | 0.12365 | -122.0044 | -121.0051 | -48.827 | -121.2548 | -0.034533 | 0.059493 | 0.094744 | -122.2766 | -0.001223 | -0.057737 | 0.48923 | 0.18961 | 0.19083 | -0.045401 | 0.018366 | -0.27345 | -0.13982 | 0.99808 | 0.74837 | 1.0218 | -0.045793 | -0.010542 | 122.0507 | 122.0631 | 122.1268 | 120.7088 | -122.1097 | 121.9686 | 122.0627 | 122.0979 | 73.1762 | -122.3819
2056.1719 | 122.1817 | -121.9894 | 0.11444 | 1.4211e-13 | -0.057083 | -0.0096432 | 0.062588 | -0.0098456 | 0.052181 | -0.0054937 | -0.00028425 | -0.0029698 | -0.0051488 | 0.035517 | -0.014513 | -121.5094 | -1.3081 | -121.8044 | 0.052128 | 0.055306 | 0.11907 | -122.0044 | -120.9959 | -49.3536 | -121.2456 | -0.025376 | 0.059493 | 0.094744 | -122.2629 | -0.014956 | -0.062313 | 0.48007 | 0.18503 | 0.19999 | -0.059135 | 0.004632 | -0.27345 | -0.13982 | 0.9935 | 0.7438 | 1.0172 | -0.054948 | -0.019697 | 122.0416 | 122.0447 | 122.1085 | 120.6814 | -122.1188 | 121.9641 | 122.0489 | 122.0842 | 72.6359 | -122.3773
2057.8594 | 122.2549 | -121.9574 | 0.07782 | 1.4211e-13 | -0.056869 | -0.010071 | 0.062374 | -0.010059 | 0.052608 | -0.013124 | -7.0448e-05 | -0.0031834 | -0.0051488 | 0.035517 | -0.014941 | -121.5048 | -1.3081 | -121.809 | 0.047549 | 0.050727 | 0.12365 | -122.0044 | -120.9776 | -49.8023 | -121.2365 | -0.025376 | 0.06865 | 0.094744 | -122.272 | -0.047 | -0.030271 | 0.45261 | 0.14841 | 0.19541 | -0.027093 | 0.045832 | -0.31465 | -0.1032 | 0.97977 | 0.72091 | 1.0356 | -0.00917 | 0.016924 | 122.0049 | 122.0081 | 122.081 | 120.6493 | -122.0822 | 121.932 | 122.026 | 122.0521 | 72.1551 | -122.3499
2059.625 | 122.1817 | -121.9757 | 0.10529 | 1.4211e-13 | -0.057083 | -0.009857 | 0.062588 | -0.009632 | 0.052608 | 0.0021363 | -7.0448e-05 | -0.0033972 | -0.0049352 | 0.035517 | -0.014941 | -121.5139 | -1.3172 | -121.8136 | 0.047549 | 0.055306 | 0.11907 | -122.009 | -120.973 | -50.2235 | -121.2273 | -0.039111 | 0.06865 | 0.11306 | -122.2675 | -0.033268 | -0.057737 | 0.46176 | 0.16214 | 0.19541 | -0.04998 | 0.013787 | -0.29176 | -0.1444 | 1.0027 | 0.74838 | 1.0401 | -0.036636 | 0.007773 | 122.0233 | 122.031 | 122.0948 | 120.6585 | -122.1143 | 121.9366 | 122.0444 | 122.0888 | 71.7522 | -122.3728
2061.3125 | 122.2549 | -121.9482 | 0.068665 | 1.4211e-13 | -0.057083 | -0.010284 | 0.062374 | -0.0098456 | 0.052608 | -0.013124 | -7.0448e-05 | -0.0033972 | -0.0055762 | 0.035517 | -0.014513 | -121.5185 | -1.3355 | -121.8181 | 0.052128 | 0.055306 | 0.11907 | -122.009 | -120.9456 | -50.6631 | -121.2136 | -0.034533 | 0.064071 | 0.090166 | -122.272 | -0.060734 | -0.016537 | 0.42972 | 0.1301 | 0.19084 | -0.013359 | 0.050408 | -0.3238 | -0.1032 | 1.0027 | 0.73465 | 1.0585 | -0.004594 | 0.021501 | 122.0004 | 122.0035 | 122.0673 | 120.6127 | -122.0776 | 121.9137 | 122.0123 | 122.0384 | 71.2852 | -122.3407
2063.0625 | 122.1497 | -121.9986 | 0.11444 | 1.4211e-13 | -0.057083 | -0.009857 | 0.06216 | -0.010059 | 0.052608 | 0.0021363 | -0.00028425 | -0.0033972 | -0.0051488 | 0.035517 | -0.014727 | -121.5185 | -1.3447 | -121.8181 | 0.042971 | 0.055306 | 0.11907 | -122.0136 | -120.9364 | -51.1026 | -121.209 | -0.034533 | 0.059493 | 0.094744 | -122.2766 | -0.014959 | -0.07147 | 0.48007 | 0.18046 | 0.19541 | -0.059135 | 0.004632 | -0.27803 | -0.14897 | 1.0622 | 0.78958 | 1.0676 | -0.054948 | -0.019697 | 122.0416 | 122.0539 | 122.1177 | 120.6539 | -122.128 | 121.9641 | 122.0581 | 122.0933 | 70.896 | -122.3911
2064.75 | 122.1863 | -121.962 | 0.11444 | 1.4211e-13 | -0.056869 | -0.010284 | 0.062374 | -0.0098456 | 0.052394 | -0.0054937 | 0.00014315 | -0.0036108 | -0.0053626 | 0.03573 | -0.014727 | -121.5185 | -1.3493 | -121.8136 | 0.056706 | 0.050727 | 0.11907 | -122.0136 | -120.9135 | -51.5697 | -121.1999 | -0.020797 | 0.06865 | 0.099323 | -122.2766 | -0.05158 | -0.057735 | 0.44345 | 0.14841 | 0.19999 | -0.063714 | 0.004632 | -0.31465 | -0.13524 | 1.0485 | 0.76212 | 1.0768 | -0.045791 | -0.015118 | 122.0187 | 122.0127 | 122.081 | 120.6127 | -122.128 | 121.9412 | 122.0306 | 122.0613 | 70.3923 | -122.3911
2066.5156 | 122.2504 | -121.962 | 0.091553 | 1.4211e-13 | -0.057296 | -0.009857 | 0.062374 | -0.010273 | 0.052822 | -0.013124 | -7.0448e-05 | -0.0036108 | -0.0051488 | 0.035517 | -0.014727 | -121.5139 | -1.3584 | -121.8136 | 0.056706 | 0.059885 | 0.11907 | -122.0181 | -120.8998 | -52.0184 | -121.1953 | -0.029954 | 0.06865 | 0.094744 | -122.2812 | -0.056159 | -0.034847 | 0.44803 | 0.14841 | 0.20457 | -0.031668 | 0.02752 | -0.31923 | -0.12151 | 1.0622 | 0.7667 | 1.0859 | -0.022903 | 0.003191 | 122.0187 | 122.0219 | 122.081 | 120.6035 | -122.1097 | 121.932 | 122.0306 | 122.0567 | 69.9436 | -122.3728
2068.2656 | 122.1725 | -121.9711 | 0.10071 | 1.4211e-13 | -0.057296 | -0.010284 | 0.062374 | -0.010273 | 0.052608 | -0.0054937 | 0.00014315 | -0.0031834 | -0.0049352 | 0.035517 | -0.014941 | -121.5231 | -1.3676 | -121.8136 | 0.047549 | 0.050727 | 0.11449 | -122.0181 | -120.9044 | -52.7235 | -121.1815 | -0.020797 | 0.06865 | 0.094744 | -122.2812 | -0.047004 | -0.053159 | 0.44803 | 0.15757 | 0.20457 | -0.049981 | 0.013786 | -0.31007 | -0.12151 | 1.0668 | 0.78959 | 1.0997 | -0.032058 | -0.005964 | 122.0187 | 122.0219 | 122.0856 | 120.6035 | -122.1188 | 121.9503 | 122.0398 | 122.0659 | 69.2476 | -122.3819
2070.0156 | 122.1222 | -122.0123 | 0.10986 | 1.4211e-13 | -0.057083 | -0.010071 | 0.06216 | -0.010273 | 0.052608 | -0.013124 | -0.00028425 | -0.0031834 | -0.0047216 | 0.03573 | -0.014727 | -121.5231 | -1.3905 | -121.8227 | 0.047549 | 0.055306 | 0.11449 | -122.0227 | -120.8998 | -53.1447 | -121.177 | -0.025376 | 0.073228 | 0.099323 | -122.2812 | -0.010383 | -0.062314 | 0.48923 | 0.18961 | 0.19999 | -0.054557 | 0.004631 | -0.26887 | -0.13524 | 1.1125 | 0.83537 | 1.1042 | -0.036635 | -0.01054 | 122.0599 | 122.0676 | 122.1268 | 120.6218 | -122.1326 | 121.987 | 122.0856 | 122.1117 | 68.8676 | -122.3911
2071.7031 | 122.2504 | -121.9803 | 0.073242 | 1.4211e-13 | -0.057296 | -0.009857 | 0.06216 | -0.010273 | 0.052608 | -0.0054937 | -7.0448e-05 | -0.0033972 | -0.0051488 | 0.03573 | -0.014727 | -121.5231 | -1.3951 | -121.8227 | 0.056706 | 0.050727 | 0.12365 | -122.0136 | -120.8815 | -53.7262 | -121.1632 | -0.029954 | 0.064071 | 0.1039 | -122.2766 | -0.033269 | -0.016536 | 0.45719 | 0.15757 | 0.19083 | -0.022515 | 0.05041 | -0.29634 | -0.1032 | 1.0988 | 0.81706 | 1.1134 | -0.009171 | 0.030659 | 122.037 | 122.031 | 122.1039 | 120.5852 | -122.0868 | 121.9503 | 122.0444 | 122.0842 | 68.2541 | -122.3499
2073.4688 | 122.2275 | -121.9666 | 0.091553 | 1.4211e-13 | -0.05751 | -0.010071 | 0.062374 | -0.010273 | 0.052608 | -0.0054937 | -0.00028425 | -0.0029698 | -0.0053626 | 0.03573 | -0.014727 | -121.5185 | -1.4042 | -121.8365 | 0.047549 | 0.055306 | 0.11907 | -122.0227 | -120.8677 | -54.1749 | -121.1495 | -0.034533 | 0.06865 | 0.094744 | -122.2766 | -0.056159 | -0.044004 | 0.44803 | 0.1301 | 0.18626 | -0.036247 | 0.02752 | -0.31007 | -0.12609 | 1.0988 | 0.81706 | 1.1271 | -0.022903 | 0.003191 | 122.0141 | 122.0219 | 122.0856 | 120.5623 | -122.1143 | 121.932 | 122.0352 | 122.0613 | 67.7916 | -122.3682
2075.2031 | 122.2366 | -121.9711 | 0.091553 | 1.4211e-13 | -0.057296 | -0.009857 | 0.062588 | -0.010273 | 0.052608 | -0.013124 | -7.0448e-05 | -0.0033972 | -0.0051488 | 0.03573 | -0.014941 | -121.5185 | -1.4134 | -121.8319 | 0.047549 | 0.055306 | 0.11449 | -122.0227 | -120.8586 | -54.5 | -121.1495 | -0.029954 | 0.073228 | 0.094744 | -122.2858 | -0.051582 | -0.044004 | 0.45261 | 0.13925 | 0.19084 | -0.036247 | 0.022941 | -0.31465 | -0.12151 | 1.1126 | 0.82164 | 1.1363 | -0.018325 | 0.003191 | 122.0187 | 122.0264 | 122.0856 | 120.5577 | -122.1143 | 121.9412 | 122.0444 | 122.0659 | 67.4711 | -122.3773
2076.9062 | 122.2321 | -121.9666 | 0.082397 | 1.4211e-13 | -0.057296 | -0.009857 | 0.062588 | -0.0098456 | 0.052608 | -0.0054937 | -0.00028425 | -0.0031834 | -0.0049352 | 0.035944 | -0.014727 | -121.5277 | -1.4317 | -121.8227 | 0.047549 | 0.050727 | 0.12365 | -122.0227 | -120.8448 | -54.8801 | -121.1312 | -0.034533 | 0.06865 | 0.099323 | -122.2904 | -0.056159 | -0.034848 | 0.43887 | 0.14383 | 0.19999 | -0.03167 | 0.041255 | -0.32381 | -0.11693 | 1.1217 | 0.83538 | 1.1592 | -0.013747 | 0.016926 | 122.0141 | 122.0173 | 122.0902 | 120.5349 | -122.1051 | 121.932 | 122.0352 | 122.0659 | 67.0865 | -122.3728
2078.6406 | 122.3007 | -121.962 | 0.07782 | 1.4211e-13 | -0.057724 | -0.009857 | 0.06216 | -0.010059 | 0.052394 | -0.020755 | -0.00028425 | -0.0031834 | -0.0051488 | 0.035944 | -0.014941 | -121.5323 | -1.4363 | -121.8227 | 0.052128 | 0.055306 | 0.12365 | -122.0273 | -120.8219 | -55.1868 | -121.1174 | -0.025376 | 0.064071 | 0.099323 | -122.2904 | -0.065316 | -0.025692 | 0.42972 | 0.13925 | 0.20457 | -0.022514 | 0.045832 | -0.32839 | -0.1032 | 1.14 | 0.84453 | 1.1729 | -0.013749 | 0.021503 | 122.0141 | 122.0173 | 122.0856 | 120.5257 | -122.1051 | 121.9366 | 122.026 | 122.0613 | 66.7751 | -122.3682
2080.3906 | 122.1954 | -122.0032 | 0.091553 | 1.4211e-13 | -0.057083 | -0.010071 | 0.062374 | -0.010059 | 0.052608 | -0.013124 | -7.0448e-05 | -0.0033972 | -0.0051488 | 0.03573 | -0.014941 | -121.5277 | -1.4409 | -121.8319 | 0.056706 | 0.055306 | 0.11449 | -122.0273 | -120.8174 | -55.631 | -121.1174 | -0.034533 | 0.06865 | 0.090166 | -122.2949 | -0.024117 | -0.034847 | 0.47549 | 0.1713 | 0.19542 | -0.036247 | 0.022941 | -0.29177 | -0.12609 | 1.1858 | 0.88573 | 1.1775 | -0.022903 | -0.001387 | 122.0599 | 122.0585 | 122.1177 | 120.5623 | -122.1188 | 121.9686 | 122.0718 | 122.0933 | 66.3722 | -122.3865
2082.1406 | 122.1451 | -122.0169 | 0.1236 | 1.4211e-13 | -0.057296 | -0.010284 | 0.061947 | -0.010273 | 0.052394 | -0.0054937 | 0.00014315 | -0.0029698 | -0.0051488 | 0.03573 | -0.014513 | -121.5323 | -1.4592 | -121.8273 | 0.047549 | 0.055306 | 0.11907 | -122.0181 | -120.8036 | -55.9057 | -121.0991 | -0.029954 | 0.073228 | 0.099323 | -122.2858 | -0.001227 | -0.076047 | 0.48465 | 0.18961 | 0.19084 | -0.06829 | -0.004523 | -0.26887 | -0.15355 | 1.2133 | 0.91778 | 1.1867 | -0.050368 | -0.024273 | 122.0645 | 122.0722 | 122.136 | 120.5577 | -122.1417 | 121.987 | 122.0901 | 122.1162 | 66.1112 | -122.4094
2083.8906 | 122.2366 | -121.9711 | 0.073242 | 1.4211e-13 | -0.057296 | -0.009857 | 0.061947 | -0.010487 | 0.052394 | -0.0054937 | -0.00028425 | -0.0033972 | -0.0049352 | 0.03573 | -0.014513 | -121.5277 | -1.4683 | -121.8273 | 0.056706 | 0.050727 | 0.12365 | -122.0273 | -120.7991 | -56.3819 | -121.0762 | -0.034533 | 0.064071 | 0.10848 | -122.2949 | -0.056161 | -0.016536 | 0.44345 | 0.14383 | 0.19999 | -0.022515 | 0.05041 | -0.32381 | -0.10778 | 1.1721 | 0.8949 | 1.2187 | -0.009171 | 0.035238 | 122.0278 | 122.0219 | 122.0948 | 120.5028 | -122.1005 | 121.9366 | 122.0352 | 122.0796 | 65.5893 | -122.3682
2085.5781 | 122.1268 | -122.0078 | 0.10986 | 1.4211e-13 | -0.057724 | -0.009857 | 0.062588 | -0.010059 | 0.052608 | -0.0054937 | 0.00014315 | -0.0031834 | -0.0053626 | 0.03573 | -0.014513 | -121.5323 | -1.4866 | -121.8319 | 0.056706 | 0.050727 | 0.11907 | -122.0181 | -120.7807 | -56.6978 | -121.0717 | -0.029954 | 0.059493 | 0.099323 | -122.2904 | -0.010383 | -0.053157 | 0.47549 | 0.17588 | 0.18626 | -0.059136 | 0.00921 | -0.28261 | -0.13982 | 1.227 | 0.9361 | 1.2187 | -0.05037 | -0.01054 | 122.0645 | 122.0585 | 122.1268 | 120.5211 | -122.128 | 121.9778 | 122.0672 | 122.1071 | 65.3099 | -122.4002
2087.3281 | 122.2092 | -122.0078 | 0.09613 | 1.4211e-13 | -0.05751 | -0.010071 | 0.062374 | -0.010273 | 0.052822 | -0.013124 | -7.0448e-05 | -0.0031834 | -0.0051488 | 0.035944 | -0.014727 | -121.5323 | -1.4958 | -121.8319 | 0.056706 | 0.050727 | 0.11907 | -122.0273 | -120.7533 | -57.0137 | -121.0671 | -0.025376 | 0.059493 | 0.094744 | -122.2904 | -0.01954 | -0.039424 | 0.47549 | 0.17588 | 0.19542 | -0.045403 | 0.022943 | -0.28261 | -0.12151 | 1.2545 | 0.94068 | 1.2233 | -0.036637 | -0.001386 | 122.0645 | 122.0585 | 122.1268 | 120.512 | -122.1234 | 121.9824 | 122.0672 | 122.1025 | 64.994 | -122.3865
2089.0938 | 122.2137 | -122.0032 | 0.10986 | 1.4211e-13 | -0.05751 | -0.010284 | 0.06216 | -0.010059 | 0.052608 | -0.0054937 | 0.00014315 | -0.0031834 | -0.0051488 | 0.035944 | -0.014727 | -121.5277 | -1.505 | -121.8365 | 0.052128 | 0.055306 | 0.11449 | -122.0227 | -120.735 | -57.3663 | -121.0533 | -0.029954 | 0.06865 | 0.094744 | -122.2904 | -0.019538 | -0.057735 | 0.47549 | 0.16672 | 0.18626 | -0.054557 | 0.004631 | -0.28719 | -0.13982 | 1.2682 | 0.94984 | 1.237 | -0.041213 | -0.015119 | 122.0553 | 122.0585 | 122.1177 | 120.4982 | -122.1326 | 121.9732 | 122.0718 | 122.0979 | 64.6369 | -122.4002
2090.7812 | 122.1497 | -122.0215 | 0.11902 | 1.4211e-13 | -0.057296 | -0.0096432 | 0.062588 | -0.010273 | 0.052608 | -0.020755 | -7.0448e-05 | -0.0033972 | -0.0047216 | 0.036158 | -0.014727 | -121.5323 | -1.5233 | -121.8319 | 0.047549 | 0.055306 | 0.11449 | -122.0319 | -120.7258 | -57.7326 | -121.0396 | -0.020797 | 0.059493 | 0.099323 | -122.2949 | -0.010386 | -0.07147 | 0.48923 | 0.18961 | 0.19999 | -0.063713 | -0.004525 | -0.27346 | -0.13982 | 1.2957 | 0.98188 | 1.2553 | -0.059526 | -0.019696 | 122.069 | 122.0768 | 122.136 | 120.4982 | -122.1509 | 122.0007 | 122.081 | 122.1208 | 64.2889 | -122.414
2092.5312 | 122.1588 | -122.0306 | 0.09613 | 1.4211e-13 | -0.057296 | -0.010284 | 0.062374 | -0.010059 | 0.052608 | -0.0054937 | -0.00049785 | -0.0033972 | -0.0049352 | 0.035944 | -0.0143 | -121.5323 | -1.5324 | -121.8365 | 0.052128 | 0.050727 | 0.11449 | -122.0319 | -120.7075 | -58.0211 | -121.0304 | -0.029954 | 0.064071 | 0.094744 | -122.2949 | -0.00123 | -0.044002 | 0.49838 | 0.19419 | 0.19541 | -0.045403 | 0.018364 | -0.2643 | -0.12608 | 1.3232 | 1.0002 | 1.2645 | -0.032059 | -0.001386 | 122.0828 | 122.0814 | 122.1451 | 120.4982 | -122.128 | 122.0007 | 122.0947 | 122.1254 | 64.0096 | -122.3911
2094.2812 | 122.2641 | -121.994 | 0.082397 | 1.4211e-13 | -0.05751 | -0.009857 | 0.062374 | -0.010273 | 0.052394 | -0.020755 | -0.00028425 | -0.0031834 | -0.0051488 | 0.036158 | -0.014513 | -121.5323 | -1.5416 | -121.841 | 0.056706 | 0.055306 | 0.11907 | -122.0364 | -120.6846 | -58.4423 | -121.0121 | -0.029954 | 0.064071 | 0.094744 | -122.2904 | -0.04243 | -0.025691 | 0.46176 | 0.15299 | 0.19542 | -0.027091 | 0.036676 | -0.29634 | -0.11235 | 1.3094 | 0.98189 | 1.2782 | -0.018326 | 0.012347 | 122.0507 | 122.0493 | 122.1131 | 120.4524 | -122.1188 | 121.9641 | 122.0581 | 122.0888 | 63.5517 | -122.3728
2096.0469 | 122.1359 | -122.0078 | 0.11902 | 1.4211e-13 | -0.05751 | -0.010071 | 0.06216 | -0.0098456 | 0.052608 | -0.013124 | -7.0448e-05 | -0.0031834 | -0.0049352 | 0.035944 | -0.0143 | -121.5323 | -1.5599 | -121.8502 | 0.052128 | 0.050727 | 0.11907 | -122.0319 | -120.6617 | -58.5522 | -120.9984 | -0.025376 | 0.059493 | 0.094744 | -122.2949 | -0.024119 | -0.066891 | 0.47549 | 0.15756 | 0.18168 | -0.068292 | 5.4e-05 | -0.28719 | -0.14439 | 1.3461 | 1.0094 | 1.2965 | -0.059526 | -0.024275 | 122.0599 | 122.0585 | 122.1268 | 120.4479 | -122.1509 | 121.9824 | 122.0672 | 122.1025 | 63.4556 | -122.414
2097.7969 | 122.1954 | -122.0032 | 0.09613 | 1.4211e-13 | -0.057724 | -0.010071 | 0.062374 | -0.010059 | 0.052822 | -0.020755 | -0.00028425 | -0.0031834 | -0.0053626 | 0.036158 | -0.014513 | -121.5368 | -1.5645 | -121.841 | 0.052128 | 0.046148 | 0.11907 | -122.0181 | -120.6617 | -58.8498 | -120.9847 | -0.020797 | 0.059493 | 0.094744 | -122.2995 | -0.01496 | -0.044002 | 0.46634 | 0.16214 | 0.1771 | -0.049982 | 0.022943 | -0.29635 | -0.11693 | 1.3415 | 1.0185 | 1.3149 | -0.036637 | -0.001386 | 122.0553 | 122.0493 | 122.1222 | 120.4387 | -122.1143 | 121.9824 | 122.0627 | 122.0979 | 63.1534 | -122.3956
2099.4844 | 122.2733 | -121.9849 | 0.068665 | 1.4211e-13 | -0.05751 | -0.010071 | 0.062374 | -0.010273 | 0.052822 | 0.0021363 | 0.00014315 | -0.0033972 | -0.0049352 | 0.036158 | -0.0143 | -121.5368 | -1.5828 | -121.841 | 0.047549 | 0.059885 | 0.11907 | -122.0319 | -120.6342 | -59.0558 | -120.9755 | -0.034533 | 0.06865 | 0.099323 | -122.2949 | -0.047007 | -0.021116 | 0.44803 | 0.14383 | 0.19084 | -0.00878 | 0.050408 | -0.31008 | -0.1032 | 1.3506 | 1.0094 | 1.3194 | -1.5e-05 | 0.030658 | 122.0324 | 122.0447 | 122.1039 | 120.4021 | -122.1005 | 121.9503 | 122.0535 | 122.0842 | 62.929 | -122.3636
2101.2344 | 122.2824 | -121.9894 | 0.07782 | 1.4211e-13 | -0.057724 | -0.010071 | 0.062588 | -0.010059 | 0.052394 | -0.0054937 | -7.0448e-05 | -0.0031834 | -0.0051488 | 0.036371 | -0.014513 | -121.5368 | -1.5874 | -121.841 | 0.047549 | 0.055306 | 0.11907 | -122.0273 | -120.6159 | -59.1199 | -120.9663 | -0.034533 | 0.059493 | 0.094744 | -122.2904 | -0.03785 | -0.030271 | 0.4526 | 0.14841 | 0.18626 | -0.022514 | 0.041253 | -0.30092 | -0.11235 | 1.3735 | 1.0231 | 1.324 | -0.018327 | 0.016924 | 122.037 | 122.0447 | 122.1085 | 120.4021 | -122.1051 | 121.9549 | 122.0489 | 122.0842 | 62.8695 | -122.3682
2102.9219 | 122.168 | -122.0306 | 0.10986 | 1.4211e-13 | -0.057937 | -0.010071 | 0.062588 | -0.010059 | 0.052394 | -0.013124 | -7.0448e-05 | -0.0031834 | -0.0049352 | 0.036158 | -0.014727 | -121.5414 | -1.6011 | -121.8365 | 0.047549 | 0.050727 | 0.12365 | -122.0364 | -120.5976 | -59.3351 | -120.9572 | -0.029954 | 0.054914 | 0.094744 | -122.2995 | -0.005809 | -0.062314 | 0.48923 | 0.19419 | 0.19999 | -0.059136 | 0.013789 | -0.26888 | -0.13982 | 1.433 | 1.0735 | 1.3423 | -0.054949 | -0.015119 | 122.0782 | 122.0814 | 122.1543 | 120.4295 | -122.1463 | 122.0007 | 122.0856 | 122.1254 | 62.6955 | -122.4094
2104.6719 | 122.2824 | -121.9803 | 0.09613 | 1.4211e-13 | -0.057937 | -0.010284 | 0.062374 | -0.010273 | 0.052608 | -0.0054937 | 0.00014315 | -0.0033972 | -0.0051488 | 0.036158 | -0.014513 | -121.5368 | -1.6194 | -121.8456 | 0.052128 | 0.050727 | 0.12823 | -122.0319 | -120.5701 | -59.3764 | -120.9389 | -0.029954 | 0.06865 | 0.1039 | -122.2995 | -0.051584 | -0.044002 | 0.44345 | 0.13468 | 0.18626 | -0.045403 | 0.0321 | -0.31923 | -0.12608 | 1.4102 | 1.0414 | 1.3606 | -0.02748 | 0.007771 | 122.0324 | 122.031 | 122.1085 | 120.3609 | -122.128 | 121.9503 | 122.0489 | 122.0842 | 62.6039 | -122.3956
2106.4375 | 122.319 | -121.9986 | 0.07782 | 1.4211e-13 | -0.057937 | -0.010284 | 0.06216 | -0.010059 | 0.052394 | 0.0021363 | 0.00014315 | -0.0033972 | -0.0051488 | 0.036799 | -0.014513 | -121.5277 | -1.6286 | -121.841 | 0.047549 | 0.050727 | 0.12365 | -122.0319 | -120.5426 | -59.4862 | -120.9297 | -0.025376 | 0.064071 | 0.099323 | -122.2995 | -0.033274 | -0.030271 | 0.47092 | 0.15756 | 0.19084 | -0.027093 | 0.045832 | -0.30092 | -0.1032 | 1.4559 | 1.0689 | 1.3698 | -0.013749 | 0.021503 | 122.0461 | 122.0493 | 122.1222 | 120.37 | -122.1097 | 121.9732 | 122.0627 | 122.0979 | 62.5124 | -122.3773
2108.1406 | 122.2778 | -121.9803 | 0.068665 | 1.4211e-13 | -0.057937 | -0.010284 | 0.06216 | -0.010059 | 0.052608 | -0.0054937 | -7.0448e-05 | -0.0036108 | -0.0051488 | 0.036371 | -0.014513 | -121.5414 | -1.6469 | -121.841 | 0.056706 | 0.050727 | 0.11449 | -122.0364 | -120.5198 | -59.6465 | -120.916 | -0.025376 | 0.06865 | 0.1039 | -122.2949 | -0.056163 | -0.011959 | 0.43887 | 0.13925 | 0.19542 | -0.017938 | 0.045829 | -0.31465 | -0.094041 | 1.4605 | 1.0643 | 1.379 | -1.5e-05 | 0.035236 | 122.037 | 122.031 | 122.0948 | 120.3334 | -122.1051 | 121.9549 | 122.0489 | 122.0842 | 62.3338 | -122.3636
2109.875 | 122.3053 | -121.9849 | 0.09613 | 1.4211e-13 | -0.057937 | -0.010071 | 0.06216 | -0.010487 | 0.052394 | -0.0054937 | -7.0448e-05 | -0.0029698 | -0.0053626 | 0.036799 | -0.0143 | -121.546 | -1.6606 | -121.8456 | 0.047549 | 0.050727 | 0.12365 | -122.041 | -120.4969 | -59.7106 | -120.9068 | -0.029954 | 0.059493 | 0.099323 | -122.2995 | -0.056165 | -0.048581 | 0.43887 | 0.13925 | 0.19542 | -0.045403 | 0.027522 | -0.31466 | -0.12608 | 1.488 | 1.078 | 1.3927 | -0.036637 | 0.003193 | 122.0324 | 122.0356 | 122.1085 | 120.3242 | -122.1372 | 121.9549 | 122.0444 | 122.0842 | 62.2743 | -122.3956
2111.6406 | 122.2458 | -122.0078 | 0.086975 | 1.4211e-13 | -0.057724 | -0.010284 | 0.062588 | -0.010487 | 0.052394 | -0.013124 | -7.0448e-05 | -0.0031834 | -0.0051488 | 0.036585 | -0.014086 | -121.5414 | -1.6744 | -121.8456 | 0.056706 | 0.055306 | 0.11907 | -122.0319 | -120.474 | -59.9945 | -120.9022 | -0.025376 | 0.06865 | 0.099323 | -122.3041 | -0.024119 | -0.030269 | 0.46634 | 0.16214 | 0.18626 | -0.031669 | 0.032098 | -0.29635 | -0.11235 | 1.5338 | 1.1055 | 1.4019 | -0.018325 | 0.012348 | 122.0645 | 122.0631 | 122.1268 | 120.3334 | -122.1188 | 121.9824 | 122.0764 | 122.1071 | 62.0133 | -122.3911
2113.4062 | 122.2137 | -121.994 | 0.10986 | 1.4211e-13 | -0.057937 | -0.010071 | 0.06216 | -0.010273 | 0.052608 | -0.0054937 | 0.00014315 | -0.0031834 | -0.0053626 | 0.036585 | -0.014086 | -121.5414 | -1.6835 | -121.8502 | 0.052128 | 0.059885 | 0.11907 | -122.0319 | -120.3641 | -60.5119 | -120.8977 | -0.025376 | 0.06865 | 0.099323 | -122.2995 | -0.037851 | -0.057735 | 0.4526 | 0.14383 | 0.18168 | -0.049978 | 0.00921 | -0.3055 | -0.13524 | 1.6299 | 1.0964 | 1.4019 | -0.041213 | -0.01054 | 122.0461 | 122.0539 | 122.1131 | 120.3105 | -122.1417 | 121.9686 | 122.0627 | 122.0933 | 61.4821 | -122.4094
2115.0938 | 122.1588 | -122.0306 | 0.1236 | 1.4211e-13 | -0.057724 | -0.010071 | 0.06216 | -0.010273 | 0.052608 | -0.013124 | 0.00014315 | -0.0029698 | -0.0053626 | 0.036371 | -0.013873 | -121.5368 | -1.7018 | -121.8548 | 0.056706 | 0.055306 | 0.11907 | -122.041 | -120.2679 | -61.13 | -120.8839 | -0.029954 | 0.064071 | 0.094744 | -122.3087 | -0.010388 | -0.06689 | 0.4938 | 0.17587 | 0.18626 | -0.06829 | -0.004523 | -0.27804 | -0.15355 | 1.7627 | 1.1467 | 1.4248 | -0.059525 | -0.028852 | 122.0873 | 122.0859 | 122.1497 | 120.3288 | -122.1646 | 122.0007 | 122.0947 | 122.1254 | 60.9006 | -122.4323
2116.8438 | 122.2641 | -121.9711 | 0.091553 | 1.4211e-13 | -0.057724 | -0.010071 | 0.062374 | -0.010273 | 0.052394 | -0.0054937 | 0.00014315 | -0.0031834 | -0.0053626 | 0.036371 | -0.013659 | -121.5414 | -1.7156 | -121.8548 | 0.052128 | 0.055306 | 0.12365 | -122.0364 | -120.2221 | -61.2628 | -120.8656 | -0.025376 | 0.059493 | 0.099323 | -122.3087 | -0.065319 | -0.039425 | 0.42972 | 0.11636 | 0.18168 | -0.036247 | 0.032099 | -0.33755 | -0.11693 | 1.749 | 1.1055 | 1.4431 | -0.03206 | 0.00777 | 122.0233 | 122.0264 | 122.0948 | 120.2556 | -122.128 | 121.9458 | 122.0306 | 122.0705 | 60.7084 | -122.4002
2118.5938 | 122.3236 | -122.0078 | 0.068665 | 1.4211e-13 | -0.058151 | -0.010071 | 0.062588 | -0.0098456 | 0.052394 | -0.013124 | 0.00014315 | -0.0031834 | -0.0051488 | 0.036799 | -0.013873 | -121.5414 | -1.7293 | -121.8548 | 0.052128 | 0.046148 | 0.12365 | -122.0364 | -120.1855 | -61.5604 | -120.8519 | -0.025376 | 0.064071 | 0.099323 | -122.3133 | -0.028698 | -0.016537 | 0.46634 | 0.15298 | 0.18168 | -0.022517 | 0.054987 | -0.3055 | -0.094041 | 1.8222 | 1.1559 | 1.4614 | -0.004594 | 0.030658 | 122.0599 | 122.0539 | 122.1314 | 120.2784 | -122.1051 | 121.9824 | 122.0718 | 122.1071 | 60.4474 | -122.3819
2120.2812 | 122.1817 | -122.0306 | 0.1236 | 1.4211e-13 | -0.058151 | -0.010498 | 0.062588 | -0.010487 | 0.052608 | -0.013124 | -7.0448e-05 | -0.0031834 | -0.0051488 | 0.036585 | -0.014086 | -121.5368 | -1.7339 | -121.841 | 0.047549 | 0.059885 | 0.12365 | -122.041 | -120.1351 | -61.6199 | -120.8473 | -0.034533 | 0.06865 | 0.099323 | -122.3041 | -0.010388 | -0.076047 | 0.4938 | 0.18961 | 0.2 | -0.063711 | 5.6e-05 | -0.27346 | -0.15813 | 1.8955 | 1.1833 | 1.4568 | -0.054946 | -0.024273 | 122.0782 | 122.0905 | 122.1543 | 120.2968 | -122.1646 | 121.9961 | 122.0993 | 122.13 | 60.4107 | -122.4277
2122.0469 | 122.2229 | -122.0123 | 0.10071 | 1.4211e-13 | -0.058365 | -0.010071 | 0.062374 | -0.010273 | 0.052394 | -0.0054937 | 0.00014315 | -0.0031834 | -0.0049352 | 0.036585 | -0.013873 | -121.5414 | -1.7522 | -121.8548 | 0.052128 | 0.055306 | 0.11907 | -122.041 | -120.0985 | -61.7252 | -120.8336 | -0.029954 | 0.059493 | 0.1039 | -122.3087 | -0.028699 | -0.04858 | 0.47091 | 0.15756 | 0.18626 | -0.045402 | 0.018365 | -0.29635 | -0.13066 | 1.9138 | 1.1788 | 1.4751 | -0.041215 | 0.003193 | 122.0645 | 122.0676 | 122.1314 | 120.2601 | -122.1417 | 121.9824 | 122.0718 | 122.1162 | 60.2871 | -122.4094
2123.7969 | 122.2916 | -121.9849 | 0.07782 | 1.4211e-13 | -0.057937 | -0.010071 | 0.062374 | -0.010059 | 0.052394 | -0.020755 | 0.00014315 | -0.0029698 | -0.0051488 | 0.036799 | -0.013873 | -121.5414 | -1.7659 | -121.8456 | 0.047549 | 0.050727 | 0.12823 | -122.0456 | -120.0527 | -61.8901 | -120.8198 | -0.034533 | 0.059493 | 0.1039 | -122.2949 | -0.060744 | -0.030271 | 0.44345 | 0.13925 | 0.2 | -0.027093 | 0.05041 | -0.31008 | -0.11235 | 1.9321 | 1.165 | 1.4751 | -0.018327 | 0.026081 | 122.0324 | 122.0356 | 122.1131 | 120.2189 | -122.1234 | 121.9503 | 122.0444 | 122.0888 | 60.0948 | -122.3728
2125.4844 | 122.1817 | -122.0078 | 0.11902 | 1.4211e-13 | -0.058151 | -0.010284 | 0.062374 | -0.010273 | 0.052394 | 0.0021363 | 0.00035675 | -0.0031834 | -0.0051488 | 0.036799 | -0.013873 | -121.546 | -1.7842 | -121.8548 | 0.052128 | 0.055306 | 0.11907 | -122.0502 | -120.039 | -62.8974 | -120.8107 | -0.025376 | 0.06865 | 0.094744 | -122.3087 | -0.042435 | -0.066891 | 0.46176 | 0.15298 | 0.19542 | -0.063713 | 5.4e-05 | -0.30093 | -0.14439 | 1.9688 | 1.1971 | 1.498 | -0.050369 | -0.024275 | 122.0599 | 122.0631 | 122.1268 | 120.2235 | -122.1692 | 121.9824 | 122.0764 | 122.1025 | 59.1104 | -122.4277
2127.2344 | 122.287 | -122.0169 | 0.07782 | 1.4211e-13 | -0.058151 | -0.010071 | 0.062801 | -0.010273 | 0.052608 | -0.020755 | 0.00014315 | -0.0031834 | -0.0051488 | 0.036799 | -0.013873 | -121.546 | -1.8026 | -121.8502 | 0.052128 | 0.059885 | 0.11907 | -122.0502 | -120.0161 | -63.4377 | -120.7878 | -0.025376 | 0.064071 | 0.099323 | -122.3178 | -0.033279 | -0.025692 | 0.47091 | 0.16672 | 0.2 | -0.017935 | 0.041253 | -0.30093 | -0.1032 | 2.0008 | 1.2291 | 1.5301 | -0.013749 | 0.021503 | 122.069 | 122.0768 | 122.136 | 120.2143 | -122.128 | 121.9915 | 122.081 | 122.1162 | 58.5792 | -122.3957
2129 | 122.1771 | -122.0352 | 0.10071 | 1.4211e-13 | -0.058365 | -0.010071 | 0.062374 | -0.010059 | 0.052394 | -0.013124 | 0.00014315 | -0.0029698 | -0.0047216 | 0.036585 | -0.013659 | -121.546 | -1.8071 | -121.8548 | 0.052128 | 0.055306 | 0.12365 | -122.0502 | -119.9703 | -63.662 | -120.7832 | -0.029954 | 0.064071 | 0.094744 | -122.3041 | -0.014969 | -0.04858 | 0.48922 | 0.18045 | 0.19542 | -0.045402 | 0.022944 | -0.26888 | -0.13066 | 2.0649 | 1.252 | 1.5209 | -0.036637 | -0.005964 | 122.0873 | 122.0905 | 122.1589 | 120.2281 | -122.1509 | 122.0053 | 122.0993 | 122.13 | 58.3732 | -122.4048
2130.6875 | 122.1771 | -122.0215 | 0.10529 | 1.4211e-13 | -0.057937 | -0.010071 | 0.062588 | -0.010059 | 0.052822 | -0.013124 | 0.00035675 | -0.0031834 | -0.0049352 | 0.036799 | -0.013659 | -121.5414 | -1.8209 | -121.8502 | 0.052128 | 0.055306 | 0.11907 | -122.0456 | -119.9428 | -63.8772 | -120.7695 | -0.025376 | 0.059493 | 0.099323 | -122.3133 | -0.024123 | -0.053158 | 0.48007 | 0.1713 | 0.19542 | -0.04998 | 0.013787 | -0.29177 | -0.13066 | 2.0786 | 1.252 | 1.5438 | -0.045793 | -0.005963 | 122.0736 | 122.0768 | 122.1406 | 120.2006 | -122.1509 | 121.9961 | 122.081 | 122.1208 | 58.1443 | -122.4185
2132.4531 | 122.287 | -121.9849 | 0.09613 | 1.4211e-13 | -0.058151 | -0.010071 | 0.062588 | -0.010487 | 0.052394 | -0.013124 | 0.00035675 | -0.0027562 | -0.0055762 | 0.036799 | -0.013659 | -121.5551 | -1.8392 | -121.8548 | 0.052128 | 0.055306 | 0.12365 | -122.0502 | -119.9154 | -64.0878 | -120.7466 | -0.025376 | 0.06865 | 0.099323 | -122.3087 | -0.065323 | -0.044002 | 0.42971 | 0.13009 | 0.19542 | -0.040824 | 0.027522 | -0.32381 | -0.12151 | 2.0695 | 1.2383 | 1.5621 | -0.02748 | 0.003193 | 122.037 | 122.0402 | 122.1085 | 120.1457 | -122.1463 | 121.9595 | 122.0535 | 122.0842 | 57.897 | -122.4048
2134.2031 | 122.1725 | -122.0352 | 0.11902 | 1.4211e-13 | -0.058365 | -0.010284 | 0.062374 | -0.010273 | 0.052394 | -0.0054937 | 0.00014315 | -0.0029698 | -0.0049352 | 0.036371 | -0.013873 | -121.5414 | -1.8529 | -121.8548 | 0.061284 | 0.055306 | 0.12365 | -122.0502 | -119.8879 | -64.1107 | -120.7328 | -0.029954 | 0.064071 | 0.099323 | -122.3178 | -0.014969 | -0.057735 | 0.4938 | 0.18045 | 0.19542 | -0.063713 | 0.004633 | -0.28262 | -0.14897 | 2.1473 | 1.3024 | 1.585 | -0.054948 | -0.019696 | 122.0965 | 122.0905 | 122.1589 | 120.1823 | -122.1692 | 122.0053 | 122.0993 | 122.1345 | 57.9245 | -122.4369
2135.875 | 122.2595 | -122.0078 | 0.086975 | 1.4211e-13 | -0.058365 | -0.010071 | 0.062374 | -0.010273 | 0.052394 | -0.0054937 | 0.00035675 | -0.0027562 | -0.0049352 | 0.037012 | -0.013873 | -121.546 | -1.8667 | -121.8593 | 0.056706 | 0.059885 | 0.12365 | -122.0502 | -119.8558 | -64.3351 | -120.7282 | -0.020797 | 0.059493 | 0.10848 | -122.3133 | -0.042435 | -0.030269 | 0.46176 | 0.1484 | 0.19084 | -0.02709 | 0.036677 | -0.3055 | -0.10777 | 2.1519 | 1.2795 | 1.585 | -0.027482 | 0.021505 | 122.0645 | 122.0676 | 122.1314 | 120.1411 | -122.1372 | 121.987 | 122.0672 | 122.1162 | 57.6727 | -122.4002
2137.6406 | 122.168 | -122.0581 | 0.1236 | 1.4211e-13 | -0.058365 | -0.010071 | 0.062588 | -0.0098456 | 0.052608 | -0.0054937 | 0.00057035 | -0.0029698 | -0.0051488 | 0.037012 | -0.013445 | -121.5414 | -1.885 | -121.8548 | 0.052128 | 0.050727 | 0.12365 | -122.0456 | -119.8284 | -64.303 | -120.7008 | -0.025376 | 0.073228 | 0.099323 | -122.3133 | 0.012498 | -0.071468 | 0.51669 | 0.20334 | 0.19084 | -0.072869 | 5.6e-05 | -0.25515 | -0.14897 | 2.2297 | 1.3573 | 1.6125 | -0.050368 | -0.024273 | 122.1102 | 122.1088 | 122.1818 | 120.1731 | -122.1692 | 122.0327 | 122.1313 | 122.1574 | 57.7551 | -122.4369
2139.3438 | 122.2961 | -121.9803 | 0.064087 | 1.4211e-13 | -0.058365 | -0.010071 | 0.062588 | -0.010273 | 0.052394 | -0.013124 | 0.00014315 | -0.0029698 | -0.0049352 | 0.037226 | -0.013659 | -121.5506 | -1.8941 | -121.8548 | 0.056706 | 0.059885 | 0.12823 | -122.041 | -119.7872 | -64.6236 | -120.6962 | -0.034533 | 0.06865 | 0.1039 | -122.3178 | -0.060742 | -0.007381 | 0.42971 | 0.12552 | 0.18626 | -0.004202 | 0.064143 | -0.33755 | -0.09862 | 2.1931 | 1.2841 | 1.6216 | 0.004563 | 0.039814 | 122.037 | 122.0402 | 122.1085 | 120.0862 | -122.1051 | 121.9458 | 122.0489 | 122.0842 | 57.3567 | -122.3819
2141.0938 | 122.287 | -122.0078 | 0.09613 | 1.4211e-13 | -0.058365 | -0.010071 | 0.062588 | -0.010273 | 0.052394 | 0.0021363 | 0.00014315 | -0.0027562 | -0.0051488 | 0.036799 | -0.013659 | -121.546 | -1.9124 | -121.8548 | 0.061284 | 0.055306 | 0.12365 | -122.0548 | -119.7368 | -64.7518 | -120.6733 | -0.034533 | 0.073228 | 0.099323 | -122.3133 | -0.047014 | -0.034846 | 0.46176 | 0.15298 | 0.2 | -0.040824 | 0.027522 | -0.3055 | -0.13066 | 2.271 | 1.3344 | 1.6399 | -0.022902 | 0.003193 | 122.069 | 122.0631 | 122.1314 | 120.0953 | -122.1509 | 121.9732 | 122.081 | 122.1071 | 57.256 | -122.4094
2142.8594 | 122.2824 | -121.9986 | 0.091553 | 1.4211e-13 | -0.058578 | -0.010498 | 0.062374 | -0.010487 | 0.052394 | 0.0021363 | 0.00035675 | -0.0029698 | -0.0047216 | 0.037226 | -0.013445 | -121.546 | -1.9353 | -121.8593 | 0.047549 | 0.055306 | 0.11907 | -122.0548 | -119.7139 | -64.6877 | -120.6596 | -0.034533 | 0.06865 | 0.099323 | -122.3224 | -0.056169 | -0.044004 | 0.4526 | 0.13925 | 0.19542 | -0.036247 | 0.02752 | -0.32382 | -0.12609 | 2.2847 | 1.339 | 1.6628 | -0.022903 | 0.00777 | 122.0461 | 122.0539 | 122.1177 | 120.0633 | -122.1463 | 121.9641 | 122.0672 | 122.0979 | 57.3109 | -122.414
2144.6094 | 122.2641 | -122.0078 | 0.07782 | 1.4211e-13 | -0.058578 | -0.010498 | 0.062374 | -0.010487 | 0.052181 | -0.013124 | 0.00035675 | -0.0031834 | -0.0053626 | 0.036799 | -0.013445 | -121.5551 | -1.9537 | -121.8548 | 0.052128 | 0.050727 | 0.11907 | -122.0548 | -119.6818 | -64.9029 | -120.6413 | -0.025376 | 0.064071 | 0.094744 | -122.3178 | -0.047014 | -0.025692 | 0.4526 | 0.15298 | 0.2 | -0.027093 | 0.041253 | -0.31008 | -0.1032 | 2.3259 | 1.3665 | 1.6766 | -0.013749 | 0.016924 | 122.0599 | 122.0585 | 122.1268 | 120.0541 | -122.1326 | 121.9824 | 122.0718 | 122.1025 | 57.1049 | -122.3957
2146.2969 | 122.1909 | -122.0444 | 0.11444 | 1.4211e-13 | -0.058578 | -0.010071 | 0.062588 | -0.010487 | 0.052394 | -0.013124 | 0.00035675 | -0.0027562 | -0.0049352 | 0.037226 | -0.013659 | -121.546 | -1.9674 | -121.8593 | 0.047549 | 0.055306 | 0.11907 | -122.0502 | -119.6406 | -64.9578 | -120.6184 | -0.025376 | 0.06865 | 0.1039 | -122.3224 | -0.005813 | -0.066892 | 0.49838 | 0.18503 | 0.19084 | -0.059135 | 0.004632 | -0.27804 | -0.13982 | 2.4037 | 1.426 | 1.7041 | -0.045791 | -0.01054 | 122.0919 | 122.0997 | 122.1634 | 120.077 | -122.1646 | 122.019 | 122.113 | 122.1483 | 57.0866 | -122.4369
2148.0625 | 122.2458 | -122.0032 | 0.07782 | 1.4211e-13 | -0.058365 | -0.010284 | 0.062374 | -0.010059 | 0.052394 | -0.013124 | 0.00035675 | -0.0029698 | -0.0053626 | 0.037012 | -0.013659 | -121.546 | -1.9857 | -121.8639 | 0.052128 | 0.064464 | 0.11907 | -122.0548 | -119.5994 | -66.0201 | -120.6 | -0.025376 | 0.077807 | 0.099323 | -122.3178 | -0.051591 | -0.025692 | 0.45718 | 0.13925 | 0.19084 | -0.013356 | 0.041253 | -0.31466 | -0.1032 | 2.4037 | 1.4031 | 1.7178 | -1.3e-05 | 0.021503 | 122.0553 | 122.0676 | 122.1222 | 120.0175 | -122.1326 | 121.9778 | 122.081 | 122.1025 | 55.9831 | -122.3957
2149.75 | 122.3099 | -121.9803 | 0.054932 | 1.4211e-13 | -0.058578 | -0.010284 | 0.062374 | -0.010487 | 0.052181 | 0.0021363 | 0.00014315 | -0.0029698 | -0.0055762 | 0.037012 | -0.013445 | -121.5506 | -1.9857 | -121.8639 | 0.052128 | 0.059885 | 0.12823 | -122.0502 | -119.5628 | -65.988 | -120.5909 | -0.029954 | 0.073228 | 0.099323 | -122.3224 | -0.0699 | -0.002804 | 0.42971 | 0.11636 | 0.18626 | 0.004953 | 0.073298 | -0.34213 | -0.084886 | 2.4175 | 1.3894 | 1.7315 | 0.018296 | 0.044391 | 122.0324 | 122.0402 | 122.1085 | 119.9946 | -122.1051 | 121.9503 | 122.0535 | 122.0796 | 55.9923 | -122.3773
2151.5 | 122.3007 | -122.0078 | 0.082397 | 1.4211e-13 | -0.058792 | -0.010071 | 0.062374 | -0.010487 | 0.052181 | -0.0054937 | 0.00057035 | -0.0027562 | -0.0051488 | 0.037012 | -0.013445 | -121.546 | -2.0086 | -121.8639 | 0.056706 | 0.064464 | 0.12365 | -122.0548 | -119.5124 | -66.0109 | -120.5726 | -0.020797 | 0.06865 | 0.1039 | -122.327 | -0.047014 | -0.025691 | 0.46176 | 0.14383 | 0.19084 | -0.017933 | 0.041255 | -0.31924 | -0.10319 | 2.4953 | 1.4352 | 1.7544 | -0.013747 | 0.021504 | 122.0645 | 122.0722 | 122.1314 | 119.9992 | -122.1372 | 121.987 | 122.0764 | 122.1117 | 55.9968 | -122.4094
2153.1875 | 122.1863 | -122.049 | 0.11444 | 1.4211e-13 | -0.058578 | -0.010284 | 0.062374 | -0.010487 | 0.052608 | -0.0054937 | 0.00035675 | -0.0029698 | -0.0051488 | 0.037226 | -0.013445 | -121.546 | -2.0178 | -121.8639 | 0.056706 | 0.055306 | 0.12823 | -122.0548 | -119.485 | -66.1437 | -120.5588 | -0.016219 | 0.06865 | 0.094744 | -122.3178 | -0.005815 | -0.057735 | 0.50296 | 0.18503 | 0.19084 | -0.059135 | 0.013789 | -0.26888 | -0.13066 | 2.564 | 1.4901 | 1.759 | -0.045791 | -0.019697 | 122.1057 | 122.1043 | 122.1772 | 120.0312 | -122.1692 | 122.0327 | 122.1176 | 122.1437 | 55.9053 | -122.4323
2154.9219 | 122.1771 | -122.0261 | 0.11444 | 1.4211e-13 | -0.058792 | -0.010284 | 0.062588 | -0.010487 | 0.052608 | -0.020755 | 0.00057035 | -0.0029698 | -0.0051488 | 0.036585 | -0.013445 | -121.5506 | -2.0361 | -121.8639 | 0.052128 | 0.064464 | 0.12365 | -122.0548 | -119.4438 | -66.2536 | -120.5359 | -0.025376 | 0.06865 | 0.1039 | -122.327 | -0.028703 | -0.062313 | 0.47549 | 0.16214 | 0.19084 | -0.049977 | 0.009211 | -0.30093 | -0.13982 | 2.5823 | 1.4901 | 1.791 | -0.045791 | -0.01054 | 122.0782 | 122.0905 | 122.1497 | 119.99 | -122.1692 | 122.0007 | 122.0947 | 122.13 | 55.7725 | -122.4414
2156.6719 | 122.2321 | -121.9849 | 0.13275 | 1.4211e-13 | -0.058365 | -0.009857 | 0.062588 | -0.010273 | 0.052608 | -0.0054937 | 0.00057035 | -0.0031834 | -0.0055762 | 0.037012 | -0.013659 | -121.5368 | -2.0498 | -121.8456 | 0.070441 | 0.073622 | 0.13281 | -122.1006 | -119.3842 | -66.1528 | -120.5131 | -0.016219 | 0.082386 | 0.1039 | -122.3087 | -0.11569 | -0.06231 | 0.44803 | 0.13925 | 0.25494 | -0.059129 | 5.8e-05 | -0.32381 | -0.14897 | 2.6006 | 1.4718 | 1.7956 | -0.050365 | -0.02885 | 122.0553 | 122.0585 | 122.1177 | 119.9351 | -122.2333 | 121.9686 | 122.0672 | 122.0888 | 55.832 | -122.4414
2158.4219 | 122.1863 | -121.994 | 0.16022 | 1.4211e-13 | -0.058792 | -0.010071 | 0.062374 | -0.010487 | 0.052181 | -0.0054937 | 0.00035675 | -0.0029698 | -0.0053626 | 0.037012 | -0.013445 | -121.5094 | -2.0635 | -121.8181 | 0.088755 | 0.091937 | 0.16028 | -122.0227 | -119.3156 | -66.075 | -120.4627 | 0.006674 | 0.10528 | 0.14053 | -122.2766 | -0.028693 | -0.071462 | 0.48465 | 0.17588 | 0.20457 | -0.06828 | 6.3e-05 | -0.28261 | -0.15354 | 2.6785 | 1.5313 | 1.8139 | -0.054938 | -0.019687 | 122.0828 | 122.086 | 122.1543 | 119.9305 | -122.1829 | 122.0007 | 122.0993 | 122.1345 | 55.919 | -122.4368
2160.1094 | 122.1634 | -121.9803 | 0.14191 | 1.4211e-13 | -0.058578 | -0.010071 | 0.062588 | -0.010487 | 0.052608 | -0.013124 | 0.00035675 | -0.0027562 | -0.0049352 | 0.037653 | -0.013659 | -121.4956 | -2.0773 | -121.8227 | 0.084176 | 0.096516 | 0.16028 | -122.0136 | -119.2698 | -66.0384 | -120.4352 | 0.015831 | 0.10986 | 0.13595 | -122.2766 | -0.033269 | -0.057731 | 0.48466 | 0.15757 | 0.19083 | -0.045391 | 0.018373 | -0.29634 | -0.12608 | 2.7105 | 1.5451 | 1.8414 | -0.03205 | -0.005955 | 122.0645 | 122.0768 | 122.1406 | 119.903 | -122.1555 | 121.9961 | 122.0901 | 122.1162 | 55.9419 | -122.4185
2161.8594 | 122.2641 | -121.962 | 0.1236 | 1.4211e-13 | -0.059006 | -0.010284 | 0.062588 | -0.010487 | 0.052394 | -0.013124 | 0.00035675 | -0.0029698 | -0.0049352 | 0.037653 | -0.013232 | -121.5094 | -2.0864 | -121.8181 | 0.088755 | 0.091937 | 0.16028 | -122.0227 | -119.2423 | -65.8232 | -120.4169 | -0.002483 | 0.096121 | 0.14053 | -122.2766 | -0.060737 | -0.034841 | 0.45261 | 0.14383 | 0.20457 | -0.031659 | 0.036684 | -0.31465 | -0.12608 | 2.7197 | 1.5451 | 1.8597 | -0.027475 | 0.016934 | 122.0507 | 122.0539 | 122.1223 | 119.8755 | -122.1463 | 121.9595 | 122.0581 | 122.1025 | 56.1388 | -122.4002
2163.5469 | 122.3236 | -121.9666 | 0.10986 | 1.4211e-13 | -0.059006 | -0.010284 | 0.062588 | -0.010273 | 0.052394 | -0.0054937 | 0.00014315 | -0.0027562 | -0.0049352 | 0.03744 | -0.013018 | -121.5094 | -2.1093 | -121.8227 | 0.088755 | 0.096516 | 0.16028 | -121.9998 | -119.1873 | -65.7682 | -120.4077 | 0.006674 | 0.1007 | 0.13595 | -122.2812 | -0.033265 | -0.021108 | 0.45719 | 0.14383 | 0.1771 | -0.013347 | 0.050417 | -0.31465 | -0.10319 | 2.7792 | 1.5588 | 1.8735 | -0.009163 | 0.026089 | 122.0553 | 122.0631 | 122.1268 | 119.8572 | -122.1097 | 121.9732 | 122.0673 | 122.1025 | 56.1983 | -122.3911
2165.2969 | 122.2137 | -121.9528 | 0.14648 | 1.4211e-13 | -0.058792 | -0.010284 | 0.062374 | -0.010059 | 0.052394 | -0.020755 | 0.00035675 | -0.0029698 | -0.0049352 | 0.037226 | -0.013232 | -121.5094 | -2.1276 | -121.8181 | 0.084176 | 0.087359 | 0.16486 | -122.0136 | -119.1461 | -65.7591 | -120.3894 | 0.006674 | 0.096121 | 0.13137 | -122.2766 | -0.060735 | -0.062308 | 0.44345 | 0.13468 | 0.19541 | -0.059125 | 0.018375 | -0.3238 | -0.13981 | 2.8067 | 1.5634 | 1.8872 | -0.050363 | -0.015111 | 122.037 | 122.0402 | 122.1177 | 119.8252 | -122.16 | 121.9595 | 122.0489 | 122.0842 | 56.1937 | -122.4231
2167.0469 | 122.2641 | -121.962 | 0.11444 | 1.4211e-13 | -0.058792 | -0.010284 | 0.062374 | -0.0107 | 0.052394 | -0.013124 | -7.0448e-05 | -0.0029698 | -0.0049352 | 0.03744 | -0.012804 | -121.5094 | -2.1414 | -121.8181 | 0.093333 | 0.091937 | 0.16028 | -122.0227 | -119.0866 | -65.7911 | -120.3711 | -0.002483 | 0.1007 | 0.13137 | -122.2766 | -0.060737 | -0.021108 | 0.45261 | 0.14383 | 0.20457 | -0.022504 | 0.045839 | -0.31465 | -0.11692 | 2.8754 | 1.5909 | 1.9055 | -0.013741 | 0.016932 | 122.0553 | 122.0539 | 122.1223 | 119.8206 | -122.1372 | 121.9595 | 122.0627 | 122.0933 | 56.1709 | -122.3911
2168.7344 | 122.2458 | -121.9666 | 0.12817 | 1.4211e-13 | -0.059006 | -0.010498 | 0.06216 | -0.010273 | 0.052394 | -0.013124 | 0.00078395 | -0.0029698 | -0.0051488 | 0.037226 | -0.013232 | -121.5048 | -2.1551 | -121.8227 | 0.084176 | 0.096516 | 0.16944 | -122.0181 | -119.05 | -65.5256 | -120.3391 | 0.011252 | 0.1007 | 0.12679 | -122.2812 | -0.051581 | -0.043998 | 0.46176 | 0.14383 | 0.19541 | -0.031658 | 0.041264 | -0.31465 | -0.11692 | 2.9166 | 1.6275 | 1.9421 | -0.027474 | -0.00138 | 122.0507 | 122.0631 | 122.136 | 119.8114 | -122.1463 | 121.9778 | 122.0673 | 122.0933 | 56.441 | -122.4094
2170.4844 | 122.2137 | -121.962 | 0.12817 | 1.4211e-13 | -0.058578 | -0.010712 | 0.062374 | -0.0107 | 0.052181 | -0.020755 | 0.00078395 | -0.0029698 | -0.0051488 | 0.037012 | -0.013232 | -121.4911 | -2.178 | -121.8181 | 0.088755 | 0.096516 | 0.1557 | -122.0136 | -119.0088 | -65.5439 | -120.3253 | 0.006674 | 0.091543 | 0.13137 | -122.272 | -0.05158 | -0.039419 | 0.47092 | 0.14383 | 0.19541 | -0.031658 | 0.027528 | -0.31007 | -0.1215 | 2.9532 | 1.6367 | 1.9467 | -0.036631 | 0.003199 | 122.0507 | 122.0585 | 122.1177 | 119.784 | -122.1417 | 121.9686 | 122.0535 | 122.0933 | 56.4181 | -122.4002
2172.1875 | 122.1542 | -121.9986 | 0.14191 | 1.4211e-13 | -0.058578 | -0.010284 | 0.062374 | -0.010059 | 0.052181 | -0.0054937 | 0.00057035 | -0.0027562 | -0.0049352 | 0.037653 | -0.013232 | -121.5048 | -2.178 | -121.8136 | 0.093333 | 0.091937 | 0.16028 | -122.009 | -118.963 | -65.4935 | -120.3116 | 0.011252 | 0.10528 | 0.13595 | -122.2766 | -0.01038 | -0.048574 | 0.49381 | 0.18503 | 0.19541 | -0.04997 | 0.018373 | -0.27803 | -0.13065 | 3.0356 | 1.687 | 1.965 | -0.036628 | -0.005955 | 122.0919 | 122.0905 | 122.1589 | 119.8206 | -122.1509 | 122.0098 | 122.1039 | 122.1345 | 56.5051 | -122.4185
2173.9375 | 122.1771 | -121.9986 | 0.16937 | 1.4211e-13 | -0.058792 | -0.009857 | 0.062374 | -0.010273 | 0.052394 | -0.013124 | 0.00057035 | -0.0027562 | -0.0051488 | 0.037867 | -0.013445 | -121.5002 | -2.2009 | -121.8136 | 0.088755 | 0.096516 | 0.16028 | -122.0136 | -118.9126 | -66.3085 | -120.2063 | 0.006674 | 0.096121 | 0.13137 | -122.272 | -0.014959 | -0.080618 | 0.49839 | 0.18503 | 0.19999 | -0.072857 | -0.009093 | -0.27345 | -0.1627 | 3.086 | 1.7923 | 2.0658 | -0.073252 | -0.038 | 122.0874 | 122.0951 | 122.1589 | 119.7977 | -122.1829 | 122.0053 | 122.0947 | 122.13 | 55.6901 | -122.4414
2175.6875 | 122.2275 | -121.9986 | 0.16022 | 1.4211e-13 | -0.058792 | -0.010712 | 0.062374 | -0.0107 | 0.052181 | -0.0054937 | 0.00057035 | -0.0029698 | -0.0049352 | 0.037867 | -0.013232 | -121.5002 | -2.2192 | -121.8136 | 0.093333 | 0.091937 | 0.1557 | -122.0181 | -118.8668 | -66.8534 | -120.1559 | 0.002095 | 0.10528 | 0.13595 | -122.2812 | -0.019538 | -0.066884 | 0.49839 | 0.18503 | 0.20457 | -0.06828 | -0.004515 | -0.28261 | -0.15812 | 3.1318 | 1.8427 | 2.1253 | -0.054938 | -0.024265 | 122.0919 | 122.0905 | 122.1543 | 119.7794 | -122.1784 | 122.0007 | 122.1039 | 122.1345 | 55.1452 | -122.4414
2177.4531 | 122.1771 | -121.9894 | 0.14648 | 1.4211e-13 | -0.059219 | -0.010284 | 0.062588 | -0.0107 | 0.052181 | -0.0054937 | 0.00057035 | -0.0025424 | -0.0049352 | 0.037867 | -0.013232 | -121.5002 | -2.233 | -121.8227 | 0.088755 | 0.096516 | 0.1557 | -122.0136 | -118.8211 | -66.9541 | -120.1193 | 0.006674 | 0.10986 | 0.13595 | -122.2812 | -0.024114 | -0.057729 | 0.48923 | 0.16672 | 0.19083 | -0.049968 | 0.009218 | -0.29176 | -0.13981 | 3.1684 | 1.8702 | 2.1619 | -0.036627 | -0.010532 | 122.0782 | 122.086 | 122.1451 | 119.7565 | -122.16 | 121.9961 | 122.0993 | 122.1254 | 55.0353 | -122.4277
2179.1875 | 122.2275 | -121.9482 | 0.15564 | 1.4211e-13 | -0.058792 | -0.010498 | 0.062374 | -0.0107 | 0.052394 | -0.013124 | 0.00057035 | -0.0029698 | -0.0047216 | 0.03744 | -0.012804 | -121.5048 | -2.2467 | -121.8227 | 0.088755 | 0.1011 | 0.16028 | -122.0227 | -118.7844 | -67.151 | -120.0598 | 0.011252 | 0.10528 | 0.13595 | -122.272 | -0.07447 | -0.066885 | 0.44345 | 0.12552 | 0.19999 | -0.054545 | 0.00464 | -0.3238 | -0.14439 | 3.1638 | 1.8885 | 2.2123 | -0.050361 | -0.019688 | 122.037 | 122.0493 | 122.1085 | 119.7016 | -122.1784 | 121.9595 | 122.0535 | 122.0842 | 54.7972 | -122.4277
2180.875 | 122.1542 | -121.9894 | 0.14191 | 1.4211e-13 | -0.058578 | -0.010498 | 0.061947 | -0.010487 | 0.052394 | 0.0021363 | 0.00035675 | -0.0027562 | -0.0047216 | 0.037653 | -0.012804 | -121.5002 | -2.265 | -121.8181 | 0.093333 | 0.091937 | 0.16486 | -122.0181 | -118.7249 | -67.1006 | -120.0277 | 0.015831 | 0.1007 | 0.14053 | -122.2766 | -0.028693 | -0.048574 | 0.48923 | 0.1713 | 0.19999 | -0.04997 | 0.022952 | -0.28718 | -0.12608 | 3.2645 | 1.9617 | 2.2489 | -0.041207 | -0.001377 | 122.0828 | 122.0814 | 122.1543 | 119.7244 | -122.16 | 122.0053 | 122.0901 | 122.13 | 54.8888 | -122.4185
2182.6406 | 122.2961 | -121.9299 | 0.12817 | 1.4211e-13 | -0.059006 | -0.010284 | 0.062588 | -0.0107 | 0.052394 | -0.013124 | 0.00057035 | -0.0027562 | -0.0051488 | 0.037867 | -0.012804 | -121.5002 | -2.2833 | -121.8136 | 0.084176 | 0.096516 | 0.16486 | -122.009 | -118.6608 | -67.5951 | -119.9819 | 0.006674 | 0.1007 | 0.14053 | -122.2766 | -0.079044 | -0.043998 | 0.42972 | 0.11637 | 0.19541 | -0.031658 | 0.036685 | -0.34669 | -0.1215 | 3.2691 | 1.948 | 2.2947 | -0.027474 | 0.012356 | 122.0141 | 122.0264 | 122.0948 | 119.6466 | -122.1372 | 121.9366 | 122.0306 | 122.0705 | 54.3348 | -122.4048
2184.3906 | 122.1771 | -122.0078 | 0.15564 | 1.4211e-13 | -0.059433 | -0.010284 | 0.06216 | -0.010487 | 0.052181 | -0.0054937 | 0.00057035 | -0.0027562 | -0.0047216 | 0.038081 | -0.013018 | -121.5002 | -2.2925 | -121.8227 | 0.093333 | 0.1011 | 0.16486 | -122.0181 | -118.6196 | -67.8515 | -119.9407 | 0.015831 | 0.10986 | 0.13595 | -122.2812 | -0.010383 | -0.062307 | 0.50754 | 0.18503 | 0.19541 | -0.054545 | 0.009219 | -0.27345 | -0.13981 | 3.3882 | 2.067 | 2.3405 | -0.045783 | -0.019688 | 122.1011 | 122.1088 | 122.1726 | 119.7153 | -122.1738 | 122.0236 | 122.1176 | 122.1437 | 54.1562 | -122.4368
2186.1406 | 122.1771 | -121.9849 | 0.16022 | 1.4211e-13 | -0.059006 | -0.010284 | 0.062588 | -0.0107 | 0.052394 | -0.0054937 | 0.00057035 | -0.0031834 | -0.0047216 | 0.038081 | -0.012804 | -121.4956 | -2.3154 | -121.8136 | 0.093333 | 0.091937 | 0.16486 | -122.0136 | -118.6013 | -68.4697 | -119.9087 | 0.011252 | 0.1007 | 0.14053 | -122.272 | -0.028692 | -0.066884 | 0.48923 | 0.1713 | 0.19999 | -0.06828 | 0.004642 | -0.28718 | -0.14896 | 3.3836 | 2.0762 | 2.3634 | -0.059517 | -0.019687 | 122.0782 | 122.0768 | 122.1497 | 119.6695 | -122.1738 | 121.9961 | 122.0856 | 122.1254 | 53.5152 | -122.4323
2187.8281 | 122.1588 | -121.9986 | 0.14648 | 1.4211e-13 | -0.059219 | -0.010498 | 0.062588 | -0.010487 | 0.052181 | -0.0054937 | 0.00078395 | -0.0029698 | -0.0049352 | 0.038081 | -0.012804 | -121.5048 | -2.3245 | -121.8181 | 0.088755 | 0.096516 | 0.16486 | -122.009 | -118.5372 | -68.6025 | -119.8491 | 0.011252 | 0.10986 | 0.13595 | -122.272 | -0.01038 | -0.057729 | 0.49381 | 0.18046 | 0.19084 | -0.049968 | 0.018375 | -0.27345 | -0.13523 | 3.4614 | 2.1495 | 2.4229 | -0.036627 | -0.010532 | 122.0874 | 122.0951 | 122.1635 | 119.6741 | -122.1555 | 122.0098 | 122.1085 | 122.1345 | 53.3961 | -122.4185
2189.5781 | 122.2504 | -121.962 | 0.12817 | 1.4211e-13 | -0.059433 | -0.010071 | 0.06216 | -0.0107 | 0.052608 | -0.013124 | 0.00078395 | -0.0027562 | -0.0049352 | 0.038294 | -0.012804 | -121.4956 | -2.3428 | -121.8181 | 0.097912 | 0.1011 | 0.16028 | -122.0136 | -118.4822 | -68.9687 | -119.8217 | 0.011252 | 0.10528 | 0.13595 | -122.272 | -0.05158 | -0.030262 | 0.46634 | 0.14383 | 0.19541 | -0.027079 | 0.032106 | -0.31007 | -0.11692 | 3.4797 | 2.1403 | 2.4504 | -0.022895 | 0.007778 | 122.0599 | 122.0631 | 122.1223 | 119.6191 | -122.1417 | 121.9732 | 122.0673 | 122.0979 | 52.9932 | -122.4002
2191.3281 | 122.2046 | -121.9711 | 0.17395 | 1.4211e-13 | -0.059219 | -0.010498 | 0.062374 | -0.010273 | 0.052394 | -0.013124 | 0.00078395 | -0.0025424 | -0.0049352 | 0.038294 | -0.012591 | -121.4911 | -2.3703 | -121.8136 | 0.097912 | 0.1011 | 0.16486 | -122.0044 | -118.409 | -69.3167 | -119.7713 | 0.006674 | 0.1007 | 0.14053 | -122.2766 | -0.033267 | -0.076038 | 0.48008 | 0.15757 | 0.19083 | -0.072855 | -0.009091 | -0.30549 | -0.16728 | 3.5622 | 2.1998 | 2.5053 | -0.07325 | -0.03342 | 122.069 | 122.0722 | 122.136 | 119.6008 | -122.1783 | 121.9778 | 122.0718 | 122.1117 | 52.6544 | -122.4506
2193.0938 | 122.287 | -121.9391 | 0.11902 | 1.4211e-13 | -0.059219 | -0.010284 | 0.062801 | -0.010487 | 0.052394 | -0.013124 | 0.00078395 | -0.0027562 | -0.0051488 | 0.037867 | -0.012377 | -121.5002 | -2.3749 | -121.8136 | 0.093333 | 0.1011 | 0.16486 | -122.0273 | -118.3449 | -69.6281 | -119.7255 | 0.011252 | 0.10528 | 0.13595 | -122.2766 | -0.088204 | -0.025686 | 0.43888 | 0.12552 | 0.21373 | -0.017924 | 0.04584 | -0.33754 | -0.10777 | 3.5942 | 2.2136 | 2.5511 | -0.01374 | 0.016933 | 122.0324 | 122.0402 | 122.1039 | 119.5642 | -122.1463 | 121.9503 | 122.0444 | 122.075 | 52.311 | -122.3956
2194.7812 | 122.2137 | -121.9666 | 0.14191 | 1.4211e-13 | -0.059006 | -0.010498 | 0.062374 | -0.010273 | 0.052608 | -0.0054937 | 0.00035675 | -0.0025424 | -0.004508 | 0.038508 | -0.012591 | -121.5002 | -2.4024 | -121.8136 | 0.093333 | 0.1011 | 0.16944 | -122.0136 | -118.2945 | -70.0264 | -119.6751 | 0.006674 | 0.1007 | 0.13595 | -122.272 | -0.047002 | -0.048574 | 0.46634 | 0.15299 | 0.19999 | -0.040812 | 0.027531 | -0.30549 | -0.13523 | 3.6721 | 2.2914 | 2.5969 | -0.041207 | -0.005955 | 122.0599 | 122.0676 | 122.136 | 119.5642 | -122.1555 | 121.9732 | 122.0673 | 122.1025 | 51.9401 | -122.414
2196.5469 | 122.2504 | -121.9711 | 0.12817 | 1.4211e-13 | -0.059219 | -0.010284 | 0.06216 | -0.010487 | 0.052181 | -0.013124 | 0.00078395 | -0.0029698 | -0.0051488 | 0.038508 | -0.012591 | -121.4956 | -2.4207 | -121.8181 | 0.097912 | 0.10567 | 0.16486 | -122.0227 | -118.2121 | -70.3744 | -119.6294 | 0.006674 | 0.10528 | 0.13595 | -122.2766 | -0.051582 | -0.030262 | 0.4755 | 0.15299 | 0.20457 | -0.0225 | 0.036685 | -0.30549 | -0.1215 | 3.759 | 2.3418 | 2.6473 | -0.022895 | 0.007778 | 122.069 | 122.0768 | 122.136 | 119.5505 | -122.1509 | 121.9778 | 122.0764 | 122.1071 | 51.5967 | -122.4048
2198.2969 | 122.3099 | -121.9482 | 0.12817 | 1.4211e-13 | -0.059219 | -0.010284 | 0.062374 | -0.010487 | 0.052181 | -0.013124 | 0.0012114 | -0.0023288 | -0.0047216 | 0.038508 | -0.012591 | -121.4911 | -2.4207 | -121.8136 | 0.088755 | 0.1011 | 0.16486 | -122.0181 | -118.1663 | -70.8185 | -119.5882 | 0.015831 | 0.1007 | 0.14053 | -122.2766 | -0.069892 | -0.039419 | 0.45719 | 0.13468 | 0.20457 | -0.027079 | 0.036685 | -0.32838 | -0.11234 | 3.7819 | 2.3601 | 2.6885 | -0.027474 | 0.012356 | 122.037 | 122.0493 | 122.1131 | 119.5276 | -122.1463 | 121.9641 | 122.0489 | 122.0888 | 51.1297 | -122.4048
2199.9844 | 122.1634 | -121.9894 | 0.15106 | 1.4211e-13 | -0.059433 | -0.010071 | 0.062374 | -0.0107 | 0.052608 | -0.028385 | 0.00078395 | -0.0023288 | -0.0049352 | 0.038508 | -0.012163 | -121.4956 | -2.4573 | -121.8181 | 0.084176 | 0.1011 | 0.16486 | -122.0136 | -118.0885 | -71.194 | -119.5424 | 0.011252 | 0.11444 | 0.14053 | -122.2766 | -0.024114 | -0.066886 | 0.49381 | 0.1713 | 0.19541 | -0.049967 | 0.013797 | -0.28718 | -0.13981 | 3.901 | 2.4471 | 2.7343 | -0.036626 | -0.010532 | 122.0736 | 122.0905 | 122.1543 | 119.5321 | -122.1646 | 122.0007 | 122.1039 | 122.13 | 50.7954 | -122.4277
2201.75 | 122.1954 | -121.9528 | 0.13733 | 1.4211e-13 | -0.059647 | -0.010284 | 0.06216 | -0.010487 | 0.052394 | -0.013124 | 0.00057035 | -0.0027562 | -0.0049352 | 0.038508 | -0.012163 | -121.4956 | -2.471 | -121.8136 | 0.097912 | 0.1011 | 0.16944 | -122.0227 | -118.0244 | -71.5832 | -119.4874 | 0.015831 | 0.11444 | 0.14053 | -122.2812 | -0.069892 | -0.039417 | 0.45719 | 0.13926 | 0.20915 | -0.036234 | 0.032109 | -0.32838 | -0.1215 | 3.9285 | 2.4654 | 2.7938 | -0.022893 | 0.003201 | 122.0507 | 122.0539 | 122.1223 | 119.4818 | -122.16 | 121.9687 | 122.0673 | 122.0934 | 50.3696 | -122.4185
2203.4531 | 122.2549 | -121.9757 | 0.12817 | 1.4211e-13 | -0.059433 | -0.010498 | 0.062374 | -0.010487 | 0.052394 | -0.0054937 | 0.00078395 | -0.0023288 | -0.004508 | 0.038722 | -0.012163 | -121.4956 | -2.4802 | -121.8227 | 0.093333 | 0.1011 | 0.16028 | -122.0273 | -117.9374 | -72.0044 | -119.4416 | 0.002095 | 0.1007 | 0.14053 | -122.2812 | -0.051583 | -0.034841 | 0.48008 | 0.15299 | 0.20457 | -0.027079 | 0.032106 | -0.3055 | -0.12608 | 4.0383 | 2.5341 | 2.8396 | -0.027474 | 0.012356 | 122.069 | 122.0768 | 122.136 | 119.4955 | -122.1555 | 121.9778 | 122.0764 | 122.1162 | 49.9713 | -122.4094
2205.125 | 122.2275 | -121.9666 | 0.15564 | 1.4211e-13 | -0.059647 | -0.010284 | 0.062801 | -0.010273 | 0.052394 | -0.0054937 | 0.00078395 | -0.0023288 | -0.004508 | 0.038935 | -0.012163 | -121.5002 | -2.5077 | -121.8136 | 0.088755 | 0.096516 | 0.16944 | -122.0227 | -117.8275 | -72.4944 | -119.3958 | 0.011252 | 0.10986 | 0.13595 | -122.2858 | -0.056159 | -0.066885 | 0.46634 | 0.15299 | 0.20915 | -0.059124 | 0.013798 | -0.31923 | -0.14439 | 4.1391 | 2.5707 | 2.8899 | -0.045783 | -0.019688 | 122.0553 | 122.0631 | 122.136 | 119.4589 | -122.1784 | 121.9778 | 122.0764 | 122.1025 | 49.4722 | -122.4414
2206.875 | 122.1863 | -122.0169 | 0.13275 | 1.4211e-13 | -0.059219 | -0.010712 | 0.06216 | -0.010487 | 0.051753 | -0.0054937 | 0.00057035 | -0.0025424 | -0.004508 | 0.038722 | -0.01195 | -121.5048 | -2.5214 | -121.8181 | 0.088755 | 0.096516 | 0.16486 | -122.0181 | -117.5115 | -72.9751 | -119.3409 | 0.011252 | 0.1007 | 0.13137 | -122.2904 | -0.001227 | -0.043996 | 0.51212 | 0.19877 | 0.19999 | -0.036235 | 0.032108 | -0.27345 | -0.1215 | 4.5054 | 2.676 | 2.9495 | -0.032051 | -0.001378 | 122.1057 | 122.1134 | 122.1818 | 119.4955 | -122.1509 | 122.0282 | 122.1176 | 122.1483 | 49.0418 | -122.4231
2208.625 | 122.3328 | -121.9437 | 0.1236 | 1.4211e-13 | -0.059647 | -0.010498 | 0.062588 | -0.0107 | 0.052181 | -0.013124 | 0.0012114 | -0.0021152 | -0.004508 | 0.038508 | -0.011736 | -121.5002 | -2.5443 | -121.8136 | 0.093333 | 0.096516 | 0.16486 | -122.0136 | -117.6581 | -73.4421 | -119.2814 | 0.006674 | 0.10528 | 0.13595 | -122.2858 | -0.06989 | -0.030263 | 0.44346 | 0.1301 | 0.19999 | -0.02708 | 0.041263 | -0.34212 | -0.11692 | 4.2856 | 2.6623 | 3.0044 | -0.018317 | 0.012356 | 122.037 | 122.0402 | 122.1085 | 119.3994 | -122.1372 | 121.9503 | 122.0489 | 122.0796 | 48.5015 | -122.4094
2210.3281 | 122.2549 | -121.9803 | 0.13733 | 1.4211e-13 | -0.059647 | -0.010712 | 0.061947 | -0.0107 | 0.052181 | -0.013124 | 0.00057035 | -0.0025424 | -0.0047216 | 0.038935 | -0.011736 | -121.4956 | -2.5626 | -121.8227 | 0.093333 | 0.096516 | 0.16028 | -122.0181 | -117.6031 | -74.0053 | -119.2264 | 0.006674 | 0.1007 | 0.13595 | -122.2812 | -0.037848 | -0.043996 | 0.48466 | 0.15757 | 0.19541 | -0.040813 | 0.022951 | -0.30092 | -0.13065 | 4.3772 | 2.7539 | 3.0548 | -0.036629 | -0.001377 | 122.0736 | 122.0768 | 122.1406 | 119.4177 | -122.1555 | 121.987 | 122.081 | 122.1162 | 47.975 | -122.4185
2212.0781 | 122.3053 | -121.9391 | 0.12817 | 1.4211e-13 | -0.059647 | -0.010284 | 0.06216 | -0.010914 | 0.051967 | 0.0021363 | 0.00078395 | -0.0025424 | -0.0047216 | 0.038722 | -0.011736 | -121.5048 | -2.5809 | -121.8227 | 0.088755 | 0.096516 | 0.16486 | -122.0227 | -117.4886 | -74.5044 | -119.1486 | 0.011252 | 0.10528 | 0.14053 | -122.2904 | -0.083625 | -0.039419 | 0.4343 | 0.11637 | 0.19999 | -0.031658 | 0.036685 | -0.35127 | -0.11692 | 4.4504 | 2.7905 | 3.1418 | -0.022895 | 0.012356 | 122.0278 | 122.0356 | 122.1039 | 119.3582 | -122.1509 | 121.9503 | 122.0444 | 122.0796 | 47.4347 | -122.4185
2213.8438 | 122.3007 | -121.9666 | 0.11902 | 1.4211e-13 | -0.059647 | -0.010284 | 0.06216 | -0.010273 | 0.052181 | -0.0054937 | 0.00057035 | -0.0025424 | -0.0042942 | 0.038935 | -0.011736 | -121.5002 | -2.5947 | -121.8136 | 0.093333 | 0.096516 | 0.16486 | -122.0181 | -117.3833 | -74.6784 | -119.0753 | 0.006674 | 0.10528 | 0.13595 | -122.2858 | -0.051581 | -0.025686 | 0.46634 | 0.15299 | 0.20457 | -0.022503 | 0.04584 | -0.31923 | -0.11235 | 4.5832 | 2.8912 | 3.2104 | -0.01374 | 0.016933 | 122.0599 | 122.0631 | 122.1314 | 119.3719 | -122.1372 | 121.9732 | 122.0718 | 122.1025 | 47.2882 | -122.4048
2215.5938 | 122.2916 | -121.9528 | 0.1236 | 1.4211e-13 | -0.059647 | -0.010498 | 0.062374 | -0.010914 | 0.051967 | 0.0021363 | 0.00078395 | -0.0021152 | -0.0040806 | 0.039149 | -0.011309 | -121.5002 | -2.6221 | -121.8227 | 0.093333 | 0.1011 | 0.16486 | -122.0136 | -117.2872 | -75.1317 | -119.0112 | 0.011252 | 0.1007 | 0.13137 | -122.2812 | -0.060735 | -0.030263 | 0.45261 | 0.1301 | 0.19083 | -0.022501 | 0.041263 | -0.32838 | -0.11234 | 4.6656 | 2.9416 | 3.27 | -0.022896 | 0.007777 | 122.0462 | 122.0539 | 122.1177 | 119.3307 | -122.1372 | 121.9641 | 122.0535 | 122.0842 | 46.8211 | -122.4048
2217.2812 | 122.2824 | -121.9666 | 0.09613 | 1.4211e-13 | -0.059647 | -0.010284 | 0.062374 | -0.010487 | 0.052181 | -0.013124 | 0.00078395 | -0.0023288 | -0.0040806 | 0.039363 | -0.011309 | -121.5048 | -2.6542 | -121.8227 | 0.093333 | 0.096516 | 0.16028 | -122.0319 | -117.1819 | -75.5896 | -118.9242 | 0.006674 | 0.1007 | 0.13595 | -122.2812 | -0.065317 | -0.002797 | 0.46176 | 0.14383 | 0.20915 | 0.000386 | 0.06415 | -0.31465 | -0.089456 | 4.7847 | 3.0423 | 3.357 | 0.00457 | 0.039822 | 122.0599 | 122.0631 | 122.1268 | 119.3124 | -122.128 | 121.9732 | 122.0673 | 122.1025 | 46.377 | -122.3773
2219.0312 | 122.2046 | -121.9666 | 0.13733 | 1.4211e-13 | -0.059433 | -0.010284 | 0.062374 | -0.010487 | 0.052181 | -0.0054937 | 0.00099775 | -0.0021152 | -0.0042942 | 0.039149 | -0.011309 | -121.5048 | -2.6679 | -121.8181 | 0.093333 | 0.096516 | 0.16486 | -122.0273 | -117.0582 | -76.1024 | -118.851 | 0.006674 | 0.10528 | 0.13595 | -122.2904 | -0.060738 | -0.043996 | 0.46176 | 0.14841 | 0.20915 | -0.040813 | 0.02753 | -0.32381 | -0.13065 | 4.9083 | 3.1156 | 3.4394 | -0.03205 | -0.001377 | 122.0599 | 122.0631 | 122.1314 | 119.2986 | -122.1646 | 121.9732 | 122.0718 | 122.1025 | 45.8642 | -122.4277
2220.7969 | 122.3053 | -121.9482 | 0.10529 | 1.4211e-13 | -0.059647 | -0.010284 | 0.062588 | -0.0107 | 0.051967 | -0.013124 | 0.00078395 | -0.0021152 | -0.0040806 | 0.039363 | -0.011095 | -121.4956 | -2.6908 | -121.8319 | 0.088755 | 0.091937 | 0.16486 | -122.0227 | -116.9438 | -76.5511 | -118.7686 | 0.015831 | 0.10986 | 0.13595 | -122.2812 | -0.07447 | -0.016531 | 0.45261 | 0.11637 | 0.19084 | -0.013349 | 0.059573 | -0.33296 | -0.089455 | 5.0045 | 3.1797 | 3.5126 | 0.004571 | 0.030666 | 122.037 | 122.0402 | 122.1131 | 119.2574 | -122.128 | 121.9641 | 122.0581 | 122.0842 | 45.3972 | -122.3865
2222.5 | 122.1909 | -122.0535 | 0.14648 | 1.4211e-13 | -0.060074 | -0.010712 | 0.062588 | -0.010914 | 0.052181 | -0.0054937 | 0.00078395 | -0.0021152 | -0.0042942 | 0.039577 | -0.011095 | -121.4956 | -2.7137 | -121.8227 | 0.10249 | 0.096516 | 0.16028 | -122.0227 | -116.811 | -77.0135 | -118.677 | 0.002095 | 0.10528 | 0.14053 | -122.2858 | 0.030816 | -0.043994 | 0.5579 | 0.23081 | 0.19999 | -0.049968 | 0.013796 | -0.23225 | -0.14439 | 5.2425 | 3.3765 | 3.6088 | -0.041205 | -0.005954 | 122.156 | 122.15 | 122.2138 | 119.3398 | -122.1692 | 122.0556 | 122.1588 | 122.1941 | 45.04 | -122.4323
2224.25 | 122.2961 | -121.9574 | 0.11444 | 1.4211e-13 | -0.05986 | -0.010498 | 0.062374 | -0.010914 | 0.051967 | -0.013124 | 0.001425 | -0.0025424 | -0.0042942 | 0.039577 | -0.010668 | -121.4911 | -2.732 | -121.8227 | 0.093333 | 0.10567 | 0.16028 | -122.0227 | -116.7011 | -77.5126 | -118.5808 | 0.011252 | 0.10986 | 0.14053 | -122.2812 | -0.065315 | -0.021108 | 0.46634 | 0.13468 | 0.19999 | -0.008767 | 0.045839 | -0.32381 | -0.10319 | 5.2563 | 3.3766 | 3.7004 | -0.004584 | 0.026089 | 122.0507 | 122.0631 | 122.1177 | 119.2254 | -122.1372 | 121.9686 | 122.0673 | 122.0979 | 44.4448 | -122.3956
2226 | 122.2046 | -121.9849 | 0.14648 | 1.4211e-13 | -0.05986 | -0.010071 | 0.062588 | -0.0107 | 0.052181 | -0.013124 | 0.0012114 | -0.0021152 | -0.0040806 | 0.039577 | -0.010881 | -121.4956 | -2.7458 | -121.8181 | 0.093333 | 0.1011 | 0.16944 | -122.0227 | -116.5775 | -77.9659 | -118.4938 | 0.011252 | 0.10986 | 0.14053 | -122.2858 | -0.037849 | -0.053151 | 0.48923 | 0.16672 | 0.20457 | -0.045389 | 0.022954 | -0.30092 | -0.13523 | 5.4074 | 3.491 | 3.7919 | -0.036627 | -0.005954 | 122.0782 | 122.086 | 122.1543 | 119.2391 | -122.1692 | 121.9961 | 122.0947 | 122.1254 | 44.019 | -122.4323
2227.6875 | 122.2 | -121.9986 | 0.14648 | 1.4211e-13 | -0.05986 | -0.010712 | 0.062588 | -0.010914 | 0.052181 | -0.0054937 | 0.0012114 | -0.0016878 | -0.0040806 | 0.039577 | -0.010668 | -121.5048 | -2.7641 | -121.8181 | 0.10249 | 0.1011 | 0.16486 | -122.0181 | -116.463 | -78.4284 | -118.4068 | 0.011252 | 0.10528 | 0.14053 | -122.2858 | -0.019538 | -0.043994 | 0.49381 | 0.18046 | 0.19999 | -0.045389 | 0.018375 | -0.28719 | -0.13523 | 5.5356 | 3.5918 | 3.8789 | -0.041205 | -0.005954 | 122.1011 | 122.0997 | 122.1635 | 119.2345 | -122.1646 | 122.0098 | 122.1039 | 122.1391 | 43.5702 | -122.4323
2229.4688 | 122.2687 | -121.9711 | 0.12817 | 1.4211e-13 | -0.05986 | -0.010498 | 0.062588 | -0.010914 | 0.051967 | 0.0021363 | 0.00099775 | -0.0021152 | -0.0040806 | 0.039577 | -0.01024 | -121.4911 | -2.7961 | -121.8227 | 0.088755 | 0.10567 | 0.16944 | -122.0181 | -116.3623 | -78.9366 | -118.3153 | 0.015831 | 0.10528 | 0.13137 | -122.2858 | -0.047004 | -0.039419 | 0.48008 | 0.14841 | 0.19541 | -0.0225 | 0.041264 | -0.31465 | -0.11234 | 5.6088 | 3.6559 | 3.9705 | -0.022895 | 0.003199 | 122.0599 | 122.0768 | 122.1406 | 119.175 | -122.1463 | 121.987 | 122.0764 | 122.1025 | 43.0345 | -122.414
2231.2188 | 122.2 | -121.994 | 0.18768 | 1.4211e-13 | -0.059647 | -0.010498 | 0.062374 | -0.010914 | 0.052181 | -0.013124 | 0.0012114 | -0.0019016 | -0.0040806 | 0.040004 | -0.010668 | -121.4911 | -2.819 | -121.809 | 0.11165 | 0.10567 | 0.1786 | -122.009 | -116.1929 | -79.3487 | -118.2145 | 0.020409 | 0.12359 | 0.14511 | -122.2766 | -0.014957 | -0.076036 | 0.50297 | 0.18503 | 0.19999 | -0.082009 | -0.009088 | -0.28261 | -0.16727 | 5.8011 | 3.7795 | 4.0621 | -0.06409 | -0.042574 | 122.1057 | 122.0997 | 122.1726 | 119.175 | -122.1967 | 122.0144 | 122.1176 | 122.1391 | 42.6453 | -122.4643
2232.9062 | 122.2183 | -121.4584 | 0.55389 | 1.4211e-13 | -0.05986 | -0.010284 | 0.062374 | -0.0107 | 0.052394 | -0.020755 | 0.0012114 | -0.0016878 | -0.0040806 | 0.040004 | -0.010027 | -121.0241 | -2.8236 | -121.3283 | 0.50539 | 0.51778 | 0.58151 | -121.5236 | -115.616 | -79.4036 | -117.6605 | 0.42332 | 0.52651 | 0.56176 | -121.7913 | -0.065175 | -0.048506 | 0.43438 | 0.13017 | 0.19535 | -0.036117 | 0.027618 | -0.33284 | -0.13058 | 5.8425 | 3.7979 | 4.1308 | -0.027384 | 0.007868 | 121.9638 | 121.9762 | 122.0399 | 118.6348 | -122.0775 | 121.8818 | 121.9849 | 122.0202 | 42.0548 | -122.3452
2234.6562 | 122.2321 | -121.4127 | 0.53558 | 1.4211e-13 | -0.05986 | -0.010284 | 0.062374 | -0.0107 | 0.052181 | -0.013124 | 0.0012114 | -0.0014742 | -0.003867 | 0.03979 | -0.010027 | -120.9966 | -2.8511 | -121.31 | 0.50997 | 0.5132 | 0.57693 | -121.5099 | -115.4557 | -79.8935 | -117.5644 | 0.42332 | 0.52651 | 0.55718 | -121.773 | -0.097214 | -0.025617 | 0.41607 | 0.10271 | 0.19992 | -0.022384 | 0.04135 | -0.3603 | -0.11227 | 5.957 | 3.8483 | 4.2086 | -0.009073 | 0.0216 | 121.9226 | 121.9259 | 121.9896 | 118.5616 | -122.0455 | 121.836 | 121.9392 | 121.9698 | 41.5191 | -122.3085
2236.4062 | 122.081 | -121.4584 | 0.55847 | 1.4211e-13 | -0.060074 | -0.010498 | 0.062588 | -0.010914 | 0.051967 | -0.013124 | 0.0012114 | -0.0019016 | -0.0040806 | 0.040004 | -0.010027 | -120.9829 | -2.8648 | -121.3054 | 0.50081 | 0.50862 | 0.58151 | -121.5007 | -115.2954 | -80.2003 | -117.4682 | 0.42332 | 0.51277 | 0.54803 | -121.7592 | -0.04228 | -0.057662 | 0.47558 | 0.15306 | 0.19534 | -0.049852 | 0.02304 | -0.30078 | -0.13515 | 6.163 | 3.9902 | 4.291 | -0.045698 | -0.010446 | 121.9592 | 121.9671 | 122.0399 | 118.5936 | -122.0592 | 121.8818 | 121.9712 | 122.0065 | 41.2581 | -122.3177
2238.1719 | 122.0856 | -121.4676 | 0.5722 | 1.4211e-13 | -0.05986 | -0.010498 | 0.062374 | -0.0107 | 0.052181 | -0.0054937 | 0.00078395 | -0.0014742 | -0.0040806 | 0.040218 | -0.01024 | -120.9783 | -2.8831 | -121.2916 | 0.50081 | 0.5132 | 0.57235 | -121.487 | -115.1443 | -80.4567 | -117.3675 | 0.41874 | 0.51735 | 0.55718 | -121.7638 | -0.019388 | -0.071395 | 0.48932 | 0.17595 | 0.19534 | -0.059006 | 0.00015 | -0.29621 | -0.15347 | 6.3232 | 4.1001 | 4.3963 | -0.054852 | -0.015022 | 121.9684 | 121.9808 | 122.0399 | 118.5845 | -122.0592 | 121.8863 | 121.9849 | 122.0248 | 41.0109 | -122.336
2239.8594 | 122.1817 | -121.4401 | 0.5127 | 1.4211e-13 | -0.060074 | -0.010284 | 0.062374 | -0.0107 | 0.051753 | -0.0054937 | 0.0012114 | -0.0014742 | -0.0040806 | 0.040218 | -0.0098132 | -120.9691 | -2.906 | -121.2962 | 0.50081 | 0.50404 | 0.57235 | -121.487 | -115.0299 | -80.736 | -117.2805 | 0.41874 | 0.51277 | 0.54803 | -121.7638 | -0.046853 | -0.011885 | 0.47101 | 0.14391 | 0.19076 | -0.008654 | 0.05966 | -0.32367 | -0.093957 | 6.4102 | 4.1596 | 4.4833 | 7.9e-05 | 0.035331 | 121.9409 | 121.9442 | 122.0125 | 118.5341 | -121.9997 | 121.8589 | 121.9529 | 121.9882 | 40.7041 | -122.2765
2241.6094 | 122.0718 | -121.4676 | 0.56305 | 1.4211e-13 | -0.060074 | -0.010498 | 0.062588 | -0.0107 | 0.051967 | -0.0054937 | 0.0012114 | -0.0012606 | -0.0036534 | 0.040431 | -0.0095994 | -120.9783 | -2.9335 | -121.2871 | 0.49623 | 0.50404 | 0.57235 | -121.487 | -114.8834 | -80.91 | -117.1797 | 0.41874 | 0.51277 | 0.54345 | -121.7592 | -0.019388 | -0.066818 | 0.48932 | 0.18053 | 0.19992 | -0.059008 | 0.009306 | -0.29163 | -0.14431 | 6.5842 | 4.2878 | 4.5795 | -0.050275 | -0.019602 | 121.9638 | 121.9716 | 122.0399 | 118.5341 | -122.05 | 121.8863 | 121.9804 | 122.011 | 40.5576 | -122.3223
2243.3594 | 122.0901 | -121.1105 | 0.54474 | 1.4211e-13 | -0.060288 | -0.010284 | 0.062588 | -0.010487 | 0.052181 | -0.0054937 | 0.0012114 | -0.0014742 | -0.0036534 | 0.040431 | -0.0095994 | -120.9783 | -2.9609 | -121.3008 | 0.49165 | 0.4903 | 0.55862 | -121.4961 | -114.7552 | -81.084 | -117.0928 | 0.40042 | 0.50362 | 0.53429 | -121.7684 | -0.3856 | -0.053086 | 0.13226 | -0.19026 | 0.19534 | -0.054435 | 0.01388 | -0.65784 | -0.14431 | 6.3554 | 4.0178 | 4.6756 | -0.041122 | -0.010449 | 121.6022 | 121.6008 | 121.6692 | 118.1496 | -122.0409 | 121.511 | 121.6142 | 121.6448 | 40.0265 | -122.3131
2245.1094 | 122.1863 | -121.4172 | 0.50354 | 1.4211e-13 | -0.060074 | -0.010925 | 0.062374 | -0.010914 | 0.051967 | -0.013124 | 0.00099775 | -0.0012606 | -0.0036534 | 0.040218 | -0.0095994 | -120.9829 | -2.9793 | -121.2962 | 0.4825 | 0.48573 | 0.55862 | -121.4916 | -114.5857 | -80.9558 | -116.992 | 0.40042 | 0.49904 | 0.52513 | -121.7592 | -0.074321 | -0.021044 | 0.43438 | 0.12102 | 0.19534 | -0.017815 | 0.055079 | -0.34198 | -0.10312 | 6.8315 | 4.4252 | 4.7672 | -0.004502 | 0.021593 | 121.8997 | 121.903 | 121.9759 | 118.438 | -121.9951 | 121.8177 | 121.9163 | 121.9424 | 40.4614 | -122.2628
2246.7969 | 121.8475 | -121.1563 | 0.54474 | 1.4211e-13 | -0.05986 | -0.010498 | 0.06216 | -0.010487 | 0.051753 | -0.013124 | 0.0012114 | -0.0012606 | -0.0034396 | 0.040645 | -0.0091722 | -120.9691 | -3.0067 | -121.2916 | 0.4825 | 0.4903 | 0.55404 | -121.4824 | -114.4072 | -80.9467 | -116.8867 | 0.40042 | 0.49904 | 0.52513 | -121.7546 | -0.32609 | -0.062243 | 0.18719 | -0.13533 | 0.19076 | -0.054435 | 0.009301 | -0.59833 | -0.14431 | 6.7491 | 4.2696 | 4.8679 | -0.045701 | -0.019606 | 121.6388 | 121.6466 | 121.7104 | 118.1496 | -122.0271 | 121.5567 | 121.6553 | 121.6814 | 40.2097 | -122.2994
2248.5469 | 121.4447 | -120.8267 | 0.54932 | 1.4211e-13 | -0.060288 | -0.010925 | 0.062374 | -0.0107 | 0.051967 | -0.0054937 | 0.0012114 | -0.0014742 | -0.0030124 | 0.041286 | -0.0091722 | -120.9737 | -3.025 | -121.2916 | 0.48707 | 0.48573 | 0.55404 | -121.487 | -114.2698 | -80.8871 | -116.7631 | 0.39585 | 0.49904 | 0.52513 | -121.7592 | -0.66026 | -0.062241 | -0.14697 | -0.46492 | 0.19534 | -0.063591 | 0.004724 | -0.9325 | -0.15347 | 6.5569 | 4.0636 | 4.9961 | -0.050278 | -0.024183 | 121.3138 | 121.3124 | 121.3808 | 117.8017 | -122.0363 | 121.2226 | 121.3258 | 121.3519 | 39.9396 | -122.3085
2250.2344 | 121.8292 | -121.2616 | 0.52643 | 1.4211e-13 | -0.060288 | -0.010284 | 0.062374 | -0.0107 | 0.052181 | -0.013124 | 0.0012114 | -0.00061965 | -0.003226 | 0.040859 | -0.0089584 | -120.9691 | -3.0479 | -121.2871 | 0.4825 | 0.48573 | 0.54488 | -121.487 | -114.0958 | -80.7406 | -116.6257 | 0.39585 | 0.49446 | 0.52513 | -121.7501 | -0.22538 | -0.043932 | 0.29248 | -0.025464 | 0.19992 | -0.040703 | 0.018455 | -0.48846 | -0.13058 | 7.1658 | 4.6359 | 5.1243 | -0.031968 | -0.001295 | 121.7441 | 121.7473 | 121.8065 | 118.2137 | -122.0134 | 121.6574 | 121.7561 | 121.7867 | 40.521 | -122.2765
2252 | 122.168 | -121.4264 | 0.49439 | 1.4211e-13 | -0.060074 | -0.010284 | 0.062588 | -0.010914 | 0.052181 | -0.020755 | 0.0012114 | -0.00083325 | -0.0034396 | 0.041286 | -0.0087448 | -120.9737 | -3.0708 | -121.2825 | 0.46418 | 0.48115 | 0.54946 | -121.4778 | -113.8944 | -80.5895 | -116.5158 | 0.38669 | 0.48988 | 0.52513 | -121.7546 | -0.051428 | -0.030202 | 0.4527 | 0.14391 | 0.19534 | -0.013239 | 0.055077 | -0.32825 | -0.1077 | 7.532 | 4.9106 | 5.2388 | -0.004504 | 0.030748 | 121.8906 | 121.9075 | 121.9759 | 118.3556 | -121.9722 | 121.8131 | 121.9163 | 121.9515 | 40.8369 | -122.249
2253.7031 | 122.1268 | -121.4493 | 0.52643 | 1.4211e-13 | -0.060074 | -0.010925 | 0.06216 | -0.0107 | 0.051326 | -0.013124 | 0.0012114 | -0.00083325 | -0.003226 | 0.041286 | -0.0083176 | -120.9783 | -3.0937 | -121.2916 | 0.46876 | 0.47657 | 0.5403 | -121.487 | -113.7295 | -80.3835 | -116.4059 | 0.37753 | 0.48072 | 0.50682 | -121.773 | -0.037698 | -0.057667 | 0.47101 | 0.15764 | 0.19534 | -0.049861 | 0.013876 | -0.32367 | -0.1489 | 7.7198 | 5.0433 | 5.367 | -0.045704 | -0.01961 | 121.918 | 121.9258 | 121.9896 | 118.3556 | -122.0134 | 121.8268 | 121.93 | 121.9561 | 41.0658 | -122.2994
2255.4688 | 122.168 | -121.431 | 0.46692 | 1.4211e-13 | -0.060288 | -0.010712 | 0.062588 | -0.0107 | 0.051753 | -0.0054937 | 0.0012114 | -0.00061965 | -0.003226 | 0.041286 | -0.0083176 | -120.9966 | -3.1212 | -121.3145 | 0.44587 | 0.45367 | 0.51741 | -121.5099 | -113.5601 | -80.182 | -116.3098 | 0.35464 | 0.46241 | 0.49308 | -121.7821 | -0.078904 | -0.02105 | 0.43438 | 0.11644 | 0.19534 | -0.013246 | 0.050492 | -0.35114 | -0.11228 | 7.8709 | 5.1212 | 5.4723 | -0.004509 | 0.026164 | 121.8768 | 121.8846 | 121.9484 | 118.3098 | -121.9768 | 121.7856 | 121.8934 | 121.9241 | 41.249 | -122.249
2257.2188 | 122.1039 | -121.4401 | 0.50812 | 1.4211e-13 | -0.060074 | -0.010498 | 0.062588 | -0.0107 | 0.051967 | -0.020755 | 0.00099775 | -0.00083325 | -0.0030124 | 0.0415 | -0.0081038 | -120.9691 | -3.1395 | -121.2871 | 0.46418 | 0.48115 | 0.54488 | -121.487 | -113.3541 | -79.8386 | -116.1587 | 0.39127 | 0.48072 | 0.51598 | -121.7546 | -0.046853 | -0.043935 | 0.47101 | 0.15306 | 0.19992 | -0.026972 | 0.036765 | -0.31451 | -0.11685 | 8.0861 | 5.2814 | 5.5959 | -0.027394 | 0.007858 | 121.9043 | 121.9213 | 121.985 | 118.3006 | -121.9951 | 121.8314 | 121.9208 | 121.9561 | 41.6015 | -122.2628
2258.9844 | 122.113 | -121.4172 | 0.50354 | 1.4211e-13 | -0.060288 | -0.010498 | 0.062374 | -0.010487 | 0.051753 | -0.0054937 | 0.0016386 | -0.00040585 | -0.0027988 | 0.041286 | -0.0078902 | -120.96 | -3.167 | -121.2779 | 0.46418 | 0.47199 | 0.5403 | -121.4824 | -113.2121 | -79.5914 | -116.0442 | 0.38211 | 0.4853 | 0.5114 | -121.7455 | -0.065163 | -0.039357 | 0.45728 | 0.13933 | 0.20449 | -0.031552 | 0.036764 | -0.32825 | -0.12143 | 8.2051 | 5.373 | 5.7013 | -0.018237 | 0.007857 | 121.8814 | 121.8892 | 121.9575 | 118.2503 | -121.9859 | 121.7993 | 121.9025 | 121.9286 | 41.8259 | -122.249
2260.6719 | 122.0993 | -121.3852 | 0.49439 | 1.4211e-13 | -0.060288 | -0.010712 | 0.06216 | -0.011128 | 0.051967 | -0.0054937 | 0.001425 | -0.00019225 | -0.002585 | 0.041286 | -0.0076766 | -120.9645 | -3.1853 | -121.2825 | 0.4596 | 0.48115 | 0.53573 | -121.487 | -113.029 | -79.2846 | -115.9298 | 0.37753 | 0.48988 | 0.50682 | -121.7501 | -0.10178 | -0.034781 | 0.42065 | 0.10271 | 0.20449 | -0.013239 | 0.041341 | -0.36487 | -0.11685 | 8.3562 | 5.4554 | 5.8203 | -0.004504 | 0.012433 | 121.8448 | 121.8663 | 121.9209 | 118.1999 | -121.9814 | 121.7627 | 121.8751 | 121.892 | 42.1006 | -122.2444
2262.3594 | 122.1542 | -121.4172 | 0.49896 | 1.4211e-13 | -0.060074 | -0.010925 | 0.062374 | -0.0107 | 0.051753 | -0.020755 | 0.001425 | 2.1352e-05 | -0.0027988 | 0.0415 | -0.007463 | -120.96 | -3.2174 | -121.2871 | 0.46418 | 0.47199 | 0.53573 | -121.4778 | -112.8733 | -79.0328 | -115.8153 | 0.38211 | 0.48072 | 0.5114 | -121.7455 | -0.060584 | -0.034779 | 0.45728 | 0.13018 | 0.19076 | -0.026974 | 0.036764 | -0.32825 | -0.11685 | 8.5439 | 5.6019 | 5.9302 | -0.018238 | 0.012435 | 121.8814 | 121.8892 | 121.953 | 118.1999 | -121.9768 | 121.7993 | 121.898 | 121.9286 | 42.3845 | -122.2444
2264.1094 | 122.113 | -121.3943 | 0.5127 | 1.4211e-13 | -0.060288 | -0.011139 | 0.06216 | -0.010487 | 0.052181 | -0.020755 | 0.001425 | 2.1352e-05 | -0.0021578 | 0.041713 | -0.0072492 | -120.96 | -3.2402 | -121.2733 | 0.4596 | 0.47199 | 0.53115 | -121.4778 | -112.7176 | -78.726 | -115.7329 | 0.37753 | 0.47614 | 0.50682 | -121.7409 | -0.083472 | -0.053091 | 0.43439 | 0.12102 | 0.20449 | -0.040707 | 0.018452 | -0.34656 | -0.13516 | 8.6767 | 5.6615 | 6.008 | -0.03655 | -0.005877 | 121.854 | 121.8663 | 121.9255 | 118.1541 | -121.9905 | 121.7719 | 121.8705 | 121.9012 | 42.6684 | -122.2536
2265.7969 | 121.8887 | -121.4035 | 0.52185 | 1.4211e-13 | -0.060501 | -0.010712 | 0.062801 | -0.010487 | 0.051753 | -0.020755 | 0.0012114 | 0.00023495 | -0.0021578 | 0.042141 | -0.0070356 | -120.9508 | -3.2586 | -121.2687 | 0.45503 | 0.46741 | 0.53115 | -121.4687 | -112.4795 | -78.4421 | -115.5955 | 0.37753 | 0.4853 | 0.50682 | -121.7455 | -0.06516 | -0.066825 | 0.4527 | 0.13475 | 0.19992 | -0.054442 | 0.009296 | -0.34198 | -0.14432 | 8.924 | 5.808 | 6.15 | -0.036548 | -0.015033 | 121.8585 | 121.8709 | 121.9347 | 118.1449 | -121.9905 | 121.781 | 121.8888 | 121.9103 | 42.9614 | -122.2673
2267.5469 | 122.1313 | -121.3898 | 0.48065 | 1.4211e-13 | -0.060288 | -0.010498 | 0.062588 | -0.0107 | 0.051753 | -0.0054937 | 0.001425 | 2.1352e-05 | -0.0021578 | 0.041713 | -0.0066084 | -120.9508 | -3.286 | -121.2779 | 0.4596 | 0.46741 | 0.53573 | -121.4687 | -112.4521 | -78.2132 | -115.4856 | 0.37295 | 0.48072 | 0.50224 | -121.7409 | -0.078892 | -0.021048 | 0.43897 | 0.11187 | 0.19076 | -0.013243 | 0.055074 | -0.35113 | -0.1077 | 8.9377 | 5.9041 | 6.2553 | 7.2e-05 | 0.021588 | 121.8494 | 121.8572 | 121.9255 | 118.1037 | -121.9493 | 121.7627 | 121.8705 | 121.892 | 43.1766 | -122.2216
2269.2969 | 122.1085 | -121.4127 | 0.48065 | 1.4211e-13 | -0.060715 | -0.010498 | 0.062588 | -0.010914 | 0.051967 | -0.0054937 | 0.0012114 | 0.00023495 | -0.0021578 | 0.041927 | -0.0066084 | -120.9462 | -3.2998 | -121.2687 | 0.4596 | 0.47199 | 0.53573 | -121.4687 | -112.3101 | -77.9018 | -115.4124 | 0.37753 | 0.47157 | 0.50682 | -121.7501 | -0.056004 | -0.021048 | 0.46643 | 0.14391 | 0.19992 | -0.008664 | 0.055074 | -0.3374 | -0.10312 | 9.1025 | 6.0003 | 6.3377 | -0.009085 | 0.026166 | 121.8723 | 121.8846 | 121.9484 | 118.1129 | -121.9493 | 121.7902 | 121.8842 | 121.9195 | 43.5108 | -122.2307
2270.9688 | 121.701 | -121.0007 | 0.52643 | 1.4211e-13 | -0.060715 | -0.010498 | 0.062588 | -0.011128 | 0.051967 | -0.020755 | 0.001425 | -0.00019225 | -0.0019442 | 0.042354 | -0.0063946 | -120.9508 | -3.3318 | -121.2733 | 0.45503 | 0.46283 | 0.53573 | -121.4641 | -112.1865 | -77.6271 | -115.3254 | 0.37295 | 0.47157 | 0.49766 | -121.7409 | -0.46341 | -0.071402 | 0.049868 | -0.27266 | 0.19076 | -0.063598 | 0.009298 | -0.74023 | -0.15348 | 8.8142 | 5.6753 | 6.4155 | -0.054861 | -0.028767 | 121.4557 | 121.4635 | 121.5364 | 117.6689 | -121.9905 | 121.3736 | 121.4722 | 121.4983 | 43.3736 | -122.2673
2272.7188 | 122.0673 | -121.1975 | 0.50812 | 1.4211e-13 | -0.060929 | -0.010498 | 0.062374 | -0.010914 | 0.051967 | -0.0054937 | 0.0016386 | 0.00066235 | -0.0021578 | 0.042141 | -0.006181 | -120.9508 | -3.3501 | -121.2916 | 0.44587 | 0.45825 | 0.51741 | -121.4824 | -112.1041 | -77.2013 | -115.2246 | 0.3638 | 0.47157 | 0.49308 | -121.7501 | -0.28489 | -0.062249 | 0.24671 | -0.094129 | 0.19076 | -0.049867 | 0.009293 | -0.55255 | -0.14432 | 9.0934 | 5.9729 | 6.5254 | -0.036551 | -0.015035 | 121.6434 | 121.6558 | 121.7149 | 117.8474 | -121.9905 | 121.5613 | 121.6691 | 121.6906 | 43.9962 | -122.2582
2274.4688 | 121.9894 | -121.4081 | 0.50812 | 1.4211e-13 | -0.060501 | -0.010712 | 0.062588 | -0.0107 | 0.051967 | -0.0054937 | 0.0016386 | 0.00044875 | -0.0017306 | 0.042354 | -0.0057538 | -120.96 | -3.3776 | -121.2733 | 0.44129 | 0.44909 | 0.53115 | -121.4778 | -111.9347 | -76.5969 | -115.0964 | 0.3638 | 0.45783 | 0.49308 | -121.7409 | -0.069739 | -0.066827 | 0.44812 | 0.13475 | 0.20449 | -0.059024 | 0.023029 | -0.33282 | -0.14432 | 9.4734 | 6.3116 | 6.6445 | -0.050287 | -0.015035 | 121.8494 | 121.8572 | 121.9392 | 118.0305 | -121.9859 | 121.7719 | 121.8659 | 121.9012 | 44.8112 | -122.249
2276.1562 | 122.1176 | -121.4676 | 0.38452 | 1.4211e-13 | -0.060715 | -0.010498 | 0.062374 | -0.010914 | 0.052181 | -0.020755 | 0.0018522 | 0.00066235 | -0.0017306 | 0.042568 | -0.0059674 | -120.9829 | -3.4097 | -121.3054 | 0.42298 | 0.42162 | 0.48994 | -121.5328 | -111.8935 | -76.2123 | -115.014 | 0.33632 | 0.43036 | 0.46103 | -121.773 | -0.065178 | 0.038456 | 0.48474 | 0.16222 | 0.22739 | 0.037099 | 0.10542 | -0.30536 | -0.048196 | 9.5741 | 6.4536 | 6.7589 | 0.045838 | 0.076511 | 121.8906 | 121.8892 | 121.9575 | 118.0579 | -121.9173 | 121.8039 | 121.8979 | 121.9286 | 45.2553 | -122.1575
2277.9062 | 122.0352 | -121.5591 | 0.39368 | 1.4211e-13 | -0.060501 | -0.010071 | 0.062801 | -0.0107 | 0.051967 | -0.020755 | 0.0018522 | 0.00066235 | -0.0017306 | 0.042568 | -0.0059674 | -121.1019 | -3.4417 | -121.429 | 0.30852 | 0.32088 | 0.39379 | -121.693 | -111.8614 | -76.1482 | -115.0735 | 0.22644 | 0.32963 | 0.35572 | -121.9057 | -0.13389 | -0.08516 | 0.45725 | 0.13016 | 0.26404 | -0.072793 | 0.000112 | -0.3466 | -0.16724 | 9.6977 | 6.4856 | 6.8322 | -0.064047 | -0.037953 | 121.8677 | 121.88 | 121.9529 | 118.1174 | -122.0867 | 121.7856 | 121.8888 | 121.9149 | 45.411 | -122.2994
2279.6562 | 121.994 | -121.4493 | 0.49896 | 1.4211e-13 | -0.060501 | -0.010712 | 0.06216 | -0.011128 | 0.051753 | -0.020755 | 0.0016386 | 0.00066235 | -0.0017306 | 0.042782 | -0.0059674 | -120.96 | -3.4463 | -121.2916 | 0.43671 | 0.44451 | 0.51283 | -121.487 | -111.6004 | -75.791 | -114.808 | 0.35464 | 0.45783 | 0.47935 | -121.7638 | -0.037698 | -0.06225 | 0.48932 | 0.15764 | 0.19534 | -0.054447 | 0.013871 | -0.31452 | -0.14432 | 9.8489 | 6.6413 | 6.9558 | -0.041131 | -0.019615 | 121.886 | 121.8938 | 121.9621 | 118.003 | -121.9859 | 121.8039 | 121.9071 | 121.9286 | 45.6583 | -122.2628
2281.3438 | 121.9894 | -121.4676 | 0.48523 | 1.4211e-13 | -0.060501 | -0.010712 | 0.061947 | -0.010914 | 0.051967 | 0.0021363 | 0.0018522 | 0.00066235 | -0.0015168 | 0.042568 | -0.0057538 | -120.9554 | -3.4875 | -121.2916 | 0.43671 | 0.43994 | 0.50825 | -121.4916 | -111.5592 | -75.3789 | -114.7485 | 0.35006 | 0.45325 | 0.48392 | -121.7546 | -0.023967 | -0.048517 | 0.51221 | 0.17595 | 0.19992 | -0.045293 | 0.023025 | -0.28705 | -0.13517 | 9.9084 | 6.7191 | 7.0062 | -0.031977 | -0.001304 | 121.9043 | 121.9075 | 121.9758 | 117.9801 | -121.9768 | 121.8177 | 121.9208 | 121.9515 | 46.0886 | -122.2399
2283.0938 | 122.0444 | -121.4493 | 0.48981 | 1.4211e-13 | -0.061143 | -0.010284 | 0.062374 | -0.011128 | 0.051753 | -0.013124 | 0.0016386 | 0.00044875 | -0.0015168 | 0.042782 | -0.0059674 | -120.96 | -3.5058 | -121.2916 | 0.39093 | 0.43536 | 0.50825 | -121.4824 | -111.4951 | -74.9669 | -114.6889 | 0.35464 | 0.4441 | 0.47477 | -121.7501 | -0.033119 | -0.098879 | 0.48932 | 0.15764 | 0.19076 | -0.05445 | 0.018447 | -0.30078 | -0.13517 | 9.9542 | 6.7603 | 7.0611 | -0.045712 | -0.015039 | 121.8402 | 121.8846 | 121.9575 | 117.9435 | -121.9722 | 121.8039 | 121.8934 | 121.924 | 46.4824 | -122.2399
2284.8594 | 121.9986 | -121.7377 | 0.25177 | 1.4211e-13 | -0.060929 | -0.010498 | 0.061947 | -0.010914 | 0.051753 | -0.013124 | 0.0018522 | 0.0010898 | -0.0019442 | 0.042995 | -0.0057538 | -121.2118 | -3.5424 | -121.5389 | 0.14827 | 0.19267 | 0.25185 | -121.7342 | -111.6874 | -74.7654 | -114.8721 | 0.098244 | 0.18769 | 0.21837 | -122.0111 | 0.003431 | -0.1035 | 0.5259 | 0.19881 | 0.19537 | -0.059096 | 8.2e-05 | -0.27338 | -0.15353 | 10.0502 | 6.8656 | 7.139 | -0.064077 | -0.033404 | 121.8859 | 121.9303 | 121.9895 | 118.1952 | -121.986 | 121.8359 | 121.9254 | 121.956 | 46.9723 | -122.2628
2286.625 | 122.0627 | -121.7743 | 0.10986 | 1.4211e-13 | -0.060929 | -0.010284 | 0.062588 | -0.010914 | 0.051753 | -0.020755 | 0.0024932 | 0.00044875 | -0.0013032 | 0.042782 | -0.0053264 | -121.285 | -3.5699 | -121.6121 | 0.084176 | 0.1011 | 0.16944 | -121.8075 | -111.1883 | -72.444 | -114.7027 | 0.024988 | 0.10986 | 0.14053 | -122.0797 | -0.033211 | -0.025687 | 0.48927 | 0.16217 | 0.19538 | -0.008768 | 0.059575 | -0.30544 | -0.084875 | 10.5859 | 7.0716 | 7.3771 | -6e-06 | 0.030667 | 121.8585 | 121.8754 | 121.9437 | 118.2044 | -121.9174 | 121.7993 | 121.8841 | 121.9148 | 49.3303 | -122.1896
2288.375 | 121.9757 | -121.7651 | 0.15106 | 1.4211e-13 | -0.060715 | -0.010498 | 0.062374 | -0.0107 | 0.051753 | -0.0054937 | 0.0029204 | 0.0010898 | -0.0017306 | 0.043209 | -0.0046854 | -121.285 | -3.5928 | -121.6075 | 0.070441 | 0.091937 | 0.16486 | -121.8121 | -111.0189 | -71.6152 | -114.634 | 0.006674 | 0.096121 | 0.13137 | -122.0889 | -0.046945 | -0.080621 | 0.48011 | 0.1576 | 0.20454 | -0.059125 | 0.013797 | -0.32376 | -0.14439 | 10.7462 | 7.1312 | 7.4549 | -0.054941 | -0.019689 | 121.8356 | 121.8571 | 121.93 | 118.1723 | -121.9631 | 121.7718 | 121.8613 | 121.8965 | 50.1499 | -122.24
2290.0625 | 122.0444 | -121.7606 | 0.10986 | 1.4211e-13 | -0.060715 | -0.010925 | 0.06216 | -0.010914 | 0.051753 | -0.0054937 | 0.003134 | 0.00087595 | -0.0015168 | 0.043423 | -0.0042582 | -121.2896 | -3.6248 | -121.6213 | 0.065863 | 0.08278 | 0.16028 | -121.8121 | -110.8953 | -70.8918 | -114.5561 | 0.002095 | 0.096121 | 0.13595 | -122.0843 | -0.051523 | -0.044 | 0.47096 | 0.13928 | 0.19081 | -0.027083 | 0.050417 | -0.32376 | -0.10777 | 10.8653 | 7.2044 | 7.5282 | -0.013742 | 0.026089 | 121.8264 | 121.8433 | 121.9208 | 118.1357 | -121.9219 | 121.7627 | 121.8567 | 121.8965 | 50.8688 | -122.1942
2291.8125 | 122.0673 | -121.7285 | 0.10071 | 1.4211e-13 | -0.060715 | -0.010925 | 0.062801 | -0.011128 | 0.051967 | -0.0054937 | 0.0035614 | 0.0010898 | -0.0017306 | 0.043423 | -0.0036172 | -121.2804 | -3.6477 | -121.6167 | 0.061284 | 0.091937 | 0.16486 | -121.8121 | -110.7351 | -70.2004 | -114.4508 | -0.007062 | 0.1007 | 0.13137 | -122.0797 | -0.083566 | -0.039424 | 0.44807 | 0.11182 | 0.19539 | -0.008771 | 0.064151 | -0.35122 | -0.10777 | 10.9935 | 7.2777 | 7.6289 | -8e-06 | 0.030665 | 121.7898 | 121.8205 | 121.8934 | 118.0808 | -121.9128 | 121.7215 | 121.8292 | 121.8599 | 51.5281 | -122.1804
2293.5625 | 122.0673 | -121.7422 | 0.10986 | 1.4211e-13 | -0.060501 | -0.010925 | 0.06216 | -0.011128 | 0.052181 | -0.0054937 | 0.0033478 | 0.0010898 | -0.0017306 | 0.043209 | -0.0040444 | -121.2759 | -3.6752 | -121.6213 | 0.070441 | 0.087359 | 0.16028 | -121.8075 | -110.4374 | -69.6372 | -114.3501 | -0.01164 | 0.096121 | 0.12222 | -122.0843 | -0.065254 | -0.039422 | 0.46638 | 0.12097 | 0.18623 | -0.022504 | 0.050417 | -0.34207 | -0.1215 | 11.3048 | 7.3921 | 7.7342 | -0.013742 | 0.012353 | 121.8127 | 121.8296 | 121.9025 | 118.067 | -121.9174 | 121.7306 | 121.8384 | 121.8645 | 52.105 | -122.1942
2295.2656 | 121.994 | -121.7789 | 0.14648 | 1.4211e-13 | -0.061356 | -0.010712 | 0.062374 | -0.010914 | 0.051753 | 0.0021363 | 0.0033478 | 0.00087595 | -0.0015168 | 0.04385 | -0.0038308 | -121.2804 | -3.7027 | -121.6075 | 0.070441 | 0.096516 | 0.16028 | -121.8029 | -110.2039 | -69.0054 | -114.2723 | -0.002483 | 0.10528 | 0.12222 | -122.0797 | -0.024054 | -0.076043 | 0.49842 | 0.17133 | 0.19538 | -0.049968 | 0.013796 | -0.30087 | -0.14897 | 11.575 | 7.5066 | 7.8075 | -0.041205 | -0.024268 | 121.8493 | 121.8754 | 121.9391 | 118.0762 | -121.9494 | 121.7764 | 121.8841 | 121.9011 | 52.7735 | -122.2262
2297.0156 | 121.9299 | -121.7651 | 0.15106 | 1.4211e-13 | -0.060929 | -0.010498 | 0.062588 | -0.011341 | 0.052181 | -0.013124 | 0.003775 | 0.0013034 | -0.0019442 | 0.043636 | -0.0031898 | -121.2713 | -3.7256 | -121.603 | 0.079598 | 0.091937 | 0.16486 | -121.8121 | -109.8971 | -68.2865 | -114.1441 | 0.006674 | 0.1007 | 0.13137 | -122.0706 | -0.046945 | -0.071464 | 0.49385 | 0.16217 | 0.20912 | -0.059125 | 0.013797 | -0.30544 | -0.14439 | 11.868 | 7.6211 | 7.9265 | -0.050362 | -0.019689 | 121.8447 | 121.8571 | 121.93 | 118.0396 | -121.9631 | 121.7718 | 121.8658 | 121.8965 | 53.4786 | -122.2216
2298.7812 | 122.0123 | -121.7285 | 0.1236 | 1.4211e-13 | -0.060715 | -0.010712 | 0.06216 | -0.010914 | 0.051753 | -0.0054937 | 0.0035614 | 0.0013034 | -0.0017306 | 0.043636 | -0.0031898 | -121.2713 | -3.7576 | -121.603 | 0.065863 | 0.08278 | 0.16028 | -121.8029 | -109.5446 | -67.4211 | -114.0571 | -0.002483 | 0.096121 | 0.13137 | -122.066 | -0.074408 | -0.057733 | 0.45723 | 0.12555 | 0.19996 | -0.040816 | 0.036684 | -0.33748 | -0.12608 | 12.1839 | 7.6714 | 8.0089 | -0.027475 | 0.007777 | 121.7944 | 121.8113 | 121.8888 | 117.9709 | -121.9265 | 121.726 | 121.8246 | 121.8599 | 54.3074 | -122.1896
2300.5469 | 122.0215 | -121.7697 | 0.10529 | 1.4211e-13 | -0.061143 | -0.010712 | 0.062374 | -0.010914 | 0.051967 | -0.013124 | 0.0042022 | 0.0013034 | -0.0017306 | 0.04385 | -0.002549 | -121.2804 | -3.7897 | -121.6121 | 0.052128 | 0.078201 | 0.1557 | -121.8029 | -109.0638 | -66.6931 | -113.9792 | -0.01164 | 0.086964 | 0.12222 | -122.0843 | -0.03321 | -0.053158 | 0.48927 | 0.15759 | 0.1908 | -0.027085 | 0.050416 | -0.3146 | -0.11693 | 12.7059 | 7.7905 | 8.1051 | -0.018322 | 0.01693 | 121.8218 | 121.8479 | 121.9254 | 117.98 | -121.9082 | 121.7581 | 121.8567 | 121.8919 | 55.0766 | -122.1896
2302.2344 | 122.0718 | -121.7468 | 0.1236 | 1.4211e-13 | -0.060929 | -0.010498 | 0.06216 | -0.011128 | 0.05154 | -0.013124 | 0.0039886 | 0.0013034 | -0.0015168 | 0.04385 | -0.0021216 | -121.2713 | -3.8126 | -121.6167 | 0.056706 | 0.078201 | 0.1557 | -121.8075 | -108.5556 | -66.0567 | -113.9197 | -0.007062 | 0.091543 | 0.12222 | -122.0843 | -0.060677 | -0.06689 | 0.47554 | 0.13013 | 0.19081 | -0.045395 | 0.032106 | -0.33749 | -0.13066 | 13.1912 | 7.8271 | 8.1646 | -0.032053 | -0.00138 | 121.8035 | 121.825 | 121.9025 | 117.9343 | -121.9311 | 121.7398 | 121.8384 | 121.869 | 55.6901 | -122.2079
2303.9844 | 122.0306 | -121.7514 | 0.10986 | 1.4211e-13 | -0.061143 | -0.010925 | 0.06216 | -0.010914 | 0.051753 | -0.013124 | 0.0042022 | 0.0013034 | -0.0019442 | 0.04385 | -0.001908 | -121.2667 | -3.84 | -121.603 | 0.061284 | 0.087359 | 0.16028 | -121.7983 | -108.4365 | -65.5759 | -113.8464 | -0.002483 | 0.096121 | 0.12222 | -122.0614 | -0.046941 | -0.048579 | 0.48469 | 0.14844 | 0.19538 | -0.022504 | 0.050417 | -0.31002 | -0.11235 | 13.3149 | 7.905 | 8.215 | -0.013742 | 0.012353 | 121.8127 | 121.8388 | 121.9117 | 117.9114 | -121.9082 | 121.7489 | 121.8475 | 121.8736 | 56.1755 | -122.1713
2305.6719 | 122.0215 | -121.7377 | 0.10071 | 1.4211e-13 | -0.061143 | -0.010498 | 0.062588 | -0.011555 | 0.052181 | -0.0054937 | 0.004416 | 0.001517 | -0.0021578 | 0.044064 | -0.0014806 | -121.2713 | -3.8767 | -121.5984 | 0.061284 | 0.091937 | 0.16028 | -121.8029 | -108.2076 | -64.9624 | -113.764 | -0.002483 | 0.096121 | 0.12222 | -122.0706 | -0.065253 | -0.039424 | 0.46638 | 0.13929 | 0.20454 | -0.008771 | 0.059572 | -0.33291 | -0.10319 | 13.5301 | 7.9736 | 8.3065 | -0.004587 | 0.021508 | 121.799 | 121.8296 | 121.898 | 117.861 | -121.9036 | 121.7352 | 121.8338 | 121.8599 | 56.7753 | -122.1713
2307.4375 | 122.0764 | -121.7194 | 0.086975 | 1.4211e-13 | -0.06157 | -0.010498 | 0.06216 | -0.010914 | 0.051967 | -0.0054937 | 0.004416 | 0.001517 | -0.0019442 | 0.044277 | -0.0016942 | -121.2576 | -3.9087 | -121.5938 | 0.065863 | 0.091937 | 0.16028 | -121.7938 | -108.1847 | -64.3351 | -113.6999 | -0.002483 | 0.096121 | 0.12222 | -122.0614 | -0.074406 | -0.021112 | 0.4618 | 0.12555 | 0.19996 | 0.004962 | 0.073305 | -0.34206 | -0.089458 | 13.5347 | 8.0194 | 8.3615 | 0.009146 | 0.035241 | 121.7852 | 121.8113 | 121.8796 | 117.8106 | -121.8807 | 121.7169 | 121.8155 | 121.8416 | 57.3843 | -122.1484
2309.1406 | 122.0306 | -121.7331 | 0.11444 | 1.4211e-13 | -0.061143 | -0.010498 | 0.06216 | -0.0107 | 0.051967 | -0.013124 | 0.0042022 | 0.0017306 | -0.0021578 | 0.04385 | -0.00083958 | -121.2576 | -3.9362 | -121.5846 | 0.07502 | 0.08278 | 0.16028 | -121.7938 | -107.8093 | -63.401 | -113.6084 | -0.002483 | 0.086964 | 0.12679 | -122.0706 | -0.060673 | -0.039421 | 0.47554 | 0.14844 | 0.20912 | -0.031661 | 0.045839 | -0.33749 | -0.11692 | 13.9238 | 8.1247 | 8.4622 | -0.027477 | 0.012353 | 121.8081 | 121.8159 | 121.8934 | 117.7969 | -121.9082 | 121.7306 | 121.8201 | 121.8599 | 58.3321 | -122.185
2310.8906 | 121.9162 | -121.7606 | 0.14191 | 1.4211e-13 | -0.061356 | -0.010498 | 0.061947 | -0.011128 | 0.052181 | -0.020755 | 0.0042022 | 0.0013034 | -0.0017306 | 0.044491 | -0.00062598 | -121.253 | -3.9637 | -121.5846 | 0.065863 | 0.087359 | 0.16028 | -121.78 | -107.6719 | -62.8104 | -113.5214 | 0.002095 | 0.1007 | 0.13137 | -122.0568 | -0.01947 | -0.076044 | 0.50758 | 0.17591 | 0.19538 | -0.054548 | 0.018373 | -0.29628 | -0.13981 | 14.0887 | 8.2392 | 8.5355 | -0.041207 | -0.010534 | 121.8264 | 121.8479 | 121.9208 | 117.7969 | -121.9219 | 121.7627 | 121.8613 | 121.8919 | 58.9502 | -122.1987
2312.6562 | 122.0306 | -121.6965 | 0.13733 | 1.4211e-13 | -0.061143 | -0.010498 | 0.06216 | -0.011128 | 0.051967 | -0.013124 | 0.0046296 | 0.001517 | -0.0019442 | 0.044064 | 0.024158 | -121.2438 | -3.9866 | -121.5755 | 0.070441 | 0.1011 | 0.16944 | -121.8441 | -107.443 | -62.0595 | -113.4298 | 0.011252 | 0.10528 | 0.14053 | -122.0294 | -0.14766 | -0.066888 | 0.45265 | 0.12098 | 0.26864 | -0.036234 | 0.032109 | -0.3329 | -0.12608 | 14.2535 | 8.2667 | 8.5996 | -0.03205 | 0.003201 | 121.7669 | 121.7976 | 121.8659 | 117.7099 | -121.9815 | 121.7077 | 121.8018 | 121.837 | 59.637 | -122.1667
2314.3594 | 122.0306 | -121.4951 | 0.16479 | 1.4211e-13 | -0.061356 | -0.010498 | 0.06216 | -0.011341 | 0.051967 | -0.013124 | 0.004416 | 0.001517 | -0.0017306 | 0.045132 | 0.52005 | -120.9462 | -4.0003 | -121.2825 | 0.30852 | 0.35294 | 0.42584 | -121.5557 | -106.4311 | -28.7906 | -112.2302 | 0.27223 | 0.35252 | 0.39235 | -121.599 | -0.060606 | 0.14372 | 0.54883 | 0.21257 | 0.27318 | 0.18814 | 0.26104 | -0.1039 | 0.10743 | 15.064 | 9.2649 | 9.3688 | 0.18773 | 0.22756 | 121.8036 | 121.848 | 121.9209 | 117.4948 | -121.7205 | 121.7673 | 121.8476 | 121.8874 | 92.7045 | -121.7638
2316.1094 | 121.9254 | -121.7148 | 0.14191 | 1.4211e-13 | -0.060929 | -0.010712 | 0.061947 | -0.011128 | 0.05154 | -0.0054937 | 0.00014315 | -0.0038244 | -0.0060034 | 0.038081 | -0.00083958 | -121.2301 | -4.0461 | -121.5709 | 0.07502 | 0.08278 | 0.16028 | -121.78 | -0.18668 | -0.16905 | -0.28529 | -0.002483 | 0.091543 | 0.12679 | -0.36104 | -0.065246 | -0.066887 | 0.4847 | 0.14387 | 0.20911 | -0.059127 | 0.018373 | 121.3537 | -0.14439 | 121.5281 | 121.4295 | 0.075751 | -0.050364 | -0.015113 | 121.7898 | 121.7976 | 121.8751 | 117.6687 | -121.9219 | 121.7123 | 121.8063 | 121.8416 | 121.5457 | -0.50294
2317.8594 | 121.9437 | -121.7377 | 0.14191 | 1.4211e-13 | -0.061143 | -0.010712 | 0.06216 | -0.010487 | 0.051753 | -0.013124 | -0.00028425 | -0.0038244 | -0.0055762 | 0.038294 | -0.00041238 | -121.2438 | -4.0827 | -121.5801 | 0.084176 | 0.087359 | 0.14655 | -121.7755 | -0.20042 | -0.21026 | -0.29902 | -0.007062 | 0.096121 | 0.13137 | -0.42972 | -0.03778 | -0.057731 | 0.49385 | 0.1576 | 0.19538 | -0.054548 | 0.004638 | 121.308 | -0.14897 | 121.5373 | 121.4386 | 0.1307 | -0.045786 | -0.010534 | 121.8218 | 121.825 | 121.8842 | 117.655 | -121.9174 | 121.7306 | 121.8338 | 121.869 | 121.5274 | -0.57163
2319.5469 | 122.0123 | -121.7194 | 0.11444 | 1.4211e-13 | -0.061143 | -0.010712 | 0.062374 | -0.011341 | 0.051967 | -0.013124 | -0.00028425 | -0.0038244 | -0.0057898 | 0.038294 | -0.00083958 | -121.2438 | -4.1102 | -121.5755 | 0.07502 | 0.08278 | 0.15112 | -121.7755 | -0.49345 | -0.38425 | -0.61953 | -0.002483 | 0.096121 | 0.12222 | -0.7594 | -0.056091 | -0.039421 | 0.47554 | 0.14387 | 0.19996 | -0.031661 | 0.036682 | 120.96 | -0.11692 | 121.2259 | 121.0998 | 0.13986 | -0.01832 | 0.007775 | 121.7944 | 121.8021 | 121.8705 | 117.6092 | -121.8899 | 121.7169 | 121.8155 | 121.8416 | 121.3351 | -0.87384
2321.2344 | 121.875 | -121.7239 | 0.14191 | 1.4211e-13 | -0.061143 | -0.010498 | 0.061947 | -0.011128 | 0.05154 | -0.013124 | 0.00014315 | -0.0033972 | -0.0060034 | 0.037653 | -0.00041238 | -121.2255 | -4.1468 | -121.5526 | 0.079598 | 0.1011 | 0.17402 | -121.7846 | -0.45225 | -0.36594 | -0.57832 | 0.011252 | 0.11901 | 0.14053 | -0.71361 | -0.06067 | -0.062309 | 0.49843 | 0.17134 | 0.23201 | -0.040812 | 0.032109 | 121.0103 | -0.13065 | 121.2717 | 121.1456 | 0.13528 | -0.022893 | -0.001377 | 121.8035 | 121.825 | 121.898 | 117.5771 | -121.9265 | 121.7352 | 121.843 | 121.8645 | 121.358 | -0.85551
2323 | 121.9849 | -121.7468 | 0.14648 | 1.4211e-13 | -0.061356 | -0.010712 | 0.06216 | -0.011128 | 0.051753 | -0.0054937 | -0.00049785 | -0.0036108 | -0.0060034 | 0.038294 | -0.0010534 | -121.2347 | -4.1789 | -121.5618 | 0.061284 | 0.087359 | 0.16028 | -121.7938 | -0.42935 | -0.35678 | -0.55543 | 0.006674 | 0.096121 | 0.13137 | -0.68613 | -0.04694 | -0.0852 | 0.51216 | 0.18507 | 0.23201 | -0.059125 | 0.013796 | 121.0607 | -0.13981 | 121.3175 | 121.1914 | 0.1307 | -0.050363 | -0.015111 | 121.8081 | 121.8342 | 121.9071 | 117.568 | -121.9403 | 121.7535 | 121.8429 | 121.8782 | 121.39 | -0.83262
2324.7031 | 121.9299 | -121.701 | 0.10529 | 1.4211e-13 | -0.061143 | -0.010925 | 0.062374 | -0.011128 | 0.051753 | -0.020755 | -0.00049785 | -0.0038244 | -0.0060034 | 0.037867 | -0.00062598 | -121.2072 | -4.2155 | -121.5526 | 0.07502 | 0.1011 | 0.17402 | -121.8304 | -0.40646 | -0.33847 | -0.52338 | 0.020409 | 0.10986 | 0.14969 | -0.64492 | -0.12935 | -0.030266 | 0.49386 | 0.14845 | 0.2778 | -0.004191 | 0.06873 | 121.0561 | -0.084877 | 121.2946 | 121.1777 | 0.12155 | 0.004571 | 0.044401 | 121.7761 | 121.8021 | 121.8751 | 117.4856 | -121.9357 | 121.7215 | 121.8109 | 121.8507 | 121.3626 | -0.75021
2326.4531 | 121.9254 | -121.7422 | 0.13275 | 1.4211e-13 | -0.061143 | -0.010925 | 0.061947 | -0.011128 | 0.051753 | -0.013124 | -7.0448e-05 | -0.0036108 | -0.0057898 | 0.038294 | -0.00062598 | -121.2347 | -4.2475 | -121.5618 | 0.056706 | 0.087359 | 0.16028 | -121.7709 | -0.44309 | -0.37052 | -0.57374 | -0.007062 | 0.096121 | 0.12679 | -0.70445 | -0.028623 | -0.076045 | 0.50759 | 0.18049 | 0.20911 | -0.045392 | 0.027529 | 121.0378 | -0.13981 | 121.2992 | 121.1685 | 0.1307 | -0.03663 | -0.005957 | 121.799 | 121.8296 | 121.9025 | 117.4947 | -121.9036 | 121.7352 | 121.8384 | 121.869 | 121.3717 | -0.8372
2328.2031 | 122.0169 | -121.669 | 0.10071 | 1.4211e-13 | -0.061356 | -0.010925 | 0.06216 | -0.011555 | 0.051753 | -0.0054937 | -0.00049785 | -0.0036108 | -0.0053626 | 0.038081 | -0.00062598 | -120.8501 | -4.2704 | -121.1772 | 0.38635 | 0.43994 | 0.50368 | -121.4046 | -0.25994 | -0.21026 | -0.3906 | 0.3409 | 0.4441 | 0.47477 | -0.53045 | 0.26445 | 0.28564 | 0.81893 | 0.49182 | 0.22738 | 0.33923 | 0.40297 | 121.1386 | 0.2402 | 121.4091 | 121.2784 | 0.13986 | 0.34339 | 0.37406 | 122.0554 | 122.1089 | 122.1727 | 117.3986 | -121.5053 | 122.0099 | 122.1131 | 122.1438 | 121.4587 | -0.63116
2329.9688 | 121.962 | -121.7148 | 0.10529 | 1.4211e-13 | -0.06157 | -0.011139 | 0.062374 | -0.011128 | 0.051753 | -0.013124 | -0.00049785 | -0.004038 | -0.0057898 | 0.038294 | -0.00083958 | -121.2484 | -4.3116 | -121.5663 | 0.038393 | 0.064464 | 0.13739 | -121.7846 | -0.34693 | -0.26521 | -0.46386 | -0.016219 | 0.082386 | 0.1039 | -0.59456 | -0.069825 | -0.066893 | 0.46639 | 0.14845 | 0.21827 | -0.040822 | 0.032101 | 121.1202 | -0.12151 | 121.3678 | 121.2509 | 0.1307 | -0.0229 | -0.001385 | 121.7532 | 121.7792 | 121.8522 | 117.4031 | -121.8899 | 121.6986 | 121.7972 | 121.8187 | 121.4496 | -0.69984
2331.6562 | 121.9757 | -121.7331 | 0.086975 | 1.4211e-13 | -0.06157 | -0.010712 | 0.061733 | -0.010914 | 0.051753 | -0.0054937 | -7.0448e-05 | -0.0038244 | -0.0053626 | 0.038294 | -0.0010534 | -121.2392 | -4.3391 | -121.5663 | 0.038393 | 0.064464 | 0.14197 | -121.78 | -0.32862 | -0.26063 | -0.44554 | -0.016219 | 0.077807 | 0.1039 | -0.58082 | -0.046936 | -0.048582 | 0.49385 | 0.16676 | 0.21369 | -0.022511 | 0.054991 | 121.1523 | -0.10319 | 121.4045 | 121.2876 | 0.13528 | -0.009168 | 0.016926 | 121.7715 | 121.7976 | 121.8751 | 117.394 | -121.867 | 121.7169 | 121.8109 | 121.837 | 121.4725 | -0.6678
2333.4062 | 122.0444 | -121.7148 | 0.07782 | 1.4211e-13 | -0.06157 | -0.010925 | 0.061733 | -0.010914 | 0.051753 | -0.0054937 | -7.0448e-05 | -0.0038244 | -0.0055762 | 0.038294 | -0.00083958 | -121.2484 | -4.3803 | -121.5663 | 0.042971 | 0.064464 | 0.13281 | -121.7846 | -0.3103 | -0.25147 | -0.42265 | -0.016219 | 0.077807 | 0.1039 | -0.55793 | -0.069825 | -0.034849 | 0.46639 | 0.14845 | 0.21827 | -0.013356 | 0.054989 | 121.1569 | -0.094039 | 121.4045 | 121.2921 | 0.13528 | -1.3e-05 | 0.026081 | 121.7578 | 121.7792 | 121.8476 | 117.3345 | -121.8624 | 121.6986 | 121.7926 | 121.8187 | 121.4633 | -0.63575
2335.1562 | 121.9986 | -121.7331 | 0.064087 | 1.4211e-13 | -0.061356 | -0.010925 | 0.062374 | -0.011341 | 0.051753 | -0.0054937 | -0.00028425 | -0.0038244 | -0.0055762 | 0.038294 | -0.0010534 | -121.2347 | -4.4169 | -121.5663 | 0.047549 | 0.073622 | 0.14197 | -121.7938 | -0.15921 | -0.1599 | -0.25781 | -0.020797 | 0.082386 | 0.10848 | -0.37935 | -0.060673 | -0.016538 | 0.49843 | 0.16676 | 0.22743 | 0.009535 | 0.077879 | 121.3537 | -0.084884 | 121.5739 | 121.4753 | 0.12154 | 0.018299 | 0.044393 | 121.7806 | 121.8067 | 121.8751 | 117.3161 | -121.8579 | 121.7123 | 121.8155 | 121.8416 | 121.5732 | -0.44344
2336.9219 | 121.8658 | -121.7651 | 0.10986 | 1.4211e-13 | -0.06157 | -0.011139 | 0.06216 | -0.010914 | 0.051753 | -0.013124 | -0.00028425 | -0.0036108 | -0.0057898 | 0.038722 | -0.00083958 | -121.2438 | -4.4536 | -121.5709 | 0.047549 | 0.064464 | 0.13739 | -121.7709 | -0.15463 | -0.1599 | -0.24408 | -0.025376 | 0.082386 | 0.10848 | -0.37935 | -0.005735 | -0.062314 | 0.52132 | 0.19422 | 0.19996 | -0.045399 | 0.027524 | 121.3858 | -0.13524 | 121.6105 | 121.5211 | 0.13528 | -0.027477 | -0.001383 | 121.8127 | 121.8296 | 121.9025 | 117.3116 | -121.8807 | 121.7398 | 121.8475 | 121.8736 | 121.6052 | -0.48922
2338.6094 | 121.9345 | -121.7468 | 0.11444 | 1.4211e-13 | -0.061784 | -0.010712 | 0.06216 | -0.011341 | 0.051753 | -0.0054937 | -0.00028425 | -0.0036108 | -0.0055762 | 0.038508 | -0.0010534 | -121.2438 | -4.4902 | -121.5618 | 0.042971 | 0.069043 | 0.13739 | -121.78 | -0.072212 | -0.11411 | -0.17082 | -0.01164 | 0.077807 | 0.1039 | -0.29236 | -0.033203 | -0.07147 | 0.50301 | 0.18507 | 0.21827 | -0.045398 | 0.022946 | 121.4545 | -0.12608 | 121.6746 | 121.576 | 0.12154 | -0.036634 | -0.01054 | 121.7898 | 121.8159 | 121.8842 | 117.2566 | -121.8945 | 121.7352 | 121.8246 | 121.8507 | 121.6327 | -0.4068
2340.3594 | 121.962 | -121.7514 | 0.09613 | 1.4211e-13 | -0.061784 | -0.011139 | 0.061947 | -0.011341 | 0.051326 | -0.0054937 | -7.0448e-05 | -0.0038244 | -0.0057898 | 0.038294 | -0.00062598 | -121.2255 | -4.5177 | -121.5618 | 0.042971 | 0.064464 | 0.13739 | -121.7709 | -0.19584 | -0.16905 | -0.30818 | -0.016219 | 0.082386 | 0.10848 | -0.43888 | -0.019468 | -0.053159 | 0.5259 | 0.18965 | 0.20911 | -0.031666 | 0.041257 | 121.3125 | -0.11235 | 121.5556 | 121.4432 | 0.1307 | -0.013744 | 0.01235 | 121.7944 | 121.8159 | 121.8888 | 117.2337 | -121.867 | 121.7352 | 121.8338 | 121.8599 | 121.5824 | -0.53501
2342.1094 | 121.9254 | -121.6919 | 0.10529 | 1.4211e-13 | -0.061784 | -0.010925 | 0.062374 | -0.010914 | 0.05154 | -0.013124 | 0.00014315 | -0.0033972 | -0.0057898 | 0.038508 | -0.00083958 | -121.1843 | -4.5451 | -121.4977 | 0.042971 | 0.069043 | 0.12823 | -121.7571 | 0.001048 | -0.008798 | -0.10214 | -0.025376 | 0.073228 | 0.1039 | -0.22367 | -0.06524 | -0.062315 | 0.50759 | 0.19423 | 0.25947 | -0.036243 | 0.022944 | 121.4682 | -0.13066 | 121.6929 | 121.5898 | 0.12154 | -0.032058 | -0.001385 | 121.7349 | 121.7609 | 121.8201 | 117.1467 | -121.8624 | 121.6665 | 121.7651 | 121.7958 | 121.6831 | -0.32896
2343.7969 | 121.9711 | -121.8109 | 0.10529 | 1.4211e-13 | -0.06157 | -0.011139 | 0.062374 | -0.011128 | 0.052181 | -0.013124 | -0.00049785 | -0.0038244 | -0.0062172 | 0.038722 | -0.0010534 | -121.3491 | -4.5909 | -121.6396 | 0.038393 | 0.050727 | 0.13739 | -121.835 | 0.005626 | -0.017956 | -0.10214 | -0.039111 | 0.06865 | 0.099323 | -0.23741 | -0.024064 | -0.066893 | 0.46179 | 0.17132 | 0.19539 | -0.054559 | 0.032101 | 121.5735 | -0.1444 | 121.8165 | 121.7088 | 0.13527 | -0.036636 | -0.005963 | 121.8493 | 121.8616 | 121.9483 | 117.22 | -121.9403 | 121.7718 | 121.8796 | 121.9102 | 121.793 | -0.3427
2345.5625 | 122.1039 | -121.7926 | 0.086975 | 1.4211e-13 | -0.06157 | -0.010498 | 0.062374 | -0.011128 | 0.051967 | -0.0054937 | -0.00049785 | -0.0036108 | -0.0053626 | 0.038294 | -0.00083958 | -121.3812 | -4.6367 | -121.6579 | 0.038393 | 0.055306 | 0.12823 | -121.8716 | 0.005626 | -0.013377 | -0.097559 | -0.034533 | 0.064071 | 0.1039 | -0.22367 | -0.079005 | -0.048582 | 0.41143 | 0.1347 | 0.21371 | -0.031669 | 0.041255 | 121.5689 | -0.12151 | 121.7982 | 121.695 | 0.12611 | -0.022904 | 0.016926 | 121.831 | 121.8479 | 121.9208 | 117.1559 | -121.9586 | 121.7581 | 121.8567 | 121.8965 | 121.7792 | -0.31065
2347.25 | 122.1405 | -121.7972 | 0.07782 | 1.4211e-13 | -0.061784 | -0.011353 | 0.06216 | -0.011128 | 0.051753 | -0.020755 | -0.00028425 | -0.0036108 | -0.0057898 | 0.038508 | -0.00083958 | -121.3812 | -4.6688 | -121.6854 | 0.038393 | 0.059885 | 0.13281 | -121.8899 | -0.031003 | -0.031692 | -0.13877 | -0.029954 | 0.059493 | 0.1039 | -0.26946 | -0.092744 | -0.039427 | 0.41601 | 0.11181 | 0.20455 | -0.017935 | 0.054989 | 121.5277 | -0.10777 | 121.7662 | 121.6584 | 0.13069 | -0.018327 | 0.026081 | 121.8356 | 121.8571 | 121.93 | 117.1284 | -121.9677 | 121.7672 | 121.8567 | 121.9011 | 121.7655 | -0.34728
2349 | 122.1451 | -121.8155 | 0.086975 | 1.4211e-13 | -0.061356 | -0.010925 | 0.061947 | -0.010914 | 0.051753 | -0.0054937 | -7.0448e-05 | -0.004038 | -0.0055762 | 0.038722 | -0.001267 | -121.4041 | -4.71 | -121.6808 | 0.033814 | 0.055306 | 0.12823 | -121.8991 | -0.040161 | -0.036271 | -0.15708 | -0.029954 | 0.054914 | 0.099323 | -0.27862 | -0.08359 | -0.053161 | 0.41143 | 0.1347 | 0.21829 | -0.031669 | 0.041255 | 121.5369 | -0.11693 | 121.7753 | 121.6584 | 0.12154 | -0.032061 | 0.012348 | 121.8493 | 121.8708 | 121.9437 | 117.1055 | -121.9861 | 121.7855 | 121.8704 | 121.9148 | 121.7792 | -0.36559
2350.7656 | 122.0581 | -121.8613 | 0.07782 | 1.4211e-13 | -0.061356 | -0.010712 | 0.062374 | -0.011128 | 0.051967 | -0.020755 | -7.0448e-05 | -0.0036108 | -0.0057898 | 0.038935 | -0.00083958 | -121.4086 | -4.7512 | -121.6991 | 0.038393 | 0.059885 | 0.13281 | -121.9082 | -0.00811 | -0.022535 | -0.12045 | -0.034533 | 0.064071 | 0.094744 | -0.24199 | -0.046972 | -0.039427 | 0.45262 | 0.16216 | 0.20913 | -0.017935 | 0.054989 | 121.6193 | -0.11235 | 121.8532 | 121.7408 | 0.12154 | -0.013749 | 0.016924 | 121.8997 | 121.9212 | 121.9941 | 117.1101 | -121.9861 | 121.8267 | 121.9253 | 121.956 | 121.8387 | -0.31981
2352.5156 | 122.1268 | -121.843 | 0.091553 | 1.4211e-13 | -0.06157 | -0.010925 | 0.061733 | -0.011128 | 0.051967 | 0.0021363 | -0.00028425 | -0.0033972 | -0.0055762 | 0.038722 | -0.001267 | -121.4178 | -4.7832 | -121.6945 | 0.029236 | 0.050727 | 0.13739 | -121.9174 | 0.005626 | -0.017956 | -0.092981 | -0.04369 | 0.059493 | 0.099323 | -0.2191 | -0.07444 | -0.062317 | 0.42516 | 0.14843 | 0.22287 | -0.040826 | 0.045834 | 121.6239 | -0.13524 | 121.8486 | 121.75 | 0.12611 | -0.03206 | 0.00777 | 121.8722 | 121.8937 | 121.9803 | 117.0597 | -122.0089 | 121.7993 | 121.9025 | 121.9423 | 121.825 | -0.31065
2354.2656 | 122.1588 | -121.8292 | 0.082397 | 1.4211e-13 | -0.061784 | -0.010925 | 0.06216 | -0.011128 | 0.052181 | -0.0054937 | -7.0448e-05 | -0.0036108 | -0.0057898 | 0.038508 | -0.00083958 | -121.4224 | -4.8199 | -121.7083 | 0.038393 | 0.064464 | 0.12365 | -121.9174 | -0.026425 | -0.031692 | -0.13419 | -0.029954 | 0.06865 | 0.1039 | -0.2603 | -0.088173 | -0.044004 | 0.40685 | 0.12096 | 0.20913 | -0.017933 | 0.041255 | 121.5689 | -0.11235 | 121.8028 | 121.695 | 0.12611 | -0.013747 | 0.021504 | 121.8676 | 121.8937 | 121.9529 | 117.0094 | -121.9998 | 121.7993 | 121.8979 | 121.9331 | 121.7975 | -0.3427
2356.0312 | 122.1451 | -121.8704 | 0.07782 | 1.4211e-13 | -0.06157 | -0.010925 | 0.062374 | -0.010914 | 0.05154 | -0.0054937 | -0.00028425 | -0.0033972 | -0.0060034 | 0.038508 | -0.0010534 | -121.4224 | -4.8702 | -121.7083 | 0.038393 | 0.059885 | 0.12365 | -121.922 | -0.017267 | -0.031692 | -0.11587 | -0.025376 | 0.064071 | 0.1039 | -0.24199 | -0.051554 | -0.039427 | 0.44805 | 0.16216 | 0.21371 | -0.017935 | 0.045832 | 121.6284 | -0.1032 | 121.8532 | 121.7545 | 0.12612 | -0.013749 | 0.026081 | 121.9088 | 121.9303 | 121.9941 | 117.0002 | -121.9998 | 121.845 | 121.9345 | 121.9743 | 121.8387 | -0.31981
2357.7344 | 122.0398 | -121.9116 | 0.1236 | 1.4211e-13 | -0.061997 | -0.010712 | 0.062374 | -0.011128 | 0.05154 | -0.0054937 | -7.0448e-05 | -0.0036108 | -0.0055762 | 0.038722 | -0.0010534 | -121.4361 | -4.9114 | -121.7174 | 0.038393 | 0.064464 | 0.13739 | -121.9174 | -0.012689 | -0.027113 | -0.13419 | -0.034533 | 0.059493 | 0.094744 | -0.24657 | -0.005776 | -0.085203 | 0.47551 | 0.1942 | 0.19998 | -0.059132 | 0.013791 | 121.6651 | -0.15813 | 121.8989 | 121.7774 | 0.11238 | -0.064103 | -0.028852 | 121.95 | 121.9761 | 122.049 | 117.0002 | -122.041 | 121.8771 | 121.9711 | 122.0064 | 121.8845 | -0.37016
2359.4844 | 122.2092 | -121.8613 | 0.059509 | 1.4211e-13 | -0.061997 | -0.011353 | 0.062374 | -0.011341 | 0.051753 | -0.020755 | -0.00028425 | -0.0038244 | -0.0057898 | 0.038294 | -0.00083958 | -121.4361 | -4.9526 | -121.7174 | 0.038393 | 0.059885 | 0.12823 | -121.9357 | 0.014784 | -0.017956 | -0.097559 | -0.029954 | 0.064071 | 0.094744 | -0.2191 | -0.074446 | -0.021116 | 0.42516 | 0.14385 | 0.21829 | 0.000376 | 0.068721 | 121.6422 | -0.089463 | 121.8761 | 121.7637 | 0.12154 | 0.004562 | 0.035235 | 121.8997 | 121.9212 | 121.9895 | 116.9086 | -121.9952 | 121.8313 | 121.9253 | 121.956 | 121.8433 | -0.2786
2361.1719 | 122.0673 | -121.9116 | 0.091553 | 1.4211e-13 | -0.061997 | -0.010712 | 0.06216 | -0.0107 | 0.051753 | -0.0054937 | -0.00049785 | -0.004038 | -0.0057898 | 0.038508 | -0.0010534 | -121.4407 | -4.9984 | -121.7312 | 0.029236 | 0.064464 | 0.13281 | -121.9357 | 0.001048 | -0.017956 | -0.1113 | -0.025376 | 0.064071 | 0.094744 | -0.23741 | -0.024092 | -0.062317 | 0.47093 | 0.18047 | 0.20456 | -0.027089 | 0.041256 | 121.6742 | -0.11693 | 121.9127 | 121.8003 | 0.12611 | -0.027482 | 0.003191 | 121.9409 | 121.9761 | 122.0444 | 116.9132 | -122.0273 | 121.8862 | 121.9757 | 122.0064 | 121.8937 | -0.32896
2362.9375 | 122.0901 | -121.8933 | 0.11444 | 1.4211e-13 | -0.061356 | -0.011353 | 0.06216 | -0.011341 | 0.05154 | -0.0054937 | -7.0448e-05 | -0.0038244 | -0.0057898 | 0.038508 | -0.001267 | -121.4453 | -5.0442 | -121.7312 | 0.038393 | 0.059885 | 0.13281 | -121.9403 | 0.001048 | -0.027113 | -0.10672 | -0.034533 | 0.064071 | 0.099323 | -0.23283 | -0.046981 | -0.076048 | 0.44804 | 0.16216 | 0.20914 | -0.054556 | 0.018368 | 121.6605 | -0.14897 | 121.8944 | 121.7866 | 0.12611 | -0.05037 | -0.015118 | 121.9317 | 121.9532 | 122.0261 | 116.8491 | -122.0547 | 121.8588 | 121.9574 | 121.9926 | 121.8662 | -0.34727
2364.6875 | 122.1451 | -121.9116 | 0.07782 | 1.4211e-13 | -0.061784 | -0.011139 | 0.06216 | -0.011128 | 0.051967 | -0.0054937 | -0.00028425 | -0.0036108 | -0.0057898 | 0.038722 | -0.00083958 | -121.4453 | -5.0946 | -121.7312 | 0.038393 | 0.059885 | 0.13281 | -121.9449 | 0.001048 | -0.022535 | -0.11587 | -0.025376 | 0.06865 | 0.099323 | -0.23283 | -0.03325 | -0.039427 | 0.46635 | 0.18047 | 0.21372 | -0.017935 | 0.054989 | 121.6788 | -0.1032 | 121.9127 | 121.7957 | 0.11696 | -0.00917 | 0.021503 | 121.95 | 121.9715 | 122.0444 | 116.817 | -122.0227 | 121.8862 | 121.9803 | 122.0109 | 121.8891 | -0.31065
2366.375 | 122.1405 | -121.9025 | 0.07782 | 1.4211e-13 | -0.061997 | -0.010925 | 0.06216 | -0.011341 | 0.051753 | -0.013124 | -0.00049785 | -0.0036108 | -0.0055762 | 0.038722 | -0.00083958 | -121.4498 | -5.1312 | -121.7312 | 0.029236 | 0.064464 | 0.13739 | -121.9403 | 0.001048 | -0.027113 | -0.10672 | -0.025376 | 0.064071 | 0.094744 | -0.22367 | -0.037826 | -0.048584 | 0.45262 | 0.17131 | 0.20914 | -0.013356 | 0.059567 | 121.6788 | -0.1032 | 121.9035 | 121.7957 | 0.11696 | -0.013749 | 0.016924 | 121.9317 | 121.9669 | 122.0399 | 116.7713 | -122.0181 | 121.8771 | 121.9665 | 121.9972 | 121.8754 | -0.30149
2368.125 | 122.1771 | -121.8704 | 0.073242 | 1.4211e-13 | -0.061784 | -0.011139 | 0.062374 | -0.011128 | 0.051753 | -0.0054937 | -7.0448e-05 | -0.0036108 | -0.0060034 | 0.039363 | -0.00083958 | -121.4498 | -5.1861 | -121.7403 | 0.029236 | 0.064464 | 0.13281 | -121.9494 | 0.001048 | -0.017956 | -0.10672 | -0.039111 | 0.064071 | 0.094744 | -0.23283 | -0.079028 | -0.044006 | 0.42057 | 0.13011 | 0.20914 | -0.008778 | 0.059567 | 121.6376 | -0.11235 | 121.8715 | 121.7637 | 0.12611 | -0.009171 | 0.021502 | 121.8997 | 121.9349 | 122.0032 | 116.6843 | -122.0227 | 121.8313 | 121.9345 | 121.9652 | 121.8525 | -0.30607
2369.875 | 122.0764 | -121.962 | 0.10529 | 1.4211e-13 | -0.062211 | -0.010925 | 0.06216 | -0.011341 | 0.051753 | -0.013124 | -0.00028425 | -0.004038 | -0.0057898 | 0.039149 | -0.001267 | -121.459 | -5.2411 | -121.7403 | 0.033814 | 0.064464 | 0.13281 | -121.954 | 0.005626 | -0.017956 | -0.1113 | -0.029954 | 0.06865 | 0.099323 | -0.23283 | 0.007946 | -0.071472 | 0.50297 | 0.22166 | 0.21372 | -0.040822 | 0.027523 | 121.7291 | -0.13524 | 121.9676 | 121.8507 | 0.12154 | -0.036636 | -0.005963 | 121.9958 | 122.0264 | 122.0948 | 116.7209 | -122.0593 | 121.932 | 122.0306 | 122.0613 | 121.944 | -0.33812
2371.5625 | 122.113 | -121.9162 | 0.09613 | 1.4211e-13 | -0.061997 | -0.011139 | 0.062374 | -0.011341 | 0.05154 | -0.013124 | -0.00028425 | -0.0038244 | -0.0057898 | 0.038722 | -0.00083958 | -121.4636 | -5.2869 | -121.7357 | 0.042971 | 0.059885 | 0.13739 | -121.9586 | 0.001048 | -0.017956 | -0.10672 | -0.029954 | 0.06865 | 0.094744 | -0.22825 | -0.042408 | -0.053159 | 0.45262 | 0.18047 | 0.22288 | -0.036245 | 0.041257 | 121.6879 | -0.12608 | 121.9172 | 121.8095 | 0.12154 | -0.02748 | -0.001386 | 121.9592 | 121.9761 | 122.0536 | 116.6293 | -122.0547 | 121.8862 | 121.9848 | 122.0109 | 121.8982 | -0.32438
2373.3125 | 122.2 | -121.9162 | 0.068665 | 1.4211e-13 | -0.061997 | -0.010925 | 0.06216 | -0.0107 | 0.05154 | -0.013124 | -0.00049785 | -0.0038244 | -0.0057898 | 0.039149 | -0.001267 | -121.4544 | -5.3281 | -121.7449 | 0.033814 | 0.064464 | 0.12365 | -121.9586 | -0.003531 | -0.022535 | -0.11587 | -0.025376 | 0.064071 | 0.094744 | -0.23283 | -0.042408 | -0.034851 | 0.46177 | 0.17131 | 0.21372 | -0.004201 | 0.054987 | 121.6834 | -0.094041 | 121.9127 | 121.8003 | 0.11696 | -0.004594 | 0.026079 | 121.95 | 121.9807 | 122.0399 | 116.5881 | -122.0273 | 121.8908 | 121.9803 | 122.0109 | 121.8937 | -0.3015
2375.0781 | 122.0764 | -121.9482 | 0.11444 | 1.4211e-13 | -0.062211 | -0.010925 | 0.06216 | -0.011341 | 0.05154 | -0.020755 | -0.00028425 | -0.0038244 | -0.0060034 | 0.038935 | -0.00083958 | -121.4636 | -5.383 | -121.7449 | 0.042971 | 0.059885 | 0.13281 | -121.9632 | -0.031003 | -0.022535 | -0.13877 | -0.029954 | 0.073228 | 0.094744 | -0.2603 | -0.014944 | -0.07147 | 0.48466 | 0.20335 | 0.2183 | -0.054556 | 0.018368 | 121.6879 | -0.14439 | 121.9172 | 121.8095 | 0.12154 | -0.041213 | -0.019697 | 121.9912 | 122.0081 | 122.0811 | 116.5652 | -122.0776 | 121.9183 | 122.0215 | 122.043 | 121.9257 | -0.37474
2376.7656 | 122.0718 | -121.9345 | 0.09613 | 1.4211e-13 | -0.062211 | -0.011139 | 0.061947 | -0.011341 | 0.05154 | -0.013124 | -0.00028425 | -0.0038244 | -0.0057898 | 0.038935 | -0.001267 | -121.4636 | -5.4288 | -121.7495 | 0.033814 | 0.064464 | 0.13281 | -121.9678 | -0.031003 | -0.022535 | -0.14335 | -0.029954 | 0.06865 | 0.094744 | -0.26488 | -0.033256 | -0.062316 | 0.47093 | 0.18504 | 0.2183 | -0.031666 | 0.036679 | 121.6696 | -0.12608 | 121.9035 | 121.7912 | 0.12154 | -0.02748 | -0.001386 | 121.9683 | 121.999 | 122.0673 | 116.5057 | -122.0639 | 121.9046 | 122.0032 | 122.0293 | 121.912 | -0.36101
2378.5156 | 122.0764 | -121.9345 | 0.10986 | 1.4211e-13 | -0.061997 | -0.010925 | 0.06216 | -0.011128 | 0.05154 | 0.0021363 | -7.0448e-05 | -0.0038244 | -0.0055762 | 0.038722 | -0.0010534 | -121.459 | -5.4792 | -121.7632 | 0.038393 | 0.064464 | 0.14197 | -121.9769 | -0.012689 | -0.022535 | -0.12503 | -0.025376 | 0.073228 | 0.10848 | -0.23741 | -0.042414 | -0.07147 | 0.47551 | 0.17131 | 0.21372 | -0.045399 | 0.032103 | 121.6971 | -0.13524 | 121.9218 | 121.8095 | 0.11238 | -0.036635 | -0.001383 | 121.9729 | 121.999 | 122.0765 | 116.4553 | -122.0868 | 121.9091 | 122.0077 | 122.043 | 121.912 | -0.34727
2380.2031 | 122.1817 | -121.9208 | 0.086975 | 1.4211e-13 | -0.061997 | -0.011139 | 0.062374 | -0.011555 | 0.051753 | -0.020755 | -0.00028425 | -0.0038244 | -0.0057898 | 0.038935 | -0.0010534 | -121.4727 | -5.5204 | -121.7495 | 0.033814 | 0.059885 | 0.13281 | -121.9815 | -0.003531 | -0.013377 | -0.1113 | -0.029954 | 0.073228 | 0.094744 | -0.23283 | -0.060726 | -0.053161 | 0.44804 | 0.17131 | 0.23204 | -0.02709 | 0.045834 | 121.6879 | -0.11693 | 121.9172 | 121.8095 | 0.12154 | -0.013747 | 0.007769 | 121.9546 | 121.9807 | 122.0536 | 116.4004 | -122.0685 | 121.8908 | 121.994 | 122.0155 | 121.9074 | -0.31981
2381.9531 | 122.0535 | -121.9345 | 0.11902 | 1.4211e-13 | -0.062425 | -0.011139 | 0.061947 | -0.011128 | 0.05154 | -0.013124 | 0.00014315 | -0.0038244 | -0.0062172 | 0.039363 | -0.0010534 | -121.4727 | -5.5708 | -121.7586 | 0.038393 | 0.069043 | 0.12365 | -121.9769 | -0.003531 | -0.008798 | -0.10672 | -0.025376 | 0.06865 | 0.099323 | -0.22825 | -0.042414 | -0.080626 | 0.46177 | 0.17589 | 0.2183 | -0.049976 | 0.004633 | 121.7063 | -0.14439 | 121.931 | 121.8278 | 0.12154 | -0.050369 | -0.019696 | 121.9729 | 122.0036 | 122.0582 | 116.3638 | -122.0959 | 121.9091 | 122.0032 | 122.0338 | 121.9257 | -0.34727
2383.7188 | 122.0901 | -121.962 | 0.10071 | 1.4211e-13 | -0.061784 | -0.011139 | 0.06216 | -0.011555 | 0.051326 | -0.020755 | -0.00071145 | -0.0036108 | -0.0062172 | 0.039363 | -0.0010534 | -121.4727 | -5.6257 | -121.754 | 0.038393 | 0.059885 | 0.13281 | -121.9815 | -0.017267 | -0.008798 | -0.13419 | -0.029954 | 0.06865 | 0.099323 | -0.24657 | -0.019527 | -0.062315 | 0.48924 | 0.20793 | 0.22746 | -0.040823 | 0.032101 | 121.7154 | -0.13066 | 121.9447 | 121.8278 | 0.11238 | -0.032058 | -0.001385 | 122.0004 | 122.0219 | 122.0948 | 116.3363 | -122.0822 | 121.932 | 122.0306 | 122.0613 | 121.9532 | -0.34728
2385.4844 | 122.1451 | -121.9116 | 0.10071 | 1.4211e-13 | -0.061997 | -0.010925 | 0.062801 | -0.011341 | 0.05154 | -0.013124 | -0.00049785 | -0.0042518 | -0.0060034 | 0.038935 | -0.001267 | -121.4727 | -5.6669 | -121.7632 | 0.033814 | 0.059885 | 0.13281 | -121.9769 | -0.035582 | -0.00422 | -0.13877 | -0.029954 | 0.064071 | 0.094744 | -0.25572 | -0.065302 | -0.066894 | 0.43888 | 0.14842 | 0.21372 | -0.040823 | 0.032101 | 121.6559 | -0.13066 | 121.876 | 121.7729 | 0.11696 | -0.036637 | -0.005964 | 121.9454 | 121.9715 | 122.0444 | 116.2447 | -122.0776 | 121.8817 | 121.9757 | 122.0064 | 121.9074 | -0.35643
2387.2344 | 122.1039 | -121.9711 | 0.09613 | 1.4211e-13 | -0.062211 | -0.011139 | 0.06216 | -0.011128 | 0.051753 | -0.020755 | -0.00071145 | -0.004038 | -0.0057898 | 0.039149 | -0.001267 | -121.4773 | -5.7127 | -121.7678 | 0.038393 | 0.055306 | 0.13739 | -121.9861 | -0.026425 | -0.013377 | -0.13877 | -0.029954 | 0.073228 | 0.099323 | -0.2603 | -0.014951 | -0.057737 | 0.49381 | 0.20335 | 0.2183 | -0.040824 | 0.041257 | 121.7108 | -0.12608 | 121.9447 | 121.8324 | 0.12154 | -0.022902 | 0.003193 | 122.0095 | 122.0264 | 122.1085 | 116.2584 | -122.0822 | 121.9412 | 122.0444 | 122.0705 | 121.9578 | -0.35643
2388.9219 | 122.2275 | -121.9162 | 0.064087 | 1.4211e-13 | -0.061997 | -0.011139 | 0.06216 | -0.011128 | 0.05154 | -0.013124 | -0.00049785 | -0.004038 | -0.0057898 | 0.038722 | -0.001267 | -121.4819 | -5.7631 | -121.7632 | 0.029236 | 0.064464 | 0.13281 | -121.9861 | -0.031003 | -0.013377 | -0.13877 | -0.034533 | 0.064071 | 0.1039 | -0.26488 | -0.069882 | -0.034851 | 0.4343 | 0.153 | 0.22288 | 0.000377 | 0.068722 | 121.6513 | -0.09862 | 121.8852 | 121.7774 | 0.12611 | -1.6e-05 | 0.039814 | 121.9454 | 121.9807 | 122.049 | 116.1531 | -122.0502 | 121.8817 | 121.9803 | 122.0201 | 121.9028 | -0.32897
2390.6719 | 122.1771 | -121.9345 | 0.09613 | 1.4211e-13 | -0.061997 | -0.011139 | 0.06216 | -0.011341 | 0.051753 | -0.0054937 | -7.0448e-05 | -0.0038244 | -0.0057898 | 0.038935 | -0.0010534 | -121.4819 | -5.8088 | -121.7678 | 0.042971 | 0.064464 | 0.13281 | -121.9907 | -0.035582 | -0.008798 | -0.14335 | -0.029954 | 0.073228 | 0.094744 | -0.2603 | -0.056151 | -0.053159 | 0.45261 | 0.16673 | 0.22288 | -0.031666 | 0.036679 | 121.6742 | -0.12608 | 121.8989 | 121.7912 | 0.11696 | -0.022902 | -0.001386 | 121.9775 | 121.999 | 122.0673 | 116.1257 | -122.0868 | 121.9046 | 122.0077 | 122.0293 | 121.9257 | -0.35643
2392.4219 | 122.0901 | -121.9437 | 0.10986 | 1.4211e-13 | -0.062425 | -0.011139 | 0.06216 | -0.011341 | 0.051967 | -0.013124 | -0.00071145 | -0.0036108 | -0.0057898 | 0.039149 | -0.0014806 | -121.4819 | -5.8684 | -121.7724 | 0.042971 | 0.059885 | 0.13739 | -121.9815 | -0.026425 | -0.00422 | -0.13877 | -0.025376 | 0.073228 | 0.099323 | -0.25572 | -0.037837 | -0.066892 | 0.46177 | 0.17131 | 0.20914 | -0.049978 | 0.027524 | 121.6879 | -0.13524 | 121.9172 | 121.8049 | 0.11696 | -0.036635 | -0.01054 | 121.9866 | 122.0035 | 122.0811 | 116.0753 | -122.0914 | 121.9183 | 122.0169 | 122.043 | 121.9394 | -0.36559
2394.1719 | 122.2 | -121.962 | 0.07782 | 1.4211e-13 | -0.062425 | -0.011139 | 0.06216 | -0.011128 | 0.051967 | -0.0054937 | -7.0448e-05 | -0.0033972 | -0.0057898 | 0.038935 | -0.0010534 | -121.4865 | -5.9187 | -121.7769 | 0.033814 | 0.055306 | 0.14197 | -121.9907 | -0.021846 | 0.000359 | -0.13877 | -0.029954 | 0.077807 | 0.099323 | -0.2603 | -0.028685 | -0.044006 | 0.4755 | 0.18504 | 0.21372 | -0.022514 | 0.064146 | 121.7017 | -0.10777 | 121.9401 | 121.8232 | 0.12154 | -1.3e-05 | 0.021503 | 121.9958 | 122.0173 | 122.1039 | 116.0432 | -122.0685 | 121.932 | 122.0398 | 122.0613 | 121.9623 | -0.33812
2395.8594 | 122.1497 | -121.9528 | 0.10986 | 1.4211e-13 | -0.062425 | -0.010925 | 0.06216 | -0.011555 | 0.05154 | -0.013124 | -7.0448e-05 | -0.0038244 | -0.0060034 | 0.039363 | -0.00083958 | -121.4911 | -5.9737 | -121.7724 | 0.033814 | 0.059885 | 0.13281 | -121.9952 | -0.021846 | 0.004938 | -0.13419 | -0.029954 | 0.077807 | 0.1039 | -0.2603 | -0.042419 | -0.076049 | 0.46177 | 0.18046 | 0.22288 | -0.049978 | 0.022946 | 121.6925 | -0.13982 | 121.931 | 121.8186 | 0.12611 | -0.032056 | -0.005962 | 121.9866 | 122.0127 | 122.0856 | 115.9792 | -122.1051 | 121.9229 | 122.0306 | 122.0567 | 121.9578 | -0.37017
2397.6094 | 122.0901 | -121.9711 | 0.1236 | 1.4211e-13 | -0.062425 | -0.010925 | 0.06216 | -0.011128 | 0.051112 | -0.020755 | -7.0448e-05 | -0.0038244 | -0.0060034 | 0.039149 | -0.0010534 | -121.4865 | -6.024 | -121.7769 | 0.042971 | 0.055306 | 0.13281 | -121.9998 | -0.012689 | 0.009516 | -0.13419 | -0.029954 | 0.073228 | 0.099323 | -0.2603 | -0.028688 | -0.080625 | 0.48466 | 0.19419 | 0.22288 | -0.06829 | 0.009213 | 121.7108 | -0.15355 | 121.9584 | 121.8369 | 0.12611 | -0.050368 | -0.024273 | 122.0141 | 122.0264 | 122.1039 | 115.9471 | -122.1234 | 121.9412 | 122.0444 | 122.0705 | 121.9806 | -0.3839
2399.2969 | 122.1085 | -121.9849 | 0.10071 | 1.4211e-13 | -0.062425 | -0.011353 | 0.06216 | -0.011555 | 0.05154 | -0.013124 | -7.0448e-05 | -0.0038244 | -0.0060034 | 0.039363 | -0.00083958 | -121.4911 | -6.079 | -121.7769 | 0.038393 | 0.059885 | 0.14197 | -121.9998 | -0.021846 | 0.014095 | -0.13419 | -0.029954 | 0.064071 | 0.099323 | -0.24657 | -0.014955 | -0.062315 | 0.49381 | 0.20793 | 0.22288 | -0.040823 | 0.041258 | 121.7383 | -0.13066 | 121.963 | 121.8507 | 0.11238 | -0.036637 | -0.001385 | 122.0233 | 122.0447 | 122.1268 | 115.9059 | -122.1005 | 121.9549 | 122.0489 | 122.0842 | 121.999 | -0.34728
2401.0625 | 122.2366 | -121.9116 | 0.054932 | 1.4211e-13 | -0.062425 | -0.010925 | 0.062374 | -0.011341 | 0.051967 | -0.013124 | -7.0448e-05 | -0.0036108 | -0.0060034 | 0.039149 | -0.00083958 | -121.4956 | -6.1385 | -121.7861 | 0.038393 | 0.059885 | 0.13281 | -122.0044 | -0.012689 | 0.018674 | -0.13419 | -0.034533 | 0.064071 | 0.094744 | -0.24657 | -0.092776 | -0.016539 | 0.41599 | 0.12553 | 0.2183 | 0.004953 | 0.077877 | 121.6651 | -0.089465 | 121.8989 | 121.7774 | 0.11238 | 0.009139 | 0.039812 | 121.95 | 121.9715 | 122.0444 | 115.7731 | -122.0593 | 121.8771 | 121.9757 | 122.0064 | 121.9303 | -0.3015
2402.75 | 122.2275 | -121.9254 | 0.059509 | 1.4211e-13 | -0.062638 | -0.011139 | 0.062374 | -0.011769 | 0.052181 | -0.013124 | -7.0448e-05 | -0.0036108 | -0.0055762 | 0.039149 | -0.0014806 | -121.4956 | -6.198 | -121.7769 | 0.033814 | 0.064464 | 0.13281 | -122.0044 | -0.012689 | 0.023253 | -0.12961 | -0.029954 | 0.064071 | 0.099323 | -0.24657 | -0.079043 | -0.025695 | 0.42972 | 0.14842 | 0.22746 | 0.004955 | 0.0733 | 121.6788 | -0.089463 | 121.9127 | 121.7957 | 0.11696 | 0.004562 | 0.039814 | 121.9592 | 121.9898 | 122.0582 | 115.7273 | -122.0639 | 121.8954 | 121.9894 | 122.0247 | 121.9486 | -0.30608
2404.5 | 122.2412 | -121.8979 | 0.073242 | 1.4211e-13 | -0.062638 | -0.010925 | 0.061947 | -0.011555 | 0.051326 | -0.013124 | -0.00049785 | -0.0038244 | -0.0060034 | 0.038935 | -0.0010534 | -121.4911 | -6.2575 | -121.7815 | 0.038393 | 0.059885 | 0.12823 | -122.0044 | -0.012689 | 0.027831 | -0.12045 | -0.029954 | 0.064071 | 0.090166 | -0.24199 | -0.10651 | -0.034849 | 0.40684 | 0.11637 | 0.22288 | -0.013357 | 0.054988 | 121.6559 | -0.1032 | 121.8852 | 121.7774 | 0.12154 | -0.009171 | 0.016924 | 121.9363 | 121.9578 | 122.0261 | 115.6403 | -122.0776 | 121.8679 | 121.962 | 121.9881 | 121.9257 | -0.31523
2406.2031 | 122.1588 | -121.9437 | 0.091553 | 1.4211e-13 | -0.062425 | -0.011139 | 0.06216 | -0.011555 | 0.051326 | -0.0054937 | -0.00028425 | -0.0038244 | -0.0057898 | 0.039577 | -0.001267 | -121.4956 | -6.3216 | -121.7861 | 0.033814 | 0.059885 | 0.13281 | -121.9998 | -0.003531 | 0.023253 | -0.12045 | -0.029954 | 0.064071 | 0.1039 | -0.23741 | -0.056153 | -0.057739 | 0.44803 | 0.15757 | 0.21373 | -0.031668 | 0.041256 | 121.7063 | -0.12151 | 121.9401 | 121.8232 | 0.11696 | -0.027482 | 0.012348 | 121.9775 | 122.0035 | 122.0765 | 115.622 | -122.0914 | 121.9137 | 122.0077 | 122.0476 | 121.9669 | -0.32896
2407.9531 | 122.1542 | -121.9849 | 0.10071 | 1.4211e-13 | -0.062211 | -0.010925 | 0.062374 | -0.011555 | 0.05154 | -0.0054937 | -7.0448e-05 | -0.0036108 | -0.0060034 | 0.039149 | -0.0010534 | -121.4956 | -6.3812 | -121.7907 | 0.038393 | 0.059885 | 0.13281 | -122.0044 | -0.003531 | 0.023253 | -0.11587 | -0.034533 | 0.073228 | 0.099323 | -0.24199 | -0.019534 | -0.062315 | 0.48923 | 0.19419 | 0.21372 | -0.040823 | 0.032101 | 121.7429 | -0.13524 | 121.9813 | 121.869 | 0.12612 | -0.02748 | -0.001385 | 122.0233 | 122.0447 | 122.1177 | 115.6037 | -122.1051 | 121.9503 | 122.0581 | 122.0842 | 122.0081 | -0.3427
2409.7031 | 122.2504 | -121.9345 | 0.068665 | 1.4211e-13 | -0.062638 | -0.010925 | 0.062588 | -0.011769 | 0.051967 | -0.0054937 | -7.0448e-05 | -0.0033972 | -0.0060034 | 0.039363 | -0.0014806 | -121.4956 | -6.4315 | -121.7907 | 0.033814 | 0.069043 | 0.14197 | -122.009 | -0.012689 | 0.03241 | -0.10672 | -0.020797 | 0.06865 | 0.099323 | -0.23741 | -0.074467 | -0.034851 | 0.43888 | 0.14384 | 0.2183 | 0.000378 | 0.073301 | 121.6971 | -0.089462 | 121.9218 | 121.8278 | 0.13069 | -1.5e-05 | 0.030658 | 121.9683 | 122.0036 | 122.0765 | 115.503 | -122.0776 | 121.9137 | 122.0032 | 122.0338 | 121.9669 | -0.30607
2411.4688 | 122.2504 | -121.9666 | 0.07782 | 1.4211e-13 | -0.062638 | -0.011139 | 0.06216 | -0.011769 | 0.05154 | -0.0054937 | -0.00028425 | -0.0038244 | -0.0057898 | 0.039577 | -0.001267 | -121.4956 | -6.4911 | -121.7998 | 0.033814 | 0.064464 | 0.13739 | -122.0136 | -0.012689 | 0.036989 | -0.12045 | -0.029954 | 0.064071 | 0.1039 | -0.23283 | -0.047002 | -0.044006 | 0.47092 | 0.16672 | 0.21373 | -0.013356 | 0.059567 | 121.7337 | -0.10777 | 121.9539 | 121.8461 | 0.11238 | -0.013749 | 0.026081 | 122.0004 | 122.031 | 122.1039 | 115.4755 | -122.0914 | 121.9366 | 122.0306 | 122.0705 | 122.0035 | -0.31065
2413.2188 | 122.1039 | -121.9849 | 0.11444 | 1.4211e-13 | -0.062638 | -0.011139 | 0.061947 | -0.011341 | 0.051326 | -0.013124 | -0.00028425 | -0.0038244 | -0.0060034 | 0.039363 | -0.00083958 | -121.5002 | -6.5597 | -121.7907 | 0.033814 | 0.059885 | 0.13281 | -122.0136 | -0.012689 | 0.03241 | -0.1113 | -0.034533 | 0.073228 | 0.099323 | -0.23741 | -0.028692 | -0.080627 | 0.48465 | 0.19419 | 0.22288 | -0.054556 | 0.018368 | 121.7475 | -0.14897 | 121.9722 | 121.8736 | 0.12611 | -0.041213 | -0.015118 | 122.0187 | 122.0447 | 122.1177 | 115.4251 | -122.128 | 121.9503 | 122.0581 | 122.0842 | 122.0173 | -0.35185
2414.9688 | 122.2778 | -121.9437 | 0.07782 | 1.4211e-13 | -0.062211 | -0.011139 | 0.062374 | -0.011555 | 0.05154 | -0.013124 | -0.00028425 | -0.004038 | -0.0057898 | 0.039577 | -0.001267 | -121.4956 | -6.6193 | -121.7952 | 0.038393 | 0.064464 | 0.13281 | -122.0136 | -0.012689 | 0.041567 | -0.11587 | -0.025376 | 0.073228 | 0.099323 | -0.22825 | -0.06989 | -0.039427 | 0.44803 | 0.14841 | 0.21831 | -0.013356 | 0.054989 | 121.7154 | -0.1032 | 121.931 | 121.8278 | 0.11238 | -0.004592 | 0.021503 | 121.9821 | 122.0081 | 122.0765 | 115.3244 | -122.0914 | 121.9183 | 122.0169 | 122.043 | 121.9852 | -0.30607
2416.6562 | 122.1634 | -121.994 | 0.10986 | 1.4211e-13 | -0.062638 | -0.011139 | 0.062588 | -0.011341 | 0.051326 | -0.013124 | -7.0448e-05 | -0.0036108 | -0.0060034 | 0.039149 | -0.0010534 | -121.5048 | -6.6879 | -121.7952 | 0.033814 | 0.073622 | 0.13739 | -122.0181 | 0.014784 | 0.036989 | -0.042615 | -0.025376 | 0.077807 | 0.1039 | -0.19162 | -0.024115 | -0.076049 | 0.48923 | 0.19877 | 0.22288 | -0.036241 | 0.027524 | 121.8024 | -0.13524 | 122.0088 | 121.9514 | 0.14901 | -0.032056 | -0.005962 | 122.0278 | 122.0676 | 122.1314 | 115.3061 | -122.128 | 121.9686 | 122.0718 | 122.0979 | 122.031 | -0.30149
2418.3438 | 122.2275 | -121.9894 | 0.068665 | 1.4211e-13 | -0.062852 | -0.011139 | 0.061947 | -0.011341 | 0.05154 | -0.020755 | -0.00028425 | -0.0036108 | -0.0053626 | 0.039577 | -0.0010534 | -121.5002 | -6.7703 | -121.7998 | 0.042971 | 0.069043 | 0.13281 | -122.0181 | 0.023941 | 0.041567 | -0.047194 | -0.029954 | 0.073228 | 0.094744 | -0.19162 | -0.028693 | -0.025694 | 0.48923 | 0.18961 | 0.21831 | 0.000378 | 0.064144 | 121.7978 | -0.098619 | 122.0134 | 121.9422 | 0.14443 | 0.004563 | 0.026079 | 122.0324 | 122.0585 | 122.1222 | 115.2191 | -122.0868 | 121.9595 | 122.0627 | 122.0842 | 122.031 | -0.26029
2420.0938 | 122.2687 | -121.9254 | 0.059509 | 1.4211e-13 | -0.063066 | -0.010498 | 0.06216 | -0.011128 | 0.051753 | -0.013124 | -0.00049785 | -0.0036108 | -0.0062172 | 0.039363 | -0.001267 | -121.5094 | -6.8253 | -121.8044 | 0.038393 | 0.064464 | 0.13739 | -122.0227 | 0.033099 | 0.050725 | -0.042615 | -0.029954 | 0.064071 | 0.099323 | -0.18704 | -0.097358 | -0.021116 | 0.41599 | 0.12095 | 0.21831 | 0.004955 | 0.077878 | 121.7383 | -0.089463 | 121.9585 | 121.8827 | 0.14443 | 0.004562 | 0.039814 | 121.9637 | 121.9898 | 122.0627 | 115.1001 | -122.0822 | 121.8954 | 121.9894 | 122.0247 | 121.9761 | -0.24655
2421.7969 | 122.3053 | -121.9574 | 0.054932 | 1.4211e-13 | -0.062852 | -0.011139 | 0.06216 | -0.011341 | 0.05154 | -0.013124 | -0.00028425 | -0.0036108 | -0.0057898 | 0.039149 | -0.0010534 | -121.5002 | -6.8894 | -121.7998 | 0.038393 | 0.059885 | 0.13281 | -122.0319 | 0.023941 | 0.041567 | -0.047194 | -0.025376 | 0.073228 | 0.094744 | -0.18246 | -0.074473 | -0.016539 | 0.45719 | 0.15757 | 0.23204 | 0.004953 | 0.077877 | 121.7749 | -0.080308 | 121.9813 | 121.9102 | 0.13527 | 0.018296 | 0.039812 | 121.9958 | 122.0173 | 122.0902 | 115.068 | -122.0868 | 121.932 | 122.0306 | 122.0521 | 121.999 | -0.2374
2423.5625 | 122.2733 | -121.9757 | 0.091553 | 1.4211e-13 | -0.062638 | -0.010925 | 0.06216 | -0.011128 | 0.051326 | 0.0021363 | -0.00049785 | -0.0033972 | -0.0057898 | 0.039363 | -0.0010534 | -121.5048 | -6.9581 | -121.8044 | 0.042971 | 0.064464 | 0.13739 | -122.0227 | 0.019362 | 0.046146 | -0.042615 | -0.029954 | 0.06865 | 0.099323 | -0.18704 | -0.047004 | -0.048582 | 0.47092 | 0.1713 | 0.21831 | -0.027089 | 0.045834 | 121.7887 | -0.12151 | 121.9951 | 121.9331 | 0.14443 | -0.022903 | 0.00777 | 122.0187 | 122.0402 | 122.1131 | 115.0176 | -122.1143 | 121.9458 | 122.0444 | 122.075 | 122.0219 | -0.2786
2425.25 | 122.1405 | -121.9894 | 0.11444 | 1.4211e-13 | -0.062638 | -0.011353 | 0.06216 | -0.011769 | 0.051326 | -0.020755 | -0.00049785 | -0.0038244 | -0.0062172 | 0.039577 | -0.001267 | -121.5002 | -7.0267 | -121.809 | 0.033814 | 0.059885 | 0.13281 | -122.0227 | 0.02852 | 0.046146 | -0.047194 | -0.025376 | 0.077807 | 0.099323 | -0.18246 | -0.033271 | -0.080627 | 0.48923 | 0.18046 | 0.21373 | -0.054556 | 0.018368 | 121.807 | -0.13982 | 122.018 | 121.9422 | 0.13527 | -0.036634 | -0.015118 | 122.0233 | 122.0493 | 122.1222 | 114.9627 | -122.1372 | 121.9641 | 122.0672 | 122.0888 | 122.0356 | -0.2969
2427 | 122.2595 | -121.9666 | 0.07782 | 1.4211e-13 | -0.062852 | -0.010925 | 0.062588 | -0.011769 | 0.051326 | -0.0054937 | -0.00028425 | -0.0033972 | -0.0055762 | 0.039363 | -0.0010534 | -121.5048 | -7.0954 | -121.8136 | 0.038393 | 0.069043 | 0.14655 | -122.0227 | 0.02852 | 0.050725 | -0.047194 | -0.034533 | 0.06865 | 0.099323 | -0.17788 | -0.056159 | -0.039427 | 0.46176 | 0.15299 | 0.20915 | -0.008777 | 0.068725 | 121.7887 | -0.11235 | 121.9951 | 121.9194 | 0.13069 | -0.00917 | 0.021503 | 122.0049 | 122.0356 | 122.1131 | 114.8711 | -122.1005 | 121.932 | 122.0352 | 122.0659 | 122.0173 | -0.2557
2428.6875 | 122.2137 | -121.9666 | 0.068665 | 1.4211e-13 | -0.063066 | -0.011353 | 0.06216 | -0.011341 | 0.051753 | -0.020755 | -0.00049785 | -0.0038244 | -0.0062172 | 0.039149 | -0.0014806 | -121.5002 | -7.1687 | -121.8136 | 0.029236 | 0.059885 | 0.14197 | -122.0273 | 0.023941 | 0.046146 | -0.047194 | -0.025376 | 0.06865 | 0.094744 | -0.18246 | -0.060738 | -0.039429 | 0.46634 | 0.15299 | 0.21373 | -0.00878 | 0.073301 | 121.7841 | -0.094041 | 121.9905 | 121.9194 | 0.13527 | -1.5e-05 | 0.026079 | 121.9958 | 122.0264 | 122.1085 | 114.7979 | -122.096 | 121.9412 | 122.0352 | 122.0613 | 122.0127 | -0.25113
2430.4375 | 122.1771 | -121.994 | 0.10071 | 1.4211e-13 | -0.062852 | -0.011353 | 0.062374 | -0.011128 | 0.05154 | -0.013124 | -7.0448e-05 | -0.004038 | -0.0055762 | 0.039577 | -0.0014806 | -121.5094 | -7.2328 | -121.8136 | 0.042971 | 0.064464 | 0.14197 | -122.0319 | 0.02852 | 0.096512 | -0.042615 | -0.020797 | 0.06865 | 0.10848 | -0.17788 | -0.037851 | -0.057737 | 0.48465 | 0.18046 | 0.21831 | -0.036244 | 0.041258 | 121.8161 | -0.12151 | 122.0225 | 121.9514 | 0.13527 | -0.032058 | 0.007772 | 122.037 | 122.0585 | 122.136 | 114.7612 | -122.1326 | 121.9732 | 122.0627 | 122.1025 | 122.0905 | -0.27859
2432.2031 | 122.1817 | -121.9894 | 0.1236 | 1.4211e-13 | -0.063066 | -0.010925 | 0.06216 | -0.011341 | 0.051326 | -0.0054937 | -0.00049785 | -0.0036108 | -0.0060034 | 0.039577 | -0.0014806 | -121.5139 | -7.306 | -121.8136 | 0.029236 | 0.064464 | 0.13739 | -122.0273 | 0.02852 | 0.087354 | -0.056351 | -0.020797 | 0.073228 | 0.1039 | -0.17788 | -0.03785 | -0.09436 | 0.4755 | 0.17588 | 0.21373 | -0.059132 | 0.013791 | 121.8116 | -0.14439 | 122.018 | 121.9331 | 0.12153 | -0.050368 | -0.019695 | 122.0187 | 122.0539 | 122.1268 | 114.6834 | -122.1509 | 121.9686 | 122.0627 | 122.0933 | 122.0768 | -0.30148
2433.8906 | 122.2183 | -121.9757 | 0.073242 | 1.4211e-13 | -0.062852 | -0.010925 | 0.062374 | -0.011555 | 0.051753 | -0.028385 | -7.0448e-05 | -0.0038244 | -0.0060034 | 0.039363 | -0.0010534 | -121.5094 | -7.3793 | -121.8136 | 0.038393 | 0.064464 | 0.13281 | -122.041 | 0.023941 | 0.091933 | -0.051772 | -0.034533 | 0.06865 | 0.10848 | -0.18246 | -0.06532 | -0.034849 | 0.46634 | 0.16214 | 0.22746 | -0.008778 | 0.059567 | 121.7932 | -0.10778 | 121.9996 | 121.9239 | 0.13069 | -0.004592 | 0.035238 | 122.0141 | 122.0402 | 122.1085 | 114.5964 | -122.1143 | 121.9412 | 122.0444 | 122.0842 | 122.0676 | -0.25571
2435.6562 | 122.2229 | -121.9711 | 0.086975 | 1.4211e-13 | -0.062852 | -0.010925 | 0.062374 | -0.011341 | 0.051967 | -0.0054937 | -7.0448e-05 | -0.0036108 | -0.0053626 | 0.03979 | -0.0014806 | -121.5094 | -7.4617 | -121.8136 | 0.042971 | 0.069043 | 0.13739 | -122.0319 | 0.023941 | 0.087354 | -0.042615 | -0.025376 | 0.06865 | 0.094744 | -0.18246 | -0.06074 | -0.044004 | 0.46176 | 0.15757 | 0.21831 | -0.017932 | 0.050412 | 121.7887 | -0.11235 | 121.9951 | 121.9285 | 0.13985 | -0.018325 | 0.007769 | 122.0141 | 122.0402 | 122.1085 | 114.5094 | -122.1188 | 121.9458 | 122.0398 | 122.0659 | 122.0585 | -0.26944
2437.4062 | 122.1497 | -122.0078 | 0.11902 | 1.4211e-13 | -0.062852 | -0.010925 | 0.06216 | -0.011341 | 0.051326 | 0.0021363 | -0.00071145 | -0.0038244 | -0.0057898 | 0.03979 | -0.0016942 | -121.5094 | -7.5304 | -121.8136 | 0.042971 | 0.064464 | 0.13739 | -122.041 | 0.02852 | 0.091933 | -0.056351 | -0.025376 | 0.077807 | 0.099323 | -0.16873 | -0.033277 | -0.076048 | 0.49838 | 0.19419 | 0.22746 | -0.054555 | 0.018368 | 121.839 | -0.14439 | 122.0363 | 121.9514 | 0.11238 | -0.041212 | -0.019696 | 122.0507 | 122.0722 | 122.1451 | 114.4774 | -122.16 | 121.9824 | 122.0856 | 122.1071 | 122.0997 | -0.28775
2439.0938 | 122.2641 | -121.9894 | 0.073242 | 1.4211e-13 | -0.062638 | -0.011353 | 0.062374 | -0.011341 | 0.051112 | -0.020755 | -7.0448e-05 | -0.0036108 | -0.0060034 | 0.039577 | -0.0010534 | -121.5094 | -7.567 | -121.809 | 0.042971 | 0.069043 | 0.14197 | -122.0456 | 0.02852 | 0.087354 | -0.051772 | -0.034533 | 0.06865 | 0.099323 | -0.17788 | -0.056166 | -0.030271 | 0.48007 | 0.18046 | 0.23662 | -0.004199 | 0.068724 | 121.8116 | -0.10778 | 122.018 | 121.9377 | 0.12611 | -0.004592 | 0.026081 | 122.0324 | 122.0585 | 122.1314 | 114.4224 | -122.1188 | 121.9549 | 122.0581 | 122.0888 | 122.0768 | -0.25113
2440.8594 | 122.1634 | -122.0078 | 0.10529 | 1.4211e-13 | -0.063066 | -0.011139 | 0.062374 | -0.011555 | 0.05154 | -0.0054937 | 0.00014315 | -0.0038244 | -0.0060034 | 0.039577 | -0.0014806 | -121.5048 | -7.6494 | -121.8181 | 0.038393 | 0.059885 | 0.14197 | -122.0364 | 0.02852 | 0.091933 | -0.051772 | -0.034533 | 0.06865 | 0.1039 | -0.17788 | -0.028698 | -0.066893 | 0.50296 | 0.18961 | 0.21831 | -0.045401 | 0.03668 | 121.8299 | -0.13982 | 122.0363 | 121.956 | 0.12611 | -0.036636 | -0.001385 | 122.0461 | 122.0676 | 122.1497 | 114.3583 | -122.1417 | 121.9732 | 122.0764 | 122.1117 | 122.0997 | -0.28317
2442.625 | 122.2595 | -121.9757 | 0.073242 | 1.4211e-13 | -0.063279 | -0.011566 | 0.062374 | -0.011769 | 0.05154 | -0.013124 | -0.00049785 | -0.0038244 | -0.0057898 | 0.039577 | -0.0014806 | -121.5139 | -7.7227 | -121.8181 | 0.038393 | 0.059885 | 0.13739 | -122.0456 | 0.033099 | 0.096512 | -0.042615 | -0.025376 | 0.073228 | 0.1039 | -0.17788 | -0.069899 | -0.034849 | 0.46176 | 0.15757 | 0.22747 | -0.013357 | 0.064145 | 121.7978 | -0.098618 | 122.0088 | 121.9331 | 0.13527 | -1.4e-05 | 0.030659 | 122.0141 | 122.0356 | 122.1131 | 114.253 | -122.1188 | 121.9503 | 122.0489 | 122.0796 | 122.0722 | -0.25113
2444.3125 | 122.2183 | -121.9666 | 0.091553 | 1.4211e-13 | -0.063066 | -0.011139 | 0.061947 | -0.011128 | 0.05154 | -0.013124 | -0.00028425 | -0.0033972 | -0.0062172 | 0.039577 | -0.0014806 | -121.5139 | -7.8005 | -121.8181 | 0.038393 | 0.059885 | 0.13739 | -122.041 | 0.02852 | 0.096512 | -0.051772 | -0.029954 | 0.073228 | 0.099323 | -0.17788 | -0.074475 | -0.05316 | 0.45261 | 0.14841 | 0.22289 | -0.031668 | 0.045834 | 121.7887 | -0.12151 | 121.9951 | 121.9148 | 0.12611 | -0.018325 | 0.00777 | 122.0049 | 122.0264 | 122.1039 | 114.166 | -122.1326 | 121.9366 | 122.0398 | 122.0659 | 122.0631 | -0.26944
2446.0781 | 122.2092 | -122.0078 | 0.10529 | 1.4211e-13 | -0.063066 | -0.011566 | 0.062374 | -0.011341 | 0.05154 | -0.0054937 | -7.0448e-05 | -0.0038244 | -0.0057898 | 0.039363 | -0.001267 | -121.5185 | -7.8829 | -121.8181 | 0.029236 | 0.064464 | 0.14197 | -122.0456 | 0.02852 | 0.091933 | -0.047194 | -0.025376 | 0.077807 | 0.094744 | -0.17788 | -0.037856 | -0.07605 | 0.48923 | 0.18961 | 0.22747 | -0.040822 | 0.03668 | 121.8299 | -0.13066 | 122.0363 | 121.9606 | 0.13069 | -0.027479 | -0.010542 | 122.037 | 122.0722 | 122.1497 | 114.1248 | -122.1509 | 121.9824 | 122.0856 | 122.1025 | 122.0997 | -0.28317
2447.7656 | 122.2 | -122.0398 | 0.10071 | 1.4211e-13 | -0.063066 | -0.011353 | 0.06216 | -0.011341 | 0.051753 | -0.0054937 | 0.00035675 | -0.0038244 | -0.0057898 | 0.03979 | -0.001267 | -121.5094 | -7.9516 | -121.8181 | 0.038393 | 0.069043 | 0.14197 | -122.0502 | 0.023941 | 0.091933 | -0.051772 | -0.034533 | 0.064071 | 0.099323 | -0.18246 | -0.010391 | -0.062315 | 0.53043 | 0.22165 | 0.23204 | -0.031665 | 0.041258 | 121.8573 | -0.13524 | 122.0637 | 121.988 | 0.13069 | -0.036637 | -0.001385 | 122.0782 | 122.1088 | 122.1818 | 114.0882 | -122.1509 | 122.0053 | 122.1039 | 122.1391 | 122.1317 | -0.28317
2449.5312 | 122.2412 | -121.9849 | 0.086975 | 1.4211e-13 | -0.063279 | -0.011353 | 0.06216 | -0.011769 | 0.05154 | -0.013124 | -7.0448e-05 | -0.0038244 | -0.0055762 | 0.03979 | -0.001267 | -121.5139 | -8.0386 | -121.8136 | 0.042971 | 0.059885 | 0.13281 | -122.0502 | 0.02852 | 0.096512 | -0.042615 | -0.029954 | 0.077807 | 0.099323 | -0.17331 | -0.065323 | -0.044004 | 0.47092 | 0.1713 | 0.23662 | -0.02709 | 0.045834 | 121.8116 | -0.11693 | 122.0134 | 121.9422 | 0.13069 | -0.009168 | 0.012348 | 122.0278 | 122.0447 | 122.1177 | 113.9462 | -122.1372 | 121.9549 | 122.0627 | 122.0842 | 122.0814 | -0.26028
2451.2969 | 122.2504 | -121.9803 | 0.07782 | 1.4211e-13 | -0.063493 | -0.011139 | 0.062374 | -0.011555 | 0.05154 | -0.0054937 | -0.00028425 | -0.0036108 | -0.0060034 | 0.039577 | -0.0010534 | -121.5048 | -8.1302 | -121.8227 | 0.038393 | 0.064464 | 0.13739 | -122.0502 | 0.02852 | 0.091933 | -0.047194 | -0.020797 | 0.06865 | 0.099323 | -0.17788 | -0.0699 | -0.039427 | 0.4755 | 0.15757 | 0.22747 | -0.013356 | 0.059567 | 121.8024 | -0.098617 | 122.0088 | 121.9331 | 0.13069 | -0.00917 | 0.021503 | 122.0187 | 122.0448 | 122.1177 | 113.8501 | -122.128 | 121.9595 | 122.0489 | 122.0796 | 122.0722 | -0.2557
2453.0781 | 122.1542 | -122.0261 | 0.091553 | 1.4211e-13 | -0.063066 | -0.011353 | 0.06216 | -0.011769 | 0.05154 | -0.013124 | -0.00028425 | -0.0038244 | -0.0060034 | 0.03979 | -0.0010534 | -121.5094 | -8.2218 | -121.8319 | 0.042971 | 0.069043 | 0.14197 | -122.0548 | 0.023941 | 0.096512 | -0.042615 | -0.025376 | 0.06865 | 0.1039 | -0.18246 | -0.028703 | -0.048582 | 0.5167 | 0.19419 | 0.22289 | -0.02251 | 0.050413 | 121.8436 | -0.11693 | 122.05 | 121.9834 | 0.13985 | -0.022903 | 0.012348 | 122.069 | 122.0951 | 122.168 | 113.8043 | -122.1463 | 122.0007 | 122.0947 | 122.13 | 122.1226 | -0.27402
2454.7656 | 122.2183 | -122.0032 | 0.086975 | 1.4211e-13 | -0.063279 | -0.011139 | 0.062588 | -0.011555 | 0.051326 | -0.013124 | 0.00035675 | -0.0031834 | -0.0064308 | 0.03979 | -0.0010534 | -121.5139 | -8.2996 | -121.8227 | 0.038393 | 0.069043 | 0.1557 | -122.0502 | 0.055992 | 0.096512 | -0.042615 | -0.029954 | 0.073228 | 0.10848 | -0.16873 | -0.047012 | -0.048582 | 0.48923 | 0.18045 | 0.22747 | -0.017932 | 0.068727 | 121.8344 | -0.11693 | 122.0592 | 121.9606 | 0.12611 | -0.013747 | 0.021505 | 122.0416 | 122.0722 | 122.1589 | 113.7036 | -122.1372 | 121.9732 | 122.0764 | 122.1117 | 122.0997 | -0.2557
2456.5156 | 122.2641 | -122.0078 | 0.086975 | 1.4211e-13 | -0.063493 | -0.011139 | 0.062588 | -0.011555 | 0.05154 | -0.0054937 | -7.0448e-05 | -0.0036108 | -0.0062172 | 0.040004 | -0.0014806 | -121.5185 | -8.3866 | -121.8227 | 0.038393 | 0.064464 | 0.13739 | -122.0548 | 0.06515 | 0.096512 | -0.051772 | -0.029954 | 0.073228 | 0.1039 | -0.16415 | -0.047014 | -0.048582 | 0.48923 | 0.18503 | 0.23204 | -0.022511 | 0.050412 | 121.8436 | -0.11693 | 122.0729 | 121.956 | 0.11238 | -0.013747 | 0.016926 | 122.0461 | 122.0722 | 122.1451 | 113.6212 | -122.1417 | 121.9778 | 122.081 | 122.1117 | 122.1043 | -0.25112
2458.2031 | 122.3099 | -121.962 | 0.073242 | 1.4211e-13 | -0.063279 | -0.010925 | 0.062588 | -0.011341 | 0.05154 | 0.0021363 | -7.0448e-05 | -0.004038 | -0.0057898 | 0.03979 | -0.0010534 | -121.5048 | -8.4736 | -121.8273 | 0.042971 | 0.064464 | 0.13739 | -122.0593 | 0.055992 | 0.087354 | -0.051772 | -0.020797 | 0.06865 | 0.1039 | -0.15499 | -0.097369 | -0.030271 | 0.45719 | 0.13468 | 0.23205 | -0.008778 | 0.064145 | 121.807 | -0.094039 | 122.018 | 121.9102 | 0.10322 | -0.004592 | 0.030659 | 122.0049 | 122.0264 | 122.0994 | 113.4884 | -122.1326 | 121.9412 | 122.0306 | 122.0659 | 122.0493 | -0.22823
2459.9531 | 122.3145 | -121.9894 | 0.082397 | 1.4211e-13 | -0.063279 | -0.011566 | 0.062374 | -0.011555 | 0.05154 | -0.0054937 | -7.0448e-05 | -0.0036108 | -0.0060034 | 0.039577 | -0.001908 | -121.5185 | -8.5468 | -121.8319 | 0.047549 | 0.073622 | 0.14197 | -122.0593 | 0.055992 | 0.096512 | -0.047194 | -0.034533 | 0.06865 | 0.1039 | -0.16415 | -0.069903 | -0.034848 | 0.47092 | 0.15757 | 0.22747 | -0.008775 | 0.059569 | 121.8253 | -0.11693 | 122.0454 | 121.9422 | 0.11695 | -0.013747 | 0.021504 | 122.037 | 122.0631 | 122.1314 | 113.4426 | -122.1417 | 121.9549 | 122.0581 | 122.0933 | 122.086 | -0.24655
2461.7188 | 122.168 | -122.0444 | 0.10071 | 1.4211e-13 | -0.063066 | -0.011353 | 0.06216 | -0.011341 | 0.05154 | -0.013124 | -7.0448e-05 | -0.0038244 | -0.0053626 | 0.040004 | -0.001267 | -121.5139 | -8.6522 | -121.8273 | 0.029236 | 0.059885 | 0.13281 | -122.0548 | 0.060571 | 0.096512 | -0.051772 | -0.025376 | 0.064071 | 0.1039 | -0.15957 | -0.010392 | -0.071472 | 0.53043 | 0.21707 | 0.22747 | -0.040823 | 0.032101 | 121.8848 | -0.12608 | 122.1049 | 121.9926 | 0.1078 | -0.036637 | 0.003193 | 122.0736 | 122.1043 | 122.1772 | 113.3922 | -122.1555 | 122.019 | 122.1084 | 122.1483 | 122.1409 | -0.26028
2463.4062 | 122.2046 | -122.0078 | 0.10071 | 1.4211e-13 | -0.063279 | -0.011353 | 0.061947 | -0.011555 | 0.051326 | -0.013124 | 0.00014315 | -0.0038244 | -0.0057898 | 0.03979 | -0.001267 | -121.5185 | -8.7391 | -121.8227 | 0.038393 | 0.064464 | 0.14197 | -122.0685 | 0.060571 | 0.091933 | -0.056351 | -0.029954 | 0.073228 | 0.099323 | -0.15957 | -0.060751 | -0.062315 | 0.48923 | 0.18503 | 0.24578 | -0.036244 | 0.041258 | 121.8482 | -0.13066 | 122.0683 | 121.9514 | 0.10322 | -0.02748 | -0.001385 | 122.0461 | 122.0722 | 122.1497 | 113.2686 | -122.1692 | 121.9778 | 122.081 | 122.1071 | 122.0997 | -0.26028
2465.1562 | 122.1817 | -122.049 | 0.10529 | 1.4211e-13 | -0.062852 | -0.011353 | 0.06216 | -0.011555 | 0.05154 | -0.013124 | -7.0448e-05 | -0.0038244 | -0.0057898 | 0.03979 | -0.001267 | -121.5185 | -8.8445 | -121.8181 | 0.038393 | 0.069043 | 0.13739 | -122.0593 | 0.06515 | 0.096512 | -0.047194 | -0.034533 | 0.06865 | 0.10848 | -0.15957 | -0.010394 | -0.066893 | 0.53043 | 0.23081 | 0.2412 | -0.036243 | 0.032101 | 121.8894 | -0.13982 | 122.1141 | 122.0018 | 0.11238 | -0.036636 | 0.003194 | 122.0873 | 122.118 | 122.1863 | 113.2045 | -122.1646 | 122.0144 | 122.1176 | 122.1574 | 122.1455 | -0.26486
2466.9219 | 122.2824 | -122.0078 | 0.09613 | 1.4211e-13 | -0.063493 | -0.010925 | 0.062374 | -0.011769 | 0.051753 | 0.0021363 | 0.00014315 | -0.004038 | -0.0057898 | 0.03979 | -0.001267 | -121.5185 | -8.9589 | -121.8181 | 0.038393 | 0.064464 | 0.13739 | -122.0639 | 0.060571 | 0.091933 | -0.047194 | -0.025376 | 0.073228 | 0.1039 | -0.15957 | -0.056172 | -0.057737 | 0.48923 | 0.18961 | 0.24578 | -0.031666 | 0.041257 | 121.8482 | -0.12151 | 122.0683 | 121.9606 | 0.11238 | -0.022902 | 0.007771 | 122.0461 | 122.0722 | 122.1451 | 113.0488 | -122.1601 | 121.9824 | 122.081 | 122.1117 | 122.0997 | -0.2557
2468.6875 | 122.2916 | -122.0032 | 0.086975 | 1.4211e-13 | -0.063493 | -0.011353 | 0.06216 | -0.011341 | 0.051326 | 0.0021363 | -7.0448e-05 | -0.0036108 | -0.0060034 | 0.039577 | -0.0010534 | -121.5185 | -9.0734 | -121.8227 | 0.038393 | 0.069043 | 0.13739 | -122.0685 | 0.060571 | 0.096512 | -0.047194 | -0.020797 | 0.073228 | 0.099323 | -0.16415 | -0.065328 | -0.048582 | 0.48465 | 0.18045 | 0.24578 | -0.017932 | 0.050412 | 121.839 | -0.10777 | 122.0637 | 121.956 | 0.11695 | -0.013747 | 0.012348 | 122.0416 | 122.0722 | 122.1406 | 112.9298 | -122.1555 | 121.9824 | 122.0764 | 122.1025 | 122.0997 | -0.25112
2470.375 | 122.1817 | -122.0261 | 0.1236 | 1.4211e-13 | -0.063279 | -0.011139 | 0.06216 | -0.011555 | 0.051753 | -0.0054937 | 0.00014315 | -0.0038244 | -0.0062172 | 0.03979 | -0.0014806 | -121.5185 | -9.1421 | -121.8227 | 0.038393 | 0.069043 | 0.14197 | -122.0685 | 0.051413 | 0.096512 | -0.056351 | -0.029954 | 0.077807 | 0.1039 | -0.15957 | -0.04244 | -0.085203 | 0.50754 | 0.20334 | 0.24578 | -0.054553 | 0.01837 | 121.8665 | -0.15355 | 122.0775 | 121.9697 | 0.10322 | -0.045789 | -0.019695 | 122.0645 | 122.0951 | 122.168 | 112.884 | -122.1921 | 121.9961 | 122.1039 | 122.13 | 122.1226 | -0.28317
2472.1406 | 122.168 | -122.0444 | 0.11444 | 1.4211e-13 | -0.063066 | -0.011353 | 0.062588 | -0.011341 | 0.051326 | -0.028385 | -7.0448e-05 | -0.0038244 | -0.0060034 | 0.040004 | -0.0014806 | -121.5139 | -9.2336 | -121.8227 | 0.042971 | 0.064464 | 0.13739 | -122.0731 | 0.023941 | 0.096512 | -0.042615 | -0.025376 | 0.06865 | 0.094744 | -0.15957 | -0.028708 | -0.07147 | 0.53043 | 0.22165 | 0.25036 | -0.049977 | 0.022946 | 121.8848 | -0.13982 | 122.0683 | 122.0018 | 0.11695 | -0.045791 | -0.019697 | 122.0873 | 122.1088 | 122.1818 | 112.8107 | -122.1875 | 122.019 | 122.113 | 122.1391 | 122.1409 | -0.27401
2473.9062 | 122.1634 | -122.0352 | 0.11902 | 1.4211e-13 | -0.063493 | -0.011353 | 0.06216 | -0.011555 | 0.05154 | -0.013124 | -7.0448e-05 | -0.004038 | -0.0062172 | 0.040004 | -0.0014806 | -121.5185 | -9.3389 | -121.8227 | 0.047549 | 0.064464 | 0.13281 | -122.0685 | 0.02852 | 0.096512 | -0.047194 | -0.020797 | 0.077807 | 0.10848 | -0.16415 | -0.033285 | -0.07147 | 0.51669 | 0.2125 | 0.24578 | -0.054555 | 0.01379 | 121.8711 | -0.13982 | 122.0637 | 121.988 | 0.11695 | -0.041212 | -0.010539 | 122.0828 | 122.0997 | 122.168 | 112.6963 | -122.1875 | 122.0144 | 122.113 | 122.1437 | 122.1317 | -0.28317
2475.6094 | 122.2183 | -121.9849 | 0.12817 | 1.4211e-13 | -0.063707 | -0.011566 | 0.06216 | -0.011555 | 0.05154 | -0.0054937 | 0.00014315 | -0.0038244 | -0.0060034 | 0.040004 | -0.0016942 | -121.5185 | -9.4534 | -121.8365 | 0.042971 | 0.064464 | 0.14655 | -122.0731 | 0.019362 | 0.078197 | -0.047194 | -0.025376 | 0.06865 | 0.099323 | -0.17331 | -0.088218 | -0.085203 | 0.46634 | 0.14841 | 0.23663 | -0.06371 | 0.018371 | 121.8116 | -0.15355 | 122.0042 | 121.9377 | 0.12611 | -0.059524 | -0.028851 | 122.0278 | 122.0493 | 122.1314 | 112.5315 | -122.2013 | 121.9595 | 122.0535 | 122.0842 | 122.0631 | -0.30148
2477.2969 | 122.2549 | -122.0261 | 0.064087 | 1.4211e-13 | -0.063707 | -0.011566 | 0.062801 | -0.011555 | 0.051326 | -0.013124 | -0.00028425 | -0.0036108 | -0.0060034 | 0.040004 | -0.0016942 | -121.5139 | -9.5725 | -121.8273 | 0.038393 | 0.069043 | 0.14655 | -122.0731 | 0.02852 | 0.073618 | -0.056351 | -0.025376 | 0.073228 | 0.099323 | -0.16873 | -0.047019 | -0.025694 | 0.51212 | 0.19876 | 0.24578 | 0.004956 | 0.082458 | 121.8573 | -0.089463 | 122.0546 | 121.9697 | 0.11238 | 0.009141 | 0.035236 | 122.0645 | 122.0951 | 122.1726 | 112.4536 | -122.1372 | 122.0007 | 122.0993 | 122.1254 | 122.0997 | -0.23281
2479.0469 | 122.2549 | -122.0078 | 0.091553 | 1.4211e-13 | -0.063493 | -0.011566 | 0.062374 | -0.011555 | 0.051753 | -0.013124 | -7.0448e-05 | -0.004038 | -0.0057898 | 0.040218 | -0.001267 | -121.5185 | -9.6778 | -121.8319 | 0.038393 | 0.064464 | 0.13739 | -122.0822 | 0.033099 | 0.073618 | -0.051772 | -0.025376 | 0.073228 | 0.094744 | -0.17331 | -0.074487 | -0.05316 | 0.48923 | 0.17588 | 0.25036 | -0.027089 | 0.045834 | 121.8344 | -0.11693 | 122.0409 | 121.956 | 0.12153 | -0.018325 | 0.003191 | 122.0461 | 122.0722 | 122.1451 | 112.33 | -122.1738 | 121.9824 | 122.081 | 122.1025 | 122.0814 | -0.26486
2480.7969 | 122.2961 | -122.0032 | 0.068665 | 1.4211e-13 | -0.063279 | -0.010925 | 0.062374 | -0.011341 | 0.051326 | -0.013124 | -7.0448e-05 | -0.0036108 | -0.0062172 | 0.040004 | -0.001267 | -121.5139 | -9.7968 | -121.8319 | 0.042971 | 0.050727 | 0.14197 | -122.0777 | 0.033099 | 0.078197 | -0.047194 | -0.029954 | 0.077807 | 0.1039 | -0.16415 | -0.074486 | -0.025694 | 0.48923 | 0.1713 | 0.24578 | -0.017938 | 0.073301 | 121.839 | -0.098619 | 122.0363 | 121.956 | 0.11695 | 0.009142 | 0.035236 | 122.0461 | 122.0539 | 122.1451 | 112.2064 | -122.1463 | 121.9732 | 122.081 | 122.1071 | 122.0814 | -0.23281
2482.5 | 122.1771 | -122.0581 | 0.11444 | 1.4211e-13 | -0.063279 | -0.011139 | 0.06216 | -0.011341 | 0.051326 | -0.0054937 | 0.00014315 | -0.0038244 | -0.0060034 | 0.040218 | -0.0014806 | -121.5277 | -9.9067 | -121.8273 | 0.033814 | 0.073622 | 0.15112 | -122.0777 | 0.02852 | 0.087354 | -0.047194 | -0.025376 | 0.06865 | 0.1039 | -0.16873 | -0.019555 | -0.080627 | 0.53042 | 0.23081 | 0.25036 | -0.040819 | 0.036682 | 121.8894 | -0.13982 | 122.0866 | 122.0109 | 0.12153 | -0.045791 | -0.01054 | 122.0919 | 122.1317 | 122.2092 | 112.1514 | -122.1921 | 122.0327 | 122.1268 | 122.162 | 122.1455 | -0.28317
2484.25 | 122.3145 | -122.0078 | 0.054932 | 1.4211e-13 | -0.064134 | -0.011566 | 0.06216 | -0.011769 | 0.05154 | -0.013124 | -0.00028425 | -0.0042518 | -0.0062172 | 0.03979 | -0.0016942 | -121.5185 | -10.0257 | -121.8365 | 0.042971 | 0.069043 | 0.14197 | -122.0822 | 0.037677 | 0.087354 | -0.042615 | -0.020797 | 0.073228 | 0.1039 | -0.16415 | -0.074487 | -0.011961 | 0.48923 | 0.1713 | 0.24578 | 0.014111 | 0.087034 | 121.8436 | -0.075729 | 122.0454 | 121.9651 | 0.12153 | 0.018296 | 0.048969 | 122.0507 | 122.0768 | 122.1497 | 111.982 | -122.1372 | 121.987 | 122.081 | 122.1117 | 122.0951 | -0.21908
2486 | 122.2733 | -122.0078 | 0.082397 | 1.4211e-13 | -0.06392 | -0.011139 | 0.062374 | -0.011769 | 0.051753 | -0.0054937 | -0.00028425 | -0.004038 | -0.0057898 | 0.040218 | -0.0014806 | -121.5185 | -10.1448 | -121.8273 | 0.033814 | 0.069043 | 0.14197 | -122.0868 | 0.02852 | 0.082776 | -0.038036 | -0.029954 | 0.077807 | 0.1039 | -0.16873 | -0.079066 | -0.048583 | 0.48923 | 0.18045 | 0.25952 | -0.013354 | 0.059569 | 121.839 | -0.11235 | 122.0363 | 121.9697 | 0.13069 | -0.00459 | 0.021504 | 122.0416 | 122.0768 | 122.1497 | 111.863 | -122.1692 | 121.9778 | 122.0856 | 122.1117 | 122.0905 | -0.25112
2487.7031 | 122.1909 | -122.0398 | 0.11444 | 1.4211e-13 | -0.063707 | -0.011353 | 0.06216 | -0.011341 | 0.051326 | -0.013124 | -7.0448e-05 | -0.0038244 | -0.0060034 | 0.040004 | -0.0016942 | -121.5185 | -10.2547 | -121.8273 | 0.042971 | 0.064464 | 0.13739 | -122.0777 | 0.033099 | 0.073618 | -0.051772 | -0.029954 | 0.073228 | 0.1039 | -0.17331 | -0.037865 | -0.07147 | 0.52127 | 0.2125 | 0.25036 | -0.049977 | 0.022946 | 121.8665 | -0.14439 | 122.0729 | 121.988 | 0.12153 | -0.041213 | -0.01054 | 122.0828 | 122.1043 | 122.1772 | 111.7851 | -122.1921 | 122.0098 | 122.113 | 122.1437 | 122.1134 | -0.28775
2489.4531 | 122.1771 | -122.0535 | 0.12817 | 1.4211e-13 | -0.063493 | -0.011139 | 0.062588 | -0.011982 | 0.05154 | -0.013124 | -0.00028425 | -0.0038244 | -0.0062172 | 0.03979 | -0.001267 | -121.5185 | -10.3645 | -121.8319 | 0.042971 | 0.069043 | 0.13739 | -122.0777 | 0.019362 | 0.087354 | -0.051772 | -0.029954 | 0.073228 | 0.10848 | -0.17331 | -0.024132 | -0.085203 | 0.535 | 0.22165 | 0.24578 | -0.059131 | 0.009213 | 121.8802 | -0.15813 | 122.0729 | 122.0018 | 0.12153 | -0.054946 | -0.019694 | 122.0965 | 122.1226 | 122.1909 | 111.689 | -122.2058 | 122.0236 | 122.1268 | 122.162 | 122.1409 | -0.30148
2491.2031 | 122.3236 | -122.0078 | 0.07782 | 1.4211e-13 | -0.063707 | -0.011139 | 0.06216 | -0.011555 | 0.051326 | -0.0054937 | -7.0448e-05 | -0.0036108 | -0.0060034 | 0.040004 | -0.0016942 | -121.5185 | -10.4927 | -121.8319 | 0.042971 | 0.064464 | 0.13739 | -122.0868 | 0.023941 | 0.10567 | -0.070087 | -0.025376 | 0.073228 | 0.1039 | -0.17788 | -0.079066 | -0.034849 | 0.48923 | 0.17588 | 0.25494 | -0.013356 | 0.059567 | 121.8299 | -0.1032 | 122.0317 | 121.9377 | 0.1078 | -0.004592 | 0.026081 | 122.0507 | 122.0722 | 122.1451 | 111.515 | -122.1646 | 121.9824 | 122.081 | 122.1117 | 122.1134 | -0.2557
2492.8906 | 122.1863 | -122.0169 | 0.12817 | 1.4211e-13 | -0.06392 | -0.011566 | 0.06216 | -0.011341 | 0.051326 | -0.0054937 | -7.0448e-05 | -0.0038244 | -0.0062172 | 0.040218 | -0.0014806 | -121.5185 | -10.6255 | -121.8181 | 0.042971 | 0.073622 | 0.14197 | -122.0822 | 0.02852 | 0.091933 | -0.074666 | -0.020797 | 0.06865 | 0.10848 | -0.17331 | -0.065331 | -0.085203 | 0.49838 | 0.19877 | 0.2641 | -0.054552 | 0.013792 | 121.8436 | -0.14897 | 122.0454 | 121.9422 | 0.09864 | -0.059524 | -0.019694 | 122.0599 | 122.0905 | 122.1589 | 111.3914 | -122.2104 | 121.9961 | 122.0856 | 122.1254 | 122.1088 | -0.30148
2494.6406 | 122.2092 | -122.049 | 0.10986 | 1.4211e-13 | -0.063493 | -0.011353 | 0.062374 | -0.011555 | 0.051112 | -0.0054937 | -7.0448e-05 | -0.0038244 | -0.0062172 | 0.040004 | -0.0014806 | -121.5139 | -10.7446 | -121.8319 | 0.038393 | 0.073622 | 0.14655 | -122.0822 | 0.023941 | 0.096512 | -0.070087 | -0.020797 | 0.077807 | 0.099323 | -0.18246 | -0.033288 | -0.07147 | 0.535 | 0.21707 | 0.25036 | -0.036241 | 0.036682 | 121.8665 | -0.13066 | 122.0729 | 121.9789 | 0.11238 | -0.032056 | -0.01054 | 122.0873 | 122.1226 | 122.1955 | 111.3044 | -122.1921 | 122.0282 | 122.1268 | 122.1483 | 122.1455 | -0.29233
2496.3281 | 122.1954 | -122.0581 | 0.11902 | 1.4211e-13 | -0.063707 | -0.011566 | 0.06216 | -0.011769 | 0.051326 | -0.0054937 | -0.00049785 | -0.0033972 | -0.0064308 | 0.040218 | -0.0016942 | -121.5231 | -10.8545 | -121.8319 | 0.038393 | 0.069043 | 0.15112 | -122.0777 | 0.02852 | 0.082776 | -0.065509 | -0.025376 | 0.073228 | 0.10848 | -0.16873 | -0.019555 | -0.080626 | 0.535 | 0.22623 | 0.24578 | -0.049976 | 0.032104 | 121.8894 | -0.14439 | 122.0866 | 121.9926 | 0.10322 | -0.045791 | -0.010539 | 122.0965 | 122.1271 | 122.2092 | 111.2036 | -122.1967 | 122.0327 | 122.1313 | 122.1666 | 122.1409 | -0.28775
2498.1094 | 122.2229 | -122.049 | 0.10071 | 1.4211e-13 | -0.06392 | -0.011353 | 0.06216 | -0.011769 | 0.05154 | -0.0054937 | 0.00014315 | -0.0038244 | -0.0062172 | 0.040218 | -0.001267 | -121.5231 | -10.9369 | -121.8273 | 0.042971 | 0.073622 | 0.14197 | -122.0868 | 0.037677 | 0.091933 | -0.051772 | -0.025376 | 0.06865 | 0.099323 | -0.16415 | -0.037867 | -0.057737 | 0.52585 | 0.22165 | 0.25952 | -0.027086 | 0.041258 | 121.8848 | -0.12608 | 122.0866 | 121.9972 | 0.11238 | -0.032058 | -0.001385 | 122.0919 | 122.1226 | 122.1909 | 111.1121 | -122.1875 | 122.0236 | 122.1176 | 122.1483 | 122.1409 | -0.26486
2499.7969 | 122.2046 | -122.081 | 0.10529 | 1.4211e-13 | -0.06392 | -0.01178 | 0.06216 | -0.011982 | 0.05154 | -0.028385 | -7.0448e-05 | -0.0036108 | -0.0060034 | 0.040218 | -0.001908 | -121.5139 | -11.0651 | -121.8227 | 0.042971 | 0.069043 | 0.13739 | -122.096 | 0.02852 | 0.10567 | -0.051772 | -0.025376 | 0.073228 | 0.1039 | -0.16873 | -0.014981 | -0.062315 | 0.56705 | 0.25827 | 0.27325 | -0.036243 | 0.032101 | 121.9123 | -0.13066 | 122.1095 | 122.0292 | 0.11696 | -0.032058 | -0.001385 | 122.124 | 122.15 | 122.2184 | 111.0159 | -122.2013 | 122.0556 | 122.1542 | 122.1849 | 122.1867 | -0.27401
2501.5469 | 122.3282 | -122.0123 | 0.086975 | 1.4211e-13 | -0.06392 | -0.011353 | 0.06216 | -0.011128 | 0.051753 | -0.013124 | -7.0448e-05 | -0.0038244 | -0.0060034 | 0.040004 | -0.0016942 | -121.5185 | -11.2024 | -121.8273 | 0.042971 | 0.073622 | 0.14655 | -122.0868 | 0.037677 | 0.096512 | -0.042615 | -0.025376 | 0.073228 | 0.10848 | -0.16415 | -0.074488 | -0.044004 | 0.49381 | 0.18503 | 0.25952 | -0.013353 | 0.05957 | 121.8482 | -0.11235 | 122.05 | 121.9697 | 0.12153 | -0.013747 | 0.021505 | 122.0553 | 122.086 | 122.1589 | 110.8099 | -122.1738 | 121.987 | 122.0856 | 122.1208 | 122.1088 | -0.25112
2503.2969 | 122.2733 | -122.0215 | 0.091553 | 1.4211e-13 | -0.063707 | -0.011566 | 0.061947 | -0.011555 | 0.05154 | -0.028385 | -0.00049785 | -0.0038244 | -0.0062172 | 0.040218 | -0.0016942 | -121.5139 | -11.3261 | -121.8273 | 0.038393 | 0.064464 | 0.14655 | -122.0914 | 0.037677 | 0.091933 | -0.056351 | -0.025376 | 0.073228 | 0.099323 | -0.17331 | -0.069912 | -0.05316 | 0.50754 | 0.19419 | 0.2641 | -0.027089 | 0.054992 | 121.8482 | -0.11693 | 122.0592 | 121.9651 | 0.11695 | -0.018325 | 0.00777 | 122.0599 | 122.0859 | 122.168 | 110.6954 | -122.1829 | 121.9961 | 122.0947 | 122.1208 | 122.1134 | -0.26486
2505.0469 | 122.319 | -122.0169 | 0.082397 | 1.4211e-13 | -0.064348 | -0.011353 | 0.06216 | -0.011982 | 0.05154 | -0.013124 | -0.00028425 | -0.0038244 | -0.0060034 | 0.040431 | -0.0014806 | -121.5231 | -11.468 | -121.8273 | 0.042971 | 0.073622 | 0.14197 | -122.0914 | 0.037677 | 0.091933 | -0.047194 | -0.025376 | 0.06865 | 0.099323 | -0.16415 | -0.074489 | -0.039426 | 0.49381 | 0.18961 | 0.2641 | -0.008775 | 0.059569 | 121.8528 | -0.10777 | 122.0546 | 121.9697 | 0.11695 | -0.013747 | 0.016926 | 122.0599 | 122.0905 | 122.1589 | 110.5489 | -122.1738 | 121.9915 | 122.0856 | 122.1162 | 122.1088 | -0.24655
2506.7344 | 122.319 | -122.0261 | 0.086975 | 1.4211e-13 | -0.063707 | -0.011353 | 0.06216 | -0.011769 | 0.05154 | -0.0054937 | -7.0448e-05 | -0.004038 | -0.0060034 | 0.040645 | -0.0014806 | -121.5185 | -11.6054 | -121.8319 | 0.033814 | 0.064464 | 0.15112 | -122.0914 | 0.037677 | 0.087354 | -0.06093 | -0.029954 | 0.073228 | 0.099323 | -0.16873 | -0.065334 | -0.053161 | 0.50754 | 0.19419 | 0.25952 | -0.022511 | 0.064148 | 121.8573 | -0.11693 | 122.0637 | 121.9651 | 0.1078 | -0.013747 | 0.012348 | 122.0599 | 122.0905 | 122.1772 | 110.4207 | -122.1784 | 121.9961 | 122.0993 | 122.1254 | 122.1134 | -0.2557
2508.5 | 122.1817 | -122.0535 | 0.1236 | 1.4211e-13 | -0.06392 | -0.011566 | 0.06216 | -0.011555 | 0.051753 | -0.020755 | -7.0448e-05 | -0.004038 | -0.0062172 | 0.040645 | -0.0016942 | -121.5139 | -11.7427 | -121.8319 | 0.042971 | 0.064464 | 0.14655 | -122.096 | 0.042256 | 0.091933 | -0.051772 | -0.025376 | 0.073228 | 0.1039 | -0.15957 | -0.042447 | -0.080625 | 0.53958 | 0.22165 | 0.2641 | -0.059132 | 0.022949 | 121.894 | -0.14897 | 122.0958 | 122.0018 | 0.1078 | -0.050368 | -0.019695 | 122.0965 | 122.118 | 122.2001 | 110.3108 | -122.2196 | 122.0282 | 122.1268 | 122.1574 | 122.1455 | -0.28317
2510.2031 | 122.3373 | -122.0306 | 0.086975 | 1.4211e-13 | -0.064348 | -0.01178 | 0.06216 | -0.011769 | 0.051326 | -0.013124 | -7.0448e-05 | -0.0038244 | -0.0064308 | 0.040218 | -0.001908 | -121.5139 | -11.8801 | -121.8365 | 0.038393 | 0.073622 | 0.14655 | -122.0914 | 0.037677 | 0.091933 | -0.051772 | -0.016219 | 0.073228 | 0.1039 | -0.16873 | -0.060756 | -0.048582 | 0.51669 | 0.19419 | 0.25494 | -0.013353 | 0.05957 | 121.8619 | -0.10319 | 122.0683 | 121.9789 | 0.11696 | -0.013747 | 0.016926 | 122.069 | 122.1043 | 122.1772 | 110.1506 | -122.1784 | 122.0144 | 122.1039 | 122.1345 | 122.1226 | -0.2557
2511.9531 | 122.2687 | -122.0169 | 0.091553 | 1.4211e-13 | -0.064561 | -0.011566 | 0.06216 | -0.011555 | 0.05154 | -0.013124 | -7.0448e-05 | -0.004038 | -0.0062172 | 0.040431 | -0.001908 | -121.5139 | -12.0449 | -121.8319 | 0.047549 | 0.069043 | 0.14197 | -122.1006 | 0.037677 | 0.087354 | -0.047194 | -0.039111 | 0.082386 | 0.1039 | -0.16415 | -0.083647 | -0.044004 | 0.50296 | 0.18503 | 0.26868 | -0.02251 | 0.050413 | 121.8528 | -0.13066 | 122.0546 | 121.9697 | 0.11695 | -0.009167 | 0.012348 | 122.0645 | 122.0859 | 122.1589 | 109.972 | -122.1921 | 121.9778 | 122.0993 | 122.1208 | 122.1043 | -0.2557
2513.7031 | 122.3602 | -122.0261 | 0.082397 | 1.4211e-13 | -0.064134 | -0.011139 | 0.062374 | -0.011555 | 0.051112 | -0.013124 | -0.00028425 | -0.0042518 | -0.0066444 | 0.040859 | -0.001908 | -121.5139 | -12.2189 | -121.8365 | 0.038393 | 0.064464 | 0.14655 | -122.096 | 0.037677 | 0.082776 | -0.047194 | -0.034533 | 0.073228 | 0.1039 | -0.15499 | -0.069913 | -0.044004 | 0.51212 | 0.18961 | 0.25952 | -0.017933 | 0.064148 | 121.8711 | -0.11693 | 122.0637 | 121.9789 | 0.1078 | -0.009169 | 0.021504 | 122.0645 | 122.0905 | 122.1726 | 109.8072 | -122.1784 | 121.9915 | 122.0993 | 122.13 | 122.1088 | -0.23739
2515.3906 | 122.1954 | -122.0673 | 0.11902 | 1.4211e-13 | -0.06392 | -0.011353 | 0.062374 | -0.011769 | 0.05154 | -0.0054937 | 0.00014315 | -0.0038244 | -0.0062172 | 0.040645 | -0.0014806 | -121.5185 | -12.3608 | -121.8319 | 0.038393 | 0.069043 | 0.15112 | -122.0914 | 0.037677 | 0.087354 | -0.056351 | -0.039111 | 0.077807 | 0.099323 | -0.16873 | -0.024135 | -0.080626 | 0.54874 | 0.23539 | 0.25952 | -0.049976 | 0.032104 | 121.8985 | -0.15813 | 122.1049 | 122.0109 | 0.11238 | -0.041212 | -0.019696 | 122.1057 | 122.1363 | 122.2184 | 109.7064 | -122.2104 | 122.0281 | 122.1451 | 122.1666 | 122.1546 | -0.28775
2517.1406 | 122.2595 | -122.0535 | 0.10986 | 1.4211e-13 | -0.064134 | -0.011353 | 0.06216 | -0.011982 | 0.051112 | -0.013124 | -7.0448e-05 | -0.0036108 | -0.0062172 | 0.040859 | -0.0016942 | -121.5185 | -12.4982 | -121.8227 | 0.033814 | 0.069043 | 0.15112 | -122.1006 | 0.037677 | 0.091933 | -0.051772 | -0.029954 | 0.06865 | 0.10848 | -0.15957 | -0.047026 | -0.076049 | 0.535 | 0.23081 | 0.27783 | -0.04082 | 0.04126 | 121.894 | -0.13982 | 122.0912 | 122.0018 | 0.1078 | -0.041213 | -0.001383 | 122.0873 | 122.1226 | 122.2047 | 109.5554 | -122.2104 | 122.0236 | 122.1222 | 122.162 | 122.1455 | -0.26943
2518.8281 | 122.2595 | -122.0398 | 0.10986 | 1.4211e-13 | -0.064348 | -0.011139 | 0.06216 | -0.011769 | 0.05154 | -0.013124 | -7.0448e-05 | -0.0038244 | -0.0062172 | 0.040431 | -0.0014806 | -121.5185 | -12.6493 | -121.8227 | 0.042971 | 0.064464 | 0.14655 | -122.0914 | 0.042256 | 0.082776 | -0.051772 | -0.034533 | 0.073228 | 0.1039 | -0.15499 | -0.051601 | -0.066892 | 0.52127 | 0.21707 | 0.26868 | -0.045399 | 0.036682 | 121.8848 | -0.1444 | 122.0821 | 121.988 | 0.10322 | -0.036635 | -0.005962 | 122.0828 | 122.1043 | 122.1863 | 109.3905 | -122.2013 | 122.0053 | 122.113 | 122.1437 | 122.1226 | -0.26485
2520.5781 | 122.319 | -122.0123 | 0.091553 | 1.4211e-13 | -0.064348 | -0.01178 | 0.062588 | -0.011769 | 0.051326 | -0.013124 | -7.0448e-05 | -0.0038244 | -0.0060034 | 0.040431 | -0.001908 | -121.5277 | -12.8049 | -121.8227 | 0.038393 | 0.069043 | 0.14655 | -122.096 | 0.042256 | 0.096512 | -0.056351 | -0.04369 | 0.073228 | 0.1039 | -0.15957 | -0.083646 | -0.05316 | 0.48465 | 0.18961 | 0.27325 | -0.02251 | 0.054992 | 121.8528 | -0.13524 | 122.0546 | 121.956 | 0.10322 | -0.018325 | 0.012348 | 122.0507 | 122.0814 | 122.1589 | 109.2074 | -122.1875 | 121.9686 | 122.0856 | 122.1162 | 122.1088 | -0.25112
2522.2812 | 122.3053 | -122.0215 | 0.086975 | 1.4211e-13 | -0.064134 | -0.011566 | 0.06216 | -0.011555 | 0.05154 | -0.020755 | -7.0448e-05 | -0.0038244 | -0.0060034 | 0.040431 | -0.0016942 | -121.5185 | -12.9652 | -121.8227 | 0.038393 | 0.059885 | 0.14655 | -122.1051 | 0.042256 | 0.087354 | -0.051772 | -0.034533 | 0.073228 | 0.1039 | -0.15499 | -0.083649 | -0.048582 | 0.50296 | 0.19876 | 0.28241 | -0.02709 | 0.05957 | 121.8665 | -0.12151 | 122.0637 | 121.9697 | 0.10322 | -0.013747 | 0.016926 | 122.0599 | 122.0814 | 122.168 | 109.0563 | -122.1921 | 121.987 | 122.0947 | 122.1254 | 122.1088 | -0.24197
2524.0469 | 122.3511 | -122.0261 | 0.07782 | 1.4211e-13 | -0.064561 | -0.01178 | 0.061733 | -0.011769 | 0.05154 | 0.0021363 | -0.00049785 | -0.004038 | -0.0060034 | 0.040645 | -0.001908 | -121.5139 | -13.1712 | -121.8227 | 0.042971 | 0.069043 | 0.14655 | -122.1006 | 0.046835 | 0.10109 | -0.047194 | -0.039111 | 0.077807 | 0.1039 | -0.15957 | -0.074492 | -0.034849 | 0.51212 | 0.20334 | 0.27783 | -0.008777 | 0.068725 | 121.8665 | -0.11693 | 122.0729 | 121.9789 | 0.11238 | -1.3e-05 | 0.026081 | 122.069 | 122.0951 | 122.1726 | 108.8548 | -122.1784 | 121.987 | 122.1039 | 122.13 | 122.1272 | -0.23739
2525.7344 | 122.3557 | -122.0352 | 0.07782 | 1.4211e-13 | -0.064348 | -0.011353 | 0.06216 | -0.011769 | 0.051326 | -0.013124 | -7.0448e-05 | -0.0038244 | -0.0064308 | 0.040645 | -0.0016942 | -121.5139 | -13.3406 | -121.8181 | 0.038393 | 0.064464 | 0.15112 | -122.1051 | 0.051413 | 0.096512 | -0.056351 | -0.039111 | 0.077807 | 0.10848 | -0.15041 | -0.069916 | -0.039427 | 0.52127 | 0.21708 | 0.28699 | -0.013356 | 0.073303 | 121.8848 | -0.11693 | 122.0866 | 121.9789 | 0.094061 | -1.3e-05 | 0.03066 | 122.0736 | 122.0997 | 122.1863 | 108.6946 | -122.183 | 121.9961 | 122.113 | 122.1437 | 122.1317 | -0.22823
2527.4844 | 122.3419 | -122.0261 | 0.086975 | 1.4211e-13 | -0.064134 | -0.01178 | 0.062588 | -0.011555 | 0.051326 | -0.013124 | 0.00014315 | -0.0042518 | -0.0062172 | 0.040431 | -0.0021216 | -121.5139 | -13.4963 | -121.8227 | 0.047549 | 0.069043 | 0.14197 | -122.1097 | 0.051413 | 0.10567 | -0.056351 | -0.04369 | 0.077807 | 0.1039 | -0.15041 | -0.08365 | -0.039426 | 0.51212 | 0.20334 | 0.28699 | -0.017932 | 0.054991 | 121.8756 | -0.13067 | 122.0775 | 121.9697 | 0.094061 | -0.009168 | 0.016926 | 122.0736 | 122.0951 | 122.168 | 108.5297 | -122.1967 | 121.9824 | 122.1039 | 122.13 | 122.1317 | -0.23739
2529.2344 | 122.2549 | -122.0627 | 0.09613 | 1.4211e-13 | -0.064348 | -0.011994 | 0.062588 | -0.011769 | 0.051326 | -0.013124 | -0.00028425 | -0.0038244 | -0.0057898 | 0.040859 | -0.0021216 | -121.5139 | -13.7069 | -121.8181 | 0.047549 | 0.073622 | 0.14197 | -122.1051 | 0.046835 | 0.10109 | -0.042615 | -0.039111 | 0.077807 | 0.1039 | -0.15957 | -0.04245 | -0.048581 | 0.54874 | 0.24454 | 0.28699 | -0.022508 | 0.045836 | 121.9031 | -0.13524 | 122.1095 | 122.0201 | 0.11695 | -0.018323 | 0.007771 | 122.1102 | 122.1363 | 122.2046 | 108.3558 | -122.2013 | 122.0236 | 122.1405 | 122.1666 | 122.1638 | -0.2557
2531 | 122.2504 | -122.0764 | 0.10986 | 1.4211e-13 | -0.064561 | -0.011353 | 0.06216 | -0.011769 | 0.051967 | -0.013124 | 0.00014315 | -0.004038 | -0.0060034 | 0.040645 | -0.001908 | -121.5139 | -13.8947 | -121.8273 | 0.038393 | 0.073622 | 0.15112 | -122.1051 | 0.051413 | 0.11025 | -0.056351 | -0.034533 | 0.073228 | 0.1039 | -0.15499 | -0.028717 | -0.07147 | 0.56247 | 0.24912 | 0.27783 | -0.036241 | 0.04126 | 121.9214 | -0.1444 | 122.1278 | 122.0201 | 0.09864 | -0.036635 | -0.005962 | 122.1148 | 122.15 | 122.2275 | 108.1818 | -122.215 | 122.0419 | 122.1496 | 122.1803 | 122.1867 | -0.26485
2532.7031 | 122.374 | -122.0261 | 0.082397 | 1.4211e-13 | -0.064348 | -0.01178 | 0.062374 | -0.011769 | 0.05154 | -0.013124 | -7.0448e-05 | -0.0038244 | -0.0060034 | 0.040859 | -0.0021216 | -121.5094 | -14.0778 | -121.8273 | 0.042971 | 0.069043 | 0.14197 | -122.1097 | 0.051413 | 0.10567 | -0.051772 | -0.039111 | 0.077807 | 0.1039 | -0.15957 | -0.08365 | -0.039426 | 0.5167 | 0.19876 | 0.28241 | -0.013354 | 0.059569 | 121.8665 | -0.12151 | 122.0775 | 121.9743 | 0.1078 | -0.00459 | 0.021504 | 122.069 | 122.0951 | 122.168 | 107.9483 | -122.1921 | 121.987 | 122.1039 | 122.13 | 122.1317 | -0.24197
2534.4688 | 122.3282 | -122.0169 | 0.082397 | 1.4211e-13 | -0.064348 | -0.011353 | 0.061947 | -0.011982 | 0.05154 | -0.028385 | -7.0448e-05 | -0.0038244 | -0.0062172 | 0.040431 | -0.0016942 | -121.5048 | -14.2655 | -121.8273 | 0.047549 | 0.069043 | 0.14197 | -122.1097 | 0.051413 | 0.10109 | -0.051772 | -0.034533 | 0.077807 | 0.10848 | -0.15957 | -0.092805 | -0.034848 | 0.51212 | 0.18961 | 0.28241 | -0.013354 | 0.059569 | 121.8573 | -0.11693 | 122.0683 | 121.9651 | 0.1078 | -0.00459 | 0.026083 | 122.0645 | 122.0859 | 122.1589 | 107.7514 | -122.1921 | 121.9824 | 122.0947 | 122.1254 | 122.118 | -0.24197
2536.1562 | 122.3648 | -122.0215 | 0.073242 | 1.4211e-13 | -0.064561 | -0.011353 | 0.062374 | -0.011555 | 0.05154 | 0.0021363 | -7.0448e-05 | -0.004038 | -0.0060034 | 0.040859 | -0.0021216 | -121.5048 | -14.4807 | -121.8273 | 0.042971 | 0.073622 | 0.15112 | -122.1097 | 0.051413 | 0.10109 | -0.051772 | -0.039111 | 0.082386 | 0.1039 | -0.15499 | -0.088228 | -0.030271 | 0.5167 | 0.19419 | 0.28241 | 0.00038 | 0.077881 | 121.8665 | -0.11235 | 122.0729 | 121.9697 | 0.10322 | 0.009144 | 0.030659 | 122.0645 | 122.0951 | 122.1726 | 107.5408 | -122.183 | 121.9824 | 122.1039 | 122.1254 | 122.1226 | -0.22823
2537.9219 | 121.2524 | -50.7202 | 56.3553 | 1.4211e-13 | -0.064134 | -0.011353 | 0.06216 | -0.012196 | 0.04983 | -0.020755 | 0.63508 | 0.7209 | 0.40741 | 0.057952 | -0.019427 | -56.2948 | -3.1166 | -56.6051 | 64.4838 | 64.6136 | 64.2607 | -56.4891 | 10.3993 | 63.4018 | 40.2592 | 64.2613 | 64.3156 | 64.6301 | 8.3112 | -5.7689 | 8.1285 | -5.5746 | -5.8849 | -0.11597 | 8.2583 | 7.9054 | 59.0315 | 7.906 | 61.1195 | 90.9794 | 31.9479 | 7.9603 | 8.2749 | 115.204 | 115.3338 | 114.9809 | 47.6036 | -112.8444 | 114.9815 | 115.0358 | 115.3504 | 114.122 | -48.044
2539.6719 | 121.6736 | -0.082397 | 121.2067 | 1.4211e-13 | -0.063493 | -0.010284 | 0.062588 | -0.01241 | 0.049617 | -0.0054937 | 0.045862 | 0.024165 | 0.0098064 | 0.040859 | -0.001908 | 0.028518 | 5.5507 | -0.035879 | 121.4435 | 121.2732 | 121.127 | -0.15464 | 0.060571 | 0.10109 | -0.051772 | -0.04369 | 0.06865 | 0.099323 | -0.14583 | -0.072239 | 0.23684 | 0.11091 | 0.046518 | 0.11876 | 0.06651 | -0.079706 | -0.063436 | -121.2504 | 0.14297 | 0.030625 | 0.094061 | -121.138 | -121.1073 | 121.5259 | 121.3556 | 121.2094 | 5.6331 | -121.3613 | 0.038707 | 0.15105 | 0.18172 | 0.18349 | -121.3525
2541.4219 | 121.7697 | -0.09613 | 121.1334 | 1.4211e-13 | -0.063493 | -0.010498 | 0.062801 | -0.012196 | 0.04983 | -0.0054937 | 0.045648 | 0.024165 | 0.0098064 | 0.040859 | -0.001908 | 0.05141 | 5.3446 | -0.022144 | 121.5442 | 121.3693 | 121.2368 | -0.15006 | 0.055992 | 0.091933 | -0.051772 | -0.048268 | 0.073228 | 0.099323 | -0.15957 | -0.053927 | 0.41081 | 0.14754 | 0.073986 | 0.12791 | 0.23591 | 0.10342 | -0.06344 | -121.1817 | 0.15212 | 0.044358 | 0.1078 | -121.0602 | -121.0341 | 121.6404 | 121.4655 | 121.333 | 5.4408 | -121.2835 | 0.047862 | 0.16936 | 0.19545 | 0.18806 | -121.293
2543.125 | 121.3348 | -0.054932 | 117.8741 | 1.4211e-13 | -0.063707 | -0.010925 | 0.063015 | -0.01241 | 0.049617 | 0.0021363 | 0.045648 | 0.023951 | 0.0098064 | 0.040645 | -0.0021216 | 0.042253 | 5.2805 | -0.017566 | 121.6083 | 121.4289 | 121.2964 | -0.13632 | 0.055992 | 0.096512 | -0.051772 | -0.052847 | 0.064071 | 0.094744 | -0.15499 | -0.081388 | 3.7342 | 0.097185 | 0.037366 | 0.11875 | 3.5547 | 3.4222 | -0.10006 | -117.927 | 0.11092 | 0.00316 | 0.10322 | -117.8101 | -117.7794 | 121.6633 | 121.4838 | 121.3513 | 5.3355 | -118.0105 | 0.002085 | 0.119 | 0.14968 | 0.15144 | -118.0291
2544.875 | 117.1509 | -40.6631 | 76.6342 | 1.4211e-13 | -0.063707 | -0.011139 | 0.060878 | -0.011982 | 0.047053 | -0.0054937 | 0.045648 | 0.023951 | 0.0098064 | 0.040859 | -0.0023352 | -22.0576 | 0.8576 | -22.0711 | 96.0884 | 95.8693 | 95.8805 | -22.2663 | 0.051413 | 0.087354 | -0.070087 | -0.048268 | 0.059493 | 0.099323 | -0.15957 | 18.3969 | 19.4542 | 18.6055 | 18.592 | 0.19512 | 19.2351 | 19.2463 | 40.5036 | -76.6825 | 40.7146 | 40.5931 | 0.089483 | -76.5747 | -76.5349 | 136.7515 | 136.5324 | 136.5437 | 41.5208 | -98.9005 | 40.6149 | 40.7226 | 40.7625 | 40.7505 | -76.7938
2546.5625 | 121.3989 | -0.42572 | 120.0256 | 1.4211e-13 | -0.063707 | -0.010498 | 0.062588 | -0.012196 | 0.049403 | -0.013124 | 0.045648 | 0.023524 | 0.010234 | 0.040859 | -0.0023352 | -0.3286 | 5.1935 | -0.37925 | 120.8208 | 120.6504 | 120.5088 | -0.4889 | 0.042256 | 0.091933 | -0.06093 | -0.048268 | 0.064071 | 0.094744 | -0.15957 | -0.063177 | 0.79521 | 0.097124 | 0.04647 | 0.10965 | 0.62481 | 0.48321 | 0.26615 | -120.0739 | 0.46798 | 0.36479 | 0.09864 | -119.9616 | -119.9309 | 121.2466 | 121.0762 | 120.9346 | 5.6193 | -120.5145 | 0.37745 | 0.48979 | 0.52046 | 0.51765 | -120.1852
2548.3125 | 121.2845 | -0.27466 | 115.8234 | 1.4211e-13 | -0.063707 | -0.010498 | 0.062374 | -0.012196 | 0.049617 | -0.013124 | 0.045862 | 0.024165 | 0.010447 | 0.040645 | -0.0016942 | -0.1363 | 5.2393 | -0.19154 | 120.917 | 120.7512 | 120.6187 | -0.30574 | 0.051413 | 0.091933 | -0.06093 | -0.048268 | 0.064071 | 0.099323 | -0.16415 | -0.031082 | 5.0936 | 0.13835 | 0.083117 | 0.1142 | 4.9278 | 4.7954 | 0.11051 | -115.8716 | 0.32607 | 0.21373 | 0.10322 | -115.7593 | -115.724 | 121.1916 | 121.0258 | 120.8934 | 5.514 | -116.1291 | 0.22639 | 0.33873 | 0.37398 | 0.36659 | -115.9875
2550.0781 | 109.1034 | 0.091553 | 102.7176 | 1.4211e-13 | -0.06392 | -0.010712 | 0.062374 | -0.012196 | 0.049403 | -0.0054937 | 0.045862 | 0.02331 | 0.010661 | 0.040859 | -0.0023352 | -0.053893 | 5.2897 | -0.10913 | 120.7613 | 120.5863 | 120.4539 | -0.23706 | 0.051413 | 0.091933 | -0.06093 | -0.052847 | 0.059493 | 0.094744 | -0.15957 | -0.32861 | 18.0437 | -0.14545 | -0.20069 | 0.12792 | 17.8687 | 17.7363 | -0.25112 | -102.7704 | -0.04014 | -0.15248 | 0.09864 | -102.6581 | -102.6228 | 120.6698 | 120.4948 | 120.3624 | 5.1981 | -102.9546 | -0.1444 | -0.03206 | 0.003191 | 0.00038 | -102.8772
2551.7969 | 121.2708 | -0.15564 | 121.0693 | 1.4211e-13 | -0.06392 | -0.010925 | 0.062801 | -0.012196 | 0.049403 | -0.0054937 | 0.045648 | 0.023951 | 0.010661 | 0.041072 | -0.0021216 | -0.026423 | 5.2714 | -0.081662 | 120.9674 | 120.7878 | 120.6645 | -0.19585 | 0.055992 | 0.10109 | -0.06093 | -0.039111 | 0.059493 | 0.090166 | -0.16415 | -0.040206 | -0.10199 | 0.12922 | 0.073978 | 0.11418 | -0.28153 | -0.40482 | -0.008509 | -121.1084 | 0.21163 | 0.09471 | 0.10322 | -121.0098 | -120.9792 | 121.123 | 120.9434 | 120.8202 | 5.427 | -121.2652 | 0.11653 | 0.21513 | 0.24581 | 0.25673 | -121.2335
2553.5625 | 121.2662 | -0.1831 | 120.3964 | 1.4211e-13 | -0.063707 | -0.010284 | 0.062588 | -0.01241 | 0.049617 | -0.0054937 | 0.045648 | 0.023737 | 0.010447 | 0.040859 | -0.0021216 | -0.008109 | 5.2897 | -0.072505 | 121.0498 | 120.8748 | 120.7561 | -0.19585 | 0.060571 | 0.096512 | -0.056351 | -0.048268 | 0.064071 | 0.090166 | -0.16415 | -0.012741 | 0.65334 | 0.175 | 0.1106 | 0.12334 | 0.47839 | 0.35967 | 0.018956 | -120.4447 | 0.24368 | 0.12675 | 0.1078 | -120.3324 | -120.3063 | 121.2329 | 121.0579 | 120.9392 | 5.4728 | -120.5923 | 0.13484 | 0.24718 | 0.27327 | 0.27962 | -120.5606
2555.3281 | 121.3211 | -0.19226 | 106.7551 | 1.4211e-13 | -0.063493 | -0.010498 | 0.062801 | -0.01241 | 0.049403 | -0.013124 | 0.045862 | 0.023737 | 0.010661 | 0.041072 | -0.0021216 | -0.031001 | 5.2988 | -0.090818 | 121.0864 | 120.9206 | 120.779 | -0.2279 | 0.060571 | 0.087354 | -0.056351 | -0.048268 | 0.064071 | 0.094744 | -0.16873 | -0.035638 | 14.3313 | 0.16126 | 0.10144 | 0.13708 | 14.1655 | 14.0239 | 0.023533 | -106.8033 | 0.25283 | 0.13591 | 0.11238 | -106.691 | -106.6603 | 121.2786 | 121.1129 | 120.9712 | 5.4911 | -106.983 | 0.14399 | 0.25633 | 0.287 | 0.27962 | -106.9238
2557.0938 | 120.7809 | -61.2076 | 59.0286 | 1.4211e-13 | -0.064348 | -0.011353 | 0.061733 | -0.011982 | 0.050044 | -0.013124 | 0.045434 | 0.023951 | 0.010447 | 0.041072 | -0.001908 | -61.0884 | -6.5597 | -61.188 | 59.2369 | 59.1692 | 59.1418 | -61.3336 | 0.060571 | 0.091933 | -0.065509 | -0.04369 | 0.06865 | 0.090166 | -0.16415 | -0.12607 | 0.20832 | 0.1192 | 0.019609 | 0.14567 | 0.1406 | 0.11321 | 61.0434 | -59.0723 | 61.2682 | 61.1421 | 0.09864 | -58.96 | -58.9385 | 120.4445 | 120.3768 | 120.3494 | 54.6478 | -120.3623 | 61.1639 | 61.2762 | 61.2977 | 61.2995 | -59.1928
2558.7969 | 120.9503 | -116.3452 | 4.1107 | 1.4211e-13 | -0.064775 | -0.011566 | 0.061733 | -0.012623 | 0.050471 | -0.013124 | 0.045434 | 0.023737 | 0.010447 | 0.040859 | -0.001908 | -95.1607 | -14.3846 | -94.9162 | 25.4622 | 25.0013 | 25.686 | -95.5428 | 0.051413 | 0.10109 | -0.06093 | -0.04369 | 0.077807 | 0.094744 | -0.16873 | 20.8024 | 21.3515 | 21.1845 | 21.429 | 0.62663 | 20.8906 | 21.5753 | 116.1765 | -4.1544 | 116.3966 | 116.2843 | 0.1078 | -4.0329 | -4.016 | 141.8074 | 141.3465 | 142.0312 | 101.9607 | -99.6535 | 116.3015 | 116.423 | 116.44 | 116.4463 | -4.2794
2560.5625 | 120.9412 | -61.0428 | 59.4955 | 1.4211e-13 | -0.064561 | -0.011139 | 0.06216 | -0.011982 | 0.050044 | -0.013124 | 0.045221 | 0.023737 | 0.010447 | 0.041072 | -0.0021216 | -61.0472 | -6.4544 | -61.1376 | 59.4018 | 59.3982 | 59.3616 | -61.2787 | 0.06515 | 0.091933 | -0.06093 | -0.04369 | 0.064071 | 0.090166 | -0.16873 | -0.23591 | -0.093774 | -0.00439 | -0.094825 | 0.14109 | -0.097376 | -0.13393 | 60.8741 | -59.5392 | 61.1079 | 60.9819 | 0.1078 | -59.4315 | -59.4054 | 120.4446 | 120.441 | 120.4044 | 54.5884 | -120.7742 | 60.9991 | 61.1069 | 61.133 | 61.1347 | -59.6643
2562.2969 | 120.9091 | -114.4318 | 6.0104 | 1.4211e-13 | -0.064775 | -0.01178 | 0.061306 | -0.011982 | 0.050258 | -0.013124 | 0.045434 | 0.023737 | 0.010447 | 0.040859 | -0.0023352 | -108.0489 | -16.8891 | -107.9872 | 12.3771 | 12.0475 | 12.55 | -108.5469 | 0.055992 | 0.091933 | -0.06093 | -0.052847 | 0.073228 | 0.099323 | -0.15499 | 5.8848 | 6.3667 | 6.3829 | 6.4446 | 0.55978 | 6.0371 | 6.5395 | 114.2768 | -6.0633 | 114.4878 | 114.3708 | 0.094061 | -5.9372 | -5.9111 | 126.8089 | 126.4793 | 126.9817 | 97.5427 | -114.5574 | 114.3789 | 114.505 | 114.5311 | 114.5237 | -6.1654
2564.0625 | 121.106 | -116.2079 | 4.4449 | 1.4211e-13 | -0.064989 | -0.01178 | 0.061519 | -0.011555 | 0.050685 | -0.0054937 | 0.045434 | 0.023951 | 0.010875 | 0.040859 | -0.0021216 | -115.356 | -17.9742 | -115.6329 | 4.8594 | 4.8678 | 4.9403 | -116.0106 | 0.060571 | 0.087354 | -0.065509 | -0.048268 | 0.06865 | 0.1039 | -0.15499 | 0.1973 | 0.41455 | 0.85187 | 0.575 | 0.3777 | 0.42287 | 0.49546 | 116.0529 | -4.4932 | 116.2685 | 116.1424 | 0.089482 | -4.3762 | -4.341 | 121.0673 | 121.0756 | 121.1482 | 98.2337 | -120.4555 | 116.1596 | 116.2765 | 116.3118 | 116.2952 | -4.5999
2565.75 | 120.1721 | -0.10529 | 120.3918 | 1.4211e-13 | -0.06392 | -0.010712 | 0.061519 | -0.012196 | 0.048548 | -0.013124 | 0.045648 | 0.023737 | 0.010661 | 0.041072 | -0.001908 | -11.3259 | 4.8593 | -11.7609 | 107.6534 | 107.8615 | 107.089 | -11.4508 | 0.055992 | 0.091933 | -0.070087 | -0.057425 | 0.064071 | 0.094744 | -0.16415 | -11.3456 | -12.7384 | -11.2206 | -11.6556 | -0.31001 | -12.5303 | -13.3029 | -0.058863 | -120.4493 | 0.16128 | 0.035199 | 0.094062 | -120.3278 | -120.2971 | 107.7587 | 107.9668 | 107.1943 | 4.9646 | -131.8427 | 0.047861 | 0.16936 | 0.20003 | 0.19722 | -120.556
2567.5156 | 120.9045 | -0.10071 | 119.9387 | 1.4211e-13 | -0.064348 | -0.010712 | 0.062374 | -0.01241 | 0.049189 | -0.013124 | 0.045648 | 0.023951 | 0.010447 | 0.040859 | -0.0023352 | 0.055988 | 5.9948 | -0.003831 | 120.6972 | 120.536 | 120.4081 | -0.1409 | 0.06515 | 0.091933 | -0.056351 | -0.04369 | 0.064071 | 0.094744 | -0.16873 | -0.040191 | 0.75857 | 0.1567 | 0.096877 | 0.13707 | 0.59731 | 0.46946 | -0.06802 | -119.9823 | 0.16586 | 0.044357 | 0.11238 | -119.8746 | -119.8439 | 120.7979 | 120.6367 | 120.5088 | 6.0955 | -120.0796 | 0.057018 | 0.16478 | 0.19545 | 0.19264 | -120.1074
2569.2188 | 121.5637 | 0.022888 | 91.3605 | 1.4211e-13 | -0.06392 | -0.010712 | 0.062374 | -0.01241 | 0.049189 | -0.013124 | 0.045648 | 0.023737 | 0.010661 | 0.040645 | -0.0021216 | 0.060567 | 5.8574 | 0.009904 | 120.8163 | 120.6504 | 120.5226 | -0.13632 | 0.060571 | 0.096512 | -0.070087 | -0.048268 | 0.073228 | 0.094744 | -0.17331 | -0.15921 | 29.4558 | 0.037679 | -0.012984 | 0.14622 | 29.29 | 29.1621 | -0.19619 | -91.4087 | 0.037683 | -0.092975 | 0.10322 | -91.2872 | -91.2657 | 120.7934 | 120.6276 | 120.4997 | 5.8346 | -91.4968 | -0.071156 | 0.05034 | 0.071856 | 0.073624 | -91.5338
2570.9688 | 120.4147 | -0.059509 | 120.2271 | 1.4211e-13 | -0.064134 | -0.010925 | 0.062801 | -0.012196 | 0.049403 | -0.020755 | 0.045434 | 0.023737 | 0.010447 | 0.041072 | -0.001908 | 0.065145 | 5.8071 | 0.005325 | 120.8758 | 120.7145 | 120.5958 | -0.12716 | 0.06515 | 0.096512 | -0.06093 | -0.052847 | 0.077807 | 0.090166 | -0.16415 | -0.067653 | 0.64873 | 0.12465 | 0.064834 | 0.13249 | 0.4875 | 0.36879 | -0.10464 | -120.2799 | 0.12466 | -0.001421 | 0.10322 | -120.1492 | -120.1369 | 120.9353 | 120.7741 | 120.6553 | 5.8666 | -120.3542 | 0.006662 | 0.13732 | 0.14968 | 0.15602 | -120.3912
2572.7188 | 120.5612 | -0.07782 | 120.639 | 1.4211e-13 | -0.06392 | -0.010925 | 0.062588 | -0.01241 | 0.049403 | -0.020755 | 0.045648 | 0.023737 | 0.010447 | 0.041072 | -0.0021216 | 0.069723 | 5.8071 | 0.014482 | 120.9307 | 120.7603 | 120.6416 | -0.12258 | 0.051413 | 0.091933 | -0.065509 | -0.048268 | 0.073228 | 0.090166 | -0.16415 | -0.044763 | 0.29169 | 0.14754 | 0.092302 | 0.13706 | 0.1213 | 0.002589 | -0.086329 | -120.6873 | 0.12923 | 0.012311 | 0.09864 | -120.5658 | -120.5489 | 121.0085 | 120.8382 | 120.7194 | 5.8849 | -120.7616 | 0.029552 | 0.15105 | 0.16799 | 0.16975 | -120.8032
2574.4688 | 120.5383 | -0.032043 | 120.4926 | 1.4211e-13 | -0.064134 | -0.010712 | 0.062374 | -0.012196 | 0.049189 | -0.013124 | 0.045434 | 0.023737 | 0.010661 | 0.0415 | -0.0023352 | 0.069723 | 5.8254 | 0.014482 | 120.9765 | 120.8061 | 120.6874 | -0.118 | 0.051413 | 0.096512 | -0.06093 | -0.048268 | 0.073228 | 0.099323 | -0.15957 | -0.085961 | 0.48395 | 0.10177 | 0.046525 | 0.13249 | 0.31357 | 0.19486 | -0.12753 | -120.5408 | 0.083456 | -0.028887 | 0.09864 | -120.4193 | -120.3932 | 121.0086 | 120.8382 | 120.7195 | 5.8574 | -120.6106 | -0.016225 | 0.10527 | 0.13137 | 0.12856 | -120.6521
2576.2188 | 104.0359 | 0.09613 | 121.1472 | 1.4211e-13 | -0.064134 | -0.010712 | 0.062588 | -0.011982 | 0.049617 | -0.013124 | 0.045862 | 0.023737 | 0.010234 | 0.040859 | -0.001908 | 0.074302 | 5.8529 | 0.01906 | 121.0177 | 120.8382 | 120.7286 | -0.12258 | 0.046835 | 0.087354 | -0.06093 | -0.04369 | 0.073228 | 0.094744 | -0.16415 | -0.21871 | -0.12944 | -0.021828 | -0.07707 | 0.14164 | -0.30898 | -0.41854 | -0.26028 | -121.1908 | -0.049295 | -0.15706 | 0.10322 | -121.0739 | -121.0524 | 120.9216 | 120.742 | 120.6325 | 5.7567 | -121.2697 | -0.13982 | -0.022902 | -0.001386 | -0.008776 | -121.3113
2577.9844 | 120.4742 | -0.073242 | 120.2957 | 1.4211e-13 | -0.064134 | -0.010498 | 0.062588 | -0.01241 | 0.049403 | -0.013124 | 0.045434 | 0.023951 | 0.010447 | 0.041286 | -0.0021216 | 0.069723 | 5.8712 | 0.005325 | 121.0452 | 120.8794 | 120.7698 | -0.12716 | 0.051413 | 0.096512 | -0.06093 | -0.052847 | 0.059493 | 0.090166 | -0.16415 | -0.05392 | 0.74947 | 0.14297 | 0.078567 | 0.13249 | 0.58367 | 0.47411 | -0.090907 | -120.3486 | 0.12466 | 0.012312 | 0.10322 | -120.2362 | -120.2055 | 121.1184 | 120.9526 | 120.8431 | 5.9444 | -120.4229 | 0.020395 | 0.13273 | 0.16341 | 0.16975 | -120.4599
2579.7344 | 112.7747 | 0.17853 | 105.4596 | 1.4211e-13 | -0.064348 | -0.010498 | 0.062801 | -0.012623 | 0.049617 | -0.013124 | 0.045648 | 0.023524 | 0.010661 | 0.0415 | -0.0023352 | 0.074302 | 5.9215 | 0.01906 | 121.0818 | 120.9114 | 120.8065 | -0.12716 | 0.060571 | 0.091933 | -0.065509 | -0.057425 | 0.059493 | 0.099323 | -0.16415 | -0.30569 | 15.6222 | -0.10423 | -0.15947 | 0.14622 | 15.4518 | 15.3469 | -0.34268 | -105.517 | -0.11796 | -0.24404 | 0.09864 | -105.4001 | -105.3603 | 120.9033 | 120.7329 | 120.6279 | 5.743 | -105.5868 | -0.23595 | -0.11904 | -0.079205 | -0.086595 | -105.6237
2581.4219 | 120.8771 | 0.050354 | 120.3232 | 1.4211e-13 | -0.064348 | -0.010712 | 0.062588 | -0.012196 | 0.049617 | 0.0021363 | 0.045434 | 0.023737 | 0.010447 | 0.041286 | -0.0021216 | 0.07888 | 5.9673 | 0.014482 | 121.1139 | 120.9572 | 120.8339 | -0.12258 | 0.055992 | 0.082776 | -0.06093 | -0.04369 | 0.059493 | 0.094744 | -0.16415 | -0.17294 | 0.79068 | 0.028526 | -0.035872 | 0.13706 | 0.63405 | 0.51075 | -0.2145 | -120.3669 | 0.005638 | -0.11128 | 0.10322 | -120.2637 | -120.2284 | 121.0635 | 120.9069 | 120.7836 | 5.917 | -120.4458 | -0.094044 | 0.009139 | 0.04439 | 0.032422 | -120.4873
2583.1875 | 121.3669 | 0.036621 | 106.7139 | 1.4211e-13 | -0.064134 | -0.010712 | 0.062801 | -0.012196 | 0.049403 | -0.013124 | 0.045434 | 0.023524 | 0.010661 | 0.041713 | -0.0021216 | 0.074302 | 6.0085 | 0.014482 | 121.1368 | 120.9755 | 120.8614 | -0.118 | 0.060571 | 0.096512 | -0.06093 | -0.057425 | 0.064071 | 0.085587 | -0.15957 | -0.15463 | 14.4229 | 0.037681 | -0.022139 | 0.13249 | 14.2617 | 14.1475 | -0.19619 | -106.7713 | 0.02395 | -0.097551 | 0.09864 | -106.6498 | -106.6283 | 121.1001 | 120.9389 | 120.8248 | 5.9719 | -106.8319 | -0.094046 | 0.02745 | 0.048966 | 0.059891 | -106.8734
2584.875 | 121.2799 | -0.086975 | 113.1866 | 1.4211e-13 | -0.064561 | -0.010284 | 0.062588 | -0.01241 | 0.049403 | -0.013124 | 0.045434 | 0.022669 | 0.010661 | 0.0415 | -0.0023352 | 0.07888 | 6.0543 | 0.014482 | 121.1596 | 121.0076 | 120.8843 | -0.12716 | 0.055992 | 0.087354 | -0.065509 | -0.048268 | 0.064071 | 0.099323 | -0.16873 | -0.040187 | 7.973 | 0.16586 | 0.10146 | 0.14164 | 7.821 | 7.6976 | -0.081753 | -113.2349 | 0.14297 | 0.021466 | 0.10322 | -113.1226 | -113.0873 | 121.2466 | 121.0946 | 120.9713 | 6.1413 | -113.3138 | 0.038707 | 0.15105 | 0.1863 | 0.17433 | -113.3554
2586.625 | 121.051 | -0.018311 | 121.3623 | 1.4211e-13 | -0.064775 | -0.011139 | 0.062801 | -0.01241 | 0.048976 | -0.0054937 | 0.045221 | 0.022669 | 0.010447 | 0.041286 | -0.002549 | 0.083459 | 6.1001 | 0.023639 | 121.1917 | 121.0305 | 120.9163 | -0.13632 | 0.051413 | 0.091933 | -0.070087 | -0.052847 | 0.064071 | 0.094744 | -0.16873 | -0.11801 | -0.17061 | 0.10177 | 0.04195 | 0.15996 | -0.33181 | -0.44596 | -0.15042 | -121.4152 | 0.069724 | -0.051776 | 0.098641 | -121.2982 | -121.2676 | 121.21 | 121.0488 | 120.9347 | 6.1184 | -121.4986 | -0.034536 | 0.082382 | 0.11305 | 0.11024 | -121.531
2588.3906 | 121.4172 | -0.07782 | 121.2479 | 1.4211e-13 | -0.064348 | -0.010712 | 0.063015 | -0.01241 | 0.049617 | -0.0054937 | 0.045221 | 0.023096 | 0.010447 | 0.041286 | -0.0023352 | 0.083459 | 6.1688 | 0.01906 | 121.21 | 121.0488 | 120.9392 | -0.14548 | 0.055992 | 0.091933 | -0.06093 | -0.048268 | 0.054914 | 0.090166 | -0.16873 | -0.067658 | -0.037858 | 0.16128 | 0.09688 | 0.16454 | -0.19906 | -0.30863 | -0.090908 | -121.2961 | 0.13381 | 0.01689 | 0.1078 | -121.193 | -121.1577 | 121.2878 | 121.1266 | 121.0171 | 6.2466 | -121.3933 | 0.029552 | 0.13273 | 0.16799 | 0.16975 | -121.4166
2590.1562 | 121.3303 | -0.12817 | 120.7443 | 1.4211e-13 | -0.064348 | -0.010925 | 0.063229 | -0.01241 | 0.049403 | -0.0054937 | 0.045648 | 0.022883 | 0.010875 | 0.041286 | -0.0021216 | 0.088037 | 6.2191 | 0.023639 | 121.2421 | 121.0763 | 120.9576 | -0.118 | 0.060571 | 0.091933 | -0.065509 | -0.048268 | 0.064071 | 0.090166 | -0.16415 | 0.01017 | 0.49773 | 0.21621 | 0.15181 | 0.14164 | 0.33196 | 0.21323 | -0.035975 | -120.7926 | 0.18874 | 0.062665 | 0.09864 | -120.6803 | -120.6542 | 121.3702 | 121.2045 | 121.0857 | 6.3473 | -120.8623 | 0.079906 | 0.19224 | 0.21834 | 0.22011 | -120.9085
2591.9062 | 121.4859 | -0.19226 | 120.4971 | 1.4211e-13 | -0.064134 | -0.011139 | 0.062801 | -0.011982 | 0.04983 | -0.013124 | 0.045648 | 0.022883 | 0.010234 | 0.0415 | -0.0021216 | 0.010204 | 6.2604 | -0.054192 | 121.1642 | 121.003 | 120.8889 | -0.20958 | 0.055992 | 0.096512 | -0.065509 | -0.04369 | 0.064071 | 0.094744 | -0.15957 | -0.017322 | 0.66709 | 0.20246 | 0.13807 | 0.15539 | 0.50589 | 0.39174 | 0.032691 | -120.5408 | 0.24825 | 0.12675 | 0.094061 | -120.4331 | -120.4024 | 121.3565 | 121.1953 | 121.0811 | 6.4526 | -120.7067 | 0.14857 | 0.25633 | 0.287 | 0.28877 | -120.6567
2593.6094 | 120.6894 | -0.10071 | 116.7114 | 1.4211e-13 | -0.064775 | -0.010925 | 0.062588 | -0.012196 | 0.048976 | -0.0054937 | 0.045648 | 0.022883 | 0.010447 | 0.040859 | -0.002549 | 0.074302 | 6.4023 | 0.023639 | 120.4729 | 120.3116 | 120.1929 | -0.12716 | 0.051413 | 0.091933 | -0.065509 | -0.048268 | 0.06865 | 0.094744 | -0.15957 | -0.026454 | 3.7615 | 0.17501 | 0.12435 | 0.1508 | 3.6002 | 3.4815 | -0.058862 | -116.7597 | 0.15212 | 0.035199 | 0.094061 | -116.6428 | -116.6167 | 120.5736 | 120.4123 | 120.2936 | 6.503 | -116.8386 | 0.05244 | 0.16936 | 0.19545 | 0.19264 | -116.871
2595.3594 | 120.8725 | -0.13275 | 120.2911 | 1.4211e-13 | -0.064561 | -0.010498 | 0.062374 | -0.011769 | 0.049403 | -0.0054937 | 0.045221 | 0.022669 | 0.010875 | 0.041286 | -0.0027626 | 0.083459 | 6.3977 | 0.032795 | 120.7247 | 120.5589 | 120.4402 | -0.11342 | 0.051413 | 0.091933 | -0.065509 | -0.048268 | 0.059493 | 0.094744 | -0.15957 | 0.019326 | 0.43356 | 0.21621 | 0.16555 | 0.14622 | 0.26772 | 0.14903 | -0.026819 | -120.3394 | 0.18416 | 0.067242 | 0.094061 | -120.2316 | -120.1964 | 120.8574 | 120.6916 | 120.5729 | 6.5305 | -120.4046 | 0.084483 | 0.19224 | 0.2275 | 0.22468 | -120.4507
2597.0469 | 120.8908 | -0.11444 | 120.2133 | 1.4211e-13 | -0.064348 | -0.010925 | 0.062588 | -0.012196 | 0.049403 | -0.020755 | 0.045434 | 0.022669 | 0.010447 | 0.0415 | -0.0021216 | 0.088037 | 6.4664 | 0.032795 | 120.83 | 120.6688 | 120.5455 | -0.11342 | 0.046835 | 0.087354 | -0.06093 | -0.039111 | 0.06865 | 0.090166 | -0.16415 | 0.001016 | 0.61668 | 0.20248 | 0.14724 | 0.14622 | 0.45544 | 0.33216 | -0.049708 | -120.2524 | 0.16128 | 0.053511 | 0.10322 | -120.1447 | -120.1232 | 120.9444 | 120.7832 | 120.6599 | 6.5808 | -120.3267 | 0.07533 | 0.18309 | 0.20461 | 0.2018 | -120.3775
2598.7969 | 120.7535 | -0.14191 | 120.1904 | 1.4211e-13 | -0.064561 | -0.010925 | 0.062588 | -0.012196 | 0.04983 | 0.0021363 | 0.045221 | 0.022883 | 0.010447 | 0.0415 | -0.001908 | 0.097194 | 6.5213 | 0.032795 | 120.9033 | 120.742 | 120.6279 | -0.10885 | 0.055992 | 0.091933 | -0.065509 | -0.04369 | 0.064071 | 0.094744 | -0.16415 | 0.03306 | 0.71282 | 0.2391 | 0.1747 | 0.14164 | 0.55159 | 0.43746 | -0.022242 | -120.2341 | 0.1979 | 0.076398 | 0.09864 | -120.1264 | -120.0957 | 121.0452 | 120.8839 | 120.7698 | 6.6632 | -120.2993 | 0.098217 | 0.20598 | 0.23665 | 0.23384 | -120.3546
2600.5469 | 120.3415 | -0.11444 | 120.1767 | 1.4211e-13 | -0.064775 | -0.010712 | 0.062588 | -0.012196 | 0.049189 | -0.028385 | 0.045434 | 0.022669 | 0.010447 | 0.041286 | -0.002549 | 0.092615 | 6.59 | 0.028217 | 120.9445 | 120.7924 | 120.6828 | -0.11342 | 0.051413 | 0.087354 | -0.06093 | -0.04369 | 0.059493 | 0.094744 | -0.15957 | 0.001016 | 0.76776 | 0.20706 | 0.14266 | 0.14164 | 0.61569 | 0.50614 | -0.045129 | -120.2204 | 0.16585 | 0.053511 | 0.09864 | -120.1172 | -120.082 | 121.0589 | 120.9068 | 120.7973 | 6.7045 | -120.2901 | 0.070751 | 0.17393 | 0.20919 | 0.2018 | -120.3363
2602.2969 | 121.1792 | -0.13275 | 120.6253 | 1.4211e-13 | -0.064775 | -0.010925 | 0.062801 | -0.011982 | 0.049189 | -0.0054937 | 0.045434 | 0.022669 | 0.010234 | 0.041713 | -0.0021216 | 0.10177 | 6.6679 | 0.037373 | 121.004 | 120.8519 | 120.7286 | -0.10885 | 0.055992 | 0.087354 | -0.06093 | -0.052847 | 0.059493 | 0.094744 | -0.15957 | 0.023904 | 0.37867 | 0.23452 | 0.17012 | 0.14622 | 0.22661 | 0.10332 | -0.026819 | -120.6782 | 0.18874 | 0.071821 | 0.09864 | -120.5658 | -120.5306 | 121.1367 | 120.9847 | 120.8614 | 6.8006 | -120.7342 | 0.079904 | 0.19224 | 0.2275 | 0.2201 | -120.7849
2604 | 121.0831 | -0.082397 | 121.0144 | 1.4211e-13 | -0.064989 | -0.011139 | 0.062801 | -0.012196 | 0.049617 | -0.013124 | 0.045648 | 0.022883 | 0.010234 | 0.041286 | -0.0023352 | 0.10635 | 6.7274 | 0.037373 | 121.0452 | 120.8931 | 120.7698 | -0.10885 | 0.051413 | 0.096512 | -0.065509 | -0.048268 | 0.06865 | 0.099323 | -0.15957 | -0.02645 | 0.03078 | 0.18875 | 0.11977 | 0.14622 | -0.12128 | -0.24458 | -0.077173 | -121.0627 | 0.13381 | 0.016888 | 0.094061 | -120.9458 | -120.9151 | 121.1276 | 120.9755 | 120.8522 | 6.8098 | -121.1233 | 0.034129 | 0.15105 | 0.18172 | 0.17891 | -121.174
2605.75 | 120.8908 | -0.073242 | 120.6482 | 1.4211e-13 | -0.064775 | -0.010925 | 0.062588 | -0.012196 | 0.049617 | -0.020755 | 0.045434 | 0.022883 | 0.010447 | 0.0415 | -0.002549 | 0.11093 | 6.8098 | 0.041952 | 121.0818 | 120.9298 | 120.8065 | -0.11342 | 0.060571 | 0.096512 | -0.074666 | -0.048268 | 0.073228 | 0.094744 | -0.16415 | -0.040183 | 0.43362 | 0.18417 | 0.11519 | 0.15538 | 0.28156 | 0.15826 | -0.090907 | -120.6965 | 0.13381 | -0.001424 | 0.089483 | -120.575 | -120.5534 | 121.1551 | 121.003 | 120.8797 | 6.883 | -120.7616 | 0.024974 | 0.14647 | 0.16799 | 0.16975 | -120.8123
2607.5156 | 120.9641 | -0.10529 | 120.6116 | 1.4211e-13 | -0.064348 | -0.010712 | 0.062801 | -0.012196 | 0.049617 | -0.0054937 | 0.045434 | 0.022883 | 0.010661 | 0.041286 | -0.002549 | 0.11093 | 6.8876 | 0.04653 | 121.1139 | 120.9618 | 120.8522 | -0.10427 | 0.051413 | 0.091933 | -0.070087 | -0.04369 | 0.06865 | 0.099323 | -0.16873 | 0.001018 | 0.50229 | 0.21621 | 0.15182 | 0.1508 | 0.35024 | 0.24067 | -0.063442 | -120.6553 | 0.1567 | 0.035199 | 0.098641 | -120.5429 | -120.5122 | 121.2191 | 121.0671 | 120.9575 | 6.9929 | -120.7158 | 0.061596 | 0.17394 | 0.20461 | 0.19722 | -120.7803
2609.2188 | 120.8679 | -0.091553 | 120.3369 | 1.4211e-13 | -0.064561 | -0.010925 | 0.062374 | -0.01241 | 0.049403 | -0.013124 | 0.045434 | 0.022883 | 0.010875 | 0.041927 | -0.0021216 | 0.10177 | 6.9746 | 0.041952 | 121.1505 | 120.9939 | 120.8751 | -0.11342 | 0.051413 | 0.087354 | -0.06093 | -0.048268 | 0.06865 | 0.099323 | -0.15957 | -0.021872 | 0.81357 | 0.19332 | 0.1335 | 0.15538 | 0.65695 | 0.53822 | -0.068017 | -120.3852 | 0.14297 | 0.030623 | 0.09864 | -120.2683 | -120.2376 | 121.242 | 121.0854 | 120.9667 | 7.0662 | -120.4503 | 0.043285 | 0.1602 | 0.19088 | 0.17891 | -120.4965
2610.9688 | 121.3852 | -0.07782 | 121.2799 | 1.4211e-13 | -0.064561 | -0.010712 | 0.062588 | -0.01241 | 0.049403 | -0.013124 | 0.045862 | 0.022883 | 0.010234 | 0.0415 | -0.0021216 | 0.11093 | 7.0616 | 0.04653 | 121.178 | 121.0213 | 120.9118 | -0.099689 | 0.046835 | 0.091933 | -0.065509 | -0.048268 | 0.06865 | 0.094744 | -0.16415 | -0.021869 | -0.10195 | 0.18875 | 0.12435 | 0.14622 | -0.25857 | -0.36814 | -0.086329 | -121.3282 | 0.12466 | 0.012311 | 0.09864 | -121.2113 | -121.1852 | 121.2558 | 121.0992 | 120.9896 | 7.1394 | -121.3796 | 0.029552 | 0.14647 | 0.17256 | 0.16975 | -121.4441
2612.6562 | 121.0098 | -0.10071 | 120.4285 | 1.4211e-13 | -0.064561 | -0.010925 | 0.062801 | -0.012623 | 0.049617 | -0.0054937 | 0.045434 | 0.022456 | 0.010447 | 0.041286 | -0.002549 | 0.11093 | 7.1349 | 0.041952 | 121.2054 | 121.0442 | 120.9392 | -0.11342 | 0.051413 | 0.096512 | -0.070087 | -0.039111 | 0.077807 | 0.094744 | -0.15957 | -0.012717 | 0.77696 | 0.21164 | 0.14266 | 0.15538 | 0.61576 | 0.51077 | -0.058862 | -120.4676 | 0.15212 | 0.030621 | 0.089483 | -120.3507 | -120.3337 | 121.3061 | 121.1449 | 121.0399 | 7.2356 | -120.5419 | 0.061597 | 0.17852 | 0.19545 | 0.19722 | -120.588
2614.4062 | 121.0144 | -0.1236 | 120.7443 | 1.4211e-13 | -0.064775 | -0.011353 | 0.062801 | -0.012196 | 0.04983 | -0.020755 | 0.045434 | 0.022669 | 0.010447 | 0.041286 | -0.002549 | 0.11093 | 7.2173 | 0.04653 | 121.2283 | 121.0717 | 120.9621 | -0.11342 | 0.046835 | 0.091933 | -0.06093 | -0.052847 | 0.073228 | 0.094744 | -0.15957 | 0.010171 | 0.48399 | 0.23452 | 0.17013 | 0.15996 | 0.32738 | 0.2178 | -0.035974 | -120.7972 | 0.17043 | 0.062666 | 0.09864 | -120.6711 | -120.6496 | 121.3519 | 121.1953 | 121.0857 | 7.3409 | -120.8577 | 0.070749 | 0.19682 | 0.21834 | 0.21553 | -120.9039
2616.1562 | 120.7809 | -0.073242 | 120.7672 | 1.4211e-13 | -0.064989 | -0.011139 | 0.062801 | -0.01241 | 0.049617 | -0.013124 | 0.045434 | 0.022883 | 0.01002 | 0.041713 | -0.0027626 | 0.11551 | 7.2997 | 0.051108 | 121.2512 | 121.0946 | 120.9896 | -0.10885 | 0.042256 | 0.091933 | -0.065509 | -0.04369 | 0.059493 | 0.094744 | -0.16415 | -0.035605 | 0.484 | 0.18875 | 0.12435 | 0.15996 | 0.32738 | 0.22239 | -0.090907 | -120.8109 | 0.1155 | 0.007733 | 0.09864 | -120.7077 | -120.6725 | 121.3245 | 121.1678 | 121.0628 | 7.3729 | -120.8761 | 0.029552 | 0.13273 | 0.16799 | 0.16518 | -120.9314
2617.8438 | 121.106 | -0.091553 | 121.1975 | 1.4211e-13 | -0.064989 | -0.011139 | 0.062801 | -0.01241 | 0.049617 | 0.0021363 | 0.045434 | 0.022883 | 0.010447 | 0.041713 | -0.0023352 | 0.12009 | 7.3867 | 0.04653 | 121.2741 | 121.1129 | 121.0079 | -0.10885 | 0.051413 | 0.096512 | -0.06093 | -0.04369 | 0.06865 | 0.094744 | -0.15957 | -0.017294 | 0.076593 | 0.21164 | 0.13808 | 0.15538 | -0.084597 | -0.18959 | -0.068017 | -121.2412 | 0.14297 | 0.030623 | 0.09864 | -121.1289 | -121.1028 | 121.3657 | 121.2045 | 121.0995 | 7.4782 | -121.3064 | 0.047863 | 0.1602 | 0.1863 | 0.18806 | -121.3571
2619.5938 | 121.0419 | -0.10071 | 120.9412 | 1.4211e-13 | -0.064348 | -0.011139 | 0.062588 | -0.011982 | 0.048976 | -0.0054937 | 0.045221 | 0.022883 | 0.010447 | 0.0415 | -0.0027626 | 0.088037 | 7.4783 | 0.014482 | 120.83 | 120.6825 | 120.5638 | -0.12258 | 0.042256 | 0.096512 | -0.065509 | -0.057425 | 0.064071 | 0.094744 | -0.15499 | -0.021875 | -0.11116 | 0.18874 | 0.11519 | 0.13706 | -0.25867 | -0.37737 | -0.054283 | -120.9986 | 0.14296 | 0.035199 | 0.089482 | -120.8771 | -120.8464 | 120.9307 | 120.7832 | 120.6645 | 7.579 | -121.0637 | 0.043283 | 0.16478 | 0.19545 | 0.19722 | -121.0962
2621.2812 | 121.2387 | -0.11902 | 112.7792 | 1.4211e-13 | -0.064989 | -0.011139 | 0.062374 | -0.01241 | 0.049617 | -0.020755 | 0.045434 | 0.022669 | 0.010447 | 0.041713 | -0.002549 | 0.11093 | 7.5469 | 0.051108 | 121.1047 | 120.9481 | 120.8477 | -0.12258 | 0.046835 | 0.091933 | -0.070087 | -0.052847 | 0.06865 | 0.094744 | -0.15957 | -0.003564 | 8.3255 | 0.22995 | 0.17013 | 0.17369 | 8.1688 | 8.0684 | -0.040551 | -112.8321 | 0.16585 | 0.048932 | 0.089483 | -112.7106 | -112.6845 | 121.2237 | 121.0671 | 120.9667 | 7.666 | -112.9018 | 0.066172 | 0.18767 | 0.21376 | 0.21095 | -112.9388
2623.0312 | 121.2387 | -57.6324 | 63.0753 | 1.4211e-13 | -0.065202 | -0.011566 | 0.06216 | -0.011982 | 0.050044 | 0.0021363 | 0.045648 | 0.022883 | 0.010447 | 0.0415 | -0.002549 | -58.6939 | -10.5614 | -58.8027 | 62.0023 | 61.9578 | 61.9256 | -58.9847 | 0.046835 | 0.091933 | -0.065509 | -0.048268 | 0.073228 | 0.099323 | -0.15499 | -1.3522 | -1.073 | -1.0614 | -1.1702 | 0.18197 | -1.1175 | -1.1496 | 57.4775 | -63.1235 | 57.6793 | 57.5669 | 0.089482 | -63.002 | -62.9759 | 119.6347 | 119.5902 | 119.5581 | 47.071 | -122.0599 | 57.5842 | 57.7057 | 57.7318 | 57.7244 | -63.2302
2624.7969 | 120.4422 | -11.6135 | 109.1354 | 1.4211e-13 | -0.064989 | -0.010712 | 0.062801 | -0.012196 | 0.049617 | -0.0054937 | 0.045648 | 0.022883 | 0.010447 | 0.041927 | -0.002549 | -11.5502 | 4.2366 | -11.6739 | 109.4573 | 109.3313 | 109.2409 | -11.6477 | 0.037677 | 0.096512 | -0.065509 | -0.04369 | 0.06865 | 0.094744 | -0.16415 | -0.034272 | 0.32185 | 0.063239 | -0.060404 | -0.026132 | 0.1959 | 0.10547 | 11.4493 | -109.1791 | 11.6511 | 11.548 | 0.09864 | -109.0668 | -109.0407 | 121.0707 | 120.9448 | 120.8544 | 15.8501 | -120.7832 | 11.5698 | 11.6821 | 11.7082 | 11.71 | -109.2996
2626.5625 | 120.4926 | -12.6022 | 108.3481 | 1.4211e-13 | -0.064989 | -0.010925 | 0.062801 | -0.01241 | 0.050044 | -0.020755 | 0.045648 | 0.022883 | 0.010234 | 0.0415 | -0.002549 | -12.3972 | 3.9939 | -12.5117 | 108.6744 | 108.5392 | 108.4534 | -12.4903 | 0.042256 | 0.087354 | -0.070087 | -0.048268 | 0.059493 | 0.099323 | -0.15957 | 0.11198 | 0.3263 | 0.20501 | 0.09054 | -0.021436 | 0.1911 | 0.1053 | 12.4427 | -108.3964 | 12.6445 | 12.5321 | 0.089483 | -108.2886 | -108.2488 | 121.2766 | 121.1414 | 121.0556 | 16.5962 | -120.8383 | 12.554 | 12.6617 | 12.7016 | 12.6896 | -108.5077
2628.2656 | 121.0876 | -15.8386 | 105.3406 | 1.4211e-13 | -0.065202 | -0.011353 | 0.063015 | -0.01241 | 0.050044 | -0.020755 | 0.045434 | 0.023096 | 0.010234 | 0.0415 | -0.002549 | -15.9958 | 2.9088 | -16.069 | 105.1261 | 104.9997 | 104.9141 | -16.0481 | 0.037677 | 0.087354 | -0.065509 | -0.04369 | 0.059493 | 0.090166 | -0.16415 | -0.20946 | -0.21445 | -0.15722 | -0.23039 | -0.020935 | -0.3409 | -0.42645 | 15.6745 | -105.3843 | 15.8763 | 15.7731 | 0.09864 | -105.2811 | -105.2504 | 120.9648 | 120.8383 | 120.7527 | 18.7474 | -121.3887 | 15.7949 | 15.8981 | 15.9288 | 15.926 | -105.5047
2630.0312 | 121.1426 | -16.8594 | 104.3884 | 1.4211e-13 | -0.064989 | -0.011139 | 0.062801 | -0.012196 | 0.049617 | -0.0054937 | 0.045221 | 0.022883 | 0.010447 | 0.041286 | -0.0023352 | -16.6002 | 2.7623 | -16.6688 | 104.563 | 104.4365 | 104.351 | -16.6525 | 0.033099 | 0.087354 | -0.074666 | -0.04369 | 0.06865 | 0.094744 | -0.15957 | 0.20693 | 0.17456 | 0.25925 | 0.19066 | -0.016271 | 0.048042 | -0.037469 | 16.6999 | -104.4321 | 16.8925 | 16.7848 | 0.084904 | -104.3198 | -104.2937 | 121.4224 | 121.2959 | 121.2104 | 19.6217 | -121.0409 | 16.8157 | 16.9281 | 16.9542 | 16.9468 | -104.548
2631.7812 | 121.3943 | -18.3151 | 102.9282 | 1.4211e-13 | -0.064989 | -0.010925 | 0.062801 | -0.012196 | 0.04983 | -0.013124 | 0.045434 | 0.022669 | 0.010234 | 0.041713 | -0.002549 | -18.0103 | 2.3365 | -18.1109 | 103.1849 | 103.0628 | 102.982 | -18.0537 | 0.037677 | 0.091933 | -0.070087 | -0.057425 | 0.06865 | 0.094744 | -0.16415 | 0.26147 | 0.25673 | 0.30479 | 0.20419 | -0.057279 | 0.13463 | 0.053795 | 18.151 | -102.9856 | 18.3528 | 18.245 | 0.094062 | -102.8595 | -102.8334 | 121.5 | 121.3779 | 121.2971 | 20.6516 | -120.9818 | 18.2577 | 18.3838 | 18.4099 | 18.4071 | -103.0923
2633.5312 | 121.5271 | -58.1268 | 62.8738 | 1.4211e-13 | -0.065416 | -0.011353 | 0.062588 | -0.01241 | 0.050258 | -0.0054937 | 0.045434 | 0.022669 | 0.01002 | 0.041713 | -0.002549 | -58.1857 | -10.9735 | -58.2441 | 62.7989 | 62.7454 | 62.7315 | -58.4901 | 0.037677 | 0.096512 | -0.070087 | -0.048268 | 0.077807 | 0.090166 | -0.16415 | -0.3633 | -0.074907 | -0.058853 | -0.11731 | 0.246 | -0.12848 | -0.14238 | 57.9627 | -62.9221 | 58.1645 | 58.0567 | 0.094062 | -62.796 | -62.7837 | 120.9258 | 120.8722 | 120.8583 | 47.1533 | -121.364 | 58.0786 | 58.2046 | 58.217 | 58.2233 | -63.038
2635.25 | 121.5317 | -58.3054 | 62.7502 | 1.4211e-13 | -0.06563 | -0.011353 | 0.062588 | -0.01241 | 0.050471 | -0.013124 | 0.045221 | 0.022883 | 0.010447 | 0.041927 | -0.002549 | -58.1353 | -10.9094 | -58.1846 | 62.8218 | 62.8186 | 62.8001 | -58.4398 | 0.02852 | 0.091933 | -0.065509 | -0.04369 | 0.064071 | 0.090166 | -0.16415 | -0.13441 | 0.071581 | 0.17004 | 0.12074 | 0.25515 | 0.068381 | 0.049897 | 58.1412 | -62.7939 | 58.3339 | 58.2399 | 0.09864 | -62.6862 | -62.6601 | 121.1272 | 121.124 | 121.1055 | 47.396 | -121.19 | 58.2617 | 58.3694 | 58.3955 | 58.3973 | -62.9144
2637 | 121.4081 | -58.5938 | 62.6404 | 1.4211e-13 | -0.065202 | -0.011139 | 0.062588 | -0.011769 | 0.050258 | -0.0054937 | 0.045221 | 0.022456 | 0.010234 | 0.0415 | -0.002549 | -58.3322 | -11.0468 | -58.3861 | 62.6387 | 62.5851 | 62.6262 | -58.568 | 0.037677 | 0.091933 | -0.065509 | -0.039111 | 0.06865 | 0.090166 | -0.16873 | 0.025774 | -0.001691 | 0.26156 | 0.20768 | 0.18191 | -0.055281 | -0.014226 | 58.425 | -62.6795 | 58.6314 | 58.5282 | 0.10322 | -62.5717 | -62.5502 | 121.2324 | 121.1788 | 121.2199 | 47.547 | -121.2084 | 58.5546 | 58.6624 | 58.6839 | 58.6857 | -62.8091
2638.6875 | 121.5088 | -58.1863 | 63.0386 | 1.4211e-13 | -0.06563 | -0.011566 | 0.062374 | -0.011982 | 0.050471 | -0.020755 | 0.045221 | 0.022669 | 0.010447 | 0.041713 | -0.002549 | -58.0941 | -11.0468 | -58.1526 | 62.8905 | 62.8278 | 62.8185 | -58.3299 | 0.033099 | 0.091933 | -0.065509 | -0.048268 | 0.064071 | 0.099323 | -0.15499 | -0.14353 | -0.14813 | 0.092224 | 0.033768 | 0.1773 | -0.21085 | -0.22018 | 58.0313 | -63.0869 | 58.2194 | 58.1208 | 0.089482 | -62.9746 | -62.9393 | 121.0768 | 121.0141 | 121.0048 | 47.1396 | -121.3685 | 58.1381 | 58.2504 | 58.2857 | 58.2783 | -63.1936
2640.4531 | 121.4401 | -56.0394 | 65.2496 | 1.4211e-13 | -0.065843 | -0.011566 | 0.062801 | -0.01241 | 0.050258 | -0.013124 | 0.045434 | 0.022669 | 0.010234 | 0.0415 | -0.002549 | -55.7637 | -10.3096 | -55.8222 | 65.2575 | 65.1859 | 65.1673 | -55.99 | 0.033099 | 0.096512 | -0.074666 | -0.04369 | 0.06865 | 0.099323 | -0.16415 | 0.049387 | 0.007894 | 0.27571 | 0.2172 | 0.16782 | -0.063705 | -0.082355 | 55.8753 | -65.2933 | 56.0725 | 55.9648 | 0.089483 | -65.181 | -65.1503 | 121.297 | 121.2254 | 121.2067 | 45.7298 | -121.2397 | 55.9957 | 56.1081 | 56.1388 | 56.1359 | -65.4138
2642.2031 | 120.7031 | -33.0505 | 88.2385 | 1.4211e-13 | -0.065416 | -0.011353 | 0.062588 | -0.011982 | 0.050044 | -0.013124 | 0.045221 | 0.022456 | 0.010234 | 0.041713 | -0.0023352 | -34.0988 | -2.6542 | -34.1578 | 87.101 | 87.0411 | 86.9523 | -34.1531 | 0.033099 | 0.10109 | -0.079245 | -0.048268 | 0.06865 | 0.099323 | -0.16415 | -1.1026 | -1.1375 | -1.0482 | -1.1073 | -0.004654 | -1.1974 | -1.2863 | 32.8864 | -88.2868 | 33.0836 | 32.9713 | 0.084904 | -88.1699 | -88.1392 | 120.1516 | 120.0917 | 120.0028 | 30.3964 | -122.3917 | 33.0023 | 33.1192 | 33.1499 | 33.1516 | -88.4027
2643.8906 | 121.3623 | -23.8174 | 97.5403 | 1.4211e-13 | -0.06563 | -0.010925 | 0.062801 | -0.01241 | 0.050258 | -0.020755 | 0.045434 | 0.022669 | 0.010234 | 0.041713 | -0.0027626 | -24.0584 | 0.68362 | -24.1222 | 97.233 | 97.1377 | 97.0527 | -24.107 | 0.033099 | 0.091933 | -0.079245 | -0.04369 | 0.06865 | 0.099323 | -0.16415 | -0.28955 | -0.30729 | -0.24094 | -0.30477 | -0.015223 | -0.40262 | -0.48762 | 23.6533 | -97.584 | 23.8505 | 23.7382 | 0.084904 | -97.4716 | -97.441 | 121.0504 | 120.9551 | 120.8701 | 24.5011 | -121.6473 | 23.7738 | 23.8861 | 23.9168 | 23.9094 | -97.7044
2645.6406 | 121.2341 | -15.1062 | 106.3477 | 1.4211e-13 | -0.06563 | -0.010925 | 0.062801 | -0.01241 | 0.049617 | -0.013124 | 0.045221 | 0.022669 | 0.01002 | 0.042141 | -0.0027626 | -15.0481 | 3.7513 | -15.135 | 106.2433 | 106.1261 | 106.0359 | -15.1415 | 0.023941 | 0.091933 | -0.070087 | -0.04369 | 0.064071 | 0.099323 | -0.15499 | -0.035255 | -0.1044 | 0.058088 | -0.028847 | 0.006408 | -0.22156 | -0.31177 | 14.9512 | -106.3913 | 15.1301 | 15.0361 | 0.084904 | -106.2836 | -106.2483 | 121.3495 | 121.2323 | 121.1421 | 18.8575 | -121.4891 | 15.0625 | 15.1703 | 15.2055 | 15.1981 | -106.5026
2647.3906 | 121.1243 | -13.5361 | 107.84 | 1.4211e-13 | -0.06563 | -0.011353 | 0.062801 | -0.012196 | 0.04983 | -0.0054937 | 0.045434 | 0.022669 | 0.010234 | 0.041927 | -0.0031898 | -13.5189 | 4.2275 | -13.6196 | 107.7816 | 107.6555 | 107.5743 | -13.635 | 0.023941 | 0.091933 | -0.070087 | -0.04369 | 0.064071 | 0.090166 | -0.15957 | -0.098918 | -0.058372 | 0.01714 | -0.083565 | 0.015353 | -0.18451 | -0.26567 | 13.3765 | -107.8837 | 13.56 | 13.466 | 0.089483 | -107.7759 | -107.7498 | 121.3177 | 121.1915 | 121.1104 | 17.7635 | -121.475 | 13.4924 | 13.6001 | 13.6262 | 13.628 | -107.9995
2649.1406 | 121.3028 | -14.3509 | 107.016 | 1.4211e-13 | -0.065416 | -0.011353 | 0.063015 | -0.012196 | 0.050044 | -0.0054937 | 0.045007 | 0.022456 | 0.010447 | 0.041927 | -0.0027626 | -14.5079 | 3.8978 | -14.5902 | 106.8018 | 106.6801 | 106.6036 | -14.624 | 0.033099 | 0.091933 | -0.065509 | -0.04369 | 0.073228 | 0.085587 | -0.15957 | -0.27315 | -0.21417 | -0.15697 | -0.23934 | 0.033804 | -0.33585 | -0.41236 | 14.1913 | -107.0597 | 14.384 | 14.2854 | 0.094061 | -106.9428 | -106.9304 | 121.1527 | 121.031 | 120.9545 | 18.2487 | -121.64 | 14.3072 | 14.4241 | 14.4365 | 14.4428 | -107.1756
2650.8906 | 120.1721 | -23.259 | 97.5128 | 1.4211e-13 | -0.065416 | -0.011353 | 0.062588 | -0.012196 | 0.04983 | -0.0054937 | 0.045007 | 0.022669 | 0.010234 | 0.042141 | -0.0029762 | -25.9859 | -0.094744 | -26.1275 | 94.5729 | 94.5918 | 94.4154 | -26.0851 | 0.037677 | 0.087354 | -0.070087 | -0.048268 | 0.06865 | 0.099323 | -0.15957 | -2.8261 | -2.9399 | -2.7269 | -2.8685 | -0.042415 | -2.921 | -3.0974 | 23.0994 | -97.5611 | 23.2966 | 23.1889 | 0.089483 | -97.4442 | -97.4135 | 117.8319 | 117.8508 | 117.6744 | 23.1642 | -123.5979 | 23.2107 | 23.3276 | 23.3583 | 23.3463 | -97.6724
2652.5781 | 121.2662 | -15.1794 | 105.9814 | 1.4211e-13 | -0.065416 | -0.011353 | 0.062801 | -0.012196 | 0.049617 | -0.020755 | 0.045221 | 0.022456 | 0.010447 | 0.041927 | -0.0027626 | -15.3915 | 3.7604 | -15.515 | 105.6343 | 105.5079 | 105.4224 | -15.4757 | 0.037677 | 0.091933 | -0.070087 | -0.04369 | 0.06865 | 0.094744 | -0.16415 | -0.29627 | -0.34711 | -0.21205 | -0.3356 | -0.039329 | -0.47351 | -0.55909 | 15.0153 | -106.0251 | 15.2171 | 15.1094 | 0.094062 | -105.9128 | -105.8867 | 120.8138 | 120.6874 | 120.6018 | 18.9399 | -121.4572 | 15.1358 | 15.2481 | 15.2742 | 15.2714 | -106.1456
2654.2812 | 120.5154 | -15.271 | 105.542 | 1.4211e-13 | -0.06563 | -0.010925 | 0.062588 | -0.012623 | 0.050044 | -0.020755 | 0.045434 | 0.022669 | 0.010447 | 0.041927 | -0.002549 | -15.0344 | 3.7925 | -15.1488 | 106.0876 | 105.9567 | 105.8756 | -15.1323 | 0.02852 | 0.087354 | -0.070087 | -0.048268 | 0.064071 | 0.094744 | -0.15957 | 0.1387 | 0.5456 | 0.23662 | 0.12221 | -0.016485 | 0.41468 | 0.33364 | 15.1114 | -105.5903 | 15.2995 | 15.2009 | 0.089483 | -105.4779 | -105.4472 | 121.3586 | 121.2277 | 121.1466 | 19.0635 | -120.6743 | 15.2227 | 15.3351 | 15.3657 | 15.3583 | -105.7016
2656.0312 | 121.5179 | -59.3216 | 61.702 | 1.4211e-13 | -0.065843 | -0.011353 | 0.06216 | -0.012196 | 0.050258 | -0.0054937 | 0.045007 | 0.022456 | 0.010234 | 0.041713 | -0.002549 | -58.964 | -12.7637 | -59.0408 | 61.9748 | 61.9166 | 61.9027 | -59.3281 | 0.033099 | 0.096512 | -0.070087 | -0.052847 | 0.06865 | 0.094744 | -0.16415 | -0.006484 | 0.27286 | 0.35758 | 0.28083 | 0.28732 | 0.21461 | 0.20077 | 59.1574 | -61.7548 | 59.3547 | 59.2515 | 0.094062 | -61.6333 | -61.6072 | 121.2964 | 121.2382 | 121.2243 | 46.5579 | -121.03 | 59.2687 | 59.3902 | 59.4163 | 59.4181 | -61.8661
2657.7812 | 120.7672 | -18.6768 | 102.5757 | 1.4211e-13 | -0.06563 | -0.011353 | 0.062374 | -0.012196 | 0.050258 | 0.0021363 | 0.045221 | 0.022669 | 0.01002 | 0.041927 | -0.0029762 | -54.262 | -10.7034 | -54.4121 | 66.5761 | 66.6878 | 66.4859 | -54.5248 | 0.033099 | 0.091933 | -0.074666 | -0.04369 | 0.073228 | 0.094744 | -0.16873 | -35.848 | -35.9996 | -35.5852 | -35.7354 | 0.11267 | -35.8879 | -36.0898 | 18.508 | -102.6194 | 18.7099 | 18.6021 | 0.094062 | -102.5025 | -102.4809 | 85.2529 | 85.3646 | 85.1627 | 7.9734 | -157.1005 | 18.6331 | 18.75 | 18.7715 | 18.7687 | -102.7444
2659.5469 | 121.5363 | -58.905 | 62.1735 | 1.4211e-13 | -0.065843 | -0.011353 | 0.062801 | -0.012196 | 0.050258 | -0.013124 | 0.045221 | 0.022456 | 0.010234 | 0.042141 | -0.0029762 | -47.6233 | -9.1924 | -47.4714 | 73.7825 | 73.4417 | 73.8392 | -47.9907 | 0.042256 | 0.091933 | -0.065509 | -0.039111 | 0.06865 | 0.099323 | -0.16415 | 10.9144 | 11.609 | 11.2817 | 11.4336 | 0.51922 | 11.2683 | 11.6657 | 58.7409 | -62.2126 | 58.9473 | 58.8395 | 0.09864 | -62.1048 | -62.0741 | 132.6875 | 132.3468 | 132.7442 | 49.7126 | -110.1641 | 58.8659 | 58.9737 | 59.0044 | 58.997 | -62.3376
2661.3125 | 121.5042 | -57.7286 | 63.414 | 1.4211e-13 | -0.066057 | -0.011566 | 0.062588 | -0.011769 | 0.050471 | -0.013124 | 0.045434 | 0.022456 | 0.01002 | 0.041927 | -0.0029762 | -57.1006 | -12.4661 | -57.1637 | 63.9344 | 63.8672 | 63.8715 | -57.4736 | 0.051413 | 0.082776 | -0.074666 | -0.039111 | 0.06865 | 0.094744 | -0.15957 | 0.25496 | 0.52037 | 0.62797 | 0.56491 | 0.30995 | 0.4532 | 0.45753 | 57.569 | -63.4531 | 57.78 | 57.6539 | 0.084904 | -63.3454 | -63.3193 | 121.663 | 121.5958 | 121.6001 | 45.2624 | -120.8876 | 57.6895 | 57.7972 | 57.8233 | 57.8114 | -63.5736
2663.0781 | 121.5775 | -57.1289 | 64.0594 | 1.4211e-13 | -0.066057 | -0.011566 | 0.062374 | -0.01241 | 0.050471 | -0.013124 | 0.045434 | 0.022242 | 0.0098064 | 0.041713 | -0.0027626 | -56.9816 | -12.4799 | -57.0813 | 64.0168 | 63.9908 | 63.9677 | -57.3591 | 0.037677 | 0.091933 | -0.079245 | -0.04369 | 0.06865 | 0.099323 | -0.16415 | -0.23023 | -0.042664 | 0.14734 | 0.047651 | 0.27788 | -0.068619 | -0.091763 | 56.9648 | -64.1031 | 57.1666 | 57.0497 | 0.084904 | -63.9908 | -63.9601 | 121.1457 | 121.1197 | 121.0966 | 44.649 | -121.4186 | 57.0852 | 57.1976 | 57.2282 | 57.2208 | -64.2236
2664.7812 | 121.7194 | -43.4601 | 73.5443 | 1.4211e-13 | -0.066271 | -0.011353 | 0.062374 | -0.012196 | 0.050471 | -0.0054937 | 0.045221 | 0.022669 | 0.010234 | 0.041927 | -0.0029762 | -51.9545 | -10.5843 | -52.068 | 69.1446 | 69.0963 | 69.0545 | -52.2536 | 0.046835 | 0.087354 | -0.074666 | -0.04369 | 0.064071 | 0.099323 | -0.15499 | -8.7936 | -4.3997 | -8.4944 | -8.608 | 0.1856 | -4.448 | -4.4898 | 43.3051 | -73.588 | 43.5069 | 43.3854 | 0.080325 | -73.4802 | -73.445 | 112.6047 | 112.5564 | 112.5146 | 32.8758 | -125.798 | 43.4164 | 43.5242 | 43.5594 | 43.5474 | -73.6993
2666.5312 | 121.637 | -59.6741 | 61.5555 | 1.4211e-13 | -0.066271 | -0.011566 | 0.062374 | -0.01241 | 0.050899 | -0.013124 | 0.045648 | 0.022456 | 0.010661 | 0.042141 | -0.002549 | -57.8286 | -13.1117 | -57.9237 | 63.2522 | 63.1941 | 63.1847 | -58.1925 | 0.037677 | 0.087354 | -0.070087 | -0.04369 | 0.064071 | 0.099323 | -0.15499 | 1.4816 | 1.6967 | 1.8455 | 1.7504 | 0.26885 | 1.6386 | 1.6293 | 59.5191 | -61.5992 | 59.7117 | 59.604 | 0.084904 | -61.4914 | -61.4562 | 122.9263 | 122.8682 | 122.8588 | 46.5624 | -119.748 | 59.6304 | 59.7381 | 59.7734 | 59.7614 | -61.7105
2668.2188 | 121.6324 | -58.5022 | 62.796 | 1.4211e-13 | -0.066271 | -0.011353 | 0.062801 | -0.011982 | 0.050258 | -0.020755 | 0.045434 | 0.022669 | 0.01002 | 0.042354 | -0.0027626 | -57.6637 | -13.0842 | -57.7268 | 63.4353 | 63.3727 | 63.3725 | -58.0322 | 0.037677 | 0.091933 | -0.074666 | -0.04369 | 0.06865 | 0.099323 | -0.16415 | 0.46996 | 0.63931 | 0.83845 | 0.7754 | 0.30545 | 0.57665 | 0.57645 | 58.338 | -62.8397 | 58.5399 | 58.4275 | 0.089483 | -62.7274 | -62.6967 | 121.9375 | 121.8749 | 121.8747 | 45.418 | -120.8283 | 58.4585 | 58.5708 | 58.6015 | 58.5941 | -62.9602
2669.9844 | 121.7422 | -53.1189 | 67.1265 | 1.4211e-13 | -0.065843 | -0.011353 | 0.062374 | -0.011982 | 0.050258 | -0.013124 | 0.045221 | 0.022456 | 0.01002 | 0.042141 | -0.0029762 | -53.4562 | -11.5733 | -53.4507 | 67.7665 | 67.6357 | 67.7267 | -53.8151 | 0.042256 | 0.091933 | -0.074666 | -0.04369 | 0.059493 | 0.094744 | -0.16415 | -0.69616 | 0.64002 | -0.33731 | -0.33178 | 0.36437 | 0.50919 | 0.60025 | 52.9547 | -67.1702 | 53.1612 | 53.0442 | 0.089483 | -67.067 | -67.0317 | 120.8854 | 120.7545 | 120.8456 | 41.5456 | -120.9415 | 53.0752 | 53.1784 | 53.2136 | 53.2108 | -67.2906
2671.75 | 121.3989 | -13.9801 | 107.5058 | 1.4211e-13 | -0.065843 | -0.011139 | 0.063015 | -0.011982 | 0.04983 | -0.0054937 | 0.045007 | 0.022883 | 0.010447 | 0.042354 | -0.002549 | -17.8501 | 3.4674 | -18.0926 | 103.2994 | 103.3101 | 103.014 | -17.9483 | 0.042256 | 0.082776 | -0.074666 | -0.048268 | 0.06865 | 0.099323 | -0.15957 | -3.9682 | -4.2064 | -3.87 | -4.1125 | -0.14428 | -4.1957 | -4.4918 | 13.8205 | -107.5541 | 14.0224 | 13.9054 | 0.084904 | -107.4371 | -107.4065 | 117.2795 | 117.2902 | 116.9941 | 17.4475 | -125.4541 | 13.9318 | 14.0488 | 14.0794 | 14.0629 | -107.6654
2673.5 | 121.7468 | -57.724 | 63.5605 | 1.4211e-13 | -0.066271 | -0.011353 | 0.062588 | -0.012196 | 0.050258 | -0.0054937 | 0.045221 | 0.022456 | 0.010234 | 0.041927 | -0.0027626 | -56.2948 | -13.3498 | -56.3213 | 64.8958 | 64.7692 | 64.8651 | -56.7135 | 0.046835 | 0.091933 | -0.070087 | -0.04369 | 0.064071 | 0.099323 | -0.15499 | 1.0105 | 1.3353 | 1.4292 | 1.4027 | 0.39225 | 1.2088 | 1.3046 | 57.569 | -63.6042 | 57.7708 | 57.6539 | 0.084904 | -63.4964 | -63.4612 | 122.6198 | 122.4932 | 122.5891 | 44.3742 | -120.274 | 57.6803 | 57.7881 | 57.8233 | 57.8159 | -63.7155
2675.2812 | 121.6599 | -57.4356 | 63.9084 | 1.4211e-13 | -0.066271 | -0.011139 | 0.062588 | -0.011982 | 0.050258 | -0.020755 | 0.045221 | 0.022669 | 0.01002 | 0.042141 | -0.002549 | -57.0914 | -13.4643 | -57.1911 | 63.9435 | 63.9542 | 63.9311 | -57.524 | 0.042256 | 0.082776 | -0.070087 | -0.048268 | 0.06865 | 0.1039 | -0.16415 | -0.088373 | 0.035144 | 0.34416 | 0.24448 | 0.33285 | 0.045812 | 0.02267 | 57.2715 | -63.9567 | 57.4779 | 57.3655 | 0.094062 | -63.8397 | -63.8045 | 121.3791 | 121.3898 | 121.3667 | 43.9713 | -121.4324 | 57.3873 | 57.5043 | 57.5395 | 57.5184 | -64.0725
2677.0469 | 121.6919 | -55.188 | 66.1697 | 1.4211e-13 | -0.066271 | -0.011566 | 0.062588 | -0.01241 | 0.050258 | -0.0054937 | 0.045007 | 0.022883 | 0.01002 | 0.042141 | -0.0027626 | -54.9671 | -12.6767 | -55.076 | 66.0908 | 66.1063 | 66.0784 | -55.3124 | 0.033099 | 0.087354 | -0.070087 | -0.039111 | 0.06865 | 0.1039 | -0.15957 | -0.12437 | -0.078945 | 0.22091 | 0.11202 | 0.23639 | -0.063446 | -0.091318 | 55.0284 | -66.2089 | 55.2211 | 55.1179 | 0.089483 | -66.1011 | -66.0658 | 121.2788 | 121.2943 | 121.2664 | 42.5112 | -121.4821 | 55.1489 | 55.2566 | 55.2919 | 55.2753 | -66.3293
2678.7344 | 121.6827 | -53.2791 | 68.161 | 1.4211e-13 | -0.066057 | -0.011566 | 0.062588 | -0.011982 | 0.050471 | -0.0054937 | 0.045221 | 0.022669 | 0.0098064 | 0.041927 | -0.0029762 | -53.0899 | -12.0586 | -53.1851 | 68.0091 | 67.9287 | 67.9785 | -53.4625 | 0.051413 | 0.087354 | -0.06093 | -0.04369 | 0.064071 | 0.099323 | -0.15957 | -0.18336 | -0.15187 | 0.18918 | 0.093976 | 0.27734 | -0.23231 | -0.18247 | 53.1195 | -68.2047 | 53.3305 | 53.2182 | 0.09864 | -68.0969 | -68.0617 | 121.2883 | 121.2078 | 121.2577 | 41.2205 | -121.6235 | 53.2354 | 53.3432 | 53.3784 | 53.3665 | -68.3206
2680.4844 | 121.6507 | -52.4094 | 69.0537 | 1.4211e-13 | -0.066484 | -0.011139 | 0.062588 | -0.012196 | 0.050258 | -0.0054937 | 0.045221 | 0.022669 | 0.010447 | 0.042354 | -0.0029762 | -52.6367 | -11.9808 | -52.7319 | 68.4853 | 68.4186 | 68.3906 | -53.0229 | 0.042256 | 0.091933 | -0.070087 | -0.052847 | 0.064071 | 0.1039 | -0.15499 | -0.61354 | -0.56836 | -0.22732 | -0.32252 | 0.29101 | -0.635 | -0.66304 | 52.2544 | -69.1065 | 52.4516 | 52.3393 | 0.084904 | -68.9896 | -68.9497 | 120.8947 | 120.828 | 120.8 | 40.4286 | -122.0765 | 52.3565 | 52.4734 | 52.5133 | 52.5013 | -69.2086
2682.1875 | 121.7285 | -51.059 | 70.3537 | 1.4211e-13 | -0.066057 | -0.011353 | 0.062801 | -0.01241 | 0.050471 | -0.0054937 | 0.045434 | 0.022883 | 0.010234 | 0.042354 | -0.0029762 | -50.4024 | -11.0559 | -50.4931 | 70.7287 | 70.6394 | 70.6387 | -50.7884 | 0.046835 | 0.087354 | -0.070087 | -0.048268 | 0.073228 | 0.099323 | -0.15499 | 0.27058 | 0.375 | 0.65654 | 0.56585 | 0.29527 | 0.28573 | 0.28501 | 50.904 | -70.402 | 51.1058 | 50.9889 | 0.084904 | -70.2805 | -70.2544 | 121.7877 | 121.6984 | 121.6977 | 40.003 | -121.1421 | 51.0107 | 51.1322 | 51.1583 | 51.1463 | -70.5087
2683.9531 | 121.6324 | -47.5845 | 73.9471 | 1.4211e-13 | -0.066484 | -0.011566 | 0.063015 | -0.011982 | 0.050471 | -0.013124 | 0.045648 | 0.022456 | 0.01002 | 0.042141 | -0.0027626 | -47.6142 | -9.9571 | -47.7095 | 73.5444 | 73.4875 | 73.4545 | -47.9174 | 0.051413 | 0.10109 | -0.074666 | -0.04369 | 0.064071 | 0.094744 | -0.16415 | -0.33286 | -0.40273 | -0.029652 | -0.12498 | 0.20788 | -0.45962 | -0.49259 | 47.4204 | -73.9908 | 47.6359 | 47.5099 | 0.089483 | -73.8831 | -73.8524 | 121.1289 | 121.0721 | 121.0391 | 37.6275 | -121.8645 | 47.5408 | 47.6486 | 47.6793 | 47.6856 | -74.1113
2685.7188 | 121.756 | -44.2566 | 77.2202 | 1.4211e-13 | -0.066271 | -0.011566 | 0.062801 | -0.011982 | 0.050471 | -0.0054937 | 0.045221 | 0.022242 | 0.01002 | 0.042354 | -0.0029762 | -44.1529 | -8.5011 | -44.2392 | 77.0515 | 76.9904 | 76.9434 | -44.4328 | 0.042256 | 0.091933 | -0.079245 | -0.04369 | 0.073228 | 0.099323 | -0.16415 | -0.17624 | -0.1687 | 0.10367 | 0.017414 | 0.19366 | -0.22976 | -0.27671 | 44.0924 | -77.2638 | 44.2988 | 44.1773 | 0.084904 | -77.1469 | -77.1208 | 121.308 | 121.247 | 121.2 | 35.7555 | -121.653 | 44.2129 | 44.3298 | 44.3559 | 44.3485 | -77.3843
2687.4062 | 121.6415 | -41.4871 | 80.04 | 1.4211e-13 | -0.066271 | -0.011139 | 0.062801 | -0.012196 | 0.050471 | -0.013124 | 0.045007 | 0.022456 | 0.01002 | 0.042568 | -0.0031898 | -41.0167 | -7.1366 | -41.1122 | 80.2517 | 80.1544 | 80.1118 | -41.3421 | 0.037677 | 0.091933 | -0.074666 | -0.048268 | 0.06865 | 0.090166 | -0.16415 | 0.14506 | 0.21177 | 0.47039 | 0.37491 | 0.22985 | 0.11445 | 0.07186 | 41.323 | -80.0882 | 41.5248 | 41.4125 | 0.089483 | -79.9713 | -79.9498 | 121.7389 | 121.6416 | 121.599 | 34.3505 | -121.382 | 41.4389 | 41.5558 | 41.5773 | 41.5791 | -80.2041
2689.1562 | 121.669 | -38.6215 | 82.901 | 1.4211e-13 | -0.066271 | -0.010925 | 0.063015 | -0.01241 | 0.050044 | -0.013124 | 0.045221 | 0.022456 | 0.010234 | 0.042568 | -0.0031898 | -38.9336 | -6.3445 | -39.0199 | 82.3853 | 82.3706 | 82.3141 | -39.1991 | 0.037677 | 0.087354 | -0.074666 | -0.048268 | 0.073228 | 0.1039 | -0.15957 | -0.5776 | -0.51572 | -0.31204 | -0.39842 | 0.17919 | -0.53037 | -0.58686 | 38.462 | -82.9493 | 38.6592 | 38.5469 | 0.084904 | -82.8278 | -82.7971 | 121.0068 | 120.9922 | 120.9357 | 32.277 | -122.1001 | 38.5733 | 38.6947 | 38.7254 | 38.7089 | -83.0606
2690.9219 | 121.7514 | -45.5246 | 75.9796 | 1.4211e-13 | -0.066484 | -0.011139 | 0.062801 | -0.012196 | 0.050258 | -0.0054937 | 0.044794 | 0.022669 | 0.01002 | 0.042568 | -0.0031898 | -45.5539 | -9.49 | -45.6401 | 75.7008 | 75.6946 | 75.6569 | -45.8248 | 0.051413 | 0.082776 | -0.070087 | -0.04369 | 0.06865 | 0.099323 | -0.16415 | -0.30023 | -0.27878 | -0.029315 | -0.11554 | 0.1847 | -0.28505 | -0.32276 | 45.3604 | -76.0233 | 45.576 | 45.4545 | 0.094062 | -75.911 | -75.8803 | 121.2254 | 121.2192 | 121.1815 | 36.0346 | -121.8044 | 45.4809 | 45.5932 | 45.6239 | 45.6074 | -76.1438
2692.625 | 120.9274 | -41.9952 | 79.6143 | 1.4211e-13 | -0.066271 | -0.011353 | 0.062801 | -0.011769 | 0.050685 | -0.0054937 | 0.045221 | 0.022669 | 0.010234 | 0.042568 | -0.0029762 | -42.4864 | -8.1622 | -42.591 | 78.7867 | 78.7212 | 78.6787 | -42.7615 | 0.042256 | 0.087354 | -0.070087 | -0.04369 | 0.073228 | 0.1039 | -0.15499 | -0.76629 | -0.82759 | -0.49115 | -0.59576 | 0.17053 | -0.89303 | -0.93552 | 41.8402 | -79.6579 | 42.0375 | 41.9252 | 0.084904 | -79.541 | -79.5104 | 120.7819 | 120.7165 | 120.674 | 33.833 | -122.3758 | 41.9515 | 42.0685 | 42.0991 | 42.0826 | -79.7692
2694.3594 | 121.4767 | -40.48 | 81.0745 | 1.4211e-13 | -0.066271 | -0.01178 | 0.062801 | -0.012196 | 0.050685 | -0.020755 | 0.044794 | 0.022883 | 0.010234 | 0.042354 | -0.0027626 | -40.4078 | -7.2603 | -40.4896 | 80.9202 | 80.8184 | 80.794 | -40.701 | 0.051413 | 0.091933 | -0.065509 | -0.04369 | 0.077807 | 0.094744 | -0.15957 | -0.22097 | -0.15433 | 0.072238 | -0.009524 | 0.21145 | -0.25615 | -0.28047 | 40.3205 | -81.1182 | 40.5315 | 40.4145 | 0.094061 | -80.9967 | -80.9798 | 121.4002 | 121.2984 | 121.2741 | 33.2198 | -121.7755 | 40.4364 | 40.5578 | 40.5748 | 40.572 | -81.2341
2696.0781 | 121.756 | -43.2587 | 78.2867 | 1.4211e-13 | -0.066271 | -0.011139 | 0.062801 | -0.011769 | 0.050685 | -0.013124 | 0.045007 | 0.022883 | 0.01002 | 0.042568 | -0.0031898 | -44.4459 | -9.3389 | -44.5368 | 76.8637 | 76.8164 | 76.774 | -44.7854 | 0.046835 | 0.096512 | -0.065509 | -0.04369 | 0.06865 | 0.090166 | -0.16415 | -1.5267 | -1.423 | -1.1873 | -1.2781 | 0.24865 | -1.4703 | -1.5127 | 43.0945 | -78.3304 | 43.3055 | 43.1932 | 0.09864 | -78.2181 | -78.1966 | 120.1224 | 120.0751 | 120.0327 | 33.9197 | -123.0722 | 43.215 | 43.3273 | 43.3488 | 43.3552 | -78.4509
2697.8281 | 121.7926 | -40.8188 | 80.69 | 1.4211e-13 | -0.066484 | -0.011353 | 0.062801 | -0.012196 | 0.050471 | -0.013124 | 0.044794 | 0.022669 | 0.01002 | 0.042568 | -0.0029762 | -39.9591 | -7.2648 | -40.0455 | 81.3506 | 81.2763 | 81.2244 | -40.2202 | 0.046835 | 0.091933 | -0.065509 | -0.052847 | 0.073228 | 0.099323 | -0.15957 | 0.59856 | 0.66056 | 0.85966 | 0.77331 | 0.17475 | 0.58627 | 0.53444 | 40.6592 | -80.7428 | 40.8656 | 40.7533 | 0.094061 | -80.6168 | -80.5907 | 122.1693 | 122.0951 | 122.0432 | 33.554 | -120.9102 | 40.7659 | 40.892 | 40.9181 | 40.9107 | -80.8496
2699.5938 | 121.8018 | -39.949 | 81.4819 | 1.4211e-13 | -0.066698 | -0.011353 | 0.062801 | -0.012196 | 0.050685 | -0.0054937 | 0.045007 | 0.022456 | 0.01002 | 0.042568 | -0.0029762 | -39.721 | -7.2465 | -39.7982 | 81.5886 | 81.4869 | 81.4579 | -40.0096 | 0.051413 | 0.091933 | -0.065509 | -0.048268 | 0.077807 | 0.099323 | -0.16415 | -0.060559 | 0.1067 | 0.22799 | 0.15079 | 0.21135 | 0.004966 | -0.023987 | 39.7849 | -81.5302 | 40.0004 | 39.8835 | 0.09864 | -81.4041 | -81.3826 | 121.5377 | 121.4359 | 121.407 | 32.7025 | -121.4915 | 39.9008 | 40.0268 | 40.0484 | 40.041 | -81.6461
2701.2969 | 121.8201 | -44.1971 | 77.2888 | 1.4211e-13 | -0.066698 | -0.011353 | 0.063015 | -0.012196 | 0.050258 | -0.0054937 | 0.044794 | 0.022669 | 0.01002 | 0.042568 | -0.0031898 | -43.9835 | -9.403 | -44.0606 | 77.3033 | 77.2193 | 77.1907 | -44.3413 | 0.042256 | 0.091933 | -0.065509 | -0.039111 | 0.073228 | 0.1039 | -0.16415 | -0.14418 | 0.014448 | 0.21356 | 0.13646 | 0.28063 | -0.069476 | -0.098129 | 44.0329 | -77.3279 | 44.2393 | 44.1316 | 0.09864 | -77.2156 | -77.1849 | 121.5003 | 121.4164 | 121.3878 | 34.794 | -121.6301 | 44.158 | 44.2703 | 44.301 | 44.289 | -77.453
2703.0469 | 121.6873 | -42.7277 | 79.0787 | 1.4211e-13 | -0.066912 | -0.011353 | 0.062801 | -0.012196 | 0.050258 | -0.0054937 | 0.045007 | 0.022242 | 0.0098064 | 0.042568 | -0.0031898 | -41.1816 | -8.1668 | -41.2587 | 80.1236 | 80.0354 | 80.0111 | -41.5298 | 0.042256 | 0.082776 | -0.070087 | -0.048268 | 0.077807 | 0.094744 | -0.15499 | 1.1979 | 1.0449 | 1.5461 | 1.4689 | 0.27108 | 0.95671 | 0.93243 | 42.5727 | -79.1269 | 42.7699 | 42.6576 | 0.084904 | -79.0009 | -78.9839 | 122.8512 | 122.763 | 122.7388 | 34.5608 | -120.6085 | 42.6794 | 42.8055 | 42.8224 | 42.8104 | -79.2337
2704.8438 | 121.8567 | -38.4659 | 82.8415 | 1.4211e-13 | -0.066271 | -0.011566 | 0.063015 | -0.01241 | 0.050471 | -0.020755 | 0.045434 | 0.022669 | 0.01002 | 0.042782 | -0.0034036 | -37.9172 | -6.6421 | -38.0036 | 83.4429 | 83.3368 | 83.3214 | -38.1918 | 0.046835 | 0.091933 | -0.065509 | -0.048268 | 0.06865 | 0.1039 | -0.16415 | 0.27412 | 0.60139 | 0.54872 | 0.46232 | 0.1882 | 0.49529 | 0.47995 | 38.3017 | -82.8898 | 38.5127 | 38.4004 | 0.09864 | -82.7728 | -82.7376 | 121.9088 | 121.8027 | 121.7873 | 31.8237 | -121.0333 | 38.4176 | 38.5345 | 38.5698 | 38.5578 | -83.0056
2706.5312 | 121.7926 | -37.294 | 84.4116 | 1.4211e-13 | -0.066698 | -0.011353 | 0.062801 | -0.011982 | 0.050471 | -0.0054937 | 0.045007 | 0.022456 | 0.010234 | 0.042782 | -0.002549 | -37.9263 | -6.6925 | -38.0173 | 83.4108 | 83.323 | 83.2894 | -38.2467 | 0.051413 | 0.091933 | -0.065509 | -0.048268 | 0.06865 | 0.099323 | -0.15957 | -0.9527 | -1.0008 | -0.63231 | -0.72329 | 0.22942 | -1.0886 | -1.1222 | 37.1344 | -84.4599 | 37.3454 | 37.2285 | 0.094061 | -84.343 | -84.3123 | 120.7048 | 120.6171 | 120.5834 | 30.6015 | -122.6583 | 37.2457 | 37.3627 | 37.3933 | 37.3859 | -84.5712
2708.2969 | 120.9412 | -31.7368 | 89.9139 | 1.4211e-13 | -0.066484 | -0.011139 | 0.063015 | -0.012196 | 0.050044 | -0.020755 | 0.045007 | 0.022669 | 0.010234 | 0.042995 | -0.0027626 | -31.8966 | -3.7851 | -31.9694 | 89.5047 | 89.413 | 89.3698 | -32.1522 | 0.051413 | 0.091933 | -0.070087 | -0.052847 | 0.06865 | 0.094744 | -0.16415 | -0.41541 | -0.40927 | -0.15983 | -0.23263 | 0.18277 | -0.50092 | -0.54417 | 31.5726 | -89.9668 | 31.7882 | 31.6667 | 0.094062 | -89.8453 | -89.8192 | 121.2414 | 121.1498 | 121.1065 | 27.9517 | -122.0661 | 31.6839 | 31.8054 | 31.8315 | 31.8287 | -90.0781
2710.0625 | 121.4996 | -30.5649 | 91.0721 | 1.4211e-13 | -0.066484 | -0.011353 | 0.062801 | -0.012196 | 0.050685 | -0.0054937 | 0.044794 | 0.022669 | 0.010234 | 0.042568 | -0.0031898 | -29.5891 | -2.7229 | -29.6894 | 91.8396 | 91.7483 | 91.6865 | -29.8215 | 0.046835 | 0.091933 | -0.070087 | -0.048268 | 0.073228 | 0.1039 | -0.15499 | 0.74339 | 0.76756 | 0.97581 | 0.87548 | 0.13209 | 0.67619 | 0.61446 | 30.4099 | -91.1204 | 30.6117 | 30.4948 | 0.084904 | -90.9989 | -90.9682 | 122.4045 | 122.3132 | 122.2514 | 27.842 | -120.8936 | 30.5166 | 30.6381 | 30.6688 | 30.6568 | -91.2271
2711.7656 | 120.9595 | -29.0543 | 92.6834 | 1.4211e-13 | -0.066698 | -0.011353 | 0.063015 | -0.012196 | 0.050258 | -0.013124 | 0.045007 | 0.022456 | 0.0098064 | 0.042354 | -0.0027626 | -29.0442 | -2.5077 | -29.1034 | 92.4028 | 92.3069 | 92.2497 | -29.2766 | 0.042256 | 0.087354 | -0.06093 | -0.048268 | 0.059493 | 0.099323 | -0.15499 | -0.22234 | -0.28062 | 0.010015 | -0.049122 | 0.17321 | -0.37651 | -0.4337 | 28.8993 | -92.7317 | 29.0965 | 28.9933 | 0.094061 | -92.6239 | -92.5841 | 121.457 | 121.3612 | 121.304 | 26.5466 | -121.96 | 29.006 | 29.1138 | 29.1536 | 29.1416 | -92.8384
2713.4688 | 121.756 | -41.1942 | 80.4474 | 1.4211e-13 | -0.066484 | -0.011353 | 0.062801 | -0.011982 | 0.050044 | -0.013124 | 0.045221 | 0.022456 | 0.010234 | 0.042568 | -0.0029762 | -34.4101 | -5.3327 | -34.5012 | 87.0369 | 86.9129 | 86.9111 | -34.7209 | 0.042256 | 0.096512 | -0.070087 | -0.048268 | 0.073228 | 0.099323 | -0.15957 | 6.4732 | 6.5895 | 6.784 | 6.693 | 0.21976 | 6.4655 | 6.4637 | 41.0346 | -80.4957 | 41.2364 | 41.1241 | 0.089483 | -80.3742 | -80.3481 | 128.2311 | 128.1071 | 128.1052 | 35.8615 | -115.1683 | 41.1459 | 41.2674 | 41.2935 | 41.2907 | -80.607
2715.25 | 121.9116 | -120.0027 | 1.6067 | 1.4211e-13 | -0.067553 | -0.012207 | 0.061947 | -0.012196 | 0.05154 | -0.013124 | 0.045007 | 0.022456 | 0.01002 | 0.042568 | -0.0031898 | -118.95 | -48.9164 | -119.268 | 1.7553 | 1.7587 | 1.8727 | -120.0446 | 0.037677 | 0.087354 | -0.070087 | -0.039111 | 0.073228 | 0.099323 | -0.15957 | -0.04187 | 0.14854 | 1.0527 | 0.73471 | 0.77658 | 0.15192 | 0.26593 | 119.8432 | -1.6459 | 120.0404 | 119.9327 | 0.089483 | -1.5335 | -1.5074 | 121.758 | 121.7614 | 121.8754 | 71.0864 | -121.6514 | 119.9636 | 120.076 | 120.1021 | 120.0901 | -1.7663
2717.0156 | 121.9757 | -121.1655 | 0.46692 | 1.4211e-13 | -0.067553 | -0.011994 | 0.062374 | -0.011769 | 0.05154 | -0.013124 | 0.045221 | 0.022883 | 0.0098064 | 0.042568 | -0.0034036 | -120.2091 | -49.5345 | -120.5591 | 0.47334 | 0.4903 | 0.59983 | -121.3313 | 0.051413 | 0.091933 | -0.06093 | -0.04369 | 0.059493 | 0.10848 | -0.15957 | -0.16583 | 0.00642 | 0.95636 | 0.60635 | 0.77218 | 0.023385 | 0.13291 | 121.0059 | -0.51061 | 121.2169 | 121.1045 | 0.09864 | -0.40743 | -0.35844 | 121.6388 | 121.6558 | 121.7653 | 71.631 | -121.7982 | 121.1218 | 121.225 | 121.2739 | 121.2574 | -0.62649
2718.7031 | 121.843 | -121.2891 | 0.45319 | 1.4211e-13 | -0.067766 | -0.012207 | 0.062374 | -0.011769 | 0.05154 | -0.020755 | 0.044794 | 0.022669 | 0.010447 | 0.042568 | -0.0029762 | -120.2457 | -49.9054 | -120.5912 | 0.40466 | 0.46741 | 0.55862 | -121.3679 | 0.046835 | 0.091933 | -0.06093 | -0.048268 | 0.073228 | 0.1039 | -0.15957 | -0.078864 | -0.048522 | 1.0433 | 0.6979 | 0.77676 | 0.014223 | 0.10543 | 121.1295 | -0.50145 | 121.3359 | 121.2281 | 0.09864 | -0.37996 | -0.34928 | 121.6937 | 121.7565 | 121.8477 | 71.3837 | -121.8211 | 121.2408 | 121.3623 | 121.393 | 121.381 | -0.61276
2720.4062 | 121.9803 | -121.2112 | 0.48065 | 1.4211e-13 | -0.067553 | -0.012207 | 0.061733 | -0.011982 | 0.051326 | -0.020755 | 0.045007 | 0.022669 | 0.01002 | 0.042782 | -0.0029762 | -120.2274 | -50.1984 | -120.5728 | 0.41382 | 0.47657 | 0.58151 | -121.3588 | 0.055992 | 0.096512 | -0.070087 | -0.034533 | 0.064071 | 0.099323 | -0.15499 | -0.14753 | -0.066832 | 0.98382 | 0.63839 | 0.78592 | -0.004085 | 0.10086 | 121.0563 | -0.51519 | 121.2672 | 121.1412 | 0.084904 | -0.41658 | -0.38133 | 121.6251 | 121.6878 | 121.7928 | 71.0129 | -121.8394 | 121.1767 | 121.2753 | 121.3106 | 121.3078 | -0.63564
2722.1562 | 122.0306 | -120.9366 | 0.68665 | 1.4211e-13 | -0.067125 | -0.01178 | 0.062374 | -0.011982 | 0.05154 | -0.020755 | 0.044794 | 0.022456 | 0.010234 | 0.042782 | -0.0029762 | -120.0122 | -50.3129 | -120.3622 | 0.67479 | 0.68262 | 0.79671 | -121.1665 | 0.055992 | 0.091933 | -0.070087 | -0.048268 | 0.06865 | 0.1039 | -0.15957 | -0.22987 | -0.011858 | 0.92435 | 0.57434 | 0.80421 | -0.004027 | 0.11006 | 120.777 | -0.73491 | 120.9926 | 120.8665 | 0.089483 | -0.618 | -0.58274 | 121.6114 | 121.6192 | 121.7333 | 70.6237 | -121.8531 | 120.8883 | 121.0052 | 121.0405 | 121.0285 | -0.84622
2723.8438 | 102.681 | -61.9354 | 59.7519 | 1.4211e-13 | -0.067125 | -0.01178 | 0.063015 | -0.011982 | 0.050685 | -0.013124 | 0.045221 | 0.022669 | 0.01002 | 0.042995 | -0.0031898 | -61.6241 | -19.6637 | -61.774 | 59.4842 | 59.444 | 59.4257 | -62.1395 | 0.055992 | 0.091933 | -0.070087 | -0.04369 | 0.077807 | 0.099323 | -0.15499 | -0.20411 | -0.26771 | 0.31137 | 0.16143 | 0.36554 | -0.30794 | -0.32618 | 61.7804 | -59.7956 | 61.9914 | 61.8653 | 0.084904 | -59.6741 | -59.6526 | 121.4196 | 121.3794 | 121.3611 | 42.2717 | -121.8914 | 61.8917 | 62.0132 | 62.0347 | 62.0274 | -59.9069
2725.6094 | 121.4172 | -61.5005 | 60.1913 | 1.4211e-13 | -0.067125 | -0.011566 | 0.062588 | -0.012196 | 0.051112 | -0.013124 | 0.045007 | 0.022456 | 0.0098064 | 0.042995 | -0.0036172 | -61.0472 | -19.7965 | -61.1788 | 60.0839 | 60.0346 | 60.0255 | -61.5718 | 0.046835 | 0.091933 | -0.065509 | -0.04369 | 0.06865 | 0.094744 | -0.15499 | -0.071202 | -0.1074 | 0.45337 | 0.32173 | 0.39294 | -0.15671 | -0.16584 | 61.3456 | -60.235 | 61.5474 | 61.435 | 0.089482 | -60.1227 | -60.0966 | 121.5845 | 121.5352 | 121.5261 | 41.7041 | -121.7631 | 61.4569 | 61.5692 | 61.5953 | 61.5925 | -60.3463
2727.2969 | 121.6324 | -61.3815 | 60.3149 | 1.4211e-13 | -0.067125 | -0.011566 | 0.063015 | -0.011769 | 0.050258 | -0.013124 | 0.045221 | 0.022456 | 0.0095928 | 0.042782 | -0.0031898 | -60.8732 | -19.9338 | -60.9682 | 60.2579 | 60.2086 | 60.2041 | -61.4069 | 0.042256 | 0.096512 | -0.065509 | -0.04369 | 0.06865 | 0.099323 | -0.15499 | -0.025378 | -0.057013 | 0.50833 | 0.41332 | 0.43869 | -0.1063 | -0.11087 | 61.2265 | -60.3586 | 61.4238 | 61.316 | 0.089482 | -60.2463 | -60.2156 | 121.6395 | 121.5902 | 121.5856 | 41.4477 | -121.7218 | 61.3378 | 61.4502 | 61.4809 | 61.478 | -60.4699
2729.0469 | 121.907 | -61.8988 | 59.7382 | 1.4211e-13 | -0.067339 | -0.01178 | 0.063015 | -0.011982 | 0.050685 | -0.0054937 | 0.045221 | 0.022242 | 0.010234 | 0.043209 | -0.0031898 | -61.3402 | -20.3734 | -61.4215 | 59.7909 | 59.7279 | 59.7371 | -61.8785 | 0.042256 | 0.091933 | -0.074666 | -0.04369 | 0.073228 | 0.10848 | -0.16415 | 0.020265 | 0.052773 | 0.55861 | 0.47734 | 0.45707 | -0.010308 | -0.001103 | 61.7347 | -59.7818 | 61.9411 | 61.8241 | 0.089483 | -59.6649 | -59.6297 | 121.6897 | 121.6267 | 121.6359 | 41.5254 | -121.6167 | 61.8551 | 61.972 | 62.0073 | 61.9907 | -59.9023
2730.75 | 121.669 | -61.8393 | 59.8572 | 1.4211e-13 | -0.067125 | -0.01178 | 0.062801 | -0.01241 | 0.050685 | -0.020755 | 0.04458 | 0.022456 | 0.01002 | 0.043209 | -0.0036172 | -61.2853 | -20.5245 | -61.426 | 59.7909 | 59.737 | 59.7325 | -61.8877 | 0.051413 | 0.091933 | -0.056351 | -0.052847 | 0.06865 | 0.1039 | -0.15499 | -0.048402 | -0.066246 | 0.55404 | 0.41325 | 0.46165 | -0.12017 | -0.1247 | 61.6843 | -59.91 | 61.8907 | 61.7829 | 0.09864 | -59.7885 | -59.7533 | 121.6302 | 121.5763 | 121.5718 | 41.3148 | -121.7449 | 61.7864 | 61.9079 | 61.9432 | 61.9312 | -60.0122
2732.4375 | 121.875 | -62.1048 | 59.6237 | 1.4211e-13 | -0.066912 | -0.011566 | 0.062801 | -0.011982 | 0.050685 | -0.013124 | 0.045007 | 0.022669 | 0.01002 | 0.042995 | -0.0034036 | -61.473 | -20.79 | -61.6138 | 59.5986 | 59.5493 | 59.5448 | -62.08 | 0.051413 | 0.091933 | -0.074666 | -0.04369 | 0.073228 | 0.1039 | -0.15957 | 0.024786 | -0.025078 | 0.63183 | 0.49104 | 0.46626 | -0.074445 | -0.078963 | 61.9452 | -59.6674 | 62.1562 | 62.0301 | 0.084904 | -59.5505 | -59.5198 | 121.7034 | 121.6541 | 121.6496 | 41.3148 | -121.7037 | 62.0611 | 62.178 | 62.2087 | 62.1967 | -59.7833
2734.1875 | 121.9162 | -62.059 | 59.6191 | 1.4211e-13 | -0.066912 | -0.01178 | 0.063015 | -0.011982 | 0.050685 | 0.0097668 | 0.045007 | 0.022456 | 0.0098064 | 0.042568 | -0.0031898 | -61.5187 | -20.9823 | -61.6504 | 59.5574 | 59.5035 | 59.5081 | -62.135 | 0.042256 | 0.091933 | -0.06093 | -0.04369 | 0.073228 | 0.1039 | -0.15499 | -0.075937 | -0.061706 | 0.54027 | 0.40864 | 0.48458 | -0.11566 | -0.11102 | 61.904 | -59.6628 | 62.1013 | 61.9981 | 0.094061 | -59.5459 | -59.5152 | 121.6165 | 121.5625 | 121.5671 | 41.0767 | -121.7541 | 62.0153 | 62.1322 | 62.1629 | 62.151 | -59.7741
2735.875 | 121.8613 | -62.2559 | 59.5047 | 1.4211e-13 | -0.067125 | -0.011353 | 0.062801 | -0.012196 | 0.050685 | -0.0054937 | 0.045007 | 0.022456 | 0.01002 | 0.042782 | -0.0031898 | -61.6286 | -21.2342 | -61.7648 | 59.4384 | 59.3936 | 59.3937 | -62.254 | 0.046835 | 0.091933 | -0.065509 | -0.04369 | 0.06865 | 0.1039 | -0.15499 | 0.001849 | -0.066303 | 0.62723 | 0.49102 | 0.48917 | -0.11111 | -0.11104 | 62.1009 | -59.5484 | 62.3027 | 62.1904 | 0.089482 | -59.4361 | -59.4008 | 121.6943 | 121.6494 | 121.6495 | 41.0217 | -121.7587 | 62.2122 | 62.3245 | 62.3598 | 62.3478 | -59.6597
2737.6406 | 121.9391 | -62.7457 | 58.9417 | 1.4211e-13 | -0.066912 | -0.011566 | 0.063015 | -0.011982 | 0.050685 | -0.013124 | 0.045007 | 0.022669 | 0.0098064 | 0.042782 | -0.0031898 | -62.1414 | -21.692 | -62.2868 | 58.9256 | 58.8716 | 58.8717 | -62.7806 | 0.046835 | 0.087354 | -0.065509 | -0.048268 | 0.06865 | 0.1039 | -0.15041 | -0.03492 | -0.016033 | 0.60426 | 0.45891 | 0.49383 | -0.070058 | -0.06995 | 62.5953 | -58.9899 | 62.7925 | 62.6802 | 0.084903 | -58.873 | -58.8377 | 121.6713 | 121.6173 | 121.6174 | 41.0537 | -121.7222 | 62.6974 | 62.8143 | 62.8496 | 62.833 | -59.0921
2739.3281 | 121.8796 | -63.1851 | 58.6075 | 1.4211e-13 | -0.067125 | -0.011566 | 0.063229 | -0.012196 | 0.050471 | 0.0021363 | 0.044794 | 0.022883 | 0.0095928 | 0.043209 | -0.0034036 | -62.5764 | -22.0079 | -62.7263 | 58.4678 | 58.4183 | 58.423 | -63.2293 | 0.051413 | 0.091933 | -0.065509 | -0.039111 | 0.073228 | 0.10848 | -0.16415 | -0.044201 | -0.1397 | 0.60876 | 0.45885 | 0.50305 | -0.18921 | -0.18449 | 63.021 | -58.6466 | 63.2365 | 63.1196 | 0.09864 | -58.5343 | -58.499 | 121.6529 | 121.6034 | 121.6081 | 41.1772 | -121.8368 | 63.146 | 63.2583 | 63.2936 | 63.2771 | -58.7716
2741.0781 | 121.9025 | -63.9267 | 57.8293 | 1.4211e-13 | -0.067553 | -0.011353 | 0.062801 | -0.012196 | 0.050685 | -0.013124 | 0.045007 | 0.022242 | 0.0098064 | 0.043423 | -0.0034036 | -63.3684 | -22.5986 | -63.5229 | 57.6757 | 57.6215 | 57.6263 | -64.0398 | 0.051413 | 0.096512 | -0.070087 | -0.039111 | 0.06865 | 0.1039 | -0.15957 | -0.11309 | -0.15357 | 0.55828 | 0.4038 | 0.5169 | -0.20774 | -0.20296 | 63.7671 | -57.8684 | 63.9781 | 63.8566 | 0.089483 | -57.7606 | -57.7254 | 121.6024 | 121.5482 | 121.553 | 41.3281 | -121.8691 | 63.8876 | 63.9953 | 64.0306 | 64.0232 | -57.9889
2742.7656 | 121.8933 | -2.4399 | 119.014 | 1.4211e-13 | -0.066698 | -0.011353 | 0.063015 | -0.011982 | 0.050258 | -0.013124 | 0.044794 | 0.022669 | 0.01002 | 0.042782 | -0.0036172 | -1.2351 | 12.6567 | -1.3727 | 120.1844 | 120.0414 | 119.9594 | -1.8122 | 0.055992 | 0.091933 | -0.065509 | -0.04369 | 0.059493 | 0.099323 | -0.15957 | 0.62767 | 1.1705 | 1.2048 | 1.0671 | 0.43947 | 1.0275 | 0.94544 | 2.2803 | -119.0577 | 2.4959 | 2.3744 | 0.094061 | -118.9545 | -118.9147 | 122.6243 | 122.4813 | 122.3993 | 15.0965 | -120.8262 | 2.3962 | 2.4994 | 2.5392 | 2.5318 | -119.1735
2744.5156 | 121.9666 | -4.0054 | 117.453 | 1.4211e-13 | -0.067339 | -0.010925 | 0.063015 | -0.01241 | 0.050258 | -0.0054937 | 0.044794 | 0.022669 | 0.0095928 | 0.042995 | -0.0031898 | -3.0802 | 11.5074 | -3.2178 | 118.3256 | 118.219 | 118.1646 | -3.6804 | 0.055992 | 0.091933 | -0.065509 | -0.039111 | 0.06865 | 0.094744 | -0.16415 | 0.32502 | 0.87262 | 0.92522 | 0.78765 | 0.46262 | 0.76603 | 0.7116 | 3.8413 | -117.4921 | 4.0614 | 3.9399 | 0.09864 | -117.3844 | -117.3583 | 122.3311 | 122.2245 | 122.17 | 15.5129 | -121.1334 | 3.9663 | 4.0741 | 4.1002 | 4.0974 | -117.6172
2746.2812 | 121.788 | -116.5512 | 4.8019 | 1.4211e-13 | -0.067766 | -0.012207 | 0.062374 | -0.011982 | 0.051326 | -0.020755 | 0.044794 | 0.022456 | 0.01002 | 0.042995 | -0.0034036 | -114.097 | -52.7578 | -114.2686 | 6.5672 | 6.4566 | 6.7214 | -115.2276 | 0.042256 | 0.087354 | -0.070087 | -0.039111 | 0.073228 | 0.10848 | -0.15041 | 1.3236 | 1.7652 | 2.4543 | 2.2827 | 0.95903 | 1.6547 | 1.9195 | 116.4008 | -4.8411 | 116.5935 | 116.4811 | 0.080325 | -4.7287 | -4.6935 | 123.1184 | 123.0079 | 123.2726 | 63.7934 | -120.0295 | 116.5121 | 116.6244 | 116.6597 | 116.6386 | -4.9524
2748.0469 | 121.756 | -117.2745 | 4.1199 | 1.4211e-13 | -0.067766 | -0.012635 | 0.062374 | -0.011982 | 0.051326 | -0.013124 | 0.044794 | 0.022456 | 0.0095928 | 0.043209 | -0.0034036 | -116.1893 | -53.6049 | -116.5302 | 4.1544 | 4.1626 | 4.2581 | -117.4529 | 0.051413 | 0.091933 | -0.056351 | -0.04369 | 0.06865 | 0.099323 | -0.15957 | -0.17847 | 0.03449 | 1.0852 | 0.74425 | 0.92272 | 0.042728 | 0.13826 | 117.1149 | -4.1636 | 117.3259 | 117.2181 | 0.10322 | -4.0512 | -4.0206 | 121.4288 | 121.4371 | 121.5326 | 63.6696 | -121.5728 | 117.2308 | 117.3431 | 117.3738 | 117.3664 | -4.2794
2749.75 | 121.7377 | -117.5583 | 3.8452 | 1.4211e-13 | -0.06798 | -0.012207 | 0.062374 | -0.011982 | 0.051326 | -0.0054937 | 0.045007 | 0.022456 | 0.0095928 | 0.042782 | -0.0036172 | -116.4365 | -53.9254 | -116.7866 | 3.843 | 3.8558 | 3.9422 | -117.6269 | 0.051413 | 0.096512 | -0.051772 | -0.034533 | 0.06865 | 0.094744 | -0.15957 | -0.068656 | -0.002182 | 1.1218 | 0.77168 | 0.84033 | 0.010598 | 0.096991 | 117.3987 | -3.8797 | 117.6097 | 117.5065 | 0.1078 | -3.7766 | -3.7505 | 121.4013 | 121.4141 | 121.5005 | 63.6329 | -121.4722 | 117.5238 | 117.6269 | 117.653 | 117.6548 | -4.0048
2751.5312 | 121.6599 | -117.7139 | 3.6484 | 1.4211e-13 | -0.067766 | -0.012207 | 0.06216 | -0.011769 | 0.051326 | -0.013124 | 0.045007 | 0.022669 | 0.01002 | 0.042995 | -0.0034036 | -116.5647 | -54.1818 | -116.9194 | 3.6507 | 3.6681 | 3.7636 | -117.7826 | 0.051413 | 0.087354 | -0.06093 | -0.039111 | 0.073228 | 0.10848 | -0.15041 | -0.0687 | 0.002365 | 1.1492 | 0.79455 | 0.86325 | 0.019702 | 0.11526 | 117.5635 | -3.6875 | 117.7653 | 117.653 | 0.089482 | -3.5751 | -3.5399 | 121.3647 | 121.382 | 121.4776 | 63.5322 | -121.431 | 117.6748 | 117.7872 | 117.8224 | 117.8013 | -3.7988
2753.2188 | 121.5912 | -117.7826 | 3.6026 | 1.4211e-13 | -0.06798 | -0.012207 | 0.061733 | -0.011769 | 0.051326 | -0.020755 | 0.044794 | 0.022456 | 0.0095928 | 0.042995 | -0.0036172 | -116.6013 | -54.4611 | -116.956 | 3.5363 | 3.5994 | 3.695 | -117.8238 | 0.046835 | 0.096512 | -0.051772 | -0.052847 | 0.077807 | 0.1039 | -0.15957 | -0.041246 | -0.066319 | 1.1813 | 0.82659 | 0.86783 | -0.003206 | 0.092362 | 117.623 | -3.6554 | 117.8294 | 117.7308 | 0.1078 | -3.5248 | -3.4987 | 121.3189 | 121.382 | 121.4776 | 63.3215 | -121.4264 | 117.7297 | 117.8604 | 117.8865 | 117.8791 | -3.7622
2754.9844 | 121.582 | -117.7277 | 3.5751 | 1.4211e-13 | -0.06798 | -0.012635 | 0.062374 | -0.011982 | 0.051112 | -0.0054937 | 0.044794 | 0.022242 | 0.01002 | 0.042782 | -0.0036172 | -116.5647 | -54.6213 | -116.9194 | 3.5409 | 3.5994 | 3.6995 | -117.7872 | 0.051413 | 0.091933 | -0.06093 | -0.04369 | 0.06865 | 0.1039 | -0.15499 | -0.059546 | -0.034275 | 1.163 | 0.80828 | 0.86783 | 0.02426 | 0.12441 | 117.5727 | -3.6188 | 117.7791 | 117.6667 | 0.094061 | -3.5065 | -3.4712 | 121.2685 | 121.3271 | 121.4272 | 63.1063 | -121.3623 | 117.684 | 117.7963 | 117.8316 | 117.8196 | -3.7301
2756.75 | 121.5729 | -117.897 | 3.4287 | 1.4211e-13 | -0.067766 | -0.012421 | 0.061947 | -0.011555 | 0.050899 | -0.0054937 | 0.045007 | 0.022456 | 0.0098064 | 0.043209 | -0.0036172 | -116.7021 | -54.9876 | -117.0613 | 3.3486 | 3.4162 | 3.5118 | -117.9566 | 0.046835 | 0.091933 | -0.070087 | -0.04369 | 0.073228 | 0.1039 | -0.15957 | -0.059593 | -0.080083 | 1.195 | 0.83573 | 0.89532 | -0.012413 | 0.083167 | 117.7375 | -3.4723 | 117.9439 | 117.8269 | 0.089483 | -3.3554 | -3.3247 | 121.2456 | 121.3133 | 121.4089 | 62.9094 | -121.3853 | 117.8533 | 117.9703 | 118.0009 | 117.989 | -3.5882
2758.5156 | 121.5225 | -117.9749 | 3.2318 | 1.4211e-13 | -0.06798 | -0.012207 | 0.061947 | -0.011769 | 0.051753 | -0.0054937 | 0.045007 | 0.022669 | 0.01002 | 0.043423 | -0.0034036 | -116.8486 | -55.3631 | -117.217 | 3.2341 | 3.2468 | 3.347 | -118.1902 | 0.051413 | 0.087354 | -0.065509 | -0.029954 | 0.073228 | 0.10848 | -0.15041 | -0.2153 | 0.002295 | 1.1263 | 0.75788 | 0.97318 | 0.015004 | 0.11518 | 117.8244 | -3.2618 | 118.0263 | 117.9093 | 0.084903 | -3.1586 | -3.1233 | 121.209 | 121.2217 | 121.3218 | 62.6118 | -121.422 | 117.9449 | 118.0481 | 118.0833 | 118.0622 | -3.3822
2760.2031 | 121.5683 | -118.0481 | 3.154 | 1.4211e-13 | -0.06798 | -0.012207 | 0.06216 | -0.011769 | 0.051326 | 0.0021363 | 0.045007 | 0.022456 | 0.0098064 | 0.043423 | -0.0036172 | -116.8898 | -55.679 | -117.2536 | 3.1151 | 3.1781 | 3.2737 | -118.2405 | 0.042256 | 0.091933 | -0.065509 | -0.039111 | 0.077807 | 0.1039 | -0.15499 | -0.19243 | -0.038923 | 1.1583 | 0.7945 | 0.98692 | 0.024141 | 0.11974 | 117.8931 | -3.1931 | 118.0904 | 117.9826 | 0.089482 | -3.0762 | -3.0501 | 121.1632 | 121.2262 | 121.3218 | 62.3691 | -121.3945 | 118.009 | 118.1259 | 118.152 | 118.14 | -3.309
2761.9531 | 121.5729 | -118.1305 | 3.1128 | 1.4211e-13 | -0.06798 | -0.012207 | 0.06216 | -0.011982 | 0.05154 | -0.020755 | 0.044366 | 0.022669 | 0.0098064 | 0.043209 | -0.0031898 | -116.9035 | -55.9537 | -117.2628 | 3.0601 | 3.1323 | 3.2371 | -118.1947 | 0.042256 | 0.091933 | -0.06093 | -0.04369 | 0.06865 | 0.099323 | -0.15957 | -0.064239 | -0.052664 | 1.227 | 0.86774 | 0.93198 | 0.01955 | 0.12431 | 117.9709 | -3.1565 | 118.1727 | 118.0696 | 0.09864 | -3.0441 | -3.0135 | 121.1906 | 121.2628 | 121.3676 | 62.1768 | -121.3075 | 118.0868 | 118.1991 | 118.2298 | 118.2224 | -3.2724
2763.7031 | 121.4539 | -118.1946 | 3.1219 | 1.4211e-13 | -0.06798 | -0.012207 | 0.061733 | -0.012196 | 0.051326 | -0.020755 | 0.04458 | 0.022028 | 0.0098064 | 0.043209 | -0.0034036 | -116.9081 | -56.2467 | -117.2811 | 3.0235 | 3.0911 | 3.1867 | -118.213 | 0.051413 | 0.091933 | -0.065509 | -0.04369 | 0.06865 | 0.099323 | -0.15041 | -0.018467 | -0.098447 | 1.2865 | 0.91352 | 0.93198 | -0.030815 | 0.064789 | 118.0442 | -3.1656 | 118.246 | 118.1291 | 0.084903 | -3.0533 | -3.0226 | 121.2181 | 121.2857 | 121.3813 | 61.9479 | -121.335 | 118.1509 | 118.2632 | 118.2939 | 118.2865 | -3.2724
2765.4531 | 121.3989 | -118.2312 | 3.067 | 1.4211e-13 | -0.06798 | -0.012207 | 0.06216 | -0.011769 | 0.051326 | -0.020755 | 0.04458 | 0.022242 | 0.0098064 | 0.043423 | -0.0036172 | -116.9172 | -56.494 | -117.2994 | 2.9823 | 3.0499 | 3.1547 | -118.2405 | 0.051413 | 0.091933 | -0.070087 | -0.039111 | 0.073228 | 0.1039 | -0.15957 | -0.00932 | -0.084721 | 1.314 | 0.93182 | 0.94114 | -0.017094 | 0.087669 | 118.0716 | -3.1061 | 118.2826 | 118.1611 | 0.089483 | -2.9938 | -2.9631 | 121.2135 | 121.2811 | 121.3859 | 61.7372 | -121.3075 | 118.1921 | 118.3044 | 118.3351 | 118.3231 | -3.2266
2767.2188 | 121.4905 | -118.2312 | 2.9984 | 1.4211e-13 | -0.06798 | -0.011994 | 0.061947 | -0.011341 | 0.051326 | -0.0054937 | 0.045007 | 0.022242 | 0.0095928 | 0.043423 | -0.0038308 | -116.9447 | -56.7733 | -117.3223 | 2.9411 | 3.0041 | 3.1089 | -118.2726 | 0.051413 | 0.082776 | -0.065509 | -0.039111 | 0.082386 | 0.094744 | -0.15499 | -0.041372 | -0.057262 | 1.2865 | 0.90893 | 0.9503 | 0.005781 | 0.11055 | 118.0762 | -3.0375 | 118.2826 | 118.1657 | 0.089482 | -2.916 | -2.9036 | 121.1723 | 121.2353 | 121.3401 | 61.4579 | -121.2709 | 118.1921 | 118.3136 | 118.3259 | 118.314 | -3.1533
2768.9062 | 121.4401 | -118.2541 | 2.9526 | 1.4211e-13 | -0.068194 | -0.012207 | 0.061947 | -0.011982 | 0.05154 | -0.013124 | 0.045007 | 0.022242 | 0.0098064 | 0.043423 | -0.0038308 | -116.9539 | -56.9793 | -117.336 | 2.8999 | 2.9675 | 3.0631 | -118.3046 | 0.046835 | 0.091933 | -0.065509 | -0.039111 | 0.082386 | 0.1039 | -0.14583 | -0.050537 | -0.052691 | 1.3002 | 0.91808 | 0.96862 | 0.014926 | 0.11054 | 118.1083 | -2.9917 | 118.3009 | 118.1886 | 0.080324 | -2.8702 | -2.8487 | 121.154 | 121.2216 | 121.3172 | 61.2748 | -121.2572 | 118.215 | 118.3365 | 118.358 | 118.346 | -3.0984
2770.6719 | 121.4539 | -118.2587 | 2.916 | 1.4211e-13 | -0.068407 | -0.012421 | 0.061733 | -0.011769 | 0.05154 | -0.020755 | 0.04458 | 0.022242 | 0.0098064 | 0.043209 | -0.0038308 | -116.9676 | -57.309 | -117.3497 | 2.8724 | 2.9263 | 3.0311 | -118.3321 | 0.051413 | 0.091933 | -0.065509 | -0.039111 | 0.073228 | 0.10848 | -0.15499 | -0.073432 | -0.04354 | 1.2911 | 0.90893 | 0.98236 | 0.010337 | 0.11511 | 118.1037 | -2.9551 | 118.3101 | 118.1932 | 0.089482 | -2.8427 | -2.8075 | 121.1311 | 121.185 | 121.2897 | 60.9497 | -121.2481 | 118.2196 | 118.3319 | 118.3671 | 118.3506 | -3.0709
2772.3906 | 121.3943 | -118.309 | 2.8931 | 1.4211e-13 | -0.06798 | -0.012207 | 0.061733 | -0.011982 | 0.051326 | -0.013124 | 0.044794 | 0.022242 | 0.0095928 | 0.043209 | -0.0036172 | -116.9859 | -57.4143 | -117.3681 | 2.8312 | 2.8897 | 2.9807 | -118.3596 | 0.046835 | 0.091933 | -0.070087 | -0.034533 | 0.06865 | 0.099323 | -0.15041 | -0.050552 | -0.061857 | 1.3231 | 0.94097 | 0.99152 | -0.003406 | 0.087634 | 118.1586 | -2.9276 | 118.3559 | 118.2389 | 0.080325 | -2.8244 | -2.7937 | 121.1402 | 121.1987 | 121.2897 | 60.8948 | -121.2526 | 118.2745 | 118.3777 | 118.4083 | 118.401 | -3.0435
2774.1562 | 121.376 | -118.3456 | 2.8427 | 1.4211e-13 | -0.068194 | -0.012207 | 0.061733 | -0.011982 | 0.051112 | -0.020755 | 0.044794 | 0.022456 | 0.0095928 | 0.043423 | -0.0036172 | -116.9859 | -57.7348 | -117.3772 | 2.79 | 2.8485 | 2.9578 | -118.3779 | 0.042256 | 0.091933 | -0.070087 | -0.04369 | 0.077807 | 0.099323 | -0.15957 | -0.032247 | -0.052708 | 1.3597 | 0.96843 | 1.0007 | 0.005738 | 0.11509 | 118.1861 | -2.8864 | 118.3879 | 118.2756 | 0.089483 | -2.7649 | -2.7434 | 121.1356 | 121.1941 | 121.3034 | 60.6109 | -121.2206 | 118.302 | 118.4234 | 118.445 | 118.4376 | -3.0023
2775.9219 | 121.0693 | -118.396 | 2.861 | 1.4211e-13 | -0.067766 | -0.012421 | 0.06216 | -0.012196 | 0.051326 | -0.013124 | 0.04458 | 0.022456 | 0.0098064 | 0.043423 | -0.0036172 | -116.9859 | -57.8538 | -117.3818 | 2.7625 | 2.8301 | 2.9212 | -118.3962 | 0.051413 | 0.087354 | -0.065509 | -0.039111 | 0.077807 | 0.1039 | -0.15499 | -0.000208 | -0.09849 | 1.4101 | 1.0142 | 1.0144 | -0.030889 | 0.060155 | 118.241 | -2.9001 | 118.4474 | 118.3305 | 0.089482 | -2.7832 | -2.7571 | 121.1585 | 121.2261 | 121.3172 | 60.5422 | -121.2572 | 118.3569 | 118.4738 | 118.4999 | 118.4834 | -3.016
2777.6875 | 121.4035 | -118.3411 | 2.7878 | 1.4211e-13 | -0.068407 | -0.012207 | 0.061947 | -0.011982 | 0.051326 | -0.013124 | 0.045007 | 0.022242 | 0.0098064 | 0.043423 | -0.0038308 | -116.9905 | -58.0873 | -117.3864 | 2.7396 | 2.7981 | 2.8937 | -118.4099 | 0.055992 | 0.087354 | -0.065509 | -0.04369 | 0.082386 | 0.099323 | -0.15499 | -0.068877 | -0.04814 | 1.3506 | 0.9547 | 1.0236 | 0.010301 | 0.10593 | 118.1861 | -2.8315 | 118.3971 | 118.2756 | 0.089482 | -2.7054 | -2.6885 | 121.0807 | 121.1391 | 121.2348 | 60.2537 | -121.1977 | 118.2974 | 118.4235 | 118.4404 | 118.4284 | -2.9428
2779.3906 | 121.344 | -118.3731 | 2.7969 | 1.4211e-13 | -0.068194 | -0.012207 | 0.061733 | -0.011769 | 0.050899 | -0.013124 | 0.045007 | 0.022456 | 0.0098064 | 0.043636 | -0.0036172 | -116.9813 | -58.275 | -117.3864 | 2.7213 | 2.7798 | 2.88 | -118.4191 | 0.051413 | 0.087354 | -0.065509 | -0.04369 | 0.082386 | 0.1039 | -0.15041 | -0.045991 | -0.075608 | 1.3918 | 0.98674 | 1.0327 | -0.01717 | 0.083034 | 118.2227 | -2.8406 | 118.4245 | 118.3076 | 0.084903 | -2.7146 | -2.693 | 121.0944 | 121.1529 | 121.2531 | 60.0981 | -121.216 | 118.3294 | 118.4555 | 118.477 | 118.4605 | -2.9473
2781.1562 | 121.344 | -118.3823 | 2.7649 | 1.4211e-13 | -0.068621 | -0.012207 | 0.061947 | -0.011982 | 0.05154 | -0.0054937 | 0.045007 | 0.022456 | 0.0093792 | 0.043209 | -0.0038308 | -116.9905 | -58.4811 | -117.3909 | 2.6847 | 2.7523 | 2.8525 | -118.4328 | 0.051413 | 0.082776 | -0.06093 | -0.04369 | 0.077807 | 0.10848 | -0.15499 | -0.050573 | -0.080192 | 1.3918 | 0.99132 | 1.0419 | -0.0126 | 0.087606 | 118.2273 | -2.8086 | 118.4337 | 118.3213 | 0.094061 | -2.6871 | -2.6564 | 121.067 | 121.1346 | 121.2348 | 59.9012 | -121.1977 | 118.3386 | 118.4601 | 118.4907 | 118.465 | -2.9199
2782.8594 | 121.3303 | -118.3685 | 2.7695 | 1.4211e-13 | -0.06798 | -0.012207 | 0.06216 | -0.011982 | 0.051112 | -0.013124 | 0.045007 | 0.022242 | 0.0095928 | 0.04385 | -0.0038308 | -116.9584 | -58.6642 | -117.3772 | 2.6801 | 2.7431 | 2.8433 | -118.4328 | 0.051413 | 0.091933 | -0.06093 | -0.039111 | 0.06865 | 0.1039 | -0.15041 | -0.064306 | -0.089348 | 1.4101 | 0.99132 | 1.0556 | -0.026335 | 0.073871 | 118.2181 | -2.8086 | 118.4199 | 118.3076 | 0.089482 | -2.7008 | -2.6656 | 121.0487 | 121.1117 | 121.2119 | 59.7043 | -121.2023 | 118.3294 | 118.4372 | 118.4724 | 118.4605 | -2.9199
2784.625 | 121.3303 | -118.3731 | 2.7512 | 1.4211e-13 | -0.06798 | -0.012207 | 0.061733 | -0.011982 | 0.05154 | -0.013124 | 0.045007 | 0.022028 | 0.0095928 | 0.043423 | -0.0038308 | -116.9447 | -58.8428 | -117.3635 | 2.6847 | 2.7431 | 2.8433 | -118.4283 | 0.051413 | 0.087354 | -0.06093 | -0.04369 | 0.073228 | 0.1039 | -0.15957 | -0.055149 | -0.066459 | 1.4284 | 1.0096 | 1.0648 | -0.008025 | 0.092181 | 118.2135 | -2.7948 | 118.4245 | 118.3122 | 0.09864 | -2.6779 | -2.6473 | 121.0578 | 121.1162 | 121.2164 | 59.5303 | -121.1794 | 118.3294 | 118.4463 | 118.477 | 118.4605 | -2.9107
2786.3906 | 121.0922 | -118.3273 | 2.8152 | 1.4211e-13 | -0.068407 | -0.012421 | 0.062374 | -0.011982 | 0.051326 | -0.013124 | 0.04458 | 0.022028 | 0.0095928 | 0.043636 | -0.0034036 | -116.8852 | -58.9847 | -117.3131 | 2.703 | 2.7706 | 2.8662 | -118.387 | 0.046835 | 0.091933 | -0.065509 | -0.039111 | 0.073228 | 0.1039 | -0.15499 | -0.059714 | -0.11223 | 1.4421 | 1.0142 | 1.0739 | -0.044639 | 0.050987 | 118.1723 | -2.8544 | 118.3742 | 118.2618 | 0.089482 | -2.742 | -2.7113 | 121.0303 | 121.0979 | 121.1936 | 59.3426 | -121.2023 | 118.2882 | 118.4006 | 118.4312 | 118.4193 | -2.9702
2788.1562 | 121.4493 | -118.3548 | 2.623 | 1.4211e-13 | -0.068194 | -0.012207 | 0.06216 | -0.011769 | 0.05154 | -0.0054937 | 0.044794 | 0.021815 | 0.0098064 | 0.04385 | -0.0038308 | -116.9356 | -59.2778 | -117.3681 | 2.6893 | 2.6973 | 2.793 | -118.5473 | 0.051413 | 0.091933 | -0.065509 | -0.034533 | 0.073228 | 0.1039 | -0.15499 | -0.19251 | 0.066293 | 1.4192 | 0.98674 | 1.1793 | 0.07436 | 0.16999 | 118.1998 | -2.6575 | 118.4062 | 118.2893 | 0.089482 | -2.5498 | -2.5191 | 121.0441 | 121.0521 | 121.1478 | 59.077 | -121.1703 | 118.3203 | 118.428 | 118.4587 | 118.4467 | -2.778
2789.8594 | 121.2891 | -118.4738 | 2.6321 | 1.4211e-13 | -0.068621 | -0.012207 | 0.06216 | -0.011769 | 0.051112 | -0.0054937 | 0.04458 | 0.022456 | 0.0095928 | 0.04385 | -0.0034036 | -117.0042 | -59.4426 | -117.4321 | 2.5428 | 2.6012 | 2.706 | -118.5427 | 0.051413 | 0.087354 | -0.065509 | -0.04369 | 0.077807 | 0.1039 | -0.15957 | -0.068914 | -0.08937 | 1.4696 | 1.0417 | 1.1106 | -0.030953 | 0.073842 | 118.3142 | -2.6758 | 118.5252 | 118.4083 | 0.094061 | -2.5543 | -2.5282 | 121.0166 | 121.075 | 121.1798 | 59.0312 | -121.1749 | 118.4301 | 118.5516 | 118.5777 | 118.5612 | -2.7917
2791.625 | 121.376 | -118.4692 | 2.5543 | 1.4211e-13 | -0.068407 | -0.012207 | 0.061733 | -0.011769 | 0.05154 | -0.013124 | 0.044794 | 0.022242 | 0.0098064 | 0.043423 | -0.0040444 | -117.0042 | -59.6898 | -117.4413 | 2.5153 | 2.5783 | 2.6785 | -118.5519 | 0.051413 | 0.087354 | -0.065509 | -0.04369 | 0.077807 | 0.094744 | -0.15041 | -0.08265 | -0.039021 | 1.465 | 1.0279 | 1.1106 | 0.023973 | 0.12419 | 118.3188 | -2.598 | 118.5207 | 118.4037 | 0.084903 | -2.4765 | -2.4596 | 120.9845 | 121.0475 | 121.1478 | 58.7794 | -121.1062 | 118.4255 | 118.547 | 118.564 | 118.5566 | -2.7047
2793.3125 | 121.3623 | -118.5013 | 2.5452 | 1.4211e-13 | -0.068621 | -0.011994 | 0.061947 | -0.011555 | 0.051326 | -0.013124 | 0.04458 | 0.022456 | 0.0095928 | 0.04385 | -0.0038308 | -116.9859 | -59.818 | -117.4321 | 2.497 | 2.5691 | 2.6694 | -118.561 | 0.055992 | 0.091933 | -0.065509 | -0.04369 | 0.073228 | 0.10848 | -0.16415 | -0.059763 | -0.048179 | 1.5154 | 1.0691 | 1.1289 | 0.02397 | 0.12419 | 118.3371 | -2.5889 | 118.5573 | 118.4358 | 0.09864 | -2.4719 | -2.4367 | 120.9983 | 121.0704 | 121.1706 | 58.6832 | -121.1062 | 118.4576 | 118.5745 | 118.6098 | 118.5932 | -2.7093
2795.0781 | 121.3028 | -118.5379 | 2.5543 | 1.4211e-13 | -0.068407 | -0.012421 | 0.061733 | -0.011982 | 0.051326 | 0.0021363 | 0.045007 | 0.022242 | 0.0091656 | 0.043423 | -0.0036172 | -116.9859 | -60.0149 | -117.423 | 2.4878 | 2.5417 | 2.651 | -118.5702 | 0.051413 | 0.091933 | -0.065509 | -0.039111 | 0.073228 | 0.1039 | -0.15957 | -0.0323 | -0.066491 | 1.552 | 1.1149 | 1.1472 | -0.012659 | 0.096719 | 118.3783 | -2.5934 | 118.5893 | 118.4724 | 0.094061 | -2.4811 | -2.4504 | 121.0257 | 121.0796 | 121.1889 | 58.523 | -121.1245 | 118.4988 | 118.6111 | 118.6418 | 118.6298 | -2.7139
2796.7812 | 121.2158 | -118.5745 | 2.5635 | 1.4211e-13 | -0.068621 | -0.012207 | 0.061519 | -0.011341 | 0.051112 | -0.0054937 | 0.044794 | 0.022456 | 0.0093792 | 0.044064 | -0.0038308 | -116.9859 | -60.1614 | -117.4276 | 2.4649 | 2.5325 | 2.6327 | -118.5885 | 0.051413 | 0.087354 | -0.065509 | -0.039111 | 0.073228 | 0.1039 | -0.15499 | -0.013995 | -0.098539 | 1.5886 | 1.147 | 1.1609 | -0.030973 | 0.069249 | 118.4195 | -2.6026 | 118.6259 | 118.509 | 0.089482 | -2.4902 | -2.4596 | 121.0395 | 121.107 | 121.2073 | 58.4131 | -121.152 | 118.5354 | 118.6478 | 118.6784 | 118.6619 | -2.7185
2798.5469 | 120.6757 | -1.0025 | 119.6411 | 1.4211e-13 | -0.067766 | -0.011139 | 0.063015 | -0.012623 | 0.049189 | -0.020755 | 0.044794 | 0.022028 | 0.0098064 | 0.044277 | -0.0038308 | -0.15462 | 15.8022 | -0.37925 | 119.6762 | 119.5332 | 119.4375 | -1.075 | 0.051413 | 0.096512 | -0.065509 | -0.04369 | 0.073228 | 0.10848 | -0.15957 | -0.072498 | 0.035133 | 0.84788 | 0.62325 | 0.69575 | -0.10793 | -0.20366 | 0.84293 | -119.6848 | 1.0539 | 0.93699 | 0.094061 | -119.5679 | -119.5326 | 120.6787 | 120.5357 | 120.44 | 16.8047 | -120.7161 | 0.95881 | 1.0757 | 1.111 | 1.099 | -119.8007
2800.25 | 121.0327 | -1.0117 | 119.7418 | 1.4211e-13 | -0.067553 | -0.011139 | 0.062801 | -0.01241 | 0.049189 | -0.013124 | 0.04458 | 0.022242 | 0.0098064 | 0.043636 | -0.0036172 | -0.099677 | 15.6877 | -0.32431 | 119.9693 | 119.8308 | 119.7259 | -1.0292 | 0.046835 | 0.091933 | -0.065509 | -0.029954 | 0.06865 | 0.099323 | -0.15957 | -0.017552 | 0.22744 | 0.91198 | 0.68735 | 0.7049 | 0.088993 | -0.015914 | 0.85209 | -119.7718 | 1.0585 | 0.94615 | 0.094061 | -119.6732 | -119.6425 | 120.9809 | 120.8425 | 120.7376 | 16.6994 | -120.771 | 0.9817 | 1.0803 | 1.111 | 1.1036 | -119.9014
2802 | 121.0693 | -0.93384 | 119.9707 | 1.4211e-13 | -0.067553 | -0.010925 | 0.063015 | -0.012623 | 0.049403 | -0.0054937 | 0.04458 | 0.022456 | 0.0093792 | 0.04385 | -0.0040444 | -0.076785 | 15.7243 | -0.29226 | 120.0883 | 119.9407 | 119.8495 | -1.0109 | 0.051413 | 0.087354 | -0.065509 | -0.039111 | 0.06865 | 0.099323 | -0.15499 | -0.077057 | 0.1176 | 0.85705 | 0.64158 | 0.71863 | -0.029995 | -0.12117 | 0.77885 | -120.0098 | 0.98525 | 0.86833 | 0.089482 | -119.9021 | -119.8714 | 121.0221 | 120.8745 | 120.7834 | 16.6582 | -120.9816 | 0.89473 | 1.0025 | 1.0332 | 1.0212 | -120.1257
2803.75 | 121.051 | -0.95673 | 120.0668 | 1.4211e-13 | -0.067766 | -0.011353 | 0.063229 | -0.01241 | 0.049617 | -0.013124 | 0.045007 | 0.022242 | 0.0093792 | 0.044064 | -0.0036172 | -0.058472 | 15.7106 | -0.28311 | 120.1616 | 120.0277 | 119.9274 | -1.0017 | 0.046835 | 0.091933 | -0.06093 | -0.04369 | 0.06865 | 0.094744 | -0.15957 | -0.045011 | 0.094722 | 0.89825 | 0.67362 | 0.71863 | -0.039125 | -0.13947 | 0.79716 | -120.1105 | 1.0036 | 0.8958 | 0.09864 | -119.9982 | -119.9721 | 121.1183 | 120.9844 | 120.8841 | 16.6673 | -121.0686 | 0.91304 | 1.0254 | 1.0515 | 1.0487 | -120.2264
2805.4531 | 121.1288 | -1.1581 | 119.9432 | 1.4211e-13 | -0.067553 | -0.011353 | 0.062801 | -0.012196 | 0.049617 | -0.013124 | 0.04458 | 0.022456 | 0.0098064 | 0.04385 | -0.0038308 | -0.049315 | 15.7289 | -0.28311 | 120.1524 | 120.0827 | 119.9915 | -1.0109 | 0.051413 | 0.091933 | -0.070087 | -0.04369 | 0.073228 | 0.1039 | -0.15957 | 0.14725 | 0.20916 | 1.1088 | 0.87504 | 0.72779 | 0.13942 | 0.048228 | 0.99857 | -119.9869 | 1.2096 | 1.0881 | 0.089483 | -119.87 | -119.8393 | 121.3105 | 121.2408 | 121.1496 | 16.887 | -120.9541 | 1.1145 | 1.2314 | 1.262 | 1.2501 | -120.1028
2807.2031 | 121.1197 | -0.96588 | 120.1904 | 1.4211e-13 | -0.067766 | -0.011353 | 0.063229 | -0.012623 | 0.049617 | -0.013124 | 0.04458 | 0.022456 | 0.0095928 | 0.043636 | -0.0040444 | -0.026423 | 15.8113 | -0.25564 | 120.2165 | 120.1376 | 120.0418 | -1.0063 | 0.046835 | 0.087354 | -0.06093 | -0.039111 | 0.073228 | 0.099323 | -0.15041 | -0.040435 | 0.026065 | 0.93946 | 0.71024 | 0.75068 | -0.052828 | -0.1486 | 0.81547 | -120.2295 | 1.0127 | 0.90495 | 0.089482 | -120.1172 | -120.0911 | 121.1824 | 121.1035 | 121.0077 | 16.7772 | -121.1967 | 0.92677 | 1.0391 | 1.0652 | 1.0532 | -120.3408
2808.9062 | 121.2479 | -0.93842 | 120.2133 | 1.4211e-13 | -0.067766 | -0.010925 | 0.063015 | -0.012196 | 0.049617 | -0.020755 | 0.045007 | 0.022242 | 0.0095928 | 0.043636 | -0.0038308 | -0.017266 | 15.848 | -0.25106 | 120.2623 | 120.1147 | 120.0876 | -0.99716 | 0.042256 | 0.091933 | -0.070087 | -0.039111 | 0.073228 | 0.099323 | -0.15041 | -0.058742 | 0.048961 | 0.92115 | 0.68736 | 0.7461 | -0.09861 | -0.1257 | 0.788 | -120.2524 | 0.98067 | 0.86833 | 0.080325 | -120.1401 | -120.114 | 121.2007 | 121.0531 | 121.026 | 16.7864 | -121.2105 | 0.89931 | 1.0116 | 1.0377 | 1.0303 | -120.3637
2810.6562 | 121.2479 | -0.95673 | 120.282 | 1.4211e-13 | -0.067553 | -0.011139 | 0.063229 | -0.012196 | 0.049617 | -0.0054937 | 0.044794 | 0.022242 | 0.0095928 | 0.043636 | -0.0036172 | 0.001048 | 15.9533 | -0.23732 | 120.3081 | 120.1651 | 120.1288 | -0.99716 | 0.046835 | 0.087354 | -0.070087 | -0.039111 | 0.06865 | 0.1039 | -0.15499 | -0.040432 | 0.026081 | 0.95777 | 0.7194 | 0.75984 | -0.11691 | -0.15316 | 0.80173 | -120.3211 | 1.0036 | 0.88664 | 0.084904 | -120.2133 | -120.1781 | 121.2648 | 121.1218 | 121.0855 | 16.91 | -121.2791 | 0.91761 | 1.0254 | 1.0606 | 1.0441 | -120.437
2812.4219 | 121.3806 | -0.91095 | 120.3232 | 1.4211e-13 | -0.067553 | -0.010925 | 0.063229 | -0.012196 | 0.050044 | -0.0054937 | 0.04458 | 0.022028 | 0.0093792 | 0.04385 | -0.0040444 | 0.014783 | 16.0723 | -0.22359 | 120.3401 | 120.1971 | 120.1655 | -0.99716 | 0.051413 | 0.091933 | -0.070087 | -0.034533 | 0.073228 | 0.099323 | -0.15499 | -0.086208 | 0.016931 | 0.92573 | 0.68736 | 0.77357 | -0.12605 | -0.15773 | 0.75596 | -120.3577 | 0.96236 | 0.84086 | 0.084904 | -120.25 | -120.2239 | 121.2511 | 121.1081 | 121.0764 | 16.9833 | -121.3203 | 0.87642 | 0.98418 | 1.0103 | 1.0029 | -120.4782
2814.1875 | 121.1884 | -0.93384 | 120.369 | 1.4211e-13 | -0.067766 | -0.011139 | 0.063015 | -0.012623 | 0.04983 | -0.020755 | 0.04458 | 0.022242 | 0.0095928 | 0.04385 | -0.0038308 | 0.037675 | 16.173 | -0.20528 | 120.3722 | 120.2338 | 120.138 | -0.99716 | 0.051413 | 0.087354 | -0.065509 | -0.048268 | 0.064071 | 0.1039 | -0.15499 | -0.06332 | 0.003203 | 0.97151 | 0.72856 | 0.79188 | -0.1352 | -0.23098 | 0.77885 | -120.4172 | 0.98525 | 0.86833 | 0.089482 | -120.3049 | -120.2651 | 121.306 | 121.1676 | 121.0718 | 17.1069 | -121.3661 | 0.88557 | 0.99791 | 1.0377 | 1.0212 | -120.5239
2815.9375 | 120.5566 | -0.95673 | 120.401 | 1.4211e-13 | -0.067766 | -0.011353 | 0.063229 | -0.012196 | 0.049617 | -0.020755 | 0.04458 | 0.022242 | 0.0093792 | 0.044491 | -0.0036172 | 0.05141 | 16.2738 | -0.19612 | 120.4088 | 120.2567 | 120.1609 | -0.9239 | 0.055992 | 0.091933 | -0.065509 | -0.04369 | 0.077807 | 0.099323 | -0.15041 | 0.032831 | 0.007787 | 1.0081 | 0.76061 | 0.72778 | -0.14435 | -0.24013 | 0.80631 | -120.4447 | 1.0127 | 0.89122 | 0.084903 | -120.3232 | -120.3017 | 121.3655 | 121.2134 | 121.1176 | 17.2305 | -121.3249 | 0.91304 | 1.0345 | 1.056 | 1.0487 | -120.5514
2817.6562 | 121.3989 | -0.92926 | 120.3827 | 1.4211e-13 | -0.06798 | -0.010925 | 0.063229 | -0.01241 | 0.049617 | -0.013124 | 0.044366 | 0.022242 | 0.0095928 | 0.044064 | -0.0040444 | 0.055988 | 16.3424 | -0.18696 | 120.4317 | 120.2933 | 120.2021 | -0.93305 | 0.046835 | 0.087354 | -0.070087 | -0.039111 | 0.077807 | 0.099323 | -0.15499 | -0.003793 | 0.04899 | 0.98525 | 0.7423 | 0.74609 | -0.089404 | -0.18061 | 0.77427 | -120.4218 | 0.97609 | 0.85917 | 0.084904 | -120.3049 | -120.2834 | 121.3609 | 121.2225 | 121.1313 | 17.2717 | -121.3157 | 0.89015 | 1.0071 | 1.0286 | 1.0166 | -120.5377
2819.3594 | 121.463 | -0.90637 | 120.4422 | 1.4211e-13 | -0.067553 | -0.011139 | 0.063656 | -0.01241 | 0.04983 | -0.013124 | 0.04458 | 0.022242 | 0.0093792 | 0.044277 | -0.0036172 | 0.074302 | 16.4249 | -0.17781 | 120.4454 | 120.3024 | 120.2341 | -0.9239 | 0.046835 | 0.082776 | -0.065509 | -0.04369 | 0.064071 | 0.10848 | -0.15041 | -0.017523 | 0.003215 | 0.98067 | 0.72857 | 0.74609 | -0.13976 | -0.20807 | 0.75596 | -120.4859 | 0.95321 | 0.84086 | 0.084903 | -120.3781 | -120.3337 | 121.3518 | 121.2088 | 121.1405 | 17.3312 | -121.3661 | 0.86268 | 0.97044 | 1.0149 | 0.98915 | -120.5926
2821.1094 | 121.431 | -0.93842 | 120.4468 | 1.4211e-13 | -0.067553 | -0.011139 | 0.063443 | -0.011982 | 0.050044 | -0.013124 | 0.04458 | 0.022242 | 0.0098064 | 0.044064 | -0.0040444 | 0.088037 | 16.489 | -0.16407 | 120.482 | 120.3391 | 120.2524 | -0.9239 | 0.042256 | 0.087354 | -0.065509 | -0.034533 | 0.06865 | 0.1039 | -0.15957 | 0.014521 | 0.035265 | 1.0265 | 0.77435 | 0.75982 | -0.1077 | -0.19433 | 0.77885 | -120.4813 | 0.98067 | 0.87291 | 0.094061 | -120.3781 | -120.3429 | 121.4205 | 121.2775 | 121.1909 | 17.4274 | -121.3707 | 0.90388 | 1.0071 | 1.0423 | 1.0258 | -120.6063
2822.875 | 120.8221 | -0.97961 | 120.5292 | 1.4211e-13 | -0.06798 | -0.011139 | 0.063656 | -0.01241 | 0.050258 | -0.0054937 | 0.04458 | 0.022242 | 0.0089518 | 0.044277 | -0.0040444 | 0.097194 | 16.5759 | -0.15949 | 120.5004 | 120.3574 | 120.2753 | -0.92847 | 0.042256 | 0.082776 | -0.065509 | -0.039111 | 0.073228 | 0.099323 | -0.15041 | 0.05114 | -0.028819 | 1.0768 | 0.82012 | 0.76898 | -0.17178 | -0.25384 | 0.8292 | -120.5683 | 1.0219 | 0.9141 | 0.084903 | -120.4559 | -120.4299 | 121.48 | 121.337 | 121.255 | 17.5556 | -121.4576 | 0.9405 | 1.0528 | 1.0789 | 1.0624 | -120.6796
2824.6406 | 121.3669 | -0.9201 | 120.5063 | 1.4211e-13 | -0.06798 | -0.011566 | 0.063229 | -0.012196 | 0.050044 | -0.0054937 | 0.04458 | 0.022456 | 0.0095928 | 0.04385 | -0.0038308 | 0.11551 | 16.6767 | -0.14118 | 120.5232 | 120.3757 | 120.2982 | -0.92847 | 0.046835 | 0.087354 | -0.06093 | -0.04369 | 0.082386 | 0.1039 | -0.15041 | -0.008369 | 0.01696 | 1.0356 | 0.77892 | 0.78729 | -0.13058 | -0.20806 | 0.76969 | -120.55 | 0.96694 | 0.85917 | 0.089482 | -120.4239 | -120.4024 | 121.4434 | 121.2958 | 121.2183 | 17.5968 | -121.4348 | 0.87641 | 1.0025 | 1.024 | 1.0075 | -120.6567
2826.3438 | 121.5637 | -0.9201 | 120.4834 | 1.4211e-13 | -0.067766 | -0.011139 | 0.063229 | -0.012196 | 0.050471 | -0.013124 | 0.044153 | 0.022456 | 0.0095928 | 0.044064 | -0.0038308 | 0.13382 | 16.7225 | -0.1366 | 120.537 | 120.394 | 120.3257 | -0.91932 | 0.046835 | 0.091933 | -0.074666 | -0.039111 | 0.073228 | 0.1039 | -0.15957 | 0.000789 | 0.053585 | 1.0539 | 0.7835 | 0.78272 | -0.089376 | -0.15769 | 0.76053 | -120.5225 | 0.96694 | 0.84544 | 0.084904 | -120.4102 | -120.3795 | 121.4571 | 121.3141 | 121.2458 | 17.6426 | -121.4027 | 0.88099 | 0.99333 | 1.024 | 1.012 | -120.643
2828.1094 | 121.2799 | -0.93384 | 120.2225 | 1.4211e-13 | -0.067766 | -0.010925 | 0.063229 | -0.012196 | 0.04983 | -0.0054937 | 0.04458 | 0.022456 | 0.0095928 | 0.044277 | -0.0036172 | 0.15671 | 16.8049 | -0.11829 | 120.5645 | 120.4215 | 120.3257 | -0.91474 | 0.046835 | 0.087354 | -0.06093 | -0.04369 | 0.073228 | 0.10848 | -0.15957 | 0.019101 | 0.34198 | 1.0906 | 0.81555 | 0.79645 | 0.19902 | 0.10323 | 0.77427 | -120.2662 | 0.98067 | 0.87291 | 0.09864 | -120.1492 | -120.114 | 121.4983 | 121.3553 | 121.2595 | 17.7387 | -121.1372 | 0.89015 | 1.0071 | 1.0423 | 1.0212 | -120.382
2829.8125 | 120.6757 | -0.9613 | 119.7968 | 1.4211e-13 | -0.06798 | -0.010925 | 0.063229 | -0.01241 | 0.050258 | -0.028385 | 0.04458 | 0.021815 | 0.0093792 | 0.044277 | -0.0040444 | 0.17045 | 16.8919 | -0.10455 | 120.5736 | 120.4398 | 120.3623 | -0.91932 | 0.046835 | 0.082776 | -0.06093 | -0.04369 | 0.073228 | 0.1039 | -0.15499 | 0.041988 | 0.77686 | 1.1318 | 0.85675 | 0.81476 | 0.64306 | 0.56558 | 0.80631 | -119.8404 | 1.0081 | 0.90037 | 0.094061 | -119.7235 | -119.6929 | 121.5349 | 121.4011 | 121.3236 | 17.8532 | -120.7161 | 0.91761 | 1.0345 | 1.0652 | 1.0441 | -119.9517
2831.5781 | 121.5408 | -0.9201 | 120.5154 | 1.4211e-13 | -0.06798 | -0.011353 | 0.063229 | -0.012196 | 0.050044 | -0.013124 | 0.044366 | 0.022242 | 0.0098064 | 0.044277 | -0.0040444 | 0.1796 | 16.9834 | -0.08624 | 120.5965 | 120.449 | 120.3806 | -0.9239 | 0.046835 | 0.091933 | -0.065509 | -0.039111 | 0.06865 | 0.1039 | -0.15041 | -0.00379 | 0.08106 | 1.0997 | 0.83386 | 0.83766 | -0.066473 | -0.13479 | 0.76969 | -120.5546 | 0.96694 | 0.8546 | 0.084903 | -120.4468 | -120.4115 | 121.5166 | 121.3691 | 121.3008 | 17.9035 | -121.4393 | 0.88099 | 0.98875 | 1.024 | 1.012 | -120.6659
2833.2812 | 121.1975 | -0.94299 | 120.575 | 1.4211e-13 | -0.06798 | -0.010712 | 0.063229 | -0.012196 | 0.050258 | -0.013124 | 0.044366 | 0.021815 | 0.0095928 | 0.044064 | -0.0038308 | 0.19334 | 17.0247 | -0.081662 | 120.6148 | 120.4673 | 120.3898 | -0.91932 | 0.042256 | 0.087354 | -0.070087 | -0.04369 | 0.06865 | 0.1039 | -0.14583 | 0.023677 | 0.039864 | 1.1363 | 0.86133 | 0.83765 | -0.10767 | -0.18515 | 0.79716 | -120.6186 | 0.98525 | 0.87291 | 0.075746 | -120.5063 | -120.4711 | 121.5578 | 121.4103 | 121.3328 | 17.9676 | -121.4943 | 0.8993 | 1.0116 | 1.0469 | 1.0303 | -120.7208
2835.0469 | 120.8588 | -0.96588 | 120.5933 | 1.4211e-13 | -0.067766 | -0.011139 | 0.063656 | -0.012623 | 0.050258 | 0.0021363 | 0.044794 | 0.022028 | 0.0095928 | 0.044277 | -0.0038308 | 0.21165 | 17.0842 | -0.072505 | 120.624 | 120.4856 | 120.4127 | -0.9239 | 0.046835 | 0.091933 | -0.065509 | -0.039111 | 0.073228 | 0.10848 | -0.15499 | 0.041986 | 0.03071 | 1.1775 | 0.89338 | 0.85139 | -0.10766 | -0.18057 | 0.81089 | -120.6324 | 1.0127 | 0.90037 | 0.089482 | -120.52 | -120.4848 | 121.5899 | 121.4515 | 121.3786 | 18.0501 | -121.5172 | 0.92677 | 1.0391 | 1.0744 | 1.0578 | -120.7483
2836.8125 | 120.8176 | -0.92468 | 119.9707 | 1.4211e-13 | -0.068407 | -0.010925 | 0.063443 | -0.012196 | 0.050258 | -0.013124 | 0.04458 | 0.022028 | 0.0095928 | 0.044277 | -0.0042582 | 0.22539 | 17.2536 | -0.054192 | 120.6423 | 120.4993 | 120.4219 | -0.9239 | 0.042256 | 0.087354 | -0.06093 | -0.04369 | 0.077807 | 0.094744 | -0.15041 | 0.000788 | 0.67158 | 1.1501 | 0.87049 | 0.8697 | 0.52863 | 0.45115 | 0.77427 | -120.0144 | 0.96694 | 0.86375 | 0.089482 | -119.8929 | -119.876 | 121.567 | 121.424 | 121.3465 | 18.1783 | -120.8946 | 0.88099 | 1.0025 | 1.0194 | 1.012 | -120.1211
2838.5156 | 121.1975 | -0.95215 | 120.6253 | 1.4211e-13 | -0.06798 | -0.010925 | 0.063443 | -0.011769 | 0.050044 | -0.020755 | 0.04458 | 0.022242 | 0.0093792 | 0.044277 | -0.0042582 | 0.2437 | 17.3177 | -0.049614 | 120.6514 | 120.5177 | 120.4402 | -0.92847 | 0.046835 | 0.087354 | -0.065509 | -0.039111 | 0.077807 | 0.10848 | -0.15041 | 0.023674 | 0.026137 | 1.1959 | 0.90253 | 0.87886 | -0.10765 | -0.18514 | 0.80174 | -120.6644 | 0.99898 | 0.88664 | 0.084903 | -120.5475 | -120.5168 | 121.6036 | 121.4698 | 121.3923 | 18.2698 | -121.5538 | 0.91304 | 1.03 | 1.0606 | 1.0395 | -120.7757
2840.2188 | 120.9091 | -0.97046 | 120.6711 | 1.4211e-13 | -0.068194 | -0.011139 | 0.063229 | -0.012196 | 0.050258 | -0.0054937 | 0.044153 | 0.022242 | 0.0098064 | 0.044491 | -0.0040444 | 0.26659 | 17.423 | -0.040457 | 120.6606 | 120.5314 | 120.4493 | -0.92847 | 0.046835 | 0.087354 | -0.065509 | -0.034533 | 0.073228 | 0.094744 | -0.15499 | 0.041985 | -0.010483 | 1.2371 | 0.93 | 0.88802 | -0.13969 | -0.22176 | 0.81547 | -120.7056 | 1.0173 | 0.90495 | 0.089482 | -120.5979 | -120.5763 | 121.6311 | 121.5018 | 121.4198 | 18.3934 | -121.5996 | 0.93593 | 1.0437 | 1.0652 | 1.0578 | -120.8261
2841.9844 | 121.3165 | -0.9613 | 120.5978 | 1.4211e-13 | -0.068194 | -0.011139 | 0.063656 | -0.012623 | 0.050044 | -0.0054937 | 0.04458 | 0.022242 | 0.0098064 | 0.044491 | -0.0040444 | 0.26659 | 17.597 | -0.031301 | 120.6789 | 120.5314 | 120.4585 | -0.92847 | 0.051413 | 0.087354 | -0.070087 | -0.048268 | 0.086964 | 0.094744 | -0.15957 | 0.03283 | 0.081074 | 1.2279 | 0.93 | 0.89717 | -0.066449 | -0.13936 | 0.80173 | -120.6461 | 1.0127 | 0.89122 | 0.089483 | -120.5109 | -120.5031 | 121.6402 | 121.4927 | 121.4198 | 18.5583 | -121.5263 | 0.91304 | 1.0483 | 1.056 | 1.0487 | -120.7574
2843.7344 | 121.0236 | -0.95673 | 120.3323 | 1.4211e-13 | -0.068194 | -0.011139 | 0.063443 | -0.012196 | 0.050471 | -0.0054937 | 0.044366 | 0.022456 | 0.0095928 | 0.044064 | -0.0040444 | 0.28491 | 17.6748 | -0.022144 | 120.6881 | 120.5543 | 120.4676 | -0.92847 | 0.042256 | 0.091933 | -0.06093 | -0.04369 | 0.077807 | 0.1039 | -0.15957 | 0.028252 | 0.35573 | 1.2416 | 0.93458 | 0.90633 | 0.22195 | 0.1353 | 0.79716 | -120.376 | 0.99898 | 0.8958 | 0.09864 | -120.2545 | -120.2284 | 121.6448 | 121.511 | 121.4244 | 18.6315 | -121.2608 | 0.91304 | 1.0345 | 1.0606 | 1.0487 | -120.4919
2845.4375 | 121.2662 | -0.97961 | 120.4926 | 1.4211e-13 | -0.068407 | -0.011139 | 0.063656 | -0.012196 | 0.050258 | -0.0054937 | 0.044366 | 0.022028 | 0.0093792 | 0.044277 | -0.0042582 | 0.3078 | 17.8122 | -0.003831 | 120.7064 | 120.5589 | 120.486 | -0.92847 | 0.042256 | 0.087354 | -0.065509 | -0.04369 | 0.082386 | 0.1039 | -0.15499 | 0.05114 | 0.21383 | 1.2874 | 0.97578 | 0.92464 | 0.066309 | -0.006599 | 0.82462 | -120.5362 | 1.0219 | 0.9141 | 0.089482 | -120.4102 | -120.3887 | 121.686 | 121.5385 | 121.4656 | 18.7918 | -121.421 | 0.93592 | 1.062 | 1.0835 | 1.067 | -120.6475
2847.2031 | 121.7102 | -0.93842 | 120.6528 | 1.4211e-13 | -0.068194 | -0.011353 | 0.063443 | -0.012196 | 0.050471 | -0.0054937 | 0.044366 | 0.022242 | 0.0093792 | 0.044064 | -0.0040444 | 0.31238 | 17.9724 | 0.009904 | 120.7201 | 120.5772 | 120.4951 | -0.93305 | 0.046835 | 0.087354 | -0.065509 | -0.04369 | 0.082386 | 0.11306 | -0.15041 | 0.005363 | 0.067347 | 1.2508 | 0.94832 | 0.94296 | -0.075592 | -0.15766 | 0.788 | -120.6965 | 0.98525 | 0.87291 | 0.084903 | -120.5704 | -120.5397 | 121.6585 | 121.5156 | 121.4335 | 18.9108 | -121.5858 | 0.89473 | 1.0208 | 1.0515 | 1.0258 | -120.8032
2848.9062 | 121.019 | -0.9613 | 120.0577 | 1.4211e-13 | -0.06798 | -0.011139 | 0.063656 | -0.012196 | 0.050685 | -0.0054937 | 0.04458 | 0.021815 | 0.0093792 | 0.044491 | -0.0040444 | 0.32611 | 18.0365 | 0.014482 | 120.7201 | 120.5818 | 120.5088 | -0.92847 | 0.042256 | 0.091933 | -0.06093 | -0.034533 | 0.082386 | 0.1039 | -0.15499 | 0.03283 | 0.66244 | 1.2874 | 0.97579 | 0.94296 | 0.52408 | 0.45117 | 0.80631 | -120.0922 | 1.0036 | 0.90037 | 0.094061 | -119.9753 | -119.9538 | 121.6814 | 121.5431 | 121.4702 | 18.9978 | -120.9862 | 0.92677 | 1.0437 | 1.0652 | 1.0532 | -120.2127
2850.6562 | 121.17 | -0.98877 | 120.2225 | 1.4211e-13 | -0.067766 | -0.011139 | 0.06387 | -0.01241 | 0.050685 | -0.013124 | 0.044366 | 0.022242 | 0.0093792 | 0.044064 | -0.0042582 | 0.34901 | 18.1281 | 0.023639 | 120.7339 | 120.5818 | 120.518 | -0.92847 | 0.046835 | 0.087354 | -0.065509 | -0.039111 | 0.086964 | 0.11306 | -0.15957 | 0.060296 | 0.51138 | 1.3378 | 1.0124 | 0.95211 | 0.35928 | 0.29553 | 0.8292 | -120.2616 | 1.0356 | 0.92326 | 0.094061 | -120.1355 | -120.1094 | 121.7226 | 121.5705 | 121.5068 | 19.1169 | -121.1509 | 0.94966 | 1.0757 | 1.1018 | 1.0761 | -120.382
2852.4219 | 121.6919 | -0.93842 | 120.7031 | 1.4211e-13 | -0.068194 | -0.010925 | 0.063656 | -0.01241 | 0.050471 | -0.013124 | 0.044153 | 0.022242 | 0.0091656 | 0.044277 | -0.0040444 | 0.35816 | 18.2563 | 0.032795 | 120.743 | 120.6047 | 120.5272 | -0.93763 | 0.046835 | 0.091933 | -0.051772 | -0.048268 | 0.082386 | 0.1039 | -0.15499 | 0.000784 | 0.039885 | 1.2966 | 0.97121 | 0.97043 | -0.098473 | -0.17596 | 0.78343 | -120.7514 | 0.98525 | 0.88664 | 0.10322 | -120.6207 | -120.5992 | 121.6814 | 121.5431 | 121.4656 | 19.1947 | -121.6408 | 0.89015 | 1.0208 | 1.0423 | 1.0303 | -120.8581
2854.1875 | 121.7194 | -0.94299 | 120.7031 | 1.4211e-13 | -0.068194 | -0.010925 | 0.063656 | -0.012623 | 0.050471 | -0.013124 | 0.044366 | 0.022028 | 0.0095928 | 0.044491 | -0.0038308 | 0.37648 | 18.3845 | 0.041952 | 120.7476 | 120.6092 | 120.5409 | -0.94221 | 0.051413 | 0.087354 | -0.070087 | -0.04369 | 0.082386 | 0.099323 | -0.15499 | 0.000782 | 0.044463 | 1.3195 | 0.98494 | 0.98416 | -0.093894 | -0.16223 | 0.788 | -120.7468 | 0.99441 | 0.87291 | 0.084904 | -120.6207 | -120.6038 | 121.6906 | 121.5522 | 121.4839 | 19.3275 | -121.6453 | 0.8993 | 1.0254 | 1.0423 | 1.0303 | -120.8581
2855.875 | 121.7422 | -0.9201 | 120.5521 | 1.4211e-13 | -0.06798 | -0.011139 | 0.063656 | -0.012196 | 0.050899 | -0.0054937 | 0.044794 | 0.022242 | 0.0095928 | 0.044277 | -0.0040444 | 0.39479 | 18.5127 | 0.055687 | 120.7567 | 120.6138 | 120.5501 | -0.93763 | 0.046835 | 0.087354 | -0.070087 | -0.048268 | 0.077807 | 0.1039 | -0.15041 | -0.017527 | 0.20468 | 1.3149 | 0.97579 | 0.99332 | 0.061747 | -0.002008 | 0.76969 | -120.6003 | 0.96694 | 0.85002 | 0.080325 | -120.4743 | -120.4482 | 121.6769 | 121.5339 | 121.4702 | 19.4328 | -121.4897 | 0.87184 | 0.99791 | 1.024 | 1.0075 | -120.7025
2857.6562 | 121.7468 | -0.95673 | 120.6345 | 1.4211e-13 | -0.068194 | -0.010925 | 0.06387 | -0.011769 | 0.050685 | -0.020755 | 0.04458 | 0.022669 | 0.0093792 | 0.044491 | -0.0044718 | 0.39479 | 18.4715 | 0.069421 | 120.7751 | 120.6367 | 120.5592 | -0.94221 | 0.051413 | 0.087354 | -0.06093 | -0.039111 | 0.073228 | 0.1039 | -0.15957 | 0.014515 | 0.1406 | 1.3515 | 1.0261 | 1.0116 | 0.002245 | -0.075248 | 0.79716 | -120.6736 | 1.0081 | 0.8958 | 0.09864 | -120.5612 | -120.5306 | 121.7318 | 121.5934 | 121.5159 | 19.4282 | -121.5767 | 0.91761 | 1.03 | 1.0606 | 1.0441 | -120.794
2859.3594 | 121.3806 | -0.98877 | 120.6665 | 1.4211e-13 | -0.067766 | -0.011139 | 0.063443 | -0.012196 | 0.050685 | -0.020755 | 0.044366 | 0.022242 | 0.0089518 | 0.044491 | -0.0044718 | 0.40395 | 18.412 | 0.074 | 120.7705 | 120.6413 | 120.5592 | -0.94221 | 0.046835 | 0.087354 | -0.065509 | -0.04369 | 0.077807 | 0.10848 | -0.15499 | 0.046559 | 0.10398 | 1.3927 | 1.0628 | 1.0162 | -0.02522 | -0.10729 | 0.83378 | -120.7102 | 1.0356 | 0.92326 | 0.089482 | -120.5887 | -120.558 | 121.7593 | 121.6301 | 121.548 | 19.4007 | -121.6087 | 0.94508 | 1.0666 | 1.0973 | 1.0761 | -120.8215
2861.125 | 121.8109 | -0.9613 | 120.7397 | 1.4211e-13 | -0.068194 | -0.010925 | 0.063443 | -0.011982 | 0.050899 | -0.0054937 | 0.04458 | 0.022242 | 0.0093792 | 0.044705 | -0.0040444 | 0.42226 | 18.5035 | 0.087735 | 120.7842 | 120.6459 | 120.5729 | -0.95137 | 0.042256 | 0.087354 | -0.070087 | -0.039111 | 0.077807 | 0.099323 | -0.15957 | 0.009935 | 0.04447 | 1.3836 | 1.049 | 1.0391 | -0.093883 | -0.1668 | 0.80173 | -120.7789 | 1.0036 | 0.89122 | 0.089483 | -120.6619 | -120.6404 | 121.7455 | 121.6072 | 121.5343 | 19.4648 | -121.6911 | 0.92219 | 1.0391 | 1.0606 | 1.0487 | -120.8993
2862.8906 | 121.1929 | -0.97961 | 120.6207 | 1.4211e-13 | -0.068194 | -0.010712 | 0.063656 | -0.012623 | 0.051112 | -0.020755 | 0.044366 | 0.022242 | 0.0091656 | 0.044491 | -0.0044718 | 0.42226 | 18.5676 | 0.10147 | 120.7888 | 120.655 | 120.5775 | -0.95595 | 0.042256 | 0.087354 | -0.070087 | -0.034533 | 0.082386 | 0.1039 | -0.15499 | 0.023666 | 0.16807 | 1.4019 | 1.0811 | 1.0574 | 0.034293 | -0.043201 | 0.82462 | -120.6553 | 1.0219 | 0.90953 | 0.084904 | -120.5383 | -120.5168 | 121.7684 | 121.6346 | 121.5571 | 19.5473 | -121.5767 | 0.94508 | 1.062 | 1.0835 | 1.067 | -120.7757
2864.5781 | 121.3211 | -0.98877 | 120.7672 | 1.4211e-13 | -0.068407 | -0.010712 | 0.06387 | -0.012196 | 0.050685 | -0.0054937 | 0.04458 | 0.022242 | 0.0095928 | 0.044277 | -0.0042582 | 0.44057 | 18.6272 | 0.1152 | 120.798 | 120.6596 | 120.5913 | -0.95137 | 0.046835 | 0.087354 | -0.070087 | -0.04369 | 0.077807 | 0.1039 | -0.15499 | 0.037401 | 0.030739 | 1.4293 | 1.104 | 1.0666 | -0.10761 | -0.17595 | 0.83378 | -120.8109 | 1.0356 | 0.91868 | 0.084904 | -120.6894 | -120.6633 | 121.7867 | 121.6484 | 121.58 | 19.6159 | -121.7186 | 0.94508 | 1.0666 | 1.0927 | 1.0761 | -120.9222
2866.3281 | 121.6782 | -0.98419 | 120.7306 | 1.4211e-13 | -0.068407 | -0.010925 | 0.06387 | -0.01241 | 0.050899 | -0.013124 | 0.044366 | 0.022242 | 0.0093792 | 0.044277 | -0.0044718 | 0.44973 | 18.6913 | 0.1381 | 120.8117 | 120.6779 | 120.5958 | -0.95137 | 0.051413 | 0.087354 | -0.065509 | -0.039111 | 0.086964 | 0.10848 | -0.16415 | 0.032823 | 0.081095 | 1.4339 | 1.1223 | 1.0895 | -0.052676 | -0.13475 | 0.82004 | -120.7697 | 1.0356 | 0.91868 | 0.09864 | -120.6436 | -120.6221 | 121.7959 | 121.6621 | 121.58 | 19.6755 | -121.682 | 0.94508 | 1.0712 | 1.0927 | 1.0715 | -120.8947
2868.0938 | 121.2296 | -0.98877 | 120.2637 | 1.4211e-13 | -0.068194 | -0.010925 | 0.063656 | -0.011982 | 0.050258 | -0.020755 | 0.044366 | 0.022242 | 0.0093792 | 0.044918 | -0.0040444 | 0.46804 | 18.3204 | 0.13352 | 120.8208 | 120.6733 | 120.6096 | -0.94679 | 0.051413 | 0.078197 | -0.070087 | -0.04369 | 0.086964 | 0.099323 | -0.15957 | 0.04198 | 0.55717 | 1.4568 | 1.1223 | 1.0803 | 0.40966 | 0.34591 | 0.8292 | -120.3074 | 1.0402 | 0.91868 | 0.089483 | -120.1767 | -120.1643 | 121.8096 | 121.6621 | 121.5983 | 19.3092 | -121.2105 | 0.94508 | 1.0757 | 1.0881 | 1.067 | -120.4232
2869.7812 | 121.8338 | -0.95673 | 120.6985 | 1.4211e-13 | -0.068194 | -0.010925 | 0.06387 | -0.012623 | 0.051112 | -0.013124 | 0.044366 | 0.022456 | 0.0091656 | 0.044705 | -0.0042582 | 0.59166 | 18.2426 | 0.13352 | 120.83 | 120.6825 | 120.6233 | -0.94221 | 0.055992 | 0.082776 | -0.06093 | -0.039111 | 0.082386 | 0.099323 | -0.15499 | 0.014515 | 0.13145 | 1.5484 | 1.0902 | 1.0757 | -0.016053 | -0.075234 | 0.80173 | -120.7377 | 1.0127 | 0.8958 | 0.094061 | -120.6162 | -120.5992 | 121.7867 | 121.6392 | 121.58 | 19.1993 | -121.6408 | 0.91761 | 1.0391 | 1.056 | 1.0395 | -120.8535
2871.5312 | 121.843 | -0.97504 | 120.7855 | 1.4211e-13 | -0.068407 | -0.010712 | 0.06387 | -0.01241 | 0.050685 | -0.013124 | 0.04458 | 0.022456 | 0.0093792 | 0.044491 | -0.0042582 | 0.61913 | 18.1968 | 0.14267 | 120.8346 | 120.6917 | 120.637 | -0.95595 | 0.042256 | 0.087354 | -0.070087 | -0.039111 | 0.082386 | 0.099323 | -0.15957 | 0.019089 | 0.049056 | 1.5942 | 1.1177 | 1.0986 | -0.09387 | -0.14847 | 0.81547 | -120.8246 | 1.0173 | 0.90495 | 0.089483 | -120.7031 | -120.6862 | 121.8096 | 121.6667 | 121.6121 | 19.1718 | -121.7415 | 0.93593 | 1.0574 | 1.0744 | 1.0624 | -120.9451
2873.2344 | 121.8704 | -0.96588 | 120.7809 | 1.4211e-13 | -0.06798 | -0.010712 | 0.06387 | -0.01241 | 0.050899 | 0.0021363 | 0.043939 | 0.022028 | 0.0091656 | 0.044705 | -0.0042582 | 0.6466 | 18.2563 | 0.15183 | 120.8346 | 120.7008 | 120.637 | -0.96053 | 0.051413 | 0.087354 | -0.070087 | -0.048268 | 0.082386 | 0.099323 | -0.15957 | 0.005355 | 0.053633 | 1.6125 | 1.1177 | 1.1124 | -0.080135 | -0.1439 | 0.80631 | -120.8292 | 1.0173 | 0.89579 | 0.089483 | -120.6986 | -120.6816 | 121.8005 | 121.6667 | 121.6029 | 19.2222 | -121.7415 | 0.91761 | 1.0483 | 1.0652 | 1.0532 | -120.9405
2874.9844 | 121.6095 | -0.99792 | 120.845 | 1.4211e-13 | -0.06798 | -0.011139 | 0.064297 | -0.01241 | 0.050899 | -0.0054937 | 0.044366 | 0.022028 | 0.0093792 | 0.044491 | -0.0042582 | 0.67407 | 18.3524 | 0.16099 | 120.8437 | 120.7008 | 120.6325 | -0.95595 | 0.042256 | 0.087354 | -0.070087 | -0.039111 | 0.082386 | 0.1039 | -0.15499 | 0.041977 | -0.001297 | 1.672 | 1.1589 | 1.1169 | -0.14422 | -0.21256 | 0.84293 | -120.8841 | 1.0402 | 0.92784 | 0.084904 | -120.7626 | -120.7411 | 121.8417 | 121.6987 | 121.6304 | 19.3504 | -121.801 | 0.95881 | 1.0803 | 1.1018 | 1.0853 | -121
2876.7344 | 121.8842 | -0.96588 | 120.7764 | 1.4211e-13 | -0.068194 | -0.010925 | 0.064297 | -0.011982 | 0.050899 | -0.013124 | 0.044366 | 0.022456 | 0.0093792 | 0.044277 | -0.0040444 | 0.69238 | 18.4532 | 0.16099 | 120.8392 | 120.71 | 120.637 | -0.9651 | 0.046835 | 0.087354 | -0.06093 | -0.04369 | 0.086964 | 0.1039 | -0.15041 | 0.000776 | 0.062789 | 1.6583 | 1.1269 | 1.1261 | -0.066399 | -0.13932 | 0.81547 | -120.8201 | 1.0127 | 0.90495 | 0.089482 | -120.6894 | -120.6725 | 121.805 | 121.6758 | 121.6029 | 19.4191 | -121.7415 | 0.92219 | 1.0528 | 1.0698 | 1.0532 | -120.9268
2878.5 | 121.7697 | -0.99792 | 120.7855 | 1.4211e-13 | -0.068407 | -0.010925 | 0.064084 | -0.01241 | 0.051112 | -0.020755 | 0.044153 | 0.022456 | 0.0091656 | 0.044918 | -0.0042582 | 0.7107 | 18.5173 | 0.18388 | 120.8575 | 120.7237 | 120.6416 | -0.97884 | 0.046835 | 0.087354 | -0.065509 | -0.039111 | 0.086964 | 0.1039 | -0.15957 | 0.019083 | 0.071948 | 1.7086 | 1.1818 | 1.1627 | -0.061817 | -0.1439 | 0.83835 | -120.8246 | 1.0448 | 0.93242 | 0.094061 | -120.6986 | -120.6816 | 121.8554 | 121.7216 | 121.6396 | 19.5152 | -121.7644 | 0.95881 | 1.0849 | 1.1018 | 1.0853 | -120.9451
2880.2656 | 121.8475 | -0.97504 | 120.7809 | 1.4211e-13 | -0.068407 | -0.011139 | 0.064297 | -0.01241 | 0.051112 | -0.020755 | 0.044366 | 0.022028 | 0.0085246 | 0.044918 | -0.0040444 | 0.74275 | 18.6409 | 0.19761 | 120.8575 | 120.7237 | 120.6554 | -0.97426 | 0.046835 | 0.087354 | -0.070087 | -0.034533 | 0.091543 | 0.1039 | -0.15041 | 0.000774 | 0.076525 | 1.7178 | 1.1726 | 1.1719 | -0.05724 | -0.12558 | 0.82463 | -120.8155 | 1.0219 | 0.90495 | 0.080325 | -120.6894 | -120.677 | 121.8325 | 121.6987 | 121.6304 | 19.6159 | -121.7552 | 0.9405 | 1.0666 | 1.0789 | 1.0624 | -120.9314
2882.0156 | 121.9254 | -0.97504 | 120.7809 | 1.4211e-13 | -0.068194 | -0.011139 | 0.06387 | -0.012196 | 0.051326 | -0.013124 | 0.043939 | 0.022028 | 0.0093792 | 0.044705 | -0.0042582 | 0.77022 | 17.8992 | 0.30749 | 120.8575 | 120.7329 | 120.6691 | -0.96968 | 0.046835 | 0.091933 | -0.065509 | -0.04369 | 0.077807 | 0.1039 | -0.15499 | 0.005353 | 0.076525 | 1.7453 | 1.2825 | 1.2772 | -0.048083 | -0.11185 | 0.82005 | -120.8246 | 1.0219 | 0.90953 | 0.089482 | -120.7031 | -120.677 | 121.8325 | 121.7079 | 121.6441 | 18.8742 | -121.7506 | 0.93135 | 1.0528 | 1.0789 | 1.067 | -120.9359
2883.7812 | 121.9116 | -0.97046 | 120.8084 | 1.4211e-13 | -0.06798 | -0.010712 | 0.064297 | -0.011982 | 0.051326 | -0.0054937 | 0.044153 | 0.022242 | 0.0091656 | 0.044918 | -0.0046854 | 0.79311 | 17.6977 | 0.33954 | 120.8666 | 120.7283 | 120.6691 | -0.96968 | 0.046835 | 0.091933 | -0.065509 | -0.039111 | 0.077807 | 0.1039 | -0.15499 | 0.000775 | 0.058216 | 1.7636 | 1.31 | 1.3092 | -0.080128 | -0.13931 | 0.81547 | -120.8475 | 1.0173 | 0.90495 | 0.089482 | -120.7306 | -120.7045 | 121.8371 | 121.6987 | 121.6396 | 18.6682 | -121.7781 | 0.93135 | 1.0483 | 1.0744 | 1.0624 | -120.9634
2885.5 | 121.788 | -1.0071 | 120.7443 | 1.4211e-13 | -0.067553 | -0.010712 | 0.064084 | -0.012196 | 0.051753 | -0.020755 | 0.043939 | 0.022028 | 0.0091656 | 0.044705 | -0.0042582 | 0.90757 | 17.7206 | 0.35785 | 120.8804 | 120.7374 | 120.6645 | -0.97426 | 0.046835 | 0.087354 | -0.065509 | -0.039111 | 0.082386 | 0.1039 | -0.15957 | 0.032817 | 0.13604 | 1.9146 | 1.3649 | 1.3321 | -0.006883 | -0.079804 | 0.84751 | -120.7834 | 1.0539 | 0.94157 | 0.094061 | -120.6619 | -120.6404 | 121.8874 | 121.7445 | 121.6716 | 18.7277 | -121.7186 | 0.96797 | 1.0895 | 1.111 | 1.0944 | -120.9039
2887.25 | 121.875 | -0.99792 | 120.845 | 1.4211e-13 | -0.068407 | -0.010712 | 0.064297 | -0.012196 | 0.051326 | -0.013124 | 0.044153 | 0.022028 | 0.0093792 | 0.044705 | -0.0042582 | 0.96709 | 17.9907 | 0.44484 | 120.8758 | 120.7374 | 120.6828 | -0.97426 | 0.033099 | 0.091933 | -0.070087 | -0.039111 | 0.077807 | 0.1039 | -0.15957 | 0.023662 | 0.030751 | 1.965 | 1.4428 | 1.4191 | -0.10759 | -0.1622 | 0.83835 | -120.8841 | 1.031 | 0.92784 | 0.089483 | -120.7672 | -120.7411 | 121.8737 | 121.7354 | 121.6808 | 18.9887 | -121.8193 | 0.95881 | 1.0757 | 1.1018 | 1.0899 | -121.0046
2888.9375 | 90.3076 | -0.11902 | 89.5386 | 1.4211e-13 | -0.068194 | -0.010498 | 0.064297 | -0.012196 | 0.051326 | -0.028385 | 0.044366 | 0.022028 | 0.0091656 | 0.044918 | -0.004899 | 0.9854 | 18.0915 | 0.48147 | 120.9353 | 120.8015 | 120.7286 | -1.0246 | 0.042256 | 0.087354 | -0.065509 | -0.039111 | 0.082386 | 0.1039 | -0.15499 | -0.90561 | 31.3967 | 1.1044 | 0.60049 | 1.5061 | 31.263 | 31.19 | -0.035972 | -89.5777 | 0.16128 | 0.05351 | 0.089482 | -89.4562 | -89.4347 | 121.0543 | 120.9206 | 120.8476 | 18.2105 | -90.5632 | 0.079908 | 0.20141 | 0.22292 | 0.20637 | -89.6936
2890.6875 | 118.2678 | -0.68207 | 95.6726 | 1.4211e-13 | -0.06798 | -0.010498 | 0.064297 | -0.011982 | 0.051326 | -0.013124 | 0.044366 | 0.022456 | 0.0093792 | 0.044918 | -0.0042582 | 1.0403 | 18.1098 | 0.52725 | 120.8758 | 120.8107 | 120.7378 | -1.0063 | 0.046835 | 0.087354 | -0.065509 | -0.039111 | 0.082386 | 0.10848 | -0.15499 | -0.32425 | 25.2032 | 1.7224 | 1.2093 | 1.5336 | 25.1381 | 25.0652 | 0.52708 | -95.7117 | 0.7289 | 0.61656 | 0.089482 | -95.5902 | -95.5641 | 121.5579 | 121.4928 | 121.4198 | 18.7918 | -96.6789 | 0.64296 | 0.76445 | 0.79055 | 0.76942 | -95.8276
2892.4375 | 94.8257 | -0.98877 | 92.2897 | 1.4211e-13 | -0.068194 | -0.010498 | 0.064511 | -0.011982 | 0.051326 | -0.028385 | 0.044366 | 0.022028 | 0.0089518 | 0.045132 | -0.0044718 | 1.077 | 18.0777 | 0.55472 | 120.9399 | 120.8107 | 120.7332 | -1.0201 | 0.037677 | 0.091933 | -0.074666 | -0.04369 | 0.077807 | 0.11306 | -0.15957 | -0.031283 | 28.6501 | 2.0657 | 1.5435 | 1.5748 | 28.521 | 28.4435 | 0.8292 | -92.3334 | 1.0264 | 0.9141 | 0.084904 | -92.2119 | -92.1767 | 121.9287 | 121.7995 | 121.722 | 19.0665 | -93.3098 | 0.94508 | 1.0666 | 1.1018 | 1.0807 | -92.4493
2894.2031 | 121.4127 | -22.7417 | 88.3667 | 1.4211e-13 | -0.068194 | -0.010498 | 0.064297 | -0.01241 | 0.051112 | -0.0054937 | 0.04458 | 0.022028 | 0.0091656 | 0.045346 | -0.0044718 | 0.60082 | 17.6199 | 0.069421 | 120.4408 | 120.3116 | 120.2387 | -1.7115 | 0.046835 | 0.091933 | -0.065509 | -0.048268 | 0.082386 | 0.1039 | -0.15957 | 21.0302 | 32.0741 | 23.3425 | 22.8111 | 1.7809 | 31.9449 | 31.872 | 22.5821 | -88.415 | 22.7885 | 22.6762 | 0.094061 | -88.2843 | -88.2628 | 143.1825 | 143.0533 | 142.9804 | 40.3616 | -90.0782 | 22.6934 | 22.8241 | 22.8456 | 22.8336 | -88.5263
2895.9062 | 121.9986 | -20.4483 | 88.0554 | 1.4211e-13 | -0.068194 | -0.010284 | 0.064725 | -0.011982 | 0.05154 | -0.0054937 | 0.044366 | 0.022242 | 0.0087382 | 0.044918 | -0.0044718 | 1.077 | 17.858 | 0.53183 | 120.8895 | 120.7558 | 120.6828 | -1.0704 | 0.042256 | 0.087354 | -0.06093 | -0.039111 | 0.077807 | -0.11129 | -0.15957 | 19.3779 | 32.8341 | 21.5253 | 20.9801 | 1.6022 | 32.7003 | 32.6274 | 20.2887 | -88.0945 | 20.4906 | 20.3874 | 0.09864 | -87.9776 | -88.1667 | 141.3378 | 141.2041 | 141.1311 | 38.3063 | -89.1258 | 20.4092 | 20.5261 | 20.337 | 20.5357 | -88.215
2897.6719 | 121.9345 | -0.86975 | 115.4388 | 1.4211e-13 | -0.068194 | -0.010712 | 0.064511 | -0.011769 | 0.051326 | -0.013124 | 0.044366 | 0.022456 | 0.0091656 | 0.044705 | -0.004899 | 1.1182 | 17.8076 | 0.55472 | 120.8895 | 120.7603 | 120.6783 | -1.7756 | 0.037677 | 0.082776 | -0.070087 | -0.039111 | 0.077807 | -0.092979 | -0.15041 | -0.90582 | 5.4507 | 1.9879 | 1.4245 | 2.3303 | 5.3215 | 5.2394 | 0.71934 | -115.478 | 0.90743 | 0.79966 | 0.080325 | -115.361 | -115.5318 | 121.7593 | 121.6301 | 121.548 | 18.6773 | -117.2144 | 0.83064 | 0.94756 | 0.77677 | 0.95253 | -115.5893
2899.4219 | 121.9208 | -4.8843 | 116.5604 | 1.4211e-13 | -0.068194 | -0.010498 | 0.064084 | -0.011769 | 0.051326 | -0.013124 | 0.044366 | 0.022456 | 0.0089518 | 0.045132 | -0.0046854 | -0.16835 | 16.7454 | -0.7272 | 119.5526 | 119.4279 | 119.355 | -3.0989 | 0.046835 | 0.091933 | -0.06093 | -0.039111 | 0.077807 | -0.10214 | -0.15041 | 1.7855 | 2.9923 | 4.716 | 4.1571 | 2.3717 | 2.8675 | 2.7947 | 4.7339 | -116.5995 | 4.9312 | 4.8234 | 0.089482 | -116.4826 | -116.6625 | 124.437 | 124.3122 | 124.2394 | 21.6297 | -119.6592 | 4.8452 | 4.9621 | 4.7822 | 4.9763 | -116.7108
2901.1719 | 121.6873 | -120.195 | 1.2405 | 1.4211e-13 | -0.069476 | -0.011566 | 0.062588 | -0.010914 | 0.05389 | -0.0054937 | 0.044366 | 0.021815 | 0.0091656 | 0.045346 | -0.0044718 | -116.7433 | -72.7205 | -117.5466 | 1.27 | 1.287 | 1.4102 | -120.3651 | 0.046835 | 0.087354 | -0.06093 | -0.034533 | 0.086964 | -0.10671 | -0.15041 | -0.17014 | 0.029439 | 3.4517 | 2.6484 | 2.8185 | 0.046497 | 0.1697 | 120.0446 | -1.2751 | 120.2418 | 120.1341 | 0.089482 | -1.1536 | -1.3473 | 121.465 | 121.482 | 121.6052 | 47.4745 | -121.6057 | 120.1605 | 120.282 | 120.0883 | 120.2824 | -1.391
2902.9375 | 121.7285 | -120.1721 | 1.2314 | 1.4211e-13 | -0.069262 | -0.01178 | 0.062588 | -0.0107 | 0.054104 | -0.0054937 | 0.044366 | 0.021815 | 0.0093792 | 0.045346 | -0.0044718 | -116.638 | -72.9037 | -117.4184 | 1.2334 | 1.255 | 1.3782 | -120.3239 | 0.046835 | 0.091933 | -0.056351 | -0.034533 | 0.073228 | -0.10671 | -0.15499 | -0.15181 | 0.001968 | 3.5342 | 2.7537 | 2.9055 | 0.0236 | 0.14681 | 120.0171 | -1.2659 | 120.219 | 120.1158 | 0.09864 | -1.1582 | -1.3381 | 121.4055 | 121.4271 | 121.5503 | 47.2684 | -121.5553 | 120.1376 | 120.2453 | 120.0654 | 120.2641 | -1.3864
2904.625 | 121.5683 | -120.1859 | 1.2405 | 1.4211e-13 | -0.069689 | -0.01178 | 0.062801 | -0.010914 | 0.054104 | -0.013124 | 0.044153 | 0.022028 | 0.0087382 | 0.045132 | -0.0044718 | -116.551 | -73.2242 | -117.3085 | 1.2242 | 1.2367 | 1.3645 | -120.2965 | 0.046835 | 0.087354 | -0.065509 | -0.029954 | 0.077807 | -0.10214 | -0.15041 | -0.11061 | -0.016345 | 3.6349 | 2.8773 | 2.9879 | -0.003871 | 0.12391 | 120.0354 | -1.2705 | 120.2327 | 120.1203 | 0.084903 | -1.1627 | -1.3427 | 121.41 | 121.4225 | 121.5503 | 46.9617 | -121.537 | 120.1559 | 120.2637 | 120.0837 | 120.2732 | -1.391
2906.3125 | 121.6003 | -120.163 | 1.1993 | 1.4211e-13 | -0.069689 | -0.011994 | 0.063015 | -0.0107 | 0.05389 | -0.013124 | 0.044366 | 0.022028 | 0.0089518 | 0.045346 | -0.004899 | -116.4457 | -73.4714 | -117.2032 | 1.215 | 1.2367 | 1.3645 | -120.182 | 0.051413 | 0.091933 | -0.06093 | -0.029954 | 0.082386 | -0.12045 | -0.14583 | -0.019021 | 0.015697 | 3.7173 | 2.9597 | 2.9787 | 0.037328 | 0.16511 | 120.0171 | -1.2293 | 120.2144 | 120.102 | 0.084903 | -1.117 | -1.3198 | 121.378 | 121.3996 | 121.5274 | 46.6915 | -121.3813 | 120.133 | 120.2454 | 120.0425 | 120.2549 | -1.3452
2908.0781 | 121.55 | -120.1309 | 1.2039 | 1.4211e-13 | -0.069262 | -0.012207 | 0.062801 | -0.0107 | 0.054104 | -0.0054937 | 0.04458 | 0.022028 | 0.0093792 | 0.044918 | -0.0042582 | -116.3404 | -73.65 | -117.1254 | 1.2105 | 1.2367 | 1.3507 | -120.1591 | 0.042256 | 0.082776 | -0.065509 | -0.034533 | 0.086964 | -0.11587 | -0.15499 | -0.02817 | 0.006542 | 3.7906 | 3.0055 | 3.0337 | 0.032751 | 0.1468 | 119.9759 | -1.2385 | 120.1732 | 120.0654 | 0.089482 | -1.117 | -1.3198 | 121.3414 | 121.3676 | 121.4816 | 46.4809 | -121.363 | 120.0964 | 120.2179 | 120.015 | 120.2137 | -1.3589
2909.8281 | 121.5134 | -120.1401 | 1.2039 | 1.4211e-13 | -0.069689 | -0.012421 | 0.062801 | -0.0107 | 0.054531 | -0.013124 | 0.044153 | 0.022028 | 0.0089518 | 0.045132 | -0.0046854 | -116.258 | -73.8057 | -117.043 | 1.1555 | 1.2321 | 1.3599 | -120.1362 | 0.051413 | 0.087354 | -0.065509 | -0.039111 | 0.082386 | -0.11587 | -0.15041 | 0.00388 | -0.048399 | 3.8821 | 3.0971 | 3.0932 | 0.028172 | 0.15596 | 119.9897 | -1.243 | 120.1915 | 120.0746 | 0.084903 | -1.1215 | -1.3198 | 121.2956 | 121.3722 | 121.4999 | 46.3344 | -121.3401 | 120.101 | 120.2225 | 120.0242 | 120.2274 | -1.3543
2911.5781 | 121.5271 | -120.1035 | 1.2085 | 1.4211e-13 | -0.069476 | -0.011994 | 0.063015 | -0.011128 | 0.054531 | -0.013124 | 0.044153 | 0.022028 | 0.0087382 | 0.045346 | -0.0046854 | -116.1069 | -74.0712 | -116.9606 | 1.1601 | 1.2275 | 1.3416 | -120.127 | 0.051413 | 0.087354 | -0.06093 | -0.039111 | 0.086964 | -0.060928 | -0.086309 | -0.023583 | -0.048398 | 3.9966 | 3.1429 | 3.1665 | 0.019015 | 0.13306 | 120.0171 | -1.2476 | 120.1549 | 120.0425 | 0.025379 | -1.1215 | -1.2694 | 121.2636 | 121.331 | 121.445 | 46.0322 | -121.3355 | 120.0643 | 120.1904 | 120.0425 | 120.1908 | -1.2948
2913.2812 | 121.5134 | -120.0714 | 1.2039 | 1.4211e-13 | -0.069689 | -0.011566 | 0.063443 | -0.0107 | 0.054104 | -0.013124 | 0.044366 | 0.022028 | 0.0093792 | 0.045132 | -0.0046854 | -115.997 | -74.4009 | -116.8782 | 1.1555 | 1.2229 | 1.3461 | -120.1179 | 0.055992 | 0.078197 | -0.065509 | -0.039111 | 0.086964 | -0.12045 | -0.15041 | -0.046469 | -0.048399 | 4.0744 | 3.1932 | 3.2397 | 0.019014 | 0.14222 | 119.921 | -1.243 | 120.1274 | 120.0059 | 0.084903 | -1.117 | -1.3244 | 121.2269 | 121.2943 | 121.4175 | 45.6705 | -121.3218 | 120.0323 | 120.1584 | 119.951 | 120.1496 | -1.3543
2915.0312 | 121.344 | -120.0989 | 1.2268 | 1.4211e-13 | -0.069903 | -0.01178 | 0.063015 | -0.010487 | 0.054317 | -0.013124 | 0.044366 | 0.022028 | 0.0091656 | 0.045346 | -0.0044718 | -115.9054 | -74.6893 | -116.7912 | 1.1601 | 1.2229 | 1.3416 | -120.0996 | 0.051413 | 0.073618 | -0.06093 | -0.039111 | 0.077807 | -0.10671 | -0.15041 | -0.000687 | -0.066709 | 4.1935 | 3.3077 | 3.3084 | -0.003875 | 0.11475 | 119.9485 | -1.2659 | 120.1503 | 120.0379 | 0.089482 | -1.149 | -1.3335 | 121.259 | 121.3218 | 121.4404 | 45.4095 | -121.3264 | 120.0598 | 120.1767 | 119.9922 | 120.1725 | -1.3772
2916.7344 | 121.431 | -120.0348 | 1.2131 | 1.4211e-13 | -0.069476 | -0.01178 | 0.063015 | -0.010273 | 0.054531 | -0.020755 | 0.044366 | 0.022242 | 0.0087382 | 0.045132 | -0.0046854 | -115.8139 | -74.9732 | -116.6905 | 1.1509 | 1.2275 | 1.337 | -120.0858 | 0.046835 | 0.073618 | -0.070087 | -0.034533 | 0.082386 | -0.12503 | -0.15041 | -0.051037 | -0.062133 | 4.2209 | 3.3443 | 3.3954 | 0.014437 | 0.12391 | 119.8844 | -1.2476 | 120.0816 | 119.9647 | 0.080325 | -1.1307 | -1.3381 | 121.1857 | 121.2623 | 121.3718 | 45.0616 | -121.2989 | 120.0003 | 120.1172 | 119.9098 | 120.1084 | -1.3635
2918.5 | 121.3715 | -120.0302 | 1.2314 | 1.4211e-13 | -0.069476 | -0.011566 | 0.063015 | -0.010273 | 0.054317 | -0.020755 | 0.043939 | 0.022028 | 0.0087382 | 0.045132 | -0.0046854 | -115.7223 | -75.2342 | -116.6081 | 1.1555 | 1.2138 | 1.3416 | -120.0675 | 0.046835 | 0.073618 | -0.070087 | -0.039111 | 0.077807 | -0.12503 | -0.14583 | -0.0373 | -0.075865 | 4.3079 | 3.4222 | 3.4595 | -0.01761 | 0.11018 | 119.8844 | -1.2705 | 120.077 | 119.9601 | 0.075746 | -1.1536 | -1.3564 | 121.1857 | 121.244 | 121.3718 | 44.796 | -121.2989 | 119.9911 | 120.108 | 119.9052 | 120.1038 | -1.3772
2920.2031 | 121.4127 | -119.9936 | 1.1993 | 1.4211e-13 | -0.069262 | -0.011566 | 0.063015 | -0.010059 | 0.054958 | -0.013124 | 0.044366 | 0.022028 | 0.0091656 | 0.045132 | -0.0046854 | -115.6078 | -75.541 | -116.5211 | 1.1509 | 1.2229 | 1.337 | -120.0584 | 0.042256 | 0.082776 | -0.070087 | -0.039111 | 0.077807 | -0.097557 | -0.15499 | -0.064763 | -0.0484 | 4.3858 | 3.4725 | 3.5373 | 0.023591 | 0.13764 | 119.8386 | -1.2385 | 120.0358 | 119.9235 | 0.084904 | -1.1215 | -1.2969 | 121.1445 | 121.2165 | 121.3306 | 44.4526 | -121.2577 | 119.9545 | 120.0714 | 119.896 | 120.0764 | -1.3543
2921.9688 | 121.3806 | -120.0073 | 1.181 | 1.4211e-13 | -0.069476 | -0.011994 | 0.063229 | -0.010273 | 0.054745 | -0.020755 | 0.043939 | 0.021815 | 0.0087382 | 0.045132 | -0.004899 | -115.5071 | -75.7928 | -116.4295 | 1.1509 | 1.2184 | 1.3507 | -120.0446 | 0.046835 | 0.073618 | -0.070087 | -0.039111 | 0.077807 | -0.12045 | -0.15499 | -0.037293 | -0.030089 | 4.5002 | 3.5778 | 3.6151 | 0.037323 | 0.16969 | 119.8523 | -1.2201 | 120.0542 | 119.9372 | 0.084904 | -1.1032 | -1.3015 | 121.1583 | 121.2257 | 121.358 | 44.2145 | -121.2256 | 119.9682 | 120.0851 | 119.8869 | 120.0809 | -1.336
2923.6719 | 121.3303 | -120.0027 | 1.2314 | 1.4211e-13 | -0.069689 | -0.011994 | 0.063015 | -0.010273 | 0.054745 | -0.020755 | 0.044366 | 0.021815 | 0.0093792 | 0.045132 | -0.004899 | -115.4064 | -76.0858 | -116.3334 | 1.1418 | 1.2229 | 1.3324 | -120.0217 | 0.051413 | 0.06904 | -0.070087 | -0.039111 | 0.077807 | -0.12045 | -0.15041 | -0.018975 | -0.0896 | 4.5964 | 3.6694 | 3.6884 | -0.008452 | 0.10102 | 119.8523 | -1.2705 | 120.0542 | 119.9327 | 0.080325 | -1.1536 | -1.3518 | 121.1445 | 121.2257 | 121.3351 | 43.9169 | -121.2531 | 119.9636 | 120.0806 | 119.8823 | 120.0718 | -1.3818
2925.4219 | 121.2158 | -120.0119 | 1.2222 | 1.4211e-13 | -0.069262 | -0.011353 | 0.062801 | -0.010059 | 0.054745 | -0.013124 | 0.043939 | 0.022242 | 0.0089518 | 0.045132 | -0.0046854 | -115.2919 | -76.3972 | -116.2464 | 1.1464 | 1.2138 | 1.3324 | -120.0263 | 0.046835 | 0.073618 | -0.070087 | -0.039111 | 0.073228 | -0.12503 | -0.15041 | -0.014399 | -0.075867 | 4.72 | 3.7655 | 3.7799 | -0.008455 | 0.11017 | 119.8615 | -1.2613 | 120.0587 | 119.9418 | 0.080325 | -1.149 | -1.3473 | 121.1583 | 121.2257 | 121.3443 | 43.6147 | -121.2485 | 119.9728 | 120.0851 | 119.8869 | 120.0855 | -1.3726
2927.1719 | 121.1609 | -119.9799 | 1.2222 | 1.4211e-13 | -0.069476 | -0.01178 | 0.063443 | -0.010059 | 0.054958 | -0.0054937 | 0.044153 | 0.021815 | 0.0089518 | 0.045346 | -0.0044718 | -115.1775 | -76.6169 | -116.1548 | 1.1464 | 1.2184 | 1.3324 | -120.0126 | 0.042256 | 0.073618 | -0.06093 | -0.039111 | 0.086964 | -0.12961 | -0.15041 | -0.032707 | -0.075867 | 4.8024 | 3.825 | 3.8578 | -0.003876 | 0.11017 | 119.8294 | -1.2613 | 120.0221 | 119.9189 | 0.089482 | -1.1353 | -1.3518 | 121.1262 | 121.1982 | 121.3123 | 43.3629 | -121.2348 | 119.9407 | 120.0668 | 119.8503 | 120.0535 | -1.3726
2928.875 | 121.3531 | -119.9524 | 1.1856 | 1.4211e-13 | -0.069262 | -0.011353 | 0.063015 | -0.010059 | 0.055386 | -0.013124 | 0.044153 | 0.022028 | 0.0089518 | 0.045559 | -0.0046854 | -115.0538 | -76.91 | -116.0587 | 1.1418 | 1.2184 | 1.3278 | -120.008 | 0.051413 | 0.073618 | -0.065509 | -0.034533 | 0.082386 | -0.12503 | -0.14583 | -0.055593 | -0.043824 | 4.8986 | 3.8937 | 3.9493 | 0.032745 | 0.14222 | 119.8066 | -1.2201 | 120.0038 | 119.8869 | 0.080324 | -1.1032 | -1.3106 | 121.0942 | 121.1707 | 121.2802 | 43.0424 | -121.1936 | 119.9179 | 120.0348 | 119.8274 | 120.026 | -1.3314
2930.6406 | 121.344 | -119.9524 | 1.1948 | 1.4211e-13 | -0.069262 | -0.011566 | 0.063229 | -0.010059 | 0.055172 | -0.013124 | 0.044153 | 0.021815 | 0.0089518 | 0.045346 | -0.0046854 | -114.9348 | -77.1847 | -115.9625 | 1.1418 | 1.2184 | 1.3324 | -119.9942 | 0.051413 | 0.082776 | -0.070087 | -0.039111 | 0.077807 | -0.11587 | -0.15041 | -0.041856 | -0.052979 | 5.0176 | 3.9899 | 4.0317 | 0.02359 | 0.13764 | 119.802 | -1.2339 | 120.0038 | 119.8823 | 0.080325 | -1.117 | -1.3106 | 121.0942 | 121.1707 | 121.2848 | 42.7677 | -121.189 | 119.9133 | 120.0302 | 119.8365 | 120.0352 | -1.3452
2932.4062 | 121.344 | -119.9249 | 1.1948 | 1.4211e-13 | -0.069476 | -0.011566 | 0.063443 | -0.010273 | 0.055599 | -0.020755 | 0.043725 | 0.021601 | 0.0087382 | 0.045132 | -0.0046854 | -114.8066 | -77.464 | -115.8526 | 1.1418 | 1.2092 | 1.3324 | -119.9851 | 0.046835 | 0.073618 | -0.065509 | -0.039111 | 0.082386 | -0.097557 | -0.15041 | -0.060164 | -0.052979 | 5.1183 | 4.0723 | 4.1324 | 0.014432 | 0.13764 | 119.7745 | -1.2339 | 119.9718 | 119.8594 | 0.084903 | -1.1124 | -1.2923 | 121.0667 | 121.1341 | 121.2573 | 42.461 | -121.1799 | 119.8858 | 120.0073 | 119.8274 | 119.9985 | -1.3452
2934.1719 | 121.344 | -119.9249 | 1.2085 | 1.4211e-13 | -0.069476 | -0.011353 | 0.063229 | -0.010059 | 0.055813 | -0.0054937 | 0.044366 | 0.022028 | 0.0087382 | 0.045346 | -0.0044718 | -114.6967 | -77.7891 | -115.7428 | 1.1464 | 1.2138 | 1.3232 | -119.9714 | 0.042256 | 0.073618 | -0.065509 | -0.029954 | 0.082386 | -0.11129 | -0.15041 | -0.046427 | -0.062134 | 5.2282 | 4.1822 | 4.2286 | 0.005278 | 0.11475 | 119.7745 | -1.2385 | 119.9672 | 119.8594 | 0.084903 | -1.1261 | -1.3198 | 121.0713 | 121.1387 | 121.2482 | 42.1359 | -121.1799 | 119.895 | 120.0073 | 119.8136 | 119.9985 | -1.3589
2935.9375 | 121.3028 | -119.9158 | 1.2039 | 1.4211e-13 | -0.069262 | -0.011566 | 0.063229 | -0.0098456 | 0.055599 | -0.028385 | 0.043939 | 0.022028 | 0.0093792 | 0.045773 | -0.0046854 | -114.5685 | -78.0867 | -115.6466 | 1.1464 | 1.2138 | 1.3278 | -119.9759 | 0.051413 | 0.078197 | -0.06093 | -0.039111 | 0.082386 | -0.12503 | -0.15499 | -0.060162 | -0.057556 | 5.3472 | 4.2692 | 4.3293 | 0.009856 | 0.12391 | 119.7608 | -1.243 | 119.9672 | 119.8548 | 0.094061 | -1.1215 | -1.3289 | 121.0621 | 121.1295 | 121.2436 | 41.8291 | -121.1799 | 119.8767 | 119.9982 | 119.7907 | 119.994 | -1.3589
2937.6406 | 121.3028 | -119.8883 | 1.2085 | 1.4211e-13 | -0.069903 | -0.01178 | 0.063443 | -0.009632 | 0.055599 | 0.0021363 | 0.044153 | 0.021815 | 0.0089518 | 0.045132 | -0.0046854 | -114.4449 | -78.3522 | -115.5413 | 1.1509 | 1.2138 | 1.3278 | -120.008 | 0.055992 | 0.078197 | -0.06093 | -0.039111 | 0.082386 | -0.0884 | -0.14583 | -0.11968 | -0.057555 | 5.4434 | 4.347 | 4.4667 | 0.005278 | 0.11933 | 119.7425 | -1.2476 | 119.9443 | 119.8274 | 0.084903 | -1.1261 | -1.2969 | 121.0392 | 121.1021 | 121.2161 | 41.5361 | -121.2165 | 119.8492 | 119.9707 | 119.7999 | 119.9665 | -1.3543
2939.4062 | 121.2158 | -119.6594 | 1.4282 | 1.4211e-13 | -0.069903 | -0.011139 | 0.063656 | -0.009632 | 0.056027 | -0.013124 | 0.043939 | 0.021815 | 0.0091656 | 0.045559 | -0.0046854 | -114.0878 | -78.4942 | -115.2117 | 1.3295 | 1.4015 | 1.511 | -119.747 | 0.046835 | 0.06904 | -0.065509 | -0.039111 | 0.086964 | -0.12503 | -0.15041 | -0.087563 | -0.098725 | 5.5716 | 4.4477 | 4.5353 | -0.026713 | 0.082745 | 119.509 | -1.4673 | 119.7063 | 119.5939 | 0.084903 | -1.3413 | -1.5533 | 120.9889 | 121.0609 | 121.1704 | 41.1653 | -121.1752 | 119.6203 | 119.7464 | 119.5344 | 119.7285 | -1.5786
2941.1562 | 121.5271 | -0.68207 | 120.5338 | 1.4211e-13 | -0.068194 | -0.009857 | 0.065152 | -0.011341 | 0.052394 | -0.0054937 | 0.043939 | 0.022028 | 0.0089518 | 0.045346 | -0.0046854 | 2.8717 | 16.2921 | 1.8824 | 120.1524 | 120.0827 | 119.8907 | -2.3663 | 0.051413 | 0.064461 | -0.065509 | -0.039111 | 0.082386 | -0.12503 | -0.15041 | -1.6842 | -0.38135 | 3.5538 | 2.5645 | 4.2487 | -0.4511 | -0.64302 | 0.53166 | -120.5729 | 0.73348 | 0.61656 | 0.084903 | -120.4514 | -120.6588 | 120.8345 | 120.7647 | 120.5728 | 16.9741 | -122.9 | 0.64296 | 0.76445 | 0.55704 | 0.74653 | -120.6842
2942.9062 | 121.6278 | -0.45776 | 120.8954 | 1.4211e-13 | -0.068194 | -0.009857 | 0.065366 | -0.0107 | 0.052608 | -0.0054937 | 0.044366 | 0.022242 | 0.0091656 | 0.045559 | -0.0044718 | 3.5172 | 16.6355 | 2.5646 | 121.0223 | 120.8931 | 120.8156 | -0.59879 | 0.037677 | 0.064461 | -0.06093 | -0.034533 | 0.082386 | -0.12961 | -0.15499 | -0.14103 | 0.12691 | 3.975 | 3.0223 | 3.1634 | -0.002261 | -0.079772 | 0.30277 | -120.9299 | 0.49544 | 0.39683 | 0.094061 | -120.813 | -121.025 | 121.4801 | 121.3509 | 121.2734 | 17.0932 | -121.4942 | 0.42323 | 0.54015 | 0.32816 | 0.52223 | -121.0504
2944.6094 | 115.9332 | -0.22888 | 115.8691 | 1.4211e-13 | -0.068407 | -0.0096432 | 0.061519 | -0.010487 | 0.048121 | -0.013124 | 0.043725 | 0.021815 | 0.0093792 | 0.045559 | -0.0042582 | 3.0731 | 15.5458 | 2.1296 | 115.2901 | 115.1832 | 115.1198 | -0.94679 | 0.046835 | 0.06904 | -0.065509 | -0.034533 | 0.077807 | -0.12961 | -0.15041 | -0.71791 | -0.57899 | 3.302 | 2.3585 | 3.0764 | -0.68594 | -0.74931 | 0.07847 | -115.9037 | 0.27572 | 0.16337 | 0.084903 | -115.7913 | -115.9987 | 115.519 | 115.4121 | 115.3487 | 15.7746 | -116.8159 | 0.19435 | 0.30669 | 0.099275 | 0.29792 | -116.0196
2946.375 | 120.9961 | -0.59967 | 120.4514 | 1.4211e-13 | -0.068407 | -0.0094296 | 0.065152 | -0.010914 | 0.052394 | -0.0054937 | 0.043939 | 0.021815 | 0.0089518 | 0.045773 | -0.004899 | 3.6729 | 16.521 | 2.6699 | 120.45 | 120.3162 | 120.312 | -0.5759 | 0.046835 | 0.064461 | -0.070087 | -0.034533 | 0.082386 | -0.092979 | -0.15957 | 0.023773 | -0.001362 | 4.2726 | 3.2696 | 3.2458 | -0.13518 | -0.13939 | 0.4401 | -120.4859 | 0.6465 | 0.52958 | 0.089483 | -120.369 | -120.5443 | 121.0497 | 120.9159 | 120.9116 | 17.1207 | -121.0273 | 0.56514 | 0.68206 | 0.50669 | 0.66413 | -120.6109
2948.1406 | 121.1472 | -0.52643 | 120.5292 | 1.4211e-13 | -0.068194 | -0.0092158 | 0.065579 | -0.010273 | 0.052394 | -0.0054937 | 0.044153 | 0.022028 | 0.0091656 | 0.045559 | -0.0051128 | 3.8698 | 16.64 | 2.8301 | 120.6698 | 120.536 | 120.4768 | -0.50263 | 0.046835 | 0.06904 | -0.070087 | -0.034533 | 0.082386 | -0.12503 | -0.15499 | 0.023794 | 0.14058 | 4.3962 | 3.3566 | 3.3328 | 0.006794 | -0.052378 | 0.37144 | -120.5637 | 0.57326 | 0.45634 | 0.084904 | -120.4468 | -120.6542 | 121.1962 | 121.0624 | 121.0032 | 17.1665 | -121.0318 | 0.4919 | 0.60881 | 0.4014 | 0.59547 | -120.6842
2949.8438 | 121.2158 | -0.52643 | 120.7764 | 1.4211e-13 | -0.068194 | -0.0092158 | 0.065793 | -0.0107 | 0.052181 | -0.020755 | 0.043939 | 0.021601 | 0.0089518 | 0.045346 | -0.004899 | 4.0392 | 16.727 | 2.9537 | 120.7888 | 120.6504 | 120.5913 | -0.47516 | 0.042256 | 0.059882 | -0.06093 | -0.029954 | 0.086964 | -0.12503 | -0.15041 | 0.051268 | 0.012427 | 4.5656 | 3.4802 | 3.4289 | -0.12592 | -0.1851 | 0.37602 | -120.8063 | 0.56868 | 0.4655 | 0.089482 | -120.6894 | -120.9014 | 121.3152 | 121.1769 | 121.1177 | 17.2535 | -121.2515 | 0.49647 | 0.61339 | 0.4014 | 0.58631 | -120.9268
2951.6094 | 120.8267 | -0.52643 | 120.8405 | 1.4211e-13 | -0.067766 | -0.0087886 | 0.065579 | -0.0107 | 0.052822 | -0.020755 | 0.043939 | 0.021815 | 0.0085246 | 0.045559 | -0.0044718 | 4.1811 | 16.8003 | 3.059 | 120.8529 | 120.7145 | 120.6599 | -0.466 | 0.046835 | 0.064461 | -0.065509 | -0.039111 | 0.086964 | -0.12503 | -0.15041 | 0.060425 | 0.012437 | 4.7075 | 3.5855 | 3.525 | -0.12591 | -0.18051 | 0.37602 | -120.8796 | 0.57326 | 0.46092 | 0.084903 | -120.7535 | -120.9655 | 121.3793 | 121.241 | 121.1864 | 17.3267 | -121.3065 | 0.48732 | 0.61339 | 0.4014 | 0.59089 | -120.9909
2953.375 | 120.8771 | -0.48065 | 120.7993 | 1.4211e-13 | -0.068407 | -0.0090022 | 0.066007 | -0.0107 | 0.052608 | -0.013124 | 0.043939 | 0.022028 | 0.0089518 | 0.045773 | -0.0051128 | 4.3093 | 16.8781 | 3.1598 | 120.9078 | 120.7649 | 120.7149 | -0.47516 | 0.037677 | 0.064461 | -0.065509 | -0.039111 | 0.086964 | -0.10214 | -0.15499 | 0.005492 | 0.10858 | 4.79 | 3.6404 | 3.6349 | -0.03434 | -0.08437 | 0.32566 | -120.8384 | 0.51833 | 0.41514 | 0.089482 | -120.7123 | -120.9014 | 121.3885 | 121.2456 | 121.1955 | 17.3588 | -121.2744 | 0.44154 | 0.56762 | 0.37852 | 0.54511 | -120.9542
2955.1406 | 121.4218 | -0.46692 | 120.8771 | 1.4211e-13 | -0.068194 | -0.0090022 | 0.066007 | -0.010487 | 0.053249 | -0.013124 | 0.044153 | 0.022242 | 0.0087382 | 0.045559 | -0.0046854 | 4.4604 | 17.0155 | 3.2742 | 120.9399 | 120.8107 | 120.7515 | -0.466 | 0.042256 | 0.06904 | -0.06093 | -0.039111 | 0.091543 | -0.12961 | -0.15499 | 0.000916 | 0.062806 | 4.9273 | 3.7411 | 3.7402 | -0.066371 | -0.12556 | 0.31193 | -120.9162 | 0.50917 | 0.40599 | 0.094061 | -120.7855 | -121.0067 | 121.4068 | 121.2776 | 121.2184 | 17.4824 | -121.3431 | 0.42781 | 0.55846 | 0.33731 | 0.53596 | -121.0321
2956.8906 | 121.0373 | -0.48065 | 120.7672 | 1.4211e-13 | -0.068194 | -0.0090022 | 0.066434 | -0.010487 | 0.053463 | -0.0054937 | 0.043725 | 0.021601 | 0.0087382 | 0.045773 | -0.0046854 | 4.6206 | 17.1849 | 3.3841 | 120.9994 | 120.8473 | 120.7836 | -0.45227 | 0.042256 | 0.06904 | -0.06093 | -0.04369 | 0.091543 | -0.12045 | -0.15499 | 0.028386 | 0.23219 | 5.1013 | 3.8647 | 3.8364 | 0.080123 | 0.016352 | 0.32566 | -120.8109 | 0.52291 | 0.41972 | 0.094061 | -120.6757 | -120.8877 | 121.4801 | 121.328 | 121.2642 | 17.6656 | -121.2195 | 0.43696 | 0.5722 | 0.3602 | 0.54969 | -120.9222
2958.5938 | 120.9091 | -0.48981 | 120.4834 | 1.4211e-13 | -0.06798 | -0.0087886 | 0.066648 | -0.010487 | 0.053463 | -0.013124 | 0.044153 | 0.021601 | 0.0091656 | 0.045773 | -0.004899 | 4.7351 | 17.3177 | 3.4665 | 120.9994 | 120.8611 | 120.7973 | -0.48432 | 0.046835 | 0.06904 | -0.070087 | -0.039111 | 0.086964 | -0.12961 | -0.15499 | 0.005489 | 0.516 | 5.2249 | 3.9563 | 3.9508 | 0.37767 | 0.3139 | 0.33482 | -120.5225 | 0.53664 | 0.41972 | 0.084904 | -120.3964 | -120.613 | 121.4892 | 121.3509 | 121.2871 | 17.8075 | -120.9677 | 0.4507 | 0.57677 | 0.3602 | 0.55885 | -120.6384
2960.2969 | 120.8176 | -0.4715 | 120.7626 | 1.4211e-13 | -0.06798 | -0.0085748 | 0.066861 | -0.010059 | 0.053249 | -0.0054937 | 0.044153 | 0.021815 | 0.0091656 | 0.045987 | -0.0051128 | 4.9045 | 17.5649 | 3.5947 | 121.036 | 120.9023 | 120.8522 | -0.45227 | 0.042256 | 0.06904 | -0.065509 | -0.034533 | 0.082386 | -0.12503 | -0.15041 | 0.019231 | 0.27339 | 5.376 | 4.0662 | 4.047 | 0.13965 | 0.089609 | 0.32109 | -120.7972 | 0.51375 | 0.40599 | 0.084903 | -120.6802 | -120.8877 | 121.5075 | 121.3738 | 121.3237 | 18.0364 | -121.2149 | 0.43696 | 0.55388 | 0.34647 | 0.54054 | -120.913
2962.0469 | 121.4035 | -0.42114 | 121.0098 | 1.4211e-13 | -0.06798 | -0.0085748 | 0.066861 | -0.010273 | 0.053676 | 0.0021363 | 0.043939 | 0.022028 | 0.0091656 | 0.045987 | -0.0046854 | 5.0785 | 17.8259 | 3.7229 | 121.0818 | 120.9527 | 120.8935 | -0.43853 | 0.042256 | 0.073618 | -0.065509 | -0.039111 | 0.091543 | -0.11587 | -0.15499 | -0.017386 | 0.071984 | 5.4996 | 4.144 | 4.1614 | -0.057176 | -0.11638 | 0.26615 | -121.0489 | 0.4634 | 0.35563 | 0.089482 | -120.9183 | -121.1257 | 121.503 | 121.3738 | 121.3146 | 18.247 | -121.4484 | 0.38203 | 0.51269 | 0.30527 | 0.49476 | -121.1648
2963.8125 | 120.7581 | -0.46692 | 120.4834 | 1.4211e-13 | -0.068407 | -0.0083612 | 0.066861 | -0.010273 | 0.05389 | -0.013124 | 0.043939 | 0.021815 | 0.0089518 | 0.045559 | -0.004899 | 5.2479 | 18.1006 | 3.8282 | 121.1139 | 120.9847 | 120.9255 | -0.42479 | 0.051413 | 0.06904 | -0.070087 | -0.034533 | 0.082386 | -0.12045 | -0.15957 | 0.042127 | 0.63046 | 5.7148 | 4.2951 | 4.253 | 0.50131 | 0.4421 | 0.30735 | -120.5179 | 0.51833 | 0.39683 | 0.089483 | -120.401 | -120.6038 | 121.5808 | 121.4516 | 121.3924 | 18.5675 | -120.9082 | 0.43239 | 0.5493 | 0.34647 | 0.53596 | -120.643
2965.5625 | 109.5978 | -0.38452 | 120.3873 | 1.4211e-13 | -0.068194 | -0.0081476 | 0.066861 | -0.0098456 | 0.054317 | -0.020755 | 0.043939 | 0.022028 | 0.0087382 | 0.045559 | -0.0046854 | 5.3852 | 18.3845 | 3.9426 | 121.1047 | 120.9755 | 120.9163 | -0.45227 | 0.042256 | 0.059882 | -0.070087 | -0.034533 | 0.086964 | -0.12045 | -0.15041 | -0.067745 | 0.71743 | 5.7698 | 4.3272 | 4.3949 | 0.58828 | 0.52907 | 0.23411 | -120.4218 | 0.42678 | 0.31443 | 0.080325 | -120.3003 | -120.5077 | 121.4892 | 121.3601 | 121.3009 | 18.769 | -120.8395 | 0.34999 | 0.47148 | 0.26407 | 0.4444 | -120.5377
2967.3125 | 120.8633 | -0.50354 | 121.0419 | 1.4211e-13 | -0.06798 | -0.0083612 | 0.067289 | -0.009632 | 0.054317 | -0.0054937 | 0.043939 | 0.021815 | 0.0087382 | 0.045773 | -0.0051128 | 5.5501 | 18.7737 | 4.0663 | 121.1368 | 120.9984 | 120.953 | -0.44769 | 0.051413 | 0.06904 | -0.06093 | -0.034533 | 0.077807 | -0.10671 | -0.15041 | 0.055853 | 0.094881 | 6.0536 | 4.5698 | 4.5139 | -0.04343 | -0.088898 | 0.35313 | -121.0764 | 0.55495 | 0.44261 | 0.089482 | -120.9641 | -121.1486 | 121.6403 | 121.502 | 121.4565 | 19.2772 | -121.4896 | 0.46901 | 0.58135 | 0.39683 | 0.57258 | -121.1923
2969.0781 | 120.9778 | -0.48065 | 120.3735 | 1.4211e-13 | -0.068194 | -0.0081476 | 0.067289 | -0.009632 | 0.054104 | -0.013124 | 0.043725 | 0.021601 | 0.0091656 | 0.045773 | -0.004899 | 5.7103 | 19.1491 | 4.1807 | 121.1505 | 121.0122 | 120.953 | -0.45685 | 0.051413 | 0.064461 | -0.065509 | -0.034533 | 0.096121 | -0.12503 | -0.15957 | 0.023807 | 0.77695 | 6.1909 | 4.6614 | 4.6376 | 0.63864 | 0.57944 | 0.32108 | -120.4081 | 0.53207 | 0.41514 | 0.094061 | -120.2774 | -120.4986 | 121.6311 | 121.4928 | 121.4336 | 19.6298 | -120.8304 | 0.44612 | 0.57677 | 0.35562 | 0.54511 | -120.5331
2970.8438 | 121.4996 | -0.45776 | 121.1105 | 1.4211e-13 | -0.06798 | -0.0079338 | 0.067502 | -0.0094182 | 0.054958 | -0.020755 | 0.043725 | 0.021815 | 0.0089518 | 0.0462 | -0.004899 | 5.8889 | 19.6024 | 4.2952 | 121.1505 | 121.0213 | 120.9713 | -0.466 | 0.046835 | 0.064461 | -0.06093 | -0.039111 | 0.096121 | -0.12045 | -0.15041 | -0.008239 | 0.039952 | 6.3466 | 4.7529 | 4.7612 | -0.0892 | -0.13925 | 0.30735 | -121.1496 | 0.5046 | 0.39683 | 0.089482 | -121.0144 | -121.231 | 121.6083 | 121.4791 | 121.4291 | 20.0602 | -121.5765 | 0.41865 | 0.55388 | 0.33731 | 0.52223 | -121.2609
2972.6094 | 121.8109 | -0.43945 | 120.6848 | 1.4211e-13 | -0.06798 | -0.0079338 | 0.067716 | -0.009632 | 0.054958 | -0.020755 | 0.044366 | 0.021815 | 0.0087382 | 0.045346 | -0.0046854 | 6.072 | 20.074 | 4.4234 | 121.1825 | 121.0442 | 120.9804 | -0.46142 | 0.037677 | 0.06904 | -0.065509 | -0.039111 | 0.082386 | -0.12045 | -0.15499 | -0.021971 | 0.49772 | 6.5114 | 4.8628 | 4.8848 | 0.35941 | 0.29563 | 0.28446 | -120.7239 | 0.47713 | 0.37394 | 0.089482 | -120.6024 | -120.8053 | 121.622 | 121.4837 | 121.4199 | 20.5135 | -121.1462 | 0.40034 | 0.52184 | 0.319 | 0.50849 | -120.8398
2974.3594 | 121.6873 | -0.45319 | 121.138 | 1.4211e-13 | -0.067553 | -0.0075064 | 0.067716 | -0.0094182 | 0.055386 | -0.0054937 | 0.043939 | 0.021815 | 0.0089518 | 0.045773 | -0.0044718 | 6.2597 | 20.5639 | 4.5653 | 121.1963 | 121.0717 | 121.0125 | -0.45685 | 0.042256 | 0.064461 | -0.06093 | -0.039111 | 0.082386 | -0.12045 | -0.15499 | -0.003659 | 0.05827 | 6.7129 | 5.0185 | 5.0221 | -0.066297 | -0.12551 | 0.29819 | -121.1771 | 0.49544 | 0.39226 | 0.094061 | -121.0556 | -121.2585 | 121.6495 | 121.5249 | 121.4657 | 21.0171 | -121.5948 | 0.41407 | 0.53557 | 0.33274 | 0.51765 | -121.293
2976.0781 | 121.7285 | -0.45319 | 120.9457 | 1.4211e-13 | -0.068194 | -0.0075064 | 0.067716 | -0.008991 | 0.055386 | -0.013124 | 0.043939 | 0.022028 | 0.0087382 | 0.045773 | -0.004899 | 6.4657 | 21.0172 | 4.6981 | 121.2192 | 121.0854 | 121.0308 | -0.44769 | 0.046835 | 0.06904 | -0.074666 | -0.04369 | 0.082386 | -0.12045 | -0.15499 | 0.005499 | 0.27342 | 6.9189 | 5.1512 | 5.1458 | 0.1397 | 0.085068 | 0.29819 | -120.9894 | 0.50002 | 0.37852 | 0.080325 | -120.8634 | -121.0662 | 121.6723 | 121.5386 | 121.484 | 21.4704 | -121.3934 | 0.4095 | 0.53557 | 0.33274 | 0.52223 | -121.1007
2977.8281 | 121.1609 | -0.46234 | 121.0144 | 1.4211e-13 | -0.067766 | -0.0070792 | 0.068571 | -0.0092046 | 0.055599 | -0.013124 | 0.043725 | 0.022028 | 0.0087382 | 0.045773 | -0.0044718 | 6.626 | 21.4522 | 4.84 | 121.2283 | 121.09 | 121.04 | -0.45685 | 0.037677 | 0.073618 | -0.065509 | -0.029954 | 0.082386 | -0.12045 | -0.15499 | 0.005496 | 0.21392 | 7.0883 | 5.3023 | 5.2968 | 0.075614 | 0.025561 | 0.30735 | -121.0444 | 0.50002 | 0.39683 | 0.089482 | -120.932 | -121.1349 | 121.6907 | 121.5524 | 121.5023 | 21.9145 | -121.4712 | 0.43239 | 0.54473 | 0.34189 | 0.53596 | -121.1694
2979.5938 | 121.7194 | -0.4715 | 120.9229 | 1.4211e-13 | -0.06798 | -0.0070792 | 0.068357 | -0.0094182 | 0.055813 | -0.013124 | 0.044366 | 0.022028 | 0.0085246 | 0.045987 | -0.004899 | 6.7954 | 21.9192 | 4.927 | 121.2329 | 121.0992 | 121.0491 | -0.45685 | 0.046835 | 0.06904 | -0.065509 | -0.029954 | 0.082386 | -0.10214 | -0.15499 | 0.014652 | 0.31005 | 7.2669 | 5.3985 | 5.3838 | 0.17632 | 0.12627 | 0.31651 | -120.9528 | 0.51833 | 0.40599 | 0.089482 | -120.8405 | -121.025 | 121.7044 | 121.5707 | 121.5206 | 22.3907 | -121.3797 | 0.44154 | 0.55388 | 0.36936 | 0.54054 | -121.0778
2981.3438 | 121.7102 | -0.50354 | 121.138 | 1.4211e-13 | -0.067766 | -0.0066518 | 0.068571 | -0.0094182 | 0.05624 | -0.013124 | 0.043725 | 0.021815 | 0.0087382 | 0.045987 | -0.0053264 | 6.9694 | 22.3404 | 5.0277 | 121.2283 | 121.0854 | 121.0308 | -0.4889 | 0.051413 | 0.073618 | -0.074666 | -0.034533 | 0.082386 | -0.10671 | -0.15499 | 0.014643 | 0.090319 | 7.4729 | 5.5312 | 5.5166 | -0.05256 | -0.10719 | 0.34855 | -121.1725 | 0.55495 | 0.42887 | 0.080325 | -121.0556 | -121.2447 | 121.7319 | 121.589 | 121.5343 | 22.8439 | -121.6269 | 0.46901 | 0.58593 | 0.39683 | 0.57716 | -121.293
2983.0938 | 121.7285 | -0.52185 | 120.8267 | 1.4211e-13 | -0.067553 | -0.006438 | 0.068785 | -0.0087772 | 0.056668 | -0.020755 | 0.043939 | 0.021815 | 0.0087382 | 0.046414 | -0.0051128 | 7.1479 | 22.8028 | 5.0918 | 121.2192 | 121.0809 | 121.0262 | -0.50263 | 0.042256 | 0.06904 | -0.070087 | -0.034533 | 0.082386 | -0.13419 | -0.15499 | 0.019217 | 0.39244 | 7.6698 | 5.6136 | 5.5944 | 0.25414 | 0.19951 | 0.36686 | -120.8613 | 0.56411 | 0.45176 | 0.084904 | -120.7443 | -120.9609 | 121.741 | 121.6027 | 121.5481 | 23.3247 | -121.3294 | 0.48732 | 0.60424 | 0.38766 | 0.59089 | -120.9817
2984.8594 | 120.9549 | -0.59052 | 120.8221 | 1.4211e-13 | -0.067766 | -0.0066518 | 0.068998 | -0.0087772 | 0.056881 | -0.013124 | 0.044153 | 0.022028 | 0.0087382 | 0.045987 | -0.0051128 | 7.3082 | 23.16 | 5.1788 | 121.2008 | 121.0671 | 121.0171 | -0.52553 | 0.042256 | 0.06904 | -0.065509 | -0.04369 | 0.082386 | -0.12503 | -0.16415 | 0.064986 | 0.37871 | 7.8987 | 5.7693 | 5.7043 | 0.24498 | 0.19493 | 0.42637 | -120.8658 | 0.63277 | 0.52501 | 0.09864 | -120.7398 | -120.9472 | 121.7914 | 121.6576 | 121.6076 | 23.7505 | -121.3477 | 0.54683 | 0.6729 | 0.46549 | 0.65956 | -120.9863
2986.5625 | 120.9137 | -0.56763 | 120.6848 | 1.4211e-13 | -0.067766 | -0.0062244 | 0.068998 | -0.008991 | 0.056668 | -0.020755 | 0.043725 | 0.021601 | 0.0089518 | 0.045773 | -0.0051128 | 7.4547 | 23.5171 | 5.2246 | 121.21 | 121.0809 | 121.0262 | -0.52095 | 0.055992 | 0.059882 | -0.06093 | -0.039111 | 0.091543 | -0.13419 | -0.15499 | 0.046677 | 0.52519 | 8.0223 | 5.7922 | 5.7455 | 0.39605 | 0.34142 | 0.41264 | -120.7239 | 0.62362 | 0.5067 | 0.094061 | -120.5933 | -120.819 | 121.7776 | 121.6485 | 121.5939 | 24.0847 | -121.2058 | 0.52852 | 0.65917 | 0.43344 | 0.62751 | -120.8398
2988.2656 | 121.5637 | -0.54932 | 121.1838 | 1.4211e-13 | -0.06798 | -0.0060108 | 0.069212 | -0.0085636 | 0.056881 | -0.013124 | 0.043725 | 0.021815 | 0.0089518 | 0.045987 | -0.0051128 | 7.6195 | 23.9154 | 5.2795 | 121.2146 | 121.0809 | 121.0262 | -0.53011 | 0.046835 | 0.064461 | -0.065509 | -0.034533 | 0.091543 | -0.11129 | -0.16415 | 0.019208 | 0.030807 | 8.1688 | 5.8288 | 5.8096 | -0.10292 | -0.15755 | 0.38517 | -121.2183 | 0.59615 | 0.48381 | 0.09864 | -121.0922 | -121.2951 | 121.7639 | 121.6302 | 121.5755 | 24.4648 | -121.7139 | 0.51478 | 0.64086 | 0.43802 | 0.61378 | -121.3479
2990.0156 | 121.2387 | -0.54474 | 120.3781 | 1.4211e-13 | -0.067553 | -0.005797 | 0.069212 | -0.0087772 | 0.057095 | -0.0054937 | 0.043725 | 0.021601 | 0.008311 | 0.045987 | -0.004899 | 7.7431 | 24.3 | 5.2978 | 121.2054 | 121.0717 | 121.0217 | -0.54842 | 0.046835 | 0.073618 | -0.056351 | -0.029954 | 0.082386 | -0.12503 | -0.15041 | -0.003684 | 0.82731 | 8.2878 | 5.8426 | 5.8462 | 0.69359 | 0.64354 | 0.39433 | -120.4081 | 0.59157 | 0.48839 | 0.094061 | -120.2957 | -120.5031 | 121.7502 | 121.6164 | 121.5664 | 24.8448 | -120.9265 | 0.51478 | 0.62712 | 0.41971 | 0.61836 | -120.5285
2991.7656 | 120.9595 | -0.59967 | 120.6757 | 1.4211e-13 | -0.067766 | -0.005797 | 0.069426 | -0.008991 | 0.057309 | -0.013124 | 0.043725 | 0.021601 | 0.008311 | 0.045987 | -0.004899 | 7.8942 | 24.5015 | 5.3711 | 121.2192 | 121.0992 | 121.04 | -0.54384 | 0.046835 | 0.064461 | -0.070087 | -0.039111 | 0.086964 | -0.065507 | -0.15499 | 0.055826 | 0.5435 | 8.4939 | 5.9707 | 5.9149 | 0.42352 | 0.36431 | 0.44468 | -120.7148 | 0.6465 | 0.52958 | 0.084904 | -120.5887 | -120.7412 | 121.8188 | 121.6988 | 121.6396 | 25.1012 | -121.2195 | 0.56056 | 0.68663 | 0.53416 | 0.66413 | -120.8306
2993.5156 | 120.9824 | -0.58136 | 121.0236 | 1.4211e-13 | -0.067766 | -0.005797 | 0.069426 | -0.0087772 | 0.057522 | -0.013124 | 0.043939 | 0.021601 | 0.0089518 | 0.045987 | -0.0051128 | 8.0132 | 24.7304 | 5.4306 | 121.2192 | 121.1038 | 121.0445 | -0.54842 | 0.055992 | 0.064461 | -0.065509 | -0.034533 | 0.073228 | -0.11587 | -0.15957 | 0.032937 | 0.1956 | 8.5946 | 6.0119 | 5.979 | 0.080195 | 0.020984 | 0.42179 | -121.0581 | 0.63735 | 0.51585 | 0.094061 | -120.9503 | -121.1394 | 121.8005 | 121.6851 | 121.6259 | 25.3118 | -121.572 | 0.54683 | 0.65459 | 0.46549 | 0.64582 | -121.1831
2995.2188 | 121.637 | -0.58136 | 121.1975 | 1.4211e-13 | -0.067766 | -0.0053696 | 0.069639 | -0.0085636 | 0.05795 | -0.0054937 | 0.043939 | 0.021387 | 0.0085246 | 0.045987 | -0.004899 | 8.1689 | 25.0876 | 5.4809 | 121.2421 | 121.1129 | 121.0629 | -0.54842 | 0.046835 | 0.059882 | -0.065509 | -0.039111 | 0.086964 | -0.12045 | -0.15499 | 0.032937 | 0.044544 | 8.7503 | 6.0623 | 6.0294 | -0.084597 | -0.13465 | 0.42637 | -121.2366 | 0.62819 | 0.51585 | 0.089482 | -121.1105 | -121.318 | 121.8234 | 121.6943 | 121.6442 | 25.6689 | -121.7459 | 0.54225 | 0.66832 | 0.46091 | 0.64124 | -121.3525
2996.9688 | 121.2982 | -0.60425 | 121.0144 | 1.4211e-13 | -0.067553 | -0.0049424 | 0.07028 | -0.0087772 | 0.058591 | -0.013124 | 0.043939 | 0.021601 | 0.0087382 | 0.045987 | -0.0051128 | 8.3291 | 25.3714 | 5.5542 | 121.2512 | 121.1175 | 121.0674 | -0.54842 | 0.046835 | 0.064461 | -0.074666 | -0.034533 | 0.082386 | -0.12503 | -0.15041 | 0.055825 | 0.23681 | 8.9334 | 6.1584 | 6.1026 | 0.10309 | 0.053033 | 0.45384 | -121.0489 | 0.65108 | 0.52958 | 0.075746 | -120.932 | -121.1394 | 121.8555 | 121.7217 | 121.6717 | 25.9757 | -121.5628 | 0.56971 | 0.68663 | 0.47922 | 0.66871 | -121.1648
2998.7344 | 121.3806 | -0.61798 | 121.1151 | 1.4211e-13 | -0.067553 | -0.0047286 | 0.07028 | -0.0087772 | 0.058163 | 0.0021363 | 0.043939 | 0.021387 | 0.008311 | 0.045987 | -0.00554 | 8.4299 | 25.5134 | 5.6 | 121.2421 | 121.1129 | 121.0629 | -0.57132 | 0.046835 | 0.064461 | -0.065509 | -0.039111 | 0.086964 | -0.12961 | -0.15957 | 0.046663 | 0.12694 | 9.0478 | 6.218 | 6.1713 | -0.002199 | -0.052254 | 0.45841 | -121.1542 | 0.66482 | 0.55247 | 0.094061 | -121.0281 | -121.2447 | 121.86 | 121.7309 | 121.6808 | 26.1314 | -121.6864 | 0.57887 | 0.70495 | 0.48837 | 0.68244 | -121.2747
3000.5 | 121.8292 | -0.53101 | 121.225 | 1.4211e-13 | -0.067766 | -0.0049424 | 0.070494 | -0.0085636 | 0.058377 | -0.0054937 | 0.043725 | 0.021601 | 0.0087382 | 0.046414 | -0.004899 | 8.4985 | 25.8201 | 5.7099 | 121.3107 | 121.1816 | 121.1361 | -0.51179 | 0.046835 | 0.073618 | -0.065509 | -0.034533 | 0.091543 | -0.097557 | -0.15499 | 0.019214 | 0.085754 | 9.0295 | 6.2409 | 6.2217 | -0.043379 | -0.08886 | 0.37601 | -121.2595 | 0.57784 | 0.4655 | 0.089482 | -121.1334 | -121.3225 | 121.8417 | 121.7126 | 121.6671 | 26.3512 | -121.7368 | 0.49647 | 0.62255 | 0.43345 | 0.60462 | -121.38
3002.2031 | 121.9162 | -0.5127 | 121.2616 | 1.4211e-13 | -0.067339 | -0.0047286 | 0.070708 | -0.0085636 | 0.058804 | -0.013124 | 0.043939 | 0.021601 | 0.0080974 | 0.045987 | -0.0053264 | 8.6084 | 26.1361 | 5.8197 | 121.3382 | 121.1999 | 121.1544 | -0.4889 | 0.042256 | 0.06904 | -0.06093 | -0.025376 | 0.091543 | -0.097557 | -0.15499 | 0.023798 | 0.076604 | 9.1211 | 6.3324 | 6.3086 | -0.061684 | -0.10717 | 0.3577 | -121.287 | 0.55495 | 0.45177 | 0.094061 | -121.1701 | -121.3592 | 121.8509 | 121.7126 | 121.6671 | 26.6488 | -121.7505 | 0.48732 | 0.60424 | 0.41514 | 0.58174 | -121.4166
3003.9688 | 121.8475 | -0.48065 | 121.2936 | 1.4211e-13 | -0.067553 | -0.0047286 | 0.07028 | -0.00835 | 0.058591 | -0.013124 | 0.043512 | 0.021815 | 0.0085246 | 0.046414 | -0.0053264 | 8.7046 | 26.3238 | 5.9067 | 121.3519 | 121.232 | 121.1819 | -0.4889 | 0.037677 | 0.06904 | -0.070087 | -0.04369 | 0.086964 | -0.12045 | -0.15957 | -0.008245 | 0.058296 | 9.1852 | 6.3874 | 6.3956 | -0.061675 | -0.11174 | 0.32108 | -121.3373 | 0.51833 | 0.41057 | 0.089483 | -121.2067 | -121.4141 | 121.8326 | 121.7126 | 121.6626 | 26.8044 | -121.7825 | 0.43696 | 0.56762 | 0.3602 | 0.54969 | -121.4532
3005.6875 | 121.0922 | -0.54932 | 121.2662 | 1.4211e-13 | -0.067125 | -0.004515 | 0.070921 | -0.0085636 | 0.059018 | -0.020755 | 0.043725 | 0.021601 | 0.0085246 | 0.045987 | -0.0053264 | 8.8328 | 26.3833 | 5.98 | 121.3382 | 121.2091 | 121.1636 | -0.51179 | 0.046835 | 0.064461 | -0.065509 | -0.034533 | 0.086964 | -0.12961 | -0.15957 | 0.037524 | 0.072027 | 9.3821 | 6.5293 | 6.4918 | -0.057103 | -0.10259 | 0.38975 | -121.3007 | 0.59615 | 0.48381 | 0.094061 | -121.1792 | -121.3958 | 121.8875 | 121.7584 | 121.7129 | 26.9326 | -121.778 | 0.51478 | 0.63628 | 0.41971 | 0.61378 | -121.4257
3007.4375 | 121.312 | -0.54474 | 121.1929 | 1.4211e-13 | -0.067553 | -0.004515 | 0.071349 | -0.0085636 | 0.059018 | -0.0054937 | 0.043725 | 0.021815 | 0.0089518 | 0.045987 | -0.0053264 | 8.9381 | 26.4886 | 6.0807 | 121.3611 | 121.232 | 121.1865 | -0.49348 | 0.037677 | 0.059882 | -0.070087 | -0.034533 | 0.096121 | -0.11587 | -0.15499 | 0.051263 | 0.16816 | 9.4828 | 6.6254 | 6.5742 | 0.039033 | -0.006451 | 0.38975 | -121.2275 | 0.58242 | 0.47465 | 0.084904 | -121.0968 | -121.3088 | 121.9058 | 121.7767 | 121.7312 | 27.0334 | -121.6864 | 0.51021 | 0.64086 | 0.42887 | 0.60462 | -121.3479
3009.1875 | 121.9208 | -0.6958 | 121.106 | 1.4211e-13 | -0.067553 | -0.003874 | 0.071135 | -0.00835 | 0.059232 | -0.013124 | 0.043298 | 0.021815 | 0.0085246 | 0.046414 | -0.0053264 | 8.819 | 26.2963 | 5.925 | 121.1459 | 121.0305 | 120.9759 | -0.71327 | 0.046835 | 0.06904 | -0.070087 | -0.029954 | 0.086964 | -0.12503 | -0.15957 | -0.017464 | 0.039951 | 9.5148 | 6.6208 | 6.6383 | -0.075465 | -0.13009 | 0.53623 | -121.1359 | 0.74264 | 0.62571 | 0.089483 | -121.019 | -121.231 | 121.8417 | 121.7263 | 121.6717 | 26.9921 | -121.8192 | 0.66585 | 0.78277 | 0.57077 | 0.76484 | -121.2655
3010.8906 | 121.2982 | -0.7782 | 120.6573 | 1.4211e-13 | -0.066698 | -0.0043014 | 0.07199 | -0.0081362 | 0.059445 | -0.013124 | 0.043939 | 0.021815 | 0.0089518 | 0.0462 | -0.0051128 | 9.0846 | 27.4135 | 6.2043 | 121.2146 | 121.09 | 121.0491 | -0.65832 | 0.037677 | 0.064461 | -0.065509 | -0.039111 | 0.086964 | -0.12503 | -0.15957 | 0.11988 | 0.55724 | 9.8628 | 6.9825 | 6.8626 | 0.43267 | 0.39177 | 0.61863 | -120.6965 | 0.81587 | 0.71269 | 0.094061 | -120.5704 | -120.7824 | 121.9928 | 121.8682 | 121.8273 | 28.1917 | -121.3157 | 0.73909 | 0.86516 | 0.65317 | 0.84266 | -120.8169
3012.6406 | 121.4081 | -1.1032 | 120.0577 | 1.4211e-13 | -0.066057 | -0.0043014 | 0.071776 | -0.0081362 | 0.059873 | 0.0021363 | 0.043725 | 0.021174 | 0.0085246 | 0.046628 | -0.0051128 | 8.9518 | 27.5005 | 6.0029 | 120.8208 | 120.6962 | 120.6554 | -1.0475 | 0.046835 | 0.06904 | -0.070087 | -0.039111 | 0.082386 | -0.079243 | -0.16415 | 0.055684 | 0.76317 | 10.055 | 7.1061 | 7.0504 | 0.63855 | 0.59768 | 0.93906 | -120.0968 | 1.15 | 1.0331 | 0.094062 | -119.9753 | -120.1369 | 121.9241 | 121.7994 | 121.7586 | 28.6037 | -121.1052 | 1.0641 | 1.1856 | 1.024 | 1.1723 | -120.2218
3014.4062 | 121.312 | -1.2039 | 119.9341 | 1.4211e-13 | -0.066271 | -0.0040876 | 0.071562 | -0.007709 | 0.0603 | -0.0054937 | 0.043512 | 0.021601 | 0.0085246 | 0.046414 | -0.0053264 | 9.0388 | 27.8118 | 6.0441 | 120.7155 | 120.5863 | 120.5501 | -1.1666 | 0.037677 | 0.06904 | -0.06093 | -0.039111 | 0.082386 | -0.12503 | -0.15499 | 0.03734 | 0.78146 | 10.2427 | 7.248 | 7.2107 | 0.65225 | 0.61597 | 1.0489 | -119.9732 | 1.2416 | 1.143 | 0.094061 | -119.8517 | -120.0591 | 121.9195 | 121.7903 | 121.754 | 29.0158 | -121.1007 | 1.1648 | 1.2863 | 1.0789 | 1.273 | -120.0891
3016.1719 | 121.907 | -1.1719 | 120.6436 | 1.4211e-13 | -0.06563 | -0.003874 | 0.072204 | -0.0074952 | 0.060514 | -0.013124 | 0.043939 | 0.021601 | 0.008311 | 0.046841 | -0.0053264 | 9.2128 | 28.2056 | 6.2089 | 120.7064 | 120.5772 | 120.5363 | -1.1941 | 0.046835 | 0.06904 | -0.065509 | -0.034533 | 0.082386 | -0.13419 | -0.15957 | -0.022177 | 0.062767 | 10.3846 | 7.3808 | 7.4029 | -0.066437 | -0.1073 | 1.0123 | -120.6781 | 1.2187 | 1.1064 | 0.094061 | -120.5612 | -120.7778 | 121.8783 | 121.7491 | 121.7082 | 29.3775 | -121.8377 | 1.1373 | 1.2543 | 1.0377 | 1.2409 | -120.8032
3017.8594 | 121.9391 | -1.2085 | 120.639 | 1.4211e-13 | -0.06563 | -0.0036602 | 0.07199 | -0.007709 | 0.060727 | -0.0054937 | 0.043512 | 0.021387 | 0.0087382 | 0.0462 | -0.00554 | 9.3455 | 28.6039 | 6.3691 | 120.6926 | 120.5726 | 120.5226 | -1.2032 | 0.046835 | 0.073618 | -0.070087 | -0.034533 | 0.086964 | -0.12503 | -0.15957 | 0.005287 | 0.05361 | 10.554 | 7.5776 | 7.5723 | -0.066438 | -0.11646 | 1.0489 | -120.6736 | 1.2553 | 1.1384 | 0.089483 | -120.5521 | -120.7641 | 121.9011 | 121.7811 | 121.7311 | 29.8124 | -121.8422 | 1.174 | 1.2955 | 1.0835 | 1.2821 | -120.7986
3019.625 | 121.4676 | -1.2405 | 120.6482 | 1.4211e-13 | -0.065416 | -0.003233 | 0.072204 | -0.0072816 | 0.060727 | -0.013124 | 0.043725 | 0.021601 | 0.0085246 | 0.046628 | -0.0053264 | 9.5287 | 29.0069 | 6.5111 | 120.6881 | 120.5634 | 120.5134 | -1.2124 | 0.046835 | 0.073618 | -0.070087 | -0.034533 | 0.086964 | -0.13419 | -0.15499 | 0.028173 | 0.039876 | 10.7692 | 7.7516 | 7.7234 | -0.084751 | -0.13477 | 1.0855 | -120.6827 | 1.2874 | 1.1705 | 0.084904 | -120.5612 | -120.7824 | 121.9286 | 121.804 | 121.754 | 30.2474 | -121.8606 | 1.206 | 1.3275 | 1.1064 | 1.3142 | -120.8032
3021.3281 | 121.9482 | -1.2177 | 120.607 | 1.4211e-13 | -0.065202 | -0.0036602 | 0.072417 | -0.007709 | 0.061368 | -0.0054937 | 0.043939 | 0.021387 | 0.0080974 | 0.0462 | -0.0053264 | 9.6614 | 29.4052 | 6.6805 | 120.6835 | 120.5589 | 120.5134 | -1.2307 | 0.051413 | 0.064461 | -0.074666 | -0.034533 | 0.082386 | -0.11587 | -0.15499 | -0.013032 | 0.076496 | 10.8791 | 7.8981 | 7.9111 | -0.048132 | -0.093569 | 1.0627 | -120.6415 | 1.2691 | 1.143 | 0.080325 | -120.5246 | -120.7229 | 121.9011 | 121.7765 | 121.7311 | 30.6228 | -121.8377 | 1.1831 | 1.3 | 1.1018 | 1.2821 | -120.762
3023.0781 | 121.9757 | -1.236 | 120.6024 | 1.4211e-13 | -0.064775 | -0.0034466 | 0.072417 | -0.007068 | 0.061582 | -0.0054937 | 0.043725 | 0.021601 | 0.0087382 | 0.046628 | -0.0051128 | 9.7667 | 29.7303 | 6.8087 | 120.6743 | 120.5543 | 120.5088 | -1.2398 | 0.037677 | 0.06904 | -0.065509 | -0.04369 | 0.073228 | -0.12503 | -0.15041 | -0.003879 | 0.071917 | 11.0027 | 8.0446 | 8.0485 | -0.048133 | -0.093569 | 1.0856 | -120.6461 | 1.2736 | 1.1705 | 0.084903 | -120.5292 | -120.7274 | 121.9103 | 121.7902 | 121.7448 | 30.9662 | -121.8423 | 1.1923 | 1.3092 | 1.1109 | 1.305 | -120.7528
3024.7812 | 121.4905 | -1.3 | 120.2133 | 1.4211e-13 | -0.064775 | -0.0030192 | 0.073058 | -0.007068 | 0.061368 | -0.020755 | 0.043725 | 0.021815 | 0.0085246 | 0.046628 | -0.0051128 | 9.8446 | 30.1378 | 6.9368 | 120.6606 | 120.536 | 120.4951 | -1.2536 | 0.042256 | 0.06904 | -0.074666 | -0.034533 | 0.077807 | -0.12961 | -0.15957 | 0.046471 | 0.44728 | 11.1446 | 8.2369 | 8.1904 | 0.32265 | 0.28179 | 1.1405 | -120.2479 | 1.3423 | 1.2254 | 0.084904 | -120.1355 | -120.3429 | 121.9606 | 121.836 | 121.7952 | 31.4378 | -121.4669 | 1.2655 | 1.3779 | 1.1704 | 1.3691 | -120.3729
3026.5312 | 121.5317 | -1.3229 | 119.9524 | 1.4211e-13 | -0.064561 | -0.0034466 | 0.073272 | -0.0068542 | 0.061582 | -0.0054937 | 0.043939 | 0.021601 | 0.0080974 | 0.046628 | -0.0051128 | 9.9041 | 30.3987 | 7.0284 | 120.6469 | 120.5314 | 120.4905 | -1.2765 | 0.042256 | 0.073618 | -0.06093 | -0.034533 | 0.082386 | -0.12503 | -0.15041 | 0.046465 | 0.69447 | 11.227 | 8.3513 | 8.3049 | 0.579 | 0.53814 | 1.1725 | -119.9869 | 1.3652 | 1.262 | 0.089482 | -119.87 | -120.0774 | 121.9698 | 121.8543 | 121.8135 | 31.7217 | -121.2289 | 1.2884 | 1.4053 | 1.1979 | 1.3966 | -120.1028
3028.2969 | 121.3577 | -1.3367 | 120.0577 | 1.4211e-13 | -0.06392 | -0.0030192 | 0.073272 | -0.0068542 | 0.061796 | -0.0054937 | 0.043725 | 0.021601 | 0.0085246 | 0.046628 | -0.0051128 | 9.9728 | 30.6139 | 7.1062 | 120.6331 | 120.5177 | 120.4722 | -1.2902 | 0.051413 | 0.06904 | -0.065509 | -0.034533 | 0.091543 | -0.092979 | -0.15041 | 0.046461 | 0.57545 | 11.3094 | 8.4429 | 8.3964 | 0.45998 | 0.41454 | 1.1863 | -120.0922 | 1.3881 | 1.2712 | 0.084903 | -119.9661 | -120.1507 | 121.9698 | 121.8543 | 121.8089 | 31.9506 | -121.3479 | 1.3021 | 1.4282 | 1.2437 | 1.4057 | -120.2081
3030.0781 | 122.0169 | -51.8005 | 69.7861 | 1.4211e-13 | -0.064561 | -0.003874 | 0.072417 | -0.0062134 | 0.064146 | -0.013124 | 0.043939 | 0.021387 | 0.0087382 | 0.046628 | -0.0051128 | -16.971 | 8.1925 | -19.4661 | 93.117 | 92.7511 | 93.2295 | -29.3224 | 0.046835 | 0.06904 | -0.070087 | -0.029954 | 0.082386 | -0.12961 | -0.15499 | 22.4782 | 23.3309 | 34.8295 | 32.3344 | 9.8563 | 22.965 | 23.4435 | 51.6455 | -69.816 | 51.8474 | 51.7304 | 0.084904 | -69.7037 | -69.9157 | 144.9176 | 144.5516 | 145.0301 | 59.9931 | -99.1085 | 51.7706 | 51.8829 | 51.6709 | 51.8696 | -69.9411
3031.7812 | 122.0306 | -0.1831 | 121.6003 | 1.4211e-13 | -0.064134 | -0.0025918 | 0.073699 | -0.007068 | 0.062009 | -0.0054937 | 0.044153 | 0.021387 | 0.0085246 | 0.046414 | -0.0053264 | 11.0258 | 31.6991 | 8.2233 | 121.5076 | 121.3876 | 121.3422 | -0.47974 | 0.051413 | 0.064461 | -0.06093 | -0.034533 | 0.082386 | -0.12503 | -0.15499 | -0.29663 | -0.092741 | 11.2089 | 8.4064 | 8.7031 | -0.21269 | -0.25819 | 0.028114 | -121.6349 | 0.23452 | 0.12217 | 0.094061 | -121.518 | -121.7254 | 121.6907 | 121.5708 | 121.5253 | 31.8822 | -122.0801 | 0.14857 | 0.26549 | 0.058076 | 0.24757 | -121.7553
3033.5469 | 121.9437 | -0.13733 | 121.756 | 1.4211e-13 | -0.063707 | -0.0025918 | 0.073699 | -0.0066406 | 0.062223 | -0.013124 | 0.043725 | 0.021815 | 0.0085246 | 0.046841 | -0.0051128 | 11.3921 | 32.0928 | 8.6171 | 121.851 | 121.7677 | 121.7176 | -0.16837 | 0.037677 | 0.064461 | -0.070087 | -0.034533 | 0.082386 | -0.12045 | -0.15499 | -0.031044 | 0.094999 | 11.5294 | 8.7544 | 8.7854 | 0.011718 | -0.038382 | -0.017662 | -121.7905 | 0.17501 | 0.067242 | 0.084904 | -121.6736 | -121.8764 | 121.9883 | 121.905 | 121.8549 | 32.2302 | -121.9244 | 0.1028 | 0.21971 | 0.016879 | 0.20179 | -121.911
3035.25 | 121.9528 | -0.15106 | 121.7834 | 1.4211e-13 | -0.063493 | -0.0021646 | 0.073913 | -0.0066406 | 0.062009 | -0.013124 | 0.043725 | 0.021815 | 0.008311 | 0.046414 | -0.0057538 | 11.4699 | 32.0654 | 8.6812 | 121.851 | 121.7998 | 121.7496 | -0.16379 | 0.046835 | 0.06904 | -0.06093 | -0.034533 | 0.082386 | -0.13419 | -0.15499 | -0.012732 | 0.067533 | 11.621 | 8.8322 | 8.845 | 0.016305 | -0.033798 | -0.003929 | -121.818 | 0.1979 | 0.090132 | 0.094061 | -121.7011 | -121.9176 | 122.002 | 121.9508 | 121.9007 | 32.2164 | -121.9472 | 0.11653 | 0.23345 | 0.016876 | 0.2201 | -121.9384
3037 | 121.9254 | -0.12817 | 121.8109 | 1.4211e-13 | -0.063279 | -0.0021646 | 0.073699 | -0.0068542 | 0.06265 | -0.0054937 | 0.043725 | 0.021815 | 0.0085246 | 0.046628 | -0.0051128 | 11.5889 | 31.9875 | 8.7453 | 121.8693 | 121.754 | 121.713 | -0.10885 | 0.046835 | 0.06904 | -0.065509 | -0.039111 | 0.082386 | -0.13419 | -0.15041 | 0.019327 | 0.05838 | 11.7171 | 8.8734 | 8.8541 | -0.05695 | -0.097893 | -0.022238 | -121.85 | 0.17501 | 0.062665 | 0.084903 | -121.7285 | -121.9451 | 121.9975 | 121.8821 | 121.8412 | 32.1157 | -121.9198 | 0.089063 | 0.21056 | -0.006012 | 0.19721 | -121.9613
3038.75 | 121.9757 | -0.13733 | 121.8201 | 1.4211e-13 | -0.063279 | -0.0023782 | 0.073913 | -0.006427 | 0.062437 | -0.013124 | 0.043512 | 0.021387 | 0.0089518 | 0.046628 | -0.0053264 | 11.7355 | 31.9463 | 8.7727 | 121.8785 | 121.7585 | 121.7268 | -0.10885 | 0.051413 | 0.073618 | -0.074666 | -0.034533 | 0.091543 | -0.10214 | -0.15499 | 0.028482 | 0.058382 | 11.8728 | 8.9101 | 8.8816 | -0.061527 | -0.093312 | -0.017662 | -121.8546 | 0.18874 | 0.062663 | 0.080325 | -121.7285 | -121.9222 | 122.0158 | 121.8959 | 121.8641 | 32.0836 | -121.9289 | 0.1028 | 0.22887 | 0.035193 | 0.21095 | -121.9751
3040.5156 | 122.0261 | -0.09613 | 121.8384 | 1.4211e-13 | -0.063066 | -0.0021646 | 0.073913 | -0.0066406 | 0.06265 | -0.0054937 | 0.043512 | 0.021815 | 0.0087382 | 0.046628 | -0.00554 | 11.8728 | 31.8914 | 8.8094 | 121.8876 | 121.7723 | 121.7359 | -0.11342 | 0.060571 | 0.073618 | -0.065509 | -0.029954 | 0.086964 | -0.0884 | -0.15041 | -0.017295 | 0.049228 | 11.9689 | 8.9055 | 8.9228 | -0.066101 | -0.10247 | -0.054282 | -121.8683 | 0.1567 | 0.030621 | 0.084903 | -121.7514 | -121.9268 | 121.9837 | 121.8684 | 121.832 | 31.9875 | -121.9518 | 0.066176 | 0.18309 | 0.00773 | 0.16975 | -121.9888
3042.2656 | 122.0673 | -0.09613 | 121.8246 | 1.4211e-13 | -0.062638 | -0.0015234 | 0.074127 | -0.0066406 | 0.062864 | -0.013124 | 0.043512 | 0.021387 | 0.0085246 | 0.047055 | -0.0053264 | 11.969 | 31.8044 | 8.8231 | 121.9013 | 121.7769 | 121.7496 | -0.10885 | 0.051413 | 0.06904 | -0.06093 | -0.034533 | 0.082386 | -0.12503 | -0.15499 | -0.012717 | 0.076696 | 12.0651 | 8.9192 | 8.9319 | -0.047789 | -0.074997 | -0.058861 | -121.8592 | 0.14754 | 0.0352 | 0.094061 | -121.7423 | -121.9497 | 121.9975 | 121.873 | 121.8458 | 31.9005 | -121.9335 | 0.061597 | 0.17852 | -0.028899 | 0.16517 | -121.9796
3044.0156 | 122.0306 | -0.11444 | 121.843 | 1.4211e-13 | -0.062425 | -0.0015234 | 0.073913 | -0.0068542 | 0.062864 | -0.013124 | 0.043939 | 0.021601 | 0.0087382 | 0.046628 | -0.00554 | 12.0239 | 31.6762 | 8.8368 | 121.9151 | 121.7952 | 121.7588 | -0.10885 | 0.051413 | 0.064461 | -0.06093 | -0.029954 | 0.086964 | -0.12961 | -0.15499 | 0.005594 | 0.07212 | 12.1383 | 8.9513 | 8.9457 | -0.047784 | -0.084151 | -0.04055 | -121.8729 | 0.16585 | 0.053511 | 0.094061 | -121.756 | -121.9726 | 122.0295 | 121.9096 | 121.8732 | 31.7906 | -121.9518 | 0.084487 | 0.20141 | -0.015166 | 0.1789 | -121.9979
3045.7188 | 121.9208 | -0.16479 | 121.8567 | 1.4211e-13 | -0.063066 | -0.0013098 | 0.073913 | -0.006427 | 0.063291 | -0.0054937 | 0.043939 | 0.021174 | 0.0078836 | 0.046841 | -0.0053264 | 12.1429 | 31.5571 | 8.759 | 121.9105 | 121.7952 | 121.7588 | -0.11342 | 0.046835 | 0.064461 | -0.070087 | -0.034533 | 0.091543 | -0.097557 | -0.15957 | 0.05137 | 0.05381 | 12.3077 | 8.9238 | 8.8724 | -0.061516 | -0.097883 | 0.005225 | -121.8912 | 0.21163 | 0.094708 | 0.089483 | -121.7651 | -121.9542 | 122.0753 | 121.96 | 121.9236 | 31.7219 | -121.9701 | 0.13026 | 0.25634 | 0.067238 | 0.22926 | -122.0163
3047.4688 | 121.9574 | -0.14191 | 121.8338 | 1.4211e-13 | -0.062425 | -0.0015234 | 0.074127 | -0.0066406 | 0.063505 | -0.020755 | 0.043512 | 0.021387 | 0.008311 | 0.046628 | -0.0051128 | 12.2253 | 31.4839 | 8.7773 | 121.9197 | 121.8043 | 121.768 | -0.10885 | 0.046835 | 0.064461 | -0.06093 | -0.039111 | 0.086964 | -0.12045 | -0.15499 | 0.03306 | 0.085855 | 12.3673 | 8.9192 | 8.8862 | -0.02947 | -0.065838 | -0.013084 | -121.8729 | 0.18874 | 0.080977 | 0.094061 | -121.7468 | -121.9543 | 122.0616 | 121.9462 | 121.9099 | 31.6258 | -121.9426 | 0.1028 | 0.22887 | 0.021457 | 0.20637 | -121.9888
3049.1562 | 121.2982 | -0.12817 | 121.2662 | 1.4211e-13 | -0.062211 | -0.0010962 | 0.07434 | -0.006427 | 0.063505 | -0.028385 | 0.043725 | 0.021815 | 0.0085246 | 0.046841 | -0.00554 | 12.3215 | 31.2504 | 8.7819 | 121.9288 | 121.8135 | 121.7863 | -0.11342 | 0.046835 | 0.06904 | -0.070087 | -0.029954 | 0.082386 | -0.11587 | -0.15957 | 0.014749 | 0.66264 | 12.4497 | 8.9101 | 8.8953 | 0.54731 | 0.5201 | -0.031396 | -121.2961 | 0.17501 | 0.058087 | 0.089483 | -121.1838 | -121.382 | 122.057 | 121.9417 | 121.9145 | 31.3785 | -121.3796 | 0.09822 | 0.21056 | 0.012302 | 0.19721 | -121.4257
3050.9219 | 122.0718 | -0.082397 | 121.7331 | 1.4211e-13 | -0.062211 | -0.0010962 | 0.07434 | -0.0062134 | 0.063291 | -0.013124 | 0.043512 | 0.021601 | 0.0085246 | 0.047055 | -0.00554 | 12.381 | 31.1359 | 8.7865 | 121.9334 | 121.8135 | 121.7863 | -0.10885 | 0.055992 | 0.059882 | -0.065509 | -0.034533 | 0.086964 | -0.11587 | -0.15957 | -0.02645 | 0.2003 | 12.4634 | 8.8689 | 8.8953 | 0.080396 | 0.053185 | -0.077173 | -121.7676 | 0.13839 | 0.016888 | 0.094061 | -121.6461 | -121.849 | 122.0158 | 121.8959 | 121.8687 | 31.2183 | -121.8419 | 0.047864 | 0.16936 | -0.033475 | 0.14228 | -121.8927
3052.6719 | 121.4996 | -0.15106 | 121.344 | 1.4211e-13 | -0.061784 | -0.0010962 | 0.07434 | -0.0068542 | 0.063291 | -0.0054937 | 0.043725 | 0.021601 | 0.008311 | 0.046628 | -0.00554 | 12.4314 | 31.0214 | 8.7132 | 121.9517 | 121.8226 | 121.7909 | -0.10885 | 0.046835 | 0.064461 | -0.070087 | -0.034533 | 0.086964 | -0.12503 | -0.15499 | 0.042215 | 0.60771 | 12.5824 | 8.8643 | 8.8221 | 0.47865 | 0.44686 | -0.003929 | -121.3785 | 0.1979 | 0.080975 | 0.084904 | -121.257 | -121.469 | 122.1028 | 121.9737 | 121.9419 | 31.1725 | -121.4528 | 0.11653 | 0.23803 | 0.026033 | 0.21552 | -121.499
3054.3594 | 121.431 | -0.15564 | 121.3257 | 1.4211e-13 | -0.061997 | -0.0010962 | 0.07434 | -0.0066406 | 0.063505 | -0.020755 | 0.043512 | 0.021387 | 0.008311 | 0.047055 | -0.0053264 | 12.4772 | 30.8429 | 8.6857 | 121.9471 | 121.8364 | 121.8 | -0.10885 | 0.051413 | 0.064461 | -0.074666 | -0.034533 | 0.091543 | -0.12503 | -0.15499 | 0.046793 | 0.62144 | 12.6328 | 8.8414 | 8.7946 | 0.5107 | 0.47433 | 0.000649 | -121.3602 | 0.20705 | 0.080974 | 0.080325 | -121.2341 | -121.4507 | 122.1028 | 121.992 | 121.9557 | 30.9985 | -121.4345 | 0.12111 | 0.24718 | 0.030611 | 0.2201 | -121.4807
3056.125 | 122.0764 | -0.091553 | 121.9162 | 1.4211e-13 | -0.061784 | -0.0010962 | 0.074768 | -0.0068542 | 0.063505 | -0.020755 | 0.043725 | 0.021174 | 0.0085246 | 0.046841 | -0.00554 | 12.5229 | 30.5224 | 8.6262 | 121.9609 | 121.8364 | 121.8092 | -0.10885 | 0.055992 | 0.073618 | -0.074666 | -0.034533 | 0.096121 | -0.12961 | -0.15957 | -0.017294 | 0.044662 | 12.6145 | 8.7178 | 8.7351 | -0.079816 | -0.10703 | -0.068017 | -121.9507 | 0.14754 | 0.016887 | 0.084904 | -121.8201 | -122.0458 | 122.0524 | 121.9279 | 121.9007 | 30.6139 | -122.025 | 0.05702 | 0.18767 | -0.038054 | 0.16517 | -122.0758
3057.8281 | 121.6644 | -0.13733 | 121.9437 | 1.4211e-13 | -0.061997 | -0.00066884 | 0.074554 | -0.0068542 | 0.063078 | -0.013124 | 0.043725 | 0.021174 | 0.0087382 | 0.046841 | -0.0053264 | 12.5687 | 30.1103 | 8.553 | 121.9563 | 121.8455 | 121.8275 | -0.10427 | 0.046835 | 0.064461 | -0.06093 | -0.034533 | 0.086964 | -0.12961 | -0.15499 | 0.033061 | 0.012618 | 12.7061 | 8.6903 | 8.6572 | -0.098124 | -0.11618 | -0.017662 | -121.9782 | 0.18416 | 0.076399 | 0.094061 | -121.8567 | -122.0733 | 122.0936 | 121.9829 | 121.9648 | 30.2476 | -122.0479 | 0.1028 | 0.22429 | 0.007722 | 0.20179 | -122.0987
3059.5781 | 122.0718 | -0.10071 | 121.8979 | 1.4211e-13 | -0.061784 | -0.00088244 | 0.07434 | -0.0066406 | 0.063719 | -0.013124 | 0.043512 | 0.021601 | 0.008311 | 0.047055 | -0.0051128 | 12.6328 | 29.9134 | 8.498 | 121.9792 | 121.8455 | 121.8275 | -0.10885 | 0.051413 | 0.06904 | -0.065509 | -0.039111 | 0.086964 | -0.12503 | -0.15957 | -0.008139 | 0.081287 | 12.7335 | 8.5987 | 8.6069 | -0.052347 | -0.070403 | -0.058862 | -121.937 | 0.15212 | 0.035199 | 0.094061 | -121.8109 | -122.0229 | 122.0799 | 121.9462 | 121.9282 | 30.0141 | -122.0067 | 0.061597 | 0.18767 | -0.024321 | 0.16975 | -122.0575
3061.3438 | 122.0718 | -0.086975 | 121.9208 | 1.4211e-13 | -0.061356 | -0.00066884 | 0.074554 | -0.0066406 | 0.063291 | -0.013124 | 0.043725 | 0.021387 | 0.0080974 | 0.046841 | -0.00554 | 12.642 | 29.6158 | 8.466 | 121.9746 | 121.8501 | 121.8321 | -0.11342 | 0.055992 | 0.064461 | -0.070087 | -0.034533 | 0.086964 | -0.10671 | -0.15499 | -0.02645 | 0.05382 | 12.729 | 8.553 | 8.5794 | -0.070656 | -0.088712 | -0.068016 | -121.9553 | 0.14297 | 0.016888 | 0.084904 | -121.8338 | -122.0275 | 122.0616 | 121.9371 | 121.919 | 29.7028 | -122.0342 | 0.052442 | 0.17394 | -0.019739 | 0.15144 | -122.0758
3063.1094 | 122.1085 | -0.10071 | 121.8475 | 1.4211e-13 | -0.061784 | -0.00045504 | 0.074981 | -0.0072816 | 0.063291 | -0.013124 | 0.043512 | 0.021387 | 0.0080974 | 0.047055 | -0.0051128 | 12.6649 | 29.2861 | 8.4065 | 121.9746 | 121.8593 | 121.8412 | -0.10885 | 0.055992 | 0.06904 | -0.070087 | -0.034533 | 0.1007 | -0.12503 | -0.15957 | -0.008139 | 0.12706 | 12.7656 | 8.5072 | 8.5153 | 0.011744 | -0.006313 | -0.058862 | -121.8821 | 0.1567 | 0.030621 | 0.089483 | -121.7468 | -121.9726 | 122.0753 | 121.96 | 121.9419 | 29.3869 | -121.9564 | 0.066175 | 0.20141 | -0.024321 | 0.16975 | -122.0071
3064.8125 | 122.1359 | -0.082397 | 121.9391 | 1.4211e-13 | -0.061143 | -0.00045504 | 0.074981 | -0.0068542 | 0.063505 | -0.0054937 | 0.043725 | 0.021387 | 0.008311 | 0.046841 | -0.00554 | 12.6374 | 28.9107 | 8.3332 | 121.9838 | 121.8593 | 121.8458 | -0.10885 | 0.046835 | 0.06904 | -0.065509 | -0.034533 | 0.091543 | -0.12503 | -0.15499 | -0.02645 | 0.044666 | 12.7198 | 8.4156 | 8.4421 | -0.079809 | -0.093287 | -0.072594 | -121.9736 | 0.12923 | 0.016888 | 0.089482 | -121.8475 | -122.0641 | 122.0661 | 121.9417 | 121.9282 | 28.9931 | -122.0479 | 0.047864 | 0.17394 | -0.042632 | 0.15144 | -122.0941
3066.5781 | 121.4996 | -0.15564 | 121.3348 | 1.4211e-13 | -0.06157 | 0.00018596 | 0.075409 | -0.0072816 | 0.063078 | -0.0054937 | 0.043512 | 0.02096 | 0.0080974 | 0.047055 | -0.0053264 | 12.6832 | 28.7459 | 8.3286 | 121.9975 | 121.8822 | 121.855 | -0.090531 | 0.046835 | 0.064461 | -0.065509 | -0.034533 | 0.091543 | -0.11587 | -0.15957 | 0.065109 | 0.66265 | 12.8388 | 8.4843 | 8.4192 | 0.54733 | 0.52012 | -0.00393 | -121.3694 | 0.20248 | 0.090131 | 0.094061 | -121.2433 | -121.4507 | 122.1531 | 122.0378 | 122.0106 | 28.9015 | -121.4254 | 0.12111 | 0.24718 | 0.039768 | 0.2201 | -121.4944
3068.2812 | 122.1222 | -0.10986 | 121.9391 | 1.4211e-13 | -0.061356 | 0.00061316 | 0.075836 | -0.0068542 | 0.063291 | -0.0054937 | 0.043512 | 0.021174 | 0.0080974 | 0.046841 | -0.0057538 | 12.7015 | 28.3613 | 8.2829 | 121.9975 | 121.8776 | 121.855 | -0.09511 | 0.046835 | 0.064461 | -0.065509 | -0.029954 | 0.091543 | -0.11587 | -0.15041 | 0.014753 | 0.058401 | 12.8114 | 8.3927 | 8.378 | -0.061493 | -0.08413 | -0.040549 | -121.969 | 0.1567 | 0.044354 | 0.084903 | -121.8475 | -122.055 | 122.1074 | 121.9875 | 121.9648 | 28.4711 | -122.0342 | 0.079909 | 0.20141 | -0.006009 | 0.17432 | -122.0895
3070.0312 | 122.113 | -0.086975 | 121.9803 | 1.4211e-13 | -0.06157 | 0.00039956 | 0.075409 | -0.007068 | 0.063078 | -0.020755 | 0.043512 | 0.021174 | 0.008311 | 0.046841 | -0.00554 | 12.7015 | 28.082 | 8.2279 | 122.0021 | 121.8913 | 121.8687 | -0.085952 | 0.046835 | 0.064461 | -0.065509 | -0.034533 | 0.086964 | -0.10671 | -0.16415 | 0.001023 | 0.021781 | 12.7885 | 8.3149 | 8.3139 | -0.088956 | -0.11159 | -0.077174 | -122.0148 | 0.13381 | 0.021466 | 0.09864 | -121.8933 | -122.087 | 122.089 | 121.9783 | 121.9557 | 28.169 | -122.0662 | 0.052442 | 0.17394 | -0.019739 | 0.15144 | -122.1444
3071.7969 | 121.5958 | -0.12817 | 121.6003 | 1.4211e-13 | -0.06157 | 0.00082696 | 0.07605 | -0.007068 | 0.063291 | -0.013124 | 0.043512 | 0.021601 | 0.0085246 | 0.047269 | -0.0057538 | 12.6649 | 27.7065 | 8.1684 | 122.0066 | 121.8959 | 121.8733 | -0.099689 | 0.046835 | 0.06904 | -0.070087 | -0.034533 | 0.091543 | -0.12503 | -0.15499 | 0.028485 | 0.4063 | 12.793 | 8.2966 | 8.2681 | 0.29557 | 0.27293 | -0.026817 | -121.6349 | 0.17501 | 0.058087 | 0.084904 | -121.5088 | -121.7254 | 122.1348 | 122.0241 | 122.0014 | 27.8347 | -121.7 | 0.093641 | 0.21972 | 0.003145 | 0.19721 | -121.7553
3073.5625 | 122.1176 | -0.10529 | 121.9574 | 1.4211e-13 | -0.061356 | 0.0016816 | 0.076477 | -0.0072816 | 0.063291 | -0.020755 | 0.043298 | 0.021174 | 0.0085246 | 0.046841 | -0.00554 | 12.6053 | 27.3586 | 8.1272 | 122.0204 | 121.9005 | 121.8824 | -0.085952 | 0.051413 | 0.06904 | -0.070087 | -0.025376 | 0.086964 | -0.12045 | -0.15957 | 0.019334 | 0.062983 | 12.7106 | 8.2325 | 8.2131 | -0.056909 | -0.074969 | -0.054284 | -121.9828 | 0.1567 | 0.035199 | 0.089483 | -121.8704 | -122.0778 | 122.1257 | 122.0058 | 121.9877 | 27.4638 | -122.0433 | 0.07991 | 0.19225 | -0.015164 | 0.17433 | -122.117
3075.2656 | 122.1222 | -0.068665 | 121.8292 | 1.4211e-13 | -0.074177 | 0.012793 | -0.012415 | -0.013692 | -0.024524 | -0.0054937 | 0.043512 | 0.021387 | 0.0080974 | 0.047482 | -0.0053264 | -0.081363 | -0.026065 | -0.12287 | 0.27647 | 0.29799 | 0.44873 | -0.099689 | 0.046835 | 0.06904 | -0.065509 | -0.034533 | 0.086964 | -0.12503 | -0.15499 | -0.031024 | -121.5528 | -0.012698 | -0.054201 | -0.023177 | -121.5312 | -121.3805 | -0.086326 | -121.8638 | 0.1155 | 0.003156 | 0.089482 | -121.7423 | -121.9543 | 0.34513 | 0.36665 | 0.5174 | 0.0426 | -121.9289 | 0.034132 | 0.15563 | -0.056364 | 0.13771 | -121.9842
3077.0312 | 122.0901 | -0.12817 | 121.7514 | 1.4211e-13 | -0.073749 | 0.0044596 | -0.013056 | -0.013264 | -0.024311 | -0.0054937 | 0.043084 | 0.021601 | 0.008311 | 0.046841 | -0.00554 | -0.053893 | -0.035222 | -0.08624 | 0.16659 | 0.19267 | 0.32511 | -0.099689 | 0.046835 | 0.06904 | -0.070087 | -0.04369 | 0.091543 | -0.12503 | -0.15957 | 0.028485 | -121.5848 | 0.074281 | 0.041934 | 0.013449 | -121.5587 | -121.4263 | -0.031396 | -121.7951 | 0.17501 | 0.058087 | 0.089483 | -121.6599 | -121.8764 | 0.29476 | 0.32085 | 0.45328 | 0.092952 | -121.8511 | 0.084484 | 0.21972 | 0.003145 | 0.19721 | -121.911
3078.7969 | 122.0398 | -0.12817 | 121.9711 | 1.4211e-13 | -0.073536 | 0.0040322 | -0.012629 | -0.013478 | -0.023883 | -0.013124 | 0.043298 | 0.021601 | 0.008311 | 0.047055 | -0.0059674 | -0.049315 | -0.044379 | -0.077084 | 0.15743 | 0.17894 | 0.32053 | -0.10427 | 0.046835 | 0.059882 | -0.065509 | -0.034533 | 0.082386 | -0.12961 | -0.15499 | 0.023906 | -121.8137 | 0.078859 | 0.05109 | 0.027184 | -121.7922 | -121.6506 | -0.026817 | -122.0057 | 0.17501 | 0.062665 | 0.089482 | -121.8887 | -122.1007 | 0.2856 | 0.30711 | 0.44871 | 0.083795 | -122.0754 | 0.093641 | 0.21056 | -0.001433 | 0.18806 | -122.1261
3080.5 | 122.1634 | -0.086975 | 121.9711 | 1.4211e-13 | -0.073963 | 0.0042458 | -0.012629 | -0.013692 | -0.024097 | 0.0021363 | 0.043298 | 0.021601 | 0.0080974 | 0.047269 | -0.0057538 | -0.040158 | -0.039801 | -0.077084 | 0.12538 | 0.17894 | 0.31595 | -0.099689 | 0.046835 | 0.064461 | -0.06093 | -0.034533 | 0.086964 | -0.12503 | -0.15957 | -0.012714 | -121.8457 | 0.046817 | 0.009891 | 0.022605 | -121.7922 | -121.6552 | -0.072595 | -122.0057 | 0.13381 | 0.026045 | 0.09864 | -121.8842 | -122.0962 | 0.21236 | 0.26591 | 0.40293 | 0.047174 | -122.0708 | 0.052442 | 0.17394 | -0.038054 | 0.15144 | -122.1307
3082.2031 | 122.1771 | -0.07782 | 121.9711 | 1.4211e-13 | -0.073749 | 0.0040322 | -0.012629 | -0.013692 | -0.024311 | -0.020755 | 0.043298 | 0.021601 | 0.008311 | 0.047055 | -0.0057538 | -0.044736 | -0.035222 | -0.072505 | 0.11622 | 0.16978 | 0.30222 | -0.099689 | 0.046835 | 0.064461 | -0.065509 | -0.034533 | 0.091543 | -0.12503 | -0.15499 | -0.021869 | -121.8549 | 0.033084 | 0.005315 | 0.027184 | -121.8014 | -121.6689 | -0.077171 | -122.0057 | 0.12466 | 0.012311 | 0.089482 | -121.8796 | -122.0962 | 0.19404 | 0.2476 | 0.38004 | 0.042598 | -122.0708 | 0.043287 | 0.16936 | -0.047209 | 0.14228 | -122.1261
3083.9688 | 122.0581 | -0.1236 | 122.0352 | 1.4211e-13 | -0.073536 | 0.0036048 | -0.012842 | -0.013478 | -0.024311 | -0.013124 | 0.043084 | 0.021387 | 0.0085246 | 0.047055 | -0.0057538 | -0.03558 | -0.039801 | -0.067927 | 0.11165 | 0.1652 | 0.3068 | -0.099689 | 0.046835 | 0.064461 | -0.065509 | -0.029954 | 0.082386 | -0.10214 | -0.15499 | 0.023907 | -121.9236 | 0.088016 | 0.055669 | 0.031762 | -121.87 | -121.7284 | -0.031395 | -122.0652 | 0.17043 | 0.058087 | 0.089482 | -121.9528 | -122.1374 | 0.23524 | 0.2888 | 0.43039 | 0.083795 | -122.1349 | 0.093642 | 0.20598 | 0.02146 | 0.18806 | -122.1902
3085.6719 | 122.0627 | -0.13275 | 122.0444 | 1.4211e-13 | -0.073749 | 0.0040322 | -0.012842 | -0.013692 | -0.024097 | -0.013124 | 0.043298 | 0.02096 | 0.0080974 | 0.047055 | -0.0057538 | -0.03558 | -0.035222 | -0.072505 | 0.11165 | 0.1652 | 0.3068 | -0.09511 | 0.051413 | 0.064461 | -0.065509 | -0.029954 | 0.091543 | -0.092979 | -0.15499 | 0.037641 | -121.9327 | 0.097171 | 0.060246 | 0.022605 | -121.8792 | -121.7376 | -0.02224 | -122.0743 | 0.18416 | 0.067242 | 0.089482 | -121.9528 | -122.1374 | 0.2444 | 0.29795 | 0.43955 | 0.097529 | -122.1395 | 0.1028 | 0.22429 | 0.039772 | 0.19721 | -122.1994
3087.4375 | 122.1405 | -0.10071 | 122.0444 | 1.4211e-13 | -0.073963 | 0.0040322 | -0.013056 | -0.013478 | -0.023883 | -0.0054937 | 0.043725 | 0.021387 | 0.0085246 | 0.047055 | -0.0057538 | -0.03558 | -0.039801 | -0.072505 | 0.11165 | 0.16062 | 0.28848 | -0.090531 | 0.046835 | 0.064461 | -0.065509 | -0.034533 | 0.086964 | -0.12503 | -0.15499 | 0.010177 | -121.9327 | 0.065128 | 0.028203 | 0.018026 | -121.8838 | -121.7559 | -0.054283 | -122.0789 | 0.14754 | 0.035199 | 0.089482 | -121.9574 | -122.1694 | 0.21236 | 0.26133 | 0.38919 | 0.060907 | -122.1349 | 0.066175 | 0.18767 | -0.024321 | 0.16517 | -122.1994
3089.1875 | 122.0993 | -0.11902 | 121.9162 | 1.4211e-13 | -0.073963 | 0.0038184 | -0.012629 | -0.013905 | -0.024097 | -0.020755 | 0.043084 | 0.021387 | 0.008311 | 0.047482 | -0.00554 | -0.031001 | -0.039801 | -0.072505 | 0.10707 | 0.16062 | 0.28848 | -0.090531 | 0.051413 | 0.064461 | -0.06093 | -0.029954 | 0.091543 | -0.12045 | -0.15957 | 0.028488 | -121.8091 | 0.088018 | 0.046514 | 0.018026 | -121.7556 | -121.6277 | -0.040551 | -121.9462 | 0.17043 | 0.058089 | 0.09864 | -121.8247 | -122.0366 | 0.22609 | 0.27964 | 0.4075 | 0.079218 | -122.0067 | 0.089065 | 0.21056 | -0.001431 | 0.18348 | -122.0758
3090.8906 | 122.0764 | -0.1236 | 122.0398 | 1.4211e-13 | -0.073536 | 0.0036048 | -0.012629 | -0.013692 | -0.024097 | -0.013124 | 0.043512 | 0.021601 | 0.008311 | 0.047269 | -0.0057538 | -0.031001 | -0.044379 | -0.072505 | 0.11165 | 0.16062 | 0.29306 | -0.090531 | 0.051413 | 0.06904 | -0.065509 | -0.029954 | 0.086964 | -0.12045 | -0.15957 | 0.033065 | -121.9281 | 0.092595 | 0.051091 | 0.018026 | -121.8792 | -121.7467 | -0.035974 | -122.0697 | 0.17501 | 0.058087 | 0.094061 | -121.9528 | -122.1602 | 0.23524 | 0.28422 | 0.41666 | 0.079217 | -122.1303 | 0.093642 | 0.21056 | 0.003146 | 0.19264 | -122.1994
3092.6406 | 122.1909 | -0.07782 | 122.0215 | 1.4211e-13 | -0.074177 | 0.0038184 | -0.012842 | -0.013905 | -0.023883 | -0.020755 | 0.043298 | 0.021387 | 0.008311 | 0.047269 | -0.00554 | -0.031001 | -0.048958 | -0.067927 | 0.10707 | 0.15604 | 0.29306 | -0.09511 | 0.051413 | 0.064461 | -0.056351 | -0.029954 | 0.086964 | -0.0884 | -0.16873 | -0.01729 | -121.9144 | 0.046819 | 0.009893 | 0.027183 | -121.8654 | -121.7284 | -0.090908 | -122.0514 | 0.12923 | 0.021469 | 0.11238 | -121.9345 | -122.1099 | 0.18489 | 0.23386 | 0.37088 | 0.028862 | -122.1166 | 0.047866 | 0.16478 | -0.01058 | 0.14228 | -122.1902
3094.3438 | 122.2229 | -0.086975 | 122.0032 | 1.4211e-13 | -0.073963 | 0.0038184 | -0.013056 | -0.013692 | -0.024311 | -0.020755 | 0.043084 | 0.021601 | 0.0078836 | 0.047269 | -0.0059674 | -0.026423 | -0.048958 | -0.067927 | 0.10249 | 0.15146 | 0.28848 | -0.090531 | 0.046835 | 0.064461 | -0.065509 | -0.039111 | 0.086964 | -0.11129 | -0.15957 | -0.003556 | -121.9007 | 0.060552 | 0.019048 | 0.022604 | -121.8517 | -121.7147 | -0.072595 | -122.0423 | 0.13381 | 0.021466 | 0.094061 | -121.9162 | -122.1145 | 0.18946 | 0.23844 | 0.37546 | 0.038017 | -122.0937 | 0.047864 | 0.17394 | -0.024318 | 0.15144 | -122.1627
3096.1094 | 122.0947 | -0.1236 | 122.0764 | 1.4211e-13 | -0.073963 | 0.0044596 | -0.012842 | -0.013905 | -0.023883 | 0.0021363 | 0.043512 | 0.021387 | 0.008311 | 0.047269 | -0.006181 | -0.031001 | -0.048958 | -0.072505 | 0.10707 | 0.15604 | 0.28848 | -0.090531 | 0.046835 | 0.064461 | -0.06093 | -0.04369 | 0.086964 | -0.12503 | -0.15041 | 0.033065 | -121.9693 | 0.092595 | 0.051091 | 0.018026 | -121.9204 | -121.7879 | -0.026816 | -122.1201 | 0.17043 | 0.062666 | 0.089482 | -121.9895 | -122.2014 | 0.23066 | 0.27964 | 0.41208 | 0.074638 | -122.1669 | 0.079906 | 0.21056 | -0.001433 | 0.18806 | -122.2268
3097.875 | 122.2229 | -0.082397 | 121.9849 | 1.4211e-13 | -0.074177 | 0.0038184 | -0.012629 | -0.013692 | -0.024097 | -0.020755 | 0.043298 | 0.021387 | 0.008311 | 0.047482 | -0.0059674 | -0.03558 | -0.053537 | -0.067927 | 0.10249 | 0.15604 | 0.2839 | -0.099689 | 0.037677 | 0.064461 | -0.056351 | -0.034533 | 0.082386 | -0.11129 | -0.16415 | -0.017292 | -121.8824 | 0.046817 | 0.01447 | 0.031762 | -121.8288 | -121.701 | -0.081752 | -122.0194 | 0.12007 | 0.026046 | 0.1078 | -121.9025 | -122.0962 | 0.18489 | 0.23844 | 0.3663 | 0.02886 | -122.0846 | 0.047864 | 0.16478 | -0.028896 | 0.14686 | -122.149
3099.5781 | 122.0535 | -0.1236 | 121.9299 | 1.4211e-13 | -0.074177 | 0.0038184 | -0.013056 | -0.014119 | -0.024311 | -0.0054937 | 0.043512 | 0.021601 | 0.008311 | 0.047482 | -0.0053264 | -0.031001 | -0.053537 | -0.063349 | 0.097912 | 0.15146 | 0.27932 | -0.081373 | 0.051413 | 0.064461 | -0.065509 | -0.039111 | 0.091543 | -0.13419 | -0.15957 | 0.042223 | -121.832 | 0.092595 | 0.060247 | 0.018024 | -121.7785 | -121.6506 | -0.035974 | -121.969 | 0.17501 | 0.058087 | 0.094061 | -121.8384 | -122.0641 | 0.22151 | 0.27506 | 0.40292 | 0.070059 | -122.0113 | 0.084485 | 0.21514 | -0.01059 | 0.18806 | -122.0895
3101.3281 | 122.168 | -0.091553 | 122.0398 | 1.4211e-13 | -0.07439 | 0.0040322 | -0.012842 | -0.013692 | -0.024097 | -0.013124 | 0.043298 | 0.021601 | 0.0080974 | 0.047482 | -0.0059674 | -0.031001 | -0.058115 | -0.067927 | 0.093333 | 0.14688 | 0.27475 | -0.099689 | 0.051413 | 0.064461 | -0.074666 | -0.039111 | 0.091543 | -0.10671 | -0.15041 | -0.008136 | -121.9465 | 0.060552 | 0.023626 | 0.031762 | -121.8929 | -121.7651 | -0.058859 | -122.0789 | 0.14297 | 0.016887 | 0.075746 | -121.9483 | -122.1465 | 0.18489 | 0.23844 | 0.3663 | 0.033438 | -122.1395 | 0.052442 | 0.1831 | -0.015161 | 0.15601 | -122.1902
3103.0938 | 122.2092 | -0.086975 | 122.0581 | 1.4211e-13 | -0.07439 | 0.0040322 | -0.012842 | -0.013692 | -0.024097 | -0.0054937 | 0.043084 | 0.021387 | 0.0078836 | 0.047482 | -0.0057538 | -0.031001 | -0.053537 | -0.067927 | 0.088755 | 0.14231 | 0.27475 | -0.09511 | 0.046835 | 0.064461 | -0.070087 | -0.029954 | 0.086964 | -0.12503 | -0.15041 | -0.008135 | -121.9693 | 0.055974 | 0.019048 | 0.027183 | -121.9158 | -121.7834 | -0.063437 | -122.0881 | 0.13381 | 0.016888 | 0.080325 | -121.9711 | -122.1831 | 0.17573 | 0.22928 | 0.36172 | 0.033438 | -122.1532 | 0.057021 | 0.17394 | -0.038054 | 0.15144 | -122.2085
3104.7969 | 121.9757 | -0.13275 | 121.756 | 1.4211e-13 | -0.074177 | 0.0029638 | -0.01327 | -0.014119 | -0.024097 | -0.0054937 | 0.043298 | 0.021387 | 0.0078836 | 0.047696 | -0.0057538 | -0.040158 | -0.058115 | -0.072505 | 0.10249 | 0.14231 | 0.27017 | -0.099689 | 0.042256 | 0.064461 | -0.065509 | -0.034533 | 0.091543 | -0.12045 | -0.15957 | 0.033062 | -121.6535 | 0.092593 | 0.060246 | 0.027184 | -121.6137 | -121.4858 | -0.026819 | -121.7905 | 0.17501 | 0.067242 | 0.094061 | -121.6644 | -121.8764 | 0.23524 | 0.27506 | 0.40292 | 0.074636 | -121.8557 | 0.098218 | 0.22429 | 0.012301 | 0.19721 | -121.9156
3106.5625 | 122.2 | -0.082397 | 122.0398 | 1.4211e-13 | -0.07439 | 0.0029638 | -0.013056 | -0.013692 | -0.024311 | -0.013124 | 0.043298 | 0.021174 | 0.0080974 | 0.047269 | -0.0059674 | -0.031001 | -0.053537 | -0.067927 | 0.10249 | 0.14231 | 0.27475 | -0.10427 | 0.051413 | 0.059882 | -0.056351 | -0.034533 | 0.086964 | -0.083821 | -0.15041 | -0.021871 | -121.9373 | 0.051396 | 0.01447 | 0.036341 | -121.8975 | -121.7651 | -0.068015 | -122.0743 | 0.13381 | 0.026046 | 0.094061 | -121.9528 | -122.1236 | 0.18489 | 0.2247 | 0.35714 | 0.02886 | -122.1441 | 0.047864 | 0.16936 | -0.001424 | 0.14228 | -122.1902
3108.3281 | 122.2275 | -0.082397 | 122.0627 | 1.4211e-13 | -0.07439 | 0.0031774 | -0.012842 | -0.013905 | -0.024097 | -0.020755 | 0.043298 | 0.021387 | 0.0080974 | 0.047482 | -0.0053264 | -0.03558 | -0.048958 | -0.067927 | 0.097912 | 0.14688 | 0.27017 | -0.099689 | 0.051413 | 0.064461 | -0.065509 | -0.029954 | 0.096121 | -0.13419 | -0.15499 | -0.017292 | -121.9648 | 0.046817 | 0.01447 | 0.031762 | -121.9158 | -121.7925 | -0.072594 | -122.0926 | 0.13381 | 0.016888 | 0.089482 | -121.9666 | -122.1969 | 0.18031 | 0.22928 | 0.35256 | 0.033439 | -122.1624 | 0.052443 | 0.17852 | -0.051789 | 0.14686 | -122.2177
3110.0938 | 121.9299 | -0.13733 | 121.7148 | 1.4211e-13 | -0.074604 | 0.0031774 | -0.012842 | -0.013478 | -0.023883 | -0.013124 | 0.042871 | 0.021387 | 0.008311 | 0.047696 | -0.0057538 | -0.040158 | -0.062694 | -0.072505 | 0.093333 | 0.13773 | 0.27017 | -0.099689 | 0.051413 | 0.064461 | -0.06093 | -0.048268 | 0.086964 | -0.12961 | -0.15957 | 0.03764 | -121.6214 | 0.097171 | 0.064824 | 0.027184 | -121.5771 | -121.4446 | -0.022241 | -121.7631 | 0.18874 | 0.076399 | 0.09864 | -121.6278 | -121.8444 | 0.23066 | 0.27506 | 0.4075 | 0.074635 | -121.8145 | 0.089061 | 0.22429 | 0.007722 | 0.20179 | -121.8744
3111.8594 | 122.1954 | -0.09613 | 122.0901 | 1.4211e-13 | -0.074177 | 0.0029638 | -0.012629 | -0.014119 | -0.024311 | 0.0021363 | 0.043298 | 0.02096 | 0.0080974 | 0.047269 | -0.0059674 | -0.03558 | -0.067272 | -0.067927 | 0.10249 | 0.13773 | 0.27475 | -0.099689 | 0.051413 | 0.073618 | -0.06093 | -0.034533 | 0.096121 | -0.097557 | -0.15499 | -0.003559 | -121.9877 | 0.06055 | 0.028203 | 0.031762 | -121.9524 | -121.8154 | -0.058861 | -122.1247 | 0.14754 | 0.0352 | 0.094061 | -121.994 | -122.1877 | 0.19862 | 0.23386 | 0.37088 | 0.028858 | -122.1898 | 0.061597 | 0.19225 | -0.001427 | 0.16975 | -122.2451
3113.5625 | 122.1313 | -0.13275 | 122.1176 | 1.4211e-13 | -0.074177 | 0.0029638 | -0.013056 | -0.013692 | -0.024524 | -0.020755 | 0.043298 | 0.021387 | 0.0080974 | 0.047482 | -0.0057538 | -0.026423 | -0.062694 | -0.072505 | 0.097912 | 0.14231 | 0.26559 | -0.085952 | 0.051413 | 0.06904 | -0.06093 | -0.039111 | 0.086964 | -0.12503 | -0.15499 | 0.046799 | -122.0197 | 0.10633 | 0.060246 | 0.013447 | -121.9753 | -121.852 | -0.02224 | -122.1567 | 0.18416 | 0.071821 | 0.094061 | -122.0307 | -122.2426 | 0.23066 | 0.27506 | 0.39834 | 0.070057 | -122.2036 | 0.09364 | 0.21971 | 0.007722 | 0.20179 | -122.2726
3115.3281 | 121.9849 | -0.1236 | 122.1359 | 1.4211e-13 | -0.074604 | 0.0031774 | -0.012842 | -0.014332 | -0.023883 | -0.020755 | 0.042871 | 0.021387 | 0.008311 | 0.04791 | -0.00554 | -0.040158 | -0.062694 | -0.081662 | 0.097912 | 0.13773 | 0.26101 | -0.099689 | 0.046835 | 0.059882 | -0.065509 | -0.034533 | 0.082386 | -0.12961 | -0.15957 | 0.023907 | -122.038 | 0.083438 | 0.041934 | 0.018027 | -121.9982 | -121.8749 | -0.035974 | -122.1705 | 0.17043 | 0.058087 | 0.094061 | -122.0535 | -122.2655 | 0.22151 | 0.26132 | 0.38461 | 0.060902 | -122.2356 | 0.089063 | 0.20598 | -0.006011 | 0.18348 | -122.2955
3117.0938 | 122.0627 | -0.10529 | 122.1222 | 1.4211e-13 | -0.07439 | 0.0033912 | -0.013056 | -0.013478 | -0.024097 | -0.020755 | 0.043298 | 0.021387 | 0.0080974 | 0.04791 | -0.0057538 | -0.03558 | -0.067272 | -0.067927 | 0.097912 | 0.14231 | 0.27475 | -0.10427 | 0.042256 | 0.064461 | -0.070087 | -0.034533 | 0.091543 | -0.079243 | -0.16415 | 0.001018 | -122.0243 | 0.069706 | 0.037359 | 0.036341 | -121.9799 | -121.8474 | -0.058863 | -122.1567 | 0.14754 | 0.035199 | 0.094062 | -122.0306 | -122.2014 | 0.2032 | 0.24759 | 0.38003 | 0.038014 | -122.2265 | 0.070753 | 0.19683 | 0.026043 | 0.16975 | -122.2863
3118.7812 | 122.287 | -0.091553 | 122.081 | 1.4211e-13 | -0.074604 | 0.0029638 | -0.012842 | -0.013692 | -0.024311 | -0.0054937 | 0.043512 | 0.021174 | 0.008311 | 0.047482 | -0.0057538 | -0.03558 | -0.067272 | -0.072505 | 0.088755 | 0.13773 | 0.26101 | -0.09511 | 0.046835 | 0.06904 | -0.065509 | -0.029954 | 0.086964 | -0.12503 | -0.15957 | -0.003557 | -121.9922 | 0.055973 | 0.019048 | 0.022605 | -121.9433 | -121.82 | -0.068017 | -122.1109 | 0.13839 | 0.026044 | 0.094061 | -121.994 | -122.206 | 0.18031 | 0.22928 | 0.35256 | 0.024281 | -122.1761 | 0.061599 | 0.17852 | -0.033476 | 0.16059 | -122.2406
3120.5469 | 122.2412 | -0.082397 | 122.0856 | 1.4211e-13 | -0.07439 | 0.0033912 | -0.013056 | -0.013692 | -0.024311 | -0.0054937 | 0.043084 | 0.021174 | 0.0080974 | 0.04791 | -0.0059674 | -0.044736 | -0.062694 | -0.072505 | 0.093333 | 0.13315 | 0.25643 | -0.10427 | 0.051413 | 0.064461 | -0.065509 | -0.039111 | 0.086964 | -0.12961 | -0.16415 | -0.021871 | -121.9922 | 0.037661 | 0.009892 | 0.031763 | -121.9524 | -121.8291 | -0.081752 | -122.1247 | 0.13381 | 0.016888 | 0.09864 | -121.9986 | -122.2152 | 0.17573 | 0.21554 | 0.33883 | 0.019703 | -122.1898 | 0.043286 | 0.16936 | -0.04721 | 0.14686 | -122.2497
3122.25 | 122.0306 | -0.32501 | 121.8475 | 1.4211e-13 | -0.074818 | 0.0029638 | -0.012629 | -0.013905 | -0.023456 | -0.028385 | 0.043084 | 0.021174 | 0.008311 | 0.047696 | -0.0057538 | -0.2004 | -0.12222 | -0.25106 | 0.056706 | 0.1011 | 0.22438 | -0.36527 | 0.046835 | 0.064461 | -0.06093 | -0.034533 | 0.086964 | -0.12961 | -0.15957 | -0.040254 | -121.7908 | 0.12461 | 0.073954 | 0.11421 | -121.7464 | -121.6232 | 0.16544 | -121.8821 | 0.37185 | 0.26408 | 0.09864 | -121.7606 | -121.9771 | 0.38172 | 0.42611 | 0.54939 | 0.2028 | -122.2128 | 0.29048 | 0.41198 | 0.19541 | 0.38947 | -122.0071
3124.0156 | 122.1359 | -1.03 | 120.9915 | 1.4211e-13 | -0.07439 | 0.0029638 | -0.012842 | -0.013692 | -0.023456 | -0.0054937 | 0.043298 | 0.021174 | 0.0080974 | 0.04791 | -0.0057538 | -0.4751 | -0.21379 | -0.53033 | 0.006344 | 0.046148 | 0.1786 | -0.75448 | 0.046835 | 0.06904 | -0.065509 | -0.025376 | 0.096121 | -0.12503 | -0.16415 | 0.27549 | -120.9852 | 0.55486 | 0.49963 | 0.22414 | -120.9454 | -120.8129 | 0.86582 | -121.0169 | 1.0768 | 0.96446 | 0.09864 | -120.8954 | -121.1165 | 1.0363 | 1.0761 | 1.2086 | 0.81618 | -121.746 | 1.0046 | 1.1261 | 0.90494 | 1.099 | -121.1557
3125.7812 | 121.7789 | -1.7761 | 119.9112 | 1.4211e-13 | -0.074604 | 0.002109 | -0.012415 | -0.013478 | -0.02196 | -0.013124 | 0.043084 | 0.021387 | 0.00767 | 0.04791 | -0.0057538 | -1.3084 | -0.46561 | -1.3682 | -0.19968 | -0.20111 | -0.073228 | -2.0869 | 0.046835 | 0.064461 | -0.065509 | -0.029954 | 0.091543 | -0.11129 | -0.15957 | -0.31082 | -120.1109 | 0.46775 | 0.40796 | 0.71878 | -120.1123 | -119.9844 | 1.6166 | -119.9411 | 1.823 | 1.7106 | 0.094061 | -119.8197 | -120.0225 | 1.5764 | 1.575 | 1.7029 | 1.3105 | -121.9981 | 1.7462 | 1.8677 | 1.6648 | 1.8406 | -120.0708
3127.5 | 121.3165 | -2.8976 | 118.2358 | 1.4211e-13 | -0.074604 | 0.0012544 | -0.011347 | -0.013264 | -0.021319 | -0.0054937 | 0.043084 | 0.021601 | 0.0078836 | 0.04791 | -0.00554 | -1.7525 | -0.56176 | -1.8351 | -0.17221 | -0.16448 | -0.0366 | -2.8562 | 0.051413 | 0.064461 | -0.06093 | -0.034533 | 0.091543 | -0.12045 | -0.15957 | 0.041443 | -118.408 | 1.1452 | 1.0625 | 1.0211 | -118.4003 | -118.2724 | 2.7381 | -118.2703 | 2.9491 | 2.8367 | 0.09864 | -118.1442 | -118.3562 | 2.7254 | 2.7332 | 2.861 | 2.3359 | -121.092 | 2.8631 | 2.9892 | 2.7772 | 2.9621 | -118.3953
3129.1875 | 121.7056 | -67.6666 | 54.9088 | 1.4211e-13 | -0.07204 | -0.036567 | 0.024552 | 0.014512 | 0.16371 | -0.020755 | 0.043298 | 0.02096 | 0.0078836 | 0.048123 | -0.00554 | -39.1396 | -15.2637 | -30.0648 | -5.1123 | -4.9724 | -4.9998 | -66.4987 | 0.046835 | 0.06904 | -0.070087 | -0.025376 | 0.1007 | -0.11129 | -0.15957 | 1.168 | -60.021 | 28.527 | 37.6018 | 36.4339 | -59.8811 | -59.9086 | 67.5071 | -54.9341 | 67.7135 | 67.5965 | 0.089483 | -54.8081 | -55.02 | 62.5543 | 62.6943 | 62.6668 | 52.403 | -121.4074 | 67.6412 | 67.7673 | 67.5553 | 67.7357 | -55.0683
3130.9375 | 121.701 | -89.5203 | 32.0023 | 1.4211e-13 | -0.070971 | -0.050669 | 0.038228 | 0.032246 | 0.81154 | -0.0054937 | 0.043084 | 0.021387 | 0.0085246 | 0.047696 | -0.0059674 | -51.1579 | -31.5452 | -29.4605 | -7.0077 | -6.836 | -6.8908 | -89.3979 | 0.046835 | 0.064461 | -0.070087 | -0.039111 | 0.1007 | -0.10671 | -0.14583 | 0.12239 | -39.01 | 38.3624 | 60.0598 | 59.9374 | -38.8382 | -38.893 | 89.3744 | -32.0414 | 89.5671 | 89.4502 | 0.075746 | -31.9016 | -32.109 | 82.5125 | 82.6843 | 82.6295 | 57.9751 | -121.4001 | 89.4812 | 89.621 | 89.4136 | 89.5847 | -32.1481
3132.7031 | 121.8155 | -80.4565 | 40.8829 | 1.4211e-13 | -0.071613 | -0.042122 | 0.029894 | 0.026691 | 1.5703 | -0.013124 | 0.043084 | 0.021387 | 0.0078836 | 0.047696 | -0.006181 | -41.6989 | -34.9242 | -22.8952 | -6.3439 | -6.1949 | -6.2177 | -75.1254 | 0.051413 | 0.06904 | -0.065509 | -0.034533 | 0.1007 | -0.12961 | -0.15499 | 5.3312 | -47.2268 | 38.7576 | 57.5613 | 52.2301 | -47.0778 | -47.1006 | 80.3016 | -40.9174 | 80.508 | 80.391 | 0.089482 | -40.7822 | -41.0125 | 74.1127 | 74.2616 | 74.2388 | 45.5324 | -116.0082 | 80.422 | 80.5572 | 80.3269 | 80.5256 | -41.0379
3134.4688 | 121.6141 | -85.1349 | 36.0718 | 1.4211e-13 | -0.071185 | -0.050669 | 0.038014 | 0.033528 | 2.5422 | -0.013124 | 0.043084 | 0.021174 | 0.0080974 | 0.04791 | -0.0057538 | -41.4837 | -37.1952 | -24.7128 | -6.2432 | -6.0942 | -6.1307 | -86.1514 | 0.055992 | 0.064461 | -0.06093 | -0.034533 | 0.096121 | -0.13419 | -0.15499 | -1.0165 | -42.3149 | 43.6512 | 60.4221 | 61.4386 | -42.166 | -42.2025 | 84.9799 | -36.1063 | 85.1909 | 85.074 | 0.094061 | -35.9757 | -36.206 | 78.8917 | 79.0407 | 79.0042 | 47.9397 | -122.2232 | 85.1004 | 85.231 | 85.0007 | 85.1993 | -36.2268
3136.2344 | 121.5775 | -90.2847 | 31.0089 | 1.4211e-13 | -0.070544 | -0.050883 | 0.037373 | 0.038015 | 2.7604 | -0.028385 | 0.043084 | 0.021174 | 0.0078836 | 0.04791 | -0.0057538 | -34.4696 | -28.1662 | -22.9364 | -6.3622 | -6.2178 | -6.2498 | -90.4602 | 0.051413 | 0.064461 | -0.06093 | -0.029954 | 0.1007 | -0.12961 | -0.15499 | -0.17546 | -37.3711 | 55.8151 | 67.3483 | 67.5237 | -37.2267 | -37.2587 | 90.1297 | -31.0389 | 90.3361 | 90.2238 | 0.094061 | -30.9082 | -31.1385 | 83.9225 | 84.0669 | 84.035 | 62.1186 | -121.4691 | 90.2548 | 90.3854 | 90.1551 | 90.3492 | -31.1639
3137.9531 | 121.3074 | -63.533 | 57.5912 | 1.4211e-13 | 5.0459 | -0.11221 | -5.041 | 0.01964 | 6.0059 | -0.013124 | 0.042871 | 0.021387 | 0.0080974 | 0.047696 | -0.0059674 | -26.549 | -21.0556 | -19.5943 | -8.8025 | -8.6813 | -9.0107 | -62.4097 | 0.051413 | 0.06904 | -0.06093 | -0.029954 | 0.096121 | -0.12961 | -0.15957 | 1.1233 | -66.3937 | 36.984 | 43.9387 | 42.8154 | -66.2725 | -66.6019 | 63.3734 | -57.6212 | 63.5844 | 63.4721 | 0.09864 | -57.4951 | -57.7209 | 54.7305 | 54.8517 | 54.5224 | 42.4774 | -120.0009 | 63.5031 | 63.6291 | 63.4034 | 63.6021 | -57.7508
3139.7031 | 120.6573 | -46.2891 | 74.7162 | 1.4211e-13 | 6.9467 | -0.47589 | -6.9952 | 0.022204 | 7.0163 | -0.0054937 | 0.042871 | 0.021174 | 0.0078836 | 0.048123 | -0.0063946 | -31.7363 | -25.9272 | -25.4545 | -8.8071 | -8.6904 | -9.0107 | -73.7242 | 0.055992 | 0.064461 | -0.065509 | -0.025376 | 0.096121 | -0.11129 | -0.14583 | -27.4352 | -83.5232 | 14.5527 | 20.8346 | 48.2697 | -83.4066 | -83.7268 | 46.1432 | -74.7416 | 46.3451 | 46.2236 | 0.080324 | -74.6201 | -74.8275 | 37.482 | 37.5986 | 37.2784 | 20.3618 | -148.4404 | 46.2637 | 46.3852 | 46.1778 | 46.3535 | -74.862
3141.4531 | 121.7651 | -72.757 | 48.5138 | 1.4211e-13 | -0.039989 | -0.021823 | -0.082717 | -0.013692 | -0.0027307 | -0.013124 | 0.043512 | 0.021174 | 0.008311 | 0.048123 | -0.006181 | -0.053893 | -0.003172 | -0.072505 | 0.07502 | 0.12399 | 0.25185 | -0.11342 | 0.046835 | 0.064461 | -0.070087 | -0.034533 | 0.091543 | -0.12503 | -0.15957 | 72.6435 | -48.4388 | 72.7031 | 72.6845 | 0.04092 | -48.3898 | -48.2619 | 72.5974 | -48.5483 | 72.8038 | 72.6869 | 0.089483 | -48.4223 | -48.6388 | 72.832 | 72.8809 | 73.0088 | 72.7538 | -48.6272 | 72.7224 | 72.8485 | 72.6319 | 72.8214 | -48.6734
3143.2031 | 121.637 | -80.1453 | 41.2033 | 1.4211e-13 | -0.04063 | -0.021182 | -0.081648 | -0.013905 | -0.0033715 | -0.0054937 | 0.043084 | 0.021174 | 0.0078836 | 0.048337 | -0.0057538 | -0.049315 | -0.003172 | -0.072505 | 0.084176 | 0.11941 | 0.24727 | -0.118 | 0.046835 | 0.06904 | -0.06093 | -0.029954 | 0.096121 | -0.11587 | -0.15957 | 80.0273 | -41.1191 | 80.0959 | 80.0728 | 0.045499 | -41.0839 | -40.956 | 79.9857 | -41.2333 | 80.1921 | 80.0843 | 0.09864 | -41.1072 | -41.3192 | 80.2294 | 80.2647 | 80.3925 | 80.1421 | -41.3213 | 80.1153 | 80.2414 | 80.0294 | 80.2143 | -41.3629
3144.8906 | 121.1517 | -1.3 | 120.52 | 1.4211e-13 | -0.040416 | -0.021609 | -0.081221 | -0.013905 | -0.0033715 | -0.0054937 | 0.043084 | 0.021174 | 0.00767 | 0.04791 | -0.0057538 | -0.026423 | 0.001407 | -0.054192 | 0.079598 | 0.11483 | 0.24727 | -0.09511 | 0.046835 | 0.064461 | -0.070087 | -0.034533 | 0.096121 | -0.12961 | -0.15957 | 1.2049 | -120.4404 | 1.2736 | 1.2459 | 0.040918 | -120.4052 | -120.2727 | 1.1405 | -120.5546 | 1.3469 | 1.23 | 0.089483 | -120.4239 | -120.6496 | 1.3796 | 1.4149 | 1.5473 | 1.3015 | -120.6151 | 1.2655 | 1.3962 | 1.1704 | 1.3645 | -120.6796
3146.6562 | 121.7422 | -83.8715 | 37.3489 | 1.4211e-13 | -0.040844 | -0.022037 | -0.081435 | -0.013692 | -0.0033715 | -0.0054937 | 0.042657 | 0.02096 | 0.0080974 | 0.048337 | -0.0057538 | -0.026423 | -0.003172 | -0.067927 | 0.07502 | 0.11483 | 0.23812 | -0.11342 | 0.046835 | 0.064461 | -0.065509 | -0.034533 | 0.096121 | -0.12045 | -0.15957 | 83.758 | -37.2739 | 83.845 | 83.8035 | 0.045498 | -37.2341 | -37.1108 | 83.7119 | -37.3835 | 83.9183 | 83.806 | 0.094061 | -37.2528 | -37.4694 | 83.9465 | 83.9863 | 84.1096 | 83.8683 | -37.4624 | 83.8369 | 83.9676 | 83.751 | 83.9359 | -37.5085
3148.3438 | 121.637 | -97.5632 | 23.7213 | 1.4211e-13 | -0.040844 | -0.022037 | -0.081221 | -0.013905 | -0.0037989 | 0.0021363 | 0.043084 | 0.021174 | 0.0080974 | 0.048337 | -0.0059674 | -0.026423 | -0.016908 | -0.077084 | 0.070441 | 0.12399 | 0.24727 | -0.10427 | 0.055992 | 0.064461 | -0.065509 | -0.034533 | 0.086964 | -0.12503 | -0.15957 | 97.4589 | -23.6509 | 97.5367 | 97.4861 | 0.027184 | -23.5973 | -23.474 | 97.4036 | -23.7558 | 97.6192 | 97.4977 | 0.094061 | -23.6343 | -23.8463 | 97.6336 | 97.6872 | 97.8104 | 97.5463 | -23.8256 | 97.5286 | 97.6501 | 97.4381 | 97.6276 | -23.8809
3150.1094 | 121.5912 | -120.108 | 1.1627 | 1.4211e-13 | -0.040844 | -0.021609 | -0.081435 | -0.014119 | -0.0025169 | -0.0054937 | 0.042871 | 0.021387 | 0.00767 | 0.048123 | -0.0059674 | -0.031001 | -0.030644 | -0.072505 | 0.065863 | 0.11483 | 0.24727 | -0.099689 | 0.046835 | 0.06904 | -0.06093 | -0.039111 | 0.091543 | -0.13419 | -0.16415 | 120.0083 | -1.0969 | 120.077 | 120.0355 | 0.027184 | -1.0479 | -0.91545 | 119.9439 | -1.2018 | 120.1549 | 120.0471 | 0.10322 | -1.0712 | -1.2969 | 120.1739 | 120.2229 | 120.3553 | 120.0774 | -1.2624 | 120.0689 | 120.1996 | 119.9738 | 120.1771 | -1.3269
3151.8125 | 121.5317 | -120.1401 | 1.1948 | 1.4211e-13 | -0.04063 | -0.021609 | -0.081648 | -0.013692 | -0.0029443 | -0.0054937 | 0.043084 | 0.02096 | 0.0080974 | 0.048123 | -0.0057538 | -0.026423 | -0.035222 | -0.072505 | 0.065863 | 0.11941 | 0.24269 | -0.10885 | 0.042256 | 0.064461 | -0.06093 | -0.034533 | 0.096121 | -0.12961 | -0.16415 | 120.0312 | -1.1289 | 120.1137 | 120.0676 | 0.036342 | -1.0754 | -0.95207 | 119.9759 | -1.2293 | 120.1823 | 120.0791 | 0.10322 | -1.0986 | -1.3244 | 120.2059 | 120.2595 | 120.3828 | 120.1049 | -1.3036 | 120.1055 | 120.2362 | 120.0105 | 120.2045 | -1.3589
3153.5781 | 121.5683 | -120.108 | 1.1719 | 1.4211e-13 | -0.041485 | -0.021823 | -0.081435 | -0.014119 | -0.0029443 | -0.028385 | 0.042871 | 0.021387 | 0.00767 | 0.048337 | -0.0059674 | -0.03558 | -0.026065 | -0.072505 | 0.07502 | 0.11483 | 0.24269 | -0.10427 | 0.055992 | 0.06904 | -0.06093 | -0.025376 | 0.096121 | -0.12045 | -0.16873 | 120.0038 | -1.0969 | 120.0725 | 120.0355 | 0.031763 | -1.057 | -0.92918 | 119.9393 | -1.1973 | 120.164 | 120.0471 | 0.1078 | -1.0758 | -1.2923 | 120.1831 | 120.2229 | 120.3507 | 120.082 | -1.2761 | 120.0827 | 120.2042 | 119.9876 | 120.1771 | -1.3406
3155.3438 | 121.0968 | -0.054932 | 121.6278 | 1.4211e-13 | -0.041698 | -0.021609 | -0.081221 | -0.014119 | -0.0029443 | -0.013124 | 0.043084 | 0.021174 | 0.00767 | 0.048551 | -0.0059674 | -0.026423 | 0.005985 | -0.063349 | 0.070441 | 0.11941 | 0.24269 | -0.10427 | 0.042256 | 0.064461 | -0.06093 | -0.034533 | 0.1007 | -0.10214 | -0.15499 | -0.049336 | -121.5574 | 0.028509 | -0.008417 | 0.040919 | -121.5084 | -121.3851 | -0.10006 | -121.6623 | 0.097188 | -0.005998 | 0.094061 | -121.5271 | -121.7299 | 0.12537 | 0.17434 | 0.29763 | 0.060917 | -121.7321 | 0.020399 | 0.15563 | -0.047204 | 0.11939 | -121.7828
3157.0312 | 120.7535 | 0.11902 | 107.2815 | 1.4211e-13 | -0.041912 | -0.021182 | -0.081007 | -0.014119 | -0.0029443 | -0.013124 | 0.043084 | 0.021174 | 0.00767 | 0.048337 | -0.006181 | -0.03558 | 0.001407 | -0.054192 | 0.084176 | 0.12399 | 0.25185 | -0.10427 | 0.051413 | 0.059882 | -0.074666 | -0.039111 | 0.1007 | -0.12961 | -0.15957 | -0.22329 | -107.1973 | -0.1546 | -0.17321 | 0.050076 | -107.1575 | -107.0296 | -0.27859 | -107.3206 | -0.067606 | -0.19368 | 0.084904 | -107.1808 | -107.4111 | -0.034843 | 0.004971 | 0.13283 | -0.11761 | -107.3858 | -0.15813 | -0.018319 | -0.24863 | -0.059137 | -107.4411
3158.7969 | 119.4443 | 0.11902 | 116.6245 | 1.4211e-13 | -0.041912 | -0.021823 | -0.081435 | -0.014119 | -0.0029443 | -0.013124 | 0.043084 | 0.02096 | 0.00767 | 0.048337 | -0.006181 | -0.026423 | -0.003172 | -0.05877 | 0.07502 | 0.11941 | 0.24269 | -0.09511 | 0.042256 | 0.06904 | -0.056351 | -0.025376 | 0.096121 | -0.12961 | -0.15957 | -0.21413 | -116.5494 | -0.14544 | -0.17779 | 0.03634 | -116.505 | -116.3818 | -0.27859 | -116.6498 | -0.076763 | -0.17537 | 0.10322 | -116.5283 | -116.7541 | -0.043999 | 0.000392 | 0.12368 | -0.12219 | -116.7196 | -0.14439 | -0.022898 | -0.24863 | -0.049979 | -116.784
3160.5625 | 104.2145 | 0.17853 | 118.1534 | 1.4211e-13 | -0.042126 | -0.021609 | -0.081221 | -0.014119 | -0.0029443 | -0.0054937 | 0.043084 | 0.020746 | 0.0078836 | 0.048337 | -0.0063946 | -0.021844 | -0.003172 | -0.063349 | 0.079598 | 0.12399 | 0.25185 | -0.099689 | 0.046835 | 0.059882 | -0.06093 | -0.029954 | 0.1007 | -0.12961 | -0.16415 | -0.27822 | -118.0738 | -0.20037 | -0.24188 | 0.03634 | -118.0294 | -117.9015 | -0.34268 | -118.1833 | -0.13169 | -0.23946 | 0.10322 | -118.0527 | -118.283 | -0.09893 | -0.054538 | 0.073324 | -0.1817 | -118.2531 | -0.20848 | -0.077828 | -0.30813 | -0.11865 | -118.3175
3162.2656 | 98.6298 | 0.004578 | 106.6315 | 1.4211e-13 | -0.041698 | -0.021182 | -0.081007 | -0.014119 | -0.0029443 | -0.013124 | 0.042657 | 0.020746 | 0.0080974 | 0.048337 | -0.0057538 | -0.026423 | 0.015142 | -0.067927 | 0.07502 | 0.11483 | 0.24727 | -0.085952 | 0.042256 | 0.064461 | -0.065509 | -0.029954 | 0.096121 | -0.12961 | -0.16415 | -0.09053 | -106.5564 | -0.031001 | -0.072505 | 0.018025 | -106.5166 | -106.3842 | -0.16873 | -106.6614 | 0.037678 | -0.070087 | 0.09864 | -106.5353 | -106.7611 | 0.070442 | 0.11025 | 0.2427 | 0.010564 | -106.7174 | -0.034532 | 0.091543 | -0.13418 | 0.059883 | -106.7956
3164.0156 | 91.0446 | -0.20142 | 91.571 | 1.4211e-13 | -0.042339 | -0.021396 | -0.081221 | -0.013692 | -0.0031579 | -0.0054937 | 0.043084 | 0.021174 | 0.0080974 | 0.048123 | -0.006181 | -0.026423 | 0.001407 | -0.054192 | 0.07502 | 0.12399 | 0.25185 | -0.090531 | 0.055992 | 0.064461 | -0.06093 | -0.029954 | 0.096121 | -0.0884 | -0.16873 | 0.11089 | -91.496 | 0.17499 | 0.14722 | 0.036339 | -91.4471 | -91.3192 | 0.032688 | -91.601 | 0.25741 | 0.14049 | 0.1078 | -91.4749 | -91.6594 | 0.27644 | 0.32541 | 0.45327 | 0.20282 | -91.6616 | 0.17146 | 0.29754 | 0.11302 | 0.26588 | -91.7398
3165.7656 | 121.788 | 0.022888 | 115.8829 | 1.4211e-13 | -0.041485 | -0.021396 | -0.081435 | -0.014332 | -0.0031579 | -0.020755 | 0.043298 | 0.021174 | 0.00767 | 0.048337 | -0.006181 | -0.026423 | -0.007751 | -0.05877 | 0.079598 | 0.11025 | 0.23812 | -0.09511 | 0.055992 | 0.064461 | -0.06093 | -0.034533 | 0.091543 | -0.10214 | -0.15957 | -0.118 | -115.8033 | -0.049311 | -0.081658 | 0.03634 | -115.7726 | -115.6448 | -0.18246 | -115.9174 | 0.033104 | -0.083818 | 0.09864 | -115.7913 | -115.985 | 0.05671 | 0.087365 | 0.21523 | -0.030639 | -115.978 | -0.057421 | 0.068655 | -0.12502 | 0.041573 | -116.0424
3167.4688 | 121.1426 | -0.013733 | 121.0327 | 1.4211e-13 | -0.041912 | -0.021396 | -0.081007 | -0.014332 | -0.0027307 | -0.013124 | 0.043298 | 0.021174 | 0.00767 | 0.048337 | -0.006181 | -0.031001 | -0.007751 | -0.054192 | 0.065863 | 0.10567 | 0.23812 | -0.099689 | 0.051413 | 0.055303 | -0.065509 | -0.029954 | 0.096121 | -0.12961 | -0.16415 | -0.085956 | -120.9669 | -0.017268 | -0.040459 | 0.045497 | -120.927 | -120.7946 | -0.15042 | -121.0627 | 0.065146 | -0.051776 | 0.09864 | -120.9366 | -121.1623 | 0.079596 | 0.11941 | 0.25185 | 0.005982 | -121.1324 | -0.016221 | 0.10985 | -0.11587 | 0.069036 | -121.1969
3169.2188 | 121.431 | -0.07782 | 121.2433 | 1.4211e-13 | -0.041912 | -0.021609 | -0.081221 | -0.013905 | -0.0033715 | -0.013124 | 0.043084 | 0.02096 | 0.0078836 | 0.048123 | -0.0063946 | -0.03558 | -0.007751 | -0.054192 | 0.070441 | 0.11025 | 0.23354 | -0.099689 | 0.046835 | 0.06904 | -0.070087 | -0.029954 | 0.096121 | -0.12503 | -0.15957 | -0.021869 | -121.1728 | 0.04224 | 0.023628 | 0.045497 | -121.133 | -121.0097 | -0.08175 | -121.2732 | 0.12466 | 0.007733 | 0.089483 | -121.1472 | -121.3683 | 0.14826 | 0.18807 | 0.31136 | 0.070069 | -121.343 | 0.047866 | 0.17394 | -0.047209 | 0.14686 | -121.4029
3170.9219 | 121.1929 | -0.018311 | 121.1105 | 1.4211e-13 | -0.042126 | -0.021609 | -0.081007 | -0.013905 | -0.0033715 | -0.013124 | 0.042871 | 0.02096 | 0.00767 | 0.048551 | -0.0063946 | -0.03558 | -0.003172 | -0.05877 | 0.065863 | 0.11025 | 0.23354 | -0.10427 | 0.046835 | 0.059882 | -0.065509 | -0.034533 | 0.096121 | -0.12503 | -0.16415 | -0.085957 | -121.0447 | -0.017269 | -0.040459 | 0.045498 | -121.0003 | -120.877 | -0.14584 | -121.1451 | 0.065146 | -0.047198 | 0.09864 | -121.0144 | -121.2356 | 0.084174 | 0.12856 | 0.25185 | 0.015139 | -121.2148 | -0.016222 | 0.11443 | -0.10672 | 0.078193 | -121.2747
3172.6875 | 121.2891 | -0.036621 | 121.0922 | 1.4211e-13 | -0.042126 | -0.021396 | -0.081221 | -0.013905 | -0.0031579 | -0.013124 | 0.042871 | 0.02096 | 0.0078836 | 0.048551 | -0.0059674 | -0.03558 | -0.007751 | -0.054192 | 0.07502 | 0.11941 | 0.23812 | -0.10885 | 0.051413 | 0.064461 | -0.065509 | -0.034533 | 0.096121 | -0.12503 | -0.16415 | -0.072226 | -121.0172 | 0.001041 | -0.017571 | 0.054655 | -120.9728 | -120.8541 | -0.12753 | -121.1268 | 0.088034 | -0.028888 | 0.09864 | -120.9961 | -121.2173 | 0.11164 | 0.15603 | 0.27474 | 0.02887 | -121.2011 | 0.002088 | 0.13274 | -0.088408 | 0.10108 | -121.2564
3174.4375 | 121.4401 | -0.10071 | 121.1655 | 1.4211e-13 | -0.042126 | -0.021609 | -0.081221 | -0.013905 | -0.0031579 | -0.013124 | 0.043084 | 0.02096 | 0.00767 | 0.048337 | -0.006181 | -0.021844 | 0.001407 | -0.054192 | 0.065863 | 0.11483 | 0.24727 | -0.09511 | 0.051413 | 0.064461 | -0.065509 | -0.029954 | 0.086964 | -0.12503 | -0.15499 | 0.005598 | -121.0996 | 0.078864 | 0.046516 | 0.040918 | -121.0506 | -120.9182 | -0.054283 | -121.1954 | 0.15212 | 0.035199 | 0.089482 | -121.0785 | -121.2905 | 0.16657 | 0.21554 | 0.34798 | 0.10212 | -121.2606 | 0.070754 | 0.18767 | -0.024321 | 0.16517 | -121.3205
3176.1875 | 121.4951 | -0.073242 | 121.17 | 1.4211e-13 | -0.042339 | -0.021396 | -0.081435 | -0.014332 | -0.0029443 | -0.0054937 | 0.042657 | 0.02096 | 0.0078836 | 0.048551 | -0.006181 | -0.026423 | -0.012329 | -0.054192 | 0.070441 | 0.11483 | 0.23812 | -0.099689 | 0.046835 | 0.073618 | -0.06093 | -0.039111 | 0.096121 | -0.12045 | -0.16415 | -0.026447 | -121.0996 | 0.046819 | 0.01905 | 0.045497 | -121.0552 | -120.9319 | -0.090907 | -121.2092 | 0.12008 | 0.012312 | 0.10322 | -121.0739 | -121.2905 | 0.14368 | 0.18807 | 0.31136 | 0.060913 | -121.2697 | 0.034131 | 0.16936 | -0.047208 | 0.14686 | -121.3342
3177.9062 | 91.0492 | -0.10986 | 114.9902 | 1.4211e-13 | -0.042339 | -0.021609 | -0.080794 | -0.013692 | -0.0029443 | -0.0054937 | 0.042871 | 0.021174 | 0.00767 | 0.048764 | -0.006181 | -0.026423 | 0.001407 | -0.054192 | 0.07502 | 0.11483 | 0.25643 | -0.09511 | 0.042256 | 0.059882 | -0.065509 | -0.034533 | 0.091543 | -0.12961 | -0.15957 | 0.014753 | -114.9152 | 0.08344 | 0.055671 | 0.040918 | -114.8754 | -114.7338 | -0.049707 | -115.0248 | 0.15212 | 0.044354 | 0.094061 | -114.8987 | -115.1198 | 0.18488 | 0.2247 | 0.36629 | 0.11127 | -115.0853 | 0.07533 | 0.20141 | -0.019744 | 0.16975 | -115.1498
3179.6719 | 117.0639 | 0 | 118.1351 | 1.4211e-13 | -0.042767 | -0.021823 | -0.081221 | -0.013692 | -0.0027307 | -0.0054937 | 0.042657 | 0.020746 | 0.00767 | 0.048337 | -0.0059674 | -0.021844 | 0.001407 | -0.045036 | 0.07502 | 0.11941 | 0.24269 | -0.076794 | 0.046835 | 0.059882 | -0.06093 | -0.034533 | 0.091543 | -0.12045 | -0.16873 | -0.076794 | -118.0601 | -0.021844 | -0.045036 | 0.031758 | -118.0157 | -117.8924 | -0.16873 | -118.1696 | 0.046835 | -0.06093 | 0.1078 | -118.0435 | -118.2555 | 0.07502 | 0.11941 | 0.24269 | 0.001407 | -118.2119 | -0.034533 | 0.091543 | -0.12045 | 0.059882 | -118.3038
3181.4375 | 91.127 | -0.036621 | 109.433 | 1.4211e-13 | -0.042553 | -0.021396 | -0.081007 | -0.014119 | -0.0029443 | -0.0054937 | 0.042871 | 0.02096 | 0.00767 | 0.048764 | -0.006181 | -0.026423 | 0.001407 | -0.040457 | 0.070441 | 0.12399 | 0.23812 | -0.076794 | 0.051413 | 0.059882 | -0.06093 | -0.034533 | 0.096121 | -0.12503 | -0.15957 | -0.040173 | -109.3625 | 0.010198 | -0.003836 | 0.036337 | -109.309 | -109.1949 | -0.12295 | -109.4675 | 0.088034 | -0.024309 | 0.09864 | -109.3369 | -109.558 | 0.10706 | 0.16061 | 0.27474 | 0.038028 | -109.5098 | 0.002088 | 0.13274 | -0.088408 | 0.096503 | -109.5926
3183.2031 | 116.0706 | -0.041199 | 116.7572 | 1.4211e-13 | -0.042339 | -0.021609 | -0.081435 | -0.014332 | -0.0027307 | -0.0054937 | 0.042871 | 0.02096 | 0.00767 | 0.048978 | -0.006181 | -0.031001 | 0.001407 | -0.049614 | 0.07502 | 0.12399 | 0.24269 | -0.058478 | 0.046835 | 0.06904 | -0.06093 | -0.029954 | 0.096121 | -0.12961 | -0.15957 | -0.017279 | -116.6822 | 0.010198 | -0.008415 | 0.008864 | -116.6332 | -116.5145 | -0.11837 | -116.7872 | 0.088034 | -0.019731 | 0.09864 | -116.6611 | -116.8868 | 0.11622 | 0.16519 | 0.28389 | 0.042606 | -116.8157 | 0.011245 | 0.13732 | -0.088408 | 0.11024 | -116.9168
3184.9062 | 121.3715 | -0.064087 | 122.081 | 1.4211e-13 | -0.042339 | -0.021609 | -0.081435 | -0.014332 | -0.0031579 | -0.0054937 | 0.042871 | 0.02096 | 0.00767 | 0.048551 | -0.0059674 | -0.017266 | 0.005985 | -0.049614 | 0.079598 | 0.11941 | 0.24727 | -0.085952 | 0.046835 | 0.064461 | -0.070087 | -0.029954 | 0.096121 | -0.12045 | -0.15957 | -0.021865 | -122.0014 | 0.046821 | 0.014473 | 0.036338 | -121.9616 | -121.8337 | -0.095483 | -122.1109 | 0.11092 | -0.006 | 0.089483 | -121.9849 | -122.2014 | 0.14369 | 0.1835 | 0.31136 | 0.070072 | -122.1669 | 0.034133 | 0.16021 | -0.056363 | 0.12855 | -122.2406
3186.6562 | 121.4996 | -0.068665 | 121.2891 | 1.4211e-13 | -0.042339 | -0.021609 | -0.081221 | -0.014332 | -0.0031579 | -0.013124 | 0.043084 | 0.021174 | 0.0078836 | 0.048551 | -0.0059674 | -0.021844 | 0.010564 | -0.045036 | 0.088755 | 0.11483 | 0.24727 | -0.035584 | 0.051413 | 0.064461 | -0.056351 | -0.025376 | 0.091543 | -0.12961 | -0.15499 | 0.033081 | -121.2003 | 0.046821 | 0.023629 | -0.009452 | -121.1742 | -121.0418 | -0.086326 | -121.3144 | 0.12008 | 0.012314 | 0.09864 | -121.1975 | -121.4187 | 0.15742 | 0.1835 | 0.31594 | 0.079229 | -121.3246 | 0.043289 | 0.16021 | -0.060942 | 0.13313 | -121.4441
3188.4219 | 121.4905 | -0.073242 | 121.9711 | 1.4211e-13 | -0.042339 | -0.021609 | -0.081221 | -0.014119 | -0.0035853 | -0.020755 | 0.043298 | 0.02096 | 0.0078836 | 0.048764 | -0.0059674 | -0.021844 | 0.005985 | -0.049614 | 0.079598 | 0.11941 | 0.24269 | -0.085952 | 0.046835 | 0.059882 | -0.070087 | -0.034533 | 0.091543 | -0.12961 | -0.15957 | -0.01271 | -121.8915 | 0.051398 | 0.023628 | 0.036338 | -121.8517 | -121.7284 | -0.086328 | -122.0057 | 0.12008 | 0.003155 | 0.089483 | -121.8796 | -122.1007 | 0.15284 | 0.19265 | 0.31594 | 0.079227 | -122.0571 | 0.038709 | 0.16479 | -0.056365 | 0.13312 | -122.1307
3190.125 | 93.5349 | -0.036621 | 92.8757 | 1.4211e-13 | -0.042767 | -0.021609 | -0.081007 | -0.014119 | -0.0031579 | -0.013124 | 0.043084 | 0.02096 | 0.0078836 | 0.048551 | -0.0063946 | -0.017266 | 0.001407 | -0.049614 | 0.07502 | 0.12399 | 0.24269 | -0.058478 | 0.051413 | 0.059882 | -0.065509 | -0.029954 | 0.086964 | -0.11587 | -0.15499 | -0.021857 | -92.8007 | 0.019355 | -0.012993 | 0.008864 | -92.7517 | -92.633 | -0.11837 | -92.9056 | 0.088034 | -0.028888 | 0.089482 | -92.7887 | -92.9915 | 0.11164 | 0.16061 | 0.27932 | 0.038028 | -92.9341 | 0.006667 | 0.12359 | -0.079251 | 0.096503 | -93.0307
3191.875 | 121.463 | -0.068665 | 121.4081 | 1.4211e-13 | -0.042339 | -0.021823 | -0.080794 | -0.014332 | -0.0029443 | -0.020755 | 0.042871 | 0.020746 | 0.00767 | 0.048764 | -0.0063946 | -0.021844 | 0.010564 | -0.049614 | 0.070441 | 0.12399 | 0.24269 | -0.076794 | 0.046835 | 0.055303 | -0.06093 | -0.034533 | 0.091543 | -0.12045 | -0.15499 | -0.008129 | -121.3376 | 0.046821 | 0.019051 | 0.02718 | -121.2841 | -121.1654 | -0.086326 | -121.4426 | 0.1155 | 0.007735 | 0.094061 | -121.3165 | -121.5285 | 0.13911 | 0.19266 | 0.31136 | 0.079229 | -121.4849 | 0.034132 | 0.16021 | -0.051785 | 0.12397 | -121.5631
3193.6406 | 100.177 | 0.20142 | 111.7767 | 1.4211e-13 | -0.042553 | -0.021823 | -0.080794 | -0.014119 | -0.0029443 | -0.020755 | 0.042657 | 0.02096 | 0.0074564 | 0.048764 | -0.006181 | -0.017266 | 0.005985 | -0.054192 | 0.07502 | 0.11941 | 0.24269 | -0.076794 | 0.046835 | 0.059882 | -0.06093 | -0.034533 | 0.1007 | -0.12045 | -0.16415 | -0.27821 | -111.7017 | -0.21868 | -0.25561 | 0.022602 | -111.6573 | -111.534 | -0.36557 | -111.8113 | -0.15458 | -0.26235 | 0.10322 | -111.676 | -111.8972 | -0.1264 | -0.082005 | 0.041279 | -0.19543 | -111.8535 | -0.23595 | -0.10072 | -0.32187 | -0.14153 | -111.9409
3195.3594 | 113.0859 | 0.013733 | 121.257 | 1.4211e-13 | -0.042767 | -0.021396 | -0.080794 | -0.014119 | -0.0031579 | -0.013124 | 0.042657 | 0.021387 | 0.0074564 | 0.048764 | -0.0059674 | -0.021844 | 0.005985 | -0.054192 | 0.07502 | 0.11941 | 0.23812 | -0.049321 | 0.046835 | 0.06904 | -0.056351 | -0.034533 | 0.091543 | -0.12961 | -0.15499 | -0.063054 | -121.182 | -0.035577 | -0.067925 | -0.004871 | -121.1376 | -121.0189 | -0.16872 | -121.2916 | 0.033102 | -0.070084 | 0.09864 | -121.1655 | -121.3866 | 0.061287 | 0.10568 | 0.22438 | -0.007748 | -121.3063 | -0.048266 | 0.07781 | -0.14334 | 0.055307 | -121.412
3197.1094 | 121.5088 | -0.091553 | 121.5363 | 1.4211e-13 | -0.042553 | -0.021609 | -0.081007 | -0.014119 | -0.0029443 | -0.020755 | 0.042871 | 0.021174 | 0.0080974 | 0.048764 | -0.006181 | -0.017266 | 0.005985 | -0.049614 | 0.07502 | 0.11941 | 0.24727 | -0.049321 | 0.042256 | 0.064461 | -0.056351 | -0.034533 | 0.096121 | -0.13419 | -0.15957 | 0.042232 | -121.4612 | 0.074287 | 0.041939 | -0.000293 | -121.4168 | -121.289 | -0.068017 | -121.5708 | 0.13381 | 0.035202 | 0.10322 | -121.4401 | -121.6704 | 0.16657 | 0.21096 | 0.33883 | 0.097538 | -121.5856 | 0.05702 | 0.18767 | -0.042633 | 0.15601 | -121.6958
3198.8125 | 121.7606 | -0.07782 | 121.8063 | 1.4211e-13 | -0.042126 | -0.021609 | -0.081007 | -0.014332 | -0.0029443 | 0.0021363 | 0.042871 | 0.020746 | 0.0078836 | 0.048337 | -0.0059674 | -0.021844 | 0.001407 | -0.045036 | 0.070441 | 0.12857 | 0.24727 | -0.063057 | 0.051413 | 0.059882 | -0.06093 | -0.034533 | 0.096121 | -0.13419 | -0.15499 | 0.014763 | -121.7359 | 0.055976 | 0.032784 | 0.018021 | -121.6778 | -121.5591 | -0.077171 | -121.8409 | 0.12923 | 0.01689 | 0.094061 | -121.7102 | -121.9405 | 0.14826 | 0.20639 | 0.32509 | 0.079227 | -121.8694 | 0.043287 | 0.17394 | -0.056366 | 0.1377 | -121.9613
3200.5781 | 93.6172 | 0.63171 | 121.4813 | 1.4211e-13 | -0.042126 | -0.021823 | -0.081435 | -0.014119 | -0.0031579 | -0.020755 | 0.042657 | 0.02096 | 0.0078836 | 0.048764 | -0.006181 | -0.021844 | 0.005985 | -0.049614 | 0.07502 | 0.11941 | 0.23812 | -0.076794 | 0.037677 | 0.059882 | -0.056351 | -0.034533 | 0.096121 | -0.12503 | -0.16415 | -0.70851 | -121.4063 | -0.65356 | -0.68133 | 0.02718 | -121.3619 | -121.2432 | -0.79586 | -121.5159 | -0.59404 | -0.68807 | 0.1078 | -121.3852 | -121.6064 | -0.55669 | -0.5123 | -0.3936 | -0.62573 | -121.5581 | -0.66625 | -0.53559 | -0.75674 | -0.57183 | -121.6455
3202.2969 | 120.5933 | 0.004578 | 121.5683 | 1.4211e-13 | -0.042767 | -0.021609 | -0.08058 | -0.014119 | -0.0031579 | -0.013124 | 0.042443 | 0.020746 | 0.0078836 | 0.048764 | -0.0063946 | -0.017266 | 0.001407 | -0.049614 | 0.079598 | 0.12399 | 0.23812 | -0.072215 | 0.046835 | 0.06904 | -0.056351 | -0.020797 | 0.096121 | -0.12961 | -0.15499 | -0.076793 | -121.4887 | -0.021844 | -0.054192 | 0.022601 | -121.4443 | -121.3302 | -0.15957 | -121.5891 | 0.042257 | -0.060929 | 0.09864 | -121.4722 | -121.6979 | 0.07502 | 0.11941 | 0.23354 | -0.003171 | -121.6405 | -0.025375 | 0.091543 | -0.13418 | 0.064462 | -121.7233
3204.0625 | 121.5317 | -0.064087 | 121.7651 | 1.4211e-13 | -0.042767 | -0.021823 | -0.081007 | -0.013905 | -0.0031579 | -0.020755 | 0.042871 | 0.020746 | 0.0078836 | 0.048764 | -0.006181 | -0.021844 | 0.005985 | -0.049614 | 0.07502 | 0.11941 | 0.24269 | -0.076794 | 0.051413 | 0.06904 | -0.065509 | -0.029954 | 0.096121 | -0.12961 | -0.15957 | -0.012707 | -121.6901 | 0.042243 | 0.014473 | 0.02718 | -121.6457 | -121.5224 | -0.095483 | -121.7951 | 0.1155 | -0.001422 | 0.094061 | -121.669 | -121.8947 | 0.13911 | 0.1835 | 0.30678 | 0.070072 | -121.8419 | 0.034133 | 0.16021 | -0.06552 | 0.13313 | -121.9247
3205.7656 | 121.4584 | -0.068665 | 121.8155 | 1.4211e-13 | -0.042767 | -0.021396 | -0.081221 | -0.014332 | -0.0031579 | -0.013124 | 0.042657 | 0.02096 | 0.0074564 | 0.048764 | -0.0063946 | -0.017266 | 0.010564 | -0.045036 | 0.07502 | 0.11483 | 0.24727 | -0.067636 | 0.042256 | 0.06904 | -0.056351 | -0.029954 | 0.096121 | -0.12961 | -0.16415 | 0.001029 | -121.7405 | 0.051399 | 0.023629 | 0.0226 | -121.7007 | -121.5682 | -0.095484 | -121.8454 | 0.11092 | 0.012314 | 0.1078 | -121.7194 | -121.9451 | 0.14369 | 0.1835 | 0.31594 | 0.079229 | -121.8831 | 0.038711 | 0.16479 | -0.060942 | 0.13771 | -121.9796
3207.5156 | 96.8719 | 0.1831 | 121.3623 | 1.4211e-13 | -0.042767 | -0.021609 | -0.080794 | -0.013905 | -0.0029443 | -0.0054937 | 0.043084 | 0.020746 | 0.0078836 | 0.048978 | -0.006181 | -0.017266 | 0.001407 | -0.049614 | 0.065863 | 0.11483 | 0.24269 | -0.053899 | 0.042256 | 0.059882 | -0.065509 | -0.029954 | 0.091543 | -0.12961 | -0.15957 | -0.237 | -121.2964 | -0.20037 | -0.23272 | 0.004285 | -121.2475 | -121.1196 | -0.34267 | -121.3923 | -0.14085 | -0.24861 | 0.094061 | -121.2708 | -121.4919 | -0.11724 | -0.068273 | 0.05959 | -0.1817 | -121.4162 | -0.21306 | -0.091562 | -0.31271 | -0.12322 | -121.5219
3209.2188 | 121.7468 | -0.07782 | 121.8842 | 1.4211e-13 | -0.042339 | -0.021396 | -0.08058 | -0.014119 | -0.0033715 | -0.0054937 | 0.043084 | 0.021174 | 0.00767 | 0.048551 | -0.006181 | -0.017266 | 0.005985 | -0.049614 | 0.07502 | 0.11941 | 0.24269 | -0.081373 | 0.051413 | 0.064461 | -0.06093 | -0.039111 | 0.096121 | -0.12503 | -0.16415 | -0.003553 | -121.8091 | 0.060554 | 0.028206 | 0.031759 | -121.7647 | -121.6415 | -0.086329 | -121.9233 | 0.12923 | 0.01689 | 0.10322 | -121.788 | -122.0092 | 0.15284 | 0.19723 | 0.32051 | 0.083805 | -121.9655 | 0.038709 | 0.17394 | -0.047209 | 0.14228 | -122.0483
3210.9844 | 121.8704 | -0.082397 | 122.0078 | 1.4211e-13 | -0.042553 | -0.021609 | -0.08058 | -0.014332 | -0.0031579 | -0.028385 | 0.042871 | 0.021387 | 0.0072428 | 0.048978 | -0.0059674 | -0.021844 | 0.015142 | -0.045036 | 0.07502 | 0.10567 | 0.23812 | -0.063057 | 0.055992 | 0.06904 | -0.06093 | -0.029954 | 0.096121 | -0.12503 | -0.15957 | 0.01934 | -121.9327 | 0.060553 | 0.037361 | 0.018021 | -121.9021 | -121.7696 | -0.077173 | -122.0377 | 0.13839 | 0.021467 | 0.09864 | -121.9116 | -122.1328 | 0.15742 | 0.18807 | 0.32051 | 0.097539 | -122.0708 | 0.052443 | 0.17852 | -0.042632 | 0.15144 | -122.1673
3212.75 | 111.2595 | 0.073242 | 121.4035 | 1.4211e-13 | -0.042553 | -0.021823 | -0.080366 | -0.014546 | -0.0033715 | -0.0054937 | 0.042871 | 0.020746 | 0.00767 | 0.048764 | -0.006181 | -0.021844 | 0.005985 | -0.045036 | 0.079598 | 0.11941 | 0.24727 | -0.090531 | 0.046835 | 0.059882 | -0.056351 | -0.034533 | 0.091543 | -0.13876 | -0.15957 | -0.16377 | -121.3239 | -0.095086 | -0.11828 | 0.045495 | -121.2841 | -121.1562 | -0.23281 | -121.438 | -0.026407 | -0.12959 | 0.10322 | -121.312 | -121.5423 | 0.006356 | 0.046169 | 0.17403 | -0.067257 | -121.494 | -0.10778 | 0.018301 | -0.21201 | -0.01336 | -121.5631
3214.4531 | 121.9116 | -0.082397 | 121.9803 | 1.4211e-13 | -0.042553 | -0.021823 | -0.080794 | -0.014119 | -0.0033715 | -0.020755 | 0.042871 | 0.02096 | 0.00767 | 0.048978 | -0.006181 | -0.031001 | 0.005985 | -0.054192 | 0.07502 | 0.11941 | 0.23812 | -0.049321 | 0.046835 | 0.06904 | -0.056351 | -0.034533 | 0.096121 | -0.12961 | -0.15957 | 0.033076 | -121.9053 | 0.051396 | 0.028205 | -0.004871 | -121.8609 | -121.7422 | -0.077173 | -122.0148 | 0.12923 | 0.026046 | 0.10322 | -121.8842 | -122.1099 | 0.15742 | 0.20181 | 0.32051 | 0.088382 | -122.0296 | 0.047864 | 0.17852 | -0.04721 | 0.15144 | -122.1399
3216.2031 | 121.7285 | -0.059509 | 122.0261 | 1.4211e-13 | -0.04298 | -0.021823 | -0.080794 | -0.014119 | -0.0033715 | -0.013124 | 0.043084 | 0.020746 | 0.00767 | 0.049192 | -0.0063946 | -0.031001 | -0.007751 | -0.063349 | 0.056706 | 0.091937 | 0.22896 | -0.090531 | 0.046835 | 0.055303 | -0.06093 | -0.025376 | 0.091543 | -0.12045 | -0.15957 | -0.031022 | -121.9694 | 0.028508 | -0.00384 | 0.027182 | -121.9341 | -121.7971 | -0.10006 | -122.0514 | 0.10634 | -0.001421 | 0.09864 | -121.9345 | -122.1465 | 0.11621 | 0.15145 | 0.28847 | 0.051758 | -122.1166 | 0.034133 | 0.15105 | -0.060941 | 0.11481 | -122.1856
3217.9844 | 121.8246 | -0.054932 | 121.9894 | 1.4211e-13 | -0.04298 | -0.021396 | -0.08058 | -0.014332 | -0.0035853 | 0.0021363 | 0.042657 | 0.021174 | 0.0074564 | 0.048978 | -0.0063946 | -0.026423 | 0.005985 | -0.054192 | 0.070441 | 0.11025 | 0.24269 | -0.049321 | 0.046835 | 0.073618 | -0.06093 | -0.029954 | 0.091543 | -0.13876 | -0.16415 | 0.005611 | -121.919 | 0.028509 | 0.00074 | -0.004871 | -121.8792 | -121.7467 | -0.10922 | -122.0194 | 0.10177 | -0.005998 | 0.10322 | -121.8979 | -122.1282 | 0.12537 | 0.16518 | 0.29763 | 0.060917 | -122.0388 | 0.024978 | 0.14647 | -0.083833 | 0.12855 | -122.1536
3219.75 | 121.9757 | -0.07782 | 122.0535 | 1.4211e-13 | -0.04298 | -0.021823 | -0.080794 | -0.014119 | -0.0031579 | -0.0054937 | 0.042871 | 0.02096 | 0.0074564 | 0.049192 | -0.006181 | -0.021844 | 0.001407 | -0.049614 | 0.070441 | 0.11483 | 0.24269 | -0.031005 | 0.042256 | 0.06904 | -0.051772 | -0.034533 | 0.096121 | -0.12961 | -0.16873 | 0.046815 | -121.9831 | 0.055976 | 0.028206 | -0.018609 | -121.9387 | -121.8108 | -0.090908 | -122.0881 | 0.12008 | 0.026048 | 0.11696 | -121.9574 | -122.1831 | 0.14826 | 0.19265 | 0.32051 | 0.079227 | -122.0845 | 0.043287 | 0.17394 | -0.051787 | 0.14686 | -122.2223
3221.5312 | 121.4172 | -0.059509 | 121.7926 | 1.4211e-13 | -0.042767 | -0.021182 | -0.080366 | -0.014332 | -0.0035853 | -0.013124 | 0.042871 | 0.02096 | 0.0074564 | 0.048978 | -0.006181 | -0.049315 | -0.012329 | -0.072505 | 0.056706 | 0.096516 | 0.21522 | -0.10885 | 0.051413 | 0.064461 | -0.06093 | -0.039111 | 0.096121 | -0.12503 | -0.15957 | -0.049338 | -121.7359 | 0.010194 | -0.012996 | 0.036342 | -121.6961 | -121.5774 | -0.10006 | -121.8317 | 0.11092 | -0.001421 | 0.09864 | -121.6965 | -121.9176 | 0.11621 | 0.15602 | 0.27473 | 0.04718 | -121.9014 | 0.020398 | 0.15563 | -0.06552 | 0.12397 | -121.9522
3223.2344 | 121.4493 | -0.07782 | 121.8887 | 1.4211e-13 | -0.04298 | -0.021396 | -0.080794 | -0.014119 | -0.0033715 | -0.0054937 | 0.042871 | 0.02096 | 0.007029 | 0.049405 | -0.0066084 | -0.06305 | -0.035222 | -0.08624 | 0.038393 | 0.064464 | 0.20149 | -0.13632 | 0.042256 | 0.059882 | -0.056351 | -0.029954 | 0.086964 | -0.13419 | -0.15499 | -0.0585 | -121.8503 | 0.01477 | -0.00842 | 0.05008 | -121.8243 | -121.6872 | -0.077171 | -121.9187 | 0.12008 | 0.021469 | 0.09864 | -121.8018 | -122.0229 | 0.11621 | 0.14228 | 0.27931 | 0.042598 | -122.0251 | 0.047866 | 0.16478 | -0.056366 | 0.1377 | -122.0437
3225.0156 | 122.0718 | -0.07782 | 122.0673 | 1.4211e-13 | -0.04298 | -0.021396 | -0.080794 | -0.014119 | -0.0033715 | -0.013124 | 0.042657 | 0.02096 | 0.00767 | 0.049192 | -0.006181 | -0.067628 | -0.035222 | -0.090818 | 0.033814 | 0.069043 | 0.19233 | -0.13174 | 0.046835 | 0.059882 | -0.051772 | -0.029954 | 0.096121 | -0.12503 | -0.15957 | -0.053921 | -122.0334 | 0.010192 | -0.012998 | 0.040923 | -121.9982 | -121.8749 | -0.08175 | -122.0972 | 0.12466 | 0.026048 | 0.1078 | -121.9711 | -122.1923 | 0.11163 | 0.14686 | 0.27015 | 0.042598 | -122.199 | 0.047866 | 0.17394 | -0.047209 | 0.1377 | -122.2268
3226.7188 | 122.0078 | -0.022888 | 121.962 | 1.4211e-13 | -0.043194 | -0.022037 | -0.08058 | -0.014119 | -0.0033715 | -0.013124 | 0.042871 | 0.020746 | 0.00767 | 0.048978 | -0.0063946 | -0.06305 | -0.039801 | -0.10455 | 0.042971 | 0.073622 | 0.19691 | -0.13632 | 0.046835 | 0.055303 | -0.06093 | -0.039111 | 0.1007 | -0.12961 | -0.15957 | -0.11343 | -121.919 | -0.040162 | -0.081665 | 0.031767 | -121.8884 | -121.7651 | -0.13668 | -122.0011 | 0.069723 | -0.038042 | 0.09864 | -121.8613 | -122.0916 | 0.065859 | 0.09651 | 0.2198 | -0.016913 | -122.0983 | -0.016223 | 0.12359 | -0.10672 | 0.078191 | -122.1215
3228.4844 | 112.1429 | 0.013733 | 121.3898 | 1.4211e-13 | -0.04298 | -0.021609 | -0.080794 | -0.014546 | -0.0035853 | -0.013124 | 0.042657 | 0.021174 | 0.0072428 | 0.049192 | -0.0066084 | -0.053893 | -0.030644 | -0.095397 | 0.033814 | 0.078201 | 0.19691 | -0.12716 | 0.051413 | 0.064461 | -0.06093 | -0.029954 | 0.091543 | -0.12961 | -0.16415 | -0.14089 | -121.356 | -0.067626 | -0.10913 | 0.031765 | -121.3116 | -121.1929 | -0.17788 | -121.4197 | 0.03768 | -0.074663 | 0.10322 | -121.2982 | -121.5194 | 0.020081 | 0.064468 | 0.18318 | -0.044377 | -121.5169 | -0.043687 | 0.07781 | -0.14334 | 0.050728 | -121.5539
3230.1719 | 114.4043 | -0.032043 | 121.431 | 1.4211e-13 | -0.043194 | -0.021823 | -0.080794 | -0.014332 | -0.0035853 | -0.013124 | 0.042657 | 0.020746 | 0.00767 | 0.049192 | -0.006822 | -0.03558 | -0.007751 | -0.063349 | 0.061284 | 0.1011 | 0.22438 | -0.11342 | 0.046835 | 0.059882 | -0.065509 | -0.029954 | 0.096121 | -0.12961 | -0.15957 | -0.081382 | -121.3697 | -0.003537 | -0.031306 | 0.050076 | -121.3299 | -121.2066 | -0.12753 | -121.4609 | 0.078878 | -0.033466 | 0.094061 | -121.3348 | -121.5606 | 0.093327 | 0.13314 | 0.25642 | 0.024292 | -121.5444 | 0.002089 | 0.12816 | -0.097564 | 0.091925 | -121.5905
3231.9375 | 122.1725 | -0.073242 | 121.8475 | 1.4211e-13 | -0.042767 | -0.021609 | -0.080794 | -0.014546 | -0.0033715 | -0.013124 | 0.042657 | 0.020746 | 0.0074564 | 0.048978 | -0.0063946 | -0.058472 | -0.030644 | -0.08624 | 0.047549 | 0.087359 | 0.20607 | -0.09511 | 0.042256 | 0.064461 | -0.065509 | -0.025376 | 0.096121 | -0.12961 | -0.16415 | -0.021868 | -121.8 | 0.01477 | -0.012998 | 0.00887 | -121.7602 | -121.6415 | -0.090907 | -121.8729 | 0.1155 | 0.007733 | 0.09864 | -121.7514 | -121.9771 | 0.12079 | 0.1606 | 0.27931 | 0.042598 | -121.9426 | 0.047866 | 0.16936 | -0.056365 | 0.1377 | -122.0117
3233.7031 | 122.2229 | -0.091553 | 121.9025 | 1.4211e-13 | -0.04298 | -0.021609 | -0.080794 | -0.014119 | -0.0031579 | -0.028385 | 0.042657 | 0.02096 | 0.0074564 | 0.049192 | -0.0066084 | -0.058472 | -0.035222 | -0.095397 | 0.033814 | 0.078201 | 0.19233 | -0.12716 | 0.046835 | 0.059882 | -0.070087 | -0.034533 | 0.096121 | -0.12961 | -0.15957 | -0.035609 | -121.8687 | 0.033081 | -0.003844 | 0.031765 | -121.8243 | -121.7101 | -0.068017 | -121.937 | 0.13839 | 0.021466 | 0.089483 | -121.8063 | -122.0321 | 0.12537 | 0.16975 | 0.28388 | 0.056331 | -122.0296 | 0.05702 | 0.18767 | -0.038054 | 0.15143 | -122.062
3235.3906 | 119.5496 | -0.032043 | 121.4813 | 1.4211e-13 | -0.043408 | -0.021609 | -0.080794 | -0.014119 | -0.0033715 | -0.028385 | 0.042443 | 0.020533 | 0.00767 | 0.049405 | -0.0063946 | -0.040158 | -0.007751 | -0.067927 | 0.07502 | 0.1011 | 0.22896 | -0.10427 | 0.046835 | 0.059882 | -0.065509 | -0.029954 | 0.091543 | -0.13419 | -0.16873 | -0.072225 | -121.4063 | -0.008115 | -0.035884 | 0.036341 | -121.3802 | -121.2524 | -0.13669 | -121.5113 | 0.078878 | -0.033466 | 0.10322 | -121.3898 | -121.6155 | 0.10706 | 0.13314 | 0.261 | 0.024292 | -121.5856 | 0.002089 | 0.12359 | -0.10214 | 0.091925 | -121.6501
3237.1562 | 117.2012 | -0.045776 | 121.4767 | 1.4211e-13 | -0.043194 | -0.021609 | -0.080794 | -0.014546 | -0.0035853 | -0.020755 | 0.042657 | 0.020746 | 0.00767 | 0.048978 | -0.0066084 | -0.058472 | -0.026065 | -0.08624 | 0.042971 | 0.078201 | 0.20149 | -0.13174 | 0.042256 | 0.059882 | -0.06093 | -0.025376 | 0.091543 | -0.12503 | -0.15957 | -0.085965 | -121.4338 | -0.012696 | -0.040464 | 0.045501 | -121.3985 | -121.2753 | -0.11379 | -121.5021 | 0.088032 | -0.015154 | 0.09864 | -121.3852 | -121.6018 | 0.088747 | 0.12398 | 0.24726 | 0.019711 | -121.6085 | 0.0204 | 0.13732 | -0.079253 | 0.10566 | -121.6363
3238.9219 | 122.0215 | -0.086975 | 122.0306 | 1.4211e-13 | -0.043194 | -0.021396 | -0.080794 | -0.014119 | -0.0029443 | -0.020755 | 0.042657 | 0.020746 | 0.0072428 | 0.049192 | -0.0063946 | -0.017266 | 0.015142 | -0.045036 | 0.079598 | 0.12399 | 0.23812 | -0.053899 | 0.046835 | 0.055303 | -0.056351 | -0.025376 | 0.091543 | -0.12503 | -0.15957 | 0.033076 | -121.951 | 0.069709 | 0.041939 | 0.008863 | -121.9066 | -121.7925 | -0.072595 | -122.056 | 0.13381 | 0.030624 | 0.10322 | -121.9391 | -122.1557 | 0.16657 | 0.21097 | 0.32509 | 0.10212 | -122.0845 | 0.061599 | 0.17852 | -0.038054 | 0.14228 | -122.1902
3240.6875 | 122.2961 | -0.050354 | 121.4035 | 1.4211e-13 | -0.043408 | -0.021609 | -0.080366 | -0.013905 | -0.0033715 | -0.013124 | 0.042657 | 0.020746 | 0.00767 | 0.049405 | -0.006822 | -0.017266 | 0.001407 | -0.045036 | 0.07502 | 0.12399 | 0.24269 | -0.058478 | 0.046835 | 0.06904 | -0.06093 | -0.034533 | 0.086964 | -0.12961 | -0.16415 | -0.008124 | -121.3285 | 0.033088 | 0.005318 | 0.013442 | -121.2795 | -121.1608 | -0.11379 | -121.438 | 0.097189 | -0.010576 | 0.10322 | -121.3165 | -121.5331 | 0.12537 | 0.17434 | 0.29305 | 0.051761 | -121.462 | 0.015821 | 0.13732 | -0.079253 | 0.11939 | -121.5677
3242.4531 | 122.2092 | -0.073242 | 121.6599 | 1.4211e-13 | -0.043408 | -0.021396 | -0.08058 | -0.013905 | -0.0035853 | -0.013124 | 0.042657 | 0.021174 | 0.0074564 | 0.048978 | -0.0063946 | -0.021844 | 0.001407 | -0.035879 | 0.079598 | 0.12399 | 0.23812 | -0.063057 | 0.046835 | 0.064461 | -0.065509 | -0.029954 | 0.091543 | -0.13876 | -0.15499 | 0.010185 | -121.5803 | 0.051398 | 0.037363 | 0.027178 | -121.5359 | -121.4217 | -0.081749 | -121.6898 | 0.12008 | 0.007733 | 0.089482 | -121.5683 | -121.7986 | 0.15284 | 0.19723 | 0.31136 | 0.074649 | -121.7229 | 0.043288 | 0.16479 | -0.065523 | 0.1377 | -121.8148
3244.1562 | 121.669 | -0.11444 | 121.9116 | 1.4211e-13 | -0.043621 | -0.021609 | -0.080794 | -0.014332 | -0.0033715 | -0.028385 | 0.042657 | 0.020746 | 0.0074564 | 0.049192 | -0.0063946 | -0.06305 | -0.030644 | -0.090818 | 0.042971 | 0.08278 | 0.19691 | -0.13174 | 0.046835 | 0.059882 | -0.065509 | -0.034533 | 0.086964 | -0.10671 | -0.16873 | -0.0173 | -121.8687 | 0.051391 | 0.023623 | 0.040923 | -121.8288 | -121.7147 | -0.054287 | -121.9462 | 0.16128 | 0.048932 | 0.10322 | -121.8247 | -122.0183 | 0.15741 | 0.19722 | 0.31135 | 0.083797 | -122.0434 | 0.079908 | 0.20141 | 0.007727 | 0.17432 | -122.0803
3245.9219 | 121.6461 | -0.10071 | 121.5088 | 1.4211e-13 | -0.043621 | -0.021823 | -0.08058 | -0.014332 | -0.0037989 | -0.0054937 | 0.042657 | 0.020746 | 0.0074564 | 0.049192 | -0.0063946 | -0.049315 | -0.021486 | -0.081662 | 0.042971 | 0.091937 | 0.21522 | -0.118 | 0.042256 | 0.06904 | -0.065509 | -0.029954 | 0.086964 | -0.12045 | -0.16873 | -0.017296 | -121.4658 | 0.051393 | 0.019046 | 0.036342 | -121.4169 | -121.2936 | -0.06802 | -121.5387 | 0.14296 | 0.035199 | 0.10322 | -121.4218 | -121.6292 | 0.14368 | 0.19265 | 0.31593 | 0.079222 | -121.6268 | 0.070754 | 0.18767 | -0.019742 | 0.16975 | -121.6775
3247.7031 | 121.4584 | -0.12817 | 121.8933 | 1.4211e-13 | -0.043408 | -0.021609 | -0.080366 | -0.014119 | -0.0037989 | -0.013124 | 0.042657 | 0.020746 | 0.00767 | 0.049192 | -0.0066084 | -0.03558 | 0.001407 | -0.072505 | 0.056706 | 0.1011 | 0.22438 | -0.085952 | 0.042256 | 0.064461 | -0.06093 | -0.029954 | 0.086964 | -0.12961 | -0.15499 | 0.042222 | -121.8366 | 0.092594 | 0.055669 | 0.013447 | -121.7922 | -121.6689 | -0.026817 | -121.9233 | 0.17043 | 0.067244 | 0.094061 | -121.8063 | -122.0229 | 0.18488 | 0.22927 | 0.35256 | 0.12958 | -121.9793 | 0.09822 | 0.21514 | -0.001433 | 0.19264 | -122.0483
3249.4844 | 122.1954 | -0.073242 | 122.1497 | 1.4211e-13 | -0.043408 | -0.021396 | -0.080794 | -0.014119 | -0.0033715 | -0.013124 | 0.042871 | 0.020746 | 0.0074564 | 0.049192 | -0.0066084 | -0.017266 | 0.010564 | -0.054192 | 0.070441 | 0.11025 | 0.23812 | -0.031005 | 0.046835 | 0.059882 | -0.06093 | -0.034533 | 0.096121 | -0.12961 | -0.16415 | 0.042237 | -122.0792 | 0.055976 | 0.01905 | -0.023187 | -122.0394 | -121.9115 | -0.090907 | -122.1842 | 0.12008 | 0.012312 | 0.10322 | -122.0535 | -122.2793 | 0.14368 | 0.1835 | 0.31136 | 0.083806 | -122.1807 | 0.038709 | 0.16936 | -0.056365 | 0.13312 | -122.3138
3251.1719 | 121.6095 | -0.11444 | 121.8613 | 1.4211e-13 | -0.043835 | -0.021396 | -0.080794 | -0.014332 | -0.0033715 | -0.028385 | 0.042443 | 0.02096 | 0.0072428 | 0.049405 | -0.0063946 | -0.017266 | 0.005985 | -0.049614 | 0.088755 | 0.11941 | 0.24727 | -0.044742 | 0.046835 | 0.059882 | -0.056351 | -0.039111 | 0.096121 | -0.12503 | -0.16415 | 0.069699 | -121.7725 | 0.097175 | 0.064827 | -0.004872 | -121.7419 | -121.614 | -0.049708 | -121.9004 | 0.16128 | 0.05809 | 0.1078 | -121.7651 | -121.9863 | 0.2032 | 0.23385 | 0.36172 | 0.12043 | -121.906 | 0.07533 | 0.21056 | -0.010588 | 0.17432 | -122.0254
3252.9844 | 122.2916 | -0.073242 | 121.962 | 1.4211e-13 | -0.043835 | -0.021609 | -0.080794 | -0.014546 | -0.0031579 | -0.0054937 | 0.042443 | 0.020746 | 0.007029 | 0.049192 | -0.0063946 | -0.021844 | 0.015142 | -0.049614 | 0.079598 | 0.12399 | 0.23812 | -0.049321 | 0.046835 | 0.059882 | -0.06093 | -0.034533 | 0.086964 | -0.12961 | -0.16415 | 0.023921 | -121.8824 | 0.051398 | 0.023628 | -0.000293 | -121.838 | -121.7239 | -0.090907 | -121.9965 | 0.12008 | 0.012312 | 0.10322 | -121.875 | -122.0916 | 0.15284 | 0.19723 | 0.31136 | 0.088384 | -122.0113 | 0.038709 | 0.16021 | -0.056365 | 0.13312 | -122.1261
3256.1875 | 121.9482 | -0.10529 | 122.1497 | 1.4211e-13 | -0.043408 | -0.021609 | -0.080794 | -0.014332 | -0.0031579 | -0.028385 | 0.042657 | 0.020746 | 0.0072428 | 0.049405 | -0.0063946 | -0.031001 | 0.001407 | -0.05877 | 0.070441 | 0.11483 | 0.24269 | -0.081373 | 0.046835 | 0.059882 | -0.056351 | -0.034533 | 0.096121 | -0.13419 | -0.16415 | 0.023913 | -122.0792 | 0.074285 | 0.046516 | 0.022603 | -122.0348 | -121.907 | -0.058863 | -122.1842 | 0.15212 | 0.048935 | 0.1078 | -122.0535 | -122.2838 | 0.17573 | 0.22012 | 0.34798 | 0.10669 | -122.231 | 0.070753 | 0.20141 | -0.0289 | 0.16517 | -122.3138
3260.4844 | 121.9528 | -0.086975 | 122.2 | 1.4211e-13 | -0.043621 | -0.021396 | -0.080794 | -0.013905 | -0.0031579 | -0.028385 | 0.042871 | 0.020533 | 0.0072428 | 0.049192 | -0.0063946 | -0.021844 | 0.001407 | -0.045036 | 0.070441 | 0.11941 | 0.24727 | -0.035584 | 0.051413 | 0.059882 | -0.056351 | -0.039111 | 0.096121 | -0.13876 | -0.16415 | 0.051391 | -122.1296 | 0.065131 | 0.041939 | -0.009452 | -122.0806 | -121.9527 | -0.077174 | -122.2391 | 0.13839 | 0.030624 | 0.1078 | -122.1039 | -122.3388 | 0.15742 | 0.20639 | 0.33425 | 0.088382 | -122.2356 | 0.047864 | 0.1831 | -0.05179 | 0.14686 | -122.3642
3266.3125 | 121.4767 | -0.091553 | 122.0581 | 1.4211e-13 | -0.043835 | -0.021609 | -0.081007 | -0.014332 | -0.0033715 | -0.013124 | 0.04223 | 0.020533 | 0.0074564 | 0.049619 | -0.0066084 | -0.021844 | 0.005985 | -0.049614 | 0.07502 | 0.12399 | 0.24727 | -0.076794 | 0.046835 | 0.06904 | -0.06093 | -0.034533 | 0.096121 | -0.12961 | -0.15957 | 0.014759 | -121.9831 | 0.069709 | 0.041939 | 0.02718 | -121.9341 | -121.8108 | -0.068017 | -122.0926 | 0.13839 | 0.030623 | 0.09864 | -121.962 | -122.1877 | 0.16657 | 0.21554 | 0.33883 | 0.097538 | -122.1349 | 0.05702 | 0.18767 | -0.038054 | 0.16059 | -122.2177
3268 | 122.2321 | -0.07782 | 122.1863 | 1.4211e-13 | -0.043835 | -0.021396 | -0.08058 | -0.014332 | -0.0031579 | -0.013124 | 0.042443 | 0.020319 | 0.0074564 | 0.049192 | -0.006822 | -0.026423 | 0.010564 | -0.045036 | 0.070441 | 0.12399 | 0.23812 | -0.063057 | 0.046835 | 0.064461 | -0.065509 | -0.029954 | 0.091543 | -0.12961 | -0.16415 | 0.014763 | -122.1158 | 0.051397 | 0.032784 | 0.018021 | -122.0623 | -121.9482 | -0.086329 | -122.2162 | 0.12466 | 0.012311 | 0.09864 | -122.0947 | -122.3159 | 0.14826 | 0.20181 | 0.31594 | 0.088384 | -122.2493 | 0.047866 | 0.16936 | -0.051787 | 0.14228 | -122.3504
3269.6875 | 121.5912 | -0.11902 | 122.2595 | 1.4211e-13 | -0.043835 | -0.021823 | -0.080794 | -0.014119 | -0.0033715 | -0.028385 | 0.042657 | 0.020746 | 0.0072428 | 0.049405 | -0.0063946 | -0.012688 | 0.010564 | -0.049614 | 0.070441 | 0.11483 | 0.24269 | -0.031005 | 0.046835 | 0.059882 | -0.056351 | -0.025376 | 0.086964 | -0.11587 | -0.16415 | 0.088014 | -122.1891 | 0.10633 | 0.069405 | -0.018609 | -122.1447 | -122.0168 | -0.04513 | -122.2849 | 0.16585 | 0.062668 | 0.1078 | -122.1726 | -122.3754 | 0.18946 | 0.23385 | 0.36171 | 0.12958 | -122.2905 | 0.093643 | 0.20598 | 0.003147 | 0.1789 | -122.4237
3271.4531 | 121.7422 | -0.1236 | 122.2549 | 1.4211e-13 | -0.043621 | -0.021609 | -0.080794 | -0.014332 | -0.0035853 | -0.0054937 | 0.042443 | 0.020746 | 0.0074564 | 0.049833 | -0.0066084 | -0.021844 | 0.005985 | -0.049614 | 0.065863 | 0.11941 | 0.24269 | -0.058478 | 0.046835 | 0.064461 | -0.06093 | -0.034533 | 0.096121 | -0.12961 | -0.16415 | 0.065118 | -122.1891 | 0.10175 | 0.073982 | 0.008864 | -122.1355 | -122.0122 | -0.040553 | -122.2895 | 0.17043 | 0.062666 | 0.10322 | -122.1588 | -122.3846 | 0.18946 | 0.24301 | 0.36629 | 0.12958 | -122.3134 | 0.089063 | 0.21972 | -0.006011 | 0.18806 | -122.4191
3273.2188 | 121.7514 | -0.10529 | 122.2275 | 1.4211e-13 | -0.044049 | -0.021396 | -0.08058 | -0.014546 | -0.0031579 | -0.0054937 | 0.042443 | 0.020319 | 0.0074564 | 0.049619 | -0.0066084 | -0.026423 | 0.010564 | -0.049614 | 0.084176 | 0.12399 | 0.24269 | -0.012689 | 0.055992 | 0.059882 | -0.065509 | -0.025376 | 0.086964 | -0.13419 | -0.16873 | 0.092597 | -122.1433 | 0.078863 | 0.055672 | -0.036925 | -122.1035 | -121.9848 | -0.063442 | -122.2529 | 0.16128 | 0.039777 | 0.10322 | -122.1405 | -122.3617 | 0.18946 | 0.22928 | 0.34798 | 0.11585 | -122.2402 | 0.07991 | 0.19225 | -0.0289 | 0.16517 | -122.3962
3274.9844 | 121.6187 | -0.09613 | 121.7377 | 1.4211e-13 | -0.044049 | -0.021609 | -0.08058 | -0.014332 | -0.0035853 | -0.013124 | 0.042443 | 0.020533 | 0.0074564 | 0.049619 | -0.006822 | -0.026423 | 0.001407 | -0.049614 | 0.07502 | 0.11941 | 0.23812 | -0.072215 | 0.051413 | 0.059882 | -0.065509 | -0.025376 | 0.096121 | -0.11587 | -0.16415 | 0.023915 | -121.6627 | 0.069707 | 0.046516 | 0.022601 | -121.6183 | -121.4996 | -0.068019 | -121.763 | 0.14754 | 0.030621 | 0.09864 | -121.6416 | -121.8535 | 0.17115 | 0.21554 | 0.33425 | 0.097537 | -121.8099 | 0.070754 | 0.19225 | -0.019742 | 0.15601 | -121.9018
3276.75 | 121.7834 | -0.10529 | 122.2458 | 1.4211e-13 | -0.043621 | -0.021823 | -0.080794 | -0.014332 | -0.0031579 | -0.020755 | 0.042443 | 0.021174 | 0.0074564 | 0.049833 | -0.0063946 | -0.021844 | 0.010564 | -0.045036 | 0.07502 | 0.11483 | 0.24269 | -0.049321 | 0.046835 | 0.055303 | -0.06093 | -0.029954 | 0.096121 | -0.12961 | -0.16873 | 0.055965 | -122.1708 | 0.083442 | 0.06025 | 0.004285 | -122.131 | -122.0031 | -0.063442 | -122.2757 | 0.15212 | 0.044356 | 0.1078 | -122.1497 | -122.3754 | 0.18031 | 0.22012 | 0.34798 | 0.11585 | -122.2951 | 0.075332 | 0.20141 | -0.024321 | 0.16059 | -122.4145
3278.4531 | 122.374 | -0.07782 | 122.2229 | 1.4211e-13 | -0.044049 | -0.021609 | -0.080794 | -0.014119 | -0.0033715 | -0.028385 | 0.042443 | 0.020533 | 0.0074564 | 0.049405 | -0.0063946 | -0.017266 | 0.001407 | -0.035879 | 0.070441 | 0.12399 | 0.24269 | -0.049321 | 0.051413 | 0.059882 | -0.06093 | -0.025376 | 0.1007 | -0.12503 | -0.16873 | 0.028499 | -122.1525 | 0.060554 | 0.041941 | 0.013442 | -122.0989 | -121.9802 | -0.090908 | -122.2483 | 0.12923 | 0.01689 | 0.1078 | -122.1222 | -122.3479 | 0.14826 | 0.20181 | 0.32051 | 0.079227 | -122.2722 | 0.052444 | 0.17852 | -0.047209 | 0.1377 | -122.3916
3280.2188 | 121.9437 | -0.10529 | 122.2412 | 1.4211e-13 | -0.043621 | -0.021609 | -0.080794 | -0.014332 | -0.0033715 | -0.028385 | 0.042443 | 0.020746 | 0.0074564 | 0.049833 | -0.006822 | -0.017266 | 0.001407 | -0.040457 | 0.065863 | 0.11941 | 0.23812 | -0.003531 | 0.042256 | 0.055303 | -0.065509 | -0.025376 | 0.096121 | -0.13419 | -0.16415 | 0.10175 | -122.1753 | 0.08802 | 0.064829 | -0.036926 | -122.1218 | -122.0031 | -0.058863 | -122.2666 | 0.14754 | 0.039777 | 0.09864 | -122.1451 | -122.3754 | 0.17115 | 0.2247 | 0.3434 | 0.10669 | -122.2447 | 0.07991 | 0.20141 | -0.0289 | 0.16059 | -122.4054
3281.9219 | 122.3602 | -0.059509 | 122.2183 | 1.4211e-13 | -0.043835 | -0.021823 | -0.080794 | -0.014546 | -0.0035853 | -0.020755 | 0.042657 | 0.020533 | 0.0074564 | 0.049405 | -0.006822 | -0.021844 | 0.005985 | -0.040457 | 0.084176 | 0.12399 | 0.24269 | -0.035584 | 0.051413 | 0.064461 | -0.051772 | -0.029954 | 0.096121 | -0.12961 | -0.15957 | 0.023925 | -122.1341 | 0.037665 | 0.019052 | -0.004873 | -122.0943 | -121.9756 | -0.10006 | -122.2483 | 0.11092 | 0.007737 | 0.1078 | -122.1222 | -122.3479 | 0.14369 | 0.1835 | 0.3022 | 0.065494 | -122.2539 | 0.029555 | 0.15563 | -0.070098 | 0.12397 | -122.3779
3283.7031 | 122.3969 | -0.07782 | 122.2183 | 1.4211e-13 | -0.044049 | -0.021823 | -0.080794 | -0.014332 | -0.0033715 | -0.020755 | 0.042657 | 0.020746 | 0.0074564 | 0.049619 | -0.006822 | -0.008109 | 0.005985 | -0.040457 | 0.079598 | 0.11483 | 0.23812 | -0.017268 | 0.051413 | 0.059882 | -0.06093 | -0.034533 | 0.096121 | -0.12961 | -0.16873 | 0.060552 | -122.1387 | 0.069711 | 0.037363 | -0.023189 | -122.1035 | -121.9802 | -0.090908 | -122.2529 | 0.12923 | 0.01689 | 0.1078 | -122.1222 | -122.3479 | 0.15742 | 0.19265 | 0.31594 | 0.083805 | -122.2356 | 0.043287 | 0.17394 | -0.051787 | 0.1377 | -122.3871
3285.4219 | 122.0306 | -0.11444 | 122.2824 | 1.4211e-13 | -0.044049 | -0.021823 | -0.080794 | -0.014332 | -0.0031579 | -0.020755 | 0.04223 | 0.020533 | 0.0074564 | 0.049833 | -0.006822 | -0.017266 | 0.005985 | -0.045036 | 0.070441 | 0.11941 | 0.23354 | -0.081373 | 0.051413 | 0.064461 | -0.065509 | -0.025376 | 0.096121 | -0.12503 | -0.15499 | 0.033068 | -122.212 | 0.097175 | 0.069405 | 0.036337 | -122.163 | -122.0489 | -0.04055 | -122.3078 | 0.16585 | 0.048932 | 0.089482 | -122.1863 | -122.4074 | 0.18488 | 0.23385 | 0.34798 | 0.12043 | -122.3638 | 0.089065 | 0.21056 | -0.010588 | 0.1789 | -122.4374
3287.1875 | 122.0673 | -0.11902 | 122.2458 | 1.4211e-13 | -0.043835 | -0.021823 | -0.08058 | -0.014546 | -0.0037989 | -0.020755 | 0.042871 | 0.02096 | 0.0072428 | 0.050046 | -0.006822 | -0.021844 | 0.005985 | -0.045036 | 0.079598 | 0.12399 | 0.23812 | -0.049321 | 0.046835 | 0.064461 | -0.06093 | -0.029954 | 0.1007 | -0.12503 | -0.16415 | 0.069698 | -122.1662 | 0.097175 | 0.073983 | 0.004285 | -122.1218 | -122.0077 | -0.04513 | -122.2757 | 0.16585 | 0.058089 | 0.10322 | -122.1451 | -122.3708 | 0.19862 | 0.24301 | 0.35714 | 0.125 | -122.2951 | 0.089065 | 0.21972 | -0.00601 | 0.18348 | -122.4099
3288.8906 | 122.3785 | -0.09613 | 122.2321 | 1.4211e-13 | -0.043835 | -0.021823 | -0.080794 | -0.014332 | -0.0033715 | -0.020755 | 0.042443 | 0.020533 | 0.0074564 | 0.049833 | -0.006822 | -0.021844 | 0.001407 | -0.045036 | 0.079598 | 0.11941 | 0.23354 | -0.049321 | 0.046835 | 0.064461 | -0.056351 | -0.034533 | 0.1007 | -0.13419 | -0.15957 | 0.046809 | -122.1525 | 0.074286 | 0.051094 | 0.004285 | -122.1126 | -121.9985 | -0.06344 | -122.2666 | 0.14297 | 0.039779 | 0.10322 | -122.1314 | -122.3662 | 0.17573 | 0.21554 | 0.32967 | 0.097537 | -122.2814 | 0.061597 | 0.19683 | -0.038056 | 0.16059 | -122.3916
3290.6719 | 122.374 | -0.09613 | 122.2137 | 1.4211e-13 | -0.044049 | -0.021609 | -0.08058 | -0.014332 | -0.0035853 | -0.020755 | 0.042443 | 0.020746 | 0.0072428 | 0.049833 | -0.0066084 | -0.021844 | 0.010564 | -0.049614 | 0.070441 | 0.12399 | 0.23812 | -0.017268 | 0.046835 | 0.059882 | -0.06093 | -0.025376 | 0.091543 | -0.12961 | -0.15499 | 0.078862 | -122.1433 | 0.074286 | 0.046516 | -0.032346 | -122.0898 | -121.9756 | -0.058861 | -122.2391 | 0.14297 | 0.0352 | 0.094061 | -122.1222 | -122.3434 | 0.16657 | 0.22012 | 0.33425 | 0.10669 | -122.231 | 0.070754 | 0.18767 | -0.033477 | 0.15601 | -122.3687
3292.3594 | 121.8613 | -0.11444 | 121.6599 | 1.4211e-13 | -0.044049 | -0.021609 | -0.080794 | -0.013905 | -0.0035853 | -0.036016 | 0.042443 | 0.020319 | 0.007029 | 0.050046 | -0.006822 | -0.021844 | 0.005985 | -0.045036 | 0.084176 | 0.11483 | 0.24269 | -0.040163 | 0.051413 | 0.059882 | -0.070087 | -0.029954 | 0.096121 | -0.11129 | -0.16873 | 0.074278 | -121.5757 | 0.092597 | 0.069405 | -0.004873 | -121.545 | -121.4172 | -0.054287 | -121.6898 | 0.16585 | 0.044354 | 0.098641 | -121.5637 | -121.7711 | 0.19862 | 0.22927 | 0.35714 | 0.12043 | -121.7 | 0.084487 | 0.21056 | 0.003148 | 0.17432 | -121.8286
3294.1094 | 122.374 | -0.082397 | 122.2458 | 1.4211e-13 | -0.044049 | -0.021609 | -0.08058 | -0.014546 | -0.0037989 | -0.028385 | 0.042443 | 0.020746 | 0.007029 | 0.050046 | -0.006822 | -0.021844 | 0.010564 | -0.045036 | 0.07502 | 0.11025 | 0.24269 | -0.00811 | 0.051413 | 0.059882 | -0.051772 | -0.034533 | 0.1007 | -0.12961 | -0.15499 | 0.074287 | -122.1708 | 0.060553 | 0.037361 | -0.036926 | -122.1355 | -122.0031 | -0.072594 | -122.2803 | 0.13381 | 0.030625 | 0.10322 | -122.1451 | -122.3754 | 0.15742 | 0.19265 | 0.32509 | 0.092961 | -122.2539 | 0.047864 | 0.1831 | -0.04721 | 0.14228 | -122.4008
3295.8125 | 122.4197 | -0.059509 | 122.2595 | 1.4211e-13 | -0.044049 | -0.021396 | -0.080794 | -0.014546 | -0.0035853 | -0.028385 | 0.04223 | 0.020533 | 0.0072428 | 0.049833 | -0.006822 | -0.012688 | 0.005985 | -0.045036 | 0.070441 | 0.12857 | 0.23812 | -0.072215 | 0.046835 | 0.064461 | -0.056351 | -0.029954 | 0.091543 | -0.12503 | -0.16415 | -0.012706 | -122.1891 | 0.046821 | 0.014473 | 0.027179 | -122.131 | -122.0214 | -0.10464 | -122.2895 | 0.10634 | 0.003158 | 0.1078 | -122.168 | -122.3846 | 0.12995 | 0.18808 | 0.29763 | 0.065494 | -122.3317 | 0.029555 | 0.15105 | -0.06552 | 0.12397 | -122.4237
3297.5625 | 122.4106 | -0.068665 | 122.2549 | 1.4211e-13 | -0.043835 | -0.021609 | -0.08058 | -0.014332 | -0.0033715 | -0.020755 | 0.04223 | 0.020319 | 0.007029 | 0.049833 | -0.006822 | -0.021844 | 0.005985 | -0.049614 | 0.07502 | 0.12399 | 0.23812 | -0.031005 | 0.046835 | 0.064461 | -0.056351 | -0.029954 | 0.091543 | -0.10671 | -0.15957 | 0.03766 | -122.1799 | 0.046821 | 0.019051 | -0.018609 | -122.131 | -122.0168 | -0.090905 | -122.2849 | 0.1155 | 0.012314 | 0.10322 | -122.1634 | -122.3617 | 0.14369 | 0.19266 | 0.30678 | 0.07465 | -122.2859 | 0.038711 | 0.16021 | -0.038049 | 0.13313 | -122.4145
3299.3281 | 122.4564 | -0.073242 | 122.2504 | 1.4211e-13 | -0.044262 | -0.021609 | -0.08058 | -0.014332 | -0.0035853 | -0.028385 | 0.04223 | 0.020105 | 0.007029 | 0.050046 | -0.006822 | -0.017266 | 0.010564 | -0.040457 | 0.07502 | 0.11941 | 0.24269 | -0.035584 | 0.042256 | 0.06904 | -0.06093 | -0.025376 | 0.096121 | -0.13419 | -0.15957 | 0.037658 | -122.1753 | 0.055976 | 0.032785 | -0.004873 | -122.131 | -122.0077 | -0.086328 | -122.2757 | 0.1155 | 0.012312 | 0.09864 | -122.1542 | -122.3846 | 0.14826 | 0.19265 | 0.31594 | 0.083806 | -122.2859 | 0.047866 | 0.16936 | -0.060944 | 0.14228 | -122.4099
3301.1094 | 122.3785 | -0.091553 | 122.2595 | 1.4211e-13 | -0.044049 | -0.021609 | -0.080794 | -0.014546 | -0.0037989 | -0.020755 | 0.04223 | 0.020319 | 0.0068154 | 0.050046 | -0.0066084 | -0.017266 | 0.010564 | -0.045036 | 0.079598 | 0.11941 | 0.24269 | -0.049321 | 0.042256 | 0.064461 | -0.06093 | -0.025376 | 0.1007 | -0.12503 | -0.16873 | 0.042232 | -122.1799 | 0.074287 | 0.046517 | 0.004285 | -122.1401 | -122.0168 | -0.077175 | -122.2849 | 0.13381 | 0.030623 | 0.1078 | -122.1588 | -122.3846 | 0.17115 | 0.21096 | 0.33425 | 0.10212 | -122.3088 | 0.066177 | 0.19225 | -0.033476 | 0.15601 | -122.4282
3302.8125 | 122.0535 | -0.11902 | 121.8796 | 1.4211e-13 | -0.043835 | -0.021823 | -0.08058 | -0.01476 | -0.0037989 | -0.028385 | 0.042657 | 0.020533 | 0.0074564 | 0.049833 | -0.0070356 | -0.017266 | 0.010564 | -0.045036 | 0.07502 | 0.11025 | 0.23354 | -0.00811 | 0.046835 | 0.064461 | -0.06093 | -0.029954 | 0.10528 | -0.13419 | -0.15957 | 0.11091 | -121.8046 | 0.10175 | 0.073983 | -0.036926 | -121.7693 | -121.646 | -0.040551 | -121.9095 | 0.16585 | 0.058089 | 0.09864 | -121.7743 | -122.0138 | 0.19404 | 0.22927 | 0.35256 | 0.12958 | -121.8877 | 0.089065 | 0.2243 | -0.015167 | 0.18348 | -122.0391
3304.5781 | 121.8475 | -0.11444 | 121.5637 | 1.4211e-13 | -0.044262 | -0.021823 | -0.08058 | -0.014332 | -0.0035853 | -0.020755 | 0.042443 | 0.020105 | 0.0072428 | 0.05026 | -0.0070356 | -0.017266 | 0.010564 | -0.049614 | 0.070441 | 0.11941 | 0.23812 | -0.012689 | 0.046835 | 0.059882 | -0.056351 | -0.025376 | 0.1007 | -0.12961 | -0.16873 | 0.10175 | -121.4933 | 0.097175 | 0.064827 | -0.036925 | -121.4443 | -121.3256 | -0.054287 | -121.5891 | 0.16128 | 0.05809 | 0.11238 | -121.463 | -121.6933 | 0.18488 | 0.23385 | 0.35256 | 0.12501 | -121.5764 | 0.089065 | 0.21514 | -0.015166 | 0.17432 | -121.7324
3306.3594 | 122.4152 | -0.07782 | 122.2229 | 1.4211e-13 | -0.044262 | -0.021396 | -0.08058 | -0.01476 | -0.0037989 | -0.028385 | 0.042657 | 0.020319 | 0.0074564 | 0.050046 | -0.006822 | -0.017266 | 0.005985 | -0.054192 | 0.07502 | 0.12399 | 0.24269 | -0.021847 | 0.042256 | 0.064461 | -0.06093 | -0.025376 | 0.096121 | -0.12961 | -0.16415 | 0.055973 | -122.1479 | 0.060554 | 0.023628 | -0.032345 | -122.0989 | -121.9802 | -0.086329 | -122.2483 | 0.12008 | 0.01689 | 0.10322 | -122.1268 | -122.3525 | 0.15284 | 0.20181 | 0.32051 | 0.083805 | -122.2447 | 0.052444 | 0.17394 | -0.051787 | 0.14228 | -122.387
3308.125 | 121.8338 | -0.10529 | 121.6965 | 1.4211e-13 | -0.04469 | -0.021182 | -0.08058 | -0.014546 | -0.0035853 | -0.020755 | 0.042657 | 0.020746 | 0.0072428 | 0.050474 | -0.0066084 | -0.017266 | 0.005985 | -0.054192 | 0.070441 | 0.11483 | 0.24269 | -0.026426 | 0.055992 | 0.059882 | -0.056351 | -0.034533 | 0.091543 | -0.13876 | -0.16415 | 0.07886 | -121.626 | 0.08802 | 0.051094 | -0.027766 | -121.5816 | -121.4538 | -0.058863 | -121.731 | 0.16128 | 0.048935 | 0.1078 | -121.6049 | -121.8352 | 0.17573 | 0.22012 | 0.34798 | 0.11127 | -121.7229 | 0.070753 | 0.19683 | -0.033479 | 0.16517 | -121.8606
3309.8906 | 122.4152 | -0.09613 | 122.2824 | 1.4211e-13 | -0.044476 | -0.021396 | -0.080794 | -0.014332 | -0.0035853 | -0.028385 | 0.04223 | 0.020533 | 0.0074564 | 0.050046 | -0.006822 | -0.021844 | 0.010564 | -0.045036 | 0.079598 | 0.11941 | 0.24269 | -0.00811 | 0.051413 | 0.059882 | -0.065509 | -0.025376 | 0.1007 | -0.11129 | -0.15957 | 0.08802 | -122.2028 | 0.074286 | 0.051094 | -0.036926 | -122.163 | -122.0397 | -0.06344 | -122.3078 | 0.14754 | 0.030621 | 0.094061 | -122.1817 | -122.3937 | 0.17573 | 0.21554 | 0.33882 | 0.10669 | -122.2905 | 0.070754 | 0.19683 | -0.015163 | 0.15601 | -122.442
3311.5938 | 122.4426 | -0.068665 | 122.049 | 1.4211e-13 | -0.044262 | -0.021396 | -0.08058 | -0.014332 | -0.0035853 | -0.036016 | 0.042443 | 0.020105 | 0.007029 | 0.050046 | -0.0070356 | -0.021844 | 0.015142 | -0.040457 | 0.07502 | 0.11941 | 0.23354 | -0.021847 | 0.046835 | 0.059882 | -0.065509 | -0.029954 | 0.096121 | -0.12961 | -0.16873 | 0.046818 | -121.9739 | 0.046821 | 0.028208 | -0.01861 | -121.9295 | -121.8154 | -0.10006 | -122.0789 | 0.1155 | 0.003156 | 0.10322 | -121.9528 | -122.1786 | 0.14369 | 0.18808 | 0.3022 | 0.083807 | -122.0708 | 0.038711 | 0.16479 | -0.060942 | 0.12855 | -122.2177
3313.2812 | 122.4152 | -0.086975 | 122.3099 | 1.4211e-13 | -0.044476 | -0.021609 | -0.080366 | -0.014546 | -0.0040125 | -0.020755 | 0.042443 | 0.020105 | 0.007029 | 0.050046 | -0.006822 | -0.021844 | 0.005985 | -0.045036 | 0.070441 | 0.11483 | 0.23812 | -0.012689 | 0.051413 | 0.059882 | -0.06093 | -0.025376 | 0.1007 | -0.12961 | -0.15957 | 0.074286 | -122.2394 | 0.065131 | 0.041939 | -0.032347 | -122.195 | -122.0718 | -0.072595 | -122.3353 | 0.13839 | 0.026045 | 0.09864 | -122.2092 | -122.4395 | 0.15742 | 0.20181 | 0.32509 | 0.09296 | -122.3226 | 0.061599 | 0.18767 | -0.042632 | 0.14686 | -122.4694
3315.0469 | 122.0078 | -0.10071 | 122.3328 | 1.4211e-13 | -0.044262 | -0.021609 | -0.080366 | -0.014546 | -0.0035853 | -0.043646 | 0.04223 | 0.020533 | 0.0074564 | 0.050474 | -0.006822 | -0.021844 | 0.015142 | -0.054192 | 0.07502 | 0.11025 | 0.23812 | -0.026426 | 0.042256 | 0.059882 | -0.06093 | -0.025376 | 0.1007 | -0.12961 | -0.16873 | 0.074282 | -122.2577 | 0.078864 | 0.046516 | -0.027766 | -122.2225 | -122.0946 | -0.06802 | -122.3581 | 0.14296 | 0.039778 | 0.1078 | -122.2321 | -122.4624 | 0.17573 | 0.21096 | 0.33882 | 0.11585 | -122.3592 | 0.075332 | 0.20141 | -0.028899 | 0.16059 | -122.5015
3316.8125 | 122.4106 | -0.082397 | 122.2916 | 1.4211e-13 | -0.044476 | -0.021182 | -0.080794 | -0.014332 | -0.0040125 | -0.013124 | 0.04223 | 0.020319 | 0.007029 | 0.05026 | -0.006822 | -0.008109 | 0.010564 | -0.054192 | 0.07502 | 0.11483 | 0.23812 | 0.005627 | 0.051413 | 0.055303 | -0.065509 | -0.034533 | 0.10528 | -0.12961 | -0.16415 | 0.088024 | -122.2165 | 0.074288 | 0.028205 | -0.059819 | -122.1767 | -122.0534 | -0.081752 | -122.3261 | 0.13381 | 0.016888 | 0.09864 | -122.1863 | -122.4212 | 0.15742 | 0.19723 | 0.32051 | 0.092961 | -122.2859 | 0.047864 | 0.18768 | -0.04721 | 0.1377 | -122.4557
3318.5781 | 122.3099 | -0.11902 | 122.319 | 1.4211e-13 | -0.04469 | -0.021609 | -0.080366 | -0.014546 | -0.0037989 | -0.028385 | 0.04223 | 0.020319 | 0.0068154 | 0.05026 | -0.006822 | -0.026423 | 0.001407 | -0.049614 | 0.079598 | 0.11483 | 0.24269 | 0.005627 | 0.051413 | 0.059882 | -0.070087 | -0.029954 | 0.096121 | -0.13419 | -0.16415 | 0.12465 | -122.2394 | 0.092596 | 0.069405 | -0.055241 | -122.2042 | -122.0763 | -0.04513 | -122.349 | 0.17043 | 0.048932 | 0.094062 | -122.2229 | -122.4532 | 0.19862 | 0.23385 | 0.36171 | 0.12043 | -122.3134 | 0.089065 | 0.21514 | -0.015167 | 0.1789 | -122.4832
3320.2812 | 122.2412 | -0.11902 | 122.2916 | 1.4211e-13 | -0.044476 | -0.021609 | -0.080794 | -0.014546 | -0.0040125 | -0.020755 | 0.042443 | 0.020533 | 0.007029 | 0.049833 | -0.0063946 | -0.026423 | 0.001407 | -0.054192 | 0.070441 | 0.11483 | 0.23354 | -0.00811 | 0.051413 | 0.055303 | -0.06093 | -0.029954 | 0.096121 | -0.12503 | -0.15957 | 0.11091 | -122.2211 | 0.092596 | 0.064827 | -0.046082 | -122.1767 | -122.058 | -0.040551 | -122.3215 | 0.17043 | 0.058089 | 0.09864 | -122.1954 | -122.4166 | 0.18946 | 0.23385 | 0.35256 | 0.12043 | -122.2997 | 0.089065 | 0.21514 | -0.00601 | 0.17432 | -122.4511
3322.0625 | 122.1588 | -0.13275 | 121.9254 | 1.4211e-13 | -0.044903 | -0.022037 | -0.080366 | -0.014332 | -0.0037989 | -0.020755 | 0.042443 | 0.020319 | 0.007029 | 0.05026 | -0.0070356 | -0.021844 | 0.005985 | -0.040457 | 0.07502 | 0.11941 | 0.23354 | -0.035584 | 0.046835 | 0.059882 | -0.070087 | -0.029954 | 0.091543 | -0.12961 | -0.16415 | 0.097167 | -121.8503 | 0.11091 | 0.092294 | -0.004873 | -121.8059 | -121.6918 | -0.031398 | -121.9553 | 0.17959 | 0.062664 | 0.094062 | -121.8338 | -122.055 | 0.20777 | 0.25216 | 0.36629 | 0.13874 | -121.9609 | 0.1028 | 0.22429 | 0.003144 | 0.19263 | -122.0895
3323.7656 | 122.3511 | -0.09613 | 121.9757 | 1.4211e-13 | -0.04469 | -0.021396 | -0.080366 | -0.014332 | -0.0037989 | -0.028385 | 0.04223 | 0.020319 | 0.0068154 | 0.05026 | -0.007463 | -0.031001 | 0.010564 | -0.045036 | 0.079598 | 0.11941 | 0.24269 | -0.063057 | 0.042256 | 0.064461 | -0.065509 | -0.029954 | 0.096121 | -0.12961 | -0.15957 | 0.033073 | -121.8961 | 0.065129 | 0.051094 | 0.018021 | -121.8563 | -121.733 | -0.06344 | -122.0057 | 0.13839 | 0.030621 | 0.094061 | -121.8796 | -122.1053 | 0.17573 | 0.21554 | 0.33882 | 0.10669 | -122.0388 | 0.066176 | 0.19225 | -0.033477 | 0.16059 | -122.1353
3325.4688 | 122.4289 | -0.064087 | 122.2961 | 1.4211e-13 | -0.04469 | -0.021609 | -0.08058 | -0.014332 | -0.0037989 | -0.028385 | 0.042443 | 0.020533 | 0.0068154 | 0.05026 | -0.0070356 | -0.021844 | 0.005985 | -0.045036 | 0.065863 | 0.11483 | 0.24269 | -0.058478 | 0.042256 | 0.059882 | -0.065509 | -0.020797 | 0.096121 | -0.13419 | -0.16873 | 0.005609 | -122.2303 | 0.042243 | 0.019051 | 0.013442 | -122.1813 | -122.0534 | -0.10464 | -122.3169 | 0.10634 | -0.001422 | 0.10322 | -122.2 | -122.4303 | 0.12995 | 0.17892 | 0.30678 | 0.070072 | -122.3546 | 0.04329 | 0.16021 | -0.070099 | 0.12397 | -122.4649
3327.2344 | 122.0215 | -0.09613 | 122.3511 | 1.4211e-13 | -0.044903 | -0.021609 | -0.080366 | -0.014546 | -0.0035853 | -0.028385 | 0.042016 | 0.020105 | 0.007029 | 0.050474 | -0.0072492 | -0.021844 | 0.001407 | -0.049614 | 0.079598 | 0.11483 | 0.23354 | -0.021847 | 0.042256 | 0.059882 | -0.06093 | -0.020797 | 0.086964 | -0.12961 | -0.16415 | 0.074283 | -122.2715 | 0.074286 | 0.046516 | -0.027767 | -122.2362 | -122.1175 | -0.068019 | -122.3719 | 0.13839 | 0.0352 | 0.10322 | -122.2641 | -122.4807 | 0.17573 | 0.21096 | 0.32967 | 0.097537 | -122.3729 | 0.075333 | 0.18309 | -0.033477 | 0.15601 | -122.5152
3329 | 122.4243 | -0.07782 | 122.3145 | 1.4211e-13 | -0.044262 | -0.021823 | -0.08058 | -0.014332 | -0.0040125 | -0.028385 | 0.04223 | 0.020319 | 0.0068154 | 0.050688 | -0.0070356 | -0.017266 | 0.010564 | -0.045036 | 0.07502 | 0.11941 | 0.23812 | 0.001048 | 0.042256 | 0.064461 | -0.056351 | -0.020797 | 0.096121 | -0.13876 | -0.15499 | 0.078868 | -122.2394 | 0.060554 | 0.032784 | -0.046084 | -122.195 | -122.0763 | -0.077171 | -122.3353 | 0.12008 | 0.021469 | 0.09864 | -122.2183 | -122.4532 | 0.15284 | 0.19723 | 0.31594 | 0.088384 | -122.3134 | 0.057023 | 0.17394 | -0.060945 | 0.14228 | -122.4694
3330.7031 | 122.1863 | -0.11902 | 122.3419 | 1.4211e-13 | -0.04469 | -0.021823 | -0.079939 | -0.014546 | -0.0037989 | -0.036016 | 0.04223 | 0.020533 | 0.007029 | 0.050046 | -0.0072492 | -0.026423 | 0.005985 | -0.049614 | 0.070441 | 0.11483 | 0.23354 | -0.035584 | 0.046835 | 0.059882 | -0.065509 | -0.020797 | 0.1007 | -0.12045 | -0.16415 | 0.083435 | -122.2715 | 0.092596 | 0.069405 | -0.01403 | -122.2271 | -122.1084 | -0.04513 | -122.3627 | 0.16585 | 0.05351 | 0.09864 | -122.2412 | -122.4624 | 0.18946 | 0.23385 | 0.35256 | 0.125 | -122.3775 | 0.098222 | 0.21972 | -0.001431 | 0.1789 | -122.5061
3332.4219 | 122.4792 | -0.050354 | 122.3053 | 1.4211e-13 | -0.04469 | -0.021609 | -0.080153 | -0.014546 | -0.0037989 | -0.036016 | 0.04223 | 0.020319 | 0.0068154 | 0.050474 | -0.006822 | -0.017266 | 0.005985 | -0.049614 | 0.070441 | 0.11025 | 0.22896 | -0.053899 | 0.051413 | 0.055303 | -0.06093 | -0.020797 | 0.096121 | -0.13419 | -0.15499 | -0.003545 | -122.2349 | 0.033088 | 0.00074 | 0.004285 | -122.195 | -122.0763 | -0.10464 | -122.3261 | 0.10177 | -0.010576 | 0.094061 | -122.2092 | -122.4395 | 0.1208 | 0.16061 | 0.27931 | 0.056339 | -122.3592 | 0.029557 | 0.14647 | -0.083832 | 0.10566 | -122.4603
3334.1875 | 122.4838 | -0.059509 | 122.3282 | 1.4211e-13 | -0.044903 | -0.021823 | -0.080366 | -0.01476 | -0.0035853 | -0.028385 | 0.042016 | 0.020533 | 0.0068154 | 0.050688 | -0.0070356 | -0.026423 | 0.005985 | -0.054192 | 0.065863 | 0.11941 | 0.22896 | -0.085952 | 0.042256 | 0.059882 | -0.056351 | -0.016219 | 0.1007 | -0.12961 | -0.15957 | -0.026443 | -122.2623 | 0.033086 | 0.005317 | 0.03176 | -122.2088 | -122.0992 | -0.10006 | -122.3444 | 0.10176 | 0.003158 | 0.10322 | -122.2275 | -122.4578 | 0.12537 | 0.17892 | 0.28847 | 0.065494 | -122.4141 | 0.04329 | 0.16021 | -0.070098 | 0.11939 | -122.4878
3335.8906 | 122.4426 | -0.073242 | 122.3419 | 1.4211e-13 | -0.044903 | -0.021609 | -0.080366 | -0.01476 | -0.0040125 | -0.020755 | 0.042443 | 0.020319 | 0.007029 | 0.05026 | -0.0070356 | -0.026423 | 0.005985 | -0.054192 | 0.065863 | 0.11483 | 0.23812 | -0.085952 | 0.046835 | 0.059882 | -0.070087 | -0.029954 | 0.096121 | -0.12961 | -0.16415 | -0.01271 | -122.2761 | 0.046819 | 0.01905 | 0.03176 | -122.2271 | -122.1038 | -0.090907 | -122.3719 | 0.12008 | 0.003155 | 0.094062 | -122.2458 | -122.4715 | 0.13911 | 0.18807 | 0.31136 | 0.079227 | -122.4279 | 0.043288 | 0.16936 | -0.056365 | 0.13312 | -122.5061
3337.6562 | 122.3557 | -0.1236 | 122.3831 | 1.4211e-13 | -0.045117 | -0.021609 | -0.080153 | -0.014332 | -0.0033715 | -0.028385 | 0.042443 | 0.020533 | 0.0072428 | 0.05026 | -0.0066084 | -0.026423 | 0.001407 | -0.054192 | 0.065863 | 0.1011 | 0.23354 | -0.058478 | 0.046835 | 0.064461 | -0.056351 | -0.029954 | 0.096121 | -0.12045 | -0.16873 | 0.065118 | -122.3173 | 0.097173 | 0.069404 | 0.004286 | -122.282 | -122.1496 | -0.045132 | -122.4131 | 0.17043 | 0.067245 | 0.11238 | -122.287 | -122.5036 | 0.18946 | 0.22469 | 0.35713 | 0.125 | -122.4416 | 0.093642 | 0.21972 | 0.003146 | 0.18806 | -122.5518
3339.3438 | 122.438 | -0.07782 | 122.3419 | 1.4211e-13 | -0.045117 | -0.021823 | -0.080366 | -0.01476 | -0.0040125 | -0.020755 | 0.04223 | 0.020319 | 0.0072428 | 0.050474 | -0.0070356 | -0.026423 | -0.007751 | -0.05877 | 0.061284 | 0.1011 | 0.22896 | -0.076794 | 0.042256 | 0.064461 | -0.051772 | -0.029954 | 0.096121 | -0.13419 | -0.16873 | 0.001026 | -122.2806 | 0.051397 | 0.01905 | 0.018024 | -122.2408 | -122.113 | -0.090908 | -122.3719 | 0.12008 | 0.026048 | 0.11696 | -122.2458 | -122.4761 | 0.1391 | 0.17891 | 0.30678 | 0.070069 | -122.4187 | 0.047866 | 0.17394 | -0.056366 | 0.14228 | -122.5106
3341.125 | 122.374 | -0.13275 | 122.3602 | 1.4211e-13 | -0.044903 | -0.021823 | -0.080366 | -0.014332 | -0.0035853 | -0.028385 | 0.04223 | 0.020319 | 0.0066018 | 0.050688 | -0.0070356 | -0.03558 | -0.003172 | -0.063349 | 0.061284 | 0.10567 | 0.22438 | -0.040163 | 0.037677 | 0.064461 | -0.065509 | -0.029954 | 0.091543 | -0.12503 | -0.17331 | 0.092588 | -122.2989 | 0.097171 | 0.069402 | -0.023186 | -122.2546 | -122.1358 | -0.040555 | -122.3902 | 0.17043 | 0.067242 | 0.1078 | -122.2687 | -122.4853 | 0.19404 | 0.23842 | 0.35713 | 0.12958 | -122.4004 | 0.1028 | 0.22429 | 0.007722 | 0.19721 | -122.5335
3342.8906 | 122.2549 | -0.10071 | 122.2778 | 1.4211e-13 | -0.04469 | -0.021823 | -0.08058 | -0.014973 | -0.0040125 | -0.036016 | 0.042016 | 0.020105 | 0.007029 | 0.050688 | -0.006822 | -0.03558 | -0.007751 | -0.063349 | 0.052128 | 0.1011 | 0.21522 | -0.076794 | 0.046835 | 0.059882 | -0.06093 | -0.025376 | 0.096121 | -0.13876 | -0.15499 | 0.023914 | -122.2257 | 0.065128 | 0.037359 | 0.013445 | -122.1767 | -122.0626 | -0.054283 | -122.3032 | 0.14754 | 0.039778 | 0.094061 | -122.1817 | -122.4166 | 0.15284 | 0.2018 | 0.31593 | 0.092957 | -122.3546 | 0.075332 | 0.19683 | -0.038057 | 0.16059 | -122.4328
3344.6406 | 122.4564 | -0.064087 | 122.3328 | 1.4211e-13 | -0.045331 | -0.021823 | -0.080366 | -0.014546 | -0.0037989 | -0.036016 | 0.04223 | 0.020105 | 0.0068154 | 0.050688 | -0.0072492 | -0.031001 | -0.003172 | -0.067927 | 0.061284 | 0.10567 | 0.22896 | -0.072215 | 0.042256 | 0.059882 | -0.070087 | -0.020797 | 0.1007 | -0.13419 | -0.15499 | -0.008128 | -122.2715 | 0.033086 | -0.00384 | 0.004288 | -122.2271 | -122.1038 | -0.090904 | -122.3536 | 0.10634 | -0.006 | 0.084904 | -122.2321 | -122.4669 | 0.12537 | 0.16976 | 0.29305 | 0.060915 | -122.405 | 0.04329 | 0.16479 | -0.070099 | 0.12397 | -122.4878
3346.3438 | 122.3648 | -0.091553 | 122.374 | 1.4211e-13 | -0.04469 | -0.022037 | -0.080153 | -0.014546 | -0.0037989 | -0.013124 | 0.04223 | 0.020533 | 0.007029 | 0.05026 | -0.007463 | -0.03558 | -0.003172 | -0.063349 | 0.056706 | 0.11025 | 0.22896 | -0.031005 | 0.046835 | 0.059882 | -0.056351 | -0.034533 | 0.096121 | -0.12961 | -0.15957 | 0.060548 | -122.3173 | 0.055973 | 0.028204 | -0.032344 | -122.2637 | -122.145 | -0.068017 | -122.4085 | 0.13839 | 0.035202 | 0.10322 | -122.2778 | -122.5036 | 0.14826 | 0.20181 | 0.32051 | 0.088381 | -122.405 | 0.05702 | 0.18767 | -0.038054 | 0.15143 | -122.5335
3348.1094 | 122.3648 | -0.10986 | 122.3969 | 1.4211e-13 | -0.045117 | -0.021609 | -0.080153 | -0.014546 | -0.0035853 | -0.028385 | 0.042016 | 0.020319 | 0.0072428 | 0.050474 | -0.0070356 | -0.021844 | -0.003172 | -0.05877 | 0.061284 | 0.096516 | 0.23354 | -0.085952 | 0.051413 | 0.064461 | -0.065509 | -0.025376 | 0.1007 | -0.12503 | -0.16415 | 0.023911 | -122.3356 | 0.088019 | 0.051093 | 0.027182 | -122.3003 | -122.1633 | -0.054286 | -122.4222 | 0.16128 | 0.044354 | 0.09864 | -122.2962 | -122.5219 | 0.17115 | 0.20638 | 0.3434 | 0.10669 | -122.4828 | 0.084487 | 0.21056 | -0.015166 | 0.17432 | -122.561
3349.8594 | 122.3877 | -0.11444 | 122.3694 | 1.4211e-13 | -0.045117 | -0.021609 | -0.080153 | -0.014332 | -0.0040125 | -0.028385 | 0.04223 | 0.020319 | 0.0066018 | 0.050688 | -0.007463 | -0.021844 | 0.001407 | -0.063349 | 0.065863 | 0.1011 | 0.22438 | -0.090531 | 0.046835 | 0.064461 | -0.06093 | -0.029954 | 0.1007 | -0.12961 | -0.16873 | 0.02391 | -122.3035 | 0.092597 | 0.051092 | 0.027182 | -122.2683 | -122.145 | -0.054287 | -122.3993 | 0.16128 | 0.053511 | 0.1078 | -122.2687 | -122.499 | 0.1803 | 0.21554 | 0.33882 | 0.11585 | -122.4599 | 0.084487 | 0.21514 | -0.015166 | 0.1789 | -122.5381
3351.6094 | 122.5113 | -0.059509 | 122.3694 | 1.4211e-13 | -0.045117 | -0.021823 | -0.080366 | -0.014973 | -0.0042263 | -0.043646 | 0.04223 | 0.020533 | 0.007029 | 0.05026 | -0.0066084 | -0.026423 | 0.005985 | -0.054192 | 0.07502 | 0.10567 | 0.23354 | -0.049321 | 0.046835 | 0.059882 | -0.051772 | -0.029954 | 0.096121 | -0.12503 | -0.15499 | 0.010188 | -122.2944 | 0.033086 | 0.005317 | -0.004871 | -122.2637 | -122.1358 | -0.095482 | -122.3993 | 0.10634 | 0.007737 | 0.10322 | -122.2733 | -122.4944 | 0.13453 | 0.16518 | 0.29305 | 0.065494 | -122.4187 | 0.029555 | 0.15563 | -0.06552 | 0.11939 | -122.5244
3353.3281 | 122.3923 | -0.10529 | 122.3877 | 1.4211e-13 | -0.045117 | -0.021609 | -0.080366 | -0.014546 | -0.0035853 | -0.036016 | 0.04223 | 0.020319 | 0.0068154 | 0.050474 | -0.0072492 | -0.012688 | 0.005985 | -0.054192 | 0.065863 | 0.11025 | 0.23812 | -0.053899 | 0.046835 | 0.064461 | -0.065509 | -0.020797 | 0.091543 | -0.12961 | -0.16873 | 0.051387 | -122.3218 | 0.092598 | 0.051094 | -0.000293 | -122.2774 | -122.1496 | -0.063442 | -122.4085 | 0.15212 | 0.039777 | 0.10322 | -122.2962 | -122.5173 | 0.17115 | 0.21554 | 0.3434 | 0.11127 | -122.4416 | 0.084489 | 0.19683 | -0.024321 | 0.16975 | -122.5564
3355.0625 | 122.3877 | -0.11902 | 122.3785 | 1.4211e-13 | -0.045117 | -0.022037 | -0.080366 | -0.01476 | -0.0040125 | -0.020755 | 0.04223 | 0.020105 | 0.0066018 | 0.050474 | -0.0072492 | -0.021844 | 0.010564 | -0.049614 | 0.065863 | 0.11483 | 0.24269 | -0.044742 | 0.042256 | 0.059882 | -0.051772 | -0.020797 | 0.1007 | -0.12503 | -0.15957 | 0.074277 | -122.3127 | 0.097175 | 0.069405 | -0.004872 | -122.2637 | -122.1358 | -0.040551 | -122.3993 | 0.16128 | 0.067247 | 0.1078 | -122.2778 | -122.5036 | 0.18488 | 0.23385 | 0.36171 | 0.12958 | -122.4233 | 0.098222 | 0.21972 | -0.00601 | 0.1789 | -122.5381
3356.8281 | 122.3602 | -0.10071 | 122.3694 | 1.4211e-13 | -0.045331 | -0.021609 | -0.080366 | -0.014332 | -0.0040125 | -0.028385 | 0.04223 | 0.020319 | 0.0068154 | 0.050474 | -0.0072492 | -0.026423 | 0.015142 | -0.049614 | 0.07502 | 0.11941 | 0.22896 | -0.035584 | 0.046835 | 0.055303 | -0.06093 | -0.029954 | 0.1007 | -0.12503 | -0.16873 | 0.065124 | -122.2944 | 0.074285 | 0.051094 | -0.01403 | -122.25 | -122.1404 | -0.06802 | -122.3993 | 0.14754 | 0.039778 | 0.1078 | -122.2687 | -122.4944 | 0.17573 | 0.22012 | 0.32967 | 0.11585 | -122.405 | 0.070754 | 0.20141 | -0.024321 | 0.15601 | -122.5381
3358.5938 | 122.4655 | -0.07782 | 122.3694 | 1.4211e-13 | -0.045758 | -0.021609 | -0.080153 | -0.01476 | -0.0040125 | -0.013124 | 0.04223 | 0.020319 | 0.0068154 | 0.050474 | -0.0070356 | -0.031001 | 0.001407 | -0.054192 | 0.070441 | 0.10567 | 0.23812 | -0.081373 | 0.046835 | 0.06904 | -0.056351 | -0.029954 | 0.096121 | -0.12961 | -0.15957 | -0.003553 | -122.2989 | 0.046819 | 0.023628 | 0.027181 | -122.2637 | -122.1313 | -0.08175 | -122.3993 | 0.12466 | 0.021469 | 0.10322 | -122.2733 | -122.499 | 0.14826 | 0.18349 | 0.31594 | 0.079227 | -122.4508 | 0.047866 | 0.17394 | -0.051787 | 0.14686 | -122.529
3360.2812 | 122.438 | -0.1236 | 122.3923 | 1.4211e-13 | -0.045117 | -0.021609 | -0.08058 | -0.014546 | -0.0040125 | -0.028385 | 0.042016 | 0.020319 | 0.0068154 | 0.050901 | -0.0072492 | -0.031001 | 0.005985 | -0.05877 | 0.070441 | 0.10567 | 0.23812 | -0.076794 | 0.042256 | 0.055303 | -0.06093 | -0.039111 | 0.1007 | -0.12961 | -0.15957 | 0.046802 | -122.3218 | 0.092595 | 0.064826 | 0.018024 | -122.2866 | -122.1542 | -0.035974 | -122.4314 | 0.16585 | 0.062666 | 0.09864 | -122.2916 | -122.5219 | 0.19404 | 0.22927 | 0.36171 | 0.12958 | -122.4691 | 0.084485 | 0.2243 | -0.006011 | 0.1789 | -122.5518
3362.0469 | 122.3923 | -0.10071 | 122.2504 | 1.4211e-13 | -0.045117 | -0.021609 | -0.079939 | -0.014546 | -0.0037989 | -0.028385 | 0.04223 | 0.020319 | 0.0068154 | 0.050474 | -0.007463 | -0.026423 | 0.005985 | -0.05877 | 0.065863 | 0.11025 | 0.22896 | -0.049321 | 0.046835 | 0.059882 | -0.06093 | -0.034533 | 0.1007 | -0.13419 | -0.16873 | 0.051387 | -122.1845 | 0.074285 | 0.041938 | -0.009449 | -122.1401 | -122.0214 | -0.06802 | -122.2849 | 0.14754 | 0.039778 | 0.1078 | -122.1497 | -122.3846 | 0.16657 | 0.21096 | 0.32967 | 0.10669 | -122.2997 | 0.066175 | 0.20141 | -0.033478 | 0.16059 | -122.4191
3363.8125 | 122.4014 | -0.10529 | 122.1909 | 1.4211e-13 | -0.045117 | -0.021823 | -0.080366 | -0.014546 | -0.0040125 | -0.036016 | 0.04223 | 0.020746 | 0.0068154 | 0.050688 | -0.0070356 | -0.040158 | -0.003172 | -0.063349 | 0.056706 | 0.096516 | 0.22438 | -0.076794 | 0.051413 | 0.055303 | -0.06093 | -0.025376 | 0.096121 | -0.12961 | -0.16415 | 0.028492 | -122.1342 | 0.065128 | 0.041937 | 0.013445 | -122.0943 | -121.9665 | -0.058863 | -122.2162 | 0.1567 | 0.044356 | 0.10322 | -122.0947 | -122.3205 | 0.16199 | 0.2018 | 0.32967 | 0.10211 | -122.2677 | 0.07991 | 0.20141 | -0.024321 | 0.16059 | -122.355
3365.5781 | 122.319 | -0.10986 | 122.1771 | 1.4211e-13 | -0.044903 | -0.021823 | -0.080366 | -0.014546 | -0.0037989 | -0.036016 | 0.041803 | 0.020105 | 0.0066018 | 0.050901 | -0.007463 | -0.031001 | -0.012329 | -0.05877 | 0.061284 | 0.1011 | 0.22438 | -0.053899 | 0.046835 | 0.055303 | -0.065509 | -0.025376 | 0.096121 | -0.10671 | -0.16415 | 0.055964 | -122.1158 | 0.078862 | 0.051093 | -0.004871 | -122.076 | -121.9527 | -0.054286 | -122.2025 | 0.1567 | 0.044354 | 0.09864 | -122.081 | -122.2838 | 0.17115 | 0.21096 | 0.33424 | 0.097534 | -122.231 | 0.084487 | 0.20598 | 0.003149 | 0.16517 | -122.3413
3367.2969 | 122.2275 | -0.10529 | 122.3785 | 1.4211e-13 | -0.045331 | -0.021609 | -0.079939 | -0.014546 | -0.0037989 | -0.24204 | 0.04223 | 0.019892 | 0.007029 | 0.051115 | -0.0070356 | -0.03558 | 0.001407 | -0.05877 | 0.061284 | 0.11483 | 0.22438 | -0.067636 | 0.046835 | 0.064461 | -0.056351 | -0.020797 | 0.1007 | -0.12961 | -0.16415 | 0.03765 | -122.3173 | 0.069706 | 0.046516 | 0.008866 | -122.2637 | -122.1542 | -0.058863 | -122.3993 | 0.15212 | 0.048935 | 0.1078 | -122.2778 | -122.5081 | 0.16657 | 0.22012 | 0.32967 | 0.10669 | -122.4462 | 0.084489 | 0.20599 | -0.024321 | 0.16975 | -122.5427
3369 | 122.4701 | -0.082397 | 122.406 | 1.4211e-13 | -0.045117 | -0.021396 | -0.080153 | -0.01476 | -0.0042263 | -0.24967 | 0.04223 | 0.020319 | 0.0068154 | 0.050688 | -0.0070356 | -0.026423 | 0.005985 | -0.05877 | 0.070441 | 0.1011 | 0.22896 | -0.049321 | 0.046835 | 0.059882 | -0.06093 | -0.025376 | 0.1007 | -0.13419 | -0.16873 | 0.033076 | -122.3356 | 0.055974 | 0.023627 | -0.009449 | -122.3049 | -122.177 | -0.086331 | -122.4314 | 0.12923 | 0.021467 | 0.1078 | -122.3053 | -122.5402 | 0.15284 | 0.18349 | 0.31136 | 0.088382 | -122.4553 | 0.057021 | 0.1831 | -0.051789 | 0.14228 | -122.5747
3370.7031 | 122.3465 | -0.086975 | 122.4014 | 1.4211e-13 | -0.045331 | -0.021823 | -0.080153 | -0.014546 | -0.0042263 | -0.22678 | 0.042016 | 0.020319 | 0.0068154 | 0.050688 | -0.0072492 | -0.026423 | 0.001407 | -0.063349 | 0.070441 | 0.10567 | 0.22896 | -0.067636 | 0.037677 | 0.055303 | -0.065509 | -0.025376 | 0.1007 | -0.12961 | -0.16415 | 0.019339 | -122.331 | 0.060552 | 0.023626 | 0.004287 | -122.2958 | -122.1725 | -0.077174 | -122.4268 | 0.12465 | 0.021466 | 0.09864 | -122.3007 | -122.531 | 0.15742 | 0.19265 | 0.31593 | 0.088382 | -122.4691 | 0.061599 | 0.18767 | -0.042632 | 0.14228 | -122.5656
3372.4531 | 122.4518 | -0.082397 | 122.406 | 1.4211e-13 | -0.045331 | -0.021823 | -0.080153 | -0.014546 | -0.0040125 | -0.23441 | 0.04223 | 0.020319 | 0.007029 | 0.050901 | -0.0072492 | -0.021844 | 0.001407 | -0.05877 | 0.070441 | 0.11025 | 0.23354 | -0.026426 | 0.046835 | 0.059882 | -0.06093 | -0.029954 | 0.1007 | -0.12961 | -0.16415 | 0.055971 | -122.3356 | 0.060553 | 0.023627 | -0.032344 | -122.2958 | -122.1725 | -0.081752 | -122.436 | 0.12923 | 0.021467 | 0.10322 | -122.3053 | -122.5356 | 0.15284 | 0.19265 | 0.31593 | 0.083804 | -122.4324 | 0.052443 | 0.1831 | -0.04721 | 0.14228 | -122.5702
3374.1562 | 122.5433 | -0.059509 | 122.3831 | 1.4211e-13 | -0.045544 | -0.021823 | -0.080153 | -0.014546 | -0.0042263 | -0.23441 | 0.04223 | 0.020105 | 0.0068154 | 0.050688 | -0.007463 | -0.021844 | -0.003172 | -0.054192 | 0.079598 | 0.11941 | 0.23354 | -0.00811 | 0.051413 | 0.059882 | -0.06093 | -0.020797 | 0.1007 | -0.13876 | -0.16415 | 0.051399 | -122.3035 | 0.037665 | 0.005317 | -0.046082 | -122.2637 | -122.1496 | -0.10464 | -122.4039 | 0.11092 | -0.001421 | 0.10322 | -122.2824 | -122.5219 | 0.13911 | 0.17892 | 0.29305 | 0.056337 | -122.3912 | 0.038712 | 0.16021 | -0.079256 | 0.11939 | -122.5473
3375.9219 | 122.4472 | -0.11902 | 122.4426 | 1.4211e-13 | -0.045544 | -0.021609 | -0.080366 | -0.014332 | -0.0042263 | -0.23441 | 0.041803 | 0.019678 | 0.0068154 | 0.051115 | -0.0070356 | -0.026423 | -0.003172 | -0.05877 | 0.070441 | 0.10567 | 0.22896 | -0.044742 | 0.046835 | 0.064461 | -0.065509 | -0.029954 | 0.091543 | -0.13419 | -0.17331 | 0.074277 | -122.3722 | 0.092596 | 0.060249 | -0.014028 | -122.337 | -122.2137 | -0.054287 | -122.4726 | 0.16585 | 0.05351 | 0.1078 | -122.3511 | -122.5768 | 0.18946 | 0.22469 | 0.34798 | 0.11585 | -122.4874 | 0.089065 | 0.21056 | -0.015167 | 0.18348 | -122.6159
3377.6875 | 122.4197 | -0.10986 | 122.438 | 1.4211e-13 | -0.045331 | -0.021609 | -0.080366 | -0.014546 | -0.0040125 | -0.23441 | 0.042016 | 0.020319 | 0.0068154 | 0.051115 | -0.007463 | -0.026423 | 0.001407 | -0.054192 | 0.070441 | 0.11025 | 0.22896 | -0.063057 | 0.046835 | 0.055303 | -0.056351 | -0.025376 | 0.091543 | -0.12961 | -0.15957 | 0.046806 | -122.3676 | 0.08344 | 0.055671 | 0.008865 | -122.3278 | -122.2091 | -0.049707 | -122.4634 | 0.1567 | 0.053512 | 0.10322 | -122.3465 | -122.5677 | 0.1803 | 0.22012 | 0.33882 | 0.11127 | -122.5011 | 0.084487 | 0.20141 | -0.019744 | 0.16517 | -122.5976
3379.4375 | 122.4655 | -0.09613 | 122.438 | 1.4211e-13 | -0.045117 | -0.021396 | -0.08058 | -0.01476 | -0.0040125 | -0.24967 | 0.042016 | 0.020319 | 0.0068154 | 0.051115 | -0.0078902 | -0.031001 | 0.005985 | -0.054192 | 0.070441 | 0.1011 | 0.23354 | -0.021847 | 0.046835 | 0.055303 | -0.06093 | -0.029954 | 0.1007 | -0.12961 | -0.15957 | 0.074283 | -122.3676 | 0.065129 | 0.041938 | -0.032345 | -122.337 | -122.2045 | -0.06344 | -122.468 | 0.14297 | 0.0352 | 0.09864 | -122.3373 | -122.5677 | 0.16657 | 0.19722 | 0.32967 | 0.10211 | -122.4599 | 0.066176 | 0.19683 | -0.033477 | 0.15143 | -122.5976
3381.1406 | 122.5525 | -0.086975 | 122.3831 | 1.4211e-13 | -0.045331 | -0.021823 | -0.080153 | -0.014973 | -0.0037989 | -0.24204 | 0.041803 | 0.020533 | 0.0066018 | 0.050901 | -0.0076766 | -0.021844 | 0.001407 | -0.049614 | 0.070441 | 0.11483 | 0.23354 | -0.021847 | 0.046835 | 0.059882 | -0.06093 | -0.029954 | 0.091543 | -0.12961 | -0.16415 | 0.065128 | -122.3127 | 0.065131 | 0.037361 | -0.027767 | -122.2683 | -122.1496 | -0.077174 | -122.4131 | 0.13381 | 0.026045 | 0.10322 | -122.2916 | -122.5127 | 0.15742 | 0.20181 | 0.32051 | 0.088382 | -122.405 | 0.057021 | 0.17852 | -0.042632 | 0.14686 | -122.5473
3382.9062 | 122.4884 | -0.09613 | 122.438 | 1.4211e-13 | -0.045758 | -0.021823 | -0.079939 | -0.014973 | -0.0042263 | -0.24967 | 0.042016 | 0.019892 | 0.0066018 | 0.050901 | -0.0072492 | -0.026423 | 0.005985 | -0.05877 | 0.070441 | 0.11025 | 0.23812 | -0.044742 | 0.051413 | 0.059882 | -0.065509 | -0.025376 | 0.1007 | -0.13419 | -0.16415 | 0.051388 | -122.3676 | 0.069707 | 0.03736 | -0.014028 | -122.3278 | -122.1999 | -0.068019 | -122.4634 | 0.14754 | 0.030621 | 0.09864 | -122.3373 | -122.5722 | 0.16657 | 0.20638 | 0.33425 | 0.10211 | -122.4828 | 0.070754 | 0.19683 | -0.038056 | 0.15601 | -122.6022
3384.6562 | 122.5296 | -0.086975 | 122.4243 | 1.4211e-13 | -0.045544 | -0.021609 | -0.080366 | -0.01476 | -0.0040125 | -0.22678 | 0.042016 | 0.020105 | 0.0068154 | 0.051115 | -0.007463 | -0.012688 | 0.001407 | -0.049614 | 0.07502 | 0.10567 | 0.23812 | -0.031005 | 0.046835 | 0.06904 | -0.056351 | -0.034533 | 0.091543 | -0.11587 | -0.15957 | 0.05597 | -122.3493 | 0.074287 | 0.037361 | -0.018609 | -122.3186 | -122.1862 | -0.072595 | -122.4588 | 0.13381 | 0.030624 | 0.10322 | -122.3328 | -122.5402 | 0.162 | 0.19265 | 0.32509 | 0.088382 | -122.4553 | 0.052442 | 0.17852 | -0.028897 | 0.15602 | -122.5839
3386.4062 | 122.58 | -0.064087 | 122.3831 | 1.4211e-13 | -0.045758 | -0.021823 | -0.080366 | -0.014546 | -0.0040125 | -0.23441 | 0.04223 | 0.020319 | 0.007029 | 0.051115 | -0.007463 | -0.026423 | 0.010564 | -0.054192 | 0.079598 | 0.11483 | 0.23354 | -0.040163 | 0.042256 | 0.073618 | -0.065509 | -0.025376 | 0.096121 | -0.13876 | -0.16415 | 0.023924 | -122.3035 | 0.037664 | 0.009895 | -0.014029 | -122.2683 | -122.1496 | -0.10006 | -122.4085 | 0.10634 | -0.001422 | 0.09864 | -122.287 | -122.5219 | 0.14369 | 0.17892 | 0.29763 | 0.074651 | -122.4233 | 0.038711 | 0.16021 | -0.074678 | 0.13771 | -122.5473
3388.1094 | 122.5296 | -0.086975 | 122.3877 | 1.4211e-13 | -0.045544 | -0.021823 | -0.079939 | -0.014546 | -0.0042263 | -0.24204 | 0.04223 | 0.019892 | 0.0072428 | 0.051115 | -0.007463 | -0.021844 | 0.005985 | -0.049614 | 0.07502 | 0.10567 | 0.24269 | -0.072215 | 0.046835 | 0.073618 | -0.06093 | -0.029954 | 0.1007 | -0.13419 | -0.16415 | 0.01476 | -122.3127 | 0.065131 | 0.037361 | 0.022601 | -122.282 | -122.145 | -0.077174 | -122.4176 | 0.13381 | 0.026045 | 0.10322 | -122.287 | -122.5219 | 0.162 | 0.19265 | 0.32967 | 0.09296 | -122.4599 | 0.057021 | 0.18767 | -0.047211 | 0.16059 | -122.5518
3389.8594 | 122.3694 | -0.10071 | 122.4518 | 1.4211e-13 | -0.045758 | -0.021823 | -0.080366 | -0.014546 | -0.0042263 | -0.24204 | 0.04223 | 0.019892 | 0.0068154 | 0.051329 | -0.007463 | -0.026423 | 0.010564 | -0.045036 | 0.065863 | 0.11941 | 0.23354 | -0.017268 | 0.046835 | 0.064461 | -0.056351 | -0.020797 | 0.1007 | -0.12961 | -0.16873 | 0.08344 | -122.3859 | 0.074285 | 0.055672 | -0.027768 | -122.3324 | -122.2182 | -0.06802 | -122.4726 | 0.14754 | 0.044357 | 0.11238 | -122.3511 | -122.5814 | 0.16657 | 0.22012 | 0.33425 | 0.11127 | -122.469 | 0.079911 | 0.20141 | -0.028899 | 0.16517 | -122.6205
3391.625 | 122.5113 | -0.09613 | 122.4197 | 1.4211e-13 | -0.046185 | -0.021823 | -0.080366 | -0.01476 | -0.0044399 | -0.24204 | 0.041803 | 0.020533 | 0.0066018 | 0.051115 | -0.007463 | -0.021844 | 0.015142 | -0.049614 | 0.07502 | 0.12399 | 0.23812 | -0.053899 | 0.042256 | 0.06904 | -0.056351 | -0.029954 | 0.096121 | -0.11129 | -0.16415 | 0.042231 | -122.3447 | 0.074286 | 0.046516 | 0.004285 | -122.2957 | -122.1816 | -0.068019 | -122.4497 | 0.13839 | 0.039779 | 0.1078 | -122.3236 | -122.531 | 0.17115 | 0.22012 | 0.33425 | 0.11127 | -122.4736 | 0.066176 | 0.19225 | -0.015163 | 0.16517 | -122.5839
3393.3281 | 122.5845 | -0.068665 | 122.4106 | 1.4211e-13 | -0.045972 | -0.021609 | -0.080153 | -0.014546 | -0.0042263 | -0.23441 | 0.041803 | 0.020533 | 0.0063882 | 0.051115 | -0.0072492 | -0.021844 | 0.005985 | -0.049614 | 0.07502 | 0.11941 | 0.24269 | -0.049321 | 0.042256 | 0.059882 | -0.06093 | -0.029954 | 0.1007 | -0.12961 | -0.16873 | 0.019344 | -122.3356 | 0.046821 | 0.019051 | -0.000293 | -122.2912 | -122.1679 | -0.10006 | -122.4405 | 0.11092 | 0.007735 | 0.1078 | -122.3099 | -122.5402 | 0.14369 | 0.18808 | 0.31136 | 0.07465 | -122.4599 | 0.038711 | 0.16936 | -0.060942 | 0.12855 | -122.5793
3395.0781 | 122.5616 | -0.073242 | 122.4243 | 1.4211e-13 | -0.045972 | -0.021823 | -0.080153 | -0.015187 | -0.0040125 | -0.24204 | 0.04223 | 0.020105 | 0.0066018 | 0.051115 | -0.0076766 | -0.017266 | 0.015142 | -0.05877 | 0.07502 | 0.12399 | 0.23812 | -0.026426 | 0.042256 | 0.059882 | -0.070087 | -0.025376 | 0.096121 | -0.13876 | -0.16415 | 0.046816 | -122.3493 | 0.055976 | 0.014472 | -0.032344 | -122.3003 | -122.1862 | -0.090907 | -122.4497 | 0.1155 | 0.003155 | 0.094062 | -122.3282 | -122.5631 | 0.14826 | 0.19723 | 0.31136 | 0.088384 | -122.4507 | 0.047866 | 0.16936 | -0.065523 | 0.13312 | -122.5885
3396.8438 | 122.5342 | -0.091553 | 122.4197 | 1.4211e-13 | -0.045544 | -0.022037 | -0.080153 | -0.01476 | -0.0040125 | -0.23441 | 0.04223 | 0.020319 | 0.0068154 | 0.051329 | -0.0076766 | -0.021844 | 0.010564 | -0.045036 | 0.065863 | 0.11483 | 0.24727 | -0.021847 | 0.046835 | 0.06904 | -0.065509 | -0.025376 | 0.10528 | -0.12961 | -0.16873 | 0.069706 | -122.3539 | 0.069709 | 0.046517 | -0.023189 | -122.3049 | -122.1725 | -0.077175 | -122.4451 | 0.13839 | 0.026044 | 0.10322 | -122.3145 | -122.5493 | 0.15742 | 0.20638 | 0.33883 | 0.10212 | -122.4416 | 0.066177 | 0.19683 | -0.038054 | 0.16059 | -122.5885
3398.6094 | 122.5662 | -0.050354 | 122.406 | 1.4211e-13 | -0.045758 | -0.021609 | -0.080153 | -0.01476 | -0.0042263 | -0.23441 | 0.04223 | 0.019892 | 0.0066018 | 0.051115 | -0.007463 | -0.017266 | 0.015142 | -0.054192 | 0.079598 | 0.11941 | 0.24269 | -0.00811 | 0.046835 | 0.064461 | -0.06093 | -0.020797 | 0.1007 | -0.12961 | -0.16873 | 0.042244 | -122.3264 | 0.033088 | -0.003838 | -0.046082 | -122.2866 | -122.1633 | -0.11837 | -122.4268 | 0.097189 | -0.010576 | 0.1078 | -122.3053 | -122.5356 | 0.12995 | 0.16976 | 0.29305 | 0.065496 | -122.4141 | 0.029557 | 0.15105 | -0.079253 | 0.11482 | -122.5747
3400.2969 | 122.4701 | -0.11902 | 122.4747 | 1.4211e-13 | -0.045758 | -0.021823 | -0.080366 | -0.01476 | -0.0040125 | -0.23441 | 0.042016 | 0.020105 | 0.0066018 | 0.051115 | -0.0076766 | -0.021844 | 0.005985 | -0.045036 | 0.07502 | 0.11941 | 0.23812 | -0.003531 | 0.051413 | 0.059882 | -0.065509 | -0.034533 | 0.11444 | -0.13419 | -0.16415 | 0.11549 | -122.3997 | 0.097175 | 0.073983 | -0.041505 | -122.3553 | -122.2366 | -0.04513 | -122.5092 | 0.17043 | 0.05351 | 0.09864 | -122.3602 | -122.6089 | 0.19404 | 0.23843 | 0.35714 | 0.125 | -122.4782 | 0.084486 | 0.23345 | -0.015167 | 0.1789 | -122.6388
3402.0625 | 122.4747 | -0.10986 | 122.4518 | 1.4211e-13 | -0.046185 | -0.022037 | -0.080366 | -0.01476 | -0.0040125 | -0.24204 | 0.042016 | 0.020105 | 0.0066018 | 0.051115 | -0.007463 | -0.026423 | 0.010564 | -0.045036 | 0.070441 | 0.12399 | 0.24269 | -0.021847 | 0.046835 | 0.059882 | -0.065509 | -0.020797 | 0.10528 | -0.13419 | -0.16415 | 0.088016 | -122.3813 | 0.08344 | 0.064827 | -0.023189 | -122.3278 | -122.2091 | -0.054286 | -122.4726 | 0.1567 | 0.044354 | 0.09864 | -122.3465 | -122.586 | 0.1803 | 0.23385 | 0.35256 | 0.12043 | -122.4736 | 0.089066 | 0.21514 | -0.024323 | 0.16975 | -122.6159
3403.8125 | 122.5983 | -0.054932 | 122.4197 | 1.4211e-13 | -0.045972 | -0.021609 | -0.080366 | -0.014973 | -0.0044399 | -0.24204 | 0.042016 | 0.020319 | 0.0063882 | 0.051329 | -0.007463 | -0.026423 | 0.010564 | -0.049614 | 0.079598 | 0.11941 | 0.23812 | 0.019363 | 0.046835 | 0.064461 | -0.06093 | -0.020797 | 0.1007 | -0.12961 | -0.16415 | 0.074295 | -122.3401 | 0.028509 | 0.005318 | -0.068977 | -122.3003 | -122.1816 | -0.10922 | -122.4405 | 0.10177 | -0.005998 | 0.10322 | -122.319 | -122.5493 | 0.13453 | 0.17434 | 0.29305 | 0.065496 | -122.4004 | 0.034135 | 0.15563 | -0.074675 | 0.11939 | -122.5839
3405.5625 | 122.4655 | -0.11444 | 122.4426 | 1.4211e-13 | -0.045972 | -0.021823 | -0.080153 | -0.014332 | -0.0044399 | -0.23441 | 0.041589 | 0.019678 | 0.0063882 | 0.051329 | -0.007463 | -0.017266 | -0.007751 | -0.049614 | 0.07502 | 0.11483 | 0.23812 | -0.035584 | 0.037677 | 0.064461 | -0.065509 | -0.029954 | 0.1007 | -0.12961 | -0.15957 | 0.078857 | -122.3676 | 0.097175 | 0.064827 | -0.01403 | -122.3278 | -122.2045 | -0.045129 | -122.4726 | 0.15212 | 0.048932 | 0.094061 | -122.3419 | -122.5722 | 0.18946 | 0.22927 | 0.35256 | 0.10669 | -122.4782 | 0.084487 | 0.21514 | -0.015166 | 0.1789 | -122.6022
3407.2656 | 122.3648 | -0.091553 | 122.0535 | 1.4211e-13 | -0.046185 | -0.021396 | -0.080153 | -0.01476 | -0.0044399 | -0.23441 | 0.04223 | 0.020533 | 0.0066018 | 0.050901 | -0.0076766 | -0.008109 | 0.001407 | -0.040457 | 0.070441 | 0.11941 | 0.24269 | -0.00811 | 0.051413 | 0.059882 | -0.070087 | -0.020797 | 0.10986 | -0.13419 | -0.16873 | 0.083443 | -121.9831 | 0.083444 | 0.051096 | -0.032347 | -121.9341 | -121.8108 | -0.077175 | -122.0743 | 0.14297 | 0.021466 | 0.098641 | -121.9437 | -122.1877 | 0.16199 | 0.21096 | 0.33425 | 0.09296 | -122.0616 | 0.070756 | 0.20141 | -0.042633 | 0.15143 | -122.2223
3409.0312 | 122.5342 | -0.086975 | 122.4518 | 1.4211e-13 | -0.046399 | -0.021396 | -0.080366 | -0.014546 | -0.0040125 | -0.24204 | 0.042016 | 0.020105 | 0.0068154 | 0.051542 | -0.0072492 | -0.021844 | 0.005985 | -0.040457 | 0.079598 | 0.11941 | 0.24269 | -0.031005 | 0.046835 | 0.073618 | -0.065509 | -0.020797 | 0.10528 | -0.12961 | -0.16873 | 0.05597 | -122.3722 | 0.065131 | 0.046518 | -0.009452 | -122.3324 | -122.2091 | -0.081753 | -122.4726 | 0.13381 | 0.021466 | 0.10322 | -122.3465 | -122.5814 | 0.16657 | 0.20639 | 0.32967 | 0.09296 | -122.4828 | 0.066178 | 0.19225 | -0.042632 | 0.16059 | -122.6205
3410.7344 | 122.438 | -0.091553 | 122.4564 | 1.4211e-13 | -0.045972 | -0.021396 | -0.080153 | -0.014546 | -0.0042263 | -0.24204 | 0.041803 | 0.020319 | 0.0063882 | 0.051329 | -0.007463 | -0.017266 | 0.001407 | -0.045036 | 0.065863 | 0.12857 | 0.24727 | -0.035584 | 0.051413 | 0.059882 | -0.06093 | -0.025376 | 0.1007 | -0.13876 | -0.16415 | 0.055969 | -122.3905 | 0.074287 | 0.046517 | -0.009452 | -122.3278 | -122.2091 | -0.072596 | -122.4817 | 0.14297 | 0.030623 | 0.10322 | -122.3557 | -122.5951 | 0.15742 | 0.22012 | 0.33883 | 0.09296 | -122.4919 | 0.066177 | 0.19225 | -0.047212 | 0.15143 | -122.6205
3412.5 | 122.5754 | -0.050354 | 122.4426 | 1.4211e-13 | -0.046399 | -0.022037 | -0.080153 | -0.014332 | -0.0042263 | -0.24204 | 0.041589 | 0.020105 | 0.0066018 | 0.051115 | -0.007463 | -0.026423 | 0.001407 | -0.045036 | 0.070441 | 0.12857 | 0.24269 | 0.010206 | 0.042256 | 0.06904 | -0.056351 | -0.025376 | 0.096121 | -0.12503 | -0.16415 | 0.06056 | -122.3722 | 0.023931 | 0.005318 | -0.055242 | -122.3141 | -122.1999 | -0.11379 | -122.468 | 0.09261 | -0.005997 | 0.1078 | -122.3465 | -122.5677 | 0.1208 | 0.17892 | 0.29305 | 0.051761 | -122.4324 | 0.024978 | 0.14647 | -0.074675 | 0.11939 | -122.6068
3414.2656 | 122.5937 | -0.050354 | 122.4426 | 1.4211e-13 | -0.045972 | -0.021823 | -0.080153 | -0.014546 | -0.0042263 | -0.24204 | 0.041803 | 0.019892 | 0.0063882 | 0.05197 | -0.007463 | -0.021844 | 0.001407 | -0.040457 | 0.07502 | 0.12399 | 0.24727 | -0.035584 | 0.046835 | 0.06904 | -0.06093 | -0.034533 | 0.10986 | -0.13419 | -0.16873 | 0.01477 | -122.3676 | 0.02851 | 0.009897 | -0.004873 | -122.3186 | -122.1954 | -0.11837 | -122.4772 | 0.097189 | -0.010576 | 0.1078 | -122.3328 | -122.5768 | 0.12537 | 0.17434 | 0.29763 | 0.051761 | -122.4782 | 0.015821 | 0.16021 | -0.083832 | 0.11939 | -122.6114
3416.0312 | 122.5113 | -0.11902 | 122.4838 | 1.4211e-13 | -0.045972 | -0.021823 | -0.080153 | -0.01476 | -0.0042263 | -0.24204 | 0.042016 | 0.019892 | 0.0063882 | 0.051756 | -0.0076766 | -0.012688 | 0.005985 | -0.045036 | 0.07502 | 0.11941 | 0.24727 | -0.026426 | 0.046835 | 0.06904 | -0.070087 | -0.029954 | 0.10986 | -0.10671 | -0.16415 | 0.092593 | -122.4088 | 0.10633 | 0.073983 | -0.01861 | -122.3644 | -122.2366 | -0.04513 | -122.5138 | 0.16585 | 0.048932 | 0.094062 | -122.374 | -122.5905 | 0.19404 | 0.23843 | 0.36629 | 0.125 | -122.5103 | 0.089065 | 0.22888 | 0.012305 | 0.18806 | -122.648
3417.7344 | 122.6074 | -0.082397 | 122.4289 | 1.4211e-13 | -0.045972 | -0.021823 | -0.080153 | -0.014546 | -0.0042263 | -0.24967 | 0.041803 | 0.020105 | 0.0063882 | 0.051542 | -0.0078902 | -0.026423 | 0.001407 | -0.045036 | 0.079598 | 0.12399 | 0.24269 | -0.031005 | 0.042256 | 0.064461 | -0.06093 | -0.029954 | 0.1007 | -0.13419 | -0.16873 | 0.051392 | -122.3493 | 0.055974 | 0.037361 | -0.014031 | -122.3049 | -122.1862 | -0.086331 | -122.4588 | 0.12465 | 0.021467 | 0.1078 | -122.3282 | -122.5631 | 0.162 | 0.20639 | 0.32509 | 0.083804 | -122.4599 | 0.052443 | 0.1831 | -0.051789 | 0.14686 | -122.5976
3419.5 | 122.4884 | -0.09613 | 122.4655 | 1.4211e-13 | -0.046613 | -0.021396 | -0.080153 | -0.01476 | -0.0044399 | -0.24204 | 0.041803 | 0.020105 | 0.0063882 | 0.05197 | -0.007463 | -0.017266 | 0.001407 | -0.049614 | 0.070441 | 0.12399 | 0.24269 | -0.012689 | 0.051413 | 0.073618 | -0.065509 | -0.025376 | 0.1007 | -0.12503 | -0.16415 | 0.083441 | -122.3951 | 0.078864 | 0.046516 | -0.036925 | -122.3415 | -122.2228 | -0.068019 | -122.4909 | 0.14754 | 0.030621 | 0.09864 | -122.3648 | -122.5905 | 0.16657 | 0.22012 | 0.33882 | 0.097537 | -122.4782 | 0.070754 | 0.19683 | -0.028899 | 0.16975 | -122.6297
3421.2031 | 122.5021 | -0.10529 | 122.4838 | 1.4211e-13 | -0.045972 | -0.021609 | -0.080366 | -0.01476 | -0.0044399 | -0.24204 | 0.042016 | 0.020105 | 0.0066018 | 0.051329 | -0.007463 | -0.012688 | -0.003172 | -0.045036 | 0.07502 | 0.12399 | 0.23812 | -0.058478 | 0.051413 | 0.064461 | -0.06093 | -0.020797 | 0.096121 | -0.092979 | -0.16873 | 0.046808 | -122.4088 | 0.092598 | 0.06025 | 0.013442 | -122.3598 | -122.2457 | -0.063442 | -122.5046 | 0.1567 | 0.044356 | 0.1078 | -122.3877 | -122.5768 | 0.18031 | 0.22928 | 0.3434 | 0.10211 | -122.5423 | 0.084489 | 0.20141 | 0.012307 | 0.16975 | -122.6526
3422.9531 | 122.5983 | -0.068665 | 122.4335 | 1.4211e-13 | -0.046399 | -0.022037 | -0.080153 | -0.014973 | -0.0042263 | -0.24204 | 0.041375 | 0.019678 | 0.0066018 | 0.051542 | -0.007463 | -0.021844 | 0.001407 | -0.045036 | 0.07502 | 0.12857 | 0.23812 | -0.031005 | 0.046835 | 0.073618 | -0.06093 | -0.025376 | 0.096121 | -0.12503 | -0.15957 | 0.03766 | -122.3585 | 0.046821 | 0.023629 | -0.014031 | -122.3049 | -122.1954 | -0.090905 | -122.4588 | 0.1155 | 0.007735 | 0.09864 | -122.3374 | -122.5585 | 0.14369 | 0.19723 | 0.30678 | 0.070072 | -122.4645 | 0.043289 | 0.16479 | -0.056364 | 0.14228 | -122.593
3424.7031 | 122.4838 | -0.09613 | 122.4564 | 1.4211e-13 | -0.045972 | -0.021609 | -0.079939 | -0.014546 | -0.0044399 | -0.24967 | 0.04223 | 0.020105 | 0.0066018 | 0.051542 | -0.0081038 | -0.017266 | 0.005985 | -0.040457 | 0.07502 | 0.12399 | 0.24269 | 0.019363 | 0.046835 | 0.073618 | -0.056351 | -0.025376 | 0.10528 | -0.13419 | -0.16415 | 0.11549 | -122.3813 | 0.078864 | 0.055673 | -0.05982 | -122.3324 | -122.2137 | -0.068019 | -122.4817 | 0.14297 | 0.039779 | 0.1078 | -122.3511 | -122.5905 | 0.17115 | 0.22012 | 0.33882 | 0.10211 | -122.437 | 0.070754 | 0.20141 | -0.038056 | 0.16975 | -122.6205
3426.4531 | 122.6028 | -0.068665 | 122.4518 | 1.4211e-13 | -0.046185 | -0.022037 | -0.080366 | -0.014973 | -0.0044399 | -0.24204 | 0.042016 | 0.020105 | 0.0063882 | 0.051542 | -0.0076766 | -0.021844 | 0.005985 | -0.040457 | 0.07502 | 0.12399 | 0.23354 | -0.021847 | 0.051413 | 0.073618 | -0.065509 | -0.025376 | 0.10986 | -0.10671 | -0.17331 | 0.046818 | -122.3768 | 0.046821 | 0.028208 | -0.01861 | -122.3278 | -122.2182 | -0.10464 | -122.4772 | 0.12008 | 0.003156 | 0.1078 | -122.3419 | -122.5585 | 0.14369 | 0.19266 | 0.3022 | 0.07465 | -122.4736 | 0.043289 | 0.17852 | -0.038049 | 0.14228 | -122.6251
3428.1719 | 122.5616 | -0.086975 | 122.4609 | 1.4211e-13 | -0.046185 | -0.021823 | -0.080153 | -0.01476 | -0.0042263 | -0.23441 | 0.041803 | 0.019678 | 0.0063882 | 0.051542 | -0.0078902 | -0.012688 | 0.001407 | -0.040457 | 0.07502 | 0.11483 | 0.24727 | 0.001048 | 0.051413 | 0.078197 | -0.06093 | -0.020797 | 0.1007 | -0.12961 | -0.16873 | 0.088023 | -122.3859 | 0.074287 | 0.046518 | -0.041505 | -122.3461 | -122.2137 | -0.081753 | -122.4817 | 0.13839 | 0.026045 | 0.1078 | -122.3602 | -122.5905 | 0.162 | 0.20181 | 0.33425 | 0.088382 | -122.4599 | 0.066178 | 0.18767 | -0.042632 | 0.16517 | -122.6297
3429.9375 | 122.6395 | -0.050354 | 122.4564 | 1.4211e-13 | -0.046613 | -0.021609 | -0.080366 | -0.014973 | -0.0042263 | -0.24204 | 0.041589 | 0.020105 | 0.0063882 | 0.051542 | -0.0076766 | -0.012688 | 0.010564 | -0.040457 | 0.070441 | 0.12857 | 0.24727 | 0.019363 | 0.046835 | 0.073618 | -0.070087 | -0.029954 | 0.10528 | -0.13419 | -0.16415 | 0.069717 | -122.3859 | 0.037666 | 0.009897 | -0.05982 | -122.3278 | -122.2091 | -0.11379 | -122.4863 | 0.097189 | -0.019733 | 0.094062 | -122.3511 | -122.5905 | 0.1208 | 0.17892 | 0.29763 | 0.060918 | -122.437 | 0.0204 | 0.15563 | -0.083832 | 0.12397 | -122.6205
3431.6875 | 122.5113 | -0.10071 | 122.4976 | 1.4211e-13 | -0.046399 | -0.021823 | -0.079939 | -0.01476 | -0.0042263 | -0.24967 | 0.04223 | 0.019892 | 0.0061744 | 0.051329 | -0.0076766 | -0.021844 | 0.010564 | -0.049614 | 0.079598 | 0.11941 | 0.24269 | 0.019363 | 0.046835 | 0.06904 | -0.056351 | -0.020797 | 0.10986 | -0.13419 | -0.15957 | 0.12007 | -122.418 | 0.078864 | 0.051094 | -0.068977 | -122.3781 | -122.2549 | -0.058862 | -122.5184 | 0.14754 | 0.044357 | 0.10322 | -122.3877 | -122.6317 | 0.18031 | 0.22012 | 0.3434 | 0.11127 | -122.4782 | 0.079911 | 0.21057 | -0.033478 | 0.16975 | -122.6571
3433.4688 | 122.4884 | -0.11444 | 122.5342 | 1.4211e-13 | -0.046399 | -0.021609 | -0.079725 | -0.014546 | -0.0040125 | -0.24204 | 0.041803 | 0.020105 | 0.0068154 | 0.051756 | -0.007463 | -0.012688 | 0.005985 | -0.049614 | 0.079598 | 0.11025 | 0.23812 | 0.019363 | 0.037677 | 0.073618 | -0.06093 | -0.025376 | 0.11444 | -0.13419 | -0.16415 | 0.1338 | -122.4546 | 0.10175 | 0.064827 | -0.068977 | -122.4239 | -122.2961 | -0.049708 | -122.5596 | 0.15212 | 0.053511 | 0.10322 | -122.4197 | -122.6684 | 0.19404 | 0.22469 | 0.35256 | 0.12043 | -122.5148 | 0.089065 | 0.22888 | -0.019745 | 0.18806 | -122.6983
3435.2188 | 122.612 | -0.07782 | 122.4792 | 1.4211e-13 | -0.046613 | -0.022037 | -0.080153 | -0.01476 | -0.0037989 | -0.23441 | 0.042016 | 0.020105 | 0.0063882 | 0.051542 | -0.0081038 | -0.021844 | 0.010564 | -0.045036 | 0.079598 | 0.11941 | 0.24269 | -0.040163 | 0.042256 | 0.064461 | -0.06093 | -0.020797 | 0.10528 | -0.13419 | -0.16415 | 0.037657 | -122.3996 | 0.055976 | 0.032784 | -0.004873 | -122.3598 | -122.2366 | -0.086329 | -122.5 | 0.12008 | 0.01689 | 0.10322 | -122.374 | -122.6134 | 0.15742 | 0.19723 | 0.32051 | 0.088384 | -122.5194 | 0.057023 | 0.1831 | -0.056366 | 0.14228 | -122.6434
3436.9219 | 122.5845 | -0.059509 | 122.4655 | 1.4211e-13 | -0.046399 | -0.021823 | -0.079725 | -0.014546 | -0.0044399 | -0.24204 | 0.041803 | 0.019892 | 0.0068154 | 0.051756 | -0.0078902 | -0.017266 | 0.005985 | -0.05877 | 0.079598 | 0.11941 | 0.23812 | 0.023942 | 0.046835 | 0.078197 | -0.065509 | -0.025376 | 0.10528 | -0.12961 | -0.16415 | 0.083451 | -122.3859 | 0.042243 | 0.000739 | -0.082712 | -122.3461 | -122.2274 | -0.10464 | -122.4909 | 0.10634 | -0.006 | 0.09864 | -122.3602 | -122.5951 | 0.13911 | 0.17892 | 0.29763 | 0.065494 | -122.4416 | 0.034133 | 0.16479 | -0.070098 | 0.13771 | -122.6297
3438.7031 | 122.4884 | -0.10529 | 122.525 | 1.4211e-13 | -0.046613 | -0.021823 | -0.079939 | -0.01476 | -0.0042263 | -0.24967 | 0.042016 | 0.019892 | 0.0063882 | 0.051542 | -0.0076766 | -0.017266 | 0.005985 | -0.040457 | 0.070441 | 0.11483 | 0.24269 | -0.003531 | 0.046835 | 0.073618 | -0.06093 | -0.025376 | 0.10528 | -0.12503 | -0.17331 | 0.10175 | -122.4546 | 0.08802 | 0.064829 | -0.036926 | -122.4102 | -122.2823 | -0.06802 | -122.5504 | 0.15212 | 0.044356 | 0.11238 | -122.4197 | -122.6501 | 0.17573 | 0.22012 | 0.34798 | 0.11127 | -122.5286 | 0.07991 | 0.21057 | -0.019743 | 0.1789 | -122.6983
3440.4062 | 122.5983 | -0.068665 | 122.4747 | 1.4211e-13 | -0.046613 | -0.021609 | -0.079939 | -0.01476 | -0.0042263 | -0.24204 | 0.042016 | 0.019892 | 0.0066018 | 0.051756 | -0.0078902 | -0.012688 | 0.010564 | -0.045036 | 0.079598 | 0.11483 | 0.24727 | 0.014784 | 0.046835 | 0.073618 | -0.065509 | -0.025376 | 0.1007 | -0.13419 | -0.15957 | 0.083449 | -122.3951 | 0.055977 | 0.023629 | -0.05982 | -122.3598 | -122.2274 | -0.090905 | -122.5 | 0.1155 | 0.003156 | 0.094061 | -122.374 | -122.6089 | 0.14826 | 0.1835 | 0.31594 | 0.079229 | -122.4599 | 0.043289 | 0.16936 | -0.065521 | 0.14228 | -122.6342
3442.1719 | 122.58 | -0.10529 | 122.4701 | 1.4211e-13 | -0.046613 | -0.021396 | -0.079939 | -0.014546 | -0.0042263 | -0.23441 | 0.042016 | 0.020319 | 0.0063882 | 0.05197 | -0.0076766 | -0.008109 | 0.010564 | -0.040457 | 0.07502 | 0.12399 | 0.24269 | 0.001048 | 0.051413 | 0.06904 | -0.065509 | -0.025376 | 0.10528 | -0.12961 | -0.16415 | 0.10633 | -122.3951 | 0.097177 | 0.064829 | -0.041505 | -122.3461 | -122.2274 | -0.058863 | -122.4955 | 0.1567 | 0.039777 | 0.09864 | -122.3648 | -122.5997 | 0.18031 | 0.22928 | 0.34798 | 0.11585 | -122.469 | 0.07991 | 0.21057 | -0.024321 | 0.17433 | -122.6342
3443.9375 | 122.6486 | -0.064087 | 122.4747 | 1.4211e-13 | -0.046826 | -0.021609 | -0.079939 | -0.014973 | -0.0042263 | -0.23441 | 0.041803 | 0.019678 | 0.0063882 | 0.05197 | -0.0076766 | -0.012688 | 0.001407 | -0.040457 | 0.079598 | 0.12399 | 0.24727 | -0.031005 | 0.042256 | 0.06904 | -0.056351 | -0.025376 | 0.1007 | -0.12503 | -0.16873 | 0.033082 | -122.3951 | 0.051399 | 0.02363 | -0.009452 | -122.3507 | -122.2274 | -0.10464 | -122.5 | 0.10634 | 0.007736 | 0.11238 | -122.374 | -122.5997 | 0.14369 | 0.18808 | 0.31136 | 0.065494 | -122.5057 | 0.038711 | 0.16479 | -0.060942 | 0.13313 | -122.6434
3445.6875 | 122.5525 | -0.10529 | 122.5159 | 1.4211e-13 | -0.046613 | -0.021609 | -0.080153 | -0.015187 | -0.0044399 | -0.2573 | 0.042016 | 0.020105 | 0.0061744 | 0.051115 | -0.0076766 | -0.012688 | 0.005985 | -0.040457 | 0.079598 | 0.12857 | 0.24727 | 0.0331 | 0.042256 | 0.06904 | -0.065509 | -0.025376 | 0.10528 | -0.12961 | -0.16415 | 0.13839 | -122.4363 | 0.092598 | 0.064829 | -0.073557 | -122.3873 | -122.2686 | -0.058863 | -122.5412 | 0.14754 | 0.039777 | 0.09864 | -122.4106 | -122.6455 | 0.18488 | 0.23385 | 0.35256 | 0.11127 | -122.4828 | 0.07991 | 0.21057 | -0.024321 | 0.17433 | -122.68
3447.3906 | 122.5983 | -0.059509 | 122.4609 | 1.4211e-13 | -0.046613 | -0.021609 | -0.080366 | -0.015187 | -0.0044399 | -0.24204 | 0.041803 | 0.020105 | 0.0063882 | 0.051756 | -0.0078902 | -0.012688 | 0.005985 | -0.031301 | 0.07502 | 0.12857 | 0.25185 | 0.055995 | 0.051413 | 0.073618 | -0.056351 | -0.025376 | 0.10528 | -0.12961 | -0.17331 | 0.1155 | -122.3859 | 0.046821 | 0.028208 | -0.087296 | -122.3324 | -122.2091 | -0.1138 | -122.4863 | 0.11092 | 0.003158 | 0.11695 | -122.3557 | -122.5905 | 0.13453 | 0.18808 | 0.31136 | 0.065494 | -122.4049 | 0.034133 | 0.16479 | -0.070098 | 0.13313 | -122.6342
3449.1562 | 122.6395 | -0.091553 | 122.493 | 1.4211e-13 | -0.046399 | -0.021823 | -0.080153 | -0.014973 | -0.0044399 | -0.23441 | 0.041803 | 0.020105 | 0.0061744 | 0.051542 | -0.0078902 | -0.012688 | 0.015142 | -0.031301 | 0.088755 | 0.12399 | 0.25185 | 0.0331 | 0.046835 | 0.064461 | -0.065509 | -0.029954 | 0.10528 | -0.12961 | -0.16873 | 0.12465 | -122.4042 | 0.078865 | 0.060252 | -0.064401 | -122.369 | -122.2411 | -0.077175 | -122.5229 | 0.13839 | 0.026044 | 0.10322 | -122.3877 | -122.6226 | 0.18031 | 0.21554 | 0.34341 | 0.10669 | -122.4599 | 0.061599 | 0.19683 | -0.038054 | 0.15601 | -122.6617
3450.8594 | 122.6212 | -0.064087 | 122.4655 | 1.4211e-13 | -0.046613 | -0.021609 | -0.080153 | -0.01476 | -0.0042263 | -0.23441 | 0.041803 | 0.019678 | 0.0066018 | 0.05197 | -0.0081038 | 0.001048 | 0.010564 | -0.040457 | 0.079598 | 0.11941 | 0.25185 | 0.019363 | 0.046835 | 0.06904 | -0.06093 | -0.025376 | 0.1007 | -0.13419 | -0.15499 | 0.08345 | -122.3859 | 0.065135 | 0.02363 | -0.05982 | -122.3461 | -122.2137 | -0.090904 | -122.4909 | 0.11092 | 0.003157 | 0.094061 | -122.3648 | -122.5997 | 0.14369 | 0.1835 | 0.31594 | 0.074651 | -122.4462 | 0.038711 | 0.16479 | -0.070099 | 0.13313 | -122.6205
3452.625 | 122.6074 | -0.086975 | 122.4747 | 1.4211e-13 | -0.046826 | -0.021609 | -0.079939 | -0.014973 | -0.0042263 | -0.22678 | 0.041803 | 0.020105 | 0.0063882 | 0.051542 | -0.0083176 | -0.008109 | 0.005985 | -0.035879 | 0.088755 | 0.12399 | 0.25185 | 0.051416 | 0.042256 | 0.064461 | -0.06093 | -0.025376 | 0.1007 | -0.13419 | -0.16415 | 0.13839 | -122.3859 | 0.078866 | 0.051096 | -0.087295 | -122.3507 | -122.2228 | -0.077174 | -122.5 | 0.12923 | 0.026045 | 0.10322 | -122.374 | -122.6089 | 0.17573 | 0.21097 | 0.33883 | 0.09296 | -122.4233 | 0.061599 | 0.18767 | -0.047211 | 0.15144 | -122.6388
3454.4062 | 122.6578 | -0.041199 | 122.4701 | 1.4211e-13 | -0.046613 | -0.022037 | -0.079939 | -0.01476 | -0.0042263 | -0.23441 | 0.041803 | 0.019678 | 0.0061744 | 0.051756 | -0.0078902 | -0.008109 | 0.010564 | -0.035879 | 0.079598 | 0.13315 | 0.25185 | 0.0331 | 0.051413 | 0.073618 | -0.065509 | -0.029954 | 0.10528 | -0.12961 | -0.16415 | 0.074299 | -122.3905 | 0.03309 | 0.00532 | -0.068979 | -122.3369 | -122.2182 | -0.12295 | -122.5 | 0.092612 | -0.02431 | 0.09864 | -122.3648 | -122.5997 | 0.1208 | 0.17435 | 0.29305 | 0.051763 | -122.437 | 0.011245 | 0.14648 | -0.088408 | 0.11482 | -122.6342
3456.1875 | 122.5433 | -0.11902 | 122.5388 | 1.4211e-13 | -0.04704 | -0.021609 | -0.080153 | -0.015187 | -0.0044399 | -0.24204 | 0.041803 | 0.020105 | 0.0063882 | 0.05197 | -0.0076766 | -0.012688 | 0.010564 | -0.045036 | 0.079598 | 0.12399 | 0.24727 | 0.051416 | 0.042256 | 0.073618 | -0.065509 | -0.025376 | 0.10528 | -0.13419 | -0.16873 | 0.17044 | -122.4592 | 0.10633 | 0.073983 | -0.096452 | -122.4148 | -122.2915 | -0.049709 | -122.5641 | 0.16128 | 0.05351 | 0.10322 | -122.4335 | -122.6729 | 0.19862 | 0.24301 | 0.36629 | 0.12958 | -122.4873 | 0.093643 | 0.2243 | -0.015167 | 0.19264 | -122.7075
3457.8906 | 122.6395 | -0.068665 | 122.4564 | 1.4211e-13 | -0.047254 | -0.021609 | -0.080153 | -0.014973 | -0.0042263 | -0.24204 | 0.042016 | 0.020105 | 0.0061744 | 0.051542 | -0.0078902 | -0.008109 | 0.010564 | -0.035879 | 0.079598 | 0.12399 | 0.25643 | 0.023942 | 0.046835 | 0.073618 | -0.065509 | -0.025376 | 0.1007 | -0.12961 | -0.15957 | 0.092607 | -122.3768 | 0.060556 | 0.032786 | -0.059821 | -122.3324 | -122.1999 | -0.090905 | -122.4817 | 0.1155 | 0.003156 | 0.094061 | -122.3557 | -122.586 | 0.14826 | 0.19266 | 0.3251 | 0.079229 | -122.4324 | 0.043289 | 0.16936 | -0.060942 | 0.14228 | -122.6159
3459.6562 | 122.525 | -0.11444 | 122.4976 | 1.4211e-13 | -0.046826 | -0.021609 | -0.080153 | -0.01476 | -0.0046535 | -0.23441 | 0.042016 | 0.019892 | 0.0061744 | 0.05197 | -0.0078902 | -0.012688 | 0.010564 | -0.040457 | 0.084176 | 0.12857 | 0.24727 | 0.0331 | 0.046835 | 0.06904 | -0.06093 | -0.025376 | 0.10528 | -0.13419 | -0.16415 | 0.14754 | -122.4134 | 0.10175 | 0.073984 | -0.073557 | -122.369 | -122.2503 | -0.049708 | -122.5229 | 0.16128 | 0.053511 | 0.10322 | -122.3923 | -122.6317 | 0.19862 | 0.24301 | 0.36172 | 0.12501 | -122.4645 | 0.089065 | 0.21972 | -0.019745 | 0.18348 | -122.6617
3461.4219 | 122.5571 | -0.082397 | 122.5433 | 1.4211e-13 | -0.046826 | -0.021396 | -0.079939 | -0.014546 | -0.0040125 | -0.24204 | 0.041375 | 0.019892 | 0.0063882 | 0.052183 | -0.0081038 | -0.012688 | 0.010564 | -0.031301 | 0.084176 | 0.12399 | 0.25185 | 0.042258 | 0.046835 | 0.06904 | -0.06093 | -0.025376 | 0.1007 | -0.13419 | -0.16873 | 0.12465 | -122.4592 | 0.069709 | 0.051096 | -0.073559 | -122.4193 | -122.2915 | -0.086331 | -122.5687 | 0.12923 | 0.021467 | 0.1078 | -122.4426 | -122.6775 | 0.16657 | 0.20639 | 0.33425 | 0.092961 | -122.5011 | 0.057021 | 0.1831 | -0.051789 | 0.15144 | -122.7121
3463.1875 | 122.6212 | -0.082397 | 122.5067 | 1.4211e-13 | -0.046826 | -0.021609 | -0.079939 | -0.014973 | -0.0042263 | -0.24204 | 0.041589 | 0.019892 | 0.0063882 | 0.052183 | -0.0078902 | -0.012688 | 0.010564 | -0.031301 | 0.079598 | 0.12399 | 0.24727 | 0.042258 | 0.037677 | 0.06904 | -0.065509 | -0.025376 | 0.10528 | -0.12961 | -0.16873 | 0.12465 | -122.4271 | 0.069709 | 0.051096 | -0.073559 | -122.3827 | -122.2594 | -0.086331 | -122.5321 | 0.12007 | 0.016888 | 0.10322 | -122.4014 | -122.6363 | 0.162 | 0.20639 | 0.32967 | 0.092961 | -122.4645 | 0.057021 | 0.18768 | -0.04721 | 0.15144 | -122.6754
3464.9375 | 122.5708 | -0.09613 | 122.4838 | 1.4211e-13 | -0.047254 | -0.021823 | -0.079939 | -0.014973 | -0.0042263 | -0.24204 | 0.041589 | 0.019892 | 0.0061744 | 0.05197 | -0.0078902 | -0.012688 | 0.010564 | -0.045036 | 0.079598 | 0.13315 | 0.25185 | 0.046837 | 0.051413 | 0.073618 | -0.065509 | -0.020797 | 0.10986 | -0.13876 | -0.16873 | 0.14297 | -122.4042 | 0.083442 | 0.051094 | -0.091873 | -122.3507 | -122.232 | -0.072598 | -122.5046 | 0.14754 | 0.030621 | 0.10322 | -122.374 | -122.6226 | 0.17573 | 0.22928 | 0.34798 | 0.10669 | -122.437 | 0.075333 | 0.20599 | -0.042635 | 0.16975 | -122.6526
3466.6406 | 122.5388 | -0.1236 | 122.5113 | 1.4211e-13 | -0.046826 | -0.021823 | -0.080153 | -0.015187 | -0.0046535 | -0.23441 | 0.041375 | 0.019678 | 0.0066018 | 0.052183 | -0.0078902 | -0.017266 | 0.005985 | -0.040457 | 0.088755 | 0.12399 | 0.25185 | 0.0331 | 0.046835 | 0.073618 | -0.06093 | -0.020797 | 0.10528 | -0.12503 | -0.16415 | 0.1567 | -122.4225 | 0.10633 | 0.083139 | -0.073557 | -122.3873 | -122.2594 | -0.040553 | -122.5321 | 0.17043 | 0.062666 | 0.10322 | -122.406 | -122.6363 | 0.21235 | 0.24759 | 0.37545 | 0.12958 | -122.4782 | 0.1028 | 0.22887 | -0.001433 | 0.19721 | -122.6754
3468.4062 | 122.6578 | -0.068665 | 122.5204 | 1.4211e-13 | -0.046826 | -0.021823 | -0.079939 | -0.01476 | -0.0040125 | -0.24204 | 0.042016 | 0.019892 | 0.0061744 | 0.05197 | -0.0081038 | -0.012688 | 0.010564 | -0.040457 | 0.088755 | 0.13315 | 0.25185 | -0.00811 | 0.042256 | 0.06904 | -0.06093 | -0.025376 | 0.10528 | -0.12961 | -0.17331 | 0.060555 | -122.4317 | 0.055977 | 0.028208 | -0.032347 | -122.3873 | -122.2686 | -0.10464 | -122.5458 | 0.11092 | 0.007735 | 0.11238 | -122.4152 | -122.6501 | 0.15742 | 0.20181 | 0.32052 | 0.079229 | -122.5286 | 0.043289 | 0.17394 | -0.060942 | 0.13771 | -122.6938
3470.1094 | 122.4976 | -0.11902 | 122.5525 | 1.4211e-13 | -0.046613 | -0.021823 | -0.080153 | -0.01476 | -0.0044399 | -0.22678 | 0.042016 | 0.019678 | 0.0057472 | 0.052183 | -0.0081038 | -0.012688 | 0.010564 | -0.031301 | 0.084176 | 0.12399 | 0.25643 | 0.005627 | 0.042256 | 0.06904 | -0.065509 | -0.020797 | 0.10986 | -0.13419 | -0.16873 | 0.12465 | -122.4683 | 0.10633 | 0.087718 | -0.036928 | -122.4285 | -122.2961 | -0.049709 | -122.5733 | 0.16128 | 0.05351 | 0.10322 | -122.4426 | -122.6867 | 0.2032 | 0.24301 | 0.37545 | 0.12958 | -122.5469 | 0.098222 | 0.22888 | -0.015167 | 0.18806 | -122.7212
3471.8594 | 122.5296 | -0.11902 | 122.5433 | 1.4211e-13 | -0.046613 | -0.021823 | -0.080153 | -0.014973 | -0.0042263 | -0.23441 | 0.04223 | 0.019464 | 0.0063882 | 0.052183 | -0.0078902 | -0.008109 | 0.005985 | -0.035879 | 0.088755 | 0.12857 | 0.25185 | 0.0331 | 0.042256 | 0.073618 | -0.06093 | -0.029954 | 0.10528 | -0.12961 | -0.16873 | 0.15212 | -122.4546 | 0.11091 | 0.08314 | -0.068979 | -122.4148 | -122.2915 | -0.049709 | -122.5733 | 0.16128 | 0.058089 | 0.1078 | -122.4381 | -122.6729 | 0.20777 | 0.24759 | 0.37087 | 0.125 | -122.5102 | 0.089065 | 0.2243 | -0.010588 | 0.19264 | -122.7121
3473.6406 | 122.6212 | -0.07782 | 122.5113 | 1.4211e-13 | -0.04704 | -0.021823 | -0.079939 | -0.015187 | -0.0044399 | -0.24204 | 0.041589 | 0.019892 | 0.0059608 | 0.052397 | -0.0081038 | -0.003531 | 0.010564 | -0.040457 | 0.084176 | 0.12399 | 0.24727 | 0.028521 | 0.046835 | 0.073618 | -0.051772 | -0.025376 | 0.10528 | -0.13419 | -0.17331 | 0.10634 | -122.4271 | 0.074289 | 0.037363 | -0.068978 | -122.3873 | -122.264 | -0.095486 | -122.5367 | 0.12466 | 0.026048 | 0.12153 | -122.406 | -122.6455 | 0.162 | 0.20181 | 0.32509 | 0.088384 | -122.4828 | 0.052444 | 0.1831 | -0.056366 | 0.15144 | -122.6846
3475.3438 | 122.5754 | -0.10529 | 122.5708 | 1.4211e-13 | -0.04704 | -0.021823 | -0.079939 | -0.014973 | -0.0044399 | -0.24204 | 0.041589 | 0.019678 | 0.0061744 | 0.052183 | -0.0078902 | -0.003531 | 0.015142 | -0.040457 | 0.079598 | 0.12399 | 0.24727 | 0.069732 | 0.033099 | 0.078197 | -0.065509 | -0.025376 | 0.10986 | -0.12961 | -0.16873 | 0.17502 | -122.4912 | 0.10175 | 0.064829 | -0.11019 | -122.4468 | -122.3235 | -0.063442 | -122.5962 | 0.13839 | 0.039777 | 0.10322 | -122.4609 | -122.7004 | 0.18488 | 0.22928 | 0.35256 | 0.12043 | -122.5011 | 0.07991 | 0.21514 | -0.024321 | 0.18348 | -122.7395
3477.0469 | 122.5891 | -0.086975 | 122.5388 | 1.4211e-13 | -0.04704 | -0.021823 | -0.079725 | -0.01476 | -0.0044399 | -0.24967 | 0.041589 | 0.019678 | 0.0061744 | 0.05197 | -0.0081038 | -0.012688 | 0.010564 | -0.045036 | 0.084176 | 0.12857 | 0.24727 | 0.051416 | 0.042256 | 0.073618 | -0.06093 | -0.034533 | 0.10528 | -0.12961 | -0.16873 | 0.13839 | -122.4546 | 0.074287 | 0.041939 | -0.096452 | -122.4102 | -122.2915 | -0.081753 | -122.5733 | 0.12923 | 0.026045 | 0.1078 | -122.4335 | -122.6684 | 0.17115 | 0.21554 | 0.33425 | 0.097539 | -122.4873 | 0.052442 | 0.19225 | -0.042632 | 0.16059 | -122.7075
3478.8125 | 122.6578 | -0.073242 | 122.4838 | 1.4211e-13 | -0.046826 | -0.021823 | -0.079725 | -0.01476 | -0.0044399 | -0.23441 | 0.041589 | 0.019678 | 0.0063882 | 0.05197 | -0.0083176 | -0.003531 | 0.010564 | -0.035879 | 0.084176 | 0.12857 | 0.24269 | 0.014784 | 0.037677 | 0.064461 | -0.06093 | -0.025376 | 0.10986 | -0.13419 | -0.16415 | 0.088026 | -122.3996 | 0.069711 | 0.037363 | -0.050663 | -122.3553 | -122.2411 | -0.090907 | -122.5092 | 0.11092 | 0.012312 | 0.10322 | -122.374 | -122.618 | 0.15742 | 0.20181 | 0.31594 | 0.083806 | -122.469 | 0.047866 | 0.1831 | -0.060944 | 0.1377 | -122.648
3480.5781 | 122.6303 | -0.073242 | 122.5159 | 1.4211e-13 | -0.04704 | -0.021396 | -0.079725 | -0.01476 | -0.0044399 | -0.24204 | 0.042016 | 0.020319 | 0.0063882 | 0.05197 | -0.0076766 | -0.008109 | 0.015142 | -0.035879 | 0.084176 | 0.12857 | 0.25185 | 0.005627 | 0.046835 | 0.073618 | -0.06093 | -0.025376 | 0.10528 | -0.13876 | -0.15957 | 0.078869 | -122.4317 | 0.065133 | 0.037363 | -0.041506 | -122.3873 | -122.264 | -0.086328 | -122.5412 | 0.12008 | 0.012312 | 0.09864 | -122.4106 | -122.6546 | 0.15742 | 0.20181 | 0.32509 | 0.088384 | -122.5102 | 0.047866 | 0.17852 | -0.065523 | 0.14686 | -122.6754
3482.2812 | 122.5754 | -0.10986 | 122.5571 | 1.4211e-13 | -0.047254 | -0.021609 | -0.079725 | -0.014973 | -0.0046535 | -0.24967 | 0.041589 | 0.019678 | 0.0063882 | 0.052397 | -0.0081038 | -0.012688 | 0.005985 | -0.040457 | 0.088755 | 0.12399 | 0.24727 | 0.0331 | 0.046835 | 0.059882 | -0.06093 | -0.025376 | 0.11444 | -0.12961 | -0.17331 | 0.14296 | -122.4683 | 0.097175 | 0.069406 | -0.073557 | -122.4331 | -122.3098 | -0.063443 | -122.5824 | 0.1567 | 0.048933 | 0.11238 | -122.4426 | -122.6867 | 0.19862 | 0.23385 | 0.35714 | 0.11585 | -122.524 | 0.084487 | 0.2243 | -0.019744 | 0.16975 | -122.7304
3484.0625 | 122.6349 | -0.07782 | 122.5525 | 1.4211e-13 | -0.04704 | -0.021609 | -0.079725 | -0.015187 | -0.0042263 | -0.23441 | 0.042016 | 0.019892 | 0.0061744 | 0.052397 | -0.0081038 | -0.008109 | 0.010564 | -0.045036 | 0.084176 | 0.12857 | 0.24269 | 0.037679 | 0.046835 | 0.064461 | -0.056351 | -0.034533 | 0.10986 | -0.12961 | -0.16873 | 0.1155 | -122.4683 | 0.069711 | 0.032784 | -0.082715 | -122.4239 | -122.3098 | -0.090908 | -122.587 | 0.12466 | 0.021469 | 0.11238 | -122.4426 | -122.6821 | 0.162 | 0.20639 | 0.32051 | 0.088384 | -122.5148 | 0.043287 | 0.18768 | -0.051787 | 0.14228 | -122.7212
3485.8281 | 122.6028 | -0.086975 | 122.5571 | 1.4211e-13 | -0.047254 | -0.021823 | -0.079725 | -0.014546 | -0.0044399 | -0.24204 | 0.041589 | 0.019892 | 0.0061744 | 0.052183 | -0.0078902 | -0.012688 | 0.019721 | -0.040457 | 0.079598 | 0.12857 | 0.24727 | 0.051416 | 0.055992 | 0.064461 | -0.06093 | -0.020797 | 0.10986 | -0.12961 | -0.17331 | 0.13839 | -122.4775 | 0.074287 | 0.046518 | -0.091873 | -122.4285 | -122.3098 | -0.086331 | -122.5779 | 0.14297 | 0.026045 | 0.11238 | -122.4472 | -122.6867 | 0.16657 | 0.21554 | 0.33425 | 0.1067 | -122.5057 | 0.066178 | 0.19683 | -0.042632 | 0.15144 | -122.7304
3487.5938 | 122.5616 | -0.10529 | 122.5433 | 1.4211e-13 | -0.047254 | -0.022037 | -0.079939 | -0.014973 | -0.0044399 | -0.24204 | 0.041803 | 0.019892 | 0.0063882 | 0.052183 | -0.0083176 | -0.008109 | 0.010564 | -0.040457 | 0.084176 | 0.12399 | 0.25185 | 0.0331 | 0.042256 | 0.064461 | -0.056351 | -0.025376 | 0.1007 | -0.13419 | -0.16873 | 0.13839 | -122.4592 | 0.097177 | 0.064829 | -0.073557 | -122.4193 | -122.2915 | -0.063442 | -122.5687 | 0.14754 | 0.048935 | 0.11238 | -122.4426 | -122.6775 | 0.18946 | 0.22928 | 0.35714 | 0.11585 | -122.5102 | 0.07991 | 0.20599 | -0.0289 | 0.16975 | -122.7121
3489.2969 | 122.6303 | -0.091553 | 122.5479 | 1.4211e-13 | -0.047254 | -0.021609 | -0.079939 | -0.015187 | -0.0044399 | -0.24204 | 0.041589 | 0.019678 | 0.0059608 | 0.052611 | -0.0085312 | -0.012688 | 0.015142 | -0.040457 | 0.084176 | 0.11941 | 0.24727 | 0.014784 | 0.051413 | 0.064461 | -0.06093 | -0.025376 | 0.096121 | -0.13419 | -0.16873 | 0.10634 | -122.4637 | 0.078865 | 0.051096 | -0.055241 | -122.4285 | -122.3006 | -0.077175 | -122.5733 | 0.14297 | 0.030623 | 0.1078 | -122.4518 | -122.6821 | 0.17573 | 0.21096 | 0.33883 | 0.10669 | -122.5331 | 0.066177 | 0.18767 | -0.042633 | 0.15601 | -122.7166
3491.0625 | 122.5845 | -0.10529 | 122.5708 | 1.4211e-13 | -0.04704 | -0.021823 | -0.079512 | -0.01476 | -0.0042263 | -0.24967 | 0.041589 | 0.020319 | 0.0061744 | 0.05197 | -0.0081038 | -0.012688 | 0.010564 | -0.040457 | 0.079598 | 0.12399 | 0.25185 | 0.010206 | 0.055992 | 0.06904 | -0.06093 | -0.025376 | 0.1007 | -0.12961 | -0.16873 | 0.11549 | -122.4912 | 0.092598 | 0.064829 | -0.050663 | -122.4468 | -122.3189 | -0.063442 | -122.5962 | 0.16128 | 0.044356 | 0.1078 | -122.4701 | -122.7004 | 0.18488 | 0.22928 | 0.35714 | 0.11585 | -122.5606 | 0.07991 | 0.20599 | -0.024321 | 0.17433 | -122.7395
3492.8125 | 122.5754 | -0.10071 | 122.5525 | 1.4211e-13 | -0.047254 | -0.021609 | -0.079512 | -0.015187 | -0.0044399 | -0.24967 | 0.041803 | 0.019678 | 0.0063882 | 0.052183 | -0.0085312 | -0.008109 | 0.005985 | -0.040457 | 0.084176 | 0.12399 | 0.22438 | 0.014784 | 0.042256 | 0.059882 | -0.06093 | -0.020797 | 0.10528 | -0.13419 | -0.16873 | 0.11549 | -122.4683 | 0.092599 | 0.060251 | -0.055241 | -122.4285 | -122.3281 | -0.06802 | -122.5733 | 0.14296 | 0.039778 | 0.1078 | -122.4472 | -122.6867 | 0.18488 | 0.2247 | 0.32509 | 0.10669 | -122.5377 | 0.079911 | 0.20599 | -0.033478 | 0.16059 | -122.7212
3494.5781 | 122.5616 | -0.11902 | 122.5571 | 1.4211e-13 | -0.04704 | -0.022037 | -0.079939 | -0.015187 | -0.0042263 | -0.24967 | 0.041803 | 0.019464 | 0.0061744 | 0.052183 | -0.0083176 | -0.012688 | 0.005985 | -0.031301 | 0.079598 | 0.12857 | 0.21522 | 0.005627 | 0.046835 | 0.06904 | -0.06093 | -0.020797 | 0.1007 | -0.13876 | -0.16873 | 0.12465 | -122.4775 | 0.10633 | 0.087718 | -0.036928 | -122.4285 | -122.3418 | -0.049709 | -122.5779 | 0.16585 | 0.058089 | 0.1078 | -122.4564 | -122.6958 | 0.19862 | 0.24759 | 0.33424 | 0.125 | -122.5514 | 0.098222 | 0.21972 | -0.019746 | 0.18806 | -122.7258
3496.2812 | 122.6532 | -0.073242 | 122.5388 | 1.4211e-13 | -0.047254 | -0.021609 | -0.079725 | -0.014973 | -0.0040125 | -0.24967 | 0.041162 | 0.019464 | 0.0063882 | 0.052183 | -0.0083176 | -0.008109 | 0.015142 | -0.035879 | 0.088755 | 0.12857 | 0.22438 | 0.055995 | 0.046835 | 0.073618 | -0.06093 | -0.016219 | 0.10986 | -0.13419 | -0.15957 | 0.12924 | -122.45 | 0.065133 | 0.037363 | -0.091874 | -122.4102 | -122.3144 | -0.086328 | -122.555 | 0.12008 | 0.012312 | 0.09864 | -122.4289 | -122.6729 | 0.162 | 0.20181 | 0.29762 | 0.088384 | -122.4828 | 0.057023 | 0.1831 | -0.060944 | 0.14686 | -122.6983
3498.0469 | 122.6395 | -0.068665 | 122.5342 | 1.4211e-13 | -0.047254 | -0.021823 | -0.079725 | -0.015187 | -0.0042263 | -0.24204 | 0.041803 | 0.019678 | 0.0055336 | 0.052397 | -0.0083176 | -0.017266 | 0.010564 | -0.045036 | 0.088755 | 0.12399 | 0.2198 | 0.0331 | 0.051413 | 0.064461 | -0.056351 | -0.016219 | 0.10528 | -0.12503 | -0.16873 | 0.10176 | -122.4454 | 0.051399 | 0.023629 | -0.078136 | -122.4102 | -122.3144 | -0.10006 | -122.5504 | 0.12008 | 0.012314 | 0.11238 | -122.4289 | -122.6592 | 0.15742 | 0.19266 | 0.28847 | 0.079229 | -122.5011 | 0.052446 | 0.17394 | -0.056364 | 0.13313 | -122.7029
3499.8281 | 122.5662 | -0.10071 | 122.5754 | 1.4211e-13 | -0.047254 | -0.021823 | -0.079939 | -0.015187 | -0.0042263 | -0.24204 | 0.041375 | 0.019678 | 0.0063882 | 0.052183 | -0.0083176 | -0.012688 | 0.0243 | -0.035879 | 0.084176 | 0.11941 | 0.22896 | 0.046837 | 0.046835 | 0.078197 | -0.056351 | -0.025376 | 0.1007 | -0.12961 | -0.16415 | 0.14755 | -122.4912 | 0.08802 | 0.064829 | -0.082716 | -122.456 | -122.3464 | -0.063441 | -122.6008 | 0.14754 | 0.044357 | 0.1078 | -122.4747 | -122.705 | 0.18488 | 0.22012 | 0.32967 | 0.12501 | -122.5285 | 0.075332 | 0.20141 | -0.028899 | 0.17891 | -122.7395
3501.5312 | 122.699 | -0.086975 | 122.5388 | 1.4211e-13 | -0.04704 | -0.021823 | -0.079512 | -0.014973 | -0.0044399 | -0.23441 | 0.041375 | 0.019892 | 0.0061744 | 0.052611 | -0.0081038 | -0.012688 | 0.010564 | -0.040457 | 0.079598 | 0.12857 | 0.22438 | 0.037679 | 0.051413 | 0.06904 | -0.065509 | -0.020797 | 0.11444 | -0.12503 | -0.17331 | 0.12465 | -122.4592 | 0.074287 | 0.046518 | -0.078136 | -122.4102 | -122.3144 | -0.086331 | -122.5596 | 0.13839 | 0.021466 | 0.1078 | -122.4243 | -122.6638 | 0.16657 | 0.21554 | 0.31136 | 0.097539 | -122.5011 | 0.066178 | 0.20141 | -0.038054 | 0.15602 | -122.7121
3503.2344 | 122.6395 | -0.068665 | 122.5525 | 1.4211e-13 | -0.047467 | -0.021823 | -0.079725 | -0.014973 | -0.0044399 | -0.24204 | 0.041375 | 0.019678 | 0.0059608 | 0.052824 | -0.0083176 | -0.012688 | 0.019721 | -0.035879 | 0.079598 | 0.12399 | 0.21522 | 0.037679 | 0.042256 | 0.064461 | -0.070087 | -0.020797 | 0.10528 | -0.13419 | -0.17788 | 0.10634 | -122.4729 | 0.055977 | 0.032786 | -0.073558 | -122.4285 | -122.3373 | -0.10922 | -122.5733 | 0.11092 | -0.001422 | 0.1078 | -122.4472 | -122.6867 | 0.14826 | 0.19266 | 0.28389 | 0.088386 | -122.5148 | 0.047868 | 0.17394 | -0.065521 | 0.13313 | -122.7304
3505 | 122.6944 | -0.059509 | 122.5525 | 1.4211e-13 | -0.047254 | -0.021609 | -0.079298 | -0.015187 | -0.0044399 | -0.24967 | 0.041589 | 0.019678 | 0.0059608 | 0.052183 | -0.0081038 | -0.008109 | 0.015142 | -0.035879 | 0.084176 | 0.12399 | 0.21522 | 0.0331 | 0.042256 | 0.06904 | -0.065509 | -0.020797 | 0.1007 | -0.13419 | -0.16873 | 0.092609 | -122.4683 | 0.0514 | 0.02363 | -0.068979 | -122.4285 | -122.3373 | -0.10922 | -122.5733 | 0.10176 | -0.006 | 0.10322 | -122.4518 | -122.6867 | 0.14369 | 0.1835 | 0.27473 | 0.074651 | -122.5194 | 0.038712 | 0.16021 | -0.074677 | 0.12855 | -122.7212
3506.7031 | 122.7036 | -0.073242 | 122.5479 | 1.4211e-13 | -0.047467 | -0.021823 | -0.079939 | -0.015187 | -0.0044399 | -0.24967 | 0.041375 | 0.019464 | 0.0061744 | 0.052397 | -0.0083176 | -0.021844 | 0.005985 | -0.049614 | 0.079598 | 0.11941 | 0.21522 | 0.005627 | 0.046835 | 0.059882 | -0.06093 | -0.016219 | 0.1007 | -0.12961 | -0.16873 | 0.078869 | -122.4683 | 0.051398 | 0.023628 | -0.055241 | -122.4285 | -122.3327 | -0.095486 | -122.5641 | 0.12008 | 0.012312 | 0.1078 | -122.4472 | -122.6775 | 0.15284 | 0.19265 | 0.28847 | 0.079227 | -122.5423 | 0.057023 | 0.17394 | -0.056365 | 0.13312 | -122.7166
3508.4688 | 122.5983 | -0.10071 | 122.5891 | 1.4211e-13 | -0.047681 | -0.021823 | -0.079512 | -0.01476 | -0.0042263 | -0.24204 | 0.041803 | 0.020105 | 0.0061744 | 0.052397 | -0.0083176 | -0.021844 | 0.015142 | -0.045036 | 0.070441 | 0.12399 | 0.2198 | 0.001048 | 0.051413 | 0.06904 | -0.056351 | -0.016219 | 0.10986 | -0.12503 | -0.16415 | 0.10176 | -122.5187 | 0.078864 | 0.055672 | -0.046084 | -122.4651 | -122.3693 | -0.063441 | -122.6053 | 0.15212 | 0.044357 | 0.1078 | -122.4793 | -122.7141 | 0.17115 | 0.2247 | 0.32051 | 0.11585 | -122.5881 | 0.084489 | 0.21057 | -0.024321 | 0.16975 | -122.7533
3510.1719 | 122.6807 | -0.059509 | 122.5571 | 1.4211e-13 | -0.047467 | -0.021823 | -0.079512 | -0.014973 | -0.0042263 | -0.24204 | 0.041375 | 0.019251 | 0.0059608 | 0.052397 | -0.0085312 | -0.012688 | 0.001407 | -0.040457 | 0.079598 | 0.11483 | 0.21064 | -0.026426 | 0.046835 | 0.06904 | -0.070087 | -0.025376 | 0.10528 | -0.12961 | -0.16873 | 0.033083 | -122.4775 | 0.046821 | 0.019052 | -0.014031 | -122.4422 | -122.3464 | -0.10922 | -122.5824 | 0.10634 | -0.010578 | 0.098641 | -122.4518 | -122.6867 | 0.13911 | 0.17434 | 0.27015 | 0.060916 | -122.5835 | 0.034133 | 0.16479 | -0.070098 | 0.12855 | -122.7258
3511.9375 | 122.6166 | -0.082397 | 122.5616 | 1.4211e-13 | -0.047254 | -0.021823 | -0.079512 | -0.015187 | -0.0044399 | -0.24204 | 0.041589 | 0.020105 | 0.0059608 | 0.052611 | -0.0081038 | -0.017266 | 0.005985 | -0.040457 | 0.070441 | 0.11941 | 0.21064 | 0.001048 | 0.051413 | 0.06904 | -0.056351 | -0.01164 | 0.10986 | -0.12503 | -0.16873 | 0.083445 | -122.4912 | 0.065131 | 0.04194 | -0.041505 | -122.4422 | -122.351 | -0.086331 | -122.5733 | 0.13381 | 0.026046 | 0.11238 | -122.4518 | -122.6867 | 0.15284 | 0.20181 | 0.29304 | 0.088382 | -122.5606 | 0.070757 | 0.19225 | -0.042632 | 0.15144 | -122.7304
3513.6562 | 122.58 | -0.13275 | 122.5708 | 1.4211e-13 | -0.047254 | -0.022037 | -0.079298 | -0.01476 | -0.0044399 | -0.24204 | 0.041162 | 0.019678 | 0.0059608 | 0.053038 | -0.0083176 | -0.012688 | 0.010564 | -0.045036 | 0.084176 | 0.12399 | 0.21064 | -0.00811 | 0.037677 | 0.064461 | -0.056351 | -0.016219 | 0.10528 | -0.13876 | -0.17331 | 0.12464 | -122.4866 | 0.12006 | 0.087715 | -0.036926 | -122.4468 | -122.3602 | -0.040555 | -122.587 | 0.17043 | 0.0764 | 0.11695 | -122.4655 | -122.7096 | 0.21693 | 0.25674 | 0.3434 | 0.14331 | -122.5789 | 0.11653 | 0.23803 | -0.006014 | 0.19721 | -122.7441
3515.4219 | 122.6532 | -0.086975 | 122.5342 | 1.4211e-13 | -0.047254 | -0.022037 | -0.079939 | -0.015187 | -0.0044399 | -0.24204 | 0.041375 | 0.019892 | 0.0061744 | 0.052397 | -0.0081038 | -0.012688 | 0.010564 | -0.045036 | 0.079598 | 0.12399 | 0.21522 | -0.003531 | 0.051413 | 0.064461 | -0.06093 | -0.020797 | 0.10986 | -0.12961 | -0.17788 | 0.083444 | -122.4546 | 0.074287 | 0.041939 | -0.041505 | -122.4102 | -122.319 | -0.09091 | -122.555 | 0.13839 | 0.026045 | 0.11695 | -122.4243 | -122.6638 | 0.16657 | 0.21097 | 0.3022 | 0.097539 | -122.5377 | 0.066178 | 0.19683 | -0.042632 | 0.15144 | -122.7121
3517.1719 | 122.6898 | -0.068665 | 122.5479 | 1.4211e-13 | -0.047254 | -0.021609 | -0.080153 | -0.015187 | -0.0044399 | -0.24967 | 0.041589 | 0.019678 | 0.0061744 | 0.052397 | -0.0085312 | -0.021844 | 0.010564 | -0.045036 | 0.07502 | 0.12399 | 0.21064 | 0.0331 | 0.037677 | 0.064461 | -0.065509 | -0.020797 | 0.1007 | -0.13419 | -0.16415 | 0.10176 | -122.4729 | 0.046821 | 0.023629 | -0.078136 | -122.4239 | -122.3373 | -0.095484 | -122.5687 | 0.10634 | 0.003156 | 0.09864 | -122.4472 | -122.6821 | 0.14369 | 0.19266 | 0.27931 | 0.079229 | -122.5148 | 0.047868 | 0.16936 | -0.065521 | 0.13313 | -122.7121
3518.875 | 122.6761 | -0.091553 | 122.5433 | 1.4211e-13 | -0.047467 | -0.021823 | -0.079725 | -0.014973 | -0.0042263 | -0.22678 | 0.041162 | 0.019892 | 0.0057472 | 0.052397 | -0.0085312 | -0.017266 | 0.010564 | -0.045036 | 0.07502 | 0.12857 | 0.20607 | -0.017268 | 0.051413 | 0.064461 | -0.056351 | -0.025376 | 0.10986 | -0.13876 | -0.17331 | 0.074285 | -122.4683 | 0.074287 | 0.046517 | -0.027768 | -122.4148 | -122.3373 | -0.081753 | -122.5687 | 0.14297 | 0.035202 | 0.11695 | -122.4335 | -122.6821 | 0.16657 | 0.22012 | 0.29762 | 0.10212 | -122.5606 | 0.066177 | 0.20141 | -0.047212 | 0.15601 | -122.7166
3520.625 | 122.5708 | -0.10529 | 122.612 | 1.4211e-13 | -0.047467 | -0.022037 | -0.079512 | -0.015187 | -0.0044399 | -0.24967 | 0.041589 | 0.019678 | 0.0057472 | 0.053038 | -0.0081038 | -0.017266 | 0.005985 | -0.040457 | 0.079598 | 0.11941 | 0.21522 | 0.005627 | 0.046835 | 0.064461 | -0.065509 | -0.020797 | 0.10986 | -0.13876 | -0.17331 | 0.11091 | -122.5324 | 0.08802 | 0.064829 | -0.046084 | -122.4926 | -122.3968 | -0.06802 | -122.6328 | 0.15212 | 0.039777 | 0.1078 | -122.5021 | -122.7508 | 0.18488 | 0.2247 | 0.32051 | 0.11127 | -122.6064 | 0.084489 | 0.21514 | -0.033479 | 0.16975 | -122.7853
3522.3906 | 122.6303 | -0.10071 | 122.58 | 1.4211e-13 | -0.047467 | -0.021609 | -0.079939 | -0.015187 | -0.0044399 | -0.24967 | 0.041589 | 0.019464 | 0.0059608 | 0.052397 | -0.0081038 | -0.012688 | 0.005985 | -0.045036 | 0.070441 | 0.11483 | 0.21522 | 0.001048 | 0.046835 | 0.06904 | -0.056351 | -0.016219 | 0.10528 | -0.12503 | -0.16873 | 0.10176 | -122.5095 | 0.08802 | 0.055672 | -0.046084 | -122.4651 | -122.3647 | -0.06802 | -122.5962 | 0.14754 | 0.044357 | 0.11238 | -122.4747 | -122.705 | 0.17115 | 0.21554 | 0.31593 | 0.10669 | -122.5789 | 0.084489 | 0.20599 | -0.024321 | 0.16975 | -122.7487
3524.0938 | 122.5937 | -0.10071 | 122.5937 | 1.4211e-13 | -0.047895 | -0.021823 | -0.079725 | -0.014973 | -0.0046535 | -0.23441 | 0.041375 | 0.019464 | 0.0059608 | 0.052611 | -0.0083176 | -0.017266 | 0.010564 | -0.035879 | 0.079598 | 0.12399 | 0.21064 | 0.005627 | 0.046835 | 0.055303 | -0.065509 | -0.016219 | 0.10986 | -0.13419 | -0.17788 | 0.10634 | -122.5141 | 0.083442 | 0.064829 | -0.041506 | -122.4697 | -122.383 | -0.077177 | -122.6099 | 0.14754 | 0.035199 | 0.11238 | -122.4838 | -122.7279 | 0.18031 | 0.2247 | 0.31135 | 0.11127 | -122.5881 | 0.084489 | 0.21057 | -0.033478 | 0.15601 | -122.7716
3525.8438 | 122.644 | -0.09613 | 122.5891 | 1.4211e-13 | -0.047681 | -0.021609 | -0.079725 | -0.014973 | -0.0044399 | -0.24204 | 0.041162 | 0.019892 | 0.0061744 | 0.052824 | -0.0087448 | -0.012688 | 0.005985 | -0.045036 | 0.070441 | 0.11941 | 0.21522 | -0.012689 | 0.051413 | 0.06904 | -0.056351 | -0.020797 | 0.10528 | -0.14334 | -0.17331 | 0.083441 | -122.5187 | 0.083442 | 0.051094 | -0.032347 | -122.4697 | -122.3739 | -0.077176 | -122.6099 | 0.14754 | 0.039779 | 0.11695 | -122.4838 | -122.7325 | 0.16657 | 0.21554 | 0.31135 | 0.10211 | -122.6018 | 0.075333 | 0.20141 | -0.047213 | 0.16517 | -122.7624
3527.6094 | 122.7127 | -0.07782 | 122.5754 | 1.4211e-13 | -0.047681 | -0.022037 | -0.079512 | -0.014973 | -0.0044399 | -0.24967 | 0.041162 | 0.019251 | 0.0059608 | 0.052397 | -0.0085312 | -0.012688 | 0.005985 | -0.045036 | 0.079598 | 0.12857 | 0.21522 | 0.001048 | 0.042256 | 0.06904 | -0.06093 | -0.025376 | 0.10528 | -0.12961 | -0.16873 | 0.078868 | -122.4958 | 0.065132 | 0.032784 | -0.046084 | -122.4468 | -122.3602 | -0.090908 | -122.6008 | 0.12008 | 0.01689 | 0.1078 | -122.4701 | -122.705 | 0.15742 | 0.20639 | 0.29304 | 0.083805 | -122.5743 | 0.052444 | 0.1831 | -0.051787 | 0.14686 | -122.7441
3529.3281 | 122.6074 | -0.091553 | 122.6074 | 1.4211e-13 | -0.047895 | -0.021823 | -0.079512 | -0.015187 | -0.0048673 | -0.24204 | 0.041589 | 0.019464 | 0.0059608 | 0.052611 | -0.0085312 | -0.012688 | 0.015142 | -0.045036 | 0.079598 | 0.11483 | 0.2198 | 0.019363 | 0.046835 | 0.064461 | -0.065509 | -0.016219 | 0.1007 | -0.13419 | -0.15957 | 0.11092 | -122.5278 | 0.078865 | 0.046517 | -0.064399 | -122.4926 | -122.3876 | -0.068017 | -122.6236 | 0.13839 | 0.026044 | 0.094061 | -122.5067 | -122.7416 | 0.17115 | 0.20638 | 0.31135 | 0.10669 | -122.5881 | 0.075334 | 0.19225 | -0.042633 | 0.15601 | -122.767
3531.0938 | 122.5937 | -0.1236 | 122.5983 | 1.4211e-13 | -0.048108 | -0.02225 | -0.079512 | -0.014973 | -0.0044399 | -0.24967 | 0.041375 | 0.019251 | 0.0059608 | 0.052824 | -0.0083176 | -0.017266 | 0.005985 | -0.049614 | 0.079598 | 0.11941 | 0.2198 | 0.010206 | 0.037677 | 0.059882 | -0.056351 | -0.025376 | 0.1007 | -0.13419 | -0.17788 | 0.1338 | -122.5187 | 0.10633 | 0.073982 | -0.05982 | -122.4789 | -122.3785 | -0.054289 | -122.6236 | 0.16127 | 0.067245 | 0.12153 | -122.4976 | -122.7325 | 0.20319 | 0.24301 | 0.3434 | 0.12958 | -122.5881 | 0.09822 | 0.2243 | -0.01059 | 0.18348 | -122.7762
3532.8438 | 122.6349 | -0.11444 | 122.6028 | 1.4211e-13 | -0.048322 | -0.022037 | -0.079725 | -0.014973 | -0.0044399 | -0.23441 | 0.041375 | 0.019678 | 0.0059608 | 0.052611 | -0.0081038 | -0.017266 | -0.003172 | -0.040457 | 0.07502 | 0.11941 | 0.21064 | -0.017268 | 0.042256 | 0.059882 | -0.065509 | -0.025376 | 0.10986 | -0.13876 | -0.17331 | 0.097173 | -122.5278 | 0.097175 | 0.073984 | -0.023189 | -122.4834 | -122.3922 | -0.058865 | -122.6282 | 0.1567 | 0.048932 | 0.1078 | -122.493 | -122.7416 | 0.18946 | 0.23385 | 0.32509 | 0.11127 | -122.6201 | 0.089065 | 0.2243 | -0.024324 | 0.17432 | -122.7762
3534.5469 | 122.6486 | -0.09613 | 122.6257 | 1.4211e-13 | -0.047895 | -0.021823 | -0.079512 | -0.01476 | -0.0046535 | -0.2573 | 0.041375 | 0.019251 | 0.0059608 | 0.052824 | -0.0087448 | -0.017266 | 0.001407 | -0.040457 | 0.079598 | 0.12399 | 0.2198 | -0.026426 | 0.042256 | 0.06904 | -0.056351 | -0.020797 | 0.11901 | -0.13876 | -0.16873 | 0.069704 | -122.5461 | 0.078864 | 0.055673 | -0.014031 | -122.5017 | -122.4059 | -0.072598 | -122.6465 | 0.13839 | 0.039779 | 0.11238 | -122.5067 | -122.7645 | 0.17573 | 0.22012 | 0.31593 | 0.097537 | -122.6522 | 0.075333 | 0.21514 | -0.042635 | 0.16517 | -122.7945
3536.25 | 122.6303 | -0.07782 | 122.5891 | 1.4211e-13 | -0.048108 | -0.022037 | -0.079725 | -0.014973 | -0.0042263 | -0.22678 | 0.041589 | 0.019892 | 0.0059608 | 0.053038 | -0.0083176 | -0.012688 | 0.010564 | -0.045036 | 0.079598 | 0.12857 | 0.2198 | -0.072215 | 0.055992 | 0.06904 | -0.056351 | -0.025376 | 0.11444 | -0.12961 | -0.16415 | 0.005605 | -122.5095 | 0.065132 | 0.032784 | 0.027179 | -122.4605 | -122.3693 | -0.086329 | -122.6145 | 0.13381 | 0.021469 | 0.1078 | -122.4747 | -122.7187 | 0.15742 | 0.20639 | 0.29762 | 0.088384 | -122.6613 | 0.052444 | 0.19226 | -0.051787 | 0.14686 | -122.7533
3538.0156 | 122.6486 | -0.082397 | 122.58 | 1.4211e-13 | -0.048108 | -0.021823 | -0.079725 | -0.014973 | -0.0042263 | -0.24204 | 0.041589 | 0.019464 | 0.0059608 | 0.053038 | -0.0081038 | -0.012688 | 0.028878 | -0.035879 | 0.097912 | 0.087359 | 0.24269 | 0.023942 | 0.051413 | 0.087354 | -0.056351 | -0.016219 | 0.12359 | -0.047193 | -0.17331 | 0.10634 | -122.482 | 0.069709 | 0.046518 | -0.059821 | -122.4926 | -122.3373 | -0.090909 | -122.5962 | 0.13381 | 0.026046 | 0.11695 | -122.4564 | -122.6271 | 0.18031 | 0.16976 | 0.32509 | 0.11127 | -122.556 | 0.066178 | 0.20599 | 0.035204 | 0.16975 | -122.7533
3539.7188 | 122.6486 | -0.091553 | 122.6028 | 1.4211e-13 | -0.047895 | -0.021823 | -0.079939 | -0.014973 | -0.0044399 | -0.23441 | 0.041375 | 0.019678 | 0.0059608 | 0.052611 | -0.0083176 | -0.026423 | 0.005985 | -0.045036 | 0.070441 | 0.055306 | 0.20607 | -0.003531 | 0.046835 | 0.064461 | -0.06093 | -0.025376 | 0.10986 | -0.13876 | -0.17331 | 0.088022 | -122.5324 | 0.06513 | 0.046517 | -0.041505 | -122.5475 | -122.3968 | -0.081753 | -122.6282 | 0.13839 | 0.030623 | 0.11238 | -122.493 | -122.7416 | 0.16199 | 0.14686 | 0.29762 | 0.097538 | -122.6064 | 0.066177 | 0.20141 | -0.047212 | 0.15601 | -122.7762
3541.4219 | 122.7493 | -0.086975 | 122.5571 | 1.4211e-13 | -0.047895 | -0.021823 | -0.079725 | -0.014973 | -0.0044399 | -0.24967 | 0.041589 | 0.019678 | 0.0063882 | 0.052824 | -0.0085312 | -0.012688 | 0.005985 | -0.054192 | 0.079598 | 0.046148 | 0.21522 | 0.037679 | 0.046835 | 0.06904 | -0.06093 | -0.025376 | 0.10986 | -0.12961 | -0.17331 | 0.12465 | -122.4775 | 0.074287 | 0.032783 | -0.091871 | -122.5109 | -122.3418 | -0.086331 | -122.5824 | 0.13381 | 0.026045 | 0.11238 | -122.4472 | -122.6867 | 0.16657 | 0.13312 | 0.3022 | 0.09296 | -122.5194 | 0.061599 | 0.19683 | -0.042632 | 0.15602 | -122.7304
3543.1719 | 122.6898 | -0.068665 | 122.5662 | 1.4211e-13 | -0.048322 | -0.021823 | -0.079512 | -0.014973 | -0.0042263 | -0.24204 | 0.041375 | 0.019251 | 0.0059608 | 0.052824 | -0.0083176 | -0.012688 | 0.005985 | -0.045036 | 0.079598 | 0.046148 | 0.21522 | -0.00811 | 0.037677 | 0.059882 | -0.06093 | -0.025376 | 0.10986 | -0.13419 | -0.16873 | 0.060555 | -122.4866 | 0.055977 | 0.023629 | -0.036926 | -122.5201 | -122.351 | -0.10006 | -122.5916 | 0.10634 | 0.007735 | 0.1078 | -122.4564 | -122.7004 | 0.14826 | 0.11481 | 0.28389 | 0.07465 | -122.5743 | 0.043289 | 0.17852 | -0.065521 | 0.12855 | -122.735
3544.9375 | 122.6303 | -0.10986 | 122.5937 | 1.4211e-13 | -0.048536 | -0.022464 | -0.079512 | -0.01476 | -0.0044399 | -0.23441 | 0.041375 | 0.019464 | 0.0059608 | 0.052824 | -0.0085312 | -0.021844 | 0.010564 | -0.035879 | 0.079598 | 0.041569 | 0.21522 | -0.003531 | 0.046835 | 0.064461 | -0.065509 | -0.020797 | 0.10986 | -0.13876 | -0.16873 | 0.10633 | -122.5141 | 0.088019 | 0.073984 | -0.032348 | -122.5521 | -122.3785 | -0.058865 | -122.6145 | 0.1567 | 0.044354 | 0.10322 | -122.4838 | -122.7325 | 0.18946 | 0.15143 | 0.32509 | 0.12043 | -122.5972 | 0.089066 | 0.21972 | -0.028902 | 0.17432 | -122.7624
3546.6875 | 122.7402 | -0.054932 | 122.5708 | 1.4211e-13 | -0.047895 | -0.022037 | -0.079512 | -0.014973 | -0.0042263 | -0.24204 | 0.041162 | 0.019251 | 0.0055336 | 0.052611 | -0.0085312 | -0.017266 | 0.015142 | -0.054192 | 0.084176 | 0.041569 | 0.21522 | -0.012689 | 0.051413 | 0.059882 | -0.065509 | -0.029954 | 0.10986 | -0.12961 | -0.16873 | 0.042243 | -122.4866 | 0.037666 | 0.00074 | -0.041503 | -122.5292 | -122.3556 | -0.1138 | -122.6008 | 0.10634 | -0.010577 | 0.10322 | -122.4609 | -122.7004 | 0.13911 | 0.096501 | 0.27016 | 0.070074 | -122.5835 | 0.024978 | 0.16479 | -0.074675 | 0.11481 | -122.7395
3548.3906 | 122.7264 | -0.068665 | 122.5571 | 1.4211e-13 | -0.047681 | -0.021823 | -0.079512 | -0.014973 | -0.0040125 | -0.24967 | 0.041162 | 0.019678 | 0.0059608 | 0.053252 | -0.0087448 | -0.012688 | 0.001407 | -0.040457 | 0.070441 | 0.046148 | 0.21064 | 0.028521 | 0.051413 | 0.064461 | -0.051772 | -0.01164 | 0.11444 | -0.12961 | -0.16873 | 0.097186 | -122.4866 | 0.055977 | 0.028208 | -0.068978 | -122.5109 | -122.3464 | -0.10006 | -122.5687 | 0.12008 | 0.016893 | 0.11696 | -122.4426 | -122.6867 | 0.13911 | 0.11481 | 0.27931 | 0.070072 | -122.5285 | 0.057025 | 0.1831 | -0.060942 | 0.13313 | -122.7258
3550.1719 | 122.5937 | -0.12817 | 122.6212 | 1.4211e-13 | -0.048108 | -0.021823 | -0.079725 | -0.015187 | -0.0040125 | -0.23441 | 0.041589 | 0.019678 | 0.0059608 | 0.052824 | -0.0087448 | -0.017266 | -0.003172 | -0.045036 | 0.079598 | 0.041569 | 0.2198 | -0.00811 | 0.046835 | 0.059882 | -0.06093 | -0.025376 | 0.10986 | -0.13419 | -0.16873 | 0.12006 | -122.5416 | 0.11091 | 0.083138 | -0.036926 | -122.5796 | -122.4014 | -0.040554 | -122.6465 | 0.17501 | 0.067244 | 0.1078 | -122.5113 | -122.7553 | 0.20777 | 0.16974 | 0.34798 | 0.125 | -122.6293 | 0.1028 | 0.23803 | -0.006012 | 0.18806 | -122.7899
3551.875 | 122.6578 | -0.086975 | 122.5937 | 1.4211e-13 | -0.048108 | -0.021823 | -0.079725 | -0.014973 | -0.0040125 | -0.24204 | 0.041162 | 0.019037 | 0.0057472 | 0.052611 | -0.0081038 | -0.021844 | 0.005985 | -0.045036 | 0.07502 | 0.046148 | 0.2198 | 0.028521 | 0.042256 | 0.064461 | -0.06093 | -0.020797 | 0.10528 | -0.13419 | -0.16873 | 0.1155 | -122.5187 | 0.065131 | 0.041939 | -0.073557 | -122.5475 | -122.3739 | -0.081753 | -122.6145 | 0.12923 | 0.026045 | 0.1078 | -122.4884 | -122.7279 | 0.162 | 0.13312 | 0.30678 | 0.09296 | -122.5652 | 0.066178 | 0.19225 | -0.047211 | 0.15144 | -122.7624
3553.6406 | 122.7081 | -0.07782 | 122.5891 | 1.4211e-13 | -0.048108 | -0.021823 | -0.079512 | -0.015187 | -0.0042263 | -0.24204 | 0.041162 | 0.019464 | 0.0057472 | 0.052824 | -0.0085312 | -0.017266 | 0.005985 | -0.040457 | 0.070441 | 0.046148 | 0.2198 | 0.023942 | 0.042256 | 0.059882 | -0.065509 | -0.025376 | 0.10986 | -0.12961 | -0.16873 | 0.10176 | -122.5187 | 0.060554 | 0.037363 | -0.064399 | -122.543 | -122.3693 | -0.090908 | -122.6145 | 0.12008 | 0.012311 | 0.10322 | -122.4793 | -122.7187 | 0.14826 | 0.12397 | 0.29762 | 0.083805 | -122.5652 | 0.052444 | 0.18768 | -0.051787 | 0.1377 | -122.7578
3555.3438 | 122.6257 | -0.10071 | 122.612 | 1.4211e-13 | -0.048108 | -0.022037 | -0.079512 | -0.015187 | -0.0042263 | -0.24967 | 0.041375 | 0.019251 | 0.0059608 | 0.053252 | -0.0087448 | -0.017266 | 0.001407 | -0.049614 | 0.079598 | 0.03699 | 0.21522 | -0.017268 | 0.037677 | 0.064461 | -0.065509 | -0.020797 | 0.10528 | -0.13876 | -0.17331 | 0.08344 | -122.5324 | 0.083442 | 0.051094 | -0.032346 | -122.575 | -122.3968 | -0.072598 | -122.6328 | 0.13839 | 0.035199 | 0.1078 | -122.5067 | -122.7508 | 0.18031 | 0.1377 | 0.31593 | 0.10212 | -122.6293 | 0.079911 | 0.20599 | -0.038057 | 0.16517 | -122.7853
3557.0938 | 122.7493 | -0.064087 | 122.5891 | 1.4211e-13 | -0.048322 | -0.022037 | -0.079298 | -0.015187 | -0.0042263 | -0.24204 | 0.041162 | 0.019251 | 0.0057472 | 0.052824 | -0.0087448 | -0.012688 | 0.005985 | -0.045036 | 0.07502 | 0.046148 | 0.22438 | 0.019363 | 0.046835 | 0.059882 | -0.06093 | -0.020797 | 0.1007 | -0.12961 | -0.16873 | 0.08345 | -122.5141 | 0.051399 | 0.019051 | -0.064399 | -122.543 | -122.3647 | -0.10464 | -122.6099 | 0.11092 | 0.003157 | 0.1078 | -122.4884 | -122.7187 | 0.13911 | 0.11023 | 0.28847 | 0.070072 | -122.5697 | 0.04329 | 0.16479 | -0.06552 | 0.12397 | -122.7578
3558.7812 | 122.612 | -0.10071 | 122.6303 | 1.4211e-13 | -0.048322 | -0.021823 | -0.079725 | -0.015401 | -0.0040125 | -0.23441 | 0.041375 | 0.019678 | 0.0055336 | 0.053252 | -0.0087448 | -0.017266 | 0.001407 | -0.045036 | 0.079598 | 0.046148 | 0.2198 | -0.00811 | 0.042256 | 0.059882 | -0.065509 | -0.020797 | 0.1007 | -0.12503 | -0.17788 | 0.092598 | -122.5507 | 0.083442 | 0.055672 | -0.036926 | -122.5842 | -122.4105 | -0.077177 | -122.6511 | 0.14296 | 0.035199 | 0.11238 | -122.5296 | -122.7553 | 0.18031 | 0.14686 | 0.32051 | 0.10212 | -122.6384 | 0.079911 | 0.20141 | -0.024321 | 0.16059 | -122.8082
3560.5312 | 122.7264 | -0.082397 | 122.5983 | 1.4211e-13 | -0.048536 | -0.021823 | -0.079725 | -0.015187 | -0.0044399 | -0.24204 | 0.041375 | 0.019678 | 0.0057472 | 0.052824 | -0.0083176 | -0.017266 | 0.010564 | -0.040457 | 0.070441 | 0.046148 | 0.2198 | -0.044742 | 0.051413 | 0.06904 | -0.06093 | -0.025376 | 0.11444 | -0.11587 | -0.16415 | 0.037655 | -122.5278 | 0.065131 | 0.04194 | 0.004285 | -122.5521 | -122.3785 | -0.081752 | -122.6236 | 0.13381 | 0.021467 | 0.10322 | -122.4838 | -122.7141 | 0.15284 | 0.12854 | 0.3022 | 0.092961 | -122.643 | 0.057021 | 0.19683 | -0.033475 | 0.15144 | -122.7624
3562.2969 | 122.7402 | -0.068665 | 122.58 | 1.4211e-13 | -0.048536 | -0.022037 | -0.079725 | -0.015187 | -0.0044399 | -0.22678 | 0.041375 | 0.019678 | 0.0057472 | 0.052824 | -0.0089584 | -0.012688 | 0.005985 | -0.045036 | 0.07502 | 0.046148 | 0.2198 | -0.044742 | 0.046835 | 0.064461 | -0.06093 | -0.020797 | 0.11444 | -0.13419 | -0.17788 | 0.023923 | -122.5049 | 0.055977 | 0.023629 | -0.000294 | -122.5338 | -122.3602 | -0.10922 | -122.6008 | 0.1155 | 0.007735 | 0.11695 | -122.4655 | -122.7141 | 0.14369 | 0.11481 | 0.28847 | 0.07465 | -122.6247 | 0.047868 | 0.1831 | -0.065521 | 0.13313 | -122.7578
3564.0625 | 122.699 | -0.086975 | 122.5845 | 1.4211e-13 | -0.048322 | -0.022037 | -0.079939 | -0.014973 | -0.0044399 | -0.23441 | 0.041162 | 0.019678 | 0.0055336 | 0.053252 | -0.0083176 | -0.021844 | 0.005985 | -0.045036 | 0.07502 | 0.041569 | 0.21522 | -0.026426 | 0.037677 | 0.064461 | -0.06093 | -0.020797 | 0.10528 | -0.13419 | -0.17331 | 0.060549 | -122.5095 | 0.065131 | 0.041939 | -0.01861 | -122.543 | -122.3693 | -0.086331 | -122.6053 | 0.12465 | 0.026045 | 0.11238 | -122.4793 | -122.7187 | 0.162 | 0.12854 | 0.3022 | 0.09296 | -122.611 | 0.066178 | 0.19225 | -0.047211 | 0.15144 | -122.7578
3565.8438 | 122.6166 | -0.11902 | 122.6349 | 1.4211e-13 | -0.048749 | -0.021823 | -0.079725 | -0.015187 | -0.0048673 | -0.24204 | 0.040948 | 0.019464 | 0.0057472 | 0.053038 | -0.0087448 | -0.017266 | 0.001407 | -0.040457 | 0.07502 | 0.050727 | 0.21064 | -0.044742 | 0.046835 | 0.059882 | -0.06093 | -0.029954 | 0.11444 | -0.12961 | -0.17331 | 0.074277 | -122.5599 | 0.10175 | 0.078562 | 0.004285 | -122.5842 | -122.4242 | -0.054287 | -122.6648 | 0.16585 | 0.058089 | 0.11238 | -122.5205 | -122.7645 | 0.19404 | 0.16975 | 0.32966 | 0.12043 | -122.6796 | 0.089065 | 0.23345 | -0.010588 | 0.1789 | -122.8082
3567.5469 | 122.731 | -0.091553 | 122.5937 | 1.4211e-13 | -0.048322 | -0.021182 | -0.079725 | -0.015614 | -0.0044399 | -0.24204 | 0.041375 | 0.019251 | 0.0057472 | 0.053038 | -0.0083176 | -0.012688 | 0.005985 | -0.035879 | 0.07502 | 0.03699 | 0.21064 | -0.017268 | 0.051413 | 0.059882 | -0.06093 | -0.025376 | 0.11444 | -0.12961 | -0.17331 | 0.074285 | -122.5187 | 0.078865 | 0.055674 | -0.018611 | -122.5567 | -122.383 | -0.081753 | -122.6191 | 0.14297 | 0.030623 | 0.11238 | -122.4793 | -122.7233 | 0.16657 | 0.12854 | 0.3022 | 0.097538 | -122.611 | 0.066177 | 0.20599 | -0.038054 | 0.15143 | -122.767
3569.3125 | 122.7173 | -0.086975 | 122.5937 | 1.4211e-13 | -0.048322 | -0.021609 | -0.079512 | -0.015187 | -0.0044399 | -0.24204 | 0.040948 | 0.019251 | 0.0055336 | 0.053038 | -0.0083176 | -0.017266 | 0.010564 | -0.045036 | 0.079598 | 0.050727 | 0.21522 | 0.001048 | 0.051413 | 0.064461 | -0.065509 | -0.025376 | 0.10528 | -0.13419 | -0.16415 | 0.088023 | -122.5141 | 0.069709 | 0.041939 | -0.046084 | -122.543 | -122.3785 | -0.077174 | -122.6191 | 0.13839 | 0.021466 | 0.09864 | -122.4884 | -122.7279 | 0.16657 | 0.1377 | 0.3022 | 0.097539 | -122.5926 | 0.061599 | 0.19225 | -0.047211 | 0.15144 | -122.7578
3571.0781 | 122.6303 | -0.10529 | 122.6212 | 1.4211e-13 | -0.048322 | -0.021823 | -0.079725 | -0.014973 | -0.0044399 | -0.24204 | 0.041375 | 0.019464 | 0.0057472 | 0.053252 | -0.0078902 | -0.012688 | 0.010564 | -0.045036 | 0.07502 | 0.050727 | 0.21522 | 0.005627 | 0.051413 | 0.059882 | -0.065509 | -0.016219 | 0.11444 | -0.13419 | -0.16873 | 0.11091 | -122.5461 | 0.092598 | 0.06025 | -0.050663 | -122.5704 | -122.4059 | -0.063442 | -122.6374 | 0.1567 | 0.039777 | 0.10322 | -122.5067 | -122.7553 | 0.18031 | 0.15601 | 0.32051 | 0.11585 | -122.6155 | 0.089067 | 0.21972 | -0.0289 | 0.16517 | -122.7899
3572.8438 | 122.6303 | -0.10071 | 122.6624 | 1.4211e-13 | -0.048108 | -0.021609 | -0.079084 | -0.014973 | -0.0044399 | -0.24204 | 0.041162 | 0.019251 | 0.0061744 | 0.053252 | -0.0076766 | -0.017266 | 0.010564 | -0.049614 | 0.07502 | 0.046148 | 0.2198 | -0.040163 | 0.042256 | 0.059882 | -0.065509 | -0.025376 | 0.11444 | -0.12503 | -0.17788 | 0.060545 | -122.5873 | 0.083442 | 0.051094 | -0.009451 | -122.6162 | -122.4426 | -0.077177 | -122.6877 | 0.14296 | 0.035199 | 0.11238 | -122.5479 | -122.7874 | 0.17573 | 0.14686 | 0.32051 | 0.11127 | -122.7025 | 0.075332 | 0.21514 | -0.024321 | 0.16059 | -122.8402
3574.5312 | 122.7219 | -0.082397 | 122.5937 | 1.4211e-13 | -0.048536 | -0.022037 | -0.079512 | -0.015187 | -0.0048673 | -0.24204 | 0.041375 | 0.019464 | 0.0057472 | 0.053465 | -0.0081038 | -0.017266 | 0.005985 | -0.045036 | 0.084176 | 0.046148 | 0.21522 | 0.014784 | 0.046835 | 0.064461 | -0.051772 | -0.029954 | 0.10986 | -0.13876 | -0.16873 | 0.097181 | -122.5095 | 0.065131 | 0.037361 | -0.05982 | -122.5475 | -122.3785 | -0.086331 | -122.6236 | 0.12923 | 0.030625 | 0.11696 | -122.4838 | -122.7325 | 0.16657 | 0.12854 | 0.29762 | 0.088382 | -122.5789 | 0.052443 | 0.19225 | -0.056368 | 0.14686 | -122.7624
3576.3281 | 122.6303 | -0.10986 | 122.6486 | 1.4211e-13 | -0.048536 | -0.022037 | -0.079725 | -0.015187 | -0.0042263 | -0.23441 | 0.041375 | 0.019464 | 0.0059608 | 0.053465 | -0.0076766 | -0.017266 | 0.001407 | -0.045036 | 0.084176 | 0.046148 | 0.21522 | -0.017268 | 0.042256 | 0.064461 | -0.06093 | -0.025376 | 0.10986 | -0.12961 | -0.16415 | 0.092595 | -122.5644 | 0.092597 | 0.064827 | -0.027768 | -122.6025 | -122.4334 | -0.054286 | -122.674 | 0.15212 | 0.048933 | 0.10322 | -122.5388 | -122.7782 | 0.19404 | 0.15601 | 0.32509 | 0.11127 | -122.6659 | 0.084487 | 0.21972 | -0.019744 | 0.17432 | -122.8128
3578.0938 | 122.7264 | -0.091553 | 122.612 | 1.4211e-13 | -0.048749 | -0.022037 | -0.079725 | -0.015187 | -0.0046535 | -0.2573 | 0.041375 | 0.019678 | 0.0057472 | 0.053465 | -0.0081038 | -0.012688 | 0.015142 | -0.049614 | 0.079598 | 0.046148 | 0.2198 | -0.00811 | 0.051413 | 0.064461 | -0.065509 | -0.025376 | 0.11444 | -0.13876 | -0.17331 | 0.083443 | -122.5324 | 0.078865 | 0.041939 | -0.041504 | -122.5659 | -122.3922 | -0.081753 | -122.6374 | 0.14297 | 0.026044 | 0.1078 | -122.4976 | -122.7508 | 0.17115 | 0.1377 | 0.31135 | 0.10669 | -122.6201 | 0.066177 | 0.20599 | -0.047212 | 0.15601 | -122.7853
3579.8594 | 122.6074 | -0.10986 | 122.644 | 1.4211e-13 | -0.048536 | -0.021823 | -0.079512 | -0.015187 | -0.0042263 | -0.23441 | 0.041162 | 0.019251 | 0.0057472 | 0.053252 | -0.0076766 | -0.021844 | 0.005985 | -0.045036 | 0.07502 | 0.041569 | 0.21522 | -0.017268 | 0.042256 | 0.059882 | -0.056351 | -0.025376 | 0.10986 | -0.13419 | -0.16415 | 0.092595 | -122.569 | 0.088019 | 0.064827 | -0.027768 | -122.6025 | -122.4288 | -0.054286 | -122.6694 | 0.15212 | 0.053512 | 0.1078 | -122.5342 | -122.7782 | 0.18488 | 0.15143 | 0.32509 | 0.11585 | -122.6613 | 0.084487 | 0.21972 | -0.024323 | 0.16975 | -122.8082
3581.5625 | 122.7081 | -0.07782 | 122.5937 | 1.4211e-13 | -0.048963 | -0.021823 | -0.079725 | -0.014973 | -0.0044399 | -0.24967 | 0.041162 | 0.019251 | 0.0057472 | 0.053038 | -0.0081038 | -0.021844 | 0.010564 | -0.035879 | 0.093333 | 0.046148 | 0.21522 | 0.023942 | 0.042256 | 0.064461 | -0.06093 | -0.016219 | 0.11444 | -0.12961 | -0.16873 | 0.10176 | -122.5004 | 0.055976 | 0.041941 | -0.059821 | -122.5475 | -122.3785 | -0.090908 | -122.6099 | 0.12008 | 0.01689 | 0.1078 | -122.4793 | -122.7233 | 0.17115 | 0.12397 | 0.29304 | 0.088384 | -122.5697 | 0.061601 | 0.19226 | -0.051787 | 0.14228 | -122.7624
3583.2656 | 122.6624 | -0.10986 | 122.6532 | 1.4211e-13 | -0.048749 | -0.022037 | -0.079512 | -0.015187 | -0.0044399 | -0.22678 | 0.041375 | 0.019464 | 0.0055336 | 0.053038 | -0.0083176 | -0.012688 | 0.010564 | -0.040457 | 0.079598 | 0.046148 | 0.20607 | 0.028521 | 0.042256 | 0.059882 | -0.065509 | -0.016219 | 0.10986 | -0.13419 | -0.17331 | 0.13838 | -122.5736 | 0.097175 | 0.069406 | -0.068978 | -122.6071 | -122.4471 | -0.063443 | -122.6694 | 0.15212 | 0.044354 | 0.1078 | -122.5433 | -122.7874 | 0.18946 | 0.15601 | 0.31593 | 0.12043 | -122.6247 | 0.093644 | 0.21972 | -0.024323 | 0.16975 | -122.8265
3585.0312 | 122.7768 | -0.068665 | 122.5983 | 1.4211e-13 | -0.048322 | -0.021823 | -0.079725 | -0.015401 | -0.0046535 | -0.24204 | 0.041375 | 0.019464 | 0.0057472 | 0.053465 | -0.0078902 | -0.012688 | 0.005985 | -0.049614 | 0.07502 | 0.046148 | 0.21064 | -0.012689 | 0.046835 | 0.064461 | -0.06093 | -0.01164 | 0.11901 | -0.13876 | -0.16873 | 0.055976 | -122.5232 | 0.055977 | 0.019051 | -0.036925 | -122.5521 | -122.3876 | -0.10006 | -122.6099 | 0.1155 | 0.007735 | 0.1078 | -122.4793 | -122.737 | 0.14369 | 0.11481 | 0.27931 | 0.07465 | -122.611 | 0.057025 | 0.18768 | -0.0701 | 0.13313 | -122.767
3586.7969 | 122.7448 | -0.086975 | 122.5983 | 1.4211e-13 | -0.048322 | -0.021823 | -0.080153 | -0.015401 | -0.0044399 | -0.23441 | 0.040948 | 0.019251 | 0.0057472 | 0.053465 | -0.0076766 | -0.008109 | 0.005985 | -0.045036 | 0.079598 | 0.046148 | 0.2198 | 0.042258 | 0.037677 | 0.064461 | -0.06093 | -0.016219 | 0.11444 | -0.12961 | -0.16873 | 0.12923 | -122.5187 | 0.078866 | 0.041939 | -0.087294 | -122.5521 | -122.3785 | -0.081753 | -122.6145 | 0.12465 | 0.026045 | 0.1078 | -122.4838 | -122.7279 | 0.16657 | 0.13312 | 0.30678 | 0.09296 | -122.556 | 0.070756 | 0.20141 | -0.042632 | 0.15144 | -122.767
3588.5625 | 122.6852 | -0.10071 | 122.644 | 1.4211e-13 | -0.048536 | -0.021823 | -0.079512 | -0.014973 | -0.0042263 | -0.23441 | 0.041162 | 0.019464 | 0.0057472 | 0.053465 | -0.0081038 | -0.012688 | 0.005985 | -0.049614 | 0.070441 | 0.046148 | 0.2198 | -0.035584 | 0.037677 | 0.064461 | -0.065509 | -0.020797 | 0.10986 | -0.13419 | -0.16873 | 0.065124 | -122.5736 | 0.08802 | 0.051094 | -0.01403 | -122.5979 | -122.4242 | -0.06802 | -122.6648 | 0.13839 | 0.035199 | 0.10322 | -122.5342 | -122.7782 | 0.17115 | 0.14686 | 0.32051 | 0.10669 | -122.6796 | 0.079911 | 0.21057 | -0.033478 | 0.16517 | -122.8128
3590.3281 | 122.7356 | -0.086975 | 122.6028 | 1.4211e-13 | -0.048749 | -0.02225 | -0.079725 | -0.014973 | -0.0044399 | -0.24204 | 0.041162 | 0.019464 | 0.0057472 | 0.053465 | -0.0081038 | -0.012688 | 0.010564 | -0.049614 | 0.07502 | 0.03699 | 0.21064 | -0.012689 | 0.046835 | 0.073618 | -0.065509 | -0.016219 | 0.10986 | -0.13419 | -0.16873 | 0.074286 | -122.5278 | 0.074287 | 0.037361 | -0.036925 | -122.5659 | -122.3922 | -0.081753 | -122.6191 | 0.13381 | 0.021466 | 0.10322 | -122.493 | -122.737 | 0.162 | 0.12396 | 0.29762 | 0.097539 | -122.6155 | 0.070756 | 0.19683 | -0.047211 | 0.16059 | -122.7716
3592.0312 | 122.6486 | -0.12817 | 122.6349 | 1.4211e-13 | -0.048963 | -0.021823 | -0.079512 | -0.015614 | -0.0042263 | -0.24967 | 0.041162 | 0.019037 | 0.0057472 | 0.053465 | -0.0081038 | -0.017266 | 0.001407 | -0.045036 | 0.079598 | 0.041569 | 0.21522 | 0.014784 | 0.037677 | 0.064461 | -0.051772 | -0.020797 | 0.10986 | -0.12503 | -0.17331 | 0.14296 | -122.5553 | 0.11091 | 0.083138 | -0.05982 | -122.5933 | -122.4197 | -0.045132 | -122.6557 | 0.16585 | 0.076402 | 0.12153 | -122.525 | -122.7599 | 0.20777 | 0.16974 | 0.3434 | 0.12958 | -122.6201 | 0.10738 | 0.23803 | 0.003145 | 0.19264 | -122.8082
3593.7969 | 122.7448 | -0.082397 | 122.6028 | 1.4211e-13 | -0.048963 | -0.021609 | -0.079939 | -0.015401 | -0.0044399 | -0.24967 | 0.041162 | 0.019678 | 0.0055336 | 0.053252 | -0.0081038 | -0.017266 | 0.010564 | -0.045036 | 0.079598 | 0.041569 | 0.21522 | -0.017268 | 0.042256 | 0.064461 | -0.06093 | -0.020797 | 0.10986 | -0.12961 | -0.18246 | 0.065129 | -122.5232 | 0.065131 | 0.037361 | -0.027768 | -122.5613 | -122.3876 | -0.10007 | -122.6236 | 0.12465 | 0.021467 | 0.12153 | -122.493 | -122.7325 | 0.162 | 0.12397 | 0.29762 | 0.092961 | -122.6201 | 0.0616 | 0.19225 | -0.04721 | 0.14686 | -122.7853
3595.5625 | 122.7081 | -0.09613 | 122.6349 | 1.4211e-13 | -0.048749 | -0.021823 | -0.079939 | -0.015401 | -0.0044399 | -0.24204 | 0.041162 | 0.019251 | 0.0055336 | 0.053465 | -0.0081038 | -0.017266 | 0.005985 | -0.045036 | 0.070441 | 0.050727 | 0.21064 | -0.026426 | 0.046835 | 0.064461 | -0.06093 | -0.025376 | 0.11444 | -0.13419 | -0.17331 | 0.069704 | -122.5644 | 0.078864 | 0.051094 | -0.01861 | -122.5842 | -122.4242 | -0.077176 | -122.6603 | 0.14297 | 0.0352 | 0.11238 | -122.5205 | -122.7691 | 0.16657 | 0.14686 | 0.30678 | 0.10211 | -122.6613 | 0.070754 | 0.21057 | -0.038056 | 0.16059 | -122.8082
3597.3281 | 122.6715 | -0.12817 | 122.6807 | 1.4211e-13 | -0.048963 | -0.021823 | -0.079512 | -0.015187 | -0.0046535 | -0.23441 | 0.040948 | 0.019464 | 0.0059608 | 0.053465 | -0.0078902 | -0.012688 | 0.005985 | -0.045036 | 0.079598 | 0.046148 | 0.21522 | -0.021847 | 0.046835 | 0.059882 | -0.06093 | -0.020797 | 0.11444 | -0.12045 | -0.17331 | 0.10633 | -122.6011 | 0.11549 | 0.083138 | -0.023189 | -122.6345 | -122.4654 | -0.045132 | -122.7015 | 0.17501 | 0.067244 | 0.11238 | -122.5662 | -122.8011 | 0.20777 | 0.17432 | 0.3434 | 0.13416 | -122.7025 | 0.10738 | 0.24261 | 0.007724 | 0.18806 | -122.854
3599.0938 | 122.6578 | -0.10071 | 122.644 | 1.4211e-13 | -0.048749 | -0.021609 | -0.079725 | -0.015187 | -0.0042263 | -0.24204 | 0.040734 | 0.019464 | 0.0055336 | 0.053679 | -0.0083176 | -0.017266 | -0.003172 | -0.035879 | 0.07502 | 0.041569 | 0.21064 | 0.014784 | 0.046835 | 0.06904 | -0.056351 | -0.025376 | 0.10986 | -0.12503 | -0.17331 | 0.11549 | -122.569 | 0.083442 | 0.064829 | -0.050663 | -122.6025 | -122.4334 | -0.072598 | -122.6694 | 0.14754 | 0.044357 | 0.11695 | -122.5342 | -122.7691 | 0.17573 | 0.14228 | 0.31135 | 0.097536 | -122.6293 | 0.075332 | 0.21057 | -0.024321 | 0.16975 | -122.8173
3600.7969 | 122.644 | -0.10986 | 122.6761 | 1.4211e-13 | -0.048963 | -0.022037 | -0.079298 | -0.015187 | -0.0046535 | -0.24967 | 0.041162 | 0.019464 | 0.0057472 | 0.053465 | -0.0083176 | -0.026423 | 0.005985 | -0.040457 | 0.084176 | 0.041569 | 0.21522 | 0.005627 | 0.042256 | 0.059882 | -0.06093 | -0.020797 | 0.10986 | -0.13419 | -0.16415 | 0.11549 | -122.5919 | 0.08344 | 0.069406 | -0.046084 | -122.6345 | -122.4609 | -0.054286 | -122.6969 | 0.15212 | 0.048933 | 0.10322 | -122.5662 | -122.8103 | 0.19404 | 0.15143 | 0.32509 | 0.11585 | -122.6705 | 0.089066 | 0.21972 | -0.024323 | 0.16975 | -122.8402
3602.5625 | 122.644 | -0.11444 | 122.6852 | 1.4211e-13 | -0.048749 | -0.022037 | -0.079298 | -0.015401 | -0.0046535 | -0.23441 | 0.040948 | 0.019464 | 0.0057472 | 0.053679 | -0.0083176 | -0.017266 | 0.005985 | -0.045036 | 0.07502 | 0.046148 | 0.22438 | 0.042258 | 0.042256 | 0.059882 | -0.056351 | -0.020797 | 0.10986 | -0.13419 | -0.17788 | 0.1567 | -122.6102 | 0.097175 | 0.069405 | -0.087294 | -122.6391 | -122.4609 | -0.063444 | -122.706 | 0.1567 | 0.05809 | 0.12153 | -122.5754 | -122.8194 | 0.18946 | 0.16059 | 0.33882 | 0.12043 | -122.643 | 0.093644 | 0.2243 | -0.019745 | 0.17432 | -122.8631
3604.2656 | 122.731 | -0.091553 | 122.6212 | 1.4211e-13 | -0.048963 | -0.022037 | -0.079512 | -0.015401 | -0.0046535 | -0.24204 | 0.041162 | 0.019678 | 0.0055336 | 0.053679 | -0.0085312 | -0.012688 | 0.015142 | -0.045036 | 0.07502 | 0.050727 | 0.22438 | 0.001048 | 0.042256 | 0.06904 | -0.070087 | -0.016219 | 0.10986 | -0.13876 | -0.17788 | 0.092601 | -122.5461 | 0.078865 | 0.046517 | -0.046084 | -122.5704 | -122.3968 | -0.086332 | -122.6374 | 0.13381 | 0.021466 | 0.1078 | -122.5113 | -122.7599 | 0.16657 | 0.14228 | 0.31593 | 0.10669 | -122.6201 | 0.075334 | 0.20141 | -0.047212 | 0.16059 | -122.799
3606.0312 | 122.7402 | -0.082397 | 122.6212 | 1.4211e-13 | -0.048963 | -0.022037 | -0.079298 | -0.01476 | -0.0044399 | -0.24204 | 0.040948 | 0.019464 | 0.0055336 | 0.053252 | -0.0085312 | -0.017266 | 0.015142 | -0.040457 | 0.079598 | 0.055306 | 0.21522 | 0.014784 | 0.046835 | 0.059882 | -0.051772 | -0.025376 | 0.10986 | -0.11587 | -0.17331 | 0.097181 | -122.5416 | 0.065131 | 0.04194 | -0.055241 | -122.5658 | -122.4059 | -0.090909 | -122.6465 | 0.12923 | 0.030625 | 0.12153 | -122.5113 | -122.737 | 0.162 | 0.1377 | 0.29762 | 0.097539 | -122.6064 | 0.057021 | 0.19225 | -0.033475 | 0.14228 | -122.7945
3607.7812 | 122.731 | -0.086975 | 122.6074 | 1.4211e-13 | -0.048749 | -0.022037 | -0.079084 | -0.015614 | -0.0048673 | -0.24204 | 0.041162 | 0.019464 | 0.0055336 | 0.053465 | -0.0085312 | -0.021844 | 0.010564 | -0.049614 | 0.084176 | 0.046148 | 0.21522 | 0.010206 | 0.046835 | 0.06904 | -0.06093 | -0.025376 | 0.11444 | -0.13876 | -0.17331 | 0.097181 | -122.5232 | 0.065131 | 0.037361 | -0.05982 | -122.5613 | -122.3922 | -0.086331 | -122.6328 | 0.13381 | 0.026045 | 0.11238 | -122.493 | -122.7462 | 0.17115 | 0.13312 | 0.3022 | 0.097539 | -122.5972 | 0.061599 | 0.20141 | -0.05179 | 0.15602 | -122.7807
3609.5312 | 122.7905 | -0.073242 | 122.5891 | 1.4211e-13 | -0.048963 | -0.022037 | -0.079298 | -0.015187 | -0.0044399 | -0.23441 | 0.041162 | 0.019251 | 0.0053198 | 0.053679 | -0.0083176 | -0.017266 | 0.005985 | -0.040457 | 0.079598 | 0.041569 | 0.2198 | 0.005627 | 0.042256 | 0.064461 | -0.056351 | -0.020797 | 0.1007 | -0.13876 | -0.16873 | 0.078869 | -122.5095 | 0.055976 | 0.032785 | -0.046084 | -122.5475 | -122.3693 | -0.095486 | -122.6099 | 0.1155 | 0.016891 | 0.11238 | -122.4884 | -122.7279 | 0.15284 | 0.11481 | 0.29304 | 0.079227 | -122.5835 | 0.052445 | 0.17394 | -0.065523 | 0.1377 | -122.7578
3611.2969 | 122.7402 | -0.086975 | 122.6166 | 1.4211e-13 | -0.048963 | -0.022037 | -0.079084 | -0.015401 | -0.0044399 | -0.23441 | 0.040948 | 0.019464 | 0.0057472 | 0.053679 | -0.0089584 | -0.017266 | 0.010564 | -0.054192 | 0.079598 | 0.050727 | 0.2198 | 0.019363 | 0.042256 | 0.059882 | -0.06093 | -0.020797 | 0.1007 | -0.12961 | -0.17331 | 0.10634 | -122.537 | 0.069709 | 0.032783 | -0.073555 | -122.5659 | -122.3968 | -0.086331 | -122.6374 | 0.12923 | 0.026045 | 0.11238 | -122.5159 | -122.7462 | 0.16657 | 0.1377 | 0.30678 | 0.097539 | -122.5972 | 0.066178 | 0.18767 | -0.042632 | 0.14686 | -122.7899
3613.0469 | 122.7951 | -0.068665 | 122.6074 | 1.4211e-13 | -0.048749 | -0.022037 | -0.079512 | -0.015187 | -0.0044399 | -0.24967 | 0.040948 | 0.018823 | 0.0057472 | 0.053679 | -0.0083176 | -0.008109 | 0.010564 | -0.045036 | 0.07502 | 0.046148 | 0.21522 | 0.023942 | 0.037677 | 0.06904 | -0.06093 | -0.016219 | 0.11444 | -0.13876 | -0.16415 | 0.092607 | -122.5324 | 0.060556 | 0.023629 | -0.068978 | -122.5613 | -122.3922 | -0.095484 | -122.6236 | 0.10634 | 0.007735 | 0.10322 | -122.493 | -122.7462 | 0.14369 | 0.11481 | 0.28389 | 0.079229 | -122.5835 | 0.052446 | 0.1831 | -0.0701 | 0.13771 | -122.7716
3614.8125 | 122.6852 | -0.10529 | 122.6624 | 1.4211e-13 | -0.048749 | -0.021609 | -0.079512 | -0.015401 | -0.0044399 | -0.24967 | 0.040948 | 0.019037 | 0.0057472 | 0.053679 | -0.0083176 | -0.017266 | 0.015142 | -0.040457 | 0.079598 | 0.041569 | 0.2198 | 0.0331 | 0.042256 | 0.064461 | -0.06093 | -0.029954 | 0.10528 | -0.12961 | -0.16873 | 0.13839 | -122.5828 | 0.08802 | 0.064829 | -0.073557 | -122.6208 | -122.4426 | -0.063442 | -122.6923 | 0.14754 | 0.044356 | 0.1078 | -122.5571 | -122.792 | 0.18488 | 0.14686 | 0.32509 | 0.12043 | -122.6293 | 0.075332 | 0.21057 | -0.024321 | 0.16975 | -122.8311
3616.5312 | 122.6852 | -0.10071 | 122.6532 | 1.4211e-13 | -0.048749 | -0.022037 | -0.079512 | -0.015401 | -0.0044399 | -0.24967 | 0.040734 | 0.019037 | 0.0057472 | 0.053679 | -0.0085312 | -0.012688 | 0.001407 | -0.054192 | 0.079598 | 0.041569 | 0.2198 | -0.003531 | 0.042256 | 0.059882 | -0.06093 | -0.020797 | 0.11444 | -0.12961 | -0.17331 | 0.097177 | -122.5736 | 0.08802 | 0.046516 | -0.050661 | -122.6116 | -122.4334 | -0.072598 | -122.674 | 0.14296 | 0.039778 | 0.11238 | -122.5388 | -122.7828 | 0.18031 | 0.14228 | 0.32051 | 0.10212 | -122.6567 | 0.079911 | 0.21514 | -0.028899 | 0.16059 | -122.8265
3618.2969 | 122.7722 | -0.086975 | 122.6166 | 1.4211e-13 | -0.049177 | -0.022037 | -0.079512 | -0.015401 | -0.0046535 | -0.24967 | 0.041162 | 0.019464 | 0.0055336 | 0.053679 | -0.0081038 | -0.012688 | 0.010564 | -0.040457 | 0.084176 | 0.041569 | 0.21064 | -0.035584 | 0.051413 | 0.06904 | -0.06093 | -0.016219 | 0.11444 | -0.14334 | -0.17788 | 0.051391 | -122.5324 | 0.074287 | 0.046518 | -0.004873 | -122.575 | -122.4059 | -0.09091 | -122.6328 | 0.13839 | 0.026045 | 0.11695 | -122.5021 | -122.7599 | 0.17115 | 0.12854 | 0.29762 | 0.097539 | -122.6522 | 0.070756 | 0.20141 | -0.056368 | 0.15602 | -122.7945
3620.0625 | 122.7768 | -0.082397 | 122.6257 | 1.4211e-13 | -0.048749 | -0.022037 | -0.079512 | -0.015401 | -0.0044399 | -0.23441 | 0.041375 | 0.018823 | 0.0053198 | 0.053893 | -0.0085312 | -0.017266 | 0.010564 | -0.040457 | 0.079598 | 0.046148 | 0.2198 | 0.001048 | 0.046835 | 0.06904 | -0.06093 | -0.016219 | 0.10986 | -0.12503 | -0.17331 | 0.083445 | -122.5461 | 0.065131 | 0.04194 | -0.041505 | -122.5796 | -122.4059 | -0.090909 | -122.642 | 0.12923 | 0.021467 | 0.11238 | -122.5159 | -122.7508 | 0.162 | 0.12854 | 0.3022 | 0.092961 | -122.6247 | 0.066178 | 0.19225 | -0.042632 | 0.15144 | -122.799
3621.7656 | 122.818 | -0.068665 | 122.6395 | 1.4211e-13 | -0.049177 | -0.022037 | -0.079298 | -0.01476 | -0.0046535 | -0.24204 | 0.041162 | 0.019464 | 0.0055336 | 0.053252 | -0.0085312 | -0.017266 | 0.010564 | -0.040457 | 0.079598 | 0.041569 | 0.2198 | 0.023942 | 0.046835 | 0.064461 | -0.06093 | -0.020797 | 0.10986 | -0.13419 | -0.17788 | 0.092607 | -122.5599 | 0.051399 | 0.028208 | -0.064399 | -122.5979 | -122.4197 | -0.10922 | -122.6603 | 0.1155 | 0.007735 | 0.11695 | -122.5296 | -122.7737 | 0.14826 | 0.11023 | 0.28847 | 0.079229 | -122.6155 | 0.047868 | 0.17852 | -0.065521 | 0.13313 | -122.8174
3623.5312 | 122.7951 | -0.064087 | 122.6303 | 1.4211e-13 | -0.048963 | -0.022037 | -0.079298 | -0.015614 | -0.0050809 | -0.24204 | 0.040734 | 0.019251 | 0.0057472 | 0.053679 | -0.0085312 | -0.008109 | 0.010564 | -0.049614 | 0.079598 | 0.041569 | 0.2198 | 0.0331 | 0.046835 | 0.064461 | -0.06093 | -0.020797 | 0.11444 | -0.14334 | -0.17788 | 0.097187 | -122.5507 | 0.055978 | 0.014473 | -0.082714 | -122.5887 | -122.4105 | -0.1138 | -122.6511 | 0.11092 | 0.003157 | 0.11695 | -122.5159 | -122.7737 | 0.14369 | 0.10566 | 0.28389 | 0.074651 | -122.5972 | 0.04329 | 0.17852 | -0.079256 | 0.12855 | -122.8082
3625.2188 | 122.6624 | -0.10986 | 122.6807 | 1.4211e-13 | -0.048963 | -0.02225 | -0.079512 | -0.014973 | -0.0046535 | -0.22678 | 0.041162 | 0.019037 | 0.0057472 | 0.053679 | -0.0085312 | -0.021844 | 0.010564 | -0.035879 | 0.079598 | 0.041569 | 0.21522 | -0.003531 | 0.046835 | 0.059882 | -0.056351 | -0.016219 | 0.11444 | -0.13876 | -0.17331 | 0.10633 | -122.6011 | 0.088019 | 0.073984 | -0.032348 | -122.6391 | -122.4654 | -0.063443 | -122.6969 | 0.1567 | 0.053512 | 0.11695 | -122.5662 | -122.8194 | 0.18946 | 0.15143 | 0.32509 | 0.12043 | -122.6842 | 0.093644 | 0.2243 | -0.028902 | 0.16975 | -122.854
3626.9844 | 122.7036 | -0.086975 | 122.6624 | 1.4211e-13 | -0.049177 | -0.021823 | -0.079298 | -0.015614 | -0.0048673 | -0.24967 | 0.040948 | 0.019251 | 0.0061744 | 0.053679 | -0.0083176 | -0.012688 | 0.010564 | -0.049614 | 0.07502 | 0.050727 | 0.21522 | 0.014784 | 0.051413 | 0.059882 | -0.065509 | -0.020797 | 0.11444 | -0.13419 | -0.17331 | 0.10176 | -122.5873 | 0.074287 | 0.037361 | -0.064398 | -122.6116 | -122.4471 | -0.086331 | -122.6832 | 0.13839 | 0.021466 | 0.1078 | -122.5479 | -122.7965 | 0.162 | 0.1377 | 0.3022 | 0.097539 | -122.6476 | 0.066178 | 0.20141 | -0.047211 | 0.14686 | -122.8357
3628.75 | 122.7173 | -0.10529 | 122.6395 | 1.4211e-13 | -0.04939 | -0.022464 | -0.079298 | -0.015187 | -0.0046535 | -0.24204 | 0.041162 | 0.019251 | 0.0053198 | 0.053679 | -0.0081038 | -0.012688 | 0.010564 | -0.035879 | 0.079598 | 0.050727 | 0.22438 | 0.014784 | 0.042256 | 0.055303 | -0.065509 | -0.020797 | 0.10986 | -0.13876 | -0.17788 | 0.12007 | -122.5599 | 0.092598 | 0.069407 | -0.050663 | -122.5887 | -122.4151 | -0.072599 | -122.6603 | 0.14754 | 0.039777 | 0.11238 | -122.5296 | -122.7782 | 0.18488 | 0.15601 | 0.32967 | 0.11585 | -122.6247 | 0.084489 | 0.21514 | -0.033479 | 0.16059 | -122.8174
3630.5156 | 122.6669 | -0.1236 | 122.6761 | 1.4211e-13 | -0.048963 | -0.022037 | -0.079298 | -0.015187 | -0.0046535 | -0.23441 | 0.040734 | 0.019251 | 0.0053198 | 0.053893 | -0.0085312 | -0.017266 | 0.005985 | -0.054192 | 0.079598 | 0.041569 | 0.2198 | 0.010206 | 0.051413 | 0.059882 | -0.056351 | -0.01164 | 0.10986 | -0.13876 | -0.16873 | 0.1338 | -122.5965 | 0.10633 | 0.069404 | -0.064398 | -122.6345 | -122.4563 | -0.045132 | -122.6877 | 0.17501 | 0.067245 | 0.11238 | -122.5662 | -122.8149 | 0.20319 | 0.16517 | 0.3434 | 0.12958 | -122.6659 | 0.11196 | 0.23345 | -0.015169 | 0.18348 | -122.8448
3632.2812 | 122.7859 | -0.045776 | 122.6624 | 1.4211e-13 | -0.049177 | -0.021823 | -0.079512 | -0.015401 | -0.0048673 | -0.24967 | 0.040734 | 0.019464 | 0.0055336 | 0.053465 | -0.0085312 | -0.017266 | 0.005985 | -0.045036 | 0.079598 | 0.050727 | 0.21522 | 0.023942 | 0.042256 | 0.064461 | -0.06093 | -0.01164 | 0.10986 | -0.12961 | -0.18246 | 0.069718 | -122.5828 | 0.02851 | 0.00074 | -0.068978 | -122.6116 | -122.4471 | -0.13669 | -122.674 | 0.088032 | -0.015154 | 0.12153 | -122.5525 | -122.792 | 0.12537 | 0.096503 | 0.261 | 0.051761 | -122.6384 | 0.034136 | 0.15563 | -0.083831 | 0.11024 | -122.8448
3634.0469 | 122.7539 | -0.07782 | 122.6761 | 1.4211e-13 | -0.048963 | -0.022037 | -0.079298 | -0.015401 | -0.0048673 | -0.24204 | 0.040734 | 0.019037 | 0.0053198 | 0.053679 | -0.0085312 | -0.017266 | 0.005985 | -0.049614 | 0.079598 | 0.03699 | 0.2198 | 0.023942 | 0.042256 | 0.059882 | -0.06093 | -0.020797 | 0.10528 | -0.13419 | -0.17331 | 0.10176 | -122.5965 | 0.060554 | 0.028206 | -0.073556 | -122.6391 | -122.4563 | -0.095486 | -122.6969 | 0.12008 | 0.01689 | 0.11238 | -122.5708 | -122.8103 | 0.15742 | 0.11481 | 0.29762 | 0.083805 | -122.6521 | 0.057023 | 0.1831 | -0.056366 | 0.1377 | -122.8494
3635.8125 | 122.8043 | -0.041199 | 122.6349 | 1.4211e-13 | -0.049177 | -0.021609 | -0.079298 | -0.015187 | -0.0048673 | -0.23441 | 0.040948 | 0.019037 | 0.0053198 | 0.053679 | -0.0085312 | -0.012688 | 0.005985 | -0.045036 | 0.079598 | 0.046148 | 0.2198 | 0.037679 | 0.042256 | 0.064461 | -0.065509 | -0.016219 | 0.10986 | -0.13876 | -0.17331 | 0.078878 | -122.5553 | 0.028511 | -0.003837 | -0.082715 | -122.5887 | -122.4151 | -0.13211 | -122.6511 | 0.083455 | -0.02431 | 0.1078 | -122.525 | -122.7737 | 0.1208 | 0.087347 | 0.261 | 0.047184 | -122.5972 | 0.02498 | 0.15106 | -0.097566 | 0.10566 | -122.8082
3637.5 | 122.699 | -0.11444 | 122.6807 | 1.4211e-13 | -0.049604 | -0.022037 | -0.079512 | -0.015614 | -0.0046535 | -0.24204 | 0.040948 | 0.019037 | 0.0055336 | 0.053679 | -0.0085312 | -0.021844 | 0.005985 | -0.035879 | 0.07502 | 0.03699 | 0.2198 | -0.00811 | 0.042256 | 0.050725 | -0.056351 | -0.020797 | 0.10986 | -0.12961 | -0.17788 | 0.10633 | -122.6056 | 0.092597 | 0.078562 | -0.027769 | -122.6437 | -122.4609 | -0.063444 | -122.7015 | 0.1567 | 0.05809 | 0.12153 | -122.5708 | -122.8103 | 0.18946 | 0.15143 | 0.33424 | 0.12043 | -122.6888 | 0.093644 | 0.2243 | -0.015166 | 0.16517 | -122.8585
3639.2031 | 122.6898 | -0.11902 | 122.6715 | 1.4211e-13 | -0.048963 | -0.021823 | -0.079298 | -0.015401 | -0.0046535 | -0.24204 | 0.040734 | 0.019251 | 0.0055336 | 0.053893 | -0.0087448 | -0.012688 | 0.010564 | -0.040457 | 0.070441 | 0.046148 | 0.21522 | -0.00811 | 0.042256 | 0.055303 | -0.056351 | -0.016219 | 0.10528 | -0.13419 | -0.17331 | 0.11091 | -122.6011 | 0.10633 | 0.078562 | -0.032347 | -122.6254 | -122.4563 | -0.054287 | -122.6877 | 0.16128 | 0.062668 | 0.11695 | -122.5662 | -122.8057 | 0.18946 | 0.16517 | 0.33424 | 0.12958 | -122.6796 | 0.1028 | 0.2243 | -0.015167 | 0.17432 | -122.8448
3640.9688 | 122.818 | -0.068665 | 122.6486 | 1.4211e-13 | -0.049177 | -0.022037 | -0.079298 | -0.015401 | -0.0048673 | -0.24204 | 0.040734 | 0.019037 | 0.0053198 | 0.053679 | -0.0087448 | -0.008109 | 0.010564 | -0.045036 | 0.084176 | 0.041569 | 0.2198 | -0.012689 | 0.046835 | 0.064461 | -0.065509 | -0.020797 | 0.1007 | -0.12503 | -0.17331 | 0.055976 | -122.5644 | 0.060556 | 0.023629 | -0.032347 | -122.6071 | -122.4288 | -0.10464 | -122.6694 | 0.1155 | 0.003156 | 0.1078 | -122.5479 | -122.7737 | 0.15284 | 0.11023 | 0.28847 | 0.079229 | -122.6613 | 0.047868 | 0.16936 | -0.056364 | 0.13313 | -122.8219
3642.7188 | 122.6898 | -0.11902 | 122.6715 | 1.4211e-13 | -0.04939 | -0.02225 | -0.079298 | -0.015614 | -0.0048673 | -0.24204 | 0.040734 | 0.019037 | 0.0053198 | 0.053679 | -0.0085312 | -0.021844 | 0.005985 | -0.040457 | 0.084176 | 0.046148 | 0.21522 | -0.035584 | 0.046835 | 0.059882 | -0.065509 | -0.016219 | 0.11901 | -0.13419 | -0.17788 | 0.083435 | -122.5873 | 0.097175 | 0.078562 | -0.004873 | -122.6254 | -122.4563 | -0.058866 | -122.6877 | 0.16585 | 0.05351 | 0.11238 | -122.5525 | -122.8057 | 0.2032 | 0.16517 | 0.33424 | 0.125 | -122.7071 | 0.1028 | 0.23803 | -0.015167 | 0.1789 | -122.8494
3644.4688 | 122.6715 | -0.1236 | 122.699 | 1.4211e-13 | -0.04939 | -0.022037 | -0.079512 | -0.015187 | -0.0046535 | -0.24204 | 0.040948 | 0.019037 | 0.0051062 | 0.054106 | -0.0087448 | -0.017266 | 0.005985 | -0.045036 | 0.079598 | 0.050727 | 0.21522 | -0.026426 | 0.046835 | 0.059882 | -0.065509 | -0.025376 | 0.10986 | -0.13419 | -0.17788 | 0.09717 | -122.6194 | 0.10633 | 0.07856 | -0.01861 | -122.6482 | -122.4838 | -0.054289 | -122.7244 | 0.17043 | 0.058087 | 0.11238 | -122.5891 | -122.8332 | 0.20319 | 0.17432 | 0.33882 | 0.12958 | -122.7254 | 0.09822 | 0.23345 | -0.01059 | 0.18348 | -122.8769
3646.2344 | 122.7173 | -0.11444 | 122.699 | 1.4211e-13 | -0.04939 | -0.022037 | -0.079298 | -0.015401 | -0.0050809 | -0.22678 | 0.040734 | 0.019251 | 0.0053198 | 0.054106 | -0.0085312 | -0.021844 | -0.003172 | -0.045036 | 0.07502 | 0.046148 | 0.2198 | -0.00811 | 0.046835 | 0.059882 | -0.06093 | -0.020797 | 0.10528 | -0.13876 | -0.17331 | 0.10633 | -122.624 | 0.092597 | 0.069405 | -0.036926 | -122.6528 | -122.4792 | -0.058865 | -122.7198 | 0.16128 | 0.053511 | 0.11238 | -122.5937 | -122.8377 | 0.18946 | 0.16059 | 0.33424 | 0.11127 | -122.7071 | 0.093644 | 0.21972 | -0.024324 | 0.17432 | -122.8723
3647.9375 | 122.8043 | -0.073242 | 122.6532 | 1.4211e-13 | -0.04939 | -0.022037 | -0.079298 | -0.015401 | -0.0048673 | -0.24204 | 0.041162 | 0.018823 | 0.0055336 | 0.05432 | -0.0085312 | -0.017266 | 0.005985 | -0.045036 | 0.084176 | 0.050727 | 0.21522 | 0.005627 | 0.042256 | 0.055303 | -0.051772 | -0.025376 | 0.10986 | -0.12503 | -0.17331 | 0.078869 | -122.569 | 0.055976 | 0.028206 | -0.050663 | -122.6025 | -122.438 | -0.10006 | -122.6786 | 0.1155 | 0.02147 | 0.12153 | -122.5433 | -122.7782 | 0.15742 | 0.12397 | 0.28847 | 0.079227 | -122.6476 | 0.047866 | 0.1831 | -0.051787 | 0.12854 | -122.8265
3649.7031 | 122.7585 | -0.091553 | 122.6532 | 1.4211e-13 | -0.049604 | -0.022037 | -0.079084 | -0.015614 | -0.0048673 | -0.23441 | 0.040521 | 0.019037 | 0.0053198 | 0.054106 | -0.0085312 | -0.026423 | 0.010564 | -0.040457 | 0.084176 | 0.041569 | 0.2198 | 0.010206 | 0.046835 | 0.059882 | -0.056351 | -0.020797 | 0.11444 | -0.12961 | -0.17331 | 0.10176 | -122.569 | 0.06513 | 0.051096 | -0.050663 | -122.6116 | -122.4334 | -0.081753 | -122.674 | 0.13839 | 0.035202 | 0.11695 | -122.5388 | -122.7828 | 0.17573 | 0.13312 | 0.31135 | 0.10212 | -122.643 | 0.070756 | 0.20599 | -0.038054 | 0.15143 | -122.8265
3651.4844 | 122.6807 | -0.10071 | 122.6624 | 1.4211e-13 | -0.049604 | -0.02225 | -0.079298 | -0.015401 | -0.0048673 | -0.23441 | 0.040948 | 0.019037 | 0.0053198 | 0.054106 | -0.0089584 | -0.017266 | 0.010564 | -0.045036 | 0.084176 | 0.050727 | 0.2198 | 0.019363 | 0.042256 | 0.06904 | -0.06093 | -0.016219 | 0.11444 | -0.13419 | -0.16873 | 0.12007 | -122.5782 | 0.083442 | 0.055672 | -0.064399 | -122.6116 | -122.4426 | -0.06802 | -122.6786 | 0.14296 | 0.039778 | 0.1078 | -122.5479 | -122.7965 | 0.18488 | 0.15144 | 0.32051 | 0.11127 | -122.643 | 0.084489 | 0.21514 | -0.033478 | 0.16975 | -122.8311
3653.25 | 122.7951 | -0.059509 | 122.6624 | 1.4211e-13 | -0.049604 | -0.021823 | -0.079298 | -0.015187 | -0.0044399 | -0.23441 | 0.040734 | 0.019037 | 0.0053198 | 0.054106 | -0.0087448 | -0.021844 | 0.010564 | -0.040457 | 0.079598 | 0.050727 | 0.2198 | -0.040163 | 0.046835 | 0.059882 | -0.056351 | -0.025376 | 0.10986 | -0.11129 | -0.16873 | 0.019346 | -122.5828 | 0.037665 | 0.019052 | -0.000294 | -122.6116 | -122.4426 | -0.10922 | -122.6877 | 0.10634 | 0.003158 | 0.11238 | -122.5525 | -122.7736 | 0.13911 | 0.11024 | 0.27931 | 0.070073 | -122.7025 | 0.034133 | 0.16937 | -0.051784 | 0.11939 | -122.8311
3654.9531 | 122.7585 | -0.073242 | 122.6807 | 1.4211e-13 | -0.049604 | -0.022037 | -0.07887 | -0.015401 | -0.0048673 | -0.24967 | 0.040734 | 0.018823 | 0.0053198 | 0.053893 | -0.0089584 | -0.017266 | 0.005985 | -0.035879 | 0.079598 | 0.046148 | 0.21064 | -0.035584 | 0.042256 | 0.064461 | -0.051772 | -0.016219 | 0.10528 | -0.12961 | -0.17331 | 0.037658 | -122.6011 | 0.055976 | 0.037363 | -0.000295 | -122.6345 | -122.47 | -0.10006 | -122.6969 | 0.1155 | 0.02147 | 0.12153 | -122.5754 | -122.8103 | 0.15284 | 0.11939 | 0.28389 | 0.079227 | -122.7162 | 0.057023 | 0.17852 | -0.056365 | 0.1377 | -122.854
3656.7344 | 122.7905 | -0.07782 | 122.6761 | 1.4211e-13 | -0.04939 | -0.022037 | -0.079512 | -0.015187 | -0.0046535 | -0.24967 | 0.040948 | 0.019037 | 0.0053198 | 0.053893 | -0.0087448 | -0.021844 | 0.001407 | -0.045036 | 0.079598 | 0.050727 | 0.21522 | 0.014784 | 0.037677 | 0.059882 | -0.065509 | -0.020797 | 0.11444 | -0.12045 | -0.17331 | 0.092604 | -122.5965 | 0.055976 | 0.032784 | -0.05982 | -122.6254 | -122.4609 | -0.095486 | -122.6969 | 0.1155 | 0.012311 | 0.1078 | -122.5617 | -122.7965 | 0.15742 | 0.12855 | 0.29304 | 0.079227 | -122.6613 | 0.057023 | 0.19226 | -0.04263 | 0.1377 | -122.8494
3658.4375 | 122.699 | -0.11444 | 122.6761 | 1.4211e-13 | -0.049604 | -0.022037 | -0.079084 | -0.015401 | -0.0048673 | -0.24204 | 0.040307 | 0.019037 | 0.0053198 | 0.053893 | -0.0089584 | -0.012688 | 0.019721 | -0.045036 | 0.079598 | 0.041569 | 0.21522 | -0.021847 | 0.046835 | 0.055303 | -0.056351 | -0.020797 | 0.10986 | -0.13419 | -0.16873 | 0.092594 | -122.5965 | 0.10175 | 0.069405 | -0.023189 | -122.6345 | -122.4609 | -0.054287 | -122.6969 | 0.16128 | 0.05809 | 0.11238 | -122.5662 | -122.8103 | 0.19404 | 0.15601 | 0.32966 | 0.13416 | -122.6979 | 0.093644 | 0.2243 | -0.019745 | 0.16974 | -122.8448
3660.1875 | 122.6761 | -0.10529 | 122.6898 | 1.4211e-13 | -0.049604 | -0.022037 | -0.079512 | -0.015401 | -0.0048673 | -0.24204 | 0.040948 | 0.019251 | 0.0057472 | 0.054534 | -0.0085312 | -0.017266 | 0.005985 | -0.045036 | 0.065863 | 0.055306 | 0.2198 | -0.012689 | 0.051413 | 0.064461 | -0.065509 | -0.025376 | 0.10986 | -0.13419 | -0.16873 | 0.092597 | -122.624 | 0.08802 | 0.06025 | -0.032347 | -122.6345 | -122.47 | -0.063442 | -122.7152 | 0.1567 | 0.039777 | 0.10322 | -122.58 | -122.824 | 0.17115 | 0.16059 | 0.32509 | 0.11127 | -122.7025 | 0.07991 | 0.21514 | -0.0289 | 0.16975 | -122.8585
3661.8906 | 122.6852 | -0.12817 | 122.6807 | 1.4211e-13 | -0.049604 | -0.022037 | -0.079298 | -0.015401 | -0.0048673 | -0.24204 | 0.040734 | 0.018823 | 0.0053198 | 0.054106 | -0.0091722 | -0.021844 | 0.001407 | -0.040457 | 0.07502 | 0.050727 | 0.2198 | 0.005627 | 0.042256 | 0.064461 | -0.06093 | -0.016219 | 0.11444 | -0.13876 | -0.17788 | 0.1338 | -122.6056 | 0.10633 | 0.087717 | -0.046084 | -122.6299 | -122.4609 | -0.049711 | -122.6969 | 0.17043 | 0.067244 | 0.11695 | -122.5662 | -122.8194 | 0.20319 | 0.1789 | 0.34798 | 0.12958 | -122.675 | 0.11196 | 0.24261 | -0.010591 | 0.19264 | -122.8585
3663.6562 | 122.8134 | -0.073242 | 122.6532 | 1.4211e-13 | -0.049818 | -0.022037 | -0.079298 | -0.015401 | -0.0046535 | -0.24204 | 0.040521 | 0.019037 | 0.0053198 | 0.053893 | -0.0085312 | -0.017266 | 0.010564 | -0.045036 | 0.079598 | 0.050727 | 0.21522 | 0.001048 | 0.042256 | 0.059882 | -0.06093 | -0.020797 | 0.11444 | -0.13876 | -0.17788 | 0.07429 | -122.5736 | 0.055976 | 0.028206 | -0.046084 | -122.6025 | -122.438 | -0.10464 | -122.674 | 0.1155 | 0.012312 | 0.11695 | -122.5388 | -122.792 | 0.15284 | 0.12397 | 0.28847 | 0.083806 | -122.6522 | 0.052445 | 0.18768 | -0.065523 | 0.13312 | -122.8311
3665.4062 | 122.7539 | -0.086975 | 122.644 | 1.4211e-13 | -0.049818 | -0.02225 | -0.079512 | -0.015401 | -0.0046535 | -0.24204 | 0.040948 | 0.018823 | 0.0051062 | 0.054106 | -0.0089584 | -0.012688 | 0.010564 | -0.040457 | 0.084176 | 0.050727 | 0.22438 | 0.046837 | 0.046835 | 0.055303 | -0.06093 | -0.020797 | 0.10986 | -0.12961 | -0.17788 | 0.13381 | -122.5599 | 0.074287 | 0.046518 | -0.087294 | -122.5933 | -122.4197 | -0.09091 | -122.6648 | 0.13381 | 0.026045 | 0.11695 | -122.5342 | -122.7736 | 0.17115 | 0.1377 | 0.31136 | 0.097539 | -122.5972 | 0.066178 | 0.19683 | -0.042632 | 0.14228 | -122.8219
3667.1719 | 122.7722 | -0.082397 | 122.6578 | 1.4211e-13 | -0.049604 | -0.021823 | -0.079298 | -0.015401 | -0.0050809 | -0.23441 | 0.040734 | 0.019251 | 0.0048926 | 0.053893 | -0.0087448 | -0.021844 | 0.005985 | -0.035879 | 0.084176 | 0.050727 | 0.21522 | 0.0331 | 0.042256 | 0.059882 | -0.056351 | -0.020797 | 0.11444 | -0.14334 | -0.16873 | 0.1155 | -122.5736 | 0.060553 | 0.046518 | -0.068979 | -122.607 | -122.4426 | -0.086331 | -122.6786 | 0.12465 | 0.026046 | 0.11238 | -122.5433 | -122.8011 | 0.16657 | 0.13312 | 0.29762 | 0.088382 | -122.6247 | 0.0616 | 0.19683 | -0.060946 | 0.14228 | -122.8265
3668.875 | 122.6898 | -0.10986 | 122.7081 | 1.4211e-13 | -0.049818 | -0.021823 | -0.079298 | -0.015187 | -0.0050809 | -0.24204 | 0.040948 | 0.019251 | 0.0053198 | 0.054106 | -0.0083176 | -0.017266 | 0.005985 | -0.049614 | 0.084176 | 0.055306 | 0.2198 | 0.001048 | 0.046835 | 0.059882 | -0.06093 | -0.020797 | 0.11444 | -0.13876 | -0.17331 | 0.11091 | -122.624 | 0.092597 | 0.060249 | -0.050662 | -122.6528 | -122.4883 | -0.063443 | -122.7289 | 0.1567 | 0.048933 | 0.11238 | -122.5937 | -122.8469 | 0.19404 | 0.16517 | 0.32966 | 0.11585 | -122.7071 | 0.089066 | 0.2243 | -0.028902 | 0.16975 | -122.8814
3670.6406 | 122.8088 | -0.059509 | 122.6944 | 1.4211e-13 | -0.04939 | -0.02225 | -0.079512 | -0.015401 | -0.0048673 | -0.24204 | 0.040734 | 0.018823 | 0.0055336 | 0.054534 | -0.0089584 | -0.017266 | 0.010564 | -0.049614 | 0.084176 | 0.050727 | 0.21522 | 0.019363 | 0.046835 | 0.064461 | -0.065509 | -0.016219 | 0.11444 | -0.13419 | -0.17788 | 0.078872 | -122.6102 | 0.042243 | 0.009895 | -0.068977 | -122.6437 | -122.4792 | -0.11838 | -122.7106 | 0.10634 | -0.006 | 0.11238 | -122.58 | -122.8286 | 0.14369 | 0.11024 | 0.27473 | 0.070073 | -122.675 | 0.04329 | 0.17394 | -0.074677 | 0.12397 | -122.8723
3672.4062 | 122.699 | -0.10986 | 122.6807 | 1.4211e-13 | -0.049818 | -0.022037 | -0.079512 | -0.015401 | -0.0048673 | -0.2573 | 0.040734 | 0.019037 | 0.0051062 | 0.054106 | -0.0087448 | -0.012688 | 0.010564 | -0.054192 | 0.07502 | 0.055306 | 0.2198 | 0.037679 | 0.042256 | 0.064461 | -0.056351 | -0.025376 | 0.11444 | -0.13419 | -0.18246 | 0.14754 | -122.6056 | 0.097175 | 0.055671 | -0.091871 | -122.6254 | -122.4609 | -0.072601 | -122.706 | 0.15212 | 0.053512 | 0.12611 | -122.5662 | -122.8148 | 0.18488 | 0.16517 | 0.32966 | 0.12043 | -122.643 | 0.084487 | 0.2243 | -0.024323 | 0.17432 | -122.8631
3674.1562 | 122.699 | -0.10529 | 122.7081 | 1.4211e-13 | -0.050245 | -0.022037 | -0.079512 | -0.015401 | -0.0048673 | -0.24204 | 0.040948 | 0.019037 | 0.0051062 | 0.054534 | -0.0087448 | -0.012688 | 0.001407 | -0.045036 | 0.079598 | 0.050727 | 0.21064 | 0.014784 | 0.051413 | 0.059882 | -0.065509 | -0.025376 | 0.11444 | -0.13876 | -0.17788 | 0.12007 | -122.6285 | 0.092598 | 0.06025 | -0.05982 | -122.6574 | -122.4975 | -0.072599 | -122.7335 | 0.1567 | 0.039777 | 0.11238 | -122.5937 | -122.8469 | 0.18488 | 0.15601 | 0.31593 | 0.10669 | -122.6933 | 0.07991 | 0.21972 | -0.033479 | 0.16517 | -122.886
3675.8594 | 122.7859 | -0.07782 | 122.6669 | 1.4211e-13 | -0.04939 | -0.022037 | -0.079298 | -0.015187 | -0.0046535 | -0.24967 | 0.040734 | 0.019037 | 0.0051062 | 0.054106 | -0.0087448 | -0.012688 | 0.015142 | -0.040457 | 0.07502 | 0.050727 | 0.21522 | 0.023942 | 0.046835 | 0.06904 | -0.070087 | -0.016219 | 0.11444 | -0.13419 | -0.17788 | 0.10176 | -122.5919 | 0.065132 | 0.037363 | -0.064399 | -122.6162 | -122.4517 | -0.10006 | -122.6832 | 0.12466 | 0.007733 | 0.1078 | -122.5525 | -122.8011 | 0.15284 | 0.12855 | 0.29304 | 0.092962 | -122.643 | 0.061601 | 0.19226 | -0.056366 | 0.14686 | -122.8448
3677.625 | 122.7127 | -0.1236 | 122.6944 | 1.4211e-13 | -0.049818 | -0.021823 | -0.079084 | -0.015828 | -0.0048673 | -0.24967 | 0.040734 | 0.019037 | 0.0053198 | 0.05432 | -0.0091722 | -0.017266 | 0.010564 | -0.040457 | 0.079598 | 0.041569 | 0.22438 | 0.010206 | 0.046835 | 0.064461 | -0.06093 | -0.016219 | 0.10986 | -0.12961 | -0.17788 | 0.1338 | -122.6148 | 0.10633 | 0.083139 | -0.050663 | -122.6528 | -122.47 | -0.054289 | -122.7106 | 0.17043 | 0.062666 | 0.11695 | -122.5845 | -122.824 | 0.20319 | 0.16517 | 0.34798 | 0.13416 | -122.6842 | 0.10738 | 0.23345 | -0.006011 | 0.18806 | -122.8723
3679.3125 | 122.7036 | -0.11444 | 122.7081 | 1.4211e-13 | -0.050032 | -0.021823 | -0.079298 | -0.014973 | -0.0048673 | -0.23441 | 0.040734 | 0.018823 | 0.0053198 | 0.05432 | -0.0091722 | -0.021844 | 0.001407 | -0.045036 | 0.079598 | 0.050727 | 0.2198 | 0.060574 | 0.046835 | 0.059882 | -0.056351 | -0.016219 | 0.11444 | -0.12961 | -0.17331 | 0.17502 | -122.6285 | 0.092597 | 0.069405 | -0.10561 | -122.6574 | -122.4883 | -0.058865 | -122.7243 | 0.16128 | 0.05809 | 0.11695 | -122.5937 | -122.8377 | 0.19404 | 0.16517 | 0.33424 | 0.11585 | -122.6476 | 0.098222 | 0.22888 | -0.015166 | 0.17432 | -122.8814
3681.0781 | 122.8363 | -0.054932 | 122.6715 | 1.4211e-13 | -0.049604 | -0.021823 | -0.079084 | -0.015614 | -0.0048673 | -0.24967 | 0.040734 | 0.019037 | 0.0057472 | 0.054106 | -0.0089584 | -0.012688 | 0.010564 | -0.049614 | 0.079598 | 0.046148 | 0.21064 | 0.078889 | 0.051413 | 0.055303 | -0.070087 | -0.025376 | 0.10986 | -0.13419 | -0.17331 | 0.13382 | -122.5919 | 0.042244 | 0.005318 | -0.1285 | -122.6254 | -122.4609 | -0.11837 | -122.6969 | 0.10634 | -0.015155 | 0.10322 | -122.5617 | -122.8057 | 0.13453 | 0.10108 | 0.26558 | 0.065496 | -122.5926 | 0.029556 | 0.16479 | -0.079254 | 0.11023 | -122.8448
3682.7812 | 122.7814 | -0.09613 | 122.6852 | 1.4211e-13 | -0.049818 | -0.02225 | -0.079512 | -0.015828 | -0.0048673 | -0.24204 | 0.040734 | 0.019037 | 0.0053198 | 0.05432 | -0.0087448 | -0.012688 | 0.015142 | -0.045036 | 0.079598 | 0.046148 | 0.21064 | 0.014784 | 0.046835 | 0.064461 | -0.06093 | -0.020797 | 0.12359 | -0.12961 | -0.17331 | 0.11091 | -122.6056 | 0.083442 | 0.051094 | -0.05982 | -122.6391 | -122.4746 | -0.077176 | -122.706 | 0.14297 | 0.0352 | 0.11238 | -122.5616 | -122.8148 | 0.17573 | 0.14228 | 0.30678 | 0.11127 | -122.6705 | 0.075333 | 0.21972 | -0.033477 | 0.16059 | -122.8585
3684.5312 | 122.8363 | -0.082397 | 122.6715 | 1.4211e-13 | -0.04939 | -0.022037 | -0.079512 | -0.015614 | -0.0050809 | -0.24204 | 0.040307 | 0.018823 | 0.0055336 | 0.054747 | -0.0093858 | -0.008109 | 0.010564 | -0.040457 | 0.079598 | 0.050727 | 0.22438 | 0.014784 | 0.046835 | 0.064461 | -0.06093 | -0.016219 | 0.11444 | -0.13876 | -0.17331 | 0.097181 | -122.5919 | 0.074288 | 0.04194 | -0.055241 | -122.6208 | -122.4471 | -0.090909 | -122.6877 | 0.12923 | 0.021467 | 0.11238 | -122.5571 | -122.8103 | 0.162 | 0.13312 | 0.30678 | 0.092961 | -122.6567 | 0.066178 | 0.19683 | -0.056368 | 0.14686 | -122.8448
3686.2344 | 122.8363 | -0.045776 | 122.6578 | 1.4211e-13 | -0.050032 | -0.022037 | -0.079298 | -0.015828 | -0.0050809 | -0.24204 | 0.040948 | 0.018823 | 0.0053198 | 0.05432 | -0.0093858 | -0.012688 | 0.005985 | -0.049614 | 0.079598 | 0.046148 | 0.2198 | 0.010206 | 0.046835 | 0.064461 | -0.065509 | -0.01164 | 0.11901 | -0.13876 | -0.17788 | 0.055982 | -122.5782 | 0.033088 | -0.003838 | -0.05982 | -122.6116 | -122.438 | -0.13211 | -122.6694 | 0.092611 | -0.019733 | 0.11238 | -122.5388 | -122.7965 | 0.12537 | 0.091924 | 0.26558 | 0.051761 | -122.6476 | 0.034136 | 0.16479 | -0.092989 | 0.11024 | -122.8357
3688 | 122.8455 | -0.064087 | 122.6532 | 1.4211e-13 | -0.049604 | -0.022037 | -0.079298 | -0.015401 | -0.0050809 | -0.23441 | 0.040734 | 0.018823 | 0.0055336 | 0.054534 | -0.0091722 | -0.021844 | 0.005985 | -0.045036 | 0.084176 | 0.041569 | 0.2198 | 0.001048 | 0.042256 | 0.059882 | -0.06093 | -0.020797 | 0.10986 | -0.12961 | -0.16873 | 0.065135 | -122.569 | 0.042243 | 0.019051 | -0.046084 | -122.6116 | -122.4334 | -0.10464 | -122.674 | 0.10634 | 0.003157 | 0.1078 | -122.5433 | -122.7828 | 0.14826 | 0.10566 | 0.28389 | 0.070072 | -122.6522 | 0.04329 | 0.17394 | -0.06552 | 0.12397 | -122.8219
3689.7656 | 122.7539 | -0.10071 | 122.7127 | 1.4211e-13 | -0.050032 | -0.02225 | -0.079084 | -0.015614 | -0.0052945 | -0.23441 | 0.040734 | 0.019037 | 0.0051062 | 0.054961 | -0.0089584 | -0.017266 | 0.010564 | -0.045036 | 0.088755 | 0.050727 | 0.2198 | -0.003531 | 0.042256 | 0.059882 | -0.06093 | -0.020797 | 0.11901 | -0.13419 | -0.18246 | 0.097177 | -122.624 | 0.083442 | 0.055672 | -0.041505 | -122.662 | -122.4929 | -0.081756 | -122.7335 | 0.14296 | 0.039778 | 0.12153 | -122.5937 | -122.8469 | 0.18946 | 0.15144 | 0.32051 | 0.11127 | -122.7162 | 0.079911 | 0.21972 | -0.033478 | 0.16059 | -122.8952
3691.4688 | 122.7036 | -0.10986 | 122.699 | 1.4211e-13 | -0.049818 | -0.02225 | -0.079512 | -0.015614 | -0.0050809 | -0.24967 | 0.040734 | 0.018823 | 0.0053198 | 0.054106 | -0.0091722 | -0.021844 | 0.001407 | -0.049614 | 0.070441 | 0.046148 | 0.2198 | 0.028521 | 0.051413 | 0.06904 | -0.070087 | -0.016219 | 0.11901 | -0.13876 | -0.18246 | 0.13838 | -122.6285 | 0.088019 | 0.060249 | -0.078135 | -122.6528 | -122.4792 | -0.072601 | -122.7152 | 0.16128 | 0.039776 | 0.11238 | -122.58 | -122.8377 | 0.1803 | 0.15601 | 0.32966 | 0.11127 | -122.6705 | 0.093644 | 0.22888 | -0.028902 | 0.1789 | -122.8814
3693.2344 | 122.7081 | -0.12817 | 122.7173 | 1.4211e-13 | -0.050459 | -0.022037 | -0.079725 | -0.015828 | -0.0055083 | -0.24204 | 0.040734 | 0.018823 | 0.0053198 | 0.054106 | -0.0091722 | -0.017266 | 0.010564 | -0.045036 | 0.084176 | 0.041569 | 0.22438 | 0.014784 | 0.046835 | 0.06904 | -0.06093 | -0.020797 | 0.11901 | -0.13876 | -0.17788 | 0.14296 | -122.6331 | 0.11091 | 0.083138 | -0.05982 | -122.6757 | -122.4929 | -0.049711 | -122.7381 | 0.17501 | 0.067244 | 0.11695 | -122.5983 | -122.8561 | 0.21235 | 0.16974 | 0.35256 | 0.13874 | -122.7025 | 0.10738 | 0.24719 | -0.010591 | 0.19721 | -122.8952
3695 | 122.7219 | -0.10986 | 122.7264 | 1.4211e-13 | -0.050032 | -0.02225 | -0.079512 | -0.015401 | -0.0048673 | -0.24204 | 0.040521 | 0.01861 | 0.0048926 | 0.054534 | -0.0091722 | -0.017266 | 0.010564 | -0.045036 | 0.079598 | 0.041569 | 0.22896 | 0.001048 | 0.037677 | 0.064461 | -0.065509 | -0.020797 | 0.11444 | -0.13419 | -0.17331 | 0.11091 | -122.6468 | 0.092597 | 0.064827 | -0.046084 | -122.6849 | -122.4975 | -0.063443 | -122.7472 | 0.14754 | 0.044354 | 0.1078 | -122.612 | -122.8606 | 0.18946 | 0.15143 | 0.33882 | 0.12043 | -122.7254 | 0.089066 | 0.2243 | -0.024323 | 0.17432 | -122.8997
3696.7031 | 122.7768 | -0.10986 | 122.7127 | 1.4211e-13 | -0.049818 | -0.02225 | -0.079298 | -0.015187 | -0.0050809 | -0.24204 | 0.040734 | 0.018823 | 0.004679 | 0.054534 | -0.0091722 | -0.017266 | 0.005985 | -0.040457 | 0.079598 | 0.050727 | 0.2198 | 0.046837 | 0.042256 | 0.064461 | -0.06093 | -0.020797 | 0.11444 | -0.13876 | -0.17331 | 0.1567 | -122.6331 | 0.092597 | 0.069406 | -0.087294 | -122.662 | -122.4929 | -0.063443 | -122.7335 | 0.15212 | 0.048933 | 0.11238 | -122.5983 | -122.8515 | 0.18946 | 0.16059 | 0.32966 | 0.11585 | -122.6659 | 0.089066 | 0.2243 | -0.028902 | 0.17432 | -122.886
3698.4688 | 122.7402 | -0.10986 | 122.7173 | 1.4211e-13 | -0.049818 | -0.02225 | -0.079512 | -0.015401 | -0.0050809 | -0.2573 | 0.040734 | 0.018823 | 0.0055336 | 0.054534 | -0.0089584 | -0.021844 | 0.005985 | -0.049614 | 0.070441 | 0.055306 | 0.2198 | 0.014784 | 0.046835 | 0.055303 | -0.065509 | -0.025376 | 0.11444 | -0.12961 | -0.17331 | 0.12465 | -122.6468 | 0.088019 | 0.060249 | -0.064398 | -122.662 | -122.4975 | -0.063443 | -122.7427 | 0.1567 | 0.044354 | 0.1078 | -122.6028 | -122.8469 | 0.1803 | 0.16517 | 0.32966 | 0.11585 | -122.7025 | 0.084487 | 0.2243 | -0.019744 | 0.16517 | -122.8906
3700.2188 | 122.7539 | -0.09613 | 122.699 | 1.4211e-13 | -0.050459 | -0.021823 | -0.079512 | -0.015614 | -0.0050809 | -0.24204 | 0.040734 | 0.019251 | 0.004679 | 0.05432 | -0.0089584 | -0.017266 | 0.005985 | -0.040457 | 0.079598 | 0.041569 | 0.22438 | -0.003531 | 0.046835 | 0.064461 | -0.065509 | -0.016219 | 0.11444 | -0.13419 | -0.17331 | 0.092599 | -122.6194 | 0.078864 | 0.055673 | -0.036926 | -122.6574 | -122.4746 | -0.077176 | -122.7152 | 0.14297 | 0.030621 | 0.1078 | -122.5845 | -122.8332 | 0.17573 | 0.1377 | 0.32051 | 0.10211 | -122.7025 | 0.079911 | 0.21057 | -0.038056 | 0.16059 | -122.8723
3701.9219 | 122.7036 | -0.1236 | 122.7402 | 1.4211e-13 | -0.050032 | -0.021823 | -0.079298 | -0.015828 | -0.0050809 | -0.24967 | 0.040521 | 0.018823 | 0.0053198 | 0.054106 | -0.0091722 | -0.026423 | 0.005985 | -0.049614 | 0.07502 | 0.046148 | 0.21064 | 0.014784 | 0.042256 | 0.059882 | -0.06093 | -0.01164 | 0.11444 | -0.13419 | -0.17788 | 0.13838 | -122.6652 | 0.097173 | 0.073982 | -0.064398 | -122.694 | -122.5295 | -0.054289 | -122.7518 | 0.16585 | 0.062666 | 0.11695 | -122.6257 | -122.8744 | 0.19862 | 0.16974 | 0.33424 | 0.12958 | -122.7254 | 0.11196 | 0.23803 | -0.01059 | 0.18348 | -122.9181
3703.6719 | 122.8592 | -0.068665 | 122.7036 | 1.4211e-13 | -0.050673 | -0.02225 | -0.079512 | -0.015187 | -0.0055083 | -0.23441 | 0.040521 | 0.01861 | 0.0053198 | 0.054534 | -0.0091722 | -0.012688 | 0.005985 | -0.045036 | 0.084176 | 0.041569 | 0.2198 | 0.023942 | 0.042256 | 0.064461 | -0.070087 | -0.016219 | 0.10986 | -0.13876 | -0.17788 | 0.092607 | -122.6194 | 0.055977 | 0.023629 | -0.068978 | -122.662 | -122.4838 | -0.10922 | -122.7198 | 0.11092 | -0.001422 | 0.1078 | -122.5937 | -122.8423 | 0.15284 | 0.11023 | 0.28847 | 0.07465 | -122.6796 | 0.052446 | 0.17852 | -0.0701 | 0.13313 | -122.8814
3705.4375 | 122.7264 | -0.10529 | 122.7402 | 1.4211e-13 | -0.050032 | -0.02225 | -0.079084 | -0.015614 | -0.0052945 | -0.24967 | 0.040521 | 0.019037 | 0.0053198 | 0.054747 | -0.0093858 | -0.017266 | 0.001407 | -0.045036 | 0.084176 | 0.041569 | 0.22438 | 0.037679 | 0.051413 | 0.064461 | -0.065509 | -0.020797 | 0.11444 | -0.12961 | -0.18246 | 0.14297 | -122.656 | 0.08802 | 0.06025 | -0.082715 | -122.6986 | -122.5158 | -0.077178 | -122.761 | 0.1567 | 0.039777 | 0.11695 | -122.6257 | -122.8698 | 0.18946 | 0.14686 | 0.32967 | 0.10669 | -122.7025 | 0.084489 | 0.21972 | -0.024321 | 0.16975 | -122.9226
3707.1875 | 122.7997 | -0.07782 | 122.6944 | 1.4211e-13 | -0.050673 | -0.022464 | -0.079298 | -0.015614 | -0.0052945 | -0.23441 | 0.040307 | 0.018823 | 0.0048926 | 0.054534 | -0.0091722 | -0.017266 | 0.010564 | -0.049614 | 0.079598 | 0.046148 | 0.2198 | 0.042258 | 0.046835 | 0.059882 | -0.065509 | -0.025376 | 0.10528 | -0.13876 | -0.17788 | 0.12008 | -122.6148 | 0.060554 | 0.028206 | -0.091872 | -122.6482 | -122.4746 | -0.10006 | -122.7198 | 0.12466 | 0.012311 | 0.11238 | -122.5891 | -122.8332 | 0.15742 | 0.12397 | 0.29762 | 0.088384 | -122.6521 | 0.052444 | 0.1831 | -0.060945 | 0.1377 | -122.8723
3708.8906 | 122.7264 | -0.11444 | 122.7356 | 1.4211e-13 | -0.050459 | -0.02225 | -0.079298 | -0.015401 | -0.0052945 | -0.24204 | 0.040307 | 0.019251 | 0.0051062 | 0.054534 | -0.0091722 | -0.017266 | -0.003172 | -0.045036 | 0.084176 | 0.046148 | 0.2198 | 0.042258 | 0.046835 | 0.064461 | -0.056351 | -0.025376 | 0.10986 | -0.13876 | -0.17788 | 0.1567 | -122.6514 | 0.097175 | 0.069405 | -0.087294 | -122.6894 | -122.5158 | -0.063444 | -122.761 | 0.16128 | 0.05809 | 0.12153 | -122.6257 | -122.8744 | 0.19862 | 0.16059 | 0.33424 | 0.11127 | -122.6933 | 0.089065 | 0.2243 | -0.024324 | 0.1789 | -122.9135
3710.6562 | 122.7722 | -0.07782 | 122.699 | 1.4211e-13 | -0.050673 | -0.022037 | -0.07887 | -0.015401 | -0.0055083 | -0.24967 | 0.040734 | 0.019037 | 0.0051062 | 0.054961 | -0.0089584 | -0.017266 | 0.005985 | -0.049614 | 0.079598 | 0.046148 | 0.2198 | 0.014784 | 0.046835 | 0.064461 | -0.06093 | -0.016219 | 0.11444 | -0.12961 | -0.17788 | 0.092604 | -122.6194 | 0.060554 | 0.028206 | -0.064398 | -122.6528 | -122.4792 | -0.10006 | -122.7152 | 0.12466 | 0.01689 | 0.11695 | -122.5845 | -122.8286 | 0.15742 | 0.12397 | 0.29762 | 0.083805 | -122.6842 | 0.061601 | 0.19226 | -0.051787 | 0.14228 | -122.8769
3712.3594 | 122.7539 | -0.1236 | 122.7356 | 1.4211e-13 | -0.050459 | -0.021823 | -0.079512 | -0.015401 | -0.0050809 | -0.24967 | 0.040307 | 0.01861 | 0.0053198 | 0.054534 | -0.0089584 | -0.031001 | 0.005985 | -0.040457 | 0.07502 | 0.050727 | 0.22438 | 0.023942 | 0.046835 | 0.059882 | -0.06093 | -0.020797 | 0.11444 | -0.13419 | -0.17788 | 0.14754 | -122.6606 | 0.092595 | 0.083139 | -0.064399 | -122.6849 | -122.5112 | -0.054289 | -122.7564 | 0.17043 | 0.062666 | 0.11695 | -122.6212 | -122.8698 | 0.19862 | 0.17432 | 0.34798 | 0.12958 | -122.7117 | 0.1028 | 0.23803 | -0.01059 | 0.18348 | -122.9135
3714.125 | 122.8409 | -0.064087 | 122.7081 | 1.4211e-13 | -0.050459 | -0.022037 | -0.079725 | -0.015401 | -0.0055083 | -0.23441 | 0.040734 | 0.018823 | 0.0051062 | 0.054534 | -0.0091722 | -0.017266 | 0.001407 | -0.045036 | 0.07502 | 0.046148 | 0.2198 | 0.028521 | 0.046835 | 0.06904 | -0.056351 | -0.020797 | 0.10986 | -0.12961 | -0.17331 | 0.092608 | -122.6331 | 0.046821 | 0.019051 | -0.073557 | -122.662 | -122.4883 | -0.10922 | -122.7289 | 0.11092 | 0.007736 | 0.11695 | -122.5983 | -122.8377 | 0.13911 | 0.11023 | 0.28389 | 0.065494 | -122.6796 | 0.04329 | 0.17394 | -0.06552 | 0.13313 | -122.8814
3715.8125 | 122.7036 | -0.10071 | 122.7448 | 1.4211e-13 | -0.050459 | -0.021823 | -0.079512 | -0.015614 | -0.0052945 | -0.24204 | 0.040307 | 0.019037 | 0.0051062 | 0.054747 | -0.0089584 | -0.017266 | 0.010564 | -0.040457 | 0.079598 | 0.050727 | 0.22438 | 0.0331 | 0.046835 | 0.059882 | -0.06093 | -0.016219 | 0.11901 | -0.12961 | -0.16873 | 0.13381 | -122.6652 | 0.083442 | 0.060251 | -0.073557 | -122.694 | -122.5204 | -0.06802 | -122.761 | 0.14754 | 0.039778 | 0.1078 | -122.6257 | -122.8744 | 0.18031 | 0.15144 | 0.32509 | 0.11127 | -122.7117 | 0.084489 | 0.21972 | -0.028899 | 0.16059 | -122.9135
3717.5781 | 122.8409 | -0.064087 | 122.699 | 1.4211e-13 | -0.050459 | -0.021609 | -0.079298 | -0.015614 | -0.0050809 | -0.24967 | 0.040521 | 0.018823 | 0.0053198 | 0.054747 | -0.0091722 | -0.017266 | 0.001407 | -0.045036 | 0.084176 | 0.050727 | 0.22438 | -0.003531 | 0.046835 | 0.064461 | -0.065509 | -0.016219 | 0.11444 | -0.13419 | -0.18246 | 0.060556 | -122.6148 | 0.046821 | 0.019051 | -0.041505 | -122.6482 | -122.4746 | -0.11838 | -122.7152 | 0.11092 | -0.001422 | 0.11695 | -122.5845 | -122.8332 | 0.14826 | 0.11481 | 0.28847 | 0.065494 | -122.7025 | 0.047868 | 0.17852 | -0.070099 | 0.12855 | -122.8814
3719.2812 | 122.7081 | -0.10529 | 122.7173 | 1.4211e-13 | -0.050245 | -0.022037 | -0.079298 | -0.015614 | -0.0055083 | -0.23441 | 0.040521 | 0.018823 | 0.0051062 | 0.054747 | -0.0093858 | -0.017266 | 0.001407 | -0.049614 | 0.084176 | 0.046148 | 0.2198 | 0.046837 | 0.046835 | 0.064461 | -0.056351 | -0.016219 | 0.12817 | -0.13419 | -0.17788 | 0.15212 | -122.6331 | 0.08802 | 0.055672 | -0.096451 | -122.6711 | -122.4975 | -0.072599 | -122.7335 | 0.15212 | 0.048935 | 0.12153 | -122.5891 | -122.8515 | 0.18946 | 0.15143 | 0.32509 | 0.10669 | -122.6704 | 0.089067 | 0.23346 | -0.0289 | 0.16975 | -122.8952
3721.0469 | 122.7264 | -0.11902 | 122.7264 | 1.4211e-13 | -0.050459 | -0.02225 | -0.079084 | -0.015614 | -0.0055083 | -0.23441 | 0.040521 | 0.018823 | 0.0053198 | 0.054747 | -0.0091722 | -0.012688 | 0.001407 | -0.049614 | 0.079598 | 0.046148 | 0.2198 | 0.0331 | 0.042256 | 0.059882 | -0.06093 | -0.01164 | 0.11444 | -0.13419 | -0.18246 | 0.15212 | -122.6468 | 0.10633 | 0.069405 | -0.082714 | -122.6803 | -122.5066 | -0.063445 | -122.7381 | 0.16128 | 0.058089 | 0.12153 | -122.612 | -122.8606 | 0.19862 | 0.16517 | 0.33882 | 0.12043 | -122.6933 | 0.10738 | 0.23345 | -0.015167 | 0.1789 | -122.9089
3722.75 | 122.8455 | -0.07782 | 122.7219 | 1.4211e-13 | -0.050459 | -0.022037 | -0.079512 | -0.015187 | -0.0057219 | -0.24967 | 0.040093 | 0.018396 | 0.0051062 | 0.054747 | -0.0095994 | -0.008109 | 0.005985 | -0.040457 | 0.084176 | 0.050727 | 0.21522 | 0.037679 | 0.042256 | 0.059882 | -0.06093 | -0.016219 | 0.11901 | -0.13876 | -0.17788 | 0.1155 | -122.6377 | 0.069711 | 0.037363 | -0.078136 | -122.6711 | -122.5066 | -0.10006 | -122.7381 | 0.12008 | 0.01689 | 0.11695 | -122.6028 | -122.8606 | 0.162 | 0.12855 | 0.29304 | 0.083805 | -122.6842 | 0.061601 | 0.19683 | -0.060945 | 0.1377 | -122.8997
3724.5156 | 122.8546 | -0.059509 | 122.731 | 1.4211e-13 | -0.050459 | -0.022037 | -0.079298 | -0.015614 | -0.0052945 | -0.24204 | 0.040307 | 0.019037 | 0.0051062 | 0.054961 | -0.0091722 | -0.012688 | 0.005985 | -0.045036 | 0.084176 | 0.055306 | 0.22438 | 0.078889 | 0.042256 | 0.059882 | -0.065509 | -0.016219 | 0.12359 | -0.13419 | -0.17331 | 0.1384 | -122.6468 | 0.046821 | 0.014473 | -0.12393 | -122.6757 | -122.5066 | -0.1138 | -122.7472 | 0.10176 | -0.006 | 0.1078 | -122.6074 | -122.8652 | 0.14369 | 0.11482 | 0.28389 | 0.065494 | -122.6521 | 0.04329 | 0.1831 | -0.074677 | 0.11939 | -122.9043
3726.2188 | 122.7997 | -0.091553 | 122.6898 | 1.4211e-13 | -0.050673 | -0.022464 | -0.079512 | -0.015187 | -0.0055083 | -0.24967 | 0.040521 | 0.01861 | 0.0053198 | 0.054747 | -0.0095994 | -0.012688 | 0.005985 | -0.035879 | 0.079598 | 0.050727 | 0.2198 | 0.037679 | 0.046835 | 0.059882 | -0.070087 | -0.020797 | 0.11901 | -0.13876 | -0.18246 | 0.12923 | -122.6102 | 0.078865 | 0.055674 | -0.073558 | -122.6391 | -122.47 | -0.090911 | -122.7106 | 0.13839 | 0.021466 | 0.11238 | -122.5708 | -122.8286 | 0.17115 | 0.14228 | 0.31135 | 0.097538 | -122.6521 | 0.070756 | 0.21057 | -0.047212 | 0.15143 | -122.8723
3727.9844 | 122.7081 | -0.11902 | 122.7356 | 1.4211e-13 | -0.050245 | -0.022037 | -0.079298 | -0.015614 | -0.0059355 | -0.24204 | 0.040521 | 0.019037 | 0.0051062 | 0.054534 | -0.0091722 | -0.021844 | 0.001407 | -0.040457 | 0.079598 | 0.046148 | 0.21522 | 0.005627 | 0.042256 | 0.055303 | -0.065509 | -0.01164 | 0.12359 | -0.13419 | -0.17331 | 0.12465 | -122.656 | 0.097175 | 0.078562 | -0.046084 | -122.6894 | -122.5204 | -0.054287 | -122.7472 | 0.16128 | 0.05351 | 0.1078 | -122.612 | -122.8698 | 0.19862 | 0.16517 | 0.33424 | 0.12043 | -122.73 | 0.10738 | 0.24261 | -0.015167 | 0.17432 | -122.9089
3729.7344 | 122.7219 | -0.10071 | 122.7356 | 1.4211e-13 | -0.050459 | -0.022037 | -0.079298 | -0.015828 | -0.0052945 | -0.24967 | 0.040093 | 0.018823 | 0.0051062 | 0.054961 | -0.0093858 | -0.012688 | 0.001407 | -0.045036 | 0.079598 | 0.055306 | 0.22438 | 0.014784 | 0.042256 | 0.059882 | -0.06093 | -0.016219 | 0.11901 | -0.13419 | -0.17788 | 0.11549 | -122.656 | 0.08802 | 0.055672 | -0.05982 | -122.6803 | -122.5112 | -0.077177 | -122.7518 | 0.14296 | 0.039778 | 0.11695 | -122.6166 | -122.8698 | 0.18031 | 0.15601 | 0.32509 | 0.10212 | -122.7208 | 0.084489 | 0.21972 | -0.033478 | 0.16059 | -122.9135
3731.5 | 122.7539 | -0.11444 | 122.7356 | 1.4211e-13 | -0.0511 | -0.022037 | -0.079298 | -0.015614 | -0.0057219 | -0.24204 | 0.040734 | 0.018182 | 0.0053198 | 0.054747 | -0.0091722 | -0.021844 | 0.010564 | -0.040457 | 0.07502 | 0.046148 | 0.2198 | 0.010206 | 0.055992 | 0.064461 | -0.065509 | -0.020797 | 0.10986 | -0.13419 | -0.18246 | 0.12465 | -122.6606 | 0.092597 | 0.073984 | -0.050663 | -122.6894 | -122.5158 | -0.068023 | -122.7564 | 0.17043 | 0.048932 | 0.11695 | -122.6257 | -122.8698 | 0.18946 | 0.16059 | 0.33424 | 0.12501 | -122.7254 | 0.093644 | 0.2243 | -0.019745 | 0.1789 | -122.9181
3733.2812 | 122.7722 | -0.11902 | 122.7676 | 1.4211e-13 | -0.050245 | -0.02225 | -0.079084 | -0.015828 | -0.0055083 | -0.24204 | 0.040307 | 0.018823 | 0.004679 | 0.054961 | -0.0091722 | -0.021844 | 0.005985 | -0.035879 | 0.079598 | 0.046148 | 0.22438 | 0.051416 | 0.042256 | 0.064461 | -0.06093 | -0.020797 | 0.11901 | -0.13876 | -0.17788 | 0.17044 | -122.688 | 0.097175 | 0.08314 | -0.087295 | -122.7215 | -122.5433 | -0.058866 | -122.7884 | 0.16128 | 0.058089 | 0.11695 | -122.6486 | -122.9064 | 0.19862 | 0.16517 | 0.3434 | 0.125 | -122.7162 | 0.098222 | 0.23803 | -0.019746 | 0.18348 | -122.9455
3735.0469 | 122.7127 | -0.11902 | 122.7219 | 1.4211e-13 | -0.050245 | -0.022037 | -0.079298 | -0.015828 | -0.0055083 | -0.23441 | 0.040307 | 0.01861 | 0.0048926 | 0.054961 | -0.0087448 | -0.017266 | 0.010564 | -0.040457 | 0.07502 | 0.046148 | 0.2198 | 0.001048 | 0.042256 | 0.064461 | -0.06093 | -0.016219 | 0.11444 | -0.12503 | -0.17331 | 0.12007 | -122.6468 | 0.10175 | 0.078562 | -0.041505 | -122.6757 | -122.5021 | -0.054287 | -122.7381 | 0.16128 | 0.058089 | 0.11238 | -122.6074 | -122.8469 | 0.19404 | 0.16517 | 0.33882 | 0.12958 | -122.7208 | 0.1028 | 0.23345 | -0.00601 | 0.18348 | -122.8952
3736.7656 | 122.7814 | -0.091553 | 122.7173 | 1.4211e-13 | -0.050459 | -0.022037 | -0.079512 | -0.015401 | -0.0057219 | -0.24967 | 0.040521 | 0.019037 | 0.0048926 | 0.054961 | -0.0093858 | -0.017266 | 0.005985 | -0.045036 | 0.07502 | 0.050727 | 0.22896 | 0.023942 | 0.037677 | 0.064461 | -0.070087 | -0.025376 | 0.11444 | -0.13419 | -0.17788 | 0.1155 | -122.6423 | 0.074287 | 0.046517 | -0.068978 | -122.6666 | -122.4883 | -0.086332 | -122.7427 | 0.12923 | 0.021466 | 0.1078 | -122.6028 | -122.8515 | 0.16657 | 0.14228 | 0.32051 | 0.097538 | -122.6933 | 0.066177 | 0.20599 | -0.042633 | 0.15601 | -122.8952
3738.4844 | 122.8683 | -0.07782 | 122.6898 | 1.4211e-13 | -0.050673 | -0.022037 | -0.079512 | -0.015614 | -0.0057219 | -0.24204 | 0.040093 | 0.01861 | 0.0053198 | 0.054961 | -0.0093858 | -0.017266 | 0.005985 | -0.049614 | 0.084176 | 0.050727 | 0.21522 | 0.005627 | 0.051413 | 0.06904 | -0.065509 | -0.016219 | 0.11444 | -0.13419 | -0.17331 | 0.083447 | -122.6056 | 0.060554 | 0.028206 | -0.055241 | -122.6391 | -122.4746 | -0.095486 | -122.706 | 0.12923 | 0.012311 | 0.1078 | -122.5754 | -122.824 | 0.162 | 0.12855 | 0.29304 | 0.083805 | -122.6842 | 0.061601 | 0.19226 | -0.056366 | 0.14686 | -122.8631
3740.25 | 122.8226 | -0.086975 | 122.6807 | 1.4211e-13 | -0.050245 | -0.022037 | -0.079084 | -0.015614 | -0.0059355 | -0.24967 | 0.040093 | 0.01861 | 0.004679 | 0.054747 | -0.0091722 | -0.017266 | 0.005985 | -0.045036 | 0.079598 | 0.046148 | 0.21522 | 0.055995 | 0.042256 | 0.064461 | -0.056351 | -0.020797 | 0.11444 | -0.13419 | -0.17788 | 0.14297 | -122.6011 | 0.069709 | 0.041939 | -0.10103 | -122.6345 | -122.4654 | -0.09091 | -122.7015 | 0.12923 | 0.030624 | 0.12153 | -122.5662 | -122.8148 | 0.16657 | 0.13312 | 0.3022 | 0.09296 | -122.6247 | 0.066178 | 0.20141 | -0.047211 | 0.15144 | -122.8585
3742.0156 | 122.8638 | -0.068665 | 122.6944 | 1.4211e-13 | -0.050673 | -0.022464 | -0.079512 | -0.015828 | -0.0055083 | -0.23441 | 0.040307 | 0.018823 | 0.0051062 | 0.054961 | -0.0091722 | -0.017266 | 0.005985 | -0.049614 | 0.07502 | 0.050727 | 0.2198 | 0.005627 | 0.042256 | 0.06904 | -0.065509 | -0.016219 | 0.10986 | -0.11129 | -0.18704 | 0.074292 | -122.6194 | 0.051399 | 0.019051 | -0.055241 | -122.6437 | -122.4746 | -0.11838 | -122.7106 | 0.11092 | 0.003156 | 0.12153 | -122.5845 | -122.8057 | 0.14369 | 0.11939 | 0.28847 | 0.07465 | -122.6888 | 0.052446 | 0.17852 | -0.042628 | 0.13771 | -122.8814
3743.7188 | 122.818 | -0.082397 | 122.7081 | 1.4211e-13 | -0.050459 | -0.022037 | -0.079084 | -0.015187 | -0.0055083 | -0.24204 | 0.040093 | 0.01861 | 0.004679 | 0.054747 | -0.0093858 | -0.021844 | 0.001407 | -0.040457 | 0.07502 | 0.046148 | 0.22438 | 0.010206 | 0.042256 | 0.06904 | -0.056351 | -0.007062 | 0.11444 | -0.13419 | -0.17331 | 0.092603 | -122.6331 | 0.060553 | 0.04194 | -0.050663 | -122.662 | -122.4837 | -0.090909 | -122.7152 | 0.12465 | 0.026046 | 0.11695 | -122.5937 | -122.8423 | 0.15742 | 0.12854 | 0.30678 | 0.083804 | -122.6979 | 0.075335 | 0.19683 | -0.051789 | 0.15144 | -122.8814
3745.4844 | 122.8592 | -0.086975 | 122.7081 | 1.4211e-13 | -0.050459 | -0.022037 | -0.079298 | -0.015401 | -0.0055083 | -0.24967 | 0.040307 | 0.018823 | 0.0051062 | 0.054961 | -0.0091722 | -0.017266 | 0.001407 | -0.035879 | 0.088755 | 0.050727 | 0.2198 | 0.019363 | 0.046835 | 0.064461 | -0.056351 | -0.016219 | 0.11444 | -0.13419 | -0.17788 | 0.10634 | -122.6194 | 0.069709 | 0.051096 | -0.055242 | -122.6574 | -122.4883 | -0.09091 | -122.7243 | 0.13381 | 0.030624 | 0.12153 | -122.5937 | -122.8423 | 0.17573 | 0.1377 | 0.30678 | 0.088382 | -122.6888 | 0.070756 | 0.20141 | -0.047211 | 0.15144 | -122.886
3747.1719 | 122.8729 | -0.07782 | 122.699 | 1.4211e-13 | -0.0511 | -0.022037 | -0.079512 | -0.015401 | -0.0055083 | -0.23441 | 0.040521 | 0.019037 | 0.0048926 | 0.054961 | -0.0093858 | -0.021844 | 0.001407 | -0.049614 | 0.084176 | 0.041569 | 0.22896 | 0.010206 | 0.046835 | 0.064461 | -0.070087 | -0.016219 | 0.11444 | -0.13419 | -0.17788 | 0.088026 | -122.6148 | 0.055976 | 0.028206 | -0.05982 | -122.6574 | -122.47 | -0.10006 | -122.7152 | 0.12466 | 0.007733 | 0.1078 | -122.5845 | -122.8332 | 0.162 | 0.11939 | 0.30678 | 0.079227 | -122.6888 | 0.061601 | 0.19226 | -0.056366 | 0.14228 | -122.8769
3748.9375 | 122.7859 | -0.09613 | 122.7356 | 1.4211e-13 | -0.050673 | -0.021823 | -0.079084 | -0.016042 | -0.0055083 | -0.24967 | 0.040521 | 0.01861 | 0.0048926 | 0.055175 | -0.0093858 | -0.026423 | 0.010564 | -0.040457 | 0.079598 | 0.046148 | 0.2198 | 0.051416 | 0.046835 | 0.059882 | -0.065509 | -0.01164 | 0.11444 | -0.13419 | -0.17788 | 0.14755 | -122.656 | 0.069707 | 0.055673 | -0.091873 | -122.6894 | -122.5158 | -0.081755 | -122.7472 | 0.14297 | 0.030621 | 0.11238 | -122.6212 | -122.8698 | 0.17573 | 0.14228 | 0.31593 | 0.10669 | -122.6842 | 0.08449 | 0.21057 | -0.038056 | 0.15601 | -122.9135
3750.6875 | 122.7356 | -0.1236 | 122.7448 | 1.4211e-13 | -0.050459 | -0.022037 | -0.079298 | -0.015401 | -0.0057219 | -0.24967 | 0.040307 | 0.01861 | 0.0053198 | 0.054747 | -0.0091722 | -0.012688 | 0.005985 | -0.049614 | 0.079598 | 0.050727 | 0.2198 | 0.023942 | 0.046835 | 0.064461 | -0.056351 | -0.020797 | 0.12359 | -0.12961 | -0.17788 | 0.14754 | -122.6652 | 0.11091 | 0.073982 | -0.073556 | -122.694 | -122.5249 | -0.054289 | -122.7655 | 0.17043 | 0.067245 | 0.12153 | -122.6212 | -122.8744 | 0.20319 | 0.17432 | 0.3434 | 0.12958 | -122.7208 | 0.1028 | 0.24719 | -0.006011 | 0.18806 | -122.9226
3752.4531 | 122.7493 | -0.14648 | 122.7539 | 1.4211e-13 | -0.050886 | -0.022037 | -0.079084 | -0.015401 | -0.0052945 | -0.24204 | 0.040521 | 0.018823 | 0.004679 | 0.054961 | -0.0098132 | -0.017266 | 0.001407 | -0.045036 | 0.079598 | 0.050727 | 0.2198 | 0.019363 | 0.055992 | 0.059882 | -0.070087 | -0.016219 | 0.12359 | -0.13876 | -0.18704 | 0.16585 | -122.6743 | 0.12922 | 0.10145 | -0.064399 | -122.7032 | -122.5341 | -0.040559 | -122.7701 | 0.20248 | 0.076397 | 0.11696 | -122.6303 | -122.8927 | 0.22608 | 0.19721 | 0.36629 | 0.14789 | -122.7345 | 0.13026 | 0.27008 | 0.007719 | 0.20637 | -122.9409
3754.2031 | 122.7402 | -0.11444 | 122.7356 | 1.4211e-13 | -0.050886 | -0.022037 | -0.079084 | -0.015614 | -0.0059355 | -0.24967 | 0.039666 | 0.018823 | 0.004679 | 0.055175 | -0.0095994 | -0.012688 | 0.010564 | -0.049614 | 0.079598 | 0.046148 | 0.22896 | 0.014784 | 0.051413 | 0.064461 | -0.065509 | -0.016219 | 0.11901 | -0.12961 | -0.17788 | 0.12923 | -122.656 | 0.10175 | 0.064827 | -0.064398 | -122.6894 | -122.5066 | -0.063444 | -122.7518 | 0.16585 | 0.048932 | 0.11238 | -122.6166 | -122.8652 | 0.19404 | 0.16059 | 0.3434 | 0.12501 | -122.7208 | 0.098222 | 0.23345 | -0.015166 | 0.1789 | -122.9135
3755.9062 | 122.818 | -0.091553 | 122.7264 | 1.4211e-13 | -0.050886 | -0.021823 | -0.079084 | -0.015187 | -0.0055083 | -0.24204 | 0.040093 | 0.018823 | 0.0048926 | 0.055175 | -0.0095994 | -0.017266 | 0.005985 | -0.040457 | 0.079598 | 0.046148 | 0.21522 | 0.0331 | 0.046835 | 0.06904 | -0.065509 | -0.016219 | 0.11901 | -0.14334 | -0.17331 | 0.12465 | -122.6468 | 0.074287 | 0.051096 | -0.073557 | -122.6803 | -122.5112 | -0.081753 | -122.7427 | 0.13839 | 0.026044 | 0.1078 | -122.6074 | -122.8698 | 0.17115 | 0.1377 | 0.30678 | 0.097538 | -122.6933 | 0.075334 | 0.21057 | -0.05179 | 0.16059 | -122.8997
3757.6719 | 122.7219 | -0.10986 | 122.7219 | 1.4211e-13 | -0.050459 | -0.02225 | -0.079084 | -0.015614 | -0.0057219 | -0.23441 | 0.040307 | 0.01861 | 0.004679 | 0.055175 | -0.0093858 | -0.021844 | 0.001407 | -0.049614 | 0.079598 | 0.046148 | 0.22896 | 0.010206 | 0.046835 | 0.06904 | -0.065509 | -0.01164 | 0.11901 | -0.13419 | -0.17788 | 0.12007 | -122.6423 | 0.088019 | 0.060249 | -0.05982 | -122.6757 | -122.4929 | -0.068022 | -122.7335 | 0.1567 | 0.044354 | 0.11238 | -122.6028 | -122.856 | 0.18946 | 0.15601 | 0.33882 | 0.11127 | -122.7117 | 0.098223 | 0.22888 | -0.024323 | 0.1789 | -122.8997
3759.4375 | 122.8546 | -0.091553 | 122.7219 | 1.4211e-13 | -0.0511 | -0.021823 | -0.079084 | -0.015828 | -0.0055083 | -0.23441 | 0.040521 | 0.01861 | 0.004679 | 0.055175 | -0.0095994 | -0.021844 | 0.010564 | -0.049614 | 0.07502 | 0.046148 | 0.22438 | -0.00811 | 0.046835 | 0.059882 | -0.056351 | -0.01164 | 0.12359 | -0.13876 | -0.17331 | 0.083443 | -122.6468 | 0.069709 | 0.041939 | -0.041504 | -122.6757 | -122.4975 | -0.081753 | -122.7335 | 0.13839 | 0.035202 | 0.11695 | -122.5983 | -122.8606 | 0.16657 | 0.1377 | 0.31593 | 0.10212 | -122.73 | 0.079913 | 0.21515 | -0.047212 | 0.15143 | -122.8952
3761.1406 | 122.85 | -0.082397 | 122.7081 | 1.4211e-13 | -0.050886 | -0.022037 | -0.079298 | -0.015614 | -0.0057219 | -0.24204 | 0.040307 | 0.018396 | 0.004679 | 0.054747 | -0.0093858 | -0.026423 | -0.003172 | -0.049614 | 0.07502 | 0.055306 | 0.2198 | 0.046837 | 0.046835 | 0.06904 | -0.070087 | -0.020797 | 0.11444 | -0.13419 | -0.17788 | 0.12923 | -122.6331 | 0.055974 | 0.032783 | -0.096451 | -122.6528 | -122.4883 | -0.095488 | -122.7289 | 0.12923 | 0.01231 | 0.1078 | -122.5937 | -122.8423 | 0.15742 | 0.1377 | 0.3022 | 0.079225 | -122.6613 | 0.0616 | 0.19683 | -0.051789 | 0.15144 | -122.886
3762.9062 | 122.8455 | -0.09613 | 122.7127 | 1.4211e-13 | -0.0511 | -0.02225 | -0.079084 | -0.015828 | -0.0059355 | -0.2573 | 0.040521 | 0.018396 | 0.0048926 | 0.055175 | -0.0091722 | -0.017266 | 0.010564 | -0.054192 | 0.084176 | 0.041569 | 0.2198 | -0.00811 | 0.051413 | 0.064461 | -0.056351 | -0.020797 | 0.11444 | -0.13419 | -0.17331 | 0.08802 | -122.6285 | 0.078864 | 0.041938 | -0.046082 | -122.6711 | -122.4929 | -0.077176 | -122.7335 | 0.14754 | 0.039779 | 0.11695 | -122.5983 | -122.8469 | 0.18031 | 0.1377 | 0.31593 | 0.10669 | -122.7208 | 0.075333 | 0.21057 | -0.038056 | 0.16059 | -122.886
3764.6719 | 122.8592 | -0.07782 | 122.7127 | 1.4211e-13 | -0.0511 | -0.022037 | -0.079512 | -0.015828 | -0.0057219 | -0.24204 | 0.040307 | 0.01861 | 0.004679 | 0.055175 | -0.0093858 | -0.026423 | 0.005985 | -0.045036 | 0.079598 | 0.041569 | 0.22896 | 0.028521 | 0.042256 | 0.064461 | -0.065509 | -0.016219 | 0.11444 | -0.13419 | -0.17788 | 0.10634 | -122.6331 | 0.051397 | 0.032784 | -0.073557 | -122.6711 | -122.4837 | -0.10006 | -122.7289 | 0.12008 | 0.012311 | 0.11238 | -122.5983 | -122.8469 | 0.15742 | 0.11939 | 0.30678 | 0.083805 | -122.6842 | 0.061601 | 0.19226 | -0.056366 | 0.14228 | -122.8906
3766.375 | 122.8775 | -0.07782 | 122.7173 | 1.4211e-13 | -0.050886 | -0.022037 | -0.079084 | -0.015614 | -0.0055083 | -0.24967 | 0.040093 | 0.018823 | 0.0048926 | 0.055388 | -0.0091722 | -0.017266 | 0.010564 | -0.045036 | 0.079598 | 0.050727 | 0.2198 | 0.014784 | 0.037677 | 0.06904 | -0.065509 | -0.016219 | 0.12359 | -0.13876 | -0.17331 | 0.092604 | -122.6377 | 0.060554 | 0.032784 | -0.05982 | -122.6666 | -122.4975 | -0.095486 | -122.7335 | 0.1155 | 0.012311 | 0.1078 | -122.5937 | -122.8561 | 0.15742 | 0.12855 | 0.29762 | 0.088384 | -122.7025 | 0.061601 | 0.20141 | -0.060945 | 0.14686 | -122.8906
3768.1406 | 122.7814 | -0.091553 | 122.7448 | 1.4211e-13 | -0.0511 | -0.022464 | -0.079512 | -0.015828 | -0.0057219 | -0.24204 | 0.040307 | 0.018823 | 0.004679 | 0.055175 | -0.0095994 | -0.017266 | 0.001407 | -0.045036 | 0.07502 | 0.050727 | 0.2198 | 0.001048 | 0.051413 | 0.064461 | -0.056351 | -0.016219 | 0.12359 | -0.13876 | -0.18246 | 0.092601 | -122.6697 | 0.074287 | 0.046517 | -0.046084 | -122.694 | -122.5249 | -0.090911 | -122.761 | 0.14297 | 0.035202 | 0.12611 | -122.6212 | -122.8835 | 0.16657 | 0.14228 | 0.31135 | 0.09296 | -122.7437 | 0.075334 | 0.21515 | -0.047212 | 0.15601 | -122.9272
3769.8438 | 122.8821 | -0.082397 | 122.7219 | 1.4211e-13 | -0.0511 | -0.021823 | -0.079512 | -0.015828 | -0.0055083 | -0.24204 | 0.040093 | 0.018823 | 0.0051062 | 0.055602 | -0.0093858 | -0.017266 | 0.005985 | -0.049614 | 0.07502 | 0.050727 | 0.21522 | 0.005627 | 0.046835 | 0.064461 | -0.065509 | -0.016219 | 0.11901 | -0.13419 | -0.18246 | 0.088024 | -122.6468 | 0.065131 | 0.032783 | -0.055241 | -122.6711 | -122.5066 | -0.10007 | -122.7381 | 0.12923 | 0.016888 | 0.11695 | -122.6028 | -122.856 | 0.15742 | 0.13312 | 0.29762 | 0.088382 | -122.7162 | 0.066178 | 0.20141 | -0.051789 | 0.14686 | -122.9043
3771.6094 | 122.8455 | -0.082397 | 122.7264 | 1.4211e-13 | -0.050673 | -0.021823 | -0.079298 | -0.015401 | -0.0057219 | -0.24204 | 0.040093 | 0.018396 | 0.0048926 | 0.055175 | -0.0095994 | -0.017266 | 0.015142 | -0.049614 | 0.07502 | 0.055306 | 0.23354 | 0.0331 | 0.051413 | 0.073618 | -0.070087 | -0.01164 | 0.11901 | -0.13876 | -0.17331 | 0.1155 | -122.6514 | 0.065131 | 0.032783 | -0.082714 | -122.6711 | -122.4929 | -0.090909 | -122.7381 | 0.13381 | 0.01231 | 0.10322 | -122.6074 | -122.8652 | 0.15742 | 0.1377 | 0.31593 | 0.097539 | -122.6933 | 0.070757 | 0.20141 | -0.056368 | 0.15602 | -122.8997
3773.375 | 122.7676 | -0.10986 | 122.7448 | 1.4211e-13 | -0.051314 | -0.02225 | -0.079298 | -0.015614 | -0.0057219 | -0.24967 | 0.040307 | 0.018396 | 0.004679 | 0.055602 | -0.0095994 | -0.026423 | 0.005985 | -0.049614 | 0.079598 | 0.050727 | 0.2198 | 0.010206 | 0.046835 | 0.064461 | -0.074666 | -0.016219 | 0.11444 | -0.12045 | -0.17788 | 0.12007 | -122.6652 | 0.08344 | 0.060249 | -0.05982 | -122.694 | -122.5249 | -0.068022 | -122.761 | 0.1567 | 0.035197 | 0.10322 | -122.6303 | -122.8652 | 0.18946 | 0.16059 | 0.32966 | 0.11585 | -122.7345 | 0.093644 | 0.2243 | -0.010587 | 0.17432 | -122.9226
3775.1406 | 122.8455 | -0.09613 | 122.7036 | 1.4211e-13 | -0.051314 | -0.021823 | -0.079512 | -0.015614 | -0.0057219 | -0.2573 | 0.040093 | 0.018396 | 0.0048926 | 0.055175 | -0.0093858 | -0.026423 | 0.005985 | -0.045036 | 0.084176 | 0.050727 | 0.22438 | 0.046837 | 0.042256 | 0.064461 | -0.056351 | -0.016219 | 0.11901 | -0.13876 | -0.17331 | 0.14297 | -122.6194 | 0.069707 | 0.051094 | -0.091873 | -122.6528 | -122.4792 | -0.077176 | -122.7198 | 0.13839 | 0.039779 | 0.11695 | -122.5845 | -122.8423 | 0.18031 | 0.14686 | 0.32051 | 0.10211 | -122.6567 | 0.079911 | 0.21514 | -0.042635 | 0.16059 | -122.8769
3776.8438 | 122.85 | -0.064087 | 122.7173 | 1.4211e-13 | -0.0511 | -0.022037 | -0.079084 | -0.015614 | -0.0057219 | -0.23441 | 0.040307 | 0.01861 | 0.004679 | 0.055388 | -0.0098132 | -0.017266 | 0.005985 | -0.045036 | 0.079598 | 0.050727 | 0.22438 | -0.035584 | 0.042256 | 0.059882 | -0.070087 | -0.016219 | 0.11444 | -0.13876 | -0.18704 | 0.028503 | -122.6377 | 0.046821 | 0.019051 | -0.009452 | -122.6666 | -122.4929 | -0.12296 | -122.7335 | 0.10634 | -0.006 | 0.11696 | -122.6028 | -122.8561 | 0.14369 | 0.11481 | 0.28847 | 0.070072 | -122.7529 | 0.047868 | 0.17852 | -0.074678 | 0.12397 | -122.9043
3778.625 | 122.85 | -0.086975 | 122.7127 | 1.4211e-13 | -0.051314 | -0.022037 | -0.079725 | -0.016042 | -0.0055083 | -0.24967 | 0.040307 | 0.018182 | 0.0051062 | 0.055388 | -0.0095994 | -0.021844 | 0.010564 | -0.045036 | 0.07502 | 0.046148 | 0.22896 | 0.023942 | 0.042256 | 0.06904 | -0.065509 | -0.020797 | 0.11901 | -0.13419 | -0.17788 | 0.11092 | -122.6377 | 0.065131 | 0.041939 | -0.068978 | -122.6666 | -122.4837 | -0.09091 | -122.7335 | 0.12923 | 0.021466 | 0.11238 | -122.5937 | -122.8469 | 0.162 | 0.13312 | 0.31593 | 0.097539 | -122.6888 | 0.066178 | 0.20599 | -0.047211 | 0.15602 | -122.8906
3780.3125 | 122.8043 | -0.10071 | 122.7402 | 1.4211e-13 | -0.0511 | -0.021823 | -0.07887 | -0.015614 | -0.0057219 | -0.24967 | 0.039666 | 0.018396 | 0.0044652 | 0.055602 | -0.0098132 | -0.021844 | 0.010564 | -0.049614 | 0.079598 | 0.050727 | 0.22438 | 0.042258 | 0.046835 | 0.06904 | -0.06093 | -0.016219 | 0.11444 | -0.12961 | -0.18246 | 0.14297 | -122.6606 | 0.078864 | 0.051094 | -0.091872 | -122.6894 | -122.5158 | -0.081756 | -122.7564 | 0.14754 | 0.039778 | 0.12153 | -122.6257 | -122.8698 | 0.18031 | 0.15144 | 0.32509 | 0.11127 | -122.6979 | 0.084489 | 0.21514 | -0.028899 | 0.16975 | -122.9226
3782.0781 | 122.8638 | -0.091553 | 122.6944 | 1.4211e-13 | -0.051527 | -0.022037 | -0.079298 | -0.015828 | -0.0057219 | -0.22678 | 0.040093 | 0.018396 | 0.0048926 | 0.055175 | -0.0095994 | -0.021844 | 0.001407 | -0.040457 | 0.079598 | 0.041569 | 0.22438 | 0.042258 | 0.042256 | 0.064461 | -0.056351 | -0.016219 | 0.11444 | -0.12961 | -0.17788 | 0.13381 | -122.6148 | 0.069709 | 0.051096 | -0.082715 | -122.6528 | -122.47 | -0.086332 | -122.7106 | 0.13381 | 0.035202 | 0.12153 | -122.58 | -122.824 | 0.17115 | 0.13312 | 0.31593 | 0.09296 | -122.6521 | 0.075334 | 0.20599 | -0.038054 | 0.15601 | -122.8723
3783.8438 | 122.7631 | -0.1236 | 122.7585 | 1.4211e-13 | -0.0511 | -0.021823 | -0.079084 | -0.015614 | -0.0057219 | -0.24204 | 0.040093 | 0.018396 | 0.0048926 | 0.055388 | -0.0095994 | -0.021844 | 0.005985 | -0.049614 | 0.079598 | 0.041569 | 0.22896 | 0.051416 | 0.042256 | 0.064461 | -0.065509 | -0.01164 | 0.11444 | -0.12961 | -0.18246 | 0.17501 | -122.6789 | 0.10175 | 0.073982 | -0.10103 | -122.7169 | -122.5295 | -0.058868 | -122.7701 | 0.16585 | 0.058087 | 0.11695 | -122.644 | -122.8881 | 0.20319 | 0.16517 | 0.35256 | 0.12958 | -122.7071 | 0.11196 | 0.23803 | -0.006011 | 0.18806 | -122.9409
3785.5469 | 122.8134 | -0.086975 | 122.7402 | 1.4211e-13 | -0.0511 | -0.021609 | -0.079298 | -0.015614 | -0.0061493 | -0.23441 | 0.040093 | 0.01861 | 0.0048926 | 0.054961 | -0.0093858 | -0.021844 | 0.005985 | -0.049614 | 0.088755 | 0.050727 | 0.22438 | 0.051416 | 0.042256 | 0.064461 | -0.065509 | -0.016219 | 0.11901 | -0.12961 | -0.18246 | 0.13839 | -122.6514 | 0.065131 | 0.037361 | -0.10103 | -122.6894 | -122.5158 | -0.095489 | -122.7564 | 0.12923 | 0.021466 | 0.11695 | -122.6212 | -122.8698 | 0.17573 | 0.1377 | 0.31136 | 0.09296 | -122.6888 | 0.070756 | 0.20599 | -0.042632 | 0.15144 | -122.9226
3787.2969 | 122.7676 | -0.10529 | 122.7493 | 1.4211e-13 | -0.051527 | -0.022037 | -0.079084 | -0.015614 | -0.0059355 | -0.23441 | 0.040093 | 0.018823 | 0.0051062 | 0.055388 | -0.0095994 | -0.026423 | 0.010564 | -0.045036 | 0.084176 | 0.046148 | 0.22438 | 0.042258 | 0.051413 | 0.055303 | -0.056351 | -0.020797 | 0.10986 | -0.12961 | -0.17331 | 0.14754 | -122.6652 | 0.078863 | 0.06025 | -0.087294 | -122.7032 | -122.5249 | -0.06802 | -122.7701 | 0.1567 | 0.048935 | 0.11695 | -122.6395 | -122.8789 | 0.18946 | 0.15143 | 0.32967 | 0.11585 | -122.7071 | 0.084489 | 0.21514 | -0.024321 | 0.16059 | -122.9226
3789.0625 | 122.7722 | -0.10986 | 122.7722 | 1.4211e-13 | -0.051527 | -0.022037 | -0.079084 | -0.015614 | -0.0057219 | -0.24204 | 0.040093 | 0.01861 | 0.0048926 | 0.055388 | -0.0095994 | -0.017266 | 0.010564 | -0.040457 | 0.084176 | 0.046148 | 0.2198 | 0.042258 | 0.051413 | 0.073618 | -0.070087 | -0.020797 | 0.11444 | -0.13876 | -0.17788 | 0.15212 | -122.688 | 0.092597 | 0.069406 | -0.082715 | -122.7261 | -122.5524 | -0.068022 | -122.793 | 0.16128 | 0.039776 | 0.1078 | -122.6578 | -122.911 | 0.19404 | 0.15601 | 0.32966 | 0.12043 | -122.73 | 0.089066 | 0.2243 | -0.028902 | 0.18348 | -122.9501
3790.75 | 122.8683 | -0.073242 | 122.7219 | 1.4211e-13 | -0.051314 | -0.02225 | -0.078657 | -0.016042 | -0.0063629 | -0.24204 | 0.040093 | 0.018823 | 0.0044652 | 0.055388 | -0.010027 | -0.021844 | 0.010564 | -0.045036 | 0.088755 | 0.055306 | 0.2198 | 0.037679 | 0.046835 | 0.06904 | -0.065509 | -0.016219 | 0.11901 | -0.092979 | -0.1321 | 0.11092 | -122.6331 | 0.051398 | 0.028206 | -0.082715 | -122.6666 | -122.5021 | -0.058855 | -122.7381 | 0.12008 | 0.007733 | 0.066588 | -122.6028 | -122.8148 | 0.162 | 0.12855 | 0.29304 | 0.083806 | -122.6842 | 0.057023 | 0.19226 | -0.019737 | 0.14228 | -122.854
3792.5156 | 122.8912 | -0.07782 | 122.7356 | 1.4211e-13 | -0.051314 | -0.022037 | -0.079084 | -0.015614 | -0.0055083 | -0.2573 | 0.03988 | 0.018396 | 0.0044652 | 0.055816 | -0.0095994 | -0.021844 | 0.005985 | -0.049614 | 0.079598 | 0.050727 | 0.22438 | 0.019363 | 0.046835 | 0.06904 | -0.065509 | -0.020797 | 0.11444 | -0.13419 | -0.18246 | 0.097183 | -122.656 | 0.055976 | 0.028206 | -0.068977 | -122.6849 | -122.5112 | -0.10464 | -122.7564 | 0.12466 | 0.012311 | 0.11695 | -122.6212 | -122.8698 | 0.15742 | 0.12855 | 0.3022 | 0.083805 | -122.7162 | 0.057023 | 0.19226 | -0.056366 | 0.14686 | -122.9181
3794.2812 | 122.7951 | -0.10529 | 122.7264 | 1.4211e-13 | -0.051741 | -0.02225 | -0.079084 | -0.015614 | -0.0059355 | -0.24204 | 0.040093 | 0.018396 | 0.0051062 | 0.055388 | -0.0091722 | -0.021844 | 0.001407 | -0.045036 | 0.07502 | 0.050727 | 0.2198 | -0.003531 | 0.046835 | 0.06904 | -0.06093 | -0.020797 | 0.11901 | -0.11129 | -0.18246 | 0.10175 | -122.6514 | 0.083442 | 0.06025 | -0.041505 | -122.6757 | -122.5066 | -0.077178 | -122.7472 | 0.15212 | 0.044356 | 0.12153 | -122.6074 | -122.8377 | 0.18031 | 0.15601 | 0.32509 | 0.10669 | -122.73 | 0.084489 | 0.2243 | -0.006007 | 0.17433 | -122.9089
3796.0469 | 122.7676 | -0.10529 | 122.731 | 1.4211e-13 | -0.050886 | -0.02225 | -0.079298 | -0.015614 | -0.0057219 | -0.24967 | 0.040307 | 0.01861 | 0.0048926 | 0.055602 | -0.0098132 | -0.021844 | 0.001407 | -0.049614 | 0.084176 | 0.050727 | 0.2198 | 0.005627 | 0.051413 | 0.055303 | -0.065509 | -0.01164 | 0.11901 | -0.13419 | -0.16873 | 0.11091 | -122.6468 | 0.083442 | 0.055672 | -0.055241 | -122.6803 | -122.5112 | -0.063442 | -122.7427 | 0.1567 | 0.039777 | 0.10322 | -122.612 | -122.8652 | 0.18946 | 0.15601 | 0.32509 | 0.10669 | -122.7254 | 0.093646 | 0.2243 | -0.0289 | 0.16059 | -122.8997
3797.8125 | 122.8592 | -0.07782 | 122.7127 | 1.4211e-13 | -0.051527 | -0.022037 | -0.07887 | -0.015614 | -0.0059355 | -0.24204 | 0.040093 | 0.01861 | 0.0051062 | 0.055388 | -0.0095994 | -0.012688 | 0.010564 | -0.040457 | 0.079598 | 0.050727 | 0.22438 | 0.0331 | 0.046835 | 0.06904 | -0.06093 | -0.016219 | 0.12359 | -0.12961 | -0.17788 | 0.11092 | -122.6331 | 0.065132 | 0.037363 | -0.073557 | -122.662 | -122.4883 | -0.10006 | -122.7289 | 0.12466 | 0.01689 | 0.11695 | -122.5891 | -122.8423 | 0.15742 | 0.12855 | 0.3022 | 0.088384 | -122.6796 | 0.061601 | 0.20141 | -0.051787 | 0.14686 | -122.8906
3799.5312 | 122.8867 | -0.07782 | 122.699 | 1.4211e-13 | -0.051527 | -0.021823 | -0.079084 | -0.015614 | -0.0059355 | -0.24967 | 0.03988 | 0.018182 | 0.004679 | 0.055602 | -0.0093858 | -0.021844 | 0.015142 | -0.049614 | 0.084176 | 0.046148 | 0.22438 | 0.0331 | 0.042256 | 0.064461 | -0.06093 | -0.01164 | 0.11444 | -0.13419 | -0.17331 | 0.11092 | -122.6148 | 0.055976 | 0.028206 | -0.082714 | -122.6528 | -122.4746 | -0.095486 | -122.7106 | 0.12008 | 0.01689 | 0.11238 | -122.5845 | -122.8332 | 0.162 | 0.12397 | 0.3022 | 0.092962 | -122.6659 | 0.06618 | 0.19226 | -0.056366 | 0.14228 | -122.8723
3801.2344 | 122.8317 | -0.091553 | 122.7219 | 1.4211e-13 | -0.0511 | -0.021823 | -0.079298 | -0.015828 | -0.0055083 | -0.24204 | 0.040093 | 0.01861 | 0.004679 | 0.056029 | -0.0098132 | -0.017266 | 0.015142 | -0.045036 | 0.079598 | 0.050727 | 0.22896 | -0.035584 | 0.051413 | 0.06904 | -0.065509 | -0.016219 | 0.12359 | -0.14334 | -0.18246 | 0.055969 | -122.6423 | 0.074287 | 0.046517 | -0.009452 | -122.6711 | -122.4929 | -0.090911 | -122.7381 | 0.14297 | 0.026044 | 0.11695 | -122.5983 | -122.8652 | 0.17115 | 0.14228 | 0.32051 | 0.10669 | -122.7574 | 0.075334 | 0.21515 | -0.05179 | 0.16059 | -122.9043
3802.9844 | 122.8912 | -0.054932 | 122.7356 | 1.4211e-13 | -0.051527 | -0.022037 | -0.079084 | -0.015401 | -0.0061493 | -0.23441 | 0.040093 | 0.018396 | 0.0048926 | 0.055388 | -0.0095994 | -0.012688 | 0.001407 | -0.045036 | 0.084176 | 0.055306 | 0.21522 | 0.005627 | 0.046835 | 0.064461 | -0.06093 | -0.01164 | 0.11444 | -0.14334 | -0.17788 | 0.060559 | -122.6514 | 0.042244 | 0.009896 | -0.050663 | -122.6803 | -122.5204 | -0.12295 | -122.7472 | 0.10177 | -0.005998 | 0.11695 | -122.6212 | -122.8789 | 0.13911 | 0.11024 | 0.27016 | 0.056339 | -122.73 | 0.043292 | 0.16937 | -0.088411 | 0.11939 | -122.9135
3804.6875 | 122.8088 | -0.09613 | 122.7585 | 1.4211e-13 | -0.051741 | -0.02225 | -0.079298 | -0.015828 | -0.0057219 | -0.23441 | 0.03988 | 0.019037 | 0.004679 | 0.055816 | -0.0095994 | -0.012688 | 0.001407 | -0.040457 | 0.079598 | 0.050727 | 0.22438 | -0.012689 | 0.051413 | 0.064461 | -0.070087 | -0.016219 | 0.10986 | -0.13419 | -0.16873 | 0.083441 | -122.6789 | 0.083442 | 0.055673 | -0.027768 | -122.7078 | -122.5341 | -0.072598 | -122.7747 | 0.14754 | 0.026043 | 0.098641 | -122.6486 | -122.8927 | 0.17573 | 0.14686 | 0.32051 | 0.097537 | -122.7712 | 0.079911 | 0.20599 | -0.038056 | 0.16059 | -122.9272
3806.3906 | 122.7722 | -0.10071 | 122.7676 | 1.4211e-13 | -0.051527 | -0.022464 | -0.079298 | -0.015614 | -0.0055083 | -0.24967 | 0.040093 | 0.01861 | 0.0044652 | 0.055602 | -0.0098132 | -0.021844 | 0.001407 | -0.045036 | 0.084176 | 0.050727 | 0.2198 | 0.010206 | 0.051413 | 0.064461 | -0.074666 | -0.01164 | 0.12359 | -0.13876 | -0.18246 | 0.11091 | -122.6835 | 0.078864 | 0.055672 | -0.055242 | -122.7169 | -122.5478 | -0.081756 | -122.7793 | 0.15212 | 0.026042 | 0.1078 | -122.644 | -122.9064 | 0.18488 | 0.15144 | 0.32051 | 0.10212 | -122.7574 | 0.089068 | 0.2243 | -0.038057 | 0.16517 | -122.9501
3808.1562 | 122.8546 | -0.086975 | 122.7356 | 1.4211e-13 | -0.051527 | -0.021823 | -0.079084 | -0.015828 | -0.0059355 | -0.23441 | 0.039666 | 0.018182 | 0.004679 | 0.055816 | -0.010027 | -0.017266 | 0.005985 | -0.049614 | 0.079598 | 0.050727 | 0.22438 | 0.010206 | 0.051413 | 0.073618 | -0.056351 | -0.007062 | 0.11901 | -0.13876 | -0.18246 | 0.097181 | -122.656 | 0.069709 | 0.037361 | -0.05982 | -122.6849 | -122.5112 | -0.095489 | -122.7427 | 0.13839 | 0.030624 | 0.12611 | -122.6166 | -122.8744 | 0.16657 | 0.1377 | 0.31136 | 0.09296 | -122.7254 | 0.079913 | 0.20599 | -0.05179 | 0.16059 | -122.9181
3809.9219 | 122.7814 | -0.091553 | 122.7493 | 1.4211e-13 | -0.051527 | -0.021823 | -0.079084 | -0.016042 | -0.0059355 | -0.24967 | 0.040093 | 0.01861 | 0.0048926 | 0.055602 | -0.0098132 | -0.017266 | 0.010564 | -0.049614 | 0.079598 | 0.050727 | 0.22438 | 0.005627 | 0.042256 | 0.078197 | -0.06093 | -0.01164 | 0.11901 | -0.13876 | -0.18246 | 0.09718 | -122.6697 | 0.074287 | 0.041939 | -0.055241 | -122.6986 | -122.5249 | -0.090911 | -122.761 | 0.13381 | 0.030623 | 0.12153 | -122.6303 | -122.8881 | 0.17115 | 0.14228 | 0.31593 | 0.10212 | -122.7437 | 0.079913 | 0.21057 | -0.047212 | 0.16975 | -122.9318
3811.7031 | 122.8271 | -0.086975 | 122.7631 | 1.4211e-13 | -0.051527 | -0.021823 | -0.07887 | -0.015828 | -0.0055083 | -0.23441 | 0.040093 | 0.018396 | 0.0044652 | 0.055388 | -0.0095994 | -0.017266 | 0.005985 | -0.045036 | 0.079598 | 0.046148 | 0.22438 | 0.014784 | 0.046835 | 0.06904 | -0.06093 | -0.016219 | 0.11901 | -0.13876 | -0.17788 | 0.10176 | -122.6835 | 0.069709 | 0.041939 | -0.05982 | -122.7169 | -122.5387 | -0.09091 | -122.7793 | 0.13381 | 0.026045 | 0.11695 | -122.644 | -122.9018 | 0.16657 | 0.13312 | 0.31136 | 0.09296 | -122.7483 | 0.070756 | 0.20599 | -0.05179 | 0.15602 | -122.9409
3813.4062 | 122.85 | -0.091553 | 122.7631 | 1.4211e-13 | -0.051741 | -0.021823 | -0.07887 | -0.016042 | -0.0057219 | -0.24967 | 0.040093 | 0.01861 | 0.0042516 | 0.056029 | -0.0095994 | -0.012688 | 0.001407 | -0.049614 | 0.084176 | 0.050727 | 0.2198 | 0.005627 | 0.051413 | 0.06904 | -0.065509 | -0.016219 | 0.10986 | -0.13419 | -0.17788 | 0.09718 | -122.6789 | 0.078865 | 0.041939 | -0.055241 | -122.7123 | -122.5433 | -0.086332 | -122.7793 | 0.14297 | 0.026044 | 0.11238 | -122.6532 | -122.8972 | 0.17573 | 0.14228 | 0.31135 | 0.09296 | -122.7574 | 0.075334 | 0.20141 | -0.042633 | 0.16059 | -122.9409
3815.1719 | 122.8226 | -0.10529 | 122.7676 | 1.4211e-13 | -0.051955 | -0.022037 | -0.07887 | -0.015828 | -0.0063629 | -0.24204 | 0.040093 | 0.018182 | 0.004679 | 0.055602 | -0.0098132 | -0.021844 | 0.010564 | -0.049614 | 0.07502 | 0.050727 | 0.22438 | 0.014784 | 0.042256 | 0.06904 | -0.06093 | -0.016219 | 0.12817 | -0.14334 | -0.16873 | 0.12007 | -122.6926 | 0.083442 | 0.055672 | -0.064398 | -122.7169 | -122.5433 | -0.063442 | -122.7839 | 0.14754 | 0.044356 | 0.1078 | -122.6395 | -122.911 | 0.18031 | 0.15601 | 0.32967 | 0.11585 | -122.7529 | 0.089067 | 0.23346 | -0.038057 | 0.17433 | -122.9364
3816.9375 | 122.8638 | -0.091553 | 122.7448 | 1.4211e-13 | -0.051741 | -0.022037 | -0.079298 | -0.015614 | -0.0057219 | -0.24204 | 0.03988 | 0.01861 | 0.0048926 | 0.055816 | -0.010027 | -0.021844 | 0.005985 | -0.049614 | 0.079598 | 0.050727 | 0.2198 | -0.049321 | 0.042256 | 0.06904 | -0.06093 | -0.016219 | 0.12817 | -0.13876 | -0.17331 | 0.042232 | -122.6652 | 0.069709 | 0.041939 | -0.000293 | -122.694 | -122.5249 | -0.081753 | -122.761 | 0.13381 | 0.030623 | 0.11238 | -122.6166 | -122.8835 | 0.17115 | 0.14228 | 0.31135 | 0.097538 | -122.7941 | 0.075334 | 0.21973 | -0.047212 | 0.16059 | -122.9181
3818.7188 | 122.7676 | -0.1236 | 122.7768 | 1.4211e-13 | -0.051527 | -0.022037 | -0.079084 | -0.015828 | -0.0059355 | -0.23441 | 0.03988 | 0.018396 | 0.0044652 | 0.056029 | -0.010027 | -0.021844 | -0.003172 | -0.049614 | 0.084176 | 0.050727 | 0.22896 | -0.053899 | 0.037677 | 0.06904 | -0.065509 | -0.01164 | 0.11901 | -0.13419 | -0.17788 | 0.069697 | -122.6926 | 0.10175 | 0.073982 | 0.004285 | -122.7261 | -122.5478 | -0.054289 | -122.7884 | 0.16127 | 0.058087 | 0.11238 | -122.6578 | -122.911 | 0.20777 | 0.17432 | 0.35256 | 0.12042 | -122.8307 | 0.11196 | 0.24261 | -0.01059 | 0.19264 | -122.9547
3820.4375 | 122.8683 | -0.10071 | 122.7585 | 1.4211e-13 | -0.051527 | -0.02225 | -0.079084 | -0.016042 | -0.0061493 | -0.24204 | 0.040093 | 0.018396 | 0.004679 | 0.055816 | -0.0098132 | -0.017266 | 0.005985 | -0.045036 | 0.079598 | 0.050727 | 0.22438 | -0.035584 | 0.037677 | 0.073618 | -0.06093 | -0.016219 | 0.11901 | -0.13876 | -0.17331 | 0.065124 | -122.6789 | 0.083442 | 0.055672 | -0.009452 | -122.7078 | -122.5341 | -0.072598 | -122.7747 | 0.13839 | 0.039778 | 0.11238 | -122.6395 | -122.8972 | 0.18031 | 0.15144 | 0.32509 | 0.10669 | -122.7941 | 0.084489 | 0.21972 | -0.038057 | 0.17433 | -122.9318
3822.2031 | 122.8592 | -0.10529 | 122.7356 | 1.4211e-13 | -0.051955 | -0.022037 | -0.07887 | -0.015828 | -0.0063629 | -0.22678 | 0.039666 | 0.01861 | 0.0044652 | 0.055602 | -0.0098132 | -0.012688 | 0.005985 | -0.035879 | 0.079598 | 0.055306 | 0.23354 | -0.049321 | 0.046835 | 0.06904 | -0.065509 | -0.016219 | 0.11901 | -0.12961 | -0.17788 | 0.055965 | -122.656 | 0.092598 | 0.069407 | 0.013442 | -122.6803 | -122.5021 | -0.072599 | -122.7518 | 0.15212 | 0.039777 | 0.11238 | -122.6166 | -122.8652 | 0.18488 | 0.16059 | 0.33882 | 0.11127 | -122.7849 | 0.089067 | 0.2243 | -0.024321 | 0.17433 | -122.9135
3823.9688 | 122.8043 | -0.11902 | 122.7768 | 1.4211e-13 | -0.051741 | -0.022037 | -0.07887 | -0.015401 | -0.0059355 | -0.24204 | 0.040093 | 0.017969 | 0.0044652 | 0.055602 | -0.0098132 | -0.012688 | 0.001407 | -0.049614 | 0.084176 | 0.055306 | 0.2198 | -0.003531 | 0.051413 | 0.073618 | -0.074666 | -0.007062 | 0.11901 | -0.13419 | -0.17788 | 0.11549 | -122.6926 | 0.10633 | 0.069405 | -0.046083 | -122.7215 | -122.557 | -0.058866 | -122.7839 | 0.17043 | 0.044353 | 0.10322 | -122.6578 | -122.911 | 0.2032 | 0.17433 | 0.33882 | 0.12043 | -122.7803 | 0.11196 | 0.23803 | -0.015167 | 0.19264 | -122.9547
3825.6719 | 122.905 | -0.059509 | 122.7448 | 1.4211e-13 | -0.052168 | -0.02225 | -0.078657 | -0.015401 | -0.0061493 | -0.23441 | 0.040093 | 0.018182 | 0.0044652 | 0.055602 | -0.0095994 | -0.021844 | 0.005985 | -0.049614 | 0.084176 | 0.046148 | 0.22438 | 0.001048 | 0.042256 | 0.06904 | -0.06093 | -0.020797 | 0.11901 | -0.13876 | -0.18246 | 0.060557 | -122.6606 | 0.037665 | 0.009895 | -0.050662 | -122.6986 | -122.5204 | -0.12295 | -122.7655 | 0.10176 | -0.001421 | 0.12153 | -122.6257 | -122.8835 | 0.14369 | 0.10566 | 0.28389 | 0.065494 | -122.7437 | 0.038712 | 0.17852 | -0.079256 | 0.12855 | -122.9272
3827.375 | 122.9187 | -0.068665 | 122.7081 | 1.4211e-13 | -0.052168 | -0.022037 | -0.07887 | -0.015401 | -0.0059355 | -0.24204 | 0.03988 | 0.018182 | 0.004679 | 0.055816 | -0.0095994 | -0.017266 | 0.010564 | -0.045036 | 0.084176 | 0.059885 | 0.2198 | -0.017268 | 0.046835 | 0.078197 | -0.06093 | -0.016219 | 0.11444 | -0.13876 | -0.17331 | 0.051397 | -122.624 | 0.051399 | 0.023629 | -0.027768 | -122.6482 | -122.4883 | -0.10464 | -122.7243 | 0.1155 | 0.007735 | 0.11238 | -122.5937 | -122.8469 | 0.15284 | 0.12855 | 0.28847 | 0.079229 | -122.7254 | 0.052446 | 0.1831 | -0.0701 | 0.14686 | -122.8814
3829.1406 | 122.8867 | -0.082397 | 122.7585 | 1.4211e-13 | -0.051955 | -0.022037 | -0.078443 | -0.016042 | -0.0063629 | -0.23441 | 0.03988 | 0.018396 | 0.0048926 | 0.056029 | -0.0098132 | -0.021844 | 0.005985 | -0.049614 | 0.079598 | 0.046148 | 0.21522 | 0.0331 | 0.042256 | 0.06904 | -0.070087 | -0.007062 | 0.12359 | -0.13419 | -0.18246 | 0.1155 | -122.6789 | 0.060553 | 0.032783 | -0.082714 | -122.7123 | -122.5433 | -0.10007 | -122.7655 | 0.12465 | 0.01231 | 0.11238 | -122.6349 | -122.8927 | 0.162 | 0.12854 | 0.29762 | 0.088382 | -122.7254 | 0.075335 | 0.20599 | -0.051789 | 0.15144 | -122.9409
3830.9062 | 122.7722 | -0.11444 | 122.7951 | 1.4211e-13 | -0.051955 | -0.02225 | -0.078657 | -0.015614 | -0.0059355 | -0.24204 | 0.039453 | 0.01861 | 0.0042516 | 0.055816 | -0.0098132 | -0.012688 | 0.001407 | -0.035879 | 0.084176 | 0.046148 | 0.21522 | 0.005627 | 0.060571 | 0.06904 | -0.065509 | -0.007062 | 0.10986 | -0.10671 | -0.17788 | 0.12007 | -122.7109 | 0.10175 | 0.078562 | -0.041506 | -122.749 | -122.5799 | -0.063444 | -122.8022 | 0.17501 | 0.048932 | 0.11238 | -122.6852 | -122.9018 | 0.19862 | 0.16059 | 0.32966 | 0.11585 | -122.7895 | 0.10738 | 0.2243 | 0.007727 | 0.18348 | -122.973
3832.625 | 122.8271 | -0.086975 | 122.7768 | 1.4211e-13 | -0.052168 | -0.022037 | -0.079084 | -0.016042 | -0.0061493 | -0.24204 | 0.039666 | 0.018182 | 0.0044652 | 0.055602 | -0.0098132 | -0.021844 | 0.010564 | -0.049614 | 0.070441 | 0.046148 | 0.22438 | 0.023942 | 0.042256 | 0.06904 | -0.070087 | -0.016219 | 0.12359 | -0.13419 | -0.18246 | 0.11092 | -122.7064 | 0.065131 | 0.037361 | -0.073556 | -122.7306 | -122.5524 | -0.095489 | -122.793 | 0.12923 | 0.016888 | 0.11238 | -122.6532 | -122.911 | 0.15742 | 0.13312 | 0.31136 | 0.097539 | -122.7529 | 0.070756 | 0.21057 | -0.047211 | 0.15602 | -122.9593
3834.4062 | 122.9233 | -0.07782 | 122.7173 | 1.4211e-13 | -0.051955 | -0.022037 | -0.079084 | -0.015828 | -0.0059355 | -0.22678 | 0.03988 | 0.018182 | 0.0044652 | 0.055816 | -0.0098132 | -0.017266 | 0.010564 | -0.045036 | 0.07502 | 0.050727 | 0.22438 | -0.021847 | 0.042256 | 0.06904 | -0.06093 | -0.020797 | 0.11901 | -0.12961 | -0.17788 | 0.055973 | -122.6423 | 0.060554 | 0.032784 | -0.023189 | -122.6666 | -122.4929 | -0.10006 | -122.7381 | 0.12008 | 0.01689 | 0.11695 | -122.5983 | -122.8469 | 0.15284 | 0.12855 | 0.3022 | 0.088384 | -122.7391 | 0.057023 | 0.19683 | -0.051787 | 0.14686 | -122.8952
3836.1719 | 122.7859 | -0.11902 | 122.7997 | 1.4211e-13 | -0.052168 | -0.022464 | -0.07887 | -0.015614 | -0.0061493 | -0.23441 | 0.03988 | 0.01861 | 0.0048926 | 0.055816 | -0.010027 | -0.017266 | 0.005985 | -0.045036 | 0.07502 | 0.050727 | 0.22438 | -0.035584 | 0.042256 | 0.059882 | -0.070087 | -0.016219 | 0.12359 | -0.14334 | -0.18246 | 0.083435 | -122.7247 | 0.10175 | 0.073983 | -0.009452 | -122.749 | -122.5753 | -0.063445 | -122.8159 | 0.16128 | 0.048932 | 0.11238 | -122.6761 | -122.943 | 0.19404 | 0.16975 | 0.3434 | 0.125 | -122.8353 | 0.1028 | 0.24261 | -0.024324 | 0.1789 | -122.9821
3837.9375 | 122.7722 | -0.091553 | 122.7905 | 1.4211e-13 | -0.051955 | -0.022037 | -0.07887 | -0.015828 | -0.0061493 | -0.24204 | 0.040093 | 0.01861 | 0.0044652 | 0.055816 | -0.0098132 | -0.021844 | 0.005985 | -0.045036 | 0.079598 | 0.023254 | 0.2198 | -0.058478 | 0.046835 | 0.064461 | -0.06093 | -0.01164 | 0.12359 | -0.13876 | -0.18246 | 0.033075 | -122.7109 | 0.069709 | 0.046517 | 0.013442 | -122.7673 | -122.5707 | -0.090911 | -122.8022 | 0.13839 | 0.030623 | 0.12153 | -122.6669 | -122.9293 | 0.17115 | 0.11481 | 0.31135 | 0.097538 | -122.849 | 0.079913 | 0.21515 | -0.047212 | 0.15601 | -122.973
3839.6562 | 122.9141 | -0.054932 | 122.7631 | 1.4211e-13 | -0.052382 | -0.022037 | -0.078443 | -0.015828 | -0.0063629 | -0.21915 | 0.039666 | 0.018396 | 0.0048926 | 0.056029 | -0.0098132 | -0.012688 | 0.001407 | -0.049614 | 0.07502 | 0.055306 | 0.23354 | -0.044742 | 0.051413 | 0.073618 | -0.065509 | -0.020797 | 0.11901 | -0.13419 | -0.17788 | 0.01019 | -122.688 | 0.042244 | 0.005318 | -0.004872 | -122.7078 | -122.5295 | -0.12295 | -122.7839 | 0.10634 | -0.010577 | 0.11238 | -122.644 | -122.8972 | 0.12995 | 0.11024 | 0.28847 | 0.056339 | -122.8078 | 0.034135 | 0.17395 | -0.079254 | 0.12855 | -122.9409
3841.3594 | 122.8592 | -0.086975 | 122.7356 | 1.4211e-13 | -0.052168 | -0.022037 | -0.079084 | -0.015614 | -0.0061493 | -0.24204 | 0.039666 | 0.018396 | 0.0044652 | 0.055602 | -0.0098132 | -0.012688 | 0.010564 | -0.045036 | 0.088755 | 0.050727 | 0.22438 | -0.017268 | 0.046835 | 0.06904 | -0.056351 | -0.01164 | 0.11444 | -0.13419 | -0.18246 | 0.069707 | -122.6468 | 0.074287 | 0.041939 | -0.027768 | -122.6849 | -122.5112 | -0.095489 | -122.7472 | 0.13381 | 0.030624 | 0.12611 | -122.6212 | -122.8698 | 0.17573 | 0.1377 | 0.31136 | 0.097539 | -122.7529 | 0.075335 | 0.20141 | -0.047211 | 0.15602 | -122.9181
3843.1094 | 122.8867 | -0.082397 | 122.7264 | 1.4211e-13 | -0.052382 | -0.021823 | -0.07887 | -0.015828 | -0.0063629 | -0.24204 | 0.03988 | 0.018182 | 0.004679 | 0.056029 | -0.0098132 | -0.017266 | 0.010564 | -0.049614 | 0.088755 | 0.050727 | 0.23354 | -0.00811 | 0.042256 | 0.064461 | -0.065509 | -0.016219 | 0.12359 | -0.13876 | -0.18246 | 0.074287 | -122.6377 | 0.065131 | 0.032783 | -0.041504 | -122.6757 | -122.4929 | -0.10007 | -122.7427 | 0.12465 | 0.016888 | 0.11695 | -122.6028 | -122.8652 | 0.17115 | 0.13312 | 0.31593 | 0.092961 | -122.7345 | 0.066178 | 0.20599 | -0.056368 | 0.14686 | -122.9089
3844.875 | 122.7814 | -0.09613 | 122.7631 | 1.4211e-13 | -0.052382 | -0.021609 | -0.07887 | -0.015614 | -0.0061493 | -0.24204 | 0.039666 | 0.01861 | 0.0048926 | 0.056029 | -0.0098132 | -0.026423 | -0.003172 | -0.045036 | 0.079598 | 0.050727 | 0.2198 | 0.005627 | 0.042256 | 0.073618 | -0.070087 | -0.020797 | 0.11901 | -0.13419 | -0.17788 | 0.10176 | -122.6835 | 0.069707 | 0.051094 | -0.050663 | -122.7123 | -122.5433 | -0.081755 | -122.7839 | 0.13839 | 0.026043 | 0.1078 | -122.644 | -122.8972 | 0.17573 | 0.14686 | 0.31593 | 0.092958 | -122.7574 | 0.075333 | 0.21514 | -0.038056 | 0.16975 | -122.9409
3846.6406 | 122.8912 | -0.07782 | 122.7402 | 1.4211e-13 | -0.052382 | -0.022037 | -0.07887 | -0.015614 | -0.0061493 | -0.24204 | 0.03988 | 0.018182 | 0.0042516 | 0.056029 | -0.010027 | -0.017266 | 0.010564 | -0.045036 | 0.079598 | 0.041569 | 0.22896 | -0.081373 | 0.046835 | 0.073618 | -0.06093 | -0.020797 | 0.12359 | -0.13419 | -0.17331 | -0.003553 | -122.6606 | 0.060554 | 0.032784 | 0.036337 | -122.6986 | -122.5112 | -0.095486 | -122.761 | 0.12466 | 0.01689 | 0.11238 | -122.6166 | -122.8744 | 0.15742 | 0.11939 | 0.30678 | 0.088384 | -122.8215 | 0.057023 | 0.20141 | -0.056366 | 0.15144 | -122.9135
3848.3906 | 122.9095 | -0.068665 | 122.7493 | 1.4211e-13 | -0.052382 | -0.02225 | -0.078657 | -0.015614 | -0.0057219 | -0.24204 | 0.03988 | 0.017969 | 0.0042516 | 0.056029 | -0.0098132 | -0.012688 | 0.015142 | -0.045036 | 0.079598 | 0.03699 | 0.22438 | 0.010206 | 0.042256 | 0.06904 | -0.056351 | -0.01164 | 0.11901 | -0.13876 | -0.17788 | 0.078871 | -122.6697 | 0.055977 | 0.023629 | -0.055242 | -122.7123 | -122.5249 | -0.10922 | -122.761 | 0.11092 | 0.012314 | 0.12153 | -122.6303 | -122.8881 | 0.14826 | 0.10565 | 0.29305 | 0.083807 | -122.7391 | 0.057025 | 0.18768 | -0.0701 | 0.13771 | -122.9272
3850.0938 | 122.8455 | -0.013733 | 122.8867 | 1.4211e-13 | -0.052382 | -0.021823 | -0.07887 | -0.015828 | -0.0061493 | -0.22678 | 0.03988 | 0.018396 | 0.0044652 | 0.056029 | -0.0098132 | -0.021844 | 0.010564 | -0.035879 | 0.084176 | 0.004938 | 0.22896 | -0.076794 | 0.042256 | 0.073618 | -0.06093 | -0.016219 | 0.12359 | -0.12961 | -0.18246 | -0.063061 | -122.8025 | -0.008111 | -0.022146 | 0.040915 | -122.8817 | -122.6577 | -0.16873 | -122.9029 | 0.055989 | -0.047197 | 0.12153 | -122.7631 | -123.0163 | 0.097909 | 0.018671 | 0.24269 | 0.024297 | -122.9635 | -0.002486 | 0.13733 | -0.11587 | 0.087351 | -123.0691
3851.8594 | 122.7676 | -0.10986 | 122.7951 | 1.4211e-13 | -0.052382 | -0.022037 | -0.07887 | -0.015828 | -0.0057219 | -0.24204 | 0.03988 | 0.018182 | 0.0044652 | 0.056029 | -0.01024 | -0.03558 | 0.005985 | -0.054192 | 0.088755 | 0.018675 | 0.2198 | -0.09511 | 0.037677 | 0.073618 | -0.074666 | -0.025376 | 0.10986 | -0.12961 | -0.18704 | 0.014753 | -122.7064 | 0.074283 | 0.055671 | 0.040918 | -122.7764 | -122.5753 | -0.07718 | -122.8205 | 0.14754 | 0.035197 | 0.11238 | -122.6852 | -122.9247 | 0.19862 | 0.12854 | 0.32966 | 0.11585 | -122.8902 | 0.084487 | 0.21972 | -0.019744 | 0.18348 | -122.9821
3853.5625 | 122.9279 | -0.086975 | 122.7539 | 1.4211e-13 | -0.052168 | -0.022037 | -0.07887 | -0.016042 | -0.0065765 | -0.24967 | 0.039666 | 0.018823 | 0.004038 | 0.055816 | -0.010454 | -0.021844 | 0.005985 | -0.049614 | 0.084176 | 0.059885 | 0.23354 | -0.10885 | 0.042256 | 0.064461 | -0.065509 | -0.01164 | 0.11901 | -0.13876 | -0.16415 | -0.021872 | -122.6697 | 0.065131 | 0.037361 | 0.059233 | -122.694 | -122.5204 | -0.077174 | -122.7655 | 0.12923 | 0.021466 | 0.09864 | -122.6349 | -122.8927 | 0.17115 | 0.14686 | 0.32051 | 0.09296 | -122.8628 | 0.075335 | 0.20599 | -0.05179 | 0.15144 | -122.9181
3855.3438 | 122.9141 | -0.073242 | 122.7539 | 1.4211e-13 | -0.052596 | -0.022037 | -0.079084 | -0.015828 | -0.0061493 | -0.22678 | 0.039666 | 0.018396 | 0.004679 | 0.056243 | -0.0095994 | -0.026423 | 0.005985 | -0.045036 | 0.084176 | 0.050727 | 0.22438 | 0.014784 | 0.042256 | 0.073618 | -0.065509 | -0.01164 | 0.11901 | -0.11129 | -0.17788 | 0.088026 | -122.6697 | 0.046819 | 0.028206 | -0.05982 | -122.7032 | -122.5295 | -0.10464 | -122.7655 | 0.1155 | 0.007733 | 0.11238 | -122.6349 | -122.8652 | 0.15742 | 0.12397 | 0.29762 | 0.079227 | -122.7391 | 0.061602 | 0.19226 | -0.038051 | 0.14686 | -122.9318
3857.1094 | 122.8729 | -0.064087 | 122.7539 | 1.4211e-13 | -0.052382 | -0.021823 | -0.078657 | -0.016042 | -0.0061493 | -0.23441 | 0.040093 | 0.018396 | 0.0042516 | 0.056029 | -0.0098132 | -0.021844 | 0.005985 | -0.049614 | 0.084176 | 0.046148 | 0.22896 | 0.0331 | 0.046835 | 0.064461 | -0.06093 | -0.01164 | 0.12359 | -0.13419 | -0.16873 | 0.097187 | -122.6697 | 0.042243 | 0.014473 | -0.082714 | -122.7078 | -122.5249 | -0.10464 | -122.7655 | 0.11092 | 0.003157 | 0.1078 | -122.6303 | -122.8881 | 0.14826 | 0.11023 | 0.29305 | 0.070072 | -122.7208 | 0.052447 | 0.18768 | -0.070099 | 0.12855 | -122.9226
3858.8125 | 122.8088 | -0.10529 | 122.7859 | 1.4211e-13 | -0.052596 | -0.02225 | -0.078657 | -0.015828 | -0.0061493 | -0.24204 | 0.039666 | 0.018182 | 0.0044652 | 0.056029 | -0.010027 | -0.017266 | 0.005985 | -0.049614 | 0.084176 | 0.046148 | 0.23354 | 0.07431 | 0.042256 | 0.06904 | -0.06093 | -0.01164 | 0.11444 | -0.13876 | -0.18704 | 0.1796 | -122.7018 | 0.08802 | 0.055672 | -0.12392 | -122.7398 | -122.5524 | -0.081757 | -122.7976 | 0.14754 | 0.044356 | 0.12611 | -122.6715 | -122.9247 | 0.18946 | 0.15143 | 0.33882 | 0.11127 | -122.7116 | 0.093646 | 0.21972 | -0.033479 | 0.17433 | -122.973
3860.5781 | 122.9233 | -0.086975 | 122.7493 | 1.4211e-13 | -0.052596 | -0.022037 | -0.078657 | -0.015828 | -0.0061493 | -0.23441 | 0.03988 | 0.018182 | 0.004038 | 0.056243 | -0.01024 | -0.021844 | 0.005985 | -0.049614 | 0.079598 | 0.041569 | 0.22438 | 0.078889 | 0.042256 | 0.059882 | -0.065509 | -0.016219 | 0.11901 | -0.14334 | -0.18246 | 0.16586 | -122.6697 | 0.065131 | 0.037361 | -0.1285 | -122.7078 | -122.5249 | -0.095489 | -122.7655 | 0.12923 | 0.021466 | 0.11695 | -122.6303 | -122.8927 | 0.16657 | 0.12854 | 0.31136 | 0.09296 | -122.6704 | 0.070756 | 0.20599 | -0.056368 | 0.14686 | -122.9318
3862.3438 | 122.7997 | -0.10986 | 122.7814 | 1.4211e-13 | -0.052382 | -0.022037 | -0.079084 | -0.015401 | -0.0063629 | -0.24204 | 0.03988 | 0.018182 | 0.0042516 | 0.056243 | -0.0098132 | -0.021844 | 0.005985 | -0.049614 | 0.079598 | 0.055306 | 0.22896 | 0.060574 | 0.037677 | 0.06904 | -0.065509 | -0.01164 | 0.10986 | -0.13419 | -0.18246 | 0.17044 | -122.7018 | 0.088019 | 0.060249 | -0.11019 | -122.7261 | -122.5524 | -0.072601 | -122.793 | 0.14754 | 0.044354 | 0.11695 | -122.6715 | -122.9156 | 0.18946 | 0.16517 | 0.33882 | 0.11585 | -122.7208 | 0.098223 | 0.21972 | -0.024323 | 0.1789 | -122.9638
3864.1094 | 122.8638 | -0.07782 | 122.7539 | 1.4211e-13 | -0.052809 | -0.022037 | -0.078657 | -0.016042 | -0.0061493 | -0.24204 | 0.040093 | 0.018182 | 0.0044652 | 0.056029 | -0.010027 | -0.021844 | 0.001407 | -0.040457 | 0.088755 | 0.055306 | 0.21522 | -0.021847 | 0.046835 | 0.064461 | -0.06093 | -0.016219 | 0.11901 | -0.12961 | -0.18246 | 0.055973 | -122.6652 | 0.055976 | 0.037363 | -0.01861 | -122.6986 | -122.5387 | -0.10464 | -122.7701 | 0.12466 | 0.01689 | 0.12153 | -122.6349 | -122.8835 | 0.16658 | 0.13313 | 0.29304 | 0.079227 | -122.7758 | 0.061601 | 0.19683 | -0.051787 | 0.14228 | -122.9364
3865.875 | 122.8317 | -0.14191 | 122.7997 | 1.4211e-13 | -0.052382 | -0.022037 | -0.07887 | -0.015614 | -0.0065765 | -0.24204 | 0.03988 | 0.017969 | 0.004038 | 0.056243 | -0.010027 | -0.021844 | 0.001407 | -0.045036 | 0.084176 | 0.050727 | 0.22896 | 0.042258 | 0.042256 | 0.073618 | -0.06093 | -0.01164 | 0.12359 | -0.11129 | -0.18704 | 0.18416 | -122.7155 | 0.12006 | 0.096871 | -0.087294 | -122.749 | -122.5707 | -0.045136 | -122.8113 | 0.18416 | 0.080977 | 0.12611 | -122.6761 | -122.911 | 0.22608 | 0.19263 | 0.37087 | 0.14331 | -122.7574 | 0.13027 | 0.2655 | 0.030614 | 0.21553 | -122.9867
3867.6406 | 122.8226 | -0.11902 | 122.7722 | 1.4211e-13 | -0.052596 | -0.02225 | -0.078443 | -0.015828 | -0.0061493 | -0.24204 | 0.039666 | 0.018182 | 0.0042516 | 0.056029 | -0.010454 | -0.017266 | 0.005985 | -0.045036 | 0.07502 | 0.050727 | 0.22438 | 0.051416 | 0.046835 | 0.064461 | -0.065509 | -0.016219 | 0.12359 | -0.13876 | -0.17788 | 0.17044 | -122.6972 | 0.10175 | 0.073983 | -0.096452 | -122.7215 | -122.5478 | -0.058866 | -122.7884 | 0.16585 | 0.05351 | 0.11238 | -122.6486 | -122.911 | 0.19404 | 0.16975 | 0.3434 | 0.125 | -122.7208 | 0.1028 | 0.24261 | -0.019746 | 0.18348 | -122.9501
3869.3281 | 122.9187 | -0.068665 | 122.731 | 1.4211e-13 | -0.052809 | -0.022464 | -0.078657 | -0.016255 | -0.0063629 | -0.24967 | 0.039453 | 0.018182 | 0.0044652 | 0.056457 | -0.01024 | -0.012688 | 0.010564 | -0.045036 | 0.084176 | 0.041569 | 0.23354 | -0.012689 | 0.051413 | 0.06904 | -0.070087 | -0.016219 | 0.12817 | -0.10671 | -0.18704 | 0.055976 | -122.6468 | 0.055977 | 0.023629 | -0.032347 | -122.6894 | -122.4975 | -0.11838 | -122.7472 | 0.12008 | -0.001422 | 0.11696 | -122.6028 | -122.8377 | 0.15284 | 0.11023 | 0.3022 | 0.079229 | -122.7437 | 0.052446 | 0.19684 | -0.038049 | 0.13771 | -122.9181
3871.1094 | 122.8546 | -0.091553 | 122.7493 | 1.4211e-13 | -0.052596 | -0.02225 | -0.07887 | -0.016255 | -0.0065765 | -0.24967 | 0.039666 | 0.018182 | 0.0044652 | 0.056243 | -0.01024 | -0.026423 | 0.001407 | -0.040457 | 0.088755 | 0.050727 | 0.22438 | 0.046837 | 0.046835 | 0.06904 | -0.070087 | -0.016219 | 0.12359 | -0.13419 | -0.17788 | 0.13839 | -122.6606 | 0.06513 | 0.051096 | -0.087294 | -122.6986 | -122.5249 | -0.086332 | -122.7655 | 0.13839 | 0.021466 | 0.1078 | -122.6257 | -122.8835 | 0.18031 | 0.14228 | 0.31593 | 0.09296 | -122.7025 | 0.075334 | 0.21515 | -0.042633 | 0.16059 | -122.9272
3872.8125 | 122.9416 | -0.086975 | 122.7493 | 1.4211e-13 | -0.052809 | -0.022037 | -0.078657 | -0.015828 | -0.0063629 | -0.24204 | 0.039239 | 0.018396 | 0.0042516 | 0.056457 | -0.01024 | -0.012688 | 0.001407 | -0.049614 | 0.079598 | 0.046148 | 0.22896 | 0.051416 | 0.046835 | 0.073618 | -0.065509 | -0.007062 | 0.11901 | -0.13876 | -0.18246 | 0.13839 | -122.6697 | 0.074287 | 0.037361 | -0.10103 | -122.7032 | -122.5204 | -0.095489 | -122.7564 | 0.13381 | 0.021466 | 0.11695 | -122.6303 | -122.8881 | 0.16657 | 0.13312 | 0.31593 | 0.088382 | -122.6979 | 0.079913 | 0.20599 | -0.05179 | 0.16059 | -122.9318
3874.5781 | 122.8821 | -0.09613 | 122.7814 | 1.4211e-13 | -0.052809 | -0.022037 | -0.07887 | -0.015828 | -0.0065765 | -0.23441 | 0.039666 | 0.017969 | 0.0042516 | 0.056243 | -0.010027 | -0.017266 | 0.010564 | -0.040457 | 0.088755 | 0.050727 | 0.22438 | 0.046837 | 0.046835 | 0.06904 | -0.06093 | -0.01164 | 0.11901 | -0.13876 | -0.18246 | 0.14297 | -122.6926 | 0.078864 | 0.055673 | -0.087294 | -122.7306 | -122.557 | -0.086334 | -122.793 | 0.14297 | 0.0352 | 0.12153 | -122.6624 | -122.9201 | 0.18488 | 0.14686 | 0.32051 | 0.10669 | -122.7345 | 0.08449 | 0.21514 | -0.042635 | 0.16517 | -122.9638
3876.2812 | 122.818 | -0.091553 | 122.7997 | 1.4211e-13 | -0.052596 | -0.022037 | -0.079084 | -0.015614 | -0.0063629 | -0.24967 | 0.039453 | 0.01861 | 0.0042516 | 0.056243 | -0.010027 | -0.012688 | 0.005985 | -0.035879 | 0.088755 | 0.055306 | 0.2198 | 0.055995 | 0.046835 | 0.073618 | -0.070087 | -0.01164 | 0.12359 | -0.13876 | -0.17788 | 0.14755 | -122.7109 | 0.078865 | 0.055674 | -0.091874 | -122.7444 | -122.5799 | -0.086332 | -122.8113 | 0.13839 | 0.021466 | 0.1078 | -122.6761 | -122.9384 | 0.18031 | 0.14686 | 0.31135 | 0.097538 | -122.7437 | 0.079913 | 0.21515 | -0.047212 | 0.16517 | -122.9776
3878.0469 | 122.9324 | -0.082397 | 122.7722 | 1.4211e-13 | -0.052596 | -0.022464 | -0.078657 | -0.016042 | -0.0061493 | -0.2573 | 0.039666 | 0.018182 | 0.0044652 | 0.05667 | -0.01024 | -0.012688 | 0.005985 | -0.040457 | 0.084176 | 0.050727 | 0.22438 | 0.0331 | 0.042256 | 0.073618 | -0.070087 | -0.020797 | 0.11444 | -0.13419 | -0.17788 | 0.1155 | -122.688 | 0.069709 | 0.04194 | -0.073557 | -122.7215 | -122.5478 | -0.095488 | -122.793 | 0.12465 | 0.01231 | 0.1078 | -122.6578 | -122.9064 | 0.16657 | 0.13312 | 0.30678 | 0.088382 | -122.7391 | 0.0616 | 0.19683 | -0.051789 | 0.15602 | -122.9501
3879.7969 | 122.9553 | -0.07782 | 122.7448 | 1.4211e-13 | -0.053023 | -0.02225 | -0.078657 | -0.016042 | -0.0063629 | -0.24967 | 0.039453 | 0.017969 | 0.0042516 | 0.056457 | -0.01024 | -0.021844 | 0.001407 | -0.040457 | 0.079598 | 0.046148 | 0.22896 | 0.10178 | 0.046835 | 0.064461 | -0.056351 | -0.016219 | 0.11901 | -0.13876 | -0.18246 | 0.1796 | -122.6652 | 0.055976 | 0.037363 | -0.14224 | -122.6986 | -122.5158 | -0.10464 | -122.761 | 0.12466 | 0.021469 | 0.12611 | -122.6257 | -122.8835 | 0.15742 | 0.12397 | 0.30678 | 0.079227 | -122.643 | 0.061601 | 0.19683 | -0.060945 | 0.14228 | -122.9272
3881.5625 | 122.8271 | -0.10071 | 122.7951 | 1.4211e-13 | -0.053023 | -0.022037 | -0.07887 | -0.016042 | -0.0063629 | -0.24204 | 0.039666 | 0.01861 | 0.0042516 | 0.05667 | -0.010027 | -0.012688 | 0.001407 | -0.040457 | 0.079598 | 0.050727 | 0.22896 | 0.088047 | 0.046835 | 0.073618 | -0.065509 | -0.01164 | 0.11901 | -0.12961 | -0.17788 | 0.18876 | -122.7155 | 0.08802 | 0.060251 | -0.1285 | -122.7444 | -122.5661 | -0.077177 | -122.8067 | 0.14754 | 0.035199 | 0.11238 | -122.6761 | -122.9247 | 0.18031 | 0.15144 | 0.32967 | 0.10212 | -122.7071 | 0.089068 | 0.21972 | -0.028899 | 0.17433 | -122.973
3883.3281 | 122.8729 | -0.091553 | 122.7768 | 1.4211e-13 | -0.052809 | -0.022037 | -0.078657 | -0.015614 | -0.0059355 | -0.24967 | 0.039666 | 0.017969 | 0.004038 | 0.056029 | -0.010027 | -0.017266 | 0.010564 | -0.035879 | 0.084176 | 0.050727 | 0.22438 | 0.028521 | 0.042256 | 0.06904 | -0.06093 | -0.016219 | 0.12359 | -0.13419 | -0.18246 | 0.12007 | -122.6926 | 0.074287 | 0.055674 | -0.0644 | -122.7261 | -122.5524 | -0.090911 | -122.793 | 0.13381 | 0.030623 | 0.12153 | -122.6532 | -122.911 | 0.17573 | 0.14228 | 0.31593 | 0.10212 | -122.7483 | 0.075334 | 0.21515 | -0.042633 | 0.16059 | -122.9593
3885.0938 | 122.8775 | -0.082397 | 122.7859 | 1.4211e-13 | -0.052596 | -0.02225 | -0.07887 | -0.016255 | -0.0063629 | -0.24967 | 0.039666 | 0.017969 | 0.0042516 | 0.056457 | -0.01024 | -0.021844 | 0.001407 | -0.035879 | 0.084176 | 0.046148 | 0.22896 | -0.017268 | 0.051413 | 0.073618 | -0.070087 | -0.01164 | 0.12359 | -0.12503 | -0.18246 | 0.065129 | -122.7018 | 0.060553 | 0.046518 | -0.018611 | -122.7398 | -122.557 | -0.10007 | -122.7976 | 0.13381 | 0.01231 | 0.11238 | -122.6624 | -122.911 | 0.16657 | 0.12854 | 0.31136 | 0.083804 | -122.8032 | 0.070757 | 0.20599 | -0.042632 | 0.15602 | -122.9684
3886.7812 | 122.818 | -0.1236 | 122.7768 | 1.4211e-13 | -0.052596 | -0.02225 | -0.079084 | -0.016042 | -0.0063629 | -0.2573 | 0.03988 | 0.018396 | 0.0042516 | 0.056457 | -0.01024 | -0.026423 | 0.010564 | -0.040457 | 0.084176 | 0.046148 | 0.22896 | 0.010206 | 0.042256 | 0.064461 | -0.065509 | -0.01164 | 0.12359 | -0.13876 | -0.17331 | 0.1338 | -122.6926 | 0.097173 | 0.083139 | -0.050663 | -122.7306 | -122.5478 | -0.04971 | -122.7884 | 0.16585 | 0.058087 | 0.1078 | -122.6532 | -122.9156 | 0.20777 | 0.16974 | 0.35256 | 0.13416 | -122.7666 | 0.11196 | 0.24719 | -0.015169 | 0.18806 | -122.9501
3888.5312 | 122.8546 | -0.11444 | 122.8043 | 1.4211e-13 | -0.053023 | -0.022037 | -0.079298 | -0.015828 | -0.0063629 | -0.24967 | 0.03988 | 0.018182 | 0.0044652 | 0.05667 | -0.010027 | -0.021844 | 0.001407 | -0.045036 | 0.079598 | 0.055306 | 0.22896 | 0.010206 | 0.051413 | 0.073618 | -0.065509 | -0.007062 | 0.11901 | -0.14334 | -0.17788 | 0.12465 | -122.7247 | 0.092597 | 0.069405 | -0.055242 | -122.749 | -122.5753 | -0.063444 | -122.8113 | 0.16585 | 0.048932 | 0.11238 | -122.6852 | -122.9476 | 0.19404 | 0.16975 | 0.3434 | 0.11585 | -122.7941 | 0.10738 | 0.23345 | -0.028902 | 0.18806 | -122.9821
3890.2344 | 122.8134 | -0.10529 | 122.8134 | 1.4211e-13 | -0.053237 | -0.022037 | -0.079084 | -0.015828 | -0.0061493 | -0.24967 | 0.03988 | 0.017541 | 0.0044652 | 0.056029 | -0.01024 | -0.026423 | 0.001407 | -0.045036 | 0.07502 | 0.050727 | 0.2198 | 0.055995 | 0.046835 | 0.073618 | -0.070087 | -0.01164 | 0.12359 | -0.14334 | -0.17788 | 0.16128 | -122.7384 | 0.078863 | 0.06025 | -0.10103 | -122.7627 | -122.5936 | -0.072599 | -122.8251 | 0.15212 | 0.035199 | 0.1078 | -122.6898 | -122.9568 | 0.18031 | 0.15601 | 0.32509 | 0.10669 | -122.7574 | 0.093646 | 0.22888 | -0.038057 | 0.1789 | -122.9913
3891.9844 | 122.8134 | -0.091553 | 122.8043 | 1.4211e-13 | -0.053237 | -0.022464 | -0.07887 | -0.016042 | -0.0065765 | -0.24967 | 0.039453 | 0.018396 | 0.004038 | 0.056457 | -0.0098132 | -0.026423 | 0.010564 | -0.045036 | 0.079598 | 0.055306 | 0.21522 | 0.0331 | 0.046835 | 0.06904 | -0.056351 | -0.01164 | 0.12359 | -0.12503 | -0.18704 | 0.12465 | -122.7247 | 0.06513 | 0.046517 | -0.078136 | -122.749 | -122.589 | -0.09549 | -122.8159 | 0.13839 | 0.035202 | 0.13069 | -122.6807 | -122.9293 | 0.17115 | 0.14686 | 0.30678 | 0.10212 | -122.7712 | 0.079913 | 0.21515 | -0.033476 | 0.16059 | -122.9913
3893.75 | 122.9233 | -0.07782 | 122.7356 | 1.4211e-13 | -0.052809 | -0.022037 | -0.078657 | -0.015614 | -0.0065765 | -0.24204 | 0.039666 | 0.018396 | 0.004038 | 0.056243 | -0.010027 | -0.017266 | 0.010564 | -0.040457 | 0.084176 | 0.055306 | 0.22896 | 0.07431 | 0.046835 | 0.06904 | -0.065509 | -0.01164 | 0.11901 | -0.13876 | -0.18704 | 0.15213 | -122.6514 | 0.060554 | 0.037363 | -0.11477 | -122.6803 | -122.5066 | -0.10922 | -122.7472 | 0.12466 | 0.012311 | 0.12153 | -122.6166 | -122.8744 | 0.162 | 0.13313 | 0.30678 | 0.088384 | -122.6613 | 0.06618 | 0.19683 | -0.060945 | 0.14686 | -122.9226
3895.5156 | 122.8592 | -0.11444 | 122.8317 | 1.4211e-13 | -0.052596 | -0.02225 | -0.078657 | -0.016042 | -0.0065765 | -0.24204 | 0.039666 | 0.018182 | 0.004038 | 0.05667 | -0.01024 | -0.021844 | 0.005985 | -0.045036 | 0.079598 | 0.050727 | 0.22896 | 0.046837 | 0.051413 | 0.06904 | -0.065509 | -0.01164 | 0.12359 | -0.13876 | -0.18246 | 0.16128 | -122.7521 | 0.092597 | 0.069405 | -0.091873 | -122.781 | -122.6028 | -0.068023 | -122.8434 | 0.16585 | 0.048932 | 0.11695 | -122.7081 | -122.9705 | 0.19404 | 0.16517 | 0.3434 | 0.12043 | -122.7849 | 0.1028 | 0.23803 | -0.024324 | 0.18348 | -123.0142

## Thermal Data
Fire Time | B Position - Middle | D Position - 3' | D Position - Middle | D Position - 7'
-0.0583 | 11.5619 | 11.8028 | 11.4754 | 11.3328
0.9417 | 11.5572 | 11.7919 | 11.4776 | 11.3396
1.9417 | 11.5493 | 11.791 | 11.4738 | 11.3432
2.9417 | 11.5643 | 11.7938 | 11.473 | 11.3362
3.9417 | 11.5625 | 11.8975 | 11.6364 | 11.3356
4.9417 | 11.5861 | 11.8908 | 11.7283 | 11.3602
5.9417 | 11.5821 | 11.9285 | 12.1803 | 11.4919
6.9417 | 11.5964 | 12.4525 | 13.1849 | 11.9841
7.9417 | 11.6636 | 13.4049 | 14.9767 | 12.8124
8.9417 | 12.0506 | 15.2439 | 17.3875 | 13.8912
9.9417 | 12.7602 | 16.837 | 20.8801 | 15.0979
10.9417 | 14.019 | 18.7787 | 22.8732 | 15.9998
11.9417 | 14.8174 | 20.9919 | 25.639 | 17.595
12.9417 | 16.2291 | 23.1498 | 27.4367 | 18.9792
13.9417 | 17.593 | 24.7058 | 29.2454 | 20.1379
14.9417 | 18.8965 | 27.4029 | 32.1325 | 21.894
15.9417 | 20.493 | 29.2854 | 33.9997 | 24.117
16.9417 | 21.8667 | 30.9587 | 35.3315 | 26.057
17.9417 | 24.054 | 35.309 | 40.8634 | 28.8808
18.9417 | 25.0599 | 35.879 | 40.6854 | 30.2624
19.9417 | 27.9298 | 38.8776 | 43.447 | 31.9071
20.9417 | 31.637 | 46.9869 | 53.1825 | 33.6822
21.9417 | 32.8858 | 47.237 | 52.9027 | 36.7446
22.9417 | 33.4431 | 50.4234 | 55.4296 | 39.4767
23.9417 | 32.7347 | 47.8403 | 53.6915 | 41.4244
24.9417 | 36.7014 | 56.5425 | 65.6909 | 43.5684
25.9417 | 37.5564 | 58.5784 | 70.097 | 45.9187
26.9417 | 38.6308 | 60.9643 | 74.5392 | 47.9044
27.9417 | 39.688 | 63.3436 | 78.1845 | 52.1024
28.9417 | 41.6967 | 65.6166 | 80.6038 | 54.3732
29.9417 | 42.675 | 69.1985 | 85.0907 | 57.3204
30.9417 | 44.2965 | 71.9391 | 88.1583 | 59.3292
31.9417 | 45.5452 | 74.0425 | 90.6853 | 62.6812
32.9417 | 47.6999 | 75.4303 | 88.752 | 64.694
33.9417 | 49.4848 | 78.337 | 92.022 | 67.8388
34.9417 | 51.239 | 74.3246 | 85.2271 | 71.522
35.9417 | 53.424 | 75.8322 | 87.4335 | 73.5374
36.9417 | 55.306 | 76.5804 | 88.4006 | 76.2117
37.9417 | 56.3246 | 77.5829 | 89.5664 | 78.4931
38.9417 | 57.4937 | 79.9358 | 91.5744 | 80.0712
39.9417 | 56.7033 | 77.8879 | 88.9974 | 82.6658
40.9417 | 58.7386 | 80.6469 | 92.4333 | 84.1058
41.9417 | 62.9134 | 85.6652 | 96.9393 | 86.4991
42.9417 | 64.7413 | 87.7813 | 97.8098 | 88.6567
43.9417 | 66.4752 | 90.1641 | 101.4653 | 90.344
44.9417 | 66.253 | 90.1499 | 101.1627 | 93.4065
45.9417 | 67.742 | 93.1827 | 105.2474 | 95.5381
46.9417 | 68.5944 | 94.7943 | 107.0171 | 98.8728
47.9417 | 68.7961 | 94.4418 | 106.5222 | 100.2907
48.9417 | 70.7653 | 97.7341 | 109.8277 | 101.7942
49.9417 | 73.3124 | 99.3601 | 111.2313 | 103.5861
50.9417 | 74.5635 | 104.6541 | 118.1557 | 106.7343
51.9417 | 75.0255 | 105.1404 | 117.6325 | 109.1248
52.9417 | 75.5395 | 103.0872 | 114.8231 | 111.98
53.9417 | 76.2905 | 106.8334 | 119.0376 | 116.0427
54.9417 | 78.5767 | 112.1765 | 124.6833 | 118.6933
55.9417 | 79.4191 | 113.4263 | 126.4759 | 120.9568
56.9417 | 80.7875 | 114.6013 | 128.013 | 121.5866
57.9417 | 81.378 | 115.6314 | 129.2743 | 121.9387
58.9417 | 81.9163 | 116.1524 | 130.1634 | 123.5765
59.9417 | 82.9586 | 116.0033 | 129.3784 | 125.7787
60.9417 | 85.1504 | 118.2123 | 132.2417 | 127.6253
61.9417 | 85.5758 | 117.4836 | 132.0158 | 128.7739
62.9417 | 86.6657 | 118.3356 | 133.4686 | 130.5474
63.9417 | 87.6761 | 120.5679 | 136.011 | 131.3926
64.9417 | 88.5306 | 121.5353 | 136.8832 | 131.8166
65.9417 | 89.2559 | 123.2034 | 140.2308 | 132.5447
66.9417 | 89.9864 | 119.4941 | 135.6998 | 133.2027
67.9417 | 91.0911 | 123.1792 | 141.5717 | 133.9393
68.9417 | 91.3392 | 122.2046 | 140.4703 | 135.0433
69.9417 | 91.5518 | 124.0322 | 147.9267 | 135.4114
70.9417 | 92.2852 | 124.5521 | 148.2678 | 136.33
71.9417 | 92.9748 | 124.6656 | 148.9727 | 137.7874
72.9417 | 94.0329 | 124.995 | 147.1024 | 137.6061
73.9417 | 95.5673 | 125.3464 | 150.5391 | 138.934
74.9417 | 96.316 | 125.2868 | 151.8977 | 140.6171
75.9417 | 96.894 | 125.61 | 151.4981 | 140.8418
76.9417 | 98.4116 | 126.3635 | 151.8586 | 142.1607
77.9417 | 98.927 | 127.038 | 152.12 | 143.1109
78.9417 | 99.4571 | 127.4111 | 152.7169 | 145.0466
79.9417 | 99.8077 | 129.2468 | 155.1826 | 148.3839
80.9417 | 100.6363 | 130.2911 | 156.731 | 150.9433
81.9417 | 101.6434 | 130.5121 | 157.6015 | 151.4888
82.9417 | 101.7404 | 130.434 | 158.49 | 151.0678
83.9417 | 102.6884 | 130.5157 | 159.6408 | 153.1839
84.9417 | 103.416 | 130.5046 | 159.5689 | 152.8999
85.9417 | 103.8884 | 130.4638 | 160.698 | 154.0223
86.9417 | 104.4877 | 130.6696 | 161.1953 | 154.7669
87.9417 | 104.8456 | 131.3146 | 161.7792 | 154.5656
88.9417 | 105.6287 | 131.7138 | 162.4359 | 154.9308
89.9417 | 106.3145 | 132.289 | 162.6538 | 155.8489
90.9417 | 106.8242 | 132.9168 | 162.006 | 156.4614
91.9417 | 107.9164 | 132.8007 | 163.1921 | 156.5277
92.9417 | 108.6395 | 132.7804 | 163.058 | 157.8595
93.9417 | 109.1897 | 134.429 | 165.038 | 157.9274
94.9417 | 109.2328 | 135.1866 | 167.08 | 158.8781
95.9417 | 109.2004 | 137.081 | 167.9648 | 159.0682
96.9417 | 109.415 | 137.6181 | 167.7209 | 160.125
97.9417 | 110.4075 | 138.567 | 168.452 | 161.486
98.9417 | 111.5042 | 139.5016 | 169.1538 | 161.6847
99.9417 | 112.5081 | 141.4981 | 170.0998 | 160.9945
100.9417 | 113.3744 | 142.1185 | 170.7357 | 161.8765
101.9417 | 114.1465 | 142.544 | 170.9054 | 161.9735
102.9417 | 113.8326 | 143.6879 | 171.2288 | 162.0901
103.9417 | 114.2404 | 143.6283 | 172.044 | 163.8446
104.9417 | 115.0151 | 143.9977 | 172.3453 | 165.4336
105.9417 | 116.5826 | 145.4973 | 172.4705 | 165.2332
106.9417 | 117.0569 | 146.4515 | 171.5814 | 164.4338
107.9417 | 117.4643 | 146.1667 | 171.3597 | 163.7681
108.9417 | 118.6623 | 145.8388 | 172.3141 | 165.8408
109.9417 | 119.8892 | 147.6189 | 173.7399 | 167.1337
110.9417 | 120.3914 | 147.901 | 174.2996 | 168.0638
111.9417 | 120.1374 | 149.5473 | 175.2624 | 168.51
112.9417 | 120.1718 | 149.1172 | 174.9432 | 167.5151
113.9417 | 120.0497 | 148.6593 | 174.7945 | 166.3006
114.9417 | 120.3234 | 148.8674 | 174.693 | 166.8373
115.9417 | 120.2123 | 149.5739 | 175.9843 | 169.0706
116.9417 | 120.4041 | 150.3259 | 176.9747 | 169.7537
117.9417 | 120.4356 | 149.6397 | 177.9215 | 169.4385
118.9417 | 121.1965 | 149.4065 | 177.3803 | 168.701
119.9417 | 121.2942 | 149.41 | 177.9273 | 168.1279
120.9417 | 121.5927 | 149.464 | 177.8954 | 167.8545
121.9417 | 121.6696 | 152.1613 | 179.1139 | 168.2777
122.9417 | 121.6093 | 152.307 | 179.0396 | 168.4592
123.9417 | 121.4106 | 153.5862 | 179.3011 | 169.313
124.9417 | 121.4894 | 154.2603 | 179.8754 | 170.6303
125.9417 | 122.0875 | 153.623 | 180.3675 | 170.174
126.9417 | 122.9196 | 154.0755 | 180.8799 | 171.4577
127.9417 | 123.2534 | 154.1109 | 180.1535 | 172.4216
128.9417 | 123.8664 | 154.3126 | 180.6644 | 172.7012
129.9417 | 124.411 | 154.9909 | 180.6393 | 174.2893
130.9417 | 125.304 | 155.5198 | 181.5581 | 177.2545
131.9417 | 124.9177 | 155.3517 | 181.4636 | 177.2008
132.9417 | 125.0539 | 155.5517 | 182.1144 | 177.9912
133.9417 | 125.448 | 154.3882 | 181.4286 | 177.989
134.9417 | 126.2357 | 154.0314 | 181.2224 | 178.2199
135.9417 | 126.3227 | 153.1652 | 180.7834 | 177.6379
136.9417 | 126.8333 | 153.4053 | 180.7517 | 177.5842
137.9417 | 127.1914 | 154.1048 | 180.1149 | 176.4909
138.9417 | 127.1226 | 153.8305 | 179.2384 | 175.5952
139.9417 | 127.5269 | 153.5911 | 179.2645 | 174.9716
140.9417 | 127.7171 | 153.5124 | 178.8909 | 174.9335
141.9417 | 128.0022 | 153.9911 | 178.3715 | 174.9524
142.9417 | 128.1853 | 153.7967 | 178.3254 | 175.5028
143.9417 | 128.7728 | 153.3986 | 178.5366 | 175.8855
144.9417 | 129.2593 | 152.9891 | 178.8597 | 176.2321
145.9417 | 129.2439 | 152.3531 | 178.817 | 176.7225
146.9417 | 129.3077 | 151.5737 | 178.8797 | 177.2539
147.9417 | 129.4396 | 151.0783 | 179.4902 | 176.5207
148.9417 | 129.0823 | 150.6233 | 179.5741 | 176.5991
149.9417 | 129.1515 | 150.0427 | 179.762 | 176.9945
150.9417 | 129.3264 | 151.6362 | 179.4542 | 177.1964
151.9417 | 130.0483 | 151.9101 | 178.8653 | 176.5909
152.9417 | 129.9712 | 151.566 | 178.4114 | 175.6158
153.9417 | 130.1776 | 150.9315 | 178.8568 | 175.7421
154.9573 | 130.0944 | 150.4126 | 179.2123 | 175.8096
155.9573 | 130.0598 | 150.3509 | 179.9837 | 176.2744
156.9417 | 130.9671 | 152.1468 | 181.329 | 177.4139
157.9417 | 131.4445 | 152.3926 | 181.7539 | 179.0903
158.9573 | 132.0262 | 151.846 | 182.5342 | 179.1285
159.9573 | 131.1074 | 152.4408 | 182.3576 | 178.6614
160.9573 | 131.8454 | 153.1072 | 182.6421 | 180.4834
161.9417 | 132.0178 | 152.8166 | 182.8688 | 181.5091
162.9417 | 132.2798 | 153.3604 | 182.9629 | 181.7594
163.9417 | 133.4801 | 153.7739 | 182.9384 | 181.6397
164.9417 | 134.1109 | 154.8788 | 182.8704 | 182.0409
165.9417 | 134.4529 | 155.1417 | 182.612 | 181.7078
166.9417 | 134.3815 | 155.7164 | 183.815 | 181.7737
167.9417 | 134.8464 | 157.2267 | 184.3522 | 183.1406
168.9417 | 135.6925 | 157.8743 | 184.4263 | 182.8331
169.9417 | 136.1764 | 157.4116 | 185.8178 | 184.3202
170.9417 | 136.3322 | 156.5813 | 185.8257 | 186.1713
171.9417 | 136.5974 | 156.129 | 185.7477 | 185.6222
172.9417 | 136.5616 | 155.3415 | 185.1235 | 185.3756
173.9417 | 136.6308 | 155.6815 | 184.7131 | 184.7774
174.9417 | 136.4321 | 155.1167 | 183.7559 | 184.2936
175.9417 | 136.2473 | 154.9607 | 183.1019 | 184.21
176.9417 | 136.1553 | 153.6618 | 182.4911 | 183.0752
177.9417 | 135.7311 | 154.0104 | 182.7579 | 183.0031
178.9417 | 135.6088 | 154.3202 | 183.4107 | 182.3711
179.9417 | 135.4108 | 154.2647 | 183.2482 | 182.0688
180.9417 | 135.7616 | 153.8632 | 182.675 | 181.6577
181.9417 | 135.5509 | 153.0097 | 182.17 | 181.0452
182.9417 | 135.294 | 152.4067 | 182.1001 | 181.1879
183.9417 | 135.4864 | 151.9193 | 181.7301 | 181.089
184.9417 | 135.5416 | 152.1595 | 182.6132 | 180.8635
185.9417 | 135.6551 | 152.0075 | 182.6915 | 179.8251
186.9417 | 135.5918 | 151.7481 | 182.0705 | 179.769
187.9417 | 135.8234 | 151.849 | 182.1361 | 179.899
188.9417 | 135.812 | 152.0735 | 182.1173 | 179.821
189.9417 | 135.8232 | 152.8326 | 182.1702 | 180.6917
190.9417 | 135.9248 | 152.8279 | 182.1847 | 180.1166
191.9417 | 135.771 | 152.8493 | 183.4655 | 180.5893
192.9417 | 136.1532 | 152.7956 | 183.7709 | 180.5756
193.9417 | 136.3865 | 152.4876 | 183.1899 | 180.2214
194.9417 | 136.2942 | 151.9351 | 182.4465 | 179.8324
195.9417 | 136.1827 | 151.432 | 183.6519 | 180.0713
196.9417 | 135.9978 | 151.5884 | 184.3508 | 180.7898
197.9417 | 135.5813 | 151.5089 | 184.8734 | 181.5161
198.9417 | 135.9425 | 152.3125 | 185.5504 | 182.8755
199.9417 | 136.1714 | 153.9351 | 186.6073 | 184.0719
200.9417 | 135.9948 | 154.9559 | 186.6291 | 183.2145
201.9417 | 136.2344 | 154.2374 | 185.8939 | 182.5464
202.9417 | 136.2529 | 153.586 | 185.4287 | 182.1386
203.9417 | 136.228 | 153.3457 | 186.2511 | 181.7373
204.9417 | 135.9096 | 153.8222 | 186.4666 | 181.6914
205.9417 | 135.3441 | 153.0749 | 184.8797 | 181.7351
206.9417 | 135.595 | 154.2851 | 185.0178 | 181.3462
207.9417 | 135.0602 | 155.5515 | 185.3876 | 182.0176
208.9417 | 134.9647 | 155.866 | 187.6117 | 182.3882
209.9417 | 135.1865 | 156.4572 | 187.5284 | 183.1426
210.9417 | 135.3902 | 156.5278 | 186.6088 | 182.6467
211.9417 | 135.6645 | 156.261 | 186.5635 | 182.2744
212.9417 | 135.5073 | 155.9351 | 186.2679 | 181.3329
213.9417 | 135.854 | 156.002 | 185.8115 | 180.8305
214.9417 | 135.9664 | 155.7574 | 186.1428 | 180.5396
215.9417 | 136.0828 | 155.2491 | 185.4092 | 179.8499
216.9417 | 135.9551 | 155.0172 | 184.786 | 179.0659
217.9417 | 135.5387 | 154.5279 | 183.7735 | 178.4883
218.9417 | 135.8865 | 154.2752 | 183.3913 | 177.9809
219.9417 | 135.9853 | 154.712 | 183.0127 | 177.4787
220.9417 | 135.9159 | 154.9064 | 183.1664 | 177.6903
221.9417 | 135.8063 | 154.5053 | 183.1467 | 176.8876
222.9417 | 135.7651 | 155.2409 | 183.575 | 177.3904
223.9417 | 135.825 | 155.3344 | 183.7657 | 177.5008
224.9417 | 136.2422 | 155.4889 | 184.0111 | 178.0317
225.9417 | 135.572 | 155.0686 | 183.1901 | 178.0887
226.9417 | 135.7534 | 154.2088 | 183.187 | 178.1374
227.9417 | 136.6335 | 153.8999 | 182.4377 | 177.1365
228.9417 | 136.8419 | 153.7671 | 182.3046 | 176.5526
229.9417 | 137.8803 | 154.2169 | 182.2756 | 175.9669
230.9417 | 138.8563 | 154.264 | 182.7728 | 175.8618
231.9417 | 139.5635 | 154.3433 | 183.7782 | 175.9701
232.9417 | 140.1407 | 154.0286 | 183.3027 | 176.2585
233.9417 | 139.335 | 153.7213 | 184.4897 | 176.2476
234.9417 | 139.3661 | 153.8041 | 185.0619 | 176.4327
235.9417 | 139.4163 | 153.9808 | 183.7453 | 175.6694
236.9417 | 138.9872 | 153.5114 | 183.5515 | 174.8313
237.9417 | 138.7993 | 153.1278 | 182.9494 | 174.8016
238.9417 | 139.0887 | 153.2913 | 183.3517 | 174.5451
239.9417 | 139.4376 | 152.8559 | 184.0359 | 173.832
240.9417 | 139.1869 | 153.0514 | 183.9104 | 173.3012
241.9417 | 139.0628 | 153.1392 | 182.8015 | 173.3804
242.9417 | 138.9426 | 153.0168 | 181.8099 | 172.6081
243.9417 | 138.8806 | 152.8286 | 182.2155 | 172.2989
244.9417 | 138.9538 | 153.1399 | 182.3167 | 172.1234
245.9417 | 139.3271 | 152.9657 | 182.2229 | 171.977
246.9417 | 139.7254 | 153.248 | 182.2157 | 172.0285
247.9417 | 140.2683 | 153.084 | 182.2182 | 172.1437
248.9417 | 140.1657 | 153.0942 | 183.1126 | 172.3397
249.9417 | 140.2921 | 153.6087 | 182.7579 | 172.0498
250.9417 | 140.5186 | 153.8048 | 183.4941 | 171.3451
251.9417 | 140.6622 | 154.161 | 183.4146 | 171.0273
252.9417 | 140.5263 | 155.0276 | 184.65 | 173.0216
253.9417 | 140.8936 | 155.7337 | 185.0334 | 174.753
254.9417 | 141.5772 | 156.6367 | 186.0198 | 176.314
255.9417 | 142.5863 | 156.1369 | 186.6617 | 175.8369
256.9417 | 143.1105 | 156.442 | 186.958 | 176.4592
257.9417 | 143.5914 | 157.6885 | 188.5098 | 177.4774
258.9417 | 143.7067 | 157.6525 | 188.9605 | 178.318
259.9417 | 144.1709 | 158.2362 | 191.0553 | 179.4258
260.9417 | 145.1153 | 160.0707 | 191.7934 | 180.8709
261.9417 | 145.6975 | 160.8528 | 193.6154 | 182.0111
262.9417 | 145.7617 | 161.5652 | 193.8004 | 183.6436
263.9417 | 145.4209 | 162.6861 | 195.129 | 183.681
264.9417 | 145.5644 | 162.7364 | 195.5509 | 184.2695
265.9417 | 145.2236 | 163.147 | 195.6002 | 184.5263
266.9417 | 145.4077 | 163.2367 | 195.5597 | 183.9444
267.9417 | 145.3011 | 162.7778 | 195.3288 | 183.5388
268.9417 | 144.9479 | 162.519 | 195.118 | 182.6742
269.9417 | 145.3267 | 162.2405 | 194.5315 | 181.639
270.9417 | 145.2668 | 161.9144 | 194.1262 | 181.1859
271.9417 | 145.7573 | 163.326 | 194.0764 | 180.9527
272.9417 | 146.9945 | 164.1968 | 195.0036 | 181.5749
273.9417 | 147.2238 | 163.5508 | 194.6135 | 181.2518
274.9417 | 147.452 | 163.8263 | 194.7728 | 181.2615
275.9417 | 146.7307 | 163.5918 | 194.6081 | 181.8327
276.9417 | 145.6136 | 162.9556 | 194.179 | 181.7489
277.9417 | 147.4516 | 162.1538 | 194.8268 | 181.7851
278.9417 | 147.1033 | 161.9662 | 195.5343 | 181.7285
279.9417 | 147.9014 | 162.6255 | 195.9159 | 180.9506
280.9417 | 148.6062 | 163.2911 | 197.3364 | 181.1268
281.9417 | 148.141 | 163.5768 | 197.0193 | 181.839
282.9417 | 148.8377 | 163.0584 | 196.997 | 182.0558
283.9417 | 148.1874 | 162.752 | 196.9718 | 182.4748
284.9417 | 148.3663 | 162.7832 | 197.1596 | 182.7981
285.9417 | 147.9522 | 162.6958 | 197.177 | 183.1785
286.9417 | 147.9604 | 163.6439 | 197.5006 | 184.5947
287.9417 | 148.7098 | 165.6738 | 198.5935 | 185.6913
288.9417 | 149.0651 | 166.4612 | 198.989 | 185.3556
289.9417 | 149.5162 | 165.766 | 198.6305 | 185.1645
290.9417 | 149.8117 | 165.8888 | 197.6862 | 184.7484
291.9417 | 150.1582 | 166.0675 | 198.5431 | 186.4019
292.9417 | 150.6516 | 168.1778 | 199.4255 | 187.5125
293.9417 | 151.2061 | 169.313 | 199.8679 | 187.7744
294.9417 | 151.5087 | 169.2145 | 199.7596 | 187.8813
295.9417 | 151.361 | 169.345 | 201.4859 | 189.4623
296.9417 | 151.8808 | 169.3594 | 201.5257 | 190.9412
297.9417 | 153.1018 | 169.76 | 201.1277 | 191.4656
298.9417 | 151.6508 | 169.3953 | 201.091 | 190.8521
299.9417 | 152.0834 | 168.3394 | 201.7326 | 190.7713
300.9417 | 152.0972 | 167.3822 | 201.2759 | 189.559
301.9417 | 152.3885 | 167.3734 | 200.8361 | 188.9001
302.9417 | 151.9926 | 167.2297 | 201.9283 | 188.681
303.9417 | 151.8769 | 167.7724 | 202.0572 | 191.866
304.9417 | 151.7821 | 168.7455 | 202.6538 | 191.4626
305.9417 | 152.4071 | 170.2825 | 202.8834 | 190.3149
306.9417 | 153.4903 | 170.2356 | 202.6599 | 190.2247
307.9417 | 152.9688 | 170.0688 | 202.8096 | 190.2906
308.9417 | 152.5576 | 170.1259 | 202.5012 | 190.7783
309.9417 | 152.8344 | 170.1437 | 201.7262 | 191.9079
310.9417 | 153.0848 | 172.084 | 202.8268 | 193.0914
311.9417 | 153.5343 | 174.2571 | 203.3767 | 194.9111
312.9417 | 154.0986 | 173.8448 | 202.8359 | 194.8887
313.9417 | 154.5038 | 174.9302 | 203.0793 | 194.7274
314.9417 | 154.9373 | 175.0798 | 203.5225 | 195.6986
315.9417 | 154.2596 | 174.2757 | 203.572 | 196.5969
316.9417 | 153.9943 | 176.1109 | 204.5026 | 198.1327
317.9417 | 154.0467 | 176.6762 | 205.3392 | 199.8685
318.9417 | 154.9797 | 176.9112 | 205.2108 | 200.2654
319.9417 | 155.1032 | 177.5094 | 204.8769 | 199.7839
320.9417 | 155.0388 | 176.4935 | 205.8005 | 199.4182
321.9417 | 155.9701 | 176.0599 | 206.5248 | 200.1466
322.9417 | 156.1752 | 176.0909 | 207.1906 | 201.2034
323.9417 | 155.8861 | 174.9712 | 206.5732 | 200.6592
324.9417 | 155.904 | 173.9909 | 205.6193 | 200.8347
325.9417 | 155.7043 | 173.6745 | 205.7966 | 201.0552
326.9417 | 155.929 | 174.5362 | 205.8448 | 201.595
327.9417 | 156.0287 | 174.7497 | 206.0527 | 201.0425
328.9417 | 156.8697 | 174.2184 | 206.3381 | 201.1469
329.9417 | 157.2342 | 173.7284 | 205.6204 | 199.8493
330.9417 | 156.0911 | 173.4981 | 205.3031 | 199.5896
331.9417 | 155.8958 | 172.7501 | 204.8074 | 198.157
332.9417 | 155.5038 | 172.2169 | 204.2497 | 197.4736
333.9417 | 155.555 | 171.6114 | 203.5771 | 197.3942
334.9417 | 155.6116 | 170.6693 | 202.831 | 197.4642
335.9417 | 155.4911 | 170.2903 | 202.394 | 197.0719
336.9417 | 155.9922 | 170.9421 | 202.7941 | 197.7182
337.9417 | 155.9337 | 170.8014 | 202.26 | 197.3054
338.9417 | 156.4569 | 170.5618 | 202.2783 | 197.9991
339.9417 | 155.6902 | 170.2795 | 201.4472 | 198.2605
340.9417 | 155.9974 | 169.86 | 201.1567 | 197.9746
341.9417 | 155.3636 | 169.9376 | 201.5933 | 197.7261
342.9417 | 155.144 | 169.878 | 201.4648 | 196.4836
343.9417 | 155.4282 | 169.6089 | 202.3401 | 196.3356
344.9417 | 156.1445 | 169.7991 | 202.7341 | 196.28
345.9417 | 156.5652 | 171.078 | 203.6341 | 195.9355
346.9417 | 157.1276 | 171.0168 | 203.3358 | 195.2662
347.9417 | 157.911 | 170.8124 | 202.9717 | 194.9616
348.9417 | 158.0097 | 170.9059 | 202.3213 | 194.4869
349.9417 | 158.2258 | 171.4543 | 201.8074 | 193.8124
350.9417 | 157.5633 | 172.4846 | 202.0972 | 193.4544
351.9417 | 157.6055 | 173.6622 | 202.4316 | 193.3585
352.9417 | 157.36 | 173.8106 | 203.295 | 193.5375
353.9417 | 156.7477 | 173.3646 | 203.9228 | 193.1227
354.9417 | 156.547 | 173.508 | 204.6495 | 193.3925
355.9417 | 156.4609 | 172.8866 | 205.9416 | 193.5362
356.9417 | 156.8791 | 172.2038 | 206.1694 | 194.3854
357.9417 | 157.9218 | 172.8649 | 206.6075 | 195.3498
358.9417 | 158.6168 | 172.3257 | 207.5799 | 196.5712
359.9417 | 158.9931 | 172.2586 | 208.1195 | 198.6684
360.9417 | 158.8737 | 172.634 | 209.0126 | 199.5289
361.9417 | 159.6247 | 172.5183 | 209.5661 | 199.8753
362.9417 | 159.8349 | 171.8313 | 208.9605 | 199.3003
363.9417 | 160.0906 | 171.3593 | 208.8063 | 198.9791
364.9417 | 160.3443 | 172.2481 | 208.3454 | 198.9913
365.9417 | 160.1025 | 172.1427 | 208.1024 | 199.0929
366.9417 | 160.6742 | 172.7819 | 208.8412 | 199.3453
367.9417 | 161.0969 | 172.5167 | 209.0526 | 198.9977
368.9417 | 161.1076 | 171.9552 | 208.1828 | 198.4461
369.9417 | 160.5999 | 172.8374 | 208.5229 | 198.8052
370.9417 | 160.6287 | 172.9793 | 208.6481 | 200.0736
371.9417 | 160.825 | 172.6901 | 207.9636 | 199.4672
372.9417 | 161.3514 | 173.9477 | 207.8603 | 199.3487
373.9417 | 160.898 | 174.4578 | 208.5833 | 200.4509
374.9417 | 160.5351 | 174.6321 | 208.8669 | 200.2706
375.9417 | 160.797 | 174.0699 | 209.6703 | 201.1268
376.9417 | 161.0115 | 175.2438 | 210.3226 | 201.952
377.9417 | 160.8669 | 176.2428 | 210.7799 | 202.9567
378.9417 | 160.8584 | 176.8512 | 210.9001 | 202.9282
379.9417 | 161.6098 | 176.589 | 211.3122 | 204.1214
380.9417 | 161.1811 | 176.6005 | 211.3053 | 204.7561
381.9417 | 161.2856 | 178.2455 | 211.8071 | 204.3042
382.9417 | 161.8801 | 178.6582 | 212.5332 | 205.1691
383.9417 | 162.3672 | 178.7125 | 212.1964 | 205.3453
384.9417 | 162.8295 | 178.0517 | 213.3216 | 205.6784
385.9417 | 163.3183 | 178.5703 | 214.0423 | 206.161
386.9417 | 163.3059 | 177.9301 | 214.4005 | 206.5292
387.9417 | 163.1268 | 176.9846 | 214.8162 | 206.9333
388.9417 | 163.4189 | 179.2871 | 216.4576 | 208.2032
389.9417 | 163.6405 | 180.4235 | 216.6359 | 208.6084
390.9417 | 163.6778 | 180.3808 | 217.3065 | 209.3975
391.9417 | 163.9652 | 179.934 | 217.6292 | 210.1625
392.9417 | 164.6463 | 179.9671 | 217.3835 | 209.3468
393.9417 | 164.7435 | 179.396 | 216.5486 | 208.346
394.9417 | 164.8553 | 179.294 | 217.302 | 208.3727
395.9417 | 164.7266 | 178.7324 | 217.7362 | 210.1419
396.9417 | 164.6082 | 179.1257 | 218.4788 | 210.8546
397.9417 | 164.616 | 180.4471 | 219.2421 | 211.4235
398.9417 | 164.4667 | 180.8371 | 218.3046 | 212.1529
399.9417 | 165.083 | 180.5551 | 217.9258 | 211.9894
400.9417 | 165.7397 | 180.2553 | 219.0374 | 212.2192
401.9417 | 164.9353 | 179.5468 | 218.5142 | 212.3511
402.9417 | 165.3512 | 180.1136 | 217.9454 | 212.9885
403.9417 | 165.9546 | 179.6659 | 217.5323 | 212.7684
404.9417 | 165.7706 | 178.9444 | 216.6522 | 211.7024
405.9417 | 165.5151 | 178.2974 | 215.3832 | 210.828
406.9417 | 165.627 | 178.0325 | 214.4561 | 210.8308
407.9417 | 165.4144 | 177.7389 | 214.3064 | 210.6253
408.9417 | 165.247 | 177.4732 | 215.5022 | 210.9504
409.9417 | 165.3024 | 177.3469 | 215.0181 | 211.6204
410.9417 | 165.5028 | 177.2102 | 214.625 | 211.3162
411.9417 | 165.7917 | 177.4026 | 213.7816 | 211.4033
412.9417 | 165.5861 | 178.6373 | 213.9893 | 211.7773
413.9417 | 165.772 | 178.9481 | 214.1319 | 213.1743
414.9417 | 165.9683 | 178.6821 | 214.5908 | 212.5125
415.9417 | 165.6338 | 178.7738 | 213.9725 | 211.6388
416.9417 | 165.567 | 178.6287 | 212.9393 | 211.2999
417.9417 | 165.5713 | 177.7353 | 212.4173 | 210.3455
418.9417 | 165.0767 | 177.738 | 211.9543 | 210.07
419.9417 | 164.725 | 179.3364 | 213.2681 | 211.018
420.9417 | 164.5762 | 180.3547 | 214.5197 | 211.2503
421.9417 | 164.1058 | 180.3676 | 215.0616 | 211.9066
422.9417 | 163.8593 | 180.3287 | 215.6255 | 211.9332
423.9417 | 163.6346 | 180.5784 | 216.4651 | 211.3648
424.9417 | 163.2782 | 180.618 | 216.7357 | 211.2102
425.9417 | 163.4881 | 180.1948 | 216.6618 | 210.2201
426.9417 | 163.6653 | 180.6137 | 217.2327 | 209.3007
427.9417 | 163.7914 | 180.5249 | 217.4242 | 208.2321
428.9417 | 163.9282 | 180.152 | 216.2317 | 207.2624
429.9417 | 164.1999 | 179.7619 | 215.6581 | 207.4076
430.9417 | 164.2742 | 180.5323 | 215.8583 | 207.736
431.9417 | 164.1725 | 180.6243 | 215.6705 | 207.7401
432.9417 | 164.3838 | 180.0259 | 215.9556 | 207.3118
433.9417 | 164.6074 | 178.9764 | 215.686 | 206.1142
434.9417 | 164.6499 | 179.0204 | 215.52 | 205.3817
435.9417 | 165.8791 | 179.2997 | 215.8646 | 204.321
436.9417 | 166.8051 | 180.3228 | 216.8989 | 204.8434
437.9417 | 165.6035 | 180.9064 | 217.6317 | 204.9138
438.9417 | 165.0145 | 180.5761 | 217.9873 | 204.7719
439.9417 | 166.3084 | 180.8758 | 218.0175 | 204.6122
440.9417 | 167.1487 | 180.4832 | 218.5694 | 205.5029
441.9417 | 165.628 | 179.892 | 218.6192 | 205.66
442.9417 | 166.6051 | 180.2618 | 219.0182 | 206.6633
443.9417 | 166.563 | 180.7608 | 220.2642 | 207.5098
444.9417 | 166.3374 | 180.4321 | 220.7611 | 207.518
445.9417 | 166.5057 | 180.3853 | 220.4161 | 207.5448
446.9417 | 167.4201 | 179.803 | 221.0158 | 208.0531
447.9417 | 167.4341 | 179.638 | 221.038 | 207.7269
448.9417 | 167.3481 | 179.1423 | 223.0611 | 209.1741
449.9417 | 167.5886 | 178.2449 | 223.1191 | 209.7785
450.9417 | 168.2873 | 178.3382 | 223.0183 | 209.6033
451.9417 | 168.6155 | 178.4135 | 223.4494 | 209.4245
452.9417 | 168.9791 | 178.0388 | 223.3022 | 209.4017
453.9417 | 168.8908 | 178.8984 | 222.5309 | 209.2525
454.9417 | 168.787 | 178.7057 | 221.2587 | 208.3687
455.9417 | 168.477 | 178.3599 | 220.3046 | 208.2714
456.9417 | 168.6401 | 178.3463 | 220.7017 | 207.9981
457.9417 | 169.1139 | 178.4403 | 221.0671 | 208.1978
458.9417 | 169.1139 | 178.941 | 221.1989 | 208.7119
459.9417 | 170.1699 | 179.8366 | 222.7923 | 209.2707
460.9417 | 170.6141 | 179.9214 | 224.5486 | 210.1036
461.9417 | 170.9447 | 179.6565 | 225.0205 | 210.4213
462.9417 | 170.9703 | 179.9077 | 225.3532 | 211.1903
463.9417 | 171.3935 | 180.0726 | 224.6308 | 211.708
464.9417 | 171.1358 | 180.1609 | 225.7447 | 212.1958
465.9417 | 170.7166 | 180.0603 | 226.1429 | 212.3232
466.9417 | 170.9542 | 180.6192 | 226.1747 | 213.0332
467.9417 | 172.386 | 180.9828 | 226.2315 | 213.1386
468.9417 | 173.0628 | 181.8235 | 225.9849 | 213.1013
469.9417 | 172.7769 | 181.4048 | 226.1844 | 213.2971
470.9417 | 172.6616 | 181.7188 | 226.7267 | 213.6174
471.9417 | 171.9074 | 180.9948 | 226.8886 | 212.7199
472.9417 | 172.3435 | 181.042 | 227.2702 | 213.4626
473.9417 | 171.6332 | 181.3638 | 227.1582 | 213.5796
474.9417 | 170.9822 | 182.8676 | 228.0526 | 214.3335
475.9417 | 170.8964 | 184.6554 | 228.9717 | 214.9794
476.9417 | 171.3745 | 184.6043 | 229.6923 | 215.5556
477.9417 | 172.5616 | 184.9599 | 230.383 | 215.1705
478.9417 | 172.439 | 184.498 | 230.2122 | 213.9581
479.9417 | 172.5748 | 183.7807 | 229.1808 | 213.1947
480.9417 | 173.0865 | 184.0179 | 230.0893 | 213.5279
481.9417 | 172.3788 | 186.0868 | 230.2076 | 214.8378
482.9417 | 172.9574 | 186.0369 | 230.0894 | 214.2948
483.9417 | 173.1453 | 185.5024 | 229.637 | 213.7748
484.9417 | 173.445 | 185.4174 | 229.7525 | 214.2131
485.9417 | 174.1146 | 184.8268 | 228.9588 | 214.4751
486.9417 | 175.0079 | 184.2892 | 229.5142 | 214.4977
487.9417 | 175.1204 | 184.4178 | 229.7383 | 215.2001
488.9417 | 174.7383 | 184.4363 | 230.2022 | 215.0667
489.9417 | 174.6164 | 185.6069 | 229.694 | 214.739
490.9417 | 174.3099 | 186.488 | 229.7221 | 215.6512
491.9417 | 174.2083 | 187.3543 | 231.1293 | 215.6259
492.9417 | 175.1888 | 187.6167 | 231.731 | 216.1013
493.9417 | 175.2743 | 187.7211 | 231.7535 | 214.9241
494.9417 | 175.5143 | 187.0546 | 230.7994 | 215.5802
495.9417 | 176.4335 | 186.5998 | 231.0598 | 215.6613
496.9417 | 176.8497 | 186.0877 | 231.7241 | 216.6782
497.9417 | 177.1501 | 185.7274 | 231.2416 | 216.1985
498.9417 | 177.0284 | 185.2917 | 231.1856 | 215.6939
499.9417 | 176.95 | 185.4243 | 230.9798 | 215.5084
500.9573 | 176.873 | 185.6208 | 231.3188 | 215.4414
501.9417 | 176.9182 | 185.4193 | 230.5564 | 215.226
502.9417 | 177.3073 | 185.0718 | 230.1198 | 214.641
503.9417 | 177.1074 | 185.3146 | 229.7589 | 214.2809
504.9417 | 177.1624 | 186.1932 | 230.4101 | 213.9985
505.9417 | 176.7227 | 186.1993 | 230.3448 | 214.1232
506.9417 | 177.1768 | 186.0758 | 231.0104 | 214.2115
507.9417 | 177.2252 | 187.4308 | 232.1221 | 214.6258
508.9417 | 177.1501 | 187.6729 | 231.2523 | 214.6836
509.9417 | 177.1965 | 187.483 | 231.4791 | 214.2725
510.9417 | 176.4136 | 188.4045 | 231.9986 | 214.0366
511.9417 | 176.9925 | 188.0585 | 231.0093 | 213.2042
512.9417 | 176.8972 | 188.2364 | 231.2423 | 212.3372
513.9417 | 176.5665 | 188.4269 | 231.6257 | 211.5222
514.9417 | 176.4651 | 189.1566 | 233.7351 | 212.9317
515.9417 | 176.6714 | 191.0352 | 234.7783 | 215.7094
516.9417 | 177.859 | 192.3345 | 235.3718 | 217.0262
517.9417 | 177.7235 | 193.7113 | 237.3819 | 218.3286
518.9573 | 176.0793 | 195.0068 | 239.1755 | 219.0544
519.9417 | 175.4535 | 195.6573 | 239.3251 | 219.5321
520.9417 | 175.549 | 196.7871 | 239.8064 | 220.8472
521.9417 | 175.7548 | 197.4862 | 241.2497 | 222.5475
522.9417 | 176.5145 | 198.3017 | 243.8224 | 223.5298
523.9417 | 177.1133 | 197.5011 | 244.6951 | 224.6422
524.9417 | 177.628 | 198.473 | 245.5642 | 224.9641
525.9417 | 178.1462 | 198.0735 | 245.4736 | 225.1956
526.9417 | 178.156 | 198.5017 | 245.592 | 224.3207
527.9417 | 178.8494 | 199.28 | 246.153 | 224.577
528.9417 | 178.4571 | 200.1603 | 246.2928 | 225.8906
529.9417 | 178.7802 | 199.2891 | 246.2019 | 226.2101
530.9417 | 179.1056 | 199.6824 | 247.6888 | 226.9009
531.9417 | 178.8959 | 199.2775 | 246.8428 | 225.5904
532.9417 | 179.3435 | 201.5689 | 246.7434 | 226.623
533.9417 | 179.2481 | 202.2868 | 247.1392 | 228.6439
534.9417 | 179.7291 | 202.8011 | 246.1909 | 229.4105
535.9417 | 180.44 | 202.0429 | 245.7454 | 230.2397
536.9417 | 181.1394 | 201.9344 | 246.0598 | 231.0402
537.9417 | 181.6601 | 203.4211 | 245.7871 | 231.9099
538.9417 | 181.4345 | 205.0136 | 245.8147 | 232.1321
539.9417 | 181.8776 | 204.471 | 245.4251 | 232.687
540.9417 | 182.2668 | 205.1073 | 244.6678 | 232.1338
541.9417 | 183.2713 | 206.1284 | 244.2223 | 230.7219
542.9417 | 184.1278 | 204.6969 | 243.9995 | 229.3351
543.9417 | 184.1357 | 205.3808 | 243.5198 | 228.4711
544.9417 | 183.9207 | 204.8842 | 242.8314 | 227.0547
545.9417 | 184.8178 | 204.1257 | 242.6205 | 226.4299
546.9417 | 184.4418 | 203.1058 | 242.1038 | 226.409
547.9417 | 184.4766 | 202.4609 | 241.8727 | 225.0494
548.9573 | 184.0776 | 201.3593 | 242.0668 | 224.8945
549.9417 | 184.0968 | 201.199 | 241.6725 | 225.1685
550.9417 | 184.6257 | 200.0474 | 241.1491 | 225.3531
551.9417 | 184.3201 | 199.4157 | 241.2878 | 224.9171
552.9417 | 184.8254 | 198.3872 | 240.9124 | 224.5159
553.9417 | 184.7817 | 197.789 | 240.0721 | 223.0383
554.9417 | 184.5702 | 197.432 | 239.2072 | 222.8742
555.9417 | 184.4484 | 197.3208 | 238.2096 | 221.8736
556.9417 | 184.5918 | 197.5185 | 238.5011 | 221.6772
557.9417 | 183.8643 | 197.6038 | 237.7817 | 221.2022
558.9417 | 183.9278 | 196.3406 | 237.2272 | 220.036
559.9417 | 184.4856 | 195.6418 | 237.6685 | 220.3866
560.9417 | 185.8028 | 195.2912 | 238.4454 | 220.3275
561.9417 | 185.6057 | 195.4621 | 238.1494 | 220.5609
562.9417 | 185.5512 | 195.0968 | 237.4031 | 219.3851
563.9417 | 185.4875 | 194.6346 | 237.6559 | 219.3752
564.9417 | 185.1966 | 195.5989 | 237.9571 | 220.1644
565.9417 | 185.4124 | 196.0629 | 238.6935 | 219.9751
566.9417 | 185.5334 | 197.3074 | 238.2418 | 221.0577
567.9417 | 185.5298 | 197.8277 | 238.8899 | 221.2085
568.9417 | 185.7835 | 198.2206 | 240.1475 | 222.2977
569.9417 | 185.7813 | 200.042 | 241.2096 | 223.1714
570.9417 | 185.9889 | 200.2381 | 242.5728 | 223.4537
571.9417 | 185.614 | 200.5636 | 243.4487 | 223.8289
572.9417 | 185.9869 | 201.004 | 245.0686 | 223.255
573.9417 | 186.8005 | 201.1934 | 244.8522 | 222.8004
574.9417 | 188.1089 | 201.9168 | 246.0794 | 223.4553
575.9417 | 187.7939 | 201.646 | 247.135 | 227.1266
576.9417 | 187.5164 | 203.0761 | 247.0019 | 227.094
577.9417 | 187.8215 | 201.6791 | 246.5879 | 225.421
578.9417 | 188.267 | 201.3859 | 246.7182 | 225.9159
579.9417 | 188.0087 | 200.5183 | 246.2765 | 226.5241
580.9417 | 187.9158 | 199.4421 | 246.0277 | 226.4933
581.9417 | 188.2853 | 199.4369 | 245.6541 | 225.6312
582.9417 | 188.3647 | 198.6972 | 245.534 | 225.9128
583.9417 | 188.2676 | 198.3472 | 244.9933 | 224.9538
584.9417 | 187.4141 | 197.9479 | 244.613 | 225.2495
585.9417 | 187.2837 | 198.2713 | 244.9366 | 224.1111
586.9417 | 187.3016 | 198.0382 | 246.529 | 224.6477
587.9417 | 188.0118 | 199.6885 | 248.2331 | 225.5054
588.9417 | 188.8958 | 200.3591 | 250.5154 | 225.6477
589.9417 | 189.3909 | 201.7236 | 251.274 | 225.7609
590.9417 | 188.7235 | 202.8831 | 251.2225 | 225.5967
591.9417 | 188.3245 | 203.0709 | 250.9568 | 225.07
592.9417 | 187.3586 | 203.8407 | 251.4816 | 224.5899
593.9417 | 187.8219 | 204.4731 | 251.4941 | 224.4502
594.9417 | 189.2716 | 205.0337 | 252.6066 | 223.2272
595.9417 | 190.6349 | 205.6754 | 253.1667 | 222.8004
596.9417 | 191.8109 | 206.6908 | 255.1089 | 222.7261
597.9417 | 191.6544 | 206.6565 | 255.2825 | 222.8933
598.9417 | 191.1642 | 207.0706 | 256.0955 | 221.8108
599.9417 | 190.7633 | 207.7862 | 256.1517 | 222.8713
600.9417 | 191.2031 | 207.7842 | 255.3482 | 225.4172
601.9417 | 191.407 | 208.8775 | 255.7996 | 228.1635
602.9417 | 192.3398 | 208.4103 | 257.8699 | 230.3439
603.9417 | 192.1017 | 209.0106 | 257.887 | 231.9594
604.9417 | 192.4832 | 209.0756 | 257.6776 | 232.9166
605.9417 | 193.2201 | 208.5956 | 258.9959 | 235.3064
606.9417 | 193.3408 | 208.2133 | 259.1194 | 235.8875
607.9417 | 194.1298 | 207.3472 | 259.6128 | 236.2476
608.9573 | 194.394 | 207.8961 | 260.0014 | 235.9436
609.9417 | 194.9881 | 209.3751 | 261.5361 | 237.4168
610.9573 | 196.8058 | 210.0429 | 261.9415 | 236.9037
611.9573 | 195.8075 | 210.0256 | 261.0964 | 237.5623
612.9417 | 196.1591 | 209.7585 | 261.3285 | 236.5239
613.9573 | 197.0328 | 209.9524 | 261.1732 | 235.4658
614.9417 | 195.9128 | 210.6155 | 261.3125 | 236.0416
615.9417 | 195.0361 | 211.2794 | 261.813 | 236.0852
616.9417 | 194.6528 | 210.9536 | 262.6674 | 235.8868
617.9417 | 194.8762 | 211.7844 | 264.5229 | 236.2799
618.9417 | 195.8196 | 212.9583 | 264.2817 | 236.2264
619.9417 | 194.7833 | 213.7813 | 265.7519 | 236.2916
620.9417 | 194.2892 | 213.4856 | 265.5076 | 236.317
621.9417 | 193.4025 | 214.0889 | 265.7324 | 237.3926
622.9417 | 194.5748 | 214.4016 | 267.25 | 237.7618
623.9417 | 195.5297 | 214.036 | 267.4108 | 237.4849
624.9417 | 195.6226 | 214.878 | 267.574 | 237.9505
625.9417 | 195.9673 | 215.4612 | 267.3967 | 238.8884
626.9417 | 196.1427 | 214.4209 | 266.3652 | 238.8858
627.9417 | 196.9338 | 214.2817 | 266.6452 | 239.2933
628.9417 | 196.4566 | 213.7961 | 265.6471 | 238.967
629.9417 | 196.9676 | 215.9903 | 266.7276 | 238.5571
630.9417 | 197.3796 | 215.8462 | 266.3672 | 239.4095
631.9417 | 197.5457 | 216.1886 | 266.7114 | 239.4957
632.9417 | 198.9365 | 216.7453 | 268.3471 | 238.5713
633.9417 | 199.0844 | 217.6778 | 269.2023 | 237.7777
634.9417 | 198.504 | 218.2103 | 268.742 | 237.0982
635.9417 | 199.1155 | 219.0656 | 268.4222 | 237.9358
636.9417 | 200.0957 | 219.166 | 268.1548 | 237.5616
637.9417 | 199.9969 | 218.9721 | 267.2771 | 236.1798
638.9417 | 199.5632 | 218.3819 | 266.4981 | 234.8718
639.9417 | 199.48 | 218.072 | 265.7886 | 234.5476
640.9417 | 200.1197 | 218.1774 | 265.176 | 232.9766
641.9417 | 199.5936 | 218.2961 | 265.2095 | 232.6287
642.9417 | 199.1293 | 218.1927 | 265.9929 | 232.0219
643.9417 | 198.6646 | 217.7511 | 266.4352 | 232.1121
644.9417 | 198.0402 | 217.943 | 267.0738 | 231.5094
645.9417 | 197.8333 | 218.3514 | 266.736 | 232.5148
646.9417 | 197.6498 | 217.7459 | 265.5946 | 234.6814
647.9417 | 197.5073 | 217.4671 | 265.2067 | 234.864
648.9417 | 197.2226 | 217.6617 | 265.1431 | 235.3364
649.9417 | 196.5633 | 217.7591 | 264.9586 | 236.163
650.9417 | 196.5261 | 218.8671 | 267.1222 | 238.254
651.9417 | 197.3099 | 219.2683 | 266.7409 | 239.4846
652.9417 | 197.9927 | 219.288 | 267.3245 | 238.7646
653.9417 | 198.7901 | 220.0929 | 267.2058 | 237.4851
654.9417 | 199.9565 | 220.7394 | 268.1912 | 237.5636
655.9417 | 200.3045 | 221.5949 | 268.5506 | 237.0393
656.9417 | 200.8385 | 220.6841 | 268.2782 | 235.6275
657.9417 | 200.3056 | 221.2719 | 269.1017 | 234.7454
658.9417 | 200.0621 | 220.7004 | 268.3812 | 234.0645
659.9417 | 200.1447 | 220.9461 | 268.6341 | 234.9949
660.9417 | 199.3331 | 220.1448 | 271.1792 | 236.8184
661.9417 | 199.3097 | 219.8905 | 272.346 | 237.5871
662.9417 | 200.0596 | 220.1318 | 273.3749 | 237.9238
663.9417 | 201.1928 | 220.6317 | 273.4088 | 237.4644
664.9417 | 202.0372 | 221.6409 | 272.7573 | 236.6091
665.9417 | 202.9307 | 221.5337 | 272.0029 | 235.2022
666.9417 | 203.4076 | 221.3143 | 270.9444 | 234.4515
667.9417 | 202.9516 | 220.8599 | 271.7417 | 234.1621
668.9417 | 203.3655 | 223.45 | 272.5763 | 233.6205
669.9417 | 203.5152 | 223.8548 | 273.7161 | 234.438
670.9417 | 205.0167 | 223.3847 | 272.9323 | 234.8976
671.9417 | 205.5469 | 224.8076 | 272.1351 | 235.2406
672.9417 | 203.9501 | 225.519 | 271.6599 | 235.3234
673.9417 | 202.955 | 225.777 | 271.7359 | 236.5938
674.9417 | 202.4179 | 225.0749 | 272.9912 | 238.2557
675.9417 | 202.5341 | 225.5788 | 273.3978 | 238.002
676.9417 | 203.2874 | 225.0543 | 274.0625 | 238.6979
677.9417 | 203.7735 | 224.3263 | 273.694 | 239.1805
678.9417 | 204.1852 | 223.7053 | 275.2364 | 241.5929
679.9417 | 204.2453 | 223.978 | 275.6297 | 242.0146
680.9417 | 204.4454 | 224.3694 | 275.207 | 242.2227
681.9417 | 204.9427 | 223.5645 | 275.6107 | 241.2506
682.9417 | 204.4204 | 225.6209 | 276.1986 | 240.628
683.9417 | 204.1167 | 225.5991 | 275.7732 | 239.885
684.9417 | 204.9421 | 225.3039 | 276.2662 | 239.6108
685.9417 | 205.1134 | 224.6264 | 276.9627 | 240.2268
686.9417 | 205.0428 | 224.9347 | 276.9696 | 239.763
687.9417 | 204.0736 | 224.2881 | 277.5255 | 239.4245
688.9417 | 204.0975 | 223.6785 | 277.2336 | 239.6505
689.9417 | 204.6184 | 223.4516 | 276.7035 | 240.09
690.9417 | 203.804 | 223.6163 | 277.1733 | 240.4602
691.9417 | 203.1481 | 224.3683 | 276.5399 | 242.4249
692.9417 | 204.2003 | 223.9276 | 275.9168 | 242.6385
693.9417 | 205.3029 | 224.1004 | 275.3213 | 242.1082
694.9417 | 205.1901 | 224.7511 | 274.5905 | 242.1402
695.9417 | 205.2853 | 225.1236 | 275.331 | 242.1818
696.9417 | 205.7219 | 225.0979 | 275.2459 | 244.3235
697.9417 | 206.2279 | 225.9692 | 275.6972 | 245.5552
698.9417 | 205.7582 | 225.4197 | 275.8036 | 246.1878
699.9417 | 206.1573 | 225.1946 | 275.8087 | 246.5009
700.9417 | 205.9595 | 225.4094 | 275.8552 | 247.7864
701.9417 | 205.7111 | 226.7427 | 275.6481 | 248.75
702.9417 | 204.5742 | 226.7886 | 275.0726 | 249.7356
703.9417 | 203.6642 | 227.4951 | 274.3862 | 249.6505
704.9417 | 204.0865 | 226.2819 | 274.4795 | 248.9735
705.9417 | 203.5717 | 226.7214 | 274.4246 | 247.1632
706.9417 | 203.4591 | 226.3723 | 273.6923 | 246.1591
707.9417 | 202.8171 | 225.5164 | 273.4478 | 244.7998
708.9417 | 203.3006 | 225.8762 | 273.8425 | 243.9992
709.9417 | 204.0872 | 225.8308 | 273.1051 | 245.0069
710.9417 | 203.8694 | 225.4647 | 273.2381 | 244.7086
711.9417 | 204.22 | 225.2732 | 273.2807 | 244.6479
712.9417 | 204.496 | 224.1218 | 272.7491 | 243.5209
713.9417 | 205.1549 | 223.7075 | 272.3323 | 242.8597
714.9417 | 205.6095 | 223.5078 | 271.9556 | 241.179
715.9417 | 205.9091 | 223.1344 | 270.8245 | 239.7657
716.9417 | 206.5066 | 224.4841 | 270.5862 | 238.3403
717.9417 | 207.469 | 224.1936 | 270.6522 | 238.4882
718.9417 | 207.4208 | 224.4312 | 270.017 | 238.5211
719.9417 | 207.6669 | 224.6443 | 269.85 | 237.2903
720.9417 | 206.9833 | 223.6004 | 269.7061 | 238.1393
721.9417 | 206.3079 | 222.886 | 269.117 | 237.9103
722.9417 | 207.3585 | 223.0985 | 269.6227 | 237.3872
723.9417 | 208.5264 | 222.9582 | 270.3835 | 237.1468
724.9417 | 208.6199 | 222.2261 | 270.748 | 237.1982
725.9417 | 207.593 | 221.5885 | 271.1245 | 236.4559
726.9417 | 207.3892 | 220.663 | 271.9276 | 235.3305
727.9417 | 206.7397 | 220.59 | 272.1284 | 234.3901
728.9417 | 207.5857 | 220.6359 | 272.3802 | 233.4954
729.9417 | 206.6947 | 220.0766 | 272.5111 | 233.2914
730.9417 | 206.6455 | 219.7562 | 271.0022 | 233.7071
731.9417 | 206.7521 | 219.0462 | 270.1717 | 232.9367
732.9417 | 207.1266 | 218.7031 | 269.4379 | 233.0743
733.9417 | 207.4147 | 219.2757 | 269.4803 | 233.2152
734.9417 | 207.4328 | 218.6153 | 268.4003 | 232.4229
735.9417 | 207.0318 | 217.9788 | 267.2366 | 232.4026
736.9417 | 207.1586 | 218.029 | 267.3036 | 232.4384
737.9417 | 207.5967 | 218.2887 | 267.3468 | 232.2349
738.9417 | 207.1999 | 218.3279 | 266.9118 | 232.8179
739.9417 | 208.1462 | 219.0656 | 267.7913 | 232.9014
740.9417 | 208.8945 | 220.5265 | 269.5925 | 233.6044
741.9417 | 208.9742 | 220.5153 | 269.3383 | 234.8889
742.9417 | 209.2186 | 221.325 | 271.4469 | 236.4507
743.9417 | 208.0137 | 222.7554 | 272.6683 | 238.7112
744.9417 | 207.7973 | 222.7236 | 272.629 | 240.6762
745.9417 | 209.3002 | 222.927 | 272.7397 | 241.6879
746.9417 | 209.1202 | 222.6253 | 272.1147 | 240.5616
747.9417 | 208.564 | 222.37 | 271.3041 | 239.6718
748.9417 | 209.9797 | 222.9569 | 272.4258 | 240.4575
749.9417 | 210.8097 | 223.3887 | 272.5873 | 239.8184
750.9417 | 211.5361 | 223.2121 | 271.5799 | 238.3595
751.9417 | 212.4576 | 223.2892 | 271.251 | 238.3103
752.9417 | 213.3055 | 222.7823 | 271.6556 | 237.583
753.9417 | 214.2358 | 222.8763 | 272.2542 | 237.4065
754.9417 | 214.282 | 222.1476 | 272.9017 | 236.6022
755.9417 | 214.3133 | 221.6258 | 272.315 | 235.4474
756.9417 | 213.2521 | 221.5603 | 271.7416 | 234.9511
757.9417 | 213.1983 | 221.8829 | 270.8263 | 235.6494
758.9573 | 213.2743 | 221.8985 | 272.0252 | 235.1188
759.9417 | 212.6932 | 222.1019 | 271.5999 | 235.4722
760.9417 | 212.8995 | 221.7944 | 271.5164 | 235.2376
761.9417 | 213.0813 | 222.1651 | 270.5886 | 234.4787
762.9417 | 213.8044 | 221.9746 | 269.9617 | 233.5212
763.9417 | 214.004 | 222.6329 | 270.6644 | 234.8316
764.9417 | 214.5551 | 222.3513 | 271.5135 | 234.4946
765.9417 | 213.0918 | 222.5146 | 271.9846 | 234.2631
766.9417 | 212.98 | 222.5403 | 271.0112 | 235.7167
767.9417 | 213.4053 | 222.3644 | 271.1449 | 236.4363
768.9417 | 212.9498 | 222.5242 | 269.7744 | 237.7567
769.9417 | 213.3082 | 223.3664 | 269.821 | 238.0908
770.9417 | 213.0255 | 223.8644 | 270.8988 | 238.7036
771.9417 | 213.7711 | 224.2914 | 270.9936 | 240.1431
772.9417 | 214.539 | 226.1776 | 271.4726 | 240.9785
773.9417 | 215.2669 | 227.1331 | 272.7658 | 242.8913
774.9417 | 215.3959 | 227.1939 | 273.551 | 242.7806
775.9417 | 214.9489 | 230.2787 | 275.3699 | 242.0269
776.9417 | 214.5026 | 230.3179 | 275.8369 | 242.3471
777.9417 | 214.8554 | 230.3508 | 276.7761 | 241.9501
778.9417 | 214.8156 | 231.7176 | 276.4798 | 241.4903
779.9417 | 214.929 | 232.9832 | 276.6188 | 240.317
780.9417 | 214.6943 | 232.5971 | 276.8125 | 239.9595
781.9417 | 214.8202 | 232.9943 | 276.6761 | 238.7401
782.9417 | 215.2064 | 233.8456 | 277.3907 | 238.6924
783.9417 | 215.596 | 233.8239 | 277.8017 | 237.0064
784.9417 | 215.0141 | 234.2973 | 278.2437 | 236.7002
785.9417 | 215.2325 | 233.9426 | 277.5255 | 235.3748
786.9417 | 215.8056 | 232.9274 | 279.4688 | 235.26
787.9417 | 214.791 | 233.1158 | 279.7468 | 235.5885
788.9417 | 215.3591 | 234.2875 | 280.0353 | 236.8508
789.9417 | 215.4443 | 236.9803 | 280.2311 | 237.7596
790.9417 | 214.5044 | 236.1576 | 279.827 | 237.6807
791.9417 | 214.623 | 236.4141 | 279.8962 | 236.909
792.9417 | 215.8062 | 237.5345 | 280.2386 | 236.5381
793.9417 | 215.7544 | 238.5784 | 280.0869 | 235.5916
794.9417 | 215.663 | 240.6767 | 280.427 | 234.6777
795.9417 | 215.756 | 242.3364 | 280.5906 | 233.8509
796.9417 | 215.6885 | 243.4956 | 280.6979 | 233.3027
797.9417 | 215.7685 | 243.8539 | 280.9223 | 234.2543
798.9417 | 215.3156 | 243.799 | 281.376 | 236.3569
799.9417 | 215.6287 | 244.7059 | 281.7408 | 237.605
800.9417 | 216.093 | 245.1361 | 281.0242 | 236.6092
801.9417 | 216.6586 | 245.0917 | 281.9518 | 235.9162
802.9417 | 217.6434 | 244.6151 | 282.406 | 236.2274
803.9417 | 217.4092 | 244.2278 | 282.968 | 236.7213
804.9417 | 217.107 | 244.8635 | 282.4458 | 237.076
805.9417 | 217.8029 | 245.3506 | 282.6659 | 236.2918
806.9417 | 218.7561 | 244.3881 | 281.9034 | 235.1184
807.9417 | 219.8337 | 244.6009 | 281.9482 | 233.9458
808.9417 | 220.3883 | 244.3161 | 282.3231 | 234.0331
809.9417 | 219.8097 | 243.9741 | 282.5542 | 234.5342
810.9417 | 219.8396 | 242.5395 | 282.1981 | 235.0142
811.9417 | 219.8148 | 243.3207 | 283.4417 | 238.2314
812.9417 | 219.0257 | 242.9857 | 284.0734 | 241.0596
813.9417 | 218.8267 | 243.2351 | 284.0911 | 242.6488
814.9417 | 219.9067 | 243.7955 | 283.0255 | 243.2813
815.9417 | 219.7875 | 242.9847 | 282.7552 | 243.0861
816.9417 | 219.9024 | 243.1233 | 283.1462 | 243.4372
817.9417 | 219.8372 | 242.8683 | 283.1213 | 244.5297
818.9417 | 219.704 | 244.3518 | 282.9165 | 244.1751
819.9417 | 219.5004 | 244.5873 | 282.5735 | 243.6171
820.9417 | 219.1371 | 244.4662 | 282.5309 | 243.1102
821.9417 | 219.1668 | 243.6882 | 282.1635 | 242.9424
822.9417 | 219.1044 | 244.3445 | 282.394 | 242.5154
823.9417 | 219.2952 | 244.7986 | 282.7881 | 241.775
824.9417 | 220.4565 | 244.3978 | 283.0645 | 242.54
825.9417 | 221.3609 | 244.2283 | 283.0195 | 243.5965
826.9417 | 221.0582 | 244.6414 | 282.2657 | 243.1556
827.9417 | 221.3314 | 243.9716 | 282.0613 | 242.8371
828.9417 | 221.3265 | 242.4935 | 280.8182 | 243.6961
829.9417 | 221.5893 | 241.874 | 280.7811 | 244.6875
830.9417 | 221.4705 | 241.5361 | 280.0903 | 243.3569
831.9417 | 221.6797 | 241.1278 | 279.2763 | 242.1016
832.9417 | 222.3865 | 241.3103 | 279.2557 | 240.8868
833.9417 | 222.7042 | 240.5395 | 278.4558 | 239.5255
834.9417 | 222.3828 | 239.7678 | 277.5059 | 238.4009
835.9417 | 222.5582 | 238.7524 | 276.8684 | 237.2012
836.9417 | 221.9669 | 238.1705 | 276.9753 | 236.8519
837.9417 | 221.1173 | 237.7802 | 276.7267 | 236.2173
838.9417 | 220.9279 | 236.7927 | 276.2501 | 236.3893
839.9417 | 220.8223 | 237.3753 | 276.8425 | 236.3723
840.9417 | 221.2617 | 238.4944 | 277.995 | 235.6897
841.9417 | 221.6451 | 238.1657 | 277.5795 | 235.8027
842.9417 | 221.2708 | 237.6074 | 276.6959 | 235.4562
843.9417 | 221.4315 | 237.1714 | 276.6325 | 235.2249
844.9417 | 222.2824 | 236.9088 | 276.8523 | 234.5938
845.9417 | 222.3626 | 236.4802 | 276.3867 | 233.4389
846.9417 | 222.4601 | 236.8448 | 276.6004 | 233.6636
847.9417 | 222.5225 | 236.6126 | 276.1474 | 232.7949
848.9417 | 222.1178 | 235.7558 | 275.6927 | 231.9731
849.9417 | 222.0402 | 235.002 | 275.4158 | 231.2247
850.9417 | 222.0447 | 235.0414 | 275.3745 | 230.5294
851.9417 | 221.4938 | 235.9313 | 276.7111 | 231.7915
852.9417 | 220.9259 | 237.1334 | 277.1019 | 233.4273
853.9417 | 221.1041 | 237.2571 | 277.7867 | 235.3097
854.9417 | 220.6861 | 238.365 | 278.0912 | 236.7197
855.9417 | 220.6681 | 240.1355 | 279.0817 | 238.7969
856.9417 | 221.034 | 239.9201 | 278.6778 | 239.3403
857.9417 | 221.3212 | 239.7638 | 278.6696 | 239.7409
858.9417 | 221.045 | 240.3725 | 279.1037 | 239.17
859.9417 | 220.7587 | 242.4074 | 279.9964 | 241.4562
860.9417 | 221.3629 | 243.042 | 280.4345 | 242.7641
861.9417 | 220.0516 | 242.6056 | 281.4092 | 242.9527
862.9417 | 221.5503 | 242.0733 | 281.3843 | 242.7306
863.9417 | 222.4737 | 243.7584 | 282.9644 | 244.0231
864.9417 | 222.8345 | 245.0188 | 283.7422 | 245.725
865.9417 | 222.2173 | 245.1684 | 283.5862 | 245.9067
866.9417 | 222.3398 | 244.4086 | 283.8998 | 245.6922
867.9417 | 222.3773 | 245.5349 | 283.5133 | 246.2995
868.9417 | 222.9643 | 246.3226 | 284.6075 | 246.8588
869.9417 | 223.8461 | 246.2711 | 285.3614 | 246.8314
870.9417 | 223.2596 | 245.598 | 284.8152 | 246.8248
871.9417 | 223.8902 | 244.7147 | 285.4272 | 247.6324
872.9417 | 223.7319 | 244.1484 | 285.193 | 247.7889
873.9417 | 224.7431 | 244.2119 | 286.631 | 248.3918
874.9417 | 225.1386 | 244.4096 | 287.3023 | 247.3351
875.9417 | 225.7867 | 243.8545 | 286.4728 | 246.5262
876.9417 | 225.9934 | 242.9581 | 285.9053 | 246.6137
877.9417 | 225.2442 | 242.4688 | 285.8991 | 246.0313
878.9417 | 223.9803 | 241.1841 | 285.5016 | 245.7453
879.9417 | 224.4564 | 241.3345 | 285.1841 | 244.5578
880.9417 | 224.4495 | 241.2459 | 285.7296 | 243.8708
881.9417 | 224.7603 | 242.9315 | 285.5958 | 242.897
882.9417 | 225.9422 | 243.5096 | 285.1142 | 242.2746
883.9417 | 226.452 | 243.4558 | 286.1436 | 240.8212
884.9417 | 226.6946 | 243.0715 | 285.8098 | 240.3684
885.9417 | 227.9984 | 242.3864 | 286.9285 | 240.2102
886.9417 | 228.444 | 241.1177 | 287.2333 | 241.4958
887.9417 | 228.6427 | 240.7331 | 287.0391 | 240.8094
888.9417 | 228.597 | 239.6201 | 287.2386 | 240.1352
889.9417 | 229.144 | 239.0535 | 287.5058 | 239.4495
890.9417 | 230.2102 | 239.9467 | 287.6096 | 239.1487
891.9417 | 230.2024 | 239.2314 | 288.1151 | 238.1664
892.9417 | 231.3131 | 239.2825 | 289.5397 | 238.2238
893.9417 | 231.0191 | 238.4385 | 288.5807 | 237.3996
894.9417 | 231.3633 | 238.0733 | 287.636 | 236.8154
895.9417 | 230.8166 | 237.7682 | 286.7362 | 236.289
896.9417 | 230.5705 | 237.6082 | 286.17 | 236.0917
897.9417 | 230.8026 | 237.9011 | 285.8104 | 235.6576
898.9417 | 230.7935 | 237.5397 | 284.7798 | 235.7814
899.9417 | 230.8125 | 237.4756 | 284.8421 | 235.1215
900.9417 | 231.5887 | 237.4179 | 285.8225 | 235.2167
901.9417 | 231.7081 | 236.4804 | 284.3544 | 234.7245
902.9417 | 232.5364 | 236.4776 | 283.4723 | 235.0864
903.9417 | 232.3091 | 236.355 | 282.9816 | 234.4117
904.9417 | 232.2624 | 235.5645 | 282.2907 | 233.8537
905.9417 | 231.6365 | 235.106 | 280.9582 | 233.5661
906.9417 | 230.6014 | 234.5757 | 279.744 | 233.4657
907.9417 | 229.8351 | 235.2737 | 279.5756 | 232.9998
908.9417 | 229.1377 | 235.9143 | 280.3564 | 234.8209
909.9417 | 229.4761 | 236.2777 | 281.3465 | 234.9178
910.9417 | 229.915 | 235.9351 | 281.7425 | 235.477
911.9417 | 229.8677 | 235.8319 | 281.6163 | 235.6782
912.9417 | 229.0054 | 235.4659 | 282.3873 | 235.8047
913.9417 | 228.5269 | 235.7206 | 284.4015 | 237.8274
914.9417 | 229.6501 | 235.3956 | 285.842 | 238.4733
915.9417 | 229.7956 | 236.0818 | 288.0828 | 240.3533
916.9417 | 230.6746 | 237.218 | 288.0425 | 240.6955
917.9417 | 232.1546 | 237.0973 | 288.6624 | 241.5344
918.9417 | 232.4796 | 237.1203 | 287.2958 | 240.6807
919.9417 | 232.4456 | 237.1059 | 286.9869 | 240.6468
920.9417 | 233.4481 | 237.5661 | 286.6794 | 240.9618
921.9417 | 234.7746 | 237.3328 | 286.3032 | 241.9351
922.9417 | 235.2641 | 237.6447 | 287.0666 | 243.6536
923.9417 | 235.2377 | 238.1871 | 289.5363 | 244.4277
924.9417 | 234.6366 | 240.2447 | 290.6424 | 245.9541
925.9417 | 233.5163 | 241.7795 | 292.2097 | 246.0581
926.9417 | 234.5057 | 243.6955 | 293.6728 | 245.9296
927.9417 | 235.9989 | 243.8265 | 293.6225 | 246.5676
928.9417 | 235.7453 | 243.7507 | 293.8034 | 247.0659
929.9417 | 235.6029 | 247.5647 | 294.5163 | 249.0238
930.9417 | 236.3613 | 248.6207 | 294.6392 | 251.3697
931.9417 | 237.1899 | 250.7029 | 295.2106 | 253.6577
932.9417 | 238.7016 | 251.8394 | 296.9146 | 256.2954
933.9417 | 240.1394 | 252.7951 | 299.0617 | 256.6577
934.9417 | 241.2667 | 252.692 | 298.3663 | 257.3928
935.9417 | 242.8469 | 252.6269 | 299.0896 | 256.2669
936.9417 | 243.8804 | 252.1053 | 299.3958 | 255.5262
937.9417 | 244.974 | 251.844 | 298.22 | 255.0323
938.9417 | 245.9116 | 252.2176 | 299.168 | 254.055
939.9417 | 246.5877 | 251.6724 | 300.1647 | 252.8097
940.9417 | 247.1324 | 251.0086 | 299.1794 | 251.8627
941.9417 | 246.9833 | 251.1103 | 298.3707 | 250.7641
942.9417 | 248.8364 | 251.0789 | 300.2387 | 250.8672
943.9417 | 249.6011 | 251.054 | 299.1481 | 250.0109
944.9417 | 249.5755 | 251.7164 | 299.5488 | 250.277
945.9417 | 250.7562 | 252.1141 | 301.387 | 249.8254
946.9417 | 250.0124 | 251.3989 | 300.8865 | 249.3988
947.9417 | 249.9779 | 250.895 | 300.6796 | 249.3329
948.9417 | 249.761 | 250.8211 | 299.6891 | 249.374
949.9417 | 248.7892 | 250.6291 | 299.7143 | 249.3117
950.9417 | 248.8379 | 251.396 | 301.3321 | 250.774
951.9417 | 248.563 | 250.6656 | 302.2452 | 251.7518
952.9417 | 249.3178 | 250.1703 | 302.6528 | 252.2913
953.9417 | 250.2255 | 249.6813 | 301.1673 | 251.8274
954.9417 | 250.3233 | 249.6309 | 301.2496 | 251.8059
955.9417 | 249.8208 | 249.1954 | 300.3829 | 251.9845
956.9417 | 249.7692 | 248.8728 | 298.6783 | 252.3437
957.9417 | 249.0715 | 248.0548 | 297.6916 | 252.1758
958.9417 | 249.4154 | 247.4338 | 295.97 | 251.3928
959.9417 | 249.5619 | 247.5977 | 295.2259 | 250.7924
960.9417 | 250.8769 | 246.7396 | 294.013 | 250.0604
961.9417 | 249.8299 | 246.6148 | 292.7301 | 249.8455
962.9417 | 250.5012 | 247.2239 | 293.7469 | 248.8996
963.9417 | 250.7331 | 247.4135 | 294.418 | 248.6224
964.9417 | 250.9237 | 247.0083 | 293.955 | 248.1658
965.9417 | 251.0222 | 247.6322 | 294.6167 | 247.7752
966.9417 | 251.5188 | 247.5575 | 295.9341 | 248.4791
967.9417 | 252.7982 | 247.2721 | 297.0595 | 247.8926
968.9417 | 252.8969 | 246.4086 | 296.4518 | 247.5703
969.9417 | 252.5748 | 247.0055 | 296.9028 | 248.2172
970.9417 | 252.3135 | 248.7578 | 298.6714 | 250.3595
971.9417 | 252.2542 | 251.7339 | 300.4444 | 250.5069
972.9417 | 252.6443 | 252.1241 | 300.6803 | 251.7689
973.9417 | 252.9073 | 254.0158 | 301.5795 | 252.5484
974.9417 | 254.4364 | 255.5848 | 302.4335 | 256.0282
975.9417 | 254.8813 | 257.2632 | 304.2337 | 256.2313
976.9417 | 254.8355 | 258.0735 | 305.0179 | 256.0959
977.9417 | 253.9855 | 259.0902 | 307.0989 | 259.6651
978.9417 | 253.8298 | 260.1711 | 306.1459 | 261.2815
979.9417 | 254.2922 | 260.3167 | 305.8249 | 261.5091
980.9417 | 254.3854 | 260.049 | 305.7165 | 260.9944
981.9417 | 253.313 | 259.7122 | 304.4712 | 260.8194
982.9417 | 252.7091 | 261.5372 | 306.1002 | 262.6375
983.9417 | 252.2827 | 264.6113 | 307.4051 | 264.6452
984.9417 | 253.5627 | 266.3495 | 308.3332 | 265.0286
985.9417 | 253.5916 | 267.8309 | 308.535 | 265.028
986.9417 | 253.1188 | 268.5599 | 308.2241 | 264.1223
987.9417 | 253.2415 | 267.4933 | 306.9748 | 263.0232
988.9417 | 253.2467 | 267.2328 | 307.4815 | 263.3166
989.9417 | 253.9856 | 266.4622 | 307.3007 | 263.7551
990.9417 | 254.1449 | 265.7301 | 309.0674 | 265.9117
991.9417 | 254.6697 | 265.764 | 309.372 | 265.6724
992.9417 | 254.8824 | 265.5176 | 309.3572 | 265.0094
993.9417 | 254.9058 | 266.1736 | 309.9069 | 264.8654
994.9417 | 255.0314 | 267.2643 | 310.1335 | 265.3482
995.9417 | 256.3195 | 268.2777 | 311.0989 | 265.1619
996.9417 | 257.0045 | 268.2617 | 312.656 | 266.0212
997.9417 | 257.3312 | 268.7821 | 314.4918 | 267.8404
998.9417 | 258.2308 | 268.858 | 315.0602 | 268.3973
999.9417 | 259.799 | 269.7207 | 316.2672 | 270.1248
1000.9417 | 259.8523 | 269.3655 | 315.6184 | 269.8977
1001.9417 | 259.9276 | 268.2568 | 314.9883 | 268.4409
1002.9417 | 259.6241 | 268.5583 | 315.8193 | 267.4791
1003.9417 | 259.3549 | 270.4455 | 317.0373 | 267.8372
1004.9417 | 258.7914 | 270.8606 | 317.387 | 267.2888
1005.9417 | 258.6116 | 272.9407 | 317.4425 | 267.0415
1006.9417 | 258.1778 | 274.3702 | 317.577 | 266.3691
1007.9417 | 257.6627 | 275.0551 | 318.9512 | 265.343
1008.9417 | 257.9537 | 276.1946 | 318.6182 | 265.8723
1009.9417 | 257.5617 | 278.0397 | 319.5108 | 264.7826
1010.9417 | 256.8196 | 278.4702 | 319.6381 | 264.4147
1011.9417 | 256.6128 | 278.9502 | 319.14 | 264.0132
1012.9417 | 256.1155 | 280.1018 | 318.7748 | 265.1108
1013.9417 | 257.6029 | 281.3442 | 321.1267 | 266.1858
1014.9417 | 257.8129 | 282.0985 | 320.8365 | 265.9058
1015.9417 | 256.9904 | 282.3597 | 320.7624 | 265.6137
1016.9417 | 256.9328 | 283.5242 | 320.323 | 265.7089
1017.9417 | 256.4777 | 283.2212 | 319.526 | 265.1993
1018.9417 | 255.9421 | 282.744 | 318.278 | 264.2711
1019.9417 | 256.3793 | 282.3493 | 318.2563 | 263.6664
1020.9417 | 256.3675 | 284.114 | 319.5247 | 264.3917
1021.9417 | 255.4941 | 284.4913 | 321.8212 | 264.9175
1022.9417 | 254.9241 | 284.498 | 321.6411 | 264.2311
1023.9417 | 254.9763 | 284.6935 | 323.7052 | 264.0181
1024.9417 | 254.4229 | 284.441 | 323.0906 | 263.0305
1025.9417 | 254.2228 | 284.1491 | 322.3325 | 262.3828
1026.9417 | 254.3157 | 283.1774 | 321.436 | 262.0315
1027.9417 | 254.4898 | 282.4532 | 321.2045 | 261.4972
1028.9417 | 254.4241 | 282.1405 | 321.1574 | 260.8853
1029.9417 | 253.9549 | 281.6436 | 322.3807 | 260.5117
1030.9417 | 252.9193 | 281.4518 | 321.1047 | 259.8737
1031.9417 | 253.3605 | 280.5843 | 318.8617 | 259.1117
1032.9417 | 253.8295 | 280.3992 | 320.6837 | 259.4057
1033.9417 | 252.9336 | 281.1508 | 320.0248 | 258.6077
1034.9417 | 252.4508 | 281.6072 | 318.9516 | 257.5185
1035.9417 | 252.1884 | 281.5331 | 317.8768 | 256.5037
1036.9417 | 252.627 | 280.9653 | 318.5486 | 256.1913
1037.9417 | 251.9876 | 280.173 | 318.6197 | 255.8647
1038.9417 | 251.4152 | 280.6619 | 319.3677 | 255.5653
1039.9417 | 251.1872 | 281.4942 | 319.0402 | 254.9246
1040.9417 | 250.4389 | 282.5712 | 317.5682 | 254.1837
1041.9417 | 250.5332 | 282.8708 | 318.2588 | 253.8436
1042.9417 | 249.6471 | 282.4869 | 317.9823 | 253.5574
1043.9417 | 249.274 | 282.5733 | 318.3441 | 253.2502
1044.9417 | 249.7539 | 282.8195 | 319.2317 | 253.1206
1045.9417 | 251.1254 | 283.137 | 320.6193 | 253.8949
1046.9417 | 251.0571 | 283.5438 | 321.4939 | 254.5171
1047.9417 | 251.0518 | 282.7753 | 322.5626 | 254.851
1048.9417 | 251.1734 | 283.6753 | 322.9818 | 254.6326
1049.9417 | 251.5236 | 283.872 | 324.6217 | 255.4599
1050.9417 | 252.7928 | 284.0997 | 325.5916 | 257.1026
1051.9417 | 252.5082 | 284.2334 | 326.1395 | 256.8765
1052.9417 | 252.881 | 284.8437 | 325.1493 | 257.3017
1053.9417 | 253.4552 | 285.2271 | 324.5451 | 257.4773
1054.9417 | 253.6595 | 285.2414 | 324.3642 | 258.1181
1055.9417 | 253.9935 | 285.1989 | 324.2677 | 257.6449
1056.9417 | 254.0241 | 286.0287 | 324.9462 | 259.8979
1057.9417 | 254.8909 | 287.0262 | 327.5725 | 261.8524
1058.9417 | 255.0816 | 287.3242 | 326.429 | 261.4372
1059.9417 | 255.2131 | 286.9078 | 325.5635 | 261.3842
1060.9417 | 255.9518 | 286.7745 | 325.5171 | 262.1871
1061.9417 | 255.4236 | 286.4055 | 326.2328 | 263.0279
1062.9417 | 255.2121 | 288.0328 | 325.6181 | 262.5074
1063.9417 | 256.5797 | 287.3634 | 325.349 | 263.3365
1064.9417 | 256.7843 | 287.4663 | 325.3669 | 265.6327
1065.9417 | 256.5331 | 287.1665 | 325.3247 | 265.1415
1066.9417 | 256.752 | 287.2342 | 325.2674 | 265.1252
1067.9417 | 256.3952 | 287.2229 | 325.4964 | 264.3056
1068.9417 | 256.8077 | 287.2896 | 326.577 | 263.8849
1069.9417 | 256.2279 | 287.0415 | 326.8669 | 264.2878
1070.9417 | 256.7295 | 286.7443 | 327.1237 | 264.9208
1071.9417 | 257.017 | 287.8515 | 328.1068 | 265.3595
1072.9417 | 257.6687 | 287.4841 | 328.4368 | 266.1156
1073.9573 | 257.6863 | 287.4147 | 328.198 | 265.8742
1074.9417 | 257.5723 | 287.4889 | 329.1908 | 265.4554
1075.9417 | 257.7054 | 286.7305 | 330.7458 | 265.9996
1076.9417 | 256.7889 | 285.8574 | 330.7423 | 265.7207
1077.9417 | 256.2925 | 286.343 | 329.9511 | 265.1585
1078.9417 | 256.1775 | 287.2519 | 329.4328 | 264.1232
1079.9573 | 255.5214 | 288.1363 | 328.5806 | 263.2922
1080.9417 | 254.718 | 287.5171 | 326.1667 | 262.1438
1081.9417 | 254.562 | 288.5435 | 326.2817 | 262.1131
1082.9417 | 254.4099 | 289.2419 | 325.3259 | 261.6107
1083.9417 | 254.3271 | 290.2278 | 325.4383 | 260.8889
1084.9417 | 253.8251 | 290.6417 | 324.8634 | 260.2236
1085.9417 | 254.5643 | 290.4532 | 324.9513 | 260.1548
1086.9417 | 254.6412 | 291.6482 | 325.0229 | 259.9916
1087.9417 | 253.8729 | 292.2115 | 322.9183 | 259.3139
1088.9417 | 253.395 | 292.0943 | 321.5548 | 258.5323
1089.9417 | 252.6561 | 292.9495 | 321.6771 | 258.0322
1090.9417 | 252.8343 | 294.3377 | 322.552 | 258.6358
1091.9417 | 254.8805 | 295.4138 | 324.1948 | 259.4112
1092.9417 | 255.6389 | 297.1944 | 325.5955 | 259.0132
1093.9417 | 255.9824 | 297.5953 | 326.1956 | 258.1965
1094.9417 | 255.8116 | 298.4913 | 325.876 | 258.3107
1095.9417 | 255.796 | 299.5739 | 325.5141 | 258.4452
1096.9417 | 255.6041 | 298.6273 | 325.2394 | 258.7689
1097.9417 | 255.1752 | 298.3938 | 324.5076 | 257.8649
1098.9417 | 255.8518 | 298.4146 | 323.9211 | 257.9249
1099.9417 | 256.8694 | 298.1741 | 323.4874 | 259.1972
1100.9417 | 257.2799 | 298.0903 | 324.2014 | 258.3993
1101.9417 | 257.8651 | 297.2889 | 324.2254 | 258.6255
1102.9417 | 259.0798 | 296.2355 | 325.3358 | 259.0667
1103.9417 | 259.5108 | 296.7308 | 325.6586 | 260.5257
1104.9417 | 260.5233 | 296.3527 | 326.5203 | 261.7451
1105.9417 | 260.115 | 296.2888 | 327.046 | 262.0695
1106.9417 | 260.1186 | 296.1895 | 325.6547 | 261.798
1107.9417 | 259.972 | 297.2145 | 325.4269 | 261.7625
1108.9417 | 259.6403 | 297.9624 | 325.5146 | 261.6498
1109.9417 | 258.8388 | 298.55 | 324.3692 | 260.9035
1110.9417 | 258.4805 | 298.4863 | 324.1392 | 260.2167
1111.9417 | 258.7719 | 297.8458 | 325.3203 | 261.1536
1112.9417 | 259.4118 | 296.5632 | 325.285 | 261.2522
1113.9417 | 259.7463 | 295.3813 | 324.6927 | 261.6943
1114.9417 | 260.7163 | 295.9475 | 325.4094 | 263.7898
1115.9417 | 261.2488 | 295.5927 | 324.9493 | 264.7164
1116.9417 | 261.215 | 294.538 | 325.4288 | 264.1508
1117.9417 | 262.7978 | 295.1109 | 326.7615 | 265.1932
1118.9417 | 262.9409 | 296.3389 | 327.398 | 266.593
1119.9417 | 263.1593 | 296.7289 | 328.0595 | 266.1802
1120.9417 | 263.154 | 296.7003 | 327.9991 | 266.1176
1121.9417 | 262.496 | 296.7412 | 328.4582 | 266.3852
1122.9417 | 261.9759 | 297.6615 | 329.2672 | 266.8332
1123.9417 | 261.9543 | 297.8126 | 329.3583 | 267.2384
1124.9417 | 261.9823 | 298.3618 | 329.1646 | 268.8285
1125.9417 | 262.2877 | 298.1194 | 329.1578 | 268.8071
1126.9417 | 262.1822 | 297.8128 | 328.9583 | 268.6232
1127.9417 | 262.5253 | 298.5788 | 329.4546 | 270.3692
1128.9417 | 262.8532 | 300.3239 | 330.4339 | 272.5328
1129.9417 | 263.2635 | 300.4608 | 330.7457 | 271.595
1130.9417 | 263.309 | 300.731 | 329.9715 | 271.0576
1131.9417 | 264.2771 | 301.3314 | 329.9341 | 271.7943
1132.9417 | 264.3795 | 301.9904 | 330.1801 | 271.2415
1133.9417 | 263.9167 | 301.0759 | 330.808 | 270.2612
1134.9417 | 263.6552 | 301.7854 | 329.5746 | 269.7745
1135.9417 | 263.9285 | 301.8463 | 328.7306 | 269.5632
1136.9417 | 263.4082 | 301.9196 | 328.903 | 269.2808
1137.9417 | 262.91 | 301.5458 | 328.0219 | 268.231
1138.9417 | 263.0691 | 303.0768 | 329.4198 | 267.9103
1139.9417 | 263.0807 | 301.9972 | 328.9145 | 267.306
1140.9417 | 262.9818 | 302.4766 | 328.3126 | 266.4284
1141.9417 | 263.2346 | 302.1083 | 328.5255 | 266.2312
1142.9417 | 263.9936 | 301.4855 | 328.4458 | 267.9419
1143.9417 | 263.9267 | 303.0712 | 329.6417 | 272.8065
1144.9417 | 265.5065 | 303.7149 | 330.1043 | 275.2894
1145.9417 | 266.2708 | 303.4007 | 329.3545 | 275.6553
1146.9417 | 266.4579 | 302.8789 | 327.8056 | 274.2741
1147.9417 | 265.4014 | 302.3524 | 327.3061 | 273.6819
1148.9417 | 264.9391 | 302.3361 | 326.7304 | 273.3039
1149.9417 | 265.5405 | 302.6197 | 327.7482 | 273.7162
1150.9417 | 265.9437 | 301.2931 | 327.5609 | 275.0349
1151.9417 | 265.6157 | 300.7481 | 326.78 | 274.1396
1152.9417 | 264.8961 | 301.1486 | 328.2727 | 274.6083
1153.9417 | 264.6649 | 300.9602 | 328.465 | 276.0891
1154.9417 | 265.0334 | 299.7881 | 330.1023 | 277.2534
1155.9417 | 265.3318 | 300.2694 | 329.9116 | 276.4048
1156.9417 | 265.9788 | 300.539 | 331.746 | 278.432
1157.9417 | 266.6777 | 301.3434 | 332.6021 | 278.6426
1158.9417 | 266.5558 | 303.419 | 332.8962 | 278.3012
1159.9417 | 266.9955 | 303.3205 | 333.2135 | 277.7932
1160.9417 | 267.165 | 304.415 | 333.8163 | 277.8957
1161.9417 | 267.193 | 303.7642 | 333.9047 | 277.6028
1162.9417 | 267.2406 | 302.8025 | 332.7566 | 278.1819
1163.9417 | 266.7151 | 302.8517 | 331.5775 | 278.0882
1164.9417 | 267.7039 | 302.4079 | 330.6059 | 277.5916
1165.9417 | 266.4454 | 302.6134 | 330.4371 | 278.8054
1166.9417 | 266.4474 | 301.6112 | 329.6649 | 277.8644
1167.9417 | 266.6246 | 300.7164 | 329.9262 | 277.5813
1168.9417 | 266.5914 | 301.1397 | 330.2704 | 276.9967
1169.9417 | 267.4606 | 300.9976 | 330.0888 | 277.0231
1170.9417 | 268.0167 | 302.0184 | 331.4275 | 278.9485
1171.9417 | 267.1546 | 302.0621 | 331.8423 | 278.9023
1172.9417 | 267.0162 | 301.346 | 331.7161 | 278.3637
1173.9417 | 267.2279 | 302.1685 | 332.7957 | 279.0227
1174.9417 | 266.3962 | 301.6165 | 333.6481 | 278.86
1175.9417 | 266.4066 | 301.7263 | 333.4908 | 278.615
1176.9417 | 266.6241 | 302.2732 | 334.3124 | 278.4236
1177.9417 | 266.6255 | 302.7549 | 334.6615 | 277.9373
1178.9417 | 268.7443 | 302.2272 | 336.6888 | 277.955
1179.9417 | 268.6684 | 301.5437 | 337.1383 | 278.288
1180.9417 | 268.9194 | 302.327 | 337.8394 | 278.6198
1181.9417 | 268.8037 | 301.3994 | 337.9855 | 278.4988
1182.9417 | 268.8784 | 301.1115 | 338.4535 | 277.737
1183.9417 | 269.2212 | 302.7275 | 338.9508 | 276.9659
1184.9417 | 269.577 | 303.6722 | 338.5847 | 277.0231
1185.9417 | 269.6783 | 304.1082 | 338.6435 | 277.914
1186.9417 | 269.2907 | 304.872 | 338.1893 | 279.0009
1187.9417 | 269.1854 | 304.9426 | 337.7177 | 280.1612
1188.9417 | 269.338 | 306.3633 | 337.6676 | 279.8845
1189.9417 | 269.7383 | 306.1798 | 337.0813 | 280.495
1190.9417 | 270.8534 | 306.1384 | 337.445 | 282.5222
1191.9417 | 271.4008 | 306.0196 | 338.9058 | 285.08
1192.9417 | 272.0024 | 304.8723 | 338.047 | 284.1009
1193.9417 | 270.7698 | 305.0169 | 337.3743 | 283.7039
1194.9417 | 271.2629 | 304.3787 | 337.2468 | 283.6652
1195.9417 | 272.206 | 304.303 | 336.7823 | 284.7285
1196.9417 | 272.2482 | 305.3569 | 337.7378 | 285.8878
1197.9417 | 272.0941 | 305.2717 | 337.7459 | 288.1005
1198.9417 | 273.1731 | 304.9241 | 336.4401 | 287.1713
1199.9417 | 273.3675 | 304.2219 | 337.0393 | 286.3577
1200.9417 | 275.2387 | 304.2771 | 338.0605 | 285.1651
1201.9417 | 274.5186 | 303.599 | 336.097 | 284.2307
1202.9417 | 274.2896 | 302.4688 | 334.613 | 282.8863
1203.9417 | 274.3145 | 302.2057 | 333.3627 | 281.9027
1204.9417 | 273.4664 | 301.1953 | 333.9523 | 280.9164
1205.9417 | 273.6937 | 302.4378 | 334.8454 | 280.3568
1206.9417 | 274.3623 | 301.7405 | 334.2849 | 280.3333
1207.9417 | 275.0203 | 301.2344 | 333.7282 | 279.0928
1208.9417 | 276.6415 | 300.9683 | 334.6367 | 278.6378
1209.9417 | 277.7709 | 299.71 | 332.3297 | 277.2843
1210.9417 | 277.0765 | 298.755 | 331.8596 | 276.3298
1211.9417 | 278.0371 | 297.5223 | 332.2677 | 275.5716
1212.9417 | 277.4588 | 296.5571 | 331.1071 | 274.8053
1213.9417 | 276.9239 | 295.7446 | 330.7505 | 274.8868
1214.9417 | 277.4201 | 294.9677 | 330.5628 | 274.7428
1215.9417 | 277.5715 | 294.0658 | 330.0741 | 274.8322
1216.9417 | 278.5587 | 293.8313 | 330.7492 | 276.111
1217.9417 | 279.105 | 293.4195 | 332.4857 | 275.8247
1218.9417 | 279.5702 | 293.5464 | 332.6207 | 275.2109
1219.9417 | 279.9699 | 293.2477 | 333.3154 | 276.3968
1220.9417 | 279.1939 | 293.9684 | 333.9056 | 277.0857
1221.9417 | 279.3632 | 294.9435 | 334.5461 | 277.8616
1222.9417 | 280.1318 | 294.6826 | 335.8408 | 280.4584
1223.9417 | 280.1048 | 294.4705 | 336.0759 | 281.7626
1224.9417 | 281.1538 | 296.2172 | 337.3592 | 285.7664
1225.9417 | 280.4185 | 295.2257 | 337.4574 | 286.5538
1226.9417 | 279.6027 | 296.0462 | 337.4873 | 287.874
1227.9417 | 279.3826 | 296.5816 | 338.2317 | 287.1596
1228.9417 | 279.2106 | 297.3649 | 339.2857 | 285.845
1229.9417 | 278.7801 | 298.1399 | 339.3838 | 285.9947
1230.9417 | 278.6013 | 298.6805 | 339.3862 | 287.1488
1231.9417 | 277.8338 | 298.3978 | 340.3262 | 287.1067
1232.9417 | 278.0583 | 298.5518 | 340.1057 | 285.6807
1233.9417 | 278.7783 | 300.5227 | 339.9518 | 285.8071
1234.9417 | 277.988 | 301.0547 | 340.205 | 285.997
1235.9417 | 277.4482 | 301.1271 | 339.1102 | 284.9396
1236.9417 | 276.3098 | 302.3084 | 338.9299 | 286.1994
1237.9417 | 275.8361 | 303.2578 | 338.8589 | 286.2102
1238.9417 | 275.8336 | 303.5479 | 339.4312 | 287.2865
1239.9417 | 274.8138 | 302.963 | 340.8244 | 286.4767
1240.9417 | 274.2794 | 302.3979 | 339.943 | 285.1824
1241.9417 | 274.2972 | 302.3251 | 338.3828 | 283.6639
1242.9417 | 274.1451 | 301.0323 | 337.0837 | 282.4569
1243.9417 | 274.2813 | 299.8785 | 336.3973 | 281.1254
1244.9417 | 275.2182 | 300.4028 | 337.4809 | 281.2089
1245.9417 | 275.4965 | 299.6464 | 337.8313 | 282.8804
1246.9417 | 276.156 | 299.5129 | 337.7283 | 281.9411
1247.9417 | 276.3043 | 300.2725 | 338.1475 | 281.4068
1248.9417 | 276.4105 | 299.0163 | 338.5226 | 282.109
1249.9417 | 277.079 | 299.4603 | 338.4586 | 281.3029
1250.9417 | 277.4739 | 299.3879 | 338.5923 | 280.9571
1251.9417 | 277.8018 | 299.2299 | 338.8613 | 282.1505
1252.9417 | 278.3158 | 298.8451 | 338.662 | 283.1426
1253.9417 | 277.4273 | 298.1511 | 339.3949 | 283.7395
1254.9417 | 278.4054 | 297.865 | 339.9714 | 283.5474
1255.9417 | 277.3866 | 297.9624 | 340.0658 | 283.2603
1256.9417 | 277.6725 | 298.9475 | 341.1183 | 283.2315
1257.9417 | 277.5126 | 299.4737 | 341.0985 | 282.5446
1258.9417 | 277.3962 | 299.517 | 341.3624 | 281.6245
1259.9417 | 278.5431 | 299.6159 | 341.9484 | 281.18
1260.9417 | 278.7866 | 300.7248 | 342.4852 | 281.5984
1261.9417 | 278.4793 | 300.9396 | 342.9503 | 280.8474
1262.9417 | 278.8405 | 300.5331 | 343.1984 | 281.8189
1263.9417 | 278.5219 | 299.7165 | 343.3656 | 282.1061
1264.9417 | 278.8298 | 300.3757 | 343.8085 | 282.0179
1265.9417 | 277.8303 | 298.9948 | 342.8137 | 281.134
1266.9417 | 277.9666 | 298.8739 | 342.2955 | 280.7776
1267.9417 | 278.2699 | 299.5782 | 342.7246 | 282.9693
1268.9417 | 278.4909 | 299.0439 | 342.9795 | 284.3343
1269.9417 | 278.7132 | 298.3099 | 341.5587 | 284.1924
1270.9417 | 279.1194 | 297.1603 | 341.3158 | 284.1037
1271.9417 | 278.6534 | 296.0587 | 341.8114 | 284.034
1272.9417 | 277.8386 | 295.3203 | 342.1069 | 284.1245
1273.9417 | 277.0403 | 295.4257 | 341.756 | 282.852
1274.9417 | 276.2543 | 296.009 | 340.505 | 281.6986
1275.9417 | 276.7205 | 296.5958 | 340.5769 | 281.0376
1276.9417 | 276.3482 | 296.7093 | 340.6313 | 280.9182
1277.9417 | 276.4272 | 297.6366 | 339.9764 | 280.634
1278.9417 | 276.0868 | 297.8041 | 340.8165 | 280.3847
1279.9417 | 276.5286 | 298.4497 | 341.0037 | 279.436
1280.9417 | 276.2738 | 297.8378 | 340.081 | 278.4484
1281.9417 | 276.1684 | 298.6593 | 340.6184 | 277.8009
1282.9417 | 275.0041 | 300.7681 | 340.3309 | 276.8542
1283.9417 | 273.8282 | 301.5977 | 340.4124 | 275.9651
1284.9417 | 273.4376 | 301.3381 | 339.5432 | 276.5493
1285.9417 | 273.0345 | 300.8829 | 337.9028 | 275.7312
1286.9417 | 272.7927 | 301.1066 | 336.9984 | 274.3777
1287.9417 | 272.6491 | 301.5063 | 336.7207 | 274.1638
1288.9417 | 271.4787 | 301.2477 | 335.1612 | 274.005
1289.9417 | 271.0431 | 300.6284 | 332.8385 | 273.0502
1290.9417 | 271.4783 | 300.8872 | 330.7552 | 272.1347
1291.9417 | 270.9071 | 299.8617 | 328.5922 | 271.448
1292.9417 | 270.6046 | 299.5449 | 327.4484 | 273.3472
1293.9417 | 270.7211 | 299.0169 | 327.6864 | 272.7117
1294.9417 | 270.8121 | 300.1879 | 328.2295 | 273.5894
1295.9417 | 271.0784 | 300.3907 | 328.6643 | 273.0928
1296.9417 | 270.8735 | 300.6517 | 327.7459 | 272.404
1297.9417 | 271.5827 | 300.9687 | 327.9826 | 272.1138
1298.9417 | 272.7165 | 302.0907 | 330.5563 | 273.6104
1299.9417 | 273.2719 | 302.6294 | 332.981 | 275.629
1300.9417 | 273.0554 | 301.9912 | 334.2363 | 276.1287
1301.9417 | 272.8486 | 301.8246 | 333.791 | 275.8642
1302.9417 | 273.2929 | 302.6261 | 334.0207 | 275.4059
1303.9417 | 273.1688 | 302.5121 | 335.2262 | 275.5108
1304.9417 | 273.0512 | 302.3582 | 334.8324 | 274.7034
1305.9417 | 272.9916 | 302.5259 | 334.9997 | 274.78
1306.9417 | 272.5443 | 303.2145 | 335.1097 | 274.8228
1307.9417 | 272.2558 | 303.4553 | 334.2818 | 275.0397
1308.9417 | 271.6769 | 303.1594 | 334.2497 | 274.3396
1309.9417 | 270.9934 | 301.9733 | 332.6728 | 273.9272
1310.9417 | 270.3941 | 302.1154 | 331.5203 | 273.5078
1311.9417 | 269.6595 | 301.7079 | 331.0633 | 272.8823
1312.9417 | 269.2921 | 301.5863 | 329.9262 | 272.5671
1313.9417 | 268.2506 | 301.8516 | 328.5157 | 271.4084
1314.9417 | 267.582 | 301.4237 | 327.4123 | 270.5902
1315.9417 | 267.1213 | 301.8681 | 327.6836 | 270.5425
1316.9417 | 266.6829 | 301.7848 | 328.1238 | 270.5412
1317.9417 | 266.9898 | 303.0277 | 329.8281 | 270.3481
1318.9417 | 267.0603 | 304.2071 | 330.5077 | 270.5227
1319.9417 | 267.5136 | 303.6032 | 329.6206 | 271.0712
1320.9417 | 267.7679 | 302.5338 | 328.7587 | 270.5234
1321.9417 | 268.2986 | 301.6388 | 329.5839 | 272.1623
1322.9417 | 268.9083 | 301.3822 | 330.2653 | 273.1206
1323.9417 | 270.2134 | 302.4901 | 332.5884 | 275.6424
1324.9417 | 269.9686 | 302.0932 | 333.2123 | 274.9591
1325.9417 | 270.0334 | 304.4045 | 334.965 | 275.5641
1326.9417 | 270.0617 | 304.8469 | 335.8874 | 276.5226
1327.9417 | 270.924 | 305.0112 | 335.7517 | 275.6453
1328.9417 | 270.6072 | 305.3195 | 334.3784 | 275.6069
1329.9417 | 271.935 | 306.0289 | 334.0773 | 275.2237
1330.9417 | 273.2645 | 306.7803 | 334.0681 | 275.741
1331.9417 | 274.9332 | 306.815 | 334.3965 | 276.016
1332.9417 | 276.2654 | 307.3993 | 335.033 | 277.711
1333.9417 | 277.3181 | 307.6923 | 335.9466 | 279.4338
1334.9417 | 278.0195 | 307.7208 | 337.4147 | 280.5485
1335.9417 | 278.5391 | 307.1165 | 338.0092 | 281.7937
1336.9417 | 278.5717 | 307.2474 | 337.6017 | 282.5671
1337.9417 | 278.6625 | 307.5063 | 337.9107 | 282.2121
1338.9417 | 279.5078 | 306.927 | 338.7268 | 281.9647
1339.9417 | 278.8958 | 307.5779 | 338.6274 | 280.6813
1340.9417 | 278.2314 | 307.5519 | 338.7222 | 280.1322
1341.9417 | 277.6112 | 307.8655 | 339.3824 | 279.7016
1342.9417 | 276.9458 | 308.4744 | 339.6815 | 279.7955
1343.9417 | 277.3645 | 309.1068 | 339.27 | 279.6983
1344.9417 | 276.824 | 309.3103 | 338.1243 | 279.4258
1345.9417 | 276.582 | 310.0368 | 337.9597 | 278.7479
1346.9417 | 276.5981 | 311.7084 | 337.6958 | 278.498
1347.9417 | 276.2508 | 311.1128 | 336.9968 | 277.4309
1348.9417 | 275.6821 | 311.1472 | 335.8818 | 277.3619
1349.9417 | 275.8712 | 310.8135 | 335.2597 | 276.961
1350.9417 | 275.5578 | 310.2181 | 334.8072 | 276.4471
1351.9417 | 275.2509 | 309.9935 | 334.6231 | 275.6872
1352.9417 | 274.6624 | 311.6128 | 335.467 | 277.2652
1353.9417 | 274.8621 | 312.0519 | 335.4297 | 277.5438
1354.9417 | 275.4553 | 312.5222 | 334.99 | 277.7305
1355.9417 | 276.5031 | 311.6557 | 333.2898 | 276.7622
1356.9417 | 277.4134 | 310.6687 | 332.5627 | 276.0343
1357.9417 | 277.5165 | 309.6916 | 333.0983 | 276.6135
1358.9417 | 276.6143 | 310.8874 | 334.692 | 276.5979
1359.9417 | 277.4244 | 310.7347 | 335.3565 | 277.0314
1360.9417 | 276.9034 | 310.7316 | 335.4855 | 276.8722
1361.9417 | 276.7473 | 310.6742 | 335.5085 | 276.8249
1362.9417 | 277.0547 | 311.7584 | 335.8001 | 277.4882
1363.9417 | 277.3302 | 311.4161 | 336.1079 | 278.1818
1364.9417 | 276.8106 | 310.7347 | 337.8215 | 278.1711
1365.9417 | 275.6259 | 311.318 | 338.5276 | 278.0934
1366.9417 | 275.573 | 310.7172 | 338.5352 | 278.3585
1367.9417 | 275.577 | 310.0788 | 338.3426 | 278.597
1368.9417 | 275.8554 | 309.8997 | 339.8701 | 278.2008
1369.9417 | 276.9169 | 309.8712 | 341.1727 | 278.8794
1370.9417 | 277.0927 | 309.6148 | 343.5164 | 279.5912
1371.9417 | 277.5335 | 309.432 | 343.4427 | 278.8277
1372.9417 | 277.9752 | 310.0589 | 343.8833 | 278.1204
1373.9417 | 278.5725 | 310.7688 | 345.4259 | 278.1112
1374.9417 | 279.2977 | 310.2967 | 345.7164 | 278.8883
1375.9417 | 279.3102 | 311.0884 | 347.7152 | 279.7255
1376.9417 | 278.8833 | 311.5387 | 346.1224 | 278.7727
1377.9417 | 278.1231 | 312.8388 | 345.1848 | 278.0981
1378.9417 | 277.1623 | 314.1968 | 345.3545 | 277.7654
1379.9417 | 277.0867 | 314.4934 | 344.8948 | 277.6748
1380.9417 | 276.808 | 314.7107 | 345.0203 | 277.0941
1381.9417 | 276.3785 | 314.7562 | 343.0668 | 276.383
1382.9417 | 276.0855 | 314.8214 | 341.7768 | 275.5554
1383.9417 | 276.4082 | 314.9762 | 341.389 | 275.2372
1384.9417 | 276.1397 | 314.591 | 341.3579 | 275.4194
1385.9417 | 275.6825 | 314.9535 | 340.8572 | 275.8553
1386.9417 | 275.1983 | 314.227 | 339.4705 | 275.3012
1387.9417 | 275.1181 | 313.8289 | 339.841 | 276.082
1388.9417 | 274.4746 | 314.5587 | 339.8401 | 276.1323
1389.9417 | 274.7279 | 315.3238 | 339.9358 | 275.8773
1390.9417 | 274.9469 | 315.6202 | 338.3663 | 275.1182
1391.9417 | 274.8737 | 314.8989 | 337.2359 | 274.8615
1392.9417 | 274.8794 | 313.6905 | 336.8095 | 274.4429
1393.9417 | 275.0148 | 313.2941 | 336.8366 | 274.214
1394.9417 | 275.6093 | 313.4787 | 336.9332 | 275.038
1395.9417 | 275.8089 | 312.8208 | 337.4955 | 275.3233
1396.9417 | 275.6108 | 312.5817 | 337.4034 | 275.3544
1397.9417 | 275.0504 | 311.6762 | 336.6686 | 275.3438
1398.9417 | 274.6837 | 311.8164 | 336.7598 | 275.9277
1399.9417 | 275.3095 | 312.9316 | 336.2874 | 276.1013
1400.9417 | 275.1386 | 313.7878 | 336.6235 | 276.1714
1401.9417 | 275.102 | 313.8213 | 337.5899 | 276.271
1402.9417 | 275.3082 | 314.4453 | 338.0439 | 276.4228
1403.9417 | 275.4809 | 314.7608 | 337.3457 | 276.54
1404.9417 | 275.3119 | 313.8216 | 335.9698 | 276.5923
1405.9417 | 275.1102 | 313.2505 | 335.0195 | 276.7977
1406.9417 | 274.9479 | 313.4691 | 335.4876 | 278.2627
1407.9417 | 275.0679 | 313.8554 | 335.0042 | 279.8954
1408.9417 | 275.3417 | 314.091 | 334.9111 | 279.491
1409.9417 | 275.5257 | 313.2793 | 335.1096 | 279.3553
1410.9417 | 276.2331 | 313.1345 | 336.4237 | 279.6361
1411.9417 | 277.3905 | 314.5441 | 338.4892 | 281.3129
1412.9417 | 277.8788 | 313.3968 | 338.3213 | 282.3417
1413.9417 | 278.1224 | 313.3906 | 338.3481 | 282.4822
1414.9417 | 278.1801 | 313.8021 | 339.1705 | 282.8375
1415.9417 | 278.8415 | 313.4294 | 338.9243 | 282.6844
1416.9417 | 278.2593 | 312.5883 | 339.6116 | 282.0778
1417.9417 | 278.0169 | 312.2648 | 339.3169 | 281.3087
1418.9417 | 277.8163 | 312.0993 | 339.5393 | 280.9014
1419.9417 | 277.3446 | 311.8771 | 339.1248 | 280.2537
1420.9417 | 277.3386 | 312.4421 | 339.0406 | 279.9853
1421.9417 | 277.566 | 312.992 | 339.5516 | 279.7871
1422.9417 | 277.7252 | 313.2496 | 338.551 | 279.3498
1423.9417 | 278.1882 | 313.5036 | 339.9911 | 279.2358
1424.9417 | 277.8952 | 313.9987 | 339.8763 | 278.5747
1425.9417 | 278.0121 | 313.8507 | 340.4594 | 278.0047
1426.9417 | 278.364 | 315.6859 | 340.8121 | 278.22
1427.9417 | 278.317 | 315.8912 | 341.9855 | 278.6983
1428.9417 | 278.0421 | 315.644 | 340.8573 | 278.143
1429.9417 | 278.0974 | 316.251 | 340.8359 | 278.8184
1430.9417 | 278.4326 | 317.9195 | 342.1539 | 279.6147
1431.9417 | 278.7454 | 320.7091 | 343.4337 | 280.3726
1432.9417 | 278.9108 | 321.3331 | 344.9571 | 281.3535
1433.9417 | 279.247 | 322.481 | 344.6495 | 280.9157
1434.9417 | 280.2269 | 324.1999 | 344.4209 | 280.8114
1435.9417 | 280.7396 | 323.5536 | 344.4242 | 281.2469
1436.9417 | 280.8941 | 324.1123 | 345.1578 | 283.4328
1437.9417 | 282.2009 | 323.3379 | 346.0622 | 286.5184
1438.9417 | 282.3057 | 323.0737 | 346.4592 | 289.5261
1439.9417 | 282.679 | 322.1558 | 345.9524 | 289.3675
1440.9417 | 282.4296 | 320.8659 | 346.44 | 288.9067
1441.9417 | 282.6527 | 320.5398 | 345.6483 | 288.2492
1442.9417 | 282.4125 | 320.9414 | 346.5053 | 288.0058
1443.9417 | 282.5792 | 320.4485 | 347.3747 | 287.7025
1444.9417 | 283.3114 | 320.9864 | 348.0816 | 287.4709
1445.9417 | 282.9706 | 321.3649 | 349.0935 | 286.8042
1446.9417 | 282.3523 | 321.6379 | 349.5699 | 286.3519
1447.9417 | 282.2976 | 321.0838 | 349.8017 | 285.986
1448.9417 | 281.1541 | 321.5552 | 349.0142 | 285.3541
1449.9417 | 280.8579 | 321.6464 | 348.1906 | 284.5419
1450.9417 | 280.7108 | 321.1309 | 348.3581 | 284.0407
1451.9417 | 280.8326 | 321.3107 | 348.5301 | 283.628
1452.9417 | 280.9151 | 322.4973 | 349.0556 | 283.291
1453.9417 | 280.6608 | 322.5796 | 348.6288 | 282.8512
1454.9417 | 281.0096 | 322.8668 | 348.3621 | 282.5162
1455.9417 | 281.1981 | 322.8323 | 349.9633 | 282.9444
1456.9417 | 281.7312 | 322.2866 | 349.6679 | 282.4199
1457.9417 | 281.6968 | 321.8354 | 349.5077 | 282.3383
1458.9417 | 282.2061 | 321.2279 | 349.7461 | 282.2226
1459.9417 | 282.2753 | 320.6309 | 349.7659 | 282.181
1460.9417 | 282.0776 | 321.104 | 349.9665 | 282.7406
1461.9417 | 282.387 | 320.8274 | 352.3457 | 284.5539
1462.9417 | 282.4627 | 321.3604 | 353.5264 | 284.9375
1463.9417 | 282.6217 | 321.5646 | 353.3775 | 284.5855
1464.9417 | 282.3927 | 322.2081 | 353.0622 | 284.0889
1465.9417 | 282.6865 | 323.0153 | 351.8654 | 283.355
1466.9417 | 282.4127 | 323.3295 | 350.3898 | 282.814
1467.9417 | 282.6067 | 323.3793 | 349.2627 | 282.5962
1468.9417 | 283.2335 | 323.016 | 348.6365 | 282.7466
1469.9417 | 283.9541 | 322.6962 | 348.0539 | 284.1207
1470.9417 | 284.6009 | 323.2304 | 348.4579 | 286.3685
1471.9417 | 286.5438 | 324.1553 | 350.7709 | 286.8238
1472.9417 | 286.6252 | 323.0496 | 351.1886 | 286.0877
1473.9417 | 286.0892 | 323.5367 | 351.5008 | 286.2977
1474.9417 | 286.9755 | 323.3581 | 351.4984 | 286.817
1475.9417 | 286.7273 | 323.9479 | 351.5213 | 286.5433
1476.9417 | 287.1452 | 325.3312 | 351.7392 | 287.3288
1477.9417 | 287.6212 | 326.0242 | 351.7692 | 288.5915
1478.9417 | 287.7985 | 325.8393 | 352.055 | 289.0807
1479.9417 | 288.5839 | 326.1801 | 352.8671 | 289.5431
1480.9417 | 289.3371 | 325.5268 | 353.0854 | 290.0974
1481.9417 | 289.6274 | 325.2 | 353.2863 | 290.2553
1482.9417 | 289.1781 | 325.9589 | 354.2182 | 289.9102
1483.9417 | 288.5249 | 326.7929 | 354.1052 | 291.3095
1484.9417 | 288.5038 | 327.4343 | 352.9204 | 291.6962
1485.9417 | 289.7716 | 327.9749 | 353.0554 | 292.9844
1486.9417 | 289.9268 | 328.4204 | 353.5767 | 292.623
1487.9417 | 289.1499 | 328.7863 | 353.6963 | 292.7518
1488.9417 | 289.3131 | 328.7872 | 352.2264 | 292.3732
1489.9417 | 288.142 | 327.4624 | 351.189 | 291.6097
1490.9417 | 288.1922 | 327.3898 | 350.7198 | 291.8371
1491.9417 | 288.6673 | 327.6458 | 351.1406 | 291.7135
1492.9417 | 289.1321 | 328.0468 | 352.3094 | 291.8804
1493.9417 | 289.1891 | 328.072 | 352.0191 | 291.7937
1494.9417 | 288.4856 | 327.2744 | 350.9203 | 291.7137
1495.9417 | 288.5116 | 326.2818 | 351.0179 | 291.9064
1496.9417 | 289.3723 | 327.682 | 352.0891 | 292.899
1497.9417 | 289.8384 | 328.8472 | 352.3139 | 293.5557
1498.9417 | 290.2834 | 329.7277 | 353.1598 | 293.2539
1499.9417 | 289.9433 | 330.0132 | 352.6048 | 293.0983
1500.9417 | 291.0028 | 331.1127 | 353.5515 | 294.5199
1501.9417 | 290.2863 | 332.6393 | 355.0835 | 294.6653
1502.9417 | 289.8202 | 332.6179 | 354.9677 | 293.6871
1503.9417 | 290.8602 | 333.103 | 354.9617 | 293.0299
1504.9417 | 292.1348 | 334.0207 | 357.1651 | 294.3323
1505.9417 | 293.247 | 334.8797 | 359.1519 | 295.1002
1506.9417 | 294.1952 | 336.6412 | 360.8491 | 297.1845
1507.9417 | 295.5462 | 336.2893 | 361.04 | 296.6238
1508.9417 | 296.6749 | 337.0033 | 361.5707 | 296.7947
1509.9417 | 297.4932 | 337.16 | 362.9105 | 296.7065
1510.9417 | 298.8246 | 337.9121 | 363.2792 | 297.3699
1511.9417 | 301.1826 | 338.9375 | 364.8371 | 298.7628
1512.9417 | 302.4776 | 338.8346 | 366.4195 | 300.0994
1513.9417 | 304.3784 | 338.7949 | 367.9635 | 301.2811
1514.9417 | 305.6142 | 339.5175 | 369.429 | 302.0288
1515.9417 | 307.1186 | 340.3154 | 370.3279 | 303.309
1516.9417 | 308.325 | 341.523 | 372.4479 | 304.1663
1517.9417 | 311.0302 | 342.4343 | 375.108 | 307.303
1518.9417 | 311.9936 | 344.4732 | 377.6679 | 310.8738
1519.9417 | 313.9506 | 345.2031 | 379.8592 | 313.1544
1520.9417 | 315.695 | 345.6884 | 382.1192 | 315.7636
1521.9417 | 318.1036 | 345.3053 | 382.863 | 317.6082
1522.9417 | 321.5595 | 344.0759 | 383.2939 | 317.1629
1523.9417 | 322.0683 | 343.1488 | 383.0945 | 317.4852
1524.9417 | 321.6751 | 342.2291 | 383.475 | 318.5868
1525.9417 | 322.45 | 341.1797 | 382.6031 | 318.2134
1526.9417 | 322.8061 | 341.6266 | 381.7686 | 318.5686
1527.9417 | 324.5552 | 342.3049 | 383.8894 | 318.6002
1528.9417 | 326.0464 | 342.3467 | 385.4189 | 319.4944
1529.9417 | 328.0685 | 342.2807 | 387.3424 | 322.8144
1530.9417 | 329.6174 | 341.8722 | 386.834 | 322.4838
1531.9417 | 328.5399 | 340.7525 | 386.1465 | 321.4102
1532.9417 | 329.1567 | 341.338 | 386.458 | 321.5385
1533.9417 | 328.5187 | 341.3524 | 387.2529 | 321.6843
1534.9417 | 328.6531 | 341.5381 | 389.0643 | 321.922
1535.9417 | 328.867 | 341.9176 | 388.5354 | 322.2659
1536.9417 | 330.4422 | 342.7323 | 390.4808 | 322.2043
1537.9417 | 330.8522 | 342.3891 | 391.1125 | 321.6953
1538.9417 | 331.0317 | 342.689 | 391.8747 | 321.636
1539.9417 | 332.1987 | 342.2296 | 391.7879 | 321.6441
1540.9417 | 332.185 | 342.3187 | 392.0703 | 321.8852
1541.9417 | 334.0174 | 343.8453 | 394.7341 | 324.7077
1542.9417 | 335.6103 | 344.5166 | 396.2056 | 325.5508
1543.9417 | 335.6397 | 345.7532 | 397.5862 | 326.0636
1544.9417 | 336.3093 | 347.385 | 400.2699 | 325.3829
1545.9417 | 337.2892 | 349.0003 | 403.6852 | 325.8211
1546.9417 | 337.0843 | 350.2294 | 403.6157 | 324.9225
1547.9417 | 336.4679 | 351.0233 | 404.1923 | 324.7415
1548.9417 | 335.5587 | 351.6926 | 405.1407 | 326.2007
1549.9417 | 334.6491 | 353.4369 | 404.1279 | 324.7683
1550.9417 | 333.5848 | 353.621 | 402.8917 | 323.844
1551.9417 | 332.9453 | 353.1307 | 401.7094 | 323.7491
1552.9417 | 333.3635 | 354.0651 | 401.7344 | 324.182
1553.9417 | 332.6101 | 353.3549 | 402.1645 | 323.1541
1554.9417 | 331.9433 | 353.8871 | 402.2304 | 323.0172
1555.9417 | 330.5781 | 354.411 | 401.8451 | 321.6463
1556.9417 | 330.3131 | 356.0391 | 404.6743 | 321.7493
1557.9417 | 329.0408 | 356.9165 | 405.725 | 322.4301
1558.9417 | 328.7742 | 357.7191 | 404.2264 | 321.312
1559.9417 | 328.8297 | 358.2969 | 402.2178 | 320.0723
1560.9417 | 328.0882 | 359.9901 | 401.2102 | 319.3916
1561.9417 | 327.2759 | 361.4355 | 401.412 | 319.1504
1562.9417 | 326.5799 | 362.9026 | 399.6793 | 318.8316
1563.9417 | 325.8989 | 364.5127 | 399.7497 | 318.3337
1564.9417 | 325.383 | 364.9557 | 399.5855 | 318.9142
1565.9417 | 324.9986 | 365.2665 | 397.7959 | 319.0348
1566.9417 | 325.0239 | 365.9467 | 397.4403 | 318.7265
1567.9417 | 327.5188 | 367.3332 | 398.67 | 320.8452
1568.9417 | 329.0242 | 368.2774 | 399.8063 | 322.6128
1569.9417 | 329.6709 | 368.0749 | 400.8848 | 323.1674
1570.9417 | 332.23 | 367.8604 | 403.1497 | 323.4675
1571.9417 | 333.038 | 370.2239 | 404.7833 | 326.5062
1572.9417 | 334.5535 | 371.9716 | 405.4935 | 328.087
1573.9417 | 334.7684 | 372.956 | 405.2758 | 328.267
1574.9417 | 335.7757 | 374.0583 | 404.6768 | 328.5553
1575.9417 | 337.5585 | 375.9334 | 406.1011 | 329.6423
1576.9417 | 339.4806 | 377.23 | 409.2408 | 332.7507
1577.9417 | 339.6878 | 379.4086 | 411.4642 | 333.6707
1578.9417 | 339.1952 | 380.412 | 411.5152 | 334.2772
1579.9417 | 339.2438 | 380.8539 | 411.1837 | 334.3761
1580.9417 | 339.6757 | 381.176 | 411.2096 | 333.8097
1581.9417 | 339.2838 | 380.8771 | 409.6591 | 333.1286
1582.9417 | 339.5399 | 380.9835 | 409.7611 | 334.0999
1583.9417 | 340.2436 | 382.2607 | 411.1884 | 333.8524
1584.9417 | 340.7769 | 383.2677 | 411.2545 | 333.5512
1585.9417 | 341.0375 | 383.1992 | 411.8725 | 333.2084
1586.9417 | 341.9336 | 384.5698 | 413.0621 | 334.0425
1587.9417 | 342.4347 | 385.4177 | 414.1994 | 336.2257
1588.9417 | 343.3814 | 384.9085 | 413.79 | 335.6605
1589.9417 | 343.1496 | 384.7487 | 412.3489 | 334.7472
1590.9417 | 342.9622 | 384.5605 | 411.7216 | 335.6124
1591.9417 | 343.4499 | 383.9261 | 411.4312 | 336.7528
1592.9417 | 342.3592 | 383.4565 | 410.9726 | 335.9327
1593.9417 | 342.0854 | 383.1228 | 411.1078 | 335.5215
1594.9417 | 341.5536 | 382.8483 | 410.7248 | 335.2231
1595.9417 | 341.7156 | 382.6243 | 410.8389 | 335.2308
1596.9417 | 342.8358 | 382.7704 | 410.6238 | 335.3404
1597.9417 | 342.6606 | 381.5081 | 408.5805 | 334.5826
1598.9417 | 343.5142 | 380.4793 | 406.9974 | 333.8966
1599.9573 | 344.7905 | 380.5435 | 409.37 | 333.4748
1600.9417 | 344.6722 | 380.3844 | 408.919 | 333.421
1601.9417 | 344.6188 | 380.2932 | 410.802 | 333.1708
1602.9417 | 345.3946 | 380.6382 | 410.8178 | 332.8432
1603.9417 | 345.5655 | 381.1225 | 410.541 | 333.6525
1604.9417 | 344.9113 | 380.7138 | 409.7971 | 332.5124
1605.9417 | 344.3119 | 381.2802 | 410.2727 | 331.992
1606.9417 | 346.1897 | 381.777 | 411.2288 | 331.807
1607.9417 | 346.0033 | 381.1183 | 412.0151 | 332.1294
1608.9417 | 345.6863 | 380.3999 | 411.5643 | 331.025
1609.9417 | 345.1481 | 381.3191 | 413.0109 | 332.8579
1610.9417 | 344.7829 | 382.3518 | 413.0442 | 332.9742
1611.9417 | 345.5289 | 383.3149 | 412.4986 | 333.0207
1612.9417 | 344.9276 | 383.6155 | 411.492 | 331.7234
1613.9417 | 344.0802 | 383.7498 | 409.8439 | 330.7142
1614.9417 | 343.823 | 384.9806 | 408.9741 | 329.8555
1615.9417 | 343.0865 | 385.7699 | 408.3734 | 329.6967
1616.9417 | 343.5371 | 386.141 | 408.3845 | 330.7606
1617.9417 | 344.6657 | 387.6186 | 409.4649 | 332.6896
1618.9573 | 344.5322 | 388.1413 | 410.7136 | 334.0553
1619.9417 | 343.7747 | 388.4912 | 409.8355 | 333.9811
1620.9417 | 345.5026 | 389.3982 | 409.7884 | 332.9908
1621.9417 | 347.3426 | 389.3266 | 410.2761 | 331.7875
1622.9417 | 349.5245 | 389.6126 | 411.6545 | 331.6992
1623.9573 | 348.7167 | 389.4454 | 411.6901 | 331.3532
1624.9417 | 348.8056 | 388.4962 | 410.6917 | 331.5146
1625.9417 | 348.8637 | 389.8457 | 412.7315 | 333.0583
1626.9573 | 349.2818 | 391.1129 | 416.1872 | 334.9832
1627.9417 | 348.952 | 392.0681 | 416.5406 | 335.3184
1628.9417 | 349.5555 | 391.4209 | 416.0931 | 334.6674
1629.9573 | 350.2472 | 390.4135 | 414.404 | 334.8249
1630.9417 | 353.0252 | 390.6259 | 415.7334 | 336.7752
1631.9417 | 354.2342 | 390.9616 | 416.0516 | 337.3487
1632.9417 | 354.4547 | 391.1955 | 416.8189 | 337.9678
1633.9573 | 354.6888 | 391.7286 | 416.4971 | 337.6495
1634.9417 | 354.2006 | 391.9094 | 415.8362 | 337.6088
1635.9417 | 354.3373 | 392.1732 | 415.4717 | 336.7674
1636.9417 | 356.6734 | 391.8457 | 415.8842 | 336.5484
1637.9417 | 356.4532 | 390.5894 | 415.7887 | 336.0543
1638.9573 | 355.5461 | 389.5473 | 414.0819 | 336.1656
1639.9417 | 355.315 | 388.0774 | 411.7813 | 335.5348
1640.9417 | 354.9892 | 387.2901 | 410.8375 | 334.9602
1641.9417 | 355.1448 | 386.9064 | 410.1412 | 334.279
1642.9417 | 355.5961 | 386.9179 | 410.3554 | 333.6793
1643.9417 | 356.7465 | 387.0128 | 412.725 | 333.5982
1644.9417 | 359.08 | 387.0785 | 416.7648 | 333.4764
1645.9417 | 360.931 | 386.6073 | 417.3468 | 333.7606
1646.9417 | 361.0028 | 386.8866 | 418.9422 | 333.6087
1647.9417 | 361.4868 | 387.0613 | 420.2001 | 334.2976
1648.9417 | 361.3687 | 387.1283 | 418.7997 | 333.9236
1649.9417 | 360.1492 | 386.7241 | 417.4416 | 333.382
1650.9417 | 359.9765 | 386.4407 | 417.068 | 334.2703
1651.9417 | 360.2682 | 386.811 | 418.1364 | 333.9832
1652.9417 | 360.5404 | 387.6775 | 416.0441 | 332.6956
1653.9417 | 359.4032 | 388.2385 | 415.965 | 333.7308
1654.9417 | 359.8342 | 389.7833 | 417.6664 | 334.1754
1655.9417 | 361.2773 | 391.3256 | 419.6757 | 337.2863
1656.9417 | 362.7802 | 392.2027 | 421.4354 | 338.4911
1657.9417 | 364.0527 | 393.3008 | 420.9879 | 338.527
1658.9417 | 364.2379 | 393.6872 | 418.8736 | 337.5411
1659.9417 | 364.0685 | 394.8392 | 419.7524 | 337.7676
1660.9417 | 364.1769 | 396.5421 | 421.0836 | 337.7492
1661.9417 | 363.5788 | 397.9922 | 422.1971 | 338.1297
1662.9417 | 364.4179 | 398.1947 | 424.0328 | 339.8968
1663.9417 | 366.6079 | 398.8293 | 424.5694 | 341.3888
1664.9417 | 368.7017 | 398.3443 | 426.9744 | 341.7074
1665.9417 | 368.6569 | 397.6716 | 425.4545 | 340.8547
1666.9417 | 368.1114 | 397.654 | 425.1315 | 340.2063
1667.9417 | 368.575 | 398.2572 | 425.216 | 339.7588
1668.9417 | 368.4179 | 397.5956 | 426.6496 | 339.5155
1669.9417 | 367.3564 | 398.6137 | 426.8899 | 340.2488
1670.9417 | 367.8286 | 399.8383 | 427.736 | 340.1456
1671.9417 | 367.0922 | 399.5798 | 426.4273 | 339.7242
1672.9417 | 367.8075 | 399.4678 | 426.2303 | 339.5992
1673.9417 | 369.4788 | 400.6698 | 427.1088 | 339.1824
1674.9417 | 369.5234 | 401.0378 | 428.0848 | 339.1168
1675.9417 | 369.2531 | 400.7676 | 428.4149 | 338.8518
1676.9417 | 370.4121 | 400.5418 | 428.6113 | 339.7582
1677.9417 | 369.3168 | 399.8849 | 427.4183 | 339.1783
1678.9417 | 368.4521 | 400.7038 | 427.3059 | 339.8605
1679.9417 | 367.7077 | 402.1463 | 427.4206 | 342.2901
1680.9417 | 367.2685 | 402.2993 | 427.375 | 343.0018
1681.9417 | 367.3529 | 403.5911 | 428.4477 | 343.1906
1682.9417 | 367.6897 | 403.0242 | 428.0609 | 343.0413
1683.9417 | 369.4262 | 403.6881 | 429.4789 | 343.7153
1684.9417 | 370.2649 | 403.0602 | 429.5384 | 342.5942
1685.9417 | 370.4477 | 402.3825 | 428.9781 | 342.0184
1686.9417 | 370.3474 | 402.0093 | 429.0969 | 342.5261
1687.9417 | 369.4619 | 402.3697 | 429.7079 | 344.55
1688.9417 | 370.7072 | 402.9002 | 429.9703 | 343.7356
1689.9417 | 370.7101 | 404.3406 | 432.6577 | 343.9578
1690.9417 | 371.3792 | 405.7602 | 434.171 | 345.6522
1691.9417 | 371.1367 | 406.737 | 434.1221 | 345.8483
1692.9417 | 371.9913 | 406.7674 | 433.9302 | 347.7012
1693.9417 | 371.2918 | 406.4852 | 433.427 | 348.9763
1694.9417 | 372.6077 | 407.0356 | 434.0745 | 349.2627
1695.9417 | 373.6104 | 407.2025 | 434.3825 | 350.7467
1696.9417 | 373.6695 | 408.5101 | 436.0134 | 351.1112
1697.9417 | 374.6337 | 408.8115 | 436.5698 | 352.6415
1698.9417 | 377.3428 | 409.2352 | 437.5696 | 352.8438
1699.9417 | 378.8198 | 409.9669 | 440.7262 | 352.9653
1700.9417 | 379.461 | 408.5345 | 439.2925 | 351.9477
1701.9417 | 381.1002 | 408.8791 | 442.1184 | 351.2122
1702.9417 | 382.6585 | 408.5847 | 442.3447 | 350.3787
1703.9417 | 383.633 | 409.0212 | 443.0199 | 350.2264
1704.9417 | 385.3819 | 408.1591 | 442.8775 | 350.0335
1705.9417 | 384.5472 | 409.2008 | 446.8461 | 351.9905
1706.9417 | 384.5243 | 410.3122 | 447.1028 | 352.7861
1707.9417 | 383.518 | 410.6089 | 446.7437 | 352.1845
1708.9417 | 382.9541 | 410.8975 | 444.3539 | 351.0654
1709.9417 | 382.3439 | 411.0229 | 442.8543 | 350.6939
1710.9417 | 382.2979 | 412.1791 | 444.053 | 352.0932
1711.9417 | 382.452 | 413.5684 | 445.852 | 351.9362
1712.9417 | 382.1512 | 413.5145 | 446.3322 | 353.8474
1713.9417 | 381.0109 | 413.1726 | 446.7311 | 355.2957
1714.9417 | 378.9294 | 414.0301 | 446.5635 | 356.4687
1715.9417 | 379.6528 | 414.6342 | 445.0847 | 356.5897
1716.9417 | 379.8186 | 414.3635 | 444.5197 | 358.035
1717.9417 | 378.8104 | 412.853 | 444.3367 | 357.9026
1718.9417 | 378.3075 | 412.7747 | 443.2931 | 357.4167
1719.9417 | 377.7975 | 412.4103 | 443.2708 | 357.0428
1720.9417 | 378.7728 | 412.8093 | 443.0146 | 356.6659
1721.9417 | 380.1967 | 412.8584 | 443.1028 | 356.2197
1722.9417 | 379.7998 | 412.7561 | 442.5813 | 355.3738
1723.9417 | 379.4481 | 411.6043 | 441.3355 | 354.8157
1724.9417 | 379.7147 | 411.7357 | 442.1831 | 355.2158
1725.9417 | 379.4986 | 412.3898 | 441.9201 | 354.6599
1726.9417 | 378.3687 | 411.5803 | 440.5704 | 353.3798
1727.9417 | 380.1008 | 410.836 | 440.548 | 353.5857
1728.9417 | 379.5005 | 410.392 | 440.724 | 353.4074
1729.9417 | 379.4219 | 410.3264 | 439.4961 | 352.9946
1730.9417 | 379.7587 | 409.3905 | 438.8886 | 355.3985
1731.9417 | 380.6897 | 408.8045 | 439.1478 | 355.4711
1732.9417 | 381.3858 | 408.8433 | 440.7985 | 355.1366
1733.9417 | 381.9818 | 409.434 | 440.7846 | 355.0263
1734.9417 | 384.1845 | 408.9587 | 440.3777 | 354.3781
1735.9417 | 384.7248 | 407.8519 | 439.4478 | 353.7902
1736.9417 | 384.4522 | 407.5596 | 440.4512 | 354.6567
1737.9417 | 385.4456 | 407.9055 | 441.799 | 357.3216
1738.9417 | 387.2918 | 407.4448 | 440.7539 | 358.0117
1739.9417 | 387.7454 | 406.4265 | 439.8025 | 357.1658
1740.9417 | 387.5577 | 406.3327 | 439.9236 | 356.6057
1741.9417 | 387.935 | 407.1079 | 440.4966 | 357.5808
1742.9417 | 386.9712 | 408.1552 | 442.2284 | 358.6332
1743.9417 | 386.8725 | 408.7547 | 444.7471 | 358.9421
1744.9417 | 386.3335 | 409.1282 | 444.6815 | 360.8767
1745.9417 | 387.0301 | 409.7069 | 445.7213 | 360.043
1746.9417 | 388.4016 | 410.0883 | 445.28 | 359.4839
1747.9417 | 387.4979 | 409.6998 | 444.0915 | 358.7843
1748.9417 | 386.3302 | 409.9965 | 444.3705 | 359.261
1749.9417 | 386.1321 | 410.1363 | 444.0356 | 358.9801
1750.9417 | 386.0572 | 410.2598 | 446.2935 | 360.398
1751.9417 | 389.6104 | 412.3658 | 449.1376 | 360.4204
1752.9417 | 390.7688 | 414.804 | 452.0674 | 360.2353
1753.9417 | 390.5055 | 416.6242 | 453.9329 | 360.8636
1754.9417 | 391.8981 | 417.1219 | 453.5869 | 360.1794
1755.9417 | 394.3438 | 419.6514 | 457.1871 | 360.5948
1756.9417 | 394.6856 | 421.7747 | 459.8401 | 360.9791
1757.9417 | 394.2139 | 423.2224 | 463.1896 | 360.6883
1758.9417 | 393.8513 | 424.5607 | 463.2059 | 360.0112
1759.9417 | 392.7616 | 426.2799 | 461.2028 | 359.4246
1760.9417 | 391.2329 | 426.8251 | 459.184 | 359.8958
1761.9417 | 391.6321 | 428.6843 | 460.0653 | 362.9942
1762.9417 | 390.657 | 429.0408 | 460.4113 | 364.4917
1763.9417 | 390.881 | 429.9774 | 459.0439 | 363.2498
1764.9417 | 391.4028 | 429.7876 | 460.5511 | 364.2277
1765.9417 | 391.0574 | 429.2941 | 461.172 | 363.5953
1766.9417 | 390.9518 | 429.4979 | 461.6034 | 363.5501
1767.9417 | 392.7306 | 429.8843 | 462.2052 | 362.749
1768.9417 | 393.3308 | 431.2846 | 462.8759 | 362.4628
1769.9417 | 393.371 | 431.094 | 462.1588 | 362.2217
1770.9417 | 393.291 | 431.7544 | 462.5369 | 364.1638
1771.9417 | 393.6669 | 432.5659 | 463.0585 | 363.4808
1772.9573 | 394.3591 | 433.614 | 463.924 | 363.1723
1773.9417 | 394.3762 | 433.3644 | 463.2099 | 362.9108
1774.9417 | 394.8732 | 432.9609 | 463.8042 | 362.438
1775.9417 | 396.1452 | 432.0571 | 461.8865 | 362.7799
1776.9417 | 397.2645 | 431.6152 | 459.7698 | 362.6467
1777.9417 | 396.9186 | 431.2628 | 458.5135 | 362.6462
1778.9417 | 396.5593 | 429.9924 | 458.0104 | 362.8601
1779.9417 | 396.8833 | 429.4335 | 458.6869 | 362.7615
1780.9417 | 398.8592 | 428.8021 | 458.3131 | 362.1547
1781.9417 | 398.1085 | 428.1375 | 457.8175 | 362.7639
1782.9417 | 397.2686 | 427.7909 | 456.0965 | 362.8074
1783.9417 | 397.3572 | 426.8117 | 455.1063 | 362.7472
1784.9417 | 396.4693 | 426.6072 | 454.0813 | 361.6505
1785.9417 | 396.3187 | 428.1326 | 454.1202 | 362.0961
1786.9417 | 397.0823 | 429.3924 | 454.666 | 361.7714
1787.9417 | 398.4679 | 429.5842 | 454.7255 | 363.5476
1788.9417 | 399.2608 | 429.1938 | 453.4332 | 363.2043
1789.9417 | 399.7505 | 429.339 | 453.3727 | 361.9693
1790.9417 | 399.9374 | 428.5467 | 454.0645 | 361.8346
1791.9417 | 399.5546 | 428.0526 | 452.9045 | 361.4941
1792.9417 | 398.9087 | 427.8454 | 453.5833 | 360.969
1793.9417 | 397.6668 | 427.4685 | 451.499 | 360.067
1794.9417 | 396.2782 | 427.3832 | 450.2591 | 359.1647
1795.9417 | 396.1341 | 427.8558 | 450.9163 | 359.2923
1796.9417 | 395.111 | 428.2669 | 451.463 | 358.7237
1797.9417 | 395.4619 | 428.8687 | 454.2027 | 359.4496
1798.9417 | 395.852 | 430.3325 | 456.7237 | 359.4419
1799.9417 | 396.849 | 432.0706 | 458.1349 | 359.4641
1800.9417 | 398.089 | 433.2121 | 460.8356 | 360.7219
1801.9417 | 398.0176 | 434.8404 | 462.7526 | 361.0057
1802.9417 | 397.4537 | 435.4703 | 462.2629 | 361.8838
1803.9417 | 397.2019 | 435.4287 | 461.8157 | 361.8942
1804.9417 | 397.0357 | 436.1364 | 461.6455 | 363.6311
1805.9417 | 397.5577 | 436.6053 | 461.562 | 364.7624
1806.9417 | 398.5261 | 435.7915 | 460.0892 | 365.7671
1807.9417 | 398.2564 | 434.5017 | 458.7178 | 365.2389
1808.9417 | 398.0011 | 434.4619 | 457.8984 | 364.7152
1809.9417 | 398.3449 | 435.279 | 457.9533 | 364.7019
1810.9417 | 398.2064 | 435.8161 | 456.9042 | 363.5369
1811.9417 | 399.6342 | 434.6521 | 454.4361 | 363.1938
1812.9417 | 398.9796 | 434.6302 | 454.2308 | 362.8893
1813.9417 | 397.6952 | 434.1292 | 452.103 | 362.1764
1814.9417 | 397.8209 | 433.9392 | 450.5 | 361.8706
1815.9417 | 398.8229 | 434.7763 | 449.463 | 361.2968
1816.9417 | 397.7227 | 434.0965 | 448.0186 | 360.2269
1817.9417 | 398.0913 | 433.6048 | 446.1725 | 359.1461
1818.9417 | 398.9109 | 434.0812 | 446.0137 | 359.6568
1819.9417 | 399.2262 | 433.1401 | 444.3957 | 358.6795
1820.9417 | 400.3028 | 433.8435 | 444.755 | 358.5144
1821.9417 | 401.3071 | 433.4517 | 444.7072 | 358.2682
1822.9417 | 403.3628 | 434.0228 | 445.7153 | 358.2552
1823.9417 | 404.8222 | 433.7911 | 446.4392 | 358.0217
1824.9417 | 405.5025 | 432.8833 | 447.0936 | 358.1986
1825.9417 | 407.3684 | 432.9394 | 448.5377 | 358.2807
1826.9417 | 409.3323 | 433.3717 | 450.4993 | 358.5019
1827.9417 | 408.8196 | 433.2125 | 451.1523 | 358.6506
1828.9417 | 410.2038 | 432.566 | 452.1892 | 359.2212
1829.9417 | 410.8069 | 432.3795 | 453.539 | 358.7776
1830.9417 | 410.4777 | 431.8276 | 452.1776 | 358.4288
1831.9417 | 410.181 | 431.2641 | 451.1376 | 358.3518
1832.9417 | 410.7986 | 430.3204 | 451.3061 | 358.419
1833.9417 | 410.423 | 429.3433 | 451.0626 | 358.5953
1834.9417 | 410.3391 | 429.9339 | 451.6585 | 359.3925
1835.9417 | 410.4696 | 432.5136 | 453.6516 | 360.0598
1836.9417 | 412.5247 | 433.9389 | 456.5903 | 363.3467
1837.9417 | 414.1937 | 433.2984 | 458.0485 | 365.2825
1838.9417 | 415.6267 | 433.5983 | 459.8869 | 365.9708
1839.9417 | 416.8971 | 434.9591 | 461.0507 | 367.242
1840.9417 | 418.0489 | 434.3344 | 463.0025 | 367.4733
1841.9417 | 419.9834 | 434.1331 | 464.3851 | 368.5311
1842.9417 | 419.9001 | 433.6853 | 464.3782 | 369.2673
1843.9417 | 419.7071 | 434.6186 | 464.5964 | 370.7303
1844.9417 | 419.1852 | 435.3946 | 464.3049 | 371.4377
1845.9417 | 417.5698 | 435.4584 | 461.7934 | 370.0725
1846.9417 | 415.7026 | 435.6135 | 459.1278 | 368.85
1847.9417 | 417.1169 | 436.1261 | 457.9942 | 368.1238
1848.9417 | 418.0697 | 437.0841 | 459.179 | 368.0408
1849.9417 | 420.7595 | 436.0896 | 459.156 | 367.8867
1850.9417 | 421.1944 | 435.3538 | 458.7578 | 367.8527
1851.9417 | 421.2724 | 435.4384 | 459.9027 | 368.5046
1852.9417 | 421.9984 | 436.6827 | 460.418 | 369.2365
1853.9417 | 419.8783 | 436.5507 | 458.8862 | 369.1567
1854.9417 | 420.5919 | 435.0515 | 457.9866 | 368.9708
1855.9417 | 421.1992 | 434.6762 | 457.6281 | 368.9529
1856.9417 | 420.2335 | 435.1042 | 457.5792 | 368.7789
1857.9417 | 420.5332 | 435.3753 | 458.5256 | 368.4817
1858.9417 | 419.2357 | 436.0536 | 457.9689 | 367.5403
1859.9417 | 419.3294 | 436.0881 | 457.1242 | 367.2791
1860.9417 | 419.0305 | 435.4524 | 458.0995 | 366.7737
1861.9417 | 419.4583 | 435.3215 | 457.9589 | 366.703
1862.9417 | 417.1059 | 434.6355 | 457.0336 | 367.0335
1863.9417 | 415.3425 | 434.1629 | 457.113 | 368.3265
1864.9417 | 414.585 | 433.8694 | 456.9248 | 369.2524
1865.9417 | 413.1363 | 433.4977 | 456.4273 | 369.2109
1866.9417 | 411.9503 | 433.6817 | 453.6389 | 368.7447
1867.9417 | 412.7212 | 432.9384 | 452.863 | 368.1026
1868.9417 | 411.229 | 432.924 | 451.8734 | 368.3895
1869.9417 | 411.6693 | 433.6101 | 453.0483 | 367.8127
1870.9417 | 412.3046 | 434.841 | 453.3714 | 367.1415
1871.9417 | 413.3705 | 435.1304 | 452.9001 | 366.2327
1872.9417 | 412.6381 | 436.0314 | 453.4572 | 366.6417
1873.9417 | 413.5758 | 435.6578 | 453.3639 | 366.4963
1874.9417 | 413.0614 | 437.2662 | 451.825 | 366.6004
1875.9417 | 413.0173 | 436.3294 | 450.1486 | 365.6843
1876.9417 | 411.1958 | 436.6755 | 449.4662 | 365.3949
1877.9417 | 412.0838 | 436.0779 | 448.6883 | 366.2835
1878.9417 | 412.7208 | 437.0661 | 449.0564 | 365.6252
1879.9417 | 413.4362 | 437.1384 | 449.1994 | 365.1045
1880.9417 | 413.5653 | 437.1923 | 448.8567 | 364.9889
1881.9417 | 414.2829 | 436.6962 | 449.5341 | 364.9979
1882.9417 | 414.0323 | 434.9837 | 448.6538 | 365.0438
1883.9417 | 414.0031 | 434.8059 | 450.0996 | 367.0312
1884.9417 | 414.607 | 435.173 | 451.0579 | 367.752
1885.9417 | 414.3947 | 435.5721 | 450.2908 | 367.6879
1886.9417 | 415.3593 | 435.95 | 452.1189 | 368.4002
1887.9417 | 416.5793 | 436.2635 | 452.1663 | 370.2312
1888.9417 | 418.2602 | 436.5066 | 453.4581 | 369.7421
1889.9417 | 419.2224 | 436.2715 | 453.582 | 370.7443
1890.9417 | 419.6535 | 435.1396 | 453.5643 | 370.6173
1891.9417 | 418.7865 | 435.4289 | 453.0531 | 370.8641
1892.9417 | 418.6867 | 434.9257 | 453.3644 | 370.8069
1893.9417 | 416.6617 | 434.3303 | 452.9999 | 371.1743
1894.9417 | 416.1178 | 435.0938 | 452.2872 | 371.8474
1895.9417 | 414.2961 | 434.8428 | 452.2997 | 371.0667
1896.9417 | 414.1187 | 435.192 | 453.8279 | 371.5037
1897.9417 | 414.1576 | 434.7862 | 454.332 | 371.2408
1898.9417 | 414.4125 | 435.5029 | 453.6688 | 371.3504
1899.9417 | 415.8839 | 436.9547 | 455.2182 | 374.1341
1900.9417 | 416.5632 | 437.5719 | 456.7529 | 373.9045
1901.9417 | 415.271 | 436.8911 | 455.8529 | 372.7232
1902.9417 | 414.6398 | 437.0758 | 456.4392 | 372.604
1903.9417 | 415.7411 | 438.779 | 458.2721 | 373.8274
1904.9417 | 415.652 | 438.867 | 458.246 | 373.3882
1905.9417 | 416.9542 | 438.4899 | 458.7561 | 372.9919
1906.9417 | 417.2078 | 437.4781 | 459.097 | 373.5408
1907.9417 | 416.9998 | 437.504 | 461.2635 | 374.1789
1908.9573 | 416.8566 | 438.0952 | 461.3295 | 373.9666
1909.9417 | 415.3822 | 438.3103 | 461.0492 | 373.9931
1910.9417 | 415.0136 | 438.2101 | 461.5805 | 373.8246
1911.9417 | 414.9425 | 438.5718 | 460.8703 | 374.1147
1912.9417 | 413.6379 | 439.3821 | 460.0259 | 373.2617
1913.9417 | 415.0306 | 440.1224 | 459.804 | 372.9044
1914.9417 | 415.4692 | 439.7765 | 460.4537 | 372.393
1915.9417 | 415.6621 | 440.6236 | 460.5801 | 373.0866
1916.9417 | 416.072 | 441.5991 | 461.915 | 373.0919
1917.9417 | 414.7033 | 442.17 | 461.8592 | 372.8236
1918.9417 | 413.4225 | 441.8177 | 460.8686 | 372.462
1919.9417 | 413.141 | 442.0935 | 460.2519 | 372.5753
1920.9417 | 413.3837 | 441.7127 | 458.8188 | 371.7143
1921.9417 | 413.7852 | 441.2388 | 457.9357 | 371.2029
1922.9417 | 413.8782 | 441.2812 | 458.2524 | 371.0161
1923.9573 | 413.6876 | 442.4904 | 459.7843 | 371.4047
1924.9417 | 413.1345 | 442.4131 | 459.1577 | 371.2417
1925.9417 | 413.1073 | 441.0632 | 457.314 | 370.4691
1926.9417 | 412.8221 | 441.0859 | 456.5652 | 370.1422
1927.9417 | 411.5278 | 441.5835 | 455.5862 | 370.7719
1928.9417 | 410.5819 | 441.4419 | 455.6804 | 371.1604
1929.9573 | 410.1892 | 441.7475 | 456.282 | 372.5701
1930.9417 | 409.8774 | 443.4164 | 457.4465 | 372.2617
1931.9573 | 410.534 | 443.516 | 457.4935 | 372.0945
1932.9417 | 409.3652 | 443.2605 | 457.1024 | 371.987
1933.9573 | 411.1412 | 443.906 | 457.3126 | 371.7829
1934.9417 | 411.9206 | 443.7104 | 455.7499 | 372.0128
1935.9417 | 412.3575 | 443.3595 | 454.902 | 370.884
1936.9417 | 412.4551 | 444.0166 | 454.4728 | 370.9952
1937.9417 | 413.5749 | 445.0266 | 452.9862 | 370.4236
1938.9417 | 413.4345 | 444.9049 | 452.4485 | 369.1346
1939.9417 | 414.5754 | 445.9532 | 451.5675 | 368.8927
1940.9417 | 413.5496 | 445.3821 | 450.2178 | 368.1209
1941.9417 | 414.1578 | 444.641 | 449.3929 | 368.2425
1942.9417 | 414.713 | 443.7991 | 449.6416 | 367.8315
1943.9417 | 414.8473 | 444.7398 | 450.5325 | 367.5836
1944.9417 | 415.8356 | 444.1307 | 449.072 | 366.8513
1945.9417 | 417.8126 | 443.5959 | 449.1315 | 366.5396
1946.9417 | 419.8626 | 443.005 | 449.9176 | 367.5141
1947.9417 | 420.28 | 442.5577 | 450.5622 | 367.7817
1948.9417 | 420.5957 | 442.4422 | 450.9554 | 368.3438
1949.9417 | 420.0435 | 442.154 | 452.0603 | 368.6289
1950.9417 | 421.3985 | 441.8894 | 453.7363 | 368.5804
1951.9417 | 421.8907 | 441.2606 | 454.0209 | 368.4726
1952.9417 | 421.4755 | 440.8446 | 454.2842 | 368.6883
1953.9417 | 422.7458 | 440.7013 | 455.8176 | 369.9255
1954.9417 | 425.2389 | 440.0738 | 457.2882 | 370.192
1955.9417 | 427.2472 | 440.8564 | 457.1113 | 370.6546
1956.9417 | 426.8146 | 441.2662 | 457.2844 | 370.9687
1957.9417 | 425.5023 | 440.6023 | 458.2458 | 370.7498
1958.9417 | 423.4144 | 440.6625 | 456.3681 | 370.7183
1959.9417 | 424.5711 | 443.7127 | 456.2616 | 371.2175
1960.9417 | 424.7993 | 446.8852 | 457.4345 | 371.7594
1961.9417 | 424.4937 | 447.6417 | 457.1489 | 372.3538
1962.9417 | 425.7318 | 446.7311 | 457.311 | 372.5418
1963.9417 | 429.6832 | 446.7941 | 459.0382 | 373.5102
1964.9417 | 431.8663 | 445.1107 | 459.2534 | 373.8789
1965.9417 | 430.7521 | 443.7294 | 460.3801 | 374.2182
1966.9417 | 429.446 | 443.4014 | 459.8878 | 374.8656
1967.9417 | 428.7459 | 443.2046 | 461.4771 | 375.7352
1968.9573 | 428.5678 | 444.4178 | 463.0715 | 375.7282
1969.9417 | 427.0183 | 444.4854 | 463.1891 | 376.2704
1970.9417 | 426.1394 | 444.6253 | 464.3665 | 376.9497
1971.9417 | 425.1668 | 445.4826 | 465.7857 | 378.3571
1972.9417 | 424.1912 | 446.4746 | 466.0331 | 379.4203
1973.9417 | 422.9713 | 447.2209 | 465.7017 | 379.2797
1974.9417 | 422.0246 | 447.6658 | 465.1312 | 379.7717
1975.9417 | 420.9678 | 446.9703 | 465.9492 | 380.3603
1976.9417 | 420.5722 | 446.1591 | 465.2316 | 381.772
1977.9417 | 420.3329 | 444.8205 | 465.4864 | 381.9992
1978.9417 | 418.842 | 444.7158 | 464.5631 | 381.4079
1979.9417 | 417.5566 | 443.7297 | 463.0656 | 380.725
1980.9417 | 418.0645 | 443.6604 | 463.3729 | 381.8453
1981.9417 | 418.0068 | 443.3281 | 462.4262 | 381.9613
1982.9417 | 417.8516 | 443.1321 | 463.1097 | 381.6361
1983.9417 | 417.7606 | 443.1298 | 464.6901 | 381.4649
1984.9417 | 416.8388 | 442.3249 | 463.0132 | 381.5679
1985.9417 | 416.2008 | 442.7495 | 462.4027 | 381.6036
1986.9417 | 415.0682 | 442.9805 | 462.1202 | 382.0898
1987.9417 | 413.6695 | 443.4934 | 461.5847 | 381.3118
1988.9417 | 414.4758 | 443.2162 | 461.3921 | 380.9853
1989.9417 | 412.925 | 442.6715 | 460.2991 | 380.7078
1990.9417 | 412.7679 | 442.1717 | 458.2727 | 379.8955
1991.9417 | 413.7279 | 443.3449 | 458.7738 | 380.8711
1992.9417 | 414.1341 | 444.055 | 457.1925 | 380.4656
1993.9573 | 413.7083 | 444.3915 | 458.3354 | 379.7807
1994.9417 | 413.4973 | 445.5069 | 458.0824 | 378.8341
1995.9417 | 414.1831 | 445.5402 | 456.5541 | 378.8542
1996.9417 | 411.9867 | 445.4349 | 455.3233 | 377.8909
1997.9417 | 410.9694 | 445.3207 | 454.9061 | 377.7102
1998.9417 | 411.6783 | 445.0298 | 455.798 | 378.7767
1999.9417 | 411.3145 | 444.4317 | 455.7119 | 378.5627
2000.9417 | 411.9008 | 444.2296 | 455.9191 | 379.6276
2001.9417 | 412.4926 | 444.2629 | 456.0713 | 379.7463
2002.9417 | 411.3687 | 443.7913 | 454.5587 | 378.7534
2003.9417 | 410.9166 | 444.4479 | 453.3083 | 379.5509
2004.9417 | 409.696 | 444.9021 | 452.6329 | 378.8555
2005.9417 | 410.4778 | 445.1023 | 452.875 | 378.6773
2006.9417 | 411.4713 | 445.3476 | 452.6875 | 378.3148
2007.9417 | 410.1978 | 445.135 | 452.9788 | 378.4752
2008.9417 | 410.186 | 445.1334 | 454.2357 | 380.0714
2009.9417 | 409.4911 | 445.8683 | 453.8518 | 379.7922
2010.9417 | 409.0394 | 445.6602 | 452.0395 | 378.8466
2011.9417 | 408.9759 | 445.9777 | 451.6168 | 379.1126
2012.9417 | 409.6277 | 446.7617 | 452.1715 | 378.6582
2013.9417 | 409.8975 | 446.5843 | 452.8245 | 377.5841
2014.9417 | 410.9424 | 446.2423 | 454.3079 | 377.2238
2015.9417 | 410.3739 | 445.5001 | 453.1628 | 376.5262
2016.9417 | 410.4723 | 444.7573 | 452.9233 | 376.7703
2017.9417 | 409.6818 | 445.5094 | 451.6569 | 376.2002
2018.9417 | 407.5269 | 445.3092 | 449.9036 | 374.944
2019.9417 | 405.9589 | 445.8377 | 450.4359 | 374.8003
2020.9417 | 404.3545 | 446.1748 | 451.4232 | 375.8339
2021.9417 | 403.3474 | 446.5581 | 451.4781 | 376.4311
2022.9417 | 404.3885 | 446.2915 | 450.1203 | 375.2745
2023.9417 | 404.9045 | 446.6328 | 448.5899 | 374.8923
2024.9417 | 404.4415 | 446.6401 | 447.3679 | 374.425
2025.9417 | 402.5145 | 445.7251 | 446.0294 | 373.8718
2026.9417 | 401.2388 | 445.5461 | 444.5556 | 373.5203
2027.9417 | 400.8272 | 446.4707 | 444.1194 | 373.3921
2028.9417 | 400.7753 | 447.3213 | 444.3398 | 373.092
2029.9417 | 401.4662 | 447.966 | 444.9017 | 372.88
2030.9417 | 404.0344 | 448.6638 | 445.3887 | 372.9484
2031.9417 | 405.8634 | 448.8886 | 446.5438 | 373.3916
2032.9417 | 407.35 | 448.7308 | 446.8064 | 373.2445
2033.9417 | 407.4962 | 448.315 | 451.2433 | 372.7914
2034.9417 | 405.9095 | 447.549 | 461.8138 | 372.3228
2035.9417 | 405.6802 | 447.9837 | 459.9727 | 372.5683
2036.9417 | 405.6842 | 449.0651 | 459.6348 | 372.4344
2037.9417 | 407.2082 | 449.7903 | 458.8266 | 372.1424
2038.9417 | 408.6233 | 449.609 | 458.8742 | 372.3355
2039.9417 | 409.602 | 451.6784 | 458.5107 | 372.1827
2040.9417 | 409.7422 | 451.93 | 458.5392 | 371.952
2041.9417 | 409.1266 | 452.1751 | 457.6087 | 372.5393
2042.9417 | 409.3187 | 452.6201 | 457.1775 | 372.4459
2043.9417 | 410.3612 | 452.1994 | 455.649 | 371.8444
2044.9417 | 411.4906 | 451.3493 | 455.9807 | 371.9493
2045.9417 | 411.1983 | 450.6931 | 457.2944 | 371.98
2046.9417 | 412.482 | 450.6883 | 458.0506 | 372.8321
2047.9417 | 412.5852 | 450.5249 | 458.6734 | 373.2198
2048.9417 | 413.1174 | 449.624 | 457.0272 | 372.7194
2049.9417 | 412.7059 | 448.8622 | 455.1838 | 373.096
2050.9417 | 413.0275 | 448.8256 | 453.9664 | 374.4521
2051.9417 | 414.4324 | 448.9796 | 456.0766 | 375.53
2052.9417 | 412.8898 | 447.8188 | 454.6766 | 375.1927
2053.9417 | 412.2788 | 447.8888 | 455.5949 | 374.8233
2054.9417 | 411.9725 | 448.9669 | 453.7047 | 374.8735
2055.9417 | 410.7328 | 449.4732 | 453.7338 | 375.8913
2056.9417 | 409.942 | 449.0227 | 453.2934 | 375.9688
2057.9417 | 409.3357 | 448.8663 | 453.852 | 376.5497
2058.9417 | 408.6004 | 447.8706 | 452.2434 | 376.0438
2059.9417 | 408.2197 | 447.1147 | 453.3594 | 378.2602
2060.9417 | 409.7755 | 446.9301 | 453.9872 | 377.7703
2061.9417 | 410.4624 | 446.9955 | 454.5391 | 377.6582
2062.9417 | 410.5189 | 446.5263 | 455.9093 | 377.1792
2063.9417 | 410.6077 | 446.1028 | 455.427 | 376.5284
2064.9417 | 410.3834 | 446.1731 | 454.4582 | 375.9758
2065.9417 | 409.4869 | 445.9086 | 452.7546 | 375.4189
2066.9417 | 409.3739 | 445.8526 | 451.1322 | 376.0353
2067.9417 | 409.2162 | 445.8998 | 450.6944 | 375.0073
2068.9417 | 408.2264 | 446.0555 | 450.9938 | 374.6249
2069.9417 | 408.6829 | 446.17 | 449.9847 | 374.0953
2070.9417 | 409.4786 | 446.8309 | 450.3087 | 373.6765
2071.9417 | 409.1352 | 447.7633 | 449.5819 | 373.5012
2072.9417 | 409.9533 | 448.4898 | 449.2704 | 372.9642
2073.9417 | 410.1091 | 448.1335 | 447.072 | 372.4398
2074.9417 | 409.4561 | 447.158 | 444.9542 | 371.8358
2075.9417 | 409.6318 | 447.7399 | 445.3026 | 371.6202
2076.9417 | 410.6029 | 449.5838 | 447.2996 | 371.803
2077.9417 | 411.045 | 451.3225 | 448.7358 | 372.1051
2078.9417 | 410.9235 | 452.8124 | 448.8159 | 372.1263
2079.9417 | 410.2675 | 453.92 | 448.6293 | 371.8009
2080.9417 | 410.2067 | 454.2013 | 449.9153 | 371.7409
2081.9417 | 411.4466 | 454.8286 | 452.0656 | 371.7981
2082.9417 | 412.5653 | 454.4085 | 451.2574 | 372.2641
2083.9417 | 413.6575 | 453.3646 | 451.6034 | 372.635
2084.9417 | 414.4061 | 454.8656 | 452.8161 | 373.0626
2085.9417 | 412.9858 | 455.6339 | 451.5363 | 373.4711
2086.9417 | 413.1914 | 454.3667 | 450.2938 | 372.6929
2087.9417 | 413.8183 | 453.4906 | 449.2624 | 372.3342
2088.9417 | 416.6487 | 455.6161 | 453.4643 | 373.5464
2089.9417 | 418.6976 | 455.5503 | 456.4567 | 374.3056
2090.9417 | 421.8532 | 453.9657 | 455.9215 | 375.2536
2091.9417 | 423.2624 | 454.2497 | 457.48 | 375.7988
2092.9417 | 423.8889 | 454.0069 | 460.1498 | 376.0781
2093.9417 | 421.8617 | 453.6756 | 459.6842 | 375.8321
2094.9417 | 421.761 | 453.329 | 459.699 | 375.9855
2095.9417 | 419.4339 | 453.3331 | 459.0963 | 376.1918
2096.9417 | 418.6927 | 453.0371 | 458.9225 | 376.5256
2097.9417 | 417.3183 | 452.8073 | 459.8519 | 377.7835
2098.9417 | 415.4746 | 451.928 | 459.5814 | 378.1624
2099.9417 | 413.9368 | 451.7611 | 456.4371 | 379.8325
2100.9417 | 413.5891 | 451.9308 | 456.1791 | 379.5484
2101.9417 | 411.9165 | 451.394 | 454.1362 | 378.5395
2102.9417 | 410.9101 | 453.0113 | 453.2636 | 378.1951
2103.9417 | 409.0926 | 452.571 | 452.36 | 377.6901
2104.9417 | 408.7712 | 452.5751 | 452.4526 | 377.2403
2105.9417 | 408.443 | 452.2441 | 452.6381 | 377.644
2106.9417 | 407.5765 | 451.8285 | 453.1531 | 378.5725
2107.9417 | 407.1516 | 452.2606 | 452.2294 | 378.9232
2108.9417 | 405.0005 | 451.8246 | 451.9246 | 378.4595
2109.9417 | 404.7413 | 451.9878 | 451.7817 | 378.1742
2110.9417 | 405.6179 | 452.0529 | 451.0606 | 377.287
2111.9417 | 405.6564 | 452.1956 | 450.0644 | 376.5066
2112.9417 | 404.9299 | 452.8052 | 449.8646 | 375.6209
2113.9417 | 408.0754 | 454.5688 | 451.4329 | 375.4103
2114.9417 | 409.1053 | 453.1771 | 452.5151 | 375.2909
2115.9417 | 409.5711 | 452.4675 | 451.4449 | 375.1942
2116.9417 | 409.9401 | 454.4748 | 453.0442 | 376.2208
2117.9417 | 411.2606 | 456.1586 | 453.1622 | 376.089
2118.9417 | 413.3612 | 457.5076 | 453.4074 | 375.6862
2119.9417 | 413.671 | 457.4329 | 452.9968 | 375.764
2120.9417 | 414.3228 | 457.4404 | 454.1923 | 376.8664
2121.9417 | 416.1661 | 459.6685 | 457.4079 | 378.9591
2122.9417 | 417.7071 | 458.7606 | 458.1147 | 379.8815
2123.9417 | 417.2581 | 459.6371 | 458.3147 | 380.5317
2124.9417 | 416.9433 | 460.3668 | 459.1315 | 381.4432
2125.9417 | 416.8594 | 463.4115 | 459.9072 | 381.113
2126.9417 | 416.3575 | 463.9819 | 458.7047 | 380.6648
2127.9417 | 415.6329 | 463.8078 | 459.4444 | 380.5632
2128.9417 | 415.145 | 464.7635 | 460.6501 | 381.8357
2129.9417 | 416.9787 | 465.9423 | 461.0174 | 382.0845
2130.9417 | 417.7843 | 465.7591 | 462.3269 | 383.6167
2131.9417 | 418.01 | 465.5557 | 465.3836 | 385.9159
2132.9417 | 419.9493 | 467.0176 | 467.4455 | 387.9474
2133.9417 | 420.1382 | 467.7808 | 469.6103 | 388.0861
2134.9417 | 420.9426 | 467.676 | 469.0255 | 387.9777
2135.9417 | 422.1103 | 467.7102 | 470.9884 | 388.0344
2136.9417 | 422.6931 | 468.5629 | 473.56 | 388.1309
2137.9417 | 423.9237 | 469.4551 | 476.9836 | 388.534
2138.9417 | 426.4285 | 469.6332 | 478.523 | 390.0402
2139.9417 | 427.9796 | 470.0551 | 481.5723 | 390.6369
2140.9417 | 427.7537 | 471.1698 | 482.0031 | 392.6242
2141.9417 | 427.9529 | 470.6281 | 482.3677 | 392.1139
2142.9417 | 428.7101 | 468.6131 | 481.6339 | 392.5515
2143.9417 | 430.4009 | 468.666 | 480.7177 | 395.2685
2144.9417 | 432.0087 | 468.4811 | 480.9885 | 395.1075
2145.9417 | 430.6371 | 468.307 | 481.3299 | 395.4077
2146.9417 | 428.4005 | 468.5239 | 479.4063 | 395.4436
2147.9417 | 426.5502 | 467.5304 | 476.7304 | 394.5076
2148.9417 | 426.4676 | 467.1483 | 475.4232 | 395.5651
2149.9417 | 426.5312 | 466.6554 | 473.0836 | 394.107
2150.9417 | 425.0936 | 467.0737 | 472.6186 | 393.5872
2151.9417 | 424.3196 | 466.7933 | 472.6939 | 393.4028
2152.9417 | 424.0935 | 466.0502 | 471.8592 | 394.1977
2153.9417 | 425.4499 | 466.9914 | 475.5833 | 394.7134
2154.9417 | 425.8107 | 467.086 | 477.4742 | 395.4104
2155.9417 | 427.3223 | 467.7217 | 477.9253 | 396.7263
2156.9417 | 427.5609 | 466.4494 | 482.7553 | 398.2562
2157.9417 | 428.0107 | 466.2276 | 483.0662 | 398.1094
2158.9417 | 427.7078 | 466.4045 | 482.618 | 398.186
2159.9417 | 427.4058 | 466.772 | 482.023 | 397.8326
2160.9417 | 427.7657 | 466.1688 | 480.3999 | 397.0207
2161.9417 | 428.9251 | 465.2164 | 480.9228 | 397.7128
2162.9417 | 429.1412 | 465.8522 | 482.1056 | 398.1909
2163.9417 | 431.4087 | 465.5939 | 481.9344 | 399.4394
2164.9417 | 431.1392 | 465.2828 | 483.8295 | 399.6302
2165.9417 | 433.4701 | 466.9306 | 485.7582 | 401.5208
2166.9417 | 434.466 | 468.5839 | 492.0424 | 404.0979
2167.9417 | 435.0107 | 469.5833 | 497.4594 | 405.1957
2168.9417 | 435.361 | 469.9897 | 498.0806 | 405.1741
2169.9417 | 434.9276 | 471.6916 | 500.3206 | 404.3541
2170.9417 | 434.3978 | 471.4845 | 497.2548 | 403.3904
2171.9417 | 432.7382 | 470.7132 | 494.6288 | 401.5419
2172.9417 | 432.2113 | 471.8085 | 496.4845 | 401.3696
2173.9417 | 434.2213 | 474.3854 | 498.7385 | 402.1582
2174.9417 | 433.2315 | 474.7159 | 497.2764 | 401.3242
2175.9417 | 431.4975 | 475.5697 | 493.6323 | 400.2184
2176.9417 | 429.8361 | 476.6823 | 489.9547 | 399.0387
2177.9417 | 428.128 | 477.3887 | 487.1442 | 397.8675
2178.9417 | 428.0163 | 477.4597 | 486.4743 | 397.5712
2179.9417 | 428.141 | 478.2747 | 486.1305 | 397.9232
2180.9417 | 428.9585 | 479.78 | 485.534 | 397.6596
2181.9417 | 430.6404 | 480.0709 | 484.8997 | 397.3872
2182.9417 | 429.7535 | 477.966 | 483.8324 | 396.9166
2183.9417 | 429.2227 | 478.8347 | 483.7123 | 397.3288
2184.9417 | 427.6756 | 479.6335 | 482.9144 | 397.9061
2185.9417 | 427.6449 | 480.3566 | 481.6663 | 396.5194
2186.9573 | 426.6654 | 481.2254 | 479.5084 | 395.8733
2187.9417 | 426.6602 | 480.9984 | 481.0121 | 395.7107
2188.9417 | 424.248 | 479.1164 | 477.3385 | 394.383
2189.9417 | 424.2451 | 479.7271 | 478.4508 | 394.9127
2190.9417 | 426.366 | 480.8284 | 479.4892 | 397.6096
2191.9417 | 428.7965 | 480.7453 | 479.1592 | 397.9762
2192.9417 | 428.8665 | 480.9739 | 480.282 | 397.5802
2193.9417 | 427.9012 | 480.4626 | 481.4159 | 396.9456
2194.9417 | 428.1409 | 480.8509 | 480.8392 | 396.7181
2195.9417 | 428.0819 | 481.384 | 483.2627 | 396.7857
2196.9417 | 429.0173 | 481.6291 | 483.7726 | 396.3344
2197.9417 | 430.1788 | 482.7413 | 484.1063 | 396.8153
2198.9417 | 432.8322 | 483.3662 | 482.9678 | 396.8406
2199.9417 | 432.7258 | 483.1699 | 481.2588 | 395.9939
2200.9417 | 435.3407 | 484.3281 | 483.9223 | 397.0123
2201.9417 | 437.3979 | 484.0852 | 483.7728 | 396.6542
2202.9417 | 438.4274 | 482.1712 | 484.502 | 396.4528
2203.9417 | 437.8142 | 481.6477 | 484.6859 | 397.0303
2204.9417 | 437.2126 | 482.6333 | 489.5563 | 398.7466
2205.9417 | 435.9973 | 483.3929 | 491.3752 | 398.6461
2206.9417 | 436.0631 | 485.2719 | 492.661 | 398.4664
2207.9417 | 437.2614 | 485.9512 | 495.4052 | 398.7286
2208.9417 | 439.4239 | 487.2517 | 500.8231 | 401.1849
2209.9417 | 441.6501 | 486.7499 | 504.8221 | 403.6425
2210.9417 | 443.1516 | 487.1264 | 507.7366 | 404.5242
2211.9417 | 443.6555 | 486.8443 | 508.7052 | 404.8316
2212.9417 | 445.251 | 488.0858 | 513.0732 | 405.6335
2213.9417 | 446.3243 | 490.4273 | 516.499 | 405.9761
2214.9417 | 446.0177 | 492.047 | 518.2055 | 406.6998
2215.9417 | 444.937 | 495.0604 | 518.3788 | 406.2307
2216.9417 | 444.1047 | 496.5984 | 517.016 | 406.6765
2217.9417 | 445.2899 | 496.0887 | 522.2749 | 407.8575
2218.9417 | 446.1338 | 498.704 | 527.3515 | 410.6866
2219.9417 | 445.5977 | 499.9985 | 528.2778 | 410.3835
2220.9417 | 444.7278 | 501.7962 | 531.8118 | 410.2355
2221.9417 | 445.3915 | 504.6946 | 534.1455 | 410.0206
2222.9417 | 445.2623 | 506.0667 | 535.221 | 409.1535
2223.9417 | 446.5959 | 509.7679 | 541.9746 | 409.343
2224.9417 | 446.5429 | 512.103 | 542.6807 | 410.2509
2225.9417 | 444.9597 | 512.2724 | 541.8253 | 409.7747
2226.9417 | 445.4812 | 514.9535 | 547.3606 | 410.0365
2227.9417 | 446.4329 | 514.5334 | 546.6538 | 410.3673
2228.9417 | 446.3447 | 516.3923 | 544.8666 | 409.7668
2229.9417 | 445.4772 | 516.3843 | 542.3722 | 408.7591
2230.9417 | 443.6343 | 515.8019 | 539.5498 | 408.6371
2231.9417 | 443.8828 | 515.7226 | 535.8294 | 409.0722
2232.9417 | 444.6229 | 517.4452 | 536.6406 | 410.2665
2233.9417 | 445.9999 | 518.989 | 536.9727 | 410.7431
2234.9417 | 445.3805 | 519.9262 | 535.3861 | 411.6283
2235.9417 | 447.0663 | 523.4052 | 540.7631 | 411.9772
2236.9417 | 448.506 | 527.5005 | 546.8046 | 412.6277
2237.9417 | 450.212 | 529.8556 | 546.1285 | 413.4483
2238.9417 | 452.4253 | 531.747 | 546.8405 | 414.1168
2239.9417 | 453.6468 | 532.8239 | 547.1615 | 415.3291
2240.9417 | 454.0836 | 533.8341 | 549.9325 | 416.1323
2241.9417 | 454.5831 | 537.3935 | 550.2865 | 416.3074
2242.9417 | 453.1395 | 541.5471 | 547.9784 | 417.2148
2243.9417 | 452.7033 | 544.4352 | 548.1054 | 417.5151
2244.9417 | 451.3989 | 545.8107 | 545.86 | 417.192
2245.9417 | 452.2807 | 545.4846 | 549.6859 | 417.1942
2246.9417 | 449.6343 | 546.0119 | 550.9733 | 416.3246
2247.9417 | 449.8212 | 547.0391 | 563.664 | 417.9833
2248.9417 | 450.5189 | 549.2423 | 565.287 | 419.7265
2249.9417 | 449.3928 | 549.728 | 559.2762 | 420.0367
2250.9417 | 449.3031 | 549.7679 | 558.5431 | 419.6431
2251.9417 | 450.853 | 551.941 | 557.0463 | 419.7013
2252.9417 | 451.338 | 551.88 | 558.0432 | 420.0863
2253.9417 | 451.2139 | 552.9035 | 555.6649 | 418.9465
2254.9417 | 449.3704 | 552.2023 | 574.5684 | 417.7382
2255.9417 | 448.3461 | 555.8069 | 588.498 | 417.3729
2256.9417 | 448.7169 | 556.0787 | 596.708 | 416.7266
2257.9417 | 448.1801 | 556.6399 | 626.2458 | 416.136
2258.9417 | 446.916 | 557.5061 | 649.2319 | 415.381
2259.9417 | 446.4249 | 560.6434 | 650.3263 | 414.9005
2260.9417 | 445.9127 | 565.8271 | 645.4826 | 415.0705
2261.9417 | 448.3939 | 571.0893 | 637.581 | 415.6711
2262.9417 | 450.3527 | 569.9283 | 622.7631 | 415.2779
2263.9573 | 453.9484 | 584.5247 | 628.4558 | 415.7058
2264.9417 | 452.1516 | 587.5276 | 622.1218 | 415.4748
2265.9417 | 452.4827 | 592.1173 | 628.0247 | 415.5788
2266.9417 | 452.4194 | 595.3801 | 619.6773 | 416.0895
2267.9417 | 452.3169 | 599.804 | 609.3712 | 415.7926
2268.9573 | 453.6531 | 603.3321 | 600.9428 | 417.5111
2269.9417 | 454.3208 | 602.6868 | 596.3751 | 420.8164
2270.9417 | 456.3328 | 603.9978 | 594.6972 | 421.4863
2271.9417 | 455.7896 | 600.766 | 588.3732 | 421.5703
2272.9417 | 456.3756 | 606.8919 | 581.0312 | 420.0736
2273.9417 | 457.4392 | 607.387 | 597.9232 | 419.4505
2274.9417 | 459.1725 | 612.1851 | 598.5445 | 419.6706
2275.9417 | 460.1563 | 611.0408 | 594.8632 | 420.6773
2276.9417 | 461.144 | 612.4583 | 595.5533 | 421.2782
2277.9417 | 462.4929 | 611.6227 | 593.8093 | 421.8875
2278.9417 | 463.9219 | 609.0357 | 592.4938 | 422.5381
2279.9417 | 465.8872 | 606.3078 | 586.8414 | 423.23
2280.9417 | 469.0638 | 614.5418 | 595.8545 | 424.1873
2281.9417 | 471.4892 | 614.606 | 593.9411 | 429.0547
2282.9417 | 472.0668 | 613.4337 | 593.8226 | 431.072
2283.9417 | 470.0379 | 610.8147 | 598.5258 | 430.5704
2284.9417 | 469.0906 | 610.8859 | 595.0298 | 430.7796
2285.9417 | 468.903 | 609.8707 | 594.9801 | 429.6792
2286.9417 | 468.1951 | 609.3367 | 602.4289 | 429.824
2287.9417 | 468.4075 | 606.9183 | 599.3326 | 429.5531
2288.9417 | 468.9025 | 605.6665 | 602.4962 | 428.7322
2289.9417 | 470.3143 | 606.596 | 600.8621 | 427.745
2290.9417 | 470.3244 | 603.375 | 599.8659 | 427.7459
2291.9417 | 469.522 | 599.7107 | 597.7229 | 428.9924
2292.9417 | 468.6189 | 599.6812 | 600.0629 | 428.5676
2293.9417 | 469.1097 | 605.6995 | 609.021 | 428.1772
2294.9417 | 468.4825 | 606.8377 | 621.9909 | 426.8467
2295.9417 | 468.5643 | 607.0872 | 628.308 | 426.35
2296.9417 | 467.1148 | 608.835 | 631.5206 | 426.158
2297.9417 | 465.7493 | 612.274 | 644.6347 | 426.5814
2298.9417 | 465.4918 | 611.8712 | 646.936 | 427.0509
2299.9417 | 465.6966 | 609.7234 | 637.6864 | 428.1264
2300.9417 | 465.3697 | 611.8514 | 630.1801 | 428.7078
2301.9417 | 465.9073 | 618.532 | 633.3695 | 428.8343
2302.9417 | 466.425 | 619.1132 | 646.8757 | 429.5243
2303.9417 | 467.5383 | 621.7017 | 661.4916 | 430.3894
2304.9417 | 470.3857 | 626.2258 | 671.9092 | 431.511
2305.9417 | 470.455 | 630.6326 | 680.1454 | 432.5126
2306.9417 | 470.8933 | 634.2161 | 687.3507 | 433.8981
2307.9417 | 469.7886 | 639.6434 | 698.599 | 434.6946
2308.9417 | 470.475 | 638.5953 | 695.3887 | 435.83
2309.9417 | 470.3155 | 639.2885 | 695.3551 | 437.7969
2310.9417 | 471.8026 | 645.3381 | 698.6233 | 439.0066
2311.9417 | 474.8033 | 644.9123 | 701.0939 | 440.7592
2312.9417 | 477.7307 | 645.0404 | 694.4226 | 443.9601
2313.9417 | 478.7538 | 648.6915 | 695.6329 | 445.4175
2314.9417 | 480.1627 | 648.964 | 700.217 | 445.9332
2315.9417 | 483.4094 | 649.4921 | 696.4313 | 446.9954
2316.9417 | 486.4742 | 651.2148 | 694.4726 | 446.6524
2317.9417 | 490.7034 | 649.1613 | 692.9941 | 447.0707
2318.9417 | 490.7568 | 648.2709 | 694.7531 | 448.7757
2319.9417 | 491.3899 | 650.1795 | 699.4142 | 450.9958
2320.9417 | 494.3359 | 654.093 | 706.4943 | 451.6879
2321.9417 | 498.8695 | 655.2291 | 709.0984 | 453.3562
2322.9417 | 502.8368 | 654.5223 | 713.9386 | 455.9444
2323.9417 | 506.9492 | 653.7735 | 710.5952 | 457.2351
2324.9417 | 509.4523 | 650.7178 | 710.1325 | 457.6529
2325.9417 | 510.475 | 647.4728 | 718.912 | 457.9348
2326.9417 | 511.2955 | 650.2907 | 731.6948 | 458.0105
2327.9417 | 511.1359 | 647.1073 | 728.0389 | 459.0968
2328.9417 | 513.1823 | 648.0687 | 716.3784 | 459.6728
2329.9417 | 516.8843 | 652.7343 | 710.7848 | 462.1384
2330.9417 | 515.5999 | 654.6247 | 710.0989 | 462.6684
2331.9417 | 517.44 | 655.2578 | 698.0357 | 465.1392
2332.9417 | 518.053 | 659.577 | 692.7817 | 464.7632
2333.9417 | 517.4904 | 663.1196 | 695.3395 | 467.7319
2334.9417 | 517.0795 | 665.2881 | 700.221 | 467.9057
2335.9417 | 518.1944 | 660.7971 | 700.0303 | 470.237
2336.9417 | 518.848 | 659.5164 | 702.2715 | 469.635
2337.9417 | 519.518 | 662.8933 | 700.4327 | 470.0929
2338.9417 | 519.7905 | 664.9005 | 695.7762 | 471.0293
2339.9417 | 520.8137 | 668.5065 | 704.9708 | 471.8512
2340.9417 | 521.3101 | 668.9745 | 710.7506 | 473.0512
2341.9417 | 519.9754 | 672.5754 | 718.5821 | 472.403
2342.9417 | 517.6682 | 671.1115 | 711.6142 | 471.2827
2343.9417 | 519.1034 | 672.1344 | 715.0535 | 471.3257
2344.9417 | 519.3299 | 668.8918 | 704.4928 | 470.2175
2345.9417 | 518.2486 | 666.7744 | 694.2996 | 469.3072
2346.9417 | 517.3604 | 674.1958 | 696.4107 | 470.2485
2347.9417 | 517.898 | 674.7364 | 695.2095 | 472.7356
2348.9417 | 517.2592 | 679.8166 | 694.6907 | 473.4601
2349.9417 | 516.7899 | 679.3759 | 706.7451 | 474.1718
2350.9417 | 515.4847 | 681.6931 | 707.879 | 474.5645
2351.9417 | 517.8989 | 681.5998 | 703.7243 | 478.321
2352.9417 | 519.4518 | 681.8054 | 700.0645 | 481.1548
2353.9417 | 522.142 | 684.06 | 708.8561 | 481.3875
2354.9417 | 522.7623 | 683.1583 | 705.374 | 485.9507
2355.9417 | 522.3155 | 681.03 | 699.8952 | 489.0475
2356.9417 | 525.4901 | 680.7568 | 698.0845 | 488.9012
2357.9417 | 524.9966 | 680.5805 | 691.4801 | 489.7622
2358.9417 | 524.5201 | 677.7208 | 696.7864 | 489.6421
2359.9417 | 525.8965 | 674.0742 | 699.3877 | 489.5787
2360.9417 | 525.6928 | 674.0144 | 692.7471 | 488.7708
2361.9417 | 527.4803 | 673.2545 | 695.4137 | 490.0445
2362.9417 | 530.0882 | 673.7999 | 694.2407 | 490.4184
2363.9417 | 529.6756 | 673.5891 | 691.7476 | 489.8639
2364.9417 | 531.4308 | 675.4347 | 691.5459 | 490.9928
2365.9417 | 532.0499 | 674.0287 | 690.4821 | 491.4723
2366.9417 | 534.4053 | 676.6327 | 693.8296 | 494.9433
2367.9417 | 534.3543 | 676.5159 | 692.3154 | 496.522
2368.9417 | 532.4265 | 677.4521 | 691.1258 | 497.438
2369.9417 | 533.3546 | 679.0046 | 700.0343 | 497.5856
2370.9417 | 534.0295 | 678.8544 | 711.3452 | 501.258
2371.9417 | 534.3841 | 680.2167 | 720.5158 | 502.3526
2372.9417 | 534.2636 | 681.0036 | 720.0167 | 503.1611
2373.9417 | 533.7781 | 683.5254 | 730.6815 | 502.4287
2374.9417 | 531.0007 | 687.2889 | 746.7761 | 502.3784
2375.9417 | 529.6397 | 690.983 | 748.0097 | 503.0233
2376.9417 | 529.7765 | 692.0413 | 757.1918 | 503.6772
2377.9417 | 530.4618 | 694.2727 | 759.0132 | 504.4517
2378.9417 | 529.2506 | 696.8127 | 763.715 | 504.3843
2379.9417 | 528.2987 | 697.8652 | 746.922 | 504.6259
2380.9417 | 529.9162 | 694.9659 | 738.9149 | 505.9312
2381.9417 | 529.9126 | 691.9693 | 729.054 | 506.2064
2382.9417 | 529.0533 | 688.8021 | 719.1475 | 505.6485
2383.9417 | 527.1742 | 685.5388 | 715.2902 | 505.1017
2384.9417 | 524.8355 | 687.124 | 706.015 | 504.6049
2385.9417 | 523.8671 | 685.088 | 699.1183 | 508.1613
2386.9417 | 525.7121 | 683.3308 | 695.7064 | 510.8135
2387.9417 | 526.3411 | 680.8166 | 689.7938 | 513.327
2388.9573 | 529.8573 | 680.8642 | 698.0328 | 511.9051
2389.9417 | 529.4632 | 679.2208 | 705.9732 | 511.4153
2390.9417 | 530.0273 | 679.5 | 714.2983 | 512.935
2391.9417 | 528.8202 | 681.8878 | 721.2635 | 514.2889
2392.9417 | 526.9176 | 683.205 | 733.2921 | 513.9609
2393.9417 | 525.9321 | 682.1667 | 725.6049 | 515.8823
2394.9417 | 524.6976 | 682.503 | 727.7548 | 518.1557
2395.9417 | 525.8354 | 681.8165 | 718.1194 | 520.8093
2396.9417 | 528.7729 | 681.6248 | 712.6935 | 520.2493
2397.9417 | 532.0945 | 679.9246 | 704.5944 | 522.3222
2398.9417 | 534.2354 | 680.5034 | 697.0466 | 522.024
2399.9417 | 532.1346 | 682.1989 | 693.9094 | 520.6283
2400.9417 | 532.4085 | 684.4256 | 699.0904 | 521.0034
2401.9417 | 533.0076 | 686.3119 | 697.0087 | 520.7039
2402.9417 | 532.5224 | 689.3653 | 699.898 | 520.6394
2403.9417 | 533.5835 | 688.3962 | 694.4724 | 521.2537
2404.9417 | 532.1802 | 688.5422 | 693.632 | 523.9586
2405.9417 | 530.6351 | 692.0364 | 692.5997 | 524.3228
2406.9417 | 529.9378 | 694.2624 | 713.6946 | 523.983
2407.9417 | 528.4845 | 697.3767 | 710.0229 | 523.1173
2408.9417 | 527.5047 | 695.8529 | 703.339 | 522.9726
2409.9417 | 524.63 | 693.5928 | 696.4552 | 524.6565
2410.9417 | 522.9142 | 689.2228 | 689.8701 | 524.7332
2411.9417 | 521.2609 | 687.8075 | 681.937 | 523.0069
2412.9417 | 519.9896 | 689.4785 | 676.5043 | 524.3836
2413.9417 | 519.932 | 690.692 | 681.221 | 522.6942
2414.9417 | 520.8992 | 690.8181 | 698.0094 | 523.636
2415.9417 | 521.645 | 690.6819 | 695.7118 | 523.748
2416.9417 | 520.7081 | 693.4088 | 690.1812 | 522.9506
2417.9417 | 521.8344 | 694.3678 | 690.5713 | 524.577
2418.9417 | 520.5681 | 690.096 | 687.6206 | 525.6126
2419.9417 | 520.7173 | 688.1877 | 681.4698 | 527.126
2420.9417 | 521.6106 | 688.1051 | 677.63 | 527.8286
2421.9573 | 519.6726 | 687.9251 | 673.346 | 528.0592
2422.9417 | 521.8125 | 688.1155 | 673.3532 | 528.3656
2423.9417 | 526.1176 | 687.5159 | 676.3899 | 530.5214
2424.9417 | 528.3882 | 689.9074 | 676.8725 | 530.9887
2425.9573 | 527.4891 | 691.9033 | 674.5744 | 530.2098
2426.9417 | 527.7139 | 690.2175 | 672.505 | 532.41
2427.9573 | 527.4007 | 688.3078 | 667.672 | 533.2677
2428.9573 | 526.5995 | 687.5501 | 664.7949 | 534.2666
2429.9573 | 525.697 | 684.5331 | 660.452 | 532.8405
2430.9417 | 524.6207 | 681.4343 | 657.5514 | 532.4774
2431.9417 | 526.4455 | 679.2248 | 656.1883 | 533.0417
2432.9573 | 526.7847 | 679.0268 | 652.4491 | 531.316
2433.9417 | 526.3669 | 677.8186 | 651.2217 | 530.8769
2434.9573 | 526.0902 | 677.7971 | 651.7094 | 529.5045
2435.9417 | 526.5933 | 677.2131 | 649.1806 | 528.7801
2436.9417 | 528.011 | 678.9938 | 647.9017 | 527.2481
2437.9417 | 529.4644 | 680.0602 | 654.3764 | 528.436
2438.9417 | 531.5491 | 680.307 | 661.5533 | 527.2945
2439.9417 | 530.6522 | 682.762 | 671.6603 | 528.0706
2440.9417 | 529.7423 | 681.7994 | 668.8107 | 526.352
2441.9417 | 530.3086 | 685.9228 | 676.0137 | 525.4384
2442.9417 | 528.6233 | 687.7577 | 673.4469 | 524.1038
2443.9417 | 527.1678 | 691.9981 | 677.19 | 523.0967
2444.9417 | 526.6446 | 694.019 | 677.0043 | 523.82
2445.9417 | 525.3143 | 700.1578 | 678.1238 | 524.0875
2446.9417 | 527.4376 | 703.6801 | 682.1717 | 524.7846
2447.9417 | 526.2245 | 704.9231 | 674.9241 | 525.3373
2448.9573 | 526.5144 | 706.7598 | 669.0774 | 523.3123
2449.9417 | 524.6008 | 707.0451 | 679.3935 | 522.778
2450.9417 | 524.7707 | 706.7923 | 687.4073 | 523.0528
2451.9417 | 527.0804 | 702.9613 | 680.298 | 524.2363
2452.9417 | 530.473 | 699.8926 | 681.2691 | 523.6171
2453.9417 | 530.799 | 703.2196 | 682.6653 | 525.3336
2454.9417 | 529.8453 | 704.2815 | 680.6707 | 524.7056
2455.9417 | 529.3824 | 704.748 | 678.4139 | 524.6843
2456.9417 | 528.3346 | 703.2021 | 677.823 | 524.8581
2457.9417 | 530.998 | 701.6385 | 674.4511 | 528.1255
2458.9417 | 532.3586 | 698.9859 | 668.7155 | 529.4207
2459.9417 | 534.3301 | 699.5024 | 669.0958 | 529.6265
2460.9417 | 534.3265 | 698.0303 | 665.6275 | 527.1894
2461.9417 | 534.4919 | 696.9313 | 665.0516 | 528.8463
2462.9417 | 535.0231 | 693.9271 | 661.311 | 530.5915
2463.9417 | 533.7529 | 692.9134 | 660.2449 | 530.4894
2464.9417 | 532.4478 | 691.4103 | 653.5945 | 530.6645
2465.9417 | 538.1186 | 698.3673 | 652.7972 | 531.5827
2466.9417 | 541.7055 | 698.6265 | 663.7299 | 531.78
2467.9417 | 539.0077 | 697.2798 | 659.12 | 532.0693
2468.9417 | 534.8968 | 695.2603 | 656.7954 | 530.2729
2469.9417 | 534.2092 | 695.261 | 653.1401 | 529.7897
2470.9417 | 533.5163 | 693.4017 | 648.6183 | 529.2546
2471.9417 | 532.385 | 693.0052 | 648.5095 | 529.6086
2472.9417 | 529.1856 | 694.1967 | 648.7873 | 528.413
2473.9417 | 527.7974 | 695.7647 | 650.7295 | 527.3464
2474.9417 | 527.0107 | 699.5066 | 664.3295 | 524.792
2475.9417 | 529.0243 | 698.7681 | 662.8387 | 525.9439
2476.9417 | 531.0467 | 700.818 | 661.207 | 526.907
2477.9417 | 535.3936 | 699.7426 | 658.0527 | 533.2354
2478.9417 | 538.8041 | 699.2902 | 658.6948 | 531.3675
2479.9417 | 537.5511 | 699.7972 | 662.222 | 530.6984
2480.9417 | 533.4283 | 701.0847 | 660.7027 | 532.9239
2481.9417 | 532.4523 | 703.0394 | 657.0309 | 531.8797
2482.9417 | 531.0833 | 702.4334 | 664.9852 | 532.3053
2483.9417 | 529.0303 | 703.9596 | 671.6133 | 534.5241
2484.9417 | 529.1208 | 707.6495 | 668.703 | 535.3529
2485.9417 | 529.2905 | 702.8051 | 665.3461 | 535.5499
2486.9417 | 527.824 | 700.8203 | 661.699 | 535.5383
2487.9417 | 530.5956 | 700.9336 | 659.724 | 536.2718
2488.9417 | 531.9795 | 697.6521 | 657.3821 | 536.1673
2489.9417 | 534.4116 | 696.2976 | 655.3475 | 537.346
2490.9417 | 536.3853 | 694.29 | 654.8212 | 536.1812
2491.9417 | 539.9497 | 692.0221 | 658.6042 | 538.1531
2492.9417 | 541.6552 | 692.674 | 667.9431 | 538.6
2493.9417 | 542.1059 | 694.118 | 669.2435 | 536.3588
2494.9417 | 545.5769 | 695.4184 | 673.6984 | 537.2352
2495.9417 | 551.0935 | 692.3608 | 684.7274 | 542.5908
2496.9417 | 554.1958 | 691.248 | 685.1817 | 550.8808
2497.9417 | 557.0317 | 693.703 | 682.4881 | 548.6011
2498.9417 | 556.037 | 694.0553 | 686.7898 | 549.0858
2499.9417 | 554.0567 | 692.7924 | 683.8438 | 546.0688
2500.9417 | 553.715 | 692.3052 | 682.881 | 548.1305
2501.9417 | 556.2735 | 694.9662 | 700.0151 | 551.9526
2502.9417 | 553.9301 | 698.1319 | 705.341 | 557.004
2503.9417 | 562.3468 | 698.2354 | 718.0749 | 568.3937
2504.9417 | 571.946 | 701.0666 | 720.1619 | 574.5419
2505.9417 | 570.5721 | 703.375 | 717.8247 | 579.3353
2506.9417 | 567.6926 | 708.1456 | 716.059 | 578.6075
2507.9417 | 567.7041 | 709.0798 | 723.6951 | 582.9558
2508.9417 | 566.873 | 708.1132 | 728.7535 | 585.8399
2509.9417 | 567.5582 | 706.2907 | 722.8726 | 586.954
2510.9417 | 569.0917 | 703.594 | 721.3095 | 589.0612
2511.9417 | 569.9186 | 701.4943 | 716.2981 | 589.6708
2512.9417 | 569.9097 | 705.2713 | 717.7586 | 592.5523
2513.9417 | 576.2123 | 709.8811 | 718.039 | 595.5321
2514.9417 | 576.8046 | 711.4861 | 715.566 | 597.6794
2515.9417 | 576.6543 | 711.3326 | 711.3397 | 605.9748
2516.9417 | 575.5711 | 712.3321 | 710.0535 | 608.1076
2517.9417 | 572.3842 | 712.8942 | 715.5046 | 609.888
2518.9417 | 572.5686 | 710.6884 | 710.065 | 606.6011
2519.9417 | 572.5619 | 710.249 | 703.6898 | 608.8769
2520.9417 | 584.3642 | 706.9792 | 697.0278 | 619.6467
2521.9417 | 580.1623 | 708.5505 | 692.2982 | 625.5622
2522.9417 | 582.2382 | 706.0403 | 689.5376 | 621.2494
2523.9417 | 582.313 | 704.3442 | 685.7267 | 615.6536
2524.9417 | 581.8809 | 701.8613 | 680.037 | 614.4114
2525.9417 | 578.5575 | 704.3095 | 681.4313 | 609.3435
2526.9417 | 580.1872 | 705.3955 | 675.2899 | 605.2548
2527.9417 | 581.511 | 704.8087 | 674.8505 | 603.7108
2528.9417 | 578.9384 | 703.3309 | 669.9525 | 602.8607
2529.9417 | 578.3439 | 701.5937 | 668.696 | 597.9589
2530.9417 | 574.41 | 700.8128 | 666.2559 | 593.3084
2531.9417 | 573.2464 | 696.8971 | 664.8122 | 590.7195
2532.9417 | 571.0626 | 696.0094 | 661.5422 | 587.2387
2533.9417 | 566.3411 | 697.1524 | 670.5569 | 589.8169
2534.9417 | 568.0459 | 701.3177 | 678.6135 | 588.2062
2535.9417 | 565.4435 | 700.6779 | 682.6608 | 586.7669
2536.9417 | 560.646 | 706.7592 | 678.6343 | 583.0791
2537.9417 | 561.1491 | 705.5614 | 676.6726 | 581.1525
2538.9417 | 557.0033 | 707.3384 | 676.5249 | 579.337
2539.9417 | 554.6221 | 706.1494 | 678.3656 | 576.3724
2540.9417 | 552.1512 | 704.6907 | 679.2783 | 576.089
2541.9417 | 551.2364 | 701.7455 | 675.0822 | 574.7841
2542.9417 | 551.2554 | 700.6231 | 674.768 | 574.4285
2543.9417 | 550.2514 | 702.574 | 677.5931 | 574.4147
2544.9417 | 550.2673 | 701.6586 | 675.9924 | 572.9128
2545.9417 | 549.192 | 699.878 | 676.778 | 571.9588
2546.9417 | 546.0566 | 704.7869 | 683.6141 | 579.9119
2547.9417 | 545.9626 | 709.7221 | 686.4013 | 581.6976
2548.9417 | 546.0963 | 709.5465 | 687.0933 | 578.8703
2549.9417 | 545.321 | 711.1716 | 686.8735 | 578.5938
2550.9417 | 545.1369 | 715.3872 | 683.2947 | 574.5383
2551.9417 | 545.5193 | 715.0439 | 680.3565 | 571.1591
2552.9417 | 545.1212 | 714.9606 | 682.5997 | 573.3455
2553.9417 | 544.451 | 709.9563 | 681.647 | 575.3648
2554.9417 | 545.0413 | 707.9179 | 680.0684 | 573.9027
2555.9417 | 544.1275 | 708.515 | 681.1858 | 573.2861
2556.9417 | 544.2434 | 708.8544 | 677.8507 | 574.5685
2557.9417 | 542.8825 | 711.1589 | 680.632 | 570.2863
2558.9417 | 540.7029 | 716.0885 | 690.5333 | 569.1786
2559.9417 | 539.7375 | 716.5805 | 691.03 | 571.2953
2560.9417 | 541.2744 | 717.065 | 692.4952 | 581.7652
2561.9417 | 544.1037 | 719.4936 | 704.227 | 579.1993
2562.9417 | 543.9952 | 718.777 | 700.7064 | 581.59
2563.9417 | 545.3665 | 717.8933 | 695.8799 | 587.263
2564.9417 | 544.3101 | 717.3117 | 694.009 | 583.9632
2565.9417 | 542.0243 | 715.5369 | 691.5968 | 581.2201
2566.9417 | 545.3012 | 715.4968 | 688.3646 | 579.0659
2567.9417 | 548.2865 | 710.8069 | 685.1692 | 577.4474
2568.9417 | 553.5696 | 710.7529 | 683.4536 | 578.5694
2569.9417 | 553.4991 | 708.4813 | 678.4485 | 577.8277
2570.9417 | 555.2732 | 706.4579 | 674.815 | 575.1331
2571.9417 | 554.5214 | 706.283 | 671.9347 | 573.9367
2572.9417 | 555.6664 | 704.8964 | 673.801 | 574.2956
2573.9417 | 557.2251 | 703.6341 | 673.0973 | 572.4401
2574.9417 | 560.99 | 702.4687 | 677.7897 | 572.6032
2575.9417 | 561.2891 | 700.5353 | 679.0204 | 572.216
2576.9417 | 565.4279 | 701.2243 | 683.87 | 573.4157
2577.9417 | 573.7981 | 703.6511 | 681.2724 | 575.6269
2578.9417 | 575.573 | 702.0352 | 677.7994 | 572.1072
2579.9417 | 577.5751 | 704.3994 | 679.7843 | 574.2518
2580.9417 | 588.8568 | 703.8177 | 679.1308 | 575.7269
2581.9417 | 614.5187 | 704.0493 | 680.6918 | 578.8979
2582.9417 | 623.9118 | 702.4333 | 678.4071 | 582.1421
2583.9417 | 613.4836 | 701.956 | 678.6172 | 584.055
2584.9417 | 616.9092 | 701.5802 | 686.2936 | 606.2839
2585.9417 | 613.7591 | 703.0186 | 687.4258 | 614.2862
2586.9417 | 610.445 | 701.8159 | 691.7866 | 617.0037
2587.9417 | 606.548 | 702.4134 | 695.917 | 619.6862
2588.9417 | 608.0114 | 704.3828 | 696.4597 | 619.2114
2589.9417 | 602.8588 | 704.8622 | 690.9019 | 616.4606
2590.9417 | 601.4631 | 705.2924 | 696.223 | 613.6692
2591.9417 | 596.8634 | 707.2514 | 714.693 | 623.2532
2592.9417 | 593.8786 | 705.2728 | 720.4857 | 623.6526
2593.9417 | 587.557 | 703.7005 | 710.9868 | 625.9232
2594.9417 | 584.7207 | 702.823 | 704.2112 | 631.935
2595.9417 | 579.6517 | 706.1653 | 698.5432 | 627.6018
2596.9417 | 575.5077 | 703.7335 | 688.9565 | 624.5947
2597.9417 | 572.4538 | 702.5409 | 684.7589 | 624.3892
2598.9417 | 569.8805 | 703.3741 | 701.1142 | 626.6784
2599.9417 | 568.0162 | 702.2048 | 711.0298 | 638.8568
2600.9417 | 566.6171 | 703.6454 | 710.9809 | 654.6669
2601.9417 | 567.0212 | 706.4037 | 705.226 | 649.1937
2602.9417 | 567.553 | 706.7811 | 700.7266 | 646.4731
2603.9417 | 583.2904 | 703.9849 | 698.4983 | 648.6761
2604.9417 | 580.2242 | 700.4722 | 697.4256 | 642.0925
2605.9417 | 578.7881 | 699.8073 | 695.2657 | 635.7388
2606.9417 | 577.1153 | 699.4225 | 693.2926 | 646.077
2607.9417 | 574.2635 | 698.8614 | 688.7087 | 640.587
2608.9417 | 578.1962 | 697.5876 | 688.325 | 643.2037
2609.9417 | 578.6967 | 699.4633 | 695.9023 | 643.7499
2610.9417 | 577.6217 | 699.125 | 687.7853 | 641.2157
2611.9417 | 572.9366 | 699.5618 | 693.9684 | 639.6982
2612.9417 | 570.7624 | 698.6526 | 700.4953 | 638.8638
2613.9417 | 566.1381 | 699.9038 | 702.8408 | 645.1125
2614.9417 | 568.6179 | 700.9283 | 693.8403 | 641.0995
2615.9417 | 565.3834 | 701.8638 | 692.8749 | 632.0426
2616.9417 | 566.8626 | 702.9561 | 708.1198 | 626.5696
2617.9417 | 566.9226 | 705.2633 | 702.3198 | 624.8169
2618.9417 | 575.9845 | 707.8224 | 703.1328 | 622.0555
2619.9417 | 574.1398 | 707.0201 | 699.4431 | 619.3113
2620.9417 | 575.8002 | 705.4648 | 693.0411 | 615.6149
2621.9417 | 573.66 | 702.8182 | 687.3999 | 615.3397
2622.9417 | 572.8529 | 700.4399 | 699.9859 | 613.8003
2623.9417 | 578.7466 | 701.1884 | 700.5788 | 610.578
2624.9417 | 578.7651 | 702.0749 | 700.906 | 613.9899
2625.9417 | 586.1025 | 705.1387 | 696.2233 | 614.3854
2626.9417 | 582.3751 | 708.3933 | 710.2847 | 610.8629
2627.9417 | 578.8243 | 713.9228 | 707.3308 | 615.6245
2628.9417 | 575.2241 | 715.1996 | 713.388 | 620.3602
2629.9417 | 574.7613 | 719.9924 | 708.407 | 619.3319
2630.9417 | 575.506 | 720.0191 | 705.6787 | 617.4422
2631.9417 | 571.9295 | 717.1594 | 700.2357 | 613.2005
2632.9417 | 568.1207 | 713.202 | 697.3334 | 609.2995
2633.9417 | 569.2843 | 714.3725 | 692.2399 | 605.4019
2634.9417 | 571.4937 | 710.7312 | 686.6266 | 602.5023
2635.9417 | 572.2273 | 706.6773 | 681.9752 | 600.2531
2636.9417 | 577.1118 | 705.5616 | 675.9309 | 597.5673
2637.9417 | 578.5172 | 705.6869 | 679.8613 | 596.8881
2638.9417 | 587.36 | 705.6335 | 680.3638 | 595.7157
2639.9417 | 585.7028 | 708.9793 | 684.7057 | 594.0418
2640.9417 | 593.0267 | 710.281 | 682.1762 | 596.8849
2641.9417 | 591.7778 | 713.8541 | 683.1695 | 596.3167
2642.9417 | 590.8446 | 715.9527 | 679.058 | 597.34
2643.9417 | 592.5867 | 714.2618 | 678.169 | 595.4176
2644.9417 | 594.5366 | 714.08 | 676.3492 | 594.207
2645.9417 | 591.9451 | 712.9925 | 674.499 | 595.3302
2646.9417 | 589.5347 | 707.7693 | 674.4694 | 594.3369
2647.9417 | 599.2669 | 705.445 | 672.2162 | 597.9382
2648.9417 | 600.6609 | 705.5978 | 675.105 | 597.5074
2649.9417 | 604.0755 | 703.3518 | 673.4765 | 598.2573
2650.9417 | 598.6414 | 704.1902 | 674.7441 | 597.8185
2651.9417 | 592.8424 | 703.5462 | 673.8855 | 593.8226
2652.9417 | 590.531 | 706.6963 | 684.6319 | 595.5536
2653.9417 | 589.6712 | 704.6642 | 689.2225 | 595.7345
2654.9417 | 588.691 | 705.9188 | 694.252 | 600.3144
2655.9417 | 589.2476 | 710.6196 | 699.2757 | 602.388
2656.9417 | 594.3653 | 711.9399 | 692.7958 | 601.4875
2657.9417 | 595.1424 | 713.3795 | 697.4778 | 599.2329
2658.9417 | 591.5163 | 712.0629 | 694.5615 | 600.8976
2659.9417 | 590.0303 | 711.7804 | 691.4533 | 601.5993
2660.9417 | 589.8529 | 711.8009 | 695.3217 | 602.0188
2661.9417 | 587.7183 | 712.2817 | 703.4394 | 598.5442
2662.9417 | 583.7756 | 712.4256 | 704.6747 | 596.9747
2663.9417 | 583.5831 | 710.5981 | 707.7174 | 599.9821
2664.9417 | 588.4622 | 710.2001 | 713.4411 | 600.7274
2665.9417 | 586.2492 | 710.548 | 702.0169 | 602.9154
2666.9417 | 583.247 | 710.995 | 700.7947 | 599.8904
2667.9417 | 580.8335 | 711.2975 | 706.7121 | 603.0489
2668.9417 | 579.0782 | 708.7712 | 707.7767 | 602.56
2669.9417 | 581.7783 | 706.6603 | 706.3144 | 602.8
2670.9417 | 585.1351 | 703.104 | 699.3246 | 602.7998
2671.9417 | 585.6341 | 703.6901 | 694.8023 | 601.5307
2672.9417 | 590.1663 | 702.1138 | 692.3285 | 600.831
2673.9417 | 591.8287 | 704.197 | 691.0964 | 600.5531
2674.9417 | 595.9914 | 704.5867 | 696.227 | 602.9142
2675.9417 | 592.9168 | 707.9115 | 696.1544 | 613.9231
2676.9417 | 600.6691 | 706.5727 | 698.9635 | 614.727
2677.9417 | 599.4525 | 705.8344 | 692.5226 | 610.4494
2678.9417 | 596.4717 | 704.9878 | 695.1426 | 607.7729
2679.9417 | 596.4344 | 705.4175 | 691.8869 | 605.8913
2680.9417 | 593.1137 | 705.3116 | 689.1283 | 607.7212
2681.9417 | 591.3445 | 706.5033 | 686.3448 | 606.4168
2682.9417 | 592.9229 | 707.1411 | 688.2157 | 607.2858
2683.9417 | 617.8888 | 709.0195 | 691.5291 | 614.5633
2684.9417 | 615.2471 | 709.1447 | 695.6933 | 614.1653
2685.9417 | 614.7682 | 709.2332 | 697.9976 | 613.817
2686.9417 | 607.4986 | 709.3226 | 700.1378 | 620.7485
2687.9417 | 609.9792 | 710.4551 | 711.3492 | 623.9119
2688.9417 | 615.9329 | 710.9922 | 710.2625 | 626.0702
2689.9417 | 633.4359 | 715.1386 | 709.8628 | 622.6407
2690.9417 | 635.5143 | 717.9739 | 722.014 | 619.6988
2691.9417 | 642.5679 | 718.3464 | 718.8931 | 615.9886
2692.9417 | 634.7707 | 717.8208 | 717.642 | 612.8101
2693.9417 | 635.6723 | 716.8169 | 712.7258 | 614.6431
2694.9417 | 630.2942 | 716.2566 | 708.8997 | 614.4525
2695.9417 | 625.0971 | 716.8463 | 716.7521 | 614.8442
2696.9417 | 623.8853 | 716.9019 | 712.1664 | 617.6685
2697.9417 | 619.9058 | 719.7677 | 720.1994 | 615.855
2698.9417 | 618.2444 | 717.2296 | 713.6124 | 619.1579
2699.9417 | 618.6403 | 715.1327 | 706.1126 | 614.8738
2700.9417 | 613.5166 | 715.14 | 700.2432 | 612.5282
2701.9417 | 622.178 | 711.4971 | 703.4722 | 610.2076
2702.9417 | 626.2963 | 708.7778 | 698.479 | 611.103
2703.9417 | 635.1261 | 709.8311 | 698.9484 | 612.5892
2704.9417 | 628.3584 | 713.1613 | 696.7098 | 611.1451
2705.9417 | 625.7445 | 715.0013 | 698.0481 | 619.0094
2706.9417 | 629.0049 | 713.3417 | 693.9842 | 618.0976
2707.9417 | 623.8342 | 713.9337 | 690.937 | 615.8718
2708.9417 | 617.7751 | 717.3766 | 683.5633 | 616.5167
2709.9417 | 609.6365 | 721.3804 | 696.7702 | 615.1462
2710.9417 | 606.1945 | 721.8136 | 699.6317 | 616.9541
2711.9417 | 603.4858 | 720.8164 | 700.6478 | 615.6787
2712.9417 | 605.3608 | 717.8292 | 693.9037 | 612.6754
2713.9417 | 606.4303 | 712.8165 | 688.7385 | 609.5137
2714.9417 | 605.8056 | 709.334 | 687.4954 | 607.7486
2715.9417 | 612.3211 | 708.661 | 686.2656 | 607.6092
2716.9417 | 610.8827 | 705.6033 | 686.3245 | 607.9755
2717.9417 | 615.6125 | 704.303 | 684.0329 | 608.61
2718.9417 | 616.2831 | 704.5743 | 681.8739 | 605.9568
2719.9417 | 614.4496 | 706.0605 | 679.6225 | 605.6417
2720.9417 | 615.6846 | 706.3954 | 677.9345 | 609.0748
2721.9417 | 623.0423 | 707.9549 | 678.0104 | 610.9428
2722.9417 | 618.6875 | 710.0312 | 684.5963 | 609.9525
2723.9417 | 627.2267 | 709.511 | 689.5036 | 609.5177
2724.9417 | 635.5558 | 707.9619 | 684.715 | 609.522
2725.9417 | 632.0373 | 709.3589 | 690.6437 | 610.5595
2726.9417 | 628.0208 | 711.6044 | 685.7756 | 610.7565
2727.9417 | 622.0967 | 711.0681 | 680.3528 | 609.9868
2728.9417 | 621.6154 | 708.9191 | 681.7767 | 612.6515
2729.9417 | 619.8664 | 707.119 | 684.9519 | 614.2516
2730.9417 | 615.9832 | 714.0587 | 694.0987 | 614.0517
2731.9417 | 618.0519 | 714.8916 | 701.2484 | 625.8492
2732.9417 | 611.5919 | 717.7049 | 711.3215 | 624.4193
2733.9417 | 607.9952 | 717.2514 | 711.5783 | 622.3317
2734.9417 | 603.2161 | 718.9508 | 713.4715 | 622.6961
2735.9417 | 600.4689 | 721.8026 | 708.0057 | 619.1081
2736.9417 | 601.6236 | 720.548 | 703.4427 | 616.8053
2737.9417 | 599.052 | 715.7322 | 697.8568 | 616.853
2738.9417 | 601.6847 | 712.8139 | 692.3767 | 618.0756
2739.9417 | 605.0228 | 711.3866 | 687.8015 | 617.1972
2740.9417 | 605.3364 | 708.2523 | 682.4496 | 614.7233
2741.9417 | 602.4653 | 706.4213 | 683.0951 | 614.5902
2742.9417 | 603.1162 | 704.694 | 678.6318 | 612.4994
2743.9417 | 604.0038 | 706.9061 | 685.8822 | 616.9339
2744.9417 | 606.7282 | 705.1121 | 683.1771 | 617.8531
2745.9417 | 604.2303 | 705.4372 | 682.8751 | 616.5424
2746.9417 | 617.9305 | 705.6352 | 685.8546 | 617.8353
2747.9417 | 617.3296 | 703.2991 | 684.4332 | 616.6216
2748.9417 | 622.7899 | 703.1614 | 680.6473 | 613.5373
2749.9417 | 629.7683 | 703.9111 | 684.4577 | 609.8112
2750.9417 | 629.8689 | 704.6064 | 680.1552 | 609.8173
2751.9417 | 643.4244 | 701.6759 | 678.6815 | 610.1122
2752.9417 | 642.3588 | 701.2776 | 681.1198 | 611.4122
2753.9417 | 648.3522 | 703.6637 | 680.5533 | 612.4971
2754.9417 | 653.5 | 706.5196 | 682.3448 | 614.9032
2755.9417 | 653.4186 | 706.6255 | 682.9011 | 616.2507
2756.9417 | 657.3439 | 705.0766 | 681.0695 | 616.7229
2757.9417 | 654.0747 | 707.0678 | 682.821 | 613.7744
2758.9417 | 651.1751 | 707.8282 | 681.6056 | 613.4408
2759.9417 | 658.7654 | 707.0398 | 680.2311 | 612.2444
2760.9417 | 655.5302 | 706.2782 | 680.3103 | 616.4126
2761.9417 | 648.7944 | 706.4582 | 678.4082 | 616.6534
2762.9417 | 652.9283 | 708.6708 | 685.6522 | 620.8131
2763.9417 | 654.7324 | 710.5286 | 685.808 | 628.3558
2764.9417 | 659.5945 | 712.7914 | 684.0926 | 625.2703
2765.9417 | 652.3076 | 711.9333 | 683.7827 | 622.6678
2766.9417 | 657.3049 | 714.1837 | 686.8166 | 625.0571
2767.9417 | 654.4622 | 715.1765 | 688.4722 | 630.3435
2768.9417 | 655.1346 | 718.0642 | 692.5094 | 628.0857
2769.9417 | 654.6226 | 720.1433 | 696.4218 | 632.1057
2770.9417 | 659.1102 | 720.0449 | 691.4302 | 629.2633
2771.9417 | 656.611 | 716.625 | 690.2387 | 630.6726
2772.9417 | 671.6778 | 720.6391 | 687.2136 | 647.1027
2773.9417 | 667.786 | 716.3895 | 693.6509 | 657.7903
2774.9417 | 662.6003 | 714.4686 | 695.5246 | 655.4268
2775.9417 | 663.8163 | 715.1802 | 702.3148 | 659.457
2776.9417 | 657.0877 | 715.9581 | 706.5156 | 662.3599
2777.9417 | 652.3408 | 713.3782 | 711.1281 | 669.305
2778.9417 | 662.4726 | 714.3847 | 710.9516 | 676.8073
2779.9417 | 680.3356 | 716.5631 | 715.0841 | 677.3609
2780.9417 | 677.9566 | 718.7435 | 719.7192 | 671.5335
2781.9417 | 667.7423 | 720.3633 | 731.0504 | 673.5003
2782.9417 | 669.8712 | 719.7106 | 731.4842 | 668.8785
2783.9417 | 664.4932 | 714.8743 | 731.8677 | 664.3268
2784.9417 | 661.8892 | 713.4997 | 737.0598 | 660.9183
2785.9417 | 659.0798 | 710.797 | 724.4249 | 656.4054
2786.9417 | 661.6568 | 712.0759 | 720.482 | 651.0225
2787.9417 | 662.4596 | 713.7795 | 724.2727 | 653.6082
2788.9417 | 658.0558 | 713.4472 | 720.2878 | 652.4909
2789.9417 | 655.9214 | 714.6865 | 713.5212 | 648.9628
2790.9417 | 659.547 | 713.2307 | 712.7511 | 646.6418
2791.9417 | 656.7502 | 711.8852 | 707.0353 | 640.9643
2792.9417 | 656.48 | 708.9252 | 702.5568 | 637.2212
2793.9417 | 667.6263 | 707.0782 | 704.6012 | 638.7247
2794.9417 | 671.3824 | 707.4312 | 705.5321 | 646.3213
2795.9417 | 686.6863 | 710.5553 | 705.9337 | 666.2753
2796.9417 | 688.058 | 712.0094 | 714.5068 | 662.7691
2797.9417 | 694.8509 | 712.71 | 727.8788 | 667.699
2798.9417 | 694.2886 | 713.6632 | 726.7036 | 663.3006
2799.9417 | 700.239 | 712.9774 | 719.6273 | 664.6142
2800.9417 | 696.8299 | 709.7425 | 713.0126 | 659.1709
2801.9417 | 693.0747 | 709.1288 | 705.7867 | 654.5452
2802.9417 | 686.2651 | 705.513 | 702.2557 | 650.326
2803.9417 | 686.1805 | 708.197 | 706.4137 | 648.7908
2804.9417 | 684.4138 | 711.3537 | 707.2575 | 650.3612
2805.9417 | 686.4265 | 710.9627 | 705.2042 | 648.8345
2806.9417 | 682.6857 | 711.0288 | 710.1884 | 654.3733
2807.9417 | 689.4711 | 712.7896 | 707.8462 | 657.8031
2808.9417 | 695.1912 | 712.253 | 709.6976 | 657.0388
2809.9417 | 693.2383 | 711.799 | 705.558 | 654.5208
2810.9417 | 697.3016 | 713.5352 | 709.1723 | 654.3685
2811.9417 | 683.7386 | 714.6141 | 707.6375 | 650.8396
2812.9417 | 682.0273 | 713.3097 | 700.5404 | 655.8097
2813.9417 | 679.8517 | 710.4532 | 700.7773 | 656.4364
2814.9417 | 673.3612 | 707.721 | 700.6958 | 653.33
2815.9417 | 671.0699 | 705.6685 | 698.9072 | 650.4471
2816.9417 | 670.9594 | 705.0538 | 696.5036 | 646.3556
2817.9417 | 663.1265 | 702.1363 | 695.1909 | 643.0227
2818.9417 | 661.825 | 702.6176 | 690.0225 | 639.6828
2819.9417 | 661.1527 | 704.5905 | 690.6345 | 636.8774
2820.9417 | 657.7331 | 704.9905 | 690.0232 | 635.4393
2821.9417 | 661.4609 | 704.2089 | 690.8999 | 646.2826
2822.9417 | 666.1719 | 703.1099 | 688.8367 | 641.2505
2823.9417 | 666.2946 | 705.9991 | 690.0565 | 637.9945
2824.9417 | 667.3308 | 705.9252 | 692.5881 | 639.433
2825.9417 | 666.6836 | 709.6078 | 693.0249 | 639.3724
2826.9417 | 667.8175 | 715.2328 | 706.4515 | 639.1342
2827.9417 | 679.7996 | 715.8052 | 704.7114 | 648.4642
2828.9417 | 684.2778 | 713.1996 | 710.7274 | 657.9129
2829.9417 | 695.1779 | 711.2496 | 705.9941 | 655.376
2830.9417 | 689.7966 | 709.6055 | 701.3895 | 648.6445
2831.9417 | 680.5801 | 712.0139 | 707.3182 | 643.8213
2832.9417 | 678.1515 | 713.2286 | 709.7099 | 643.6815
2833.9417 | 684.199 | 712.01 | 706.8711 | 642.924
2834.9417 | 679.2358 | 708.3486 | 699.6428 | 641.7458
2835.9417 | 674.3705 | 708.7523 | 698.0692 | 638.3148
2836.9417 | 680.1127 | 706.6372 | 695.9555 | 636.2502
2837.9417 | 675.804 | 706.138 | 696.54 | 636.1701
2838.9417 | 691.7853 | 706.8326 | 696.762 | 633.3406
2839.9417 | 688.0619 | 705.8271 | 701.6191 | 635.5071
2840.9417 | 698.2174 | 703.7539 | 710.9781 | 639.3866
2841.9417 | 704.0264 | 705.2776 | 714.7515 | 640.3262
2842.9417 | 703.883 | 705.7632 | 715.1435 | 646.6597
2843.9417 | 700.2272 | 704.7453 | 718.0362 | 645.6903
2844.9417 | 696.2732 | 703.6313 | 711.9486 | 647.5172
2845.9417 | 697.1083 | 701.0293 | 705.3983 | 651.2308
2846.9417 | 694.4687 | 700.7043 | 705.2302 | 652.5827
2847.9417 | 695.9393 | 702.6873 | 699.5108 | 645.7942
2848.9417 | 691.3876 | 701.2135 | 696.8457 | 642.1226
2849.9417 | 691.3172 | 702.1323 | 705.7299 | 643.1438
2850.9417 | 683.936 | 708.9429 | 705.1437 | 638.6335
2851.9417 | 700.4128 | 708.132 | 720.906 | 651.6403
2852.9417 | 706.0443 | 705.8735 | 722.4566 | 649.2169
2853.9417 | 708.4142 | 706.4215 | 723.0703 | 651.2973
2854.9417 | 710.8346 | 710.514 | 726.7987 | 650.0971
2855.9417 | 703.9417 | 708.0356 | 725.347 | 651.8021
2856.9417 | 723.057 | 708.3189 | 727.3762 | 657.9376
2857.9417 | 723.2682 | 708.0849 | 736.8234 | 665.4899
2858.9417 | 724.2155 | 716.3303 | 739.358 | 666.2763
2859.9417 | 715.8371 | 714.2632 | 730.7145 | 661.8778
2860.9417 | 717.9793 | 716.4027 | 726.0828 | 659.1652
2861.9417 | 720.7331 | 716.6151 | 722.5087 | 655.4538
2862.9417 | 725.791 | 716.0959 | 725.4654 | 661.5418
2863.9417 | 732.9204 | 721.3691 | 733.7229 | 662.9762
2864.9417 | 736.6316 | 716.7398 | 736.3565 | 661.5044
2865.9417 | 731.7836 | 717.5319 | 743.344 | 662.2215
2866.9417 | 724.7599 | 715.3798 | 736.4403 | 663.6712
2867.9417 | 718.8151 | 712.9122 | 732.4745 | 663.1616
2868.9417 | 724.3425 | 712.0563 | 730.1045 | 668.0959
2869.9417 | 731.2397 | 712.902 | 729.5933 | 670.2343
2870.9417 | 728.4312 | 710.0881 | 732.5997 | 670.3174
2871.9417 | 736.9113 | 710.5863 | 729.1163 | 666.9741
2872.9417 | 727.7567 | 708.646 | 727.4039 | 665.123
2873.9417 | 727.4436 | 714.3988 | 744.4472 | 663.3467
2874.9417 | 720.6998 | 713.798 | 741.1754 | 662.386
2875.9417 | 713.9607 | 710.0948 | 726.7395 | 665.2072
2876.9417 | 706.9354 | 709.8955 | 719.9045 | 662.0468
2877.9417 | 703.6983 | 710.2961 | 718.5903 | 660.4111
2878.9417 | 713.3727 | 710.4881 | 715.2132 | 657.77
2879.9417 | 711.5342 | 711.2758 | 719.37 | 656.3084
2880.9417 | 708.3388 | 711.9238 | 717.8135 | 655.4894
2881.9417 | 707.5275 | 710.9469 | 716.2069 | 655.5564
2882.9417 | 712.6635 | 710.8311 | 711.9496 | 656.563
2883.9417 | 714.2391 | 711.825 | 715.7085 | 657.9065
2884.9417 | 714.8143 | 713.1141 | 721.3004 | 660.1642
2885.9417 | 721.6523 | 713.5086 | 725.8587 | 663.6571
2886.9417 | 725.69 | 711.1558 | 727.2473 | 662.0613
2887.9417 | 725.3857 | 707.4292 | 730.4379 | 667.7519
2888.9417 | 723.7248 | 704.9884 | 729.8809 | 668.0839
2889.9417 | 721.3801 | 700.3809 | 717.4561 | 666.3685
2890.9417 | 715.8363 | 698.6864 | 710.6364 | 664.7506
2891.9417 | 708.2881 | 697.6339 | 707.0606 | 664.4446
2892.9417 | 709.1252 | 697.1008 | 706.993 | 661.6179
2893.9417 | 711.266 | 695.3313 | 701.9761 | 658.9687
2894.9417 | 713.7355 | 694.0595 | 704.881 | 657.367
2895.9417 | 715.2096 | 691.319 | 705.3485 | 657.6036
2896.9417 | 713.938 | 692.9971 | 707.3779 | 656.3083
2897.9417 | 713.6898 | 696.3735 | 715.0451 | 655.777
2898.9417 | 716.9743 | 695.5881 | 705.7975 | 656.8434
2899.9417 | 722.9426 | 694.7855 | 711.3929 | 655.8168
2900.9417 | 722.726 | 692.5804 | 705.9233 | 654.1834
2901.9417 | 732.3996 | 690.3918 | 705.3777 | 656.3825
2902.9417 | 739.2708 | 689.8206 | 704.7504 | 658.0403
2903.9417 | 738.6342 | 694.3602 | 704.6493 | 653.9707
2904.9417 | 724.3495 | 693.555 | 703.1327 | 649.5179
2905.9417 | 724.4238 | 690.6058 | 699.1804 | 649.9421
2906.9417 | 728.5545 | 692.7477 | 707.4716 | 653.0554
2907.9417 | 737.2383 | 694.9595 | 710.1471 | 652.239
2908.9417 | 736.6057 | 695.5041 | 716.0809 | 652.8421
2909.9417 | 729.7916 | 693.9 | 710.3364 | 652.2114
2910.9417 | 736.7108 | 690.9706 | 705.4055 | 652.8487
2911.9417 | 738.7834 | 690.9171 | 702.2819 | 656.7792
2912.9417 | 730.6457 | 690.2098 | 700.2817 | 651.5797
2913.9729 | 727.0041 | 692.049 | 701.6736 | 647.5684
2914.9417 | 724.2738 | 691.9616 | 707.6315 | 651.218
2915.9417 | 727.9565 | 690.2904 | 703.7388 | 648.9456
2916.9417 | 744.7047 | 687.2545 | 702.8591 | 646.5499
2917.9417 | 741.2905 | 684.8917 | 699.7038 | 644.2021
2918.9417 | 739.3172 | 683.7356 | 695.5714 | 643.5429
2919.9417 | 738.9673 | 685.1594 | 694.9408 | 644.8654
2920.9417 | 735.6804 | 685.3038 | 694.1908 | 641.6846
2921.9417 | 727.213 | 685.6373 | 698.258 | 643.4507
2922.9417 | 729.4394 | 684.8142 | 694.5309 | 644.0947
2923.9417 | 726.8421 | 682.8723 | 691.9922 | 643.5321
2924.9417 | 719.6264 | 679.3934 | 688.8204 | 641.7018
2925.9417 | 719.74 | 677.8298 | 686.9438 | 640.0641
2926.9417 | 722.2985 | 675.8382 | 682.6596 | 637.3785
2927.9417 | 725.6992 | 675.3527 | 682.6933 | 640.938
2928.9417 | 732.8814 | 674.4107 | 688.9454 | 645.4699
2929.9417 | 722.9113 | 674.3532 | 687.495 | 644.1506
2930.9417 | 723.3841 | 673.566 | 689.8806 | 645.0426
2931.9417 | 720.0528 | 672.4626 | 691.7393 | 650.7108
2932.9417 | 723.7255 | 670.8076 | 693.3883 | 649.0432
2933.9417 | 727.7729 | 670.344 | 695.8512 | 649.5217
2934.9417 | 721.4185 | 671.0598 | 697.0747 | 655.829
2935.9417 | 730.9901 | 672.5294 | 696.3083 | 659.0084
2936.9417 | 731.8145 | 673.4169 | 696.6812 | 659.0705
2937.9417 | 734.75 | 673.9223 | 702.0865 | 659.383
2938.9417 | 736.0164 | 673.8035 | 706.0501 | 658.1256
2939.9417 | 737.5089 | 672.8424 | 704.6351 | 656.97
2940.9417 | 745.5162 | 671.8107 | 700.8104 | 653.8582
2941.9417 | 740.0017 | 670.3929 | 699.1367 | 654.673
2942.9417 | 735.9862 | 669.7013 | 708.9203 | 652.9781
2943.9417 | 733.8492 | 669.6599 | 700.4531 | 660.7736
2944.9417 | 724.9528 | 668.2224 | 698.3486 | 654.9859
2945.9417 | 726.2018 | 670.6491 | 702.4461 | 654.8295
2946.9417 | 723.9741 | 671.478 | 701.4981 | 654.5894
2947.9417 | 728.0328 | 671.0496 | 694.7746 | 655.6738
2948.9417 | 721.9582 | 669.7864 | 695.7984 | 651.7549
2949.9417 | 718.2793 | 668.046 | 693.827 | 648.6378
2950.9573 | 728.1909 | 666.9192 | 692.6566 | 651.2643
2951.9417 | 730.5281 | 665.96 | 693.853 | 648.9578
2952.9417 | 721.5822 | 664.0078 | 691.952 | 657.7013
2953.9417 | 728.6917 | 665.0316 | 691.8008 | 658.4135
2954.9417 | 723.2008 | 664.7999 | 695.0353 | 656.8564
2955.9417 | 723.1826 | 664.6211 | 699.0339 | 656.0878
2956.9417 | 729.279 | 664.7757 | 695.1379 | 652.2312
2957.9417 | 727.2519 | 666.5454 | 693.362 | 650.5127
2958.9417 | 720.0708 | 668.6186 | 705.5345 | 648.5344
2959.9417 | 721.9642 | 668.5762 | 711.8752 | 651.495
2960.9417 | 714.9033 | 667.8707 | 703.9777 | 648.7124
2961.9417 | 724.6179 | 667.9365 | 703.2619 | 647.0472
2962.9417 | 719.748 | 666.3483 | 699.3342 | 648.8043
2963.9417 | 724.1217 | 666.174 | 698.7502 | 649.5022
2964.9417 | 725.9968 | 667.2608 | 699.3696 | 648.493
2965.9417 | 713.9933 | 667.5524 | 693.7861 | 648.067
2966.9417 | 715.9042 | 666.7539 | 686.3112 | 646.9698
2967.9417 | 722.4594 | 664.7234 | 686.7548 | 649.8522
2968.9417 | 734.6233 | 664.6338 | 688.129 | 656.944
2969.9417 | 728.1813 | 665.9465 | 695.278 | 659.964
2970.9417 | 736.634 | 669.3962 | 695.4688 | 657.2398
2971.9417 | 728.1478 | 670.8938 | 699.7406 | 654.9213
2972.9417 | 734.5498 | 669.2243 | 700.8343 | 652.8255
2973.9417 | 726.6343 | 666.7127 | 698.711 | 648.5663
2974.9417 | 724.5889 | 666.8869 | 699.6054 | 647.2889
2975.9417 | 732.3704 | 667.4687 | 703.2608 | 646.3205
2976.9417 | 734.0743 | 665.9112 | 703.4418 | 650.8369
2977.9417 | 729.8036 | 667.9315 | 701.4491 | 647.7438
2978.9417 | 727.208 | 671.1565 | 705.0827 | 646.1649
2979.9417 | 720.2783 | 670.327 | 699.8221 | 643.6758
2980.9573 | 719.4539 | 667.8338 | 702.9594 | 642.5104
2981.9417 | 722.7046 | 665.0674 | 703.5814 | 640.3134
2982.9417 | 723.3196 | 668.0932 | 705.8602 | 642.3802
2983.9417 | 727.1045 | 671.1605 | 707.8986 | 648.5608
2984.9417 | 735.1142 | 671.4138 | 709.937 | 648.2426
2985.9417 | 732.2151 | 671.3523 | 700.3219 | 648.9936
2986.9417 | 732.549 | 669.6668 | 694.1998 | 649.7403
2987.9417 | 734.2722 | 667.6332 | 692.89 | 649.7502
2988.9417 | 730.4306 | 665.8833 | 691.3316 | 648.0717
2989.9417 | 729.5384 | 663.9895 | 687.3856 | 645.4696
2990.9417 | 727.8225 | 663.9783 | 689.2686 | 649.9532
2991.9417 | 731.4506 | 665.2036 | 696.2404 | 657.8403
2992.9417 | 729.3155 | 666.4153 | 707.8256 | 657.8839
2993.9417 | 735.404 | 665.3142 | 705.5854 | 660.501
2994.9417 | 733.451 | 665.8148 | 705.9182 | 659.9842
2995.9417 | 736.6465 | 673.0549 | 709.7661 | 674.9297
2996.9417 | 733.1037 | 676.8012 | 710.6741 | 680.1956
2997.9417 | 732.1206 | 676.456 | 708.1818 | 675.7148
2998.9417 | 733.7197 | 677.8088 | 710.0547 | 673.4243
2999.9417 | 728.833 | 679.3967 | 713.5429 | 675.0351
3000.9417 | 736.6657 | 678.2187 | 718.0424 | 667.8808
3001.9417 | 735.0202 | 679.4736 | 719.5944 | 671.0536
3002.9417 | 736.7931 | 682.2446 | 714.4008 | 668.3177
3003.9417 | 734.1217 | 679.5345 | 707.4603 | 665.3546
3004.9417 | 736.1517 | 675.792 | 696.8689 | 659.0712
3005.9417 | 735.076 | 674.1499 | 692.1173 | 655.0745
3006.9417 | 735.4988 | 671.6261 | 686.6993 | 651.9216
3007.9417 | 728.3594 | 670.8546 | 691.4152 | 649.0267
3008.9417 | 722.2259 | 668.7164 | 689.298 | 647.3608
3009.9417 | 723.724 | 668.5308 | 689.3236 | 646.2597
3010.9417 | 731.3445 | 668.0296 | 690.046 | 646.1056
3011.9417 | 734.0583 | 667.1759 | 687.5039 | 644.7095
3012.9417 | 726.5016 | 667.0077 | 685.0096 | 649.8673
3013.9417 | 726.6811 | 665.7231 | 682.8529 | 647.6875
3014.9417 | 724.1017 | 664.1401 | 686.4674 | 645.758
3015.9417 | 725.5382 | 662.7936 | 683.9268 | 646.8169
3016.9417 | 725.1743 | 661.353 | 685.4077 | 649.0365
3017.9417 | 731.8287 | 660.069 | 678.2607 | 646.618
3018.9417 | 734.7802 | 658.3258 | 674.4373 | 643.707
3019.9417 | 730.9998 | 656.6051 | 671.4568 | 642.6888
3020.9417 | 725.0937 | 655.3379 | 667.831 | 641.9739
3021.9417 | 717.4465 | 655.5588 | 670.0311 | 643.1455
3022.9417 | 720.163 | 656.3646 | 671.6698 | 644.3947
3023.9417 | 727.413 | 656.1888 | 672.7967 | 643.6324
3024.9417 | 722.6209 | 653.9608 | 669.8556 | 643.8334
3025.9417 | 733.5943 | 652.5243 | 669.09 | 641.6336
3026.9417 | 746.1019 | 651.2912 | 664.7893 | 655.1789
3027.9417 | 741.9895 | 650.9942 | 662.6315 | 648.1648
3028.9417 | 740.939 | 650.8845 | 664.1474 | 646.5226
3029.9417 | 737.8796 | 651.2283 | 661.4989 | 643.8543
3030.9417 | 730.471 | 651.3824 | 665.9654 | 645.0206
3031.9417 | 729.0325 | 651.6087 | 666.5832 | 652.1104
3032.9417 | 735.8179 | 652.2211 | 666.1838 | 659.2776
3033.9417 | 740.5257 | 653.544 | 665.1806 | 656.7786
3034.9417 | 741.5732 | 653.5838 | 666.4085 | 656.1255
3035.9417 | 735.672 | 652.0034 | 665.7633 | 662.6534
3036.9417 | 728.9271 | 650.4184 | 662.0473 | 659.3245
3037.9417 | 725.87 | 650.1203 | 660.5414 | 656.6068
3038.9417 | 722.7941 | 649.1173 | 661.8184 | 654.8307
3039.9417 | 717.03 | 648.2473 | 663.5295 | 652.79
3040.9417 | 710.9746 | 648.173 | 674.2826 | 651.3546
3041.9417 | 704.1611 | 649.4308 | 674.7558 | 648.1859
3042.9417 | 704.3925 | 648.9982 | 677.9821 | 650.969
3043.9417 | 716.0755 | 648.3849 | 679.8676 | 653.936
3044.9417 | 709.9687 | 646.8735 | 678.2119 | 651.4955
3045.9417 | 706.1596 | 646.7769 | 673.1678 | 647.5743
3046.9417 | 711.3926 | 645.7171 | 672.5913 | 644.9678
3047.9417 | 715.6748 | 645.3734 | 672.6043 | 644.3855
3048.9417 | 715.8304 | 644.8769 | 671.8835 | 645.0678
3049.9417 | 711.4785 | 644.1372 | 671.7521 | 642.9143
3050.9417 | 716.5767 | 642.951 | 671.1382 | 644.9963
3051.9417 | 705.4744 | 642.7357 | 671.418 | 642.7656
3052.9417 | 700.3974 | 642.9719 | 667.8495 | 641.007
3053.9417 | 702.6965 | 645.2615 | 667.7718 | 642.3141
3054.9417 | 708.4149 | 644.6944 | 668.2109 | 641.4966
3055.9417 | 705.4436 | 644.2833 | 668.6985 | 642.1619
3056.9417 | 711.6827 | 643.5372 | 667.0879 | 645.5467
3057.9417 | 705.6194 | 641.5906 | 662.0911 | 641.4177
3058.9417 | 699.2074 | 640.5985 | 661.7278 | 637.9934
3059.9417 | 693.0511 | 639.797 | 660.3921 | 637.7263
3060.9417 | 692.7936 | 639.4434 | 659.9939 | 637.1707
3061.9417 | 706.1654 | 638.4306 | 656.8789 | 635.583
3062.9417 | 710.0637 | 638.5507 | 652.6282 | 633.9736
3063.9417 | 705.0821 | 638.0088 | 650.5297 | 631.8035
3064.9417 | 702.9826 | 637.78 | 653.2333 | 633.3799
3065.9417 | 702.9806 | 639.3664 | 654.4612 | 633.1895
3066.9417 | 714.8057 | 639.4719 | 655.8395 | 638.3771
3067.9417 | 717.9687 | 639.9892 | 657.939 | 644.1002
3068.9417 | 710.7401 | 640.7868 | 663.7545 | 648.1003
3069.9417 | 702.7726 | 643.1356 | 665.3125 | 648.4703
3070.9417 | 694.6379 | 643.2359 | 662.0608 | 645.4634
3071.9417 | 692.2121 | 642.3544 | 662.8716 | 644.5729
3072.9417 | 706.363 | 642.1729 | 665.5195 | 641.7238
3073.9417 | 714.8825 | 643.1636 | 664.5603 | 640.9159
3074.9417 | 721.5884 | 643.1672 | 662.2755 | 640.3158
3075.9417 | 714.1262 | 642.749 | 666.9275 | 637.7691
3076.9417 | 714.2621 | 644.4594 | 669.3097 | 640.3476
3077.9417 | 720.6463 | 645.1647 | 666.9332 | 640.8759
3078.9417 | 722.3776 | 644.7085 | 663.1198 | 639.3762
3079.9417 | 725.4323 | 646.8322 | 665.933 | 642.7671
3080.9417 | 719.4907 | 647.1386 | 665.9346 | 639.5172
3081.9417 | 711.1909 | 648.7921 | 685.8666 | 636.8863
3082.9417 | 716.0667 | 648.5567 | 685.339 | 637.9767
3083.9417 | 716.7688 | 651.3412 | 681.5068 | 636.8096
3084.9417 | 718.6203 | 650.3305 | 679.5828 | 642.2711
3085.9417 | 721.7138 | 652.1327 | 679.114 | 645.6524
3086.9417 | 716.3954 | 651.4021 | 675.7021 | 644.2511
3087.9417 | 713.8585 | 651.3722 | 675.3076 | 640.755
3088.9417 | 718.6576 | 650.1359 | 671.0253 | 637.5752
3089.9417 | 725.3847 | 648.4573 | 667.6587 | 643.9078
3090.9417 | 724.5469 | 646.9821 | 667.8236 | 649.7568
3091.9417 | 725.6715 | 646.651 | 668.2948 | 645.629
3092.9417 | 724.0761 | 645.2588 | 668.9741 | 646.0414
3093.9417 | 716.8777 | 643.2923 | 663.3959 | 643.8825
3094.9417 | 711.4032 | 641.8853 | 661.7738 | 643.6674
3095.9417 | 706.5561 | 641.2802 | 660.0497 | 643.6857
3096.9417 | 710.3722 | 643.1895 | 662.7879 | 642.8279
3097.9417 | 714.4983 | 644.6704 | 665.5316 | 643.3332
3098.9417 | 715.8085 | 643.9354 | 662.7513 | 642.4623
3099.9417 | 713.0971 | 641.3809 | 661.8769 | 649.0225
3100.9417 | 711.2638 | 639.7095 | 659.3107 | 645.5646
3101.9417 | 704.8735 | 639 | 657.2383 | 641.7723
3102.9417 | 705.5227 | 637.212 | 657.5405 | 637.6963
3103.9417 | 707.3336 | 636.2529 | 658.2759 | 639.0234
3104.9417 | 710.1161 | 637.116 | 657.0956 | 640.8469
3105.9417 | 706.5982 | 638.2436 | 656.6398 | 657.9986
3106.9417 | 710.2462 | 637.073 | 653.7021 | 659.7728
3107.9417 | 708.1168 | 635.5008 | 652.4633 | 660.2274
3108.9417 | 706.3862 | 635.6656 | 651.2251 | 654.7049
3109.9417 | 711.4363 | 635.3083 | 654.9538 | 651.752
3110.9417 | 709.1543 | 636.0632 | 656.0688 | 647.9398
3111.9417 | 711.7897 | 636.5165 | 653.0012 | 643.5386
3112.9417 | 711.6488 | 636.7685 | 652.0999 | 643.386
3113.9417 | 712.5611 | 638.2191 | 649.8928 | 642.6003
3114.9417 | 708.788 | 638.5252 | 653.4013 | 648.1376
3115.9417 | 709.7116 | 638.5614 | 657.1486 | 653.551
3116.9417 | 708.0592 | 638.4052 | 656.0187 | 648.3098
3117.9417 | 707.8352 | 638.9165 | 653.2288 | 644.0997
3118.9417 | 710.5969 | 638.299 | 652.8547 | 643.3299
3119.9417 | 711.1961 | 637.5935 | 652.5199 | 641.3461
3120.9417 | 711.6249 | 636.2111 | 649.0514 | 641.2235
3121.9417 | 716.9736 | 637.1497 | 649.8083 | 645.2489
3122.9417 | 714.5825 | 636.6707 | 651.5929 | 645.2273
3123.9417 | 711.9967 | 637.2612 | 653.2674 | 641.2362
3124.9417 | 712.0828 | 637.2677 | 653.9332 | 638.7927
3125.9417 | 709.5621 | 637.2815 | 654.4946 | 639.9276
3126.9417 | 711.0388 | 637.3381 | 653.0593 | 644.3873
3127.9417 | 705.9718 | 636.1203 | 650.1196 | 646.3033
3128.9417 | 710.4935 | 635.878 | 646.6007 | 644.2416
3129.9417 | 713.638 | 634.5321 | 649.6158 | 645.8342
3130.9417 | 705.2297 | 635.1576 | 649.2845 | 642.0553
3131.9417 | 704.4271 | 634.3999 | 649.0117 | 640.9711
3132.9417 | 708.6789 | 633.511 | 645.0946 | 636.9172
3133.9417 | 705.8185 | 632.8702 | 644.1932 | 633.1157
3134.9417 | 710.3741 | 632.8632 | 646.3948 | 632.0249
3135.9417 | 714.0955 | 632.9484 | 644.3213 | 635.7937
3136.9417 | 710.9691 | 630.8838 | 641.3976 | 636.6179
3137.9417 | 709.4785 | 631.0714 | 638.9469 | 634.7647
3138.9417 | 710.645 | 631.3599 | 641.0544 | 634.2674
3139.9417 | 715.0354 | 631.2552 | 640.5595 | 634.2705
3140.9417 | 715.1211 | 631.2949 | 643.5011 | 639.0271
3141.9417 | 716.695 | 631.7479 | 644.2917 | 636.6731
3142.9417 | 719.6424 | 634.192 | 649.9903 | 645.9966
3143.9417 | 717.5988 | 635.7046 | 651.2622 | 644.4433
3144.9417 | 722.4366 | 634.6331 | 652.5559 | 642.5963
3145.9417 | 712.8364 | 635.3193 | 651.7788 | 639.6349
3146.9417 | 716.8254 | 634.1177 | 651.3486 | 637.0511
3147.9417 | 720.1452 | 634.9224 | 650.47 | 638.1942
3148.9417 | 711.8437 | 633.5861 | 645.8482 | 636.7033
3149.9417 | 710.4644 | 633.0256 | 645.382 | 633.7573
3150.9417 | 712.0367 | 615.8281 | 646.5564 | 623.9133
3151.9417 | 706.6888 | 635.9367 | 640.0458 | 627.0848
3152.9417 | 712.6823 | 636.9995 | 653.0896 | 625.4842
3153.9417 | 708.7727 | 637.4946 | 651.5306 | 624.4453
3154.9417 | 706.7417 | 638.8037 | 650.1578 | 629.1905
3155.9417 | 712.1516 | 641.354 | 653.8215 | 631.3322
3156.9417 | 721.2908 | 639.8755 | 649.198 | 639.6872
3157.9417 | 727.925 | 639.76 | 652.1699 | 635.0501
3158.9417 | 728.5061 | 640.5104 | 650.97 | 630.3126
3159.9417 | 731.7323 | 641.7199 | 653.7515 | 627.2139
3160.9417 | 723.2936 | 641.0452 | 648.1321 | 629.1361
3161.9417 | 722.1674 | 641.8209 | 646.2277 | 625.6458
3162.9417 | 719.6156 | 640.6064 | 643.7486 | 629.2812
3163.9417 | 713.0074 | 639.4227 | 644.4785 | 626.6236
3164.9417 | 716.7077 | 638.8201 | 648.7321 | 631.1109
3165.9417 | 714.1019 | 638.24 | 649.0501 | 630.3812
3166.9417 | 708.1838 | 638.0106 | 644.3172 | 630.036
3167.9417 | 714.4474 | 637.6994 | 644.6805 | 628.3969
3168.9417 | 718.0886 | 637.38 | 645.027 | 631.3945
3169.9417 | 714.3689 | 637.1994 | 645.3648 | 630.4409
3170.9417 | 716.688 | 637.2798 | 645.2962 | 627.6937
3171.9417 | 710.7199 | 635.5942 | 642.8604 | 627.0623
3172.9417 | 707.8984 | 634.5948 | 639.4196 | 623.7085
3173.9417 | 713.2487 | 633.3158 | 644.5773 | 622.3129
3174.9417 | 722.4729 | 632.7983 | 645.4571 | 625.4749
3175.9417 | 722.6916 | 632.001 | 643.6599 | 625.1713
3176.9417 | 715.764 | 630.7075 | 642.6261 | 623.9896
3177.9417 | 707.4065 | 629.6375 | 641.3832 | 626.6554
3178.9417 | 702.828 | 629.0786 | 644.5787 | 629.1928
3179.9417 | 694.7499 | 628.9655 | 643.324 | 628.9063
3180.9417 | 694.4841 | 632.0047 | 643.0603 | 628.8553
3181.9417 | 691.5565 | 632.7786 | 656.2295 | 627.947
3182.9417 | 694.3479 | 632.5319 | 651.7935 | 626.4135
3183.9417 | 691.2577 | 632.6495 | 651.9598 | 629.1065
3184.9417 | 691.4747 | 630.7879 | 649.3647 | 628.445
3185.9417 | 688.849 | 632.0091 | 649.0009 | 630.7274
3186.9417 | 689.5442 | 633.2796 | 648.8761 | 630.4675
3187.9417 | 702.3415 | 633.2981 | 649.5423 | 628.6475
3188.9417 | 706.3147 | 632.5552 | 652.3795 | 631.844
3189.9417 | 701.7839 | 633.1724 | 655.6277 | 637.9072
3190.9417 | 695.6644 | 634.2474 | 656.147 | 643.5493
3191.9417 | 697.7752 | 635.5227 | 656.0789 | 644.4544
3192.9417 | 692.6717 | 635.9384 | 660.9962 | 641.3573
3193.9417 | 704.3915 | 637.4971 | 662.2604 | 639.3174
3194.9417 | 700.2465 | 639.3825 | 661.8335 | 643.8718
3195.9417 | 700.5178 | 640.9212 | 664.5871 | 642.2326
3196.9417 | 697.2585 | 640.3582 | 658.8715 | 640.5126
3197.9417 | 695.1903 | 639.9422 | 660.3294 | 640.2778
3198.9417 | 691.287 | 640.2548 | 657.4607 | 640.1846
3199.9417 | 693.171 | 640.0501 | 659.8103 | 637.8899
3200.9417 | 691.2557 | 638.8891 | 656.6092 | 641.9103
3201.9417 | 690.4777 | 637.4096 | 653.28 | 637.4856
3202.9417 | 685.8024 | 636.8801 | 650.3776 | 637.432
3203.9417 | 696.8356 | 637.3805 | 647.89 | 635.1632
3204.9417 | 699.0323 | 638.0452 | 648.8762 | 635.0703
3205.9417 | 704.0171 | 636.9822 | 651.7838 | 632.7174
3206.9417 | 702.125 | 635.873 | 649.3067 | 632.1805
3207.9417 | 698.1206 | 635.3545 | 649.8099 | 631.2815
3208.9417 | 699.515 | 636.2539 | 647.9643 | 629.2678
3209.9417 | 694.2556 | 636.7614 | 650.5258 | 627.5503
3210.9417 | 694.2463 | 636.9699 | 650.824 | 627.3973
3211.9417 | 685.9423 | 635.9981 | 648.3649 | 627.0097
3212.9417 | 692.1055 | 636.244 | 645.8169 | 628.2635
3213.9417 | 696.7482 | 636.2933 | 649.3644 | 626.8753
3214.9417 | 710.7972 | 637.4095 | 646.0884 | 629.2468
3215.9417 | 702.8471 | 636.498 | 644.6231 | 627.0264
3216.9417 | 696.3342 | 635.5569 | 644.0775 | 624.862
3217.9417 | 705.884 | 634.7888 | 644.0562 | 627.3845
3218.9417 | 699.0927 | 635.445 | 647.0566 | 628.3219
3219.9417 | 698.4866 | 634.6995 | 648.9573 | 634.8443
3220.9417 | 699.0707 | 633.7369 | 652.8833 | 638.7161
3221.9417 | 706.1713 | 633.2656 | 660.3833 | 634.018
3222.9417 | 700.4296 | 634.1209 | 659.913 | 632.0687
3223.9417 | 707.079 | 636.6427 | 670.1812 | 632.2619
3224.9417 | 707.868 | 637.4531 | 677.1602 | 631.153
3225.9417 | 702.5368 | 638.3723 | 675.902 | 639.2491
3226.9417 | 705.3026 | 639.1265 | 683.1643 | 637.8236
3227.9417 | 699.3872 | 639.0024 | 678.0748 | 636.6242
3228.9417 | 698.9906 | 638.254 | 671.333 | 638.7967
3229.9417 | 699.881 | 637.3367 | 671.4593 | 638.3736
3230.9417 | 695.7134 | 637.2678 | 672.5729 | 637.284
3231.9417 | 697.5921 | 638.8795 | 667.8125 | 644.3007
3232.9417 | 696.0441 | 638.5481 | 661.4447 | 639.7416
3233.9417 | 695.1065 | 636.4598 | 659.7438 | 637.0723
3234.9417 | 688.7798 | 635.7393 | 654.2118 | 638.5744
3235.9417 | 690.4309 | 634.6745 | 654.6919 | 635.8622
3236.9417 | 692.2813 | 635.2187 | 652.7266 | 635.0664
3237.9417 | 691.3026 | 635.4423 | 657.5711 | 638.1318
3238.9417 | 691.703 | 635.1956 | 656.8526 | 636.2251
3239.9417 | 691.7943 | 634.6834 | 654.2769 | 633.9655
3240.9417 | 696.8712 | 634.0801 | 658.9478 | 632.6632
3241.9417 | 708.0175 | 636.7517 | 666.0884 | 633.8548
3242.9417 | 709.5794 | 639.2835 | 677.0035 | 637.7535
3243.9417 | 711.4528 | 642.7695 | 676.9833 | 637.8438
3244.9417 | 710.7365 | 645.0746 | 675.6003 | 636.7338
3245.9417 | 710.3006 | 644.1778 | 672.6347 | 637.4324
3246.9417 | 708.8715 | 643.1107 | 669.4403 | 636.8722
3247.9417 | 714.4499 | 641.1562 | 666.2824 | 641.4115
3248.9417 | 707.3693 | 640.3402 | 659.562 | 637.2335
3249.9417 | 698.5426 | 639.4449 | 655.8482 | 634.5951
3250.9417 | 698.5254 | 641.9166 | 665.3989 | 637.3925
3251.9417 | 698.1613 | 644.2278 | 668.927 | 636.3594
3252.9417 | 701.7815 | 643.2689 | 665.9292 | 636.6032
3253.9417 | 701.6102 | 643.0823 | 662.5964 | 643.1636
3254.9417 | 700.695 | 642.432 | 664.4399 | 644.0557
3255.9417 | 705.6491 | 645.2305 | 669.5725 | 647.3036
3256.9417 | 706.8106 | 644.962 | 671.9307 | 645.8708
3257.9417 | 705.0657 | 644.5647 | 666.6067 | 650.4008
3258.9417 | 698.1187 | 642.5944 | 663.094 | 651.6813
3259.9417 | 693.1837 | 646.1138 | 668.6514 | 653.2023
3260.9417 | 689.1106 | 645.7417 | 664.1258 | 650.7717
3261.9417 | 686.5732 | 644.0179 | 656.1468 | 645.4091
3262.9417 | 687.7528 | 645.2378 | 662.9725 | 639.576
3263.9417 | 694.3627 | 645.7952 | 660.8494 | 639.4995
3264.9417 | 696.2807 | 645.7887 | 657.7615 | 636.8407
3265.9417 | 696.0678 | 647.4265 | 652.7082 | 645.7918
3266.9417 | 696.3646 | 652.2331 | 656.9267 | 645.686
3267.9417 | 690.7349 | 651.6941 | 654.5315 | 641.8471
3268.9417 | 688.3476 | 651.0515 | 662.9708 | 647.0915
3269.9417 | 686.3123 | 648.494 | 658.2853 | 642.2198
3270.9417 | 685.7941 | 646.2331 | 657.2129 | 637.0911
3271.9417 | 684.1091 | 644.0303 | 655.0131 | 634.9155
3272.9417 | 687.4397 | 641.5578 | 650.3611 | 631.3082
3273.9417 | 697.7507 | 640.0657 | 665.3037 | 633.1566
3274.9417 | 695.3566 | 638.6696 | 659.8796 | 630.8268
3275.9417 | 701.563 | 640.0633 | 659.7413 | 627.5177
3276.9417 | 691.8936 | 638.8906 | 662.8327 | 624.3771
3277.9417 | 692.4807 | 637.6382 | 663.9238 | 625.626
3278.9417 | 693.3492 | 636.2021 | 654.862 | 627.9086
3279.9417 | 694.2152 | 636.4124 | 653.818 | 624.834
3280.9417 | 688.6103 | 636.9773 | 652.8902 | 635.8743
3281.9417 | 688.2435 | 640.6393 | 675.7977 | 641.0924
3282.9417 | 678.879 | 642.5121 | 680.5293 | 642.6121
3283.9417 | 679.9255 | 641.8157 | 668.4116 | 643.8722
3284.9417 | 679.232 | 640.1072 | 659.8416 | 644.7683
3285.9417 | 681.5703 | 638.8778 | 654.432 | 642.6373
3286.9417 | 684.2757 | 638.0313 | 651.8365 | 641.7379
3287.9417 | 681.0558 | 637.4993 | 655.4688 | 637.1719
3288.9417 | 683.5919 | 637.3147 | 651.953 | 632.4842
3289.9417 | 686.1722 | 637.6132 | 655.6128 | 632.9557
3290.9417 | 685.0979 | 638.5456 | 660.6541 | 630.3011
3291.9417 | 681.5566 | 642.9023 | 669.6059 | 626.4512
3292.9417 | 683.3381 | 641.1672 | 663.1636 | 622.3571
3293.9417 | 679.925 | 640.0548 | 656.7005 | 628.2074
3294.9417 | 678.9544 | 637.4683 | 650.0345 | 629.9658
3295.9417 | 681.203 | 636.291 | 647.6191 | 627.9436
3296.9417 | 681.9312 | 635.7591 | 643.2632 | 627.2127
3297.9417 | 675.5186 | 634.1905 | 639.6083 | 625.7429
3298.9417 | 672.2442 | 633.3896 | 637.4874 | 624.1051
3299.9417 | 671.3628 | 633.3626 | 635.436 | 621.777
3300.9417 | 676.5901 | 633.3423 | 636.0087 | 619.5886
3301.9417 | 682.1429 | 632.3124 | 634.1442 | 618.1507
3302.9417 | 679.9226 | 632.9833 | 632.4497 | 616.0775
3303.9417 | 684.5869 | 634.1168 | 634.7452 | 614.3247
3304.9417 | 686.6154 | 635.1432 | 639.4139 | 613.271
3305.9417 | 688.1939 | 642.4263 | 641.6647 | 613.5836
3306.9417 | 686.7971 | 643.2305 | 656.9145 | 626.9478
3307.9417 | 679.9406 | 645.467 | 655.2586 | 631.2473
3308.9417 | 676.027 | 645.8183 | 667.7796 | 631.0084
3309.9417 | 675.8759 | 650.0321 | 673.5384 | 627.7174
3310.9417 | 676.6281 | 655.3073 | 675.0016 | 632.861
3311.9417 | 674.1993 | 656.3626 | 677.591 | 632.9539
3312.9417 | 671.0856 | 656.6757 | 684.1711 | 631.8792
3313.9417 | 666.908 | 659.3473 | 690.7293 | 628.8167
3314.9417 | 678.0234 | 657.5979 | 687.7183 | 629.5288
3315.9417 | 684.5566 | 664.3338 | 682.6471 | 629.2078
3316.9417 | 685.103 | 660.5023 | 674.4173 | 626.3567
3317.9417 | 683.4219 | 656.3827 | 668.3994 | 625.9364
3318.9417 | 685.7506 | 654.2323 | 661.6014 | 623.5983
3319.9417 | 685.8859 | 656.5139 | 661.9896 | 624.908
3320.9417 | 695.0233 | 657.2881 | 661.274 | 627.8624
3321.9417 | 699.3324 | 656.3317 | 656.8015 | 634.7171
3322.9417 | 686.6423 | 651.833 | 649.6825 | 630.3164
3323.9417 | 681.0016 | 652.6707 | 647.5688 | 625.6189
3324.9417 | 676.1645 | 648.7113 | 647.2612 | 624.171
3325.9417 | 673.1435 | 647.8995 | 650.4015 | 625.3748
3326.9417 | 668.3043 | 650.9335 | 652.2135 | 627.2377
3327.9417 | 669.2443 | 652.7272 | 651.5305 | 628.9782
3328.9417 | 677.8299 | 651.0909 | 649.4944 | 626.9866
3329.9417 | 684.7087 | 649.446 | 647.6973 | 624.7521
3330.9417 | 684.7494 | 648.7942 | 664.3908 | 623.9854
3331.9417 | 686.7762 | 648.8059 | 667.9352 | 624.0773
3332.9417 | 689.3606 | 651.0055 | 669.8273 | 622.7767
3333.9417 | 689.5676 | 647.9484 | 661.9403 | 622.5005
3334.9417 | 689.4275 | 647.2993 | 665.1917 | 623.6183
3335.9417 | 690.3647 | 647.9363 | 678.2794 | 635.5665
3336.9417 | 682.3215 | 647.9024 | 677.5191 | 641.0211
3337.9417 | 680.6291 | 646.974 | 687.7077 | 638.7104
3338.9417 | 677.9999 | 649.036 | 687.3433 | 635.9464
3339.9417 | 678.2924 | 651.4171 | 696.5293 | 634.9911
3340.9417 | 680.4502 | 653.0143 | 695.6432 | 631.1833
3341.9417 | 678.8879 | 654.0405 | 685.3162 | 627.4039
3342.9417 | 677.7717 | 650.8969 | 683.4275 | 624.6837
3343.9417 | 680.3562 | 648.429 | 686.9267 | 623.2855
3344.9417 | 682.1289 | 650.5199 | 688.8435 | 623.4139
3345.9417 | 677.4777 | 647.7076 | 678.1472 | 621.6578
3346.9417 | 672.2258 | 645.6654 | 669.5052 | 620.5613
3347.9417 | 669.9643 | 643.8422 | 661.6478 | 618.73
3348.9417 | 671.1098 | 646.8932 | 660.9208 | 616.0647
3349.9417 | 673.8197 | 646.7905 | 653.0252 | 614.3408
3350.9417 | 676.0067 | 643.8472 | 647.0967 | 611.3878
3351.9417 | 676.2647 | 640.9833 | 642.6996 | 607.4098
3352.9417 | 671.9449 | 638.7828 | 637.6626 | 604.3198
3353.9417 | 666.135 | 637.8497 | 637.7823 | 612.454
3354.9417 | 670.955 | 634.7117 | 647.7009 | 613.9913
3355.9417 | 666.1223 | 633.4445 | 644.9306 | 613.9605
3356.9417 | 663.3273 | 632.0429 | 642.8357 | 612.9175
3357.9417 | 663.1988 | 631.4187 | 639.8374 | 610.5571
3358.9417 | 667.0342 | 631.0184 | 643.3247 | 612.5088
3359.9417 | 670.3529 | 630.7873 | 642.6698 | 610.9514
3360.9417 | 670.3363 | 628.7347 | 638.5066 | 611.2842
3361.9417 | 670.0466 | 628.4096 | 634.8059 | 614.7995
3362.9417 | 663.1074 | 627.6015 | 631.1848 | 615.811
3363.9417 | 662.4234 | 626.2337 | 628.4657 | 619.1994
3364.9417 | 658.0073 | 625.4936 | 634.7933 | 618.0025
3365.9417 | 666.6946 | 626.9093 | 646.3399 | 624.9752
3366.9417 | 665.7213 | 625.9852 | 641.4001 | 625.9489
3367.9417 | 661.9531 | 624.6858 | 639.4008 | 627.224
3368.9417 | 661.4984 | 624.6799 | 640.0606 | 625.5719
3369.9417 | 663.0291 | 624.4139 | 638.2876 | 630.2934
3370.9417 | 667.0406 | 624.4217 | 640.0606 | 628.4767
3371.9417 | 667.0461 | 624.4505 | 637.748 | 624.7173
3372.9417 | 666.6755 | 622.5288 | 632.9949 | 621.7044
3373.9417 | 667.2563 | 620.8044 | 633.1479 | 618.2556
3374.9417 | 669.0449 | 620.5314 | 634.3695 | 617.6872
3375.9417 | 670.5474 | 620.8045 | 643.3748 | 618.0897
3376.9417 | 666.8976 | 630.4906 | 651.9267 | 616.2506
3377.9417 | 663.8446 | 633.2189 | 665.3876 | 613.8878
3378.9417 | 656.3766 | 632.6168 | 658.2528 | 614.2115
3379.9417 | 661.9367 | 633.1091 | 657.2768 | 623.5351
3380.9417 | 664.9316 | 633.5126 | 657.2473 | 625.0696
3381.9417 | 663.5886 | 634.9915 | 655.5262 | 624.8329
3382.9417 | 662.6495 | 634.7117 | 649.9065 | 620.6917
3383.9417 | 660.1468 | 632.8213 | 642.1359 | 618.572
3384.9417 | 665.0662 | 632.2133 | 636.8053 | 617.7452
3385.9417 | 659.5062 | 634.5194 | 633.8557 | 620.9846
3386.9417 | 658.595 | 640.6773 | 646.8217 | 619.5534
3387.9417 | 650.1334 | 645.8262 | 663.0524 | 617.2119
3388.9417 | 648.5518 | 647.7689 | 664.7099 | 614.7678
3389.9417 | 645.2399 | 645.621 | 664.6437 | 612.4559
3390.9417 | 646.3554 | 642.7234 | 658.5902 | 613.7068
3391.9417 | 643.7487 | 641.0862 | 658.4941 | 612.2626
3392.9417 | 643.3953 | 639.2179 | 662.1145 | 613.9808
3393.9417 | 647.0629 | 641.6387 | 664.9325 | 613.8235
3394.9417 | 653.6609 | 639.586 | 658.8685 | 614.3351
3395.9417 | 650.8798 | 637.6258 | 650.3576 | 615.0312
3396.9417 | 650.0243 | 637.2519 | 658.4583 | 613.7652
3397.9417 | 644.2342 | 633.8559 | 653.0966 | 616.4416
3398.9417 | 640.7649 | 630.4363 | 645.598 | 617.2356
3399.9417 | 646.0769 | 630.3832 | 639.9051 | 615.4788
3400.9417 | 644.1249 | 628.5914 | 634.8113 | 613.5835
3401.9417 | 644.9572 | 626.911 | 636.2015 | 611.269
3402.9417 | 644.4561 | 625.6194 | 636.7723 | 610.3817
3403.9417 | 651.7632 | 624.1223 | 634.2059 | 609.9202
3404.9417 | 658.027 | 624.5311 | 633.3983 | 610.1705
3405.9417 | 652.3646 | 624.0972 | 629.547 | 613.2969
3406.9417 | 647.1972 | 622.4307 | 625.3566 | 613.4276
3407.9417 | 642.3442 | 621.8546 | 623.6477 | 610.0571
3408.9417 | 645.2401 | 620.1127 | 621.1776 | 608.7786
3409.9417 | 646.3433 | 620.8557 | 618.5554 | 606.2859
3410.9417 | 641.6385 | 621.4096 | 624.5905 | 604.8718
3411.9417 | 641.7767 | 620.9006 | 621.8176 | 606.0489
3412.9417 | 638.8156 | 619.4891 | 622.4313 | 609.739
3413.9417 | 639.7829 | 623.8197 | 627.0996 | 608.8351
3414.9417 | 643.9226 | 626.2103 | 641.6914 | 608.4351
3415.9417 | 648.5917 | 627.0941 | 642.8537 | 613.3483
3416.9417 | 652.2405 | 630.2706 | 648.2189 | 614.3275
3417.9417 | 651.9858 | 633.736 | 654.2374 | 625.4178
3418.9417 | 655.3365 | 640.7633 | 669.2431 | 630.0465
3419.9417 | 654.4404 | 643.3046 | 668.7749 | 624.9498
3420.9417 | 655.1907 | 645.2275 | 663.7991 | 621.9211
3421.9417 | 658.0726 | 646.9838 | 660.9042 | 619.7738
3422.9417 | 656.8134 | 644.1276 | 654.1665 | 616.1553
3423.9417 | 657.955 | 642.472 | 659.8017 | 613.855
3424.9417 | 664.3324 | 645.2076 | 662.9036 | 616.0463
3425.9417 | 662.0693 | 644.5578 | 654.7244 | 615.6673
3426.9417 | 658.3943 | 644.7794 | 649.8391 | 614.8413
3427.9417 | 654.821 | 642.7911 | 645.4064 | 612.2217
3428.9417 | 656.4932 | 640.7676 | 641.6685 | 610.0803
3429.9417 | 665.5764 | 638.7586 | 638.3803 | 608.934
3430.9417 | 660.863 | 635.3722 | 637.4578 | 611.6485
3431.9417 | 664.1441 | 634.4503 | 638.5505 | 611.0377
3432.9417 | 663.24 | 635.6864 | 639.8154 | 614.1121
3433.9417 | 661.3064 | 639.9158 | 641.7101 | 613.378
3434.9417 | 664.3453 | 642.5294 | 642.04 | 611.3335
3435.9417 | 657.6587 | 645.1499 | 655.16 | 609.6736
3436.9417 | 656.0032 | 646.1686 | 663.3287 | 609.6908
3437.9417 | 658.2374 | 649.5991 | 661.5701 | 610.4753
3438.9417 | 653.7804 | 653.3394 | 664.4686 | 609.4475
3439.9417 | 657.4759 | 656.6586 | 676.5718 | 606.6214
3440.9417 | 654.5702 | 659.2434 | 680.0751 | 606.6451
3441.9417 | 653.3103 | 657.8648 | 679.9437 | 605.9297
3442.9417 | 652.5649 | 651.8976 | 674.5858 | 607.2552
3443.9417 | 651.6141 | 647.1683 | 668.595 | 611.5811
3444.9417 | 650.5719 | 644.5904 | 668.2296 | 612.0496
3445.9417 | 647.5079 | 643.6009 | 669.851 | 610.6537
3446.9417 | 639.1166 | 644.9864 | 663.4006 | 608.9984
3447.9417 | 634.797 | 647.1617 | 675.3375 | 606.2049
3448.9417 | 630.9284 | 647.4457 | 673.5225 | 608.6514
3449.9417 | 629.8509 | 643.1283 | 662.6453 | 608.8173
3450.9417 | 625.8575 | 638.9975 | 662.3993 | 615.8244
3451.9417 | 634.6799 | 635.7489 | 659.5598 | 621.9134
3452.9417 | 633.2966 | 635.748 | 654.2232 | 626.9298
3453.9417 | 632.1121 | 634.701 | 664.282 | 629.9971
3454.9417 | 634.9388 | 633.9257 | 666.7995 | 629.0219
3455.9417 | 638.5446 | 636.9372 | 672.1301 | 630.6848
3456.9417 | 636.8926 | 637.0165 | 661.4148 | 638.5536
3457.9417 | 643.9376 | 634.814 | 660.7955 | 636.5538
3458.9417 | 643.6611 | 632.7582 | 653.0388 | 633.603
3459.9417 | 644.2318 | 631.8081 | 647.8598 | 628.2634
3460.9417 | 646.4891 | 630.6853 | 644.783 | 624.4119
3461.9417 | 646.7775 | 630.1071 | 641.974 | 626.7501
3462.9417 | 647.498 | 628.0416 | 638.5872 | 633.3681
3463.9417 | 647.6882 | 627.3585 | 641.0397 | 640.6998
3464.9417 | 650.8493 | 628.8887 | 647.0563 | 638.0149
3465.9417 | 650.3916 | 629.2141 | 642.419 | 635.2934
3466.9417 | 645.3447 | 627.5339 | 636.354 | 631.0474
3467.9417 | 646.6509 | 627.403 | 631.0175 | 627.9537
3468.9417 | 639.7139 | 626.582 | 624.4678 | 623.7163
3469.9417 | 636.6304 | 628.0002 | 624.2833 | 621.6453
3470.9417 | 633.6126 | 629.0747 | 632.9147 | 624.9455
3471.9417 | 629.0124 | 630.8085 | 636.3451 | 620.1225
3472.9417 | 634.1799 | 633.1329 | 648.2045 | 617.5843
3473.9417 | 636.2922 | 635.4785 | 660.0829 | 616.2139
3474.9417 | 633.9891 | 635.5517 | 661.1553 | 612.6774
3475.9417 | 637.0363 | 636.7674 | 653.3271 | 610.823
3476.9417 | 637.3023 | 635.1461 | 648.0723 | 608.6435
3477.9417 | 638.9816 | 632.7116 | 643.4582 | 607.2668
3478.9417 | 640.3358 | 631.0288 | 641.0716 | 609.1904
3479.9417 | 637.4009 | 629.6374 | 640.8647 | 614.4185
3480.9417 | 639.0402 | 629.6166 | 642.8208 | 618.7119
3481.9417 | 640.5143 | 628.4645 | 646.6255 | 622.9838
3482.9417 | 640.3439 | 631.0316 | 643.6017 | 620.321
3483.9417 | 638.1198 | 634.1756 | 638.671 | 619.8899
3484.9417 | 632.7609 | 635.4526 | 649.7912 | 615.906
3485.9417 | 635.3023 | 637.4428 | 657.557 | 615.9782
3486.9417 | 633.9287 | 638.2629 | 657.2526 | 612.7185
3487.9417 | 640.0839 | 637.6425 | 657.9158 | 608.0681
3488.9417 | 644.6069 | 636.2563 | 658.9704 | 607.782
3489.9417 | 646.5839 | 640.0867 | 664.3378 | 606.359
3490.9417 | 642.5069 | 642.469 | 671.0189 | 612.2082
3491.9417 | 637.7277 | 642.3916 | 669.6859 | 610.9
3492.9417 | 639.4764 | 643.3285 | 662.0656 | 608.244
3493.9417 | 639.2294 | 640.4557 | 660.1884 | 608.1529
3494.9417 | 636.9538 | 637.6863 | 653.9288 | 606.7931
3495.9417 | 637.8961 | 635.3471 | 654.3017 | 606.5763
3496.9417 | 639.8075 | 635.1729 | 652.7891 | 606.9405
3497.9417 | 639.6373 | 634.6892 | 646.4965 | 604.7174
3498.9417 | 647.1478 | 634.9847 | 645.3491 | 603.1666
3499.9417 | 645.4901 | 633.5379 | 646.6766 | 601.1934
3500.9417 | 642.3348 | 632.8403 | 646.4378 | 603.7807
3501.9417 | 642.1774 | 631.2017 | 650.4091 | 606.2631
3502.9417 | 638.6115 | 635.1886 | 659.9339 | 606.7079
3503.9417 | 634.3343 | 638.055 | 657.0363 | 604.7251
3504.9417 | 631.3769 | 635.929 | 661.3477 | 603.991
3505.9417 | 631.0646 | 635.2882 | 655.1818 | 603.2465
3506.9417 | 626.676 | 634.0578 | 651.7851 | 613.4084
3507.9417 | 626.046 | 633.4491 | 649.4197 | 613.3361
3508.9417 | 625.2199 | 632.0018 | 655.6318 | 612.883
3509.9417 | 625.8708 | 630.3091 | 649.9836 | 619.029
3510.9417 | 623.9199 | 629.9748 | 647.909 | 615.4925
3511.9417 | 625.9446 | 632.503 | 654.7332 | 618.845
3512.9417 | 634.8582 | 634.3511 | 652.3081 | 617.4484
3513.9573 | 636.8146 | 635.7242 | 660.3518 | 613.76
3514.9417 | 634.822 | 635.2505 | 655.9161 | 610.931
3515.9417 | 631.6627 | 631.8447 | 650.6315 | 613.3546
3516.9417 | 629.9692 | 630.7966 | 645.1344 | 620.3401
3517.9417 | 627.4748 | 634.1039 | 655.3332 | 622.2497
3518.9417 | 627.0586 | 634.5168 | 652.1019 | 618.6618
3519.9417 | 625.1409 | 635.0597 | 657.0302 | 614.5281
3520.9417 | 627.2477 | 636.6491 | 665.1497 | 611.9228
3521.9417 | 627.222 | 641.2285 | 669.6716 | 608.9829
3522.9417 | 621.8661 | 640.4652 | 676.0091 | 604.6707
3523.9417 | 624.9696 | 637.4047 | 675.6392 | 613.6725
3524.9417 | 625.7494 | 635.4238 | 668.7127 | 611.4557
3525.9417 | 630.1723 | 635.5544 | 666.6833 | 614.8371
3526.9417 | 628.495 | 634.1844 | 660.9375 | 612.8338
3527.9417 | 632.2607 | 634.4745 | 672.9013 | 610.0488
3528.9417 | 630.2735 | 635.3475 | 674.1599 | 606.1138
3529.9417 | 631.534 | 636.5925 | 678.0781 | 603.9404
3530.9417 | 637.1623 | 637.0864 | 668.7607 | 603.8448
3531.9417 | 642.945 | 638.4597 | 675.7619 | 607.2567
3532.9417 | 645.5414 | 638.8308 | 674.3459 | 611.4362
3533.9417 | 643.2432 | 640.1479 | 673.1599 | 609.5766
3534.9417 | 638.2288 | 640.8457 | 683.9205 | 612.5674
3535.9417 | 634.0776 | 641.0058 | 686.4968 | 610.5246
3536.9417 | 631.7261 | 639.9472 | 684.4809 | 606.9981
3537.9417 | 629.7688 | 643.4659 | 674.6948 | 606.1957
3538.9417 | 627.0917 | 645.2243 | 669.9914 | 604.2529
3539.9417 | 622.8745 | 646.0931 | 677.7355 | 603.6391
3540.9417 | 620.2255 | 646.2382 | 675.0631 | 601.2828
3541.9417 | 615.2354 | 646.3174 | 675.4702 | 599.177
3542.9417 | 612.8717 | 643.1588 | 671.1833 | 595.5523
3543.9417 | 614.634 | 640.2553 | 659.4678 | 595.3041
3544.9417 | 619.4426 | 638.221 | 657.4867 | 598.2195
3545.9417 | 624.9923 | 636.2503 | 649.679 | 606.3525
3546.9417 | 623.63 | 634.168 | 646.0874 | 602.2232
3547.9417 | 619.8878 | 631.9465 | 638.7757 | 600.3996
3548.9417 | 619.5473 | 630.3387 | 633.2186 | 600.1153
3549.9417 | 622.236 | 629.0078 | 630.0538 | 598.4243
3550.9417 | 621.8643 | 627.3209 | 625.592 | 607.2957
3551.9417 | 619.3286 | 627.3636 | 630.8623 | 609.4093
3552.9417 | 620.6602 | 627.3515 | 628.1017 | 605.9603
3553.9417 | 623.2134 | 627.2281 | 632.2323 | 602.0677
3554.9417 | 620.0894 | 630.9602 | 640.3157 | 598.2728
3555.9417 | 621.6927 | 633.0039 | 643.0129 | 597.062
3556.9417 | 622.4712 | 634.2325 | 643.8969 | 595.4638
3557.9417 | 618.7091 | 636.9224 | 651.6262 | 592.322
3558.9417 | 618.6114 | 638.0909 | 654.3106 | 590.9757
3559.9417 | 620.1906 | 639.2701 | 661.2882 | 590.2157
3560.9417 | 615.4875 | 638.9021 | 660.0143 | 588.2292
3561.9417 | 621.1642 | 637.5178 | 651.4014 | 590.0906
3562.9417 | 616.6651 | 635.4887 | 642.3214 | 592.3712
3563.9417 | 617.3241 | 635.621 | 655.9262 | 589.698
3564.9417 | 613.4693 | 635.3791 | 654.3381 | 594.8506
3565.9417 | 615.6495 | 635.4138 | 656.9407 | 592.3961
3566.9417 | 615.9005 | 635.4547 | 650.6139 | 589.3428
3567.9417 | 612.7819 | 638.5461 | 650.19 | 587.8633
3568.9417 | 607.8804 | 637.1017 | 649.4127 | 592.0632
3569.9417 | 607.5042 | 637.0371 | 656.9947 | 589.9037
3570.9417 | 612.0154 | 637.3963 | 659.3007 | 589.9382
3571.9417 | 629.6717 | 636.8945 | 653.3523 | 588.7764
3572.9417 | 632.3957 | 635.2605 | 649.3897 | 588.4749
3573.9417 | 632.4817 | 635.0463 | 643.1896 | 587.5125
3574.9417 | 637.5866 | 635.0573 | 637.2447 | 585.873
3575.9417 | 631.3846 | 634.8873 | 631.0609 | 583.9218
3576.9417 | 637.1574 | 635.8668 | 627.4876 | 582.3667
3577.9417 | 635.5769 | 636.1178 | 633.0457 | 580.1457
3578.9417 | 626.9676 | 635.007 | 632.2154 | 578.2574
3579.9417 | 619.8234 | 633.4329 | 629.9554 | 577.0146
3580.9417 | 615.9788 | 630.9253 | 626.5641 | 581.5157
3581.9417 | 618.1732 | 629.0934 | 626.254 | 580.6646
3582.9417 | 610.3984 | 628.0301 | 623.3828 | 580.5329
3583.9417 | 609.5109 | 627.9041 | 622.7398 | 581.665
3584.9417 | 618.2814 | 626.6077 | 623.5377 | 585.5327
3585.9417 | 614.3469 | 626.6091 | 628.7227 | 586.8924
3586.9417 | 611.9451 | 629.7154 | 632.8677 | 588.7207
3587.9417 | 607.9986 | 631.346 | 644.0118 | 587.934
3588.9417 | 608.4335 | 633.5226 | 643.9288 | 586.2629
3589.9417 | 610.6287 | 634.9773 | 645.0727 | 587.3118
3590.9417 | 612.0847 | 634.3144 | 641.1021 | 586.8176
3591.9417 | 609.0518 | 632.7829 | 634.5087 | 586.9932
3592.9417 | 606.2589 | 632.1362 | 628.8134 | 586.3844
3593.9417 | 603.5495 | 631.4301 | 631.0286 | 588.1445
3594.9417 | 599.0631 | 630.5919 | 633.7432 | 588.0533
3595.9417 | 599.1761 | 628.0557 | 630.5344 | 586.6595
3596.9417 | 599.6349 | 626.1627 | 628.002 | 591.3438
3597.9417 | 593.6332 | 625.7294 | 629.08 | 593.9457
3598.9417 | 593.1924 | 626.5662 | 626.1379 | 593.2498
3599.9417 | 593.5785 | 626.6793 | 621.3575 | 592.8583
3600.9417 | 591.9908 | 625.6049 | 618.8579 | 597.9599
3601.9417 | 590.6049 | 623.8512 | 616.2146 | 595.7092
3602.9417 | 594.9084 | 622.7852 | 613.6406 | 596.5004
3603.9417 | 597.6993 | 621.3124 | 611.7859 | 594.4453
3604.9417 | 599.6776 | 622.22 | 611.4725 | 593.9045
3605.9417 | 602.1789 | 621.3269 | 608.7817 | 595.113
3606.9417 | 602.7701 | 621.2447 | 605.7544 | 596.1665
3607.9417 | 597.5918 | 620.7859 | 603.3155 | 594.4162
3608.9417 | 600.7516 | 618.774 | 603.348 | 593.8771
3609.9417 | 599.8345 | 618.638 | 605.78 | 593.7724
3610.9417 | 595.3301 | 619.1123 | 608.5494 | 588.3328
3611.9417 | 593.8547 | 620.6191 | 613.311 | 583.8257
3612.9417 | 598.9115 | 618.7763 | 617.6078 | 582.7248
3613.9417 | 603.2729 | 619.8881 | 618.2693 | 583.1692
3614.9417 | 601.7551 | 620.3365 | 615.194 | 582.139
3615.9417 | 601.1856 | 621.0078 | 611.0446 | 582.0445
3616.9417 | 595.7202 | 620.071 | 609.8669 | 580.8501
3617.9417 | 593.7426 | 620.0906 | 618.5429 | 580.8653
3618.9417 | 599.6184 | 621.7979 | 619.1266 | 579.6763
3619.9417 | 598.9599 | 620.4318 | 620.979 | 582.8455
3620.9417 | 601.8753 | 620.8516 | 621.0271 | 582.3759
3621.9417 | 599.2031 | 625.7916 | 619.275 | 582.3527
3622.9417 | 594.4687 | 625.64 | 622.7008 | 585.0502
3623.9417 | 594.2119 | 626.9783 | 622.1797 | 585.3878
3624.9417 | 597.8579 | 626.619 | 631.5233 | 588.0313
3625.9417 | 593.931 | 628.6952 | 636.7976 | 585.6056
3626.9417 | 589.2469 | 628.0047 | 630.9068 | 583.9463
3627.9417 | 589.9079 | 630.6591 | 631.8097 | 580.9506
3628.9417 | 585.8654 | 630.9605 | 630.0497 | 579.8826
3629.9417 | 584.1947 | 631.4784 | 631.2518 | 578.5272
3630.9417 | 582.9054 | 630.674 | 626.5441 | 580.5775
3631.9417 | 583.7098 | 629.9538 | 632.5195 | 578.3953
3632.9417 | 583.0604 | 627.288 | 627.3683 | 576.8057
3633.9573 | 587.2533 | 624.806 | 628.5732 | 579.4192
3634.9417 | 600.4243 | 624.0488 | 635.17 | 582.3824
3635.9417 | 609.9207 | 622.0994 | 631.5979 | 580.2601
3636.9417 | 610.8033 | 621.11 | 630.4182 | 582.4398
3637.9573 | 609.7591 | 620.1268 | 628.9775 | 582.5923
3638.9417 | 608.4077 | 618.6606 | 620.8609 | 587.7821
3639.9417 | 605.6463 | 618.0771 | 616.1388 | 585.874
3640.9417 | 613.4227 | 617.3568 | 620.2505 | 592.7644
3641.9417 | 621.7608 | 616.8733 | 619.1136 | 590.7329
3642.9417 | 623.0367 | 616.1923 | 613.4548 | 589.4673
3643.9417 | 625.2688 | 614.9347 | 608.0683 | 586.8246
3644.9417 | 615.9537 | 616.8936 | 607.8834 | 585.7229
3645.9417 | 610.327 | 617.3081 | 609.527 | 583.8203
3646.9417 | 613.4259 | 619.1672 | 622.2122 | 583.0132
3647.9417 | 620.0103 | 620.7719 | 619.7947 | 581.8746
3648.9417 | 616.1616 | 621.617 | 622.2136 | 581.5678
3649.9417 | 607.8872 | 622.039 | 617.1899 | 586.8654
3650.9417 | 609.1551 | 621.5814 | 615.0044 | 591.1205
3651.9417 | 607.1755 | 620.2003 | 611.4014 | 589.4323
3652.9417 | 602.518 | 619.6752 | 607.9272 | 591.1897
3653.9417 | 595.4548 | 618.0128 | 603.1188 | 595.4695
3654.9417 | 591.7007 | 616.7372 | 604.2129 | 594.2287
3655.9417 | 589.1235 | 616.7555 | 601.4906 | 591.9173
3656.9417 | 589.871 | 616.0442 | 605.3402 | 587.6623
3657.9417 | 587.411 | 614.9827 | 601.7658 | 587.4439
3658.9417 | 587.7283 | 613.9437 | 600.9618 | 587.5209
3659.9417 | 590.7643 | 612.898 | 598.4496 | 584.1498
3660.9417 | 588.7319 | 613.9942 | 598.3933 | 587.9778
3661.9417 | 592.7353 | 615.5919 | 610.898 | 584.5999
3662.9417 | 593.5619 | 616.1097 | 619.1521 | 582.675
3663.9417 | 592.9026 | 616.9516 | 620.5094 | 580.6742
3664.9417 | 589.928 | 617.7089 | 625.3843 | 580.4708
3665.9417 | 596.1273 | 616.8381 | 622.8666 | 578.0962
3666.9417 | 593.1135 | 615.6493 | 622.3969 | 577.6138
3667.9417 | 591.5602 | 615.0979 | 619.0903 | 578.3031
3668.9417 | 594.4646 | 613.6147 | 614.0522 | 577.0024
3669.9417 | 596.2686 | 612.0506 | 615.9289 | 576.0956
3670.9417 | 598.2375 | 613.2983 | 616.6582 | 579.7816
3671.9417 | 600.7446 | 612.4432 | 614.2467 | 578.7339
3672.9417 | 601.3056 | 611.2786 | 611.0039 | 578.5852
3673.9417 | 600.7394 | 609.8446 | 608.5028 | 576.4516
3674.9417 | 601.0108 | 609.0009 | 605.4856 | 574.9877
3675.9417 | 597.4692 | 608.1677 | 602.1301 | 574.3431
3676.9417 | 597.8797 | 607.8146 | 600.2704 | 572.7115
3677.9417 | 597.7019 | 607.1034 | 600.1327 | 573.7789
3678.9417 | 597.1536 | 605.4102 | 596.6095 | 573.3211
3679.9417 | 597.4572 | 606.4884 | 593.7962 | 571.9091
3680.9417 | 591.4719 | 610.7566 | 597.6391 | 572.1689
3681.9417 | 589.4383 | 612.5801 | 597.8113 | 571.3583
3682.9417 | 588.3301 | 613.4211 | 601.7389 | 571.6767
3683.9417 | 587.9562 | 614.3916 | 612.3235 | 569.7235
3684.9417 | 588.1187 | 613.2527 | 619.575 | 568.1401
3685.9417 | 591.431 | 614.731 | 614.6384 | 568.2068
3686.9417 | 590.0604 | 616.6645 | 620.4126 | 567.3456
3687.9417 | 592.271 | 619.7067 | 619.4974 | 567.6065
3688.9417 | 587.4778 | 619.8167 | 629.9871 | 567.2767
3689.9417 | 587.9451 | 619.0007 | 637.2356 | 566.7502
3690.9417 | 588.5937 | 618.2532 | 636.9796 | 568.0836
3691.9417 | 593.8262 | 618.7042 | 630.3558 | 569.4886
3692.9417 | 595.4819 | 620.7832 | 631.472 | 573.8937
3693.9417 | 593.3162 | 620.5359 | 625.2003 | 574.8425
3694.9417 | 595.0853 | 619.0599 | 629.2496 | 573.2395
3695.9417 | 594.5552 | 620.0057 | 641.5737 | 572.6102
3696.9417 | 595.5063 | 618.671 | 631.9453 | 571.3639
3697.9417 | 595.563 | 619.1755 | 625.7799 | 569.9594
3698.9417 | 596.4524 | 619.2922 | 636.7497 | 571.7613
3699.9417 | 596.2946 | 618.8163 | 643.8224 | 572.3044
3700.9417 | 597.4719 | 618.16 | 647.5122 | 570.4601
3701.9417 | 597.5824 | 618.8568 | 639.3714 | 570.6002
3702.9417 | 594.2274 | 620 | 638.4765 | 570.0072
3703.9417 | 590.5795 | 618.3211 | 639.8895 | 568.1421
3704.9417 | 590.3381 | 615.705 | 636.4252 | 567.1394
3705.9417 | 602.8761 | 616.0135 | 635.0336 | 567.0859
3706.9417 | 597.94 | 617.5833 | 633.8845 | 566.8435
3707.9417 | 594.4831 | 619.1245 | 637.4277 | 566.2899
3708.9417 | 590.8732 | 617.608 | 630.6191 | 567.5311
3709.9417 | 588.5075 | 615.5485 | 627.4878 | 566.8193
3710.9417 | 588.4538 | 615.3093 | 627.2157 | 567.8852
3711.9417 | 585.9749 | 614.0103 | 619.4473 | 567.4089
3712.9417 | 586.9367 | 612.9855 | 619.1992 | 567.0909
3713.9417 | 596.105 | 611.3692 | 615.6596 | 566.9674
3714.9417 | 599.0439 | 609.884 | 613.5428 | 567.2009
3715.9417 | 601.8952 | 608.9227 | 609.4461 | 566.9548
3716.9417 | 596.6832 | 607.1044 | 608.0619 | 566.5639
3717.9417 | 595.2135 | 606.9795 | 609.4297 | 567.4771
3718.9417 | 599.9587 | 607.2341 | 610.8602 | 569.0601
3719.9417 | 607.3922 | 609.4516 | 607.9803 | 569.4293
3720.9417 | 598.5954 | 610.6103 | 613.4827 | 568.1228
3721.9417 | 593.4342 | 610.6019 | 610.545 | 566.5775
3722.9417 | 590.1144 | 611.345 | 608.0458 | 565.4188
3723.9417 | 588.0282 | 610.0337 | 610.863 | 567.161
3724.9417 | 586.0117 | 611.511 | 607.9906 | 566.0281
3725.9417 | 583.8142 | 611.2316 | 608.2627 | 565.5987
3726.9417 | 585.7633 | 612.3651 | 611.3843 | 566.7604
3727.9417 | 585.9706 | 612.3147 | 626.3056 | 566.1383
3728.9417 | 583.8759 | 614.0461 | 628.4691 | 566.0663
3729.9417 | 579.238 | 614.1774 | 624.3404 | 565.1734
3730.9417 | 577.2952 | 614.2356 | 623.5211 | 565.7798
3731.9417 | 573.9945 | 617.0317 | 624.4539 | 564.8565
3732.9417 | 571.9203 | 617.4069 | 620.8402 | 563.6454
3733.9417 | 572.6286 | 616.1595 | 618.6769 | 563.856
3734.9417 | 573.0609 | 617.2545 | 624.0119 | 563.4681
3735.9417 | 578.3215 | 616.3884 | 622.3533 | 568.7037
3736.9417 | 578.7849 | 613.9002 | 617.0809 | 567.2638
3737.9417 | 577.2135 | 612.9518 | 613.0154 | 566.26
3738.9417 | 573.9754 | 612.5205 | 610.5511 | 571.665
3739.9417 | 574.5052 | 612.281 | 610.8014 | 575.9467
3740.9417 | 575.7267 | 613.2069 | 610.9861 | 575.26
3741.9417 | 576.7416 | 612.8844 | 608.8176 | 573.661
3742.9417 | 580.0982 | 612.2912 | 607.1916 | 573.1633
3743.9417 | 578.7616 | 610.9298 | 606.3376 | 572.2157
3744.9417 | 578.9828 | 609.3336 | 603.0921 | 576.1042
3745.9417 | 575.4249 | 609.5165 | 603.3689 | 573.2685
3746.9417 | 574.7893 | 608.6365 | 604.5503 | 573.6602
3747.9417 | 574.3794 | 609.5562 | 602.6422 | 577.1175
3748.9417 | 578.0302 | 609.1317 | 606.057 | 575.2517
3749.9417 | 579.6133 | 608.1495 | 602.2407 | 572.2843
3750.9417 | 582.4364 | 607.5556 | 598.8712 | 572.1747
3751.9417 | 583.6582 | 606.052 | 598.4901 | 571.7353
3752.9417 | 587.8735 | 605.3171 | 598.082 | 570.9375
3753.9417 | 590.1653 | 603.9911 | 595.0577 | 569.7133
3754.9417 | 587.0017 | 604.0246 | 593.1122 | 566.503
3755.9417 | 582.5894 | 603.5846 | 592.2825 | 568.8169
3756.9417 | 583.5327 | 603.9875 | 591.3979 | 571.4774
3757.9417 | 584.7501 | 605.9335 | 592.5124 | 572.6462
3758.9417 | 579.4157 | 605.8576 | 594.0417 | 572.314
3759.9417 | 579.6836 | 605.7608 | 597.7227 | 571.638
3760.9417 | 581.2128 | 605.1452 | 600.6709 | 570.9915
3761.9417 | 586.2547 | 605.0594 | 603.6616 | 574.1558
3762.9417 | 591.3082 | 605.8616 | 604.4243 | 573.5246
3763.9417 | 589.1368 | 607.95 | 608.023 | 573.5443
3764.9417 | 590.8528 | 606.8999 | 609.9066 | 571.973
3765.9417 | 592.3325 | 607.0223 | 608.5189 | 574.4047
3766.9417 | 594.4522 | 605.7649 | 604.862 | 573.7713
3767.9417 | 595.4164 | 605.2658 | 604.9074 | 574.5201
3768.9417 | 599.0672 | 604.8555 | 604.9535 | 577.3215
3769.9417 | 604.1166 | 604.5904 | 603.7334 | 578.4818
3770.9417 | 604.5753 | 604.5337 | 605.2499 | 580.1869
3771.9417 | 602.2651 | 603.7536 | 603.9595 | 578.9173
3772.9417 | 602.045 | 601.4082 | 601.0558 | 578.79
3773.9417 | 601.2298 | 600.2016 | 599.5507 | 577.3469
3774.9417 | 601.5012 | 601.1454 | 598.8737 | 576.2466
3775.9417 | 602.6551 | 602.4765 | 601.4132 | 574.1922
3776.9417 | 601.2573 | 603.2273 | 610.0442 | 572.9276
3777.9417 | 597.0923 | 604.2147 | 617.415 | 571.5286
3778.9417 | 592.5393 | 604.3952 | 624.7006 | 572.5934
3779.9417 | 587.094 | 605.676 | 626.3542 | 570.8664
3780.9417 | 587.3588 | 609.2768 | 624.2703 | 570.3492
3781.9417 | 584.5087 | 611.4731 | 625.529 | 570.3526
3782.9417 | 583.3985 | 612.1077 | 626.1879 | 569.0258
3783.9417 | 582.7509 | 612.5955 | 626.9676 | 567.8043
3784.9417 | 581.3152 | 613.2984 | 625.4312 | 566.9168
3785.9417 | 583.5462 | 612.04 | 627.4798 | 567.2887
3786.9417 | 588.5344 | 610.745 | 624.589 | 571.503
3787.9417 | 590.7279 | 609.5123 | 625.6216 | 574.3289
3788.9417 | 594.8265 | 609.1847 | 624.9154 | 573.795
3789.9417 | 592.8034 | 606.9694 | 620.2857 | 572.3057
3790.9417 | 592.5121 | 604.6342 | 618.2578 | 571.0826
3791.9417 | 605.5588 | 603.6459 | 616.5825 | 570.3728
3792.9417 | 607.6422 | 604.8665 | 617.7858 | 572.0974
3793.9417 | 603.503 | 607.6469 | 618.1402 | 571.2377
3794.9417 | 597.7825 | 608.2004 | 626.5281 | 570.2512
3795.9417 | 592.6409 | 609.95 | 623.4765 | 568.9469
3796.9417 | 588.0134 | 609.5333 | 619.5954 | 568.0854
3797.9417 | 584.7305 | 608.9686 | 626.3611 | 567.4775
3798.9417 | 583.8406 | 610.4655 | 623.5504 | 567.4558
3799.9417 | 583.5926 | 612.452 | 631.1551 | 566.0902
3800.9417 | 580.7865 | 612.1684 | 628.3749 | 565.8477
3801.9417 | 577.3962 | 611.4217 | 630.725 | 564.755
3802.9417 | 576.7478 | 612.7225 | 634.2335 | 563.7833
3803.9417 | 574.4658 | 612.1986 | 626.4217 | 562.779
3804.9417 | 576.8514 | 612.5462 | 632.4643 | 561.8457
3805.9417 | 578.7868 | 612.8779 | 633.7068 | 563.4076
3806.9417 | 580.6214 | 611.7098 | 628.7087 | 563.9546
3807.9417 | 581.7701 | 609.873 | 623.1975 | 562.7947
3808.9417 | 582.9041 | 608.9543 | 619.0974 | 562.97
3809.9417 | 582.0206 | 608.8369 | 616.5596 | 562.632
3810.9417 | 579.9822 | 610.2401 | 623.3097 | 561.957
3811.9417 | 580.8541 | 610.9643 | 621.9387 | 562.732
3812.9417 | 580.2189 | 609.542 | 619.2293 | 563.4011
3813.9417 | 581.4869 | 609.0033 | 625.3266 | 562.6779
3814.9417 | 583.6151 | 608.0971 | 622.5574 | 562.0934
3815.9417 | 580.9027 | 609.693 | 621.6008 | 561.4877
3816.9417 | 576.6258 | 611.4108 | 620.3785 | 560.757
3817.9417 | 574.4166 | 611.0819 | 623.571 | 560.6757
3818.9417 | 574.9367 | 610.6978 | 636.2939 | 560.297
3819.9417 | 574.8478 | 610.1855 | 640.4088 | 560.244
3820.9417 | 574.0877 | 607.8844 | 629.8296 | 559.3011
3821.9417 | 579.1739 | 609.3292 | 627.3475 | 559.2369
3822.9417 | 577.0436 | 610.3475 | 620.5228 | 559.4976
3823.9417 | 577.3242 | 611.0457 | 619.5562 | 558.892
3824.9417 | 578.4619 | 611.6315 | 620.3224 | 559.4324
3825.9417 | 578.669 | 610.6927 | 621.4152 | 560.3074
3826.9417 | 575.4721 | 610.5862 | 620.9374 | 560.7544
3827.9417 | 572.2671 | 611.286 | 619.9998 | 559.7191
3828.9417 | 570.7245 | 611.872 | 620.0318 | 558.4766
3829.9417 | 567.4175 | 611.0738 | 617.6622 | 558.1379
3830.9417 | 566.916 | 609.6488 | 613.9349 | 558.4656
3831.9417 | 566.3286 | 608.0923 | 612.7332 | 563.5471
3832.9417 | 568.5066 | 606.1824 | 612.2756 | 565.0613
3833.9417 | 569.8791 | 605.6928 | 610.5301 | 567.6531
3834.9417 | 572.9395 | 606.7181 | 609.8186 | 569.4776
3835.9417 | 573.3374 | 609.1125 | 607.0378 | 569.2672
3836.9417 | 573.5619 | 610.9355 | 607.1308 | 573.0681
3837.9417 | 574.7899 | 610.35 | 609.7364 | 571.7897
3838.9417 | 575.6408 | 609.2344 | 611.5949 | 569.8041
3839.9417 | 573.9485 | 607.6896 | 609.8214 | 569.1114
3840.9417 | 572.3891 | 606.0001 | 605.1833 | 570.4459
3841.9417 | 577.2821 | 609.55 | 606.8019 | 571.3858
3842.9417 | 579.5251 | 611.344 | 605.0538 | 572.1595
3843.9417 | 577.5499 | 611.1593 | 605.889 | 572.2305
3844.9417 | 579.3346 | 611.6746 | 604.2483 | 574.2086
3845.9417 | 579.2812 | 611.761 | 611.099 | 572.7688
3846.9417 | 577.0285 | 611.0048 | 609.8349 | 571.887
3847.9417 | 577.521 | 611.8881 | 613.6499 | 572.8286
3848.9417 | 576.0515 | 611.6662 | 616.8151 | 570.9203
3849.9417 | 572.8591 | 610.0703 | 620.855 | 568.9684
3850.9417 | 571.1211 | 611.3991 | 619.9034 | 568.2395
3851.9573 | 570.146 | 613.5228 | 620.8869 | 567.144
3852.9417 | 570.9235 | 614.8877 | 621.2645 | 567.33
3853.9417 | 571.2009 | 614.1374 | 616.1086 | 566.2748
3854.9417 | 569.2967 | 612.3843 | 611.8182 | 565.2557
3855.9417 | 569.4508 | 612.1553 | 617.0554 | 565.6926
3856.9417 | 566.6291 | 612.2115 | 613.6656 | 564.4153
3857.9417 | 565.1939 | 611.8342 | 610.023 | 564.8794
3858.9417 | 564.4394 | 612.7232 | 609.3177 | 566.5466
3859.9417 | 563.9851 | 612.823 | 615.5335 | 565.5175
3860.9417 | 561.8665 | 611.9614 | 616.4789 | 564.8752
3861.9417 | 560.7917 | 611.8686 | 613.5307 | 564.6509
3862.9417 | 560.958 | 611.388 | 611.9034 | 564.1365
3863.9417 | 560.88 | 610.9499 | 609.1856 | 563.6999
3864.9417 | 563.9449 | 609.0738 | 607.1631 | 562.741
3865.9417 | 567.3601 | 609.1281 | 606.7727 | 564.3609
3866.9417 | 568.8454 | 609.6025 | 604.0527 | 563.1687
3867.9417 | 565.9227 | 609.4522 | 602.4926 | 562.0681
3868.9417 | 563.8566 | 609.0438 | 603.1295 | 561.6137
3869.9417 | 564.1611 | 610.0845 | 601.3313 | 562.3217
3870.9417 | 563.72 | 609.6823 | 599.3254 | 561.6471
3871.9417 | 563.6129 | 611.5581 | 600.3015 | 562.1421
3872.9417 | 563.2261 | 610.2241 | 598.231 | 561.4591
3873.9417 | 565.7606 | 610.0963 | 599.3765 | 562.5754
3874.9417 | 568.38 | 611.9077 | 602.9741 | 563.6805
3875.9417 | 570.1762 | 611.9587 | 600.8466 | 563.3595
3876.9417 | 568.0702 | 613.2573 | 603.9802 | 562.4413
3877.9417 | 567.5823 | 614.1513 | 604.0469 | 561.4721
3878.9417 | 566.6233 | 613.3185 | 602.6993 | 561.9712
3879.9417 | 566.8477 | 611.648 | 611.6579 | 561.1754
3880.9417 | 569.5387 | 612.0063 | 613.294 | 562.4644
3881.9573 | 571.4518 | 611.8132 | 614.6486 | 563.1557
3882.9417 | 572.7789 | 612.3564 | 614.7663 | 563.6733
3883.9417 | 573.8266 | 611.509 | 617.3024 | 564.1544
3884.9417 | 573.0304 | 611.9797 | 614.73 | 564.7486
3885.9417 | 572.1411 | 612.9828 | 613.5441 | 564.8902
3886.9417 | 569.1577 | 613.7435 | 612.5809 | 566.9424
3887.9417 | 569.2867 | 614.1093 | 614.6831 | 566.7621
3888.9417 | 569.1969 | 613.5946 | 615.2123 | 567.1953
3889.9417 | 571.1263 | 613.2786 | 617.907 | 568.7786
3890.9417 | 569.2367 | 610.1991 | 615.4265 | 568.0414
3891.9417 | 570.182 | 608.8792 | 613.6143 | 569.0571
3892.9417 | 569.5116 | 608.1813 | 610.5143 | 569.7922
3893.9417 | 569.3008 | 611.3183 | 611.7791 | 570.808
3894.9417 | 568.5471 | 610.7829 | 612.3791 | 569.4947