## Test Conditions
DESIREE-FIRE Intermediate Scale Test 7 - Circuit Data Only
Test Date: | 2010-03-09
DCSim DAQ Start Time | 13:14
DCSim Time for Synchronization | 13:16
Heat Source Synchronization | 0:00 | hours:minutes:seconds
Heat Source DAQ Start Time | 13:15
Fire Time | 14:00
Offset | 0:46 | hours:minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 2760 | seconds
Heat Source Offset | 0:45 | hours:minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 2695 | seconds
Heat Source Stop Time | 14:40
Test Duration | 0:40 | hours:minutes:seconds
| 2400 | seconds
CT500 turns | 2 | 1 or 2 | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 turns | 5 | 1 or 5
Pre-Test Baseline: | Gathered | Gathered or Not Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit Number | Cable Type |  | Cable TC Channel | Air TC Channel
1" Solenoid Valve | PE/PVC, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 2, 3, and 4 represents the conduit temperature 3', 5', and 7' down the conduit located in B Position. These are labeled as "B Position - Conduit - 3'", "B Position - Conduit - Middle", " B Position - Conduit - 7'", respectively.
Large Coil | PE/PVC, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 2, 3, and 4 represents the conduit temperature 3', 5', and 7' down the conduit located in B Position. These are labeled as "B Position - Conduit - 3'", "B Position - Conduit - Middle", " B Position - Conduit - 7'", respectively.
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | 1"Coil_CT500 | 1"Coil_CT35_1_P | 1"Coil_CT35_2_G | 1"Coil_CT35_3_R | 1"Coil_CT35_4_N2 | 1"Coil_CT35_5_S | 1"Coil_CT35_6_N1 | LgCoil_CT500 | LgCoil_CT35_1_P | LgCoil_CT35_2_G | LgCoil_CT35_3_N2 | LgCoil_CT35_4_S | LgCoil_CT35_5_N1 | 1"Coil_VT7_1_G | 1"Coil_VT7_2_R | 1"Coil_VT7_3_SP | 1"Coil_VT7_4_S | 1"Coil_VTU_1_P | 1"Coil_VTU_2_N2 | 1"Coil_VTU_3_N1 | LgCoil_VT7_1_R | LgCoil_VT7_2_SP | LgCoil_VT7_3_S | LgCoil_VTU_1_P | LgCoil_VTU_2_G | LgCoil_VTU_3_N2 | LgCoil_VTU_4_N1 | {1"Valve} V(N2) - V(Batt -) | {1"Valve} V(N1) - V(Batt -) | {1"Valve} V(P) - V(Batt +) | {1"Valve} V(R) - V(Batt -) | {1"Valve} V(S) - V(Batt -) | {1"Valve} V(S) - V(N1) | {1"Valve} V(G) - V(Batt +) | {LgCoil} V(N2) - V(Batt -) | {LgCoil} V(N1) - V(Batt -) | {LgCoil} V(P) - V(Batt +) | {LgCoil} V(R) - V(Batt -) | {LgCoil} V(S) - V(Batt -) | {LgCoil} V(S) - V(N1) | {LgCoil} V(G) - V(Batt +) | {1"Valve} V(P) - V(Batt -) | {1"Valve} V(G) - V(Batt -) | {1"Valve} V(SP) - V(Batt -) | {1"Valve} V(N1) - V(Batt +) | {LgCoil} V(P) - V(Batt -) | {LgCoil} V(G) - V(Batt -) | {LgCoil} V(SP) - V(Batt -) | {LgCoil} V(N1) - V(Batt +)
-0.8125 | 121.9803 | -60.9421 | 60.9146 | -0.020752 | 0.010846 | 0.067345 | 0.0039265 | 0.066371 | 0.0014441 | 0.00090584 | -0.011673 | -0.0019909 | 0.06307 | 0.066245 | 0.0049005 | -0.0055564 | 60.9329 | -60.8139 | -0.027466 | -60.9741 | 60.9146 | -60.9879 | -60.8917 | -61.3174 | -0.022888 | -61.3174 | 60.8414 | 60.8688 | -60.8505 | -61.0016 | -0.045776 | 0.050354 | 0 | 0.12817 | -0.032043 | -0.082397 | 0.01831 | 0.091553 | -0.059509 | -0.073242 | -0.37537 | -0.37537 | -0.31586 | -0.045777 | 121.8567 | 121.875 | 60.9146 | -121.8063 | 121.7834 | 121.8109 | 60.9192 | -121.9162
0.9375 | 122.0352 | -60.9192 | 60.9375 | -0.020752 | 0.014477 | 0.06649 | 0.0060627 | 0.068293 | 0.0059303 | 0.00069204 | -0.011673 | -0.0011365 | 0.06542 | 0.064749 | 0.0040461 | -0.0070516 | 60.9833 | -60.7315 | 0.086975 | -60.9283 | 60.8871 | -60.9741 | -60.878 | -61.235 | 0.07782 | -61.235 | 60.8368 | 60.8963 | -60.8322 | -60.9787 | -0.054932 | 0.041198 | -0.050354 | 0.18768 | -0.009156 | -0.050354 | 0.045776 | 0.086975 | -0.05951 | -0.10071 | -0.31586 | -0.31586 | -0.25635 | -0.041199 | 121.8063 | 121.9025 | 61.0062 | -121.8155 | 121.756 | 121.8155 | 60.997 | -121.9162
2.6094 | 122.0718 | -60.8917 | 60.9055 | -0.020752 | 0.011914 | 0.066063 | 0.0049945 | 0.067011 | -0.0019739 | -0.0016578 | -0.0040437 | -0.0054089 | 0.063925 | 0.064749 | -0.0012945 | -0.0066244 | 60.9467 | -60.6995 | 0.086975 | -60.91 | 60.8368 | -60.9833 | -60.8597 | -61.2762 | 0.10071 | -61.2213 | 60.8002 | 60.8643 | -60.8231 | -60.9879 | -0.091552 | 0.032044 | -0.068665 | 0.19226 | -0.01831 | -0.050354 | 0.041198 | 0.068665 | -0.09613 | -0.10529 | -0.38452 | -0.32959 | -0.23346 | -0.041199 | 121.7285 | 121.8384 | 60.9787 | -121.7651 | 121.6919 | 121.756 | 60.9924 | -121.8933
4.3438 | 121.9666 | -60.9375 | 60.9375 | 0.0021362 | 0.012341 | 0.068626 | 0.00050847 | 0.066157 | 0.0046485 | -0.00037596 | 0.0035858 | -0.0034863 | 0.060293 | 0.065817 | 0.0074641 | -0.0055564 | 60.9375 | -60.791 | 0.013733 | -60.965 | 60.8917 | -60.965 | -60.8917 | -61.3083 | -0.009155 | -61.2991 | 60.8459 | 60.878 | -60.8414 | -61.0062 | -0.027466 | 0.045776 | -0.045776 | 0.14648 | -0.027466 | -0.073242 | 0 | 0.09613 | -0.068665 | -0.091553 | -0.37079 | -0.36163 | -0.29297 | -0.059509 | 121.8292 | 121.875 | 60.9512 | -121.8292 | 121.7834 | 121.8155 | 60.9283 | -121.9437
6.0938 | 122.1222 | -60.9146 | 60.8826 | -0.013122 | 0.010205 | 0.066917 | 0.0039265 | 0.064448 | -0.0051781 | -0.0022986 | 0.0035858 | -0.0081861 | 0.061788 | 0.064108 | 0.00062806 | -0.0036336 | 60.9695 | -60.672 | 0.086975 | -60.9055 | 60.8414 | -60.9924 | -60.9009 | -61.2488 | 0.16479 | -61.1252 | 60.7498 | 60.8231 | -60.8322 | -61.0107 | -0.07782 | 0.013733 | -0.041198 | 0.24262 | 0.009155 | -0.004578 | 0.086975 | 0.082398 | -0.09613 | -0.13275 | -0.33417 | -0.21057 | -0.11444 | -0.059509 | 121.756 | 121.8842 | 61.0016 | -121.7834 | 121.6644 | 121.7377 | 61.0794 | -121.8933
7.8281 | 121.9894 | -60.9695 | 60.9238 | -0.020752 | 0.0063596 | 0.06884 | 0.0026447 | 0.065302 | -0.0026147 | -0.0035804 | -0.019302 | -0.0071179 | 0.061575 | 0.063895 | 0.0010553 | -0.0027792 | 60.9192 | -60.759 | -0.004578 | -60.9604 | 60.8414 | -60.9695 | -60.8734 | -61.3266 | 0.032043 | -61.2213 | 60.7407 | 60.8093 | -60.8459 | -61.0153 | 0 | 0.09613 | -0.082397 | 0.21057 | 0.009155 | -0.086975 | -0.004578 | 0.1236 | -0.045777 | -0.1831 | -0.35706 | -0.25177 | -0.20599 | -0.11444 | 121.8109 | 121.8887 | 60.965 | -121.7972 | 121.7102 | 121.7789 | 61.0016 | -121.9391
9.5469 | 122.0993 | -60.878 | 60.9375 | 0.0021362 | 0.015332 | 0.067131 | 0.0037127 | 0.065943 | 0.0059303 | -0.002085 | -0.011673 | -0.00092292 | 0.064993 | 0.064536 | 0.0046869 | -0.0072652 | 60.9833 | -60.7452 | 0.064087 | -60.9055 | 60.9055 | -60.9741 | -60.8826 | -61.2305 | 0.11444 | -61.2076 | 60.8643 | 60.8963 | -60.8368 | -60.9879 | -0.09613 | -0.004577 | -0.032043 | 0.13275 | -0.027466 | -0.022889 | 0.045776 | 0.041199 | -0.10986 | -0.073242 | -0.35248 | -0.32959 | -0.21973 | -0.041199 | 121.7834 | 121.8613 | 60.9421 | -121.8201 | 121.7422 | 121.7743 | 60.9924 | -121.9254
11.2188 | 122.0261 | -60.9421 | 60.91 | -0.013122 | 0.011059 | 0.067558 | 0.0020039 | 0.063807 | -0.00047854 | -0.00037596 | -0.0040437 | -0.0036999 | 0.062002 | 0.066672 | 0.0055415 | -0.0055564 | 60.9192 | -60.8093 | -0.032043 | -60.9787 | 60.8917 | -60.9695 | -60.9009 | -61.3037 | -0.009155 | -61.2762 | 60.8231 | 60.8688 | -60.878 | -60.9879 | -0.027465 | 0.041199 | -0.01831 | 0.13275 | -0.036621 | -0.07782 | 0.009155 | 0.064087 | -0.045776 | -0.086975 | -0.36163 | -0.33417 | -0.28839 | -0.041199 | 121.8338 | 121.8613 | 60.91 | -121.8109 | 121.7651 | 121.8109 | 60.9329 | -121.8979
12.9531 | 122.0718 | -60.8917 | 60.9055 | -0.020752 | 0.010205 | 0.067772 | 0.0054217 | 0.06872 | -0.0056055 | -0.0012306 | -0.011673 | -0.0073315 | 0.064352 | 0.063254 | -0.00086734 | -0.0049154 | 60.965 | -60.6766 | 0.11902 | -60.9055 | 60.8185 | -60.9741 | -60.91 | -61.235 | 0.16937 | -61.1343 | 60.759 | 60.7956 | -60.878 | -60.997 | -0.082397 | -0.01831 | -0.086976 | 0.21515 | -0.013733 | 0.004577 | 0.059509 | 0.013733 | -0.10528 | -0.14648 | -0.34332 | -0.24261 | -0.13733 | -0.10986 | 121.7102 | 121.8567 | 61.0107 | -121.8155 | 121.6507 | 121.6873 | 61.0611 | -121.9025
14.625 | 122.0856 | -60.9146 | 60.878 | 0.0021362 | 0.011059 | 0.068199 | 0.0062763 | 0.06573 | -0.0045373 | -0.0027258 | -0.0040437 | -0.0062635 | 0.063497 | 0.066245 | -1.2744e-05 | -0.0049154 | 60.9421 | -60.7361 | 0.027466 | -60.9192 | 60.8322 | -60.9833 | -60.8826 | -61.2534 | 0.10529 | -61.171 | 60.7361 | 60.8185 | -60.8551 | -61.0245 | -0.068664 | 0.032044 | -0.045777 | 0.17853 | -0.004577 | -0.036621 | 0.064087 | 0.059509 | -0.10986 | -0.14191 | -0.33875 | -0.25635 | -0.14648 | -0.05951 | 121.7468 | 121.8567 | 60.9421 | -121.7606 | 121.6507 | 121.7331 | 61.0199 | -121.9025
16.375 | 122.1085 | -60.8826 | 60.9009 | 0.0021362 | 0.011059 | 0.069267 | 0.0060627 | 0.067652 | 0.0022987 | -0.005503 | -0.0040437 | -0.0015637 | 0.06542 | 0.064108 | 0.0044733 | -0.0087606 | 60.9238 | -60.7956 | 0.027466 | -60.9421 | 60.9192 | -60.9604 | -60.9329 | -61.2808 | 0.064087 | -61.2442 | 60.8597 | 60.8643 | -60.8414 | -60.997 | -0.07782 | -0.050354 | 0.01831 | 0.086975 | -0.05951 | -0.009156 | 0.022888 | 0.041198 | -0.11444 | -0.041199 | -0.39825 | -0.36163 | -0.24719 | -0.036621 | 121.8018 | 121.8063 | 60.91 | -121.8338 | 121.7422 | 121.7468 | 60.9467 | -121.8979
18.1094 | 122.0856 | -60.9055 | 60.8734 | -0.013122 | 0.0065732 | 0.071617 | 0.0026447 | 0.067011 | -0.0026147 | -0.0014442 | -0.0040437 | -0.0049817 | 0.061361 | 0.064322 | 0.0025507 | -0.0049154 | 60.9375 | -60.7407 | 0.032043 | -60.9512 | 60.8276 | -60.9787 | -60.8963 | -61.2808 | 0.086975 | -61.1847 | 60.759 | 60.791 | -60.8505 | -61.0291 | -0.073242 | 0.009156 | -0.045776 | 0.16479 | -0.045776 | -0.054932 | 0.064087 | 0.054932 | -0.1236 | -0.11444 | -0.37537 | -0.27923 | -0.15564 | -0.082397 | 121.7331 | 121.843 | 60.9375 | -121.7697 | 121.6644 | 121.6965 | 60.9924 | -121.9025
19.8438 | 121.9986 | -60.9375 | 60.9009 | -0.0054933 | 0.012341 | 0.067131 | 0.0011493 | 0.067866 | 0.00080326 | -0.0014442 | 0.0035858 | -0.0030591 | 0.060507 | 0.064322 | 0.0053279 | -0.007479 | 60.9833 | -60.7132 | 0.064087 | -60.8963 | 60.8139 | -60.9695 | -60.878 | -61.2167 | 0.082397 | -61.1755 | 60.7544 | 60.791 | -60.8276 | -61.0199 | -0.032043 | 0.059509 | -0.086975 | 0.2243 | 0.041199 | -0.01831 | 0.082397 | 0.10986 | -0.082397 | -0.14648 | -0.27924 | -0.23804 | -0.15564 | -0.10986 | 121.7514 | 121.9208 | 61.0016 | -121.7789 | 121.6919 | 121.7285 | 61.0199 | -121.9208
21.5312 | 122.0627 | -60.9329 | 60.878 | 0.0021362 | 0.012127 | 0.069481 | 0.0056355 | 0.067439 | -0.0019739 | -0.0027258 | -0.011673 | -0.0062635 | 0.06542 | 0.064749 | -0.00086734 | -0.0061972 | 60.91 | -60.7498 | 0.022888 | -60.9375 | 60.8459 | -60.9604 | -60.9192 | -61.2808 | 0.07782 | -61.1801 | 60.7773 | 60.7864 | -60.8551 | -61.0199 | -0.027466 | 0.013733 | -0.032044 | 0.1831 | -0.004578 | -0.018311 | 0.032043 | 0.077819 | -0.086975 | -0.10071 | -0.3479 | -0.24719 | -0.16022 | -0.091553 | 121.7789 | 121.843 | 60.9558 | -121.7972 | 121.7102 | 121.7194 | 61.0107 | -121.8979
23.2812 | 121.9986 | -60.9604 | 60.9192 | -0.0054933 | 0.0117 | 0.066917 | 0.0034991 | 0.06573 | 0.0020849 | 0.00047844 | -0.019302 | -0.0049817 | 0.062429 | 0.066031 | 0.0040461 | -0.006838 | 60.9787 | -60.7132 | 0.045776 | -60.9009 | 60.8185 | -60.9512 | -60.8643 | -61.2076 | 0.07782 | -61.1664 | 60.7636 | 60.7819 | -60.8505 | -61.0153 | 0.009155 | 0.09613 | -0.10071 | 0.24719 | 0.059509 | -0.036621 | 0.05951 | 0.10986 | -0.054932 | -0.15564 | -0.24719 | -0.20599 | -0.15106 | -0.13733 | 121.7789 | 121.9391 | 61.0062 | -121.7834 | 121.7239 | 121.7422 | 61.0382 | -121.9345
25.0156 | 121.9528 | -60.965 | 60.878 | -0.0054933 | 0.011059 | 0.067986 | 0.0030719 | 0.068934 | -0.0026147 | -0.0016578 | -0.011673 | -0.0064771 | 0.06307 | 0.063681 | 0.0023371 | -0.007479 | 60.9512 | -60.7132 | 0.018311 | -60.9329 | 60.791 | -60.9695 | -60.9009 | -61.2808 | 0.064087 | -61.2076 | 60.7407 | 60.8093 | -60.8551 | -61.0153 | -0.004577 | 0.064087 | -0.086975 | 0.25177 | 0.032044 | -0.032043 | 0.073242 | 0.10986 | -0.050354 | -0.13733 | -0.31586 | -0.24262 | -0.19226 | -0.068665 | 121.756 | 121.9162 | 60.9833 | -121.7789 | 121.7056 | 121.7743 | 61.0291 | -121.8933
26.6875 | 121.9849 | -60.9375 | 60.8963 | 0.0097657 | 0.0076414 | 0.068199 | 0.0022175 | 0.064234 | -0.0036829 | -0.0035804 | -0.0040437 | -0.0066907 | 0.061361 | 0.064963 | 0.0019099 | -0.0059836 | 60.9055 | -60.7544 | -0.013733 | -60.9695 | 60.8231 | -60.9833 | -60.8917 | -61.3174 | 0.036621 | -61.2305 | 60.759 | 60.8047 | -60.8414 | -61.0245 | -0.045776 | 0.045776 | -0.073242 | 0.1831 | -0.032043 | -0.077819 | 0.009156 | 0.09613 | -0.086975 | -0.13733 | -0.37994 | -0.29297 | -0.20599 | -0.091552 | 121.7606 | 121.843 | 60.9238 | -121.788 | 121.6965 | 121.7422 | 60.9741 | -121.9208
28.4219 | 122.0398 | -60.8871 | 60.9238 | -0.013122 | 0.011914 | 0.070549 | 0.0056355 | 0.065089 | -5.1338e-05 | -0.0018714 | -0.0040437 | -0.0045545 | 0.063711 | 0.066672 | 0.0029779 | -0.0064108 | 60.9375 | -60.7544 | 0.036621 | -60.9421 | 60.8734 | -60.9467 | -60.878 | -61.2808 | 0.054932 | -61.2534 | 60.8368 | 60.8551 | -60.8551 | -61.0153 | -0.059509 | 0.009155 | -0.050354 | 0.13275 | -0.054932 | -0.064087 | 0.013733 | 0.032043 | -0.12817 | -0.086975 | -0.39368 | -0.36621 | -0.23804 | -0.068664 | 121.7606 | 121.8246 | 60.9238 | -121.8018 | 121.7239 | 121.7422 | 60.9421 | -121.9391
30.0938 | 121.962 | -60.9375 | 60.8826 | -0.013122 | 0.0093504 | 0.067558 | 0.0041401 | 0.063593 | -0.00047854 | -0.0033668 | -0.0040437 | -0.0054089 | 0.063284 | 0.064322 | 0.0019099 | -0.0076926 | 60.9238 | -60.7407 | 0.009155 | -60.9467 | 60.8047 | -60.9787 | -60.8917 | -61.2808 | 0.036621 | -61.2488 | 60.7544 | 60.7819 | -60.8826 | -61.0245 | -0.041199 | 0.045776 | -0.077819 | 0.19684 | -0.009155 | -0.054931 | 0.041199 | 0.054932 | -0.086975 | -0.12817 | -0.34332 | -0.31128 | -0.2243 | -0.10071 | 121.7422 | 121.8613 | 60.9467 | -121.7743 | 121.6919 | 121.7194 | 60.9741 | -121.907
31.8594 | 121.9391 | -60.9375 | 60.9421 | -0.013122 | 0.012982 | 0.065636 | -0.0012005 | 0.065089 | 0.0065711 | -0.002085 | -0.0040437 | -0.0030591 | 0.064138 | 0.066031 | 0.0059687 | -0.0083334 | 60.9421 | -60.759 | 0.032043 | -60.9238 | 60.9009 | -60.9467 | -60.8734 | -61.2717 | 0.018311 | -61.2717 | 60.8414 | 60.8322 | -60.8505 | -61.0062 | -0.009155 | 0.064087 | -0.041199 | 0.17853 | 0.013733 | -0.050354 | 0 | 0.086975 | -0.068665 | -0.10071 | -0.33417 | -0.33417 | -0.2655 | -0.10986 | 121.8384 | 121.8796 | 60.9695 | -121.8155 | 121.7789 | 121.7697 | 60.9558 | -121.9482
33.5938 | 122.0581 | -60.878 | 60.9192 | -0.013122 | 0.01405 | 0.068199 | 0.0049945 | 0.067652 | -0.0011193 | -0.002085 | -0.0040437 | -0.0043409 | 0.066061 | 0.064749 | 0.0038325 | -0.0064108 | 60.8963 | -60.759 | 0.004578 | -60.9604 | 60.9009 | -60.9695 | -60.9055 | -61.3037 | 0.050354 | -61.2534 | 60.8368 | 60.8826 | -60.8505 | -61.0016 | -0.091552 | -0.027466 | -0.01831 | 0.11902 | -0.082397 | -0.054931 | -0.022888 | 0.027466 | -0.1236 | -0.082397 | -0.42572 | -0.37537 | -0.25177 | -0.036621 | 121.7789 | 121.7743 | 60.8826 | -121.8246 | 121.7148 | 121.7606 | 60.9283 | -121.9208
35.3281 | 121.9528 | -60.9467 | 60.8963 | -0.0054933 | 0.011059 | 0.068626 | 0.0039265 | 0.066371 | -0.0015465 | -0.0035804 | -0.0040437 | -0.0071179 | 0.062002 | 0.06539 | 0.0019099 | -0.0059836 | 60.9009 | -60.6995 | 0.032043 | -60.9421 | 60.7773 | -60.9741 | -60.9055 | -61.2762 | 0.064087 | -61.1984 | 60.7407 | 60.7864 | -60.8368 | -61.0153 | -0.027466 | 0.041198 | -0.11902 | 0.24719 | 0.004577 | -0.036621 | 0.004578 | 0.10986 | -0.068665 | -0.15564 | -0.32959 | -0.25177 | -0.1831 | -0.10986 | 121.7239 | 121.8475 | 60.9787 | -121.8018 | 121.6873 | 121.7331 | 61.0107 | -121.9116
37 | 122.0718 | -60.8917 | 60.8643 | -0.013122 | 0.0084958 | 0.070763 | 0.0037127 | 0.065089 | -0.0036829 | -0.00058956 | -0.0040437 | -0.0081861 | 0.060507 | 0.063681 | 0.0010553 | -0.0055564 | 60.91 | -60.7407 | 0.036621 | -60.9192 | 60.8276 | -60.965 | -60.9055 | -61.2534 | 0.11444 | -61.1572 | 60.7681 | 60.7864 | -60.8459 | -60.9833 | -0.073242 | -0.013733 | -0.036621 | 0.15106 | -0.027465 | -0.013732 | 0.045776 | 0.045777 | -0.091552 | -0.096131 | -0.36163 | -0.2655 | -0.17395 | -0.07782 | 121.7194 | 121.8018 | 60.9283 | -121.7697 | 121.6599 | 121.6782 | 61.0062 | -121.8475
38.75 | 122.0581 | -60.9055 | 60.878 | -0.013122 | 0.014264 | 0.069054 | 0.0060627 | 0.067866 | -0.0021875 | -0.0044348 | -0.0040437 | -0.0054089 | 0.062856 | 0.063895 | 0.00041446 | -0.0081198 | 60.9833 | -60.6491 | 0.09613 | -60.8917 | 60.8185 | -60.9558 | -60.8688 | -61.203 | 0.16022 | -61.1343 | 60.7636 | 60.7544 | -60.8368 | -61.0062 | -0.050354 | 0.036622 | -0.05951 | 0.25635 | 0.013733 | -0.022889 | 0.10528 | 0.068665 | -0.10071 | -0.11444 | -0.29755 | -0.22888 | -0.12817 | -0.1236 | 121.7239 | 121.8887 | 61.0016 | -121.7468 | 121.669 | 121.6599 | 61.0657 | -121.8842
40.4844 | 122.0856 | -60.9055 | 60.8551 | -0.0054933 | 0.0048642 | 0.070335 | 0.0037127 | 0.064662 | -0.0024011 | -0.002085 | 0.0035858 | -0.0047681 | 0.059011 | 0.064963 | 0.0025507 | -0.0076926 | 60.91 | -60.7132 | 0.018311 | -60.9238 | 60.8185 | -60.9512 | -60.8917 | -61.2488 | 0.10529 | -61.171 | 60.7407 | 60.7636 | -60.8414 | -61.0062 | -0.045776 | 0.013733 | -0.036622 | 0.19226 | -0.01831 | -0.032043 | 0.054931 | 0.064087 | -0.10071 | -0.11444 | -0.34332 | -0.2655 | -0.16479 | -0.091553 | 121.7239 | 121.8155 | 60.9238 | -121.7468 | 121.6461 | 121.669 | 61.0107 | -121.8613
42.1562 | 121.9803 | -60.9421 | 60.8871 | -0.0054933 | 0.0093504 | 0.068413 | 0.00072207 | 0.066157 | 0.0014441 | -0.0014442 | -0.0040437 | -0.0047681 | 0.059011 | 0.06539 | 0.0061823 | -0.0091878 | 60.9787 | -60.6857 | 0.059509 | -60.878 | 60.8093 | -60.965 | -60.8734 | -61.1893 | 0.091553 | -61.1801 | 60.7544 | 60.7864 | -60.8185 | -60.9879 | -0.022888 | 0.068665 | -0.07782 | 0.25635 | 0.064087 | -0.004578 | 0.091553 | 0.1236 | -0.045776 | -0.13275 | -0.24719 | -0.23804 | -0.19226 | -0.10071 | 121.7514 | 121.9208 | 61.0016 | -121.7606 | 121.6965 | 121.7285 | 61.0336 | -121.875
43.9062 | 121.9482 | -60.9329 | 60.9329 | 0.0021362 | 0.014264 | 0.067558 | 0.0013629 | 0.068293 | 0.0048621 | 0.00069204 | -0.0040437 | -0.0030591 | 0.061575 | 0.065176 | 0.0068231 | -0.0053426 | 60.9055 | -60.8368 | -0.032043 | -60.9558 | 60.9055 | -60.9558 | -60.8826 | -61.2717 | -0.036621 | -61.2579 | 60.8322 | 60.8963 | -60.8276 | -60.9924 | -0.022889 | 0.050354 | -0.027465 | 0.09613 | -0.022889 | -0.073243 | -0.027465 | 0.10528 | -0.05951 | -0.10071 | -0.33875 | -0.32501 | -0.2655 | -0.036621 | 121.8384 | 121.8384 | 60.9009 | -121.8155 | 121.7651 | 121.8292 | 60.8963 | -121.9254
45.6562 | 121.9391 | -60.9604 | 60.8917 | -0.0054933 | 0.0099912 | 0.067986 | 0.0041401 | 0.065516 | -0.0015465 | -0.0012306 | -0.0040437 | -0.0058361 | 0.061788 | 0.063681 | 0.0012689 | -0.0038474 | 60.9558 | -60.6949 | 0.068665 | -60.9238 | 60.8047 | -60.9604 | -60.8826 | -61.2488 | 0.059509 | -61.1801 | 60.704 | 60.7864 | -60.8414 | -61.0382 | 0 | 0.07782 | -0.086975 | 0.2655 | 0.036621 | -0.041199 | 0.064087 | 0.11902 | -0.07782 | -0.18768 | -0.28839 | -0.21973 | -0.14191 | -0.10529 | 121.7651 | 121.9162 | 61.0291 | -121.7743 | 121.6644 | 121.7468 | 61.0199 | -121.9299
47.4062 | 121.9666 | -60.9238 | 60.9238 | -0.0054933 | 0.010846 | 0.066917 | 0.0028583 | 0.065943 | 0.0016577 | 0.001333 | -0.0040437 | -0.0013501 | 0.063711 | 0.066885 | 0.0059687 | -0.0047018 | 60.9009 | -60.8139 | -0.027466 | -60.9558 | 60.8871 | -60.9467 | -60.8551 | -61.29 | -0.032043 | -61.2717 | 60.8231 | 60.8551 | -60.8231 | -60.997 | -0.022888 | 0.068664 | -0.036621 | 0.10986 | -0.032044 | -0.10071 | -0.022888 | 0.10071 | -0.073242 | -0.10071 | -0.36621 | -0.3479 | -0.27466 | -0.068664 | 121.8109 | 121.8246 | 60.8963 | -121.7789 | 121.7468 | 121.7789 | 60.8917 | -121.9208
49.0781 | 121.9482 | -60.9283 | 60.9009 | -0.0054933 | 0.01405 | 0.069695 | 0.0026447 | 0.063166 | 0.0033667 | -0.00037596 | -0.011673 | -0.0039135 | 0.064138 | 0.066245 | 0.0036189 | -0.005129 | 60.8826 | -60.8139 | -0.018311 | -60.9558 | 60.8963 | -60.9604 | -60.878 | -61.2991 | -0.018311 | -61.2625 | 60.8459 | 60.8734 | -60.8185 | -60.9741 | -0.032043 | 0.050354 | -0.004578 | 0.11444 | -0.027466 | -0.07782 | -0.018311 | 0.10986 | -0.045776 | -0.054932 | -0.37079 | -0.33417 | -0.28839 | -0.027466 | 121.8246 | 121.8109 | 60.91 | -121.7789 | 121.7743 | 121.8018 | 60.91 | -121.875
50.8281 | 121.9849 | -60.9192 | 60.9055 | -0.020752 | 0.015973 | 0.065636 | 0.0034991 | 0.065302 | 0.0027259 | 0.00090584 | -0.0040437 | -0.00070932 | 0.063497 | 0.064322 | 0.0036189 | -0.0059836 | 60.9787 | -60.7086 | 0.073242 | -60.9009 | 60.8871 | -60.9192 | -60.8551 | -61.2442 | 0.073242 | -61.1938 | 60.8322 | 60.8643 | -60.8185 | -60.9741 | 0 | 0.064086 | -0.018311 | 0.21057 | 0.01831 | -0.045776 | 0.073242 | 0.10071 | -0.054932 | -0.073243 | -0.32501 | -0.27466 | -0.21973 | -0.041199 | 121.8063 | 121.8979 | 60.9924 | -121.7606 | 121.7514 | 121.7834 | 60.9924 | -121.8796
52.4844 | 122.0444 | -60.8871 | 60.9146 | -0.0054933 | 0.014477 | 0.069054 | 0.0077717 | 0.061671 | -0.0024011 | 0.00026484 | -0.011673 | -0.0064771 | 0.064565 | 0.061972 | -0.00022634 | -0.0047018 | 60.8643 | -60.7773 | 0.018311 | -60.9467 | 60.8505 | -60.965 | -60.8826 | -61.3129 | 0.045776 | -61.2396 | 60.8551 | 60.8734 | -60.8688 | -60.9879 | -0.07782 | 0.004578 | -0.064087 | 0.10986 | -0.059509 | -0.064087 | -0.050354 | 0.018311 | -0.10071 | -0.059509 | -0.42572 | -0.35248 | -0.25177 | -0.041199 | 121.7377 | 121.7514 | 60.9055 | -121.7972 | 121.7422 | 121.7606 | 60.9329 | -121.9025
54.2188 | 122.0718 | -60.8963 | 60.8688 | 0.0021362 | 0.009564 | 0.067986 | 0.0071307 | 0.063807 | -0.0066735 | -0.0014442 | -0.0040437 | -0.0083997 | 0.06542 | 0.063895 | -0.00086734 | -0.0044882 | 60.9375 | -60.6628 | 0.086975 | -60.8963 | 60.7864 | -60.9695 | -60.8643 | -61.2213 | 0.17395 | -61.1114 | 60.7086 | 60.7681 | -60.8276 | -60.9741 | -0.073242 | 0.032043 | -0.082397 | 0.23346 | 0 | -0.032043 | 0.068665 | 0.068664 | -0.07782 | -0.16022 | -0.32501 | -0.21515 | -0.13733 | -0.10071 | 121.6827 | 121.8338 | 60.9833 | -121.7331 | 121.6049 | 121.6644 | 61.0703 | -121.843
55.8906 | 121.9757 | -60.9283 | 60.9329 | -0.0054933 | 0.011273 | 0.06649 | 0.0043537 | 0.067225 | 0.0027259 | -0.00080316 | -0.0040437 | -0.0019909 | 0.06307 | 0.065817 | 0.0044733 | -0.006838 | 60.8963 | -60.8047 | -0.027466 | -60.9467 | 60.9055 | -60.9512 | -60.8551 | -61.2991 | -0.027466 | -61.2534 | 60.8322 | 60.8505 | -60.8459 | -61.0062 | -0.022888 | 0.073242 | -0.027465 | 0.1236 | -0.01831 | -0.091552 | -0.036621 | 0.082398 | -0.07782 | -0.10071 | -0.37079 | -0.32501 | -0.24719 | -0.082397 | 121.8338 | 121.8246 | 60.9009 | -121.788 | 121.7606 | 121.7789 | 60.9009 | -121.9391
57.625 | 122.0901 | -60.8688 | 60.8826 | -0.020752 | 0.015973 | 0.070122 | 0.0079853 | 0.065302 | -0.00090574 | -0.0016578 | 0.0035858 | -0.0054089 | 0.06542 | 0.063895 | 0.0016963 | -0.0066244 | 60.8826 | -60.7819 | 0.004578 | -60.9192 | 60.8826 | -60.9604 | -60.8826 | -61.2854 | 0.045776 | -61.2259 | 60.8231 | 60.8597 | -60.8459 | -61.0107 | -0.091553 | -0.013733 | 0 | 0.086975 | -0.050354 | -0.036621 | 0 | 0.022888 | -0.14191 | -0.059509 | -0.41657 | -0.35706 | -0.21515 | -0.022888 | 121.7514 | 121.7514 | 60.8734 | -121.7651 | 121.6919 | 121.7285 | 60.9146 | -121.8933
59.2969 | 122.0261 | -60.8963 | 60.8597 | -0.0054933 | 0.010632 | 0.068626 | 0.0081989 | 0.065516 | -0.0041101 | -0.0033668 | -0.011673 | -0.0081861 | 0.061575 | 0.063467 | 0.00020086 | -0.0047018 | 60.9375 | -60.6491 | 0.10986 | -60.878 | 60.7956 | -60.9604 | -60.8871 | -61.2213 | 0.16479 | -61.1206 | 60.7315 | 60.7636 | -60.8231 | -60.9924 | -0.064087 | 0.009155 | -0.064087 | 0.24719 | 0.01831 | 0.009155 | 0.07782 | 0.073242 | -0.096131 | -0.12817 | -0.32501 | -0.2243 | -0.12817 | -0.09613 | 121.6919 | 121.8338 | 61.0062 | -121.7468 | 121.6278 | 121.6599 | 61.0611 | -121.8521
61.0469 | 122.0993 | -60.8643 | 60.9146 | -0.0054933 | 0.0091366 | 0.066917 | 0.0047809 | 0.067652 | 0.0029395 | -0.0014442 | -0.019302 | -0.0028455 | 0.062216 | 0.067099 | 0.0031915 | -0.0098288 | 60.9009 | -60.7544 | 0.022888 | -60.9146 | 60.8643 | -60.9512 | -60.8551 | -61.2579 | 0.091553 | -61.203 | 60.8597 | 60.8643 | -60.8139 | -60.9879 | -0.086975 | 0.009155 | -0.050354 | 0.10986 | -0.050354 | -0.059509 | -0.013733 | 0.050354 | -0.1236 | -0.054932 | -0.39368 | -0.33875 | -0.21515 | -0.050354 | 121.7285 | 121.7651 | 60.8871 | -121.7697 | 121.7239 | 121.7285 | 60.9558 | -121.9025
62.7188 | 122.0123 | -60.8963 | 60.8597 | -0.013122 | 0.010846 | 0.068199 | 0.0069171 | 0.064448 | -0.0060327 | -0.0025122 | -0.011673 | -0.0069043 | 0.063711 | 0.063254 | 0.00062806 | -0.0049154 | 60.9283 | -60.6537 | 0.10986 | -60.8871 | 60.7864 | -60.9283 | -60.8963 | -61.2122 | 0.16937 | -61.1298 | 60.7315 | 60.7819 | -60.8139 | -61.0016 | -0.032044 | 0 | -0.073242 | 0.24261 | 0.009155 | 0.009155 | 0.068665 | 0.082397 | -0.10529 | -0.12817 | -0.31586 | -0.23346 | -0.12817 | -0.07782 | 121.6827 | 121.8246 | 61.0062 | -121.756 | 121.6278 | 121.6782 | 61.0657 | -121.8613
64.4531 | 121.9345 | -60.9146 | 60.9467 | -0.0054933 | 0.0117 | 0.068413 | -0.00013253 | 0.065516 | 0.0044349 | -0.0012306 | -0.0040437 | -0.0028455 | 0.061788 | 0.066245 | 0.0055415 | -0.0070516 | 60.9238 | -60.7452 | 0.018311 | -60.9329 | 60.9238 | -60.9421 | -60.8734 | -61.2625 | 0.018311 | -61.2442 | 60.8185 | 60.8643 | -60.8093 | -60.9833 | -0.027466 | 0.041199 | -0.022888 | 0.16937 | -0.01831 | -0.059509 | -0.022888 | 0.10529 | -0.068664 | -0.12817 | -0.3479 | -0.32959 | -0.26093 | -0.082397 | 121.8384 | 121.8384 | 60.9329 | -121.8201 | 121.7331 | 121.7789 | 60.9329 | -121.9299
66.2031 | 121.9482 | -60.8917 | 60.91 | -0.013122 | 0.010205 | 0.06649 | 0.0028583 | 0.066157 | 0.0027259 | 0.00026484 | -0.0040437 | -0.00092292 | 0.066488 | 0.064536 | 0.0040461 | -0.0032064 | 60.8597 | -60.8047 | -0.041199 | -60.9512 | 60.8871 | -60.9741 | -60.8643 | -61.2946 | -0.009155 | -61.2579 | 60.8322 | 60.8597 | -60.8185 | -61.0016 | -0.082397 | 0.027466 | -0.022888 | 0.086975 | -0.059509 | -0.086975 | -0.050354 | 0.073243 | -0.10986 | -0.07782 | -0.40283 | -0.36621 | -0.25635 | -0.050354 | 121.7789 | 121.7514 | 60.8505 | -121.7743 | 121.7239 | 121.7514 | 60.8826 | -121.9116
67.9375 | 121.9208 | -60.9421 | 60.8826 | -0.013122 | 0.010205 | 0.069695 | 0.0045673 | 0.067011 | -0.0045373 | 5.1244e-05 | -0.0040437 | -0.0083997 | 0.062216 | 0.064108 | 0.0027643 | -0.0044882 | 60.8917 | -60.7132 | 0.018311 | -60.9192 | 60.759 | -60.9512 | -60.8597 | -61.2717 | 0.054932 | -61.1938 | 60.7178 | 60.7819 | -60.8276 | -61.0199 | -0.009155 | 0.082398 | -0.1236 | 0.22888 | 0.022889 | -0.059509 | 0.009156 | 0.11444 | -0.077819 | -0.16479 | -0.32959 | -0.25177 | -0.17395 | -0.10071 | 121.7011 | 121.8338 | 60.9604 | -121.7422 | 121.6599 | 121.7239 | 60.997 | -121.9025
69.6719 | 121.9711 | -60.8826 | 60.9283 | 0.0021362 | 0.01405 | 0.067986 | 0.0032855 | 0.06338 | 0.0012305 | 5.1244e-05 | -0.019302 | -0.0028455 | 0.062643 | 0.06539 | 0.0046869 | -0.0076926 | 60.9695 | -60.704 | 0.073242 | -60.9009 | 60.8505 | -60.9146 | -60.8368 | -61.2305 | 0.068665 | -61.2076 | 60.8368 | 60.8826 | -60.8185 | -60.9787 | -0.032044 | 0.045776 | -0.07782 | 0.17853 | -0.018311 | -0.064087 | 0.041198 | 0.064087 | -0.096131 | -0.091553 | -0.3479 | -0.32501 | -0.22888 | -0.045777 | 121.7331 | 121.8521 | 60.9558 | -121.7651 | 121.7194 | 121.7651 | 60.9512 | -121.907
71.3438 | 121.9208 | -60.9604 | 60.8688 | -0.0054933 | 0.008923 | 0.067131 | 0.0069171 | 0.062739 | -0.0047509 | -0.0016578 | -0.011673 | -0.0073315 | 0.06307 | 0.063254 | 0.0012689 | -0.0021384 | 60.8826 | -60.7315 | 0.018311 | -60.9467 | 60.8139 | -60.9329 | -60.8688 | -61.3129 | 0.032043 | -61.2167 | 60.7407 | 60.7864 | -60.8505 | -61.0016 | 0.027466 | 0.091553 | -0.054931 | 0.22888 | 0.013733 | -0.07782 | 0.013733 | 0.10986 | -0.041199 | -0.12817 | -0.35248 | -0.25635 | -0.21515 | -0.082397 | 121.7743 | 121.843 | 60.9787 | -121.7377 | 121.7011 | 121.7468 | 60.9924 | -121.8704
73.0781 | 121.9666 | -60.9283 | 60.8963 | 0.0021362 | 0.014264 | 0.069908 | 0.0026447 | 0.063593 | 0.0022987 | -0.00080316 | -0.011673 | -0.0039135 | 0.063497 | 0.067526 | 0.0057551 | -0.0059836 | 60.878 | -60.7864 | -0.032043 | -60.9283 | 60.91 | -60.9238 | -60.8688 | -61.2991 | -0.032043 | -61.2488 | 60.8322 | 60.8551 | -60.8276 | -60.9787 | 0.004578 | 0.05951 | 0.013733 | 0.14191 | 0 | -0.05951 | -0.01831 | 0.10071 | -0.050354 | -0.064087 | -0.37079 | -0.32043 | -0.27008 | -0.041198 | 121.8384 | 121.8063 | 60.8963 | -121.7651 | 121.7606 | 121.7834 | 60.8963 | -121.875
74.75 | 121.9528 | -60.9009 | 60.9192 | 0.0021362 | 0.012768 | 0.066917 | 0.0022175 | 0.067225 | 0.0040077 | -0.002085 | 0.0035858 | -0.0034863 | 0.060934 | 0.064749 | 0.0036189 | -0.0053426 | 60.9695 | -60.6995 | 0.068665 | -60.8826 | 60.8688 | -60.9192 | -60.8414 | -61.2259 | 0.059509 | -61.2122 | 60.8414 | 60.8826 | -60.8047 | -60.9741 | -0.01831 | 0.059509 | -0.050354 | 0.20142 | 0.018311 | -0.041198 | 0.050354 | 0.09613 | -0.073242 | -0.077819 | -0.32501 | -0.31128 | -0.23804 | -0.036621 | 121.7697 | 121.8704 | 60.9695 | -121.7606 | 121.7422 | 121.7834 | 60.9604 | -121.8933
76.5 | 121.9254 | -60.91 | 60.9329 | -0.0054933 | 0.01405 | 0.065849 | 0.0043537 | 0.065516 | 0.0040077 | 0.0026148 | -0.019302 | -0.0039135 | 0.063925 | 0.066245 | 0.0057551 | -0.0070516 | 60.9055 | -60.7407 | 0.032043 | -60.9055 | 60.8871 | -60.9192 | -60.8551 | -61.2625 | 0.013733 | -61.2579 | 60.8185 | 60.8276 | -60.8414 | -60.997 | -0.009155 | 0.054931 | -0.045776 | 0.16937 | 0.004577 | -0.050354 | -0.027465 | 0.068664 | -0.086975 | -0.11444 | -0.35248 | -0.3479 | -0.26093 | -0.10528 | 121.7972 | 121.8155 | 60.9421 | -121.788 | 121.7285 | 121.7377 | 60.9238 | -121.9299
78.2344 | 121.994 | -60.878 | 60.9238 | 0.0021362 | 0.011914 | 0.068413 | 0.0069171 | 0.069788 | -0.0047509 | -0.0022986 | 0.0035858 | -0.0081861 | 0.065206 | 0.064322 | -1.2744e-05 | -0.0032064 | 60.9192 | -60.6537 | 0.09613 | -60.8734 | 60.8185 | -60.9146 | -60.8368 | -61.2488 | 0.13275 | -61.171 | 60.7956 | 60.8139 | -60.8047 | -60.9924 | -0.036621 | 0.041199 | -0.10529 | 0.2243 | 0.004578 | -0.036621 | -0.004578 | 0.073242 | -0.11444 | -0.12817 | -0.37079 | -0.29297 | -0.17853 | -0.10986 | 121.6965 | 121.7972 | 60.9741 | -121.7606 | 121.6736 | 121.6919 | 61.0107 | -121.9162
79.9531 | 121.9299 | -60.9146 | 60.9283 | -0.0054933 | 0.013196 | 0.067131 | 0.0028583 | 0.067439 | 0.0010169 | -0.00037596 | -0.0040437 | -0.0043409 | 0.062643 | 0.066245 | 0.0051141 | -0.00577 | 60.8871 | -60.7727 | -0.004578 | -60.9238 | 60.91 | -60.9421 | -60.8505 | -61.29 | -0.004578 | -61.2534 | 60.8231 | 60.8963 | -60.8185 | -60.9787 | -0.027466 | 0.064087 | -0.018311 | 0.14191 | -0.009155 | -0.073242 | -0.041199 | 0.096131 | -0.064087 | -0.10529 | -0.37537 | -0.33875 | -0.27466 | -0.032044 | 121.8246 | 121.8018 | 60.91 | -121.7789 | 121.7377 | 121.8109 | 60.91 | -121.907
81.625 | 121.9299 | -60.9375 | 60.8643 | -0.020752 | 0.012127 | 0.068199 | 0.0026447 | 0.066584 | -0.0030419 | -0.0012306 | 0.0035858 | -0.0079725 | 0.059439 | 0.064749 | 0.0029779 | -0.0053426 | 60.9283 | -60.6674 | 0.064087 | -60.8917 | 60.7864 | -60.9329 | -60.8734 | -61.2259 | 0.09613 | -61.1343 | 60.7727 | 60.7681 | -60.8368 | -60.9879 | 0.004578 | 0.064087 | -0.07782 | 0.27008 | 0.045776 | -0.018311 | 0.064087 | 0.10071 | -0.050354 | -0.091553 | -0.28839 | -0.19684 | -0.14648 | -0.096131 | 121.7239 | 121.8658 | 61.0016 | -121.7377 | 121.7102 | 121.7056 | 61.0336 | -121.8521
83.3594 | 121.907 | -60.9421 | 60.8734 | -0.0054933 | 0.0097776 | 0.066704 | 0.0013629 | 0.067652 | -0.0030419 | -0.0010168 | -0.011673 | -0.0071179 | 0.061788 | 0.06304 | 0.0019099 | -0.0053426 | 60.9283 | -60.6766 | 0.068665 | -60.878 | 60.7864 | -60.9238 | -60.8505 | -61.2259 | 0.086975 | -61.1435 | 60.7498 | 60.7636 | -60.8185 | -60.9833 | 0.018311 | 0.091553 | -0.086975 | 0.2655 | 0.064087 | -0.027466 | 0.054932 | 0.1236 | -0.041198 | -0.1236 | -0.28381 | -0.20142 | -0.16022 | -0.10986 | 121.7285 | 121.8704 | 61.0107 | -121.7239 | 121.6919 | 121.7056 | 61.0291 | -121.8567
85.0938 | 122.0581 | -60.8734 | 60.8963 | -0.0054933 | 0.010846 | 0.068413 | 0.0052081 | 0.065302 | 0.0020849 | -0.0014442 | -0.0040437 | -0.0045545 | 0.062643 | 0.064749 | 0.0036189 | -0.0059836 | 60.8734 | -60.7727 | 0 | -60.9329 | 60.9009 | -60.9421 | -60.8643 | -61.3083 | 0.036621 | -61.2167 | 60.8322 | 60.8643 | -60.8231 | -60.9787 | -0.068665 | 0.009155 | 0.004578 | 0.10071 | -0.059509 | -0.068664 | -0.022888 | 0.050354 | -0.10529 | -0.064087 | -0.43488 | -0.34332 | -0.23804 | -0.032043 | 121.7743 | 121.7468 | 60.8734 | -121.7606 | 121.7056 | 121.7377 | 60.91 | -121.875
86.7812 | 121.9299 | -60.91 | 60.9146 | -0.0054933 | 0.012127 | 0.06649 | 8.127e-05 | 0.065943 | 0.0018713 | -0.0012306 | -0.0040437 | -0.0034863 | 0.059439 | 0.066458 | 0.0053279 | -0.0064108 | 60.9375 | -60.7224 | 0.045776 | -60.9055 | 60.8597 | -60.9283 | -60.8734 | -61.2442 | 0.045776 | -61.2305 | 60.8139 | 60.8551 | -60.8047 | -60.9695 | -0.018311 | 0.036621 | -0.054932 | 0.18768 | 0.004577 | -0.032044 | 0.022888 | 0.10529 | -0.059509 | -0.10071 | -0.33417 | -0.32043 | -0.26093 | -0.059509 | 121.7697 | 121.8475 | 60.9558 | -121.788 | 121.7239 | 121.7651 | 60.9558 | -121.8842
88.5312 | 122.0169 | -60.9055 | 60.8322 | -0.013122 | 0.0082822 | 0.067986 | 0.0026447 | 0.06872 | -0.0041101 | -0.0033668 | -0.0040437 | -0.0083997 | 0.06307 | 0.06539 | 0.00062806 | -0.005129 | 60.8459 | -60.7315 | 0.022888 | -60.9192 | 60.7819 | -60.9283 | -60.8734 | -61.2808 | 0.068665 | -61.1664 | 60.7498 | 60.7864 | -60.8322 | -61.0245 | -0.022888 | 0.032044 | -0.050354 | 0.17395 | -0.013732 | -0.045776 | 0.013733 | 0.073243 | -0.11902 | -0.082397 | -0.37537 | -0.26093 | -0.14191 | -0.045776 | 121.6873 | 121.7514 | 60.9283 | -121.7056 | 121.6553 | 121.6919 | 60.9741 | -121.8567
90.2031 | 121.962 | -60.9283 | 60.8917 | 0.0021362 | 0.0097776 | 0.065422 | 0.0022175 | 0.067439 | 0.00016226 | -0.0029394 | -0.011673 | -0.0069043 | 0.063497 | 0.064108 | 0.0034051 | -0.0064108 | 60.9558 | -60.6857 | 0.054932 | -60.878 | 60.7864 | -60.9238 | -60.8643 | -61.1893 | 0.07782 | -61.1481 | 60.7407 | 60.7727 | -60.8322 | -60.9695 | 0.004578 | 0.064087 | -0.10529 | 0.24262 | 0.050354 | -0.013733 | 0.064087 | 0.096131 | -0.041198 | -0.15106 | -0.26093 | -0.21973 | -0.17853 | -0.11902 | 121.7148 | 121.8842 | 60.9833 | -121.756 | 121.669 | 121.7011 | 61.0062 | -121.8613
91.9062 | 121.8933 | -60.9558 | 60.878 | -0.0054933 | 0.010205 | 0.068199 | 0.0017901 | 0.06573 | -0.0030419 | -0.0014442 | -0.011673 | -0.0049817 | 0.062856 | 0.063895 | 0.0031915 | -0.0055564 | 60.9329 | -60.6857 | 0.059509 | -60.9009 | 60.7727 | -60.9512 | -60.8826 | -61.2534 | 0.054932 | -61.1847 | 60.7269 | 60.759 | -60.8459 | -60.997 | 0.004578 | 0.073243 | -0.10529 | 0.27008 | 0.054932 | -0.018311 | 0.054931 | 0.10986 | -0.041198 | -0.15106 | -0.29755 | -0.22888 | -0.18768 | -0.11902 | 121.7285 | 121.8887 | 61.0153 | -121.7606 | 121.6827 | 121.7148 | 61.0107 | -121.875
93.6406 | 122.049 | -60.8414 | 60.8917 | -0.013122 | 0.015545 | 0.067131 | 0.0077717 | 0.066157 | 0.0010169 | -0.0027258 | -0.011673 | -0.0030591 | 0.063284 | 0.064322 | 0.0014825 | -0.0076926 | 60.8826 | -60.7727 | 0.018311 | -60.9146 | 60.8871 | -60.9375 | -60.8963 | -61.29 | 0.045776 | -61.2167 | 60.8505 | 60.8459 | -60.8231 | -60.965 | -0.09613 | -0.054931 | -0.004578 | 0.068665 | -0.073242 | -0.018311 | -0.009156 | 0.018311 | -0.1236 | -0.041199 | -0.44861 | -0.37537 | -0.25177 | -0.045777 | 121.7285 | 121.7239 | 60.8597 | -121.788 | 121.6919 | 121.6873 | 60.8871 | -121.8567
95.3906 | 121.907 | -60.9512 | 60.878 | -0.013122 | 0.010418 | 0.064781 | 0.0077717 | 0.066584 | -0.0026147 | -0.0022986 | -0.0040437 | -0.0064771 | 0.063497 | 0.062827 | 0.00020086 | -0.0061972 | 60.8826 | -60.7086 | 0.022888 | -60.9192 | 60.7819 | -60.91 | -60.8551 | -61.2579 | 0.032043 | -61.1984 | 60.7452 | 60.7773 | -60.8322 | -60.997 | 0.041199 | 0.09613 | -0.096131 | 0.24262 | 0.032044 | -0.064086 | 0.004577 | 0.11902 | -0.045776 | -0.13275 | -0.3067 | -0.24719 | -0.20142 | -0.10071 | 121.7331 | 121.8338 | 60.9741 | -121.7331 | 121.6965 | 121.7285 | 60.9833 | -121.875
97.0781 | 122.0078 | -60.8734 | 60.8734 | -0.013122 | 0.012341 | 0.067772 | 0.0047809 | 0.066371 | 0.0010169 | -0.0027258 | -0.0040437 | -0.0086133 | 0.063925 | 0.065604 | 0.0021235 | -0.0079062 | 60.9467 | -60.6537 | 0.10986 | -60.8597 | 60.7819 | -60.9238 | -60.8368 | -61.1847 | 0.15106 | -61.1252 | 60.7544 | 60.7681 | -60.8231 | -60.9833 | -0.050354 | 0.036621 | -0.091553 | 0.21973 | 0.013733 | -0.022888 | 0.073242 | 0.050354 | -0.10986 | -0.11902 | -0.31128 | -0.25177 | -0.14191 | -0.10529 | 121.6553 | 121.8201 | 60.9833 | -121.7102 | 121.6278 | 121.6415 | 61.0245 | -121.8567
98.8281 | 121.9666 | -60.878 | 60.8734 | 0.0021362 | 0.013409 | 0.066277 | 0.0017901 | 0.065943 | 0.0048621 | -0.0010168 | -0.011673 | -0.0032727 | 0.062643 | 0.064963 | 0.0070367 | -0.0079062 | 60.9604 | -60.672 | 0.091553 | -60.8734 | 60.8871 | -60.9009 | -60.8368 | -61.203 | 0.068665 | -61.203 | 60.8231 | 60.8459 | -60.8185 | -60.9787 | -0.022888 | 0.041199 | 0.013733 | 0.20599 | 0.004578 | -0.036621 | 0.086975 | 0.05951 | -0.10071 | -0.050354 | -0.32501 | -0.32501 | -0.2243 | -0.027466 | 121.7651 | 121.8384 | 60.9695 | -121.7102 | 121.7011 | 121.7239 | 60.9467 | -121.8521
100.5469 | 121.9528 | -60.9146 | 60.8643 | -0.0054933 | 0.0067868 | 0.067772 | 0.0054217 | 0.064875 | -0.0032555 | -0.0010168 | -0.011673 | -0.0077587 | 0.062216 | 0.063467 | 0.00084166 | -0.0066244 | 60.8505 | -60.7315 | 0.013733 | -60.9283 | 60.8139 | -60.9558 | -60.8597 | -61.2671 | 0.054932 | -61.1984 | 60.7452 | 60.7727 | -60.8368 | -60.9924 | -0.041199 | 0.054932 | -0.050354 | 0.18311 | -0.013733 | -0.068665 | -0.013733 | 0.07782 | -0.07782 | -0.11902 | -0.35248 | -0.28381 | -0.20599 | -0.091553 | 121.7285 | 121.7651 | 60.9283 | -121.7239 | 121.6599 | 121.6873 | 60.9695 | -121.8567
102.2188 | 122.0398 | -60.8414 | 60.8597 | -0.013122 | 0.012982 | 0.063713 | 0.0071307 | 0.06573 | -0.00047854 | -0.0033668 | -0.011673 | -0.0034863 | 0.064138 | 0.06539 | 0.0038325 | -0.006838 | 60.8643 | -60.7681 | 0.018311 | -60.9055 | 60.8826 | -60.9467 | -60.8871 | -61.2534 | 0.059509 | -61.2167 | 60.8002 | 60.8459 | -60.8231 | -60.9833 | -0.10529 | -0.045776 | 0.022888 | 0.073243 | -0.064087 | -0.018311 | 0.004578 | 0.018311 | -0.14191 | -0.059509 | -0.41199 | -0.37537 | -0.23346 | -0.013733 | 121.7239 | 121.7056 | 60.8597 | -121.7468 | 121.6415 | 121.6873 | 60.9009 | -121.843
103.9531 | 122.0352 | -60.8368 | 60.878 | -0.0054933 | 0.016186 | 0.065208 | 0.0047809 | 0.063593 | 0.0040077 | -0.00037596 | -0.019302 | -0.0036999 | 0.064565 | 0.06539 | 0.0044733 | -0.0070516 | 60.9146 | -60.6812 | 0.073242 | -60.8734 | 60.8688 | -60.9146 | -60.8505 | -61.1938 | 0.09613 | -61.1664 | 60.8368 | 60.8231 | -60.7956 | -60.965 | -0.07782 | -0.013733 | -0.009156 | 0.15564 | -0.036621 | -0.022888 | 0.036621 | 0.041199 | -0.12817 | -0.041199 | -0.35706 | -0.32959 | -0.20142 | -0.054932 | 121.7056 | 121.7514 | 60.91 | -121.7285 | 121.6736 | 121.6599 | 60.9329 | -121.843
105.6875 | 121.9711 | -60.8643 | 60.8917 | -0.013122 | 0.011487 | 0.067558 | 0.0060627 | 0.06808 | -0.0019739 | 0.00090584 | -0.011673 | -0.0032727 | 0.063497 | 0.064963 | 0.0012689 | -0.005129 | 60.9009 | -60.6674 | 0.064087 | -60.8963 | 60.8139 | -60.9421 | -60.8688 | -61.2717 | 0.082397 | -61.203 | 60.791 | 60.8368 | -60.8047 | -60.9924 | -0.07782 | -0.004577 | -0.07782 | 0.19684 | -0.032043 | -0.027466 | 0.009155 | 0.059509 | -0.12817 | -0.10071 | -0.40741 | -0.33875 | -0.21057 | -0.054932 | 121.6782 | 121.7651 | 60.9283 | -121.7606 | 121.6553 | 121.7011 | 60.9467 | -121.8842
107.3594 | 121.9574 | -60.9055 | 60.8734 | -0.013122 | 0.010846 | 0.067986 | -0.00034613 | 0.064234 | -0.00069214 | 0.001333 | -0.011673 | -0.0036999 | 0.061148 | 0.064536 | 0.0034051 | -0.0070516 | 60.8871 | -60.7315 | -0.009155 | -60.91 | 60.8414 | -60.9329 | -60.8643 | -61.2122 | 0.045776 | -61.1572 | 60.7498 | 60.759 | -60.8185 | -60.9741 | -0.027465 | 0.041199 | -0.032043 | 0.17395 | -0.004577 | -0.045776 | 0.013733 | 0.086976 | -0.068664 | -0.1236 | -0.3067 | -0.25177 | -0.18311 | -0.11444 | 121.7468 | 121.7926 | 60.8963 | -121.7377 | 121.6553 | 121.6644 | 60.9512 | -121.8475
109.0312 | 121.8933 | -60.8917 | 60.9146 | -0.0054933 | 0.012555 | 0.068199 | 0.0015765 | 0.067011 | 0.0046485 | -0.0016578 | -0.019302 | -0.0045545 | 0.063284 | 0.065604 | 0.0063959 | -0.006838 | 60.9283 | -60.7086 | 0.054932 | -60.9009 | 60.8917 | -60.9146 | -60.8459 | -61.2442 | 0.032043 | -61.235 | 60.8047 | 60.8459 | -60.8002 | -60.9741 | -0.022888 | 0.045777 | -0.022888 | 0.18311 | -0.009155 | -0.054932 | 0.013733 | 0.091553 | -0.082397 | -0.10986 | -0.35248 | -0.34332 | -0.26093 | -0.068665 | 121.7834 | 121.8201 | 60.9467 | -121.7606 | 121.6965 | 121.7377 | 60.9238 | -121.8887
110.7812 | 122.0444 | -60.8322 | 60.8734 | 0.0021362 | 0.013409 | 0.067772 | 0.0054217 | 0.069788 | 0.00058966 | -0.0016578 | 0.0035858 | -0.0032727 | 0.063925 | 0.063254 | 0.0023371 | -0.0053426 | 60.9009 | -60.704 | 0.059509 | -60.8871 | 60.8826 | -60.9283 | -60.8414 | -61.2213 | 0.09613 | -61.1755 | 60.8093 | 60.8322 | -60.8047 | -60.9741 | -0.096131 | -0.009156 | 0.009155 | 0.12817 | -0.054932 | -0.045776 | 0.027466 | 0.027465 | -0.14191 | -0.064087 | -0.3891 | -0.34332 | -0.20142 | -0.041199 | 121.7148 | 121.7331 | 60.8917 | -121.7148 | 121.6415 | 121.6644 | 60.9283 | -121.8475
112.5312 | 122.0078 | -60.8597 | 60.8871 | -0.0054933 | 0.013836 | 0.067772 | 0.0043537 | 0.065516 | 0.0018713 | 0.0028284 | 0.0035858 | -0.0036999 | 0.062856 | 0.063895 | 0.0055415 | -0.00577 | 60.9283 | -60.6537 | 0.07782 | -60.8688 | 60.8597 | -60.9146 | -60.8368 | -61.1984 | 0.10529 | -61.1572 | 60.8185 | 60.8368 | -60.791 | -60.9512 | -0.054932 | 0.022888 | -0.027466 | 0.20599 | -0.009155 | -0.032043 | 0.041199 | 0.068664 | -0.091553 | -0.068665 | -0.33875 | -0.29755 | -0.20599 | -0.050354 | 121.7194 | 121.788 | 60.9375 | -121.7239 | 121.6782 | 121.6965 | 60.965 | -121.8384
114.2031 | 122.0352 | -60.8459 | 60.8734 | -0.013122 | 0.014691 | 0.068199 | 0.0086261 | 0.066157 | -0.0011193 | -0.0027258 | -0.011673 | -0.0043409 | 0.062856 | 0.06539 | 0.0021235 | -0.006838 | 60.8459 | -60.7315 | -0.004578 | -60.9146 | 60.8597 | -60.9146 | -60.8643 | -61.2717 | 0.082397 | -61.1984 | 60.8093 | 60.8551 | -60.8047 | -60.9741 | -0.068665 | -0.018311 | -0.013733 | 0.11444 | -0.068665 | -0.050354 | -0.027466 | 0.041198 | -0.12817 | -0.064087 | -0.42572 | -0.35248 | -0.2243 | -0.01831 | 121.7056 | 121.6919 | 60.8414 | -121.7377 | 121.6553 | 121.7011 | 60.9283 | -121.8475
115.9531 | 121.9711 | -60.8505 | 60.8643 | -0.0054933 | 0.015332 | 0.066277 | 0.0073443 | 0.067225 | -0.0047509 | -0.00080316 | -0.0040437 | -0.0066907 | 0.065206 | 0.066031 | 0.0010553 | -0.007479 | 60.878 | -60.6537 | 0.073242 | -60.8643 | 60.8276 | -60.9329 | -60.8551 | -61.2717 | 0.10071 | -61.1755 | 60.7773 | 60.8139 | -60.8276 | -60.9787 | -0.082397 | -0.004578 | -0.036621 | 0.19684 | -0.013733 | -0.009155 | 0.013733 | 0.022888 | -0.12817 | -0.086975 | -0.42114 | -0.32501 | -0.19684 | -0.050354 | 121.6782 | 121.7285 | 60.9238 | -121.7194 | 121.6278 | 121.6644 | 60.9512 | -121.843
117.7031 | 121.9025 | -60.9192 | 60.9009 | -0.0054933 | 0.013409 | 0.065422 | 0.0032855 | 0.068293 | 0.0020849 | -0.00058956 | 0.0035858 | -0.0034863 | 0.063711 | 0.06774 | 0.0063959 | -0.0059836 | 60.8551 | -60.7498 | -0.009155 | -60.9192 | 60.878 | -60.9146 | -60.8597 | -61.2808 | -0.004578 | -61.235 | 60.8322 | 60.8368 | -60.8002 | -60.9879 | 0.004577 | 0.059509 | -0.022888 | 0.16937 | 0 | -0.059509 | -0.045776 | 0.11902 | -0.068665 | -0.068665 | -0.36163 | -0.31586 | -0.24719 | -0.064087 | 121.7972 | 121.7743 | 60.91 | -121.7606 | 121.7514 | 121.756 | 60.9146 | -121.8887
119.375 | 121.907 | -60.8963 | 60.9146 | -0.0054933 | 0.015332 | 0.067345 | 0.0022175 | 0.065516 | 0.0029395 | -0.00037596 | -0.0040437 | -0.0026319 | 0.063497 | 0.066672 | 0.0044733 | -0.0066244 | 60.9055 | -60.6903 | 0.045776 | -60.8871 | 60.8871 | -60.9467 | -60.8597 | -61.2305 | 0.045776 | -61.2076 | 60.8002 | 60.8505 | -60.7956 | -60.9467 | -0.050354 | 0.036621 | -0.027466 | 0.20599 | 0.009155 | -0.027466 | -0.009155 | 0.10071 | -0.050354 | -0.11444 | -0.33417 | -0.31128 | -0.26093 | -0.064087 | 121.7834 | 121.8018 | 60.9421 | -121.7743 | 121.6965 | 121.7468 | 60.9421 | -121.8613
121.1094 | 122.0215 | -60.8414 | 60.8963 | -0.020752 | 0.012555 | 0.067558 | 0.0052081 | 0.062525 | -0.0015465 | -0.0029394 | -0.0040437 | -0.0039135 | 0.062856 | 0.06539 | 0.00084166 | -0.0053426 | 60.8368 | -60.7452 | 0.009155 | -60.9146 | 60.878 | -60.9329 | -60.8505 | -61.29 | 0.045776 | -61.2213 | 60.8139 | 60.8505 | -60.8093 | -60.9604 | -0.091552 | -0.009155 | -0.01831 | 0.096131 | -0.073242 | -0.064087 | -0.059509 | 0.032044 | -0.11902 | -0.082397 | -0.44861 | -0.37994 | -0.26093 | -0.045776 | 121.7194 | 121.6782 | 60.8505 | -121.7468 | 121.6553 | 121.6919 | 60.8871 | -121.8567
122.8594 | 121.9391 | -60.91 | 60.8551 | -0.0054933 | 0.012555 | 0.068199 | 0.0020039 | 0.066584 | -0.00069214 | -0.002085 | -0.0040437 | -0.0039135 | 0.062643 | 0.067099 | 0.0046869 | -0.0029928 | 60.8551 | -60.7269 | -0.018311 | -60.9192 | 60.8459 | -60.91 | -60.8688 | -61.2625 | 0.022888 | -61.1801 | 60.7819 | 60.7819 | -60.8047 | -60.9833 | 0 | 0.041199 | -0.009156 | 0.18311 | -0.009155 | -0.050354 | 0 | 0.10529 | -0.073242 | -0.073243 | -0.35248 | -0.27008 | -0.19684 | -0.073243 | 121.756 | 121.7651 | 60.8917 | -121.7239 | 121.6919 | 121.6919 | 60.9329 | -121.8384
124.5312 | 121.8796 | -60.8871 | 60.91 | -0.013122 | 0.012982 | 0.066277 | 0.0017901 | 0.065089 | 0.00058966 | 0.00026484 | -0.0040437 | -0.0028455 | 0.06307 | 0.066031 | 0.0053279 | -0.0055564 | 60.8643 | -60.7452 | 0.013733 | -60.91 | 60.8597 | -60.9055 | -60.8459 | -61.2717 | -0.009155 | -61.2442 | 60.7956 | 60.8276 | -60.8047 | -60.9879 | -0.018311 | 0.041199 | -0.050354 | 0.14191 | -0.022888 | -0.064087 | -0.045776 | 0.082397 | -0.10071 | -0.11444 | -0.38452 | -0.35706 | -0.25635 | -0.082397 | 121.7468 | 121.7514 | 60.9009 | -121.756 | 121.6827 | 121.7148 | 60.878 | -121.8979
126.2656 | 122.0123 | -60.8597 | 60.878 | -0.0054933 | 0.011914 | 0.067772 | 0.0064899 | 0.065089 | -0.0013329 | -0.0040076 | -0.0040437 | -0.0058361 | 0.063497 | 0.06539 | -1.2744e-05 | -0.004061 | 60.8414 | -60.7407 | 0.022888 | -60.9146 | 60.8688 | -60.9467 | -60.8551 | -61.3129 | 0.041199 | -61.2259 | 60.8231 | 60.8459 | -60.8368 | -60.9741 | -0.086975 | 0.004577 | -0.009156 | 0.11902 | -0.054932 | -0.059509 | -0.036621 | 0.022888 | -0.11444 | -0.054932 | -0.45319 | -0.36621 | -0.25177 | -0.032044 | 121.7285 | 121.701 | 60.8826 | -121.7331 | 121.6827 | 121.7056 | 60.9009 | -121.8521
127.9375 | 122.0352 | -60.8414 | 60.878 | -0.020752 | 0.0164 | 0.063927 | 0.0092669 | 0.065516 | 0.00080326 | -0.0031532 | 0.0035858 | -0.0028455 | 0.063711 | 0.066458 | 0.0038325 | -0.0066244 | 60.8414 | -60.7361 | 0.018311 | -60.8963 | 60.8643 | -60.9283 | -60.8505 | -61.2488 | 0.082397 | -61.1664 | 60.8185 | 60.8459 | -60.7956 | -60.9604 | -0.086975 | -0.009155 | -0.013733 | 0.10529 | -0.054931 | -0.045776 | -0.036621 | 0.045777 | -0.11902 | -0.05951 | -0.40741 | -0.32501 | -0.20599 | -0.032044 | 121.7056 | 121.6827 | 60.8597 | -121.7285 | 121.6599 | 121.6873 | 60.9238 | -121.8384
129.6719 | 122.0169 | -60.8322 | 60.8551 | -0.013122 | 0.01405 | 0.067558 | 0.0073443 | 0.065089 | 0.0025123 | 0.00090584 | -0.0040437 | -0.0060497 | 0.065847 | 0.065176 | 0.0025507 | -0.0072652 | 60.8826 | -60.704 | 0.041199 | -60.8734 | 60.8734 | -60.9238 | -60.8368 | -61.235 | 0.068665 | -61.1618 | 60.8139 | 60.8459 | -60.8231 | -60.9604 | -0.091553 | -0.004578 | 0.01831 | 0.12817 | -0.041199 | -0.036621 | 0.027465 | 0.009155 | -0.12817 | -0.041199 | -0.40283 | -0.32959 | -0.20142 | -0.009156 | 121.7056 | 121.7148 | 60.8734 | -121.6919 | 121.6461 | 121.6782 | 60.9009 | -121.8155
131.4062 | 122.0169 | -60.8551 | 60.8231 | -0.013122 | 0.011059 | 0.070335 | 0.0043537 | 0.065302 | -0.0053919 | -0.0031532 | -0.011673 | -0.0075451 | 0.06307 | 0.065604 | 0.0012689 | -0.005129 | 60.8963 | -60.64 | 0.073242 | -60.878 | 60.7681 | -60.9283 | -60.8414 | -61.2259 | 0.14191 | -61.0703 | 60.7086 | 60.7773 | -60.7864 | -60.9695 | -0.073242 | 0.013733 | -0.054932 | 0.21515 | -0.022888 | -0.036621 | 0.073242 | 0.068665 | -0.11444 | -0.11444 | -0.37079 | -0.21515 | -0.10071 | -0.045776 | 121.6232 | 121.7514 | 60.9283 | -121.6644 | 121.5637 | 121.6324 | 60.997 | -121.7926
133.1562 | 121.8887 | -60.9238 | 60.878 | 0.0021362 | 0.012768 | 0.06884 | 0.0030719 | 0.062739 | -0.0034691 | -0.005503 | -0.011673 | -0.0077587 | 0.062643 | 0.06539 | 0.00041446 | -0.0061972 | 60.8597 | -60.6995 | 0.009155 | -60.91 | 60.8047 | -60.9375 | -60.8551 | -61.2762 | 0.027466 | -61.1984 | 60.7086 | 60.7681 | -60.8276 | -60.9924 | -0.013733 | 0.068664 | -0.073242 | 0.2243 | 0.013733 | -0.054931 | -0.018311 | 0.09613 | -0.068665 | -0.16937 | -0.35248 | -0.27466 | -0.20599 | -0.10986 | 121.7285 | 121.7834 | 60.9329 | -121.7331 | 121.6324 | 121.6919 | 60.9512 | -121.8704
134.9062 | 121.9025 | -60.9329 | 60.8414 | -0.0054933 | 0.011273 | 0.066917 | 0.00029487 | 0.067225 | -0.00047854 | -0.0029394 | -0.019302 | -0.0047681 | 0.060507 | 0.063254 | 0.0029779 | -0.006838 | 60.9238 | -60.6674 | 0.064087 | -60.8688 | 60.759 | -60.9329 | -60.8276 | -61.1755 | 0.059509 | -61.1206 | 60.7086 | 60.759 | -60.8231 | -60.9467 | 0 | 0.10528 | -0.082398 | 0.2655 | 0.064087 | -0.041198 | 0.082397 | 0.10986 | -0.013733 | -0.13275 | -0.24262 | -0.18768 | -0.17395 | -0.082398 | 121.6919 | 121.8567 | 60.997 | -121.669 | 121.6415 | 121.6919 | 60.9924 | -121.788
136.6562 | 121.9025 | -60.9055 | 60.9238 | -0.0054933 | 0.017468 | 0.067131 | 0.0058491 | 0.066798 | 0.0029395 | 5.1244e-05 | 0.0035858 | -0.00028192 | 0.064565 | 0.064749 | 0.0057551 | -0.007479 | 60.8688 | -60.7956 | -0.045776 | -60.9146 | 60.878 | -60.9238 | -60.8505 | -61.2671 | -0.027466 | -61.2396 | 60.8093 | 60.8322 | -60.8047 | -60.9512 | -0.01831 | 0.054932 | -0.045776 | 0.10986 | -0.009155 | -0.064087 | -0.054932 | 0.10071 | -0.045776 | -0.11444 | -0.36163 | -0.33417 | -0.28839 | -0.091553 | 121.7834 | 121.7743 | 60.8597 | -121.7743 | 121.7148 | 121.7377 | 60.878 | -121.875
138.3906 | 121.9162 | -60.8643 | 60.8871 | -0.013122 | 0.01405 | 0.065422 | 0.0034991 | 0.067011 | 0.0031531 | -0.00058956 | -0.011673 | -0.0024183 | 0.062429 | 0.066885 | 0.0057551 | -0.0055564 | 60.9238 | -60.6812 | 0.064087 | -60.8597 | 60.8734 | -60.8963 | -60.8276 | -61.2213 | 0.041199 | -61.203 | 60.8093 | 60.8368 | -60.8002 | -60.9695 | -0.032043 | 0.036621 | -0.013733 | 0.18311 | 0.004578 | -0.032043 | 0.036621 | 0.064087 | -0.10529 | -0.07782 | -0.35706 | -0.33875 | -0.23346 | -0.050354 | 121.7377 | 121.788 | 60.9283 | -121.7148 | 121.6736 | 121.7011 | 60.9055 | -121.8567
140.0625 | 121.9986 | -60.8459 | 60.8368 | -0.0054933 | 0.0117 | 0.069267 | 0.0077717 | 0.065943 | -0.0051781 | -0.0027258 | -0.011673 | -0.010109 | 0.064138 | 0.06304 | -0.0023627 | -0.0042746 | 60.9192 | -60.5896 | 0.09613 | -60.8597 | 60.7727 | -60.9146 | -60.8459 | -61.1893 | 0.17853 | -61.0977 | 60.7224 | 60.7636 | -60.8139 | -60.9741 | -0.068665 | 0 | -0.064087 | 0.25635 | -0.013733 | -0.013733 | 0.082397 | 0.032043 | -0.12817 | -0.11444 | -0.34332 | -0.25177 | -0.1236 | -0.073242 | 121.6187 | 121.7651 | 60.9421 | -121.6827 | 121.5683 | 121.6095 | 61.0245 | -121.8109
141.8125 | 121.9849 | -60.8871 | 60.8597 | 0.0021362 | 0.012127 | 0.068626 | 0.0067035 | 0.064662 | -0.0034691 | -0.0025122 | -0.011673 | -0.0064771 | 0.063497 | 0.063681 | 0.0025507 | -0.0076926 | 60.9329 | -60.5988 | 0.09613 | -60.8505 | 60.7727 | -60.9238 | -60.8551 | -61.203 | 0.15564 | -61.0977 | 60.7224 | 60.7681 | -60.7956 | -60.9879 | -0.036621 | 0.032043 | -0.086975 | 0.28839 | 0.036621 | 0.004578 | 0.073242 | 0.091553 | -0.10071 | -0.13733 | -0.31586 | -0.21057 | -0.10986 | -0.091553 | 121.6599 | 121.8201 | 60.9833 | -121.7148 | 121.6095 | 121.6553 | 61.0428 | -121.8475
143.5469 | 121.8979 | -60.9192 | 60.8688 | -0.0054933 | 0.0091366 | 0.06649 | -0.00013253 | 0.064234 | -0.00090574 | -0.0016578 | -0.011673 | -0.0062635 | 0.059652 | 0.064322 | 0.0055415 | -0.008547 | 60.9375 | -60.6491 | 0.059509 | -60.8597 | 60.7864 | -60.9192 | -60.8368 | -61.1801 | 0.073242 | -61.1252 | 60.7315 | 60.759 | -60.8185 | -60.9604 | 0 | 0.082397 | -0.082397 | 0.27008 | 0.059509 | -0.022888 | 0.068665 | 0.10071 | -0.041199 | -0.13733 | -0.26093 | -0.20599 | -0.16479 | -0.10986 | 121.7056 | 121.8567 | 60.9787 | -121.7056 | 121.6507 | 121.6782 | 60.9924 | -121.8292
145.2812 | 121.9986 | -60.8414 | 60.8917 | -0.0054933 | 0.018109 | 0.065208 | 0.0047809 | 0.066371 | 0.0027259 | -0.0010168 | -0.0040437 | -0.0030591 | 0.063711 | 0.064963 | 0.0027643 | -0.006838 | 60.9238 | -60.7132 | 0.050354 | -60.8734 | 60.878 | -60.91 | -60.8505 | -61.1984 | 0.082397 | -61.1618 | 60.8185 | 60.8459 | -60.8047 | -60.9558 | -0.068664 | -0.009155 | -0.013733 | 0.12817 | -0.032043 | -0.022888 | 0.032043 | 0.036621 | -0.11444 | -0.073243 | -0.35706 | -0.32043 | -0.20599 | -0.045777 | 121.7194 | 121.7651 | 60.8917 | -121.7422 | 121.6599 | 121.6873 | 60.9238 | -121.8475
146.9531 | 121.8842 | -60.9009 | 60.8826 | -0.013122 | 0.013196 | 0.066063 | 0.0045673 | 0.069788 | 0.0046485 | -0.00058956 | -0.011673 | -0.0011365 | 0.063925 | 0.065176 | 0.0068231 | -0.006838 | 60.8917 | -60.7224 | 0.036621 | -60.8826 | 60.8688 | -60.9055 | -60.8551 | -61.2259 | 0.009155 | -61.235 | 60.8002 | 60.8322 | -60.8093 | -60.9741 | -0.004578 | 0.045776 | -0.013733 | 0.17853 | 0.018311 | -0.027465 | 0.009156 | 0.091553 | -0.073242 | -0.082397 | -0.32501 | -0.33417 | -0.26093 | -0.050354 | 121.7697 | 121.7926 | 60.9375 | -121.7377 | 121.7011 | 121.7331 | 60.91 | -121.8567
148.6875 | 121.9208 | -60.8963 | 60.9055 | 0.0021362 | 0.0117 | 0.067558 | 0.0024311 | 0.066371 | 0.0027259 | -0.00037596 | -0.019302 | -0.0045545 | 0.063284 | 0.065817 | 0.0057551 | -0.0042746 | 60.8459 | -60.7636 | -0.009155 | -60.9283 | 60.8368 | -60.9421 | -60.8276 | -61.2671 | -0.018311 | -61.2442 | 60.8185 | 60.8185 | -60.8185 | -60.9833 | -0.045777 | 0.068664 | -0.068665 | 0.13275 | -0.032044 | -0.10071 | -0.05951 | 0.07782 | -0.086975 | -0.086976 | -0.37079 | -0.3479 | -0.26093 | -0.086976 | 121.7331 | 121.7422 | 60.8871 | -121.7331 | 121.7148 | 121.7148 | 60.878 | -121.8887
150.4219 | 121.9391 | -60.9283 | 60.8414 | -0.0054933 | 0.0099912 | 0.067131 | 0.0022175 | 0.06338 | 0.00016226 | -0.00080316 | 0.0035858 | -0.0054089 | 0.06072 | 0.064108 | 0.0034051 | -0.0055564 | 60.8414 | -60.7178 | -0.004578 | -60.9055 | 60.7956 | -60.9055 | -60.8597 | -61.2122 | 0.054932 | -61.1435 | 60.7224 | 60.7544 | -60.8002 | -60.9741 | 0.022888 | 0.068665 | -0.045777 | 0.21057 | 0.022888 | -0.045777 | 0 | 0.12817 | -0.045776 | -0.11902 | -0.28381 | -0.21515 | -0.16937 | -0.086975 | 121.7239 | 121.7697 | 60.9238 | -121.701 | 121.6507 | 121.6827 | 60.9833 | -121.8155
152.1094 | 122.0398 | -60.8368 | 60.8597 | -0.0054933 | 0.013196 | 0.066063 | 0.0052081 | 0.06573 | 0.00016226 | -0.00080316 | -0.011673 | -0.0028455 | 0.064138 | 0.064749 | 0.0044733 | -0.0070516 | 60.8597 | -60.7269 | 0.032043 | -60.8917 | 60.8414 | -60.9238 | -60.8551 | -61.235 | 0.07782 | -61.1801 | 60.7956 | 60.8322 | -60.7819 | -60.9558 | -0.086975 | -0.018311 | -0.01831 | 0.10986 | -0.054932 | -0.036621 | 0 | 0.054932 | -0.11902 | -0.064087 | -0.39825 | -0.34332 | -0.2243 | -0.027466 | 121.6782 | 121.6965 | 60.8688 | -121.7148 | 121.6324 | 121.669 | 60.9146 | -121.8155
153.8594 | 121.9116 | -69.2276 | 52.4963 | -0.013122 | 0.010632 | 0.068199 | 0.0071307 | 0.066371 | -0.0058191 | -0.0040076 | -0.0040437 | -0.0083997 | 0.064138 | 0.06539 | 0.0012689 | -0.0055564 | 52.5009 | -69.0033 | -0.068665 | -69.2459 | 52.4185 | -69.3192 | -69.2184 | -69.6396 | 0.009155 | -69.5114 | 52.3911 | 52.4048 | -69.1681 | -69.3329 | -0.091553 | 0.009155 | -0.07782 | 0.2243 | -0.018311 | -0.027466 | 0.004578 | 0.059509 | -0.10529 | -0.10529 | -0.41199 | -0.28381 | -0.17853 | -0.091553 | 121.6461 | 121.7285 | 69.1589 | -121.7148 | 121.6187 | 121.6324 | 69.2368 | -121.8292
155.5938 | 121.875 | -70.4224 | 51.3428 | 0.0021362 | 0.0082822 | 0.068199 | 0.0022175 | 0.065516 | 0.0014441 | -0.0029394 | -0.011673 | -0.0079725 | 0.061575 | 0.064108 | 0.0014825 | -0.0055564 | 51.416 | -70.0653 | -0.059509 | -70.3171 | 51.2833 | -70.4178 | -70.3262 | -70.7245 | 0.045776 | -70.6238 | 51.2009 | 51.2466 | -70.3217 | -70.4956 | 0.004577 | 0.09613 | -0.059509 | 0.35706 | 0.10529 | 0.009155 | 0.073243 | 0.10071 | -0.073242 | -0.14191 | -0.30212 | -0.20142 | -0.12817 | -0.09613 | 121.7056 | 121.8384 | 70.3629 | -121.669 | 121.6232 | 121.669 | 70.4681 | -121.8384
157.3594 | 122.0215 | -70.5139 | 51.1688 | -0.0054933 | 0.012768 | 0.069481 | 0.0064899 | 0.066584 | -0.0017603 | -0.0027258 | 0.0035858 | -0.0071179 | 0.063284 | 0.063254 | 0.00084166 | -0.0072652 | 51.2741 | -70.1935 | -0.032043 | -70.4727 | 51.0956 | -70.6284 | -70.5185 | -70.8939 | 0.11902 | -70.7474 | 51.0544 | 51.0681 | -70.4773 | -70.6604 | -0.11444 | -0.004578 | -0.073242 | 0.32043 | 0.041199 | 0.045777 | 0.10529 | 0.036621 | -0.14648 | -0.11444 | -0.37994 | -0.23346 | -0.086975 | -0.10071 | 121.6095 | 121.788 | 70.4819 | -121.6873 | 121.5683 | 121.582 | 70.6329 | -121.8292
159.0312 | 121.8887 | -70.784 | 50.9811 | -0.0054933 | 0.0080686 | 0.069481 | 0.0020039 | 0.06573 | -0.0028283 | -0.0033668 | -0.011673 | -0.0064771 | 0.059652 | 0.063467 | 0.0034051 | -0.0070516 | 51.0178 | -70.5002 | -0.12817 | -70.7336 | 50.9033 | -70.816 | -70.7382 | -71.1411 | 0.022888 | -71.022 | 50.8392 | 50.9033 | -70.6696 | -70.871 | -0.032043 | 0.045777 | -0.07782 | 0.28381 | 0.050354 | 0.004577 | 0.036621 | 0.11444 | -0.086975 | -0.14191 | -0.35706 | -0.23804 | -0.15106 | -0.07782 | 121.6873 | 121.8018 | 70.6558 | -121.7194 | 121.6232 | 121.6873 | 70.8069 | -121.8521
160.75 | 121.9757 | -60.8963 | 60.8368 | 0.0021362 | 0.015332 | 0.067558 | 0.0081989 | 0.067439 | 0.0037939 | -0.0029394 | -0.011673 | -0.0043409 | 0.065847 | 0.062827 | 0.0025507 | -0.0083334 | 60.8322 | -60.7544 | 0.004578 | -60.9283 | 60.8459 | -60.9375 | -60.8734 | -61.2991 | 0.027466 | -61.2442 | 60.7864 | 60.791 | -60.8597 | -61.0107 | -0.041199 | 0.022888 | 0.009155 | 0.14191 | -0.032044 | -0.054932 | -0.004578 | 0.036621 | -0.11444 | -0.050354 | -0.40283 | -0.3479 | -0.23346 | -0.045776 | 121.7422 | 121.7285 | 60.9009 | -121.7102 | 121.6827 | 121.6873 | 60.9238 | -121.8475
162.4219 | 121.8567 | -60.9558 | 60.8368 | 0.0021362 | 0.013409 | 0.064568 | 0.0013629 | 0.062739 | 0.0029395 | -0.00037596 | -0.019302 | -6.8316e-05 | 0.064565 | 0.064749 | 0.0057551 | -0.007479 | 60.8231 | -60.7681 | -0.004578 | -60.9283 | 60.8093 | -60.9512 | -60.8734 | -61.2808 | -0.013733 | -61.2854 | 60.7727 | 60.7819 | -60.8414 | -60.997 | 0.004578 | 0.082398 | -0.027466 | 0.18768 | 0.027466 | -0.054932 | -0.013733 | 0.11444 | -0.041198 | -0.064087 | -0.32501 | -0.32959 | -0.28839 | -0.054932 | 121.7651 | 121.7789 | 60.9512 | -121.7102 | 121.7285 | 121.7377 | 60.9421 | -121.8338
164.0938 | 121.994 | -60.8871 | 60.8231 | 0.0021362 | 0.012768 | 0.06884 | 0.0047809 | 0.066157 | 0.0014441 | -0.0014442 | -0.011673 | -0.0058361 | 0.066061 | 0.063895 | 0.0029779 | -0.008547 | 60.8002 | -60.759 | 0 | -60.9238 | 60.8047 | -60.9467 | -60.878 | -61.2717 | 0.064087 | -61.2305 | 60.7636 | 60.7681 | -60.8368 | -60.9741 | -0.059509 | 0.009155 | -0.01831 | 0.12817 | -0.036621 | -0.045776 | -0.022888 | 0.050354 | -0.086975 | -0.059509 | -0.38452 | -0.34332 | -0.25635 | -0.054932 | 121.6919 | 121.6873 | 60.8871 | -121.7011 | 121.6507 | 121.6553 | 60.9512 | -121.7972
165.8281 | 121.8887 | -60.9558 | 60.8093 | -0.0054933 | 0.0093504 | 0.072258 | 0.0026447 | 0.065943 | -0.0013329 | -0.00058956 | -0.0040437 | -0.0041271 | 0.060079 | 0.066245 | 0.0040461 | -0.00577 | 60.878 | -60.6812 | 0.054932 | -60.9055 | 60.7452 | -60.9604 | -60.8551 | -61.2213 | 0.086975 | -61.1572 | 60.6628 | 60.704 | -60.8459 | -60.9924 | -0.004577 | 0.10071 | -0.064087 | 0.27466 | 0.050354 | -0.050354 | 0.068665 | 0.10986 | -0.036621 | -0.14648 | -0.2655 | -0.20142 | -0.16479 | -0.10529 | 121.701 | 121.8338 | 61.0107 | -121.6644 | 121.6187 | 121.6599 | 61.0428 | -121.8018
167.5 | 121.8658 | -60.9604 | 60.8002 | -0.0054933 | 0.011273 | 0.066917 | 0.0030719 | 0.064875 | -0.0032555 | -0.0027258 | -0.0040437 | -0.0073315 | 0.06072 | 0.06304 | 0.0023371 | -0.0055564 | 60.8505 | -60.6949 | 0.054932 | -60.9375 | 60.6949 | -60.9558 | -60.8963 | -61.2717 | 0.068665 | -61.1984 | 60.64 | 60.6903 | -60.8826 | -61.0245 | 0.004577 | 0.064087 | -0.10529 | 0.2655 | 0.022888 | -0.041199 | 0.050354 | 0.07782 | -0.064087 | -0.16022 | -0.31128 | -0.23804 | -0.17395 | -0.10986 | 121.6553 | 121.8109 | 61.0153 | -121.6965 | 121.6003 | 121.6507 | 61.0291 | -121.8246
169.2344 | 121.8842 | -61.0062 | 60.7773 | -0.0054933 | 0.012982 | 0.067131 | 0.0030719 | 0.063166 | 0.0031531 | 0.00090584 | -0.0040437 | -0.0039135 | 0.060934 | 0.064108 | 0.0042597 | -0.0061972 | 60.7315 | -60.8734 | -0.036621 | -61.0199 | 60.7498 | -61.0291 | -60.9695 | -61.3724 | -0.018311 | -61.3312 | 60.6995 | 60.7269 | -60.9055 | -61.0474 | -0.022888 | 0.036622 | -0.027466 | 0.13275 | -0.013732 | -0.050354 | -0.045777 | 0.10071 | -0.041198 | -0.07782 | -0.36621 | -0.32501 | -0.28381 | -0.050354 | 121.756 | 121.7377 | 60.9695 | -121.7468 | 121.7056 | 121.7331 | 60.9879 | -121.8246
170.9062 | 121.8658 | -60.9833 | 60.791 | -0.0054933 | 0.014905 | 0.066917 | 0.0037127 | 0.066371 | 0.0031531 | -0.0010168 | -0.011673 | -0.0049817 | 0.061148 | 0.064108 | 0.0055415 | -0.0072652 | 60.7498 | -60.8459 | 0 | -61.0153 | 60.7178 | -61.0107 | -60.965 | -61.3541 | -0.004578 | -61.3266 | 60.6812 | 60.7452 | -60.9055 | -61.0794 | -0.027466 | 0.01831 | -0.073243 | 0.13733 | -0.032044 | -0.050354 | -0.041199 | 0.077819 | -0.096131 | -0.10986 | -0.37079 | -0.34332 | -0.24719 | -0.045777 | 121.701 | 121.7331 | 60.9833 | -121.756 | 121.6644 | 121.7285 | 60.9787 | -121.8704
172.6406 | 121.8979 | -61.084 | 60.6766 | -0.013122 | 0.010632 | 0.065422 | 0.0028583 | 0.062525 | 0.0018713 | -0.0016578 | -0.019302 | -0.0049817 | 0.064565 | 0.066885 | 0.0031915 | -0.0055564 | 60.466 | -61.1206 | -0.091553 | -61.2717 | 60.4935 | -61.2671 | -61.1938 | -61.5051 | 0.027466 | -61.4502 | 60.553 | 60.5667 | -61.0428 | -61.1984 | -0.18311 | -0.10986 | -0.18311 | -0.036621 | -0.18768 | -0.077819 | -0.21057 | 0.041198 | -0.11444 | -0.1236 | -0.42114 | -0.36621 | -0.25177 | -0.10986 | 121.5775 | 121.55 | 60.9924 | -121.8704 | 121.637 | 121.6507 | 61.1114 | -121.875
174.375 | 121.8063 | -70.9488 | 50.8301 | -0.0054933 | 0.009564 | 0.067558 | 0.0045673 | 0.065943 | -0.0041101 | -0.0012306 | -0.011673 | -0.0069043 | 0.062002 | 0.065817 | 0.0019099 | -0.0047018 | 50.5783 | -71.0175 | 1.0895 | -71.3837 | 50.4227 | -71.4111 | -71.3196 | -71.4249 | 2.7969 | -71.2143 | 50.5234 | 50.592 | -70.9579 | -71.0999 | -0.46234 | -0.37079 | -0.40741 | -0.068664 | -0.43488 | -0.064087 | -0.25177 | -0.009155 | -0.15106 | -0.3067 | -0.47607 | -0.2655 | -0.11444 | -0.23804 | 121.3715 | 121.5271 | 72.0383 | -122.1497 | 121.4722 | 121.5408 | 73.7457 | -121.9299
176.0625 | 121.9528 | -70.3995 | 51.329 | -0.0054933 | 0.014264 | 0.068626 | 0.0064899 | 0.064021 | 0.00016226 | -0.0018714 | -0.0040437 | -0.0015637 | 0.062429 | 0.063681 | 0.0042597 | -0.0076926 | 51.4526 | -70.0653 | -0.10071 | -70.2896 | 51.4069 | -70.3949 | -70.3171 | -70.6604 | 0.10071 | -70.5872 | 51.3474 | 51.3611 | -70.2438 | -70.4224 | 0.004578 | 0.082397 | 0.077819 | 0.33417 | 0.10986 | 0.027466 | 0.1236 | 0.15564 | -0.022888 | 0.01831 | -0.26093 | -0.18768 | -0.16479 | 0.032043 | 121.8063 | 121.8521 | 70.2988 | -121.6461 | 121.7468 | 121.7606 | 70.5002 | -121.7514
177.8125 | 121.907 | -69.7861 | 52.034 | -0.013122 | 0.013836 | 0.068199 | 0.0030719 | 0.067652 | 0.0022987 | -0.00058956 | -0.011673 | -0.0045545 | 0.06307 | 0.067526 | 0.0036189 | -0.0083334 | 52.0477 | -69.4656 | -0.16937 | -69.6808 | 51.9974 | -69.7952 | -69.6899 | -70.0836 | 0.086975 | -69.9875 | 51.9287 | 51.9745 | -69.6442 | -69.8273 | -0.009155 | 0.096131 | -0.036622 | 0.32044 | 0.10529 | 0.009155 | 0.013732 | 0.14191 | -0.041199 | -0.10529 | -0.29755 | -0.20142 | -0.16022 | -0.05951 | 121.7834 | 121.8338 | 69.6167 | -121.7239 | 121.7148 | 121.7606 | 69.873 | -121.8613
179.5625 | 121.9482 | -71.4386 | 50.2533 | -0.0054933 | 0.013196 | 0.067345 | 0.0062763 | 0.065943 | -0.00069214 | -0.00058956 | -0.019302 | -0.0039135 | 0.062429 | 0.063467 | 0.0019099 | -0.0070516 | 50.2716 | -71.2097 | -0.27924 | -71.4294 | 50.2716 | -71.5164 | -71.4111 | -71.8231 | 0.059509 | -71.7087 | 50.235 | 50.2487 | -71.3882 | -71.5576 | -0.077819 | 0.027466 | 0.01831 | 0.22888 | 0.009156 | -0.01831 | 0.01831 | 0.050354 | -0.11902 | -0.018311 | -0.38452 | -0.27008 | -0.15106 | -0.004578 | 121.7102 | 121.7102 | 71.1594 | -121.6644 | 121.6736 | 121.6873 | 71.4981 | -121.8109
181.2344 | 121.8979 | -73.2422 | 48.4177 | 0.0021362 | 0.01405 | 0.068199 | 0.010549 | 0.065516 | -0.0060327 | -0.0012306 | 0.0035858 | -0.0081861 | 0.065206 | 0.066672 | 0.0010553 | -0.006838 | 48.4863 | -72.9172 | -0.21057 | -73.201 | 48.349 | -73.3337 | -73.2376 | -73.6359 | 0.13733 | -73.4894 | 48.3398 | 48.3536 | -73.2376 | -73.3978 | -0.091553 | 0.004577 | -0.068665 | 0.32501 | 0.041198 | 0.036621 | 0.068664 | 0.004577 | -0.15564 | -0.07782 | -0.39368 | -0.24719 | -0.091553 | -0.064087 | 121.5912 | 121.7285 | 73.0316 | -121.6553 | 121.582 | 121.5958 | 73.3795 | -121.8155
182.9844 | 121.8887 | -72.3358 | 49.4064 | -0.0054933 | 0.012982 | 0.067558 | 0.0020039 | 0.064875 | 0.00037606 | -0.00080316 | -0.0040437 | -0.0041271 | 0.064565 | 0.066031 | 0.0063959 | -0.0053426 | 49.4522 | -72.084 | -0.29755 | -72.3129 | 49.3927 | -72.3862 | -72.29 | -72.7386 | -0.018311 | -72.6517 | 49.3057 | 49.3423 | -72.29 | -72.4686 | -0.050354 | 0.045776 | -0.013733 | 0.25177 | 0.022888 | -0.022888 | 0.045776 | 0.045776 | -0.13275 | -0.10071 | -0.40283 | -0.31586 | -0.18311 | -0.064087 | 121.7285 | 121.788 | 72.0383 | -121.6965 | 121.6415 | 121.6782 | 72.3175 | -121.875
184.7188 | 122.0078 | -109.5612 | 12.0758 | -0.013122 | 0.012555 | 0.067558 | 0.0073443 | 0.067011 | -0.0034691 | -0.0016578 | -0.011673 | -0.0056225 | 0.064993 | 0.064963 | 0.0025507 | -0.005129 | 12.0712 | -109.0851 | -2.0004 | -109.4925 | 12.0392 | -109.8404 | -109.6664 | -110.1425 | -0.027466 | -109.8679 | 11.9751 | 12.0209 | -109.6344 | -109.8358 | -0.27924 | -0.10529 | -0.036621 | 0.47607 | 0.068664 | 0.17395 | -0.004578 | -0.073242 | -0.27466 | -0.10071 | -0.58136 | -0.3067 | -0.032044 | -0.054932 | 121.6003 | 121.6324 | 107.5607 | -121.7422 | 121.5363 | 121.582 | 109.5337 | -121.9116
186.4062 | 122.0032 | -110.2295 | 11.4395 | -0.013122 | 0.013623 | 0.065849 | 0.0039265 | 0.065302 | -0.0036829 | -0.0025122 | -0.0040437 | -0.0066907 | 0.064565 | 0.06539 | -0.0010809 | -0.0070516 | 11.5173 | -109.6161 | -2.037 | -110.0555 | 11.4212 | -110.3943 | -110.2386 | -110.6689 | 0.091553 | -110.376 | 11.348 | 11.38 | -110.2066 | -110.4172 | -0.1648 | -0.009155 | -0.01831 | 0.6134 | 0.17395 | 0.1831 | 0.07782 | 0.022888 | -0.18768 | -0.091553 | -0.43945 | -0.14649 | 0.041198 | -0.059509 | 121.6507 | 121.7468 | 108.1924 | -121.6782 | 121.5775 | 121.6095 | 110.321 | -121.8567
188.1562 | 121.9162 | -110.4584 | 11.261 | 0.0021362 | 0.011273 | 0.067772 | 0.0022175 | 0.066584 | 0.0040077 | -0.0018714 | -0.019302 | -0.0022045 | 0.061788 | 0.067953 | 0.0059687 | -0.008547 | 11.2015 | -110.0143 | -2.3026 | -110.3714 | 11.2473 | -110.6232 | -110.4767 | -110.9802 | -0.11444 | -110.7468 | 11.1832 | 11.2198 | -110.408 | -110.6735 | -0.16479 | -0.018311 | -0.013733 | 0.44403 | 0.086975 | 0.10529 | -0.059509 | 0.050354 | -0.21515 | -0.077819 | -0.52185 | -0.28839 | -0.073242 | -0.041198 | 121.7056 | 121.6599 | 108.1558 | -121.7377 | 121.6415 | 121.6782 | 110.3439 | -121.9345
189.8906 | 121.9345 | -110.8337 | 10.9177 | 0.0021362 | 0.014477 | 0.06649 | 8.127e-05 | 0.064875 | 0.00037606 | -0.002085 | -0.0040437 | -0.0056225 | 0.061361 | 0.066031 | 0.0059687 | -0.0059836 | 10.849 | -110.3485 | -2.3666 | -110.7285 | 10.8856 | -110.9756 | -110.8063 | -111.3235 | -0.07782 | -111.0489 | 10.7941 | 10.849 | -110.7971 | -110.9665 | -0.14191 | 0.027466 | -0.032044 | 0.48523 | 0.10529 | 0.077819 | -0.068665 | 0.036621 | -0.13275 | -0.1236 | -0.48981 | -0.21515 | -0.082397 | -0.068665 | 121.7194 | 121.6827 | 108.4671 | -121.7239 | 121.6278 | 121.6827 | 110.7559 | -121.8842
191.5625 | 121.8658 | -111.0718 | 10.7071 | -0.013122 | 0.01405 | 0.067345 | 0.0026447 | 0.067439 | 0.0031531 | -0.00058956 | 0.0035858 | -0.0032727 | 0.061575 | 0.066031 | 0.0066095 | -0.007479 | 10.6567 | -110.5774 | -2.33 | -110.9207 | 10.6659 | -111.1725 | -111.0397 | -111.525 | -0.059509 | -111.351 | 10.5972 | 10.6247 | -110.9894 | -111.2183 | -0.10071 | 0.032043 | -0.041198 | 0.49438 | 0.15106 | 0.11902 | -0.050354 | 0.082397 | -0.14648 | -0.10986 | -0.45319 | -0.27924 | -0.13275 | -0.082397 | 121.7377 | 121.7285 | 108.7418 | -121.7468 | 121.669 | 121.6965 | 111.0123 | -121.9254
193.3125 | 121.8521 | -111.4426 | 10.3455 | 0.0021362 | 0.015118 | 0.066917 | 0.0034991 | 0.065516 | 0.0031531 | -0.00080316 | -0.0040437 | -0.0032727 | 0.061575 | 0.064749 | 0.0068231 | -0.0036336 | 10.2264 | -110.9573 | -2.4353 | -111.2915 | 10.3134 | -111.5204 | -111.3602 | -111.9049 | -0.050354 | -111.6119 | 10.2722 | 10.3134 | -111.2961 | -111.4883 | -0.07782 | 0.082398 | -0.032043 | 0.48523 | 0.15106 | 0.068664 | -0.11902 | 0.14648 | -0.045776 | -0.073242 | -0.46234 | -0.16937 | -0.1236 | -0.032043 | 121.756 | 121.669 | 109.0073 | -121.7056 | 121.7148 | 121.756 | 111.3922 | -121.8338
195.0469 | 121.9574 | -111.0764 | 10.6064 | -0.0054933 | 0.011059 | 0.067986 | 0.0073443 | 0.067011 | -0.0043237 | -0.0014442 | -0.0040437 | -0.0079725 | 0.063497 | 0.064108 | -0.00022634 | -0.0047018 | 10.6293 | -110.408 | -2.298 | -110.9161 | 10.5606 | -111.2183 | -111.0397 | -111.5295 | 0.11444 | -111.2137 | 10.4965 | 10.5469 | -111.0168 | -111.2412 | -0.14191 | 0.036621 | -0.045776 | 0.66834 | 0.16022 | 0.1236 | 0.022888 | 0.059509 | -0.16479 | -0.10986 | -0.45319 | -0.13733 | 0.027466 | -0.059509 | 121.637 | 121.7056 | 108.7784 | -121.6461 | 121.5729 | 121.6232 | 111.1908 | -121.8475
196.7188 | 121.8567 | -111.5112 | 10.2539 | -0.0054933 | 0.0093504 | 0.06884 | 0.0058491 | 0.064021 | -0.0041101 | -0.0031532 | 0.0035858 | -0.0083997 | 0.060507 | 0.064963 | 0.0014825 | -0.0064108 | 10.2173 | -110.9344 | -2.4216 | -111.3235 | 10.1944 | -111.5616 | -111.4151 | -111.969 | -0.022888 | -111.6531 | 10.1395 | 10.1761 | -111.3922 | -111.6074 | -0.050354 | 0.09613 | -0.059509 | 0.57678 | 0.18768 | 0.091553 | -0.036621 | 0.11902 | -0.096131 | -0.11444 | -0.45776 | -0.14191 | -0.045776 | -0.07782 | 121.7056 | 121.7285 | 109.0897 | -121.669 | 121.6507 | 121.6873 | 111.4883 | -121.8613
198.4531 | 121.8704 | -111.4151 | 10.3775 | 0.0021362 | 0.0097776 | 0.069054 | 8.127e-05 | 0.06808 | -0.00026494 | -0.0014442 | 0.0035858 | -0.0075451 | 0.060293 | 0.063895 | 0.0055415 | -0.00577 | 10.3958 | -110.7513 | -2.3438 | -111.1267 | 10.3088 | -111.4059 | -111.2823 | -111.7218 | 0.027466 | -111.525 | 10.2219 | 10.2722 | -111.2778 | -111.4426 | 0.009155 | 0.13275 | -0.068664 | 0.66376 | 0.28839 | 0.15564 | 0.018311 | 0.13733 | -0.027466 | -0.15564 | -0.3067 | -0.10986 | -0.082397 | -0.10529 | 121.7239 | 121.8109 | 109.0713 | -121.6599 | 121.637 | 121.6873 | 111.4426 | -121.8201
200.1875 | 121.9528 | -111.8271 | 9.8969 | -0.013122 | 0.013409 | 0.06884 | 0.0079853 | 0.065302 | -0.0015465 | -0.0018714 | -0.011673 | -0.0069043 | 0.064993 | 0.06304 | 0.0021235 | -0.006838 | 9.9472 | -111.1725 | -2.3941 | -111.6028 | 9.8648 | -111.8866 | -111.7264 | -112.2116 | 0.10529 | -111.9324 | 9.7778 | 9.819 | -111.731 | -111.9507 | -0.05951 | 0.10071 | -0.032044 | 0.6546 | 0.2243 | 0.1236 | 0.050354 | 0.09613 | -0.1236 | -0.11902 | -0.38452 | -0.10529 | 0.018311 | -0.07782 | 121.6919 | 121.7743 | 109.433 | -121.6232 | 121.6049 | 121.6461 | 111.9324 | -121.8475
201.9219 | 121.8567 | -111.969 | 9.8328 | -0.013122 | 0.011914 | 0.066917 | 0.0022175 | 0.066157 | 0.0044349 | 0.00069204 | -0.0040437 | -0.0028455 | 0.063711 | 0.065817 | 0.0053279 | -0.0064108 | 9.6451 | -111.4792 | -2.5818 | -111.85 | 9.7824 | -112.0697 | -111.8912 | -112.4405 | -0.11444 | -112.2025 | 9.7321 | 9.7549 | -111.882 | -112.0605 | -0.10071 | 0.07782 | -0.050354 | 0.48981 | 0.11902 | 0.041198 | -0.18768 | 0.086975 | -0.091553 | -0.10071 | -0.4715 | -0.23346 | -0.14191 | -0.07782 | 121.7514 | 121.6141 | 109.3872 | -121.7239 | 121.701 | 121.7239 | 111.8546 | -121.8933
203.5938 | 121.7606 | -67.2272 | 54.6341 | 0.0097657 | 0.010205 | 0.069908 | 0.0037127 | 0.065516 | -0.0051781 | -0.002085 | -0.0040437 | -0.0079725 | 0.063284 | 0.064749 | 0.0023371 | -0.0053426 | 54.6204 | -66.8472 | -0.28381 | -67.1082 | 54.5334 | -67.0715 | -67.0074 | -67.4789 | 0.059509 | -67.3416 | 54.4693 | 54.5334 | -66.9708 | -67.1768 | 0.15564 | 0.21973 | -0.10071 | 0.37994 | 0.11902 | -0.10071 | -0.013733 | 0.25635 | 0.050354 | -0.16479 | -0.25177 | -0.11444 | -0.1648 | -0.10071 | 121.7606 | 121.8475 | 66.9434 | -121.6415 | 121.6965 | 121.7606 | 67.2867 | -121.8109
205.3281 | 121.8109 | -67.7353 | 54.0665 | -0.0054933 | 0.012768 | 0.068413 | 0.00072207 | 0.066157 | 0.0031531 | -0.00058956 | -0.0040437 | -0.0049817 | 0.060934 | 0.066031 | 0.0070367 | -0.0070516 | 54.0482 | -67.4927 | -0.29297 | -67.6666 | 54.0115 | -67.6895 | -67.6209 | -68.074 | -0.027466 | -68.0008 | 53.9703 | 54.0115 | -67.5797 | -67.7261 | 0.045777 | 0.11444 | -0.054931 | 0.24262 | 0.068665 | -0.045776 | -0.01831 | 0.15564 | 0.009156 | -0.09613 | -0.33875 | -0.2655 | -0.27466 | -0.054931 | 121.7468 | 121.7834 | 67.4423 | -121.6873 | 121.7056 | 121.7468 | 67.7078 | -121.7926
207 | 121.7834 | -65.4602 | 56.3416 | -0.0054933 | 0.015759 | 0.065422 | 0.0028583 | 0.064021 | 0.0031531 | -0.0010168 | -0.011673 | -0.0036999 | 0.062856 | 0.065176 | 0.0051141 | -0.0070516 | 56.3324 | -65.1993 | -0.25635 | -65.3915 | 56.2958 | -65.3961 | -65.3275 | -65.7852 | -0.17853 | -65.744 | 56.2363 | 56.282 | -65.3229 | -65.4785 | 0.064087 | 0.13275 | -0.045777 | 0.26093 | 0.068664 | -0.064087 | -0.009156 | 0.13733 | -0.018311 | -0.10529 | -0.32501 | -0.28381 | -0.2655 | -0.05951 | 121.756 | 121.7926 | 65.2039 | -121.669 | 121.6965 | 121.7422 | 65.2817 | -121.8201
208.7344 | 121.8887 | -61.1252 | 60.5804 | -0.013122 | 0.013409 | 0.068413 | 0.0077717 | 0.065943 | -0.0032555 | -0.0010168 | 0.0035858 | -0.0086133 | 0.065634 | 0.064749 | 0.0014825 | -0.00577 | 60.553 | -60.9787 | -0.045776 | -61.1526 | 60.5392 | -61.1298 | -61.0657 | -61.5326 | 0.073242 | -61.4365 | 60.5118 | 60.5301 | -61.0657 | -61.2167 | -0.004578 | 0.059509 | -0.041198 | 0.14648 | -0.027466 | -0.086975 | -0.027465 | 0.059509 | -0.091553 | -0.068664 | -0.40741 | -0.31128 | -0.21973 | -0.050354 | 121.6644 | 121.6782 | 61.0794 | -121.6461 | 121.637 | 121.6553 | 61.1984 | -121.7972
210.4219 | 121.8704 | -61.0977 | 60.5896 | -0.0054933 | 0.012555 | 0.068413 | 0.0073443 | 0.065516 | -0.0030419 | -0.003794 | -0.011673 | -0.0066907 | 0.064993 | 0.06539 | -0.00022634 | -0.0076926 | 60.6079 | -60.8734 | 0.036621 | -61.0886 | 60.4935 | -61.1435 | -61.0611 | -61.4685 | 0.16479 | -61.377 | 60.466 | 60.466 | -61.0703 | -61.2167 | -0.045777 | 0.036621 | -0.096131 | 0.2243 | 0.009155 | -0.027466 | 0.01831 | 0.027466 | -0.11902 | -0.1236 | -0.37079 | -0.27924 | -0.16022 | -0.1236 | 121.5912 | 121.7056 | 61.1343 | -121.6507 | 121.5637 | 121.5637 | 61.2625 | -121.8063
212.1562 | 121.875 | -61.084 | 60.6171 | -0.020752 | 0.015332 | 0.068626 | 0.0037127 | 0.06338 | -0.0026147 | -0.002085 | 0.0035858 | -0.0056225 | 0.062216 | 0.063681 | 0.0023371 | -0.0064108 | 60.5896 | -60.9146 | 0.013733 | -61.116 | 60.5301 | -61.1618 | -61.0748 | -61.5097 | 0.10529 | -61.4319 | 60.4752 | 60.5301 | -61.0931 | -61.203 | -0.07782 | 0.009155 | -0.086975 | 0.16937 | -0.032044 | -0.041199 | -0.027465 | -0.009156 | -0.11902 | -0.14191 | -0.42572 | -0.3479 | -0.22888 | -0.086975 | 121.6141 | 121.6736 | 61.0977 | -121.6919 | 121.5591 | 121.6141 | 61.1893 | -121.8201
213.9062 | 121.8613 | -61.1526 | 60.5759 | -0.020752 | 0.012555 | 0.067986 | 0.00029487 | 0.06573 | 0.0040077 | -0.002085 | -0.0040437 | -0.0043409 | 0.061575 | 0.065604 | 0.0063959 | -0.0072652 | 60.553 | -61.0291 | -0.091553 | -61.1664 | 60.5392 | -61.1755 | -61.1069 | -61.5417 | -0.013733 | -61.4731 | 60.5026 | 60.5255 | -61.0886 | -61.2259 | -0.022888 | 0.045776 | -0.036621 | 0.1236 | -0.013733 | -0.059509 | -0.022888 | 0.064087 | -0.073242 | -0.073242 | -0.3891 | -0.32043 | -0.24719 | -0.050354 | 121.6919 | 121.7056 | 61.0611 | -121.6827 | 121.6553 | 121.6782 | 61.1389 | -121.8018
215.5938 | 121.8155 | -61.1801 | 60.553 | 0.0021362 | 0.011487 | 0.06649 | 0.0060627 | 0.064875 | -0.0028283 | -0.00080316 | -0.011673 | -0.0062635 | 0.062002 | 0.063254 | 0.0038325 | -0.0049154 | 60.6033 | -60.9283 | 0.009155 | -61.1481 | 60.4385 | -61.1893 | -61.0931 | -61.4685 | 0.10071 | -61.4044 | 60.379 | 60.466 | -61.0886 | -61.235 | -0.009155 | 0.086975 | -0.11444 | 0.25177 | 0.032044 | -0.054931 | 0.050354 | 0.091553 | -0.054931 | -0.17395 | -0.28839 | -0.2243 | -0.16937 | -0.086976 | 121.6187 | 121.7834 | 61.1893 | -121.6461 | 121.5591 | 121.6461 | 61.2808 | -121.788
217.3281 | 121.9391 | -61.1114 | 60.5392 | -0.0054933 | 0.015759 | 0.070122 | 0.0037127 | 0.066157 | 0.00058966 | -0.0018714 | -0.0040437 | -0.0034863 | 0.064779 | 0.064749 | 0.0051141 | -0.007479 | 60.553 | -60.9787 | -0.013733 | -61.1572 | 60.5484 | -61.1893 | -61.1206 | -61.5143 | 0.086975 | -61.4685 | 60.4843 | 60.5164 | -61.0977 | -61.2396 | -0.07782 | -0.009155 | 0.009155 | 0.13275 | -0.045777 | -0.036622 | 0.013733 | 0.013733 | -0.12817 | -0.054932 | -0.40283 | -0.35706 | -0.22888 | -0.022889 | 121.6599 | 121.6644 | 61.0977 | -121.6599 | 121.5958 | 121.6278 | 61.1984 | -121.7789
219 | 121.8567 | -61.203 | 60.5576 | -0.013122 | 0.012982 | 0.065422 | 0.0026447 | 0.066371 | 0.0020849 | -0.00058956 | -0.0040437 | -0.0019909 | 0.064138 | 0.066885 | 0.0053279 | -0.0053426 | 60.5164 | -61.0611 | -0.086975 | -61.2076 | 60.5026 | -61.2167 | -61.1481 | -61.5692 | -0.022888 | -61.528 | 60.4477 | 60.4843 | -61.116 | -61.2625 | -0.013733 | 0.054932 | -0.054931 | 0.14191 | -0.004578 | -0.05951 | -0.041199 | 0.086975 | -0.059509 | -0.10986 | -0.36621 | -0.32501 | -0.2655 | -0.073242 | 121.7056 | 121.7194 | 61.116 | -121.7056 | 121.6507 | 121.6873 | 61.1801 | -121.8201
220.7344 | 121.9711 | -61.171 | 60.4477 | -0.013122 | 0.010418 | 0.06884 | 0.0069171 | 0.065516 | -0.0058191 | -0.0027258 | -0.0040437 | -0.0071179 | 0.062643 | 0.064536 | -0.00086734 | -0.0047018 | 60.5072 | -60.9787 | -0.009155 | -61.203 | 60.4294 | -61.2259 | -61.1572 | -61.5555 | 0.13275 | -61.4136 | 60.3607 | 60.4019 | -61.1252 | -61.29 | -0.054932 | 0.013732 | -0.018311 | 0.19226 | -0.032044 | -0.045776 | 0.059509 | 0.045776 | -0.11902 | -0.086975 | -0.38452 | -0.24261 | -0.1236 | -0.045776 | 121.6003 | 121.6782 | 61.1618 | -121.6049 | 121.5317 | 121.5729 | 61.3037 | -121.7377
222.4844 | 121.8613 | -61.2076 | 60.4523 | -0.0054933 | 0.0117 | 0.068626 | 0.0032855 | 0.064662 | -0.0051781 | -0.0031532 | -0.011673 | -0.0079725 | 0.059225 | 0.064963 | 0.00062806 | -0.006838 | 60.4568 | -61.0382 | -0.045776 | -61.2534 | 60.3745 | -61.2442 | -61.171 | -61.5967 | 0.050354 | -61.5051 | 60.3424 | 60.3928 | -61.1664 | -61.3129 | -0.036621 | 0.036622 | -0.07782 | 0.16937 | -0.045776 | -0.082398 | 0.004577 | 0.041199 | -0.10529 | -0.10986 | -0.3891 | -0.29755 | -0.19226 | -0.05951 | 121.582 | 121.6644 | 61.1618 | -121.6232 | 121.55 | 121.6003 | 61.2579 | -121.7651
224.2188 | 121.8521 | -61.2579 | 60.4752 | -0.013122 | 0.013409 | 0.067772 | 0.0037127 | 0.064662 | -0.0028283 | -0.0033668 | -0.0040437 | -0.0073315 | 0.061788 | 0.063254 | 0.0021235 | -0.006838 | 60.4706 | -61.0428 | -0.045776 | -61.2396 | 60.3973 | -61.2579 | -61.1801 | -61.6104 | 0.032043 | -61.5234 | 60.347 | 60.3745 | -61.1984 | -61.3129 | 0 | 0.07782 | -0.07782 | 0.21515 | 0.018311 | -0.059509 | -0.004578 | 0.05951 | -0.054931 | -0.12817 | -0.35248 | -0.2655 | -0.21057 | -0.10071 | 121.6553 | 121.7285 | 61.2122 | -121.6553 | 121.6049 | 121.6324 | 61.29 | -121.788
225.9062 | 121.8658 | -61.5234 | 60.1685 | -0.0054933 | 0.0117 | 0.06884 | 0.0020039 | 0.06808 | 0.0027259 | -0.00037596 | -0.011673 | -0.0032727 | 0.062856 | 0.063895 | 0.0040461 | -0.0081198 | 60.1868 | -61.3632 | -0.032043 | -61.5509 | 60.1639 | -61.5692 | -61.4777 | -61.8622 | 0.041199 | -61.8073 | 60.0723 | 60.0906 | -61.4502 | -61.615 | -0.045777 | 0.045776 | -0.004578 | 0.16022 | -0.027466 | -0.073242 | 0.018311 | 0.073242 | -0.091553 | -0.09613 | -0.33875 | -0.28381 | -0.19226 | -0.07782 | 121.6873 | 121.7102 | 61.4914 | -121.6461 | 121.5958 | 121.6141 | 61.5646 | -121.7834
227.6562 | 121.8292 | -61.8896 | 59.8434 | -0.020752 | 0.014691 | 0.065208 | 0.0030719 | 0.065302 | 0.0018713 | -0.0025122 | -0.0040437 | -0.0034863 | 0.062002 | 0.065604 | 0.0049005 | -0.0061972 | 59.7748 | -61.7798 | -0.082397 | -61.9492 | 59.7839 | -61.972 | -61.8805 | -62.3108 | -0.036621 | -62.2925 | 59.7061 | 59.7427 | -61.8256 | -62.027 | -0.082398 | 0.009155 | -0.059509 | 0.10986 | -0.05951 | -0.068665 | -0.068665 | 0.064086 | -0.13733 | -0.13733 | -0.42114 | -0.40283 | -0.2655 | -0.10071 | 121.6736 | 121.6644 | 61.8073 | -121.7239 | 121.5958 | 121.6324 | 61.853 | -121.8704
229.4062 | 121.907 | -61.6608 | 60.0082 | -0.0054933 | 0.015118 | 0.067345 | 0.0058491 | 0.062953 | 0.0020849 | 0.00026484 | -0.011673 | -0.0017773 | 0.063284 | 0.065817 | 0.0044733 | -0.0072652 | 60.0357 | -61.5051 | 0.022888 | -61.7111 | 59.967 | -61.7523 | -61.7065 | -62.0361 | 0.09613 | -62.0087 | 59.8938 | 59.9533 | -61.6425 | -61.821 | -0.091552 | -0.045776 | -0.041199 | 0.15564 | -0.050354 | -0.004578 | 0.027466 | 0.018311 | -0.16022 | -0.11444 | -0.37537 | -0.3479 | -0.18768 | -0.054932 | 121.6278 | 121.6965 | 61.6837 | -121.7148 | 121.5546 | 121.6141 | 61.7569 | -121.8292
231.1406 | 121.9482 | -61.4365 | 60.2234 | -0.013122 | 0.014691 | 0.066277 | 0.0060627 | 0.066157 | 0.0012305 | 0.00069204 | -0.011673 | -0.0047681 | 0.064565 | 0.067313 | 0.0019099 | -0.0076926 | 60.2097 | -61.3083 | -0.022888 | -61.4914 | 60.1822 | -61.5646 | -61.4548 | -61.8439 | 0.082397 | -61.7889 | 60.1135 | 60.1639 | -61.4502 | -61.6013 | -0.12817 | -0.018311 | -0.041199 | 0.12817 | -0.054932 | -0.036621 | -0.013733 | -0.013733 | -0.16479 | -0.10986 | -0.40741 | -0.35248 | -0.18768 | -0.05951 | 121.6187 | 121.6461 | 61.4136 | -121.6782 | 121.55 | 121.6003 | 61.5189 | -121.8246
232.875 | 121.8338 | -61.9858 | 59.761 | -0.0054933 | 0.013836 | 0.065636 | 0.0054217 | 0.065302 | 0.0010169 | 5.1244e-05 | -0.0040437 | -0.0041271 | 0.065206 | 0.066245 | 0.0049005 | -0.0061972 | 59.6695 | -61.8347 | -0.064087 | -61.9995 | 59.7061 | -62.0132 | -61.9492 | -62.3749 | -0.032043 | -62.3337 | 59.6649 | 59.6603 | -61.8942 | -62.059 | -0.027466 | 0.036621 | -0.054931 | 0.15106 | -0.013733 | -0.050354 | -0.091552 | 0.091553 | -0.073242 | -0.09613 | -0.3891 | -0.3479 | -0.27466 | -0.10071 | 121.6919 | 121.6553 | 61.9217 | -121.7102 | 121.6507 | 121.6461 | 61.9537 | -121.8201
234.6094 | 121.8613 | -62.1872 | 59.5505 | -0.013122 | 0.012768 | 0.069054 | 0.0020039 | 0.064875 | -0.00047854 | -0.0022986 | -0.019302 | -0.0045545 | 0.063711 | 0.064108 | 0.0053279 | -0.006838 | 59.491 | -62.0361 | -0.073242 | -62.1964 | 59.5184 | -62.2101 | -62.1002 | -62.5854 | -0.036621 | -62.5397 | 59.4452 | 59.4727 | -62.1094 | -62.2879 | -0.022888 | 0.086975 | -0.032043 | 0.15106 | -0.009155 | -0.09613 | -0.059509 | 0.07782 | -0.10071 | -0.10529 | -0.39825 | -0.35248 | -0.25177 | -0.07782 | 121.7056 | 121.6782 | 62.114 | -121.6507 | 121.6324 | 121.6599 | 62.1506 | -121.8384
236.3438 | 121.8796 | -64.6408 | 57.0786 | -0.013122 | 0.011914 | 0.068199 | 0.0043537 | 0.063166 | -0.00047854 | -0.00037596 | 0.0035858 | -0.0024183 | 0.061361 | 0.06539 | 0.0027643 | -0.0032064 | 57.0786 | -64.4394 | -0.14648 | -64.6225 | 57.0877 | -64.6408 | -64.5767 | -65.007 | -0.022888 | -64.9155 | 57.0007 | 57.0419 | -64.5401 | -64.6957 | 0 | 0.064087 | 0.009156 | 0.20142 | 0.01831 | -0.045777 | 0 | 0.10071 | -0.054932 | -0.07782 | -0.36621 | -0.27466 | -0.21973 | -0.036621 | 121.7285 | 121.7194 | 64.4943 | -121.6553 | 121.6415 | 121.6827 | 64.6179 | -121.7743
238.0156 | 121.9299 | -65.2771 | 56.3324 | 0.0021362 | 0.0065732 | 0.067772 | 0.0041401 | 0.066371 | -0.0049645 | -0.0031532 | -0.019302 | -0.01139 | 0.060507 | 0.064536 | -0.00022634 | -0.0027792 | 56.456 | -64.9704 | -0.1236 | -65.1672 | 56.4194 | -65.2542 | -65.181 | -65.5975 | 0.059509 | -65.4373 | 56.3599 | 56.4056 | -65.1306 | -65.3503 | 0.022889 | 0.096131 | 0.086976 | 0.3067 | 0.10986 | 0.013733 | 0.1236 | 0.14648 | -0.073242 | 0.027466 | -0.32043 | -0.16022 | -0.086975 | 0.073243 | 121.6965 | 121.7331 | 65.1535 | -121.5134 | 121.637 | 121.6827 | 65.3366 | -121.6827
239.75 | 121.8887 | -65.0299 | 56.6666 | -0.0054933 | 0.011273 | 0.067345 | 0.0045673 | 0.064662 | -0.0019739 | -0.0010168 | -0.0040437 | -0.0071179 | 0.059652 | 0.063681 | 0.0049005 | -0.0059836 | 56.7307 | -64.7873 | 0.064087 | -65.0253 | 56.6208 | -65.0574 | -64.9933 | -65.3824 | 0.20142 | -65.2954 | 56.5063 | 56.5567 | -64.975 | -65.1489 | -0.027466 | 0.036621 | -0.045776 | 0.24262 | 0.004577 | -0.032044 | 0.064087 | 0.054931 | -0.11902 | -0.16022 | -0.35248 | -0.2655 | -0.14648 | -0.10986 | 121.6507 | 121.7606 | 65.094 | -121.6599 | 121.5363 | 121.5866 | 65.2313 | -121.8155
241.4688 | 121.8887 | -65.6616 | 56.0211 | -0.0054933 | 0.0117 | 0.069695 | 0.0071307 | 0.067652 | -0.0034691 | -0.0010168 | -0.019302 | -0.0058361 | 0.064352 | 0.067526 | 0.00020086 | -0.0064108 | 56.0761 | -65.3778 | -0.2243 | -65.5884 | 55.9937 | -65.6525 | -65.6021 | -66.0599 | -0.12817 | -65.9317 | 55.957 | 55.9799 | -65.5884 | -65.7532 | 0.009155 | 0.059509 | -0.027466 | 0.28381 | 0.073242 | 0.013733 | 0.054932 | 0.073242 | -0.091553 | -0.064087 | -0.39825 | -0.27008 | -0.17853 | -0.041199 | 121.6553 | 121.7377 | 65.4373 | -121.6232 | 121.6187 | 121.6415 | 65.5334 | -121.7743
243.1562 | 121.8979 | -65.0482 | 56.6071 | -0.0054933 | 0.016186 | 0.070335 | 0.0039265 | 0.067439 | -0.0026147 | -0.0014442 | 0.0035858 | -0.0056225 | 0.06307 | 0.063681 | 0.0016963 | -0.0070516 | 56.6437 | -64.7919 | -0.022888 | -65.0299 | 56.543 | -65.0986 | -65.0391 | -65.4419 | 0.10986 | -65.3275 | 56.4835 | 56.5155 | -65.0299 | -65.181 | -0.050354 | 0.009156 | -0.064087 | 0.25635 | 0.018311 | 0.009155 | 0.036621 | 0.018311 | -0.13275 | -0.1236 | -0.39368 | -0.27924 | -0.14648 | -0.091553 | 121.5912 | 121.6919 | 65.0253 | -121.6461 | 121.5317 | 121.5637 | 65.1581 | -121.788
244.8906 | 121.9666 | -64.801 | 56.8176 | -0.013122 | 0.015545 | 0.068413 | 0.0032855 | 0.065089 | 0.0033667 | -0.0014442 | -0.011673 | -0.0015637 | 0.064352 | 0.064963 | 0.0034051 | -0.0081198 | 56.7627 | -64.769 | -0.059509 | -64.9292 | 56.7169 | -65.007 | -64.8972 | -65.2954 | 0.11444 | -65.2359 | 56.6666 | 56.6711 | -64.8743 | -65.0528 | -0.20599 | -0.096131 | -0.10071 | 0.032043 | -0.12817 | -0.032043 | -0.054932 | -0.073243 | -0.25177 | -0.15106 | -0.49439 | -0.43488 | -0.18311 | -0.14648 | 121.5179 | 121.5637 | 64.7415 | -121.7148 | 121.4676 | 121.4722 | 64.9155 | -121.8704
246.5625 | 121.9116 | -65.5014 | 56.1401 | 0.0021362 | 0.013409 | 0.066063 | 0.0069171 | 0.06338 | -0.00047854 | -0.0016578 | -0.0040437 | -0.0081861 | 0.063711 | 0.065817 | 0.0019099 | -0.0076926 | 56.1035 | -65.3595 | -0.14648 | -65.5884 | 56.0944 | -65.6158 | -65.5563 | -65.9912 | 0.018311 | -65.8997 | 56.0486 | 56.0577 | -65.5426 | -65.6616 | -0.11444 | -0.054931 | -0.045777 | 0.14191 | -0.086975 | -0.032044 | -0.036621 | -0.041199 | -0.16022 | -0.091553 | -0.48981 | -0.39825 | -0.23804 | -0.082398 | 121.5958 | 121.6049 | 65.3549 | -121.6965 | 121.55 | 121.5591 | 65.5197 | -121.8018
248.3125 | 121.9025 | -65.1581 | 56.5063 | -0.013122 | 0.016186 | 0.067772 | 0.0064899 | 0.065302 | -0.0017603 | -0.0022986 | -0.0040437 | -0.0062635 | 0.064993 | 0.063467 | 0.0031915 | -0.0064108 | 56.4423 | -65.0299 | -0.059509 | -65.2496 | 56.3828 | -65.2954 | -65.2039 | -65.6479 | 0.086975 | -65.5609 | 56.3736 | 56.3828 | -65.2176 | -65.3412 | -0.13733 | -0.045776 | -0.1236 | 0.12817 | -0.091553 | -0.045777 | -0.064087 | -0.059509 | -0.18311 | -0.13275 | -0.48981 | -0.40283 | -0.21973 | -0.1236 | 121.5408 | 121.6003 | 65.0986 | -121.7102 | 121.5317 | 121.5408 | 65.2451 | -121.8475
249.9844 | 121.9025 | -65.4144 | 56.282 | -0.0054933 | 0.013836 | 0.067131 | 0.0067035 | 0.063807 | -0.0038965 | -0.0018714 | -0.011673 | -0.0049817 | 0.063711 | 0.06539 | 0.0019099 | -0.0066244 | 56.3141 | -65.1352 | 0.036621 | -65.3732 | 56.1722 | -65.4739 | -65.3824 | -65.744 | 0.22888 | -65.6342 | 56.163 | 56.1813 | -65.3549 | -65.5472 | -0.059509 | 0.032044 | -0.10986 | 0.27924 | 0.041199 | 0.009155 | 0.032044 | 0.05951 | -0.13275 | -0.11902 | -0.32959 | -0.21973 | -0.086975 | -0.10071 | 121.5866 | 121.7285 | 65.451 | -121.6644 | 121.5775 | 121.5958 | 65.6433 | -121.8292
251.7188 | 121.9574 | -65.2496 | 56.3599 | -0.013122 | 0.010205 | 0.067986 | 0.0047809 | 0.067011 | -0.0058191 | -0.0046484 | -0.019302 | -0.0066907 | 0.06072 | 0.065176 | 0.00084166 | -0.0064108 | 56.5292 | -64.9155 | -0.032043 | -65.1489 | 56.4514 | -65.2084 | -65.1489 | -65.5334 | 0.14648 | -65.419 | 56.3461 | 56.3828 | -65.0986 | -65.2863 | 0.041199 | 0.10071 | 0.091553 | 0.33417 | 0.10071 | 0 | 0.16937 | 0.15106 | -0.036621 | -0.013733 | -0.28381 | -0.16937 | -0.13275 | 0.022888 | 121.7011 | 121.7789 | 65.2176 | -121.5088 | 121.5958 | 121.6324 | 65.3961 | -121.6461
253.3906 | 121.8887 | -65.062 | 56.5842 | -0.0054933 | 0.015545 | 0.068199 | 0.0034991 | 0.06573 | -0.0024011 | -0.0035804 | -0.0040437 | -0.0026319 | 0.060507 | 0.063681 | 0.0040461 | -0.007479 | 56.6895 | -64.7552 | -0.041199 | -64.9933 | 56.5796 | -65.1169 | -65.0116 | -65.419 | 0.082397 | -65.3229 | 56.5201 | 56.575 | -64.9979 | -65.1489 | -0.054931 | 0.050354 | -0.004577 | 0.3067 | 0.068665 | 0.018311 | 0.10529 | 0.064087 | -0.086975 | -0.064086 | -0.35706 | -0.26093 | -0.17395 | -0.009155 | 121.6415 | 121.7514 | 65.0208 | -121.5958 | 121.582 | 121.637 | 65.1443 | -121.7331
255.0625 | 121.9482 | -64.9658 | 56.6757 | -0.013122 | 0.011487 | 0.068413 | 0.0056355 | 0.064875 | -0.0024011 | -0.003794 | -0.011673 | -0.0058361 | 0.06307 | 0.06304 | 0.0019099 | -0.0087606 | 56.7673 | -64.6545 | -0.004578 | -64.9384 | 56.6345 | -65.0391 | -64.9567 | -65.3137 | 0.17395 | -65.181 | 56.5292 | 56.6025 | -64.9063 | -65.094 | -0.073242 | 0.009155 | -0.041199 | 0.31128 | 0.027466 | 0.018311 | 0.091553 | 0.059509 | -0.12817 | -0.14648 | -0.3479 | -0.21515 | -0.086975 | -0.073242 | 121.6003 | 121.7331 | 64.9612 | -121.6324 | 121.4951 | 121.5683 | 65.1398 | -121.7697
256.7969 | 121.8292 | -65.0665 | 56.6299 | -0.0054933 | 0.0082822 | 0.067131 | 0.0024311 | 0.063807 | -0.0026147 | -0.0033668 | -0.011673 | -0.0077587 | 0.061361 | 0.063254 | 0.0034051 | -0.00577 | 56.662 | -64.7873 | -0.12817 | -64.9979 | 56.6025 | -65.0574 | -64.9475 | -65.3961 | 0 | -65.2817 | 56.5659 | 56.5796 | -64.92 | -65.1031 | 0.009155 | 0.11902 | -0.027466 | 0.27924 | 0.068664 | -0.050354 | 0.032043 | 0.14648 | -0.036621 | -0.064087 | -0.32959 | -0.21515 | -0.17853 | -0.050354 | 121.669 | 121.7285 | 64.9384 | -121.5775 | 121.6324 | 121.6461 | 65.0665 | -121.7331
258.5312 | 121.7972 | -64.1693 | 57.5134 | -0.020752 | 0.007855 | 0.067558 | 0.00029487 | 0.066157 | -5.1338e-05 | -0.0040076 | 0.0035858 | -0.0054089 | 0.059439 | 0.064322 | 0.0063959 | -0.0072652 | 57.6004 | -63.8626 | -0.018311 | -64.1281 | 57.4677 | -64.1876 | -64.0961 | -64.4165 | 0.11444 | -64.3524 | 57.4173 | 57.4448 | -64.0594 | -64.2242 | -0.01831 | 0.073243 | -0.045777 | 0.3067 | 0.041199 | -0.032044 | 0.086975 | 0.10986 | -0.054931 | -0.096131 | -0.24719 | -0.1831 | -0.12817 | -0.068665 | 121.637 | 121.7697 | 64.151 | -121.6095 | 121.5866 | 121.6141 | 64.2838 | -121.7377
260.2656 | 121.907 | -63.8855 | 57.7606 | -0.0054933 | 0.012341 | 0.063927 | 0.0084125 | 0.063593 | -0.00047854 | -0.002085 | -0.019302 | -0.0066907 | 0.064779 | 0.061972 | 0.0025507 | -0.0072652 | 57.7789 | -63.6749 | -0.07782 | -63.9038 | 57.6508 | -64.0045 | -63.8947 | -64.2197 | 0.1236 | -64.1144 | 57.6599 | 57.6736 | -63.8168 | -63.9954 | -0.11902 | -0.009155 | -0.10986 | 0.21057 | -0.018311 | -0.009156 | 0.018311 | 0.068665 | -0.10986 | -0.10071 | -0.33417 | -0.22888 | -0.11902 | -0.086975 | 121.5363 | 121.6644 | 63.8077 | -121.6553 | 121.5454 | 121.5591 | 64.0091 | -121.756
262 | 121.4676 | -28.775 | 93.0588 | 0.0021362 | 0.0099912 | 0.066063 | 0.0017901 | 0.066157 | 0.00080326 | -0.003794 | -0.011673 | -0.0056225 | 0.06072 | 0.063681 | 0.0072505 | -0.0070516 | 92.9718 | -28.7292 | 0.55389 | -28.8391 | 92.8894 | -28.6652 | -28.6743 | -28.9627 | 0.1831 | -29.0268 | 92.8986 | 92.9031 | -28.6331 | -28.7521 | 0.10986 | 0.10071 | -0.16937 | 0.045776 | -0.064087 | -0.16479 | -0.086975 | 0.14191 | 0.022888 | -0.16022 | -0.18768 | -0.25177 | -0.27466 | -0.15564 | 121.6644 | 121.7468 | 29.3289 | -121.7331 | 121.6736 | 121.6782 | 28.9581 | -121.8109
263.7344 | 121.9528 | -63.5651 | 57.962 | -0.0054933 | 0.014264 | 0.067558 | 0.0062763 | 0.064234 | -0.0017603 | -0.0031532 | -0.0040437 | -0.0081861 | 0.061361 | 0.063467 | 0.0046869 | -0.0072652 | 58.1818 | -63.2584 | -0.59967 | -63.5376 | 58.0444 | -63.6063 | -63.5422 | -63.9084 | -0.44861 | -63.8031 | 57.9346 | 57.9849 | -63.5193 | -63.6795 | -0.041199 | 0.022888 | 0.082398 | 0.3067 | 0.027465 | 0.004577 | 0.21973 | 0.045776 | -0.11444 | -0.027466 | -0.34332 | -0.23804 | -0.1236 | 0.022888 | 121.6095 | 121.7468 | 62.9654 | -121.5042 | 121.4996 | 121.55 | 63.1165 | -121.6415
265.4062 | 122.0261 | -47.9462 | 73.732 | 0.0097657 | 0.017041 | 0.066277 | 0.0045673 | 0.066371 | 0.0052893 | 5.1244e-05 | -0.0040437 | -0.0022045 | 0.061361 | 0.066245 | 0.0040461 | -0.0083334 | 74.501 | -47.1725 | 0.07782 | -47.9416 | 73.97 | -47.7127 | -47.5754 | -48.6832 | -0.19684 | -48.2346 | 73.732 | 73.7961 | -47.7814 | -47.8821 | 0.23346 | 0.37079 | 0.23804 | 0.77362 | 0.004578 | -0.36621 | 0.76904 | 0.1648 | 0.064087 | 0 | -0.737 | -0.28839 | -0.35248 | 0.064087 | 121.9162 | 122.4472 | 48.024 | -121.3074 | 121.6782 | 121.7422 | 47.7493 | -121.6141
267.1406 | 121.7148 | -27.4521 | 94.3542 | -0.013122 | 0.013836 | 0.067558 | 8.127e-05 | 0.064234 | -0.0015465 | -0.0029394 | -0.011673 | -0.0066907 | 0.060507 | 0.064536 | 0.0029779 | -0.0047018 | 94.4092 | -27.2827 | 0.62714 | -27.3972 | 94.3314 | -27.2324 | -27.2507 | -27.6077 | 0.091553 | -27.6672 | 94.249 | 94.3085 | -27.2552 | -27.388 | 0.21973 | 0.20142 | -0.022888 | 0.16937 | 0.054931 | -0.14648 | 0.054932 | 0.19684 | 0.064087 | -0.10529 | -0.15564 | -0.21515 | -0.27924 | -0.045776 | 121.7834 | 121.8613 | 28.0792 | -121.6049 | 121.701 | 121.7606 | 27.5436 | -121.7422
268.8906 | 121.7926 | -27.0813 | 94.6838 | -0.013122 | 0.009564 | 0.069481 | 0.00029487 | 0.067225 | 0.0020849 | -0.0029394 | -0.011673 | -0.0049817 | 0.058584 | 0.062186 | 0.0042597 | -0.0081198 | 94.6335 | -27.095 | 0.63171 | -27.1774 | 94.5511 | -27.0309 | -27.0493 | -27.3422 | 0.16937 | -27.388 | 94.5145 | 94.5648 | -27.0035 | -27.1042 | 0.050354 | 0.032044 | -0.13275 | -0.013733 | -0.09613 | -0.12817 | -0.050354 | 0.07782 | -0.022888 | -0.16937 | -0.26093 | -0.3067 | -0.28381 | -0.11902 | 121.6324 | 121.7148 | 27.713 | -121.7331 | 121.5958 | 121.6461 | 27.2507 | -121.788
270.5781 | 121.8933 | -26.6647 | 95.0226 | -0.0054933 | 0.012768 | 0.069267 | 0.0058491 | 0.066371 | -0.0045373 | -0.0040076 | -0.0040437 | -0.0071179 | 0.06072 | 0.063467 | 0.0012689 | -0.0070516 | 95.0592 | -26.6373 | 0.64545 | -26.7426 | 94.9631 | -26.6235 | -26.6418 | -26.9211 | 0.16479 | -26.9394 | 94.8944 | 94.9951 | -26.5869 | -26.6922 | 0.041199 | 0.022888 | -0.059509 | 0.027466 | -0.07782 | -0.10071 | 0.036621 | 0.07782 | -0.027466 | -0.12817 | -0.25635 | -0.27466 | -0.24719 | -0.027466 | 121.6278 | 121.7239 | 27.3102 | -121.6644 | 121.5591 | 121.6599 | 26.8295 | -121.7148
272.3125 | 121.7697 | -26.564 | 95.2148 | -0.013122 | 0.0097776 | 0.068413 | -0.00034613 | 0.064021 | 0.0014441 | -0.00058956 | -0.0040437 | -0.0069043 | 0.05773 | 0.061972 | 0.0059687 | -0.008547 | 95.137 | -26.6006 | 0.65002 | -26.6556 | 95.0317 | -26.5411 | -26.5594 | -26.8158 | 0.14648 | -26.8753 | 94.9997 | 95.05 | -26.5137 | -26.5961 | 0.022888 | 0.004578 | -0.18311 | -0.036621 | -0.091553 | -0.096131 | -0.07782 | 0.050354 | -0.032043 | -0.21515 | -0.25177 | -0.31128 | -0.27924 | -0.16479 | 121.5958 | 121.701 | 27.214 | -121.7743 | 121.5637 | 121.6141 | 26.7105 | -121.8109
274.0469 | 121.8658 | -26.619 | 95.1187 | -0.0054933 | 0.016827 | 0.068626 | 0.0034991 | 0.065089 | 0.0044349 | -0.0016578 | -0.0040437 | -0.00092292 | 0.062643 | 0.065604 | 0.0057551 | -0.0089742 | 95.0729 | -26.6693 | 0.68207 | -26.6968 | 95.0821 | -26.619 | -26.6098 | -26.8662 | 0.18768 | -26.9806 | 95.0272 | 95.0592 | -26.5549 | -26.6327 | 0 | 0.009156 | -0.036621 | -0.050354 | -0.077819 | -0.086975 | -0.045776 | 0.064087 | -0.013732 | -0.091552 | -0.24719 | -0.36163 | -0.3479 | -0.059509 | 121.7011 | 121.6919 | 27.301 | -121.7285 | 121.6461 | 121.6782 | 26.8066 | -121.7514
275.7812 | 121.8246 | -26.683 | 95.0455 | -0.0054933 | 0.012768 | 0.067772 | 0.0030719 | 0.066584 | -5.1338e-05 | 0.001333 | -0.011673 | -0.0056225 | 0.06307 | 0.063467 | 0.0066095 | -0.0064108 | 94.9493 | -26.77 | 0.54016 | -26.8158 | 95.0409 | -26.6418 | -26.6693 | -26.9669 | 0.036621 | -27.0493 | 94.9356 | 94.9677 | -26.6052 | -26.7288 | 0.041198 | 0.013732 | -0.004577 | -0.086976 | -0.13275 | -0.14648 | -0.09613 | 0.077819 | -0.045777 | -0.10986 | -0.28381 | -0.36621 | -0.32043 | -0.07782 | 121.7239 | 121.6324 | 27.2232 | -121.7148 | 121.6187 | 121.6507 | 26.7197 | -121.7743
277.4531 | 121.8109 | -26.5091 | 95.2286 | -0.0054933 | 0.0117 | 0.06649 | 0.0030719 | 0.062312 | 0.0016577 | -0.00058956 | -0.0040437 | -0.0066907 | 0.061148 | 0.06304 | 0.0044733 | -0.0076926 | 95.1828 | -26.5366 | 0.62714 | -26.619 | 95.1233 | -26.4725 | -26.4725 | -26.7609 | 0.11902 | -26.8387 | 95.0363 | 95.1141 | -26.445 | -26.5457 | 0.036621 | 0.036621 | -0.10529 | -0.027466 | -0.10986 | -0.14648 | -0.045777 | 0.064087 | -0.036621 | -0.19226 | -0.25177 | -0.32959 | -0.29297 | -0.11444 | 121.6324 | 121.6919 | 27.1362 | -121.7011 | 121.5454 | 121.6232 | 26.6281 | -121.7743
279.125 | 121.907 | -26.6876 | 94.9768 | -0.0054933 | 0.010418 | 0.069267 | 0.0047809 | 0.067866 | -0.0062463 | -0.003794 | -0.0040437 | -0.0075451 | 0.062216 | 0.062186 | -1.2744e-05 | -0.0047018 | 94.9905 | -26.6876 | 0.65918 | -26.77 | 94.9722 | -26.6281 | -26.6739 | -26.9211 | 0.23346 | -26.9302 | 94.9127 | 94.9814 | -26.5778 | -26.6785 | 0.059509 | 0.013733 | -0.004578 | 0 | -0.082398 | -0.096131 | 0.013733 | 0.10986 | 0.009155 | -0.064087 | -0.23346 | -0.24262 | -0.25177 | 0.004577 | 121.6599 | 121.6782 | 27.3468 | -121.6507 | 121.6003 | 121.669 | 26.9211 | -121.6553
280.8594 | 121.8704 | -27.1912 | 94.4962 | -0.013122 | 0.014905 | 0.067986 | 0.0075581 | 0.066584 | -0.00047854 | 0.00026484 | -0.011673 | -0.0051953 | 0.063497 | 0.064536 | 0.00084166 | -0.0079062 | 94.9081 | -26.738 | 0.66834 | -26.7517 | 94.9768 | -26.6556 | -26.6785 | -27.063 | 0.027466 | -27.1225 | 94.9265 | 94.9951 | -26.6373 | -26.7059 | 0.53558 | 0.51269 | 0.48065 | 0.45319 | 0.43945 | -0.073242 | 0.41199 | 0.55389 | 0.48523 | 0.4303 | 0.12817 | 0.068664 | -0.41656 | 0.49896 | 122.168 | 122.0993 | 27.8595 | -121.1746 | 122.1176 | 122.1863 | 27.2186 | -121.2021
282.5938 | 121.8109 | -26.8341 | 94.9356 | -0.0054933 | 0.012341 | 0.066063 | 0.00072207 | 0.065516 | -5.1338e-05 | -0.0012306 | -0.0040437 | -0.0045545 | 0.062002 | 0.064108 | 0.0036189 | -0.0081198 | 94.8761 | -26.8387 | 0.64087 | -26.8799 | 94.8303 | -26.7609 | -26.7975 | -27.1271 | 0.064087 | -27.1591 | 94.6793 | 94.7662 | -26.7975 | -26.8707 | 0.073242 | 0.036621 | -0.10529 | -0.004578 | -0.045777 | -0.082398 | -0.059509 | 0.036621 | -0.036622 | -0.25635 | -0.29297 | -0.32501 | -0.28839 | -0.16937 | 121.6644 | 121.7102 | 27.475 | -121.7331 | 121.5134 | 121.6003 | 26.8982 | -121.8063
284.3281 | 121.7651 | -26.9348 | 94.7983 | -0.020752 | 0.014477 | 0.066704 | 0.0022175 | 0.063166 | 0.0057165 | -0.0018714 | 0.0035858 | -0.0026319 | 0.061361 | 0.063681 | 0.0076777 | -0.006838 | 94.5694 | -27.1591 | 0.54932 | -27.182 | 94.6793 | -27.0218 | -27.0401 | -27.2278 | 0.14648 | -27.3376 | 94.7296 | 94.7891 | -26.8478 | -26.9669 | -0.086976 | -0.10529 | -0.11902 | -0.22431 | -0.24719 | -0.14191 | -0.22888 | 0.086975 | -0.032044 | -0.068665 | -0.29297 | -0.40283 | -0.37079 | -0.009155 | 121.6141 | 121.5042 | 27.4841 | -121.8384 | 121.6644 | 121.7239 | 27.0813 | -121.7651
286.0625 | 121.7926 | -26.8295 | 94.9722 | -0.020752 | 0.013196 | 0.067558 | 0.0026447 | 0.065302 | 0.0014441 | -0.00080316 | -0.0040437 | -0.0022045 | 0.061361 | 0.063681 | 0.0055415 | -0.0079062 | 94.8166 | -26.9348 | 0.54932 | -26.9394 | 94.9173 | -26.7929 | -26.7929 | -27.1271 | 0.018311 | -27.2049 | 94.8624 | 94.931 | -26.7151 | -26.8158 | 0.036621 | 0.036621 | -0.054932 | -0.10528 | -0.10986 | -0.14648 | -0.15564 | 0.11444 | 0.013733 | -0.10986 | -0.29755 | -0.37537 | -0.3891 | -0.041199 | 121.7468 | 121.6461 | 27.3788 | -121.7651 | 121.6919 | 121.7606 | 26.8478 | -121.788
287.7969 | 121.7514 | -26.6098 | 95.1462 | -0.013122 | 0.013196 | 0.067558 | 0.0056355 | 0.064234 | 0.0012305 | 0.00069204 | -0.011673 | -0.0043409 | 0.061575 | 0.063895 | 0.0049005 | -0.0072652 | 94.9997 | -26.738 | 0.55389 | -26.7426 | 95.1233 | -26.5503 | -26.5732 | -26.9165 | 0.009155 | -27.0538 | 95.0912 | 95.1141 | -26.5228 | -26.6464 | 0.059509 | 0.036621 | -0.022888 | -0.12817 | -0.13275 | -0.16937 | -0.14648 | 0.086975 | -0.036621 | -0.054931 | -0.3067 | -0.44403 | -0.40741 | -0.032043 | 121.7331 | 121.6095 | 27.1637 | -121.7194 | 121.701 | 121.7239 | 26.619 | -121.7926
289.5312 | 121.7606 | -26.7105 | 95.0821 | -0.0054933 | 0.014905 | 0.067558 | 0.0011493 | 0.063807 | 0.0020849 | 0.00069204 | -0.011673 | -0.0034863 | 0.064138 | 0.064108 | 0.0070367 | -0.0076926 | 94.9585 | -26.77 | 0.56305 | -26.8066 | 95.018 | -26.6647 | -26.6647 | -27.0035 | 0.013733 | -27.0905 | 94.9493 | 95.0317 | -26.6418 | -26.7471 | 0.045776 | 0.045776 | -0.064087 | -0.05951 | -0.096131 | -0.14191 | -0.1236 | 0.068664 | -0.036621 | -0.13275 | -0.29297 | -0.37994 | -0.34332 | -0.050354 | 121.7285 | 121.669 | 27.2736 | -121.7468 | 121.6599 | 121.7422 | 26.7242 | -121.8292
291.2031 | 121.8063 | -26.6602 | 95.0638 | -0.0054933 | 0.013196 | 0.068199 | 0.0022175 | 0.064021 | 0.00037606 | -0.0040076 | -0.011673 | -0.0049817 | 0.063497 | 0.06304 | 0.0061823 | -0.0055564 | 94.9539 | -26.7654 | 0.62714 | -26.8158 | 94.9585 | -26.6922 | -26.7014 | -27.0126 | 0.10986 | -27.0905 | 94.931 | 94.9768 | -26.6281 | -26.738 | -0.032044 | -0.041199 | -0.10529 | -0.10529 | -0.15564 | -0.11444 | -0.10986 | 0.032043 | -0.07782 | -0.13275 | -0.35248 | -0.4303 | -0.35248 | -0.086975 | 121.6187 | 121.6141 | 27.2873 | -121.7651 | 121.5912 | 121.637 | 26.77 | -121.8018
292.9375 | 121.8842 | -26.4038 | 95.3064 | -0.013122 | 0.013409 | 0.066917 | 0.0045673 | 0.064234 | -0.0043237 | -0.0014442 | -0.0040437 | -0.0081861 | 0.063284 | 0.062827 | 0.00041446 | -0.0044882 | 95.0821 | -26.5961 | 0.45776 | -26.5961 | 95.0912 | -26.5045 | -26.532 | -26.825 | -0.013733 | -26.7014 | 95.0729 | 95.2194 | -26.3763 | -26.4313 | -0.10071 | -0.12817 | -0.21515 | -0.19226 | -0.19226 | -0.064087 | -0.2243 | 0.027466 | -0.027465 | -0.23346 | -0.42114 | -0.29755 | -0.27008 | -0.086975 | 121.4951 | 121.4859 | 26.8616 | -121.8384 | 121.4767 | 121.6232 | 26.3901 | -121.7377
294.6094 | 121.8979 | -21.373 | 100.2914 | -0.013122 | 0.015759 | 0.066063 | 0.0073443 | 0.066157 | 0.00058966 | -0.003794 | -0.026932 | -0.0019909 | 0.065634 | 0.064322 | 0.0019099 | -0.0087606 | 100.1083 | -21.5973 | 0.7782 | -21.5424 | 100.2777 | -21.4325 | -21.46 | -21.7163 | 0.13733 | -21.7987 | 100.2457 | 100.3189 | -21.3364 | -21.4508 | -0.059509 | -0.086975 | -0.013733 | -0.2243 | -0.16937 | -0.082397 | -0.18311 | 0.036621 | -0.07782 | -0.045776 | -0.34332 | -0.42572 | -0.3479 | 0.027466 | 121.6507 | 121.4813 | 22.1512 | -121.7514 | 121.6187 | 121.6919 | 21.5103 | -121.7422
296.3438 | 121.8842 | -20.9381 | 100.7492 | -0.0054933 | 0.013196 | 0.068626 | 0.0073443 | 0.064875 | -0.0056055 | -0.0044348 | 0.0035858 | -0.0071179 | 0.062002 | 0.064108 | 0.0010553 | -0.0081198 | 100.7172 | -20.9976 | 0.98877 | -21.0251 | 100.6302 | -20.9381 | -20.993 | -21.3364 | 0.25177 | -21.2814 | 100.4974 | 100.5936 | -20.9839 | -21.0571 | 0 | -0.054932 | -0.11902 | -0.05951 | -0.086975 | -0.032043 | -0.032044 | -0.045777 | -0.11902 | -0.25177 | -0.39825 | -0.34332 | -0.2243 | -0.15564 | 121.5683 | 121.6553 | 21.9269 | -121.7422 | 121.4355 | 121.5317 | 21.1899 | -121.8063
298.0156 | 89.4928 | -0.15106 | 69.1818 | -0.0054933 | 0.012127 | 0.066704 | 0.00093567 | 0.065089 | -0.00069214 | -0.0029394 | -0.011673 | -0.0049817 | 0.061148 | 0.066031 | 0.0042597 | -0.0076926 | 101.0513 | -20.6909 | 1.3138 | -20.6818 | 101.001 | -20.5399 | -20.5902 | -20.787 | 0.49896 | -20.9015 | 100.9827 | 101.0422 | -20.5124 | -20.6223 | -20.3888 | -20.4391 | 31.8192 | -20.5399 | -20.5307 | -0.091553 | 31.8695 | -20.3613 | -20.4712 | 31.8008 | -20.636 | -20.7504 | -0.27924 | 31.8604 | 101.152 | 101.2024 | 1.4648 | -89.772 | 101.1337 | 101.1932 | 0.65002 | -89.8041
299.7656 | 121.9162 | -20.2515 | 97.9935 | -0.013122 | 0.014264 | 0.067345 | 0.0032855 | 0.064875 | 0.00080326 | -0.0016578 | -0.0040437 | -0.0049817 | 0.062002 | 0.06304 | 0.0044733 | -0.0066244 | 101.4038 | -20.3064 | 0.97961 | -20.2698 | 101.5091 | -20.1141 | -20.1416 | -20.3705 | 0.15106 | -20.4575 | 101.4908 | 101.5503 | -20.0317 | -20.1416 | 0.13733 | 0.10986 | 3.5156 | -0.054931 | -0.01831 | -0.12817 | 3.4103 | 0.21973 | 0.10986 | 3.4973 | -0.11902 | -0.20599 | -0.31586 | 3.5568 | 121.7606 | 121.6553 | 21.2311 | -118.1351 | 121.7422 | 121.8018 | 20.4025 | -118.1351
301.5 | 121.9711 | -118.2312 | 3.3875 | -0.013122 | 0.017895 | 0.067772 | 0.0039265 | 0.064662 | 0.0040077 | 0.00090584 | -0.0040437 | -0.0026319 | 0.063925 | 0.066672 | 0.0046869 | -0.0049154 | 3.3417 | -117.691 | -2.9388 | -118.1122 | 3.3966 | -118.483 | -118.2953 | -118.7576 | -0.091553 | -118.4738 | 3.3142 | 3.3279 | -118.3228 | -118.4784 | -0.25177 | -0.064087 | 0.009155 | 0.54016 | 0.11902 | 0.1831 | -0.045776 | -0.091553 | -0.24719 | -0.073242 | -0.52643 | -0.24262 | 0.004578 | -0.059509 | 121.6278 | 121.5729 | 115.2924 | -121.6827 | 121.5454 | 121.5591 | 118.1396 | -121.8658
303.2344 | 121.9116 | -119.6594 | 1.9913 | -0.013122 | 0.012127 | 0.068413 | 0.0069171 | 0.066371 | -0.0060327 | -0.0035804 | 0.0035858 | -0.0066907 | 0.062856 | 0.064108 | -0.0012945 | -0.0064108 | 1.8951 | -119.0598 | -3.1586 | -119.4901 | 1.9867 | -119.8196 | -119.6457 | -120.1813 | -0.082397 | -119.838 | 1.8997 | 1.9592 | -119.6594 | -119.87 | -0.16022 | 0.013733 | -0.004578 | 0.59967 | 0.16937 | 0.15564 | -0.09613 | 0 | -0.21057 | -0.091553 | -0.52185 | -0.17853 | 0.032043 | -0.032043 | 121.6461 | 121.5546 | 116.5009 | -121.637 | 121.5591 | 121.6187 | 119.577 | -121.8613
304.9688 | 121.9116 | -119.6777 | 2.0279 | -0.0054933 | 0.012555 | 0.068199 | 0.0037127 | 0.066584 | 0.0016577 | -0.0014442 | -0.0040437 | -0.0032727 | 0.061148 | 0.064322 | 0.0070367 | -0.005129 | 1.9363 | -119.0414 | -3.186 | -119.4946 | 1.9913 | -119.8059 | -119.6503 | -120.0989 | -0.036621 | -119.8151 | 1.8997 | 1.9363 | -119.632 | -119.8013 | -0.12817 | 0.027465 | -0.036621 | 0.63629 | 0.1831 | 0.15564 | -0.091553 | 0.045776 | -0.1236 | -0.12817 | -0.42114 | -0.13733 | -0.013732 | -0.091553 | 121.669 | 121.6141 | 116.4917 | -121.6782 | 121.5775 | 121.6141 | 119.6411 | -121.8292
306.6406 | 121.8109 | -119.7372 | 1.9958 | -0.0054933 | 0.0080686 | 0.066277 | 0.0026447 | 0.065943 | -0.0036829 | -0.0031532 | -0.0040437 | -0.0069043 | 0.061148 | 0.064963 | 0.0019099 | -0.006838 | 1.918 | -119.0323 | -3.2135 | -119.5084 | 1.9592 | -119.8151 | -119.6411 | -120.1904 | -0.050354 | -119.8517 | 1.8997 | 1.9226 | -119.5999 | -119.8517 | -0.077819 | 0.096131 | -0.036621 | 0.70496 | 0.22888 | 0.13275 | -0.07782 | 0.13733 | -0.11444 | -0.096131 | -0.45319 | -0.11444 | 0 | -0.073243 | 121.6965 | 121.6553 | 116.5237 | -121.637 | 121.637 | 121.6599 | 119.6869 | -121.8475
308.375 | 121.8063 | -119.7693 | 1.9409 | 0.0021362 | 0.0076414 | 0.068413 | 0.0039265 | 0.066157 | -0.0036829 | -0.0044348 | -0.0040437 | -0.0056225 | 0.061575 | 0.065604 | 0.00084166 | -0.0064108 | 1.8448 | -119.0964 | -3.2593 | -119.5541 | 1.9135 | -119.8059 | -119.6732 | -120.2316 | -0.045776 | -119.8746 | 1.8173 | 1.8539 | -119.6411 | -119.8975 | -0.036621 | 0.09613 | -0.027466 | 0.67291 | 0.21515 | 0.11902 | -0.09613 | 0.12817 | -0.12817 | -0.1236 | -0.46234 | -0.10529 | 0.022888 | -0.086975 | 121.6827 | 121.6141 | 116.51 | -121.6141 | 121.5866 | 121.6232 | 119.7235 | -121.8384
310.0469 | 121.8796 | -119.8242 | 1.8539 | -0.013122 | 0.014905 | 0.068199 | 0.0088397 | 0.066371 | -0.0015465 | -0.002085 | -0.011673 | -0.0060497 | 0.061788 | 0.067099 | 0.0019099 | -0.0064108 | 1.8311 | -119.0826 | -3.2043 | -119.5587 | 1.8219 | -119.8975 | -119.7281 | -120.2316 | 0.064087 | -119.8837 | 1.7395 | 1.7761 | -119.7235 | -119.9158 | -0.073242 | 0.096131 | -0.032044 | 0.74158 | 0.2655 | 0.16937 | -0.022888 | 0.10071 | -0.091552 | -0.11444 | -0.40741 | -0.059509 | 0.032043 | -0.07782 | 121.6461 | 121.6553 | 116.6199 | -121.582 | 121.5637 | 121.6003 | 119.8883 | -121.7697
311.7812 | 121.8704 | -119.8608 | 1.8173 | -0.013122 | 0.012341 | 0.068413 | 0.0058491 | 0.066371 | 0.00016226 | -0.0029394 | -0.0040437 | -0.0071179 | 0.063711 | 0.066031 | 0.00084166 | -0.0066244 | 1.8127 | -119.1193 | -3.2135 | -119.5862 | 1.8036 | -119.9341 | -119.7601 | -120.2362 | 0.07782 | -119.9295 | 1.7258 | 1.7578 | -119.7281 | -119.9707 | -0.073242 | 0.10071 | -0.013733 | 0.74158 | 0.27466 | 0.17395 | -0.004578 | 0.13275 | -0.10986 | -0.091553 | -0.37537 | -0.068664 | 0.041199 | -0.05951 | 121.6644 | 121.6736 | 116.6473 | -121.5775 | 121.5866 | 121.6187 | 119.9387 | -121.788
313.5156 | 121.7651 | -119.7556 | 1.9913 | -0.0054933 | 0.014905 | 0.068199 | 0.0028583 | 0.066371 | -0.0019739 | -0.0010168 | -0.0040437 | -0.0066907 | 0.063925 | 0.066245 | 0.0014825 | -0.007479 | 1.9318 | -119.0048 | -3.2684 | -119.4717 | 1.9547 | -119.7647 | -119.6136 | -120.1401 | -0.027466 | -119.8151 | 1.8814 | 1.9043 | -119.6045 | -119.838 | -0.009155 | 0.14191 | -0.036621 | 0.75073 | 0.28381 | 0.14191 | -0.059509 | 0.15106 | -0.082398 | -0.10986 | -0.38452 | -0.059509 | 0.022889 | -0.086975 | 121.7102 | 121.6873 | 116.4871 | -121.6049 | 121.637 | 121.6599 | 119.7281 | -121.8292
315.2031 | 121.843 | -119.3893 | 2.2659 | -0.0054933 | 0.0164 | 0.066917 | 0.0075581 | 0.067439 | 0.00080326 | -0.0027258 | -0.019302 | -0.0019909 | 0.062856 | 0.068167 | 0.0034051 | -0.006838 | 2.1515 | -118.7759 | -3.3279 | -119.2245 | 2.2751 | -119.4946 | -119.3253 | -119.9066 | -0.036621 | -119.5953 | 2.2293 | 2.2339 | -119.3481 | -119.5312 | -0.10529 | 0.064087 | 0.009155 | 0.6134 | 0.16479 | 0.10071 | -0.11444 | 0.041198 | -0.14191 | -0.036621 | -0.51727 | -0.20599 | -0.064087 | -0.032043 | 121.6644 | 121.5408 | 116.0614 | -121.5912 | 121.6187 | 121.6232 | 119.3527 | -121.7972
316.9531 | 121.756 | -119.1834 | 2.5406 | -0.013122 | 0.014264 | 0.067345 | 0.00050847 | 0.066798 | 0.0012305 | -0.002085 | -0.0040437 | -0.0051953 | 0.062216 | 0.063895 | 0.0053279 | -0.0096152 | 2.5085 | -118.4326 | -3.2455 | -118.9041 | 2.4673 | -119.1925 | -119.0689 | -119.5404 | 0.032043 | -119.2291 | 2.3941 | 2.4399 | -119.0689 | -119.2886 | -0.009155 | 0.11444 | -0.073242 | 0.75073 | 0.27924 | 0.16479 | -0.032043 | 0.11444 | -0.10528 | -0.14648 | -0.35706 | -0.045776 | 0.059509 | -0.10071 | 121.6507 | 121.6919 | 115.9378 | -121.6095 | 121.5775 | 121.6232 | 119.2154 | -121.8292
318.625 | 121.7468 | -118.8766 | 2.8381 | -0.013122 | 0.0097776 | 0.067345 | -0.00013253 | 0.065089 | -0.0041101 | -0.0033668 | 0.0035858 | -0.0077587 | 0.058798 | 0.065817 | 0.0044733 | -0.0064108 | 2.71 | -118.2358 | -3.3051 | -118.6981 | 2.7557 | -118.9636 | -118.7759 | -119.371 | -0.045776 | -119.0506 | 2.6367 | 2.6779 | -118.808 | -119.014 | -0.086975 | 0.10071 | -0.082398 | 0.64087 | 0.17853 | 0.07782 | -0.12817 | 0.068665 | -0.13733 | -0.20142 | -0.49438 | -0.17395 | -0.036621 | -0.16022 | 121.6324 | 121.5866 | 115.5716 | -121.6141 | 121.5134 | 121.5546 | 118.8309 | -121.8521
320.3594 | 121.8155 | -119.4351 | 2.2247 | -0.013122 | 0.0099912 | 0.069695 | 0.0045673 | 0.06338 | -0.0024011 | -0.0040076 | 0.0035858 | -0.0051953 | 0.061788 | 0.064749 | 0.0029779 | -0.0066244 | 2.1561 | -118.7622 | -3.3234 | -119.2017 | 2.2064 | -119.4946 | -119.3436 | -119.8883 | 0.013733 | -119.5496 | 2.1194 | 2.1652 | -119.3207 | -119.5633 | -0.059509 | 0.091553 | -0.01831 | 0.67291 | 0.23346 | 0.14191 | -0.068664 | 0.11444 | -0.12817 | -0.10528 | -0.45319 | -0.11444 | 0.013732 | -0.059509 | 121.6415 | 121.5912 | 116.1118 | -121.5683 | 121.5546 | 121.6003 | 119.4489 | -121.788
322.0312 | 121.8658 | -119.5679 | 2.0462 | -0.013122 | 0.012127 | 0.066917 | 0.0064899 | 0.067652 | -0.0017603 | -0.0035804 | -0.0040437 | -0.0039135 | 0.062429 | 0.06539 | 0.0012689 | -0.006838 | 2.0966 | -118.8171 | -3.2776 | -119.3344 | 2.0599 | -119.632 | -119.4717 | -119.9799 | 0.073242 | -119.6411 | 1.9592 | 2.005 | -119.4534 | -119.6686 | -0.064087 | 0.09613 | 0.013733 | 0.75073 | 0.23346 | 0.13733 | 0.050354 | 0.11444 | -0.10071 | -0.086975 | -0.41199 | -0.073242 | 0.027466 | -0.041199 | 121.6278 | 121.6644 | 116.2903 | -121.5179 | 121.5271 | 121.5729 | 119.6411 | -121.7148
323.75 | 121.5591 | -118.4921 | 3.0212 | -0.020752 | 0.014477 | 0.06649 | 0.0030719 | 0.065089 | 0.0061439 | -0.0014442 | -0.011673 | -0.0022045 | 0.06307 | 0.065817 | 0.0063959 | -0.007479 | 2.8656 | -117.9016 | -3.4332 | -118.2861 | 2.9709 | -118.5516 | -118.3823 | -118.9545 | -0.24719 | -118.6981 | 2.8839 | 2.9205 | -118.3594 | -118.5654 | -0.05951 | 0.10986 | -0.050354 | 0.59051 | 0.20599 | 0.09613 | -0.15564 | 0.13275 | -0.073243 | -0.13733 | -0.46234 | -0.20599 | -0.13275 | -0.10071 | 121.463 | 121.3577 | 115.0589 | -121.4035 | 121.376 | 121.4127 | 118.2449 | -121.5866
325.4844 | 121.3486 | -118.602 | 3.1128 | -0.013122 | 0.015332 | 0.063713 | 0.0034991 | 0.069148 | 0.0029395 | -0.00016236 | -0.011673 | -0.0022045 | 0.063711 | 0.067099 | 0.0059687 | -0.0066244 | 2.9388 | -118.0252 | -3.3508 | -118.4097 | 3.0762 | -118.6569 | -118.5013 | -119.0872 | -0.082397 | -118.8217 | 2.9846 | 3.0304 | -118.5013 | -118.7302 | -0.054931 | 0.10071 | -0.036621 | 0.57678 | 0.19226 | 0.091553 | -0.17395 | 0.10071 | -0.12817 | -0.12817 | -0.48523 | -0.21973 | -0.091552 | -0.082397 | 121.6782 | 121.5408 | 115.2512 | -121.6141 | 121.5866 | 121.6324 | 118.5196 | -121.843
327.2188 | 121.8338 | -118.6569 | 2.9846 | -0.0054933 | 0.017041 | 0.068199 | 0.0069171 | 0.065302 | 0.0014441 | -0.0010168 | -0.0040437 | -0.0045545 | 0.06542 | 0.066031 | 0.0019099 | -0.0083334 | 2.8427 | -118.0893 | -3.3508 | -118.5333 | 2.9755 | -118.7897 | -118.6111 | -119.1971 | -0.041199 | -118.8858 | 2.9022 | 2.916 | -118.6249 | -118.8217 | -0.13275 | 0.045776 | -0.009155 | 0.56763 | 0.1236 | 0.07782 | -0.14191 | 0.032043 | -0.16479 | -0.082397 | -0.54016 | -0.22888 | -0.064087 | -0.068664 | 121.6324 | 121.4996 | 115.3061 | -121.5958 | 121.5591 | 121.5729 | 118.6157 | -121.8063
328.9531 | 121.8384 | -118.8309 | 2.7878 | -0.013122 | 0.011273 | 0.06649 | 0.0067035 | 0.067011 | -0.0036829 | -0.0014442 | -0.0040437 | -0.0086133 | 0.063497 | 0.063895 | 0.00041446 | -0.005129 | 2.71 | -118.1625 | -3.2867 | -118.6203 | 2.7466 | -118.895 | -118.7714 | -119.3253 | 0.045776 | -118.9362 | 2.6733 | 2.71 | -118.7714 | -118.9819 | -0.064086 | 0.05951 | -0.041199 | 0.66833 | 0.21057 | 0.15106 | -0.07782 | 0.05951 | -0.15106 | -0.11444 | -0.49438 | -0.10528 | 0.045777 | -0.07782 | 121.5775 | 121.5408 | 115.5441 | -121.5591 | 121.5042 | 121.5408 | 118.8766 | -121.7697
330.7188 | 121.7789 | -118.808 | 2.8748 | 0.0021362 | 0.011059 | 0.065208 | 0.0041401 | 0.064021 | 0.0020849 | -0.0018714 | 0.0035858 | -0.0054089 | 0.061575 | 0.064108 | 0.0061823 | -0.0076926 | 2.7924 | -118.1305 | -3.3234 | -118.5699 | 2.8336 | -118.8583 | -118.7073 | -119.1971 | 0.022888 | -118.9041 | 2.7695 | 2.7878 | -118.6844 | -118.8904 | -0.050354 | 0.10071 | -0.041199 | 0.67749 | 0.23804 | 0.13733 | -0.082398 | 0.1236 | -0.082398 | -0.10529 | -0.3891 | -0.096131 | -0.013733 | -0.086975 | 121.6415 | 121.6003 | 115.4846 | -121.582 | 121.5775 | 121.5958 | 118.8309 | -121.7651
332.3906 | 121.7056 | -119.1055 | 2.5681 | -0.013122 | 0.0074278 | 0.06884 | 0.0024311 | 0.06808 | -0.0017603 | -0.0025122 | -0.0040437 | -0.0079725 | 0.059866 | 0.064322 | 0.0046869 | -0.005129 | 2.5131 | -118.3731 | -3.3142 | -118.8629 | 2.5177 | -119.1696 | -118.9957 | -119.5541 | 0.022888 | -119.22 | 2.4353 | 2.4857 | -119.014 | -119.2017 | -0.064087 | 0.10986 | -0.050354 | 0.73242 | 0.24262 | 0.13275 | -0.054931 | 0.091553 | -0.09613 | -0.13275 | -0.44861 | -0.11444 | -0.018311 | -0.082397 | 121.6232 | 121.6187 | 115.7913 | -121.5637 | 121.5408 | 121.5912 | 119.1284 | -121.7697
334.0625 | 121.6965 | -118.721 | 2.9709 | -0.013122 | 0.011059 | 0.069267 | 0.00029487 | 0.06573 | 0.00037606 | -0.0016578 | -0.011673 | -0.0073315 | 0.06072 | 0.066458 | 0.0038325 | -0.0049154 | 2.9434 | -117.9794 | -3.2822 | -118.4692 | 2.9297 | -118.7531 | -118.5883 | -119.1467 | 0.018311 | -118.8171 | 2.8656 | 2.8748 | -118.5837 | -118.8034 | -0.032044 | 0.13275 | -0.041199 | 0.74158 | 0.25177 | 0.11902 | -0.027466 | 0.13733 | -0.082398 | -0.10529 | -0.42572 | -0.096131 | -0.013733 | -0.09613 | 121.6507 | 121.6644 | 115.4388 | -121.5591 | 121.5866 | 121.5958 | 118.7393 | -121.7743
335.7969 | 121.7285 | -119.1879 | 2.5269 | -0.0054933 | 0.0082822 | 0.068199 | 0.0017901 | 0.067225 | -0.0015465 | -0.0040076 | -0.0040437 | -0.0062635 | 0.058798 | 0.064749 | 0.0038325 | -0.0047018 | 2.4719 | -118.4647 | -3.3325 | -118.9453 | 2.4445 | -119.1971 | -119.0598 | -119.6136 | 0.004578 | -119.2657 | 2.4124 | 2.4261 | -119.0689 | -119.2703 | -0.009156 | 0.12817 | -0.082397 | 0.72327 | 0.24262 | 0.11444 | -0.054931 | 0.11902 | -0.082398 | -0.11444 | -0.42572 | -0.07782 | 0.004578 | -0.10071 | 121.6324 | 121.6599 | 115.8554 | -121.5866 | 121.6003 | 121.6141 | 119.1925 | -121.7972
337.5312 | 121.7377 | -119.3298 | 2.4033 | 0.0021362 | 0.015332 | 0.067345 | 0.0026447 | 0.065516 | 0.0061439 | -0.002085 | -0.011673 | -0.0028455 | 0.063497 | 0.065176 | 0.0044733 | -0.0070516 | 2.2202 | -118.7576 | -3.4424 | -119.1422 | 2.3712 | -119.3939 | -119.2291 | -119.8196 | -0.10529 | -119.5358 | 2.2934 | 2.3209 | -119.252 | -119.458 | -0.064087 | 0.10071 | -0.032043 | 0.57221 | 0.18768 | 0.086975 | -0.1831 | 0.07782 | -0.12817 | -0.10986 | -0.48981 | -0.20599 | -0.07782 | -0.082397 | 121.7011 | 121.55 | 115.8875 | -121.6324 | 121.6232 | 121.6507 | 119.2245 | -121.8613
339.2656 | 121.8155 | -118.8171 | 2.8107 | -0.0054933 | 0.014477 | 0.067345 | 0.0090533 | 0.067652 | 0.00016226 | 0.00069204 | -0.0040437 | -0.0062635 | 0.066061 | 0.064963 | -0.00022634 | -0.0042746 | 2.6871 | -118.2358 | -3.3691 | -118.6844 | 2.8198 | -118.9453 | -118.7714 | -119.3756 | -0.032043 | -119.0414 | 2.7512 | 2.774 | -118.8034 | -119.0002 | -0.12817 | 0.045777 | 0.009155 | 0.58136 | 0.13275 | 0.086975 | -0.1236 | 0.013733 | -0.1831 | -0.059509 | -0.55847 | -0.2243 | -0.041199 | -0.036621 | 121.637 | 121.5042 | 115.448 | -121.582 | 121.5683 | 121.5912 | 118.7851 | -121.8109
341 | 121.8338 | -119.2612 | 2.3621 | -0.013122 | 0.016186 | 0.065208 | 0.0062763 | 0.064662 | 0.0052893 | 0.00069204 | -0.011673 | -0.0036999 | 0.063284 | 0.067099 | 0.0053279 | -0.0087606 | 2.3071 | -118.634 | -3.3508 | -119.0918 | 2.3575 | -119.3665 | -119.1925 | -119.7372 | 0.032043 | -119.4397 | 2.2797 | 2.3209 | -119.2245 | -119.4397 | -0.10529 | 0.068664 | -0.004578 | 0.62714 | 0.16937 | 0.10071 | -0.054932 | 0.036621 | -0.17853 | -0.082398 | -0.47608 | -0.17853 | 0 | -0.041199 | 121.6187 | 121.5683 | 115.9103 | -121.5546 | 121.5408 | 121.582 | 119.2932 | -121.8018
342.6719 | 121.7514 | -119.3436 | 2.3438 | -0.0054933 | 0.010632 | 0.067131 | 0.0024311 | 0.065516 | -0.00026494 | 0.00047844 | -0.0040437 | -0.0086133 | 0.062002 | 0.065604 | 0.0046869 | -0.0061972 | 2.2934 | -118.5928 | -3.3325 | -119.0918 | 2.2797 | -119.3893 | -119.2383 | -119.7372 | 0.041199 | -119.4077 | 2.211 | 2.2476 | -119.2383 | -119.4351 | -0.045776 | 0.10529 | -0.064087 | 0.75073 | 0.25177 | 0.14648 | -0.050354 | 0.10529 | -0.091553 | -0.13275 | -0.39368 | -0.064087 | 0.027466 | -0.09613 | 121.6232 | 121.637 | 116.011 | -121.582 | 121.5546 | 121.5912 | 119.3848 | -121.7789
344.4062 | 121.7422 | -119.252 | 2.449 | -0.013122 | 0.0097776 | 0.069054 | 0.0067035 | 0.062739 | -0.0026147 | -0.0016578 | -0.011673 | -0.0077587 | 0.06307 | 0.066031 | 0.0016963 | -0.0055564 | 2.3209 | -118.5654 | -3.4149 | -119.046 | 2.3895 | -119.3161 | -119.1605 | -119.7281 | -0.009155 | -119.3802 | 2.3163 | 2.3392 | -119.1467 | -119.3481 | -0.064087 | 0.091553 | -0.05951 | 0.68664 | 0.20599 | 0.11444 | -0.12817 | 0.10529 | -0.096131 | -0.13275 | -0.47607 | -0.12817 | -0.032043 | -0.10986 | 121.6415 | 121.5729 | 115.8371 | -121.6095 | 121.5683 | 121.5912 | 119.2429 | -121.7972
346.1562 | 121.7331 | -119.1055 | 2.5955 | 0.0021362 | 0.011914 | 0.06884 | 0.0056355 | 0.066584 | -0.0013329 | -0.0031532 | -0.0040437 | -0.0045545 | 0.059225 | 0.064536 | 0.0036189 | -0.005129 | 2.5269 | -118.4052 | -3.3783 | -118.8904 | 2.5497 | -119.1467 | -118.9728 | -119.5633 | 0.009155 | -119.1971 | 2.449 | 2.4948 | -119.0002 | -119.2062 | -0.041199 | 0.13275 | -0.045776 | 0.70038 | 0.21515 | 0.082397 | -0.068665 | 0.10529 | -0.10071 | -0.14648 | -0.45776 | -0.091553 | 0.009155 | -0.10071 | 121.6553 | 121.6324 | 115.7272 | -121.5683 | 121.5546 | 121.6003 | 119.1147 | -121.8018
347.8906 | 121.7834 | -119.133 | 2.5772 | -0.013122 | 0.011487 | 0.064995 | 0.0013629 | 0.066157 | 0.0016577 | -0.00080316 | -0.011673 | -0.0026319 | 0.059866 | 0.064963 | 0.0070367 | -0.0098288 | 2.4399 | -118.5013 | -3.4149 | -118.9407 | 2.5223 | -119.2154 | -119.0689 | -119.5679 | 0.013733 | -119.2566 | 2.4216 | 2.4536 | -119.0506 | -119.2245 | -0.082397 | 0.064087 | -0.054931 | 0.63171 | 0.19226 | 0.12817 | -0.13733 | 0.082398 | -0.091552 | -0.15564 | -0.43487 | -0.1236 | -0.032044 | -0.1236 | 121.6553 | 121.5729 | 115.7181 | -121.6461 | 121.5546 | 121.5866 | 119.1467 | -121.8018
349.5625 | 121.8475 | -119.2062 | 2.4078 | -0.013122 | 0.011059 | 0.070549 | 0.0028583 | 0.066157 | -0.0034691 | -0.0025122 | -0.019302 | -0.0073315 | 0.060293 | 0.062827 | 0.0027643 | -0.0066244 | 2.3346 | -118.5608 | -3.4012 | -119.0277 | 2.4124 | -119.2932 | -119.133 | -119.7098 | 0.027466 | -119.3298 | 2.298 | 2.3575 | -119.1422 | -119.3527 | -0.086975 | 0.073242 | 0.004578 | 0.64545 | 0.17853 | 0.10529 | -0.073242 | 0.064087 | -0.14648 | -0.10986 | -0.50354 | -0.1236 | 0.022888 | -0.050354 | 121.6187 | 121.5408 | 115.8051 | -121.5408 | 121.5042 | 121.5637 | 119.2337 | -121.7606
351.2969 | 121.8658 | -119.2062 | 2.4445 | -0.013122 | 0.010846 | 0.06884 | 0.0052081 | 0.064234 | -0.0047509 | -0.0042212 | -0.011673 | -0.0069043 | 0.06307 | 0.065817 | 0.0023371 | -0.0072652 | 2.3666 | -118.5562 | -3.4058 | -119.014 | 2.4078 | -119.2841 | -119.133 | -119.696 | 0.054932 | -119.3253 | 2.3117 | 2.3621 | -119.1193 | -119.3344 | -0.07782 | 0.073242 | -0.036621 | 0.65002 | 0.19226 | 0.11902 | -0.07782 | 0.086975 | -0.12817 | -0.13275 | -0.48981 | -0.11902 | 0.009156 | -0.082397 | 121.6141 | 121.5729 | 115.8005 | -121.5775 | 121.5179 | 121.5683 | 119.2612 | -121.7789
353.0469 | 121.7422 | -119.0964 | 2.5772 | 0.0097657 | 0.010846 | 0.068626 | 0.0017901 | 0.067439 | 0.0016577 | -0.002085 | 0.0035858 | -0.0047681 | 0.058798 | 0.064749 | 0.0051141 | -0.0094016 | 2.5497 | -118.3868 | -3.3371 | -118.8721 | 2.5085 | -119.1467 | -118.9819 | -119.5038 | 0.036621 | -119.1834 | 2.4353 | 2.4536 | -118.9957 | -119.1971 | -0.050354 | 0.11444 | -0.068664 | 0.70953 | 0.22431 | 0.10986 | -0.027465 | 0.10071 | -0.10071 | -0.14191 | -0.40741 | -0.086975 | 0.013733 | -0.1236 | 121.6049 | 121.6461 | 115.7593 | -121.5591 | 121.5317 | 121.55 | 119.133 | -121.7743
354.7188 | 121.7331 | -118.7485 | 2.9663 | -0.013122 | 0.011059 | 0.067986 | 0.0011493 | 0.06808 | 0.0010169 | -0.0027258 | -0.011673 | -0.0066907 | 0.060934 | 0.064322 | 0.0053279 | -0.0079062 | 2.9297 | -118.0161 | -3.3279 | -118.4875 | 2.8793 | -118.7622 | -118.6203 | -119.1238 | 0.045776 | -118.8126 | 2.8107 | 2.8519 | -118.6203 | -118.8171 | -0.013733 | 0.12817 | -0.086976 | 0.73242 | 0.26093 | 0.13275 | -0.036622 | 0.12817 | -0.068665 | -0.15564 | -0.37537 | -0.064087 | 0.004578 | -0.11444 | 121.6278 | 121.6782 | 115.4205 | -121.5866 | 121.5591 | 121.6003 | 118.7943 | -121.7834
356.4688 | 121.756 | -118.9362 | 2.774 | -0.013122 | 0.011914 | 0.067345 | 0.0047809 | 0.066157 | -0.00047854 | -0.0018714 | -0.011673 | -0.0060497 | 0.061148 | 0.06539 | 0.0053279 | -0.0079062 | 2.742 | -118.2175 | -3.3737 | -118.6707 | 2.6917 | -118.9499 | -118.8126 | -119.3207 | 0.050354 | -119.0094 | 2.6093 | 2.655 | -118.8217 | -119.0002 | -0.013733 | 0.1236 | -0.082398 | 0.71869 | 0.2655 | 0.14191 | -0.032044 | 0.11444 | -0.064087 | -0.1648 | -0.38452 | -0.073242 | -0.009155 | -0.11902 | 121.6278 | 121.6782 | 115.5624 | -121.5866 | 121.5454 | 121.5912 | 118.9865 | -121.7743
358.1562 | 121.7377 | -118.6981 | 2.9846 | -0.0054933 | 0.010846 | 0.065422 | 0.0041401 | 0.065089 | -0.0013329 | -0.0010168 | -0.011673 | -0.0049817 | 0.062002 | 0.06539 | 0.0036189 | -0.005129 | 2.9251 | -118.0252 | -3.3966 | -118.4921 | 2.948 | -118.7347 | -118.5791 | -119.1559 | -0.018311 | -118.8217 | 2.8885 | 2.9251 | -118.5791 | -118.8034 | -0.036621 | 0.11902 | -0.036621 | 0.67291 | 0.20599 | 0.086976 | -0.059509 | 0.11902 | -0.10529 | -0.09613 | -0.45776 | -0.1236 | -0.01831 | -0.059509 | 121.6461 | 121.6232 | 115.3015 | -121.5637 | 121.5866 | 121.6232 | 118.6798 | -121.788
359.9062 | 121.8475 | -118.5104 | 3.067 | -0.013122 | 0.015545 | 0.069054 | 0.0045673 | 0.066584 | -0.00047854 | -0.0025122 | -0.019302 | -0.0051953 | 0.062643 | 0.064749 | 0.0042597 | -0.0079062 | 2.9938 | -117.9932 | -3.4332 | -118.4097 | 3.1128 | -118.6752 | -118.5059 | -119.0826 | -0.032043 | -118.7805 | 3.035 | 3.0624 | -118.5013 | -118.7027 | -0.16479 | 0.004578 | 0.045776 | 0.51727 | 0.10071 | 0.09613 | -0.073243 | 0.009155 | -0.19226 | -0.032044 | -0.57221 | -0.27008 | -0.07782 | -0.004578 | 121.6232 | 121.5042 | 115.0772 | -121.5729 | 121.5454 | 121.5729 | 118.4784 | -121.7697
361.5781 | 121.8567 | -118.5883 | 3.0167 | -0.013122 | 0.013409 | 0.069054 | 0.0043537 | 0.066584 | -0.0015465 | -0.0018714 | -0.0040437 | -0.0062635 | 0.06307 | 0.066031 | -0.0030035 | -0.0081198 | 3.0304 | -117.8925 | -3.3279 | -118.3868 | 3.0167 | -118.6707 | -118.5104 | -119.0231 | 0.10986 | -118.6661 | 2.8885 | 2.9434 | -118.5196 | -118.7622 | -0.082397 | 0.07782 | 0 | 0.6958 | 0.20142 | 0.1236 | 0.013733 | 0.068665 | -0.17395 | -0.12817 | -0.43488 | -0.07782 | 0.09613 | -0.073243 | 121.6049 | 121.6187 | 115.2603 | -121.5271 | 121.4767 | 121.5317 | 118.6981 | -121.7789
363.25 | 121.8155 | -118.0115 | 3.5843 | -0.0054933 | 0.0084958 | 0.068199 | 0.0017901 | 0.065302 | -0.00047854 | -0.0035804 | -0.0040437 | -0.0069043 | 0.06072 | 0.066672 | 0.0023371 | -0.0053426 | 3.4927 | -117.4438 | -3.4103 | -117.9291 | 3.5156 | -118.1534 | -118.0069 | -118.5654 | -0.050354 | -118.2541 | 3.4332 | 3.4515 | -118.0252 | -118.2129 | -0.14191 | 0.004578 | -0.068665 | 0.56763 | 0.082398 | 0.07782 | -0.091553 | -0.013733 | -0.20142 | -0.15106 | -0.55389 | -0.24261 | -0.041198 | -0.13275 | 121.5271 | 121.5042 | 114.6011 | -121.5912 | 121.4447 | 121.463 | 117.9611 | -121.7972
364.9844 | 121.8063 | -119.3619 | 2.2888 | -0.020752 | 0.010418 | 0.069267 | 0.0024311 | 0.065302 | -0.0024011 | -0.0018714 | -0.019302 | -0.0077587 | 0.061575 | 0.065176 | 0.0040461 | -0.0070516 | 2.2247 | -118.7347 | -3.5431 | -119.2474 | 2.243 | -119.4901 | -119.2749 | -119.838 | -0.013733 | -119.5084 | 2.1973 | 2.2202 | -119.2795 | -119.5038 | -0.12817 | 0.086975 | -0.045776 | 0.62714 | 0.11444 | 0.027465 | -0.064087 | 0.082397 | -0.14191 | -0.091552 | -0.47607 | -0.14648 | -0.004578 | -0.068664 | 121.6049 | 121.5866 | 115.8188 | -121.5637 | 121.5591 | 121.582 | 119.3481 | -121.7926
366.7188 | 121.9025 | -119.6045 | 2.0325 | -0.0054933 | 0.012127 | 0.066063 | 0.0011493 | 0.066371 | 0.0046485 | -0.002085 | -0.0040437 | -0.0015637 | 0.062643 | 0.066885 | 0.0076777 | -0.0076926 | 1.9958 | -118.9728 | -3.4515 | -119.4305 | 2.0554 | -119.7281 | -119.5587 | -120.076 | 0.009155 | -119.8105 | 1.9592 | 1.9821 | -119.5679 | -119.8013 | -0.1236 | 0.045776 | 0.022888 | 0.63171 | 0.17395 | 0.12817 | -0.036621 | 0.036621 | -0.19684 | -0.073242 | -0.4715 | -0.20599 | -0.009155 | -0.050354 | 121.6599 | 121.6003 | 116.153 | -121.5912 | 121.5637 | 121.5866 | 119.6136 | -121.8338
368.3906 | 121.9116 | -120.1996 | 1.4603 | -0.0054933 | 0.016186 | 0.06649 | 0.0073443 | 0.064021 | 0.0022987 | -0.0027258 | -0.019302 | -0.0039135 | 0.06307 | 0.06304 | 0.0040461 | -0.0081198 | 1.3687 | -119.5908 | -3.5202 | -120.0211 | 1.4832 | -120.3415 | -120.1721 | -120.6985 | 0 | -120.401 | 1.3824 | 1.4236 | -120.1767 | -120.3552 | -0.14191 | 0.027466 | 0.022888 | 0.60883 | 0.17853 | 0.15106 | -0.091553 | 0.022888 | -0.15564 | -0.07782 | -0.49896 | -0.20142 | -0.045776 | -0.036621 | 121.6827 | 121.5683 | 116.6794 | -121.6324 | 121.582 | 121.6232 | 120.1996 | -121.8155
370.0625 | 121.8613 | -120.3644 | 1.3229 | -0.0054933 | 0.015332 | 0.066917 | 0.0041401 | 0.067225 | 0.0033667 | 0.00090584 | -0.011673 | -0.0030591 | 0.063711 | 0.065604 | 0.0040461 | -0.007479 | 1.2543 | -119.6777 | -3.5019 | -120.1538 | 1.3138 | -120.4468 | -120.3186 | -120.845 | 0.022888 | -120.5383 | 1.236 | 1.2634 | -120.3369 | -120.5338 | -0.082397 | 0.045776 | -0.009155 | 0.68665 | 0.21057 | 0.16479 | -0.068665 | 0.027466 | -0.16937 | -0.086975 | -0.48065 | -0.17395 | -0.004578 | -0.059509 | 121.6782 | 121.6187 | 116.8625 | -121.6415 | 121.6003 | 121.6278 | 120.3873 | -121.8567
371.7969 | 121.8796 | -120.1263 | 1.5656 | 0.0021362 | 0.010418 | 0.067131 | 0.0069171 | 0.070002 | -0.0045373 | -0.002085 | -0.011673 | -0.0071179 | 0.063711 | 0.063254 | 0.00041446 | -0.007479 | 1.4832 | -119.3985 | -3.4607 | -119.9203 | 1.4832 | -120.2362 | -120.0714 | -120.6024 | 0.12817 | -120.2408 | 1.3962 | 1.4374 | -120.0714 | -120.2911 | -0.10986 | 0.054932 | -0.082398 | 0.72784 | 0.20599 | 0.15106 | -0.082398 | 0.054932 | -0.16479 | -0.16937 | -0.47607 | -0.11444 | 0.050354 | -0.12817 | 121.6095 | 121.6095 | 116.6656 | -121.637 | 121.5225 | 121.5637 | 120.2545 | -121.8567
373.4688 | 121.9345 | -120.1309 | 1.5427 | -0.0054933 | 0.015545 | 0.063072 | 0.0069171 | 0.067011 | 0.0016577 | -0.00037596 | -0.0040437 | -0.0030591 | 0.064993 | 0.066672 | 0.0040461 | -0.0070516 | 1.4374 | -119.5404 | -3.5614 | -119.9753 | 1.5518 | -120.2499 | -120.0714 | -120.6528 | -0.004578 | -120.3186 | 1.4832 | 1.4969 | -120.1035 | -120.2957 | -0.11902 | 0.059509 | 0.009155 | 0.59051 | 0.15564 | 0.09613 | -0.10529 | 0.027465 | -0.16479 | -0.05951 | -0.52185 | -0.18768 | -0.022889 | -0.045777 | 121.6827 | 121.5683 | 116.5695 | -121.6141 | 121.6141 | 121.6278 | 120.1263 | -121.8384
375.2031 | 121.9254 | -120.0485 | 1.6525 | -0.020752 | 0.017682 | 0.066063 | 0.0045673 | 0.067225 | -0.00047854 | -0.0018714 | 0.0035858 | -0.0056225 | 0.062429 | 0.064536 | 0.0046869 | -0.0079062 | 1.5289 | -119.426 | -3.5568 | -119.8471 | 1.6479 | -120.1447 | -119.989 | -120.5429 | 0 | -120.2362 | 1.5701 | 1.6022 | -120.0165 | -120.1904 | -0.09613 | 0.059509 | -0.004578 | 0.62256 | 0.20142 | 0.14191 | -0.1236 | 0.032044 | -0.14191 | -0.082398 | -0.49438 | -0.18768 | -0.045776 | -0.050354 | 121.6965 | 121.5775 | 116.4917 | -121.6415 | 121.6187 | 121.6507 | 120.0485 | -121.843
376.9375 | 121.9116 | -120.5566 | 1.1124 | -0.013122 | 0.0117 | 0.068199 | 0.0067035 | 0.067652 | -0.0053919 | -0.0027258 | -0.0040437 | -0.0088269 | 0.05837 | 0.065817 | 0.0010553 | -0.0042746 | 1.0986 | -119.8242 | -3.5065 | -120.3323 | 1.0941 | -120.6436 | -120.4788 | -121.0007 | 0.10986 | -120.6207 | 1.0071 | 1.03 | -120.5063 | -120.7123 | -0.086975 | 0.07782 | -0.018311 | 0.73242 | 0.22431 | 0.14648 | -0.013733 | 0.050354 | -0.15564 | -0.10529 | -0.44403 | -0.064087 | 0.091552 | -0.082398 | 121.6507 | 121.6553 | 117.0502 | -121.5912 | 121.5637 | 121.5866 | 120.6665 | -121.8246
378.6719 | 121.8018 | -120.2911 | 1.4191 | -0.0054933 | 0.0117 | 0.067558 | 0.0024311 | 0.066584 | -0.0045373 | -0.002085 | -0.011673 | -0.0069043 | 0.062856 | 0.065817 | 0.00084166 | -0.0044882 | 1.3092 | -119.6457 | -3.6072 | -120.1172 | 1.3733 | -120.369 | -120.1904 | -120.7718 | -0.027466 | -120.4056 | 1.3184 | 1.3504 | -120.2042 | -120.4376 | -0.07782 | 0.10071 | -0.045776 | 0.64545 | 0.17395 | 0.073243 | -0.10986 | 0.086975 | -0.14648 | -0.10071 | -0.48065 | -0.11444 | 0.032043 | -0.068664 | 121.6644 | 121.6003 | 116.684 | -121.6095 | 121.6095 | 121.6415 | 120.2637 | -121.8567
380.3594 | 121.9345 | -120.4697 | 1.2451 | -0.0054933 | 0.014905 | 0.069267 | 0.0034991 | 0.064234 | 0.0029395 | -0.0031532 | 0.0035858 | -0.0036999 | 0.063284 | 0.06774 | 0.0049005 | -0.007479 | 1.1398 | -119.8791 | -3.7491 | -120.2957 | 1.2177 | -120.5566 | -120.4376 | -120.9641 | -0.14648 | -120.6436 | 1.1719 | 1.1948 | -120.4422 | -120.6207 | -0.086975 | 0.032044 | -0.027466 | 0.59052 | 0.17395 | 0.14191 | -0.10529 | 0.027466 | -0.15106 | -0.073242 | -0.49438 | -0.17395 | -0.022888 | -0.050354 | 121.6873 | 121.6095 | 116.7206 | -121.6827 | 121.6415 | 121.6644 | 120.3232 | -121.8658
382.0938 | 121.8521 | -120.2637 | 1.4648 | -0.0054933 | 0.012982 | 0.066063 | 0.0052081 | 0.06338 | -0.0049645 | -0.0029394 | -0.0040437 | -0.0077587 | 0.061575 | 0.064536 | 0.0023371 | -0.0064108 | 1.355 | -119.5816 | -3.6072 | -120.0439 | 1.4465 | -120.3369 | -120.1584 | -120.7397 | 0 | -120.3506 | 1.3687 | 1.3916 | -120.163 | -120.3827 | -0.073242 | 0.10529 | -0.018311 | 0.68207 | 0.21973 | 0.11444 | -0.10986 | 0.10071 | -0.11902 | -0.096131 | -0.47607 | -0.086975 | 0.032043 | -0.073242 | 121.7102 | 121.6187 | 116.6565 | -121.6232 | 121.6324 | 121.6553 | 120.2637 | -121.8475
383.8438 | 121.7743 | -120.314 | 1.4557 | -0.0054933 | 0.016827 | 0.066704 | 0.0026447 | 0.065089 | 0.0048621 | -0.0014442 | -0.011673 | -0.0045545 | 0.062216 | 0.066672 | 0.0068231 | -0.008547 | 1.3458 | -119.6594 | -3.5843 | -120.0851 | 1.4282 | -120.3506 | -120.2087 | -120.7764 | -0.041199 | -120.4926 | 1.3641 | 1.3962 | -120.2225 | -120.4102 | -0.036621 | 0.10529 | -0.027465 | 0.6546 | 0.22888 | 0.1236 | -0.10986 | 0.091553 | -0.09613 | -0.091552 | -0.46234 | -0.17853 | -0.082398 | -0.059509 | 121.7422 | 121.6599 | 116.7297 | -121.6644 | 121.6782 | 121.7102 | 120.2728 | -121.8658
385.5312 | 121.875 | -120.3278 | 1.3504 | -0.020752 | 0.014691 | 0.067558 | 0.0052081 | 0.065516 | -0.0026147 | -0.0022986 | -0.0040437 | -0.0086133 | 0.063925 | 0.064536 | 0.0025507 | -0.0070516 | 1.3412 | -119.5633 | -3.5156 | -120.0897 | 1.3458 | -120.3964 | -120.2454 | -120.7626 | 0.10529 | -120.3918 | 1.268 | 1.2955 | -120.2637 | -120.4605 | -0.068664 | 0.082398 | -0.004578 | 0.76447 | 0.23804 | 0.15564 | -0.009155 | 0.064087 | -0.13275 | -0.082398 | -0.43488 | -0.064087 | 0.068664 | -0.054932 | 121.6736 | 121.669 | 116.8121 | -121.5958 | 121.5958 | 121.6232 | 120.433 | -121.8109
387.2656 | 121.8567 | -120.0577 | 1.6571 | -0.0054933 | 0.013836 | 0.067345 | 0.0030719 | 0.06573 | -0.00047854 | -0.002085 | -0.0040437 | -0.0066907 | 0.061575 | 0.062186 | 0.0027643 | -0.0064108 | 1.5976 | -119.3344 | -3.5156 | -119.8196 | 1.6159 | -120.1035 | -119.9478 | -120.5338 | 0.041199 | -120.1767 | 1.5793 | 1.6113 | -120.0211 | -120.195 | -0.045777 | 0.10986 | -0.041198 | 0.72327 | 0.23804 | 0.12817 | -0.059509 | 0.036621 | -0.13733 | -0.077819 | -0.47607 | -0.11902 | 0.01831 | -0.045776 | 121.6736 | 121.6553 | 116.5421 | -121.6049 | 121.637 | 121.669 | 120.0989 | -121.8521
389 | 121.7468 | -120.1492 | 1.6022 | -0.0054933 | 0.0099912 | 0.068626 | 0.0015765 | 0.066798 | -0.0030419 | -0.0025122 | 0.0035858 | -0.0071179 | 0.06072 | 0.064322 | 0.0046869 | -0.004061 | 1.5015 | -119.4397 | -3.5385 | -119.9432 | 1.5152 | -120.2271 | -120.0623 | -120.6207 | 0.013733 | -120.2545 | 1.4191 | 1.4557 | -120.0577 | -120.3003 | -0.07782 | 0.086975 | -0.086975 | 0.70953 | 0.20599 | 0.11902 | -0.10071 | 0.091553 | -0.15106 | -0.18311 | -0.4715 | -0.10529 | 0.045776 | -0.14648 | 121.6644 | 121.6507 | 116.6107 | -121.6644 | 121.5683 | 121.6049 | 120.163 | -121.9025
390.75 | 121.7606 | -120.1813 | 1.5472 | 0.0021362 | 0.011273 | 0.068413 | 0.00072207 | 0.068507 | -0.0011193 | -0.00016236 | 0.0035858 | -0.0075451 | 0.06072 | 0.063895 | 0.0036189 | -0.0061972 | 1.5015 | -119.4489 | -3.5339 | -119.9478 | 1.5152 | -120.2362 | -120.0851 | -120.6024 | 0.054932 | -120.2591 | 1.4099 | 1.4465 | -120.0943 | -120.3003 | -0.054932 | 0.09613 | -0.032043 | 0.73242 | 0.23346 | 0.13733 | -0.045776 | 0.086975 | -0.11902 | -0.13733 | -0.42114 | -0.07782 | 0.041199 | -0.10071 | 121.6965 | 121.6827 | 116.6473 | -121.6324 | 121.5912 | 121.6278 | 120.2362 | -121.8475
392.4375 | 121.8246 | -120.1035 | 1.6205 | -0.0054933 | 0.012127 | 0.067131 | 0.0032855 | 0.067866 | 0.0022987 | 0.0011194 | -0.019302 | -0.0022045 | 0.059439 | 0.064963 | 0.0040461 | -0.0072652 | 1.474 | -119.5267 | -3.6346 | -119.957 | 1.6113 | -120.2042 | -120.0394 | -120.6299 | -0.073242 | -120.3278 | 1.5289 | 1.5564 | -120.0577 | -120.2545 | -0.10071 | 0.064087 | -0.009155 | 0.57678 | 0.14648 | 0.082398 | -0.14648 | 0.045777 | -0.15106 | -0.091552 | -0.52643 | -0.2243 | -0.073242 | -0.064087 | 121.7148 | 121.5775 | 116.4688 | -121.6599 | 121.6324 | 121.6599 | 120.0302 | -121.875
394.1875 | 121.9025 | -120.0943 | 1.6113 | -0.013122 | 0.014264 | 0.066704 | 0.0043537 | 0.067866 | 0.0029395 | -0.0022986 | 0.0035858 | -0.0051953 | 0.061361 | 0.066031 | 0.0053279 | -0.0061972 | 1.5015 | -119.4626 | -3.5843 | -119.9249 | 1.5884 | -120.2087 | -120.0623 | -120.5933 | 0.009155 | -120.282 | 1.4969 | 1.5381 | -120.0394 | -120.2774 | -0.11444 | 0.032043 | -0.022888 | 0.63171 | 0.16937 | 0.13733 | -0.10986 | 0.054931 | -0.18311 | -0.11444 | -0.49896 | -0.18768 | -0.004577 | -0.073242 | 121.6827 | 121.5958 | 116.51 | -121.6736 | 121.5912 | 121.6324 | 120.1035 | -121.8887
395.9531 | 121.7789 | -120.1172 | 1.6388 | -0.020752 | 0.014264 | 0.066277 | 0.0020039 | 0.066584 | 0.0048621 | 0.00047844 | -0.0040437 | -0.0043409 | 0.059439 | 0.06774 | 0.0074641 | -0.0091878 | 1.474 | -119.5129 | -3.6209 | -119.9478 | 1.6205 | -120.1813 | -120.0623 | -120.6482 | -0.091553 | -120.3369 | 1.5335 | 1.5656 | -120.0714 | -120.2682 | -0.064087 | 0.054931 | -0.018311 | 0.60425 | 0.16937 | 0.11444 | -0.1648 | 0.045776 | -0.15106 | -0.10529 | -0.53101 | -0.21973 | -0.068664 | -0.073242 | 121.7377 | 121.5912 | 116.4963 | -121.7011 | 121.6507 | 121.6827 | 120.0256 | -121.907
397.6406 | 121.8338 | -120.1218 | 1.5701 | -0.020752 | 0.014477 | 0.066704 | 0.0039265 | 0.064021 | 0.0027259 | -0.0010168 | -0.011673 | -0.0056225 | 0.063925 | 0.06539 | 0.0044733 | -0.0049154 | 1.4832 | -119.4809 | -3.6118 | -119.9432 | 1.6342 | -120.1859 | -120.0348 | -120.6345 | -0.041199 | -120.3003 | 1.4832 | 1.5289 | -120.0668 | -120.2957 | -0.064087 | 0.086975 | 0.064087 | 0.64087 | 0.17853 | 0.091553 | -0.086975 | 0.054932 | -0.17395 | -0.086975 | -0.5127 | -0.17853 | -0.004578 | -0.041198 | 121.756 | 121.6049 | 116.51 | -121.6049 | 121.6049 | 121.6507 | 120.0806 | -121.8658
399.375 | 121.9025 | -120.3918 | 1.2955 | -0.013122 | 0.012982 | 0.069054 | 0.0084125 | 0.06573 | -0.0049645 | -0.0014442 | -0.019302 | -0.010322 | 0.059652 | 0.063254 | -0.0010809 | -0.0053426 | 1.268 | -119.6365 | -3.5431 | -120.1584 | 1.268 | -120.4697 | -120.3278 | -120.8725 | 0.09613 | -120.4514 | 1.1948 | 1.2314 | -120.3552 | -120.5429 | -0.07782 | 0.064087 | -0.027466 | 0.75531 | 0.23346 | 0.16937 | -0.027466 | 0.036621 | -0.15106 | -0.10071 | -0.48065 | -0.059509 | 0.091553 | -0.064087 | 121.6599 | 121.6599 | 116.8488 | -121.6232 | 121.5866 | 121.6232 | 120.488 | -121.8384
401.0469 | 121.8475 | -120.1813 | 1.5106 | -0.0054933 | 0.012341 | 0.067772 | 0.0079853 | 0.066798 | -0.0019739 | -0.0033668 | 0.0035858 | -0.0086133 | 0.062216 | 0.063254 | 0.0025507 | -0.0059836 | 1.3779 | -119.5816 | -3.6209 | -120.0394 | 1.4969 | -120.2957 | -120.1447 | -120.7672 | -0.027466 | -120.401 | 1.4236 | 1.4511 | -120.1767 | -120.3827 | -0.11444 | 0.036621 | -0.013733 | 0.59967 | 0.14191 | 0.10529 | -0.13275 | 0.004577 | -0.20142 | -0.086975 | -0.58594 | -0.21973 | -0.018311 | -0.059509 | 121.6782 | 121.5591 | 116.5604 | -121.6553 | 121.6049 | 121.6324 | 120.1538 | -121.8933
402.7969 | 121.8704 | -120.4742 | 1.2085 | -0.0054933 | 0.013836 | 0.06884 | 0.0039265 | 0.067652 | -0.0026147 | -0.0010168 | -0.019302 | -0.0054089 | 0.062856 | 0.063681 | 0.0031915 | -0.0055564 | 1.1856 | -119.7372 | -3.5385 | -120.2499 | 1.1993 | -120.5658 | -120.369 | -120.9137 | 0.091553 | -120.5521 | 1.1353 | 1.1627 | -120.3873 | -120.6299 | -0.091553 | 0.10528 | -0.009155 | 0.737 | 0.2243 | 0.11902 | -0.022888 | 0.086975 | -0.15564 | -0.073242 | -0.43945 | -0.07782 | 0.07782 | -0.045776 | 121.6736 | 121.6599 | 116.9357 | -121.5775 | 121.6095 | 121.637 | 120.5658 | -121.8384
404.5312 | 121.7834 | -120.5017 | 1.2589 | -0.020752 | 0.0099912 | 0.068413 | -0.00077333 | 0.065943 | -0.0013329 | -0.0048622 | -0.011673 | -0.0088269 | 0.059652 | 0.064108 | 0.0034051 | -0.0064108 | 1.1856 | -119.8105 | -3.5934 | -120.3003 | 1.1993 | -120.5383 | -120.3964 | -120.9686 | 0.009155 | -120.6024 | 1.1215 | 1.1673 | -120.3781 | -120.6116 | -0.036621 | 0.10529 | -0.059509 | 0.69122 | 0.20142 | 0.09613 | -0.073242 | 0.1236 | -0.10986 | -0.13733 | -0.46692 | -0.10071 | 0.009155 | -0.091553 | 121.7011 | 121.6873 | 116.9083 | -121.6553 | 121.6232 | 121.669 | 120.5109 | -121.8704
406.2812 | 121.8567 | -120.0302 | 1.6708 | -0.0054933 | 0.009564 | 0.068199 | 0.0052081 | 0.066371 | -0.0015465 | -0.0040076 | -0.0040437 | -0.0064771 | 0.062216 | 0.064536 | 0.00062806 | -0.0081198 | 1.6205 | -119.3893 | -3.6163 | -119.8013 | 1.68 | -120.076 | -119.9203 | -120.4788 | 0.009155 | -120.1584 | 1.5656 | 1.6251 | -119.957 | -120.163 | -0.045777 | 0.10986 | 0.009156 | 0.64087 | 0.22888 | 0.11902 | -0.050354 | 0.073242 | -0.13275 | -0.10528 | -0.44861 | -0.12817 | 0.004578 | -0.045776 | 121.7102 | 121.6507 | 116.4139 | -121.5912 | 121.5958 | 121.6553 | 120.0394 | -121.8338
408.0156 | 121.8155 | -120.52 | 1.2222 | -0.013122 | 0.012127 | 0.064995 | 0.0020039 | 0.06573 | 0.0018713 | -0.0022986 | -0.019302 | -0.0064771 | 0.059866 | 0.06539 | 0.0057551 | -0.0070516 | 1.1902 | -119.7739 | -3.5889 | -120.2682 | 1.1765 | -120.5887 | -120.3964 | -120.9183 | 0.041199 | -120.5933 | 1.0895 | 1.1124 | -120.4559 | -120.6619 | -0.068664 | 0.1236 | -0.045776 | 0.74616 | 0.25177 | 0.12817 | -0.032043 | 0.064087 | -0.14191 | -0.13275 | -0.39825 | -0.073242 | 0.068664 | -0.10986 | 121.6965 | 121.7102 | 116.9312 | -121.6187 | 121.6095 | 121.6324 | 120.5612 | -121.8842
409.75 | 121.8292 | -120.5475 | 1.236 | -0.0054933 | 0.014691 | 0.069908 | 0.0032855 | 0.064448 | 0.0033667 | -0.00080316 | 0.0035858 | -0.0060497 | 0.061788 | 0.066031 | 0.0070367 | -0.0070516 | 1.0986 | -119.9478 | -3.6896 | -120.3415 | 1.236 | -120.607 | -120.4514 | -121.0373 | -0.09613 | -120.7352 | 1.1536 | 1.1719 | -120.4697 | -120.6757 | -0.05951 | 0.09613 | 0 | 0.59967 | 0.20599 | 0.10986 | -0.13733 | 0.077819 | -0.12817 | -0.082398 | -0.48981 | -0.18768 | -0.059509 | -0.064087 | 121.7834 | 121.6461 | 116.8579 | -121.6873 | 121.701 | 121.7194 | 120.4514 | -121.9116
411.4219 | 121.8063 | -120.4697 | 1.3138 | -0.013122 | 0.011487 | 0.065636 | 0.0030719 | 0.064234 | 0.00058966 | 0.00069204 | -0.026932 | -0.0060497 | 0.061148 | 0.064322 | 0.0021235 | -0.0083334 | 1.2497 | -119.7281 | -3.598 | -120.1996 | 1.236 | -120.5017 | -120.3369 | -120.8496 | 0.041199 | -120.5338 | 1.1536 | 1.2085 | -120.3598 | -120.575 | -0.032043 | 0.13275 | -0.07782 | 0.74158 | 0.27008 | 0.13733 | -0.064087 | 0.10986 | -0.10528 | -0.16022 | -0.37994 | -0.064086 | 0.041199 | -0.10529 | 121.7056 | 121.7194 | 116.8716 | -121.6507 | 121.6232 | 121.6782 | 120.5109 | -121.8887
413.1719 | 121.7834 | -120.4742 | 1.3046 | -0.013122 | 0.014691 | 0.067772 | 0.0028583 | 0.064021 | 0.0029395 | -0.00058956 | -0.011673 | -0.0056225 | 0.060079 | 0.064536 | 0.0068231 | -0.005129 | 1.1398 | -119.8471 | -3.6942 | -120.2774 | 1.3 | -120.5154 | -120.3598 | -120.9915 | -0.086975 | -120.6711 | 1.2222 | 1.2543 | -120.3918 | -120.5933 | -0.041199 | 0.11444 | -0.004577 | 0.62714 | 0.19684 | 0.082397 | -0.16479 | 0.082397 | -0.11902 | -0.082397 | -0.51727 | -0.19684 | -0.07782 | -0.050354 | 121.7743 | 121.6141 | 116.7801 | -121.6644 | 121.6965 | 121.7285 | 120.3873 | -121.8979
414.9219 | 121.9025 | -120.5383 | 1.1627 | 0.0021362 | 0.014905 | 0.06649 | 0.0047809 | 0.066157 | 0.00016226 | 0.00026484 | -0.0040437 | -0.0030591 | 0.06307 | 0.065176 | 0.0051141 | -0.0064108 | 1.0941 | -119.8791 | -3.6301 | -120.3598 | 1.1765 | -120.6436 | -120.488 | -121.0602 | 0.004578 | -120.6711 | 1.062 | 1.1078 | -120.5338 | -120.7077 | -0.10529 | 0.050354 | 0.013733 | 0.65918 | 0.17853 | 0.12817 | -0.068665 | 0.004578 | -0.16937 | -0.10071 | -0.52185 | -0.13275 | 0.036621 | -0.054932 | 121.7148 | 121.6324 | 116.9083 | -121.6507 | 121.6003 | 121.6461 | 120.5429 | -121.8704
416.6094 | 121.7514 | -120.6482 | 1.1261 | -0.020752 | 0.012768 | 0.066704 | 0.0049945 | 0.063166 | -0.0032555 | -0.0018714 | 0.0035858 | -0.0069043 | 0.060934 | 0.063895 | 0.0014825 | -0.0038474 | 1.0437 | -119.9112 | -3.6301 | -120.4147 | 1.0712 | -120.694 | -120.488 | -121.0922 | 0.004578 | -120.7306 | 0.98877 | 1.0254 | -120.5429 | -120.7626 | -0.045777 | 0.16022 | -0.054932 | 0.737 | 0.23346 | 0.073242 | -0.082398 | 0.10529 | -0.11444 | -0.13733 | -0.44403 | -0.082398 | 0.032043 | -0.10071 | 121.7194 | 121.6919 | 117.0181 | -121.6141 | 121.637 | 121.6736 | 120.6528 | -121.8887
418.3438 | 121.8384 | -120.5566 | 1.181 | -0.0054933 | 0.017468 | 0.065208 | 0.0052081 | 0.06573 | 0.0027259 | -0.0025122 | -0.0040437 | -0.0030591 | 0.062429 | 0.066672 | 0.0046869 | -0.006838 | 1.1124 | -119.8837 | -3.6118 | -120.3552 | 1.1673 | -120.6436 | -120.5017 | -121.019 | 0.013733 | -120.7306 | 1.1032 | 1.1124 | -120.52 | -120.7077 | -0.086975 | 0.054932 | -0.013733 | 0.67291 | 0.20142 | 0.14648 | -0.068664 | 0.036621 | -0.15106 | -0.07782 | -0.46234 | -0.17395 | -0.022888 | -0.068664 | 121.7239 | 121.669 | 116.9449 | -121.6827 | 121.6599 | 121.669 | 120.5704 | -121.8887
420.0781 | 121.8155 | -120.6299 | 1.1536 | -0.013122 | 0.014905 | 0.067131 | 0.0026447 | 0.066371 | 0.0042213 | -0.00016236 | -0.011673 | -0.0032727 | 0.063497 | 0.064963 | 0.0063959 | -0.0070516 | 1.0574 | -119.9341 | -3.6392 | -120.4147 | 1.1307 | -120.6985 | -120.5154 | -121.0922 | -0.022888 | -120.7764 | 1.0483 | 1.0666 | -120.5383 | -120.7535 | -0.068664 | 0.11444 | -0.022888 | 0.6958 | 0.21515 | 0.10071 | -0.09613 | 0.091553 | -0.1236 | -0.10529 | -0.46234 | -0.14648 | -0.022888 | -0.086975 | 121.7606 | 121.6873 | 116.9907 | -121.669 | 121.6782 | 121.6965 | 120.607 | -121.907
421.75 | 121.8109 | -120.4605 | 1.3092 | 0.0021362 | 0.013836 | 0.069267 | 0.0020039 | 0.065302 | 0.0022987 | 5.1244e-05 | -0.011673 | -0.0077587 | 0.061361 | 0.064322 | 0.0038325 | -0.0055564 | 1.268 | -119.7235 | -3.6118 | -120.1904 | 1.2451 | -120.5063 | -120.3369 | -120.8633 | 0.041199 | -120.5154 | 1.1719 | 1.2131 | -120.369 | -120.5383 | -0.045777 | 0.1236 | -0.064087 | 0.737 | 0.27008 | 0.14648 | -0.041199 | 0.091552 | -0.07782 | -0.13733 | -0.40283 | -0.054932 | 0.022888 | -0.09613 | 121.7056 | 121.7285 | 116.8488 | -121.6461 | 121.6324 | 121.6736 | 120.5017 | -121.8475
423.4844 | 121.9025 | -120.4788 | 1.2268 | -0.020752 | 0.015545 | 0.067345 | 0.0079853 | 0.067225 | -0.0017603 | -0.0033668 | -0.011673 | -0.0043409 | 0.062643 | 0.064536 | 0.0029779 | -0.0059836 | 1.0895 | -119.8791 | -3.6942 | -120.3461 | 1.2222 | -120.5704 | -120.4376 | -121.051 | -0.041199 | -120.6848 | 1.1856 | 1.1856 | -120.488 | -120.6436 | -0.091553 | 0.041199 | -0.004578 | 0.59967 | 0.13275 | 0.091553 | -0.13733 | -0.009155 | -0.16479 | -0.041199 | -0.5722 | -0.20599 | -0.041198 | -0.041199 | 121.701 | 121.5683 | 116.7847 | -121.6644 | 121.6644 | 121.6644 | 120.4376 | -121.8704
425.2188 | 121.9208 | -120.4239 | 1.2589 | -0.0054933 | 0.0097776 | 0.067558 | 0.0030719 | 0.065516 | -0.0034691 | -0.0035804 | -0.0040437 | -0.0098951 | 0.061148 | 0.06774 | -1.2744e-05 | -0.0049154 | 1.2451 | -119.6777 | -3.598 | -120.195 | 1.2497 | -120.5063 | -120.3323 | -120.8679 | 0.10529 | -120.4834 | 1.1627 | 1.2039 | -120.3598 | -120.5795 | -0.082398 | 0.091553 | -0.009155 | 0.74616 | 0.22888 | 0.13733 | -0.013733 | 0.064087 | -0.15564 | -0.09613 | -0.44403 | -0.059509 | 0.096131 | -0.054932 | 121.6736 | 121.669 | 116.8259 | -121.5912 | 121.5866 | 121.6278 | 120.5292 | -121.8384
426.8906 | 121.788 | -120.5566 | 1.2314 | -0.0054933 | 0.013836 | 0.067558 | 0.0034991 | 0.064021 | 0.0033667 | -0.00058956 | -0.011673 | -0.0051953 | 0.062429 | 0.065817 | 0.0055415 | -0.0094016 | 1.1169 | -119.8929 | -3.6346 | -120.3415 | 1.1902 | -120.6162 | -120.433 | -121.0327 | -0.045776 | -120.7306 | 1.1261 | 1.1581 | -120.4697 | -120.7077 | -0.059509 | 0.1236 | -0.041198 | 0.66376 | 0.21515 | 0.091552 | -0.11444 | 0.086975 | -0.15106 | -0.10529 | -0.47607 | -0.17395 | -0.022888 | -0.073242 | 121.7468 | 121.6736 | 116.922 | -121.6644 | 121.6827 | 121.7148 | 120.5109 | -121.9391
428.625 | 121.8704 | -120.5933 | 1.1581 | -0.0054933 | 0.015545 | 0.067986 | 0.0069171 | 0.070643 | -0.0026147 | -0.0031532 | -0.0040437 | -0.0069043 | 0.065634 | 0.065604 | 0.00020086 | -0.006838 | 1.0345 | -119.9341 | -3.685 | -120.3827 | 1.1627 | -120.6665 | -120.488 | -121.1105 | -0.032043 | -120.7581 | 1.0941 | 1.1124 | -120.5566 | -120.7214 | -0.073242 | 0.10529 | 0.004578 | 0.65918 | 0.21057 | 0.10529 | -0.1236 | 0.036621 | -0.12817 | -0.064087 | -0.51727 | -0.16479 | -0.036621 | -0.045776 | 121.756 | 121.6278 | 116.9083 | -121.6461 | 121.6873 | 121.7056 | 120.5612 | -121.8796
430.3594 | 121.7789 | -120.5658 | 1.1627 | -0.0054933 | 0.010846 | 0.067345 | 0.0011493 | 0.066584 | -0.0011193 | 5.1244e-05 | -0.0040437 | -0.0069043 | 0.059866 | 0.064963 | 0.0010553 | -0.0072652 | 1.1124 | -119.8425 | -3.6209 | -120.3323 | 1.1078 | -120.6299 | -120.4651 | -120.9961 | 0.027466 | -120.6482 | 1.0254 | 1.0895 | -120.488 | -120.6711 | -0.064087 | 0.10071 | -0.054932 | 0.72327 | 0.23346 | 0.13275 | -0.050354 | 0.07782 | -0.10529 | -0.13733 | -0.4303 | -0.082397 | 0.022889 | -0.073242 | 121.6736 | 121.6782 | 116.9449 | -121.6278 | 121.5912 | 121.6553 | 120.5933 | -121.8338
432.1094 | 121.7468 | -120.6299 | 1.1307 | -0.0054933 | 0.011487 | 0.066917 | 0.0047809 | 0.066584 | -0.0049645 | -0.0022986 | -0.0040437 | -0.0079725 | 0.061575 | 0.064322 | 0.0029779 | -0.0055564 | 1.0712 | -119.8654 | -3.7994 | -120.4102 | 1.0803 | -120.6711 | -120.52 | -121.0876 | -0.21973 | -120.726 | 1.0025 | 1.0437 | -120.5429 | -120.7443 | -0.041199 | 0.10986 | -0.050354 | 0.76447 | 0.21973 | 0.10986 | -0.059509 | 0.086975 | -0.11444 | -0.12817 | -0.45776 | -0.09613 | 0.018311 | -0.086975 | 121.7102 | 121.7011 | 116.8304 | -121.6507 | 121.6324 | 121.6736 | 120.4102 | -121.875
433.8438 | 121.8292 | -119.9066 | 1.8402 | 0.0097657 | 0.013196 | 0.06884 | 0.0020039 | 0.065089 | 0.0020849 | -0.0033668 | -0.0040437 | -0.0024183 | 0.060934 | 0.064963 | 0.0070367 | -0.011111 | 1.7578 | -119.252 | -3.6301 | -119.7098 | 1.8265 | -119.9661 | -119.7922 | -120.3598 | 0.018311 | -120.0165 | 1.7212 | 1.7715 | -119.8471 | -120.0027 | -0.059509 | 0.11444 | -0.013733 | 0.6546 | 0.19684 | 0.082397 | -0.082398 | 0.059509 | -0.096131 | -0.11902 | -0.45319 | -0.10986 | -0.013732 | -0.068665 | 121.7331 | 121.6644 | 116.2766 | -121.6324 | 121.6278 | 121.6782 | 119.9249 | -121.843
435.5156 | 121.8842 | -121.0007 | 0.71411 | -0.0054933 | 0.016186 | 0.06649 | 0.0022175 | 0.06573 | 0.0065711 | -0.00016236 | -0.0040437 | -0.0026319 | 0.060934 | 0.064108 | 0.0057551 | -0.0079062 | 0.67291 | -120.3552 | -3.6713 | -120.8084 | 0.73242 | -121.0968 | -120.9595 | -121.4767 | 0.013733 | -121.1655 | 0.61798 | 0.67291 | -120.9732 | -121.1609 | -0.096131 | 0.041198 | 0.018311 | 0.64545 | 0.19226 | 0.15106 | -0.041198 | 0.027465 | -0.16022 | -0.09613 | -0.47608 | -0.16479 | -0.004577 | -0.041198 | 121.7331 | 121.6736 | 117.3294 | -121.6736 | 121.6187 | 121.6736 | 121.0144 | -121.875
437.25 | 121.8704 | -120.8084 | 0.90637 | -0.0054933 | 0.014477 | 0.06649 | 0.0041401 | 0.067011 | -0.0017603 | -0.0018714 | -0.0040437 | -0.0096813 | 0.064565 | 0.064749 | 0.0019099 | -0.0053426 | 0.84228 | -120.0851 | -3.6346 | -120.5933 | 0.84686 | -120.9045 | -120.7169 | -121.2753 | 0.07782 | -120.9229 | 0.75989 | 0.83313 | -120.7901 | -120.9457 | -0.09613 | 0.091553 | -0.059509 | 0.72327 | 0.21515 | 0.1236 | -0.064087 | 0.018311 | -0.13733 | -0.14648 | -0.46692 | -0.11444 | 0.022888 | -0.073242 | 121.6553 | 121.6507 | 117.1738 | -121.6232 | 121.5683 | 121.6415 | 120.8862 | -121.8521
438.9844 | 121.7972 | -121.2479 | 0.49896 | 0.0021362 | 0.010418 | 0.065208 | 0.0015765 | 0.068293 | -0.00047854 | 5.1244e-05 | -0.0040437 | -0.0051953 | 0.059439 | 0.065176 | 0.0053279 | -0.0079062 | 0.46692 | -120.5063 | -3.6896 | -120.9961 | 0.47607 | -121.2799 | -121.1243 | -121.6644 | 0.032043 | -121.3257 | 0.37079 | 0.41199 | -121.1975 | -121.3531 | -0.032043 | 0.1236 | -0.022888 | 0.74158 | 0.25177 | 0.12817 | -0.032043 | 0.050354 | -0.10528 | -0.12817 | -0.41656 | -0.07782 | 0.027465 | -0.086975 | 121.7239 | 121.7148 | 117.5583 | -121.6232 | 121.6187 | 121.6599 | 121.2799 | -121.8521
440.7188 | 121.9162 | -121.2067 | 0.48065 | -0.0054933 | 0.010632 | 0.069695 | 0.0028583 | 0.065516 | -0.0068871 | -0.0040076 | -0.0040437 | -0.0088269 | 0.059866 | 0.064108 | -1.2744e-05 | -0.00577 | 0.44861 | -120.5063 | -3.6987 | -121.0144 | 0.47607 | -121.312 | -121.1472 | -121.6782 | 0.068665 | -121.2982 | 0.37079 | 0.41199 | -121.1975 | -121.3715 | -0.10529 | 0.059509 | -0.004578 | 0.70038 | 0.19226 | 0.13275 | -0.032044 | 0.009155 | -0.16479 | -0.10986 | -0.4715 | -0.091553 | 0.073242 | -0.068665 | 121.6827 | 121.6553 | 117.5079 | -121.6278 | 121.5775 | 121.6187 | 121.2753 | -121.8521
442.3906 | 121.7789 | -121.4172 | 0.36163 | -0.013122 | 0.012982 | 0.067558 | 0.0045673 | 0.06338 | -0.0019739 | -0.0025122 | -0.011673 | -0.0036999 | 0.059439 | 0.066031 | 0.0027643 | -0.0072652 | 0.3067 | -120.6894 | -3.7399 | -121.1838 | 0.31586 | -121.4264 | -121.2616 | -121.8613 | -0.018311 | -121.4951 | 0.23804 | 0.29755 | -121.3257 | -121.5179 | -0.009156 | 0.15564 | -0.045776 | 0.72784 | 0.23346 | 0.07782 | -0.054931 | 0.091552 | -0.10071 | -0.1236 | -0.44403 | -0.07782 | 0.022888 | -0.064087 | 121.7331 | 121.7239 | 117.6773 | -121.6232 | 121.6553 | 121.7148 | 121.3989 | -121.8796
444.0781 | 121.788 | -121.4218 | 0.37537 | -0.0054933 | 0.0117 | 0.067772 | 0.0054217 | 0.066371 | -0.0024011 | -0.0046484 | 0.0035858 | -0.0075451 | 0.061575 | 0.063895 | 0.0019099 | -0.0079062 | 0.28839 | -120.726 | -3.772 | -121.1929 | 0.31128 | -121.4447 | -121.2936 | -121.8933 | -0.022888 | -121.5134 | 0.25177 | 0.27008 | -121.3577 | -121.5271 | -0.022888 | 0.12817 | -0.064087 | 0.6958 | 0.22888 | 0.10071 | -0.086975 | 0.064087 | -0.10529 | -0.1236 | -0.4715 | -0.091553 | 0.013733 | -0.10528 | 121.7331 | 121.7102 | 117.6498 | -121.669 | 121.6736 | 121.6919 | 121.3989 | -121.9025
445.8281 | 121.8246 | -121.1838 | 0.55847 | -0.020752 | 0.015973 | 0.067986 | 0.0011493 | 0.065302 | 0.0050757 | -0.002085 | -0.019302 | -0.0039135 | 0.060934 | 0.06539 | 0.0070367 | -0.0083334 | 0.44403 | -120.5841 | -3.7903 | -121.0098 | 0.59052 | -121.2433 | -121.0968 | -121.6965 | -0.091553 | -121.376 | 0.49439 | 0.50812 | -121.1426 | -121.3257 | -0.059509 | 0.086975 | 0.032043 | 0.59967 | 0.17395 | 0.086975 | -0.11444 | 0.041199 | -0.14191 | -0.064087 | -0.51269 | -0.19226 | -0.050354 | -0.050354 | 121.7743 | 121.6278 | 117.3935 | -121.6553 | 121.6782 | 121.6919 | 121.0922 | -121.8842
447.5625 | 121.6003 | -121.3989 | 0.17853 | -0.013122 | 0.014905 | 0.064781 | 0.0034991 | 0.065302 | 0.0050757 | -0.0014442 | -0.011673 | -0.00092292 | 0.061788 | 0.06539 | 0.0068231 | -0.0066244 | 0.036621 | -120.7901 | -3.8315 | -121.2112 | 0.16022 | -121.4584 | -121.3257 | -121.9208 | -0.086975 | -121.6232 | 0.07782 | 0.12817 | -121.3669 | -121.5591 | -0.059509 | 0.073242 | -0.018311 | 0.60883 | 0.18768 | 0.11444 | -0.14191 | 0.032044 | -0.16022 | -0.10071 | -0.52185 | -0.2243 | -0.064087 | -0.050354 | 121.5591 | 121.4355 | 117.5674 | -121.5042 | 121.4767 | 121.5271 | 121.312 | -121.7377
449.2344 | 121.788 | -121.5866 | 0.16479 | -0.0054933 | 0.015759 | 0.068199 | 0.0043537 | 0.066371 | 0.0037939 | -0.00058956 | -0.011673 | -0.0028455 | 0.062643 | 0.065604 | 0.0051141 | -0.0089742 | 0.064087 | -120.9091 | -3.772 | -121.3806 | 0.14191 | -121.6415 | -121.4722 | -122.0627 | -0.032043 | -121.7606 | 0.086975 | 0.10529 | -121.5591 | -121.7285 | -0.054932 | 0.11444 | -0.022888 | 0.67749 | 0.20599 | 0.091553 | -0.10071 | 0.027466 | -0.14191 | -0.07782 | -0.47607 | -0.17395 | -0.032043 | -0.059509 | 121.7285 | 121.6507 | 117.8146 | -121.637 | 121.6736 | 121.6919 | 121.5546 | -121.8933
450.9844 | 121.7697 | -121.5866 | 0.16937 | -0.0054933 | 0.012127 | 0.06649 | 0.0034991 | 0.06573 | -0.0038965 | -0.0010168 | -0.0040437 | -0.0075451 | 0.061148 | 0.064536 | 0.0016963 | -0.0055564 | 0.11902 | -120.8038 | -3.7308 | -121.312 | 0.11902 | -121.6049 | -121.4539 | -122.0169 | 0.050354 | -121.6553 | 0.036621 | 0.07782 | -121.4996 | -121.7102 | -0.01831 | 0.13275 | -0.050354 | 0.78278 | 0.27466 | 0.14191 | -0.050354 | 0.086975 | -0.1236 | -0.13275 | -0.4303 | -0.068664 | 0.054932 | -0.091553 | 121.7056 | 121.7056 | 117.8558 | -121.6232 | 121.6232 | 121.6644 | 121.637 | -121.8796
452.6719 | 121.8613 | -121.55 | 0.14648 | 0.0097657 | 0.013836 | 0.06884 | 0.0075581 | 0.065516 | -0.0021875 | -0.0025122 | 0.0035858 | -0.0064771 | 0.063497 | 0.064536 | 0.0012689 | -0.0061972 | 0.082397 | -120.8588 | -3.7628 | -121.3394 | 0.13275 | -121.637 | -121.4767 | -122.0856 | 0.004578 | -121.7102 | 0.082397 | 0.1236 | -121.5591 | -121.7331 | -0.086975 | 0.073242 | -0.013733 | 0.69122 | 0.21057 | 0.13733 | -0.064087 | -0.009155 | -0.1831 | -0.064087 | -0.53558 | -0.16022 | 0.022888 | -0.022888 | 121.6827 | 121.6324 | 117.7872 | -121.6232 | 121.6324 | 121.6736 | 121.5546 | -121.8796
454.4062 | 121.7972 | -121.5866 | 0.1831 | -0.013122 | 0.014691 | 0.066917 | 0.0017901 | 0.067225 | -0.0013329 | -0.0012306 | -0.019302 | -0.0062635 | 0.061361 | 0.065176 | 0.0038325 | -0.0087606 | 0.14191 | -120.8359 | -3.7308 | -121.3165 | 0.10529 | -121.6095 | -121.4355 | -121.9894 | 0.036621 | -121.6278 | 0.041199 | 0.082397 | -121.5179 | -121.701 | -0.022888 | 0.15106 | -0.077819 | 0.75073 | 0.27008 | 0.11902 | -0.041198 | 0.068665 | -0.11444 | -0.14191 | -0.40283 | -0.041199 | 0.073242 | -0.10071 | 121.6919 | 121.7285 | 117.8558 | -121.6187 | 121.6278 | 121.669 | 121.6232 | -121.8842
456.1562 | 121.7606 | -121.5866 | 0.19226 | -0.013122 | 0.013623 | 0.069908 | 0.0028583 | 0.067225 | -0.0045373 | -0.002085 | -0.011673 | -0.0081861 | 0.060934 | 0.063681 | 0.0023371 | -0.0047018 | 0.11444 | -120.8633 | -3.772 | -121.3577 | 0.12817 | -121.6003 | -121.4767 | -122.0535 | -0.004578 | -121.6736 | 0.027466 | 0.091553 | -121.5225 | -121.701 | -0.013733 | 0.10986 | -0.064087 | 0.72327 | 0.22888 | 0.11902 | -0.07782 | 0.064087 | -0.11444 | -0.16479 | -0.46692 | -0.086975 | 0.027466 | -0.10071 | 121.7148 | 121.701 | 117.8146 | -121.669 | 121.6141 | 121.6782 | 121.582 | -121.8933
457.9062 | 121.8338 | -121.5729 | 0.16479 | -0.0054933 | 0.012555 | 0.067345 | 0.0024311 | 0.065089 | -0.00090574 | -0.0010168 | -0.011673 | -0.0064771 | 0.061148 | 0.063895 | 0.0031915 | -0.0083334 | 0.10986 | -120.8725 | -3.7811 | -121.3394 | 0.15106 | -121.6278 | -121.4676 | -121.9803 | 0.018311 | -121.6599 | 0.041199 | 0.082397 | -121.4996 | -121.6919 | -0.054932 | 0.10529 | -0.013733 | 0.70038 | 0.23346 | 0.12817 | -0.054932 | 0.073242 | -0.11902 | -0.1236 | -0.40741 | -0.086975 | 0.032044 | -0.082398 | 121.7239 | 121.6827 | 117.7917 | -121.6324 | 121.6141 | 121.6553 | 121.5912 | -121.8567
459.5938 | 121.7789 | -121.5866 | 0.17395 | -0.0054933 | 0.0097776 | 0.069267 | 0.0030719 | 0.065516 | 0.00016226 | -0.002085 | 0.0035858 | -0.0075451 | 0.062216 | 0.064749 | 0.0038325 | -0.0070516 | 0.14191 | -120.8221 | -3.7537 | -121.3303 | 0.10529 | -121.6003 | -121.4676 | -121.9986 | 0.032043 | -121.6599 | 0.045776 | 0.086975 | -121.4951 | -121.6873 | -0.013733 | 0.11902 | -0.068664 | 0.76447 | 0.25635 | 0.13733 | -0.032043 | 0.091553 | -0.10071 | -0.12817 | -0.41199 | -0.073242 | 0.027466 | -0.086975 | 121.6919 | 121.7285 | 117.8329 | -121.6415 | 121.6324 | 121.6736 | 121.6187 | -121.8613
461.3438 | 121.843 | -121.5729 | 0.16479 | -0.013122 | 0.013196 | 0.068413 | 0.0058491 | 0.065089 | -0.0015465 | -0.0029394 | -0.0040437 | -0.0069043 | 0.061575 | 0.065176 | 0.0029779 | -0.0061972 | 0.059509 | -120.9 | -3.8361 | -121.3669 | 0.12817 | -121.6507 | -121.4813 | -122.081 | -0.013733 | -121.6827 | 0.045776 | 0.09613 | -121.5363 | -121.7239 | -0.07782 | 0.091553 | -0.036621 | 0.67291 | 0.20599 | 0.11444 | -0.10529 | 0.036621 | -0.15106 | -0.11902 | -0.50812 | -0.10986 | 0.041199 | -0.068665 | 121.701 | 121.6324 | 117.7368 | -121.6461 | 121.6187 | 121.669 | 121.5591 | -121.8887
463.0156 | 121.9116 | -121.5408 | 0.13733 | -0.013122 | 0.0117 | 0.070976 | 0.0052081 | 0.064448 | -0.0019739 | -0.0035804 | -0.011673 | -0.0073315 | 0.060934 | 0.063681 | 0.0016963 | -0.0064108 | 0.15564 | -120.8084 | -3.7445 | -121.3303 | 0.11902 | -121.6141 | -121.4722 | -121.9986 | 0.09613 | -121.6049 | 0.054932 | 0.068665 | -121.5179 | -121.7148 | -0.073242 | 0.068665 | -0.01831 | 0.73242 | 0.21057 | 0.14191 | 0.018311 | 0.022889 | -0.17395 | -0.082397 | -0.45776 | -0.064086 | 0.10986 | -0.068664 | 121.6599 | 121.6965 | 117.7963 | -121.6095 | 121.5958 | 121.6095 | 121.637 | -121.8521
464.75 | 121.7743 | -121.5729 | 0.18768 | -0.013122 | 0.009564 | 0.067772 | 0.0011493 | 0.06808 | 0.0018713 | -0.0014442 | -0.0040437 | -0.0058361 | 0.061148 | 0.062399 | 0.0057551 | -0.0070516 | 0.14648 | -120.8313 | -3.7628 | -121.3394 | 0.10529 | -121.6187 | -121.4767 | -121.9894 | 0.041199 | -121.6507 | 0.036621 | 0.059509 | -121.5271 | -121.7102 | -0.045776 | 0.09613 | -0.082397 | 0.74158 | 0.23346 | 0.13733 | -0.041199 | 0.045776 | -0.13733 | -0.15106 | -0.41657 | -0.07782 | 0.059509 | -0.12817 | 121.6782 | 121.7194 | 117.8101 | -121.6644 | 121.6095 | 121.6324 | 121.6141 | -121.8979
466.4844 | 121.8521 | -121.6187 | 0.16022 | 0.0021362 | 0.0099912 | 0.068626 | 0.0039265 | 0.064448 | -0.0021875 | -0.0027258 | 0.0035858 | -0.0077587 | 0.059011 | 0.062186 | 0.0010553 | -0.008547 | 0.073242 | -120.8862 | -3.8086 | -121.3669 | 0.12817 | -121.6095 | -121.4447 | -122.0398 | 0.036621 | -121.6644 | 0.054932 | 0.082397 | -121.5271 | -121.7148 | 0.009155 | 0.17395 | -0.032043 | 0.73242 | 0.25177 | 0.07782 | -0.086975 | 0.091552 | -0.096131 | -0.10528 | -0.42114 | -0.045777 | 0.050354 | -0.07782 | 121.7468 | 121.6919 | 117.8101 | -121.6049 | 121.6736 | 121.701 | 121.6553 | -121.875
468.1719 | 121.875 | -121.5637 | 0.13275 | 0.0021362 | 0.010205 | 0.069908 | 0.0067035 | 0.064021 | -0.0024011 | -0.0048622 | -0.019302 | -0.0073315 | 0.061148 | 0.066458 | 0.0027643 | -0.007479 | 0.10986 | -120.8725 | -3.8132 | -121.3486 | 0.14648 | -121.6324 | -121.4813 | -122.0352 | 0.059509 | -121.6599 | 0.036621 | 0.09613 | -121.5454 | -121.7331 | -0.068664 | 0.082398 | 0.013733 | 0.69122 | 0.21515 | 0.13275 | -0.022888 | 0.018311 | -0.16937 | -0.09613 | -0.4715 | -0.09613 | 0.073242 | -0.036621 | 121.7102 | 121.6736 | 117.7506 | -121.6141 | 121.6003 | 121.6599 | 121.6232 | -121.8658
469.8906 | 121.8658 | -121.5683 | 0.15106 | -0.013122 | 0.016186 | 0.065636 | 0.0054217 | 0.06573 | 0.0084937 | -0.0014442 | -0.011673 | -0.0024183 | 0.063284 | 0.067313 | 0.0049005 | -0.0091878 | 0.11444 | -120.9137 | -3.7765 | -121.3943 | 0.14648 | -121.669 | -121.5179 | -122.0352 | 0.018311 | -121.7468 | 0.050354 | 0.086975 | -121.6049 | -121.7331 | -0.10071 | 0.050354 | -0.004578 | 0.6546 | 0.17395 | 0.1236 | -0.036621 | -0.036621 | -0.16479 | -0.10071 | -0.46692 | -0.17853 | -0.013733 | -0.064087 | 121.7148 | 121.6827 | 117.7917 | -121.669 | 121.6187 | 121.6553 | 121.5866 | -121.8842
471.5781 | 121.7606 | -121.6095 | 0.16937 | -0.013122 | 0.012127 | 0.068199 | 0.0030719 | 0.066371 | -0.0024011 | -0.0018714 | -0.011673 | -0.0071179 | 0.06072 | 0.066245 | 0.0051141 | -0.0091878 | 0.11902 | -120.845 | -3.7811 | -121.3669 | 0.1236 | -121.6461 | -121.4676 | -122.0169 | 0.022888 | -121.6599 | 0.032043 | 0.082397 | -121.55 | -121.7331 | -0.036621 | 0.14191 | -0.045777 | 0.76447 | 0.24262 | 0.10071 | -0.050354 | 0.059509 | -0.1236 | -0.13733 | -0.40741 | -0.050354 | 0.073242 | -0.086976 | 121.7331 | 121.7285 | 117.8284 | -121.637 | 121.6415 | 121.6919 | 121.6324 | -121.9025
473.25 | 121.8018 | -121.6049 | 0.17395 | -0.0054933 | 0.013623 | 0.068199 | 0.0011493 | 0.06338 | 0.0018713 | -0.00016236 | -0.0040437 | -0.0047681 | 0.05837 | 0.06304 | 0.0055415 | -0.0047018 | 0.14648 | -120.845 | -3.7811 | -121.3348 | 0.10529 | -121.637 | -121.4676 | -122.0078 | 0.054932 | -121.669 | 0.032043 | 0.073242 | -121.5363 | -121.7148 | -0.032044 | 0.13733 | -0.068664 | 0.75989 | 0.27008 | 0.13275 | -0.027466 | 0.068664 | -0.10986 | -0.14191 | -0.40283 | -0.064087 | 0.045777 | -0.10071 | 121.7102 | 121.7514 | 117.8238 | -121.6415 | 121.637 | 121.6782 | 121.6599 | -121.8887
474.9844 | 121.8521 | -121.5729 | 0.15106 | -0.013122 | 0.012341 | 0.068413 | 0.0071307 | 0.067011 | 0.00016226 | -0.0012306 | -0.011673 | -0.0071179 | 0.061148 | 0.064108 | 0.0010553 | -0.006838 | 0.068665 | -120.8862 | -3.8086 | -121.3943 | 0.14648 | -121.701 | -121.5363 | -122.113 | -0.004578 | -121.7697 | 0.068665 | 0.09613 | -121.6003 | -121.7514 | -0.12817 | 0.036621 | -0.004578 | 0.68665 | 0.17853 | 0.14191 | -0.082397 | -0.027466 | -0.17853 | -0.082397 | -0.54016 | -0.19684 | -0.01831 | -0.054932 | 121.7194 | 121.6415 | 117.7643 | -121.6873 | 121.6415 | 121.669 | 121.5683 | -121.9025
476.6562 | 121.8567 | -121.5775 | 0.16937 | 0.0021362 | 0.017041 | 0.064354 | 0.0067035 | 0.067011 | 0.0025123 | -0.0012306 | -0.019302 | -0.0043409 | 0.062216 | 0.066458 | 0.0061823 | -0.008547 | 0.082397 | -120.8954 | -3.7857 | -121.3943 | 0.13275 | -121.6553 | -121.5225 | -122.0673 | 0.018311 | -121.7514 | 0.054932 | 0.07782 | -121.5775 | -121.756 | -0.077819 | 0.054932 | -0.036622 | 0.68207 | 0.18311 | 0.12817 | -0.086976 | 0 | -0.17853 | -0.11444 | -0.48981 | -0.17395 | 0.004577 | -0.091553 | 121.7102 | 121.6599 | 117.7917 | -121.6919 | 121.6324 | 121.6553 | 121.5958 | -121.9254
478.3906 | 121.7972 | -121.6003 | 0.1831 | -0.013122 | 0.017041 | 0.066277 | 0.00093567 | 0.067225 | 0.0040077 | -0.0010168 | -0.0040437 | -0.0036999 | 0.063711 | 0.066245 | 0.0061823 | -0.006838 | 0.004578 | -121.0144 | -3.9093 | -121.431 | 0.17395 | -121.701 | -121.5408 | -122.1176 | -0.09613 | -121.8201 | 0.082397 | 0.12817 | -121.5912 | -121.7789 | -0.10071 | 0.059509 | -0.009155 | 0.58594 | 0.16937 | 0.10986 | -0.17853 | 0.009155 | -0.17853 | -0.10071 | -0.51727 | -0.21973 | -0.041198 | -0.054931 | 121.7743 | 121.6049 | 117.691 | -121.7239 | 121.6827 | 121.7285 | 121.5042 | -121.962
480.125 | 121.8201 | -121.6095 | 0.17853 | -0.013122 | 0.015332 | 0.064781 | 0.0049945 | 0.067652 | 0.0020849 | 0.0026148 | -0.019302 | -0.0026319 | 0.064138 | 0.065817 | 0.0055415 | -0.0070516 | 0.064087 | -120.9366 | -3.8223 | -121.4081 | 0.15564 | -121.6873 | -121.5042 | -122.0901 | -0.013733 | -121.7743 | 0.073242 | 0.09613 | -121.5958 | -121.7789 | -0.07782 | 0.10529 | -0.022888 | 0.67291 | 0.20142 | 0.09613 | -0.11444 | 0.013733 | -0.16937 | -0.10529 | -0.48065 | -0.16479 | 0.004578 | -0.082398 | 121.7651 | 121.6736 | 117.7872 | -121.6827 | 121.6827 | 121.7056 | 121.5958 | -121.9574
481.875 | 121.7926 | -121.6095 | 0.16937 | 0.0021362 | 0.012127 | 0.069054 | 0.0056355 | 0.066371 | -0.0058191 | -0.0022986 | -0.019302 | -0.0077587 | 0.061575 | 0.06539 | -0.0012945 | -0.0066244 | 0.068665 | -120.8908 | -3.8589 | -121.3806 | 0.10071 | -121.6507 | -121.4813 | -122.1039 | 0 | -121.7102 | 0.022888 | 0.082397 | -121.5683 | -121.7514 | -0.041199 | 0.12817 | -0.068665 | 0.71869 | 0.22888 | 0.10071 | -0.10071 | 0.041199 | -0.14191 | -0.14649 | -0.49438 | -0.10071 | 0.041199 | -0.086976 | 121.7102 | 121.6782 | 117.7505 | -121.6507 | 121.6324 | 121.6919 | 121.6095 | -121.9208
483.5625 | 121.9299 | -121.5546 | 0.14648 | -0.020752 | 0.0099912 | 0.068626 | 0.0043537 | 0.067866 | -0.0036829 | -0.0029394 | -0.011673 | -0.0073315 | 0.059652 | 0.064108 | -1.2744e-05 | -0.0053426 | 0.07782 | -120.8679 | -3.7949 | -121.3669 | 0.13275 | -121.6599 | -121.4905 | -122.0581 | 0.086975 | -121.6553 | 0.041199 | 0.073242 | -121.5637 | -121.7377 | -0.10529 | 0.064086 | -0.013733 | 0.68664 | 0.18768 | 0.1236 | -0.068664 | -0.009156 | -0.18311 | -0.10529 | -0.50354 | -0.10071 | 0.082398 | -0.073242 | 121.6873 | 121.6324 | 117.7597 | -121.637 | 121.5958 | 121.6278 | 121.6415 | -121.8842
485.2969 | 121.843 | -121.6003 | 0.16479 | -0.013122 | 0.01405 | 0.065636 | 0.0022175 | 0.066798 | 0.0022987 | -0.0027258 | -0.0040437 | -0.0022045 | 0.063497 | 0.065604 | 0.0076777 | -0.0072652 | 0.032043 | -121.0144 | -3.9093 | -121.4447 | 0.17395 | -121.6736 | -121.5317 | -122.1313 | -0.09613 | -121.8201 | 0.07782 | 0.10071 | -121.6141 | -121.7651 | -0.073242 | 0.068665 | 0.009155 | 0.58594 | 0.15564 | 0.086975 | -0.13275 | -0.013733 | -0.16479 | -0.086975 | -0.53101 | -0.21973 | -0.054931 | -0.064087 | 121.7743 | 121.6324 | 117.691 | -121.6965 | 121.6782 | 121.701 | 121.5042 | -121.9299
487.0312 | 121.8018 | -121.6187 | 0.15564 | -0.013122 | 0.007214 | 0.070122 | 0.0028583 | 0.065516 | -0.0034691 | -0.002085 | -0.011673 | -0.0054089 | 0.060507 | 0.06539 | 0.0027643 | -0.0066244 | 0.082397 | -120.8954 | -3.8223 | -121.3852 | 0.1236 | -121.669 | -121.5042 | -122.1039 | 0.009155 | -121.7056 | 0.059509 | 0.082397 | -121.5958 | -121.7422 | -0.050354 | 0.11444 | -0.032044 | 0.72327 | 0.23346 | 0.11902 | -0.073243 | 0.022888 | -0.1236 | -0.096131 | -0.48523 | -0.086975 | 0.036622 | -0.073243 | 121.7422 | 121.701 | 117.7963 | -121.6599 | 121.6782 | 121.701 | 121.6278 | -121.8979
488.7031 | 121.9254 | -121.5683 | 0.14191 | -0.020752 | 0.010205 | 0.067986 | 0.0049945 | 0.067439 | -0.0041101 | -0.0040076 | -0.0040437 | -0.0071179 | 0.060934 | 0.063467 | 0.00020086 | -0.0061972 | 0.073242 | -120.9091 | -3.8406 | -121.3898 | 0.14648 | -121.6736 | -121.5363 | -122.081 | 0.022888 | -121.6827 | 0.054932 | 0.091553 | -121.5637 | -121.7331 | -0.10529 | 0.032043 | 0.004577 | 0.65918 | 0.17853 | 0.14648 | -0.068665 | 0.004577 | -0.16479 | -0.086975 | -0.5127 | -0.11444 | 0.050354 | -0.050354 | 121.7148 | 121.6415 | 117.7277 | -121.6782 | 121.6232 | 121.6599 | 121.5912 | -121.875
490.4375 | 121.9299 | -121.582 | 0.15564 | -0.013122 | 0.012555 | 0.067986 | 0.0054217 | 0.065302 | -0.0028283 | -0.0063574 | -0.0040437 | -0.0073315 | 0.05837 | 0.064108 | 0.0012689 | -0.007479 | 0.15564 | -120.8267 | -3.7903 | -121.3486 | 0.10529 | -121.637 | -121.5088 | -122.0352 | 0.086975 | -121.6232 | 0.045776 | 0.082397 | -121.5591 | -121.7148 | -0.054932 | 0.073242 | -0.050354 | 0.75531 | 0.23346 | 0.16022 | 0 | 0.022888 | -0.13275 | -0.10986 | -0.45319 | -0.041199 | 0.091553 | -0.073243 | 121.6873 | 121.7377 | 117.7917 | -121.6644 | 121.6278 | 121.6644 | 121.669 | -121.8704
492.1094 | 121.8063 | -121.6187 | 0.20142 | -0.0054933 | 0.016613 | 0.065636 | 0.0017901 | 0.066584 | 0.0044349 | -0.0014442 | -0.0040437 | -0.0028455 | 0.063284 | 0.066031 | 0.0053279 | -0.0087606 | 0.10986 | -120.9457 | -3.8452 | -121.4081 | 0.14648 | -121.669 | -121.5225 | -122.0901 | -0.027466 | -121.788 | 0.054932 | 0.11444 | -121.6141 | -121.7834 | -0.050354 | 0.09613 | -0.054932 | 0.67291 | 0.21057 | 0.11444 | -0.091553 | 0.004577 | -0.16479 | -0.14648 | -0.4715 | -0.16937 | -0.004578 | -0.086975 | 121.7651 | 121.7285 | 117.7734 | -121.7239 | 121.6736 | 121.7331 | 121.5912 | -121.9849
493.8438 | 121.8292 | -121.6187 | 0.16937 | -0.0054933 | 0.011273 | 0.068626 | 0.0041401 | 0.067225 | -0.0021875 | -0.0018714 | 0.0035858 | -0.0077587 | 0.061361 | 0.06539 | 0.00062806 | -0.006838 | 0.068665 | -120.9137 | -3.8635 | -121.3989 | 0.1236 | -121.669 | -121.5088 | -122.1085 | -0.032043 | -121.7194 | 0.045776 | 0.10071 | -121.5958 | -121.7377 | -0.050354 | 0.10986 | -0.045777 | 0.70496 | 0.21973 | 0.10986 | -0.10071 | 0.022888 | -0.11902 | -0.1236 | -0.48981 | -0.10071 | 0.018311 | -0.068665 | 121.7422 | 121.6873 | 117.7551 | -121.6782 | 121.6644 | 121.7194 | 121.5866 | -121.907
495.5938 | 121.8384 | -121.6324 | 0.15106 | -0.013122 | 0.012555 | 0.065422 | 0.0047809 | 0.065943 | 0.0037939 | 0.00090584 | 0.0035858 | -0.0032727 | 0.062002 | 0.065176 | 0.0055415 | -0.0083334 | 0.027466 | -121.0327 | -3.9139 | -121.4722 | 0.16479 | -121.7056 | -121.5454 | -122.1405 | -0.09613 | -121.8338 | 0.091553 | 0.10986 | -121.6232 | -121.788 | -0.073242 | 0.086975 | 0.013733 | 0.59967 | 0.16022 | 0.073242 | -0.1236 | 0.009155 | -0.15564 | -0.059509 | -0.50812 | -0.20142 | -0.045776 | -0.041199 | 121.7972 | 121.6599 | 117.7185 | -121.6965 | 121.7239 | 121.7422 | 121.5363 | -121.9391
497.2812 | 121.9391 | -121.582 | 0.14648 | -0.0054933 | 0.013196 | 0.06649 | 0.0069171 | 0.067011 | -0.0041101 | -0.0029394 | -0.0040437 | -0.0077587 | 0.06307 | 0.064322 | 0.00062806 | -0.0049154 | 0.10986 | -120.8633 | -3.7994 | -121.3669 | 0.13275 | -121.6415 | -121.4951 | -122.0581 | 0.082397 | -121.637 | 0.036621 | 0.073242 | -121.5775 | -121.7651 | -0.05951 | 0.086975 | -0.013733 | 0.71869 | 0.21515 | 0.12817 | -0.036621 | 0.004577 | -0.18311 | -0.10986 | -0.47607 | -0.054932 | 0.12817 | -0.073242 | 121.7148 | 121.6919 | 117.7826 | -121.6415 | 121.6187 | 121.6553 | 121.6644 | -121.9116
499.0156 | 121.8201 | -121.6049 | 0.17395 | -0.013122 | 0.0082822 | 0.070335 | 0.0032855 | 0.065302 | -0.0030419 | -0.0025122 | -0.011673 | -0.0083997 | 0.058584 | 0.066458 | 0.0040461 | -0.0066244 | 0.10071 | -120.8862 | -3.8635 | -121.3898 | 0.13275 | -121.6507 | -121.5088 | -122.1039 | -0.004578 | -121.7148 | 0.050354 | 0.073242 | -121.6003 | -121.7377 | -0.045777 | 0.09613 | -0.041199 | 0.71869 | 0.21515 | 0.11902 | -0.073242 | 0.004577 | -0.13275 | -0.1236 | -0.49896 | -0.10986 | 0.022888 | -0.10071 | 121.7377 | 121.7056 | 117.7414 | -121.6827 | 121.6553 | 121.6782 | 121.6003 | -121.9116
500.7656 | 121.9437 | -121.582 | 0.13733 | -0.0054933 | 0.012768 | 0.071617 | 0.0030719 | 0.068934 | -0.0036829 | -0.0027258 | 0.0035858 | -0.0086133 | 0.059866 | 0.06304 | 0.0031915 | -0.0079062 | 0.16479 | -120.8359 | -3.7765 | -121.3577 | 0.1236 | -121.6507 | -121.4767 | -122.0398 | 0.10986 | -121.6599 | 0.036621 | 0.064087 | -121.5683 | -121.7468 | -0.068665 | 0.10528 | -0.013733 | 0.74616 | 0.2243 | 0.11902 | 0.027466 | 0.013733 | -0.16479 | -0.10071 | -0.45776 | -0.07782 | 0.086975 | -0.073242 | 121.7056 | 121.7468 | 117.8055 | -121.6141 | 121.6187 | 121.6461 | 121.6919 | -121.8842
502.4531 | 121.9391 | -121.5683 | 0.14191 | -0.013122 | 0.014691 | 0.065849 | 0.0026447 | 0.064234 | 0.0035803 | 0.00090584 | -0.0040437 | -0.0039135 | 0.062856 | 0.063254 | 0.0076777 | -0.0083334 | 0.082397 | -120.9229 | -3.8452 | -121.4035 | 0.16022 | -121.6965 | -121.55 | -122.0764 | 0.013733 | -121.7514 | 0.059509 | 0.091553 | -121.6232 | -121.788 | -0.12817 | 0.01831 | 0.01831 | 0.64545 | 0.16479 | 0.14648 | -0.05951 | -0.054932 | -0.21973 | -0.082398 | -0.50812 | -0.18311 | 0.036621 | -0.050354 | 121.7285 | 121.6507 | 117.7231 | -121.6919 | 121.6278 | 121.6599 | 121.582 | -121.9299
504.1875 | 121.8658 | -121.5912 | 0.16022 | -0.013122 | 0.0117 | 0.068626 | 0.0041401 | 0.064234 | -0.0051781 | -0.0012306 | -0.011673 | -0.0064771 | 0.059011 | 0.064749 | 0.0010553 | -0.0064108 | 0.054932 | -120.9183 | -3.8864 | -121.4127 | 0.12817 | -121.6553 | -121.5179 | -122.1039 | -0.018311 | -121.7285 | 0.045776 | 0.10529 | -121.582 | -121.7377 | -0.064086 | 0.073243 | -0.032043 | 0.67291 | 0.17853 | 0.10528 | -0.10528 | 0.009156 | -0.14648 | -0.11444 | -0.51269 | -0.13733 | 0.009155 | -0.054931 | 121.7194 | 121.6461 | 117.7048 | -121.6782 | 121.637 | 121.6965 | 121.5729 | -121.8979
505.9375 | 121.8658 | -121.582 | 0.15564 | 0.0021362 | 0.01405 | 0.068199 | 0.0011493 | 0.066157 | 0.0020849 | -0.0012306 | -0.019302 | -0.0051953 | 0.06072 | 0.066031 | 0.0066095 | -0.0087606 | 0.13275 | -120.8954 | -3.8361 | -121.3715 | 0.11902 | -121.6553 | -121.5363 | -122.0261 | 0.032043 | -121.701 | 0.018311 | 0.064087 | -121.5912 | -121.7422 | -0.073242 | 0.045776 | -0.036621 | 0.68664 | 0.21057 | 0.16479 | -0.022889 | -0.009156 | -0.16022 | -0.13733 | -0.44403 | -0.11902 | 0.041199 | -0.091553 | 121.701 | 121.7148 | 117.746 | -121.6919 | 121.6003 | 121.6461 | 121.6141 | -121.8979
507.6094 | 121.9666 | -121.5729 | 0.14191 | -0.0054933 | 0.019818 | 0.067131 | 0.0062763 | 0.067439 | 0.0016577 | -0.0022986 | -0.0040437 | -0.0058361 | 0.065206 | 0.063895 | 0.0042597 | -0.0072652 | 0.059509 | -121.0007 | -3.8956 | -121.4401 | 0.16937 | -121.6919 | -121.5637 | -122.1176 | -0.009155 | -121.7743 | 0.059509 | 0.10986 | -121.6278 | -121.7789 | -0.11902 | 0.009155 | 0.027466 | 0.5722 | 0.13275 | 0.1236 | -0.082398 | -0.054932 | -0.20599 | -0.082398 | -0.54474 | -0.20142 | 0.004578 | -0.032044 | 121.7422 | 121.6324 | 117.6773 | -121.7056 | 121.6324 | 121.6827 | 121.5637 | -121.9208
509.3438 | 121.9299 | -121.5958 | 0.12817 | -0.013122 | 0.013623 | 0.067986 | 0.0071307 | 0.067866 | -0.0036829 | -0.0033668 | -0.011673 | -0.010322 | 0.061575 | 0.065604 | 0.0019099 | -0.0055564 | 0.13275 | -120.8313 | -3.8132 | -121.3531 | 0.13733 | -121.6644 | -121.5271 | -122.049 | 0.10529 | -121.669 | 0.027466 | 0.068665 | -121.5866 | -121.7468 | -0.068665 | 0.068664 | 0.009155 | 0.76447 | 0.24262 | 0.17395 | 0.004577 | 0.009155 | -0.15106 | -0.10071 | -0.45319 | -0.073242 | 0.07782 | -0.059509 | 121.7331 | 121.7285 | 117.7826 | -121.6553 | 121.6232 | 121.6644 | 121.7011 | -121.875
511.0781 | 121.9162 | -121.6095 | 0.16479 | -0.0054933 | 0.016613 | 0.06649 | 0.0056355 | 0.067439 | -0.0021875 | -0.00080316 | -0.0040437 | -0.0071179 | 0.062429 | 0.066885 | 0.0038325 | -0.0070516 | 0.12817 | -120.8679 | -3.8177 | -121.376 | 0.11902 | -121.669 | -121.5088 | -122.0856 | 0.082397 | -121.7148 | 0.032043 | 0.086975 | -121.6095 | -121.7606 | -0.059509 | 0.10071 | -0.045776 | 0.74158 | 0.23346 | 0.13275 | -0.036621 | 0 | -0.15106 | -0.13275 | -0.47607 | -0.10529 | 0.045776 | -0.07782 | 121.7285 | 121.7377 | 117.7917 | -121.6736 | 121.6415 | 121.6965 | 121.6919 | -121.9254
512.8281 | 121.7972 | -121.6141 | 0.16022 | -0.013122 | 0.013836 | 0.067772 | 0.0037127 | 0.068293 | -0.0032555 | -0.002085 | 0.011215 | -0.0086133 | 0.060934 | 0.066245 | 0.0046869 | -0.0070516 | 0.09613 | -120.8817 | -3.8589 | -121.3898 | 0.11902 | -121.6553 | -121.4996 | -122.0627 | 0.027466 | -121.6965 | 0.054932 | 0.07782 | -121.5958 | -121.7422 | -0.041198 | 0.11444 | -0.041198 | 0.73242 | 0.2243 | 0.10986 | -0.064087 | 0.018311 | -0.12817 | -0.10528 | -0.44861 | -0.082397 | 0.045777 | -0.082397 | 121.7331 | 121.7102 | 117.7551 | -121.6599 | 121.669 | 121.6919 | 121.6415 | -121.9025
514.5156 | 121.875 | -121.6049 | 0.15106 | -0.0054933 | 0.014691 | 0.065422 | 0.0026447 | 0.066371 | 0.0033667 | -0.00058956 | -0.0040437 | -0.0058361 | 0.058157 | 0.064322 | 0.0063959 | -0.0091878 | 0.13733 | -120.8954 | -3.8498 | -121.3852 | 0.12817 | -121.6782 | -121.4996 | -122.0444 | 0.018311 | -121.6919 | 0.032043 | 0.068665 | -121.6003 | -121.7468 | -0.073243 | 0.10528 | -0.022888 | 0.70953 | 0.21973 | 0.11444 | -0.013733 | 0.004577 | -0.14191 | -0.11902 | -0.43945 | -0.086976 | 0.054931 | -0.082397 | 121.7331 | 121.7422 | 117.7551 | -121.6507 | 121.637 | 121.6736 | 121.6232 | -121.8979
516.25 | 121.8658 | -121.6141 | 0.16022 | -0.020752 | 0.014691 | 0.067772 | 0.0017901 | 0.064875 | 0.0025123 | -0.00080316 | 0.0035858 | -0.0054089 | 0.058157 | 0.066031 | 0.0059687 | -0.006838 | 0.054932 | -120.9824 | -3.9322 | -121.4539 | 0.15106 | -121.6736 | -121.5179 | -122.1039 | -0.054932 | -121.7789 | 0.054932 | 0.10529 | -121.6232 | -121.7743 | -0.059509 | 0.096131 | -0.009155 | 0.63171 | 0.16022 | 0.064087 | -0.10528 | -0.009155 | -0.16022 | -0.10528 | -0.48981 | -0.16479 | -0.004578 | -0.054931 | 121.7651 | 121.669 | 117.6819 | -121.6782 | 121.669 | 121.7194 | 121.5591 | -121.9345
518 | 121.8933 | -121.6095 | 0.14191 | 0.0021362 | 0.015545 | 0.067772 | 0.0047809 | 0.064021 | -0.0028283 | -0.0022986 | -0.0040437 | -0.0090405 | 0.062002 | 0.063467 | 0.0036189 | -0.0079062 | 0.10986 | -120.8862 | -3.8406 | -121.3806 | 0.11902 | -121.6644 | -121.5271 | -122.1039 | 0.045776 | -121.7331 | 0.054932 | 0.10529 | -121.6141 | -121.788 | -0.054932 | 0.082397 | -0.022888 | 0.72327 | 0.22888 | 0.14648 | -0.032044 | -0.004578 | -0.17853 | -0.086975 | -0.49438 | -0.1236 | 0.054932 | -0.036621 | 121.7285 | 121.7194 | 117.7689 | -121.669 | 121.6644 | 121.7148 | 121.6553 | -121.9299
519.6719 | 121.907 | -121.6003 | 0.14648 | -0.020752 | 0.0099912 | 0.069481 | 0.0045673 | 0.067225 | -0.0041101 | -0.0025122 | -0.0040437 | -0.0064771 | 0.060079 | 0.064963 | 0.0019099 | -0.0081198 | 0.13733 | -120.8221 | -3.8132 | -121.3531 | 0.12817 | -121.6324 | -121.5042 | -122.049 | 0.10529 | -121.6644 | 0.027466 | 0.086975 | -121.5912 | -121.7651 | -0.032043 | 0.096131 | -0.01831 | 0.7782 | 0.24719 | 0.15106 | -0.009155 | 0.009155 | -0.16479 | -0.11902 | -0.44861 | -0.064087 | 0.10071 | -0.059509 | 121.7285 | 121.7377 | 117.7872 | -121.6507 | 121.6278 | 121.6873 | 121.7056 | -121.9116
521.4062 | 121.9482 | -121.5591 | 0.12817 | -0.013122 | 0.012982 | 0.067986 | 0.0075581 | 0.065302 | -0.0032555 | -0.0046484 | -0.011673 | -0.0060497 | 0.059439 | 0.064108 | 0.0014825 | -0.0070516 | 0.14191 | -120.845 | -3.8452 | -121.3577 | 0.13275 | -121.6461 | -121.5088 | -122.0398 | 0.086975 | -121.6461 | 0.041199 | 0.07782 | -121.55 | -121.7468 | -0.086975 | 0.050354 | 0.004577 | 0.71411 | 0.20142 | 0.15106 | 0.013733 | 0.009155 | -0.18768 | -0.086975 | -0.48065 | -0.086975 | 0.10071 | -0.050354 | 121.6919 | 121.7011 | 117.7139 | -121.637 | 121.6003 | 121.637 | 121.6461 | -121.875
523.1562 | 121.9574 | -121.5683 | 0.13733 | -0.020752 | 0.015332 | 0.067345 | 0.0039265 | 0.065302 | 0.0033667 | -0.0029394 | -0.019302 | -0.0015637 | 0.060293 | 0.06774 | 0.0031915 | -0.007479 | 0.045776 | -121.0052 | -3.9276 | -121.4355 | 0.16479 | -121.6965 | -121.5408 | -122.1313 | -0.022888 | -121.7926 | 0.073242 | 0.10986 | -121.6141 | -121.7651 | -0.12817 | 0.027465 | 0.027466 | 0.56305 | 0.13275 | 0.10529 | -0.091553 | -0.045777 | -0.19684 | -0.064087 | -0.56305 | -0.22431 | -0.027466 | -0.027466 | 121.7331 | 121.6141 | 117.6407 | -121.6782 | 121.6415 | 121.6782 | 121.5454 | -121.9025
524.8906 | 121.8933 | -121.6049 | 0.15564 | -0.0054933 | 0.015118 | 0.06884 | 0.0067035 | 0.064662 | -0.00047854 | 5.1244e-05 | -0.011673 | -0.0086133 | 0.064138 | 0.064108 | 0.0029779 | -0.006838 | 0.11902 | -120.8633 | -3.8315 | -121.3806 | 0.13275 | -121.6415 | -121.5363 | -122.0764 | 0.082397 | -121.6873 | 0.036621 | 0.07782 | -121.6049 | -121.756 | -0.036622 | 0.068664 | -0.022889 | 0.74158 | 0.2243 | 0.15564 | -0.036621 | 0 | -0.15106 | -0.11902 | -0.4715 | -0.082398 | 0.068664 | -0.07782 | 121.7377 | 121.7239 | 117.7734 | -121.6919 | 121.6415 | 121.6827 | 121.6873 | -121.9116
526.5625 | 121.9345 | -121.5454 | 0.12817 | -0.013122 | 0.012982 | 0.069267 | 0.0067035 | 0.064875 | -0.0034691 | -0.00080316 | -0.0040437 | -0.0088269 | 0.059866 | 0.064749 | 0.0016963 | -0.0087606 | 0.13275 | -120.8176 | -3.8223 | -121.3531 | 0.11902 | -121.6507 | -121.5225 | -122.049 | 0.09613 | -121.6599 | 0.032043 | 0.091553 | -121.6049 | -121.7468 | -0.10529 | 0.022888 | -0.009155 | 0.72784 | 0.19226 | 0.16937 | 0.004577 | -0.059509 | -0.20142 | -0.096131 | -0.50354 | -0.11444 | 0.086975 | -0.036621 | 121.6644 | 121.6782 | 117.7231 | -121.6507 | 121.5775 | 121.637 | 121.6415 | -121.875
528.3125 | 121.8201 | -121.6324 | 0.1831 | -0.020752 | 0.015332 | 0.064995 | 0.0024311 | 0.064875 | 0.0063575 | -0.00080316 | -0.011673 | -0.0032727 | 0.062856 | 0.06539 | 0.0068231 | -0.007479 | 0.041199 | -121.0052 | -3.9551 | -121.4539 | 0.15564 | -121.6736 | -121.5637 | -122.1634 | -0.082397 | -121.8521 | 0.082397 | 0.10986 | -121.6415 | -121.7834 | -0.041199 | 0.068664 | -0.027465 | 0.62714 | 0.17853 | 0.10986 | -0.14191 | -0.009156 | -0.15106 | -0.10071 | -0.53101 | -0.21973 | -0.068665 | -0.073242 | 121.788 | 121.6736 | 117.6773 | -121.7468 | 121.7148 | 121.7422 | 121.55 | -121.9666
529.9844 | 121.8475 | -121.6415 | 0.16937 | -0.0054933 | 0.016186 | 0.067558 | 0.0028583 | 0.067866 | 0.0022987 | 0.00069204 | -0.0040437 | -0.0047681 | 0.062002 | 0.06539 | 0.0068231 | -0.0059836 | 0.018311 | -121.0144 | -3.9642 | -121.4539 | 0.15564 | -121.6782 | -121.5363 | -122.1542 | -0.091553 | -121.8246 | 0.07782 | 0.10529 | -121.6278 | -121.7651 | -0.036621 | 0.10529 | -0.013733 | 0.62714 | 0.18768 | 0.082398 | -0.15106 | 0.013733 | -0.1236 | -0.091553 | -0.51269 | -0.1831 | -0.059509 | -0.064087 | 121.7972 | 121.6599 | 117.6773 | -121.7056 | 121.7194 | 121.7468 | 121.55 | -121.9345
531.7188 | 121.8201 | -121.6415 | 0.1831 | -0.013122 | 0.017468 | 0.066917 | 0.0037127 | 0.067652 | 0.0044349 | -0.0010168 | -0.019302 | -0.0022045 | 0.061148 | 0.063681 | 0.0059687 | -0.0053426 | 0.009155 | -121.0144 | -3.9459 | -121.4767 | 0.15106 | -121.6827 | -121.55 | -122.1725 | -0.07782 | -121.8567 | 0.082397 | 0.12817 | -121.6278 | -121.8063 | -0.041198 | 0.091553 | -0.032043 | 0.62714 | 0.16479 | 0.073242 | -0.17395 | 0.013733 | -0.16479 | -0.10071 | -0.531 | -0.21515 | -0.050354 | -0.054931 | 121.7926 | 121.6507 | 117.6956 | -121.7331 | 121.7239 | 121.7697 | 121.5637 | -121.9894
533.4531 | 121.8201 | -121.6324 | 0.17853 | -0.013122 | 0.015973 | 0.067345 | 0.0039265 | 0.066798 | 0.0037939 | -0.00037596 | -0.0040437 | -0.0049817 | 0.062216 | 0.064536 | 0.0063959 | -0.0061972 | 0.032043 | -120.9686 | -3.923 | -121.4447 | 0.17395 | -121.6827 | -121.5775 | -122.1588 | -0.059509 | -121.8246 | 0.086975 | 0.1236 | -121.6049 | -121.788 | -0.050354 | 0.054931 | -0.004578 | 0.66376 | 0.18768 | 0.13275 | -0.14648 | 0.027466 | -0.15564 | -0.091553 | -0.52643 | -0.19226 | -0.036621 | -0.054932 | 121.8063 | 121.6644 | 117.7094 | -121.756 | 121.7194 | 121.756 | 121.5729 | -121.9666
535.125 | 121.8155 | -121.6232 | 0.1831 | -0.013122 | 0.015545 | 0.067131 | 0.0045673 | 0.067011 | 0.0012305 | 5.1244e-05 | -0.0040437 | -0.0051953 | 0.062002 | 0.064963 | 0.0051141 | -0.0059836 | 0 | -120.9915 | -3.9688 | -121.4264 | 0.16479 | -121.6599 | -121.5088 | -122.1588 | -0.091553 | -121.7834 | 0.073242 | 0.11444 | -121.6141 | -121.7514 | -0.036621 | 0.11444 | -0.01831 | 0.63171 | 0.19684 | 0.082397 | -0.1831 | 0.009155 | -0.12817 | -0.10986 | -0.53558 | -0.16022 | -0.032043 | -0.068664 | 121.788 | 121.6232 | 117.6544 | -121.6919 | 121.6965 | 121.7377 | 121.5317 | -121.9345
536.875 | 121.8246 | -121.6187 | 0.18768 | -0.013122 | 0.012127 | 0.068199 | 0.0034991 | 0.065302 | -0.0051781 | 0.00047844 | 0.011215 | -0.0073315 | 0.059439 | 0.062399 | 0.0044733 | -0.006838 | 0.10071 | -120.8542 | -3.8544 | -121.3669 | 0.13733 | -121.6599 | -121.4767 | -122.0444 | 0.041199 | -121.6736 | 0.036621 | 0.086975 | -121.582 | -121.7377 | -0.041199 | 0.14191 | -0.050354 | 0.76447 | 0.25177 | 0.10986 | -0.086975 | 0.036621 | -0.11902 | -0.15106 | -0.42572 | -0.054932 | 0.064087 | -0.10071 | 121.756 | 121.7194 | 117.7643 | -121.6644 | 121.6553 | 121.7056 | 121.6599 | -121.9254
538.5469 | 121.8201 | -121.6278 | 0.19684 | -0.013122 | 0.016186 | 0.066277 | 0.0013629 | 0.067652 | 0.0025123 | -0.00037596 | -0.011673 | -0.0022045 | 0.059866 | 0.06539 | 0.0061823 | -0.0047018 | 0.045776 | -120.9824 | -3.9368 | -121.431 | 0.16022 | -121.6599 | -121.55 | -122.1725 | -0.054932 | -121.8246 | 0.11444 | 0.11902 | -121.6095 | -121.7743 | -0.032043 | 0.07782 | -0.036621 | 0.64545 | 0.19684 | 0.11902 | -0.15106 | 0.018311 | -0.14648 | -0.082397 | -0.54474 | -0.19684 | -0.050354 | -0.077819 | 121.788 | 121.6736 | 117.691 | -121.7468 | 121.7422 | 121.7468 | 121.5729 | -121.9711
540.2812 | 121.9528 | -121.6003 | 0.13275 | -0.0054933 | 0.015759 | 0.067345 | 0.0081989 | 0.06338 | -0.0024011 | -0.0022986 | -0.026932 | -0.0049817 | 0.064779 | 0.066245 | 0.00062806 | -0.005129 | 0.013733 | -120.9778 | -3.9413 | -121.4447 | 0.18768 | -121.701 | -121.5591 | -122.1817 | -0.036621 | -121.7926 | 0.086975 | 0.14191 | -121.6324 | -121.7697 | -0.10071 | 0.041199 | 0.054932 | 0.62256 | 0.15564 | 0.11444 | -0.11902 | -0.032043 | -0.16937 | -0.045776 | -0.58136 | -0.19226 | -0.022889 | 0.009156 | 121.788 | 121.6141 | 117.659 | -121.6919 | 121.6873 | 121.7422 | 121.5637 | -121.9025
542.0312 | 121.9391 | -121.5958 | 0.15106 | -0.013122 | 0.016186 | 0.070122 | 0.0071307 | 0.065302 | -0.0015465 | -0.0016578 | -0.011673 | -0.0054089 | 0.064352 | 0.063467 | 0.0025507 | -0.0066244 | 0.009155 | -120.9961 | -3.9459 | -121.4584 | 0.18768 | -121.6965 | -121.5637 | -122.1863 | -0.036621 | -121.7972 | 0.086975 | 0.13275 | -121.6141 | -121.8063 | -0.10071 | 0.032043 | 0.036621 | 0.59967 | 0.13733 | 0.10529 | -0.14191 | -0.018311 | -0.21057 | -0.064087 | -0.59051 | -0.20142 | 0.009155 | -0.018311 | 121.7834 | 121.6049 | 117.6498 | -121.7148 | 121.6827 | 121.7285 | 121.5591 | -121.9574
543.7656 | 121.8475 | -121.637 | 0.19684 | -0.0054933 | 0.014691 | 0.066917 | 0.0041401 | 0.066157 | 0.0012305 | -0.0025122 | -0.011673 | -0.0064771 | 0.062429 | 0.066245 | 0.0044733 | -0.0083334 | 0.018311 | -121.0556 | -3.978 | -121.4676 | 0.17853 | -121.701 | -121.5225 | -122.1725 | -0.10986 | -121.843 | 0.09613 | 0.11902 | -121.6278 | -121.7972 | -0.064087 | 0.11444 | -0.01831 | 0.58136 | 0.16937 | 0.054932 | -0.17853 | 0.009155 | -0.16022 | -0.10071 | -0.53558 | -0.20599 | -0.045777 | -0.077819 | 121.8155 | 121.6553 | 117.659 | -121.7194 | 121.7331 | 121.756 | 121.5271 | -121.994
545.4375 | 121.8384 | -121.637 | 0.17853 | -0.013122 | 0.012768 | 0.069695 | 0.0028583 | 0.064875 | -0.0034691 | -0.002085 | -0.011673 | -0.0073315 | 0.060079 | 0.064749 | 0.0049005 | -0.00577 | 0.11902 | -120.8633 | -3.8635 | -121.3669 | 0.11444 | -121.637 | -121.4996 | -122.0764 | 0.045776 | -121.6827 | 0.032043 | 0.082397 | -121.5958 | -121.7743 | 0 | 0.13733 | -0.064087 | 0.77362 | 0.27008 | 0.13275 | -0.059509 | 0.041199 | -0.13733 | -0.14648 | -0.43945 | -0.045776 | 0.091553 | -0.096131 | 121.7514 | 121.756 | 117.7734 | -121.6782 | 121.669 | 121.7194 | 121.6827 | -121.9528
547.1719 | 121.8201 | -121.637 | 0.17395 | -0.0054933 | 0.009564 | 0.066277 | 0.0052081 | 0.065089 | -0.0068871 | -0.0016578 | -0.011673 | -0.0069043 | 0.061148 | 0.06304 | 0.0044733 | -0.0049154 | 0.10071 | -120.8954 | -3.8773 | -121.4127 | 0.11902 | -121.6553 | -121.4859 | -122.1222 | 0.004578 | -121.7331 | 0.045776 | 0.086975 | -121.6095 | -121.7697 | -0.01831 | 0.15106 | -0.054931 | 0.74158 | 0.2243 | 0.073242 | -0.073242 | 0.027466 | -0.13275 | -0.12817 | -0.48523 | -0.09613 | 0.036621 | -0.086975 | 121.756 | 121.7377 | 117.7597 | -121.6599 | 121.6827 | 121.7239 | 121.6415 | -121.9437
548.9219 | 121.8338 | -121.6553 | 0.17853 | -0.013122 | 0.017682 | 0.065422 | 0.0062763 | 0.067225 | 0.0048621 | 0.0017602 | -0.011673 | -0.0051953 | 0.061361 | 0.06539 | 0.0038325 | -0.010042 | 0.050354 | -121.0144 | -3.9322 | -121.4584 | 0.16479 | -121.6873 | -121.5546 | -122.1634 | -0.073242 | -121.8338 | 0.091553 | 0.13275 | -121.6278 | -121.8018 | -0.032044 | 0.10071 | -0.013733 | 0.64087 | 0.19684 | 0.09613 | -0.12817 | 0.027465 | -0.14649 | -0.086975 | -0.50812 | -0.17853 | -0.032043 | -0.045777 | 121.8201 | 121.7056 | 117.7231 | -121.7331 | 121.7468 | 121.788 | 121.582 | -121.9803
550.5938 | 121.8338 | -121.6461 | 0.19226 | -0.013122 | 0.014691 | 0.069267 | 0.0022175 | 0.065943 | -0.0036829 | -0.0018714 | -0.011673 | -0.0073315 | 0.060507 | 0.063254 | 0.0034051 | -0.007479 | 0.11902 | -120.8679 | -3.8635 | -121.3943 | 0.1236 | -121.6644 | -121.5134 | -122.0993 | 0.022888 | -121.7102 | 0.036621 | 0.10071 | -121.5912 | -121.7377 | -0.018311 | 0.13275 | -0.068665 | 0.7782 | 0.25177 | 0.11902 | -0.073242 | 0.054931 | -0.091553 | -0.15564 | -0.45319 | -0.064087 | 0.027466 | -0.091553 | 121.7697 | 121.7651 | 117.7826 | -121.7056 | 121.6827 | 121.7468 | 121.669 | -121.9299
552.3281 | 121.9757 | -121.6232 | 0.13275 | -0.0054933 | 0.0117 | 0.071403 | 0.0052081 | 0.066371 | -0.0047509 | -0.0035804 | -0.011673 | -0.0086133 | 0.059866 | 0.062186 | 0.0027643 | -0.007479 | 0.10529 | -120.8954 | -3.891 | -121.3989 | 0.13275 | -121.6599 | -121.5179 | -122.0993 | 0.059509 | -121.6873 | 0.032043 | 0.07782 | -121.6141 | -121.7697 | -0.036621 | 0.10529 | 0 | 0.72784 | 0.2243 | 0.11902 | -0.027465 | 0.009155 | -0.14648 | -0.10071 | -0.47607 | -0.064087 | 0.082397 | -0.054931 | 121.756 | 121.7285 | 117.7322 | -121.6507 | 121.6553 | 121.7011 | 121.6827 | -121.9025
554.0625 | 121.8384 | -121.6324 | 0.16022 | -0.013122 | 0.015118 | 0.068199 | 0.0024311 | 0.065302 | 0.0022987 | -0.0027258 | 0.0035858 | -0.0056225 | 0.05773 | 0.066031 | 0.0046869 | -0.006838 | 0.16022 | -120.9 | -3.8589 | -121.3898 | 0.11444 | -121.669 | -121.5363 | -122.0535 | 0.032043 | -121.6965 | 0.045776 | 0.07782 | -121.6049 | -121.7468 | -0.036621 | 0.09613 | -0.045776 | 0.73242 | 0.24261 | 0.14648 | 0 | 0.027466 | -0.11444 | -0.11444 | -0.42114 | -0.064087 | 0.050354 | -0.082397 | 121.7468 | 121.7926 | 117.7734 | -121.6965 | 121.6782 | 121.7102 | 121.6644 | -121.907
555.8125 | 121.9437 | -121.6232 | 0.16479 | -0.020752 | 0.011914 | 0.06884 | 0.0043537 | 0.066584 | -0.0036829 | -0.0029394 | -0.019302 | -0.0075451 | 0.061361 | 0.063681 | 0.0016963 | -0.0072652 | 0.059509 | -120.9595 | -3.9597 | -121.431 | 0.13733 | -121.6599 | -121.5454 | -122.1268 | -0.013733 | -121.7239 | 0.054932 | 0.09613 | -121.6324 | -121.7697 | -0.036621 | 0.07782 | -0.027466 | 0.66376 | 0.19226 | 0.11444 | -0.10529 | -0.009155 | -0.14648 | -0.10986 | -0.50354 | -0.10071 | 0.045776 | -0.068665 | 121.7606 | 121.6827 | 117.6636 | -121.7102 | 121.6782 | 121.7194 | 121.6095 | -121.9345
557.4844 | 121.8567 | -121.6232 | 0.19226 | -0.0054933 | 0.015759 | 0.067986 | 0.0022175 | 0.064875 | -0.00069214 | -0.0040076 | -0.0040437 | -0.0069043 | 0.059011 | 0.06304 | 0.0055415 | -0.010897 | 0.16022 | -120.9045 | -3.8864 | -121.4081 | 0.10529 | -121.6736 | -121.5363 | -122.081 | 0.022888 | -121.7102 | 0.045776 | 0.082397 | -121.6141 | -121.756 | -0.050354 | 0.086975 | -0.086975 | 0.71869 | 0.21515 | 0.12817 | -0.032044 | 0.009155 | -0.13275 | -0.14648 | -0.45776 | -0.086975 | 0.045776 | -0.10986 | 121.7285 | 121.7834 | 117.7368 | -121.7285 | 121.669 | 121.7056 | 121.6461 | -121.9482
559.2188 | 121.8796 | -121.6599 | 0.1831 | -0.013122 | 0.017254 | 0.067986 | 0.0047809 | 0.065089 | 0.0044349 | 5.1244e-05 | -0.011673 | -0.0043409 | 0.062856 | 0.067313 | 0.0055415 | -0.008547 | 0.045776 | -121.0693 | -3.9917 | -121.4859 | 0.17853 | -121.6965 | -121.5546 | -122.1954 | -0.10986 | -121.8613 | 0.082397 | 0.1236 | -121.669 | -121.8109 | -0.036621 | 0.10529 | -0.004577 | 0.59051 | 0.17395 | 0.068664 | -0.13733 | -0.009155 | -0.15106 | -0.10071 | -0.53558 | -0.20142 | -0.050354 | -0.059509 | 121.8384 | 121.7056 | 117.6682 | -121.7377 | 121.7422 | 121.7834 | 121.55 | -121.994
560.9688 | 121.8979 | -121.6415 | 0.17395 | -0.020752 | 0.014691 | 0.069054 | 0.0041401 | 0.068293 | -0.00069214 | -0.002085 | -0.011673 | -0.0041271 | 0.060293 | 0.066885 | 0.0061823 | -0.0089742 | 0.11444 | -120.9412 | -3.9139 | -121.4264 | 0.1236 | -121.6553 | -121.5591 | -122.0718 | 0 | -121.7331 | 0.050354 | 0.091553 | -121.637 | -121.7468 | -0.013732 | 0.082398 | -0.050354 | 0.70038 | 0.21515 | 0.13275 | -0.059509 | 0.004578 | -0.10528 | -0.1236 | -0.4303 | -0.091552 | 0.013733 | -0.082397 | 121.7651 | 121.756 | 117.7277 | -121.7331 | 121.6919 | 121.7331 | 121.6415 | -121.9208
562.6406 | 121.994 | -121.6141 | 0.15106 | -0.013122 | 0.015332 | 0.069481 | 0.0064899 | 0.064234 | 0.0033667 | -0.0018714 | -0.0040437 | -0.0045545 | 0.064779 | 0.065604 | 0.0051141 | -0.0070516 | 0.045776 | -121.0281 | -3.9734 | -121.4676 | 0.17395 | -121.7331 | -121.582 | -122.1497 | -0.013733 | -121.8155 | 0.09613 | 0.12817 | -121.669 | -121.8384 | -0.11902 | 0.032044 | 0.022888 | 0.58594 | 0.14648 | 0.11444 | -0.10529 | -0.054931 | -0.2243 | -0.054932 | -0.53558 | -0.20142 | 0.022888 | -0.022888 | 121.788 | 121.6599 | 117.6407 | -121.7331 | 121.7102 | 121.7422 | 121.6003 | -121.9894
564.3906 | 121.9345 | -121.6278 | 0.15106 | -0.013122 | 0.013409 | 0.069054 | 0.0056355 | 0.066157 | -0.0024011 | -0.0044348 | -0.011673 | -0.0077587 | 0.063284 | 0.064749 | 0.0019099 | -0.0072652 | 0.11444 | -120.8908 | -3.8635 | -121.4035 | 0.11902 | -121.7102 | -121.5408 | -122.0993 | 0.07782 | -121.7285 | 0.032043 | 0.07782 | -121.6461 | -121.7834 | -0.082397 | 0.086975 | -0.032043 | 0.737 | 0.22431 | 0.13733 | -0.036621 | -0.01831 | -0.15564 | -0.11902 | -0.4715 | -0.10071 | 0.054931 | -0.073242 | 121.7468 | 121.7422 | 117.7643 | -121.6919 | 121.6599 | 121.7056 | 121.7056 | -121.9345
566.0625 | 121.9391 | -121.6187 | 0.14648 | 0.0021362 | 0.014691 | 0.067345 | 0.0073443 | 0.066157 | -0.0024011 | -0.0022986 | -0.019302 | -0.010536 | 0.064565 | 0.063681 | -0.0015081 | -0.008547 | 0.11902 | -120.8817 | -3.8681 | -121.3898 | 0.1236 | -121.6782 | -121.5591 | -122.113 | 0.073242 | -121.7194 | 0.054932 | 0.10529 | -121.6736 | -121.8018 | -0.05951 | 0.059509 | -0.022888 | 0.737 | 0.22888 | 0.16937 | -0.027465 | -0.054932 | -0.18311 | -0.091552 | -0.49439 | -0.10071 | 0.082398 | -0.041198 | 121.7422 | 121.7377 | 117.7505 | -121.7056 | 121.6736 | 121.7239 | 121.6919 | -121.9482
567.8125 | 121.9528 | -121.5958 | 0.15564 | -0.013122 | 0.011914 | 0.067558 | 0.0037127 | 0.065089 | -0.0028283 | -0.0018714 | -0.0040437 | -0.0098951 | 0.061361 | 0.065817 | 0.0034051 | -0.0083334 | 0.064087 | -120.9549 | -3.9459 | -121.4447 | 0.14191 | -121.7148 | -121.5546 | -122.1359 | 0.013733 | -121.7331 | 0.059509 | 0.09613 | -121.6324 | -121.788 | -0.11902 | 0.041199 | -0.013733 | 0.64087 | 0.15106 | 0.10986 | -0.091553 | -0.036621 | -0.19226 | -0.096131 | -0.54016 | -0.13733 | 0.054932 | -0.05951 | 121.7377 | 121.6599 | 117.6498 | -121.7102 | 121.6553 | 121.6919 | 121.6095 | -121.9437
569.4844 | 121.8475 | -121.6873 | 0.16937 | -0.013122 | 0.012127 | 0.070549 | 0.0011493 | 0.065302 | 0.0014441 | -0.0025122 | -0.0040437 | -0.0060497 | 0.059866 | 0.063895 | 0.0059687 | -0.0081198 | 0.12817 | -120.9 | -3.9001 | -121.4218 | 0.11902 | -121.6782 | -121.5408 | -122.081 | 0.018311 | -121.7377 | 0.045776 | 0.059509 | -121.6141 | -121.7926 | 0.009155 | 0.14648 | -0.050354 | 0.78735 | 0.2655 | 0.11902 | -0.041199 | 0.073242 | -0.10529 | -0.1236 | -0.39368 | -0.050354 | 0.054932 | -0.10986 | 121.8063 | 121.8155 | 117.7872 | -121.7102 | 121.7331 | 121.7468 | 121.7056 | -121.962
571.2188 | 121.8979 | -121.6507 | 0.16937 | -0.0054933 | 0.015332 | 0.069695 | 0.00072207 | 0.065302 | 0.0022987 | -0.0033668 | -0.011673 | -0.0060497 | 0.060293 | 0.062613 | 0.0066095 | -0.0083334 | 0.14648 | -120.9137 | -3.9093 | -121.4172 | 0.13275 | -121.6919 | -121.5546 | -122.0535 | 0.022888 | -121.7285 | 0.041199 | 0.07782 | -121.6507 | -121.7606 | -0.041199 | 0.096131 | -0.036622 | 0.737 | 0.23346 | 0.13733 | -0.022889 | 0 | -0.10986 | -0.12817 | -0.40283 | -0.07782 | 0.032043 | -0.091553 | 121.7834 | 121.7972 | 117.7414 | -121.7239 | 121.6919 | 121.7285 | 121.6736 | -121.9299
572.9844 | 121.9666 | -121.6232 | 0.14191 | -0.0054933 | 0.014264 | 0.067558 | 0.0047809 | 0.065302 | -0.0034691 | -0.0027258 | -0.011673 | -0.0073315 | 0.061361 | 0.064322 | 0.0016963 | -0.0070516 | 0.073242 | -120.9503 | -3.9413 | -121.4355 | 0.14191 | -121.6873 | -121.5454 | -122.113 | 0.004578 | -121.7422 | 0.041199 | 0.09613 | -121.6507 | -121.788 | -0.064087 | 0.07782 | 0 | 0.67291 | 0.18768 | 0.10986 | -0.068665 | -0.027466 | -0.16479 | -0.10071 | -0.48981 | -0.11902 | 0.045776 | -0.045777 | 121.7651 | 121.6965 | 117.6819 | -121.6873 | 121.6644 | 121.7194 | 121.6278 | -121.9299
574.6562 | 121.9849 | -121.6141 | 0.15106 | -0.0054933 | 0.014264 | 0.067345 | 0.0047809 | 0.065089 | -0.0036829 | -0.0033668 | -0.0040437 | -0.0088269 | 0.061788 | 0.064749 | 0.0023371 | -0.0094016 | 0.09613 | -120.9549 | -3.9413 | -121.4264 | 0.15564 | -121.6919 | -121.5408 | -122.1222 | 0.041199 | -121.7148 | 0.050354 | 0.073242 | -121.6461 | -121.7926 | -0.07782 | 0.073242 | 0.004578 | 0.65918 | 0.18768 | 0.11444 | -0.054932 | -0.032043 | -0.17853 | -0.10071 | -0.50812 | -0.10071 | 0.07782 | -0.07782 | 121.7697 | 121.7102 | 117.6727 | -121.6919 | 121.6644 | 121.6873 | 121.6553 | -121.9437
576.3906 | 121.9208 | -121.6507 | 0.16937 | -0.0054933 | 0.014264 | 0.06884 | 0.00050847 | 0.066157 | 0.0063575 | -0.0029394 | -0.0040437 | -0.0034863 | 0.059225 | 0.064963 | 0.0081049 | -0.0081198 | 0.082397 | -121.019 | -4.01 | -121.4996 | 0.17853 | -121.6827 | -121.582 | -122.1451 | -0.059509 | -121.8109 | 0.07782 | 0.10071 | -121.6507 | -121.8109 | -0.032043 | 0.068665 | 0.009155 | 0.63171 | 0.15106 | 0.082397 | -0.086976 | 0 | -0.16022 | -0.091553 | -0.49439 | -0.16022 | 0 | -0.068665 | 121.8292 | 121.7331 | 117.6407 | -121.7514 | 121.7285 | 121.7514 | 121.5912 | -121.9803
578.125 | 122.0032 | -121.6141 | 0.16479 | 0.0021362 | 0.013409 | 0.068626 | 0.0062763 | 0.070429 | -0.0024011 | -0.002085 | -0.019302 | -0.0077587 | 0.062002 | 0.061972 | 0.0025507 | -0.0064108 | 0.15106 | -120.8542 | -3.8956 | -121.3852 | 0.1236 | -121.6873 | -121.5637 | -122.0856 | 0.07782 | -121.6599 | 0.036621 | 0.07782 | -121.6644 | -121.7834 | -0.073242 | 0.050354 | -0.041199 | 0.75989 | 0.22888 | 0.17853 | -0.013733 | -0.050354 | -0.16937 | -0.12817 | -0.4715 | -0.045776 | 0.1236 | -0.086975 | 121.7377 | 121.7651 | 117.7185 | -121.7285 | 121.6507 | 121.6919 | 121.6919 | -121.9482
579.8594 | 121.994 | -121.6324 | 0.14191 | -0.0054933 | 0.017682 | 0.066917 | 0.0075581 | 0.064021 | 0.0031531 | -0.0040076 | 0.0035858 | -0.0039135 | 0.062856 | 0.065604 | 0.0029779 | -0.0079062 | 0.036621 | -121.0281 | -4.0054 | -121.4813 | 0.16937 | -121.7514 | -121.6095 | -122.1909 | -0.050354 | -121.8338 | 0.10529 | 0.12817 | -121.7148 | -121.8338 | -0.11902 | 0.022888 | 0.027466 | 0.60425 | 0.15106 | 0.12817 | -0.10529 | -0.082398 | -0.20142 | -0.036621 | -0.55847 | -0.20142 | 0 | -0.013733 | 121.8018 | 121.669 | 117.627 | -121.7514 | 121.7377 | 121.7606 | 121.582 | -121.9757
581.5938 | 121.9574 | -121.6187 | 0.16022 | 0.0021362 | 0.012341 | 0.066917 | 0.0045673 | 0.065302 | -0.0038965 | -0.0014442 | -0.0040437 | -0.0081861 | 0.061788 | 0.06539 | 0.0010553 | -0.0079062 | 0.059509 | -120.9549 | -3.9825 | -121.4401 | 0.13733 | -121.7102 | -121.5637 | -122.1497 | 0 | -121.7468 | 0.041199 | 0.086975 | -121.6324 | -121.8063 | -0.091553 | 0.054931 | -0.022888 | 0.66376 | 0.17853 | 0.1236 | -0.10071 | -0.013733 | -0.18768 | -0.11902 | -0.53101 | -0.12817 | 0.059509 | -0.073242 | 121.756 | 121.6782 | 117.6361 | -121.7239 | 121.6599 | 121.7056 | 121.6187 | -121.9666
583.2812 | 121.9849 | -121.6049 | 0.14191 | -0.013122 | 0.013623 | 0.066917 | 0.0077717 | 0.065089 | -0.00026494 | -0.0012306 | 0.0035858 | -0.0064771 | 0.062429 | 0.065817 | 0.0010553 | -0.0076926 | 0.10529 | -120.9 | -3.9276 | -121.4127 | 0.13733 | -121.6965 | -121.55 | -122.0856 | 0.064087 | -121.6873 | 0.045776 | 0.073242 | -121.637 | -121.7834 | -0.091553 | 0.054931 | -0.004578 | 0.70496 | 0.19226 | 0.13733 | -0.036621 | -0.032044 | -0.17853 | -0.096131 | -0.48065 | -0.082398 | 0.09613 | -0.068665 | 121.7422 | 121.7102 | 117.6773 | -121.6919 | 121.6507 | 121.6782 | 121.669 | -121.9254
585.0312 | 121.9208 | -121.6599 | 0.17395 | -0.013122 | 0.013409 | 0.069267 | 0.0032855 | 0.064875 | 0.0040077 | -0.0010168 | -0.0040437 | -0.0039135 | 0.062216 | 0.063467 | 0.0068231 | -0.0091878 | 0.11444 | -120.932 | -3.9413 | -121.4127 | 0.14648 | -121.6873 | -121.55 | -122.081 | 0.027466 | -121.7331 | 0.045776 | 0.082397 | -121.6187 | -121.7926 | -0.027466 | 0.10986 | -0.027466 | 0.72784 | 0.24719 | 0.13733 | -0.059509 | 0.041199 | -0.13275 | -0.12817 | -0.42114 | -0.073242 | 0.05951 | -0.091553 | 121.8063 | 121.7743 | 117.7185 | -121.7239 | 121.7056 | 121.7422 | 121.6873 | -121.9666
586.7031 | 121.9116 | -121.6644 | 0.17853 | -0.020752 | 0.013409 | 0.067772 | 0.0015765 | 0.064662 | 0.0016577 | -0.00080316 | -0.0040437 | -0.0056225 | 0.06072 | 0.062613 | 0.0063959 | -0.0070516 | 0.14648 | -120.9183 | -3.9276 | -121.3943 | 0.14191 | -121.6736 | -121.5866 | -122.0673 | 0.041199 | -121.7239 | 0.041199 | 0.07782 | -121.6232 | -121.7514 | -0.009155 | 0.07782 | -0.036621 | 0.74616 | 0.27008 | 0.19226 | -0.032044 | 0.041199 | -0.086975 | -0.13733 | -0.40283 | -0.059509 | 0.027466 | -0.10071 | 121.8063 | 121.8109 | 117.7368 | -121.7651 | 121.7056 | 121.7422 | 121.7056 | -121.9299
588.4375 | 121.9162 | -121.6461 | 0.17853 | -0.013122 | 0.015118 | 0.068199 | 0.0030719 | 0.06573 | 0.0035803 | -0.00037596 | -0.0040437 | -0.0051953 | 0.060507 | 0.063467 | 0.0066095 | -0.0059836 | 0.086975 | -120.9732 | -3.9917 | -121.4676 | 0.16022 | -121.6873 | -121.5866 | -122.1039 | 0.004578 | -121.7468 | 0.045776 | 0.086975 | -121.6461 | -121.8155 | -0.041199 | 0.059509 | -0.018311 | 0.67291 | 0.17853 | 0.11902 | -0.091553 | 0 | -0.16937 | -0.13275 | -0.45776 | -0.10071 | 0.068665 | -0.091553 | 121.8063 | 121.7331 | 117.6544 | -121.7651 | 121.6919 | 121.7331 | 121.6507 | -121.994
590.1719 | 121.9757 | -121.6232 | 0.16022 | -0.020752 | 0.015118 | 0.068413 | 0.0073443 | 0.066371 | 0.0022987 | -0.0027258 | -0.011673 | -0.0045545 | 0.062429 | 0.064536 | 0.0023371 | -0.0096152 | 0.022888 | -121.0052 | -3.9963 | -121.4996 | 0.18768 | -121.7468 | -121.582 | -122.1954 | -0.045776 | -121.8384 | 0.09613 | 0.12817 | -121.7194 | -121.8475 | -0.1236 | 0.041199 | 0.027466 | 0.61798 | 0.1236 | 0.082397 | -0.13733 | -0.09613 | -0.2243 | -0.064087 | -0.5722 | -0.21515 | 0.009155 | -0.032043 | 121.8109 | 121.6461 | 117.627 | -121.7422 | 121.7194 | 121.7514 | 121.5775 | -122.0078
591.9219 | 121.8796 | -121.6736 | 0.19684 | -0.013122 | 0.017895 | 0.067772 | 0.0032855 | 0.066157 | 0.0061439 | 0.001333 | -0.011673 | -0.0041271 | 0.062002 | 0.066245 | 0.0070367 | -0.008547 | 0.086975 | -120.9595 | -3.9551 | -121.4676 | 0.15564 | -121.6965 | -121.5866 | -122.1725 | -0.027466 | -121.8292 | 0.059509 | 0.10986 | -121.6599 | -121.843 | -0.022888 | 0.086975 | -0.041198 | 0.71411 | 0.20599 | 0.11902 | -0.10986 | 0.013733 | -0.16937 | -0.13733 | -0.49896 | -0.15564 | 0.013733 | -0.086975 | 121.8292 | 121.7606 | 117.7185 | -121.7834 | 121.7331 | 121.7834 | 121.6461 | -122.0398
593.6094 | 121.875 | -121.6782 | 0.17853 | -0.0054933 | 0.0084958 | 0.069054 | 0.0034991 | 0.062739 | -0.0049645 | -0.00037596 | -0.0040437 | -0.0083997 | 0.058584 | 0.063895 | 0.0019099 | -0.0047018 | 0.059509 | -120.9366 | -3.9825 | -121.4539 | 0.1236 | -121.6965 | -121.5225 | -122.1725 | -0.022888 | -121.7743 | 0.050354 | 0.091553 | -121.637 | -121.8155 | -0.01831 | 0.15564 | -0.054932 | 0.74158 | 0.22431 | 0.068665 | -0.11902 | 0.041199 | -0.13733 | -0.12817 | -0.49438 | -0.09613 | 0.041199 | -0.086975 | 121.8018 | 121.7377 | 117.6956 | -121.701 | 121.7285 | 121.7697 | 121.6553 | -121.994
595.3438 | 121.8704 | -121.6782 | 0.18768 | -0.013122 | 0.014264 | 0.068626 | 0.0020039 | 0.066584 | 0.0010169 | -0.00037596 | -0.0040437 | -0.0064771 | 0.059652 | 0.065817 | 0.0038325 | -0.0083334 | 0.14191 | -120.9 | -3.9185 | -121.4127 | 0.12817 | -121.7102 | -121.5179 | -122.0718 | 0.041199 | -121.7148 | 0.032043 | 0.073242 | -121.6461 | -121.7926 | -0.032043 | 0.16022 | -0.059509 | 0.7782 | 0.2655 | 0.10528 | -0.045776 | 0.032044 | -0.11444 | -0.15564 | -0.39368 | -0.036621 | 0.07782 | -0.11444 | 121.8063 | 121.8201 | 117.7597 | -121.7056 | 121.7102 | 121.7514 | 121.7194 | -121.9803
597.0938 | 121.9299 | -121.6461 | 0.1831 | -0.013122 | 0.015332 | 0.069054 | 0.0041401 | 0.067011 | 0.0025123 | -0.00058956 | 0.0035858 | -0.0032727 | 0.060507 | 0.065817 | 0.0068231 | -0.0076926 | 0.07782 | -121.0144 | -3.9963 | -121.4859 | 0.17395 | -121.6827 | -121.582 | -122.1405 | -0.027466 | -121.7697 | 0.050354 | 0.09613 | -121.6782 | -121.7972 | -0.036621 | 0.064087 | -0.009155 | 0.63171 | 0.16022 | 0.09613 | -0.10528 | -0.032044 | -0.15106 | -0.13275 | -0.49438 | -0.1236 | 0.027466 | -0.086975 | 121.8201 | 121.7239 | 117.6498 | -121.7651 | 121.6965 | 121.7422 | 121.6187 | -121.9803
598.7812 | 121.8887 | -121.6461 | 0.1831 | -0.0054933 | 0.013196 | 0.067131 | 0.0037127 | 0.065943 | -0.0026147 | -0.0016578 | 0.0035858 | -0.0077587 | 0.059439 | 0.063467 | 0.0014825 | -0.00577 | 0.082397 | -120.9549 | -3.9917 | -121.4584 | 0.13275 | -121.6827 | -121.5591 | -122.1725 | -0.009155 | -121.7651 | 0.041199 | 0.086975 | -121.669 | -121.8109 | -0.036621 | 0.086975 | -0.050354 | 0.69122 | 0.18768 | 0.10071 | -0.10071 | -0.022888 | -0.16479 | -0.14191 | -0.52643 | -0.11902 | 0.045776 | -0.09613 | 121.7789 | 121.7285 | 117.6544 | -121.7422 | 121.6873 | 121.7331 | 121.637 | -121.994
600.5156 | 121.9254 | -121.6873 | 0.17853 | 0.0021362 | 0.015973 | 0.068413 | 0.0034991 | 0.066584 | 0.0018713 | -0.00058956 | -0.011673 | -0.0043409 | 0.061361 | 0.065604 | 0.0066095 | -0.007479 | 0.068665 | -121.0327 | -4.0421 | -121.4951 | 0.16937 | -121.7102 | -121.5637 | -122.1725 | -0.073242 | -121.8109 | 0.07782 | 0.10071 | -121.6599 | -121.8292 | -0.022888 | 0.1236 | -0.009155 | 0.6546 | 0.19226 | 0.068665 | -0.10986 | 0.027466 | -0.14191 | -0.10071 | -0.48523 | -0.1236 | 0.018311 | -0.07782 | 121.8567 | 121.756 | 117.6453 | -121.7422 | 121.7651 | 121.788 | 121.6141 | -122.0078
602.25 | 121.962 | -121.6278 | 0.15106 | -0.0054933 | 0.013623 | 0.067772 | 0.0067035 | 0.065943 | -0.0013329 | -0.002085 | -0.0040437 | -0.0092541 | 0.062002 | 0.064749 | 0.0023371 | -0.0070516 | 0.13733 | -120.8817 | -3.9093 | -121.4218 | 0.10986 | -121.6919 | -121.5408 | -122.0901 | 0.09613 | -121.7102 | 0.036621 | 0.073242 | -121.6324 | -121.7697 | -0.064087 | 0.086975 | -0.041199 | 0.74616 | 0.20599 | 0.11902 | -0.013733 | -0.004577 | -0.14191 | -0.11444 | -0.46234 | -0.082397 | 0.059509 | -0.07782 | 121.7377 | 121.7651 | 117.7185 | -121.6919 | 121.6644 | 121.701 | 121.7239 | -121.9208
604 | 121.875 | -121.669 | 0.20142 | -0.013122 | 0.012768 | 0.068413 | 0.0030719 | 0.066798 | -0.00047854 | -0.0014442 | -0.0040437 | -0.0047681 | 0.06072 | 0.065604 | 0.0029779 | -0.0072652 | 0.14648 | -120.9045 | -3.9322 | -121.4264 | 0.12817 | -121.6873 | -121.5408 | -122.0993 | 0.036621 | -121.7148 | 0.045776 | 0.086975 | -121.6324 | -121.8155 | -0.018311 | 0.12817 | -0.073242 | 0.76447 | 0.24261 | 0.11444 | -0.054932 | 0.036621 | -0.14648 | -0.15564 | -0.4303 | -0.045777 | 0.10071 | -0.11444 | 121.7972 | 121.8155 | 117.7368 | -121.7422 | 121.7148 | 121.756 | 121.7056 | -122.0169
605.6875 | 122.0169 | -121.6278 | 0.15106 | -0.0054933 | 0.013836 | 0.070976 | 0.0056355 | 0.067866 | -0.0024011 | -0.0033668 | -0.011673 | -0.0077587 | 0.059439 | 0.063254 | 0.0019099 | -0.008547 | 0.11444 | -120.932 | -3.9551 | -121.4447 | 0.13275 | -121.6873 | -121.5363 | -122.1268 | 0.054932 | -121.7148 | 0.068665 | 0.09613 | -121.6324 | -121.7972 | -0.059509 | 0.091553 | -0.018311 | 0.6958 | 0.18311 | 0.091553 | -0.036621 | -0.004577 | -0.16937 | -0.082397 | -0.49896 | -0.086975 | 0.082397 | -0.054932 | 121.7606 | 121.7422 | 117.6727 | -121.6873 | 121.6965 | 121.7239 | 121.6827 | -121.9482
607.4219 | 122.0123 | -121.6187 | 0.14191 | -0.013122 | 0.011914 | 0.069695 | 0.0071307 | 0.064234 | -0.00047854 | -0.0050758 | 0.0035858 | -0.0058361 | 0.062643 | 0.064749 | 0.0019099 | -0.0098288 | 0.15564 | -120.9045 | -3.9413 | -121.4172 | 0.11444 | -121.701 | -121.5546 | -122.0993 | 0.086975 | -121.6919 | 0.054932 | 0.086975 | -121.6415 | -121.7972 | -0.082398 | 0.064087 | -0.027466 | 0.71411 | 0.20142 | 0.13733 | 0.013733 | -0.022889 | -0.17853 | -0.086975 | -0.48065 | -0.073243 | 0.10528 | -0.054932 | 121.7331 | 121.7743 | 117.6773 | -121.6965 | 121.6736 | 121.7056 | 121.7056 | -121.9391
609.1094 | 122.0078 | -121.6232 | 0.15106 | -0.020752 | 0.019177 | 0.065422 | 0.0041401 | 0.067011 | 0.0037939 | -0.0031532 | -0.011673 | -0.0032727 | 0.064138 | 0.066458 | 0.0055415 | -0.0096152 | 0.068665 | -121.0281 | -4.0329 | -121.4905 | 0.17853 | -121.7285 | -121.5729 | -122.1817 | -0.022888 | -121.8338 | 0.091553 | 0.1236 | -121.7102 | -121.8658 | -0.10529 | 0.050354 | 0.027466 | 0.59509 | 0.13275 | 0.082397 | -0.082397 | -0.086975 | -0.24261 | -0.059509 | -0.55847 | -0.21057 | 0.032044 | -0.027466 | 121.8018 | 121.6919 | 117.5903 | -121.7239 | 121.7148 | 121.7468 | 121.6003 | -122.0169
610.8438 | 121.9757 | -121.6461 | 0.15564 | -0.013122 | 0.0164 | 0.067131 | 0.0086261 | 0.063807 | 0.0014441 | -0.0016578 | -0.0040437 | -0.0054089 | 0.063497 | 0.065176 | 0.0027643 | -0.0096152 | 0.036621 | -121.0144 | -4.0375 | -121.5134 | 0.1831 | -121.7377 | -121.5866 | -122.2229 | -0.045776 | -121.8475 | 0.09613 | 0.14191 | -121.7102 | -121.8475 | -0.091553 | 0.059509 | 0.027465 | 0.63171 | 0.13275 | 0.073242 | -0.11902 | -0.064087 | -0.20142 | -0.05951 | -0.57678 | -0.20142 | 0 | -0.013733 | 121.8292 | 121.6827 | 117.6086 | -121.7422 | 121.7422 | 121.788 | 121.6003 | -122.0032
612.5781 | 121.9574 | -121.6415 | 0.16937 | -0.0054933 | 0.016613 | 0.066277 | 0.0075581 | 0.065302 | 0.00037606 | -0.0018714 | -0.0040437 | -0.0056225 | 0.063711 | 0.066672 | 0.0023371 | -0.0089742 | 0.036621 | -121.0052 | -4.0283 | -121.4951 | 0.15564 | -121.7331 | -121.6187 | -122.2137 | -0.004578 | -121.8338 | 0.086975 | 0.11902 | -121.7056 | -121.8613 | -0.091552 | 0.022889 | -0.013733 | 0.63629 | 0.14648 | 0.1236 | -0.13275 | -0.064086 | -0.21973 | -0.082398 | -0.5722 | -0.19226 | 0.027466 | -0.050354 | 121.7972 | 121.6782 | 117.6132 | -121.788 | 121.7285 | 121.7606 | 121.637 | -122.0306
614.25 | 121.8842 | -121.669 | 0.18768 | -0.013122 | 0.013196 | 0.070976 | 8.127e-05 | 0.064662 | -0.00069214 | -0.0022986 | 0.0035858 | -0.0073315 | 0.061361 | 0.065817 | 0.0049005 | -0.0066244 | 0.15106 | -120.8908 | -3.9413 | -121.4127 | 0.11444 | -121.6965 | -121.5729 | -122.0764 | 0.041199 | -121.7239 | 0.036621 | 0.07782 | -121.669 | -121.8201 | -0.027466 | 0.09613 | -0.073242 | 0.7782 | 0.25635 | 0.16022 | -0.036621 | 0 | -0.15106 | -0.15106 | -0.40741 | -0.054932 | 0.09613 | -0.10986 | 121.7834 | 121.8201 | 117.7277 | -121.7606 | 121.7056 | 121.7468 | 121.7102 | -122.0078
615.9844 | 121.8979 | -121.6553 | 0.1831 | -0.013122 | 0.0093504 | 0.070976 | 0.0020039 | 0.065516 | -0.0024011 | -0.0033668 | -0.0040437 | -0.0058361 | 0.059652 | 0.064749 | 0.0040461 | -0.0061972 | 0.082397 | -120.9595 | -4.0192 | -121.463 | 0.13275 | -121.7148 | -121.5408 | -122.168 | -0.027466 | -121.7697 | 0.086975 | 0.10986 | -121.6415 | -121.8018 | -0.05951 | 0.11444 | -0.050354 | 0.6958 | 0.19226 | 0.07782 | -0.10071 | 0.013732 | -0.14649 | -0.09613 | -0.5127 | -0.11444 | 0.032044 | -0.073242 | 121.788 | 121.7377 | 117.6361 | -121.7239 | 121.7422 | 121.7651 | 121.6278 | -121.9849
617.7344 | 121.8933 | -121.701 | 0.18768 | -0.0054933 | 0.014691 | 0.06884 | 0.0039265 | 0.066157 | -0.0021875 | -0.0018714 | -0.019302 | -0.0079725 | 0.060079 | 0.064108 | 0.0027643 | -0.0066244 | 0.09613 | -120.9778 | -4.0237 | -121.4539 | 0.15564 | -121.6827 | -121.5637 | -122.1634 | -0.022888 | -121.7789 | 0.064087 | 0.11902 | -121.6461 | -121.8201 | 0.018311 | 0.13733 | -0.032043 | 0.72327 | 0.24719 | 0.10986 | -0.091553 | 0.054932 | -0.11902 | -0.1236 | -0.46234 | -0.07782 | 0.041198 | -0.068664 | 121.8567 | 121.7972 | 117.6773 | -121.7514 | 121.7651 | 121.8201 | 121.6782 | -122.0078
619.4844 | 122.0032 | -121.6141 | 0.14648 | -0.013122 | 0.01405 | 0.070122 | 0.0067035 | 0.065089 | -0.00069214 | -0.0035804 | 0.0035858 | -0.0090405 | 0.060934 | 0.062399 | 0.0014825 | -0.0070516 | 0.09613 | -120.9549 | -3.9917 | -121.4584 | 0.14648 | -121.701 | -121.5637 | -122.1359 | 0.032043 | -121.7239 | 0.054932 | 0.073242 | -121.6919 | -121.8063 | -0.086975 | 0.050354 | 0 | 0.65918 | 0.15564 | 0.10529 | -0.050354 | -0.07782 | -0.19226 | -0.091552 | -0.52185 | -0.10986 | 0.082397 | -0.073242 | 121.7606 | 121.7102 | 117.6224 | -121.7102 | 121.669 | 121.6873 | 121.6461 | -121.9528
621.1562 | 122.0123 | -121.6049 | 0.13733 | -0.013122 | 0.014264 | 0.069054 | 0.0064899 | 0.066371 | -0.0021875 | -0.0035804 | -0.0040437 | -0.0064771 | 0.059439 | 0.064536 | 0.0010553 | -0.0098288 | 0.16937 | -120.8725 | -3.923 | -121.4218 | 0.13733 | -121.6827 | -121.5317 | -122.0764 | 0.091553 | -121.6965 | 0.059509 | 0.09613 | -121.6599 | -121.843 | -0.07782 | 0.073242 | 0 | 0.73242 | 0.1831 | 0.10986 | 0.032044 | -0.054932 | -0.23804 | -0.07782 | -0.4715 | -0.091553 | 0.14648 | -0.041199 | 121.7422 | 121.7743 | 117.6819 | -121.669 | 121.6644 | 121.701 | 121.6965 | -121.9803
622.9062 | 121.9711 | -121.6507 | 0.16479 | -0.020752 | 0.017041 | 0.066277 | 0.00093567 | 0.065516 | 0.0048621 | 0.00069204 | -0.0040437 | -0.0026319 | 0.061788 | 0.067313 | 0.0066095 | -0.010683 | 0.14191 | -120.9641 | -3.9825 | -121.4539 | 0.17853 | -121.7194 | -121.582 | -122.113 | 0.022888 | -121.8018 | 0.068665 | 0.10529 | -121.6827 | -121.8475 | -0.068664 | 0.068665 | 0.013733 | 0.68665 | 0.19684 | 0.12817 | -0.022888 | -0.032043 | -0.19684 | -0.09613 | -0.46234 | -0.15106 | 0.045776 | -0.059509 | 121.8292 | 121.7926 | 117.6682 | -121.7468 | 121.7194 | 121.756 | 121.6736 | -122.0123
624.5781 | 121.962 | -121.6644 | 0.16022 | -0.013122 | 0.017041 | 0.068413 | 0.0062763 | 0.06338 | -5.1338e-05 | -0.0029394 | 0.0035858 | -0.0069043 | 0.062429 | 0.066245 | 0.0036189 | -0.0055564 | 0.054932 | -120.9915 | -4.0237 | -121.4951 | 0.15564 | -121.7422 | -121.6003 | -122.2046 | -0.036621 | -121.8338 | 0.10986 | 0.14191 | -121.7239 | -121.8521 | -0.07782 | 0.064087 | -0.004577 | 0.67291 | 0.16937 | 0.10529 | -0.10528 | -0.059509 | -0.18768 | -0.050354 | -0.54016 | -0.16937 | 0.018311 | -0.01831 | 121.8201 | 121.7194 | 117.6407 | -121.7606 | 121.7743 | 121.8063 | 121.6278 | -122.0123
626.3125 | 121.9391 | -121.6461 | 0.17853 | -0.013122 | 0.015118 | 0.06649 | 0.0045673 | 0.064448 | 0.0025123 | -0.00058956 | -0.0040437 | -0.0056225 | 0.063711 | 0.066672 | 0.0051141 | -0.0091878 | 0.073242 | -121.0236 | -4.0421 | -121.5042 | 0.17853 | -121.7285 | -121.6095 | -122.1359 | -0.036621 | -121.8063 | 0.07782 | 0.10529 | -121.6965 | -121.843 | -0.082398 | 0.036621 | 0 | 0.62256 | 0.14191 | 0.10529 | -0.10529 | -0.050354 | -0.19684 | -0.10071 | -0.48981 | -0.16022 | 0.036622 | -0.073242 | 121.8246 | 121.7194 | 117.6041 | -121.788 | 121.7239 | 121.7514 | 121.6095 | -122.0215
628 | 122.0123 | -121.6232 | 0.15564 | -0.0054933 | 0.015545 | 0.070335 | 0.0062763 | 0.065302 | -0.0034691 | -0.0010168 | -0.011673 | -0.0094677 | 0.06307 | 0.064749 | 0.0021235 | -0.0055564 | 0.1236 | -120.8725 | -3.9322 | -121.4081 | 0.15564 | -121.6873 | -121.5683 | -122.1039 | 0.09613 | -121.6827 | 0.050354 | 0.09613 | -121.6553 | -121.843 | -0.064087 | 0.054932 | 0 | 0.75073 | 0.21515 | 0.16022 | -0.032044 | -0.032043 | -0.21973 | -0.10529 | -0.48065 | -0.059509 | 0.16022 | -0.05951 | 121.7789 | 121.7468 | 117.691 | -121.7239 | 121.6736 | 121.7194 | 121.7194 | -121.9986
629.7344 | 122.0078 | -121.6278 | 0.15106 | -0.0054933 | 0.011273 | 0.068413 | 0.0039265 | 0.066584 | -0.0038965 | -0.0050758 | -0.011673 | -0.0090405 | 0.058798 | 0.064108 | 0.0023371 | -0.008547 | 0.073242 | -120.9595 | -4.0192 | -121.4493 | 0.14648 | -121.701 | -121.5683 | -122.1542 | 0.027466 | -121.7422 | 0.050354 | 0.10071 | -121.6644 | -121.8521 | -0.073242 | 0.05951 | -0.004578 | 0.66833 | 0.17853 | 0.11902 | -0.07782 | -0.036621 | -0.2243 | -0.10071 | -0.52643 | -0.11444 | 0.10986 | -0.050354 | 121.7743 | 121.701 | 117.6086 | -121.7194 | 121.6782 | 121.7285 | 121.6553 | -122.0032
631.4062 | 122.0032 | -121.6278 | 0.14648 | -0.013122 | 0.0117 | 0.069054 | 0.0034991 | 0.063593 | -0.0026147 | -0.0029394 | -0.011673 | -0.0071179 | 0.062856 | 0.064108 | 0.0034051 | -0.0094016 | 0.09613 | -120.9549 | -4.0146 | -121.4447 | 0.13275 | -121.701 | -121.5729 | -122.1405 | 0.036621 | -121.7331 | 0.054932 | 0.09613 | -121.6599 | -121.8338 | -0.073242 | 0.054932 | -0.013733 | 0.67291 | 0.18311 | 0.12817 | -0.050354 | -0.032043 | -0.20599 | -0.091552 | -0.51269 | -0.10528 | 0.10071 | -0.050354 | 121.7606 | 121.7239 | 117.6132 | -121.7194 | 121.6827 | 121.7239 | 121.6644 | -121.9803
633.0938 | 122.0215 | -121.637 | 0.16022 | -0.020752 | 0.015118 | 0.067558 | 0.0069171 | 0.065089 | -0.0024011 | -0.0040076 | -0.019302 | -0.0073315 | 0.062002 | 0.065817 | 0.0027643 | -0.0076926 | 0.13733 | -120.9183 | -3.9642 | -121.4127 | 0.14191 | -121.7056 | -121.5637 | -122.1085 | 0.059509 | -121.701 | 0.050354 | 0.082397 | -121.6644 | -121.8475 | -0.068664 | 0.073242 | -0.01831 | 0.71869 | 0.2243 | 0.15106 | -0.022888 | -0.027466 | -0.21057 | -0.10986 | -0.4715 | -0.064087 | 0.14648 | -0.07782 | 121.7789 | 121.7743 | 117.6727 | -121.7239 | 121.6873 | 121.7194 | 121.6965 | -122.0078
634.8438 | 121.9528 | -121.6507 | 0.16022 | -0.0054933 | 0.013836 | 0.068626 | 0.0069171 | 0.067439 | -0.00047854 | -0.003794 | -0.026932 | -0.0060497 | 0.062429 | 0.064536 | 0.00084166 | -0.0076926 | 0.082397 | -120.9869 | -4.0329 | -121.4859 | 0.14191 | -121.701 | -121.5683 | -122.1725 | -0.013733 | -121.756 | 0.07782 | 0.091553 | -121.6644 | -121.8338 | -0.050354 | 0.082398 | -0.01831 | 0.66376 | 0.16479 | 0.082397 | -0.07782 | -0.013733 | -0.1831 | -0.082397 | -0.52185 | -0.10529 | 0.07782 | -0.068664 | 121.7926 | 121.7331 | 117.6178 | -121.7285 | 121.7285 | 121.7422 | 121.637 | -121.994
636.5156 | 121.9528 | -121.6736 | 0.16937 | -0.013122 | 0.010205 | 0.069267 | 0.0034991 | 0.064662 | -0.0045373 | -0.0031532 | -0.0040437 | -0.0051953 | 0.059011 | 0.062827 | 0.0044733 | -0.006838 | 0.073242 | -120.9824 | -4.0329 | -121.4539 | 0.14191 | -121.6919 | -121.5637 | -122.1588 | -0.009155 | -121.7651 | 0.054932 | 0.086975 | -121.6736 | -121.8475 | -0.018311 | 0.10986 | -0.027466 | 0.69122 | 0.21973 | 0.10986 | -0.096131 | 0 | -0.17395 | -0.11444 | -0.48523 | -0.091553 | 0.082397 | -0.082398 | 121.8155 | 121.7468 | 117.6407 | -121.7331 | 121.7285 | 121.7606 | 121.6644 | -122.0169
638.2656 | 122.0352 | -121.6415 | 0.13275 | -0.0054933 | 0.01405 | 0.06884 | 0.0047809 | 0.064234 | -0.0024011 | -0.003794 | -0.019302 | -0.0083997 | 0.061361 | 0.064963 | 0.0040461 | -0.0066244 | 0.16022 | -120.8679 | -3.9597 | -121.4264 | 0.12817 | -121.6919 | -121.55 | -122.0993 | 0.10071 | -121.7102 | 0.050354 | 0.091553 | -121.6782 | -121.8338 | -0.050354 | 0.091553 | -0.004577 | 0.77362 | 0.21515 | 0.1236 | 0.027466 | -0.036621 | -0.19226 | -0.082397 | -0.45776 | -0.068664 | 0.1236 | -0.041198 | 121.7697 | 121.8018 | 117.6819 | -121.6827 | 121.6919 | 121.7331 | 121.7422 | -121.9666
640 | 121.8887 | -121.7285 | 0.19684 | 0.0021362 | 0.018322 | 0.06649 | 0.0028583 | 0.067225 | 0.0076391 | -0.0010168 | -0.0040437 | -0.0034863 | 0.060934 | 0.064749 | 0.0083185 | -0.011324 | 0.054932 | -121.0419 | -4.0466 | -121.5179 | 0.16937 | -121.7422 | -121.6187 | -122.2092 | -0.09613 | -121.8933 | 0.10071 | 0.1236 | -121.7148 | -121.8842 | -0.013733 | 0.10986 | -0.027465 | 0.68665 | 0.21057 | 0.10071 | -0.14191 | 0.013733 | -0.15564 | -0.09613 | -0.48065 | -0.16479 | -0.009156 | -0.073242 | 121.8979 | 121.7834 | 117.6819 | -121.8155 | 121.8292 | 121.8521 | 121.6324 | -122.081
641.6562 | 122.0169 | -121.6599 | 0.12817 | -0.0054933 | 0.015118 | 0.06649 | 0.0056355 | 0.064662 | 0.0014441 | -0.00080316 | -0.011673 | -0.0066907 | 0.063497 | 0.064963 | 0.0049005 | -0.0072652 | 0.045776 | -121.0327 | -4.0512 | -121.5042 | 0.1831 | -121.7651 | -121.5958 | -122.2092 | -0.032043 | -121.8658 | 0.09613 | 0.13733 | -121.7377 | -121.9025 | -0.10529 | 0.064087 | 0.054931 | 0.62714 | 0.15564 | 0.091553 | -0.082398 | -0.07782 | -0.24262 | -0.032044 | -0.54932 | -0.20599 | 0.036621 | 0.009155 | 121.843 | 121.7056 | 117.6086 | -121.7239 | 121.756 | 121.7972 | 121.6278 | -122.0306
643.4062 | 122.0215 | -121.6736 | 0.14191 | -0.0054933 | 0.016827 | 0.066917 | 0.0043537 | 0.067225 | 0.0014441 | -0.0012306 | -0.0040437 | -0.0043409 | 0.062002 | 0.067313 | 0.0040461 | -0.0072652 | 0.086975 | -120.9869 | -3.9871 | -121.4584 | 0.17395 | -121.7331 | -121.5958 | -122.1405 | 0.018311 | -121.8063 | 0.082397 | 0.10986 | -121.701 | -121.8887 | -0.059509 | 0.07782 | 0.032043 | 0.68665 | 0.21515 | 0.13733 | -0.054932 | -0.027466 | -0.21515 | -0.05951 | -0.46692 | -0.13275 | 0.082398 | -0.032044 | 121.8475 | 121.7606 | 117.6865 | -121.7377 | 121.756 | 121.7834 | 121.6919 | -122.0306
645.0781 | 122.0261 | -121.6599 | 0.15106 | -0.020752 | 0.018963 | 0.066277 | 0.0041401 | 0.066371 | 0.0010169 | 5.1244e-05 | -0.011673 | -0.0032727 | 0.06307 | 0.066245 | 0.0055415 | -0.0064108 | 0.082397 | -121.0007 | -4.0009 | -121.4767 | 0.16479 | -121.7331 | -121.6049 | -122.1725 | 0.027466 | -121.8063 | 0.068665 | 0.09613 | -121.7194 | -121.9025 | -0.073242 | 0.054932 | 0.013733 | 0.65918 | 0.1831 | 0.12817 | -0.068665 | -0.059509 | -0.24262 | -0.082397 | -0.51269 | -0.14648 | 0.096131 | -0.054932 | 121.8246 | 121.7422 | 117.659 | -121.756 | 121.7285 | 121.756 | 121.6873 | -122.0535
646.8125 | 122.0215 | -121.6873 | 0.13733 | -0.013122 | 0.019604 | 0.066704 | 0.0071307 | 0.067011 | -0.00026494 | -0.0027258 | -0.0040437 | -0.0051953 | 0.062429 | 0.064963 | 0.0012689 | -0.0059836 | -0.027466 | -121.051 | -4.0649 | -121.5317 | 0.16937 | -121.7834 | -121.6415 | -122.2595 | -0.032043 | -121.8887 | 0.068665 | 0.11444 | -121.7697 | -121.9254 | -0.09613 | 0.045776 | 0.032044 | 0.63629 | 0.15564 | 0.10986 | -0.16479 | -0.082397 | -0.23804 | -0.068664 | -0.5722 | -0.20142 | 0.036621 | -0.022888 | 121.8567 | 121.6599 | 117.6224 | -121.7789 | 121.756 | 121.8018 | 121.6553 | -122.0627
648.5469 | 121.9025 | -121.7239 | 0.16022 | -0.0054933 | 0.017895 | 0.067131 | 0.0054217 | 0.067225 | 0.0020849 | 0.00047844 | -0.0040437 | -0.0047681 | 0.063711 | 0.06539 | 0.0038325 | -0.008547 | 0.054932 | -121.0236 | -4.01 | -121.5134 | 0.1236 | -121.7606 | -121.6232 | -122.2137 | -0.027466 | -121.8842 | 0.064087 | 0.07782 | -121.7331 | -121.9254 | -0.036621 | 0.10071 | -0.036621 | 0.70038 | 0.21057 | 0.10986 | -0.10528 | -0.009155 | -0.20142 | -0.09613 | -0.48981 | -0.16022 | 0.041199 | -0.082397 | 121.8475 | 121.7789 | 117.7139 | -121.7834 | 121.788 | 121.8018 | 121.6965 | -122.0856
650.2188 | 121.9803 | -121.7056 | 0.13275 | -0.0054933 | 0.017041 | 0.068199 | 0.0054217 | 0.067652 | 0.00037606 | -0.00016236 | 0.0035858 | -0.0064771 | 0.064138 | 0.067313 | 0.0053279 | -0.0066244 | 0.050354 | -120.9961 | -4.0009 | -121.5134 | 0.13275 | -121.7606 | -121.6141 | -122.2 | 0.018311 | -121.8384 | 0.027466 | 0.091553 | -121.7514 | -121.9116 | -0.054932 | 0.091552 | 0 | 0.70953 | 0.19226 | 0.10071 | -0.082397 | -0.045777 | -0.20599 | -0.10529 | -0.49438 | -0.13275 | 0.073242 | -0.041198 | 121.8384 | 121.756 | 117.7048 | -121.7468 | 121.7331 | 121.7972 | 121.7239 | -122.0444
651.9688 | 122.0078 | -121.6873 | 0.10071 | -0.013122 | 0.012341 | 0.068626 | 0.0084125 | 0.06872 | -0.0077417 | -0.0027258 | -0.019302 | -0.010536 | 0.062856 | 0.062399 | -0.0010809 | -0.0042746 | 0.050354 | -120.932 | -3.9825 | -121.463 | 0.10986 | -121.7468 | -121.6141 | -122.1771 | 0.10986 | -121.7285 | 0.022888 | 0.073242 | -121.7056 | -121.8979 | -0.059509 | 0.073242 | 0.009155 | 0.75531 | 0.2243 | 0.15106 | -0.050354 | -0.01831 | -0.21057 | -0.07782 | -0.48981 | -0.041199 | 0.16937 | -0.027466 | 121.7972 | 121.7377 | 117.7048 | -121.7148 | 121.7102 | 121.7606 | 121.7972 | -121.9986
653.7188 | 121.9986 | -121.7102 | 0.14191 | -0.0054933 | 0.013623 | 0.069054 | 0.0088397 | 0.066371 | -0.0013329 | -0.0035804 | -0.0040437 | -0.0034863 | 0.06072 | 0.065817 | 0.0027643 | -0.0076926 | -0.013733 | -121.0693 | -4.0741 | -121.5546 | 0.14648 | -121.788 | -121.6461 | -122.287 | -0.036621 | -121.8887 | 0.068665 | 0.10529 | -121.7514 | -121.9437 | -0.07782 | 0.064087 | 0.004577 | 0.64087 | 0.15564 | 0.091553 | -0.15564 | -0.041199 | -0.23346 | -0.073242 | -0.57678 | -0.17853 | 0.054932 | -0.036621 | 121.8567 | 121.6965 | 117.6361 | -121.788 | 121.7789 | 121.8155 | 121.6736 | -122.0856
655.4062 | 122.0078 | -121.6873 | 0.13275 | -0.013122 | 0.013836 | 0.072472 | 0.0054217 | 0.064448 | 0.00058966 | -0.002085 | -0.011673 | -0.0051953 | 0.061788 | 0.067313 | 0.0055415 | -0.0061972 | -0.004578 | -121.0785 | -4.0787 | -121.5591 | 0.14648 | -121.7926 | -121.6599 | -122.2916 | -0.059509 | -121.8796 | 0.07782 | 0.10986 | -121.756 | -121.907 | -0.10529 | 0.027466 | 0.013733 | 0.60883 | 0.12817 | 0.10071 | -0.13733 | -0.068664 | -0.21973 | -0.054931 | -0.60425 | -0.19226 | 0.027465 | -0.022888 | 121.8338 | 121.6827 | 117.6086 | -121.7926 | 121.7651 | 121.7972 | 121.6278 | -122.0398
657.1406 | 121.9986 | -121.6919 | 0.1236 | -0.0054933 | 0.014477 | 0.06649 | 0.0037127 | 0.064234 | -0.0041101 | -0.002085 | -0.011673 | -0.0079725 | 0.059652 | 0.064963 | 0.0038325 | -0.0059836 | 0.022888 | -121.0098 | -4.0558 | -121.5179 | 0.1236 | -121.756 | -121.6187 | -122.2321 | 0.013733 | -121.788 | 0.032043 | 0.068665 | -121.701 | -121.907 | -0.064086 | 0.073243 | 0 | 0.68207 | 0.17395 | 0.10071 | -0.10071 | -0.009155 | -0.21515 | -0.091553 | -0.54016 | -0.09613 | 0.11902 | -0.054931 | 121.8155 | 121.7148 | 117.6361 | -121.7422 | 121.7239 | 121.7606 | 121.7056 | -122.0306
658.8906 | 121.9894 | -121.6965 | 0.13733 | -0.0054933 | 0.015973 | 0.066704 | 0.00050847 | 0.066584 | 0.0063575 | -0.00080316 | -0.0040437 | -0.0032727 | 0.059011 | 0.066031 | 0.0066095 | -0.010683 | 0.09613 | -121.019 | -4.0054 | -121.5134 | 0.12817 | -121.7834 | -121.637 | -122.2046 | 0.013733 | -121.8521 | 0.050354 | 0.086975 | -121.7239 | -121.9025 | -0.086975 | 0.059509 | -0.009155 | 0.67749 | 0.1831 | 0.1236 | -0.041199 | -0.027466 | -0.20599 | -0.086975 | -0.50812 | -0.15564 | 0.050354 | -0.050354 | 121.8246 | 121.7926 | 117.691 | -121.7743 | 121.7468 | 121.7834 | 121.7102 | -122.0398
660.5625 | 121.9894 | -121.6919 | 0.13733 | -0.013122 | 0.017682 | 0.065849 | 0.0047809 | 0.064662 | 0.0037939 | 0.00090584 | -0.011673 | -0.0034863 | 0.063925 | 0.063254 | 0.0057551 | -0.007479 | 0.059509 | -121.0236 | -3.9963 | -121.5134 | 0.14191 | -121.7697 | -121.6415 | -122.2046 | 0.013733 | -121.8521 | 0.050354 | 0.091553 | -121.7606 | -121.9208 | -0.077819 | 0.050354 | 0.004578 | 0.66833 | 0.17853 | 0.12817 | -0.07782 | -0.068664 | -0.22888 | -0.086975 | -0.51269 | -0.16022 | 0.068664 | -0.045776 | 121.8338 | 121.7514 | 117.6956 | -121.7789 | 121.7422 | 121.7834 | 121.7056 | -122.0581
662.2969 | 121.9894 | -121.7148 | 0.13275 | -0.020752 | 0.017254 | 0.068413 | 0.0075581 | 0.065516 | -0.0021875 | -0.0012306 | -0.011673 | -0.0069043 | 0.062002 | 0.065604 | 0.0021235 | -0.0066244 | -0.009155 | -121.051 | -4.0604 | -121.5408 | 0.13733 | -121.788 | -121.6461 | -122.2916 | -0.032043 | -121.8933 | 0.059509 | 0.09613 | -121.7834 | -121.9254 | -0.073242 | 0.068665 | 0.004578 | 0.66376 | 0.17395 | 0.10528 | -0.14191 | -0.068664 | -0.21057 | -0.073242 | -0.57678 | -0.17853 | 0.032043 | -0.036621 | 121.8521 | 121.7056 | 117.6544 | -121.7789 | 121.7743 | 121.8109 | 121.6827 | -122.0581
664.0312 | 121.907 | -121.7514 | 0.15106 | -0.020752 | 0.018322 | 0.066704 | 0.0045673 | 0.065516 | 0.0025123 | 0.00047844 | -0.011673 | -0.0030591 | 0.062429 | 0.065604 | 0.0057551 | -0.0083334 | 0.050354 | -121.0464 | -4.0283 | -121.5408 | 0.12817 | -121.7834 | -121.6141 | -122.2412 | -0.045776 | -121.907 | 0.054932 | 0.09613 | -121.7331 | -121.9254 | -0.032043 | 0.13733 | -0.022888 | 0.70496 | 0.21057 | 0.073242 | -0.10071 | 0.018311 | -0.17395 | -0.09613 | -0.48981 | -0.15564 | 0.018311 | -0.054932 | 121.8796 | 121.8018 | 117.7231 | -121.7651 | 121.8063 | 121.8475 | 121.7056 | -122.0764
665.7812 | 121.8933 | -121.7377 | 0.16022 | 0.0021362 | 0.012982 | 0.065636 | 0.0037127 | 0.064875 | -0.0068871 | -0.0027258 | -0.011673 | -0.0090405 | 0.062002 | 0.064749 | 0.0019099 | -0.00577 | 0.013733 | -121.0052 | -4.0558 | -121.5225 | 0.10529 | -121.756 | -121.6049 | -122.2458 | -0.027466 | -121.8292 | 0.018311 | 0.07782 | -121.7239 | -121.8796 | -0.01831 | 0.13275 | -0.054931 | 0.73242 | 0.21515 | 0.082397 | -0.14648 | 0.013733 | -0.14191 | -0.14191 | -0.50812 | -0.091553 | 0.050354 | -0.082397 | 121.843 | 121.7514 | 117.6819 | -121.7651 | 121.756 | 121.8155 | 121.7102 | -122.0398
667.5156 | 121.8842 | -121.7239 | 0.15564 | -0.013122 | 0.011487 | 0.067558 | 0.0013629 | 0.066371 | -0.0026147 | -0.0029394 | -0.011673 | -0.0051953 | 0.059225 | 0.062613 | 0.0038325 | -0.0064108 | 0.09613 | -120.9595 | -4.0009 | -121.4859 | 0.07782 | -121.7377 | -121.6049 | -122.1817 | 0.009155 | -121.7697 | 0.018311 | 0.045776 | -121.7102 | -121.907 | -0.013733 | 0.11902 | -0.07782 | 0.76447 | 0.23804 | 0.11902 | -0.05951 | 0.013733 | -0.1831 | -0.13733 | -0.45776 | -0.045776 | 0.13733 | -0.10986 | 121.8018 | 121.8201 | 117.7231 | -121.7606 | 121.7422 | 121.7697 | 121.7331 | -122.0627
669.1875 | 121.9849 | -121.6919 | 0.09613 | -0.013122 | 0.014477 | 0.069054 | 0.0039265 | 0.064234 | -0.0019739 | -0.003794 | -0.0040437 | -0.0075451 | 0.06072 | 0.063681 | 0.00062806 | -0.006838 | 0.10071 | -120.9457 | -3.978 | -121.4676 | 0.09613 | -121.7239 | -121.6141 | -122.1725 | 0.091553 | -121.7743 | 0.009155 | 0.059509 | -121.7239 | -121.875 | -0.032043 | 0.07782 | 0 | 0.74616 | 0.22431 | 0.14648 | 0.004578 | -0.032043 | -0.1831 | -0.086975 | -0.48065 | -0.082397 | 0.10071 | -0.036621 | 121.788 | 121.7926 | 117.7139 | -121.7102 | 121.7011 | 121.7514 | 121.7834 | -121.9711
670.9375 | 121.8979 | -121.7422 | 0.15106 | -0.020752 | 0.011059 | 0.069908 | 0.0015765 | 0.06573 | -0.0038965 | -0.0040076 | -0.0040437 | -0.0066907 | 0.058157 | 0.063681 | 0.0034051 | -0.0061972 | 0.054932 | -121.019 | -4.0512 | -121.5271 | 0.10986 | -121.7697 | -121.6278 | -122.2275 | -0.022888 | -121.8384 | 0.027466 | 0.059509 | -121.7056 | -121.9116 | -0.027465 | 0.11444 | -0.041199 | 0.72327 | 0.21515 | 0.10071 | -0.09613 | 0.036622 | -0.16937 | -0.1236 | -0.48523 | -0.09613 | 0.073242 | -0.091553 | 121.8521 | 121.7972 | 117.691 | -121.7789 | 121.7697 | 121.8018 | 121.7194 | -122.0627
672.6094 | 121.9345 | -121.7285 | 0.13733 | -0.0054933 | 0.014691 | 0.066063 | 0.0020039 | 0.067866 | 0.0020849 | -0.0027258 | -0.0040437 | -0.0056225 | 0.057516 | 0.064108 | 0.0061823 | -0.006838 | 0.12817 | -120.9824 | -3.9963 | -121.4767 | 0.091553 | -121.7422 | -121.6003 | -122.1451 | 0.032043 | -121.7743 | 0.018311 | 0.045776 | -121.7285 | -121.9116 | -0.013733 | 0.12817 | -0.045776 | 0.74616 | 0.25177 | 0.1236 | -0.009155 | 0 | -0.1831 | -0.11902 | -0.41657 | -0.045776 | 0.13733 | -0.091553 | 121.8201 | 121.8567 | 117.7322 | -121.7377 | 121.7468 | 121.7743 | 121.7606 | -122.0489
674.3594 | 121.9528 | -121.7239 | 0.12817 | -0.0054933 | 0.016186 | 0.066917 | 0.0022175 | 0.065516 | 0.0018713 | -0.002085 | 0.0035858 | -0.0036999 | 0.061361 | 0.064963 | 0.0042597 | -0.0070516 | 0.022888 | -121.0968 | -4.0878 | -121.5546 | 0.13733 | -121.788 | -121.6324 | -122.2321 | -0.068665 | -121.875 | 0.041199 | 0.086975 | -121.7697 | -121.9116 | -0.064087 | 0.091553 | 0.009155 | 0.62714 | 0.16937 | 0.07782 | -0.10529 | -0.045776 | -0.18768 | -0.086975 | -0.50812 | -0.15106 | 0.036621 | -0.041199 | 121.8613 | 121.7468 | 117.6361 | -121.7606 | 121.7651 | 121.8109 | 121.6553 | -122.0398
676.1094 | 121.9391 | -121.7194 | 0.15564 | -0.020752 | 0.014264 | 0.067558 | 0.0060627 | 0.065302 | 0.0014441 | 5.1244e-05 | -0.011673 | -0.0032727 | 0.060507 | 0.065604 | 0.0053279 | -0.0087606 | 0.018311 | -121.1105 | -4.097 | -121.5637 | 0.14191 | -121.7972 | -121.6644 | -122.2641 | -0.09613 | -121.907 | 0.054932 | 0.09613 | -121.7834 | -121.9116 | -0.07782 | 0.054931 | -0.013733 | 0.60882 | 0.15564 | 0.10071 | -0.13733 | -0.064087 | -0.19226 | -0.10071 | -0.54474 | -0.18768 | 0.004578 | -0.05951 | 121.8613 | 121.7377 | 117.6224 | -121.8201 | 121.7743 | 121.8155 | 121.6232 | -122.0673
677.8594 | 121.994 | -121.7148 | 0.1236 | -0.0054933 | 0.0117 | 0.069908 | 0.0043537 | 0.065302 | -0.0045373 | -0.002085 | -0.011673 | -0.010109 | 0.062429 | 0.062827 | 0.0027643 | -0.005129 | 0.022888 | -121.019 | -4.0649 | -121.5271 | 0.10071 | -121.7743 | -121.6232 | -122.2275 | -0.009155 | -121.8063 | 0.027466 | 0.054932 | -121.7102 | -121.9025 | -0.059509 | 0.091553 | -0.022888 | 0.6958 | 0.18768 | 0.09613 | -0.10071 | 0.004578 | -0.18768 | -0.09613 | -0.5127 | -0.091552 | 0.096131 | -0.068664 | 121.8155 | 121.7377 | 117.6498 | -121.7468 | 121.7422 | 121.7697 | 121.7056 | -122.0261
679.5938 | 121.9894 | -121.7194 | 0.12817 | -0.020752 | 0.016186 | 0.070335 | 0.0088397 | 0.067011 | -5.1338e-05 | -0.003794 | -0.0040437 | -0.0039135 | 0.063711 | 0.06539 | 0.0010553 | -0.0081198 | 0.018311 | -121.051 | -4.0604 | -121.5454 | 0.13275 | -121.7926 | -121.6736 | -122.287 | -0.050354 | -121.8887 | 0.064087 | 0.10529 | -121.7743 | -121.9162 | -0.073243 | 0.045776 | 0.004577 | 0.66833 | 0.17395 | 0.12817 | -0.10986 | -0.054932 | -0.19684 | -0.064087 | -0.56763 | -0.16937 | 0.027466 | -0.022888 | 121.8521 | 121.7377 | 117.659 | -121.8018 | 121.7834 | 121.8246 | 121.669 | -122.0444
681.2656 | 122.0261 | -121.6736 | 0.12817 | -0.0054933 | 0.015973 | 0.06884 | 0.0092669 | 0.064875 | -0.0021875 | -0.0027258 | -0.011673 | -0.0086133 | 0.062216 | 0.064536 | 0.0012689 | -0.0076926 | 0.10986 | -120.9366 | -3.9734 | -121.4676 | 0.10071 | -121.7697 | -121.6049 | -122.1634 | 0.10071 | -121.7377 | 0.009155 | 0.041199 | -121.7285 | -121.8613 | -0.09613 | 0.068665 | -0.027466 | 0.737 | 0.20599 | 0.13733 | -0.018311 | -0.054932 | -0.18768 | -0.11902 | -0.48981 | -0.064087 | 0.1236 | -0.086975 | 121.7743 | 121.7834 | 117.7002 | -121.7331 | 121.6827 | 121.7148 | 121.7743 | -121.9894
683 | 121.9254 | -121.6965 | 0.16479 | -0.0054933 | 0.013409 | 0.067772 | 0.0032855 | 0.066798 | 0.0027259 | -0.00080316 | 0.0035858 | -0.0088269 | 0.060293 | 0.066672 | 0.0040461 | -0.011751 | 0.1236 | -120.9457 | -4.01 | -121.4584 | 0.11902 | -121.7422 | -121.582 | -122.1222 | 0.050354 | -121.7697 | 0.027466 | 0.068665 | -121.7056 | -121.8887 | -0.045777 | 0.11444 | -0.045776 | 0.75073 | 0.23804 | 0.1236 | -0.041199 | -0.009155 | -0.19226 | -0.13733 | -0.42572 | -0.073242 | 0.11902 | -0.09613 | 121.8155 | 121.8201 | 117.6865 | -121.7468 | 121.7239 | 121.7651 | 121.7468 | -122.0535
684.75 | 121.9482 | -121.7285 | 0.13733 | -0.0054933 | 0.015332 | 0.069054 | 0.0056355 | 0.065089 | -0.00026494 | -0.0031532 | -0.0040437 | -0.0081861 | 0.063711 | 0.064749 | 0.00084166 | -0.0070516 | 0.027466 | -121.0327 | -4.0787 | -121.5363 | 0.12817 | -121.756 | -121.6095 | -122.2412 | -0.032043 | -121.8338 | 0.009155 | 0.050354 | -121.7422 | -121.907 | -0.027465 | 0.11902 | -0.009155 | 0.6958 | 0.19226 | 0.073242 | -0.10986 | -0.013733 | -0.17853 | -0.12817 | -0.5127 | -0.10528 | 0.073242 | -0.086975 | 121.8567 | 121.756 | 117.6498 | -121.7468 | 121.7377 | 121.7789 | 121.6965 | -122.0444
686.4219 | 122.0261 | -121.6965 | 0.11444 | -0.013122 | 0.012341 | 0.069481 | 0.0058491 | 0.064875 | -0.0028283 | -0.0031532 | 0.0035858 | -0.0058361 | 0.062643 | 0.064322 | 0.0025507 | -0.0083334 | 0.064087 | -121.0144 | -4.0466 | -121.4996 | 0.10529 | -121.756 | -121.6187 | -122.1954 | 0.018311 | -121.7972 | 0.036621 | 0.059509 | -121.7377 | -121.907 | -0.059509 | 0.07782 | -0.009155 | 0.68207 | 0.19684 | 0.11902 | -0.050354 | -0.041199 | -0.21057 | -0.07782 | -0.49896 | -0.10071 | 0.10986 | -0.054932 | 121.8018 | 121.7606 | 117.6498 | -121.7331 | 121.7331 | 121.756 | 121.7148 | -122.0215
688.1562 | 122.0123 | -121.7102 | 0.11444 | -0.0054933 | 0.012982 | 0.069054 | 0.0064899 | 0.06573 | 0.00080326 | -0.002085 | -0.0040437 | -0.0062635 | 0.060079 | 0.066885 | 0.0034051 | -0.008547 | 0.14648 | -120.9366 | -3.978 | -121.4676 | 0.10071 | -121.7697 | -121.6187 | -122.168 | 0.082397 | -121.788 | 0.009155 | 0.050354 | -121.7285 | -121.8796 | -0.059509 | 0.091553 | -0.013733 | 0.77362 | 0.24262 | 0.15106 | 0.032043 | -0.018311 | -0.16937 | -0.10529 | -0.45776 | -0.07782 | 0.091553 | -0.064087 | 121.8109 | 121.8567 | 117.7322 | -121.7331 | 121.7194 | 121.7606 | 121.7926 | -121.994
689.9062 | 122.0078 | -121.7285 | 0.11902 | -0.013122 | 0.013409 | 0.067345 | 0.0037127 | 0.064662 | 0.0022987 | -0.0014442 | -0.011673 | -0.0045545 | 0.061148 | 0.06539 | 0.0042597 | -0.0079062 | 0.004578 | -121.0785 | -4.0833 | -121.55 | 0.15106 | -121.7972 | -121.6553 | -122.2778 | -0.064087 | -121.9162 | 0.082397 | 0.091553 | -121.7926 | -121.9345 | -0.068664 | 0.073243 | 0.032043 | 0.65002 | 0.17853 | 0.10528 | -0.11444 | -0.064087 | -0.20599 | -0.036622 | -0.54932 | -0.18768 | 0.01831 | -0.027466 | 121.8796 | 121.7331 | 117.6453 | -121.7743 | 121.8109 | 121.8201 | 121.6644 | -122.0535
691.5781 | 122.0261 | -121.6965 | 0.1236 | -0.013122 | 0.016613 | 0.070549 | 0.0067035 | 0.065089 | 0.0016577 | -0.0018714 | -0.019302 | -0.0039135 | 0.062216 | 0.064749 | 0.0053279 | -0.0089742 | 0 | -121.0922 | -4.0833 | -121.5591 | 0.16479 | -121.8155 | -121.6782 | -122.2824 | -0.054932 | -121.9162 | 0.073242 | 0.10071 | -121.7697 | -121.9162 | -0.11902 | 0.01831 | 0.041199 | 0.60425 | 0.13733 | 0.11902 | -0.1236 | -0.073242 | -0.21973 | -0.050354 | -0.58594 | -0.21973 | 0 | -0.022888 | 121.8613 | 121.6965 | 117.6132 | -121.8018 | 121.7697 | 121.7972 | 121.6415 | -122.0398
693.3281 | 121.9711 | -121.7331 | 0.14191 | -0.0054933 | 0.014477 | 0.067345 | 0.00050847 | 0.065943 | 0.0012305 | -0.0016578 | -0.011673 | -0.0043409 | 0.06072 | 0.066031 | 0.0089593 | -0.0083334 | 0.045776 | -121.0464 | -4.0878 | -121.55 | 0.13733 | -121.7834 | -121.6415 | -122.1909 | -0.036621 | -121.8475 | 0.022888 | 0.086975 | -121.7422 | -121.8842 | -0.050354 | 0.091552 | -0.004578 | 0.68664 | 0.1831 | 0.091553 | -0.096131 | -0.009156 | -0.15106 | -0.11902 | -0.45776 | -0.11444 | 0.036621 | -0.054932 | 121.8704 | 121.7789 | 117.6453 | -121.7834 | 121.756 | 121.8201 | 121.6965 | -122.0261
695.0156 | 121.9254 | -121.7514 | 0.17395 | -0.013122 | 0.014691 | 0.06649 | 0.0058491 | 0.06808 | 0.00037606 | -0.00037596 | -0.0040437 | -0.0075451 | 0.062216 | 0.066458 | 0.0029779 | -0.00577 | 0.11902 | -120.9549 | -4.0009 | -121.4859 | 0.10986 | -121.7285 | -121.6049 | -122.1497 | 0.036621 | -121.7697 | 0.018311 | 0.054932 | -121.7194 | -121.8796 | 0.022888 | 0.14648 | -0.064087 | 0.79651 | 0.2655 | 0.11902 | -0.054931 | 0.032044 | -0.12817 | -0.15564 | -0.39825 | -0.01831 | 0.10986 | -0.11902 | 121.8613 | 121.8704 | 117.7505 | -121.7789 | 121.7697 | 121.8063 | 121.788 | -122.0535
696.75 | 121.9254 | -121.7514 | 0.15106 | -0.013122 | 0.017041 | 0.067345 | 0.00093567 | 0.064875 | 0.0025123 | 0.001333 | -0.019302 | -0.0013501 | 0.061361 | 0.064536 | 0.0076777 | -0.0076926 | -0.013733 | -121.1472 | -4.1382 | -121.5775 | 0.14648 | -121.8155 | -121.6644 | -122.2641 | -0.11444 | -121.9299 | 0.050354 | 0.11444 | -121.7606 | -121.9437 | -0.064087 | 0.086975 | -0.004578 | 0.60425 | 0.17395 | 0.086975 | -0.16479 | -0.009155 | -0.19226 | -0.10071 | -0.5127 | -0.17853 | 0.013733 | -0.036621 | 121.8979 | 121.7377 | 117.6132 | -121.8155 | 121.8018 | 121.8658 | 121.637 | -122.0947
698.5 | 121.9666 | -121.7239 | 0.13275 | 0.0021362 | 0.012982 | 0.069267 | 0.0073443 | 0.065302 | -0.0041101 | -0.0016578 | -0.011673 | -0.0086133 | 0.060293 | 0.064108 | 0.00041446 | -0.0064108 | 0.013733 | -121.0373 | -4.0787 | -121.5271 | 0.11444 | -121.7697 | -121.6415 | -122.2275 | -0.004578 | -121.8384 | 0.018311 | 0.064087 | -121.7285 | -121.8887 | -0.045776 | 0.082397 | -0.01831 | 0.68665 | 0.19684 | 0.11444 | -0.11902 | -0.004578 | -0.16479 | -0.11444 | -0.50354 | -0.11444 | 0.050354 | -0.068664 | 121.8384 | 121.7377 | 117.6453 | -121.7743 | 121.7422 | 121.788 | 121.7194 | -122.0215
700.2344 | 121.994 | -121.6827 | 0.13275 | -0.013122 | 0.01405 | 0.067131 | 0.0079853 | 0.065943 | -0.00069214 | -0.00058956 | -0.0040437 | -0.0071179 | 0.061361 | 0.065817 | 0.00062806 | -0.0087606 | 0.07782 | -120.9503 | -4.0192 | -121.4722 | 0.1236 | -121.756 | -121.5958 | -122.2183 | 0.045776 | -121.8063 | 0.032043 | 0.086975 | -121.7606 | -121.9116 | -0.073242 | 0.086975 | -0.009155 | 0.73242 | 0.21057 | 0.1236 | -0.054931 | -0.07782 | -0.22888 | -0.10071 | -0.53558 | -0.1236 | 0.10529 | -0.045776 | 121.8063 | 121.7606 | 117.6636 | -121.7285 | 121.7148 | 121.7697 | 121.7285 | -122.0444
701.9219 | 121.9849 | -121.7148 | 0.15106 | -0.0054933 | 0.017041 | 0.065636 | 0.0037127 | 0.067652 | 0.0055029 | -0.0029394 | 0.0035858 | -0.0034863 | 0.063284 | 0.064536 | 0.0068231 | -0.0081198 | 0.082397 | -121.0007 | -4.0421 | -121.5271 | 0.13733 | -121.7926 | -121.6324 | -122.2092 | 0 | -121.8658 | 0.050354 | 0.091553 | -121.7789 | -121.9299 | -0.07782 | 0.082398 | -0.013733 | 0.71411 | 0.18768 | 0.10528 | -0.068665 | -0.064087 | -0.21515 | -0.10071 | -0.49438 | -0.15106 | 0.064087 | -0.059509 | 121.8521 | 121.7972 | 117.6727 | -121.7834 | 121.7651 | 121.8063 | 121.7148 | -122.081
703.6719 | 121.9345 | -121.7285 | 0.16937 | -0.0054933 | 0.014905 | 0.067345 | 0.0013629 | 0.066157 | 0.0010169 | -0.00058956 | -0.0040437 | -0.0045545 | 0.060934 | 0.064963 | 0.0070367 | -0.0059836 | 0.004578 | -121.0968 | -4.1473 | -121.5683 | 0.14648 | -121.8018 | -121.6507 | -122.2687 | -0.09613 | -121.907 | 0.059509 | 0.091553 | -121.7789 | -121.9391 | -0.073242 | 0.07782 | -0.022889 | 0.63171 | 0.16022 | 0.082398 | -0.16479 | -0.050354 | -0.21057 | -0.10986 | -0.54016 | -0.17853 | 0.032044 | -0.07782 | 121.875 | 121.7331 | 117.5812 | -121.8201 | 121.788 | 121.8201 | 121.6324 | -122.1085
705.4219 | 121.907 | -121.7422 | 0.17853 | -0.020752 | 0.011487 | 0.069908 | 0.0026447 | 0.062739 | -0.0062463 | -0.0016578 | 0.0035858 | -0.0098951 | 0.060293 | 0.062399 | 0.0046869 | -0.0066244 | 0.050354 | -120.9915 | -4.0604 | -121.5271 | 0.086975 | -121.7651 | -121.6187 | -122.2412 | -0.013733 | -121.8292 | 0.013733 | 0.054932 | -121.7331 | -121.9162 | -0.022888 | 0.1236 | -0.091553 | 0.75073 | 0.21515 | 0.091552 | -0.12817 | 0.009156 | -0.17395 | -0.16479 | -0.49896 | -0.086975 | 0.086975 | -0.1236 | 121.8292 | 121.7926 | 117.6819 | -121.7972 | 121.756 | 121.7972 | 121.7285 | -122.0947
707.1406 | 122.0352 | -121.7102 | 0.10071 | -0.0054933 | 0.019177 | 0.06649 | 0.0084125 | 0.067011 | 0.00058966 | -0.0014442 | -0.011673 | -0.0030591 | 0.063284 | 0.067526 | 0.0025507 | -0.006838 | -0.009155 | -121.1105 | -4.1107 | -121.5683 | 0.15106 | -121.8109 | -121.6782 | -122.2778 | -0.050354 | -121.907 | 0.068665 | 0.07782 | -121.7697 | -121.9482 | -0.10071 | 0.032043 | 0.050354 | 0.59967 | 0.14191 | 0.10986 | -0.10986 | -0.059509 | -0.23804 | -0.032043 | -0.56763 | -0.19684 | 0.041199 | -0.022888 | 121.8613 | 121.701 | 117.5995 | -121.7789 | 121.7789 | 121.788 | 121.6599 | -122.0489
708.875 | 121.994 | -121.7102 | 0.13275 | -0.013122 | 0.016613 | 0.067345 | 0.0071307 | 0.067866 | -0.0038965 | -0.0042212 | -0.011673 | -0.0081861 | 0.062216 | 0.064536 | 0.00084166 | -0.0072652 | 0.064087 | -120.9595 | -4.0192 | -121.4951 | 0.10986 | -121.7834 | -121.6415 | -122.2458 | 0.018311 | -121.8475 | 0.045776 | 0.091553 | -121.756 | -121.9345 | -0.073242 | 0.068664 | -0.022888 | 0.75073 | 0.21515 | 0.14648 | -0.068664 | -0.045776 | -0.2243 | -0.086975 | -0.53558 | -0.13733 | 0.086975 | -0.041198 | 121.8201 | 121.7743 | 117.691 | -121.7743 | 121.756 | 121.8018 | 121.7285 | -122.0673
710.5469 | 121.9116 | -121.7331 | 0.15564 | -0.0054933 | 0.010632 | 0.070976 | 0.0049945 | 0.06808 | -0.0019739 | -0.00037596 | -0.0040437 | -0.0073315 | 0.060079 | 0.066031 | 0.0034051 | -0.007479 | 0.10071 | -120.9595 | -4.0283 | -121.4905 | 0.10529 | -121.756 | -121.6049 | -122.2092 | 0.013733 | -121.7834 | 0.022888 | 0.050354 | -121.7422 | -121.9162 | -0.022888 | 0.12817 | -0.050354 | 0.77362 | 0.24261 | 0.11444 | -0.054932 | -0.009156 | -0.18311 | -0.13275 | -0.47607 | -0.050354 | 0.13275 | -0.10529 | 121.8384 | 121.8338 | 117.7048 | -121.7606 | 121.756 | 121.7834 | 121.7468 | -122.0718
712.2812 | 121.9208 | -121.756 | 0.16937 | -0.020752 | 0.017041 | 0.068199 | 0.0049945 | 0.066157 | 0.0055029 | -0.00058956 | -0.019302 | -0.0039135 | 0.063497 | 0.066458 | 0.0068231 | -0.0079062 | 0.041199 | -121.0602 | -4.0833 | -121.5408 | 0.16479 | -121.8018 | -121.6232 | -122.2412 | -0.054932 | -121.9162 | 0.068665 | 0.10071 | -121.7743 | -121.9345 | -0.045777 | 0.13275 | -0.004578 | 0.6958 | 0.21515 | 0.082397 | -0.12817 | -0.018311 | -0.17853 | -0.10071 | -0.48523 | -0.16022 | 0.01831 | -0.068665 | 121.9208 | 121.7972 | 117.6727 | -121.7926 | 121.8246 | 121.8567 | 121.701 | -122.1039
714 | 122.0306 | -121.6919 | 0.12817 | -0.013122 | 0.014264 | 0.067772 | 0.0081989 | 0.064448 | -0.0041101 | -0.0022986 | -0.011673 | -0.0098951 | 0.060934 | 0.064963 | 0.0012689 | -0.0072652 | 0.10986 | -120.9045 | -4.01 | -121.4767 | 0.11444 | -121.7834 | -121.6095 | -122.1954 | 0.082397 | -121.7514 | 0.027466 | 0.059509 | -121.7239 | -121.8842 | -0.091552 | 0.082398 | -0.013733 | 0.78735 | 0.21515 | 0.13275 | -0.018311 | -0.032043 | -0.19226 | -0.10071 | -0.50354 | -0.059509 | 0.13275 | -0.068665 | 121.8063 | 121.8018 | 117.6819 | -121.7377 | 121.7194 | 121.7514 | 121.7743 | -122.0123
715.6875 | 121.9666 | -121.7422 | 0.16937 | -0.0054933 | 0.016827 | 0.070122 | 0.0011493 | 0.065302 | 0.0048621 | -0.0012306 | -0.0040437 | -0.0026319 | 0.060934 | 0.066672 | 0.0066095 | -0.0076926 | 0.004578 | -121.0968 | -4.1382 | -121.5775 | 0.16479 | -121.7926 | -121.6599 | -122.2778 | -0.10986 | -121.9391 | 0.068665 | 0.086975 | -121.7651 | -121.9208 | -0.050354 | 0.082398 | -0.004578 | 0.64545 | 0.16479 | 0.082397 | -0.16479 | -0.022888 | -0.17853 | -0.10071 | -0.53558 | -0.19684 | -0.018311 | -0.082398 | 121.907 | 121.7468 | 117.6041 | -121.8292 | 121.8109 | 121.8292 | 121.6324 | -122.0901
717.4375 | 122.0444 | -121.6965 | 0.13275 | -0.013122 | 0.016827 | 0.067772 | 0.0049945 | 0.067225 | 0.00080326 | 0.00069204 | 0.0035858 | -0.0036999 | 0.062216 | 0.066245 | 0.0078913 | -0.0072652 | 0.041199 | -121.0236 | -4.0833 | -121.5225 | 0.14648 | -121.7789 | -121.6507 | -122.2275 | 0.004578 | -121.8613 | 0.068665 | 0.068665 | -121.7514 | -121.9299 | -0.082398 | 0.045776 | 0.013733 | 0.67291 | 0.17395 | 0.12817 | -0.091552 | -0.054932 | -0.23346 | -0.064086 | -0.53101 | -0.16479 | 0.068665 | -0.064086 | 121.843 | 121.7377 | 117.6132 | -121.7834 | 121.7651 | 121.7651 | 121.701 | -122.0627
719.1875 | 121.907 | -121.7331 | 0.16937 | -0.0054933 | 0.017254 | 0.067131 | 0.0045673 | 0.064662 | 0.0033667 | 0.00026484 | -0.019302 | -0.0034863 | 0.061361 | 0.06539 | 0.0068231 | -0.0070516 | 0.022888 | -121.0876 | -4.1061 | -121.5637 | 0.1236 | -121.7972 | -121.669 | -122.2687 | -0.07782 | -121.9254 | 0.064087 | 0.10071 | -121.7514 | -121.9437 | -0.064087 | 0.064087 | -0.045777 | 0.64545 | 0.16937 | 0.10528 | -0.14649 | -0.018311 | -0.21057 | -0.10529 | -0.53558 | -0.19226 | 0.018311 | -0.068665 | 121.8567 | 121.756 | 117.627 | -121.8384 | 121.7972 | 121.8338 | 121.6553 | -122.113
720.9375 | 122.0215 | -121.6782 | 0.12817 | -0.0054933 | 0.01875 | 0.065422 | 0.0067035 | 0.06338 | 0.0010169 | 0.00047844 | -0.019302 | -0.0036999 | 0.062002 | 0.066672 | 0.0025507 | -0.006838 | 0.050354 | -121.0464 | -4.0695 | -121.5225 | 0.13275 | -121.788 | -121.669 | -122.2229 | 0.018311 | -121.8567 | 0.073242 | 0.10529 | -121.7789 | -121.9391 | -0.10986 | 0.009156 | 0.004577 | 0.63171 | 0.15564 | 0.14648 | -0.07782 | -0.10071 | -0.26093 | -0.054932 | -0.54474 | -0.17853 | 0.082398 | -0.022888 | 121.8109 | 121.7285 | 117.6086 | -121.7972 | 121.7514 | 121.7834 | 121.6965 | -122.0673
722.6094 | 122.0398 | -121.6782 | 0.11902 | -0.020752 | 0.019818 | 0.06649 | 0.0067035 | 0.064875 | 0.00037606 | -0.0010168 | -0.0040437 | -0.0060497 | 0.066061 | 0.064108 | 0.0027643 | -0.0079062 | 0.036621 | -121.0419 | -4.0741 | -121.5317 | 0.14648 | -121.8018 | -121.6644 | -122.2366 | 0.009155 | -121.8567 | 0.068665 | 0.10071 | -121.7697 | -121.9162 | -0.1236 | 0.013733 | 0.027465 | 0.63629 | 0.14648 | 0.13275 | -0.082398 | -0.091552 | -0.23804 | -0.050354 | -0.55847 | -0.17853 | 0.05951 | -0.018311 | 121.8246 | 121.7148 | 117.6041 | -121.7834 | 121.7468 | 121.7789 | 121.6873 | -122.0352
724.3438 | 122.0215 | -121.7331 | 0.13733 | -0.0054933 | 0.016613 | 0.069481 | 0.0054217 | 0.064021 | -0.0041101 | -0.0022986 | -0.019302 | -0.0071179 | 0.064565 | 0.064108 | -0.00086734 | -0.0049154 | 0.07782 | -120.9503 | -4.0237 | -121.4905 | 0.10529 | -121.7606 | -121.637 | -122.2229 | 0.086975 | -121.8018 | 0.032043 | 0.07782 | -121.7606 | -121.9162 | -0.027466 | 0.09613 | -0.032043 | 0.78278 | 0.24261 | 0.14648 | -0.059509 | -0.027466 | -0.18311 | -0.10529 | -0.48981 | -0.068665 | 0.11444 | -0.059509 | 121.8384 | 121.8109 | 117.7094 | -121.7743 | 121.7651 | 121.8109 | 121.8201 | -122.0535
726.0938 | 122.0169 | -121.6873 | 0.1236 | -0.013122 | 0.015332 | 0.067772 | 0.0086261 | 0.068507 | -0.0058191 | -0.0027258 | -0.0040437 | -0.0075451 | 0.061788 | 0.065176 | 0.00041446 | -0.007479 | 0.086975 | -120.9183 | -4.0329 | -121.4584 | 0.11444 | -121.7651 | -121.637 | -122.1863 | 0.082397 | -121.7697 | 0.009155 | 0.054932 | -121.7331 | -121.9162 | -0.07782 | 0.050354 | -0.009155 | 0.76904 | 0.22888 | 0.17853 | -0.036621 | -0.045776 | -0.22888 | -0.11444 | -0.49896 | -0.082397 | 0.14649 | -0.068664 | 121.8018 | 121.7743 | 117.6544 | -121.7606 | 121.6965 | 121.7422 | 121.7697 | -122.0398
727.8438 | 121.9894 | -121.701 | 0.14648 | -0.013122 | 0.020459 | 0.065849 | 0.0020039 | 0.067866 | 0.0031531 | -0.00016236 | -0.0040437 | -0.0026319 | 0.062856 | 0.067953 | 0.0055415 | -0.0091878 | 0.091553 | -121.019 | -4.0649 | -121.5317 | 0.1236 | -121.7926 | -121.6644 | -122.2229 | 0.013733 | -121.8704 | 0.07782 | 0.082397 | -121.7651 | -121.9345 | -0.091553 | 0.036621 | -0.022888 | 0.68207 | 0.16937 | 0.13275 | -0.054931 | -0.064087 | -0.23346 | -0.068664 | -0.52185 | -0.16937 | 0.064087 | -0.064087 | 121.8246 | 121.7926 | 117.6361 | -121.8109 | 121.7789 | 121.7834 | 121.7148 | -122.081
729.5156 | 121.9025 | -121.7331 | 0.16022 | 0.0021362 | 0.012555 | 0.070763 | 0.0020039 | 0.06573 | -0.0013329 | -0.00037596 | -0.011673 | -0.0090405 | 0.059439 | 0.067099 | 0.0034051 | -0.0059836 | 0.082397 | -120.9595 | -4.0512 | -121.5042 | 0.09613 | -121.788 | -121.6232 | -122.2092 | 0.018311 | -121.8018 | 0.013733 | 0.068665 | -121.7606 | -121.9162 | -0.054932 | 0.10986 | -0.064087 | 0.77362 | 0.22888 | 0.11902 | -0.07782 | -0.027466 | -0.18311 | -0.14648 | -0.47607 | -0.068665 | 0.11444 | -0.091552 | 121.8292 | 121.8155 | 117.6819 | -121.7834 | 121.7468 | 121.8018 | 121.7514 | -122.0764
731.25 | 121.9299 | -121.7377 | 0.15106 | -0.013122 | 0.018109 | 0.069695 | 0.0028583 | 0.066584 | 0.0029395 | -0.0022986 | -0.0040437 | -0.0049817 | 0.062216 | 0.063895 | 0.0055415 | -0.0066244 | 0 | -121.138 | -4.1748 | -121.5912 | 0.16022 | -121.7972 | -121.6965 | -122.287 | -0.10071 | -121.9391 | 0.068665 | 0.10529 | -121.7606 | -121.9528 | -0.059509 | 0.041199 | 0.009155 | 0.59967 | 0.14648 | 0.10528 | -0.15106 | -0.022888 | -0.21515 | -0.082397 | -0.54932 | -0.20142 | 0.013733 | -0.045776 | 121.8979 | 121.7377 | 117.5629 | -121.8475 | 121.8063 | 121.843 | 121.637 | -122.1039
733.0156 | 121.9391 | -121.7606 | 0.13733 | 0.0021362 | 0.016613 | 0.068626 | 0.0037127 | 0.064448 | 0.0020849 | -0.00058956 | -0.011673 | -0.0041271 | 0.060507 | 0.063467 | 0.0046869 | -0.0061972 | -0.009155 | -121.1472 | -4.1611 | -121.5912 | 0.15564 | -121.7972 | -121.6507 | -122.3007 | -0.11444 | -121.9254 | 0.073242 | 0.10071 | -121.8063 | -121.9345 | -0.036621 | 0.10986 | 0.018311 | 0.6134 | 0.16937 | 0.059509 | -0.14648 | -0.045776 | -0.17395 | -0.064087 | -0.54016 | -0.16479 | 0.009155 | -0.036621 | 121.9162 | 121.7514 | 117.5995 | -121.788 | 121.8338 | 121.8613 | 121.6461 | -122.0718
734.7031 | 121.9162 | -121.7651 | 0.16022 | 0.0021362 | 0.013196 | 0.070763 | 0.0049945 | 0.06573 | -0.0045373 | -0.0022986 | 0.0035858 | -0.010536 | 0.061361 | 0.061972 | 0.0021235 | -0.005129 | 0.064087 | -120.9915 | -4.0833 | -121.5363 | 0.10071 | -121.756 | -121.6049 | -122.2504 | -0.018311 | -121.8246 | 0.013733 | 0.07782 | -121.7422 | -121.9254 | 0.009156 | 0.16022 | -0.059509 | 0.77362 | 0.22888 | 0.068664 | -0.09613 | 0.022888 | -0.16022 | -0.14648 | -0.48523 | -0.059509 | 0.10071 | -0.082397 | 121.8658 | 121.8292 | 117.6819 | -121.7651 | 121.7789 | 121.843 | 121.7468 | -122.0856
736.4531 | 121.9208 | -121.7606 | 0.16479 | -0.013122 | 0.016186 | 0.066704 | 0.0032855 | 0.064448 | 0.0040077 | -0.002085 | -0.011673 | -0.0019909 | 0.062216 | 0.064749 | 0.0070367 | -0.0079062 | 0.004578 | -121.1105 | -4.1519 | -121.5866 | 0.13275 | -121.7926 | -121.6644 | -122.2961 | -0.10986 | -121.9528 | 0.054932 | 0.1236 | -121.7789 | -121.9666 | -0.032044 | 0.09613 | -0.032044 | 0.65002 | 0.17395 | 0.07782 | -0.16022 | -0.018311 | -0.20599 | -0.10986 | -0.53558 | -0.19226 | 0.013733 | -0.041199 | 121.8933 | 121.7651 | 117.6086 | -121.8292 | 121.8155 | 121.8842 | 121.6507 | -122.1313
738.2031 | 121.9208 | -121.7468 | 0.16022 | -0.0054933 | 0.015545 | 0.066704 | 0.0030719 | 0.067011 | 0.0029395 | 0.00047844 | -0.011673 | -0.0032727 | 0.064352 | 0.067099 | 0.0049005 | -0.0072652 | 0.004578 | -121.1151 | -4.1245 | -121.5683 | 0.15106 | -121.7789 | -121.6736 | -122.3053 | -0.10986 | -121.9666 | 0.07782 | 0.09613 | -121.8155 | -121.9482 | -0.032044 | 0.073242 | -0.009155 | 0.63171 | 0.17853 | 0.10529 | -0.15564 | -0.068665 | -0.20142 | -0.082397 | -0.55847 | -0.21973 | -0.018311 | -0.064087 | 121.8979 | 121.7514 | 117.6224 | -121.8338 | 121.8246 | 121.843 | 121.637 | -122.1085
739.9531 | 121.962 | -121.7468 | 0.15106 | -0.0054933 | 0.016613 | 0.067345 | 0.0056355 | 0.064448 | -0.0011193 | 0.0015466 | -0.011673 | -0.0071179 | 0.063925 | 0.066458 | 0.0034051 | -0.006838 | 0 | -121.1151 | -4.1611 | -121.5683 | 0.13275 | -121.7972 | -121.6507 | -122.3053 | -0.086975 | -121.8979 | 0.064087 | 0.091553 | -121.7651 | -121.9299 | -0.050354 | 0.09613 | -0.018311 | 0.63171 | 0.17853 | 0.082398 | -0.15106 | -0.018311 | -0.18311 | -0.086975 | -0.55847 | -0.15106 | 0.032044 | -0.059509 | 121.8796 | 121.7468 | 117.5858 | -121.8018 | 121.8109 | 121.8384 | 121.6599 | -122.081
741.625 | 121.9254 | -121.7468 | 0.15106 | -0.0054933 | 0.01875 | 0.067345 | 0.0034991 | 0.062525 | 0.0014441 | -0.00037596 | -0.019302 | -0.0036999 | 0.06072 | 0.066245 | 0.0053279 | -0.0072652 | 0 | -121.1517 | -4.1656 | -121.6003 | 0.15106 | -121.8155 | -121.6599 | -122.3099 | -0.12817 | -121.9391 | 0.054932 | 0.09613 | -121.7606 | -121.9437 | -0.068665 | 0.086975 | 0 | 0.59509 | 0.14648 | 0.059509 | -0.15106 | -0.013733 | -0.19684 | -0.09613 | -0.56305 | -0.19226 | 0.004578 | -0.054932 | 121.8979 | 121.7468 | 117.5812 | -121.8109 | 121.8018 | 121.843 | 121.6187 | -122.0947
743.3594 | 121.9894 | -121.7239 | 0.14191 | -0.0054933 | 0.016613 | 0.067131 | 0.0028583 | 0.065943 | 0.0014441 | -0.00058956 | -0.011673 | -0.0062635 | 0.059439 | 0.064536 | 0.0057551 | -0.0064108 | 0.004578 | -121.0831 | -4.1519 | -121.5683 | 0.15564 | -121.8201 | -121.669 | -122.2549 | -0.059509 | -121.8796 | 0.050354 | 0.07782 | -121.7743 | -121.9391 | -0.09613 | 0.054932 | 0.013733 | 0.64087 | 0.15564 | 0.10071 | -0.13733 | -0.050354 | -0.21515 | -0.091553 | -0.53101 | -0.15564 | 0.059509 | -0.064087 | 121.8796 | 121.7285 | 117.572 | -121.8109 | 121.7743 | 121.8018 | 121.6644 | -122.081
745.0938 | 121.9528 | -121.7468 | 0.16022 | -0.013122 | 0.0164 | 0.068413 | 0.0062763 | 0.065943 | 0.0014441 | -0.0022986 | -0.019302 | -0.0056225 | 0.059439 | 0.063467 | 0.0053279 | -0.0079062 | -0.018311 | -121.1288 | -4.1748 | -121.582 | 0.14191 | -121.8063 | -121.6782 | -122.3099 | -0.10986 | -121.9391 | 0.07782 | 0.09613 | -121.8109 | -121.9528 | -0.059509 | 0.068664 | -0.01831 | 0.61798 | 0.16479 | 0.096131 | -0.17853 | -0.064087 | -0.20599 | -0.082397 | -0.56305 | -0.19226 | 0.013733 | -0.064087 | 121.8887 | 121.7285 | 117.572 | -121.8384 | 121.8246 | 121.843 | 121.637 | -122.113
746.8281 | 122.0673 | -121.7056 | 0.12817 | -0.0054933 | 0.017895 | 0.06884 | 0.0054217 | 0.065089 | 0.0012305 | -0.0012306 | -0.026932 | -0.0054089 | 0.062216 | 0.065176 | 0.0023371 | -0.006838 | -0.013733 | -121.0785 | -4.1473 | -121.5683 | 0.15564 | -121.788 | -121.6736 | -122.3007 | -0.054932 | -121.9208 | 0.064087 | 0.082397 | -121.7972 | -121.9345 | -0.082398 | 0.032043 | 0.027466 | 0.62714 | 0.13733 | 0.10529 | -0.14191 | -0.091553 | -0.22888 | -0.064087 | -0.59509 | -0.21515 | 0.013733 | -0.045777 | 121.8613 | 121.6919 | 117.5583 | -121.8018 | 121.7697 | 121.788 | 121.6507 | -122.0627
748.5156 | 121.9894 | -121.7239 | 0.12817 | -0.013122 | 0.013623 | 0.069908 | 0.0054217 | 0.065302 | -0.0071007 | -0.0033668 | -0.0040437 | -0.0088269 | 0.062002 | 0.063254 | 0.00084166 | -0.005129 | 0.009155 | -121.0281 | -4.1519 | -121.5408 | 0.10529 | -121.7606 | -121.6415 | -122.2595 | -0.018311 | -121.8384 | 0.036621 | 0.064087 | -121.7514 | -121.9208 | -0.036621 | 0.082397 | -0.022888 | 0.6958 | 0.1831 | 0.10071 | -0.11902 | -0.027466 | -0.19684 | -0.091553 | -0.53558 | -0.11444 | 0.082397 | -0.064087 | 121.8292 | 121.7331 | 117.572 | -121.7697 | 121.7606 | 121.788 | 121.7056 | -122.049
750.25 | 121.9803 | -121.7285 | 0.15106 | -0.013122 | 0.017468 | 0.067558 | 0.0054217 | 0.064021 | 0.00016226 | -0.002085 | -0.0040437 | -0.0077587 | 0.06307 | 0.066245 | 0.0040461 | -0.0094016 | 0.054932 | -121.0556 | -4.1382 | -121.5546 | 0.1236 | -121.7697 | -121.6415 | -122.2092 | -0.032043 | -121.8338 | 0.027466 | 0.064087 | -121.756 | -121.9208 | -0.041198 | 0.086975 | -0.027466 | 0.67291 | 0.17395 | 0.086976 | -0.09613 | -0.027465 | -0.19226 | -0.1236 | -0.48065 | -0.10528 | 0.086975 | -0.086975 | 121.8521 | 121.7834 | 117.5903 | -121.7926 | 121.756 | 121.7926 | 121.6965 | -122.0718
751.9375 | 121.9528 | -121.7514 | 0.15106 | -0.020752 | 0.015973 | 0.067558 | 0.0022175 | 0.064875 | 0.0027259 | -0.0014442 | -0.011673 | -0.0036999 | 0.06072 | 0.064108 | 0.0061823 | -0.0070516 | 0 | -121.1517 | -4.184 | -121.6095 | 0.16022 | -121.7834 | -121.6553 | -122.2916 | -0.11902 | -121.9299 | 0.054932 | 0.091553 | -121.7972 | -121.9574 | -0.032043 | 0.096131 | 0.009155 | 0.59967 | 0.14191 | 0.045776 | -0.15106 | -0.045776 | -0.20599 | -0.09613 | -0.54016 | -0.17853 | 0.027465 | -0.059509 | 121.9116 | 121.7514 | 117.5674 | -121.8063 | 121.8063 | 121.843 | 121.6324 | -122.1085
753.6719 | 121.962 | -121.7422 | 0.15106 | -0.013122 | 0.0164 | 0.067772 | 0.0034991 | 0.065943 | 0.0020849 | -0.0025122 | 0.0035858 | -0.0047681 | 0.061788 | 0.066031 | 0.0036189 | -0.0070516 | -0.018311 | -121.1334 | -4.1885 | -121.582 | 0.15106 | -121.8155 | -121.6644 | -122.2961 | -0.10071 | -121.9345 | 0.068665 | 0.10529 | -121.7972 | -121.9574 | -0.073242 | 0.07782 | 0 | 0.60883 | 0.16022 | 0.082398 | -0.16937 | -0.054931 | -0.21515 | -0.082397 | -0.55389 | -0.19226 | 0.022888 | -0.045776 | 121.8933 | 121.7239 | 117.5537 | -121.8155 | 121.8109 | 121.8475 | 121.6415 | -122.1085
755.4219 | 121.9162 | -121.7743 | 0.16937 | -0.028381 | 0.018322 | 0.069481 | 0.0058491 | 0.068293 | 0.0031531 | 0.00047844 | -0.011673 | -0.0054089 | 0.061361 | 0.064536 | 0.0068231 | -0.0070516 | -0.004578 | -121.106 | -4.1565 | -121.5958 | 0.13733 | -121.8018 | -121.6599 | -122.3145 | -0.09613 | -121.9574 | 0.050354 | 0.10071 | -121.7743 | -121.9528 | -0.027466 | 0.11444 | -0.032044 | 0.66833 | 0.17853 | 0.064087 | -0.17395 | 0 | -0.17853 | -0.11902 | -0.54016 | -0.1831 | -0.004577 | -0.068665 | 121.9116 | 121.7697 | 117.6178 | -121.8292 | 121.8246 | 121.875 | 121.6782 | -122.1222
757.1562 | 122.0398 | -121.7331 | 0.1236 | -0.0054933 | 0.017254 | 0.068413 | 0.0096943 | 0.067652 | -0.0015465 | -0.0031532 | -0.0040437 | -0.0083997 | 0.062856 | 0.064536 | -0.00086734 | -0.0083334 | 0.036621 | -121.0007 | -4.1016 | -121.5179 | 0.10529 | -121.7606 | -121.6553 | -122.2778 | -0.009155 | -121.8796 | 0.054932 | 0.10071 | -121.7834 | -121.962 | -0.027466 | 0.07782 | -0.01831 | 0.73242 | 0.21515 | 0.13733 | -0.086975 | -0.050354 | -0.22888 | -0.068664 | -0.54474 | -0.14648 | 0.082397 | -0.022888 | 121.8384 | 121.7697 | 117.6315 | -121.7789 | 121.788 | 121.8338 | 121.7239 | -122.0856
758.8906 | 122.0078 | -121.7194 | 0.15106 | -0.020752 | 0.018322 | 0.067345 | 0.0052081 | 0.064234 | 0.0012305 | -0.0031532 | 0.0035858 | -0.0047681 | 0.064352 | 0.068594 | 0.0063959 | -0.01047 | 0.064087 | -121.0144 | -4.0833 | -121.5363 | 0.15106 | -121.8063 | -121.6644 | -122.2458 | -0.013733 | -121.8796 | 0.045776 | 0.086975 | -121.7743 | -121.9391 | -0.086975 | 0.054931 | 0 | 0.70496 | 0.1831 | 0.12817 | -0.086975 | -0.054932 | -0.21973 | -0.10529 | -0.52643 | -0.16022 | 0.059509 | -0.064087 | 121.8704 | 121.7834 | 117.6361 | -121.8155 | 121.7651 | 121.8063 | 121.7056 | -122.0901
760.5625 | 121.9574 | -121.7606 | 0.14648 | -0.0054933 | 0.011487 | 0.069481 | 0.0037127 | 0.067011 | -0.0068871 | -0.0031532 | -0.0040437 | -0.0094677 | 0.060293 | 0.063681 | 0.00062806 | -0.0072652 | 0.018311 | -121.0419 | -4.1565 | -121.5363 | 0.1236 | -121.7743 | -121.6232 | -122.2824 | -0.018311 | -121.843 | 0.041199 | 0.091553 | -121.756 | -121.9345 | -0.013733 | 0.13733 | -0.022888 | 0.71869 | 0.2243 | 0.086975 | -0.12817 | 0.004578 | -0.17395 | -0.10529 | -0.52185 | -0.082398 | 0.091552 | -0.054931 | 121.8842 | 121.7789 | 117.6041 | -121.7697 | 121.8018 | 121.8521 | 121.7422 | -122.081
762.2969 | 122.0078 | -121.7148 | 0.14648 | -0.013122 | 0.015759 | 0.067772 | 0.0054217 | 0.069361 | 0.00058966 | -0.0025122 | -0.0040437 | -0.0043409 | 0.062002 | 0.064963 | 0.0023371 | -0.0083334 | 0 | -121.1014 | -4.1748 | -121.5866 | 0.16022 | -121.8292 | -121.6553 | -122.3099 | -0.068665 | -121.9162 | 0.082397 | 0.1236 | -121.7972 | -121.9437 | -0.11444 | 0.05951 | 0.013733 | 0.6134 | 0.12817 | 0.068664 | -0.14648 | -0.082397 | -0.22888 | -0.064087 | -0.59509 | -0.20142 | 0.027466 | -0.022888 | 121.875 | 121.7148 | 117.54 | -121.8018 | 121.7972 | 121.8384 | 121.6461 | -122.0901
763.9688 | 122.0718 | -121.7102 | 0.13733 | -0.013122 | 0.019604 | 0.067345 | 0.0073443 | 0.065516 | 0.00037606 | -0.00080316 | -0.011673 | -0.0039135 | 0.064779 | 0.065604 | 0.0057551 | -0.0094016 | 0.027466 | -121.0785 | -4.1382 | -121.5408 | 0.15106 | -121.788 | -121.6736 | -122.2504 | -0.022888 | -121.8887 | 0.082397 | 0.10986 | -121.7972 | -121.9345 | -0.07782 | 0.036621 | 0.013733 | 0.63171 | 0.16937 | 0.13275 | -0.10986 | -0.086975 | -0.2243 | -0.054932 | -0.54016 | -0.17853 | 0.045776 | -0.027466 | 121.8613 | 121.7377 | 117.572 | -121.8109 | 121.7926 | 121.8201 | 121.6873 | -122.0718
765.7188 | 121.9391 | -121.7606 | 0.16022 | -0.013122 | 0.017254 | 0.069054 | 0.0026447 | 0.066584 | 0.0027259 | -0.00058956 | -0.0040437 | -0.0030591 | 0.063925 | 0.068808 | 0.0046869 | -0.0059836 | -0.013733 | -121.1472 | -4.1885 | -121.5958 | 0.15564 | -121.788 | -121.6873 | -122.3145 | -0.11444 | -121.9482 | 0.073242 | 0.10529 | -121.8246 | -121.9482 | -0.027466 | 0.073242 | -0.004577 | 0.6134 | 0.16479 | 0.091553 | -0.17395 | -0.064087 | -0.18768 | -0.086975 | -0.55389 | -0.18768 | 0 | -0.054931 | 121.9162 | 121.7468 | 117.572 | -121.8475 | 121.8338 | 121.8658 | 121.6461 | -122.1085
767.4531 | 122.0215 | -121.7239 | 0.14191 | -0.013122 | 0.018536 | 0.067131 | 0.0088397 | 0.068934 | -0.0021875 | -0.0010168 | -0.011673 | -0.0056225 | 0.063711 | 0.064963 | 0.0036189 | -0.007479 | 0.004578 | -121.0602 | -4.1519 | -121.5775 | 0.15106 | -121.7834 | -121.669 | -122.3145 | -0.059509 | -121.9162 | 0.064087 | 0.10071 | -121.7972 | -121.9345 | -0.059509 | 0.054932 | 0.009155 | 0.66376 | 0.14648 | 0.091552 | -0.13733 | -0.073242 | -0.21057 | -0.07782 | -0.59051 | -0.19226 | 0.01831 | -0.041199 | 121.875 | 121.7285 | 117.572 | -121.8109 | 121.788 | 121.8246 | 121.6644 | -122.0764
769.1875 | 122.0398 | -121.7056 | 0.10529 | -0.0054933 | 0.0091366 | 0.067986 | 0.0041401 | 0.064234 | -0.0041101 | -0.00080316 | -0.011673 | -0.0079725 | 0.059652 | 0.066031 | -1.2744e-05 | -0.0066244 | 0.050354 | -121.0144 | -4.1428 | -121.5225 | 0.11902 | -121.7834 | -121.637 | -122.2366 | 0.036621 | -121.788 | 0.036621 | 0.073242 | -121.7468 | -121.9254 | -0.07782 | 0.068664 | 0.013733 | 0.69122 | 0.18311 | 0.11444 | -0.054932 | -0.041199 | -0.21973 | -0.068665 | -0.53101 | -0.082398 | 0.13733 | -0.032044 | 121.8246 | 121.756 | 117.5629 | -121.7422 | 121.7422 | 121.7789 | 121.7422 | -122.0306
770.9375 | 122.0352 | -121.701 | 0.12817 | -0.0054933 | 0.014691 | 0.06884 | 0.0041401 | 0.069361 | -0.0021875 | -0.0033668 | -0.0040437 | -0.0071179 | 0.061788 | 0.065604 | 0.0023371 | -0.0083334 | 0.11444 | -120.9366 | -4.0833 | -121.4767 | 0.10529 | -121.7789 | -121.6324 | -122.2046 | 0.064087 | -121.7834 | 0.022888 | 0.068665 | -121.7651 | -121.8979 | -0.07782 | 0.068665 | -0.022888 | 0.76447 | 0.2243 | 0.15564 | -0.013733 | -0.064087 | -0.19684 | -0.10529 | -0.50354 | -0.082397 | 0.11444 | -0.059509 | 121.8063 | 121.8155 | 117.6178 | -121.7606 | 121.7239 | 121.7697 | 121.7651 | -122.0261
772.6094 | 121.9254 | -121.7697 | 0.16937 | -0.013122 | 0.015759 | 0.067345 | 0.0045673 | 0.065943 | -0.0034691 | -0.0040076 | -0.011673 | -0.0077587 | 0.062216 | 0.064963 | 0.0038325 | -0.0087606 | 0.073242 | -121.0327 | -4.1473 | -121.55 | 0.10986 | -121.7468 | -121.6415 | -122.2412 | -0.041199 | -121.843 | 0.032043 | 0.068665 | -121.788 | -121.9254 | 0.022888 | 0.12817 | -0.05951 | 0.737 | 0.21973 | 0.091553 | -0.096131 | -0.018311 | -0.15564 | -0.13733 | -0.4715 | -0.073243 | 0.082397 | -0.10071 | 121.8796 | 121.843 | 117.6224 | -121.8109 | 121.8018 | 121.8384 | 121.7285 | -122.0947
774.3438 | 121.9757 | -121.7514 | 0.14648 | 0.0021362 | 0.015118 | 0.07119 | 0.0013629 | 0.064021 | 0.0016577 | -0.0025122 | -0.0040437 | -0.0039135 | 0.057089 | 0.063254 | 0.0083185 | -0.0091878 | 0.091553 | -121.0327 | -4.1473 | -121.5454 | 0.1236 | -121.7697 | -121.6644 | -122.1817 | -0.013733 | -121.8384 | 0.036621 | 0.068665 | -121.7743 | -121.9116 | -0.01831 | 0.086975 | -0.022888 | 0.71869 | 0.20599 | 0.11902 | -0.054931 | -0.022888 | -0.16022 | -0.10986 | -0.4303 | -0.086975 | 0.073242 | -0.077819 | 121.875 | 121.843 | 117.6041 | -121.8109 | 121.788 | 121.8201 | 121.7377 | -122.0581
776.0938 | 122.1085 | -121.7239 | 0.12817 | -0.013122 | 0.01875 | 0.067131 | 0.0064899 | 0.06872 | 0.0025123 | -0.002085 | -0.0040437 | -0.0054089 | 0.063711 | 0.066031 | 0.0040461 | -0.0094016 | 0.013733 | -121.1014 | -4.184 | -121.5591 | 0.15106 | -121.7972 | -121.6965 | -122.2549 | -0.041199 | -121.8933 | 0.054932 | 0.10071 | -121.8063 | -121.9803 | -0.073242 | 0.027466 | 0.022888 | 0.62256 | 0.16479 | 0.13733 | -0.11444 | -0.082397 | -0.25635 | -0.073242 | -0.53101 | -0.16937 | 0.086975 | -0.027466 | 121.875 | 121.7377 | 117.54 | -121.8246 | 121.7789 | 121.8246 | 121.6827 | -122.1085
777.8281 | 122.0169 | -121.7239 | 0.09613 | 0.0021362 | 0.013836 | 0.06884 | 0.0058491 | 0.06808 | -0.0034691 | -0.0014442 | -0.011673 | -0.0098951 | 0.062856 | 0.063895 | 0.0023371 | -0.0070516 | 0.10529 | -120.9503 | -4.0878 | -121.4951 | 0.10529 | -121.7651 | -121.6415 | -122.1817 | 0.059509 | -121.7972 | 0.022888 | 0.073242 | -121.7651 | -121.9254 | -0.041199 | 0.082397 | 0.009156 | 0.77362 | 0.22888 | 0.14648 | 0.009156 | -0.041199 | -0.20142 | -0.073242 | -0.45776 | -0.073242 | 0.12817 | -0.022888 | 121.8292 | 121.8292 | 117.6361 | -121.7377 | 121.7468 | 121.7972 | 121.7834 | -122.0215
779.5156 | 122.0398 | -121.7285 | 0.12817 | -0.013122 | 0.018322 | 0.06884 | 0.0049945 | 0.065302 | 0.00037606 | -0.0031532 | -0.019302 | -0.0041271 | 0.06307 | 0.066031 | 0.0036189 | -0.0089742 | 0.013733 | -121.0785 | -4.216 | -121.5866 | 0.16022 | -121.7972 | -121.7056 | -122.3145 | -0.07782 | -121.9299 | 0.059509 | 0.10071 | -121.8246 | -121.962 | -0.068664 | 0.022889 | 0.032043 | 0.65002 | 0.14191 | 0.11902 | -0.11444 | -0.09613 | -0.23346 | -0.068665 | -0.58594 | -0.20142 | 0.032043 | -0.027466 | 121.8887 | 121.7422 | 117.5125 | -121.8338 | 121.788 | 121.8292 | 121.6507 | -122.0901
781.2656 | 121.9299 | -121.7377 | 0.14648 | -0.013122 | 0.012768 | 0.069481 | 0.0017901 | 0.065943 | 0.0016577 | -0.00037596 | -0.0040437 | -0.0069043 | 0.061361 | 0.065817 | 0.0046869 | -0.008547 | 0.10986 | -120.9686 | -4.1107 | -121.4996 | 0.09613 | -121.7606 | -121.6278 | -122.1634 | 0.013733 | -121.788 | 0.022888 | 0.045776 | -121.7377 | -121.9482 | -0.022888 | 0.10986 | -0.050354 | 0.76904 | 0.23804 | 0.12817 | -0.036621 | 0 | -0.21057 | -0.1236 | -0.42572 | -0.050354 | 0.16022 | -0.10071 | 121.8338 | 121.8475 | 117.627 | -121.7743 | 121.7606 | 121.7834 | 121.7514 | -122.0947
783 | 121.9574 | -121.7514 | 0.16022 | -0.013122 | 0.014477 | 0.067345 | 0.0017901 | 0.067866 | 0.00080326 | -0.0010168 | -0.011673 | -0.0081861 | 0.06072 | 0.063254 | 0.0063959 | -0.007479 | 0.10986 | -120.9686 | -4.129 | -121.4996 | 0.11444 | -121.7789 | -121.6278 | -122.1817 | 0.004578 | -121.7834 | 0.018311 | 0.036621 | -121.756 | -121.9025 | -0.027466 | 0.1236 | -0.045776 | 0.78278 | 0.25177 | 0.12817 | -0.050354 | -0.004577 | -0.15106 | -0.14191 | -0.4303 | -0.032043 | 0.11902 | -0.1236 | 121.8658 | 121.8613 | 117.6224 | -121.788 | 121.7697 | 121.788 | 121.756 | -122.0627
784.6719 | 121.9528 | -121.756 | 0.16022 | -0.013122 | 0.019391 | 0.067345 | 0.0045673 | 0.064875 | 0.0048621 | 5.1244e-05 | 0.0035858 | -0.0013501 | 0.060934 | 0.064536 | 0.0072505 | -0.0098288 | 0.068665 | -121.0281 | -4.1611 | -121.5454 | 0.12817 | -121.8063 | -121.6599 | -122.2458 | -0.059509 | -121.9025 | 0.064087 | 0.086975 | -121.788 | -121.9528 | -0.050354 | 0.09613 | -0.032043 | 0.72784 | 0.21057 | 0.11444 | -0.091552 | -0.032044 | -0.19684 | -0.09613 | -0.48981 | -0.14648 | 0.050354 | -0.073242 | 121.8842 | 121.8246 | 117.5949 | -121.8201 | 121.8201 | 121.843 | 121.6965 | -122.113
786.4219 | 121.9757 | -121.7422 | 0.14648 | -0.0054933 | 0.019604 | 0.067131 | 0.0058491 | 0.066157 | 0.00080326 | -0.002085 | -0.011673 | -0.0049817 | 0.059652 | 0.06304 | 0.0061823 | -0.0066244 | 0.009155 | -121.1014 | -4.248 | -121.5866 | 0.14191 | -121.7697 | -121.669 | -122.2916 | -0.1236 | -121.9162 | 0.045776 | 0.086975 | -121.8109 | -121.9437 | -0.027465 | 0.073243 | -0.004577 | 0.64087 | 0.15564 | 0.082397 | -0.13733 | -0.068664 | -0.20142 | -0.10071 | -0.54932 | -0.17395 | 0.027466 | -0.059509 | 121.8842 | 121.7514 | 117.4942 | -121.8155 | 121.788 | 121.8292 | 121.6187 | -122.0901
788.1719 | 121.9391 | -121.6827 | 0.14191 | -0.0054933 | 0.017682 | 0.066704 | 0.0028583 | 0.067439 | 0.0014441 | 0.00026484 | -0.019302 | -0.0028455 | 0.062002 | 0.066245 | 0.0053279 | -0.0070516 | 0.041199 | -120.9961 | -4.1931 | -121.4951 | 0.11444 | -121.7056 | -121.5729 | -122.1634 | -0.036621 | -121.7743 | 0.022888 | 0.068665 | -121.7331 | -121.8658 | -0.022888 | 0.10986 | -0.027466 | 0.68664 | 0.18768 | 0.07782 | -0.10071 | -0.050354 | -0.18311 | -0.11902 | -0.48065 | -0.091553 | 0.091553 | -0.073242 | 121.7972 | 121.7239 | 117.4896 | -121.7148 | 121.7056 | 121.7514 | 121.6461 | -122.0078
789.9219 | 122.0215 | -121.6461 | 0.11444 | -0.020752 | 0.012555 | 0.069695 | 0.0060627 | 0.067225 | -0.0058191 | -0.00080316 | 0.0035858 | -0.0060497 | 0.059652 | 0.063254 | -0.00065374 | -0.0042746 | 0.073242 | -120.9274 | -4.1473 | -121.4676 | 0.09613 | -121.7331 | -121.6232 | -122.1588 | 0.022888 | -121.7331 | 0.004578 | 0.045776 | -121.7377 | -121.8933 | -0.086975 | 0.022888 | -0.018311 | 0.71869 | 0.17853 | 0.15564 | -0.041199 | -0.091553 | -0.24719 | -0.10986 | -0.51269 | -0.086975 | 0.16022 | -0.068665 | 121.7422 | 121.7194 | 117.4988 | -121.7377 | 121.6507 | 121.6919 | 121.669 | -122.0078
791.5938 | 121.9162 | -121.7194 | 0.16022 | -0.0054933 | 0.017895 | 0.068413 | 0.0034991 | 0.066157 | 0.0031531 | -0.0018714 | -0.019302 | -0.0043409 | 0.06307 | 0.066245 | 0.0061823 | -0.0064108 | -0.004578 | -121.1151 | -4.2618 | -121.5591 | 0.12817 | -121.7468 | -121.6324 | -122.2687 | -0.15564 | -121.9208 | 0.045776 | 0.091553 | -121.7697 | -121.9437 | -0.027466 | 0.086975 | -0.032043 | 0.60425 | 0.16022 | 0.073242 | -0.16479 | -0.050354 | -0.22431 | -0.11444 | -0.54932 | -0.20142 | 0.022889 | -0.068664 | 121.8475 | 121.7148 | 117.4576 | -121.7926 | 121.7651 | 121.8109 | 121.5637 | -122.1039
793.3281 | 121.9025 | -121.7285 | 0.13733 | 0.0021362 | 0.010418 | 0.069481 | 0.0052081 | 0.063807 | -0.0045373 | -0.002085 | 0.0035858 | -0.0077587 | 0.060934 | 0.064322 | 0.0023371 | -0.0055564 | 0.027466 | -121.0007 | -4.2114 | -121.5134 | 0.10529 | -121.7514 | -121.5866 | -122.2366 | -0.14648 | -121.8292 | 0.009155 | 0.054932 | -121.756 | -121.9254 | -0.022888 | 0.14191 | -0.032043 | 0.72785 | 0.21515 | 0.073242 | -0.10986 | -0.027465 | -0.19684 | -0.12817 | -0.50812 | -0.10071 | 0.09613 | -0.082397 | 121.8338 | 121.756 | 117.5171 | -121.7239 | 121.7377 | 121.7834 | 121.582 | -122.0627
795 | 121.907 | -121.7514 | 0.13733 | -0.013122 | 0.015973 | 0.067558 | 0.0039265 | 0.065089 | -0.0011193 | -0.0014442 | -0.026932 | -0.0045545 | 0.059439 | 0.06304 | 0.0031915 | -0.0066244 | 0.10529 | -120.9549 | -4.1473 | -121.4996 | 0.091553 | -121.7514 | -121.6003 | -122.1725 | -0.15564 | -121.7789 | 0.009155 | 0.036621 | -121.7194 | -121.907 | 0 | 0.15106 | -0.045776 | 0.79651 | 0.25177 | 0.10071 | -0.032043 | 0.032044 | -0.15564 | -0.12817 | -0.42114 | -0.027466 | 0.12817 | -0.10071 | 121.843 | 121.8567 | 117.6041 | -121.7377 | 121.7606 | 121.788 | 121.5958 | -122.0444
796.7344 | 122.0261 | -121.7148 | 0.11444 | -0.0054933 | 0.013623 | 0.067558 | 0.0077717 | 0.065516 | -0.0045373 | -0.0025122 | -0.011673 | -0.0071179 | 0.062216 | 0.06304 | 0.0019099 | -0.0083334 | 0.10529 | -120.9274 | -4.129 | -121.4767 | 0.07782 | -121.756 | -121.6003 | -122.1588 | -0.19684 | -121.7468 | 0.018311 | 0.041199 | -121.7285 | -121.8842 | -0.041198 | 0.11444 | -0.036621 | 0.78735 | 0.23804 | 0.1236 | -0.009155 | -0.013733 | -0.16937 | -0.09613 | -0.44403 | -0.032043 | 0.13733 | -0.073242 | 121.7926 | 121.8201 | 117.5858 | -121.7148 | 121.7331 | 121.756 | 121.5179 | -121.9986
798.4688 | 121.994 | -121.7239 | 0.11444 | -0.013122 | 0.013836 | 0.069481 | 0.0062763 | 0.066798 | -0.0021875 | -0.0022986 | 0.0035858 | -0.0098951 | 0.061361 | 0.064108 | 0.0025507 | -0.0083334 | 0.036621 | -121.0236 | -4.2252 | -121.5225 | 0.10071 | -121.7422 | -121.5958 | -122.2275 | -0.43945 | -121.8201 | 0.032043 | 0.064087 | -121.7606 | -121.9208 | -0.018311 | 0.12817 | -0.013733 | 0.70038 | 0.20142 | 0.073242 | -0.07782 | -0.036621 | -0.19684 | -0.082398 | -0.50354 | -0.09613 | 0.10071 | -0.050354 | 121.8246 | 121.7606 | 117.4988 | -121.7102 | 121.756 | 121.788 | 121.2845 | -122.0352
800.2031 | 122.0352 | -121.6873 | 0.10529 | -0.013122 | 0.0093504 | 0.070549 | 0.0039265 | 0.064662 | -0.0019739 | -0.0029394 | -0.0040437 | -0.0062635 | 0.060293 | 0.061545 | 0.0049005 | -0.0083334 | 0.1236 | -120.9274 | -4.1611 | -121.5088 | 0.10071 | -121.7606 | -121.6095 | -122.1497 | -0.37079 | -121.7743 | -0.004578 | 0.050354 | -121.7377 | -121.9208 | -0.073242 | 0.07782 | -0.004578 | 0.75989 | 0.17853 | 0.10071 | 0.01831 | -0.050354 | -0.23346 | -0.10986 | -0.46234 | -0.086975 | 0.14648 | -0.054932 | 121.788 | 121.8109 | 117.5262 | -121.7148 | 121.6827 | 121.7377 | 121.3165 | -122.0261
801.9375 | 121.9482 | -121.7606 | 0.13275 | -0.013122 | 0.016827 | 0.066917 | 0.0026447 | 0.064234 | 0.0063575 | -0.002085 | -0.0040437 | -0.0045545 | 0.062002 | 0.066031 | 0.0091731 | -0.0096152 | 0.022888 | -121.1288 | -4.2801 | -121.582 | 0.13733 | -121.7972 | -121.6553 | -122.2733 | -0.6134 | -121.9345 | 0.059509 | 0.086975 | -121.8155 | -121.9391 | -0.036621 | 0.10529 | 0.004578 | 0.63171 | 0.17853 | 0.073242 | -0.10986 | -0.054932 | -0.17853 | -0.073242 | -0.51269 | -0.17395 | 0.004578 | -0.045776 | 121.8979 | 121.7834 | 117.4805 | -121.788 | 121.8201 | 121.8475 | 121.1472 | -122.0718
803.625 | 121.9528 | -121.7422 | 0.12817 | -0.013122 | 0.01875 | 0.06649 | 0.0043537 | 0.066584 | 0.0018713 | 5.1244e-05 | -0.011673 | -0.0043409 | 0.061361 | 0.065176 | 0.0063959 | -0.0076926 | 0.032043 | -121.0968 | -4.2572 | -121.5546 | 0.13275 | -121.7789 | -121.6553 | -122.2046 | -0.58136 | -121.8613 | 0.041199 | 0.059509 | -121.756 | -121.9116 | -0.036621 | 0.086976 | 0.004577 | 0.64545 | 0.18768 | 0.10071 | -0.096131 | -0.013732 | -0.16937 | -0.086975 | -0.46234 | -0.11902 | 0.050354 | -0.068665 | 121.875 | 121.7743 | 117.485 | -121.7834 | 121.7834 | 121.8018 | 121.1609 | -122.0398
805.375 | 121.9711 | -121.7422 | 0.13733 | -0.013122 | 0.016613 | 0.067131 | 0.0058491 | 0.063807 | 0.0010169 | 0.00026484 | -0.011673 | -0.0060497 | 0.062216 | 0.064963 | 0.0055415 | -0.008547 | 0.068665 | -121.0098 | -4.216 | -121.5088 | 0.12817 | -121.7651 | -121.6095 | -122.1634 | -0.62256 | -121.8155 | 0.009155 | 0.036621 | -121.7651 | -121.8887 | -0.022888 | 0.13275 | -0.009155 | 0.73242 | 0.23346 | 0.10071 | -0.068664 | -0.022888 | -0.14648 | -0.12817 | -0.42114 | -0.073242 | 0.073242 | -0.10071 | 121.8704 | 121.8109 | 117.5262 | -121.7468 | 121.7514 | 121.7789 | 121.1197 | -122.0261
807.1094 | 121.9208 | -121.756 | 0.14191 | -0.013122 | 0.017895 | 0.069054 | 0.0056355 | 0.063166 | 0.0035803 | 0.00090584 | -0.019302 | -0.0036999 | 0.061575 | 0.063467 | 0.0063959 | -0.0083334 | 0.054932 | -121.0373 | -4.216 | -121.55 | 0.12817 | -121.7834 | -121.6599 | -122.2183 | -0.73242 | -121.9025 | 0.022888 | 0.091553 | -121.8063 | -121.9711 | -0.027466 | 0.09613 | -0.013733 | 0.71869 | 0.20599 | 0.10986 | -0.086975 | -0.050354 | -0.21515 | -0.11902 | -0.46234 | -0.14648 | 0.068664 | -0.050354 | 121.8842 | 121.8109 | 117.54 | -121.8018 | 121.7789 | 121.8475 | 121.0236 | -122.113
808.8438 | 121.9162 | -121.7834 | 0.13733 | -0.0054933 | 0.016613 | 0.067131 | 0.0052081 | 0.066584 | 0.0012305 | 0.00090584 | -0.019302 | -0.0045545 | 0.063284 | 0.067099 | 0.0044733 | -0.0089742 | 0.036621 | -121.0373 | -4.2526 | -121.5637 | 0.11902 | -121.7743 | -121.6415 | -122.2687 | -0.72784 | -121.9208 | 0.032043 | 0.07782 | -121.7972 | -121.9666 | 0.009155 | 0.14191 | -0.01831 | 0.74616 | 0.21973 | 0.07782 | -0.10071 | -0.013733 | -0.18311 | -0.10529 | -0.48523 | -0.13733 | 0.045777 | -0.059509 | 121.9025 | 121.8201 | 117.5308 | -121.7789 | 121.8155 | 121.8613 | 121.0556 | -122.1039
810.5312 | 122.0398 | -121.7239 | 0.1236 | -0.020752 | 0.016613 | 0.068413 | 0.0062763 | 0.066798 | -0.00047854 | -0.0029394 | -0.011673 | -0.0066907 | 0.063925 | 0.064108 | 0.0019099 | -0.0079062 | -0.041199 | -121.0831 | -4.2984 | -121.5775 | 0.14648 | -121.8063 | -121.6782 | -122.287 | -0.75073 | -121.9162 | 0.064087 | 0.10986 | -121.8109 | -121.9391 | -0.082397 | 0.045776 | 0.022888 | 0.64087 | 0.14648 | 0.10071 | -0.16479 | -0.086975 | -0.21515 | -0.059509 | -0.56305 | -0.19226 | 0.022888 | -0.013733 | 121.8704 | 121.6827 | 117.4255 | -121.8018 | 121.788 | 121.8338 | 120.9732 | -122.0627
812.2656 | 121.9025 | -121.756 | 0.15564 | -0.020752 | 0.014477 | 0.067986 | 0.0045673 | 0.069148 | -0.0028283 | -0.0018714 | -0.0040437 | -0.0096813 | 0.06307 | 0.065817 | 0.0044733 | -0.0061972 | 0.082397 | -120.9686 | -4.216 | -121.5271 | 0.086975 | -121.7697 | -121.6461 | -122.1817 | -0.65002 | -121.8109 | 0.013733 | 0.041199 | -121.7697 | -121.9025 | -0.013733 | 0.10986 | -0.068665 | 0.78735 | 0.22888 | 0.11902 | -0.073243 | -0.013733 | -0.14648 | -0.14191 | -0.42572 | -0.054932 | 0.091553 | -0.11444 | 121.843 | 121.8384 | 117.54 | -121.8018 | 121.7697 | 121.7972 | 121.106 | -122.0581
813.9375 | 122.0398 | -121.7056 | 0.11444 | -0.013122 | 0.013836 | 0.070335 | 0.0041401 | 0.066584 | -0.0047509 | -0.0029394 | -0.0040437 | -0.0071179 | 0.060293 | 0.062613 | 0.0019099 | -0.0072652 | 0.086975 | -120.9549 | -4.216 | -121.5134 | 0.09613 | -121.7606 | -121.6415 | -122.1817 | -0.66834 | -121.7606 | 0 | 0.045776 | -121.756 | -121.9162 | -0.054932 | 0.064086 | -0.018311 | 0.75073 | 0.19226 | 0.12817 | -0.027466 | -0.050354 | -0.21057 | -0.11444 | -0.47607 | -0.054932 | 0.15564 | -0.068665 | 121.8018 | 121.7926 | 117.4896 | -121.756 | 121.7056 | 121.7514 | 121.0373 | -122.0306
815.6719 | 122.0123 | -121.7285 | 0.13275 | -0.020752 | 0.016186 | 0.070763 | 0.0056355 | 0.067011 | 0.00037606 | -0.0048622 | 0.0035858 | -0.0047681 | 0.062856 | 0.064322 | 0.0038325 | -0.008547 | 0.013733 | -121.0648 | -4.2847 | -121.5729 | 0.13733 | -121.8063 | -121.6736 | -122.2961 | -0.84228 | -121.9025 | 0.068665 | 0.10529 | -121.8292 | -121.9803 | -0.077819 | 0.054932 | 0.004578 | 0.66376 | 0.15564 | 0.10071 | -0.11902 | -0.10071 | -0.25177 | -0.064086 | -0.56763 | -0.17395 | 0.07782 | -0.027465 | 121.8658 | 121.7422 | 117.4438 | -121.8063 | 121.7972 | 121.8338 | 120.8862 | -122.113
817.4062 | 121.9757 | -121.756 | 0.13733 | -0.0054933 | 0.014264 | 0.067772 | 0.0030719 | 0.066584 | 0.00080326 | -0.002085 | -0.0040437 | -0.0043409 | 0.060293 | 0.066245 | 0.0044733 | -0.010042 | 0.073242 | -121.0327 | -4.2343 | -121.5408 | 0.10986 | -121.7606 | -121.6461 | -122.1771 | -0.86517 | -121.8155 | 0.009155 | 0.054932 | -121.788 | -121.9025 | -0.004578 | 0.10986 | -0.027466 | 0.72327 | 0.21515 | 0.10528 | -0.064087 | -0.032044 | -0.14648 | -0.12817 | -0.42114 | -0.05951 | 0.086975 | -0.082397 | 121.8658 | 121.8292 | 117.5217 | -121.7834 | 121.7651 | 121.8109 | 120.8908 | -122.0398
819.0938 | 121.9574 | -121.7606 | 0.11902 | -0.020752 | 0.015759 | 0.069481 | 0.0028583 | 0.066157 | 0.0014441 | -0.002085 | 0.0035858 | -0.0043409 | 0.061148 | 0.065176 | 0.0049005 | -0.0053426 | 0.009155 | -121.1105 | -4.3259 | -121.5912 | 0.14648 | -121.7972 | -121.6827 | -122.2504 | -1.0254 | -121.8979 | 0.036621 | 0.07782 | -121.7972 | -121.9574 | -0.036621 | 0.07782 | 0.027465 | 0.65002 | 0.16937 | 0.091552 | -0.10986 | -0.036621 | -0.19684 | -0.082398 | -0.48981 | -0.13733 | 0.059509 | -0.041199 | 121.907 | 121.7697 | 117.4347 | -121.8018 | 121.7972 | 121.8384 | 120.7352 | -122.0764
820.8438 | 121.9116 | -121.8063 | 0.14648 | -0.020752 | 0.017254 | 0.066063 | 0.0073443 | 0.066798 | 0.0025123 | 0.00026484 | -0.0040437 | -0.0015637 | 0.061148 | 0.066245 | 0.0057551 | -0.0083334 | 0 | -121.1288 | -4.3213 | -121.5866 | 0.1236 | -121.8201 | -121.669 | -122.2824 | -1.1124 | -121.9711 | 0.068665 | 0.09613 | -121.8155 | -121.9803 | -0.013733 | 0.13733 | -0.022888 | 0.67749 | 0.21973 | 0.082397 | -0.14648 | -0.009156 | -0.17395 | -0.077819 | -0.47607 | -0.16479 | 0.009156 | -0.050354 | 121.9299 | 121.8063 | 117.485 | -121.8155 | 121.875 | 121.9025 | 120.694 | -122.1268
822.5781 | 122.0032 | -121.7102 | 0.14648 | 0.0021362 | 0.016613 | 0.06884 | 0.0088397 | 0.067225 | -0.0024011 | -0.0016578 | 0.0035858 | -0.0056225 | 0.06307 | 0.067526 | 0.00084166 | -0.0076926 | 0.041199 | -121.0144 | -4.2435 | -121.5363 | 0.10986 | -121.8292 | -121.6873 | -122.287 | -1.0941 | -121.8842 | 0.054932 | 0.091553 | -121.8246 | -121.962 | -0.11902 | 0.022888 | -0.036621 | 0.6958 | 0.17395 | 0.15106 | -0.10529 | -0.11444 | -0.25177 | -0.091552 | -0.57678 | -0.17395 | 0.07782 | -0.054931 | 121.8201 | 121.7514 | 117.4667 | -121.8338 | 121.7651 | 121.8018 | 120.6162 | -122.1085
824.25 | 122.0398 | -121.7331 | 0.12817 | -0.0054933 | 0.015332 | 0.067772 | 0.0069171 | 0.065516 | -0.0017603 | -0.0025122 | -0.0040437 | -0.0043409 | 0.060934 | 0.066245 | 0.0034051 | -0.0070516 | -0.022888 | -121.1014 | -4.3259 | -121.5912 | 0.15564 | -121.8384 | -121.6507 | -122.3007 | -1.2451 | -121.9208 | 0.059509 | 0.10529 | -121.8384 | -121.994 | -0.10529 | 0.082397 | 0.027466 | 0.63171 | 0.14191 | 0.059509 | -0.15106 | -0.10529 | -0.26093 | -0.068665 | -0.56763 | -0.18768 | 0.073243 | -0.022888 | 121.8887 | 121.7102 | 117.4072 | -121.7789 | 121.7926 | 121.8384 | 120.488 | -122.1222
826 | 122.049 | -121.7194 | 0.10071 | -0.0054933 | 0.013409 | 0.069267 | 0.0041401 | 0.066371 | -0.0049645 | -0.0046484 | 0.0035858 | -0.0088269 | 0.060507 | 0.064322 | 0.00084166 | -0.0049154 | 0.032043 | -121.0007 | -4.2801 | -121.5454 | 0.11444 | -121.7789 | -121.6461 | -122.2275 | -1.181 | -121.8063 | 0.027466 | 0.059509 | -121.7743 | -121.9437 | -0.05951 | 0.073242 | 0.013733 | 0.71869 | 0.17395 | 0.10071 | -0.068665 | -0.054932 | -0.22431 | -0.073242 | -0.50812 | -0.086975 | 0.13733 | -0.041199 | 121.8338 | 121.7514 | 117.4393 | -121.7468 | 121.7468 | 121.7789 | 120.5383 | -122.0444
827.6719 | 122.0123 | -121.7331 | 0.13733 | -0.020752 | 0.012768 | 0.06884 | 0.0049945 | 0.064875 | -0.0045373 | -0.0033668 | -0.011673 | -0.0081861 | 0.060507 | 0.066031 | 0.0012689 | -0.0066244 | 0.027466 | -121.0327 | -4.2847 | -121.5454 | 0.11444 | -121.7834 | -121.6049 | -122.2275 | -1.1902 | -121.8155 | 0.013733 | 0.064087 | -121.7514 | -121.9208 | -0.050354 | 0.12817 | -0.022888 | 0.70038 | 0.18768 | 0.059509 | -0.10986 | -0.018311 | -0.18768 | -0.1236 | -0.49439 | -0.082398 | 0.10529 | -0.073242 | 121.8475 | 121.7606 | 117.4484 | -121.7422 | 121.7468 | 121.7972 | 120.5429 | -122.0581
829.4062 | 121.9711 | -121.7834 | 0.14648 | -0.013122 | 0.017682 | 0.067772 | 0.0024311 | 0.068934 | 0.0035803 | -0.00080316 | 0.011215 | -0.0022045 | 0.061575 | 0.066672 | 0.0068231 | -0.007479 | 0.018311 | -121.1288 | -4.3533 | -121.6003 | 0.15106 | -121.7972 | -121.669 | -122.2641 | -1.3641 | -121.9345 | 0.050354 | 0.082397 | -121.8201 | -121.9666 | -0.013733 | 0.11444 | 0.004578 | 0.6546 | 0.1831 | 0.068664 | -0.12817 | -0.036621 | -0.18311 | -0.09613 | -0.48065 | -0.15106 | 0.032044 | -0.064087 | 121.9345 | 121.8018 | 117.4301 | -121.8155 | 121.8338 | 121.8658 | 120.4193 | -122.113
831.0938 | 122.0261 | -121.7102 | 0.10986 | -0.0054933 | 0.016186 | 0.07119 | 0.0052081 | 0.062525 | -0.0045373 | -0.0010168 | -0.011673 | -0.0071179 | 0.061788 | 0.064108 | 0.0040461 | -0.007479 | 0.10071 | -120.9 | -4.2252 | -121.5088 | 0.09613 | -121.788 | -121.6278 | -122.168 | -1.0757 | -121.7834 | 0.013733 | 0.050354 | -121.788 | -121.9299 | -0.07782 | 0.082397 | -0.013733 | 0.81024 | 0.20142 | 0.11902 | -0.009155 | -0.07782 | -0.21973 | -0.09613 | -0.45776 | -0.073242 | 0.14648 | -0.059509 | 121.8063 | 121.8109 | 117.485 | -121.7377 | 121.7239 | 121.7606 | 120.6345 | -122.0398
832.8281 | 121.9986 | -121.756 | 0.13733 | 0.0021362 | 0.014264 | 0.069054 | 0.0020039 | 0.06573 | 0.0018713 | -0.002085 | -0.011673 | -0.0062635 | 0.060507 | 0.066031 | 0.0072505 | -0.0091878 | 0.054932 | -121.051 | -4.4128 | -121.5546 | 0.1236 | -121.7651 | -121.637 | -122.1771 | -1.181 | -121.8475 | 0.013733 | 0.059509 | -121.788 | -121.9345 | -0.009156 | 0.11902 | -0.013733 | 0.70496 | 0.20142 | 0.082398 | -0.082397 | -0.032044 | -0.17853 | -0.1236 | -0.42114 | -0.091553 | 0.086975 | -0.07782 | 121.8796 | 121.8109 | 117.3431 | -121.7743 | 121.7697 | 121.8155 | 120.575 | -122.0718
834.5156 | 121.9437 | -121.7697 | 0.14648 | -0.0054933 | 0.012768 | 0.067131 | 0.0039265 | 0.06573 | -0.0032555 | -0.0010168 | 0.011215 | -0.0073315 | 0.059225 | 0.06539 | 0.0025507 | -0.0089742 | 0.064087 | -121.0236 | -4.6326 | -121.5454 | 0.10071 | -121.7789 | -121.6324 | -122.2137 | -1.2817 | -121.8384 | 0.027466 | 0.045776 | -121.7743 | -121.9299 | -0.009156 | 0.13733 | -0.045776 | 0.74615 | 0.2243 | 0.086975 | -0.082397 | -0.004578 | -0.16022 | -0.11902 | -0.44403 | -0.068665 | 0.091553 | -0.10071 | 121.8704 | 121.8338 | 117.1371 | -121.7789 | 121.7972 | 121.8155 | 120.488 | -122.0764
836.2656 | 122.0398 | -121.7056 | 0.10529 | -0.013122 | 0.013623 | 0.068413 | 0.0075581 | 0.067225 | -0.0026147 | -0.0022986 | 0.0035858 | -0.0069043 | 0.063497 | 0.064749 | 0.00020086 | -0.0098288 | 0.073242 | -120.9595 | -4.6555 | -121.5134 | 0.091553 | -121.7514 | -121.6644 | -122.1909 | -1.2543 | -121.7972 | 0.009155 | 0.041199 | -121.7743 | -121.9711 | -0.045777 | 0.041198 | -0.013733 | 0.74615 | 0.19226 | 0.15106 | -0.032044 | -0.068665 | -0.2655 | -0.096131 | -0.48523 | -0.091553 | 0.17395 | -0.064087 | 121.7972 | 121.7789 | 117.0502 | -121.7697 | 121.7148 | 121.7468 | 120.4514 | -122.0764
838 | 121.9254 | -121.7606 | 0.13733 | -0.013122 | 0.01405 | 0.068413 | 0.00029487 | 0.069148 | 0.0016577 | -0.00080316 | 0.0035858 | -0.0079725 | 0.06072 | 0.063467 | 0.0036189 | -0.0072652 | 0.11444 | -120.9412 | -4.6921 | -121.5134 | 0.07782 | -121.7972 | -121.6141 | -122.1634 | -1.4099 | -121.8109 | 0.004578 | 0.041199 | -121.7834 | -121.9482 | -0.036621 | 0.14648 | -0.059509 | 0.8194 | 0.24719 | 0.10071 | -0.022888 | -0.022888 | -0.18768 | -0.13275 | -0.40283 | -0.050354 | 0.13733 | -0.09613 | 121.8384 | 121.875 | 117.0685 | -121.7514 | 121.7651 | 121.8018 | 120.3506 | -122.0856
839.6719 | 122.0261 | -121.7377 | 0.13275 | -0.013122 | 0.020031 | 0.067558 | 0.0020039 | 0.06808 | 0.0014441 | -0.00080316 | -0.0040437 | -0.0019909 | 0.06072 | 0.065604 | 0.0087457 | -0.010683 | 0.073242 | -121.0052 | -4.6143 | -121.55 | 0.12817 | -121.8018 | -121.669 | -122.2137 | -1.3321 | -121.875 | 0.050354 | 0.086975 | -121.8109 | -121.994 | -0.064087 | 0.068665 | -0.004577 | 0.73242 | 0.18768 | 0.11902 | -0.059509 | -0.073242 | -0.25635 | -0.082397 | -0.47607 | -0.13733 | 0.11902 | -0.045776 | 121.8658 | 121.8109 | 117.1234 | -121.8018 | 121.788 | 121.8246 | 120.4056 | -122.1268
841.4219 | 121.9345 | -121.7972 | 0.15106 | -0.013122 | 0.010418 | 0.069695 | 0.0056355 | 0.065516 | -0.0038965 | -0.0012306 | -0.011673 | -0.0081861 | 0.059011 | 0.064749 | 0.0031915 | -0.0079062 | 0.064087 | -120.9915 | -4.3671 | -121.5591 | 0.07782 | -121.7697 | -121.6461 | -122.2412 | -1.268 | -121.8521 | 0.009155 | 0.041199 | -121.7743 | -121.962 | 0.027466 | 0.15106 | -0.073242 | 0.80566 | 0.23804 | 0.086975 | -0.086975 | 0.022888 | -0.16479 | -0.14191 | -0.44403 | -0.054932 | 0.10986 | -0.10986 | 121.875 | 121.8613 | 117.4301 | -121.7972 | 121.8063 | 121.8384 | 120.5292 | -122.113
843.1094 | 122.0078 | -121.7102 | 0.1236 | -0.013122 | 0.014691 | 0.069481 | 0.0077717 | 0.063807 | -0.0026147 | -0.0029394 | -0.0040437 | -0.0075451 | 0.060934 | 0.065176 | 0.0016963 | -0.0070516 | 0.10071 | -120.9366 | -4.3442 | -121.5317 | 0.10529 | -121.7606 | -121.637 | -122.1863 | -1.0162 | -121.8155 | 0 | 0.054932 | -121.7697 | -121.9254 | -0.050354 | 0.073242 | -0.01831 | 0.77362 | 0.17853 | 0.10529 | -0.022888 | -0.059509 | -0.21515 | -0.1236 | -0.47607 | -0.10529 | 0.10986 | -0.068664 | 121.8155 | 121.8109 | 117.366 | -121.7606 | 121.7102 | 121.7651 | 120.694 | -122.049
844.8438 | 122.0123 | -121.7514 | 0.11902 | -0.013122 | 0.018322 | 0.066704 | 0.0026447 | 0.065516 | 0.0042213 | -0.0029394 | -0.0040437 | -0.0051953 | 0.061788 | 0.063895 | 0.0074641 | -0.0079062 | 0.086975 | -121.0144 | -4.6692 | -121.5591 | 0.1236 | -121.7972 | -121.6827 | -122.2 | -1.0071 | -121.8933 | 0.054932 | 0.07782 | -121.7926 | -121.9711 | -0.045776 | 0.068665 | 0.004577 | 0.737 | 0.19226 | 0.1236 | -0.032044 | -0.041199 | -0.21973 | -0.064087 | -0.44861 | -0.14191 | 0.077819 | -0.041199 | 121.875 | 121.8384 | 117.0822 | -121.8018 | 121.8063 | 121.8292 | 120.7443 | -122.0901
846.5312 | 121.994 | -121.7651 | 0.13275 | -0.013122 | 0.015545 | 0.069695 | 0.0039265 | 0.063166 | 0.00058966 | 0.0017602 | -0.0040437 | -0.0058361 | 0.060293 | 0.063254 | 0.0042597 | -0.0070516 | 0.027466 | -121.0327 | -5.0446 | -121.5729 | 0.1236 | -121.788 | -121.6553 | -122.2 | -1.0986 | -121.8704 | 0.022888 | 0.07782 | -121.8155 | -121.9254 | -0.022888 | 0.10986 | -0.009155 | 0.73242 | 0.19226 | 0.082397 | -0.10529 | -0.050354 | -0.16022 | -0.10986 | -0.43488 | -0.10529 | 0.054932 | -0.054931 | 121.8887 | 121.7926 | 116.7206 | -121.788 | 121.788 | 121.843 | 120.6665 | -122.0581
848.2812 | 121.9894 | -121.7743 | 0.14191 | -0.0054933 | 0.015332 | 0.068413 | 0.0037127 | 0.066798 | 0.0014441 | 0.00069204 | -0.0040437 | -0.0036999 | 0.062643 | 0.064749 | 0.0040461 | -0.0083334 | 0.018311 | -121.0693 | -5.1498 | -121.6049 | 0.14648 | -121.7972 | -121.6644 | -122.2412 | -1.1856 | -121.8933 | 0.032043 | 0.068665 | -121.8292 | -121.962 | -0.022888 | 0.10986 | 0.004577 | 0.70496 | 0.16937 | 0.05951 | -0.1236 | -0.054932 | -0.18768 | -0.10986 | -0.46692 | -0.11902 | 0.068664 | -0.073242 | 121.9208 | 121.7926 | 116.6245 | -121.8063 | 121.8063 | 121.843 | 120.5887 | -122.1039
850.0156 | 122.0123 | -121.7422 | 0.12817 | -0.013122 | 0.020245 | 0.067345 | 0.0064899 | 0.064448 | 0.0025123 | -0.00058956 | -0.011673 | -0.0036999 | 0.063284 | 0.067313 | 0.0059687 | -0.008547 | 0.073242 | -120.9915 | -5.191 | -121.5591 | 0.14191 | -121.8018 | -121.6553 | -122.2275 | -1.1353 | -121.8933 | 0.032043 | 0.07782 | -121.8475 | -121.9894 | -0.059509 | 0.086976 | 0.013733 | 0.75073 | 0.18311 | 0.09613 | -0.054932 | -0.10528 | -0.24719 | -0.096131 | -0.48523 | -0.15106 | 0.09613 | -0.050354 | 121.8842 | 121.8155 | 116.5512 | -121.7834 | 121.7743 | 121.8201 | 120.607 | -122.1176
851.7031 | 122.0673 | -121.7239 | 0.10071 | -0.0054933 | 0.016186 | 0.07119 | 0.0084125 | 0.066584 | -0.0071007 | -0.0031532 | -0.011673 | -0.0079725 | 0.062002 | 0.065176 | -0.00065374 | -0.0087606 | 0.091553 | -120.9045 | -5.397 | -121.5134 | 0.11444 | -121.7514 | -121.6461 | -122.1817 | -1.1627 | -121.7789 | 0.013733 | 0.059509 | -121.7834 | -121.9345 | -0.027466 | 0.07782 | 0.013733 | 0.8194 | 0.21057 | 0.13275 | -0.009155 | -0.059509 | -0.21057 | -0.086975 | -0.45776 | -0.054932 | 0.15564 | -0.041199 | 121.8384 | 121.8155 | 116.3269 | -121.7468 | 121.7377 | 121.7834 | 120.5612 | -122.0352
853.4375 | 122.0215 | -121.7422 | 0.12817 | -0.0054933 | 0.012127 | 0.070549 | 0.0043537 | 0.065516 | -0.0041101 | -0.0035804 | -0.011673 | -0.0071179 | 0.058798 | 0.063467 | 0.0021235 | -0.0076926 | 0.013733 | -121.0007 | -5.5847 | -121.5683 | 0.10529 | -121.7926 | -121.6644 | -122.2412 | -1.2497 | -121.8475 | 0.022888 | 0.059509 | -121.8109 | -121.9437 | -0.050354 | 0.07782 | -0.022888 | 0.74158 | 0.17395 | 0.096131 | -0.11444 | -0.068664 | -0.20142 | -0.10529 | -0.49896 | -0.10528 | 0.096131 | -0.068665 | 121.8475 | 121.756 | 116.1575 | -121.7926 | 121.7651 | 121.8018 | 120.4926 | -122.0718
855.1094 | 122.0718 | -121.7148 | 0.1236 | -0.0054933 | 0.013836 | 0.068199 | 0.0052081 | 0.063807 | -0.0036829 | -0.0029394 | -0.011673 | -0.0083997 | 0.06072 | 0.065604 | 0.0021235 | -0.0072652 | 0.07782 | -120.9869 | -5.6808 | -121.5179 | 0.10986 | -121.8018 | -121.6553 | -122.1909 | -1.1948 | -121.7789 | 0.032043 | 0.064087 | -121.7926 | -121.9254 | -0.086975 | 0.05951 | -0.013733 | 0.72785 | 0.19684 | 0.13733 | -0.045776 | -0.07782 | -0.21057 | -0.091553 | -0.47607 | -0.064087 | 0.14648 | -0.059509 | 121.8246 | 121.7926 | 116.0339 | -121.7789 | 121.7468 | 121.7789 | 120.52 | -122.049
856.8594 | 122.0673 | -121.7422 | 0.11444 | -0.013122 | 0.018322 | 0.067345 | 0.0026447 | 0.067652 | 0.0033667 | -0.0014442 | -0.011673 | -0.0019909 | 0.06307 | 0.064536 | 0.0076777 | -0.01047 | 0.073242 | -121.0144 | -5.7037 | -121.5546 | 0.14648 | -121.8338 | -121.6873 | -122.2183 | -1.5427 | -121.8979 | 0.041199 | 0.073242 | -121.8246 | -121.9803 | -0.091552 | 0.054932 | 0.032043 | 0.72785 | 0.18768 | 0.13275 | -0.041199 | -0.082397 | -0.23804 | -0.073242 | -0.47607 | -0.15564 | 0.082398 | -0.041199 | 121.8887 | 121.8155 | 116.0385 | -121.8018 | 121.7834 | 121.8155 | 120.1996 | -122.0947
858.6094 | 121.8979 | -121.7743 | 0.15106 | -0.020752 | 0.013196 | 0.070122 | 0.0020039 | 0.064448 | -0.0015465 | -0.0025122 | -0.0040437 | -0.0071179 | 0.06072 | 0.064108 | 0.0025507 | -0.0061972 | 0.082397 | -120.9412 | -5.6946 | -121.55 | 0.091553 | -121.788 | -121.6232 | -122.2183 | -1.5427 | -121.8521 | 0.013733 | 0.054932 | -121.8063 | -121.9757 | -0.013733 | 0.15106 | -0.059509 | 0.83313 | 0.2243 | 0.073242 | -0.068665 | -0.032043 | -0.20142 | -0.13733 | -0.44403 | -0.07782 | 0.1236 | -0.09613 | 121.8658 | 121.8567 | 116.0797 | -121.7743 | 121.788 | 121.8292 | 120.2316 | -122.1268
860.3438 | 121.9345 | -121.7834 | 0.16022 | -0.013122 | 0.018963 | 0.067772 | 0.0049945 | 0.064662 | 0.0052893 | -0.002085 | -0.011673 | -0.0030591 | 0.061788 | 0.064322 | 0.0078913 | -0.0076926 | 0.036621 | -121.0602 | -5.9601 | -121.5775 | 0.1236 | -121.8063 | -121.6736 | -122.2733 | -1.5152 | -121.9528 | 0.054932 | 0.10529 | -121.8155 | -121.9711 | -0.022888 | 0.10986 | -0.036621 | 0.72327 | 0.20599 | 0.09613 | -0.1236 | -0.032044 | -0.18768 | -0.10528 | -0.48981 | -0.16937 | 0.01831 | -0.054931 | 121.907 | 121.8201 | 115.8234 | -121.8338 | 121.8384 | 121.8887 | 120.2682 | -122.1313
862.0938 | 122.081 | -121.7377 | 0.13275 | -0.013122 | 0.015973 | 0.068626 | 0.0067035 | 0.066371 | 0.00058966 | -0.0022986 | 0.0035858 | -0.0064771 | 0.063284 | 0.066031 | 0.0019099 | -0.008547 | -0.004578 | -121.0739 | -5.7587 | -121.6049 | 0.14648 | -121.8155 | -121.6873 | -122.287 | -1.7441 | -121.9437 | 0.064087 | 0.07782 | -121.8475 | -121.9894 | -0.07782 | 0.050354 | 0.013733 | 0.66376 | 0.13275 | 0.082398 | -0.13733 | -0.10986 | -0.25177 | -0.068664 | -0.54932 | -0.20599 | 0.045776 | -0.054931 | 121.8842 | 121.7331 | 115.979 | -121.8201 | 121.8018 | 121.8155 | 119.9936 | -122.1222
863.8438 | 121.9345 | -121.7834 | 0.14648 | -0.013122 | 0.017041 | 0.067131 | 0.0064899 | 0.067439 | 0.0018713 | -0.00037596 | -0.0040437 | -0.0032727 | 0.062856 | 0.066245 | 0.0053279 | -0.0076926 | 0.013733 | -121.051 | -5.658 | -121.5958 | 0.1236 | -121.8155 | -121.6599 | -122.2824 | -2.1332 | -121.9528 | 0.054932 | 0.10529 | -121.8109 | -121.9757 | -0.032044 | 0.1236 | -0.022888 | 0.73242 | 0.18768 | 0.064087 | -0.13275 | -0.027466 | -0.19226 | -0.091552 | -0.49896 | -0.16937 | 0.022888 | -0.041198 | 121.907 | 121.7972 | 116.1255 | -121.8063 | 121.8384 | 121.8887 | 119.6503 | -122.1222
865.5312 | 122.0581 | -121.7377 | 0.11444 | 0.0021362 | 0.017682 | 0.066063 | 0.0058491 | 0.06808 | 0.00080326 | -0.00016236 | -0.0040437 | -0.0030591 | 0.062429 | 0.067953 | 0.0046869 | -0.0061972 | 0.045776 | -121.0144 | -5.5984 | -121.5591 | 0.13275 | -121.8109 | -121.6827 | -122.2458 | -2.2293 | -121.8842 | 0.032043 | 0.064087 | -121.8018 | -121.9803 | -0.073242 | 0.054932 | 0.01831 | 0.72327 | 0.17853 | 0.1236 | -0.068665 | -0.064087 | -0.24262 | -0.082398 | -0.50812 | -0.14648 | 0.096131 | -0.050354 | 121.8704 | 121.7834 | 116.1392 | -121.7972 | 121.7697 | 121.8018 | 119.5084 | -122.0947
867.2656 | 122.0261 | -121.7331 | 0.11444 | -0.020752 | 0.016827 | 0.06884 | 0.0064899 | 0.064448 | -0.0030419 | -0.0027258 | -0.0040437 | -0.0071179 | 0.062429 | 0.064749 | 0.0012689 | -0.008547 | -0.013733 | -121.051 | -5.6671 | -121.6003 | 0.11902 | -121.8292 | -121.6782 | -122.3099 | -2.3621 | -121.9162 | 0.059509 | 0.10071 | -121.8567 | -121.9711 | -0.096131 | 0.054931 | 0.004578 | 0.68207 | 0.13275 | 0.07782 | -0.12817 | -0.1236 | -0.23804 | -0.054932 | -0.57678 | -0.18311 | 0.054931 | -0.013733 | 121.8521 | 121.7194 | 116.066 | -121.7926 | 121.7926 | 121.8338 | 119.371 | -122.0856
869 | 121.994 | -121.7789 | 0.1236 | 0.0021362 | 0.013196 | 0.067772 | 0.0064899 | 0.067011 | -0.0053919 | -0.0018714 | -0.0040437 | -0.0094677 | 0.062002 | 0.064536 | 0.00062806 | -0.0059836 | -0.004578 | -121.0373 | -5.7999 | -121.5546 | 0.11902 | -121.788 | -121.6415 | -122.2458 | -2.4902 | -121.8475 | 0.022888 | 0.07782 | -121.8338 | -121.9391 | -0.009155 | 0.13733 | -0.004577 | 0.74158 | 0.22431 | 0.086976 | -0.12817 | -0.054931 | -0.16022 | -0.10071 | -0.46692 | -0.068664 | 0.091553 | -0.045776 | 121.8979 | 121.7743 | 115.979 | -121.7651 | 121.8018 | 121.8567 | 119.2886 | -122.0627
870.75 | 122.0123 | -121.7514 | 0.13733 | -0.013122 | 0.014905 | 0.069481 | 0.0067035 | 0.064875 | -0.0021875 | -0.0050758 | -0.019302 | -0.0039135 | 0.061361 | 0.066245 | 0.0025507 | -0.0094016 | 0.054932 | -120.9824 | -5.7266 | -121.5591 | 0.11444 | -121.8109 | -121.6736 | -122.2549 | -2.3758 | -121.8933 | 0.054932 | 0.091553 | -121.843 | -121.962 | -0.059509 | 0.07782 | -0.022888 | 0.76904 | 0.19226 | 0.11444 | -0.082397 | -0.091553 | -0.21057 | -0.082397 | -0.50354 | -0.14191 | 0.068664 | -0.045776 | 121.8658 | 121.8063 | 116.0248 | -121.8109 | 121.8063 | 121.843 | 119.3756 | -122.0993
872.4219 | 121.9208 | -121.7972 | 0.14191 | -0.013122 | 0.017254 | 0.067131 | 0.0026447 | 0.063593 | 0.0040077 | 5.1244e-05 | -0.0040437 | -0.0034863 | 0.060934 | 0.06539 | 0.0081049 | -0.0098288 | -0.009155 | -121.1014 | -5.928 | -121.6049 | 0.12817 | -121.8063 | -121.6644 | -122.2824 | -2.0096 | -121.9711 | 0.064087 | 0.082397 | -121.8155 | -121.9803 | -0.009155 | 0.13275 | -0.013733 | 0.6958 | 0.19226 | 0.05951 | -0.15106 | -0.018311 | -0.18311 | -0.07782 | -0.48523 | -0.17395 | 0.009156 | -0.05951 | 121.9254 | 121.788 | 115.8691 | -121.8063 | 121.8613 | 121.8796 | 119.7876 | -122.1222
874.1562 | 121.9757 | -121.788 | 0.16479 | -0.020752 | 0.017468 | 0.064781 | 0.0017901 | 0.066798 | 0.0025123 | -0.0029394 | -0.0040437 | -0.0022045 | 0.061361 | 0.065817 | 0.0053279 | -0.006838 | -0.004578 | -121.1197 | -5.8914 | -121.6049 | 0.15564 | -121.8155 | -121.6965 | -122.2961 | -1.9363 | -121.962 | 0.054932 | 0.091553 | -121.8384 | -121.9528 | -0.027466 | 0.091553 | -0.009155 | 0.66833 | 0.18311 | 0.091553 | -0.16937 | -0.050354 | -0.16479 | -0.10986 | -0.50812 | -0.17395 | -0.009155 | -0.073242 | 121.9437 | 121.7834 | 115.8966 | -121.8613 | 121.843 | 121.8796 | 119.8517 | -122.1176
875.9062 | 121.9574 | -121.8018 | 0.15564 | -0.013122 | 0.018322 | 0.068413 | 0.0026447 | 0.068934 | 0.0016577 | -0.0012306 | -0.019302 | -0.0028455 | 0.06307 | 0.065817 | 0.0044733 | -0.0066244 | -0.022888 | -121.1426 | -5.896 | -121.6278 | 0.15564 | -121.8155 | -121.6873 | -122.3099 | -1.8448 | -121.9757 | 0.068665 | 0.086975 | -121.8475 | -122.0123 | -0.013733 | 0.11444 | 0 | 0.65918 | 0.17395 | 0.059509 | -0.17853 | -0.045776 | -0.21057 | -0.086975 | -0.50812 | -0.17395 | 0.036621 | -0.068665 | 121.9574 | 121.7789 | 115.9058 | -121.843 | 121.8704 | 121.8887 | 119.957 | -122.168
877.6562 | 121.9391 | -121.788 | 0.14191 | -0.013122 | 0.014264 | 0.067558 | 0.0049945 | 0.067011 | -0.0058191 | -0.002085 | -0.011673 | -0.0077587 | 0.063711 | 0.064963 | -0.00044014 | -0.00577 | 0.041199 | -121.0281 | -5.9006 | -121.5683 | 0.09613 | -121.788 | -121.6324 | -122.2687 | -1.799 | -121.8475 | 0.027466 | 0.059509 | -121.8292 | -121.962 | 0 | 0.15564 | -0.045777 | 0.75989 | 0.21973 | 0.064087 | -0.10071 | -0.041199 | -0.17395 | -0.11444 | -0.48065 | -0.059509 | 0.11444 | -0.082398 | 121.8842 | 121.8292 | 115.8875 | -121.7743 | 121.8155 | 121.8475 | 119.989 | -122.1039
879.3281 | 121.9437 | -121.7606 | 0.12817 | 0.0021362 | 0.010418 | 0.069054 | 0.0034991 | 0.066798 | -0.0030419 | -0.0033668 | -0.019302 | -0.0077587 | 0.061788 | 0.064108 | 0.0038325 | -0.007479 | 0.059509 | -121.0144 | -5.5756 | -121.5729 | 0.082397 | -121.7834 | -121.669 | -122.2641 | -1.799 | -121.8658 | 0.032043 | 0.059509 | -121.8201 | -121.9574 | -0.022888 | 0.091553 | -0.045777 | 0.74616 | 0.18768 | 0.09613 | -0.068665 | -0.059509 | -0.19684 | -0.096131 | -0.50354 | -0.10529 | 0.091552 | -0.068665 | 121.843 | 121.8201 | 116.185 | -121.7972 | 121.7926 | 121.8201 | 119.9615 | -122.0856
881 | 121.9849 | -121.756 | 0.13733 | -0.0054933 | 0.016186 | 0.066277 | 0.0037127 | 0.067866 | -0.00026494 | -0.002085 | -0.011673 | -0.0041271 | 0.061148 | 0.064963 | 0.0044733 | -0.0094016 | 0.10529 | -121.0007 | -5.3604 | -121.5454 | 0.10071 | -121.7926 | -121.6644 | -122.1863 | -1.8219 | -121.8201 | 0.022888 | 0.059509 | -121.8018 | -121.9116 | -0.036622 | 0.091552 | -0.036621 | 0.75531 | 0.21057 | 0.11902 | -0.032043 | -0.045777 | -0.15564 | -0.11444 | -0.4303 | -0.064087 | 0.091553 | -0.07782 | 121.8567 | 121.8613 | 116.3956 | -121.8018 | 121.7789 | 121.8155 | 119.9341 | -122.0489
882.75 | 122.0306 | -121.7148 | 0.10986 | -0.013122 | 0.012127 | 0.070976 | 0.0069171 | 0.067652 | -0.0064599 | -0.0031532 | -0.011673 | -0.0071179 | 0.06072 | 0.064108 | 0.0012689 | -0.0053426 | 0.036621 | -121.0419 | -5.4108 | -121.5683 | 0.11444 | -121.7834 | -121.669 | -122.2504 | -1.9775 | -121.8475 | 0.036621 | 0.068665 | -121.8063 | -121.962 | -0.068664 | 0.045777 | 0.004578 | 0.67291 | 0.14648 | 0.10071 | -0.073242 | -0.091552 | -0.24719 | -0.073242 | -0.53558 | -0.13275 | 0.11444 | -0.041198 | 121.8292 | 121.7514 | 116.304 | -121.7789 | 121.7514 | 121.7834 | 119.7372 | -122.0718
884.4844 | 121.9437 | -121.8018 | 0.14191 | -0.0054933 | 0.018536 | 0.068413 | 0.00050847 | 0.066371 | 0.0065711 | -0.00016236 | 0.0035858 | -0.0011365 | 0.061788 | 0.066245 | 0.0074641 | -0.008547 | 0.045776 | -121.1014 | -5.0171 | -121.6003 | 0.12817 | -121.8155 | -121.6782 | -122.2687 | -2.0828 | -121.962 | 0.054932 | 0.10529 | -121.8292 | -121.9757 | -0.013733 | 0.1236 | -0.013733 | 0.70038 | 0.20142 | 0.07782 | -0.096131 | -0.027466 | -0.17395 | -0.086975 | -0.46692 | -0.16022 | 0.013733 | -0.036621 | 121.9299 | 121.8475 | 116.7847 | -121.8201 | 121.8567 | 121.907 | 119.7189 | -122.1176
886.1562 | 122.0078 | -121.7743 | 0.12817 | -0.0054933 | 0.015332 | 0.069481 | 0.0037127 | 0.065516 | 0.0016577 | -0.0027258 | -0.011673 | -0.0049817 | 0.061788 | 0.064963 | 0.0055415 | -0.0076926 | 0.045776 | -121.0602 | -5.159 | -121.5637 | 0.1236 | -121.7926 | -121.6599 | -122.1954 | -2.092 | -121.8475 | 0 | 0.068665 | -121.8338 | -121.962 | -0.018311 | 0.11444 | -0.004578 | 0.71411 | 0.21057 | 0.09613 | -0.082398 | -0.059509 | -0.18768 | -0.12817 | -0.42114 | -0.073242 | 0.11444 | -0.059509 | 121.8979 | 121.8201 | 116.6153 | -121.788 | 121.7743 | 121.843 | 119.6823 | -122.0901
887.9062 | 122.0535 | -121.7377 | 0.11902 | -0.0054933 | 0.015118 | 0.071403 | 0.0090533 | 0.062312 | -0.0053919 | -0.00037596 | -0.0040437 | -0.0056225 | 0.062643 | 0.064322 | -1.2744e-05 | -0.00577 | 0.045776 | -121.019 | -5.6717 | -121.55 | 0.10071 | -121.7789 | -121.6599 | -122.2275 | -2.2385 | -121.8201 | 0.022888 | 0.054932 | -121.8018 | -121.9757 | -0.041199 | 0.07782 | -0.018311 | 0.71869 | 0.18768 | 0.10986 | -0.073243 | -0.064087 | -0.23804 | -0.096131 | -0.48981 | -0.082397 | 0.15564 | -0.064087 | 121.8384 | 121.7834 | 116.066 | -121.7789 | 121.7606 | 121.7926 | 119.4992 | -122.0947
889.5938 | 122.0627 | -121.7422 | 0.11902 | -0.013122 | 0.014691 | 0.069054 | 0.0045673 | 0.068507 | -0.0024011 | -0.0012306 | -0.011673 | -0.0056225 | 0.060934 | 0.064322 | 0.00062806 | -0.007479 | 0.1236 | -120.9412 | -5.7312 | -121.5179 | 0.10071 | -121.7697 | -121.6507 | -122.1771 | -2.092 | -121.7926 | 0.004578 | 0.045776 | -121.8063 | -121.9528 | -0.027465 | 0.091553 | -0.018311 | 0.80109 | 0.22431 | 0.13275 | 0.004577 | -0.064086 | -0.21057 | -0.11444 | -0.43488 | -0.050354 | 0.16022 | -0.073243 | 121.843 | 121.8658 | 116.011 | -121.7697 | 121.7468 | 121.788 | 119.6503 | -122.0718
891.3438 | 122.0901 | -121.7331 | 0.1236 | 0.0021362 | 0.020886 | 0.066704 | 0.0060627 | 0.065516 | 0.0027259 | -0.0014442 | -0.0040437 | -0.0015637 | 0.062429 | 0.066885 | 0.0059687 | -0.0098288 | 0.07782 | -121.0464 | -5.9509 | -121.5775 | 0.12817 | -121.8155 | -121.6782 | -122.2046 | -2.1561 | -121.9116 | 0.041199 | 0.082397 | -121.8292 | -121.9803 | -0.082398 | 0.054931 | 0.004578 | 0.68664 | 0.15564 | 0.10071 | -0.045776 | -0.096131 | -0.24719 | -0.082397 | -0.4715 | -0.17853 | 0.068665 | -0.041199 | 121.8613 | 121.8109 | 115.7822 | -121.8018 | 121.7743 | 121.8155 | 119.577 | -122.1039
893.0938 | 122.0215 | -121.7377 | 0.13275 | 0.0021362 | 0.013623 | 0.068626 | 0.0058491 | 0.06573 | -0.0013329 | -0.0035804 | 0.0035858 | -0.0054089 | 0.062856 | 0.06539 | 0.0027643 | -0.0089742 | 0.032043 | -121.0556 | -6.1111 | -121.582 | 0.13275 | -121.8292 | -121.6873 | -122.2824 | -2.3254 | -121.9345 | 0.073242 | 0.09613 | -121.8658 | -121.9986 | -0.091553 | 0.050354 | 0 | 0.68207 | 0.15564 | 0.10529 | -0.10071 | -0.12817 | -0.26093 | -0.059509 | -0.54474 | -0.19684 | 0.064087 | -0.036621 | 121.8704 | 121.7697 | 115.6265 | -121.8201 | 121.8109 | 121.8338 | 119.4122 | -122.1313
894.8281 | 122.0856 | -121.7102 | 0.11902 | -0.028381 | 0.014905 | 0.069267 | 0.0045673 | 0.066371 | -0.0051781 | -0.0016578 | -0.011673 | -0.0071179 | 0.06307 | 0.064322 | 0.0025507 | -0.0091878 | 0.11444 | -120.9412 | -6.102 | -121.5317 | 0.10986 | -121.7972 | -121.6553 | -122.1725 | -2.3621 | -121.788 | 0.009155 | 0.054932 | -121.8063 | -121.9894 | -0.086975 | 0.054932 | -0.009156 | 0.76904 | 0.17853 | 0.1236 | -0.004578 | -0.09613 | -0.27924 | -0.10986 | -0.46234 | -0.07782 | 0.20142 | -0.064087 | 121.8201 | 121.8246 | 115.6082 | -121.7743 | 121.7194 | 121.7651 | 119.3481 | -122.1085
896.5156 | 122.0535 | -121.756 | 0.10529 | 0.0097657 | 0.019604 | 0.065849 | 0.0041401 | 0.064875 | 0.0046485 | -0.00037596 | -0.0040437 | -0.0030591 | 0.064352 | 0.066458 | 0.0068231 | -0.0094016 | 0.082397 | -121.0373 | -6.395 | -121.5637 | 0.14648 | -121.8018 | -121.6553 | -122.2137 | -2.4445 | -121.8979 | 0.036621 | 0.091553 | -121.8246 | -121.9666 | -0.045777 | 0.10071 | 0.041198 | 0.71869 | 0.19226 | 0.091552 | -0.022889 | -0.068665 | -0.21057 | -0.068665 | -0.45776 | -0.14191 | 0.068665 | -0.013733 | 121.9025 | 121.8384 | 115.361 | -121.7606 | 121.7926 | 121.8475 | 119.3115 | -122.0718
898.25 | 121.9803 | -121.7743 | 0.16937 | -0.013122 | 0.017468 | 0.06414 | 0.0034991 | 0.066798 | 0.0031531 | -0.0016578 | 0.0035858 | -0.0022045 | 0.061788 | 0.066245 | 0.0066095 | -0.0087606 | 0.073242 | -121.0327 | -6.5414 | -121.582 | 0.11902 | -121.8384 | -121.6965 | -122.2321 | -2.3529 | -121.9208 | 0.041199 | 0.082397 | -121.8246 | -121.994 | -0.064087 | 0.07782 | -0.050354 | 0.74158 | 0.19226 | 0.11444 | -0.096131 | -0.050354 | -0.21973 | -0.12817 | -0.45776 | -0.14648 | 0.073243 | -0.086976 | 121.8933 | 121.8475 | 115.2328 | -121.8658 | 121.8155 | 121.8567 | 119.4214 | -122.1634
900 | 122.0032 | -121.7926 | 0.14648 | -0.013122 | 0.018322 | 0.069054 | 0.0052081 | 0.066798 | 0.0027259 | -0.0010168 | -0.0040437 | -0.0041271 | 0.062429 | 0.06539 | 0.0076777 | -0.0081198 | 0.054932 | -121.0236 | -6.6238 | -121.5775 | 0.1236 | -121.8338 | -121.7102 | -122.2321 | -2.417 | -121.9116 | 0.054932 | 0.068665 | -121.8384 | -121.9849 | -0.041198 | 0.082398 | -0.022888 | 0.76904 | 0.21515 | 0.13275 | -0.091552 | -0.045776 | -0.19226 | -0.091552 | -0.43945 | -0.11902 | 0.073242 | -0.077819 | 121.9162 | 121.8475 | 115.1688 | -121.8567 | 121.8475 | 121.8613 | 119.3756 | -122.1313
901.6719 | 121.9254 | -121.7972 | 0.13275 | -0.020752 | 0.015332 | 0.071403 | 0.0045673 | 0.06573 | -0.0041101 | -0.0027258 | -0.011673 | -0.010109 | 0.061575 | 0.063681 | 0.0044733 | -0.0042746 | 0.064087 | -120.9641 | -6.7154 | -121.5546 | 0.082397 | -121.7926 | -121.6553 | -122.2229 | -2.1423 | -121.8521 | 0.013733 | 0.050354 | -121.8246 | -121.9528 | 0.004577 | 0.14191 | -0.050354 | 0.83313 | 0.24262 | 0.10071 | -0.068664 | -0.027466 | -0.15564 | -0.11902 | -0.42572 | -0.054932 | 0.10071 | -0.082397 | 121.8796 | 121.8613 | 115.0818 | -121.788 | 121.8109 | 121.8475 | 119.6548 | -122.0856
903.4062 | 121.9849 | -121.7606 | 0.15106 | 0.0021362 | 0.015973 | 0.067986 | 0.0045673 | 0.066798 | 0.0033667 | 0.00047844 | -0.011673 | -0.0054089 | 0.060934 | 0.066458 | 0.0053279 | -0.0089742 | 0.018311 | -121.0648 | -6.8207 | -121.6095 | 0.12817 | -121.8246 | -121.701 | -122.2 | -2.5131 | -121.875 | 0.013733 | 0.050354 | -121.8475 | -121.9666 | -0.064087 | 0.059509 | -0.022888 | 0.6958 | 0.15106 | 0.091553 | -0.13275 | -0.086975 | -0.20599 | -0.13733 | -0.43945 | -0.11444 | 0.091553 | -0.10071 | 121.8887 | 121.7789 | 114.9399 | -121.8521 | 121.7743 | 121.8109 | 119.2474 | -122.1176
905.1406 | 122.0352 | -121.7194 | 0.10071 | -0.020752 | 0.015118 | 0.069908 | 0.0052081 | 0.065302 | -0.0036829 | -0.0027258 | -0.011673 | -0.0079725 | 0.062856 | 0.062827 | 0.0053279 | -0.0066244 | 0.086975 | -120.9549 | -7.1365 | -121.5225 | 0.09613 | -121.788 | -121.6827 | -122.1909 | -2.4994 | -121.8292 | 0.009155 | 0.045776 | -121.7972 | -121.9666 | -0.068665 | 0.036621 | -0.004578 | 0.76447 | 0.19684 | 0.16022 | -0.013733 | -0.07782 | -0.24719 | -0.091553 | -0.4715 | -0.10986 | 0.13733 | -0.054932 | 121.8155 | 121.8063 | 114.5828 | -121.7834 | 121.7285 | 121.7651 | 119.22 | -122.0673
906.8281 | 122.0718 | -121.756 | 0.11902 | -0.0054933 | 0.016186 | 0.067345 | 0.0047809 | 0.066371 | 0.0022987 | -0.0014442 | -0.0040437 | -0.0019909 | 0.06307 | 0.06774 | 0.0068231 | -0.010042 | 0.050354 | -121.0693 | -7.7454 | -121.5866 | 0.14648 | -121.8155 | -121.6965 | -122.2092 | -2.2247 | -121.907 | 0.036621 | 0.082397 | -121.8338 | -121.994 | -0.05951 | 0.059509 | 0.027465 | 0.68664 | 0.16937 | 0.10986 | -0.068665 | -0.07782 | -0.23804 | -0.082398 | -0.45319 | -0.15106 | 0.086976 | -0.036622 | 121.9025 | 121.8063 | 114.0106 | -121.8155 | 121.7926 | 121.8384 | 119.5312 | -122.113
908.5625 | 122.049 | -121.7651 | 0.11444 | -0.0054933 | 0.016186 | 0.067986 | 0.0069171 | 0.06872 | -0.0021875 | -0.0027258 | -0.011673 | -0.0049817 | 0.062216 | 0.066458 | 0.0036189 | -0.0081198 | 0 | -121.0739 | -7.8461 | -121.6049 | 0.12817 | -121.8338 | -121.7056 | -122.2961 | -2.2385 | -121.9345 | 0.050354 | 0.10071 | -121.8658 | -121.9849 | -0.068664 | 0.05951 | 0.013733 | 0.69122 | 0.16022 | 0.10071 | -0.11444 | -0.10071 | -0.21973 | -0.064087 | -0.53101 | -0.16937 | 0.050354 | -0.013733 | 121.8933 | 121.7651 | 113.9191 | -121.8201 | 121.8155 | 121.8658 | 119.5267 | -122.0993
910.2969 | 122.0581 | -121.756 | 0.1236 | -0.0054933 | 0.016613 | 0.068626 | 0.0090533 | 0.067652 | -0.0015465 | -0.0031532 | -0.011673 | -0.0047681 | 0.062216 | 0.066458 | 0.0012689 | -0.007479 | -0.009155 | -121.0968 | -7.5211 | -121.6141 | 0.13733 | -121.8201 | -121.6965 | -122.3053 | -2.2659 | -121.9437 | 0.073242 | 0.086975 | -121.875 | -122.0078 | -0.064087 | 0.059509 | 0.013733 | 0.65918 | 0.14191 | 0.082397 | -0.13275 | -0.11902 | -0.25177 | -0.050354 | -0.54932 | -0.18768 | 0.064086 | -0.036621 | 121.8933 | 121.7468 | 114.2349 | -121.8201 | 121.8292 | 121.843 | 119.4901 | -122.1313
911.9844 | 122.0032 | -121.7926 | 0.13733 | -0.0054933 | 0.016613 | 0.068413 | 0.0037127 | 0.068934 | 0.00080326 | -0.002085 | -0.0040437 | -0.0049817 | 0.062643 | 0.064322 | 0.0027643 | -0.0089742 | 0.022888 | -121.0785 | -7.7637 | -121.6049 | 0.11444 | -121.8155 | -121.6873 | -122.2229 | -2.4628 | -121.8796 | 0.013733 | 0.054932 | -121.8384 | -121.9757 | -0.022888 | 0.10529 | -0.022888 | 0.71411 | 0.18768 | 0.082398 | -0.11444 | -0.045776 | -0.1831 | -0.1236 | -0.4303 | -0.086975 | 0.09613 | -0.082397 | 121.907 | 121.8155 | 114.0289 | -121.8246 | 121.8063 | 121.8475 | 119.3298 | -122.113
913.7188 | 122.0947 | -121.7285 | 0.11902 | -0.020752 | 0.021313 | 0.065636 | 0.0069171 | 0.066798 | 0.00058966 | -0.0012306 | 0.0035858 | -0.0041271 | 0.063497 | 0.067099 | 0.0046869 | -0.0087606 | 0 | -121.0693 | -7.9514 | -121.5775 | 0.14648 | -121.8338 | -121.6965 | -122.2595 | -2.5726 | -121.9345 | 0.045776 | 0.086975 | -121.8292 | -121.9986 | -0.10528 | 0.032044 | 0.027465 | 0.65918 | 0.15106 | 0.11902 | -0.11902 | -0.10071 | -0.27008 | -0.073243 | -0.53101 | -0.20599 | 0.064087 | -0.032044 | 121.875 | 121.7285 | 113.7772 | -121.8155 | 121.7743 | 121.8155 | 119.1559 | -122.1176
915.3906 | 121.9666 | -121.7743 | 0.13733 | -0.013122 | 0.013623 | 0.067986 | 0.0020039 | 0.064021 | -0.0013329 | -0.002085 | -0.011673 | -0.0077587 | 0.059011 | 0.063895 | 0.0027643 | -0.008547 | 0.07782 | -120.9778 | -7.9559 | -121.5179 | 0.091553 | -121.8018 | -121.6415 | -122.1725 | -2.7328 | -121.8292 | 0.013733 | 0.032043 | -121.7972 | -121.9666 | -0.027466 | 0.13275 | -0.045776 | 0.79651 | 0.25635 | 0.1236 | -0.059509 | -0.022888 | -0.19226 | -0.1236 | -0.39825 | -0.054932 | 0.13733 | -0.10529 | 121.8658 | 121.8521 | 113.8184 | -121.7789 | 121.788 | 121.8063 | 119.0414 | -122.1039
917.1406 | 121.9437 | -121.7926 | 0.15106 | 0.0097657 | 0.015545 | 0.068413 | 0.0045673 | 0.064448 | -0.0011193 | 0.00026484 | -0.011673 | -0.0096813 | 0.062002 | 0.062613 | 0.0021235 | -0.0083334 | 0.054932 | -120.9915 | -8.0566 | -121.5775 | 0.10071 | -121.788 | -121.6782 | -122.2275 | -3.1815 | -121.8521 | 0.004578 | 0.064087 | -121.8155 | -121.9666 | 0.004578 | 0.11444 | -0.050354 | 0.80109 | 0.21515 | 0.10071 | -0.09613 | -0.022888 | -0.17395 | -0.14648 | -0.43488 | -0.059509 | 0.11444 | -0.086975 | 121.8933 | 121.8475 | 113.736 | -121.8292 | 121.7972 | 121.8567 | 118.6111 | -122.1176
918.875 | 122.0535 | -121.7422 | 0.12817 | -0.0054933 | 0.013623 | 0.069481 | 0.0043537 | 0.06573 | -0.0053919 | -0.0029394 | -0.011673 | -0.0066907 | 0.06072 | 0.063681 | 0.0036189 | -0.0064108 | 0.022888 | -121.0327 | -8.345 | -121.5637 | 0.10986 | -121.8292 | -121.6736 | -122.2412 | -3.8727 | -121.8521 | 0.013733 | 0.068665 | -121.788 | -121.9345 | -0.086975 | 0.068665 | -0.018311 | 0.70953 | 0.17853 | 0.10986 | -0.10529 | -0.045776 | -0.19226 | -0.11444 | -0.49896 | -0.10986 | 0.082397 | -0.059509 | 121.8521 | 121.7651 | 113.3972 | -121.8018 | 121.756 | 121.8109 | 117.8696 | -122.0627
920.625 | 122.0718 | -121.7514 | 0.11444 | -0.028381 | 0.014905 | 0.068199 | 0.0049945 | 0.066584 | -0.0032555 | -0.0048622 | -0.019302 | -0.0039135 | 0.06072 | 0.06539 | 0.0031915 | -0.0096152 | 0.10529 | -120.9686 | -8.3679 | -121.5408 | 0.09613 | -121.8109 | -121.6599 | -122.1771 | -4.2206 | -121.788 | 0.013733 | 0.064087 | -121.7697 | -121.9757 | -0.059509 | 0.091553 | -0.018311 | 0.78278 | 0.21057 | 0.11902 | -0.009155 | -0.01831 | -0.2243 | -0.10071 | -0.42572 | -0.036621 | 0.18768 | -0.050354 | 121.8475 | 121.8567 | 113.3835 | -121.7743 | 121.7651 | 121.8155 | 117.5308 | -122.0901
922.3125 | 122.0947 | -121.7514 | 0.09613 | -0.013122 | 0.017468 | 0.069267 | 0.0056355 | 0.064448 | 0.00058966 | -0.0044348 | -0.011673 | -0.0019909 | 0.061575 | 0.065604 | 0.0038325 | -0.0094016 | 0.009155 | -121.1151 | -8.313 | -121.6232 | 0.16022 | -121.8384 | -121.7194 | -122.2778 | -5.4108 | -121.9666 | 0.059509 | 0.10529 | -121.8338 | -122.0078 | -0.086975 | 0.032044 | 0.064087 | 0.63629 | 0.12817 | 0.09613 | -0.086975 | -0.082397 | -0.25635 | -0.036621 | -0.52643 | -0.21515 | 0.041198 | 0.009156 | 121.9116 | 121.7606 | 113.4384 | -121.8155 | 121.8109 | 121.8567 | 116.3406 | -122.1039
923.9844 | 122.0261 | -121.7468 | 0.13275 | -0.0054933 | 0.018963 | 0.06649 | 0.0049945 | 0.067652 | 0.0037939 | -0.00016236 | -0.011673 | -0.0017773 | 0.060934 | 0.064749 | 0.0059687 | -0.0098288 | 0.082397 | -121.0373 | -8.107 | -121.5866 | 0.13733 | -121.7926 | -121.6782 | -122.1954 | -5.9143 | -121.9299 | 0.036621 | 0.073242 | -121.8475 | -122.0078 | -0.045777 | 0.068664 | 0.004578 | 0.70953 | 0.16022 | 0.091553 | -0.050354 | -0.10071 | -0.26093 | -0.09613 | -0.44861 | -0.18311 | 0.077819 | -0.059509 | 121.8842 | 121.8292 | 113.6398 | -121.8109 | 121.7834 | 121.8201 | 115.8325 | -122.1405
925.7344 | 122.0993 | -121.7606 | 0.12817 | -0.020752 | 0.016186 | 0.067986 | 0.0034991 | 0.065089 | 0.0020849 | -0.00037596 | -0.011673 | -0.0026319 | 0.063925 | 0.067526 | 0.0051141 | -0.0072652 | 0.009155 | -121.0831 | -8.313 | -121.582 | 0.14191 | -121.8292 | -121.7194 | -122.2366 | -6.546 | -121.9254 | 0.045776 | 0.07782 | -121.8475 | -121.9757 | -0.068665 | 0.041199 | 0.013733 | 0.67749 | 0.17853 | 0.13733 | -0.11902 | -0.086975 | -0.21515 | -0.082398 | -0.47607 | -0.16479 | 0.050354 | -0.050354 | 121.9025 | 121.7697 | 113.4476 | -121.8475 | 121.8063 | 121.8384 | 115.2145 | -122.1039
927.4688 | 122.0398 | -121.7514 | 0.11444 | -0.0054933 | 0.017041 | 0.069267 | 0.0073443 | 0.065302 | -0.0028283 | -0.0018714 | 0.0035858 | -0.0069043 | 0.06307 | 0.06774 | 0.0036189 | -0.0064108 | 0 | -121.0693 | -8.7982 | -121.6095 | 0.11902 | -121.8155 | -121.6827 | -122.2778 | -7.6492 | -121.9437 | 0.054932 | 0.09613 | -121.8704 | -121.9757 | -0.064087 | 0.068665 | 0.004578 | 0.68207 | 0.14191 | 0.073242 | -0.11444 | -0.11902 | -0.2243 | -0.059509 | -0.52643 | -0.19226 | 0.032043 | -0.018311 | 121.8704 | 121.7514 | 112.9532 | -121.7972 | 121.8063 | 121.8475 | 114.1022 | -122.0901
929.2031 | 121.962 | -121.7697 | 0.15564 | -0.013122 | 0.013623 | 0.064995 | 0.0024311 | 0.067225 | -0.0017603 | -0.00080316 | -0.011673 | -0.0056225 | 0.059011 | 0.065817 | 0.0029779 | -0.0081198 | 0.086975 | -120.9641 | -8.4274 | -121.5317 | 0.091553 | -121.7926 | -121.6919 | -122.1359 | -7.695 | -121.8292 | 0 | 0.054932 | -121.8109 | -121.9711 | -0.022889 | 0.077819 | -0.064087 | 0.80566 | 0.23804 | 0.16022 | -0.068665 | -0.041199 | -0.20142 | -0.15564 | -0.36621 | -0.05951 | 0.14191 | -0.10071 | 121.8613 | 121.8567 | 113.3423 | -121.8475 | 121.7697 | 121.8246 | 114.0747 | -122.1268
930.9531 | 122.0352 | -121.756 | 0.11444 | -0.020752 | 0.017254 | 0.068626 | 0.0052081 | 0.065516 | -0.0024011 | -0.0031532 | -0.011673 | -0.0071179 | 0.062002 | 0.064536 | 0.0038325 | -0.0096152 | 0.086975 | -120.9641 | -8.3359 | -121.5225 | 0.073242 | -121.7972 | -121.6599 | -122.1771 | -8.7204 | -121.8292 | 0.004578 | 0.059509 | -121.8246 | -121.9711 | -0.041199 | 0.09613 | -0.041199 | 0.79193 | 0.23346 | 0.13733 | -0.027466 | -0.068665 | -0.21515 | -0.10986 | -0.42114 | -0.073243 | 0.14191 | -0.054932 | 121.8292 | 121.843 | 113.4201 | -121.7743 | 121.7606 | 121.8155 | 113.0356 | -122.0856
932.7031 | 121.9986 | -121.7834 | 0.13275 | -0.0054933 | 0.017682 | 0.068413 | 0.0034991 | 0.068507 | 0.0035803 | -0.0016578 | -0.0040437 | -0.0036999 | 0.061361 | 0.065176 | 0.0089593 | -0.0089742 | 0 | -121.1105 | -8.6197 | -121.6324 | 0.15106 | -121.8201 | -121.7056 | -122.2641 | -9.8007 | -121.9666 | 0.059509 | 0.073242 | -121.8338 | -122.0123 | -0.036621 | 0.07782 | 0.018311 | 0.67291 | 0.15106 | 0.073242 | -0.13275 | -0.050354 | -0.22888 | -0.073242 | -0.48065 | -0.18311 | 0.045776 | -0.059509 | 121.9345 | 121.7834 | 113.1638 | -121.8384 | 121.843 | 121.8567 | 111.9827 | -122.1451
934.4531 | 122.0627 | -121.7514 | 0.13275 | -0.020752 | 0.017468 | 0.070122 | 0.0037127 | 0.067439 | 0.0035803 | -0.0012306 | -0.011673 | -0.00070932 | 0.060934 | 0.065604 | 0.0072505 | -0.0087606 | 0.059509 | -121.0373 | -8.0521 | -121.5775 | 0.14648 | -121.8109 | -121.6873 | -122.2046 | -9.9426 | -121.9162 | 0.045776 | 0.07782 | -121.8292 | -121.9894 | -0.059509 | 0.064087 | 0.013733 | 0.71411 | 0.17395 | 0.10986 | -0.073242 | -0.07782 | -0.23804 | -0.086975 | -0.45319 | -0.1648 | 0.073242 | -0.054931 | 121.8979 | 121.8109 | 113.6993 | -121.8201 | 121.7972 | 121.8292 | 111.8088 | -122.1222
936.125 | 121.962 | -121.7834 | 0.16479 | -0.013122 | 0.018109 | 0.068626 | 0.0049945 | 0.06573 | 0.0012305 | -0.00058956 | -0.011673 | -0.0024183 | 0.063711 | 0.064536 | 0.0061823 | -0.006838 | -0.004578 | -121.1014 | -8.2718 | -121.6232 | 0.13733 | -121.8246 | -121.7148 | -122.2595 | -10.8856 | -121.9894 | 0.054932 | 0.091553 | -121.8613 | -122.0078 | -0.041199 | 0.068664 | -0.027466 | 0.68207 | 0.16022 | 0.091553 | -0.16937 | -0.07782 | -0.2243 | -0.10986 | -0.47607 | -0.20599 | 0.01831 | -0.073242 | 121.9208 | 121.7789 | 113.5117 | -121.8796 | 121.8384 | 121.875 | 110.8978 | -122.1725
937.875 | 121.9528 | -121.7972 | 0.14648 | -0.0054933 | 0.013196 | 0.069481 | 0.0073443 | 0.065089 | -0.0062463 | -0.0010168 | -0.011673 | -0.0071179 | 0.062643 | 0.065817 | 0.0012689 | -0.0079062 | 0.022888 | -121.0419 | -8.638 | -121.5729 | 0.10986 | -121.7697 | -121.6553 | -122.2458 | -11.9385 | -121.8704 | 0.022888 | 0.082397 | -121.8109 | -121.9666 | 0.027466 | 0.14191 | -0.036621 | 0.75531 | 0.2243 | 0.082397 | -0.1236 | -0.013733 | -0.16937 | -0.1236 | -0.44861 | -0.073242 | 0.096131 | -0.064087 | 121.907 | 121.8201 | 113.1592 | -121.8018 | 121.8201 | 121.8796 | 109.8587 | -122.113
939.5469 | 121.9711 | -121.8063 | 0.15106 | -0.0054933 | 0.012982 | 0.070122 | 0.0034991 | 0.064662 | -0.0041101 | -0.0048622 | -0.019302 | -0.0051953 | 0.059439 | 0.064536 | 0.0021235 | -0.0072652 | 0.050354 | -121.0281 | -8.6014 | -121.5775 | 0.11444 | -121.8063 | -121.6827 | -122.2412 | -12.8769 | -121.875 | 0.027466 | 0.054932 | -121.8246 | -121.9711 | 0 | 0.1236 | -0.036621 | 0.7782 | 0.22888 | 0.10528 | -0.10071 | -0.018311 | -0.16479 | -0.1236 | -0.43488 | -0.068665 | 0.09613 | -0.09613 | 121.9208 | 121.8567 | 113.205 | -121.8338 | 121.8338 | 121.8613 | 108.9294 | -122.1222
941.2969 | 122.0901 | -121.7468 | 0.12817 | -0.020752 | 0.014691 | 0.069267 | 0.0069171 | 0.065089 | -0.0045373 | -0.0061438 | -0.0040437 | -0.0077587 | 0.062002 | 0.064322 | 0.0014825 | -0.0091878 | 0.10529 | -120.9732 | -8.2169 | -121.5408 | 0.10529 | -121.8063 | -121.6507 | -122.168 | -13.5773 | -121.8063 | 0.004578 | 0.045776 | -121.8109 | -121.9299 | -0.059509 | 0.09613 | -0.022888 | 0.77362 | 0.20599 | 0.10986 | -0.022888 | -0.064087 | -0.18311 | -0.1236 | -0.42114 | -0.059509 | 0.1236 | -0.082398 | 121.8521 | 121.8521 | 113.53 | -121.7789 | 121.7514 | 121.7926 | 108.1696 | -122.0581
943.0469 | 122.0306 | -121.7697 | 0.1236 | -0.013122 | 0.018322 | 0.068626 | 0.0064899 | 0.067652 | -0.0013329 | -0.0029394 | -0.011673 | -0.0047681 | 0.063925 | 0.064963 | 0.0029779 | -0.0083334 | 0.054932 | -121.0602 | -8.4686 | -121.5912 | 0.1236 | -121.8155 | -121.6965 | -122.2641 | -13.9618 | -121.9254 | 0.041199 | 0.086975 | -121.8658 | -122.0032 | -0.045777 | 0.073242 | 0 | 0.70953 | 0.17853 | 0.10528 | -0.068664 | -0.096131 | -0.23346 | -0.082397 | -0.49439 | -0.15564 | 0.07782 | -0.036621 | 121.8933 | 121.8246 | 113.3011 | -121.8201 | 121.8109 | 121.8567 | 107.8079 | -122.1268
944.7344 | 122.0627 | -121.7239 | 0.11444 | -0.013122 | 0.014905 | 0.067558 | 0.0064899 | 0.067439 | 0.0010169 | -0.0012306 | -0.019302 | -0.0060497 | 0.064138 | 0.066458 | 0.0031915 | -0.0089742 | -0.004578 | -121.1197 | -8.4229 | -121.6278 | 0.16022 | -121.8155 | -121.7239 | -122.2595 | -14.2456 | -121.9666 | 0.064087 | 0.10071 | -121.875 | -122.0032 | -0.091553 | 0 | 0.045776 | 0.60425 | 0.09613 | 0.09613 | -0.11902 | -0.15106 | -0.27924 | -0.050354 | -0.53558 | -0.24262 | 0.036621 | -0.013733 | 121.8842 | 121.7194 | 113.3011 | -121.8384 | 121.788 | 121.8246 | 107.4783 | -122.1176
946.4844 | 122.0627 | -121.7468 | 0.11902 | -0.013122 | 0.016186 | 0.069908 | 0.0069171 | 0.066157 | -0.00069214 | -0.0027258 | -0.0040437 | -0.0043409 | 0.064138 | 0.066458 | 0.0053279 | -0.0089742 | 0 | -121.106 | -8.2535 | -121.6324 | 0.14648 | -121.8613 | -121.7056 | -122.2778 | -14.4745 | -121.9482 | 0.073242 | 0.086975 | -121.8521 | -122.0123 | -0.11444 | 0.041199 | 0.027465 | 0.64087 | 0.11444 | 0.073242 | -0.11902 | -0.10529 | -0.2655 | -0.045777 | -0.53101 | -0.20142 | 0.064087 | -0.032044 | 121.8933 | 121.7468 | 113.4933 | -121.8246 | 121.8201 | 121.8338 | 107.2723 | -122.1313
948.2344 | 121.9757 | -121.7972 | 0.13733 | -0.0054933 | 0.018109 | 0.066277 | 0.0015765 | 0.068507 | 0.0029395 | 0.001333 | -0.0040437 | -0.0034863 | 0.06307 | 0.066672 | 0.0057551 | -0.008547 | 0.054932 | -121.051 | -8.9172 | -121.6003 | 0.11902 | -121.8246 | -121.6965 | -122.2275 | -13.4491 | -121.9299 | 0.059509 | 0.086975 | -121.8521 | -122.0032 | -0.027466 | 0.10071 | -0.01831 | 0.74616 | 0.19684 | 0.09613 | -0.082397 | -0.054932 | -0.20599 | -0.07782 | -0.4303 | -0.13275 | 0.073242 | -0.050354 | 121.9162 | 121.8521 | 112.8799 | -121.8338 | 121.8567 | 121.8842 | 108.3481 | -122.1405
949.9688 | 122.0581 | -121.7422 | 0.10529 | -0.020752 | 0.013409 | 0.070335 | 0.0073443 | 0.066798 | -0.0041101 | -0.0014442 | -0.011673 | -0.0069043 | 0.060079 | 0.066031 | -0.00065374 | -0.0047018 | 0.082397 | -120.932 | -9.407 | -121.5271 | 0.082397 | -121.8246 | -121.6644 | -122.1725 | -13.6322 | -121.8155 | 0.009155 | 0.027466 | -121.8292 | -121.9666 | -0.082397 | 0.07782 | -0.022889 | 0.81024 | 0.21515 | 0.13733 | -0.022889 | -0.086975 | -0.2243 | -0.096131 | -0.4303 | -0.073242 | 0.15106 | -0.07782 | 121.8246 | 121.8246 | 112.3352 | -121.7697 | 121.7514 | 121.7697 | 108.11 | -122.0718
951.6406 | 121.9849 | -121.7834 | 0.14191 | -0.020752 | 0.015545 | 0.066063 | 0.0069171 | 0.066584 | -0.0032555 | -0.0042212 | -0.0040437 | -0.0064771 | 0.063284 | 0.066458 | 0.0014825 | -0.0070516 | 0.045776 | -121.0693 | -9.4299 | -121.5912 | 0.10529 | -121.8155 | -121.6827 | -122.2321 | -13.5727 | -121.8704 | 0.022888 | 0.082397 | -121.8338 | -121.9894 | -0.032044 | 0.10071 | -0.036621 | 0.71411 | 0.19226 | 0.091552 | -0.096131 | -0.050354 | -0.20599 | -0.11902 | -0.44861 | -0.086975 | 0.11902 | -0.05951 | 121.8887 | 121.8292 | 112.3535 | -121.8246 | 121.8063 | 121.8658 | 108.2108 | -122.1313
953.4062 | 122.0306 | -121.7789 | 0.12817 | -0.020752 | 0.017041 | 0.069054 | 0.0045673 | 0.065302 | 0.0031531 | -0.0012306 | -0.0040437 | -0.0028455 | 0.061788 | 0.065604 | 0.0074641 | -0.010042 | 0.086975 | -121.0464 | -9.2606 | -121.582 | 0.15106 | -121.8292 | -121.6873 | -122.1725 | -13.6917 | -121.9299 | 0.041199 | 0.086975 | -121.8658 | -122.0032 | -0.050354 | 0.091553 | 0.022888 | 0.73242 | 0.19684 | 0.10529 | -0.041199 | -0.086975 | -0.2243 | -0.086975 | -0.39368 | -0.15106 | 0.073242 | -0.041199 | 121.9299 | 121.8658 | 112.5183 | -121.8155 | 121.8201 | 121.8658 | 108.0872 | -122.1313
955.0781 | 122.0215 | -121.7377 | 0.1236 | -0.013122 | 0.017254 | 0.068626 | 0.0058491 | 0.066798 | -0.0013329 | -0.0031532 | -0.0040437 | -0.0064771 | 0.062429 | 0.064108 | 0.0027643 | -0.0076926 | 0.064087 | -120.9686 | -9.2422 | -121.5408 | 0.10071 | -121.8155 | -121.6736 | -122.2092 | -14.9643 | -121.8887 | 0.032043 | 0.064087 | -121.8521 | -122.0032 | -0.07782 | 0.064087 | -0.022888 | 0.76904 | 0.19684 | 0.13275 | -0.059509 | -0.11444 | -0.2655 | -0.091553 | -0.4715 | -0.15106 | 0.11444 | -0.059509 | 121.8384 | 121.8018 | 112.4954 | -121.7972 | 121.7697 | 121.8018 | 106.7734 | -122.1268
956.8281 | 121.9803 | -121.8155 | 0.14191 | -0.013122 | 0.016186 | 0.06884 | 0.0054217 | 0.066371 | -0.0034691 | -0.0022986 | -0.011673 | -0.0079725 | 0.061575 | 0.065176 | 0.00020086 | -0.0064108 | 0.027466 | -121.0327 | -9.2651 | -121.5775 | 0.10986 | -121.8109 | -121.6553 | -122.2137 | -15.9073 | -121.8933 | 0.022888 | 0.054932 | -121.8292 | -121.9803 | 0.004578 | 0.16022 | -0.032044 | 0.78278 | 0.23804 | 0.077819 | -0.11444 | -0.013733 | -0.1648 | -0.11902 | -0.39825 | -0.07782 | 0.086975 | -0.086975 | 121.9254 | 121.843 | 112.5504 | -121.7972 | 121.8384 | 121.8704 | 105.9082 | -122.1222
958.5938 | 122.0032 | -121.7697 | 0.13275 | -0.020752 | 0.015118 | 0.068199 | 0.0026447 | 0.066157 | 0.00080326 | -0.0018714 | -0.011673 | -0.0079725 | 0.060507 | 0.065176 | 0.0070367 | -0.0087606 | 0.09613 | -121.0007 | -9.8694 | -121.5454 | 0.10529 | -121.7972 | -121.6827 | -122.1359 | -16.8823 | -121.8384 | 0 | 0.045776 | -121.8384 | -121.9757 | -0.027466 | 0.086975 | -0.027465 | 0.76904 | 0.2243 | 0.13733 | -0.036621 | -0.068665 | -0.20599 | -0.13275 | -0.36621 | -0.068665 | 0.13733 | -0.086975 | 121.875 | 121.8658 | 111.9003 | -121.8155 | 121.7697 | 121.8155 | 104.8874 | -122.1085
960.2656 | 121.9528 | -121.8063 | 0.14648 | -0.013122 | 0.012982 | 0.068413 | 0.00093567 | 0.063807 | -0.0019739 | -0.0010168 | 0.0035858 | -0.0056225 | 0.060079 | 0.066031 | 0.0051141 | -0.0081198 | 0.091553 | -120.9778 | -10.3683 | -121.5363 | 0.086975 | -121.8246 | -121.6782 | -122.1359 | -15.8249 | -121.8475 | 0.013733 | 0.041199 | -121.8063 | -121.9711 | -0.018311 | 0.12817 | -0.059509 | 0.82855 | 0.27008 | 0.14191 | -0.054931 | 0 | -0.16479 | -0.13275 | -0.32959 | -0.041199 | 0.1236 | -0.10529 | 121.8933 | 121.8979 | 111.438 | -121.8246 | 121.8201 | 121.8475 | 105.9814 | -122.1176
962 | 122.0261 | -121.788 | 0.12817 | -0.013122 | 0.015118 | 0.070763 | 0.0075581 | 0.067011 | -0.0032555 | -0.0012306 | -0.019302 | -0.0047681 | 0.061788 | 0.063681 | 0.0036189 | -0.0083334 | 0.050354 | -121.0007 | -10.556 | -121.55 | 0.11444 | -121.843 | -121.7285 | -122.2275 | -17.7841 | -121.9116 | 0.032043 | 0.068665 | -121.8567 | -121.9894 | -0.054932 | 0.059509 | -0.013733 | 0.78735 | 0.23804 | 0.17853 | -0.07782 | -0.068664 | -0.20142 | -0.096131 | -0.43945 | -0.1236 | 0.07782 | -0.059509 | 121.9025 | 121.8384 | 111.232 | -121.8567 | 121.8201 | 121.8567 | 104.0039 | -122.1176
963.7031 | 121.9574 | -121.8109 | 0.16937 | -0.013122 | 0.018109 | 0.068413 | 0.0037127 | 0.064875 | 0.0035803 | 5.1244e-05 | -0.011673 | -0.0017773 | 0.059652 | 0.06539 | 0.0078913 | -0.010683 | 0.009155 | -121.138 | -10.7803 | -121.6187 | 0.14191 | -121.8521 | -121.7285 | -122.2321 | -17.9764 | -121.9757 | 0.045776 | 0.082397 | -121.8292 | -122.0032 | -0.041199 | 0.082397 | -0.027466 | 0.67291 | 0.19226 | 0.10986 | -0.16022 | -0.018311 | -0.19226 | -0.1236 | -0.42114 | -0.16479 | 0.027466 | -0.086976 | 121.9528 | 121.8201 | 111.0306 | -121.8979 | 121.8567 | 121.8933 | 103.8345 | -122.1725
965.4375 | 122.0444 | -121.7743 | 0.1236 | -0.0054933 | 0.017041 | 0.069908 | 0.0052081 | 0.065943 | -0.00090574 | -0.00080316 | -0.011673 | -0.0045545 | 0.062002 | 0.066245 | 0.0019099 | -0.007479 | -0.004578 | -121.0693 | -11.3297 | -121.6187 | 0.1236 | -121.8567 | -121.7102 | -122.2458 | -18.306 | -121.9345 | 0.054932 | 0.086975 | -121.8704 | -122.0032 | -0.082397 | 0.064087 | 0 | 0.70496 | 0.15564 | 0.091553 | -0.12817 | -0.09613 | -0.22888 | -0.068664 | -0.4715 | -0.16022 | 0.068665 | -0.036621 | 121.8979 | 121.7697 | 110.4446 | -121.8338 | 121.8292 | 121.8613 | 103.4683 | -122.1268
967.1094 | 121.9849 | -121.8063 | 0.15106 | -0.0054933 | 0.01875 | 0.065849 | 0.0071307 | 0.066584 | 0.0046485 | -0.00080316 | -0.0040437 | -0.00070932 | 0.063925 | 0.066031 | 0.0059687 | -0.0087606 | 0.059509 | -121.0556 | -11.0779 | -121.5912 | 0.12817 | -121.8246 | -121.701 | -122.1771 | -17.1936 | -121.962 | 0.045776 | 0.086975 | -121.843 | -122.0215 | -0.018311 | 0.10529 | -0.022888 | 0.75073 | 0.21515 | 0.10986 | -0.091553 | -0.036622 | -0.21515 | -0.10529 | -0.37079 | -0.15564 | 0.059509 | -0.064087 | 121.9345 | 121.8658 | 110.7285 | -121.8521 | 121.8521 | 121.8933 | 104.6127 | -122.1725
968.8438 | 121.9345 | -121.7743 | 0.13733 | -0.0054933 | 0.011487 | 0.070122 | -0.00013253 | 0.064234 | -0.0043237 | -0.00037596 | -0.019302 | -0.0075451 | 0.06072 | 0.066672 | 0.0046869 | -0.005129 | 0.07782 | -120.9595 | -10.7025 | -121.5637 | 0.10529 | -121.8155 | -121.6599 | -122.1222 | -18.2281 | -121.8384 | -0.009155 | 0.022888 | -121.8384 | -121.9666 | -0.041199 | 0.11444 | -0.032043 | 0.81482 | 0.21057 | 0.09613 | -0.059509 | -0.064087 | -0.19226 | -0.14648 | -0.3479 | -0.064087 | 0.12817 | -0.11444 | 121.8796 | 121.8521 | 111.0718 | -121.7972 | 121.7651 | 121.7972 | 103.5461 | -122.1039
970.5781 | 122.0444 | -121.7651 | 0.1236 | -0.013122 | 0.018109 | 0.066063 | 0.0026447 | 0.064234 | 0.0025123 | -0.0016578 | -0.0040437 | -0.0026319 | 0.062643 | 0.06539 | 0.0066095 | -0.0091878 | 0.054932 | -121.0464 | -10.7941 | -121.582 | 0.1236 | -121.8292 | -121.7056 | -122.1542 | -18.4479 | -121.907 | 0.041199 | 0.07782 | -121.8567 | -122.0123 | -0.064087 | 0.05951 | 0 | 0.71869 | 0.18311 | 0.1236 | -0.068664 | -0.091552 | -0.24719 | -0.082397 | -0.3891 | -0.14191 | 0.10529 | -0.045776 | 121.8887 | 121.8201 | 110.9711 | -121.8292 | 121.8063 | 121.843 | 103.3173 | -122.1359
972.3125 | 121.9894 | -121.7789 | 0.12817 | -0.0054933 | 0.015118 | 0.06884 | 0.0037127 | 0.062312 | -0.00090574 | -0.00080316 | -0.011673 | -0.0054089 | 0.060079 | 0.064963 | 0.0053279 | -0.0064108 | 0.082397 | -120.9641 | -11.2427 | -121.5363 | 0.082397 | -121.8109 | -121.6599 | -122.1359 | -19.2398 | -121.8521 | -0.004578 | 0.036621 | -121.8521 | -121.9711 | -0.032043 | 0.11902 | -0.045777 | 0.81482 | 0.24262 | 0.1236 | -0.045777 | -0.073242 | -0.19226 | -0.13275 | -0.35706 | -0.073242 | 0.11902 | -0.091553 | 121.8613 | 121.8613 | 110.5362 | -121.788 | 121.7743 | 121.8155 | 102.5391 | -122.0993
973.9844 | 121.9894 | -121.7834 | 0.16937 | -0.0054933 | 0.018109 | 0.067345 | 0.0056355 | 0.065943 | 0.0018713 | 0.00047844 | 0.0035858 | -0.0019909 | 0.060934 | 0.068381 | 0.0055415 | -0.0070516 | -0.004578 | -121.1609 | -11.618 | -121.6507 | 0.15106 | -121.8521 | -121.7056 | -122.2595 | -20.4437 | -121.994 | 0.054932 | 0.07782 | -121.875 | -122.0078 | -0.068665 | 0.07782 | -0.018311 | 0.62256 | 0.13275 | 0.054931 | -0.17395 | -0.091553 | -0.2243 | -0.11444 | -0.47607 | -0.21057 | 0.013732 | -0.091553 | 121.9345 | 121.7789 | 110.1654 | -121.875 | 121.8384 | 121.8613 | 101.3397 | -122.1771
975.7188 | 122.0581 | -121.7789 | 0.1236 | -0.020752 | 0.017254 | 0.068413 | 0.0094807 | 0.066371 | -0.00047854 | -0.0018714 | -0.0040437 | -0.0034863 | 0.063284 | 0.066885 | 0.0019099 | -0.0070516 | -0.027466 | -121.0922 | -11.1923 | -121.6278 | 0.15106 | -121.8475 | -121.7194 | -122.2549 | -21.0434 | -121.962 | 0.054932 | 0.091553 | -121.875 | -121.9803 | -0.068664 | 0.05951 | 0.027466 | 0.68665 | 0.15106 | 0.091552 | -0.15106 | -0.09613 | -0.20142 | -0.068664 | -0.47607 | -0.1831 | 0.018311 | -0.032043 | 121.9299 | 121.7514 | 110.5865 | -121.843 | 121.8338 | 121.8704 | 100.7355 | -122.1039
977.4688 | 122.0993 | -121.7697 | 0.10986 | -0.013122 | 0.015545 | 0.06884 | 0.0062763 | 0.066584 | -5.1338e-05 | -0.0033668 | -0.0040437 | -0.0034863 | 0.063711 | 0.066245 | 0.0034051 | -0.0081198 | 0.013733 | -121.0648 | -11.8057 | -121.5775 | 0.15106 | -121.8475 | -121.701 | -122.2 | -20.5078 | -121.9345 | 0.054932 | 0.068665 | -121.8658 | -122.0261 | -0.07782 | 0.068664 | 0.041199 | 0.70496 | 0.19226 | 0.1236 | -0.09613 | -0.096131 | -0.25635 | -0.054931 | -0.4303 | -0.1648 | 0.091553 | -0.041198 | 121.9208 | 121.7834 | 109.964 | -121.8109 | 121.8246 | 121.8384 | 101.2619 | -122.1359
979.1406 | 121.9986 | -121.8063 | 0.1236 | -0.013122 | 0.015973 | 0.066063 | 0.0026447 | 0.063807 | 0.0016577 | 0.00026484 | 0.0035858 | -0.0034863 | 0.062856 | 0.066245 | 0.0042597 | -0.0076926 | 0.054932 | -121.0236 | -11.8286 | -121.582 | 0.12817 | -121.8567 | -121.6919 | -122.1863 | -20.4941 | -121.9299 | 0.032043 | 0.068665 | -121.8384 | -122.0352 | -0.050354 | 0.11444 | 0.004578 | 0.78278 | 0.2243 | 0.10986 | -0.068664 | -0.032044 | -0.22888 | -0.091553 | -0.37994 | -0.1236 | 0.10529 | -0.054931 | 121.9345 | 121.8613 | 109.9777 | -121.8155 | 121.8384 | 121.875 | 101.3123 | -122.1588
980.8906 | 122.0078 | -121.788 | 0.13733 | -0.020752 | 0.016186 | 0.069695 | 0.0052081 | 0.065516 | -0.0017603 | 0.0011194 | 0.0035858 | -0.0047681 | 0.06072 | 0.064749 | 0.0046869 | -0.007479 | 0.004578 | -121.0876 | -12.4191 | -121.6232 | 0.14191 | -121.8155 | -121.7239 | -122.1954 | -20.6955 | -121.9162 | 0.032043 | 0.07782 | -121.8796 | -121.9803 | -0.027466 | 0.064087 | 0.004578 | 0.70038 | 0.16479 | 0.10071 | -0.13275 | -0.091553 | -0.19226 | -0.10529 | -0.40741 | -0.12817 | 0.064087 | -0.059509 | 121.9299 | 121.7926 | 109.3689 | -121.8613 | 121.8201 | 121.8658 | 101.0925 | -122.1176
982.5781 | 122.0673 | -121.7514 | 0.10986 | -0.0054933 | 0.015332 | 0.068626 | 0.0058491 | 0.065089 | -0.0060327 | -0.0010168 | -0.011673 | -0.0073315 | 0.063497 | 0.062827 | 0.00062806 | -0.006838 | 0.07782 | -120.9045 | -12.3047 | -121.5271 | 0.10529 | -121.8109 | -121.6782 | -122.1313 | -20.1096 | -121.8109 | 0.004578 | 0.050354 | -121.8521 | -121.9574 | -0.059509 | 0.073242 | -0.004577 | 0.84686 | 0.2243 | 0.15106 | -0.032043 | -0.10071 | -0.20599 | -0.10529 | -0.37994 | -0.059509 | 0.14648 | -0.059509 | 121.8567 | 121.8292 | 109.4467 | -121.788 | 121.756 | 121.8018 | 101.6418 | -122.0673
984.3125 | 122.0032 | -121.7697 | 0.14191 | -0.013122 | 0.017468 | 0.06884 | 0.0022175 | 0.064234 | -0.00026494 | -0.0031532 | -0.0040437 | -0.0056225 | 0.06072 | 0.062827 | 0.0083185 | -0.0059836 | 0.022888 | -121.0876 | -13.1241 | -121.6278 | 0.14191 | -121.8338 | -121.6919 | -122.1954 | -20.2927 | -121.9162 | 0.032043 | 0.068665 | -121.8613 | -121.9986 | -0.064087 | 0.077819 | 0 | 0.68207 | 0.14191 | 0.064087 | -0.11902 | -0.091553 | -0.22888 | -0.10986 | -0.42572 | -0.14649 | 0.082397 | -0.073242 | 121.9116 | 121.7926 | 108.6456 | -121.8338 | 121.8018 | 121.8384 | 101.477 | -122.1405
985.9844 | 122.0078 | -121.7926 | 0.12817 | -0.013122 | 0.018322 | 0.067986 | 0.0032855 | 0.065943 | 0.0022987 | 0.00047844 | -0.011673 | -0.0030591 | 0.061148 | 0.065604 | 0.0061823 | -0.0083334 | 0.004578 | -121.106 | -13.3118 | -121.6278 | 0.13733 | -121.8292 | -121.7148 | -122.2 | -20.929 | -121.9437 | 0.045776 | 0.086975 | -121.8613 | -122.0032 | -0.036621 | 0.07782 | 0.009155 | 0.68665 | 0.16479 | 0.086975 | -0.1236 | -0.068664 | -0.21057 | -0.082398 | -0.40741 | -0.15106 | 0.059509 | -0.041199 | 121.9299 | 121.7972 | 108.4808 | -121.843 | 121.8384 | 121.8796 | 100.8636 | -122.1313
987.7188 | 122.081 | -121.7468 | 0.10529 | -0.013122 | 0.012341 | 0.069908 | 0.0060627 | 0.066371 | -0.0058191 | -0.0025122 | -0.011673 | -0.0081861 | 0.060293 | 0.064108 | 0.0014825 | -0.0072652 | 0.050354 | -120.9686 | -13.266 | -121.5454 | 0.09613 | -121.8201 | -121.6919 | -122.1588 | -20.1004 | -121.8246 | 0.036621 | 0.059509 | -121.8292 | -121.9894 | -0.073242 | 0.054931 | -0.009156 | 0.7782 | 0.20142 | 0.14648 | -0.054932 | -0.082398 | -0.24262 | -0.068665 | -0.41199 | -0.07782 | 0.16479 | -0.045777 | 121.843 | 121.7972 | 108.4808 | -121.7972 | 121.7834 | 121.8063 | 101.6464 | -122.0947
989.3906 | 122.0444 | -121.7697 | 0.10986 | -0.020752 | 0.016613 | 0.070763 | 0.0084125 | 0.068293 | 0.0010169 | -0.0044348 | -0.019302 | -0.0043409 | 0.062856 | 0.066672 | -0.00044014 | -0.0087606 | 0.004578 | -121.0693 | -13.4079 | -121.6187 | 0.14648 | -121.8475 | -121.7194 | -122.2641 | -20.5673 | -121.9528 | 0.050354 | 0.091553 | -121.8887 | -122.0215 | -0.07782 | 0.050354 | 0.036621 | 0.70038 | 0.15106 | 0.10071 | -0.10529 | -0.11902 | -0.25177 | -0.059509 | -0.49439 | -0.18311 | 0.068664 | -0.01831 | 121.9162 | 121.7743 | 108.3618 | -121.8292 | 121.8201 | 121.8613 | 101.2024 | -122.1313
991.0625 | 122.0947 | -121.7743 | 0.1236 | -0.013122 | 0.020031 | 0.066277 | 0.0069171 | 0.066584 | 0.0018713 | -0.00016236 | -0.011673 | -0.0045545 | 0.064352 | 0.064963 | 0.0053279 | -0.0089742 | 0.045776 | -121.0464 | -14.0671 | -121.5866 | 0.13275 | -121.8292 | -121.6827 | -122.1817 | -21.0571 | -121.9208 | 0.036621 | 0.07782 | -121.8658 | -122.0123 | -0.054932 | 0.091553 | 0.009155 | 0.72784 | 0.18768 | 0.09613 | -0.07782 | -0.091553 | -0.23804 | -0.086975 | -0.40741 | -0.14648 | 0.091553 | -0.045776 | 121.907 | 121.8201 | 107.7072 | -121.8063 | 121.8109 | 121.8521 | 100.7172 | -122.1359
992.8125 | 122.0078 | -121.756 | 0.13733 | -0.013122 | 0.016186 | 0.064781 | 0.0028583 | 0.06573 | 0.0035803 | 0.0011194 | -0.011673 | -0.0030591 | 0.062856 | 0.064963 | 0.0044733 | -0.0072652 | 0 | -121.0831 | -14.5432 | -121.6278 | 0.14191 | -121.8338 | -121.6965 | -122.2137 | -21.3867 | -121.962 | 0.032043 | 0.07782 | -121.8567 | -121.994 | -0.07782 | 0.059509 | 0.004578 | 0.67291 | 0.12817 | 0.068664 | -0.13733 | -0.10071 | -0.23804 | -0.10529 | -0.45776 | -0.20599 | 0.032044 | -0.059509 | 121.8979 | 121.756 | 107.2128 | -121.8338 | 121.788 | 121.8338 | 100.3693 | -122.1313
994.5469 | 122.0215 | -121.7743 | 0.11902 | -0.0054933 | 0.013623 | 0.069908 | 0.0052081 | 0.064662 | -0.0051781 | -0.0012306 | -0.026932 | -0.0090405 | 0.062002 | 0.066245 | -0.00065374 | -0.007479 | 0.009155 | -121.0281 | -14.2548 | -121.582 | 0.10529 | -121.8063 | -121.6827 | -122.2092 | -19.9814 | -121.8704 | 0.013733 | 0.064087 | -121.8658 | -121.9894 | -0.032043 | 0.091553 | -0.013733 | 0.74616 | 0.19226 | 0.10071 | -0.10986 | -0.091553 | -0.21515 | -0.10529 | -0.43487 | -0.09613 | 0.11902 | -0.054932 | 121.8796 | 121.7834 | 107.5195 | -121.8018 | 121.788 | 121.8384 | 101.7929 | -122.1085
996.2969 | 122.0123 | -121.7972 | 0.13275 | -0.013122 | 0.015545 | 0.068413 | -0.00077333 | 0.065302 | 0.0012305 | -0.00037596 | 0.0035858 | -0.0028455 | 0.057516 | 0.065176 | 0.0046869 | -0.0087606 | 0.10529 | -120.9824 | -14.0579 | -121.5591 | 0.11444 | -121.8063 | -121.6873 | -122.1222 | -20.2423 | -121.8521 | -0.009155 | 0.054932 | -121.8384 | -121.9711 | -0.009155 | 0.10986 | -0.01831 | 0.81482 | 0.23804 | 0.12817 | -0.027465 | -0.041199 | -0.17395 | -0.14191 | -0.32501 | -0.054932 | 0.11902 | -0.077819 | 121.9116 | 121.9025 | 107.7393 | -121.8201 | 121.788 | 121.8521 | 101.5549 | -122.1039
998.0312 | 122.0078 | -121.7926 | 0.13733 | -0.0054933 | 0.015759 | 0.068199 | 0.0026447 | 0.066371 | 0.00037606 | -0.0014442 | -0.011673 | -0.0051953 | 0.062856 | 0.064963 | 0.0072505 | -0.0089742 | 0.10529 | -120.9595 | -14.1998 | -121.55 | 0.09613 | -121.8018 | -121.6736 | -122.1222 | -20.3156 | -121.8521 | 0.004578 | 0.059509 | -121.8155 | -121.9711 | -0.009155 | 0.11902 | -0.041199 | 0.83313 | 0.24262 | 0.1236 | -0.032043 | -0.022888 | -0.17853 | -0.13275 | -0.32959 | -0.059509 | 0.11902 | -0.07782 | 121.8887 | 121.8979 | 107.5928 | -121.8109 | 121.7972 | 121.8521 | 101.4771 | -122.1085
999.7812 | 122.0123 | -121.7834 | 0.1236 | -0.013122 | 0.015118 | 0.06884 | 0.0067035 | 0.064234 | -0.0060327 | -0.002085 | -0.0040437 | -0.0064771 | 0.064352 | 0.063467 | 0.00062806 | -0.0079062 | 0.018311 | -121.0144 | -14.6118 | -121.5775 | 0.10529 | -121.8246 | -121.6873 | -122.1909 | -20.3384 | -121.8887 | 0.032043 | 0.07782 | -121.8292 | -121.994 | -0.041199 | 0.09613 | -0.01831 | 0.76904 | 0.20599 | 0.10986 | -0.10528 | -0.045777 | -0.21057 | -0.091553 | -0.40741 | -0.10529 | 0.10529 | -0.045776 | 121.8887 | 121.8018 | 107.1716 | -121.8109 | 121.8155 | 121.8613 | 101.445 | -122.1176
1001.5312 | 122.049 | -121.7743 | 0.13275 | -0.013122 | 0.015332 | 0.069695 | 0.0071307 | 0.066157 | -0.0028283 | -0.0048622 | -0.0040437 | -0.0058361 | 0.062002 | 0.066885 | 0.00041446 | -0.0079062 | 0.027466 | -121.019 | -16.4108 | -121.5912 | 0.11444 | -121.8292 | -121.6919 | -122.1771 | -21.6385 | -121.8658 | 0.013733 | 0.059509 | -121.8613 | -121.962 | -0.054932 | 0.082397 | -0.01831 | 0.75531 | 0.1831 | 0.10071 | -0.10529 | -0.086975 | -0.18768 | -0.11902 | -0.40283 | -0.091553 | 0.09613 | -0.073242 | 121.8887 | 121.8018 | 105.3635 | -121.8246 | 121.788 | 121.8338 | 100.1358 | -122.0947
1003.2188 | 122.0078 | -121.8109 | 0.13733 | 0.0021362 | 0.015545 | 0.067131 | 0.0024311 | 0.069148 | 0.0046485 | -0.0022986 | -0.019302 | -6.8316e-05 | 0.060934 | 0.067099 | 0.0068231 | -0.0098288 | 0.045776 | -121.0831 | -15.9485 | -121.6232 | 0.14191 | -121.8384 | -121.7331 | -122.1725 | -20.668 | -121.9162 | 0.027466 | 0.064087 | -121.8338 | -122.0123 | -0.027466 | 0.07782 | 0.004578 | 0.72784 | 0.18768 | 0.10986 | -0.091553 | -0.022888 | -0.20142 | -0.10986 | -0.36163 | -0.10529 | 0.09613 | -0.073242 | 121.9528 | 121.8567 | 105.8624 | -121.8704 | 121.8384 | 121.875 | 101.1429 | -122.1497
1004.9531 | 122.0535 | -121.7926 | 0.11444 | 0.0021362 | 0.015973 | 0.068413 | 0.0043537 | 0.064448 | -0.0015465 | -0.0040076 | -0.0040437 | -0.0073315 | 0.063925 | 0.066458 | 0.0051141 | -0.0083334 | 0.022888 | -121.0144 | -15.802 | -121.6003 | 0.13275 | -121.8567 | -121.7239 | -122.2321 | -20.9106 | -121.9574 | 0.050354 | 0.082397 | -121.8796 | -122.0123 | -0.064086 | 0.068665 | 0.01831 | 0.7782 | 0.19226 | 0.1236 | -0.091553 | -0.086975 | -0.21973 | -0.064087 | -0.43945 | -0.16479 | 0.054932 | -0.032044 | 121.9254 | 121.8155 | 105.9906 | -121.8384 | 121.843 | 121.875 | 100.882 | -122.1268
1006.625 | 122.081 | -121.7514 | 0.1236 | -0.0054933 | 0.018109 | 0.068413 | 0.0058491 | 0.066157 | -5.1338e-05 | -0.0031532 | -0.0040437 | -0.0047681 | 0.064779 | 0.065817 | 0.0027643 | -0.0072652 | -0.013733 | -121.0693 | -15.8386 | -121.6278 | 0.14191 | -121.843 | -121.6965 | -122.2412 | -21.1853 | -121.9711 | 0.054932 | 0.09613 | -121.8704 | -122.0169 | -0.091553 | 0.054932 | 0.018311 | 0.68207 | 0.1236 | 0.068664 | -0.13733 | -0.11902 | -0.2655 | -0.068664 | -0.48981 | -0.21973 | 0.045777 | -0.027466 | 121.8933 | 121.7377 | 105.9128 | -121.8201 | 121.8063 | 121.8475 | 100.5661 | -122.1405
1008.3125 | 122.1222 | -121.756 | 0.11902 | -0.0054933 | 0.019177 | 0.066277 | 0.0056355 | 0.064448 | 0.0027259 | -0.0012306 | -0.011673 | -0.0036999 | 0.064352 | 0.064963 | 0.0038325 | -0.0089742 | -0.004578 | -121.0373 | -15.5731 | -121.6095 | 0.13733 | -121.8384 | -121.7239 | -122.1863 | -22.3206 | -121.9528 | 0.054932 | 0.09613 | -121.8567 | -122.0169 | -0.082398 | 0.032043 | 0.01831 | 0.71869 | 0.14648 | 0.11444 | -0.1236 | -0.10071 | -0.26093 | -0.064087 | -0.4303 | -0.19684 | 0.064087 | -0.022889 | 121.8933 | 121.7514 | 106.1829 | -121.843 | 121.8109 | 121.8521 | 99.4354 | -122.1359
1010.0469 | 122.0673 | -121.7422 | 0.10529 | -0.013122 | 0.014477 | 0.071403 | 0.0054217 | 0.066371 | -0.0071007 | -0.0033668 | -0.0040437 | -0.0066907 | 0.061148 | 0.064749 | -0.00022634 | -0.008547 | 0.09613 | -120.8954 | -16.1545 | -121.5454 | 0.11444 | -121.8246 | -121.6507 | -122.113 | -22.0551 | -121.8246 | 0 | 0.064087 | -121.8246 | -121.9803 | -0.082397 | 0.091553 | 0.009155 | 0.84686 | 0.19684 | 0.10529 | -0.009156 | -0.082397 | -0.23804 | -0.10529 | -0.37079 | -0.082397 | 0.15564 | -0.041199 | 121.8567 | 121.8384 | 105.5878 | -121.756 | 121.7422 | 121.8063 | 99.6872 | -122.0856
1011.7812 | 122.0673 | -121.7743 | 0.11444 | 0.0021362 | 0.017254 | 0.069054 | 0.0039265 | 0.064875 | 0.00016226 | -0.0031532 | -0.0040437 | -0.0051953 | 0.061361 | 0.065604 | 0.0023371 | -0.008547 | -0.013733 | -121.0327 | -16.1179 | -121.6278 | 0.13275 | -121.8475 | -121.7194 | -122.2366 | -22.229 | -121.9528 | 0.050354 | 0.09613 | -121.9025 | -122.0352 | -0.073242 | 0.054932 | 0.01831 | 0.74158 | 0.14648 | 0.091552 | -0.12817 | -0.12817 | -0.26093 | -0.064087 | -0.46234 | -0.17853 | 0.082397 | -0.018311 | 121.907 | 121.7606 | 105.6564 | -121.8338 | 121.8246 | 121.8704 | 99.5453 | -122.1497
1013.4688 | 122.0306 | -121.7743 | 0.11902 | -0.013122 | 0.013836 | 0.071617 | 0.0047809 | 0.065516 | -0.0028283 | -0.0012306 | 0.0035858 | -0.0083997 | 0.061788 | 0.062827 | 0.0027643 | -0.0072652 | 0.018311 | -120.9732 | -16.4246 | -121.5866 | 0.1236 | -121.8155 | -121.6965 | -122.1863 | -21.8353 | -121.875 | 0.018311 | 0.054932 | -121.8384 | -122.0032 | -0.041199 | 0.07782 | 0.004577 | 0.80109 | 0.18768 | 0.10986 | -0.10071 | -0.064087 | -0.22888 | -0.10071 | -0.41199 | -0.10071 | 0.12817 | -0.064087 | 121.8979 | 121.7926 | 105.3497 | -121.8155 | 121.7926 | 121.8292 | 99.939 | -122.1222
1015.2031 | 121.994 | -121.7743 | 0.14648 | -0.0054933 | 0.016827 | 0.066704 | 0.00093567 | 0.063807 | 0.0044349 | 0.00026484 | -0.011673 | -0.0011365 | 0.063284 | 0.064963 | 0.0076777 | -0.0098288 | 0.082397 | -120.9869 | -16.6306 | -121.6095 | 0.13733 | -121.8292 | -121.7056 | -122.1817 | -22.1603 | -121.9528 | 0.041199 | 0.068665 | -121.8887 | -122.0169 | -0.054932 | 0.068665 | -0.009155 | 0.78735 | 0.16479 | 0.09613 | -0.064087 | -0.11444 | -0.24262 | -0.10529 | -0.40741 | -0.17853 | 0.064087 | -0.077819 | 121.9116 | 121.8567 | 105.1437 | -121.8521 | 121.8155 | 121.843 | 99.614 | -122.1634
1016.9375 | 122.0673 | -121.7789 | 0.1236 | -0.0054933 | 0.017895 | 0.066704 | 0.0084125 | 0.063166 | -0.00069214 | -0.0012306 | 0.0035858 | -0.0051953 | 0.06542 | 0.065817 | 0.0025507 | -0.0064108 | -0.018311 | -121.0098 | -17.5781 | -121.6324 | 0.13275 | -121.8796 | -121.7285 | -122.2458 | -22.76 | -121.9574 | 0.050354 | 0.10529 | -121.8887 | -122.0352 | -0.10071 | 0.050354 | 0.009155 | 0.76904 | 0.14648 | 0.096131 | -0.14191 | -0.10986 | -0.25635 | -0.073242 | -0.46692 | -0.17853 | 0.07782 | -0.01831 | 121.9116 | 121.7606 | 104.2007 | -121.8521 | 121.8292 | 121.8842 | 99.0189 | -122.1588
1018.6875 | 122.0078 | -121.7697 | 0.13275 | -0.0054933 | 0.014691 | 0.068626 | 0.0030719 | 0.066371 | -5.1338e-05 | 5.1244e-05 | -0.011673 | -0.0056225 | 0.061148 | 0.065176 | 0.0070367 | -0.0083334 | 0.082397 | -120.9183 | -17.8391 | -121.5408 | 0.10986 | -121.8338 | -121.6827 | -122.1222 | -23.3734 | -121.8521 | 0.022888 | 0.045776 | -121.8521 | -121.9849 | -0.064087 | 0.086975 | -0.022888 | 0.85144 | 0.22888 | 0.14191 | -0.050354 | -0.082398 | -0.21515 | -0.10986 | -0.35248 | -0.082398 | 0.13275 | -0.086975 | 121.8796 | 121.8521 | 103.9307 | -121.8155 | 121.7926 | 121.8155 | 98.3963 | -122.1176
1020.4375 | 122.0444 | -121.788 | 0.12817 | -0.0054933 | 0.014691 | 0.070549 | 0.0079853 | 0.064875 | 0.00058966 | -0.0027258 | -0.0040437 | -0.0056225 | 0.060507 | 0.065604 | 0.0031915 | -0.0064108 | -0.013733 | -120.9915 | -17.4179 | -121.6141 | 0.1236 | -121.8384 | -121.7285 | -122.2458 | -23.3139 | -121.9437 | 0.054932 | 0.091553 | -121.907 | -122.0123 | -0.050354 | 0.059509 | -0.004578 | 0.79651 | 0.17395 | 0.11444 | -0.14191 | -0.11902 | -0.2243 | -0.073242 | -0.45776 | -0.15564 | 0.068664 | -0.036621 | 121.9116 | 121.7743 | 104.3701 | -121.8567 | 121.843 | 121.8796 | 98.4741 | -122.1405
1022.125 | 122.0764 | -121.7606 | 0.11902 | -0.020752 | 0.017682 | 0.070335 | 0.0073443 | 0.066371 | -0.00026494 | -0.0022986 | -0.011673 | -0.0039135 | 0.063711 | 0.066672 | 0.0034051 | -0.0061972 | -0.009155 | -121.0373 | -17.4133 | -121.6232 | 0.15564 | -121.8475 | -121.7377 | -122.2412 | -23.0804 | -121.9894 | 0.068665 | 0.082397 | -121.8887 | -122.0352 | -0.086975 | 0.022888 | 0.036621 | 0.72327 | 0.13733 | 0.11444 | -0.12817 | -0.12817 | -0.27466 | -0.050354 | -0.48065 | -0.22888 | 0.045776 | -0.036622 | 121.9162 | 121.7514 | 104.3472 | -121.8567 | 121.8292 | 121.843 | 98.6801 | -122.1542
1023.875 | 121.9711 | -121.8201 | 0.16022 | -0.013122 | 0.013623 | 0.069481 | 0.00093567 | 0.066584 | -0.0034691 | -0.0027258 | -0.011673 | -0.0071179 | 0.058584 | 0.066245 | 0.0027643 | -0.0059836 | 0.068665 | -120.9366 | -17.9214 | -121.5958 | 0.11902 | -121.7972 | -121.6736 | -122.1817 | -23.7076 | -121.875 | 0.013733 | 0.064087 | -121.843 | -121.9894 | 0.022888 | 0.14648 | -0.041198 | 0.88348 | 0.2243 | 0.07782 | -0.091552 | -0.022889 | -0.16937 | -0.14648 | -0.36163 | -0.054932 | 0.11444 | -0.09613 | 121.9391 | 121.8887 | 103.8986 | -121.8338 | 121.8338 | 121.8842 | 98.1125 | -122.1497
1025.5469 | 122.0856 | -121.7743 | 0.09613 | -0.020752 | 0.0164 | 0.072472 | 0.0058491 | 0.064662 | -0.0034691 | -0.0033668 | -0.011673 | -0.0064771 | 0.062856 | 0.063681 | 0.0029779 | -0.010897 | 0.10529 | -120.8679 | -18.2281 | -121.5363 | 0.10071 | -121.8063 | -121.669 | -122.1085 | -24.2661 | -121.8292 | 0.018311 | 0.050354 | -121.843 | -121.9894 | -0.032043 | 0.10529 | 0.004578 | 0.90637 | 0.23804 | 0.13275 | 0.009156 | -0.068665 | -0.21515 | -0.077819 | -0.33417 | -0.054932 | 0.16022 | -0.045776 | 121.875 | 121.8796 | 103.5461 | -121.7651 | 121.7926 | 121.8246 | 97.5082 | -122.0856
1027.2812 | 121.9849 | -121.8109 | 0.15564 | 0.0021362 | 0.0117 | 0.067345 | 0.0039265 | 0.065516 | -0.0030419 | -0.0012306 | -0.0040437 | -0.0071179 | 0.060079 | 0.065817 | 0.0025507 | -0.0081198 | 0.050354 | -120.9641 | -19.4046 | -121.5958 | 0.10071 | -121.8109 | -121.701 | -122.1863 | -24.1013 | -121.9025 | 0.032043 | 0.064087 | -121.8384 | -122.0032 | 0 | 0.10986 | -0.054932 | 0.84686 | 0.21515 | 0.10529 | -0.10529 | -0.027466 | -0.19226 | -0.1236 | -0.37537 | -0.091553 | 0.10071 | -0.091553 | 121.9116 | 121.8613 | 102.4063 | -121.8567 | 121.843 | 121.875 | 97.7097 | -122.1588
1028.9531 | 122.0947 | -121.7834 | 0.13733 | 0.0021362 | 0.018963 | 0.067131 | 0.0075581 | 0.066371 | 0.0052893 | -0.0031532 | -0.011673 | -0.0032727 | 0.062002 | 0.067313 | 0.0055415 | -0.0094016 | 0.022888 | -121.0052 | -20.5536 | -121.6049 | 0.12817 | -121.875 | -121.7285 | -122.1542 | -24.4904 | -121.9299 | 0.045776 | 0.082397 | -121.8796 | -122.0078 | -0.091553 | 0.054931 | -0.009155 | 0.7782 | 0.17853 | 0.1236 | -0.11444 | -0.096131 | -0.2243 | -0.091553 | -0.37079 | -0.14648 | 0.077819 | -0.054932 | 121.9116 | 121.8063 | 101.2299 | -121.8658 | 121.8292 | 121.8658 | 97.2931 | -122.1451
1030.6875 | 122.0764 | -121.7697 | 0.10071 | -0.013122 | 0.016827 | 0.070549 | 0.0049945 | 0.067011 | -0.0013329 | -0.0018714 | -0.019302 | -0.0090405 | 0.061788 | 0.064322 | 0.0012689 | -0.0066244 | 0.1236 | -120.8542 | -20.6543 | -121.5363 | 0.10529 | -121.8201 | -121.6873 | -122.1176 | -24.44 | -121.8246 | 0.013733 | 0.045776 | -121.843 | -121.9711 | -0.050354 | 0.082397 | 0.004578 | 0.91553 | 0.23346 | 0.15106 | 0.022888 | -0.073243 | -0.20142 | -0.086975 | -0.3479 | -0.054932 | 0.14648 | -0.054932 | 121.875 | 121.8933 | 101.1154 | -121.788 | 121.7834 | 121.8155 | 97.3297 | -122.0718
1032.4219 | 122.0169 | -121.7834 | 0.13275 | -0.013122 | 0.017468 | 0.068626 | 0.0017901 | 0.066584 | 0.0042213 | -0.0025122 | 0.0035858 | -0.0049817 | 0.061788 | 0.065604 | 0.0072505 | -0.007479 | 0.018311 | -120.9961 | -21.7667 | -121.6278 | 0.15106 | -121.8567 | -121.7285 | -122.1725 | -25.2686 | -121.9345 | 0.045776 | 0.064087 | -121.8704 | -122.0169 | -0.073242 | 0.054931 | 0.018311 | 0.78735 | 0.15564 | 0.10071 | -0.11444 | -0.086975 | -0.23346 | -0.086975 | -0.3891 | -0.15106 | 0.082398 | -0.068664 | 121.9345 | 121.8018 | 100.0168 | -121.8613 | 121.8292 | 121.8475 | 96.5149 | -122.1497
1034.1562 | 122.0123 | -121.7926 | 0.13275 | -0.013122 | 0.018109 | 0.06884 | 0.0026447 | 0.06338 | 0.0025123 | 0.001333 | -0.0040437 | -0.0024183 | 0.060293 | 0.064322 | 0.0081049 | -0.0087606 | 0.004578 | -121.0052 | -20.787 | -121.6415 | 0.13275 | -121.843 | -121.7239 | -122.1771 | -25.4974 | -121.9482 | 0.036621 | 0.073242 | -121.8704 | -122.0306 | -0.050354 | 0.068665 | 0 | 0.78735 | 0.15106 | 0.082397 | -0.12817 | -0.077819 | -0.23804 | -0.09613 | -0.38452 | -0.15564 | 0.082398 | -0.059509 | 121.9254 | 121.7972 | 101.0056 | -121.8567 | 121.8292 | 121.8658 | 96.2952 | -122.1634
1035.9062 | 122.0306 | -121.7926 | 0.14191 | -0.020752 | 0.016613 | 0.068413 | 0.0032855 | 0.066157 | 0.00016226 | 0.0015466 | -0.0040437 | -0.0028455 | 0.059866 | 0.065817 | 0.0068231 | -0.0072652 | 0.027466 | -121.0007 | -20.8511 | -121.6232 | 0.11444 | -121.8246 | -121.7194 | -122.1313 | -27.182 | -121.9208 | 0.032043 | 0.068665 | -121.8338 | -121.9894 | -0.032043 | 0.073243 | -0.027466 | 0.79193 | 0.16937 | 0.09613 | -0.11444 | -0.041198 | -0.19684 | -0.10986 | -0.33875 | -0.12817 | 0.068665 | -0.073242 | 121.907 | 121.8201 | 100.9415 | -121.8613 | 121.8246 | 121.8613 | 94.6106 | -122.1313
1037.5781 | 122.0123 | -121.8109 | 0.14648 | -0.013122 | 0.017682 | 0.069481 | 0.0041401 | 0.068934 | 0.0020849 | -0.0018714 | -0.0040437 | -0.0045545 | 0.062856 | 0.066458 | 0.0057551 | -0.00577 | 0.004578 | -121.0236 | -20.5307 | -121.6324 | 0.14648 | -121.8521 | -121.7056 | -122.2046 | -27.2369 | -121.9894 | 0.045776 | 0.091553 | -121.8933 | -122.0032 | -0.041199 | 0.10529 | 0 | 0.78735 | 0.17853 | 0.073242 | -0.14191 | -0.082398 | -0.19226 | -0.10071 | -0.39368 | -0.17853 | 0.013733 | -0.054931 | 121.9574 | 121.8155 | 101.2802 | -121.8521 | 121.8567 | 121.9025 | 94.574 | -122.1497
1039.3125 | 121.962 | -121.7789 | 0.13275 | -0.0054933 | 0.013409 | 0.06884 | 0.0039265 | 0.064234 | -0.0019739 | -0.00037596 | -0.019302 | -0.0043409 | 0.059866 | 0.06539 | 0.0036189 | -0.0066244 | 0.09613 | -120.8862 | -21.2677 | -121.5546 | 0.082397 | -121.8109 | -121.6919 | -122.0764 | -26.9119 | -121.8384 | 0.004578 | 0.045776 | -121.8246 | -121.9894 | -0.032043 | 0.086975 | -0.050354 | 0.89264 | 0.22431 | 0.13733 | -0.036621 | -0.045776 | -0.21057 | -0.12817 | -0.29755 | -0.059509 | 0.15106 | -0.086975 | 121.8613 | 121.875 | 100.5112 | -121.8246 | 121.7834 | 121.8246 | 94.8669 | -122.1222
1040.9844 | 121.962 | -121.8155 | 0.14191 | -0.013122 | 0.012341 | 0.071617 | 0.0060627 | 0.066584 | -0.0036829 | -0.0012306 | -0.0040437 | -0.0073315 | 0.060079 | 0.063467 | 0.0012689 | -0.0089742 | 0.045776 | -120.9366 | -21.4966 | -121.6049 | 0.10071 | -121.8201 | -121.6782 | -122.1359 | -26.5228 | -121.8796 | 0.027466 | 0.059509 | -121.8521 | -121.9894 | -0.004577 | 0.13733 | -0.041199 | 0.87891 | 0.21057 | 0.073243 | -0.096131 | -0.036621 | -0.17395 | -0.11444 | -0.32043 | -0.064087 | 0.10986 | -0.082398 | 121.9162 | 121.8613 | 100.3189 | -121.8201 | 121.843 | 121.875 | 95.2927 | -122.1313
1042.7188 | 121.9894 | -121.8018 | 0.15106 | -0.013122 | 0.019177 | 0.067986 | 0.0028583 | 0.065302 | 0.0035803 | 0.00026484 | -0.0040437 | -0.0032727 | 0.061575 | 0.064749 | 0.0068231 | -0.0089742 | 0.009155 | -121.0419 | -19.9631 | -121.6324 | 0.14191 | -121.8338 | -121.701 | -122.1817 | -24.0143 | -121.9986 | 0.064087 | 0.10529 | -121.8887 | -122.0169 | -0.032043 | 0.10071 | -0.009155 | 0.75989 | 0.16937 | 0.068665 | -0.14191 | -0.086975 | -0.21515 | -0.086975 | -0.37994 | -0.19684 | 0.018311 | -0.045776 | 121.9437 | 121.8109 | 101.8387 | -121.8521 | 121.8658 | 121.907 | 97.7875 | -122.168
1044.4688 | 122.0078 | -121.8018 | 0.15106 | -0.0054933 | 0.019177 | 0.067986 | 0.0034991 | 0.068293 | 0.0018713 | 0.001333 | -0.0040437 | -0.0034863 | 0.059866 | 0.063681 | 0.0072505 | -0.0081198 | 0 | -121.019 | -21.3181 | -121.6232 | 0.14191 | -121.8521 | -121.7148 | -122.1771 | -24.4125 | -121.9757 | 0.045776 | 0.07782 | -121.907 | -122.0444 | -0.050354 | 0.086975 | -0.009155 | 0.78278 | 0.17853 | 0.091553 | -0.15106 | -0.10528 | -0.24261 | -0.10529 | -0.37537 | -0.17395 | 0.068665 | -0.073242 | 121.9437 | 121.8018 | 100.4837 | -121.8658 | 121.8475 | 121.8796 | 97.3892 | -122.1954
1046.2188 | 122.0169 | -121.7972 | 0.1236 | -0.013122 | 0.016186 | 0.067772 | 0.0056355 | 0.066798 | 0.0014441 | -0.00080316 | -0.0040437 | -0.0056225 | 0.061148 | 0.064963 | 0.0055415 | -0.0087606 | 0.082397 | -120.9091 | -20.6223 | -121.5454 | 0.10529 | -121.8018 | -121.7148 | -122.0718 | -24.9252 | -121.8704 | 0.004578 | 0.050354 | -121.8292 | -121.9757 | -0.004578 | 0.082397 | -0.01831 | 0.88806 | 0.25177 | 0.16937 | -0.041199 | -0.032044 | -0.17853 | -0.11902 | -0.27466 | -0.073242 | 0.10529 | -0.073242 | 121.9025 | 121.8796 | 101.1749 | -121.8384 | 121.8018 | 121.8475 | 96.8719 | -122.0993
1047.9688 | 122.0993 | -121.7789 | 0.12817 | -0.0054933 | 0.019177 | 0.069267 | 0.0054217 | 0.066584 | 0.0035803 | 0.00069204 | -0.0040437 | -0.0041271 | 0.061148 | 0.065604 | 0.0063959 | -0.008547 | 0.041199 | -120.9229 | -21.6751 | -121.6003 | 0.11902 | -121.843 | -121.7194 | -122.1359 | -24.5178 | -121.9391 | 0.041199 | 0.068665 | -121.8613 | -122.0215 | -0.064087 | 0.05951 | -0.009155 | 0.85602 | 0.17853 | 0.11902 | -0.086975 | -0.082397 | -0.24261 | -0.086975 | -0.35706 | -0.16022 | 0.082397 | -0.059509 | 121.8979 | 121.8201 | 100.1038 | -121.8475 | 121.8201 | 121.8475 | 97.261 | -122.1497
1049.6562 | 121.9711 | -121.788 | 0.14648 | -0.013122 | 0.013623 | 0.069054 | 0.0062763 | 0.064448 | -0.0036829 | -0.0016578 | -0.0040437 | -0.0079725 | 0.060079 | 0.065176 | -1.2744e-05 | -0.0059836 | 0.036621 | -120.8817 | -21.0068 | -121.5912 | 0.091553 | -121.8109 | -121.7056 | -122.1313 | -24.4949 | -121.8887 | 0.013733 | 0.041199 | -121.843 | -121.9757 | -0.022888 | 0.082398 | -0.054931 | 0.90637 | 0.19684 | 0.11444 | -0.10986 | -0.054932 | -0.18768 | -0.13275 | -0.34332 | -0.10071 | 0.086975 | -0.10529 | 121.8796 | 121.8246 | 100.7812 | -121.8521 | 121.8018 | 121.8292 | 97.2931 | -122.1222
1051.4062 | 121.9803 | -121.8018 | 0.13275 | -0.0054933 | 0.0164 | 0.068626 | 0.0052081 | 0.06808 | 0.00037606 | -0.0042212 | -0.0040437 | -0.0073315 | 0.061148 | 0.066245 | 0.0023371 | -0.0096152 | 0.10071 | -120.8633 | -22.3206 | -121.5454 | 0.086975 | -121.7926 | -121.6919 | -122.0718 | -23.1857 | -121.8613 | -0.009155 | 0.036621 | -121.8201 | -121.994 | 0.009155 | 0.10986 | -0.045776 | 0.93842 | 0.25635 | 0.14648 | -0.032043 | -0.01831 | -0.19226 | -0.14191 | -0.27008 | -0.059509 | 0.13275 | -0.09613 | 121.8887 | 121.9025 | 99.4812 | -121.8246 | 121.7926 | 121.8384 | 98.616 | -122.1268
1053.1562 | 121.9711 | -121.8292 | 0.14648 | -0.0054933 | 0.012555 | 0.070335 | 0.0015765 | 0.063166 | -0.0036829 | -0.003794 | -0.011673 | -0.0088269 | 0.060293 | 0.065817 | 0.0036189 | -0.0070516 | 0.059509 | -120.8771 | -21.7804 | -121.5912 | 0.086975 | -121.8018 | -121.6782 | -122.1359 | -24.1882 | -121.8796 | 0.013733 | 0.064087 | -121.8338 | -121.994 | 0.027466 | 0.15106 | -0.059509 | 0.95215 | 0.23804 | 0.086975 | -0.086975 | -0.004577 | -0.16479 | -0.13275 | -0.3067 | -0.050354 | 0.11444 | -0.082397 | 121.9162 | 121.8887 | 100.0488 | -121.8246 | 121.843 | 121.8933 | 97.641 | -122.1405
1054.9062 | 122.0535 | -121.7606 | 0.1236 | -0.013122 | 0.015118 | 0.069695 | 0.0081989 | 0.067652 | -0.0017603 | -0.0040076 | -0.011673 | -0.0064771 | 0.063284 | 0.064536 | 0.0010553 | -0.008547 | 0.10529 | -120.8176 | -21.1533 | -121.5454 | 0.091553 | -121.8246 | -121.6827 | -122.081 | -24.1333 | -121.8521 | 0.018311 | 0.059509 | -121.8246 | -121.9849 | -0.064087 | 0.07782 | -0.032043 | 0.94299 | 0.21515 | 0.13733 | -0.01831 | -0.064087 | -0.2243 | -0.10528 | -0.32044 | -0.091553 | 0.13275 | -0.064087 | 121.8521 | 121.8658 | 100.6073 | -121.8063 | 121.7789 | 121.8201 | 97.6273 | -122.1085
1056.6406 | 122.0032 | -121.8201 | 0.13275 | -0.013122 | 0.015332 | 0.06884 | 0.0058491 | 0.06338 | -0.0047509 | -0.0035804 | -0.011673 | -0.0075451 | 0.061788 | 0.06539 | 0.0021235 | -0.0089742 | 0.045776 | -120.9 | -21.4279 | -121.6003 | 0.10071 | -121.8338 | -121.6919 | -122.1451 | -23.204 | -121.9025 | 0.009155 | 0.068665 | -121.843 | -121.994 | -0.013733 | 0.12817 | -0.032043 | 0.92011 | 0.21973 | 0.091553 | -0.086975 | -0.022889 | -0.17395 | -0.1236 | -0.32501 | -0.082398 | 0.091553 | -0.064086 | 121.9208 | 121.8658 | 100.3922 | -121.8246 | 121.8292 | 121.8887 | 98.616 | -122.1268
1058.3438 | 121.9986 | -121.8063 | 0.14648 | -0.0054933 | 0.015118 | 0.066917 | 0.0034991 | 0.067866 | 0.0020849 | -0.00080316 | -0.011673 | -0.0047681 | 0.061575 | 0.066672 | 0.0076777 | -0.01047 | 0.12817 | -120.8221 | -21.5057 | -121.5408 | 0.086975 | -121.8292 | -121.6873 | -122.0535 | -24.0509 | -121.8567 | -0.009155 | 0.032043 | -121.843 | -121.9849 | -0.022889 | 0.11902 | -0.059509 | 0.98419 | 0.2655 | 0.14648 | -0.01831 | -0.036622 | -0.17853 | -0.15564 | -0.24719 | -0.050354 | 0.12817 | -0.11444 | 121.8933 | 121.9345 | 100.3006 | -121.8338 | 121.7972 | 121.8384 | 97.7554 | -122.1313
1060.0781 | 122.0993 | -121.7606 | 0.10986 | -0.020752 | 0.016613 | 0.069481 | 0.0069171 | 0.065302 | -0.0021875 | -0.0042212 | -0.011673 | -0.0086133 | 0.062002 | 0.064536 | 0.00020086 | -0.0083334 | 0.073242 | -120.8359 | -22.0184 | -121.5637 | 0.10986 | -121.8246 | -121.6873 | -122.0673 | -24.6323 | -121.843 | -0.004578 | 0.041199 | -121.8567 | -121.9894 | -0.064087 | 0.073242 | 0 | 0.92468 | 0.19684 | 0.1236 | -0.036621 | -0.09613 | -0.22888 | -0.11444 | -0.3067 | -0.082398 | 0.14648 | -0.068664 | 121.8704 | 121.8338 | 99.7421 | -121.7972 | 121.756 | 121.8018 | 97.1283 | -122.0993
1061.8281 | 122.0673 | -121.7468 | 0.11902 | -0.013122 | 0.01405 | 0.067558 | 0.0067035 | 0.066371 | -0.00069214 | -0.0027258 | -0.0040437 | -0.0069043 | 0.062429 | 0.064749 | 0.0038325 | -0.0098288 | 0.11902 | -120.7855 | -24.2477 | -121.5408 | 0.09613 | -121.8384 | -121.6873 | -122.0261 | -25.6989 | -121.8475 | 0.013733 | 0.068665 | -121.8613 | -121.962 | -0.091553 | 0.059509 | -0.022889 | 0.9613 | 0.20599 | 0.14648 | 0 | -0.11444 | -0.21515 | -0.10529 | -0.27924 | -0.10071 | 0.11444 | -0.050354 | 121.843 | 121.8658 | 97.4991 | -121.8063 | 121.7606 | 121.8155 | 96.048 | -122.081
1063.5156 | 121.9666 | -121.8063 | 0.13733 | -0.0054933 | 0.011487 | 0.068199 | 0.0045673 | 0.064021 | 0.00037606 | -0.002085 | 0.0035858 | -0.0051953 | 0.059866 | 0.065604 | 0.0019099 | -0.0091878 | 0.054932 | -120.8679 | -24.0417 | -121.5958 | 0.09613 | -121.8201 | -121.6919 | -122.081 | -25.6348 | -121.8842 | 0.022888 | 0.059509 | -121.8521 | -121.9894 | -0.013733 | 0.11444 | -0.041199 | 0.93842 | 0.21057 | 0.096131 | -0.082397 | -0.045777 | -0.18311 | -0.11444 | -0.27466 | -0.07782 | 0.10529 | -0.07782 | 121.9025 | 121.8613 | 97.7646 | -121.8292 | 121.8292 | 121.8658 | 96.1716 | -122.1268
1065.25 | 122.1176 | -121.756 | 0.10986 | 0.0097657 | 0.017895 | 0.06884 | 0.0060627 | 0.06872 | 0.0014441 | 5.1244e-05 | -0.011673 | -0.0032727 | 0.062429 | 0.06539 | 0.0061823 | -0.010256 | 0.022888 | -120.9549 | -26.3351 | -121.6324 | 0.14191 | -121.8384 | -121.7331 | -122.0764 | -24.234 | -121.962 | 0.045776 | 0.073242 | -121.8842 | -122.0306 | -0.082398 | 0.022888 | 0.032044 | 0.80109 | 0.1236 | 0.10071 | -0.086975 | -0.12817 | -0.27466 | -0.064087 | -0.32043 | -0.20599 | 0.068665 | -0.036621 | 121.8979 | 121.7789 | 95.4208 | -121.843 | 121.8018 | 121.8292 | 97.522 | -122.1405
1066.9844 | 121.9803 | -121.788 | 0.14191 | -0.013122 | 0.011487 | 0.070335 | 0.0024311 | 0.065516 | -0.00047854 | -0.00016236 | -0.011673 | -0.0049817 | 0.060079 | 0.06539 | 0.0044733 | -0.0083334 | 0.073242 | -120.845 | -27.4292 | -121.5683 | 0.091553 | -121.8063 | -121.6873 | -122.0764 | -23.0988 | -121.8933 | 0.018311 | 0.050354 | -121.8567 | -122.0032 | -0.01831 | 0.10071 | -0.050354 | 0.94299 | 0.21973 | 0.11902 | -0.068665 | -0.068664 | -0.21515 | -0.1236 | -0.28839 | -0.10529 | 0.10986 | -0.091553 | 121.8796 | 121.8613 | 94.3588 | -121.8292 | 121.8063 | 121.8384 | 98.6893 | -122.1451
1068.6719 | 121.9894 | -121.8246 | 0.13733 | -0.013122 | 0.01875 | 0.06884 | 0.0028583 | 0.066584 | 0.0033667 | -0.0014442 | -0.0040437 | -0.0015637 | 0.062002 | 0.06539 | 0.0083185 | -0.011111 | 0.013733 | -120.9595 | -28.3676 | -121.6507 | 0.13733 | -121.8521 | -121.7377 | -122.1268 | -23.6389 | -122.0123 | 0.045776 | 0.10529 | -121.8796 | -122.0169 | -0.027466 | 0.086975 | 0 | 0.86517 | 0.17395 | 0.086975 | -0.1236 | -0.054932 | -0.19226 | -0.091553 | -0.30212 | -0.18768 | 0.004578 | -0.032043 | 121.962 | 121.8384 | 93.457 | -121.875 | 121.8704 | 121.9299 | 98.1857 | -122.1542
1070.4219 | 122.0444 | -121.8063 | 0.1236 | -0.013122 | 0.015973 | 0.070335 | 0.0054217 | 0.066798 | 0.0014441 | 0.00047844 | -0.0040437 | -0.0041271 | 0.063284 | 0.065817 | 0.0055415 | -0.0064108 | 0.004578 | -120.9366 | -28.299 | -121.6507 | 0.15106 | -121.8658 | -121.7468 | -122.1268 | -23.5748 | -121.9757 | 0.045776 | 0.07782 | -121.875 | -122.0352 | -0.05951 | 0.059509 | 0.027466 | 0.86975 | 0.15564 | 0.09613 | -0.11902 | -0.068665 | -0.22888 | -0.07782 | -0.32043 | -0.16937 | 0.059509 | -0.045776 | 121.9574 | 121.8109 | 93.5074 | -121.8704 | 121.8521 | 121.8842 | 98.2315 | -122.1588
1072.1562 | 122.0764 | -121.7972 | 0.12817 | -0.013122 | 0.018963 | 0.067772 | 0.0079853 | 0.067652 | 0.0033667 | -0.0014442 | -0.026932 | -0.0056225 | 0.064352 | 0.066458 | 0.0074641 | -0.0064108 | 0.064087 | -120.8588 | -27.7313 | -121.5775 | 0.14191 | -121.8521 | -121.7148 | -122.0627 | -23.1171 | -121.9299 | 0.022888 | 0.07782 | -121.8842 | -122.0123 | -0.054932 | 0.082397 | 0.013733 | 0.93841 | 0.21973 | 0.13733 | -0.064087 | -0.086975 | -0.21515 | -0.10529 | -0.2655 | -0.13275 | 0.082397 | -0.050354 | 121.9391 | 121.8613 | 94.0659 | -121.843 | 121.8201 | 121.875 | 98.6801 | -122.1405
1073.9219 | 122.0718 | -121.7651 | 0.10986 | -0.020752 | 0.015332 | 0.068626 | 0.0062763 | 0.065943 | -0.0062463 | -0.0014442 | 0.0035858 | -0.0098951 | 0.061575 | 0.063254 | 0.0025507 | -0.005129 | 0.073242 | -120.7764 | -28.2898 | -121.55 | 0.086975 | -121.843 | -121.6919 | -122.0581 | -21.6568 | -121.8521 | -0.004578 | 0.050354 | -121.8567 | -121.9894 | -0.07782 | 0.073242 | -0.022888 | 0.98877 | 0.21515 | 0.14191 | -0.036621 | -0.091552 | -0.2243 | -0.11444 | -0.29297 | -0.086975 | 0.13733 | -0.059509 | 121.8521 | 121.8384 | 93.4753 | -121.8018 | 121.7606 | 121.8155 | 100.1083 | -122.0993
1075.6562 | 122.0993 | -121.7651 | 0.11902 | -0.028381 | 0.016613 | 0.069481 | 0.0060627 | 0.067225 | -0.0053919 | -0.0048622 | -0.011673 | -0.0073315 | 0.062002 | 0.066458 | -0.00022634 | -0.0066244 | 0.091553 | -120.7443 | -28.3859 | -121.5408 | 0.10529 | -121.8109 | -121.701 | -122.0261 | -21.0022 | -121.8246 | -0.004578 | 0.054932 | -121.8567 | -122.0078 | -0.045776 | 0.064087 | -0.013733 | 1.0208 | 0.2243 | 0.16022 | -0.027466 | -0.091552 | -0.24261 | -0.1236 | -0.26093 | -0.059509 | 0.1831 | -0.064087 | 121.8704 | 121.8567 | 93.3792 | -121.8201 | 121.7606 | 121.8201 | 100.7629 | -122.1268
1077.3281 | 122.0764 | -121.7606 | 0.10529 | -0.013122 | 0.016186 | 0.066917 | 0.0094807 | 0.067225 | 0.00080326 | -0.0029394 | -0.0040437 | -0.0036999 | 0.061575 | 0.065604 | 0.0027643 | -0.0070516 | -0.009155 | -120.9045 | -28.9902 | -121.6278 | 0.13275 | -121.8842 | -121.7285 | -122.1634 | -20.7596 | -121.9757 | 0.064087 | 0.082397 | -121.9254 | -122.0444 | -0.1236 | 0.032043 | 0.027465 | 0.85602 | 0.13275 | 0.10071 | -0.11444 | -0.16479 | -0.28381 | -0.041199 | -0.40283 | -0.21515 | 0.068665 | -0.022889 | 121.8933 | 121.7514 | 92.7704 | -121.8338 | 121.8246 | 121.843 | 101.001 | -122.1497
1079.0625 | 121.9849 | -121.8292 | 0.15106 | -0.0054933 | 0.019177 | 0.065636 | 0.0043537 | 0.063807 | 0.0059303 | -0.00037596 | -0.011673 | -0.0028455 | 0.063284 | 0.068594 | 0.0059687 | -0.010042 | 0.032043 | -120.9045 | -29.1779 | -121.6141 | 0.13275 | -121.8521 | -121.7514 | -122.1359 | -21.6843 | -121.9894 | 0.059509 | 0.073242 | -121.8887 | -122.0444 | -0.022888 | 0.07782 | -0.018311 | 0.92468 | 0.21515 | 0.13733 | -0.11902 | -0.059509 | -0.21515 | -0.091553 | -0.3067 | -0.16022 | 0.054932 | -0.07782 | 121.962 | 121.8613 | 92.6514 | -121.9025 | 121.8887 | 121.9025 | 100.145 | -122.1954
1080.7969 | 122.0993 | -121.7468 | 0.1236 | -0.0054933 | 0.020031 | 0.069267 | 0.0052081 | 0.066798 | 0.0016577 | 0.00026484 | -0.0040437 | -0.0043409 | 0.06307 | 0.066885 | 0.0061823 | -0.0079062 | 0.032043 | -120.845 | -29.5074 | -121.6003 | 0.1236 | -121.8567 | -121.7377 | -122.0764 | -20.8923 | -121.9116 | 0.045776 | 0.082397 | -121.8979 | -122.0352 | -0.10986 | 0.009155 | 0 | 0.90179 | 0.14648 | 0.13733 | -0.091553 | -0.15106 | -0.28839 | -0.07782 | -0.32959 | -0.16479 | 0.1236 | -0.041199 | 121.8704 | 121.7789 | 92.2394 | -121.8613 | 121.7926 | 121.8292 | 100.8545 | -122.1588
1082.4688 | 122.113 | -121.7926 | 0.12817 | -0.0054933 | 0.015759 | 0.069054 | 0.0047809 | 0.066371 | -0.00069214 | -0.0016578 | 0.0035858 | -0.0041271 | 0.061361 | 0.067953 | 0.0044733 | -0.0087606 | -0.032043 | -120.8908 | -30.3818 | -121.6141 | 0.16479 | -121.8704 | -121.7422 | -122.1634 | -20.517 | -121.9666 | 0.050354 | 0.07782 | -121.8842 | -122.0261 | -0.077819 | 0.050354 | 0.036621 | 0.90179 | 0.17853 | 0.12817 | -0.16022 | -0.091552 | -0.23346 | -0.07782 | -0.37079 | -0.17395 | 0.059509 | -0.050354 | 121.9574 | 121.7606 | 91.4108 | -121.8704 | 121.843 | 121.8704 | 101.2756 | -122.1542
1084.2188 | 121.994 | -121.8292 | 0.14648 | 0.0021362 | 0.010632 | 0.069054 | 0.0041401 | 0.064021 | -0.0056055 | -0.0044348 | -0.011673 | -0.0092541 | 0.061788 | 0.065817 | 0.00062806 | -0.0038474 | 0.027466 | -120.8313 | -30.0568 | -121.6003 | 0.10529 | -121.8292 | -121.6873 | -122.113 | -20.3522 | -121.8842 | 0.022888 | 0.045776 | -121.8613 | -121.9986 | 0 | 0.14191 | -0.041198 | 0.99792 | 0.22888 | 0.086975 | -0.11902 | -0.032043 | -0.16937 | -0.1236 | -0.28381 | -0.054931 | 0.11444 | -0.10071 | 121.9345 | 121.8567 | 91.7725 | -121.8338 | 121.8521 | 121.875 | 101.4771 | -122.1451
1085.9531 | 121.9757 | -121.7926 | 0.13733 | -0.0054933 | 0.01405 | 0.068626 | 0.00093567 | 0.067225 | -0.0013329 | 0.00026484 | -0.011673 | -0.0049817 | 0.059866 | 0.066031 | 0.0040461 | -0.0079062 | 0.09613 | -120.7718 | -30.5603 | -121.55 | 0.086975 | -121.7972 | -121.6736 | -122.0535 | -20.43 | -121.8521 | 0.004578 | 0.036621 | -121.8521 | -122.0032 | -0.004577 | 0.11902 | -0.050354 | 1.0208 | 0.24262 | 0.1236 | -0.041199 | -0.059509 | -0.21057 | -0.13275 | -0.26093 | -0.059509 | 0.15106 | -0.10071 | 121.8796 | 121.8887 | 91.2323 | -121.8109 | 121.7972 | 121.8292 | 101.3626 | -122.1405
1087.625 | 122.0352 | -121.8063 | 0.13733 | -0.013122 | 0.017468 | 0.067772 | 0.0047809 | 0.06573 | 0.0016577 | -0.00037596 | -0.0040437 | -0.0017773 | 0.062216 | 0.065604 | 0.0055415 | -0.007479 | 0.022888 | -120.9045 | -31.3568 | -121.6415 | 0.13275 | -121.8567 | -121.7239 | -122.113 | -20.0088 | -121.9437 | 0.041199 | 0.064087 | -121.875 | -121.994 | -0.050354 | 0.082397 | -0.004578 | 0.90179 | 0.16479 | 0.082397 | -0.11444 | -0.068665 | -0.18768 | -0.09613 | -0.3067 | -0.13733 | 0.050354 | -0.073242 | 121.9391 | 121.8292 | 90.4495 | -121.8613 | 121.8475 | 121.8704 | 101.7975 | -122.1313
1089.375 | 122.0993 | -121.7926 | 0.10071 | -0.0054933 | 0.019177 | 0.069481 | 0.0090533 | 0.069361 | 0.00016226 | -0.0012306 | -0.011673 | -0.0034863 | 0.06307 | 0.066031 | 0.0019099 | -0.0098288 | -0.009155 | -120.9229 | -30.2948 | -121.6461 | 0.14191 | -121.8796 | -121.7422 | -122.1634 | -20.874 | -121.9711 | 0.068665 | 0.10071 | -121.8796 | -122.0352 | -0.086975 | 0.050354 | 0.041199 | 0.86975 | 0.14648 | 0.096131 | -0.10986 | -0.086975 | -0.24261 | -0.032043 | -0.37079 | -0.17853 | 0.064087 | 0 | 121.9345 | 121.7834 | 91.4978 | -121.843 | 121.8613 | 121.8933 | 100.9186 | -122.1359
1091.1094 | 122.0444 | -121.8155 | 0.13275 | -0.020752 | 0.017468 | 0.068626 | 0.0060627 | 0.065516 | -0.0021875 | -0.003794 | -0.011673 | -0.0049817 | 0.063284 | 0.066458 | 0.0023371 | -0.0087606 | 0.036621 | -120.8313 | -30.7068 | -121.5866 | 0.1236 | -121.8338 | -121.7194 | -122.1542 | -20.3018 | -121.9528 | 0.041199 | 0.082397 | -121.9025 | -122.0398 | -0.01831 | 0.096131 | -0.009155 | 0.98419 | 0.22888 | 0.13275 | -0.09613 | -0.086975 | -0.2243 | -0.091552 | -0.33875 | -0.13733 | 0.086975 | -0.050354 | 121.9391 | 121.8521 | 91.1087 | -121.8521 | 121.8567 | 121.8979 | 101.5137 | -122.1725
1092.8594 | 122.0718 | -121.8109 | 0.11902 | -0.013122 | 0.01875 | 0.067772 | 0.0079853 | 0.065943 | -0.0019739 | -0.00058956 | -0.0040437 | -0.0051953 | 0.062216 | 0.066458 | 0.0023371 | -0.008547 | 0.022888 | -120.8405 | -30.8533 | -121.6187 | 0.12817 | -121.8567 | -121.7285 | -122.1725 | -19.368 | -121.9574 | 0.041199 | 0.073242 | -121.9025 | -122.0581 | -0.045776 | 0.082397 | 0.009155 | 0.97046 | 0.19226 | 0.10986 | -0.096131 | -0.091553 | -0.24719 | -0.07782 | -0.36163 | -0.14648 | 0.10071 | -0.045777 | 121.9391 | 121.8338 | 90.9576 | -121.8475 | 121.8521 | 121.8842 | 102.4429 | -122.1771
1094.5469 | 121.9894 | -121.8155 | 0.11444 | 0.0021362 | 0.017041 | 0.067986 | 0.0015765 | 0.064448 | -0.00026494 | -0.0010168 | 0.0035858 | -0.0034863 | 0.06307 | 0.068167 | 0.0072505 | -0.0091878 | 0.045776 | -120.8405 | -31.0684 | -121.5912 | 0.11444 | -121.8292 | -121.6827 | -122.0535 | -18.2007 | -121.8796 | 0.013733 | 0.064087 | -121.875 | -121.994 | -0.013733 | 0.13275 | 0 | 0.97504 | 0.2243 | 0.091552 | -0.068665 | -0.059509 | -0.17853 | -0.10071 | -0.23804 | -0.064087 | 0.11444 | -0.050354 | 121.9299 | 121.8613 | 90.7471 | -121.7972 | 121.8292 | 121.8796 | 103.6148 | -122.1085
1096.2812 | 122.0123 | -121.8292 | 0.1236 | -0.013122 | 0.019391 | 0.067558 | 0.0045673 | 0.067011 | 0.0033667 | 0.00090584 | -0.011673 | -0.0034863 | 0.064352 | 0.066031 | 0.0070367 | -0.010042 | 0.064087 | -120.813 | -31.4026 | -121.6003 | 0.13275 | -121.8292 | -121.7194 | -122.1039 | -18.8782 | -121.962 | 0.032043 | 0.068665 | -121.8933 | -122.049 | 0 | 0.10986 | 0.009155 | 1.0162 | 0.22888 | 0.11902 | -0.059509 | -0.064087 | -0.21973 | -0.091553 | -0.27466 | -0.13275 | 0.086975 | -0.054931 | 121.962 | 121.8933 | 90.4266 | -121.843 | 121.8613 | 121.8979 | 102.951 | -122.1725
1098.0156 | 122.081 | -121.8201 | 0.11902 | -0.0054933 | 0.020459 | 0.068199 | 0.0052081 | 0.065516 | 0.0014441 | -0.00080316 | -0.011673 | -0.0024183 | 0.062002 | 0.064963 | 0.0055415 | -0.0070516 | 0.027466 | -120.8176 | -31.7322 | -121.5958 | 0.12817 | -121.875 | -121.7331 | -122.0993 | -17.9626 | -121.9345 | 0.032043 | 0.068665 | -121.8796 | -122.049 | -0.054932 | 0.086975 | 0.009155 | 1.0025 | 0.2243 | 0.13733 | -0.091553 | -0.05951 | -0.22888 | -0.086976 | -0.27924 | -0.11444 | 0.11444 | -0.050354 | 121.9482 | 121.8475 | 90.0879 | -121.8521 | 121.8521 | 121.8887 | 103.8574 | -122.168
1099.75 | 121.9711 | -121.8384 | 0.15106 | -0.013122 | 0.019391 | 0.068199 | 0.0041401 | 0.068507 | 0.00058966 | 0.00090584 | -0.0040437 | -0.0036999 | 0.061361 | 0.064536 | 0.0057551 | -0.007479 | -0.032043 | -120.8908 | -30.5649 | -121.637 | 0.14648 | -121.8658 | -121.7194 | -122.1542 | -18.4113 | -122.0078 | 0.050354 | 0.091553 | -121.9025 | -122.0352 | -0.027466 | 0.11902 | -0.004578 | 0.94757 | 0.20142 | 0.082397 | -0.18311 | -0.064087 | -0.19684 | -0.10071 | -0.31586 | -0.16937 | 0.027466 | -0.059509 | 121.9849 | 121.8063 | 91.2735 | -121.8704 | 121.8887 | 121.9299 | 103.4271 | -122.1863
1101.5 | 121.7239 | -121.5134 | 0.13733 | -0.013122 | 0.014905 | 0.070335 | 0.0060627 | 0.063593 | -0.0053919 | -0.0031532 | 0.0035858 | -0.0075451 | 0.060293 | 0.063895 | 0.0012689 | -0.006838 | -0.018311 | -120.5429 | -30.7114 | -121.3165 | 0.11444 | -121.5591 | -121.4218 | -121.8704 | -18.5028 | -121.5912 | 0.009155 | 0.054932 | -121.5637 | -121.7102 | -0.045776 | 0.091553 | -0.022888 | 0.97046 | 0.19684 | 0.10529 | -0.15564 | -0.050354 | -0.19684 | -0.12817 | -0.35706 | -0.07782 | 0.11902 | -0.082397 | 121.6278 | 121.4951 | 90.802 | -121.5591 | 121.5225 | 121.5683 | 103.0106 | -121.8475
1103.1719 | 121.9208 | -121.5912 | 0.09613 | -0.020752 | 0.013623 | 0.072472 | 0.0079853 | 0.065302 | -0.0053919 | -0.0067848 | 0.011215 | -0.0075451 | 0.06072 | 0.065176 | 0.0019099 | -0.0081198 | 0.032043 | -120.6253 | -31.6544 | -121.4081 | 0.10071 | -121.6644 | -121.55 | -121.9391 | -19.7342 | -121.6736 | 0.022888 | 0.045776 | -121.669 | -121.8384 | -0.073242 | 0.041199 | 0.004578 | 0.96588 | 0.18311 | 0.14191 | -0.064087 | -0.077819 | -0.24719 | -0.073242 | -0.3479 | -0.082397 | 0.16479 | -0.050354 | 121.6919 | 121.6232 | 89.9368 | -121.6461 | 121.6141 | 121.637 | 101.857 | -121.9345
1104.9375 | 121.8842 | -121.6827 | 0.13733 | -0.013122 | 0.017895 | 0.069481 | 0.0013629 | 0.069361 | 0.0020849 | 5.1244e-05 | -0.0040437 | -0.0032727 | 0.06072 | 0.065604 | 0.0076777 | -0.0091878 | 0.059509 | -120.6573 | -32.4646 | -121.4539 | 0.10529 | -121.6873 | -121.5591 | -121.9299 | -20.4941 | -121.7468 | 0.013733 | 0.059509 | -121.7148 | -121.8521 | -0.004578 | 0.1236 | -0.032043 | 1.0254 | 0.22888 | 0.10529 | -0.07782 | -0.032044 | -0.16937 | -0.1236 | -0.24719 | -0.064087 | 0.10529 | -0.07782 | 121.788 | 121.7422 | 89.2181 | -121.6965 | 121.6965 | 121.7422 | 101.1887 | -121.9894
1106.6719 | 121.8475 | -121.7102 | 0.13275 | -0.013122 | 0.016613 | 0.067986 | 0.0030719 | 0.06808 | -0.0026147 | -0.0033668 | 0.0035858 | -0.0062635 | 0.059652 | 0.066031 | 0.0044733 | -0.0087606 | 0.086975 | -120.5933 | -33.3618 | -121.431 | 0.09613 | -121.701 | -121.5546 | -121.9299 | -20.5994 | -121.7239 | 0 | 0.045776 | -121.7331 | -121.875 | 0.009155 | 0.15564 | -0.036621 | 1.1169 | 0.27924 | 0.1236 | -0.045776 | -0.022888 | -0.16479 | -0.13275 | -0.21973 | -0.013733 | 0.15106 | -0.086975 | 121.8063 | 121.7972 | 88.3484 | -121.6873 | 121.7102 | 121.756 | 101.1108 | -122.0078
1108.3438 | 121.8704 | -121.6736 | 0.13733 | -0.013122 | 0.015118 | 0.069908 | 0.0026447 | 0.069148 | 0.00080326 | -0.0031532 | -0.0040437 | -0.0047681 | 0.059652 | 0.064749 | 0.0059687 | -0.0072652 | 0.10986 | -120.6299 | -33.49 | -121.4401 | 0.09613 | -121.7102 | -121.5546 | -121.9299 | -21.7575 | -121.7422 | -0.004578 | 0.059509 | -121.7285 | -121.8658 | -0.036621 | 0.11902 | -0.041199 | 1.0437 | 0.23346 | 0.11444 | -0.027466 | -0.054932 | -0.19226 | -0.14191 | -0.25635 | -0.068665 | 0.1236 | -0.07782 | 121.7697 | 121.7834 | 88.1836 | -121.6919 | 121.669 | 121.7331 | 99.9161 | -122.0032
1110.0938 | 121.9437 | -121.6736 | 0.13275 | -0.013122 | 0.015332 | 0.070976 | 0.0094807 | 0.066371 | 0.00037606 | -0.0042212 | 0.0035858 | -0.0058361 | 0.062643 | 0.064963 | 0.0019099 | -0.0079062 | 0.032043 | -120.7214 | -33.4579 | -121.5179 | 0.11444 | -121.701 | -121.6049 | -122.0673 | -21.2997 | -121.8475 | 0.050354 | 0.082397 | -121.788 | -121.9116 | -0.027466 | 0.068665 | -0.01831 | 0.95215 | 0.15564 | 0.086975 | -0.10071 | -0.11444 | -0.23804 | -0.082397 | -0.39368 | -0.17395 | 0.064087 | -0.050354 | 121.788 | 121.7056 | 88.2156 | -121.7377 | 121.7239 | 121.756 | 100.3738 | -122.0444
1111.8281 | 122.0169 | -121.6507 | 0.09613 | -0.013122 | 0.0211 | 0.067558 | 0.0067035 | 0.066157 | 0.0033667 | -0.002085 | -0.0040437 | -0.0056225 | 0.064565 | 0.067526 | 0.0044733 | -0.01047 | 0.032043 | -120.7306 | -33.6502 | -121.4859 | 0.13733 | -121.7606 | -121.6095 | -122.0032 | -21.7438 | -121.8292 | 0.054932 | 0.086975 | -121.7697 | -121.9299 | -0.10986 | 0.041199 | 0.041199 | 0.9201 | 0.16479 | 0.1236 | -0.064087 | -0.11902 | -0.27924 | -0.041198 | -0.35248 | -0.17853 | 0.10071 | -0.009155 | 121.788 | 121.6827 | 88.0005 | -121.7056 | 121.7056 | 121.7377 | 99.9069 | -122.0261
1113.5156 | 121.875 | -121.7102 | 0.13733 | -0.013122 | 0.013196 | 0.069695 | 0.0028583 | 0.066157 | -0.0030419 | -0.0046484 | -0.011673 | -0.0066907 | 0.063925 | 0.063254 | 0.0034051 | -0.0072652 | 0.054932 | -120.6757 | -33.5358 | -121.4996 | 0.086975 | -121.7148 | -121.6049 | -121.994 | -21.8811 | -121.788 | 0.018311 | 0.045776 | -121.7697 | -121.9254 | -0.004578 | 0.10529 | -0.050354 | 1.0345 | 0.21057 | 0.10528 | -0.082397 | -0.059509 | -0.21515 | -0.11902 | -0.28381 | -0.07782 | 0.13733 | -0.091553 | 121.7972 | 121.7651 | 88.1744 | -121.7422 | 121.7285 | 121.756 | 99.8291 | -122.0627
1115.2656 | 122.0261 | -121.6553 | 0.10986 | -0.020752 | 0.017895 | 0.068199 | 0.0062763 | 0.065302 | 0.0014441 | -0.00080316 | -0.0040437 | -0.0026319 | 0.066274 | 0.067313 | 0.0042597 | -0.0094016 | 0.004578 | -120.7626 | -33.3389 | -121.5088 | 0.15106 | -121.7606 | -121.6232 | -122.0306 | -22.8241 | -121.8613 | 0.068665 | 0.073242 | -121.8018 | -121.9345 | -0.10529 | 0.032043 | 0.041199 | 0.89264 | 0.14648 | 0.11444 | -0.10529 | -0.14649 | -0.27924 | -0.041198 | -0.37537 | -0.20599 | 0.073242 | -0.036621 | 121.8063 | 121.6599 | 88.3163 | -121.7331 | 121.7239 | 121.7285 | 98.8312 | -122.0444
1117 | 121.9482 | -121.6827 | 0.11902 | -0.0054933 | 0.011914 | 0.068626 | 0.0075581 | 0.067011 | -0.0024011 | -0.0044348 | 0.0035858 | -0.0077587 | 0.061788 | 0.064322 | 0.0034051 | -0.00577 | 0.004578 | -120.6985 | -33.2932 | -121.4859 | 0.10986 | -121.7239 | -121.6324 | -122.0306 | -22.8287 | -121.7972 | 0 | 0.059509 | -121.7697 | -121.9345 | -0.041199 | 0.050354 | -0.009156 | 0.98419 | 0.19684 | 0.14648 | -0.11444 | -0.086975 | -0.25177 | -0.11902 | -0.3479 | -0.11444 | 0.13733 | -0.05951 | 121.7926 | 121.6873 | 88.3896 | -121.7514 | 121.6827 | 121.7422 | 98.8541 | -122.0535
1118.6875 | 122.0215 | -121.6553 | 0.11444 | -0.013122 | 0.015973 | 0.069695 | 0.0060627 | 0.065943 | 0.0022987 | -0.0025122 | -0.0040437 | -0.0039135 | 0.062002 | 0.066245 | 0.0027643 | -0.0070516 | 0 | -120.7581 | -32.0251 | -121.5317 | 0.13275 | -121.7789 | -121.637 | -122.0673 | -23.0164 | -121.8887 | 0.054932 | 0.10986 | -121.8201 | -121.9391 | -0.1236 | 0.01831 | 0.01831 | 0.89722 | 0.1236 | 0.10529 | -0.11444 | -0.1648 | -0.28381 | -0.059509 | -0.41199 | -0.23346 | 0.050354 | -0.004578 | 121.788 | 121.6553 | 89.6301 | -121.7514 | 121.7102 | 121.7651 | 98.6389 | -122.0535
1120.4531 | 121.9208 | -121.6919 | 0.12817 | -0.020752 | 0.013623 | 0.070549 | 0.0073443 | 0.069148 | -0.0047509 | -0.0029394 | -0.011673 | -0.0062635 | 0.064779 | 0.065817 | 0.0034051 | -0.006838 | 0.009155 | -120.7169 | -31.5903 | -121.4905 | 0.10529 | -121.7239 | -121.6049 | -122.0261 | -23.0667 | -121.8063 | 0.022888 | 0.068665 | -121.7834 | -121.9299 | -0.032043 | 0.086976 | -0.022888 | 0.97504 | 0.20142 | 0.11444 | -0.11902 | -0.091552 | -0.23804 | -0.10529 | -0.33417 | -0.11444 | 0.1236 | -0.059509 | 121.7972 | 121.7011 | 90.1016 | -121.7331 | 121.7148 | 121.7606 | 98.6252 | -122.0581
1122.125 | 121.9528 | -121.7056 | 0.11902 | -0.020752 | 0.0164 | 0.067345 | 0.00093567 | 0.066798 | 0.0033667 | -0.0014442 | -0.019302 | -0.0022045 | 0.06072 | 0.063895 | 0.0072505 | -0.0083334 | 0.032043 | -120.7809 | -31.2973 | -121.5637 | 0.13275 | -121.7422 | -121.6278 | -122.0032 | -24.2477 | -121.8475 | 0.027466 | 0.054932 | -121.7697 | -121.9299 | -0.036622 | 0.077819 | 0.013732 | 0.92468 | 0.14191 | 0.064087 | -0.086976 | -0.064087 | -0.2243 | -0.091553 | -0.29755 | -0.14191 | 0.082398 | -0.064087 | 121.8384 | 121.7377 | 90.4083 | -121.7468 | 121.7331 | 121.7606 | 97.4579 | -122.049
1123.875 | 121.9757 | -121.7056 | 0.10986 | -0.013122 | 0.017041 | 0.069695 | 0.0075581 | 0.065516 | -0.0011193 | -0.0012306 | -0.011673 | -0.0041271 | 0.063284 | 0.066031 | 0.0034051 | -0.006838 | 0.054932 | -120.7077 | -30.7617 | -121.5042 | 0.10529 | -121.756 | -121.6049 | -122.049 | -23.5748 | -121.8384 | 0.045776 | 0.086975 | -121.8018 | -121.9437 | -0.050354 | 0.10071 | -0.004577 | 0.99792 | 0.20142 | 0.10071 | -0.054931 | -0.096131 | -0.23804 | -0.064087 | -0.34332 | -0.13275 | 0.10529 | -0.022888 | 121.8109 | 121.7606 | 90.9439 | -121.7148 | 121.7514 | 121.7926 | 98.1308 | -122.0535
1125.625 | 121.9666 | -121.6965 | 0.11902 | -0.013122 | 0.010418 | 0.070122 | 0.0032855 | 0.068293 | -0.0036829 | -0.0022986 | 0.0035858 | -0.0056225 | 0.06072 | 0.064749 | 0.0031915 | -0.0079062 | 0.009155 | -120.6894 | -30.4825 | -121.5134 | 0.10529 | -121.7514 | -121.6278 | -122.0261 | -24.3851 | -121.7926 | 0.018311 | 0.045776 | -121.7834 | -121.9208 | -0.054932 | 0.068664 | -0.013733 | 1.0071 | 0.1831 | 0.11444 | -0.10986 | -0.086975 | -0.2243 | -0.10071 | -0.32959 | -0.096131 | 0.12817 | -0.073243 | 121.8018 | 121.7056 | 91.214 | -121.7468 | 121.7148 | 121.7422 | 97.3114 | -122.0398
1127.2969 | 121.8933 | -121.7377 | 0.13275 | -0.0054933 | 0.013623 | 0.070549 | 0.0032855 | 0.067011 | -0.0038965 | -0.0025122 | -0.0040437 | -0.0047681 | 0.060507 | 0.064963 | 0.0046869 | -0.0061972 | 0.054932 | -120.6894 | -30.6747 | -121.5271 | 0.11444 | -121.7514 | -121.6003 | -122.0215 | -24.2935 | -121.8109 | -0.013733 | 0.059509 | -121.788 | -121.9254 | -0.013733 | 0.13733 | -0.01831 | 1.0483 | 0.21057 | 0.073242 | -0.077819 | -0.050354 | -0.18768 | -0.14648 | -0.28381 | -0.073242 | 0.11444 | -0.073242 | 121.8521 | 121.7926 | 91.0629 | -121.7331 | 121.7239 | 121.7972 | 97.4442 | -122.0581
1129.0469 | 121.9162 | -121.7331 | 0.14191 | -0.0054933 | 0.017254 | 0.067131 | 0.0028583 | 0.06573 | 0.0014441 | -0.00080316 | 0.011215 | -0.0043409 | 0.062216 | 0.065176 | 0.0061823 | -0.0096152 | 0.1236 | -120.6757 | -30.5969 | -121.4584 | 0.091553 | -121.7468 | -121.5958 | -121.9528 | -23.5748 | -121.7743 | -0.009155 | 0.041199 | -121.788 | -121.9025 | -0.013733 | 0.13733 | -0.050354 | 1.0574 | 0.27466 | 0.13733 | -0.018311 | -0.054932 | -0.16937 | -0.15106 | -0.21973 | -0.041199 | 0.12817 | -0.10071 | 121.8246 | 121.8567 | 91.1362 | -121.7377 | 121.7239 | 121.7743 | 98.1583 | -122.0444
1130.7969 | 122.0169 | -121.6919 | 0.11902 | -0.020752 | 0.017468 | 0.067131 | 0.0047809 | 0.06573 | 0.0050757 | -0.002085 | -0.011673 | -0.00070932 | 0.064138 | 0.066885 | 0.0057551 | -0.010897 | 0.068665 | -120.7169 | -31.192 | -121.5317 | 0.13733 | -121.7514 | -121.6461 | -122.0032 | -24.1928 | -121.8521 | 0.041199 | 0.086975 | -121.8201 | -121.9254 | -0.059509 | 0.045777 | 0.01831 | 0.97504 | 0.16022 | 0.11444 | -0.050354 | -0.12817 | -0.23346 | -0.07782 | -0.31128 | -0.16022 | 0.073242 | -0.032044 | 121.8292 | 121.7606 | 90.4999 | -121.7651 | 121.7331 | 121.7789 | 97.4991 | -122.0444
1132.5312 | 121.9574 | -121.7239 | 0.1236 | -0.013122 | 0.0164 | 0.066704 | 0.0011493 | 0.066584 | 0.0035803 | -0.00016236 | -0.019302 | -0.0030591 | 0.060507 | 0.066885 | 0.0057551 | -0.0087606 | 0.027466 | -120.7397 | -31.8787 | -121.5408 | 0.10071 | -121.7514 | -121.637 | -122.0032 | -24.4858 | -121.8155 | 0.013733 | 0.050354 | -121.7972 | -121.9299 | -0.027466 | 0.086975 | -0.022888 | 0.98419 | 0.1831 | 0.09613 | -0.09613 | -0.073242 | -0.20599 | -0.10986 | -0.27924 | -0.091553 | 0.11444 | -0.073242 | 121.8246 | 121.7514 | 89.8453 | -121.7606 | 121.7377 | 121.7743 | 97.2382 | -122.0535
1134.2031 | 122.0352 | -121.6919 | 0.10529 | -0.0054933 | 0.010632 | 0.069267 | 0.0062763 | 0.066371 | -0.0053919 | -0.0042212 | 0.0035858 | -0.0079725 | 0.061575 | 0.063467 | 0.0019099 | -0.0064108 | 0.054932 | -120.6757 | -30.423 | -121.5042 | 0.10529 | -121.7331 | -121.6141 | -121.9894 | -24.5316 | -121.756 | 0.013733 | 0.050354 | -121.7972 | -121.9162 | -0.041198 | 0.07782 | 0 | 1.0162 | 0.18768 | 0.10986 | -0.050354 | -0.10528 | -0.2243 | -0.091553 | -0.29755 | -0.064086 | 0.16022 | -0.054932 | 121.7972 | 121.7468 | 91.2689 | -121.7194 | 121.7056 | 121.7422 | 97.1603 | -122.0215
1135.9531 | 121.9116 | -121.7377 | 0.14191 | -0.013122 | 0.017468 | 0.067558 | 0.0049945 | 0.067652 | 0.0048621 | 5.1244e-05 | -0.0040437 | -0.00028192 | 0.062002 | 0.066245 | 0.0091731 | -0.0081198 | 0.036621 | -120.7672 | -30.4001 | -121.55 | 0.15564 | -121.7606 | -121.6415 | -122.0535 | -24.2386 | -121.9116 | 0.054932 | 0.064087 | -121.8155 | -121.9803 | -0.022888 | 0.09613 | 0.013733 | 0.97046 | 0.18768 | 0.091553 | -0.10529 | -0.07782 | -0.24262 | -0.086975 | -0.31586 | -0.17395 | 0.068665 | -0.07782 | 121.8933 | 121.7743 | 91.3376 | -121.7834 | 121.7926 | 121.8018 | 97.4991 | -122.1222
1137.7031 | 122.0123 | -121.7194 | 0.11902 | -0.020752 | 0.014264 | 0.070976 | 0.0071307 | 0.064021 | -0.0060327 | -0.0014442 | -0.011673 | -0.0060497 | 0.061148 | 0.062827 | 0.0010553 | -0.0047018 | 0.086975 | -120.6116 | -31.4301 | -121.4493 | 0.086975 | -121.7422 | -121.6415 | -121.9849 | -24.527 | -121.7697 | 0 | 0.036621 | -121.7743 | -121.9437 | -0.022889 | 0.077819 | -0.032044 | 1.1078 | 0.27008 | 0.19226 | -0.032044 | -0.054932 | -0.22431 | -0.11902 | -0.2655 | -0.050354 | 0.17395 | -0.082398 | 121.8063 | 121.8063 | 90.2893 | -121.7606 | 121.7194 | 121.756 | 97.1924 | -122.0627
1139.3906 | 122.0032 | -121.7056 | 0.1236 | -0.0054933 | 0.018322 | 0.067558 | 0.0062763 | 0.066157 | 0.0057165 | 0.00090584 | -0.011673 | -0.0015637 | 0.062856 | 0.06774 | 0.0051141 | -0.010042 | 0.059509 | -120.7397 | -31.1417 | -121.5088 | 0.11444 | -121.7972 | -121.6095 | -121.9986 | -24.8932 | -121.8658 | 0.050354 | 0.082397 | -121.8018 | -121.9254 | -0.091553 | 0.09613 | -0.009155 | 0.96588 | 0.19684 | 0.10071 | -0.064087 | -0.096131 | -0.21973 | -0.073242 | -0.29297 | -0.16022 | 0.059509 | -0.041199 | 121.8201 | 121.7651 | 90.564 | -121.7331 | 121.756 | 121.788 | 96.8124 | -122.049
1141.0625 | 121.9437 | -121.7285 | 0.13275 | -0.0054933 | 0.018109 | 0.069054 | 0.0045673 | 0.065302 | 0.0020849 | 0.0015466 | -0.011673 | -0.0039135 | 0.062002 | 0.067099 | 0.0074641 | -0.0070516 | 0 | -120.8221 | -30.7297 | -121.5683 | 0.14191 | -121.8018 | -121.6599 | -122.0673 | -25.3693 | -121.9116 | 0.045776 | 0.10529 | -121.8521 | -121.9528 | -0.073242 | 0.068665 | 0.009156 | 0.90637 | 0.16022 | 0.091553 | -0.13275 | -0.1236 | -0.2243 | -0.086975 | -0.33875 | -0.1831 | 0.041199 | -0.027465 | 121.8704 | 121.7285 | 90.9988 | -121.7926 | 121.7743 | 121.8338 | 96.3593 | -122.0856
1142.8125 | 122.0032 | -121.7285 | 0.1236 | -0.0054933 | 0.014691 | 0.069908 | 0.0052081 | 0.065302 | -0.0071007 | 0.00090584 | 0.0035858 | -0.0092541 | 0.062429 | 0.064963 | 0.0012689 | -0.0053426 | -0.004578 | -120.7214 | -29.8737 | -121.5317 | 0.11444 | -121.7697 | -121.637 | -122.0078 | -25.3555 | -121.7972 | 0.013733 | 0.050354 | -121.7972 | -121.9574 | -0.041198 | 0.091553 | -0.009155 | 1.0071 | 0.19684 | 0.10529 | -0.12817 | -0.068664 | -0.22888 | -0.10986 | -0.27923 | -0.068664 | 0.16022 | -0.073242 | 121.843 | 121.7239 | 91.8549 | -121.7606 | 121.7422 | 121.7789 | 96.373 | -122.081
1144.5625 | 121.9574 | -121.7514 | 0.1236 | -0.0054933 | 0.01405 | 0.068626 | 0.0030719 | 0.065302 | 0.0014441 | -0.0033668 | -0.011673 | -0.0024183 | 0.06072 | 0.06539 | 0.0070367 | -0.0076926 | 0.059509 | -120.7443 | -30.7709 | -121.5225 | 0.11902 | -121.7514 | -121.6553 | -121.9803 | -25.5753 | -121.8109 | 0.013733 | 0.045776 | -121.7926 | -121.9254 | 0 | 0.096131 | -0.004577 | 1.0071 | 0.22888 | 0.13275 | -0.064087 | -0.041199 | -0.17395 | -0.10986 | -0.22888 | -0.059509 | 0.11444 | -0.07782 | 121.8704 | 121.8109 | 90.9805 | -121.7789 | 121.7651 | 121.7972 | 96.1761 | -122.049
1146.25 | 121.9894 | -121.7194 | 0.10529 | -0.013122 | 0.012768 | 0.069054 | 0.0037127 | 0.068293 | -0.0024011 | -0.00080316 | -0.0040437 | -0.0045545 | 0.062002 | 0.064749 | 0.0029779 | -0.0079062 | 0.041199 | -120.7123 | -30.8075 | -121.5271 | 0.10986 | -121.7743 | -121.6415 | -122.0535 | -25.8316 | -121.875 | 0.050354 | 0.082397 | -121.8704 | -121.9482 | -0.054932 | 0.077819 | 0.004577 | 1.0071 | 0.19226 | 0.11444 | -0.064087 | -0.15106 | -0.22888 | -0.054932 | -0.33417 | -0.15564 | 0.073242 | -0.022889 | 121.8292 | 121.7606 | 90.9119 | -121.7468 | 121.7697 | 121.8018 | 95.8878 | -122.0535
1147.9844 | 121.907 | -121.7514 | 0.15564 | -0.0054933 | 0.012768 | 0.070976 | 0.0015765 | 0.064448 | -0.0015465 | -0.0027258 | -0.0040437 | -0.0056225 | 0.059225 | 0.064536 | 0.0038325 | -0.010256 | 0.091553 | -120.6482 | -30.3085 | -121.4859 | 0.091553 | -121.7514 | -121.6049 | -121.962 | -24.6094 | -121.8063 | 0.004578 | 0.059509 | -121.7834 | -121.9757 | 0 | 0.14648 | -0.064087 | 1.1032 | 0.2655 | 0.11902 | -0.064087 | -0.032043 | -0.2243 | -0.15106 | -0.21057 | -0.054931 | 0.16937 | -0.096131 | 121.843 | 121.843 | 91.4429 | -121.7606 | 121.756 | 121.8109 | 97.142 | -122.1313
1149.7344 | 122.049 | -121.7056 | 0.10986 | -0.013122 | 0.016827 | 0.068199 | 0.0052081 | 0.066584 | 0.0029395 | -0.0014442 | -0.011673 | -0.0017773 | 0.062002 | 0.065604 | 0.0049005 | -0.0087606 | 0.045776 | -120.7581 | -30.9677 | -121.5317 | 0.14648 | -121.788 | -121.6599 | -121.9986 | -26.4816 | -121.8658 | 0.041199 | 0.082397 | -121.8109 | -121.9574 | -0.082398 | 0.045776 | 0.036621 | 0.94757 | 0.17395 | 0.12817 | -0.064087 | -0.10529 | -0.25177 | -0.068664 | -0.29297 | -0.16022 | 0.091552 | -0.027466 | 121.8521 | 121.7514 | 90.7379 | -121.7697 | 121.7468 | 121.788 | 95.224 | -122.0673
1151.4219 | 122.0673 | -121.6965 | 0.10529 | -0.013122 | 0.017468 | 0.065849 | 0.0041401 | 0.064662 | 0.00080326 | -0.002085 | -0.0040437 | -0.0051953 | 0.062856 | 0.065176 | 0.0057551 | -0.0089742 | 0 | -120.7718 | -30.2811 | -121.5454 | 0.15106 | -121.7972 | -121.6599 | -122.0306 | -26.3351 | -121.8842 | 0.045776 | 0.09613 | -121.843 | -121.962 | -0.10071 | 0.036621 | 0.045776 | 0.92468 | 0.15106 | 0.11444 | -0.10529 | -0.14648 | -0.2655 | -0.05951 | -0.33417 | -0.18768 | 0.07782 | -0.009156 | 121.8475 | 121.6965 | 91.4154 | -121.7651 | 121.7422 | 121.7926 | 95.3613 | -122.0673
1153.0938 | 121.9208 | -121.7651 | 0.15106 | -0.013122 | 0.020245 | 0.06649 | 0.0045673 | 0.065516 | 0.0035803 | -0.00080316 | -0.0040437 | -0.0019909 | 0.063497 | 0.067313 | 0.0059687 | -0.0076926 | 0.022888 | -120.7352 | -30.3726 | -121.5454 | 0.11902 | -121.7834 | -121.6461 | -122.0398 | -26.9669 | -121.9299 | 0.032043 | 0.068665 | -121.8338 | -121.9757 | -0.01831 | 0.11902 | -0.032043 | 1.03 | 0.21973 | 0.10071 | -0.12817 | -0.068664 | -0.21057 | -0.11902 | -0.27466 | -0.16479 | 0.045776 | -0.082397 | 121.8842 | 121.788 | 91.3925 | -121.7972 | 121.7972 | 121.8338 | 94.7983 | -122.1268
1154.8438 | 122.0261 | -121.7102 | 0.10986 | -0.0054933 | 0.019391 | 0.069267 | 0.0058491 | 0.068507 | 0.0010169 | -0.0010168 | -0.0040437 | -0.0030591 | 0.064779 | 0.066245 | 0.0031915 | -0.007479 | 0.032043 | -120.7077 | -30.2353 | -121.5179 | 0.1236 | -121.7789 | -121.6736 | -122.0169 | -26.9623 | -121.875 | 0.045776 | 0.054932 | -121.8201 | -121.9666 | -0.068665 | 0.036621 | 0.013733 | 1.0025 | 0.19226 | 0.15564 | -0.07782 | -0.10986 | -0.25635 | -0.064087 | -0.3067 | -0.16479 | 0.091553 | -0.054931 | 121.8338 | 121.7422 | 91.4749 | -121.7834 | 121.756 | 121.7651 | 94.7479 | -122.0764
1156.5938 | 121.9025 | -121.7743 | 0.12817 | 0.0097657 | 0.016613 | 0.06884 | 0.0037127 | 0.067011 | 0.0031531 | 0.001333 | -0.0040437 | -0.0024183 | 0.06307 | 0.066031 | 0.0044733 | -0.006838 | -0.045776 | -120.7809 | -30.2856 | -121.582 | 0.14191 | -121.8018 | -121.6644 | -122.0856 | -26.6144 | -121.9162 | 0.027466 | 0.09613 | -121.8384 | -121.962 | -0.027466 | 0.10986 | 0.013733 | 0.99335 | 0.19226 | 0.082398 | -0.17395 | -0.064087 | -0.18768 | -0.10071 | -0.31128 | -0.14191 | 0.045776 | -0.032044 | 121.9162 | 121.7285 | 91.4886 | -121.7926 | 121.8018 | 121.8704 | 95.1599 | -122.0901
1158.2656 | 121.8887 | -121.7422 | 0.14648 | -0.013122 | 0.015545 | 0.068413 | 0.0030719 | 0.063166 | -0.0041101 | -0.0010168 | -0.011673 | -0.0079725 | 0.061148 | 0.064749 | 0.0044733 | -0.0076926 | 0.068665 | -120.6207 | -29.2191 | -121.5134 | 0.10071 | -121.7514 | -121.637 | -121.9894 | -26.7609 | -121.7926 | -0.004578 | 0.041199 | -121.7789 | -121.9391 | -0.009155 | 0.10529 | -0.045776 | 1.1215 | 0.22888 | 0.1236 | -0.077819 | -0.036621 | -0.19684 | -0.15106 | -0.24719 | -0.050354 | 0.14648 | -0.10529 | 121.843 | 121.8109 | 92.5232 | -121.7834 | 121.7377 | 121.7834 | 94.9814 | -122.0856
1159.9375 | 122.0078 | -121.7056 | 0.10529 | -0.020752 | 0.015118 | 0.069908 | 0.0071307 | 0.066157 | -0.0032555 | -0.0029394 | -0.019302 | -0.0051953 | 0.06307 | 0.063681 | 0.0038325 | -0.0064108 | 0.064087 | -120.6528 | -28.9948 | -121.4859 | 0.10071 | -121.7697 | -121.6415 | -122.0444 | -26.651 | -121.8338 | 0.022888 | 0.068665 | -121.8155 | -121.9345 | -0.064087 | 0.064086 | -0.004578 | 1.0529 | 0.21973 | 0.15564 | -0.041199 | -0.10986 | -0.22888 | -0.082398 | -0.33875 | -0.12817 | 0.10071 | -0.036621 | 121.8063 | 121.7697 | 92.7109 | -121.7468 | 121.7285 | 121.7743 | 95.0546 | -122.0398
1161.625 | 121.9299 | -121.7514 | 0.15106 | -0.020752 | 0.016613 | 0.069267 | 0.0052081 | 0.066584 | 0.0046485 | -0.00080316 | 0.0035858 | -0.0022045 | 0.063284 | 0.069662 | 0.0049005 | -0.0096152 | 0.050354 | -120.7443 | -29.5166 | -121.5546 | 0.12817 | -121.7972 | -121.6415 | -122.0444 | -26.445 | -121.9162 | 0.050354 | 0.082397 | -121.8109 | -121.9666 | -0.045776 | 0.10986 | -0.022888 | 1.0071 | 0.19684 | 0.086976 | -0.10071 | -0.059509 | -0.21515 | -0.10071 | -0.29297 | -0.1648 | 0.050354 | -0.068665 | 121.8796 | 121.8018 | 92.2348 | -121.7926 | 121.8018 | 121.8338 | 95.3064 | -122.1176
1164.7656 | 121.9894 | -121.7194 | 0.12817 | -0.0054933 | 0.017682 | 0.069267 | 0.0086261 | 0.064021 | -0.0047509 | -0.0018714 | -0.011673 | -0.0064771 | 0.062643 | 0.066031 | 0.0012689 | -0.0072652 | 0.059509 | -120.6482 | -29.3015 | -121.4951 | 0.11902 | -121.788 | -121.6461 | -122.0306 | -26.5732 | -121.8384 | 0.032043 | 0.064087 | -121.8155 | -121.9757 | -0.068665 | 0.073242 | -0.009155 | 1.0712 | 0.2243 | 0.15106 | -0.068665 | -0.096131 | -0.25635 | -0.096131 | -0.31128 | -0.11902 | 0.13733 | -0.064087 | 121.8384 | 121.7789 | 92.4179 | -121.7743 | 121.7514 | 121.7834 | 95.1462 | -122.1039
1168.5 | 121.9162 | -121.756 | 0.13275 | -0.013122 | 0.0099912 | 0.069695 | 0.00050847 | 0.064662 | -0.0028283 | -0.0031532 | -0.011673 | -0.0083997 | 0.060293 | 0.06304 | 0.0044733 | -0.0061972 | 0.036621 | -120.6894 | -30.0385 | -121.5363 | 0.10071 | -121.7697 | -121.6187 | -122.0306 | -27.3743 | -121.8475 | 0.022888 | 0.059509 | -121.8201 | -121.9574 | -0.013733 | 0.13733 | -0.032043 | 1.0666 | 0.21973 | 0.082397 | -0.09613 | -0.064087 | -0.20142 | -0.10986 | -0.27466 | -0.091553 | 0.10986 | -0.073242 | 121.8567 | 121.7926 | 91.7175 | -121.7514 | 121.7789 | 121.8155 | 94.3817 | -122.0901
1173.7812 | 122.0627 | -121.7239 | 0.10986 | -0.0054933 | 0.017041 | 0.06884 | 0.0064899 | 0.064875 | 0.0012305 | -0.0040076 | -0.0040437 | -0.0026319 | 0.063711 | 0.065604 | 0.0038325 | -0.010256 | 0.009155 | -120.7993 | -29.6173 | -121.55 | 0.12817 | -121.8338 | -121.6644 | -122.0398 | -26.825 | -121.9116 | 0.041199 | 0.091553 | -121.8658 | -121.9711 | -0.10986 | 0.059509 | 0.018311 | 0.92468 | 0.17395 | 0.11444 | -0.10071 | -0.14191 | -0.24719 | -0.068664 | -0.31586 | -0.18768 | 0.059509 | -0.01831 | 121.8521 | 121.7331 | 92.1066 | -121.7743 | 121.7651 | 121.8155 | 94.899 | -122.081
1176.4062 | 121.962 | -121.7468 | 0.13733 | -0.013122 | 0.015545 | 0.068413 | 0.0043537 | 0.064448 | 0.00058966 | -0.0014442 | -0.011673 | -0.0047681 | 0.061788 | 0.066885 | 0.0063959 | -0.008547 | 0.10071 | -120.6848 | -29.1 | -121.4905 | 0.11444 | -121.7789 | -121.6278 | -121.9208 | -26.7426 | -121.8063 | 0.013733 | 0.041199 | -121.8109 | -121.9345 | -0.032044 | 0.11902 | -0.022888 | 1.062 | 0.25635 | 0.13733 | -0.036621 | -0.064087 | -0.18768 | -0.1236 | -0.17395 | -0.059509 | 0.12817 | -0.09613 | 121.8613 | 121.8475 | 92.6468 | -121.7651 | 121.7606 | 121.788 | 95.0043 | -122.0718
1178.0938 | 121.9391 | -121.7422 | 0.14191 | -0.0054933 | 0.012341 | 0.072044 | 0.0049945 | 0.065089 | -0.0036829 | -0.0022986 | -0.0040437 | -0.0077587 | 0.061788 | 0.065176 | 0.0040461 | -0.0079062 | 0.041199 | -120.7214 | -29.0405 | -121.5408 | 0.11902 | -121.7697 | -121.6415 | -121.994 | -24.6185 | -121.8292 | 0.013733 | 0.050354 | -121.7834 | -121.9757 | -0.027465 | 0.10071 | -0.022888 | 1.0208 | 0.20142 | 0.10071 | -0.10071 | -0.041198 | -0.23346 | -0.12817 | -0.25177 | -0.086975 | 0.14648 | -0.091553 | 121.8613 | 121.7834 | 92.7017 | -121.7834 | 121.756 | 121.7926 | 97.1237 | -122.1176
1179.8438 | 121.9391 | -121.7789 | 0.14648 | -0.0054933 | 0.018322 | 0.06649 | 0.0047809 | 0.065302 | 0.0042213 | 0.00047844 | 0.0035858 | 0.00078608 | 0.061788 | 0.066885 | 0.0068231 | -0.0098288 | 0.07782 | -120.7672 | -28.5828 | -121.55 | 0.14191 | -121.8018 | -121.6507 | -121.9894 | -24.0097 | -121.9025 | 0.041199 | 0.086975 | -121.8246 | -121.9711 | -0.022888 | 0.12817 | -0.004577 | 1.0117 | 0.22888 | 0.10071 | -0.068664 | -0.045776 | -0.19226 | -0.10529 | -0.21057 | -0.1236 | 0.068664 | -0.059509 | 121.9208 | 121.8567 | 93.1961 | -121.7972 | 121.8201 | 121.8658 | 97.7692 | -122.1176
1181.5781 | 121.9345 | -121.7285 | 0.14648 | -0.013122 | 0.014691 | 0.068413 | 0.0022175 | 0.065302 | 0.0016577 | 5.1244e-05 | 0.0035858 | -0.0064771 | 0.059866 | 0.062613 | 0.0059687 | -0.0076926 | 0.091553 | -120.694 | -29.8874 | -121.4859 | 0.082397 | -121.7743 | -121.6278 | -121.9299 | -23.3917 | -121.7972 | -0.027466 | 0.022888 | -121.8063 | -121.9299 | -0.045776 | 0.10071 | -0.064087 | 1.0345 | 0.24262 | 0.14191 | -0.054931 | -0.077819 | -0.20142 | -0.17395 | -0.20142 | -0.068664 | 0.13275 | -0.1236 | 121.8109 | 121.8201 | 91.8411 | -121.7743 | 121.701 | 121.7514 | 98.3368 | -122.0764
1183.2812 | 121.962 | -121.7377 | 0.11902 | -0.013122 | 0.018536 | 0.068413 | 0.0047809 | 0.065302 | 0.0012305 | -0.0010168 | -0.011673 | -0.0054089 | 0.062856 | 0.064108 | 0.0066095 | -0.010256 | 0.036621 | -120.7306 | -29.155 | -121.5271 | 0.10986 | -121.7651 | -121.6736 | -121.9254 | -23.7213 | -121.8292 | 0.009155 | 0.045776 | -121.8109 | -121.9666 | -0.027466 | 0.064087 | -0.009156 | 1.0071 | 0.21057 | 0.14648 | -0.082398 | -0.073242 | -0.22888 | -0.10986 | -0.18768 | -0.091553 | 0.13733 | -0.073243 | 121.8475 | 121.7743 | 92.5827 | -121.7926 | 121.7468 | 121.7834 | 98.0164 | -122.0856
1185.0156 | 121.9116 | -121.7834 | 0.14191 | -0.028381 | 0.01875 | 0.067131 | 0.0047809 | 0.06808 | 0.0018713 | -0.0016578 | -0.0040437 | -0.0032727 | 0.061575 | 0.065604 | 0.0087457 | -0.0081198 | -0.018311 | -120.8038 | -28.9581 | -121.582 | 0.14648 | -121.8018 | -121.6782 | -122.049 | -23.204 | -121.962 | 0.054932 | 0.082397 | -121.8338 | -121.9986 | -0.018311 | 0.10528 | 0.004577 | 0.97961 | 0.20142 | 0.096131 | -0.16022 | -0.050354 | -0.21515 | -0.086975 | -0.2655 | -0.17853 | 0.036621 | -0.05951 | 121.9299 | 121.7651 | 92.8253 | -121.8201 | 121.8384 | 121.8658 | 98.5794 | -122.1405
1186.6875 | 122.0078 | -121.7285 | 0.1236 | -0.013122 | 0.017468 | 0.069481 | 0.010762 | 0.065943 | -0.0043237 | -0.0010168 | -0.0040437 | -0.0054089 | 0.063925 | 0.062827 | 0.00020086 | -0.0064108 | 0.050354 | -120.6619 | -29.0222 | -121.5225 | 0.11444 | -121.8018 | -121.6415 | -122.0215 | -23.6115 | -121.8704 | 0.036621 | 0.073242 | -121.8384 | -121.9757 | -0.073242 | 0.086975 | -0.009155 | 1.0666 | 0.20599 | 0.11902 | -0.073242 | -0.10986 | -0.24719 | -0.086975 | -0.29297 | -0.14191 | 0.10529 | -0.050354 | 121.843 | 121.7789 | 92.7063 | -121.7651 | 121.7651 | 121.8018 | 98.1171 | -122.0993
1188.4219 | 122.049 | -121.701 | 0.10529 | -0.013122 | 0.014691 | 0.070763 | 0.0064899 | 0.065943 | -0.0041101 | -0.0031532 | 0.011215 | -0.0086133 | 0.062429 | 0.065604 | 0.0019099 | -0.0083334 | 0.09613 | -120.5978 | -28.4821 | -121.4951 | 0.11902 | -121.756 | -121.637 | -121.9162 | -22.7051 | -121.7697 | -0.009155 | 0.041199 | -121.7789 | -121.9528 | -0.054931 | 0.064087 | 0.013733 | 1.1032 | 0.20599 | 0.14191 | -0.009156 | -0.07782 | -0.25177 | -0.11444 | -0.21515 | -0.068664 | 0.18311 | -0.064087 | 121.8201 | 121.7972 | 93.219 | -121.7422 | 121.6919 | 121.7422 | 98.996 | -122.0581
1190.0938 | 122.0169 | -121.701 | 0.12817 | 0.0021362 | 0.015973 | 0.069908 | 0.0084125 | 0.065089 | -0.00090574 | -0.0042212 | -0.0040437 | -0.0079725 | 0.060507 | 0.066672 | 0.0025507 | -0.010683 | 0.10986 | -120.6253 | -29.5944 | -121.4722 | 0.10071 | -121.7606 | -121.6415 | -121.9116 | -22.5952 | -121.7697 | 0.004578 | 0.054932 | -121.7834 | -121.9116 | -0.059509 | 0.059509 | -0.027466 | 1.0757 | 0.22888 | 0.16937 | -0.018311 | -0.082397 | -0.21057 | -0.1236 | -0.21057 | -0.068664 | 0.14191 | -0.073242 | 121.8018 | 121.8109 | 92.1066 | -121.7697 | 121.7056 | 121.756 | 99.1058 | -122.0398
1191.8438 | 121.9666 | -121.7606 | 0.14648 | -0.020752 | 0.016827 | 0.066917 | 0.0013629 | 0.066798 | 0.0040077 | 0.00090584 | -0.011673 | -0.00028192 | 0.062002 | 0.066885 | 0.0055415 | -0.0087606 | 0.032043 | -120.7901 | -29.0039 | -121.5775 | 0.14191 | -121.8109 | -121.6553 | -121.9574 | -22.7737 | -121.8796 | 0.041199 | 0.064087 | -121.8201 | -121.9803 | -0.050354 | 0.10529 | -0.004577 | 0.97046 | 0.1831 | 0.077819 | -0.11444 | -0.059509 | -0.21973 | -0.10529 | -0.19684 | -0.11902 | 0.10071 | -0.082397 | 121.9025 | 121.7926 | 92.7567 | -121.8018 | 121.8018 | 121.8246 | 98.9868 | -122.1268
1193.5781 | 121.9345 | -121.756 | 0.16022 | -0.013122 | 0.019818 | 0.068626 | 0.0026447 | 0.065089 | 0.0059303 | 0.0015466 | -0.0040437 | -0.00092292 | 0.062856 | 0.064536 | 0.0061823 | -0.0076926 | 0.009155 | -120.7718 | -29.7226 | -121.5775 | 0.15106 | -121.7789 | -121.6415 | -121.9986 | -22.6593 | -121.9482 | 0.045776 | 0.091553 | -121.8384 | -121.9803 | -0.022889 | 0.11444 | -0.009155 | 0.98419 | 0.17853 | 0.064087 | -0.15106 | -0.082398 | -0.22431 | -0.11444 | -0.24262 | -0.19226 | 0.032044 | -0.068664 | 121.907 | 121.7651 | 92.0334 | -121.8018 | 121.8018 | 121.8475 | 99.0967 | -122.1405
1195.25 | 121.9391 | -121.7743 | 0.15564 | -0.0054933 | 0.017682 | 0.069481 | 0.0030719 | 0.064875 | 0.0046485 | -0.00037596 | -0.011673 | -0.0045545 | 0.06542 | 0.065817 | 0.0061823 | -0.0079062 | -0.022888 | -120.7947 | -29.8553 | -121.5912 | 0.14191 | -121.8109 | -121.6553 | -122.0261 | -23.1812 | -121.962 | 0.054932 | 0.082397 | -121.8475 | -122.0123 | -0.036621 | 0.11902 | -0.013733 | 0.97961 | 0.1831 | 0.064086 | -0.17853 | -0.073242 | -0.23804 | -0.10071 | -0.25177 | -0.18768 | 0.050354 | -0.073243 | 121.9162 | 121.7514 | 91.9189 | -121.8109 | 121.8292 | 121.8567 | 98.5931 | -122.168
1197 | 121.9803 | -121.7285 | 0.13275 | 0.0097657 | 0.015973 | 0.068413 | 0.0028583 | 0.063807 | 0.00080326 | -0.00058956 | 0.0035858 | -0.0051953 | 0.061788 | 0.063467 | 0.0066095 | -0.0072652 | 0.054932 | -120.6848 | -30.455 | -121.5225 | 0.11902 | -121.7743 | -121.6461 | -121.9391 | -23.877 | -121.8155 | 0.013733 | 0.050354 | -121.8018 | -121.9437 | -0.045776 | 0.082398 | -0.013732 | 1.0437 | 0.20599 | 0.1236 | -0.077819 | -0.073242 | -0.21515 | -0.11902 | -0.21057 | -0.086975 | 0.12817 | -0.082397 | 121.8475 | 121.7834 | 91.2735 | -121.7789 | 121.7422 | 121.7789 | 97.8516 | -122.0764
1198.7344 | 121.9666 | -121.7651 | 0.12817 | -0.0054933 | 0.020031 | 0.067345 | 0.0037127 | 0.067011 | 0.0035803 | 5.1244e-05 | 0.0035858 | -0.0026319 | 0.061788 | 0.064749 | 0.0070367 | -0.0066244 | 0.054932 | -120.6985 | -30.5878 | -121.55 | 0.13733 | -121.788 | -121.6507 | -121.9986 | -23.5703 | -121.8979 | 0.027466 | 0.10071 | -121.8155 | -122.0123 | -0.022888 | 0.11444 | 0.009155 | 1.0666 | 0.21515 | 0.10071 | -0.073242 | -0.050354 | -0.24719 | -0.10071 | -0.23346 | -0.13275 | 0.11444 | -0.027466 | 121.9025 | 121.8201 | 91.1774 | -121.7789 | 121.7926 | 121.8658 | 98.1949 | -122.1405
1200.4844 | 121.9162 | -121.7789 | 0.1236 | -0.013122 | 0.013836 | 0.070122 | 0.0034991 | 0.065302 | -0.0032555 | -0.0029394 | -0.0040437 | -0.0077587 | 0.062856 | 0.065176 | 0.0027643 | -0.0047018 | 0.050354 | -120.6528 | -30.3223 | -121.5225 | 0.09613 | -121.756 | -121.6553 | -121.9986 | -23.2224 | -121.8338 | 0.004578 | 0.041199 | -121.8384 | -121.9482 | 0.022889 | 0.1236 | -0.027466 | 1.1261 | 0.25635 | 0.13275 | -0.073242 | -0.059509 | -0.16937 | -0.11902 | -0.21973 | -0.054931 | 0.11444 | -0.082397 | 121.875 | 121.8292 | 91.4566 | -121.7789 | 121.7834 | 121.8201 | 98.5565 | -122.0718
1202.1562 | 122.0078 | -121.7102 | 0.13275 | -0.013122 | 0.018322 | 0.069054 | 0.0099079 | 0.064448 | -0.0017603 | -0.002085 | 0.0035858 | -0.0045545 | 0.063925 | 0.066672 | 0.0023371 | -0.008547 | -0.013733 | -120.7214 | -31.073 | -121.5866 | 0.14191 | -121.8109 | -121.6553 | -122.0261 | -23.2819 | -121.9025 | 0.054932 | 0.086975 | -121.843 | -121.9757 | -0.10071 | 0.054932 | 0.009156 | 0.98877 | 0.1236 | 0.068664 | -0.14648 | -0.13275 | -0.2655 | -0.077819 | -0.31586 | -0.19226 | 0.073242 | -0.045776 | 121.8521 | 121.6965 | 90.6372 | -121.788 | 121.7651 | 121.7972 | 98.4283 | -122.1085
1203.8906 | 121.9574 | -121.7377 | 0.13275 | -0.0054933 | 0.015759 | 0.069695 | 0.0030719 | 0.06573 | -0.00026494 | 5.1244e-05 | -0.011673 | -0.0056225 | 0.061575 | 0.066458 | 0.0055415 | -0.0081198 | 0.10986 | -120.639 | -30.6061 | -121.5134 | 0.09613 | -121.7651 | -121.6507 | -121.9162 | -23.8037 | -121.7972 | 0.018311 | 0.032043 | -121.7926 | -121.9574 | -0.027466 | 0.086975 | -0.036621 | 1.0986 | 0.2243 | 0.13733 | -0.022888 | -0.054932 | -0.21973 | -0.11444 | -0.17853 | -0.059509 | 0.16022 | -0.10071 | 121.8338 | 121.8475 | 91.1316 | -121.7834 | 121.756 | 121.7697 | 97.934 | -122.0901
1205.625 | 122.0535 | -121.7331 | 0.11444 | -0.013122 | 0.018536 | 0.066917 | 0.0067035 | 0.069788 | 0.0022987 | -0.00037596 | -0.0040437 | -0.0028455 | 0.064138 | 0.065604 | 0.0049005 | -0.0096152 | 0 | -120.7306 | -30.4047 | -121.5363 | 0.13733 | -121.8201 | -121.6873 | -121.9757 | -22.2427 | -121.8887 | 0.041199 | 0.073242 | -121.8246 | -121.9757 | -0.086975 | 0.045776 | 0.022888 | 1.0025 | 0.19684 | 0.15106 | -0.11444 | -0.091553 | -0.24262 | -0.073242 | -0.24262 | -0.15564 | 0.086975 | -0.041199 | 121.8704 | 121.7331 | 91.3284 | -121.8018 | 121.7743 | 121.8063 | 99.4904 | -122.0901
1207.375 | 122.0032 | -121.7285 | 0.10529 | -0.013122 | 0.015973 | 0.070763 | 0.0067035 | 0.066584 | -0.0041101 | -0.0010168 | -0.0040437 | -0.0069043 | 0.061361 | 0.064536 | 0.0010553 | -0.0072652 | 0.091553 | -120.6253 | -30.1117 | -121.4996 | 0.091553 | -121.788 | -121.6415 | -121.9208 | -22.7554 | -121.7972 | 0 | 0.041199 | -121.8018 | -121.9574 | -0.059509 | 0.086975 | -0.013733 | 1.1032 | 0.22888 | 0.14191 | -0.013733 | -0.073242 | -0.22888 | -0.10529 | -0.19226 | -0.068664 | 0.16022 | -0.064087 | 121.8201 | 121.8201 | 91.6168 | -121.7468 | 121.7285 | 121.7697 | 98.9731 | -122.0627
1209.0625 | 122.0215 | -121.7377 | 0.13275 | -0.0054933 | 0.016827 | 0.070122 | 0.0054217 | 0.066798 | -0.0024011 | -0.0033668 | 0.0035858 | -0.0034863 | 0.064138 | 0.066031 | 0.0025507 | -0.0098288 | -0.009155 | -120.7306 | -29.4846 | -121.5683 | 0.14191 | -121.8338 | -121.6782 | -122.0261 | -22.9477 | -121.9254 | 0.041199 | 0.091553 | -121.8613 | -121.9894 | -0.09613 | 0.059509 | 0.009156 | 1.0071 | 0.16937 | 0.10986 | -0.14191 | -0.1236 | -0.25177 | -0.091552 | -0.28839 | -0.18768 | 0.064087 | -0.041198 | 121.8796 | 121.7285 | 92.2531 | -121.8109 | 121.7789 | 121.8292 | 98.79 | -122.1222
1210.7969 | 122.0078 | -121.7102 | 0.1236 | -0.013122 | 0.0117 | 0.070122 | 0.0026447 | 0.064875 | -0.0064599 | -0.0040076 | -0.0040437 | -0.0073315 | 0.06072 | 0.064536 | 0.0038325 | -0.0070516 | 0.022888 | -120.6985 | -29.3427 | -121.5454 | 0.11902 | -121.7697 | -121.6461 | -121.9711 | -22.316 | -121.8201 | 0.018311 | 0.073242 | -121.8201 | -121.9482 | -0.059509 | 0.064087 | -0.004577 | 1.0117 | 0.16479 | 0.10071 | -0.10071 | -0.10986 | -0.23804 | -0.10528 | -0.26093 | -0.10986 | 0.12817 | -0.050354 | 121.8292 | 121.7331 | 92.3676 | -121.7697 | 121.7285 | 121.7834 | 99.3942 | -122.0718
1212.5469 | 122.0398 | -121.7102 | 0.11902 | -0.013122 | 0.017254 | 0.069481 | 0.0075581 | 0.068293 | -0.0043237 | -0.0025122 | -0.011673 | -0.0073315 | 0.063284 | 0.065604 | 0.0027643 | -0.0089742 | 0.11902 | -120.6162 | -29.7729 | -121.5088 | 0.09613 | -121.788 | -121.637 | -121.8933 | -22.467 | -121.7789 | 0.013733 | 0.050354 | -121.7972 | -121.9711 | -0.07782 | 0.073242 | -0.022889 | 1.0941 | 0.20142 | 0.12817 | 0 | -0.086975 | -0.26093 | -0.10529 | -0.18311 | -0.068665 | 0.19226 | -0.068665 | 121.8063 | 121.8292 | 91.9373 | -121.756 | 121.7239 | 121.7606 | 99.2432 | -122.0901
1214.2188 | 122.049 | -121.6919 | 0.082397 | -0.020752 | 0.013623 | 0.06884 | 0.0034991 | 0.065943 | -0.0019739 | -0.0033668 | -0.0040437 | -0.0066907 | 0.062643 | 0.067953 | 0.0019099 | -0.01047 | 0.10986 | -120.6802 | -29.2099 | -121.5225 | 0.09613 | -121.7789 | -121.6415 | -121.9162 | -21.6568 | -121.7743 | 0.018311 | 0.059509 | -121.7972 | -121.9254 | -0.086975 | 0.050354 | 0.013733 | 1.0117 | 0.16937 | 0.11902 | 0.027466 | -0.10528 | -0.23346 | -0.064086 | -0.2243 | -0.082397 | 0.15106 | -0.022888 | 121.788 | 121.8018 | 92.482 | -121.7239 | 121.7102 | 121.7514 | 100.0351 | -122.0078
1215.9531 | 121.9208 | -121.8018 | 0.15564 | -0.013122 | 0.020031 | 0.065208 | 0.0039265 | 0.067439 | 0.0052893 | -0.0012306 | -0.0040437 | -0.0030591 | 0.063711 | 0.066031 | 0.0074641 | -0.012179 | 0.064087 | -120.7809 | -28.981 | -121.55 | 0.12817 | -121.8155 | -121.6644 | -121.9711 | -21.6705 | -121.9345 | 0.036621 | 0.07782 | -121.843 | -121.9803 | -0.013733 | 0.13733 | -0.027466 | 1.0208 | 0.25177 | 0.11444 | -0.091553 | -0.041199 | -0.17853 | -0.11902 | -0.16937 | -0.13275 | 0.045777 | -0.07782 | 121.9299 | 121.8658 | 92.8207 | -121.8201 | 121.8384 | 121.8796 | 100.1312 | -122.1359
1217.6406 | 122.0581 | -121.7651 | 0.10986 | -0.020752 | 0.017682 | 0.066917 | 0.0075581 | 0.066157 | 0.0029395 | -0.0027258 | -0.0040437 | -0.0049817 | 0.064352 | 0.065604 | 0.0055415 | -0.0081198 | -0.009155 | -120.7672 | -28.0426 | -121.5683 | 0.14648 | -121.8384 | -121.6782 | -122.0169 | -21.6751 | -121.9116 | 0.036621 | 0.07782 | -121.843 | -122.0032 | -0.073242 | 0.086975 | 0.036621 | 0.99792 | 0.19684 | 0.10986 | -0.11902 | -0.07782 | -0.23804 | -0.073242 | -0.25177 | -0.14648 | 0.091553 | -0.032043 | 121.9116 | 121.756 | 93.7225 | -121.788 | 121.8018 | 121.843 | 100.09 | -122.113
1219.375 | 122.0581 | -121.6919 | 0.11902 | -0.013122 | 0.0164 | 0.070122 | 0.0062763 | 0.063807 | -0.0038965 | -0.0033668 | -0.0040437 | -0.0062635 | 0.06307 | 0.066458 | 0.00084166 | -0.006838 | 0.064087 | -120.6665 | -27.5665 | -121.5042 | 0.10071 | -121.7789 | -121.6461 | -121.9391 | -21.7026 | -121.7834 | 0.009155 | 0.045776 | -121.7926 | -121.9254 | -0.086975 | 0.045777 | -0.018311 | 1.0254 | 0.18768 | 0.14191 | -0.054932 | -0.10071 | -0.23346 | -0.10986 | -0.24719 | -0.091552 | 0.14191 | -0.073243 | 121.7926 | 121.756 | 94.1254 | -121.7651 | 121.7011 | 121.7377 | 99.9893 | -122.0444
1221.125 | 122.0673 | -121.7285 | 0.09613 | -0.013122 | 0.016827 | 0.069695 | 0.0056355 | 0.065089 | -0.0030419 | -0.0042212 | -0.0040437 | -0.0056225 | 0.06307 | 0.064963 | -0.00044014 | -0.0079062 | 0.12817 | -120.5841 | -28.2532 | -121.5134 | 0.09613 | -121.7606 | -121.637 | -121.907 | -21.8536 | -121.7834 | 0.004578 | 0.041199 | -121.8063 | -121.9482 | -0.032043 | 0.091553 | 0 | 1.1444 | 0.21515 | 0.1236 | 0.032044 | -0.077819 | -0.21973 | -0.091552 | -0.17853 | -0.054931 | 0.16479 | -0.054931 | 121.8246 | 121.8567 | 93.4753 | -121.7331 | 121.7331 | 121.7697 | 99.8749 | -122.0444
1222.8906 | 121.9254 | -121.7789 | 0.14191 | 0.0021362 | 0.014264 | 0.068413 | 0.0034991 | 0.066371 | -0.00047854 | 0.00026484 | -0.011673 | -0.0064771 | 0.061148 | 0.064322 | 0.0066095 | -0.0083334 | 0.10986 | -120.6116 | -28.1845 | -121.5042 | 0.10986 | -121.7789 | -121.6278 | -121.9254 | -22.0963 | -121.8063 | 0.004578 | 0.045776 | -121.8201 | -121.9437 | 0 | 0.15106 | -0.032044 | 1.1673 | 0.27466 | 0.1236 | -0.032044 | -0.041198 | -0.16479 | -0.13733 | -0.14648 | -0.027465 | 0.13733 | -0.096131 | 121.8887 | 121.8887 | 93.5944 | -121.7697 | 121.7834 | 121.8246 | 99.6826 | -122.0856
1224.5625 | 121.9025 | -121.7697 | 0.14648 | -0.013122 | 0.011914 | 0.070976 | 0.0022175 | 0.066157 | -0.0013329 | -0.0014442 | -0.0040437 | -0.0047681 | 0.059225 | 0.064536 | 0.0055415 | -0.006838 | 0.10071 | -120.6116 | -28.2394 | -121.5179 | 0.10986 | -121.7651 | -121.6278 | -121.9574 | -22.1191 | -121.8201 | 0.009155 | 0.050354 | -121.7972 | -121.9757 | 0.004577 | 0.14191 | -0.036621 | 1.1581 | 0.25177 | 0.10986 | -0.045776 | -0.027466 | -0.20599 | -0.13733 | -0.18768 | -0.050354 | 0.15564 | -0.09613 | 121.8796 | 121.8704 | 93.5303 | -121.7743 | 121.7789 | 121.8201 | 99.6506 | -122.1222
1226.2969 | 121.9894 | -121.7285 | 0.11444 | 0.0021362 | 0.016827 | 0.068626 | 0.0086261 | 0.065516 | -5.1338e-05 | -0.0046484 | 0.011215 | -0.0045545 | 0.063925 | 0.064108 | 0.0023371 | -0.008547 | 0.086975 | -120.6345 | -27.8549 | -121.5042 | 0.11902 | -121.7834 | -121.6324 | -121.9849 | -21.1075 | -121.8521 | 0.041199 | 0.064087 | -121.8155 | -121.9757 | -0.054931 | 0.096131 | 0.004578 | 1.0941 | 0.22431 | 0.12817 | -0.027466 | -0.086975 | -0.24719 | -0.073242 | -0.25635 | -0.1236 | 0.1236 | -0.050354 | 121.8475 | 121.8155 | 93.8736 | -121.7468 | 121.7697 | 121.7926 | 100.621 | -122.0901
1228.0312 | 121.994 | -121.7468 | 0.1236 | -0.0054933 | 0.015332 | 0.070549 | 0.0073443 | 0.066584 | -0.0011193 | -0.0031532 | -0.0040437 | -0.0066907 | 0.062002 | 0.064963 | 0.0025507 | -0.0098288 | 0.09613 | -120.5933 | -26.9531 | -121.4996 | 0.10986 | -121.788 | -121.6461 | -121.9528 | -21.0205 | -121.8246 | 0.018311 | 0.068665 | -121.8384 | -121.9437 | -0.041199 | 0.10071 | -0.013733 | 1.1536 | 0.24719 | 0.14648 | -0.027466 | -0.091553 | -0.19684 | -0.10528 | -0.20599 | -0.07782 | 0.11902 | -0.054931 | 121.8567 | 121.843 | 94.7937 | -121.7697 | 121.7651 | 121.8155 | 100.7263 | -122.0673
1229.7031 | 122.0398 | -121.7422 | 0.10529 | -0.013122 | 0.017895 | 0.067131 | 0.0043537 | 0.067866 | 0.0029395 | -0.0016578 | -0.011673 | -0.0019909 | 0.062216 | 0.067313 | 0.0061823 | -0.0089742 | 0.073242 | -120.6528 | -27.7771 | -121.5317 | 0.12817 | -121.8109 | -121.669 | -121.9666 | -21.2906 | -121.8796 | 0.041199 | 0.068665 | -121.8338 | -121.9711 | -0.068664 | 0.073243 | 0.022888 | 1.0895 | 0.21057 | 0.13733 | -0.032044 | -0.091552 | -0.22888 | -0.064087 | -0.2243 | -0.13733 | 0.091552 | -0.036621 | 121.8704 | 121.8155 | 93.9651 | -121.7743 | 121.7834 | 121.8109 | 100.4517 | -122.0764
1231.4531 | 121.9711 | -121.7514 | 0.1236 | -0.013122 | 0.013836 | 0.068413 | 0.00029487 | 0.064875 | 0.0012305 | -0.00058956 | -0.0040437 | -0.0049817 | 0.06307 | 0.062613 | 0.0066095 | -0.0072652 | 0.050354 | -120.6665 | -27.1683 | -121.5408 | 0.10986 | -121.7789 | -121.637 | -121.9299 | -20.9656 | -121.8201 | -0.004578 | 0.027466 | -121.8109 | -121.9391 | -0.027466 | 0.11444 | -0.013733 | 1.0849 | 0.21057 | 0.09613 | -0.073242 | -0.059509 | -0.18768 | -0.12817 | -0.17853 | -0.068664 | 0.11902 | -0.09613 | 121.8613 | 121.8018 | 94.5831 | -121.7606 | 121.7468 | 121.7789 | 100.7858 | -122.0627
1233.1406 | 122.0123 | -121.7606 | 0.1236 | -0.013122 | 0.021954 | 0.068413 | 0.0069171 | 0.066157 | 0.0044349 | 0.00090584 | -0.0040437 | -0.0036999 | 0.065847 | 0.066245 | 0.0066095 | -0.0072652 | 0.064087 | -120.6619 | -26.8616 | -121.55 | 0.1236 | -121.8155 | -121.6919 | -121.962 | -21.4325 | -121.8796 | 0.032043 | 0.073242 | -121.8246 | -121.9894 | -0.054932 | 0.068664 | 0 | 1.0986 | 0.21057 | 0.14191 | -0.059509 | -0.064087 | -0.22888 | -0.091553 | -0.20142 | -0.11902 | 0.10986 | -0.050354 | 121.8842 | 121.8246 | 94.899 | -121.8155 | 121.7926 | 121.8338 | 100.3281 | -122.113
1234.875 | 121.9803 | -121.7468 | 0.15106 | -0.013122 | 0.013196 | 0.068413 | 0.0034991 | 0.064448 | -0.00047854 | -0.0022986 | -0.0040437 | -0.0043409 | 0.06072 | 0.06539 | 0.0053279 | -0.0053426 | 0.036621 | -120.6573 | -26.0971 | -121.5271 | 0.10986 | -121.7834 | -121.6644 | -121.9574 | -21.0342 | -121.8201 | 0.004578 | 0.059509 | -121.843 | -121.9711 | -0.036621 | 0.082397 | -0.041199 | 1.0895 | 0.21973 | 0.13733 | -0.11444 | -0.096131 | -0.2243 | -0.14648 | -0.21057 | -0.073242 | 0.15106 | -0.091553 | 121.8567 | 121.7834 | 95.6497 | -121.8155 | 121.7514 | 121.8063 | 100.7126 | -122.1222
1236.5469 | 121.962 | -121.7331 | 0.13275 | -0.0054933 | 0.017468 | 0.066063 | 0.0041401 | 0.06338 | 0.00037606 | -0.0010168 | -0.011673 | -0.0030591 | 0.060507 | 0.065817 | 0.0074641 | -0.0064108 | -0.004578 | -120.7031 | -26.2711 | -121.5775 | 0.13275 | -121.7697 | -121.6553 | -121.9849 | -20.7275 | -121.8658 | 0.050354 | 0.064087 | -121.843 | -121.9711 | -0.036621 | 0.07782 | 0 | 1.03 | 0.15564 | 0.077819 | -0.13733 | -0.10986 | -0.23804 | -0.082397 | -0.25177 | -0.13275 | 0.10529 | -0.068664 | 121.8658 | 121.7285 | 95.462 | -121.788 | 121.7834 | 121.7972 | 101.0056 | -122.1039
1238.2969 | 121.9711 | -121.7377 | 0.12817 | -0.013122 | 0.013196 | 0.070763 | 0.0047809 | 0.064448 | -0.0062463 | -0.0022986 | -0.011673 | -0.0058361 | 0.062643 | 0.066031 | 0.0014825 | -0.0053426 | -0.009155 | -120.6619 | -26.5503 | -121.5454 | 0.11444 | -121.7789 | -121.6415 | -122.0169 | -20.8191 | -121.8246 | 0.022888 | 0.050354 | -121.7926 | -121.9482 | -0.041199 | 0.09613 | -0.013733 | 1.0757 | 0.19226 | 0.096131 | -0.13733 | -0.054932 | -0.21057 | -0.10529 | -0.27924 | -0.086975 | 0.1236 | -0.07782 | 121.8521 | 121.7285 | 95.1874 | -121.7697 | 121.7606 | 121.788 | 100.9186 | -122.0764
1239.9688 | 122.0123 | -121.7056 | 0.10986 | -0.0054933 | 0.018322 | 0.070763 | 0.0069171 | 0.065943 | -0.0032555 | -0.0014442 | -0.0040437 | -0.0047681 | 0.06307 | 0.067099 | 0.0012689 | -0.010683 | 0.091553 | -120.6024 | -26.5732 | -121.4951 | 0.10529 | -121.7606 | -121.6599 | -121.9757 | -19.9036 | -121.788 | 0.009155 | 0.050354 | -121.8246 | -121.9711 | -0.054932 | 0.045776 | -0.004577 | 1.1032 | 0.21057 | 0.16479 | -0.01831 | -0.11902 | -0.2655 | -0.10071 | -0.27008 | -0.082398 | 0.1831 | -0.059509 | 121.8109 | 121.7972 | 95.1324 | -121.7697 | 121.7148 | 121.756 | 101.8021 | -122.081
1241.7031 | 121.9711 | -121.7651 | 0.13733 | -0.013122 | 0.016613 | 0.068626 | 0.0056355 | 0.065516 | 0.0035803 | -0.0029394 | -0.0040437 | -0.0047681 | 0.062216 | 0.068381 | 0.0072505 | -0.0087606 | 0.027466 | -120.7443 | -26.5778 | -121.5775 | 0.14191 | -121.7834 | -121.6599 | -122.0306 | -20.3842 | -121.907 | 0.045776 | 0.086975 | -121.8246 | -121.962 | -0.01831 | 0.10529 | 0.004578 | 1.0208 | 0.18768 | 0.082397 | -0.10986 | -0.059509 | -0.19684 | -0.091553 | -0.2655 | -0.14191 | 0.054932 | -0.050354 | 121.907 | 121.7926 | 95.1874 | -121.7972 | 121.8109 | 121.8521 | 101.3809 | -122.0993
1243.3906 | 122.0169 | -121.7148 | 0.10071 | -0.013122 | 0.013409 | 0.070122 | 0.0077717 | 0.065516 | -0.0038965 | -0.00080316 | 0.0035858 | -0.0058361 | 0.061788 | 0.06774 | 0.0014825 | -0.0081198 | 0.027466 | -120.6757 | -26.2344 | -121.5363 | 0.10529 | -121.788 | -121.6232 | -122.0032 | -20.3339 | -121.8063 | 0.013733 | 0.045776 | -121.8155 | -121.962 | -0.073242 | 0.091553 | 0.004578 | 1.0391 | 0.17853 | 0.086975 | -0.073242 | -0.10071 | -0.24719 | -0.086975 | -0.28839 | -0.091552 | 0.15564 | -0.054932 | 121.8201 | 121.7422 | 95.4803 | -121.7239 | 121.7285 | 121.7606 | 101.3809 | -122.0627
1245.125 | 121.962 | -121.7422 | 0.12817 | -0.013122 | 0.012341 | 0.070335 | 0.0062763 | 0.063593 | -0.0036829 | -0.0010168 | -0.0040437 | -0.0075451 | 0.060507 | 0.066031 | 0.0027643 | -0.0089742 | 0.041199 | -120.7077 | -26.4267 | -121.5591 | 0.10986 | -121.7789 | -121.6644 | -122.0169 | -20.5627 | -121.8292 | 0.022888 | 0.068665 | -121.7926 | -121.962 | -0.036621 | 0.07782 | -0.018311 | 1.0345 | 0.18311 | 0.10529 | -0.086975 | -0.050354 | -0.21973 | -0.10529 | -0.27466 | -0.086975 | 0.13275 | -0.059509 | 121.8521 | 121.7834 | 95.3156 | -121.7926 | 121.7651 | 121.8109 | 101.1795 | -122.0901
1246.875 | 122.081 | -121.7148 | 0.10529 | -0.0054933 | 0.015545 | 0.067131 | 0.0030719 | 0.065943 | 0.0044349 | -0.0014442 | -0.011673 | -0.0011365 | 0.062429 | 0.066458 | 0.0053279 | -0.012179 | 0.036621 | -120.7535 | -25.0763 | -121.5454 | 0.15106 | -121.8338 | -121.6965 | -122.0261 | -20.3751 | -121.8979 | 0.059509 | 0.086975 | -121.8338 | -121.9666 | -0.11902 | 0.018311 | 0.045776 | 0.9613 | 0.16937 | 0.15106 | -0.068665 | -0.11902 | -0.25177 | -0.045777 | -0.31128 | -0.1831 | 0.068665 | -0.018311 | 121.8658 | 121.7514 | 96.6385 | -121.8018 | 121.7743 | 121.8018 | 101.3397 | -122.0718
1248.5625 | 122.0123 | -121.7468 | 0.1236 | -0.013122 | 0.01875 | 0.068199 | 0.0015765 | 0.067866 | 0.0031531 | -0.00016236 | -0.0040437 | 0.00014528 | 0.06307 | 0.066458 | 0.010455 | -0.0066244 | 0.07782 | -120.7169 | -25.0168 | -121.55 | 0.13275 | -121.8109 | -121.6644 | -121.994 | -19.5511 | -121.8887 | 0.041199 | 0.073242 | -121.8292 | -121.9849 | -0.064087 | 0.082397 | 0.009155 | 1.03 | 0.19684 | 0.11444 | -0.045776 | -0.082398 | -0.23804 | -0.082397 | -0.24719 | -0.14191 | 0.09613 | -0.050354 | 121.8796 | 121.8246 | 96.73 | -121.788 | 121.788 | 121.8201 | 102.1957 | -122.1085
1250.2969 | 122.0398 | -121.7056 | 0.10986 | 0.0021362 | 0.017682 | 0.06884 | 0.0086261 | 0.066584 | -0.0047509 | -0.0025122 | -0.011673 | -0.0077587 | 0.063497 | 0.064322 | -0.00022634 | -0.00577 | 0.082397 | -120.5978 | -25.1862 | -121.4859 | 0.10071 | -121.788 | -121.6507 | -121.9574 | -20.0684 | -121.788 | -0.004578 | 0.050354 | -121.7834 | -121.9482 | -0.082398 | 0.054931 | -0.009155 | 1.1078 | 0.21973 | 0.16479 | -0.027466 | -0.07782 | -0.24261 | -0.11444 | -0.25177 | -0.082398 | 0.16022 | -0.059509 | 121.8063 | 121.788 | 96.5195 | -121.7606 | 121.701 | 121.756 | 101.6373 | -122.0581
1252.0312 | 122.081 | -121.7331 | 0.11444 | -0.013122 | 0.018963 | 0.067772 | 0.0064899 | 0.066371 | 0.0014441 | 5.1244e-05 | 0.0035858 | -0.0032727 | 0.062002 | 0.067953 | 0.0057551 | -0.010256 | 0.027466 | -120.7626 | -24.8245 | -121.5408 | 0.12817 | -121.8338 | -121.6873 | -122.0215 | -19.0887 | -121.8933 | 0.032043 | 0.09613 | -121.8292 | -121.9894 | -0.10071 | 0.045776 | 0.013733 | 0.97046 | 0.19226 | 0.14648 | -0.086975 | -0.096131 | -0.25635 | -0.082398 | -0.28839 | -0.16022 | 0.09613 | -0.018311 | 121.8613 | 121.7606 | 96.9086 | -121.8018 | 121.7651 | 121.8292 | 102.6443 | -122.1039
1253.7656 | 122.0535 | -121.7285 | 0.10071 | -0.013122 | 0.020031 | 0.068199 | 0.0062763 | 0.06808 | 0.00037606 | 0.00047844 | -0.0040437 | -0.0045545 | 0.064352 | 0.064749 | 0.0040461 | -0.0096152 | -0.004578 | -120.813 | -24.8108 | -121.5729 | 0.13733 | -121.8063 | -121.6919 | -121.9849 | -19.3405 | -121.9025 | 0.050354 | 0.086975 | -121.8704 | -121.9849 | -0.077819 | 0.036621 | 0.036621 | 0.91553 | 0.15564 | 0.11902 | -0.10529 | -0.14191 | -0.25635 | -0.050354 | -0.25635 | -0.17395 | 0.082397 | -0.013733 | 121.8658 | 121.7239 | 96.9177 | -121.7926 | 121.7789 | 121.8155 | 102.388 | -122.0856
1255.4375 | 121.962 | -121.756 | 0.12817 | -0.0054933 | 0.017041 | 0.068626 | 0.0028583 | 0.066157 | 0.0018713 | -0.0012306 | -0.0040437 | -0.0045545 | 0.062643 | 0.069449 | 0.0063959 | -0.007479 | -0.004578 | -120.8267 | -24.8428 | -121.5912 | 0.15106 | -121.8063 | -121.6736 | -122.0261 | -18.663 | -121.9299 | 0.054932 | 0.091553 | -121.8292 | -121.9986 | -0.050354 | 0.082397 | 0.022888 | 0.92926 | 0.16479 | 0.082397 | -0.13275 | -0.073243 | -0.24262 | -0.073242 | -0.27008 | -0.17395 | 0.068664 | -0.036621 | 121.907 | 121.7514 | 96.9131 | -121.8018 | 121.8109 | 121.8475 | 103.093 | -122.1268
1257.1094 | 122.0352 | -121.7285 | 0.10986 | -0.013122 | 0.013196 | 0.069695 | 0.0056355 | 0.068934 | -0.0077417 | -0.0022986 | -0.0040437 | -0.0073315 | 0.062002 | 0.064536 | 0.0014825 | -0.005129 | 0.004578 | -120.7306 | -24.9023 | -121.5317 | 0.10529 | -121.7697 | -121.6415 | -121.9849 | -19.3451 | -121.8246 | 0.027466 | 0.064087 | -121.8292 | -121.9482 | -0.041198 | 0.086975 | -0.004577 | 0.99792 | 0.19684 | 0.10986 | -0.10529 | -0.10071 | -0.21973 | -0.082397 | -0.25635 | -0.09613 | 0.1236 | -0.045776 | 121.8338 | 121.7331 | 96.8262 | -121.7514 | 121.756 | 121.7926 | 102.3834 | -122.0581
1258.8438 | 121.9528 | -121.7514 | 0.13733 | -0.0054933 | 0.013409 | 0.068413 | 0.0060627 | 0.06338 | -0.0030419 | -0.0025122 | -0.011673 | -0.0083997 | 0.063925 | 0.063467 | 0.0049005 | -0.00577 | 0.009155 | -120.7306 | -24.2386 | -121.5408 | 0.12817 | -121.7926 | -121.6324 | -121.9986 | -19.7571 | -121.8292 | 0.013733 | 0.059509 | -121.8521 | -121.9711 | -0.041199 | 0.11902 | -0.009155 | 1.0208 | 0.21057 | 0.091552 | -0.12817 | -0.10071 | -0.21973 | -0.1236 | -0.24719 | -0.07782 | 0.14191 | -0.07782 | 121.8796 | 121.7606 | 97.5128 | -121.7697 | 121.7651 | 121.8109 | 101.9943 | -122.1085
1260.5781 | 121.907 | -121.7514 | 0.13733 | -0.020752 | 0.012982 | 0.071403 | 0.0028583 | 0.066371 | 0.00016226 | -0.0035804 | -0.019302 | -0.0066907 | 0.062429 | 0.063895 | 0.0044733 | -0.0061972 | 0.091553 | -120.6985 | -24.5361 | -121.5179 | 0.091553 | -121.788 | -121.6232 | -121.9208 | -19.1299 | -121.8246 | 0 | 0.050354 | -121.8018 | -121.962 | -0.036621 | 0.12817 | -0.045776 | 1.0529 | 0.23346 | 0.10529 | -0.045776 | -0.050354 | -0.21057 | -0.13733 | -0.16937 | -0.073242 | 0.13733 | -0.086975 | 121.843 | 121.843 | 97.2153 | -121.7606 | 121.7514 | 121.8018 | 102.6215 | -122.0993
1262.3125 | 122.0169 | -121.7606 | 0.12817 | -0.0054933 | 0.012127 | 0.06884 | 0.0030719 | 0.065943 | -0.0034691 | -0.0050758 | -0.0040437 | -0.0058361 | 0.062002 | 0.063467 | 0.0027643 | -0.0059836 | 0.009155 | -120.7535 | -24.1379 | -121.5363 | 0.10986 | -121.788 | -121.6644 | -121.9482 | -18.7408 | -121.8338 | 0.013733 | 0.059509 | -121.8018 | -121.9482 | -0.027466 | 0.09613 | -0.018311 | 1.0071 | 0.2243 | 0.12817 | -0.11902 | -0.041199 | -0.18768 | -0.11444 | -0.18768 | -0.073242 | 0.11444 | -0.068665 | 121.8704 | 121.7697 | 97.6227 | -121.7926 | 121.7743 | 121.8201 | 103.0197 | -122.0764
1263.9844 | 122.049 | -121.7468 | 0.11902 | -0.013122 | 0.016613 | 0.070763 | 0.0064899 | 0.064662 | 0.0014441 | -0.0059302 | -0.0040437 | -0.0024183 | 0.063925 | 0.067099 | 0.0016963 | -0.011111 | 0.022888 | -120.8313 | -23.9319 | -121.5775 | 0.13733 | -121.8338 | -121.7102 | -122.0078 | -18.5806 | -121.9208 | 0.059509 | 0.091553 | -121.8613 | -121.9666 | -0.086975 | 0.036621 | 0.01831 | 0.91553 | 0.16937 | 0.13275 | -0.096131 | -0.11444 | -0.21973 | -0.05951 | -0.26093 | -0.17395 | 0.045777 | -0.027466 | 121.8842 | 121.7697 | 97.8149 | -121.8292 | 121.8063 | 121.8384 | 103.1662 | -122.0856
1265.7188 | 122.0123 | -121.7422 | 0.10071 | -0.0054933 | 0.018963 | 0.068626 | 0.0041401 | 0.068934 | -0.00026494 | -0.0035804 | -0.011673 | -0.0032727 | 0.062856 | 0.064749 | 0.0029779 | -0.010683 | 0.10071 | -120.6985 | -23.2269 | -121.4951 | 0.07782 | -121.7789 | -121.6461 | -121.9254 | -18.8324 | -121.8201 | 0.036621 | 0.054932 | -121.8109 | -121.9666 | -0.036621 | 0.096131 | -0.022888 | 1.0437 | 0.24719 | 0.15106 | 0 | -0.068664 | -0.2243 | -0.064087 | -0.1831 | -0.077819 | 0.14648 | -0.045776 | 121.8201 | 121.843 | 98.5153 | -121.7468 | 121.7789 | 121.7972 | 102.9099 | -122.0673
1267.4531 | 122.0535 | -121.7285 | 0.10529 | -0.020752 | 0.016827 | 0.068199 | 0.0060627 | 0.064448 | 0.0022987 | -0.0016578 | -0.011673 | -0.00070932 | 0.061575 | 0.06539 | 0.0051141 | -0.0094016 | -0.004578 | -120.8496 | -22.9889 | -121.5866 | 0.12817 | -121.843 | -121.6919 | -121.9757 | -18.1229 | -121.9437 | 0.064087 | 0.10071 | -121.843 | -121.9803 | -0.11444 | 0.036621 | 0.022888 | 0.87891 | 0.14191 | 0.10529 | -0.10986 | -0.11444 | -0.25177 | -0.041199 | -0.24719 | -0.21515 | 0.036621 | -0.004578 | 121.8567 | 121.7239 | 98.7396 | -121.7972 | 121.7926 | 121.8292 | 103.6057 | -122.0856
1269.1875 | 122.0078 | -121.7331 | 0.12817 | -0.013122 | 0.018536 | 0.067772 | 0.0052081 | 0.067011 | 0.0042213 | 0.0028284 | 0.0035858 | -0.0049817 | 0.063711 | 0.06539 | 0.0068231 | -0.0089742 | 0.082397 | -120.7626 | -23.0438 | -121.55 | 0.12817 | -121.8155 | -121.6644 | -121.9162 | -18.1732 | -121.8842 | 0.032043 | 0.059509 | -121.8292 | -121.9757 | -0.082398 | 0.068664 | 0 | 0.97046 | 0.1831 | 0.11444 | -0.045777 | -0.096131 | -0.24262 | -0.096131 | -0.18311 | -0.15106 | 0.091553 | -0.068665 | 121.8613 | 121.8155 | 98.6893 | -121.7926 | 121.7651 | 121.7926 | 103.5599 | -122.1039
1270.9531 | 121.9666 | -121.7697 | 0.1236 | -0.0054933 | 0.017895 | 0.067772 | 0.0047809 | 0.067011 | 0.0027259 | -0.0027258 | -0.0040437 | -0.0024183 | 0.063284 | 0.066458 | 0.0044733 | -0.005129 | -0.004578 | -120.8267 | -24.2706 | -121.5958 | 0.15106 | -121.8201 | -121.701 | -121.9391 | -18.1 | -121.9345 | 0.036621 | 0.086975 | -121.8567 | -121.9986 | -0.050354 | 0.068664 | 0.027466 | 0.94299 | 0.17395 | 0.10529 | -0.12817 | -0.086975 | -0.22888 | -0.086975 | -0.16937 | -0.1648 | 0.064087 | -0.036621 | 121.9208 | 121.7651 | 97.4991 | -121.8246 | 121.8063 | 121.8567 | 103.6697 | -122.1222
1272.6406 | 122.0306 | -121.7285 | 0.11902 | -0.013122 | 0.015973 | 0.070549 | 0.0069171 | 0.06573 | -0.0047509 | -0.0018714 | -0.019302 | -0.0069043 | 0.063925 | 0.063681 | 0.00041446 | -0.0089742 | 0.064087 | -120.6619 | -24.0784 | -121.4813 | 0.09613 | -121.7834 | -121.6507 | -121.8658 | -17.72 | -121.7834 | -0.004578 | 0.027466 | -121.8063 | -121.9437 | -0.054931 | 0.07782 | -0.022889 | 1.0666 | 0.24719 | 0.16937 | -0.054932 | -0.077819 | -0.21515 | -0.1236 | -0.13733 | -0.054931 | 0.16022 | -0.091553 | 121.8246 | 121.7926 | 97.6501 | -121.7697 | 121.7239 | 121.756 | 104.0085 | -122.0627
1274.3906 | 122.0627 | -121.7148 | 0.10986 | -0.013122 | 0.018536 | 0.070976 | 0.0079853 | 0.066798 | 0.0016577 | -0.00058956 | -0.011673 | -0.0032727 | 0.063925 | 0.066885 | 0.0042597 | -0.0089742 | 0.009155 | -120.7809 | -23.877 | -121.5363 | 0.15564 | -121.8018 | -121.6736 | -121.9254 | -17.5552 | -121.8704 | 0.045776 | 0.091553 | -121.8246 | -121.9894 | -0.086975 | 0.041199 | 0.045777 | 0.93384 | 0.17853 | 0.13733 | -0.10071 | -0.10986 | -0.27466 | -0.064087 | -0.21057 | -0.15564 | 0.11902 | -0.01831 | 121.8704 | 121.7239 | 97.8378 | -121.7834 | 121.7606 | 121.8063 | 104.1595 | -122.0993
1276.0625 | 121.9986 | -121.7194 | 0.11902 | -0.013122 | 0.017895 | 0.066917 | 0.0032855 | 0.068507 | 0.0031531 | 0.00047844 | -0.011673 | -0.0022045 | 0.064779 | 0.064963 | 0.0072505 | -0.0066244 | 0.045776 | -120.7489 | -23.2452 | -121.5363 | 0.13733 | -121.7926 | -121.669 | -121.8842 | -16.6443 | -121.8567 | 0.032043 | 0.073242 | -121.8155 | -121.962 | -0.073243 | 0.050354 | 0.01831 | 0.97046 | 0.1831 | 0.13275 | -0.073243 | -0.096131 | -0.24262 | -0.086976 | -0.1648 | -0.13733 | 0.10529 | -0.045777 | 121.8567 | 121.7651 | 98.4741 | -121.788 | 121.7514 | 121.7926 | 105.0751 | -122.081
1277.8125 | 122.0261 | -121.7194 | 0.11444 | -0.020752 | 0.015118 | 0.069054 | 0.0045673 | 0.067225 | -0.00026494 | -0.0010168 | -0.011673 | -0.0028455 | 0.061361 | 0.067099 | 0.0027643 | -0.0066244 | -0.027466 | -120.7993 | -23.3871 | -121.5729 | 0.13275 | -121.7926 | -121.6782 | -121.9757 | -16.2827 | -121.907 | 0.064087 | 0.07782 | -121.8292 | -121.9803 | -0.073243 | 0.041198 | 0.01831 | 0.9201 | 0.14648 | 0.10529 | -0.14191 | -0.10986 | -0.26093 | -0.050354 | -0.25635 | -0.18768 | 0.073243 | -0.036621 | 121.8521 | 121.6919 | 98.3322 | -121.7926 | 121.7834 | 121.7972 | 105.4367 | -122.0947
1279.5625 | 121.994 | -121.7239 | 0.09613 | -0.020752 | 0.0164 | 0.070763 | 0.0079853 | 0.066584 | -0.0047509 | -0.0031532 | -0.019302 | -0.0071179 | 0.062643 | 0.065176 | 0.0027643 | -0.0081198 | 0.064087 | -120.6573 | -23.2773 | -121.4859 | 0.10986 | -121.7834 | -121.6187 | -121.8979 | -15.8249 | -121.7697 | 0.022888 | 0.045776 | -121.7834 | -121.9482 | -0.059509 | 0.10529 | 0.013733 | 1.0666 | 0.23804 | 0.13275 | -0.032043 | -0.059509 | -0.2243 | -0.073242 | -0.17395 | -0.045776 | 0.17853 | -0.050354 | 121.8338 | 121.788 | 98.4467 | -121.7148 | 121.7468 | 121.7697 | 105.899 | -122.0444
1281.2969 | 121.9803 | -121.7285 | 0.1236 | -0.0054933 | 0.0164 | 0.069267 | 0.0015765 | 0.064875 | 0.0027259 | -0.0016578 | -0.011673 | -0.0034863 | 0.061575 | 0.067953 | 0.0042597 | -0.0096152 | 0.013733 | -120.7764 | -23.2681 | -121.5591 | 0.12817 | -121.7834 | -121.6644 | -121.8887 | -15.6784 | -121.8155 | 0.022888 | 0.036621 | -121.7926 | -121.9254 | -0.054931 | 0.064087 | 0.004578 | 0.95215 | 0.16937 | 0.10529 | -0.10986 | -0.064087 | -0.19684 | -0.10071 | -0.16022 | -0.086975 | 0.10986 | -0.086975 | 121.8567 | 121.7422 | 98.4604 | -121.788 | 121.7514 | 121.7651 | 106.0501 | -122.049
1282.9844 | 121.8933 | -121.7285 | 0.13733 | -0.0054933 | 0.016186 | 0.06884 | 0.0062763 | 0.067866 | 0.0012305 | -0.0022986 | -0.019302 | -0.0073315 | 0.062216 | 0.06774 | 0.0036189 | -0.010042 | 0.10986 | -120.6757 | -23.465 | -121.4767 | 0.073242 | -121.756 | -121.6278 | -121.8384 | -15.6921 | -121.7972 | -0.004578 | 0.068665 | -121.7514 | -121.9254 | -0.027465 | 0.10071 | -0.064087 | 1.0529 | 0.25177 | 0.15106 | -0.027466 | -0.022888 | -0.19684 | -0.14191 | -0.10986 | -0.068664 | 0.12817 | -0.068664 | 121.8018 | 121.8384 | 98.2635 | -121.7651 | 121.7239 | 121.7972 | 106.0364 | -122.0627
1284.7344 | 121.8155 | -120.8679 | 0.79651 | 0.0021362 | 0.019818 | 0.070549 | 0.0041401 | 0.064875 | 0.0029395 | 0.00047844 | -0.0040437 | -0.0030591 | 0.061361 | 0.064963 | 0.0076777 | -0.0094016 | 0.5722 | -120.0577 | -23.1033 | -120.8176 | 0.6546 | -120.9595 | -120.8176 | -121.1014 | -15.0055 | -120.7993 | 0.64087 | 0.69122 | -120.9229 | -121.1334 | -0.091553 | 0.050354 | -0.14191 | 0.81024 | 0.050354 | 0 | -0.2243 | -0.054932 | -0.2655 | -0.15564 | -0.23346 | 0.068665 | 0.33417 | -0.10529 | 121.5225 | 121.4401 | 97.7646 | -121.6141 | 121.5088 | 121.5591 | 105.8624 | -121.9299
1286.4844 | 121.4813 | -9.1187 | 112.5916 | -0.0054933 | 0.017895 | 0.06884 | 0.0037127 | 0.06573 | 0.00037606 | -0.0018714 | -0.011673 | -0.0041271 | 0.063284 | 0.061758 | 0.0049005 | -0.0091878 | 112.3672 | -8.9447 | 15.8798 | -9.0363 | 112.5412 | -9.0408 | -9.1187 | -9.0637 | 8.0566 | -9.3109 | 112.4496 | 112.5 | -9.0683 | -9.1461 | 0.077819 | 0 | -0.050354 | 0.17395 | 0.082397 | 0.082397 | -0.2243 | 0.050354 | -0.027466 | -0.14191 | 0.054931 | -0.19226 | -0.16479 | -0.091553 | 121.6599 | 121.4859 | 24.9985 | -121.7102 | 121.5683 | 121.6187 | 17.1753 | -121.7377
1288.2344 | 121.6873 | -8.7753 | 112.9669 | -0.013122 | 0.020672 | 0.06884 | 0.0075581 | 0.06808 | 0.0016577 | -0.0018714 | -0.011673 | -0.0034863 | 0.061788 | 0.064536 | 0.0044733 | -0.0070516 | 112.7792 | -8.5739 | 15.4175 | -8.7067 | 112.9211 | -8.7158 | -8.7753 | -8.9127 | 8.107 | -9.3658 | 112.4908 | 112.4908 | -9.1324 | -9.2468 | 0.05951 | 0 | -0.045776 | 0.20142 | 0.068665 | 0.068665 | -0.18768 | -0.35705 | -0.4715 | -0.47607 | -0.13733 | -0.59051 | -0.11902 | -0.47607 | 121.6965 | 121.5546 | 24.1928 | -121.7422 | 121.2662 | 121.2662 | 16.8823 | -122.2137
1289.9219 | 121.7194 | -9.2148 | 112.5229 | -0.013122 | 0.017254 | 0.069908 | 0.0037127 | 0.065089 | 0.0016577 | -0.0018714 | -0.019302 | -0.0054089 | 0.060934 | 0.061972 | 0.0040461 | -0.0066244 | 112.3444 | -9.0637 | 15.1611 | -9.137 | 112.4634 | -9.1873 | -9.2422 | -9.1049 | 7.2006 | -9.3567 | 112.3489 | 112.4359 | -9.1873 | -9.2606 | 0.027466 | -0.027466 | -0.059509 | 0.15106 | 0.07782 | 0.10529 | -0.17853 | 0.027466 | -0.045776 | -0.17395 | 0.10986 | -0.14191 | -0.09613 | -0.086975 | 121.6782 | 121.5591 | 24.3759 | -121.7651 | 121.5637 | 121.6507 | 16.4154 | -121.7834
1291.6719 | 121.6919 | -8.8806 | 112.8845 | -0.0054933 | 0.014905 | 0.072258 | 0.0049945 | 0.063807 | -0.0024011 | -0.0018714 | -0.011673 | -0.0054089 | 0.060079 | 0.061972 | 0.0023371 | -0.0089742 | 112.8067 | -8.5419 | 15.2023 | -8.7067 | 112.8159 | -8.7708 | -8.8394 | -8.7112 | 7.0312 | -8.931 | 112.7426 | 112.8708 | -8.7891 | -8.8669 | 0.10986 | 0.041198 | -0.068664 | 0.33875 | 0.17395 | 0.13275 | -0.077819 | 0.091553 | 0.013733 | -0.14191 | 0.16937 | -0.050354 | -0.064087 | -0.013732 | 121.6965 | 121.6873 | 24.0829 | -121.7239 | 121.6232 | 121.7514 | 15.9119 | -121.7514
1293.4219 | 121.8796 | -8.6472 | 113.0859 | 0.0021362 | 0.0211 | 0.069054 | 0.0071307 | 0.064448 | 0.0020849 | -0.003794 | 0.0035858 | -0.0030591 | 0.061575 | 0.064108 | 0.0040461 | -0.011324 | 112.9578 | -8.4961 | 15.3214 | -8.5785 | 113.0951 | -8.6334 | -8.6975 | -8.5739 | 6.8939 | -8.8394 | 112.9898 | 113.0768 | -8.6426 | -8.7662 | 0.013733 | -0.050354 | 0.009156 | 0.15106 | 0.068665 | 0.11902 | -0.12817 | 0.004578 | -0.11902 | -0.09613 | 0.073242 | -0.19226 | -0.073243 | -0.009155 | 121.7422 | 121.6049 | 23.9685 | -121.7834 | 121.637 | 121.7239 | 15.5411 | -121.8521
1295.1562 | 121.7972 | -9.2514 | 112.4771 | -0.0054933 | 0.017468 | 0.067986 | 0.0020039 | 0.062739 | -0.0017603 | -0.0010168 | 0.0035858 | -0.0043409 | 0.061148 | 0.062827 | 0.0066095 | -0.0089742 | 112.4084 | -8.9996 | 14.7766 | -9.1324 | 112.4176 | -9.2194 | -9.2834 | -9.1049 | 6.6833 | -9.3842 | 112.3489 | 112.4588 | -9.2422 | -9.3018 | 0.032044 | -0.032043 | -0.059509 | 0.25177 | 0.11902 | 0.15106 | -0.068665 | 0.009155 | -0.050354 | -0.12817 | 0.14649 | -0.13275 | -0.082397 | -0.018311 | 121.669 | 121.6599 | 24.028 | -121.7606 | 121.6003 | 121.7102 | 15.9348 | -121.7789
1296.9062 | 121.8155 | -9.3063 | 112.4634 | -0.0054933 | 0.018963 | 0.068199 | 0.0017901 | 0.064234 | -0.00026494 | -0.0018714 | -0.019302 | -0.0045545 | 0.06072 | 0.06304 | 0.0066095 | -0.0081198 | 112.3077 | -9.1507 | 14.0396 | -9.2789 | 112.3627 | -9.3155 | -9.3567 | -9.1919 | 6.5369 | -9.4391 | 112.2849 | 112.3672 | -9.2834 | -9.3842 | -0.009156 | -0.050354 | -0.10071 | 0.15564 | 0.027465 | 0.077819 | -0.15564 | 0.022888 | -0.07782 | -0.17853 | 0.11444 | -0.13275 | -0.054932 | -0.09613 | 121.669 | 121.6141 | 23.3459 | -121.8201 | 121.5912 | 121.6736 | 15.8432 | -121.8475
1298.5938 | 121.8384 | -8.8486 | 112.9028 | -0.013122 | 0.018963 | 0.07119 | 0.0075581 | 0.066157 | -0.0015465 | -0.0035804 | -0.0040437 | -0.0032727 | 0.064565 | 0.063467 | 0.00041446 | -0.0079062 | 112.7426 | -8.67 | 14.8453 | -8.7845 | 112.8571 | -8.8623 | -8.9035 | -8.844 | 6.7337 | -9.0775 | 112.7701 | 112.8571 | -8.9035 | -8.9767 | -0.013733 | -0.054931 | -0.045776 | 0.17853 | 0.064087 | 0.11902 | -0.16022 | -0.054931 | -0.12817 | -0.13275 | 0.004578 | -0.22888 | -0.10071 | -0.045776 | 121.7056 | 121.5912 | 23.6938 | -121.8063 | 121.6187 | 121.7056 | 15.5823 | -121.8796
1300.3438 | 121.8246 | -8.3817 | 113.4064 | -0.013122 | 0.017254 | 0.069481 | 0.0030719 | 0.064662 | -0.00026494 | -0.0018714 | -0.0040437 | -0.0034863 | 0.061575 | 0.062827 | 0.0057551 | -0.0089742 | 113.2462 | -8.2123 | 14.3875 | -8.3084 | 113.4064 | -8.3588 | -8.4412 | -8.2809 | 6.7474 | -8.5785 | 113.3011 | 113.3652 | -8.3954 | -8.4549 | 0.022888 | -0.059509 | 0 | 0.16937 | 0.073242 | 0.13275 | -0.16022 | -0.013733 | -0.073242 | -0.10529 | 0.10071 | -0.19684 | -0.1236 | -0.041199 | 121.788 | 121.6278 | 22.7692 | -121.8475 | 121.6827 | 121.7468 | 15.1291 | -121.8613
1302.0625 | 121.7743 | -8.8989 | 112.9211 | -0.013122 | 0.012555 | 0.071403 | 0.0011493 | 0.061457 | -0.0036829 | -0.0027258 | -0.011673 | -0.0077587 | 0.059866 | 0.061758 | 0.0046869 | -0.007479 | 112.8067 | -8.6105 | 14.241 | -8.7662 | 112.7975 | -8.8531 | -8.9127 | -8.7433 | 7.4799 | -9.0042 | 112.7197 | 112.8433 | -8.876 | -8.9447 | 0.045777 | -0.013733 | -0.1236 | 0.28839 | 0.13275 | 0.14649 | -0.11444 | 0.022888 | -0.045776 | -0.20142 | 0.15564 | -0.10529 | -0.059509 | -0.07782 | 121.6965 | 121.7056 | 23.14 | -121.8338 | 121.6187 | 121.7422 | 16.3788 | -121.8658
1303.7656 | 121.9162 | -8.1116 | 113.6261 | 0.0021362 | 0.014905 | 0.070976 | 0.0075581 | 0.064875 | -0.0058191 | -0.0040076 | -0.011673 | -0.0069043 | 0.060293 | 0.062827 | 0.00020086 | -0.0091878 | 113.5117 | -7.8781 | 14.6484 | -8.0063 | 113.6261 | -8.0978 | -8.1848 | -8.0109 | 7.5943 | -8.2214 | 113.5162 | 113.6078 | -8.1253 | -8.194 | 0.013733 | -0.073242 | 0 | 0.23346 | 0.10529 | 0.17853 | -0.11444 | -0.013733 | -0.082398 | -0.10986 | 0.10071 | -0.10986 | -0.027466 | -0.018311 | 121.7377 | 121.6232 | 22.76 | -121.8109 | 121.6278 | 121.7194 | 15.7059 | -121.8201
1305.4531 | 121.9574 | -8.4457 | 113.2874 | -0.020752 | 0.019391 | 0.066917 | 0.0069171 | 0.062953 | 0.00080326 | -0.0052894 | 0.0035858 | -0.0024183 | 0.063284 | 0.065817 | 0.0036189 | -0.0096152 | 113.1683 | -8.3176 | 15.1703 | -8.3908 | 113.2919 | -8.4595 | -8.5327 | -8.3725 | 7.4982 | -8.67 | 113.2553 | 113.2828 | -8.4961 | -8.5419 | -0.013733 | -0.086975 | 0.004577 | 0.12817 | 0.054932 | 0.14191 | -0.11902 | -0.050354 | -0.09613 | -0.032044 | 0.073242 | -0.2243 | -0.12817 | -0.004578 | 121.7377 | 121.6141 | 23.616 | -121.8201 | 121.701 | 121.7285 | 15.9439 | -121.8292
1307.1562 | 121.907 | -8.8852 | 112.8616 | -0.013122 | 0.020031 | 0.071617 | 0.0079853 | 0.064662 | -0.0030419 | -0.0040076 | -0.011673 | -0.0026319 | 0.065847 | 0.066031 | 0.0010553 | -0.0096152 | 112.7289 | -8.7387 | 16.0721 | -8.8531 | 112.8479 | -8.9035 | -8.9859 | -8.8348 | 7.4387 | -9.1049 | 112.7975 | 112.8983 | -8.931 | -8.9722 | -0.01831 | -0.10071 | -0.013733 | 0.14648 | 0.032044 | 0.13275 | -0.13275 | -0.045776 | -0.086975 | -0.064087 | 0.050354 | -0.21973 | -0.13275 | 0.036621 | 121.7331 | 121.6141 | 24.9573 | -121.8475 | 121.6827 | 121.7834 | 16.3239 | -121.8338
1308.8438 | 121.9345 | -8.2855 | 113.4842 | -0.0054933 | 0.017041 | 0.06884 | 0.0079853 | 0.067439 | -0.0015465 | -0.003794 | -0.0040437 | -0.0026319 | 0.062856 | 0.065817 | 0.0034051 | -0.0098288 | 113.3194 | -8.1253 | 17.0883 | -8.2535 | 113.4659 | -8.2993 | -8.4 | -8.2443 | 7.8415 | -8.519 | 113.3972 | 113.4842 | -8.313 | -8.4 | -0.013733 | -0.11444 | -0.018311 | 0.16022 | 0.032043 | 0.14648 | -0.16479 | -0.027466 | -0.11444 | -0.086975 | 0.041198 | -0.23346 | -0.11902 | 0 | 121.7514 | 121.6049 | 25.3738 | -121.8842 | 121.6827 | 121.7697 | 16.127 | -121.8842
1310.5469 | 121.9666 | -8.931 | 112.8204 | 0.0021362 | 0.012555 | 0.071403 | 0.0049945 | 0.063166 | -0.0047509 | -0.0050758 | -0.019302 | -0.0047681 | 0.061575 | 0.063467 | 0.00020086 | -0.0083334 | 112.7106 | -8.6838 | 17.5369 | -8.8531 | 112.7701 | -8.9264 | -8.9996 | -8.8165 | 7.9651 | -9.05 | 112.6968 | 112.8021 | -8.9584 | -9.0317 | 0.004577 | -0.068665 | -0.050354 | 0.24719 | 0.07782 | 0.14649 | -0.10986 | -0.027466 | -0.10071 | -0.1236 | 0.11444 | -0.11902 | -0.018311 | -0.018311 | 121.7011 | 121.6415 | 26.4679 | -121.8201 | 121.6278 | 121.7331 | 16.8961 | -121.8521
1312.2344 | 121.8658 | -8.6197 | 113.1821 | 0.0097657 | 0.0164 | 0.067986 | 0.0013629 | 0.065302 | 0.0010169 | -0.0027258 | -0.019302 | -0.0030591 | 0.06072 | 0.064963 | 0.0053279 | -0.010256 | 113.0585 | -8.4091 | 17.7246 | -8.5419 | 113.1363 | -8.5831 | -8.6792 | -8.4366 | 8.1161 | -8.7479 | 113.0676 | 113.1546 | -8.606 | -8.6563 | 0.036621 | -0.059509 | -0.045776 | 0.21057 | 0.07782 | 0.13733 | -0.1236 | 0.013733 | -0.036621 | -0.11444 | 0.18311 | -0.12817 | -0.091553 | -0.027466 | 121.756 | 121.6782 | 26.3443 | -121.8613 | 121.6873 | 121.7743 | 16.7358 | -121.8384
1313.9375 | 121.8704 | -8.9539 | 112.8708 | -0.013122 | 0.017041 | 0.070976 | 0.0015765 | 0.062312 | 0.0018713 | -0.002085 | -0.0040437 | -0.0013501 | 0.064138 | 0.064536 | 0.0046869 | -0.010042 | 112.6785 | -8.812 | 17.3355 | -8.9127 | 112.8342 | -8.9584 | -9.0454 | -8.8898 | 8.3908 | -9.2011 | 112.7701 | 112.825 | -8.9722 | -9.0317 | -0.004578 | -0.091553 | -0.036622 | 0.14191 | 0.041198 | 0.13275 | -0.19226 | -0.018311 | -0.07782 | -0.10071 | 0.064086 | -0.24719 | -0.16937 | -0.045777 | 121.788 | 121.6324 | 26.2894 | -121.9162 | 121.7239 | 121.7789 | 17.3447 | -121.9025
1315.6094 | 121.8658 | -8.9722 | 112.8662 | 0.0021362 | 0.018963 | 0.067558 | 0.0041401 | 0.062098 | 0.0020849 | -0.0014442 | 0.0035858 | -0.0017773 | 0.063497 | 0.064963 | 0.0063959 | -0.0081198 | 112.674 | -8.7845 | 16.8732 | -8.9035 | 112.8342 | -8.9355 | -9.0317 | -8.8577 | 8.7112 | -9.1782 | 112.7563 | 112.8342 | -8.9447 | -9.0317 | 0.036621 | -0.059509 | -0.032044 | 0.18768 | 0.068665 | 0.12817 | -0.19226 | 0.027466 | -0.059509 | -0.10986 | 0.11444 | -0.20599 | -0.14649 | -0.032044 | 121.8063 | 121.6461 | 25.8453 | -121.8979 | 121.7285 | 121.8063 | 17.6834 | -121.8979
1317.2812 | 121.907 | -8.5281 | 113.2507 | -0.013122 | 0.012768 | 0.069695 | 0.0041401 | 0.06573 | -0.0058191 | -0.0046484 | -0.011673 | -0.0062635 | 0.064565 | 0.062613 | 0.00084166 | -0.00577 | 113.0859 | -8.3267 | 19.0659 | -8.4595 | 113.2095 | -8.5327 | -8.606 | -8.4229 | 9.1232 | -8.6472 | 113.1271 | 113.2416 | -8.5419 | -8.6014 | -0.004578 | -0.07782 | -0.041198 | 0.20142 | 0.068664 | 0.14648 | -0.16479 | -0.013733 | -0.073242 | -0.1236 | 0.10528 | -0.11902 | -0.045777 | -0.009155 | 121.7377 | 121.6141 | 27.594 | -121.8567 | 121.6553 | 121.7697 | 17.6514 | -121.8521
1318.9688 | 121.9711 | -8.725 | 113.0493 | 0.0021362 | 0.018963 | 0.069695 | 0.0081989 | 0.063593 | -0.00069214 | -0.0022986 | -0.019302 | 0.00014528 | 0.065847 | 0.064963 | 0.0014825 | -0.010256 | 112.8708 | -8.6243 | 18.782 | -8.7112 | 113.0539 | -8.7708 | -8.8577 | -8.7204 | 9.3658 | -8.9813 | 112.9532 | 113.0585 | -8.7891 | -8.8165 | -0.045776 | -0.13275 | 0.004578 | 0.10071 | 0.013733 | 0.14648 | -0.17853 | -0.064086 | -0.091552 | -0.09613 | 0.004578 | -0.25635 | -0.16479 | 0.009156 | 121.7789 | 121.5958 | 27.507 | -121.907 | 121.6782 | 121.7834 | 18.0908 | -121.8658
1320.6406 | 121.9666 | -9.05 | 112.7563 | -0.0054933 | 0.018322 | 0.069695 | 0.0081989 | 0.064662 | -0.00090574 | -0.0010168 | -0.019302 | -0.0024183 | 0.06542 | 0.063895 | 0.0025507 | -0.0089742 | 112.5595 | -8.9493 | 18.2785 | -9.0271 | 112.7518 | -9.0866 | -9.1461 | -9.0271 | 9.7229 | -9.3292 | 112.6328 | 112.7197 | -9.1232 | -9.1827 | -0.036621 | -0.09613 | -0.004578 | 0.10071 | 0.022888 | 0.11902 | -0.19684 | -0.073242 | -0.13275 | -0.1236 | 0.022888 | -0.27924 | -0.14649 | -0.036621 | 121.8018 | 121.6095 | 27.3285 | -121.9025 | 121.6827 | 121.7697 | 18.7729 | -121.9391
1322.3281 | 121.9803 | -8.6929 | 113.0676 | -0.013122 | 0.014264 | 0.070335 | 0.0084125 | 0.062312 | -0.0049645 | -0.0031532 | -0.011673 | -0.0066907 | 0.062429 | 0.060477 | 0.0014825 | -0.0070516 | 112.9852 | -8.432 | 19.6838 | -8.5922 | 113.0447 | -8.67 | -8.7524 | -8.5556 | 10.7437 | -8.7753 | 112.9532 | 113.0539 | -8.7204 | -8.7708 | 0.022888 | -0.059509 | -0.022888 | 0.26093 | 0.10071 | 0.16022 | -0.082398 | -0.027466 | -0.07782 | -0.11444 | 0.13733 | -0.082398 | -0.004578 | -0.013733 | 121.7377 | 121.6782 | 28.3768 | -121.8201 | 121.6461 | 121.7468 | 19.4366 | -121.8384
1324 | 121.962 | -8.6746 | 113.0722 | -0.0054933 | 0.015332 | 0.070549 | 0.0039265 | 0.064875 | -0.0028283 | -0.003794 | -0.0040437 | -0.0032727 | 0.064352 | 0.06304 | 0.00020086 | -0.011751 | 113.0127 | -8.4366 | 18.3929 | -8.5831 | 113.0447 | -8.6884 | -8.7387 | -8.5556 | 10.9772 | -8.7845 | 112.9486 | 113.0219 | -8.7112 | -8.7708 | -0.013732 | -0.064086 | -0.027466 | 0.23804 | 0.091553 | 0.15564 | -0.05951 | -0.036621 | -0.09613 | -0.1236 | 0.11902 | -0.10986 | -0.013733 | -0.050354 | 121.7194 | 121.6873 | 27.0676 | -121.8109 | 121.6232 | 121.6965 | 19.6518 | -121.843
1325.6875 | 121.9162 | -8.7341 | 113.0402 | -0.013122 | 0.018109 | 0.070122 | 0.0069171 | 0.065089 | -0.0030419 | -0.0014442 | -0.019302 | -0.0049817 | 0.062216 | 0.06539 | 0.0025507 | -0.010256 | 112.9852 | -8.4641 | 18.5257 | -8.6014 | 113.0219 | -8.7112 | -8.7891 | -8.5693 | 10.9406 | -8.8486 | 112.9395 | 112.999 | -8.7433 | -8.7891 | 0.022888 | -0.054931 | -0.01831 | 0.27008 | 0.13275 | 0.18768 | -0.054932 | -0.009155 | -0.054931 | -0.10071 | 0.16479 | -0.11444 | -0.05951 | -0.041199 | 121.756 | 121.7194 | 27.2598 | -121.8292 | 121.6736 | 121.7331 | 19.6747 | -121.8292
1327.4062 | 121.9299 | -14.6896 | 107.1259 | -0.0054933 | 0.018322 | 0.070122 | 0.0058491 | 0.06338 | -0.0017603 | -0.0033668 | -0.019302 | -0.00092292 | 0.064352 | 0.06539 | 0.0025507 | -0.0096152 | 106.9244 | -14.6301 | 17.1936 | -14.7858 | 107.0206 | -14.772 | -14.8178 | -14.7858 | 9.6771 | -15.065 | 106.9519 | 107.0251 | -14.8178 | -14.8544 | -0.082398 | -0.12817 | -0.10529 | 0.059509 | -0.096131 | 0.032043 | -0.20142 | -0.12817 | -0.16479 | -0.17395 | -0.096131 | -0.37537 | -0.21057 | -0.10071 | 121.7102 | 121.6141 | 31.8832 | -121.9437 | 121.6415 | 121.7148 | 24.3668 | -121.9803
1329.0938 | 121.8567 | -12.4008 | 109.4604 | -0.0054933 | 0.014264 | 0.069695 | 0.00093567 | 0.064448 | 0.0029395 | -0.0016578 | -0.0040437 | -0.0054089 | 0.060934 | 0.062827 | 0.0070367 | -0.006838 | 109.4788 | -12.0026 | 17.9077 | -12.1674 | 109.5245 | -12.2177 | -12.2635 | -12.0804 | 10.4141 | -12.3734 | 109.4421 | 109.52 | -12.204 | -12.2818 | 0.18311 | 0.13733 | 0.064087 | 0.39825 | 0.23346 | 0.096131 | 0.018311 | 0.19684 | 0.11902 | -0.01831 | 0.32043 | 0.027466 | -0.091553 | 0.059509 | 121.9254 | 121.8796 | 30.3085 | -121.7239 | 121.843 | 121.9208 | 22.8149 | -121.7422
1330.8594 | 121.843 | -11.3068 | 110.5362 | 0.0021362 | 0.012982 | 0.072044 | 0.0032855 | 0.063807 | -0.0045373 | -0.0046484 | -0.0040437 | -0.0051953 | 0.062429 | 0.061758 | 0.0021235 | -0.0070516 | 110.3577 | -11.1191 | 18.2053 | -11.2564 | 110.4538 | -11.261 | -11.3297 | -11.2198 | 10.8078 | -11.4807 | 110.3943 | 110.463 | -11.2747 | -11.348 | 0.045777 | -0.022888 | -0.082398 | 0.18768 | 0.050354 | 0.073242 | -0.17853 | 0.032044 | -0.041198 | -0.14191 | 0.086975 | -0.17395 | -0.13275 | -0.073242 | 121.7606 | 121.6644 | 29.512 | -121.8658 | 121.7011 | 121.7697 | 22.1146 | -121.8842
1332.5938 | 121.8384 | -11.5036 | 110.3806 | -0.013122 | 0.012768 | 0.069054 | 0.0032855 | 0.065089 | -0.0011193 | -0.0027258 | -0.019302 | -0.0064771 | 0.061361 | 0.062186 | 0.0031915 | -0.0089742 | 110.1883 | -11.3022 | 17.4912 | -11.4166 | 110.3119 | -11.4349 | -11.499 | -11.4395 | 10.849 | -11.7233 | 110.1883 | 110.2844 | -11.4853 | -11.5677 | 0.068664 | 0.004578 | -0.068664 | 0.20142 | 0.086975 | 0.082397 | -0.19226 | 0.01831 | -0.064087 | -0.19226 | 0.064087 | -0.21973 | -0.15564 | -0.09613 | 121.8155 | 121.6919 | 28.9948 | -121.8796 | 121.6919 | 121.788 | 22.3526 | -121.9482
1334.2812 | 121.9254 | -11.2015 | 110.5728 | -0.0054933 | 0.017468 | 0.070976 | 0.0073443 | 0.063593 | -0.00069214 | -0.0035804 | -0.011673 | -0.0039135 | 0.063711 | 0.065176 | 0.0034051 | -0.0089742 | 110.463 | -11.0367 | 17.0151 | -11.2152 | 110.5911 | -11.2106 | -11.2701 | -11.1374 | 11.4532 | -11.4853 | 110.4584 | 110.5225 | -11.3297 | -11.3663 | -0.009155 | -0.068665 | 0.01831 | 0.16479 | -0.013733 | 0.054932 | -0.10986 | -0.12817 | -0.16479 | -0.11444 | 0.064087 | -0.28381 | -0.11902 | -0.050354 | 121.7926 | 121.6644 | 28.2166 | -121.843 | 121.6599 | 121.7239 | 22.6547 | -121.9391
1336.0312 | 121.8521 | -11.1786 | 110.6873 | 0.0021362 | 0.019177 | 0.070976 | 0.0013629 | 0.064662 | 0.0046485 | 5.1244e-05 | -0.0040437 | -0.00049552 | 0.064138 | 0.064536 | 0.0087457 | -0.0089742 | 110.495 | -11.0962 | 17.3676 | -11.1694 | 110.6598 | -11.142 | -11.2244 | -11.0962 | 11.5311 | -11.4716 | 110.5591 | 110.6186 | -11.174 | -11.2518 | 0.036621 | -0.045776 | -0.027466 | 0.082398 | 0.009155 | 0.054931 | -0.19226 | 0.004578 | -0.073242 | -0.12817 | 0.082398 | -0.29297 | -0.21973 | -0.068665 | 121.8384 | 121.6736 | 28.5461 | -121.9116 | 121.7377 | 121.7972 | 22.7097 | -121.9391
1337.7812 | 121.9757 | -11.3388 | 110.4538 | -0.013122 | 0.017682 | 0.070976 | 0.0039265 | 0.06338 | -0.0026147 | -0.0031532 | -0.011673 | -0.0034863 | 0.064565 | 0.063467 | 0.0046869 | -0.0091878 | 110.2982 | -11.2106 | 17.6056 | -11.3251 | 110.5087 | -11.3342 | -11.3983 | -11.2976 | 11.618 | -11.5814 | 110.4263 | 110.4996 | -11.3571 | -11.4029 | 0.004577 | -0.059509 | 0.054932 | 0.12817 | 0.013733 | 0.073242 | -0.15564 | -0.018311 | -0.064087 | -0.027465 | 0.041199 | -0.24262 | -0.17853 | 0.045777 | 121.8475 | 121.637 | 28.9444 | -121.8521 | 121.7651 | 121.8384 | 22.9568 | -121.8567
1339.5312 | 121.8384 | -11.2473 | 110.582 | -0.0054933 | 0.017041 | 0.068626 | 0.0058491 | 0.063593 | 0.0027259 | 0.0017602 | -0.019302 | -0.0019909 | 0.063284 | 0.066031 | 0.0076777 | -0.008547 | 110.3989 | -11.1694 | 17.7658 | -11.2518 | 110.5957 | -11.261 | -11.3068 | -11.2106 | 11.3525 | -11.5356 | 110.4996 | 110.5682 | -11.2747 | -11.3571 | -0.013733 | -0.05951 | 0.013733 | 0.077819 | -0.004578 | 0.054932 | -0.1831 | -0.027466 | -0.10986 | -0.082397 | 0.036621 | -0.28839 | -0.17853 | -0.013733 | 121.843 | 121.6461 | 29.0131 | -121.8887 | 121.7468 | 121.8155 | 22.5998 | -121.9391
1341.2188 | 121.8796 | -11.1832 | 110.6598 | -0.013122 | 0.022381 | 0.066917 | 0.0024311 | 0.066371 | 0.0029395 | 0.00069204 | -0.0040437 | -0.0039135 | 0.064565 | 0.063467 | 0.0076777 | -0.0076926 | 110.4584 | -11.0367 | 17.395 | -11.1465 | 110.6644 | -11.1465 | -11.1832 | -11.142 | 11.412 | -11.4716 | 110.5545 | 110.6186 | -11.2106 | -11.2793 | 0.036622 | 0 | 0.004578 | 0.14648 | 0.036622 | 0.036622 | -0.20142 | -0.027465 | -0.09613 | -0.10529 | 0.041199 | -0.28839 | -0.19226 | -0.041199 | 121.8475 | 121.6415 | 28.5782 | -121.843 | 121.7377 | 121.8018 | 22.5952 | -121.9391
1342.9531 | 121.9666 | -9.6359 | 112.1384 | 0.0021362 | 0.010846 | 0.071403 | 0.0052081 | 0.064234 | -0.0066735 | -0.00058956 | -0.0040437 | -0.0069043 | 0.062429 | 0.061972 | -0.00086734 | -0.0070516 | 112.0239 | -9.4208 | 18.0084 | -9.5489 | 112.1338 | -9.6222 | -9.6909 | -9.5352 | 11.7828 | -9.7641 | 112.0331 | 112.1338 | -9.6359 | -9.7183 | 0.013733 | -0.054932 | -0.004578 | 0.21515 | 0.086975 | 0.14191 | -0.11444 | 0 | -0.082398 | -0.10529 | 0.10071 | -0.12817 | -0.045776 | -0.004578 | 121.7697 | 121.6599 | 27.6443 | -121.8292 | 121.669 | 121.7697 | 21.4188 | -121.8567
1344.7031 | 121.8658 | -9.4711 | 112.3856 | -0.013122 | 0.016827 | 0.06649 | 0.0049945 | 0.065943 | -0.00026494 | 0.00069204 | -0.011673 | -0.0034863 | 0.063497 | 0.065604 | 0.0042597 | -0.0098288 | 112.326 | -9.2102 | 16.4383 | -9.3338 | 112.3306 | -9.3796 | -9.4803 | -9.2468 | 11.7508 | -9.5444 | 112.2757 | 112.3306 | -9.4162 | -9.462 | 0.091552 | -0.009156 | -0.054932 | 0.26093 | 0.13733 | 0.14649 | -0.059509 | 0.054931 | 0.009155 | -0.10986 | 0.2243 | -0.073243 | -0.082398 | -0.054932 | 121.8018 | 121.7972 | 25.9094 | -121.8658 | 121.7468 | 121.8018 | 21.2219 | -121.8475
1346.4531 | 121.8658 | -9.8923 | 111.9781 | -0.0054933 | 0.017254 | 0.069054 | 0.0028583 | 0.064448 | 0.0018713 | -0.0016578 | -0.011673 | -0.00070932 | 0.062216 | 0.064322 | 0.0061823 | -0.0089742 | 111.7996 | -9.7824 | 16.6992 | -9.8328 | 111.9736 | -9.8694 | -9.9335 | -9.787 | 11.5356 | -10.1074 | 111.8774 | 111.9644 | -9.8694 | -9.9518 | 0.022888 | -0.041199 | -0.004577 | 0.10986 | 0.059509 | 0.10071 | -0.17853 | 0.022888 | -0.059509 | -0.10071 | 0.10529 | -0.21515 | -0.15564 | -0.013732 | 121.8658 | 121.6919 | 26.5915 | -121.9116 | 121.7697 | 121.8567 | 21.4279 | -121.9299
1348.1406 | 117.5903 | -7.814 | 109.8175 | -0.013122 | 0.018322 | 0.065422 | 0.0037127 | 0.061244 | 0.0020849 | -0.00058956 | -0.0040437 | -0.0039135 | 0.062216 | 0.061545 | 0.0059687 | -0.0089742 | 109.671 | -7.608 | 17.1158 | -7.7087 | 109.8175 | -7.7408 | -7.8323 | -7.6172 | 12.204 | -7.9056 | 109.7534 | 109.845 | -7.7271 | -7.814 | 0.073242 | -0.01831 | 0 | 0.20599 | 0.10529 | 0.1236 | -0.14648 | 0.086975 | 0 | -0.064087 | 0.19684 | -0.091553 | -0.091553 | 0.027466 | 117.6315 | 117.485 | 24.9298 | -117.6498 | 117.5674 | 117.659 | 20.018 | -117.6315
1349.875 | 116.9998 | -9.7595 | 107.2861 | -0.013122 | 0.018109 | 0.064995 | 0.0052081 | 0.061244 | 0.0022987 | 0.00047844 | -0.019302 | -0.0036999 | 0.062429 | 0.062186 | 0.0070367 | -0.0083334 | 107.1304 | -9.613 | 14.7491 | -9.7 | 107.2815 | -9.7412 | -9.7824 | -9.6725 | 11.1237 | -10.0113 | 107.2266 | 107.2861 | -9.7504 | -9.8282 | 0.01831 | -0.022889 | -0.004578 | 0.14648 | 0.059509 | 0.082398 | -0.15564 | 0.009155 | -0.068665 | -0.05951 | 0.086975 | -0.25177 | -0.18311 | 0 | 117.041 | 116.89 | 24.5087 | -117.0685 | 116.9861 | 117.0456 | 20.8832 | -117.1143
1351.5469 | 116.7206 | -9.5673 | 107.0206 | -0.013122 | 0.013836 | 0.066917 | 0.0067035 | 0.060816 | -0.0053919 | -0.0016578 | -0.011673 | -0.0071179 | 0.06072 | 0.061758 | 0.0012689 | -0.0064108 | 106.8695 | -9.4116 | 15.033 | -9.5261 | 107.0068 | -9.5764 | -9.6405 | -9.4986 | 11.1786 | -9.7275 | 106.8924 | 106.9702 | -9.581 | -9.6497 | -0.009155 | -0.073242 | -0.013733 | 0.15564 | 0.041199 | 0.11444 | -0.15106 | -0.013733 | -0.082397 | -0.12817 | 0.068665 | -0.16022 | -0.07782 | -0.050354 | 116.5741 | 116.4368 | 24.6002 | -116.6611 | 116.4597 | 116.5375 | 20.7459 | -116.6702
1353.2812 | 116.4322 | -9.0866 | 107.1487 | -0.0054933 | 0.017041 | 0.065208 | 0.0060627 | 0.061244 | -0.0015465 | -0.002085 | -0.0040437 | -0.0028455 | 0.060934 | 0.061331 | 0.0040461 | -0.010897 | 107.0297 | -9.0134 | 13.3896 | -9.05 | 107.1579 | -9.1278 | -9.1965 | -8.9722 | 11.1099 | -9.3063 | 107.1259 | 107.1945 | -9.1141 | -9.1827 | -0.041199 | -0.10986 | 0.009155 | 0.073242 | 0.036621 | 0.14648 | -0.11902 | -0.027466 | -0.09613 | -0.022889 | 0.11444 | -0.21973 | -0.1236 | 0.045776 | 116.2445 | 116.1163 | 22.4762 | -116.3452 | 116.2125 | 116.2811 | 20.1965 | -116.3315
1354.9531 | 116.0568 | -9.1461 | 106.9199 | -0.020752 | 0.017895 | 0.06414 | 0.0041401 | 0.063166 | 0.0027259 | 0.00069204 | 0.0035858 | -0.0013501 | 0.060079 | 0.061758 | 0.0076777 | -0.0083334 | 106.7688 | -8.9951 | 13.9938 | -9.0866 | 106.9153 | -9.1278 | -9.2102 | -9.0729 | 10.9131 | -9.4116 | 106.7871 | 106.9016 | -9.1644 | -9.2285 | 0.01831 | -0.064087 | -0.004578 | 0.15106 | 0.059509 | 0.1236 | -0.15106 | -0.018311 | -0.082398 | -0.13275 | 0.073242 | -0.2655 | -0.1831 | -0.018311 | 116.0614 | 115.9149 | 23.14 | -116.1301 | 115.9332 | 116.0477 | 20.0592 | -116.1484
1356.6875 | 115.9012 | -9.137 | 106.6315 | -0.020752 | 0.017041 | 0.066704 | 0.0060627 | 0.064021 | -0.0049645 | -0.0035804 | -0.019302 | -0.0041271 | 0.061575 | 0.06069 | -0.00065374 | -0.0076926 | 106.4987 | -8.9951 | 14.0259 | -9.137 | 106.5262 | -9.2102 | -9.288 | -9.0637 | 11.055 | -9.3338 | 106.485 | 106.5811 | -9.2011 | -9.2743 | -0.073242 | -0.15106 | -0.10529 | 0.14191 | 0 | 0.15106 | -0.13275 | -0.064087 | -0.13733 | -0.14648 | 0.073242 | -0.19684 | -0.059509 | -0.050354 | 115.6631 | 115.6357 | 23.1628 | -115.9195 | 115.6219 | 115.7181 | 20.192 | -115.9058
1358.375 | 115.6998 | -89.6942 | 25.795 | -0.013122 | 0.012341 | 0.064781 | 0.0049945 | 0.061884 | 0.00080326 | -0.0035804 | 0.0035858 | -0.0034863 | 0.059439 | 0.062399 | 0.0063959 | -0.0091878 | 25.9232 | -88.9984 | -13.5223 | -89.5569 | 25.795 | -89.8773 | -89.7125 | -89.534 | -10.73 | -89.8315 | 25.7172 | 25.7355 | -89.8315 | -89.9231 | -0.1831 | -0.01831 | 0 | 0.6958 | 0.13733 | 0.15564 | 0.12817 | -0.13733 | -0.22888 | -0.07782 | 0.16022 | -0.13733 | 0.091553 | -0.059509 | 115.4892 | 115.6174 | 76.1719 | -115.5075 | 115.4114 | 115.4297 | 78.9642 | -115.7181
1360.0469 | 115.6952 | -89.5706 | 25.7172 | -0.013122 | 0.011487 | 0.067772 | 0.0062763 | 0.060816 | -0.0053919 | -0.0029394 | -0.011673 | -0.0047681 | 0.059652 | 0.06069 | 0.00062806 | -0.010256 | 25.8545 | -88.9252 | -13.8336 | -89.4882 | 25.7721 | -89.7675 | -89.6439 | -89.4699 | -10.9131 | -89.7217 | 25.6531 | 25.6989 | -89.7308 | -89.8636 | -0.19684 | -0.073242 | 0.054932 | 0.64545 | 0.082398 | 0.15564 | 0.13733 | -0.16022 | -0.29297 | -0.064087 | 0.10071 | -0.15106 | 0.14191 | -0.01831 | 115.3427 | 115.4251 | 75.737 | -115.361 | 115.2237 | 115.2695 | 78.6575 | -115.5807
1361.7812 | 115.5487 | -89.5569 | 25.6897 | -0.013122 | 0.018536 | 0.066917 | 0.0041401 | 0.062098 | 0.0035803 | -0.0025122 | -0.0040437 | -0.00092292 | 0.060293 | 0.063895 | 0.0081049 | -0.011111 | 25.8179 | -88.9069 | -13.4674 | -89.4653 | 25.7629 | -89.6576 | -89.5889 | -89.4287 | -11.1511 | -89.7675 | 25.6668 | 25.6943 | -89.6393 | -89.8407 | -0.10071 | -0.032043 | 0.073242 | 0.65002 | 0.091553 | 0.1236 | 0.12817 | -0.082397 | -0.28381 | -0.022888 | 0.12817 | -0.21057 | 0.073242 | 0.004578 | 115.3198 | 115.3748 | 76.0895 | -115.2786 | 115.2237 | 115.2512 | 78.4058 | -115.5304
1363.4688 | 115.3473 | -89.4974 | 25.7034 | -0.013122 | 0.013409 | 0.066704 | 0.0030719 | 0.059107 | -0.0032555 | -0.0027258 | -0.0040437 | -0.0054089 | 0.060507 | 0.061972 | 0.0031915 | -0.0076926 | 25.7309 | -88.8199 | -13.9572 | -89.3921 | 25.708 | -89.5569 | -89.4699 | -89.3692 | -11.2335 | -89.6576 | 25.6119 | 25.6393 | -89.5706 | -89.7171 | -0.05951 | 0.027465 | 0.004578 | 0.67749 | 0.10529 | 0.07782 | 0.027466 | -0.073243 | -0.21973 | -0.091553 | 0.12817 | -0.16022 | 0.059509 | -0.064087 | 115.2054 | 115.2283 | 75.5402 | -115.1733 | 115.1093 | 115.1367 | 78.2639 | -115.4205
1365.2188 | 115.2237 | -89.4608 | 25.6668 | -0.013122 | 0.013196 | 0.066063 | 0.0056355 | 0.061671 | -0.0019739 | -0.0048622 | -0.011673 | -0.0062635 | 0.057943 | 0.062399 | 0.0057551 | -0.0072652 | 25.7629 | -88.7329 | -12.4558 | -89.3143 | 25.6668 | -89.4653 | -89.4104 | -89.2868 | -10.4416 | -89.5889 | 25.5615 | 25.589 | -89.4791 | -89.6576 | -0.004578 | 0.050354 | 0 | 0.72784 | 0.14648 | 0.09613 | 0.09613 | -0.018311 | -0.19684 | -0.10529 | 0.17395 | -0.12817 | 0.068665 | -0.07782 | 115.1276 | 115.2237 | 77.005 | -115.0772 | 115.0223 | 115.0497 | 79.0192 | -115.3244
1366.9531 | 115.1733 | -89.4012 | 25.6348 | -0.0054933 | 0.016827 | 0.064995 | 0.0043537 | 0.061671 | -5.1338e-05 | -0.0016578 | -0.011673 | -0.0032727 | 0.057302 | 0.062613 | 0.0068231 | -0.0089742 | 25.7629 | -88.6688 | -12.9181 | -89.2365 | 25.6119 | -89.4196 | -89.3509 | -89.1495 | -10.3455 | -89.4974 | 25.5569 | 25.5569 | -89.4058 | -89.5844 | -0.018311 | 0.050354 | -0.022889 | 0.73242 | 0.16479 | 0.11444 | 0.12817 | -0.004578 | -0.18311 | -0.07782 | 0.25177 | -0.09613 | 0.086976 | -0.07782 | 115.0131 | 115.1642 | 76.4832 | -114.9857 | 114.9582 | 114.9582 | 79.0558 | -115.2191
1368.6406 | 115.2145 | -89.3143 | 25.6073 | 0.0021362 | 0.018963 | 0.065208 | 0.0056355 | 0.062098 | 0.0050757 | 0.00069204 | -0.019302 | -0.00092292 | 0.059652 | 0.06304 | 0.0061823 | -0.0091878 | 25.7126 | -88.7009 | -12.6068 | -89.2319 | 25.6393 | -89.4241 | -89.3326 | -89.1541 | -10.1349 | -89.5615 | 25.5478 | 25.5981 | -89.4241 | -89.5706 | -0.10986 | -0.018311 | 0.032043 | 0.6134 | 0.082397 | 0.10071 | 0.10529 | -0.10986 | -0.25635 | -0.059509 | 0.16022 | -0.24719 | 0.009156 | -0.009155 | 114.9536 | 115.0269 | 76.7075 | -114.9399 | 114.8621 | 114.9124 | 79.1794 | -115.1779
1370.3906 | 115.1047 | -89.3417 | 25.6256 | -0.0054933 | 0.014905 | 0.064354 | 0.0039265 | 0.061671 | 0.0012305 | -0.0022986 | -0.011673 | -0.0015637 | 0.061148 | 0.06304 | 0.0031915 | -0.0076926 | 25.6348 | -88.7238 | -12.8632 | -89.2456 | 25.6393 | -89.3784 | -89.3188 | -89.1357 | -10.3821 | -89.5477 | 25.5753 | 25.589 | -89.36 | -89.5248 | -0.036621 | 0.022888 | 0.013733 | 0.61798 | 0.096131 | 0.073243 | 0.009156 | -0.01831 | -0.1831 | -0.050354 | 0.20599 | -0.20599 | -0.022888 | -0.036621 | 114.9811 | 114.9765 | 76.4786 | -114.9445 | 114.917 | 114.9307 | 78.9597 | -115.1505
1372.125 | 115.0269 | -89.2868 | 25.589 | -0.013122 | 0.014691 | 0.064995 | 0.0054217 | 0.062739 | -0.0011193 | -0.0016578 | -0.011673 | -0.0054089 | 0.057943 | 0.06069 | 0.0059687 | -0.0061972 | 25.7034 | -88.5773 | -12.03 | -89.1312 | 25.5661 | -89.3417 | -89.2273 | -89.003 | -9.7733 | -89.4104 | 25.4883 | 25.5203 | -89.3326 | -89.4836 | -0.054932 | 0.059509 | -0.022888 | 0.70953 | 0.15564 | 0.09613 | 0.11444 | -0.045777 | -0.19684 | -0.10071 | 0.28381 | -0.1236 | 0.073243 | -0.068664 | 114.8529 | 114.9902 | 77.2568 | -114.8163 | 114.7751 | 114.8071 | 79.5136 | -115.0726
1373.875 | 115.0772 | -89.2685 | 25.5569 | -0.013122 | 0.018109 | 0.066063 | 0.0071307 | 0.062312 | 0.0014441 | -0.0010168 | 0.0035858 | -0.0011365 | 0.057516 | 0.06304 | 0.0049005 | -0.011111 | 25.6622 | -88.6093 | -11.5677 | -89.1724 | 25.6027 | -89.3463 | -89.241 | -89.035 | -10.0159 | -89.4608 | 25.502 | 25.5295 | -89.3143 | -89.4745 | -0.077819 | 0.027466 | 0.045776 | 0.65918 | 0.096131 | 0.068665 | 0.10528 | -0.045776 | -0.20599 | -0.054932 | 0.23346 | -0.19226 | 0.013733 | -0.027466 | 114.8712 | 114.9307 | 77.7008 | -114.798 | 114.7705 | 114.798 | 79.2526 | -115.0314
1375.5625 | 114.9673 | -89.2593 | 25.5341 | 0.0021362 | 0.015118 | 0.063499 | 0.0045673 | 0.062525 | -0.0028283 | -0.0010168 | -0.0040437 | -0.0049817 | 0.059652 | 0.062399 | 0.0044733 | -0.0081198 | 25.6531 | -88.5361 | -11.3846 | -89.1037 | 25.5386 | -89.2868 | -89.2044 | -88.9618 | -9.6268 | -89.3738 | 25.4654 | 25.4654 | -89.3005 | -89.4379 | -0.027466 | 0.054931 | 0.004577 | 0.72327 | 0.15564 | 0.10071 | 0.11902 | -0.041199 | -0.17853 | -0.068665 | 0.29755 | -0.11444 | 0.064087 | -0.068665 | 114.798 | 114.9124 | 77.8748 | -114.7385 | 114.7247 | 114.7247 | 79.6326 | -114.9719
1377.3125 | 114.9765 | -89.2731 | 25.5753 | -0.013122 | 0.019391 | 0.063927 | 0.0073443 | 0.062098 | 0.0029395 | 5.1244e-05 | -0.026932 | -0.0041271 | 0.06072 | 0.063254 | 0.0068231 | -0.010897 | 25.6027 | -88.6093 | -11.5173 | -89.1586 | 25.5569 | -89.3143 | -89.2181 | -88.9847 | -9.7824 | -89.4699 | 25.4791 | 25.502 | -89.328 | -89.4928 | -0.041199 | 0.054931 | -0.01831 | 0.66376 | 0.11444 | 0.05951 | 0.027466 | -0.054932 | -0.21973 | -0.09613 | 0.28839 | -0.19684 | 0.022888 | -0.073242 | 114.83 | 114.8758 | 77.7557 | -114.7934 | 114.7522 | 114.7751 | 79.4907 | -115.0681
1379.0625 | 115.004 | -89.2365 | 25.5203 | -0.013122 | 0.015332 | 0.066917 | 0.0090533 | 0.064234 | -0.0043237 | -0.0029394 | -0.0040437 | -0.0062635 | 0.060507 | 0.06069 | 0.0014825 | -0.0076926 | 25.5981 | -88.5086 | -12.0026 | -89.09 | 25.5203 | -89.3097 | -89.1907 | -88.9664 | -9.6451 | -89.3921 | 25.4517 | 25.4837 | -89.296 | -89.4562 | -0.073242 | 0.045776 | 0 | 0.72784 | 0.14648 | 0.10071 | 0.07782 | -0.059509 | -0.21973 | -0.068665 | 0.27008 | -0.15564 | 0.064087 | -0.036621 | 114.7568 | 114.8346 | 77.2339 | -114.711 | 114.6881 | 114.7202 | 79.5914 | -114.9765
1380.75 | 114.8895 | -89.2502 | 25.5524 | -0.013122 | 0.012341 | 0.066277 | 0.0020039 | 0.059321 | -0.0026147 | -0.0014442 | -0.011673 | -0.0064771 | 0.05773 | 0.06304 | 0.0036189 | -0.0072652 | 25.621 | -88.5132 | -11.5448 | -89.1037 | 25.5112 | -89.2502 | -89.1632 | -88.916 | -9.2285 | -89.3509 | 25.4288 | 25.4471 | -89.2548 | -89.4287 | 0 | 0.086975 | -0.041199 | 0.737 | 0.14648 | 0.059509 | 0.068665 | -0.004578 | -0.17853 | -0.1236 | 0.33417 | -0.10071 | 0.07782 | -0.10529 | 114.7614 | 114.8712 | 77.7054 | -114.7156 | 114.679 | 114.6973 | 80.0217 | -114.9811
1382.4844 | 114.949 | -89.2456 | 25.5249 | -0.0054933 | 0.018536 | 0.062859 | 0.0060627 | 0.064448 | 0.00016226 | -0.00080316 | 0.0035858 | -0.0019909 | 0.060079 | 0.063467 | 0.0042597 | -0.010683 | 25.5478 | -88.6505 | -12.6343 | -89.1861 | 25.5753 | -89.296 | -89.2044 | -88.9069 | -9.1736 | -89.4241 | 25.4562 | 25.4883 | -89.3097 | -89.4287 | -0.050354 | 0.041198 | 0.050354 | 0.59509 | 0.059509 | 0.018311 | 0.022889 | -0.064087 | -0.18311 | -0.068664 | 0.33875 | -0.17853 | 0.004578 | -0.036621 | 114.8209 | 114.7934 | 76.6113 | -114.7293 | 114.7018 | 114.7339 | 80.072 | -114.9536
1384.1719 | 114.9902 | -89.2227 | 25.502 | -0.0054933 | 0.015332 | 0.064354 | 0.0067035 | 0.065089 | -0.0034691 | -0.002085 | 0.0035858 | -0.0043409 | 0.058157 | 0.063254 | 0.0010553 | -0.010042 | 25.621 | -88.5269 | -11.9019 | -89.0945 | 25.5203 | -89.296 | -89.1907 | -88.8702 | -8.9218 | -89.3692 | 25.4196 | 25.4379 | -89.2548 | -89.4287 | -0.073242 | 0.032043 | 0.018311 | 0.6958 | 0.12817 | 0.096131 | 0.11902 | -0.032044 | -0.20599 | -0.082397 | 0.35248 | -0.14648 | 0.059509 | -0.064087 | 114.743 | 114.8438 | 77.3209 | -114.6927 | 114.6423 | 114.6606 | 80.3009 | -114.9307
1385.9375 | 115.004 | -89.2639 | 25.5249 | -0.0054933 | 0.015118 | 0.063072 | 0.0069171 | 0.06103 | -0.0013329 | -0.0044348 | -0.0040437 | -0.0043409 | 0.05837 | 0.061545 | 0.0031915 | -0.0087606 | 25.5524 | -88.6414 | -12.4786 | -89.1815 | 25.5753 | -89.3463 | -89.241 | -88.9572 | -8.9722 | -89.4836 | 25.4883 | 25.5157 | -89.3143 | -89.4745 | -0.082397 | 0.022888 | 0.050354 | 0.62256 | 0.082397 | 0.059509 | 0.027466 | -0.050354 | -0.21057 | -0.036621 | 0.3067 | -0.21973 | -0.009156 | -0.009155 | 114.8392 | 114.8163 | 76.7853 | -114.7659 | 114.7522 | 114.7797 | 80.2917 | -114.9994
1387.6875 | 118.0756 | -117.6453 | 0.32044 | -0.013122 | 0.013409 | 0.069695 | 0.0026447 | 0.063807 | -0.00069214 | -0.002085 | -0.0040437 | -0.0032727 | 0.058157 | 0.063895 | 0.0042597 | -0.0076926 | 0.27008 | -116.6977 | -24.1241 | -117.4347 | 0.27466 | -117.7414 | -117.5949 | -117.0914 | -17.0883 | -117.746 | 0.19226 | 0.21515 | -117.7048 | -117.865 | -0.09613 | 0.050354 | -0.045777 | 0.94757 | 0.21057 | 0.16022 | -0.050354 | -0.059509 | -0.21973 | -0.12817 | 0.55389 | -0.10071 | 0.11902 | -0.10529 | 117.9199 | 117.9153 | 93.5211 | -117.9153 | 117.8375 | 117.8604 | 100.5569 | -118.1854
1389.3594 | 118.5196 | -117.9565 | 0.27008 | -0.028381 | 0.020886 | 0.065208 | 0.0088397 | 0.062953 | 0.0029395 | -0.003794 | -0.011673 | -0.00092292 | 0.061788 | 0.066885 | 0.0046869 | -0.010683 | 0.16937 | -117.1417 | -24.6643 | -117.8192 | 0.34332 | -118.0801 | -117.952 | -117.485 | -17.3309 | -118.1763 | 0.2243 | 0.26093 | -118.0756 | -118.2312 | -0.1236 | 0.004578 | 0.073242 | 0.81482 | 0.13733 | 0.13275 | -0.10071 | -0.11902 | -0.27466 | -0.045777 | 0.4715 | -0.21973 | 0.054931 | -0.009156 | 118.2999 | 118.1259 | 93.2922 | -118.222 | 118.1808 | 118.2175 | 100.6256 | -118.5013
1391.0312 | 118.5425 | -118.2083 | 0.3067 | -0.0054933 | 0.018322 | 0.066704 | 0.0030719 | 0.063593 | 0.0016577 | -0.0025122 | 0.0035858 | -0.0013501 | 0.061148 | 0.067313 | 0.0068231 | -0.0070516 | 0.12817 | -117.3477 | -23.79 | -118.0344 | 0.31586 | -118.2678 | -118.1213 | -117.6178 | -17.0792 | -118.3823 | 0.20599 | 0.23346 | -118.2541 | -118.4189 | -0.059509 | 0.086975 | 0.009155 | 0.8606 | 0.17395 | 0.086975 | -0.17853 | -0.045776 | -0.21057 | -0.10071 | 0.59052 | -0.17395 | 0.036621 | -0.073243 | 118.5242 | 118.3365 | 94.4183 | -118.428 | 118.4143 | 118.4418 | 101.1292 | -118.7256
1392.7656 | 118.689 | -118.2495 | 0.32501 | 0.0021362 | 0.016827 | 0.067345 | 0.0037127 | 0.066371 | -0.0028283 | 0.002401 | -0.0040437 | -0.0051953 | 0.059439 | 0.065176 | 0.0038325 | -0.0070516 | 0.27008 | -117.3019 | -24.0372 | -118.0115 | 0.32501 | -118.2999 | -118.1717 | -117.5079 | -17.3035 | -118.309 | 0.20599 | 0.23346 | -118.2907 | -118.4143 | -0.050354 | 0.07782 | 0 | 0.94757 | 0.23804 | 0.16022 | -0.054931 | -0.041198 | -0.16479 | -0.11902 | 0.74158 | -0.059509 | 0.10529 | -0.091553 | 118.5745 | 118.5196 | 94.2123 | -118.4967 | 118.4555 | 118.483 | 100.946 | -118.7393
1394.5156 | 118.8263 | -118.3228 | 0.3479 | -0.013122 | 0.014905 | 0.067558 | 0.0069171 | 0.064448 | -0.0060327 | -0.0033668 | -0.011673 | -0.0051953 | 0.062643 | 0.064749 | 0.0025507 | -0.007479 | 0.21973 | -117.4072 | -23.2452 | -118.1213 | 0.36163 | -118.3777 | -118.2541 | -117.6498 | -17.0151 | -118.4097 | 0.25635 | 0.30212 | -118.3548 | -118.5013 | -0.054932 | 0.068665 | 0.013733 | 0.91553 | 0.20142 | 0.13275 | -0.12817 | -0.032043 | -0.17853 | -0.091552 | 0.67291 | -0.086975 | 0.091553 | -0.045776 | 118.6844 | 118.5425 | 95.0775 | -118.602 | 118.5791 | 118.6249 | 101.3077 | -118.8492
1396.1875 | 118.8538 | -118.5242 | 0.27466 | 0.0021362 | 0.013409 | 0.066277 | 0.0039265 | 0.062953 | -0.0034691 | -0.0033668 | -0.011673 | -0.0032727 | 0.059011 | 0.063895 | 0.0036189 | -0.0072652 | 0.16479 | -117.5949 | -23.7122 | -118.3273 | 0.25177 | -118.5699 | -118.4189 | -117.8055 | -17.1204 | -118.6157 | 0.16479 | 0.21057 | -118.5333 | -118.7027 | -0.045776 | 0.10529 | -0.022888 | 0.92926 | 0.19684 | 0.091552 | -0.10986 | -0.009155 | -0.17853 | -0.10986 | 0.71869 | -0.091553 | 0.086975 | -0.064087 | 118.7759 | 118.689 | 94.812 | -118.6935 | 118.689 | 118.7347 | 101.4038 | -118.9774
1397.9375 | 119.0369 | -118.5791 | 0.24719 | -0.0054933 | 0.017041 | 0.068413 | 0.0060627 | 0.064662 | 0.0010169 | -0.0029394 | 0.011215 | -0.0019909 | 0.062002 | 0.067953 | 0.0029779 | -0.0094016 | 0.14191 | -117.7551 | -24.1425 | -118.4418 | 0.29755 | -118.689 | -118.5379 | -117.8741 | -17.2989 | -118.7897 | 0.20142 | 0.23804 | -118.6844 | -118.8263 | -0.10986 | 0.041199 | 0.050354 | 0.82398 | 0.13733 | 0.096131 | -0.10528 | -0.10528 | -0.24719 | -0.045776 | 0.70496 | -0.21057 | 0.036621 | -0.009155 | 118.8766 | 118.721 | 94.4366 | -118.7851 | 118.7805 | 118.8171 | 101.2802 | -119.0735
1399.6875 | 119.0231 | -118.7119 | 0.27466 | -0.0054933 | 0.016613 | 0.06884 | 0.0028583 | 0.063593 | -0.0021875 | 5.1244e-05 | -0.011673 | -0.0030591 | 0.058584 | 0.062827 | 0.0070367 | -0.0081198 | 0.2655 | -117.7139 | -24.4629 | -118.428 | 0.26093 | -118.7073 | -118.5562 | -117.8284 | -17.4912 | -118.721 | 0.15106 | 0.17853 | -118.6798 | -118.8629 | 0.004578 | 0.15564 | -0.013733 | 0.99793 | 0.28381 | 0.12817 | -0.009155 | 0.032043 | -0.15106 | -0.1236 | 0.88348 | -0.009155 | 0.14191 | -0.09613 | 118.9728 | 118.9774 | 94.249 | -118.8309 | 118.8629 | 118.8904 | 101.2207 | -119.1376
1401.4219 | 119.0964 | -118.7668 | 0.27466 | -0.020752 | 0.017468 | 0.066704 | 0.0043537 | 0.063166 | 0.0046485 | -0.0016578 | -0.0040437 | -0.00070932 | 0.060293 | 0.066672 | 0.0074641 | -0.008547 | 0.14191 | -117.9565 | -24.8703 | -118.6066 | 0.3067 | -118.8126 | -118.6752 | -117.9657 | -17.4591 | -118.959 | 0.21515 | 0.23804 | -118.8034 | -118.9819 | -0.045776 | 0.091553 | 0.032044 | 0.81024 | 0.16022 | 0.068665 | -0.13275 | -0.036621 | -0.21515 | -0.059509 | 0.80109 | -0.19226 | 0.022889 | -0.036621 | 119.0735 | 118.9087 | 93.8965 | -118.9499 | 118.9819 | 119.0048 | 101.3077 | -119.2566
1403.1094 | 119.1925 | -118.8538 | 0.29755 | -0.020752 | 0.019604 | 0.06649 | 0.0045673 | 0.065089 | 0.0044349 | 0.00090584 | -0.019302 | -0.0013501 | 0.061575 | 0.06539 | 0.0068231 | -0.006838 | 0.19226 | -117.9291 | -24.8383 | -118.6386 | 0.30212 | -118.8995 | -118.7485 | -117.9657 | -17.4774 | -118.9911 | 0.17853 | 0.24261 | -118.8675 | -119.0643 | -0.045776 | 0.10529 | 0.004578 | 0.92468 | 0.21515 | 0.10986 | -0.10528 | -0.013733 | -0.21057 | -0.11902 | 0.88806 | -0.13733 | 0.073242 | -0.054931 | 119.1559 | 119.046 | 94.0155 | -119.046 | 119.0323 | 119.0964 | 101.3763 | -119.3619
1404.8594 | 119.3253 | -118.9041 | 0.27008 | 0.0021362 | 0.015973 | 0.069054 | 0.0081989 | 0.067439 | -0.0021875 | -0.0022986 | -0.011673 | -0.0060497 | 0.062002 | 0.064322 | 0.0025507 | -0.0066244 | 0.20142 | -117.9474 | -26.5274 | -118.689 | 0.27924 | -118.9728 | -118.8126 | -118.0389 | -17.7658 | -119.0231 | 0.20599 | 0.24719 | -118.9362 | -119.1101 | -0.068664 | 0.091553 | 0.009155 | 0.95673 | 0.21515 | 0.1236 | -0.068665 | -0.032043 | -0.20599 | -0.064087 | 0.86517 | -0.11902 | 0.086975 | -0.022889 | 119.1834 | 119.1055 | 92.3767 | -119.0826 | 119.1101 | 119.1513 | 101.1383 | -119.3802
1406.5938 | 119.4397 | -118.9728 | 0.2655 | -0.013122 | 0.016827 | 0.068626 | 0.0060627 | 0.065943 | -0.00047854 | -0.0016578 | -0.019302 | -0.0015637 | 0.062002 | 0.065604 | 0.0029779 | -0.0094016 | 0.14648 | -118.0984 | -25.5615 | -118.8126 | 0.34332 | -119.0369 | -118.9133 | -118.1305 | -17.5003 | -119.1376 | 0.23346 | 0.27008 | -119.0323 | -119.1879 | -0.064087 | 0.059509 | 0.07782 | 0.87433 | 0.16022 | 0.10071 | -0.11902 | -0.05951 | -0.21515 | -0.032044 | 0.84229 | -0.16479 | 0.050354 | 0.004578 | 119.3161 | 119.1193 | 93.4113 | -119.1788 | 119.2062 | 119.2429 | 101.4725 | -119.4534
1408.2656 | 119.4214 | -118.9865 | 0.31128 | 0.0097657 | 0.017254 | 0.068199 | 0.0045673 | 0.066798 | 0.00080326 | -0.0018714 | -0.011673 | -0.0028455 | 0.059225 | 0.065604 | 0.0066095 | -0.0087606 | 0.16937 | -118.1442 | -26.4175 | -118.8492 | 0.35248 | -119.0598 | -118.9407 | -118.0984 | -17.514 | -119.1742 | 0.23346 | 0.27008 | -119.0323 | -119.2017 | -0.073242 | 0.045776 | 0.041199 | 0.84228 | 0.13733 | 0.091553 | -0.14191 | -0.045777 | -0.21515 | -0.07782 | 0.88806 | -0.18768 | 0.027466 | -0.041198 | 119.339 | 119.1559 | 92.569 | -119.252 | 119.22 | 119.2566 | 101.4725 | -119.5129
1410.0156 | 119.5541 | -119.0552 | 0.29755 | -0.013122 | 0.015759 | 0.069267 | 0.0071307 | 0.06338 | -0.0024011 | -0.0010168 | -0.0040437 | -0.0034863 | 0.063284 | 0.065176 | 0.0012689 | -0.0066244 | 0.15564 | -118.1946 | -26.4587 | -118.9087 | 0.35706 | -119.1376 | -118.9911 | -118.1717 | -17.5049 | -119.2429 | 0.25177 | 0.28381 | -119.1101 | -119.3024 | -0.082397 | 0.064087 | 0.05951 | 0.8606 | 0.14648 | 0.082398 | -0.14191 | -0.054931 | -0.24719 | -0.045776 | 0.88348 | -0.18768 | 0.059509 | -0.013733 | 119.4122 | 119.2108 | 92.5964 | -119.2886 | 119.3069 | 119.339 | 101.5503 | -119.5999
1411.75 | 119.4946 | -119.1422 | 0.32501 | -0.0054933 | 0.011487 | 0.067772 | 0.0052081 | 0.061884 | -0.0034691 | -0.0014442 | 0.0035858 | -0.0045545 | 0.06072 | 0.066031 | 0.0014825 | -0.0064108 | 0.24261 | -118.1808 | -26.9348 | -118.9407 | 0.29755 | -119.1605 | -119.0414 | -118.2175 | -17.4866 | -119.2108 | 0.19226 | 0.23804 | -119.1742 | -119.3527 | -0.01831 | 0.10071 | -0.027466 | 0.9613 | 0.20142 | 0.10071 | -0.082397 | -0.032043 | -0.21057 | -0.13275 | 0.92468 | -0.068664 | 0.14191 | -0.086975 | 119.4397 | 119.3848 | 92.2073 | -119.3665 | 119.3344 | 119.3802 | 101.6556 | -119.6777
1413.4219 | 119.6548 | -119.1742 | 0.31128 | 0.0021362 | 0.016827 | 0.069267 | 0.0079853 | 0.061457 | -0.0015465 | -0.0016578 | 0.011215 | -0.0041271 | 0.062856 | 0.065176 | 0.0025507 | -0.0087606 | 0.19226 | -118.3273 | -26.9073 | -119.0323 | 0.32959 | -119.2657 | -119.1376 | -118.2678 | -16.9189 | -119.3527 | 0.21973 | 0.28381 | -119.2612 | -119.426 | -0.091553 | 0.036621 | 0.018311 | 0.84686 | 0.14191 | 0.10529 | -0.11902 | -0.086975 | -0.25177 | -0.091552 | 0.90637 | -0.17853 | 0.073242 | -0.027466 | 119.5038 | 119.3665 | 92.2668 | -119.4489 | 119.3939 | 119.458 | 102.2552 | -119.7372
1415.1719 | 119.7876 | -119.252 | 0.27924 | -0.0054933 | 0.015332 | 0.068413 | 0.0054217 | 0.062953 | 0.0014441 | -0.002085 | -0.0040437 | -0.0039135 | 0.062643 | 0.064749 | 0.0055415 | -0.010256 | 0.16937 | -118.4326 | -25.9552 | -119.101 | 0.33417 | -119.3298 | -119.2291 | -118.2724 | -17.1249 | -119.426 | 0.23346 | 0.25635 | -119.339 | -119.5038 | -0.07782 | 0.022888 | 0.054931 | 0.8194 | 0.15106 | 0.12817 | -0.10986 | -0.086975 | -0.25177 | -0.045777 | 0.97961 | -0.17395 | 0.07782 | -0.022888 | 119.5862 | 119.4214 | 93.2968 | -119.5084 | 119.4855 | 119.5084 | 102.1271 | -119.783
1416.9219 | 119.8059 | -119.2474 | 0.28839 | -0.013122 | 0.013409 | 0.069481 | 0.0058491 | 0.064875 | -0.0058191 | -0.0025122 | -0.0040437 | -0.0049817 | 0.059439 | 0.064749 | 0.0010553 | -0.0083334 | 0.24261 | -118.3365 | -26.7151 | -119.0826 | 0.3067 | -119.3527 | -119.2154 | -118.2632 | -16.7358 | -119.339 | 0.19684 | 0.26093 | -119.3481 | -119.4946 | -0.10528 | 0.032044 | 0.018311 | 0.91095 | 0.16479 | 0.13275 | -0.045776 | -0.10071 | -0.24719 | -0.091553 | 0.98419 | -0.091552 | 0.15564 | -0.027466 | 119.5541 | 119.4901 | 92.5323 | -119.5038 | 119.4443 | 119.5084 | 102.5116 | -119.783
1418.6562 | 119.8471 | -119.3344 | 0.3067 | -0.0054933 | 0.015545 | 0.067131 | 0.0081989 | 0.066584 | -0.0021875 | -0.0018714 | 0.0035858 | -0.0060497 | 0.062216 | 0.064322 | 0.0025507 | -0.0087606 | 0.28381 | -118.2999 | -27.4933 | -119.101 | 0.31586 | -119.3985 | -119.2383 | -118.2999 | -17.189 | -119.3802 | 0.21515 | 0.25177 | -119.3802 | -119.5404 | -0.064087 | 0.096131 | 0.009155 | 1.0345 | 0.23346 | 0.13733 | -0.022889 | -0.045776 | -0.20599 | -0.091553 | 1.0345 | -0.045776 | 0.16022 | -0.054932 | 119.6503 | 119.6182 | 91.8411 | -119.545 | 119.5496 | 119.5862 | 102.1454 | -119.8471
1420.4062 | 119.8242 | -119.426 | 0.32959 | -0.013122 | 0.011914 | 0.068626 | 0.0073443 | 0.064234 | -0.0024011 | -0.0029394 | 0.0035858 | -0.0075451 | 0.059439 | 0.064108 | 0.0063959 | -0.0072652 | 0.24719 | -118.4601 | -27.2598 | -119.1971 | 0.32501 | -119.4305 | -119.3207 | -118.3777 | -16.832 | -119.5038 | 0.23804 | 0.2655 | -119.4763 | -119.6182 | -0.004578 | 0.10528 | -0.004578 | 0.96588 | 0.22888 | 0.1236 | -0.082398 | -0.050354 | -0.19226 | -0.091553 | 1.0483 | -0.07782 | 0.11444 | -0.064087 | 119.751 | 119.6732 | 92.1661 | -119.6503 | 119.664 | 119.6915 | 102.594 | -119.9478
1422.0781 | 119.8425 | -119.4855 | 0.34332 | -0.013122 | 0.013623 | 0.070549 | 0.0054217 | 0.067225 | -0.0030419 | -0.0042212 | -0.011673 | -0.0041271 | 0.059652 | 0.064963 | 0.0042597 | -0.0070516 | 0.27466 | -118.483 | -28.9627 | -119.252 | 0.32959 | -119.4855 | -119.3527 | -118.4052 | -17.6331 | -119.545 | 0.23346 | 0.2655 | -119.5084 | -119.6503 | 0 | 0.13275 | -0.013733 | 1.0025 | 0.23346 | 0.10071 | -0.068665 | -0.022888 | -0.16479 | -0.10986 | 1.0803 | -0.059509 | 0.10529 | -0.07782 | 119.8151 | 119.7601 | 90.5228 | -119.696 | 119.7189 | 119.751 | 101.8524 | -119.9936
1423.8281 | 119.9707 | -119.5038 | 0.35248 | -0.028381 | 0.015545 | 0.068626 | 0.00072207 | 0.066371 | 0.0020849 | -0.0010168 | -0.0040437 | -0.0026319 | 0.060507 | 0.06304 | 0.0055415 | -0.0089742 | 0.24261 | -118.602 | -28.9673 | -119.339 | 0.36163 | -119.5724 | -119.4305 | -118.5196 | -17.4728 | -119.6228 | 0.27008 | 0.28381 | -119.545 | -119.7189 | -0.068665 | 0.073242 | 0.009155 | 0.90179 | 0.16479 | 0.091553 | -0.10986 | -0.041199 | -0.21515 | -0.082397 | 0.98419 | -0.11902 | 0.09613 | -0.068665 | 119.8654 | 119.7464 | 90.5365 | -119.783 | 119.7739 | 119.7876 | 102.0309 | -120.0714
1425.5781 | 119.9203 | -119.6182 | 0.30212 | -0.013122 | 0.015759 | 0.06884 | 0.0039265 | 0.066157 | -0.0028283 | -0.0022986 | -0.0040437 | 0.025566 | -0.0097755 | 0.021384 | 0.0019099 | -0.0081198 | 0.24261 | -118.5654 | -23.8037 | -119.3893 | 0.25635 | -119.6411 | -119.5175 | 0.16022 | -2.5726 | 0.15564 | 0.22888 | 0.21057 | 0.12817 | 0.07782 | -0.022888 | 0.10071 | -0.045776 | 1.0529 | 0.22888 | 0.12817 | -0.059509 | 119.7464 | 119.696 | -0.073242 | 119.7784 | 119.7739 | 0.07782 | -0.091553 | 119.8746 | 119.8608 | 95.8145 | -119.8196 | 119.8471 | 119.8288 | 117.0456 | -0.2243
1427.3281 | 120.0485 | -119.664 | 0.29297 | -0.013122 | 0.014264 | 0.06884 | 0.0039265 | 0.062953 | 0.0031531 | -0.0018714 | -0.011673 | 0.027489 | -0.011271 | 0.020316 | 0.0053279 | -0.010256 | 0.24719 | -118.6295 | -23.9731 | -119.4626 | 0.29755 | -119.7098 | -119.5679 | 0.21973 | -2.4994 | 0.15564 | 0.23346 | 0.22888 | 0.1831 | 0.091553 | -0.045777 | 0.09613 | 0.004577 | 1.0345 | 0.20142 | 0.10529 | -0.045777 | 119.8471 | 119.7556 | -0.05951 | 119.8837 | 119.8196 | 0.064087 | -0.064087 | 119.9615 | 119.9112 | 95.6909 | -119.8608 | 119.8975 | 119.8929 | 117.1646 | -0.20142
1429.0781 | 120.0806 | -119.7372 | 0.31586 | -0.0054933 | 0.014905 | 0.06884 | 0.0041401 | 0.065943 | -0.00026494 | -0.0014442 | -0.011673 | 0.026207 | -0.010416 | 0.021597 | 0.0044733 | -0.008547 | 0.27008 | -118.6111 | -23.5565 | -119.4534 | 0.27008 | -119.7418 | -119.5908 | 0.24261 | -2.4216 | 0.18768 | 0.20599 | 0.19226 | 0.16022 | 0.091553 | -0.004577 | 0.14648 | -0.045776 | 1.1261 | 0.28381 | 0.13733 | -0.045776 | 119.8975 | 119.8288 | -0.10986 | 119.9799 | 119.9249 | 0.09613 | -0.1236 | 120.0073 | 120.0073 | 96.1807 | -119.9066 | 119.9432 | 119.9295 | 117.3157 | -0.2243
1430.8281 | 120.2545 | -119.7189 | 0.27924 | -0.0054933 | 0.01405 | 0.069267 | 0.0064899 | 0.066371 | -0.0028283 | -0.0027258 | 0.011215 | 0.024285 | -0.011271 | 0.02117 | 0.00062806 | -0.0094016 | 0.25635 | -118.6386 | -23.5474 | -119.5084 | 0.28839 | -119.7968 | -119.6457 | 0.20142 | -2.4673 | 0.2243 | 0.24261 | 0.22888 | 0.16479 | 0.07782 | -0.07782 | 0.073242 | 0.009155 | 1.0803 | 0.21057 | 0.13733 | -0.022888 | 119.8837 | 119.7968 | -0.036621 | 119.9203 | 119.9432 | 0.14648 | -0.050354 | 120.0073 | 119.9753 | 96.1716 | -119.9249 | 119.9615 | 119.9478 | 117.2516 | -0.20142
1432.5156 | 120.2774 | -119.7556 | 0.28839 | -0.0054933 | 0.015759 | 0.069267 | 0.0073443 | 0.066157 | -0.0036829 | -0.0042212 | -0.011673 | 0.025353 | -0.0093481 | 0.021597 | -0.00065374 | -0.010897 | 0.28381 | -118.6615 | -23.4695 | -119.5404 | 0.3067 | -119.8288 | -119.7006 | 0.20142 | -2.3666 | 0.21973 | 0.21515 | 0.21973 | 0.17395 | 0.10529 | -0.073242 | 0.054931 | 0.018311 | 1.0941 | 0.21515 | 0.16022 | -0.004578 | 119.9295 | 119.8608 | -0.073242 | 119.957 | 119.9753 | 0.11444 | -0.068664 | 120.0623 | 120.0394 | 96.286 | -119.989 | 119.9707 | 119.9753 | 117.3889 | -0.18311
1434.2656 | 120.3323 | -119.783 | 0.27924 | -0.0054933 | 0.015759 | 0.068199 | 0.0058491 | 0.065089 | 0.0022987 | -0.0010168 | -0.0040437 | 0.030907 | -0.0093481 | 0.023093 | 0.0055415 | -0.0098288 | 0.20599 | -118.8629 | -23.5611 | -119.6548 | 0.33417 | -119.9341 | -119.7647 | 0.14648 | -2.6779 | 0.059509 | 0.2655 | 0.27008 | 0.13275 | 0.041199 | -0.15106 | 0.018311 | 0.054931 | 0.9201 | 0.12817 | 0.10986 | -0.073242 | 119.9158 | 119.8242 | -0.013733 | 119.9295 | 119.8425 | 0.01831 | -0.009155 | 120.1172 | 119.989 | 96.2219 | -120.0439 | 120.0485 | 120.0531 | 117.1051 | -0.23804
1436.0156 | 120.2545 | -119.8975 | 0.30212 | -0.0054933 | 0.017254 | 0.065849 | 0.0049945 | 0.064448 | 0.0035803 | -0.00058956 | 0.011215 | 0.030052 | -0.0099891 | 0.021597 | 0.0076777 | -0.010256 | 0.16937 | -118.895 | -24.0234 | -119.7189 | 0.33417 | -119.9203 | -119.8242 | 0.12817 | -2.5772 | 0.050354 | 0.28381 | 0.2655 | 0.13275 | 0.059509 | -0.022888 | 0.073242 | 0.032043 | 1.0025 | 0.17853 | 0.10529 | -0.13275 | 120.0302 | 119.957 | -0.018311 | 120.0256 | 119.9478 | -0.009155 | -0.036621 | 120.2316 | 120.0668 | 95.874 | -120.1263 | 120.1813 | 120.163 | 117.3203 | -0.24261
1437.6875 | 120.3049 | -119.9158 | 0.31586 | -0.0054933 | 0.017254 | 0.069695 | 0.0022175 | 0.065302 | 0.0010169 | -0.0010168 | -0.0040437 | 0.029839 | -0.010416 | 0.023306 | 0.0051141 | -0.010683 | 0.15564 | -118.8995 | -24.8611 | -119.7556 | 0.32501 | -119.989 | -119.87 | 0.11902 | -2.6321 | 0.054932 | 0.25177 | 0.27008 | 0.14191 | 0.050354 | -0.073243 | 0.045776 | 0.009155 | 1.0162 | 0.16022 | 0.11444 | -0.16022 | 120.0577 | 119.9661 | -0.064087 | 120.0348 | 119.9707 | 0.004578 | -0.045776 | 120.2408 | 120.0714 | 95.0546 | -120.1859 | 120.1675 | 120.1859 | 117.2836 | -0.2655
1439.4375 | 120.4239 | -119.9112 | 0.29297 | -0.020752 | 0.012341 | 0.069908 | 0.0062763 | 0.064448 | -0.0043237 | -0.0022986 | -0.011673 | 0.02343 | -0.011912 | 0.019461 | 0.0014825 | -0.0089742 | 0.21973 | -118.7759 | -24.8474 | -119.7144 | 0.31128 | -119.989 | -119.8517 | 0.20599 | -2.4216 | 0.21973 | 0.22888 | 0.21973 | 0.1831 | 0.10986 | -0.07782 | 0.059509 | 0.01831 | 1.1353 | 0.19684 | 0.13733 | -0.073242 | 120.0943 | 120.0211 | -0.064087 | 120.1172 | 120.1309 | 0.10986 | -0.073242 | 120.2225 | 120.1309 | 95.0638 | -120.1447 | 120.1401 | 120.1309 | 117.4896 | -0.18311
1441.1094 | 120.4285 | -119.957 | 0.31128 | -0.020752 | 0.016827 | 0.070335 | 0.0064899 | 0.067225 | -0.0028283 | -0.0044348 | -0.011673 | 0.025139 | -0.0097755 | 0.02117 | 0.00084166 | -0.0087606 | 0.2655 | -118.8034 | -24.765 | -119.7464 | 0.29297 | -120.0119 | -119.902 | 0.21515 | -2.3941 | 0.19684 | 0.24261 | 0.24719 | 0.17853 | 0.09613 | -0.054932 | 0.054931 | -0.01831 | 1.1536 | 0.21057 | 0.15564 | -0.045776 | 120.1355 | 120.0531 | -0.068664 | 120.1721 | 120.1538 | 0.10071 | -0.064087 | 120.2499 | 120.2225 | 95.192 | -120.2133 | 120.1996 | 120.2042 | 117.5629 | -0.21515
1442.8594 | 120.4514 | -120.0348 | 0.33417 | -0.013122 | 0.015973 | 0.065849 | 0.0043537 | 0.065302 | 0.0029395 | -0.00058956 | -0.0040437 | 0.028771 | -0.01063 | 0.024802 | 0.0070367 | -0.0089742 | 0.19226 | -118.9636 | -25.6119 | -119.8563 | 0.33417 | -120.0943 | -119.957 | 0.13733 | -2.7008 | 0.068665 | 0.26093 | 0.28381 | 0.16479 | 0.082397 | -0.059509 | 0.07782 | 0 | 1.0712 | 0.17853 | 0.10071 | -0.14191 | 120.1996 | 120.1172 | -0.073242 | 120.1721 | 120.1035 | -0.013732 | -0.050354 | 120.369 | 120.2271 | 94.4229 | -120.2911 | 120.2957 | 120.3186 | 117.334 | -0.25177
1444.5469 | 120.5154 | -120.0485 | 0.30212 | -0.0054933 | 0.018536 | 0.068413 | 0.0062763 | 0.066157 | -0.0045373 | -0.0042212 | -0.011673 | 0.024498 | -0.011698 | 0.021384 | 0.0025507 | -0.0087606 | 0.24261 | -118.8446 | -25.8957 | -119.8151 | 0.28839 | -120.1172 | -119.9753 | 0.17395 | -2.5726 | 0.16479 | 0.25177 | 0.27466 | 0.16479 | 0.082397 | -0.068664 | 0.073242 | -0.013733 | 1.2039 | 0.23346 | 0.16022 | -0.059509 | 120.2133 | 120.1309 | -0.050354 | 120.2225 | 120.2133 | 0.082398 | -0.027466 | 120.3369 | 120.2911 | 94.1528 | -120.2774 | 120.3003 | 120.3232 | 117.4759 | -0.21973
1446.2969 | 120.5887 | -120.0623 | 0.29755 | -0.0054933 | 0.015973 | 0.068199 | 0.0088397 | 0.064662 | -0.0053919 | -0.0033668 | -0.011673 | 0.024498 | -0.0093481 | 0.020316 | 0.00062806 | -0.0098288 | 0.27924 | -118.8583 | -26.0376 | -119.8517 | 0.29297 | -120.1035 | -119.9936 | 0.21057 | -2.5452 | 0.21973 | 0.2243 | 0.24719 | 0.1831 | 0.10529 | -0.041199 | 0.068665 | -0.004577 | 1.2039 | 0.21057 | 0.14191 | -0.01831 | 120.2454 | 120.1675 | -0.073242 | 120.2728 | 120.282 | 0.11444 | -0.050354 | 120.3552 | 120.3415 | 94.0247 | -120.2911 | 120.2866 | 120.3094 | 117.5171 | -0.19226
1447.9844 | 120.5154 | -120.1492 | 0.32044 | 0.0021362 | 0.017041 | 0.067986 | 0.0047809 | 0.066371 | 0.0035803 | -0.0010168 | 0.0035858 | 0.028343 | -0.010203 | 0.023947 | 0.0068231 | -0.013674 | 0.26093 | -118.9819 | -26.5961 | -119.9295 | 0.31586 | -120.195 | -120.0485 | 0.16937 | -2.7008 | 0.10071 | 0.26093 | 0.27466 | 0.14648 | 0.059509 | -0.045776 | 0.10071 | -0.004578 | 1.1673 | 0.21973 | 0.11902 | -0.05951 | 120.2957 | 120.2087 | -0.05951 | 120.3186 | 120.2499 | 0.041199 | -0.045777 | 120.4651 | 120.4102 | 93.5532 | -120.369 | 120.4102 | 120.4239 | 117.4484 | -0.26093
1449.7344 | 120.6299 | -120.1538 | 0.32044 | -0.0054933 | 0.015545 | 0.071403 | 0.0045673 | 0.065302 | -5.1338e-05 | -0.00058956 | 0.0035858 | 0.027916 | -0.0084937 | 0.020529 | 0.0046869 | -0.0091878 | 0.15106 | -119.0094 | -25.3326 | -119.9936 | 0.33417 | -120.2545 | -120.1126 | 0.10529 | -2.7237 | 0.07782 | 0.27924 | 0.27008 | 0.14648 | 0.064087 | -0.10071 | 0.041199 | 0.013732 | 1.1444 | 0.16022 | 0.11902 | -0.16937 | 120.3003 | 120.2179 | -0.041199 | 120.2591 | 120.2316 | 0.013733 | -0.050354 | 120.488 | 120.3049 | 94.8212 | -120.433 | 120.433 | 120.4239 | 117.4301 | -0.25635
1451.4062 | 120.5658 | -120.2316 | 0.32501 | -0.0054933 | 0.018109 | 0.066277 | 0.0024311 | 0.066371 | 0.0027259 | -0.0016578 | -0.019302 | 0.030052 | -0.0097755 | 0.02117 | 0.0070367 | -0.0089742 | 0.15564 | -119.0735 | -26.0513 | -120.0302 | 0.33417 | -120.2637 | -120.1492 | 0.13275 | -2.9068 | 0.068665 | 0.27924 | 0.27924 | 0.16022 | 0.086975 | -0.032044 | 0.082397 | 0.009155 | 1.1581 | 0.20142 | 0.11902 | -0.16937 | 120.3918 | 120.3186 | -0.045776 | 120.3644 | 120.3003 | -0.01831 | -0.045776 | 120.5658 | 120.3873 | 94.1803 | -120.4742 | 120.5109 | 120.5109 | 117.3248 | -0.23804
1453.0938 | 120.7031 | -120.2179 | 0.27924 | -0.0054933 | 0.015973 | 0.070976 | 0.0069171 | 0.066798 | -0.0058191 | -0.0029394 | -0.0040437 | 0.025139 | -0.0097755 | 0.019888 | -1.2744e-05 | -0.007479 | 0.23804 | -118.8995 | -25.7812 | -119.9615 | 0.28381 | -120.2545 | -120.1309 | 0.21057 | -2.8427 | 0.21057 | 0.23346 | 0.22888 | 0.20142 | 0.10529 | -0.036621 | 0.086976 | 0.004577 | 1.3184 | 0.25635 | 0.16937 | -0.041199 | 120.4193 | 120.3232 | -0.045777 | 120.4285 | 120.4285 | 0.10529 | -0.050354 | 120.5017 | 120.4559 | 94.4366 | -120.4102 | 120.4514 | 120.4468 | 117.3752 | -0.17395
1454.8281 | 120.6207 | -120.2316 | 0.31586 | -0.020752 | 0.010205 | 0.070763 | 0.0043537 | 0.065302 | -0.0019739 | -0.0031532 | -0.019302 | 0.024925 | -0.012125 | 0.021811 | 0.0027643 | -0.0081198 | 0.21057 | -119.0048 | -25.3143 | -120.0302 | 0.31128 | -120.2591 | -120.1447 | 0.16479 | -2.9297 | 0.1831 | 0.27466 | 0.26093 | 0.1831 | 0.10986 | -0.027466 | 0.086975 | -0.004578 | 1.2268 | 0.20142 | 0.11444 | -0.10529 | 120.4147 | 120.3415 | -0.041199 | 120.3964 | 120.4147 | 0.073242 | -0.054932 | 120.5429 | 120.4422 | 94.9173 | -120.4605 | 120.5063 | 120.4926 | 117.3019 | -0.20599
1456.5 | 120.7169 | -120.2637 | 0.3067 | -0.013122 | 0.017682 | 0.069908 | 0.0090533 | 0.064448 | -0.0019739 | -0.0027258 | -0.0040437 | 0.025353 | -0.0091345 | 0.020956 | 0.0016963 | -0.010042 | 0.2655 | -119.0186 | -24.8657 | -120.0119 | 0.30212 | -120.3186 | -120.1904 | 0.19226 | -2.9938 | 0.19684 | 0.25177 | 0.27008 | 0.19684 | 0.10529 | -0.054932 | 0.073242 | -0.004578 | 1.2451 | 0.25177 | 0.17853 | -0.041199 | 120.4605 | 120.369 | -0.054932 | 120.4559 | 120.4605 | 0.091552 | -0.036621 | 120.5658 | 120.5292 | 95.3979 | -120.4971 | 120.5154 | 120.5338 | 117.2699 | -0.20142
1458.25 | 120.6528 | -120.314 | 0.33875 | -0.0054933 | 0.012982 | 0.068413 | 0.00072207 | 0.062312 | -0.00026494 | -0.0025122 | -0.0040437 | 0.025566 | -0.011057 | 0.022452 | 0.0034051 | -0.010042 | 0.27008 | -119.0643 | -25.8774 | -120.108 | 0.29297 | -120.3232 | -120.1996 | 0.19684 | -3.0579 | 0.19226 | 0.2655 | 0.24261 | 0.17853 | 0.11444 | -0.009155 | 0.11444 | -0.045776 | 1.2497 | 0.20599 | 0.091553 | -0.068664 | 120.4926 | 120.4285 | -0.073242 | 120.5109 | 120.5063 | 0.07782 | -0.09613 | 120.607 | 120.5841 | 94.4366 | -120.5383 | 120.5795 | 120.5566 | 117.2562 | -0.2243
1459.9844 | 120.7031 | -120.369 | 0.31586 | -0.020752 | 0.011914 | 0.072258 | 0.0032855 | 0.065943 | -0.0019739 | -0.0025122 | -0.0040437 | 0.026848 | -0.014689 | 0.022025 | 0.0053279 | -0.010256 | 0.25635 | -119.0826 | -26.5823 | -120.1218 | 0.28839 | -120.3644 | -120.2454 | 0.1831 | -3.1036 | 0.17395 | 0.25177 | 0.25177 | 0.21057 | 0.09613 | 0.004578 | 0.1236 | -0.027466 | 1.2863 | 0.24719 | 0.1236 | -0.059509 | 120.5795 | 120.4651 | -0.064087 | 120.5521 | 120.5429 | 0.07782 | -0.064087 | 120.6573 | 120.6253 | 93.7866 | -120.5612 | 120.6207 | 120.6207 | 117.2653 | -0.21973
1461.6562 | 120.8588 | -120.3369 | 0.3067 | -0.013122 | 0.012982 | 0.070122 | 0.0060627 | 0.064448 | -0.0028283 | -0.002085 | -0.0040437 | 0.025994 | -0.011484 | 0.020316 | 0.0019099 | -0.0091878 | 0.2655 | -119.0689 | -25.8087 | -120.1263 | 0.3067 | -120.3918 | -120.2545 | 0.21057 | -3.0304 | 0.24261 | 0.23346 | 0.24261 | 0.19226 | 0.1236 | -0.054932 | 0.082397 | 0 | 1.268 | 0.21057 | 0.12817 | -0.041199 | 120.5292 | 120.4605 | -0.073243 | 120.5475 | 120.5795 | 0.11902 | -0.064087 | 120.6436 | 120.6024 | 94.5282 | -120.5612 | 120.5704 | 120.5795 | 117.3065 | -0.18311
1463.4062 | 120.813 | -120.3644 | 0.34332 | -0.0054933 | 0.014477 | 0.069054 | 0.0028583 | 0.067011 | 0.0042213 | -0.0029394 | -0.011673 | 0.030693 | -0.013193 | 0.02352 | 0.0081049 | -0.010256 | 0.24719 | -119.1559 | -25.708 | -120.1813 | 0.30212 | -120.4468 | -120.314 | 0.21515 | -3.0808 | 0.19684 | 0.25177 | 0.24719 | 0.17853 | 0.1236 | -0.082397 | 0.050354 | -0.041199 | 1.2085 | 0.18311 | 0.13275 | -0.096131 | 120.5429 | 120.488 | -0.091553 | 120.5795 | 120.5612 | 0.073242 | -0.096131 | 120.6665 | 120.6116 | 94.6564 | -120.6573 | 120.6161 | 120.6116 | 117.2836 | -0.21973
1465.0938 | 120.8862 | -120.3873 | 0.28381 | -0.013122 | 0.017682 | 0.069267 | 0.0056355 | 0.064234 | 0.00037606 | -0.0022986 | -0.0040437 | 0.027489 | -0.01063 | 0.022452 | 0.0034051 | -0.01047 | 0.18768 | -119.2383 | -24.9893 | -120.2408 | 0.35248 | -120.4788 | -120.3506 | 0.11902 | -3.2181 | 0.091553 | 0.31586 | 0.28381 | 0.16479 | 0.068665 | -0.091553 | 0.036621 | 0.068665 | 1.149 | 0.14648 | 0.10986 | -0.09613 | 120.5521 | 120.4559 | 0.032044 | 120.5063 | 120.4788 | 0.022888 | 0 | 120.7397 | 120.575 | 95.3979 | -120.6345 | 120.7031 | 120.6711 | 117.1692 | -0.21515
1466.8438 | 120.8176 | -120.4514 | 0.32501 | -0.0054933 | 0.016186 | 0.067772 | 0.00050847 | 0.064662 | 0.0050757 | -0.0018714 | -0.011673 | 0.030693 | -0.0089209 | 0.022025 | 0.0057551 | -0.011111 | 0.16937 | -119.2703 | -26.4267 | -120.2591 | 0.33417 | -120.5063 | -120.3552 | 0.15564 | -3.1631 | 0.068665 | 0.28839 | 0.29297 | 0.14648 | 0.10071 | -0.054932 | 0.09613 | 0.009155 | 1.181 | 0.19226 | 0.096131 | -0.15564 | 120.5978 | 120.5521 | -0.036621 | 120.607 | 120.52 | -0.032043 | -0.032043 | 120.7855 | 120.6207 | 94.0247 | -120.6802 | 120.7397 | 120.7443 | 117.2882 | -0.2243
1468.5781 | 120.8313 | -120.4651 | 0.32501 | 0.0021362 | 0.013196 | 0.069481 | 0.0056355 | 0.062953 | -0.0058191 | -0.0014442 | -0.0040437 | 0.024071 | -0.010843 | 0.020316 | 0.0012689 | -0.008547 | 0.21973 | -119.1925 | -24.2157 | -120.2637 | 0.3067 | -120.4788 | -120.3552 | 0.17853 | -3.0121 | 0.16937 | 0.24719 | 0.25635 | 0.19226 | 0.12817 | -0.013733 | 0.10986 | -0.01831 | 1.2726 | 0.20142 | 0.091553 | -0.10529 | 120.6573 | 120.5933 | -0.07782 | 120.6436 | 120.6345 | 0.041199 | -0.068664 | 120.7718 | 120.6848 | 96.2494 | -120.6802 | 120.7123 | 120.7214 | 117.453 | -0.19684
1470.2656 | 120.9412 | -120.4559 | 0.32501 | 0.0021362 | 0.017468 | 0.069695 | 0.0064899 | 0.066798 | -0.0015465 | -0.0012306 | 0.0035858 | 0.026421 | -0.0099891 | 0.020316 | 0.0031915 | -0.0087606 | 0.26093 | -119.1788 | -23.4467 | -120.2316 | 0.3067 | -120.52 | -120.4056 | 0.27466 | -2.7786 | 0.20142 | 0.25635 | 0.2655 | 0.19684 | 0.11902 | -0.064087 | 0.050354 | -0.01831 | 1.2772 | 0.22431 | 0.17395 | -0.064087 | 120.6528 | 120.575 | -0.068664 | 120.7306 | 120.6573 | 0.082397 | -0.059509 | 120.7626 | 120.7169 | 97.0093 | -120.7306 | 120.7123 | 120.7214 | 117.6773 | -0.20599
1472 | 120.9915 | -120.4697 | 0.28839 | -0.013122 | 0.014477 | 0.070122 | 0.0045673 | 0.066371 | -0.0038965 | -0.0022986 | -0.0040437 | 0.024925 | -0.012766 | 0.019888 | 0.0010553 | -0.0081198 | 0.25177 | -119.2245 | -23.6984 | -120.2682 | 0.3067 | -120.52 | -120.3918 | 0.27924 | -2.6871 | 0.22888 | 0.26093 | 0.25635 | 0.22888 | 0.1236 | -0.050354 | 0.07782 | 0.018311 | 1.2451 | 0.20142 | 0.1236 | -0.036621 | 120.6985 | 120.5933 | -0.027466 | 120.7489 | 120.6985 | 0.10529 | -0.032043 | 120.7764 | 120.7214 | 96.7712 | -120.6802 | 120.7306 | 120.726 | 117.7826 | -0.1648
1473.7344 | 121.0007 | -120.52 | 0.30212 | -0.020752 | 0.018109 | 0.067772 | 0.0079853 | 0.065943 | -0.00026494 | -0.0018714 | 0.0035858 | 0.029412 | -0.0093481 | 0.02352 | 0.0027643 | -0.012179 | 0.20142 | -119.3527 | -23.053 | -120.3598 | 0.3479 | -120.5978 | -120.4697 | 0.20142 | -2.8381 | 0.086975 | 0.3067 | 0.30212 | 0.15106 | 0.068665 | -0.077819 | 0.050354 | 0.045776 | 1.1673 | 0.16022 | 0.10986 | -0.10071 | 120.6711 | 120.5887 | 0.004578 | 120.7214 | 120.607 | 0.01831 | 0 | 120.8679 | 120.7214 | 97.467 | -120.7718 | 120.8267 | 120.8221 | 117.6819 | -0.23346
1475.4844 | 121.019 | -120.5475 | 0.32044 | -0.013122 | 0.017254 | 0.069267 | 0.0056355 | 0.065089 | 0.00058966 | -0.002085 | -0.0040437 | 0.027916 | -0.0095619 | 0.021384 | 0.0046869 | -0.0096152 | 0.17395 | -119.3436 | -23.1903 | -120.3827 | 0.34332 | -120.6299 | -120.488 | 0.19226 | -2.7466 | 0.091553 | 0.30212 | 0.27924 | 0.15564 | 0.086975 | -0.082398 | 0.059509 | 0.022888 | 1.2039 | 0.16479 | 0.10529 | -0.14649 | 120.7031 | 120.6345 | -0.018311 | 120.7397 | 120.639 | 0.004578 | -0.041199 | 120.8908 | 120.7214 | 97.3572 | -120.8084 | 120.8496 | 120.8267 | 117.8009 | -0.23346
1477.1562 | 120.9457 | -120.5658 | 0.3479 | -0.0054933 | 0.017895 | 0.069695 | 0.0047809 | 0.067225 | 0.0046485 | -0.0012306 | 0.0035858 | 0.03048 | -0.0095619 | 0.021384 | 0.0083185 | -0.010256 | 0.26093 | -119.3298 | -23.9548 | -120.3735 | 0.34332 | -120.6436 | -120.4971 | 0.25635 | -2.8015 | 0.10986 | 0.29297 | 0.27008 | 0.20142 | 0.07782 | -0.07782 | 0.068665 | -0.004577 | 1.236 | 0.19226 | 0.1236 | -0.086975 | 120.7672 | 120.6436 | -0.054931 | 120.8221 | 120.6757 | 0.032043 | -0.077819 | 120.9091 | 120.8267 | 96.611 | -120.845 | 120.8588 | 120.8359 | 117.7643 | -0.27008
1478.9062 | 120.9686 | -120.6162 | 0.33875 | 0.0097657 | 0.016186 | 0.069695 | 0.0056355 | 0.066371 | -0.0021875 | 5.1244e-05 | 0.0035858 | 0.025566 | -0.010203 | 0.020529 | 0.0055415 | -0.0070516 | 0.27924 | -119.2612 | -23.497 | -120.3278 | 0.32501 | -120.6162 | -120.4926 | 0.25177 | -2.9022 | 0.2243 | 0.2243 | 0.22888 | 0.20599 | 0.13275 | 0 | 0.1236 | -0.013733 | 1.355 | 0.28839 | 0.16479 | -0.059509 | 120.8221 | 120.7489 | -0.11444 | 120.8679 | 120.8405 | 0.091553 | -0.10986 | 120.9412 | 120.8954 | 97.1191 | -120.8313 | 120.8405 | 120.845 | 117.7139 | -0.20599
1480.6719 | 120.9732 | -120.6345 | 0.33417 | -0.0054933 | 0.019177 | 0.069481 | 0.0049945 | 0.06872 | 0.0029395 | -0.00016236 | -0.011673 | 0.03048 | -0.0091345 | 0.021384 | 0.0076777 | -0.0096152 | 0.19684 | -119.4031 | -23.7946 | -120.4285 | 0.36163 | -120.6848 | -120.5338 | 0.13275 | -2.8519 | 0.07782 | 0.28839 | 0.28839 | 0.17395 | 0.10071 | -0.050354 | 0.10071 | 0.027466 | 1.2314 | 0.20599 | 0.10529 | -0.13733 | 120.8084 | 120.7352 | -0.045776 | 120.7672 | 120.7123 | -0.022888 | -0.045776 | 120.9961 | 120.8313 | 96.8399 | -120.8679 | 120.9229 | 120.9229 | 117.7826 | -0.23346
1482.3438 | 121.019 | -120.639 | 0.33875 | -0.0054933 | 0.0164 | 0.07119 | 0.0045673 | 0.065943 | -0.0032555 | 0.00069204 | -0.011673 | 0.025139 | -0.012552 | 0.018607 | 0.0066095 | -0.0070516 | 0.26093 | -119.3115 | -23.6801 | -120.369 | 0.3067 | -120.639 | -120.52 | 0.25177 | -2.9022 | 0.21973 | 0.24261 | 0.26093 | 0.20142 | 0.13275 | 0 | 0.11902 | -0.032043 | 1.3275 | 0.27008 | 0.15106 | -0.07782 | 120.8405 | 120.7718 | -0.09613 | 120.8908 | 120.8588 | 0.086976 | -0.07782 | 120.9457 | 120.9 | 96.9589 | -120.8588 | 120.8817 | 120.9 | 117.7368 | -0.20599
1484.0156 | 121.1243 | -120.6024 | 0.29755 | 0.0021362 | 0.017254 | 0.06884 | 0.0096943 | 0.06573 | -0.0045373 | -0.0014442 | -0.011673 | 0.024071 | -0.0097755 | 0.019675 | 0.00041446 | -0.0081198 | 0.27924 | -119.3253 | -23.2773 | -120.3781 | 0.28381 | -120.694 | -120.5475 | 0.22888 | -2.7786 | 0.23346 | 0.25635 | 0.26093 | 0.21973 | 0.13275 | -0.091553 | 0.054932 | -0.013733 | 1.2772 | 0.2243 | 0.16937 | -0.01831 | 120.8221 | 120.7352 | -0.041198 | 120.8313 | 120.8359 | 0.10071 | -0.036621 | 120.8862 | 120.8817 | 97.3251 | -120.845 | 120.8588 | 120.8633 | 117.8238 | -0.16479
1485.7656 | 121.1746 | -120.6299 | 0.31128 | -0.020752 | 0.015973 | 0.069267 | 0.0084125 | 0.067225 | 0.00037606 | -0.0025122 | 0.0035858 | 0.027489 | -0.0074255 | 0.020956 | 0.0025507 | -0.0096152 | 0.1831 | -119.4763 | -23.6755 | -120.4926 | 0.35248 | -120.7306 | -120.6024 | 0.11902 | -3.0167 | 0.082397 | 0.29297 | 0.30212 | 0.16479 | 0.086975 | -0.10071 | 0.027466 | 0.041199 | 1.1536 | 0.13733 | 0.10986 | -0.12817 | 120.7947 | 120.7169 | -0.01831 | 120.7489 | 120.7123 | -0.004578 | -0.009155 | 120.9824 | 120.813 | 96.9543 | -120.9137 | 120.9229 | 120.932 | 117.6132 | -0.2243
1487.5 | 121.1746 | -120.6619 | 0.30212 | -0.013122 | 0.012982 | 0.070549 | 0.0054217 | 0.064448 | -0.0056055 | -0.0031532 | -0.011673 | 0.025353 | -0.011912 | 0.020529 | -0.00022634 | -0.0091878 | 0.26093 | -119.3481 | -24.1241 | -120.433 | 0.3067 | -120.726 | -120.5795 | 0.22888 | -2.8839 | 0.26093 | 0.24719 | 0.27924 | 0.21057 | 0.11902 | -0.064087 | 0.082397 | 0.004578 | 1.3138 | 0.22888 | 0.14648 | -0.041199 | 120.8725 | 120.7809 | -0.054932 | 120.8908 | 120.9229 | 0.14191 | -0.022888 | 120.9686 | 120.9229 | 96.5378 | -120.8817 | 120.9091 | 120.9412 | 117.778 | -0.18311
1489.2344 | 121.0922 | -120.7214 | 0.34332 | -0.0054933 | 0.019818 | 0.068413 | 0.0017901 | 0.064875 | 0.0033667 | -0.0014442 | -0.011673 | 0.030693 | -0.0095619 | 0.022025 | 0.0076777 | -0.011111 | 0.19226 | -119.5358 | -24.2981 | -120.5475 | 0.3479 | -120.7672 | -120.6345 | 0.13275 | -3.3371 | 0.068665 | 0.27924 | 0.27924 | 0.18768 | 0.091553 | -0.045776 | 0.086976 | 0.004577 | 1.1856 | 0.17395 | 0.086975 | -0.15106 | 120.9091 | 120.813 | -0.064087 | 120.8542 | 120.7901 | -0.022888 | -0.064087 | 121.0693 | 120.9137 | 96.4233 | -120.9778 | 121.0007 | 121.0007 | 117.3843 | -0.25177
1490.9844 | 121.2021 | -120.6802 | 0.3067 | -0.013122 | 0.013623 | 0.071403 | 0.0073443 | 0.065089 | -0.0058191 | -0.0014442 | -0.019302 | 0.024498 | -0.010203 | 0.019034 | 0.0021235 | -0.0079062 | 0.21057 | -119.4397 | -24.408 | -120.4971 | 0.31128 | -120.7718 | -120.6345 | 0.20599 | -3.1769 | 0.22888 | 0.23804 | 0.25177 | 0.21515 | 0.11444 | -0.091553 | 0.045777 | 0.004577 | 1.2405 | 0.18311 | 0.13733 | -0.096131 | 120.8954 | 120.7947 | -0.068665 | 120.8862 | 120.9091 | 0.11444 | -0.054932 | 120.9915 | 120.8908 | 96.2723 | -120.9412 | 120.9183 | 120.932 | 117.5034 | -0.19226
1492.6562 | 121.2387 | -120.6985 | 0.29755 | -0.013122 | 0.020031 | 0.067131 | 0.0047809 | 0.066798 | 0.00058966 | -0.0014442 | -0.0040437 | 0.03048 | -0.0087073 | 0.022665 | 0.0046869 | -0.011965 | 0.24719 | -119.5038 | -24.8291 | -120.5154 | 0.3479 | -120.8221 | -120.6894 | 0.17853 | -3.566 | 0.13733 | 0.29297 | 0.27924 | 0.1831 | 0.091553 | -0.1236 | 0.009155 | 0.050354 | 1.1948 | 0.18311 | 0.17395 | -0.050354 | 120.8817 | 120.7901 | -0.004577 | 120.8771 | 120.8359 | 0.045776 | -0.01831 | 121.0464 | 120.9457 | 95.8694 | -120.9869 | 120.9915 | 120.9778 | 117.1326 | -0.20599
1494.3906 | 121.2204 | -120.7306 | 0.32959 | 0.0021362 | 0.018322 | 0.068413 | 0.0088397 | 0.064875 | 0.00037606 | -0.0014442 | -0.011673 | 0.028557 | -0.0080665 | 0.024374 | 0.0029779 | -0.0087606 | 0.19226 | -119.5358 | -25.0671 | -120.5841 | 0.32959 | -120.8267 | -120.6848 | 0.12817 | -3.7537 | 0.10529 | 0.28839 | 0.28839 | 0.20142 | 0.10071 | -0.09613 | 0.045777 | 0 | 1.1948 | 0.14648 | 0.10071 | -0.13733 | 120.932 | 120.8313 | -0.041199 | 120.8588 | 120.8359 | 0.004578 | -0.041199 | 121.0602 | 120.9229 | 95.6635 | -121.0144 | 121.019 | 121.019 | 116.9769 | -0.22888
1496.125 | 121.2158 | -120.7764 | 0.31128 | -0.0054933 | 0.020459 | 0.069267 | 0.0032855 | 0.064234 | 0.0042213 | -0.00080316 | -0.0040437 | 0.028343 | -0.010203 | 0.020316 | 0.0078913 | -0.010897 | 0.25177 | -119.5129 | -25.5203 | -120.5658 | 0.32959 | -120.8221 | -120.7077 | 0.17395 | -3.7216 | 0.1236 | 0.2655 | 0.2655 | 0.17395 | 0.10071 | -0.045777 | 0.068664 | 0.018311 | 1.2634 | 0.21057 | 0.14191 | -0.059509 | 120.9503 | 120.8771 | -0.045776 | 120.9503 | 120.9 | 0.022888 | -0.045776 | 121.106 | 121.0281 | 95.256 | -121.019 | 121.0419 | 121.0419 | 117.0547 | -0.21057
1497.7969 | 121.2799 | -120.7718 | 0.27924 | -0.013122 | 0.014905 | 0.06884 | 0.0064899 | 0.065089 | -0.0053919 | -0.0040076 | -0.0040437 | 0.024285 | -0.011698 | 0.018393 | 0.0021235 | -0.0081198 | 0.24719 | -119.426 | -25.7812 | -120.5429 | 0.29755 | -120.8405 | -120.7214 | 0.2243 | -3.5522 | 0.24261 | 0.2243 | 0.2243 | 0.19684 | 0.10071 | -0.068664 | 0.050354 | 0.01831 | 1.3458 | 0.22888 | 0.17853 | -0.032044 | 120.9686 | 120.8725 | -0.054932 | 120.9961 | 121.0144 | 0.14191 | -0.054932 | 121.0693 | 121.019 | 94.9905 | -121.0007 | 120.9961 | 120.9961 | 117.2195 | -0.17853
1499.5312 | 121.3074 | -120.8084 | 0.2655 | -0.0054933 | 0.014477 | 0.070549 | 0.0060627 | 0.067652 | -0.0049645 | -0.0040076 | -0.0040437 | 0.025994 | -0.012766 | 0.019888 | -0.0010809 | -0.010042 | 0.26093 | -119.4809 | -25.6714 | -120.5658 | 0.28839 | -120.8359 | -120.7077 | 0.21057 | -3.9001 | 0.26093 | 0.21515 | 0.2243 | 0.19684 | 0.11902 | -0.027465 | 0.10071 | 0.022888 | 1.3275 | 0.24262 | 0.14191 | -0.004578 | 121.0052 | 120.9274 | -0.050354 | 121.019 | 121.0693 | 0.14191 | -0.041199 | 121.0968 | 121.0693 | 95.137 | -120.9732 | 121.0236 | 121.0327 | 116.9083 | -0.14648
1501.2188 | 121.2845 | -120.7993 | 0.28381 | -0.0054933 | 0.013623 | 0.071403 | 0.0052081 | 0.065943 | -0.0058191 | -0.0016578 | -0.011673 | 0.025353 | -0.0091345 | 0.019675 | 0.0038325 | -0.0094016 | 0.18768 | -119.577 | -26.0651 | -120.6299 | 0.28839 | -120.8633 | -120.7443 | 0.16479 | -3.9413 | 0.17853 | 0.23804 | 0.23346 | 0.20142 | 0.10071 | -0.064087 | 0.054931 | 0.004578 | 1.2222 | 0.16937 | 0.11444 | -0.09613 | 121.0007 | 120.9 | -0.045776 | 120.9641 | 120.9778 | 0.07782 | -0.050354 | 121.0876 | 120.9869 | 94.7342 | -121.0281 | 121.0373 | 121.0327 | 116.8579 | -0.1831
1502.9531 | 121.2524 | -120.8725 | 0.28381 | 0.0021362 | 0.017254 | 0.069908 | -0.00055973 | 0.064662 | 0.0033667 | -0.0016578 | -0.019302 | 0.027489 | -0.010416 | 0.020956 | 0.0076777 | -0.0098288 | 0.26093 | -119.5587 | -26.5778 | -120.6024 | 0.29755 | -120.9 | -120.7581 | 0.24261 | -4.216 | 0.17395 | 0.2243 | 0.23346 | 0.19226 | 0.10986 | -0.027465 | 0.11444 | 0.013733 | 1.3138 | 0.27008 | 0.15564 | -0.022888 | 121.0648 | 120.9824 | -0.059509 | 121.1151 | 121.0464 | 0.064087 | -0.050354 | 121.17 | 121.1334 | 94.2947 | -121.0419 | 121.0968 | 121.106 | 116.6565 | -0.17395
1504.625 | 121.2067 | -120.9091 | 0.29755 | -0.0054933 | 0.014264 | 0.069054 | 0.0022175 | 0.065302 | -0.00047854 | 5.1244e-05 | -0.011673 | 0.025139 | -0.011912 | 0.021597 | 0.0055415 | -0.010256 | 0.25635 | -119.6365 | -26.5686 | -120.6162 | 0.27466 | -120.9091 | -120.7718 | 0.21515 | -4.2023 | 0.20142 | 0.23804 | 0.21515 | 0.20142 | 0.10986 | 0 | 0.13733 | -0.022888 | 1.2726 | 0.29297 | 0.15564 | -0.041198 | 121.1105 | 121.019 | -0.059509 | 121.1243 | 121.1105 | 0.091553 | -0.082397 | 121.1838 | 121.1655 | 94.3405 | -121.0693 | 121.1472 | 121.1243 | 116.7068 | -0.18768
1506.375 | 121.2341 | -120.8908 | 0.31586 | -0.020752 | 0.019604 | 0.068413 | 0.0041401 | 0.067011 | 0.0027259 | -0.0027258 | -0.019302 | 0.031121 | -0.01063 | 0.018607 | 0.0057551 | -0.01047 | 0.17853 | -119.8013 | -27.2964 | -120.7077 | 0.32044 | -120.9503 | -120.8221 | 0.1236 | -4.5136 | 0.054932 | 0.27008 | 0.27924 | 0.16479 | 0.07782 | -0.059509 | 0.068664 | 0.004578 | 1.0895 | 0.18311 | 0.11444 | -0.13733 | 121.0556 | 120.9686 | -0.045776 | 121.0144 | 120.9457 | -0.022888 | -0.036621 | 121.2112 | 121.0693 | 93.5944 | -121.138 | 121.1609 | 121.17 | 116.3773 | -0.23804
1508.1094 | 121.2708 | -120.9274 | 0.27924 | -0.0054933 | 0.013409 | 0.069695 | 0.0034991 | 0.065089 | -0.0053919 | -0.00016236 | 0.0035858 | 0.025139 | -0.011271 | 0.018393 | 0.0036189 | -0.0079062 | 0.18768 | -119.7418 | -26.2115 | -120.694 | 0.26093 | -120.9549 | -120.7993 | 0.14191 | -4.3304 | 0.14191 | 0.21515 | 0.20599 | 0.15564 | 0.086975 | -0.027466 | 0.12817 | -0.018311 | 1.1856 | 0.23346 | 0.10529 | -0.091553 | 121.0831 | 121.0144 | -0.064087 | 121.0693 | 121.0693 | 0.054932 | -0.073242 | 121.1884 | 121.1151 | 94.7159 | -121.0785 | 121.1426 | 121.1334 | 116.597 | -0.19226
1509.8594 | 121.3531 | -120.9183 | 0.29297 | -0.0054933 | 0.0164 | 0.070549 | 0.0064899 | 0.065943 | -0.0032555 | -0.0025122 | -0.011673 | 0.024498 | -0.010203 | 0.019888 | 0.0021235 | -0.0072652 | 0.19226 | -119.7372 | -26.4175 | -120.7169 | 0.27924 | -120.9686 | -120.813 | 0.16937 | -4.3396 | 0.16937 | 0.2243 | 0.21515 | 0.15564 | 0.086975 | -0.050354 | 0.10529 | -0.013733 | 1.181 | 0.20142 | 0.09613 | -0.10071 | 121.0739 | 121.0052 | -0.068665 | 121.0876 | 121.0876 | 0.082398 | -0.07782 | 121.1975 | 121.1105 | 94.5007 | -121.106 | 121.1426 | 121.1334 | 116.5787 | -0.20599
1511.5469 | 121.2891 | -120.9869 | 0.3067 | -0.013122 | 0.019818 | 0.068626 | 0.0028583 | 0.065516 | 0.0048621 | -0.0014442 | -0.0040437 | 0.031761 | -0.0084937 | 0.022238 | 0.0081049 | -0.011538 | 0.23346 | -119.7556 | -27.3239 | -120.7397 | 0.28839 | -121.0052 | -120.8908 | 0.15106 | -4.4403 | 0.050354 | 0.23804 | 0.2655 | 0.15106 | 0.068665 | -0.018311 | 0.09613 | -0.018311 | 1.2314 | 0.24719 | 0.15106 | -0.073243 | 121.138 | 121.0556 | -0.068665 | 121.138 | 121.0373 | -0.018311 | -0.041199 | 121.2753 | 121.2204 | 93.663 | -121.1975 | 121.225 | 121.2524 | 116.5466 | -0.23804
1513.2969 | 121.4218 | -120.9229 | 0.27008 | -0.013122 | 0.013409 | 0.070549 | 0.0073443 | 0.065302 | -0.0038965 | -0.0022986 | -0.0040437 | 0.024071 | -0.010416 | 0.01882 | 0.0010553 | -0.0079062 | 0.24261 | -119.6823 | -27.2415 | -120.6802 | 0.2655 | -121.0144 | -120.8633 | 0.20142 | -4.5273 | 0.21973 | 0.19226 | 0.21973 | 0.17853 | 0.09613 | -0.091552 | 0.05951 | -0.004578 | 1.2405 | 0.24262 | 0.1831 | -0.027466 | 121.1014 | 121.019 | -0.07782 | 121.1243 | 121.1426 | 0.1236 | -0.050354 | 121.1884 | 121.1655 | 93.6813 | -121.1334 | 121.1151 | 121.1426 | 116.3956 | -0.17395
1514.9688 | 121.4447 | -120.9503 | 0.25635 | -0.013122 | 0.019177 | 0.067345 | 0.0099079 | 0.067225 | 0.0014441 | -0.0027258 | -0.0040437 | 0.028771 | -0.0074255 | 0.021597 | 0.0021235 | -0.010683 | 0.16479 | -119.8242 | -28.006 | -120.7901 | 0.33875 | -121.0556 | -120.9137 | 0.10529 | -4.7882 | 0.050354 | 0.27008 | 0.24261 | 0.13275 | 0.064087 | -0.10529 | 0.036621 | 0.082397 | 1.1261 | 0.16022 | 0.1236 | -0.091553 | 121.0831 | 121.0144 | 0.013733 | 121.0556 | 121.0007 | -0.013733 | -0.013733 | 121.2891 | 121.1151 | 92.9443 | -121.17 | 121.2204 | 121.1929 | 116.1621 | -0.19226
1516.7188 | 121.3715 | -120.9778 | 0.27008 | -0.020752 | 0.017895 | 0.067131 | 0.0026447 | 0.065302 | 0.0042213 | -0.0010168 | 0.0035858 | 0.031334 | -0.010203 | 0.021384 | 0.0083185 | -0.010683 | 0.24261 | -119.7601 | -26.6647 | -120.7581 | 0.30212 | -121.0464 | -120.9137 | 0.16937 | -4.509 | 0.091553 | 0.25635 | 0.24261 | 0.15564 | 0.073242 | -0.068665 | 0.064087 | 0.032043 | 1.2177 | 0.21973 | 0.15564 | -0.027466 | 121.1334 | 121.051 | -0.013733 | 121.1472 | 121.0693 | 0.018311 | -0.027466 | 121.2799 | 121.2204 | 94.313 | -121.1838 | 121.2341 | 121.2204 | 116.4688 | -0.19684
1518.4531 | 121.4264 | -120.9686 | 0.28381 | -0.0054933 | 0.017041 | 0.069695 | 0.0084125 | 0.066584 | -0.00069214 | -0.0010168 | 0.0035858 | 0.028557 | -0.0078529 | 0.020102 | 0.0021235 | -0.006838 | 0.13733 | -119.8013 | -25.882 | -120.8176 | 0.32501 | -121.0693 | -120.9274 | 0.091553 | -4.4312 | 0.073242 | 0.27008 | 0.25635 | 0.14648 | 0.050354 | -0.10071 | 0.041199 | 0.041199 | 1.1673 | 0.15106 | 0.10986 | -0.14648 | 121.1151 | 121.019 | -0.013732 | 121.0602 | 121.0419 | 0.022888 | -0.027465 | 121.2936 | 121.106 | 95.0867 | -121.2112 | 121.2387 | 121.225 | 116.5375 | -0.23346
1520.125 | 121.344 | -121.2158 | 0.14191 | -0.020752 | 0.01875 | 0.067986 | 0.0030719 | 0.067866 | 0.0033667 | 5.1244e-05 | -0.011673 | 0.029625 | -0.010416 | 0.020956 | 0.0072505 | -0.0098288 | -0.027466 | -120.0119 | -26.4633 | -120.9869 | 0.1236 | -121.2204 | -121.0922 | -0.050354 | -4.4952 | -0.14191 | 0.091553 | 0.091553 | -0.018311 | -0.1236 | -0.004578 | 0.1236 | -0.018311 | 1.2039 | 0.22888 | 0.10529 | -0.16937 | 121.1975 | 121.0922 | -0.050354 | 121.1655 | 121.0739 | -0.018311 | -0.050354 | 121.3394 | 121.1884 | 94.7525 | -121.2341 | 121.3074 | 121.3074 | 116.7206 | -0.2655
1521.875 | 121.4355 | -121.1563 | 0.10986 | -0.020752 | 0.0164 | 0.07119 | 0.0086261 | 0.065089 | -0.0030419 | 0.00026484 | -0.011673 | 0.026207 | -0.0097755 | 0.019888 | -0.00022634 | -0.0076926 | 0.032043 | -119.9112 | -25.7538 | -120.9366 | 0.10986 | -121.225 | -121.0785 | -0.027466 | -4.3854 | -0.032043 | 0.059509 | 0.064087 | -0.013733 | -0.073242 | -0.068665 | 0.07782 | 0 | 1.2451 | 0.21973 | 0.14191 | -0.07782 | 121.1426 | 121.0831 | -0.050354 | 121.1288 | 121.1243 | 0.041199 | -0.045776 | 121.2662 | 121.1884 | 95.4025 | -121.1884 | 121.2158 | 121.2204 | 116.7709 | -0.18311
1523.625 | 121.3898 | -121.2296 | 0.14191 | -0.0054933 | 0.012982 | 0.069481 | 0.0071307 | 0.064875 | -0.0032555 | -0.0014442 | -0.011673 | 0.025353 | -0.0080665 | 0.020316 | -0.00044014 | -0.0081198 | 0.013733 | -119.9661 | -25.621 | -120.9732 | 0.11444 | -121.2387 | -121.106 | -0.018311 | -4.3304 | -0.018311 | 0.059509 | 0.068665 | 0.022888 | -0.086975 | -0.009155 | 0.1236 | -0.027466 | 1.2634 | 0.25635 | 0.13275 | -0.12817 | 121.2524 | 121.1426 | -0.082398 | 121.2112 | 121.2112 | 0.068664 | -0.073242 | 121.344 | 121.2433 | 95.6085 | -121.2479 | 121.2891 | 121.2982 | 116.8991 | -0.22888
1525.375 | 121.4264 | -121.2158 | 0.13733 | 0.0021362 | 0.017041 | 0.068199 | 0.0043537 | 0.062739 | 0.0040077 | -0.0040076 | -0.0040437 | 0.029839 | -0.011271 | 0.022665 | 0.0053279 | -0.010897 | -0.009155 | -120.0668 | -25.6393 | -121.0098 | 0.15106 | -121.2936 | -121.1563 | -0.064087 | -4.2206 | -0.11444 | 0.09613 | 0.068665 | -0.004578 | -0.09613 | -0.07782 | 0.059509 | 0.013733 | 1.149 | 0.20599 | 0.14648 | -0.14648 | 121.2112 | 121.1197 | -0.041199 | 121.1517 | 121.1014 | -0.018311 | -0.068664 | 121.3669 | 121.2067 | 95.5765 | -121.2936 | 121.3119 | 121.2845 | 116.9952 | -0.23346
1527.0469 | 121.4035 | -121.2479 | 0.13275 | -0.0054933 | 0.018963 | 0.067345 | 0.0020039 | 0.065516 | 0.0031531 | -0.00037596 | -0.0040437 | 0.028984 | -0.0087073 | 0.022665 | 0.0078913 | -0.010256 | -0.018311 | -120.0943 | -25.3326 | -121.051 | 0.14648 | -121.3028 | -121.138 | -0.068665 | -3.7537 | -0.1236 | 0.091553 | 0.07782 | -0.018311 | -0.09613 | -0.054931 | 0.10986 | 0.013733 | 1.1536 | 0.19684 | 0.086975 | -0.15106 | 121.2296 | 121.1517 | -0.041198 | 121.1792 | 121.1243 | -0.027466 | -0.054931 | 121.3943 | 121.2296 | 95.9152 | -121.2708 | 121.3394 | 121.3257 | 117.4942 | -0.22888
1528.7969 | 121.4172 | -121.2387 | 0.14648 | 0.0021362 | 0.019177 | 0.067345 | 0.0041401 | 0.063807 | 0.0014441 | -0.0018714 | -0.011673 | 0.029625 | -0.011271 | 0.021597 | 0.0057551 | -0.0076926 | -0.045776 | -120.1172 | -25.9781 | -121.0785 | 0.15106 | -121.3028 | -121.17 | -0.059509 | -3.9413 | -0.14191 | 0.082397 | 0.091553 | -0.013733 | -0.09613 | -0.064087 | 0.068664 | 0.004578 | 1.1215 | 0.16022 | 0.091553 | -0.19226 | 121.225 | 121.1426 | -0.064087 | 121.1792 | 121.0968 | -0.045777 | -0.054931 | 121.3898 | 121.1929 | 95.2606 | -121.3165 | 121.3211 | 121.3303 | 117.2974 | -0.24261
1530.5625 | 121.5042 | -121.2662 | 0.10071 | 0.0021362 | 0.015759 | 0.070763 | 0.0077717 | 0.064875 | -0.0041101 | -0.0025122 | -0.0040437 | 0.026848 | -0.0084937 | 0.020956 | 0.0014825 | -0.0089742 | -0.027466 | -120.0485 | -25.8957 | -121.0556 | 0.11444 | -121.3211 | -121.1838 | -0.086975 | -4.0787 | -0.09613 | 0.086975 | 0.082397 | -0.027466 | -0.09613 | -0.054932 | 0.082397 | 0.013733 | 1.2177 | 0.21057 | 0.12817 | -0.12817 | 121.2387 | 121.17 | -0.013733 | 121.1792 | 121.17 | 0 | -0.018311 | 121.3806 | 121.2387 | 95.3705 | -121.2845 | 121.3531 | 121.3486 | 117.1875 | -0.19684
1532.25 | 121.5042 | -121.2616 | 0.10071 | -0.013122 | 0.016827 | 0.06884 | 0.0039265 | 0.067652 | 0.0020849 | -0.0014442 | -0.0040437 | 0.028557 | -0.0091345 | 0.021811 | 0.0059687 | -0.0096152 | 0.045776 | -120.0256 | -26.2253 | -121.0236 | 0.14191 | -121.3028 | -121.2158 | -0.013733 | -4.2068 | -0.054932 | 0.086975 | 0.064087 | -0.013733 | -0.068665 | -0.041198 | 0.045777 | 0.041199 | 1.236 | 0.23804 | 0.19226 | -0.054932 | 121.2479 | 121.1929 | -0.013733 | 121.2479 | 121.2067 | 0.013733 | -0.036621 | 121.4035 | 121.3074 | 95.0363 | -121.3165 | 121.3486 | 121.3257 | 117.0547 | -0.16937
1534 | 121.4447 | -121.2753 | 0.13733 | -0.0054933 | 0.018963 | 0.068626 | 0.0028583 | 0.066584 | 0.00037606 | 0.00090584 | -0.0040437 | 0.026634 | -0.0074255 | 0.022452 | 0.0036189 | -0.0089742 | 0.004578 | -120.076 | -25.7629 | -121.0602 | 0.14648 | -121.3394 | -121.1929 | -0.027466 | -4.0604 | -0.11902 | 0.10071 | 0.068665 | -0.013733 | -0.10071 | -0.064087 | 0.082398 | 0.009155 | 1.1993 | 0.21515 | 0.13275 | -0.13275 | 121.2616 | 121.1746 | -0.036621 | 121.2479 | 121.1563 | -0.018311 | -0.068664 | 121.4218 | 121.2799 | 95.5124 | -121.3303 | 121.376 | 121.344 | 117.215 | -0.23804
1535.6875 | 121.4584 | -121.2936 | 0.11444 | -0.0054933 | 0.01875 | 0.067345 | 0.0062763 | 0.067866 | 0.0020849 | -0.0012306 | -0.019302 | 0.026207 | -0.01063 | 0.022238 | 0.0068231 | -0.010683 | 0.018311 | -120.0668 | -26.8158 | -121.0602 | 0.11902 | -121.3257 | -121.1975 | -0.027466 | -4.0146 | -0.091553 | 0.082397 | 0.073242 | -0.022888 | -0.09613 | -0.032044 | 0.09613 | 0.004578 | 1.2268 | 0.23346 | 0.13733 | -0.09613 | 121.2708 | 121.1975 | -0.032044 | 121.2662 | 121.2021 | 0.004577 | -0.041199 | 121.4127 | 121.312 | 94.4778 | -121.312 | 121.376 | 121.3669 | 117.2791 | -0.21057
1537.4219 | 121.5363 | -121.2845 | 0.10529 | -0.0054933 | 0.015759 | 0.069054 | 0.0090533 | 0.066371 | -0.0043237 | -0.002085 | -0.0040437 | 0.026207 | -0.010843 | 0.020529 | 0.0010553 | -0.0083334 | 0.059509 | -119.9707 | -26.1429 | -121.0098 | 0.10529 | -121.3211 | -121.1975 | 0.027466 | -3.8269 | 0.032043 | 0.050354 | 0.045776 | 0.009155 | -0.054932 | -0.036621 | 0.086975 | 0 | 1.3138 | 0.27466 | 0.18768 | -0.045777 | 121.2936 | 121.2296 | -0.054932 | 121.312 | 121.3165 | 0.086975 | -0.05951 | 121.3898 | 121.344 | 95.1416 | -121.3028 | 121.3348 | 121.3303 | 117.4576 | -0.16022
1539.1719 | 121.4539 | -121.3165 | 0.13275 | -0.0054933 | 0.014264 | 0.069908 | 0.0060627 | 0.06872 | -0.0030419 | -0.00058956 | -0.0040437 | 0.027275 | -0.011484 | 0.021811 | 0.0023371 | -0.0076926 | 0.073242 | -119.9982 | -25.9323 | -121.0556 | 0.11902 | -121.3303 | -121.1838 | 0.013733 | -3.6896 | 0 | 0.068665 | 0.050354 | 0.009155 | -0.059509 | -0.013733 | 0.13275 | -0.013732 | 1.3184 | 0.26093 | 0.12817 | -0.059509 | 121.3257 | 121.257 | -0.064086 | 121.3303 | 121.3165 | 0.059509 | -0.082397 | 121.4355 | 121.3898 | 95.3842 | -121.3165 | 121.3852 | 121.3669 | 117.627 | -0.19226
1540.9375 | 121.5729 | -121.2708 | 0.082397 | -0.0054933 | 0.015759 | 0.071403 | 0.0045673 | 0.067011 | -0.0043237 | -0.0040076 | -0.0040437 | 0.023857 | -0.011057 | 0.021811 | 0.0021235 | -0.0089742 | 0.086975 | -119.9661 | -25.3693 | -121.0556 | 0.10986 | -121.3303 | -121.2067 | 0.054932 | -3.5797 | 0.059509 | 0.036621 | 0.054932 | 0.018311 | -0.045776 | -0.059509 | 0.064087 | 0.027466 | 1.3046 | 0.21515 | 0.15106 | 0.004578 | 121.2891 | 121.225 | -0.045776 | 121.3257 | 121.3303 | 0.10528 | -0.027465 | 121.3806 | 121.3577 | 95.9015 | -121.2891 | 121.3074 | 121.3257 | 117.691 | -0.12817
1542.625 | 121.637 | -121.2845 | 0.10986 | -0.013122 | 0.01875 | 0.067345 | 0.0075581 | 0.066157 | 0.0012305 | -0.0014442 | -0.011673 | 0.029625 | -0.0076393 | 0.022665 | 0.0040461 | -0.0096152 | 0.013733 | -120.1126 | -24.733 | -121.1288 | 0.15106 | -121.3898 | -121.2616 | -0.027466 | -3.9185 | -0.10071 | 0.09613 | 0.091553 | -0.027466 | -0.073242 | -0.10529 | 0.022888 | 0.041199 | 1.1719 | 0.15564 | 0.13275 | -0.09613 | 121.257 | 121.2112 | -0.013733 | 121.257 | 121.1838 | -0.027466 | -0.01831 | 121.4355 | 121.2982 | 96.5515 | -121.3715 | 121.3806 | 121.376 | 117.366 | -0.18311
1544.375 | 121.6324 | -121.3028 | 0.086975 | -0.013122 | 0.014477 | 0.069695 | 0.0052081 | 0.06338 | -0.0049645 | -0.0027258 | -0.0040437 | 0.023644 | -0.010203 | 0.022238 | 0.0016963 | -0.010897 | 0.091553 | -119.9844 | -25.0397 | -121.0693 | 0.11902 | -121.3623 | -121.257 | 0.036621 | -3.479 | 0.054932 | 0.045776 | 0.054932 | 0.004578 | -0.059509 | -0.05951 | 0.045776 | 0.032044 | 1.3184 | 0.23346 | 0.18768 | 0.004578 | 121.3074 | 121.2433 | -0.041199 | 121.3394 | 121.3577 | 0.11444 | -0.032043 | 121.4218 | 121.3943 | 96.2631 | -121.344 | 121.3486 | 121.3577 | 117.8238 | -0.14648
1546.0469 | 121.6553 | -121.3074 | 0.09613 | -0.013122 | 0.019818 | 0.067986 | 0.0058491 | 0.066584 | 0.0037939 | 0.00026484 | -0.011673 | 0.029412 | -0.0084937 | 0.023093 | 0.0057551 | -0.0098288 | 0.027466 | -120.0806 | -24.7971 | -121.106 | 0.10986 | -121.3989 | -121.2662 | 0 | -3.4836 | -0.07782 | 0.082397 | 0.10071 | 0 | -0.09613 | -0.091553 | 0.041199 | 0.013733 | 1.2268 | 0.20142 | 0.16022 | -0.068664 | 121.3074 | 121.2112 | -0.013733 | 121.3074 | 121.2296 | 0.01831 | 0.004578 | 121.4172 | 121.3348 | 96.5103 | -121.3623 | 121.3898 | 121.4081 | 117.8238 | -0.19226
1547.7969 | 121.5271 | -121.3531 | 0.1236 | -0.028381 | 0.017254 | 0.067345 | 0.0017901 | 0.064448 | 0.0035803 | -0.002085 | -0.011673 | 0.030052 | -0.010203 | 0.024374 | 0.0076777 | -0.011111 | 0.068665 | -120.0806 | -24.8383 | -121.1426 | 0.13275 | -121.4081 | -121.2708 | -0.004578 | -3.7857 | -0.091553 | 0.073242 | 0.091553 | -0.009155 | -0.068665 | -0.054932 | 0.082397 | 0.009155 | 1.2726 | 0.21057 | 0.12817 | -0.054931 | 121.344 | 121.2845 | -0.050354 | 121.3486 | 121.2616 | -0.022888 | -0.032043 | 121.4859 | 121.4218 | 96.5149 | -121.3943 | 121.4264 | 121.4447 | 117.5674 | -0.19226
1549.5312 | 121.6278 | -121.3486 | 0.11444 | -0.0054933 | 0.018536 | 0.069481 | 0.0073443 | 0.066371 | -0.0017603 | -0.0016578 | -0.0040437 | 0.027062 | -0.0084937 | 0.024161 | 0.0029779 | -0.008547 | 0 | -120.1218 | -25.1129 | -121.1609 | 0.14648 | -121.4172 | -121.2982 | -0.073242 | -3.685 | -0.09613 | 0.09613 | 0.09613 | -0.004578 | -0.091553 | -0.068664 | 0.050354 | 0.032043 | 1.2268 | 0.18768 | 0.13733 | -0.11444 | 121.344 | 121.257 | -0.018311 | 121.2753 | 121.2524 | -0.004577 | -0.018311 | 121.4951 | 121.3486 | 96.2357 | -121.4127 | 121.4447 | 121.4447 | 117.6636 | -0.20599
1551.2656 | 121.6141 | -121.3669 | 0.11444 | 0.0021362 | 0.019604 | 0.067772 | 0.0041401 | 0.06573 | 0.0029395 | -0.00016236 | -0.019302 | 0.029412 | -0.0097755 | 0.02352 | 0.0066095 | -0.0096152 | 0.059509 | -120.0485 | -25.4379 | -121.138 | 0.15106 | -121.4493 | -121.2982 | -0.013733 | -3.5614 | -0.086975 | 0.091553 | 0.073242 | 0.009155 | -0.086975 | -0.082398 | 0.068664 | 0.036621 | 1.3184 | 0.22888 | 0.16022 | -0.054932 | 121.376 | 121.2799 | -0.022888 | 121.3531 | 121.2799 | 0 | -0.041199 | 121.5179 | 121.4264 | 95.929 | -121.4127 | 121.4584 | 121.4401 | 117.8055 | -0.20142
1552.9375 | 121.5408 | -121.4127 | 0.14191 | -0.013122 | 0.014691 | 0.069695 | 0.0030719 | 0.066798 | -0.0034691 | -0.0010168 | -0.011673 | 0.025353 | -0.0097755 | 0.022665 | 0.0029779 | -0.0081198 | 0.059509 | -120.0027 | -25.2319 | -121.1243 | 0.10071 | -121.3989 | -121.2753 | 0.009155 | -3.6301 | 0.009155 | 0.050354 | 0.054932 | 0.018311 | -0.068665 | 0.013733 | 0.13733 | -0.041199 | 1.4099 | 0.28839 | 0.15106 | -0.082398 | 121.431 | 121.344 | -0.091553 | 121.4218 | 121.4218 | 0.07782 | -0.086975 | 121.5134 | 121.4722 | 96.1807 | -121.4172 | 121.463 | 121.4676 | 117.7826 | -0.21057
1554.6719 | 121.5729 | -121.3943 | 0.14191 | -0.013122 | 0.013409 | 0.069908 | 0.0026447 | 0.066584 | -0.0030419 | -0.0010168 | -0.011673 | 0.02578 | -0.010416 | 0.021597 | 0.0066095 | -0.0079062 | 0.082397 | -119.9982 | -25.3967 | -121.1472 | 0.086975 | -121.4035 | -121.257 | 0.032043 | -3.7491 | 0.022888 | 0.054932 | 0.054932 | 0.018311 | -0.064087 | -0.009155 | 0.13733 | -0.054932 | 1.3962 | 0.24719 | 0.10986 | -0.05951 | 121.4127 | 121.3303 | -0.086975 | 121.4264 | 121.4172 | 0.086975 | -0.086975 | 121.4813 | 121.4767 | 95.9976 | -121.3989 | 121.4493 | 121.4493 | 117.6453 | -0.20599
1556.4219 | 121.6644 | -121.3943 | 0.09613 | -0.0054933 | 0.016613 | 0.068413 | 0.0077717 | 0.06573 | -0.0028283 | -0.0018714 | -0.0040437 | 0.025353 | -0.0087073 | 0.021597 | -0.00086734 | -0.0096152 | 0.091553 | -120.0027 | -25.1724 | -121.1243 | 0.09613 | -121.431 | -121.2891 | 0.032043 | -3.8406 | 0.045776 | 0.054932 | 0.054932 | 0.004578 | -0.073242 | -0.036621 | 0.10529 | 0 | 1.3916 | 0.27008 | 0.16479 | -0.004577 | 121.3989 | 121.3211 | -0.041198 | 121.4264 | 121.4401 | 0.11902 | -0.041198 | 121.4905 | 121.4859 | 96.2219 | -121.3852 | 121.4493 | 121.4493 | 117.5537 | -0.16937
1558.1719 | 121.582 | -121.4355 | 0.13275 | 0.0021362 | 0.017468 | 0.067986 | 0.0039265 | 0.067011 | 0.0069983 | -0.00037596 | -0.019302 | 0.030907 | -0.010416 | 0.022025 | 0.0063959 | -0.010042 | 0.027466 | -120.1721 | -24.6552 | -121.2067 | 0.15106 | -121.463 | -121.3394 | -0.059509 | -3.9322 | -0.13275 | 0.10071 | 0.086975 | -0.018311 | -0.091553 | -0.027466 | 0.09613 | 0.018311 | 1.2634 | 0.22888 | 0.13275 | -0.10529 | 121.4172 | 121.344 | -0.032043 | 121.376 | 121.3028 | -0.041198 | -0.045776 | 121.5866 | 121.463 | 96.7804 | -121.4722 | 121.5363 | 121.5225 | 117.5034 | -0.2243
1559.9062 | 121.6461 | -121.4264 | 0.12817 | -0.0054933 | 0.016186 | 0.067345 | 0.0039265 | 0.065943 | 0.0012305 | 0.0011194 | 0.0035858 | 0.027916 | -0.010203 | 0.022452 | 0.0066095 | -0.0089742 | -0.027466 | -120.1767 | -24.7101 | -121.2341 | 0.16022 | -121.4767 | -121.3577 | -0.064087 | -3.5431 | -0.11902 | 0.07782 | 0.091553 | -0.027466 | -0.09613 | -0.050354 | 0.068665 | 0.032043 | 1.2497 | 0.19226 | 0.1236 | -0.15564 | 121.3989 | 121.3303 | -0.050354 | 121.3623 | 121.3074 | -0.022889 | -0.036621 | 121.5866 | 121.3989 | 96.7163 | -121.4859 | 121.5042 | 121.5179 | 117.8833 | -0.2243
1561.5781 | 121.6965 | -121.4081 | 0.11444 | -0.013122 | 0.017254 | 0.068626 | 0.0086261 | 0.066584 | -0.00047854 | -0.00058956 | 0.0035858 | 0.027916 | -0.0095619 | 0.022025 | 0.0021235 | -0.0079062 | -0.027466 | -120.1538 | -24.7787 | -121.2387 | 0.14191 | -121.5225 | -121.3623 | -0.091553 | -3.5065 | -0.10529 | 0.086975 | 0.086975 | -0.036621 | -0.086975 | -0.11444 | 0.045776 | 0.027466 | 1.2543 | 0.16937 | 0.1236 | -0.14191 | 121.3715 | 121.3211 | -0.027466 | 121.3165 | 121.3028 | -0.018311 | -0.027466 | 121.55 | 121.3806 | 96.6293 | -121.4767 | 121.4951 | 121.4951 | 117.9016 | -0.20142
1563.3438 | 121.6095 | -121.4493 | 0.15106 | -0.013122 | 0.015759 | 0.068413 | 0.0028583 | 0.067866 | 0.0022987 | 0.00047844 | -0.011673 | 0.03048 | -0.0089209 | 0.023734 | 0.0083185 | -0.0094016 | 0.022888 | -120.1401 | -24.8062 | -121.2158 | 0.15106 | -121.4905 | -121.3669 | -0.050354 | -3.5202 | -0.14648 | 0.07782 | 0.091553 | -0.022888 | -0.091553 | -0.041199 | 0.082398 | 0 | 1.3092 | 0.23346 | 0.15106 | -0.12817 | 121.4264 | 121.3577 | -0.073242 | 121.3989 | 121.3028 | -0.054931 | -0.059509 | 121.6003 | 121.4722 | 96.6431 | -121.5179 | 121.5271 | 121.5408 | 117.9291 | -0.24261
1565.0312 | 121.6141 | -121.4676 | 0.12817 | -0.0054933 | 0.014691 | 0.070763 | 0.0043537 | 0.063807 | -0.0045373 | -0.0012306 | -0.0040437 | 0.025139 | -0.010416 | 0.020743 | 0.0036189 | -0.0081198 | 0.045776 | -120.0897 | -24.6918 | -121.2021 | 0.091553 | -121.463 | -121.3303 | -0.24261 | -3.4378 | -0.23804 | 0.045776 | 0.054932 | -0.20599 | -0.29755 | 0.004577 | 0.13733 | -0.036621 | 1.3779 | 0.2655 | 0.12817 | -0.082398 | 121.2616 | 121.17 | -0.082398 | 121.225 | 121.2296 | 0.059509 | -0.073242 | 121.5591 | 121.5134 | 96.7758 | -121.4584 | 121.5134 | 121.5225 | 118.0298 | -0.42572
1566.7812 | 121.7056 | -121.4447 | 0.11902 | -0.0054933 | 0.020031 | 0.069695 | 0.0047809 | 0.066798 | 0.0042213 | 0.00090584 | 0.0035858 | 0.031761 | -0.0082801 | 0.024374 | 0.0049005 | -0.010256 | 0.054932 | -120.1035 | -24.4766 | -121.2067 | 0.15106 | -121.5088 | -121.376 | -0.022888 | -3.5477 | -0.07782 | 0.091553 | 0.068665 | -0.027466 | -0.086975 | -0.064087 | 0.068664 | 0.032043 | 1.3412 | 0.23804 | 0.16937 | -0.064087 | 121.4172 | 121.3577 | -0.027466 | 121.4218 | 121.3669 | 0.009155 | -0.050354 | 121.5958 | 121.4996 | 96.9681 | -121.4951 | 121.5363 | 121.5134 | 117.897 | -0.20599
1568.5156 | 121.6736 | -121.4676 | 0.13275 | -0.013122 | 0.018109 | 0.069908 | 0.0047809 | 0.068934 | 0.00058966 | -0.0010168 | -0.0040437 | 0.02813 | -0.0089209 | 0.022879 | 0.0061823 | -0.0087606 | -0.004578 | -120.1492 | -24.2523 | -121.2616 | 0.15564 | -121.5271 | -121.3852 | -0.013733 | -3.5339 | -0.073242 | 0.086975 | 0.064087 | -0.004578 | -0.068665 | -0.05951 | 0.082397 | 0.022889 | 1.3184 | 0.20599 | 0.1236 | -0.13733 | 121.463 | 121.3989 | -0.045776 | 121.4539 | 121.3943 | -0.004577 | -0.068664 | 121.6232 | 121.463 | 97.2153 | -121.5179 | 121.5546 | 121.5317 | 117.9337 | -0.20142
1570.25 | 121.7194 | -121.4676 | 0.10071 | -0.013122 | 0.012127 | 0.071617 | 0.0069171 | 0.067866 | -0.0058191 | -0.0027258 | -0.0040437 | 0.023644 | -0.011912 | 0.021384 | 0.0019099 | -0.0087606 | 0.045776 | -119.9982 | -24.6277 | -121.1838 | 0.086975 | -121.5088 | -121.3715 | 0.027466 | -3.3783 | 0.018311 | 0.041199 | 0.054932 | 0.032043 | -0.054932 | -0.041199 | 0.09613 | -0.013733 | 1.4694 | 0.28381 | 0.18768 | -0.054932 | 121.4996 | 121.4127 | -0.059509 | 121.4951 | 121.4859 | 0.073243 | -0.045776 | 121.5546 | 121.5134 | 96.8399 | -121.4722 | 121.5088 | 121.5225 | 118.0893 | -0.15564
1571.9375 | 121.6599 | -121.4767 | 0.11444 | 0.0021362 | 0.015118 | 0.068199 | 0.0032855 | 0.063593 | -0.0017603 | -0.00037596 | -0.0040437 | 0.026421 | -0.010416 | 0.019888 | 0.0068231 | -0.007479 | 0.07782 | -120.0073 | -24.4446 | -121.1792 | 0.086975 | -121.5134 | -121.3715 | 0.041199 | -3.4653 | 0.009155 | 0.022888 | 0.036621 | 0.013733 | -0.068665 | -0.036621 | 0.10529 | -0.027466 | 1.4694 | 0.29755 | 0.19226 | -0.036621 | 121.4905 | 121.4081 | -0.091553 | 121.5179 | 121.4859 | 0.07782 | -0.07782 | 121.5637 | 121.5546 | 97.0322 | -121.4859 | 121.4996 | 121.5134 | 118.0115 | -0.18311
1573.6719 | 121.788 | -121.4813 | 0.13733 | -0.0054933 | 0.015332 | 0.066917 | 0.0052081 | 0.066584 | 0.0014441 | 0.00026484 | -0.0040437 | 0.02578 | -0.013834 | 0.022238 | 0.0049005 | -0.0089742 | 0.068665 | -119.9478 | -24.3668 | -121.2021 | 0.086975 | -121.5042 | -121.3898 | 0.050354 | -3.3966 | 0.018311 | 0.022888 | 0.018311 | 0.032043 | -0.036621 | -0.022888 | 0.091552 | -0.050354 | 1.5335 | 0.27924 | 0.18768 | -0.068664 | 121.5134 | 121.4447 | -0.11444 | 121.5317 | 121.4996 | 0.054932 | -0.11902 | 121.5683 | 121.55 | 97.1146 | -121.5271 | 121.5042 | 121.4996 | 118.0847 | -0.17395
1575.4062 | 121.7972 | -121.4447 | 0.086975 | -0.0054933 | 0.013836 | 0.073326 | 0.0086261 | 0.067652 | -0.0041101 | -0.0031532 | -0.019302 | 0.024712 | -0.012766 | 0.018393 | 0.0019099 | -0.0087606 | 0.07782 | -119.9478 | -25.2594 | -121.225 | 0.10071 | -121.5179 | -121.4127 | 0.041199 | -3.3142 | 0.054932 | 0.045776 | 0.041199 | 0.018311 | -0.045776 | -0.073242 | 0.032043 | 0.013733 | 1.4969 | 0.21973 | 0.18768 | -0.009155 | 121.463 | 121.3989 | -0.041199 | 121.4859 | 121.4996 | 0.10071 | -0.045776 | 121.5454 | 121.5225 | 96.1853 | -121.4996 | 121.4905 | 121.4859 | 118.1305 | -0.13275
1577.0938 | 121.7331 | -121.4996 | 0.11902 | -0.013122 | 0.015973 | 0.069908 | 0.0037127 | 0.067439 | 0.0031531 | -0.0010168 | -0.011673 | 0.029839 | -0.01063 | 0.021811 | 0.0057551 | -0.011324 | 0.018311 | -120.0623 | -25.1678 | -121.2891 | 0.13275 | -121.5546 | -121.4355 | 0.009155 | -2.9526 | -0.050354 | 0.054932 | 0.068665 | 0.013733 | -0.064087 | -0.054931 | 0.064087 | 0.013732 | 1.4374 | 0.21057 | 0.14648 | -0.10071 | 121.5134 | 121.4355 | -0.064087 | 121.5088 | 121.4493 | 0.013733 | -0.050354 | 121.6324 | 121.5179 | 96.3318 | -121.5546 | 121.5546 | 121.5683 | 118.5471 | -0.18311
1578.8438 | 121.6919 | -121.5179 | 0.11444 | 0.0021362 | 0.018109 | 0.069267 | 0.0011493 | 0.064021 | 0.0014441 | -0.0010168 | -0.011673 | 0.027062 | -0.012125 | 0.022452 | 0.0055415 | -0.010256 | 0.086975 | -120.0165 | -24.6185 | -121.2112 | 0.10529 | -121.5408 | -121.3943 | 0.064087 | -2.8976 | 0.013733 | 0.041199 | 0.041199 | 0.022888 | -0.045776 | -0.022889 | 0.1236 | -0.009155 | 1.5015 | 0.3067 | 0.1831 | -0.027466 | 121.5408 | 121.4722 | -0.073242 | 121.582 | 121.5317 | 0.059509 | -0.073242 | 121.6232 | 121.6049 | 96.8994 | -121.5088 | 121.5591 | 121.5591 | 118.6203 | -0.16022
1580.5938 | 121.7331 | -121.5271 | 0.11902 | -0.013122 | 0.015545 | 0.069695 | 0.0049945 | 0.064875 | 0.0016577 | -0.0012306 | 0.0035858 | 0.026207 | -0.011057 | 0.018607 | 0.0051141 | -0.0089742 | 0.082397 | -119.9844 | -24.5773 | -121.2204 | 0.10529 | -121.5454 | -121.3898 | 0.064087 | -2.7695 | 0.013733 | 0.032043 | 0.032043 | 0.027466 | -0.050354 | -0.01831 | 0.13733 | -0.013733 | 1.5427 | 0.3067 | 0.16937 | -0.036622 | 121.5546 | 121.4767 | -0.086976 | 121.5912 | 121.5408 | 0.064087 | -0.086976 | 121.6324 | 121.6095 | 96.9498 | -121.5088 | 121.5591 | 121.5591 | 118.7576 | -0.16937
1582.3438 | 121.7926 | -121.5134 | 0.11444 | -0.0054933 | 0.015332 | 0.069481 | 0.0075581 | 0.065302 | -0.0053919 | -0.0018714 | -0.011673 | 0.024498 | -0.0095619 | 0.019675 | 0.00041446 | -0.0087606 | 0.022888 | -120.0531 | -24.4675 | -121.2799 | 0.10529 | -121.5775 | -121.4355 | 0.013733 | -2.6962 | 0.004578 | 0.036621 | 0.050354 | 0.022888 | -0.050354 | -0.064087 | 0.07782 | -0.009155 | 1.4603 | 0.23346 | 0.15564 | -0.091553 | 121.5363 | 121.463 | -0.07782 | 121.5271 | 121.5179 | 0.054932 | -0.064087 | 121.6187 | 121.5363 | 97.0459 | -121.55 | 121.55 | 121.5637 | 118.8171 | -0.16479
1584.0938 | 121.7834 | -121.4996 | 0.10529 | -0.020752 | 0.017468 | 0.070335 | 0.0084125 | 0.06808 | -0.0011193 | -0.0027258 | -0.011673 | 0.025994 | -0.0093481 | 0.019888 | 0.0014825 | -0.010256 | 0.07782 | -119.9478 | -24.646 | -121.2524 | 0.11902 | -121.582 | -121.4584 | -0.022888 | -2.9297 | -0.045776 | 0.068665 | 0.073242 | 0 | -0.07782 | -0.082397 | 0.041199 | 0.013733 | 1.5518 | 0.24719 | 0.20599 | -0.027466 | 121.4996 | 121.4218 | -0.036621 | 121.4767 | 121.4539 | 0.032044 | -0.032044 | 121.6187 | 121.5775 | 96.8536 | -121.5637 | 121.5683 | 121.5729 | 118.5699 | -0.18311
1585.8594 | 121.7239 | -121.5546 | 0.13275 | -0.0054933 | 0.018109 | 0.067986 | 0.0022175 | 0.065943 | 0.0052893 | 0.00069204 | 0.0035858 | 0.029625 | -0.010416 | 0.024802 | 0.0087457 | -0.01047 | -0.004578 | -120.076 | -24.2844 | -121.3303 | 0.15106 | -121.5958 | -121.4859 | -0.064087 | -3.154 | -0.17395 | 0.09613 | 0.082397 | -0.009155 | -0.091553 | -0.041199 | 0.068664 | 0.018311 | 1.4786 | 0.2243 | 0.15564 | -0.13733 | 121.5454 | 121.463 | -0.036621 | 121.4905 | 121.3806 | -0.082397 | -0.050354 | 121.7056 | 121.55 | 97.2702 | -121.6187 | 121.6507 | 121.637 | 118.4006 | -0.2243
1587.5469 | 121.7514 | -121.5363 | 0.11444 | -0.0054933 | 0.015118 | 0.068199 | 0.0062763 | 0.065516 | -0.0058191 | -0.0010168 | -0.0040437 | 0.025566 | -0.0097755 | 0.022025 | -1.2744e-05 | -0.0083334 | 0.027466 | -120.0256 | -24.3759 | -121.2891 | 0.10529 | -121.5912 | -121.4493 | 0.004578 | -2.8015 | -0.013733 | 0.050354 | 0.073242 | 0.032043 | -0.064087 | -0.054932 | 0.086975 | -0.009155 | 1.5106 | 0.24719 | 0.16022 | -0.086975 | 121.5683 | 121.4722 | -0.064087 | 121.5408 | 121.5225 | 0.050354 | -0.041199 | 121.6415 | 121.5637 | 97.1603 | -121.5637 | 121.5866 | 121.6095 | 118.7347 | -0.17853
1589.2969 | 121.8155 | -121.5271 | 0.10529 | -0.013122 | 0.016827 | 0.067558 | 0.0090533 | 0.064021 | -0.0024011 | -0.0046484 | 0.0035858 | 0.024925 | -0.01063 | 0.021384 | 0.0014825 | -0.0094016 | 0.10071 | -119.9066 | -24.6368 | -121.2524 | 0.11444 | -121.5866 | -121.463 | 0.054932 | -2.916 | 0.041199 | 0.041199 | 0.041199 | 0.018311 | -0.050354 | -0.059509 | 0.064087 | 0.009155 | 1.6205 | 0.27466 | 0.21057 | -0.004578 | 121.5454 | 121.4767 | -0.064087 | 121.582 | 121.5683 | 0.091553 | -0.064087 | 121.6415 | 121.6278 | 96.8903 | -121.5683 | 121.5683 | 121.5683 | 118.6111 | -0.15564
1591.0469 | 121.8246 | -121.5363 | 0.13275 | -0.013122 | 0.018109 | 0.07119 | 0.0071307 | 0.067652 | -0.0034691 | -0.0014442 | 0.0035858 | 0.026848 | -0.0084937 | 0.021384 | 0.0025507 | -0.011538 | 0.09613 | -119.9158 | -24.8383 | -121.257 | 0.10071 | -121.5958 | -121.4676 | 0.045776 | -2.8564 | 0.009155 | 0.064087 | 0.064087 | 0.041199 | -0.054932 | -0.059509 | 0.068665 | -0.032043 | 1.6205 | 0.27924 | 0.21057 | -0.036621 | 121.5775 | 121.4813 | -0.068664 | 121.582 | 121.5454 | 0.064087 | -0.068664 | 121.637 | 121.6324 | 96.698 | -121.6003 | 121.6003 | 121.6003 | 118.6798 | -0.18768
1592.7344 | 121.7148 | -121.5683 | 0.13733 | -0.0054933 | 0.012768 | 0.069481 | 0.0037127 | 0.06573 | -5.1338e-05 | -0.0033668 | -0.019302 | 0.025566 | -0.01063 | 0.020529 | 0.0053279 | -0.0081198 | 0.091553 | -119.9387 | -24.6277 | -121.3211 | 0.10529 | -121.6278 | -121.4355 | 0.022888 | -3.0121 | -0.013733 | 0.036621 | 0.059509 | 0.013733 | -0.064087 | -0.05951 | 0.13275 | -0.032043 | 1.6296 | 0.24719 | 0.11444 | -0.045776 | 121.582 | 121.5042 | -0.10071 | 121.5912 | 121.5546 | 0.050354 | -0.07782 | 121.6736 | 121.6599 | 96.9406 | -121.5729 | 121.6049 | 121.6278 | 118.5562 | -0.20142
1594.4688 | 121.8521 | -121.5317 | 0.10529 | -0.020752 | 0.014905 | 0.069695 | 0.0067035 | 0.067225 | -0.0041101 | -0.0033668 | -0.019302 | 0.026848 | -0.010843 | 0.023947 | 0.0023371 | -0.0089742 | 0.036621 | -119.9661 | -25.3418 | -121.312 | 0.10071 | -121.6141 | -121.4951 | 0.022888 | -3.0167 | 0.022888 | 0.050354 | 0.068665 | 0.018311 | -0.054932 | -0.082398 | 0.036621 | -0.004578 | 1.5656 | 0.21973 | 0.18311 | -0.068665 | 121.55 | 121.4767 | -0.054932 | 121.5546 | 121.5546 | 0.07782 | -0.036621 | 121.6324 | 121.5683 | 96.1899 | -121.6003 | 121.582 | 121.6003 | 118.515 | -0.16022
1596.2344 | 121.843 | -121.5317 | 0.10071 | -0.020752 | 0.01405 | 0.072044 | 0.0056355 | 0.069148 | -0.0017603 | -0.0035804 | -0.0040437 | 0.025994 | -0.0095619 | 0.020743 | 0.0042597 | -0.010256 | 0.086975 | -119.838 | -24.9619 | -121.2845 | 0.11444 | -121.6232 | -121.4859 | 0.07782 | -3.0396 | 0.022888 | 0.045776 | 0.032043 | 0.036621 | -0.045776 | -0.091553 | 0.045776 | 0.013733 | 1.6937 | 0.24719 | 0.20142 | -0.013733 | 121.5683 | 121.4859 | -0.054932 | 121.6095 | 121.5546 | 0.068664 | -0.068665 | 121.6461 | 121.6187 | 96.5698 | -121.5866 | 121.5775 | 121.5637 | 118.4921 | -0.14648
1597.9375 | 121.8338 | -121.5775 | 0.13275 | -0.020752 | 0.017682 | 0.069267 | 0.0022175 | 0.065943 | 0.0072119 | 0.0019738 | -0.0040437 | 0.030266 | -0.0082801 | 0.021811 | 0.0081049 | -0.011324 | 0.068665 | -119.9249 | -24.8199 | -121.344 | 0.13733 | -121.6507 | -121.5042 | 0.018311 | -3.0991 | -0.091553 | 0.082397 | 0.073242 | 0 | -0.082397 | -0.073242 | 0.073243 | 0.004578 | 1.6525 | 0.23346 | 0.16022 | -0.064086 | 121.5775 | 121.4951 | -0.050354 | 121.5958 | 121.4859 | -0.009156 | -0.059509 | 121.7148 | 121.6461 | 96.7575 | -121.637 | 121.6599 | 121.6507 | 118.4784 | -0.21515
1599.6875 | 121.7651 | -121.6278 | 0.12817 | -0.0054933 | 0.016613 | 0.068626 | 0.0060627 | 0.06573 | 0.0057165 | -0.00016236 | -0.011673 | 0.028557 | -0.0095619 | 0.02117 | 0.0070367 | -0.010256 | -0.022888 | -120.0348 | -24.971 | -121.3898 | 0.12817 | -121.6507 | -121.5363 | -0.045776 | -3.067 | -0.16022 | 0.091553 | 0.073242 | 0 | -0.07782 | -0.022888 | 0.091553 | 0 | 1.593 | 0.23804 | 0.14648 | -0.15106 | 121.6278 | 121.55 | -0.036621 | 121.582 | 121.4676 | -0.082397 | -0.054932 | 121.756 | 121.6049 | 96.6568 | -121.6644 | 121.7194 | 121.701 | 118.5608 | -0.20599
1601.375 | 121.8887 | -121.5729 | 0.10071 | 0.0021362 | 0.01405 | 0.070335 | 0.0064899 | 0.066157 | 0.0010169 | -0.0035804 | -0.011673 | 0.025994 | -0.010416 | 0.021384 | 0.0031915 | -0.0096152 | -0.036621 | -120.1035 | -24.6094 | -121.3806 | 0.13733 | -121.6919 | -121.55 | -0.07782 | -2.8336 | -0.1236 | 0.091553 | 0.082397 | -0.022888 | -0.082397 | -0.11902 | 0.022888 | 0.036621 | 1.4694 | 0.19226 | 0.16937 | -0.13733 | 121.55 | 121.4905 | -0.009155 | 121.4951 | 121.4493 | -0.041199 | -0.018311 | 121.7102 | 121.5363 | 96.9635 | -121.6507 | 121.6644 | 121.6553 | 118.7393 | -0.18311
1603.1094 | 121.9116 | -121.5775 | 0.10071 | 0.0021362 | 0.019391 | 0.068199 | 0.0094807 | 0.066157 | 0.0012305 | -0.002085 | -0.026932 | 0.029198 | -0.0091345 | 0.023734 | 0.0023371 | -0.0072652 | -0.027466 | -120.0623 | -23.2681 | -121.3852 | 0.14648 | -121.7102 | -121.5408 | -0.073242 | -2.6825 | -0.13275 | 0.10071 | 0.10071 | -0.018311 | -0.09613 | -0.13275 | 0.036621 | 0.045776 | 1.5152 | 0.19226 | 0.15564 | -0.12817 | 121.5591 | 121.4813 | 0 | 121.5042 | 121.4447 | -0.036621 | 0 | 121.7239 | 121.55 | 98.3093 | -121.6415 | 121.6782 | 121.6782 | 118.895 | -0.19684
1604.8594 | 121.8475 | -121.6141 | 0.11444 | -0.0054933 | 0.017682 | 0.069695 | 0.0047809 | 0.065943 | 0.0031531 | 0.00090584 | -0.019302 | 0.029412 | -0.0084937 | 0.023306 | 0.0046869 | -0.010042 | 0.036621 | -120.0027 | -24.3988 | -121.3577 | 0.13275 | -121.6644 | -121.5408 | 0 | -2.5955 | -0.073242 | 0.068665 | 0.07782 | 0.013733 | -0.091553 | -0.050354 | 0.073242 | 0.01831 | 1.6113 | 0.25635 | 0.18311 | -0.07782 | 121.6278 | 121.5225 | -0.045776 | 121.6141 | 121.5408 | 0.018311 | -0.036621 | 121.7468 | 121.6507 | 97.2153 | -121.6553 | 121.6827 | 121.6919 | 119.0186 | -0.20599
1606.6094 | 121.8292 | -121.5958 | 0.12817 | -0.013122 | 0.014264 | 0.068626 | 0.0039265 | 0.067225 | -0.00069214 | 0.0015466 | -0.0040437 | 0.025566 | -0.01063 | 0.019461 | 0.0063959 | -0.0091878 | 0.059509 | -119.9066 | -24.3576 | -121.2982 | 0.091553 | -121.6599 | -121.5134 | 0.041199 | -2.6825 | 0.004578 | 0.032043 | 0.045776 | 0.027466 | -0.041199 | -0.064087 | 0.082397 | -0.036621 | 1.6891 | 0.29755 | 0.21515 | -0.068665 | 121.6232 | 121.5546 | -0.096131 | 121.637 | 121.6003 | 0.045777 | -0.082398 | 121.6873 | 121.6553 | 97.2382 | -121.6415 | 121.6278 | 121.6415 | 118.9133 | -0.16937
1608.3125 | 121.843 | -121.6278 | 0.1236 | -0.013122 | 0.015973 | 0.067986 | 0.0041401 | 0.066371 | -0.00069214 | 0.00090584 | -0.019302 | 0.027916 | -0.010843 | 0.021597 | 0.0034051 | -0.0081198 | 0.054932 | -119.9615 | -24.5773 | -121.344 | 0.09613 | -121.6507 | -121.5271 | 0.041199 | -2.5177 | 0.018311 | 0.045776 | 0.045776 | 0.013733 | -0.050354 | -0.022888 | 0.10071 | -0.027466 | 1.6663 | 0.28381 | 0.18311 | -0.068664 | 121.6415 | 121.5775 | -0.07782 | 121.669 | 121.6461 | 0.068665 | -0.07782 | 121.7239 | 121.6827 | 97.0505 | -121.6507 | 121.6736 | 121.6736 | 119.1101 | -0.17395
1610.0469 | 121.8109 | -121.6599 | 0.13733 | 0.0021362 | 0.018109 | 0.070976 | 0.0039265 | 0.067225 | 0.0031531 | 5.1244e-05 | -0.0040437 | 0.028557 | -0.0093481 | 0.020316 | 0.0051141 | -0.010256 | -0.036621 | -120.0897 | -24.9664 | -121.4172 | 0.14648 | -121.7056 | -121.5637 | -0.064087 | -2.5406 | -0.10529 | 0.073242 | 0.091553 | 0.004578 | -0.086975 | -0.045776 | 0.09613 | 0.009155 | 1.5701 | 0.24262 | 0.14648 | -0.17395 | 121.6644 | 121.5729 | -0.064087 | 121.5958 | 121.5546 | -0.018311 | -0.045776 | 121.8063 | 121.6232 | 96.6934 | -121.701 | 121.7331 | 121.7514 | 119.1193 | -0.2243
1611.7344 | 121.9025 | -121.6278 | 0.07782 | -0.013122 | 0.015545 | 0.07119 | 0.0060627 | 0.067011 | -0.0060327 | -0.0027258 | 0.0035858 | 0.024925 | -0.011271 | 0.019888 | 0.0029779 | -0.008547 | 0.045776 | -119.902 | -25.0397 | -121.344 | 0.07782 | -121.6736 | -121.55 | 0 | -2.3621 | 0.013733 | 0.045776 | 0.050354 | 0.027466 | -0.059509 | -0.045776 | 0.07782 | 0 | 1.7258 | 0.28381 | 0.20599 | -0.032044 | 121.6553 | 121.5683 | -0.032044 | 121.6278 | 121.6415 | 0.073242 | -0.027466 | 121.7056 | 121.6736 | 96.5881 | -121.6278 | 121.6736 | 121.6782 | 119.2657 | -0.13733
1613.4844 | 121.9482 | -121.582 | 0.10529 | -0.013122 | 0.015759 | 0.069054 | 0.0054217 | 0.065302 | 0.00080326 | -0.002085 | 0.011215 | 0.027489 | -0.0095619 | 0.02117 | 0.0042597 | -0.010256 | -0.032043 | -120.0943 | -24.3073 | -121.4035 | 0.16937 | -121.6965 | -121.5729 | -0.068665 | -2.4261 | -0.10986 | 0.082397 | 0.091553 | -0.004578 | -0.082397 | -0.11444 | 0.009155 | 0.064087 | 1.4877 | 0.17853 | 0.16937 | -0.13733 | 121.5775 | 121.4996 | -0.022889 | 121.5134 | 121.4722 | -0.027466 | -0.013733 | 121.7514 | 121.55 | 97.2748 | -121.6782 | 121.6644 | 121.6736 | 119.1559 | -0.18768
1615.1719 | 121.9437 | -121.6187 | 0.10986 | -0.0054933 | 0.015118 | 0.06884 | 0.0073443 | 0.067439 | -0.0015465 | -0.0010168 | -0.0040437 | 0.030907 | -0.0080665 | 0.022025 | 0.0023371 | -0.0089742 | -0.045776 | -120.0714 | -24.6277 | -121.4127 | 0.15106 | -121.7148 | -121.6232 | -0.086975 | -2.3346 | -0.10529 | 0.09613 | 0.07782 | -0.013733 | -0.086975 | -0.096131 | -0.004578 | 0.041199 | 1.5472 | 0.20599 | 0.21057 | -0.15564 | 121.6049 | 121.5317 | -0.013733 | 121.5317 | 121.5134 | -0.018311 | -0.032043 | 121.7697 | 121.5729 | 96.991 | -121.7331 | 121.7148 | 121.6965 | 119.2841 | -0.19684
1616.9219 | 121.9574 | -121.6049 | 0.082397 | -0.0054933 | 0.013836 | 0.072044 | 0.0041401 | 0.066157 | -0.0036829 | -0.0022986 | 0.0035858 | 0.02343 | -0.010416 | 0.020956 | 0.0023371 | -0.007479 | 0.036621 | -119.9341 | -24.646 | -121.3623 | 0.10986 | -121.701 | -121.5683 | 0.004578 | -2.2247 | 0.050354 | 0.045776 | 0.027466 | 0.027466 | -0.064087 | -0.096131 | 0.036621 | 0.027466 | 1.6708 | 0.24261 | 0.20599 | -0.045776 | 121.6324 | 121.5408 | -0.036621 | 121.6095 | 121.6553 | 0.11444 | -0.054931 | 121.7148 | 121.6415 | 96.9589 | -121.6507 | 121.6507 | 121.6324 | 119.3802 | -0.14648
1618.6562 | 121.9666 | -121.6324 | 0.082397 | -0.0054933 | 0.01405 | 0.070976 | 0.0052081 | 0.064234 | -0.0045373 | -0.002085 | -0.011673 | 0.02343 | -0.0082801 | 0.019888 | 0.00041446 | -0.0089742 | 0.027466 | -119.957 | -24.614 | -121.3806 | 0.10529 | -121.7056 | -121.5591 | 0.013733 | -2.2568 | 0.032043 | 0.059509 | 0.059509 | 0.022888 | -0.054932 | -0.073242 | 0.073242 | 0.022889 | 1.6754 | 0.25177 | 0.17853 | -0.054931 | 121.6553 | 121.5775 | -0.022888 | 121.6461 | 121.6644 | 0.086975 | -0.022888 | 121.7377 | 121.6599 | 97.0184 | -121.6415 | 121.6919 | 121.6919 | 119.3756 | -0.13733
1620.3281 | 121.9437 | -121.669 | 0.10071 | -0.020752 | 0.018963 | 0.070122 | 0.0071307 | 0.065302 | 0.0014441 | -0.0040076 | 0.0035858 | 0.026848 | -0.0099891 | 0.022665 | 0.0027643 | -0.0094016 | 0 | -119.9982 | -24.8428 | -121.4584 | 0.15106 | -121.7239 | -121.6187 | -0.2243 | -2.3804 | -0.27924 | 0.086975 | 0.086975 | -0.17395 | -0.24261 | -0.054932 | 0.050354 | 0.050354 | 1.6708 | 0.21057 | 0.16022 | -0.10071 | 121.4951 | 121.4264 | -0.013733 | 121.4447 | 121.3898 | -0.036621 | -0.013733 | 121.8201 | 121.669 | 96.8262 | -121.7194 | 121.756 | 121.756 | 119.2886 | -0.34332
1622.0781 | 121.9757 | -121.6415 | 0.068665 | -0.013122 | 0.013836 | 0.070763 | 0.0058491 | 0.065943 | -0.0034691 | -0.00080316 | -0.011673 | 0.024071 | -0.0093481 | 0.02117 | 0.00062806 | -0.008547 | 0.036621 | -119.5038 | -25.1999 | -121.3806 | 0.09613 | -121.7331 | -121.5958 | -0.2243 | -2.2385 | -0.22888 | 0.054932 | 0.027466 | -0.23804 | -0.32959 | -0.091552 | 0.045777 | 0.027465 | 2.1378 | 0.26093 | 0.21515 | -0.032044 | 121.4035 | 121.312 | -0.013733 | 121.4172 | 121.4127 | 0.10071 | -0.041199 | 121.7377 | 121.6782 | 96.4417 | -121.6644 | 121.6965 | 121.669 | 119.4031 | -0.39826
1623.7656 | 121.9711 | -121.6232 | 0.082397 | -0.0054933 | 0.01405 | 0.070122 | 0.0058491 | 0.064448 | -0.0019739 | -0.0042212 | -0.011673 | 0.025353 | -0.0099891 | 0.020956 | 0.0012689 | -0.0089742 | 0.086975 | -119.9478 | -25.4105 | -121.3806 | 0.11444 | -121.7468 | -121.5637 | 0.032043 | -2.2659 | 0.059509 | 0.059509 | 0.045776 | 0.036621 | -0.064087 | -0.1236 | 0.059509 | 0.032044 | 1.6754 | 0.24262 | 0.18311 | 0.004578 | 121.6599 | 121.5591 | -0.022888 | 121.6553 | 121.6827 | 0.1236 | -0.036621 | 121.7377 | 121.7102 | 96.2128 | -121.6461 | 121.6827 | 121.669 | 119.3573 | -0.14648
1625.5156 | 121.9162 | -121.6827 | 0.11444 | -0.013122 | 0.015332 | 0.07119 | 0.0037127 | 0.066371 | -0.00090574 | -0.0025122 | -0.0040437 | 0.024498 | -0.010843 | 0.019888 | 0.0038325 | -0.01047 | 0.018311 | -120.0027 | -25.3372 | -121.4264 | 0.10529 | -121.7285 | -121.582 | -0.004578 | -2.2385 | -0.004578 | 0.059509 | 0.045776 | 0.004578 | -0.059509 | -0.045777 | 0.10071 | -0.009155 | 1.68 | 0.25635 | 0.15564 | -0.09613 | 121.6873 | 121.6232 | -0.054932 | 121.6782 | 121.6782 | 0.054931 | -0.068665 | 121.788 | 121.701 | 96.3455 | -121.6965 | 121.7422 | 121.7285 | 119.4443 | -0.17395
1627.25 | 121.875 | -121.7102 | 0.11444 | -0.0054933 | 0.0093504 | 0.07119 | 0.0041401 | 0.065302 | -0.0019739 | -0.0022986 | -0.0040437 | 0.024712 | -0.01063 | 0.020956 | 0.0049005 | -0.010042 | 0.032043 | -119.8746 | -25.502 | -121.4218 | 0.10986 | -121.7331 | -121.5912 | -0.022888 | -2.3666 | -0.036621 | 0.041199 | 0.064087 | 0.032043 | -0.054932 | -0.022888 | 0.11902 | -0.004578 | 1.8356 | 0.28839 | 0.16937 | -0.082398 | 121.7422 | 121.6553 | -0.073242 | 121.6873 | 121.6736 | 0.018311 | -0.050354 | 121.8201 | 121.7422 | 96.2082 | -121.7056 | 121.7514 | 121.7743 | 119.3436 | -0.16937
1629 | 121.994 | -121.6507 | 0.086975 | -0.013122 | 0.015332 | 0.06884 | 0.0069171 | 0.066584 | -0.0019739 | -0.0010168 | 0.0035858 | 0.026634 | -0.010203 | 0.01882 | 0.0010553 | -0.01047 | 0.064087 | -119.9753 | -25.5844 | -121.4035 | 0.09613 | -121.7285 | -121.6232 | 0.041199 | -2.6413 | 0.022888 | 0.068665 | 0.059509 | 0.018311 | -0.050354 | -0.07782 | 0.027466 | 0.009155 | 1.6754 | 0.24719 | 0.21973 | -0.022888 | 121.669 | 121.6003 | -0.01831 | 121.6919 | 121.6736 | 0.073242 | -0.027466 | 121.7468 | 121.7148 | 96.0663 | -121.7102 | 121.7194 | 121.7102 | 119.0094 | -0.13733
1630.75 | 122.0078 | -121.6644 | 0.10529 | 0.0021362 | 0.01875 | 0.070976 | 0.0039265 | 0.066157 | 0.0022987 | -0.0040076 | -0.0040437 | 0.030907 | -0.0095619 | 0.024374 | 0.0051141 | -0.0094016 | 0.018311 | -120.0851 | -25.9689 | -121.4767 | 0.13275 | -121.788 | -121.6599 | -0.054932 | -2.6825 | -0.11444 | 0.09613 | 0.09613 | -0.004578 | -0.07782 | -0.1236 | 0.004578 | 0.027465 | 1.5793 | 0.18768 | 0.1831 | -0.086975 | 121.6599 | 121.5866 | -0.009156 | 121.6095 | 121.55 | -0.036621 | -0.009156 | 121.7972 | 121.6827 | 95.6955 | -121.7651 | 121.7606 | 121.7606 | 118.9819 | -0.18311
1632.4375 | 122.0123 | -121.6736 | 0.10071 | -0.013122 | 0.017041 | 0.069908 | 0.0060627 | 0.067011 | 0.00037606 | -0.0018714 | -0.011673 | 0.025139 | -0.010203 | 0.022025 | 0.00084166 | -0.010042 | 0.09613 | -119.9249 | -26.4542 | -121.3852 | 0.10529 | -121.7377 | -121.6049 | 0.041199 | -2.5589 | 0.041199 | 0.027466 | 0.059509 | 0.022888 | -0.036621 | -0.064087 | 0.068665 | 0.004578 | 1.7487 | 0.28839 | 0.21973 | -0.004578 | 121.6965 | 121.637 | -0.073242 | 121.7148 | 121.7148 | 0.07782 | -0.041199 | 121.7789 | 121.7697 | 95.2194 | -121.7056 | 121.7011 | 121.7331 | 119.1147 | -0.13733
1634.1875 | 121.9025 | -121.7285 | 0.10986 | -0.013122 | 0.012982 | 0.069908 | 0.0056355 | 0.065516 | -0.0017603 | -0.00037596 | -0.011673 | 0.023857 | -0.012552 | 0.022665 | 0.0034051 | -0.0089742 | 0.036621 | -120.0577 | -26.3672 | -121.4447 | 0.11902 | -121.7697 | -121.6095 | 0 | -2.5864 | -0.036621 | 0.059509 | 0.064087 | 0.009155 | -0.045776 | -0.041198 | 0.11902 | 0.009156 | 1.6708 | 0.28381 | 0.16479 | -0.073242 | 121.7377 | 121.6827 | -0.050354 | 121.7285 | 121.6919 | 0.009155 | -0.045776 | 121.8475 | 121.7651 | 95.3613 | -121.7194 | 121.788 | 121.7926 | 119.1422 | -0.15564
1635.875 | 121.8933 | -121.7377 | 0.13733 | -0.013122 | 0.019177 | 0.069908 | 0.0024311 | 0.065089 | 0.0061439 | 0.00090584 | -0.011673 | 0.03048 | -0.011057 | 0.023947 | 0.0076777 | -0.01047 | 0.032043 | -120.1126 | -26.5686 | -121.4767 | 0.14191 | -121.7743 | -121.6644 | -0.045776 | -2.8656 | -0.14648 | 0.09613 | 0.09613 | -0.004578 | -0.086975 | -0.036621 | 0.073242 | 0.004578 | 1.6251 | 0.26093 | 0.18768 | -0.10529 | 121.7331 | 121.6507 | -0.041199 | 121.6919 | 121.5912 | -0.059509 | -0.041199 | 121.8796 | 121.7697 | 95.1691 | -121.8018 | 121.8338 | 121.8338 | 118.8721 | -0.2243
1637.625 | 121.9345 | -121.7285 | 0.1236 | -0.013122 | 0.013623 | 0.068626 | 0.0052081 | 0.066371 | 0.0029395 | 0.00069204 | -0.011673 | 0.02578 | -0.0093481 | 0.022879 | 0.0040461 | -0.008547 | 0.10986 | -120.0119 | -26.1795 | -121.4127 | 0.07782 | -121.7468 | -121.6095 | 0.086975 | -2.5269 | 0.004578 | 0.032043 | 0.036621 | 0.050354 | -0.050354 | -0.01831 | 0.11902 | -0.045776 | 1.7166 | 0.31586 | 0.19684 | -0.013733 | 121.7789 | 121.6782 | -0.091553 | 121.8155 | 121.7331 | 0.054932 | -0.086975 | 121.8063 | 121.8384 | 95.549 | -121.7331 | 121.7606 | 121.7651 | 119.2017 | -0.17395
1639.375 | 122.0215 | -121.6873 | 0.09613 | -0.020752 | 0.013623 | 0.068413 | 0.0067035 | 0.064234 | -0.0034691 | -0.0014442 | -0.011673 | 0.027275 | -0.0091345 | 0.02117 | 0.0019099 | -0.0096152 | 0.064087 | -120.0256 | -26.2939 | -121.431 | 0.10529 | -121.7697 | -121.6324 | 0.036621 | -2.2934 | 0.027466 | 0.054932 | 0.036621 | 0.018311 | -0.050354 | -0.082397 | 0.054932 | 0.009156 | 1.6617 | 0.25635 | 0.20142 | -0.032043 | 121.7056 | 121.637 | -0.041198 | 121.7239 | 121.7148 | 0.07782 | -0.059509 | 121.7926 | 121.7514 | 95.3934 | -121.7285 | 121.7422 | 121.7239 | 119.3939 | -0.14648
1641.0469 | 122.0352 | -121.6965 | 0.086975 | -0.0054933 | 0.012982 | 0.072258 | 0.0084125 | 0.067439 | -0.0036829 | -0.0022986 | -0.0040437 | 0.025353 | -0.0089209 | 0.022665 | 0.0029779 | -0.010683 | 0.091553 | -119.9982 | -26.6235 | -121.4264 | 0.10071 | -121.7834 | -121.6049 | 0.054932 | -2.4078 | 0.041199 | 0.045776 | 0.041199 | 0.041199 | -0.054932 | -0.086975 | 0.091553 | 0.013733 | 1.6983 | 0.27008 | 0.17853 | 0.004578 | 121.7377 | 121.6415 | -0.041199 | 121.7514 | 121.7377 | 0.096131 | -0.045776 | 121.7972 | 121.788 | 95.0729 | -121.6919 | 121.7422 | 121.7377 | 119.2886 | -0.14191
1642.7969 | 121.9574 | -121.7285 | 0.13275 | -0.013122 | 0.015973 | 0.069908 | 0.0032855 | 0.063166 | 0.0037939 | 0.0017602 | -0.019302 | 0.029625 | -0.01063 | 0.022879 | 0.0083185 | -0.010683 | 0.022888 | -120.1035 | -27.0218 | -121.4996 | 0.13275 | -121.7926 | -121.6919 | -0.004578 | -2.4673 | -0.07782 | 0.064087 | 0.064087 | 0.004578 | -0.068665 | -0.064087 | 0.036621 | 0 | 1.6251 | 0.22888 | 0.19226 | -0.10986 | 121.7331 | 121.6599 | -0.068664 | 121.7239 | 121.6507 | -0.009155 | -0.068664 | 121.8613 | 121.7514 | 94.7067 | -121.8246 | 121.7926 | 121.7926 | 119.2612 | -0.20142
1644.5312 | 121.9254 | -121.7194 | 0.14191 | -0.0054933 | 0.015759 | 0.069908 | 0.00029487 | 0.06573 | 0.0020849 | -0.00037596 | -0.011673 | 0.02578 | -0.011698 | 0.021811 | 0.0061823 | -0.010256 | 0.09613 | -119.9936 | -26.3718 | -121.4264 | 0.10986 | -121.7651 | -121.6507 | 0.073242 | -2.4124 | 0.022888 | 0.032043 | 0.027466 | 0.045776 | -0.027466 | -0.045777 | 0.068664 | -0.032044 | 1.7258 | 0.29297 | 0.2243 | -0.045777 | 121.7651 | 121.6919 | -0.10986 | 121.7926 | 121.7422 | 0.050354 | -0.11444 | 121.8292 | 121.8155 | 95.3476 | -121.7926 | 121.7514 | 121.7468 | 119.3069 | -0.16937
1646.2031 | 122.049 | -121.7148 | 0.10529 | -0.013122 | 0.014264 | 0.070976 | 0.0092669 | 0.066371 | -0.0032555 | -0.0016578 | -0.011673 | 0.024925 | -0.0097755 | 0.019247 | 0.0014825 | -0.0091878 | 0.09613 | -119.9753 | -26.1017 | -121.4172 | 0.1236 | -121.8063 | -121.6461 | 0.032043 | -2.3987 | 0.045776 | 0.059509 | 0.059509 | 0.018311 | -0.032043 | -0.091552 | 0.068665 | 0.01831 | 1.7395 | 0.29755 | 0.22888 | -0.009156 | 121.7331 | 121.6827 | -0.045777 | 121.7468 | 121.7606 | 0.077819 | -0.045777 | 121.8384 | 121.8109 | 95.6131 | -121.7514 | 121.7743 | 121.7743 | 119.3161 | -0.13733
1647.9531 | 121.962 | -121.7468 | 0.1236 | 0.0097657 | 0.016827 | 0.06884 | 0.0032855 | 0.068934 | 0.0042213 | 0.0015466 | -0.0040437 | 0.02813 | -0.011484 | 0.023947 | 0.0059687 | -0.0083334 | 0.013733 | -120.1813 | -26.8662 | -121.5225 | 0.14648 | -121.8338 | -121.7056 | -0.032043 | -2.504 | -0.09613 | 0.082397 | 0.086975 | -0.004578 | -0.091553 | -0.086975 | 0.041199 | 0.022888 | 1.5656 | 0.2243 | 0.18311 | -0.10986 | 121.7422 | 121.6553 | -0.041199 | 121.7148 | 121.6507 | -0.004577 | -0.036621 | 121.8933 | 121.7606 | 94.8807 | -121.8292 | 121.8292 | 121.8338 | 119.2429 | -0.21515
1649.6875 | 121.9666 | -121.7743 | 0.11902 | -0.013122 | 0.013409 | 0.069908 | 0.0056355 | 0.067866 | -0.0034691 | -0.00080316 | -0.019302 | 0.025353 | -0.010416 | 0.019461 | 0.0031915 | -0.006838 | 0.022888 | -120.0897 | -28.1204 | -121.4996 | 0.11902 | -121.8109 | -121.6736 | -0.018311 | -2.33 | -0.009155 | 0.054932 | 0.041199 | 0.004578 | -0.054932 | -0.036621 | 0.10071 | 0 | 1.6846 | 0.27466 | 0.17395 | -0.096131 | 121.7789 | 121.7194 | -0.064087 | 121.756 | 121.7651 | 0.045777 | -0.07782 | 121.8933 | 121.7972 | 93.6539 | -121.7926 | 121.8292 | 121.8155 | 119.4443 | -0.17395
1651.3594 | 121.9528 | -121.7697 | 0.11444 | -0.0054933 | 0.018536 | 0.068413 | 0.0062763 | 0.066157 | 0.0065711 | -0.0012306 | 0.0035858 | 0.031121 | -0.0082801 | 0.023093 | 0.0061823 | -0.0091878 | 0.068665 | -120.1172 | -28.3951 | -121.4722 | 0.13275 | -121.8063 | -121.7056 | -0.018311 | -2.2202 | -0.09613 | 0.068665 | 0.064087 | 0.013733 | -0.068665 | -0.036621 | 0.064087 | 0.01831 | 1.6525 | 0.29755 | 0.23346 | -0.045776 | 121.7834 | 121.701 | -0.045776 | 121.7514 | 121.6736 | -0.027465 | -0.050354 | 121.9025 | 121.8384 | 93.3746 | -121.8201 | 121.8384 | 121.8338 | 119.5496 | -0.18311
1653.1094 | 122.081 | -121.7239 | 0.091553 | -0.0054933 | 0.014691 | 0.070549 | 0.0060627 | 0.067011 | -0.0036829 | -0.0027258 | -0.011673 | 0.024925 | -0.011057 | 0.019034 | 0.0014825 | -0.0087606 | 0.086975 | -119.9936 | -26.7746 | -121.431 | 0.10071 | -121.8063 | -121.6553 | 0.054932 | -1.9684 | 0.036621 | 0.041199 | 0.059509 | 0.036621 | -0.041199 | -0.082397 | 0.068665 | 0.009155 | 1.7303 | 0.29297 | 0.2243 | -0.004578 | 121.7606 | 121.6827 | -0.050354 | 121.7789 | 121.7606 | 0.07782 | -0.032044 | 121.8246 | 121.8109 | 94.9493 | -121.7468 | 121.7651 | 121.7834 | 119.7556 | -0.13275
1654.8438 | 122.0215 | -121.756 | 0.10071 | -0.020752 | 0.019391 | 0.069267 | 0.0086261 | 0.073634 | 0.00016226 | -0.00016236 | -0.0040437 | 0.02813 | -0.0087073 | 0.020743 | 0.0019099 | -0.0083334 | 0.009155 | -117.7094 | -24.2294 | -121.5363 | 0.11902 | -121.8246 | -121.7194 | -0.064087 | -2.0462 | -0.086975 | 0.07782 | 0.082397 | -0.013733 | -0.10071 | -0.068665 | 0.036621 | 0.018311 | 4.0466 | 0.21973 | 0.1831 | -0.091553 | 121.7422 | 121.6553 | -0.022888 | 121.6919 | 121.669 | 0.013733 | -0.018311 | 121.875 | 121.7651 | 97.5266 | -121.8201 | 121.8338 | 121.8384 | 119.7098 | -0.20142
1656.5781 | 122.0306 | -121.7697 | 0.1236 | -0.0054933 | 0.018322 | 0.070763 | 0.0067035 | 0.070216 | -0.00047854 | -0.00058956 | -0.0040437 | 0.027703 | -0.0087073 | 0.022238 | 0.0027643 | -0.0089742 | 0.036621 | -116.3132 | -26.326 | -121.4722 | 0.11444 | -121.8292 | -121.7239 | -0.041199 | -2.2385 | -0.064087 | 0.073242 | 0.09613 | 0.013733 | -0.082397 | -0.05951 | 0.045776 | -0.009155 | 5.4565 | 0.29755 | 0.25177 | -0.086975 | 121.7834 | 121.6873 | -0.050354 | 121.7285 | 121.7056 | 0.01831 | -0.027466 | 121.8842 | 121.8063 | 95.4437 | -121.8475 | 121.843 | 121.8658 | 119.5312 | -0.20599
1658.25 | 121.9437 | -121.8018 | 0.1236 | -0.0054933 | 0.012555 | 0.070976 | 0.0060627 | 0.069361 | -0.0032555 | -0.0022986 | -0.019302 | 0.02578 | -0.012125 | 0.020316 | 0.0042597 | -0.010897 | 0.054932 | -115.7776 | -27.1317 | -121.4859 | 0.09613 | -121.8109 | -121.669 | -0.009155 | -2.1652 | -0.013733 | 0.068665 | 0.041199 | 0.027466 | -0.050354 | -0.009155 | 0.13275 | -0.027466 | 6.0242 | 0.31586 | 0.1831 | -0.068664 | 121.8292 | 121.7514 | -0.054931 | 121.7926 | 121.788 | 0.036621 | -0.082397 | 121.8979 | 121.8567 | 94.6701 | -121.7926 | 121.8704 | 121.843 | 119.6365 | -0.17395
1659.9844 | 121.9849 | -121.8109 | 0.13733 | -0.013122 | 0.0093504 | 0.069267 | 0.0030719 | 0.069575 | -0.0024011 | -0.0010168 | 0.011215 | 0.026634 | -0.0089209 | 0.022025 | 0.0031915 | -0.0089742 | 0.027466 | -115.4343 | -26.9943 | -121.4996 | 0.10529 | -121.8155 | -121.6965 | -0.022888 | -2.1423 | -0.022888 | 0.050354 | 0.050354 | 0.022888 | -0.064087 | -0.004578 | 0.11444 | -0.032043 | 6.3766 | 0.31128 | 0.19684 | -0.10986 | 121.8338 | 121.7468 | -0.086975 | 121.788 | 121.788 | 0.041199 | -0.086975 | 121.9162 | 121.8384 | 94.8166 | -121.8338 | 121.8613 | 121.8613 | 119.6686 | -0.20142
1661.7188 | 122.0856 | -121.7514 | 0.10529 | -0.0054933 | 0.010846 | 0.073326 | 0.0052081 | 0.069575 | -0.0013329 | -0.0029394 | 0.0035858 | 0.027703 | -0.011912 | 0.020743 | 0.0012689 | -0.0087606 | 0.045776 | -115.123 | -27.1545 | -121.4767 | 0.10529 | -121.8704 | -121.701 | 0 | -2.2018 | 0.009155 | 0.045776 | 0.041199 | 0.018311 | -0.054932 | -0.11902 | 0.050354 | 0 | 6.6284 | 0.27466 | 0.2243 | -0.05951 | 121.7697 | 121.6965 | -0.05951 | 121.7514 | 121.7606 | 0.064087 | -0.064087 | 121.8567 | 121.7972 | 94.5969 | -121.8063 | 121.7972 | 121.7926 | 119.5496 | -0.16022
1663.4844 | 122.0627 | -121.7789 | 0.073242 | -0.013122 | 0.018322 | 0.070122 | 0.0075581 | 0.070857 | -0.00047854 | -0.002085 | 0.0035858 | 0.026634 | -0.0099891 | 0.019675 | 0.0031915 | -0.0091878 | 0.086975 | -114.8483 | -25.7263 | -121.4447 | 0.10529 | -121.8475 | -121.6965 | 0.032043 | -2.1606 | 0.022888 | 0.045776 | 0.041199 | 0.022888 | -0.068665 | -0.068664 | 0.082398 | 0.032044 | 6.9305 | 0.33417 | 0.25177 | 0.013733 | 121.8018 | 121.7102 | -0.027466 | 121.8109 | 121.8018 | 0.091553 | -0.032043 | 121.8842 | 121.8658 | 96.0526 | -121.7697 | 121.8246 | 121.8201 | 119.6182 | -0.14191
1665.1562 | 122.0947 | -121.7789 | 0.11444 | -0.013122 | 0.016827 | 0.068199 | 0.0090533 | 0.07342 | 0.0029395 | -0.0010168 | -0.0040437 | 0.030693 | -0.0080665 | 0.023734 | 0.0061823 | -0.012179 | -0.004578 | -114.7293 | -26.7975 | -121.55 | 0.16937 | -121.8704 | -121.7422 | -0.045776 | -2.4582 | -0.10986 | 0.09613 | 0.07782 | -0.009155 | -0.07782 | -0.091552 | 0.036621 | 0.054932 | 7.0496 | 0.22888 | 0.19226 | -0.11902 | 121.7697 | 121.701 | -0.018311 | 121.7331 | 121.669 | -0.032043 | -0.036621 | 121.9482 | 121.7743 | 94.9814 | -121.8567 | 121.875 | 121.8567 | 119.3207 | -0.19226
1666.9062 | 122.0856 | -121.7697 | 0.11444 | -0.013122 | 0.018109 | 0.06884 | 0.0022175 | 0.07342 | 0.0052893 | 0.0015466 | 0.0035858 | 0.029839 | -0.010203 | 0.022879 | 0.0074641 | -0.01047 | 0.054932 | -114.2578 | -26.4771 | -121.55 | 0.12817 | -121.843 | -121.7377 | -0.013733 | -2.1652 | -0.073242 | 0.091553 | 0.064087 | 0 | -0.086975 | -0.073243 | 0.032043 | 0.013733 | 7.5119 | 0.21973 | 0.18768 | -0.059509 | 121.7697 | 121.6827 | -0.022888 | 121.756 | 121.6965 | 0.013733 | -0.050354 | 121.8979 | 121.8246 | 95.2927 | -121.8521 | 121.8613 | 121.8338 | 119.6045 | -0.20142
1668.5938 | 121.994 | -121.8246 | 0.14648 | -0.020752 | 0.013409 | 0.070549 | 0.0052081 | 0.071284 | -0.0049645 | -0.00080316 | -0.0040437 | 0.024285 | -0.01063 | 0.02117 | -0.00044014 | -0.0083334 | 0.032043 | -113.6627 | -26.3489 | -121.5317 | 0.09613 | -121.8658 | -121.7102 | -0.022888 | -2.0325 | -0.013733 | 0.07782 | 0.050354 | 0.027466 | -0.059509 | -0.041199 | 0.11444 | -0.050354 | 8.1619 | 0.29297 | 0.17853 | -0.11444 | 121.8521 | 121.7651 | -0.068664 | 121.8018 | 121.8109 | 0.045776 | -0.09613 | 121.9208 | 121.8567 | 95.4758 | -121.8567 | 121.9025 | 121.875 | 119.7922 | -0.20599
1670.3438 | 122.1222 | -121.8018 | 0.11902 | -0.013122 | 0.020031 | 0.06884 | 0.0075581 | 0.071284 | 0.0042213 | -0.00037596 | -0.0040437 | 0.028343 | -0.0074255 | 0.024588 | 0.0034051 | -0.010256 | -0.009155 | -113.1363 | -26.3168 | -121.5591 | 0.14648 | -121.8658 | -121.7789 | -0.068665 | -2.1057 | -0.10529 | 0.09613 | 0.09613 | 0 | -0.082397 | -0.064087 | 0.022888 | 0.027465 | 8.6655 | 0.24262 | 0.21973 | -0.12817 | 121.8018 | 121.7194 | -0.022889 | 121.7331 | 121.6965 | -0.022889 | -0.022889 | 121.9482 | 121.7926 | 95.4849 | -121.8979 | 121.8979 | 121.8979 | 119.696 | -0.20142
1672.0156 | 122.0078 | -121.8246 | 0.11902 | -0.0054933 | 0.020031 | 0.068199 | 0.0056355 | 0.072566 | 0.0040077 | 0.0011194 | -0.011673 | 0.031761 | -0.0093481 | 0.022238 | 0.0087457 | -0.010256 | 0.059509 | -112.4451 | -25.5707 | -121.5271 | 0.15106 | -121.8613 | -121.7422 | -0.032043 | -2.0508 | -0.10529 | 0.09613 | 0.068665 | -0.009155 | -0.086975 | -0.036621 | 0.082397 | 0.032043 | 9.3796 | 0.29755 | 0.21515 | -0.05951 | 121.8155 | 121.7377 | -0.022889 | 121.7926 | 121.7194 | -0.018311 | -0.050354 | 121.9757 | 121.8842 | 96.254 | -121.8613 | 121.9208 | 121.8933 | 119.7739 | -0.20599
1673.75 | 122.0352 | -121.8109 | 0.11902 | -0.0054933 | 0.020031 | 0.066917 | 0.0043537 | 0.077052 | -0.00047854 | 0.00090584 | 0.011215 | 0.026207 | -0.0099891 | 0.020102 | 0.0072505 | -0.0091878 | 0.013733 | -111.6623 | -26.1887 | -121.5454 | 0.1236 | -121.8842 | -121.7422 | 0.004578 | -1.9135 | -0.022888 | 0.050354 | 0.073242 | 0.018311 | -0.036621 | -0.073242 | 0.068664 | 0.004577 | 10.1486 | 0.2655 | 0.19684 | -0.10529 | 121.8292 | 121.7743 | -0.068665 | 121.8155 | 121.788 | 0.013733 | -0.045777 | 121.9345 | 121.8246 | 95.6223 | -121.8613 | 121.8613 | 121.8842 | 119.8975 | -0.15564
1675.5 | 122.0352 | -121.7789 | 0.10986 | -0.0054933 | 0.016827 | 0.067131 | 0.0047809 | 0.075343 | 0.00037606 | 0.0015466 | -0.0040437 | 0.028984 | -0.011271 | 0.020956 | 0.0046869 | -0.0072652 | 0.004578 | -110.8246 | -25.8957 | -121.5683 | 0.14191 | -121.8796 | -121.756 | -0.009155 | -1.9913 | -0.050354 | 0.036621 | 0.050354 | 0.009155 | -0.068665 | -0.10071 | 0.022889 | 0.032044 | 10.9543 | 0.21057 | 0.18768 | -0.10529 | 121.788 | 121.7102 | -0.073242 | 121.7697 | 121.7285 | 0.018311 | -0.059509 | 121.9208 | 121.7834 | 95.8832 | -121.8658 | 121.8155 | 121.8292 | 119.7876 | -0.17853
1677.2188 | 122.113 | -121.7926 | 0.10986 | -0.013122 | 0.014264 | 0.072044 | 0.0049945 | 0.075984 | -0.0019739 | 5.1244e-05 | -0.0040437 | 0.027489 | -0.0093481 | 0.019675 | 0.0063959 | -0.0087606 | -0.036621 | -108.3252 | -25.9186 | -121.582 | 0.15106 | -121.9025 | -121.7789 | -0.086975 | -2.0187 | -0.091553 | 0.091553 | 0.073242 | 0 | -0.082397 | -0.10986 | 0.013733 | 0.041199 | 13.4674 | 0.21057 | 0.19684 | -0.14648 | 121.7926 | 121.7102 | -0.01831 | 121.7056 | 121.701 | -0.009156 | -0.036621 | 121.9437 | 121.756 | 95.874 | -121.8887 | 121.8842 | 121.8658 | 119.7739 | -0.19226
1678.9062 | 122.1039 | -121.7697 | 0.16479 | -0.0054933 | 0.019177 | 0.068626 | 0.010549 | 0.067652 | -0.00069214 | 0.16326 | -0.0040437 | 0.027275 | -0.0097755 | 0.022238 | 0.0023371 | -0.0083334 | 0.018311 | -120.0394 | -26.0788 | -121.5088 | 0.17853 | -121.8521 | -121.7056 | -0.059509 | -2.1057 | -0.07782 | 0.11444 | 0.12817 | 0.050354 | -0.059509 | -0.082398 | 0.064087 | 0.013733 | 1.7303 | 0.26093 | 0.19684 | -0.14648 | 121.8201 | 121.7102 | -0.050354 | 121.7102 | 121.6919 | -0.018311 | -0.036621 | 121.9482 | 121.788 | 95.6909 | -121.8704 | 121.8842 | 121.8979 | 119.664 | -0.2243
1680.6562 | 122.1359 | -121.8475 | 0.09613 | -0.0054933 | 0.016186 | 0.067986 | 0.0075581 | 0.070216 | -0.0015465 | -0.00016236 | -0.011673 | 0.029198 | -0.010203 | 0.022238 | 0.0046869 | -0.0079062 | -0.009155 | -120.1126 | -25.5569 | -121.5408 | 0.12817 | -121.8933 | -121.7697 | -0.073242 | -2.0096 | -0.086975 | 0.082397 | 0.10071 | -0.013733 | -0.091553 | -0.045777 | 0.07782 | 0.032044 | 1.7349 | 0.3067 | 0.22888 | -0.10528 | 121.8338 | 121.756 | -0.013733 | 121.7743 | 121.7606 | 0.004578 | 0.004578 | 121.9757 | 121.8384 | 96.2906 | -121.8658 | 121.9299 | 121.9482 | 119.838 | -0.18768
1682.3906 | 122.1222 | -121.8292 | 0.10986 | -0.013122 | 0.018963 | 0.067772 | 0.0071307 | 0.070643 | 0.00080326 | -0.0029394 | -0.011673 | 0.028343 | -0.0082801 | 0.024161 | 0.0027643 | -0.0072652 | -0.027466 | -120.1218 | -25.4334 | -121.5775 | 0.14648 | -121.9254 | -121.7834 | -0.086975 | -2.0416 | -0.10529 | 0.10071 | 0.091553 | -0.018311 | -0.07782 | -0.09613 | 0.045777 | 0.036621 | 1.7075 | 0.25177 | 0.20599 | -0.13733 | 121.8109 | 121.7514 | -0.009155 | 121.7422 | 121.7239 | -0.027466 | -0.01831 | 121.9757 | 121.8018 | 96.3959 | -121.8933 | 121.9299 | 121.9208 | 119.7876 | -0.18768
1684.0781 | 122.1313 | -121.8338 | 0.10986 | -0.020752 | 0.020459 | 0.068199 | 0.0067035 | 0.068934 | 0.00037606 | 0.0017602 | 0.0035858 | 0.029198 | -0.0091345 | 0.024161 | 0.0031915 | -0.010256 | 0.004578 | -120.1218 | -25.4334 | -121.5546 | 0.13275 | -121.9208 | -121.8109 | -0.045776 | -2.0142 | -0.086975 | 0.091553 | 0.086975 | -0.018311 | -0.068665 | -0.086975 | 0.022888 | 0.022888 | 1.712 | 0.27924 | 0.25635 | -0.10529 | 121.8155 | 121.7651 | -0.01831 | 121.788 | 121.7468 | -0.01831 | -0.022888 | 121.9666 | 121.8384 | 96.4005 | -121.9208 | 121.9254 | 121.9208 | 119.8196 | -0.17853
1685.75 | 122.0215 | -121.8521 | 0.14191 | -0.0054933 | 0.011059 | 0.071403 | 0.0043537 | 0.070429 | -0.0062463 | 0.0011194 | -0.011673 | 0.023216 | -0.01063 | 0.020956 | 0.0016963 | -0.0064108 | 0.009155 | -120.076 | -25.3922 | -121.5408 | 0.09613 | -121.8796 | -121.7697 | -0.045776 | -2.0279 | -0.022888 | 0.045776 | 0.054932 | 0.022888 | -0.054932 | -0.027466 | 0.082398 | -0.045777 | 1.7761 | 0.31128 | 0.22888 | -0.13275 | 121.875 | 121.7972 | -0.096131 | 121.8063 | 121.8292 | 0.032044 | -0.086975 | 121.9482 | 121.8613 | 96.46 | -121.9116 | 121.8979 | 121.907 | 119.8242 | -0.19684
1687.4844 | 122.1405 | -121.8338 | 0.10529 | 0.0021362 | 0.015973 | 0.070122 | 0.0069171 | 0.071925 | 0.0018713 | 0.00047844 | -0.011673 | 0.027703 | -0.0091345 | 0.022665 | 0.0034051 | -0.0094016 | -0.009155 | -119.7693 | -25.0305 | -121.5042 | 0.12817 | -121.9254 | -121.7972 | -0.10529 | -1.9958 | -0.10986 | 0.09613 | 0.10071 | -0.018311 | -0.068665 | -0.091553 | 0.036621 | 0.022888 | 2.0645 | 0.32959 | 0.29297 | -0.11444 | 121.8155 | 121.7651 | -0.009156 | 121.7285 | 121.7239 | -0.041198 | -0.004578 | 121.962 | 121.8246 | 96.8033 | -121.9025 | 121.9299 | 121.9345 | 119.838 | -0.17395
1689.1719 | 122.0398 | -121.8567 | 0.14648 | 0.0021362 | 0.01875 | 0.069481 | 0.0028583 | 0.072779 | 0.0029395 | 0.0019738 | -0.011673 | 0.029198 | -0.011271 | 0.02117 | 0.0078913 | -0.0083334 | -0.027466 | -120.1904 | -25.2823 | -121.6003 | 0.14648 | -121.9437 | -121.7926 | -0.073242 | -2.1011 | -0.11444 | 0.07782 | 0.09613 | -0.004578 | -0.09613 | -0.086976 | 0.064086 | 0 | 1.6663 | 0.25635 | 0.19226 | -0.17395 | 121.8521 | 121.7606 | -0.068664 | 121.7834 | 121.7422 | -0.018311 | -0.050354 | 122.0032 | 121.8292 | 96.5744 | -121.9391 | 121.9345 | 121.9528 | 119.7556 | -0.24261
1690.9375 | 122.0764 | -121.8567 | 0.1236 | -0.013122 | 0.019177 | 0.069267 | 0.0034991 | 0.12448 | 0.00016226 | 0.0017602 | -0.011673 | 0.029412 | -0.011271 | 0.021384 | 0.0068231 | -0.0079062 | 0.045776 | -23.9594 | -23.2956 | -121.5088 | 0.13275 | -121.8979 | -121.7377 | 0.041199 | -1.8036 | 0.009155 | 0.059509 | 0.059509 | 0.027466 | -0.022888 | -0.041199 | 0.11902 | 0.009155 | 97.8973 | 0.3479 | 0.22888 | -0.07782 | 121.8842 | 121.8338 | -0.064087 | 121.8979 | 121.8658 | 0.032043 | -0.064087 | 121.9894 | 121.9025 | 98.5611 | -121.8613 | 121.9162 | 121.9162 | 120.0531 | -0.14648
1692.6875 | 122.1313 | -121.7834 | 0.14191 | -0.013122 | 0.017468 | 0.070549 | 0.0092669 | 0.12704 | -0.0047509 | 0.1075 | -0.0040437 | 0.023857 | -0.0080665 | 0.020743 | 0.00084166 | -0.010042 | 0.10071 | -18.8004 | -23.5062 | -121.4218 | 0.14191 | -121.8384 | -121.701 | 0.068665 | -1.6754 | 0.073242 | 0.073242 | 0.082397 | 0.054932 | -0.004578 | -0.054932 | 0.082397 | 0 | 102.9831 | 0.36163 | 0.27924 | -0.041199 | 121.8384 | 121.7789 | -0.068665 | 121.8521 | 121.8567 | 0.07782 | -0.05951 | 121.9254 | 121.8842 | 98.2773 | -121.843 | 121.8567 | 121.8658 | 120.108 | -0.14649
1694.4219 | 122.113 | -121.843 | 0.13733 | -0.0054933 | 0.016827 | 0.069054 | 0.0075581 | 0.12597 | -0.0024011 | -0.0012306 | -0.019302 | 0.024712 | -0.0082801 | 0.021811 | 0.00084166 | -0.0081198 | 0.07782 | -17.4591 | -23.4192 | -121.4493 | 0.10071 | -121.8933 | -121.7468 | 0.041199 | -1.8173 | 0.032043 | 0.059509 | 0.054932 | 0.041199 | -0.032043 | -0.050354 | 0.096131 | -0.036621 | 104.3839 | 0.39368 | 0.29755 | -0.059509 | 121.8842 | 121.8109 | -0.07782 | 121.8842 | 121.875 | 0.064086 | -0.082397 | 121.9437 | 121.9208 | 98.4238 | -121.8842 | 121.9025 | 121.8979 | 120.0256 | -0.16937
1696.0938 | 122.049 | -121.8201 | 0.22888 | -0.0054933 | 0.019818 | 0.068413 | 0.0056355 | 0.12725 | 0.0052893 | 0.0021874 | -0.011673 | 0.029412 | -0.010203 | 0.022452 | 0.0074641 | -0.0091878 | 0.013733 | -16.7541 | -23.9136 | -121.55 | 0.16022 | -121.8796 | -121.756 | -0.26093 | -1.9547 | -0.36163 | 0.09613 | 0.091553 | -0.21515 | -0.31128 | -0.05951 | 0.064087 | -0.068665 | 105.0659 | 0.27008 | 0.20599 | -0.21515 | 121.6049 | 121.5088 | -0.13275 | 121.5591 | 121.4584 | -0.050354 | -0.13733 | 121.9803 | 121.8338 | 97.9065 | -121.9849 | 121.9162 | 121.9116 | 119.8654 | -0.54016
1697.8438 | 122.113 | -121.875 | 0.13275 | -0.0054933 | 0.018322 | 0.069908 | 0.0052081 | 0.12725 | -0.00069214 | -0.0018714 | -0.019302 | 0.02813 | -0.0099891 | 0.020529 | 0.0036189 | -0.010256 | -0.004578 | -16.1362 | -23.9731 | -121.5363 | 0.13733 | -121.9208 | -121.7743 | -0.12817 | -1.7487 | -0.14648 | 0.09613 | 0.10529 | -0.064087 | -0.13733 | -0.045776 | 0.10071 | 0.004578 | 105.7388 | 0.33875 | 0.23804 | -0.13733 | 121.8109 | 121.7377 | -0.036621 | 121.7468 | 121.7285 | -0.009155 | -0.027465 | 122.0123 | 121.8704 | 97.9019 | -121.907 | 121.9711 | 121.9803 | 120.1263 | -0.27008
1699.5156 | 122.0306 | -121.8842 | 0.14191 | -0.013122 | 0.01875 | 0.07119 | 8.127e-05 | 0.12576 | 0.0055029 | 0.0036828 | -0.011673 | 0.028343 | -0.012339 | 0.024161 | 0.0068231 | -0.0076926 | 0.009155 | -15.8295 | -24.0784 | -121.5408 | 0.15564 | -121.8933 | -121.7651 | -0.28381 | -2.0599 | -0.39368 | 0.11444 | 0.10071 | -0.23804 | -0.32044 | -0.009156 | 0.11902 | 0.013733 | 106.0547 | 0.34332 | 0.2243 | -0.13275 | 121.6461 | 121.5637 | -0.027466 | 121.6003 | 121.4905 | -0.073242 | -0.041199 | 122.0398 | 121.8933 | 97.8058 | -121.907 | 121.9986 | 121.9849 | 119.8242 | -0.46234
1701.25 | 122.0261 | -121.8887 | 0.14648 | 0.0021362 | 0.014691 | 0.071403 | 0.0032855 | 0.12747 | -0.0041101 | 0.00026484 | 0.0035858 | 0.024071 | -0.012552 | 0.019675 | 0.0040461 | -0.007479 | 0.073242 | -15.3214 | -23.8403 | -121.4813 | 0.086975 | -121.8796 | -121.7377 | -0.17853 | -1.8539 | -0.21057 | 0.054932 | 0.059509 | -0.19226 | -0.26093 | 0.009155 | 0.15106 | -0.059509 | 106.5674 | 0.40741 | 0.25635 | -0.073242 | 121.6965 | 121.6278 | -0.091552 | 121.7102 | 121.6782 | 0.050354 | -0.086975 | 121.9757 | 121.962 | 98.0484 | -121.8842 | 121.9437 | 121.9482 | 120.0348 | -0.40741
1703 | 122.0627 | -121.8887 | 0.13275 | -0.020752 | 0.017468 | 0.068626 | 0.0032855 | 0.12704 | 0.00080326 | 0.00090584 | -0.011673 | 0.024071 | -0.011271 | 0.021597 | 0.0059687 | -0.0087606 | 0.10071 | -15.097 | -24.0372 | -121.4676 | 0.10986 | -121.907 | -121.7606 | 0.07782 | -1.6022 | 0.032043 | 0.045776 | 0.036621 | 0.041199 | -0.041199 | -0.01831 | 0.12817 | -0.022888 | 106.7917 | 0.42114 | 0.29297 | -0.032043 | 121.9299 | 121.8475 | -0.086975 | 121.9666 | 121.9208 | 0.073242 | -0.09613 | 121.9986 | 121.9894 | 97.8516 | -121.8933 | 121.9345 | 121.9254 | 120.2866 | -0.17395
1704.6719 | 122.1405 | -121.8704 | 0.11902 | -0.013122 | 0.015759 | 0.070549 | 0.0084125 | 0.1311 | -0.0026147 | -0.00058956 | -0.0040437 | 0.024925 | -0.010416 | 0.019675 | 0.0012689 | -0.0098288 | 0.09613 | -15.0558 | -23.6984 | -121.4447 | 0.10529 | -121.8887 | -121.7697 | 0.041199 | -1.7349 | 0.013733 | 0.064087 | 0.068665 | 0.036621 | -0.022888 | -0.018311 | 0.10071 | -0.013733 | 106.8146 | 0.42572 | 0.32501 | -0.022889 | 121.907 | 121.8475 | -0.054932 | 121.9116 | 121.8842 | 0.036621 | -0.050354 | 121.9757 | 121.9666 | 98.172 | -121.8887 | 121.9345 | 121.9391 | 120.1355 | -0.14191
1706.4219 | 122.2 | -121.8658 | 0.1236 | -0.0054933 | 0.014264 | 0.074394 | 0.0062763 | 0.13024 | -0.0028283 | 0.073324 | -0.0040437 | 0.024498 | -0.010203 | 0.021597 | 0.0016963 | -0.0098288 | 0.10986 | -14.8499 | -23.8632 | -121.4264 | 0.15564 | -121.8796 | -121.7056 | 0.073242 | -1.4603 | 0.086975 | 0.086975 | 0.082397 | 0.064087 | -0.004578 | -0.013733 | 0.16022 | 0.032044 | 107.016 | 0.43945 | 0.27923 | -0.013733 | 121.9299 | 121.8613 | -0.036621 | 121.9391 | 121.9528 | 0.091553 | -0.041199 | 122.0215 | 121.9757 | 98.0026 | -121.8292 | 121.9528 | 121.9482 | 120.4056 | -0.12817
1708.1094 | 122.0947 | -121.8842 | 0.13733 | -0.0054933 | 0.018109 | 0.069267 | 0.0064899 | 0.12918 | 0.0027259 | 0.0017602 | -0.011673 | 0.027703 | -0.0097755 | 0.023093 | 0.0051141 | -0.01047 | 0.11444 | -14.6942 | -24.0372 | -121.4905 | 0.1236 | -121.8887 | -121.756 | 0.050354 | -1.6342 | -0.009155 | 0.054932 | 0.068665 | 0.022888 | -0.07782 | -0.004578 | 0.12817 | -0.013733 | 107.1899 | 0.39368 | 0.2655 | -0.022888 | 121.907 | 121.8063 | -0.082397 | 121.9345 | 121.875 | 0.068665 | -0.068664 | 122.0078 | 121.9986 | 97.847 | -121.8933 | 121.9391 | 121.9528 | 120.2499 | -0.21515
1709.8594 | 122.1771 | -121.8475 | 0.11902 | -0.020752 | 0.015759 | 0.071403 | 0.0069171 | 0.13046 | -0.0026147 | -0.0014442 | 0.0035858 | 0.024712 | -0.0087073 | 0.02117 | 0.0012689 | -0.0089742 | 0.09613 | -14.4928 | -23.941 | -121.4767 | 0.13275 | -121.9208 | -121.788 | 0.073242 | -1.5106 | 0.07782 | 0.050354 | 0.050354 | 0.059509 | -0.022888 | -0.073242 | 0.059509 | 0.013732 | 107.3547 | 0.37079 | 0.31128 | -0.022889 | 121.907 | 121.8246 | -0.068665 | 121.9208 | 121.9254 | 0.10071 | -0.068665 | 121.9803 | 121.9437 | 97.9065 | -121.907 | 121.8979 | 121.8979 | 120.3369 | -0.14191
1711.5469 | 122.0581 | -121.9025 | 0.14648 | -0.0054933 | 0.01875 | 0.069054 | 0.0043537 | 0.15524 | 0.0065711 | 0.0096642 | 0.0035858 | 0.031334 | -0.01063 | 0.023306 | 0.0083185 | -0.011751 | 0.032043 | -14.447 | -24.2798 | -121.5042 | 0.15106 | -121.9345 | -121.788 | -0.032043 | -1.6479 | 0.059509 | 0.10071 | 0.1236 | 0.013733 | -0.059509 | -0.032043 | 0.11444 | 0.004578 | 107.4554 | 0.39826 | 0.28381 | -0.11444 | 121.9162 | 121.843 | -0.045776 | 121.8704 | 121.962 | 0.11902 | -0.022888 | 122.0535 | 121.9345 | 97.6227 | -121.9345 | 122.0032 | 122.0261 | 120.2545 | -0.20599
1713.2969 | 122.1268 | -121.7972 | 0.10986 | -0.0054933 | 0.78202 | 0.070763 | 0.0052081 | 0.15801 | 0.75596 | -0.0042212 | -0.011673 | 0.025566 | -0.010416 | 0.020956 | 0.00084166 | -0.0098288 | 0.018311 | -14.0671 | -23.0896 | -2.5864 | 0.10071 | -121.8109 | -121.669 | 0.086975 | -1.0437 | 0.059509 | 0.068665 | 0.064087 | 0.059509 | -0.018311 | -0.013733 | 0.12817 | -0.009155 | 107.7301 | 119.2108 | 119.0826 | -0.091552 | 121.8567 | 121.7789 | -0.041198 | 121.8842 | 121.8567 | 0.07782 | -0.045776 | 121.8979 | 121.8155 | 98.7076 | -121.7789 | 121.8658 | 121.8613 | 120.7535 | -0.12817
1715.0469 | 122.1268 | -121.7926 | 0.11902 | -0.0054933 | 0.78758 | 0.071403 | 0.0060627 | 0.15759 | 0.76173 | -0.00037596 | -0.011673 | 0.028771 | -0.0097755 | 0.02352 | 0.0036189 | -0.0089742 | -0.059509 | -14.1861 | -23.259 | -2.6596 | 0.12817 | -121.843 | -121.7148 | -0.041199 | -1.181 | -0.11444 | 0.10986 | 0.10529 | 0.004578 | -0.054932 | -0.050354 | 0.07782 | 0.009155 | 107.6065 | 119.133 | 119.0552 | -0.17853 | 121.7972 | 121.7377 | -0.009156 | 121.7514 | 121.6782 | -0.059509 | -0.013733 | 121.9208 | 121.7331 | 98.5336 | -121.8338 | 121.9025 | 121.8979 | 120.6116 | -0.17395
1716.7344 | 122.0718 | -121.8384 | 0.14191 | -0.013122 | 0.7863 | 0.070122 | 0.0032855 | 0.16079 | 0.76386 | 0.00090584 | 0.0035858 | 0.031975 | -0.0097755 | 0.021384 | 0.0072505 | -0.011538 | 0.009155 | -13.9572 | -21.7209 | -2.6459 | 0.1236 | -121.8338 | -121.6965 | 0.041199 | -1.0941 | -0.054932 | 0.086975 | 0.082397 | 0.009155 | -0.068665 | 0.004578 | 0.14191 | -0.018311 | 107.8812 | 119.1925 | 119.0506 | -0.13275 | 121.8475 | 121.7697 | -0.054932 | 121.8796 | 121.7834 | 0.013733 | -0.05951 | 121.962 | 121.8475 | 100.1175 | -121.8384 | 121.9254 | 121.9208 | 120.7443 | -0.21057
1718.5 | 122.0947 | -121.8109 | 0.11444 | 0.0021362 | 0.78651 | 0.068626 | 0.0067035 | 0.15332 | 0.75981 | 0.00069204 | -0.011673 | 0.029412 | -0.0089209 | 0.023734 | 0.0025507 | -0.008547 | -0.068665 | -13.884 | -23.2361 | -2.6688 | 0.11902 | -121.8338 | -121.6965 | -0.036621 | -1.1856 | -0.10071 | 0.086975 | 0.10071 | 0.018311 | -0.068665 | -0.022888 | 0.11444 | 0.004578 | 107.9269 | 119.1422 | 119.0277 | -0.18311 | 121.8292 | 121.7422 | -0.027466 | 121.7743 | 121.7102 | -0.032043 | -0.013733 | 121.9299 | 121.7422 | 98.5748 | -121.8109 | 121.8979 | 121.9116 | 120.6253 | -0.18311
1720.2344 | 122.1085 | -121.788 | 0.12817 | -0.0054933 | 0.78608 | 0.068199 | 0.0039265 | 0.15588 | 0.76109 | 0.0026148 | -0.011673 | 0.027062 | -0.01063 | 0.023947 | 0.0053279 | -0.0096152 | -0.054932 | -13.7787 | -23.5199 | -2.6093 | 0.10986 | -121.8292 | -121.701 | -0.009155 | -1.1856 | -0.07782 | 0.10986 | 0.10529 | 0.022888 | -0.064087 | -0.041199 | 0.086975 | -0.018311 | 108.0093 | 119.1788 | 119.0918 | -0.18311 | 121.8109 | 121.7239 | -0.018311 | 121.7789 | 121.7102 | -0.013733 | -0.022888 | 121.8979 | 121.7331 | 98.2681 | -121.8292 | 121.8979 | 121.8933 | 120.6024 | -0.19226
1721.9219 | 122.0306 | -121.7972 | 0.13733 | -0.0054933 | 0.78587 | 0.070335 | 0.0013629 | 0.15075 | 0.75746 | 0.002401 | -0.011673 | 0.025139 | -0.011484 | 0.020102 | 0.0042597 | -0.0064108 | -0.050354 | -13.6963 | -22.9019 | -2.7924 | 0.091553 | -121.788 | -121.669 | 0.027466 | -0.96588 | 0.013733 | 0.09613 | 0.082397 | 0.050354 | -0.027466 | 0.009155 | 0.12817 | -0.045776 | 108.1009 | 119.0048 | 118.8766 | -0.18768 | 121.8475 | 121.7697 | -0.041199 | 121.8246 | 121.8109 | 0.041199 | -0.054932 | 121.8887 | 121.7468 | 98.8953 | -121.8063 | 121.8933 | 121.8796 | 120.8313 | -0.16479
1723.6719 | 121.9345 | -121.8109 | 0.16479 | -0.013122 | 0.78288 | 0.069481 | 0.0060627 | 0.15951 | 0.75425 | 0.0026148 | -0.0040437 | 0.025139 | -0.0095619 | 0.021811 | 0.0031915 | -0.0079062 | 0.036621 | -13.5452 | -20.9152 | -2.6276 | 0.068665 | -121.7331 | -121.637 | 0.050354 | -0.94757 | 0.022888 | 0.059509 | 0.050354 | 0.050354 | -0.018311 | 0.07782 | 0.17395 | -0.09613 | 108.2657 | 119.1834 | 119.0094 | -0.12817 | 121.8613 | 121.7926 | -0.10529 | 121.8613 | 121.8338 | 0.041199 | -0.11444 | 121.8796 | 121.8475 | 100.8957 | -121.8018 | 121.8704 | 121.8613 | 120.8633 | -0.18311
1725.4219 | 122.0718 | -121.6461 | 0.2243 | -0.013122 | 0.78651 | 0.067131 | 0.0084125 | 0.53421 | 0.75938 | 0.0015466 | -0.0040437 | 0.028557 | -0.0082801 | 0.021597 | 0.0046869 | -0.010256 | 0.10071 | -13.5498 | -23.1171 | -2.6367 | 0.21515 | -121.6415 | -121.5179 | -0.041199 | -0.97046 | -0.10071 | 0.1831 | 0.19684 | -0.045776 | -0.12817 | 0.004577 | 0.12817 | -0.009155 | 108.0963 | 119.0094 | 118.8812 | -0.1236 | 121.6003 | 121.5179 | -0.041199 | 121.6049 | 121.5454 | 0.027466 | -0.027466 | 121.8613 | 121.7468 | 98.5291 | -121.7422 | 121.8292 | 121.843 | 120.6757 | -0.35248
1727.0938 | 121.9711 | -121.8475 | 0.14191 | -0.0054933 | 0.78544 | 0.068626 | 0.0037127 | 0.15994 | 0.75938 | 0.0015466 | -0.0040437 | 0.029839 | -0.0087073 | 0.020956 | 0.010027 | -0.0076926 | -0.073242 | -13.559 | -22.1558 | -2.6459 | 0.11902 | -121.7972 | -121.6827 | -0.19684 | -1.0345 | -0.2655 | 0.09613 | 0.091553 | -0.14648 | -0.21515 | 0.050354 | 0.16479 | -0.022888 | 108.2886 | 119.2017 | 119.0369 | -0.21515 | 121.701 | 121.6324 | -0.045777 | 121.6507 | 121.582 | -0.050354 | -0.050354 | 121.9666 | 121.7743 | 99.6918 | -121.8246 | 121.9437 | 121.9391 | 120.813 | -0.35706
1728.8438 | 121.9757 | -121.8567 | 0.15564 | -0.013122 | 0.7863 | 0.067986 | 0.0037127 | 0.16079 | 0.75981 | 0.0019738 | -0.0040437 | 0.029625 | -0.0097755 | 0.023093 | 0.0059687 | -0.0091878 | -0.022888 | -13.4857 | -19.6335 | -2.6001 | 0.10986 | -121.8063 | -121.6782 | 0 | -0.93842 | -0.10529 | 0.086975 | 0.09613 | 0.018311 | -0.068665 | 0.050354 | 0.17853 | -0.045777 | 108.371 | 119.2566 | 119.0781 | -0.17853 | 121.875 | 121.788 | -0.068665 | 121.8567 | 121.7514 | -0.036621 | -0.05951 | 121.9666 | 121.8338 | 102.2232 | -121.8338 | 121.9437 | 121.9528 | 120.9183 | -0.22431
1730.5938 | 122.0581 | -121.7972 | 0.12817 | -0.020752 | 0.78437 | 0.06884 | 0.0084125 | 0.15502 | 0.75233 | -0.0014442 | -0.019302 | 0.026207 | -0.0065711 | 0.020529 | 0.0031915 | -0.0070516 | -0.091553 | -13.4216 | -20.7413 | -2.5726 | 0.11902 | -121.8155 | -121.6599 | -0.064087 | -0.91553 | -0.068665 | 0.091553 | 0.10071 | 0.004578 | -0.068665 | -0.018311 | 0.13733 | -0.009155 | 108.3755 | 119.2245 | 119.0872 | -0.21973 | 121.8018 | 121.7285 | -0.036621 | 121.7331 | 121.7285 | 0 | -0.027466 | 121.9162 | 121.7056 | 101.0559 | -121.788 | 121.8887 | 121.8979 | 120.8817 | -0.19684
1732.2812 | 121.962 | -121.8246 | 0.16022 | -0.013122 | 0.78715 | 0.067772 | 0.0015765 | 0.15481 | 0.76002 | -0.00016236 | -0.019302 | 0.028343 | -0.0089209 | 0.021384 | 0.0057551 | -0.0094016 | -0.054932 | -13.3987 | -20.7459 | -2.3987 | 0.12817 | -121.7972 | -121.6553 | -0.1831 | -0.93384 | -0.25635 | 0.086975 | 0.1236 | -0.11444 | -0.20142 | 0.027466 | 0.16937 | -0.032043 | 108.4259 | 119.426 | 119.2566 | -0.21515 | 121.7102 | 121.6232 | -0.073242 | 121.6415 | 121.5683 | -0.054932 | -0.036621 | 121.9528 | 121.7697 | 101.0788 | -121.8155 | 121.9116 | 121.9482 | 120.8908 | -0.36163
1734.0312 | 121.9986 | -121.7834 | 0.18768 | -0.020752 | 0.78779 | 0.068626 | 0.0056355 | 0.27615 | 0.76023 | 0.001333 | -0.019302 | 0.027489 | -0.010203 | 0.019675 | 0.0070367 | -0.0087606 | -0.059509 | -13.385 | -21.936 | -2.3666 | 0.16479 | -121.7651 | -121.6553 | -0.022888 | -0.91095 | -0.064087 | 0.13275 | 0.13275 | 0.059509 | -0.032043 | 0.01831 | 0.12817 | -0.022888 | 108.3984 | 119.4168 | 119.2886 | -0.24719 | 121.843 | 121.7514 | -0.054932 | 121.7606 | 121.7194 | -0.032044 | -0.054932 | 121.9482 | 121.7239 | 99.8474 | -121.843 | 121.9162 | 121.9162 | 120.8725 | -0.21973
1735.7812 | 122.0581 | -121.7972 | 0.10529 | -0.013122 | 0.7816 | 0.070122 | 0.0084125 | 0.15567 | 0.7519 | 5.1244e-05 | -0.019302 | 0.024498 | -0.0095619 | 0.020316 | 0.0029779 | -0.0098288 | 0 | -13.2065 | -21.3409 | -2.5589 | 0.09613 | -121.8018 | -121.6461 | -0.027466 | -0.76904 | -0.022888 | 0.068665 | 0.073242 | 0.027466 | -0.050354 | -0.004578 | 0.15106 | -0.009156 | 108.5907 | 119.2383 | 119.0872 | -0.10529 | 121.8246 | 121.7468 | -0.036621 | 121.7697 | 121.7743 | 0.027466 | -0.032044 | 121.8933 | 121.7972 | 100.4562 | -121.7514 | 121.8658 | 121.8704 | 121.0281 | -0.15564
1737.4531 | 121.9437 | -121.8292 | 0.16937 | -0.020752 | 0.78309 | 0.069054 | 0.0056355 | 0.15759 | 0.75767 | 0.0019738 | -0.0040437 | 0.029625 | -0.0082801 | 0.020956 | 0.0057551 | -0.0096152 | -0.07782 | -13.3209 | -21.8582 | -2.5864 | 0.11902 | -121.8018 | -121.669 | -0.19226 | -0.9201 | -0.27466 | 0.091553 | 0.09613 | -0.1236 | -0.21057 | 0.027466 | 0.16022 | -0.050354 | 108.5083 | 119.2429 | 119.0826 | -0.24719 | 121.7056 | 121.6187 | -0.07782 | 121.637 | 121.5546 | -0.064087 | -0.073243 | 121.9482 | 121.7514 | 99.971 | -121.8384 | 121.9208 | 121.9254 | 120.9091 | -0.37994
1739.2031 | 122.0947 | -121.7606 | 0.11902 | -0.0054933 | 0.78416 | 0.072472 | 0.0077717 | 0.15588 | 0.74763 | -0.00016236 | -0.011673 | 0.025566 | -0.011698 | 0.020956 | 0.00020086 | -0.0087606 | -0.018311 | -13.1104 | -22.1649 | -2.3712 | 0.09613 | -121.7331 | -121.6553 | 0.041199 | -0.72327 | 0.054932 | 0.059509 | 0.07782 | 0.050354 | -0.032043 | 0.027466 | 0.10529 | -0.022889 | 108.6502 | 119.3893 | 119.2841 | -0.13733 | 121.8109 | 121.7285 | -0.05951 | 121.8018 | 121.8155 | 0.086975 | -0.041199 | 121.8567 | 121.7422 | 99.5956 | -121.7743 | 121.8201 | 121.8384 | 121.0373 | -0.15106
1740.8906 | 121.9757 | -121.8292 | 0.13275 | -0.0054933 | 0.77925 | 0.070335 | 0.0041401 | 0.15609 | 0.75105 | -0.0012306 | -0.011673 | 0.026421 | -0.011057 | 0.020956 | 0.0029779 | -0.0083334 | 0.004578 | -13.0875 | -22.0871 | -2.5269 | 0.07782 | -121.7606 | -121.6049 | 0.009155 | -0.74158 | 0.009155 | 0.073242 | 0.064087 | 0.068665 | -0.045776 | 0.068665 | 0.22431 | -0.054931 | 108.7418 | 119.3024 | 119.0781 | -0.12817 | 121.8979 | 121.7834 | -0.059509 | 121.8384 | 121.8384 | 0.054931 | -0.068664 | 121.907 | 121.8338 | 99.7421 | -121.7377 | 121.9025 | 121.8933 | 121.0876 | -0.17853
1742.6406 | 121.9803 | -121.7743 | 0.12817 | -0.0054933 | 0.77882 | 0.068413 | 0.0054217 | 0.15759 | 0.75212 | -0.0027258 | -0.011673 | 0.026207 | -0.010416 | 0.021384 | 0.00062806 | -0.010683 | 0.045776 | -12.9776 | -22.11 | -2.3666 | 0.073242 | -121.7606 | -121.6324 | 0.073242 | -0.70038 | 0.050354 | 0.059509 | 0.073242 | 0.045776 | -0.032043 | 0.013733 | 0.14191 | -0.054932 | 108.7967 | 119.4077 | 119.2657 | -0.082398 | 121.8201 | 121.7422 | -0.068665 | 121.8475 | 121.8246 | 0.082397 | -0.054932 | 121.8475 | 121.8201 | 99.6643 | -121.7606 | 121.8338 | 121.8475 | 121.0739 | -0.16022
1744.3906 | 122.0901 | -121.7834 | 0.10071 | -0.013122 | 0.78331 | 0.069481 | 0.0047809 | 0.1578 | 0.75981 | 0.036367 | -0.0040437 | 0.028984 | -0.0091345 | 0.02352 | 0.0057551 | -0.011324 | -0.004578 | -13.0508 | -20.6726 | -2.298 | 0.15106 | -121.7514 | -121.6415 | -0.032043 | -0.81482 | -0.064087 | 0.1236 | 0.09613 | 0.045776 | -0.050354 | 0.032043 | 0.14191 | 0.050354 | 108.7326 | 119.4855 | 119.3436 | -0.10529 | 121.8292 | 121.7331 | 0.022888 | 121.7514 | 121.7194 | -0.013733 | -0.004578 | 121.9345 | 121.7789 | 101.1108 | -121.7422 | 121.907 | 121.8796 | 120.9686 | -0.15106
1746.1406 | 121.9803 | -121.788 | 0.14648 | -0.020752 | 0.78502 | 0.069695 | 0.0030719 | 0.15866 | 0.75788 | 0.002401 | -0.0040437 | 0.027916 | -0.0084937 | 0.022238 | 0.0074641 | -0.0081198 | -0.064087 | -13.266 | -21.46 | -2.3575 | 0.11444 | -121.8018 | -121.6553 | -0.041199 | -0.89722 | -0.13275 | 0.10529 | 0.086975 | 0.018311 | -0.064087 | -0.013733 | 0.13275 | -0.032043 | 108.522 | 119.4305 | 119.2978 | -0.21057 | 121.8063 | 121.7239 | -0.041198 | 121.7468 | 121.6553 | -0.068664 | -0.059509 | 121.9025 | 121.7239 | 100.3281 | -121.8018 | 121.8933 | 121.875 | 120.8908 | -0.21057
1747.875 | 121.962 | -121.8018 | 0.14648 | -0.0054933 | 0.77711 | 0.07119 | 0.0041401 | 0.15951 | 0.75083 | 0.001333 | -0.011673 | 0.020867 | -0.012552 | 0.021811 | 0.0031915 | -0.008547 | -0.027466 | -13.0829 | -22.1649 | -2.3254 | 0.07782 | -121.7651 | -121.5042 | -0.1236 | -0.82398 | -0.14191 | 0.07782 | 0.059509 | -0.082397 | -0.19226 | 0.036621 | 0.29755 | -0.068664 | 108.7189 | 119.4763 | 119.1788 | -0.17395 | 121.7194 | 121.6095 | -0.068664 | 121.6782 | 121.6599 | 0.050354 | -0.086975 | 121.8796 | 121.7743 | 99.6368 | -121.6507 | 121.8796 | 121.8613 | 120.9778 | -0.33874
1749.5469 | 122.0627 | -121.5363 | 0.32501 | -0.0054933 | 0.78053 | 0.069267 | 0.0060627 | 0.15673 | 0.75724 | 0.74816 | -0.0040437 | 0.028557 | -0.0084937 | 0.021384 | 0.0061823 | -0.01047 | 0.21515 | -13.0829 | -21.8628 | -2.0737 | 0.31586 | -121.4539 | -121.3531 | 0.23346 | -0.68207 | 0.15564 | 0.28839 | 0.29297 | 0.21973 | 0.15564 | 0.082398 | 0.18311 | -0.009155 | 108.4534 | 119.4626 | 119.2795 | -0.10986 | 121.756 | 121.6919 | -0.036621 | 121.7697 | 121.6919 | 0 | -0.032043 | 121.8521 | 121.7514 | 99.6735 | -121.6782 | 121.8246 | 121.8292 | 120.8542 | -0.16937
1751.2344 | 122.0169 | -121.7789 | 0.14191 | -0.0054933 | 0.78117 | 0.069481 | 0.0028583 | 0.15737 | 0.75212 | 0.0032556 | -0.019302 | 0.026634 | -0.011271 | 0.022665 | 0.0049005 | -0.010683 | -0.018311 | -13.0005 | -21.9498 | -2.3575 | 0.10986 | -121.7606 | -121.6415 | 0.050354 | -0.76904 | 0.009155 | 0.059509 | 0.068665 | 0.045776 | -0.027466 | 0.018311 | 0.13733 | -0.032044 | 108.7784 | 119.4214 | 119.2841 | -0.16022 | 121.8246 | 121.7514 | -0.082398 | 121.8292 | 121.788 | 0.036621 | -0.073242 | 121.8887 | 121.7606 | 99.8291 | -121.7834 | 121.8384 | 121.8475 | 121.0098 | -0.16937
1752.9844 | 122.0169 | -121.7651 | 0.13275 | -0.020752 | 0.78117 | 0.071403 | 0.0054217 | 0.15545 | 0.75382 | 0.0038964 | -0.0040437 | 0.026848 | -0.011271 | 0.021384 | 0.0057551 | -0.0081198 | -0.032043 | -12.9639 | -21.6614 | -2.3254 | 0.09613 | -121.7697 | -121.6553 | 0.045776 | -0.7782 | -0.004578 | 0.054932 | 0.064087 | 0.045776 | -0.022888 | -0.004577 | 0.10986 | -0.036621 | 108.8013 | 119.4397 | 119.3298 | -0.16479 | 121.8109 | 121.7422 | -0.077819 | 121.8109 | 121.7606 | 0.01831 | -0.068664 | 121.8613 | 121.7331 | 100.1038 | -121.788 | 121.8201 | 121.8292 | 120.9869 | -0.15564
1754.6719 | 122.0764 | -121.7697 | 0.13275 | -0.013122 | 0.7801 | 0.069908 | 0.0092669 | 0.1593 | 0.74891 | 0.00090584 | -0.011673 | 0.024925 | -0.0091345 | 0.018179 | -0.00022634 | -0.0096152 | 0.027466 | -12.8174 | -22.3297 | -2.2293 | 0.07782 | -121.7514 | -121.6415 | 0.064087 | -0.65002 | 0.059509 | 0.050354 | 0.059509 | 0.054932 | -0.018311 | 0.01831 | 0.12817 | -0.054931 | 108.9523 | 119.5404 | 119.4122 | -0.10529 | 121.8246 | 121.7514 | -0.082397 | 121.8338 | 121.8292 | 0.07782 | -0.073242 | 121.8475 | 121.7972 | 99.44 | -121.7743 | 121.8201 | 121.8292 | 121.1197 | -0.15106
1756.4219 | 122.049 | -121.7606 | 0.10529 | -0.0054933 | 0.77775 | 0.06649 | 0.0096943 | 0.15844 | 0.75126 | 0.00047844 | -0.0040437 | 0.025353 | -0.01063 | 0.023093 | -0.00022634 | -0.011324 | 0.022888 | -12.7945 | -22.0276 | -2.2476 | 0.07782 | -121.7422 | -121.6095 | -0.07782 | -0.70953 | -0.10986 | 0.054932 | 0.064087 | -0.10071 | -0.16479 | 0.01831 | 0.15106 | -0.027466 | 108.9661 | 119.5129 | 119.3619 | -0.082398 | 121.6599 | 121.5958 | -0.050354 | 121.6827 | 121.6507 | 0.054932 | -0.041199 | 121.8384 | 121.7834 | 99.733 | -121.7148 | 121.8155 | 121.8246 | 121.051 | -0.27008
1758.1719 | 121.994 | -121.8063 | 0.14191 | -0.0054933 | 0.78117 | 0.067558 | 0.0017901 | 0.15588 | 0.75447 | 0.0028284 | -0.011673 | 0.028771 | -0.0093481 | 0.02117 | 0.0053279 | -0.010683 | -0.054932 | -12.9227 | -22.4945 | -2.2842 | 0.11902 | -121.7743 | -121.6736 | -0.022888 | -0.85602 | -0.12817 | 0.09613 | 0.10986 | 0.009155 | -0.054932 | 0.032043 | 0.13275 | -0.022888 | 108.8837 | 119.5221 | 119.3893 | -0.19684 | 121.8155 | 121.7514 | -0.045777 | 121.7834 | 121.6782 | -0.073242 | -0.032044 | 121.9254 | 121.7514 | 99.3118 | -121.8155 | 121.9025 | 121.9162 | 120.9503 | -0.19684
1759.8438 | 122.0764 | -121.7651 | 0.11444 | -0.028381 | 0.7769 | 0.069481 | 0.0073443 | 0.15567 | 0.74635 | 0.0011194 | -0.011673 | 0.026421 | -0.0089209 | 0.022025 | 0.0016963 | -0.0091878 | 0.059509 | -12.6892 | -21.9955 | -2.1194 | 0.07782 | -121.7239 | -121.6187 | -0.082397 | -0.6546 | -0.09613 | 0.064087 | 0.07782 | -0.082397 | -0.18768 | 0.041199 | 0.14648 | -0.036621 | 109.0759 | 119.6457 | 119.4992 | -0.054932 | 121.6827 | 121.5775 | -0.050354 | 121.6827 | 121.669 | 0.091553 | -0.036621 | 121.843 | 121.8246 | 99.7696 | -121.7331 | 121.8292 | 121.843 | 121.1105 | -0.30212
1761.5938 | 122.1039 | -121.8704 | 0.10529 | -0.0054933 | 0.07301 | 0.0021896 | 0.0013629 | 0.014887 | 0.0031531 | 0.001333 | -0.019302 | 0.031548 | -0.012339 | 0.020743 | 0.0070367 | -0.01047 | 0.082397 | 0.045776 | 0.17395 | 0.14191 | 0.16479 | -0.036621 | -0.19684 | 0.064087 | 0.073242 | -0.086975 | 0.059509 | 0.059509 | 0.027466 | -0.064087 | 121.8338 | 121.6736 | 0.059509 | 121.9162 | 122.0123 | 0.33875 | -0.022889 | 121.8979 | 121.8063 | -0.045777 | 121.9345 | 121.7834 | -0.022888 | -0.045777 | 122.0352 | 121.9528 | 122.0444 | -0.30212 | 121.9299 | 121.9299 | 121.9437 | -0.16937
1763.3438 | 122.081 | -121.8979 | 0.10071 | -0.020752 | 0.066815 | 0.0045394 | 0.0034991 | 0.014033 | -0.0036829 | -0.0012306 | -0.0040437 | 0.023216 | -0.010416 | 0.020956 | 0.00041446 | -0.0072652 | 0.004578 | 0.041199 | 0.13733 | 0.14648 | 0.14648 | 0 | -0.14191 | 0.027466 | 0.09613 | -0.018311 | 0.045776 | 0.041199 | 0.013733 | -0.064087 | 121.8979 | 121.756 | 0.045776 | 121.9391 | 122.0444 | 0.28839 | -0.09613 | 121.9116 | 121.8338 | -0.054932 | 121.9254 | 121.8796 | 0.045776 | -0.059509 | 122.0444 | 121.9025 | 122.0352 | -0.24262 | 121.9437 | 121.9391 | 121.994 | -0.1648
1765.0312 | 122.0581 | -121.8887 | 0.1236 | -0.013122 | 0.07066 | 0.0015488 | 0.0034991 | 0.016383 | 0.00080326 | -0.00037596 | 0.0035858 | 0.025353 | -0.0063575 | 0.01882 | 0.0076777 | -0.010042 | 0.091553 | 0.10529 | 0.17853 | 0.17395 | 0.1236 | 0.004578 | -0.16479 | 0.11444 | 0.13275 | 0 | 0.027466 | 0.013733 | 0.041199 | -0.036621 | 121.8933 | 121.7239 | 0 | 121.994 | 122.0627 | 0.33874 | -0.032043 | 121.9299 | 121.8521 | -0.09613 | 122.0032 | 121.8887 | 0.036621 | -0.10986 | 122.0123 | 121.9803 | 122.0673 | -0.28839 | 121.9162 | 121.9025 | 122.0215 | -0.16022
1766.7812 | 122.1634 | -121.8704 | 0.10071 | -0.028381 | 0.072155 | 0.0030442 | 0.0077717 | 0.014674 | -0.0026147 | -0.002085 | -0.0040437 | 0.024498 | -0.0093481 | 0.018393 | 0.0016963 | -0.007479 | 0.082397 | 0.14191 | 0.18768 | 0.17853 | 0.12817 | -0.004578 | -0.13733 | 0.091553 | 0.1831 | 0.032043 | 0.022888 | 0.045776 | 0.027466 | -0.045776 | 121.8658 | 121.7331 | 0.027466 | 122.0123 | 122.049 | 0.31586 | -0.018311 | 121.8979 | 121.8246 | -0.07782 | 121.962 | 121.9025 | 0.077819 | -0.054932 | 121.9986 | 121.9528 | 122.0581 | -0.23804 | 121.8933 | 121.9162 | 122.0535 | -0.14648
1768.5156 | 122.0901 | -121.9299 | 0.13733 | -0.013122 | 0.074078 | 0.0013352 | 0.0030719 | 0.016596 | 0.0033667 | -0.00037596 | -0.0040437 | 0.029839 | -0.011271 | 0.022665 | 0.0051141 | -0.010256 | -0.004578 | -0.045776 | 0.022888 | 0.082397 | 0.16022 | -0.041199 | -0.17853 | -0.004578 | -0.022888 | -0.14648 | 0.068665 | 0.07782 | -0.004578 | -0.091553 | 121.8887 | 121.7514 | 0.022888 | 121.8842 | 122.0123 | 0.26092 | -0.14191 | 121.9254 | 121.8384 | -0.068664 | 121.9254 | 121.7834 | -0.054931 | -0.059509 | 122.0901 | 121.9254 | 121.9528 | -0.31586 | 121.9986 | 122.0078 | 121.907 | -0.22888
1770.1875 | 122.1268 | -121.8979 | 0.10071 | -0.013122 | 0.070874 | 0.00069421 | 0.0037127 | 0.013392 | 0.0035803 | -0.0014442 | 0.0035858 | 0.025566 | -0.010843 | 0.020102 | 0.0040461 | -0.0089742 | 0.068665 | 0.082397 | 0.12817 | 0.15564 | 0.12817 | 0 | -0.1236 | 0.11444 | 0.1236 | -0.004578 | 0.027466 | 0.036621 | 0.018311 | -0.054932 | 121.8979 | 121.7743 | 0.027466 | 121.9803 | 122.0535 | 0.27924 | -0.032043 | 121.9162 | 121.843 | -0.073242 | 122.0123 | 121.8933 | 0.050354 | -0.064087 | 122.0261 | 121.9666 | 122.0261 | -0.2243 | 121.9254 | 121.9345 | 122.0215 | -0.15564
1771.9219 | 122.1222 | -121.9254 | 0.10529 | 0.0021362 | 0.069592 | 0.00026701 | -0.00034613 | 0.016596 | 0.00016226 | -0.0031532 | -0.0040437 | 0.025139 | -0.013193 | 0.021384 | 0.0061823 | -0.0087606 | 0.082397 | 0.091553 | 0.14648 | 0.17853 | 0.12817 | 0.013733 | -0.1236 | 0.10071 | 0.13275 | 0.004578 | 0.018311 | 0.032043 | 0.032043 | -0.027466 | 121.9391 | 121.8018 | 0.022888 | 122.0169 | 122.1039 | 0.30212 | -0.022889 | 121.9574 | 121.8979 | -0.086975 | 122.0261 | 121.9299 | 0.032044 | -0.073243 | 122.0535 | 122.0078 | 122.0718 | -0.22888 | 121.9437 | 121.9574 | 122.0581 | -0.13275
1773.6094 | 122.0993 | -121.9391 | 0.11444 | -0.020752 | 0.067242 | 0.0017624 | 0.0071307 | 0.013819 | -0.0019739 | -0.0050758 | -0.0040437 | 0.025994 | -0.0097755 | 0.022025 | -0.00086734 | -0.0087606 | 0.045776 | 0.059509 | 0.10529 | 0.13733 | 0.13275 | 0 | -0.12817 | 0.027466 | 0.086975 | -0.032043 | 0.036621 | 0.045776 | 0.013733 | -0.054932 | 121.9391 | 121.8109 | 0.01831 | 121.9986 | 122.0764 | 0.2655 | -0.068665 | 121.9528 | 121.8842 | -0.07782 | 121.9666 | 121.907 | 0.022889 | -0.068665 | 122.0718 | 121.9849 | 122.0444 | -0.24262 | 121.9757 | 121.9849 | 122.0261 | -0.16937
1775.3438 | 122.1725 | -121.9162 | 0.10071 | -0.0054933 | 0.072369 | 0.0024032 | 0.0084125 | 0.015101 | -0.0015465 | -0.002085 | -0.0040437 | 0.025566 | -0.010843 | 0.019247 | 0.0012689 | -0.010683 | 0.086975 | 0.10529 | 0.16022 | 0.1831 | 0.13733 | -0.004578 | -0.13733 | 0.082397 | 0.16937 | 0.009155 | 0.045776 | 0.054932 | 0.032043 | -0.073242 | 121.9116 | 121.7789 | 0.036621 | 122.0215 | 122.0993 | 0.32043 | -0.013733 | 121.9482 | 121.843 | -0.054932 | 121.9986 | 121.9254 | 0.082397 | -0.045776 | 122.0535 | 122.0032 | 122.0764 | -0.23804 | 121.962 | 121.9711 | 122.0856 | -0.17395
1777.0781 | 122.1863 | -121.9162 | 0.086975 | -0.0054933 | 0.072369 | 0.00048061 | 0.0086261 | 0.01681 | -0.0017603 | -0.0010168 | -0.011673 | 0.027275 | -0.01063 | 0.023093 | 0.0010553 | -0.010683 | 0.10986 | 0.12817 | 0.16937 | 0.17853 | 0.14191 | 0.004578 | -0.13275 | 0.086975 | 0.1831 | 0.027466 | 0.022888 | 0.032043 | 0.032043 | -0.054932 | 121.9208 | 121.7834 | 0.054932 | 122.0444 | 122.0947 | 0.31128 | 0.022888 | 121.9482 | 121.8613 | -0.064087 | 122.0032 | 121.9437 | 0.082398 | -0.054932 | 122.0581 | 122.0261 | 122.0856 | -0.21973 | 121.9391 | 121.9482 | 122.0993 | -0.14191
1778.7656 | 122.1634 | -121.9437 | 0.11444 | -0.0054933 | 0.072369 | 5.3406e-05 | 0.0028583 | 0.012965 | 0.0052893 | -0.0012306 | 0.0035858 | 0.029198 | -0.010416 | 0.022452 | 0.0081049 | -0.010683 | 0.022888 | -0.045776 | -0.004578 | 0.091553 | 0.1831 | -0.036621 | -0.16022 | 0.022888 | -0.013733 | -0.12817 | 0.07782 | 0.050354 | 0 | -0.091553 | 121.907 | 121.7834 | 0.068664 | 121.8979 | 122.0352 | 0.25177 | -0.091553 | 121.9437 | 121.8521 | -0.036621 | 121.9666 | 121.8155 | -0.036621 | -0.064087 | 122.1268 | 121.9666 | 121.9391 | -0.27466 | 122.0215 | 121.994 | 121.9299 | -0.20599
1780.5156 | 122.2366 | -121.9025 | 0.10071 | -0.013122 | 0.073864 | 0.00026701 | 0.0043537 | 0.011683 | 0.0035803 | 0.0021874 | 0.0035858 | 0.028771 | -0.0078529 | 0.022025 | 0.0042597 | -0.0098288 | 0.036621 | 0.018311 | 0.059509 | 0.11902 | 0.16937 | -0.032043 | -0.16022 | 0.045776 | 0.086975 | -0.082397 | 0.07782 | 0.07782 | 0.009155 | -0.068665 | 121.8704 | 121.7422 | 0.068665 | 121.9208 | 122.0215 | 0.27924 | -0.064087 | 121.9116 | 121.8338 | -0.022888 | 121.9482 | 121.8201 | -0.013732 | -0.022888 | 122.0718 | 121.9391 | 121.962 | -0.26093 | 121.9803 | 121.9803 | 121.9894 | -0.16937
1782.25 | 122.287 | -121.9345 | 0.07782 | -0.0054933 | 0.072369 | -0.00058739 | 0.0024311 | 0.017024 | 0.0040077 | -0.0014442 | -0.011673 | 0.029625 | -0.012125 | 0.022238 | 0.0066095 | -0.0087606 | -0.022888 | 0.041199 | 0.041199 | 0.10986 | 0.16479 | -0.050354 | -0.17853 | 0.032043 | 0.07782 | -0.086975 | 0.07782 | 0.059509 | -0.009155 | -0.073242 | 121.8842 | 121.756 | 0.086975 | 121.9757 | 122.0444 | 0.28839 | -0.10071 | 121.9254 | 121.8613 | 0 | 121.9666 | 121.8475 | -0.013733 | -0.018311 | 122.0993 | 121.9116 | 121.9757 | -0.25635 | 122.0123 | 121.994 | 122.0123 | -0.15106
1783.9219 | 122.2412 | -121.9025 | 0.082397 | -0.0054933 | 0.068524 | 0.005394 | 0.0052081 | 0.01681 | -0.0043237 | -0.002085 | -0.0040437 | 0.022789 | -0.011271 | 0.019888 | 0.0012689 | -0.006838 | 0.027466 | 0.10529 | 0.11902 | 0.14648 | 0.14648 | 0.009155 | -0.12817 | 0.082397 | 0.16479 | 0.041199 | 0.032043 | 0.041199 | 0.013733 | -0.045776 | 121.9116 | 121.7743 | 0.064087 | 122.0078 | 122.049 | 0.27466 | -0.054931 | 121.9162 | 121.8567 | -0.050354 | 121.9849 | 121.9437 | 0.086975 | -0.041198 | 122.049 | 121.9299 | 122.0215 | -0.21057 | 121.9345 | 121.9437 | 122.0673 | -0.12817
1785.6719 | 122.2229 | -121.9254 | 0.09613 | -0.020752 | 0.072155 | 0.0011216 | 0.0067035 | 0.01446 | -0.0024011 | -0.0029394 | -0.011673 | 0.02813 | -0.01063 | 0.020316 | 0.0025507 | -0.010256 | 0.07782 | 0.14191 | 0.16479 | 0.17853 | 0.1236 | 0.009155 | -0.1236 | 0.09613 | 0.16937 | 0.032043 | 0.032043 | 0.022888 | 0.032043 | -0.054932 | 121.9345 | 121.8018 | 0.027466 | 122.0673 | 122.1039 | 0.30212 | -0.01831 | 121.9574 | 121.8704 | -0.064087 | 122.0215 | 121.9574 | 0.086975 | -0.073242 | 122.049 | 122.0032 | 122.0901 | -0.21973 | 121.9574 | 121.9482 | 122.0947 | -0.15106
1787.4219 | 122.1542 | -122.0032 | 0.11444 | -0.013122 | 0.068738 | 0.0011216 | 0.0037127 | 0.017237 | 0.0014441 | 0.00047844 | -0.011673 | 0.029412 | -0.011057 | 0.022025 | 0.0063959 | -0.011538 | 0.10529 | 0.10529 | 0.13733 | 0.17853 | 0.10986 | 0.022888 | -0.11902 | 0.11444 | 0.13733 | 0.013733 | 0.022888 | 0.036621 | 0.027466 | -0.045776 | 122.0261 | 121.8842 | -0.004578 | 122.1085 | 122.1817 | 0.29755 | -0.009155 | 122.0306 | 121.9574 | -0.091553 | 122.1176 | 122.0169 | 0.059509 | -0.07782 | 122.113 | 122.1085 | 122.1405 | -0.23346 | 122.0261 | 122.0398 | 122.1405 | -0.16022
1789.1094 | 122.2092 | -121.9528 | 0.11444 | -0.0054933 | 0.069592 | 0.0024032 | 0.0064899 | 0.014033 | 0.00016226 | -0.0022986 | -0.0040437 | 0.027916 | -0.0097755 | 0.021384 | 0.0036189 | -0.008547 | 0.032043 | 0.050354 | 0.059509 | 0.13733 | 0.16022 | -0.022888 | -0.15106 | -0.009155 | 0.064087 | -0.10071 | 0.064087 | 0.07782 | -0.004578 | -0.091553 | 121.9299 | 121.8018 | 0.045776 | 122.0032 | 122.0901 | 0.28839 | -0.082398 | 121.9482 | 121.8613 | -0.050354 | 121.9437 | 121.8521 | -0.009155 | -0.036621 | 122.113 | 121.9849 | 122.0123 | -0.2655 | 122.0169 | 122.0306 | 122.0169 | -0.20599
1790.875 | 122.1817 | -121.962 | 0.1236 | -0.020752 | 0.071301 | 0.00069421 | 0.0017901 | 0.015101 | 0.00058966 | -0.0029394 | -0.011673 | 0.027275 | -0.011057 | 0.02117 | 0.0078913 | -0.0083334 | 0.091553 | 0.09613 | 0.1236 | 0.16937 | 0.12817 | 0.018311 | -0.13275 | 0.11444 | 0.12817 | 0.004578 | 0.018311 | 0.018311 | 0.022888 | -0.059509 | 121.9803 | 121.8292 | 0.004578 | 122.0581 | 122.1313 | 0.30212 | -0.032043 | 121.9849 | 121.9025 | -0.10528 | 122.0764 | 121.9666 | 0.064087 | -0.10528 | 122.0901 | 122.0535 | 122.0856 | -0.25635 | 121.9803 | 121.9803 | 122.0901 | -0.1831
1792.6094 | 122.2366 | -121.962 | 0.086975 | -0.013122 | 0.074292 | 0.0024032 | 0.0073443 | 0.019373 | -0.0015465 | -0.0010168 | -0.0040437 | 0.027916 | -0.0076393 | 0.02117 | 0.0023371 | -0.0094016 | 0.064087 | 0.082397 | 0.10071 | 0.14648 | 0.15564 | -0.022888 | -0.13733 | 0.022888 | 0.09613 | -0.068665 | 0.07782 | 0.068665 | 0.009155 | -0.07782 | 121.9391 | 121.8246 | 0.068665 | 122.0444 | 122.1085 | 0.28381 | -0.022888 | 121.9711 | 121.8842 | -0.009155 | 121.9849 | 121.8933 | 0.009155 | -0.01831 | 122.1176 | 122.0261 | 122.0627 | -0.2243 | 122.0398 | 122.0306 | 122.0581 | -0.16479
1794.2969 | 122.1863 | -121.9894 | 0.10529 | 0.0021362 | 0.071728 | 5.3406e-05 | 0.0034991 | 0.017664 | 0.0031531 | 0.00047844 | -0.011673 | 0.026421 | -0.0078529 | 0.020102 | 0.0044733 | -0.011111 | 0.09613 | 0.10529 | 0.14191 | 0.1831 | 0.1236 | 0.022888 | -0.11444 | 0.11902 | 0.13275 | 0.009155 | 0.018311 | 0.032043 | 0.032043 | -0.032043 | 122.0123 | 121.875 | 0.01831 | 122.0947 | 122.1725 | 0.29755 | -0.009156 | 122.0215 | 121.9574 | -0.086975 | 122.1085 | 121.9986 | 0.041198 | -0.073243 | 122.113 | 122.0856 | 122.1313 | -0.21973 | 122.0078 | 122.0215 | 122.1222 | -0.13733
1796.0469 | 122.1542 | -121.9803 | 0.13275 | -0.013122 | 0.069806 | 0.0038986 | 0.0041401 | 0.012538 | -0.0017603 | -0.0012306 | 0.0035858 | 0.026848 | -0.011912 | 0.020316 | 0.0014825 | -0.0089742 | 0.050354 | 0.082397 | 0.086975 | 0.14191 | 0.14191 | 0.009155 | -0.13275 | 0.059509 | 0.10529 | -0.013733 | 0.022888 | 0.050354 | 0.032043 | -0.068665 | 121.9894 | 121.8475 | 0.009156 | 122.0627 | 122.1222 | 0.27466 | -0.082397 | 122.0123 | 121.9116 | -0.10986 | 122.0398 | 121.9666 | 0.054932 | -0.082397 | 122.1222 | 122.0306 | 122.0673 | -0.2655 | 122.0032 | 122.0306 | 122.0856 | -0.20142
1797.7344 | 122.2916 | -121.962 | 0.086975 | 0.0021362 | 0.071942 | 0.0017624 | 0.0071307 | 0.01681 | -0.0013329 | -0.0050758 | 0.0035858 | 0.024712 | -0.010416 | 0.02117 | 0.0014825 | -0.0087606 | 0.073242 | 0.10986 | 0.15106 | 0.15564 | 0.13275 | 0.004578 | -0.13275 | 0.10529 | 0.17853 | 0.027466 | 0.032043 | 0.041199 | 0.022888 | -0.045776 | 121.9666 | 121.8292 | 0.045776 | 122.0718 | 122.1176 | 0.28839 | -0.013733 | 121.9849 | 121.9162 | -0.054932 | 122.0673 | 121.9894 | 0.073242 | -0.045776 | 122.0947 | 122.0352 | 122.113 | -0.21973 | 121.994 | 122.0032 | 122.1405 | -0.13275
1799.4844 | 122.1634 | -121.9757 | 0.1236 | -0.0054933 | 0.071301 | 0.0034714 | 0.0015765 | 0.01446 | 0.0016577 | 0.00026484 | -0.011673 | 0.026634 | -0.012766 | 0.023093 | 0.0063959 | -0.010897 | 0.10986 | 0.11902 | 0.12817 | 0.16479 | 0.11444 | 0.018311 | -0.1236 | 0.10986 | 0.13733 | -0.004578 | 0.018311 | 0.045776 | 0.041199 | -0.041199 | 121.994 | 121.8521 | -0.009155 | 122.0947 | 122.1405 | 0.28839 | -0.013733 | 122.0169 | 121.9345 | -0.10528 | 122.0856 | 121.9711 | 0.036621 | -0.07782 | 122.0901 | 122.0856 | 122.1039 | -0.24719 | 121.994 | 122.0215 | 122.113 | -0.16479
1801.1562 | 122.3007 | -121.9574 | 0.07782 | -0.020752 | 0.067883 | 0.0011216 | 0.0058491 | 0.014033 | -0.0028283 | -0.0022986 | -0.011673 | 0.025566 | -0.011484 | 0.021384 | 0.0027643 | -0.0089742 | 0.10071 | 0.13275 | 0.14648 | 0.16479 | 0.13733 | 0.009155 | -0.12817 | 0.1236 | 0.18768 | 0.041199 | 0.041199 | 0.041199 | 0.045776 | -0.045776 | 121.9666 | 121.8292 | 0.059509 | 122.0901 | 122.1222 | 0.29297 | 0.022888 | 122.0032 | 121.9116 | -0.036621 | 122.081 | 121.9986 | 0.086975 | -0.036621 | 122.0947 | 122.0581 | 122.1039 | -0.20599 | 121.9986 | 121.9986 | 122.1451 | -0.1236
1802.9062 | 122.3099 | -121.9666 | 0.10071 | 0.0021362 | 0.073864 | -0.00058739 | 0.0067035 | 0.018519 | 0.0059303 | -0.00080316 | 0.0035858 | 0.028557 | -0.0099891 | 0.022238 | 0.0081049 | -0.010683 | 0.032043 | 0 | 0.036621 | 0.10986 | 0.17395 | -0.013733 | -0.16479 | 0.054932 | 0.068665 | -0.09613 | 0.091553 | 0.073242 | 0 | -0.064087 | 121.9528 | 121.8018 | 0.073242 | 121.9666 | 122.0764 | 0.27466 | -0.068665 | 121.9666 | 121.9025 | -0.009155 | 122.0215 | 121.8704 | -0.032043 | -0.027466 | 122.1405 | 121.9986 | 122.0032 | -0.2655 | 122.0581 | 122.0398 | 122.0352 | -0.1648
1804.5938 | 122.1863 | -121.9849 | 0.1236 | -0.020752 | 0.069592 | 0.00069421 | 0.0026447 | 0.014246 | 0.0016577 | 0.00047844 | 0.0035858 | 0.027275 | -0.01063 | 0.019034 | 0.0061823 | -0.0094016 | 0.09613 | 0.12817 | 0.11902 | 0.1831 | 0.12817 | 0.022888 | -0.11902 | 0.1236 | 0.13733 | 0.018311 | 0.018311 | 0.045776 | 0.027466 | -0.022888 | 122.0078 | 121.8658 | 0.004578 | 122.113 | 122.168 | 0.30212 | -0.027466 | 122.0123 | 121.962 | -0.10528 | 122.1085 | 122.0032 | 0.041199 | -0.07782 | 122.113 | 122.081 | 122.1039 | -0.24261 | 122.0032 | 122.0306 | 122.1222 | -0.14648
1806.3438 | 122.1451 | -122.0261 | 0.12817 | -0.0054933 | 0.070019 | 0.0017624 | 0.0060627 | 0.015315 | -0.00047854 | -0.0010168 | -0.019302 | 0.025566 | -0.0099891 | 0.02352 | 0.0038325 | -0.0083334 | 0.07782 | 0.10986 | 0.1236 | 0.15106 | 0.11444 | 0 | -0.11444 | 0.09613 | 0.11444 | -0.004578 | 0.041199 | 0.036621 | 0.022888 | -0.041199 | 122.0261 | 121.9116 | -0.013733 | 122.1359 | 122.1771 | 0.2655 | -0.050354 | 122.0489 | 121.9849 | -0.086975 | 122.1222 | 122.0215 | 0.036621 | -0.091553 | 122.1405 | 122.1039 | 122.1497 | -0.24262 | 122.0673 | 122.0627 | 122.1405 | -0.16937
1808.0938 | 122.168 | -122.0261 | 0.11444 | -0.020752 | 0.070874 | 0.0030442 | 0.0049945 | 0.017237 | -0.00026494 | -0.00080316 | -0.011673 | 0.027703 | -0.0089209 | 0.020956 | 0.0038325 | -0.0079062 | 0.068665 | 0.10071 | 0.1236 | 0.15106 | 0.11902 | 0.027466 | -0.11444 | 0.07782 | 0.10529 | -0.013733 | 0.027466 | 0.032043 | 0.041199 | -0.054932 | 122.0535 | 121.9116 | 0.004578 | 122.1268 | 122.1771 | 0.2655 | -0.045776 | 122.0673 | 121.9711 | -0.086975 | 122.1039 | 122.0123 | 0.041199 | -0.082398 | 122.1451 | 122.0947 | 122.1497 | -0.22888 | 122.0535 | 122.0581 | 122.1313 | -0.16937
1809.8438 | 122.2824 | -122.0078 | 0.10071 | -0.0054933 | 0.074719 | 5.3406e-05 | 0.0073443 | 0.015528 | 0.0057165 | 0.00026484 | -0.019302 | 0.030693 | -0.0093481 | 0.02352 | 0.0053279 | -0.011111 | 0.059509 | 0.064087 | 0.073242 | 0.12817 | 0.16479 | -0.013733 | -0.16022 | 0.07782 | 0.091553 | -0.073242 | 0.059509 | 0.054932 | 0.004578 | -0.07782 | 121.994 | 121.8475 | 0.064087 | 122.0718 | 122.1359 | 0.28839 | -0.041199 | 122.0123 | 121.9299 | -0.041199 | 122.0856 | 121.9345 | 0.004578 | -0.045776 | 122.1725 | 122.0673 | 122.081 | -0.26093 | 122.0673 | 122.0627 | 122.0993 | -0.17853
1811.5781 | 122.1909 | -122.0718 | 0.11444 | -0.013122 | 0.071515 | 0.0013352 | 0.0013629 | 0.014674 | 0.0029395 | 5.1244e-05 | -0.0040437 | 0.03048 | -0.0087073 | 0.022025 | 0.0066095 | -0.0094016 | -0.013733 | -0.036621 | -0.009155 | 0.073242 | 0.15564 | -0.027466 | -0.15106 | 0 | 0 | -0.15564 | 0.082397 | 0.082397 | 0.009155 | -0.091553 | 122.0444 | 121.9208 | 0.041199 | 122.0352 | 122.1451 | 0.2243 | -0.12817 | 122.081 | 121.9803 | -0.032044 | 122.0718 | 121.9162 | -0.064087 | -0.032044 | 122.2275 | 122.0581 | 122.0627 | -0.2655 | 122.1542 | 122.1542 | 122.0718 | -0.20599
1813.2656 | 122.319 | -121.9849 | 0.07782 | -0.0054933 | 0.068524 | 0.0026168 | 0.0067035 | 0.013606 | -0.0079553 | -0.002085 | -0.011673 | 0.024925 | -0.011912 | 0.017538 | 0.0014825 | -0.0072652 | 0.013733 | 0.10529 | 0.11902 | 0.14648 | 0.15106 | 0.009155 | -0.1236 | 0.07782 | 0.15106 | 0.036621 | 0.041199 | 0.036621 | 0.036621 | -0.050354 | 121.994 | 121.8613 | 0.073242 | 122.0901 | 122.1313 | 0.27008 | -0.064087 | 122.0215 | 121.9345 | -0.036621 | 122.0627 | 122.0215 | 0.086975 | -0.041199 | 122.1359 | 121.9986 | 122.1039 | -0.20142 | 122.0261 | 122.0215 | 122.1359 | -0.12817
1815.0156 | 122.3145 | -121.9757 | 0.10071 | -0.0054933 | 0.071301 | -0.00037379 | 0.0071307 | 0.014674 | -0.0034691 | -0.0046484 | -0.0040437 | 0.028343 | -0.01063 | 0.021384 | 0.0027643 | -0.0087606 | 0.09613 | 0.15106 | 0.17853 | 0.19226 | 0.12817 | 0.013733 | -0.1236 | 0.09613 | 0.1831 | 0.045776 | 0.022888 | 0.041199 | 0.050354 | -0.036621 | 121.9894 | 121.8521 | 0.027466 | 122.1268 | 122.168 | 0.31586 | -0.004578 | 122.0261 | 121.9391 | -0.07782 | 122.0718 | 122.0215 | 0.082397 | -0.059509 | 122.1039 | 122.0718 | 122.1542 | -0.2243 | 121.9986 | 122.0169 | 122.1588 | -0.13733
1816.7031 | 122.287 | -122.0352 | 0.086975 | -0.0054933 | 0.070233 | 0.0013352 | 0.0071307 | 0.014887 | 0.0010169 | -0.00037596 | 0.0035858 | 0.029625 | -0.0093481 | 0.021597 | 0.0042597 | -0.010897 | -0.004578 | 0.004578 | 0.018311 | 0.091553 | 0.18768 | -0.027466 | -0.18768 | -0.018311 | 0.041199 | -0.11444 | 0.082397 | 0.086975 | -0.027466 | -0.09613 | 122.0078 | 121.8475 | 0.10071 | 122.0398 | 122.1268 | 0.27924 | -0.091553 | 122.0078 | 121.9391 | -0.004578 | 122.0169 | 121.9208 | -0.018311 | 0 | 122.2229 | 122.0306 | 122.0535 | -0.27466 | 122.1176 | 122.1222 | 122.0764 | -0.1831
1818.4531 | 122.2137 | -122.049 | 0.10986 | -0.013122 | 0.068097 | 0.0032578 | 0.0037127 | 0.014674 | -0.0043237 | -0.003794 | -0.011673 | 0.02578 | -0.0099891 | 0.021811 | 0.0031915 | -0.0076926 | 0.054932 | 0.082397 | 0.086975 | 0.13275 | 0.13733 | 0.013733 | -0.11444 | 0.050354 | 0.09613 | -0.022888 | 0.036621 | 0.064087 | 0.032043 | -0.059509 | 122.0627 | 121.9345 | 0.027466 | 122.1313 | 122.1817 | 0.24719 | -0.054931 | 122.081 | 121.9894 | -0.073242 | 122.0993 | 122.0261 | 0.036621 | -0.045776 | 122.1863 | 122.1039 | 122.1359 | -0.2243 | 122.0856 | 122.113 | 122.1451 | -0.16937
1820.1406 | 122.2229 | -122.0673 | 0.12817 | -0.013122 | 0.074505 | 5.3406e-05 | 0.0011493 | 0.013606 | 0.0067847 | 0.00026484 | -0.019302 | 0.03048 | -0.01063 | 0.024161 | 0.0063959 | -0.011111 | 0.073242 | 0.041199 | 0.059509 | 0.1236 | 0.15106 | -0.022888 | -0.13733 | 0.041199 | 0.050354 | -0.10071 | 0.073242 | 0.064087 | 0 | -0.07782 | 122.0444 | 121.9299 | 0.022888 | 122.1085 | 122.1909 | 0.26093 | -0.054932 | 122.0673 | 121.9894 | -0.054932 | 122.1085 | 121.9666 | -0.022888 | -0.064087 | 122.2183 | 122.1405 | 122.1268 | -0.2655 | 122.1405 | 122.1313 | 122.1176 | -0.20599
1821.8906 | 122.3328 | -122.0032 | 0.082397 | -0.013122 | 0.068097 | 0.0026168 | 0.0060627 | 0.017024 | -0.0041101 | 0.00069204 | -0.0040437 | 0.024071 | -0.010843 | 0.021384 | 0.0027643 | -0.0087606 | 0.086975 | 0.15106 | 0.15564 | 0.1831 | 0.1236 | 0.018311 | -0.12817 | 0.086975 | 0.18768 | 0.036621 | 0.036621 | 0.045776 | 0.045776 | -0.064087 | 122.0215 | 121.875 | 0.041199 | 122.1542 | 122.1863 | 0.31128 | 0.004578 | 122.049 | 121.9391 | -0.045776 | 122.0901 | 122.0398 | 0.10071 | -0.036621 | 122.1268 | 122.0901 | 122.1588 | -0.21057 | 122.0398 | 122.049 | 122.1909 | -0.14648
1823.6406 | 122.2137 | -122.0947 | 0.11902 | -0.020752 | 0.072583 | 0.00069421 | 0.0017901 | 0.014887 | 0.0042213 | -0.00016236 | -0.0040437 | 0.028984 | -0.011271 | 0.02117 | 0.0070367 | -0.0094016 | -0.013733 | -0.064087 | -0.013733 | 0.07782 | 0.16937 | -0.018311 | -0.14648 | -0.004578 | -0.027466 | -0.13733 | 0.059509 | 0.086975 | 0 | -0.09613 | 122.0764 | 121.9482 | 0.050354 | 122.0306 | 122.1725 | 0.2243 | -0.13275 | 122.0947 | 121.9986 | -0.05951 | 122.0901 | 121.9574 | -0.041199 | -0.032044 | 122.2641 | 122.081 | 122.081 | -0.2655 | 122.1542 | 122.1817 | 122.0673 | -0.21515
1825.3906 | 122.2961 | -122.0352 | 0.09613 | -0.0054933 | 0.072583 | 0.0045394 | 0.0041401 | 0.013392 | -0.0034691 | -0.0029394 | -0.0040437 | 0.02578 | -0.010416 | 0.019034 | 0.0023371 | -0.0076926 | 0.068665 | 0.11902 | 0.14648 | 0.17853 | 0.14191 | 0.013733 | -0.11902 | 0.073242 | 0.16022 | -0.009155 | 0.032043 | 0.036621 | 0.032043 | -0.059509 | 122.049 | 121.9162 | 0.045777 | 122.1542 | 122.2137 | 0.29755 | -0.027465 | 122.0673 | 121.9757 | -0.064087 | 122.1085 | 122.0261 | 0.050354 | -0.059509 | 122.1771 | 122.1039 | 122.1817 | -0.21515 | 122.0673 | 122.0718 | 122.1954 | -0.15564
1827.125 | 122.2824 | -122.0627 | 0.10986 | -0.0054933 | 0.07536 | -0.0020828 | 0.0047809 | 0.016169 | 0.0050757 | -0.002085 | -0.0040437 | 0.030266 | -0.0089209 | 0.025443 | 0.0066095 | -0.0081198 | 0.068665 | 0.041199 | 0.068665 | 0.13275 | 0.16937 | -0.013733 | -0.14191 | 0.054932 | 0.073242 | -0.086975 | 0.068665 | 0.059509 | 0 | -0.07782 | 122.049 | 121.9208 | 0.05951 | 122.1039 | 122.1954 | 0.27466 | -0.041198 | 122.0627 | 121.9849 | -0.041198 | 122.1176 | 121.9757 | -0.009155 | -0.050354 | 122.2321 | 122.1313 | 122.1313 | -0.25177 | 122.1313 | 122.1222 | 122.1359 | -0.18768
1828.8594 | 122.2458 | -122.0764 | 0.10986 | -0.013122 | 0.069806 | 0.0041122 | 0.0032855 | 0.017237 | -0.0019739 | 0.00047844 | -0.011673 | 0.027062 | -0.0095619 | 0.021384 | 0.0070367 | -0.007479 | 0.082397 | 0.14191 | 0.1236 | 0.18768 | 0.11444 | 0.027466 | -0.12817 | 0.10986 | 0.13733 | 0.018311 | 0.022888 | 0.032043 | 0.022888 | -0.018311 | 122.1039 | 121.9482 | 0.004578 | 122.2183 | 122.2641 | 0.31586 | -0.027466 | 122.0993 | 122.0581 | -0.086975 | 122.1863 | 122.0947 | 0.036622 | -0.07782 | 122.1909 | 122.1588 | 122.2 | -0.23804 | 122.0993 | 122.1085 | 122.2137 | -0.12817
1830.5469 | 122.2458 | -122.0718 | 0.10529 | -0.0054933 | 0.071515 | -0.0018692 | 0.0037127 | 0.014887 | -0.0015465 | 5.1244e-05 | 0.0035858 | 0.026848 | -0.010843 | 0.020956 | 0.0051141 | -0.010256 | 0.09613 | 0.10986 | 0.12817 | 0.16937 | 0.11902 | 0.009155 | -0.10986 | 0.10986 | 0.13733 | -0.004578 | 0.027466 | 0.022888 | 0.018311 | -0.032043 | 122.081 | 121.962 | 0.013733 | 122.1817 | 122.2412 | 0.27924 | -0.009156 | 122.0901 | 122.0398 | -0.07782 | 122.1817 | 122.0673 | 0.027465 | -0.082398 | 122.1909 | 122.168 | 122.2 | -0.21515 | 122.0993 | 122.0947 | 122.2092 | -0.13733
1832.2812 | 122.2641 | -122.0856 | 0.10529 | -0.0054933 | 0.073651 | 0.0013352 | 0.0054217 | 0.015315 | 0.0033667 | -0.00016236 | -0.011673 | 0.03048 | -0.0082801 | 0.020743 | 0.0053279 | -0.01047 | 0.059509 | 0.059509 | 0.045776 | 0.13275 | 0.16022 | -0.009155 | -0.15106 | 0.036621 | 0.064087 | -0.091553 | 0.064087 | 0.059509 | 0 | -0.064087 | 122.0764 | 121.9345 | 0.054931 | 122.1451 | 122.2183 | 0.28381 | -0.045777 | 122.0856 | 122.0215 | -0.041199 | 122.1222 | 121.994 | -0.027466 | -0.045777 | 122.2458 | 122.1451 | 122.1313 | -0.25635 | 122.1497 | 122.1451 | 122.1497 | -0.16937
1834.0312 | 122.2961 | -122.0581 | 0.10986 | -0.0054933 | 0.071087 | 0.0011216 | 0.0034991 | 0.013819 | 0.0016577 | 5.1244e-05 | -0.0040437 | 0.027275 | -0.012339 | 0.022238 | 0.0057551 | -0.0098288 | 0.013733 | 0.032043 | 0.068665 | 0.12817 | 0.15106 | 0.004578 | -0.11902 | 0.09613 | 0.10986 | -0.018311 | 0.032043 | 0.032043 | 0.022888 | -0.050354 | 122.0627 | 121.9391 | 0.041199 | 122.0901 | 122.1863 | 0.24719 | -0.09613 | 122.081 | 122.0078 | -0.07782 | 122.1542 | 122.0398 | 0.032043 | -0.07782 | 122.2092 | 122.0718 | 122.1268 | -0.22888 | 122.0901 | 122.0901 | 122.168 | -0.16022
1835.7188 | 122.2321 | -122.0993 | 0.15106 | -0.013122 | 0.074078 | 0.003685 | 0.0047809 | 0.015955 | 0.0027259 | 0.00047844 | -0.0040437 | 0.028984 | -0.010416 | 0.023306 | 0.0055415 | -0.0066244 | -0.004578 | -0.013733 | 0.004578 | 0.10529 | 0.15564 | 0 | -0.15564 | -0.018311 | -0.004578 | -0.15564 | 0.07782 | 0.059509 | -0.018311 | -0.068665 | 122.0993 | 121.9437 | 0.004578 | 122.0856 | 122.2046 | 0.26093 | -0.15564 | 122.081 | 122.0306 | -0.073242 | 122.081 | 121.9437 | -0.086975 | -0.091553 | 122.2549 | 122.0947 | 122.1039 | -0.3067 | 122.1771 | 122.1588 | 122.0947 | -0.21973
1837.4688 | 122.2458 | -122.0993 | 0.1236 | -0.0054933 | 0.073651 | -0.00058739 | 0.0045673 | 0.015101 | 0.0027259 | 0.00047844 | -0.011673 | 0.03048 | -0.0091345 | 0.022238 | 0.0074641 | -0.0089742 | -0.022888 | -0.013733 | 0.004578 | 0.082397 | 0.16022 | -0.013733 | -0.15106 | -0.022888 | -0.018311 | -0.15106 | 0.082397 | 0.073242 | 0.004578 | -0.07782 | 122.0856 | 121.9482 | 0.036621 | 122.0856 | 122.1817 | 0.23346 | -0.14648 | 122.1039 | 122.0215 | -0.041199 | 122.0764 | 121.9482 | -0.073242 | -0.050354 | 122.2595 | 122.0764 | 122.1039 | -0.27466 | 122.1817 | 122.1725 | 122.081 | -0.20142
1839.1562 | 122.2412 | -122.0947 | 0.13275 | -0.0054933 | 0.07066 | 0.003685 | 0.0075581 | 0.014674 | -0.0030419 | 5.1244e-05 | 0.0035858 | 0.024498 | -0.0084937 | 0.020316 | 0.0023371 | -0.0072652 | 0.050354 | 0.13275 | 0.13733 | 0.16937 | 0.12817 | 0.013733 | -0.10986 | 0.073242 | 0.11902 | 0.013733 | 0.027466 | 0.036621 | 0.032043 | -0.041199 | 122.1085 | 121.9849 | -0.004577 | 122.2275 | 122.2641 | 0.27924 | -0.082397 | 122.1268 | 122.0535 | -0.10529 | 122.168 | 122.1085 | 0.054932 | -0.09613 | 122.2229 | 122.1451 | 122.2321 | -0.24261 | 122.1222 | 122.1313 | 122.2137 | -0.17395
1840.9219 | 122.3465 | -122.0718 | 0.086975 | -0.013122 | 0.076428 | 0.0015488 | 0.0081989 | 0.013606 | -0.0032555 | -0.0040076 | -0.011673 | 0.028557 | -0.0087073 | 0.021811 | 0.00020086 | -0.0087606 | -0.041199 | -0.018311 | 0.022888 | 0.086975 | 0.16479 | -0.018311 | -0.15106 | -0.032043 | 0.027466 | -0.09613 | 0.082397 | 0.09613 | -0.013733 | -0.082397 | 122.0535 | 121.9208 | 0.07782 | 122.0535 | 122.1588 | 0.23804 | -0.12817 | 122.0581 | 121.9894 | -0.004578 | 122.0398 | 121.9757 | -0.013733 | 0.009155 | 122.2366 | 122.0306 | 122.0947 | -0.23804 | 122.1542 | 122.168 | 122.0993 | -0.16937
1842.6562 | 122.3099 | -122.0993 | 0.10986 | -0.013122 | 0.07301 | 0.0011216 | 0.0017901 | 0.015742 | 0.00080326 | -0.00058956 | -0.019302 | 0.027275 | -0.0089209 | 0.021811 | 0.0068231 | -0.010256 | 0.036621 | 0.059509 | 0.059509 | 0.13275 | 0.14648 | 0.013733 | -0.13275 | 0.091553 | 0.10529 | 0 | 0.041199 | 0.032043 | 0.036621 | -0.054932 | 122.113 | 121.9666 | 0.036621 | 122.1588 | 122.2321 | 0.2655 | -0.073242 | 122.1359 | 122.0444 | -0.068664 | 122.1909 | 122.0993 | 0.054932 | -0.07782 | 122.2458 | 122.1359 | 122.1588 | -0.24261 | 122.1405 | 122.1313 | 122.2046 | -0.16479
1844.4062 | 122.374 | -122.081 | 0.086975 | -0.0054933 | 0.074933 | 0.0013352 | 0.0081989 | 0.015955 | -0.00047854 | -0.003794 | 0.0035858 | 0.029625 | -0.0076393 | 0.020316 | 0.0021235 | -0.008547 | -0.004578 | -0.018311 | -0.004578 | 0.082397 | 0.17853 | -0.032043 | -0.16022 | -0.018311 | 0.013733 | -0.1236 | 0.082397 | 0.073242 | -0.009155 | -0.10071 | 122.049 | 121.9208 | 0.091553 | 122.0627 | 122.1634 | 0.24261 | -0.091553 | 122.0718 | 121.9803 | -0.004578 | 122.0627 | 121.9574 | -0.022888 | -0.013733 | 122.2595 | 122.0764 | 122.0764 | -0.24719 | 122.1634 | 122.1542 | 122.0947 | -0.18768
1846.0781 | 122.2321 | -122.1085 | 0.13275 | -0.013122 | 0.066601 | 0.00069421 | -0.00098693 | 0.017878 | -0.0036829 | 0.00047844 | -0.0040437 | 0.025353 | -0.01063 | 0.021384 | 0.0053279 | -0.006838 | 0.064087 | 0.09613 | 0.11444 | 0.16022 | 0.13275 | 0.009155 | -0.1236 | 0.068665 | 0.10529 | -0.013733 | 0.041199 | 0.032043 | 0.036621 | -0.059509 | 122.1176 | 121.9849 | 0 | 122.2046 | 122.2687 | 0.28381 | -0.068664 | 122.1451 | 122.0489 | -0.091552 | 122.1771 | 122.0947 | 0.045776 | -0.10071 | 122.2412 | 122.1725 | 122.2229 | -0.25635 | 122.1497 | 122.1405 | 122.2137 | -0.19226
1847.8125 | 122.2687 | -122.1085 | 0.11902 | -0.013122 | 0.067456 | 0.0013352 | 0.0067035 | 0.014887 | -0.0043237 | -0.0010168 | -0.0040437 | 0.026207 | -0.011484 | 0.022025 | 0.0012689 | -0.0072652 | 0.054932 | 0.082397 | 0.11444 | 0.12817 | 0.12817 | 0.013733 | -0.10529 | 0.059509 | 0.082397 | -0.022888 | 0.036621 | 0.045776 | 0.036621 | -0.041199 | 122.1222 | 122.0032 | 0.009155 | 122.1909 | 122.2366 | 0.23346 | -0.064087 | 122.1451 | 122.0673 | -0.082398 | 122.168 | 122.0856 | 0.018311 | -0.073243 | 122.2366 | 122.1634 | 122.2229 | -0.22431 | 122.1451 | 122.1542 | 122.1909 | -0.16022
1849.5625 | 122.3785 | -122.0627 | 0.09613 | -0.013122 | 0.07066 | 0.0015488 | 0.0069171 | 0.017024 | 0.0031531 | 0.0011194 | -0.011673 | 0.030693 | -0.010203 | 0.022665 | 0.0066095 | -0.011965 | 0.054932 | 0.032043 | 0.045776 | 0.11902 | 0.18768 | -0.018311 | -0.1236 | 0.050354 | 0.07782 | -0.07782 | 0.068665 | 0.059509 | 0.004578 | -0.068665 | 122.0444 | 121.9391 | 0.091553 | 122.0947 | 122.1817 | 0.24261 | -0.041198 | 122.0673 | 121.994 | -0.027465 | 122.113 | 121.9849 | -0.009155 | -0.036621 | 122.2504 | 122.1176 | 122.1085 | -0.21973 | 122.1313 | 122.1222 | 122.1405 | -0.16479
1851.25 | 122.2824 | -122.113 | 0.09613 | -0.013122 | 0.073864 | 0.0015488 | 0.0041401 | 0.016169 | 0.0035803 | 0.00026484 | -0.0040437 | 0.029412 | -0.011912 | 0.02117 | 0.0083185 | -0.0098288 | 0.032043 | 0.032043 | 0.041199 | 0.10986 | 0.17395 | -0.013733 | -0.16022 | 0.032043 | 0.041199 | -0.11444 | 0.073242 | 0.068665 | 0 | -0.068665 | 122.0993 | 121.9528 | 0.07782 | 122.1451 | 122.2229 | 0.27008 | -0.064087 | 122.113 | 122.0444 | -0.022888 | 122.1451 | 121.9986 | -0.045776 | -0.027465 | 122.287 | 122.1451 | 122.1542 | -0.25635 | 122.1863 | 122.1817 | 122.1542 | -0.16479
1852.9844 | 122.2687 | -122.1039 | 0.11444 | -0.013122 | 0.077282 | 0.00048061 | 0.0062763 | 0.014246 | 0.0029395 | -0.0012306 | -0.011673 | 0.028557 | -0.0074255 | 0.022879 | 0.0016963 | -0.0089742 | -0.027466 | -0.064087 | -0.009155 | 0.07782 | 0.16479 | -0.018311 | -0.16479 | -0.004578 | -0.004578 | -0.13733 | 0.068665 | 0.073242 | -0.004578 | -0.07782 | 122.0856 | 121.9391 | 0.050354 | 122.0398 | 122.1817 | 0.24261 | -0.14191 | 122.0993 | 122.0261 | -0.045776 | 122.0993 | 121.9666 | -0.059509 | -0.041199 | 122.2687 | 122.0764 | 122.0947 | -0.27924 | 122.1725 | 122.1771 | 122.0993 | -0.19226
1854.7344 | 122.3602 | -122.0764 | 0.10529 | -0.013122 | 0.073437 | 0.0017624 | 0.0073443 | 0.018092 | -0.0053919 | -0.002085 | -0.011673 | 0.026421 | -0.0095619 | 0.020102 | -0.00022634 | -0.0066244 | 0.068665 | 0.13275 | 0.15106 | 0.19226 | 0.11902 | 0 | -0.12817 | 0.073242 | 0.17853 | 0.009155 | 0.032043 | 0.032043 | 0.036621 | -0.032043 | 122.0764 | 121.9482 | 0.013733 | 122.2092 | 122.2687 | 0.32044 | -0.036621 | 122.113 | 122.0444 | -0.073243 | 122.1497 | 122.0856 | 0.041198 | -0.073243 | 122.1954 | 122.1451 | 122.2275 | -0.23346 | 122.1085 | 122.1085 | 122.2549 | -0.13733
1856.4688 | 122.3694 | -122.1313 | 0.10529 | -0.013122 | 0.072583 | 0.0015488 | 0.0073443 | 0.017664 | -0.0024011 | -0.0010168 | -0.011673 | 0.028984 | -0.0087073 | 0.024161 | 0.0036189 | -0.0079062 | -0.027466 | 0.009155 | 0.027466 | 0.082397 | 0.15106 | -0.027466 | -0.14648 | -0.027466 | 0.018311 | -0.11444 | 0.07782 | 0.073242 | -0.013733 | -0.086975 | 122.1039 | 121.9849 | 0.045776 | 122.1405 | 122.2137 | 0.22888 | -0.13275 | 122.1176 | 122.0444 | -0.027466 | 122.1039 | 122.0169 | -0.027466 | -0.032044 | 122.2824 | 122.1039 | 122.1588 | -0.25177 | 122.2092 | 122.2046 | 122.1497 | -0.19226
1858.1406 | 122.3328 | -122.1176 | 0.11444 | -0.0054933 | 0.072583 | 0.0024032 | 0.0049945 | 0.014246 | 0.0012305 | -0.0012306 | 0.0035858 | 0.028343 | -0.0093481 | 0.02117 | 0.0049005 | -0.0098288 | 0.009155 | -0.018311 | 0.009155 | 0.07782 | 0.17853 | -0.018311 | -0.13275 | 0.018311 | 0.013733 | -0.082397 | 0.059509 | 0.064087 | 0.032043 | -0.068665 | 122.0993 | 121.9849 | 0.064087 | 122.0993 | 122.1954 | 0.21057 | -0.10529 | 122.1497 | 122.049 | -0.054932 | 122.1359 | 122.0352 | -0.013732 | -0.050354 | 122.2961 | 122.1268 | 122.1268 | -0.24719 | 122.1771 | 122.1817 | 122.1313 | -0.18311
1859.8906 | 122.3831 | -122.0947 | 0.10529 | -0.0054933 | 0.071515 | 0.00069421 | 0.0067035 | 0.015742 | -0.0017603 | -0.0027258 | -0.011673 | 0.028343 | -0.0093481 | 0.022238 | 0.0029779 | -0.0094016 | -0.027466 | -0.004578 | 0.013733 | 0.086975 | 0.1831 | -0.018311 | -0.14648 | -0.032043 | 0.050354 | -0.12817 | 0.086975 | 0.082397 | -0.018311 | -0.10529 | 122.0764 | 121.9482 | 0.077819 | 122.0901 | 122.1817 | 0.23346 | -0.13275 | 122.0764 | 121.9894 | -0.018311 | 122.0627 | 121.9666 | -0.022888 | -0.022889 | 122.2778 | 122.0673 | 122.1085 | -0.25177 | 122.1817 | 122.1771 | 122.1451 | -0.21057
1861.6406 | 122.3145 | -122.1359 | 0.10529 | 0.0021362 | 0.072796 | 0.005394 | 0.0032855 | 0.016596 | 0.0033667 | -0.002085 | -0.0040437 | 0.028343 | -0.011484 | 0.020529 | 0.0059687 | -0.010042 | -0.013733 | -0.018311 | 0 | 0.082397 | 0.17853 | -0.004578 | -0.16479 | -0.004578 | -0.018311 | -0.10986 | 0.068665 | 0.073242 | -0.013733 | -0.073242 | 122.1313 | 121.9711 | 0.073242 | 122.1176 | 122.2183 | 0.24719 | -0.11902 | 122.1222 | 122.0627 | -0.036621 | 122.1313 | 122.0261 | -0.036621 | -0.032044 | 122.3145 | 122.1222 | 122.1359 | -0.27008 | 122.2046 | 122.2092 | 122.1176 | -0.17853
1863.3281 | 122.4152 | -122.0901 | 0.10071 | -0.0054933 | 0.071515 | 0.0017624 | 0.0054217 | 0.014674 | -0.0013329 | -0.00080316 | -0.0040437 | 0.027489 | -0.0084937 | 0.021384 | 0.00084166 | -0.0087606 | -0.022888 | -0.009155 | 0.009155 | 0.086975 | 0.16937 | -0.032043 | -0.15106 | -0.027466 | 0.032043 | -0.11444 | 0.07782 | 0.086975 | -0.009155 | -0.073242 | 122.0581 | 121.9391 | 0.068665 | 122.081 | 122.1771 | 0.23804 | -0.1236 | 122.081 | 122.0169 | -0.022888 | 122.0627 | 121.9757 | -0.041199 | -0.013733 | 122.2595 | 122.0673 | 122.0993 | -0.25177 | 122.168 | 122.1771 | 122.1222 | -0.17395
1865.0781 | 122.4014 | -122.1039 | 0.07782 | -0.0054933 | 0.072369 | 0.0017624 | 0.0049945 | 0.015101 | 0.0046485 | 0.00069204 | -0.011673 | 0.030266 | -0.010203 | 0.02117 | 0.0049005 | -0.011324 | 0.059509 | 0.041199 | 0.064087 | 0.12817 | 0.16022 | -0.013733 | -0.15564 | 0.054932 | 0.086975 | -0.064087 | 0.064087 | 0.073242 | 0.013733 | -0.082397 | 122.0901 | 121.9482 | 0.082397 | 122.1451 | 122.2321 | 0.28381 | -0.018311 | 122.1176 | 122.0215 | -0.013733 | 122.1588 | 122.0398 | 0.01831 | -0.004578 | 122.2641 | 122.1634 | 122.168 | -0.23346 | 122.168 | 122.1771 | 122.1909 | -0.16022
1866.8281 | 122.3557 | -122.1268 | 0.10986 | -0.0054933 | 0.07301 | -0.00037379 | 0.0032855 | 0.013606 | 0.00037606 | 0.00047844 | -0.011673 | 0.028343 | -0.0095619 | 0.022025 | 0.0057551 | -0.0081198 | -0.013733 | -0.013733 | 0.027466 | 0.09613 | 0.15564 | 0.009155 | -0.14648 | 0.036621 | 0.041199 | -0.073242 | 0.068665 | 0.054932 | 0.032043 | -0.064087 | 122.1359 | 121.9803 | 0.045777 | 122.113 | 122.2229 | 0.24261 | -0.1236 | 122.1588 | 122.0627 | -0.041198 | 122.1634 | 122.0535 | -0.009155 | -0.054931 | 122.2824 | 122.113 | 122.1542 | -0.25635 | 122.1954 | 122.1817 | 122.168 | -0.17395
1868.5 | 122.4014 | -122.0901 | 0.11902 | 0.0021362 | 0.073651 | 0.00090781 | 0.0067035 | 0.016169 | -0.0034691 | -0.0012306 | -0.019302 | 0.025566 | -0.011271 | 0.020743 | 0.00041446 | -0.0083334 | -0.041199 | -0.009155 | 0.009155 | 0.082397 | 0.1831 | -0.027466 | -0.16479 | -0.036621 | 0.041199 | -0.10986 | 0.07782 | 0.09613 | -0.004578 | -0.07782 | 122.0627 | 121.9254 | 0.064086 | 122.081 | 122.1725 | 0.24719 | -0.16022 | 122.0856 | 122.0123 | -0.041199 | 122.0535 | 121.9803 | -0.032043 | -0.022889 | 122.2733 | 122.0489 | 122.0993 | -0.28381 | 122.168 | 122.1863 | 122.1313 | -0.19684
1870.25 | 122.2916 | -122.1588 | 0.13733 | 0.0021362 | 0.074719 | -0.001442 | 0.0030719 | 0.013178 | 0.0042213 | 0.001333 | 0.0035858 | 0.029412 | -0.0076393 | 0.025015 | 0.0053279 | -0.0094016 | -0.013733 | -0.004578 | 0.013733 | 0.091553 | 0.15564 | -0.009155 | -0.14191 | 0.004578 | 0.009155 | -0.14191 | 0.064087 | 0.082397 | 0.004578 | -0.064087 | 122.1497 | 122.0169 | 0.018311 | 122.1542 | 122.2504 | 0.23346 | -0.15106 | 122.1634 | 122.0947 | -0.073242 | 122.1634 | 122.0169 | -0.07782 | -0.054932 | 122.3145 | 122.1451 | 122.1725 | -0.27924 | 122.2229 | 122.2412 | 122.168 | -0.20142
1871.9844 | 122.3099 | -122.1588 | 0.11902 | -0.013122 | 0.077282 | 0.00048061 | 0.0054217 | 0.015955 | 0.0031531 | -0.0018714 | -0.011673 | 0.029412 | -0.0078529 | 0.022879 | 0.0046869 | -0.008547 | 0.027466 | 0.041199 | 0.068665 | 0.1236 | 0.15564 | -0.004578 | -0.13275 | 0.009155 | 0.059509 | -0.10529 | 0.054932 | 0.073242 | 0.004578 | -0.054932 | 122.1542 | 122.0261 | 0.036621 | 122.2 | 122.2824 | 0.25635 | -0.091553 | 122.1634 | 122.1039 | -0.064087 | 122.168 | 122.0535 | -0.050354 | -0.045777 | 122.3145 | 122.1863 | 122.2275 | -0.25177 | 122.2137 | 122.2321 | 122.2183 | -0.17395
1873.7344 | 122.3877 | -122.1222 | 0.11444 | 0.0021362 | 0.074292 | 0.00048061 | 0.0096943 | 0.014674 | -0.0043237 | -0.0022986 | -0.011673 | 0.025353 | -0.0080665 | 0.021811 | -1.2744e-05 | -0.007479 | -0.013733 | 0.064087 | 0.082397 | 0.14191 | 0.15106 | -0.022888 | -0.14191 | -0.013733 | 0.073242 | -0.086975 | 0.073242 | 0.068665 | -0.004578 | -0.082397 | 122.0993 | 121.9803 | 0.036621 | 122.1863 | 122.2641 | 0.28381 | -0.12817 | 122.1176 | 122.0398 | -0.041199 | 122.1085 | 122.0352 | -0.004578 | -0.045776 | 122.2733 | 122.1085 | 122.2046 | -0.25635 | 122.1954 | 122.1909 | 122.1954 | -0.19684
1875.4219 | 122.4335 | -122.1222 | 0.091553 | -0.013122 | 0.074933 | 0.0032578 | 0.0071307 | 0.014246 | -0.00026494 | -0.0027258 | 0.0035858 | 0.027916 | -0.0076393 | 0.022238 | 0.0031915 | -0.010042 | -0.041199 | -0.004578 | 0.013733 | 0.086975 | 0.17853 | -0.022888 | -0.15106 | -0.032043 | 0.027466 | -0.10529 | 0.086975 | 0.082397 | -0.018311 | -0.086975 | 122.0993 | 121.9711 | 0.086975 | 122.1176 | 122.2092 | 0.23804 | -0.13275 | 122.1039 | 122.0352 | -0.004578 | 122.0901 | 122.0169 | -0.018311 | -0.009156 | 122.3007 | 122.081 | 122.1359 | -0.24261 | 122.2092 | 122.2046 | 122.1497 | -0.17853
1877.1562 | 122.4472 | -122.1222 | 0.091553 | -0.013122 | 0.075573 | -0.001442 | 0.0064899 | 0.015315 | 0.0022987 | 0.00090584 | -0.026932 | 0.029839 | -0.0080665 | 0.022665 | 0.0031915 | -0.0096152 | -0.013733 | 0 | 0.032043 | 0.10529 | 0.17395 | -0.004578 | -0.15564 | 0.004578 | 0.068665 | -0.082397 | 0.068665 | 0.086975 | 0 | -0.073242 | 122.1176 | 121.9666 | 0.082397 | 122.1222 | 122.2275 | 0.26093 | -0.10529 | 122.1222 | 122.049 | -0.022888 | 122.1268 | 122.0398 | -0.009155 | -0.004578 | 122.2961 | 122.1085 | 122.1542 | -0.24719 | 122.1909 | 122.2092 | 122.1909 | -0.16479
1878.9062 | 122.3053 | -122.1542 | 0.14191 | -0.0054933 | 0.071515 | 0.00069421 | 0.0024311 | 0.016383 | -0.0036829 | -0.0014442 | -0.011673 | 0.023644 | -0.0099891 | 0.019247 | 0.0027643 | -0.0070516 | 0.068665 | 0.13275 | 0.14648 | 0.17853 | 0.12817 | 0.027466 | -0.091553 | 0.091553 | 0.13733 | 0.013733 | 0.013733 | 0.041199 | 0.027466 | -0.036621 | 122.1817 | 122.0627 | -0.013733 | 122.287 | 122.3328 | 0.27008 | -0.073242 | 122.1817 | 122.1176 | -0.12817 | 122.2458 | 122.168 | 0.050354 | -0.10071 | 122.2824 | 122.2229 | 122.3007 | -0.23346 | 122.168 | 122.1954 | 122.2916 | -0.17853
1880.5938 | 122.3145 | -122.168 | 0.10986 | 0.0021362 | 0.072583 | 0.00048061 | 0.0034991 | 0.016596 | 0.0046485 | 0.00069204 | -0.019302 | 0.030266 | -0.0084937 | 0.022452 | 0.0059687 | -0.011538 | 0.009155 | 0.022888 | 0.050354 | 0.10071 | 0.15564 | -0.004578 | -0.13275 | 0 | 0 | -0.13275 | 0.07782 | 0.082397 | 0.004578 | -0.073242 | 122.1634 | 122.0352 | 0.045777 | 122.1909 | 122.2687 | 0.23346 | -0.10071 | 122.1725 | 122.0947 | -0.032043 | 122.168 | 122.0352 | -0.059509 | -0.027466 | 122.3236 | 122.1771 | 122.2183 | -0.24261 | 122.2458 | 122.2504 | 122.168 | -0.18311
1882.3281 | 122.4106 | -122.1497 | 0.10071 | -0.013122 | 0.071301 | 0.00069421 | 0.0069171 | 0.018733 | -0.0034691 | -0.002085 | -0.011673 | 0.02813 | -0.011912 | 0.019675 | 0.0012689 | -0.0079062 | -0.027466 | -0.004578 | 0.009155 | 0.082397 | 0.16937 | -0.013733 | -0.13733 | -0.045776 | 0.036621 | -0.11444 | 0.09613 | 0.086975 | -0.013733 | -0.073242 | 122.1359 | 122.0123 | 0.068665 | 122.1451 | 122.2321 | 0.21973 | -0.12817 | 122.1359 | 122.0764 | -0.004578 | 122.1039 | 122.0352 | -0.041199 | -0.013733 | 122.319 | 122.1222 | 122.1588 | -0.23804 | 122.2458 | 122.2366 | 122.1863 | -0.17395
1884.0781 | 122.3877 | -122.1176 | 0.09613 | -0.0054933 | 0.072796 | 0.0030442 | 0.0062763 | 0.013819 | -0.0034691 | -0.0016578 | -0.011673 | 0.026634 | -0.011057 | 0.023306 | 0.00084166 | -0.0079062 | 0.004578 | 0.027466 | 0.059509 | 0.11444 | 0.14191 | -0.018311 | -0.1236 | -0.013733 | 0.054932 | -0.091553 | 0.086975 | 0.10529 | -0.013733 | -0.073242 | 122.0993 | 121.994 | 0.045777 | 122.1451 | 122.2321 | 0.23804 | -0.091552 | 122.1039 | 122.0444 | -0.009155 | 122.1039 | 122.0261 | -0.018311 | 0.009156 | 122.2595 | 122.1222 | 122.1771 | -0.21973 | 122.2046 | 122.2229 | 122.1725 | -0.16937
1885.8594 | 122.4609 | -122.1039 | 0.10071 | -0.0054933 | 0.069806 | 0.0032578 | 0.0047809 | 0.015528 | -0.0032555 | -0.0016578 | -0.0040437 | 0.024071 | -0.011057 | 0.020956 | 0.00041446 | -0.0087606 | 0.082397 | 0.13275 | 0.15564 | 0.17853 | 0.13733 | 0.018311 | -0.11444 | 0.09613 | 0.18768 | 0.064087 | 0.022888 | 0.050354 | 0.036621 | -0.036621 | 122.1222 | 121.9894 | 0.036621 | 122.2366 | 122.2824 | 0.29297 | -0.018311 | 122.1405 | 122.0673 | -0.07782 | 122.2 | 122.168 | 0.10071 | -0.050354 | 122.2412 | 122.1863 | 122.2595 | -0.21515 | 122.1268 | 122.1542 | 122.2916 | -0.13733
1887.5469 | 122.3969 | -122.1588 | 0.091553 | -0.013122 | 0.070019 | 0.0015488 | 0.0049945 | 0.018305 | -0.0021875 | -0.0048622 | -0.0040437 | 0.028557 | -0.0082801 | 0.023093 | 0.0025507 | -0.0091878 | 0.068665 | 0.091553 | 0.11444 | 0.15106 | 0.14648 | 0.013733 | -0.1236 | 0.018311 | 0.091553 | -0.064087 | 0.068665 | 0.059509 | 0.004578 | -0.064087 | 122.1725 | 122.0352 | 0.054931 | 122.2504 | 122.3099 | 0.27466 | -0.022888 | 122.1634 | 122.0947 | -0.022888 | 122.1771 | 122.0947 | 0 | -0.032044 | 122.3053 | 122.2275 | 122.2733 | -0.21515 | 122.2275 | 122.2183 | 122.2504 | -0.15564
1889.2969 | 122.4518 | -122.1405 | 0.07782 | -0.013122 | 0.070019 | 0.0013352 | 0.0030719 | 0.013606 | -0.0051781 | -0.0027258 | 0.0035858 | 0.024712 | -0.0093481 | 0.022879 | 0.0010553 | -0.010042 | 0.10071 | 0.12817 | 0.14191 | 0.17395 | 0.13275 | 0.013733 | -0.11444 | 0.07782 | 0.16937 | 0.041199 | 0.041199 | 0.036621 | 0.032043 | -0.041199 | 122.1542 | 122.0261 | 0.054931 | 122.2687 | 122.3145 | 0.28839 | 0.022888 | 122.1725 | 122.0993 | -0.036621 | 122.2183 | 122.1817 | 0.082398 | -0.041199 | 122.2733 | 122.2412 | 122.2824 | -0.19226 | 122.1817 | 122.1771 | 122.3099 | -0.11902
1891.0469 | 122.3419 | -122.168 | 0.10986 | -0.020752 | 0.067669 | 0.0030442 | -0.00055973 | 0.011897 | 0.00080326 | -0.0035804 | 0.0035858 | 0.027703 | -0.013407 | 0.019247 | 0.0070367 | -0.0072652 | 0.091553 | 0.11444 | 0.14648 | 0.17395 | 0.11902 | 0.032043 | -0.11444 | 0.10529 | 0.12817 | 0.009155 | 0.022888 | 0.036621 | 0.004578 | -0.032043 | 122.2 | 122.0535 | 0.009156 | 122.2824 | 122.3419 | 0.28839 | -0.01831 | 122.1725 | 122.1359 | -0.086975 | 122.2733 | 122.1771 | 0.041198 | -0.073242 | 122.287 | 122.2595 | 122.3145 | -0.2243 | 122.1909 | 122.2046 | 122.2961 | -0.14191
1892.7188 | 122.4243 | -122.1542 | 0.10986 | -0.013122 | 0.069592 | 0.0015488 | 0.0054217 | 0.015955 | -0.0041101 | -0.002085 | -0.019302 | 0.02578 | -0.011484 | 0.020529 | 0.0016963 | -0.0087606 | 0.022888 | 0.041199 | 0.09613 | 0.13733 | 0.13275 | 0.004578 | -0.12817 | 0.059509 | 0.082397 | -0.022888 | 0.050354 | 0.068665 | 0.022888 | -0.050354 | 122.1588 | 122.0261 | 0.022888 | 122.1954 | 122.2916 | 0.2655 | -0.086975 | 122.1771 | 122.1039 | -0.059509 | 122.2137 | 122.1313 | 0.027466 | -0.041198 | 122.287 | 122.1771 | 122.2504 | -0.23804 | 122.2046 | 122.2229 | 122.2366 | -0.16022
1894.4531 | 122.4609 | -122.1634 | 0.091553 | 0.0021362 | 0.07536 | -0.00058739 | 0.0041401 | 0.013606 | 0.0061439 | 5.1244e-05 | -0.0040437 | 0.030266 | -0.0084937 | 0.023093 | 0.0061823 | -0.012179 | 0.068665 | 0.032043 | 0.054932 | 0.12817 | 0.16937 | -0.009155 | -0.15106 | 0.064087 | 0.07782 | -0.086975 | 0.059509 | 0.073242 | 0 | -0.054932 | 122.1542 | 122.0123 | 0.07782 | 122.1954 | 122.2916 | 0.27924 | -0.022888 | 122.1634 | 122.1085 | -0.032044 | 122.2275 | 122.0764 | -0.032043 | -0.018311 | 122.3328 | 122.2321 | 122.2183 | -0.24261 | 122.2229 | 122.2366 | 122.2412 | -0.14649
1896.1406 | 122.4792 | -122.1542 | 0.09613 | -0.020752 | 0.076642 | 0.00090781 | 0.0052081 | 0.015955 | 0.0018713 | 0.00047844 | -0.0040437 | 0.031761 | -0.0063575 | 0.02352 | 0.0023371 | -0.01346 | 0.022888 | -0.004578 | 0.041199 | 0.11444 | 0.17395 | -0.009155 | -0.13733 | 0.050354 | 0.07782 | -0.091553 | 0.068665 | 0.059509 | 0.009155 | -0.086975 | 122.1451 | 122.0169 | 0.07782 | 122.1497 | 122.2687 | 0.25177 | -0.073242 | 122.1634 | 122.0673 | -0.027465 | 122.2046 | 122.0627 | -0.004578 | -0.036621 | 122.3282 | 122.1771 | 122.1954 | -0.23346 | 122.2229 | 122.2137 | 122.2321 | -0.1831
1897.875 | 122.4518 | -122.1085 | 0.091553 | -0.013122 | 0.072369 | 0.00048061 | 0.0056355 | 0.013178 | -0.0041101 | -0.0048622 | -0.0040437 | 0.024498 | -0.0087073 | 0.02117 | 0.00062806 | -0.0081198 | 0.07782 | 0.12817 | 0.16022 | 0.17395 | 0.1236 | 0.013733 | -0.11444 | 0.09613 | 0.21515 | 0.041199 | 0.032043 | 0.027466 | 0.032043 | -0.036621 | 122.1222 | 121.994 | 0.032043 | 122.2366 | 122.2824 | 0.28839 | -0.013733 | 122.1405 | 122.0718 | -0.05951 | 122.2046 | 122.1497 | 0.07782 | -0.064087 | 122.2321 | 122.1863 | 122.2687 | -0.20599 | 122.1405 | 122.1359 | 122.3236 | -0.12817
1899.5625 | 122.4335 | -122.1313 | 0.086975 | -0.0054933 | 0.070447 | 0.005394 | 0.0058491 | 0.017237 | -0.0028283 | -0.0012306 | -0.0040437 | 0.026848 | -0.0095619 | 0.021597 | 0.0029779 | -0.010042 | 0.10071 | 0.12817 | 0.15106 | 0.16937 | 0.13733 | 0.004578 | -0.10071 | 0.09613 | 0.20142 | 0.022888 | 0.032043 | 0.013733 | 0.036621 | -0.041199 | 122.1359 | 122.0306 | 0.050354 | 122.2595 | 122.3007 | 0.27008 | 0.013733 | 122.168 | 122.0901 | -0.054932 | 122.2275 | 122.1542 | 0.064087 | -0.073242 | 122.2687 | 122.2321 | 122.2824 | -0.18768 | 122.1634 | 122.1451 | 122.3328 | -0.12817
1901.25 | 122.3328 | -122.1909 | 0.12817 | 0.0021362 | 0.067242 | 0.0043258 | 0.0024311 | 0.013819 | 0.00037606 | -0.00058956 | -0.011673 | 0.025994 | -0.013193 | 0.022879 | 0.0061823 | -0.008547 | 0.07782 | 0.13275 | 0.16022 | 0.16479 | 0.12817 | 0.045776 | -0.10071 | 0.082397 | 0.1236 | -0.004578 | 0.027466 | 0.050354 | 0.045776 | -0.050354 | 122.2366 | 122.0901 | 0 | 122.3236 | 122.3557 | 0.2655 | -0.050354 | 122.2366 | 122.1405 | -0.10071 | 122.2733 | 122.1863 | 0.045776 | -0.07782 | 122.319 | 122.2687 | 122.3511 | -0.22888 | 122.2183 | 122.2412 | 122.3145 | -0.17853
1902.9844 | 122.3648 | -122.1771 | 0.10529 | -0.0054933 | 0.071087 | 0.001976 | 0.00093567 | 0.015528 | 0.00016226 | -0.00080316 | -0.0040437 | 0.028343 | -0.011698 | 0.019888 | 0.0081049 | -0.0094016 | 0.086975 | 0.11902 | 0.14191 | 0.17395 | 0.14191 | 0.041199 | -0.10071 | 0.12817 | 0.13275 | -0.004578 | 0.022888 | 0.032043 | 0.032043 | -0.045776 | 122.2183 | 122.0764 | 0.036621 | 122.2961 | 122.3511 | 0.27466 | -0.018311 | 122.2092 | 122.1313 | -0.082398 | 122.3053 | 122.1725 | 0.041198 | -0.073243 | 122.319 | 122.2641 | 122.319 | -0.20599 | 122.2 | 122.2092 | 122.3099 | -0.15106
1904.7188 | 122.4152 | -122.1863 | 0.086975 | -0.013122 | 0.074078 | 0.0015488 | 0.0067035 | 0.016596 | -0.00047854 | -0.0025122 | -0.0040437 | 0.027916 | -0.010203 | 0.020316 | 0.0023371 | -0.0076926 | 0.054932 | 0.091553 | 0.10071 | 0.14191 | 0.14191 | 0.004578 | -0.13275 | 0.013733 | 0.086975 | -0.073242 | 0.07782 | 0.050354 | -0.009155 | -0.064087 | 122.1909 | 122.0535 | 0.054932 | 122.2778 | 122.3282 | 0.27466 | -0.032043 | 122.1771 | 122.1222 | -0.009155 | 122.2 | 122.113 | -0.009155 | -0.036621 | 122.3282 | 122.2412 | 122.287 | -0.21973 | 122.2641 | 122.2366 | 122.2733 | -0.15106
1906.4688 | 122.3831 | -122.2092 | 0.11444 | -0.013122 | 0.07301 | 0.0017624 | 0.0034991 | 0.015101 | 0.0044349 | -0.00058956 | -0.011673 | 0.031975 | -0.011484 | 0.023306 | 0.0078913 | -0.01047 | 0.07782 | 0.054932 | 0.059509 | 0.14191 | 0.14191 | -0.004578 | -0.14191 | 0.036621 | 0.068665 | -0.10529 | 0.068665 | 0.064087 | 0 | -0.073242 | 122.2046 | 122.0673 | 0.027466 | 122.2641 | 122.3511 | 0.28381 | -0.036621 | 122.2092 | 122.1359 | -0.045776 | 122.2458 | 122.1039 | -0.032044 | -0.050354 | 122.3511 | 122.287 | 122.2687 | -0.25635 | 122.2778 | 122.2733 | 122.2778 | -0.18768
1908.1562 | 122.3877 | -122.1817 | 0.10529 | -0.0054933 | 0.070874 | 0.0024032 | 0.00072207 | 0.015101 | -0.00026494 | -0.0014442 | -0.0040437 | 0.027703 | -0.0097755 | 0.018179 | 0.0042597 | -0.007479 | 0.064087 | 0.086975 | 0.1236 | 0.16022 | 0.13733 | 0.022888 | -0.10986 | 0.1236 | 0.13733 | -0.004578 | 0.027466 | 0.032043 | 0.022888 | -0.027466 | 122.2046 | 122.0718 | 0.032043 | 122.2687 | 122.3419 | 0.27008 | -0.041199 | 122.2046 | 122.1542 | -0.07782 | 122.3053 | 122.1771 | 0.022888 | -0.073243 | 122.319 | 122.2458 | 122.3053 | -0.21515 | 122.2092 | 122.2137 | 122.319 | -0.13275
1909.9062 | 122.4243 | -122.1863 | 0.13275 | 0.0021362 | 0.073437 | -0.00016019 | 0.0039265 | 0.013606 | 0.0027259 | -0.0018714 | -0.011673 | 0.029198 | -0.010843 | 0.022238 | 0.0063959 | -0.0089742 | 0.068665 | 0.064087 | 0.073242 | 0.14191 | 0.15106 | -0.004578 | -0.14191 | 0.050354 | 0.068665 | -0.091553 | 0.050354 | 0.064087 | 0.027466 | -0.068665 | 122.1817 | 122.0444 | 0.018311 | 122.2504 | 122.3282 | 0.28381 | -0.064086 | 122.2137 | 122.1176 | -0.082397 | 122.2366 | 122.0947 | -0.022888 | -0.068664 | 122.3373 | 122.2549 | 122.2595 | -0.27466 | 122.2366 | 122.2504 | 122.2549 | -0.20142
1911.6562 | 122.4792 | -122.1634 | 0.059509 | -0.013122 | 0.070233 | 0.0030442 | 0.0081989 | 0.017451 | -0.0047509 | -0.002085 | -0.011673 | 0.025566 | -0.0087073 | 0.021597 | -0.0010809 | -0.0061972 | 0.09613 | 0.16022 | 0.16937 | 0.16937 | 0.12817 | 0.041199 | -0.09613 | 0.082397 | 0.18768 | 0.032043 | 0.027466 | 0.050354 | 0.041199 | -0.054932 | 122.2046 | 122.0673 | 0.068665 | 122.3236 | 122.3328 | 0.2655 | 0.036621 | 122.2046 | 122.1085 | -0.032043 | 122.2458 | 122.1954 | 0.086975 | -0.009155 | 122.2916 | 122.2595 | 122.3328 | -0.15564 | 122.1909 | 122.2137 | 122.3511 | -0.11444
1913.3438 | 122.3465 | -122.2 | 0.11902 | 0.0021362 | 0.069378 | 0.0024032 | 0.0030719 | 0.014674 | -0.0041101 | -0.0018714 | -0.011673 | 0.025566 | -0.010416 | 0.022025 | 0.0046869 | -0.0081198 | 0.091553 | 0.11444 | 0.15564 | 0.17853 | 0.11902 | 0.036621 | -0.09613 | 0.086975 | 0.14648 | 0.018311 | 0.018311 | 0.036621 | 0.032043 | -0.045776 | 122.2366 | 122.1039 | 0 | 122.3145 | 122.3785 | 0.27466 | -0.027466 | 122.2321 | 122.1542 | -0.10071 | 122.287 | 122.2183 | 0.064087 | -0.082398 | 122.319 | 122.2916 | 122.3557 | -0.21515 | 122.2183 | 122.2366 | 122.3465 | -0.16479
1915.0312 | 122.4106 | -122.1909 | 0.10986 | -0.013122 | 0.071728 | 0.003685 | 0.0073443 | 0.015528 | -0.0045373 | -0.0027258 | -0.0040437 | 0.023857 | -0.0099891 | 0.020743 | 0.0021235 | -0.0096152 | 0 | 0.041199 | 0.086975 | 0.11902 | 0.13275 | 0.032043 | -0.11902 | 0.041199 | 0.091553 | -0.018311 | 0.045776 | 0.032043 | 0.018311 | -0.054932 | 122.2229 | 122.0718 | 0.022888 | 122.2321 | 122.3099 | 0.23804 | -0.10986 | 122.2092 | 122.1359 | -0.064087 | 122.2321 | 122.1725 | 0.036621 | -0.07782 | 122.3236 | 122.1909 | 122.2778 | -0.22888 | 122.2366 | 122.2229 | 122.2824 | -0.16479
1916.7812 | 122.4701 | -122.1725 | 0.10986 | -0.0054933 | 0.071942 | 0.00026701 | 0.0069171 | 0.013392 | -0.0019739 | -0.0046484 | -0.011673 | 0.026848 | -0.0074255 | 0.021384 | 0.00020086 | -0.010042 | 0.036621 | 0.064087 | 0.10986 | 0.13275 | 0.14648 | 0.018311 | -0.12817 | 0.054932 | 0.11444 | 0.018311 | 0.036621 | 0.054932 | 0.032043 | -0.036621 | 122.1909 | 122.0444 | 0.036621 | 122.2366 | 122.3053 | 0.26093 | -0.073242 | 122.2046 | 122.1359 | -0.073242 | 122.2275 | 122.1909 | 0.054932 | -0.054931 | 122.319 | 122.2092 | 122.2824 | -0.23804 | 122.2092 | 122.2275 | 122.287 | -0.14648
1918.5312 | 122.4976 | -122.1909 | 0.073242 | -0.028381 | 0.071301 | -0.00058739 | 0.0058491 | 0.014674 | 0.0031531 | -0.00058956 | -0.019302 | 0.029839 | -0.0065711 | 0.023306 | 0.0053279 | -0.011965 | 0.018311 | -0.022888 | 0.009155 | 0.09613 | 0.16022 | -0.022888 | -0.15564 | 0.018311 | 0.036621 | -0.10529 | 0.07782 | 0.09613 | -0.009155 | -0.086975 | 122.168 | 122.0352 | 0.086975 | 122.168 | 122.287 | 0.25177 | -0.054931 | 122.1817 | 122.1039 | 0.004578 | 122.2092 | 122.0856 | -0.018311 | 0.022888 | 122.3511 | 122.2092 | 122.2 | -0.22888 | 122.2687 | 122.287 | 122.2275 | -0.16022
1920.2188 | 122.374 | -122.2229 | 0.1236 | -0.0054933 | 0.066601 | 0.0051804 | 0.0026447 | 0.014033 | -0.0038965 | -0.0016578 | -0.0040437 | 0.026421 | -0.013407 | 0.020956 | 0.0042597 | -0.007479 | 0.032043 | 0.059509 | 0.10529 | 0.13275 | 0.14191 | 0.018311 | -0.09613 | 0.041199 | 0.07782 | -0.045776 | 0.036621 | 0.036621 | 0.041199 | -0.059509 | 122.2412 | 122.1268 | 0.018311 | 122.2824 | 122.3557 | 0.22888 | -0.091553 | 122.2641 | 122.1634 | -0.086975 | 122.2641 | 122.1771 | 0.013733 | -0.086975 | 122.3648 | 122.2549 | 122.3282 | -0.21973 | 122.2595 | 122.2595 | 122.3007 | -0.1831
1921.9531 | 122.4518 | -122.1954 | 0.10529 | -0.020752 | 0.075146 | 0.0011216 | 0.0075581 | 0.016169 | -0.0011193 | -0.0029394 | -0.011673 | 0.027275 | -0.010416 | 0.021811 | 0.0029779 | -0.0091878 | 0.091553 | 0.10529 | 0.14191 | 0.16937 | 0.15564 | 0.022888 | -0.10071 | 0.064087 | 0.13275 | -0.013733 | 0.054932 | 0.059509 | 0.018311 | -0.059509 | 122.2183 | 122.0947 | 0.050354 | 122.3007 | 122.3648 | 0.27008 | -0.013733 | 122.2137 | 122.1359 | -0.050354 | 122.2595 | 122.1817 | 0.045776 | -0.045777 | 122.3511 | 122.287 | 122.3373 | -0.20599 | 122.2504 | 122.2549 | 122.3282 | -0.16479
1923.625 | 122.3785 | -122.2137 | 0.1236 | -0.013122 | 0.073651 | -0.00016019 | 0.00072207 | 0.01446 | 0.0055029 | 0.0026148 | -0.0040437 | 0.029839 | -0.0095619 | 0.023093 | 0.0076777 | -0.012606 | 0.036621 | -0.018311 | 0.022888 | 0.086975 | 0.16479 | 0.009155 | -0.14191 | 0.009155 | 0.004578 | -0.13275 | 0.07782 | 0.068665 | 0.013733 | -0.059509 | 122.2229 | 122.0718 | 0.041199 | 122.1954 | 122.3007 | 0.22888 | -0.086975 | 122.2275 | 122.1542 | -0.045776 | 122.2229 | 122.081 | -0.073242 | -0.054931 | 122.3785 | 122.2504 | 122.2366 | -0.2655 | 122.2916 | 122.2824 | 122.2183 | -0.1831
1925.3594 | 122.3694 | -122.2275 | 0.12817 | -0.020752 | 0.067669 | 0.0038986 | 0.0037127 | 0.014887 | -0.0043237 | -0.0014442 | -0.0040437 | 0.02578 | -0.011271 | 0.021597 | 0.0014825 | -0.006838 | 0.041199 | 0.068665 | 0.10529 | 0.13275 | 0.12817 | 0.018311 | -0.09613 | 0.059509 | 0.091553 | -0.022888 | 0.032043 | 0.054932 | 0.027466 | -0.041199 | 122.2458 | 122.1313 | 0 | 122.2961 | 122.3602 | 0.22888 | -0.086975 | 122.2549 | 122.1863 | -0.096131 | 122.287 | 122.2046 | 0.018311 | -0.073242 | 122.3557 | 122.2687 | 122.3328 | -0.2243 | 122.2595 | 122.2824 | 122.319 | -0.16937
1927.0469 | 122.4472 | -122.1863 | 0.10529 | 0.0021362 | 0.073224 | 0.0021896 | 0.0064899 | 0.01681 | -0.0013329 | 0.00026484 | -0.011673 | 0.027489 | -0.0099891 | 0.023093 | -0.00044014 | -0.0076926 | 0.036621 | 0.059509 | 0.07782 | 0.13275 | 0.14648 | 0.004578 | -0.14648 | 0.004578 | 0.064087 | -0.091553 | 0.064087 | 0.073242 | -0.013733 | -0.07782 | 122.1909 | 122.0398 | 0.041198 | 122.2458 | 122.319 | 0.27924 | -0.068665 | 122.1725 | 122.1085 | -0.041199 | 122.1909 | 122.0947 | -0.013733 | -0.032044 | 122.3328 | 122.2229 | 122.2641 | -0.25177 | 122.2504 | 122.2595 | 122.2504 | -0.18311
1928.7969 | 122.4518 | -122.1909 | 0.10071 | -0.0054933 | 0.072583 | 0.0015488 | 0.0064899 | 0.017237 | -0.0013329 | -0.0044348 | 0.0035858 | 0.027916 | -0.011271 | 0.022238 | 0.0034051 | -0.0098288 | 0.073242 | 0.10529 | 0.11902 | 0.16479 | 0.13275 | 0.004578 | -0.13733 | 0.041199 | 0.11902 | -0.041199 | 0.054932 | 0.064087 | 0.022888 | -0.050354 | 122.1954 | 122.0535 | 0.032043 | 122.2961 | 122.3557 | 0.30212 | -0.027466 | 122.2137 | 122.1405 | -0.045776 | 122.2321 | 122.1497 | 0.009155 | -0.036621 | 122.3236 | 122.2641 | 122.3099 | -0.23804 | 122.2458 | 122.2549 | 122.3099 | -0.15106
1930.5469 | 122.4243 | -122.2275 | 0.1236 | -0.0054933 | 0.072583 | 0.0024032 | 0.0032855 | 0.014887 | 0.0048621 | -0.00016236 | 0.0035858 | 0.028984 | -0.010416 | 0.022025 | 0.0070367 | -0.0089742 | 0.022888 | -0.018311 | 0.027466 | 0.09613 | 0.17395 | 0.009155 | -0.14191 | 0.059509 | 0.050354 | -0.064087 | 0.050354 | 0.059509 | 0.004578 | -0.068665 | 122.2366 | 122.0856 | 0.050354 | 122.2092 | 122.3236 | 0.23804 | -0.10071 | 122.2321 | 122.1588 | -0.073242 | 122.287 | 122.1634 | 0.004578 | -0.064087 | 122.4014 | 122.2504 | 122.2549 | -0.2655 | 122.2778 | 122.287 | 122.2778 | -0.19226
1932.2812 | 122.4518 | -122.2275 | 0.10071 | -0.0054933 | 0.074719 | 0.001976 | 0.0022175 | 0.012965 | 0.0033667 | 0.00047844 | -0.011673 | 0.030907 | -0.0095619 | 0.022238 | 0.0081049 | -0.010897 | 0.068665 | 0.064087 | 0.082397 | 0.12817 | 0.15564 | 0 | -0.13733 | 0.045776 | 0.068665 | -0.07782 | 0.07782 | 0.054932 | 0.022888 | -0.064087 | 122.2275 | 122.0901 | 0.054932 | 122.2916 | 122.3557 | 0.2655 | -0.032043 | 122.2504 | 122.1634 | -0.022888 | 122.2733 | 122.1497 | -0.013733 | -0.045776 | 122.3831 | 122.2961 | 122.3099 | -0.23804 | 122.3053 | 122.2824 | 122.2961 | -0.1648
1934.0156 | 122.493 | -122.2046 | 0.086975 | -0.0054933 | 0.071087 | 0.0024032 | 0.0060627 | 0.015528 | -0.00069214 | -0.002085 | -0.011673 | 0.027062 | -0.010416 | 0.02352 | 0.0029779 | -0.0081198 | -0.032043 | 0.004578 | 0.018311 | 0.073242 | 0.16937 | -0.004578 | -0.15106 | -0.013733 | 0.036621 | -0.10529 | 0.064087 | 0.09613 | -0.022888 | -0.082397 | 122.2 | 122.0535 | 0.082398 | 122.2092 | 122.2778 | 0.2243 | -0.11902 | 122.1817 | 122.1222 | -0.022888 | 122.1909 | 122.0993 | -0.022889 | 0.009155 | 122.374 | 122.1725 | 122.2229 | -0.23804 | 122.2687 | 122.3007 | 122.2412 | -0.16937
1935.7812 | 122.3969 | -122.2366 | 0.10529 | -0.020752 | 0.074078 | 0.0028306 | 0.0024311 | 0.016169 | 0.0033667 | -0.00037596 | -0.0040437 | 0.030907 | -0.0099891 | 0.022025 | 0.0053279 | -0.0076926 | -0.013733 | -0.036621 | 0.004578 | 0.091553 | 0.1831 | -0.013733 | -0.14191 | -0.004578 | -0.004578 | -0.13275 | 0.064087 | 0.07782 | 0.018311 | -0.073242 | 122.2229 | 122.0947 | 0.077819 | 122.2 | 122.3282 | 0.23346 | -0.11902 | 122.2549 | 122.1634 | -0.041199 | 122.2321 | 122.1039 | -0.059509 | -0.027466 | 122.4197 | 122.2229 | 122.2412 | -0.24719 | 122.3007 | 122.3145 | 122.2321 | -0.17853
1937.4531 | 122.5113 | -122.1863 | 0.073242 | -0.020752 | 0.068524 | 0.0060348 | 0.0032855 | 0.018092 | -0.0077417 | -0.002085 | -0.0040437 | 0.024071 | -0.0084937 | 0.021384 | 0.0012689 | -0.008547 | 0.013733 | 0.091553 | 0.14191 | 0.15106 | 0.12817 | 0.013733 | -0.10071 | 0.068665 | 0.16479 | 0.018311 | 0.027466 | 0.032043 | 0.027466 | -0.041199 | 122.2 | 122.0856 | 0.054932 | 122.2778 | 122.3373 | 0.25177 | -0.059509 | 122.2137 | 122.1451 | -0.045776 | 122.2549 | 122.2046 | 0.05951 | -0.041199 | 122.3145 | 122.2 | 122.3282 | -0.17395 | 122.2137 | 122.2183 | 122.3511 | -0.11444
1939.1875 | 122.4701 | -122.2229 | 0.082397 | 0.0021362 | 0.073224 | 0.001976 | 0.0081989 | 0.015955 | -0.0030419 | -0.0027258 | -0.0040437 | 0.024712 | -0.0097755 | 0.021597 | -0.00065374 | -0.01047 | 0.082397 | 0.11902 | 0.14648 | 0.17853 | 0.1236 | 0.027466 | -0.10986 | 0.07782 | 0.1831 | 0.013733 | 0.032043 | 0.036621 | 0.032043 | -0.050354 | 122.2504 | 122.113 | 0.041199 | 122.3419 | 122.4014 | 0.28839 | 0 | 122.2549 | 122.1725 | -0.050354 | 122.3007 | 122.2366 | 0.064087 | -0.045776 | 122.3465 | 122.3053 | 122.3694 | -0.19226 | 122.2549 | 122.2595 | 122.406 | -0.13275
1940.9531 | 122.4106 | -122.2275 | 0.11902 | -0.013122 | 0.068951 | -0.0018692 | 0.0011493 | 0.014674 | 0.00037606 | -0.00058956 | 0.011215 | 0.029198 | -0.0099891 | 0.021811 | 0.0053279 | -0.0079062 | 0.091553 | 0.11902 | 0.15106 | 0.18768 | 0.11444 | 0.050354 | -0.10071 | 0.10986 | 0.14191 | 0.022888 | 0.027466 | 0.032043 | 0.036621 | -0.041199 | 122.2778 | 122.1268 | -0.004578 | 122.3465 | 122.4152 | 0.28839 | -0.027466 | 122.2641 | 122.1863 | -0.091553 | 122.3373 | 122.2504 | 0.064087 | -0.086976 | 122.3419 | 122.319 | 122.3785 | -0.21973 | 122.2549 | 122.2595 | 122.3694 | -0.16022
1942.625 | 122.5204 | -122.1771 | 0.07782 | -0.0054933 | 0.071942 | 0.0013352 | 0.0081989 | 0.017878 | -0.0041101 | -0.002085 | -0.011673 | 0.026848 | -0.010416 | 0.019888 | 0.00041446 | -0.0094016 | 0.086975 | 0.14648 | 0.17853 | 0.17395 | 0.14191 | 0.041199 | -0.09613 | 0.10071 | 0.20142 | 0.059509 | 0.027466 | 0.032043 | 0.045776 | -0.027466 | 122.2183 | 122.081 | 0.064087 | 122.3236 | 122.3511 | 0.27008 | 0.009155 | 122.2229 | 122.1497 | -0.050354 | 122.2778 | 122.2366 | 0.086975 | -0.045777 | 122.319 | 122.2641 | 122.3557 | -0.17395 | 122.2046 | 122.2092 | 122.3785 | -0.10529
1944.2969 | 122.5159 | -122.2321 | 0.10071 | 0.0021362 | 0.073864 | -0.0016556 | 0.0079853 | 0.015742 | 0.0020849 | -0.00080316 | -0.0040437 | 0.02813 | -0.0072119 | 0.024161 | 0.0034051 | -0.0098288 | 0 | -0.013733 | 0.004578 | 0.086975 | 0.19226 | 0 | -0.17395 | -0.018311 | 0.022888 | -0.1236 | 0.082397 | 0.068665 | -0.013733 | -0.064087 | 122.2321 | 122.0581 | 0.091553 | 122.2183 | 122.319 | 0.26092 | -0.10071 | 122.2183 | 122.168 | -0.018311 | 122.2137 | 122.1085 | -0.059509 | -0.032043 | 122.4243 | 122.2321 | 122.2366 | -0.27466 | 122.3145 | 122.3007 | 122.2549 | -0.1648
1946.0469 | 122.3969 | -122.2458 | 0.10986 | -0.0054933 | 0.074505 | -0.00016019 | 0.0022175 | 0.016383 | 0.0012305 | -0.0014442 | -0.0040437 | 0.027275 | -0.011271 | 0.020316 | 0.0044733 | -0.0091878 | 0.10071 | 0.10986 | 0.14648 | 0.17395 | 0.12817 | 0.050354 | -0.091553 | 0.11444 | 0.14191 | 0.004578 | 0.018311 | 0.036621 | 0.036621 | -0.032043 | 122.2961 | 122.1542 | 0.018311 | 122.3557 | 122.4197 | 0.2655 | -0.009155 | 122.2824 | 122.2137 | -0.091552 | 122.3602 | 122.2504 | 0.036621 | -0.073242 | 122.374 | 122.3465 | 122.3923 | -0.20142 | 122.2641 | 122.2824 | 122.3877 | -0.14191
1947.7344 | 122.493 | -122.2137 | 0.086975 | -0.013122 | 0.072369 | 0.0021896 | 0.0071307 | 0.016383 | 0.0010169 | -0.00016236 | -0.011673 | 0.028557 | -0.0093481 | 0.020102 | 0.0031915 | -0.0081198 | 0.041199 | 0.086975 | 0.09613 | 0.14191 | 0.14648 | 0.004578 | -0.11902 | 0.009155 | 0.064087 | -0.064087 | 0.064087 | 0.082397 | -0.004578 | -0.073242 | 122.2183 | 122.0947 | 0.059509 | 122.3007 | 122.3557 | 0.26093 | -0.045776 | 122.2092 | 122.1405 | -0.022888 | 122.2229 | 122.1497 | 0.009155 | -0.004578 | 122.3602 | 122.2549 | 122.3099 | -0.20599 | 122.2778 | 122.2961 | 122.2778 | -0.16022
1949.4688 | 122.3877 | -122.2778 | 0.13275 | -0.0054933 | 0.068951 | 0.0026168 | -0.00013253 | 0.015955 | -0.00090574 | -0.00058956 | -0.011673 | 0.026421 | -0.011484 | 0.020529 | 0.0061823 | -0.008547 | 0.082397 | 0.1236 | 0.13275 | 0.14648 | 0.12817 | 0.027466 | -0.11444 | 0.091553 | 0.11444 | 0 | 0.032043 | 0.045776 | 0.036621 | -0.054932 | 122.3053 | 122.1634 | -0.004577 | 122.4014 | 122.4243 | 0.26093 | -0.050354 | 122.3145 | 122.2229 | -0.10071 | 122.3694 | 122.2778 | 0.054932 | -0.086975 | 122.406 | 122.3602 | 122.4106 | -0.24719 | 122.3099 | 122.3236 | 122.3923 | -0.18768
1951.1562 | 122.4289 | -122.2687 | 0.11444 | -0.0054933 | 0.070019 | 0.00048061 | 0.0026447 | 0.01681 | 0.0012305 | -0.0012306 | 0.0035858 | 0.027062 | -0.0089209 | 0.019034 | 0.0059687 | -0.0094016 | 0.10071 | 0.11902 | 0.13275 | 0.17853 | 0.12817 | 0.022888 | -0.091553 | 0.11444 | 0.13733 | 0.009155 | 0.018311 | 0.013733 | 0.045776 | -0.032043 | 122.2916 | 122.1771 | 0.013733 | 122.3877 | 122.4472 | 0.27008 | -0.013733 | 122.3145 | 122.2366 | -0.09613 | 122.3831 | 122.2778 | 0.041198 | -0.10071 | 122.3969 | 122.3694 | 122.4014 | -0.20599 | 122.287 | 122.2824 | 122.406 | -0.14648
1952.9062 | 122.5388 | -122.2229 | 0.091553 | -0.020752 | 0.071515 | 0.0013352 | 0.0049945 | 0.015101 | 0.0042213 | -0.00058956 | -0.011673 | 0.029412 | -0.011271 | 0.021384 | 0.0044733 | -0.010897 | 0 | -0.018311 | 0.013733 | 0.10529 | 0.15106 | 0.004578 | -0.14648 | 0 | 0.050354 | -0.10071 | 0.068665 | 0.082397 | 0.004578 | -0.073242 | 122.2275 | 122.0764 | 0.059509 | 122.2046 | 122.3282 | 0.25177 | -0.091553 | 122.2275 | 122.1497 | -0.022888 | 122.2229 | 122.1222 | -0.027466 | -0.009156 | 122.374 | 122.2229 | 122.2366 | -0.23804 | 122.2916 | 122.3053 | 122.2733 | -0.16479
1954.6562 | 122.5204 | -122.2 | 0.10529 | -0.0054933 | 0.067669 | 0.001976 | 0.0064899 | 0.01446 | -0.0041101 | -0.0018714 | -0.0040437 | 0.024498 | -0.011484 | 0.020102 | 0.0021235 | -0.0091878 | 0.041199 | 0.068665 | 0.11902 | 0.14191 | 0.13275 | 0.036621 | -0.1236 | 0.073242 | 0.12817 | 0.027466 | 0.041199 | 0.064087 | 0.032043 | -0.050354 | 122.2366 | 122.0764 | 0.027465 | 122.2687 | 122.3419 | 0.2655 | -0.064087 | 122.2321 | 122.1497 | -0.064087 | 122.2733 | 122.2275 | 0.07782 | -0.041199 | 122.3328 | 122.2412 | 122.319 | -0.22888 | 122.2412 | 122.2641 | 122.3282 | -0.15564
1956.3438 | 122.4564 | -122.2504 | 0.13275 | 0.0021362 | 0.07301 | -0.00058739 | 0.00072207 | 0.017237 | 0.0027259 | -0.0018714 | -0.011673 | 0.029412 | -0.0084937 | 0.023306 | 0.0055415 | -0.011324 | 0.091553 | 0.073242 | 0.10529 | 0.15106 | 0.12817 | 0.022888 | -0.10986 | 0.11902 | 0.11902 | -0.009155 | 0.022888 | 0.032043 | 0.032043 | -0.032043 | 122.2733 | 122.1405 | -0.004577 | 122.3236 | 122.4014 | 0.26093 | -0.041198 | 122.2824 | 122.2183 | -0.10986 | 122.3694 | 122.2412 | 0.022888 | -0.10071 | 122.3785 | 122.3419 | 122.3557 | -0.24261 | 122.2733 | 122.2824 | 122.3694 | -0.16479
1958.0938 | 122.4152 | -122.2778 | 0.11902 | 0.0021362 | 0.075146 | 0.00026701 | 0.0028583 | 0.015101 | 0.0046485 | -0.00016236 | -0.011673 | 0.031334 | -0.0093481 | 0.022238 | 0.0081049 | -0.010256 | 0.027466 | 0.004578 | 0.018311 | 0.10529 | 0.16479 | -0.004578 | -0.12817 | 0.009155 | 0.018311 | -0.13275 | 0.073242 | 0.082397 | -0.009155 | -0.082397 | 122.2733 | 122.1497 | 0.045776 | 122.2824 | 122.3831 | 0.23346 | -0.091553 | 122.2687 | 122.1954 | -0.045777 | 122.287 | 122.1451 | -0.050354 | -0.036622 | 122.4426 | 122.3053 | 122.2961 | -0.24719 | 122.3511 | 122.3602 | 122.2961 | -0.20142
1959.8438 | 122.5388 | -122.2504 | 0.073242 | -0.013122 | 0.071515 | 0.0015488 | 0.0081989 | 0.017024 | -0.0021875 | -0.003794 | -0.011673 | 0.024712 | -0.0095619 | 0.02117 | -0.00065374 | -0.0094016 | 0.073242 | 0.16022 | 0.16937 | 0.19226 | 0.1236 | 0.045776 | -0.10071 | 0.10071 | 0.1831 | 0.050354 | 0.032043 | 0.027466 | 0.036621 | -0.036621 | 122.2961 | 122.1497 | 0.050354 | 122.4106 | 122.4426 | 0.29297 | 0 | 122.287 | 122.2137 | -0.041199 | 122.3511 | 122.3007 | 0.086975 | -0.045776 | 122.374 | 122.3236 | 122.4197 | -0.17395 | 122.2824 | 122.2778 | 122.4335 | -0.10986
1961.5312 | 122.4609 | -122.2458 | 0.09613 | -0.0054933 | 0.072369 | 0.0015488 | 0.0020039 | 0.015315 | 0.0029395 | 0.00069204 | -0.011673 | 0.028557 | -0.0087073 | 0.021597 | 0.0055415 | -0.008547 | 0.018311 | 0.013733 | 0.041199 | 0.091553 | 0.15564 | 0.004578 | -0.10529 | 0.059509 | 0.059509 | -0.050354 | 0.036621 | 0.050354 | 0.018311 | -0.045776 | 122.2504 | 122.1405 | 0.05951 | 122.2595 | 122.3373 | 0.19684 | -0.077819 | 122.2641 | 122.2 | -0.059509 | 122.3053 | 122.1954 | -0.004578 | -0.045776 | 122.4014 | 122.2641 | 122.287 | -0.20142 | 122.2824 | 122.2961 | 122.3053 | -0.14191
1963.2812 | 122.4701 | -122.2549 | 0.10529 | -0.013122 | 0.074719 | -0.00080099 | 0.0034991 | 0.017024 | 0.0027259 | -0.0018714 | -0.0040437 | 0.027916 | -0.010203 | 0.02352 | 0.0070367 | -0.0083334 | 0 | -0.004578 | 0 | 0.082397 | 0.17853 | -0.009155 | -0.14648 | 0.022888 | 0.004578 | -0.09613 | 0.064087 | 0.064087 | 0.009155 | -0.054932 | 122.2458 | 122.1085 | 0.073242 | 122.2504 | 122.3373 | 0.22888 | -0.10529 | 122.2641 | 122.2 | -0.041199 | 122.2778 | 122.1588 | -0.041198 | -0.041199 | 122.4335 | 122.2549 | 122.2549 | -0.25177 | 122.319 | 122.319 | 122.2595 | -0.16022
1965.0312 | 122.4747 | -122.2641 | 0.091553 | -0.0054933 | 0.073651 | -0.00016019 | 0.0043537 | 0.015315 | 0.0027259 | 5.1244e-05 | -0.011673 | 0.02813 | -0.0093481 | 0.020316 | 0.0053279 | -0.0094016 | 0.022888 | 0.045776 | 0.073242 | 0.1236 | 0.15564 | 0.018311 | -0.10986 | 0.09613 | 0.09613 | -0.013733 | 0.032043 | 0.036621 | 0.041199 | -0.050354 | 122.2824 | 122.1542 | 0.064087 | 122.3099 | 122.3877 | 0.23346 | -0.068665 | 122.3053 | 122.2137 | -0.05951 | 122.3602 | 122.2504 | 0.036621 | -0.054932 | 122.4197 | 122.287 | 122.3373 | -0.20142 | 122.2961 | 122.3007 | 122.3602 | -0.14191
1966.7188 | 122.4609 | -122.2916 | 0.1236 | -0.020752 | 0.075573 | 0.0013352 | 0.0049945 | 0.014674 | 0.0027259 | -0.00016236 | -0.0040437 | 0.030052 | -0.0091345 | 0.020956 | 0.0046869 | -0.0089742 | -0.009155 | -0.050354 | -0.013733 | 0.086975 | 0.16937 | -0.004578 | -0.12817 | -0.013733 | -0.032043 | -0.11902 | 0.073242 | 0.073242 | 0.009155 | -0.064087 | 122.287 | 122.1634 | 0.045777 | 122.2412 | 122.3785 | 0.21515 | -0.13275 | 122.3007 | 122.2275 | -0.050354 | 122.2778 | 122.1725 | -0.054932 | -0.050354 | 122.4609 | 122.2824 | 122.2778 | -0.25177 | 122.3648 | 122.3648 | 122.2595 | -0.18768
1968.4688 | 122.5479 | -122.2046 | 0.09613 | -0.0054933 | 0.071728 | 0.0030442 | 0.0092669 | 0.014887 | -0.0038965 | -0.00058956 | -0.011673 | 0.024925 | -0.0091345 | 0.020102 | 0.00020086 | -0.008547 | 0.07782 | 0.16479 | 0.16479 | 0.17853 | 0.1236 | 0.036621 | -0.10071 | 0.07782 | 0.17853 | 0.032043 | 0.041199 | 0.036621 | 0.032043 | -0.036621 | 122.2412 | 122.1039 | 0.027466 | 122.3694 | 122.3831 | 0.27924 | -0.01831 | 122.2366 | 122.168 | -0.054931 | 122.2824 | 122.2366 | 0.068664 | -0.059509 | 122.3282 | 122.2824 | 122.3694 | -0.19684 | 122.2458 | 122.2412 | 122.3831 | -0.13275
1970.1562 | 122.5433 | -122.2412 | 0.082397 | -0.0054933 | 0.073437 | 0.0013352 | 0.0041401 | 0.016383 | 0.0048621 | 5.1244e-05 | -0.0040437 | 0.030052 | -0.01063 | 0.022025 | 0.0061823 | -0.012606 | 0.045776 | 0.032043 | 0.045776 | 0.12817 | 0.17853 | 0.009155 | -0.12817 | 0.041199 | 0.073242 | -0.07782 | 0.059509 | 0.059509 | 0.013733 | -0.050354 | 122.2504 | 122.113 | 0.096131 | 122.2733 | 122.3694 | 0.25635 | -0.036621 | 122.2549 | 122.1909 | -0.022888 | 122.2824 | 122.1634 | -0.027466 | -0.022888 | 122.4197 | 122.287 | 122.287 | -0.21057 | 122.3007 | 122.3007 | 122.3145 | -0.13275
1971.9062 | 122.4152 | -122.2778 | 0.13275 | -0.0054933 | 0.068738 | 0.00069421 | 0.0037127 | 0.017024 | -0.00090574 | 5.1244e-05 | -0.011673 | 0.025139 | -0.011271 | 0.021597 | 0.0010553 | -0.0055564 | 0.059509 | 0.10071 | 0.1236 | 0.14648 | 0.12817 | 0.022888 | -0.082397 | 0.068665 | 0.10986 | -0.022888 | 0.018311 | 0.041199 | 0.045776 | -0.041199 | 122.3007 | 122.1954 | -0.004577 | 122.3785 | 122.4243 | 0.22888 | -0.073242 | 122.3236 | 122.2366 | -0.11444 | 122.3465 | 122.2549 | 0.018311 | -0.091552 | 122.406 | 122.3373 | 122.4014 | -0.21515 | 122.2961 | 122.319 | 122.3877 | -0.17395
1973.6562 | 122.5662 | -122.2641 | 0.09613 | 0.0021362 | 0.072583 | 0.003685 | 0.010121 | 0.013178 | -0.0045373 | -0.0029394 | -0.011673 | 0.02578 | -0.0080665 | 0.021811 | -1.2744e-05 | -0.0087606 | 0.091553 | 0.14648 | 0.16937 | 0.17853 | 0.13275 | 0.027466 | -0.09613 | 0.07782 | 0.17853 | 0.032043 | 0.022888 | 0.045776 | 0.045776 | -0.036621 | 122.2916 | 122.168 | 0.036621 | 122.4106 | 122.4426 | 0.27466 | -0.004577 | 122.3099 | 122.2275 | -0.073242 | 122.3419 | 122.2961 | 0.068664 | -0.050354 | 122.3969 | 122.3557 | 122.4335 | -0.19226 | 122.287 | 122.3099 | 122.4426 | -0.13275
1975.4062 | 122.4335 | -122.2961 | 0.11902 | -0.013122 | 0.06831 | 0.00048061 | 0.0030719 | 0.018305 | -5.1338e-05 | -0.0025122 | -0.019302 | 0.026421 | -0.010843 | 0.022238 | 0.0044733 | -0.0094016 | 0.10071 | 0.11902 | 0.13733 | 0.16022 | 0.11902 | 0.032043 | -0.09613 | 0.09613 | 0.13275 | 0.013733 | 0.022888 | 0.032043 | 0.032043 | -0.032043 | 122.3282 | 122.2 | 0 | 122.4152 | 122.4564 | 0.25635 | -0.018311 | 122.3282 | 122.2641 | -0.096131 | 122.3923 | 122.3099 | 0.045776 | -0.086976 | 122.4152 | 122.3969 | 122.4335 | -0.21515 | 122.319 | 122.3282 | 122.4289 | -0.15106
1977.0938 | 122.5708 | -122.2366 | 0.086975 | -0.013122 | 0.071728 | 0.0017624 | 0.0064899 | 0.018092 | -5.1338e-05 | -0.0022986 | 0.0035858 | 0.028771 | -0.0072119 | 0.022238 | 0.0038325 | -0.010897 | -0.013733 | -0.009155 | 0.013733 | 0.091553 | 0.16937 | -0.027466 | -0.16022 | -0.009155 | 0.027466 | -0.11902 | 0.07782 | 0.086975 | 0.018311 | -0.082397 | 122.2092 | 122.0764 | 0.082398 | 122.2275 | 122.3282 | 0.25177 | -0.10071 | 122.2549 | 122.1542 | -0.009155 | 122.2275 | 122.1176 | -0.036622 | 0 | 122.406 | 122.2229 | 122.2504 | -0.24719 | 122.3145 | 122.3236 | 122.2641 | -0.16937
1978.8281 | 122.525 | -122.2595 | 0.10529 | -0.020752 | 0.07301 | 0.0011216 | 0.0069171 | 0.016169 | -0.00047854 | -0.0029394 | -0.019302 | 0.029198 | -0.0072119 | 0.023734 | 0.0027643 | -0.010897 | 0.036621 | 0.050354 | 0.068665 | 0.12817 | 0.14648 | 0.013733 | -0.1236 | 0.018311 | 0.059509 | -0.07782 | 0.068665 | 0.07782 | 0.013733 | -0.07782 | 122.2733 | 122.1359 | 0.041198 | 122.3099 | 122.3877 | 0.25177 | -0.068665 | 122.2733 | 122.1817 | -0.036621 | 122.2778 | 122.1817 | 0 | -0.027466 | 122.406 | 122.2961 | 122.3282 | -0.22888 | 122.3282 | 122.3373 | 122.319 | -0.18311
1980.5781 | 122.493 | -122.2824 | 0.11902 | -0.013122 | 0.069806 | 0.001976 | 0.00093567 | 0.014887 | 0.0016577 | 0.00047844 | -0.019302 | 0.028343 | -0.0095619 | 0.020956 | 0.0059687 | -0.0081198 | 0.064087 | 0.073242 | 0.10071 | 0.15564 | 0.1236 | 0.013733 | -0.10986 | 0.10986 | 0.10986 | 0 | 0.027466 | 0.022888 | 0.041199 | -0.022888 | 122.2961 | 122.1725 | 0.004577 | 122.3557 | 122.4381 | 0.2655 | -0.054932 | 122.3236 | 122.2595 | -0.091553 | 122.3923 | 122.2824 | 0.022888 | -0.096131 | 122.406 | 122.3465 | 122.3831 | -0.22888 | 122.3099 | 122.3053 | 122.3923 | -0.14191
1982.2656 | 122.5388 | -122.2641 | 0.07782 | -0.020752 | 0.071515 | 0.00026701 | 0.0084125 | 0.015315 | -0.0021875 | -0.00016236 | 0.0035858 | 0.026848 | -0.0089209 | 0.019675 | 0.0010553 | -0.0091878 | 0.091553 | 0.13275 | 0.15564 | 0.18768 | 0.13733 | 0.045776 | -0.10071 | 0.09613 | 0.16022 | 0.009155 | 0.022888 | 0.045776 | 0.041199 | -0.045776 | 122.3099 | 122.1634 | 0.059509 | 122.3969 | 122.4518 | 0.28839 | 0.013733 | 122.3053 | 122.2183 | -0.054932 | 122.3602 | 122.2733 | 0.054931 | -0.032044 | 122.4014 | 122.3557 | 122.4197 | -0.17853 | 122.287 | 122.3099 | 122.4243 | -0.1236
1984 | 122.5525 | -122.2641 | 0.10071 | -0.013122 | 0.072583 | 0.0032578 | 0.0081989 | 0.017237 | 0.0025123 | 0.00026484 | 0.0035858 | 0.02813 | -0.0093481 | 0.023734 | 0.0031915 | -0.0096152 | 0 | -0.022888 | 0.009155 | 0.086975 | 0.16937 | -0.009155 | -0.14648 | -0.004578 | 0.018311 | -0.1236 | 0.091553 | 0.082397 | -0.013733 | -0.07782 | 122.2549 | 122.1176 | 0.068665 | 122.2412 | 122.3511 | 0.23346 | -0.10071 | 122.2504 | 122.1863 | -0.009155 | 122.2595 | 122.1405 | -0.045776 | -0.018311 | 122.4335 | 122.2641 | 122.2733 | -0.24719 | 122.3557 | 122.3465 | 122.2824 | -0.17853
1985.6719 | 122.4472 | -122.2778 | 0.10986 | -0.0054933 | 0.066815 | 0.0047532 | 0.0020039 | 0.01446 | -0.0030419 | -0.0014442 | -0.011673 | 0.02813 | -0.012125 | 0.020743 | 0.0025507 | -0.0098288 | 0.07782 | 0.091553 | 0.11902 | 0.14191 | 0.12817 | 0.009155 | -0.091553 | 0.068665 | 0.10529 | -0.013733 | 0.045776 | 0.041199 | 0.032043 | -0.059509 | 122.287 | 122.1863 | 0.018311 | 122.3694 | 122.4197 | 0.23346 | -0.032043 | 122.3099 | 122.2183 | -0.064087 | 122.3465 | 122.2641 | 0.045776 | -0.068664 | 122.406 | 122.3557 | 122.3969 | -0.20142 | 122.3236 | 122.319 | 122.3831 | -0.16937
1987.4219 | 122.5296 | -122.2641 | 0.09613 | -0.0054933 | 0.072155 | 0.0026168 | 0.0056355 | 0.015955 | -0.00090574 | -0.0031532 | -0.011673 | 0.024925 | -0.0097755 | 0.022025 | 0.0014825 | -0.0098288 | 0.10986 | 0.1236 | 0.15564 | 0.17853 | 0.11444 | 0.041199 | -0.086975 | 0.10529 | 0.17853 | 0.013733 | 0.036621 | 0.032043 | 0.013733 | -0.041199 | 122.3053 | 122.1771 | 0.018311 | 122.3877 | 122.4426 | 0.2655 | 0.013733 | 122.2778 | 122.2229 | -0.059509 | 122.3694 | 122.2778 | 0.054932 | -0.064087 | 122.3785 | 122.374 | 122.4197 | -0.1831 | 122.3007 | 122.2961 | 122.4426 | -0.13733
1989.1094 | 122.5479 | -122.3099 | 0.10529 | -0.013122 | 0.072796 | 0.0021896 | 0.0037127 | 0.014246 | 0.0044349 | 0.00069204 | -0.011673 | 0.030693 | -0.010843 | 0.022238 | 0.0078913 | -0.0091878 | 0.091553 | 0.050354 | 0.064087 | 0.13733 | 0.15106 | 0.009155 | -0.1236 | 0.050354 | 0.07782 | -0.068665 | 0.059509 | 0.059509 | 0.018311 | -0.059509 | 122.319 | 122.1863 | 0.045776 | 122.3602 | 122.4472 | 0.26093 | -0.013733 | 122.3282 | 122.2504 | -0.045777 | 122.3602 | 122.2412 | -0.009156 | -0.045777 | 122.4609 | 122.4014 | 122.374 | -0.22888 | 122.3694 | 122.3694 | 122.3877 | -0.16479
1990.8594 | 122.5388 | -122.2549 | 0.082397 | -0.0054933 | 0.069592 | 0.0041122 | 0.0073443 | 0.015315 | -0.0041101 | -0.00080316 | -0.0040437 | 0.025566 | -0.0093481 | 0.021384 | 0.0029779 | -0.0076926 | 0.086975 | 0.14191 | 0.16479 | 0.18768 | 0.13275 | 0.027466 | -0.09613 | 0.091553 | 0.19684 | 0.022888 | 0.022888 | 0.045776 | 0.045776 | -0.041199 | 122.2824 | 122.1588 | 0.050354 | 122.3969 | 122.4426 | 0.28381 | 0.004578 | 122.3007 | 122.2137 | -0.059509 | 122.3465 | 122.2778 | 0.064087 | -0.036621 | 122.3877 | 122.3419 | 122.4197 | -0.17853 | 122.2778 | 122.3007 | 122.4518 | -0.1236
1992.6094 | 122.5891 | -122.2687 | 0.068665 | 0.0021362 | 0.071728 | 0.0024032 | 0.0054217 | 0.01681 | 0.0022987 | -0.002085 | 0.0035858 | 0.030052 | -0.0095619 | 0.02352 | 0.0049005 | -0.010256 | 0.004578 | -0.013733 | 0 | 0.091553 | 0.16022 | 0 | -0.14191 | 0.013733 | 0.050354 | -0.10986 | 0.07782 | 0.10071 | -0.004578 | -0.068665 | 122.2687 | 122.1268 | 0.091552 | 122.2549 | 122.3602 | 0.23346 | -0.064087 | 122.2641 | 122.2 | 0.009155 | 122.2824 | 122.1588 | -0.041198 | 0.032043 | 122.4289 | 122.2733 | 122.2687 | -0.21057 | 122.3465 | 122.3694 | 122.319 | -0.13733
1994.375 | 122.5891 | -122.2778 | 0.086975 | -0.013122 | 0.072583 | 0.0043258 | 0.0075581 | 0.017664 | -0.0032555 | -0.0025122 | -0.011673 | 0.02578 | -0.010416 | 0.02117 | 0.0014825 | -0.0098288 | 0.09613 | 0.16022 | 0.16479 | 0.17395 | 0.11902 | 0.027466 | -0.10529 | 0.086975 | 0.18768 | 0.041199 | 0.027466 | 0.036621 | 0.041199 | -0.032043 | 122.3053 | 122.1725 | 0.032044 | 122.438 | 122.4518 | 0.27924 | 0.009155 | 122.319 | 122.2458 | -0.059509 | 122.3648 | 122.319 | 0.073242 | -0.050354 | 122.3969 | 122.374 | 122.4426 | -0.19226 | 122.3053 | 122.3145 | 122.4655 | -0.11902
1996.0625 | 122.5342 | -122.2961 | 0.1236 | -0.013122 | 0.073651 | 0.00090781 | 0.0028583 | 0.015528 | 0.0046485 | 0.00090584 | -0.0040437 | 0.030907 | -0.0097755 | 0.022879 | 0.0074641 | -0.008547 | 0.082397 | 0.059509 | 0.059509 | 0.12817 | 0.14648 | -0.009155 | -0.14191 | 0.059509 | 0.068665 | -0.086975 | 0.082397 | 0.068665 | 0.009155 | -0.054932 | 122.287 | 122.1542 | 0.022888 | 122.3557 | 122.4243 | 0.27008 | -0.041199 | 122.3053 | 122.2412 | -0.041199 | 122.3557 | 122.2092 | -0.032043 | -0.054931 | 122.4426 | 122.3785 | 122.3557 | -0.2655 | 122.3785 | 122.3648 | 122.3648 | -0.17853
1997.8125 | 122.4838 | -122.287 | 0.10529 | -0.013122 | 0.075573 | 0.00048061 | 0.0026447 | 0.014246 | 0.0040077 | 5.1244e-05 | -0.011673 | 0.028771 | -0.0095619 | 0.022665 | 0.0078913 | -0.010042 | 0.036621 | 0.054932 | 0.050354 | 0.10529 | 0.16022 | -0.004578 | -0.12817 | 0.032043 | 0.041199 | -0.10986 | 0.054932 | 0.073242 | 0.004578 | -0.059509 | 122.2824 | 122.1588 | 0.054931 | 122.3419 | 122.3923 | 0.23346 | -0.068665 | 122.2916 | 122.2275 | -0.050354 | 122.319 | 122.1771 | -0.050354 | -0.032044 | 122.4472 | 122.3236 | 122.3373 | -0.23346 | 122.3419 | 122.3602 | 122.3282 | -0.16479
1999.5625 | 122.4655 | -122.3007 | 0.1236 | -0.0054933 | 0.068524 | 0.0030442 | 0.0045673 | 0.010829 | -0.0051781 | -0.0012306 | -0.011673 | 0.02343 | -0.0095619 | 0.019675 | 0.0027643 | -0.0066244 | 0.054932 | 0.11902 | 0.13733 | 0.15106 | 0.13733 | 0.045776 | -0.091553 | 0.045776 | 0.10986 | 0 | 0.036621 | 0.036621 | 0.013733 | -0.045776 | 122.3465 | 122.2092 | 0.013733 | 122.4197 | 122.4518 | 0.24261 | -0.068664 | 122.3145 | 122.2549 | -0.086975 | 122.3465 | 122.3007 | 0.045776 | -0.086975 | 122.438 | 122.3557 | 122.438 | -0.21515 | 122.3373 | 122.3373 | 122.4106 | -0.16937
2001.2344 | 122.5708 | -122.2733 | 0.07782 | 0.0021362 | 0.075573 | 5.3406e-05 | 0.0075581 | 0.015742 | -0.0021875 | -0.0014442 | -0.011673 | 0.029198 | -0.0080665 | 0.024802 | 0.0010553 | -0.010042 | -0.027466 | -0.022888 | 0.004578 | 0.082397 | 0.1831 | 0.004578 | -0.13733 | -0.041199 | 0.027466 | -0.13275 | 0.091553 | 0.07782 | 0.004578 | -0.082397 | 122.2778 | 122.1359 | 0.10528 | 122.2504 | 122.3557 | 0.21973 | -0.10529 | 122.2778 | 122.1909 | 0.013733 | 122.2321 | 122.1405 | -0.050354 | 0 | 122.4564 | 122.2458 | 122.2778 | -0.21515 | 122.3648 | 122.3511 | 122.3007 | -0.16022
2002.9688 | 122.4701 | -122.3373 | 0.12817 | -0.0054933 | 0.074933 | 0.0015488 | 0.0017901 | 0.016383 | 0.0027259 | -0.0010168 | 0.0035858 | 0.028557 | -0.0080665 | 0.024588 | 0.0072505 | -0.0098288 | -0.032043 | -0.059509 | -0.018311 | 0.082397 | 0.17853 | 0.004578 | -0.13275 | -0.004578 | -0.022888 | -0.1236 | 0.054932 | 0.086975 | 0.013733 | -0.07782 | 122.3419 | 122.2046 | 0.050354 | 122.2778 | 122.4197 | 0.21515 | -0.16022 | 122.3511 | 122.2595 | -0.073242 | 122.3328 | 122.2137 | -0.045776 | -0.041199 | 122.5159 | 122.3053 | 122.319 | -0.26093 | 122.3923 | 122.4243 | 122.3145 | -0.20599
2004.7031 | 122.4976 | -122.2916 | 0.11444 | -0.0054933 | 0.072369 | 0.0024032 | 0.0028583 | 0.014887 | 0.0014441 | 5.1244e-05 | -0.0040437 | 0.028984 | -0.0095619 | 0.02352 | 0.0059687 | -0.0083334 | -0.009155 | -0.013733 | 0.004578 | 0.086975 | 0.16479 | -0.018311 | -0.14191 | 0 | 0.018311 | -0.10071 | 0.050354 | 0.068665 | 0.018311 | -0.054932 | 122.2733 | 122.1497 | 0.050354 | 122.2778 | 122.3785 | 0.22888 | -0.1236 | 122.3099 | 122.2366 | -0.064087 | 122.2916 | 122.1909 | -0.045776 | -0.045776 | 122.4564 | 122.2824 | 122.2961 | -0.25635 | 122.3419 | 122.3602 | 122.3099 | -0.16937
2006.4531 | 122.6212 | -122.2824 | 0.07782 | -0.013122 | 0.074505 | 0.00026701 | 0.0069171 | 0.015101 | 0.0025123 | -0.002085 | -0.011673 | 0.028343 | -0.0072119 | 0.022665 | 0.0034051 | -0.010256 | -0.018311 | 0 | 0.018311 | 0.09613 | 0.17395 | -0.009155 | -0.15564 | -0.009155 | 0.045776 | -0.10529 | 0.054932 | 0.086975 | 0.009155 | -0.086975 | 122.2733 | 122.1268 | 0.09613 | 122.2824 | 122.3785 | 0.25177 | -0.096131 | 122.2916 | 122.1954 | -0.022888 | 122.2733 | 122.1771 | -0.018311 | 0.009155 | 122.4564 | 122.2641 | 122.3007 | -0.23346 | 122.3373 | 122.3694 | 122.3282 | -0.16479
2008.125 | 122.5296 | -122.3053 | 0.11444 | -0.0054933 | 0.072369 | 0.0017624 | 0.0039265 | 0.014674 | 0.0012305 | 0.00026484 | 0.0035858 | 0.029198 | -0.0067847 | 0.023093 | 0.0044733 | -0.0072652 | 0 | 0 | 0.022888 | 0.09613 | 0.15564 | 0.018311 | -0.1236 | 0.045776 | 0.041199 | -0.068665 | 0.059509 | 0.054932 | 0.018311 | -0.059509 | 122.3236 | 122.1817 | 0.041199 | 122.3053 | 122.4014 | 0.21973 | -0.11444 | 122.3236 | 122.2458 | -0.054932 | 122.3511 | 122.2366 | -0.009156 | -0.059509 | 122.4609 | 122.3053 | 122.3282 | -0.23804 | 122.3648 | 122.3602 | 122.3465 | -0.17395
2009.875 | 122.5571 | -122.2961 | 0.086975 | -0.020752 | 0.070447 | 0.003685 | 0.0069171 | 0.01446 | -0.0071007 | -0.0010168 | -0.0040437 | 0.026207 | -0.010843 | 0.018607 | 0.0014825 | -0.0098288 | 0.054932 | 0.13733 | 0.16022 | 0.1831 | 0.11444 | 0.036621 | -0.09613 | 0.091553 | 0.1831 | 0.018311 | 0.022888 | 0.032043 | 0.045776 | -0.050354 | 122.3328 | 122.2 | 0.027466 | 122.4335 | 122.4792 | 0.27924 | -0.032043 | 122.3419 | 122.2458 | -0.064087 | 122.3877 | 122.3145 | 0.068665 | -0.054932 | 122.4106 | 122.3511 | 122.4564 | -0.1831 | 122.319 | 122.3282 | 122.4792 | -0.13733
2011.5625 | 122.4564 | -122.3236 | 0.11444 | -0.013122 | 0.067669 | 0.0038986 | 0.0041401 | 0.012324 | -0.0038965 | -0.0022986 | -0.011673 | 0.026207 | -0.012766 | 0.020316 | 0.0016963 | -0.0087606 | 0.064087 | 0.11444 | 0.1236 | 0.14648 | 0.13275 | 0.032043 | -0.10986 | 0.059509 | 0.11902 | -0.013733 | 0.036621 | 0.050354 | 0.032043 | -0.045776 | 122.3557 | 122.2137 | 0.01831 | 122.438 | 122.4701 | 0.25635 | -0.050354 | 122.3557 | 122.2778 | -0.07782 | 122.3831 | 122.3099 | 0.032043 | -0.064087 | 122.4564 | 122.3877 | 122.4472 | -0.2243 | 122.3602 | 122.374 | 122.4426 | -0.16022
2013.2344 | 122.5983 | -122.2733 | 0.07782 | -0.013122 | 0.074078 | -0.00037379 | 0.0079853 | 0.01446 | 0.0029395 | -0.0025122 | -0.0040437 | 0.030266 | -0.0091345 | 0.022025 | 0.0046869 | -0.011538 | 0.059509 | 0.036621 | 0.07782 | 0.1236 | 0.16479 | 0.032043 | -0.13275 | 0.045776 | 0.073242 | -0.082397 | 0.050354 | 0.086975 | 0.018311 | -0.068665 | 122.3053 | 122.1405 | 0.086975 | 122.3099 | 122.3969 | 0.25635 | -0.018311 | 122.2916 | 122.2046 | -0.027466 | 122.319 | 122.1909 | -0.013732 | 0.009155 | 122.438 | 122.3328 | 122.3511 | -0.21057 | 122.3236 | 122.3602 | 122.3465 | -0.14649
2014.9688 | 122.6028 | -122.2916 | 0.082397 | -0.0054933 | 0.074078 | 0.001976 | 0.0069171 | 0.017878 | 0.0016577 | -0.0025122 | -0.0040437 | 0.029839 | -0.0082801 | 0.023306 | 0.0016963 | -0.0089742 | -0.009155 | -0.018311 | 0.013733 | 0.091553 | 0.16479 | -0.018311 | -0.13275 | 0 | 0.041199 | -0.11444 | 0.082397 | 0.073242 | 0.009155 | -0.059509 | 122.2733 | 122.1588 | 0.082398 | 122.2733 | 122.3831 | 0.2243 | -0.091552 | 122.3007 | 122.2321 | 0 | 122.2916 | 122.1771 | -0.054932 | -0.009155 | 122.4564 | 122.2824 | 122.3053 | -0.21515 | 122.374 | 122.3648 | 122.3328 | -0.14191
2016.6562 | 122.4655 | -122.3282 | 0.1236 | -0.013122 | 0.069378 | 0.0034714 | 0.0045673 | 0.014887 | -0.0038965 | -0.0016578 | -0.011673 | 0.024285 | -0.0093481 | 0.023093 | 0.0036189 | -0.0083334 | 0.050354 | 0.10986 | 0.11902 | 0.14648 | 0.11444 | 0.032043 | -0.10071 | 0.054932 | 0.11444 | -0.004578 | 0.036621 | 0.036621 | 0.045776 | -0.041199 | 122.3602 | 122.2275 | -0.009155 | 122.438 | 122.4747 | 0.24719 | -0.073242 | 122.374 | 122.287 | -0.086975 | 122.3831 | 122.3236 | 0.036621 | -0.086975 | 122.4426 | 122.3785 | 122.4472 | -0.2243 | 122.3648 | 122.3648 | 122.4426 | -0.16479
2018.4062 | 122.6028 | -122.3145 | 0.091553 | -0.013122 | 0.074078 | -0.00058739 | 0.0056355 | 0.017237 | 0.0037939 | -0.003794 | 0.0035858 | 0.030907 | -0.0097755 | 0.023947 | 0.0081049 | -0.011751 | 0.050354 | 0.054932 | 0.054932 | 0.13275 | 0.17395 | 0.004578 | -0.14191 | 0.054932 | 0.07782 | -0.073242 | 0.059509 | 0.064087 | -0.004578 | -0.064087 | 122.319 | 122.1725 | 0.082397 | 122.3694 | 122.4472 | 0.27466 | -0.041199 | 122.3099 | 122.2504 | -0.032044 | 122.3694 | 122.2412 | -0.009155 | -0.027466 | 122.4884 | 122.3648 | 122.3694 | -0.23346 | 122.374 | 122.3785 | 122.3923 | -0.15564
2020.1406 | 122.6166 | -122.3145 | 0.091553 | 0.0021362 | 0.073864 | 0.0015488 | 0.0086261 | 0.015101 | -0.00090574 | -0.0031532 | 0.0035858 | 0.029198 | -0.0065711 | 0.023306 | 0.0027643 | -0.010683 | -0.027466 | -0.013733 | 0.009155 | 0.091553 | 0.16937 | 0 | -0.14648 | -0.045776 | 0.018311 | -0.10986 | 0.082397 | 0.07782 | 0 | -0.082397 | 122.3145 | 122.168 | 0.07782 | 122.3007 | 122.406 | 0.23804 | -0.11902 | 122.3145 | 122.2321 | -0.009156 | 122.2687 | 122.2046 | -0.027466 | -0.013733 | 122.4838 | 122.287 | 122.3236 | -0.23804 | 122.3969 | 122.3923 | 122.3328 | -0.17395
2021.8906 | 122.4838 | -122.3328 | 0.11444 | -0.020752 | 0.072155 | 0.0034714 | 0.0043537 | 0.014246 | -0.0045373 | 0.00026484 | -0.0040437 | 0.025566 | -0.010416 | 0.020956 | 0.0025507 | -0.0064108 | 0.004578 | 0.073242 | 0.086975 | 0.1236 | 0.12817 | 0.032043 | -0.091553 | 0.027466 | 0.07782 | -0.022888 | 0.032043 | 0.032043 | 0.022888 | -0.036621 | 122.3648 | 122.2412 | 0.013733 | 122.406 | 122.4564 | 0.21515 | -0.10986 | 122.3557 | 122.2961 | -0.082398 | 122.3602 | 122.3099 | 0.013733 | -0.082398 | 122.4609 | 122.3373 | 122.4197 | -0.20599 | 122.3648 | 122.3648 | 122.4106 | -0.15106
2023.5781 | 122.5296 | -122.3328 | 0.11444 | -0.0054933 | 0.071515 | 0.0017624 | 0.0034991 | 0.013392 | 0.0042213 | -0.0014442 | -0.011673 | 0.029198 | -0.0099891 | 0.025443 | 0.0046869 | -0.0089742 | -0.013733 | -0.050354 | -0.009155 | 0.09613 | 0.16937 | 0 | -0.12817 | -0.018311 | -0.022888 | -0.12817 | 0.068665 | 0.064087 | -0.009155 | -0.07782 | 122.3328 | 122.2046 | 0.054932 | 122.2824 | 122.4289 | 0.2243 | -0.12817 | 122.3236 | 122.2549 | -0.045776 | 122.3145 | 122.2046 | -0.050354 | -0.050354 | 122.5021 | 122.319 | 122.3236 | -0.24262 | 122.4014 | 122.3969 | 122.3099 | -0.19226
2025.3125 | 122.525 | -122.3328 | 0.10986 | -0.013122 | 0.072583 | 0.001976 | 0.00050847 | 0.015742 | 0.0018713 | 0.00026484 | -0.011673 | 0.031761 | -0.011271 | 0.021811 | 0.0057551 | -0.01047 | -0.013733 | -0.018311 | -0.013733 | 0.086975 | 0.17853 | -0.013733 | -0.12817 | -0.009155 | -0.013733 | -0.13275 | 0.068665 | 0.082397 | 0 | -0.073242 | 122.319 | 122.2046 | 0.068665 | 122.3145 | 122.4197 | 0.21515 | -0.1236 | 122.3328 | 122.2595 | -0.041198 | 122.3236 | 122.2 | -0.059509 | -0.027466 | 122.5113 | 122.319 | 122.319 | -0.23804 | 122.4014 | 122.4152 | 122.319 | -0.18311
2027.0469 | 122.5845 | -122.3053 | 0.09613 | -0.0054933 | 0.068738 | 0.0038986 | 0.0049945 | 0.012538 | -0.0068871 | -0.0010168 | -0.0040437 | 0.024285 | -0.0095619 | 0.019034 | 0.0012689 | -0.0081198 | 0.004578 | 0.064087 | 0.09613 | 0.14648 | 0.14191 | 0.036621 | -0.10071 | 0.050354 | 0.10529 | 0.018311 | 0.059509 | 0.036621 | 0.027466 | -0.050354 | 122.3419 | 122.2046 | 0.045777 | 122.3694 | 122.4518 | 0.24719 | -0.091552 | 122.3328 | 122.2549 | -0.036621 | 122.3557 | 122.3236 | 0.068665 | -0.059509 | 122.4472 | 122.3099 | 122.4014 | -0.19684 | 122.3648 | 122.3419 | 122.4106 | -0.14648
2028.7969 | 122.5433 | -122.3282 | 0.09613 | -0.013122 | 0.067456 | 0.003685 | 0.0064899 | 0.015955 | -0.0047509 | -0.0018714 | 0.0035858 | 0.023216 | -0.010203 | 0.020743 | 0.00062806 | -0.0094016 | 0.018311 | 0.041199 | 0.09613 | 0.13733 | 0.13733 | 0.036621 | -0.10529 | 0.027466 | 0.07782 | -0.027466 | 0.050354 | 0.059509 | 0.027466 | -0.041199 | 122.3648 | 122.2229 | 0.041199 | 122.3694 | 122.4655 | 0.24262 | -0.077819 | 122.3557 | 122.287 | -0.045776 | 122.3557 | 122.3007 | 0.013733 | -0.036621 | 122.4655 | 122.3465 | 122.4243 | -0.20142 | 122.3785 | 122.3877 | 122.406 | -0.13733
2030.4688 | 122.5983 | -122.3145 | 0.086975 | -0.0054933 | 0.070874 | 0.0015488 | 0.0054217 | 0.016596 | -0.0043237 | -0.0012306 | -0.011673 | 0.026207 | -0.010203 | 0.020102 | 0.0016963 | -0.0079062 | 0.11444 | 0.13275 | 0.15106 | 0.17395 | 0.13275 | 0.022888 | -0.11444 | 0.10986 | 0.17853 | 0.027466 | 0.013733 | 0.059509 | 0.036621 | -0.036621 | 122.3373 | 122.2 | 0.045776 | 122.4472 | 122.4884 | 0.28839 | 0.027466 | 122.3511 | 122.2778 | -0.073242 | 122.4243 | 122.3419 | 0.064087 | -0.027466 | 122.4472 | 122.4289 | 122.4655 | -0.20142 | 122.3282 | 122.374 | 122.493 | -0.1236
2032.2031 | 122.5662 | -122.3236 | 0.10071 | -0.0054933 | 0.073651 | -0.00058739 | 0.0041401 | 0.015528 | -0.0011193 | -0.0027258 | -0.0040437 | 0.027703 | -0.0089209 | 0.022879 | 0.0031915 | -0.010256 | 0.073242 | 0.10529 | 0.12817 | 0.15564 | 0.12817 | 0.022888 | -0.10529 | 0.036621 | 0.11902 | -0.050354 | 0.041199 | 0.068665 | 0.013733 | -0.054932 | 122.3465 | 122.2183 | 0.027466 | 122.4289 | 122.4792 | 0.26093 | -0.027466 | 122.3373 | 122.2687 | -0.059509 | 122.3602 | 122.2733 | 0.004578 | -0.032043 | 122.4518 | 122.3968 | 122.4518 | -0.20599 | 122.3648 | 122.3923 | 122.4426 | -0.15564
2033.9531 | 122.5754 | -122.319 | 0.09613 | -0.0054933 | 0.071728 | 0.00090781 | 0.0060627 | 0.016383 | -0.00069214 | -0.002085 | -0.011673 | 0.028771 | -0.0097755 | 0.022025 | 0.0031915 | -0.011111 | 0.041199 | 0.050354 | 0.073242 | 0.11902 | 0.16022 | -0.004578 | -0.1236 | -0.009155 | 0.041199 | -0.10529 | 0.068665 | 0.073242 | 0.018311 | -0.07782 | 122.3145 | 122.1954 | 0.064087 | 122.3694 | 122.438 | 0.24261 | -0.054931 | 122.3373 | 122.2412 | -0.027465 | 122.3099 | 122.2137 | -0.027466 | -0.022888 | 122.4792 | 122.3602 | 122.3923 | -0.21973 | 122.3877 | 122.3923 | 122.3602 | -0.17395
2035.625 | 122.5021 | -122.3511 | 0.13733 | 0.0021362 | 0.074719 | -0.0018692 | 0.0032855 | 0.015742 | 0.0052893 | 0.00069204 | -0.011673 | 0.032189 | -0.0097755 | 0.022665 | 0.0063959 | -0.0091878 | 0.045776 | 0.022888 | 0.032043 | 0.10071 | 0.16479 | 0.009155 | -0.12817 | 0.041199 | 0.009155 | -0.12817 | 0.054932 | 0.054932 | 0.013733 | -0.073242 | 122.3602 | 122.2229 | 0.027466 | 122.374 | 122.4518 | 0.22888 | -0.091553 | 122.3648 | 122.2778 | -0.082397 | 122.3923 | 122.2229 | -0.054932 | -0.082397 | 122.5159 | 122.3969 | 122.3831 | -0.2655 | 122.406 | 122.406 | 122.3602 | -0.21057
2037.3906 | 122.5754 | -122.3145 | 0.091553 | -0.013122 | 0.073651 | 0.0024032 | 0.0081989 | 0.016383 | -0.0024011 | -0.0012306 | -0.0040437 | 0.025566 | -0.0080665 | 0.022238 | 0.0019099 | -0.0089742 | 0.036621 | 0.064087 | 0.064087 | 0.13275 | 0.15106 | 0 | -0.12817 | 0.018311 | 0.07782 | -0.091553 | 0.064087 | 0.073242 | 0.004578 | -0.073242 | 122.3145 | 122.1863 | 0.059509 | 122.3785 | 122.4472 | 0.26093 | -0.054932 | 122.319 | 122.2412 | -0.027466 | 122.3328 | 122.2229 | -0.018311 | -0.018311 | 122.4655 | 122.3511 | 122.3785 | -0.21973 | 122.3785 | 122.3877 | 122.3923 | -0.16479
2039.0625 | 122.5067 | -122.374 | 0.11902 | -0.020752 | 0.074078 | 0.0021896 | 0.0039265 | 0.016596 | 0.0040077 | -0.00037596 | -0.019302 | 0.031548 | -0.0095619 | 0.023734 | 0.0059687 | -0.0087606 | -0.004578 | -0.041199 | -0.013733 | 0.09613 | 0.16022 | 0 | -0.1236 | 0 | -0.018311 | -0.15106 | 0.064087 | 0.073242 | 0 | -0.073242 | 122.374 | 122.2504 | 0.041198 | 122.3328 | 122.4701 | 0.21973 | -0.1236 | 122.374 | 122.3007 | -0.054932 | 122.374 | 122.2229 | -0.07782 | -0.045777 | 122.5342 | 122.3694 | 122.3602 | -0.24261 | 122.438 | 122.4472 | 122.3557 | -0.19226
2040.7969 | 122.5571 | -122.3602 | 0.13275 | -0.0054933 | 0.071301 | 0.0030442 | 0.0026447 | 0.014887 | 0.00016226 | -0.0016578 | -0.011673 | 0.028984 | -0.010203 | 0.022238 | 0.0063959 | -0.0072652 | -0.013733 | -0.036621 | -0.013733 | 0.086975 | 0.17853 | 0 | -0.13733 | 0 | -0.013733 | -0.10986 | 0.082397 | 0.073242 | 0.013733 | -0.086975 | 122.3602 | 122.2229 | 0.045777 | 122.3236 | 122.4472 | 0.2243 | -0.14648 | 122.374 | 122.2733 | -0.050354 | 122.3602 | 122.2504 | -0.022888 | -0.059509 | 122.5388 | 122.3465 | 122.3465 | -0.27008 | 122.4426 | 122.4335 | 122.3465 | -0.21973
2042.5 | 122.5845 | -122.3373 | 0.091553 | -0.0054933 | 0.071728 | 0.0038986 | 0.0094807 | 0.01681 | -0.0038965 | 0.00069204 | -0.0040437 | 0.025566 | -0.01063 | 0.020743 | 0.0021235 | -0.0091878 | 0.082397 | 0.14191 | 0.16022 | 0.18768 | 0.11902 | 0.032043 | -0.10071 | 0.07782 | 0.16937 | 0.013733 | 0.036621 | 0.041199 | 0.050354 | -0.032043 | 122.3694 | 122.2366 | 0.027466 | 122.4792 | 122.525 | 0.28839 | -0.009156 | 122.3877 | 122.3053 | -0.054932 | 122.4152 | 122.3511 | 0.045776 | -0.050354 | 122.4564 | 122.4197 | 122.4976 | -0.19226 | 122.374 | 122.3785 | 122.5067 | -0.1236
2044.25 | 122.6395 | -122.3282 | 0.09613 | -0.020752 | 0.073224 | 0.0013352 | 0.0039265 | 0.015528 | 0.0055029 | -0.00037596 | 0.0035858 | 0.029198 | -0.0078529 | 0.024374 | 0.0055415 | -0.010897 | 0.045776 | 0.045776 | 0.041199 | 0.12817 | 0.16479 | 0.022888 | -0.1236 | 0.045776 | 0.082397 | -0.064087 | 0.032043 | 0.064087 | 0.009155 | -0.068665 | 122.3511 | 122.2046 | 0.068665 | 122.374 | 122.4564 | 0.25177 | -0.050354 | 122.3373 | 122.2595 | -0.064087 | 122.374 | 122.2641 | 0.004578 | -0.032043 | 122.493 | 122.374 | 122.3694 | -0.21973 | 122.3602 | 122.3923 | 122.4106 | -0.16479
2046 | 122.5204 | -122.374 | 0.11444 | -0.020752 | 0.074292 | 0.0032578 | 0.00072207 | 0.015742 | 0.0025123 | 0.00047844 | -0.011673 | 0.028984 | -0.010843 | 0.023734 | 0.0068231 | -0.008547 | -0.013733 | -0.041199 | -0.009155 | 0.07782 | 0.15106 | 0.013733 | -0.10986 | -0.013733 | -0.036621 | -0.13275 | 0.064087 | 0.073242 | -0.009155 | -0.068665 | 122.3877 | 122.2641 | 0.036621 | 122.3328 | 122.4518 | 0.18768 | -0.12817 | 122.3648 | 122.3053 | -0.050354 | 122.3602 | 122.2412 | -0.064086 | -0.041199 | 122.525 | 122.3602 | 122.3648 | -0.2243 | 122.438 | 122.4472 | 122.3373 | -0.18311
2047.6719 | 122.5891 | -122.3557 | 0.09613 | -0.0054933 | 0.07301 | 0.001976 | 0.0079853 | 0.01681 | -0.0028283 | -0.00058956 | -0.0040437 | 0.026421 | -0.0099891 | 0.02117 | 0.00062806 | -0.0081198 | 0.041199 | 0.09613 | 0.1236 | 0.16479 | 0.14191 | 0.050354 | -0.09613 | 0.027466 | 0.11444 | -0.054932 | 0.036621 | 0.073242 | 0.027466 | -0.064087 | 122.406 | 122.2595 | 0.045777 | 122.4518 | 122.5204 | 0.26092 | -0.054931 | 122.3831 | 122.2916 | -0.059509 | 122.3831 | 122.3007 | 0.009155 | -0.022888 | 122.4976 | 122.3969 | 122.4792 | -0.19226 | 122.3923 | 122.4289 | 122.4701 | -0.16022
2049.4219 | 122.5891 | -122.3419 | 0.10071 | -0.020752 | 0.074933 | 0.00026701 | 0.0045673 | 0.017878 | 0.0029395 | 0.001333 | -0.0040437 | 0.027916 | -0.010416 | 0.023093 | 0.0068231 | -0.0087606 | 0.064087 | 0.059509 | 0.073242 | 0.13275 | 0.15106 | 0 | -0.12817 | 0.032043 | 0.07782 | -0.068665 | 0.059509 | 0.064087 | 0.018311 | -0.073242 | 122.3419 | 122.2137 | 0.050354 | 122.4014 | 122.4747 | 0.26093 | -0.036621 | 122.3602 | 122.2687 | -0.041199 | 122.374 | 122.2733 | 0.004577 | -0.036621 | 122.493 | 122.406 | 122.4152 | -0.22888 | 122.4014 | 122.406 | 122.4197 | -0.17395
2051.1562 | 122.5159 | -122.3877 | 0.13733 | 0.0021362 | 0.074933 | 0.00048061 | 0.0067035 | 0.016596 | 0.0016577 | -0.0018714 | 0.0035858 | 0.029412 | -0.0065711 | 0.02352 | 0.0055415 | -0.0091878 | 0.013733 | -0.004578 | 0.022888 | 0.10986 | 0.16022 | 0.018311 | -0.13275 | -0.009155 | 0.013733 | -0.13733 | 0.059509 | 0.082397 | 0 | -0.068665 | 122.406 | 122.2549 | 0.022888 | 122.3831 | 122.4976 | 0.24261 | -0.1236 | 122.3877 | 122.319 | -0.07782 | 122.3785 | 122.2504 | -0.068664 | -0.054932 | 122.5479 | 122.4014 | 122.4106 | -0.27008 | 122.4472 | 122.4701 | 122.4014 | -0.20599
2052.9062 | 122.6212 | -122.3373 | 0.082397 | -0.0054933 | 0.072796 | 0.00048061 | 0.0077717 | 0.014887 | -0.0026147 | -0.0022986 | -0.0040437 | 0.027703 | -0.0076393 | 0.024374 | 0.00041446 | -0.0094016 | -0.027466 | -0.004578 | 0.027466 | 0.082397 | 0.17395 | 0 | -0.14191 | -0.041199 | 0.041199 | -0.11444 | 0.068665 | 0.091553 | -0.009155 | -0.073242 | 122.3373 | 122.1954 | 0.091553 | 122.3328 | 122.4197 | 0.2243 | -0.10986 | 122.3282 | 122.2641 | -0.013732 | 122.2961 | 122.2229 | -0.041199 | 0.009156 | 122.5113 | 122.3099 | 122.3648 | -0.2243 | 122.406 | 122.4289 | 122.3785 | -0.15564
2054.5781 | 122.5662 | -122.3557 | 0.1236 | -0.0054933 | 0.073864 | -0.00058739 | 0.0013629 | 0.016383 | -0.00047854 | 5.1244e-05 | -0.011673 | 0.030266 | -0.0087073 | 0.023306 | 0.0057551 | -0.0089742 | -0.009155 | -0.022888 | 0.009155 | 0.082397 | 0.19684 | 0.004578 | -0.1236 | 0.009155 | 0.013733 | -0.09613 | 0.050354 | 0.07782 | 0.018311 | -0.064087 | 122.3602 | 122.2321 | 0.073242 | 122.3328 | 122.438 | 0.20599 | -0.13275 | 122.374 | 122.2916 | -0.073242 | 122.3648 | 122.2595 | -0.032043 | -0.045776 | 122.5525 | 122.3465 | 122.3648 | -0.24719 | 122.406 | 122.4335 | 122.3694 | -0.18768
2056.3281 | 122.6349 | -122.3099 | 0.07782 | -0.013122 | 0.072369 | 0.0043258 | 0.0075581 | 0.016383 | -0.0071007 | -0.0027258 | 0.0035858 | 0.025566 | -0.0065711 | 0.020743 | -0.00022634 | -0.0087606 | 0.054932 | 0.14191 | 0.13275 | 0.17395 | 0.12817 | 0.032043 | -0.073242 | 0.073242 | 0.17853 | 0.045776 | 0.022888 | 0.032043 | 0.027466 | -0.022888 | 122.3419 | 122.2366 | 0.050354 | 122.4518 | 122.4838 | 0.24719 | -0.022888 | 122.3373 | 122.287 | -0.054932 | 122.3831 | 122.3557 | 0.068664 | -0.045777 | 122.438 | 122.3648 | 122.4426 | -0.15106 | 122.3328 | 122.3419 | 122.4884 | -0.10071
2058.0781 | 122.6486 | -122.3419 | 0.086975 | -0.0054933 | 0.075146 | 0.0028306 | 0.0062763 | 0.015101 | 0.0027259 | -0.0031532 | 0.0035858 | 0.030052 | -0.0072119 | 0.023306 | 0.0055415 | -0.010256 | 0.004578 | -0.009155 | 0.018311 | 0.11902 | 0.17853 | 0.009155 | -0.13275 | 0.018311 | 0.054932 | -0.07782 | 0.073242 | 0.073242 | 0 | -0.054932 | 122.3511 | 122.2092 | 0.091553 | 122.3328 | 122.4609 | 0.25177 | -0.082397 | 122.3419 | 122.287 | -0.013733 | 122.3602 | 122.2641 | -0.022888 | -0.013733 | 122.5204 | 122.3465 | 122.3602 | -0.21973 | 122.4152 | 122.4152 | 122.3969 | -0.14191
2059.8281 | 122.5159 | -122.3465 | 0.10529 | -0.0054933 | 0.066601 | 0.0017624 | 0.0028583 | 0.014033 | -0.0028283 | -0.0022986 | -0.011673 | 0.022576 | -0.012125 | 0.022238 | 0.0051141 | -0.0087606 | 0.027466 | 0.086975 | 0.1236 | 0.13275 | 0.13275 | 0.054932 | -0.09613 | 0.036621 | 0.082397 | -0.013733 | 0.041199 | 0.045776 | 0.041199 | -0.059509 | 122.4014 | 122.2504 | 0.027465 | 122.4335 | 122.4792 | 0.22888 | -0.07782 | 122.3877 | 122.287 | -0.064087 | 122.3831 | 122.3328 | 0.045776 | -0.05951 | 122.4792 | 122.374 | 122.4701 | -0.20142 | 122.3877 | 122.3923 | 122.4289 | -0.16479
2061.5156 | 122.5708 | -122.3557 | 0.1236 | -0.013122 | 0.074292 | -0.00016019 | 0.0056355 | 0.014674 | 0.0031531 | -0.0010168 | -0.011673 | 0.032402 | -0.0091345 | 0.023947 | 0.0031915 | -0.010683 | 0.082397 | 0.041199 | 0.073242 | 0.12817 | 0.16479 | 0.013733 | -0.12817 | 0.041199 | 0.054932 | -0.09613 | 0.064087 | 0.082397 | 0.013733 | -0.07782 | 122.3694 | 122.2275 | 0.041199 | 122.3969 | 122.4838 | 0.25635 | -0.041199 | 122.3694 | 122.2778 | -0.059509 | 122.3969 | 122.2595 | -0.01831 | -0.041199 | 122.5204 | 122.438 | 122.4289 | -0.25177 | 122.4197 | 122.438 | 122.4106 | -0.20142
2063.2656 | 122.5616 | -122.3602 | 0.11444 | -0.013122 | 0.068097 | 0.0043258 | 0.0060627 | 0.015315 | -0.0034691 | -0.0031532 | -0.0040437 | 0.02578 | -0.011057 | 0.019675 | 0.0012689 | -0.0081198 | 0.009155 | 0.045776 | 0.091553 | 0.13733 | 0.13275 | 0.045776 | -0.091553 | 0.022888 | 0.086975 | -0.009155 | 0.036621 | 0.050354 | 0.027466 | -0.050354 | 122.406 | 122.2687 | 0.01831 | 122.406 | 122.4976 | 0.22888 | -0.10529 | 122.3877 | 122.3099 | -0.07782 | 122.3831 | 122.3511 | 0.041199 | -0.064087 | 122.493 | 122.3694 | 122.4518 | -0.20599 | 122.3969 | 122.4106 | 122.4472 | -0.16479
2065.0156 | 122.5983 | -122.3511 | 0.09613 | -0.013122 | 0.071087 | 0.001976 | 0.0071307 | 0.015315 | -0.0034691 | -0.0031532 | -0.011673 | 0.026421 | -0.011271 | 0.019247 | 0.0021235 | -0.01047 | 0.082397 | 0.1236 | 0.15106 | 0.1831 | 0.14191 | 0.045776 | -0.09613 | 0.082397 | 0.16479 | 0.004578 | 0.027466 | 0.050354 | 0.027466 | -0.032043 | 122.3969 | 122.2549 | 0.045777 | 122.4747 | 122.5342 | 0.27924 | -0.013733 | 122.3785 | 122.319 | -0.068664 | 122.4335 | 122.3557 | 0.036621 | -0.045776 | 122.493 | 122.4335 | 122.5021 | -0.19226 | 122.3785 | 122.4014 | 122.5159 | -0.12817
2066.7031 | 122.6395 | -122.3465 | 0.091553 | -0.0054933 | 0.067883 | 0.0030442 | 0.0039265 | 0.013819 | -0.0024011 | -0.0010168 | -0.011673 | 0.026421 | -0.011057 | 0.02117 | 0.0012689 | -0.010042 | 0.027466 | 0.054932 | 0.09613 | 0.13733 | 0.13275 | 0.032043 | -0.10071 | 0.064087 | 0.10071 | 0.009155 | 0.036621 | 0.050354 | 0.041199 | -0.036621 | 122.3785 | 122.2458 | 0.041198 | 122.4014 | 122.4838 | 0.23804 | -0.064087 | 122.3877 | 122.3099 | -0.054932 | 122.4106 | 122.3557 | 0.045776 | -0.041199 | 122.4792 | 122.374 | 122.4426 | -0.19226 | 122.3831 | 122.3969 | 122.4472 | -0.12817
2068.4531 | 122.5021 | -122.3877 | 0.10071 | 0.0021362 | 0.067029 | 0.0021896 | 0.0026447 | 0.014674 | -0.0017603 | -0.0012306 | -0.019302 | 0.02578 | -0.0095619 | 0.020743 | 0.0044733 | -0.0066244 | 0.086975 | 0.091553 | 0.11902 | 0.15564 | 0.11902 | 0.032043 | -0.086975 | 0.07782 | 0.09613 | -0.013733 | 0.041199 | 0.018311 | 0.036621 | -0.022888 | 122.4197 | 122.3007 | 0.018311 | 122.4792 | 122.5433 | 0.24261 | -0.013733 | 122.4243 | 122.3648 | -0.059509 | 122.4655 | 122.374 | 0.009155 | -0.082397 | 122.5067 | 122.4747 | 122.5067 | -0.18768 | 122.4289 | 122.406 | 122.4838 | -0.1236
2070.125 | 122.644 | -122.3511 | 0.086975 | -0.013122 | 0.069806 | 0.00090781 | 0.0039265 | 0.01446 | -0.0041101 | -0.0022986 | -0.011673 | 0.02578 | -0.011698 | 0.020316 | 0.00020086 | -0.011324 | 0.11902 | 0.14648 | 0.17853 | 0.18768 | 0.12817 | 0.041199 | -0.086975 | 0.10529 | 0.17395 | 0.027466 | 0.041199 | 0.045776 | 0.022888 | -0.041199 | 122.3923 | 122.2641 | 0.041199 | 122.4976 | 122.5388 | 0.27466 | 0.032044 | 122.374 | 122.3099 | -0.045776 | 122.4564 | 122.3785 | 0.068665 | -0.041199 | 122.4792 | 122.4701 | 122.5296 | -0.17395 | 122.3923 | 122.3969 | 122.525 | -0.12817
2071.8594 | 122.612 | -122.3557 | 0.10071 | -0.0054933 | 0.076214 | 0.0011216 | 0.0056355 | 0.014674 | 0.0076391 | 0.00047844 | -0.0040437 | 0.032189 | -0.0097755 | 0.023734 | 0.0059687 | -0.01047 | 0.09613 | 0.036621 | 0.050354 | 0.14191 | 0.17395 | 0.022888 | -0.14191 | 0.073242 | 0.064087 | -0.10529 | 0.068665 | 0.068665 | 0 | -0.054932 | 122.3785 | 122.2137 | 0.073242 | 122.3923 | 122.4976 | 0.28381 | -0.004578 | 122.3557 | 122.3007 | -0.032043 | 122.4289 | 122.2504 | -0.050354 | -0.032043 | 122.5296 | 122.4518 | 122.406 | -0.24262 | 122.4243 | 122.4243 | 122.4197 | -0.15564
2073.6094 | 122.612 | -122.3557 | 0.10529 | 0.0021362 | 0.072369 | 0.0028306 | 0.0047809 | 0.013392 | -0.0026147 | -0.0012306 | -0.0040437 | 0.025353 | -0.010843 | 0.019034 | 0.0016963 | -0.0089742 | 0.068665 | 0.10986 | 0.12817 | 0.16479 | 0.13733 | 0.032043 | -0.091553 | 0.050354 | 0.11444 | -0.045776 | 0.059509 | 0.045776 | 0.013733 | -0.068665 | 122.3877 | 122.2641 | 0.032043 | 122.4655 | 122.5204 | 0.25635 | -0.036621 | 122.3694 | 122.287 | -0.045777 | 122.406 | 122.3099 | 0.022889 | -0.05951 | 122.493 | 122.4243 | 122.4838 | -0.19684 | 122.4152 | 122.4014 | 122.4701 | -0.17395
2075.3438 | 122.5571 | -122.3831 | 0.09613 | -0.013122 | 0.074078 | 0.0013352 | 0.0045673 | 0.016383 | 0.0052893 | -0.00058956 | 0.0035858 | 0.030693 | -0.0087073 | 0.023093 | 0.0078913 | -0.010256 | 0.041199 | 0.045776 | 0.032043 | 0.11444 | 0.15106 | 0.004578 | -0.1236 | 0.036621 | 0.045776 | -0.10071 | 0.059509 | 0.07782 | 0.009155 | -0.073242 | 122.3877 | 122.2595 | 0.054932 | 122.4289 | 122.4976 | 0.23804 | -0.054931 | 122.3923 | 122.3099 | -0.036621 | 122.4197 | 122.2824 | -0.027466 | -0.01831 | 122.5342 | 122.4243 | 122.4152 | -0.21973 | 122.4426 | 122.4609 | 122.4289 | -0.16937
2077.0938 | 122.6669 | -122.3602 | 0.082397 | -0.013122 | 0.07066 | 0.0017624 | 0.0034991 | 0.016596 | 0.0037939 | 5.1244e-05 | -0.011673 | 0.030266 | -0.011271 | 0.020743 | 0.0072505 | -0.0081198 | 0.027466 | 0.045776 | 0.036621 | 0.1236 | 0.17395 | 0.022888 | -0.13275 | 0.036621 | 0.064087 | -0.07782 | 0.059509 | 0.054932 | 0.022888 | -0.050354 | 122.3831 | 122.2275 | 0.091553 | 122.406 | 122.4838 | 0.25635 | -0.054931 | 122.3831 | 122.3099 | -0.022888 | 122.3969 | 122.2824 | -0.027466 | -0.027465 | 122.5342 | 122.3877 | 122.3969 | -0.21515 | 122.4197 | 122.4152 | 122.4243 | -0.13275
2078.7812 | 122.6028 | -122.3694 | 0.11444 | -0.0054933 | 0.07536 | -0.00016019 | 0.0067035 | 0.013819 | 0.0037939 | 5.1244e-05 | -0.019302 | 0.028771 | -0.0074255 | 0.023093 | 0.0046869 | -0.0089742 | 0.059509 | 0.068665 | 0.068665 | 0.14191 | 0.15106 | 0 | -0.11444 | 0.032043 | 0.073242 | -0.09613 | 0.059509 | 0.054932 | 0.018311 | -0.059509 | 122.3694 | 122.2549 | 0.036621 | 122.438 | 122.5113 | 0.25635 | -0.054932 | 122.3877 | 122.3099 | -0.054932 | 122.4014 | 122.2733 | -0.036621 | -0.059509 | 122.5204 | 122.4289 | 122.438 | -0.22888 | 122.4289 | 122.4243 | 122.4426 | -0.17395
2080.5312 | 122.6852 | -122.374 | 0.073242 | -0.020752 | 0.073864 | 0.001976 | 0.0060627 | 0.011897 | 0.00058966 | -0.00058956 | -0.019302 | 0.028557 | -0.0087073 | 0.019034 | 0.0019099 | -0.0098288 | -0.018311 | 0.018311 | 0.022888 | 0.11902 | 0.17395 | 0.004578 | -0.14648 | 0.018311 | 0.068665 | -0.082397 | 0.07782 | 0.064087 | 0.009155 | -0.068665 | 122.3785 | 122.2275 | 0.10071 | 122.3923 | 122.493 | 0.2655 | -0.091553 | 122.3831 | 122.3053 | 0.004578 | 122.3923 | 122.2916 | -0.013732 | -0.009155 | 122.5479 | 122.3557 | 122.3969 | -0.21973 | 122.4518 | 122.438 | 122.4426 | -0.14191
2082.2656 | 122.612 | -122.374 | 0.10071 | -0.0054933 | 0.067883 | 0.0021896 | 0.0045673 | 0.016383 | -0.0032555 | 5.1244e-05 | -0.0040437 | 0.025994 | -0.010416 | 0.020102 | 0.0027643 | -0.006838 | -0.009155 | 0.050354 | 0.032043 | 0.11444 | 0.16937 | 0.018311 | -0.13275 | -0.027466 | 0.050354 | -0.10071 | 0.068665 | 0.082397 | 0.009155 | -0.082397 | 122.3923 | 122.2412 | 0.068665 | 122.4243 | 122.4884 | 0.24719 | -0.10986 | 122.3831 | 122.2916 | -0.032043 | 122.3465 | 122.2733 | -0.018311 | -0.018311 | 122.5433 | 122.3648 | 122.406 | -0.23346 | 122.4426 | 122.4564 | 122.4243 | -0.18311
2083.9375 | 122.6395 | -122.3511 | 0.086975 | -0.013122 | 0.067029 | 0.0030442 | 0.0073443 | 0.014887 | -0.0077417 | -0.0014442 | -0.0040437 | 0.024071 | -0.0091345 | 0.019888 | -0.00086734 | -0.0053426 | 0 | 0.064087 | 0.091553 | 0.14191 | 0.14648 | 0.036621 | -0.091553 | 0.054932 | 0.11444 | 0.004578 | 0.036621 | 0.054932 | 0.045776 | -0.022888 | 122.3877 | 122.2595 | 0.059509 | 122.4152 | 122.493 | 0.23346 | -0.086975 | 122.3969 | 122.3282 | -0.050354 | 122.406 | 122.3557 | 0.027466 | -0.032043 | 122.4976 | 122.3511 | 122.4426 | -0.17853 | 122.3877 | 122.406 | 122.4655 | -0.10986
2085.6875 | 122.5479 | -122.3969 | 0.1236 | -0.013122 | 0.071942 | 0.0015488 | 0.0090533 | 0.012965 | -0.0026147 | -0.003794 | -0.019302 | 0.027062 | -0.01063 | 0.020316 | 0.0019099 | -0.0079062 | 0.041199 | 0.091553 | 0.11444 | 0.1236 | 0.13275 | 0.041199 | -0.086975 | 0.041199 | 0.091553 | -0.022888 | 0.027466 | 0.041199 | 0.045776 | -0.041199 | 122.4381 | 122.3099 | 0.009155 | 122.4884 | 122.5204 | 0.21057 | -0.082397 | 122.4426 | 122.3557 | -0.09613 | 122.4381 | 122.374 | 0.018311 | -0.082397 | 122.5296 | 122.4381 | 122.5113 | -0.21057 | 122.4243 | 122.4381 | 122.4884 | -0.16479
2087.4531 | 122.5708 | -122.3923 | 0.1236 | -0.020752 | 0.07536 | 5.3406e-05 | 0.0064899 | 0.016169 | 0.0029395 | -0.00080316 | -0.011673 | 0.032402 | -0.0074255 | 0.022665 | 0.0016963 | -0.012179 | 0 | -0.050354 | -0.009155 | 0.086975 | 0.16022 | -0.009155 | -0.13275 | 0 | -0.018311 | -0.14191 | 0.064087 | 0.073242 | 0.013733 | -0.073242 | 122.3831 | 122.2595 | 0.036621 | 122.3419 | 122.4792 | 0.21973 | -0.1236 | 122.406 | 122.319 | -0.059509 | 122.3923 | 122.2504 | -0.068665 | -0.050354 | 122.5525 | 122.3923 | 122.3831 | -0.25635 | 122.4564 | 122.4655 | 122.374 | -0.19684
2089.125 | 122.5433 | -122.4197 | 0.13275 | -0.0054933 | 0.069806 | 0.0032578 | 0.0030719 | 0.012538 | -0.0043237 | -0.0014442 | -0.0040437 | 0.026634 | -0.010843 | 0.022665 | 0.0023371 | -0.0079062 | 0.036621 | 0.073242 | 0.10071 | 0.13733 | 0.13275 | 0.050354 | -0.09613 | 0.050354 | 0.07782 | -0.004578 | 0.032043 | 0.045776 | 0.027466 | -0.050354 | 122.4701 | 122.3236 | 0 | 122.493 | 122.5571 | 0.23346 | -0.09613 | 122.4472 | 122.3694 | -0.10071 | 122.4701 | 122.4152 | 0.045776 | -0.086975 | 122.5525 | 122.4564 | 122.5204 | -0.22888 | 122.4518 | 122.4655 | 122.4976 | -0.18311
2090.875 | 122.612 | -122.3877 | 0.09613 | -0.0054933 | 0.072583 | 0.0026168 | 0.0079853 | 0.013819 | -0.00047854 | -0.0035804 | -0.0040437 | 0.027062 | -0.0072119 | 0.022025 | 0.0029779 | -0.011324 | 0.045776 | 0.068665 | 0.068665 | 0.13275 | 0.15106 | 0.022888 | -0.09613 | -0.009155 | 0.050354 | -0.09613 | 0.054932 | 0.082397 | 0.013733 | -0.064087 | 122.4106 | 122.2916 | 0.054932 | 122.4564 | 122.5204 | 0.22888 | -0.050354 | 122.4014 | 122.3236 | -0.041198 | 122.3785 | 122.2916 | -0.032043 | -0.013733 | 122.5388 | 122.4335 | 122.4564 | -0.19226 | 122.4426 | 122.4701 | 122.438 | -0.16022
2092.625 | 122.5937 | -122.3602 | 0.10986 | -0.020752 | 0.070233 | 0.00069421 | 0.0011493 | 0.015955 | 0.0016577 | -0.00016236 | -0.019302 | 0.030052 | -0.0099891 | 0.023734 | 0.0072505 | -0.0098288 | 0.018311 | -0.013733 | 0.027466 | 0.10071 | 0.15106 | 0.009155 | -0.10986 | 0.064087 | 0.059509 | -0.054932 | 0.054932 | 0.050354 | 0.054932 | -0.036621 | 122.3694 | 122.2504 | 0.041199 | 122.3465 | 122.4609 | 0.21057 | -0.091552 | 122.4152 | 122.3236 | -0.054931 | 122.4243 | 122.3053 | -0.018311 | -0.059509 | 122.5113 | 122.3785 | 122.3877 | -0.21973 | 122.4152 | 122.4106 | 122.4197 | -0.14648
2094.3594 | 122.5433 | -122.3877 | 0.13275 | -0.013122 | 0.070447 | 0.0038986 | 0.0020039 | 0.016383 | -0.0021875 | 0.00047844 | -0.0040437 | 0.02578 | -0.010416 | 0.019675 | 0.0068231 | -0.0083334 | 0.07782 | 0.13275 | 0.15106 | 0.16937 | 0.11902 | 0.045776 | -0.073242 | 0.10529 | 0.12817 | 0.018311 | 0.027466 | 0.013733 | 0.041199 | -0.041199 | 122.4335 | 122.3145 | -0.013732 | 122.5204 | 122.5571 | 0.24261 | -0.054931 | 122.4289 | 122.3465 | -0.10529 | 122.493 | 122.406 | 0.05951 | -0.11902 | 122.5067 | 122.4655 | 122.5388 | -0.20599 | 122.4152 | 122.4014 | 122.5159 | -0.17395
2096.0938 | 122.6578 | -122.3694 | 0.07782 | -0.0054933 | 0.068524 | 0.0021896 | 0.0049945 | 0.014246 | -0.0036829 | -0.0012306 | -0.0040437 | 0.027062 | -0.0097755 | 0.018607 | 0.0021235 | -0.008547 | 0.018311 | 0.054932 | 0.10529 | 0.13275 | 0.14191 | 0.041199 | -0.10071 | 0.041199 | 0.10071 | -0.009155 | 0.032043 | 0.068665 | 0.022888 | -0.036621 | 122.4106 | 122.2687 | 0.064087 | 122.4243 | 122.5021 | 0.23346 | -0.059509 | 122.3923 | 122.3328 | -0.045777 | 122.4106 | 122.3602 | 0.027466 | -0.009155 | 122.5113 | 122.3877 | 122.4747 | -0.17853 | 122.4014 | 122.438 | 122.4701 | -0.11444
2097.8594 | 122.6761 | -122.3694 | 0.086975 | -0.0054933 | 0.072796 | 0.0017624 | 0.0077717 | 0.014674 | -0.0017603 | -0.0025122 | -0.0040437 | 0.028343 | -0.0095619 | 0.022665 | -0.00065374 | -0.0091878 | 0.10529 | 0.15564 | 0.16022 | 0.18768 | 0.12817 | 0.041199 | -0.091553 | 0.09613 | 0.1831 | 0.036621 | 0.022888 | 0.041199 | 0.032043 | -0.045776 | 122.4106 | 122.2778 | 0.041199 | 122.525 | 122.5571 | 0.27924 | 0.018311 | 122.4014 | 122.3236 | -0.064087 | 122.4655 | 122.406 | 0.082397 | -0.045776 | 122.4976 | 122.4747 | 122.5296 | -0.17853 | 122.3923 | 122.4106 | 122.5525 | -0.13275
2099.5469 | 122.6624 | -122.406 | 0.086975 | 0.0021362 | 0.073864 | -0.00058739 | 0.0017901 | 0.015742 | 0.0046485 | 5.1244e-05 | -0.0040437 | 0.031761 | -0.0089209 | 0.021811 | 0.0057551 | -0.010683 | 0.09613 | 0.036621 | 0.054932 | 0.13733 | 0.16479 | 0 | -0.1236 | 0.059509 | 0.073242 | -0.07782 | 0.064087 | 0.064087 | 0.013733 | -0.068665 | 122.406 | 122.2824 | 0.07782 | 122.4426 | 122.5433 | 0.26093 | 0.009155 | 122.4197 | 122.3373 | -0.022888 | 122.4655 | 122.3282 | -0.009155 | -0.022888 | 122.5708 | 122.5021 | 122.4609 | -0.21057 | 122.4701 | 122.4701 | 122.4792 | -0.15564
2101.2969 | 122.5662 | -122.406 | 0.11444 | -0.013122 | 0.065747 | 0.0032578 | 0.0052081 | 0.014674 | -0.0034691 | -0.0018714 | -0.011673 | 0.024925 | -0.010416 | 0.019247 | 0.0031915 | -0.0064108 | 0.022888 | 0.073242 | 0.09613 | 0.11444 | 0.13733 | 0.018311 | -0.10071 | 0.036621 | 0.068665 | -0.022888 | 0.041199 | 0.045776 | 0.022888 | -0.045776 | 122.4243 | 122.3053 | 0.022888 | 122.4792 | 122.5204 | 0.21515 | -0.091553 | 122.4289 | 122.3602 | -0.073242 | 122.4426 | 122.3831 | 0.022888 | -0.068665 | 122.5433 | 122.4289 | 122.5021 | -0.21515 | 122.4472 | 122.4518 | 122.4747 | -0.16022
2103.0312 | 122.6486 | -122.374 | 0.086975 | -0.013122 | 0.072796 | 0.0026168 | 0.0073443 | 0.014887 | 0.0016577 | -0.0027258 | -0.011673 | 0.028984 | -0.0093481 | 0.020529 | 0.0023371 | -0.008547 | 0.027466 | 0.036621 | 0.050354 | 0.11902 | 0.16022 | 0.018311 | -0.11444 | -0.009155 | 0.032043 | -0.10529 | 0.059509 | 0.086975 | 0.004578 | -0.068665 | 122.3923 | 122.2595 | 0.073242 | 122.4106 | 122.493 | 0.23346 | -0.059509 | 122.3785 | 122.3053 | -0.027466 | 122.3648 | 122.2687 | -0.036621 | 0 | 122.5342 | 122.4014 | 122.4243 | -0.20142 | 122.4335 | 122.4609 | 122.406 | -0.15564
2104.7031 | 122.6532 | -122.3511 | 0.10071 | -0.0054933 | 0.073224 | 0.0024032 | 0.0054217 | 0.015101 | 0.0040077 | 0.00026484 | -0.0040437 | 0.029839 | -0.0074255 | 0.022879 | 0.0049005 | -0.010256 | 0.068665 | 0.050354 | 0.064087 | 0.13275 | 0.16937 | 0.018311 | -0.11444 | 0.054932 | 0.07782 | -0.068665 | 0.059509 | 0.059509 | 0.013733 | -0.054932 | 122.3694 | 122.2366 | 0.068665 | 122.4014 | 122.4838 | 0.24719 | -0.032043 | 122.3648 | 122.2961 | -0.041199 | 122.406 | 122.2824 | -0.013733 | -0.041199 | 122.5204 | 122.4197 | 122.4152 | -0.21515 | 122.4106 | 122.4106 | 122.4289 | -0.15564
2106.4531 | 122.612 | -122.4243 | 0.1236 | -0.0054933 | 0.071087 | 0.00048061 | 0.0037127 | 0.016383 | 0.0018713 | 0.0015466 | -0.0040437 | 0.030907 | -0.0099891 | 0.022665 | 0.0070367 | -0.010683 | 0.009155 | -0.013733 | 0.004578 | 0.09613 | 0.19226 | 0.022888 | -0.13275 | 0.018311 | -0.009155 | -0.10529 | 0.073242 | 0.064087 | 0.018311 | -0.054932 | 122.4472 | 122.2916 | 0.068665 | 122.4106 | 122.5204 | 0.22888 | -0.11444 | 122.4426 | 122.3694 | -0.050354 | 122.4426 | 122.319 | -0.050354 | -0.059509 | 122.6166 | 122.4335 | 122.4289 | -0.25635 | 122.4976 | 122.4884 | 122.4152 | -0.17853
2108.2031 | 122.644 | -122.3694 | 0.10529 | -0.013122 | 0.071301 | 0.0021896 | 0.0058491 | 0.01446 | -0.0045373 | -0.002085 | -0.011673 | 0.023644 | -0.010843 | 0.020316 | 0.0016963 | -0.007479 | 0.059509 | 0.13733 | 0.16479 | 0.17853 | 0.11444 | 0.045776 | -0.086975 | 0.086975 | 0.18768 | 0.018311 | 0.022888 | 0.027466 | 0.036621 | -0.027466 | 122.4152 | 122.2824 | 0.009155 | 122.5067 | 122.5479 | 0.2655 | -0.045777 | 122.406 | 122.3419 | -0.082398 | 122.4564 | 122.3877 | 0.045777 | -0.07782 | 122.4838 | 122.4289 | 122.5342 | -0.19226 | 122.3923 | 122.3969 | 122.5571 | -0.13275
2109.8906 | 122.7173 | -122.3831 | 0.086975 | -0.0054933 | 0.073651 | 0.0011216 | 0.0084125 | 0.015742 | 0.0029395 | 0.0015466 | -0.0040437 | 0.031761 | -0.0080665 | 0.024588 | 0.0040461 | -0.0094016 | 0 | 0 | 0.013733 | 0.10986 | 0.16479 | 0 | -0.13275 | 0 | 0.054932 | -0.09613 | 0.07782 | 0.086975 | 0 | -0.068665 | 122.3831 | 122.2504 | 0.07782 | 122.3831 | 122.493 | 0.24261 | -0.086975 | 122.3831 | 122.3145 | -0.009155 | 122.3831 | 122.287 | -0.027465 | 0 | 122.5479 | 122.3831 | 122.3969 | -0.21973 | 122.4609 | 122.4701 | 122.438 | -0.15564
2111.625 | 122.6898 | -122.3557 | 0.086975 | -0.0054933 | 0.074719 | 5.3406e-05 | 0.0062763 | 0.013819 | 0.0044349 | 0.00069204 | -0.0040437 | 0.030266 | -0.0084937 | 0.023947 | 0.0019099 | -0.011324 | 0.041199 | 0.041199 | 0.045776 | 0.12817 | 0.16022 | 0 | -0.12817 | 0.054932 | 0.082397 | -0.068665 | 0.064087 | 0.082397 | 0.018311 | -0.064087 | 122.3557 | 122.2275 | 0.073242 | 122.3969 | 122.4838 | 0.25635 | -0.045776 | 122.374 | 122.2916 | -0.022888 | 122.4106 | 122.287 | -0.004578 | -0.004578 | 122.5159 | 122.3969 | 122.4014 | -0.21515 | 122.4197 | 122.438 | 122.438 | -0.15106
2113.375 | 122.7081 | -122.3694 | 0.07782 | -0.013122 | 0.071515 | 0.0038986 | 0.0058491 | 0.016383 | -0.0077417 | -0.00080316 | -0.011673 | 0.024285 | -0.010843 | 0.022665 | 0.0016963 | -0.006838 | 0.073242 | 0.15564 | 0.14191 | 0.16937 | 0.1236 | 0.036621 | -0.09613 | 0.10071 | 0.19226 | 0.050354 | 0.022888 | 0.050354 | 0.032043 | -0.036621 | 122.406 | 122.2733 | 0.045776 | 122.525 | 122.5388 | 0.2655 | -0.004578 | 122.4014 | 122.3328 | -0.054932 | 122.4701 | 122.4197 | 0.086975 | -0.027466 | 122.493 | 122.4426 | 122.5113 | -0.17395 | 122.3923 | 122.4197 | 122.5616 | -0.11444
2115.0625 | 122.6532 | -122.3831 | 0.09613 | -0.013122 | 0.074078 | 0.0028306 | 0.0069171 | 0.016169 | -0.0017603 | -0.0010168 | -0.011673 | 0.028984 | -0.0087073 | 0.021597 | 0.00062806 | -0.0098288 | 0.059509 | 0.082397 | 0.091553 | 0.14191 | 0.12817 | 0.018311 | -0.10986 | 0.004578 | 0.082397 | -0.068665 | 0.050354 | 0.068665 | 0.013733 | -0.059509 | 122.4014 | 122.2733 | 0.032044 | 122.4655 | 122.525 | 0.25177 | -0.036621 | 122.3969 | 122.3236 | -0.045776 | 122.3877 | 122.3145 | -0.009156 | -0.027465 | 122.5113 | 122.4426 | 122.4747 | -0.20599 | 122.4335 | 122.4518 | 122.4655 | -0.15564
2116.8125 | 122.5571 | -122.4106 | 0.11902 | -0.0054933 | 0.068738 | 0.0032578 | 0.0022175 | 0.014887 | -0.0015465 | -0.0018714 | -0.011673 | 0.027489 | -0.012339 | 0.022025 | 0.0057551 | -0.011324 | 0.082397 | 0.11902 | 0.14648 | 0.16479 | 0.1236 | 0.050354 | -0.082397 | 0.086975 | 0.11444 | 0.009155 | 0.027466 | 0.022888 | 0.050354 | -0.032043 | 122.4609 | 122.3282 | 0.004577 | 122.5296 | 122.5754 | 0.24719 | -0.036622 | 122.4609 | 122.3785 | -0.091553 | 122.4976 | 122.4197 | 0.041198 | -0.096131 | 122.5342 | 122.493 | 122.5571 | -0.20142 | 122.438 | 122.4335 | 122.525 | -0.15106
2118.5625 | 122.612 | -122.4243 | 0.12817 | -0.020752 | 0.072583 | 0.0017624 | 0.0032855 | 0.01446 | 0.0033667 | -0.0014442 | -0.0040437 | 0.029625 | -0.0097755 | 0.02117 | 0.0081049 | -0.0089742 | 0.009155 | -0.041199 | -0.009155 | 0.091553 | 0.16937 | 0.013733 | -0.13275 | 0 | -0.027466 | -0.13733 | 0.07782 | 0.082397 | 0 | -0.068665 | 122.438 | 122.2916 | 0.041199 | 122.3831 | 122.5159 | 0.2243 | -0.11902 | 122.4243 | 122.3557 | -0.050354 | 122.4243 | 122.287 | -0.068664 | -0.045777 | 122.5937 | 122.4335 | 122.4152 | -0.26093 | 122.5021 | 122.5067 | 122.3969 | -0.19684
2120.2969 | 122.5983 | -122.4197 | 0.09613 | -0.013122 | 0.072155 | 0.001976 | 0.0024311 | 0.015101 | -0.0011193 | 0.00026484 | -0.0040437 | 0.027275 | -0.011912 | 0.019888 | 0.0061823 | -0.006838 | 0.086975 | 0.10986 | 0.13275 | 0.17395 | 0.13275 | 0.050354 | -0.07782 | 0.11444 | 0.13733 | 0.013733 | 0.027466 | 0.032043 | 0.041199 | -0.018311 | 122.4701 | 122.3419 | 0.036621 | 122.5296 | 122.5937 | 0.25177 | -0.009155 | 122.4609 | 122.4014 | -0.068664 | 122.5342 | 122.4335 | 0.032044 | -0.064087 | 122.5525 | 122.5067 | 122.5525 | -0.17395 | 122.4472 | 122.4518 | 122.5571 | -0.11444
2122.0312 | 122.6624 | -122.406 | 0.086975 | -0.013122 | 0.071728 | 0.0024032 | 0.0092669 | 0.016169 | -0.0036829 | -0.0025122 | 0.0035858 | 0.028343 | -0.0082801 | 0.020102 | 0.0010553 | -0.0076926 | 0.068665 | 0.09613 | 0.10529 | 0.15106 | 0.13275 | 0.036621 | -0.11902 | 0.022888 | 0.091553 | -0.050354 | 0.045776 | 0.064087 | 0.018311 | -0.059509 | 122.4426 | 122.287 | 0.045776 | 122.5021 | 122.5571 | 0.27008 | -0.01831 | 122.4243 | 122.3465 | -0.041199 | 122.4289 | 122.3557 | 0.009155 | -0.022888 | 122.5388 | 122.4747 | 122.5113 | -0.20599 | 122.4518 | 122.4701 | 122.4976 | -0.14648
2123.7188 | 122.6624 | -122.3923 | 0.086975 | 0.0021362 | 0.067669 | 0.0034714 | 0.0052081 | 0.01446 | -0.0036829 | -0.0044348 | -0.0040437 | 0.025353 | -0.0091345 | 0.020102 | 0.0019099 | -0.0081198 | 0.004578 | 0.059509 | 0.091553 | 0.13275 | 0.15564 | 0.018311 | -0.10071 | 0.041199 | 0.10071 | 0.004578 | 0.050354 | 0.059509 | 0.041199 | -0.041199 | 122.4106 | 122.2916 | 0.068665 | 122.4518 | 122.525 | 0.23346 | -0.082397 | 122.4335 | 122.3511 | -0.036621 | 122.4335 | 122.3969 | 0.045777 | -0.027466 | 122.5479 | 122.3969 | 122.4838 | -0.18768 | 122.4426 | 122.4518 | 122.493 | -0.12817
2125.4531 | 122.7081 | -122.3831 | 0.091553 | 0.0097657 | 0.07536 | 0.0013352 | 0.0056355 | 0.015742 | 0.0048621 | 5.1244e-05 | -0.019302 | 0.029198 | -0.0093481 | 0.022665 | 0.0046869 | -0.013033 | 0.059509 | 0.032043 | 0.059509 | 0.14191 | 0.16479 | 0.009155 | -0.13275 | 0.059509 | 0.073242 | -0.068665 | 0.068665 | 0.073242 | 0.013733 | -0.050354 | 122.3923 | 122.2504 | 0.073242 | 122.4152 | 122.525 | 0.27466 | -0.032044 | 122.3969 | 122.3328 | -0.022888 | 122.4426 | 122.3145 | -0.018311 | -0.018311 | 122.5479 | 122.4426 | 122.4426 | -0.2243 | 122.4518 | 122.4564 | 122.4564 | -0.14191
2127.1875 | 122.5662 | -122.4518 | 0.12817 | -0.0054933 | 0.076001 | 0.0024032 | 0.0024311 | 0.016169 | 0.0022987 | -0.0010168 | -0.011673 | 0.029198 | -0.0093481 | 0.024588 | 0.0063959 | -0.0076926 | -0.009155 | -0.004578 | -0.004578 | 0.091553 | 0.16022 | 0.018311 | -0.13733 | 0 | -0.004578 | -0.14191 | 0.073242 | 0.064087 | 0.009155 | -0.064087 | 122.4701 | 122.3145 | 0.032043 | 122.4472 | 122.5433 | 0.22888 | -0.13733 | 122.4609 | 122.3877 | -0.054932 | 122.4518 | 122.3099 | -0.07782 | -0.064087 | 122.612 | 122.4426 | 122.4472 | -0.2655 | 122.525 | 122.5159 | 122.4472 | -0.19226
2128.875 | 122.5937 | -122.4472 | 0.11444 | -0.013122 | 0.075146 | -0.00016019 | 0.0037127 | 0.017664 | 0.0048621 | -0.00037596 | -0.019302 | 0.029839 | -0.0091345 | 0.025229 | 0.0066095 | -0.0098288 | 0.041199 | 0.022888 | 0.036621 | 0.11902 | 0.16022 | 0.032043 | -0.1236 | 0.022888 | 0.027466 | -0.13275 | 0.073242 | 0.068665 | 0.009155 | -0.064087 | 122.4792 | 122.3236 | 0.045776 | 122.4701 | 122.5662 | 0.24261 | -0.073242 | 122.4564 | 122.3831 | -0.041199 | 122.4701 | 122.3145 | -0.068664 | -0.045776 | 122.6074 | 122.4884 | 122.4838 | -0.23804 | 122.5204 | 122.5159 | 122.4747 | -0.17853
2130.6094 | 122.6212 | -122.4197 | 0.10071 | -0.0054933 | 0.074078 | 0.0015488 | 0.0022175 | 0.016596 | -0.00026494 | -0.0012306 | -0.011673 | 0.026634 | -0.0099891 | 0.022025 | 0.0057551 | -0.0089742 | 0.013733 | 0.050354 | 0.068665 | 0.11902 | 0.13275 | 0.018311 | -0.10529 | 0.064087 | 0.091553 | 0.004578 | 0.045776 | 0.045776 | 0.032043 | -0.041199 | 122.4381 | 122.3145 | 0.032043 | 122.4701 | 122.5388 | 0.22431 | -0.086975 | 122.4518 | 122.3785 | -0.054932 | 122.4838 | 122.4243 | 0.045777 | -0.054932 | 122.5525 | 122.4335 | 122.4884 | -0.20599 | 122.4655 | 122.4655 | 122.5113 | -0.14191
2132.3594 | 122.5845 | -122.4472 | 0.11902 | -0.013122 | 0.074719 | 0.003685 | 0.0037127 | 0.015528 | 0.0035803 | -0.00016236 | -0.026932 | 0.031548 | -0.011057 | 0.021597 | 0.0061823 | -0.0070516 | 0.022888 | 0.027466 | 0.036621 | 0.10071 | 0.15564 | 0.009155 | -0.1236 | 0.004578 | 0.027466 | -0.11902 | 0.059509 | 0.059509 | 0.009155 | -0.086975 | 122.4564 | 122.3236 | 0.036621 | 122.4747 | 122.5479 | 0.2243 | -0.096131 | 122.4564 | 122.3602 | -0.05951 | 122.4518 | 122.3282 | -0.032044 | -0.05951 | 122.6028 | 122.4701 | 122.4838 | -0.24261 | 122.5067 | 122.5067 | 122.4747 | -0.20599
2134.0469 | 122.7127 | -122.3923 | 0.091553 | -0.013122 | 0.074292 | 0.0047532 | 0.0056355 | 0.016383 | 0.00016226 | 5.1244e-05 | -0.011673 | 0.027489 | -0.0082801 | 0.023947 | 0.0038325 | -0.0079062 | -0.018311 | -0.022888 | 0 | 0.10529 | 0.16479 | 0.004578 | -0.1236 | -0.009155 | 0.036621 | -0.10529 | 0.068665 | 0.068665 | 0.004578 | -0.086975 | 122.3969 | 122.2687 | 0.073242 | 122.3694 | 122.4976 | 0.22888 | -0.10986 | 122.3969 | 122.3053 | -0.022888 | 122.3831 | 122.287 | -0.018311 | -0.022888 | 122.5571 | 122.374 | 122.3923 | -0.21515 | 122.4609 | 122.4609 | 122.4289 | -0.17853
2135.7969 | 122.6395 | -122.4289 | 0.10071 | -0.013122 | 0.071728 | -0.00080099 | 0.0043537 | 0.015742 | -0.0015465 | 0.00047844 | -0.0040437 | 0.030266 | -0.0074255 | 0.02352 | 0.0021235 | -0.011111 | 0.013733 | -0.009155 | 0.054932 | 0.10986 | 0.15564 | 0.018311 | -0.091553 | 0.073242 | 0.082397 | -0.032043 | 0.036621 | 0.054932 | 0.041199 | -0.032043 | 122.4472 | 122.3373 | 0.054932 | 122.4197 | 122.5388 | 0.20142 | -0.086975 | 122.4701 | 122.3969 | -0.064087 | 122.5021 | 122.3969 | 0 | -0.045776 | 122.5845 | 122.4426 | 122.4838 | -0.19226 | 122.4655 | 122.4838 | 122.5113 | -0.13275
2137.5312 | 122.7219 | -122.4197 | 0.086975 | -0.020752 | 0.068524 | 0.007103 | 0.0067035 | 0.018305 | -0.0068871 | -0.0046484 | -0.011673 | 0.024712 | -0.0078529 | 0.019675 | 0.0023371 | -0.007479 | 0.027466 | 0.07782 | 0.10986 | 0.15106 | 0.13733 | 0.054932 | -0.086975 | 0.068665 | 0.15564 | 0.045776 | 0.027466 | 0.045776 | 0.045776 | -0.032043 | 122.4747 | 122.3328 | 0.050354 | 122.4976 | 122.5708 | 0.23804 | -0.059509 | 122.4655 | 122.3877 | -0.059509 | 122.4884 | 122.4655 | 0.077819 | -0.041199 | 122.5571 | 122.4472 | 122.5296 | -0.17395 | 122.4472 | 122.4655 | 122.5754 | -0.11902
2139.2812 | 122.6761 | -122.4014 | 0.064087 | -0.013122 | 0.071728 | 0.0041122 | 0.0069171 | 0.01446 | -0.0030419 | -0.0046484 | -0.011673 | 0.026848 | -0.0087073 | 0.021811 | 0.00041446 | -0.0076926 | 0.086975 | 0.13733 | 0.14648 | 0.17395 | 0.13275 | 0.045776 | -0.082397 | 0.082397 | 0.18768 | 0.032043 | 0.045776 | 0.050354 | 0.059509 | -0.027466 | 122.4472 | 122.319 | 0.068664 | 122.5388 | 122.5754 | 0.25635 | 0.022888 | 122.4609 | 122.374 | -0.018311 | 122.4838 | 122.4335 | 0.059509 | -0.013733 | 122.5342 | 122.4884 | 122.5479 | -0.14648 | 122.4472 | 122.4518 | 122.5891 | -0.091553
2141.0312 | 122.6852 | -122.3831 | 0.07782 | -0.013122 | 0.071515 | 0.001976 | 0.0067035 | 0.015528 | -0.0041101 | -0.0035804 | -0.0040437 | 0.026207 | -0.0091345 | 0.022025 | -1.2744e-05 | -0.010256 | 0.082397 | 0.12817 | 0.13733 | 0.17853 | 0.11902 | 0.022888 | -0.082397 | 0.091553 | 0.16022 | 0.004578 | 0.022888 | 0.045776 | 0.045776 | -0.041199 | 122.406 | 122.3007 | 0.041199 | 122.5113 | 122.5616 | 0.26092 | 0.004577 | 122.4289 | 122.3419 | -0.054932 | 122.4747 | 122.3877 | 0.045777 | -0.032044 | 122.5021 | 122.4655 | 122.5204 | -0.16022 | 122.406 | 122.4289 | 122.5433 | -0.11902
2142.7656 | 122.7036 | -122.3923 | 0.082397 | -0.0054933 | 0.072583 | 0.0034714 | 0.0026447 | 0.01446 | -0.0045373 | -0.0042212 | -0.011673 | 0.024498 | -0.011698 | 0.020316 | 0.0034051 | -0.0098288 | 0.11444 | 0.15564 | 0.16937 | 0.18768 | 0.14648 | 0.041199 | -0.07782 | 0.10071 | 0.1831 | 0.036621 | 0.032043 | 0.045776 | 0.045776 | -0.032043 | 122.4335 | 122.3145 | 0.064087 | 122.5479 | 122.58 | 0.2655 | 0.032044 | 122.438 | 122.3602 | -0.050354 | 122.493 | 122.4289 | 0.068664 | -0.036621 | 122.5388 | 122.5067 | 122.5616 | -0.16022 | 122.4243 | 122.438 | 122.5754 | -0.11444
2144.4531 | 122.5983 | -122.4335 | 0.11902 | -0.020752 | 0.073651 | -0.00080099 | 0.0039265 | 0.014674 | 0.0042213 | -0.00037596 | 0.011215 | 0.031334 | -0.0095619 | 0.022452 | 0.0076777 | -0.011111 | -0.004578 | -0.050354 | -0.018311 | 0.07782 | 0.17853 | -0.004578 | -0.09613 | 0.009155 | -0.032043 | -0.14648 | 0.086975 | 0.07782 | 0.013733 | -0.073242 | 122.4289 | 122.3373 | 0.059509 | 122.3831 | 122.5113 | 0.17395 | -0.1236 | 122.4472 | 122.3602 | -0.032044 | 122.4426 | 122.287 | -0.073242 | -0.041199 | 122.612 | 122.4289 | 122.4152 | -0.21515 | 122.5204 | 122.5113 | 122.4014 | -0.19226
2146.2031 | 122.6669 | -122.4335 | 0.09613 | -0.0054933 | 0.071515 | 0.0034714 | 0.0052081 | 0.014887 | -0.0034691 | -0.0029394 | -0.0040437 | 0.027275 | -0.010203 | 0.020743 | 0.00084166 | -0.010042 | 0.064087 | 0.10986 | 0.12817 | 0.16937 | 0.12817 | 0.036621 | -0.10071 | 0.032043 | 0.10986 | -0.045776 | 0.054932 | 0.064087 | 0.013733 | -0.045776 | 122.4701 | 122.3328 | 0.032044 | 122.5433 | 122.6028 | 0.27008 | -0.032043 | 122.4472 | 122.3877 | -0.041198 | 122.4655 | 122.3877 | 0 | -0.032043 | 122.5616 | 122.4976 | 122.5616 | -0.19684 | 122.4884 | 122.4976 | 122.5433 | -0.14191
2147.9531 | 122.6578 | -122.4335 | 0.1236 | -0.0054933 | 0.074292 | 0.0030442 | 0.0020039 | 0.015528 | 0.0048621 | -0.00080316 | -0.0040437 | 0.029625 | -0.012125 | 0.02117 | 0.0068231 | -0.010042 | 0.073242 | 0.059509 | 0.064087 | 0.12817 | 0.16022 | 0.009155 | -0.11444 | 0.054932 | 0.068665 | -0.082397 | 0.086975 | 0.054932 | 0.009155 | -0.059509 | 122.4426 | 122.319 | 0.036621 | 122.493 | 122.5616 | 0.24262 | -0.050354 | 122.4426 | 122.374 | -0.036621 | 122.4884 | 122.3511 | -0.022888 | -0.068664 | 122.5937 | 122.5067 | 122.4976 | -0.23804 | 122.5204 | 122.4884 | 122.5021 | -0.1831
2149.6406 | 122.7264 | -122.4106 | 0.086975 | -0.0054933 | 0.069378 | 0.001976 | 0.0067035 | 0.016383 | -0.0051781 | -0.0014442 | -0.0040437 | 0.024498 | -0.0097755 | 0.022238 | -1.2744e-05 | -0.0083334 | 0.022888 | 0.073242 | 0.10529 | 0.14648 | 0.14191 | 0.018311 | -0.10986 | 0.064087 | 0.15106 | 0.013733 | 0.027466 | 0.045776 | 0.041199 | -0.036621 | 122.4289 | 122.3007 | 0.054932 | 122.4838 | 122.5571 | 0.25635 | -0.064087 | 122.4518 | 122.374 | -0.059509 | 122.4747 | 122.4243 | 0.050354 | -0.041199 | 122.5525 | 122.4335 | 122.5159 | -0.19684 | 122.438 | 122.4564 | 122.5616 | -0.1236
2151.3906 | 122.7081 | -122.4243 | 0.10071 | 0.0021362 | 0.07536 | 0.0013352 | 0.0049945 | 0.016383 | 0.0037939 | 0.00047844 | -0.011673 | 0.031548 | -0.0091345 | 0.023947 | 0.0063959 | -0.011538 | 0.064087 | 0.036621 | 0.068665 | 0.1236 | 0.15564 | 0.013733 | -0.10071 | 0.050354 | 0.091553 | -0.073242 | 0.050354 | 0.086975 | 0 | -0.041199 | 122.438 | 122.3236 | 0.054932 | 122.4609 | 122.5479 | 0.2243 | -0.036621 | 122.4243 | 122.3831 | -0.050354 | 122.4747 | 122.3511 | -0.032043 | -0.013733 | 122.58 | 122.4884 | 122.493 | -0.20142 | 122.4747 | 122.5113 | 122.5159 | -0.14191
2153.0625 | 122.644 | -122.4243 | 0.10986 | -0.020752 | 0.07301 | 0.0015488 | 0.0032855 | 0.013606 | 0.00016226 | 0.0021874 | -0.011673 | 0.025139 | -0.010416 | 0.019888 | 0.010668 | -0.0091878 | 0.032043 | 0.054932 | 0.073242 | 0.13733 | 0.15106 | 0.041199 | -0.091553 | 0.091553 | 0.11902 | -0.009155 | 0.041199 | 0.036621 | 0.032043 | -0.018311 | 122.4655 | 122.3328 | 0.041199 | 122.4792 | 122.5616 | 0.22888 | -0.07782 | 122.4564 | 122.406 | -0.068664 | 122.5159 | 122.4152 | 0.009156 | -0.073242 | 122.5754 | 122.4564 | 122.4976 | -0.20142 | 122.4655 | 122.4609 | 122.5433 | -0.12817
2154.8125 | 122.6898 | -122.4197 | 0.09613 | -0.013122 | 0.072155 | 0.0028306 | 0.0054217 | 0.017237 | -0.0024011 | -0.0014442 | -0.011673 | 0.027489 | -0.0097755 | 0.022025 | 0.0021235 | -0.0096152 | 0.022888 | 0.041199 | 0.045776 | 0.11444 | 0.16937 | 0.009155 | -0.10986 | -0.013733 | 0.041199 | -0.086975 | 0.064087 | 0.07782 | 0.004578 | -0.073242 | 122.4289 | 122.3099 | 0.073243 | 122.4609 | 122.5342 | 0.2243 | -0.073242 | 122.4243 | 122.3465 | -0.032043 | 122.406 | 122.3328 | -0.013733 | -0.01831 | 122.5891 | 122.4426 | 122.4655 | -0.20599 | 122.4838 | 122.4976 | 122.4609 | -0.16937
2156.5625 | 122.7173 | -122.406 | 0.064087 | -0.013122 | 0.070233 | 0.0034714 | 0.0075581 | 0.017024 | -0.0051781 | -0.0022986 | -0.0040437 | 0.025994 | -0.010416 | 0.02352 | -0.0010809 | -0.0081198 | 0.041199 | 0.068665 | 0.10071 | 0.14191 | 0.13275 | 0.059509 | -0.09613 | 0.064087 | 0.1236 | 0.009155 | 0.059509 | 0.036621 | 0.041199 | -0.032043 | 122.4655 | 122.3099 | 0.068664 | 122.4747 | 122.5479 | 0.23804 | -0.022888 | 122.4472 | 122.374 | -0.004578 | 122.4701 | 122.4152 | 0.041198 | -0.027466 | 122.5388 | 122.4472 | 122.5067 | -0.16022 | 122.4655 | 122.4426 | 122.5296 | -0.09613
2158.25 | 122.5983 | -122.4655 | 0.10529 | -0.013122 | 0.068097 | 0.0034714 | 0.0037127 | 0.013819 | -0.0011193 | -0.0040076 | -0.0040437 | 0.028343 | -0.011271 | 0.022238 | 0.0027643 | -0.0072652 | 0.059509 | 0.073242 | 0.10071 | 0.1236 | 0.13733 | 0.027466 | -0.086975 | 0.054932 | 0.086975 | -0.032043 | 0.045776 | 0.054932 | 0.027466 | -0.041199 | 122.493 | 122.3785 | 0.032043 | 122.5388 | 122.5891 | 0.21057 | -0.045777 | 122.493 | 122.4243 | -0.05951 | 122.5204 | 122.4335 | 0.009156 | -0.050354 | 122.6028 | 122.525 | 122.5662 | -0.19226 | 122.5113 | 122.5204 | 122.5525 | -0.14649
2160 | 122.644 | -122.4655 | 0.10986 | -0.013122 | 0.07301 | -0.00016019 | 0.00029487 | 0.016169 | 0.0037939 | -0.0044348 | 0.0035858 | 0.030052 | -0.011484 | 0.021597 | 0.0066095 | -0.011324 | 0.027466 | -0.045776 | -0.027466 | 0.086975 | 0.1831 | 0.022888 | -0.14191 | 0.004578 | -0.018311 | -0.14191 | 0.068665 | 0.082397 | 0 | -0.07782 | 122.4884 | 122.3236 | 0.073242 | 122.4197 | 122.5525 | 0.22888 | -0.082397 | 122.4655 | 122.3877 | -0.041198 | 122.4701 | 122.3236 | -0.064087 | -0.027466 | 122.6486 | 122.493 | 122.438 | -0.25177 | 122.5342 | 122.5479 | 122.4472 | -0.18768
2161.6719 | 122.731 | -122.4152 | 0.07782 | -0.013122 | 0.070233 | 0.0043258 | 0.0034991 | 0.014246 | -0.0036829 | -0.0010168 | -0.011673 | 0.024925 | -0.0091345 | 0.020956 | -0.00044014 | -0.0079062 | 0.050354 | 0.086975 | 0.11444 | 0.15106 | 0.14191 | 0.027466 | -0.07782 | 0.07782 | 0.13275 | 0.032043 | 0.027466 | 0.041199 | 0.036621 | -0.022888 | 122.4426 | 122.3373 | 0.064087 | 122.5021 | 122.5662 | 0.22888 | -0.027466 | 122.4518 | 122.3923 | -0.050354 | 122.493 | 122.4472 | 0.054931 | -0.036621 | 122.5571 | 122.4655 | 122.5296 | -0.15564 | 122.4426 | 122.4564 | 122.5479 | -0.10071
2163.4219 | 122.6852 | -122.4335 | 0.09613 | -0.020752 | 0.071301 | 0.001976 | 0.0034991 | 0.01446 | 0.00016226 | -0.002085 | 0.0035858 | 0.027489 | -0.010416 | 0.021811 | 0.0023371 | -0.0091878 | 0.041199 | 0.032043 | 0.059509 | 0.13275 | 0.15106 | 0.009155 | -0.10986 | -0.013733 | 0.041199 | -0.09613 | 0.059509 | 0.073242 | 0.004578 | -0.073242 | 122.4426 | 122.3236 | 0.054932 | 122.4655 | 122.5662 | 0.24261 | -0.054931 | 122.438 | 122.3602 | -0.036621 | 122.4197 | 122.3373 | -0.022888 | -0.022888 | 122.5845 | 122.4747 | 122.493 | -0.20599 | 122.493 | 122.5067 | 122.4747 | -0.16937
2165.0938 | 122.699 | -122.4197 | 0.10529 | -0.013122 | 0.074719 | 5.3406e-05 | 0.0043537 | 0.015101 | 0.0029395 | -0.00037596 | -0.019302 | 0.031975 | -0.0084937 | 0.02352 | 0.0061823 | -0.011965 | 0.082397 | 0.045776 | 0.054932 | 0.13275 | 0.17395 | 0.009155 | -0.1236 | 0.050354 | 0.082397 | -0.09613 | 0.068665 | 0.082397 | 0.027466 | -0.050354 | 122.4289 | 122.2961 | 0.068664 | 122.4655 | 122.5525 | 0.25635 | -0.022889 | 122.4472 | 122.3694 | -0.036621 | 122.4701 | 122.3236 | -0.045776 | -0.022889 | 122.5937 | 122.5021 | 122.4747 | -0.22888 | 122.4884 | 122.5021 | 122.5021 | -0.15564
2166.8281 | 122.6944 | -122.4472 | 0.10986 | -0.0054933 | 0.075146 | -0.00058739 | 0.0026447 | 0.01681 | 0.0033667 | 0.00047844 | 0.0035858 | 0.031121 | -0.0076393 | 0.025443 | 0.0063959 | -0.0083334 | 0.07782 | 0.045776 | 0.07782 | 0.13733 | 0.17395 | 0.009155 | -0.12817 | 0.054932 | 0.07782 | -0.086975 | 0.054932 | 0.073242 | 0.032043 | -0.050354 | 122.4564 | 122.319 | 0.064087 | 122.493 | 122.5845 | 0.2655 | -0.032043 | 122.4792 | 122.3969 | -0.054931 | 122.5021 | 122.3602 | -0.036621 | -0.036621 | 122.6212 | 122.525 | 122.525 | -0.23804 | 122.5021 | 122.5204 | 122.525 | -0.16022
2168.5938 | 122.6257 | -122.4564 | 0.10071 | -0.0054933 | 0.07066 | 0.0041122 | 0.0081989 | 0.016383 | -0.0075281 | -0.002085 | -0.0040437 | 0.025566 | -0.0082801 | 0.019888 | 0.0029779 | -0.0055564 | 0.009155 | 0.054932 | 0.09613 | 0.13733 | 0.13275 | 0.018311 | -0.09613 | 0.036621 | 0.082397 | -0.036621 | 0.050354 | 0.059509 | 0.041199 | -0.059509 | 122.4747 | 122.3602 | 0.032043 | 122.5113 | 122.5937 | 0.23346 | -0.091553 | 122.4976 | 122.3969 | -0.050354 | 122.493 | 122.4197 | 0.022888 | -0.041199 | 122.5891 | 122.4655 | 122.5525 | -0.19684 | 122.5067 | 122.5159 | 122.5388 | -0.16022
2170.2812 | 122.7585 | -122.4289 | 0.10071 | -0.013122 | 0.076428 | 0.00090781 | 0.0090533 | 0.017024 | 0.0025123 | -0.0010168 | -0.0040437 | 0.029412 | -0.0084937 | 0.022879 | 0.0031915 | -0.0083334 | 0.027466 | -0.027466 | 0.018311 | 0.10071 | 0.16022 | 0.018311 | -0.14191 | -0.004578 | 0.059509 | -0.10986 | 0.073242 | 0.082397 | 0.009155 | -0.082397 | 122.4472 | 122.287 | 0.059509 | 122.4014 | 122.5296 | 0.24262 | -0.073242 | 122.438 | 122.3465 | -0.027466 | 122.4243 | 122.319 | -0.027466 | -0.018311 | 122.5891 | 122.4564 | 122.4472 | -0.24262 | 122.5021 | 122.5113 | 122.4884 | -0.18311
2172.0156 | 122.6257 | -122.4609 | 0.10071 | -0.020752 | 0.074505 | -0.00058739 | 0.0024311 | 0.015528 | 0.0029395 | -0.00016236 | 0.0035858 | 0.031121 | -0.0091345 | 0.023093 | 0.0070367 | -0.0089742 | 0.073242 | 0.045776 | 0.050354 | 0.1236 | 0.15564 | 0.032043 | -0.11902 | 0.036621 | 0.054932 | -0.091553 | 0.059509 | 0.064087 | 0 | -0.054932 | 122.493 | 122.3419 | 0.054932 | 122.5067 | 122.5845 | 0.24261 | -0.027466 | 122.4609 | 122.406 | -0.041199 | 122.4976 | 122.3694 | -0.036621 | -0.036621 | 122.6166 | 122.5342 | 122.5113 | -0.21973 | 122.5204 | 122.525 | 122.5159 | -0.15564
2173.7031 | 122.7356 | -122.4197 | 0.082397 | 0.0021362 | 0.070874 | 0.0026168 | 0.0060627 | 0.01446 | -0.00026494 | -0.00080316 | -0.011673 | 0.026421 | -0.0095619 | 0.02352 | 0.0044733 | -0.0083334 | -0.032043 | 0.004578 | 0.009155 | 0.07782 | 0.16937 | 0.004578 | -0.13733 | -0.032043 | 0.027466 | -0.10529 | 0.082397 | 0.082397 | 0 | -0.068665 | 122.4243 | 122.2824 | 0.086976 | 122.4243 | 122.4976 | 0.21515 | -0.11444 | 122.4197 | 122.3511 | 0 | 122.3877 | 122.3145 | -0.036621 | 0 | 122.5891 | 122.3877 | 122.4289 | -0.21973 | 122.5021 | 122.5021 | 122.4472 | -0.15106
2175.4375 | 122.699 | -122.4518 | 0.091553 | -0.020752 | 0.073437 | 0.0028306 | 0.0069171 | 0.015315 | -0.0026147 | -0.00058956 | -0.011673 | 0.027062 | -0.0095619 | 0.022025 | 0.0023371 | -0.0089742 | 0.050354 | 0.11902 | 0.1236 | 0.16479 | 0.12817 | 0.032043 | -0.09613 | 0.041199 | 0.14648 | -0.036621 | 0.041199 | 0.041199 | 0.036621 | -0.073242 | 122.4838 | 122.3557 | 0.036621 | 122.5708 | 122.6166 | 0.26092 | -0.041199 | 122.4884 | 122.3785 | -0.050354 | 122.493 | 122.4152 | 0.036621 | -0.050354 | 122.58 | 122.5021 | 122.5754 | -0.18768 | 122.493 | 122.493 | 122.5983 | -0.16479
2177.1094 | 122.731 | -122.4243 | 0.10071 | -0.020752 | 0.074933 | 0.00069421 | 0.0043537 | 0.016169 | 0.0010169 | 5.1244e-05 | -0.0040437 | 0.032616 | -0.0080665 | 0.024374 | 0.0059687 | -0.010256 | 0.050354 | 0.036621 | 0.050354 | 0.13275 | 0.16937 | 0.013733 | -0.11902 | 0.041199 | 0.086975 | -0.073242 | 0.054932 | 0.064087 | 0.013733 | -0.059509 | 122.438 | 122.3053 | 0.068665 | 122.4609 | 122.5571 | 0.25177 | -0.050354 | 122.438 | 122.3648 | -0.045776 | 122.4655 | 122.3511 | -0.013733 | -0.036621 | 122.5937 | 122.4747 | 122.4747 | -0.21973 | 122.4792 | 122.4884 | 122.5113 | -0.16022
2178.875 | 122.7539 | -122.4243 | 0.091553 | -0.0054933 | 0.070019 | 0.0032578 | 0.0037127 | 0.017237 | 0.0012305 | -0.0025122 | -0.011673 | 0.029839 | -0.0099891 | 0.024161 | 0.0066095 | -0.011324 | -0.004578 | 0.009155 | 0.036621 | 0.11902 | 0.15106 | 0.004578 | -0.13275 | 0.036621 | 0.082397 | -0.082397 | 0.064087 | 0.082397 | 0.004578 | -0.064087 | 122.4289 | 122.2916 | 0.059509 | 122.4335 | 122.5433 | 0.25177 | -0.096131 | 122.4289 | 122.3602 | -0.027466 | 122.4609 | 122.3419 | -0.01831 | -0.009156 | 122.5754 | 122.4197 | 122.4609 | -0.2243 | 122.4884 | 122.5067 | 122.5067 | -0.15564
2180.5625 | 122.6257 | -122.493 | 0.091553 | -0.0054933 | 0.069806 | 0.0049668 | 0.0047809 | 0.014887 | -0.0041101 | -0.0012306 | -0.011673 | 0.025353 | -0.0087073 | 0.022452 | 0.0046869 | -0.006838 | 0.036621 | 0.091553 | 0.10529 | 0.12817 | 0.11902 | 0.032043 | -0.091553 | 0.032043 | 0.082397 | 0 | 0.022888 | 0.032043 | 0.036621 | -0.036621 | 122.525 | 122.4014 | 0.027466 | 122.5845 | 122.6212 | 0.21973 | -0.054932 | 122.5296 | 122.4564 | -0.068665 | 122.525 | 122.493 | 0.036621 | -0.05951 | 122.612 | 122.5296 | 122.5983 | -0.18311 | 122.5159 | 122.525 | 122.5754 | -0.12817
2182.3125 | 122.7493 | -122.4106 | 0.073242 | -0.013122 | 0.070874 | 0.0030442 | 0.0090533 | 0.014033 | -0.0043237 | -0.002085 | -0.011673 | 0.02578 | -0.0087073 | 0.021597 | 0.00084166 | -0.008547 | 0.07782 | 0.10986 | 0.14648 | 0.1831 | 0.10986 | 0.036621 | -0.086975 | 0.091553 | 0.17395 | 0.054932 | 0.018311 | 0.045776 | 0.050354 | -0.018311 | 122.4472 | 122.3236 | 0.036621 | 122.5204 | 122.5937 | 0.27008 | 0.004578 | 122.4609 | 122.3923 | -0.054931 | 122.5021 | 122.4655 | 0.073243 | -0.027466 | 122.5204 | 122.4884 | 122.5571 | -0.16022 | 122.4289 | 122.4564 | 122.5845 | -0.091553
2184.0156 | 122.7448 | -122.438 | 0.09613 | -0.020752 | 0.070874 | 0.0043258 | 0.0058491 | 0.018305 | -0.0038965 | -0.0035804 | 0.0035858 | 0.026421 | -0.010416 | 0.020529 | 0.00041446 | -0.0087606 | 0.073242 | 0.10986 | 0.14191 | 0.17395 | 0.13733 | 0.050354 | -0.09613 | 0.082397 | 0.16937 | 0.045776 | 0.041199 | 0.050354 | 0.036621 | -0.032043 | 122.4884 | 122.3419 | 0.041199 | 122.5479 | 122.612 | 0.27008 | -0.022888 | 122.4747 | 122.406 | -0.054931 | 122.5204 | 122.4838 | 0.077819 | -0.045776 | 122.5754 | 122.5113 | 122.58 | -0.19226 | 122.4792 | 122.4884 | 122.6074 | -0.12817
2185.7656 | 122.7356 | -122.4472 | 0.082397 | -0.0054933 | 0.070233 | 0.0038986 | 0.0052081 | 0.017024 | -0.0024011 | -0.0029394 | -0.0040437 | 0.026421 | -0.011057 | 0.019888 | 0.0044733 | -0.010897 | 0.11444 | 0.16937 | 0.17853 | 0.19684 | 0.10529 | 0.045776 | -0.059509 | 0.07782 | 0.17853 | 0.027466 | 0.013733 | 0.032043 | 0.032043 | -0.018311 | 122.493 | 122.3877 | 0.022889 | 122.6166 | 122.644 | 0.25635 | 0.032044 | 122.4792 | 122.4289 | -0.068664 | 122.525 | 122.4747 | 0.045777 | -0.050354 | 122.5525 | 122.5616 | 122.6257 | -0.14191 | 122.4609 | 122.4792 | 122.6257 | -0.10071
2187.5 | 122.612 | -122.4472 | 0.10986 | -0.0054933 | 0.067029 | 0.0024032 | 0.00072207 | 0.014674 | -0.00069214 | -0.00037596 | -0.0040437 | 0.026207 | -0.0097755 | 0.019888 | 0.0044733 | -0.0096152 | 0.10071 | 0.1236 | 0.14648 | 0.16937 | 0.12817 | 0.045776 | -0.082397 | 0.10529 | 0.12817 | 0.004578 | 0.022888 | 0.013733 | 0.041199 | -0.032043 | 122.493 | 122.3648 | 0.018311 | 122.5708 | 122.6166 | 0.25177 | -0.009155 | 122.4884 | 122.4152 | -0.086975 | 122.5525 | 122.4518 | 0.036621 | -0.09613 | 122.5754 | 122.5479 | 122.5937 | -0.19226 | 122.4701 | 122.4609 | 122.5754 | -0.14191
2189.2344 | 122.7036 | -122.4564 | 0.07782 | -0.013122 | 0.067456 | 0.0034714 | 0.0056355 | 0.017451 | -0.0026147 | -0.0040076 | -0.011673 | 0.027489 | -0.0093481 | 0.020316 | 0.0031915 | -0.0087606 | 0.018311 | 0.064087 | 0.086975 | 0.14191 | 0.12817 | 0.036621 | -0.10071 | 0.045776 | 0.091553 | 0 | 0.045776 | 0.059509 | 0.027466 | -0.054932 | 122.493 | 122.3557 | 0.050354 | 122.5204 | 122.5983 | 0.24262 | -0.059509 | 122.4838 | 122.4014 | -0.032044 | 122.5021 | 122.4564 | 0.054932 | -0.018311 | 122.5845 | 122.4747 | 122.5433 | -0.17853 | 122.5021 | 122.5159 | 122.5479 | -0.13275
2190.9375 | 122.7814 | -122.4289 | 0.09613 | -0.013122 | 0.071728 | 0.0011216 | 0.0052081 | 0.017451 | 0.0046485 | -0.0025122 | -0.011673 | 0.03048 | -0.0076393 | 0.025015 | 0.0034051 | -0.011965 | 0.032043 | -0.013733 | 0 | 0.10986 | 0.18768 | -0.004578 | -0.11902 | 0.018311 | 0.041199 | -0.09613 | 0.064087 | 0.064087 | 0.013733 | -0.068665 | 122.4243 | 122.3099 | 0.091553 | 122.4152 | 122.5388 | 0.22888 | -0.064087 | 122.4426 | 122.3602 | -0.032043 | 122.4472 | 122.3328 | -0.027465 | -0.032043 | 122.6166 | 122.4609 | 122.4289 | -0.21515 | 122.493 | 122.493 | 122.4701 | -0.16479
2192.6875 | 122.6166 | -122.4838 | 0.13275 | -0.0054933 | 0.074078 | 0.00090781 | 0.0026447 | 0.015528 | 0.0065711 | 0.00047844 | -0.011673 | 0.031121 | -0.010203 | 0.02117 | 0.0091731 | -0.0089742 | -0.004578 | -0.022888 | -0.009155 | 0.073242 | 0.1831 | 0.009155 | -0.1236 | -0.013733 | -0.032043 | -0.15106 | 0.082397 | 0.07782 | 0.009155 | -0.073242 | 122.493 | 122.3602 | 0.050354 | 122.4609 | 122.5571 | 0.19684 | -0.13733 | 122.493 | 122.4106 | -0.050354 | 122.4701 | 122.3328 | -0.07782 | -0.054931 | 122.6669 | 122.4792 | 122.4747 | -0.25635 | 122.5662 | 122.5616 | 122.4518 | -0.20599
2194.3906 | 122.6669 | -122.4609 | 0.10529 | -0.0054933 | 0.07301 | 0.0026168 | 0.0037127 | 0.014674 | 0.0040077 | -0.00016236 | -0.0040437 | 0.027062 | -0.010203 | 0.022452 | 0.0042597 | -0.0059836 | -0.004578 | 0.004578 | 0.018311 | 0.086975 | 0.14648 | 0 | -0.11902 | 0.036621 | 0.032043 | -0.07782 | 0.050354 | 0.050354 | 0.022888 | -0.050354 | 122.4609 | 122.3419 | 0.041198 | 122.4655 | 122.5479 | 0.20599 | -0.10986 | 122.4838 | 122.4106 | -0.054932 | 122.4976 | 122.3831 | -0.027466 | -0.054932 | 122.6074 | 122.4564 | 122.4792 | -0.22431 | 122.5113 | 122.5113 | 122.493 | -0.15564
2196.1562 | 122.6486 | -122.4701 | 0.10986 | -0.0054933 | 0.071087 | 0.0030442 | 0.0034991 | 0.013178 | -0.00090574 | 0.00047844 | -0.019302 | 0.02578 | -0.0084937 | 0.020956 | 0.0061823 | -0.0081198 | 0.068665 | 0.10986 | 0.14648 | 0.18768 | 0.11902 | 0.041199 | -0.07782 | 0.10986 | 0.14191 | 0.004578 | 0.004578 | 0.018311 | 0.050354 | -0.009155 | 122.5113 | 122.3923 | 0.009156 | 122.58 | 122.6578 | 0.2655 | -0.041198 | 122.5204 | 122.4609 | -0.10529 | 122.58 | 122.4747 | 0.013733 | -0.091552 | 122.5891 | 122.5388 | 122.6166 | -0.18768 | 122.4747 | 122.4884 | 122.612 | -0.11902
2197.9062 | 122.6715 | -122.4747 | 0.10529 | -0.0054933 | 0.068951 | 0.003685 | 0.0030719 | 0.013606 | 0.00058966 | 5.1244e-05 | -0.0040437 | 0.030052 | -0.0082801 | 0.020956 | 0.0055415 | -0.0091878 | 0.07782 | 0.10986 | 0.12817 | 0.16022 | 0.11902 | 0.050354 | -0.091553 | 0.10529 | 0.1236 | 0.022888 | 0.009155 | 0.041199 | 0.050354 | -0.041199 | 122.525 | 122.3831 | 0.013733 | 122.5845 | 122.6349 | 0.25177 | -0.027466 | 122.525 | 122.4335 | -0.096131 | 122.58 | 122.4976 | 0.064087 | -0.064087 | 122.5937 | 122.5525 | 122.6028 | -0.19684 | 122.4838 | 122.5159 | 122.5983 | -0.14649
2199.6094 | 122.6669 | -122.4701 | 0.12817 | 0.0021362 | 0.072583 | 0.0021896 | 0.0052081 | 0.014887 | 0.0022987 | 0.00069204 | -0.0040437 | 0.031121 | -0.0074255 | 0.020316 | 0.0066095 | -0.011324 | -0.013733 | -0.032043 | 0 | 0.07782 | 0.16479 | 0.009155 | -0.10071 | -0.004578 | -0.013733 | -0.12817 | 0.059509 | 0.082397 | 0 | -0.068665 | 122.4792 | 122.3694 | 0.036621 | 122.4381 | 122.5479 | 0.17853 | -0.14191 | 122.4701 | 122.4014 | -0.068665 | 122.4655 | 122.3419 | -0.059509 | -0.045777 | 122.6349 | 122.4564 | 122.4701 | -0.22888 | 122.5296 | 122.5525 | 122.4564 | -0.19684
2201.2969 | 122.7173 | -122.4564 | 0.10071 | -0.020752 | 0.07066 | 0.0047532 | 0.0099079 | 0.012965 | -0.0041101 | 0.00026484 | -0.0040437 | 0.026848 | -0.0093481 | 0.020956 | -0.00022634 | -0.007479 | 0.068665 | 0.13733 | 0.15564 | 0.16937 | 0.10986 | 0.022888 | -0.068665 | 0.082397 | 0.17395 | 0.018311 | 0.041199 | 0.045776 | 0.059509 | -0.036621 | 122.4792 | 122.3877 | 0.009155 | 122.5937 | 122.6257 | 0.23804 | -0.032043 | 122.5159 | 122.4197 | -0.059509 | 122.5388 | 122.4747 | 0.054932 | -0.054932 | 122.5662 | 122.525 | 122.612 | -0.16937 | 122.4976 | 122.5021 | 122.6303 | -0.13733
2203.0469 | 122.7219 | -122.4884 | 0.10986 | -0.013122 | 0.073224 | 0.0017624 | 0.0073443 | 0.014246 | -0.0011193 | -0.00016236 | -0.0040437 | 0.029412 | -0.0080665 | 0.023093 | 0.00041446 | -0.0094016 | -0.018311 | 0.004578 | 0.032043 | 0.10071 | 0.16022 | 0.004578 | -0.1236 | 0.004578 | 0.027466 | -0.10986 | 0.073242 | 0.086975 | 0.004578 | -0.068665 | 122.493 | 122.3648 | 0.050354 | 122.493 | 122.5891 | 0.2243 | -0.12817 | 122.493 | 122.4197 | -0.036621 | 122.493 | 122.3785 | -0.041198 | -0.022888 | 122.6486 | 122.4701 | 122.5204 | -0.23346 | 122.5616 | 122.5754 | 122.5159 | -0.17853
2204.7344 | 122.6807 | -122.4564 | 0.10071 | -0.0054933 | 0.068524 | 0.0030442 | 0.0049945 | 0.015101 | -0.0028283 | -0.0035804 | -0.019302 | 0.025994 | -0.0097755 | 0.023947 | 0.0038325 | -0.008547 | 0.009155 | 0.059509 | 0.07782 | 0.13275 | 0.1236 | 0.041199 | -0.091553 | 0.045776 | 0.073242 | -0.027466 | 0.041199 | 0.041199 | 0.045776 | -0.027466 | 122.4976 | 122.3648 | 0.022888 | 122.5159 | 122.5891 | 0.2243 | -0.091553 | 122.5021 | 122.4289 | -0.059509 | 122.5021 | 122.4289 | 0 | -0.059509 | 122.58 | 122.4655 | 122.5342 | -0.19226 | 122.4976 | 122.4976 | 122.5296 | -0.12817
2206.4844 | 122.7722 | -122.4335 | 0.082397 | -0.0054933 | 0.073437 | 5.3406e-05 | 0.0047809 | 0.018733 | 0.0042213 | -0.0018714 | -0.0040437 | 0.031334 | -0.0080665 | 0.022238 | 0.0076777 | -0.011538 | 0.009155 | 0.013733 | 0.018311 | 0.11444 | 0.19226 | 0.022888 | -0.10986 | 0.032043 | 0.054932 | -0.091553 | 0.086975 | 0.064087 | 0.018311 | -0.073242 | 122.4564 | 122.3236 | 0.10986 | 122.4472 | 122.5479 | 0.2243 | -0.073242 | 122.4518 | 122.3602 | 0.004578 | 122.4655 | 122.3419 | -0.018311 | -0.01831 | 122.6257 | 122.4426 | 122.4518 | -0.19226 | 122.5204 | 122.4976 | 122.4884 | -0.15564
2208.1719 | 122.644 | -122.4792 | 0.10986 | -0.013122 | 0.07536 | 0.0026168 | 0.0017901 | 0.016596 | 0.0037939 | -0.0010168 | -0.0040437 | 0.029198 | -0.0078529 | 0.022238 | 0.0070367 | -0.01047 | -0.027466 | -0.036621 | -0.009155 | 0.10071 | 0.16479 | 0 | -0.12817 | -0.009155 | -0.022888 | -0.17395 | 0.073242 | 0.082397 | 0.004578 | -0.064087 | 122.4792 | 122.3511 | 0.054932 | 122.4426 | 122.58 | 0.22888 | -0.13733 | 122.4838 | 122.4152 | -0.036621 | 122.4701 | 122.3053 | -0.10986 | -0.027466 | 122.644 | 122.4518 | 122.4701 | -0.23804 | 122.5525 | 122.5616 | 122.4564 | -0.17395
2209.9219 | 122.6761 | -122.4838 | 0.091553 | -0.013122 | 0.064892 | 0.0038986 | 0.0039265 | 0.016383 | -0.0068871 | -0.00080316 | -0.0040437 | 0.025353 | -0.0089209 | 0.01882 | 0.0019099 | -0.0059836 | 0.004578 | 0.059509 | 0.09613 | 0.12817 | 0.13733 | 0.045776 | -0.10986 | 0.041199 | 0.07782 | -0.022888 | 0.045776 | 0.054932 | 0.027466 | -0.041199 | 122.5296 | 122.374 | 0.045776 | 122.5433 | 122.612 | 0.23804 | -0.086975 | 122.5113 | 122.4426 | -0.045777 | 122.525 | 122.4609 | 0.018311 | -0.036621 | 122.6212 | 122.4884 | 122.58 | -0.20142 | 122.5296 | 122.5388 | 122.5616 | -0.13275
2211.6562 | 122.7264 | -122.4747 | 0.086975 | -0.0054933 | 0.071728 | 0.001976 | 0.0086261 | 0.015742 | -0.00047854 | -0.0033668 | -0.0040437 | 0.026634 | -0.0076393 | 0.020956 | 0.0012689 | -0.010683 | 0.09613 | 0.1236 | 0.14648 | 0.16479 | 0.12817 | 0.036621 | -0.07782 | 0.07782 | 0.15564 | 0.013733 | 0.032043 | 0.032043 | 0.045776 | -0.036621 | 122.5113 | 122.3969 | 0.041199 | 122.5983 | 122.6395 | 0.24261 | 0.009155 | 122.5204 | 122.438 | -0.054932 | 122.5525 | 122.4884 | 0.050354 | -0.054932 | 122.6028 | 122.5708 | 122.6212 | -0.16479 | 122.5067 | 122.5067 | 122.6303 | -0.1236
2213.4062 | 122.6898 | -122.4655 | 0.10071 | -0.0054933 | 0.072155 | 0.0015488 | 0.0037127 | 0.015528 | 0.0022987 | 0.001333 | -0.0040437 | 0.028771 | -0.0095619 | 0.021597 | 0.0051141 | -0.010256 | 0.09613 | 0.064087 | 0.10529 | 0.16479 | 0.14648 | 0.050354 | -0.091553 | 0.11902 | 0.12817 | -0.009155 | 0.018311 | 0.036621 | 0.036621 | -0.004578 | 122.5159 | 122.374 | 0.045776 | 122.5296 | 122.6303 | 0.25635 | -0.004578 | 122.5021 | 122.4609 | -0.082397 | 122.5845 | 122.4564 | -0.004577 | -0.064087 | 122.612 | 122.5616 | 122.5708 | -0.19226 | 122.4838 | 122.5021 | 122.5937 | -0.10529
2215.0938 | 122.7493 | -122.493 | 0.064087 | -0.013122 | 0.074292 | 0.0026168 | 0.0084125 | 0.016383 | 0.00037606 | -0.0025122 | -0.0040437 | 0.031121 | -0.0074255 | 0.025015 | 0.0014825 | -0.010683 | -0.004578 | -0.013733 | 0.013733 | 0.073242 | 0.18768 | 0.013733 | -0.14648 | -0.032043 | 0.018311 | -0.10986 | 0.091553 | 0.091553 | -0.009155 | -0.091553 | 122.5067 | 122.3465 | 0.1236 | 122.4792 | 122.5662 | 0.21973 | -0.068665 | 122.4838 | 122.4014 | 0.027466 | 122.4609 | 122.3831 | -0.01831 | 0.027466 | 122.6807 | 122.4884 | 122.5067 | -0.21057 | 122.5845 | 122.5845 | 122.5113 | -0.15564
2216.8281 | 122.7264 | -122.4564 | 0.10071 | 0.0021362 | 0.072369 | 0.0013352 | 0.0086261 | 0.016383 | -0.00069214 | -0.0016578 | -0.011673 | 0.028343 | -0.0067847 | 0.024802 | 0.0012689 | -0.010042 | 0.009155 | 0.022888 | 0.045776 | 0.11444 | 0.15564 | 0.022888 | -0.11444 | -0.009155 | 0.041199 | -0.10529 | 0.082397 | 0.091553 | 0.004578 | -0.073242 | 122.4792 | 122.3419 | 0.054932 | 122.4792 | 122.5708 | 0.22888 | -0.091553 | 122.4609 | 122.3831 | -0.018311 | 122.4472 | 122.3511 | -0.032044 | -0.009155 | 122.612 | 122.4655 | 122.5021 | -0.21515 | 122.5388 | 122.5479 | 122.4976 | -0.17395
2218.5 | 122.6486 | -122.4701 | 0.11902 | -0.013122 | 0.067883 | 0.0013352 | 0.0013629 | 0.015101 | -0.0032555 | -0.0025122 | -0.011673 | 0.026207 | -0.011271 | 0.020529 | 0.0036189 | -0.0072652 | 0.045776 | 0.073242 | 0.10071 | 0.12817 | 0.11902 | 0.045776 | -0.082397 | 0.045776 | 0.082397 | -0.032043 | 0.027466 | 0.032043 | 0.032043 | -0.032043 | 122.5159 | 122.3877 | 0 | 122.5433 | 122.5983 | 0.21057 | -0.073243 | 122.5021 | 122.4381 | -0.091553 | 122.5159 | 122.4381 | 0 | -0.086976 | 122.5891 | 122.5159 | 122.5708 | -0.20142 | 122.4976 | 122.5021 | 122.5525 | -0.15106
2220.1875 | 122.6303 | -122.4976 | 0.12817 | -0.020752 | 0.068524 | 0.0028306 | 0.00072207 | 0.017237 | -0.00069214 | -0.0027258 | -0.0040437 | 0.026634 | -0.010203 | 0.020743 | 0.0057551 | -0.0083334 | 0.082397 | 0.10986 | 0.11444 | 0.13733 | 0.12817 | 0.059509 | -0.073242 | 0.07782 | 0.10071 | 0.004578 | 0.022888 | 0.041199 | 0.027466 | -0.041199 | 122.5571 | 122.4243 | 0 | 122.6074 | 122.6349 | 0.21057 | -0.045777 | 122.525 | 122.4564 | -0.10529 | 122.5754 | 122.5021 | 0.045777 | -0.086975 | 122.6257 | 122.58 | 122.612 | -0.20142 | 122.5204 | 122.5388 | 122.5983 | -0.16937
2221.9219 | 122.6944 | -122.5067 | 0.13275 | -0.013122 | 0.075787 | 0.0017624 | 0.0045673 | 0.016383 | 0.0029395 | -0.0010168 | -0.011673 | 0.030052 | -0.0078529 | 0.022238 | 0.0081049 | -0.0098288 | 0.009155 | -0.018311 | -0.009155 | 0.082397 | 0.17395 | 0.027466 | -0.13275 | 0.009155 | -0.004578 | -0.11444 | 0.073242 | 0.068665 | 0.004578 | -0.073242 | 122.5342 | 122.374 | 0.041199 | 122.4884 | 122.5891 | 0.21515 | -0.1236 | 122.5113 | 122.4335 | -0.059509 | 122.5159 | 122.3923 | -0.041199 | -0.064086 | 122.6807 | 122.5159 | 122.4976 | -0.2655 | 122.58 | 122.5754 | 122.5021 | -0.20599
2223.6875 | 122.7676 | -122.4701 | 0.086975 | 0.0097657 | 0.071728 | 0.0013352 | 0.0069171 | 0.015742 | 0.0025123 | 0.00047844 | -0.011673 | 0.031761 | -0.0093481 | 0.022665 | 0.0057551 | -0.010897 | 0.041199 | 0.032043 | 0.054932 | 0.12817 | 0.14648 | 0.009155 | -0.11444 | 0.041199 | 0.07782 | -0.073242 | 0.073242 | 0.082397 | 0.027466 | -0.050354 | 122.4792 | 122.3557 | 0.059509 | 122.5021 | 122.5983 | 0.24262 | -0.045776 | 122.4976 | 122.4197 | -0.013733 | 122.5113 | 122.3969 | -0.022888 | -0.004578 | 122.6166 | 122.5113 | 122.525 | -0.20142 | 122.5433 | 122.5525 | 122.5479 | -0.13733
2225.375 | 122.8043 | -122.4701 | 0.091553 | -0.0054933 | 0.077069 | 0.00090781 | 0.0096943 | 0.015528 | 0.0035803 | -0.0014442 | -0.011673 | 0.031121 | -0.0050757 | 0.024588 | 0.0025507 | -0.010897 | 0 | 0.004578 | 0.013733 | 0.10071 | 0.16479 | 0.004578 | -0.11902 | 0.032043 | 0.054932 | -0.086975 | 0.068665 | 0.073242 | 0.009155 | -0.064087 | 122.4747 | 122.3511 | 0.073242 | 122.4747 | 122.5708 | 0.21973 | -0.091553 | 122.4792 | 122.406 | -0.022888 | 122.5021 | 122.3831 | -0.022888 | -0.018311 | 122.6349 | 122.4701 | 122.4838 | -0.21057 | 122.5388 | 122.5433 | 122.525 | -0.15564
2227.1094 | 122.7951 | -122.4426 | 0.082397 | -0.0054933 | 0.072583 | 5.3406e-05 | 0.0041401 | 0.017878 | 0.00058966 | -0.0010168 | -0.0040437 | 0.033043 | -0.0057165 | 0.023093 | 0.0061823 | -0.0091878 | 0.009155 | 0.004578 | 0.032043 | 0.1236 | 0.16937 | 0.013733 | -0.11902 | 0.045776 | 0.091553 | -0.07782 | 0.064087 | 0.073242 | 0.032043 | -0.054932 | 122.4564 | 122.3236 | 0.086976 | 122.4472 | 122.5662 | 0.24261 | -0.073242 | 122.4747 | 122.3877 | -0.01831 | 122.4884 | 122.3648 | -0.022888 | -0.009155 | 122.612 | 122.4518 | 122.4747 | -0.20142 | 122.5067 | 122.5159 | 122.5342 | -0.13733
2228.875 | 122.7722 | -122.438 | 0.082397 | -0.0054933 | 0.067242 | 0.00069421 | 0.0081989 | 0.013178 | -0.0049645 | -0.0027258 | -0.0040437 | 0.023644 | -0.0087073 | 0.020743 | 0.0021235 | -0.0083334 | 0.018311 | 0.10529 | 0.11902 | 0.15564 | 0.14648 | 0.036621 | -0.07782 | 0.07782 | 0.16022 | 0.036621 | 0.018311 | 0.045776 | 0.032043 | -0.027466 | 122.4747 | 122.3602 | 0.064087 | 122.5433 | 122.5937 | 0.23346 | -0.064086 | 122.4701 | 122.4106 | -0.064086 | 122.5159 | 122.4747 | 0.064087 | -0.036621 | 122.5845 | 122.4564 | 122.5571 | -0.16022 | 122.4564 | 122.4838 | 122.5983 | -0.10986
2230.5625 | 122.7814 | -122.4609 | 0.086975 | -0.020752 | 0.070874 | 0.005394 | 0.0054217 | 0.01446 | -0.0030419 | -0.0035804 | -0.0040437 | 0.026207 | -0.0097755 | 0.022452 | 0.0016963 | -0.010042 | 0.068665 | 0.15106 | 0.15106 | 0.1831 | 0.13275 | 0.054932 | -0.086975 | 0.10529 | 0.19684 | 0.054932 | 0.018311 | 0.041199 | 0.050354 | -0.036621 | 122.5159 | 122.374 | 0.045776 | 122.612 | 122.644 | 0.27008 | -0.01831 | 122.5113 | 122.4243 | -0.068664 | 122.5662 | 122.5159 | 0.091553 | -0.045776 | 122.5937 | 122.5296 | 122.612 | -0.17395 | 122.4792 | 122.5021 | 122.6578 | -0.1236
2232.3125 | 122.644 | -122.4976 | 0.1236 | -0.0054933 | 0.071942 | 0.001976 | 0.0037127 | 0.01446 | -0.0030419 | -0.0035804 | -0.011673 | 0.027703 | -0.0093481 | 0.020316 | 0.0019099 | -0.008547 | 0.073242 | 0.09613 | 0.11444 | 0.13733 | 0.1236 | 0.045776 | -0.09613 | 0.054932 | 0.091553 | -0.022888 | 0.041199 | 0.054932 | 0.045776 | -0.027466 | 122.5433 | 122.4014 | 0 | 122.5937 | 122.6349 | 0.23346 | -0.050354 | 122.5433 | 122.4701 | -0.082397 | 122.5525 | 122.4747 | 0.004578 | -0.068664 | 122.6212 | 122.5708 | 122.612 | -0.21973 | 122.5388 | 122.5525 | 122.5891 | -0.15106
2234 | 122.6624 | -122.5021 | 0.12817 | -0.013122 | 0.074292 | 0.00090781 | 0.0022175 | 0.016383 | 0.0069983 | -0.0016578 | 0.0035858 | 0.032402 | -0.011057 | 0.02352 | 0.0066095 | -0.0096152 | 0.018311 | -0.027466 | -0.013733 | 0.086975 | 0.16022 | 0.018311 | -0.11902 | -0.004578 | -0.022888 | -0.14191 | 0.082397 | 0.09613 | 0 | -0.082397 | 122.5204 | 122.3831 | 0.032043 | 122.4747 | 122.5891 | 0.20599 | -0.10986 | 122.5021 | 122.4197 | -0.045777 | 122.4976 | 122.3602 | -0.05951 | -0.032044 | 122.6624 | 122.5204 | 122.4884 | -0.24719 | 122.5845 | 122.5983 | 122.4792 | -0.21057
2235.75 | 122.7127 | -122.4701 | 0.10529 | -0.013122 | 0.07066 | 0.0038986 | 0.0049945 | 0.01211 | -0.0045373 | -0.0010168 | -0.019302 | 0.025994 | -0.010203 | 0.020743 | 0.0034051 | -0.007479 | 0.009155 | 0.036621 | 0.073242 | 0.14191 | 0.13275 | 0.036621 | -0.09613 | 0.045776 | 0.091553 | 0 | 0.036621 | 0.041199 | 0.032043 | -0.050354 | 122.5067 | 122.374 | 0.027465 | 122.5067 | 122.612 | 0.23804 | -0.096131 | 122.5021 | 122.4197 | -0.068665 | 122.5159 | 122.4701 | 0.050354 | -0.064087 | 122.6028 | 122.4792 | 122.5433 | -0.20142 | 122.5067 | 122.5113 | 122.5616 | -0.15564
2237.4375 | 122.7402 | -122.4838 | 0.091553 | -0.013122 | 0.071515 | 0.0026168 | 0.0075581 | 0.014674 | -0.00047854 | -0.0027258 | -0.0040437 | 0.028984 | -0.0087073 | 0.02352 | 0.0019099 | -0.010683 | 0.032043 | 0.018311 | 0.036621 | 0.09613 | 0.16022 | 0.013733 | -0.10071 | -0.009155 | 0.045776 | -0.10071 | 0.068665 | 0.068665 | -0.013733 | -0.07782 | 122.4976 | 122.3831 | 0.068664 | 122.5021 | 122.58 | 0.19684 | -0.05951 | 122.4701 | 122.406 | -0.022888 | 122.4747 | 122.3831 | -0.022888 | -0.022888 | 122.644 | 122.5159 | 122.5204 | -0.19226 | 122.5525 | 122.5525 | 122.5296 | -0.16937
2239.1875 | 122.7905 | -122.4609 | 0.073242 | -0.013122 | 0.07301 | 0.0024032 | 0.0039265 | 0.016596 | 0.0022987 | -0.00080316 | -0.0040437 | 0.031121 | -0.0087073 | 0.022238 | 0.0072505 | -0.010256 | 0.054932 | 0.041199 | 0.050354 | 0.1236 | 0.1831 | 0.027466 | -0.12817 | 0.054932 | 0.082397 | -0.07782 | 0.059509 | 0.054932 | 0.022888 | -0.036621 | 122.4884 | 122.3328 | 0.10986 | 122.5021 | 122.5845 | 0.25177 | -0.01831 | 122.4838 | 122.4243 | -0.013733 | 122.5159 | 122.3831 | -0.041199 | -0.01831 | 122.644 | 122.5159 | 122.5113 | -0.20142 | 122.5204 | 122.5159 | 122.5433 | -0.10986
2240.9531 | 122.6761 | -122.5296 | 0.11444 | -0.013122 | 0.075573 | 0.0034714 | 0.0041401 | 0.014887 | 0.0063575 | 0.00047844 | -0.0040437 | 0.032829 | -0.0072119 | 0.022238 | 0.0076777 | -0.008547 | 0.027466 | -0.004578 | 0.027466 | 0.11444 | 0.16479 | 0.009155 | -0.10071 | 0 | 0.004578 | -0.13733 | 0.050354 | 0.054932 | 0.013733 | -0.054932 | 122.5388 | 122.4289 | 0.050354 | 122.525 | 122.644 | 0.21515 | -0.086975 | 122.5433 | 122.4747 | -0.064087 | 122.5296 | 122.3923 | -0.082397 | -0.059509 | 122.6944 | 122.5571 | 122.5571 | -0.21515 | 122.58 | 122.5845 | 122.5342 | -0.16937
2242.7031 | 122.644 | -122.525 | 0.11444 | -0.0054933 | 0.067456 | 0.00090781 | 0.0043537 | 0.013606 | -0.0021875 | -0.00016236 | -0.011673 | 0.024285 | -0.0087073 | 0.022879 | 0.0021235 | -0.008547 | 0.059509 | 0.11902 | 0.1236 | 0.15106 | 0.12817 | 0.045776 | -0.07782 | 0.059509 | 0.10529 | -0.009155 | 0.036621 | 0.041199 | 0.027466 | -0.045776 | 122.5708 | 122.4472 | 0.013733 | 122.644 | 122.6761 | 0.22888 | -0.054932 | 122.5525 | 122.4792 | -0.07782 | 122.5845 | 122.5159 | 0.036621 | -0.073242 | 122.6532 | 122.5845 | 122.6486 | -0.19226 | 122.5616 | 122.5662 | 122.6303 | -0.16022
2244.375 | 122.731 | -122.493 | 0.11444 | -0.013122 | 0.076855 | -0.00058739 | 0.0064899 | 0.019373 | 0.0029395 | 0.00026484 | -0.011673 | 0.031975 | -0.0067847 | 0.02352 | 0.0044733 | -0.010042 | 0.07782 | 0.054932 | 0.064087 | 0.13733 | 0.14648 | 0.022888 | -0.11444 | 0.059509 | 0.07782 | -0.086975 | 0.073242 | 0.073242 | 0.018311 | -0.059509 | 122.5159 | 122.3785 | 0.032043 | 122.5479 | 122.6303 | 0.25177 | -0.036621 | 122.5113 | 122.4335 | -0.041199 | 122.5525 | 122.406 | -0.027466 | -0.041199 | 122.6395 | 122.5708 | 122.5571 | -0.22888 | 122.5662 | 122.5662 | 122.5708 | -0.17395
2246.125 | 122.6532 | -122.525 | 0.11902 | -0.0054933 | 0.068524 | 0.0015488 | 0.0073443 | 0.015101 | -0.0060327 | -0.00037596 | -0.0040437 | 0.026207 | -0.0078529 | 0.020956 | 0.0023371 | -0.0055564 | 0.050354 | 0.09613 | 0.12817 | 0.15106 | 0.12817 | 0.045776 | -0.068665 | 0.036621 | 0.09613 | -0.009155 | 0.027466 | 0.032043 | 0.022888 | -0.027466 | 122.5708 | 122.4564 | 0.009155 | 122.6212 | 122.6761 | 0.21973 | -0.068665 | 122.5479 | 122.4976 | -0.091553 | 122.5616 | 122.5159 | 0.018311 | -0.086976 | 122.6532 | 122.5754 | 122.6532 | -0.18768 | 122.5525 | 122.5571 | 122.6212 | -0.14649
2247.875 | 122.7585 | -122.4884 | 0.09613 | -0.0054933 | 0.073437 | 5.3406e-05 | 0.0075581 | 0.013819 | -0.0013329 | -0.0012306 | -0.011673 | 0.027916 | -0.0084937 | 0.025443 | 0.00084166 | -0.0083334 | -0.013733 | -0.004578 | 0.022888 | 0.073242 | 0.16479 | 0.009155 | -0.14191 | -0.022888 | 0.036621 | -0.10986 | 0.068665 | 0.07782 | 0.004578 | -0.082397 | 122.4976 | 122.3465 | 0.068665 | 122.4838 | 122.5616 | 0.21515 | -0.10986 | 122.493 | 122.406 | -0.027465 | 122.4655 | 122.3785 | -0.027466 | -0.01831 | 122.6532 | 122.4747 | 122.5113 | -0.23804 | 122.5571 | 122.5662 | 122.525 | -0.17853
2249.625 | 122.6624 | -122.4838 | 0.10529 | -0.0054933 | 0.072155 | 0.0011216 | 0.0020039 | 0.014674 | 0.00080326 | 0.0034692 | -0.011673 | 0.026421 | -0.010203 | 0.019034 | 0.0051141 | -0.011751 | 0.082397 | 0.1236 | 0.13275 | 0.19226 | 0.13275 | 0.059509 | -0.073242 | 0.1236 | 0.13275 | 0.013733 | 0.032043 | 0.036621 | 0.045776 | -0.018311 | 122.5433 | 122.4106 | 0.027465 | 122.6074 | 122.6761 | 0.2655 | -0.022889 | 122.5296 | 122.4655 | -0.073243 | 122.6074 | 122.4976 | 0.032044 | -0.068665 | 122.6166 | 122.5662 | 122.6166 | -0.17853 | 122.5159 | 122.5204 | 122.6166 | -0.1236
2251.3125 | 122.7997 | -122.4792 | 0.07782 | -0.0054933 | 0.071728 | 0.0026168 | 0.0088397 | 0.012538 | -0.0051781 | -0.0031532 | -0.011673 | 0.025139 | -0.0087073 | 0.022025 | -0.00065374 | -0.0091878 | 0.064087 | 0.10986 | 0.14648 | 0.16022 | 0.1236 | 0.050354 | -0.082397 | 0.086975 | 0.15106 | 0.059509 | 0.032043 | 0.041199 | 0.050354 | -0.032043 | 122.5296 | 122.3969 | 0.045776 | 122.5891 | 122.6395 | 0.24261 | -0.013733 | 122.5296 | 122.4472 | -0.045777 | 122.5662 | 122.5388 | 0.091552 | -0.036621 | 122.6028 | 122.5433 | 122.6257 | -0.16022 | 122.5113 | 122.5204 | 122.6303 | -0.10986
2253.0625 | 122.7997 | -122.4655 | 0.086975 | -0.020752 | 0.071087 | 0.0030442 | 0.0041401 | 0.014246 | -0.0030419 | -0.0031532 | -0.0040437 | 0.026421 | -0.0089209 | 0.022238 | 0.0016963 | -0.011751 | 0.054932 | 0.10071 | 0.12817 | 0.15564 | 0.11902 | 0.041199 | -0.091553 | 0.086975 | 0.15564 | 0.041199 | 0.032043 | 0.041199 | 0.041199 | -0.036621 | 122.5067 | 122.374 | 0.032044 | 122.5662 | 122.6212 | 0.24719 | -0.032043 | 122.5067 | 122.4289 | -0.054932 | 122.5525 | 122.5067 | 0.07782 | -0.045776 | 122.5845 | 122.5204 | 122.5937 | -0.17853 | 122.4976 | 122.5067 | 122.6212 | -0.1236
2254.8281 | 122.7219 | -122.4976 | 0.11444 | -0.013122 | 0.07066 | 0.0028306 | 0.0011493 | 0.015315 | 0.0040077 | -0.0027258 | -0.0040437 | 0.030693 | -0.010843 | 0.022452 | 0.0072505 | -0.0094016 | 0.073242 | 0.068665 | 0.09613 | 0.15106 | 0.13733 | 0.041199 | -0.086975 | 0.10986 | 0.10986 | -0.004578 | 0.018311 | 0.036621 | 0.050354 | -0.032043 | 122.5388 | 122.4106 | 0.022888 | 122.5662 | 122.6486 | 0.23804 | -0.041199 | 122.5479 | 122.4655 | -0.09613 | 122.6074 | 122.493 | 0.027465 | -0.07782 | 122.6349 | 122.5708 | 122.5937 | -0.20142 | 122.5159 | 122.5342 | 122.6074 | -0.14648
2256.5156 | 122.7448 | -122.493 | 0.10071 | -0.013122 | 0.074078 | 0.0015488 | 0.0052081 | 0.017664 | -0.00069214 | -0.0040076 | -0.019302 | 0.029198 | -0.0078529 | 0.020102 | 0.0019099 | -0.0096152 | 0 | 0.036621 | 0.064087 | 0.11902 | 0.15564 | 0.018311 | -0.11444 | -0.013733 | 0.032043 | -0.086975 | 0.068665 | 0.073242 | -0.004578 | -0.068665 | 122.5113 | 122.3785 | 0.054932 | 122.5296 | 122.612 | 0.23346 | -0.10071 | 122.4884 | 122.4243 | -0.032043 | 122.4792 | 122.406 | -0.01831 | -0.027466 | 122.6486 | 122.493 | 122.5571 | -0.21515 | 122.5616 | 122.5662 | 122.525 | -0.16937
2258.2656 | 122.6761 | -122.5296 | 0.1236 | -0.0054933 | 0.070233 | 0.00026701 | 0.0052081 | 0.013392 | -0.0021875 | -0.0027258 | -0.0040437 | 0.028771 | -0.0080665 | 0.02117 | 0.0025507 | -0.0061972 | 0.050354 | 0.054932 | 0.10529 | 0.13733 | 0.1236 | 0.041199 | -0.082397 | 0.045776 | 0.09613 | -0.027466 | 0.045776 | 0.036621 | 0.027466 | -0.050354 | 122.5708 | 122.4472 | 0 | 122.5845 | 122.6669 | 0.21973 | -0.073242 | 122.5571 | 122.4792 | -0.07782 | 122.5754 | 122.5021 | 0.022888 | -0.086975 | 122.6532 | 122.58 | 122.6349 | -0.20599 | 122.5754 | 122.5662 | 122.6257 | -0.17395
2260.0156 | 122.6669 | -122.5204 | 0.12817 | 0.0021362 | 0.070874 | 0.00069421 | 0.0043537 | 0.015528 | -0.00026494 | -0.0014442 | 0.0035858 | 0.029839 | -0.010203 | 0.023306 | 0.0053279 | -0.010683 | 0.091553 | 0.11902 | 0.15106 | 0.14648 | 0.12817 | 0.054932 | -0.082397 | 0.10071 | 0.11902 | 0.004578 | 0.022888 | 0.032043 | 0.027466 | -0.032043 | 122.5754 | 122.4381 | 0 | 122.6395 | 122.6669 | 0.22888 | -0.036621 | 122.5479 | 122.4884 | -0.10529 | 122.6212 | 122.525 | 0.036621 | -0.096131 | 122.6486 | 122.612 | 122.6715 | -0.21057 | 122.5433 | 122.5525 | 122.6395 | -0.16022
2261.7031 | 122.7768 | -122.4884 | 0.10529 | -0.013122 | 0.071728 | 0.0021896 | 0.0067035 | 0.016383 | 0.0018713 | -0.0025122 | -0.019302 | 0.031548 | -0.0095619 | 0.021384 | 0.0038325 | -0.011111 | -0.004578 | -0.009155 | -0.004578 | 0.086975 | 0.1831 | 0.004578 | -0.11444 | -0.004578 | 0.027466 | -0.11902 | 0.068665 | 0.091553 | -0.018311 | -0.073242 | 122.493 | 122.374 | 0.077819 | 122.4792 | 122.5754 | 0.20142 | -0.10986 | 122.4701 | 122.4152 | -0.036621 | 122.4838 | 122.3694 | -0.045777 | -0.013733 | 122.6715 | 122.4838 | 122.4838 | -0.21973 | 122.5571 | 122.58 | 122.5159 | -0.17853
2263.4531 | 122.8134 | -122.4976 | 0.082397 | -0.013122 | 0.070874 | 0.0026168 | 0.0069171 | 0.016383 | 0.0029395 | -0.0012306 | -0.0040437 | 0.031548 | -0.0087073 | 0.022238 | 0.0046869 | -0.011324 | -0.009155 | -0.009155 | 0.004578 | 0.091553 | 0.17853 | 0 | -0.1236 | 0 | 0.041199 | -0.10529 | 0.068665 | 0.068665 | 0.022888 | -0.050354 | 122.4976 | 122.374 | 0.096131 | 122.4884 | 122.5891 | 0.21515 | -0.091552 | 122.5204 | 122.4472 | -0.013732 | 122.4976 | 122.3923 | -0.054932 | -0.013732 | 122.6761 | 122.4884 | 122.5021 | -0.20599 | 122.5662 | 122.5662 | 122.5388 | -0.13275
2265.1406 | 122.7722 | -122.4701 | 0.091553 | 0.0021362 | 0.072369 | 0.0032578 | 0.0047809 | 0.015315 | -0.0019739 | 0.00047844 | -0.019302 | 0.025566 | -0.0097755 | 0.02117 | 0.0021235 | -0.0066244 | 0.091553 | 0.14648 | 0.14648 | 0.17395 | 0.10986 | 0.050354 | -0.068665 | 0.10986 | 0.17853 | 0.022888 | 0.036621 | 0.041199 | 0.036621 | -0.018311 | 122.5204 | 122.4014 | 0.01831 | 122.6166 | 122.644 | 0.24261 | 0 | 122.5067 | 122.4518 | -0.054932 | 122.58 | 122.493 | 0.041199 | -0.050354 | 122.58 | 122.5616 | 122.6166 | -0.16022 | 122.5067 | 122.5113 | 122.6486 | -0.10986
2266.875 | 122.7951 | -122.4838 | 0.091553 | -0.013122 | 0.070874 | 0.0024032 | 0.0062763 | 0.01681 | -0.0024011 | -0.0022986 | -0.011673 | 0.027916 | -0.0084937 | 0.02117 | 0.0010553 | -0.010683 | 0.086975 | 0.14648 | 0.16022 | 0.16022 | 0.12817 | 0.059509 | -0.073242 | 0.09613 | 0.17395 | 0.036621 | 0.036621 | 0.050354 | 0.054932 | -0.045776 | 122.5433 | 122.4106 | 0.036621 | 122.6303 | 122.644 | 0.23346 | -0.004578 | 122.5388 | 122.438 | -0.054932 | 122.58 | 122.5204 | 0.082397 | -0.041199 | 122.612 | 122.5708 | 122.644 | -0.16479 | 122.5204 | 122.5342 | 122.6578 | -0.13733
2268.6094 | 122.7951 | -122.4884 | 0.068665 | -0.013122 | 0.076642 | -0.00058739 | 0.0058491 | 0.017024 | 0.0037939 | 0.00026484 | -0.011673 | 0.033684 | -0.0065711 | 0.024161 | 0.0057551 | -0.011324 | 0.059509 | 0.045776 | 0.041199 | 0.13275 | 0.15564 | 0.027466 | -0.13275 | 0.07782 | 0.073242 | -0.064087 | 0.068665 | 0.064087 | 0.013733 | -0.054932 | 122.5159 | 122.3557 | 0.086975 | 122.5342 | 122.6212 | 0.2655 | -0.009156 | 122.5021 | 122.4335 | 0 | 122.5662 | 122.4243 | -0.009155 | -0.004578 | 122.644 | 122.5479 | 122.5296 | -0.20142 | 122.5571 | 122.5525 | 122.5616 | -0.1236
2270.3594 | 122.7219 | -122.5204 | 0.10071 | -0.0054933 | 0.071515 | 0.0028306 | 0.0015765 | 0.014033 | 0.0033667 | -0.00016236 | -0.011673 | 0.030693 | -0.012339 | 0.022665 | 0.0070367 | -0.008547 | 0.032043 | 0.004578 | 0.032043 | 0.086975 | 0.14648 | 0.022888 | -0.10529 | 0.036621 | 0.027466 | -0.059509 | 0.041199 | 0.068665 | 0.027466 | -0.041199 | 122.5433 | 122.4152 | 0.045776 | 122.525 | 122.6074 | 0.19226 | -0.068665 | 122.5479 | 122.4792 | -0.059509 | 122.5571 | 122.4609 | -0.01831 | -0.032043 | 122.6669 | 122.5525 | 122.5525 | -0.20599 | 122.5616 | 122.5891 | 122.5479 | -0.14191
2272.1094 | 122.6761 | -122.5204 | 0.1236 | -0.0054933 | 0.072583 | 0.0015488 | 0.0056355 | 0.015742 | -0.0043237 | 5.1244e-05 | -0.011673 | 0.027703 | -0.0087073 | 0.019888 | 0.0038325 | -0.007479 | 0.036621 | 0.082397 | 0.09613 | 0.14191 | 0.1236 | 0.059509 | -0.068665 | 0.032043 | 0.09613 | -0.022888 | 0.027466 | 0.045776 | 0.036621 | -0.036621 | 122.58 | 122.4518 | 0 | 122.6028 | 122.6624 | 0.21057 | -0.086975 | 122.5571 | 122.4838 | -0.09613 | 122.5525 | 122.4976 | 0.013733 | -0.07782 | 122.644 | 122.5571 | 122.6166 | -0.19226 | 122.5479 | 122.5662 | 122.6166 | -0.16022
2273.875 | 122.8134 | -122.4838 | 0.091553 | -0.020752 | 0.074505 | 0.0013352 | 0.0086261 | 0.018092 | 0.00016226 | 0.00069204 | -0.011673 | 0.031761 | -0.0095619 | 0.022665 | 0.0031915 | -0.010042 | -0.004578 | -0.018311 | -0.004578 | 0.082397 | 0.17395 | 0.004578 | -0.11444 | -0.013733 | 0.018311 | -0.1236 | 0.068665 | 0.07782 | 0.013733 | -0.073242 | 122.4884 | 122.3694 | 0.082397 | 122.4655 | 122.5662 | 0.19684 | -0.096131 | 122.4976 | 122.4106 | -0.022888 | 122.4701 | 122.3602 | -0.050354 | -0.013733 | 122.6578 | 122.4792 | 122.4792 | -0.20599 | 122.5525 | 122.5616 | 122.5021 | -0.16479
2275.5625 | 122.7264 | -122.5159 | 0.10071 | -0.013122 | 0.073224 | -0.00058739 | 0.0056355 | 0.017878 | 0.0035803 | -0.00058956 | 0.0035858 | 0.030907 | -0.0063575 | 0.022665 | 0.0051141 | -0.011324 | 0.064087 | 0.07782 | 0.054932 | 0.13275 | 0.14648 | 0.022888 | -0.086975 | 0.050354 | 0.068665 | -0.091553 | 0.045776 | 0.068665 | 0 | -0.036621 | 122.5388 | 122.4289 | 0.045776 | 122.5937 | 122.6486 | 0.21973 | -0.036621 | 122.5159 | 122.4792 | -0.054932 | 122.5662 | 122.4243 | -0.054932 | -0.032043 | 122.6624 | 122.58 | 122.5708 | -0.18768 | 122.5616 | 122.5845 | 122.5845 | -0.13733
2277.2969 | 122.7173 | -122.5479 | 0.086975 | -0.013122 | 0.073224 | 0.0013352 | 0.0060627 | 0.016169 | 0.0055029 | -0.0010168 | 0.0035858 | 0.030052 | -0.0089209 | 0.021811 | 0.0061823 | -0.010042 | 0.064087 | 0.068665 | 0.054932 | 0.12817 | 0.15106 | 0.004578 | -0.10071 | 0.041199 | 0.082397 | -0.09613 | 0.050354 | 0.059509 | 0.009155 | -0.064087 | 122.5525 | 122.4472 | 0.064087 | 122.6166 | 122.6761 | 0.22888 | -0.022888 | 122.5571 | 122.4838 | -0.036621 | 122.5891 | 122.4518 | -0.032043 | -0.027466 | 122.699 | 122.612 | 122.6028 | -0.18768 | 122.5983 | 122.6074 | 122.6303 | -0.15106
2279.0625 | 122.7081 | -122.5342 | 0.10986 | -0.013122 | 0.070233 | 0.0026168 | 0.0039265 | 0.014033 | 0.00080326 | 0.0015466 | 0.0035858 | 0.028984 | -0.0078529 | 0.020743 | 0.0053279 | -0.0061972 | 0.068665 | 0.11902 | 0.13275 | 0.16937 | 0.15106 | 0.059509 | -0.086975 | 0.10529 | 0.14191 | 0.018311 | 0.036621 | 0.032043 | 0.045776 | -0.027466 | 122.5937 | 122.4472 | 0.041199 | 122.6532 | 122.7036 | 0.25635 | -0.041198 | 122.58 | 122.5067 | -0.073242 | 122.6395 | 122.5525 | 0.045777 | -0.07782 | 122.6852 | 122.6028 | 122.6669 | -0.19684 | 122.5708 | 122.5662 | 122.6761 | -0.13733
2280.75 | 122.7173 | -122.525 | 0.11444 | -0.0054933 | 0.07301 | 0.0013352 | 0.0028583 | 0.014246 | 0.00058966 | 0.00047844 | -0.0040437 | 0.031121 | -0.0097755 | 0.023093 | 0.0055415 | -0.0072652 | -0.013733 | -0.004578 | 0.032043 | 0.09613 | 0.16022 | 0.036621 | -0.091553 | 0.045776 | 0.064087 | -0.054932 | 0.027466 | 0.064087 | 0.045776 | -0.036621 | 122.5616 | 122.4335 | 0.045776 | 122.5204 | 122.6212 | 0.18768 | -0.12817 | 122.5708 | 122.4884 | -0.086975 | 122.5708 | 122.4701 | -0.018311 | -0.050354 | 122.6852 | 122.5113 | 122.5571 | -0.20599 | 122.5525 | 122.5891 | 122.5891 | -0.15106
2282.4844 | 122.731 | -122.5388 | 0.10986 | -0.0054933 | 0.074933 | 0.00069421 | 0.0043537 | 0.015528 | 0.0012305 | -0.00037596 | 0.0035858 | 0.032402 | -0.0089209 | 0.019888 | 0.0063959 | -0.0081198 | -0.013733 | -0.022888 | -0.013733 | 0.086975 | 0.17395 | 0.009155 | -0.10071 | -0.009155 | -0.009155 | -0.10986 | 0.054932 | 0.082397 | 0 | -0.07782 | 122.5479 | 122.438 | 0.064087 | 122.5159 | 122.6257 | 0.18768 | -0.1236 | 122.5388 | 122.4609 | -0.054931 | 122.5296 | 122.4289 | -0.032043 | -0.027466 | 122.7127 | 122.525 | 122.525 | -0.21057 | 122.5937 | 122.6212 | 122.5296 | -0.18768
2284.2031 | 122.6669 | -122.5525 | 0.10529 | 0.0021362 | 0.073224 | 0.0011216 | 0.0084125 | 0.015315 | -0.0036829 | -0.00080316 | -0.0040437 | 0.025994 | -0.0091345 | 0.022238 | -1.2744e-05 | -0.0081198 | 0.059509 | 0.10986 | 0.13733 | 0.15564 | 0.1236 | 0.045776 | -0.082397 | 0.068665 | 0.13275 | 0.022888 | 0.027466 | 0.036621 | 0.054932 | -0.027466 | 122.5983 | 122.4701 | 0.01831 | 122.6624 | 122.7081 | 0.23804 | -0.045777 | 122.6074 | 122.525 | -0.07782 | 122.6212 | 122.5754 | 0.050354 | -0.068665 | 122.6761 | 122.612 | 122.6898 | -0.18768 | 122.58 | 122.5891 | 122.6852 | -0.13275
2285.9219 | 122.7676 | -122.5021 | 0.091553 | -0.020752 | 0.070874 | 0.0038986 | 0.0060627 | 0.014887 | -0.0011193 | -0.0050758 | -0.011673 | 0.027703 | -0.0095619 | 0.023947 | 0.0019099 | -0.0076926 | 0.018311 | 0.073242 | 0.073242 | 0.11902 | 0.14648 | 0.013733 | -0.10529 | -0.009155 | 0.064087 | -0.09613 | 0.054932 | 0.054932 | -0.004578 | -0.07782 | 122.5159 | 122.3968 | 0.054931 | 122.5754 | 122.6212 | 0.22431 | -0.073242 | 122.4976 | 122.4243 | -0.036621 | 122.493 | 122.406 | -0.01831 | -0.036621 | 122.6486 | 122.5204 | 122.5754 | -0.19684 | 122.5571 | 122.5571 | 122.5662 | -0.16937
2287.6719 | 122.7859 | -122.4976 | 0.086975 | -0.013122 | 0.072583 | 0.0021896 | 0.0077717 | 0.01681 | -0.0028283 | -0.0029394 | -0.019302 | 0.027703 | -0.0072119 | 0.02352 | -0.00022634 | -0.0094016 | 0.068665 | 0.1236 | 0.15564 | 0.16937 | 0.1236 | 0.054932 | -0.068665 | 0.082397 | 0.17853 | 0.027466 | 0.022888 | 0.018311 | 0.050354 | -0.022888 | 122.5525 | 122.4289 | 0.036621 | 122.6212 | 122.6669 | 0.23804 | -0.01831 | 122.5479 | 122.4747 | -0.064087 | 122.58 | 122.525 | 0.050354 | -0.068664 | 122.6212 | 122.5662 | 122.6532 | -0.15564 | 122.5204 | 122.5159 | 122.6761 | -0.10986
2289.4219 | 122.7676 | -122.5021 | 0.10529 | -0.0054933 | 0.072583 | 0.0043258 | 0.0056355 | 0.018092 | -0.0043237 | -0.0014442 | -0.0040437 | 0.027275 | -0.0091345 | 0.020743 | 0.0036189 | -0.0096152 | 0.086975 | 0.11902 | 0.13733 | 0.1831 | 0.13733 | 0.041199 | -0.091553 | 0.082397 | 0.15564 | 0 | 0.041199 | 0.036621 | 0.041199 | -0.036621 | 122.5433 | 122.4106 | 0.032043 | 122.6212 | 122.6852 | 0.27466 | -0.018311 | 122.5433 | 122.4655 | -0.064087 | 122.5845 | 122.5021 | 0.036621 | -0.068665 | 122.6395 | 122.5891 | 122.6395 | -0.19684 | 122.5433 | 122.5388 | 122.6578 | -0.14191
2291.125 | 122.6944 | -122.5525 | 0.13275 | -0.0054933 | 0.074292 | 0.00026701 | 0.0024311 | 0.014674 | 0.0031531 | 0.002401 | -0.011673 | 0.029839 | -0.010843 | 0.022025 | 0.0083185 | -0.0096152 | 0.009155 | -0.027466 | -0.013733 | 0.086975 | 0.16937 | 0.013733 | -0.11902 | -0.009155 | -0.018311 | -0.14648 | 0.073242 | 0.082397 | 0.013733 | -0.059509 | 122.5662 | 122.4335 | 0.036622 | 122.525 | 122.6395 | 0.20599 | -0.1236 | 122.5662 | 122.493 | -0.059509 | 122.5433 | 122.406 | -0.086975 | -0.050354 | 122.7219 | 122.5616 | 122.5388 | -0.25177 | 122.6257 | 122.6349 | 122.5342 | -0.19226
2292.875 | 122.699 | -122.5021 | 0.11444 | -0.0054933 | 0.070447 | 0.0024032 | 0.0054217 | 0.014033 | -0.0041101 | -0.0010168 | -0.011673 | 0.027703 | -0.010416 | 0.020956 | 0.0034051 | -0.0072652 | -0.009155 | 0.068665 | 0.091553 | 0.13275 | 0.11902 | 0.041199 | -0.073242 | 0.027466 | 0.091553 | -0.022888 | 0.045776 | 0.036621 | 0.050354 | -0.027466 | 122.5433 | 122.4289 | 0.004578 | 122.5708 | 122.6349 | 0.20599 | -0.1236 | 122.5525 | 122.4747 | -0.068665 | 122.5296 | 122.4792 | 0.004578 | -0.07782 | 122.6212 | 122.493 | 122.5937 | -0.18768 | 122.5479 | 122.5388 | 122.5937 | -0.14191
2294.5469 | 122.8546 | -122.4792 | 0.068665 | -0.020752 | 0.075146 | -0.00080099 | 0.0062763 | 0.014246 | 0.0016577 | -0.0012306 | -0.0040437 | 0.032829 | -0.0074255 | 0.022452 | 0.0029779 | -0.008547 | 0.018311 | -0.009155 | 0.027466 | 0.1236 | 0.16479 | 0.004578 | -0.11902 | 0.018311 | 0.045776 | -0.10071 | 0.07782 | 0.082397 | 0.018311 | -0.059509 | 122.4838 | 122.3602 | 0.09613 | 122.4701 | 122.6028 | 0.24261 | -0.050354 | 122.4976 | 122.4197 | 0.009155 | 122.4976 | 122.3785 | -0.041199 | 0.013732 | 122.644 | 122.4976 | 122.5067 | -0.18768 | 122.5571 | 122.5616 | 122.525 | -0.12817
2296.2969 | 122.699 | -122.5479 | 0.13275 | -0.013122 | 0.07536 | 0.0017624 | 0.0034991 | 0.017024 | 0.0037939 | -0.0012306 | -0.0040437 | 0.031548 | -0.0078529 | 0.024588 | 0.0091731 | -0.008547 | 0.027466 | 0.013733 | 0.009155 | 0.11444 | 0.16479 | 0 | -0.11444 | 0.004578 | 0.013733 | -0.12817 | 0.054932 | 0.064087 | 0.013733 | -0.064087 | 122.5479 | 122.4335 | 0.032044 | 122.5616 | 122.6624 | 0.22888 | -0.10529 | 122.5616 | 122.4838 | -0.077819 | 122.5525 | 122.4197 | -0.064087 | -0.068664 | 122.7127 | 122.5754 | 122.5571 | -0.24719 | 122.6028 | 122.612 | 122.5616 | -0.19684
2297.9688 | 122.6898 | -122.5616 | 0.11902 | -0.013122 | 0.069592 | 0.0034714 | 0.0032855 | 0.015101 | -0.0038965 | 0.00047844 | -0.0040437 | 0.026848 | -0.012339 | 0.019247 | 0.0027643 | -0.005129 | 0.073242 | 0.12817 | 0.14191 | 0.16937 | 0.1236 | 0.041199 | -0.068665 | 0.07782 | 0.10986 | -0.013733 | 0.022888 | 0.032043 | 0.041199 | -0.018311 | 122.6028 | 122.493 | 0.004577 | 122.6898 | 122.731 | 0.23804 | -0.045777 | 122.6028 | 122.5433 | -0.096131 | 122.6395 | 122.5479 | 0.004578 | -0.086976 | 122.6852 | 122.6349 | 122.7036 | -0.18768 | 122.5845 | 122.5937 | 122.6715 | -0.13733
2299.7188 | 122.7264 | -122.5388 | 0.091553 | 0.0021362 | 0.071087 | 0.0047532 | 0.0056355 | 0.012965 | -0.0045373 | -0.0035804 | -0.011673 | 0.025353 | -0.0093481 | 0.019461 | 0.0027643 | -0.0047018 | 0 | 0.054932 | 0.086975 | 0.11902 | 0.14191 | 0.050354 | -0.073242 | 0.022888 | 0.064087 | -0.027466 | 0.050354 | 0.041199 | 0.036621 | -0.041199 | 122.5891 | 122.4655 | 0.050354 | 122.5937 | 122.6578 | 0.19226 | -0.091553 | 122.5754 | 122.4976 | -0.041199 | 122.5616 | 122.5113 | 0.013733 | -0.050354 | 122.6807 | 122.5388 | 122.6257 | -0.16479 | 122.5891 | 122.58 | 122.6028 | -0.13275
2301.4062 | 122.731 | -122.5296 | 0.10071 | -0.020752 | 0.072369 | 0.00069421 | 0.0045673 | 0.015528 | 0.0033667 | -0.0014442 | -0.011673 | 0.032616 | -0.0089209 | 0.020743 | 0.0076777 | -0.0091878 | 0.013733 | -0.004578 | 0.022888 | 0.091553 | 0.17853 | 0.013733 | -0.11444 | 0.050354 | 0.041199 | -0.073242 | 0.045776 | 0.050354 | 0.018311 | -0.045776 | 122.5433 | 122.4152 | 0.07782 | 122.525 | 122.6212 | 0.20599 | -0.086975 | 122.5479 | 122.4838 | -0.054932 | 122.58 | 122.4564 | -0.027466 | -0.050354 | 122.7081 | 122.5433 | 122.5525 | -0.21515 | 122.5754 | 122.58 | 122.5708 | -0.14648
2303.1406 | 122.6852 | -122.5662 | 0.11444 | -0.020752 | 0.075146 | -0.00080099 | 0.0047809 | 0.016169 | 0.0042213 | -0.00080316 | -0.0040437 | 0.031121 | -0.0080665 | 0.022025 | 0.0063959 | -0.0081198 | -0.032043 | -0.022888 | -0.009155 | 0.086975 | 0.16479 | 0.013733 | -0.13275 | 0 | -0.022888 | -0.16479 | 0.073242 | 0.082397 | 0.032043 | -0.059509 | 122.58 | 122.4335 | 0.050354 | 122.5433 | 122.6532 | 0.21973 | -0.14648 | 122.5983 | 122.5067 | -0.041199 | 122.5662 | 122.4014 | -0.10529 | -0.032044 | 122.731 | 122.5342 | 122.5571 | -0.24719 | 122.6395 | 122.6486 | 122.5433 | -0.17395
2304.8906 | 122.7768 | -122.525 | 0.10529 | -0.013122 | 0.069165 | 0.0021896 | 0.0075581 | 0.013819 | -0.0053919 | -0.0014442 | -0.0040437 | 0.023216 | -0.0076393 | 0.019034 | 0.00084166 | -0.0064108 | -0.004578 | 0.054932 | 0.082397 | 0.12817 | 0.12817 | 0.054932 | -0.10529 | 0.032043 | 0.10529 | 0 | 0.041199 | 0.050354 | 0.027466 | -0.036621 | 122.58 | 122.4197 | 0.022888 | 122.58 | 122.6532 | 0.23346 | -0.10986 | 122.5525 | 122.4884 | -0.064087 | 122.5571 | 122.525 | 0.036621 | -0.054932 | 122.6532 | 122.5204 | 122.6074 | -0.21057 | 122.5662 | 122.5754 | 122.6303 | -0.14191
2306.5781 | 122.6898 | -122.5433 | 0.1236 | -0.0054933 | 0.069378 | 0.0034714 | 0.0067035 | 0.01211 | -0.0019739 | -0.003794 | 0.0035858 | 0.028771 | -0.0076393 | 0.022238 | 0.0029779 | -0.0091878 | 0.050354 | 0.10071 | 0.13733 | 0.15564 | 0.13733 | 0.054932 | -0.09613 | 0.07782 | 0.10071 | -0.027466 | 0.027466 | 0.036621 | 0.054932 | -0.032043 | 122.5983 | 122.4472 | 0.013733 | 122.644 | 122.699 | 0.25177 | -0.073242 | 122.5983 | 122.5113 | -0.09613 | 122.6212 | 122.5159 | 0.004577 | -0.086975 | 122.6807 | 122.5937 | 122.6807 | -0.21973 | 122.5708 | 122.58 | 122.644 | -0.15564
2308.3281 | 122.7493 | -122.5342 | 0.10529 | -0.0054933 | 0.07066 | 0.0038986 | 0.0039265 | 0.014033 | 0.0020849 | -0.0029394 | -0.011673 | 0.029839 | -0.0091345 | 0.019888 | 0.0066095 | -0.0087606 | 0.082397 | 0.10529 | 0.10986 | 0.16937 | 0.13275 | 0.059509 | -0.07782 | 0.11444 | 0.11444 | -0.013733 | 0.022888 | 0.032043 | 0.036621 | -0.013733 | 122.5937 | 122.4564 | 0.027465 | 122.6395 | 122.7036 | 0.24719 | -0.022889 | 122.5708 | 122.5204 | -0.082398 | 122.6486 | 122.5204 | 0 | -0.073243 | 122.6669 | 122.6166 | 122.644 | -0.18311 | 122.5571 | 122.5662 | 122.6486 | -0.11902
2310.0781 | 122.7814 | -122.5204 | 0.073242 | -0.013122 | 0.073437 | 0.005394 | 0.010335 | 0.017664 | -0.0019739 | -0.0025122 | -0.019302 | 0.025353 | -0.0082801 | 0.020529 | 0.0012689 | -0.0098288 | 0.073242 | 0.15106 | 0.16022 | 0.16937 | 0.11902 | 0.036621 | -0.073242 | 0.09613 | 0.16022 | 0.018311 | 0.022888 | 0.032043 | 0.068665 | -0.032043 | 122.5571 | 122.4472 | 0.045777 | 122.6715 | 122.6898 | 0.24261 | 0 | 122.5891 | 122.4884 | -0.050354 | 122.6166 | 122.5388 | 0.050354 | -0.041199 | 122.6395 | 122.5937 | 122.6807 | -0.14648 | 122.5433 | 122.5525 | 122.6807 | -0.10529
2311.8281 | 122.7859 | -122.5113 | 0.086975 | -0.013122 | 0.071728 | 0.0024032 | 0.0086261 | 0.013606 | -0.0030419 | -0.0025122 | -0.019302 | 0.024285 | -0.0080665 | 0.020956 | -0.00022634 | -0.0094016 | 0 | 0.064087 | 0.091553 | 0.12817 | 0.14648 | 0.032043 | -0.07782 | 0.059509 | 0.10986 | -0.004578 | 0.036621 | 0.027466 | 0.050354 | -0.032043 | 122.5433 | 122.4335 | 0.059509 | 122.5754 | 122.6395 | 0.20599 | -0.086975 | 122.5616 | 122.4792 | -0.050354 | 122.5708 | 122.5067 | 0.027465 | -0.059509 | 122.6578 | 122.5113 | 122.6028 | -0.16479 | 122.5479 | 122.5388 | 122.6212 | -0.11902
2313.5938 | 122.7402 | -122.5479 | 0.11444 | -0.0054933 | 0.07066 | 0.00090781 | 0.0024311 | 0.015315 | 0.0016577 | 0.00026484 | 0.0035858 | 0.029839 | -0.011484 | 0.022879 | 0.0051141 | -0.012392 | 0.10071 | 0.10529 | 0.12817 | 0.17853 | 0.13275 | 0.068665 | -0.082397 | 0.1236 | 0.11902 | 0.004578 | 0.032043 | 0.018311 | 0.059509 | -0.013733 | 122.6166 | 122.4655 | 0.01831 | 122.6532 | 122.7264 | 0.26092 | -0.013733 | 122.6074 | 122.5342 | -0.082398 | 122.6715 | 122.5525 | 0.018311 | -0.09613 | 122.6807 | 122.6486 | 122.6761 | -0.19684 | 122.58 | 122.5662 | 122.6669 | -0.12817
2315.2812 | 122.8409 | -122.525 | 0.086975 | -0.0054933 | 0.07536 | 0.00069421 | 0.0043537 | 0.018519 | 0.0037939 | -0.00058956 | -0.0040437 | 0.031975 | -0.0059303 | 0.02352 | 0.0061823 | -0.012392 | 0.013733 | 0 | 0.018311 | 0.11902 | 0.15564 | 0.027466 | -0.10986 | 0.059509 | 0.073242 | -0.091553 | 0.082397 | 0.07782 | 0.022888 | -0.064087 | 122.5525 | 122.4152 | 0.068665 | 122.525 | 122.644 | 0.22888 | -0.073242 | 122.5479 | 122.4609 | -0.004578 | 122.5845 | 122.4335 | -0.027466 | -0.009155 | 122.6807 | 122.5388 | 122.5433 | -0.19684 | 122.6074 | 122.6028 | 122.5983 | -0.15106
2317.0312 | 122.7219 | -122.5662 | 0.10529 | -0.013122 | 0.070233 | 0.0028306 | 0.0045673 | 0.013819 | -0.0034691 | 5.1244e-05 | -0.011673 | 0.027275 | -0.0091345 | 0.020743 | 0.0025507 | -0.0059836 | 0.013733 | 0.086975 | 0.09613 | 0.12817 | 0.1236 | 0.045776 | -0.086975 | 0.050354 | 0.082397 | -0.036621 | 0.013733 | 0.050354 | 0.032043 | -0.045776 | 122.612 | 122.4792 | 0.01831 | 122.6532 | 122.6944 | 0.21515 | -0.091553 | 122.5983 | 122.5204 | -0.091553 | 122.6166 | 122.5296 | 0.009155 | -0.054932 | 122.6898 | 122.58 | 122.6624 | -0.19226 | 122.58 | 122.6166 | 122.6486 | -0.15106
2318.7812 | 122.7448 | -122.5388 | 0.10529 | -0.0054933 | 0.073224 | 0.0015488 | 0.0028583 | 0.016596 | 0.0022987 | 0.00047844 | -0.011673 | 0.031121 | -0.0082801 | 0.024374 | 0.0059687 | -0.010042 | 0 | -0.009155 | -0.009155 | 0.082397 | 0.17395 | 0.022888 | -0.10986 | 0.022888 | -0.004578 | -0.10986 | 0.068665 | 0.073242 | 0.018311 | -0.054932 | 122.5616 | 122.4289 | 0.068664 | 122.5296 | 122.6212 | 0.19226 | -0.10529 | 122.5571 | 122.4838 | -0.036621 | 122.5616 | 122.4289 | -0.054931 | -0.032044 | 122.7127 | 122.5388 | 122.5296 | -0.21515 | 122.6074 | 122.612 | 122.5342 | -0.16022
2320.4688 | 122.699 | -122.5433 | 0.12817 | -0.0054933 | 0.068097 | 0.0032578 | 0.0022175 | 0.018519 | -0.0011193 | -0.00016236 | -0.0040437 | 0.028771 | -0.012766 | 0.020529 | 0.0044733 | -0.0059836 | 0.086975 | 0.11902 | 0.15106 | 0.17395 | 0.10986 | 0.059509 | -0.054932 | 0.11444 | 0.13733 | 0.018311 | 0.018311 | 0.027466 | 0.064087 | -0.013733 | 122.6028 | 122.4884 | -0.018311 | 122.6624 | 122.7173 | 0.22888 | -0.041199 | 122.6074 | 122.5296 | -0.10986 | 122.6578 | 122.5616 | 0.032044 | -0.10071 | 122.6532 | 122.6303 | 122.6944 | -0.18311 | 122.5616 | 122.5708 | 122.6807 | -0.14191
2322.2031 | 122.7585 | -122.5388 | 0.10986 | -0.013122 | 0.067883 | 0.001976 | 0.0049945 | 0.019373 | -0.0051781 | -0.0014442 | -0.0040437 | 0.027489 | -0.0084937 | 0.021597 | 0.0025507 | -0.0064108 | 0.009155 | 0.064087 | 0.07782 | 0.11902 | 0.14648 | 0.036621 | -0.091553 | 0.045776 | 0.086975 | -0.013733 | 0.036621 | 0.041199 | 0.027466 | -0.027466 | 122.5754 | 122.4472 | 0.036621 | 122.6028 | 122.6578 | 0.21057 | -0.10071 | 122.5662 | 122.5113 | -0.073242 | 122.5845 | 122.525 | 0.013733 | -0.068664 | 122.6852 | 122.5479 | 122.6166 | -0.20142 | 122.5754 | 122.58 | 122.6257 | -0.13733
2323.9531 | 122.7951 | -122.5204 | 0.09613 | -0.013122 | 0.07301 | 0.0024032 | 0.0092669 | 0.015955 | -0.0032555 | -0.0016578 | -0.0040437 | 0.027489 | -0.0078529 | 0.017966 | 0.0010553 | -0.0076926 | 0.086975 | 0.13275 | 0.16022 | 0.17853 | 0.11444 | 0.036621 | -0.07782 | 0.10071 | 0.17395 | 0.022888 | 0.027466 | 0.032043 | 0.064087 | -0.027466 | 122.5571 | 122.4426 | 0.018311 | 122.6532 | 122.699 | 0.25635 | -0.009155 | 122.5845 | 122.493 | -0.068664 | 122.6212 | 122.5433 | 0.050354 | -0.064087 | 122.6349 | 122.6074 | 122.6807 | -0.17395 | 122.5479 | 122.5525 | 122.6944 | -0.1236
2325.7188 | 122.8363 | -122.4976 | 0.09613 | -0.013122 | 0.070233 | 0.0038986 | 0.0045673 | 0.014246 | -0.00069214 | -0.0027258 | -0.0040437 | 0.024712 | -0.0093481 | 0.018179 | 0.0019099 | -0.0087606 | 0.10529 | 0.14648 | 0.14648 | 0.16937 | 0.15106 | 0.054932 | -0.073242 | 0.1236 | 0.17853 | 0.032043 | 0.032043 | 0.045776 | 0.059509 | -0.027466 | 122.5525 | 122.4243 | 0.054932 | 122.644 | 122.6669 | 0.24261 | 0.009156 | 122.5571 | 122.4701 | -0.064087 | 122.6212 | 122.5296 | 0.059509 | -0.050354 | 122.6486 | 122.6028 | 122.644 | -0.16937 | 122.5296 | 122.5433 | 122.6761 | -0.1236
2327.3906 | 122.8455 | -122.5067 | 0.10986 | -0.0054933 | 0.074933 | -0.00058739 | 0.0056355 | 0.016596 | 0.0061439 | 0.00090584 | 0.0035858 | 0.032616 | -0.0076393 | 0.020956 | 0.0072505 | -0.010683 | 0.041199 | 0.013733 | 0.036621 | 0.12817 | 0.15106 | 0.018311 | -0.11444 | 0.059509 | 0.059509 | -0.07782 | 0.07782 | 0.064087 | 0.022888 | -0.068665 | 122.525 | 122.3923 | 0.041199 | 122.5204 | 122.6349 | 0.24262 | -0.068664 | 122.5296 | 122.438 | -0.032043 | 122.5662 | 122.4289 | -0.009155 | -0.045776 | 122.6578 | 122.5479 | 122.5433 | -0.2243 | 122.5845 | 122.5708 | 122.5662 | -0.17853
2329.0781 | 122.8226 | -122.5113 | 0.082397 | -0.013122 | 0.070019 | 0.0034714 | 0.0054217 | 0.014674 | -0.0034691 | -0.0016578 | -0.0040437 | 0.023003 | -0.0095619 | 0.022025 | -1.2744e-05 | -0.008547 | 0.045776 | 0.091553 | 0.11902 | 0.15564 | 0.15564 | 0.032043 | -0.091553 | 0.082397 | 0.14191 | 0.013733 | 0.018311 | 0.050354 | 0.059509 | -0.036621 | 122.5433 | 122.4197 | 0.073243 | 122.6028 | 122.6669 | 0.24719 | -0.036621 | 122.5708 | 122.4747 | -0.064086 | 122.5937 | 122.525 | 0.050354 | -0.032043 | 122.6669 | 122.5571 | 122.6303 | -0.17395 | 122.5296 | 122.5616 | 122.6532 | -0.11902
2330.8438 | 122.7722 | -122.5433 | 0.082397 | 0.0021362 | 0.068738 | 0.0041122 | 0.0079853 | 0.017237 | -0.0011193 | -0.0033668 | 0.0035858 | 0.027916 | -0.0074255 | 0.022665 | 0.0021235 | -0.0072652 | 0.013733 | 0.045776 | 0.082397 | 0.13275 | 0.14191 | 0.022888 | -0.073242 | 0.041199 | 0.09613 | -0.022888 | 0.032043 | 0.045776 | 0.041199 | -0.041199 | 122.5662 | 122.4701 | 0.05951 | 122.5891 | 122.6761 | 0.20599 | -0.068664 | 122.5845 | 122.5021 | -0.050354 | 122.5845 | 122.5204 | 0.018311 | -0.036621 | 122.6852 | 122.5571 | 122.6257 | -0.15564 | 122.5754 | 122.5891 | 122.6395 | -0.1236
2332.5938 | 122.731 | -122.5571 | 0.11444 | -0.0054933 | 0.069806 | 0.0017624 | 0.0034991 | 0.01446 | -0.0017603 | -0.0040076 | -0.0040437 | 0.027275 | -0.010203 | 0.021811 | 0.0021235 | -0.0091878 | 0.027466 | 0.054932 | 0.086975 | 0.13275 | 0.13733 | 0.050354 | -0.091553 | 0.045776 | 0.086975 | -0.027466 | 0.036621 | 0.036621 | 0.036621 | -0.041199 | 122.6074 | 122.4655 | 0.022888 | 122.612 | 122.6898 | 0.2243 | -0.086975 | 122.5937 | 122.5159 | -0.07782 | 122.6028 | 122.5296 | 0.013733 | -0.07782 | 122.6944 | 122.5845 | 122.644 | -0.20599 | 122.5937 | 122.5937 | 122.644 | -0.15564
2334.3438 | 122.7356 | -122.5479 | 0.091553 | -0.0054933 | 0.071301 | 0.0038986 | 0.0062763 | 0.013392 | -0.0013329 | -0.0048622 | -0.0040437 | 0.027275 | -0.0097755 | 0.020316 | 0.0021235 | -0.0081198 | 0.041199 | 0.059509 | 0.091553 | 0.13275 | 0.13733 | 0.045776 | -0.07782 | 0.045776 | 0.07782 | -0.036621 | 0.041199 | 0.041199 | 0.013733 | -0.050354 | 122.5937 | 122.4701 | 0.045776 | 122.6074 | 122.6807 | 0.21057 | -0.050354 | 122.5616 | 122.4976 | -0.050354 | 122.5937 | 122.5113 | 0.013733 | -0.050354 | 122.6852 | 122.5891 | 122.6395 | -0.16937 | 122.5891 | 122.5891 | 122.6257 | -0.14191
2336.1094 | 122.7448 | -122.5388 | 0.1236 | 0.0021362 | 0.074933 | 0.0011216 | 0.0034991 | 0.014246 | 0.0069983 | -0.00058956 | 0.0035858 | 0.031975 | -0.011057 | 0.024161 | 0.0068231 | -0.012606 | 0.018311 | -0.045776 | -0.009155 | 0.086975 | 0.17395 | 0 | -0.1236 | 0.027466 | -0.022888 | -0.14191 | 0.086975 | 0.07782 | 0.018311 | -0.054932 | 122.5388 | 122.4152 | 0.050354 | 122.493 | 122.6257 | 0.21057 | -0.10528 | 122.5571 | 122.4838 | -0.036621 | 122.5662 | 122.3969 | -0.086975 | -0.045776 | 122.7127 | 122.5571 | 122.5296 | -0.24719 | 122.6257 | 122.6166 | 122.5159 | -0.17853
2337.7969 | 122.7356 | -122.5708 | 0.10529 | -0.013122 | 0.07066 | 0.0034714 | 0.0049945 | 0.013819 | -0.0013329 | -0.00016236 | 0.0035858 | 0.025566 | -0.0084937 | 0.020529 | 0.0019099 | -0.008547 | 0.032043 | 0.068665 | 0.10071 | 0.1236 | 0.12817 | 0.032043 | -0.07782 | 0.050354 | 0.082397 | -0.036621 | 0.041199 | 0.059509 | 0.050354 | -0.036621 | 122.6028 | 122.493 | 0.022888 | 122.6395 | 122.6944 | 0.20142 | -0.073243 | 122.6212 | 122.5342 | -0.064087 | 122.6212 | 122.5342 | 0 | -0.045777 | 122.699 | 122.6028 | 122.6715 | -0.18311 | 122.612 | 122.6303 | 122.6532 | -0.14191
2339.5469 | 122.85 | -122.5388 | 0.082397 | -0.0054933 | 0.07536 | 0.0038986 | 0.0075581 | 0.015955 | 0.0025123 | 0.00026484 | 0.0035858 | 0.029839 | -0.0063575 | 0.023306 | 0.0031915 | -0.010256 | 0.004578 | -0.004578 | -0.004578 | 0.10071 | 0.17395 | -0.018311 | -0.14648 | 0.004578 | 0.032043 | -0.11444 | 0.07782 | 0.086975 | 0.032043 | -0.059509 | 122.5204 | 122.3923 | 0.091553 | 122.5342 | 122.6395 | 0.24719 | -0.077819 | 122.5708 | 122.4792 | -0.004577 | 122.5433 | 122.4243 | -0.054932 | 0.004578 | 122.7127 | 122.5433 | 122.5342 | -0.22888 | 122.6166 | 122.6257 | 122.5708 | -0.14191
2341.2969 | 122.7448 | -122.5616 | 0.086975 | -0.020752 | 0.069806 | 0.0021896 | 0.0045673 | 0.013606 | -0.0019739 | -0.0012306 | -0.0040437 | 0.025139 | -0.010416 | 0.022238 | 0.0019099 | -0.0089742 | 0.032043 | 0.050354 | 0.082397 | 0.11902 | 0.13733 | 0.045776 | -0.07782 | 0.050354 | 0.086975 | -0.036621 | 0.032043 | 0.045776 | 0.032043 | -0.027466 | 122.6074 | 122.4838 | 0.050354 | 122.612 | 122.6807 | 0.19684 | -0.054932 | 122.5937 | 122.5342 | -0.054932 | 122.612 | 122.525 | -0.009155 | -0.041199 | 122.699 | 122.5937 | 122.644 | -0.16479 | 122.5937 | 122.6074 | 122.6486 | -0.11444
2343.0469 | 122.7814 | -122.5571 | 0.1236 | 0.0021362 | 0.070447 | 0.003685 | 0.00029487 | 0.015528 | 0.0037939 | -0.0016578 | 0.0035858 | 0.03048 | -0.011912 | 0.023093 | 0.0091731 | -0.008547 | 0.013733 | 0.004578 | 0.018311 | 0.09613 | 0.17395 | 0.022888 | -0.10529 | 0.054932 | 0.041199 | -0.073242 | 0.059509 | 0.064087 | 0.036621 | -0.032043 | 122.58 | 122.4518 | 0.050354 | 122.5616 | 122.6532 | 0.20142 | -0.10986 | 122.5937 | 122.525 | -0.064087 | 122.612 | 122.4838 | -0.041199 | -0.059509 | 122.731 | 122.5708 | 122.5754 | -0.22888 | 122.6166 | 122.6212 | 122.5983 | -0.15564
2344.7344 | 122.8455 | -122.5113 | 0.082397 | -0.013122 | 0.070019 | 0.0028306 | 0.0069171 | 0.013178 | -0.0019739 | -0.0040076 | 0.0035858 | 0.028771 | -0.0095619 | 0.020529 | 0.00041446 | -0.0087606 | 0.091553 | 0.14648 | 0.16479 | 0.17853 | 0.12817 | 0.054932 | -0.082397 | 0.10986 | 0.18768 | 0.059509 | 0.018311 | 0.022888 | 0.045776 | -0.027466 | 122.5662 | 122.4289 | 0.045777 | 122.6578 | 122.6898 | 0.26092 | 0.009156 | 122.5571 | 122.4838 | -0.064086 | 122.6212 | 122.5708 | 0.086975 | -0.059509 | 122.6395 | 122.6028 | 122.6761 | -0.16479 | 122.5296 | 122.5342 | 122.699 | -0.10986
2346.5 | 122.7127 | -122.5891 | 0.11902 | -0.0054933 | 0.073437 | -0.00080099 | 0.0039265 | 0.01916 | 0.0046485 | 5.1244e-05 | -0.011673 | 0.031975 | -0.01063 | 0.022238 | 0.0074641 | -0.010256 | 0.050354 | 0.018311 | 0.013733 | 0.09613 | 0.16479 | 0.004578 | -0.11444 | 0.022888 | 0 | -0.13733 | 0.064087 | 0.059509 | -0.018311 | -0.073242 | 122.5937 | 122.4747 | 0.045776 | 122.6074 | 122.6852 | 0.21057 | -0.068665 | 122.5708 | 122.5159 | -0.054932 | 122.612 | 122.4518 | -0.064087 | -0.05951 | 122.7539 | 122.6395 | 122.6028 | -0.23346 | 122.6532 | 122.6486 | 122.5891 | -0.19226
2348.1719 | 122.7173 | -122.58 | 0.10529 | -0.0054933 | 0.069592 | 0.0030442 | 0.0011493 | 0.015101 | -0.0032555 | -0.0014442 | 0.0035858 | 0.026634 | -0.012339 | 0.019247 | 0.0034051 | -0.0076926 | 0.064087 | 0.13275 | 0.14648 | 0.15106 | 0.1236 | 0.041199 | -0.068665 | 0.09613 | 0.13733 | 0.022888 | 0.032043 | 0.032043 | 0.041199 | -0.036621 | 122.6212 | 122.5113 | 0.01831 | 122.7127 | 122.731 | 0.21973 | -0.041199 | 122.6212 | 122.5433 | -0.073243 | 122.6761 | 122.6028 | 0.059509 | -0.073243 | 122.7036 | 122.644 | 122.7264 | -0.17395 | 122.612 | 122.612 | 122.7173 | -0.14191
2349.9062 | 122.8592 | -122.5021 | 0.064087 | -0.0054933 | 0.070019 | 0.0038986 | 0.0062763 | 0.012965 | -0.0043237 | -0.0031532 | 0.0035858 | 0.028984 | -0.0093481 | 0.02117 | 0.00041446 | -0.0094016 | 0.086975 | 0.11444 | 0.12817 | 0.17395 | 0.14191 | 0.050354 | -0.064087 | 0.10529 | 0.16937 | 0.054932 | 0.036621 | 0.041199 | 0.050354 | -0.027466 | 122.5525 | 122.438 | 0.07782 | 122.6166 | 122.6761 | 0.23804 | 0.022888 | 122.5525 | 122.4747 | -0.027466 | 122.6074 | 122.5571 | 0.082398 | -0.022888 | 122.644 | 122.5891 | 122.6303 | -0.12817 | 122.5388 | 122.5433 | 122.6715 | -0.091553
2351.5938 | 122.818 | -122.525 | 0.082397 | -0.013122 | 0.077069 | 0.0024032 | 0.0077717 | 0.015742 | -0.0038965 | -0.0031532 | -0.0040437 | 0.031548 | -0.0061439 | 0.020743 | 0.0025507 | -0.0087606 | 0.091553 | 0.14191 | 0.14648 | 0.16937 | 0.13275 | 0.027466 | -0.086975 | 0.09613 | 0.1831 | 0.027466 | 0.022888 | 0.036621 | 0.050354 | -0.045776 | 122.5525 | 122.438 | 0.050354 | 122.6669 | 122.6944 | 0.25635 | 0.009156 | 122.5754 | 122.4792 | -0.059509 | 122.6212 | 122.5525 | 0.073242 | -0.045776 | 122.6578 | 122.6166 | 122.6715 | -0.16937 | 122.5479 | 122.5616 | 122.7081 | -0.12817
2353.3281 | 122.8592 | -122.5479 | 0.054932 | -0.013122 | 0.075146 | 0.0015488 | 0.0081989 | 0.017024 | 0.0029395 | -0.00080316 | -0.0040437 | 0.031121 | -0.0087073 | 0.024161 | 0.0040461 | -0.011965 | 0.004578 | -0.013733 | 0.022888 | 0.10071 | 0.1831 | 0.004578 | -0.12817 | 0.036621 | 0.045776 | -0.091553 | 0.086975 | 0.086975 | 0.022888 | -0.054932 | 122.5525 | 122.4197 | 0.12817 | 122.5342 | 122.6486 | 0.22888 | -0.050354 | 122.5708 | 122.493 | 0.032043 | 122.5845 | 122.4564 | -0.036621 | 0.032043 | 122.731 | 122.5525 | 122.5708 | -0.18311 | 122.6349 | 122.6349 | 122.5937 | -0.10986
2355.0625 | 122.7448 | -122.5616 | 0.11902 | -0.013122 | 0.074933 | 0.0013352 | 0.0056355 | 0.015955 | 0.0025123 | 5.1244e-05 | -0.0040437 | 0.031548 | -0.0082801 | 0.024588 | 0.0093867 | -0.0098288 | 0.073242 | 0.050354 | 0.054932 | 0.1236 | 0.16022 | 0.041199 | -0.10529 | 0.059509 | 0.064087 | -0.11444 | 0.045776 | 0.073242 | 0.022888 | -0.050354 | 122.6028 | 122.4564 | 0.041198 | 122.612 | 122.6852 | 0.22888 | -0.045777 | 122.5845 | 122.5113 | -0.073243 | 122.6212 | 122.4472 | -0.064087 | -0.045777 | 122.7219 | 122.6349 | 122.6166 | -0.22431 | 122.6074 | 122.6349 | 122.6257 | -0.16937
2356.8125 | 122.8271 | -122.5479 | 0.073242 | -0.028381 | 0.071301 | 5.3406e-05 | 0.0062763 | 0.015742 | -0.0051781 | -0.0014442 | -0.019302 | 0.024498 | -0.011057 | 0.021597 | -0.00086734 | -0.0070516 | 0.041199 | 0.07782 | 0.11902 | 0.14648 | 0.14191 | 0.050354 | -0.091553 | 0.073242 | 0.13733 | 0.027466 | 0.036621 | 0.045776 | 0.022888 | -0.032043 | 122.5983 | 122.4564 | 0.068665 | 122.6257 | 122.6944 | 0.23804 | -0.032043 | 122.5708 | 122.5159 | -0.036621 | 122.6212 | 122.5754 | 0.059509 | -0.027466 | 122.6898 | 122.5891 | 122.6669 | -0.16479 | 122.5845 | 122.5937 | 122.6852 | -0.10529
2358.5 | 122.8043 | -122.5433 | 0.09613 | -0.0054933 | 0.073651 | 0.0032578 | 0.0060627 | 0.016596 | -0.0017603 | -0.0022986 | -0.011673 | 0.030052 | -0.0087073 | 0.022238 | 0.0029779 | -0.011111 | 0.086975 | 0.11902 | 0.14191 | 0.16022 | 0.11444 | 0.036621 | -0.086975 | 0.091553 | 0.16479 | 0 | 0.041199 | 0.054932 | 0.036621 | -0.041199 | 122.58 | 122.4564 | 0.018311 | 122.6624 | 122.7036 | 0.24719 | -0.009155 | 122.58 | 122.5021 | -0.054931 | 122.6349 | 122.5433 | 0.041199 | -0.041198 | 122.6578 | 122.6303 | 122.6852 | -0.1831 | 122.5845 | 122.5983 | 122.7081 | -0.13733
2360.25 | 122.7402 | -122.5571 | 0.11444 | -0.0054933 | 0.069592 | 0.0021896 | 0.0047809 | 0.01211 | -0.0017603 | -0.0027258 | 0.0035858 | 0.02813 | -0.0091345 | 0.021597 | 0.0029779 | -0.008547 | 0.032043 | 0.054932 | 0.09613 | 0.13275 | 0.12817 | 0.059509 | -0.082397 | 0.050354 | 0.086975 | -0.013733 | 0.054932 | 0.045776 | 0.041199 | -0.036621 | 122.6166 | 122.4747 | 0.013733 | 122.612 | 122.6898 | 0.21515 | -0.082398 | 122.5983 | 122.5204 | -0.059509 | 122.6074 | 122.5433 | 0.022888 | -0.068665 | 122.6852 | 122.5891 | 122.6532 | -0.19684 | 122.612 | 122.6028 | 122.644 | -0.15106
2362 | 122.7814 | -122.5525 | 0.10529 | 0.0021362 | 0.071728 | 0.0021896 | -0.00034613 | 0.017024 | 0.0012305 | -0.0010168 | -0.019302 | 0.027275 | -0.011057 | 0.023734 | 0.0087457 | -0.011324 | 0.09613 | 0.09613 | 0.10071 | 0.16479 | 0.11902 | 0.068665 | -0.086975 | 0.1236 | 0.11444 | 0 | 0.022888 | 0.032043 | 0.050354 | -0.027466 | 122.6212 | 122.4655 | 0.013733 | 122.6486 | 122.7173 | 0.25177 | -0.009156 | 122.6028 | 122.525 | -0.082398 | 122.6761 | 122.5525 | 0.027466 | -0.073243 | 122.6715 | 122.6486 | 122.6532 | -0.19226 | 122.5754 | 122.5845 | 122.6669 | -0.13275
2363.75 | 122.7356 | -122.5891 | 0.11444 | 0.0021362 | 0.068951 | 0.0013352 | 0.0011493 | 0.01446 | 0.00016226 | -0.00016236 | 0.0035858 | 0.02813 | -0.011057 | 0.020743 | 0.0051141 | -0.0091878 | 0.09613 | 0.12817 | 0.15106 | 0.17853 | 0.1236 | 0.054932 | -0.054932 | 0.10986 | 0.14191 | 0.022888 | 0.036621 | 0.032043 | 0.050354 | -0.027466 | 122.644 | 122.5342 | 0.009155 | 122.7173 | 122.7676 | 0.23346 | -0.018311 | 122.6395 | 122.5616 | -0.07782 | 122.699 | 122.612 | 0.050354 | -0.082398 | 122.7127 | 122.6852 | 122.7402 | -0.16937 | 122.6257 | 122.6212 | 122.731 | -0.14191
2365.4219 | 122.8134 | -122.5342 | 0.086975 | -0.028381 | 0.071301 | 0.0024032 | 0.0075581 | 0.014033 | -0.0015465 | -0.002085 | -0.019302 | 0.02813 | -0.0095619 | 0.020956 | 0.0019099 | -0.0079062 | 0.082397 | 0.13733 | 0.16479 | 0.17853 | 0.1236 | 0.045776 | -0.082397 | 0.09613 | 0.17853 | 0.032043 | 0.036621 | 0.045776 | 0.045776 | -0.036621 | 122.58 | 122.4518 | 0.036621 | 122.6715 | 122.7127 | 0.26092 | -0.004578 | 122.58 | 122.4976 | -0.050354 | 122.6303 | 122.5662 | 0.068664 | -0.041199 | 122.6578 | 122.6166 | 122.699 | -0.16937 | 122.5708 | 122.58 | 122.7127 | -0.1236
2367.1719 | 122.7402 | -122.5845 | 0.1236 | -0.0054933 | 0.073864 | 0.00069421 | 0.0020039 | 0.017237 | 0.0052893 | 0.00090584 | -0.011673 | 0.031334 | -0.010416 | 0.023306 | 0.0087457 | -0.0087606 | 0.022888 | 0 | 0.022888 | 0.082397 | 0.15106 | 0.018311 | -0.1236 | 0.004578 | 0 | -0.13733 | 0.07782 | 0.073242 | 0.009155 | -0.050354 | 122.6028 | 122.4609 | 0.027466 | 122.5845 | 122.6669 | 0.20599 | -0.10071 | 122.5937 | 122.5342 | -0.045776 | 122.5891 | 122.4472 | -0.086975 | -0.050354 | 122.7356 | 122.6074 | 122.6074 | -0.24719 | 122.6624 | 122.6578 | 122.5845 | -0.17395
2368.8594 | 122.8638 | -122.5616 | 0.09613 | -0.013122 | 0.076428 | 0.0017624 | 0.0073443 | 0.014674 | 0.0033667 | 0.0028284 | -0.0040437 | 0.029198 | -0.0055029 | 0.023093 | 0.0051141 | -0.0098288 | 0.032043 | 0.050354 | 0.050354 | 0.1236 | 0.16022 | 0.009155 | -0.11444 | 0.050354 | 0.073242 | -0.07782 | 0.073242 | 0.050354 | 0.027466 | -0.054932 | 122.5708 | 122.4472 | 0.064087 | 122.612 | 122.6852 | 0.23804 | -0.064087 | 122.5891 | 122.5067 | -0.022888 | 122.612 | 122.4838 | -0.022888 | -0.045776 | 122.7219 | 122.5937 | 122.612 | -0.21057 | 122.6349 | 122.612 | 122.6349 | -0.15106
2370.6094 | 122.731 | -122.5571 | 0.10529 | -0.013122 | 0.071728 | 0.0026168 | 0.0056355 | 0.014246 | -0.0038965 | -0.00037596 | -0.019302 | 0.02578 | -0.0089209 | 0.022665 | -0.00022634 | -0.0070516 | 0.027466 | 0.10986 | 0.10986 | 0.14648 | 0.09613 | 0.041199 | -0.073242 | 0.050354 | 0.09613 | -0.018311 | 0.022888 | 0.036621 | 0.045776 | -0.022888 | 122.5983 | 122.4838 | -0.009156 | 122.6669 | 122.7036 | 0.21973 | -0.07782 | 122.6028 | 122.5342 | -0.082398 | 122.6074 | 122.5388 | 0.004577 | -0.068665 | 122.6532 | 122.5845 | 122.6669 | -0.17853 | 122.58 | 122.5937 | 122.6532 | -0.12817
2372.2969 | 122.7768 | -122.5708 | 0.11444 | -0.0054933 | 0.073224 | 0.001976 | 0.0017901 | 0.013819 | 0.0012305 | -0.0012306 | -0.011673 | 0.030907 | -0.0084937 | 0.022665 | 0.0076777 | -0.0083334 | -0.009155 | -0.004578 | 0.009155 | 0.09613 | 0.16937 | 0.018311 | -0.11444 | 0.018311 | 0 | -0.10071 | 0.068665 | 0.073242 | 0.018311 | -0.045776 | 122.5891 | 122.4564 | 0.054932 | 122.5662 | 122.6669 | 0.21057 | -0.1236 | 122.5891 | 122.525 | -0.045776 | 122.5891 | 122.4701 | -0.054932 | -0.041199 | 122.7402 | 122.5616 | 122.58 | -0.22888 | 122.6395 | 122.644 | 122.5708 | -0.16022
2373.9688 | 122.7448 | -122.5845 | 0.1236 | -0.0054933 | 0.067456 | 0.0045394 | 0.0047809 | 0.014033 | -0.0058191 | -0.0025122 | 0.0035858 | 0.025994 | -0.010843 | 0.022025 | 0.0031915 | -0.0070516 | 0 | 0.082397 | 0.09613 | 0.13733 | 0.11902 | 0.032043 | -0.073242 | 0.032043 | 0.091553 | -0.041199 | 0.036621 | 0.054932 | 0.036621 | -0.022888 | 122.6166 | 122.5113 | -0.004577 | 122.6669 | 122.7219 | 0.21057 | -0.1236 | 122.6212 | 122.5616 | -0.086975 | 122.6166 | 122.5433 | -0.018311 | -0.068664 | 122.7036 | 122.5845 | 122.6807 | -0.19684 | 122.6212 | 122.6395 | 122.6761 | -0.14648
2375.6562 | 122.8683 | -122.5342 | 0.082397 | 0.0021362 | 0.069592 | 0.0045394 | 0.0037127 | 0.012965 | -0.0028283 | -0.0031532 | -0.011673 | 0.027275 | -0.011698 | 0.02117 | 0.00020086 | -0.01047 | 0.10071 | 0.13733 | 0.15564 | 0.18768 | 0.11444 | 0.059509 | -0.064087 | 0.09613 | 0.1831 | 0.068665 | 0.036621 | 0.045776 | 0.050354 | -0.032043 | 122.5937 | 122.4701 | 0.032044 | 122.6715 | 122.7219 | 0.25177 | 0.018311 | 122.5845 | 122.5021 | -0.045776 | 122.6303 | 122.6028 | 0.10071 | -0.036621 | 122.6486 | 122.6349 | 122.6898 | -0.14648 | 122.5708 | 122.58 | 122.7173 | -0.11444
2377.3906 | 122.8546 | -122.5433 | 0.091553 | -0.013122 | 0.076001 | 0.00090781 | 0.0060627 | 0.01446 | 0.0040077 | -0.0010168 | -0.011673 | 0.031761 | -0.0076393 | 0.022025 | 0.0063959 | -0.010683 | 0.050354 | 0.009155 | 0.041199 | 0.12817 | 0.15564 | 0.018311 | -0.1236 | 0.054932 | 0.073242 | -0.068665 | 0.064087 | 0.086975 | 0.022888 | -0.059509 | 122.5616 | 122.4197 | 0.064087 | 122.5525 | 122.6715 | 0.25177 | -0.041199 | 122.5662 | 122.4838 | -0.027466 | 122.5983 | 122.4747 | -0.009156 | -0.004578 | 122.699 | 122.5937 | 122.5845 | -0.21515 | 122.6074 | 122.6303 | 122.6166 | -0.15106
2379.0781 | 122.7219 | -122.5845 | 0.1236 | -0.013122 | 0.071087 | 0.00090781 | 0.0045673 | 0.012324 | -0.0024011 | 5.1244e-05 | -0.0040437 | 0.028343 | -0.0082801 | 0.020316 | 0.0027643 | -0.0087606 | 0.073242 | 0.11444 | 0.14191 | 0.16022 | 0.10986 | 0.050354 | -0.068665 | 0.09613 | 0.11902 | -0.004578 | 0.027466 | 0.036621 | 0.045776 | -0.045776 | 122.6349 | 122.5159 | -0.013733 | 122.699 | 122.7448 | 0.22888 | -0.050354 | 122.6303 | 122.5388 | -0.09613 | 122.6807 | 122.58 | 0.041198 | -0.086975 | 122.6944 | 122.6578 | 122.7264 | -0.19226 | 122.612 | 122.6212 | 122.7036 | -0.16937
2380.8281 | 122.8271 | -122.5616 | 0.07782 | -0.013122 | 0.072796 | 0.0060348 | 0.0058491 | 0.017451 | -0.0021875 | -0.0022986 | -0.011673 | 0.027062 | -0.01063 | 0.021597 | 0.0014825 | -0.0098288 | 0.082397 | 0.13733 | 0.15106 | 0.18768 | 0.1236 | 0.050354 | -0.086975 | 0.10071 | 0.16937 | 0.022888 | 0.013733 | 0.045776 | 0.050354 | -0.022888 | 122.612 | 122.4747 | 0.045776 | 122.699 | 122.7493 | 0.27466 | 0.004577 | 122.612 | 122.5388 | -0.064087 | 122.6624 | 122.5845 | 0.045776 | -0.032044 | 122.6852 | 122.644 | 122.7127 | -0.16479 | 122.5754 | 122.6074 | 122.731 | -0.10071
2382.5781 | 122.7493 | -122.58 | 0.13275 | -0.0054933 | 0.074078 | -0.0012284 | 0.0028583 | 0.011897 | 0.0052893 | -0.00058956 | -0.0040437 | 0.033684 | -0.011057 | 0.023306 | 0.0070367 | -0.011538 | 0.054932 | 0.027466 | 0.041199 | 0.10529 | 0.17395 | 0.013733 | -0.11444 | 0.018311 | 0.018311 | -0.10986 | 0.064087 | 0.054932 | 0.018311 | -0.054932 | 122.5937 | 122.4655 | 0.041199 | 122.6074 | 122.6852 | 0.21973 | -0.077819 | 122.5983 | 122.525 | -0.068664 | 122.5983 | 122.4701 | -0.054931 | -0.077819 | 122.7539 | 122.6349 | 122.6212 | -0.24719 | 122.644 | 122.6349 | 122.5983 | -0.18768
2384.3281 | 122.8683 | -122.5433 | 0.086975 | -0.013122 | 0.070447 | 0.0028306 | 0.0096943 | 0.015955 | -0.0075281 | -0.00058956 | -0.011673 | 0.027916 | -0.0097755 | 0.018393 | 0.0012689 | -0.0079062 | 0.022888 | 0.10529 | 0.13733 | 0.16022 | 0.12817 | 0.041199 | -0.082397 | 0.086975 | 0.15564 | 0.041199 | 0.027466 | 0.027466 | 0.054932 | -0.032043 | 122.5845 | 122.4609 | 0.041199 | 122.6486 | 122.7036 | 0.24261 | -0.064087 | 122.5983 | 122.5113 | -0.059509 | 122.6303 | 122.5845 | 0.073242 | -0.059509 | 122.6715 | 122.5662 | 122.6807 | -0.16937 | 122.5708 | 122.5708 | 122.699 | -0.11902
2386.0781 | 122.8134 | -122.5845 | 0.09613 | -0.020752 | 0.076001 | 0.0013352 | 0.0060627 | 0.015315 | 0.0031531 | -0.0014442 | -0.011673 | 0.031121 | -0.0089209 | 0.025443 | 0.0049005 | -0.0096152 | 0.068665 | 0.054932 | 0.064087 | 0.13275 | 0.16479 | 0.013733 | -0.10529 | 0.064087 | 0.068665 | -0.091553 | 0.050354 | 0.082397 | 0.027466 | -0.064087 | 122.5983 | 122.4792 | 0.068665 | 122.6395 | 122.7173 | 0.23804 | -0.027465 | 122.612 | 122.5204 | -0.045776 | 122.6486 | 122.493 | -0.027466 | -0.013733 | 122.7493 | 122.6532 | 122.6486 | -0.20142 | 122.6349 | 122.6669 | 122.6532 | -0.16022
2387.8125 | 122.7402 | -122.6074 | 0.11902 | -0.020752 | 0.074719 | 0.001976 | 0.0037127 | 0.01446 | 0.0050757 | 0.00069204 | -0.0040437 | 0.031975 | -0.0078529 | 0.024374 | 0.0066095 | -0.0094016 | -0.022888 | -0.050354 | -0.013733 | 0.073242 | 0.16022 | 0.013733 | -0.1236 | 0.004578 | -0.013733 | -0.13733 | 0.064087 | 0.082397 | 0.009155 | -0.041199 | 122.6212 | 122.4838 | 0.041198 | 122.5571 | 122.6807 | 0.19684 | -0.14191 | 122.6166 | 122.5662 | -0.054932 | 122.612 | 122.4701 | -0.09613 | -0.036622 | 122.7676 | 122.5845 | 122.5937 | -0.24261 | 122.6715 | 122.6898 | 122.5937 | -0.16022
2389.4844 | 122.7448 | -122.5937 | 0.091553 | 0.0021362 | 0.065106 | 0.0038986 | 0.0039265 | 0.014674 | -0.0058191 | -0.0031532 | -0.0040437 | 0.025566 | -0.0097755 | 0.020529 | 0.0016963 | -0.0038474 | 0 | 0.064087 | 0.086975 | 0.13275 | 0.14191 | 0.050354 | -0.064087 | 0.032043 | 0.082397 | -0.027466 | 0.041199 | 0.050354 | 0.036621 | -0.036621 | 122.644 | 122.5296 | 0.050354 | 122.6578 | 122.7264 | 0.19684 | -0.091553 | 122.6303 | 122.5571 | -0.050354 | 122.6257 | 122.5662 | 0.009155 | -0.041199 | 122.7356 | 122.5937 | 122.6807 | -0.15564 | 122.6349 | 122.644 | 122.6761 | -0.12817
2391.2344 | 122.8683 | -122.5388 | 0.086975 | -0.013122 | 0.067669 | 0.0043258 | 0.0062763 | 0.015315 | -0.0056055 | -0.0018714 | -0.011673 | 0.027062 | -0.011484 | 0.023093 | 0.0019099 | -0.0072652 | 0.050354 | 0.091553 | 0.10986 | 0.15564 | 0.13275 | 0.036621 | -0.064087 | 0.07782 | 0.13733 | 0.013733 | 0.032043 | 0.032043 | 0.027466 | -0.050354 | 122.5754 | 122.4747 | 0.045776 | 122.6303 | 122.6944 | 0.21973 | -0.036621 | 122.5662 | 122.4884 | -0.054932 | 122.6166 | 122.5525 | 0.064087 | -0.054932 | 122.6715 | 122.5891 | 122.6486 | -0.15106 | 122.5708 | 122.5708 | 122.6761 | -0.13733
2392.9219 | 122.7356 | -122.5845 | 0.11444 | -0.013122 | 0.065533 | 0.0058212 | 0.0034991 | 0.014674 | -0.0028283 | -0.002085 | -0.0040437 | 0.027275 | -0.011698 | 0.01882 | 0.0055415 | -0.0096152 | 0.036621 | 0.073242 | 0.086975 | 0.14191 | 0.13275 | 0.059509 | -0.068665 | 0.032043 | 0.07782 | -0.027466 | 0.027466 | 0.045776 | 0.050354 | -0.050354 | 122.644 | 122.5159 | 0.01831 | 122.6578 | 122.7264 | 0.21057 | -0.07782 | 122.6349 | 122.5342 | -0.086975 | 122.6166 | 122.5571 | 0.022888 | -0.068665 | 122.7173 | 122.6212 | 122.6715 | -0.18311 | 122.612 | 122.6303 | 122.6624 | -0.16479
2394.6719 | 122.8821 | -122.5525 | 0.086975 | 0.0021362 | 0.071301 | 0.0026168 | 0.0062763 | 0.016383 | 0.0031531 | -0.00058956 | -0.0040437 | 0.031761 | -0.0089209 | 0.02352 | 0.0046869 | -0.011538 | 0.013733 | -0.009155 | 0.013733 | 0.11444 | 0.17853 | 0.032043 | -0.1236 | 0.027466 | 0.045776 | -0.09613 | 0.07782 | 0.07782 | 0.009155 | -0.059509 | 122.5845 | 122.4289 | 0.091553 | 122.5433 | 122.6669 | 0.23804 | -0.073242 | 122.5616 | 122.493 | -0.009155 | 122.58 | 122.4564 | -0.036621 | -0.009155 | 122.731 | 122.5662 | 122.5662 | -0.21057 | 122.6303 | 122.6303 | 122.5983 | -0.14648
2396.4375 | 122.8729 | -122.5571 | 0.07782 | -0.020752 | 0.070019 | 0.0051804 | 0.0052081 | 0.01681 | -0.0043237 | -0.0022986 | -0.019302 | 0.024285 | -0.011271 | 0.022238 | 0.00084166 | -0.010256 | 0.091553 | 0.16022 | 0.16937 | 0.17853 | 0.12817 | 0.045776 | -0.082397 | 0.09613 | 0.17853 | 0.032043 | 0.018311 | 0.022888 | 0.045776 | -0.022888 | 122.6028 | 122.4747 | 0.050354 | 122.7173 | 122.7356 | 0.26092 | 0.013733 | 122.6028 | 122.5342 | -0.059509 | 122.6532 | 122.5891 | 0.054931 | -0.054932 | 122.6852 | 122.6486 | 122.7264 | -0.16022 | 122.5754 | 122.58 | 122.7356 | -0.10071
2398.1094 | 122.8729 | -122.5479 | 0.11444 | -0.020752 | 0.074292 | 0.0028306 | 0.0064899 | 0.015742 | 0.0037939 | 5.1244e-05 | -0.011673 | 0.030052 | -0.0072119 | 0.022025 | 0.0036189 | -0.010256 | 0.004578 | -0.013733 | 0.004578 | 0.10529 | 0.1831 | 0.004578 | -0.12817 | -0.004578 | 0.022888 | -0.1236 | 0.073242 | 0.086975 | 0.018311 | -0.059509 | 122.5525 | 122.4197 | 0.068664 | 122.5342 | 122.6532 | 0.23346 | -0.10986 | 122.5662 | 122.4884 | -0.041199 | 122.5433 | 122.4243 | -0.064087 | -0.027466 | 122.731 | 122.5525 | 122.5525 | -0.24262 | 122.6212 | 122.6349 | 122.5708 | -0.17395
2399.8594 | 122.8958 | -122.5479 | 0.073242 | -0.0054933 | 0.07771 | -0.00058739 | 0.0049945 | 0.01446 | 0.0035803 | -0.00016236 | 0.0035858 | 0.031121 | -0.010203 | 0.023734 | 0.0042597 | -0.011751 | 0.032043 | 0.022888 | 0.045776 | 0.13275 | 0.16937 | 0.022888 | -0.10986 | 0.050354 | 0.068665 | -0.07782 | 0.068665 | 0.086975 | 0.013733 | -0.054932 | 122.5708 | 122.438 | 0.096131 | 122.5708 | 122.6807 | 0.24261 | -0.041199 | 122.5616 | 122.493 | -0.004577 | 122.5983 | 122.4701 | -0.022888 | 0.013733 | 122.7173 | 122.58 | 122.5937 | -0.18311 | 122.6166 | 122.6349 | 122.6166 | -0.12817
2401.5625 | 122.8317 | -122.5754 | 0.07782 | -0.013122 | 0.067669 | 0.003685 | 0.0034991 | 0.014887 | -0.0049645 | -0.0012306 | 0.0035858 | 0.027916 | -0.01063 | 0.017966 | 0.0036189 | -0.0079062 | 0.064087 | 0.15564 | 0.15106 | 0.18768 | 0.14648 | 0.059509 | -0.082397 | 0.07782 | 0.16479 | 0.013733 | 0.022888 | 0.045776 | 0.036621 | -0.036621 | 122.6349 | 122.493 | 0.068664 | 122.731 | 122.7631 | 0.27008 | -0.013733 | 122.612 | 122.5388 | -0.054932 | 122.6532 | 122.5891 | 0.050354 | -0.032044 | 122.7219 | 122.6395 | 122.7264 | -0.16022 | 122.5983 | 122.6212 | 122.7402 | -0.11444

## Thermal Data
Fire Time | B Position - Conduit - 3' | B Position - Conduit - Middle | B Position - Conduit - 7'
-0.6521 | 8.2645 | 8.3133 | 8.2534
0.3479 | 8.2699 | 8.3142 | 8.2505
1.3479 | 8.2723 | 8.3137 | 8.2586
2.3479 | 8.2695 | 8.314 | 8.2578
3.3479 | 8.2717 | 8.3166 | 8.2596
4.3479 | 8.2745 | 8.3125 | 8.2637
5.3479 | 8.2761 | 8.3134 | 8.2641
6.3479 | 8.2786 | 8.3229 | 8.2666
7.3479 | 8.2807 | 8.3188 | 8.2699
8.3479 | 8.2852 | 8.3163 | 8.266
9.3479 | 8.2833 | 8.3194 | 8.267
10.3479 | 8.2885 | 8.3301 | 8.2776
11.3479 | 8.2939 | 8.3286 | 8.2816
12.3479 | 8.3015 | 8.3879 | 8.2998
13.3479 | 8.3026 | 8.634 | 8.4226
14.3479 | 8.3025 | 8.767 | 8.528
15.3479 | 8.3589 | 8.9593 | 8.4813
16.3479 | 8.4662 | 9.1808 | 8.6417
17.3479 | 8.5179 | 9.4294 | 8.8087
18.3479 | 8.5665 | 10.1315 | 8.7719
19.3479 | 8.7356 | 9.749 | 8.7709
20.3479 | 8.7447 | 10.3754 | 8.8125
21.3479 | 8.7354 | 10.3567 | 8.9122
22.3479 | 8.7245 | 10.7277 | 9.0825
23.3479 | 8.9675 | 11.0609 | 9.1575
24.3479 | 9.2328 | 11.2852 | 9.2023
25.3479 | 9.3646 | 11.1934 | 9.4034
26.3479 | 9.3532 | 11.4773 | 9.2904
27.3479 | 9.4205 | 12.0304 | 9.4003
28.3635 | 9.5814 | 12.1095 | 9.4812
29.3479 | 9.6881 | 12.7141 | 9.7098
30.3479 | 9.8647 | 13.422 | 9.7247
31.3479 | 9.7692 | 13.2995 | 9.872
32.3479 | 9.8942 | 13.3451 | 10.0068
33.3479 | 10.0006 | 13.8081 | 10.076
34.3479 | 10.3737 | 14.1158 | 10.1519
35.3479 | 10.4122 | 14.7384 | 10.2932
36.3479 | 10.5828 | 14.7766 | 10.3695
37.3479 | 10.6399 | 15.1718 | 10.5144
38.3479 | 10.577 | 15.5336 | 10.6074
39.3479 | 10.8443 | 16.1782 | 10.8024
40.3479 | 11.094 | 16.4578 | 11.207
41.3479 | 10.9751 | 16.7561 | 11.1081
42.3479 | 11.1932 | 16.9732 | 11.1988
43.3479 | 11.3285 | 18.0417 | 11.3802
44.3479 | 11.4638 | 18.6726 | 11.5265
45.3479 | 11.3961 | 19.4505 | 11.6541
46.3479 | 11.5697 | 20.1333 | 11.7683
47.3479 | 11.8149 | 20.5187 | 11.9429
48.3479 | 11.948 | 21.7635 | 11.9937
49.3479 | 12.4373 | 21.9162 | 12.1237
50.3479 | 12.6491 | 22.0841 | 12.2808
51.3479 | 12.9052 | 22.8674 | 12.4501
52.3479 | 12.5811 | 23.485 | 12.5907
53.3479 | 12.5677 | 23.8054 | 12.7012
54.3479 | 12.8266 | 23.9237 | 12.847
55.3635 | 13.3569 | 23.9417 | 12.9155
56.3479 | 13.1053 | 24.8694 | 13.1617
57.3479 | 13.266 | 25.1519 | 13.4798
58.3479 | 13.0873 | 25.191 | 13.7404
59.3479 | 13.2924 | 25.6252 | 13.8763
60.3479 | 13.3293 | 25.9044 | 14.3738
61.3479 | 13.5944 | 26.0183 | 14.3676
62.3479 | 13.371 | 26.4312 | 14.4651
63.3479 | 13.751 | 26.8154 | 14.7592
64.3479 | 13.8711 | 27.2611 | 15.2794
65.3479 | 13.9877 | 27.2428 | 15.4017
66.3479 | 14.2192 | 28.0193 | 15.4696
67.3479 | 14.4373 | 29.0936 | 15.4464
68.3479 | 14.6262 | 28.9078 | 16.1079
69.3479 | 14.7546 | 29.0427 | 16.34
70.3479 | 14.8678 | 29.9937 | 16.3965
71.3479 | 15.3057 | 30.2883 | 16.2624
72.3479 | 15.3794 | 31.9822 | 16.3125
73.3479 | 15.6931 | 32.478 | 16.6073
74.3479 | 15.9109 | 33.4675 | 16.667
75.3479 | 15.8851 | 33.4754 | 16.8673
76.3479 | 15.9676 | 33.7696 | 16.9657
77.3479 | 16.0568 | 34.2195 | 17.1132
78.3479 | 16.4049 | 34.5741 | 17.278
79.3479 | 16.3874 | 35.6502 | 17.566
80.3479 | 16.7356 | 36.0329 | 17.6726
81.3479 | 16.4656 | 36.8994 | 17.9413
82.3479 | 16.3919 | 37.6267 | 17.998
83.3479 | 16.9686 | 37.5227 | 18.2585
84.3479 | 17.0511 | 38.3171 | 18.3062
85.3479 | 17.275 | 39.3248 | 18.6744
86.3479 | 17.2767 | 40.7226 | 18.7379
87.3479 | 17.4841 | 40.8232 | 18.814
88.3479 | 17.373 | 40.838 | 19.055
89.3479 | 17.5458 | 41.1831 | 19.1649
90.3479 | 17.738 | 42.4857 | 19.4641
91.3479 | 17.9897 | 42.3606 | 19.5095
92.3479 | 18.1045 | 43.3349 | 19.8867
93.3479 | 18.234 | 44.4842 | 19.9256
94.3479 | 18.3504 | 44.735 | 19.9887
95.3479 | 18.8383 | 44.8232 | 20.116
96.3479 | 18.7234 | 45.699 | 20.2891
97.3479 | 18.8715 | 45.9105 | 20.4877
98.3479 | 19.0043 | 46.7624 | 20.5694
99.3479 | 19.0425 | 46.6669 | 20.725
100.3479 | 19.1317 | 47.1443 | 20.8594
101.3479 | 19.2706 | 47.5291 | 21.0463
102.3479 | 19.4095 | 48.0025 | 21.2692
103.3479 | 19.4716 | 48.6631 | 21.3429
104.3479 | 19.75 | 49.2484 | 21.5597
105.3479 | 19.8844 | 49.4522 | 21.8303
106.3479 | 20.0634 | 50.5732 | 21.969
107.3479 | 20.1503 | 50.3998 | 22.0688
108.3479 | 20.3312 | 51.2269 | 22.2493
109.3479 | 20.3333 | 52.2036 | 22.576
110.3479 | 20.6294 | 52.785 | 22.4928
111.3479 | 20.9794 | 53.4765 | 22.7727
112.3479 | 21.0578 | 53.6056 | 22.9713
113.3479 | 21.2721 | 54.0903 | 22.9788
114.3479 | 21.1786 | 54.1677 | 23.3493
115.3479 | 21.5903 | 55.3061 | 23.5098
116.3479 | 21.5023 | 55.435 | 23.6034
117.3479 | 21.5465 | 55.4321 | 23.5573
118.3479 | 21.713 | 56.0705 | 23.7886
119.3479 | 21.9968 | 56.3803 | 23.9711
120.3479 | 22.2392 | 56.7223 | 24.2378
121.3479 | 22.3678 | 57.6109 | 24.4236
122.3479 | 22.5278 | 57.6352 | 24.4852
123.3479 | 22.8136 | 58.0628 | 24.7064
124.3479 | 22.9007 | 58.4014 | 24.7161
125.3479 | 23.2685 | 59.1009 | 24.9667
126.3479 | 23.3927 | 59.475 | 25.0019
127.3479 | 23.0914 | 60.2759 | 25.3191
128.3479 | 23.2411 | 60.9255 | 25.5453
129.3479 | 23.6029 | 61.7331 | 26.0287
130.3479 | 23.5029 | 61.8668 | 25.9376
131.3479 | 23.7694 | 61.9116 | 25.8704
132.3479 | 23.9211 | 62.4918 | 26.1365
133.3479 | 23.8714 | 63.5201 | 26.3208
134.3479 | 24.4851 | 63.3595 | 26.5387
135.3479 | 24.1918 | 63.9542 | 26.8133
136.3479 | 24.7921 | 64.2413 | 26.9298
137.3479 | 24.6365 | 65.3872 | 27.0965
138.3479 | 25.1736 | 66.5558 | 27.1119
139.3479 | 24.8873 | 66.6586 | 27.3445
140.3479 | 25.0115 | 67.6361 | 27.6456
141.3479 | 25.1665 | 69.1363 | 27.7934
142.3479 | 24.9746 | 69.6481 | 28.079
143.3479 | 25.161 | 70.4808 | 28.1824
144.3479 | 25.5799 | 70.7412 | 28.391
145.3479 | 25.6916 | 71.0557 | 28.6896
146.3479 | 25.5826 | 72.4053 | 28.776
147.3479 | 25.7552 | 73.3435 | 28.9748
148.3479 | 25.9058 | 74.5739 | 28.9605
149.3479 | 25.9185 | 74.2327 | 29.214
150.3479 | 25.9717 | 75.8479 | 29.3056
151.3479 | 26.3428 | 76.5151 | 29.6875
152.3479 | 26.6254 | 76.2611 | 29.8435
153.3479 | 26.7236 | 76.8218 | 29.8376
154.3479 | 26.9039 | 78.4134 | 29.9283
155.3479 | 27.5491 | 78.7422 | 30.235
156.3479 | 27.3863 | 79.5025 | 30.4197
157.3479 | 27.5744 | 79.7358 | 30.6014
158.3479 | 28.2145 | 80.8697 | 30.7768
159.3479 | 28.1927 | 80.9553 | 30.8443
160.3479 | 28.615 | 81.2713 | 31.1986
161.3479 | 28.4249 | 82.4546 | 31.3542
162.3479 | 28.2885 | 83.4955 | 31.5995
163.3479 | 28.398 | 84.0933 | 31.8433
164.3479 | 28.5401 | 84.8155 | 31.9035
165.3479 | 28.7126 | 85.3137 | 31.9194
166.3479 | 29.6791 | 85.8439 | 32.2691
167.3479 | 29.608 | 87.4114 | 32.4315
168.3479 | 29.5553 | 87.1304 | 32.594
169.3479 | 29.4994 | 88.689 | 32.8285
170.3479 | 29.4743 | 88.8535 | 33.1578
171.3479 | 29.893 | 89.771 | 33.1152
172.3479 | 30.1882 | 90.5366 | 33.2678
173.3479 | 30.1549 | 91.9262 | 33.6935
174.3479 | 30.203 | 92.2886 | 33.7717
175.3479 | 30.3532 | 92.8887 | 34.0515
176.3479 | 30.386 | 93.0631 | 34.1962
177.3479 | 30.7531 | 93.9452 | 34.3174
178.3479 | 30.8444 | 95.0665 | 34.58
179.3479 | 30.8957 | 96.061 | 34.7134
180.3479 | 31.1489 | 96.3285 | 34.8456
181.3479 | 31.5474 | 96.7385 | 35.1348
182.3479 | 31.5002 | 98.8427 | 35.3818
183.3479 | 31.5615 | 99.2002 | 35.5726
184.3479 | 31.7153 | 99.4831 | 35.648
185.3479 | 32.2056 | 100.412 | 35.8533
186.3479 | 32.0689 | 101.6036 | 36.051
187.3479 | 32.3769 | 101.5239 | 36.2539
188.3479 | 32.6032 | 101.888 | 36.4255
189.3479 | 32.6513 | 102.4256 | 36.4709
190.3479 | 32.6891 | 103.416 | 36.5637
191.3479 | 33.0927 | 105.2524 | 36.8588
192.3479 | 33.2563 | 104.8127 | 37.0826
193.3479 | 33.2839 | 106.2342 | 37.3549
194.3479 | 33.6972 | 106.5262 | 37.5133
195.3479 | 33.6792 | 107.8537 | 37.6914
196.3479 | 33.6646 | 108.8456 | 37.9993
197.3479 | 34.1303 | 109.4709 | 38.0192
198.3479 | 34.3276 | 110.9732 | 38.2327
199.3479 | 35.0091 | 110.8228 | 38.3071
200.3479 | 35.0681 | 111.1469 | 38.5973
201.3479 | 35.2096 | 112.0367 | 38.9442
202.3479 | 35.5691 | 113.1309 | 38.9899
203.3479 | 35.3671 | 113.9487 | 39.0737
204.3479 | 35.3931 | 114.7514 | 39.3752
205.3479 | 35.4066 | 116.2397 | 39.5332
206.3479 | 35.5657 | 116.5325 | 39.6995
207.3479 | 36.2859 | 116.7109 | 39.8887
208.3479 | 36.0983 | 117.4299 | 40.1261
209.3479 | 36.0784 | 117.9394 | 40.4153
210.3479 | 36.3641 | 119.5217 | 40.5343
211.3479 | 36.5156 | 119.6446 | 40.7848
212.3479 | 36.6038 | 120.5593 | 40.9123
213.3479 | 36.9599 | 121.7111 | 41.1797
214.3479 | 37.4266 | 122.3497 | 41.6147
215.3479 | 37.3233 | 122.5336 | 41.5905
216.3479 | 37.3521 | 124.3047 | 41.6312
217.3479 | 37.484 | 124.4974 | 41.8816
218.3479 | 37.6066 | 125.1336 | 42.1793
219.3479 | 38.0123 | 127.0075 | 42.2499
220.3479 | 38.1964 | 126.7587 | 42.6462
221.3479 | 38.2209 | 128.6565 | 42.6489
222.3479 | 38.3467 | 129.5009 | 42.8959
223.3479 | 38.7796 | 130.3373 | 43.2378
224.3479 | 38.9549 | 131.2667 | 43.3565
225.3479 | 39.1902 | 131.9197 | 43.5564
226.3479 | 39.246 | 132.8194 | 43.7881
227.3479 | 39.4703 | 134.6629 | 44.0493
228.3479 | 39.5058 | 134.1827 | 44.09
229.3479 | 39.8897 | 134.1615 | 44.4421
230.3479 | 40.1229 | 134.9754 | 44.4584
231.3479 | 40.4396 | 135.713 | 44.8857
232.3479 | 40.9211 | 137.2108 | 45.021
233.3479 | 40.8082 | 137.6674 | 45.5025
234.3479 | 41.5357 | 137.951 | 45.3815
235.3479 | 41.4703 | 138.0913 | 45.5433
236.3479 | 41.8579 | 139.2139 | 45.749
237.3479 | 41.8226 | 139.94 | 45.9577
238.3479 | 42.0066 | 140.2186 | 46.0572
239.3479 | 42.0613 | 140.9281 | 46.1848
240.3479 | 42.5006 | 141.5115 | 46.4833
241.3479 | 42.962 | 142.364 | 46.7877
242.3479 | 42.7575 | 143.0539 | 46.9365
243.3479 | 43.0173 | 143.8446 | 47.1378
244.3479 | 43.6393 | 144.9285 | 47.2715
245.3479 | 43.2558 | 145.8901 | 47.6494
246.3479 | 43.5305 | 146.3889 | 47.7792
247.3479 | 43.945 | 146.8688 | 47.9719
248.3479 | 44.023 | 148.1527 | 48.337
249.3479 | 44.4988 | 147.7543 | 48.3814
250.3479 | 44.8576 | 148.6877 | 48.6391
251.3479 | 45.1486 | 150.0988 | 49.0203
252.3479 | 45.3943 | 149.7335 | 49.1222
253.3479 | 45.8167 | 149.9982 | 49.2794
254.3479 | 45.7408 | 151.3043 | 49.4794
255.3479 | 45.8065 | 152.1506 | 49.6641
256.3479 | 46.2482 | 153.2041 | 49.8016
257.3479 | 46.0607 | 154.1553 | 50.1794
258.3479 | 46.1261 | 154.1267 | 50.2921
259.3479 | 46.0252 | 154.8593 | 50.7452
260.3479 | 46.4054 | 155.7628 | 50.7966
261.3479 | 46.9221 | 155.9957 | 51.116
262.3479 | 46.8431 | 156.4318 | 51.2019
263.3479 | 47.463 | 157.375 | 51.3818
264.3479 | 47.4167 | 157.5298 | 51.6994
265.3479 | 47.4389 | 158.3781 | 51.6749
266.3479 | 47.6952 | 159.3736 | 52.201
267.3479 | 48.0133 | 160.2809 | 52.2772
268.3479 | 48.1261 | 160.5388 | 52.3553
269.3479 | 48.3363 | 160.9192 | 52.7182
270.3479 | 48.6921 | 161.2204 | 52.7708
271.3479 | 54.9211 | 164.4095 | 53.7336
272.3479 | 49.0534 | 162.2344 | 53.2171
273.3479 | 49.1947 | 163.4405 | 53.4781
274.3479 | 49.7771 | 163.6526 | 53.6513
275.3479 | 50.0173 | 165.4306 | 54.089
276.3479 | 50.5369 | 165.6048 | 54.283
277.3479 | 50.6998 | 167.5372 | 54.3949
278.3479 | 50.6776 | 168.3613 | 54.7909
279.3479 | 50.6563 | 169.1158 | 55.0053
280.3479 | 50.9073 | 170.8568 | 55.3492
281.3479 | 51.146 | 172.5427 | 55.6443
282.3479 | 51.3304 | 172.7693 | 55.7099
283.3479 | 52.1222 | 174.0535 | 56.1298
284.3479 | 52.0823 | 174.7392 | 56.3789
285.3479 | 52.4964 | 175.3786 | 56.7375
286.3479 | 52.8921 | 177.3425 | 57.3546
287.3479 | 52.9196 | 178.6307 | 57.2754
288.3479 | 52.9681 | 178.3819 | 57.4099
289.3479 | 52.9516 | 179.2152 | 57.6882
290.3479 | 53.2898 | 180.2116 | 57.7874
291.3479 | 53.5869 | 180.9833 | 58.2746
292.3479 | 53.9256 | 182.8402 | 58.4104
293.3479 | 54.3544 | 183.6518 | 58.7452
294.3479 | 54.3266 | 185.4449 | 59.0285
295.3479 | 54.3841 | 185.4874 | 59.1206
296.3479 | 54.9084 | 185.8555 | 59.3939
297.3479 | 55.088 | 187.2148 | 59.736
298.3479 | 55.5175 | 187.2871 | 59.9605
299.3479 | 55.9226 | 188.3054 | 60.0681
300.3479 | 55.8315 | 189.4043 | 60.3082
301.3479 | 56.0066 | 190.8001 | 60.7198
302.3479 | 56.1591 | 192.202 | 60.9159
303.3479 | 56.188 | 192.5246 | 61.1493
304.3479 | 56.6942 | 193.2364 | 61.693
305.3479 | 57.2236 | 195.9744 | 61.7791
306.3479 | 57.1274 | 196.0224 | 62.0001
307.3479 | 57.2421 | 196.3519 | 62.0724
308.3479 | 57.3933 | 196.3678 | 62.5275
309.3479 | 58.3654 | 197.5791 | 62.7369
310.3479 | 58.158 | 199.4505 | 63.0542
311.3479 | 58.2874 | 199.6935 | 63.043
312.3479 | 58.4218 | 199.175 | 63.4126
313.3479 | 58.4755 | 201.1514 | 63.643
314.3479 | 58.8329 | 201.3294 | 63.8701
315.3479 | 59.3239 | 203.3644 | 64.2254
316.3479 | 59.3975 | 203.0514 | 64.4192
317.3479 | 59.8683 | 203.4328 | 64.8202
318.3479 | 60.0222 | 205.453 | 65.0122
319.3479 | 60.114 | 205.2447 | 65.612
320.3479 | 60.4942 | 207.6212 | 65.5676
321.3479 | 60.728 | 207.2475 | 66.1545
322.3479 | 60.8054 | 207.1913 | 66.2513
323.3479 | 60.7954 | 209.1409 | 66.675
324.3479 | 60.9718 | 210.2118 | 66.8277
325.3479 | 61.4713 | 209.8657 | 67.3772
326.3479 | 61.5152 | 211.6794 | 67.4635
327.3479 | 61.5599 | 212.7962 | 68.0422
328.3479 | 62.1738 | 213.2407 | 68.0893
329.3479 | 62.2077 | 214.4429 | 68.1739
330.3479 | 62.701 | 215.2651 | 68.4877
331.3479 | 62.8628 | 215.2757 | 68.672
332.3479 | 63.1451 | 216.4311 | 69.109
333.3479 | 63.6554 | 216.9816 | 69.2118
334.3479 | 64.0872 | 218.7429 | 69.6721
335.3479 | 63.9271 | 219.7864 | 69.8382
336.3479 | 64.2397 | 221.4619 | 70.1647
337.3479 | 64.3435 | 223.5488 | 70.5456
338.3479 | 64.4646 | 223.4985 | 70.8578
339.3479 | 64.6895 | 224.5211 | 71.1354
340.3479 | 65.1087 | 225.0593 | 71.5449
341.3479 | 65.2364 | 227.9459 | 71.8686
342.3479 | 65.2907 | 228.6976 | 72.3533
343.3479 | 65.5305 | 229.3809 | 72.5
344.3479 | 65.865 | 230.2309 | 72.8839
345.3479 | 66.2841 | 231.5687 | 73.1677
346.3479 | 66.9453 | 232.2869 | 73.5497
347.3479 | 67.1241 | 232.2266 | 73.6592
348.3479 | 67.066 | 233.4654 | 74.1304
349.3479 | 67.1948 | 234.1378 | 74.4372
350.3479 | 67.2935 | 234.0576 | 74.7914
351.3479 | 67.5667 | 234.5968 | 75.2105
352.3479 | 67.8946 | 236.0255 | 75.5637
353.3479 | 68.1224 | 236.9622 | 75.8101
354.3479 | 68.4399 | 237.3851 | 75.9789
355.3479 | 68.912 | 238.0084 | 76.0471
356.3479 | 69.4086 | 239.0016 | 76.3341
357.3479 | 69.4208 | 239.7437 | 76.7995
358.3479 | 69.7689 | 241.0822 | 77.083
359.3479 | 69.8007 | 242.0469 | 77.5436
360.3479 | 69.7961 | 243.148 | 77.9645
361.3479 | 70.1299 | 244.4764 | 78.3545
362.3479 | 70.2939 | 245.1529 | 78.7119
363.3479 | 70.8274 | 246.271 | 78.9338
364.3479 | 70.9766 | 247.0518 | 79.3256
365.3479 | 71.5022 | 247.623 | 79.6158
366.3479 | 71.6647 | 247.9363 | 79.8388
367.3479 | 72.1998 | 248.6993 | 80.0848
368.3479 | 72.2639 | 250.1824 | 80.4067
369.3479 | 72.519 | 250.6043 | 80.7078
370.3479 | 72.7456 | 250.6608 | 81.0146
371.3479 | 73.145 | 252.2615 | 81.4675
372.3479 | 73.3054 | 252.7005 | 81.8566
373.3479 | 73.2735 | 253.843 | 82.2758
374.3479 | 73.6545 | 254.4849 | 82.5558
375.3479 | 74.404 | 255.0126 | 82.7365
376.3479 | 74.6331 | 255.4549 | 83.1618
377.3479 | 74.9321 | 256.9447 | 83.7192
378.3479 | 75.3063 | 257.6613 | 83.9684
379.3479 | 75.5372 | 258.7979 | 84.2359
380.3479 | 75.7199 | 258.5284 | 84.643
381.3479 | 75.9497 | 259.9055 | 84.9178
382.3479 | 76.0794 | 261.1312 | 85.2575
383.3479 | 76.6257 | 261.1363 | 85.7257
384.3479 | 76.8759 | 262.6854 | 86.2428
385.3479 | 76.8754 | 263.9878 | 86.4679
386.3479 | 77.1094 | 265.0974 | 87.0186
387.3479 | 77.1956 | 266.3616 | 87.306
388.3479 | 77.5597 | 266.5835 | 87.7536
389.3479 | 77.9408 | 266.6784 | 87.9984
390.3479 | 78.5657 | 268.0079 | 88.3392
391.3479 | 79.4108 | 269.2439 | 88.9763
392.3479 | 79.7553 | 269.6303 | 89.1877
393.3479 | 79.8762 | 270.9154 | 89.6703
394.3479 | 80.005 | 270.514 | 89.8668
395.3479 | 80.1295 | 272.2344 | 90.356
396.3479 | 80.3672 | 272.1675 | 90.8272
397.3479 | 80.5695 | 273.3278 | 91.0854
398.3479 | 81.1007 | 273.9218 | 91.5046
399.3479 | 81.5963 | 275.9398 | 91.8381
400.3479 | 81.8621 | 276.7627 | 92.4984
401.3479 | 81.9481 | 277.3781 | 92.9667
402.3479 | 81.8689 | 276.4957 | 93.2281
403.3479 | 82.118 | 277.5292 | 93.6371
404.3479 | 82.2066 | 278.6083 | 94.3435
405.3479 | 82.4988 | 279.8933 | 94.4172
406.3479 | 83.0194 | 280.6106 | 94.78
407.3479 | 83.1207 | 280.8274 | 95.1084
408.3479 | 83.2296 | 282.1749 | 95.654
409.3479 | 84.2856 | 282.6818 | 95.9436
410.3479 | 84.5776 | 284.9649 | 96.3135
411.3479 | 84.695 | 284.8022 | 96.4996
412.3479 | 84.9082 | 285.3333 | 96.6958
413.3479 | 85.3956 | 285.3623 | 97.1215
414.3479 | 85.6518 | 286.9266 | 97.4318
415.3479 | 85.7 | 287.628 | 97.8533
416.3479 | 86.2268 | 288.5045 | 98.388
417.3479 | 86.5683 | 288.9408 | 98.9114
418.3479 | 86.8653 | 289.9914 | 99.2029
419.3479 | 87.1034 | 292.0993 | 100.1403
420.3479 | 87.2577 | 291.8517 | 100.1276
421.3479 | 87.3319 | 292.9571 | 100.7568
422.3479 | 87.8122 | 293.6606 | 100.9692
423.3479 | 87.7778 | 294.8376 | 101.448
424.3479 | 88.1448 | 295.148 | 101.6001
425.3479 | 88.4479 | 295.7239 | 102.25
426.3479 | 88.8676 | 296.9477 | 102.572
427.3479 | 89.157 | 297.2411 | 102.7712
428.3479 | 89.2909 | 299.9328 | 103.405
429.3479 | 89.5194 | 300.0989 | 104.2554
430.3479 | 89.8612 | 301.517 | 104.4598
431.3479 | 89.8797 | 301.5477 | 104.9574
432.3479 | 90.2157 | 302.3099 | 105.194
433.3479 | 90.3434 | 303.3869 | 105.7325
434.3479 | 90.9318 | 304.7608 | 106.4013
435.3479 | 91.3176 | 306.7063 | 106.6604
436.3479 | 91.5317 | 306.6525 | 107.1083
437.3479 | 91.5464 | 306.5354 | 107.362
438.3479 | 91.9443 | 307.6734 | 107.6421
439.3479 | 92.3963 | 308.5776 | 108.3297
440.3479 | 92.8058 | 309.0678 | 109.311
441.3479 | 93.4612 | 309.9436 | 109.3787
442.3479 | 93.3908 | 310.5701 | 110.0521
443.3479 | 93.8541 | 311.971 | 110.5775
444.3479 | 93.9951 | 311.7895 | 110.8221
445.3479 | 93.9584 | 312.3406 | 111.2775
446.3479 | 94.2948 | 312.7366 | 111.8268
447.3479 | 94.6671 | 313.0998 | 111.9803
448.3479 | 95.0675 | 314.3264 | 112.4728
449.3479 | 95.2055 | 314.3582 | 113.0251
450.3479 | 95.4058 | 315.1638 | 113.3759
451.3479 | 95.8394 | 315.721 | 113.9089
452.3479 | 97.7271 | 316.9058 | 114.3107
453.3479 | 96.6939 | 316.5004 | 114.4811
454.3479 | 96.9543 | 316.855 | 114.7627
455.3479 | 97.6123 | 317.7313 | 115.282
456.3479 | 98.102 | 317.779 | 115.7978
457.3479 | 97.9221 | 318.3828 | 116.27
458.3479 | 98.2492 | 318.8222 | 116.5491
459.3479 | 98.3507 | 320.3847 | 117.1221
460.3479 | 98.495 | 320.4538 | 117.754
461.3479 | 98.7211 | 321.9776 | 118.3395
462.3479 | 99.1094 | 322.9651 | 119.0218
463.3479 | 99.5145 | 322.6415 | 119.1353
464.3479 | 100.141 | 324.7322 | 119.8675
465.3479 | 100.5761 | 324.2504 | 119.9215
466.3479 | 100.5815 | 324.2137 | 120.3928
467.3479 | 100.6575 | 324.2197 | 120.5953
468.3479 | 100.9021 | 324.7814 | 120.9595
469.3479 | 101.3446 | 325.4334 | 121.6646
470.3479 | 101.4753 | 325.7084 | 122.2113
471.3479 | 101.8718 | 326.5852 | 122.3246
472.3479 | 102.012 | 327.5902 | 122.9916
473.3479 | 102.0966 | 327.8692 | 123.5243
474.3479 | 102.6163 | 328.3564 | 123.8911
475.3479 | 103.3064 | 328.8774 | 124.4604
476.3479 | 103.8584 | 329.9335 | 124.6314
477.3479 | 104.0869 | 329.8568 | 124.8276
478.3479 | 104.4179 | 330.9334 | 125.4161
479.3479 | 104.9517 | 330.5718 | 125.735
480.3479 | 105.8591 | 330.832 | 126.146
481.3479 | 105.6465 | 331.0975 | 126.6259
482.3479 | 105.5902 | 331.5017 | 126.8607
483.3479 | 105.8312 | 332.0667 | 127.2427
484.3479 | 105.7796 | 332.1763 | 127.6781
485.3479 | 106.1514 | 333.0925 | 128.1532
486.3479 | 106.532 | 333.2388 | 128.4642
487.3479 | 106.5913 | 333.5853 | 128.9355
488.3479 | 106.5804 | 334.0578 | 129.4955
489.3479 | 107.1154 | 334.4219 | 129.8249
490.3479 | 107.1223 | 335.0255 | 130.3612
491.3479 | 107.5376 | 335.7723 | 130.6993
492.3479 | 108.113 | 336.3394 | 130.9782
493.3479 | 108.6137 | 337.2048 | 131.3169
494.3479 | 109.217 | 336.9702 | 131.8173
495.3479 | 109.3579 | 336.8169 | 132.0343
496.3479 | 109.2829 | 337.8694 | 132.6101
497.3479 | 109.6868 | 337.9154 | 132.8765
498.3479 | 109.8886 | 338.8072 | 133.4742
499.3479 | 110.1325 | 338.768 | 133.7947
500.3479 | 110.2558 | 338.9076 | 134.0907
501.3479 | 110.3619 | 339.2031 | 134.5209
502.3479 | 110.7092 | 339.6376 | 135.0035
503.3479 | 111.1443 | 340.1267 | 135.2825
504.3479 | 111.3951 | 340.4768 | 135.6957
505.3479 | 111.6791 | 340.9335 | 136.164
506.3479 | 112.0573 | 341.6445 | 136.5434
507.3479 | 112.3319 | 341.605 | 136.9028
508.3479 | 112.4828 | 341.9738 | 137.4144
509.3479 | 112.7717 | 343.0498 | 138.2729
510.3479 | 113.166 | 343.7172 | 138.4843
511.3479 | 113.6781 | 344.709 | 138.7353
512.3479 | 113.938 | 344.7985 | 139.1451
513.3479 | 114.2749 | 344.7864 | 139.7228
514.3479 | 115.1409 | 345.6376 | 140.1357
515.3479 | 115.1487 | 346.0304 | 140.2788
516.3479 | 115.9305 | 345.7271 | 140.6389
517.3479 | 115.7556 | 346.0927 | 141.0899
518.3479 | 116.1674 | 346.7622 | 141.4496
519.3479 | 116.2712 | 346.7807 | 141.8445
520.3479 | 116.3812 | 347.4066 | 142.0886
521.3479 | 116.682 | 347.4505 | 142.5436
522.3479 | 117.3547 | 347.8537 | 142.9118
523.3479 | 117.4369 | 348.2066 | 143.4074
524.3479 | 117.6198 | 348.4957 | 143.8064
525.3479 | 118.1868 | 349.0572 | 144.2728
526.3479 | 118.6344 | 349.0418 | 144.4819
527.3479 | 118.8867 | 349.8889 | 144.9588
528.3479 | 119.0966 | 350.0414 | 145.4601
529.3479 | 119.1273 | 350.3847 | 145.7547
530.3479 | 119.6675 | 350.9733 | 146.257
531.3479 | 120.2005 | 351.0754 | 146.6902
532.3479 | 120.3092 | 351.4645 | 147.0641
533.3479 | 120.2812 | 351.6479 | 147.577
534.3479 | 120.4918 | 351.9553 | 148.0563
535.3479 | 120.8703 | 352.5691 | 148.4076
536.3479 | 121.6918 | 353.3479 | 148.9886
537.3479 | 122.3333 | 353.1514 | 149.2331
538.3479 | 122.857 | 353.6074 | 149.6416
539.3479 | 123.2778 | 354.1182 | 150.1334
540.3479 | 123.0194 | 354.6443 | 150.6652
541.3479 | 123.1668 | 354.5501 | 150.8998
542.3479 | 123.5209 | 354.8494 | 151.3803
543.3479 | 124.2462 | 355.4833 | 152.0161
544.3479 | 124.3999 | 355.531 | 152.1791
545.3479 | 124.3838 | 355.7614 | 152.7358
546.3479 | 124.3655 | 356.3557 | 153.0078
547.3479 | 124.9 | 356.8538 | 153.4513
548.3479 | 125.4466 | 357.3225 | 154.1042
549.3479 | 126.2511 | 358.1308 | 154.7145
550.3479 | 126.5947 | 358.0273 | 154.9279
551.3479 | 126.5537 | 358.2563 | 155.1931
552.3479 | 126.7186 | 359.1888 | 155.8756
553.3479 | 127.1515 | 359.3962 | 156.0809
554.3479 | 128.0199 | 359.6532 | 156.3193
555.3479 | 128.1432 | 359.9462 | 156.9427
556.3479 | 127.9365 | 360.4001 | 157.2249
557.3479 | 128.2141 | 360.7346 | 157.9306
558.3479 | 128.5704 | 360.8872 | 158.4303
559.3479 | 128.8312 | 361.3848 | 159.2004
560.3479 | 129.4634 | 362.1572 | 159.4204
561.3479 | 130.0283 | 362.3865 | 160.0177
562.3479 | 131.1527 | 362.9858 | 160.2767
563.3479 | 131.3158 | 362.7961 | 160.7252
564.3479 | 131.2643 | 363.3204 | 161.2718
565.3479 | 131.7906 | 364.3608 | 161.9716
566.3635 | 132.5446 | 365.1158 | 162.2426
567.3479 | 133.6509 | 364.9651 | 162.5542
568.3479 | 134.0461 | 365.4733 | 162.9416
569.3479 | 133.9189 | 366.023 | 163.9241
570.3479 | 134.0937 | 366.8693 | 164.1533
571.3479 | 134.5007 | 367.0805 | 164.6793
572.3479 | 134.3017 | 367.2373 | 164.7502
573.3479 | 134.8521 | 367.9999 | 165.4941
574.3479 | 135.4486 | 368.7668 | 166.0908
575.3479 | 135.4437 | 369.7815 | 166.7488
576.3479 | 136.4271 | 370.5064 | 166.7407
577.3479 | 136.822 | 370.5234 | 166.9074
578.3479 | 136.6173 | 370.6754 | 167.7973
579.3479 | 136.7986 | 371.2873 | 168.252
580.3479 | 137.6132 | 371.507 | 169.3856
581.3479 | 137.7347 | 371.8325 | 169.4451
582.3479 | 137.5521 | 372.0945 | 169.6261
583.3479 | 137.9336 | 372.9276 | 170.3723
584.3479 | 138.3673 | 373.3059 | 170.9007
585.3479 | 139.0796 | 373.01 | 171.2076
586.3479 | 139.0775 | 373.5729 | 171.7393
587.3479 | 139.4049 | 373.9155 | 172.0835
588.3479 | 139.5889 | 374.3522 | 172.583
589.3479 | 140.2378 | 374.8295 | 173.4171
590.3479 | 140.7733 | 374.9953 | 173.7535
591.3479 | 141.2666 | 375.1119 | 174.3594
592.3479 | 141.4539 | 375.4005 | 174.7773
593.3479 | 141.7645 | 375.9787 | 175.2037
594.3479 | 142.2198 | 376.3132 | 175.5251
595.3479 | 142.2783 | 376.8392 | 175.9362
596.3635 | 142.5668 | 377.0875 | 176.5318
597.3479 | 143.0446 | 377.8667 | 177.0247
598.3479 | 143.372 | 377.7799 | 177.9109
599.3479 | 143.6333 | 378.0301 | 177.9626
600.3479 | 143.8822 | 378.7186 | 178.4833
601.3479 | 144.3474 | 379.2261 | 179.0213
602.3479 | 144.637 | 379.6669 | 179.3924
603.3479 | 144.7941 | 379.8939 | 179.9776
604.3479 | 145.145 | 379.7358 | 180.4797
605.3479 | 145.825 | 380.6701 | 180.8401
606.3479 | 146.2201 | 380.984 | 181.4888
607.3479 | 146.5199 | 381.0723 | 181.8215
608.3479 | 146.8555 | 381.4106 | 182.2782
609.3479 | 147.0215 | 382.008 | 182.4785
610.3479 | 147.4641 | 382.4527 | 183.0585
611.3479 | 148.0176 | 382.2962 | 183.5885
612.3479 | 148.1372 | 382.7684 | 184.0635
613.3479 | 148.1264 | 383.1284 | 184.5121
614.3479 | 148.4916 | 383.7258 | 185.1976
615.3479 | 148.9029 | 383.9304 | 185.6308
616.3479 | 149.6819 | 384.0305 | 186.039
617.3479 | 149.8907 | 384.3466 | 186.5164
618.3479 | 150.6921 | 384.4556 | 186.7397
619.3479 | 150.7873 | 385.1808 | 187.3419
620.3479 | 150.6688 | 385.4023 | 187.9562
621.3479 | 150.9257 | 385.8666 | 188.5201
622.3479 | 151.2877 | 386.1527 | 188.8483
623.3479 | 151.6599 | 386.0568 | 189.2566
624.3479 | 151.9402 | 386.5725 | 189.5915
625.3479 | 152.2501 | 387.7595 | 190.0575
626.3479 | 152.9833 | 387.7008 | 190.8755
627.3479 | 153.1851 | 388.0287 | 191.1509
628.3479 | 153.0906 | 387.6108 | 191.3427
629.3479 | 153.4744 | 388.1645 | 191.6868
630.3479 | 154.1762 | 388.7495 | 192.2445
631.3479 | 154.5416 | 388.8955 | 192.9551
632.3479 | 154.6562 | 389.7484 | 193.2818
633.3479 | 154.7072 | 389.7645 | 193.4458
634.3479 | 155.0905 | 390.4176 | 194.4859
635.3479 | 155.5669 | 390.5459 | 194.8787
636.3479 | 155.6881 | 390.6547 | 195.2077
637.3479 | 155.948 | 390.6162 | 195.6673
638.3479 | 156.2687 | 391.1956 | 196.3318
639.3479 | 157.1443 | 391.8337 | 196.6385
640.3479 | 157.8059 | 391.9872 | 197.4509
641.3479 | 158.5041 | 392.1555 | 197.8735
642.3479 | 158.5134 | 392.6971 | 197.9785
643.3479 | 159.6818 | 393.0473 | 198.5814
644.3479 | 159.6344 | 393.1241 | 199.2434
645.3479 | 159.5406 | 393.3334 | 199.6105
646.3479 | 159.3405 | 393.5193 | 199.7909
647.3479 | 159.345 | 393.8106 | 200.1694
648.3479 | 159.591 | 394.1437 | 200.7742
649.3479 | 159.9207 | 394.4551 | 201.1259
650.3479 | 160.255 | 394.5784 | 201.5756
651.3479 | 160.804 | 394.8858 | 202.1066
652.3479 | 161.1273 | 395.1485 | 202.3755
653.3479 | 161.3557 | 395.2649 | 203.0015
654.3479 | 161.5171 | 395.4342 | 203.2279
655.3479 | 162.2933 | 395.6944 | 203.6952
656.3479 | 162.1416 | 396.1802 | 204.2227
657.3479 | 162.4077 | 396.3672 | 204.7221
658.3479 | 162.6551 | 396.616 | 205.0893
659.3479 | 163.1109 | 396.687 | 205.7224
660.3479 | 163.3286 | 396.885 | 206.0711
661.3479 | 163.8557 | 396.8678 | 206.5556
662.3479 | 163.9922 | 397.6968 | 207.4501
663.3479 | 164.3689 | 397.8744 | 207.6833
664.3479 | 164.8967 | 398.4357 | 208.317
665.3479 | 165.464 | 398.2402 | 208.4992
666.3479 | 165.544 | 398.2064 | 208.7566
667.3479 | 165.7281 | 399.0136 | 209.6994
668.3479 | 166.0584 | 399.2367 | 209.7088
669.3479 | 166.2807 | 399.3335 | 210.2375
670.3479 | 166.7146 | 399.9879 | 211.0191
671.3479 | 168.0871 | 399.9921 | 211.4809
672.3479 | 167.7712 | 400.0933 | 211.8517
673.3479 | 167.5068 | 400.3088 | 212.1824
674.3479 | 167.9123 | 400.5154 | 212.576
675.3479 | 168.6857 | 400.8061 | 212.7179
676.3479 | 168.5289 | 400.9998 | 213.08
677.3479 | 168.8171 | 401.1726 | 213.3526
678.3479 | 169.2182 | 401.1709 | 214.0263
679.3479 | 169.4782 | 401.5396 | 214.2043
680.3479 | 170.1517 | 401.7186 | 214.9751
681.3479 | 169.9052 | 401.8157 | 215.066
682.3479 | 170.0486 | 401.7719 | 215.6169
683.3479 | 170.3245 | 402.2496 | 216.24
684.3479 | 170.5646 | 402.6778 | 216.644
685.3479 | 170.7795 | 402.8354 | 217.1611
686.3479 | 171.1013 | 403.1947 | 217.4541
687.3479 | 171.2619 | 403.1533 | 218.1551
688.3479 | 171.7602 | 403.2401 | 218.1906
689.3479 | 171.9872 | 403.366 | 218.5636
690.3479 | 172.4378 | 403.3706 | 218.7961
691.3479 | 173.0889 | 403.394 | 219.2281
692.3479 | 173.7167 | 403.6485 | 219.7507
693.3479 | 173.464 | 403.8843 | 220.1677
694.3479 | 173.6968 | 403.8184 | 220.2599
695.3479 | 173.8105 | 404.2688 | 220.8199
696.3479 | 173.9228 | 404.5095 | 221.3421
697.3479 | 174.2949 | 404.7602 | 221.6808
698.3479 | 174.3901 | 405.0215 | 222.1313
699.3479 | 175.1109 | 404.8337 | 222.5419
700.3479 | 175.4436 | 405.143 | 222.9237
701.3479 | 175.4721 | 405.5979 | 223.6607
702.3479 | 175.6398 | 405.609 | 223.9367
703.3479 | 176.2206 | 405.7343 | 224.2569
704.3479 | 176.2489 | 405.8539 | 224.6254
705.3479 | 176.5007 | 406.0716 | 225.0154
706.3479 | 176.8577 | 406.1099 | 225.8644
707.3479 | 177.4007 | 406.5918 | 225.9931
708.3479 | 177.8001 | 406.6774 | 226.4315
709.3479 | 178.0846 | 406.8712 | 226.6579
710.3479 | 178.628 | 406.7993 | 227.0764
711.3479 | 178.6105 | 406.9141 | 227.7417
712.3479 | 178.7838 | 407.122 | 227.9242
713.3479 | 178.7823 | 407.6193 | 228.1708
714.3479 | 179.0231 | 407.7541 | 228.7568
715.3479 | 179.5396 | 407.7574 | 229.363
716.3479 | 180.1516 | 407.6572 | 229.4564
717.3479 | 180.5723 | 408.119 | 229.725
718.3479 | 180.9359 | 408.1033 | 230.1871
719.3479 | 181.1066 | 408.4204 | 230.5479
720.3479 | 181.1998 | 408.8218 | 231.3842
721.3479 | 181.5709 | 408.946 | 231.6403
722.3479 | 181.7927 | 409.1654 | 232.0403
723.3479 | 182.023 | 409.4159 | 232.2864
724.3479 | 182.5817 | 409.5663 | 232.7111
725.3479 | 183.4961 | 409.4532 | 233.1044
726.3479 | 183.8146 | 410.2488 | 233.3836
727.3479 | 183.9817 | 409.8744 | 233.7297
728.3479 | 183.9766 | 410.0232 | 234.1339
729.3479 | 184.3085 | 410.4735 | 234.6533
730.3479 | 184.8834 | 410.5702 | 235.4065
731.3479 | 184.9389 | 410.378 | 235.5042
732.3479 | 185.2865 | 411.0775 | 235.7087
733.3479 | 185.8623 | 410.5946 | 236.217
734.3479 | 186.4266 | 410.8904 | 236.6576
735.3479 | 186.6239 | 411.1655 | 236.9055
736.3479 | 186.862 | 411.3491 | 237.1459
737.3479 | 186.9756 | 411.8883 | 237.7372
738.3479 | 187.0825 | 412.0489 | 237.8997
739.3479 | 187.3829 | 412.5516 | 238.3751
740.3479 | 187.7381 | 412.5793 | 238.6971
741.3479 | 187.9319 | 412.4013 | 238.9692
742.3479 | 188.2571 | 412.8743 | 239.7372
743.3479 | 188.9181 | 413.8402 | 240.2698
744.3479 | 189.1596 | 413.2471 | 240.1794
745.3479 | 189.1168 | 413.0683 | 240.7307
746.3479 | 189.4343 | 413.3687 | 241.1941
747.3479 | 189.9057 | 413.9053 | 241.5846
748.3479 | 190.4861 | 413.7266 | 241.7372
749.3479 | 190.8565 | 414.1721 | 242.3036
750.3479 | 191.0496 | 414.721 | 242.7737
751.3479 | 191.0367 | 414.4309 | 243.1024
752.3479 | 191.0878 | 414.6677 | 243.396
753.3479 | 191.471 | 414.6612 | 243.8246
754.3479 | 192.0049 | 415.0892 | 244.2246
755.3479 | 192.6473 | 416.1966 | 245.1746
756.3479 | 192.779 | 416.3411 | 245.3794
757.3479 | 193.4553 | 416.1136 | 245.5546
758.3479 | 193.6855 | 416.0327 | 245.7922
759.3479 | 193.7898 | 416.3457 | 246.2477
760.3479 | 193.9281 | 416.1865 | 246.5951
761.3479 | 194.4329 | 416.1127 | 247.0838
762.3479 | 195.0731 | 416.3893 | 247.494
763.3479 | 195.4969 | 416.5612 | 247.6297
764.3479 | 195.7586 | 416.9904 | 248.0383
765.3479 | 196.2737 | 417.5198 | 248.5906
766.3479 | 195.9026 | 416.8372 | 248.7125
767.3479 | 196.0608 | 416.9371 | 249.1466
768.3479 | 196.5085 | 417.3546 | 249.6474
769.3479 | 196.7148 | 417.546 | 250.0056
770.3479 | 196.943 | 417.722 | 250.2165
771.3479 | 197.7971 | 418.157 | 250.8784
772.3479 | 198.1694 | 418.056 | 251.1658
773.3479 | 198.5454 | 417.9235 | 251.6204
774.3479 | 198.7146 | 418.2369 | 251.8556
775.3479 | 199.3535 | 418.3386 | 252.2101
776.3479 | 199.1804 | 418.5315 | 252.7271
777.3479 | 199.8423 | 418.5539 | 253.2223
778.3479 | 200.1757 | 419.1031 | 253.7279
779.3479 | 200.3334 | 418.9877 | 253.9848
780.3479 | 200.52 | 419.0135 | 254.1582
781.3479 | 200.8396 | 418.9768 | 254.6333
782.3479 | 201.0441 | 419.1883 | 254.9559
783.3479 | 201.35 | 419.3312 | 255.3088
784.3479 | 201.3087 | 419.5056 | 255.642
785.3479 | 201.4649 | 419.4789 | 256.2036
786.3479 | 201.774 | 419.8014 | 256.5604
787.3479 | 202.1575 | 420.0221 | 257.076
788.3479 | 202.8001 | 420.1554 | 257.2768
789.3479 | 203.2535 | 420.3452 | 257.7183
790.3479 | 203.5452 | 420.6536 | 257.8972
791.3479 | 203.8484 | 420.571 | 258.2188
792.3479 | 204.1189 | 420.6092 | 258.6619
793.3479 | 204.0469 | 420.8909 | 258.9832
794.3479 | 204.4732 | 421.1526 | 259.5191
795.3479 | 204.9115 | 420.9916 | 259.8485
796.3479 | 205.5256 | 421.6059 | 260.2153
797.3479 | 205.6914 | 422.5717 | 260.9742
798.3479 | 205.9864 | 421.6283 | 261.0376
799.3479 | 206.2677 | 421.7528 | 261.1409
800.3479 | 206.664 | 421.7117 | 261.6522
801.3479 | 206.8814 | 422.0796 | 262.185
802.3479 | 207.1852 | 422.9542 | 262.7759
803.3479 | 207.446 | 422.7814 | 262.9584
804.3479 | 207.7609 | 422.7779 | 263.1599
805.3479 | 208.0611 | 422.8025 | 263.5959
806.3479 | 208.3726 | 423.0458 | 264.073
807.3479 | 208.6886 | 423.0624 | 264.3515
808.3479 | 208.9807 | 423.067 | 264.4244
809.3479 | 209.4166 | 423.3191 | 265.0267
810.3479 | 209.5986 | 423.4165 | 265.5222
811.3479 | 209.9853 | 423.2945 | 265.8256
812.3479 | 210.8701 | 423.4715 | 266.3101
813.3479 | 210.8322 | 423.7226 | 266.7351
814.3479 | 211.0305 | 423.951 | 267.0667
815.3479 | 211.1737 | 424.0101 | 267.5291
816.3479 | 211.2453 | 424.2096 | 267.8882
817.3479 | 212.0691 | 424.6628 | 268.0089
818.3479 | 212.6209 | 424.2344 | 268.4113
819.3479 | 212.6107 | 424.5559 | 269.1579
820.3479 | 212.9407 | 425.1606 | 269.4467
821.3479 | 213.7434 | 424.7233 | 269.736
822.3479 | 213.5994 | 424.836 | 269.8786
823.3479 | 213.7062 | 424.9831 | 270.316
824.3479 | 214.291 | 425.1346 | 270.5368
825.3479 | 214.5925 | 425.1021 | 270.9086
826.3479 | 214.5643 | 425.1463 | 271.2876
827.3479 | 214.5859 | 425.3371 | 271.4612
828.3479 | 214.8872 | 425.4681 | 271.9673
829.3479 | 215.1124 | 425.576 | 272.1015
830.3479 | 215.3814 | 425.9485 | 272.7016
831.3479 | 216.0291 | 426.0289 | 273.107
832.3479 | 216.6538 | 426.0772 | 273.1958
833.3479 | 216.6216 | 425.9087 | 273.5534
834.3479 | 216.8998 | 426.2575 | 273.9757
835.3479 | 217.1695 | 426.2945 | 274.3685
836.3479 | 217.406 | 426.4575 | 274.6305
837.3479 | 217.8767 | 426.48 | 274.9813
838.3479 | 218.5018 | 426.9723 | 275.4404
839.3479 | 218.8619 | 426.9539 | 275.7728
840.3479 | 219.314 | 426.6459 | 276.1629
841.3479 | 219.2008 | 427.1002 | 276.7044
842.3479 | 219.4738 | 427.0487 | 276.8884
843.3479 | 219.8038 | 427.3007 | 277.2157
844.3479 | 220.1332 | 427.5417 | 277.6513
845.3479 | 220.259 | 427.1932 | 277.8903
846.3479 | 220.7167 | 427.4813 | 278.717
847.3479 | 220.8073 | 427.6487 | 278.8333
848.3479 | 221.4734 | 428.0268 | 278.8893
849.3479 | 221.8695 | 428.3872 | 279.1855
850.3479 | 222.2494 | 428.1261 | 279.5881
851.3479 | 222.3403 | 428.0992 | 279.9474
852.3479 | 222.6 | 428.5 | 280.1926
853.3479 | 223.1948 | 428.9042 | 280.7041
854.3479 | 223.0822 | 429.0396 | 280.8238
855.3479 | 223.2308 | 429.0225 | 281.2087
856.3479 | 223.4928 | 429.0552 | 281.5251
857.3479 | 223.9411 | 429.4216 | 282.0451
858.3479 | 223.9657 | 429.3233 | 282.3504
859.3479 | 224.5273 | 429.4619 | 282.706
860.3479 | 225.5088 | 429.4353 | 282.9045
861.3479 | 225.211 | 429.4997 | 283.2008
862.3479 | 225.7678 | 429.6273 | 283.6788
863.3479 | 225.9718 | 429.4951 | 284.2371
864.3479 | 225.9277 | 429.839 | 284.4747
865.3479 | 226.036 | 429.8938 | 284.5987
866.3479 | 226.4955 | 430.0104 | 285.22
867.3479 | 226.8012 | 430.0753 | 285.5838
868.3479 | 227.3321 | 430.5158 | 285.9839
869.3479 | 227.8068 | 430.541 | 286.4074
870.3479 | 228.315 | 430.3021 | 286.6514
871.3479 | 228.5489 | 430.5812 | 286.8989
872.3479 | 228.7068 | 430.6822 | 287.3525
873.3479 | 228.7982 | 430.8559 | 287.5499
874.3479 | 229.3279 | 430.7074 | 287.9511
875.3635 | 229.6351 | 430.9784 | 288.3255
876.3479 | 229.7565 | 430.8564 | 288.394
877.3479 | 229.8992 | 430.8199 | 288.7013
878.3479 | 230.1717 | 430.8002 | 288.9889
879.3479 | 230.5418 | 430.8603 | 289.3822
880.3479 | 230.9429 | 431.2714 | 290.0985
881.3479 | 231.2896 | 431.1158 | 290.2888
882.3479 | 231.5389 | 431.3742 | 290.3834
883.3479 | 231.8174 | 431.6717 | 291.0739
884.3479 | 231.5901 | 431.5259 | 291.3156
885.3479 | 231.9462 | 431.9436 | 291.8143
886.3479 | 232.1336 | 431.8142 | 291.8511
887.3479 | 232.4091 | 431.7323 | 291.9609
888.3479 | 232.6012 | 431.9263 | 292.6603
889.3479 | 232.8755 | 432.1015 | 292.9308
890.3479 | 233.1781 | 432.1951 | 293.0064
891.3479 | 233.3728 | 432.0916 | 293.1133
892.3479 | 233.4542 | 432.3051 | 293.5718
893.3479 | 234.1188 | 432.218 | 293.9397
894.3479 | 234.5024 | 432.1945 | 294.2763
895.3479 | 234.6072 | 431.9806 | 294.4818
896.3479 | 234.818 | 432.2896 | 294.7693
897.3479 | 235.1331 | 432.3364 | 295.2404
898.3479 | 235.4327 | 432.2344 | 295.512
899.3479 | 235.9493 | 432.6556 | 295.9542
900.3479 | 236.4416 | 432.4369 | 296.0411
901.3479 | 236.9199 | 432.6584 | 296.3123
902.3479 | 236.9216 | 432.8765 | 296.6898
903.3479 | 237.1269 | 433.6291 | 297.3277
904.3479 | 237.9351 | 434.0997 | 297.6676
905.3479 | 238.2445 | 434.3227 | 297.9204
906.3479 | 238.6399 | 434.0585 | 298.1777
907.3479 | 239.331 | 434.3567 | 298.8058
908.3479 | 238.9542 | 433.7536 | 298.6264
909.3479 | 238.8498 | 433.681 | 299.0538
910.3479 | 239.3776 | 433.5451 | 299.3215
911.3479 | 239.4163 | 433.809 | 300.0332
912.3479 | 240.4938 | 434.0548 | 300.0616
913.3479 | 240.6783 | 433.9662 | 300.2433
914.3479 | 241.3244 | 434.2376 | 300.7295
915.3479 | 241.9352 | 434.1165 | 301.1053
916.3479 | 241.8617 | 435.4006 | 301.617
917.3479 | 242.055 | 434.5881 | 301.5203
918.3479 | 242.4212 | 434.5448 | 301.9221
919.3479 | 242.5771 | 434.5493 | 302.32
920.3479 | 242.3896 | 435.0318 | 302.7743
921.3479 | 242.9587 | 435.0544 | 303.0565
922.3479 | 243.5259 | 435.2645 | 303.5356
923.3479 | 243.7364 | 435.218 | 303.6028
924.3479 | 244.2116 | 435.2281 | 303.9316
925.3479 | 244.5128 | 435.4082 | 304.4839
926.3479 | 244.667 | 435.5048 | 304.7833
927.3479 | 244.5688 | 435.2575 | 304.8171
928.3479 | 244.6025 | 435.3856 | 305.0644
929.3479 | 244.8982 | 435.8375 | 305.4782
930.3479 | 245.3319 | 435.6674 | 305.6659
931.3479 | 245.6918 | 435.5318 | 306.1749
932.3479 | 246.1308 | 435.7232 | 306.4821
933.3479 | 246.5609 | 435.686 | 306.8013
934.3479 | 246.8396 | 435.7313 | 306.9975
935.3479 | 246.88 | 435.7158 | 307.3537
936.3479 | 247.0942 | 435.8633 | 307.662
937.3479 | 247.4801 | 436.2821 | 308.2102
938.3479 | 247.7285 | 436.5503 | 308.3403
939.3479 | 247.8335 | 436.7308 | 308.7896
940.3479 | 248.5452 | 437.3188 | 309.1135
941.3479 | 249.1263 | 437.3194 | 309.49
942.3479 | 249.2775 | 437.5111 | 309.915
943.3479 | 249.7475 | 436.977 | 310.2594
944.3479 | 249.9363 | 437.3428 | 310.7564
945.3479 | 250.3415 | 436.9778 | 310.7059
946.3479 | 250.3263 | 437.0902 | 311.0803
947.3479 | 250.3355 | 436.995 | 311.4951
948.3479 | 250.3539 | 436.9602 | 311.6917
949.3479 | 250.4853 | 437.4355 | 312.117
950.3479 | 250.8454 | 437.2035 | 312.8197
951.3479 | 251.212 | 437.2673 | 312.6812
952.3479 | 251.8496 | 438.1034 | 313.3801
953.3479 | 252.5124 | 438.3467 | 313.8001
954.3479 | 252.4107 | 437.8564 | 313.7518
955.3479 | 252.6544 | 437.8766 | 314.1684
956.3479 | 252.804 | 438.14 | 314.6803
957.3479 | 253.4988 | 438.0774 | 314.8259
958.3479 | 253.682 | 438.3067 | 315.282
959.3479 | 253.6964 | 438.3081 | 315.7851
960.3479 | 254.4271 | 438.6929 | 316.1304
961.3479 | 255.1127 | 438.6306 | 316.3026
962.3479 | 255.4266 | 439.2171 | 316.4121
963.3479 | 255.8837 | 438.7109 | 316.9117
964.3479 | 256.4096 | 438.9613 | 317.3965
965.3479 | 255.8386 | 438.51 | 317.5225
966.3479 | 256.0178 | 438.5672 | 317.6981
967.3479 | 256.1431 | 438.6486 | 318.1257
968.3479 | 256.5545 | 438.6933 | 318.1683
969.3479 | 257.0157 | 438.6281 | 318.5611
970.3479 | 256.9047 | 438.8486 | 318.8107
971.3479 | 256.8716 | 439.1509 | 319.3909
972.3479 | 257.0811 | 439.5025 | 319.5837
973.3479 | 257.6322 | 439.5556 | 319.8826
974.3479 | 257.8435 | 439.7138 | 320.2848
975.3479 | 258.163 | 439.8976 | 320.8059
976.3479 | 258.8587 | 439.6856 | 321.2564
977.3479 | 258.8615 | 439.7577 | 321.1742
978.3479 | 259.4734 | 439.7383 | 321.6421
979.3479 | 259.5363 | 439.8408 | 321.9208
980.3479 | 259.3513 | 440.1607 | 321.9489
981.3479 | 259.6985 | 441.5643 | 322.5251
982.3479 | 259.9663 | 442.1062 | 322.6394
983.3479 | 260.4722 | 442.2728 | 323.1632
984.3479 | 261.1588 | 441.8314 | 323.4998
985.3479 | 261.2433 | 442.5268 | 324.2476
986.3479 | 261.683 | 442.897 | 324.6922
987.3479 | 261.81 | 443.6223 | 324.6721
988.3479 | 262.1088 | 443.6176 | 324.954
989.3479 | 262.5562 | 443.89 | 325.3972
990.3479 | 263.5051 | 444.0344 | 325.6963
991.3479 | 263.7215 | 443.4608 | 325.7745
992.3479 | 264.0426 | 443.4153 | 326.0814
993.3479 | 264.2366 | 443.4585 | 326.4031
994.3479 | 264.0647 | 443.5375 | 326.7627
995.3479 | 264.2217 | 443.3677 | 326.7439
996.3479 | 264.4124 | 443.884 | 327.3153
997.3479 | 264.5891 | 443.5776 | 327.6037
998.3479 | 264.7458 | 443.4957 | 327.836
999.3479 | 265.0155 | 443.6259 | 328.2138
1000.3479 | 265.1923 | 443.5452 | 328.3867
1001.3479 | 265.5369 | 444.0494 | 328.8787
1002.3479 | 265.7728 | 443.613 | 329.1028
1003.3479 | 265.8087 | 443.6768 | 329.2743
1004.3479 | 265.8243 | 443.6802 | 329.6015
1005.3479 | 266.0806 | 443.7511 | 330.0094
1006.3479 | 266.7538 | 443.6582 | 330.3391
1007.3479 | 267.0552 | 443.75 | 330.9938
1008.3479 | 267.2217 | 443.7714 | 330.6855
1009.3479 | 267.3539 | 443.8695 | 331.1414
1010.3479 | 268.0394 | 443.8415 | 331.3913
1011.3479 | 268.4331 | 443.8992 | 332.1256
1012.3479 | 268.9588 | 444.2389 | 332.5804
1013.3479 | 269.1713 | 444.1095 | 332.4575
1014.3479 | 269.0778 | 444.1745 | 332.9785
1015.3479 | 269.4869 | 444.5537 | 333.3531
1016.3479 | 269.5832 | 444.9627 | 333.5537
1017.3479 | 269.6228 | 444.5743 | 333.8889
1018.3479 | 269.9694 | 444.4535 | 334.3672
1019.3479 | 269.9741 | 444.4931 | 334.8965
1020.3479 | 270.46 | 444.7006 | 335.3994
1021.3479 | 270.6517 | 444.6687 | 335.375
1022.3479 | 270.7499 | 444.9995 | 336.3127
1023.3479 | 271.1141 | 444.7936 | 336.283
1024.3479 | 271.3191 | 445.4593 | 336.725
1025.3479 | 271.8235 | 445.3148 | 337.1438
1026.3479 | 272.4545 | 445.4943 | 337.3133
1027.3479 | 272.3396 | 445.7495 | 337.896
1028.3479 | 272.9261 | 445.5189 | 338.1107
1029.3479 | 273.1454 | 445.6571 | 338.4465
1030.3479 | 272.9987 | 445.5055 | 338.3592
1031.3479 | 273.3223 | 445.4594 | 338.7642
1032.3479 | 273.6458 | 445.7255 | 338.9352
1033.3479 | 273.7791 | 445.6227 | 339.3339
1034.3479 | 273.9294 | 445.6964 | 339.4959
1035.3479 | 274.2473 | 445.5578 | 339.8958
1036.3479 | 274.5637 | 446.0292 | 340.3514
1037.3479 | 274.9444 | 445.6882 | 340.2779
1038.3479 | 274.9931 | 446.003 | 341.403
1039.3479 | 275.4502 | 446.0906 | 341.2471
1040.3479 | 276.154 | 445.8535 | 341.6076
1041.3479 | 276.276 | 446.4084 | 342.0038
1042.3479 | 276.9673 | 446.0589 | 341.9098
1043.3479 | 277.2738 | 446.1595 | 342.3919
1044.3479 | 277.3918 | 446.1651 | 343.233
1045.3479 | 277.2019 | 446.1943 | 343.2815
1046.3479 | 277.7263 | 446.2527 | 343.3989
1047.3479 | 277.6925 | 446.098 | 344.0641
1048.3479 | 278.2257 | 446.9006 | 344.3186
1049.3479 | 279.2012 | 446.9673 | 344.4937
1050.3479 | 279.3823 | 446.9046 | 344.68
1051.3479 | 279.8704 | 447.4027 | 344.9366
1052.3479 | 279.5686 | 446.6192 | 345.184
1053.3479 | 280.0456 | 446.7685 | 345.4984
1054.3479 | 280.1816 | 446.5221 | 345.9903
1055.3479 | 280.0611 | 446.4258 | 346.2181
1056.3479 | 280.1846 | 446.7947 | 346.5067
1057.3479 | 280.6687 | 446.8697 | 346.9292
1058.3479 | 280.9415 | 447.0164 | 347.2657
1059.3479 | 281.4882 | 447.0794 | 347.5198
1060.3479 | 282.3587 | 447.1736 | 347.7236
1061.3479 | 282.6828 | 446.8185 | 347.9349
1062.3479 | 282.4156 | 446.8547 | 348.2476
1063.3479 | 282.4306 | 447.0613 | 348.5667
1064.3479 | 282.7476 | 447.3319 | 349.0592
1065.3479 | 283.1399 | 447.8919 | 349.3445
1066.3479 | 283.6307 | 448.7348 | 349.7755
1067.3479 | 283.8259 | 447.8598 | 349.7862
1068.3479 | 284.332 | 448.0134 | 350.0624
1069.3479 | 284.3829 | 448.0396 | 350.3723
1070.3479 | 284.6764 | 447.5902 | 350.6613
1071.3479 | 285.0604 | 447.9661 | 351.1
1072.3479 | 285.1125 | 447.9392 | 351.0659
1073.3479 | 285.5304 | 448.1102 | 351.5395
1074.3479 | 285.5738 | 447.7643 | 351.6482
1075.3479 | 285.8792 | 447.8464 | 352.2839
1076.3479 | 286.1292 | 448.1103 | 352.5363
1077.3479 | 286.2432 | 448.0706 | 352.9023
1078.3479 | 286.3586 | 447.9034 | 353.2326
1079.3479 | 286.5817 | 447.8968 | 353.8394
1080.3479 | 286.8247 | 448.2309 | 353.9796
1081.3479 | 287.6283 | 448.3145 | 354.1804
1082.3479 | 287.949 | 448.0582 | 354.3972
1083.3479 | 287.9245 | 448.2583 | 354.6927
1084.3479 | 288.29 | 448.1433 | 354.7776
1085.3479 | 288.3294 | 448.0923 | 354.8963
1086.3479 | 288.7091 | 448.0324 | 355.4491
1087.3479 | 288.8571 | 448.0159 | 356.037
1088.3479 | 289.1899 | 448.2179 | 355.8981
1089.3479 | 289.5502 | 448.2737 | 356.0333
1090.3479 | 289.9202 | 448.3604 | 356.7411
1091.3479 | 290.4765 | 448.5706 | 356.9659
1092.3479 | 290.6576 | 448.3512 | 357.1783
1093.3479 | 290.8451 | 448.3199 | 357.3811
1094.3479 | 291.0618 | 448.2431 | 357.6703
1095.3479 | 291.0745 | 448.4708 | 358.1657
1096.3479 | 291.5283 | 448.4493 | 358.1624
1097.3479 | 291.6952 | 448.509 | 358.5532
1098.3479 | 291.5783 | 448.4696 | 359.211
1099.3479 | 291.7949 | 448.7745 | 359.5523
1100.3479 | 292.0844 | 449.2571 | 360.0623
1101.3479 | 292.5519 | 448.9205 | 360.2598
1102.3479 | 292.8782 | 448.9198 | 360.296
1103.3479 | 292.9632 | 448.9708 | 360.6873
1104.3479 | 292.9582 | 449.2347 | 360.8881
1105.3479 | 293.1068 | 448.9627 | 361.0221
1106.3479 | 293.2579 | 448.7939 | 361.2277
1107.3479 | 293.2158 | 449.1081 | 361.5781
1108.3479 | 293.413 | 449.2237 | 361.952
1109.3479 | 293.8582 | 449.1577 | 362.294
1110.3479 | 294.3258 | 449.342 | 362.6704
1111.3479 | 294.4772 | 449.1937 | 362.6696
1112.3479 | 294.8222 | 449.3399 | 363.2062
1113.3479 | 294.9027 | 449.4949 | 363.3954
1114.3479 | 295.0965 | 449.4833 | 363.7468
1115.3479 | 295.3437 | 449.418 | 364.2175
1116.3479 | 295.5787 | 449.3948 | 364.1964
1117.3479 | 295.7265 | 449.6087 | 364.4847
1118.3479 | 296.4371 | 449.9423 | 365.1893
1119.3479 | 296.7574 | 449.9738 | 365.4225
1120.3479 | 296.8636 | 449.8973 | 365.2771
1121.3479 | 296.9947 | 449.621 | 365.695
1122.3479 | 297.3057 | 449.679 | 365.8838
1123.3479 | 297.9712 | 450.0374 | 366.4196
1124.3479 | 298.06 | 450.0825 | 366.6698
1125.3479 | 298.2174 | 449.9062 | 367.3231
1126.3479 | 298.5551 | 450.0231 | 367.2973
1127.3479 | 298.6876 | 450.2126 | 367.5599
1128.3479 | 299.1627 | 450.784 | 367.9235
1129.3479 | 300.0875 | 450.4958 | 368.0035
1130.3479 | 300.2381 | 450.5358 | 368.4021
1131.3479 | 300.0683 | 450.5422 | 368.3264
1132.3479 | 300.0641 | 450.5071 | 368.8527
1133.3479 | 300.9674 | 453.1389 | 369.432
1134.3479 | 301.2932 | 452.1649 | 369.8863
1135.3479 | 301.5055 | 452.7753 | 370.2995
1136.3479 | 301.9004 | 453.2002 | 370.3619
1137.3479 | 302.7036 | 453.5405 | 370.8554
1138.3479 | 302.8394 | 452.9992 | 371.3175
1139.3479 | 302.6531 | 453.7394 | 371.8994
1140.3479 | 303.1526 | 453.6916 | 372.4266
1141.3479 | 303.5549 | 453.1604 | 372.2874
1142.3479 | 304.0554 | 453.2811 | 372.2172
1143.3479 | 304.0771 | 453.1887 | 372.1994
1144.3479 | 304.8292 | 453.856 | 372.9378
1145.3479 | 304.5787 | 453.6855 | 373.7249
1146.3479 | 304.6699 | 453.6679 | 373.4015
1147.3479 | 304.9848 | 453.8518 | 373.5506
1148.3479 | 305.1105 | 454.1125 | 374.5596
1149.3479 | 305.6413 | 454.1281 | 374.4533
1150.3479 | 305.8208 | 454.4336 | 374.7884
1151.3479 | 306.6794 | 455.5753 | 375.1221
1152.3479 | 307.2541 | 455.0578 | 375.6159
1153.3479 | 307.1366 | 454.4827 | 375.5953
1154.3479 | 307.3959 | 454.8713 | 376.0375
1155.3479 | 307.4708 | 455.1235 | 376.3177
1156.3479 | 307.8417 | 455.1242 | 376.295
1157.3479 | 307.8048 | 454.8311 | 376.5691
1158.3479 | 308.3711 | 455.1538 | 376.8465
1159.3479 | 309.0763 | 455.225 | 377.1749
1160.3479 | 309.5912 | 455.0628 | 378.0702
1161.3479 | 310.2287 | 455.6666 | 378.3545
1162.3479 | 310.3549 | 455.7928 | 378.4716
1163.3479 | 310.4457 | 455.5515 | 378.3963
1164.3479 | 310.6777 | 455.7609 | 378.5627
1165.3479 | 310.9767 | 455.9645 | 379.1076
1166.3479 | 311.5792 | 455.733 | 379.7817
1167.3479 | 311.9017 | 456.1939 | 380.0655
1168.3479 | 312.4275 | 456.4256 | 379.9108
1169.3479 | 312.4332 | 456.6564 | 380.3742
1170.3479 | 312.9357 | 456.7196 | 380.7894
1171.3479 | 313.296 | 456.5134 | 381.2782
1172.3479 | 313.924 | 456.9802 | 381.3194
1173.3479 | 313.8549 | 457.2851 | 381.9369
1174.3479 | 314.3213 | 457.2312 | 382.3747
1175.3479 | 314.5226 | 457.1557 | 382.1446
1176.3479 | 315.2837 | 457.0944 | 382.2361
1177.3479 | 315.5045 | 457.3546 | 382.4571
1178.3479 | 315.8168 | 457.4128 | 382.75
1179.3479 | 316.1087 | 457.9279 | 383.3622
1180.3479 | 316.054 | 457.3336 | 383.3068
1181.3479 | 316.1125 | 457.4562 | 383.8121
1182.3479 | 316.8122 | 457.7758 | 384.1132
1183.3479 | 317.0967 | 458.18 | 384.2101
1184.3479 | 317.4283 | 458.1662 | 384.5157
1185.3479 | 317.8264 | 458.2203 | 384.6872
1186.3479 | 317.8905 | 458.3078 | 385.0589
1187.3479 | 317.8386 | 458.3438 | 385.1716
1188.3479 | 318.3227 | 458.4207 | 385.4004
1189.3479 | 318.8316 | 458.497 | 385.4671
1190.3479 | 319.145 | 458.3449 | 385.783
1191.3479 | 319.0976 | 458.263 | 385.7511
1192.3479 | 319.4639 | 458.3915 | 386.4758
1193.3479 | 319.9318 | 458.826 | 387.0676
1194.3479 | 320.1865 | 458.9449 | 387.663
1195.3479 | 320.5046 | 459.4121 | 387.6316
1196.3479 | 321.6728 | 459.7971 | 387.8482
1197.3479 | 322.0902 | 459.3079 | 388.2422
1198.3479 | 322.0843 | 459.1556 | 388.3206
1199.3479 | 321.8769 | 459.3141 | 388.6544
1200.3479 | 321.8811 | 460.1178 | 389.0509
1201.3479 | 322.0242 | 459.772 | 389.1106
1202.3479 | 322.2946 | 460.0583 | 389.606
1203.3479 | 323.239 | 460.589 | 389.5759
1204.3479 | 323.8171 | 460.2008 | 389.946
1205.3479 | 323.6963 | 460.187 | 390.3023
1206.3479 | 324.2784 | 460.0475 | 390.385
1207.3479 | 324.5086 | 460.726 | 390.822
1208.3479 | 325.0472 | 460.743 | 391.2555
1209.3479 | 325.6317 | 461.2371 | 391.3869
1210.3479 | 325.8695 | 461.8626 | 391.7392
1211.3479 | 326.3768 | 461.462 | 391.7413
1212.3479 | 326.7944 | 461.4132 | 391.9517
1213.3479 | 326.8844 | 461.58 | 391.8709
1214.3479 | 327.1022 | 461.606 | 392.1939
1215.3479 | 327.7309 | 461.6705 | 392.3765
1216.3479 | 328.2329 | 461.4372 | 392.5668
1217.3479 | 328.3434 | 461.6347 | 393.1869
1218.3479 | 328.4682 | 461.4813 | 392.9492
1219.3479 | 328.8736 | 461.9104 | 393.2094
1220.3479 | 329.1578 | 461.8224 | 393.489
1221.3479 | 329.7593 | 461.6477 | 393.615
1222.3479 | 329.4217 | 462.0725 | 393.6585
1223.3479 | 329.7811 | 462.1205 | 394.0304
1224.3479 | 329.8842 | 461.9992 | 394.29
1225.3479 | 330.3399 | 462.169 | 394.3942
1226.3479 | 330.6799 | 462.1558 | 394.6775
1227.3479 | 331.3953 | 462.0541 | 394.7066
1228.3479 | 331.8944 | 462.1834 | 395.0841
1229.3479 | 332.2917 | 462.2479 | 395.3588
1230.3479 | 332.2091 | 462.4822 | 395.5673
1231.3479 | 332.4885 | 462.4931 | 395.5778
1232.3479 | 333.5977 | 462.3331 | 395.634
1233.3479 | 333.3469 | 462.4215 | 395.966
1234.3479 | 333.8791 | 462.629 | 396.2928
1235.3479 | 334.536 | 463.2532 | 396.4667
1236.3479 | 335.1293 | 463.2352 | 396.8376
1237.3479 | 335.4718 | 462.9422 | 396.9941
1238.3479 | 335.0733 | 463.1516 | 397.3525
1239.3479 | 335.8385 | 463.3425 | 397.6264
1240.3479 | 335.7924 | 463.6617 | 397.9653
1241.3479 | 335.8389 | 463.5804 | 398.1085
1242.3479 | 336.8591 | 463.4681 | 398.5901
1243.3479 | 338.3234 | 463.3249 | 398.681
1244.3479 | 338.6204 | 463.6146 | 398.6802
1245.3479 | 339.0998 | 463.7472 | 398.7839
1246.3479 | 339.5631 | 463.6384 | 399.0268
1247.3479 | 339.4454 | 463.6845 | 399.3155
1248.3479 | 340.0247 | 464.0106 | 399.5682
1249.3479 | 340.5898 | 463.9437 | 399.8954
1250.3479 | 340.4214 | 464.2046 | 400.1905
1251.3479 | 341.3595 | 464.2205 | 400.1859
1252.3479 | 341.4866 | 464.2501 | 400.3254
1253.3479 | 341.9119 | 464.3938 | 400.5941
1254.3479 | 342.0962 | 464.2602 | 400.7079
1255.3479 | 342.1979 | 464.366 | 400.7841
1256.3479 | 342.2342 | 464.5086 | 401.2472
1257.3479 | 343.1252 | 464.4992 | 401.3836
1258.3479 | 344.0564 | 465.0175 | 401.4522
1259.3479 | 345.18 | 464.5708 | 401.8548
1260.3479 | 345.1895 | 464.77 | 401.8688
1261.3479 | 345.7316 | 464.847 | 402.3365
1262.3479 | 346.4222 | 464.9166 | 402.39
1263.3479 | 346.643 | 465.1679 | 402.7012
1264.3479 | 346.4844 | 465.3558 | 402.7322
1265.3479 | 346.2851 | 465.3855 | 403.4203
1266.3479 | 346.9657 | 465.106 | 403.3004
1267.3479 | 347.7441 | 465.1894 | 403.2449
1268.3479 | 347.54 | 465.343 | 403.5423
1269.3479 | 348.4796 | 465.9804 | 403.7558
1270.3479 | 349.1257 | 465.4264 | 403.8516
1271.3479 | 349.4117 | 465.7682 | 403.9844
1272.3479 | 349.2464 | 465.5325 | 404.2716
1273.3479 | 349.7463 | 465.6672 | 404.6244
1274.3479 | 350.4823 | 465.625 | 405.233
1275.3479 | 351.2445 | 465.8722 | 404.9992
1276.3479 | 350.7478 | 465.8581 | 405.0187
1277.3479 | 351.3406 | 466.0902 | 405.0478
1278.3479 | 351.7041 | 465.9105 | 405.3857
1279.3479 | 352.0867 | 465.9395 | 405.4937
1280.3479 | 352.9535 | 465.92 | 405.701
1281.3479 | 353.7208 | 466.0811 | 406.0688
1282.3479 | 353.5346 | 466.0232 | 406.1491
1283.3479 | 353.5229 | 466.223 | 406.1327
1284.3479 | 353.8492 | 466.4236 | 406.471
1285.3479 | 354.4244 | 466.1591 | 406.5007
1286.3479 | 354.8348 | 466.2144 | 406.7208
1287.3479 | 354.9535 | 466.3472 | 406.9097
1288.3479 | 355.7959 | 466.4533 | 407.0256
1289.3479 | 355.965 | 466.4575 | 407.1409
1290.3479 | 356.4097 | 466.4863 | 407.5207
1291.3479 | 356.7913 | 466.3698 | 407.6997
1292.3479 | 357.0651 | 466.382 | 408.1419
1293.3479 | 358.1287 | 466.4875 | 408.2428
1294.3479 | 359.0253 | 466.5232 | 408.2788
1295.3479 | 359.2721 | 466.5152 | 408.4273
1296.3479 | 359.9311 | 466.5208 | 408.4788
1297.3479 | 360.2387 | 466.5988 | 408.7026
1298.3479 | 359.5952 | 466.4086 | 409.0058
1299.3479 | 359.6762 | 466.4617 | 409.059
1300.3479 | 359.9825 | 466.7009 | 409.3536
1301.3479 | 361.0129 | 466.7411 | 409.6213
1302.3479 | 361.5123 | 466.7237 | 409.7327
1303.3479 | 362.4012 | 467.0389 | 410.1567
1304.3479 | 363.7543 | 467.2836 | 410.0737
1305.3479 | 364.5271 | 467.1597 | 410.0166
1306.3479 | 364.424 | 467.1126 | 410.4067
1307.3479 | 364.0552 | 466.8923 | 410.5944
1308.3479 | 364.0891 | 466.9622 | 410.6122
1309.3479 | 364.5129 | 467.2503 | 410.9969
1310.3479 | 365.864 | 467.2575 | 411.1799
1311.3479 | 365.8205 | 467.2294 | 411.2463
1312.3479 | 367.8478 | 467.3103 | 411.2493
1313.3479 | 367.3282 | 467.3967 | 411.4765
1314.3479 | 366.9424 | 467.7101 | 411.5047
1315.3479 | 367.4098 | 467.6397 | 411.6465
1316.3479 | 368.3248 | 467.8474 | 412.0928
1317.3479 | 369.1185 | 468.236 | 412.5377
1318.3479 | 370.0591 | 469.0127 | 412.5749
1319.3479 | 370.7663 | 469.0015 | 413.0359
1320.3479 | 370.6797 | 469.429 | 413.0325
1321.3479 | 372.3146 | 469.2667 | 413.1435
1322.3479 | 373.0809 | 469.3347 | 413.5572
1323.3479 | 371.836 | 469.4364 | 413.4546
1324.3479 | 371.4605 | 469.6173 | 413.4842
1325.3479 | 371.3918 | 469.645 | 413.5593
1326.3479 | 373.5438 | 470.3531 | 414.0196
1327.3479 | 373.9832 | 469.7162 | 414.0859
1328.3479 | 374.4633 | 470.0684 | 414.1801
1329.3479 | 375.4773 | 470.7055 | 414.1341
1330.3479 | 375.9609 | 470.8054 | 414.2868
1331.3479 | 375.6225 | 470.7531 | 414.4021
1332.3479 | 376.8656 | 470.5783 | 414.775
1333.3479 | 376.2818 | 470.4061 | 414.8034
1334.3479 | 378.3716 | 470.7419 | 415.1909
1335.3479 | 378.6788 | 470.7942 | 415.1396
1336.3479 | 378.0128 | 470.9152 | 415.3078
1337.3479 | 378.1321 | 470.893 | 415.4054
1338.3479 | 378.3621 | 470.8719 | 415.7884
1339.3479 | 379.33 | 471.0085 | 415.9123
1340.3479 | 380.7068 | 471.1623 | 415.9395
1341.3479 | 381.4446 | 470.9688 | 416.2041
1342.3479 | 381.4529 | 471.2473 | 416.3622
1343.3479 | 381.4811 | 471.3132 | 416.529
1344.3479 | 381.4084 | 471.4512 | 416.7061
1345.3479 | 383.1899 | 471.3212 | 417.0919
1346.3479 | 383.4949 | 471.7987 | 417.2243
1347.3479 | 384.2639 | 471.3819 | 417.1132
1348.3479 | 383.5317 | 471.4468 | 417.2177
1349.3479 | 383.0389 | 471.6684 | 417.7516
1350.3479 | 383.9448 | 471.6627 | 417.8908
1351.3479 | 384.0587 | 471.6355 | 419.1169
1352.3479 | 384.6862 | 471.5872 | 418.788
1353.3479 | 385.1589 | 471.6153 | 419.1705
1354.3479 | 385.9596 | 471.9682 | 418.9909
1355.3479 | 386.726 | 471.8456 | 419.2448
1356.3479 | 387.3935 | 472.0358 | 419.6343
1357.3479 | 387.5184 | 471.7062 | 419.7703
1358.3479 | 387.8446 | 472.0398 | 420.6973
1359.3479 | 388.1985 | 472.2275 | 420.193
1360.3479 | 389.8188 | 472.3075 | 420.4999
1361.3479 | 388.9035 | 472.1282 | 420.8226
1362.3479 | 389.7899 | 472.0631 | 420.8618
1363.3479 | 391.238 | 472.3165 | 421.3456
1364.3479 | 391.5129 | 472.6287 | 421.0143
1365.3479 | 391.8536 | 472.8052 | 420.94
1366.3479 | 391.4845 | 472.4329 | 421.2135
1367.3479 | 392.185 | 472.36 | 421.3686
1368.3479 | 392.1517 | 473.0235 | 421.8672
1369.3479 | 392.29 | 472.8147 | 422.1716
1370.3479 | 392.9228 | 472.4487 | 422.147
1371.3479 | 392.7659 | 472.4245 | 422.1117
1372.3479 | 393.4679 | 472.5524 | 422.313
1373.3479 | 393.8584 | 472.7214 | 422.2978
1374.3479 | 393.8817 | 472.6675 | 422.4494
1375.3479 | 394.4812 | 472.6224 | 422.367
1376.3479 | 394.932 | 472.7024 | 422.8207
1377.3479 | 395.0268 | 472.7026 | 422.8639
1378.3479 | 395.3217 | 472.5564 | 423.1527
1379.3479 | 396.121 | 472.5699 | 423.2282
1380.3479 | 397.1314 | 472.6372 | 423.3043
1381.3479 | 397.1338 | 472.8055 | 423.6236
1382.3479 | 397.2882 | 472.8206 | 424.053
1383.3479 | 397.0414 | 473.1927 | 424.4673
1384.3479 | 398.9512 | 473.1352 | 424.4004
1385.3479 | 399.5915 | 473.0732 | 425.0163
1386.3479 | 399.5178 | 473.2408 | 424.9408
1387.3479 | 399.4145 | 473.074 | 424.9281
1388.3479 | 399.917 | 473.107 | 424.7055
1389.3479 | 400.5373 | 473.2767 | 425.1082
1390.3479 | 400.6368 | 473.1606 | 425.3901
1391.3479 | 401.742 | 473.6006 | 425.3773
1392.3479 | 401.5495 | 473.5125 | 425.5488
1393.3479 | 401.1705 | 473.4731 | 425.8194
1394.3479 | 401.4777 | 473.4435 | 425.7507
1395.3479 | 402.3624 | 473.5536 | 426.0093
1396.3479 | 402.8678 | 473.5094 | 426.1532
1397.3479 | 402.9295 | 473.3833 | 426.2258
1398.3479 | 403.3512 | 473.3651 | 426.5138
1399.3479 | 404.0756 | 473.3366 | 426.3907
1400.3479 | 405.0039 | 473.4825 | 426.774
1401.3479 | 405.0977 | 473.5966 | 426.8502
1402.3479 | 405.9488 | 473.7074 | 427.244
1403.3479 | 406.4484 | 473.6233 | 427.3759
1404.3479 | 406.676 | 474.118 | 427.6928
1405.3479 | 407.5749 | 474.2814 | 427.9584
1406.3479 | 408.0706 | 474.4614 | 428.2709
1407.3479 | 408.8877 | 474.4353 | 428.3791
1408.3479 | 409.5137 | 474.3583 | 428.2916
1409.3479 | 409.0754 | 474.3713 | 429.0313
1410.3479 | 409.2879 | 474.581 | 429.7755
1411.3479 | 410.1786 | 474.6818 | 429.9208
1412.3479 | 410.5949 | 474.5137 | 429.851
1413.3479 | 410.907 | 474.6393 | 430.4894
1414.3479 | 410.8906 | 474.7997 | 430.8749
1415.3479 | 411.2986 | 474.6682 | 430.1726
1416.3479 | 411.5158 | 475.1613 | 430.29
1417.3479 | 412.1271 | 475.5472 | 430.781
1418.3479 | 412.8202 | 475.6457 | 431.0151
1419.3479 | 413.03 | 475.1238 | 431.505
1420.3479 | 412.9621 | 475.4191 | 431.4001
1421.3479 | 413.6613 | 475.864 | 431.4231
1422.3479 | 414.0053 | 476.3282 | 432.0175
1423.3479 | 414.597 | 476.4362 | 432.0112
1424.3479 | 414.9056 | 476.1134 | 432.1828
1425.3479 | 417.3424 | 475.8529 | 432.356
1426.3479 | 417.5614 | 475.9647 | 432.2872
1427.3479 | 417.4685 | 475.8968 | 432.2684
1428.3479 | 416.4324 | 475.791 | 432.5981
1429.3479 | 416.1003 | 475.8563 | 432.772
1430.3479 | 416.368 | 475.94 | 432.8293
1431.3479 | 417.0262 | 475.813 | 432.8948
1432.3479 | 417.8121 | 476.0802 | 432.9978
1433.3479 | 418.3856 | 475.9134 | 433.1815
1434.3479 | 419.9456 | 475.7051 | 433.3433
1435.3479 | 419.2916 | 475.6757 | 433.6984
1436.3479 | 418.9327 | 475.6294 | 433.7039
1437.3479 | 419.5782 | 475.7764 | 433.7006
1438.3479 | 419.9012 | 475.9637 | 434.4733
1439.3479 | 421.4218 | 476.0428 | 434.8258
1440.3479 | 422.1131 | 476.2249 | 434.9664
1441.3479 | 422.0068 | 476.0085 | 434.784
1442.3479 | 422.4452 | 475.9286 | 434.8011
1443.3479 | 423.8834 | 476.0204 | 435.2416
1444.3479 | 423.6195 | 475.9727 | 435.5907
1445.3479 | 422.4754 | 475.8752 | 435.3413
1446.3479 | 422.886 | 475.7293 | 435.6934
1447.3479 | 424.2369 | 475.7842 | 435.5804
1448.3479 | 423.8247 | 475.6172 | 435.9603
1449.3479 | 424.4176 | 475.6468 | 436.0651
1450.3479 | 424.2562 | 475.7435 | 435.9552
1451.3479 | 424.9128 | 475.9732 | 436.187
1452.3479 | 425.8741 | 476.1727 | 436.4553
1453.3479 | 425.7558 | 475.9121 | 436.3309
1454.3479 | 425.9661 | 476.0068 | 436.7142
1455.3479 | 427.0662 | 476.087 | 436.9853
1456.3479 | 426.8301 | 475.9762 | 437.0273
1457.3479 | 426.264 | 475.9754 | 437.2908
1458.3479 | 427.6448 | 475.7288 | 437.4415
1459.3479 | 428.4047 | 475.8394 | 437.6631
1460.3479 | 428.5394 | 475.9258 | 437.6366
1461.3479 | 428.8775 | 475.9033 | 437.5077
1462.3479 | 429.173 | 475.952 | 437.8838
1463.3479 | 430.5596 | 475.9904 | 438.4764
1464.3479 | 431.1311 | 476.0116 | 438.2481
1465.3479 | 431.8742 | 476.0459 | 438.3058
1466.3479 | 432.3956 | 475.8862 | 438.6753
1467.3479 | 431.6916 | 475.8941 | 438.6371
1468.3479 | 432.33 | 475.7341 | 438.8401
1469.3479 | 434.4182 | 475.7466 | 438.9528
1470.3479 | 432.7215 | 475.8601 | 439.0501
1471.3479 | 432.6527 | 475.8253 | 439.156
1472.3479 | 434.1167 | 475.7551 | 439.6172
1473.3479 | 434.1998 | 475.7875 | 439.3923
1474.3479 | 433.3123 | 475.8977 | 439.5742
1475.3479 | 434.362 | 475.8584 | 439.6258
1476.3479 | 434.6966 | 475.9022 | 439.6183
1477.3479 | 435.1966 | 475.96 | 439.7793
1478.3479 | 435.9804 | 475.8487 | 439.8787
1479.3479 | 435.9335 | 475.961 | 440.1044
1480.3479 | 436.3775 | 475.9836 | 440.2999
1481.3479 | 436.7953 | 475.9475 | 440.5253
1482.3479 | 436.75 | 475.8672 | 440.5445
1483.3479 | 436.7462 | 475.824 | 440.509
1484.3479 | 437.2702 | 475.8396 | 440.7375
1485.3479 | 437.9052 | 475.9704 | 440.6224
1486.3479 | 439.0939 | 476.0559 | 440.8429
1487.3479 | 438.4205 | 476.4225 | 441.2238
1488.3479 | 438.5969 | 475.9971 | 441.197
1489.3479 | 439.4257 | 475.9876 | 441.2775
1490.3479 | 439.9094 | 475.9596 | 441.5383
1491.3479 | 441.3939 | 476.0137 | 441.6116
1492.3479 | 441.1732 | 475.9231 | 441.8169
1493.3479 | 440.5434 | 475.7423 | 441.6339
1494.3479 | 440.2698 | 475.73 | 441.878
1495.3479 | 440.5402 | 476.5117 | 442.3049
1496.3479 | 441.7588 | 476.7257 | 442.2182
1497.3479 | 441.8394 | 476.7109 | 442.333
1498.3479 | 441.8079 | 476.5895 | 442.2962
1499.3479 | 442.8012 | 476.4259 | 442.3947
1500.3479 | 443.3624 | 476.6434 | 442.2151
1501.3479 | 443.0081 | 476.955 | 442.5642
1502.3479 | 442.4508 | 476.5564 | 442.6545
1503.3479 | 443.1657 | 476.3586 | 442.7365
1504.3479 | 443.4294 | 476.4578 | 443.1414
1505.3479 | 444.2621 | 476.5055 | 443.2253
1506.3479 | 444.42 | 476.5335 | 443.2999
1507.3479 | 444.2784 | 476.43 | 443.4818
1508.3479 | 444.5798 | 476.4855 | 443.7371
1509.3479 | 445.3074 | 476.5332 | 443.7155
1510.3479 | 445.6238 | 476.6417 | 443.8264
1511.3479 | 445.8945 | 476.5307 | 444.0527
1512.3479 | 445.76 | 476.8439 | 443.745
1513.3479 | 447.0367 | 476.5697 | 443.9481
1514.3479 | 445.9313 | 476.5986 | 444.0979
1515.3479 | 445.4336 | 476.7192 | 444.2468
1516.3479 | 445.6331 | 476.7805 | 444.3958
1517.3479 | 446.6971 | 477.1444 | 444.8645
1518.3479 | 446.8395 | 477.6122 | 445.1357
1519.3479 | 448.4798 | 477.2137 | 446.0076
1520.3479 | 448.0897 | 477.1544 | 445.2939
1521.3479 | 448.4451 | 477.2358 | 445.2634
1522.3479 | 449.1899 | 477.5777 | 446.1275
1523.3479 | 449.1653 | 477.4757 | 445.9932
1524.3479 | 449.6392 | 477.219 | 445.6019
1525.3479 | 449.5944 | 477.3644 | 446.2157
1526.3479 | 449.4035 | 477.4801 | 446.2987
1527.3479 | 450.0219 | 477.5401 | 446.0454
1528.3479 | 449.8508 | 477.4517 | 446.1732
1529.3479 | 449.3429 | 477.5491 | 446.3118
1530.3479 | 450.5177 | 477.4129 | 446.2199
1531.3479 | 451.8836 | 477.6292 | 446.3868
1532.3479 | 452.4282 | 477.7271 | 446.8256
1533.3479 | 451.7556 | 477.8557 | 447.2045
1534.3479 | 452.2133 | 477.8662 | 447.3554
1535.3479 | 452.8766 | 477.8678 | 447.4294
1536.3479 | 453.271 | 477.9145 | 447.3715
1537.3479 | 453.5216 | 477.9852 | 447.5058
1538.3479 | 452.8166 | 477.9219 | 447.7392
1539.3479 | 453.5337 | 478.0045 | 447.7035
1540.3479 | 453.8902 | 478.119 | 448.077
1541.3479 | 453.1998 | 478.2697 | 447.9975
1542.3479 | 453.2925 | 478.3927 | 448.3528
1543.3479 | 454.6076 | 478.5999 | 449.1565
1544.3479 | 454.1815 | 478.3712 | 449.0213
1545.3479 | 454.8305 | 478.4029 | 448.7668
1546.3479 | 455.2568 | 478.4354 | 448.6781
1547.3479 | 455.8985 | 478.2774 | 449.1287
1548.3479 | 458.3996 | 478.4434 | 449.3238
1549.3479 | 457.4852 | 478.5797 | 449.2662
1550.3479 | 457.9545 | 478.5686 | 449.4118
1551.3479 | 457.4852 | 478.5401 | 449.9188
1552.3479 | 458.6389 | 478.9766 | 449.5581
1553.3479 | 457.3097 | 478.7442 | 449.7405
1554.3479 | 457.2038 | 478.6967 | 449.5995
1555.3479 | 457.7446 | 478.8493 | 449.996
1556.3479 | 457.7905 | 478.7918 | 449.8567
1557.3479 | 458.1949 | 478.7259 | 450.1099
1558.3479 | 458.3781 | 478.8208 | 450.3713
1559.3479 | 458.9801 | 478.9375 | 450.4888
1560.3479 | 459.286 | 478.963 | 450.7668
1561.3479 | 459.3959 | 479.0433 | 450.7222
1562.3479 | 459.7725 | 478.967 | 450.7604
1563.3479 | 459.9464 | 478.9826 | 451.018
1564.3479 | 460.4324 | 479.2681 | 451.1846
1565.3479 | 460.8204 | 479.2375 | 451.0678
1566.3479 | 461.2507 | 479.5315 | 451.2701
1567.3479 | 462.5037 | 479.6211 | 451.6757
1568.3479 | 461.9602 | 479.579 | 451.7201
1569.3479 | 461.7674 | 479.3427 | 451.9081
1570.3479 | 462.2844 | 479.7608 | 451.9329
1571.3479 | 462.9482 | 479.9228 | 451.882
1572.3479 | 463.0797 | 480.0338 | 451.8885
1573.3479 | 463.1976 | 479.8629 | 452.0518
1574.3479 | 463.5375 | 479.9717 | 452.43
1575.3479 | 463.3565 | 480.0307 | 452.4978
1576.3479 | 463.2933 | 480.5263 | 452.6796
1577.3479 | 463.8341 | 480.3508 | 452.7987
1578.3479 | 464.0466 | 480.3445 | 452.9664
1579.3479 | 464.745 | 480.5847 | 453.4159
1580.3479 | 465.0052 | 480.4432 | 453.3445
1581.3479 | 465.1746 | 480.4121 | 453.28
1582.3479 | 465.8978 | 480.4653 | 453.2944
1583.3479 | 465.5425 | 480.2952 | 453.3323
1584.3479 | 465.7577 | 480.4511 | 453.9344
1585.3479 | 465.5614 | 480.5064 | 453.9886
1586.3479 | 465.5871 | 480.41 | 453.8766
1587.3479 | 466.3063 | 480.634 | 453.9763
1588.3479 | 467.2631 | 480.4284 | 454.3527
1589.3479 | 467.4375 | 480.4876 | 454.1714
1590.3479 | 469.3022 | 480.9035 | 454.2667
1591.3479 | 469.4956 | 480.916 | 454.4483
1592.3479 | 469.7979 | 480.6962 | 454.4536
1593.3479 | 468.6696 | 480.7116 | 454.6049
1594.3479 | 467.8183 | 480.902 | 454.7642
1595.3479 | 467.8067 | 480.8053 | 454.9376
1596.3479 | 468.5712 | 481.275 | 455.1247
1597.3479 | 470.47 | 480.9115 | 455.1007
1598.3479 | 469.6519 | 480.9544 | 455.5375
1599.3479 | 470.1733 | 481.1674 | 455.7922
1600.3479 | 470.6084 | 481.798 | 455.6991
1601.3479 | 471.0805 | 481.6804 | 455.8141
1602.3479 | 471.0747 | 481.1838 | 456.2559
1603.3479 | 470.7348 | 481.1958 | 456.1937
1604.3479 | 470.4175 | 481.0607 | 456.2406
1605.3479 | 471.5812 | 481.4194 | 456.4523
1606.3479 | 472.5292 | 481.3987 | 456.5045
1607.3479 | 472.5194 | 481.2352 | 456.4569
1608.3479 | 472.5408 | 481.2997 | 456.7324
1609.3479 | 472.3526 | 481.3341 | 457.155
1610.3479 | 473.0842 | 481.1356 | 457.132
1611.3479 | 472.6677 | 481.3053 | 457.0861
1612.3479 | 472.3783 | 481.5068 | 457.1781
1613.3479 | 473.7215 | 481.3764 | 457.1498
1614.3479 | 474.2391 | 481.4817 | 457.0971
1615.3479 | 474.4803 | 481.5835 | 457.3193
1616.3479 | 476.4644 | 481.6824 | 457.5573
1617.3635 | 476.2281 | 481.4223 | 457.6756
1618.3479 | 475.5841 | 481.5709 | 457.5353
1619.3479 | 475.6103 | 481.9796 | 457.8307
1620.3479 | 476.6602 | 481.7969 | 458.181
1621.3479 | 476.3792 | 481.7794 | 457.9921
1622.3479 | 476.101 | 481.8805 | 458.3262
1623.3479 | 476.7433 | 482.0244 | 458.437
1624.3479 | 476.0356 | 482.5533 | 458.6598
1625.3479 | 476.799 | 482.5566 | 458.7102
1626.3479 | 477.1552 | 482.6856 | 459.0746
1627.3479 | 476.8059 | 483.2348 | 459.8499
1628.3479 | 476.3558 | 482.9333 | 459.5195
1629.3479 | 477.1362 | 483.0922 | 459.5801
1630.3479 | 477.6283 | 482.8016 | 459.8323
1631.3479 | 478.1779 | 483.8037 | 460.0192
1632.3479 | 478.4659 | 483.3521 | 459.7204
1633.3479 | 478.8274 | 483.0338 | 459.8511
1634.3479 | 479.7312 | 483.0721 | 460.181
1635.3479 | 479.5842 | 483.2207 | 460.4853
1636.3479 | 479.2517 | 483.1972 | 460.4085
1637.3479 | 480.8035 | 483.1394 | 460.7041
1638.3479 | 481.613 | 483.2745 | 460.6186
1639.3479 | 480.8023 | 483.1514 | 460.635
1640.3479 | 480.4935 | 483.1255 | 460.8072
1641.3479 | 480.7433 | 483.1458 | 460.98
1642.3479 | 480.977 | 483.0471 | 460.9055
1643.3479 | 481.696 | 483.0881 | 460.9806
1644.3479 | 481.6997 | 483.1704 | 461.0359
1645.3479 | 481.8158 | 483.3296 | 461.4056
1646.3479 | 481.5836 | 483.2913 | 461.3221
1647.3635 | 482.7785 | 483.2465 | 461.5465
1648.3479 | 482.675 | 483.4363 | 462.0717
1649.3479 | 482.2017 | 483.1786 | 461.8466
1650.3479 | 482.0584 | 483.5837 | 461.7977
1651.3479 | 482.8887 | 483.686 | 462.012
1652.3479 | 482.211 | 483.1592 | 462.027
1653.3479 | 482.7825 | 483.2732 | 461.9958
1654.3479 | 483.2408 | 483.7104 | 462.3232
1655.3479 | 483.4257 | 483.8294 | 462.2972
1656.3479 | 483.5812 | 483.8929 | 462.4688
1657.3479 | 483.2151 | 483.7143 | 462.6929
1658.3479 | 482.7364 | 483.8652 | 462.8901
1659.3479 | 483.3583 | 483.9488 | 462.8245
1660.3479 | 484.2941 | 484.1631 | 462.9415
1661.3479 | 483.9739 | 484.3797 | 463.3016
1662.3479 | 484.6841 | 484.5318 | 463.3553
1663.3479 | 485.2327 | 485.5035 | 463.5093
1664.3479 | 486.2809 | 485.1593 | 463.5455
1665.3479 | 486.5855 | 485.3085 | 463.3361
1666.3479 | 487.3896 | 484.9026 | 463.2749
1667.3479 | 486.8298 | 484.9626 | 464.3367
1668.3479 | 486.6121 | 484.9907 | 464.4764
1669.3479 | 487.1019 | 485.044 | 464.5771
1670.3479 | 486.6062 | 484.7735 | 464.3009
1671.3479 | 489.066 | 485.1236 | 464.3999
1672.3479 | 489.6465 | 485.2711 | 464.5436
1673.3479 | 488.7838 | 485.6424 | 465.2712
1674.3479 | 488.5032 | 485.2614 | 464.9421
1675.3479 | 487.7986 | 485.511 | 464.9391
1676.3479 | 487.8491 | 485.648 | 467.4237
1677.3479 | 487.9121 | 486.084 | 466.227
1678.3479 | 488.3628 | 485.4085 | 466.7456
1679.3479 | 488.3674 | 485.4697 | 466.9568
1680.3479 | 488.588 | 485.529 | 467.1049
1681.3479 | 488.6193 | 485.8544 | 467.7904
1682.3479 | 488.7349 | 485.7628 | 466.9797
1683.3479 | 489.365 | 485.8974 | 466.9786
1684.3479 | 489.2683 | 485.662 | 466.9287
1685.3479 | 489.4729 | 485.7349 | 467.0692
1686.3479 | 490.5929 | 485.744 | 467.1399
1687.3479 | 490.4442 | 485.8978 | 467.4135
1688.3479 | 490.1153 | 486.3014 | 467.3321
1689.3479 | 490.689 | 486.4104 | 467.5256
1690.3479 | 491.7456 | 486.2378 | 467.833
1691.3479 | 491.0269 | 486.4707 | 468.1923
1692.3479 | 490.7023 | 486.421 | 467.9649
1693.3479 | 490.7001 | 486.2878 | 467.8655
1694.3479 | 491.496 | 486.5273 | 468.1197
1695.3479 | 491.2628 | 486.5186 | 468.1916
1696.3479 | 491.5062 | 486.2823 | 468.2662
1697.3479 | 492.1867 | 486.4998 | 468.5493
1698.3479 | 491.6173 | 487.5805 | 469.113
1699.3479 | 491.6313 | 486.7619 | 468.6462
1700.3479 | 491.4441 | 486.6824 | 468.883
1701.3479 | 491.8492 | 486.7055 | 468.9545
1702.3479 | 492.2346 | 486.8213 | 469.0358
1703.3479 | 492.66 | 486.9793 | 469.2243
1704.3479 | 492.3061 | 487.0905 | 469.6702
1705.3479 | 492.1433 | 487.0538 | 469.8621
1706.3479 | 492.2993 | 487.497 | 470.9112
1707.3479 | 492.5344 | 487.7397 | 470.8699
1708.3479 | 492.8655 | 487.7431 | 472.518
1709.3479 | 492.7888 | 488.4493 | 471.7412
1710.3479 | 493.09 | 488.1899 | 471.1677
1711.3479 | 493.3545 | 488.1289 | 471.4013
1712.3479 | 493.6749 | 488.2676 | 471.9893
1713.3479 | 492.8511 | 488.0729 | 471.931
1714.3479 | 493.8205 | 488.1769 | 471.7307
1715.3479 | 493.7654 | 488.0426 | 471.6557
1716.3479 | 493.8628 | 487.8847 | 472.1798
1717.3479 | 493.6088 | 488.319 | 471.8119
1718.3479 | 494.2162 | 488.3696 | 472.0642
1719.3479 | 495.01 | 488.2861 | 472.164
1720.3479 | 495.6396 | 488.2041 | 472.3038
1721.3479 | 496.001 | 488.2131 | 472.2922
1722.3479 | 496.0076 | 488.2202 | 472.4313
1723.3479 | 495.1579 | 488.1116 | 472.1943
1724.3479 | 495.4038 | 488.1315 | 472.369
1725.3479 | 495.5662 | 488.1922 | 472.7358
1726.3479 | 495.2276 | 488.233 | 472.5081
1727.3479 | 495.5545 | 488.2661 | 472.5125
1728.3479 | 495.5656 | 488.2658 | 472.6362
1729.3479 | 496.6992 | 488.7363 | 472.9944
1730.3479 | 497.1318 | 489.052 | 473.6239
1731.3479 | 497.0517 | 489.5576 | 473.5293
1732.3479 | 497.9247 | 489.0509 | 473.2664
1733.3479 | 497.025 | 489.2881 | 473.7952
1734.3479 | 496.3117 | 489.4871 | 474.1752
1735.3479 | 497.0485 | 489.3522 | 474.6036
1736.3479 | 497.4079 | 489.316 | 474.1333
1737.3479 | 497.5162 | 489.5041 | 474.198
1738.3479 | 497.4903 | 490.8415 | 474.4053
1739.3479 | 497.9857 | 490.1671 | 474.4917
1740.3479 | 498.4261 | 489.562 | 474.9568
1741.3479 | 498.0171 | 490.6446 | 475.1956
1742.3479 | 498.6644 | 490.2011 | 474.6325
1743.3479 | 498.0267 | 489.9785 | 474.9952
1744.3479 | 498.1694 | 490.095 | 475.1544
1745.3479 | 498.2952 | 490.1601 | 475.5488
1746.3479 | 498.3229 | 490.1314 | 475.6918
1747.3479 | 498.4898 | 490.5852 | 475.9215
1748.3479 | 499.8182 | 490.6352 | 476.3566
1749.3479 | 498.768 | 490.5271 | 476.7169
1750.3479 | 498.2727 | 490.3995 | 476.3273
1751.3479 | 498.3813 | 490.333 | 476.6708
1752.3479 | 498.741 | 490.7898 | 476.4763
1753.3479 | 499.0019 | 490.4043 | 476.747
1754.3479 | 498.5415 | 490.4362 | 476.6957
1755.3479 | 498.3405 | 490.831 | 476.6463
1756.3479 | 498.7897 | 490.7909 | 476.9071
1757.3479 | 499.3456 | 490.3273 | 476.6189
1758.3479 | 499.444 | 490.2353 | 477.0176
1759.3479 | 499.3191 | 490.5979 | 476.8812
1760.3479 | 500.0318 | 490.7004 | 476.8109
1761.3479 | 499.9879 | 490.5352 | 477.0607
1762.3479 | 499.752 | 490.8081 | 476.9895
1763.3479 | 499.9513 | 490.8054 | 477.2681
1764.3479 | 500.4632 | 490.9387 | 477.441
1765.3479 | 500.543 | 490.7641 | 477.8047
1766.3479 | 501.3578 | 491.2646 | 477.7067
1767.3479 | 501.0198 | 490.9794 | 477.6028
1768.3479 | 500.6766 | 490.8988 | 477.9025
1769.3479 | 501.2556 | 491.2683 | 477.9264
1770.3479 | 501.2241 | 491.5634 | 477.9531
1771.3479 | 501.5596 | 491.7289 | 478.6152
1772.3479 | 502.0307 | 491.9355 | 478.5137
1773.3479 | 502.3469 | 492.5069 | 478.5244
1774.3479 | 502.6094 | 492.1432 | 478.381
1775.3479 | 502.813 | 491.8212 | 478.5141
1776.3479 | 503.7051 | 492.3878 | 478.9933
1777.3479 | 503.5479 | 492.2291 | 479.6557
1778.3479 | 503.0316 | 492.021 | 478.8257
1779.3479 | 503.1882 | 492.4614 | 479.2069
1780.3479 | 503.4521 | 492.6459 | 479.4586
1781.3479 | 503.2164 | 492.675 | 480.3829
1782.3479 | 503.5054 | 493.2404 | 480.3827
1783.3479 | 503.7339 | 493.2062 | 480.5942
1784.3479 | 504.2439 | 494.1146 | 480.9265
1785.3479 | 504.3533 | 493.4858 | 480.683
1786.3479 | 504.6218 | 493.2621 | 480.9237
1787.3479 | 504.2637 | 493.3107 | 481.0105
1788.3479 | 504.0562 | 493.5707 | 481.2121
1789.3479 | 504.5684 | 493.9353 | 481.1519
1790.3479 | 504.8535 | 493.7887 | 481.7409
1791.3479 | 504.8768 | 493.7962 | 481.1525
1792.3479 | 505.4299 | 493.6855 | 481.4904
1793.3479 | 504.9735 | 493.7714 | 481.8266
1794.3479 | 505.6525 | 494.2589 | 481.8137
1795.3479 | 505.1515 | 494.2623 | 481.9506
1796.3479 | 505.1557 | 494.1538 | 481.7469
1797.3635 | 504.909 | 494.2105 | 481.6994
1798.3479 | 505.5467 | 494.6577 | 481.9438
1799.3479 | 505.7249 | 494.1984 | 482.0067
1800.3479 | 506.0043 | 494.4743 | 481.7767
1801.3479 | 506.3098 | 494.3351 | 481.88
1802.3479 | 506.6654 | 494.4093 | 482.0285
1803.3479 | 506.8233 | 494.7245 | 482.4935
1804.3479 | 506.6203 | 495.2963 | 482.9007
1805.3479 | 506.9781 | 495.7139 | 483.2169
1806.3479 | 507.3351 | 495.6143 | 482.9108
1807.3479 | 507.0569 | 496.5688 | 482.9183
1808.3479 | 506.4891 | 497.1584 | 483.0493
1809.3479 | 506.712 | 496.4317 | 483.1484
1810.3479 | 505.9295 | 496.2987 | 483.5967
1811.3479 | 506.3612 | 496.2225 | 483.5712
1812.3479 | 506.3614 | 496.0664 | 483.326
1813.3479 | 505.8294 | 496.6561 | 483.9726
1814.3479 | 506.1611 | 496.9836 | 483.9997
1815.3479 | 507.0888 | 496.5831 | 485.0898
1816.3479 | 507.3408 | 496.4095 | 484.5678
1817.3479 | 506.964 | 496.4018 | 484.6214
1818.3479 | 507.9677 | 496.6504 | 484.748
1819.3479 | 507.8302 | 497.5128 | 485.0285
1820.3479 | 507.8863 | 499.0969 | 485.4632
1821.3479 | 507.2632 | 498.4493 | 485.8208
1822.3479 | 507.7702 | 498.9685 | 484.9268
1823.3479 | 507.6466 | 498.4077 | 485.2119
1824.3479 | 507.416 | 498.19 | 485.7726
1825.3479 | 507.8716 | 498.3357 | 485.6841
1826.3479 | 507.3186 | 498.4884 | 485.741
1827.3479 | 507.8344 | 499.0955 | 485.9
1828.3479 | 508.2521 | 499.9211 | 486.5295
1829.3479 | 507.9243 | 499.12 | 486.4921
1830.3479 | 508.1916 | 499.0934 | 486.4624
1831.3479 | 508.3405 | 500.079 | 486.8005
1832.3479 | 508.2954 | 499.9858 | 486.6726
1833.3479 | 508.5865 | 499.4968 | 486.7754
1834.3479 | 508.6086 | 499.546 | 487.8724
1835.3479 | 508.5488 | 499.8646 | 488.1686
1836.3479 | 509.018 | 499.9959 | 487.9407
1837.3479 | 509.2942 | 499.7771 | 487.8077
1838.3479 | 508.6843 | 500.0436 | 487.7719
1839.3479 | 508.4474 | 500.5489 | 487.8321
1840.3479 | 508.2645 | 500.4099 | 488.2846
1841.3479 | 508.7055 | 501.0901 | 487.9994
1842.3479 | 508.157 | 500.7178 | 487.7077
1843.3479 | 509.3018 | 501.0435 | 489.0228
1844.3479 | 509.2358 | 501.0589 | 489.0212
1845.3479 | 509.056 | 500.6987 | 488.5532
1846.3479 | 509.517 | 501.5884 | 489.8863
1847.3479 | 509.0137 | 502.089 | 490.846
1848.3479 | 509.5133 | 501.4393 | 490.7438
1849.3479 | 509.5862 | 501.6534 | 490.6355
1850.3479 | 508.7655 | 502.0089 | 490.3607
1851.3479 | 509.1471 | 502.6435 | 490.4234
1852.3479 | 509.5278 | 502.2274 | 490.4464
1853.3479 | 508.8859 | 502.261 | 490.4441
1854.3479 | 509.1538 | 502.0838 | 490.9836
1855.3479 | 509.4743 | 501.9636 | 490.6665
1856.3479 | 509.1047 | 501.8724 | 490.7468
1857.3479 | 508.5686 | 501.8404 | 490.8375
1858.3479 | 508.3651 | 501.7568 | 491.2671
1859.3479 | 508.6135 | 501.8768 | 491.5389
1860.3479 | 509.4581 | 502.3024 | 491.2528
1861.3479 | 508.9659 | 502.1819 | 490.5745
1862.3479 | 508.4905 | 502.1741 | 490.7633
1863.3479 | 509.4728 | 502.1914 | 491.8015
1864.3479 | 510.0436 | 502.2624 | 491.5965
1865.3479 | 509.5384 | 502.458 | 491.6419
1866.3479 | 510.1358 | 502.4094 | 493.7881
1867.3479 | 509.488 | 503.7502 | 492.8899
1868.3479 | 509.499 | 502.8187 | 492.0355
1869.3479 | 509.3401 | 503.1045 | 492.4087
1870.3479 | 509.1389 | 503.6425 | 492.9182
1871.3479 | 508.8784 | 503.4913 | 493.5898
1872.3479 | 509.5037 | 503.6629 | 494.4279
1873.3479 | 510.0367 | 503.9241 | 494.5025
1874.3479 | 510.2855 | 504.9942 | 494.1792
1875.3479 | 509.6641 | 504.3309 | 494.4183
1876.3479 | 509.1613 | 504.2593 | 493.9103
1877.3479 | 508.8225 | 504.0872 | 493.6422
1878.3479 | 508.3214 | 505.1119 | 494.8722
1879.3479 | 508.4692 | 505.3634 | 494.6998
1880.3479 | 509.4874 | 504.7821 | 494.7492
1881.3479 | 509.6037 | 504.7576 | 495.0562
1882.3479 | 509.8765 | 504.547 | 495.2998
1883.3479 | 510.2263 | 504.9168 | 495.0382
1884.3479 | 510.5236 | 504.6054 | 494.9742
1885.3479 | 511.1724 | 504.4864 | 494.9468
1886.3479 | 510.4776 | 504.3036 | 494.5555
1887.3479 | 509.9759 | 504.529 | 494.7156
1888.3479 | 511.9748 | 504.7208 | 494.7378
1889.3479 | 511.7883 | 504.7359 | 494.8265
1890.3479 | 511.7164 | 504.9089 | 494.795
1891.3479 | 511.5556 | 504.6896 | 494.734
1892.3479 | 511.2107 | 504.6659 | 495.0162
1893.3479 | 510.8417 | 504.6617 | 495.2265
1894.3479 | 511.6727 | 504.7172 | 495.0697
1895.3479 | 511.8421 | 505.0867 | 494.9321
1896.3479 | 511.381 | 505.5085 | 494.9091
1897.3479 | 512.0377 | 505.1811 | 495.0897
1898.3479 | 512.5812 | 505.0507 | 494.9053
1899.3479 | 512.4336 | 504.878 | 495.9697
1900.3479 | 512.1502 | 506.0395 | 496.1182
1901.3479 | 512.0673 | 505.8649 | 495.9732
1902.3479 | 511.6951 | 505.6088 | 495.8834
1903.3479 | 512.0186 | 505.7468 | 496.0718
1904.3479 | 511.8334 | 505.33 | 496.3907
1905.3479 | 512.4219 | 505.252 | 496.3091
1906.3479 | 512.6839 | 505.4469 | 496.2216
1907.3479 | 512.3656 | 505.8239 | 497.3608
1908.3479 | 512.2712 | 505.7631 | 496.9083
1909.3479 | 512.5024 | 506.6454 | 496.5154
1910.3479 | 512.7684 | 506.0182 | 496.4737
1911.3479 | 513.2537 | 506.619 | 497.1629
1912.3479 | 512.4961 | 506.427 | 496.7012
1913.3479 | 513.0433 | 506.4559 | 497.9248
1914.3479 | 513.4314 | 506.2134 | 497.5232
1915.3479 | 512.7615 | 506.2603 | 498.5087
1916.3479 | 512.3117 | 506.6511 | 498.2059
1917.3479 | 512.0832 | 506.4752 | 497.3359
1918.3479 | 512.249 | 506.8742 | 497.3403
1919.3479 | 512.24 | 507.1188 | 497.5523
1920.3479 | 512.3096 | 507.2526 | 498.6054
1921.3479 | 513.2637 | 507.5005 | 498.2584
1922.3479 | 512.6956 | 507.8729 | 497.7433
1923.3479 | 512.5784 | 508.5815 | 497.8913
1924.3479 | 512.8449 | 507.6236 | 497.7143
1925.3479 | 512.5107 | 508.0858 | 497.8583
1926.3479 | 512.9178 | 508.1764 | 498.2537
1927.3479 | 512.5066 | 507.8161 | 498.0552
1928.3479 | 512.627 | 507.9052 | 498.1881
1929.3479 | 512.7587 | 507.9321 | 498.3526
1930.3479 | 512.6686 | 507.9287 | 498.5116
1931.3479 | 512.7431 | 508.4594 | 498.5584
1932.3479 | 512.9759 | 508.4245 | 498.446
1933.3479 | 513.1678 | 507.8872 | 498.3034
1934.3479 | 513.2109 | 508.1032 | 498.5849
1935.3479 | 512.3114 | 508.7403 | 498.7388
1936.3479 | 512.2106 | 509.2012 | 498.8311
1937.3479 | 512.1511 | 508.6242 | 499.1511
1938.3479 | 511.8662 | 508.9814 | 499.7902
1939.3479 | 511.8115 | 508.6497 | 499.5375
1940.3479 | 511.5174 | 508.6511 | 499.8729
1941.3479 | 511.5592 | 509.1609 | 500.0946
1942.3479 | 512.4913 | 508.8714 | 500.1115
1943.3479 | 511.7407 | 508.6841 | 500.4341
1944.3479 | 511.4653 | 509.1746 | 500.3722
1945.3479 | 511.4195 | 509.1524 | 500.0437
1946.3479 | 511.7446 | 509.7765 | 499.9789
1947.3479 | 512.0985 | 509.1077 | 499.8497
1948.3479 | 512.0866 | 509.0694 | 499.9616
1949.3479 | 512.1877 | 508.8173 | 500.2774
1950.3479 | 512.6022 | 509.0066 | 500.1616
1951.3479 | 512.7785 | 509.209 | 499.7681
1952.3479 | 512.4225 | 509.4863 | 499.9336
1953.3479 | 511.9257 | 510.3936 | 499.9852
1954.3479 | 511.3328 | 509.969 | 499.6853
1955.3479 | 510.9029 | 509.3933 | 499.9102
1956.3479 | 510.856 | 510.0451 | 500.1623
1957.3479 | 510.9121 | 511.246 | 500.1366
1958.3479 | 510.85 | 510.6222 | 500.0462
1959.3479 | 510.9115 | 510.6753 | 500.0703
1960.3479 | 510.4588 | 510.329 | 499.9906
1961.3479 | 510.41 | 510.0869 | 500.3953
1962.3479 | 510.1438 | 510.6187 | 499.9626
1963.3479 | 510.3483 | 510.5685 | 500.0773
1964.3479 | 510.0843 | 511.1078 | 500.1251
1965.3479 | 509.6371 | 510.9996 | 500.643
1966.3479 | 509.4663 | 511.6288 | 500.3696
1967.3479 | 509.5243 | 511.5697 | 500.8081
1968.3479 | 509.6005 | 511.7815 | 500.6575
1969.3479 | 509.1633 | 511.5024 | 500.9203
1970.3479 | 509.3096 | 512.2766 | 501.2449
1971.3479 | 509.6681 | 511.672 | 501.6181
1972.3479 | 510.5756 | 511.4157 | 502.0459
1973.3479 | 509.6562 | 511.5211 | 501.1858
1974.3479 | 509.1824 | 511.9383 | 500.9893
1975.3479 | 509.0106 | 512.0871 | 500.9855
1976.3479 | 509.0926 | 511.6869 | 500.786
1977.3479 | 508.7362 | 511.4994 | 500.6968
1978.3479 | 508.4423 | 511.9346 | 500.9628
1979.3479 | 509.0965 | 511.5845 | 500.8487
1980.3479 | 508.9535 | 511.7303 | 500.9519
1981.3479 | 508.7589 | 512.1762 | 501.3255
1982.3479 | 508.4537 | 512.191 | 501.2641
1983.3479 | 508.0219 | 512.1348 | 500.9926
1984.3479 | 507.8957 | 512.6606 | 500.9822
1985.3479 | 508.2449 | 512.9762 | 500.8838
1986.3479 | 508.5004 | 513.0005 | 501.2531
1987.3479 | 507.866 | 513.4069 | 501.7734
1988.3479 | 507.628 | 513.111 | 501.8968
1989.3479 | 507.8058 | 513.073 | 501.5474
1990.3479 | 507.641 | 513.4547 | 501.6292
1991.3479 | 507.3433 | 513.2931 | 501.6664
1992.3479 | 507.3252 | 513.2664 | 501.5036
1993.3479 | 507.1139 | 513.6444 | 501.2452
1994.3479 | 507.0085 | 513.7366 | 501.3594
1995.3479 | 506.7366 | 514.7438 | 501.3738
1996.3479 | 506.934 | 514.4133 | 501.0981
1997.3479 | 506.6736 | 514.8328 | 501.3015
1998.3479 | 506.5206 | 514.6779 | 501.3632
1999.3479 | 506.3737 | 514.5636 | 501.7784
2000.3479 | 506.1457 | 514.6101 | 501.2253
2001.3479 | 505.7695 | 514.9636 | 501.5971
2002.3479 | 505.8001 | 514.9594 | 501.6937
2003.3479 | 505.7864 | 515.113 | 501.9912
2004.3479 | 505.504 | 516.3254 | 501.6842
2005.3479 | 505.6507 | 515.9619 | 501.9468
2006.3479 | 505.5096 | 515.3908 | 501.7027
2007.3479 | 505.2336 | 515.5912 | 501.2904
2008.3479 | 505.4777 | 516.0354 | 501.1928
2009.3479 | 505.2983 | 516.4244 | 501.0098
2010.3479 | 505.037 | 516.7496 | 501.6574
2011.3479 | 504.738 | 515.8383 | 501.585
2012.3479 | 504.7042 | 515.8753 | 501.3343
2013.3479 | 504.7225 | 516.4263 | 501.3652
2014.3479 | 504.5581 | 516.592 | 501.2938
2015.3479 | 504.3616 | 516.547 | 501.3423
2016.3479 | 504.0537 | 516.6822 | 501.2426
2017.3479 | 504.0498 | 517.0388 | 501.2133
2018.3479 | 504.0765 | 516.9703 | 501.2935
2019.3479 | 504.1202 | 517.0941 | 501.1311
2020.3479 | 504.0021 | 517.818 | 501.535
2021.3479 | 503.8383 | 517.6446 | 501.3515
2022.3479 | 503.6498 | 517.079 | 501.4146
2023.3479 | 503.4909 | 517.0335 | 501.2306
2024.3479 | 503.2483 | 517.2618 | 501.2163
2025.3479 | 503.3536 | 517.2513 | 501.4855
2026.3479 | 503.089 | 517.6481 | 501.1882
2027.3479 | 502.9224 | 518.1478 | 501.4464
2028.3479 | 502.8513 | 517.5472 | 501.8584
2029.3479 | 502.7754 | 518.1632 | 501.3336
2030.3479 | 502.4366 | 517.7103 | 501.2753
2031.3479 | 502.7124 | 518.9357 | 501.6424
2032.3479 | 502.5919 | 518.1859 | 501.2293
2033.3479 | 502.4635 | 518.3703 | 500.8105
2034.3479 | 502.4066 | 518.1552 | 500.8088
2035.3479 | 502.0974 | 518.6099 | 501.2393
2036.3479 | 501.904 | 519.9086 | 501.9033
2037.3479 | 501.8891 | 519.34 | 501.6697
2038.3479 | 502.1964 | 519.1615 | 501.5918
2039.3479 | 501.8655 | 519.3513 | 501.1683
2040.3479 | 501.7154 | 518.6048 | 500.9676
2041.3479 | 501.8868 | 518.83 | 501.4451
2042.3479 | 502.0858 | 519.0045 | 501.3374
2043.3479 | 501.6504 | 519.0764 | 500.9306
2044.3479 | 501.1854 | 519.0131 | 500.8162
2045.3479 | 501.1517 | 519.7034 | 500.8361
2046.3479 | 501.0365 | 519.2175 | 501.2668
2047.3479 | 500.8964 | 519.8396 | 501.1071
2048.3479 | 500.8747 | 519.6533 | 501.3815
2049.3479 | 501.1103 | 519.5932 | 501.9275
2050.3479 | 500.879 | 519.9564 | 501.3515
2051.3479 | 500.4879 | 520.3528 | 501.6546
2052.3479 | 500.6352 | 519.5758 | 501.208
2053.3479 | 500.335 | 519.8091 | 501.2402
2054.3479 | 500.2605 | 520.4758 | 502.0435
2055.3479 | 500.0219 | 520.9533 | 502.7076
2056.3479 | 499.9544 | 521.3478 | 501.7786
2057.3479 | 500.0471 | 520.8926 | 501.5803
2058.3479 | 499.98 | 521.8369 | 501.6688
2059.3479 | 500.0082 | 520.6623 | 501.8409
2060.3479 | 499.796 | 520.385 | 501.2405
2061.3479 | 499.587 | 520.3235 | 501.17
2062.3479 | 499.271 | 520.3161 | 501.0558
2063.3479 | 499.2802 | 520.1785 | 501.2495
2064.3479 | 499.326 | 520.1977 | 501.4059
2065.3479 | 499.5314 | 520.0363 | 501.6831
2066.3479 | 499.778 | 519.8059 | 501.7384
2067.3479 | 499.3117 | 519.9513 | 502.0746
2068.3479 | 499.8709 | 520.3936 | 501.7242
2069.3479 | 499.7476 | 520 | 501.5513
2070.3479 | 499.5039 | 519.9286 | 501.2464
2071.3479 | 499.1632 | 520.7868 | 501.8692
2072.3479 | 499.0238 | 520.7059 | 501.6635
2073.3479 | 499.029 | 520.8216 | 502.0771
2074.3479 | 498.6819 | 521.0166 | 501.7711
2075.3479 | 498.4796 | 522.972 | 501.7658
2076.3479 | 498.4443 | 521.2036 | 501.9957
2077.3479 | 498.7709 | 521.194 | 502.1198
2078.3479 | 498.5537 | 521.0346 | 501.8349
2079.3479 | 498.3576 | 521.7474 | 502.2414
2080.3479 | 498.03 | 522.2169 | 502.6806
2081.3479 | 498.0284 | 522.0399 | 502.3236
2082.3479 | 497.9534 | 523.2715 | 502.8035
2083.3479 | 498.1937 | 523.8526 | 502.1652
2084.3479 | 498.4728 | 523.1104 | 501.9608
2085.3479 | 497.95 | 523.095 | 501.9429
2086.3479 | 497.7616 | 523.0682 | 501.8935
2087.3479 | 497.6262 | 522.9242 | 501.7059
2088.3479 | 497.5577 | 523.6851 | 502.0518
2089.3479 | 497.339 | 523.2102 | 501.7851
2090.3479 | 497.0287 | 523.5848 | 501.6861
2091.3479 | 497.2164 | 522.9647 | 501.5387
2092.3479 | 496.9195 | 523.2016 | 501.5044
2093.3479 | 496.7325 | 523.3294 | 501.5165
2094.3479 | 496.6267 | 523.1707 | 501.5401
2095.3479 | 496.685 | 523.167 | 501.4014
2096.3479 | 496.7924 | 522.9062 | 501.3577
2097.3635 | 496.5998 | 523.0887 | 501.2214
2098.3479 | 496.7075 | 522.9392 | 501.1716
2099.3479 | 496.494 | 522.956 | 501.1151
2100.3479 | 496.1681 | 523.1308 | 501.1392
2101.3479 | 496.0655 | 523.0794 | 501.0769
2102.3479 | 495.8727 | 523.1593 | 501.3675
2103.3479 | 495.6549 | 522.7844 | 501.2037
2104.3479 | 495.5701 | 522.6729 | 500.912
2105.3479 | 495.5034 | 522.5734 | 500.824
2106.3479 | 495.6121 | 522.813 | 500.722
2107.3479 | 495.462 | 522.9396 | 500.6627
2108.3479 | 495.5188 | 523.4113 | 500.969
2109.3479 | 495.2769 | 523.2924 | 500.7833
2110.3479 | 495.2233 | 523.6773 | 500.9374
2111.3479 | 495.0294 | 522.9288 | 501.2277
2112.3479 | 495.0388 | 523.2034 | 500.9955
2113.3479 | 494.8867 | 523.2196 | 500.6013
2114.3479 | 494.6968 | 524.2272 | 500.5511
2115.3479 | 494.6393 | 523.3599 | 500.8327
2116.3479 | 494.6928 | 523.3704 | 500.4285
2117.3479 | 494.4715 | 523.1426 | 500.4477
2118.3479 | 494.4713 | 523.3262 | 500.3258
2119.3479 | 494.2201 | 523.4643 | 500.376
2120.3479 | 494.2661 | 523.32 | 500.3611
2121.3479 | 494.1698 | 523.3216 | 500.3869
2122.3479 | 493.9254 | 523.8004 | 500.3951
2123.3479 | 493.9293 | 524.0029 | 500.5333
2124.3479 | 493.7389 | 524.1909 | 500.0693
2125.3479 | 493.7858 | 523.9864 | 500.1697
2126.3479 | 493.5116 | 524.0174 | 500.3005
2127.3479 | 493.4761 | 523.7188 | 500.5275
2128.3479 | 493.2743 | 523.1405 | 499.94
2129.3479 | 493.1892 | 526.304 | 499.97
2130.3479 | 493.3655 | 526.746 | 500.2569
2131.3479 | 493.2653 | 525.8919 | 500.3553
2132.3479 | 493.2088 | 526.9558 | 500.1675
2133.3479 | 493.0568 | 526.6068 | 500.4191
2134.3479 | 492.9117 | 526.4251 | 500.35
2135.3479 | 492.9485 | 528.2439 | 500.2386
2136.3479 | 493.0235 | 528.1379 | 500.4088
2137.3479 | 492.843 | 527.2557 | 500.5881
2138.3479 | 492.5817 | 527.4017 | 500.5185
2139.3479 | 492.5233 | 527.6288 | 500.4065
2140.3479 | 492.5499 | 528.4727 | 500.6407
2141.3479 | 492.5182 | 530.3404 | 501.323
2142.3479 | 492.4645 | 528.6715 | 500.8719
2143.3479 | 492.3508 | 528.719 | 500.7328
2144.3479 | 492.4966 | 528.5025 | 501.0512
2145.3479 | 492.3558 | 528.2682 | 500.8682
2146.3479 | 492.2703 | 527.9607 | 500.6779
2147.3479 | 492.024 | 528.3982 | 500.5677
2148.3479 | 492.0811 | 528.0939 | 500.5684
2149.3479 | 492.0949 | 530.0022 | 500.6004
2150.3479 | 492.0032 | 529.795 | 500.806
2151.3479 | 492.1905 | 528.7855 | 500.4627
2152.3479 | 492.148 | 529.077 | 500.586
2153.3479 | 491.8676 | 529.0944 | 500.6454
2154.3479 | 491.8454 | 530.3326 | 500.5751
2155.3479 | 491.6263 | 530.777 | 501.2061
2156.3479 | 491.4996 | 530.3172 | 501.4645
2157.3479 | 491.5673 | 530.5159 | 500.7752
2158.3479 | 491.3618 | 530.6347 | 500.76
2159.3479 | 491.2463 | 530.4981 | 500.9077
2160.3479 | 491.2551 | 530.3397 | 500.7416
2161.3479 | 491.2649 | 530.6438 | 500.7646
2162.3479 | 490.9707 | 531.1378 | 501.3844
2163.3479 | 490.971 | 530.8313 | 501.0394
2164.3479 | 490.9722 | 530.4671 | 500.7051
2165.3479 | 490.695 | 531.7151 | 500.5921
2166.3479 | 490.768 | 531.9651 | 500.694
2167.3479 | 490.8334 | 531.3695 | 500.6362
2168.3479 | 490.623 | 532.7145 | 500.6024
2169.3479 | 490.5581 | 531.9921 | 500.5571
2170.3479 | 490.4507 | 531.7181 | 500.5184
2171.3479 | 490.3281 | 531.2861 | 500.5537
2172.3479 | 490.1754 | 531.243 | 500.3631
2173.3479 | 490.2928 | 531.9606 | 500.1316
2174.3479 | 490.2667 | 532.748 | 500.1077
2175.3479 | 490.0475 | 531.428 | 500.0133
2176.3479 | 489.9296 | 531.1965 | 499.9543
2177.3479 | 489.757 | 531.8136 | 500.0432
2178.3479 | 489.7548 | 531.3946 | 500.0789
2179.3479 | 489.6619 | 531.2412 | 499.9406
2180.3479 | 489.5121 | 531.3441 | 499.9986
2181.3479 | 489.3542 | 531.2901 | 499.887
2182.3479 | 489.4124 | 531.9932 | 499.8576
2183.3479 | 489.2024 | 531.3695 | 499.66
2184.3479 | 489.2846 | 531.6989 | 499.8168
2185.3479 | 489.1914 | 531.5013 | 499.7596
2186.3479 | 488.9872 | 531.3782 | 499.9987
2187.3479 | 488.9799 | 531.6088 | 499.6971
2188.3479 | 489.0701 | 531.3867 | 499.5813
2189.3479 | 489.115 | 531.6004 | 499.9714
2190.3479 | 488.9485 | 531.855 | 499.9756
2191.3479 | 488.8102 | 532.8063 | 499.831
2192.3479 | 488.6805 | 534.1137 | 499.9953
2193.3479 | 488.7232 | 532.6471 | 499.6464
2194.3479 | 488.555 | 532.2059 | 500.0089
2195.3479 | 488.4945 | 532.4354 | 500.1045
2196.3479 | 488.4055 | 532.4183 | 500.1644
2197.3479 | 488.2696 | 532.6535 | 499.9123
2198.3635 | 488.2681 | 533.0039 | 499.882
2199.3479 | 488.3307 | 533.1382 | 500.1583
2200.3479 | 488.0957 | 532.9831 | 500.0505
2201.3479 | 488.0072 | 534.2646 | 500.2169
2202.3479 | 487.7738 | 534.8592 | 500.0847
2203.3479 | 487.7541 | 535.9594 | 500.1808
2204.3479 | 487.7581 | 534.9768 | 500.0483
2205.3479 | 487.6333 | 534.5319 | 500.1528
2206.3479 | 487.4881 | 534.3379 | 500.2041
2207.3479 | 487.3372 | 534.5591 | 500.0588
2208.3479 | 487.0511 | 534.4741 | 499.9823
2209.3479 | 487.0932 | 535.0152 | 500.0184
2210.3479 | 486.9081 | 534.3737 | 500.0166
2211.3479 | 486.8434 | 534.2223 | 499.8286
2212.3479 | 486.7566 | 534.261 | 499.7998
2213.3479 | 486.7367 | 534.5699 | 500.0208
2214.3479 | 486.808 | 534.6263 | 500.1568
2215.3479 | 486.997 | 536.7147 | 500.1742
2216.3479 | 487.0043 | 535.5689 | 499.9781
2217.3479 | 486.6957 | 534.9156 | 500.1402
2218.3479 | 486.5369 | 535.4816 | 500.2019
2219.3479 | 486.4084 | 535.015 | 500.2527
2220.3479 | 486.3771 | 534.7142 | 500.4792
2221.3479 | 486.2086 | 534.8062 | 500.367
2222.3479 | 486.3209 | 535.9527 | 500.4348
2223.3479 | 486.1877 | 534.9517 | 500.4889
2224.3479 | 486.1342 | 535.0476 | 500.8053
2225.3479 | 486.0611 | 535.3231 | 500.6683
2226.3479 | 486.0303 | 535.0707 | 500.4548
2227.3479 | 485.8934 | 535.194 | 500.8639
2228.3479 | 485.8407 | 536.4254 | 501.43
2229.3479 | 486.2454 | 536.5631 | 501.5628
2230.3479 | 486.2564 | 537.1779 | 501.4735
2231.3479 | 485.9322 | 536.2092 | 501.1226
2232.3479 | 485.6651 | 536.1972 | 501.2337
2233.3479 | 485.6551 | 536.8537 | 501.2487
2234.3479 | 485.77 | 536.8553 | 501.342
2235.3479 | 485.6818 | 536.8661 | 501.0996
2236.3479 | 485.4889 | 536.1282 | 501.1587
2237.3479 | 485.5054 | 535.8615 | 501.1143
2238.3479 | 485.2564 | 536.045 | 500.9198
2239.3479 | 485.0196 | 535.8831 | 500.7582
2240.3479 | 484.7848 | 535.9288 | 500.9864
2241.3479 | 484.7807 | 535.8831 | 501.1813
2242.3479 | 484.7949 | 535.6576 | 501.0343
2243.3479 | 484.7273 | 535.5528 | 500.9823
2244.3479 | 484.6197 | 535.7115 | 501.0215
2245.3479 | 484.4855 | 535.7904 | 501.1986
2246.3479 | 484.6911 | 535.823 | 501.0328
2247.3479 | 484.6919 | 536.4993 | 501.2304
2248.3479 | 484.6779 | 535.9244 | 501.7129
2249.3479 | 484.4493 | 536.0103 | 502.3148
2250.3479 | 484.2216 | 536.5637 | 501.7502
2251.3479 | 484.1967 | 536.6183 | 502.0169
2252.3479 | 484.1322 | 537.0027 | 501.8129
2253.3479 | 483.975 | 536.6136 | 501.8294
2254.3479 | 483.9635 | 536.5018 | 501.5987
2255.3479 | 483.8518 | 538.5162 | 501.8904
2256.3479 | 483.7475 | 536.9049 | 502.1062
2257.3479 | 483.6006 | 536.685 | 501.5759
2258.3479 | 483.5997 | 537.6389 | 501.91
2259.3479 | 483.5519 | 537.4324 | 501.7612
2260.3479 | 483.4466 | 537.8747 | 501.6639
2261.3479 | 483.262 | 538.4077 | 501.4782
2262.3479 | 483.1977 | 537.4722 | 501.3464
2263.3479 | 483.1393 | 537.196 | 501.8797
2264.3479 | 483.0948 | 537.0837 | 501.7761
2265.3479 | 483.0247 | 537.0636 | 501.628
2266.3479 | 483.0276 | 537.9627 | 502.0557
2267.3479 | 482.9245 | 537.1004 | 501.9907
2268.3479 | 482.8877 | 537.5464 | 501.9582
2269.3479 | 482.6988 | 537.7834 | 501.9459
2270.3479 | 482.7996 | 537.674 | 501.903
2271.3479 | 482.5847 | 537.2465 | 502.0439
2272.3479 | 482.502 | 537.7021 | 502.2464
2273.3479 | 482.518 | 537.1719 | 501.7681
2274.3479 | 482.4311 | 537.3754 | 501.7256
2275.3479 | 482.3842 | 537.5034 | 501.801
2276.3479 | 482.1868 | 537.3728 | 502.2521
2277.3479 | 482.172 | 537.5482 | 502.6564
2278.3479 | 482.2867 | 537.6006 | 502.3949
2279.3479 | 482.3335 | 538.2935 | 503.1884
2280.3479 | 482.5196 | 538.88 | 502.297
2281.3479 | 482.5365 | 539.515 | 502.9561
2282.3479 | 482.2139 | 539.2299 | 503.1444
2283.3479 | 482.238 | 538.846 | 502.4025
2284.3479 | 482.2673 | 539.6098 | 502.6813
2285.3479 | 482.2099 | 540.4787 | 503.1097
2286.3479 | 482.1173 | 539.8581 | 503.5408
2287.3479 | 481.9232 | 539.317 | 503.248
2288.3479 | 482.0507 | 539.9642 | 502.9462
2289.3479 | 482.0812 | 539.4762 | 502.8943
2290.3479 | 481.7949 | 538.9685 | 502.6898
2291.3479 | 481.7004 | 539.1698 | 502.7005
2292.3479 | 481.6956 | 538.7187 | 502.7458
2293.3479 | 481.7133 | 539.1113 | 502.6198
2294.3479 | 481.6174 | 538.9013 | 503.1897
2295.3479 | 481.6208 | 538.6045 | 502.6548
2296.3479 | 481.4918 | 539.1757 | 502.5683
2297.3479 | 481.4873 | 538.901 | 502.5416
2298.3479 | 481.3532 | 538.5372 | 502.7285
2299.3479 | 481.3368 | 538.3313 | 502.4337
2300.3479 | 481.3087 | 538.6365 | 502.4101
2301.3479 | 481.1201 | 538.452 | 502.3328
2302.3479 | 481.0541 | 538.0007 | 502.452
2303.3479 | 481.1289 | 539.226 | 503.2411
2304.3479 | 480.9447 | 539.4784 | 502.5288
2305.3479 | 480.9027 | 538.5757 | 502.319
2306.3479 | 480.7242 | 538.4855 | 502.4306
2307.3479 | 480.7101 | 538.8005 | 503.012
2308.3479 | 480.6572 | 538.9058 | 502.9942
2309.3479 | 480.6689 | 538.9611 | 502.8426
2310.3479 | 480.5513 | 538.9318 | 502.4125
2311.3479 | 480.4941 | 538.7403 | 502.8072
2312.3479 | 480.5073 | 539.4048 | 502.7802
2313.3479 | 480.5097 | 539.5795 | 502.722
2314.3479 | 480.3366 | 539.107 | 503.0743
2315.3479 | 480.3097 | 538.8354 | 503.8923
2316.3479 | 480.273 | 539.3801 | 503.6767
2317.3479 | 480.2759 | 539.553 | 503.4899
2318.3479 | 480.2755 | 538.9897 | 502.9928
2319.3479 | 480.265 | 538.755 | 503.0025
2320.3479 | 479.8938 | 538.8624 | 503.732
2321.3479 | 479.9354 | 539.0294 | 506.0934
2322.3479 | 480.0153 | 539.4009 | 505.9864
2323.3479 | 480.0518 | 539.9311 | 506.0886
2324.3479 | 479.9132 | 539.7902 | 505.3313
2325.3479 | 479.8096 | 539.2383 | 505.7345
2326.3479 | 479.7676 | 539.1297 | 504.8829
2327.3479 | 480.3026 | 539.8504 | 504.8446
2328.3479 | 480.3336 | 539.315 | 504.7418
2329.3479 | 479.8955 | 539.1705 | 504.5279
2330.3479 | 479.5838 | 538.9704 | 504.2274
2331.3479 | 479.5128 | 538.9406 | 504.3341
2332.3479 | 479.2233 | 538.8354 | 504.4962
2333.3479 | 479.1829 | 538.9296 | 504.5289
2334.3479 | 479.1668 | 538.8386 | 504.2857
2335.3479 | 479.1203 | 538.7658 | 504.2158
2336.3479 | 479.1057 | 538.6065 | 504.3174
2337.3479 | 479.2337 | 538.4942 | 504.2437
2338.3479 | 479.2173 | 538.667 | 504.4406
2339.3479 | 479.0033 | 538.5619 | 504.6508
2340.3479 | 478.9281 | 538.2225 | 504.6656
2341.3479 | 478.9876 | 538.0424 | 504.2865
2342.3479 | 478.8422 | 538.1596 | 504.2205
2343.3479 | 478.6943 | 538.2923 | 504.4083
2344.3479 | 478.4433 | 538.3003 | 504.1877
2345.3479 | 478.4516 | 537.9988 | 504.1119
2346.3479 | 478.3467 | 537.908 | 504.0994
2347.3479 | 478.3044 | 537.7863 | 504.2222
2348.3479 | 478.3512 | 537.9039 | 504.1763
2349.3479 | 478.2406 | 537.8019 | 504.096
2350.3479 | 478.1976 | 537.6306 | 504.0478
2351.3479 | 478.1031 | 537.7709 | 504.1778
2352.3479 | 477.9824 | 537.7401 | 503.9357
2353.3479 | 478.0302 | 537.388 | 503.8804
2354.3479 | 477.9708 | 537.4665 | 503.9148
2355.3479 | 477.8601 | 537.3216 | 504.0456
2356.3479 | 477.7893 | 537.1623 | 503.8979
2357.3479 | 477.7412 | 537.3447 | 504.1933
2358.3479 | 477.6959 | 537.1074 | 504.0437
2359.3479 | 477.6609 | 536.9758 | 503.9681
2360.3479 | 477.4684 | 536.6593 | 504.0488
2361.3479 | 477.5002 | 537.0985 | 504.061
2362.3479 | 477.4164 | 536.9204 | 504.1783
2363.3479 | 477.3814 | 536.6577 | 503.9989
2364.3479 | 477.1921 | 536.6033 | 503.8932
2365.3479 | 477.2475 | 536.9465 | 503.943
2366.3479 | 477.1854 | 536.6714 | 504.1496
2367.3479 | 477.1307 | 536.4418 | 504.1276
2368.3479 | 477.0286 | 537.1939 | 504.0759
2369.3479 | 476.9529 | 536.9591 | 504.5428
2370.3479 | 476.9166 | 536.9216 | 505.1767
2371.3479 | 476.8475 | 536.8572 | 504.7671
2372.3479 | 476.9033 | 537.1793 | 504.3381
2373.3479 | 476.8445 | 536.8369 | 504.1722
2374.3479 | 476.7457 | 537.0843 | 504.226
2375.3479 | 476.5779 | 536.928 | 504.2537
2376.3479 | 476.518 | 536.9247 | 504.0232
2377.3479 | 476.6212 | 536.585 | 503.9278
2378.3635 | 476.5003 | 536.5811 | 505.0156
2379.3479 | 476.4555 | 536.7163 | 504.8399
2380.3479 | 476.3814 | 536.5487 | 504.5338
2381.3479 | 476.3941 | 537.0733 | 504.4553
2382.3479 | 476.2506 | 537.041 | 504.7233
2383.3479 | 476.1897 | 536.7146 | 504.8149
2384.3479 | 476.097 | 536.5087 | 504.3474
2385.3479 | 476.081 | 536.5423 | 504.2818
2386.3479 | 476.1224 | 537.0772 | 504.4157
2387.3479 | 476.0409 | 536.6021 | 504.5494
2388.3479 | 476.041 | 536.9527 | 504.5657
2389.3479 | 476.1668 | 536.8575 | 504.3032
2390.3479 | 476.0474 | 536.6323 | 504.8498
2391.3479 | 475.8326 | 536.3134 | 504.8034
2392.3479 | 475.7722 | 536.9521 | 505.1071
2393.3479 | 475.7048 | 536.8201 | 505.1811
2394.3479 | 475.5969 | 536.9907 | 505.0402
2395.3479 | 475.547 | 537.1543 | 505.6362
2396.3479 | 475.5603 | 536.9366 | 506.0468
2397.3479 | 475.5341 | 537.2271 | 505.4867
2398.3479 | 475.4882 | 537.0965 | 504.9172
2399.3479 | 475.1078 | 537.0816 | 505.1158
2400.3479 | 475.1461 | 536.5778 | 505.0545