## Test Conditions
DESIREE-FIRE Intermediate Scale Test Number 9 - Circuit Simulator Data Only
Test Date: | 2010-03-17
DCSim DAQ Start Time | 13:14
DCSim Time for Synchronization | 13:15
Heat Source Synchronization | 0:00 | hour:minutes:seconds
Heat Source DAQ Start Time | 13:14
Fire Time | 13:41
Offset | 0:27 | hour:minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 1620 | seconds
Heat Source Offset | 0:26 | hour:minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 1590 | seconds
Heat Source Stop Time | 14:36
Test Duration | 0:55 | hour:minutes:seconds
| 3300 | seconds
CT500 turns | 2 | 1 or 2 | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 turns | 5 | 1 or 5
Pre-Test Baseline: | Gathered | Gathered or Not Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit number | Cable Type |  | Cable TC channel | Air TC Channel
MOV 1 | Kerite, 10c, 12AWG, without zinc wrap |  | Channel 3 represented as "B-Position - Kerite 10c w/o" in the Temperature Data File is monitoring the center of the cable sample sitting within the tray. | Channel 1 represented as "B-Position - Tray - Middle" in the Temperature Data File is monitoring the air temperature in the middle of the tray at B Position.
MOV 2 | Armored Cable, 8c, 12AWG |  | There are three cable TCs monitoring internal temperatures for the armored cables in D Position. Channels 11, 12, and 13 are represented as "D Position - Armored 3'", "D Position - Armored 5'", and "D Position - Armored 7'" in the raw temperature files. | There are three cable TCs monitoring air temperatures for the armored cables in D Position. Channels 8, 9, and 10 are represented as "D Position - 3'", "D Position - Middle", and "D Position - 7'" in the raw temperature files.
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | MOV-1_CT500 | MOV-1a_CT35_1_P | MOV-1a_CT35_2_N | MOV-1b_CT35_1_G | MOV-1b_CT35_2_R | MOV-1b_CT35_3_YO | MOV-1b_CT35_4_YC | MOV-2_CT500 | MOV-2a_CT35_1_P | MOV-2a_CT35_2_N | MOV-2b_CT35_1_G | MOV-2b_CT35_2_R | MOV-2b_CT35_3_YO | 2b_CT35_4_YC1 | MOV-1a_VT7_1_SP | MOV-1a_VTU_1_P | MOV-1a_VTU_2_N | MOV-1b_VT7_1_G | MOV-1b_VT7_2_R | MOV-1b_VT7_3_YO1 | MOV-1b_VT7_4_YC1 | MOV-2a_VT7_1_SP | MOV-2a_VTU_1_P | MOV-2a_VTU_2_N | MOV-2b_VT7_1_G | MOV-2b_VT7_2_R | 2b_VT7_3_YO1 | MOV-2b_VT7_4_YC1 | {MOV1} V(N) - V(Batt -) | {MOV1} V(P) - V(Batt +) | {MOV1} V(G) - V(Batt +) | {MOV1} V(R) - V(Batt -) | {MOV1} V(YC1) - V(Batt -) | {MOV1} V(YO1) - V(Batt -) | {MOV1} V(YC1) - V(N) | {MOV1} V(YO1) - V(N) | {MOV2} V(N) - V(Batt -) | {MOV2} V(P) - V(Batt +) | {MOV2} V(G) - V(Batt +) | {MOV2} V(R) - V(Batt -) | {MOV2} V(YC1) - V(Batt -) | {MOV2} V(YO1) - V(Batt -) | {MOV2} V(YC1) - V(N) | {MOV2} V(YO1) - V(N) | {MOV-1} V(R) - V(N) | {MOV-1} V(G) - V(N) | {MOV-2} V(R) - V(N) | {MOV-2} V(G) - V(N) | {MOV-1} V(P) - V(N) | {MOV-2} V(P) - V(N) | {MOV-1} V(P) - V(Batt -) | {MOV-2} V(P) - V(Batt -) | {MOV-1} V(N) - V(Batt +) | {MOV-2} V(N) - V(Batt +) | {MOV-1} V(G) - V(Batt -) | {MOV2} V(G) - V(Batt-) | {MOV1} V(SP) - V(Batt -) | {MOV2} V(SP) - V(Batt -)
-0.6875 | 122.1451 | -61.0107 | 61.0153 | -0.0016785 | 6.7501 | 0.067182 | 0.065142 | -0.00071343 | -0.0033369 | 0.00276 | 0.011658 | 0.0009506 | 0.070788 | 0.05956 | -0.0047039 | 0.01314 | -0.0035056 | -0.34332 | 60.7864 | -60.9192 | 61.203 | -60.759 | -61.1572 | -61.2625 | -0.32959 | 60.791 | -61.0153 | 60.9695 | -60.997 | -61.0657 | -61.3174 | 0.091553 | -0.22888 | 0.18768 | 0.25177 | -0.25177 | -0.14648 | -0.34332 | -0.23804 | -0.004578 | -0.2243 | -0.045777 | 0.013733 | -0.3067 | -0.054932 | -0.30212 | -0.050354 | 0.16022 | 122.1222 | 0.018311 | 121.9849 | 121.7056 | 121.8063 | 121.7972 | 121.8018 | -121.9345 | -122.0306 | 122.2137 | 121.9803 | 60.6674 | 60.6812
1.0469 | 122.1405 | -61.0794 | 60.9558 | -0.0016785 | 6.756 | 0.068891 | 0.065783 | 0.0024908 | -0.0063275 | -0.0012988 | -0.0036011 | 0.0030868 | 0.072711 | 0.057851 | -0.00043151 | 0.012499 | 0.00012601 | -0.4303 | 60.7178 | -60.9558 | 61.1069 | -60.8643 | -61.2808 | -61.3586 | -0.41199 | 60.6949 | -61.0565 | 60.9055 | -61.0931 | -61.1618 | -61.3586 | 0.1236 | -0.23804 | 0.15106 | 0.21515 | -0.27924 | -0.20142 | -0.40283 | -0.32501 | 0.022888 | -0.26093 | -0.050354 | -0.013733 | -0.27924 | -0.082397 | -0.30212 | -0.10528 | 0.091553 | 122.0627 | -0.036621 | 121.962 | 121.6736 | 121.7514 | 121.7972 | 121.7743 | -121.9116 | -122.0123 | 122.1863 | 121.9849 | 60.6491 | 60.6674
2.7812 | 122.1451 | -60.9833 | 61.0153 | 0.01358 | 6.7498 | 0.065901 | 0.06386 | 0.0037726 | -0.0056867 | -0.0027942 | -0.00054933 | -0.0001174 | 0.069293 | 0.062765 | -0.0014997 | 0.015063 | -0.0041464 | -0.28381 | 60.7224 | -60.8688 | 61.2717 | -60.672 | -61.116 | -61.1893 | -0.26093 | 60.7636 | -60.9512 | 60.9924 | -60.9558 | -61.0245 | -61.2762 | 0.11444 | -0.29297 | 0.25635 | 0.31128 | -0.20599 | -0.13275 | -0.32044 | -0.24719 | 0.032043 | -0.25177 | -0.022888 | 0.027465 | -0.29297 | -0.041199 | -0.32501 | -0.073242 | 0.19684 | 122.1405 | -0.004578 | 121.9437 | 121.5912 | 121.7148 | 121.7056 | 121.7468 | -121.8842 | -121.9666 | 122.2549 | 121.9757 | 60.6995 | 60.7224
4.4375 | 122.168 | -61.0199 | 60.9924 | 0.028839 | 6.7524 | 0.069959 | 0.065569 | 0.0020636 | -0.0018415 | -1.7026e-05 | 0.011658 | 0.003514 | 0.071429 | 0.060415 | -0.0029949 | 0.012926 | 0.0031168 | -0.32501 | 60.7819 | -60.9329 | 61.2259 | -60.7452 | -61.1252 | -61.2213 | -0.31128 | 60.7864 | -61.0062 | 60.9879 | -60.9787 | -61.0519 | -61.2946 | 0.086975 | -0.21057 | 0.23346 | 0.27466 | -0.20142 | -0.10529 | -0.28839 | -0.19226 | 0.013732 | -0.20599 | -0.004578 | 0.041198 | -0.27466 | -0.032044 | -0.28839 | -0.045776 | 0.18768 | 122.1588 | 0.027466 | 121.994 | 121.7148 | 121.7926 | 121.8018 | 121.8063 | -121.9254 | -121.9986 | 122.2458 | 122.0078 | 60.6949 | 60.7086
6.1719 | 122.1268 | -61.0794 | 60.9558 | -0.0016785 | 6.7488 | 0.067396 | 0.064929 | 0.0014228 | -0.0037641 | 0.00019657 | -0.00054933 | 0.0026596 | 0.069507 | 0.066183 | -0.0027813 | 0.014208 | -0.0017966 | -0.41199 | 60.7178 | -60.9604 | 61.1114 | -60.8688 | -61.2946 | -61.377 | -0.45776 | 60.704 | -61.0565 | 60.9055 | -61.0794 | -61.1664 | -61.3632 | 0.11902 | -0.23804 | 0.15564 | 0.21057 | -0.29755 | -0.21515 | -0.41656 | -0.33417 | 0.022888 | -0.25177 | -0.050354 | 0 | -0.28381 | -0.086975 | -0.3067 | -0.10986 | 0.091553 | 122.0718 | -0.022888 | 121.962 | 121.6782 | 121.7606 | 121.7972 | 121.7834 | -121.9162 | -122.0123 | 122.1909 | 121.9849 | 60.6674 | 60.6216
7.8906 | 122.1817 | -61.0382 | 60.9695 | 0.005951 | 6.74 | 0.068891 | 0.067065 | 0.0050544 | -0.0054731 | -0.0032214 | 0.0055543 | 0.0026596 | 0.070575 | 0.063192 | -0.0032087 | 0.014849 | -0.0022238 | -0.33417 | 60.759 | -60.9558 | 61.2076 | -60.7361 | -61.1664 | -61.2488 | -0.25635 | 60.7498 | -60.9879 | 60.997 | -60.9741 | -61.0519 | -61.2946 | 0.082397 | -0.21057 | 0.23804 | 0.30212 | -0.21057 | -0.12817 | -0.29297 | -0.21057 | 0.050354 | -0.21973 | 0.027466 | 0.064087 | -0.25635 | -0.013733 | -0.3067 | -0.064087 | 0.21973 | 122.1634 | 0.013733 | 121.9849 | 121.7148 | 121.7377 | 121.7972 | 121.788 | -121.9254 | -121.9574 | 122.2458 | 122.0352 | 60.704 | 60.7819
9.5625 | 122.1634 | -61.0428 | 60.9375 | 0.005951 | 6.7533 | 0.06825 | 0.065569 | 0.0014228 | -0.00098689 | -0.0019396 | 0.0025025 | 0.0020188 | 0.06972 | 0.058919 | -0.0040631 | 0.015703 | -0.0045736 | -0.33875 | 60.7315 | -60.9329 | 61.2122 | -60.7178 | -61.1572 | -61.2488 | -0.29297 | 60.7269 | -60.9924 | 60.965 | -60.9787 | -61.084 | -61.3174 | 0.10986 | -0.20599 | 0.27466 | 0.32501 | -0.20599 | -0.11444 | -0.31586 | -0.22431 | 0.050354 | -0.21057 | 0.027466 | 0.064087 | -0.27466 | -0.041198 | -0.32501 | -0.091552 | 0.21515 | 122.1451 | 0.013733 | 121.9574 | 121.6644 | 121.7194 | 121.7743 | 121.7697 | -121.8704 | -121.9299 | 122.2549 | 122.0078 | 60.704 | 60.7498
11.2969 | 122.1222 | -61.0336 | 60.9558 | -0.0016785 | 6.7507 | 0.068678 | 0.065783 | 0.0039862 | -0.0044049 | 0.0012646 | -0.00054933 | 0.0018052 | 0.070147 | 0.062765 | -0.0014997 | 0.014849 | -0.0017966 | -0.37537 | 60.7224 | -60.9238 | 61.1618 | -60.7819 | -61.2488 | -61.322 | -0.37079 | 60.7224 | -61.0245 | 60.9192 | -61.0474 | -61.116 | -61.3541 | 0.10986 | -0.23346 | 0.20599 | 0.25177 | -0.28839 | -0.21515 | -0.39825 | -0.32501 | 0.009155 | -0.23346 | -0.036622 | -0.013733 | -0.32043 | -0.082398 | -0.32959 | -0.091553 | 0.14191 | 122.0856 | -0.022888 | 121.9437 | 121.6461 | 121.7468 | 121.756 | 121.756 | -121.8796 | -121.9803 | 122.1954 | 121.9528 | 60.6583 | 60.6628
13.0156 | 122.1176 | -60.9879 | 61.0153 | -0.0016785 | 6.7541 | 0.067823 | 0.065142 | -0.001568 | -0.0037641 | -0.001726 | -0.0036011 | 0.0018052 | 0.070147 | 0.067037 | -0.0055585 | 0.012499 | 0.00098061 | -0.33417 | 60.7544 | -60.8688 | 61.1938 | -60.7498 | -61.1572 | -61.2442 | -0.31586 | 60.7819 | -60.9467 | 60.965 | -60.9695 | -61.0199 | -61.2854 | 0.11902 | -0.26093 | 0.17853 | 0.23804 | -0.25635 | -0.16937 | -0.37537 | -0.28839 | 0.041199 | -0.23346 | -0.050354 | 0.018311 | -0.29755 | -0.032043 | -0.33875 | -0.073242 | 0.11902 | 122.0627 | -0.022888 | 121.9116 | 121.6232 | 121.7285 | 121.7422 | 121.7697 | -121.8842 | -121.962 | 122.1817 | 121.9528 | 60.6537 | 60.672
14.7344 | 122.113 | -61.0199 | 60.9238 | -0.009308 | 6.7492 | 0.067396 | 0.064929 | -0.0047724 | -0.0054731 | 0.001692 | -0.00054933 | 0.0033004 | 0.070575 | 0.052083 | -0.0019269 | 0.014208 | -0.0035056 | -0.36621 | 60.7132 | -60.9375 | 61.1664 | -60.7864 | -61.235 | -61.3129 | -0.36621 | 60.7132 | -61.0107 | 60.9283 | -61.0428 | -61.1343 | -61.3403 | 0.082397 | -0.21057 | 0.24262 | 0.23346 | -0.29297 | -0.21515 | -0.37537 | -0.29755 | 0.009155 | -0.21057 | 0.004578 | -0.022889 | -0.32043 | -0.11444 | -0.32959 | -0.1236 | 0.15106 | 122.1039 | -0.032044 | 121.9391 | 121.6507 | 121.7239 | 121.7331 | 121.7331 | -121.8613 | -121.9345 | 122.1863 | 121.9482 | 60.6537 | 60.6537
16.4062 | 122.2549 | -60.9467 | 60.9375 | -0.0016785 | 6.74 | 0.066114 | 0.061938 | -0.0069086 | -0.0065411 | 0.0014784 | -0.0036011 | -0.002681 | 0.069934 | 0.066183 | -0.0051313 | 0.01784 | -0.0013694 | -0.31586 | 60.6995 | -60.878 | 61.3129 | -60.5896 | -61.0199 | -61.1298 | -0.15564 | 60.7178 | -60.9146 | 61.1023 | -60.8459 | -60.9283 | -61.1893 | 0.068664 | -0.23804 | 0.37537 | 0.35706 | -0.18311 | -0.073242 | -0.25177 | -0.14191 | 0.032043 | -0.21973 | 0.16479 | 0.10071 | -0.24262 | 0.01831 | -0.27466 | -0.013733 | 0.28839 | 122.1909 | 0.068665 | 122.0169 | 121.5775 | 121.6324 | 121.6461 | 121.6644 | -121.8155 | -121.8521 | 122.2595 | 122.0489 | 60.6308 | 60.791
18.125 | 122.2 | -61.0062 | 60.91 | 0.028839 | 6.7443 | 0.068464 | 0.065356 | -0.00071343 | 8.111e-05 | 0.0019056 | 0.0055543 | 0.000737 | 0.06972 | 0.065114 | -0.0014997 | 0.014422 | -0.0020102 | -0.37994 | 60.6583 | -60.9375 | 61.2122 | -60.7086 | -61.1481 | -61.2305 | -0.28381 | 60.6766 | -61.0016 | 60.9924 | -60.9833 | -61.0336 | -61.29 | 0.068665 | -0.25177 | 0.30212 | 0.29755 | -0.2243 | -0.14191 | -0.29297 | -0.21057 | 0.004578 | -0.23346 | 0.082398 | 0.022889 | -0.28381 | -0.027465 | -0.28839 | -0.032043 | 0.22888 | 122.1497 | 0.018311 | 121.994 | 121.5958 | 121.6782 | 121.6644 | 121.6827 | -121.8475 | -121.9116 | 122.2183 | 121.9986 | 60.6262 | 60.7224
19.8438 | 122.2183 | -60.9421 | 60.9741 | 0.01358 | 6.7447 | 0.068037 | 0.06386 | 0.0041998 | -0.00077329 | -0.0010852 | -0.00054933 | 0.000737 | 0.070575 | 0.061696 | -0.0019269 | 0.016772 | -0.0022238 | -0.39368 | 60.6903 | -60.9055 | 61.2167 | -60.7132 | -61.1389 | -61.2305 | -0.28839 | 60.6857 | -60.965 | 61.0199 | -60.9283 | -60.9787 | -61.2442 | 0.036621 | -0.28381 | 0.24262 | 0.22888 | -0.28839 | -0.19684 | -0.32501 | -0.23346 | -0.022888 | -0.28839 | 0.045776 | 0.013733 | -0.30212 | -0.036621 | -0.27924 | -0.013733 | 0.19226 | 122.1222 | 0.036621 | 121.9849 | 121.5958 | 121.6507 | 121.6324 | 121.6278 | -121.8796 | -121.9391 | 122.1588 | 121.962 | 60.5484 | 60.6537
21.5156 | 122.1817 | -60.9879 | 60.965 | 0.01358 | 6.7402 | 0.066755 | 0.067065 | 0.005268 | -0.0031231 | 0.00041017 | 0.0025025 | 0.0045822 | 0.070788 | 0.050802 | -0.0032087 | 0.015917 | -0.0045736 | -0.32044 | 60.7452 | -60.9283 | 61.2076 | -60.7224 | -61.1481 | -61.2488 | -0.25635 | 60.7498 | -60.9833 | 60.9924 | -60.9604 | -61.0336 | -61.2762 | 0.059509 | -0.21973 | 0.24262 | 0.2655 | -0.26093 | -0.16022 | -0.32043 | -0.21973 | 0.004578 | -0.21515 | 0.027466 | 0.027466 | -0.28839 | -0.045776 | -0.29297 | -0.050354 | 0.20599 | 122.1359 | 0.022888 | 121.9757 | 121.6736 | 121.7331 | 121.7331 | 121.7377 | -121.8933 | -121.9482 | 122.1954 | 121.9803 | 60.6674 | 60.7315
23.25 | 122.1085 | -61.0519 | 60.9467 | -0.0016785 | 6.7466 | 0.068037 | 0.065356 | -0.0013544 | -0.0035505 | 0.00019657 | -0.0036011 | 0.0022324 | 0.07207 | 0.056569 | -0.0047039 | 0.015063 | -0.0062826 | -0.39368 | 60.7132 | -60.9558 | 61.1206 | -60.8185 | -61.2488 | -61.3358 | -0.39368 | 60.7315 | -61.0153 | 60.9146 | -61.0611 | -61.1298 | -61.3449 | 0.09613 | -0.23346 | 0.17395 | 0.23346 | -0.28381 | -0.19684 | -0.37994 | -0.29297 | 0.036621 | -0.21515 | -0.032043 | -0.009155 | -0.29297 | -0.07782 | -0.32959 | -0.11444 | 0.13733 | 122.0764 | -0.045776 | 121.9299 | 121.669 | 121.7468 | 121.7651 | 121.7834 | -121.9025 | -121.962 | 122.1725 | 121.9666 | 60.6583 | 60.6583
24.9062 | 122.1451 | -61.0565 | 60.9146 | -0.0016785 | 6.7441 | 0.069319 | 0.067278 | 0.0012092 | -0.0033369 | -0.0025806 | -0.0036011 | 0.003514 | 0.070575 | 0.059133 | -0.0025677 | 0.013354 | 0.0016214 | -0.43488 | 60.6903 | -60.9467 | 61.116 | -60.8322 | -61.2717 | -61.3358 | -0.40741 | 60.6903 | -61.0291 | 60.9283 | -61.0519 | -61.1298 | -61.3449 | 0.10986 | -0.2243 | 0.20142 | 0.22431 | -0.27923 | -0.21515 | -0.3891 | -0.32501 | 0.027466 | -0.2243 | 0.013733 | 0.004578 | -0.28839 | -0.073242 | -0.31586 | -0.10071 | 0.11444 | 122.0627 | -0.022888 | 121.9574 | 121.637 | 121.7194 | 121.7468 | 121.7468 | -121.8613 | -121.9437 | 122.1725 | 121.9849 | 60.6216 | 60.6491
26.6406 | 122.1863 | -60.9879 | 60.9467 | 0.028839 | 6.7353 | 0.066541 | 0.06386 | -0.00049983 | -0.0035505 | -0.00087163 | 0.0086061 | -0.0007584 | 0.071643 | 0.071309 | -0.0038495 | 0.017199 | 0.00098061 | -0.3891 | 60.6857 | -60.9146 | 61.1984 | -60.7178 | -61.1526 | -61.2488 | -0.32959 | 60.7224 | -60.9833 | 60.9924 | -60.9558 | -61.0107 | -61.2625 | 0.073242 | -0.26093 | 0.25177 | 0.27008 | -0.26093 | -0.16479 | -0.33417 | -0.23804 | 0.004578 | -0.2243 | 0.045777 | 0.032043 | -0.27466 | -0.022888 | -0.27924 | -0.027466 | 0.19684 | 122.113 | 0.027465 | 121.9757 | 121.6003 | 121.7056 | 121.6736 | 121.7102 | -121.8613 | -121.9299 | 122.1863 | 121.9803 | 60.5988 | 60.6583
28.375 | 122.113 | -60.9924 | 61.0199 | -0.0016785 | 6.7325 | 0.066114 | 0.065783 | -7.2628e-05 | -0.0050457 | -0.0012988 | -0.00054933 | 0.0030868 | 0.070788 | 0.059774 | -0.0068403 | 0.013567 | -0.0020102 | -0.37079 | 60.7681 | -60.8917 | 61.171 | -60.7361 | -61.1389 | -61.2488 | -0.33417 | 60.8002 | -60.9512 | 60.9604 | -60.997 | -61.0519 | -61.29 | 0.10071 | -0.25177 | 0.15106 | 0.25635 | -0.25635 | -0.14648 | -0.35705 | -0.24719 | 0.041199 | -0.21973 | -0.059509 | -0.004577 | -0.29755 | -0.059509 | -0.33874 | -0.10071 | 0.15564 | 122.0627 | -0.045776 | 121.9116 | 121.6599 | 121.7514 | 121.7606 | 121.7926 | -121.9116 | -121.9711 | 122.1634 | 121.9528 | 60.6216 | 60.6583
30.0312 | 122.2183 | -61.0153 | 60.8963 | -0.0016785 | 6.7276 | 0.065473 | 0.067065 | 0.00185 | -0.0018415 | 0.00062377 | -0.00054933 | -0.0001174 | 0.069934 | 0.059133 | -0.0019269 | 0.01549 | -0.002651 | -0.44403 | 60.6857 | -60.9512 | 61.1481 | -60.791 | -61.2213 | -61.2991 | -0.33875 | 60.6949 | -61.0062 | 60.9924 | -60.9604 | -61.0382 | -61.2671 | 0.064087 | -0.21057 | 0.25177 | 0.2243 | -0.28381 | -0.20599 | -0.3479 | -0.27008 | 0.009155 | -0.20142 | 0.096131 | 0.054932 | -0.25177 | -0.022888 | -0.26093 | -0.032043 | 0.16022 | 122.0993 | 0.045777 | 121.9986 | 121.637 | 121.7011 | 121.7011 | 121.7102 | -121.8475 | -121.9025 | 122.1634 | 122.0078 | 60.5713 | 60.6766
31.7656 | 122.2183 | -61.0016 | 60.8871 | -0.0016785 | 6.7219 | 0.067182 | 0.062365 | 0.00078177 | -0.00055969 | -0.0025806 | 0.014709 | 0.002446 | 0.06737 | 0.064687 | -0.0012861 | 0.017412 | 0.0020486 | -0.38452 | 60.6171 | -60.91 | 61.2167 | -60.6674 | -61.1252 | -61.2122 | -0.23804 | 60.6628 | -61.0336 | 61.0199 | -60.9283 | -61.0062 | -61.2396 | 0.091553 | -0.27008 | 0.32959 | 0.33417 | -0.21057 | -0.1236 | -0.30212 | -0.21515 | -0.032043 | -0.2243 | 0.13275 | 0.073242 | -0.23804 | -0.004578 | -0.20599 | 0.027465 | 0.24262 | 122.1268 | 0.10529 | 122.0535 | 121.5271 | 121.6965 | 121.6187 | 121.6644 | -121.7972 | -121.9208 | 122.2183 | 122.0215 | 60.6171 | 60.7636
33.4844 | 122.1634 | -61.0062 | 60.9604 | 0.01358 | 6.7246 | 0.06825 | 0.066424 | 0.0020636 | -0.0031231 | 0.00083737 | 0.0055543 | 0.0003098 | 0.070788 | 0.062978 | -0.0064129 | 0.015703 | 0.0011942 | -0.33417 | 60.7269 | -60.9055 | 61.2259 | -60.6995 | -61.1526 | -61.2167 | -0.27466 | 60.7361 | -60.9833 | 60.997 | -60.9604 | -61.0519 | -61.29 | 0.10071 | -0.23346 | 0.2655 | 0.3067 | -0.21057 | -0.14648 | -0.31128 | -0.24719 | 0.022889 | -0.2243 | 0.036621 | 0.045777 | -0.28381 | -0.045776 | -0.3067 | -0.068665 | 0.20599 | 122.1313 | 0.022888 | 121.9803 | 121.6324 | 121.7194 | 121.7331 | 121.7422 | -121.8658 | -121.9437 | 122.2321 | 122.0032 | 60.672 | 60.7315
35.1562 | 122.113 | -61.0657 | 60.9375 | -0.009308 | 6.7229 | 0.067823 | 0.066638 | -0.004986 | -0.0026959 | -0.00044443 | -0.00054933 | 0.0022324 | 0.070361 | 0.055074 | -0.0034223 | 0.015063 | 0.0029032 | -0.4303 | 60.6949 | -60.9558 | 61.084 | -60.8551 | -61.2854 | -61.3449 | -0.41657 | 60.7086 | -61.0474 | 60.8963 | -61.0703 | -61.1572 | -61.3358 | 0.10986 | -0.24262 | 0.14648 | 0.21057 | -0.27924 | -0.21973 | -0.3891 | -0.32959 | 0.018311 | -0.22888 | -0.041199 | -0.004577 | -0.27008 | -0.091553 | -0.28839 | -0.10986 | 0.10071 | 122.0398 | -0.022888 | 121.9437 | 121.6507 | 121.756 | 121.7606 | 121.7743 | -121.8933 | -121.9849 | 122.1497 | 121.962 | 60.6354 | 60.6491
36.875 | 122.1359 | -61.0016 | 60.9833 | 0.02121 | 6.696 | 0.069746 | 0.06621 | 0.00185 | -0.00055969 | -0.0010852 | 0.014709 | 0.0011642 | 0.069507 | 0.055501 | -0.0055585 | 0.013781 | -0.003292 | -0.3479 | 60.7727 | -60.9055 | 61.1938 | -60.7315 | -61.1298 | -61.2213 | -0.31128 | 60.7956 | -60.9787 | 60.9741 | -60.9512 | -61.0382 | -61.2671 | 0.09613 | -0.21057 | 0.21057 | 0.27008 | -0.21973 | -0.12817 | -0.31586 | -0.2243 | 0.022888 | -0.18768 | -0.009155 | 0.050354 | -0.2655 | -0.036621 | -0.28839 | -0.059509 | 0.17395 | 122.0993 | 0.027466 | 121.9528 | 121.6782 | 121.7743 | 121.7743 | 121.7972 | -121.8887 | -121.962 | 122.1954 | 121.9757 | 60.6537 | 60.6903
38.5469 | 122.2183 | -60.9238 | 60.9741 | -0.009308 | 6.7152 | 0.068678 | 0.064288 | -0.00049983 | -0.0035505 | -0.0012988 | -0.0036011 | 0.0003098 | 0.070147 | 0.06191 | -0.0025677 | 0.016344 | -0.005001 | -0.32044 | 60.7132 | -60.8643 | 61.29 | -60.5942 | -61.0291 | -61.1435 | -0.17395 | 60.7224 | -60.9146 | 61.0703 | -60.8231 | -60.9055 | -61.1618 | 0.059509 | -0.26092 | 0.31586 | 0.32959 | -0.21973 | -0.10529 | -0.27924 | -0.16479 | 0.009155 | -0.25177 | 0.09613 | 0.10071 | -0.23804 | 0.01831 | -0.24719 | 0.009155 | 0.27008 | 122.1542 | 0.091553 | 121.9849 | 121.5775 | 121.637 | 121.637 | 121.6461 | -121.8384 | -121.8887 | 122.2137 | 121.994 | 60.6033 | 60.7498
40.2812 | 122.2275 | -60.9741 | 60.9741 | -0.016937 | 6.7199 | 0.066328 | 0.063433 | 0.00056817 | -0.0041913 | -0.0012988 | -0.0097045 | -0.000972 | 0.068866 | 0.062551 | -0.0053449 | 0.014208 | -0.0022238 | -0.30212 | 60.6949 | -60.8459 | 61.2991 | -60.5942 | -61.0336 | -61.1252 | -0.19684 | 60.7269 | -60.9238 | 61.0519 | -60.8505 | -60.9146 | -61.1755 | 0.12817 | -0.27924 | 0.32501 | 0.37994 | -0.15106 | -0.059509 | -0.27924 | -0.18768 | 0.050354 | -0.24719 | 0.07782 | 0.1236 | -0.20142 | 0.059509 | -0.25177 | 0.009155 | 0.25177 | 122.1451 | 0.073242 | 121.9757 | 121.5408 | 121.6507 | 121.669 | 121.701 | -121.8201 | -121.8979 | 122.2733 | 122.0261 | 60.672 | 60.7773
42 | 122.1909 | -60.997 | 60.9055 | 0.028839 | 6.7308 | 0.069532 | 0.065783 | 0.00078177 | -0.0022687 | -0.00087163 | 0.0086061 | 0.0013778 | 0.071216 | 0.059347 | -0.0010723 | 0.013994 | -0.0024374 | -0.39368 | 60.6491 | -60.9146 | 61.2122 | -60.6812 | -61.1389 | -61.2167 | -0.28839 | 60.6903 | -61.0016 | 60.9741 | -60.9604 | -61.0291 | -61.2762 | 0.082397 | -0.25635 | 0.3067 | 0.31586 | -0.21973 | -0.14191 | -0.30212 | -0.2243 | -0.004578 | -0.21515 | 0.068664 | 0.036621 | -0.27924 | -0.032044 | -0.27466 | -0.027466 | 0.23346 | 122.1268 | 0.041199 | 121.9757 | 121.5637 | 121.6919 | 121.6461 | 121.6873 | -121.8201 | -121.907 | 122.2092 | 121.9711 | 60.6033 | 60.7086
43.6562 | 122.2137 | -60.965 | 60.965 | 0.005951 | 6.708 | 0.066969 | 0.063647 | 0.00014097 | -0.0046185 | -0.002367 | 0.0025025 | 0.0003098 | 0.070361 | 0.061269 | -0.0032087 | 0.01549 | -8.7586e-05 | -0.39825 | 60.6857 | -60.8871 | 61.2076 | -60.6949 | -61.1252 | -61.1984 | -0.29755 | 60.6949 | -60.9558 | 61.0153 | -60.91 | -60.965 | -61.2213 | 0.07782 | -0.27924 | 0.24262 | 0.27008 | -0.23346 | -0.16022 | -0.31128 | -0.23804 | 0.009155 | -0.27008 | 0.050354 | 0.054932 | -0.25635 | 0 | -0.2655 | -0.009155 | 0.19226 | 122.0947 | 0.045777 | 121.9711 | 121.5729 | 121.6507 | 121.6507 | 121.6599 | -121.8521 | -121.9208 | 122.1725 | 121.9803 | 60.5667 | 60.6674
45.375 | 122.0901 | -60.965 | 61.0199 | -0.0016785 | 6.7135 | 0.06825 | 0.064929 | 0.00185 | -0.0035505 | -0.0032214 | -0.00054933 | 0.0011642 | 0.070788 | 0.058065 | -0.0057721 | 0.01549 | -0.0035056 | -0.37537 | 60.7452 | -60.8871 | 61.1893 | -60.7361 | -61.1389 | -61.2305 | -0.33417 | 60.7819 | -60.9512 | 60.9329 | -60.9741 | -61.0474 | -61.2717 | 0.07782 | -0.27466 | 0.16937 | 0.22888 | -0.2655 | -0.17395 | -0.34332 | -0.25177 | 0.013733 | -0.23804 | -0.086975 | -0.009155 | -0.3067 | -0.082397 | -0.32043 | -0.09613 | 0.15106 | 122.0764 | -0.022888 | 121.8842 | 121.6324 | 121.7331 | 121.7102 | 121.7468 | -121.907 | -121.9711 | 122.1542 | 121.8979 | 60.5896 | 60.6308
47.0312 | 122.2137 | -60.9283 | 60.9375 | -0.009308 | 6.718 | 0.068037 | 0.064288 | 0.0033454 | -0.0044049 | -0.0010852 | -0.00054933 | 0.0003098 | 0.069079 | 0.055929 | -0.0034223 | 0.014422 | -0.0041464 | -0.32044 | 60.6903 | -60.8322 | 61.2946 | -60.585 | -61.0153 | -61.1298 | -0.1831 | 60.7361 | -60.9375 | 61.0748 | -60.8368 | -60.9009 | -61.171 | 0.096131 | -0.24719 | 0.35706 | 0.34332 | -0.20142 | -0.086975 | -0.29755 | -0.18311 | -0.009155 | -0.20142 | 0.13733 | 0.091553 | -0.24261 | 0.027466 | -0.23346 | 0.036621 | 0.24719 | 122.1268 | 0.10071 | 122.0123 | 121.5225 | 121.6736 | 121.6187 | 121.6644 | -121.7697 | -121.875 | 122.2229 | 122.0032 | 60.6079 | 60.7452
48.75 | 122.168 | -60.9695 | 60.9375 | 0.005951 | 6.7054 | 0.070387 | 0.06322 | 0.0037726 | -0.0018415 | -0.0019396 | 0.0086061 | -0.0011856 | 0.068866 | 0.071737 | -0.0017133 | 0.013567 | -0.0037192 | -0.40741 | 60.6674 | -60.9146 | 61.1938 | -60.7086 | -61.1343 | -61.235 | -0.31586 | 60.704 | -60.9695 | 60.9604 | -60.9467 | -61.0336 | -61.2488 | 0.054931 | -0.27008 | 0.25635 | 0.26093 | -0.2655 | -0.16479 | -0.32043 | -0.21973 | 0 | -0.23346 | 0.022888 | 0.022888 | -0.27924 | -0.064087 | -0.27924 | -0.064087 | 0.20599 | 122.1085 | 0.022888 | 121.9299 | 121.582 | 121.6736 | 121.637 | 121.6736 | -121.8521 | -121.907 | 122.1634 | 121.9299 | 60.5621 | 60.6537
50.4219 | 122.0901 | -61.0291 | 60.9055 | -0.009308 | 6.7189 | 0.070814 | 0.06621 | -0.0022088 | -0.0046185 | -0.0021532 | -0.00054933 | 0.0056504 | 0.070361 | 0.062551 | -0.0038495 | 0.014208 | -0.002651 | -0.44403 | 60.704 | -60.91 | 61.0794 | -60.8551 | -61.2762 | -61.3358 | -0.4303 | 60.7086 | -61.0199 | 60.8871 | -61.0611 | -61.1435 | -61.3495 | 0.11902 | -0.20142 | 0.17395 | 0.17395 | -0.3067 | -0.24719 | -0.42572 | -0.36621 | 0.009156 | -0.19684 | -0.018311 | -0.032043 | -0.32043 | -0.11444 | -0.32959 | -0.1236 | 0.054931 | 121.9894 | -0.041199 | 121.907 | 121.6141 | 121.7285 | 121.7331 | 121.7377 | -121.8155 | -121.9254 | 122.1085 | 121.9162 | 60.585 | 60.5988
52.0938 | 122.1405 | -61.0245 | 60.8871 | -0.0016785 | 6.7014 | 0.065901 | 0.065783 | -0.0017816 | -0.0029095 | -0.001726 | -0.0036011 | 0.0022324 | 0.069507 | 0.058706 | -0.0027813 | 0.017412 | 0.00076681 | -0.44403 | 60.6903 | -60.9467 | 61.0931 | -60.8093 | -61.2488 | -61.3174 | -0.37994 | 60.6766 | -61.0382 | 60.9238 | -61.0382 | -61.1114 | -61.3174 | 0.07782 | -0.19684 | 0.20599 | 0.21515 | -0.29297 | -0.2243 | -0.37079 | -0.30212 | -0.013733 | -0.21057 | 0.036621 | -0.013733 | -0.29297 | -0.086975 | -0.27924 | -0.073242 | 0.13733 | 122.0398 | 0 | 121.962 | 121.637 | 121.7148 | 121.7148 | 121.7011 | -121.8338 | -121.9254 | 122.1176 | 121.9482 | 60.5804 | 60.6445
53.8281 | 122.1451 | -60.9741 | 60.9375 | 0.02121 | 6.7125 | 0.066328 | 0.067706 | 0.006336 | -0.0031231 | 0.0025464 | 0.0025025 | 0.0033004 | 0.070788 | 0.058706 | -0.0061993 | 0.015276 | -0.00072839 | -0.33417 | 60.7407 | -60.91 | 61.1984 | -60.6857 | -61.1206 | -61.2076 | -0.28381 | 60.7636 | -60.9741 | 60.9604 | -60.9558 | -61.0428 | -61.2534 | 0.064087 | -0.19684 | 0.26093 | 0.28839 | -0.23346 | -0.14648 | -0.29755 | -0.21057 | 0 | -0.17395 | 0.022888 | 0.01831 | -0.27924 | -0.068665 | -0.27924 | -0.068665 | 0.2243 | 122.1085 | 0.01831 | 121.9345 | 121.6507 | 121.7377 | 121.7148 | 121.7377 | -121.8475 | -121.9116 | 122.1725 | 121.9345 | 60.64 | 60.6903
55.4844 | 122.2092 | -60.9375 | 60.9375 | -0.009308 | 6.696 | 0.067823 | 0.062792 | -0.00071343 | -0.0063275 | -0.0015124 | -0.0036011 | -0.0007584 | 0.070575 | 0.064687 | -0.0034223 | 0.015063 | -0.0020102 | -0.40741 | 60.6766 | -60.878 | 61.2076 | -60.6857 | -61.1114 | -61.171 | -0.28839 | 60.6857 | -60.9375 | 61.0428 | -60.878 | -60.9421 | -61.1893 | 0.059509 | -0.26093 | 0.27008 | 0.25177 | -0.23346 | -0.17395 | -0.29297 | -0.23346 | 0 | -0.25177 | 0.10529 | 0.059509 | -0.25177 | -0.004578 | -0.25177 | -0.004578 | 0.19226 | 122.0856 | 0.059509 | 121.9803 | 121.5546 | 121.6232 | 121.6141 | 121.6232 | -121.8155 | -121.875 | 122.1451 | 121.9803 | 60.5301 | 60.6491
57.2031 | 122.1771 | -60.9879 | 60.9421 | 0.028839 | 6.6969 | 0.06761 | 0.065142 | -0.002636 | -0.0033369 | 0.0023328 | -0.00054933 | 0.0009506 | 0.071643 | 0.063619 | -0.0038495 | 0.015703 | -0.003292 | -0.39825 | 60.672 | -60.8734 | 61.1938 | -60.704 | -61.1435 | -61.2213 | -0.32044 | 60.6766 | -60.997 | 60.9879 | -60.9238 | -60.9924 | -61.2167 | 0.11444 | -0.27008 | 0.25177 | 0.28381 | -0.23346 | -0.15564 | -0.3479 | -0.27008 | -0.009155 | -0.2655 | 0.045776 | 0.064087 | -0.22888 | -0.004578 | -0.21973 | 0.004577 | 0.16937 | 122.0673 | 0.073242 | 121.9849 | 121.5454 | 121.6736 | 121.6599 | 121.6644 | -121.8155 | -121.9391 | 122.1817 | 121.9757 | 60.5896 | 60.6674
58.9219 | 122.0993 | -61.0336 | 60.9375 | -0.0016785 | 6.708 | 0.067823 | 0.064288 | 0.0024908 | -0.0054731 | -0.0019396 | -0.0036011 | 0.0030868 | 0.072497 | 0.065114 | -0.0038495 | 0.016344 | -0.0030784 | -0.44403 | 60.6766 | -60.9375 | 61.0794 | -60.8368 | -61.2671 | -61.3312 | -0.40741 | 60.6903 | -61.0245 | 60.8871 | -61.0565 | -61.1343 | -61.3266 | 0.09613 | -0.26093 | 0.14191 | 0.19684 | -0.29755 | -0.23346 | -0.39368 | -0.32959 | 0.009155 | -0.24719 | -0.050354 | -0.022889 | -0.29297 | -0.10071 | -0.30212 | -0.10986 | 0.10071 | 122.0169 | -0.032044 | 121.9116 | 121.6141 | 121.7148 | 121.7102 | 121.7239 | -121.875 | -121.962 | 122.113 | 121.9208 | 60.5896 | 60.6262
60.6562 | 122.1909 | -60.997 | 60.9009 | -0.009308 | 6.7105 | 0.067823 | 0.066851 | 0.0041998 | -0.0026959 | -0.002367 | -0.0036011 | 0.0009506 | 0.070147 | 0.061483 | -0.0021405 | 0.015917 | -0.00094199 | -0.43488 | 60.6583 | -60.91 | 61.1526 | -60.7452 | -61.1847 | -61.2717 | -0.32044 | 60.6445 | -61.0153 | 60.997 | -60.9421 | -61.0199 | -61.2396 | 0.086975 | -0.24262 | 0.25177 | 0.25177 | -0.27466 | -0.18768 | -0.36163 | -0.27466 | -0.018311 | -0.25635 | 0.09613 | 0.054931 | -0.24262 | -0.022888 | -0.2243 | -0.004577 | 0.1648 | 122.0627 | 0.073242 | 122.0123 | 121.5683 | 121.6599 | 121.6553 | 121.6415 | -121.8109 | -121.9162 | 122.1497 | 121.994 | 60.5621 | 60.6766
62.3281 | 122.0993 | -60.9741 | 60.9924 | -0.009308 | 6.6896 | 0.067396 | 0.065356 | 0.00078177 | -0.0044049 | 0.00019657 | 0.0086061 | 0.003514 | 0.071429 | 0.058278 | -0.0074811 | 0.012072 | -0.0030784 | -0.37079 | 60.7361 | -60.8643 | 61.1526 | -60.7407 | -61.1389 | -61.2122 | -0.33417 | 60.7773 | -60.9833 | 60.9467 | -60.9741 | -61.0382 | -61.2671 | 0.10986 | -0.25635 | 0.16022 | 0.23346 | -0.23804 | -0.1648 | -0.3479 | -0.27466 | -0.009155 | -0.21515 | -0.045777 | 0 | -0.29297 | -0.064087 | -0.28381 | -0.054932 | 0.1236 | 122.0169 | 0.009155 | 121.9299 | 121.6003 | 121.7606 | 121.7102 | 121.7514 | -121.8567 | -121.9757 | 122.1268 | 121.9208 | 60.6033 | 60.64
64.0469 | 122.168 | -60.9329 | 60.9558 | -0.0016785 | 6.6851 | 0.068464 | 0.063647 | 0.003559 | -0.0052595 | 0.00019657 | -0.00054933 | 0.0009506 | 0.071643 | 0.064687 | -0.0053449 | 0.014422 | -0.00094199 | -0.31128 | 60.7086 | -60.8276 | 61.2808 | -60.5942 | -61.0336 | -61.1206 | -0.20142 | 60.7132 | -60.9329 | 61.0474 | -60.8505 | -60.91 | -61.1801 | 0.10528 | -0.24719 | 0.32501 | 0.33874 | -0.18768 | -0.10071 | -0.29297 | -0.20599 | 0 | -0.24261 | 0.091552 | 0.082397 | -0.24719 | 0.022888 | -0.24719 | 0.022888 | 0.23346 | 122.1085 | 0.082397 | 121.9803 | 121.5363 | 121.6461 | 121.6415 | 121.6461 | -121.7834 | -121.8887 | 122.2137 | 121.9803 | 60.6216 | 60.7315
65.7969 | 122.0535 | -61.0016 | 60.9192 | -0.009308 | 6.6905 | 0.068037 | 0.065783 | -7.2628e-05 | -0.0033369 | 0.00019657 | -0.0036011 | 0.003514 | 0.068866 | 0.063405 | -0.0064129 | 0.013567 | -0.0024374 | -0.42114 | 60.6628 | -60.9421 | 61.0931 | -60.791 | -61.2442 | -61.3174 | -0.4303 | 60.7086 | -60.9924 | 60.8597 | -61.0657 | -61.1252 | -61.3174 | 0.059509 | -0.25635 | 0.17395 | 0.21057 | -0.31586 | -0.24262 | -0.37537 | -0.30212 | 0.009155 | -0.21057 | -0.059509 | -0.064087 | -0.31586 | -0.1236 | -0.32501 | -0.13275 | 0.15106 | 122.0352 | -0.073242 | 121.8521 | 121.6049 | 121.7011 | 121.6644 | 121.7102 | -121.8613 | -121.9116 | 122.0947 | 121.8613 | 60.5804 | 60.5713
67.4531 | 122.081 | -61.0016 | 60.9146 | -0.009308 | 6.6982 | 0.06761 | 0.064715 | 0.003559 | -0.0033369 | -0.001726 | -0.00054933 | 0.0037278 | 0.069079 | 0.064474 | -0.0027813 | 0.01549 | 0.00076681 | -0.37079 | 60.7269 | -60.8963 | 61.1618 | -60.7178 | -61.1664 | -61.2625 | -0.33875 | 60.6903 | -60.9787 | 60.9192 | -61.0107 | -61.0931 | -61.3174 | 0.10529 | -0.18768 | 0.24719 | 0.28381 | -0.26093 | -0.16479 | -0.36621 | -0.27008 | 0.022888 | -0.2243 | 0.004577 | -0.009155 | -0.31586 | -0.091553 | -0.33875 | -0.11444 | 0.17853 | 122.0581 | -0.032043 | 121.8979 | 121.6232 | 121.669 | 121.7285 | 121.6919 | -121.8109 | -121.8933 | 122.1634 | 121.9208 | 60.6308 | 60.6628
69.1719 | 122.2092 | -60.9283 | 60.9467 | -0.009308 | 6.6841 | 0.066328 | 0.064074 | -0.00028623 | -0.0031231 | -0.00087163 | -0.0066527 | 0.000737 | 0.071216 | 0.058919 | -0.0047039 | 0.014635 | -0.00072839 | -0.37994 | 60.6857 | -60.8688 | 61.2534 | -60.6216 | -61.0382 | -61.1343 | -0.24261 | 60.704 | -60.9467 | 61.0474 | -60.8597 | -60.9146 | -61.1572 | 0.05951 | -0.26093 | 0.3067 | 0.3067 | -0.20599 | -0.10986 | -0.2655 | -0.16937 | -0.01831 | -0.24261 | 0.10071 | 0.068665 | -0.22888 | 0.013733 | -0.21057 | 0.032043 | 0.24719 | 122.1222 | 0.086975 | 121.994 | 121.5546 | 121.6507 | 121.6141 | 121.6324 | -121.8155 | -121.8933 | 122.1817 | 121.9757 | 60.5484 | 60.6857
70.8906 | 122.0535 | -61.0336 | 60.9238 | -0.024567 | 6.6947 | 0.068464 | 0.063433 | -0.003277 | -0.0041913 | -0.00044443 | 0.0025025 | 0.0015914 | 0.071002 | 0.062551 | -0.0034223 | 0.014422 | -0.0035056 | -0.38452 | 60.6903 | -60.9238 | 61.1481 | -60.7636 | -61.203 | -61.29 | -0.37079 | 60.6903 | -60.9879 | 60.8871 | -61.0336 | -61.1114 | -61.3037 | 0.10986 | -0.23346 | 0.2243 | 0.27008 | -0.25635 | -0.16937 | -0.36621 | -0.27924 | 0.045776 | -0.23346 | -0.036621 | 0 | -0.27008 | -0.07782 | -0.31586 | -0.1236 | 0.16022 | 122.0718 | -0.045776 | 121.875 | 121.6141 | 121.6782 | 121.7239 | 121.7239 | -121.8475 | -121.9116 | 122.1817 | 121.9208 | 60.6491 | 60.6628
72.6094 | 122.0718 | -61.0474 | 60.9192 | -0.0016785 | 6.6885 | 0.069746 | 0.065783 | -0.00071343 | -0.0037641 | -0.0021532 | -0.00054933 | 0.0028732 | 0.070788 | 0.05721 | -0.0034223 | 0.016344 | -0.00094199 | -0.43945 | 60.6995 | -60.9055 | 61.0657 | -60.8597 | -61.2488 | -61.3449 | -0.42572 | 60.672 | -61.0107 | 60.8871 | -61.0428 | -61.1343 | -61.3312 | 0.14191 | -0.21973 | 0.14648 | 0.18768 | -0.29755 | -0.20142 | -0.43945 | -0.34332 | 0.036621 | -0.24719 | -0.032043 | 0.004577 | -0.28381 | -0.086975 | -0.32043 | -0.1236 | 0.045777 | 121.9711 | -0.032044 | 121.8979 | 121.6049 | 121.6827 | 121.7468 | 121.7194 | -121.8246 | -121.9299 | 122.113 | 121.9345 | 60.6079 | 60.6216
74.2656 | 122.1405 | -60.9833 | 60.91 | 0.01358 | 6.6913 | 0.067823 | 0.062365 | 0.0044134 | -0.0024823 | -0.0021532 | 0.0055543 | 0.000737 | 0.071643 | 0.063833 | -0.0032087 | 0.014422 | 0.0016214 | -0.42572 | 60.6766 | -60.9009 | 61.1801 | -60.6949 | -61.116 | -61.203 | -0.32959 | 60.6583 | -60.9741 | 60.9512 | -60.9558 | -61.0153 | -61.2305 | 0.082397 | -0.23346 | 0.27008 | 0.28839 | -0.21973 | -0.13275 | -0.30212 | -0.21515 | 0.009155 | -0.25177 | 0.041199 | 0.027465 | -0.24719 | -0.032044 | -0.25635 | -0.041199 | 0.20599 | 122.081 | 0.01831 | 121.9254 | 121.5775 | 121.6324 | 121.6599 | 121.6415 | -121.8109 | -121.8842 | 122.1634 | 121.9345 | 60.5576 | 60.6537
76 | 122.1909 | -60.8917 | 60.965 | -0.0016785 | 6.6956 | 0.067182 | 0.061511 | 0.00035457 | -0.0044049 | -0.0049304 | 0.0055543 | 0.0028732 | 0.071429 | 0.063833 | -0.0027813 | 0.015276 | -0.00436 | -0.32501 | 60.6583 | -60.8368 | 61.29 | -60.5942 | -61.0291 | -61.116 | -0.18768 | 60.6903 | -60.91 | 61.0519 | -60.8276 | -60.9055 | -61.1526 | 0.054932 | -0.3067 | 0.32501 | 0.29755 | -0.2243 | -0.13733 | -0.27924 | -0.19226 | -0.01831 | -0.27466 | 0.086975 | 0.064087 | -0.26092 | -0.013733 | -0.24261 | 0.004577 | 0.24262 | 122.1268 | 0.082397 | 121.962 | 121.4951 | 121.6003 | 121.55 | 121.582 | -121.8018 | -121.875 | 122.1817 | 121.9437 | 60.5667 | 60.704
77.7344 | 122.1863 | -60.9833 | 60.8231 | 0.005951 | 6.6964 | 0.06825 | 0.063647 | 0.0020636 | -0.0031231 | 0.00019657 | -0.00054933 | 0.0022324 | 0.07207 | 0.060415 | -0.0017133 | 0.017199 | -0.002651 | -0.43488 | 60.6308 | -60.9192 | 61.1526 | -60.7315 | -61.1572 | -61.2396 | -0.31586 | 60.6216 | -61.0153 | 61.0016 | -60.9329 | -61.0062 | -61.2213 | 0.064087 | -0.19226 | 0.32959 | 0.25177 | -0.25635 | -0.17395 | -0.32043 | -0.23804 | -0.032044 | -0.20142 | 0.17853 | 0.050354 | -0.23804 | -0.022889 | -0.20599 | 0.009155 | 0.18768 | 122.0718 | 0.082398 | 122.0169 | 121.55 | 121.637 | 121.6141 | 121.6049 | -121.7422 | -121.8384 | 122.1359 | 121.9849 | 60.5484 | 60.6674
79.3906 | 122.1817 | -61.0016 | 60.8688 | -0.0016785 | 6.6847 | 0.069319 | 0.06621 | -0.00092703 | -0.0063275 | -0.00087163 | -0.00054933 | 0.002446 | 0.071002 | 0.065969 | -0.0036359 | 0.016985 | 0.00098061 | -0.43488 | 60.6628 | -60.9375 | 61.1526 | -60.7498 | -61.1801 | -61.2625 | -0.32044 | 60.6354 | -61.0245 | 60.9695 | -60.9375 | -61.0016 | -61.2167 | 0.064087 | -0.20599 | 0.28381 | 0.25177 | -0.26093 | -0.17853 | -0.32501 | -0.24262 | -0.022888 | -0.23346 | 0.10071 | 0.064087 | -0.21515 | 0 | -0.19226 | 0.022888 | 0.18768 | 122.0901 | 0.086975 | 121.994 | 121.6003 | 121.6599 | 121.6644 | 121.637 | -121.8063 | -121.8933 | 122.1542 | 121.9711 | 60.5667 | 60.6812
81.0625 | 122.1451 | -60.9787 | 60.9283 | 0.005951 | 6.693 | 0.068678 | 0.064715 | -0.00092703 | -0.0052595 | -0.0019396 | 0.0055543 | 0.002446 | 0.070361 | 0.06191 | -0.0040631 | 0.01549 | -0.001583 | -0.40741 | 60.6628 | -60.8871 | 61.1664 | -60.6949 | -61.1252 | -61.2076 | -0.3479 | 60.6766 | -60.9695 | 60.965 | -60.9192 | -60.997 | -61.2213 | 0.091553 | -0.2655 | 0.23804 | 0.28381 | -0.22888 | -0.14648 | -0.32043 | -0.23804 | 0.009156 | -0.25177 | 0.036621 | 0.05951 | -0.24261 | -0.01831 | -0.25177 | -0.027466 | 0.19226 | 122.0535 | 0.050354 | 121.9345 | 121.55 | 121.6461 | 121.6415 | 121.6553 | -121.8155 | -121.8979 | 122.1451 | 121.9437 | 60.5713 | 60.6308
82.7812 | 122.1909 | -60.997 | 60.8688 | -0.009308 | 6.6836 | 0.06825 | 0.065142 | 0.0027044 | -0.0035505 | -0.0012988 | -0.00054933 | 0.0011642 | 0.070147 | 0.06661 | 0.00042289 | 0.017412 | -0.0028646 | -0.37994 | 60.6216 | -60.8917 | 61.1801 | -60.672 | -61.1298 | -61.2259 | -0.29297 | 60.6262 | -61.0016 | 60.9787 | -60.9283 | -60.997 | -61.2167 | 0.10528 | -0.24719 | 0.31128 | 0.32501 | -0.22888 | -0.13275 | -0.33417 | -0.23804 | -0.004578 | -0.24261 | 0.10986 | 0.068664 | -0.21973 | 0 | -0.21515 | 0.004578 | 0.21973 | 122.0718 | 0.073242 | 121.9803 | 121.5134 | 121.6278 | 121.6187 | 121.6232 | -121.7606 | -121.8704 | 122.1771 | 121.9757 | 60.6171 | 60.704
84.4375 | 122.1588 | -60.9375 | 60.9375 | 0.02121 | 6.674 | 0.067823 | 0.062365 | -0.0022088 | -0.0039777 | -0.0027942 | -0.00054933 | 0.0020188 | 0.06972 | 0.06191 | -0.0047039 | 0.015063 | 0.00012601 | -0.41199 | 60.6903 | -60.9238 | 61.1664 | -60.6949 | -61.1114 | -61.1938 | -0.32959 | 60.6949 | -60.9558 | 60.9741 | -60.9055 | -60.9741 | -61.2122 | 0.013733 | -0.24719 | 0.22888 | 0.24262 | -0.25635 | -0.17395 | -0.27008 | -0.18768 | -0.018311 | -0.24262 | 0.036621 | 0.032043 | -0.27466 | -0.036621 | -0.25635 | -0.01831 | 0.22888 | 122.0901 | 0.050354 | 121.9299 | 121.6141 | 121.6507 | 121.6278 | 121.6324 | -121.8613 | -121.8933 | 122.1039 | 121.9116 | 60.5255 | 60.6079
86.1562 | 122.1954 | -60.9009 | 60.9283 | 0.005951 | 6.6586 | 0.068464 | 0.064501 | -0.0056268 | -0.0052595 | -0.00044443 | -0.0036011 | 0.002446 | 0.069293 | 0.058065 | -0.0085491 | 0.01549 | -0.00072839 | -0.34332 | 60.6628 | -60.8597 | 61.2717 | -60.5667 | -61.0153 | -61.1069 | -0.16022 | 60.7086 | -60.9146 | 61.0428 | -60.8139 | -60.8871 | -61.1618 | 0.041199 | -0.2655 | 0.34332 | 0.33417 | -0.20599 | -0.11444 | -0.24719 | -0.15564 | -0.013733 | -0.21973 | 0.11444 | 0.086975 | -0.26092 | 0.013733 | -0.24719 | 0.027466 | 0.29297 | 122.1313 | 0.10071 | 121.9574 | 121.5225 | 121.6232 | 121.5637 | 121.6095 | -121.788 | -121.843 | 122.1725 | 121.9437 | 60.5576 | 60.7407
87.875 | 122.0947 | -61.0428 | 60.878 | -0.009308 | 6.658 | 0.066755 | 0.066851 | 0.0029182 | -0.0048321 | -1.7026e-05 | -0.00054933 | 0.000737 | 0.071216 | 0.06426 | -0.0027813 | 0.016558 | -0.005001 | -0.46234 | 60.6812 | -60.9283 | 61.0794 | -60.7864 | -61.2213 | -61.2946 | -0.41199 | 60.672 | -61.0336 | 60.8917 | -61.0245 | -61.1023 | -61.2946 | 0.11444 | -0.19684 | 0.20142 | 0.25635 | -0.25177 | -0.17853 | -0.36621 | -0.29297 | 0.009156 | -0.20599 | 0.013733 | 0.018311 | -0.25177 | -0.059509 | -0.26093 | -0.068665 | 0.14191 | 122.0078 | 0.009155 | 121.9254 | 121.6095 | 121.7056 | 121.7239 | 121.7148 | -121.8063 | -121.9116 | 122.1222 | 121.9345 | 60.5804 | 60.6308
89.5469 | 122.168 | -61.0016 | 60.8826 | -0.009308 | 6.6714 | 0.066541 | 0.06621 | 0.00014097 | -0.0039777 | -0.00065803 | -0.00054933 | 0.0028732 | 0.069507 | 0.058492 | -0.0032087 | 0.015917 | -0.0022238 | -0.46234 | 60.6583 | -60.9146 | 61.116 | -60.7452 | -61.1847 | -61.2671 | -0.36163 | 60.64 | -61.0107 | 60.9558 | -60.9375 | -61.0199 | -61.235 | 0.086975 | -0.2243 | 0.23346 | 0.25635 | -0.2655 | -0.1831 | -0.35248 | -0.27008 | -0.009155 | -0.24261 | 0.073243 | 0.064087 | -0.23346 | -0.01831 | -0.2243 | -0.009155 | 0.16937 | 122.0306 | 0.073242 | 121.9666 | 121.5729 | 121.6507 | 121.6599 | 121.6415 | -121.7972 | -121.8933 | 122.1176 | 121.9574 | 60.5392 | 60.64
91.2812 | 122.1542 | -60.9924 | 60.8505 | -0.009308 | 6.6492 | 0.068464 | 0.065783 | -0.0013544 | -0.0022687 | -0.0027942 | 0.014709 | 0.0022324 | 0.072711 | 0.061269 | -0.0034223 | 0.016131 | 0.00033961 | -0.41199 | 60.6445 | -60.9329 | 61.2213 | -60.6308 | -61.0886 | -61.1847 | -0.26093 | 60.6354 | -61.0062 | 60.9741 | -60.9146 | -60.9879 | -61.2213 | 0.05951 | -0.20599 | 0.37079 | 0.36163 | -0.19226 | -0.09613 | -0.25177 | -0.15564 | -0.013733 | -0.21515 | 0.1236 | 0.07782 | -0.22888 | 0.004578 | -0.21515 | 0.018311 | 0.30212 | 122.1542 | 0.091553 | 121.9803 | 121.5775 | 121.6415 | 121.637 | 121.6278 | -121.7834 | -121.8567 | 122.2137 | 121.9666 | 60.5804 | 60.7315
93 | 122.0718 | -61.0016 | 60.9055 | -0.009308 | 6.6588 | 0.068464 | 0.066851 | -0.00028623 | -0.0054731 | -0.00087163 | -0.00054933 | 0.002446 | 0.072497 | 0.058278 | -0.0064129 | 0.014208 | 0.0022622 | -0.39368 | 60.6949 | -60.91 | 61.1343 | -60.7361 | -61.1801 | -61.2625 | -0.36163 | 60.704 | -60.9924 | 60.878 | -61.0062 | -61.0977 | -61.2991 | 0.091553 | -0.21057 | 0.22888 | 0.2655 | -0.26093 | -0.17853 | -0.35248 | -0.27008 | 0.009155 | -0.20142 | -0.027466 | -0.004578 | -0.29755 | -0.09613 | -0.3067 | -0.10529 | 0.17395 | 122.0444 | -0.013733 | 121.8704 | 121.6049 | 121.6965 | 121.6965 | 121.7056 | -121.8155 | -121.8979 | 122.1359 | 121.8796 | 60.6079 | 60.64
94.7188 | 122.1725 | -60.9787 | 60.8597 | 0.005951 | 6.6505 | 0.068678 | 0.065142 | 0.0031318 | -0.0035505 | -1.7026e-05 | -0.00054933 | 0.002446 | 0.070788 | 0.065114 | -0.0057721 | 0.016772 | -0.0028646 | -0.44861 | 60.6216 | -60.91 | 61.1298 | -60.7224 | -61.1664 | -61.2534 | -0.32044 | 60.6537 | -60.9924 | 60.9604 | -60.9375 | -61.0016 | -61.2305 | 0.068665 | -0.23804 | 0.27008 | 0.25635 | -0.27466 | -0.18768 | -0.34332 | -0.25635 | -0.013733 | -0.20599 | 0.10071 | 0.041199 | -0.25177 | -0.022888 | -0.23804 | -0.009155 | 0.18768 | 122.0398 | 0.054932 | 121.9528 | 121.5317 | 121.6461 | 121.6003 | 121.6324 | -121.7697 | -121.8521 | 122.1085 | 121.9391 | 60.5301 | 60.6583
96.3906 | 122.0444 | -60.9695 | 60.965 | -0.0016785 | 6.6578 | 0.067823 | 0.067065 | -7.2628e-05 | -0.0061139 | -0.0025806 | 0.0025025 | 0.003514 | 0.071002 | 0.068319 | -0.0057721 | 0.01314 | -0.00030119 | -0.38452 | 60.7773 | -60.8597 | 61.1435 | -60.7178 | -61.1298 | -61.2076 | -0.37537 | 60.7498 | -60.9604 | 60.9146 | -60.9604 | -61.0153 | -61.235 | 0.10986 | -0.18768 | 0.17853 | 0.25177 | -0.23804 | -0.16022 | -0.3479 | -0.27008 | 0.009155 | -0.21515 | -0.050354 | 0.009155 | -0.2655 | -0.045777 | -0.27466 | -0.054932 | 0.14191 | 122.0032 | 0 | 121.875 | 121.637 | 121.7102 | 121.7468 | 121.7194 | -121.8246 | -121.9254 | 122.113 | 121.8842 | 60.585 | 60.5942
98.1094 | 122.0901 | -60.9787 | 60.9238 | 0.02121 | 6.6514 | 0.069746 | 0.068347 | 0.0022772 | -0.0035505 | -0.00065803 | 0.0055543 | 0.0033004 | 0.068866 | 0.055074 | -0.0051313 | 0.013781 | 0.0016214 | -0.36163 | 60.7407 | -60.8963 | 61.1801 | -60.6812 | -61.0931 | -61.1847 | -0.28381 | 60.7269 | -60.965 | 60.9512 | -60.91 | -61.0062 | -61.203 | 0.082398 | -0.1831 | 0.25635 | 0.29755 | -0.20599 | -0.11444 | -0.28839 | -0.19684 | 0.013733 | -0.19684 | 0.027466 | 0.068665 | -0.2243 | -0.027466 | -0.23804 | -0.041199 | 0.21515 | 122.0764 | 0.054932 | 121.9162 | 121.637 | 121.6919 | 121.7194 | 121.7056 | -121.8201 | -121.8887 | 122.1588 | 121.9299 | 60.6171 | 60.6949
99.8281 | 122.0947 | -60.9558 | 60.9375 | 0.02121 | 6.6454 | 0.068464 | 0.064288 | 0.0024908 | -0.0035505 | -0.0010852 | 0.0025025 | 0.0003098 | 0.070575 | 0.056783 | -0.0051313 | 0.013781 | -0.0022238 | -0.35706 | 60.6857 | -60.8871 | 61.1801 | -60.6583 | -61.1298 | -61.203 | -0.28839 | 60.6995 | -60.9787 | 60.9512 | -60.9192 | -61.0016 | -61.2167 | 0.068665 | -0.25177 | 0.24262 | 0.29755 | -0.24719 | -0.17395 | -0.31586 | -0.24262 | -0.022888 | -0.23804 | 0.013733 | 0.036622 | -0.26093 | -0.045776 | -0.23804 | -0.022888 | 0.22888 | 122.0673 | 0.05951 | 121.9299 | 121.5729 | 121.6782 | 121.6415 | 121.6553 | -121.8246 | -121.9162 | 122.1359 | 121.907 | 60.5988 | 60.6674
101.5 | 122.0901 | -60.9741 | 60.9695 | 0.02121 | 6.6435 | 0.066969 | 0.064288 | -7.2628e-05 | -0.00077329 | 0.0019056 | 0.011658 | 0.0022324 | 0.072497 | 0.057851 | -0.0051313 | 0.015063 | -0.001583 | -0.35706 | 60.7452 | -60.8871 | 61.171 | -60.6812 | -61.0794 | -61.1984 | -0.32959 | 60.7498 | -60.9833 | 60.9421 | -60.9329 | -61.0062 | -61.2167 | 0.086975 | -0.2243 | 0.20142 | 0.29297 | -0.2243 | -0.10529 | -0.31128 | -0.19226 | -0.009155 | -0.21973 | -0.027465 | 0.041199 | -0.24262 | -0.032044 | -0.23346 | -0.022889 | 0.20599 | 122.0581 | 0.050354 | 121.9254 | 121.6324 | 121.7331 | 121.7194 | 121.7239 | -121.8567 | -121.9528 | 122.1451 | 121.9162 | 60.6171 | 60.6445
103.2031 | 122.0901 | -60.9741 | 60.91 | 0.028839 | 6.6475 | 0.067823 | 0.062579 | 0.0037726 | -0.0052595 | 0.00019657 | 0.011658 | -0.0003312 | 0.070788 | 0.062337 | -0.00021791 | 0.015063 | -0.00051479 | -0.43488 | 60.6445 | -60.8643 | 61.1618 | -60.6903 | -61.1298 | -61.1938 | -0.33875 | 60.6537 | -60.9558 | 60.9467 | -60.9238 | -60.9924 | -61.2122 | 0.10986 | -0.2655 | 0.25177 | 0.28381 | -0.21973 | -0.15564 | -0.32959 | -0.2655 | 0.01831 | -0.25635 | 0.036621 | 0.050354 | -0.23804 | -0.018311 | -0.25635 | -0.036621 | 0.17395 | 122.0261 | 0.032044 | 121.9025 | 121.5088 | 121.6095 | 121.6187 | 121.6278 | -121.7743 | -121.8658 | 122.1359 | 121.9208 | 60.5392 | 60.6354
104.9219 | 122.1725 | -60.9879 | 60.8459 | -0.0016785 | 6.63 | 0.069319 | 0.065569 | 0.00014097 | -0.0050457 | -0.00044443 | -0.0036011 | 0.0026596 | 0.070147 | 0.05956 | -0.0019269 | 0.01549 | -0.0062826 | -0.44403 | 60.64 | -60.9055 | 61.1343 | -60.7269 | -61.1435 | -61.2396 | -0.32959 | 60.6079 | -61.0016 | 60.9604 | -60.9238 | -61.0062 | -61.2076 | 0.082397 | -0.20599 | 0.28839 | 0.26093 | -0.25177 | -0.15564 | -0.33417 | -0.23804 | -0.013733 | -0.23804 | 0.11444 | 0.064087 | -0.21973 | -0.018311 | -0.20599 | -0.004578 | 0.17853 | 122.0398 | 0.07782 | 121.962 | 121.5454 | 121.6095 | 121.6278 | 121.5958 | -121.7514 | -121.8475 | 122.1222 | 121.9482 | 60.5438 | 60.6583
106.6562 | 122.1725 | -60.9192 | 60.9238 | -0.0016785 | 6.623 | 0.065901 | 0.062792 | -0.0034906 | -0.0018415 | -0.0019396 | -0.0036011 | 0.0009506 | 0.06972 | 0.062551 | -0.0032087 | 0.015917 | -0.003292 | -0.33875 | 60.6445 | -60.8322 | 61.2762 | -60.5438 | -60.997 | -61.084 | -0.20599 | 60.6857 | -60.9009 | 61.0199 | -60.7956 | -60.8551 | -61.1343 | 0.086975 | -0.27924 | 0.35248 | 0.37537 | -0.16479 | -0.07782 | -0.25177 | -0.16479 | 0.01831 | -0.23804 | 0.09613 | 0.1236 | -0.21515 | 0.064086 | -0.23346 | 0.045776 | 0.28839 | 122.1085 | 0.10529 | 121.9208 | 121.4767 | 121.5866 | 121.5637 | 121.6049 | -121.756 | -121.8246 | 122.1954 | 121.9391 | 60.5804 | 60.7132
108.3906 | 122.1359 | -60.9055 | 60.9238 | -0.0016785 | 6.6221 | 0.068678 | 0.06322 | -0.00028623 | -0.0052595 | 0.00019657 | -0.0066527 | -0.0005448 | 0.067798 | 0.058919 | -0.0051313 | 0.013781 | -0.0024374 | -0.32501 | 60.6628 | -60.8459 | 61.2534 | -60.5896 | -61.0062 | -61.1114 | -0.21973 | 60.6995 | -60.9009 | 61.0245 | -60.8139 | -60.9055 | -61.1435 | 0.05951 | -0.26093 | 0.32959 | 0.31586 | -0.20599 | -0.10071 | -0.2655 | -0.16022 | 0.004578 | -0.2243 | 0.10071 | 0.091553 | -0.23804 | 0 | -0.24261 | -0.004578 | 0.25635 | 122.0993 | 0.086975 | 121.9254 | 121.5088 | 121.6003 | 121.5683 | 121.6049 | -121.7697 | -121.8246 | 122.1588 | 121.9299 | 60.5804 | 60.6857
110.0469 | 122.081 | -60.9421 | 60.9695 | 0.005951 | 6.6225 | 0.067396 | 0.065783 | -0.0017816 | -0.0048321 | 0.00083737 | -0.00054933 | 0.000737 | 0.069507 | 0.066823 | -0.0055585 | 0.015703 | -0.00094199 | -0.33875 | 60.6812 | -60.8231 | 61.2442 | -60.6079 | -61.0291 | -61.1114 | -0.2655 | 60.7224 | -60.9055 | 60.9741 | -60.8826 | -60.9512 | -61.1938 | 0.11902 | -0.28839 | 0.27466 | 0.33417 | -0.16937 | -0.086975 | -0.28839 | -0.20599 | 0.036621 | -0.24719 | 0.004578 | 0.05951 | -0.25177 | -0.009155 | -0.28839 | -0.045776 | 0.21515 | 122.0673 | 0.022889 | 121.8796 | 121.5042 | 121.6278 | 121.6232 | 121.6644 | -121.7926 | -121.875 | 122.1863 | 121.9162 | 60.6033 | 60.6766
111.7812 | 122.1359 | -60.9512 | 60.8643 | 0.005951 | 6.614 | 0.067823 | 0.064715 | 0.00078177 | -0.0031231 | -1.7026e-05 | -0.00054933 | -0.0001174 | 0.069934 | 0.06191 | -0.00021791 | 0.015917 | -0.00436 | -0.42114 | 60.5896 | -60.8734 | 61.1801 | -60.6491 | -61.1114 | -61.1893 | -0.28381 | 60.6216 | -60.9879 | 60.9787 | -60.8871 | -60.9741 | -61.2076 | 0.07782 | -0.27466 | 0.31586 | 0.30212 | -0.23804 | -0.16022 | -0.31586 | -0.23804 | -0.036621 | -0.24262 | 0.11444 | 0.064087 | -0.25635 | -0.022888 | -0.21973 | 0.013733 | 0.2243 | 122.0535 | 0.10071 | 121.9666 | 121.463 | 121.6095 | 121.5408 | 121.5729 | -121.7377 | -121.8521 | 122.1313 | 121.9299 | 60.5301 | 60.6674
113.4531 | 122.1634 | -60.9192 | 60.9146 | -0.016937 | 6.5845 | 0.066114 | 0.063006 | -0.0039178 | -0.0061139 | -0.0010852 | 0.0025025 | 0.0018052 | 0.06737 | 0.06661 | -0.0042767 | 0.01549 | -0.0041464 | -0.3891 | 60.6583 | -60.8505 | 61.2167 | -60.6171 | -61.0153 | -61.1114 | -0.25177 | 60.6949 | -60.9146 | 61.0474 | -60.8185 | -60.8963 | -61.1481 | 0.068664 | -0.25635 | 0.30212 | 0.30212 | -0.19226 | -0.096131 | -0.26093 | -0.1648 | 0.004577 | -0.21973 | 0.13275 | 0.10071 | -0.22888 | 0.022888 | -0.23346 | 0.018311 | 0.23346 | 122.0673 | 0.096131 | 121.962 | 121.5088 | 121.6095 | 121.5775 | 121.6141 | -121.7651 | -121.8292 | 122.1359 | 121.9666 | 60.5301 | 60.6674
115.1719 | 122.049 | -60.997 | 60.8734 | -0.0016785 | 6.6082 | 0.066755 | 0.065997 | 0.0048408 | -0.0076093 | -0.00065803 | -0.0036011 | 0.002446 | 0.068652 | 0.062337 | -0.0027813 | 0.01549 | 0.00012601 | -0.47607 | 60.6583 | -60.91 | 61.0611 | -60.7956 | -61.2122 | -61.2762 | -0.42114 | 60.6674 | -60.9695 | 60.878 | -61.0153 | -61.0977 | -61.29 | 0.086975 | -0.21515 | 0.18768 | 0.20142 | -0.27924 | -0.21515 | -0.36621 | -0.30212 | 0.027466 | -0.20599 | 0.004578 | -0.018311 | -0.29297 | -0.10071 | -0.32043 | -0.12817 | 0.11444 | 121.9711 | -0.045777 | 121.8475 | 121.5683 | 121.637 | 121.6553 | 121.6644 | -121.7834 | -121.843 | 122.0581 | 121.875 | 60.5209 | 60.5759
116.8906 | 122.1085 | -60.9558 | 60.9329 | 0.02121 | 6.592 | 0.067182 | 0.064288 | 0.00035457 | -0.0046185 | -0.001726 | 0.0025025 | 0.002446 | 0.070788 | 0.067892 | -0.0017133 | 0.014635 | -0.0017966 | -0.41199 | 60.6583 | -60.8643 | 61.1572 | -60.672 | -61.1023 | -61.1755 | -0.35248 | 60.6674 | -60.9787 | 60.9421 | -60.91 | -60.9695 | -61.2305 | 0.091553 | -0.27466 | 0.22431 | 0.28381 | -0.21973 | -0.14648 | -0.31128 | -0.23804 | -0.022888 | -0.2655 | 0.009156 | 0.045777 | -0.27466 | -0.013732 | -0.25177 | 0.009156 | 0.19226 | 122.0215 | 0.068665 | 121.9208 | 121.5225 | 121.6461 | 121.6141 | 121.6232 | -121.7972 | -121.9116 | 122.113 | 121.8979 | 60.5438 | 60.6033
118.6094 | 122.0993 | -60.9467 | 60.8871 | 0.02121 | 6.6076 | 0.063978 | 0.065356 | 0.0039862 | -0.0029095 | -0.003435 | 0.0055543 | 0.0030868 | 0.069507 | 0.061696 | -0.0036359 | 0.016558 | 0.00055321 | -0.41657 | 60.6445 | -60.878 | 61.1664 | -60.672 | -61.116 | -61.1893 | -0.3479 | 60.672 | -60.9604 | 60.9375 | -60.9238 | -60.9879 | -61.2259 | 0.068664 | -0.24262 | 0.27924 | 0.27466 | -0.24262 | -0.16937 | -0.31128 | -0.23804 | -0.013733 | -0.21515 | 0.050354 | 0.022888 | -0.27924 | -0.041199 | -0.2655 | -0.027466 | 0.20599 | 122.0444 | 0.036621 | 121.8979 | 121.5225 | 121.6324 | 121.5912 | 121.6187 | -121.7651 | -121.8475 | 122.113 | 121.8842 | 60.5301 | 60.5988
120.2656 | 122.0261 | -60.9192 | 60.9512 | -0.0016785 | 6.6063 | 0.066755 | 0.064074 | -0.00049983 | -0.0063275 | 0.001692 | -0.0036011 | 0.002446 | 0.071856 | 0.056997 | -0.0051313 | 0.014849 | -0.002651 | -0.39368 | 60.7224 | -60.8643 | 61.1481 | -60.6949 | -61.116 | -61.2076 | -0.36621 | 60.7544 | -60.9146 | 60.9146 | -60.9329 | -61.0062 | -61.2259 | 0.054931 | -0.22888 | 0.19684 | 0.2243 | -0.28839 | -0.19684 | -0.34332 | -0.25177 | 0.004577 | -0.19684 | -0.036621 | -0.013733 | -0.3067 | -0.086976 | -0.31128 | -0.091553 | 0.16937 | 122.0123 | -0.01831 | 121.8292 | 121.5866 | 121.669 | 121.6415 | 121.6736 | -121.8155 | -121.8658 | 122.0673 | 121.8338 | 60.5255 | 60.553
121.9219 | 122.1085 | -60.9558 | 60.8688 | 0.036468 | 6.5877 | 0.070173 | 0.065142 | 0.00099557 | -0.0016279 | -0.00065803 | 0.011658 | 0.0005234 | 0.068438 | 0.068746 | -0.0034223 | 0.015276 | -0.001583 | -0.40741 | 60.6445 | -60.9238 | 61.1801 | -60.64 | -61.1206 | -61.1847 | -0.29755 | 60.64 | -60.9741 | 60.9467 | -60.9238 | -60.9741 | -61.2122 | 0.032044 | -0.2243 | 0.31128 | 0.31586 | -0.22888 | -0.16479 | -0.26093 | -0.19684 | -0.01831 | -0.22888 | 0.07782 | 0.032044 | -0.25635 | -0.01831 | -0.23804 | 0 | 0.28381 | 122.1039 | 0.050354 | 121.9208 | 121.5683 | 121.6141 | 121.6003 | 121.5958 | -121.7926 | -121.843 | 122.1359 | 121.9025 | 60.5484 | 60.6583
123.6406 | 122.1313 | -60.9375 | 60.9238 | 0.005951 | 6.5815 | 0.068464 | 0.064929 | 0.0014228 | -0.0050457 | -0.00065803 | -0.00054933 | -0.0016128 | 0.068225 | 0.061483 | -0.0021405 | 0.01549 | 0.0024758 | -0.40741 | 60.6445 | -60.8734 | 61.1664 | -60.6628 | -61.1023 | -61.171 | -0.30212 | 60.6674 | -60.9238 | 61.0016 | -60.8459 | -60.9283 | -61.171 | 0.064087 | -0.27924 | 0.24262 | 0.27466 | -0.23346 | -0.16479 | -0.29755 | -0.22888 | 0.013733 | -0.25635 | 0.07782 | 0.091553 | -0.23346 | 0.009155 | -0.24719 | -0.004578 | 0.21057 | 122.0398 | 0.07782 | 121.9254 | 121.5179 | 121.5912 | 121.582 | 121.6049 | -121.7972 | -121.8475 | 122.1039 | 121.9391 | 60.5301 | 60.6354
125.2969 | 122.1634 | -60.9924 | 60.8231 | -0.009308 | 6.5982 | 0.069105 | 0.06621 | 0.0074042 | -0.0026959 | -1.7026e-05 | -0.00054933 | 0.0011642 | 0.070147 | 0.05956 | -0.0040631 | 0.01848 | -0.0024374 | -0.41657 | 60.6033 | -60.8917 | 61.171 | -60.672 | -61.1298 | -61.2076 | -0.3067 | 60.6079 | -60.9879 | 60.9741 | -60.9009 | -60.9787 | -61.1984 | 0.10071 | -0.21973 | 0.3479 | 0.32044 | -0.21515 | -0.13733 | -0.31586 | -0.23804 | 0.004578 | -0.21515 | 0.15106 | 0.091553 | -0.20599 | 0.013733 | -0.21057 | 0.009155 | 0.21973 | 122.0627 | 0.086975 | 121.962 | 121.4951 | 121.5958 | 121.5958 | 121.6003 | -121.7148 | -121.8109 | 122.1634 | 121.9666 | 60.5759 | 60.6857
127.0312 | 122.1634 | -60.8826 | 60.9329 | -0.0016785 | 6.571 | 0.066541 | 0.065783 | -0.00049983 | -0.0063275 | -0.0012988 | -0.0036011 | 9.6204e-05 | 0.069293 | 0.063192 | -0.0051313 | 0.015063 | 0.00076681 | -0.36163 | 60.6583 | -60.8414 | 61.2396 | -60.5713 | -61.0107 | -61.084 | -0.19684 | 60.6812 | -60.9329 | 61.0382 | -60.8093 | -60.8643 | -61.1252 | 0.041198 | -0.27466 | 0.3067 | 0.31128 | -0.20142 | -0.12817 | -0.24261 | -0.16937 | -0.050354 | -0.25177 | 0.10529 | 0.073242 | -0.24262 | 0.01831 | -0.19226 | 0.068664 | 0.27008 | 122.081 | 0.1236 | 121.9711 | 121.4996 | 121.6141 | 121.5408 | 121.5637 | -121.7743 | -121.8658 | 122.1222 | 121.9208 | 60.5209 | 60.6857
128.7656 | 122.1497 | -60.9558 | 60.8322 | -0.0016785 | 6.5854 | 0.068464 | 0.065356 | -0.00071343 | -0.0039777 | -0.00044443 | -0.00054933 | -0.0003312 | 0.067157 | 0.060628 | -0.0040631 | 0.016772 | -0.0045736 | -0.40741 | 60.5804 | -60.8917 | 61.1755 | -60.6537 | -61.1252 | -61.1938 | -0.28381 | 60.6033 | -60.9787 | 60.965 | -60.8826 | -60.9512 | -61.1847 | 0.064087 | -0.25177 | 0.34332 | 0.30212 | -0.23804 | -0.16937 | -0.30212 | -0.23346 | -0.022888 | -0.22888 | 0.13275 | 0.073243 | -0.22888 | 0.004578 | -0.20599 | 0.027466 | 0.23804 | 122.0673 | 0.096131 | 121.9437 | 121.4722 | 121.582 | 121.5363 | 121.5591 | -121.7239 | -121.8109 | 122.1313 | 121.9208 | 60.5484 | 60.672
130.4375 | 122.1451 | -60.9238 | 60.8826 | -0.0016785 | 6.5725 | 0.066541 | 0.063647 | 0.00056817 | -0.0061139 | 0.00083737 | 0.0025025 | 0.0026596 | 0.068011 | 0.058065 | -0.0055585 | 0.015276 | -0.0011558 | -0.42114 | 60.64 | -60.8826 | 61.1526 | -60.672 | -61.0794 | -61.171 | -0.31128 | 60.6537 | -60.9421 | 60.965 | -60.8734 | -60.9421 | -61.171 | 0.041199 | -0.24261 | 0.27008 | 0.25177 | -0.24719 | -0.15564 | -0.28839 | -0.19684 | -0.018311 | -0.22888 | 0.082398 | 0.050354 | -0.24719 | -0.018311 | -0.22888 | 0 | 0.21057 | 122.0352 | 0.068665 | 121.907 | 121.5225 | 121.5958 | 121.5637 | 121.5775 | -121.7651 | -121.8246 | 122.0764 | 121.8887 | 60.5026 | 60.6125
132.1719 | 122.1268 | -60.9192 | 60.8917 | -0.0016785 | 6.5723 | 0.067396 | 0.063433 | 0.0024908 | -0.0033369 | -0.0012988 | -0.00054933 | 0.0011642 | 0.069507 | 0.061483 | -0.0021405 | 0.015703 | 0.0026896 | -0.39825 | 60.6491 | -60.8597 | 61.1984 | -60.64 | -61.0611 | -61.1343 | -0.27008 | 60.6766 | -60.9146 | 61.0016 | -60.8322 | -60.8963 | -61.1343 | 0.059509 | -0.24262 | 0.3067 | 0.27923 | -0.21515 | -0.14191 | -0.27466 | -0.20142 | 0.004577 | -0.21515 | 0.10986 | 0.086975 | -0.21515 | 0.022888 | -0.21973 | 0.018311 | 0.21973 | 122.0581 | 0.082398 | 121.9162 | 121.5088 | 121.5912 | 121.5683 | 121.5958 | -121.7514 | -121.8063 | 122.1176 | 121.9208 | 60.5209 | 60.6491
133.8906 | 122.0856 | -60.9375 | 60.8871 | 0.01358 | 6.5358 | 0.06825 | 0.06386 | 0.0012092 | -0.0029095 | -0.0019396 | 0.0055543 | 0.0013778 | 0.069934 | 0.063405 | -0.0051313 | 0.016558 | -0.00030119 | -0.41199 | 60.6445 | -60.9009 | 61.1389 | -60.6857 | -61.1069 | -61.1801 | -0.36621 | 60.6308 | -60.9512 | 60.9375 | -60.9146 | -60.9695 | -61.1801 | 0.036621 | -0.24262 | 0.25177 | 0.25177 | -0.24262 | -0.16937 | -0.27924 | -0.20599 | -0.013733 | -0.25635 | 0.050354 | 0.022888 | -0.24262 | -0.032043 | -0.22888 | -0.01831 | 0.21515 | 122.0398 | 0.036621 | 121.8887 | 121.5454 | 121.582 | 121.582 | 121.5683 | -121.788 | -121.8384 | 122.0764 | 121.875 | 60.5255 | 60.5713
135.5625 | 122.0261 | -61.0062 | 60.8917 | -0.0016785 | 6.536 | 0.068678 | 0.068133 | -0.0022088 | -0.0037641 | -0.0010852 | -0.00054933 | 0.0028732 | 0.068652 | 0.062978 | -0.0029949 | 0.013994 | -0.0017966 | -0.45776 | 60.672 | -60.91 | 61.0428 | -60.8322 | -61.2396 | -61.2991 | -0.45319 | 60.6674 | -60.9833 | 60.8414 | -61.0474 | -61.1069 | -61.2854 | 0.096131 | -0.21973 | 0.15106 | 0.17395 | -0.29297 | -0.23346 | -0.3891 | -0.32959 | 0.022889 | -0.22431 | -0.050354 | -0.041198 | -0.27923 | -0.10071 | -0.30212 | -0.1236 | 0.07782 | 121.9528 | -0.064087 | 121.8246 | 121.582 | 121.6507 | 121.6782 | 121.6736 | -121.8018 | -121.875 | 122.049 | 121.8475 | 60.5484 | 60.553
137.2969 | 121.9986 | -60.9833 | 60.8597 | -0.0016785 | 6.5347 | 0.069319 | 0.066424 | -0.001568 | -0.0029095 | -0.001726 | 0.0025025 | 0.0026596 | 0.068866 | 0.056356 | -0.0042767 | 0.013994 | -0.0028646 | -0.45319 | 60.6812 | -60.8963 | 61.0336 | -60.7956 | -61.2167 | -61.3083 | -0.47607 | 60.6812 | -61.0016 | 60.8414 | -61.0474 | -61.1069 | -61.29 | 0.086975 | -0.17853 | 0.17395 | 0.18768 | -0.32501 | -0.23346 | -0.41199 | -0.32043 | -0.018311 | -0.17853 | -0.01831 | -0.064087 | -0.3067 | -0.1236 | -0.28839 | -0.10529 | 0.10071 | 121.9299 | -0.045776 | 121.843 | 121.5775 | 121.6827 | 121.6644 | 121.6644 | -121.756 | -121.8613 | 122.0169 | 121.8246 | 60.5301 | 60.5072
139.0156 | 122.0306 | -60.9283 | 60.9512 | 0.005951 | 6.5132 | 0.066755 | 0.064288 | -0.0037042 | -0.0048321 | -0.00023063 | -0.0036011 | 0.0022324 | 0.066516 | 0.054647 | -0.0068403 | 0.01549 | 0.00012601 | -0.35248 | 60.6766 | -60.8093 | 61.1984 | -60.64 | -61.0565 | -61.1481 | -0.31586 | 60.7132 | -60.9283 | 60.9375 | -60.9146 | -60.9741 | -61.203 | 0.11902 | -0.27466 | 0.24719 | 0.28839 | -0.21973 | -0.12817 | -0.33875 | -0.24719 | 0 | -0.23804 | -0.013733 | 0.013733 | -0.27466 | -0.045776 | -0.27466 | -0.045776 | 0.16937 | 122.0078 | 0.013733 | 121.8658 | 121.4859 | 121.6415 | 121.6049 | 121.6415 | -121.7606 | -121.8796 | 122.1268 | 121.8658 | 60.5759 | 60.6125
140.75 | 122.0123 | -60.9879 | 60.8871 | -0.009308 | 6.5038 | 0.067182 | 0.066424 | 0.0014228 | -0.0026959 | -0.001726 | -0.0036011 | 0.0033004 | 0.070788 | 0.062978 | -0.0051313 | 0.01549 | -0.0030784 | -0.4715 | 60.672 | -60.9192 | 61.0336 | -60.7819 | -61.2259 | -61.2717 | -0.4303 | 60.6445 | -60.9879 | 60.8597 | -61.0107 | -61.084 | -61.2717 | 0.068665 | -0.21515 | 0.14648 | 0.20599 | -0.28381 | -0.23804 | -0.35248 | -0.3067 | 0 | -0.24262 | -0.027466 | -0.022888 | -0.28381 | -0.09613 | -0.28381 | -0.09613 | 0.13733 | 121.9528 | -0.022888 | 121.8475 | 121.5912 | 121.6324 | 121.6599 | 121.6324 | -121.8063 | -121.875 | 122.0215 | 121.8475 | 60.5164 | 60.5576
142.4219 | 122.0718 | -60.9192 | 60.9238 | 0.02121 | 6.5305 | 0.067823 | 0.065783 | 0.00014097 | -0.0033369 | -0.00065803 | 0.0055543 | 9.6204e-05 | 0.069079 | 0.062337 | -0.0049175 | 0.015063 | -0.0022238 | -0.36163 | 60.7224 | -60.8734 | 61.1572 | -60.6857 | -61.0748 | -61.1801 | -0.30212 | 60.7224 | -60.9421 | 60.9329 | -60.91 | -60.9879 | -61.1893 | 0.045776 | -0.20142 | 0.23346 | 0.23346 | -0.26093 | -0.15564 | -0.3067 | -0.20142 | -0.022889 | -0.20142 | 0.009155 | 0.009155 | -0.27008 | -0.068665 | -0.24719 | -0.045776 | 0.18768 | 122.0306 | 0.032044 | 121.875 | 121.5958 | 121.6644 | 121.6415 | 121.6415 | -121.7972 | -121.8658 | 122.0764 | 121.8521 | 60.5576 | 60.6171
144.1406 | 122.1451 | -60.9283 | 60.8826 | -0.009308 | 6.4873 | 0.067396 | 0.063647 | -0.0039178 | -0.0065411 | -0.001726 | -0.00054933 | 0.0003098 | 0.066943 | 0.06191 | -0.0027813 | 0.017412 | -0.0022238 | -0.37994 | 60.6445 | -60.8368 | 61.2122 | -60.5759 | -61.0107 | -61.0886 | -0.24719 | 60.6812 | -60.8963 | 61.0062 | -60.8185 | -60.8688 | -61.1252 | 0.091553 | -0.23804 | 0.32959 | 0.35248 | -0.16022 | -0.082397 | -0.25177 | -0.17395 | 0.032044 | -0.20142 | 0.1236 | 0.10986 | -0.19684 | 0.05951 | -0.22888 | 0.027466 | 0.26093 | 122.049 | 0.07782 | 121.9025 | 121.4813 | 121.5775 | 121.5729 | 121.6095 | -121.7194 | -121.7789 | 122.1405 | 121.9345 | 60.5484 | 60.6812
145.875 | 122.0627 | -61.0153 | 60.8414 | -0.0016785 | 6.5134 | 0.068037 | 0.067706 | 0.00014097 | -0.0033369 | -0.0032214 | -0.0036011 | 0.0009506 | 0.068011 | 0.05956 | -0.0029949 | 0.013994 | -0.001583 | -0.46234 | 60.6674 | -60.9192 | 61.0565 | -60.7773 | -61.2167 | -61.2717 | -0.40741 | 60.6216 | -60.9879 | 60.8826 | -60.9924 | -61.0519 | -61.2488 | 0.096131 | -0.17395 | 0.21515 | 0.23804 | -0.25635 | -0.20142 | -0.35248 | -0.29755 | 0.027466 | -0.21973 | 0.041198 | 0.022888 | -0.23346 | -0.036621 | -0.26093 | -0.064087 | 0.14191 | 121.9757 | -0.004578 | 121.8704 | 121.5866 | 121.6095 | 121.6827 | 121.637 | -121.7606 | -121.8292 | 122.0718 | 121.8979 | 60.553 | 60.6079
147.5469 | 122.0627 | -60.9375 | 60.9055 | 0.02121 | 6.4307 | 0.069105 | 0.065569 | -0.00071343 | -0.0041913 | -0.00023063 | -0.00054933 | 0.0013778 | 0.071002 | 0.053152 | -0.0066265 | 0.013781 | -0.0020102 | -0.3479 | 60.672 | -60.8826 | 61.1435 | -60.6628 | -61.0886 | -61.1847 | -0.29755 | 60.6949 | -60.9604 | 60.9421 | -60.9055 | -60.9833 | -61.2076 | 0.054932 | -0.23346 | 0.23804 | 0.27466 | -0.24719 | -0.15106 | -0.30212 | -0.20599 | -0.022888 | -0.21057 | 0.036621 | 0.032043 | -0.27008 | -0.045776 | -0.24719 | -0.022888 | 0.21973 | 122.0261 | 0.054931 | 121.9025 | 121.5546 | 121.6553 | 121.6095 | 121.6324 | -121.788 | -121.8658 | 122.081 | 121.8796 | 60.5896 | 60.64
149.2656 | 122.1222 | -60.9512 | 60.8551 | 0.005951 | 6.4982 | 0.069319 | 0.064715 | 0.0016364 | -0.0044049 | -0.00087163 | -0.0036011 | 0.000737 | 0.06972 | 0.063619 | -0.0029949 | 0.019335 | -0.003292 | -0.42114 | 60.6033 | -60.8643 | 61.1481 | -60.6354 | -61.1114 | -61.1801 | -0.29755 | 60.5942 | -60.9741 | 60.965 | -60.8688 | -60.9604 | -61.1755 | 0.086975 | -0.25177 | 0.29297 | 0.31586 | -0.22888 | -0.16022 | -0.31586 | -0.24719 | -0.022888 | -0.26093 | 0.10986 | 0.082398 | -0.2243 | -0.009155 | -0.20142 | 0.013733 | 0.22888 | 122.0123 | 0.10529 | 121.9391 | 121.4676 | 121.5683 | 121.5546 | 121.5454 | -121.7194 | -121.8292 | 122.0993 | 121.9162 | 60.5301 | 60.6537
151 | 122.0581 | -60.9558 | 60.9238 | 0.01358 | 6.4568 | 0.06825 | 0.064715 | 0.00035457 | -0.0020551 | 0.00019657 | 0.0086061 | 0.0020188 | 0.068225 | 0.054006 | -0.0049175 | 0.014208 | -0.0017966 | -0.34332 | 60.7407 | -60.8688 | 61.1435 | -60.6766 | -61.0931 | -61.1755 | -0.31128 | 60.6995 | -60.9421 | 60.9375 | -60.9055 | -60.9833 | -61.1801 | 0.086976 | -0.1831 | 0.21973 | 0.27924 | -0.21973 | -0.13733 | -0.3067 | -0.22431 | 0.013733 | -0.2243 | 0.013733 | 0.050354 | -0.2243 | -0.027465 | -0.23804 | -0.041198 | 0.19226 | 122.0123 | 0.036621 | 121.8796 | 121.6095 | 121.6415 | 121.6965 | 121.6553 | -121.7926 | -121.8658 | 122.0993 | 121.8933 | 60.6125 | 60.6445
152.7344 | 122.1405 | -60.8917 | 60.9055 | -0.009308 | 6.4409 | 0.069105 | 0.065569 | 0.0016364 | -0.0076093 | -0.00044443 | 0.0025025 | 0.0011642 | 0.06737 | 0.06191 | -0.0029949 | 0.016772 | -0.00051479 | -0.38452 | 60.6308 | -60.8414 | 61.2122 | -60.5759 | -61.0062 | -61.0931 | -0.23346 | 60.6628 | -60.8917 | 61.0153 | -60.8093 | -60.8734 | -61.1069 | 0.050354 | -0.27466 | 0.3067 | 0.31586 | -0.20142 | -0.11444 | -0.25177 | -0.1648 | 0 | -0.24262 | 0.10986 | 0.082398 | -0.21515 | 0.018311 | -0.21515 | 0.018311 | 0.2655 | 122.0535 | 0.082398 | 121.907 | 121.4722 | 121.5546 | 121.5225 | 121.5546 | -121.7468 | -121.7972 | 122.1039 | 121.907 | 60.5072 | 60.6583
154.3906 | 122.0901 | -60.9055 | 60.9283 | -0.009308 | 6.4341 | 0.067823 | 0.06322 | 0.0024908 | -0.0044049 | 0.001051 | -0.0036011 | 0.0039414 | 0.067157 | 0.060842 | -0.0042767 | 0.017626 | -0.00436 | -0.31586 | 60.6491 | -60.8139 | 61.2305 | -60.5576 | -60.9924 | -61.0886 | -0.23804 | 60.6766 | -60.8688 | 61.0016 | -60.8093 | -60.8688 | -61.1298 | 0.091553 | -0.27924 | 0.30212 | 0.3479 | -0.18311 | -0.086975 | -0.27466 | -0.17853 | 0.036622 | -0.25177 | 0.073242 | 0.096131 | -0.2243 | 0.036622 | -0.26093 | 0 | 0.25635 | 122.0444 | 0.059509 | 121.8704 | 121.463 | 121.5454 | 121.5546 | 121.582 | -121.7422 | -121.7972 | 122.1359 | 121.907 | 60.5896 | 60.6674
156.125 | 122.0627 | -60.9421 | 60.8963 | 0.02121 | 6.4358 | 0.067823 | 0.06322 | -0.0028498 | -0.0031231 | -1.7026e-05 | 0.0086061 | 0.0015914 | 0.067798 | 0.064046 | -0.0055585 | 0.015917 | -0.00436 | -0.42114 | 60.6537 | -60.8459 | 61.1435 | -60.6537 | -61.0886 | -61.1572 | -0.35248 | 60.6354 | -60.9329 | 60.9238 | -60.91 | -60.9741 | -61.1984 | 0.096131 | -0.24261 | 0.24719 | 0.28839 | -0.21515 | -0.14648 | -0.31128 | -0.24262 | 0.009156 | -0.26093 | 0.027466 | 0.032044 | -0.25635 | -0.032043 | -0.2655 | -0.041199 | 0.19226 | 121.9894 | 0.022888 | 121.8567 | 121.4996 | 121.5683 | 121.5958 | 121.5775 | -121.7422 | -121.8292 | 122.0856 | 121.8658 | 60.5209 | 60.5896
157.8594 | 122.0215 | -60.965 | 60.8505 | -0.009308 | 6.4593 | 0.06825 | 0.067278 | -0.0028498 | -0.0020551 | -0.002367 | -0.0066527 | 0.0015914 | 0.069079 | 0.070028 | -0.0036359 | 0.015276 | -0.0035056 | -0.47607 | 60.6674 | -60.9192 | 61.0428 | -60.7819 | -61.2213 | -61.2671 | -0.42114 | 60.6628 | -60.9741 | 60.8597 | -61.0107 | -61.0703 | -61.2534 | 0.045777 | -0.18311 | 0.19226 | 0.18311 | -0.30212 | -0.25635 | -0.3479 | -0.30212 | -0.009155 | -0.18768 | 0.009155 | -0.045776 | -0.28839 | -0.10529 | -0.27924 | -0.09613 | 0.13733 | 121.962 | -0.036621 | 121.8338 | 121.5866 | 121.637 | 121.6324 | 121.6278 | -121.7697 | -121.8246 | 122.0078 | 121.8246 | 60.4889 | 60.5438
159.5156 | 122.113 | -60.965 | 60.8276 | -0.009308 | 6.4856 | 0.068891 | 0.065356 | 0.0050544 | -0.0050457 | -0.00087163 | -0.0036011 | 0.0020188 | 0.068011 | 0.058706 | -0.0029949 | 0.016772 | -0.0011558 | -0.47607 | 60.6445 | -60.9238 | 61.0703 | -60.7269 | -61.1801 | -61.2442 | -0.36163 | 60.6445 | -60.9695 | 60.9192 | -60.9009 | -61.0062 | -61.1984 | 0.041199 | -0.18311 | 0.24261 | 0.23804 | -0.27924 | -0.21515 | -0.32044 | -0.25635 | -0.004577 | -0.18311 | 0.091552 | 0.064087 | -0.23346 | -0.041199 | -0.22888 | -0.036622 | 0.19684 | 121.994 | 0.068664 | 121.8887 | 121.5683 | 121.6141 | 121.6095 | 121.6095 | -121.7514 | -121.7972 | 122.0352 | 121.8842 | 60.4889 | 60.6033
161.2344 | 122.0306 | -60.9375 | 60.9009 | 0.02121 | 6.4493 | 0.068037 | 0.066851 | -0.00049983 | -0.0052595 | -0.00065803 | 0.0086061 | 0.0037278 | 0.069934 | 0.058706 | -0.0057721 | 0.013994 | -0.0037192 | -0.37079 | 60.6995 | -60.8917 | 61.1481 | -60.6537 | -61.084 | -61.1664 | -0.29755 | 60.704 | -60.9146 | 60.9329 | -60.8917 | -60.9787 | -61.203 | 0.045776 | -0.20142 | 0.24719 | 0.28381 | -0.22888 | -0.14648 | -0.27466 | -0.19226 | 0.022888 | -0.19684 | 0.032043 | 0.045776 | -0.2655 | -0.041199 | -0.28839 | -0.064087 | 0.23804 | 122.0398 | 0.022888 | 121.8475 | 121.5912 | 121.6187 | 121.637 | 121.6415 | -121.7926 | -121.8155 | 122.0856 | 121.8704 | 60.5667 | 60.64
162.9531 | 122.0215 | -60.9375 | 60.9512 | 0.036468 | 6.451 | 0.06761 | 0.065356 | -0.00028623 | -0.0035505 | 0.001692 | 0.0055543 | 0.0037278 | 0.067798 | 0.063833 | -0.0053449 | 0.015703 | -0.002651 | -0.37994 | 60.7407 | -60.8551 | 61.1206 | -60.6903 | -61.1023 | -61.1801 | -0.35248 | 60.7315 | -60.9421 | 60.9192 | -60.91 | -60.965 | -61.1984 | 0.082397 | -0.21057 | 0.16937 | 0.24719 | -0.24262 | -0.16479 | -0.32501 | -0.24719 | -0.004578 | -0.21973 | -0.032044 | 0.027466 | -0.26093 | -0.027466 | -0.25635 | -0.022888 | 0.16479 | 121.9757 | 0.032044 | 121.8613 | 121.5958 | 121.6736 | 121.6782 | 121.669 | -121.8063 | -121.8933 | 122.0581 | 121.8567 | 60.5576 | 60.585
164.6719 | 122.049 | -60.9146 | 60.9238 | 0.028839 | 6.4294 | 0.069319 | 0.064074 | 0.003559 | -0.0059003 | -0.00044443 | 0.0055543 | 0.004155 | 0.068652 | 0.061056 | -0.0057721 | 0.014208 | -0.001583 | -0.35706 | 60.7086 | -60.8734 | 61.1343 | -60.6583 | -61.0748 | -61.1801 | -0.31586 | 60.704 | -60.9238 | 60.9283 | -60.9009 | -60.9741 | -61.1801 | 0.041199 | -0.21515 | 0.21057 | 0.25635 | -0.2655 | -0.16022 | -0.3067 | -0.20142 | -0.009155 | -0.21973 | 0.004578 | 0.013733 | -0.2655 | -0.059509 | -0.25635 | -0.050354 | 0.21515 | 122.0078 | 0.022888 | 121.8521 | 121.582 | 121.6278 | 121.6232 | 121.6187 | -121.7972 | -121.8475 | 122.0489 | 121.843 | 60.5576 | 60.5988
166.4219 | 122.0444 | -60.9329 | 60.9238 | 0.044098 | 6.4221 | 0.068678 | 0.064929 | 0.00099557 | -0.0041913 | 0.00041017 | 0.011658 | 0.0020188 | 0.068011 | 0.057638 | -0.0038495 | 0.016344 | -0.0017966 | -0.36621 | 60.7224 | -60.8597 | 61.1343 | -60.6628 | -61.0703 | -61.1572 | -0.34332 | 60.7498 | -60.9375 | 60.9238 | -60.8963 | -60.9695 | -61.171 | 0.073242 | -0.20142 | 0.21057 | 0.27008 | -0.22431 | -0.13733 | -0.29755 | -0.21057 | -0.004578 | -0.17395 | 0 | 0.036621 | -0.23804 | -0.036621 | -0.23346 | -0.032043 | 0.19684 | 121.994 | 0.041199 | 121.8613 | 121.582 | 121.6873 | 121.6553 | 121.6827 | -121.7834 | -121.8613 | 122.0673 | 121.8567 | 60.5667 | 60.5896
168.1406 | 122.0947 | -60.9604 | 60.8459 | -0.009308 | 6.4315 | 0.068464 | 0.064501 | 0.003559 | -0.0050457 | -0.0015124 | -0.00054933 | 0.0022324 | 0.068866 | 0.05721 | -0.0042767 | 0.015063 | -0.001583 | -0.4715 | 60.6308 | -60.8963 | 61.0657 | -60.7315 | -61.1847 | -61.2488 | -0.37994 | 60.6125 | -60.9604 | 60.9146 | -60.9329 | -60.9879 | -61.203 | 0.064087 | -0.21515 | 0.21973 | 0.22888 | -0.28839 | -0.2243 | -0.35248 | -0.28839 | 0 | -0.23346 | 0.068665 | 0.027466 | -0.24262 | -0.027466 | -0.24262 | -0.027466 | 0.16479 | 121.962 | 0.027466 | 121.875 | 121.5271 | 121.5729 | 121.5912 | 121.5729 | -121.7422 | -121.8063 | 122.0261 | 121.875 | 60.4889 | 60.5804
169.7969 | 122.113 | -60.965 | 60.8139 | -0.009308 | 6.3754 | 0.068678 | 0.061938 | -0.0011408 | -0.0052595 | -0.0012988 | -0.0036011 | 0.000737 | 0.069079 | 0.055929 | -4.308e-06 | 0.017199 | -0.0020102 | -0.40741 | 60.5576 | -60.8734 | 61.1298 | -60.6308 | -61.1069 | -61.1664 | -0.28839 | 60.5667 | -60.9421 | 60.9558 | -60.8597 | -60.9375 | -61.1664 | 0.091553 | -0.25635 | 0.31586 | 0.33417 | -0.20142 | -0.14191 | -0.29297 | -0.23346 | 0.022888 | -0.24719 | 0.14191 | 0.10529 | -0.20142 | 0.027466 | -0.2243 | 0.004578 | 0.24262 | 122.0032 | 0.082398 | 121.8979 | 121.431 | 121.5088 | 121.5225 | 121.5317 | -121.6873 | -121.756 | 122.0947 | 121.9208 | 60.5576 | 60.6766
171.4531 | 122.1222 | -60.9055 | 60.8963 | -0.0016785 | 6.3732 | 0.066969 | 0.064501 | 0.0044134 | -0.0061139 | -0.0012988 | -0.0066527 | 9.6204e-05 | 0.069079 | 0.062765 | -0.0040631 | 0.015276 | -0.002651 | -0.36163 | 60.6628 | -60.8139 | 61.2167 | -60.5621 | -60.9833 | -61.0703 | -0.21515 | 60.6491 | -60.8917 | 61.0245 | -60.8002 | -60.8459 | -61.0748 | 0.091553 | -0.23346 | 0.32043 | 0.34332 | -0.16479 | -0.077819 | -0.25635 | -0.16937 | 0.013733 | -0.24719 | 0.12817 | 0.10529 | -0.16937 | 0.05951 | -0.1831 | 0.045777 | 0.25177 | 122.0306 | 0.091553 | 121.9162 | 121.4767 | 121.5408 | 121.5683 | 121.5546 | -121.7102 | -121.788 | 122.1222 | 121.9299 | 60.5438 | 60.6903
173.125 | 122.1039 | -60.8734 | 60.8871 | -0.0016785 | 6.3531 | 0.069746 | 0.064501 | -0.0013544 | -0.0056867 | -0.0030078 | -0.0066527 | 0.0011642 | 0.065234 | 0.067892 | -0.0047039 | 0.01549 | -0.005001 | -0.32959 | 60.6583 | -60.8231 | 61.2396 | -60.5209 | -60.9741 | -61.0703 | -0.20599 | 60.6583 | -60.8688 | 61.0199 | -60.7681 | -60.8459 | -61.1069 | 0.050354 | -0.22888 | 0.35248 | 0.35248 | -0.19684 | -0.10071 | -0.24719 | -0.15106 | 0.004578 | -0.22888 | 0.13275 | 0.10529 | -0.23346 | 0.027466 | -0.23804 | 0.022888 | 0.30212 | 122.0627 | 0.10071 | 121.8887 | 121.4813 | 121.5271 | 121.5317 | 121.5317 | -121.7102 | -121.756 | 122.113 | 121.8933 | 60.5438 | 60.6674
174.7969 | 122.1039 | -60.8597 | 60.8871 | -0.009308 | 6.3651 | 0.066114 | 0.062365 | 0.0024908 | -0.0039777 | -0.0027942 | -0.0036011 | 0.0011642 | 0.06737 | 0.058492 | -0.0049175 | 0.016985 | 0.0014078 | -0.32501 | 60.6537 | -60.8139 | 61.235 | -60.5209 | -60.9787 | -61.0611 | -0.20142 | 60.6628 | -60.8734 | 61.0291 | -60.7819 | -60.8414 | -61.084 | 0.045776 | -0.23346 | 0.3479 | 0.33874 | -0.20142 | -0.11902 | -0.24719 | -0.16479 | -0.013733 | -0.2243 | 0.14191 | 0.07782 | -0.2243 | 0.01831 | -0.21057 | 0.032043 | 0.29297 | 122.0489 | 0.091553 | 121.9025 | 121.4676 | 121.5363 | 121.5134 | 121.5225 | -121.7011 | -121.7606 | 122.0947 | 121.8887 | 60.5347 | 60.6583
176.4844 | 121.9849 | -60.9055 | 60.965 | -0.009308 | 6.3972 | 0.067182 | 0.065569 | -0.0017816 | -0.0048321 | 0.00062377 | -0.00054933 | 0.002446 | 0.068652 | 0.065755 | -0.0061993 | 0.015276 | 0.0014078 | -0.38452 | 60.7269 | -60.8276 | 61.1023 | -60.6857 | -61.0794 | -61.1664 | -0.36621 | 60.7407 | -60.9146 | 60.8917 | -60.9375 | -61.0016 | -61.203 | 0.07782 | -0.23804 | 0.13733 | 0.21973 | -0.26093 | -0.17395 | -0.33874 | -0.25177 | -0.009155 | -0.2243 | -0.073242 | -0.032043 | -0.29755 | -0.09613 | -0.28839 | -0.086975 | 0.14191 | 121.9299 | -0.022888 | 121.8063 | 121.5546 | 121.6553 | 121.6324 | 121.6461 | -121.7926 | -121.8796 | 122.0078 | 121.7972 | 60.5209 | 60.5392
178.25 | 122.0673 | -60.8734 | 60.9238 | -0.0016785 | 6.3561 | 0.069319 | 0.062365 | -0.00049983 | -0.0063275 | -0.00023063 | 0.0025025 | 0.002446 | 0.067584 | 0.067464 | -0.0029949 | 0.016558 | -0.0024374 | -0.33417 | 60.6445 | -60.7819 | 61.2213 | -60.5347 | -60.9604 | -61.084 | -0.24261 | 60.6583 | -60.8963 | 60.9924 | -60.8002 | -60.8597 | -61.1023 | 0.091553 | -0.27924 | 0.29755 | 0.33874 | -0.21057 | -0.086975 | -0.30212 | -0.17853 | -0.022888 | -0.2655 | 0.068665 | 0.073242 | -0.22888 | 0.013733 | -0.20599 | 0.036621 | 0.24719 | 122.0032 | 0.09613 | 121.8887 | 121.4264 | 121.5546 | 121.5179 | 121.5317 | -121.7056 | -121.8201 | 122.0947 | 121.8658 | 60.5392 | 60.6308
179.9219 | 121.9711 | -60.9421 | 60.878 | -0.0016785 | 6.3064 | 0.068037 | 0.066851 | 0.0016364 | -0.0041913 | -0.0032214 | 0.0025025 | 0.0022324 | 0.069507 | 0.061056 | -0.0051313 | 0.014635 | -8.7586e-05 | -0.37537 | 60.6354 | -60.8688 | 61.0977 | -60.704 | -61.1252 | -61.2167 | -0.36163 | 60.6583 | -60.9421 | 60.8826 | -60.9695 | -61.0611 | -61.2305 | 0.073243 | -0.24262 | 0.21973 | 0.23804 | -0.27466 | -0.1831 | -0.3479 | -0.25635 | 0 | -0.21973 | 0.004577 | -0.027465 | -0.28839 | -0.11902 | -0.28839 | -0.11902 | 0.16479 | 121.9666 | -0.027465 | 121.8246 | 121.5042 | 121.6003 | 121.5775 | 121.6003 | -121.7468 | -121.8201 | 122.0398 | 121.8246 | 60.5667 | 60.5804
181.6094 | 122.0993 | -60.9329 | 60.8231 | -0.009308 | 6.364 | 0.068464 | 0.065142 | -0.001568 | -0.0031231 | -0.0038622 | 0.011658 | 0.0013778 | 0.06972 | 0.060201 | 0.00020929 | 0.018908 | -0.003292 | -0.41657 | 60.5759 | -60.8368 | 61.1343 | -60.6262 | -61.0886 | -61.1664 | -0.2655 | 60.6033 | -60.9787 | 60.9467 | -60.8734 | -60.9512 | -61.1618 | 0.09613 | -0.24719 | 0.31128 | 0.3067 | -0.23346 | -0.15564 | -0.32959 | -0.25177 | -0.045777 | -0.21973 | 0.1236 | 0.059509 | -0.22888 | -0.018311 | -0.1831 | 0.027466 | 0.21057 | 121.9711 | 0.10529 | 121.9254 | 121.4127 | 121.582 | 121.5088 | 121.5363 | -121.6599 | -121.8018 | 122.0673 | 121.8796 | 60.5164 | 60.6674
183.2812 | 122.113 | -60.9009 | 60.91 | 0.005951 | 6.3354 | 0.067182 | 0.065356 | -0.00028623 | -0.0073957 | -0.0012988 | -0.0036011 | 9.6204e-05 | 0.067157 | 0.063192 | -0.0055585 | 0.015063 | -0.0022238 | -0.33417 | 60.6583 | -60.791 | 61.235 | -60.5164 | -60.9741 | -61.0565 | -0.20142 | 60.6583 | -60.878 | 61.0153 | -60.7636 | -60.8414 | -61.0931 | 0.10986 | -0.25177 | 0.32501 | 0.38452 | -0.15564 | -0.073242 | -0.2655 | -0.1831 | 0.022888 | -0.25177 | 0.10529 | 0.13733 | -0.19226 | 0.059509 | -0.21515 | 0.036621 | 0.27466 | 122.0261 | 0.11444 | 121.8933 | 121.4493 | 121.5363 | 121.5591 | 121.5591 | -121.7011 | -121.788 | 122.1359 | 121.9162 | 60.5667 | 60.6995
184.9688 | 122.0764 | -60.9375 | 60.8551 | 0.028839 | 6.3568 | 0.069319 | 0.06856 | 0.0046272 | -0.0024823 | -0.0021532 | 0.0025025 | 0.0030868 | 0.068438 | 0.070669 | -0.0044903 | 0.016772 | -0.00072839 | -0.41199 | 60.6216 | -60.8963 | 61.1572 | -60.6079 | -61.0748 | -61.1572 | -0.3067 | 60.6262 | -60.9558 | 60.9283 | -60.91 | -60.965 | -61.1801 | 0.041199 | -0.23346 | 0.30212 | 0.32959 | -0.21973 | -0.13733 | -0.26093 | -0.17853 | -0.018311 | -0.22888 | 0.073242 | 0.027466 | -0.24262 | -0.027466 | -0.2243 | -0.009155 | 0.28839 | 122.0535 | 0.045777 | 121.8842 | 121.5179 | 121.582 | 121.5591 | 121.5637 | -121.7514 | -121.8109 | 122.0947 | 121.8658 | 60.5255 | 60.6308
186.6406 | 122.0444 | -60.9146 | 60.8505 | -0.0016785 | 6.2532 | 0.0706 | 0.064501 | 0.003559 | -0.0050457 | -0.0015124 | 0.0025025 | 0.0013778 | 0.067584 | 0.060628 | -0.0059857 | 0.01784 | -0.0020102 | -0.42114 | 60.6262 | -60.8643 | 61.1298 | -60.6766 | -61.0886 | -61.1572 | -0.3479 | 60.6491 | -60.9146 | 60.9238 | -60.8917 | -60.9375 | -61.1618 | 0.050354 | -0.2243 | 0.27924 | 0.23804 | -0.24262 | -0.17395 | -0.29297 | -0.2243 | 0 | -0.20142 | 0.073242 | 0.022888 | -0.24719 | -0.022888 | -0.24719 | -0.022888 | 0.18768 | 121.994 | 0.022888 | 121.8384 | 121.4905 | 121.5637 | 121.5408 | 121.5637 | -121.7148 | -121.7651 | 122.0444 | 121.8384 | 60.4935 | 60.5667
188.3281 | 122.0947 | -60.9329 | 60.8093 | -0.0016785 | 6.288 | 0.068464 | 0.061724 | 0.005268 | -0.0050457 | -0.0019396 | -0.0036011 | 0.0026596 | 0.067798 | 0.071309 | -0.0023541 | 0.01549 | -0.0020102 | -0.4303 | 60.6033 | -60.8871 | 61.1298 | -60.6949 | -61.1206 | -61.1801 | -0.31128 | 60.5942 | -60.965 | 60.9283 | -60.91 | -60.9558 | -61.1481 | 0.045776 | -0.20599 | 0.32044 | 0.23804 | -0.24719 | -0.18768 | -0.29297 | -0.23346 | -0.032044 | -0.21515 | 0.11902 | 0.022888 | -0.21515 | -0.022889 | -0.18311 | 0.009155 | 0.19226 | 122.0169 | 0.054932 | 121.8933 | 121.4905 | 121.5591 | 121.5363 | 121.5271 | -121.6965 | -121.7743 | 122.0627 | 121.8613 | 60.5026 | 60.6216
189.9844 | 122.0535 | -60.9146 | 60.8643 | 0.028839 | 6.1981 | 0.071455 | 0.065783 | 0.0033454 | -0.0048321 | 0.00062377 | 0.0055543 | 0.0011642 | 0.069079 | 0.065114 | -0.0038495 | 0.01784 | -0.0011558 | -0.42572 | 60.6125 | -60.8459 | 61.1343 | -60.6354 | -61.0794 | -61.1526 | -0.32959 | 60.6491 | -60.9283 | 60.9238 | -60.9055 | -60.9695 | -61.171 | 0.068665 | -0.25177 | 0.27008 | 0.27924 | -0.23804 | -0.1648 | -0.3067 | -0.23346 | -0.013733 | -0.21515 | 0.059509 | 0.009155 | -0.25635 | -0.054931 | -0.24261 | -0.041198 | 0.21057 | 121.9803 | 0.022888 | 121.8521 | 121.4584 | 121.5775 | 121.5271 | 121.5637 | -121.7102 | -121.7926 | 122.0489 | 121.8384 | 60.4889 | 60.585
191.6562 | 122.081 | -60.8688 | 60.9055 | 0.005951 | 6.313 | 0.069319 | 0.064501 | -0.00092703 | -0.0016279 | -0.00065803 | -0.00054933 | 0.0015914 | 0.066943 | 0.06191 | -0.0036359 | 0.016985 | -0.0011558 | -0.33875 | 60.6628 | -60.8139 | 61.2488 | -60.5209 | -60.9695 | -61.0428 | -0.21515 | 60.6583 | -60.8688 | 60.997 | -60.7727 | -60.8505 | -61.0977 | 0.054931 | -0.24262 | 0.34332 | 0.3479 | -0.17395 | -0.10071 | -0.22888 | -0.15564 | 0 | -0.24719 | 0.091552 | 0.09613 | -0.22888 | 0.01831 | -0.22888 | 0.01831 | 0.29297 | 122.0627 | 0.09613 | 121.8658 | 121.4767 | 121.5271 | 121.5317 | 121.5271 | -121.7194 | -121.7743 | 122.1176 | 121.8658 | 60.5301 | 60.6537
193.3125 | 122.0535 | -60.9146 | 60.878 | 0.02121 | 6.1987 | 0.068678 | 0.064715 | -0.0041314 | -0.0044049 | -0.0030078 | 0.0025025 | -0.000972 | 0.066943 | 0.062124 | -0.0068403 | 0.017199 | -0.0037192 | -0.42114 | 60.64 | -60.8505 | 61.1298 | -60.6674 | -61.0931 | -61.1572 | -0.36621 | 60.6491 | -60.91 | 60.9283 | -60.8871 | -60.9329 | -61.1572 | 0.064087 | -0.23804 | 0.25177 | 0.24719 | -0.24262 | -0.17853 | -0.3067 | -0.24262 | 0.004578 | -0.22888 | 0.050354 | 0.027466 | -0.24262 | -0.01831 | -0.24719 | -0.022888 | 0.18311 | 121.9803 | 0.022888 | 121.8384 | 121.4905 | 121.5591 | 121.5546 | 121.5637 | -121.7285 | -121.788 | 122.0444 | 121.843 | 60.4935 | 60.5484
195 | 122.0169 | -60.9146 | 60.9009 | 0.02121 | 6.3175 | 0.068464 | 0.065997 | 0.0029182 | -0.0065411 | -0.00087163 | 0.011658 | 0.003514 | 0.067584 | 0.053579 | -0.0057721 | 0.014849 | 0.00033961 | -0.3479 | 60.7224 | -60.8551 | 61.1343 | -60.64 | -61.0703 | -61.1481 | -0.29297 | 60.704 | -60.9192 | 60.9238 | -60.8917 | -60.9604 | -61.1755 | 0.059509 | -0.17853 | 0.23346 | 0.27466 | -0.23346 | -0.15564 | -0.29297 | -0.21515 | -0.004577 | -0.19684 | 0.022888 | 0.022888 | -0.26093 | -0.045776 | -0.25635 | -0.041199 | 0.21515 | 121.9894 | 0.027465 | 121.843 | 121.5775 | 121.6232 | 121.637 | 121.6187 | -121.756 | -121.8201 | 122.0489 | 121.8384 | 60.5667 | 60.6216
196.75 | 122.0169 | -60.9833 | 60.8231 | -0.0016785 | 6.2322 | 0.068464 | 0.06621 | -0.00092703 | -0.0039777 | -0.00044443 | -0.00054933 | 0.0028732 | 0.06737 | 0.058706 | -0.0036359 | 0.016131 | -0.001583 | -0.4715 | 60.64 | -60.9055 | 61.0153 | -60.7544 | -61.1847 | -61.2488 | -0.42114 | 60.6171 | -60.9695 | 60.8414 | -60.9787 | -61.0519 | -61.2259 | 0.077819 | -0.1831 | 0.19226 | 0.22888 | -0.2655 | -0.20142 | -0.34332 | -0.27923 | 0.013733 | -0.20599 | 0.018311 | 0.004577 | -0.24262 | -0.068665 | -0.25635 | -0.082398 | 0.15106 | 121.9208 | -0.009156 | 121.8109 | 121.5454 | 121.5866 | 121.6232 | 121.6003 | -121.7285 | -121.7926 | 121.9986 | 121.8246 | 60.5118 | 60.5621
198.4062 | 122.0764 | -60.9375 | 60.8231 | -0.009308 | 6.1904 | 0.070814 | 0.065356 | 0.0020636 | -0.0052595 | -0.0021532 | 0.0025025 | 0.0020188 | 0.069293 | 0.062124 | -0.0029949 | 0.019121 | -0.003292 | -0.43488 | 60.5988 | -60.8734 | 61.1114 | -60.6583 | -61.116 | -61.2122 | -0.32959 | 60.5988 | -60.9329 | 60.9283 | -60.9009 | -60.9604 | -61.1572 | 0.064087 | -0.2243 | 0.28839 | 0.27924 | -0.27466 | -0.17853 | -0.33875 | -0.24262 | 0.004578 | -0.2243 | 0.10529 | 0.036621 | -0.21973 | -0.022888 | -0.22431 | -0.027466 | 0.21515 | 121.9849 | 0.032043 | 121.8613 | 121.4722 | 121.5317 | 121.5363 | 121.5363 | -121.6965 | -121.756 | 122.0489 | 121.8658 | 60.5026 | 60.6079
200.0781 | 122.0947 | -60.878 | 60.9055 | -0.0016785 | 6.2645 | 0.06761 | 0.063006 | -0.0041314 | -0.0031231 | -0.001726 | -0.0036011 | 0.0011642 | 0.068225 | 0.059133 | -0.0049175 | 0.016131 | -0.0047874 | -0.35706 | 60.6216 | -60.8002 | 61.2442 | -60.4843 | -60.9375 | -61.0336 | -0.20599 | 60.6628 | -60.878 | 61.0062 | -60.7544 | -60.8276 | -61.0748 | 0.07782 | -0.28381 | 0.33875 | 0.39368 | -0.15564 | -0.059509 | -0.23346 | -0.13733 | 0 | -0.24262 | 0.10071 | 0.1236 | -0.19684 | 0.050354 | -0.19684 | 0.050354 | 0.31586 | 122.0444 | 0.1236 | 121.8842 | 121.4218 | 121.5408 | 121.4996 | 121.5408 | -121.7056 | -121.7834 | 122.1222 | 121.8842 | 60.5209 | 60.672
201.7812 | 122.0993 | -60.8643 | 60.9055 | -0.0016785 | 6.2491 | 0.067182 | 0.065356 | -0.00092703 | -0.0071821 | -0.00065803 | -0.0036011 | -0.0005448 | 0.06673 | 0.066183 | -0.0032087 | 0.015917 | -0.0017966 | -0.35706 | 60.6537 | -60.8047 | 61.2076 | -60.5209 | -60.9558 | -61.0382 | -0.20142 | 60.6308 | -60.8871 | 61.0016 | -60.7773 | -60.8185 | -61.0794 | 0.059509 | -0.25177 | 0.30212 | 0.34332 | -0.17395 | -0.091553 | -0.23346 | -0.15106 | -0.022888 | -0.27466 | 0.09613 | 0.086975 | -0.21515 | 0.045777 | -0.19226 | 0.068665 | 0.28381 | 122.0123 | 0.10986 | 121.8887 | 121.4584 | 121.5179 | 121.5179 | 121.4951 | -121.7102 | -121.7926 | 122.0718 | 121.8658 | 60.5072 | 60.6628
203.4531 | 121.962 | -60.9787 | 60.8597 | -0.009308 | 6.0936 | 0.068037 | 0.065142 | 0.0050544 | -0.0035505 | -0.0015124 | -0.0036011 | 0.0015914 | 0.069934 | 0.067464 | -0.0057721 | 0.017412 | 0.00033961 | -0.44861 | 60.6491 | -60.878 | 61.0016 | -60.7727 | -61.1984 | -61.2808 | -0.44403 | 60.6491 | -60.965 | 60.8459 | -61.0016 | -61.0703 | -61.2488 | 0.10071 | -0.21057 | 0.14191 | 0.20599 | -0.30212 | -0.21973 | -0.40283 | -0.32043 | 0.013733 | -0.21057 | -0.013733 | -0.022888 | -0.27008 | -0.091552 | -0.28381 | -0.10529 | 0.10529 | 121.8796 | -0.036621 | 121.8109 | 121.5271 | 121.6141 | 121.6278 | 121.6278 | -121.7377 | -121.8246 | 121.9803 | 121.8246 | 60.5301 | 60.5347
205.125 | 122.0901 | -60.9604 | 60.8185 | -0.009308 | 6.1081 | 0.06825 | 0.064501 | 0.003559 | -0.0039777 | -0.00087163 | 0.0025025 | 0.0018052 | 0.06673 | 0.059347 | -0.0017133 | 0.015917 | -0.0030784 | -0.41199 | 60.5759 | -60.8551 | 61.1298 | -60.64 | -61.0977 | -61.1618 | -0.31128 | 60.5988 | -60.9375 | 60.9375 | -60.8734 | -60.9512 | -61.1526 | 0.10529 | -0.24261 | 0.31128 | 0.32043 | -0.20142 | -0.13733 | -0.3067 | -0.24261 | 0.022888 | -0.21973 | 0.11902 | 0.086975 | -0.19226 | 0.009155 | -0.21515 | -0.013733 | 0.21515 | 121.9849 | 0.064087 | 121.875 | 121.431 | 121.5363 | 121.5363 | 121.5591 | -121.6736 | -121.756 | 122.0901 | 121.8979 | 60.5484 | 60.6491
206.8125 | 121.9574 | -60.8917 | 60.9741 | -0.0016785 | 6.1754 | 0.066755 | 0.06621 | 0.0014228 | -0.0031231 | -0.00087163 | -0.00054933 | 0.0026596 | 0.068866 | 0.061056 | -0.0076947 | 0.014208 | -0.001583 | -0.39368 | 60.704 | -60.8139 | 61.1023 | -60.64 | -61.0703 | -61.1389 | -0.37079 | 60.7407 | -60.878 | 60.8688 | -60.8917 | -60.9604 | -61.1755 | 0.07782 | -0.27008 | 0.12817 | 0.25177 | -0.24719 | -0.17853 | -0.32501 | -0.25635 | 0.013733 | -0.23346 | -0.10529 | 0 | -0.28381 | -0.068664 | -0.29755 | -0.082397 | 0.17395 | 121.9162 | -0.013733 | 121.7468 | 121.5179 | 121.6187 | 121.5958 | 121.6324 | -121.788 | -121.8521 | 121.994 | 121.7606 | 60.498 | 60.5209
208.5312 | 121.9574 | -60.9146 | 60.9192 | 0.005951 | 6.2408 | 0.067182 | 0.066851 | -0.0051996 | -0.0033369 | -0.00087163 | 0.011658 | 0.003514 | 0.066302 | 0.054861 | -0.0089765 | 0.013781 | -0.0047874 | -0.39825 | 60.7086 | -60.8688 | 61.0931 | -60.6628 | -61.0657 | -61.1481 | -0.34332 | 60.7269 | -60.9192 | 60.8871 | -60.9009 | -60.9695 | -61.171 | 0.045777 | -0.21057 | 0.17395 | 0.25177 | -0.23346 | -0.15106 | -0.27924 | -0.19684 | -0.004577 | -0.19226 | -0.032043 | 0.013733 | -0.25635 | -0.054931 | -0.25177 | -0.050354 | 0.20599 | 121.962 | 0.01831 | 121.8063 | 121.5775 | 121.6461 | 121.6232 | 121.6415 | -121.788 | -121.8384 | 122.0078 | 121.8018 | 60.5164 | 60.5713
210.2344 | 122.0718 | -60.8505 | 60.878 | 0.005951 | 6.128 | 0.068464 | 0.06322 | 0.0016364 | -0.0031231 | -0.00087163 | -0.00054933 | 0.000737 | 0.066516 | 0.065114 | -0.0047039 | 0.015063 | -0.0037192 | -0.34332 | 60.6628 | -60.7727 | 61.2213 | -60.498 | -60.9421 | -61.0611 | -0.2243 | 60.672 | -60.8551 | 61.0016 | -60.7636 | -60.8414 | -61.084 | 0.07782 | -0.21515 | 0.34332 | 0.35248 | -0.21057 | -0.091553 | -0.28839 | -0.16937 | -0.004578 | -0.20599 | 0.1236 | 0.086975 | -0.23346 | 0.009155 | -0.22888 | 0.013733 | 0.27466 | 121.994 | 0.091553 | 121.8567 | 121.4355 | 121.5271 | 121.5134 | 121.5225 | -121.6507 | -121.7331 | 122.0718 | 121.8521 | 60.5072 | 60.6262
211.8906 | 121.9894 | -60.9329 | 60.9146 | 0.028839 | 6.2423 | 0.067823 | 0.064929 | 0.00099557 | -0.0046185 | -0.0021532 | 0.0086061 | 0.004155 | 0.068011 | 0.066823 | -0.0059857 | 0.011858 | -0.0017966 | -0.36621 | 60.7132 | -60.8459 | 61.116 | -60.6674 | -61.0519 | -61.1435 | -0.33875 | 60.704 | -60.9329 | 60.8963 | -60.8917 | -60.9695 | -61.1664 | 0.086975 | -0.20142 | 0.20142 | 0.2655 | -0.21057 | -0.11902 | -0.29755 | -0.20599 | 0 | -0.21057 | -0.018311 | 0.041198 | -0.23346 | -0.036621 | -0.23346 | -0.036621 | 0.17853 | 121.962 | 0.041198 | 121.8292 | 121.5591 | 121.637 | 121.6461 | 121.637 | -121.7606 | -121.8475 | 122.0489 | 121.8292 | 60.5667 | 60.5942
213.5781 | 121.9986 | -60.9009 | 60.8963 | 0.036468 | 6.2047 | 0.069532 | 0.06621 | 0.0029182 | -0.0046185 | -0.00065803 | 0.0055543 | 0.0026596 | 0.068225 | 0.063405 | -0.0049175 | 0.013781 | -0.003292 | -0.35248 | 60.704 | -60.8276 | 61.1252 | -60.6445 | -61.0519 | -61.1343 | -0.33417 | 60.7132 | -60.9192 | 60.9055 | -60.8871 | -60.9604 | -61.171 | 0.073242 | -0.19226 | 0.22888 | 0.25635 | -0.23346 | -0.15106 | -0.3067 | -0.2243 | -0.01831 | -0.1831 | 0.009156 | 0.013733 | -0.27008 | -0.059509 | -0.25177 | -0.041199 | 0.18311 | 121.9528 | 0.032043 | 121.8246 | 121.5317 | 121.6324 | 121.6049 | 121.6141 | -121.7239 | -121.8155 | 122.0261 | 121.8063 | 60.5484 | 60.5667
215.3438 | 122.0444 | -60.9192 | 60.8231 | 0.028839 | 6.1673 | 0.069319 | 0.06386 | -0.0034906 | -0.0016279 | -0.00087163 | 0.014709 | 0.0011642 | 0.070361 | 0.062978 | -0.00085871 | 0.015917 | -0.0024374 | -0.41199 | 60.5942 | -60.8734 | 61.1343 | -60.5759 | -61.0474 | -61.1252 | -0.28381 | 60.5988 | -60.9421 | 60.91 | -60.8826 | -60.9375 | -61.1618 | 0.045776 | -0.22888 | 0.31128 | 0.34332 | -0.20599 | -0.12817 | -0.25177 | -0.17395 | -0.022889 | -0.2243 | 0.086975 | 0.036621 | -0.24261 | -0.018311 | -0.21973 | 0.004578 | 0.29755 | 122.0078 | 0.05951 | 121.8521 | 121.4676 | 121.5408 | 121.5134 | 121.5179 | -121.6965 | -121.7651 | 122.0535 | 121.8292 | 60.5072 | 60.6354
217.0156 | 122.0581 | -60.8734 | 60.9009 | -0.0016785 | 6.1019 | 0.067823 | 0.063433 | 0.0027044 | -0.0059003 | -0.0019396 | -0.0036011 | 0.0037278 | 0.06737 | 0.054006 | -0.0053449 | 0.018053 | -0.002651 | -0.33875 | 60.6491 | -60.7864 | 61.203 | -60.5347 | -60.9604 | -61.0519 | -0.25177 | 60.6583 | -60.8505 | 60.9833 | -60.7819 | -60.8505 | -61.0794 | 0.086975 | -0.25177 | 0.30212 | 0.33874 | -0.17853 | -0.086975 | -0.2655 | -0.17395 | 0.022888 | -0.24262 | 0.082397 | 0.091553 | -0.20599 | 0.022888 | -0.22888 | 0 | 0.25177 | 121.9894 | 0.068665 | 121.8338 | 121.4355 | 121.5088 | 121.5225 | 121.5317 | -121.6873 | -121.7514 | 122.0764 | 121.8567 | 60.5347 | 60.6216
218.75 | 122.0215 | -60.9421 | 60.8231 | -0.0016785 | 6.1829 | 0.06825 | 0.065356 | -0.00071343 | -0.0033369 | 0.00019657 | -0.00054933 | 0.0018052 | 0.068438 | 0.056142 | -0.0055585 | 0.017626 | -0.0028646 | -0.48065 | 60.6537 | -60.8826 | 61.0245 | -60.7452 | -61.1801 | -61.2396 | -0.41199 | 60.5759 | -60.9467 | 60.8963 | -60.9146 | -60.997 | -61.1801 | 0.05951 | -0.16937 | 0.20142 | 0.19684 | -0.29755 | -0.23804 | -0.35706 | -0.29755 | -0.004577 | -0.24719 | 0.073242 | 0.027466 | -0.23804 | -0.054931 | -0.23346 | -0.050354 | 0.13733 | 121.907 | 0.032043 | 121.843 | 121.5363 | 121.5225 | 121.5958 | 121.5179 | -121.7056 | -121.7697 | 121.9666 | 121.8384 | 60.4614 | 60.5301
220.4375 | 122.0947 | -60.8963 | 60.9009 | -0.0016785 | 6.1068 | 0.066541 | 0.06386 | -0.00049983 | -0.0078229 | 0.0014784 | -0.00054933 | 0.0018052 | 0.067157 | 0.061269 | -0.0053449 | 0.018053 | -0.00051479 | -0.35706 | 60.6308 | -60.7864 | 61.1847 | -60.5164 | -60.9604 | -61.0474 | -0.21515 | 60.6308 | -60.8643 | 61.0291 | -60.7544 | -60.8093 | -61.0565 | 0.10986 | -0.27008 | 0.28381 | 0.37994 | -0.15106 | -0.064087 | -0.26093 | -0.17395 | 0.032043 | -0.27008 | 0.12817 | 0.14191 | -0.16022 | 0.086975 | -0.19226 | 0.054932 | 0.27008 | 121.9711 | 0.10986 | 121.8933 | 121.4172 | 121.4951 | 121.5271 | 121.5271 | -121.6873 | -121.7651 | 122.081 | 121.9254 | 60.5392 | 60.6812
222.125 | 122.0123 | -60.8963 | 60.8643 | 0.01358 | 5.9659 | 0.067182 | 0.065142 | -0.00028623 | -0.0022687 | -0.0019396 | 0.0055543 | 0.0018052 | 0.068011 | 0.064901 | -0.0027813 | 0.01784 | -0.00072839 | -0.43488 | 60.6262 | -60.8414 | 61.0977 | -60.6354 | -61.0611 | -61.1481 | -0.36163 | 60.6354 | -60.9146 | 60.9055 | -60.878 | -60.9421 | -61.1572 | 0.054931 | -0.23804 | 0.23346 | 0.26093 | -0.25177 | -0.16479 | -0.3067 | -0.21973 | -0.018311 | -0.22888 | 0.041199 | 0.01831 | -0.26093 | -0.045777 | -0.24262 | -0.027466 | 0.20599 | 121.9391 | 0.036621 | 121.8201 | 121.4676 | 121.55 | 121.5225 | 121.5317 | -121.7056 | -121.7789 | 121.994 | 121.8018 | 60.4614 | 60.5347
223.7969 | 121.962 | -60.9283 | 60.8551 | -0.0016785 | 6.1267 | 0.066541 | 0.065997 | -7.2628e-05 | -0.0035505 | -0.0012988 | -0.0036011 | 0.0037278 | 0.071002 | 0.063192 | -0.0025677 | 0.017626 | -0.0022238 | -0.39368 | 60.6628 | -60.8505 | 61.0748 | -60.6766 | -61.116 | -61.2076 | -0.37537 | 60.64 | -60.9329 | 60.8505 | -60.9604 | -61.0611 | -61.203 | 0.07782 | -0.19226 | 0.21973 | 0.25177 | -0.27924 | -0.18768 | -0.35706 | -0.2655 | -0.004577 | -0.21515 | -0.004578 | -0.032043 | -0.27466 | -0.13275 | -0.27008 | -0.12817 | 0.17395 | 121.9254 | -0.027466 | 121.7834 | 121.5134 | 121.5729 | 121.5912 | 121.5683 | -121.7056 | -121.788 | 122.0032 | 121.7789 | 60.5347 | 60.553
225.5 | 121.9711 | -60.8826 | 60.9238 | -0.0016785 | 6.1496 | 0.066328 | 0.063006 | -0.0037042 | -0.0037641 | -0.0012988 | -0.00054933 | 0.0020188 | 0.065448 | 0.058919 | -0.0042767 | 0.014208 | -0.006069 | -0.32044 | 60.6674 | -60.791 | 61.171 | -60.5759 | -60.997 | -61.084 | -0.3067 | 60.6995 | -60.8688 | 60.9192 | -60.8551 | -60.9146 | -61.1389 | 0.091552 | -0.25635 | 0.24719 | 0.3067 | -0.20142 | -0.11444 | -0.29297 | -0.20599 | 0.013733 | -0.2243 | -0.004578 | 0.027465 | -0.25635 | -0.032044 | -0.27008 | -0.045777 | 0.21515 | 121.962 | 0.013732 | 121.788 | 121.4584 | 121.5683 | 121.55 | 121.582 | -121.7148 | -121.7926 | 122.0535 | 121.8018 | 60.5621 | 60.5759
227.1875 | 121.9391 | -60.9741 | 60.8597 | -0.0016785 | 6.1553 | 0.067396 | 0.064715 | 0.00056817 | -0.0035505 | -0.0015124 | -0.0066527 | 0.0026596 | 0.069507 | 0.054647 | -0.0036359 | 0.017412 | 0.00033961 | -0.45319 | 60.6537 | -60.8597 | 60.997 | -60.7773 | -61.1893 | -61.2625 | -0.47607 | 60.64 | -60.965 | 60.8093 | -60.997 | -61.0886 | -61.235 | 0.11444 | -0.20599 | 0.13733 | 0.19684 | -0.28839 | -0.21515 | -0.40283 | -0.32959 | 0.009155 | -0.21973 | -0.050354 | -0.022888 | -0.26093 | -0.11444 | -0.27008 | -0.1236 | 0.082397 | 121.8567 | -0.032043 | 121.7743 | 121.5134 | 121.6049 | 121.6278 | 121.6141 | -121.7194 | -121.8246 | 121.9711 | 121.7834 | 60.5209 | 60.498
228.8594 | 122.0215 | -60.9055 | 60.8643 | 0.028839 | 6.1468 | 0.067823 | 0.065142 | 0.0044134 | -0.0018415 | 0.00041017 | 0.0086061 | 0.0011642 | 0.067157 | 0.06896 | -0.0034223 | 0.01784 | -0.0030784 | -0.44403 | 60.6354 | -60.8459 | 61.1069 | -60.6445 | -61.0474 | -61.1389 | -0.35706 | 60.6262 | -60.9421 | 60.9009 | -60.8826 | -60.9467 | -61.1526 | 0.05951 | -0.22888 | 0.24262 | 0.26093 | -0.23346 | -0.14191 | -0.29297 | -0.20142 | -0.036621 | -0.23804 | 0.036621 | 0.022889 | -0.24719 | -0.041198 | -0.21057 | -0.004577 | 0.20142 | 121.9528 | 0.05951 | 121.843 | 121.4813 | 121.5683 | 121.5408 | 121.5317 | -121.7102 | -121.8063 | 122.0123 | 121.8063 | 60.4614 | 60.5484
230.5625 | 122.0627 | -60.8826 | 60.8917 | 0.005951 | 6.1094 | 0.066969 | 0.065569 | -0.004345 | -0.0048321 | -0.00087163 | -0.00054933 | 0.0011642 | 0.068225 | 0.070028 | -0.0044903 | 0.019549 | 0.001835 | -0.39368 | 60.6171 | -60.791 | 61.1435 | -60.585 | -60.9924 | -61.0794 | -0.25635 | 60.6354 | -60.8917 | 60.9879 | -60.7819 | -60.8459 | -61.0748 | 0.091552 | -0.27466 | 0.25177 | 0.29755 | -0.19684 | -0.10986 | -0.28839 | -0.20142 | -0.009156 | -0.25635 | 0.09613 | 0.10071 | -0.19226 | 0.036621 | -0.1831 | 0.045777 | 0.20599 | 121.9345 | 0.10986 | 121.8796 | 121.4081 | 121.5271 | 121.4996 | 121.5179 | -121.6827 | -121.7834 | 122.0261 | 121.8704 | 60.4889 | 60.6262
232.2344 | 122.0261 | -60.9467 | 60.7956 | -0.009308 | 6.0515 | 0.067823 | 0.064074 | 0.0014228 | -0.0063275 | -0.00087163 | 0.0025025 | 0.002446 | 0.06737 | 0.062124 | -0.0023541 | 0.018053 | -8.7586e-05 | -0.47607 | 60.6125 | -60.878 | 61.0565 | -60.704 | -61.1252 | -61.2076 | -0.36621 | 60.5896 | -60.9238 | 60.91 | -60.9055 | -60.9558 | -61.1435 | 0.068664 | -0.1831 | 0.26093 | 0.24261 | -0.26093 | -0.17853 | -0.32959 | -0.24719 | 0.022888 | -0.20599 | 0.11444 | 0.041198 | -0.19684 | -0.009156 | -0.21973 | -0.032044 | 0.17395 | 121.9345 | 0.01831 | 121.8338 | 121.4905 | 121.5134 | 121.5591 | 121.5363 | -121.6736 | -121.7194 | 122.0032 | 121.8567 | 60.4706 | 60.5804
233.8906 | 122.0627 | -60.9055 | 60.8002 | -0.009308 | 5.9688 | 0.06761 | 0.061938 | 0.0016364 | -0.0024823 | -0.00044443 | 0.017761 | 0.0030868 | 0.068652 | 0.063833 | -0.0051313 | 0.017199 | -0.00072839 | -0.41657 | 60.5667 | -60.8551 | 61.1481 | -60.585 | -61.0382 | -61.116 | -0.25177 | 60.5667 | -60.9283 | 60.9329 | -60.8643 | -60.9329 | -61.1298 | 0.050354 | -0.23346 | 0.3479 | 0.32043 | -0.21057 | -0.13275 | -0.26093 | -0.1831 | -0.022888 | -0.23346 | 0.13275 | 0.041199 | -0.2243 | -0.027465 | -0.20142 | -0.004577 | 0.27008 | 122.0032 | 0.064087 | 121.8613 | 121.4218 | 121.4951 | 121.4722 | 121.4722 | -121.6553 | -121.7285 | 122.0535 | 121.8384 | 60.4889 | 60.6537
235.5625 | 122.0215 | -60.9238 | 60.8688 | 0.01358 | 5.921 | 0.068891 | 0.065997 | 0.0031318 | -0.0056867 | -0.00023063 | -0.00054933 | 0.0011642 | 0.066943 | 0.063192 | -0.0040631 | 0.019976 | -0.0022238 | -0.43488 | 60.5988 | -60.8551 | 61.1023 | -60.64 | -61.0611 | -61.1435 | -0.34332 | 60.6445 | -60.91 | 60.9055 | -60.8871 | -60.9604 | -61.1389 | 0.068664 | -0.27008 | 0.23346 | 0.28381 | -0.21973 | -0.13733 | -0.28839 | -0.20599 | 0.013733 | -0.2243 | 0.036622 | 0.036621 | -0.21515 | -0.036621 | -0.22888 | -0.050354 | 0.21515 | 121.9574 | 0.022888 | 121.8155 | 121.4539 | 121.5546 | 121.5225 | 121.5683 | -121.7239 | -121.7789 | 122.0261 | 121.8292 | 60.4889 | 60.5804
237.2188 | 122.0352 | -60.9421 | 60.8276 | 0.02121 | 6.0287 | 0.068678 | 0.065783 | 0.0014228 | -0.0035505 | -0.0021532 | 0.011658 | 0.0037278 | 0.067157 | 0.066396 | -0.0040631 | 0.016558 | -0.003292 | -0.40741 | 60.5988 | -60.8551 | 61.1389 | -60.5713 | -61.0382 | -61.1343 | -0.27008 | 60.6125 | -60.9375 | 60.9146 | -60.8643 | -60.9375 | -61.1526 | 0.086975 | -0.22888 | 0.31128 | 0.37079 | -0.19226 | -0.09613 | -0.27923 | -0.1831 | 0.004578 | -0.21515 | 0.086975 | 0.07782 | -0.21057 | 0.004578 | -0.21515 | 0 | 0.28381 | 121.994 | 0.073242 | 121.8521 | 121.4539 | 121.55 | 121.5408 | 121.5546 | -121.6827 | -121.7651 | 122.081 | 121.8567 | 60.5347 | 60.672
238.9062 | 121.9391 | -60.9467 | 60.8643 | 0.005951 | 6.0673 | 0.068037 | 0.066851 | -0.00049983 | -0.0050457 | -0.0040758 | -0.0036011 | 0.0020188 | 0.069507 | 0.057424 | -0.0070539 | 0.018053 | -0.003292 | -0.46692 | 60.6262 | -60.8963 | 60.997 | -60.7636 | -61.1938 | -61.2442 | -0.44403 | 60.6537 | -60.9695 | 60.8139 | -60.9924 | -61.0519 | -61.2259 | 0.050354 | -0.23804 | 0.13275 | 0.1831 | -0.29755 | -0.24719 | -0.3479 | -0.29755 | -0.022888 | -0.21057 | -0.050354 | -0.045777 | -0.27924 | -0.10529 | -0.25635 | -0.082398 | 0.13275 | 121.8933 | -0.022889 | 121.7834 | 121.5225 | 121.6232 | 121.5729 | 121.6003 | -121.7606 | -121.8338 | 121.9437 | 121.7606 | 60.4797 | 60.5026
240.5781 | 121.9574 | -60.965 | 60.8551 | -0.0016785 | 5.9242 | 0.067182 | 0.065997 | 0.0016364 | -0.0037641 | -0.00065803 | -0.0036011 | 0.0028732 | 0.066943 | 0.062337 | -0.0068403 | 0.016558 | -0.00072839 | -0.38452 | 60.6491 | -60.8459 | 61.0748 | -60.6674 | -61.116 | -61.1893 | -0.36621 | 60.6354 | -60.9329 | 60.8414 | -60.9421 | -61.0199 | -61.2076 | 0.11902 | -0.20599 | 0.21973 | 0.29755 | -0.2243 | -0.15106 | -0.34332 | -0.27008 | 0.032044 | -0.21973 | -0.013733 | 0.022888 | -0.24262 | -0.054931 | -0.27466 | -0.086975 | 0.17853 | 121.9208 | -0.009156 | 121.7743 | 121.4951 | 121.5683 | 121.6141 | 121.6003 | -121.7011 | -121.788 | 122.0398 | 121.8063 | 60.5804 | 60.5988
242.25 | 121.9391 | -60.9329 | 60.8597 | -0.0016785 | 5.9197 | 0.067396 | 0.065142 | 0.00078177 | -0.0018415 | -0.00065803 | 0.0025025 | 0.0028732 | 0.066089 | 0.060842 | -0.0038495 | 0.017412 | -0.00436 | -0.39825 | 60.6445 | -60.8643 | 61.0794 | -60.6628 | -61.1069 | -61.1893 | -0.37079 | 60.6354 | -60.9192 | 60.8551 | -60.9329 | -61.0336 | -61.1984 | 0.068664 | -0.21515 | 0.21973 | 0.27008 | -0.25635 | -0.17395 | -0.32501 | -0.24262 | 0.013733 | -0.2243 | -0.004577 | 0 | -0.2655 | -0.10071 | -0.27924 | -0.11444 | 0.20142 | 121.9437 | -0.013733 | 121.7743 | 121.5088 | 121.5546 | 121.5775 | 121.5683 | -121.7239 | -121.7789 | 122.0123 | 121.788 | 60.5347 | 60.5621
243.9375 | 121.962 | -60.9238 | 60.8643 | -0.0016785 | 5.1812 | 0.06761 | 0.065569 | 0.00099557 | -0.0052595 | -0.0012988 | 0.0055543 | 0.0039414 | 0.068438 | 0.058065 | -0.0055585 | 0.016772 | -0.0028646 | -0.37994 | 60.6674 | -60.8322 | 61.1023 | -60.6125 | -61.0748 | -61.1481 | -0.32959 | 60.6445 | -60.9009 | 60.8643 | -60.8917 | -60.9787 | -61.1526 | 0.091553 | -0.19684 | 0.23804 | 0.31128 | -0.2243 | -0.15106 | -0.31586 | -0.24262 | 0.022888 | -0.21973 | 0 | 0.032043 | -0.22888 | -0.054932 | -0.25177 | -0.07782 | 0.21973 | 121.9345 | 0.009155 | 121.7651 | 121.4996 | 121.5454 | 121.5912 | 121.5683 | -121.6965 | -121.7651 | 122.0261 | 121.788 | 60.5438 | 60.5942
245.6094 | 122.0581 | -60.9238 | 60.7956 | -0.0016785 | 5.6255 | 0.066969 | 0.06386 | -0.0030634 | -0.0044049 | -0.0036486 | -0.0066527 | 9.6204e-05 | 0.065021 | 0.061269 | -0.0019269 | 0.017412 | -0.0058554 | -0.41199 | 60.5576 | -60.8276 | 61.1069 | -60.6125 | -61.0703 | -61.1526 | -0.32501 | 60.553 | -60.9467 | 60.9238 | -60.8459 | -60.9283 | -61.1298 | 0.09613 | -0.23804 | 0.31128 | 0.31128 | -0.22888 | -0.14648 | -0.32501 | -0.24261 | -0.022888 | -0.24261 | 0.12817 | 0.07782 | -0.20599 | -0.004578 | -0.18311 | 0.01831 | 0.21515 | 121.9345 | 0.10071 | 121.8704 | 121.3852 | 121.4996 | 121.4813 | 121.4767 | -121.6232 | -121.7422 | 122.0306 | 121.8475 | 60.5118 | 60.5988
247.2656 | 122.0261 | -60.9192 | 60.8185 | -0.009308 | 5.837 | 0.067823 | 0.064929 | 0.0012092 | -0.0039777 | -0.0010852 | -0.00054933 | 0.0022324 | 0.066302 | 0.065755 | -0.0038495 | 0.016344 | 0.0011942 | -0.4715 | 60.6171 | -60.8734 | 61.0062 | -60.6995 | -61.1435 | -61.2122 | -0.39825 | 60.585 | -60.9283 | 60.8963 | -60.8917 | -60.965 | -61.1572 | 0.045776 | -0.20142 | 0.18768 | 0.21973 | -0.29297 | -0.2243 | -0.33875 | -0.27008 | -0.009156 | -0.23346 | 0.07782 | 0.027465 | -0.23804 | -0.045777 | -0.22888 | -0.036621 | 0.17395 | 121.8796 | 0.036621 | 121.8246 | 121.4905 | 121.5134 | 121.5363 | 121.5042 | -121.6919 | -121.7468 | 121.9254 | 121.8155 | 60.4477 | 60.5209
248.9531 | 121.9711 | -60.965 | 60.8231 | -0.0016785 | 5.6997 | 0.06825 | 0.065783 | 0.0020636 | -0.0022687 | 0.00083737 | -0.0036011 | 0.0026596 | 0.066943 | 0.058919 | -0.0053449 | 0.017412 | -0.00051479 | -0.48065 | 60.6491 | -60.8871 | 60.9879 | -60.7498 | -61.1664 | -61.2259 | -0.42572 | 60.6079 | -60.9375 | 60.8276 | -60.9558 | -61.0199 | -61.1984 | 0.07782 | -0.17395 | 0.16479 | 0.21515 | -0.26093 | -0.20142 | -0.33874 | -0.27924 | 0.027466 | -0.21515 | 0.004578 | 0.009155 | -0.23346 | -0.054931 | -0.26093 | -0.082397 | 0.13733 | 121.875 | -0.018311 | 121.7651 | 121.5363 | 121.5454 | 121.6141 | 121.5729 | -121.7102 | -121.7606 | 121.9528 | 121.7926 | 60.4843 | 60.5392
250.6094 | 121.9666 | -60.878 | 60.91 | -0.009308 | 5.6478 | 0.06761 | 0.06322 | 0.00078177 | -0.0065411 | -0.00087163 | -0.00054933 | 0.0013778 | 0.068011 | 0.061483 | -0.0059857 | 0.014849 | -0.0039328 | -0.32959 | 60.6583 | -60.7819 | 61.171 | -60.553 | -60.9604 | -61.0611 | -0.27466 | 60.6628 | -60.8414 | 60.9192 | -60.8185 | -60.9055 | -61.116 | 0.096131 | -0.25177 | 0.26093 | 0.32501 | -0.1831 | -0.082397 | -0.27924 | -0.17853 | 0.036621 | -0.24719 | 0.009155 | 0.05951 | -0.23804 | -0.027466 | -0.27466 | -0.064087 | 0.22888 | 121.9528 | 0.022889 | 121.7606 | 121.4401 | 121.5042 | 121.5363 | 121.5408 | -121.6919 | -121.7514 | 122.049 | 121.7972 | 60.5484 | 60.6033
252.2812 | 122.0581 | -60.8505 | 60.8505 | -0.0016785 | 5.6352 | 0.067182 | 0.062365 | -0.0019952 | -0.0035505 | -0.00044443 | 0.0025025 | 0.0011642 | 0.069507 | 0.060201 | -0.0038495 | 0.016131 | -0.0030784 | -0.37537 | 60.6491 | -60.7864 | 61.171 | -60.5438 | -60.965 | -61.0519 | -0.23346 | 60.6308 | -60.8505 | 60.9833 | -60.7636 | -60.8276 | -61.0657 | 0.064087 | -0.20142 | 0.32043 | 0.3067 | -0.20142 | -0.11444 | -0.2655 | -0.17853 | 0 | -0.21973 | 0.13275 | 0.086975 | -0.21515 | 0.022888 | -0.21515 | 0.022888 | 0.24261 | 121.9574 | 0.086975 | 121.8338 | 121.4355 | 121.4813 | 121.4996 | 121.4813 | -121.637 | -121.701 | 122.0215 | 121.8338 | 60.4752 | 60.6171
253.9531 | 122.0535 | -60.8414 | 60.8551 | -0.0016785 | 5.8127 | 0.066755 | 0.064074 | -0.0013544 | -0.0059003 | -0.0038622 | -0.0036011 | 0.0003098 | 0.06737 | 0.063833 | -0.0055585 | 0.018267 | -0.00094199 | -0.34332 | 60.6216 | -60.7864 | 61.1801 | -60.5026 | -60.9375 | -61.0428 | -0.21057 | 60.6445 | -60.8368 | 60.9879 | -60.7452 | -60.8093 | -61.0611 | 0.054932 | -0.23346 | 0.32501 | 0.33874 | -0.20142 | -0.09613 | -0.25635 | -0.15106 | 0.004578 | -0.21057 | 0.13275 | 0.096131 | -0.21973 | 0.032044 | -0.2243 | 0.027466 | 0.28381 | 121.9666 | 0.091553 | 121.8246 | 121.4081 | 121.4813 | 121.463 | 121.4859 | -121.6415 | -121.6919 | 122.0215 | 121.8292 | 60.498 | 60.6308
255.625 | 121.9711 | -60.8871 | 60.9146 | -0.016937 | 5.3258 | 0.069959 | 0.062792 | -0.0037042 | -0.0073957 | -0.0027942 | -0.00054933 | 0.0011642 | 0.065234 | 0.061483 | -0.0042767 | 0.016985 | -0.0062826 | -0.33875 | 60.6354 | -60.7819 | 61.1755 | -60.553 | -60.9375 | -61.0611 | -0.2655 | 60.672 | -60.8368 | 60.9238 | -60.8185 | -60.8826 | -61.084 | 0.10529 | -0.27924 | 0.26093 | 0.33417 | -0.17395 | -0.050354 | -0.27924 | -0.15564 | 0.050354 | -0.24262 | 0.009155 | 0.068665 | -0.19684 | 0.004578 | -0.24719 | -0.045776 | 0.22888 | 121.9574 | 0.018311 | 121.7606 | 121.4172 | 121.5088 | 121.5225 | 121.5591 | -121.6965 | -121.7514 | 122.0627 | 121.8109 | 60.5484 | 60.6216
257.2969 | 122.0581 | -60.8643 | 60.8963 | 0.005951 | 5.0052 | 0.068678 | 0.064074 | 0.00099557 | -0.0054731 | -0.0040758 | -0.0066527 | 0.0026596 | 0.065875 | 0.066823 | -0.0038495 | 0.014208 | 0.00012601 | -0.33417 | 60.6125 | -60.7727 | 61.203 | -60.5026 | -60.9375 | -61.0336 | -0.20599 | 60.6445 | -60.8368 | 60.9879 | -60.7361 | -60.791 | -61.0565 | 0.091553 | -0.28381 | 0.3067 | 0.36163 | -0.16937 | -0.073242 | -0.26093 | -0.16479 | 0.027466 | -0.25177 | 0.091553 | 0.12817 | -0.19226 | 0.073242 | -0.21973 | 0.045776 | 0.27008 | 121.9757 | 0.10071 | 121.8246 | 121.3852 | 121.4813 | 121.4767 | 121.5088 | -121.669 | -121.7331 | 122.0673 | 121.8521 | 60.5301 | 60.6583
258.9844 | 122.0078 | -60.9009 | 60.8551 | 0.01358 | 5.1306 | 0.067396 | 0.065783 | 0.0022772 | -0.0046185 | -0.00023063 | 0.0025025 | 0.0020188 | 0.068438 | 0.070241 | -0.0053449 | 0.017199 | -0.002651 | -0.4303 | 60.6171 | -60.8322 | 61.0794 | -60.6216 | -61.0519 | -61.1435 | -0.34332 | 60.6171 | -60.9009 | 60.9009 | -60.8734 | -60.9146 | -61.1114 | 0.068665 | -0.23804 | 0.2243 | 0.27924 | -0.24261 | -0.15106 | -0.31128 | -0.21973 | 0 | -0.23804 | 0.045776 | 0.027466 | -0.21057 | -0.013733 | -0.21057 | -0.013733 | 0.21057 | 121.9116 | 0.027466 | 121.8018 | 121.4493 | 121.5179 | 121.5179 | 121.5179 | -121.6873 | -121.756 | 121.9803 | 121.8018 | 60.4706 | 60.5576
260.7188 | 122.0535 | -60.8505 | 60.8551 | -0.0016785 | 5.2468 | 0.066755 | 0.062579 | 0.00014097 | -0.0029095 | 0.00019657 | -0.0036011 | 0.0005234 | 0.066302 | 0.059774 | -0.0061993 | 0.016344 | 0.00076681 | -0.33875 | 60.6354 | -60.7956 | 61.2076 | -60.5072 | -60.9421 | -61.0245 | -0.2243 | 60.6628 | -60.8368 | 60.9924 | -60.7452 | -60.8093 | -61.0519 | 0.054932 | -0.21973 | 0.35248 | 0.34332 | -0.17395 | -0.091553 | -0.22888 | -0.14649 | 0.013733 | -0.19226 | 0.13733 | 0.10529 | -0.20142 | 0.041199 | -0.21515 | 0.027466 | 0.28839 | 122.0032 | 0.091553 | 121.8292 | 121.431 | 121.4996 | 121.4859 | 121.5134 | -121.6507 | -121.6919 | 122.0581 | 121.843 | 60.5118 | 60.6262
262.4531 | 122.0581 | -60.8505 | 60.8826 | -0.0016785 | 5.3414 | 0.067823 | 0.06386 | -0.00049983 | -0.0052595 | -0.00087163 | -0.0036011 | 0.0011642 | 0.066089 | 0.061056 | -0.0049175 | 0.017626 | -0.005001 | -0.34332 | 60.6171 | -60.7773 | 61.203 | -60.4797 | -60.9283 | -61.0107 | -0.22888 | 60.6491 | -60.8505 | 60.9924 | -60.7407 | -60.8002 | -61.0382 | 0.073242 | -0.2655 | 0.32044 | 0.37079 | -0.16022 | -0.07782 | -0.23346 | -0.15106 | 0 | -0.23346 | 0.10986 | 0.10986 | -0.18768 | 0.050354 | -0.18768 | 0.050354 | 0.29755 | 121.9803 | 0.10986 | 121.843 | 121.3943 | 121.4996 | 121.4676 | 121.4996 | -121.6599 | -121.7331 | 122.0535 | 121.843 | 60.5072 | 60.6216
264.1406 | 121.9116 | -60.9558 | 60.8276 | -0.0016785 | 5.2013 | 0.068037 | 0.068133 | -0.004986 | -0.0033369 | -0.0010852 | -0.00054933 | 0.0045822 | 0.068652 | 0.059347 | -0.0040631 | 0.016558 | -0.0037192 | -0.47607 | 60.6354 | -60.8643 | 60.9879 | -60.759 | -61.1847 | -61.2534 | -0.46692 | 60.6262 | -60.9421 | 60.791 | -60.9879 | -61.0657 | -61.1938 | 0.091553 | -0.19226 | 0.16022 | 0.19684 | -0.29755 | -0.22888 | -0.3891 | -0.32043 | 0.013733 | -0.20142 | -0.036621 | -0.032043 | -0.23804 | -0.10986 | -0.25177 | -0.1236 | 0.10529 | 121.8521 | -0.045776 | 121.7331 | 121.4996 | 121.5683 | 121.5912 | 121.582 | -121.6919 | -121.7697 | 121.9437 | 121.7468 | 60.4797 | 60.4889
265.8438 | 122.0352 | -60.9329 | 60.7864 | 0.005951 | 5.2201 | 0.06825 | 0.065142 | 0.0012092 | -0.0033369 | -0.00087163 | -0.00054933 | 0.002446 | 0.068652 | 0.061056 | -0.0047039 | 0.016985 | 0.0020486 | -0.46234 | 60.5942 | -60.8643 | 61.0565 | -60.6628 | -61.1069 | -61.171 | -0.37079 | 60.5804 | -60.9375 | 60.9192 | -60.8597 | -60.9375 | -61.1206 | 0.068664 | -0.19226 | 0.27008 | 0.27008 | -0.23804 | -0.17395 | -0.3067 | -0.24262 | -0.004578 | -0.20599 | 0.13275 | 0.073242 | -0.18768 | -0.004578 | -0.1831 | 0 | 0.20142 | 121.9208 | 0.07782 | 121.8567 | 121.4584 | 121.5179 | 121.5271 | 121.5134 | -121.6507 | -121.7239 | 121.9894 | 121.8521 | 60.4706 | 60.5621
267.5156 | 122.0673 | -60.8459 | 60.8734 | -0.009308 | 5.4743 | 0.066969 | 0.06386 | -0.0037042 | -0.0020551 | -0.00044443 | 0.0025025 | 9.6204e-05 | 0.067157 | 0.065755 | -0.0023541 | 0.016772 | -0.006069 | -0.35248 | 60.6216 | -60.7636 | 61.203 | -60.4797 | -60.9146 | -61.0062 | -0.21973 | 60.6583 | -60.8505 | 60.9924 | -60.7315 | -60.8047 | -61.0428 | 0.082397 | -0.25177 | 0.32959 | 0.36621 | -0.16022 | -0.068665 | -0.24262 | -0.15106 | -0.004578 | -0.21515 | 0.11902 | 0.11444 | -0.19684 | 0.041198 | -0.19226 | 0.045776 | 0.28381 | 121.9666 | 0.11902 | 121.843 | 121.3852 | 121.5088 | 121.4676 | 121.5042 | -121.637 | -121.7239 | 122.049 | 121.8384 | 60.4935 | 60.6262
269.1875 | 121.9162 | -60.9787 | 60.8597 | 0.005951 | 5.5993 | 0.06761 | 0.064288 | 0.0024908 | -0.0044049 | -0.0019396 | 0.0025025 | 0.0039414 | 0.066943 | 0.061056 | -0.0042767 | 0.017412 | -0.0011558 | -0.4715 | 60.6216 | -60.8688 | 60.9879 | -60.7498 | -61.1755 | -61.2488 | -0.45776 | 60.6171 | -60.9421 | 60.8139 | -60.9558 | -61.0382 | -61.203 | 0.10986 | -0.23804 | 0.12817 | 0.22888 | -0.27008 | -0.19684 | -0.37994 | -0.3067 | 0.036621 | -0.24262 | -0.045776 | 0.022888 | -0.2243 | -0.059509 | -0.26093 | -0.09613 | 0.11902 | 121.8567 | -0.013733 | 121.756 | 121.4905 | 121.5591 | 121.6003 | 121.5958 | -121.7285 | -121.8018 | 121.9666 | 121.7926 | 60.5072 | 60.5209
270.9375 | 121.9574 | -60.8917 | 60.8734 | 0.005951 | 5.4688 | 0.068678 | 0.065356 | 0.0012092 | -0.0022687 | -0.0012988 | 0.0055543 | 0.0022324 | 0.069079 | 0.055715 | -0.0053449 | 0.016772 | -8.7586e-05 | -0.37079 | 60.672 | -60.8368 | 61.1023 | -60.6033 | -61.0474 | -61.116 | -0.29755 | 60.6354 | -60.9146 | 60.8963 | -60.878 | -60.9421 | -61.1481 | 0.054932 | -0.20142 | 0.22888 | 0.28839 | -0.2243 | -0.15564 | -0.27924 | -0.21057 | -0.022888 | -0.23804 | 0.022888 | 0.013733 | -0.25635 | -0.050354 | -0.23346 | -0.027466 | 0.23346 | 121.9391 | 0.036621 | 121.8109 | 121.5088 | 121.55 | 121.5637 | 121.5271 | -121.7102 | -121.788 | 121.994 | 121.788 | 60.5209 | 60.5942
272.6875 | 121.9391 | -60.8643 | 60.9329 | -0.0016785 | 5.8372 | 0.068464 | 0.06322 | -0.002636 | -0.0052595 | -0.001726 | -0.0036011 | 9.6204e-05 | 0.066302 | 0.063619 | -0.0072675 | 0.016558 | -0.0052146 | -0.3479 | 60.6491 | -60.7727 | 61.1481 | -60.5347 | -60.965 | -61.0657 | -0.28381 | 60.6583 | -60.8643 | 60.91 | -60.8322 | -60.8871 | -61.1252 | 0.091553 | -0.28381 | 0.21515 | 0.32959 | -0.20142 | -0.10071 | -0.29297 | -0.19226 | 0 | -0.27466 | -0.022888 | 0.032044 | -0.26093 | -0.022888 | -0.26093 | -0.022888 | 0.23804 | 121.9208 | 0.032044 | 121.7743 | 121.4218 | 121.5225 | 121.5134 | 121.5225 | -121.7056 | -121.7972 | 122.0123 | 121.7743 | 60.5164 | 60.5804
274.4375 | 122.0535 | -60.8414 | 60.8826 | -0.009308 | 5.175 | 0.066755 | 0.062792 | 0.003559 | -0.0056867 | -0.0015124 | -0.0036011 | 0.000737 | 0.068225 | 0.056356 | -0.0025677 | 0.015276 | -0.0024374 | -0.35248 | 60.6354 | -60.7681 | 61.1801 | -60.5118 | -60.9512 | -61.0382 | -0.22888 | 60.6216 | -60.8231 | 60.9924 | -60.7361 | -60.8002 | -61.0519 | 0.073243 | -0.24719 | 0.29755 | 0.32959 | -0.19684 | -0.10986 | -0.27008 | -0.18311 | 0.018311 | -0.26093 | 0.10986 | 0.10529 | -0.21057 | 0.041199 | -0.22888 | 0.022888 | 0.25635 | 121.9482 | 0.086975 | 121.8155 | 121.4035 | 121.4447 | 121.4767 | 121.463 | -121.6507 | -121.7056 | 122.0215 | 121.8338 | 60.4889 | 60.6125
276.1875 | 121.907 | -60.8414 | 60.91 | -0.0016785 | 4.7136 | 0.067823 | 0.06621 | -0.001568 | -0.0069683 | -0.0032214 | -0.00054933 | 0.003514 | 0.067584 | 0.058919 | -0.0083355 | 0.014849 | -0.0035056 | -0.38452 | 60.6949 | -60.791 | 61.0703 | -60.64 | -61.0382 | -61.1435 | -0.3891 | 60.7178 | -60.8597 | 60.8643 | -60.878 | -60.9467 | -61.1206 | 0.050354 | -0.21515 | 0.16022 | 0.20142 | -0.30212 | -0.19684 | -0.35248 | -0.24719 | -0.01831 | -0.19226 | -0.045776 | -0.036621 | -0.27923 | -0.10529 | -0.26093 | -0.086975 | 0.15106 | 121.8613 | -0.018311 | 121.7239 | 121.4859 | 121.5775 | 121.5363 | 121.5591 | -121.7011 | -121.7697 | 121.9116 | 121.7056 | 60.4568 | 60.4523
277.875 | 121.9254 | -60.9283 | 60.8322 | 0.005951 | 4.7352 | 0.066969 | 0.066638 | 0.00099557 | -0.0073957 | -0.002367 | 0.0025025 | 0.003514 | 0.068011 | 0.054433 | -0.0029949 | 0.015276 | -0.0035056 | -0.48065 | 60.64 | -60.9146 | 60.9695 | -60.7544 | -61.171 | -61.2488 | -0.48065 | 60.6079 | -60.9329 | 60.7956 | -60.9695 | -61.0565 | -61.2122 | 0.013733 | -0.19226 | 0.13733 | 0.17395 | -0.32043 | -0.24261 | -0.33417 | -0.25635 | -0.004577 | -0.2243 | -0.036621 | -0.041198 | -0.28381 | -0.12817 | -0.27924 | -0.1236 | 0.16022 | 121.8842 | -0.036621 | 121.7285 | 121.5546 | 121.5408 | 121.5683 | 121.5363 | -121.7468 | -121.7651 | 121.8979 | 121.7239 | 60.4477 | 60.4477
279.6094 | 121.9254 | -60.8826 | 60.8963 | -0.0016785 | 5.2692 | 0.06761 | 0.064501 | 0.0022772 | -0.0035505 | 0.0029736 | 0.0086061 | 0.0037278 | 0.070147 | 0.064474 | -0.0047039 | 0.016344 | 0.00012601 | -0.40283 | 60.6995 | -60.8093 | 61.0748 | -60.64 | -61.0428 | -61.1343 | -0.36163 | 60.7224 | -60.8688 | 60.8826 | -60.878 | -60.9512 | -61.1343 | 0.073242 | -0.19684 | 0.17853 | 0.24261 | -0.25177 | -0.16022 | -0.32501 | -0.23346 | 0.013733 | -0.17395 | -0.013733 | 0.004577 | -0.25177 | -0.068665 | -0.2655 | -0.082398 | 0.16937 | 121.8842 | -0.009156 | 121.7514 | 121.5088 | 121.5912 | 121.582 | 121.6049 | -121.7056 | -121.7651 | 121.9574 | 121.7651 | 60.4797 | 60.5209
281.3281 | 122.0352 | -60.8963 | 60.7773 | -0.0016785 | 5.1163 | 0.068464 | 0.06322 | -0.0019952 | -0.0022687 | -1.7026e-05 | -0.00054933 | 0.0011642 | 0.066302 | 0.06191 | -0.0014997 | 0.019976 | -0.00030119 | -0.41657 | 60.5576 | -60.8276 | 61.1023 | -60.6079 | -61.0519 | -61.1389 | -0.31586 | 60.5301 | -60.9055 | 60.9329 | -60.8231 | -60.9009 | -61.0977 | 0.068664 | -0.21973 | 0.32501 | 0.28839 | -0.24262 | -0.15564 | -0.31128 | -0.2243 | -0.009156 | -0.24719 | 0.15564 | 0.073242 | -0.20142 | -0.004578 | -0.19226 | 0.004578 | 0.21973 | 121.9299 | 0.082398 | 121.8384 | 121.3852 | 121.4355 | 121.4539 | 121.4264 | -121.6049 | -121.6827 | 121.9986 | 121.8292 | 60.4797 | 60.5804
283 | 122.0078 | -60.9009 | 60.7681 | 0.036468 | 5.1532 | 0.068891 | 0.065356 | 0.0037726 | -0.0046185 | -0.001726 | 0.011658 | 0.0022324 | 0.069079 | 0.063405 | -0.0032087 | 0.020617 | -0.0013694 | -0.40741 | 60.6079 | -60.8643 | 61.1252 | -60.5713 | -61.0245 | -61.1069 | -0.27924 | 60.585 | -60.9192 | 60.9055 | -60.8414 | -60.9146 | -61.1298 | 0.036621 | -0.16022 | 0.35706 | 0.32959 | -0.20599 | -0.1236 | -0.24262 | -0.16022 | -0.01831 | -0.1831 | 0.13733 | 0.059509 | -0.22888 | -0.013733 | -0.21057 | 0.004577 | 0.29297 | 121.9894 | 0.077819 | 121.8246 | 121.4722 | 121.5042 | 121.5088 | 121.4859 | -121.6324 | -121.6873 | 122.0261 | 121.8063 | 60.4935 | 60.6216
284.7344 | 121.9391 | -60.8917 | 60.8643 | 0.036468 | 4.9317 | 0.068678 | 0.065569 | 0.008045 | -0.0018415 | -0.002367 | 0.0086061 | 0.0033004 | 0.067157 | 0.052511 | -0.0057721 | 0.018694 | -0.0047874 | -0.36621 | 60.704 | -60.8185 | 61.1023 | -60.6125 | -61.0107 | -61.116 | -0.34332 | 60.6857 | -60.9009 | 60.8734 | -60.8505 | -60.9329 | -61.116 | 0.073243 | -0.16022 | 0.23804 | 0.27924 | -0.2243 | -0.11902 | -0.29755 | -0.19226 | -0.009155 | -0.17853 | 0.009155 | 0.041199 | -0.2243 | -0.041198 | -0.21515 | -0.032043 | 0.20599 | 121.9208 | 0.050354 | 121.7743 | 121.5225 | 121.5866 | 121.5958 | 121.5775 | -121.6827 | -121.7651 | 121.994 | 121.7651 | 60.5255 | 60.5484
286.4219 | 121.9437 | -60.8871 | 60.9009 | 0.028839 | 4.7369 | 0.066755 | 0.067065 | 0.0031318 | -0.0052595 | -0.00087163 | 0.014709 | 0.005223 | 0.06673 | 0.054647 | -0.0066265 | 0.01784 | -0.00094199 | -0.36621 | 60.7086 | -60.8459 | 61.0748 | -60.6125 | -61.0153 | -61.0931 | -0.33875 | 60.6995 | -60.9009 | 60.8917 | -60.8643 | -60.9329 | -61.1114 | 0.041199 | -0.19226 | 0.17395 | 0.27466 | -0.20599 | -0.12817 | -0.24719 | -0.16937 | -0.013733 | -0.20142 | -0.009155 | 0.022888 | -0.2243 | -0.045776 | -0.21057 | -0.032043 | 0.23346 | 121.9208 | 0.036621 | 121.7926 | 121.5546 | 121.6003 | 121.5958 | 121.5866 | -121.7468 | -121.8018 | 121.962 | 121.7789 | 60.5209 | 60.5484
288.1562 | 121.907 | -60.8688 | 60.9055 | -0.0016785 | 4.4615 | 0.066114 | 0.06621 | 0.00035457 | -0.0044049 | -0.0040758 | 0.0025025 | 0.003514 | 0.067157 | 0.063192 | -0.0057721 | 0.015917 | -0.0030784 | -0.39368 | 60.704 | -60.8002 | 61.0519 | -60.6491 | -61.0565 | -61.1298 | -0.37079 | 60.7086 | -60.8826 | 60.8597 | -60.8871 | -60.9512 | -61.1298 | 0.068664 | -0.20142 | 0.14648 | 0.21973 | -0.26093 | -0.18768 | -0.32959 | -0.25635 | -0.013733 | -0.19684 | -0.045777 | -0.018311 | -0.26093 | -0.082398 | -0.24719 | -0.068665 | 0.15106 | 121.8521 | -0.004578 | 121.7422 | 121.5042 | 121.5912 | 121.5729 | 121.5775 | -121.7056 | -121.788 | 121.9208 | 121.7285 | 60.4752 | 60.498
289.8281 | 121.9345 | -60.878 | 60.9146 | 0.028839 | 5.3237 | 0.06761 | 0.067492 | 0.0037726 | -0.0061139 | -0.0021532 | 0.011658 | 0.0030868 | 0.069507 | 0.061483 | -0.0049175 | 0.016985 | -0.00072839 | -0.37994 | 60.7178 | -60.8414 | 61.0611 | -60.6354 | -61.0291 | -61.1343 | -0.36621 | 60.7086 | -60.9009 | 60.878 | -60.8643 | -60.9238 | -61.1206 | 0.036621 | -0.19684 | 0.14648 | 0.24262 | -0.25635 | -0.15106 | -0.29297 | -0.18768 | -0.022888 | -0.20599 | -0.036621 | 0.013733 | -0.24261 | -0.045776 | -0.21973 | -0.022888 | 0.20599 | 121.9025 | 0.036621 | 121.7789 | 121.5591 | 121.6095 | 121.5958 | 121.5866 | -121.756 | -121.8155 | 121.9391 | 121.756 | 60.498 | 60.5118
291.5625 | 121.9894 | -60.9055 | 60.8047 | 0.036468 | 5.4121 | 0.071882 | 0.065783 | 0.0020636 | -0.0033369 | -0.0021532 | 0.011658 | 0.0013778 | 0.06737 | 0.065542 | -0.0044903 | 0.020189 | -0.001583 | -0.42114 | 60.6079 | -60.8231 | 61.1069 | -60.5896 | -61.0428 | -61.1114 | -0.30212 | 60.585 | -60.9375 | 60.91 | -60.8459 | -60.9146 | -61.116 | 0.082398 | -0.19684 | 0.30212 | 0.31586 | -0.20599 | -0.13733 | -0.28839 | -0.21973 | -0.032043 | -0.21973 | 0.10529 | 0.05951 | -0.21057 | -0.009155 | -0.17853 | 0.022888 | 0.23346 | 121.9299 | 0.091553 | 121.8475 | 121.431 | 121.5225 | 121.5134 | 121.4905 | -121.6278 | -121.7422 | 122.0123 | 121.8155 | 60.4843 | 60.6033
293.2969 | 121.8796 | -60.9192 | 60.8505 | -0.0016785 | 5.5108 | 0.0706 | 0.064715 | 0.00099557 | -0.0046185 | 0.00019657 | -0.00054933 | 0.0026596 | 0.068011 | 0.058065 | -0.0044903 | 0.01848 | 0.0016214 | -0.46234 | 60.6216 | -60.8414 | 60.9924 | -60.7315 | -61.1481 | -61.2167 | -0.44861 | 60.6354 | -60.9192 | 60.8002 | -60.9695 | -61.0336 | -61.1755 | 0.077819 | -0.22888 | 0.14191 | 0.18768 | -0.29755 | -0.22888 | -0.37537 | -0.3067 | 0 | -0.21515 | -0.050354 | -0.050354 | -0.25635 | -0.11444 | -0.25635 | -0.11444 | 0.10986 | 121.8338 | -0.050354 | 121.7194 | 121.463 | 121.5546 | 121.5408 | 121.5546 | -121.6919 | -121.7697 | 121.9116 | 121.7194 | 60.4568 | 60.4706
294.9688 | 121.8979 | -60.8688 | 60.9192 | -0.009308 | 5.5563 | 0.066541 | 0.064929 | -0.001568 | -0.0059003 | -0.00044443 | -0.0036011 | 0.002446 | 0.068225 | 0.05721 | -0.0083355 | 0.015917 | 0.00012601 | -0.3891 | 60.6903 | -60.791 | 61.0748 | -60.6171 | -61.0291 | -61.116 | -0.3479 | 60.672 | -60.8551 | 60.8597 | -60.8688 | -60.9238 | -61.1252 | 0.077819 | -0.22888 | 0.15564 | 0.25177 | -0.24719 | -0.16022 | -0.32501 | -0.23804 | 0.013732 | -0.24719 | -0.059509 | 0 | -0.25635 | -0.054932 | -0.27008 | -0.068664 | 0.17395 | 121.8658 | -0.013732 | 121.7148 | 121.4813 | 121.5271 | 121.5591 | 121.5408 | -121.7102 | -121.7743 | 121.9437 | 121.7285 | 60.4797 | 60.5209
296.7031 | 122.0398 | -60.8871 | 60.7819 | 0.005951 | 5.6708 | 0.06825 | 0.063433 | 0.0027044 | -0.0044049 | -0.002367 | -0.0036011 | 0.0022324 | 0.067584 | 0.063405 | -0.0021405 | 0.017626 | -0.0052146 | -0.44403 | 60.5484 | -60.8414 | 61.0703 | -60.6125 | -61.0565 | -61.1343 | -0.32959 | 60.5392 | -60.9146 | 60.9192 | -60.8368 | -60.9238 | -61.0931 | 0.045776 | -0.23346 | 0.28839 | 0.27466 | -0.24719 | -0.16937 | -0.29297 | -0.21515 | -0.027466 | -0.24261 | 0.13733 | 0.050354 | -0.20599 | -0.036621 | -0.17853 | -0.009155 | 0.22888 | 121.9116 | 0.07782 | 121.8338 | 121.3898 | 121.4539 | 121.4355 | 121.4264 | -121.6232 | -121.6965 | 121.9574 | 121.8063 | 60.4431 | 60.5576
298.4375 | 121.9711 | -60.9375 | 60.8185 | -0.0016785 | 5.5258 | 0.067182 | 0.06621 | -0.00049983 | -0.0048321 | -0.001726 | -0.00054933 | 0.0026596 | 0.067157 | 0.069173 | -0.00021791 | 0.020617 | -0.00094199 | -0.46692 | 60.6354 | -60.8551 | 60.9787 | -60.7086 | -61.1389 | -61.2213 | -0.43488 | 60.5988 | -60.9192 | 60.8459 | -60.9192 | -60.9879 | -61.1572 | 0.082397 | -0.1831 | 0.16022 | 0.22888 | -0.28381 | -0.20142 | -0.36621 | -0.28381 | 0.018311 | -0.21973 | 0.027466 | 0.018311 | -0.21973 | -0.050354 | -0.23804 | -0.068665 | 0.14648 | 121.8338 | 0 | 121.7651 | 121.4905 | 121.5179 | 121.5729 | 121.5363 | -121.6736 | -121.7377 | 121.9162 | 121.7834 | 60.4706 | 60.5026
300.1719 | 121.9849 | -60.8963 | 60.8551 | 0.01358 | 5.5303 | 0.068464 | 0.064929 | -7.2628e-05 | -0.0033369 | -0.0010852 | 0.0055543 | 0.0020188 | 0.065021 | 0.055715 | -0.0029949 | 0.018908 | -0.0011558 | -0.41657 | 60.6171 | -60.8139 | 61.0611 | -60.6308 | -61.0474 | -61.1252 | -0.34332 | 60.6171 | -60.9009 | 60.91 | -60.8276 | -60.8871 | -61.0931 | 0.082397 | -0.23804 | 0.20599 | 0.2655 | -0.22888 | -0.15106 | -0.31128 | -0.23346 | -0.004578 | -0.23804 | 0.054931 | 0.068664 | -0.19684 | 0.009155 | -0.19226 | 0.013733 | 0.18311 | 121.875 | 0.073242 | 121.8109 | 121.431 | 121.5179 | 121.5134 | 121.5134 | -121.669 | -121.756 | 121.9574 | 121.8063 | 60.4797 | 60.553
301.8594 | 121.9574 | -60.8551 | 60.9055 | -0.0016785 | 3.6854 | 0.067823 | 0.063433 | 0.00185 | -0.0044049 | -0.0025806 | -0.00054933 | 0.002446 | 0.067157 | 0.058492 | -0.0051313 | 0.016131 | -0.0020102 | -0.32959 | 60.6491 | -60.7819 | 61.1618 | -60.5347 | -60.9192 | -61.0565 | -0.27008 | 60.6812 | -60.8139 | 60.9283 | -60.8047 | -60.8871 | -61.0703 | 0.073243 | -0.25635 | 0.25635 | 0.32043 | -0.20142 | -0.064086 | -0.27466 | -0.13733 | 0.041199 | -0.22431 | 0.022888 | 0.050354 | -0.21515 | -0.032043 | -0.25635 | -0.073242 | 0.24719 | 121.9437 | 0.009155 | 121.7422 | 121.431 | 121.4951 | 121.5042 | 121.5363 | -121.6873 | -121.7194 | 122.0169 | 121.7834 | 60.5255 | 60.585
303.6094 | 122.0032 | -60.8963 | 60.8139 | 0.028839 | 3.4252 | 0.067823 | 0.065783 | 0.0022772 | -0.0037641 | 0.00083737 | 0.0086061 | 0.003514 | 0.069293 | 0.058065 | -0.0029949 | 0.018053 | -0.0045736 | -0.38452 | 60.5942 | -60.8231 | 61.1206 | -60.5667 | -61.0245 | -61.1023 | -0.28839 | 60.6308 | -60.9283 | 60.8917 | -60.8551 | -60.91 | -61.116 | 0.073242 | -0.21973 | 0.3067 | 0.32959 | -0.20599 | -0.12817 | -0.27924 | -0.20142 | -0.032044 | -0.18311 | 0.07782 | 0.041198 | -0.21973 | -0.013733 | -0.18768 | 0.018311 | 0.25635 | 121.9437 | 0.073242 | 121.8201 | 121.4172 | 121.5591 | 121.4905 | 121.5271 | -121.637 | -121.7422 | 122.0169 | 121.788 | 60.5118 | 60.6079
305.2656 | 122.0306 | -60.8414 | 60.8597 | -0.0016785 | 0 | 0.066328 | 0.062365 | -0.003277 | -0.0063275 | 0.00041017 | -0.00054933 | 0.0009506 | 0.06673 | 0.060415 | -0.0038495 | 0.017626 | -0.001583 | -0.3479 | 60.6033 | -60.7864 | 61.1893 | -60.466 | -60.8917 | -61.0016 | -0.21515 | 60.6354 | -60.8368 | 60.9787 | -60.7315 | -60.791 | -61.0245 | 0.054932 | -0.25635 | 0.32959 | 0.37537 | -0.16022 | -0.050354 | -0.21515 | -0.10529 | 0.004578 | -0.2243 | 0.11902 | 0.10986 | -0.18311 | 0.050354 | -0.18768 | 0.045776 | 0.32043 | 121.9757 | 0.10529 | 121.8155 | 121.3898 | 121.4722 | 121.4447 | 121.4767 | -121.6461 | -121.6965 | 122.0306 | 121.8201 | 60.4935 | 60.6262
307 | 121.8887 | -60.9421 | 60.8551 | -0.0016785 | 0 | 0.069105 | 0.066851 | 0.0054816 | -0.0041913 | -0.0010852 | -0.0036011 | 0.0047958 | 0.067157 | 0.063619 | -0.0072675 | 0.016985 | -0.0013694 | -0.39368 | 60.6262 | -60.8276 | 61.0428 | -60.6537 | -61.0794 | -61.1847 | -0.37994 | 60.6354 | -60.8871 | 60.8047 | -60.9375 | -61.0107 | -61.1755 | 0.11444 | -0.22888 | 0.18768 | 0.28839 | -0.24261 | -0.13733 | -0.35705 | -0.25177 | 0.054932 | -0.21973 | -0.050354 | 0.004578 | -0.23346 | -0.068664 | -0.28839 | -0.1236 | 0.17395 | 121.8704 | -0.050354 | 121.6919 | 121.4539 | 121.5225 | 121.5683 | 121.5775 | -121.6827 | -121.7422 | 121.9849 | 121.7468 | 60.5484 | 60.5621
308.75 | 122.0123 | -60.8963 | 60.7956 | -0.0016785 | 0 | 0.069532 | 0.063647 | 0.0012092 | -0.0041913 | -0.002367 | 0.011658 | 0.0005234 | 0.068225 | 0.061696 | -0.0023541 | 0.01848 | -0.003292 | -0.41199 | 60.5347 | -60.8368 | 61.1023 | -60.5576 | -61.0016 | -61.1023 | -0.29297 | 60.6033 | -60.9283 | 60.9055 | -60.8276 | -60.9055 | -61.1069 | 0.059509 | -0.26092 | 0.3067 | 0.33875 | -0.20599 | -0.10529 | -0.2655 | -0.16479 | -0.032044 | -0.19226 | 0.10986 | 0.068664 | -0.21057 | -0.009156 | -0.17853 | 0.022888 | 0.27924 | 121.9391 | 0.10071 | 121.8338 | 121.3715 | 121.5317 | 121.431 | 121.4996 | -121.6324 | -121.7239 | 121.9986 | 121.8018 | 60.4843 | 60.6033
310.4219 | 122.0123 | -60.8688 | 60.7636 | -0.0016785 | 0 | 0.068464 | 0.063006 | 0.00014097 | -0.0014141 | -0.001726 | 0.0025025 | 0.000737 | 0.065234 | 0.065328 | -0.0025677 | 0.019549 | -0.0058554 | -0.46692 | 60.5713 | -60.8414 | 61.0336 | -60.6445 | -61.084 | -61.1481 | -0.37079 | 60.553 | -60.8963 | 60.9238 | -60.8459 | -60.9146 | -61.0977 | 0.027465 | -0.19226 | 0.27008 | 0.2243 | -0.27924 | -0.21515 | -0.3067 | -0.24261 | -0.027466 | -0.21057 | 0.16022 | 0.022888 | -0.22888 | -0.045777 | -0.20142 | -0.018311 | 0.19684 | 121.875 | 0.050354 | 121.8201 | 121.4127 | 121.4493 | 121.4401 | 121.4218 | -121.6049 | -121.6599 | 121.9025 | 121.7926 | 60.4019 | 60.498
312.1562 | 121.8979 | -60.878 | 60.9146 | 0.005951 | 0 | 0.065046 | 0.06386 | 0.0014228 | -0.0065411 | 0.00041017 | -0.00054933 | 0.002446 | 0.068866 | 0.05187 | -0.0079083 | 0.016985 | -0.0024374 | -0.39368 | 60.6857 | -60.8002 | 61.0474 | -60.6354 | -61.0291 | -61.1206 | -0.37537 | 60.6766 | -60.8643 | 60.8505 | -60.8871 | -60.9375 | -61.1206 | 0.07782 | -0.22888 | 0.13275 | 0.24262 | -0.24261 | -0.15106 | -0.32043 | -0.22888 | 0.013733 | -0.23804 | -0.064087 | -0.009155 | -0.24261 | -0.059509 | -0.25635 | -0.073242 | 0.16479 | 121.8475 | -0.022888 | 121.7148 | 121.4859 | 121.5408 | 121.5637 | 121.5546 | -121.7148 | -121.7789 | 121.9254 | 121.7285 | 60.4843 | 60.5026
313.8906 | 121.9757 | -60.8917 | 60.8185 | 0.02121 | 0 | 0.06825 | 0.063433 | 0.0024908 | -0.0050457 | -0.00023063 | 0.0025025 | 0.0013778 | 0.070361 | 0.068105 | -0.0032087 | 0.015917 | -0.001583 | -0.42572 | 60.5942 | -60.8414 | 61.0703 | -60.585 | -61.0291 | -61.1069 | -0.33417 | 60.6079 | -60.9421 | 60.8826 | -60.8551 | -60.91 | -61.116 | 0.050354 | -0.2243 | 0.25177 | 0.3067 | -0.21515 | -0.13733 | -0.2655 | -0.18768 | -0.050354 | -0.21057 | 0.064087 | 0.036621 | -0.2243 | -0.01831 | -0.17395 | 0.032044 | 0.25635 | 121.9116 | 0.086975 | 121.8246 | 121.4355 | 121.55 | 121.4859 | 121.4996 | -121.6599 | -121.7606 | 121.962 | 121.7743 | 60.466 | 60.5576
315.5781 | 122.0352 | -60.8414 | 60.8551 | -0.016937 | 0 | 0.067823 | 0.064074 | 0.0039862 | -0.0061139 | -0.0025806 | -0.00054933 | 0.0020188 | 0.068225 | 0.05721 | -0.0042767 | 0.017199 | -0.0017966 | -0.37079 | 60.6171 | -60.7727 | 61.1389 | -60.5072 | -60.9283 | -61.0245 | -0.21973 | 60.6445 | -60.8414 | 60.9879 | -60.7315 | -60.791 | -61.0199 | 0.068665 | -0.23804 | 0.28381 | 0.33417 | -0.18311 | -0.086975 | -0.25177 | -0.15564 | 0 | -0.21057 | 0.13275 | 0.10986 | -0.17853 | 0.050354 | -0.17853 | 0.050354 | 0.2655 | 121.9116 | 0.10986 | 121.8292 | 121.3898 | 121.4859 | 121.4584 | 121.4859 | -121.6278 | -121.6965 | 121.9803 | 121.8292 | 60.4706 | 60.6216
317.2969 | 121.9803 | -60.8414 | 60.8414 | 0.02121 | 0 | 0.068464 | 0.063006 | 0.0016364 | -0.0029095 | -0.0032214 | -0.00054933 | 0.0028732 | 0.067157 | 0.06426 | -0.0029949 | 0.01784 | -0.002651 | -0.42572 | 60.5896 | -60.8231 | 61.0611 | -60.6125 | -61.0382 | -61.1206 | -0.33875 | 60.6125 | -60.8688 | 60.9055 | -60.8231 | -60.8871 | -61.0703 | 0.018311 | -0.25177 | 0.21973 | 0.22888 | -0.27923 | -0.19684 | -0.29755 | -0.21515 | -0.027465 | -0.22888 | 0.064087 | 0.018311 | -0.22888 | -0.045776 | -0.20142 | -0.018311 | 0.21057 | 121.8842 | 0.045776 | 121.7743 | 121.4127 | 121.4813 | 121.431 | 121.4539 | -121.6644 | -121.7102 | 121.9025 | 121.7468 | 60.4156 | 60.5026
319.0312 | 121.9711 | -60.8734 | 60.8414 | 0.005951 | 0 | 0.068891 | 0.064288 | -0.002636 | -0.0029095 | -0.0025806 | 0.0055543 | 0.0030868 | 0.067157 | 0.060842 | -0.0042767 | 0.01848 | -0.00051479 | -0.41657 | 60.5988 | -60.8276 | 61.0886 | -60.5896 | -61.0199 | -61.0977 | -0.33417 | 60.6171 | -60.91 | 60.8734 | -60.8597 | -60.91 | -61.1069 | 0.045776 | -0.24262 | 0.24719 | 0.28381 | -0.2243 | -0.14648 | -0.27008 | -0.19226 | -0.036621 | -0.22431 | 0.032043 | 0.013733 | -0.23346 | -0.036621 | -0.19684 | 0 | 0.23804 | 121.9162 | 0.050354 | 121.7834 | 121.4264 | 121.5271 | 121.4722 | 121.4905 | -121.669 | -121.7514 | 121.962 | 121.7468 | 60.4568 | 60.5392
320.7031 | 121.9894 | -60.8826 | 60.7956 | 0.005951 | 0 | 0.066114 | 0.065142 | 0.0031318 | -0.0031231 | -0.0032214 | -0.0036011 | 0.002446 | 0.067798 | 0.058492 | -0.0042767 | 0.017199 | -8.7586e-05 | -0.46234 | 60.5804 | -60.8459 | 61.0245 | -60.6537 | -61.0794 | -61.1801 | -0.35248 | 60.5804 | -60.9192 | 60.8826 | -60.8688 | -60.9329 | -61.1069 | 0.036621 | -0.21515 | 0.22888 | 0.22888 | -0.29755 | -0.19684 | -0.33417 | -0.23346 | -0.036621 | -0.21515 | 0.086975 | 0.013733 | -0.22431 | -0.050354 | -0.18768 | -0.013733 | 0.19226 | 121.8704 | 0.050354 | 121.8018 | 121.4264 | 121.4996 | 121.463 | 121.463 | -121.6415 | -121.7148 | 121.907 | 121.7651 | 60.4202 | 60.5301
322.4375 | 122.0032 | -60.8505 | 60.8459 | 0.005951 | 0 | 0.068037 | 0.06386 | -0.00092703 | -0.0044049 | -1.7026e-05 | 0.0025025 | 0.0005234 | 0.067157 | 0.072378 | -0.0059857 | 0.017199 | 0.0011942 | -0.43945 | 60.6079 | -60.7956 | 61.0657 | -60.6079 | -61.0199 | -61.0794 | -0.33417 | 60.6033 | -60.8734 | 60.9146 | -60.8139 | -60.8551 | -61.0657 | 0.054932 | -0.23804 | 0.21973 | 0.24262 | -0.22888 | -0.16937 | -0.28381 | -0.2243 | -0.022888 | -0.24261 | 0.068665 | 0.036621 | -0.21515 | -0.004578 | -0.19226 | 0.01831 | 0.18768 | 121.8613 | 0.059509 | 121.788 | 121.4035 | 121.4767 | 121.4584 | 121.4539 | -121.6415 | -121.7194 | 121.9162 | 121.7651 | 60.4111 | 60.5164
324.1094 | 121.9711 | -60.878 | 60.8139 | 0.036468 | 0 | 0.069105 | 0.064929 | -0.00092703 | -0.0050457 | 0.00019657 | 0.0055543 | 0.0026596 | 0.06737 | 0.070882 | -0.0049175 | 0.017626 | -0.00030119 | -0.41199 | 60.5896 | -60.8459 | 61.0977 | -60.5667 | -61.0336 | -61.1023 | -0.3067 | 60.585 | -60.9009 | 60.8963 | -60.8322 | -60.9146 | -61.1114 | 0.032044 | -0.2243 | 0.28381 | 0.31128 | -0.2243 | -0.15564 | -0.25635 | -0.18768 | -0.022888 | -0.22888 | 0.082397 | 0.045777 | -0.23346 | -0.036621 | -0.21057 | -0.013733 | 0.27924 | 121.9437 | 0.068665 | 121.7972 | 121.4355 | 121.4859 | 121.4676 | 121.463 | -121.6599 | -121.7148 | 121.9757 | 121.7743 | 60.466 | 60.5713
325.8438 | 121.9391 | -60.8917 | 60.8322 | 0.02121 | 0 | 0.069532 | 0.067919 | 0.0029182 | -0.0026959 | 0.00083737 | 0.0055543 | 0.0054368 | 0.066302 | 0.056997 | -0.0076947 | 0.017199 | -0.0017966 | -0.35706 | 60.6537 | -60.8322 | 61.0703 | -60.585 | -61.0199 | -61.116 | -0.3067 | 60.6537 | -60.8871 | 60.8826 | -60.8459 | -60.9238 | -61.1069 | 0.05951 | -0.17853 | 0.23804 | 0.3067 | -0.2243 | -0.12817 | -0.28381 | -0.18768 | 0.004578 | -0.17853 | 0.050354 | 0.045777 | -0.21515 | -0.032043 | -0.21973 | -0.036621 | 0.24719 | 121.9025 | 0.041199 | 121.7697 | 121.4859 | 121.5408 | 121.5454 | 121.5454 | -121.6644 | -121.7194 | 121.962 | 121.7743 | 60.5347 | 60.585
327.5156 | 122.0123 | -60.8231 | 60.8322 | 0.005951 | 0 | 0.065473 | 0.06386 | 0.00099557 | -0.0026959 | -0.00065803 | -0.00054933 | 0.0022324 | 0.067157 | 0.058278 | -0.0032087 | 0.017626 | -0.00436 | -0.41199 | 60.6125 | -60.7956 | 61.1298 | -60.5347 | -60.9558 | -61.0428 | -0.2655 | 60.6308 | -60.8414 | 60.9604 | -60.7407 | -60.8093 | -61.0199 | 0.027466 | -0.21973 | 0.29755 | 0.28839 | -0.21973 | -0.13275 | -0.24719 | -0.16022 | -0.018311 | -0.20142 | 0.12817 | 0.082397 | -0.19684 | 0.013733 | -0.17853 | 0.032044 | 0.26092 | 121.9254 | 0.10071 | 121.8018 | 121.4081 | 121.4722 | 121.4355 | 121.4539 | -121.6278 | -121.6736 | 121.9528 | 121.7834 | 60.4111 | 60.5576
329.25 | 121.9254 | -60.8597 | 60.9055 | 0.036468 | 0 | 0.066969 | 0.067919 | 0.005268 | -0.0050457 | -0.00044443 | 0.014709 | 0.0018052 | 0.067584 | 0.058706 | -0.0081219 | 0.016131 | -0.0028646 | -0.37994 | 60.704 | -60.8093 | 61.0565 | -60.6308 | -61.0291 | -61.1114 | -0.36163 | 60.6949 | -60.878 | 60.8643 | -60.8505 | -60.9055 | -61.1023 | 0.050354 | -0.20142 | 0.15106 | 0.22888 | -0.25177 | -0.16937 | -0.30212 | -0.21973 | -0.018311 | -0.21057 | -0.041199 | 0.009155 | -0.24262 | -0.045777 | -0.2243 | -0.027466 | 0.17853 | 121.8658 | 0.027466 | 121.7422 | 121.5134 | 121.5729 | 121.5637 | 121.5546 | -121.7148 | -121.7834 | 121.9162 | 121.7239 | 60.4797 | 60.498
330.9844 | 122.0261 | -60.8505 | 60.8505 | 0.005951 | 0 | 0.065687 | 0.062792 | -0.0011408 | -0.0039777 | 0.00041017 | -0.00054933 | 0.0003098 | 0.068225 | 0.059987 | -0.0040631 | 0.016131 | -0.0041464 | -0.38452 | 60.6308 | -60.7864 | 61.1343 | -60.5164 | -60.9238 | -61.0245 | -0.23804 | 60.6216 | -60.8688 | 60.9604 | -60.7361 | -60.7956 | -61.0245 | 0.064087 | -0.21973 | 0.28381 | 0.33417 | -0.17395 | -0.073242 | -0.23804 | -0.13733 | -0.01831 | -0.22888 | 0.10986 | 0.11444 | -0.17395 | 0.054932 | -0.15564 | 0.073242 | 0.27008 | 121.9208 | 0.13275 | 121.8292 | 121.4172 | 121.4905 | 121.4813 | 121.4722 | -121.637 | -121.7194 | 121.9849 | 121.8109 | 60.466 | 60.6125
332.6562 | 121.8704 | -60.91 | 60.8231 | -0.0016785 | 0 | 0.06825 | 0.067706 | 0.00056817 | -0.0046185 | -0.00044443 | -0.00054933 | 0.0033004 | 0.068225 | 0.056569 | -0.0036359 | 0.016772 | -0.001583 | -0.42572 | 60.64 | -60.8276 | 61.0291 | -60.6537 | -61.1069 | -61.1893 | -0.41657 | 60.6262 | -60.91 | 60.8047 | -60.9421 | -61.0153 | -61.1755 | 0.082397 | -0.1831 | 0.20599 | 0.25635 | -0.27924 | -0.19684 | -0.36163 | -0.27924 | 0 | -0.19684 | -0.01831 | -0.032044 | -0.2655 | -0.10529 | -0.2655 | -0.10529 | 0.17395 | 121.8567 | -0.032044 | 121.7148 | 121.4676 | 121.5363 | 121.55 | 121.5363 | -121.6507 | -121.7331 | 121.9391 | 121.7148 | 60.4843 | 60.4935
334.3906 | 121.9025 | -60.8688 | 60.8871 | 0.02121 | 0 | 0.065901 | 0.066424 | -0.00049983 | -0.0041913 | 0.001051 | 0.0086061 | 0.0054368 | 0.069507 | 0.062124 | -0.0087629 | 0.015917 | -8.7586e-05 | -0.38452 | 60.6812 | -60.8322 | 61.0519 | -60.6171 | -61.0153 | -61.1023 | -0.35248 | 60.6995 | -60.8826 | 60.8734 | -60.8459 | -60.91 | -61.0931 | 0.036621 | -0.20599 | 0.16479 | 0.25177 | -0.23346 | -0.14649 | -0.27008 | -0.18311 | -0.013733 | -0.18768 | -0.013733 | 0.022888 | -0.22431 | -0.041199 | -0.21057 | -0.027466 | 0.21515 | 121.8842 | 0.036621 | 121.756 | 121.5134 | 121.582 | 121.55 | 121.5683 | -121.7194 | -121.7697 | 121.9208 | 121.7422 | 60.4843 | 60.5164
336.125 | 121.9254 | -60.8826 | 60.8597 | 0.028839 | 0 | 0.066328 | 0.065356 | -0.00092703 | -0.0052595 | 0.001051 | 0.011658 | 0.004155 | 0.06737 | 0.06661 | -0.0057721 | 0.016772 | -0.00051479 | -0.37537 | 60.6766 | -60.8231 | 61.0565 | -60.6171 | -60.997 | -61.0931 | -0.35706 | 60.6766 | -60.8917 | 60.878 | -60.8459 | -60.9329 | -61.0886 | 0.059509 | -0.1831 | 0.19684 | 0.2655 | -0.21057 | -0.11444 | -0.27008 | -0.17395 | -0.009156 | -0.1831 | 0.018311 | 0.036621 | -0.20599 | -0.050354 | -0.19684 | -0.041198 | 0.20599 | 121.8796 | 0.045777 | 121.7697 | 121.4996 | 121.5683 | 121.5591 | 121.5591 | -121.6827 | -121.7514 | 121.9391 | 121.7606 | 60.5072 | 60.5255
337.8594 | 121.9254 | -60.9146 | 60.8002 | -0.009308 | 0 | 0.068464 | 0.06621 | 0.0022772 | -0.0050457 | -0.0015124 | -0.00054933 | 0.0037278 | 0.06737 | 0.057424 | -0.0027813 | 0.016772 | -0.0020102 | -0.48981 | 60.6308 | -60.8459 | 60.965 | -60.6995 | -61.1252 | -61.2122 | -0.42572 | 60.6079 | -60.9009 | 60.8047 | -60.9238 | -61.0153 | -61.1618 | 0.068665 | -0.16937 | 0.16479 | 0.21515 | -0.29755 | -0.21057 | -0.36621 | -0.27924 | 0.013733 | -0.19226 | 0.004578 | -0.009155 | -0.24719 | -0.10071 | -0.26092 | -0.11444 | 0.14648 | 121.8109 | -0.022888 | 121.7056 | 121.4767 | 121.5088 | 121.5454 | 121.5225 | -121.6461 | -121.7011 | 121.8796 | 121.7194 | 60.4248 | 60.4889
339.5469 | 121.9986 | -60.8505 | 60.8368 | 0.005951 | 0 | 0.065901 | 0.06322 | -0.0041314 | -0.0046185 | -0.0032214 | -0.0036011 | 0.0003098 | 0.06737 | 0.058492 | -0.0034223 | 0.01784 | -0.002651 | -0.37537 | 60.6308 | -60.7681 | 61.1389 | -60.5118 | -60.9283 | -61.0199 | -0.24261 | 60.6216 | -60.8459 | 60.9467 | -60.7407 | -60.8002 | -61.0016 | 0.082398 | -0.20599 | 0.30212 | 0.33874 | -0.16937 | -0.07782 | -0.25177 | -0.16022 | 0.004578 | -0.21515 | 0.10986 | 0.10986 | -0.15106 | 0.050354 | -0.15564 | 0.045776 | 0.25635 | 121.907 | 0.10529 | 121.7926 | 121.3989 | 121.4676 | 121.4813 | 121.4722 | -121.6049 | -121.6827 | 121.9894 | 121.7972 | 60.4752 | 60.6079
341.2812 | 121.9162 | -60.8688 | 60.8368 | 0.01358 | 0 | 0.069319 | 0.066638 | 0.0020636 | -0.0054731 | 0.0023328 | 0.0055543 | 0.0050094 | 0.06673 | 0.051229 | -0.0044903 | 0.016772 | -0.0075644 | -0.36621 | 60.6766 | -60.8139 | 61.0703 | -60.5896 | -61.0153 | -61.1023 | -0.32044 | 60.672 | -60.8597 | 60.8826 | -60.8231 | -60.9192 | -61.0886 | 0.054931 | -0.16022 | 0.23346 | 0.27923 | -0.23346 | -0.14649 | -0.28839 | -0.20142 | 0.009155 | -0.1648 | 0.045776 | 0.045776 | -0.21973 | -0.050354 | -0.22888 | -0.059509 | 0.2243 | 121.8842 | 0.036621 | 121.7422 | 121.4905 | 121.5317 | 121.5454 | 121.5408 | -121.6507 | -121.6965 | 121.9391 | 121.7514 | 60.5026 | 60.5484
342.9375 | 121.8796 | -60.8643 | 60.8963 | -0.009308 | 0 | 0.065473 | 0.064929 | -7.2628e-05 | -0.0052595 | -0.0019396 | -0.00054933 | 0.0022324 | 0.06737 | 0.061696 | -0.0040631 | 0.017626 | -0.0020102 | -0.35706 | 60.6674 | -60.7773 | 61.0886 | -60.5484 | -60.9833 | -61.0657 | -0.32501 | 60.6766 | -60.8368 | 60.8734 | -60.8322 | -60.9009 | -61.1069 | 0.086975 | -0.22888 | 0.19226 | 0.31586 | -0.20142 | -0.11902 | -0.28839 | -0.20599 | 0.027466 | -0.21973 | -0.022888 | 0.032044 | -0.24262 | -0.036621 | -0.27008 | -0.064087 | 0.22888 | 121.8658 | 0.004578 | 121.7102 | 121.4447 | 121.5134 | 121.5317 | 121.5408 | -121.6736 | -121.7331 | 121.9528 | 121.7377 | 60.5072 | 60.5392
344.6719 | 121.8567 | -60.8688 | 60.8963 | -0.0016785 | 0 | 0.066541 | 0.065142 | 0.00099557 | -0.0061139 | -0.0019396 | -0.0036011 | 0.0003098 | 0.068438 | 0.052511 | -0.0059857 | 0.016131 | -0.0020102 | -0.41199 | 60.6857 | -60.7819 | 61.0291 | -60.6262 | -61.0245 | -61.1114 | -0.39368 | 60.7269 | -60.8734 | 60.8459 | -60.8505 | -60.9375 | -61.116 | 0.086975 | -0.21057 | 0.13275 | 0.24261 | -0.24262 | -0.15564 | -0.32959 | -0.24262 | -0.004578 | -0.16937 | -0.050354 | 0.01831 | -0.24719 | -0.068665 | -0.24262 | -0.064087 | 0.15564 | 121.8109 | 0.022888 | 121.7194 | 121.4676 | 121.6003 | 121.5546 | 121.5958 | -121.6782 | -121.7697 | 121.8979 | 121.7148 | 60.4568 | 60.4752
346.4062 | 121.9574 | -60.8734 | 60.8231 | 0.01358 | 0 | 0.069319 | 0.063647 | 0.00035457 | -0.0033369 | 0.00041017 | 0.0055543 | 0.0005234 | 0.069507 | 0.063619 | -0.0029949 | 0.017626 | -0.002651 | -0.43488 | 60.6125 | -60.7956 | 61.0611 | -60.6033 | -61.0291 | -61.1023 | -0.36163 | 60.5988 | -60.878 | 60.8871 | -60.8368 | -60.8871 | -61.0886 | 0.07782 | -0.21057 | 0.23804 | 0.27008 | -0.22888 | -0.15564 | -0.3067 | -0.23346 | -0.004578 | -0.2243 | 0.064087 | 0.036621 | -0.21515 | -0.013733 | -0.21057 | -0.009155 | 0.19226 | 121.8567 | 0.041199 | 121.7651 | 121.4081 | 121.4767 | 121.4859 | 121.4722 | -121.6187 | -121.7011 | 121.9345 | 121.7606 | 60.4385 | 60.5118
348.0781 | 121.9208 | -60.9238 | 60.8047 | -0.0016785 | 0 | 0.065901 | 0.064501 | -0.00049983 | -0.0050457 | -0.0025806 | -0.0036011 | 0.0022324 | 0.068866 | 0.060415 | -0.0029949 | 0.018267 | -0.00436 | -0.48981 | 60.6033 | -60.8368 | 60.9741 | -60.6949 | -61.1343 | -61.2167 | -0.43945 | 60.5942 | -60.9238 | 60.8322 | -60.9055 | -60.9833 | -61.1435 | 0.086975 | -0.20142 | 0.16937 | 0.22888 | -0.29297 | -0.21057 | -0.37994 | -0.29755 | 0 | -0.21057 | 0.027465 | 0.01831 | -0.21973 | -0.059509 | -0.21973 | -0.059509 | 0.14191 | 121.8109 | 0.01831 | 121.756 | 121.4401 | 121.5179 | 121.5271 | 121.5179 | -121.6415 | -121.7285 | 121.8979 | 121.756 | 60.434 | 60.4843
349.8281 | 121.8887 | -60.9329 | 60.8002 | 0.005951 | 0 | 0.066541 | 0.067278 | 0.00056817 | -0.0050457 | -0.0019396 | -0.0036011 | 0.0026596 | 0.068438 | 0.060201 | -0.0051313 | 0.017412 | -0.0041464 | -0.48981 | 60.5988 | -60.8459 | 60.9467 | -60.7132 | -61.1252 | -61.1938 | -0.4303 | 60.6079 | -60.9238 | 60.8093 | -60.9283 | -61.0153 | -61.1618 | 0.086975 | -0.20142 | 0.14648 | 0.21973 | -0.26093 | -0.19226 | -0.3479 | -0.27924 | 0.009155 | -0.19226 | 0.009155 | 0.004577 | -0.22888 | -0.082398 | -0.23804 | -0.091553 | 0.13275 | 121.7926 | -0.004578 | 121.7331 | 121.4447 | 121.5317 | 121.5317 | 121.5408 | -121.6461 | -121.7239 | 121.8796 | 121.7422 | 60.4431 | 60.5026
351.5 | 121.8842 | -60.9192 | 60.7956 | -0.0016785 | 0 | 0.066114 | 0.065783 | -0.001568 | -0.0046185 | -0.00023063 | -0.00054933 | 0.0022324 | 0.066302 | 0.05956 | -0.0034223 | 0.016772 | -0.0024374 | -0.49896 | 60.6308 | -60.8505 | 60.9558 | -60.7132 | -61.1435 | -61.1984 | -0.42114 | 60.6171 | -60.9055 | 60.7864 | -60.9329 | -61.0153 | -61.1618 | 0.068664 | -0.16479 | 0.16022 | 0.20599 | -0.27924 | -0.2243 | -0.3479 | -0.29297 | 0.013732 | -0.17853 | -0.009155 | -0.013733 | -0.24261 | -0.096131 | -0.25635 | -0.10986 | 0.13733 | 121.8063 | -0.027465 | 121.6919 | 121.4813 | 121.5225 | 121.55 | 121.5363 | -121.6461 | -121.701 | 121.875 | 121.7056 | 60.4202 | 60.498
353.2188 | 121.9803 | -60.9055 | 60.759 | 0.005951 | 0 | 0.066114 | 0.065783 | 0.0020636 | -0.0037641 | -0.0015124 | -0.0036011 | 0.0011642 | 0.069507 | 0.056142 | -0.0029949 | 0.018053 | -0.0041464 | -0.49896 | 60.5804 | -60.8459 | 61.0062 | -60.6537 | -61.0931 | -61.171 | -0.35706 | 60.5667 | -60.9009 | 60.878 | -60.8414 | -60.9375 | -61.0931 | 0.05951 | -0.17853 | 0.24719 | 0.25177 | -0.2655 | -0.18768 | -0.32501 | -0.24719 | 0.004578 | -0.19226 | 0.11902 | 0.064087 | -0.18768 | -0.032043 | -0.19226 | -0.036621 | 0.19226 | 121.8521 | 0.059509 | 121.7789 | 121.4264 | 121.4676 | 121.4859 | 121.4722 | -121.6049 | -121.6599 | 121.9116 | 121.7834 | 60.4065 | 60.5484
354.9531 | 121.8567 | -60.8459 | 60.9055 | -0.009308 | 0 | 0.066328 | 0.064074 | -0.00071343 | -0.0046185 | -0.00087163 | -0.0036011 | 0.002446 | 0.067157 | 0.056356 | -0.0059857 | 0.01848 | -0.006069 | -0.42572 | 60.6766 | -60.8002 | 61.0291 | -60.6079 | -61.0245 | -61.1114 | -0.39368 | 60.6812 | -60.8276 | 60.8414 | -60.8414 | -60.9146 | -61.0931 | 0.045776 | -0.22888 | 0.1236 | 0.23804 | -0.2655 | -0.17853 | -0.31128 | -0.2243 | 0.01831 | -0.22431 | -0.064087 | 0.004577 | -0.24719 | -0.068665 | -0.2655 | -0.086975 | 0.19226 | 121.8292 | -0.013733 | 121.669 | 121.4767 | 121.5088 | 121.5225 | 121.5271 | -121.7056 | -121.7331 | 121.875 | 121.6873 | 60.4202 | 60.4523
356.6875 | 121.9437 | -60.8826 | 60.8002 | 0.02121 | 0 | 0.068037 | 0.065997 | 0.0014228 | -0.0033369 | -0.00087163 | 0.0086061 | 0.0043686 | 0.067798 | 0.070669 | -0.0025677 | 0.018908 | -0.0028646 | -0.42114 | 60.6033 | -60.8231 | 61.084 | -60.5392 | -61.0245 | -61.1069 | -0.30212 | 60.5896 | -60.9055 | 60.8917 | -60.8276 | -60.8963 | -61.084 | 0.059509 | -0.19684 | 0.28381 | 0.34332 | -0.22431 | -0.14191 | -0.28381 | -0.20142 | -0.022889 | -0.21057 | 0.091553 | 0.054931 | -0.20142 | -0.013733 | -0.17853 | 0.009156 | 0.28381 | 121.907 | 0.07782 | 121.7972 | 121.4264 | 121.4951 | 121.4859 | 121.4722 | -121.6232 | -121.7056 | 121.9666 | 121.7743 | 60.4614 | 60.5804
358.3594 | 122.0123 | -60.8826 | 60.7864 | -0.0016785 | 0 | 0.065687 | 0.063433 | 0.0029182 | -0.0044049 | -0.00044443 | -0.0036011 | 0.003514 | 0.066516 | 0.058065 | -0.00043151 | 0.019121 | -0.0011558 | -0.44403 | 60.5484 | -60.8368 | 61.0565 | -60.585 | -61.0291 | -61.1069 | -0.32044 | 60.5347 | -60.91 | 60.8871 | -60.8185 | -60.8917 | -61.084 | 0.045776 | -0.23804 | 0.27008 | 0.29755 | -0.22431 | -0.14648 | -0.27008 | -0.19226 | -0.027466 | -0.25177 | 0.10071 | 0.064087 | -0.20142 | -0.009156 | -0.17395 | 0.01831 | 0.25177 | 121.8933 | 0.091553 | 121.7972 | 121.3852 | 121.4447 | 121.431 | 121.4172 | -121.6232 | -121.6965 | 121.9391 | 121.7697 | 60.4385 | 60.5621
360.1094 | 121.8658 | -60.9283 | 60.8231 | -0.0016785 | 0 | 0.069532 | 0.065356 | 0.006977 | -0.0056867 | 0.001692 | 0.0025025 | 0.002446 | 0.068011 | 0.056569 | -0.0049175 | 0.019335 | -0.0030784 | -0.48981 | 60.6262 | -60.8597 | 60.965 | -60.7178 | -61.1481 | -61.2167 | -0.4715 | 60.5804 | -60.9192 | 60.7819 | -60.9558 | -61.0336 | -61.171 | 0.068665 | -0.19684 | 0.14191 | 0.21057 | -0.28839 | -0.21973 | -0.35706 | -0.28839 | 0.009156 | -0.24262 | -0.041199 | -0.027466 | -0.24261 | -0.10529 | -0.25177 | -0.11444 | 0.14191 | 121.8246 | -0.036622 | 121.701 | 121.4859 | 121.4996 | 121.5546 | 121.5088 | -121.6827 | -121.7422 | 121.8933 | 121.7102 | 60.4385 | 60.4568
361.8438 | 121.9574 | -60.8597 | 60.8047 | 0.036468 | 0 | 0.06825 | 0.064929 | -7.2628e-05 | -0.0033369 | 0.0021192 | 0.014709 | 0.002446 | 0.067798 | 0.05956 | -0.0027813 | 0.019335 | -0.0039328 | -0.4303 | 60.5896 | -60.8368 | 61.0748 | -60.5484 | -61.0062 | -61.0931 | -0.3067 | 60.5759 | -60.9009 | 60.8826 | -60.8276 | -60.9055 | -61.0886 | 0.022888 | -0.21515 | 0.27008 | 0.31128 | -0.23346 | -0.14649 | -0.25635 | -0.16937 | -0.041199 | -0.22888 | 0.077819 | 0.032043 | -0.22888 | -0.045777 | -0.18768 | -0.004578 | 0.28839 | 121.9116 | 0.073242 | 121.7834 | 121.4264 | 121.4767 | 121.4493 | 121.4355 | -121.6415 | -121.7056 | 121.9345 | 121.7422 | 60.4294 | 60.553
363.5938 | 121.8613 | -60.9192 | 60.8414 | -0.0016785 | 0 | 0.068037 | 0.06621 | -0.00028623 | -0.0026959 | -0.0012988 | -0.0036011 | 0.0043686 | 0.065021 | 0.068532 | -0.0055585 | 0.018053 | -0.0011558 | -0.45319 | 60.6216 | -60.8368 | 60.9787 | -60.6812 | -61.0977 | -61.1984 | -0.42114 | 60.5988 | -60.8963 | 60.7819 | -60.9421 | -60.9924 | -61.1481 | 0.082397 | -0.21973 | 0.13733 | 0.23804 | -0.27924 | -0.17853 | -0.36163 | -0.26093 | 0.022888 | -0.24262 | -0.05951 | -0.022889 | -0.22888 | -0.073243 | -0.25177 | -0.096131 | 0.15564 | 121.8155 | -0.045777 | 121.6782 | 121.4584 | 121.4951 | 121.5408 | 121.5179 | -121.6782 | -121.7377 | 121.8979 | 121.701 | 60.466 | 60.498
365.2656 | 121.9162 | -60.8734 | 60.8597 | 0.01358 | 0 | 0.069105 | 0.067278 | 0.00099557 | -0.0026959 | -0.0027942 | 0.0086061 | 0.004155 | 0.066302 | 0.061696 | -0.0087629 | 0.01848 | 0.00012601 | -0.37537 | 60.6537 | -60.8139 | 61.0703 | -60.6033 | -61.0016 | -61.1023 | -0.3067 | 60.6583 | -60.8643 | 60.8643 | -60.8368 | -60.91 | -61.0886 | 0.059509 | -0.20599 | 0.21057 | 0.27008 | -0.22888 | -0.12817 | -0.28839 | -0.18768 | 0.009155 | -0.20142 | 0.004578 | 0.036621 | -0.21515 | -0.036621 | -0.2243 | -0.045776 | 0.21057 | 121.8842 | 0.027466 | 121.7285 | 121.4676 | 121.5225 | 121.5271 | 121.5317 | -121.6736 | -121.7239 | 121.9437 | 121.7377 | 60.498 | 60.5667
367 | 121.9849 | -60.8826 | 60.759 | -0.0016785 | 0 | 0.067396 | 0.063433 | 0.0027044 | -0.0050457 | -0.00087163 | -0.00054933 | 0.0005234 | 0.068225 | 0.057851 | -0.0032087 | 0.01848 | -0.00094199 | -0.42114 | 60.5438 | -60.8047 | 61.0519 | -60.5713 | -61.0245 | -61.1069 | -0.31586 | 60.5576 | -60.9146 | 60.9009 | -60.8047 | -60.8734 | -61.0794 | 0.077819 | -0.21515 | 0.29297 | 0.31128 | -0.22431 | -0.14191 | -0.30212 | -0.21973 | -0.032044 | -0.20142 | 0.14191 | 0.077819 | -0.19684 | 0.009155 | -0.1648 | 0.041199 | 0.23346 | 121.8567 | 0.10986 | 121.8155 | 121.3486 | 121.4722 | 121.4264 | 121.4401 | -121.5637 | -121.6736 | 121.9345 | 121.7834 | 60.4614 | 60.5667
368.7344 | 121.9574 | -60.8963 | 60.791 | -0.0016785 | 0 | 0.067823 | 0.066424 | -0.002636 | -0.0035505 | -0.00087163 | -0.0066527 | 0.0022324 | 0.068866 | 0.061696 | -0.0049175 | 0.01848 | -0.0020102 | -0.48981 | 60.6171 | -60.8505 | 60.9558 | -60.6857 | -61.1069 | -61.1847 | -0.41199 | 60.5896 | -60.9055 | 60.8551 | -60.8734 | -60.9375 | -61.1069 | 0.045776 | -0.17395 | 0.16479 | 0.21057 | -0.28839 | -0.21057 | -0.33417 | -0.25635 | -0.009156 | -0.20142 | 0.064087 | 0.022888 | -0.21057 | -0.041199 | -0.20142 | -0.032043 | 0.16479 | 121.8063 | 0.032044 | 121.7606 | 121.4676 | 121.4951 | 121.5134 | 121.4859 | -121.6415 | -121.6965 | 121.8521 | 121.7514 | 60.4065 | 60.4843
370.4062 | 121.8613 | -60.9283 | 60.8231 | -0.0016785 | 0 | 0.067823 | 0.064929 | 0.00035457 | -0.0046185 | -0.0010852 | -0.0066527 | 0.0045822 | 0.068438 | 0.057851 | -0.0042767 | 0.018053 | -0.003292 | -0.48981 | 60.6354 | -60.8322 | 60.9329 | -60.7498 | -61.1435 | -61.2213 | -0.48065 | 60.6033 | -60.9238 | 60.7727 | -60.9512 | -61.0291 | -61.1572 | 0.096131 | -0.18768 | 0.10986 | 0.17853 | -0.29297 | -0.21515 | -0.3891 | -0.31128 | 0.004578 | -0.21973 | -0.050354 | -0.022888 | -0.22888 | -0.10071 | -0.23346 | -0.10529 | 0.082397 | 121.7651 | -0.027466 | 121.6965 | 121.4676 | 121.5271 | 121.5637 | 121.5317 | -121.6553 | -121.7468 | 121.8613 | 121.7011 | 60.4385 | 60.4477
372.1406 | 121.9757 | -60.8322 | 60.8185 | -0.0016785 | 0 | 0.065687 | 0.061083 | 0.0024908 | -0.0050457 | 0.001051 | -0.0036011 | 0.002446 | 0.068225 | 0.061269 | -0.0047039 | 0.017199 | -8.7586e-05 | -0.36621 | 60.64 | -60.7681 | 61.1481 | -60.4752 | -60.9009 | -61.0199 | -0.25177 | 60.6171 | -60.8185 | 60.9375 | -60.7269 | -60.791 | -61.0062 | 0.064087 | -0.17853 | 0.32959 | 0.35706 | -0.18768 | -0.068665 | -0.25177 | -0.13275 | 0.013733 | -0.20142 | 0.11902 | 0.10529 | -0.17395 | 0.041198 | -0.18768 | 0.027465 | 0.29297 | 121.9162 | 0.091552 | 121.756 | 121.4081 | 121.4355 | 121.4722 | 121.4493 | -121.5866 | -121.637 | 121.9803 | 121.7697 | 60.466 | 60.5804
373.875 | 121.9803 | -60.8322 | 60.8368 | -0.009308 | 0 | 0.068037 | 0.063433 | -0.00049983 | -0.0067547 | -0.00044443 | -0.0066527 | -0.0003312 | 0.066516 | 0.069814 | -0.0042767 | 0.017626 | -0.0011558 | -0.44403 | 60.6125 | -60.8093 | 61.0657 | -60.5804 | -60.9604 | -61.0748 | -0.31586 | 60.6033 | -60.8505 | 60.9192 | -60.7544 | -60.8185 | -61.0245 | 0.022888 | -0.2243 | 0.22888 | 0.25177 | -0.24262 | -0.12817 | -0.2655 | -0.15106 | -0.018311 | -0.23346 | 0.082397 | 0.077819 | -0.19226 | 0.013733 | -0.17395 | 0.032044 | 0.22888 | 121.875 | 0.09613 | 121.7697 | 121.4218 | 121.4539 | 121.4447 | 121.4355 | -121.6461 | -121.6873 | 121.8979 | 121.7514 | 60.3882 | 60.5164
375.5469 | 121.9849 | -60.9009 | 60.7773 | -0.0016785 | 0 | 0.067396 | 0.063006 | 0.0016364 | -0.0026959 | 0.0021192 | -0.0036011 | 0.0022324 | 0.065661 | 0.063619 | -0.0034223 | 0.019762 | 0.00033961 | -0.4715 | 60.5667 | -60.8231 | 61.0107 | -60.6079 | -61.0382 | -61.1206 | -0.35248 | 60.5576 | -60.8826 | 60.8826 | -60.8276 | -60.91 | -61.0611 | 0.07782 | -0.21057 | 0.23346 | 0.29297 | -0.21973 | -0.13733 | -0.29755 | -0.21515 | 0.018311 | -0.21973 | 0.10529 | 0.073242 | -0.16022 | -0.009155 | -0.17853 | -0.027466 | 0.21515 | 121.8338 | 0.054931 | 121.7651 | 121.3898 | 121.4401 | 121.4676 | 121.4584 | -121.6003 | -121.6599 | 121.9116 | 121.7834 | 60.4294 | 60.5484
377.2812 | 122.0032 | -60.9009 | 60.7407 | -0.009308 | 0 | 0.069746 | 0.06322 | -0.00028623 | -0.0041913 | -0.0030078 | -0.0066527 | 0.000737 | 0.066302 | 0.055929 | -0.0034223 | 0.018053 | -0.0017966 | -0.43488 | 60.5576 | -60.8139 | 61.0611 | -60.585 | -61.0153 | -61.1069 | -0.31586 | 60.5392 | -60.8917 | 60.8917 | -60.8047 | -60.8871 | -61.0657 | 0.086975 | -0.18311 | 0.32043 | 0.31586 | -0.20599 | -0.11444 | -0.29297 | -0.20142 | 0.009155 | -0.20142 | 0.15106 | 0.09613 | -0.16479 | 0.013733 | -0.17395 | 0.004578 | 0.22888 | 121.875 | 0.086975 | 121.7834 | 121.3715 | 121.431 | 121.4584 | 121.4401 | -121.5546 | -121.6324 | 121.962 | 121.7926 | 60.466 | 60.585
379.0156 | 121.8384 | -60.9192 | 60.8139 | -0.0016785 | 0.55457 | 0.068037 | 0.065997 | -0.0013544 | -0.0039777 | -0.001726 | 0.0025025 | 0.0028732 | 0.067157 | 0.054006 | -0.0064129 | 0.017412 | -0.0041464 | -0.47607 | 60.6125 | -60.8368 | 60.9558 | -60.7086 | -61.1069 | -61.1984 | -0.47607 | 60.6171 | -60.9009 | 60.7498 | -60.9695 | -61.0291 | -61.1847 | 0.082397 | -0.20142 | 0.14191 | 0.21057 | -0.27924 | -0.18768 | -0.36163 | -0.27008 | 0.01831 | -0.19684 | -0.064087 | -0.050354 | -0.2655 | -0.10986 | -0.28381 | -0.12817 | 0.12817 | 121.7926 | -0.068664 | 121.6507 | 121.4493 | 121.5179 | 121.5317 | 121.5363 | -121.6507 | -121.7148 | 121.875 | 121.669 | 60.4431 | 60.4431
380.75 | 121.8475 | -60.9238 | 60.8276 | -0.0016785 | 0.75153 | 0.067396 | 0.065783 | -0.0017816 | -0.0035505 | 0.00019657 | -0.00054933 | 0.004155 | 0.070788 | 0.055288 | -0.0044903 | 0.018694 | -0.0028646 | -0.48523 | 60.6171 | -60.8597 | 60.9192 | -60.7452 | -61.1206 | -61.1984 | -0.45776 | 60.5896 | -60.91 | 60.7727 | -60.9604 | -61.0291 | -61.1572 | 0.064087 | -0.21057 | 0.091552 | 0.17853 | -0.27466 | -0.19684 | -0.33875 | -0.26093 | 0.013733 | -0.23804 | -0.054932 | -0.036621 | -0.23346 | -0.10529 | -0.24719 | -0.11902 | 0.11444 | 121.7789 | -0.050354 | 121.6827 | 121.4767 | 121.4996 | 121.5408 | 121.5134 | -121.6873 | -121.7377 | 121.843 | 121.6965 | 60.4385 | 60.466
382.4062 | 121.8613 | -60.8459 | 60.9009 | -0.009308 | 1.0547 | 0.066328 | 0.065356 | 0.00185 | -0.0065411 | -0.0030078 | -0.0036011 | 0.0022324 | 0.065875 | 0.062978 | -0.0059857 | 0.016985 | -0.00436 | -0.42114 | 60.6857 | -60.7773 | 61.0245 | -60.5896 | -60.9879 | -61.0931 | -0.37537 | 60.6857 | -60.8322 | 60.8505 | -60.8414 | -60.9192 | -61.0794 | 0.068664 | -0.21515 | 0.1236 | 0.25635 | -0.24719 | -0.14191 | -0.31586 | -0.21057 | 0.013733 | -0.21515 | -0.050354 | 0.004577 | -0.23346 | -0.073242 | -0.24719 | -0.086975 | 0.18768 | 121.8018 | -0.009156 | 121.6827 | 121.463 | 121.5179 | 121.5317 | 121.5317 | -121.6782 | -121.7331 | 121.8704 | 121.6965 | 60.4248 | 60.4706
384.1562 | 121.8658 | -60.8688 | 60.8688 | -0.016937 | 0.20059 | 0.06526 | 0.06621 | -0.0019952 | -0.0054731 | 0.00062377 | 0.011658 | 0.0056504 | 0.069079 | 0.060842 | -0.0053449 | 0.016131 | -0.0041464 | -0.40283 | 60.6949 | -60.7727 | 61.0291 | -60.5942 | -60.997 | -61.0886 | -0.37537 | 60.6949 | -60.8551 | 60.8322 | -60.8505 | -60.9146 | -61.0886 | 0.09613 | -0.17395 | 0.16022 | 0.27466 | -0.21973 | -0.12817 | -0.31586 | -0.2243 | 0.013732 | -0.17395 | -0.036621 | 0.01831 | -0.21973 | -0.045777 | -0.23346 | -0.059509 | 0.17853 | 121.8018 | 0.004578 | 121.6873 | 121.4676 | 121.55 | 121.5637 | 121.5637 | -121.6415 | -121.7239 | 121.8979 | 121.701 | 60.466 | 60.4935
385.9062 | 121.843 | -60.8368 | 60.8917 | -0.009308 | 0.37833 | 0.067182 | 0.064929 | 0.0012092 | -0.0073957 | -0.002367 | -0.00054933 | 0.0003098 | 0.067157 | 0.053365 | -0.0070539 | 0.016772 | -0.003292 | -0.41199 | 60.672 | -60.7544 | 61.0428 | -60.6079 | -61.0062 | -61.0931 | -0.37079 | 60.6674 | -60.8505 | 60.8322 | -60.8368 | -60.8963 | -61.084 | 0.082397 | -0.21973 | 0.15106 | 0.22888 | -0.25635 | -0.16937 | -0.33874 | -0.25177 | -0.013733 | -0.22431 | -0.05951 | 0 | -0.24719 | -0.059509 | -0.23346 | -0.045776 | 0.14649 | 121.7972 | 0.013733 | 121.6827 | 121.4264 | 121.5179 | 121.5088 | 121.5042 | -121.6461 | -121.7422 | 121.8796 | 121.669 | 60.4248 | 60.466
387.5781 | 121.8475 | -60.8551 | 60.9055 | -0.009308 | 1.264 | 0.067396 | 0.063433 | 0.00014097 | -0.0046185 | -0.0012988 | -0.00054933 | 0.002446 | 0.065875 | 0.060415 | -0.0049175 | 0.017412 | 0.0016214 | -0.41199 | 60.6766 | -60.759 | 61.0245 | -60.6262 | -60.9787 | -61.084 | -0.37537 | 60.7132 | -60.8505 | 60.8459 | -60.8322 | -60.9055 | -61.0977 | 0.096131 | -0.22888 | 0.11902 | 0.22888 | -0.22888 | -0.1236 | -0.32501 | -0.21973 | 0.004578 | -0.19226 | -0.05951 | 0.022889 | -0.24261 | -0.050354 | -0.24719 | -0.054932 | 0.13275 | 121.7834 | 0.018311 | 121.6965 | 121.4355 | 121.5637 | 121.5317 | 121.5683 | -121.6644 | -121.756 | 121.8796 | 121.7011 | 60.4431 | 60.4797
389.2969 | 121.8613 | -60.91 | 60.8093 | -0.0016785 | 1.0149 | 0.068037 | 0.066424 | -0.0024224 | -0.0046185 | 0.0014784 | -0.00054933 | 0.0028732 | 0.067584 | 0.049306 | -0.0021405 | 0.01784 | -0.0037192 | -0.48065 | 60.6308 | -60.8414 | 60.9283 | -60.7315 | -61.1343 | -61.2122 | -0.46692 | 60.5942 | -60.9283 | 60.7681 | -60.9375 | -61.0291 | -61.1572 | 0.068664 | -0.17853 | 0.11902 | 0.17853 | -0.30212 | -0.2243 | -0.37079 | -0.29297 | -0.018311 | -0.21515 | -0.041199 | -0.027466 | -0.24719 | -0.11902 | -0.22888 | -0.10071 | 0.10986 | 121.7697 | -0.009155 | 121.6965 | 121.4722 | 121.5225 | 121.5408 | 121.5042 | -121.6507 | -121.7377 | 121.8384 | 121.6782 | 60.4294 | 60.4431
391.0312 | 121.8475 | -60.91 | 60.8368 | 0.005951 | 1.2467 | 0.066541 | 0.066638 | -0.0013544 | -0.0044049 | -0.0019396 | -0.00054933 | 0.002446 | 0.06737 | 0.05956 | -0.0036359 | 0.019549 | -0.0052146 | -0.43945 | 60.5942 | -60.7956 | 60.9833 | -60.6628 | -61.0703 | -61.1847 | -0.42114 | 60.585 | -60.9055 | 60.791 | -60.91 | -60.9879 | -61.1435 | 0.11444 | -0.24262 | 0.14648 | 0.24719 | -0.27466 | -0.16022 | -0.3891 | -0.27466 | 0.004577 | -0.25177 | -0.045776 | 0 | -0.23346 | -0.07782 | -0.23804 | -0.082397 | 0.13275 | 121.7789 | -0.004577 | 121.6965 | 121.3898 | 121.4905 | 121.5042 | 121.4951 | -121.6324 | -121.7422 | 121.8933 | 121.7011 | 60.4706 | 60.4889
392.7656 | 121.875 | -60.9009 | 60.7773 | -0.0016785 | 1.0591 | 0.067396 | 0.063647 | -0.0017816 | -0.0039777 | -0.0010852 | -0.0036011 | 9.6204e-05 | 0.06673 | 0.056997 | -0.0034223 | 0.017626 | -0.00094199 | -0.50812 | 60.6033 | -60.8093 | 60.9283 | -60.6857 | -61.1114 | -61.1847 | -0.43488 | 60.5804 | -60.9055 | 60.8047 | -60.9192 | -61.0016 | -61.1526 | 0.091553 | -0.17395 | 0.15106 | 0.21515 | -0.28381 | -0.21057 | -0.37537 | -0.30212 | -0.004578 | -0.19684 | 0.027466 | -0.01831 | -0.25177 | -0.10071 | -0.24719 | -0.09613 | 0.1236 | 121.7377 | -0.013732 | 121.7102 | 121.4127 | 121.4859 | 121.5042 | 121.4813 | -121.5866 | -121.6827 | 121.8292 | 121.7056 | 60.3928 | 60.466
394.4375 | 121.9254 | -60.8231 | 60.8276 | 0.01358 | 1.3383 | 0.066755 | 0.063433 | 0.0041998 | -0.0037641 | -0.0019396 | 0.0086061 | -0.0003312 | 0.066943 | 0.065328 | -0.0034223 | 0.017626 | 0.0016214 | -0.45319 | 60.5942 | -60.7819 | 61.0428 | -60.5667 | -60.997 | -61.0931 | -0.3479 | 60.5896 | -60.8734 | 60.8551 | -60.8322 | -60.878 | -61.0657 | 0.041199 | -0.23346 | 0.21515 | 0.25635 | -0.27008 | -0.17395 | -0.31128 | -0.21515 | -0.050354 | -0.23804 | 0.027466 | -0.009155 | -0.24262 | -0.054932 | -0.19226 | -0.004578 | 0.21515 | 121.8246 | 0.041199 | 121.7285 | 121.376 | 121.463 | 121.4172 | 121.4127 | -121.6095 | -121.7011 | 121.8658 | 121.6782 | 60.3699 | 60.4752
396.1875 | 121.9025 | -60.8734 | 60.8688 | 0.02121 | 2.7536 | 0.066328 | 0.066851 | 0.005268 | -0.0031231 | 0.0012646 | 0.0055543 | 0.0033004 | 0.066943 | 0.058492 | -0.0047039 | 0.019121 | -0.0056418 | -0.37994 | 60.6628 | -60.791 | 61.0474 | -60.5713 | -60.9924 | -61.0977 | -0.31586 | 60.6491 | -60.9009 | 60.8643 | -60.8139 | -60.8871 | -61.0657 | 0.082397 | -0.20599 | 0.17853 | 0.30212 | -0.2243 | -0.11902 | -0.3067 | -0.20142 | -0.027466 | -0.21973 | -0.004577 | 0.059509 | -0.19226 | -0.013733 | -0.16479 | 0.013733 | 0.21973 | 121.8384 | 0.086975 | 121.7651 | 121.4539 | 121.55 | 121.5363 | 121.5225 | -121.6599 | -121.7697 | 121.9208 | 121.7377 | 60.4935 | 60.5576
397.9375 | 121.8613 | -60.8459 | 60.9055 | -0.009308 | 2.7107 | 0.066114 | 0.064074 | -0.00071343 | -0.0073957 | -0.00087163 | 0.0025025 | 0.0009506 | 0.068225 | 0.058492 | -0.0055585 | 0.017412 | -0.00072839 | -0.36621 | 60.6628 | -60.7681 | 61.0519 | -60.5621 | -60.965 | -61.0703 | -0.3479 | 60.6537 | -60.8322 | 60.8505 | -60.8231 | -60.9055 | -61.0794 | 0.07782 | -0.24262 | 0.14648 | 0.28381 | -0.2243 | -0.11902 | -0.30212 | -0.19684 | 0.013733 | -0.25177 | -0.054932 | 0.022888 | -0.23346 | -0.05951 | -0.24719 | -0.073243 | 0.20599 | 121.8201 | 0.009155 | 121.6827 | 121.431 | 121.4859 | 121.5088 | 121.4996 | -121.6736 | -121.7377 | 121.8979 | 121.6965 | 60.4797 | 60.498
399.625 | 121.843 | -60.91 | 60.8139 | 0.005951 | 2.5549 | 0.067182 | 0.064929 | 0.0024908 | -0.0026959 | -0.0038622 | -0.0036011 | 0.0037278 | 0.066943 | 0.055715 | -0.0034223 | 0.01848 | -0.0041464 | -0.45776 | 60.6262 | -60.8276 | 60.9512 | -60.6903 | -61.0977 | -61.1938 | -0.45319 | 60.5988 | -60.8963 | 60.7727 | -60.9238 | -61.0062 | -61.1389 | 0.082397 | -0.18768 | 0.13733 | 0.21973 | -0.28381 | -0.18768 | -0.36621 | -0.27008 | 0.013733 | -0.21515 | -0.041199 | -0.013733 | -0.22888 | -0.096131 | -0.24262 | -0.10986 | 0.13733 | 121.7789 | -0.027466 | 121.669 | 121.4539 | 121.4951 | 121.5363 | 121.5088 | -121.6415 | -121.7102 | 121.8613 | 121.6827 | 60.4523 | 60.4568
401.3594 | 121.9482 | -60.8414 | 60.7864 | 0.036468 | 0.63275 | 0.070387 | 0.064501 | 0.0022772 | -0.0031231 | -0.00087163 | 0.011658 | 0.0020188 | 0.068652 | 0.06191 | -0.0049175 | 0.021044 | 0.0014078 | -0.43488 | 60.585 | -60.8231 | 61.0474 | -60.5576 | -61.0016 | -61.0748 | -0.29755 | 60.5759 | -60.8917 | 60.8643 | -60.8231 | -60.8734 | -61.0794 | 0.018311 | -0.20142 | 0.26093 | 0.28381 | -0.23346 | -0.16022 | -0.25177 | -0.17853 | -0.050354 | -0.21057 | 0.07782 | 0.018311 | -0.23804 | -0.032043 | -0.18768 | 0.018311 | 0.2655 | 121.8704 | 0.068665 | 121.756 | 121.4081 | 121.4676 | 121.4264 | 121.4172 | -121.6095 | -121.6782 | 121.8887 | 121.7056 | 60.4065 | 60.5438
403.0938 | 121.8292 | -60.8597 | 60.9009 | -0.0016785 | 1.6193 | 0.064619 | 0.066424 | -0.001568 | -0.0050457 | -0.0030078 | -0.0036011 | 0.0020188 | 0.068011 | 0.062551 | -0.0083355 | 0.019335 | -0.005001 | -0.41657 | 60.6583 | -60.7727 | 61.0107 | -60.6033 | -60.997 | -61.0931 | -0.37537 | 60.6812 | -60.8414 | 60.8459 | -60.8505 | -60.9055 | -61.0611 | 0.086975 | -0.24262 | 0.10986 | 0.25635 | -0.23346 | -0.13733 | -0.32043 | -0.2243 | 0.01831 | -0.21973 | -0.054932 | 0.009155 | -0.20142 | -0.045777 | -0.21973 | -0.064087 | 0.16937 | 121.7834 | -0.009155 | 121.6873 | 121.431 | 121.5225 | 121.5179 | 121.5408 | -121.6736 | -121.7422 | 121.8704 | 121.7056 | 60.4431 | 60.4843
404.8281 | 121.8475 | -60.8505 | 60.8963 | -0.009308 | 1.4971 | 0.065046 | 0.064074 | 0.0012092 | -0.0076093 | -0.0021532 | -0.00054933 | -0.0001174 | 0.070361 | 0.065969 | -0.0072675 | 0.01848 | -0.0058554 | -0.4303 | 60.6628 | -60.7819 | 61.0062 | -60.6033 | -60.997 | -61.0794 | -0.37537 | 60.6903 | -60.8093 | 60.8414 | -60.8414 | -60.91 | -61.0703 | 0.068665 | -0.23346 | 0.10986 | 0.24719 | -0.22888 | -0.14648 | -0.29755 | -0.21515 | 0.041199 | -0.20599 | -0.054931 | 0.009155 | -0.21973 | -0.059509 | -0.26093 | -0.10071 | 0.17853 | 121.788 | -0.032044 | 121.6507 | 121.4447 | 121.4996 | 121.5134 | 121.5408 | -121.6782 | -121.7056 | 121.8567 | 121.6919 | 60.4202 | 60.4752
406.5 | 121.9208 | -60.8047 | 60.8597 | -0.0016785 | 1.7964 | 0.066541 | 0.06386 | 0.00099557 | -0.0037641 | -0.0010852 | -0.00054933 | 0.000737 | 0.068011 | 0.065755 | -0.0027813 | 0.017626 | -0.0022238 | -0.36621 | 60.6079 | -60.7407 | 61.1252 | -60.4935 | -60.9009 | -60.997 | -0.24261 | 60.6537 | -60.8047 | 60.9329 | -60.7498 | -60.8139 | -61.0153 | 0.064087 | -0.25177 | 0.2655 | 0.31128 | -0.19226 | -0.09613 | -0.25635 | -0.16022 | 0 | -0.20599 | 0.073242 | 0.054932 | -0.21057 | -0.009155 | -0.21057 | -0.009155 | 0.24719 | 121.8658 | 0.054932 | 121.7377 | 121.3486 | 121.4584 | 121.4127 | 121.4584 | -121.6003 | -121.6644 | 121.9299 | 121.7377 | 60.4385 | 60.5621
408.2344 | 121.9803 | -60.8917 | 60.7452 | -0.016937 | 1.3097 | 0.068678 | 0.064501 | 0.0031318 | -0.0041913 | -0.00044443 | -0.00054933 | 0.0026596 | 0.066516 | 0.062124 | -0.0021405 | 0.019549 | -0.0035056 | -0.43488 | 60.5713 | -60.8459 | 61.0291 | -60.5804 | -61.0245 | -61.1069 | -0.31586 | 60.5392 | -60.9055 | 60.8917 | -60.791 | -60.8871 | -61.0382 | 0.045777 | -0.17395 | 0.28381 | 0.31128 | -0.21515 | -0.13275 | -0.26093 | -0.17853 | -0.013733 | -0.20599 | 0.14649 | 0.10071 | -0.14648 | 0.004578 | -0.13275 | 0.018311 | 0.2655 | 121.875 | 0.11444 | 121.7972 | 121.4172 | 121.4447 | 121.463 | 121.431 | -121.5912 | -121.6507 | 121.9208 | 121.7834 | 60.4568 | 60.5759
409.9688 | 121.962 | -60.8047 | 60.8368 | 0.005951 | 1.3787 | 0.066541 | 0.064501 | 0.00185 | -0.0046185 | 0.0014784 | -0.00054933 | -0.0007584 | 0.067798 | 0.058919 | -0.0053449 | 0.02083 | -0.0030784 | -0.3891 | 60.6125 | -60.7452 | 61.1298 | -60.4614 | -60.8734 | -60.9833 | -0.22888 | 60.6171 | -60.7864 | 60.965 | -60.6995 | -60.7727 | -60.9879 | 0.05951 | -0.2243 | 0.29297 | 0.34332 | -0.17853 | -0.068664 | -0.23804 | -0.12817 | 0.018311 | -0.21973 | 0.12817 | 0.10529 | -0.1831 | 0.032044 | -0.20142 | 0.013733 | 0.28381 | 121.875 | 0.086975 | 121.7514 | 121.3577 | 121.4035 | 121.4172 | 121.4218 | -121.582 | -121.6232 | 121.9345 | 121.7697 | 60.4156 | 60.5759
411.7031 | 121.9437 | -60.8734 | 60.759 | 0.005951 | 1.9401 | 0.067182 | 0.063006 | 0.00035457 | -0.0050457 | 0.00019657 | 0.0055543 | 0.0022324 | 0.066943 | 0.060842 | -0.0025677 | 0.020189 | -0.0037192 | -0.43945 | 60.5301 | -60.8139 | 61.084 | -60.5301 | -60.9741 | -61.0519 | -0.28839 | 60.5942 | -60.8871 | 60.8963 | -60.7956 | -60.8643 | -61.0474 | 0.059509 | -0.22888 | 0.32501 | 0.34332 | -0.17853 | -0.10071 | -0.23804 | -0.16022 | -0.013733 | -0.16479 | 0.13733 | 0.07782 | -0.17395 | 0.009155 | -0.16022 | 0.022888 | 0.28381 | 121.8979 | 0.091553 | 121.7834 | 121.344 | 121.4813 | 121.4035 | 121.4676 | -121.5729 | -121.6461 | 121.9574 | 121.7697 | 60.434 | 60.585
413.375 | 121.843 | -60.9238 | 60.8139 | -0.009308 | 1.8675 | 0.065901 | 0.066638 | 0.0046272 | -0.0035505 | -0.0012988 | -0.0036011 | 0.003514 | 0.067798 | 0.057424 | -0.0049175 | 0.018908 | -0.0022238 | -0.49439 | 60.585 | -60.8368 | 60.9421 | -60.7224 | -61.1481 | -61.203 | -0.45776 | 60.5988 | -60.9283 | 60.7773 | -60.9375 | -61.0062 | -61.1298 | 0.086975 | -0.22888 | 0.12817 | 0.20142 | -0.27924 | -0.2243 | -0.36621 | -0.31128 | -0.004578 | -0.21515 | -0.036621 | -0.013733 | -0.20599 | -0.082398 | -0.20142 | -0.07782 | 0.11444 | 121.7789 | -0.009155 | 121.7056 | 121.4218 | 121.5271 | 121.5088 | 121.5225 | -121.6507 | -121.7422 | 121.8658 | 121.701 | 60.4294 | 60.466
415.125 | 121.8658 | -60.8505 | 60.8871 | 0.051727 | 2.456 | 0.06761 | 0.065569 | 0.00014097 | -0.0044049 | -0.001726 | 0.011658 | 0.0028732 | 0.06673 | 0.061056 | -0.0064129 | 0.017412 | -0.001583 | -0.41199 | 60.6857 | -60.8047 | 61.0336 | -60.5942 | -60.9833 | -61.084 | -0.37537 | 60.704 | -60.8551 | 60.8459 | -60.8139 | -60.8963 | -61.0565 | 0.045776 | -0.20142 | 0.14648 | 0.25635 | -0.23346 | -0.13275 | -0.27923 | -0.17853 | -0.004578 | -0.18311 | -0.041199 | 0.036621 | -0.20599 | -0.045776 | -0.20142 | -0.041198 | 0.21057 | 121.8384 | 0.041199 | 121.7011 | 121.4905 | 121.5591 | 121.5363 | 121.5546 | -121.6919 | -121.7422 | 121.8842 | 121.6965 | 60.4385 | 60.4752
416.8594 | 121.9528 | -60.8414 | 60.8093 | 0.01358 | 3.2313 | 0.068037 | 0.063647 | 0.0022772 | -0.0033369 | -0.002367 | -0.0066527 | 0.002446 | 0.066943 | 0.066823 | -0.0038495 | 0.020189 | -0.0022238 | -0.45319 | 60.585 | -60.7956 | 61.0291 | -60.5804 | -60.9741 | -61.0657 | -0.35706 | 60.6079 | -60.8551 | 60.8871 | -60.7819 | -60.8505 | -61.0336 | 0.045777 | -0.2243 | 0.21973 | 0.26093 | -0.2243 | -0.13275 | -0.27008 | -0.17853 | -0.013733 | -0.20142 | 0.07782 | 0.05951 | -0.19226 | -0.009155 | -0.17853 | 0.004578 | 0.21515 | 121.8246 | 0.073243 | 121.7422 | 121.3806 | 121.463 | 121.4264 | 121.4493 | -121.6049 | -121.6644 | 121.8704 | 121.7285 | 60.3882 | 60.4843
418.5312 | 121.9803 | -60.8185 | 60.8414 | -0.016937 | 4.0898 | 0.068037 | 0.06322 | -0.0019952 | -0.0059003 | -0.0040758 | -0.0036011 | 9.6204e-05 | 0.065875 | 0.065542 | -0.0042767 | 0.016985 | -0.00072839 | -0.36163 | 60.6079 | -60.7407 | 61.1343 | -60.466 | -60.8917 | -60.997 | -0.24719 | 60.6216 | -60.8002 | 60.9329 | -60.7132 | -60.791 | -60.9924 | 0.077819 | -0.23346 | 0.29297 | 0.35248 | -0.17853 | -0.073243 | -0.25635 | -0.15106 | 0.01831 | -0.21973 | 0.091552 | 0.10528 | -0.17395 | 0.027465 | -0.19226 | 0.009155 | 0.27466 | 121.875 | 0.086975 | 121.7331 | 121.3486 | 121.4218 | 121.4264 | 121.4401 | -121.582 | -121.6415 | 121.9528 | 121.7514 | 60.4568 | 60.5713
420.2656 | 121.9528 | -60.8322 | 60.8368 | 0.005951 | 4.0558 | 0.066969 | 0.063006 | -0.0056268 | -0.0024823 | 0.00019657 | -0.00054933 | 0.0015914 | 0.067798 | 0.066396 | -0.0059857 | 0.019335 | 0.00012601 | -0.46692 | 60.5804 | -60.791 | 61.0428 | -60.5759 | -60.9787 | -61.0703 | -0.34332 | 60.5942 | -60.8505 | 60.9009 | -60.7773 | -60.8322 | -61.0245 | 0.041198 | -0.25635 | 0.20599 | 0.25635 | -0.23804 | -0.14648 | -0.27923 | -0.18768 | -0.018311 | -0.24262 | 0.064087 | 0.054931 | -0.19226 | 0 | -0.17395 | 0.018311 | 0.21515 | 121.8338 | 0.073242 | 121.7514 | 121.3715 | 121.4447 | 121.4127 | 121.4264 | -121.6278 | -121.6873 | 121.875 | 121.7331 | 60.3653 | 60.4889
421.9531 | 121.843 | -60.9009 | 60.8047 | -0.0016785 | 4.4374 | 0.068678 | 0.065569 | 0.00099557 | -0.0024823 | -0.0012988 | -0.00054933 | 0.0033004 | 0.06673 | 0.064046 | -0.0042767 | 0.020189 | 0.00098061 | -0.49896 | 60.5896 | -60.8505 | 60.9283 | -60.7178 | -61.1206 | -61.1938 | -0.45319 | 60.5896 | -60.9192 | 60.7544 | -60.9283 | -61.0016 | -61.1526 | 0.050354 | -0.21515 | 0.1236 | 0.18311 | -0.29297 | -0.21973 | -0.34332 | -0.27008 | -0.01831 | -0.21515 | -0.050354 | -0.027466 | -0.25177 | -0.10071 | -0.23346 | -0.082398 | 0.13275 | 121.7789 | -0.009156 | 121.6736 | 121.4401 | 121.5088 | 121.4905 | 121.4905 | -121.6553 | -121.7239 | 121.8292 | 121.6553 | 60.4019 | 60.4477
423.6875 | 121.9208 | -60.8734 | 60.7681 | -0.009308 | 4.18 | 0.067823 | 0.065997 | -0.0019952 | -0.0037641 | -0.00044443 | -0.00054933 | 0.0030868 | 0.065234 | 0.063833 | -0.0036359 | 0.019121 | -0.0039328 | -0.49439 | 60.6033 | -60.8139 | 60.9604 | -60.672 | -61.1023 | -61.171 | -0.41199 | 60.5438 | -60.9055 | 60.8322 | -60.8551 | -60.9329 | -61.0794 | 0.059509 | -0.16479 | 0.19226 | 0.20142 | -0.29755 | -0.22888 | -0.35706 | -0.28839 | -0.032044 | -0.2243 | 0.064087 | 0.01831 | -0.20599 | -0.059509 | -0.17395 | -0.027465 | 0.14191 | 121.7743 | 0.050354 | 121.7377 | 121.4172 | 121.4493 | 121.4767 | 121.4172 | -121.582 | -121.6736 | 121.8338 | 121.7056 | 60.379 | 60.4614
425.4219 | 121.8475 | -60.9009 | 60.8276 | -0.0016785 | 4.3739 | 0.066755 | 0.064074 | 0.0022772 | -0.0052595 | -0.00023063 | 0.0025025 | 0.0018052 | 0.065875 | 0.054861 | -0.0059857 | 0.019549 | -0.006069 | -0.4303 | 60.5942 | -60.8047 | 60.9879 | -60.6308 | -61.0611 | -61.1526 | -0.39368 | 60.5804 | -60.9055 | 60.791 | -60.9055 | -60.997 | -61.1252 | 0.09613 | -0.23346 | 0.16022 | 0.27008 | -0.25177 | -0.16022 | -0.3479 | -0.25635 | -0.004578 | -0.24719 | -0.036621 | -0.004578 | -0.2243 | -0.09613 | -0.21973 | -0.091552 | 0.17395 | 121.7926 | 0 | 121.6965 | 121.3989 | 121.4859 | 121.4951 | 121.4813 | -121.6324 | -121.7331 | 121.8887 | 121.6919 | 60.4706 | 60.5072
427.1406 | 121.9528 | -60.8826 | 60.759 | -0.0016785 | 3.5587 | 0.068464 | 0.063647 | 0.00056817 | -0.0061139 | 0.0023328 | 0.0086061 | 0.0003098 | 0.068225 | 0.064474 | -0.0027813 | 0.019121 | 0.00012601 | -0.44861 | 60.553 | -60.7956 | 61.0519 | -60.5484 | -61.0016 | -61.084 | -0.30212 | 60.5621 | -60.878 | 60.8917 | -60.7819 | -60.8643 | -61.0382 | 0.086975 | -0.20599 | 0.29297 | 0.33417 | -0.20142 | -0.11902 | -0.28839 | -0.20599 | 0.004577 | -0.19684 | 0.13275 | 0.10071 | -0.15564 | 0.01831 | -0.16022 | 0.013733 | 0.24719 | 121.8475 | 0.096131 | 121.7697 | 121.3486 | 121.4401 | 121.4355 | 121.4447 | -121.5546 | -121.637 | 121.9345 | 121.7743 | 60.434 | 60.5804
428.875 | 121.9299 | -60.7956 | 60.8597 | -0.0016785 | 3.2528 | 0.066969 | 0.061511 | -0.00028623 | -0.0050457 | -0.0030078 | -0.00054933 | -0.0007584 | 0.066516 | 0.056997 | -0.0068403 | 0.017626 | -0.00436 | -0.37537 | 60.6079 | -60.7498 | 61.116 | -60.4843 | -60.8963 | -60.9924 | -0.24719 | 60.6125 | -60.8185 | 60.9146 | -60.7315 | -60.7956 | -60.997 | 0.045776 | -0.25177 | 0.25635 | 0.31128 | -0.19684 | -0.10071 | -0.24262 | -0.14648 | -0.022888 | -0.24719 | 0.054932 | 0.064087 | -0.20142 | 0 | -0.17853 | 0.022888 | 0.2655 | 121.8658 | 0.086975 | 121.7331 | 121.3577 | 121.431 | 121.4035 | 121.4081 | -121.6095 | -121.6782 | 121.9116 | 121.7102 | 60.4202 | 60.5484
430.5625 | 121.8521 | -60.91 | 60.8093 | -0.016937 | 3.5015 | 0.068678 | 0.066638 | -0.0017816 | -0.0039777 | -0.0027942 | -0.0036011 | 0.0022324 | 0.066516 | 0.064046 | -0.0049175 | 0.019762 | -0.0028646 | -0.50354 | 60.5713 | -60.8551 | 60.9329 | -60.6995 | -61.1069 | -61.1893 | -0.46692 | 60.6125 | -60.878 | 60.7819 | -60.9055 | -60.9833 | -61.1298 | 0.054931 | -0.23804 | 0.1236 | 0.21057 | -0.27924 | -0.19684 | -0.33417 | -0.25177 | 0.032043 | -0.19684 | -0.027466 | 0.004577 | -0.21973 | -0.073242 | -0.25177 | -0.10528 | 0.15564 | 121.788 | -0.027466 | 121.6599 | 121.4264 | 121.4905 | 121.4813 | 121.5225 | -121.6644 | -121.6873 | 121.843 | 121.6919 | 60.4065 | 60.4431
432.2969 | 121.9574 | -60.8643 | 60.7498 | -0.0016785 | 3.3515 | 0.066755 | 0.064715 | 0.00035457 | -0.0063275 | -0.003435 | -0.0036011 | 0.0013778 | 0.06737 | 0.061696 | -0.0034223 | 0.019976 | -0.0037192 | -0.49439 | 60.5667 | -60.8139 | 61.0153 | -60.6125 | -61.0382 | -61.1298 | -0.36621 | 60.5347 | -60.8963 | 60.8643 | -60.8185 | -60.8871 | -61.0474 | 0.050354 | -0.18311 | 0.2655 | 0.25177 | -0.2655 | -0.17395 | -0.31586 | -0.2243 | -0.032043 | -0.21515 | 0.11444 | 0.045777 | -0.1831 | -0.022888 | -0.15106 | 0.009155 | 0.20142 | 121.8292 | 0.07782 | 121.7606 | 121.3806 | 121.431 | 121.431 | 121.3989 | -121.5637 | -121.6461 | 121.8796 | 121.7285 | 60.3699 | 60.498
434.0312 | 121.8384 | -60.8276 | 60.91 | -0.009308 | 3.3084 | 0.066114 | 0.063006 | 0.00014097 | -0.0065411 | 0.001051 | -0.0036011 | 0.0015914 | 0.067157 | 0.059347 | -0.0083355 | 0.019549 | -0.00072839 | -0.42572 | 60.6445 | -60.759 | 61.0199 | -60.585 | -60.9924 | -61.0794 | -0.36163 | 60.6628 | -60.8185 | 60.8231 | -60.8093 | -60.8871 | -61.0703 | 0.068665 | -0.2655 | 0.10986 | 0.24262 | -0.25177 | -0.16479 | -0.32044 | -0.23346 | 0.009156 | -0.24719 | -0.086975 | 0.018311 | -0.24261 | -0.059509 | -0.25177 | -0.068665 | 0.17395 | 121.7789 | 0.009155 | 121.6415 | 121.4035 | 121.4813 | 121.4722 | 121.4905 | -121.669 | -121.7285 | 121.8475 | 121.6507 | 60.4019 | 60.466
435.7812 | 121.8384 | -60.9055 | 60.791 | 0.005951 | 3.3122 | 0.068464 | 0.066638 | -0.0024224 | -0.0029095 | -0.0019396 | -0.00054933 | 0.0037278 | 0.070147 | 0.063619 | -0.0057721 | 0.016344 | -8.7586e-05 | -0.50354 | 60.6216 | -60.8505 | 60.9192 | -60.6903 | -61.1114 | -61.1938 | -0.43945 | 60.6216 | -60.9283 | 60.7819 | -60.9055 | -60.9833 | -61.1298 | 0.054932 | -0.16937 | 0.12817 | 0.21515 | -0.28839 | -0.20599 | -0.34332 | -0.26093 | -0.022888 | -0.16937 | -0.009156 | 0 | -0.2243 | -0.077819 | -0.20142 | -0.054931 | 0.16022 | 121.7697 | 0.022888 | 121.7102 | 121.4722 | 121.55 | 121.5271 | 121.5271 | -121.6415 | -121.7194 | 121.8246 | 121.6873 | 60.4019 | 60.466
437.4531 | 121.8658 | -60.8597 | 60.8185 | 0.01358 | 3.6254 | 0.066969 | 0.064288 | 0.00099557 | -0.0056867 | -0.0015124 | 0.0025025 | 0.0015914 | 0.068225 | 0.058065 | -0.0061993 | 0.01848 | -0.0022238 | -0.3891 | 60.6262 | -60.8002 | 61.0428 | -60.5759 | -60.9924 | -61.084 | -0.31586 | 60.5942 | -60.8643 | 60.8414 | -60.8231 | -60.8963 | -61.0565 | 0.059509 | -0.19226 | 0.22431 | 0.28381 | -0.2243 | -0.13275 | -0.28381 | -0.19226 | -0.004578 | -0.2243 | 0.022889 | 0.036621 | -0.19684 | -0.036621 | -0.19226 | -0.032043 | 0.2243 | 121.843 | 0.041199 | 121.7056 | 121.4264 | 121.4584 | 121.4859 | 121.4539 | -121.6187 | -121.6827 | 121.9025 | 121.701 | 60.4706 | 60.5438
439.1875 | 121.843 | -60.9009 | 60.8139 | -0.009308 | 3.7647 | 0.06761 | 0.065997 | -0.0024224 | -0.0033369 | 0.001051 | -0.0036011 | 0.0009506 | 0.06737 | 0.057638 | -0.0044903 | 0.016985 | -0.003292 | -0.50812 | 60.6079 | -60.8231 | 60.9192 | -60.6903 | -61.0886 | -61.1847 | -0.44403 | 60.5804 | -60.9146 | 60.7727 | -60.9146 | -60.9879 | -61.1206 | 0.07782 | -0.20599 | 0.10529 | 0.21057 | -0.28381 | -0.18768 | -0.36163 | -0.2655 | -0.013733 | -0.23346 | -0.041199 | -0.013733 | -0.21973 | -0.086975 | -0.20599 | -0.073242 | 0.13275 | 121.7422 | 0 | 121.6873 | 121.431 | 121.4951 | 121.5088 | 121.4813 | -121.637 | -121.7285 | 121.8201 | 121.6736 | 60.3928 | 60.4568
440.9375 | 121.907 | -60.8459 | 60.7773 | 0.028839 | 3.9358 | 0.070814 | 0.063433 | 0.0014228 | -0.00098689 | -0.00023063 | 0.011658 | 0.0028732 | 0.06673 | 0.065542 | -0.0036359 | 0.019121 | 0.00033961 | -0.4303 | 60.5438 | -60.8047 | 61.0474 | -60.5438 | -60.9787 | -61.0748 | -0.31586 | 60.585 | -60.8551 | 60.878 | -60.8047 | -60.8734 | -61.0565 | 0.041198 | -0.23346 | 0.27008 | 0.30212 | -0.22888 | -0.13275 | -0.27008 | -0.17395 | -0.009156 | -0.19226 | 0.10071 | 0.041198 | -0.21057 | -0.027466 | -0.20142 | -0.01831 | 0.26093 | 121.8521 | 0.050354 | 121.7331 | 121.3486 | 121.4401 | 121.3898 | 121.431 | -121.582 | -121.6324 | 121.8933 | 121.7239 | 60.4156 | 60.5301
442.6094 | 121.8155 | -60.91 | 60.8231 | -0.0016785 | 4.0541 | 0.067396 | 0.064929 | 0.0014228 | -0.0039777 | -0.0012988 | 0.0025025 | 0.003514 | 0.064807 | 0.059347 | -0.0029949 | 0.017412 | -0.0020102 | -0.48523 | 60.5988 | -60.8322 | 60.9329 | -60.6857 | -61.0886 | -61.1801 | -0.46692 | 60.6079 | -60.9146 | 60.7452 | -60.9512 | -61.0245 | -61.1435 | 0.07782 | -0.2243 | 0.10986 | 0.2243 | -0.27008 | -0.17853 | -0.3479 | -0.25635 | -0.004578 | -0.21515 | -0.07782 | -0.041199 | -0.23346 | -0.11444 | -0.22888 | -0.10986 | 0.14648 | 121.7651 | -0.036621 | 121.6599 | 121.431 | 121.5225 | 121.5088 | 121.5179 | -121.6553 | -121.7377 | 121.843 | 121.6553 | 60.4248 | 60.4431
444.3281 | 121.907 | -60.8551 | 60.7819 | 0.01358 | 3.8805 | 0.067823 | 0.064288 | 0.0016364 | -0.0022687 | -0.00023063 | 0.0055543 | -0.0001174 | 0.068011 | 0.06426 | -0.0032087 | 0.018267 | -0.0041464 | -0.46692 | 60.5713 | -60.8047 | 61.0153 | -60.5621 | -60.965 | -61.0703 | -0.36621 | 60.585 | -60.8597 | 60.8597 | -60.8139 | -60.878 | -61.0474 | 0.050354 | -0.21057 | 0.23346 | 0.29297 | -0.21515 | -0.10986 | -0.2655 | -0.16022 | -0.004577 | -0.19684 | 0.07782 | 0.041199 | -0.19226 | -0.022888 | -0.18768 | -0.018311 | 0.24262 | 121.8201 | 0.045776 | 121.7194 | 121.376 | 121.4447 | 121.4264 | 121.4401 | -121.5866 | -121.6415 | 121.8704 | 121.7148 | 60.3882 | 60.4889
446.0625 | 121.8933 | -60.8368 | 60.8688 | -0.016937 | 4.4654 | 0.066969 | 0.061297 | 0.00078177 | -0.0050457 | -0.0045032 | -0.00054933 | -0.0003312 | 0.067157 | 0.058706 | -0.0057721 | 0.01848 | -0.0028646 | -0.37079 | 60.5759 | -60.7544 | 61.1069 | -60.4614 | -60.8826 | -60.997 | -0.2655 | 60.6262 | -60.791 | 60.878 | -60.7361 | -60.8139 | -61.0062 | 0.082397 | -0.29297 | 0.23804 | 0.37537 | -0.16022 | -0.045776 | -0.24261 | -0.12817 | 0.045776 | -0.24261 | 0.009156 | 0.10071 | -0.16937 | 0.022888 | -0.21515 | -0.022888 | 0.29297 | 121.8613 | 0.054932 | 121.669 | 121.3303 | 121.4172 | 121.4127 | 121.463 | -121.6232 | -121.6599 | 121.9437 | 121.7148 | 60.466 | 60.5713
447.7969 | 121.8063 | -60.8917 | 60.8139 | -0.0016785 | 3.7649 | 0.067396 | 0.067065 | 0.00078177 | -0.0016279 | -0.002367 | -0.00054933 | 0.0045822 | 0.067798 | 0.052938 | -0.0017133 | 0.018267 | -0.0041464 | -0.48523 | 60.6125 | -60.8093 | 60.9238 | -60.6949 | -61.1114 | -61.1847 | -0.4715 | 60.6033 | -60.9146 | 60.7452 | -60.9421 | -61.0107 | -61.1389 | 0.082398 | -0.20142 | 0.10986 | 0.19684 | -0.29297 | -0.21973 | -0.37537 | -0.30212 | -0.022888 | -0.21057 | -0.068665 | -0.050354 | -0.24719 | -0.11902 | -0.2243 | -0.09613 | 0.11444 | 121.7331 | -0.027466 | 121.6599 | 121.4218 | 121.5179 | 121.5042 | 121.4951 | -121.6232 | -121.7285 | 121.8155 | 121.637 | 60.4065 | 60.4202
449.4688 | 121.8384 | -60.8185 | 60.8688 | 0.005951 | 4.7283 | 0.066755 | 0.064288 | 0.0029182 | -0.0050457 | -0.0030078 | -0.0036011 | 0.0022324 | 0.068438 | 0.063192 | -0.0070539 | 0.018908 | -0.0024374 | -0.36621 | 60.6583 | -60.7498 | 61.0748 | -60.5026 | -60.9192 | -61.0245 | -0.3067 | 60.6308 | -60.8047 | 60.8505 | -60.7727 | -60.8688 | -61.0382 | 0.068664 | -0.21057 | 0.20599 | 0.31586 | -0.20599 | -0.10071 | -0.27466 | -0.16937 | 0.013732 | -0.23804 | -0.01831 | 0.045776 | -0.21973 | -0.050354 | -0.23346 | -0.064086 | 0.24719 | 121.8246 | 0.032044 | 121.6553 | 121.4081 | 121.4355 | 121.4767 | 121.4493 | -121.6187 | -121.6736 | 121.8933 | 121.669 | 60.4523 | 60.5118
451.2031 | 121.8521 | -60.878 | 60.8002 | -0.0016785 | 4.6149 | 0.064832 | 0.064074 | 0.0020636 | -0.0039777 | -0.0012988 | -0.0066527 | 0.0037278 | 0.065875 | 0.061056 | -0.0061993 | 0.015703 | -0.0047874 | -0.40283 | 60.6125 | -60.8093 | 61.0199 | -60.5759 | -61.0062 | -61.1023 | -0.35706 | 60.6262 | -60.8597 | 60.8276 | -60.8505 | -60.9283 | -61.0748 | 0.068665 | -0.18768 | 0.21973 | 0.30212 | -0.2243 | -0.12817 | -0.29297 | -0.19684 | 0.018311 | -0.17395 | 0.027466 | 0.027466 | -0.19684 | -0.050354 | -0.21515 | -0.068665 | 0.23346 | 121.8292 | 0.009155 | 121.6873 | 121.4218 | 121.4859 | 121.4905 | 121.5042 | -121.6095 | -121.6599 | 121.8979 | 121.7056 | 60.4752 | 60.5209
452.9375 | 121.8933 | -60.8459 | 60.8368 | 0.01358 | 4.6916 | 0.068037 | 0.065569 | 0.0029182 | -0.0071821 | -0.0021532 | 0.0055543 | 0.0033004 | 0.06673 | 0.060842 | -0.0040631 | 0.017626 | -0.002651 | -0.39825 | 60.6491 | -60.8047 | 61.0291 | -60.5621 | -60.9787 | -61.0657 | -0.31128 | 60.6171 | -60.8551 | 60.8551 | -60.8139 | -60.8688 | -61.0611 | 0.041198 | -0.18768 | 0.19226 | 0.28381 | -0.21973 | -0.13275 | -0.26093 | -0.17395 | -0.009156 | -0.21973 | 0.018311 | 0.032043 | -0.21515 | -0.022888 | -0.20599 | -0.013732 | 0.24262 | 121.8338 | 0.041199 | 121.7102 | 121.4539 | 121.4722 | 121.4951 | 121.463 | -121.6415 | -121.6919 | 121.875 | 121.7011 | 60.4477 | 60.5347
454.6719 | 121.9437 | -60.791 | 60.8414 | -0.009308 | 5.4222 | 0.067182 | 0.061511 | -0.0017816 | -0.0084637 | -0.00023063 | -0.0066527 | 0.0005234 | 0.066516 | 0.058278 | -0.0051313 | 0.018694 | -0.0030784 | -0.37994 | 60.6033 | -60.7361 | 61.116 | -60.4614 | -60.8826 | -60.9833 | -0.24719 | 60.6079 | -60.7636 | 60.9375 | -60.6995 | -60.7727 | -60.9833 | 0.054932 | -0.23804 | 0.27466 | 0.32959 | -0.19226 | -0.091552 | -0.24719 | -0.14648 | 0.027466 | -0.23346 | 0.09613 | 0.091553 | -0.19226 | 0.018311 | -0.21973 | -0.009155 | 0.27466 | 121.8521 | 0.064087 | 121.7011 | 121.3394 | 121.3715 | 121.3943 | 121.3989 | -121.5775 | -121.6049 | 121.907 | 121.7285 | 60.4111 | 60.5438
456.3594 | 121.8704 | -60.8231 | 60.8643 | 0.028839 | 5.3577 | 0.067182 | 0.064715 | 0.0016364 | -0.0044049 | 0.00062377 | 0.014709 | 0.0030868 | 0.068225 | 0.06661 | -0.0074811 | 0.016985 | -0.0035056 | -0.40283 | 60.6628 | -60.7956 | 61.0153 | -60.5942 | -60.9833 | -61.0611 | -0.35706 | 60.6766 | -60.8597 | 60.8459 | -60.8093 | -60.8871 | -61.0474 | 0.027466 | -0.20142 | 0.15106 | 0.22888 | -0.23804 | -0.16022 | -0.2655 | -0.18768 | -0.036621 | -0.18768 | -0.018311 | 0.013733 | -0.2243 | -0.064087 | -0.18768 | -0.027466 | 0.20142 | 121.8109 | 0.050354 | 121.7056 | 121.4584 | 121.5363 | 121.4859 | 121.4996 | -121.6599 | -121.7239 | 121.8384 | 121.669 | 60.4202 | 60.466
458.0938 | 121.8796 | -60.9009 | 60.7681 | -0.0016785 | 5.3233 | 0.065687 | 0.066424 | 0.00185 | -0.0044049 | -0.0040758 | -0.0036011 | 0.0018052 | 0.070788 | 0.056997 | -0.0025677 | 0.020617 | -0.0041464 | -0.50354 | 60.6079 | -60.8322 | 60.9283 | -60.672 | -61.1069 | -61.171 | -0.43488 | 60.5759 | -60.8917 | 60.7864 | -60.8643 | -60.9329 | -61.0886 | 0.068665 | -0.16022 | 0.16022 | 0.22888 | -0.27008 | -0.20599 | -0.33875 | -0.27466 | 0.009155 | -0.19226 | 0.018311 | 0.036621 | -0.18768 | -0.032043 | -0.19684 | -0.041198 | 0.16022 | 121.7606 | 0.027466 | 121.6782 | 121.4401 | 121.4676 | 121.5088 | 121.4767 | -121.6003 | -121.6599 | 121.8292 | 121.6873 | 60.3973 | 60.466
459.8281 | 121.9116 | -60.8505 | 60.7636 | 0.02121 | 5.5121 | 0.068891 | 0.065569 | 0.0027044 | -0.0050457 | -0.001726 | 0.011658 | 0.0015914 | 0.068438 | 0.061269 | -0.0038495 | 0.020189 | -0.0041464 | -0.43488 | 60.5713 | -60.8093 | 61.0199 | -60.5118 | -60.9558 | -61.0565 | -0.29297 | 60.5576 | -60.8963 | 60.8643 | -60.8002 | -60.8734 | -61.0474 | 0.041199 | -0.19226 | 0.25635 | 0.33874 | -0.20599 | -0.10529 | -0.24719 | -0.14648 | -0.045776 | -0.20599 | 0.10071 | 0.050354 | -0.19684 | -0.022888 | -0.15106 | 0.022888 | 0.29755 | 121.8292 | 0.09613 | 121.7606 | 121.3806 | 121.4539 | 121.4218 | 121.4081 | -121.5729 | -121.6599 | 121.8704 | 121.7148 | 60.4156 | 60.5576
461.5625 | 121.8109 | -60.91 | 60.7864 | -0.0016785 | 5.7148 | 0.066755 | 0.067492 | -0.00071343 | -0.0069683 | -0.00087163 | -0.0036011 | 0.002446 | 0.066302 | 0.056783 | -0.0034223 | 0.020403 | -0.0045736 | -0.47607 | 60.6308 | -60.8368 | 60.9329 | -60.6766 | -61.0931 | -61.1847 | -0.48065 | 60.6033 | -60.8871 | 60.7407 | -60.9329 | -61.0153 | -61.1389 | 0.073242 | -0.15564 | 0.14648 | 0.23346 | -0.27466 | -0.18311 | -0.3479 | -0.25635 | 0.022888 | -0.1831 | -0.045776 | -0.022888 | -0.22888 | -0.10529 | -0.25177 | -0.12817 | 0.16022 | 121.7697 | -0.045776 | 121.6278 | 121.4676 | 121.4905 | 121.5408 | 121.5134 | -121.6232 | -121.6736 | 121.843 | 121.6507 | 60.434 | 60.4294
463.2969 | 121.9528 | -60.7956 | 60.8414 | -0.0016785 | 5.7234 | 0.064619 | 0.062151 | 0.0014228 | -0.0048321 | -0.00065803 | -0.00054933 | -0.0005448 | 0.06673 | 0.064687 | -0.0047039 | 0.020403 | 0.0014078 | -0.43488 | 60.585 | -60.7498 | 61.0886 | -60.5072 | -60.9238 | -61.0107 | -0.29755 | 60.5942 | -60.791 | 60.9375 | -60.704 | -60.7727 | -60.9604 | 0.045776 | -0.25635 | 0.24719 | 0.28839 | -0.21515 | -0.12817 | -0.26093 | -0.17395 | 0.004577 | -0.24719 | 0.09613 | 0.091552 | -0.1648 | 0.022888 | -0.16937 | 0.018311 | 0.24262 | 121.8384 | 0.086975 | 121.7285 | 121.3348 | 121.3852 | 121.3806 | 121.3898 | -121.5912 | -121.6324 | 121.8842 | 121.7331 | 60.3607 | 60.498
464.9688 | 121.962 | -60.791 | 60.8185 | 0.005951 | 5.144 | 0.066969 | 0.063433 | 0.00035457 | -0.0059003 | -0.00023063 | -0.0066527 | 0.0015914 | 0.065448 | 0.062124 | -0.0027813 | 0.020617 | -0.0037192 | -0.3891 | 60.5759 | -60.759 | 61.1069 | -60.4156 | -60.8551 | -60.9558 | -0.21973 | 60.585 | -60.7956 | 60.9375 | -60.6857 | -60.7498 | -60.9558 | 0.032044 | -0.24261 | 0.28839 | 0.37537 | -0.16479 | -0.064087 | -0.19684 | -0.096131 | -0.004577 | -0.23346 | 0.11902 | 0.10529 | -0.16479 | 0.041199 | -0.16022 | 0.045776 | 0.34332 | 121.8658 | 0.10986 | 121.7331 | 121.3348 | 121.3806 | 121.3669 | 121.376 | -121.5775 | -121.6141 | 121.8979 | 121.7285 | 60.4019 | 60.5713
466.7188 | 121.8338 | -60.8368 | 60.8597 | 0.02121 | 5.2669 | 0.066969 | 0.067492 | -0.002636 | -0.0046185 | -0.0012988 | 0.014709 | 0.004155 | 0.066943 | 0.058492 | -0.0059857 | 0.018053 | 0.0026896 | -0.37994 | 60.6857 | -60.7864 | 60.9924 | -60.5942 | -60.9787 | -61.084 | -0.36163 | 60.6674 | -60.8688 | 60.8231 | -60.8047 | -60.8734 | -61.0565 | 0.050354 | -0.17395 | 0.13275 | 0.24262 | -0.24719 | -0.14191 | -0.29755 | -0.19226 | -0.032043 | -0.19226 | -0.036621 | 0.032043 | -0.21973 | -0.036621 | -0.18768 | -0.004578 | 0.19226 | 121.7789 | 0.064086 | 121.6919 | 121.4722 | 121.5363 | 121.5225 | 121.5042 | -121.6461 | -121.7285 | 121.8292 | 121.6599 | 60.4568 | 60.4752
468.4531 | 121.9528 | -60.8002 | 60.8276 | -0.009308 | 5.3399 | 0.06526 | 0.062365 | 0.0020636 | -0.0078229 | -0.0032214 | -0.0066527 | 0.0026596 | 0.069079 | 0.062765 | -0.0064129 | 0.01784 | -0.0024374 | -0.37079 | 60.6079 | -60.7269 | 61.1206 | -60.4385 | -60.8597 | -60.9695 | -0.21057 | 60.5667 | -60.791 | 60.9421 | -60.6812 | -60.7498 | -60.965 | 0.073242 | -0.21973 | 0.29297 | 0.36163 | -0.16937 | -0.059509 | -0.24261 | -0.13275 | 0.009155 | -0.26093 | 0.11444 | 0.11902 | -0.16479 | 0.050354 | -0.17395 | 0.041199 | 0.28839 | 121.8475 | 0.10986 | 121.7331 | 121.3348 | 121.3577 | 121.4081 | 121.3669 | -121.5546 | -121.6187 | 121.9208 | 121.7422 | 60.4294 | 60.5896
470.125 | 121.8338 | -60.791 | 60.878 | -0.009308 | 5.2592 | 0.066755 | 0.064074 | 0.00035457 | -0.0044049 | -0.0021532 | -0.0066527 | 0.0013778 | 0.066089 | 0.061483 | -0.0038495 | 0.019121 | -0.005001 | -0.36163 | 60.6079 | -60.7315 | 61.0565 | -60.5255 | -60.9329 | -61.0336 | -0.32044 | 60.6537 | -60.8231 | 60.8505 | -60.7956 | -60.8505 | -61.0382 | 0.05951 | -0.27008 | 0.17853 | 0.2655 | -0.24261 | -0.14191 | -0.30212 | -0.20142 | -0.032043 | -0.2243 | -0.027466 | -0.004577 | -0.24719 | -0.059509 | -0.21515 | -0.027466 | 0.20599 | 121.788 | 0.027466 | 121.6736 | 121.3394 | 121.4767 | 121.3989 | 121.4447 | -121.6095 | -121.7011 | 121.8475 | 121.6415 | 60.4294 | 60.4706
471.8594 | 121.8246 | -60.8917 | 60.7819 | -0.016937 | 5.6813 | 0.067396 | 0.06856 | 0.00078177 | -0.0052595 | 0.0012646 | -0.0036011 | 0.002446 | 0.06737 | 0.06661 | -0.0036359 | 0.018267 | -0.0024374 | -0.50354 | 60.5988 | -60.8185 | 60.9009 | -60.7132 | -61.1023 | -61.1801 | -0.45776 | 60.5988 | -60.9146 | 60.7773 | -60.9146 | -60.997 | -61.1206 | 0.073243 | -0.18311 | 0.11902 | 0.17853 | -0.28839 | -0.21057 | -0.36163 | -0.28381 | -0.022888 | -0.18311 | -0.004577 | -0.022888 | -0.22888 | -0.10528 | -0.20599 | -0.082397 | 0.10528 | 121.7194 | 0 | 121.6919 | 121.4172 | 121.5134 | 121.4905 | 121.4905 | -121.6003 | -121.6965 | 121.7926 | 121.669 | 60.3882 | 60.434
473.6094 | 121.7926 | -60.878 | 60.8093 | -0.0016785 | 5.8614 | 0.069319 | 0.066638 | -0.00049983 | -0.0041913 | -0.0019396 | -0.00054933 | 0.0047958 | 0.066302 | 0.057851 | -0.0049175 | 0.020403 | -0.001583 | -0.46234 | 60.5896 | -60.8185 | 60.9375 | -60.6537 | -61.084 | -61.1755 | -0.42114 | 60.5988 | -60.8826 | 60.7773 | -60.9055 | -60.9787 | -61.1252 | 0.05951 | -0.21973 | 0.12817 | 0.2243 | -0.29755 | -0.20599 | -0.35706 | -0.2655 | -0.004577 | -0.21057 | -0.032043 | -0.027466 | -0.24719 | -0.10071 | -0.24262 | -0.096131 | 0.16479 | 121.756 | -0.022889 | 121.6599 | 121.4081 | 121.4813 | 121.4676 | 121.4767 | -121.6278 | -121.6919 | 121.8155 | 121.6553 | 60.4156 | 60.4568
475.2812 | 121.8521 | -60.8505 | 60.8276 | 0.005951 | 5.9804 | 0.068464 | 0.066638 | 0.0012092 | -0.0048321 | -0.00065803 | 0.0055543 | 0.0033004 | 0.069934 | 0.055074 | -0.0066265 | 0.018694 | -0.0011558 | -0.39825 | 60.6354 | -60.791 | 61.0245 | -60.5621 | -60.9787 | -61.0703 | -0.31128 | 60.6354 | -60.8551 | 60.8688 | -60.8047 | -60.878 | -61.0199 | 0.059509 | -0.19226 | 0.19684 | 0.28839 | -0.21973 | -0.12817 | -0.27923 | -0.18768 | -0.004578 | -0.19226 | 0.041198 | 0.045776 | -0.16937 | -0.027466 | -0.16479 | -0.022888 | 0.22888 | 121.8155 | 0.050354 | 121.7239 | 121.4264 | 121.4905 | 121.4859 | 121.4859 | -121.6187 | -121.6827 | 121.875 | 121.7194 | 60.4523 | 60.5392
477 | 121.8338 | -60.9192 | 60.7681 | -0.009308 | 6.3072 | 0.066328 | 0.065569 | 0.0061224 | -0.0054731 | -0.0030078 | -0.0036011 | 0.0026596 | 0.06673 | 0.059347 | -0.0027813 | 0.019549 | -0.00094199 | -0.5127 | 60.5988 | -60.8231 | 60.9055 | -60.6674 | -61.0886 | -61.171 | -0.45319 | 60.5896 | -60.878 | 60.7819 | -60.8826 | -60.965 | -61.1069 | 0.09613 | -0.16937 | 0.13733 | 0.25177 | -0.25177 | -0.16937 | -0.3479 | -0.2655 | 0.041198 | -0.17853 | 0.013733 | 0.036621 | -0.18768 | -0.045777 | -0.22888 | -0.086975 | 0.15564 | 121.7285 | -0.004577 | 121.6599 | 121.4218 | 121.4676 | 121.5179 | 121.5088 | -121.5912 | -121.6461 | 121.8246 | 121.701 | 60.4065 | 60.466
478.7344 | 121.9345 | -60.8551 | 60.7315 | -0.0016785 | 6.5326 | 0.068678 | 0.06322 | 0.0024908 | -0.0044049 | 0.00062377 | -0.0036011 | 0.0018052 | 0.067584 | 0.060201 | -0.0061993 | 0.019121 | -0.0017966 | -0.50812 | 60.5759 | -60.8185 | 60.9558 | -60.6308 | -61.0428 | -61.116 | -0.37537 | 60.5438 | -60.9009 | 60.8368 | -60.8231 | -60.8826 | -61.0428 | 0.036622 | -0.15564 | 0.2243 | 0.22431 | -0.26093 | -0.18768 | -0.29755 | -0.22431 | -0.045776 | -0.18768 | 0.10529 | 0.032044 | -0.18768 | -0.027465 | -0.14191 | 0.018311 | 0.18768 | 121.7743 | 0.07782 | 121.7377 | 121.3943 | 121.4447 | 121.431 | 121.3989 | -121.55 | -121.6324 | 121.8109 | 121.6919 | 60.347 | 60.4797
480.4062 | 121.8292 | -60.9283 | 60.8002 | -0.009308 | 6.5356 | 0.065901 | 0.065997 | 0.0046272 | -0.0052595 | -0.0010852 | -0.0036011 | 0.003514 | 0.067157 | 0.061696 | -0.0061993 | 0.018694 | -0.0013694 | -0.51727 | 60.5988 | -60.8414 | 60.8917 | -60.6903 | -61.1069 | -61.1801 | -0.46692 | 60.5759 | -60.8963 | 60.7544 | -60.9146 | -60.9924 | -61.116 | 0.086975 | -0.20142 | 0.091553 | 0.23804 | -0.25177 | -0.17853 | -0.33875 | -0.2655 | 0.032044 | -0.2243 | -0.045776 | 0.013733 | -0.18768 | -0.064087 | -0.21973 | -0.096131 | 0.15106 | 121.7331 | -0.018311 | 121.6507 | 121.4401 | 121.4722 | 121.5271 | 121.5042 | -121.6415 | -121.6965 | 121.8201 | 121.6827 | 60.4111 | 60.4614
482.1406 | 121.7972 | -60.8231 | 60.878 | -0.016937 | 6.4969 | 0.065687 | 0.064715 | -0.006054 | -0.0065411 | -0.00087163 | -0.0066527 | 0.002446 | 0.069079 | 0.059347 | -0.0081219 | 0.020617 | -0.00094199 | -0.40283 | 60.6354 | -60.7544 | 60.9787 | -60.585 | -60.9879 | -61.0657 | -0.37994 | 60.6491 | -60.8093 | 60.8322 | -60.8047 | -60.8643 | -61.0428 | 0.068664 | -0.24262 | 0.10071 | 0.23804 | -0.24262 | -0.16479 | -0.31128 | -0.23346 | 0.013733 | -0.22888 | -0.045777 | 0.01831 | -0.21973 | -0.041199 | -0.23346 | -0.054932 | 0.16937 | 121.7331 | 0.004577 | 121.6415 | 121.3898 | 121.4584 | 121.4584 | 121.4722 | -121.6324 | -121.6873 | 121.8018 | 121.6553 | 60.4202 | 60.4431
483.875 | 121.9116 | -60.8276 | 60.8047 | -0.0016785 | 6.4865 | 0.066969 | 0.062792 | 0.00056817 | -0.0037641 | -0.0021532 | -0.0066527 | 0.0015914 | 0.064807 | 0.057424 | -0.0038495 | 0.021044 | -0.0028646 | -0.46692 | 60.5804 | -60.7773 | 60.997 | -60.5621 | -60.965 | -61.0611 | -0.35248 | 60.5759 | -60.8231 | 60.8871 | -60.759 | -60.8185 | -61.0153 | 0.050354 | -0.22431 | 0.19226 | 0.2655 | -0.23346 | -0.13733 | -0.28381 | -0.18768 | 0.004578 | -0.22888 | 0.082397 | 0.068665 | -0.18768 | 0.009156 | -0.19226 | 0.004578 | 0.21515 | 121.7743 | 0.064087 | 121.7102 | 121.3577 | 121.3989 | 121.4081 | 121.4035 | -121.582 | -121.6278 | 121.8246 | 121.7148 | 60.3607 | 60.4752
485.6094 | 121.8384 | -60.878 | 60.8093 | -0.0016785 | 6.5287 | 0.066755 | 0.065997 | 0.0024908 | -0.0048321 | -0.0021532 | -0.00054933 | 0.0033004 | 0.06737 | 0.055715 | -0.0044903 | 0.01848 | -0.0028646 | -0.3891 | 60.6033 | -60.8002 | 60.997 | -60.5759 | -61.0199 | -61.1069 | -0.36163 | 60.6216 | -60.8459 | 60.8047 | -60.8414 | -60.9192 | -61.0703 | 0.07782 | -0.20599 | 0.18768 | 0.30212 | -0.22888 | -0.14191 | -0.3067 | -0.21973 | 0.032044 | -0.18768 | -0.004577 | 0.036621 | -0.19226 | -0.041198 | -0.2243 | -0.073242 | 0.2243 | 121.7972 | 0.004577 | 121.6507 | 121.4035 | 121.4676 | 121.4813 | 121.4996 | -121.6095 | -121.6553 | 121.875 | 121.6827 | 60.4889 | 60.5164
487.2812 | 121.9208 | -60.7864 | 60.7956 | -0.0016785 | 6.5723 | 0.066328 | 0.063006 | 0.0027044 | -0.0071821 | -0.005144 | -0.0066527 | -0.0003312 | 0.066516 | 0.062337 | -0.0059857 | 0.019762 | 0.00055321 | -0.44403 | 60.5667 | -60.7407 | 61.0657 | -60.4935 | -60.8963 | -60.9787 | -0.28381 | 60.5896 | -60.8093 | 60.9192 | -60.7178 | -60.7636 | -60.9604 | 0.045776 | -0.22888 | 0.27008 | 0.29297 | -0.19226 | -0.10986 | -0.23804 | -0.15564 | -0.022888 | -0.20599 | 0.1236 | 0.068665 | -0.17395 | 0.022888 | -0.15106 | 0.045776 | 0.24719 | 121.8063 | 0.091553 | 121.7285 | 121.3074 | 121.3989 | 121.3531 | 121.376 | -121.5363 | -121.6049 | 121.8521 | 121.7056 | 60.3424 | 60.5026
488.9531 | 121.9437 | -60.8551 | 60.7452 | -0.0016785 | 6.5958 | 0.068464 | 0.062792 | 0.003559 | -0.0037641 | -0.0010852 | -0.0036011 | 9.6204e-05 | 0.064593 | 0.058706 | -0.0038495 | 0.022112 | -0.006069 | -0.4303 | 60.5255 | -60.7956 | 61.0107 | -60.5484 | -61.0016 | -61.0886 | -0.31586 | 60.5118 | -60.8688 | 60.8688 | -60.7819 | -60.8597 | -61.0199 | 0.05951 | -0.21973 | 0.2655 | 0.3067 | -0.23346 | -0.14648 | -0.29297 | -0.20599 | -0.013732 | -0.23346 | 0.1236 | 0.073243 | -0.16479 | -0.004577 | -0.15106 | 0.009155 | 0.24719 | 121.8063 | 0.086975 | 121.7377 | 121.3211 | 121.3806 | 121.3806 | 121.3669 | -121.5408 | -121.6141 | 121.8658 | 121.7239 | 60.4248 | 60.5392
490.6875 | 121.8887 | -60.8459 | 60.8139 | 0.02121 | 6.5326 | 0.069105 | 0.064715 | 0.00035457 | -0.0035505 | -0.00087163 | 0.0025025 | 0.002446 | 0.06737 | 0.060201 | -0.0051313 | 0.019762 | 0.00012601 | -0.46692 | 60.5804 | -60.8185 | 61.0107 | -60.5667 | -60.9695 | -61.0565 | -0.36163 | 60.5896 | -60.8414 | 60.8322 | -60.8139 | -60.8643 | -61.0336 | 0.027466 | -0.23346 | 0.19684 | 0.27924 | -0.21057 | -0.1236 | -0.23804 | -0.15106 | 0.004577 | -0.2243 | 0.01831 | 0.032043 | -0.18768 | -0.018311 | -0.19226 | -0.022888 | 0.25177 | 121.8292 | 0.027466 | 121.6736 | 121.3989 | 121.431 | 121.4264 | 121.4355 | -121.6324 | -121.6553 | 121.8567 | 121.6782 | 60.379 | 60.4843
492.4219 | 121.8155 | -60.8276 | 60.8459 | -0.009308 | 6.6249 | 0.064832 | 0.065569 | -0.004986 | -0.0056867 | 0.00062377 | 0.011658 | 0.0047958 | 0.065875 | 0.055074 | -0.0074811 | 0.017626 | -0.0022238 | -0.41657 | 60.6674 | -60.7269 | 60.9833 | -60.5621 | -60.9558 | -61.0611 | -0.37537 | 60.6949 | -60.8597 | 60.8139 | -60.8368 | -60.8917 | -61.0428 | 0.10071 | -0.17853 | 0.13733 | 0.2655 | -0.23346 | -0.12817 | -0.33417 | -0.22888 | -0.032043 | -0.15106 | -0.032043 | -0.009155 | -0.21515 | -0.064087 | -0.18311 | -0.032044 | 0.16479 | 121.7102 | 0.022888 | 121.6736 | 121.3943 | 121.5546 | 121.4951 | 121.5225 | -121.5729 | -121.7056 | 121.8109 | 121.6415 | 60.4111 | 60.4523
494.0938 | 121.8018 | -60.8276 | 60.9009 | -0.0016785 | 6.7069 | 0.066328 | 0.064288 | 0.0016364 | -0.0050457 | -0.0010852 | -0.00054933 | 0.0020188 | 0.066943 | 0.060842 | -0.0072675 | 0.017412 | -0.0013694 | -0.41657 | 60.6354 | -60.7452 | 61.0062 | -60.5621 | -60.9787 | -61.0703 | -0.35706 | 60.6628 | -60.8002 | 60.8185 | -60.8139 | -60.878 | -61.0428 | 0.082398 | -0.2655 | 0.10529 | 0.2655 | -0.24261 | -0.15106 | -0.32501 | -0.23346 | 0.027466 | -0.23804 | -0.082398 | 0.013733 | -0.21515 | -0.050354 | -0.24262 | -0.07782 | 0.1831 | 121.7514 | -0.013733 | 121.6187 | 121.3806 | 121.463 | 121.463 | 121.4905 | -121.6461 | -121.7011 | 121.8338 | 121.6461 | 60.4111 | 60.4706
495.8438 | 121.9345 | -60.7773 | 60.8185 | -0.0016785 | 6.7122 | 0.066969 | 0.064074 | -0.006054 | -0.0041913 | 0.0021192 | -0.0036011 | 0.002446 | 0.066516 | 0.063405 | -0.0034223 | 0.01848 | -0.0041464 | -0.3891 | 60.5896 | -60.7498 | 61.0977 | -60.434 | -60.8826 | -60.9741 | -0.22888 | 60.5942 | -60.7956 | 60.9329 | -60.6812 | -60.7452 | -60.9512 | 0.027466 | -0.22888 | 0.27924 | 0.34332 | -0.19684 | -0.10529 | -0.2243 | -0.13275 | -0.01831 | -0.2243 | 0.11444 | 0.096131 | -0.17395 | 0.032044 | -0.15564 | 0.050354 | 0.31586 | 121.8475 | 0.11444 | 121.7285 | 121.3394 | 121.3898 | 121.3669 | 121.3715 | -121.5683 | -121.6141 | 121.875 | 121.7102 | 60.3882 | 60.5484
497.5625 | 121.8155 | -60.8276 | 60.8597 | -0.009308 | 6.7097 | 0.064405 | 0.065569 | 0.0016364 | -0.0069683 | -0.0025806 | -0.0066527 | 0.003514 | 0.067798 | 0.056569 | -0.0072675 | 0.016772 | -0.0017966 | -0.44403 | 60.64 | -60.7407 | 60.9879 | -60.5804 | -60.9787 | -61.0611 | -0.40283 | 60.6949 | -60.8551 | 60.8139 | -60.8322 | -60.9009 | -61.0336 | 0.086975 | -0.21973 | 0.12817 | 0.24719 | -0.23346 | -0.15106 | -0.32043 | -0.23804 | -0.027466 | -0.16479 | -0.045776 | -0.004577 | -0.20599 | -0.073242 | -0.17853 | -0.045776 | 0.16022 | 121.7285 | 0.022889 | 121.669 | 121.3806 | 121.55 | 121.4676 | 121.5225 | -121.6003 | -121.7148 | 121.8155 | 121.6415 | 60.3836 | 60.4248
499.2188 | 121.9299 | -60.7956 | 60.791 | -0.0016785 | 6.7584 | 0.06825 | 0.06386 | -0.0028498 | -0.0056867 | -0.001726 | -0.0036011 | 0.0005234 | 0.067157 | 0.065328 | -0.0049175 | 0.018908 | -0.001583 | -0.45319 | 60.5804 | -60.7636 | 61.0245 | -60.5347 | -60.9467 | -61.0336 | -0.3067 | 60.5988 | -60.8047 | 60.878 | -60.7178 | -60.7956 | -60.9695 | 0.032043 | -0.21057 | 0.23346 | 0.26092 | -0.23804 | -0.15106 | -0.27008 | -0.1831 | -0.009156 | -0.19226 | 0.086975 | 0.07782 | -0.17395 | 0 | -0.16479 | 0.009156 | 0.22888 | 121.788 | 0.086976 | 121.6827 | 121.344 | 121.4035 | 121.376 | 121.3943 | -121.5546 | -121.5958 | 121.8201 | 121.6736 | 60.3424 | 60.4889
500.9531 | 121.9254 | -60.8414 | 60.7315 | -0.016937 | 6.7479 | 0.06825 | 0.064288 | 0.00035457 | -0.0044049 | 0.00062377 | -0.0066527 | 0.003514 | 0.066943 | 0.067678 | -4.308e-06 | 0.020403 | -8.7586e-05 | -0.44861 | 60.5484 | -60.7819 | 61.0199 | -60.553 | -60.9924 | -61.0794 | -0.32501 | 60.5209 | -60.8597 | 60.878 | -60.7681 | -60.8459 | -61.0016 | 0.05951 | -0.18311 | 0.28839 | 0.28839 | -0.23804 | -0.15106 | -0.29755 | -0.21057 | -0.01831 | -0.21057 | 0.14648 | 0.073243 | -0.16022 | -0.004577 | -0.14191 | 0.013733 | 0.22888 | 121.8018 | 0.091553 | 121.7377 | 121.3303 | 121.3806 | 121.3898 | 121.3623 | -121.5134 | -121.5912 | 121.8613 | 121.7194 | 60.3928 | 60.5164
502.6875 | 121.8338 | -60.8414 | 60.8047 | 0.01358 | 6.7729 | 0.06761 | 0.066424 | 0.0027044 | -0.0037641 | -0.00065803 | 0.0055543 | 0.0028732 | 0.068225 | 0.065969 | -0.0085491 | 0.017412 | -0.0039328 | -0.38452 | 60.6491 | -60.8047 | 61.0153 | -60.5301 | -60.9604 | -61.0611 | -0.3067 | 60.6445 | -60.8551 | 60.8322 | -60.8002 | -60.8734 | -61.0245 | 0.036621 | -0.15564 | 0.21057 | 0.31128 | -0.21973 | -0.11902 | -0.25635 | -0.15564 | -0.013733 | -0.16022 | 0.027465 | 0.041199 | -0.18311 | -0.032043 | -0.16937 | -0.01831 | 0.27466 | 121.8201 | 0.054932 | 121.6873 | 121.4539 | 121.4996 | 121.4905 | 121.4859 | -121.6095 | -121.6599 | 121.8567 | 121.6736 | 60.4568 | 60.5347
504.4219 | 121.8246 | -60.8231 | 60.8643 | -0.0016785 | 6.7968 | 0.066755 | 0.065783 | -0.0037042 | -0.0086773 | -0.0036486 | -0.00054933 | 0.0015914 | 0.067157 | 0.063405 | -0.0051313 | 0.019762 | -0.0045736 | -0.36621 | 60.6216 | -60.7178 | 61.0748 | -60.498 | -60.9146 | -61.0062 | -0.32044 | 60.6171 | -60.7956 | 60.8551 | -60.7819 | -60.8414 | -61.0199 | 0.10529 | -0.24262 | 0.21057 | 0.32501 | -0.18311 | -0.091553 | -0.28839 | -0.19684 | 0.027466 | -0.24719 | -0.009155 | 0.041199 | -0.19684 | -0.018311 | -0.2243 | -0.045777 | 0.21973 | 121.7926 | 0.013733 | 121.6507 | 121.3394 | 121.4127 | 121.4447 | 121.4401 | -121.582 | -121.6599 | 121.8979 | 121.6782 | 60.4568 | 60.5026
506.1719 | 121.8155 | -60.791 | 60.878 | -0.016937 | 6.7842 | 0.066328 | 0.062151 | 0.0012092 | -0.0056867 | -0.0012988 | -0.0036011 | 0.0015914 | 0.066302 | 0.05956 | -0.0074811 | 0.018694 | -0.00030119 | -0.35248 | 60.6125 | -60.7315 | 61.0703 | -60.5026 | -60.8917 | -61.0153 | -0.30212 | 60.6216 | -60.7956 | 60.8643 | -60.7727 | -60.8368 | -61.0062 | 0.05951 | -0.2655 | 0.19226 | 0.28839 | -0.2243 | -0.10071 | -0.28381 | -0.16022 | -0.004577 | -0.25635 | -0.013733 | 0.018311 | -0.21515 | -0.045776 | -0.21057 | -0.041199 | 0.22888 | 121.8018 | 0.022888 | 121.6599 | 121.344 | 121.4172 | 121.4035 | 121.4127 | -121.6095 | -121.6736 | 121.8613 | 121.6553 | 60.4385 | 60.4889
507.8438 | 121.8063 | -60.8734 | 60.791 | -0.009308 | 6.7947 | 0.06761 | 0.066638 | -0.0013544 | -0.0061139 | -0.0038622 | 0.0025025 | 0.0047958 | 0.066943 | 0.060842 | -0.0040631 | 0.017626 | 0.00055321 | -0.5127 | 60.585 | -60.8322 | 60.8963 | -60.672 | -61.1023 | -61.1664 | -0.4715 | 60.5713 | -60.91 | 60.759 | -60.8963 | -60.9833 | -61.1023 | 0.041199 | -0.20599 | 0.10529 | 0.20142 | -0.29297 | -0.22888 | -0.33417 | -0.27008 | -0.036621 | -0.21973 | -0.032044 | -0.022888 | -0.22888 | -0.10986 | -0.19226 | -0.073242 | 0.16022 | 121.7285 | 0.013733 | 121.669 | 121.4172 | 121.4813 | 121.4584 | 121.4447 | -121.6232 | -121.7011 | 121.7697 | 121.6324 | 60.3607 | 60.4019
509.5781 | 121.8292 | -60.8139 | 60.8734 | -0.0016785 | 6.8035 | 0.067396 | 0.065783 | -0.00071343 | -0.0061139 | -0.0019396 | -0.0066527 | 0.0033004 | 0.065448 | 0.054861 | -0.0064129 | 0.019549 | 0.0029032 | -0.38452 | 60.6171 | -60.7224 | 61.0474 | -60.4889 | -60.9055 | -61.0107 | -0.32044 | 60.6308 | -60.8139 | 60.8505 | -60.7864 | -60.8322 | -61.0199 | 0.091553 | -0.25635 | 0.17395 | 0.32501 | -0.19684 | -0.091553 | -0.28839 | -0.18311 | 0 | -0.24262 | -0.022888 | 0.027466 | -0.20599 | -0.01831 | -0.20599 | -0.01831 | 0.23346 | 121.7697 | 0.027466 | 121.6644 | 121.3394 | 121.4447 | 121.431 | 121.4447 | -121.5958 | -121.6873 | 121.8613 | 121.6644 | 60.4294 | 60.4935
511.3281 | 121.8155 | -60.9009 | 60.791 | -0.0016785 | 6.8212 | 0.068037 | 0.065997 | -0.0034906 | -0.0046185 | 0.001051 | 0.0025025 | 0.0020188 | 0.069507 | 0.059987 | -0.0044903 | 0.01784 | -0.0052146 | -0.5127 | 60.5804 | -60.8276 | 60.8871 | -60.6812 | -61.1069 | -61.1755 | -0.46234 | 60.5713 | -60.8963 | 60.7773 | -60.9009 | -60.9833 | -61.0977 | 0.073242 | -0.21057 | 0.09613 | 0.21973 | -0.27466 | -0.20599 | -0.3479 | -0.27924 | 0.004578 | -0.21973 | -0.013733 | 0 | -0.19684 | -0.082397 | -0.20142 | -0.086975 | 0.14649 | 121.7148 | -0.004578 | 121.6736 | 121.4081 | 121.4676 | 121.4813 | 121.4722 | -121.6187 | -121.6873 | 121.788 | 121.6782 | 60.3882 | 60.4385
513 | 121.9208 | -60.7819 | 60.8231 | -0.0016785 | 6.812 | 0.067182 | 0.06386 | -0.00092703 | -0.0069683 | -0.0019396 | 0.0025025 | 0.0009506 | 0.068011 | 0.06191 | -0.0057721 | 0.019121 | -0.003292 | -0.3891 | 60.5988 | -60.7315 | 61.0931 | -60.4523 | -60.8688 | -60.9741 | -0.24261 | 60.6171 | -60.8139 | 60.9238 | -60.6857 | -60.7681 | -60.9604 | 0.050354 | -0.2243 | 0.27008 | 0.32959 | -0.19226 | -0.086975 | -0.24261 | -0.13733 | -0.032044 | -0.20599 | 0.10071 | 0.09613 | -0.17853 | 0.013733 | -0.14648 | 0.045777 | 0.27923 | 121.8246 | 0.12817 | 121.7377 | 121.3303 | 121.431 | 121.3806 | 121.3989 | -121.5546 | -121.637 | 121.875 | 121.7056 | 60.3928 | 60.5392
514.7344 | 121.8842 | -60.8414 | 60.7773 | 0.02121 | 6.827 | 0.068891 | 0.063006 | 0.0050544 | -0.0033369 | 0.001051 | 0.0086061 | 0.0018052 | 0.06737 | 0.068532 | -0.0051313 | 0.021471 | -0.005001 | -0.46234 | 60.5759 | -60.7727 | 61.0107 | -60.5438 | -60.9741 | -61.0565 | -0.36621 | 60.5484 | -60.878 | 60.8643 | -60.7956 | -60.8643 | -61.0107 | 0.068665 | -0.20142 | 0.23346 | 0.29755 | -0.21515 | -0.13275 | -0.28381 | -0.20142 | -0.036621 | -0.22888 | 0.086975 | 0.045777 | -0.16937 | -0.022888 | -0.13275 | 0.013733 | 0.22888 | 121.7834 | 0.082398 | 121.7422 | 121.3486 | 121.4264 | 121.4172 | 121.3898 | -121.55 | -121.6553 | 121.8521 | 121.7056 | 60.379 | 60.4752
516.4062 | 121.7926 | -60.8139 | 60.8734 | -0.0016785 | 6.8366 | 0.06526 | 0.064501 | 0.00035457 | -0.0076093 | -0.0010852 | -0.00054933 | 0.0026596 | 0.066516 | 0.073232 | -0.0061993 | 0.020189 | -0.0041464 | -0.41199 | 60.6171 | -60.7452 | 61.0016 | -60.5347 | -60.9558 | -61.0519 | -0.35706 | 60.6491 | -60.8047 | 60.8276 | -60.8047 | -60.8688 | -61.0428 | 0.068665 | -0.25635 | 0.12817 | 0.27924 | -0.23804 | -0.14191 | -0.3067 | -0.21057 | 0.009155 | -0.2243 | -0.045776 | 0.009155 | -0.22888 | -0.054931 | -0.23804 | -0.064086 | 0.21057 | 121.7468 | 0 | 121.6324 | 121.3623 | 121.4539 | 121.431 | 121.463 | -121.6187 | -121.6782 | 121.8155 | 121.6415 | 60.4019 | 60.4568
518.1406 | 121.9208 | -60.7681 | 60.7864 | -0.0016785 | 6.8409 | 0.068678 | 0.064929 | -0.00092703 | -0.0069683 | 0.0012646 | -0.00054933 | 0.0037278 | 0.065661 | 0.067464 | -0.0044903 | 0.017626 | -0.0020102 | -0.38452 | 60.585 | -60.7224 | 61.116 | -60.4385 | -60.8597 | -60.9512 | -0.2243 | 60.5988 | -60.791 | 60.9421 | -60.6674 | -60.7407 | -60.9329 | 0.045776 | -0.20142 | 0.32959 | 0.32959 | -0.18311 | -0.091553 | -0.22888 | -0.13733 | -0.022889 | -0.18768 | 0.15564 | 0.10071 | -0.16479 | 0.027465 | -0.14191 | 0.050354 | 0.28381 | 121.8384 | 0.1236 | 121.7331 | 121.3074 | 121.3898 | 121.3531 | 121.3669 | -121.5088 | -121.5775 | 121.8842 | 121.7102 | 60.3836 | 60.5438
519.875 | 121.7926 | -60.8643 | 60.8093 | -0.0016785 | 6.8449 | 0.069746 | 0.065142 | 0.00099557 | -0.0063275 | -0.00044443 | -0.0036011 | 0.0033004 | 0.067798 | 0.055929 | -0.0038495 | 0.021258 | -0.0030784 | -0.47607 | 60.585 | -60.8002 | 60.9283 | -60.6537 | -61.0886 | -61.1572 | -0.44403 | 60.5942 | -60.8597 | 60.7636 | -60.8963 | -60.9558 | -61.0931 | 0.064087 | -0.2243 | 0.11902 | 0.21057 | -0.29297 | -0.2243 | -0.35706 | -0.28839 | 0.004578 | -0.21515 | -0.045776 | -0.032043 | -0.22888 | -0.091553 | -0.23346 | -0.096131 | 0.14648 | 121.7285 | -0.036621 | 121.6232 | 121.3852 | 121.4539 | 121.4493 | 121.4584 | -121.6095 | -121.669 | 121.7926 | 121.6278 | 60.3882 | 60.4202
521.5469 | 121.7926 | -60.8688 | 60.791 | -0.0016785 | 6.8509 | 0.068037 | 0.067278 | 0.0046272 | -0.0061139 | -0.0025806 | -0.00054933 | 0.003514 | 0.066943 | 0.060842 | -0.0038495 | 0.021044 | -0.0017966 | -0.51727 | 60.5759 | -60.8276 | 60.8871 | -60.6812 | -61.1069 | -61.1755 | -0.44861 | 60.585 | -60.8917 | 60.759 | -60.9146 | -60.9741 | -61.0886 | 0.041198 | -0.21515 | 0.09613 | 0.18768 | -0.3067 | -0.23804 | -0.3479 | -0.27924 | -0.022889 | -0.20599 | -0.032044 | -0.045777 | -0.21973 | -0.10529 | -0.19684 | -0.082397 | 0.14649 | 121.7148 | -0.022888 | 121.6507 | 121.4035 | 121.4767 | 121.4447 | 121.4539 | -121.6187 | -121.6827 | 121.756 | 121.6278 | 60.3516 | 60.4202
523.2812 | 121.8613 | -60.7681 | 60.8597 | -0.0016785 | 6.8611 | 0.067396 | 0.061511 | -0.00028623 | -0.0065411 | 0.00062377 | -0.0036011 | 0.0026596 | 0.064593 | 0.057851 | -0.0087629 | 0.020403 | -0.0011558 | -0.38452 | 60.5942 | -60.7269 | 61.084 | -60.4752 | -60.878 | -60.9741 | -0.28381 | 60.6354 | -60.7864 | 60.8826 | -60.7269 | -60.8093 | -60.9787 | 0.041198 | -0.2655 | 0.2243 | 0.29297 | -0.20599 | -0.10986 | -0.24719 | -0.15106 | -0.018311 | -0.2243 | 0.022888 | 0.041198 | -0.21057 | -0.041199 | -0.19226 | -0.022888 | 0.25177 | 121.8109 | 0.059509 | 121.669 | 121.3211 | 121.4218 | 121.3623 | 121.4035 | -121.5866 | -121.6461 | 121.8521 | 121.6507 | 60.3836 | 60.4843
525.0156 | 121.7926 | -60.8917 | 60.7956 | -0.009308 | 6.872 | 0.068678 | 0.064501 | 0.0056952 | -0.0031231 | -0.0021532 | -0.0036011 | 0.0037278 | 0.069507 | 0.057424 | -0.0040631 | 0.019762 | 0.00033961 | -0.48065 | 60.5896 | -60.8276 | 60.9055 | -60.6583 | -61.0748 | -61.1664 | -0.46692 | 60.5759 | -60.8734 | 60.7407 | -60.9055 | -60.9833 | -61.1023 | 0.064087 | -0.20599 | 0.10986 | 0.23346 | -0.27466 | -0.1831 | -0.33874 | -0.24719 | 0.018311 | -0.21973 | -0.054931 | -0.013733 | -0.21057 | -0.091552 | -0.22888 | -0.10986 | 0.16937 | 121.7331 | -0.032044 | 121.6141 | 121.4172 | 121.4493 | 121.4813 | 121.4676 | -121.6232 | -121.669 | 121.7972 | 121.6324 | 60.4111 | 60.4248
526.7656 | 121.9025 | -60.8322 | 60.7727 | 0.005951 | 6.8673 | 0.067182 | 0.063433 | 0.0014228 | -0.0054731 | -0.0010852 | 0.0025025 | 0.0015914 | 0.06737 | 0.064474 | -0.0040631 | 0.02083 | -0.00030119 | -0.45776 | 60.5713 | -60.7636 | 60.9879 | -60.5621 | -60.9787 | -61.0657 | -0.36621 | 60.5896 | -60.8276 | 60.8551 | -60.7773 | -60.8139 | -61.0062 | 0.068664 | -0.20142 | 0.21515 | 0.27008 | -0.23346 | -0.14648 | -0.30212 | -0.21515 | 0.004577 | -0.18311 | 0.082398 | 0.054931 | -0.17395 | 0.01831 | -0.17853 | 0.013733 | 0.20142 | 121.7514 | 0.050354 | 121.6827 | 121.3348 | 121.4172 | 121.4035 | 121.4218 | -121.5363 | -121.6003 | 121.8201 | 121.6873 | 60.3745 | 60.466
528.5 | 121.7972 | -60.8917 | 60.7956 | -0.0016785 | 6.8817 | 0.067182 | 0.065997 | 0.00099557 | -0.0046185 | -0.00023063 | 0.0055543 | 0.0050094 | 0.06972 | 0.061056 | -0.0049175 | 0.021471 | -0.00094199 | -0.50354 | 60.5896 | -60.8414 | 60.8826 | -60.6857 | -61.0931 | -61.1801 | -0.46234 | 60.5804 | -60.8963 | 60.759 | -60.9192 | -60.9695 | -61.0931 | 0.050354 | -0.20599 | 0.086975 | 0.20599 | -0.28839 | -0.20142 | -0.33875 | -0.25177 | -0.004577 | -0.21515 | -0.036621 | -0.027465 | -0.20142 | -0.077819 | -0.19684 | -0.073242 | 0.15564 | 121.7239 | -0.022888 | 121.6553 | 121.431 | 121.4767 | 121.4813 | 121.4722 | -121.637 | -121.6919 | 121.7743 | 121.6507 | 60.3882 | 60.4294
530.1719 | 121.7789 | -60.8826 | 60.8139 | -0.009308 | 6.8876 | 0.066114 | 0.065569 | -0.0011408 | -0.0050457 | 0.0012646 | -0.0036011 | 0.0033004 | 0.068438 | 0.051229 | -0.0061993 | 0.019335 | -0.0030784 | -0.46692 | 60.5896 | -60.8093 | 60.9146 | -60.6491 | -61.0657 | -61.1618 | -0.43488 | 60.6033 | -60.878 | 60.7681 | -60.8826 | -60.9741 | -61.084 | 0.073242 | -0.2243 | 0.10071 | 0.23346 | -0.27924 | -0.18311 | -0.35248 | -0.25635 | 0.004577 | -0.21057 | -0.045777 | 0 | -0.20142 | -0.091553 | -0.20599 | -0.09613 | 0.16022 | 121.7239 | -0.004577 | 121.6461 | 121.3989 | 121.4813 | 121.4722 | 121.4859 | -121.6232 | -121.6919 | 121.7972 | 121.6507 | 60.4156 | 60.4477
531.9062 | 121.8155 | -60.8826 | 60.791 | -0.0016785 | 6.8925 | 0.06761 | 0.066424 | 0.0027044 | -0.0048321 | -0.002367 | -0.0036011 | 0.0022324 | 0.066302 | 0.059347 | -0.0061993 | 0.019121 | -0.001583 | -0.54016 | 60.5942 | -60.8139 | 60.8826 | -60.6766 | -61.0931 | -61.1664 | -0.45776 | 60.5759 | -60.8917 | 60.7636 | -60.9009 | -60.9604 | -61.0794 | 0.068664 | -0.19684 | 0.091552 | 0.20599 | -0.28381 | -0.21057 | -0.35248 | -0.27924 | -0.009156 | -0.21515 | -0.027466 | -0.018311 | -0.19684 | -0.07782 | -0.18768 | -0.068664 | 0.13733 | 121.6965 | -0.009155 | 121.6553 | 121.4081 | 121.4676 | 121.4767 | 121.4584 | -121.6049 | -121.6827 | 121.7651 | 121.6461 | 60.3424 | 60.4248
533.5781 | 121.8933 | -60.8505 | 60.7498 | -0.0016785 | 6.893 | 0.069532 | 0.062579 | -0.00071343 | -0.00013249 | 0.00041017 | -0.00054933 | 0.0026596 | 0.066943 | 0.058065 | -0.0029949 | 0.019121 | -0.00030119 | -0.49896 | 60.5438 | -60.8276 | 60.9695 | -60.5896 | -61.0199 | -61.1069 | -0.36163 | 60.553 | -60.8826 | 60.8505 | -60.791 | -60.8551 | -61.0016 | 0.022888 | -0.20599 | 0.21973 | 0.26093 | -0.25635 | -0.16937 | -0.27924 | -0.19226 | -0.032043 | -0.19684 | 0.10071 | 0.059509 | -0.15106 | -0.004578 | -0.11902 | 0.027465 | 0.23804 | 121.7972 | 0.091552 | 121.7331 | 121.3715 | 121.4355 | 121.3943 | 121.4035 | -121.5775 | -121.6324 | 121.8201 | 121.701 | 60.3516 | 60.4889
535.2969 | 121.9208 | -60.7864 | 60.7819 | 0.005951 | 6.8979 | 0.066328 | 0.06322 | -0.0024224 | -0.0073957 | -0.0019396 | -0.0066527 | -0.0003312 | 0.065875 | 0.065755 | -0.0061993 | 0.019121 | -0.00094199 | -0.41199 | 60.5988 | -60.759 | 61.0657 | -60.4706 | -60.8688 | -60.9787 | -0.24719 | 60.5484 | -60.8231 | 60.9238 | -60.6949 | -60.7498 | -60.9329 | 0.027466 | -0.18311 | 0.28381 | 0.31586 | -0.19226 | -0.082397 | -0.21973 | -0.10986 | -0.036621 | -0.23346 | 0.14191 | 0.091553 | -0.14648 | 0.036621 | -0.10986 | 0.073242 | 0.28839 | 121.8246 | 0.12817 | 121.7468 | 121.3577 | 121.3715 | 121.3852 | 121.3348 | -121.5408 | -121.6049 | 121.8521 | 121.7102 | 60.3745 | 60.5392
537.0312 | 121.9162 | -60.7864 | 60.8047 | -0.0016785 | 6.9084 | 0.068678 | 0.06386 | 0.00056817 | -0.0059003 | -0.0053576 | -0.00054933 | 0.0011642 | 0.06737 | 0.068319 | -0.0049175 | 0.016344 | 0.00012601 | -0.43945 | 60.5988 | -60.759 | 61.0382 | -60.498 | -60.91 | -60.997 | -0.30212 | 60.5759 | -60.8002 | 60.9009 | -60.7086 | -60.7544 | -60.9329 | 0.027466 | -0.20599 | 0.23346 | 0.28839 | -0.21057 | -0.1236 | -0.23804 | -0.15106 | -0.013733 | -0.22888 | 0.09613 | 0.07782 | -0.14648 | 0.032043 | -0.13275 | 0.045776 | 0.26093 | 121.7972 | 0.091553 | 121.7011 | 121.3577 | 121.376 | 121.3852 | 121.3623 | -121.5637 | -121.6049 | 121.8246 | 121.6873 | 60.347 | 60.4843
538.7812 | 121.7834 | -60.91 | 60.8047 | -0.0016785 | 6.9116 | 0.06761 | 0.067278 | 0.00056817 | -0.0014141 | -0.0021532 | -0.00054933 | 0.004155 | 0.068011 | 0.055929 | -0.0038495 | 0.01784 | 0.0014078 | -0.49439 | 60.6125 | -60.8093 | 60.878 | -60.6812 | -61.1023 | -61.171 | -0.48065 | 60.5576 | -60.8826 | 60.7544 | -60.9283 | -60.9787 | -61.1114 | 0.10071 | -0.19226 | 0.073242 | 0.22888 | -0.26093 | -0.19226 | -0.36163 | -0.29297 | 0.027466 | -0.24719 | -0.050354 | -0.018311 | -0.20142 | -0.068665 | -0.22888 | -0.096131 | 0.12817 | 121.6873 | -0.045777 | 121.637 | 121.4218 | 121.4401 | 121.5225 | 121.4676 | -121.6141 | -121.6873 | 121.788 | 121.6644 | 60.4156 | 60.4294
540.4531 | 121.7926 | -60.8231 | 60.8643 | -0.0016785 | 6.9113 | 0.065473 | 0.064715 | -0.001568 | -0.0069683 | -0.00044443 | -0.0036011 | 0.004155 | 0.06673 | 0.055715 | -0.0079083 | 0.018267 | -0.0028646 | -0.44403 | 60.6628 | -60.759 | 60.965 | -60.5804 | -60.965 | -61.0474 | -0.37079 | 60.6766 | -60.8231 | 60.7956 | -60.8047 | -60.8688 | -61.0245 | 0.064087 | -0.20142 | 0.10071 | 0.24262 | -0.2243 | -0.14191 | -0.28839 | -0.20599 | 0 | -0.18768 | -0.068665 | 0.01831 | -0.20142 | -0.045776 | -0.20142 | -0.045776 | 0.17853 | 121.7239 | 0.01831 | 121.6187 | 121.4218 | 121.4996 | 121.4859 | 121.4996 | -121.6232 | -121.6873 | 121.788 | 121.6187 | 60.379 | 60.4523
542.2031 | 121.7926 | -60.8917 | 60.7636 | -0.009308 | 6.9131 | 0.069319 | 0.067706 | 0.0046272 | -0.0048321 | -0.00087163 | -0.00054933 | 0.003514 | 0.070788 | 0.056356 | -0.0034223 | 0.019121 | 0.00033961 | -0.53101 | 60.585 | -60.8185 | 60.8734 | -60.6857 | -61.0977 | -61.1618 | -0.46234 | 60.5804 | -60.8734 | 60.7544 | -60.8917 | -60.965 | -61.0977 | 0.073243 | -0.17853 | 0.10986 | 0.20599 | -0.27008 | -0.20599 | -0.34332 | -0.27924 | 0.018311 | -0.18311 | -0.009155 | 0 | -0.20599 | -0.073242 | -0.2243 | -0.091553 | 0.13275 | 121.6919 | -0.018311 | 121.6278 | 121.4035 | 121.4539 | 121.4767 | 121.4722 | -121.582 | -121.637 | 121.7651 | 121.6461 | 60.3607 | 60.4294
543.9375 | 121.7789 | -60.8276 | 60.8597 | -0.009308 | 6.9154 | 0.067182 | 0.064288 | 0.006977 | -0.0044049 | -0.0010852 | -0.0036011 | 0.0018052 | 0.067584 | 0.060415 | -0.0083355 | 0.019976 | -0.0039328 | -0.45319 | 60.672 | -60.7544 | 60.9558 | -60.5621 | -60.9833 | -61.0611 | -0.36621 | 60.6674 | -60.8231 | 60.8231 | -60.7956 | -60.8597 | -61.0199 | 0.073242 | -0.18768 | 0.096131 | 0.2655 | -0.23346 | -0.15564 | -0.3067 | -0.22888 | 0.004578 | -0.19226 | -0.036621 | 0.032044 | -0.19226 | -0.032043 | -0.19684 | -0.036621 | 0.19226 | 121.7102 | 0.027466 | 121.6461 | 121.4264 | 121.4905 | 121.4996 | 121.4951 | -121.6141 | -121.6827 | 121.7834 | 121.6507 | 60.3745 | 60.4614
545.6719 | 121.8796 | -60.8505 | 60.7269 | 0.036468 | 6.9156 | 0.071882 | 0.065997 | 0.0024908 | -0.0018415 | 0.00041017 | 0.011658 | 0.000737 | 0.066089 | 0.070882 | -0.0019269 | 0.021685 | -0.0013694 | -0.44861 | 60.5576 | -60.8185 | 61.0336 | -60.4797 | -60.9375 | -61.0382 | -0.2655 | 60.5484 | -60.8597 | 60.8688 | -60.7864 | -60.8276 | -60.997 | 0.032044 | -0.16937 | 0.3067 | 0.37079 | -0.18768 | -0.086975 | -0.21973 | -0.11902 | -0.009155 | -0.17853 | 0.14191 | 0.064087 | -0.14648 | 0.022888 | -0.13733 | 0.032043 | 0.33874 | 121.8521 | 0.073242 | 121.7285 | 121.376 | 121.4081 | 121.4081 | 121.3989 | -121.5454 | -121.5866 | 121.8842 | 121.7194 | 60.4019 | 60.585
547.3438 | 121.9208 | -60.7636 | 60.8002 | -0.016937 | 6.9175 | 0.06825 | 0.062579 | 0.0022772 | -0.0052595 | -0.0038622 | -0.0036011 | 0.0005234 | 0.06673 | 0.063833 | -0.0049175 | 0.021044 | -0.003292 | -0.39368 | 60.6033 | -60.7361 | 61.1023 | -60.3928 | -60.8368 | -60.9375 | -0.21057 | 60.5942 | -60.7773 | 60.9329 | -60.672 | -60.7224 | -60.9329 | 0.027466 | -0.19684 | 0.30212 | 0.37079 | -0.17395 | -0.073242 | -0.20142 | -0.10071 | -0.013733 | -0.20599 | 0.13275 | 0.091553 | -0.16937 | 0.041199 | -0.15564 | 0.054932 | 0.34332 | 121.8384 | 0.10529 | 121.7102 | 121.3394 | 121.3715 | 121.3669 | 121.3577 | -121.5363 | -121.5775 | 121.8658 | 121.6965 | 60.3699 | 60.553
549.0781 | 121.843 | -60.791 | 60.8414 | -0.0016785 | 6.919 | 0.066755 | 0.062579 | -7.2628e-05 | -0.0044049 | -0.0027942 | -0.0036011 | 0.0018052 | 0.064593 | 0.068319 | -0.0051313 | 0.016772 | -0.0037192 | -0.37537 | 60.5942 | -60.7498 | 61.0794 | -60.4568 | -60.8597 | -60.9787 | -0.25177 | 60.6125 | -60.7819 | 60.8826 | -60.7269 | -60.8047 | -60.9604 | 0.041199 | -0.24719 | 0.23804 | 0.33417 | -0.18768 | -0.068664 | -0.22888 | -0.10986 | 0.009156 | -0.22888 | 0.041198 | 0.064087 | -0.16937 | -0.013733 | -0.17853 | -0.022889 | 0.29297 | 121.8292 | 0.054931 | 121.6644 | 121.344 | 121.3943 | 121.3852 | 121.4035 | -121.5912 | -121.6232 | 121.8704 | 121.6736 | 60.4156 | 60.5392
550.8281 | 121.7651 | -60.8597 | 60.8002 | -0.009308 | 6.9218 | 0.064405 | 0.064288 | 0.0044134 | -0.0037641 | -0.0015124 | -0.0066527 | 0.0039414 | 0.068225 | 0.053152 | -0.0027813 | 0.018694 | 0.0011942 | -0.48523 | 60.6033 | -60.7681 | 60.9146 | -60.6628 | -61.0794 | -61.1618 | -0.46692 | 60.6125 | -60.8643 | 60.7544 | -60.9146 | -60.9879 | -61.0931 | 0.091553 | -0.19684 | 0.11444 | 0.19684 | -0.30212 | -0.21973 | -0.39368 | -0.31128 | -0.004578 | -0.18768 | -0.045776 | -0.054932 | -0.23346 | -0.12817 | -0.22888 | -0.1236 | 0.10529 | 121.6827 | -0.050354 | 121.6187 | 121.3715 | 121.4767 | 121.463 | 121.4722 | -121.5683 | -121.6644 | 121.7743 | 121.6141 | 60.3745 | 60.3928
552.5 | 121.7926 | -60.8047 | 60.8414 | 0.005951 | 6.9235 | 0.065473 | 0.062792 | 0.00035457 | -0.0056867 | -0.001726 | -0.00054933 | 0.002446 | 0.06737 | 0.052083 | -0.0074811 | 0.020403 | -0.003292 | -0.46234 | 60.64 | -60.7452 | 60.9604 | -60.5759 | -60.9695 | -61.0565 | -0.37537 | 60.6583 | -60.8002 | 60.8139 | -60.8047 | -60.8688 | -61.0153 | 0.05951 | -0.20142 | 0.11902 | 0.22888 | -0.25177 | -0.16479 | -0.31128 | -0.2243 | 0.004578 | -0.18311 | -0.027466 | 0 | -0.21057 | -0.064086 | -0.21515 | -0.068664 | 0.16937 | 121.7056 | -0.004578 | 121.6141 | 121.3852 | 121.4584 | 121.4447 | 121.463 | -121.5866 | -121.6415 | 121.7651 | 121.6187 | 60.3424 | 60.4294
554.2344 | 121.7926 | -60.8826 | 60.7773 | -0.009308 | 6.924 | 0.067396 | 0.065356 | 0.0054816 | -0.0048321 | -0.0015124 | 0.0055543 | 0.0047958 | 0.066516 | 0.062551 | -0.0038495 | 0.019762 | -0.0028646 | -0.51727 | 60.5896 | -60.7956 | 60.8871 | -60.6903 | -61.0886 | -61.1664 | -0.45319 | 60.5667 | -60.8734 | 60.759 | -60.9009 | -60.9558 | -61.0703 | 0.086975 | -0.18768 | 0.10986 | 0.19226 | -0.28381 | -0.20599 | -0.37079 | -0.29297 | 0.009155 | -0.21057 | -0.018311 | -0.018311 | -0.18768 | -0.073243 | -0.19684 | -0.082398 | 0.10528 | 121.6827 | -0.027466 | 121.6324 | 121.3852 | 121.4401 | 121.4722 | 121.4493 | -121.5729 | -121.6507 | 121.7697 | 121.6415 | 60.3653 | 60.4294
555.9844 | 121.8796 | -60.8597 | 60.7269 | -0.009308 | 6.9252 | 0.065473 | 0.064715 | -7.2628e-05 | -0.0039777 | -0.0032214 | -0.00054933 | 0.0011642 | 0.067584 | 0.064687 | -0.0034223 | 0.018694 | -0.0045736 | -0.51727 | 60.5896 | -60.8139 | 60.91 | -60.6262 | -61.0657 | -61.1252 | -0.40283 | 60.5347 | -60.878 | 60.8231 | -60.8093 | -60.8871 | -61.0382 | 0.045776 | -0.13733 | 0.18311 | 0.23346 | -0.2655 | -0.20599 | -0.31128 | -0.25177 | -0.018311 | -0.19226 | 0.09613 | 0.050354 | -0.17853 | -0.027466 | -0.16022 | -0.009155 | 0.18768 | 121.7239 | 0.068665 | 121.7011 | 121.4035 | 121.4127 | 121.4493 | 121.3943 | -121.5408 | -121.6049 | 121.7697 | 121.6827 | 60.3424 | 60.4568
557.7188 | 121.7834 | -60.8643 | 60.7864 | -0.0016785 | 6.9299 | 0.067182 | 0.065569 | -0.00071343 | -0.0044049 | -0.00065803 | -0.0036011 | 0.0026596 | 0.066302 | 0.058065 | -0.0059857 | 0.022112 | 0.0014078 | -0.43945 | 60.6079 | -60.8002 | 60.9467 | -60.5667 | -61.0062 | -61.1023 | -0.37079 | 60.585 | -60.8551 | 60.7727 | -60.8597 | -60.9329 | -61.0657 | 0.064087 | -0.17853 | 0.16022 | 0.29755 | -0.23804 | -0.14191 | -0.30212 | -0.20599 | 0.009155 | -0.20142 | -0.013733 | 0.004578 | -0.20142 | -0.068664 | -0.21057 | -0.077819 | 0.23346 | 121.7468 | -0.004577 | 121.6278 | 121.4081 | 121.4401 | 121.4722 | 121.4493 | -121.5866 | -121.6415 | 121.8109 | 121.637 | 60.4248 | 60.4935
559.375 | 121.9162 | -60.7727 | 60.8093 | -0.009308 | 6.9282 | 0.06761 | 0.063647 | -0.00049983 | -0.0067547 | 0.0014784 | -0.00054933 | -0.0005448 | 0.066302 | 0.063405 | -0.0049175 | 0.022112 | -0.0013694 | -0.39368 | 60.6079 | -60.7315 | 61.0931 | -60.4248 | -60.8597 | -60.9604 | -0.2243 | 60.5988 | -60.7819 | 60.9283 | -60.6583 | -60.7315 | -60.9055 | 0.041199 | -0.20142 | 0.28381 | 0.3479 | -0.18768 | -0.086975 | -0.22888 | -0.12817 | -0.009155 | -0.21057 | 0.11902 | 0.11444 | -0.13275 | 0.041199 | -0.1236 | 0.050354 | 0.3067 | 121.8246 | 0.1236 | 121.7102 | 121.3394 | 121.3806 | 121.3806 | 121.3715 | -121.5408 | -121.5912 | 121.8658 | 121.7011 | 60.379 | 60.5484
561.1094 | 121.8933 | -60.791 | 60.7956 | 0.005951 | 6.9331 | 0.069532 | 0.06322 | 0.0050544 | -0.0037641 | -0.0012988 | -0.00054933 | 0.000737 | 0.06673 | 0.061483 | -0.0044903 | 0.02083 | 0.0014078 | -0.47607 | 60.5713 | -60.7727 | 60.9787 | -60.5347 | -60.965 | -61.0336 | -0.35248 | 60.5667 | -60.8414 | 60.8688 | -60.7452 | -60.7956 | -60.9695 | 0.018311 | -0.2243 | 0.18311 | 0.25635 | -0.24261 | -0.17395 | -0.26093 | -0.19226 | -0.050354 | -0.22888 | 0.073242 | 0.045777 | -0.17853 | -0.004577 | -0.12817 | 0.045777 | 0.23804 | 121.7514 | 0.096131 | 121.7102 | 121.344 | 121.4081 | 121.3623 | 121.3577 | -121.5683 | -121.637 | 121.7697 | 121.6599 | 60.3149 | 60.4385
562.8281 | 121.7789 | -60.791 | 60.878 | -0.0016785 | 6.9306 | 0.066969 | 0.06386 | 0.0016364 | -0.0054731 | 0.0023328 | -0.0036011 | 0.0030868 | 0.06673 | 0.061483 | -0.0074811 | 0.018267 | -0.0011558 | -0.41657 | 60.6308 | -60.7498 | 60.997 | -60.5576 | -60.9604 | -61.0519 | -0.36621 | 60.6537 | -60.8276 | 60.8139 | -60.7956 | -60.8643 | -61.0153 | 0.041199 | -0.24719 | 0.11902 | 0.23346 | -0.26093 | -0.16937 | -0.30212 | -0.21057 | -0.036621 | -0.2243 | -0.064087 | -0.004577 | -0.2243 | -0.073242 | -0.18768 | -0.036621 | 0.19226 | 121.7468 | 0.032044 | 121.6415 | 121.3806 | 121.4813 | 121.4218 | 121.4447 | -121.6278 | -121.7056 | 121.788 | 121.6049 | 60.3745 | 60.4248
564.5 | 121.8842 | -60.7681 | 60.7864 | 0.02121 | 6.9316 | 0.06825 | 0.063647 | -0.0034906 | -0.0073957 | -0.0015124 | -0.0066527 | 0.0026596 | 0.06673 | 0.055074 | -0.0044903 | 0.019976 | -0.003292 | -0.46692 | 60.5392 | -60.7452 | 60.9924 | -60.5301 | -60.9467 | -61.0291 | -0.33875 | 60.585 | -60.8276 | 60.8871 | -60.7452 | -60.7681 | -60.9512 | 0.022888 | -0.24719 | 0.20599 | 0.23804 | -0.26093 | -0.17853 | -0.28381 | -0.20142 | -0.05951 | -0.20142 | 0.10071 | 0.022888 | -0.18311 | 0 | -0.1236 | 0.05951 | 0.21515 | 121.7377 | 0.082398 | 121.7148 | 121.2845 | 121.4127 | 121.3074 | 121.3531 | -121.5317 | -121.6141 | 121.7606 | 121.6553 | 60.3012 | 60.4294
566.25 | 121.7606 | -60.8917 | 60.791 | -0.0016785 | 6.9346 | 0.070814 | 0.06621 | -0.0028498 | -0.0048321 | -0.00065803 | -0.0066527 | 0.0039414 | 0.064807 | 0.058706 | -0.0055585 | 0.020189 | -0.002651 | -0.50354 | 60.5896 | -60.791 | 60.8871 | -60.6766 | -61.0931 | -61.1755 | -0.48981 | 60.5896 | -60.8963 | 60.7361 | -60.9055 | -60.9604 | -61.0748 | 0.10071 | -0.20142 | 0.09613 | 0.21515 | -0.28381 | -0.20142 | -0.38452 | -0.30212 | -0.004577 | -0.20142 | -0.054932 | -0.013733 | -0.1831 | -0.068664 | -0.17853 | -0.064087 | 0.11444 | 121.6782 | -0.009156 | 121.6324 | 121.3806 | 121.4859 | 121.4813 | 121.4813 | -121.582 | -121.6873 | 121.7789 | 121.6278 | 60.3882 | 60.4019
567.9219 | 121.788 | -60.8093 | 60.8734 | -0.0016785 | 6.9351 | 0.066114 | 0.06386 | -0.0045586 | -0.0078229 | -0.001726 | -0.00054933 | 0.0015914 | 0.067798 | 0.054006 | -0.0083355 | 0.018694 | -0.0028646 | -0.42572 | 60.6537 | -60.7361 | 60.9695 | -60.5576 | -60.9558 | -61.0474 | -0.36163 | 60.6445 | -60.8002 | 60.8047 | -60.8002 | -60.8551 | -61.0107 | 0.073242 | -0.21973 | 0.09613 | 0.25177 | -0.23804 | -0.14648 | -0.31128 | -0.21973 | 0.009155 | -0.22888 | -0.068664 | 0.009155 | -0.20142 | -0.045777 | -0.21057 | -0.054932 | 0.17853 | 121.7056 | 0 | 121.6049 | 121.3898 | 121.4447 | 121.463 | 121.4539 | -121.6095 | -121.6736 | 121.7789 | 121.6141 | 60.3836 | 60.4477
569.6562 | 121.8109 | -60.8459 | 60.8185 | 0.01358 | 6.9359 | 0.06761 | 0.066851 | 0.00185 | -0.0061139 | -0.0015124 | 0.0055543 | 0.0018052 | 0.067584 | 0.058492 | -0.0044903 | 0.017626 | -0.006069 | -0.40741 | 60.6216 | -60.7636 | 61.0016 | -60.5347 | -60.965 | -61.0519 | -0.34332 | 60.6079 | -60.8414 | 60.8231 | -60.8047 | -60.878 | -61.0291 | 0.082397 | -0.19684 | 0.18311 | 0.31128 | -0.20599 | -0.11902 | -0.28839 | -0.20142 | 0.004577 | -0.21057 | 0.004578 | 0.041198 | -0.18311 | -0.032044 | -0.18768 | -0.036621 | 0.22888 | 121.7651 | 0.036621 | 121.6644 | 121.3852 | 121.4493 | 121.4676 | 121.4539 | -121.582 | -121.6599 | 121.8475 | 121.669 | 60.4385 | 60.5026
571.4219 | 121.9208 | -60.7544 | 60.8002 | -0.009308 | 6.9363 | 0.067396 | 0.061724 | -7.2628e-05 | -0.0073957 | 0.00041017 | -0.0036011 | 0.0011642 | 0.070361 | 0.061483 | -0.0049175 | 0.020189 | -0.0017966 | -0.38452 | 60.5804 | -60.7361 | 61.0611 | -60.4248 | -60.8643 | -60.9604 | -0.23804 | 60.5896 | -60.8185 | 60.9283 | -60.6674 | -60.7224 | -60.9055 | 0.018311 | -0.21973 | 0.26093 | 0.32959 | -0.20599 | -0.10986 | -0.2243 | -0.12817 | -0.064086 | -0.21057 | 0.12817 | 0.086976 | -0.15106 | 0.032044 | -0.086976 | 0.09613 | 0.31128 | 121.7972 | 0.15106 | 121.7468 | 121.3165 | 121.4081 | 121.3348 | 121.344 | -121.5363 | -121.6187 | 121.8155 | 121.6827 | 60.3699 | 60.5164
573.0938 | 121.8338 | -60.8231 | 60.8185 | 0.028839 | 6.9406 | 0.066969 | 0.064501 | -0.001568 | -0.0033369 | -0.0010852 | 0.0086061 | 0.0026596 | 0.068011 | 0.053792 | -0.0047039 | 0.018053 | -0.00436 | -0.37994 | 60.64 | -60.7636 | 61.0107 | -60.5209 | -60.9512 | -61.0336 | -0.32044 | 60.5988 | -60.8322 | 60.8368 | -60.791 | -60.8551 | -61.0016 | 0.059509 | -0.17853 | 0.19226 | 0.30212 | -0.21057 | -0.12817 | -0.27008 | -0.18768 | -0.009155 | -0.21973 | 0.018311 | 0.032043 | -0.17853 | -0.032044 | -0.16937 | -0.022889 | 0.24262 | 121.7743 | 0.041198 | 121.669 | 121.4035 | 121.431 | 121.463 | 121.4218 | -121.582 | -121.6507 | 121.8338 | 121.6599 | 60.4431 | 60.5026
574.8281 | 121.8842 | -60.8093 | 60.7864 | 0.01358 | 6.9404 | 0.066969 | 0.065569 | -0.001568 | -0.0065411 | -0.003435 | 0.0025025 | 0.0018052 | 0.066089 | 0.055715 | -0.0053449 | 0.019976 | -0.0028646 | -0.44861 | 60.6125 | -60.7407 | 60.9879 | -60.553 | -60.965 | -61.0519 | -0.37537 | 60.5438 | -60.8276 | 60.8505 | -60.7773 | -60.8047 | -60.9787 | 0.068664 | -0.17395 | 0.20142 | 0.25635 | -0.24262 | -0.15564 | -0.31128 | -0.2243 | -0.018311 | -0.24261 | 0.064087 | 0.032043 | -0.16937 | 0.004577 | -0.15106 | 0.022888 | 0.18768 | 121.7285 | 0.050354 | 121.6782 | 121.3531 | 121.3715 | 121.4218 | 121.3531 | -121.5271 | -121.6141 | 121.7972 | 121.6599 | 60.3607 | 60.434
576.5 | 121.7743 | -60.8139 | 60.8459 | -0.0016785 | 6.9398 | 0.067396 | 0.06621 | 0.0041998 | -0.0048321 | 0.001051 | 0.014709 | 0.002446 | 0.068011 | 0.063619 | -0.0070539 | 0.018267 | -0.003292 | -0.4303 | 60.6445 | -60.759 | 60.9695 | -60.5713 | -60.965 | -61.0245 | -0.37994 | 60.6766 | -60.8139 | 60.8093 | -60.8139 | -60.8551 | -60.997 | 0.054932 | -0.20142 | 0.1236 | 0.24262 | -0.21057 | -0.15106 | -0.2655 | -0.20599 | 0 | -0.16937 | -0.036621 | 0 | -0.1831 | -0.041199 | -0.1831 | -0.041199 | 0.18768 | 121.7285 | 0 | 121.6232 | 121.4035 | 121.4905 | 121.4584 | 121.4905 | -121.6049 | -121.6599 | 121.7834 | 121.6232 | 60.3836 | 60.434
578.2344 | 121.8796 | -60.8139 | 60.8002 | 0.005951 | 6.9402 | 0.069746 | 0.063433 | 0.00056817 | -0.0054731 | -0.0012988 | -0.00054933 | 0.0011642 | 0.063525 | 0.061696 | -0.0032087 | 0.021044 | -0.0020102 | -0.46692 | 60.553 | -60.7864 | 60.9924 | -60.5392 | -60.9467 | -61.0336 | -0.33417 | 60.5667 | -60.8551 | 60.8643 | -60.7361 | -60.7956 | -60.9604 | 0.027466 | -0.24719 | 0.19226 | 0.27466 | -0.21973 | -0.13275 | -0.24719 | -0.16022 | -0.041199 | -0.23346 | 0.064087 | 0.07782 | -0.14648 | 0.018311 | -0.10529 | 0.05951 | 0.24719 | 121.7789 | 0.11902 | 121.7194 | 121.3394 | 121.4218 | 121.3669 | 121.3806 | -121.5866 | -121.6553 | 121.8063 | 121.6782 | 60.347 | 60.4797
579.9062 | 121.875 | -60.8322 | 60.759 | 0.028839 | 6.9423 | 0.069746 | 0.064929 | -0.0017816 | -0.0031231 | 0.0021192 | 0.011658 | 0.0011642 | 0.070575 | 0.061056 | -0.0029949 | 0.020617 | -0.0020102 | -0.45319 | 60.553 | -60.8185 | 61.0107 | -60.4889 | -60.9375 | -61.0382 | -0.30212 | 60.5392 | -60.8551 | 60.8505 | -60.791 | -60.8322 | -60.9879 | 0.013733 | -0.20599 | 0.25177 | 0.34332 | -0.20599 | -0.10529 | -0.21973 | -0.11902 | -0.022889 | -0.21973 | 0.091553 | 0.041198 | -0.15564 | 0 | -0.13275 | 0.022889 | 0.32959 | 121.8292 | 0.064087 | 121.7056 | 121.3715 | 121.3943 | 121.3852 | 121.3715 | -121.5775 | -121.6141 | 121.843 | 121.6827 | 60.379 | 60.5301
581.6406 | 121.8201 | -60.8276 | 60.7819 | 0.02121 | 6.9455 | 0.065473 | 0.068133 | 0.0020636 | -0.0056867 | -0.0010852 | 0.0055543 | 0.0039414 | 0.065875 | 0.058919 | -0.0055585 | 0.019121 | -0.0037192 | -0.40741 | 60.6262 | -60.7864 | 60.9879 | -60.5347 | -60.965 | -61.0519 | -0.31586 | 60.5896 | -60.8322 | 60.8322 | -60.7773 | -60.8505 | -60.9879 | 0.041199 | -0.15564 | 0.20599 | 0.29297 | -0.2243 | -0.13733 | -0.2655 | -0.17853 | -0.004577 | -0.19226 | 0.050354 | 0.050354 | -0.16022 | -0.022888 | -0.15564 | -0.018311 | 0.25177 | 121.7743 | 0.054931 | 121.6644 | 121.4127 | 121.4218 | 121.4539 | 121.4172 | -121.5683 | -121.6141 | 121.8155 | 121.6599 | 60.4202 | 60.5118
583.375 | 121.8658 | -60.8368 | 60.7498 | 0.028839 | 6.9451 | 0.068891 | 0.066424 | -0.00028623 | -0.0029095 | -0.0012988 | 0.0086061 | 0.0020188 | 0.067157 | 0.065542 | -0.0034223 | 0.019976 | -0.0024374 | -0.44861 | 60.553 | -60.7956 | 60.9924 | -60.4843 | -60.9512 | -61.0245 | -0.29297 | 60.5164 | -60.8597 | 60.8276 | -60.7864 | -60.8368 | -61.0107 | 0.041199 | -0.19684 | 0.24262 | 0.35248 | -0.18768 | -0.11444 | -0.22888 | -0.15564 | -0.022888 | -0.23346 | 0.07782 | 0.050354 | -0.17395 | 0 | -0.15106 | 0.022888 | 0.31128 | 121.788 | 0.073242 | 121.6873 | 121.3486 | 121.376 | 121.3898 | 121.3531 | -121.5454 | -121.6095 | 121.8292 | 121.6644 | 60.3882 | 60.5438
585.0938 | 121.9254 | -60.791 | 60.7727 | -0.009308 | 6.9436 | 0.065901 | 0.064715 | -0.0039178 | -0.0048321 | -0.0027942 | -0.0036011 | 0.0022324 | 0.066943 | 0.060415 | -0.0047039 | 0.020617 | -0.0028646 | -0.3891 | 60.5667 | -60.7498 | 61.0382 | -60.466 | -60.8734 | -60.9695 | -0.21515 | 60.5438 | -60.8093 | 60.9192 | -60.672 | -60.7178 | -60.9146 | 0.041199 | -0.20599 | 0.2655 | 0.32501 | -0.17853 | -0.082397 | -0.21973 | -0.1236 | -0.01831 | -0.22888 | 0.14648 | 0.11902 | -0.1236 | 0.073243 | -0.10529 | 0.091553 | 0.28381 | 121.788 | 0.13733 | 121.7285 | 121.3165 | 121.3531 | 121.3577 | 121.3348 | -121.5225 | -121.582 | 121.8292 | 121.7102 | 60.4019 | 60.5759
586.8438 | 121.8155 | -60.8643 | 60.7636 | 0.02121 | 6.9477 | 0.068678 | 0.067065 | -0.0028498 | -0.0050457 | -0.0040758 | 0.0055543 | 0.004155 | 0.066516 | 0.055288 | -0.0064129 | 0.018267 | -0.0017966 | -0.40283 | 60.5942 | -60.8231 | 60.965 | -60.5576 | -60.9924 | -61.0703 | -0.32044 | 60.5667 | -60.8597 | 60.7956 | -60.8231 | -60.8734 | -61.0428 | 0.041199 | -0.16937 | 0.20142 | 0.3067 | -0.20599 | -0.12817 | -0.24719 | -0.16937 | 0.004578 | -0.19684 | 0.032043 | 0.041199 | -0.17853 | -0.009155 | -0.18311 | -0.013733 | 0.2655 | 121.788 | 0.036621 | 121.6553 | 121.4172 | 121.4264 | 121.4584 | 121.431 | -121.5866 | -121.6232 | 121.8292 | 121.6599 | 60.4614 | 60.5438
588.5156 | 121.8338 | -60.8734 | 60.7681 | 0.005951 | 6.9489 | 0.067396 | 0.067065 | 0.0020636 | -0.0050457 | -1.7026e-05 | 0.0086061 | 0.0043686 | 0.068011 | 0.063833 | -0.0055585 | 0.021044 | -0.0024374 | -0.39368 | 60.5621 | -60.8276 | 60.9375 | -60.585 | -61.0107 | -61.1023 | -0.32959 | 60.5667 | -60.8871 | 60.7864 | -60.8276 | -60.878 | -61.0291 | 0.045776 | -0.20599 | 0.16937 | 0.28839 | -0.22888 | -0.13733 | -0.27466 | -0.1831 | -0.013733 | -0.20142 | 0.018311 | 0.045776 | -0.15564 | -0.004578 | -0.14191 | 0.009155 | 0.24262 | 121.7651 | 0.059509 | 121.6736 | 121.3898 | 121.4539 | 121.4355 | 121.4401 | -121.5958 | -121.6553 | 121.8109 | 121.6599 | 60.4797 | 60.5438
590.25 | 121.7651 | -60.9558 | 60.704 | -0.009308 | 6.9481 | 0.068891 | 0.06621 | -0.001568 | -0.0031231 | -0.00044443 | -0.00054933 | 0.0033004 | 0.065661 | 0.060201 | -0.0072675 | 0.019549 | 0.0033304 | -0.49896 | 60.5301 | -60.8551 | 60.7864 | -60.7544 | -61.1618 | -61.235 | -0.48065 | 60.5072 | -60.997 | 60.6628 | -60.9741 | -61.0245 | -61.1481 | 0.10071 | -0.17395 | 0.082397 | 0.20142 | -0.27923 | -0.20599 | -0.37994 | -0.3067 | -0.041198 | -0.19684 | -0.041199 | -0.01831 | -0.19226 | -0.068664 | -0.15106 | -0.027466 | 0.10071 | 121.6415 | 0.022888 | 121.6599 | 121.3852 | 121.5042 | 121.4859 | 121.463 | -121.5591 | -121.701 | 121.7422 | 121.6187 | 60.4568 | 60.4752
592 | 121.7743 | -60.9833 | 60.6903 | -0.009308 | 6.9472 | 0.06526 | 0.067278 | 0.0059088 | -0.0050457 | -0.001726 | -0.0036011 | 0.000737 | 0.068225 | 0.059987 | -0.0061993 | 0.019976 | -0.001583 | -0.49439 | 60.4843 | -60.9055 | 60.7773 | -60.7956 | -61.2076 | -61.2991 | -0.48065 | 60.4706 | -60.9741 | 60.6262 | -61.0016 | -61.0611 | -61.1801 | 0.077819 | -0.20599 | 0.086975 | 0.18768 | -0.31586 | -0.22431 | -0.39368 | -0.30212 | 0.009155 | -0.21973 | -0.064087 | -0.018311 | -0.19684 | -0.07782 | -0.20599 | -0.086975 | 0.10986 | 121.6827 | -0.027466 | 121.6003 | 121.3898 | 121.4447 | 121.4676 | 121.4539 | -121.5958 | -121.6644 | 121.7606 | 121.6095 | 60.4889 | 60.5026
593.75 | 121.7697 | -60.9879 | 60.64 | -0.0016785 | 6.9485 | 0.067823 | 0.063647 | 0.00014097 | -0.0059003 | -0.0040758 | -0.0036011 | 0.0050094 | 0.066943 | 0.052083 | -0.0047039 | 0.019549 | 0.00012601 | -0.48981 | 60.466 | -60.9467 | 60.7269 | -60.8185 | -61.235 | -61.3083 | -0.48523 | 60.4156 | -61.0382 | 60.5896 | -61.0474 | -61.1069 | -61.2122 | 0.041199 | -0.17395 | 0.086975 | 0.16937 | -0.32044 | -0.24719 | -0.36163 | -0.28839 | -0.050354 | -0.22431 | -0.050354 | -0.059509 | -0.2243 | -0.11902 | -0.17395 | -0.068665 | 0.12817 | 121.6736 | -0.009155 | 121.6278 | 121.4127 | 121.4539 | 121.4539 | 121.4035 | -121.5866 | -121.6782 | 121.7148 | 121.5775 | 60.498 | 60.5026
595.4844 | 121.8475 | -61.0107 | 60.5804 | 0.02121 | 6.9483 | 0.066755 | 0.062579 | 0.0012092 | -0.0059003 | -0.001726 | 0.0055543 | 0.0030868 | 0.06737 | 0.059347 | -0.0055585 | 0.020617 | -0.0011558 | -0.49896 | 60.3699 | -60.9741 | 60.7864 | -60.7407 | -61.1572 | -61.2442 | -0.38452 | 60.347 | -61.0565 | 60.64 | -60.9833 | -61.0245 | -61.1847 | 0.036621 | -0.21057 | 0.20599 | 0.27008 | -0.23346 | -0.14648 | -0.27008 | -0.18311 | -0.045777 | -0.23346 | 0.05951 | 0.027466 | -0.17395 | -0.013733 | -0.12817 | 0.032044 | 0.23346 | 121.7606 | 0.073243 | 121.6965 | 121.344 | 121.4035 | 121.3806 | 121.3577 | -121.5546 | -121.637 | 121.7972 | 121.6507 | 60.5118 | 60.6262
597.1719 | 121.8613 | -61.0931 | 60.5072 | 0.028839 | 6.946 | 0.069532 | 0.065997 | 0.0016364 | -0.0041913 | -0.00023063 | 0.0025025 | 0.0033004 | 0.066943 | 0.062978 | -0.0044903 | 0.02083 | -0.00051479 | -0.46234 | 60.2921 | -61.0657 | 60.7269 | -60.7636 | -61.2076 | -61.2991 | -0.32959 | 60.2829 | -61.1023 | 60.5667 | -61.0474 | -61.0794 | -61.2442 | 0.027466 | -0.21515 | 0.21973 | 0.32959 | -0.20599 | -0.11444 | -0.23346 | -0.14191 | -0.009155 | -0.2243 | 0.059509 | 0.045777 | -0.15106 | 0.013733 | -0.14191 | 0.022888 | 0.30212 | 121.7926 | 0.054932 | 121.669 | 121.3577 | 121.3852 | 121.3852 | 121.376 | -121.5729 | -121.6095 | 121.8201 | 121.6599 | 60.6308 | 60.7635
598.9062 | 121.8201 | -61.1069 | 60.4889 | -0.0016785 | 6.9494 | 0.067182 | 0.063006 | -0.004345 | -0.0059003 | -0.00065803 | -0.0036011 | 0.0028732 | 0.06438 | 0.061696 | -0.0068403 | 0.018908 | -8.7586e-05 | -0.39368 | 60.2417 | -61.0886 | 60.704 | -60.7864 | -61.2122 | -61.322 | -0.31128 | 60.2737 | -61.1206 | 60.5118 | -61.0931 | -61.1298 | -61.2946 | 0.018311 | -0.24719 | 0.21515 | 0.32044 | -0.21515 | -0.10529 | -0.23346 | -0.1236 | -0.013732 | -0.21515 | 0.022888 | 0.013733 | -0.18768 | -0.022888 | -0.17395 | -0.009156 | 0.30212 | 121.7926 | 0.027465 | 121.6324 | 121.3303 | 121.3943 | 121.3486 | 121.3806 | -121.5775 | -121.6095 | 121.8109 | 121.6187 | 60.7132 | 60.7956
600.5781 | 121.8384 | -61.2534 | 60.3241 | 0.02121 | 6.9507 | 0.069746 | 0.065997 | 0.0016364 | -0.0035505 | -1.7026e-05 | 0.0086061 | 0.0028732 | 0.066302 | 0.062765 | -0.0044903 | 0.020189 | 0.0014078 | -0.48065 | 60.1364 | -61.2167 | 60.5301 | -60.9787 | -61.4136 | -61.4822 | -0.37994 | 60.1135 | -61.3129 | 60.379 | -61.2396 | -61.29 | -61.4273 | 0.036621 | -0.18768 | 0.20599 | 0.27466 | -0.22888 | -0.16022 | -0.2655 | -0.19684 | -0.059509 | -0.21057 | 0.054931 | 0.013733 | -0.17395 | -0.036621 | -0.11444 | 0.022888 | 0.23804 | 121.7468 | 0.073242 | 121.6919 | 121.3531 | 121.4264 | 121.3898 | 121.3669 | -121.5408 | -121.637 | 121.7834 | 121.6324 | 60.7727 | 60.8734
602.3281 | 121.9345 | -61.3495 | 60.228 | 0.005951 | 6.95 | 0.065046 | 0.06386 | -0.00028623 | -0.0059003 | -0.0021532 | -0.00054933 | 0.0009506 | 0.065448 | 0.058278 | -0.0051313 | 0.021258 | -8.7586e-05 | -0.4303 | 59.9808 | -61.3358 | 60.4843 | -61.0062 | -61.4365 | -61.5509 | -0.24719 | 59.9945 | -61.3586 | 60.3607 | -61.2305 | -61.2854 | -61.4777 | 0.013733 | -0.24719 | 0.25635 | 0.34332 | -0.20142 | -0.086975 | -0.21515 | -0.10071 | -0.009156 | -0.23346 | 0.13275 | 0.11902 | -0.12817 | 0.064087 | -0.11902 | 0.073243 | 0.32959 | 121.8201 | 0.12817 | 121.7194 | 121.3165 | 121.3531 | 121.3303 | 121.344 | -121.5637 | -121.5866 | 121.8338 | 121.7102 | 60.9192 | 61.1023
604.0625 | 121.7514 | -61.6104 | 60.0357 | -0.0016785 | 6.9532 | 0.068464 | 0.065356 | -0.00028623 | -0.0026959 | -0.0040758 | -0.0036011 | 0.0050094 | 0.068652 | 0.065328 | -0.0049175 | 0.019762 | -0.0024374 | -0.52185 | 59.8755 | -61.5417 | 60.1364 | -61.4227 | -61.8301 | -61.9125 | -0.5127 | 59.8343 | -61.6241 | 59.9991 | -61.6379 | -61.6974 | -61.7935 | 0.068665 | -0.16022 | 0.10071 | 0.18768 | -0.30212 | -0.21973 | -0.37079 | -0.28839 | -0.013733 | -0.20142 | -0.036622 | -0.027465 | -0.1831 | -0.086975 | -0.16937 | -0.073242 | 0.11902 | 121.6782 | -0.013732 | 121.6232 | 121.4172 | 121.4584 | 121.4859 | 121.4447 | -121.5775 | -121.6599 | 121.7468 | 121.6095 | 61.0886 | 61.0977
605.7969 | 121.9025 | -61.6882 | 59.8755 | 0.005951 | 6.9485 | 0.06761 | 0.064074 | 0.0022772 | -0.0067547 | -0.0012988 | -0.0036011 | 0.0013778 | 0.068011 | 0.068319 | -0.0059857 | 0.023394 | -0.0028646 | -0.43945 | 59.6603 | -61.647 | 60.1639 | -61.3174 | -61.7569 | -61.8622 | -0.29297 | 59.6832 | -61.6928 | 59.9945 | -61.5784 | -61.6287 | -61.8256 | 0.041198 | -0.21515 | 0.28839 | 0.37079 | -0.17395 | -0.068665 | -0.21515 | -0.10986 | -0.004578 | -0.19226 | 0.11902 | 0.10986 | -0.13733 | 0.059509 | -0.13275 | 0.064087 | 0.32959 | 121.8109 | 0.11444 | 121.6873 | 121.3074 | 121.376 | 121.3486 | 121.3715 | -121.5225 | -121.5683 | 121.8521 | 121.6827 | 61.2488 | 61.3953
607.4688 | 121.8475 | -61.9263 | 59.6329 | 0.02121 | 6.9498 | 0.06825 | 0.06322 | -0.001568 | -0.0059003 | -0.00087163 | -0.00054933 | 0.0030868 | 0.066943 | 0.058919 | -0.0044903 | 0.020403 | -0.003292 | -0.53101 | 59.4452 | -61.8805 | 59.8755 | -61.647 | -62.0728 | -62.1506 | -0.43945 | 59.4589 | -61.9492 | 59.7061 | -61.9034 | -61.9583 | -62.1094 | 0.045777 | -0.18768 | 0.24261 | 0.27924 | -0.2243 | -0.14648 | -0.27008 | -0.19226 | -0.022888 | -0.17395 | 0.073242 | 0.022889 | -0.1831 | -0.032043 | -0.16022 | -0.009155 | 0.23346 | 121.756 | 0.045777 | 121.6553 | 121.3257 | 121.4081 | 121.3715 | 121.3852 | -121.5134 | -121.582 | 121.8018 | 121.6324 | 61.3953 | 61.4868
609.2031 | 121.9116 | -62.1918 | 59.3903 | 0.005951 | 6.9511 | 0.066969 | 0.065356 | -0.0075494 | -0.0050457 | -0.003435 | -0.0036011 | 0.0009506 | 0.065234 | 0.064687 | -0.0044903 | 0.020189 | -0.0013694 | -0.46692 | 59.1843 | -62.1231 | 59.6558 | -61.8439 | -62.265 | -62.3657 | -0.32501 | 59.198 | -62.2101 | 59.5184 | -62.0544 | -62.1002 | -62.3016 | 0.068664 | -0.20599 | 0.2655 | 0.3479 | -0.17395 | -0.073243 | -0.24262 | -0.14191 | -0.018311 | -0.19226 | 0.12817 | 0.13733 | -0.10986 | 0.091552 | -0.091553 | 0.10986 | 0.27924 | 121.7789 | 0.15564 | 121.7285 | 121.3074 | 121.4081 | 121.376 | 121.3898 | -121.5134 | -121.6003 | 121.8475 | 121.7102 | 61.7249 | 61.8668
610.9375 | 121.9025 | -62.4664 | 59.1064 | 0.005951 | 6.9519 | 0.067396 | 0.064929 | -0.003277 | -0.0041913 | -0.0047168 | -0.0066527 | 0.0011642 | 0.06438 | 0.065969 | -0.0042767 | 0.021258 | -0.0037192 | -0.52185 | 58.9279 | -62.384 | 59.3903 | -62.114 | -62.5809 | -62.6633 | -0.41199 | 58.8959 | -62.4481 | 59.2529 | -62.3474 | -62.4069 | -62.5854 | 0.082398 | -0.17853 | 0.28381 | 0.35248 | -0.19684 | -0.11444 | -0.27924 | -0.19684 | 0.018311 | -0.21057 | 0.14648 | 0.11902 | -0.11902 | 0.05951 | -0.13733 | 0.041199 | 0.27008 | 121.7743 | 0.10071 | 121.7011 | 121.3119 | 121.344 | 121.3943 | 121.3623 | -121.4905 | -121.5546 | 121.8567 | 121.7194 | 61.9446 | 62.0544
612.6719 | 121.875 | -62.4115 | 59.1522 | -0.0016785 | 6.9545 | 0.068891 | 0.065356 | 0.0012092 | -0.0035505 | 0.0014784 | 0.011658 | 0.002446 | 0.066089 | 0.061696 | -0.0042767 | 0.020403 | 0.0016214 | -0.59052 | 58.9691 | -62.3749 | 59.4452 | -62.0636 | -62.5351 | -62.6083 | -0.45776 | 58.9737 | -62.4756 | 59.2667 | -62.3383 | -62.3886 | -62.5442 | 0.036621 | -0.18311 | 0.29297 | 0.3479 | -0.19684 | -0.1236 | -0.23346 | -0.16022 | -0.064087 | -0.17853 | 0.11444 | 0.073242 | -0.13275 | 0.022888 | -0.068664 | 0.086975 | 0.31128 | 121.8201 | 0.13733 | 121.7422 | 121.344 | 121.4493 | 121.3806 | 121.3852 | -121.5271 | -121.6278 | 121.8567 | 121.6782 | 61.821 | 61.9537
614.4375 | 121.7697 | -48.0515 | 73.6908 | 0.044098 | 6.9549 | 0.066755 | 0.064929 | -0.0039178 | -0.0046185 | 0.003401 | 0.0086061 | 0.0043686 | 0.070147 | 0.056783 | -0.0096173 | 0.019549 | -0.0039328 | 0.073242 | 73.4619 | -47.9599 | 73.8098 | -47.8317 | -48.175 | -48.2483 | 0.022888 | 73.494 | -48.0103 | 73.6038 | -48.0286 | -48.0927 | -48.1842 | 0.091553 | -0.22888 | 0.11902 | 0.21973 | -0.19684 | -0.1236 | -0.28839 | -0.21515 | 0.041199 | -0.19684 | -0.086975 | 0.022889 | -0.13275 | -0.041198 | -0.17395 | -0.082397 | 0.12817 | 121.7697 | -0.01831 | 121.6141 | 121.4218 | 121.5042 | 121.5134 | 121.5454 | -121.6507 | -121.7011 | 121.8613 | 121.6553 | 48.1247 | 48.0743
616.1562 | 121.8567 | -49.4568 | 72.1619 | 0.01358 | 6.9511 | 0.068464 | 0.064501 | -0.0034906 | -0.0050457 | -0.00087163 | -0.00054933 | 0.0020188 | 0.066943 | 0.061696 | -0.0061993 | 0.019335 | -0.0024374 | -0.050354 | 71.8826 | -49.4431 | 72.3084 | -49.2874 | -49.6353 | -49.704 | 0.07782 | 71.933 | -49.4431 | 72.1985 | -49.4202 | -49.4431 | -49.5941 | 0.013733 | -0.27924 | 0.14648 | 0.16937 | -0.24719 | -0.17853 | -0.26093 | -0.19226 | 0.013733 | -0.22888 | 0.036621 | 0.036621 | -0.13733 | 0.013733 | -0.15106 | 0 | 0.15564 | 121.7514 | 0.022888 | 121.6415 | 121.3257 | 121.376 | 121.3394 | 121.3898 | -121.6049 | -121.6049 | 121.7651 | 121.6553 | 49.4064 | 49.5346
617.8281 | 121.8475 | -60.2463 | 61.29 | 0.02121 | 6.9547 | 0.067396 | 0.06322 | 0.00078177 | -0.0065411 | -0.0021532 | 0.0086061 | 0.002446 | 0.06972 | 0.059347 | -0.0036359 | 0.020617 | -0.0037192 | -0.41199 | 61.0565 | -60.2921 | 61.5234 | -59.9762 | -60.3973 | -60.466 | -0.24719 | 61.1801 | -60.2417 | 61.3403 | -60.2188 | -60.2829 | -60.4431 | -0.045776 | -0.23346 | 0.23346 | 0.27008 | -0.21973 | -0.15106 | -0.17395 | -0.10529 | 0.004578 | -0.10986 | 0.050354 | 0.027466 | -0.19684 | -0.036621 | -0.20142 | -0.041199 | 0.31586 | 121.8155 | 0.022888 | 121.582 | 121.3486 | 121.4218 | 121.3028 | 121.4264 | -121.582 | -121.5317 | 121.7697 | 121.5866 | 59.8343 | 59.9991
619.5 | 121.7834 | -67.9138 | 53.6774 | -0.016937 | 6.9547 | 0.068464 | 0.064501 | 0.00056817 | -0.0054731 | -0.0027942 | -0.00054933 | 0.003514 | 0.06673 | 0.052297 | -0.0064129 | 0.019335 | -0.001583 | -0.80109 | 53.5446 | -67.868 | 53.8101 | -67.6575 | -68.1152 | -68.1839 | -0.80566 | 53.5034 | -67.9642 | 53.6362 | -67.9413 | -68.0145 | -68.1519 | 0.045776 | -0.13275 | 0.13275 | 0.25635 | -0.27008 | -0.20142 | -0.31586 | -0.24719 | -0.050354 | -0.17395 | -0.041199 | -0.027466 | -0.23804 | -0.10071 | -0.18768 | -0.050354 | 0.21057 | 121.6782 | 0.022888 | 121.6003 | 121.4127 | 121.4676 | 121.4584 | 121.4172 | -121.5454 | -121.6415 | 121.7239 | 121.55 | 67.1127 | 67.1082
621.2188 | 121.8979 | -71.7087 | 49.8688 | -0.0016785 | 6.9517 | 0.065046 | 0.06621 | -0.0013544 | -0.0063275 | -0.0030078 | -0.0036011 | 0.0009506 | 0.068866 | 0.064687 | -0.0053449 | 0.01848 | -0.0041464 | -1.3596 | 49.4843 | -71.8185 | 49.8734 | -71.5485 | -72.0108 | -72.0932 | -1.2451 | 49.4659 | -71.8964 | 50.029 | -71.4615 | -71.553 | -71.7911 | -0.10986 | -0.38452 | 0.004578 | 0.16022 | -0.38452 | -0.30212 | -0.27466 | -0.19226 | -0.18768 | -0.40283 | 0.16022 | 0.24719 | -0.082398 | 0.15564 | 0.10528 | 0.34332 | 0.27008 | 121.6919 | 0.43487 | 121.9254 | 121.3028 | 121.3623 | 121.1929 | 121.1746 | -121.6873 | -121.7651 | 121.582 | 121.7377 | 70.3491 | 70.4636
622.9531 | 121.9528 | -114.4318 | 7.0999 | -0.009308 | 6.9547 | 0.065687 | 0.067278 | -0.0047724 | -0.0063275 | 0.00041017 | -0.00054933 | 0.0011642 | 0.068866 | 0.062765 | -0.0027813 | 0.022539 | -0.0022238 | -8.5464 | 6.8619 | -114.4363 | 7.2739 | -113.7314 | -114.4547 | -114.5782 | -9.1736 | 6.9672 | -114.6057 | 7.196 | -114.0747 | -114.2349 | -114.5416 | -0.004577 | -0.23804 | 0.17395 | 0.70038 | -0.14648 | -0.022888 | -0.14191 | -0.018311 | -0.17395 | -0.13275 | 0.09613 | 0.35706 | -0.10986 | 0.19684 | 0.064087 | 0.37079 | 0.70496 | 121.7102 | 0.53101 | 121.8018 | 121.2982 | 121.5729 | 121.2936 | 121.3989 | -121.5363 | -121.7056 | 121.7056 | 121.6278 | 105.8853 | 105.2582
624.7031 | 121.8018 | -115.7181 | 5.928 | 0.005951 | 6.9541 | 0.066969 | 0.067065 | 0.005268 | -0.0061139 | -0.001726 | -0.0066527 | 0.0043686 | 0.067157 | 0.060201 | -0.0044903 | 0.018267 | -0.0030784 | -9.6039 | 5.8456 | -115.5899 | 5.9052 | -115.1093 | -115.7822 | -115.9103 | -10.2768 | 5.8182 | -115.8096 | 5.8731 | -115.3976 | -115.5533 | -115.8371 | 0.12817 | -0.082398 | -0.022889 | 0.60883 | -0.19226 | -0.064087 | -0.32043 | -0.19226 | -0.091552 | -0.10986 | -0.054932 | 0.32044 | -0.11902 | 0.16479 | -0.027466 | 0.25635 | 0.48065 | 121.4951 | 0.41199 | 121.6827 | 121.4355 | 121.6278 | 121.5637 | 121.5363 | -121.5179 | -121.7377 | 121.6232 | 121.5912 | 106.1142 | 105.4413
626.3906 | 121.8842 | -116.4001 | 5.191 | -0.009308 | 6.9541 | 0.068037 | 0.066424 | 0.00014097 | -0.0067547 | -0.003435 | -0.0036011 | 0.0028732 | 0.066943 | 0.063192 | -0.0038495 | 0.021258 | -0.002651 | -9.9838 | 4.9988 | -116.3681 | 5.2139 | -115.7455 | -116.4688 | -116.5833 | -10.5743 | 5.0629 | -116.5329 | 5.2322 | -116.0202 | -116.1896 | -116.4825 | 0.032043 | -0.19226 | 0.022888 | 0.6546 | -0.18311 | -0.068665 | -0.21515 | -0.10071 | -0.13275 | -0.12817 | 0.041199 | 0.37994 | -0.082398 | 0.21057 | 0.050354 | 0.34332 | 0.62256 | 121.582 | 0.5127 | 121.7651 | 121.3669 | 121.5958 | 121.3989 | 121.463 | -121.5591 | -121.7239 | 121.6141 | 121.6324 | 106.4163 | 105.8258
628.0781 | 121.843 | -116.4505 | 5.127 | -0.0016785 | 6.9554 | 0.067396 | 0.068347 | 0.00035457 | -0.0054731 | -0.00023063 | -0.0036011 | 0.0013778 | 0.06438 | 0.06191 | -0.0029949 | 0.02083 | -0.00436 | -10.3134 | 4.9393 | -116.3956 | 5.2185 | -115.7318 | -116.4368 | -116.5741 | -10.8444 | 5.0171 | -116.5192 | 5.2002 | -116.0156 | -116.1758 | -116.4734 | 0.054931 | -0.18768 | 0.091553 | 0.71869 | -0.1236 | 0.013732 | -0.17853 | -0.041199 | -0.068665 | -0.10986 | 0.073242 | 0.43488 | -0.022889 | 0.27466 | 0.045776 | 0.34332 | 0.66376 | 121.6141 | 0.50354 | 121.7194 | 121.3348 | 121.5363 | 121.3898 | 121.4676 | -121.5225 | -121.6461 | 121.669 | 121.6507 | 106.1371 | 105.6061
629.7812 | 121.8292 | -118.3914 | 3.1082 | -0.0016785 | 6.9534 | 0.06526 | 0.065569 | -0.0011408 | -0.0056867 | -0.002367 | -0.00054933 | 0.0028732 | 0.065875 | 0.062765 | -0.0066265 | 0.020403 | -0.003292 | -10.8444 | 2.9022 | -118.3411 | 3.2318 | -117.6178 | -118.3456 | -118.4692 | -11.3754 | 2.98 | -118.5104 | 3.1952 | -117.9474 | -118.1076 | -118.4555 | 0.050354 | -0.20599 | 0.1236 | 0.77362 | -0.07782 | 0.045776 | -0.12817 | -0.004578 | -0.11902 | -0.12817 | 0.086975 | 0.44403 | -0.064087 | 0.28381 | 0.054932 | 0.40283 | 0.72327 | 121.5729 | 0.56305 | 121.7056 | 121.2433 | 121.4905 | 121.2936 | 121.3715 | -121.4493 | -121.6187 | 121.6232 | 121.5866 | 107.547 | 107.016
631.4688 | 121.7377 | -118.9178 | 2.6047 | 0.01358 | 6.9545 | 0.068678 | 0.06322 | 0.00185 | -0.0052595 | -0.00087163 | 0.0055543 | 0.0015914 | 0.06737 | 0.060201 | -0.0049175 | 0.021471 | 0.00033961 | -11.1877 | 2.3895 | -118.8446 | 2.6413 | -118.19 | -118.895 | -119.0323 | -11.7828 | 2.4857 | -119.0094 | 2.5955 | -118.5242 | -118.6798 | -118.9957 | 0.073243 | -0.21515 | 0.036621 | 0.72784 | -0.11444 | 0.022889 | -0.18768 | -0.050354 | -0.091552 | -0.11902 | -0.009155 | 0.39368 | -0.07782 | 0.23804 | 0.013732 | 0.32959 | 0.6546 | 121.4859 | 0.48523 | 121.6049 | 121.2341 | 121.4951 | 121.3074 | 121.4035 | -121.4493 | -121.6141 | 121.5591 | 121.5134 | 107.7301 | 107.135
633.2031 | 121.7056 | -118.9636 | 2.5772 | -0.009308 | 6.9566 | 0.066328 | 0.064929 | -0.00071343 | -0.0050457 | 0.00083737 | -0.0036011 | 9.6204e-05 | 0.066302 | 0.059987 | -0.0079083 | 0.019335 | -0.00051479 | -11.3205 | 2.3438 | -118.8766 | 2.6596 | -118.1671 | -118.8721 | -119.0277 | -11.8515 | 2.4307 | -119.0186 | 2.5452 | -118.5333 | -118.689 | -119.014 | 0.086975 | -0.23346 | 0.082398 | 0.79651 | -0.064087 | 0.091553 | -0.15106 | 0.004578 | -0.054932 | -0.14648 | -0.032043 | 0.4303 | -0.050354 | 0.27466 | 0.004578 | 0.32959 | 0.70953 | 121.5363 | 0.48523 | 121.5637 | 121.2204 | 121.4493 | 121.3074 | 121.3943 | -121.4539 | -121.5958 | 121.6232 | 121.5088 | 107.6431 | 107.1121
634.9219 | 121.6461 | -119.1788 | 2.3666 | 0.005951 | 6.9551 | 0.067823 | 0.06621 | -0.0022088 | -0.0056867 | 0.001051 | -0.0036011 | 0.0026596 | 0.067798 | 0.063192 | -0.0036359 | 0.019976 | 0.00055321 | -11.5906 | 2.1469 | -119.1055 | 2.2934 | -118.5287 | -119.2337 | -119.3573 | -12.1902 | 2.243 | -119.2841 | 2.2751 | -118.84 | -119.0094 | -119.2795 | 0.073242 | -0.21973 | -0.073242 | 0.65002 | -0.17853 | -0.054932 | -0.25177 | -0.12817 | -0.10529 | -0.1236 | -0.091553 | 0.33874 | -0.10071 | 0.16937 | 0.004578 | 0.27466 | 0.57678 | 121.3989 | 0.44403 | 121.5591 | 121.2524 | 121.5271 | 121.3257 | 121.4218 | -121.4722 | -121.6507 | 121.4722 | 121.4539 | 107.5882 | 106.9885
636.6719 | 121.6278 | -118.959 | 2.5497 | -0.009308 | 6.9577 | 0.067396 | 0.06322 | -0.0013544 | -0.0063275 | 0.00062377 | -0.0036011 | 0.0011642 | 0.066516 | 0.062124 | -0.0076947 | 0.018053 | -0.0020102 | -11.8011 | 2.3438 | -118.8309 | 2.298 | -118.5287 | -119.1879 | -119.0506 | -12.4969 | 2.3666 | -119.2245 | 2.2293 | -118.3777 | -118.5837 | -118.9682 | 0.12817 | -0.20599 | -0.25177 | 0.4303 | -0.091553 | -0.22888 | -0.21973 | -0.35706 | -0.2655 | -0.18311 | -0.32043 | 0.58136 | -0.009156 | 0.37537 | 0.25635 | 0.64087 | 0.30212 | 121.1288 | 0.84686 | 121.4539 | 121.1746 | 121.5912 | 121.3028 | 121.3257 | -121.3806 | -121.7743 | 121.257 | 121.1884 | 107.1579 | 106.4621
638.4219 | 121.7239 | -120.0577 | 1.4236 | -0.009308 | 6.9562 | 0.068464 | 0.064715 | -0.0011408 | -0.0065411 | -1.7026e-05 | -0.00054933 | -0.0001174 | 0.065661 | 0.064901 | -0.0025677 | 0.020617 | -0.0056418 | -11.9476 | 1.2085 | -119.9432 | 1.5106 | -119.2566 | -120.0165 | -120.1355 | -12.5061 | 1.2817 | -120.1355 | 1.4786 | -119.5816 | -119.7556 | -120.0714 | 0.11444 | -0.21515 | 0.086975 | 0.80109 | -0.07782 | 0.041199 | -0.19226 | -0.073242 | -0.07782 | -0.14191 | 0.054932 | 0.47607 | -0.013733 | 0.30212 | 0.064087 | 0.37994 | 0.68664 | 121.4539 | 0.55389 | 121.6141 | 121.1517 | 121.4172 | 121.2662 | 121.3394 | -121.3669 | -121.5591 | 121.5683 | 121.5363 | 108.11 | 107.5516
640.1094 | 121.431 | -121.2616 | 0.15564 | -0.009308 | 6.9551 | 0.068037 | 0.064715 | -0.003277 | -0.0080365 | -0.00065803 | -0.00054933 | 0.0003098 | 0.065448 | 0.050588 | -0.0094037 | 0.017626 | -0.001583 | -12.2543 | -0.086975 | -121.1884 | 0.082397 | -120.5429 | -121.2524 | -121.3806 | -12.8632 | 0.027466 | -121.3211 | 0.045776 | -120.8633 | -121.0464 | -121.3531 | 0.073243 | -0.24261 | -0.073243 | 0.71869 | -0.11902 | 0.009156 | -0.19226 | -0.064087 | -0.059509 | -0.12817 | -0.10986 | 0.39825 | -0.091552 | 0.21515 | -0.032043 | 0.27466 | 0.64545 | 121.2708 | 0.45776 | 121.3669 | 121.1014 | 121.3486 | 121.1746 | 121.2891 | -121.344 | -121.4767 | 121.344 | 121.3074 | 109.0073 | 108.3984
641.8438 | 121.6141 | -121.4447 | 0.13275 | -0.009308 | 6.9564 | 0.069746 | 0.065783 | -0.00092703 | -0.0054731 | -0.0012988 | -0.0036011 | 0.0020188 | 0.068438 | 0.060415 | -0.0066265 | 0.019335 | -0.0045736 | -12.5107 | -0.10071 | -121.3486 | 0.050354 | -120.7626 | -121.4905 | -121.6003 | -13.0783 | 0 | -121.5225 | 0.027466 | -121.0739 | -121.2616 | -121.5088 | 0.09613 | -0.23346 | -0.082397 | 0.68207 | -0.15564 | -0.045777 | -0.25177 | -0.14191 | -0.07782 | -0.13275 | -0.10529 | 0.37079 | -0.064087 | 0.18311 | 0.013733 | 0.26093 | 0.58594 | 121.3989 | 0.44861 | 121.55 | 121.2479 | 121.5225 | 121.344 | 121.4447 | -121.4813 | -121.6553 | 121.4951 | 121.4722 | 108.934 | 108.3664
643.5156 | 121.7697 | -121.4218 | 0.09613 | -0.0016785 | 6.9568 | 0.066114 | 0.064501 | -0.0041314 | -0.0071821 | 0.00019657 | -0.00054933 | 0.0005234 | 0.066516 | 0.064046 | -0.0049175 | 0.020617 | -0.00030119 | -12.5793 | -0.14191 | -121.3348 | 0.20142 | -120.5978 | -121.344 | -121.4813 | -13.0188 | -0.032043 | -121.5179 | 0.16022 | -120.9229 | -121.106 | -121.4539 | 0.086975 | -0.23804 | 0.10529 | 0.82398 | -0.059509 | 0.07782 | -0.14648 | -0.009155 | -0.09613 | -0.12817 | 0.064087 | 0.49896 | -0.032043 | 0.31586 | 0.064087 | 0.41199 | 0.737 | 121.5363 | 0.59509 | 121.6782 | 121.1929 | 121.4859 | 121.2799 | 121.3898 | -121.431 | -121.6141 | 121.6232 | 121.582 | 108.8425 | 108.403
645.25 | 121.6644 | -121.4493 | 0.14648 | -0.0016785 | 6.9566 | 0.06825 | 0.066424 | 0.0012092 | -0.0061139 | -1.7026e-05 | -0.0066527 | 0.003514 | 0.065448 | 0.05187 | -0.0038495 | 0.019976 | -0.0013694 | -12.7167 | -0.082397 | -121.3943 | 0.073242 | -120.7901 | -121.5134 | -121.6415 | -13.3072 | 0.018311 | -121.5683 | 0.018311 | -121.1334 | -121.312 | -121.5775 | 0.054932 | -0.22888 | -0.073242 | 0.65918 | -0.19226 | -0.064087 | -0.24719 | -0.11902 | -0.11902 | -0.12817 | -0.12817 | 0.31586 | -0.12817 | 0.13733 | -0.009156 | 0.25635 | 0.60425 | 121.4676 | 0.43488 | 121.5866 | 121.312 | 121.5866 | 121.3669 | 121.4676 | -121.5408 | -121.7148 | 121.5225 | 121.4676 | 108.7326 | 108.1421
646.9219 | 121.7468 | -121.4767 | 0.14648 | 0.01358 | 6.9583 | 0.068037 | 0.066851 | -7.2628e-05 | -0.0048321 | -0.00023063 | -0.00054933 | 0.0026596 | 0.067157 | 0.056142 | -0.0059857 | 0.021685 | -0.00051479 | -12.7441 | -0.086975 | -121.4584 | 0.14191 | -120.726 | -121.463 | -121.5866 | -13.2889 | 0.009155 | -121.5912 | 0.082397 | -121.0464 | -121.2158 | -121.55 | 0.018311 | -0.23346 | -0.004577 | 0.75073 | -0.10986 | 0.013733 | -0.12817 | -0.004578 | -0.11444 | -0.13733 | -0.064087 | 0.4303 | -0.073242 | 0.26093 | 0.041199 | 0.37537 | 0.73242 | 121.6003 | 0.54474 | 121.6736 | 121.3715 | 121.6003 | 121.3898 | 121.4859 | -121.6049 | -121.7377 | 121.6187 | 121.5591 | 108.7326 | 108.1879
648.6562 | 121.7422 | -121.4951 | 0.13275 | 0.02121 | 6.9573 | 0.068678 | 0.064288 | -7.2628e-05 | -0.0052595 | -0.0010852 | 0.014709 | 0.003514 | 0.068225 | 0.062978 | -0.0049175 | 0.021044 | -0.0028646 | -12.8723 | -0.059509 | -121.4859 | 0.09613 | -120.7626 | -121.463 | -121.6003 | -13.4125 | 0.041199 | -121.6187 | 0.068665 | -121.0876 | -121.2616 | -121.55 | 0.009155 | -0.19226 | -0.036621 | 0.73242 | -0.10529 | 0.032043 | -0.11444 | 0.022888 | -0.1236 | -0.091552 | -0.064086 | 0.40741 | -0.054932 | 0.23346 | 0.068664 | 0.35706 | 0.72327 | 121.582 | 0.53101 | 121.6873 | 121.4264 | 121.6599 | 121.4355 | 121.5363 | -121.6187 | -121.7514 | 121.5912 | 121.5637 | 108.6227 | 108.0826
650.3906 | 121.7972 | -121.4813 | 0.10529 | -0.009308 | 6.9564 | 0.068678 | 0.064074 | 0.00078177 | -0.0048321 | -0.0025806 | 0.0025025 | 0.0013778 | 0.068011 | 0.063833 | -0.0012861 | 0.022112 | -0.00436 | -13.0096 | -0.09613 | -121.4264 | 0.11444 | -120.7855 | -121.5179 | -121.6507 | -13.5086 | -0.013733 | -121.6049 | 0.11902 | -121.0327 | -121.2433 | -121.5225 | 0.054931 | -0.20142 | 0.009155 | 0.6958 | -0.16937 | -0.036621 | -0.2243 | -0.091552 | -0.1236 | -0.11902 | 0.013733 | 0.44861 | -0.041199 | 0.23804 | 0.082397 | 0.36163 | 0.64087 | 121.5408 | 0.5722 | 121.7239 | 121.3303 | 121.5912 | 121.3852 | 121.4676 | -121.5317 | -121.7102 | 121.5958 | 121.6003 | 108.4717 | 107.9727
652.1406 | 121.8063 | -121.4767 | 0.10986 | 0.005951 | 6.956 | 0.068037 | 0.064074 | 0.0016364 | -0.0037641 | -0.0025806 | -0.0036011 | 0.0015914 | 0.068011 | 0.06191 | -0.0044903 | 0.019762 | -0.006069 | -13.0875 | -0.13275 | -121.4401 | 0.12817 | -120.7489 | -121.463 | -121.6049 | -13.5544 | -0.027466 | -121.5866 | 0.12817 | -121.0464 | -121.2158 | -121.5408 | 0.036621 | -0.24261 | 0.018311 | 0.72785 | -0.12817 | 0.013733 | -0.16479 | -0.022888 | -0.10986 | -0.13733 | 0.018311 | 0.4303 | -0.064087 | 0.26093 | 0.045776 | 0.37079 | 0.69122 | 121.5683 | 0.54016 | 121.7148 | 121.3074 | 121.5591 | 121.344 | 121.4493 | -121.55 | -121.6965 | 121.6049 | 121.6049 | 108.3893 | 107.9224
653.875 | 121.8063 | -121.4859 | 0.10986 | -0.009308 | 6.9571 | 0.06761 | 0.06386 | 0.0039862 | -0.0041913 | -0.001726 | -0.00054933 | 0.0033004 | 0.065661 | 0.058492 | -0.0040631 | 0.020403 | 0.00012601 | -13.1332 | -0.10529 | -121.4767 | 0.091553 | -120.8084 | -121.5454 | -121.6736 | -13.6322 | 0 | -121.5958 | 0.11444 | -121.0785 | -121.2387 | -121.5454 | 0.009155 | -0.21515 | -0.01831 | 0.67749 | -0.18768 | -0.059509 | -0.19684 | -0.068664 | -0.10986 | -0.10986 | 0.004578 | 0.40741 | -0.059509 | 0.24719 | 0.050354 | 0.35706 | 0.66833 | 121.5683 | 0.51727 | 121.7102 | 121.3715 | 121.5958 | 121.3806 | 121.4859 | -121.5866 | -121.7056 | 121.5775 | 121.6003 | 108.3527 | 107.8537
655.5469 | 121.7422 | -121.5454 | 0.13733 | -0.0016785 | 6.9594 | 0.06825 | 0.065997 | -0.0011408 | -0.0052595 | 0.001051 | 0.017761 | 0.000737 | 0.068011 | 0.060628 | -0.0070539 | 0.01848 | -0.0039328 | -13.147 | -0.086975 | -121.5088 | 0.073242 | -120.8176 | -121.5179 | -121.6599 | -13.7054 | 0.041199 | -121.6599 | 0.018311 | -121.1517 | -121.3257 | -121.6278 | 0.036621 | -0.2243 | -0.064087 | 0.72784 | -0.11444 | 0.027466 | -0.15106 | -0.009155 | -0.11444 | -0.09613 | -0.11902 | 0.39368 | -0.082398 | 0.21973 | 0.032043 | 0.33417 | 0.69122 | 121.582 | 0.50812 | 121.6782 | 121.4218 | 121.7011 | 121.4584 | 121.5866 | -121.6461 | -121.7972 | 121.6187 | 121.5637 | 108.3984 | 107.84
657.2812 | 121.8155 | -121.5042 | 0.10071 | 0.005951 | 6.9568 | 0.06761 | 0.064929 | 0.0016364 | -0.0039777 | -0.0010852 | 0.011658 | 0.0033004 | 0.069079 | 0.056783 | -0.0055585 | 0.020403 | -0.0028646 | -13.2065 | -0.1236 | -121.463 | 0.19684 | -120.6848 | -121.4401 | -121.5775 | -13.6414 | -0.022888 | -121.6095 | 0.13733 | -121.0739 | -121.2341 | -121.55 | 0.041198 | -0.2243 | 0.09613 | 0.8194 | -0.073243 | 0.064086 | -0.11444 | 0.022888 | -0.10529 | -0.1236 | 0.036621 | 0.4303 | -0.045777 | 0.27008 | 0.059509 | 0.37537 | 0.7782 | 121.6599 | 0.53558 | 121.7468 | 121.3394 | 121.5866 | 121.3806 | 121.4813 | -121.5637 | -121.7102 | 121.701 | 121.6415 | 108.2977 | 107.8629
659.0156 | 121.7697 | -121.5408 | 0.1236 | 0.044098 | 6.9603 | 0.065473 | 0.064929 | 0.0037726 | -0.0044049 | 0.001692 | 0.0055543 | 0.0028732 | 0.068225 | 0.061696 | -0.0079083 | 0.018053 | -0.005001 | -13.2477 | -0.082397 | -121.5271 | 0.086975 | -120.813 | -121.5042 | -121.6461 | -13.7604 | 0.036621 | -121.6324 | 0.045776 | -121.1151 | -121.2936 | -121.5775 | 0.013733 | -0.20599 | -0.036621 | 0.72785 | -0.10528 | 0.036622 | -0.11902 | 0.022889 | -0.091552 | -0.086975 | -0.07782 | 0.42572 | -0.036621 | 0.24719 | 0.054931 | 0.33875 | 0.71411 | 121.6141 | 0.51727 | 121.6782 | 121.4447 | 121.669 | 121.4584 | 121.5775 | -121.6507 | -121.756 | 121.6278 | 121.5866 | 108.2932 | 107.7805
660.75 | 121.7651 | -121.5454 | 0.11902 | -0.009308 | 6.9558 | 0.066969 | 0.06322 | 0.0014228 | -0.0046185 | -0.0025806 | -0.0036011 | 0.0005234 | 0.067798 | 0.05956 | -0.0057721 | 0.018908 | -0.00094199 | -13.2843 | -0.13275 | -121.4722 | 0.11902 | -120.7672 | -121.4813 | -121.6324 | -13.8107 | 0 | -121.6278 | 0.050354 | -121.1151 | -121.312 | -121.6278 | 0.073242 | -0.25177 | 0 | 0.7782 | -0.086975 | 0.064087 | -0.16022 | -0.009155 | -0.082398 | -0.11902 | -0.068665 | 0.4303 | -0.082398 | 0.23346 | 0 | 0.31586 | 0.70496 | 121.5912 | 0.5127 | 121.6782 | 121.3394 | 121.6278 | 121.4127 | 121.5454 | -121.5912 | -121.7468 | 121.6644 | 121.5958 | 108.2611 | 107.7347
662.4531 | 121.7102 | -121.5317 | 0.13733 | -0.016937 | 6.959 | 0.06825 | 0.066424 | -0.00071343 | -0.0046185 | -0.0012988 | 0.0055543 | 0.0033004 | 0.06737 | 0.062124 | -0.0038495 | 0.019976 | -0.0020102 | -13.3713 | -0.082397 | -121.4722 | 0.022888 | -120.9 | -121.6003 | -121.7285 | -13.9801 | 0.018311 | -121.6507 | 0.027466 | -121.225 | -121.3898 | -121.6415 | 0.059509 | -0.21973 | -0.11444 | 0.63171 | -0.19684 | -0.068665 | -0.25635 | -0.12817 | -0.11902 | -0.11902 | -0.10986 | 0.3067 | -0.10986 | 0.14191 | 0.009155 | 0.26093 | 0.5722 | 121.4951 | 0.42572 | 121.6782 | 121.3898 | 121.669 | 121.4493 | 121.55 | -121.6095 | -121.788 | 121.5546 | 121.5591 | 108.1604 | 107.5516
664.1719 | 121.8704 | -121.5225 | 0.09613 | -0.0016785 | 6.9558 | 0.067396 | 0.062792 | -0.00049983 | -0.0033369 | -0.0015124 | -0.00054933 | 0.0005234 | 0.066943 | 0.060628 | -0.0057721 | 0.020189 | -0.00030119 | -13.4079 | -0.14191 | -121.4676 | 0.17853 | -120.7031 | -121.431 | -121.5683 | -13.8245 | -0.027466 | -121.6049 | 0.15106 | -121.0281 | -121.1929 | -121.5271 | 0.054932 | -0.23804 | 0.082398 | 0.8194 | -0.045776 | 0.091553 | -0.10071 | 0.036621 | -0.082397 | -0.1236 | 0.054932 | 0.49438 | -0.004578 | 0.32959 | 0.077819 | 0.41199 | 0.76447 | 121.6461 | 0.57678 | 121.756 | 121.3257 | 121.5775 | 121.3806 | 121.4951 | -121.5637 | -121.701 | 121.701 | 121.6736 | 108.1146 | 107.6981
665.9062 | 121.7514 | -121.5546 | 0.13733 | 0.005951 | 6.959 | 0.064192 | 0.064929 | -0.00092703 | -0.0063275 | -0.00065803 | 0.014709 | 0.003514 | 0.065661 | 0.064046 | -0.0096173 | 0.018908 | -8.7586e-05 | -13.4674 | -0.10529 | -121.4767 | 0.032043 | -120.8633 | -121.5546 | -121.669 | -13.9938 | 0.041199 | -121.6736 | 0.018311 | -121.1792 | -121.3303 | -121.6324 | 0.077819 | -0.24262 | -0.10529 | 0.69122 | -0.11444 | 0 | -0.19226 | -0.077819 | -0.11902 | -0.09613 | -0.11902 | 0.37537 | -0.07782 | 0.2243 | 0.041199 | 0.34332 | 0.6134 | 121.5088 | 0.49439 | 121.6919 | 121.3715 | 121.7148 | 121.4493 | 121.5958 | -121.6141 | -121.8109 | 121.5866 | 121.5729 | 108.0872 | 107.5607
667.5938 | 121.7789 | -121.5683 | 0.11444 | 0.028839 | 6.9594 | 0.06825 | 0.065783 | 0.0037726 | -0.0065411 | 0.00062377 | 0.011658 | 0.0030868 | 0.067157 | 0.062978 | -0.0076947 | 0.02083 | -0.006069 | -13.4491 | -0.059509 | -121.5225 | 0.091553 | -120.8176 | -121.4996 | -121.6553 | -13.9984 | 0 | -121.6599 | 0.064087 | -121.1197 | -121.2891 | -121.6095 | 0.045776 | -0.17395 | -0.022888 | 0.75073 | -0.086975 | 0.068664 | -0.13275 | 0.022888 | -0.091553 | -0.11444 | -0.050354 | 0.44861 | -0.041199 | 0.27924 | 0.050354 | 0.37079 | 0.70496 | 121.6141 | 0.54016 | 121.7239 | 121.463 | 121.6599 | 121.5088 | 121.5683 | -121.637 | -121.7743 | 121.6599 | 121.6324 | 108.1192 | 107.5699
669.3281 | 121.7514 | -121.5775 | 0.11902 | -0.0016785 | 6.9601 | 0.067823 | 0.065142 | -0.00092703 | -0.0037641 | -0.00023063 | -0.0036011 | 0.0020188 | 0.06737 | 0.058706 | -0.0047039 | 0.020403 | 0.00055321 | -13.5223 | -0.09613 | -121.4905 | 0.10071 | -120.8267 | -121.5591 | -121.6873 | -14.0945 | -0.013733 | -121.637 | 0.045776 | -121.1929 | -121.3577 | -121.6049 | 0.086975 | -0.21515 | -0.018311 | 0.75073 | -0.10986 | 0.018311 | -0.19684 | -0.068664 | -0.059509 | -0.13275 | -0.073243 | 0.38452 | -0.027465 | 0.21973 | 0.032044 | 0.27924 | 0.66376 | 121.5912 | 0.44403 | 121.6827 | 121.3943 | 121.6232 | 121.4813 | 121.5637 | -121.6095 | -121.756 | 121.6782 | 121.6232 | 108.0551 | 107.4829
671.0625 | 121.8155 | -121.5271 | 0.1236 | -0.016937 | 6.9575 | 0.067396 | 0.061297 | 0.00099557 | -0.0052595 | -0.0032214 | -0.0036011 | 9.6204e-05 | 0.069293 | 0.070669 | -0.0068403 | 0.021044 | -0.001583 | -13.5498 | -0.16022 | -121.4584 | 0.1831 | -120.7169 | -121.4401 | -121.6003 | -14.0396 | -0.004578 | -121.6232 | 0.10071 | -121.0785 | -121.2341 | -121.5683 | 0.068665 | -0.28381 | 0.059509 | 0.81024 | -0.073242 | 0.086975 | -0.14191 | 0.01831 | -0.09613 | -0.12817 | -0.022888 | 0.44861 | -0.041198 | 0.29297 | 0.054932 | 0.3891 | 0.74158 | 121.6415 | 0.54474 | 121.7239 | 121.2982 | 121.6187 | 121.3669 | 121.5225 | -121.582 | -121.7468 | 121.7102 | 121.6278 | 107.9773 | 107.4875
672.7969 | 121.8613 | -121.5363 | 0.11444 | 0.005951 | 6.9562 | 0.066541 | 0.063647 | 0.0014228 | -0.0078229 | -0.00065803 | 0.0025025 | -0.000972 | 0.068225 | 0.058919 | -0.0049175 | 0.020189 | -0.00030119 | -13.6688 | -0.13275 | -121.4722 | 0.11902 | -120.7993 | -121.5134 | -121.6507 | -14.1632 | -0.027466 | -121.6324 | 0.091553 | -121.0876 | -121.257 | -121.582 | 0.064087 | -0.24719 | 0.004578 | 0.737 | -0.11444 | 0.022888 | -0.17853 | -0.041199 | -0.09613 | -0.14191 | -0.022888 | 0.44861 | -0.045776 | 0.27924 | 0.050354 | 0.37537 | 0.67291 | 121.5912 | 0.54474 | 121.7239 | 121.3394 | 121.6049 | 121.4035 | 121.5088 | -121.5866 | -121.7468 | 121.6553 | 121.6278 | 107.8674 | 107.373
674.4688 | 121.8475 | -121.4905 | 0.10071 | -0.009308 | 6.9575 | 0.069532 | 0.064074 | -0.00071343 | -0.0063275 | -0.00065803 | 0.014709 | 0.0015914 | 0.068438 | 0.067892 | -0.0025677 | 0.021471 | -0.0037192 | -13.6368 | -0.16479 | -121.4264 | 0.19684 | -120.7169 | -121.4584 | -121.5866 | -14.0945 | -0.004578 | -121.637 | 0.16022 | -121.0648 | -121.225 | -121.5408 | 0.064087 | -0.2655 | 0.09613 | 0.77362 | -0.09613 | 0.032044 | -0.16022 | -0.032043 | -0.14648 | -0.10529 | 0.059509 | 0.42572 | -0.050354 | 0.2655 | 0.09613 | 0.41199 | 0.70953 | 121.6232 | 0.5722 | 121.7972 | 121.2616 | 121.6324 | 121.3257 | 121.4859 | -121.5271 | -121.7377 | 121.6873 | 121.6507 | 107.8537 | 107.3959
676.2031 | 121.8979 | -121.5454 | 0.10529 | -0.0016785 | 6.9577 | 0.069532 | 0.062151 | -0.0045586 | -0.0073957 | -0.0032214 | -0.0036011 | 0.0015914 | 0.06737 | 0.060415 | -0.0066265 | 0.021044 | -0.0035056 | -13.6871 | -0.13275 | -121.4767 | 0.19684 | -120.694 | -121.4218 | -121.5775 | -14.1083 | -0.036621 | -121.6278 | 0.16479 | -121.0236 | -121.1746 | -121.5317 | 0.068664 | -0.23804 | 0.091552 | 0.85144 | -0.032044 | 0.1236 | -0.10071 | 0.054932 | -0.082398 | -0.14191 | 0.059509 | 0.52185 | 0.013733 | 0.37079 | 0.096131 | 0.45319 | 0.78278 | 121.6736 | 0.60425 | 121.7926 | 121.344 | 121.5912 | 121.4127 | 121.5088 | -121.582 | -121.7331 | 121.7422 | 121.7102 | 107.8583 | 107.4371
677.8906 | 121.7789 | -121.5591 | 0.11902 | 0.005951 | 6.9633 | 0.067396 | 0.064074 | -0.001568 | -0.0084637 | -0.0010852 | 0.0086061 | 0.0028732 | 0.06673 | 0.06426 | -0.0055585 | 0.02083 | -8.7586e-05 | -13.6826 | -0.10071 | -121.5042 | 0.13275 | -120.7718 | -121.4996 | -121.6553 | -14.2136 | 0.009155 | -121.669 | 0.073242 | -121.1517 | -121.3211 | -121.5958 | 0.054932 | -0.21973 | 0.013732 | 0.78735 | -0.09613 | 0.059509 | -0.15106 | 0.004577 | -0.10986 | -0.10986 | -0.045777 | 0.40741 | -0.036621 | 0.23804 | 0.073242 | 0.3479 | 0.73242 | 121.637 | 0.51727 | 121.7422 | 121.4035 | 121.6782 | 121.4584 | 121.5683 | -121.6232 | -121.788 | 121.6919 | 121.6324 | 107.8766 | 107.3456
679.625 | 121.8567 | -121.5317 | 0.091553 | 0.005951 | 6.9596 | 0.067823 | 0.063433 | 0.0020636 | -0.0073957 | -0.002367 | -0.00054933 | 0.0020188 | 0.068011 | 0.059987 | -0.0053449 | 0.020189 | -0.0017966 | -13.7787 | -0.12817 | -121.5088 | 0.12817 | -120.7626 | -121.4813 | -121.6141 | -14.3097 | -0.041199 | -121.637 | 0.10986 | -121.0785 | -121.2158 | -121.5317 | 0.022888 | -0.21973 | 0.036621 | 0.76904 | -0.082398 | 0.050354 | -0.10529 | 0.027466 | -0.10529 | -0.13275 | 0.01831 | 0.45319 | 0 | 0.31586 | 0.10529 | 0.42114 | 0.74615 | 121.637 | 0.55847 | 121.7468 | 121.3806 | 121.5958 | 121.4035 | 121.4905 | -121.6003 | -121.7285 | 121.6599 | 121.6415 | 107.753 | 107.222
681.3594 | 121.8796 | -121.5225 | 0.10529 | 0.005951 | 6.9577 | 0.068891 | 0.062365 | -0.0037042 | -0.0065411 | -0.001726 | -0.00054933 | 0.0009506 | 0.068652 | 0.060201 | -0.0057721 | 0.021471 | -0.0020102 | -13.7604 | -0.14648 | -121.4767 | 0.20599 | -120.6757 | -121.4218 | -121.5637 | -14.2502 | -0.027466 | -121.6415 | 0.1236 | -121.0419 | -121.1975 | -121.5225 | 0.045776 | -0.25177 | 0.10071 | 0.84686 | -0.041199 | 0.10071 | -0.086975 | 0.054932 | -0.11902 | -0.13275 | 0.01831 | 0.48065 | 0 | 0.32501 | 0.11902 | 0.44403 | 0.80109 | 121.6827 | 0.59967 | 121.7651 | 121.3303 | 121.6141 | 121.376 | 121.4951 | -121.582 | -121.7468 | 121.7285 | 121.6461 | 107.7621 | 107.2723
683.0625 | 121.8338 | -121.5179 | 0.11444 | 0.01358 | 6.9605 | 0.067823 | 0.062792 | -0.0045586 | -0.0065411 | -0.0012988 | 0.0055543 | 0.0005234 | 0.06737 | 0.065328 | -0.0038495 | 0.019335 | -0.0011558 | -13.8611 | -0.13275 | -121.4905 | 0.13275 | -120.7901 | -121.5134 | -121.6324 | -14.4196 | -0.013733 | -121.6461 | 0.09613 | -121.138 | -121.2753 | -121.582 | 0.027465 | -0.24719 | 0.01831 | 0.72784 | -0.11444 | 0.004577 | -0.14191 | -0.022888 | -0.12817 | -0.12817 | -0.018311 | 0.37994 | -0.064087 | 0.24261 | 0.064087 | 0.37079 | 0.70038 | 121.6232 | 0.50812 | 121.7422 | 121.3577 | 121.6324 | 121.3852 | 121.5042 | -121.6049 | -121.7606 | 121.6507 | 121.6141 | 107.6569 | 107.0984
684.7656 | 121.8796 | -121.5317 | 0.082397 | -0.0016785 | 6.9594 | 0.066328 | 0.064929 | -0.0028498 | -0.0084637 | -1.7026e-05 | 0.0025025 | 0.0003098 | 0.068866 | 0.058065 | -0.0061993 | 0.019762 | -0.0024374 | -13.8886 | -0.13275 | -121.5042 | 0.15106 | -120.7397 | -121.4493 | -121.6095 | -14.3646 | -0.027466 | -121.6415 | 0.13733 | -121.0648 | -121.1929 | -121.5225 | 0.027466 | -0.21515 | 0.068665 | 0.79193 | -0.07782 | 0.082397 | -0.10529 | 0.054931 | -0.10986 | -0.10986 | 0.054932 | 0.46692 | 0.009155 | 0.33875 | 0.11902 | 0.44861 | 0.76447 | 121.6553 | 0.57678 | 121.7789 | 121.3715 | 121.6141 | 121.3989 | 121.5042 | -121.5866 | -121.7239 | 121.6827 | 121.669 | 107.6431 | 107.1671
686.5 | 121.756 | -121.5454 | 0.12817 | 0.005951 | 6.9605 | 0.068037 | 0.064288 | 0.00099557 | -0.0054731 | -0.0012988 | -0.00054933 | 0.0045822 | 0.069079 | 0.05422 | -0.0053449 | 0.020403 | -0.003292 | -13.9481 | -0.11902 | -121.5042 | 0.050354 | -120.8771 | -121.5958 | -121.7422 | -14.5157 | 0.004578 | -121.6644 | 0.027466 | -121.2112 | -121.3669 | -121.6278 | 0.041199 | -0.24719 | -0.07782 | 0.66833 | -0.19684 | -0.050354 | -0.23804 | -0.091553 | -0.11902 | -0.1236 | -0.10071 | 0.33417 | -0.082398 | 0.17853 | 0.036621 | 0.29755 | 0.62714 | 121.5546 | 0.45319 | 121.6919 | 121.3852 | 121.669 | 121.4264 | 121.55 | -121.6324 | -121.7926 | 121.5958 | 121.5729 | 107.5974 | 107.0297
688.1719 | 121.8842 | -121.5225 | 0.091553 | -0.024567 | 6.9581 | 0.069532 | 0.064715 | 0.00078177 | -0.0026959 | -0.001726 | -0.00054933 | 0.0026596 | 0.066516 | 0.067037 | -0.0064129 | 0.021471 | -0.0024374 | -13.8977 | -0.13275 | -121.463 | 0.18768 | -120.694 | -121.4355 | -121.5866 | -14.3692 | -0.027466 | -121.6141 | 0.13275 | -121.0327 | -121.1929 | -121.5179 | 0.059509 | -0.2243 | 0.09613 | 0.82855 | -0.064087 | 0.086975 | -0.1236 | 0.027466 | -0.091553 | -0.11902 | 0.041198 | 0.48981 | 0.004578 | 0.32959 | 0.096131 | 0.42114 | 0.76904 | 121.6507 | 0.58136 | 121.7468 | 121.3303 | 121.5866 | 121.3898 | 121.4951 | -121.5546 | -121.7056 | 121.7102 | 121.6553 | 107.6248 | 107.1533
689.9062 | 121.8842 | -121.5134 | 0.091553 | -0.0016785 | 6.9594 | 0.069105 | 0.065783 | -0.0013544 | -0.0037641 | -0.0015124 | -0.0066527 | 0.0013778 | 0.065661 | 0.064687 | -0.0012861 | 0.022753 | -0.0022238 | -13.9481 | -0.14648 | -121.4401 | 0.18768 | -120.7352 | -121.4905 | -121.6187 | -14.4516 | -0.045776 | -121.6415 | 0.16022 | -121.0693 | -121.225 | -121.5225 | 0.073242 | -0.23804 | 0.09613 | 0.7782 | -0.10528 | 0.022888 | -0.17853 | -0.050354 | -0.12817 | -0.13733 | 0.068664 | 0.44403 | -0.009155 | 0.28839 | 0.11902 | 0.41657 | 0.70496 | 121.6278 | 0.5722 | 121.8018 | 121.2936 | 121.5958 | 121.3669 | 121.4676 | -121.5317 | -121.7331 | 121.7011 | 121.6736 | 107.5653 | 107.0618
691.6406 | 121.7514 | -121.5317 | 0.12817 | -0.0016785 | 6.9613 | 0.067182 | 0.06621 | -0.0030634 | -0.0029095 | -0.0019396 | -0.0036011 | 0.0037278 | 0.067157 | 0.055074 | -0.0068403 | 0.019549 | -0.00051479 | -14.0488 | -0.11902 | -121.5134 | 0.041199 | -120.9183 | -121.6232 | -121.756 | -14.6393 | -0.009155 | -121.6507 | 0.004578 | -121.225 | -121.3806 | -121.6461 | 0.01831 | -0.24719 | -0.086975 | 0.6134 | -0.2243 | -0.091553 | -0.24261 | -0.10986 | -0.11902 | -0.13733 | -0.1236 | 0.3067 | -0.11444 | 0.15106 | 0.004578 | 0.27008 | 0.59509 | 121.5546 | 0.42572 | 121.6553 | 121.3943 | 121.6415 | 121.4127 | 121.5225 | -121.6415 | -121.7789 | 121.5729 | 121.5363 | 107.4829 | 106.8924
693.3281 | 121.756 | -121.582 | 0.11902 | -0.009308 | 6.9592 | 0.068891 | 0.064929 | 0.00078177 | -0.0061139 | 0.001692 | -0.0066527 | 0.003514 | 0.068225 | 0.056783 | -0.0070539 | 0.020403 | -0.002651 | -14.0396 | -0.10071 | -121.5088 | 0.082397 | -120.8633 | -121.5912 | -121.7377 | -14.621 | 0.004578 | -121.6599 | 0.022888 | -121.2067 | -121.376 | -121.637 | 0.073242 | -0.21973 | -0.036622 | 0.71869 | -0.15564 | -0.009156 | -0.22888 | -0.082398 | -0.07782 | -0.11444 | -0.096131 | 0.37537 | -0.054932 | 0.20599 | 0.022888 | 0.28381 | 0.64545 | 121.5912 | 0.45319 | 121.6827 | 121.4081 | 121.6644 | 121.4813 | 121.5866 | -121.6278 | -121.7789 | 121.6644 | 121.6049 | 107.5424 | 106.9611
695.0625 | 121.8933 | -121.5225 | 0.09613 | -0.009308 | 6.9626 | 0.069105 | 0.061511 | -0.00071343 | -0.0067547 | -0.001726 | -0.0036011 | 0.002446 | 0.067584 | 0.058065 | -0.0047039 | 0.022753 | -0.00051479 | -14.0671 | -0.13733 | -121.463 | 0.17853 | -120.726 | -121.4813 | -121.6049 | -14.5294 | -0.036621 | -121.6278 | 0.16022 | -121.0464 | -121.2204 | -121.5179 | 0.059509 | -0.23346 | 0.082398 | 0.79651 | -0.082397 | 0.041199 | -0.14191 | -0.01831 | -0.10529 | -0.13275 | 0.064087 | 0.47607 | 0.004578 | 0.30212 | 0.10986 | 0.40741 | 0.737 | 121.6415 | 0.58136 | 121.788 | 121.3257 | 121.5912 | 121.3852 | 121.4859 | -121.5591 | -121.7239 | 121.701 | 121.6827 | 107.4554 | 106.9931
696.7969 | 121.7468 | -121.5546 | 0.13733 | -0.0016785 | 6.9613 | 0.066755 | 0.064929 | -0.0022088 | -0.0029095 | -0.0032214 | -0.00054933 | 0.002446 | 0.068011 | 0.058492 | -0.0034223 | 0.021898 | -0.0041464 | -14.1129 | -0.10986 | -121.5179 | 0.064087 | -120.8588 | -121.5912 | -121.7331 | -14.6851 | 0.004578 | -121.6599 | 0.013733 | -121.2158 | -121.3898 | -121.6415 | 0.036621 | -0.24719 | -0.073242 | 0.6958 | -0.17853 | -0.036622 | -0.21515 | -0.073243 | -0.10529 | -0.13275 | -0.1236 | 0.33875 | -0.086976 | 0.16479 | 0.01831 | 0.27008 | 0.65918 | 121.582 | 0.44403 | 121.6736 | 121.4081 | 121.6644 | 121.4447 | 121.5591 | -121.6553 | -121.7972 | 121.6187 | 121.5683 | 107.4417 | 106.8695
698.4844 | 121.8658 | -121.5317 | 0.086975 | -0.0016785 | 6.9598 | 0.069959 | 0.060015 | -0.0017816 | -0.0069683 | -0.002367 | -0.00054933 | 0.0003098 | 0.066089 | 0.059133 | -0.0072675 | 0.020617 | -0.0054282 | -14.09 | -0.15106 | -121.4767 | 0.18768 | -120.6985 | -121.4218 | -121.6095 | -14.5432 | -0.036621 | -121.6324 | 0.1236 | -121.051 | -121.2067 | -121.5317 | 0.054931 | -0.23804 | 0.10071 | 0.83313 | -0.07782 | 0.10986 | -0.13275 | 0.054932 | -0.10071 | -0.1236 | 0.036621 | 0.48065 | 0 | 0.32501 | 0.10071 | 0.42572 | 0.7782 | 121.6644 | 0.58136 | 121.756 | 121.3257 | 121.5958 | 121.3806 | 121.4951 | -121.5637 | -121.7194 | 121.7194 | 121.6553 | 107.4417 | 106.9885
700.2344 | 121.8704 | -121.4859 | 0.082397 | -0.0016785 | 6.9603 | 0.069746 | 0.064715 | -0.0024224 | -0.0022687 | 0.00083737 | -0.0066527 | 0.0011642 | 0.071429 | 0.06426 | -0.0019269 | 0.019762 | -0.0030784 | -14.1403 | -0.15106 | -121.4813 | 0.18768 | -120.7169 | -121.4767 | -121.6095 | -14.621 | -0.009155 | -121.6461 | 0.16022 | -121.0693 | -121.2387 | -121.5225 | 0.004578 | -0.23346 | 0.10529 | 0.76904 | -0.1236 | 0.009155 | -0.12817 | 0.004577 | -0.16022 | -0.091552 | 0.07782 | 0.41656 | -0.036621 | 0.24719 | 0.1236 | 0.40741 | 0.76447 | 121.669 | 0.57678 | 121.8063 | 121.3303 | 121.637 | 121.3348 | 121.4767 | -121.5637 | -121.7285 | 121.6736 | 121.6461 | 107.3456 | 106.8649
701.9688 | 121.8338 | -121.5454 | 0.09613 | 0.01358 | 6.9581 | 0.069319 | 0.061083 | 0.00056817 | -0.0065411 | -0.0012988 | 0.0025025 | -0.0005448 | 0.068438 | 0.054647 | -0.0053449 | 0.021471 | -0.003292 | -14.2181 | -0.1236 | -121.5225 | 0.11444 | -120.7901 | -121.5134 | -121.6461 | -14.74 | -0.027466 | -121.6461 | 0.086975 | -121.1243 | -121.2708 | -121.5591 | 0.022888 | -0.21973 | 0.018311 | 0.75531 | -0.10071 | 0.032043 | -0.1236 | 0.009155 | -0.10071 | -0.1236 | -0.009155 | 0.42114 | -0.013733 | 0.27466 | 0.086975 | 0.37537 | 0.73242 | 121.637 | 0.52185 | 121.7331 | 121.3989 | 121.6187 | 121.4218 | 121.5179 | -121.6187 | -121.7422 | 121.6599 | 121.6324 | 107.3273 | 106.8054
703.7188 | 121.7697 | -121.5866 | 0.10529 | -0.009308 | 6.9626 | 0.06825 | 0.065142 | 0.00078177 | -0.0037641 | 0.00083737 | 0.011658 | 0.0028732 | 0.071216 | 0.051015 | -0.0091901 | 0.018694 | -0.006069 | -14.1953 | -0.091553 | -121.5637 | 0.064087 | -120.8588 | -121.5637 | -121.6873 | -14.7446 | 0.013733 | -121.7102 | 0.013733 | -121.1884 | -121.3394 | -121.6232 | 0.022888 | -0.19684 | -0.041199 | 0.72784 | -0.10071 | 0.022888 | -0.1236 | 0 | -0.1236 | -0.091553 | -0.091553 | 0.39825 | -0.036621 | 0.24719 | 0.086975 | 0.37079 | 0.70496 | 121.6278 | 0.52185 | 121.7239 | 121.4722 | 121.7239 | 121.4951 | 121.6003 | -121.669 | -121.8155 | 121.6507 | 121.6003 | 107.3914 | 106.842
705.3906 | 121.875 | -121.5591 | 0.07782 | -0.0016785 | 6.9613 | 0.067823 | 0.062579 | -0.0013544 | -0.0041913 | -0.001726 | -0.0036011 | 9.6204e-05 | 0.067798 | 0.055501 | -0.0072675 | 0.020617 | -0.0020102 | -14.1861 | -0.16022 | -121.4951 | 0.1831 | -120.7214 | -121.4539 | -121.6141 | -14.6805 | -0.045776 | -121.637 | 0.1236 | -121.0648 | -121.2204 | -121.5363 | 0.064087 | -0.23804 | 0.10528 | 0.83771 | -0.054932 | 0.10529 | -0.11902 | 0.041199 | -0.07782 | -0.1236 | 0.045776 | 0.49439 | 0.022888 | 0.33875 | 0.10071 | 0.41656 | 0.77362 | 121.6782 | 0.5722 | 121.7606 | 121.3348 | 121.5912 | 121.3989 | 121.5134 | -121.5729 | -121.7148 | 121.7422 | 121.6827 | 107.373 | 106.8787
707.0625 | 121.8292 | -121.5637 | 0.086975 | 0.028839 | 6.9605 | 0.068891 | 0.065569 | 0.0027044 | -0.0056867 | -0.0015124 | 0.0025025 | 0.0022324 | 0.068438 | 0.054861 | -0.0029949 | 0.019549 | -0.0020102 | -14.2685 | -0.15106 | -121.5042 | 0.16937 | -120.7352 | -121.5088 | -121.6232 | -14.7491 | -0.032043 | -121.6644 | 0.091553 | -121.1243 | -121.2753 | -121.5637 | 0.05951 | -0.23804 | 0.082398 | 0.82855 | -0.059509 | 0.054932 | -0.11902 | -0.004578 | -0.10071 | -0.11902 | 0.004578 | 0.43945 | 0 | 0.28839 | 0.10071 | 0.3891 | 0.76904 | 121.6736 | 0.54016 | 121.756 | 121.3531 | 121.6324 | 121.4127 | 121.5317 | -121.5912 | -121.7514 | 121.7331 | 121.6553 | 107.2952 | 106.8146
708.8125 | 121.8613 | -121.5317 | 0.086975 | 0.036468 | 6.9624 | 0.072096 | 0.065142 | 0.00035457 | -0.0031231 | -0.00065803 | 0.0086061 | 0.0020188 | 0.064807 | 0.059133 | -0.0025677 | 0.021258 | -0.003292 | -14.2776 | -0.13275 | -121.5134 | 0.18768 | -120.7214 | -121.463 | -121.6003 | -14.7125 | -0.036621 | -121.6461 | 0.14191 | -121.1014 | -121.257 | -121.5408 | 0.01831 | -0.21973 | 0.10071 | 0.81024 | -0.068665 | 0.068664 | -0.086975 | 0.050354 | -0.11444 | -0.1236 | 0.054932 | 0.4303 | -0.009156 | 0.27466 | 0.10528 | 0.3891 | 0.79193 | 121.7011 | 0.54474 | 121.788 | 121.3806 | 121.6095 | 121.3989 | 121.4951 | -121.6003 | -121.7331 | 121.7194 | 121.6736 | 107.254 | 106.8192
710.4844 | 121.8292 | -121.5408 | 0.07782 | 0.036468 | 6.9581 | 0.06825 | 0.064501 | -0.004986 | -0.0059003 | 0.00019657 | 0.0086061 | 0.0005234 | 0.06737 | 0.063192 | -0.0040631 | 0.021471 | -0.0013694 | -14.3234 | -0.13275 | -121.5042 | 0.14648 | -120.7581 | -121.5042 | -121.6232 | -14.8041 | -0.027466 | -121.6507 | 0.091553 | -121.1426 | -121.2845 | -121.5683 | 0.036622 | -0.21057 | 0.068664 | 0.78278 | -0.082397 | 0.036622 | -0.11902 | 0 | -0.10986 | -0.10529 | 0.013733 | 0.39826 | -0.027465 | 0.25635 | 0.082398 | 0.36621 | 0.74615 | 121.6507 | 0.50812 | 121.7422 | 121.3715 | 121.6232 | 121.4081 | 121.5134 | -121.582 | -121.7285 | 121.6873 | 121.6324 | 107.2174 | 106.7368
712.1562 | 121.8338 | -121.5088 | 0.10071 | 0.028839 | 6.9624 | 0.068678 | 0.065142 | -0.00092703 | -0.0046185 | -0.0021532 | 0.0086061 | 0.002446 | 0.06972 | 0.059133 | -0.0055585 | 0.021258 | -0.00094199 | -14.3143 | -0.1236 | -121.5042 | 0.17853 | -120.7352 | -121.4813 | -121.6278 | -14.7995 | -0.027466 | -121.6278 | 0.10986 | -121.1243 | -121.2662 | -121.5683 | 0.004578 | -0.2243 | 0.07782 | 0.77362 | -0.11902 | 0.027466 | -0.1236 | 0.022888 | -0.11902 | -0.12817 | 0.009155 | 0.38452 | -0.059509 | 0.24261 | 0.05951 | 0.36163 | 0.76904 | 121.6827 | 0.50354 | 121.7377 | 121.3806 | 121.6003 | 121.3852 | 121.4813 | -121.6049 | -121.7285 | 121.6873 | 121.6187 | 107.1945 | 106.7093
713.8906 | 121.8704 | -121.5363 | 0.07782 | -0.009308 | 6.9622 | 0.069319 | 0.06621 | -0.00071343 | -0.0061139 | -0.0012988 | 0.0086061 | 0.004155 | 0.068438 | 0.056569 | -0.0044903 | 0.020403 | -0.0013694 | -14.328 | -0.16479 | -121.4859 | 0.16479 | -120.726 | -121.4539 | -121.6141 | -14.8087 | -0.022888 | -121.6461 | 0.14648 | -121.0739 | -121.2158 | -121.5408 | 0.050354 | -0.24261 | 0.086975 | 0.81024 | -0.07782 | 0.082398 | -0.12817 | 0.032044 | -0.10986 | -0.10071 | 0.068664 | 0.46234 | -0.004578 | 0.32044 | 0.10528 | 0.4303 | 0.75989 | 121.6507 | 0.5722 | 121.7926 | 121.3211 | 121.6232 | 121.3715 | 121.5134 | -121.5637 | -121.7239 | 121.701 | 121.6827 | 107.2083 | 106.7276
715.625 | 121.756 | -121.5591 | 0.11444 | -0.016937 | 6.9622 | 0.067182 | 0.064929 | -0.0017816 | -0.0052595 | -0.0019396 | -0.0066527 | 0.0018052 | 0.067157 | 0.060201 | -0.0079083 | 0.019335 | -0.002651 | -14.36 | -0.13275 | -121.55 | 0.086975 | -120.8405 | -121.5408 | -121.6919 | -14.9414 | -0.013733 | -121.6599 | 0 | -121.1792 | -121.3257 | -121.6232 | 0.009155 | -0.24719 | -0.027466 | 0.71869 | -0.13275 | 0.01831 | -0.14191 | 0.009155 | -0.10071 | -0.12817 | -0.11444 | 0.37994 | -0.064087 | 0.23346 | 0.036621 | 0.33417 | 0.70953 | 121.637 | 0.48065 | 121.6599 | 121.4172 | 121.6461 | 121.4264 | 121.5454 | -121.6644 | -121.7743 | 121.6461 | 121.5591 | 107.1991 | 106.6177
717.3594 | 121.843 | -121.55 | 0.07782 | -0.016937 | 6.9588 | 0.065901 | 0.064929 | -0.00028623 | -0.0059003 | -0.00065803 | -0.00054933 | 0.0011642 | 0.067798 | 0.058278 | -0.0070539 | 0.022326 | -0.0039328 | -14.4333 | -0.11444 | -121.5363 | 0.086975 | -120.845 | -121.5729 | -121.6827 | -14.9689 | -0.032043 | -121.6461 | 0.10071 | -121.1288 | -121.2708 | -121.55 | 0.013733 | -0.19226 | 0.009155 | 0.70496 | -0.13275 | -0.022888 | -0.14648 | -0.036621 | -0.09613 | -0.10986 | 0.022888 | 0.42114 | 0 | 0.27924 | 0.09613 | 0.37537 | 0.69122 | 121.6232 | 0.51727 | 121.7468 | 121.4218 | 121.6141 | 121.4355 | 121.5179 | -121.6141 | -121.7239 | 121.637 | 121.6507 | 107.1167 | 106.5811
719.0312 | 121.8567 | -121.5408 | 0.086975 | 0.044098 | 6.9622 | 0.069319 | 0.067278 | 0.0031318 | -0.0029095 | 0.001051 | 0.011658 | 0.0018052 | 0.068438 | 0.070669 | -0.0061993 | 0.02318 | 0.00076681 | -14.3967 | -0.13733 | -121.5088 | 0.20599 | -120.7169 | -121.463 | -121.5958 | -14.8819 | -0.036621 | -121.6415 | 0.1236 | -121.0968 | -121.2387 | -121.5317 | 0.032044 | -0.2243 | 0.11902 | 0.82398 | -0.054931 | 0.07782 | -0.086975 | 0.045776 | -0.10071 | -0.1236 | 0.036621 | 0.44403 | 0.009156 | 0.30213 | 0.10986 | 0.40283 | 0.79193 | 121.7148 | 0.54474 | 121.7651 | 121.3715 | 121.6049 | 121.4035 | 121.5042 | -121.5958 | -121.7285 | 121.7468 | 121.6644 | 107.1442 | 106.6589
720.7656 | 121.7972 | -121.5546 | 0.10071 | -0.009308 | 6.9598 | 0.066755 | 0.064501 | 0.0029182 | -0.0050457 | -0.0015124 | -0.00054933 | 0.0026596 | 0.068438 | 0.056356 | -0.0044903 | 0.021898 | -0.0039328 | -14.4882 | -0.1236 | -121.55 | 0.059509 | -120.8725 | -121.6095 | -121.7194 | -15.0146 | -0.009155 | -121.6278 | 0.064087 | -121.1746 | -121.3257 | -121.5912 | 0.004577 | -0.2243 | -0.041199 | 0.68207 | -0.16479 | -0.054932 | -0.16937 | -0.059509 | -0.073243 | -0.10986 | -0.036621 | 0.37994 | -0.036622 | 0.22888 | 0.036621 | 0.30212 | 0.67749 | 121.6095 | 0.45319 | 121.6919 | 121.4264 | 121.6187 | 121.431 | 121.5454 | -121.6507 | -121.7285 | 121.6141 | 121.6187 | 107.0663 | 106.5399
722.5 | 121.7377 | -121.582 | 0.11444 | -0.009308 | 6.9615 | 0.065687 | 0.065997 | 0.00078177 | -0.0069683 | -0.00065803 | -0.0036011 | 0.0011642 | 0.069507 | 0.055501 | -0.010899 | 0.019121 | -0.0013694 | -14.4745 | -0.10986 | -121.5546 | 0.045776 | -120.8771 | -121.5729 | -121.7056 | -15.065 | 0.013733 | -121.6827 | -0.018311 | -121.2204 | -121.3531 | -121.6324 | 0.027466 | -0.2243 | -0.068665 | 0.70496 | -0.1236 | 0.009155 | -0.15106 | -0.018311 | -0.10071 | -0.10071 | -0.13275 | 0.36163 | -0.050354 | 0.22888 | 0.050354 | 0.32959 | 0.67749 | 121.6003 | 0.46234 | 121.6644 | 121.4447 | 121.6965 | 121.4722 | 121.5958 | -121.669 | -121.7972 | 121.6278 | 121.5637 | 107.1075 | 106.517
724.1719 | 121.7789 | -121.55 | 0.11902 | 0.01358 | 6.9628 | 0.067396 | 0.063647 | 0.00035457 | -0.0052595 | 0.0014784 | -0.00054933 | 0.0050094 | 0.06737 | 0.060628 | -0.0055585 | 0.020617 | -0.0024374 | -14.4058 | -0.10986 | -121.5408 | 0.11902 | -120.8176 | -121.5317 | -121.6782 | -14.9918 | -0.036621 | -121.6507 | 0.045776 | -121.1655 | -121.312 | -121.5912 | 0.009155 | -0.22888 | 0 | 0.73242 | -0.12817 | 0.018311 | -0.13733 | 0.009156 | -0.10071 | -0.15564 | -0.073243 | 0.38452 | -0.041199 | 0.23804 | 0.059509 | 0.33875 | 0.72327 | 121.6599 | 0.48523 | 121.6965 | 121.431 | 121.6141 | 121.4401 | 121.5134 | -121.6599 | -121.7697 | 121.669 | 121.5958 | 107.1442 | 106.5582
725.9062 | 121.8155 | -121.5225 | 0.10071 | 0.01358 | 6.9607 | 0.070387 | 0.063433 | -0.00071343 | -0.0059003 | 0.001692 | 0.011658 | 0.0011642 | 0.068011 | 0.056569 | -0.0051313 | 0.020617 | 0.00055321 | -14.5294 | -0.13733 | -121.5042 | 0.13275 | -120.7855 | -121.5042 | -121.6415 | -15.0604 | -0.032043 | -121.6461 | 0.073242 | -121.1472 | -121.2891 | -121.582 | 0.018311 | -0.23804 | 0.032043 | 0.737 | -0.11902 | 0.018311 | -0.13733 | 0 | -0.1236 | -0.13275 | -0.027466 | 0.37537 | -0.059509 | 0.23346 | 0.064087 | 0.35706 | 0.71869 | 121.637 | 0.49896 | 121.7194 | 121.3669 | 121.6141 | 121.3852 | 121.4905 | -121.6049 | -121.7468 | 121.6553 | 121.5958 | 106.9931 | 106.4621
727.6406 | 121.7422 | -121.5729 | 0.10529 | -0.009308 | 6.9609 | 0.069746 | 0.065142 | -0.001568 | -0.0063275 | 0.00041017 | -0.0036011 | 0.000737 | 0.070147 | 0.055715 | -0.0064129 | 0.021898 | -0.00072839 | -14.4836 | -0.1236 | -121.5408 | 0.054932 | -120.8725 | -121.6049 | -121.7239 | -15.0879 | -0.022888 | -121.6415 | 0.004578 | -121.2067 | -121.376 | -121.6278 | 0.032043 | -0.22888 | -0.050354 | 0.70038 | -0.15106 | -0.032043 | -0.1831 | -0.064086 | -0.068665 | -0.12817 | -0.10071 | 0.36621 | -0.054932 | 0.19684 | 0.013733 | 0.2655 | 0.66834 | 121.5958 | 0.43488 | 121.6461 | 121.4172 | 121.6187 | 121.4493 | 121.55 | -121.6461 | -121.7468 | 121.6278 | 121.5775 | 107.0892 | 106.485
729.3125 | 121.8063 | -121.5317 | 0.11902 | 0.01358 | 6.9607 | 0.067823 | 0.066638 | -0.00049983 | -0.0026959 | -0.0021532 | 0.0055543 | 0.0028732 | 0.065234 | 0.055929 | -0.0059857 | 0.02083 | -0.0020102 | -14.4653 | -0.082397 | -121.5179 | 0.14648 | -120.7718 | -121.4905 | -121.637 | -15.0055 | 0.022888 | -121.6415 | 0.068665 | -121.1151 | -121.2708 | -121.5591 | 0.013733 | -0.20142 | 0.027465 | 0.75989 | -0.10529 | 0.041198 | -0.11902 | 0.027465 | -0.10986 | -0.096131 | -0.050354 | 0.41657 | -0.027466 | 0.26093 | 0.082398 | 0.37079 | 0.74615 | 121.6644 | 0.52643 | 121.7102 | 121.4355 | 121.6644 | 121.4493 | 121.5546 | -121.637 | -121.7606 | 121.6782 | 121.6003 | 107.0663 | 106.5262
731 | 121.8704 | -121.5179 | 0.091553 | -0.0016785 | 6.9615 | 0.068891 | 0.065142 | 0.00099557 | -0.0046185 | -0.0015124 | -0.0036011 | 0.0018052 | 0.068652 | 0.058919 | -0.0040631 | 0.02318 | -0.0024374 | -14.5203 | -0.13275 | -121.4722 | 0.18768 | -120.7169 | -121.463 | -121.5866 | -15.0009 | -0.041199 | -121.6187 | 0.17395 | -121.0464 | -121.1929 | -121.4676 | 0.045776 | -0.2243 | 0.09613 | 0.80109 | -0.068665 | 0.054931 | -0.11444 | 0.009155 | -0.10071 | -0.13275 | 0.082397 | 0.4715 | 0.050354 | 0.32501 | 0.15106 | 0.42572 | 0.75531 | 121.6599 | 0.5722 | 121.7926 | 121.3394 | 121.5775 | 121.3852 | 121.4767 | -121.5637 | -121.7102 | 121.7056 | 121.6919 | 106.9977 | 106.517
732.7344 | 121.8018 | -121.5363 | 0.14191 | 0.02121 | 6.9624 | 0.068678 | 0.064929 | 0.00185 | -0.0052595 | 0.00041017 | 0.0025025 | 0.0013778 | 0.065875 | 0.058492 | -0.0064129 | 0.019762 | -0.0013694 | -14.502 | -0.086975 | -121.5225 | 0.14648 | -120.7443 | -121.4905 | -121.6278 | -15.0055 | 0.032043 | -121.6232 | 0.09613 | -121.1105 | -121.257 | -121.55 | 0.013733 | -0.22888 | 0.004577 | 0.79193 | -0.091553 | 0.045776 | -0.10529 | 0.032043 | -0.086975 | -0.10986 | -0.045777 | 0.42572 | -0.013733 | 0.27924 | 0.073242 | 0.36621 | 0.7782 | 121.669 | 0.5127 | 121.7194 | 121.4355 | 121.6553 | 121.4493 | 121.5683 | -121.6644 | -121.7651 | 121.6827 | 121.6324 | 107.0343 | 106.5308
734.4688 | 121.7834 | -121.5317 | 0.13275 | 0.02121 | 6.9618 | 0.068464 | 0.06386 | -0.002636 | -0.0037641 | 0.0025464 | 0.0025025 | 0.0033004 | 0.065875 | 0.053579 | -0.0047039 | 0.018694 | -0.0039328 | -14.5157 | -0.082397 | -121.4996 | 0.14191 | -120.7443 | -121.4767 | -121.6141 | -15.0375 | 0.032043 | -121.6095 | 0.11444 | -121.106 | -121.2753 | -121.55 | 0.032043 | -0.21515 | 0.009156 | 0.78735 | -0.082398 | 0.054931 | -0.11444 | 0.022888 | -0.07782 | -0.10071 | -0.01831 | 0.42572 | -0.018311 | 0.25635 | 0.059509 | 0.33417 | 0.75531 | 121.6415 | 0.50354 | 121.7239 | 121.4172 | 121.6415 | 121.4493 | 121.5637 | -121.6324 | -121.7422 | 121.6736 | 121.6461 | 107.016 | 106.4941
736.1406 | 121.7468 | -121.5454 | 0.13733 | -0.0016785 | 6.962 | 0.06761 | 0.065569 | -0.00092703 | -0.0059003 | 0.0014784 | -0.0036011 | 0.0030868 | 0.066516 | 0.058278 | -0.0042767 | 0.019976 | -0.0041464 | -14.6347 | -0.086975 | -121.4767 | 0.050354 | -120.845 | -121.5775 | -121.6965 | -15.184 | 0.018311 | -121.6507 | 0.032043 | -121.1838 | -121.3165 | -121.5866 | 0.068664 | -0.2243 | -0.086975 | 0.70038 | -0.15106 | -0.032044 | -0.21973 | -0.10071 | -0.10529 | -0.11902 | -0.10529 | 0.36163 | -0.041199 | 0.22888 | 0.064087 | 0.33417 | 0.63171 | 121.5271 | 0.46692 | 121.6827 | 121.3898 | 121.669 | 121.4584 | 121.5637 | -121.6141 | -121.788 | 121.5958 | 121.5775 | 106.9107 | 106.3614
737.875 | 121.7743 | -121.5271 | 0.14191 | -0.0016785 | 6.9598 | 0.070173 | 0.062365 | 0.00056817 | -0.0067547 | -0.0012988 | -0.0036011 | 0.0005234 | 0.06673 | 0.056569 | -0.0074811 | 0.018908 | -0.003292 | -14.5981 | -0.14648 | -121.4584 | 0.16022 | -120.7123 | -121.431 | -121.5866 | -15.0879 | -0.018311 | -121.6187 | 0.082397 | -121.0968 | -121.2387 | -121.5317 | 0.068665 | -0.28839 | 0.01831 | 0.81482 | -0.059509 | 0.096131 | -0.12817 | 0.027466 | -0.091552 | -0.16022 | -0.05951 | 0.4303 | -0.004577 | 0.28839 | 0.086975 | 0.37994 | 0.74615 | 121.6187 | 0.52185 | 121.701 | 121.312 | 121.6003 | 121.3806 | 121.5088 | -121.6003 | -121.7606 | 121.6873 | 121.6095 | 106.929 | 106.4392
739.5625 | 121.7834 | -121.5225 | 0.11902 | 0.005951 | 6.9637 | 0.068678 | 0.066638 | 0.00185 | -0.0033369 | -0.0015124 | 0.0025025 | 0.004155 | 0.06673 | 0.056569 | -0.0040631 | 0.020617 | -0.003292 | -14.5889 | -0.082397 | -121.4951 | 0.13275 | -120.7809 | -121.4584 | -121.6095 | -15.097 | 0.018311 | -121.6049 | 0.10529 | -121.0968 | -121.257 | -121.5408 | 0.027466 | -0.20142 | 0.013732 | 0.74158 | -0.086975 | 0.064087 | -0.11444 | 0.036621 | -0.082397 | -0.10071 | -0.013733 | 0.42572 | -0.018311 | 0.2655 | 0.064086 | 0.3479 | 0.71411 | 121.6278 | 0.50812 | 121.7102 | 121.4127 | 121.6232 | 121.4401 | 121.5408 | -121.6141 | -121.7239 | 121.6553 | 121.6278 | 106.9336 | 106.4255
741.2969 | 121.8842 | -121.4996 | 0.10986 | -0.0016785 | 6.9605 | 0.067182 | 0.063647 | -0.0030634 | -0.0059003 | -0.003435 | 0.0025025 | 9.6204e-05 | 0.067157 | 0.056142 | -0.0059857 | 0.021471 | -0.0041464 | -14.6393 | -0.1236 | -121.463 | 0.1831 | -120.7031 | -121.4127 | -121.5408 | -15.1062 | -0.022888 | -121.5775 | 0.16937 | -121.0144 | -121.1655 | -121.463 | 0.036621 | -0.23346 | 0.073242 | 0.79651 | -0.041199 | 0.086975 | -0.07782 | 0.050354 | -0.07782 | -0.13275 | 0.05951 | 0.48523 | 0.036621 | 0.33417 | 0.11444 | 0.41199 | 0.75989 | 121.6461 | 0.56305 | 121.7468 | 121.3394 | 121.5546 | 121.376 | 121.4767 | -121.5729 | -121.6873 | 121.6827 | 121.669 | 106.8604 | 106.3934
743.0312 | 121.7514 | -121.5408 | 0.11902 | -0.0016785 | 6.9598 | 0.066114 | 0.064074 | -7.2628e-05 | -0.0041913 | -0.003435 | -0.00054933 | 0.002446 | 0.065448 | 0.052297 | -0.0044903 | 0.021685 | -0.0020102 | -14.7125 | -0.09613 | -121.5042 | 0.050354 | -120.8405 | -121.5591 | -121.6873 | -15.2664 | 0.018311 | -121.5958 | 0.073242 | -121.1609 | -121.3028 | -121.55 | 0.036622 | -0.21515 | -0.068665 | 0.70038 | -0.14648 | -0.01831 | -0.18311 | -0.054932 | -0.054931 | -0.10071 | -0.045777 | 0.37994 | -0.009155 | 0.23804 | 0.045776 | 0.29297 | 0.66376 | 121.5546 | 0.43488 | 121.669 | 121.4081 | 121.6141 | 121.4447 | 121.5591 | -121.6232 | -121.7148 | 121.5912 | 121.6141 | 106.8283 | 106.2744
744.7812 | 121.7697 | -121.5134 | 0.14191 | 0.02121 | 6.9635 | 0.067182 | 0.064288 | 0.003559 | -0.0054731 | -0.0015124 | 0.0025025 | 0.0033004 | 0.067584 | 0.053365 | -0.0070539 | 0.019335 | -0.0024374 | -14.5981 | -0.086975 | -121.4813 | 0.14191 | -120.7626 | -121.4767 | -121.6187 | -15.1382 | 0.009155 | -121.582 | 0.10529 | -121.0831 | -121.2433 | -121.5042 | 0.032044 | -0.22888 | 0 | 0.75073 | -0.10528 | 0.036621 | -0.13733 | 0.004577 | -0.068664 | -0.13275 | -0.036621 | 0.4303 | 0.009156 | 0.27008 | 0.07782 | 0.33875 | 0.71869 | 121.6232 | 0.49896 | 121.6873 | 121.3943 | 121.5912 | 121.4264 | 121.5225 | -121.6232 | -121.7239 | 121.6553 | 121.6187 | 106.9153 | 106.3751
746.5312 | 121.7102 | -121.4813 | 0.17853 | 0.005951 | 6.962 | 0.066541 | 0.065569 | -0.0054132 | -0.0048321 | -0.0036486 | 0.0025025 | 0.0054368 | 0.066943 | 0.059347 | -0.0034223 | 0.020617 | -0.002651 | -14.6896 | -0.064087 | -121.4722 | 0.10529 | -120.7947 | -121.4951 | -121.637 | -15.2573 | 0.050354 | -121.6644 | 0.09613 | -121.1334 | -121.2936 | -121.5454 | 0.009155 | -0.24261 | -0.073242 | 0.68664 | -0.15564 | -0.013733 | -0.16479 | -0.022888 | -0.18311 | -0.12817 | -0.082398 | 0.3479 | -0.064087 | 0.18768 | 0.11902 | 0.37079 | 0.67749 | 121.5775 | 0.53101 | 121.7606 | 121.4081 | 121.7148 | 121.4172 | 121.5317 | -121.6507 | -121.843 | 121.5866 | 121.5775 | 106.7917 | 106.2241
748.2031 | 121.7377 | -121.4859 | 0.1236 | 0.005951 | 6.9622 | 0.068678 | 0.066638 | -7.2628e-05 | -0.0065411 | -0.0030078 | -0.00054933 | 0.005864 | 0.069507 | 0.058492 | -0.0081219 | 0.0048086 | -0.013973 | -14.6439 | -0.11902 | -121.4951 | 0.10986 | -120.7855 | -121.5225 | -121.6736 | -15.2298 | -0.022888 | -121.6095 | 0.086975 | -121.1288 | -121.3074 | -121.5408 | -0.009155 | -0.24261 | -0.013733 | 0.70038 | -0.18768 | -0.036621 | -0.17853 | -0.027466 | -0.1236 | -0.14648 | -0.036621 | 0.35706 | -0.054932 | 0.17853 | 0.068664 | 0.30212 | 0.70953 | 121.6049 | 0.48065 | 121.6965 | 121.376 | 121.5866 | 121.3669 | 121.463 | -121.6187 | -121.7331 | 121.5958 | 121.5729 | 106.842 | 106.2561
749.9375 | 121.7743 | -121.4859 | 0.10529 | 0.005951 | 6.9609 | 0.063978 | 0.064929 | -0.004345 | -0.0039777 | 0.00083737 | 0.0025025 | 0.0030868 | 0.067584 | 0.056142 | -0.0040631 | 0.019762 | -0.00030119 | -14.7308 | -0.10071 | -121.4905 | 0.09613 | -120.7855 | -121.4951 | -121.6507 | -12.5381 | 0.34332 | -121.1975 | 0.054932 | -121.1472 | -121.3303 | -121.6232 | -0.004578 | -0.20599 | -0.009156 | 0.70038 | -0.16479 | -0.009155 | -0.16022 | -0.004577 | 0.28839 | 0.23804 | -0.050354 | 0.33875 | -0.13733 | 0.15564 | -0.42572 | -0.13275 | 0.70496 | 121.5866 | 0.050354 | 121.2524 | 121.3898 | 121.5408 | 121.3852 | 121.8292 | -121.5958 | -121.3028 | 121.582 | 121.5408 | 106.7551 | 108.9478
751.9062 | 121.6919 | -120.5933 | 0.92468 | 0.005951 | 6.963 | 0.06761 | 0.064929 | 0.003559 | -0.0041913 | 0.00041017 | -0.00054933 | 0.0028732 | 0.068011 | 0.056356 | -0.0034223 | 0.020189 | -0.00072839 | -14.5111 | 0.70953 | -120.5795 | 0.91553 | -119.8791 | -120.6207 | -120.7581 | -15.1199 | 0.79193 | -120.6619 | 0.84686 | -120.2499 | -120.4056 | -120.6162 | 0.013733 | -0.21515 | -0.009156 | 0.71411 | -0.16479 | -0.027466 | -0.17853 | -0.041199 | -0.068664 | -0.13275 | -0.07782 | 0.34332 | -0.022888 | 0.18768 | 0.045776 | 0.25635 | 0.70038 | 121.4951 | 0.41199 | 121.5088 | 121.2891 | 121.4539 | 121.3028 | 121.3852 | -121.5042 | -121.5866 | 121.5088 | 121.4401 | 106.0822 | 105.4733
755.4531 | 121.463 | -119.7418 | 1.4648 | 0.005951 | 6.9603 | 0.06825 | 0.065142 | -0.0013544 | -0.0041913 | -1.7026e-05 | 0.0025025 | 0.0009506 | 0.067798 | 0.065755 | -0.0025677 | 0.023821 | -0.0017966 | -14.3967 | 1.2543 | -119.7052 | 1.5427 | -118.9728 | -119.7052 | -119.8196 | -14.859 | 1.3229 | -119.8288 | 1.5518 | -119.2886 | -119.426 | -119.6777 | 0.036621 | -0.21057 | 0.07782 | 0.76904 | -0.07782 | 0.036621 | -0.11444 | 0 | -0.086975 | -0.14191 | 0.086975 | 0.45319 | 0.064087 | 0.31586 | 0.15106 | 0.40283 | 0.73242 | 121.2479 | 0.54016 | 121.3806 | 120.9595 | 121.1517 | 120.9961 | 121.0648 | -121.17 | -121.2936 | 121.2845 | 121.2936 | 105.3452 | 104.8828
759.0781 | 121.2982 | -119.7052 | 1.4557 | -0.0016785 | 6.962 | 0.066969 | 0.065569 | -0.0019952 | -0.0063275 | -0.00087163 | -0.00054933 | 0.0011642 | 0.06673 | 0.055288 | -0.0029949 | 0.022326 | -0.0037192 | -14.3829 | 1.2497 | -119.7006 | 1.4282 | -119.0552 | -119.7418 | -119.8837 | -15.0101 | 1.3641 | -119.7876 | 1.4008 | -119.3939 | -119.545 | -119.7464 | 0.004577 | -0.20599 | -0.027465 | 0.65002 | -0.17853 | -0.036621 | -0.18311 | -0.041198 | -0.082398 | -0.091552 | -0.054931 | 0.31128 | -0.041199 | 0.16022 | 0.041199 | 0.24262 | 0.64545 | 121.1288 | 0.39368 | 121.1884 | 120.9503 | 121.1517 | 120.9549 | 121.0693 | -121.1563 | -121.2433 | 121.1334 | 121.106 | 105.3223 | 104.6951
764.7344 | 121.7377 | -1.3138 | 120.1126 | 0.036468 | 6.9652 | 0.070173 | 0.074114 | -0.0034906 | -0.0052595 | 0.00062377 | 0.0086061 | 0.0056504 | 0.065875 | 0.059774 | 0.0014911 | 0.022539 | -0.001583 | 7.2556 | 120.0989 | -1.2772 | 120.3644 | -1.0666 | -1.181 | -1.2085 | 8.1207 | 119.9982 | -1.3275 | 120.1492 | -1.1673 | -1.2039 | -1.1398 | 0.036621 | -0.013733 | 0.25177 | 0.24719 | 0.10529 | 0.13275 | 0.068665 | 0.096131 | -0.013733 | -0.11444 | 0.036621 | 0.14648 | 0.17395 | 0.10986 | 0.18768 | 0.1236 | 0.21057 | 121.6415 | 0.16022 | 121.4767 | 121.376 | 121.3257 | 121.4127 | 121.312 | -121.3898 | -121.4401 | 121.6782 | 121.463 | 8.5693 | 9.4345
766.4844 | 121.6965 | -0.5127 | 120.8679 | 0.005951 | 6.9618 | 0.067823 | 0.063006 | 0.0022772 | -0.0073957 | -0.00044443 | -0.092102 | -0.0001174 | 0.066089 | 0.065328 | -0.0055585 | 0.021471 | -0.001583 | 7.5302 | 108.5403 | -0.29755 | 120.7947 | -0.33875 | -0.46234 | -0.55389 | 8.345 | 112.3764 | -0.45319 | 120.5704 | -0.41657 | -0.50354 | -0.4715 | 0.21515 | -12.3276 | -0.073242 | 0.17395 | -0.041199 | 0.050354 | -0.25635 | -0.1648 | 0.059509 | -8.4915 | -0.29755 | 0.09613 | 0.041198 | 0.009155 | -0.018311 | -0.050354 | -0.041199 | 121.0922 | 0.036621 | 121.0236 | 108.8379 | 112.8296 | 109.053 | 112.8891 | -121.1655 | -121.3211 | 121.3074 | 121.0831 | 8.0429 | 8.8577
768.1719 | 121.6232 | -0.22888 | 119.4626 | 0.005951 | 6.965 | 0.058424 | -0.018384 | 0.011463 | 0.057546 | 0.052748 | 0.048279 | 0.029576 | 0.01781 | 0.067464 | 0.035243 | 0.045611 | 0.031529 | 0.21057 | 120.8221 | 0.28381 | 90.6647 | 0.07782 | 0.082397 | 0.082397 | 8.6014 | 91.6031 | 0.027466 | 119.2017 | 0.082397 | 0.091553 | 0.091553 | 0.5127 | 1.3596 | -28.7979 | 0.3067 | 0.31128 | 0.31128 | -0.20142 | -0.20142 | 0.25635 | -27.8595 | -0.26093 | 0.31128 | 0.32044 | 0.32044 | 0.064087 | 0.064087 | -0.20599 | 90.3809 | 0.054931 | 119.1742 | 120.5383 | 91.5756 | 121.051 | 91.832 | -119.1788 | -119.4351 | 90.8936 | 119.4305 | 0.43945 | 8.8303
769.9062 | 121.7468 | -0.59052 | 120.5795 | 0.044098 | 6.9609 | 0.067182 | 0.047625 | -0.01994 | -0.0041913 | -0.0081348 | 0.045227 | -0.000972 | 0.060107 | 0.068532 | -0.019658 | 0.0058768 | -0.011196 | 7.3746 | 121.0648 | -0.054932 | 105.1483 | -0.13733 | 0.091553 | 0.091553 | 8.2809 | 107.7209 | -0.045776 | 119.6548 | -1.973 | 0.07782 | 0.091553 | 0.53558 | 0.48523 | -15.4312 | 0.45319 | 0.68207 | 0.68207 | 0.14649 | 0.14649 | 0.54474 | -12.8586 | -0.92468 | -1.3824 | 0.68207 | 0.66834 | 0.13733 | 0.1236 | -0.082397 | 105.2032 | -1.9272 | 119.7006 | 121.1197 | 107.7667 | 121.6553 | 108.3115 | -120.6345 | -120.6253 | 105.7388 | 120.2454 | 7.9651 | 8.8715
771.6406 | 121.6324 | -0.29755 | 120.7169 | 0.01358 | 6.9607 | 0.066541 | 0.061938 | 0.00099557 | -0.0044049 | -0.00065803 | -0.18976 | 0.0022324 | 0.06673 | 0.067251 | -0.0064129 | 0.021258 | -0.0039328 | 7.3196 | 103.9627 | -0.21515 | 120.575 | -0.35706 | -0.48981 | -0.49896 | 8.1619 | 105.8853 | -0.21057 | 120.5978 | -0.46234 | -0.58136 | -0.46234 | 0.082397 | -16.7541 | -0.14191 | -0.05951 | -0.20142 | -0.19226 | -0.28381 | -0.27466 | 0.086975 | -14.8315 | -0.11902 | -0.1648 | -0.1648 | -0.28381 | -0.25177 | -0.37079 | -0.14191 | 120.7901 | -0.25177 | 120.8084 | 104.1779 | 106.0959 | 104.2603 | 106.1829 | -120.932 | -120.9274 | 120.8725 | 120.8954 | 7.6172 | 8.4595
773.375 | 121.7743 | -0.1831 | 121.3028 | -0.009308 | 6.962 | 0.068037 | 0.062792 | -0.0030634 | -0.0076093 | 0.001051 | -0.082947 | 0.0009506 | 0.068225 | 0.064687 | -0.0057721 | 0.021044 | -0.002651 | 7.4936 | 120.6207 | -0.004578 | 121.4127 | 0.027466 | -0.091553 | -0.22888 | 8.4503 | 120.2866 | -0.045776 | 121.2708 | -0.022888 | -0.041199 | -0.045776 | 0.17853 | -0.68207 | 0.10986 | 0.21057 | -0.045777 | 0.091552 | -0.2243 | -0.086975 | 0.13733 | -1.0162 | -0.032043 | 0.16022 | 0.13733 | 0.14191 | 0 | 0.004577 | 0.032044 | 121.4172 | 0.022888 | 121.3165 | 120.6253 | 120.3323 | 120.8038 | 120.4697 | -121.3074 | -121.3486 | 121.5958 | 121.4539 | 7.6767 | 8.6334
775.0469 | 121.7102 | -0.18768 | 121.3531 | 0.028839 | 6.963 | 0.06761 | 0.063647 | 0.00035457 | -0.0048321 | -0.001726 | -0.055481 | 0.0013778 | 0.068866 | 0.059133 | -0.0038495 | 0.021685 | -0.0022238 | 7.4799 | 121.225 | -0.12817 | 121.4676 | 0.013733 | -0.10071 | -0.23346 | 8.3542 | 120.7077 | -0.15106 | 121.2479 | -0.07782 | -0.10071 | -0.050354 | 0.059509 | -0.12817 | 0.11444 | 0.20142 | -0.045776 | 0.086975 | -0.10528 | 0.027466 | 0.036621 | -0.64545 | -0.10528 | 0.10986 | 0.13733 | 0.086975 | 0.10071 | 0.050354 | 0.14191 | 121.5958 | 0.073242 | 121.3989 | 121.3531 | 120.8588 | 121.4127 | 120.8954 | -121.4813 | -121.5042 | 121.6553 | 121.4355 | 7.6675 | 8.5419
776.7969 | 121.7331 | -0.1831 | 121.2891 | 0.01358 | 6.9622 | 0.065687 | 0.064929 | 0.0016364 | -0.0052595 | -0.00023063 | -0.095154 | 0.002446 | 0.068438 | 0.063405 | -0.0044903 | 0.022753 | 0.0014078 | 7.4844 | 120.8221 | -0.082397 | 121.4355 | 0.004578 | -0.1236 | -0.2655 | 8.3633 | 120.488 | -0.11444 | 121.2616 | -0.022888 | -0.050354 | -0.050354 | 0.10071 | -0.46692 | 0.14648 | 0.18768 | -0.082398 | 0.059509 | -0.18311 | -0.041199 | 0.068664 | -0.80109 | -0.027465 | 0.16022 | 0.13275 | 0.13275 | 0.064087 | 0.064087 | 0.086975 | 121.5179 | 0.091553 | 121.376 | 120.9045 | 120.6024 | 121.0052 | 120.6711 | -121.3715 | -121.4035 | 121.6187 | 121.4447 | 7.6675 | 8.5464
778.4688 | 121.5317 | -121.0556 | 0.21515 | -0.0016785 | 6.9586 | 0.068037 | 0.070056 | 0.0033454 | -0.0071821 | 0.001692 | 0.020813 | 0.0009506 | 0.070361 | 0.059774 | -0.0040631 | 0.021471 | 0.0011942 | -17.9626 | 0.032043 | -121.0968 | 0.17395 | -120.2087 | -115.654 | -112.8296 | -18.631 | 0.12817 | -121.2753 | 0.13733 | -120.6711 | -121.0281 | -112.2711 | -0.041199 | -0.18311 | -0.041199 | 0.84686 | 8.226 | 5.4016 | 8.2672 | 5.4428 | -0.21973 | -0.086975 | -0.07782 | 0.38452 | 8.7845 | 0.027466 | 9.0042 | 0.24719 | 0.88806 | 121.2708 | 0.60425 | 121.4127 | 121.1288 | 121.4035 | 121.0876 | 121.1838 | -121.312 | -121.4905 | 121.2296 | 121.1929 | 103.093 | 102.4246
780.1406 | 121.5591 | -121.1975 | 0.19226 | -0.0016785 | 6.9654 | 0.068678 | 0.067065 | -0.0056268 | -0.0080365 | -0.0036486 | -0.092102 | -0.012721 | 0.06673 | 0.058065 | -0.0034223 | 0.01784 | -0.002651 | -18.4387 | -0.004578 | -121.1792 | 0.10071 | -120.6757 | -108.9844 | -104.425 | -19.1299 | 0.050354 | -121.312 | 0.091553 | -120.9137 | -120.7443 | -113.7314 | 0.018311 | -0.19684 | -0.091553 | 0.52185 | 16.7725 | 12.2131 | 16.7541 | 12.1948 | -0.11444 | -0.14191 | -0.10071 | 0.28381 | 7.4661 | 0.45319 | 7.5806 | 0.56763 | 0.50354 | 121.2799 | 0.39825 | 121.4035 | 121.1746 | 121.3623 | 121.1929 | 121.2479 | -121.3715 | -121.5042 | 121.2982 | 121.2891 | 102.7588 | 102.0676
781.8906 | 121.701 | -121.2662 | 0.10986 | -0.009308 | 6.9607 | 0.068464 | 0.067492 | 0.0033454 | -0.0026959 | 0.0014784 | 0.014709 | 0.0011642 | 0.068225 | 0.062551 | -0.0021405 | 0.022967 | 0.0014078 | -18.6401 | -0.091553 | -121.1792 | 0.23804 | -120.3278 | -120.9 | -120.9595 | -19.1986 | 0.013733 | -121.3943 | 0.21515 | -120.813 | -120.9366 | -121.0648 | 0.086975 | -0.20142 | 0.12817 | 0.93842 | 0.3067 | 0.36621 | 0.21973 | 0.27924 | -0.12817 | -0.09613 | 0.10529 | 0.45319 | 0.20142 | 0.32959 | 0.32959 | 0.45776 | 0.85144 | 121.4172 | 0.58136 | 121.6095 | 121.0876 | 121.4081 | 121.1746 | 121.2799 | -121.2891 | -121.5042 | 121.5042 | 121.4813 | 102.626 | 102.0676
783.6406 | 121.7239 | -121.3394 | 0.086975 | 0.005951 | 6.9603 | 0.06825 | 0.063647 | -0.0017816 | -0.0046185 | 0.00083737 | 0.0025025 | 0.0009506 | 0.066516 | 0.066823 | -0.0027813 | 0.024035 | 0.00098061 | -18.8278 | -0.10071 | -121.2662 | 0.15106 | -120.3781 | -120.9824 | -120.9869 | -19.368 | -0.018311 | -121.3852 | 0.1831 | -120.8817 | -120.9961 | -121.0556 | 0.073243 | -0.18768 | 0.064087 | 0.9613 | 0.35248 | 0.35706 | 0.27924 | 0.28381 | -0.045776 | -0.10529 | 0.09613 | 0.45776 | 0.28381 | 0.34332 | 0.32959 | 0.3891 | 0.88806 | 121.4172 | 0.50354 | 121.5683 | 121.1655 | 121.3669 | 121.2387 | 121.3211 | -121.3531 | -121.4722 | 121.4905 | 121.5225 | 102.5116 | 101.9714
785.375 | 121.5958 | -121.3989 | 0.11902 | -0.0016785 | 6.9641 | 0.066541 | 0.06621 | 0.00035457 | -0.0056867 | 0.00041017 | -0.055481 | -0.0090896 | 0.065875 | 0.051229 | -0.0049175 | 0.020617 | -0.002651 | -18.9285 | -0.11444 | -121.3348 | 0.073242 | -120.2499 | -121.3577 | -110.9482 | -19.5786 | -0.018311 | -121.4493 | 0.045776 | -121.0052 | -120.9915 | -121.1243 | 0.064087 | -0.23346 | -0.045777 | 1.149 | 10.4507 | 0.041199 | 10.3867 | -0.022888 | -0.050354 | -0.13733 | -0.073243 | 0.39368 | 0.27466 | 0.40741 | 0.32501 | 0.45776 | 1.0849 | 121.4081 | 0.44403 | 121.4951 | 121.2204 | 121.431 | 121.2845 | 121.3806 | -121.4539 | -121.5683 | 121.4722 | 121.4447 | 102.4704 | 101.8204
787.0469 | 121.6782 | -121.3989 | 0.10071 | -0.0016785 | 6.9607 | 0.069319 | 0.061938 | -0.0024224 | -0.0067547 | -0.00065803 | 0.0055543 | -0.0011856 | 0.064593 | 0.058065 | -0.0079083 | 0.024035 | 0.00076681 | -19.0018 | -0.15106 | -121.3303 | 0.15106 | -120.5566 | -121.1334 | -121.1609 | -19.6106 | -0.027466 | -121.4401 | 0.10071 | -120.9412 | -121.0876 | -121.3028 | 0.068665 | -0.25177 | 0.050354 | 0.84229 | 0.23804 | 0.2655 | 0.16937 | 0.19684 | -0.041199 | -0.12817 | 0 | 0.45776 | 0.096131 | 0.31128 | 0.13733 | 0.35248 | 0.77362 | 121.4813 | 0.49896 | 121.5408 | 121.1792 | 121.4127 | 121.2479 | 121.3715 | -121.431 | -121.5408 | 121.55 | 121.4996 | 102.3972 | 101.7883
788.7812 | 121.6415 | -121.4264 | 0.10986 | 0.059356 | 6.9635 | 0.066328 | 0.06621 | -0.00092703 | -0.0065411 | -0.00044443 | 0.020813 | 0.0015914 | 0.066943 | 0.06191 | -0.0087629 | 0.021258 | -0.0056418 | -19.1116 | -0.073242 | -121.3852 | 0.054932 | -120.5292 | -121.0327 | -121.1975 | -19.7845 | 0.018311 | -121.5134 | 0.032043 | -121.0144 | -121.1609 | -121.1838 | 0.041199 | -0.18311 | -0.054931 | 0.89722 | 0.22888 | 0.39368 | 0.18768 | 0.35248 | -0.086975 | -0.091552 | -0.07782 | 0.41199 | 0.24262 | 0.2655 | 0.32959 | 0.35248 | 0.85602 | 121.4401 | 0.49896 | 121.5454 | 121.312 | 121.5317 | 121.3532 | 121.4447 | -121.4951 | -121.6232 | 121.4813 | 121.4584 | 102.3148 | 101.6418
790.5312 | 121.7514 | -121.3669 | 0.086975 | -0.0016785 | 6.9635 | 0.068678 | 0.065142 | 0.0033454 | -0.0050457 | -0.00023063 | -0.00054933 | 0.0011642 | 0.06737 | 0.063833 | -0.00021791 | 0.021471 | -0.0045736 | -19.1574 | -0.13733 | -121.3165 | 0.15564 | -120.5795 | -121.2433 | -121.2112 | -19.7571 | -0.050354 | -121.4355 | 0.16937 | -120.9183 | -121.0831 | -121.3303 | 0.050354 | -0.2243 | 0.068665 | 0.78735 | 0.15564 | 0.1236 | 0.10529 | 0.073242 | -0.068665 | -0.13733 | 0.082398 | 0.44861 | 0.036621 | 0.28381 | 0.10529 | 0.35248 | 0.737 | 121.4722 | 0.51727 | 121.6049 | 121.1792 | 121.3852 | 121.2296 | 121.3165 | -121.4035 | -121.5225 | 121.5225 | 121.5363 | 102.2095 | 101.6098
792.2031 | 121.6187 | -121.4493 | 0.12817 | -0.0016785 | 6.963 | 0.06825 | 0.066638 | 0.0044134 | -0.0067547 | -0.00065803 | 0.0025025 | 0.0015914 | 0.068225 | 0.056783 | -0.0040631 | 0.021044 | -0.003292 | -19.1986 | -0.10529 | -121.3623 | 0.050354 | -120.5475 | -121.0693 | -121.4767 | -19.9402 | 0.013733 | -121.4722 | 0.022888 | -121.0556 | -121.2204 | -121.3028 | 0.086975 | -0.23346 | -0.07782 | 0.9018 | -0.027466 | 0.37994 | -0.11444 | 0.29297 | -0.022888 | -0.11444 | -0.10529 | 0.39368 | 0.14648 | 0.22888 | 0.16937 | 0.25177 | 0.81482 | 121.4127 | 0.41656 | 121.4951 | 121.257 | 121.4859 | 121.344 | 121.463 | -121.4905 | -121.6003 | 121.4996 | 121.4722 | 102.2507 | 101.5091
793.9375 | 121.701 | -121.4081 | 0.091553 | 0.02121 | 6.9622 | 0.068891 | 0.063006 | -0.0041314 | -0.0054731 | -0.0015124 | 0.011658 | 0.0015914 | 0.066516 | 0.063833 | -0.0049175 | 0.02318 | -8.7586e-05 | -19.2673 | -0.13275 | -121.3531 | 0.10071 | -120.6482 | -121.3623 | -121.4905 | -19.986 | -0.022888 | -121.4722 | 0.082397 | -120.9915 | -121.1197 | -121.4035 | 0.054932 | -0.2243 | 0.009155 | 0.75989 | -0.082398 | 0.045776 | -0.13733 | -0.009156 | -0.064087 | -0.11444 | -0.009156 | 0.41656 | 0.004578 | 0.28839 | 0.068665 | 0.35248 | 0.70496 | 121.4539 | 0.48065 | 121.5546 | 121.2204 | 121.4493 | 121.2753 | 121.3852 | -121.4447 | -121.5637 | 121.5088 | 121.4905 | 102.1408 | 101.4221
795.6719 | 121.669 | -121.4584 | 0.10986 | 0.005951 | 6.9609 | 0.068037 | 0.064501 | -0.0011408 | -0.0059003 | -0.00044443 | 0.0025025 | 0.0028732 | 0.066302 | 0.053152 | -0.0081219 | 0.021898 | -0.0022238 | -19.2078 | -0.14191 | -121.376 | 0.12817 | -120.6116 | -121.3303 | -121.3577 | -19.9768 | -0.018311 | -121.4813 | 0.041199 | -120.9915 | -121.1426 | -121.4264 | 0.082397 | -0.25177 | 0.018311 | 0.84686 | 0.10071 | 0.12817 | 0.018311 | 0.045777 | -0.022888 | -0.12817 | -0.068664 | 0.46692 | 0.032043 | 0.31586 | 0.054931 | 0.33875 | 0.76447 | 121.5042 | 0.48981 | 121.5225 | 121.2341 | 121.463 | 121.3165 | 121.4401 | -121.4859 | -121.5912 | 121.5866 | 121.4996 | 102.2507 | 101.4816
797.3438 | 121.7148 | -121.4218 | 0.086975 | 0.005951 | 6.962 | 0.066541 | 0.064715 | -0.0024224 | -0.0054731 | 0.001051 | 0.0025025 | -0.0028946 | 0.069079 | 0.067037 | -0.0049175 | 0.021471 | -0.00030119 | -19.3176 | -0.1236 | -121.3623 | 0.10986 | -120.6573 | -121.376 | -121.5134 | -20.0638 | -0.036621 | -121.4813 | 0.073242 | -120.9778 | -121.1105 | -121.4035 | 0.059509 | -0.21057 | 0.022888 | 0.76447 | -0.091553 | 0.045776 | -0.15106 | -0.013733 | -0.059509 | -0.1236 | -0.013733 | 0.44403 | 0.018311 | 0.31128 | 0.07782 | 0.37079 | 0.70496 | 121.4722 | 0.50354 | 121.5546 | 121.2387 | 121.4447 | 121.2982 | 121.3852 | -121.4493 | -121.5683 | 121.5317 | 121.4951 | 102.1042 | 101.358
799.0781 | 121.6141 | -121.463 | 0.11902 | -0.0016785 | 6.9615 | 0.067182 | 0.065997 | 0.0014228 | -0.0050457 | -0.00087163 | -0.00054933 | 0.0033004 | 0.065234 | 0.055929 | -0.0034223 | 0.019549 | -0.0028646 | -19.3314 | -0.10071 | -121.4218 | 0.041199 | -120.7626 | -121.344 | -121.2982 | -20.2286 | 0.004578 | -121.5134 | -0.013733 | -121.1014 | -121.2524 | -121.4813 | 0.041199 | -0.21973 | -0.07782 | 0.70038 | 0.16479 | 0.11902 | 0.1236 | 0.07782 | -0.050354 | -0.11444 | -0.13275 | 0.36163 | -0.01831 | 0.21057 | 0.032044 | 0.26093 | 0.65918 | 121.463 | 0.41199 | 121.4996 | 121.3211 | 121.5179 | 121.3623 | 121.4676 | -121.5408 | -121.6324 | 121.5042 | 121.4493 | 102.1317 | 101.2344
800.8281 | 121.669 | -121.4447 | 0.11444 | 0.028839 | 6.9637 | 0.068464 | 0.065783 | -0.00028623 | -0.0029095 | 0.0025464 | 0.020813 | 0.0020188 | 0.067798 | 0.064901 | -0.0083355 | 0.019549 | -8.7586e-05 | -19.3085 | -0.086975 | -121.4401 | 0.07782 | -120.726 | -121.3943 | -121.3074 | -20.1462 | 0.027466 | -121.5546 | 0.018311 | -121.0373 | -121.1746 | -121.4401 | 0.004577 | -0.20142 | -0.036621 | 0.71869 | 0.13733 | 0.050354 | 0.13275 | 0.045777 | -0.10986 | -0.086975 | -0.09613 | 0.40741 | 0.004577 | 0.27008 | 0.11444 | 0.37994 | 0.71411 | 121.5179 | 0.51727 | 121.5729 | 121.3531 | 121.582 | 121.3577 | 121.4722 | -121.5546 | -121.669 | 121.5225 | 121.463 | 102.1362 | 101.2985
802.5 | 121.6141 | -121.463 | 0.10986 | -0.009308 | 6.9618 | 0.066969 | 0.062579 | 0.00014097 | -0.0076093 | -0.00065803 | -0.00054933 | 0.0013778 | 0.06972 | 0.055074 | -0.0081219 | 0.019335 | -0.0020102 | -19.4046 | -0.10071 | -121.4172 | 0.032043 | -120.7397 | -121.4584 | -121.4722 | -20.1553 | 0.045776 | -121.5683 | 0.004578 | -121.0648 | -121.2112 | -121.4722 | 0.045777 | -0.21057 | -0.07782 | 0.72327 | -0.009155 | 0.004578 | -0.054932 | -0.041199 | -0.10528 | -0.064087 | -0.10529 | 0.39826 | -0.009155 | 0.25177 | 0.09613 | 0.35706 | 0.67749 | 121.4493 | 0.50354 | 121.5729 | 121.3165 | 121.6141 | 121.3623 | 121.5088 | -121.5271 | -121.6782 | 121.4951 | 121.4676 | 102.0584 | 101.3077
804.2344 | 121.756 | -121.3989 | 0.086975 | 0.01358 | 6.9637 | 0.066541 | 0.064501 | 0.0041998 | -0.0050457 | -0.00065803 | 0.0025025 | 0.002446 | 0.066302 | 0.060842 | -0.0010723 | 0.021471 | -0.00436 | -19.3726 | -0.15106 | -121.3806 | 0.14648 | -120.6345 | -121.3715 | -121.5225 | -20.1279 | -0.050354 | -121.4951 | 0.13733 | -120.932 | -121.1014 | -121.3623 | 0.018311 | -0.23804 | 0.059509 | 0.76447 | -0.1236 | 0.027466 | -0.14191 | 0.009155 | -0.09613 | -0.13733 | 0.050354 | 0.46692 | 0.036621 | 0.29755 | 0.13275 | 0.39368 | 0.74616 | 121.5271 | 0.56305 | 121.6324 | 121.2296 | 121.4447 | 121.2479 | 121.3486 | -121.4676 | -121.582 | 121.5454 | 121.5363 | 102.0264 | 101.2711
805.9688 | 121.6461 | -121.4767 | 0.11444 | -0.0016785 | 6.9633 | 0.068678 | 0.064074 | -0.0045586 | -0.0052595 | -0.0027942 | 0.0025025 | -0.000972 | 0.06673 | 0.064687 | -0.0091901 | 0.021471 | -0.0013694 | -19.3588 | -0.14648 | -121.4172 | 0.091553 | -120.6894 | -121.4172 | -121.5683 | -20.2377 | 0.004578 | -121.5088 | 0.004578 | -121.0602 | -121.2067 | -121.4767 | 0.05951 | -0.26093 | -0.022888 | 0.78735 | -0.091552 | 0.05951 | -0.15106 | 0 | -0.032043 | -0.10986 | -0.10986 | 0.41657 | 0 | 0.27008 | 0.032043 | 0.30212 | 0.72784 | 121.5088 | 0.44861 | 121.5134 | 121.2708 | 121.5134 | 121.3303 | 121.4813 | -121.5317 | -121.6232 | 121.5683 | 121.4813 | 102.1179 | 101.239
807.7031 | 121.7148 | -121.431 | 0.09613 | 0.028839 | 6.9633 | 0.070387 | 0.068133 | -0.0017816 | -0.0031231 | 0.00041017 | 0.011658 | 0.0011642 | 0.067157 | 0.060842 | -0.0051313 | 0.022112 | 0.00055321 | -19.368 | -0.13275 | -121.3715 | 0.16022 | -120.607 | -121.376 | -121.5088 | -20.1324 | -0.009155 | -121.5088 | 0.10529 | -121.0007 | -121.1426 | -121.4218 | 0.059509 | -0.22888 | 0.064087 | 0.82397 | -0.07782 | 0.054931 | -0.13733 | -0.004578 | -0.07782 | -0.10528 | 0.009156 | 0.4303 | 0.009155 | 0.28839 | 0.086975 | 0.36621 | 0.76447 | 121.5317 | 0.50812 | 121.6141 | 121.2387 | 121.4996 | 121.2982 | 121.4218 | -121.4676 | -121.6049 | 121.5912 | 121.5363 | 102.063 | 101.2985
809.4375 | 121.7239 | -121.4355 | 0.086975 | 0.028839 | 6.9637 | 0.070173 | 0.064501 | 0.00035457 | -0.0046185 | -0.00044443 | 0.014709 | 0.0003098 | 0.066943 | 0.0696 | -0.0053449 | 0.02318 | -0.00436 | -19.4046 | -0.14648 | -121.3898 | 0.17853 | -120.5887 | -121.3531 | -121.4813 | -20.1736 | -0.013733 | -121.5271 | 0.11444 | -120.9915 | -121.1426 | -121.4218 | 0.045776 | -0.23346 | 0.091553 | 0.84686 | -0.045776 | 0.082398 | -0.091552 | 0.036622 | -0.091553 | -0.10071 | 0.027466 | 0.44403 | 0.013733 | 0.29297 | 0.10529 | 0.38452 | 0.80109 | 121.5683 | 0.53558 | 121.6415 | 121.2433 | 121.5134 | 121.2891 | 121.4218 | -121.4767 | -121.6141 | 121.6141 | 121.55 | 102.0309 | 101.2619
811.1094 | 121.7148 | -121.4355 | 0.10071 | 0.028839 | 6.9633 | 0.06761 | 0.064929 | -0.00071343 | -0.0026959 | -0.00087163 | 0.014709 | 0.0015914 | 0.06737 | 0.066823 | -0.0042767 | 0.022753 | 0.00012601 | -19.4641 | -0.12817 | -121.4081 | 0.12817 | -120.6528 | -121.4035 | -121.5134 | -20.2515 | -0.013733 | -121.5042 | 0.073242 | -121.0327 | -121.1563 | -121.4264 | 0.027466 | -0.22888 | 0.027466 | 0.78278 | -0.07782 | 0.032044 | -0.10529 | 0.004578 | -0.068664 | -0.11444 | -0.027466 | 0.40283 | 0.009155 | 0.27924 | 0.077819 | 0.3479 | 0.75531 | 121.5363 | 0.4715 | 121.5775 | 121.2799 | 121.4905 | 121.3074 | 121.4218 | -121.5088 | -121.6049 | 121.5637 | 121.5088 | 101.9714 | 101.1841
812.8438 | 121.6507 | -121.4447 | 0.11902 | -0.0016785 | 6.9611 | 0.068891 | 0.064501 | -0.0037042 | -0.0056867 | -0.00044443 | 0.014709 | 0.0020188 | 0.068652 | 0.059133 | -0.0070539 | 0.019762 | -0.0030784 | -19.455 | -0.10071 | -121.4493 | 0.041199 | -120.7581 | -121.4584 | -121.6003 | -20.3018 | 0.032043 | -121.582 | -0.004578 | -121.1014 | -121.2296 | -121.4859 | -0.004578 | -0.21973 | -0.07782 | 0.68665 | -0.15564 | -0.013733 | -0.15106 | -0.009155 | -0.13733 | -0.086976 | -0.1236 | 0.34332 | -0.041199 | 0.21515 | 0.09613 | 0.35248 | 0.69122 | 121.4905 | 0.48065 | 121.5775 | 121.3486 | 121.6141 | 121.344 | 121.4767 | -121.5683 | -121.701 | 121.4859 | 121.4401 | 101.9897 | 101.1429
814.5156 | 121.7789 | -121.4218 | 0.091553 | -0.0016785 | 6.9601 | 0.067182 | 0.062792 | 0.0050544 | -0.0065411 | 0.00062377 | -0.00054933 | 0.0003098 | 0.067798 | 0.06426 | -0.0055585 | 0.022326 | -0.00051479 | -19.4366 | -0.14648 | -121.4127 | 0.16022 | -120.6253 | -121.3486 | -121.4859 | -20.2057 | -0.032043 | -121.5225 | 0.12817 | -120.9457 | -121.0785 | -121.3715 | 0.009155 | -0.23804 | 0.068664 | 0.79651 | -0.064087 | 0.073242 | -0.073242 | 0.064087 | -0.10071 | -0.1236 | 0.036621 | 0.47607 | 0.050354 | 0.34332 | 0.15106 | 0.44403 | 0.78735 | 121.5729 | 0.57678 | 121.6507 | 121.2662 | 121.4905 | 121.2753 | 121.3898 | -121.5042 | -121.6141 | 121.582 | 121.55 | 101.9852 | 101.2161
816.25 | 121.6553 | -121.4996 | 0.09613 | -0.0016785 | 6.963 | 0.068037 | 0.065997 | 0.0014228 | -0.0071821 | -0.0021532 | 0.0025025 | 0.0028732 | 0.066089 | 0.055715 | -0.0051313 | 0.022326 | 0.0014078 | -19.4366 | -0.10986 | -121.4401 | 0.041199 | -120.8038 | -121.5179 | -121.6324 | -20.3934 | 0.004578 | -121.55 | 0.009155 | -121.1243 | -121.257 | -121.4859 | 0.059509 | -0.20599 | -0.054931 | 0.6958 | -0.13275 | -0.01831 | -0.19226 | -0.077819 | -0.050354 | -0.091552 | -0.086975 | 0.37537 | 0.013733 | 0.24262 | 0.064087 | 0.29297 | 0.63629 | 121.4813 | 0.42572 | 121.5591 | 121.3303 | 121.5546 | 121.3898 | 121.5042 | -121.5363 | -121.6461 | 121.5408 | 121.5088 | 102.063 | 101.1063
817.9844 | 121.7239 | -121.4447 | 0.086975 | 0.036468 | 6.9613 | 0.070814 | 0.06386 | 0.0029182 | -0.0039777 | -0.00065803 | 0.011658 | 0.0003098 | 0.066943 | 0.068105 | -0.0044903 | 0.019762 | 0.0029032 | -19.4183 | -0.13275 | -121.4264 | 0.16479 | -120.6528 | -121.4035 | -121.5317 | -20.3018 | -0.022888 | -121.5408 | 0.07782 | -121.019 | -121.17 | -121.4172 | 0.01831 | -0.21973 | 0.07782 | 0.79193 | -0.086975 | 0.041199 | -0.10528 | 0.022889 | -0.096131 | -0.10986 | -0.009155 | 0.42572 | 0.027466 | 0.27466 | 0.1236 | 0.37079 | 0.77362 | 121.5912 | 0.52185 | 121.6187 | 121.2936 | 121.5179 | 121.312 | 121.4218 | -121.5134 | -121.6278 | 121.6095 | 121.5225 | 102.0264 | 101.1429
819.7188 | 121.756 | -121.4447 | 0.07782 | 0.005951 | 6.962 | 0.06761 | 0.065356 | 0.0022772 | -0.0044049 | 0.001051 | -0.0036011 | 0.0015914 | 0.068438 | 0.058492 | -0.0047039 | 0.022326 | -0.005001 | -19.5053 | -0.11444 | -121.4447 | 0.068665 | -120.7352 | -121.4951 | -121.5912 | -20.3613 | -0.018311 | -121.5179 | 0.091553 | -121.0236 | -121.1563 | -121.4035 | 0 | -0.19226 | -0.009155 | 0.70953 | -0.14648 | -0.050354 | -0.14648 | -0.050354 | -0.073242 | -0.096131 | 0.013733 | 0.42114 | 0.041199 | 0.28839 | 0.11444 | 0.36163 | 0.70953 | 121.5134 | 0.49438 | 121.6095 | 121.3303 | 121.4996 | 121.3303 | 121.4264 | -121.5225 | -121.5958 | 121.5134 | 121.5363 | 101.9394 | 101.0834
821.3906 | 121.7743 | -121.4539 | 0.09613 | 0.005951 | 6.9622 | 0.068678 | 0.062792 | -7.2628e-05 | -0.0035505 | -0.0030078 | 0.0025025 | -0.0013992 | 0.06673 | 0.068746 | -0.0049175 | 0.022539 | -0.001583 | -19.4962 | -0.15106 | -121.4218 | 0.11444 | -120.6894 | -121.4127 | -121.5637 | -20.3522 | -0.041199 | -121.5363 | 0.091553 | -121.0052 | -121.138 | -121.4264 | 0.032043 | -0.24719 | 0.018311 | 0.76447 | -0.10986 | 0.041198 | -0.14191 | 0.009155 | -0.082398 | -0.13733 | -0.004577 | 0.44861 | 0.027465 | 0.31586 | 0.10986 | 0.39825 | 0.73242 | 121.5363 | 0.53101 | 121.6278 | 121.2708 | 121.4951 | 121.3028 | 121.4127 | -121.5179 | -121.6324 | 121.5683 | 121.5454 | 101.9577 | 101.1017
823.125 | 121.788 | -121.4493 | 0.10986 | -0.0016785 | 6.9603 | 0.070387 | 0.063433 | -0.00071343 | -0.0050457 | -0.00023063 | -0.00054933 | -0.0007584 | 0.066089 | 0.062978 | -0.0074811 | 0.019335 | -0.00051479 | -19.4641 | -0.15106 | -121.4172 | 0.17395 | -120.6207 | -121.3486 | -121.4951 | -20.2744 | -0.054932 | -121.5454 | 0.1236 | -120.9457 | -121.0922 | -121.3806 | 0.032044 | -0.26093 | 0.064087 | 0.82855 | -0.045776 | 0.10071 | -0.07782 | 0.068664 | -0.09613 | -0.16479 | 0.013733 | 0.50354 | 0.068665 | 0.35706 | 0.16479 | 0.45319 | 0.79651 | 121.5912 | 0.59967 | 121.669 | 121.2662 | 121.4905 | 121.2982 | 121.3943 | -121.5271 | -121.6553 | 121.6232 | 121.5729 | 101.9852 | 101.1749
824.7969 | 121.7377 | -121.4722 | 0.091553 | 0.036468 | 6.963 | 0.069532 | 0.064929 | -0.0017816 | -0.0054731 | -0.00044443 | 0.0086061 | 0.000737 | 0.068438 | 0.064901 | -0.0049175 | 0.022753 | -0.00030119 | -19.5053 | -0.12817 | -121.4401 | 0.14648 | -120.694 | -121.4081 | -121.55 | -20.4071 | -0.018311 | -121.5546 | 0.068665 | -121.0373 | -121.17 | -121.431 | 0.032043 | -0.21973 | 0.054931 | 0.7782 | -0.07782 | 0.064087 | -0.10986 | 0.032044 | -0.082397 | -0.10986 | -0.022888 | 0.43488 | 0.041199 | 0.30212 | 0.1236 | 0.38452 | 0.74616 | 121.5866 | 0.51727 | 121.6232 | 121.312 | 121.5363 | 121.344 | 121.4539 | -121.5317 | -121.6461 | 121.6187 | 121.5408 | 101.9669 | 101.0651
826.5469 | 121.7789 | -121.4401 | 0.082397 | -0.009308 | 6.9618 | 0.069959 | 0.064929 | -0.0013544 | -0.0048321 | 0.001692 | 0.014709 | -0.0005448 | 0.068652 | 0.062124 | -0.0032087 | 0.019976 | -0.003292 | -19.4733 | -0.1236 | -121.431 | 0.20599 | -120.6162 | -121.3806 | -121.5179 | -20.3384 | -0.009155 | -121.5134 | 0.10986 | -120.9778 | -121.1426 | -121.3852 | 0.009156 | -0.20599 | 0.1236 | 0.82397 | -0.077819 | 0.05951 | -0.086975 | 0.050354 | -0.073242 | -0.091552 | 0.027466 | 0.46234 | 0.054932 | 0.29755 | 0.12817 | 0.37079 | 0.81482 | 121.637 | 0.53558 | 121.6232 | 121.3074 | 121.5042 | 121.3165 | 121.431 | -121.5134 | -121.5958 | 121.6461 | 121.55 | 101.9669 | 101.1017
828.2969 | 121.7422 | -121.431 | 0.086975 | 0.036468 | 6.9622 | 0.069959 | 0.065569 | -7.2628e-05 | -0.0033369 | -0.0010852 | 0.017761 | 0.0026596 | 0.066943 | 0.064046 | -0.0042767 | 0.022112 | -0.00094199 | -19.4824 | -0.15106 | -121.4493 | 0.17395 | -120.6345 | -121.4035 | -121.5317 | -20.3751 | 0 | -121.5408 | 0.082397 | -121.0281 | -121.1609 | -121.4355 | -0.018311 | -0.23804 | 0.086975 | 0.79651 | -0.10071 | 0.027466 | -0.082397 | 0.045777 | -0.10986 | -0.086975 | -0.004578 | 0.40283 | -0.004578 | 0.27008 | 0.10529 | 0.37994 | 0.81482 | 121.6232 | 0.5127 | 121.6232 | 121.2982 | 121.5408 | 121.2799 | 121.431 | -121.5363 | -121.6278 | 121.6049 | 121.5134 | 101.9485 | 101.0559
830.0312 | 121.6507 | -121.4813 | 0.13275 | 0.005951 | 6.9628 | 0.06761 | 0.064501 | 0.00014097 | -0.0063275 | 0.001692 | -0.0036011 | 0.0009506 | 0.067798 | 0.054861 | -0.0091901 | 0.021258 | 0.0014078 | -19.5145 | -0.10986 | -121.4722 | 0.041199 | -120.7947 | -121.4767 | -121.6232 | -20.5032 | -0.009155 | -121.582 | -0.022888 | -121.106 | -121.2433 | -121.5042 | 0.009155 | -0.24261 | -0.091552 | 0.68664 | -0.14191 | 0.004577 | -0.15106 | -0.004578 | -0.10071 | -0.14191 | -0.15564 | 0.37537 | -0.022888 | 0.23804 | 0.07782 | 0.33875 | 0.67749 | 121.5134 | 0.47607 | 121.5591 | 121.3623 | 121.5729 | 121.3715 | 121.4722 | -121.6049 | -121.7148 | 121.5225 | 121.4584 | 101.9669 | 100.9781
831.7656 | 121.6599 | -121.4859 | 0.13733 | 0.005951 | 6.9605 | 0.069105 | 0.066851 | 0.003559 | -0.0059003 | 0.001051 | -0.00054933 | 0.0020188 | 0.066302 | 0.059987 | -0.0066265 | 0.020189 | -0.0039328 | -19.5328 | -0.1236 | -121.4813 | 0.027466 | -120.8405 | -121.5546 | -121.6827 | -20.5444 | -0.018311 | -121.5729 | 0.009155 | -121.138 | -121.2845 | -121.5042 | 0.004578 | -0.26093 | -0.10986 | 0.64545 | -0.19684 | -0.068664 | -0.20142 | -0.073242 | -0.086975 | -0.15564 | -0.12817 | 0.3479 | -0.01831 | 0.20142 | 0.068665 | 0.28839 | 0.64087 | 121.5088 | 0.43488 | 121.582 | 121.3577 | 121.5546 | 121.3623 | 121.4676 | -121.6187 | -121.7102 | 121.5134 | 121.4951 | 101.9531 | 100.9415
833.5 | 121.669 | -121.4722 | 0.11444 | -0.0016785 | 6.9656 | 0.070387 | 0.065356 | 0.003559 | -0.0054731 | 0.0012646 | 0.0025025 | 0.0030868 | 0.06737 | 0.05422 | -0.0034223 | 0.019762 | -0.0035056 | -19.4595 | -0.12817 | -121.4813 | 0.086975 | -120.7397 | -121.4767 | -121.6324 | -20.4758 | -0.013733 | -121.5546 | 0.027466 | -121.1243 | -121.257 | -121.4996 | -0.009155 | -0.24262 | -0.027466 | 0.73242 | -0.16022 | -0.004578 | -0.15106 | 0.004577 | -0.082397 | -0.12817 | -0.086975 | 0.3479 | -0.027466 | 0.21515 | 0.054931 | 0.29755 | 0.74158 | 121.5683 | 0.4303 | 121.582 | 121.3531 | 121.5408 | 121.344 | 121.4584 | -121.5958 | -121.669 | 121.5591 | 121.4996 | 102.0126 | 100.9964
835.2344 | 121.7056 | -121.4859 | 0.10986 | 0.028839 | 6.963 | 0.06825 | 0.064074 | 0.0020636 | -0.0037641 | -1.7026e-05 | 0.014709 | 0.0028732 | 0.066943 | 0.061056 | -0.0076947 | 0.022539 | -0.0030784 | -19.4595 | -0.09613 | -121.4905 | 0.07782 | -120.7443 | -121.4447 | -121.5958 | -20.4803 | 0.018311 | -121.582 | 0.027466 | -121.0693 | -121.2204 | -121.463 | -0.004578 | -0.20599 | -0.032043 | 0.74158 | -0.10986 | 0.041199 | -0.10529 | 0.045777 | -0.09613 | -0.091552 | -0.082397 | 0.41656 | 0.022888 | 0.2655 | 0.11902 | 0.36163 | 0.74615 | 121.5683 | 0.51269 | 121.6095 | 121.3943 | 121.6003 | 121.3898 | 121.5042 | -121.6003 | -121.6919 | 121.5637 | 121.5134 | 102.0264 | 101.0056
836.9062 | 121.7834 | -121.4584 | 0.10529 | 0.005951 | 6.9622 | 0.068037 | 0.063006 | -0.002636 | -0.0046185 | -0.0012988 | 0.0025025 | -0.0011856 | 0.068011 | 0.060415 | -0.0044903 | 0.021044 | -0.003292 | -19.4778 | -0.16022 | -121.431 | 0.16479 | -120.6619 | -121.3852 | -121.5271 | -20.3934 | -0.050354 | -121.5637 | 0.09613 | -120.9915 | -121.1334 | -121.4218 | 0.027466 | -0.2655 | 0.059509 | 0.79651 | -0.068665 | 0.073242 | -0.096131 | 0.045776 | -0.10529 | -0.15564 | -0.009156 | 0.46692 | 0.036621 | 0.32501 | 0.14191 | 0.4303 | 0.76904 | 121.5958 | 0.5722 | 121.6599 | 121.2708 | 121.5134 | 121.2982 | 121.4081 | -121.5363 | -121.669 | 121.6232 | 121.5546 | 101.9806 | 101.0651
838.6562 | 121.7972 | -121.4493 | 0.082397 | 0.01358 | 6.963 | 0.068678 | 0.063647 | 0.00078177 | -0.0016279 | -0.0010852 | 0.0086061 | 0.0015914 | 0.068866 | 0.067251 | -0.0051313 | 0.021685 | -0.00094199 | -19.5053 | -0.16479 | -121.4035 | 0.16479 | -120.6528 | -121.4081 | -121.5591 | -20.3888 | -0.027466 | -121.5637 | 0.13275 | -121.0144 | -121.1517 | -121.3989 | 0.045777 | -0.24719 | 0.082398 | 0.79651 | -0.10986 | 0.041199 | -0.15564 | -0.004578 | -0.11444 | -0.10986 | 0.050354 | 0.43488 | 0.050354 | 0.29755 | 0.16479 | 0.41199 | 0.75073 | 121.5683 | 0.54932 | 121.6965 | 121.2387 | 121.5363 | 121.2845 | 121.4218 | -121.4859 | -121.6461 | 121.6141 | 121.582 | 101.944 | 101.0605
840.3906 | 121.6599 | -121.4996 | 0.1236 | -0.009308 | 6.9633 | 0.068037 | 0.068133 | 0.0046272 | -0.0039777 | -0.002367 | 0.0025025 | 0.0026596 | 0.068011 | 0.067892 | -0.0042767 | 0.020403 | -0.0035056 | -19.5328 | -0.14191 | -121.4539 | 0.050354 | -120.7993 | -121.55 | -121.6507 | -20.5765 | -0.009155 | -121.582 | -0.004578 | -121.1609 | -121.2891 | -121.5225 | 0.045777 | -0.2655 | -0.073242 | 0.70038 | -0.15106 | -0.050354 | -0.19684 | -0.096131 | -0.082397 | -0.13275 | -0.12817 | 0.33875 | -0.022888 | 0.21057 | 0.059509 | 0.29297 | 0.6546 | 121.5042 | 0.42114 | 121.5775 | 121.3119 | 121.5729 | 121.3577 | 121.4905 | -121.5775 | -121.7056 | 121.55 | 121.4951 | 101.9669 | 100.9232
842.125 | 121.6873 | -121.5042 | 0.13275 | -0.0016785 | 6.9628 | 0.067396 | 0.062151 | -0.00092703 | -0.0052595 | -0.0021532 | -0.00054933 | 0.0015914 | 0.066943 | 0.055288 | -0.0085491 | 0.020617 | -0.0013694 | -19.519 | -0.13275 | -121.4493 | 0.091553 | -120.7352 | -121.4447 | -121.5958 | -20.4987 | 0.004578 | -121.5546 | -0.004578 | -121.1105 | -121.2433 | -121.5088 | 0.054931 | -0.2655 | -0.041198 | 0.76904 | -0.091553 | 0.059509 | -0.14648 | 0.004578 | -0.050354 | -0.12817 | -0.13733 | 0.39368 | -0.004578 | 0.26093 | 0.045776 | 0.31128 | 0.71411 | 121.5408 | 0.44403 | 121.55 | 121.3165 | 121.5591 | 121.3715 | 121.5088 | -121.582 | -121.6873 | 121.5958 | 121.4996 | 101.9852 | 101.0056
843.8594 | 121.8018 | -121.4676 | 0.082397 | -0.0016785 | 6.9622 | 0.068678 | 0.063647 | -0.0058404 | -0.0050457 | 0.0019056 | -0.00054933 | 0.0026596 | 0.066302 | 0.057424 | -0.0021405 | 0.022967 | -0.0011558 | -19.574 | -0.14191 | -121.4355 | 0.12817 | -120.7031 | -121.463 | -121.5683 | -20.4803 | -0.041199 | -121.5637 | 0.1236 | -121.0052 | -121.1655 | -121.3943 | 0.032043 | -0.2243 | 0.045777 | 0.76447 | -0.10071 | 0.004577 | -0.13275 | -0.027466 | -0.096131 | -0.1236 | 0.041199 | 0.46234 | 0.073242 | 0.30212 | 0.16937 | 0.39826 | 0.73242 | 121.5637 | 0.55847 | 121.6873 | 121.2936 | 121.5225 | 121.3257 | 121.4264 | -121.5179 | -121.6461 | 121.5958 | 121.5912 | 101.8936 | 100.9872
845.6094 | 121.7239 | -121.4813 | 0.11444 | 0.005951 | 6.9635 | 0.06825 | 0.061938 | -0.0022088 | -0.0065411 | -0.001726 | -0.0036011 | -0.0003312 | 0.067584 | 0.05956 | -0.0064129 | 0.020617 | -0.0035056 | -19.5053 | -0.15106 | -121.4539 | 0.15564 | -120.6757 | -121.4035 | -121.5454 | -20.4575 | -0.032043 | -121.5546 | 0.054932 | -121.0419 | -121.1746 | -121.4584 | 0.027466 | -0.2655 | 0.041199 | 0.80566 | -0.064087 | 0.07782 | -0.091553 | 0.050354 | -0.073242 | -0.14648 | -0.059509 | 0.43945 | 0.022888 | 0.3067 | 0.09613 | 0.37994 | 0.7782 | 121.6095 | 0.51269 | 121.6095 | 121.3028 | 121.5225 | 121.3303 | 121.4493 | -121.5683 | -121.669 | 121.637 | 121.5363 | 101.976 | 101.0239
847.2812 | 121.7926 | -121.4539 | 0.068665 | 0.005951 | 6.9654 | 0.070173 | 0.063433 | 0.00035457 | -0.0050457 | -0.0019396 | 0.014709 | 9.6204e-05 | 0.070575 | 0.06426 | -0.0014997 | 0.022753 | -0.0017966 | -19.5328 | -0.15564 | -121.4264 | 0.16937 | -120.6573 | -121.4218 | -121.5271 | -20.43 | -0.022888 | -121.5775 | 0.13733 | -121.0144 | -121.1563 | -121.4081 | 0.027465 | -0.22431 | 0.10071 | 0.79651 | -0.073243 | 0.032043 | -0.10071 | 0.004578 | -0.1236 | -0.091553 | 0.068664 | 0.43945 | 0.045776 | 0.29755 | 0.16937 | 0.42114 | 0.76904 | 121.5958 | 0.56305 | 121.7148 | 121.2708 | 121.5546 | 121.2982 | 121.431 | -121.4951 | -121.6461 | 121.6232 | 121.5912 | 101.9211 | 101.0239
849.0156 | 121.7194 | -121.4905 | 0.10529 | 0.01358 | 6.9665 | 0.068678 | 0.06621 | 0.00099557 | -0.0037641 | -0.002367 | 0.0086061 | 0.0039414 | 0.066943 | 0.049306 | -0.0053449 | 0.021044 | -0.003292 | -19.5099 | -0.11902 | -121.4996 | 0.11902 | -120.726 | -121.4539 | -121.5958 | -20.462 | -0.004578 | -121.5775 | 0.064087 | -121.0831 | -121.2341 | -121.4722 | -0.009155 | -0.22431 | 0.013733 | 0.76447 | -0.10529 | 0.036622 | -0.09613 | 0.045777 | -0.086975 | -0.10986 | -0.041199 | 0.40741 | 0.018311 | 0.25635 | 0.10529 | 0.34332 | 0.77362 | 121.6187 | 0.49439 | 121.6415 | 121.3806 | 121.5729 | 121.3715 | 121.4859 | -121.6049 | -121.6827 | 121.6095 | 121.5546 | 101.9806 | 101.0284
850.7656 | 121.788 | -121.463 | 0.091553 | -0.009308 | 6.9633 | 0.070387 | 0.064715 | -0.0013544 | -0.0052595 | -0.0010852 | 0.020813 | 0.000737 | 0.06972 | 0.06191 | -0.0036359 | 0.022539 | 0.00033961 | -19.519 | -0.11902 | -121.4676 | 0.18768 | -120.639 | -121.4081 | -121.5179 | -20.43 | -0.009155 | -121.5637 | 0.12817 | -121.0007 | -121.1655 | -121.4127 | -0.004577 | -0.21057 | 0.09613 | 0.82398 | -0.054931 | 0.054932 | -0.050354 | 0.059509 | -0.10071 | -0.10071 | 0.036621 | 0.46234 | 0.050354 | 0.29755 | 0.15106 | 0.39826 | 0.82855 | 121.6553 | 0.56305 | 121.6919 | 121.3486 | 121.5546 | 121.344 | 121.4539 | -121.5591 | -121.6553 | 121.6507 | 121.5912 | 101.944 | 101.033
852.5 | 121.6644 | -121.5042 | 0.10986 | -0.0016785 | 6.965 | 0.069959 | 0.066424 | -0.0019952 | -0.0044049 | 0.0012646 | -0.00054933 | 0.003514 | 0.067798 | 0.06661 | -0.0057721 | 0.02083 | 0.00012601 | -19.574 | -0.13275 | -121.4767 | 0.054932 | -120.8038 | -121.5363 | -121.6644 | -20.5856 | -0.022888 | -121.6141 | -0.004578 | -121.1609 | -121.2982 | -121.5042 | 0.027465 | -0.24261 | -0.054931 | 0.70038 | -0.16022 | -0.032044 | -0.18768 | -0.059509 | -0.10986 | -0.13275 | -0.11444 | 0.34332 | 0 | 0.20599 | 0.10986 | 0.31586 | 0.67291 | 121.5317 | 0.45319 | 121.6095 | 121.344 | 121.5912 | 121.3715 | 121.4813 | -121.5866 | -121.7239 | 121.5591 | 121.4996 | 101.9302 | 100.9186
854.1719 | 121.7148 | -121.5363 | 0.10986 | 0.028839 | 6.9648 | 0.068678 | 0.06386 | 0.0037726 | -0.0052595 | 0.0029736 | 0.0086061 | 0.0028732 | 0.070147 | 0.051656 | -0.0070539 | 0.021044 | -0.00094199 | -19.5282 | -0.091553 | -121.5134 | 0.064087 | -120.7947 | -121.4813 | -121.6324 | -20.5307 | 0.009155 | -121.6187 | 0 | -121.1151 | -121.2479 | -121.4951 | 0.022888 | -0.20142 | -0.045776 | 0.74158 | -0.09613 | 0.054932 | -0.11902 | 0.032044 | -0.082397 | -0.10071 | -0.10986 | 0.42114 | 0.041199 | 0.28839 | 0.1236 | 0.37079 | 0.71869 | 121.5775 | 0.50354 | 121.6187 | 121.4218 | 121.6278 | 121.4447 | 121.5454 | -121.6232 | -121.7285 | 121.6003 | 121.5363 | 102.0081 | 101.0056
855.9062 | 121.6827 | -121.5271 | 0.10986 | 0.005951 | 6.9613 | 0.065901 | 0.063433 | 0.0014228 | -0.0050457 | -0.00087163 | -0.00054933 | 0.0028732 | 0.068011 | 0.059774 | -0.0076947 | 0.021471 | -0.0035056 | -19.574 | -0.12817 | -121.4996 | 0.064087 | -120.7901 | -121.4767 | -121.6415 | -20.5627 | -0.004578 | -121.6049 | -0.004578 | -121.1288 | -121.2753 | -121.5317 | 0.027466 | -0.23804 | -0.045776 | 0.737 | -0.11444 | 0.050354 | -0.14191 | 0.022888 | -0.077819 | -0.11444 | -0.11444 | 0.39826 | -0.004577 | 0.25177 | 0.073242 | 0.32959 | 0.70953 | 121.5637 | 0.47607 | 121.6003 | 121.3715 | 121.6003 | 121.3989 | 121.5225 | -121.6095 | -121.7148 | 121.5912 | 121.5225 | 101.9531 | 100.9644
857.5781 | 121.8063 | -121.4859 | 0.09613 | -0.0016785 | 6.9622 | 0.06825 | 0.06386 | -7.2628e-05 | -0.0059003 | -0.001726 | 0.0025025 | 9.6204e-05 | 0.067584 | 0.064687 | -0.0049175 | 0.022112 | 0.0014078 | -19.519 | -0.14648 | -121.4355 | 0.17395 | -120.6482 | -121.3623 | -121.55 | -20.43 | -0.059509 | -121.6003 | 0.1236 | -121.0144 | -121.1197 | -121.4081 | 0.050354 | -0.24261 | 0.07782 | 0.83771 | -0.064087 | 0.1236 | -0.11444 | 0.073242 | -0.11444 | -0.15564 | 0.027466 | 0.4715 | 0.07782 | 0.36621 | 0.19226 | 0.48065 | 0.78735 | 121.6095 | 0.58594 | 121.7239 | 121.2891 | 121.5408 | 121.3394 | 121.4264 | -121.5317 | -121.6965 | 121.6599 | 121.6095 | 101.9669 | 101.0559
859.3125 | 121.7422 | -121.5134 | 0.09613 | 0.005951 | 6.9622 | 0.069959 | 0.062579 | 0.00014097 | -0.0067547 | -0.00044443 | -0.00054933 | 0.0022324 | 0.06737 | 0.060628 | -0.0036359 | 0.022326 | -0.0037192 | -19.6198 | -0.11902 | -121.4676 | 0.050354 | -120.8038 | -121.5363 | -121.6553 | -20.5856 | -0.022888 | -121.582 | 0.068665 | -121.106 | -121.2341 | -121.4722 | 0.045777 | -0.21515 | -0.045776 | 0.70953 | -0.14191 | -0.022888 | -0.18768 | -0.068665 | -0.068664 | -0.11902 | -0.027465 | 0.40741 | 0.041199 | 0.27924 | 0.10986 | 0.3479 | 0.66376 | 121.5179 | 0.47607 | 121.6507 | 121.3486 | 121.5591 | 121.3943 | 121.4905 | -121.5637 | -121.6782 | 121.5637 | 121.582 | 101.8936 | 100.9277
861 | 121.7606 | -121.4996 | 0.10529 | 0.01358 | 6.9605 | 0.067396 | 0.063647 | -0.00071343 | -0.0039777 | -0.00065803 | 0.0055543 | 0.0022324 | 0.066302 | 0.061056 | -0.0044903 | 0.022539 | -0.003292 | -19.5831 | -0.13275 | -121.4722 | 0.10529 | -120.7397 | -121.4493 | -121.5958 | -20.5673 | -0.036621 | -121.5912 | 0.064087 | -121.0831 | -121.2158 | -121.4584 | 0.027466 | -0.23804 | 0 | 0.75989 | -0.09613 | 0.050354 | -0.1236 | 0.022888 | -0.091553 | -0.14191 | -0.041199 | 0.41657 | 0.041199 | 0.28381 | 0.13275 | 0.37537 | 0.73242 | 121.5775 | 0.50812 | 121.6553 | 121.3394 | 121.5546 | 121.3669 | 121.463 | -121.5775 | -121.6965 | 121.6049 | 121.5637 | 101.9165 | 100.9323
862.7344 | 121.8109 | -121.4813 | 0.082397 | -0.009308 | 6.9628 | 0.069532 | 0.064288 | 0.00035457 | -0.0050457 | -0.00044443 | -0.0036011 | 0.0011642 | 0.068866 | 0.061056 | -0.0025677 | 0.024462 | -0.00072839 | -19.5145 | -0.16022 | -121.431 | 0.16479 | -120.6802 | -121.431 | -121.5775 | -20.4803 | -0.027466 | -121.5866 | 0.15106 | -121.0098 | -121.1609 | -121.3989 | 0.050354 | -0.24261 | 0.082398 | 0.80109 | -0.096131 | 0.050354 | -0.14648 | 0 | -0.10529 | -0.10986 | 0.068665 | 0.4715 | 0.082397 | 0.32043 | 0.18768 | 0.42572 | 0.75073 | 121.5958 | 0.57678 | 121.7377 | 121.2708 | 121.5591 | 121.3211 | 121.4539 | -121.5134 | -121.669 | 121.6461 | 121.6324 | 101.9669 | 101.001
864.4062 | 121.6644 | -121.5363 | 0.12817 | -0.009308 | 6.9648 | 0.06761 | 0.064074 | 0.0020636 | -0.0050457 | -0.00023063 | -0.00054933 | 0.002446 | 0.068866 | 0.058492 | -0.0068403 | 0.021898 | -0.0047874 | -19.5877 | -0.11902 | -121.4905 | 0.022888 | -120.8496 | -121.5683 | -121.6965 | -20.6451 | 0.009155 | -121.6095 | -0.004578 | -121.1884 | -121.3257 | -121.5271 | 0.045776 | -0.24719 | -0.10529 | 0.68665 | -0.16022 | -0.032043 | -0.20599 | -0.077819 | -0.073242 | -0.11902 | -0.13275 | 0.3479 | 0.009155 | 0.21057 | 0.082397 | 0.28381 | 0.64087 | 121.5134 | 0.42114 | 121.6049 | 121.3715 | 121.6187 | 121.4172 | 121.5454 | -121.6187 | -121.7377 | 121.5591 | 121.5317 | 101.9485 | 100.8911
866.1562 | 121.6919 | -121.5363 | 0.10529 | 0.044098 | 6.9643 | 0.069105 | 0.065356 | 0.0033454 | -0.0026959 | -0.00023063 | 0.017761 | 0.0026596 | 0.070575 | 0.063833 | -0.0074811 | 0.020403 | -0.001583 | -19.519 | -0.086975 | -121.5134 | 0.064087 | -120.8038 | -121.5042 | -121.6507 | -20.5856 | 0.013733 | -121.6278 | 0.009155 | -121.1472 | -121.2662 | -121.5179 | 0.022888 | -0.19226 | -0.041199 | 0.73242 | -0.11444 | 0.032044 | -0.13733 | 0.009156 | -0.091553 | -0.091553 | -0.096131 | 0.3891 | 0.018311 | 0.27008 | 0.10986 | 0.36163 | 0.70953 | 121.5775 | 0.48065 | 121.637 | 121.4264 | 121.6415 | 121.4493 | 121.55 | -121.6187 | -121.7331 | 121.6003 | 121.5454 | 102.0172 | 100.9506
867.8906 | 121.8246 | -121.463 | 0.086975 | -0.0016785 | 6.9639 | 0.068464 | 0.06322 | 0.0071906 | -0.0048321 | -0.00044443 | 0.017761 | 0.0018052 | 0.069079 | 0.064901 | -0.0032087 | 0.022967 | 0.0033304 | -19.5145 | -0.13733 | -121.4859 | 0.21057 | -120.6528 | -121.4127 | -121.5363 | -20.462 | -0.027466 | -121.5958 | 0.12817 | -121.0281 | -121.1655 | -121.4218 | -0.022888 | -0.2243 | 0.1236 | 0.81024 | -0.073242 | 0.050354 | -0.050354 | 0.073242 | -0.13275 | -0.11444 | 0.041199 | 0.43488 | 0.041199 | 0.29755 | 0.17395 | 0.4303 | 0.83313 | 121.6965 | 0.56763 | 121.7239 | 121.3486 | 121.5683 | 121.3257 | 121.4355 | -121.5729 | -121.6827 | 121.6736 | 121.5912 | 101.9485 | 101.001
869.5625 | 121.7789 | -121.5088 | 0.086975 | 0.036468 | 6.9652 | 0.069959 | 0.062792 | 0.00014097 | -0.0033369 | -0.00044443 | 0.011658 | 0.0015914 | 0.068225 | 0.060842 | -0.0057721 | 0.021898 | -0.0017966 | -19.5099 | -0.13733 | -121.4676 | 0.17853 | -120.6757 | -121.431 | -121.55 | -20.4803 | -0.018311 | -121.5912 | 0.11444 | -121.0693 | -121.2067 | -121.4401 | 0.041199 | -0.2243 | 0.091553 | 0.83313 | -0.041199 | 0.07782 | -0.082398 | 0.036621 | -0.082398 | -0.10529 | 0.027466 | 0.43945 | 0.068664 | 0.30212 | 0.15106 | 0.38452 | 0.79193 | 121.6461 | 0.52185 | 121.7056 | 121.3303 | 121.5729 | 121.3715 | 121.4905 | -121.5546 | -121.6782 | 121.6873 | 121.6232 | 101.9989 | 101.0284
871.3125 | 121.8201 | -121.4859 | 0.073242 | 0.01358 | 6.966 | 0.067396 | 0.063433 | 0.0012092 | -0.0063275 | -0.00087163 | -0.00054933 | 0.0003098 | 0.066943 | 0.059987 | -0.0051313 | 0.024889 | -0.00436 | -19.574 | -0.14191 | -121.4722 | 0.10986 | -120.7352 | -121.4722 | -121.6049 | -20.5261 | -0.036621 | -121.5866 | 0.13275 | -121.0373 | -121.1929 | -121.4218 | 0.013733 | -0.21515 | 0.036621 | 0.75073 | -0.11902 | 0.013733 | -0.13275 | 0 | -0.10071 | -0.10986 | 0.059509 | 0.44861 | 0.064087 | 0.29297 | 0.16479 | 0.39368 | 0.737 | 121.582 | 0.54932 | 121.7194 | 121.3303 | 121.55 | 121.344 | 121.4493 | -121.5454 | -121.6599 | 121.5958 | 121.6187 | 101.9119 | 100.9598
873.0469 | 121.7422 | -121.5271 | 0.11444 | 0.028839 | 6.9633 | 0.068678 | 0.064501 | 0.00078177 | -0.0069683 | 0.0012646 | 0.014709 | 0.0022324 | 0.070361 | 0.058706 | -0.0074811 | 0.021258 | -0.00436 | -19.5419 | -0.091553 | -121.5271 | 0.064087 | -120.8038 | -121.5042 | -121.6415 | -20.5948 | 0.013733 | -121.6599 | 0.018311 | -121.1197 | -121.2616 | -121.4859 | 0 | -0.20599 | -0.050354 | 0.72327 | -0.11444 | 0.022889 | -0.11444 | 0.022889 | -0.13275 | -0.10071 | -0.09613 | 0.40741 | 0.041199 | 0.2655 | 0.17395 | 0.39825 | 0.72327 | 121.5912 | 0.54016 | 121.6782 | 121.4355 | 121.6736 | 121.4355 | 121.5408 | -121.6415 | -121.7743 | 121.5912 | 121.5454 | 101.9852 | 100.9323
874.7812 | 121.701 | -121.5408 | 0.10529 | -0.0016785 | 6.9624 | 0.066755 | 0.064929 | -0.00071343 | -0.0050457 | -0.00065803 | -0.00054933 | 0.0039414 | 0.068225 | 0.064687 | -0.0049175 | 0.024035 | -0.002651 | -19.6014 | -0.11902 | -121.5088 | 0.022888 | -120.8496 | -121.5683 | -121.701 | -20.6543 | -0.004578 | -121.6141 | 0 | -121.1655 | -121.3165 | -121.5225 | 0.032044 | -0.22431 | -0.082398 | 0.69122 | -0.16022 | -0.027465 | -0.19226 | -0.059509 | -0.073242 | -0.10986 | -0.10529 | 0.37537 | 0.018311 | 0.22431 | 0.091553 | 0.29755 | 0.65918 | 121.5317 | 0.44861 | 121.6141 | 121.3898 | 121.6095 | 121.4218 | 121.5363 | -121.6141 | -121.7194 | 121.5637 | 121.5408 | 101.9394 | 100.8865
876.4688 | 121.8475 | -121.5088 | 0.064087 | -0.0016785 | 6.9624 | 0.06761 | 0.063647 | -0.002636 | -0.0059003 | -0.0027942 | -0.0066527 | -0.000972 | 0.067798 | 0.06426 | -0.0053449 | 0.019976 | -0.0037192 | -19.5328 | -0.16022 | -121.4722 | 0.13733 | -120.7077 | -121.431 | -121.5546 | -20.517 | -0.059509 | -121.5912 | 0.11902 | -121.0281 | -121.1563 | -121.4264 | 0.036621 | -0.2243 | 0.073242 | 0.80109 | -0.045776 | 0.07782 | -0.082397 | 0.041199 | -0.082398 | -0.1236 | 0.054932 | 0.48065 | 0.082397 | 0.35248 | 0.16479 | 0.43488 | 0.76447 | 121.6095 | 0.56305 | 121.7102 | 121.312 | 121.5317 | 121.3486 | 121.4493 | -121.5363 | -121.6553 | 121.6461 | 121.6278 | 101.976 | 100.9918
878.1406 | 121.6965 | -121.5546 | 0.11444 | -0.0016785 | 6.9607 | 0.06761 | 0.06386 | -0.00049983 | -0.0039777 | -0.00087163 | 0.0025025 | 0.002446 | 0.068225 | 0.055074 | -0.0061993 | 0.022539 | -0.001583 | -19.519 | -0.14191 | -121.4722 | 0.07782 | -120.7672 | -121.4676 | -121.637 | -20.6039 | -0.022888 | -121.5958 | 0.004578 | -121.1197 | -121.2799 | -121.5225 | 0.082397 | -0.25635 | -0.036621 | 0.78735 | -0.082398 | 0.086975 | -0.16479 | 0.004578 | -0.041199 | -0.13733 | -0.10986 | 0.43487 | 0.032043 | 0.27466 | 0.073242 | 0.31586 | 0.70496 | 121.55 | 0.47607 | 121.6003 | 121.3303 | 121.5729 | 121.4127 | 121.5317 | -121.5866 | -121.7102 | 121.6324 | 121.5591 | 102.0355 | 100.9506
879.875 | 121.7422 | -121.5317 | 0.13275 | -0.009308 | 6.9615 | 0.064619 | 0.062792 | -0.00028623 | -0.0056867 | -0.0015124 | 0.0025025 | 0.0005234 | 0.068438 | 0.063619 | -0.0089765 | 0.021471 | -0.0024374 | -19.487 | -0.16479 | -121.4676 | 0.12817 | -120.726 | -121.431 | -121.6003 | -20.5719 | -0.027466 | -121.6003 | 0.032043 | -121.1151 | -121.2296 | -121.4996 | 0.064087 | -0.29755 | -0.004577 | 0.80566 | -0.068665 | 0.10071 | -0.13275 | 0.036621 | -0.068665 | -0.16022 | -0.10071 | 0.41657 | 0.032043 | 0.30212 | 0.10071 | 0.37079 | 0.74158 | 121.5958 | 0.48523 | 121.6324 | 121.3028 | 121.5729 | 121.3669 | 121.5042 | -121.6003 | -121.7331 | 121.6599 | 121.5637 | 102.0447 | 100.9598
881.5469 | 121.6782 | -121.5454 | 0.1236 | -0.0016785 | 6.9652 | 0.066969 | 0.063647 | 0.0016364 | -0.0054731 | -0.0015124 | -0.00054933 | 0.0018052 | 0.066943 | 0.056997 | -0.0032087 | 0.021258 | -0.0030784 | -19.5786 | -0.11444 | -121.5179 | 0.022888 | -120.8725 | -121.5775 | -121.7148 | -20.6818 | 0 | -121.6141 | -0.004578 | -121.1975 | -121.3303 | -121.55 | 0.027466 | -0.23804 | -0.10071 | 0.67291 | -0.16937 | -0.032044 | -0.19684 | -0.05951 | -0.068665 | -0.1236 | -0.12817 | 0.3479 | -0.004578 | 0.21515 | 0.064087 | 0.28381 | 0.64545 | 121.5408 | 0.41657 | 121.6095 | 121.4035 | 121.6141 | 121.431 | 121.5454 | -121.6415 | -121.7377 | 121.5683 | 121.5408 | 101.9669 | 100.8636
883.2812 | 121.7331 | -121.5271 | 0.11902 | 0.036468 | 6.966 | 0.066969 | 0.063647 | 0.00056817 | -0.0050457 | 0.00062377 | 0.014709 | 0.000737 | 0.068225 | 0.054433 | -0.0061993 | 0.022539 | -0.00094199 | -19.519 | -0.07782 | -121.5454 | 0.073242 | -120.7901 | -121.4722 | -121.6232 | -20.5994 | 0.013733 | -121.6461 | 0.036621 | -121.1197 | -121.257 | -121.4767 | -0.01831 | -0.19684 | -0.045777 | 0.737 | -0.09613 | 0.054932 | -0.07782 | 0.073242 | -0.11902 | -0.10529 | -0.082398 | 0.40741 | 0.050354 | 0.27008 | 0.16937 | 0.3891 | 0.75531 | 121.6187 | 0.52643 | 121.6827 | 121.4676 | 121.6599 | 121.4493 | 121.5408 | -121.6644 | -121.7651 | 121.6003 | 121.5637 | 102.0081 | 100.9277
884.9531 | 121.701 | -121.5363 | 0.11444 | -0.0016785 | 6.962 | 0.067182 | 0.064501 | 0.0012092 | -0.0056867 | -0.0019396 | 0.0025025 | 0.002446 | 0.068438 | 0.058706 | -0.0066265 | 0.019976 | -0.0022238 | -19.6014 | -0.11444 | -121.5179 | 0.041199 | -120.8313 | -121.5271 | -121.669 | -20.6451 | -0.009155 | -121.637 | 0.004578 | -121.1746 | -121.2982 | -121.5179 | 0.018311 | -0.22888 | -0.073242 | 0.70496 | -0.13275 | 0.009155 | -0.15106 | -0.009156 | -0.10071 | -0.1236 | -0.10986 | 0.36163 | 0.018311 | 0.23804 | 0.11902 | 0.33874 | 0.68664 | 121.5591 | 0.46234 | 121.6415 | 121.4035 | 121.6278 | 121.4218 | 121.5271 | -121.6324 | -121.7514 | 121.5775 | 121.5408 | 101.9348 | 100.8911
886.7031 | 121.8521 | -121.4859 | 0.068665 | -0.009308 | 6.9603 | 0.065901 | 0.062365 | -0.00071343 | -0.0041913 | -0.00044443 | -0.00054933 | 0.000737 | 0.06673 | 0.059987 | -0.0023541 | 0.021685 | -0.0022238 | -19.5236 | -0.15106 | -121.4722 | 0.16937 | -120.6573 | -121.4081 | -121.5454 | -20.5032 | -0.036621 | -121.5866 | 0.11902 | -120.9915 | -121.1334 | -121.4035 | 0.013733 | -0.21973 | 0.10071 | 0.82855 | -0.059509 | 0.07782 | -0.073242 | 0.064087 | -0.10071 | -0.10529 | 0.050354 | 0.49438 | 0.082398 | 0.35248 | 0.18311 | 0.45319 | 0.81482 | 121.6415 | 0.59509 | 121.7056 | 121.3211 | 121.55 | 121.3348 | 121.4493 | -121.5408 | -121.6553 | 121.6553 | 121.6049 | 101.9623 | 100.9827
888.375 | 121.7377 | -121.5317 | 0.11444 | 0.028839 | 6.9658 | 0.067182 | 0.06621 | -0.003277 | -0.0046185 | -0.0015124 | 0.011658 | 0.0020188 | 0.06737 | 0.054861 | -0.0059857 | 0.022753 | -0.0011558 | -19.5053 | -0.10986 | -121.5363 | 0.082397 | -120.7993 | -121.4905 | -121.637 | -20.5811 | 0.013733 | -121.6232 | 0.041199 | -121.1014 | -121.2479 | -121.4722 | -0.004578 | -0.2243 | -0.032044 | 0.73242 | -0.10529 | 0.041198 | -0.10071 | 0.045776 | -0.091553 | -0.10071 | -0.073242 | 0.4303 | 0.059509 | 0.28381 | 0.15106 | 0.37537 | 0.737 | 121.6187 | 0.52185 | 121.6644 | 121.4264 | 121.637 | 121.4218 | 121.5454 | -121.6507 | -121.7377 | 121.6141 | 121.5729 | 102.0264 | 100.9506
890.0469 | 121.7285 | -121.5363 | 0.11902 | 0.051727 | 6.962 | 0.068464 | 0.066638 | 0.0022772 | -0.0046185 | 0.00019657 | 0.017761 | 0.0039414 | 0.06972 | 0.060415 | -0.0094037 | 0.021258 | -0.0037192 | -19.5648 | -0.07782 | -121.5317 | 0.045776 | -120.8313 | -121.4996 | -121.6461 | -20.6497 | 0.018311 | -121.6507 | 0.018311 | -121.1563 | -121.2891 | -121.5042 | 0.004578 | -0.19684 | -0.073243 | 0.70496 | -0.10986 | 0.036621 | -0.11444 | 0.032043 | -0.11444 | -0.10071 | -0.10071 | 0.37994 | 0.032044 | 0.24719 | 0.14648 | 0.36163 | 0.70038 | 121.5775 | 0.49438 | 121.669 | 121.4539 | 121.669 | 121.4584 | 121.5546 | -121.6507 | -121.7697 | 121.582 | 121.5546 | 101.9714 | 100.8865
891.7812 | 121.8338 | -121.4905 | 0.082397 | -0.009308 | 6.9611 | 0.068464 | 0.061511 | 0.00014097 | -0.0056867 | -0.001726 | -0.00054933 | -0.0003312 | 0.066943 | 0.065328 | -0.0076947 | 0.021898 | -0.00094199 | -19.5328 | -0.15106 | -121.4767 | 0.16937 | -120.6848 | -121.4127 | -121.55 | -20.517 | -0.045776 | -121.5866 | 0.14648 | -121.0144 | -121.1472 | -121.431 | 0.013733 | -0.23346 | 0.086976 | 0.80566 | -0.059509 | 0.07782 | -0.073242 | 0.064087 | -0.09613 | -0.12817 | 0.064087 | 0.47607 | 0.05951 | 0.34332 | 0.15564 | 0.43945 | 0.79193 | 121.6461 | 0.5722 | 121.7331 | 121.3257 | 121.5408 | 121.3394 | 121.4447 | -121.5591 | -121.669 | 121.6599 | 121.637 | 101.9577 | 100.9735
893.4688 | 121.7377 | -121.5179 | 0.11902 | 0.036468 | 6.9628 | 0.069746 | 0.065356 | 0.0020636 | -0.0022687 | 0.00083737 | 0.0086061 | 0.0037278 | 0.06972 | 0.062978 | -0.0068403 | 0.019549 | -8.7586e-05 | -19.5328 | -0.10986 | -121.5546 | 0.073242 | -120.7993 | -121.4722 | -121.6278 | -20.6085 | 0.009155 | -121.6507 | 0.041199 | -121.1151 | -121.2524 | -121.4813 | -0.036621 | -0.22888 | -0.045777 | 0.71869 | -0.10986 | 0.045776 | -0.073243 | 0.082397 | -0.13275 | -0.10986 | -0.07782 | 0.40283 | 0.036621 | 0.2655 | 0.16937 | 0.39825 | 0.75531 | 121.6278 | 0.53558 | 121.6919 | 121.4447 | 121.6599 | 121.4081 | 121.5271 | -121.6736 | -121.7697 | 121.5912 | 121.5591 | 101.9852 | 100.9094
895.2188 | 121.6873 | -121.5363 | 0.10529 | -0.016937 | 6.9618 | 0.065473 | 0.062579 | -0.00092703 | -0.0056867 | -0.00023063 | -0.0066527 | 0.0005234 | 0.068011 | 0.061483 | -0.0059857 | 0.020617 | -0.0030784 | -19.574 | -0.10986 | -121.4905 | 0.041199 | -120.8313 | -121.5271 | -121.6736 | -20.636 | -0.009155 | -121.6461 | -0.004578 | -121.17 | -121.2891 | -121.5408 | 0.045776 | -0.21515 | -0.064087 | 0.70496 | -0.13733 | 0.009155 | -0.18311 | -0.036621 | -0.10986 | -0.11444 | -0.10986 | 0.36621 | -0.004578 | 0.24719 | 0.10528 | 0.35706 | 0.65918 | 121.5317 | 0.47607 | 121.6415 | 121.3806 | 121.637 | 121.4264 | 121.5271 | -121.5958 | -121.7514 | 121.5775 | 121.5317 | 101.9623 | 100.9003
896.9062 | 121.756 | -121.5408 | 0.086975 | 0.005951 | 6.9652 | 0.06761 | 0.066638 | 0.00056817 | -0.0054731 | -0.0012988 | 0.0086061 | 0.0018052 | 0.069293 | 0.061696 | -0.0047039 | 0.019335 | -0.0037192 | -19.4824 | -0.11902 | -121.5179 | 0.10986 | -120.7581 | -121.4905 | -121.6187 | -20.5444 | -0.004578 | -121.6232 | 0.073242 | -121.1014 | -121.2387 | -121.4767 | 0.022889 | -0.20599 | 0.022888 | 0.78278 | -0.077819 | 0.050354 | -0.10071 | 0.027465 | -0.082397 | -0.091553 | -0.013733 | 0.43945 | 0.064087 | 0.30213 | 0.14648 | 0.38452 | 0.75989 | 121.6278 | 0.52185 | 121.6965 | 121.3989 | 121.6187 | 121.4218 | 121.5363 | -121.6049 | -121.7102 | 121.6507 | 121.6141 | 102.0584 | 100.9964
898.6562 | 121.7102 | -121.5134 | 0.10071 | -0.0016785 | 6.9639 | 0.069105 | 0.065142 | 0.0024908 | -0.0046185 | -0.0021532 | -0.00054933 | 0.0011642 | 0.067157 | 0.060628 | -0.0053449 | 0.021898 | -0.0069236 | -19.5969 | -0.11902 | -121.5179 | 0.009155 | -120.8908 | -121.6049 | -121.7468 | -20.7184 | -0.022888 | -121.6278 | 0.041199 | -121.1884 | -121.3257 | -121.5225 | -0.004577 | -0.21973 | -0.091553 | 0.62256 | -0.23346 | -0.091552 | -0.22888 | -0.086975 | -0.11444 | -0.1236 | -0.059509 | 0.32501 | -0.009155 | 0.18768 | 0.10529 | 0.30212 | 0.62714 | 121.5271 | 0.43945 | 121.669 | 121.3989 | 121.6049 | 121.3943 | 121.4905 | -121.6187 | -121.7285 | 121.5225 | 121.5546 | 101.9165 | 100.795
900.3438 | 121.7148 | -121.5317 | 0.11902 | -0.009308 | 6.9637 | 0.067396 | 0.065997 | -7.2628e-05 | -0.0065411 | -0.00023063 | -0.00054933 | 0.0026596 | 0.071216 | 0.063833 | -0.0038495 | 0.021471 | -0.0024374 | -19.5465 | -0.11902 | -121.5317 | 0.045776 | -120.8221 | -121.5637 | -121.701 | -20.6589 | -0.009155 | -121.6278 | 0.027466 | -121.17 | -121.312 | -121.5317 | 0 | -0.23804 | -0.073243 | 0.70953 | -0.16937 | -0.032044 | -0.16937 | -0.032044 | -0.096131 | -0.12817 | -0.091553 | 0.36163 | 0 | 0.21973 | 0.096131 | 0.31586 | 0.70953 | 121.5775 | 0.45776 | 121.6553 | 121.4127 | 121.6187 | 121.4127 | 121.5225 | -121.6507 | -121.7468 | 121.5775 | 121.5591 | 101.9852 | 100.8728
902.1094 | 121.7697 | -121.5546 | 0.10071 | 0.036468 | 6.963 | 0.068678 | 0.064074 | 0.0037726 | -0.0037641 | 0.00062377 | 0.014709 | 0.003514 | 0.068225 | 0.055929 | -0.0057721 | 0.020189 | -0.0045736 | -19.5328 | -0.082397 | -121.5408 | 0.086975 | -120.7809 | -121.4996 | -121.6415 | -20.6268 | -0.009155 | -121.6278 | 0.041199 | -121.1151 | -121.2524 | -121.4722 | 0.013732 | -0.18311 | -0.013733 | 0.77362 | -0.086976 | 0.054931 | -0.10071 | 0.041199 | -0.073243 | -0.10986 | -0.059509 | 0.43945 | 0.082397 | 0.30212 | 0.15564 | 0.37537 | 0.75989 | 121.6278 | 0.5127 | 121.669 | 121.4584 | 121.6187 | 121.4722 | 121.5454 | -121.6415 | -121.7285 | 121.6415 | 121.5958 | 102.0218 | 100.9277
903.8438 | 121.7606 | -121.5225 | 0.11902 | 0.028839 | 6.962 | 0.068037 | 0.064715 | -0.0019952 | -0.0059003 | -0.0010852 | 0.017761 | 0.003514 | 0.069079 | 0.058065 | -0.0072675 | 0.024035 | 0.00033961 | -19.5007 | -0.091553 | -121.5683 | 0.059509 | -120.7947 | -121.4905 | -121.6187 | -20.6497 | 0.004578 | -121.6324 | 0.036621 | -121.1197 | -121.2616 | -121.4767 | -0.045776 | -0.21057 | -0.05951 | 0.72784 | -0.09613 | 0.032043 | -0.050354 | 0.077819 | -0.10986 | -0.11444 | -0.082398 | 0.40283 | 0.045776 | 0.26093 | 0.15564 | 0.37079 | 0.77362 | 121.6278 | 0.51269 | 121.669 | 121.4767 | 121.637 | 121.431 | 121.5271 | -121.6873 | -121.7514 | 121.582 | 121.5591 | 102.0218 | 100.8728
905.5156 | 121.7285 | -121.5363 | 0.11902 | -0.0016785 | 6.9635 | 0.069746 | 0.062792 | 0.00014097 | -0.0054731 | -0.0012988 | 0.0025025 | 0.0018052 | 0.069079 | 0.052511 | -0.0042767 | 0.022753 | -0.0017966 | -19.5282 | -0.13275 | -121.5179 | 0.059509 | -120.8176 | -121.5775 | -121.6782 | -20.7001 | -0.018311 | -121.6324 | 0.022888 | -121.17 | -121.3257 | -121.5271 | 0.018311 | -0.25177 | -0.05951 | 0.71869 | -0.14191 | -0.041199 | -0.16022 | -0.05951 | -0.09613 | -0.13733 | -0.096131 | 0.36621 | 0.009155 | 0.21057 | 0.10528 | 0.3067 | 0.70038 | 121.5775 | 0.46234 | 121.6553 | 121.3852 | 121.6141 | 121.4035 | 121.5179 | -121.637 | -121.7514 | 121.5958 | 121.5591 | 102.0081 | 100.8362
907.25 | 121.6919 | -121.55 | 0.13275 | -0.0016785 | 6.963 | 0.066969 | 0.063433 | -0.001568 | -0.0033369 | -0.0030078 | -0.0036011 | 0.0013778 | 0.068011 | 0.060628 | -0.0049175 | 0.022753 | -0.00030119 | -19.5648 | -0.10986 | -121.5179 | 0.018311 | -120.8908 | -121.5958 | -121.7194 | -20.7687 | -0.004578 | -121.6553 | 0.004578 | -121.2204 | -121.3394 | -121.5271 | 0.032044 | -0.24261 | -0.11444 | 0.65918 | -0.16937 | -0.045776 | -0.20142 | -0.07782 | -0.10528 | -0.13733 | -0.12817 | 0.32959 | 0.022888 | 0.21057 | 0.12817 | 0.31586 | 0.62714 | 121.5363 | 0.43487 | 121.6599 | 121.4081 | 121.6507 | 121.4401 | 121.5454 | -121.6507 | -121.788 | 121.5683 | 121.5546 | 101.9852 | 100.7812
908.9219 | 121.7148 | -121.5408 | 0.12817 | -0.016937 | 6.9652 | 0.066541 | 0.06856 | -0.0022088 | -0.0082501 | -0.00065803 | -0.00054933 | 0.0015914 | 0.067798 | 0.059347 | -0.0057721 | 0.022967 | -0.0064962 | -19.5511 | -0.12817 | -121.5225 | 0.050354 | -120.8542 | -121.582 | -121.701 | -20.7459 | -0.018311 | -121.6507 | 0.004578 | -121.1884 | -121.344 | -121.5317 | 0.018311 | -0.25635 | -0.07782 | 0.68665 | -0.16022 | -0.041198 | -0.17853 | -0.059509 | -0.10986 | -0.14649 | -0.1236 | 0.35248 | 0.009156 | 0.19684 | 0.11902 | 0.3067 | 0.66833 | 121.5729 | 0.46234 | 121.6553 | 121.3943 | 121.6324 | 121.4127 | 121.5225 | -121.6507 | -121.7789 | 121.5912 | 121.5454 | 101.9897 | 100.795
910.6562 | 121.8658 | -121.5408 | 0.07782 | 0.005951 | 6.9605 | 0.067182 | 0.061511 | 0.0022772 | -0.0046185 | -0.00087163 | -0.00054933 | -0.0005448 | 0.068438 | 0.067037 | -0.0070539 | 0.023607 | -0.0017966 | -19.5374 | -0.15106 | -121.4951 | 0.16022 | -120.6894 | -121.4264 | -121.5408 | -20.5811 | -0.064087 | -121.6049 | 0.15106 | -121.0144 | -121.1288 | -121.4081 | 0.045777 | -0.22888 | 0.082397 | 0.85144 | 0 | 0.11444 | -0.045777 | 0.068664 | -0.064086 | -0.14191 | 0.073242 | 0.52643 | 0.13275 | 0.41199 | 0.19684 | 0.47607 | 0.80566 | 121.6553 | 0.59051 | 121.756 | 121.344 | 121.5408 | 121.3898 | 121.4767 | -121.5729 | -121.6827 | 121.7011 | 121.6919 | 102.0035 | 100.9598
912.3438 | 121.7697 | -121.55 | 0.12817 | 0.036468 | 6.9648 | 0.065473 | 0.067278 | 0.005268 | -0.0061139 | 0.00083737 | 0.017761 | 0.0015914 | 0.069079 | 0.058492 | -0.0074811 | 0.023394 | 0.0014078 | -19.5053 | -0.086975 | -121.55 | 0.064087 | -120.8084 | -121.5134 | -121.6553 | -20.7001 | 0.018311 | -121.669 | 0.022888 | -121.138 | -121.2936 | -121.4905 | 0 | -0.21515 | -0.064087 | 0.74158 | -0.10528 | 0.036621 | -0.10528 | 0.036621 | -0.11902 | -0.10986 | -0.10529 | 0.41199 | 0.059509 | 0.25635 | 0.17853 | 0.37537 | 0.74158 | 121.6141 | 0.53101 | 121.6919 | 121.463 | 121.6873 | 121.463 | 121.5683 | -121.6782 | -121.7972 | 121.6141 | 121.5729 | 102.0447 | 100.8499
914.0156 | 121.7468 | -121.5546 | 0.12817 | 0.051727 | 6.9626 | 0.069532 | 0.064715 | 0.0020636 | -0.0054731 | 0.0025464 | 0.011658 | 0.0030868 | 0.06972 | 0.052724 | -0.0074811 | 0.020617 | -0.0013694 | -19.5374 | -0.07782 | -121.5591 | 0.045776 | -120.8313 | -121.55 | -121.6782 | -20.7367 | 0.018311 | -121.6553 | 0.009155 | -121.1655 | -121.2845 | -121.5042 | -0.004578 | -0.20599 | -0.082398 | 0.72327 | -0.1236 | 0.004577 | -0.11902 | 0.009155 | -0.10071 | -0.10986 | -0.11902 | 0.3891 | 0.050354 | 0.27008 | 0.15106 | 0.37079 | 0.72784 | 121.6049 | 0.48981 | 121.6644 | 121.4813 | 121.6736 | 121.4767 | 121.5729 | -121.6873 | -121.7834 | 121.6003 | 121.5637 | 102.0172 | 100.8179
915.75 | 121.7285 | -121.5591 | 0.10986 | -0.009308 | 6.9624 | 0.067396 | 0.062579 | -0.0013544 | -0.0056867 | -0.001726 | 0.0025025 | 0.0011642 | 0.06972 | 0.062124 | -0.0079083 | 0.02083 | 0.00012601 | -19.519 | -0.11902 | -121.5088 | 0.036621 | -120.813 | -121.5408 | -121.6736 | -20.7413 | -0.018311 | -121.6553 | 0 | -121.17 | -121.2891 | -121.5225 | 0.050354 | -0.22888 | -0.073242 | 0.74616 | -0.11444 | 0.01831 | -0.1648 | -0.032044 | -0.09613 | -0.12817 | -0.10986 | 0.3891 | 0.036621 | 0.27008 | 0.13275 | 0.36621 | 0.6958 | 121.5454 | 0.48523 | 121.6553 | 121.3898 | 121.637 | 121.4401 | 121.5408 | -121.6187 | -121.7651 | 121.5958 | 121.5591 | 102.0401 | 100.8179
917.4219 | 121.7056 | -121.5363 | 0.11902 | -0.009308 | 6.9648 | 0.06761 | 0.063647 | 0.00099557 | -0.0037641 | -0.00087163 | -0.00054933 | 0.0037278 | 0.065661 | 0.052511 | -0.0027813 | 0.023394 | -0.00051479 | -19.574 | -0.11902 | -121.5179 | 0.018311 | -120.8862 | -121.6049 | -121.7331 | -20.8145 | 0.004578 | -121.669 | 0.004578 | -121.2204 | -121.344 | -121.5317 | 0.018311 | -0.23804 | -0.10071 | 0.65002 | -0.19684 | -0.068664 | -0.21515 | -0.086975 | -0.13275 | -0.11444 | -0.11444 | 0.31586 | 0.004578 | 0.19226 | 0.13733 | 0.32501 | 0.63171 | 121.5363 | 0.44861 | 121.6736 | 121.3989 | 121.6736 | 121.4172 | 121.5408 | -121.637 | -121.788 | 121.5546 | 121.5408 | 101.9623 | 100.7217
919.1562 | 121.788 | -121.5408 | 0.11444 | 0.02121 | 6.9615 | 0.06761 | 0.063006 | -0.00028623 | -0.0063275 | -0.00044443 | 0.0086061 | 0.0030868 | 0.064593 | 0.055074 | -0.0061993 | 0.024035 | -0.0039328 | -19.4687 | -0.09613 | -121.5546 | 0.09613 | -120.7718 | -121.5042 | -121.637 | -20.6818 | -0.018311 | -121.6232 | 0.086975 | -121.1197 | -121.2479 | -121.4859 | -0.013732 | -0.21057 | -0.018311 | 0.76904 | -0.09613 | 0.036622 | -0.082398 | 0.050354 | -0.082397 | -0.13275 | -0.027466 | 0.42114 | 0.054932 | 0.29297 | 0.13733 | 0.37537 | 0.78278 | 121.6507 | 0.50354 | 121.7102 | 121.4584 | 121.6049 | 121.4447 | 121.5225 | -121.669 | -121.7377 | 121.637 | 121.6278 | 102.0721 | 100.8591
920.8906 | 121.7789 | -121.5408 | 0.10529 | 0.01358 | 6.9648 | 0.070387 | 0.064715 | 0.0048408 | -0.0050457 | -0.0025806 | 0.0055543 | 0.0030868 | 0.068011 | 0.052511 | -0.0059857 | 0.022326 | -0.0011558 | -19.4595 | -0.11902 | -121.5408 | 0.086975 | -120.7764 | -121.5042 | -121.6461 | -20.6955 | -0.004578 | -121.6553 | 0.068665 | -121.106 | -121.2616 | -121.4722 | 0 | -0.22431 | -0.018311 | 0.76447 | -0.10528 | 0.036622 | -0.10528 | 0.036622 | -0.11444 | -0.10986 | -0.036621 | 0.43488 | 0.068665 | 0.27924 | 0.1831 | 0.39368 | 0.76447 | 121.6278 | 0.54932 | 121.7239 | 121.4218 | 121.6507 | 121.4218 | 121.5363 | -121.6461 | -121.7606 | 121.6278 | 121.6095 | 102.0813 | 100.8453
922.5625 | 121.7972 | -121.5271 | 0.09613 | 0.01358 | 6.9626 | 0.067396 | 0.06322 | 0.00099557 | -0.0046185 | -0.001726 | 0.0025025 | 0.0015914 | 0.069934 | 0.058065 | -0.0061993 | 0.024462 | 0.0029032 | -19.5602 | -0.13275 | -121.4905 | 0.10529 | -120.7764 | -121.5042 | -121.6278 | -20.7504 | -0.022888 | -121.6599 | 0.082397 | -121.1243 | -121.225 | -121.463 | 0.036621 | -0.22888 | 0.009156 | 0.75073 | -0.10071 | 0.022889 | -0.13733 | -0.013732 | -0.13275 | -0.11902 | -0.013733 | 0.40283 | 0.064087 | 0.30212 | 0.19684 | 0.43488 | 0.71411 | 121.5958 | 0.53558 | 121.7422 | 121.3577 | 121.637 | 121.3943 | 121.5042 | -121.5866 | -121.756 | 121.6324 | 121.6095 | 101.9669 | 100.7767
924.2969 | 121.8246 | -121.5454 | 0.086975 | 0.028839 | 6.9645 | 0.069319 | 0.064929 | 0.0027044 | -0.0050457 | -0.00065803 | 0.014709 | 0.0011642 | 0.069079 | 0.060415 | -0.0027813 | 0.022753 | 0.00033961 | -19.4916 | -0.14648 | -121.5408 | 0.16479 | -120.7123 | -121.4676 | -121.6095 | -20.7001 | -0.032043 | -121.6599 | 0.09613 | -121.0968 | -121.2204 | -121.463 | 0.004577 | -0.23346 | 0.07782 | 0.83313 | -0.064087 | 0.07782 | -0.068664 | 0.073243 | -0.11444 | -0.11902 | 0.009155 | 0.44861 | 0.082397 | 0.32501 | 0.19684 | 0.43945 | 0.82855 | 121.7056 | 0.56305 | 121.756 | 121.3943 | 121.6278 | 121.3989 | 121.5134 | -121.6278 | -121.7468 | 121.7102 | 121.6415 | 102.0538 | 100.8453
926.0312 | 121.7239 | -121.5637 | 0.13275 | -0.0016785 | 6.9624 | 0.066969 | 0.06621 | -0.004345 | -0.0046185 | -0.0025806 | 0.0025025 | 0.0013778 | 0.068225 | 0.056356 | -0.0091901 | 0.023394 | 0.0014078 | -19.6014 | -0.12817 | -121.5546 | 0.032043 | -120.8542 | -121.5408 | -121.6782 | -20.8054 | -0.004578 | -121.6095 | -0.013733 | -121.1838 | -121.312 | -121.5317 | 0.009156 | -0.26093 | -0.10071 | 0.70953 | -0.11444 | 0.022888 | -0.1236 | 0.013732 | -0.045776 | -0.13733 | -0.14648 | 0.37994 | 0.032044 | 0.25177 | 0.07782 | 0.29755 | 0.70038 | 121.5866 | 0.42572 | 121.5958 | 121.4264 | 121.6049 | 121.4355 | 121.5591 | -121.6873 | -121.7422 | 121.5958 | 121.55 | 101.9623 | 100.7584
927.7812 | 121.7651 | -121.5637 | 0.11444 | 0.028839 | 6.9626 | 0.068037 | 0.064929 | 0.00185 | -0.0039777 | -1.7026e-05 | 0.017761 | 0.0026596 | 0.070147 | 0.061696 | -0.0064129 | 0.021258 | -0.0011558 | -19.519 | -0.10529 | -121.5866 | 0.068665 | -120.845 | -121.5408 | -121.6599 | -20.7596 | 0.013733 | -121.6461 | 0.041199 | -121.138 | -121.2845 | -121.4767 | -0.022888 | -0.21973 | -0.045776 | 0.71869 | -0.09613 | 0.022888 | -0.073242 | 0.045776 | -0.082397 | -0.10071 | -0.073242 | 0.42572 | 0.086975 | 0.27924 | 0.16937 | 0.36163 | 0.74158 | 121.6553 | 0.50812 | 121.6873 | 121.4813 | 121.6599 | 121.4584 | 121.5775 | -121.701 | -121.7606 | 121.6324 | 121.6049 | 102.0447 | 100.8041
929.4531 | 121.756 | -121.5729 | 0.11444 | 0.036468 | 6.963 | 0.06761 | 0.063433 | -0.0019952 | -0.0048321 | 0.001692 | 0.014709 | 0.0037278 | 0.070147 | 0.061269 | -0.0068403 | 0.021044 | -0.0039328 | -19.519 | -0.086975 | -121.5866 | 0.068665 | -120.845 | -121.5363 | -121.6553 | -20.8054 | 0.045776 | -121.6827 | 0.022888 | -121.1746 | -121.3028 | -121.5134 | -0.013733 | -0.20142 | -0.045776 | 0.72784 | -0.082397 | 0.036621 | -0.068664 | 0.050354 | -0.10986 | -0.068665 | -0.091553 | 0.39825 | 0.059509 | 0.27008 | 0.16937 | 0.37994 | 0.74158 | 121.6553 | 0.50812 | 121.7056 | 121.4996 | 121.7285 | 121.4859 | 121.6187 | -121.701 | -121.7972 | 121.6415 | 121.5958 | 102.0538 | 100.7675
931.1875 | 121.8201 | -121.5179 | 0.082397 | 0.01358 | 6.9605 | 0.069319 | 0.062151 | -0.0034906 | -0.0061139 | -0.001726 | -0.00054933 | -0.0007584 | 0.067584 | 0.060415 | -0.0038495 | 0.020403 | -0.00030119 | -19.5786 | -0.15106 | -121.5088 | 0.10529 | -120.7947 | -121.4996 | -121.637 | -20.8237 | -0.036621 | -121.6187 | 0.082397 | -121.1014 | -121.2296 | -121.4493 | 0.009155 | -0.23346 | 0.022889 | 0.72327 | -0.11902 | 0.01831 | -0.12817 | 0.009155 | -0.10071 | -0.11902 | 0 | 0.41657 | 0.068664 | 0.28839 | 0.16937 | 0.3891 | 0.71411 | 121.6141 | 0.51727 | 121.701 | 121.3577 | 121.582 | 121.3669 | 121.4813 | -121.5912 | -121.701 | 121.6232 | 121.6003 | 101.9394 | 100.6943
932.9219 | 121.7789 | -121.5775 | 0.11902 | 0.005951 | 6.962 | 0.067396 | 0.061724 | 0.0012092 | -0.0048321 | -0.001726 | -0.00054933 | 0.0013778 | 0.069507 | 0.058919 | -0.0098309 | 0.021898 | -0.003292 | -19.5145 | -0.1236 | -121.5317 | 0.10529 | -120.7672 | -121.4859 | -121.6461 | -20.8008 | -0.018311 | -121.6461 | 0.013733 | -121.1426 | -121.2662 | -121.5088 | 0.045777 | -0.24261 | -0.013733 | 0.81024 | -0.068664 | 0.091553 | -0.11444 | 0.045776 | -0.068664 | -0.13733 | -0.10529 | 0.43488 | 0.068665 | 0.31128 | 0.13733 | 0.37994 | 0.76447 | 121.637 | 0.50354 | 121.6599 | 121.4081 | 121.6278 | 121.4539 | 121.5591 | -121.6507 | -121.7651 | 121.6827 | 121.5912 | 102.063 | 100.7767
934.6562 | 121.8796 | -121.5134 | 0.082397 | -0.009308 | 6.9596 | 0.066755 | 0.063433 | -0.0039178 | -0.0073957 | -0.0025806 | -0.0036011 | -0.0011856 | 0.065021 | 0.063192 | -0.0061993 | 0.022112 | -0.0039328 | -19.5236 | -0.14648 | -121.5179 | 0.19226 | -120.6665 | -121.4172 | -121.5546 | -20.6818 | -0.059509 | -121.6141 | 0.13275 | -121.0373 | -121.1609 | -121.431 | -0.004577 | -0.22888 | 0.10986 | 0.84686 | -0.041198 | 0.096131 | -0.036621 | 0.10071 | -0.10071 | -0.14191 | 0.050354 | 0.47608 | 0.082398 | 0.35248 | 0.18311 | 0.45319 | 0.85144 | 121.7102 | 0.57678 | 121.7468 | 121.3715 | 121.5546 | 121.3669 | 121.4539 | -121.6003 | -121.6965 | 121.7056 | 121.6461 | 101.9897 | 100.8316
936.3906 | 121.7697 | -121.5637 | 0.11902 | 0.044098 | 6.9633 | 0.06761 | 0.06386 | -0.00028623 | -0.0052595 | 0.00041017 | 0.017761 | 0.000737 | 0.069079 | 0.05187 | -0.0066265 | 0.021044 | -0.00072839 | -19.5557 | -0.091553 | -121.5591 | 0.073242 | -120.8313 | -121.5225 | -121.669 | -20.8466 | 0.022888 | -121.6736 | 0.018311 | -121.1609 | -121.2708 | -121.5042 | 0.004578 | -0.21057 | -0.045777 | 0.73242 | -0.10528 | 0.041199 | -0.10986 | 0.036621 | -0.10986 | -0.096131 | -0.10071 | 0.40283 | 0.05951 | 0.29297 | 0.16937 | 0.40283 | 0.72784 | 121.6324 | 0.5127 | 121.6919 | 121.4676 | 121.6965 | 121.4722 | 121.5866 | -121.6782 | -121.7926 | 121.637 | 121.582 | 102.0081 | 100.7172
938.125 | 121.8292 | -121.5454 | 0.086975 | 0.036468 | 6.9637 | 0.06825 | 0.065142 | 0.00078177 | -0.0041913 | -0.0010852 | 0.011658 | 0.0013778 | 0.06972 | 0.060628 | -0.0044903 | 0.023607 | -0.0056418 | -19.5923 | -0.15564 | -121.5317 | 0.13733 | -120.7581 | -121.4813 | -121.6141 | -20.8054 | 0 | -121.6461 | 0.086975 | -121.1151 | -121.2387 | -121.4539 | 0.013733 | -0.24261 | 0.050354 | 0.78735 | -0.068665 | 0.064087 | -0.082398 | 0.050354 | -0.10071 | -0.086975 | 0 | 0.4303 | 0.091553 | 0.3067 | 0.19226 | 0.40741 | 0.77362 | 121.669 | 0.53101 | 121.7331 | 121.376 | 121.6461 | 121.3898 | 121.5454 | -121.6187 | -121.7331 | 121.6827 | 121.6324 | 101.9531 | 100.7401
939.8125 | 121.8246 | -121.5546 | 0.091553 | 0.005951 | 6.9618 | 0.068464 | 0.062579 | 0.00056817 | -0.0046185 | 0.00041017 | 0.0055543 | 0.0018052 | 0.067584 | 0.068746 | -0.0047039 | 0.02318 | 0.00055321 | -19.5923 | -0.15106 | -121.5225 | 0.11444 | -120.7993 | -121.5042 | -121.6232 | -20.8466 | -0.027466 | -121.6324 | 0.073242 | -121.138 | -121.2387 | -121.4722 | 0.032043 | -0.24261 | 0.022888 | 0.75531 | -0.068665 | 0.050354 | -0.10071 | 0.018311 | -0.07782 | -0.11902 | -0.018311 | 0.41656 | 0.082397 | 0.31586 | 0.16022 | 0.39368 | 0.72327 | 121.637 | 0.49438 | 121.7056 | 121.3715 | 121.6049 | 121.4035 | 121.5271 | -121.6141 | -121.7239 | 121.669 | 121.6278 | 101.9623 | 100.708
941.5625 | 121.7834 | -121.5591 | 0.11902 | 0.005951 | 6.9618 | 0.06761 | 0.065569 | -0.00092703 | -0.0031231 | 0.0019056 | 0.0086061 | 0.0013778 | 0.067157 | 0.062337 | -0.0049175 | 0.021258 | -0.0045736 | -19.519 | -0.1236 | -121.5454 | 0.11444 | -120.7809 | -121.5042 | -121.6507 | -20.7687 | 0.004578 | -121.6599 | 0.07782 | -121.1243 | -121.2616 | -121.4722 | 0.013733 | -0.24261 | -0.004578 | 0.7782 | -0.091553 | 0.054932 | -0.10529 | 0.041199 | -0.10071 | -0.11444 | -0.041199 | 0.43488 | 0.086975 | 0.29755 | 0.18768 | 0.39825 | 0.76447 | 121.6599 | 0.53558 | 121.7377 | 121.4218 | 121.6644 | 121.4355 | 121.5637 | -121.6644 | -121.7789 | 121.6736 | 121.637 | 102.0401 | 100.7904
943.2969 | 121.8704 | -121.5179 | 0.091553 | 0.005951 | 6.9622 | 0.067396 | 0.063647 | 0.0061224 | -0.0033369 | 0.00041017 | 0.0025025 | 0.0030868 | 0.069079 | 0.05187 | -0.0040631 | 0.022539 | -0.0058554 | -19.5648 | -0.16937 | -121.4813 | 0.17395 | -120.7443 | -121.4722 | -121.6141 | -20.7687 | -0.054932 | -121.6232 | 0.13275 | -121.0739 | -121.1929 | -121.4035 | 0.036621 | -0.26093 | 0.082397 | 0.77362 | -0.096131 | 0.045776 | -0.13275 | 0.009155 | -0.10529 | -0.14649 | 0.041198 | 0.44403 | 0.11444 | 0.32501 | 0.21973 | 0.4303 | 0.737 | 121.6553 | 0.54932 | 121.756 | 121.312 | 121.5683 | 121.3486 | 121.463 | -121.5729 | -121.7148 | 121.6919 | 121.6507 | 101.9531 | 100.7492
944.9688 | 121.8704 | -121.5408 | 0.091553 | -0.0016785 | 6.9609 | 0.069319 | 0.067706 | 0.00185 | -0.0044049 | -0.00023063 | 0.0025025 | 0.0026596 | 0.067157 | 0.064687 | -0.0010723 | 0.023607 | -0.00072839 | -19.5374 | -0.12817 | -121.5271 | 0.16022 | -120.7443 | -121.4951 | -121.6187 | -20.7825 | -0.054932 | -121.6187 | 0.14191 | -121.0785 | -121.1975 | -121.4081 | 0.013733 | -0.21973 | 0.068664 | 0.79651 | -0.077819 | 0.045777 | -0.091552 | 0.032044 | -0.077819 | -0.14649 | 0.050354 | 0.46234 | 0.13275 | 0.34332 | 0.21057 | 0.42114 | 0.78278 | 121.6873 | 0.54016 | 121.7606 | 121.3989 | 121.5637 | 121.4127 | 121.4859 | -121.6187 | -121.7102 | 121.7011 | 121.6827 | 102.0035 | 100.7584
946.7031 | 121.8613 | -121.5271 | 0.091553 | -0.009308 | 6.9618 | 0.066969 | 0.06322 | -0.0028498 | -0.0084637 | -0.0019396 | -0.0036011 | 0.0018052 | 0.067157 | 0.05721 | -0.0053449 | 0.021471 | -0.0011558 | -19.5236 | -0.14191 | -121.5363 | 0.1831 | -120.694 | -121.4218 | -121.582 | -20.7733 | -0.041199 | -121.637 | 0.11902 | -121.0464 | -121.1746 | -121.4401 | -0.009155 | -0.23346 | 0.091552 | 0.83313 | -0.054931 | 0.10529 | -0.045776 | 0.11444 | -0.10986 | -0.13275 | 0.027466 | 0.48065 | 0.086975 | 0.35248 | 0.19684 | 0.46234 | 0.84229 | 121.7194 | 0.59051 | 121.756 | 121.3943 | 121.5958 | 121.3852 | 121.4859 | -121.6278 | -121.7285 | 121.7102 | 121.6461 | 102.0035 | 100.7538
948.375 | 121.7422 | -121.5729 | 0.12817 | -0.016937 | 6.9643 | 0.070173 | 0.065356 | -0.00028623 | -0.0067547 | -0.0015124 | 0.0025025 | 0.0033004 | 0.069079 | 0.053152 | -0.0061993 | 0.022112 | -0.0035056 | -19.6014 | -0.13275 | -121.5683 | 0.045776 | -120.8771 | -121.5866 | -121.7239 | -20.9381 | 0.004578 | -121.6507 | -0.004578 | -121.2296 | -121.3577 | -121.55 | 0.004578 | -0.26093 | -0.082398 | 0.6958 | -0.15106 | -0.013733 | -0.15564 | -0.018311 | -0.07782 | -0.1236 | -0.13275 | 0.34332 | 0.022888 | 0.21515 | 0.10071 | 0.29297 | 0.69122 | 121.6141 | 0.42114 | 121.6461 | 121.4355 | 121.6553 | 121.4401 | 121.5775 | -121.6965 | -121.7789 | 121.6187 | 121.5683 | 101.9714 | 100.6348
950.1094 | 121.7377 | -121.5958 | 0.10986 | -0.0016785 | 6.9628 | 0.065473 | 0.061297 | 0.0033454 | -0.0054731 | -0.001726 | -0.0036011 | 0.0026596 | 0.069293 | 0.052938 | -0.0085491 | 0.022326 | -0.0028646 | -19.606 | -0.12817 | -121.5408 | 0.032043 | -120.8633 | -121.5591 | -121.6873 | -20.9381 | -0.004578 | -121.6599 | 0 | -121.1929 | -121.3028 | -121.5363 | 0.054931 | -0.23804 | -0.07782 | 0.73242 | -0.091553 | 0.036621 | -0.14648 | -0.01831 | -0.064087 | -0.11444 | -0.10986 | 0.40283 | 0.059509 | 0.29297 | 0.1236 | 0.35706 | 0.67749 | 121.5729 | 0.46692 | 121.6599 | 121.4127 | 121.6553 | 121.4676 | 121.5912 | -121.6507 | -121.7697 | 121.6278 | 121.5958 | 101.9897 | 100.6577
951.8438 | 121.7468 | -121.5775 | 0.11444 | -0.009308 | 6.9618 | 0.068037 | 0.065142 | -0.00028623 | -0.0044049 | -0.0032214 | -0.00054933 | 0.0033004 | 0.067157 | 0.056569 | -0.0044903 | 0.021258 | -0.0058554 | -19.5831 | -0.11902 | -121.5454 | 0.013733 | -120.8817 | -121.6003 | -121.7056 | -20.9976 | -0.013733 | -121.6507 | 0.013733 | -121.2158 | -121.3348 | -121.5134 | 0.032044 | -0.23346 | -0.10071 | 0.6958 | -0.12817 | -0.022888 | -0.16022 | -0.054932 | -0.073242 | -0.12817 | -0.10071 | 0.36163 | 0.064087 | 0.24262 | 0.13733 | 0.31586 | 0.66376 | 121.5591 | 0.43488 | 121.6644 | 121.4264 | 121.637 | 121.4584 | 121.5637 | -121.6599 | -121.7651 | 121.5912 | 121.5912 | 101.9943 | 100.5798
953.5938 | 121.843 | -121.5454 | 0.07782 | 0.005951 | 6.9609 | 0.067182 | 0.062151 | 0.00056817 | -0.0041913 | -0.0021532 | -0.0036011 | 0.0003098 | 0.066516 | 0.064474 | -0.0049175 | 0.021898 | -0.0037192 | -19.5648 | -0.14191 | -121.5591 | 0.10071 | -120.7809 | -121.4996 | -121.6324 | -20.9335 | -0.041199 | -121.6599 | 0.09613 | -121.1197 | -121.2296 | -121.4539 | -0.013733 | -0.21973 | 0.022888 | 0.76447 | -0.086975 | 0.045776 | -0.073242 | 0.059509 | -0.11444 | -0.11902 | 0.01831 | 0.42572 | 0.091553 | 0.31586 | 0.20599 | 0.4303 | 0.7782 | 121.6599 | 0.54016 | 121.756 | 121.4172 | 121.6187 | 121.4035 | 121.5042 | -121.637 | -121.7377 | 121.6461 | 121.6415 | 101.9806 | 100.6119
955.3438 | 121.8658 | -121.5546 | 0.091553 | -0.0016785 | 6.9622 | 0.067182 | 0.065783 | -0.0039178 | -0.0067547 | -0.00065803 | -0.00054933 | 0.0009506 | 0.069293 | 0.063619 | -0.0034223 | 0.021898 | -0.0024374 | -19.5602 | -0.16479 | -121.5271 | 0.13733 | -120.7581 | -121.4722 | -121.6003 | -20.9061 | -0.041199 | -121.6461 | 0.11444 | -121.0693 | -121.1929 | -121.4218 | 0.027465 | -0.25635 | 0.045776 | 0.79651 | -0.045777 | 0.082397 | -0.073242 | 0.054932 | -0.091553 | -0.13275 | 0.022888 | 0.48523 | 0.13275 | 0.36163 | 0.2243 | 0.45319 | 0.76904 | 121.6644 | 0.57678 | 121.7606 | 121.3623 | 121.6049 | 121.3898 | 121.5134 | -121.6187 | -121.7377 | 121.6919 | 121.669 | 101.9943 | 100.6485
957.0312 | 121.875 | -121.5408 | 0.07782 | -0.009308 | 6.9603 | 0.067396 | 0.06087 | 0.00099557 | -0.0059003 | -0.0036486 | -0.0036011 | 0.0026596 | 0.068438 | 0.058065 | -0.0064129 | 0.022326 | 0.001835 | -19.519 | -0.16479 | -121.5454 | 0.15106 | -120.7535 | -121.4493 | -121.6049 | -20.9244 | -0.032043 | -121.6232 | 0.1236 | -121.0556 | -121.17 | -121.4264 | -0.004577 | -0.24261 | 0.073242 | 0.78735 | -0.064086 | 0.091553 | -0.059509 | 0.09613 | -0.082397 | -0.10986 | 0.045776 | 0.48523 | 0.11444 | 0.37079 | 0.19684 | 0.45319 | 0.79193 | 121.6965 | 0.56763 | 121.7468 | 121.3806 | 121.5912 | 121.376 | 121.5088 | -121.6232 | -121.7011 | 121.6919 | 121.6644 | 102.0218 | 100.6165
958.7969 | 121.8338 | -121.5729 | 0.10071 | 0.036468 | 6.962 | 0.069105 | 0.06386 | 0.00035457 | -0.0044049 | -0.00044443 | 0.0055543 | 0.0030868 | 0.067798 | 0.060415 | -0.0055585 | 0.024462 | -0.0062826 | -19.5419 | -0.13275 | -121.5546 | 0.1236 | -120.7901 | -121.5134 | -121.6324 | -20.9839 | -0.027466 | -121.6415 | 0.07782 | -121.1243 | -121.2662 | -121.4767 | 0.018311 | -0.23346 | 0.022888 | 0.78278 | -0.059509 | 0.059509 | -0.07782 | 0.041198 | -0.068665 | -0.12817 | -0.022888 | 0.44861 | 0.09613 | 0.3067 | 0.16479 | 0.37537 | 0.76447 | 121.6782 | 0.51727 | 121.7194 | 121.4218 | 121.6141 | 121.4401 | 121.5454 | -121.6553 | -121.7422 | 121.6965 | 121.6507 | 102.0309 | 100.589
960.5469 | 121.8704 | -121.5454 | 0.082397 | -0.0016785 | 6.9598 | 0.067823 | 0.064074 | -0.00049983 | -0.0067547 | -0.0032214 | 0.0025025 | -0.0003312 | 0.068225 | 0.061056 | -0.0061993 | 0.022326 | -0.0017966 | -19.5602 | -0.15106 | -121.5225 | 0.1236 | -120.7672 | -121.4722 | -121.6232 | -20.961 | -0.032043 | -121.6644 | 0.1236 | -121.0693 | -121.2112 | -121.4355 | 0.022888 | -0.23346 | 0.041199 | 0.7782 | -0.07782 | 0.073242 | -0.10071 | 0.050354 | -0.11902 | -0.11444 | 0.041199 | 0.47607 | 0.10986 | 0.33417 | 0.22888 | 0.45319 | 0.75531 | 121.6461 | 0.59509 | 121.788 | 121.3715 | 121.6324 | 121.3943 | 121.5134 | -121.6049 | -121.7468 | 121.669 | 121.669 | 101.9852 | 100.5844
962.2969 | 121.8796 | -121.4996 | 0.07782 | -0.009308 | 6.9605 | 0.067182 | 0.062151 | -0.001568 | -0.0041913 | -0.002367 | -0.00054933 | 0.0011642 | 0.069079 | 0.060842 | -0.0064129 | 0.02083 | -0.0041464 | -19.487 | -0.14191 | -121.5317 | 0.17395 | -120.6848 | -121.4127 | -121.6049 | -20.8923 | -0.032043 | -121.6324 | 0.13733 | -121.051 | -121.1838 | -121.431 | -0.032043 | -0.21973 | 0.09613 | 0.81482 | -0.10528 | 0.086975 | -0.073242 | 0.11902 | -0.13275 | -0.10986 | 0.059509 | 0.44861 | 0.068665 | 0.31586 | 0.20142 | 0.44861 | 0.84686 | 121.7056 | 0.58136 | 121.7697 | 121.3898 | 121.6003 | 121.3577 | 121.4676 | -121.6095 | -121.7102 | 121.6736 | 121.637 | 102.0126 | 100.6073
963.9688 | 121.843 | -121.5454 | 0.091553 | 0.036468 | 6.9628 | 0.069319 | 0.066851 | -0.0019952 | -0.0069683 | 0.00062377 | 0.014709 | 0.0022324 | 0.068866 | 0.064901 | -0.0042767 | 0.022326 | -0.0020102 | -19.5007 | -0.13275 | -121.5363 | 0.17853 | -120.7352 | -121.4767 | -121.6278 | -20.9198 | -0.027466 | -121.6507 | 0.10071 | -121.1197 | -121.2433 | -121.4722 | 0.009155 | -0.2243 | 0.086975 | 0.81024 | -0.082398 | 0.068664 | -0.091553 | 0.059509 | -0.10529 | -0.11902 | 0.009155 | 0.42572 | 0.073242 | 0.30212 | 0.17853 | 0.40741 | 0.80109 | 121.7148 | 0.53101 | 121.7514 | 121.4035 | 121.6232 | 121.4127 | 121.5179 | -121.6278 | -121.7422 | 121.7239 | 121.6461 | 102.0447 | 100.6256
965.6562 | 121.7743 | -121.5637 | 0.10529 | 0.01358 | 6.9648 | 0.068891 | 0.065356 | 0.0033454 | -0.0041913 | -0.00087163 | 0.0025025 | 0.0037278 | 0.067798 | 0.057424 | -0.0047039 | 0.021258 | -0.0030784 | -19.5007 | -0.1236 | -121.5866 | 0.11902 | -120.8038 | -121.5546 | -121.6873 | -20.9656 | -0.022888 | -121.637 | 0.041199 | -121.1838 | -121.312 | -121.5042 | -0.022888 | -0.22888 | 0.013733 | 0.75989 | -0.1236 | 0.009156 | -0.10071 | 0.032044 | -0.073242 | -0.12817 | -0.064087 | 0.37994 | 0.05951 | 0.25177 | 0.13275 | 0.32501 | 0.78278 | 121.7056 | 0.45319 | 121.6782 | 121.463 | 121.6141 | 121.4401 | 121.5408 | -121.6919 | -121.7422 | 121.6827 | 121.6049 | 102.063 | 100.5981
967.4062 | 121.7972 | -121.5775 | 0.09613 | 0.005951 | 6.963 | 0.066969 | 0.064929 | -0.0013544 | -0.0052595 | -0.00044443 | -0.00054933 | 0.0026596 | 0.068652 | 0.065755 | -0.0047039 | 0.022539 | -0.0047874 | -19.5969 | -0.1236 | -121.5317 | 0.045776 | -120.8542 | -121.5958 | -121.7194 | -21.0617 | -0.013733 | -121.6827 | 0.073242 | -121.1426 | -121.2753 | -121.4722 | 0.045777 | -0.21973 | -0.050354 | 0.72327 | -0.14191 | -0.01831 | -0.18768 | -0.064087 | -0.10528 | -0.10986 | -0.022888 | 0.43488 | 0.10529 | 0.30212 | 0.21057 | 0.40741 | 0.67749 | 121.5775 | 0.54016 | 121.756 | 121.4081 | 121.669 | 121.4539 | 121.5637 | -121.6278 | -121.7789 | 121.6232 | 121.6507 | 101.9806 | 100.5157
969.0781 | 121.7972 | -121.5591 | 0.11444 | 0.028839 | 6.9637 | 0.066328 | 0.065997 | 0.0065498 | -0.0073957 | -0.00065803 | 0.0086061 | 0.0022324 | 0.069293 | 0.056783 | -0.0074811 | 0.022539 | -0.0056418 | -19.4916 | -0.10986 | -121.5637 | 0.10986 | -120.7855 | -121.5225 | -121.6599 | -20.9885 | -0.018311 | -121.669 | 0.050354 | -121.1288 | -121.2753 | -121.4859 | -0.004578 | -0.2243 | -0.004578 | 0.77362 | -0.10071 | 0.036621 | -0.09613 | 0.041199 | -0.10986 | -0.13275 | -0.064087 | 0.4303 | 0.073242 | 0.28381 | 0.1831 | 0.39368 | 0.7782 | 121.6736 | 0.54016 | 121.7194 | 121.4539 | 121.6507 | 121.4493 | 121.5408 | -121.6782 | -121.7834 | 121.669 | 121.6095 | 102.0676 | 100.5707
970.8125 | 121.8338 | -121.5729 | 0.086975 | 0.02121 | 6.9645 | 0.06761 | 0.06386 | 0.00078177 | -0.0035505 | -0.00065803 | 0.011658 | 0.0028732 | 0.06972 | 0.062551 | -0.0051313 | 0.02553 | -0.0028646 | -19.6014 | -0.14648 | -121.5317 | 0.10529 | -120.7809 | -121.5088 | -121.6324 | -21.0342 | -0.041199 | -121.6644 | 0.068665 | -121.1517 | -121.257 | -121.4767 | 0.041199 | -0.23346 | 0.018311 | 0.79193 | -0.059509 | 0.064087 | -0.10071 | 0.022888 | -0.091553 | -0.12817 | -0.01831 | 0.42114 | 0.09613 | 0.31586 | 0.18768 | 0.40741 | 0.75073 | 121.637 | 0.5127 | 121.7331 | 121.3852 | 121.6232 | 121.4264 | 121.5317 | -121.6187 | -121.7514 | 121.6782 | 121.6415 | 101.9714 | 100.5386
972.5 | 121.8933 | -121.55 | 0.082397 | -0.0016785 | 6.962 | 0.068891 | 0.061724 | -0.0013544 | -0.0069683 | -0.001726 | -0.00054933 | 0.0011642 | 0.068438 | 0.064901 | -0.0068403 | 0.021258 | -0.0041464 | -19.4962 | -0.15564 | -121.5408 | 0.16479 | -120.694 | -121.4264 | -121.5591 | -20.9381 | -0.073242 | -121.6461 | 0.10986 | -121.0281 | -121.1746 | -121.4264 | 0.009155 | -0.23804 | 0.082398 | 0.85602 | -0.009155 | 0.1236 | -0.01831 | 0.11444 | -0.09613 | -0.15564 | 0.027466 | 0.52185 | 0.1236 | 0.37537 | 0.21973 | 0.4715 | 0.84686 | 121.7056 | 0.61798 | 121.756 | 121.3852 | 121.5729 | 121.3943 | 121.4767 | -121.6232 | -121.7285 | 121.7148 | 121.6599 | 102.0538 | 100.6119
974.1719 | 121.8613 | -121.5271 | 0.10986 | 0.005951 | 6.9639 | 0.068464 | 0.063433 | 0.0048408 | -0.0067547 | 0.0021192 | -0.00054933 | -0.0001174 | 0.068225 | 0.061483 | -0.0059857 | 0.020189 | -0.0045736 | -19.5099 | -0.16022 | -121.5134 | 0.16937 | -120.7123 | -121.4493 | -121.6003 | -20.9656 | -0.041199 | -121.6644 | 0.12817 | -121.051 | -121.2067 | -121.463 | 0.013733 | -0.27008 | 0.05951 | 0.81482 | -0.073242 | 0.07782 | -0.086975 | 0.064087 | -0.13733 | -0.15106 | 0.018311 | 0.47608 | 0.064087 | 0.32044 | 0.20142 | 0.45776 | 0.80109 | 121.6827 | 0.6134 | 121.7926 | 121.3531 | 121.6232 | 121.3669 | 121.4859 | -121.6232 | -121.7743 | 121.6965 | 121.6553 | 102.0172 | 100.5615
975.9062 | 121.8155 | -121.5591 | 0.091553 | 0.02121 | 6.9641 | 0.068678 | 0.063433 | -0.00071343 | -0.0067547 | -0.00023063 | 0.0086061 | 0.0026596 | 0.067798 | 0.056356 | -0.0047039 | 0.022326 | -0.0028646 | -19.5557 | -0.1236 | -121.5546 | 0.12817 | -120.7901 | -121.5225 | -121.6324 | -21.0983 | -0.009155 | -121.6965 | 0.07782 | -121.138 | -121.257 | -121.4813 | 0.004578 | -0.21515 | 0.036621 | 0.76904 | -0.073242 | 0.036621 | -0.07782 | 0.032043 | -0.13733 | -0.10071 | -0.013733 | 0.42114 | 0.07782 | 0.30212 | 0.21515 | 0.43945 | 0.76447 | 121.6827 | 0.55847 | 121.7743 | 121.431 | 121.6873 | 121.4355 | 121.55 | -121.6461 | -121.788 | 121.6873 | 121.637 | 102.0035 | 100.4608
977.5781 | 121.7697 | -121.6049 | 0.13275 | -0.0016785 | 6.9624 | 0.068678 | 0.062792 | 0.00099557 | -0.0063275 | -0.0040758 | -0.00054933 | 0.0026596 | 0.06972 | 0.057851 | -0.0072675 | 0.021471 | -0.00072839 | -19.5328 | -0.14191 | -121.5591 | 0.054932 | -120.8405 | -121.5637 | -121.6919 | -21.1212 | 0 | -121.6873 | -0.022888 | -121.1929 | -121.3028 | -121.5363 | 0.045776 | -0.27466 | -0.077819 | 0.76447 | -0.086976 | 0.041198 | -0.13275 | -0.004578 | -0.082398 | -0.13275 | -0.15564 | 0.41199 | 0.068664 | 0.30212 | 0.15106 | 0.38452 | 0.71869 | 121.6141 | 0.49438 | 121.6644 | 121.4172 | 121.6873 | 121.463 | 121.6049 | -121.6919 | -121.8201 | 121.6599 | 121.582 | 102.0721 | 100.4837
979.3125 | 121.8384 | -121.5546 | 0.082397 | 0.036468 | 6.9675 | 0.071028 | 0.065142 | 0.0033454 | -0.0024823 | 0.0023328 | 0.014709 | 0.003514 | 0.070575 | 0.060842 | -0.0044903 | 0.02318 | -0.0052146 | -19.4962 | -0.14648 | -121.5408 | 0.16479 | -120.7214 | -121.463 | -121.6049 | -21.0022 | -0.013733 | -121.6736 | 0.11902 | -121.1151 | -121.225 | -121.463 | 0.013732 | -0.22888 | 0.082398 | 0.83313 | -0.050354 | 0.091552 | -0.064086 | 0.07782 | -0.11902 | -0.09613 | 0.036622 | 0.43945 | 0.091552 | 0.32959 | 0.21057 | 0.44861 | 0.8194 | 121.7056 | 0.55847 | 121.7926 | 121.3943 | 121.6599 | 121.4081 | 121.5408 | -121.6232 | -121.756 | 121.7194 | 121.6736 | 102.0584 | 100.5524
980.9844 | 121.8338 | -121.5591 | 0.09613 | -0.009308 | 6.9643 | 0.06825 | 0.06386 | -0.0041314 | -0.0065411 | -0.0021532 | -0.0036011 | 0.003514 | 0.068225 | 0.059347 | -0.0044903 | 0.022112 | -0.0024374 | -19.5419 | -0.1236 | -121.5591 | 0.073242 | -120.8542 | -121.5912 | -121.7056 | -21.1075 | -0.027466 | -121.6599 | 0.086975 | -121.1288 | -121.2753 | -121.4722 | 0 | -0.21973 | -0.022888 | 0.70496 | -0.14648 | -0.032044 | -0.14648 | -0.032044 | -0.10071 | -0.1236 | -0.009155 | 0.4303 | 0.086975 | 0.28381 | 0.18768 | 0.38452 | 0.70496 | 121.6324 | 0.53101 | 121.7468 | 121.4355 | 121.6324 | 121.4355 | 121.5317 | -121.6553 | -121.756 | 121.6324 | 121.6461 | 102.0172 | 100.4517
982.7344 | 121.8567 | -121.5637 | 0.10071 | -0.009308 | 6.9656 | 0.069532 | 0.064715 | -0.006054 | -0.0033369 | 0.00041017 | -0.00054933 | 0.002446 | 0.068438 | 0.058492 | -0.0051313 | 0.022967 | -0.0030784 | -19.5145 | -0.14191 | -121.5591 | 0.082397 | -120.8313 | -121.5683 | -121.6873 | -21.1029 | -0.027466 | -121.6736 | 0.11444 | -121.1197 | -121.2433 | -121.4447 | 0.004578 | -0.24262 | -0.018311 | 0.73242 | -0.1236 | -0.004577 | -0.12817 | -0.009155 | -0.10986 | -0.12817 | 0.013733 | 0.44403 | 0.11902 | 0.32044 | 0.22888 | 0.4303 | 0.72784 | 121.6415 | 0.55389 | 121.788 | 121.4172 | 121.6461 | 121.4218 | 121.5363 | -121.6599 | -121.7743 | 121.6461 | 121.6782 | 102.0493 | 100.4608
984.4062 | 121.875 | -121.5363 | 0.086975 | -0.009308 | 6.9648 | 0.068678 | 0.062365 | 0.00056817 | -0.0041913 | 0.0012646 | 0.017761 | 0.0018052 | 0.070575 | 0.060628 | -0.0059857 | 0.024462 | -0.001583 | -19.455 | -0.15564 | -121.5225 | 0.19226 | -120.7123 | -121.4676 | -121.5958 | -21.0251 | -0.032043 | -121.669 | 0.15564 | -121.0831 | -121.2021 | -121.4264 | 0.013733 | -0.24261 | 0.10529 | 0.82397 | -0.059509 | 0.068665 | -0.073242 | 0.054932 | -0.13275 | -0.11902 | 0.068665 | 0.45319 | 0.10986 | 0.33417 | 0.24261 | 0.46692 | 0.81024 | 121.7148 | 0.58594 | 121.8246 | 121.3669 | 121.637 | 121.3806 | 121.5042 | -121.6095 | -121.756 | 121.7285 | 121.6919 | 102.0813 | 100.5112
986.1406 | 121.7926 | -121.5591 | 0.10986 | 0.005951 | 6.9669 | 0.068678 | 0.064929 | 0.0039862 | -0.0061139 | -0.001726 | 0.0025025 | 0.003514 | 0.069934 | 0.059774 | -0.0094037 | 0.02318 | -0.0011558 | -19.4366 | -0.10071 | -121.5866 | 0.11444 | -120.8038 | -121.5179 | -121.6644 | -21.08 | -0.018311 | -121.6827 | 0.068665 | -121.138 | -121.2799 | -121.5088 | -0.027466 | -0.21057 | 0.004578 | 0.75531 | -0.10529 | 0.041199 | -0.07782 | 0.068665 | -0.1236 | -0.12817 | -0.041198 | 0.42114 | 0.050354 | 0.27924 | 0.17395 | 0.40283 | 0.78278 | 121.701 | 0.54474 | 121.7514 | 121.4859 | 121.6644 | 121.4584 | 121.5408 | -121.6965 | -121.7926 | 121.6736 | 121.6278 | 102.1225 | 100.4791
987.8906 | 121.7789 | -121.5775 | 0.11444 | 0.01358 | 6.9677 | 0.06825 | 0.06386 | 0.0031318 | -0.0050457 | 0.0012646 | 0.017761 | 0.004155 | 0.069507 | 0.057424 | -0.0068403 | 0.021685 | -0.00051479 | -19.4824 | -0.091553 | -121.5958 | 0.054932 | -120.8633 | -121.5454 | -121.6965 | -21.1578 | 0.009155 | -121.7285 | 0.013733 | -121.1655 | -121.3074 | -121.4996 | -0.01831 | -0.20599 | -0.059509 | 0.71411 | -0.11902 | 0.032044 | -0.10071 | 0.050354 | -0.15106 | -0.10529 | -0.10071 | 0.41199 | 0.07782 | 0.27008 | 0.22888 | 0.42114 | 0.73242 | 121.6507 | 0.56305 | 121.7422 | 121.5042 | 121.7377 | 121.4859 | 121.5866 | -121.7102 | -121.843 | 121.6324 | 121.5912 | 102.095 | 100.4196
989.5781 | 121.7514 | -121.5729 | 0.1236 | -0.009308 | 6.9639 | 0.068678 | 0.064074 | -0.001568 | -0.0071821 | -0.0038622 | -0.00054933 | 0.0011642 | 0.068011 | 0.057638 | -0.0096173 | 0.02083 | -0.00094199 | -19.5557 | -0.11444 | -121.5775 | 0.018311 | -120.8862 | -121.5775 | -121.7102 | -21.2173 | -0.009155 | -121.6919 | -0.022888 | -121.1975 | -121.3394 | -121.5317 | -0.004578 | -0.23804 | -0.10528 | 0.68665 | -0.13733 | -0.004578 | -0.13275 | 0 | -0.11902 | -0.13275 | -0.14648 | 0.37537 | 0.041199 | 0.23346 | 0.16022 | 0.35248 | 0.69122 | 121.5958 | 0.49439 | 121.669 | 121.463 | 121.6827 | 121.4584 | 121.5637 | -121.7011 | -121.8155 | 121.5912 | 121.55 | 102.0172 | 100.3555
991.3125 | 121.8613 | -121.5591 | 0.07782 | 0.005951 | 6.968 | 0.068464 | 0.063006 | -0.0013544 | -0.0063275 | -1.7026e-05 | -0.0066527 | 0.0018052 | 0.068438 | 0.055074 | -0.0072675 | 0.02318 | -0.0022238 | -19.4733 | -0.15106 | -121.55 | 0.16479 | -120.726 | -121.4539 | -121.6095 | -21.0846 | -0.045776 | -121.6644 | 0.11902 | -121.0785 | -121.2067 | -121.4355 | 0.009155 | -0.22888 | 0.086975 | 0.83313 | -0.050354 | 0.10529 | -0.059509 | 0.096131 | -0.10529 | -0.1236 | 0.041199 | 0.48065 | 0.1236 | 0.35248 | 0.22888 | 0.45776 | 0.82398 | 121.7148 | 0.58594 | 121.7834 | 121.3989 | 121.6187 | 121.4081 | 121.5134 | -121.6278 | -121.7422 | 121.7239 | 121.6782 | 102.0859 | 100.4745
993 | 121.7651 | -121.582 | 0.11444 | -0.016937 | 6.968 | 0.06825 | 0.062792 | -0.003277 | -0.0044049 | 0.001051 | -0.0036011 | 0.0028732 | 0.06737 | 0.055288 | -0.0055585 | 0.022326 | -0.0056418 | -19.487 | -0.13733 | -121.5775 | 0.082397 | -120.8496 | -121.5912 | -121.7056 | -21.1853 | -0.018311 | -121.6873 | 0.018311 | -121.1929 | -121.3394 | -121.5271 | 0.004577 | -0.25177 | -0.032044 | 0.73242 | -0.1236 | -0.009156 | -0.12817 | -0.013733 | -0.10529 | -0.13275 | -0.09613 | 0.3891 | 0.054931 | 0.24261 | 0.16022 | 0.3479 | 0.72785 | 121.6599 | 0.49438 | 121.7056 | 121.4401 | 121.669 | 121.4447 | 121.5637 | -121.6919 | -121.8018 | 121.6644 | 121.6003 | 102.095 | 100.3967
994.7344 | 121.8018 | -121.5775 | 0.091553 | 0.02121 | 6.9701 | 0.069532 | 0.06322 | 0.0071906 | -0.0044049 | 0.00041017 | 0.0086061 | 0.0018052 | 0.068225 | 0.066183 | -0.0064129 | 0.022753 | -0.0041464 | -19.4641 | -0.12817 | -121.5637 | 0.10071 | -120.7993 | -121.5454 | -121.6827 | -21.0983 | -0.027466 | -121.6919 | 0.07782 | -121.1517 | -121.2708 | -121.4951 | 0.013733 | -0.21973 | 0.009155 | 0.7782 | -0.10528 | 0.032044 | -0.11902 | 0.018311 | -0.11444 | -0.11902 | -0.013733 | 0.42572 | 0.082398 | 0.3067 | 0.19684 | 0.42114 | 0.76447 | 121.6644 | 0.54016 | 121.7697 | 121.4355 | 121.6644 | 121.4493 | 121.55 | -121.6553 | -121.7834 | 121.6782 | 121.6553 | 102.1133 | 100.4791
996.4688 | 121.8521 | -121.5683 | 0.073242 | 0.028839 | 6.9652 | 0.069746 | 0.064288 | -0.00071343 | -0.0044049 | 0.0019056 | 0.020813 | 0.0015914 | 0.069934 | 0.062337 | -0.0042767 | 0.023394 | 0.0014078 | -19.4962 | -0.13275 | -121.55 | 0.16937 | -120.7443 | -121.4996 | -121.6232 | -21.1395 | -0.018311 | -121.6599 | 0.10986 | -121.1105 | -121.2524 | -121.4813 | 0.01831 | -0.20599 | 0.096131 | 0.82397 | -0.054932 | 0.068664 | -0.073242 | 0.050354 | -0.091553 | -0.091553 | 0.036621 | 0.45776 | 0.086975 | 0.31586 | 0.17853 | 0.40741 | 0.80566 | 121.7194 | 0.54932 | 121.7697 | 121.4172 | 121.6415 | 121.4355 | 121.55 | -121.6232 | -121.7331 | 121.7377 | 121.6782 | 102.0721 | 100.4288
998.2188 | 121.7422 | -121.5866 | 0.11444 | -0.009308 | 6.9684 | 0.068678 | 0.065356 | 0.0048408 | -0.0046185 | -0.0025806 | -0.00054933 | 0.0018052 | 0.069507 | 0.054433 | -0.0049175 | 0.022967 | -0.0024374 | -19.5465 | -0.11902 | -121.5775 | 0.013733 | -120.9229 | -121.6187 | -121.7422 | -21.3181 | -0.013733 | -121.701 | 0.009155 | -121.2433 | -121.3806 | -121.55 | 0.009155 | -0.23346 | -0.10071 | 0.66376 | -0.15564 | -0.032043 | -0.16479 | -0.041198 | -0.11444 | -0.12817 | -0.10529 | 0.34332 | 0.036621 | 0.20599 | 0.15106 | 0.32043 | 0.6546 | 121.5912 | 0.45776 | 121.7102 | 121.4584 | 121.6873 | 121.4676 | 121.5729 | -121.6919 | -121.8155 | 121.6003 | 121.5958 | 102.0401 | 100.2686
999.9531 | 121.7239 | -121.5866 | 0.1236 | -0.0016785 | 6.9677 | 0.069746 | 0.064074 | 0.0031318 | -0.0063275 | -0.0012988 | -0.0036011 | 0.002446 | 0.069293 | 0.056783 | -0.0055585 | 0.023394 | -0.005001 | -19.5099 | -0.11444 | -121.582 | 0.022888 | -120.9091 | -121.6324 | -121.7651 | -21.3593 | 0 | -121.6827 | -0.009155 | -121.2296 | -121.376 | -121.5454 | 0.004578 | -0.23804 | -0.10071 | 0.67749 | -0.17853 | -0.045776 | -0.18311 | -0.050354 | -0.09613 | -0.1236 | -0.13275 | 0.35706 | 0.041199 | 0.21057 | 0.13733 | 0.3067 | 0.67291 | 121.6049 | 0.45319 | 121.6736 | 121.4676 | 121.6827 | 121.4722 | 121.5866 | -121.7056 | -121.8063 | 121.6095 | 121.5775 | 102.0767 | 100.2274
1001.625 | 121.8887 | -121.5546 | 0.082397 | 0.005951 | 6.9677 | 0.068464 | 0.064501 | 0.0037726 | -0.0065411 | -0.0012988 | -0.00054933 | 0.0022324 | 0.068225 | 0.060842 | -0.0029949 | 0.022967 | -0.0020102 | -19.4229 | -0.17853 | -121.5179 | 0.14648 | -120.7581 | -121.4767 | -121.6324 | -21.167 | -0.059509 | -121.637 | 0.15106 | -121.0876 | -121.2067 | -121.4127 | 0.036621 | -0.26092 | 0.064087 | 0.79651 | -0.07782 | 0.077819 | -0.11444 | 0.041198 | -0.082398 | -0.14191 | 0.068665 | 0.46692 | 0.14191 | 0.3479 | 0.2243 | 0.4303 | 0.75989 | 121.6644 | 0.54932 | 121.788 | 121.3394 | 121.5775 | 121.376 | 121.4951 | -121.6003 | -121.7194 | 121.701 | 121.7056 | 102.1317 | 100.3876
1003.375 | 121.7468 | -121.6003 | 0.10529 | -0.0016785 | 6.9652 | 0.06825 | 0.06386 | 0.003559 | -0.0050457 | -0.0032214 | 0.0025025 | 0.0022324 | 0.068652 | 0.060842 | -0.0066265 | 0.023607 | -0.0013694 | -19.519 | -0.10529 | -121.6141 | 0.009155 | -120.9137 | -121.6324 | -121.7422 | -21.3409 | -0.022888 | -121.6873 | 0.009155 | -121.2296 | -121.3577 | -121.5271 | -0.013733 | -0.21057 | -0.096131 | 0.68665 | -0.14191 | -0.032043 | -0.12817 | -0.01831 | -0.086975 | -0.12817 | -0.096131 | 0.37079 | 0.073242 | 0.24262 | 0.16022 | 0.32959 | 0.70038 | 121.6232 | 0.45776 | 121.6965 | 121.5088 | 121.6644 | 121.4951 | 121.5775 | -121.7194 | -121.7926 | 121.6095 | 121.6095 | 102.0813 | 100.2594
1005.0469 | 121.7651 | -121.6049 | 0.11444 | -0.009308 | 6.9673 | 0.066755 | 0.066638 | 0.0020636 | -0.0050457 | 0.00019657 | 0.014709 | 0.0043686 | 0.068438 | 0.051015 | -0.0087629 | 0.020189 | -0.003292 | -19.4687 | -0.073242 | -121.6324 | 0.041199 | -120.8633 | -121.5408 | -121.6919 | -21.2952 | 0.013733 | -121.6965 | 0 | -121.2021 | -121.3211 | -121.5225 | -0.027466 | -0.18768 | -0.073242 | 0.74158 | -0.086976 | 0.064086 | -0.05951 | 0.091552 | -0.091553 | -0.10071 | -0.11444 | 0.40283 | 0.082397 | 0.28381 | 0.17395 | 0.37537 | 0.76904 | 121.6736 | 0.49438 | 121.6965 | 121.5591 | 121.7102 | 121.5317 | 121.6187 | -121.7468 | -121.8109 | 121.6461 | 121.6049 | 102.1362 | 100.3098
1006.7969 | 121.8887 | -121.5729 | 0.073242 | 0.01358 | 6.9656 | 0.066541 | 0.06386 | -0.00071343 | -0.0063275 | 0.00062377 | -0.00054933 | 0.000737 | 0.06673 | 0.062124 | -0.0061993 | 0.023607 | -0.0017966 | -19.4641 | -0.16479 | -121.5591 | 0.13733 | -120.7581 | -121.463 | -121.6232 | -21.2357 | -0.059509 | -121.6415 | 0.13275 | -121.0693 | -121.1746 | -121.4127 | 0.013733 | -0.23804 | 0.064087 | 0.81482 | -0.050354 | 0.10986 | -0.064087 | 0.09613 | -0.068665 | -0.13275 | 0.059509 | 0.50354 | 0.16022 | 0.39825 | 0.22888 | 0.46692 | 0.80109 | 121.6965 | 0.5722 | 121.7743 | 121.3943 | 121.582 | 121.4081 | 121.5134 | -121.6324 | -121.7148 | 121.7102 | 121.7056 | 102.1088 | 100.3372
1008.4688 | 121.7514 | -121.6003 | 0.12817 | -0.016937 | 6.969 | 0.06526 | 0.062365 | -0.0011408 | -0.0041913 | -0.002367 | -0.00054933 | 0.0033004 | 0.06972 | 0.057424 | -0.0096173 | 0.020189 | -8.7586e-05 | -19.4962 | -0.13733 | -121.6141 | 0.027466 | -120.8771 | -121.5729 | -121.7056 | -21.3638 | 0.004578 | -121.6965 | -0.013733 | -121.1975 | -121.3257 | -121.5454 | -0.013733 | -0.2655 | -0.10071 | 0.72327 | -0.10529 | 0.027466 | -0.091552 | 0.041199 | -0.09613 | -0.1236 | -0.14191 | 0.40283 | 0.054932 | 0.27466 | 0.15106 | 0.37079 | 0.737 | 121.6415 | 0.49896 | 121.6827 | 121.4767 | 121.701 | 121.463 | 121.6049 | -121.7422 | -121.8246 | 121.6278 | 121.5866 | 102.1042 | 100.2365
1010.2031 | 121.8887 | -121.5546 | 0.082397 | -0.0016785 | 6.9665 | 0.069105 | 0.06386 | 0.00099557 | -0.0041913 | -0.0015124 | -0.0036011 | 0.0003098 | 0.06673 | 0.061056 | -0.0059857 | 0.022112 | 0.00012601 | -19.4824 | -0.14191 | -121.5408 | 0.1236 | -120.7718 | -121.4767 | -121.6324 | -21.2677 | -0.064087 | -121.6644 | 0.11902 | -121.0831 | -121.1884 | -121.4264 | 0.013732 | -0.2243 | 0.041199 | 0.78278 | -0.07782 | 0.077819 | -0.091552 | 0.064087 | -0.10986 | -0.14648 | 0.036622 | 0.4715 | 0.12817 | 0.36621 | 0.23804 | 0.47607 | 0.76904 | 121.6644 | 0.58136 | 121.7834 | 121.3989 | 121.6003 | 121.4127 | 121.4905 | -121.6232 | -121.7468 | 121.6782 | 121.6736 | 102.0721 | 100.2869
1011.875 | 121.7926 | -121.6278 | 0.10529 | 0.044098 | 6.9688 | 0.066969 | 0.064929 | 0.00099557 | -0.0054731 | -0.0012988 | 0.017761 | 0.0033004 | 0.067798 | 0.058706 | -0.0087629 | 0.022326 | -0.00436 | -19.4733 | -0.07782 | -121.6141 | 0.054932 | -120.8633 | -121.5729 | -121.7102 | -21.3638 | 0.009155 | -121.701 | 0.013733 | -121.2021 | -121.3303 | -121.5225 | 0.013733 | -0.18311 | -0.050354 | 0.76447 | -0.082397 | 0.054932 | -0.09613 | 0.041199 | -0.073242 | -0.096131 | -0.091553 | 0.42572 | 0.10529 | 0.29755 | 0.17853 | 0.37079 | 0.75073 | 121.669 | 0.49896 | 121.7148 | 121.5363 | 121.7102 | 121.55 | 121.637 | -121.7194 | -121.8063 | 121.6827 | 121.6415 | 102.1545 | 100.264
1013.6094 | 121.8979 | -121.5546 | 0.082397 | -0.009308 | 6.9695 | 0.067823 | 0.061938 | 0.0014228 | -0.0076093 | -0.0030078 | -0.0036011 | 9.6204e-05 | 0.068225 | 0.065114 | -0.0049175 | 0.024462 | -0.0028646 | -19.4458 | -0.16937 | -121.5775 | 0.16479 | -120.7306 | -121.463 | -121.6095 | -21.2402 | -0.059509 | -121.6644 | 0.13733 | -121.0602 | -121.1838 | -121.4264 | -0.022889 | -0.25177 | 0.082398 | 0.82397 | -0.054932 | 0.091552 | -0.032043 | 0.11444 | -0.10986 | -0.14191 | 0.054932 | 0.49438 | 0.12817 | 0.37079 | 0.23804 | 0.48065 | 0.84686 | 121.7422 | 0.60425 | 121.8018 | 121.4081 | 121.6049 | 121.3852 | 121.4951 | -121.6599 | -121.7468 | 121.7194 | 121.6919 | 102.1088 | 100.3143
1015.3438 | 121.8704 | -121.5775 | 0.07782 | 0.036468 | 6.9709 | 0.069959 | 0.06386 | 0.0020636 | -0.0031231 | -0.00044443 | 0.020813 | 0.0005234 | 0.069507 | 0.058065 | -0.0047039 | 0.022326 | -0.003292 | -19.4412 | -0.14648 | -121.5912 | 0.17853 | -120.7123 | -121.4813 | -121.6187 | -21.2723 | -0.018311 | -121.6782 | 0.13275 | -121.0968 | -121.2341 | -121.4447 | -0.013733 | -0.2243 | 0.10071 | 0.86517 | -0.041198 | 0.096131 | -0.027465 | 0.10986 | -0.10071 | -0.096131 | 0.054931 | 0.48065 | 0.13275 | 0.34332 | 0.23346 | 0.44403 | 0.87891 | 121.7697 | 0.58136 | 121.8109 | 121.4447 | 121.6599 | 121.431 | 121.5591 | -121.669 | -121.756 | 121.756 | 121.7102 | 102.1362 | 100.3052
1017.0156 | 121.8933 | -121.5546 | 0.086975 | -0.009308 | 6.9688 | 0.069532 | 0.06322 | 0.00078177 | -0.0071821 | -0.00087163 | -0.0036011 | 0.0026596 | 0.06673 | 0.058919 | -0.0029949 | 0.022539 | 0.00033961 | -19.4778 | -0.16022 | -121.5363 | 0.16479 | -120.7581 | -121.5088 | -121.6415 | -21.3089 | -0.041199 | -121.6461 | 0.15564 | -121.0968 | -121.2112 | -121.4218 | 0.01831 | -0.24719 | 0.07782 | 0.79651 | -0.086976 | 0.045776 | -0.10529 | 0.027466 | -0.091553 | -0.12817 | 0.068665 | 0.45776 | 0.13275 | 0.34332 | 0.2243 | 0.43488 | 0.7782 | 121.701 | 0.54932 | 121.8018 | 121.376 | 121.6049 | 121.3943 | 121.5134 | -121.6232 | -121.7331 | 121.7194 | 121.7102 | 102.0767 | 100.2457
1018.75 | 121.8796 | -121.5591 | 0.082397 | -0.009308 | 6.969 | 0.067823 | 0.064288 | 0.0014228 | -0.0078229 | -0.0012988 | -0.00054933 | 0.0005234 | 0.071002 | 0.058065 | -0.0036359 | 0.023607 | -0.0030784 | -19.4962 | -0.12817 | -121.5729 | 0.09613 | -120.8405 | -121.5454 | -121.6827 | -21.405 | -0.032043 | -121.6599 | 0.1236 | -121.1105 | -121.2387 | -121.4264 | -0.013733 | -0.21057 | 0.013733 | 0.71869 | -0.1236 | 0.013733 | -0.10986 | 0.027466 | -0.10071 | -0.11444 | 0.041199 | 0.44861 | 0.13275 | 0.32044 | 0.23346 | 0.42114 | 0.73242 | 121.669 | 0.54932 | 121.7834 | 121.4447 | 121.6278 | 121.431 | 121.5271 | -121.6553 | -121.7422 | 121.6553 | 121.6827 | 102.063 | 100.1541
1020.4844 | 121.8063 | -121.582 | 0.11444 | 0.01358 | 6.9712 | 0.066328 | 0.06386 | 0.0033454 | -0.0076093 | -0.0021532 | 0.0025025 | 0.000737 | 0.066516 | 0.058706 | -0.0074811 | 0.022539 | -0.0013694 | -19.4092 | -0.11444 | -121.5912 | 0.12817 | -120.813 | -121.5454 | -121.669 | -21.405 | -0.018311 | -121.6782 | 0.068665 | -121.1563 | -121.2845 | -121.4905 | -0.009156 | -0.22888 | 0.013733 | 0.76904 | -0.086975 | 0.036621 | -0.077819 | 0.045777 | -0.096131 | -0.13275 | -0.045776 | 0.42572 | 0.091552 | 0.29755 | 0.18768 | 0.39368 | 0.7782 | 121.7194 | 0.52185 | 121.7468 | 121.4767 | 121.6599 | 121.4676 | 121.5637 | -121.7056 | -121.7926 | 121.7102 | 121.6507 | 102.1729 | 100.177
1022.1719 | 121.8475 | -121.582 | 0.091553 | -0.009308 | 6.9686 | 0.066755 | 0.061083 | -0.00092703 | -0.0061139 | 0.00062377 | -0.00054933 | 0.0013778 | 0.069293 | 0.066396 | -0.0081219 | 0.022112 | -0.0013694 | -19.4321 | -0.14648 | -121.5546 | 0.15106 | -120.7581 | -121.4722 | -121.6278 | -21.4325 | -0.036621 | -121.6827 | 0.10529 | -121.0876 | -121.2158 | -121.4767 | 0.027466 | -0.23804 | 0.059509 | 0.82397 | -0.045777 | 0.10986 | -0.073243 | 0.082397 | -0.10071 | -0.12817 | 0.013733 | 0.49438 | 0.10528 | 0.36621 | 0.20599 | 0.46692 | 0.79651 | 121.7056 | 0.59509 | 121.788 | 121.4081 | 121.6461 | 121.4355 | 121.5454 | -121.6461 | -121.7743 | 121.7331 | 121.6873 | 102.15 | 100.1495
1023.9062 | 121.875 | -121.5775 | 0.086975 | 0.005951 | 6.9699 | 0.066541 | 0.062151 | 0.00014097 | -0.0059003 | 0.001051 | -0.00054933 | -0.0007584 | 0.068438 | 0.062978 | -0.0064129 | 0.021898 | -0.006069 | -19.4321 | -0.16022 | -121.5546 | 0.16937 | -120.7489 | -121.4722 | -121.6003 | -21.4416 | -0.054932 | -121.6599 | 0.1236 | -121.0739 | -121.2158 | -121.4401 | 0.022889 | -0.24719 | 0.082398 | 0.82855 | -0.022888 | 0.10529 | -0.045777 | 0.082397 | -0.082397 | -0.14191 | 0.036621 | 0.50354 | 0.13733 | 0.36163 | 0.21973 | 0.44403 | 0.80566 | 121.7239 | 0.58594 | 121.7834 | 121.3943 | 121.6049 | 121.4172 | 121.5225 | -121.6415 | -121.7468 | 121.7468 | 121.7011 | 102.1454 | 100.1358
1025.5781 | 121.9025 | -121.5866 | 0.07782 | 0.005951 | 6.9667 | 0.066328 | 0.063647 | -0.0037042 | -0.0063275 | -0.0012988 | -0.00054933 | -0.0003312 | 0.06673 | 0.058492 | -0.0068403 | 0.022753 | 0.00076681 | -19.5236 | -0.16022 | -121.55 | 0.14191 | -120.7718 | -121.4813 | -121.6324 | -21.4966 | -0.041199 | -121.669 | 0.1236 | -121.0831 | -121.2067 | -121.4584 | 0.036621 | -0.23804 | 0.064087 | 0.81482 | -0.045776 | 0.10529 | -0.082397 | 0.068665 | -0.082397 | -0.11902 | 0.045776 | 0.50354 | 0.12817 | 0.37994 | 0.21057 | 0.46234 | 0.7782 | 121.6919 | 0.58594 | 121.7926 | 121.3898 | 121.6278 | 121.4264 | 121.5454 | -121.6278 | -121.7468 | 121.7285 | 121.7102 | 102.063 | 100.09
1027.3125 | 121.9025 | -121.5591 | 0.068665 | -0.009308 | 6.9695 | 0.068678 | 0.066638 | 0.00014097 | -0.0041913 | -0.0036486 | -0.0036011 | 0.0020188 | 0.066516 | 0.062551 | -0.0042767 | 0.02318 | -0.0058554 | -19.4733 | -0.15564 | -121.5683 | 0.14648 | -120.7764 | -121.5179 | -121.6461 | -21.5515 | -0.050354 | -121.6644 | 0.13733 | -121.0968 | -121.2296 | -121.4218 | -0.009155 | -0.22431 | 0.077819 | 0.78278 | -0.086975 | 0.041199 | -0.07782 | 0.050354 | -0.10529 | -0.11902 | 0.068664 | 0.46234 | 0.13733 | 0.32959 | 0.24262 | 0.43488 | 0.79193 | 121.7148 | 0.56763 | 121.8018 | 121.4127 | 121.6141 | 121.4035 | 121.5088 | -121.637 | -121.7331 | 121.7056 | 121.6965 | 102.0859 | 100.0076
1029.0469 | 121.843 | -121.5775 | 0.073242 | 0.036468 | 6.9724 | 0.069319 | 0.062792 | 0.00035457 | -0.0026959 | -0.00065803 | 0.0086061 | 0.0015914 | 0.069079 | 0.064901 | -0.0044903 | 0.024248 | -0.0028646 | -19.4916 | -0.14648 | -121.5546 | 0.13275 | -120.7809 | -121.5317 | -121.6507 | -21.5836 | -0.027466 | -121.6644 | 0.086975 | -121.1426 | -121.2616 | -121.4767 | 0.022889 | -0.21973 | 0.059509 | 0.79651 | -0.073242 | 0.045777 | -0.096131 | 0.022888 | -0.086975 | -0.10071 | 0.013733 | 0.43488 | 0.10071 | 0.31586 | 0.18768 | 0.40283 | 0.77362 | 121.6873 | 0.52185 | 121.7514 | 121.4081 | 121.637 | 121.431 | 121.55 | -121.6278 | -121.7377 | 121.7102 | 121.6644 | 102.0859 | 99.9939
1030.7188 | 121.8842 | -121.582 | 0.07782 | -0.009308 | 6.9703 | 0.065473 | 0.062151 | -0.0013544 | -0.0080365 | 0.00019657 | -0.0066527 | 0.0015914 | 0.064807 | 0.058278 | -0.0083355 | 0.022112 | -0.0030784 | -19.4138 | -0.16022 | -121.5775 | 0.17853 | -120.7352 | -121.4676 | -121.6141 | -21.5607 | -0.050354 | -121.6507 | 0.13275 | -121.0876 | -121.2021 | -121.4401 | 0.004577 | -0.23804 | 0.10071 | 0.84686 | -0.032044 | 0.11444 | -0.036621 | 0.10986 | -0.068665 | -0.12817 | 0.054931 | 0.49438 | 0.14191 | 0.37994 | 0.21057 | 0.44861 | 0.84229 | 121.756 | 0.56305 | 121.7834 | 121.4172 | 121.6003 | 121.4218 | 121.5317 | -121.6553 | -121.7285 | 121.7606 | 121.7148 | 102.1683 | 100.0214
1032.4531 | 121.8613 | -121.5729 | 0.07782 | 0.01358 | 6.9729 | 0.0706 | 0.064929 | -0.00028623 | -0.0037641 | -0.0025806 | 0.014709 | 0.0030868 | 0.070361 | 0.06191 | -0.0053449 | 0.022112 | -0.00030119 | -19.4458 | -0.13275 | -121.5683 | 0.1831 | -120.7443 | -121.4996 | -121.6095 | -21.6248 | -0.027466 | -121.6919 | 0.10529 | -121.1334 | -121.2479 | -121.4493 | 0.004578 | -0.21057 | 0.10528 | 0.82855 | -0.036621 | 0.073242 | -0.041199 | 0.068664 | -0.11902 | -0.10529 | 0.027466 | 0.43945 | 0.1236 | 0.32501 | 0.24262 | 0.44403 | 0.82397 | 121.7514 | 0.55847 | 121.7972 | 121.4355 | 121.6644 | 121.4401 | 121.5454 | -121.6461 | -121.7697 | 121.756 | 121.6782 | 102.1271 | 99.9481
1034.125 | 121.8018 | -121.5912 | 0.10071 | 0.036468 | 6.9712 | 0.064832 | 0.064501 | 0.0020636 | -0.0037641 | -0.00023063 | 0.011658 | 0.0039414 | 0.06972 | 0.055715 | -0.0081219 | 0.024462 | 0.00033961 | -19.4092 | -0.082397 | -121.6095 | 0.10071 | -120.845 | -121.5637 | -121.701 | -21.6888 | 0.013733 | -121.6965 | 0.032043 | -121.1563 | -121.2891 | -121.4767 | -0.01831 | -0.18311 | 0 | 0.74616 | -0.10986 | 0.027466 | -0.091553 | 0.045776 | -0.10528 | -0.086975 | -0.068665 | 0.43488 | 0.11444 | 0.30213 | 0.21973 | 0.40741 | 0.76447 | 121.7102 | 0.54016 | 121.7285 | 121.5271 | 121.7102 | 121.5088 | 121.6049 | -121.7102 | -121.7972 | 121.6919 | 121.6232 | 102.182 | 99.9023
1035.8438 | 121.8933 | -121.5454 | 0.068665 | -0.0016785 | 6.9714 | 0.069959 | 0.063647 | -0.00071343 | -0.0061139 | -0.0015124 | -0.00054933 | 0.0009506 | 0.067157 | 0.061696 | -0.0042767 | 0.023607 | -0.0017966 | -19.3863 | -0.16022 | -121.55 | 0.14648 | -120.7809 | -121.5271 | -121.6415 | -21.6934 | -0.050354 | -121.6599 | 0.13275 | -121.0831 | -121.2296 | -121.4081 | -0.004578 | -0.22888 | 0.077819 | 0.76447 | -0.096131 | 0.01831 | -0.091553 | 0.022888 | -0.11444 | -0.11902 | 0.064086 | 0.46234 | 0.13733 | 0.31586 | 0.25177 | 0.4303 | 0.76904 | 121.6965 | 0.57678 | 121.7926 | 121.3898 | 121.6095 | 121.3852 | 121.4951 | -121.6187 | -121.7285 | 121.6919 | 121.6782 | 102.1591 | 99.852
1037.5156 | 121.8887 | -121.5637 | 0.082397 | -0.0016785 | 6.9712 | 0.068678 | 0.064074 | 0.0054816 | -0.0033369 | -0.0027942 | -0.0036011 | 9.6204e-05 | 0.065448 | 0.062124 | -0.0066265 | 0.024676 | 0.0014078 | -19.4412 | -0.15106 | -121.5866 | 0.15564 | -120.7764 | -121.5179 | -121.6461 | -21.6934 | -0.073242 | -121.6461 | 0.14648 | -121.0968 | -121.2296 | -121.3943 | -0.022888 | -0.23346 | 0.073243 | 0.78735 | -0.082397 | 0.045777 | -0.059509 | 0.068665 | -0.082397 | -0.15564 | 0.064087 | 0.46692 | 0.16937 | 0.33417 | 0.25177 | 0.41657 | 0.81024 | 121.7422 | 0.54932 | 121.7926 | 121.4355 | 121.5729 | 121.4127 | 121.4905 | -121.669 | -121.7285 | 121.7194 | 121.7102 | 102.1225 | 99.8703
1039.25 | 121.8109 | -121.6141 | 0.10529 | 0.01358 | 6.9727 | 0.068037 | 0.064715 | -0.00092703 | -0.0069683 | -0.0027942 | 0.0055543 | 0.003514 | 0.066302 | 0.054006 | -0.0083355 | 0.022539 | -0.002651 | -19.4458 | -0.11444 | -121.6141 | 0.10071 | -120.8176 | -121.5546 | -121.6827 | -21.7346 | -0.004578 | -121.6965 | 0.050354 | -121.1517 | -121.2891 | -121.4905 | 0 | -0.21973 | -0.004578 | 0.79651 | -0.068664 | 0.05951 | -0.068664 | 0.05951 | -0.082397 | -0.10986 | -0.054932 | 0.46234 | 0.1236 | 0.32501 | 0.20599 | 0.40741 | 0.79651 | 121.7148 | 0.54474 | 121.7468 | 121.4996 | 121.6919 | 121.4996 | 121.6095 | -121.7194 | -121.8018 | 121.7148 | 121.6644 | 102.1683 | 99.8795
1040.9844 | 121.8658 | -121.5591 | 0.07782 | 0.01358 | 6.9727 | 0.066755 | 0.064501 | 0.00014097 | -0.0059003 | -0.0019396 | 0.0025025 | -0.0001174 | 0.068225 | 0.061269 | -0.0047039 | 0.02318 | -0.0022238 | -19.4778 | -0.13275 | -121.582 | 0.091553 | -120.8221 | -121.5591 | -121.6644 | -21.8124 | -0.045776 | -121.6736 | 0.073242 | -121.1288 | -121.2479 | -121.4539 | -0.022888 | -0.21057 | 0.013733 | 0.737 | -0.10529 | 0 | -0.082398 | 0.022888 | -0.11444 | -0.1236 | -0.004578 | 0.4303 | 0.10529 | 0.31128 | 0.21973 | 0.42572 | 0.75989 | 121.6736 | 0.54474 | 121.7468 | 121.4493 | 121.6278 | 121.4264 | 121.5134 | -121.6599 | -121.7514 | 121.6507 | 121.6324 | 102.0813 | 99.7467
1042.7344 | 121.8658 | -121.582 | 0.09613 | 0.005951 | 6.9703 | 0.067396 | 0.06322 | -0.00092703 | -0.0059003 | 0.00083737 | 0.0055543 | 0.0022324 | 0.068438 | 0.066183 | -0.0083355 | 0.021471 | -0.0022238 | -19.5007 | -0.13733 | -121.5958 | 0.09613 | -120.8313 | -121.5454 | -121.669 | -21.8903 | -0.036621 | -121.7102 | 0.064087 | -121.1472 | -121.2845 | -121.4676 | -0.013733 | -0.23346 | 0 | 0.75073 | -0.086975 | 0.036621 | -0.073242 | 0.050354 | -0.12817 | -0.13275 | -0.032043 | 0.43488 | 0.11444 | 0.29755 | 0.24262 | 0.42572 | 0.76447 | 121.6919 | 0.56305 | 121.7743 | 121.4584 | 121.6736 | 121.4447 | 121.5454 | -121.6919 | -121.8063 | 121.6782 | 121.6461 | 102.0813 | 99.6918
1044.4062 | 121.8842 | -121.5775 | 0.07782 | 0.01358 | 6.9686 | 0.067396 | 0.062792 | -0.0017816 | -0.0063275 | -0.0021532 | -0.00054933 | 0.0011642 | 0.067157 | 0.062551 | -0.0068403 | 0.021898 | -0.0039328 | -19.4778 | -0.15106 | -121.5775 | 0.11444 | -120.8084 | -121.5271 | -121.6782 | -21.904 | -0.050354 | -121.7102 | 0.10071 | -121.0922 | -121.2158 | -121.431 | 0 | -0.22888 | 0.036621 | 0.76904 | -0.10071 | 0.050354 | -0.10071 | 0.050354 | -0.13275 | -0.12817 | 0.022888 | 0.48523 | 0.14648 | 0.36163 | 0.27924 | 0.49439 | 0.76904 | 121.6919 | 0.61798 | 121.8109 | 121.4264 | 121.6599 | 121.4264 | 121.5271 | -121.6553 | -121.788 | 121.6919 | 121.6782 | 102.0996 | 99.6735
1046.1406 | 121.907 | -121.5546 | 0.082397 | 0.005951 | 6.972 | 0.067823 | 0.064288 | 0.0014228 | -0.0050457 | -0.00044443 | -0.0066527 | 0.0020188 | 0.067157 | 0.065114 | -0.0047039 | 0.026171 | -0.0039328 | -19.4824 | -0.14648 | -121.582 | 0.13275 | -120.813 | -121.5271 | -121.6782 | -21.9086 | -0.036621 | -121.6415 | 0.11902 | -121.0922 | -121.2296 | -121.4264 | -0.027466 | -0.22888 | 0.050354 | 0.74158 | -0.1236 | 0.027465 | -0.096131 | 0.054931 | -0.086976 | -0.11902 | 0.036622 | 0.46234 | 0.12817 | 0.32501 | 0.21515 | 0.41199 | 0.76904 | 121.7148 | 0.54932 | 121.7606 | 121.4355 | 121.6049 | 121.4081 | 121.5179 | -121.6644 | -121.7239 | 121.6873 | 121.6736 | 102.0721 | 99.646
1047.8906 | 121.7697 | -121.6049 | 0.09613 | -0.009308 | 6.972 | 0.06761 | 0.065356 | 0.00056817 | -0.0044049 | -0.00023063 | -0.00054933 | 0.0026596 | 0.068438 | 0.053152 | -0.0047039 | 0.024462 | -0.0054282 | -19.4504 | -0.13275 | -121.5866 | 0.064087 | -120.8908 | -121.6278 | -121.7377 | -22.0276 | -0.013733 | -121.6827 | 0 | -121.2296 | -121.3486 | -121.5317 | 0.01831 | -0.22888 | -0.032043 | 0.71411 | -0.13275 | -0.022889 | -0.15106 | -0.041199 | -0.07782 | -0.10986 | -0.09613 | 0.37537 | 0.073242 | 0.25635 | 0.15106 | 0.33417 | 0.6958 | 121.6507 | 0.45319 | 121.6827 | 121.4539 | 121.669 | 121.4722 | 121.5912 | -121.6827 | -121.7789 | 121.669 | 121.6049 | 102.1545 | 99.5773
1049.625 | 121.8063 | -121.5912 | 0.10071 | 0.01358 | 6.9744 | 0.066969 | 0.065142 | 0.0012092 | -0.0078229 | -0.00065803 | -0.00054933 | 0.0045822 | 0.069079 | 0.054647 | -0.0074811 | 0.020189 | -0.0058554 | -19.4229 | -0.10986 | -121.6003 | 0.091553 | -120.8359 | -121.5729 | -121.6827 | -22.0047 | -0.013733 | -121.6919 | 0.036621 | -121.1792 | -121.312 | -121.5134 | -0.009155 | -0.21057 | -0.009155 | 0.75531 | -0.091552 | 0.018311 | -0.082397 | 0.027466 | -0.10071 | -0.11444 | -0.064087 | 0.41199 | 0.07782 | 0.27924 | 0.17853 | 0.37994 | 0.76447 | 121.6919 | 0.5127 | 121.7285 | 121.4905 | 121.6782 | 121.4813 | 121.5775 | -121.701 | -121.7926 | 121.6827 | 121.6278 | 102.1683 | 99.5865
1051.2969 | 121.8155 | -121.6049 | 0.11902 | 0.01358 | 6.9733 | 0.068678 | 0.064074 | 0.0031318 | -0.0076093 | 0.00019657 | 0.0025025 | 0.0013778 | 0.069293 | 0.053579 | -0.0079083 | 0.022326 | -0.0030784 | -19.3863 | -0.13275 | -121.6141 | 0.11902 | -120.8359 | -121.55 | -121.6919 | -22.0276 | -0.027466 | -121.6873 | 0.036621 | -121.1792 | -121.3028 | -121.4951 | -0.009156 | -0.25177 | 0 | 0.76904 | -0.086976 | 0.054931 | -0.07782 | 0.064087 | -0.082398 | -0.14649 | -0.082398 | 0.42572 | 0.10986 | 0.30212 | 0.19226 | 0.38452 | 0.7782 | 121.7331 | 0.50812 | 121.7239 | 121.4813 | 121.6599 | 121.4722 | 121.5775 | -121.7331 | -121.8063 | 121.7239 | 121.6415 | 102.2186 | 99.5773
1053.0312 | 121.788 | -121.6049 | 0.11444 | -0.0016785 | 6.972 | 0.06825 | 0.059588 | -0.00028623 | -0.0073957 | -0.0021532 | -0.00054933 | 0.0013778 | 0.068652 | 0.051015 | -0.0083355 | 0.02083 | -0.0028646 | -19.4229 | -0.16022 | -121.5912 | 0.09613 | -120.8038 | -121.5134 | -121.6553 | -22.0871 | -0.018311 | -121.7102 | 0.036621 | -121.1655 | -121.2799 | -121.5042 | 0.013732 | -0.27466 | -0.018311 | 0.80109 | -0.050354 | 0.091552 | -0.064086 | 0.07782 | -0.10529 | -0.13275 | -0.07782 | 0.43945 | 0.10071 | 0.32501 | 0.20599 | 0.4303 | 0.78735 | 121.6873 | 0.54474 | 121.7468 | 121.431 | 121.6919 | 121.4447 | 121.5866 | -121.7056 | -121.8246 | 121.701 | 121.6415 | 102.182 | 99.5178
1054.7812 | 121.8155 | -121.6095 | 0.082397 | 0.02121 | 6.9729 | 0.068678 | 0.064074 | 0.00099557 | -0.0035505 | -0.00087163 | 0.0055543 | 0.0013778 | 0.070147 | 0.056569 | -0.0070539 | 0.021898 | -0.00094199 | -19.3634 | -0.11444 | -121.6003 | 0.09613 | -120.8267 | -121.5637 | -121.6736 | -22.0642 | -0.009155 | -121.6965 | 0.064087 | -121.1517 | -121.2936 | -121.4767 | 0.009155 | -0.19684 | 0.013733 | 0.78278 | -0.064087 | 0.045776 | -0.073242 | 0.036621 | -0.086975 | -0.091552 | -0.01831 | 0.45776 | 0.13275 | 0.31586 | 0.21973 | 0.40283 | 0.77362 | 121.6965 | 0.54474 | 121.7606 | 121.4859 | 121.6873 | 121.4951 | 121.6003 | -121.6827 | -121.7789 | 121.7056 | 121.6736 | 102.2461 | 99.5453
1056.4531 | 121.7606 | -121.6141 | 0.10529 | -0.0016785 | 6.9718 | 0.067823 | 0.065356 | -0.0011408 | -0.0046185 | -0.00023063 | -0.0036011 | 0.002446 | 0.069934 | 0.061483 | -0.0059857 | 0.021898 | -0.0020102 | -19.4046 | -0.11444 | -121.6049 | 0.045776 | -120.8954 | -121.6095 | -121.7468 | -22.2336 | -0.018311 | -121.6873 | 0.009155 | -121.225 | -121.344 | -121.5225 | 0.009156 | -0.21973 | -0.05951 | 0.71869 | -0.13275 | 0.004578 | -0.14191 | -0.004578 | -0.073242 | -0.1236 | -0.096131 | 0.3891 | 0.091553 | 0.27008 | 0.16479 | 0.34332 | 0.70953 | 121.6507 | 0.46234 | 121.6965 | 121.4905 | 121.669 | 121.4996 | 121.5958 | -121.7102 | -121.7926 | 121.6599 | 121.6232 | 102.2095 | 99.3805
1058.2031 | 121.8246 | -121.5912 | 0.11444 | 0.028839 | 6.9739 | 0.068464 | 0.06386 | -0.0028498 | -0.0039777 | -0.00044443 | 0.0055543 | 0.0022324 | 0.068652 | 0.050588 | -0.0047039 | 0.021685 | -0.001583 | -19.3634 | -0.10529 | -121.5775 | 0.10529 | -120.813 | -121.5546 | -121.6965 | -22.1832 | -0.013733 | -121.7056 | 0.064087 | -121.1426 | -121.2845 | -121.4813 | 0.013733 | -0.21973 | -0.009155 | 0.7782 | -0.10528 | 0.036622 | -0.11902 | 0.022889 | -0.11444 | -0.12817 | -0.050354 | 0.44861 | 0.10986 | 0.3067 | 0.2243 | 0.42114 | 0.76447 | 121.6827 | 0.56305 | 121.7697 | 121.4722 | 121.6919 | 121.4859 | 121.5775 | -121.6919 | -121.8201 | 121.6965 | 121.6553 | 102.2278 | 99.408
1059.9375 | 121.8246 | -121.5912 | 0.086975 | -0.009308 | 6.9727 | 0.069105 | 0.061297 | -0.0019952 | -0.0059003 | -0.0030078 | -0.0066527 | 0.0013778 | 0.067584 | 0.062124 | -0.0076947 | 0.019976 | 0.00012601 | -19.3817 | -0.15564 | -121.5683 | 0.11902 | -120.7718 | -121.4905 | -121.6415 | -22.2519 | -0.027466 | -121.6873 | 0.054932 | -121.1288 | -121.2662 | -121.4996 | 0.022889 | -0.24261 | 0.032044 | 0.8194 | -0.050354 | 0.10071 | -0.073243 | 0.077819 | -0.09613 | -0.11444 | -0.032043 | 0.46234 | 0.091553 | 0.32501 | 0.18768 | 0.42114 | 0.79651 | 121.6873 | 0.55847 | 121.7422 | 121.4127 | 121.6599 | 121.4355 | 121.5637 | -121.6553 | -121.7743 | 121.7102 | 121.6461 | 102.2095 | 99.3393
1061.6719 | 121.7743 | -121.6324 | 0.11444 | -0.009308 | 6.9712 | 0.065046 | 0.062151 | -7.2628e-05 | -0.0071821 | -0.0025806 | -0.0036011 | -0.0011856 | 0.068438 | 0.054647 | -0.0091901 | 0.020189 | -0.0022238 | -19.3909 | -0.1236 | -121.6324 | 0.022888 | -120.8954 | -121.5866 | -121.7239 | -22.3663 | -0.009155 | -121.7148 | -0.022888 | -121.1975 | -121.3348 | -121.5454 | 0 | -0.23804 | -0.091553 | 0.737 | -0.091553 | 0.045776 | -0.091553 | 0.045776 | -0.082398 | -0.1236 | -0.13733 | 0.43488 | 0.086975 | 0.29755 | 0.16937 | 0.37994 | 0.737 | 121.6553 | 0.51727 | 121.6919 | 121.5088 | 121.7056 | 121.5088 | 121.6232 | -121.7468 | -121.8292 | 121.6553 | 121.6095 | 102.2415 | 99.2661
1063.3438 | 121.8933 | -121.5683 | 0.068665 | -0.009308 | 6.9716 | 0.066969 | 0.062579 | -0.0017816 | -0.0076093 | -0.0012988 | -0.0036011 | 0.0011642 | 0.066943 | 0.058278 | -0.0029949 | 0.02318 | -0.0011558 | -19.3726 | -0.12817 | -121.582 | 0.11902 | -120.813 | -121.55 | -121.6736 | -22.3389 | -0.054932 | -121.6736 | 0.14191 | -121.0922 | -121.2296 | -121.4172 | -0.013733 | -0.19684 | 0.050354 | 0.75531 | -0.10529 | 0.01831 | -0.091553 | 0.032043 | -0.10529 | -0.1236 | 0.073242 | 0.47607 | 0.15106 | 0.33875 | 0.25635 | 0.44403 | 0.76904 | 121.701 | 0.58136 | 121.8155 | 121.4539 | 121.6187 | 121.4401 | 121.5134 | -121.6507 | -121.7422 | 121.6873 | 121.7102 | 102.1957 | 99.2294
1065.0781 | 121.8979 | -121.5683 | 0.082397 | -0.0016785 | 6.9692 | 0.065046 | 0.06322 | -0.0017816 | -0.0069683 | -0.00065803 | -0.0066527 | 0.0009506 | 0.065875 | 0.059987 | -0.0055585 | 0.022753 | -0.0013694 | -19.3359 | -0.15106 | -121.55 | 0.15564 | -120.7535 | -121.4722 | -121.6232 | -22.3297 | -0.050354 | -121.6644 | 0.10529 | -121.0648 | -121.1929 | -121.4447 | 0.01831 | -0.23346 | 0.073243 | 0.81482 | -0.054932 | 0.09613 | -0.073242 | 0.07782 | -0.096131 | -0.13275 | 0.022889 | 0.50354 | 0.1236 | 0.37537 | 0.21973 | 0.4715 | 0.79651 | 121.7056 | 0.59967 | 121.7697 | 121.3989 | 121.6141 | 121.4172 | 121.5179 | -121.6324 | -121.7468 | 121.7239 | 121.6736 | 102.2324 | 99.2386
1066.8125 | 121.7972 | -121.6278 | 0.12817 | -0.0016785 | 6.9724 | 0.06825 | 0.060442 | 0.00014097 | -0.0069683 | -0.0032214 | -0.0036011 | 0.0003098 | 0.067798 | 0.053365 | -0.0081219 | 0.021898 | -0.0013694 | -19.3085 | -0.16022 | -121.5958 | 0.091553 | -120.8313 | -121.5408 | -121.6736 | -22.4258 | -0.022888 | -121.6827 | 0.018311 | -121.1655 | -121.3028 | -121.5317 | 0.032044 | -0.28839 | -0.036621 | 0.79651 | -0.045776 | 0.086975 | -0.07782 | 0.054931 | -0.054931 | -0.15106 | -0.10986 | 0.46234 | 0.096131 | 0.32501 | 0.15106 | 0.37994 | 0.76447 | 121.6873 | 0.51727 | 121.701 | 121.4355 | 121.6599 | 121.4676 | 121.6049 | -121.7239 | -121.8109 | 121.7194 | 121.6461 | 102.3193 | 99.202
1068.4844 | 121.7514 | -121.6049 | 0.10986 | -0.0016785 | 6.9735 | 0.068464 | 0.065569 | -0.0013544 | -0.0033369 | -0.0010852 | -0.0036011 | 0.0050094 | 0.069079 | 0.058492 | -0.0047039 | 0.02318 | -0.0020102 | -19.4 | -0.1236 | -121.6049 | 0.013733 | -120.9274 | -121.6599 | -121.7651 | -22.5952 | -0.004578 | -121.6873 | -0.013733 | -121.2433 | -121.3715 | -121.5317 | 0 | -0.23346 | -0.09613 | 0.67749 | -0.16022 | -0.054932 | -0.16022 | -0.054932 | -0.082398 | -0.11444 | -0.1236 | 0.36163 | 0.073242 | 0.23346 | 0.15564 | 0.31586 | 0.67749 | 121.6187 | 0.44403 | 121.6736 | 121.4813 | 121.6827 | 121.4813 | 121.6003 | -121.7148 | -121.7972 | 121.6187 | 121.5912 | 102.2049 | 99.0097
1070.2188 | 121.9025 | -121.5775 | 0.064087 | -0.0016785 | 6.9703 | 0.066541 | 0.062579 | -0.0030634 | -0.0054731 | -0.00065803 | -0.0066527 | 9.6204e-05 | 0.06737 | 0.060415 | -0.0047039 | 0.024462 | -0.0013694 | -19.368 | -0.16022 | -121.5591 | 0.14648 | -120.7809 | -121.4813 | -121.6232 | -22.4716 | -0.068665 | -121.6919 | 0.1236 | -121.0785 | -121.1838 | -121.4218 | 0.018311 | -0.2243 | 0.082397 | 0.79651 | -0.045776 | 0.096131 | -0.064087 | 0.07782 | -0.11444 | -0.13275 | 0.059509 | 0.49896 | 0.15564 | 0.39368 | 0.27008 | 0.50812 | 0.7782 | 121.7056 | 0.6134 | 121.8155 | 121.3989 | 121.6232 | 121.4172 | 121.5088 | -121.6232 | -121.756 | 121.7239 | 121.7011 | 102.2095 | 99.1058
1071.9531 | 121.8933 | -121.5958 | 0.082397 | 0.005951 | 6.975 | 0.070173 | 0.064929 | 0.00035457 | -0.0024823 | 0.00041017 | 0.017761 | 0.002446 | 0.071002 | 0.066396 | -0.0040631 | 0.02318 | -0.0028646 | -19.3497 | -0.15564 | -121.582 | 0.17395 | -120.7443 | -121.4951 | -121.6324 | -22.522 | -0.041199 | -121.6827 | 0.14648 | -121.0831 | -121.2112 | -121.4264 | 0.013733 | -0.23804 | 0.091553 | 0.85144 | -0.036621 | 0.10071 | -0.050354 | 0.086975 | -0.086975 | -0.1236 | 0.064087 | 0.5127 | 0.16937 | 0.38452 | 0.25635 | 0.4715 | 0.83771 | 121.756 | 0.59967 | 121.8292 | 121.4264 | 121.6415 | 121.4401 | 121.5546 | -121.6644 | -121.7651 | 121.7697 | 121.7422 | 102.2461 | 99.0738
1073.6875 | 121.9208 | -121.5683 | 0.091553 | 0.005951 | 6.9705 | 0.066114 | 0.061938 | 0.00035457 | -0.0050457 | -0.0030078 | -0.00054933 | 0.0028732 | 0.068011 | 0.067251 | -0.0079083 | 0.023607 | -0.00030119 | -19.3954 | -0.15564 | -121.5866 | 0.15106 | -120.7672 | -121.4905 | -121.6095 | -22.5632 | -0.050354 | -121.6827 | 0.13275 | -121.0648 | -121.1655 | -121.4127 | -0.018311 | -0.24719 | 0.059509 | 0.80109 | -0.041199 | 0.077819 | -0.022888 | 0.09613 | -0.11444 | -0.14191 | 0.041198 | 0.50354 | 0.15564 | 0.40283 | 0.27008 | 0.51727 | 0.8194 | 121.7377 | 0.61798 | 121.8155 | 121.431 | 121.6324 | 121.4127 | 121.5179 | -121.6782 | -121.7743 | 121.7194 | 121.701 | 102.1729 | 99.0051
1075.3594 | 121.8704 | -121.5775 | 0.10529 | -0.009308 | 6.9748 | 0.066328 | 0.063433 | -0.0034906 | -0.0080365 | 0.00041017 | -0.00054933 | 0.0013778 | 0.06737 | 0.055501 | -0.0074811 | 0.024462 | -0.0056418 | -19.3634 | -0.17853 | -121.5866 | 0.15106 | -120.7718 | -121.4951 | -121.6415 | -22.6501 | -0.036621 | -121.6644 | 0.091553 | -121.0785 | -121.1975 | -121.4584 | -0.009155 | -0.28381 | 0.045776 | 0.80566 | -0.064087 | 0.082398 | -0.054932 | 0.091553 | -0.086975 | -0.14191 | -0.013733 | 0.49896 | 0.11902 | 0.37994 | 0.20599 | 0.46692 | 0.81482 | 121.7377 | 0.58594 | 121.756 | 121.4081 | 121.6278 | 121.3989 | 121.5408 | -121.6919 | -121.7697 | 121.7285 | 121.669 | 102.2141 | 98.9273
1077.0938 | 121.8613 | -121.6049 | 0.09613 | 0.005951 | 6.9748 | 0.068891 | 0.064501 | 0.0024908 | -0.0067547 | -0.00023063 | 0.0055543 | 9.6204e-05 | 0.069079 | 0.070669 | -0.0040631 | 0.024035 | -0.0045736 | -19.4229 | -0.14191 | -121.5729 | 0.10986 | -120.8359 | -121.5317 | -121.6782 | -22.7966 | -0.036621 | -121.7239 | 0.068665 | -121.1472 | -121.2479 | -121.4767 | 0.032043 | -0.23804 | 0.013733 | 0.76904 | -0.073243 | 0.073242 | -0.10529 | 0.041199 | -0.11902 | -0.13275 | -0.027465 | 0.45776 | 0.12817 | 0.35705 | 0.24719 | 0.47607 | 0.737 | 121.6827 | 0.57678 | 121.7926 | 121.431 | 121.6873 | 121.463 | 121.5683 | -121.669 | -121.8201 | 121.7148 | 121.6736 | 102.182 | 98.8083
1078.7656 | 121.7834 | -121.6324 | 0.10071 | -0.0016785 | 6.9733 | 0.064619 | 0.06386 | 0.0029182 | -0.0063275 | 0.00019657 | 0.017761 | 0.0047958 | 0.069934 | 0.055715 | -0.01154 | 0.021471 | -0.0011558 | -19.4229 | -0.10529 | -121.6553 | 0.045776 | -120.9045 | -121.5729 | -121.7102 | -22.8836 | 0.027466 | -121.7422 | -0.004578 | -121.1975 | -121.3165 | -121.5225 | -0.022888 | -0.20599 | -0.054932 | 0.72784 | -0.07782 | 0.059509 | -0.054932 | 0.082397 | -0.10986 | -0.073242 | -0.10529 | 0.43488 | 0.10986 | 0.31586 | 0.21973 | 0.42572 | 0.75073 | 121.701 | 0.54474 | 121.7377 | 121.55 | 121.7697 | 121.5271 | 121.6599 | -121.756 | -121.843 | 121.6782 | 121.6278 | 102.2095 | 98.7488
1080.5 | 121.875 | -121.6003 | 0.09613 | 0.028839 | 6.9705 | 0.068678 | 0.062792 | -0.001568 | -0.0052595 | -0.00087163 | 0.0055543 | 0.0020188 | 0.069293 | 0.058492 | -0.0053449 | 0.02318 | -0.0028646 | -19.4275 | -0.13733 | -121.6095 | 0.086975 | -120.845 | -121.5454 | -121.6827 | -22.9752 | -0.027466 | -121.7148 | 0.068665 | -121.1426 | -121.2616 | -121.4722 | -0.009155 | -0.23346 | -0.009155 | 0.75531 | -0.082397 | 0.054932 | -0.073242 | 0.064087 | -0.11444 | -0.1236 | -0.027465 | 0.45776 | 0.12817 | 0.33875 | 0.24262 | 0.45319 | 0.76447 | 121.6965 | 0.5722 | 121.7834 | 121.4722 | 121.6873 | 121.463 | 121.5729 | -121.7056 | -121.8109 | 121.6873 | 121.669 | 102.1729 | 98.6252
1082.25 | 121.8658 | -121.582 | 0.086975 | 0.036468 | 6.9718 | 0.068891 | 0.065569 | 0.00056817 | -0.0054731 | -0.00065803 | 0.0055543 | 0.002446 | 0.067584 | 0.058706 | -0.0081219 | 0.022753 | -0.0024374 | -19.4366 | -0.12817 | -121.5866 | 0.12817 | -120.7947 | -121.5454 | -121.669 | -23.0438 | -0.022888 | -121.7102 | 0.082397 | -121.1334 | -121.2433 | -121.4584 | -0.004578 | -0.21515 | 0.041199 | 0.78735 | -0.086975 | 0.036621 | -0.082397 | 0.041199 | -0.12817 | -0.10986 | -0.004578 | 0.44861 | 0.1236 | 0.33875 | 0.25177 | 0.46692 | 0.79193 | 121.7148 | 0.57678 | 121.7926 | 121.4584 | 121.6873 | 121.4539 | 121.5591 | -121.6736 | -121.7972 | 121.7102 | 121.6644 | 102.1454 | 98.5382
1083.9375 | 121.7834 | -121.6232 | 0.09613 | -0.0016785 | 6.9739 | 0.069105 | 0.06386 | -0.0011408 | -0.0050457 | -0.003435 | 0.0025025 | 0.0020188 | 0.06737 | 0.058065 | -0.0096173 | 0.02083 | -8.7586e-05 | -19.3771 | -0.13733 | -121.6095 | 0.10071 | -120.845 | -121.5637 | -121.7102 | -23.1949 | -0.027466 | -121.7102 | 0.009155 | -121.1746 | -121.2982 | -121.5225 | 0.013733 | -0.23346 | 0.004578 | 0.7782 | -0.086975 | 0.059509 | -0.10071 | 0.045776 | -0.086975 | -0.1236 | -0.086975 | 0.44861 | 0.10071 | 0.32501 | 0.18768 | 0.41199 | 0.76447 | 121.7102 | 0.53558 | 121.7194 | 121.4722 | 121.6827 | 121.4859 | 121.5958 | -121.7056 | -121.8063 | 121.7239 | 121.6324 | 102.2461 | 98.4283
1085.6875 | 121.8704 | -121.5866 | 0.082397 | 0.028839 | 6.9699 | 0.069746 | 0.062792 | 0.00035457 | -0.0065411 | -0.001726 | 0.0086061 | -0.0022538 | 0.068866 | 0.060415 | -0.0049175 | 0.021258 | -0.00030119 | -19.4138 | -0.15106 | -121.6187 | 0.10986 | -120.8221 | -121.5591 | -121.6507 | -23.3505 | -0.009155 | -121.6919 | 0.073242 | -121.138 | -121.2341 | -121.463 | -0.032043 | -0.23346 | 0.027466 | 0.76447 | -0.064087 | 0.027466 | -0.032044 | 0.059509 | -0.10529 | -0.091552 | -0.009155 | 0.44861 | 0.1236 | 0.35248 | 0.22888 | 0.45776 | 0.79651 | 121.7285 | 0.55389 | 121.7651 | 121.4676 | 121.6827 | 121.4355 | 121.5775 | -121.701 | -121.7743 | 121.6965 | 121.6599 | 102.1729 | 98.2361
1087.4219 | 121.9345 | -121.5958 | 0.068665 | 0.005951 | 6.9733 | 0.0706 | 0.064074 | 0.00099557 | -0.0039777 | -0.00044443 | -0.0036011 | 0.0018052 | 0.068652 | 0.063833 | -0.0019269 | 0.024035 | -0.0011558 | -19.3771 | -0.17395 | -121.5637 | 0.15106 | -120.7855 | -121.5363 | -121.6644 | -23.4467 | -0.050354 | -121.6599 | 0.14191 | -121.0831 | -121.1838 | -121.4127 | 0.032043 | -0.24261 | 0.082397 | 0.81024 | -0.068665 | 0.059509 | -0.10071 | 0.027466 | -0.064087 | -0.11902 | 0.073242 | 0.5127 | 0.1831 | 0.41199 | 0.24719 | 0.47607 | 0.7782 | 121.7148 | 0.57678 | 121.8018 | 121.3898 | 121.6095 | 121.4218 | 121.5454 | -121.6324 | -121.7285 | 121.7468 | 121.7377 | 102.2186 | 98.1491
1089.1562 | 121.8384 | -121.6003 | 0.11902 | 0.02121 | 6.9748 | 0.06761 | 0.065997 | -0.0019952 | -0.0059003 | 0.0019056 | 0.0086061 | 0.0033004 | 0.070147 | 0.053152 | -0.0094037 | 0.021898 | -0.0039328 | -19.2947 | -0.09613 | -121.6278 | 0.086975 | -120.8542 | -121.5546 | -121.6965 | -23.7534 | -0.009155 | -121.7285 | 0.050354 | -121.1517 | -121.2616 | -121.4951 | -0.027466 | -0.21515 | -0.032044 | 0.74616 | -0.09613 | 0.045777 | -0.068664 | 0.073243 | -0.12817 | -0.12817 | -0.068665 | 0.44861 | 0.10529 | 0.33875 | 0.23346 | 0.46692 | 0.77362 | 121.7148 | 0.57678 | 121.7789 | 121.5317 | 121.7194 | 121.5042 | 121.5912 | -121.7468 | -121.8475 | 121.6873 | 121.6507 | 102.3056 | 97.847
1090.8906 | 121.9208 | -121.5866 | 0.086975 | -0.0016785 | 6.9716 | 0.066541 | 0.062579 | -0.0013544 | -0.0046185 | -0.003435 | -0.00054933 | 0.0020188 | 0.066943 | 0.065114 | -0.0070539 | 0.024248 | -0.0062826 | -19.3542 | -0.16479 | -121.5866 | 0.17853 | -120.7535 | -121.4722 | -121.6049 | -23.9639 | -0.059509 | -121.6736 | 0.13275 | -121.0419 | -121.1563 | -121.431 | 0 | -0.25177 | 0.091553 | 0.83313 | -0.01831 | 0.11444 | -0.01831 | 0.11444 | -0.086975 | -0.14648 | 0.045776 | 0.54474 | 0.15564 | 0.4303 | 0.24262 | 0.51727 | 0.83313 | 121.7651 | 0.63171 | 121.8063 | 121.4218 | 121.6141 | 121.4218 | 121.5271 | -121.6736 | -121.7606 | 121.7651 | 121.7194 | 102.2324 | 97.6227
1092.5781 | 121.7926 | -121.637 | 0.10529 | -0.0016785 | 6.9742 | 0.068464 | 0.065997 | -0.0011408 | -0.0050457 | -0.0027942 | -0.0036011 | 0.0026596 | 0.068438 | 0.053152 | -0.0049175 | 0.021898 | -0.00436 | -19.3771 | -0.11444 | -121.6232 | 0.013733 | -120.9595 | -121.669 | -121.8063 | -24.4263 | -0.018311 | -121.6965 | 0.018311 | -121.2433 | -121.3303 | -121.5225 | 0.013733 | -0.21973 | -0.091553 | 0.67749 | -0.16937 | -0.032043 | -0.1831 | -0.045776 | -0.059509 | -0.1236 | -0.086975 | 0.39368 | 0.11444 | 0.3067 | 0.17395 | 0.36621 | 0.66376 | 121.637 | 0.45319 | 121.7148 | 121.5088 | 121.6782 | 121.5225 | 121.6187 | -121.7285 | -121.8018 | 121.6507 | 121.6553 | 102.2598 | 97.2107
1094.3125 | 121.8704 | -121.6095 | 0.091553 | 0.02121 | 6.9739 | 0.067396 | 0.065142 | 0.0022772 | -0.0052595 | -0.0019396 | 0.0025025 | 0.0026596 | 0.068652 | 0.070455 | -0.0057721 | 0.021685 | -0.0056418 | -19.3954 | -0.14648 | -121.6095 | 0.082397 | -120.8359 | -121.5454 | -121.6827 | -24.7192 | -0.036621 | -121.6919 | 0.073242 | -121.1517 | -121.2067 | -121.4813 | 0 | -0.23804 | -0.009156 | 0.77362 | -0.073242 | 0.064087 | -0.073242 | 0.064087 | -0.082398 | -0.12817 | -0.018311 | 0.45776 | 0.12817 | 0.40283 | 0.21057 | 0.48523 | 0.77362 | 121.6919 | 0.54016 | 121.7651 | 121.463 | 121.6553 | 121.463 | 121.5729 | -121.7011 | -121.7834 | 121.6919 | 121.6827 | 102.2141 | 96.8903
1095.9844 | 121.8018 | -121.6232 | 0.10986 | -0.009308 | 6.9724 | 0.067396 | 0.062792 | -0.0039178 | -0.0054731 | -0.00065803 | 0.0025025 | 0.0037278 | 0.069934 | 0.056783 | -0.0051313 | 0.023821 | -0.0058554 | -19.4046 | -0.1236 | -121.5958 | 0 | -120.9549 | -121.6553 | -121.7789 | -25.1724 | 0 | -121.7194 | 0.004578 | -121.2158 | -121.3028 | -121.5317 | 0.027466 | -0.23346 | -0.10986 | 0.66834 | -0.15564 | -0.032043 | -0.18311 | -0.059509 | -0.09613 | -0.10986 | -0.10529 | 0.40741 | 0.091553 | 0.32044 | 0.18768 | 0.41656 | 0.64087 | 121.5958 | 0.50354 | 121.7239 | 121.4722 | 121.7194 | 121.4996 | 121.6232 | -121.7056 | -121.8292 | 121.6232 | 121.6278 | 102.2186 | 96.4508
1097.7344 | 121.7651 | -121.6415 | 0.10986 | -0.016937 | 6.9731 | 0.069105 | 0.064288 | 0.0037726 | -0.0076093 | -0.00065803 | -0.00054933 | 0.0033004 | 0.067157 | 0.053792 | -0.0074811 | 0.022112 | -0.0011558 | -19.3954 | -0.1236 | -121.6278 | 0.004578 | -120.9503 | -121.6461 | -121.788 | -25.676 | -0.009155 | -121.7148 | -0.018311 | -121.2479 | -121.3211 | -121.5454 | 0.013733 | -0.23346 | -0.10529 | 0.69122 | -0.14648 | -0.004577 | -0.16022 | -0.01831 | -0.073242 | -0.11902 | -0.12817 | 0.39368 | 0.096131 | 0.32044 | 0.16937 | 0.39368 | 0.67749 | 121.6324 | 0.46692 | 121.6965 | 121.5042 | 121.7056 | 121.5179 | 121.6324 | -121.7377 | -121.8246 | 121.6461 | 121.6232 | 102.2461 | 95.9656
1099.4844 | 121.788 | -121.6187 | 0.11902 | -0.0016785 | 6.9746 | 0.067182 | 0.067492 | -0.0011408 | -0.0041913 | 0.00062377 | -0.00054933 | 0.0030868 | 0.070147 | 0.054006 | -0.0070539 | 0.021685 | -0.003292 | -19.3451 | -0.1236 | -121.6003 | 0.073242 | -120.8679 | -121.6232 | -121.7331 | -26.1658 | -0.013733 | -121.7377 | 0.009155 | -121.1838 | -121.2845 | -121.5134 | 0.01831 | -0.24261 | -0.045777 | 0.75073 | -0.11444 | -0.004578 | -0.13275 | -0.022888 | -0.11902 | -0.13275 | -0.10986 | 0.43487 | 0.10528 | 0.33417 | 0.2243 | 0.45319 | 0.73242 | 121.6736 | 0.55389 | 121.7468 | 121.4767 | 121.7239 | 121.4951 | 121.6049 | -121.7194 | -121.8567 | 121.6919 | 121.6278 | 102.2736 | 95.4529
1101.1562 | 121.788 | -121.6232 | 0.11902 | -0.0016785 | 6.9718 | 0.06761 | 0.064074 | -0.0013544 | -0.0046185 | -0.00023063 | 0.023865 | 0.0030868 | 0.069507 | 0.054861 | -0.0089765 | 0.021044 | 0.00012601 | -19.3954 | -0.12817 | -121.6324 | 0.054932 | -120.8862 | -121.582 | -121.7148 | -26.77 | 0.022888 | -121.756 | -0.009155 | -121.1838 | -121.2524 | -121.5225 | -0.009155 | -0.24719 | -0.064087 | 0.737 | -0.091553 | 0.041199 | -0.082398 | 0.050354 | -0.13275 | -0.096131 | -0.12817 | 0.43945 | 0.10071 | 0.37079 | 0.23346 | 0.50354 | 0.74616 | 121.6873 | 0.5722 | 121.7468 | 121.5042 | 121.7789 | 121.4951 | 121.6461 | -121.7514 | -121.875 | 121.6782 | 121.6141 | 102.2278 | 94.8532
1102.8906 | 121.8658 | -121.6003 | 0.091553 | 0.036468 | 6.9739 | 0.068891 | 0.066638 | 0.0012092 | -0.0065411 | 0.0021192 | 0.0086061 | 0.0018052 | 0.070361 | 0.060842 | -0.0042767 | 0.023821 | 0.00098061 | -19.4 | -0.13733 | -121.6095 | 0.13733 | -120.7809 | -121.5317 | -121.6644 | -27.3788 | -0.036621 | -121.7331 | 0.068665 | -121.106 | -121.1884 | -121.4584 | -0.009155 | -0.22888 | 0.045776 | 0.8194 | -0.064087 | 0.068665 | -0.054932 | 0.07782 | -0.13275 | -0.12817 | -0.022888 | 0.49438 | 0.14191 | 0.41199 | 0.27466 | 0.54474 | 0.82855 | 121.7468 | 0.62714 | 121.8018 | 121.4722 | 121.6965 | 121.463 | 121.5637 | -121.7011 | -121.8246 | 121.7377 | 121.669 | 102.2003 | 94.2215
1104.6406 | 121.8109 | -121.6187 | 0.11902 | 0.028839 | 6.9746 | 0.067182 | 0.065142 | -0.0017816 | -0.0078229 | 0.0019056 | 0.014709 | 0.003514 | 0.068652 | 0.059347 | -0.0081219 | 0.02318 | 0.00012601 | -19.3634 | -0.11444 | -121.6782 | 0.041199 | -120.8954 | -121.5958 | -121.7285 | -28.2166 | 0.009155 | -121.7514 | 0.004578 | -121.1655 | -121.2296 | -121.4951 | -0.05951 | -0.23346 | -0.07782 | 0.72327 | -0.10986 | 0.022888 | -0.050354 | 0.082398 | -0.13275 | -0.10986 | -0.11444 | 0.45319 | 0.1236 | 0.3891 | 0.25635 | 0.52185 | 0.78278 | 121.7194 | 0.58594 | 121.756 | 121.5637 | 121.7606 | 121.5042 | 121.6278 | -121.7972 | -121.8704 | 121.6599 | 121.6232 | 102.2552 | 93.4021
1106.375 | 121.7972 | -121.6003 | 0.11444 | 0.044098 | 6.9744 | 0.069746 | 0.064715 | -0.001568 | -0.0052595 | -0.0015124 | 0.011658 | 0.0033004 | 0.071216 | 0.058492 | -0.0066265 | 0.022326 | -0.002651 | -19.368 | -0.073242 | -121.6599 | 0.022888 | -120.9 | -121.5775 | -121.7194 | -29.1229 | 0.018311 | -121.756 | 0.004578 | -121.1792 | -121.2204 | -121.5179 | -0.059509 | -0.18768 | -0.091553 | 0.70038 | -0.11902 | 0.022888 | -0.059509 | 0.082397 | -0.15564 | -0.09613 | -0.10986 | 0.42114 | 0.082398 | 0.37994 | 0.23804 | 0.53558 | 0.75989 | 121.6827 | 0.57678 | 121.7606 | 121.5866 | 121.7743 | 121.5271 | 121.6187 | -121.7743 | -121.8704 | 121.6232 | 121.6049 | 102.2324 | 92.4774
1108.1094 | 121.7743 | -121.6461 | 0.1236 | -0.0016785 | 6.9748 | 0.067396 | 0.063433 | -0.0017816 | -0.0048321 | -0.0032214 | -0.00054933 | 0.002446 | 0.069079 | 0.060628 | -0.0068403 | 0.021471 | -0.0020102 | -19.3542 | -0.13733 | -121.6141 | 0.036621 | -120.9 | -121.5912 | -121.7422 | -30.1575 | 0.004578 | -121.7102 | -0.027466 | -121.1563 | -121.2204 | -121.5271 | 0.032043 | -0.26093 | -0.086975 | 0.74616 | -0.096131 | 0.054931 | -0.12817 | 0.022888 | -0.064087 | -0.11902 | -0.15106 | 0.48981 | 0.11902 | 0.42572 | 0.1831 | 0.48981 | 0.71411 | 121.6507 | 0.55389 | 121.6827 | 121.4767 | 121.7148 | 121.5088 | 121.6507 | -121.7377 | -121.8338 | 121.6827 | 121.6187 | 102.2919 | 91.4886
1109.7969 | 121.9254 | -121.5637 | 0.073242 | -0.016937 | 6.9733 | 0.066328 | 0.06322 | -0.001568 | -0.0052595 | -0.0025806 | -0.0036011 | 0.000737 | 0.067584 | 0.064474 | -0.0029949 | 0.024462 | 0.00012601 | -19.3039 | -0.14648 | -121.5591 | 0.14191 | -120.8038 | -121.5363 | -121.6599 | -31.1371 | -0.036621 | -121.6599 | 0.15564 | -121.0464 | -121.0968 | -121.4081 | 0.004578 | -0.21973 | 0.068665 | 0.75989 | -0.09613 | 0.027466 | -0.10071 | 0.022888 | -0.09613 | -0.10986 | 0.082398 | 0.51727 | 0.15564 | 0.46692 | 0.25177 | 0.56305 | 0.75531 | 121.7011 | 0.6134 | 121.8155 | 121.4127 | 121.6232 | 121.4172 | 121.5271 | -121.6324 | -121.7331 | 121.7056 | 121.7194 | 102.2598 | 90.4266
1111.5312 | 121.7789 | -121.6415 | 0.1236 | -0.009308 | 6.9746 | 0.06825 | 0.064074 | 0.00014097 | -0.0033369 | -0.00065803 | 0.0025025 | 0.002446 | 0.06737 | 0.053792 | -0.0072675 | 0.023607 | -0.0017966 | -19.3268 | -0.10986 | -121.6324 | 0.022888 | -120.9686 | -121.669 | -121.788 | -32.4051 | -0.013733 | -121.7239 | -0.004578 | -121.2112 | -121.257 | -121.5454 | 0.009156 | -0.23346 | -0.10071 | 0.67291 | -0.14648 | -0.027465 | -0.15564 | -0.036621 | -0.082397 | -0.13733 | -0.12817 | 0.4303 | 0.096131 | 0.38452 | 0.17853 | 0.46692 | 0.66376 | 121.6553 | 0.5127 | 121.7194 | 121.5225 | 121.7102 | 121.5317 | 121.6278 | -121.756 | -121.8475 | 121.6644 | 121.637 | 102.3148 | 89.2365
1113.2656 | 121.9391 | -121.5866 | 0.086975 | -0.0016785 | 6.9707 | 0.06526 | 0.06322 | -0.0022088 | -0.0065411 | -0.00023063 | -0.00054933 | 0.0011642 | 0.068225 | 0.05422 | -0.0044903 | 0.022967 | -0.00436 | -19.3176 | -0.15106 | -121.5958 | 0.13275 | -120.8084 | -121.4951 | -121.6415 | -33.5129 | -0.050354 | -121.701 | 0.1236 | -121.0464 | -121.051 | -121.4218 | -0.009155 | -0.23804 | 0.045776 | 0.7782 | -0.054932 | 0.091553 | -0.045777 | 0.10071 | -0.11444 | -0.13733 | 0.036621 | 0.54016 | 0.16479 | 0.53558 | 0.27924 | 0.65002 | 0.78735 | 121.7285 | 0.6546 | 121.8246 | 121.4447 | 121.6507 | 121.4355 | 121.5363 | -121.6827 | -121.788 | 121.7194 | 121.7102 | 102.269 | 88.0737
1114.9531 | 121.7926 | -121.6141 | 0.11902 | -0.0016785 | 6.9759 | 0.068037 | 0.064715 | 0.0012092 | -0.0044049 | -0.002367 | -0.0036011 | 0.0033004 | 0.067584 | 0.050374 | -0.0072675 | 0.022539 | -0.002651 | -19.3176 | -0.13275 | -121.6187 | 0.036621 | -120.9091 | -121.6553 | -121.7651 | -35.0967 | -0.009155 | -121.7239 | 0 | -121.1884 | -121.2021 | -121.5225 | -0.004577 | -0.25177 | -0.082398 | 0.70496 | -0.15106 | -0.041198 | -0.14648 | -0.036621 | -0.10986 | -0.12817 | -0.11902 | 0.42572 | 0.091553 | 0.41199 | 0.20142 | 0.52185 | 0.70953 | 121.6553 | 0.53558 | 121.7239 | 121.4859 | 121.7148 | 121.4813 | 121.6049 | -121.7377 | -121.843 | 121.6507 | 121.6141 | 102.2964 | 86.5173
1116.6875 | 121.9437 | -121.6003 | 0.091553 | -0.009308 | 6.9724 | 0.06761 | 0.060229 | 0.0024908 | -0.0069683 | -0.0021532 | -0.0036011 | 0.0013778 | 0.069934 | 0.05956 | -0.0061993 | 0.023394 | -0.0037192 | -19.3039 | -0.15106 | -121.6003 | 0.14191 | -120.7809 | -121.4813 | -121.6324 | -36.5067 | -0.068665 | -121.6965 | 0.13733 | -121.0007 | -121.019 | -121.4035 | 0 | -0.24261 | 0.050354 | 0.8194 | -0.032043 | 0.11902 | -0.032043 | 0.11902 | -0.09613 | -0.16022 | 0.045776 | 0.59967 | 0.19684 | 0.58136 | 0.29297 | 0.67749 | 0.8194 | 121.7422 | 0.6958 | 121.8338 | 121.4493 | 121.6278 | 121.4493 | 121.5317 | -121.6919 | -121.788 | 121.7422 | 121.7377 | 102.2964 | 85.0937
1118.4375 | 121.9162 | -121.6095 | 0.086975 | -0.009308 | 6.9722 | 0.065687 | 0.060656 | -7.2628e-05 | -0.0073957 | -0.0015124 | -0.00054933 | 0.0009506 | 0.066516 | 0.058919 | -0.0055585 | 0.02318 | 0.00076681 | -19.3359 | -0.14191 | -121.6049 | 0.10071 | -120.8221 | -121.5408 | -121.669 | -38.4888 | -0.032043 | -121.7148 | 0.11902 | -121.0327 | -121.0373 | -121.431 | 0.004578 | -0.22888 | 0.013733 | 0.78735 | -0.059509 | 0.068664 | -0.064087 | 0.064086 | -0.10529 | -0.11902 | 0.032044 | 0.57678 | 0.17853 | 0.57221 | 0.28381 | 0.67749 | 0.78278 | 121.7056 | 0.68207 | 121.8338 | 121.463 | 121.6827 | 121.4676 | 121.5775 | -121.6919 | -121.8018 | 121.7102 | 121.7285 | 102.2736 | 83.1207
1120.1719 | 121.8613 | -121.5866 | 0.086975 | 0.02121 | 6.9752 | 0.066114 | 0.064501 | 0.00014097 | -0.0067547 | -0.001726 | 0.0055543 | 0.0033004 | 0.067798 | 0.064046 | -0.0034223 | 0.023394 | 0.00055321 | -19.3268 | -0.14191 | -121.6232 | 0.10071 | -120.8496 | -121.5546 | -121.6873 | -40.8142 | -0.036621 | -121.6965 | 0.068665 | -121.0693 | -121.0693 | -121.4584 | -0.036621 | -0.22888 | 0.013733 | 0.737 | -0.10071 | 0.032044 | -0.064087 | 0.068665 | -0.10986 | -0.1236 | -0.01831 | 0.51727 | 0.12817 | 0.51727 | 0.23804 | 0.62714 | 0.77362 | 121.7239 | 0.62714 | 121.7651 | 121.4813 | 121.6599 | 121.4447 | 121.55 | -121.7102 | -121.7834 | 121.6873 | 121.6553 | 102.2598 | 80.7724
1121.8438 | 121.8704 | -121.6141 | 0.086975 | 0.005951 | 6.9733 | 0.068464 | 0.063647 | 0.003559 | -0.0052595 | -0.00087163 | 0.0086061 | 0.002446 | 0.065875 | 0.057424 | -0.0066265 | 0.022967 | -0.003292 | -19.3359 | -0.13275 | -121.6187 | 0.11902 | -120.8313 | -121.5591 | -121.6827 | -43.1259 | -0.036621 | -121.7239 | 0.082397 | -121.0831 | -121.0648 | -121.4539 | -0.004577 | -0.21973 | 0.032044 | 0.78278 | -0.068664 | 0.054932 | -0.064087 | 0.059509 | -0.10986 | -0.1236 | -0.004578 | 0.53101 | 0.16022 | 0.54932 | 0.27008 | 0.65918 | 0.78735 | 121.7377 | 0.64087 | 121.8063 | 121.4859 | 121.6873 | 121.4813 | 121.5775 | -121.7056 | -121.8109 | 121.7331 | 121.6965 | 102.2781 | 78.4882
1123.5781 | 121.8704 | -121.5958 | 0.10529 | 0.028839 | 6.9767 | 0.069105 | 0.06386 | -0.00092703 | -0.0054731 | -0.001726 | 0.0025025 | 0.0015914 | 0.06972 | 0.065969 | -0.0047039 | 0.024889 | -0.00436 | -19.3634 | -0.14191 | -121.6187 | 0.10071 | -120.8313 | -121.5637 | -121.6827 | -45.7581 | -0.041199 | -121.7056 | 0.059509 | -121.0602 | -121.0464 | -121.4676 | -0.022888 | -0.24719 | -0.004578 | 0.76447 | -0.086975 | 0.032043 | -0.064087 | 0.054931 | -0.10986 | -0.14649 | -0.045777 | 0.53558 | 0.12817 | 0.54932 | 0.23804 | 0.65918 | 0.78735 | 121.7194 | 0.64545 | 121.7651 | 121.4767 | 121.6644 | 121.4539 | 121.5546 | -121.7239 | -121.8109 | 121.6965 | 121.6553 | 102.2324 | 75.8377
1125.3125 | 121.8979 | -121.6141 | 0.086975 | 0.02121 | 6.9746 | 0.067396 | 0.064715 | -0.0024224 | -0.0052595 | 0.00041017 | -0.00054933 | 9.6204e-05 | 0.066943 | 0.057638 | -0.0079083 | 0.022539 | -0.0013694 | -19.3222 | -0.14648 | -121.6049 | 0.086975 | -120.845 | -121.5637 | -121.6873 | -48.4451 | -0.036621 | -121.7102 | 0.07782 | -121.0236 | -121.0052 | -121.4493 | 0.009156 | -0.23346 | 0 | 0.76904 | -0.073242 | 0.050354 | -0.082398 | 0.041198 | -0.09613 | -0.1236 | -0.009155 | 0.59051 | 0.16479 | 0.60883 | 0.26093 | 0.70496 | 0.75989 | 121.6919 | 0.68664 | 121.788 | 121.4584 | 121.6736 | 121.4676 | 121.5775 | -121.6919 | -121.7972 | 121.701 | 121.6919 | 102.2919 | 73.1689
1126.9844 | 121.8658 | -121.6049 | 0.073242 | 0.036468 | 6.9746 | 0.0706 | 0.06386 | 0.00014097 | -0.0041913 | -0.001726 | 0.011658 | 0.0022324 | 0.072284 | 0.056783 | -0.0064129 | 0.024248 | 0.00033961 | -19.2902 | -0.13275 | -121.6141 | 0.16022 | -120.7809 | -121.55 | -121.6644 | -51.7502 | -0.022888 | -121.7285 | 0.09613 | -121.0144 | -120.9869 | -121.4584 | -0.009156 | -0.20599 | 0.086975 | 0.82397 | -0.05951 | 0.054931 | -0.050354 | 0.064087 | -0.1236 | -0.09613 | 0.022888 | 0.59051 | 0.14648 | 0.61798 | 0.27008 | 0.74158 | 0.83313 | 121.7743 | 0.71411 | 121.8246 | 121.4813 | 121.7056 | 121.4722 | 121.582 | -121.6873 | -121.8018 | 121.7651 | 121.701 | 102.3148 | 69.8547
1128.7344 | 121.9116 | -121.6141 | 0.07782 | -0.0016785 | 6.9744 | 0.065901 | 0.06322 | -0.0013544 | -0.0056867 | -0.00023063 | 0.0025025 | 0.0015914 | 0.065875 | 0.058065 | -0.0049175 | 0.026385 | -0.0041464 | -19.3039 | -0.12817 | -121.6232 | 0.091553 | -120.8588 | -121.5912 | -121.7056 | -54.2313 | -0.036621 | -121.6919 | 0.1236 | -120.9778 | -120.9549 | -121.4218 | -0.009155 | -0.20599 | 0.013733 | 0.75531 | -0.091552 | 0.022888 | -0.082397 | 0.032043 | -0.07782 | -0.11444 | 0.045776 | 0.63629 | 0.19226 | 0.65918 | 0.27008 | 0.737 | 0.76447 | 121.7148 | 0.71411 | 121.8155 | 121.4951 | 121.6553 | 121.4859 | 121.5775 | -121.7011 | -121.7697 | 121.7056 | 121.7377 | 102.3102 | 67.3828
1130.4688 | 121.9345 | -121.582 | 0.082397 | -0.009308 | 6.9735 | 0.066328 | 0.064715 | -0.0019952 | -0.0056867 | -0.0010852 | -0.0036011 | 0.000737 | 0.068866 | 0.062551 | -0.0087629 | 0.02553 | -0.0024374 | -19.2627 | -0.16479 | -121.6003 | 0.19226 | -120.7397 | -121.4767 | -121.6232 | -57.106 | -0.054932 | -121.701 | 0.12817 | -120.9091 | -120.8817 | -121.4172 | -0.018311 | -0.24719 | 0.10986 | 0.84229 | -0.041199 | 0.10528 | -0.022888 | 0.1236 | -0.11902 | -0.13733 | 0.045777 | 0.67291 | 0.16479 | 0.70038 | 0.28381 | 0.8194 | 0.8606 | 121.7926 | 0.79193 | 121.8292 | 121.4355 | 121.6461 | 121.4172 | 121.5271 | -121.6827 | -121.7834 | 121.7743 | 121.7102 | 102.3193 | 64.476
1132.2188 | 121.8842 | -121.582 | 0.07782 | 0.005951 | 6.9724 | 0.066114 | 0.061511 | 0.0012092 | -0.0052595 | -0.0010852 | 0.0055543 | 0.0026596 | 0.067584 | 0.061483 | -0.0074811 | 0.021898 | -0.0054282 | -19.313 | -0.16479 | -121.6415 | 0.10071 | -120.8542 | -121.5729 | -121.6965 | -60.2234 | -0.045776 | -121.7377 | 0.059509 | -120.9961 | -120.9503 | -121.4401 | -0.05951 | -0.24261 | 0.022888 | 0.72784 | -0.11444 | 0.009155 | -0.054931 | 0.068665 | -0.15564 | -0.1236 | -0.018311 | 0.58594 | 0.14191 | 0.63171 | 0.29755 | 0.78735 | 0.78735 | 121.7422 | 0.74158 | 121.7972 | 121.4767 | 121.6919 | 121.4172 | 121.5363 | -121.7194 | -121.8155 | 121.6827 | 121.6415 | 102.269 | 61.3586
1133.9062 | 121.7972 | -121.6187 | 0.11444 | -0.009308 | 6.9754 | 0.069532 | 0.066638 | -0.00049983 | -0.0054731 | -0.002367 | -0.00054933 | 0.0030868 | 0.068011 | 0.058492 | -0.0079083 | 0.022112 | 0.0022622 | -19.3863 | -0.11902 | -121.6461 | 0.009155 | -120.9686 | -121.669 | -121.788 | -63.1119 | -0.032043 | -121.7239 | 0.004578 | -121.0602 | -121.0236 | -121.4951 | -0.027466 | -0.23346 | -0.10529 | 0.65002 | -0.16937 | -0.050354 | -0.14191 | -0.022888 | -0.10529 | -0.14648 | -0.10986 | 0.55847 | 0.1236 | 0.59509 | 0.22888 | 0.70038 | 0.67749 | 121.6553 | 0.66376 | 121.7285 | 121.5271 | 121.6919 | 121.4996 | 121.5866 | -121.7606 | -121.8384 | 121.6278 | 121.6232 | 102.2324 | 58.5068
1135.6406 | 121.9208 | -121.5866 | 0.07782 | -0.009308 | 6.9729 | 0.066541 | 0.06322 | -0.0054132 | -0.0076093 | -0.0012988 | -0.0036011 | 0.0009506 | 0.065875 | 0.06191 | -0.0076947 | 0.021471 | -0.0024374 | -19.2856 | -0.15106 | -121.5958 | 0.15564 | -120.7489 | -121.4813 | -121.6232 | -65.7669 | -0.059509 | -121.7056 | 0.1236 | -120.8725 | -120.7993 | -121.4127 | -0.009155 | -0.22888 | 0.07782 | 0.83771 | -0.036621 | 0.10529 | -0.027466 | 0.11444 | -0.11902 | -0.13733 | 0.045776 | 0.71411 | 0.17395 | 0.78735 | 0.29297 | 0.90637 | 0.84686 | 121.7514 | 0.83313 | 121.8292 | 121.4447 | 121.6461 | 121.4355 | 121.5271 | -121.6736 | -121.7834 | 121.7422 | 121.7102 | 102.301 | 55.8197
1137.3125 | 121.8887 | -121.6187 | 0.09613 | 0.028839 | 6.9756 | 0.069746 | 0.06386 | 0.0012092 | -0.0063275 | -0.002367 | 0.0055543 | 0.0020188 | 0.070575 | 0.062124 | -0.0061993 | 0.022967 | -0.0030784 | -19.3954 | -0.12817 | -121.637 | 0.10986 | -120.8542 | -121.5775 | -121.6919 | -68.4677 | -0.041199 | -121.7239 | 0.054932 | -120.9503 | -120.845 | -121.4401 | -0.018311 | -0.2243 | 0.013733 | 0.76447 | -0.073243 | 0.041198 | -0.054932 | 0.059509 | -0.10529 | -0.13733 | -0.041198 | 0.66833 | 0.17853 | 0.77362 | 0.28381 | 0.87891 | 0.78278 | 121.7468 | 0.77362 | 121.7789 | 121.5088 | 121.6827 | 121.4905 | 121.5775 | -121.7331 | -121.8201 | 121.7285 | 121.6736 | 102.2232 | 53.1509
1138.9844 | 121.8979 | -121.6141 | 0.09613 | 0.01358 | 6.9746 | 0.066755 | 0.063647 | 0.00035457 | -0.0069683 | -0.0015124 | -0.0066527 | 0.0030868 | 0.068438 | 0.054433 | -0.0076947 | 0.02318 | -0.0028646 | -19.2764 | -0.14648 | -121.6095 | 0.16479 | -120.7764 | -121.5134 | -121.6507 | -70.9351 | -0.054932 | -121.6827 | 0.09613 | -120.8588 | -120.7581 | -121.4218 | 0.004578 | -0.24261 | 0.068665 | 0.83771 | -0.036621 | 0.10071 | -0.041199 | 0.09613 | -0.068664 | -0.15106 | 0 | 0.75531 | 0.19226 | 0.85602 | 0.26093 | 0.92468 | 0.83313 | 121.7743 | 0.82397 | 121.7789 | 121.463 | 121.6278 | 121.4676 | 121.5591 | -121.7056 | -121.7789 | 121.7789 | 121.7102 | 102.3376 | 50.679
1140.7188 | 121.8292 | -121.6553 | 0.10529 | -0.009308 | 6.975 | 0.068464 | 0.06621 | 0.0014228 | -0.0056867 | -0.0012988 | -0.0066527 | 0.0011642 | 0.06972 | 0.061056 | -0.0059857 | 0.02318 | -0.0073508 | -19.3314 | -0.10529 | -121.637 | 0.013733 | -120.932 | -121.6644 | -121.7834 | -74.2401 | -0.022888 | -121.7239 | 0.013733 | -120.9686 | -120.8542 | -121.4859 | 0.01831 | -0.21057 | -0.091553 | 0.72327 | -0.12817 | -0.009156 | -0.14648 | -0.027466 | -0.068665 | -0.12817 | -0.091553 | 0.68664 | 0.16937 | 0.80109 | 0.23804 | 0.86975 | 0.70496 | 121.6507 | 0.75531 | 121.7377 | 121.5317 | 121.7011 | 121.55 | 121.6324 | -121.7422 | -121.8292 | 121.669 | 121.669 | 102.3239 | 47.4152
1142.4531 | 121.8155 | -121.6644 | 0.10071 | 0.005951 | 6.9746 | 0.068891 | 0.064074 | 0.00014097 | -0.0067547 | 0.00062377 | -0.0036011 | 0.0043686 | 0.069293 | 0.051656 | -0.0064129 | 0.021471 | -0.0039328 | -19.3451 | -0.09613 | -121.637 | 0.013733 | -120.9686 | -121.6827 | -121.7834 | -76.6617 | -0.032043 | -121.756 | 0.013733 | -120.9686 | -120.8221 | -121.4951 | 0.027466 | -0.19684 | -0.086975 | 0.6958 | -0.11902 | -0.01831 | -0.14648 | -0.045776 | -0.091552 | -0.13275 | -0.086975 | 0.6958 | 0.16937 | 0.84229 | 0.26093 | 0.93384 | 0.66833 | 121.6507 | 0.78735 | 121.7697 | 121.5408 | 121.7239 | 121.5683 | 121.6324 | -121.7377 | -121.8567 | 121.6782 | 121.6782 | 102.3193 | 45.0027
1144.1875 | 121.8567 | -121.6187 | 0.073242 | 0.02121 | 6.9778 | 0.069532 | 0.064501 | -0.0017816 | -0.0052595 | -0.0012988 | 0.0055543 | 0.004155 | 0.06972 | 0.057851 | -0.0072675 | 0.022539 | -0.0039328 | -19.2581 | -0.11444 | -121.637 | 0.09613 | -120.8542 | -121.582 | -121.701 | -78.6118 | -0.018311 | -121.7239 | 0.054932 | -120.845 | -120.694 | -121.4355 | -0.018311 | -0.18768 | 0.022888 | 0.76447 | -0.082398 | 0.036621 | -0.064087 | 0.054932 | -0.10529 | -0.091553 | -0.01831 | 0.77362 | 0.1831 | 0.92468 | 0.28839 | 1.03 | 0.78278 | 121.7331 | 0.87891 | 121.7789 | 121.5225 | 121.7056 | 121.5042 | 121.6003 | -121.7102 | -121.7972 | 121.7148 | 121.6736 | 102.3605 | 43.0069
1145.8594 | 121.8613 | -121.6141 | 0.091553 | -0.0016785 | 6.9744 | 0.069105 | 0.066424 | -0.0039178 | -0.0044049 | -0.0045032 | -0.0066527 | 0.0022324 | 0.069079 | 0.059987 | -0.0040631 | 0.023821 | -0.001583 | -19.3359 | -0.10071 | -121.637 | 0.036621 | -120.9137 | -121.6461 | -121.7789 | -80.072 | -0.041199 | -121.7285 | 0.059509 | -120.8359 | -120.6528 | -121.4355 | -0.022888 | -0.19226 | -0.054932 | 0.70038 | -0.16479 | -0.032043 | -0.14191 | -0.009155 | -0.11444 | -0.13275 | -0.032044 | 0.7782 | 0.17853 | 0.9613 | 0.29297 | 1.0757 | 0.72327 | 121.6736 | 0.89264 | 121.788 | 121.5363 | 121.6873 | 121.5134 | 121.5729 | -121.7285 | -121.8201 | 121.6507 | 121.6736 | 102.2781 | 41.5421
1147.5938 | 121.9254 | -121.5958 | 0.086975 | -0.0016785 | 6.9735 | 0.066541 | 0.062365 | -0.00028623 | -0.0059003 | -0.0040758 | -0.0036011 | 0.0013778 | 0.067157 | 0.064687 | -0.0070539 | 0.022326 | 0.00055321 | -19.2627 | -0.15106 | -121.6049 | 0.16937 | -120.7626 | -121.4813 | -121.6461 | -80.8502 | -0.073242 | -121.6873 | 0.11444 | -120.7169 | -120.5063 | -121.3852 | -0.009155 | -0.23804 | 0.082398 | 0.83313 | -0.050354 | 0.11444 | -0.041199 | 0.1236 | -0.091553 | -0.16022 | 0.027466 | 0.87891 | 0.21057 | 1.0895 | 0.30212 | 1.181 | 0.84228 | 121.7743 | 0.97046 | 121.8018 | 121.4539 | 121.6141 | 121.4447 | 121.5225 | -121.6919 | -121.7743 | 121.7651 | 121.7102 | 102.3331 | 40.7455
1149.3281 | 121.9437 | -121.5958 | 0.086975 | -0.0016785 | 6.9739 | 0.06761 | 0.06322 | -0.0056268 | -0.0080365 | -0.0036486 | -0.0036011 | 9.6204e-05 | 0.069507 | 0.061696 | -0.0064129 | 0.024462 | -0.0024374 | -19.2673 | -0.15106 | -121.5866 | 0.16479 | -120.7626 | -121.4905 | -121.6324 | -79.6509 | -0.059509 | -121.6827 | 0.13275 | -120.6528 | -120.433 | -121.376 | 0.009155 | -0.23804 | 0.07782 | 0.83313 | -0.036621 | 0.10529 | -0.045776 | 0.09613 | -0.086975 | -0.14648 | 0.045776 | 0.94299 | 0.21973 | 1.1627 | 0.3067 | 1.2497 | 0.82397 | 121.7514 | 1.03 | 121.8155 | 121.4355 | 121.6232 | 121.4447 | 121.5363 | -121.6736 | -121.7697 | 121.7606 | 121.7285 | 102.3285 | 41.9449
1151.0625 | 121.8613 | -121.6187 | 0.10071 | 0.01358 | 6.9763 | 0.066969 | 0.065142 | 0.00185 | -0.0050457 | -0.002367 | 0.0086061 | 0.0039414 | 0.069507 | 0.055715 | -0.0068403 | 0.022539 | -0.0028646 | -19.2215 | -0.10986 | -121.6644 | 0.10071 | -120.8542 | -121.5729 | -121.7148 | -76.7715 | -0.004578 | -121.7056 | 0.059509 | -120.694 | -120.3873 | -121.4081 | -0.045777 | -0.21057 | 0 | 0.76447 | -0.096131 | 0.045776 | -0.050354 | 0.091553 | -0.086975 | -0.10529 | -0.041199 | 0.92468 | 0.21057 | 1.2314 | 0.29755 | 1.3184 | 0.81024 | 121.7651 | 1.0117 | 121.7651 | 121.5546 | 121.701 | 121.5088 | 121.6141 | -121.7651 | -121.8063 | 121.7194 | 121.6782 | 102.3972 | 44.8471
1152.8125 | 121.843 | -121.637 | 0.11444 | 0.036468 | 6.9744 | 0.070173 | 0.065783 | 0.0050544 | -0.0080365 | 0.00041017 | 0.011658 | 0.0037278 | 0.070361 | 0.061696 | -0.0059857 | 0.022539 | 0.0011942 | -19.2764 | -0.082397 | -121.6644 | 0.086975 | -120.8725 | -121.582 | -121.7148 | -77.6001 | -0.004578 | -121.7468 | 0.050354 | -120.6482 | -120.314 | -121.4127 | -0.027466 | -0.19684 | -0.027466 | 0.76447 | -0.07782 | 0.054932 | -0.050354 | 0.082398 | -0.10986 | -0.11902 | -0.064087 | 0.98877 | 0.2243 | 1.3229 | 0.33417 | 1.4328 | 0.79193 | 121.7514 | 1.0986 | 121.7972 | 121.582 | 121.7422 | 121.5546 | 121.6324 | -121.7789 | -121.8613 | 121.7239 | 121.6873 | 102.3605 | 44.0369
1154.5 | 121.8796 | -121.6187 | 0.091553 | 0.036468 | 6.9742 | 0.066541 | 0.062792 | 0.003559 | -0.0059003 | -0.0030078 | 0.0055543 | 0.0026596 | 0.068866 | 0.067037 | -0.0081219 | 0.024889 | 0.0022622 | -19.2764 | -0.11902 | -121.6049 | 0.11902 | -120.8038 | -121.5683 | -121.669 | -78.5522 | -0.054932 | -121.7239 | 0.073242 | -120.5841 | -120.1859 | -121.376 | 0.013733 | -0.21057 | 0.027466 | 0.81482 | -0.050354 | 0.050354 | -0.064087 | 0.036621 | -0.10529 | -0.14649 | -0.018311 | 1.0345 | 0.24261 | 1.4328 | 0.3479 | 1.5381 | 0.80109 | 121.7239 | 1.1398 | 121.7972 | 121.4859 | 121.669 | 121.4996 | 121.5637 | -121.6965 | -121.8155 | 121.7377 | 121.6919 | 102.3422 | 43.0664
1156.2344 | 121.8018 | -121.6324 | 0.10986 | -0.009308 | 6.9759 | 0.06761 | 0.064074 | 0.00078177 | -0.0063275 | -0.0019396 | -0.00054933 | 0.0022324 | 0.068438 | 0.061269 | -0.0047039 | 0.02318 | -0.0037192 | -19.2627 | -0.11444 | -121.6278 | 0.022888 | -120.932 | -121.669 | -121.7972 | -79.6875 | -0.013733 | -121.7468 | -0.009155 | -120.6253 | -120.2087 | -121.4401 | 0.004577 | -0.2243 | -0.086975 | 0.70038 | -0.16479 | -0.036621 | -0.16937 | -0.041198 | -0.11444 | -0.1236 | -0.11902 | 1.0071 | 0.19226 | 1.4236 | 0.3067 | 1.5381 | 0.6958 | 121.6507 | 1.1215 | 121.7377 | 121.5134 | 121.7331 | 121.5179 | 121.6187 | -121.7377 | -121.8567 | 121.6553 | 121.6232 | 102.3697 | 41.9449
1157.9688 | 121.8887 | -121.6095 | 0.09613 | 0.036468 | 6.9739 | 0.067396 | 0.062792 | 0.0024908 | -0.0039777 | -0.00065803 | 0.0086061 | 0.0020188 | 0.068866 | 0.054861 | -0.0042767 | 0.022753 | -0.00051479 | -19.2764 | -0.11902 | -121.6049 | 0.14191 | -120.7855 | -121.5591 | -121.6873 | -79.2664 | -0.041199 | -121.7148 | 0.07782 | -120.4102 | -119.9661 | -121.3669 | 0.004578 | -0.21515 | 0.045777 | 0.82398 | -0.07782 | 0.050354 | -0.082398 | 0.045776 | -0.10529 | -0.13733 | -0.01831 | 1.1993 | 0.24262 | 1.6434 | 0.3479 | 1.7487 | 0.8194 | 121.7468 | 1.3046 | 121.7926 | 121.4859 | 121.6736 | 121.4905 | 121.5683 | -121.701 | -121.8109 | 121.7514 | 121.6873 | 102.3331 | 42.3431
1159.7344 | 121.8796 | -121.6187 | 0.09613 | 0.01358 | 6.9733 | 0.066969 | 0.064074 | 0.0014228 | -0.0050457 | -0.0015124 | 0.0086061 | 0.002446 | 0.067584 | 0.065755 | -0.0055585 | 0.025316 | -0.00051479 | -19.3176 | -0.13275 | -121.6141 | 0.09613 | -120.845 | -121.5729 | -121.7102 | -79.6188 | -0.054932 | -121.7102 | 0.07782 | -120.3415 | -119.8563 | -121.3715 | 0.004577 | -0.22888 | 0 | 0.77362 | -0.091553 | 0.045776 | -0.09613 | 0.041199 | -0.091553 | -0.15106 | -0.01831 | 1.2772 | 0.24719 | 1.7624 | 0.33875 | 1.8539 | 0.76904 | 121.7102 | 1.3687 | 121.788 | 121.4813 | 121.6553 | 121.4859 | 121.5637 | -121.7102 | -121.8063 | 121.7148 | 121.6965 | 102.301 | 41.9998
1161.4219 | 121.9162 | -121.5912 | 0.068665 | 0.051727 | 6.9767 | 0.0706 | 0.064074 | 0.00035457 | -0.0026959 | -0.00087163 | 0.014709 | 0.0030868 | 0.067584 | 0.062337 | -0.0053449 | 0.023394 | -0.001583 | -19.2078 | -0.13275 | -121.6141 | 0.17853 | -120.7809 | -121.4996 | -121.6507 | -79.3945 | -0.050354 | -121.7102 | 0.13275 | -120.2087 | -119.696 | -121.3211 | -0.022888 | -0.20142 | 0.10986 | 0.81024 | -0.059509 | 0.091553 | -0.036621 | 0.11444 | -0.11902 | -0.11902 | 0.064086 | 1.3824 | 0.27008 | 1.8951 | 0.3891 | 2.0142 | 0.83313 | 121.7926 | 1.5015 | 121.843 | 121.4813 | 121.6599 | 121.4584 | 121.5408 | -121.6827 | -121.7789 | 121.7697 | 121.7239 | 102.3834 | 42.1967
1163.1562 | 121.9345 | -121.6141 | 0.082397 | -0.0016785 | 6.9718 | 0.065687 | 0.062365 | -0.0028498 | -0.0059003 | -0.002367 | -0.0036011 | 0.0015914 | 0.069934 | 0.065969 | -0.0066265 | 0.025957 | 0.0011942 | -19.2078 | -0.16022 | -121.6003 | 0.15106 | -120.7764 | -121.5088 | -121.6141 | -71.5988 | -0.064087 | -121.701 | 0.1236 | -119.9982 | -119.3802 | -121.2891 | 0.013733 | -0.24261 | 0.068665 | 0.83771 | 0 | 0.10529 | -0.013733 | 0.091553 | -0.086975 | -0.14648 | 0.041199 | 1.6159 | 0.32501 | 2.2339 | 0.41199 | 2.3209 | 0.82398 | 121.7514 | 1.7029 | 121.8246 | 121.4401 | 121.637 | 121.4539 | 121.55 | -121.6827 | -121.7834 | 121.7651 | 121.7377 | 102.4063 | 50.0153
1164.9062 | 121.9162 | -121.6049 | 0.091553 | -0.016937 | 6.9756 | 0.066755 | 0.063433 | 0.0037726 | -0.0035505 | 0.00019657 | 0.014709 | 0.0045822 | 0.070788 | 0.072591 | -0.0036359 | 0.024462 | -0.0024374 | -19.1986 | -0.13733 | -121.6278 | 0.1831 | -120.7581 | -121.5134 | -121.6507 | -67.7628 | -0.032043 | -121.7285 | 0.1236 | -119.8654 | -119.2429 | -121.2891 | -0.022889 | -0.22888 | 0.091552 | 0.84686 | -0.045777 | 0.091552 | -0.022888 | 0.11444 | -0.1236 | -0.1236 | 0.032043 | 1.7395 | 0.31586 | 2.3621 | 0.43945 | 2.4857 | 0.86975 | 121.8109 | 1.8631 | 121.8521 | 121.4905 | 121.6965 | 121.4676 | 121.5729 | -121.7194 | -121.8201 | 121.788 | 121.7285 | 102.4063 | 53.8422
1166.5781 | 121.8475 | -121.6232 | 0.09613 | -0.009308 | 6.9746 | 0.067182 | 0.066424 | -0.00028623 | -0.0063275 | -0.0021532 | -0.0036011 | 0.0039414 | 0.070361 | 0.065328 | -0.0055585 | 0.026385 | -0.0020102 | -19.3085 | -0.09613 | -121.6599 | 0.032043 | -120.9412 | -121.6644 | -121.7697 | -66.9388 | -0.018311 | -121.7468 | 0.036621 | -119.8608 | -119.1605 | -121.3486 | -0.036621 | -0.19226 | -0.064087 | 0.68207 | -0.14648 | -0.041199 | -0.10986 | -0.004578 | -0.1236 | -0.11444 | -0.059509 | 1.7624 | 0.27466 | 2.4628 | 0.39825 | 2.5864 | 0.71869 | 121.6919 | 1.886 | 121.7834 | 121.5637 | 121.7285 | 121.5271 | 121.6049 | -121.756 | -121.843 | 121.6553 | 121.6599 | 102.3148 | 54.6844
1168.2969 | 121.9391 | -121.5958 | 0.073242 | -0.0016785 | 6.9748 | 0.06761 | 0.061297 | -0.001568 | -0.0065411 | -1.7026e-05 | -0.0066527 | 0.0003098 | 0.067584 | 0.065328 | -0.0079083 | 0.02553 | 0.00033961 | -19.2123 | -0.15564 | -121.6278 | 0.15564 | -120.7581 | -121.5088 | -121.6415 | -66.4948 | -0.059509 | -121.7056 | 0.11444 | -119.5587 | -118.7943 | -121.2479 | -0.032044 | -0.22888 | 0.082398 | 0.83771 | -0.045777 | 0.086975 | -0.013733 | 0.11902 | -0.10986 | -0.13275 | 0.041199 | 2.037 | 0.3479 | 2.8015 | 0.45776 | 2.9114 | 0.86975 | 121.7834 | 2.1469 | 121.8201 | 121.4722 | 121.6461 | 121.4401 | 121.5363 | -121.701 | -121.7789 | 121.7514 | 121.7102 | 102.3834 | 55.101
1170.0469 | 121.8018 | -121.6507 | 0.13275 | -0.009308 | 6.9739 | 0.066114 | 0.061938 | -0.0056268 | -0.0056867 | -0.0019396 | -0.0036011 | 0.0022324 | 0.069293 | 0.056783 | -0.0070539 | 0.024035 | 0.00076681 | -19.2673 | -0.13275 | -121.6278 | 0.027466 | -120.9137 | -121.6095 | -121.7514 | -66.7328 | -0.027466 | -121.7468 | -0.022888 | -119.545 | -118.7393 | -121.3257 | 0.022888 | -0.2655 | -0.10529 | 0.737 | -0.10071 | 0.041199 | -0.1236 | 0.018311 | -0.09613 | -0.16022 | -0.15564 | 2.1057 | 0.32501 | 2.9114 | 0.42114 | 3.0075 | 0.71411 | 121.6553 | 2.2018 | 121.7239 | 121.4951 | 121.7194 | 121.5179 | 121.6232 | -121.7606 | -121.8796 | 121.6782 | 121.6278 | 102.3834 | 54.9179
1171.7969 | 121.8567 | -121.6232 | 0.09613 | 0.02121 | 6.9765 | 0.069532 | 0.065569 | 0.0054816 | -0.0050457 | 0.00019657 | 0.0025025 | 0.0039414 | 0.070788 | 0.054861 | -0.0072675 | 0.023821 | 0.0020486 | -19.2032 | -0.10071 | -121.6461 | 0.10986 | -120.8496 | -121.582 | -121.7102 | -66.925 | -0.013733 | -121.7331 | 0.073242 | -119.3161 | -118.4372 | -121.257 | -0.022888 | -0.19684 | 0.013733 | 0.77362 | -0.086975 | 0.041199 | -0.064087 | 0.064087 | -0.10986 | -0.10986 | -0.022888 | 2.3071 | 0.36621 | 3.186 | 0.47607 | 3.2959 | 0.79651 | 121.756 | 2.417 | 121.8063 | 121.5454 | 121.7194 | 121.5225 | 121.6095 | -121.7422 | -121.8292 | 121.7331 | 121.6965 | 102.42 | 54.6982
1173.4688 | 121.8292 | -121.6415 | 0.11902 | 0.044098 | 6.9769 | 0.069105 | 0.065569 | -0.004345 | -0.0069683 | -0.00065803 | 0.0086061 | 0.004155 | 0.070361 | 0.060201 | -0.0081219 | 0.024035 | -0.00030119 | -19.2535 | -0.07782 | -121.669 | 0.041199 | -120.9091 | -121.6095 | -121.7422 | -67.2729 | 0.018311 | -121.7468 | 0.004578 | -119.1788 | -118.2358 | -121.2708 | -0.027465 | -0.19684 | -0.07782 | 0.73242 | -0.10071 | 0.032044 | -0.073243 | 0.059509 | -0.10528 | -0.10071 | -0.11444 | 2.4628 | 0.37079 | 3.4058 | 0.47607 | 3.511 | 0.75989 | 121.7102 | 2.5681 | 121.7514 | 121.5912 | 121.7651 | 121.5637 | 121.6599 | -121.788 | -121.8658 | 121.6827 | 121.6461 | 102.388 | 54.3686
1175.2031 | 121.843 | -121.6415 | 0.10529 | 0.036468 | 6.9744 | 0.06825 | 0.068347 | -0.0034906 | -0.0046185 | 0.001692 | 0.011658 | 0.0037278 | 0.072284 | 0.050588 | -0.0068403 | 0.025103 | -0.0028646 | -19.2032 | -0.086975 | -121.6553 | 0.050354 | -120.8817 | -121.582 | -121.7102 | -66.7969 | 0.022888 | -121.7468 | 0.027466 | -118.8217 | -117.9199 | -121.2204 | -0.013732 | -0.19226 | -0.054932 | 0.75989 | -0.068664 | 0.05951 | -0.054932 | 0.073242 | -0.10528 | -0.082398 | -0.07782 | 2.8198 | 0.42114 | 3.7216 | 0.52643 | 3.8269 | 0.77362 | 121.7056 | 2.9251 | 121.7743 | 121.5683 | 121.7697 | 121.5546 | 121.6644 | -121.7606 | -121.8521 | 121.6919 | 121.669 | 102.4384 | 54.8447
1176.9375 | 121.8063 | -121.6553 | 0.13733 | -0.0016785 | 6.9737 | 0.067396 | 0.061511 | 0.00078177 | -0.0067547 | 0.0019056 | 0.0025025 | 0.0033004 | 0.071216 | 0.048238 | -0.0083355 | 0.025744 | -0.0020102 | -19.1895 | -0.13733 | -121.6415 | 0.059509 | -120.8725 | -121.5958 | -121.7194 | -67.0029 | -0.032043 | -121.7377 | 0 | -118.602 | -117.6498 | -121.2112 | 0.013732 | -0.27466 | -0.07782 | 0.78278 | -0.064087 | 0.059509 | -0.077819 | 0.045777 | -0.082398 | -0.16937 | -0.13733 | 3.0533 | 0.44403 | 4.0054 | 0.52643 | 4.0878 | 0.76904 | 121.7011 | 3.1357 | 121.7377 | 121.5042 | 121.7056 | 121.5179 | 121.6232 | -121.7789 | -121.875 | 121.7148 | 121.6553 | 102.4658 | 54.6524
1178.6719 | 121.8933 | -121.6141 | 0.086975 | 0.02121 | 6.9742 | 0.067823 | 0.061938 | -0.0045586 | -0.0056867 | -0.0010852 | -0.00054933 | -0.0001174 | 0.069293 | 0.057851 | -0.0051313 | 0.027453 | -0.001583 | -19.2032 | -0.12817 | -121.6187 | 0.068665 | -120.8633 | -121.582 | -121.6965 | -67.3599 | -0.022888 | -121.7239 | 0.086975 | -118.2632 | -117.2516 | -121.1151 | -0.004577 | -0.21515 | -0.01831 | 0.75073 | -0.082397 | 0.032044 | -0.07782 | 0.036621 | -0.10986 | -0.10986 | 0 | 3.3508 | 0.49896 | 4.3625 | 0.60883 | 4.4724 | 0.75531 | 121.6873 | 3.4607 | 121.8109 | 121.4905 | 121.7011 | 121.4859 | 121.5912 | -121.7056 | -121.8109 | 121.6827 | 121.701 | 102.4109 | 54.2542
1180.3594 | 121.9299 | -121.6003 | 0.064087 | -0.0016785 | 6.9739 | 0.065901 | 0.062365 | 0.00014097 | -0.0073957 | -0.0030078 | -0.0066527 | 0.0020188 | 0.06972 | 0.059347 | -0.0023541 | 0.028094 | 0.00076681 | -19.1757 | -0.14648 | -121.5866 | 0.1236 | -120.8313 | -121.5591 | -121.6965 | -67.4515 | -0.068665 | -121.6782 | 0.14191 | -117.9749 | -116.8854 | -121.019 | 0.013733 | -0.21057 | 0.059509 | 0.76904 | -0.09613 | 0.041199 | -0.10986 | 0.027466 | -0.07782 | -0.13275 | 0.07782 | 3.6255 | 0.58136 | 4.715 | 0.65918 | 4.7928 | 0.75531 | 121.7102 | 3.7033 | 121.8201 | 121.4401 | 121.6095 | 121.4539 | 121.5317 | -121.6507 | -121.7422 | 121.7239 | 121.7422 | 102.4246 | 54.1489
1182.0938 | 121.8246 | -121.6415 | 0.12817 | 0.01358 | 6.9733 | 0.066114 | 0.064715 | -7.2628e-05 | -0.0059003 | -0.00087163 | 0.0025025 | 0.004155 | 0.071216 | 0.063405 | -0.0053449 | 0.028307 | 0.00055321 | -19.194 | -0.12817 | -121.6324 | 0.082397 | -120.8817 | -121.6324 | -121.7285 | -67.9321 | -0.022888 | -121.7377 | 0.032043 | -117.7872 | -116.6336 | -121.0785 | 0.009156 | -0.25635 | -0.045777 | 0.75989 | -0.086975 | 0.009156 | -0.096131 | 0 | -0.09613 | -0.15106 | -0.096131 | 3.8544 | 0.56305 | 5.0079 | 0.65918 | 5.1041 | 0.75073 | 121.7148 | 3.9505 | 121.7697 | 121.5042 | 121.7148 | 121.5134 | 121.6187 | -121.7606 | -121.8658 | 121.7239 | 121.6736 | 102.4475 | 53.7094
1183.8281 | 121.8384 | -121.6278 | 0.1236 | 0.01358 | 6.9767 | 0.067396 | 0.065569 | -0.0022088 | -0.0061139 | -0.0019396 | 0.017761 | 0.002446 | 0.073779 | 0.060628 | -0.0053449 | 0.029375 | 0.00098061 | -19.2078 | -0.059509 | -121.6599 | 0.064087 | -120.8725 | -121.582 | -121.7148 | -67.5842 | -0.009155 | -121.7422 | 0.050354 | -117.4347 | -116.185 | -120.9915 | -0.032043 | -0.1831 | -0.059509 | 0.75531 | -0.086975 | 0.045777 | -0.054932 | 0.07782 | -0.11444 | -0.13275 | -0.073242 | 4.1931 | 0.63629 | 5.4428 | 0.75073 | 5.5573 | 0.78735 | 121.7239 | 4.3076 | 121.7926 | 121.6003 | 121.7331 | 121.5683 | 121.6187 | -121.7834 | -121.8658 | 121.6919 | 121.6782 | 102.42 | 54.0436
1185.5 | 121.8933 | -121.6095 | 0.10071 | 0.01358 | 6.9737 | 0.067823 | 0.061511 | -0.00028623 | -0.0056867 | -0.0025806 | 0.0055543 | 9.6204e-05 | 0.071429 | 0.062337 | -0.0055585 | 0.02788 | 0.0024758 | -19.2719 | -0.11444 | -121.6232 | 0.082397 | -120.8496 | -121.5775 | -121.701 | -67.4744 | -0.036621 | -121.7377 | 0.064087 | -117.0776 | -115.7593 | -120.9549 | -0.013733 | -0.21515 | -0.018311 | 0.75989 | -0.091553 | 0.032043 | -0.07782 | 0.045776 | -0.12817 | -0.13733 | -0.036621 | 4.5319 | 0.6546 | 5.8502 | 0.78278 | 5.9784 | 0.77362 | 121.7056 | 4.66 | 121.8018 | 121.5088 | 121.7011 | 121.4951 | 121.5729 | -121.7239 | -121.8384 | 121.6919 | 121.6736 | 102.3376 | 54.1351
1187.2344 | 121.9574 | -121.6324 | 0.082397 | -0.0016785 | 6.9737 | 0.066328 | 0.060229 | -0.001568 | -0.0069683 | -0.0015124 | -0.0066527 | 0.002446 | 0.073138 | 0.065755 | -0.0059857 | 0.026812 | -0.0020102 | -19.1757 | -0.15564 | -121.6187 | 0.15106 | -120.7718 | -121.4905 | -121.6324 | -66.9022 | -0.068665 | -121.7056 | 0.14191 | -116.5649 | -115.2832 | -120.8633 | 0.013733 | -0.23804 | 0.068665 | 0.8606 | 0 | 0.14191 | -0.013733 | 0.12817 | -0.073242 | -0.15106 | 0.05951 | 5.0674 | 0.76904 | 6.3492 | 0.84229 | 6.4224 | 0.84686 | 121.7697 | 5.1407 | 121.8475 | 121.463 | 121.637 | 121.4767 | 121.5637 | -121.701 | -121.788 | 121.7834 | 121.7743 | 102.4567 | 54.7302
1188.9688 | 121.907 | -121.5958 | 0.068665 | 0.036468 | 6.9759 | 0.06825 | 0.064715 | 0.00099557 | -0.0044049 | -0.0010852 | 0.0086061 | 0.002446 | 0.07442 | 0.070455 | -0.0025677 | 0.029162 | -8.7586e-05 | -19.1711 | -0.1236 | -121.6141 | 0.16022 | -120.7672 | -121.5317 | -121.6415 | -65.9592 | -0.027466 | -121.701 | 0.1236 | -116.2949 | -114.9948 | -120.8359 | -0.018311 | -0.19226 | 0.091552 | 0.82855 | -0.045777 | 0.064087 | -0.027466 | 0.082398 | -0.10529 | -0.096131 | 0.054931 | 5.3009 | 0.75989 | 6.601 | 0.86517 | 6.7062 | 0.84686 | 121.7743 | 5.4062 | 121.8246 | 121.4905 | 121.6736 | 121.4722 | 121.5683 | -121.6827 | -121.7697 | 121.756 | 121.7194 | 102.4246 | 55.6366
1190.7188 | 121.8567 | -121.6049 | 0.10529 | 0.028839 | 6.9752 | 0.065901 | 0.064288 | -7.2628e-05 | -0.0039777 | -0.00023063 | 0.011658 | 0.0043686 | 0.075702 | 0.058278 | -0.0066265 | 0.028307 | 0.0039712 | -19.1757 | -0.082397 | -121.6553 | 0.086975 | -120.8679 | -121.5866 | -121.7239 | -64.9155 | 0.004578 | -121.7239 | 0.054932 | -116.0019 | -114.7156 | -120.813 | -0.050354 | -0.18768 | -0.018311 | 0.737 | -0.11902 | 0.01831 | -0.068665 | 0.068664 | -0.11902 | -0.10071 | -0.050354 | 5.603 | 0.79193 | 6.8893 | 0.91095 | 7.0084 | 0.78735 | 121.7422 | 5.722 | 121.7789 | 121.5729 | 121.7285 | 121.5225 | 121.6095 | -121.7606 | -121.8292 | 121.6919 | 121.6599 | 102.4292 | 56.6895
1192.4062 | 121.8246 | -121.6507 | 0.10071 | -0.0016785 | 6.9752 | 0.068464 | 0.064715 | 0.0022772 | -0.0054731 | 0.00062377 | 0.0025025 | 0.002446 | 0.071856 | 0.056142 | -0.0068403 | 0.029589 | 0.0039712 | -19.249 | -0.11902 | -121.6507 | 0.004578 | -120.9549 | -121.6827 | -121.788 | -63.7115 | -0.032043 | -121.7422 | 0.022888 | -115.6036 | -114.4318 | -120.8221 | 0 | -0.21973 | -0.09613 | 0.6958 | -0.13733 | -0.032043 | -0.13733 | -0.032043 | -0.091553 | -0.13275 | -0.07782 | 6.0471 | 0.82855 | 7.2189 | 0.92011 | 7.3105 | 0.6958 | 121.6553 | 6.1386 | 121.7651 | 121.5317 | 121.7102 | 121.5317 | 121.6187 | -121.7514 | -121.843 | 121.6553 | 121.6736 | 102.4017 | 57.9391
1194.1406 | 121.8109 | -121.6553 | 0.1236 | -0.016937 | 6.9727 | 0.065473 | 0.065142 | -0.001568 | -0.0054731 | -0.0010852 | 0.017761 | 0.0033004 | 0.07677 | 0.062765 | -0.0083355 | 0.029162 | 0.003544 | -19.2764 | -0.10529 | -121.6507 | 0.018311 | -120.9412 | -121.6232 | -121.7606 | -63.1165 | 0.013733 | -121.7606 | -0.009155 | -115.1825 | -113.9969 | -120.7489 | 0.004577 | -0.22888 | -0.10528 | 0.71411 | -0.10529 | 0.032043 | -0.10986 | 0.027466 | -0.10529 | -0.10986 | -0.13275 | 6.4728 | 0.90637 | 7.6584 | 1.0117 | 7.7637 | 0.70953 | 121.669 | 6.5781 | 121.7514 | 121.5454 | 121.7743 | 121.55 | 121.669 | -121.7743 | -121.8842 | 121.6736 | 121.6461 | 102.3788 | 58.5388
1195.875 | 121.7972 | -121.6507 | 0.11444 | -0.009308 | 6.9737 | 0.064832 | 0.06322 | 0.0012092 | -0.0054731 | -1.7026e-05 | 0.017761 | 0.004155 | 0.075488 | 0.064687 | -0.0074811 | 0.029162 | 0.0039712 | -19.2673 | -0.10071 | -121.6415 | 0.041199 | -120.9 | -121.6187 | -121.7285 | -62.7274 | 0.027466 | -121.756 | -0.004578 | -114.7888 | -113.5483 | -120.6802 | 0.009155 | -0.21515 | -0.073242 | 0.75073 | -0.07782 | 0.032044 | -0.086975 | 0.022889 | -0.10529 | -0.086975 | -0.11902 | 6.8619 | 0.97046 | 8.1024 | 1.0757 | 8.2077 | 0.74158 | 121.6827 | 6.9672 | 121.7514 | 121.5408 | 121.7834 | 121.55 | 121.6782 | -121.756 | -121.8704 | 121.6919 | 121.6461 | 102.3834 | 58.9233
1197.5469 | 121.8246 | -121.6415 | 0.091553 | -0.009308 | 6.9746 | 0.06526 | 0.064288 | -0.00071343 | -0.0065411 | -0.0030078 | -0.00054933 | 0.0039414 | 0.075915 | 0.062124 | -0.0047039 | 0.030016 | 0.0043984 | -19.2673 | -0.11902 | -121.6415 | 0.009155 | -120.9457 | -121.6782 | -121.7697 | -62.5488 | -0.036621 | -121.7422 | 0.018311 | -114.3448 | -113.1042 | -120.5704 | 0 | -0.21057 | -0.082398 | 0.6958 | -0.12817 | -0.036621 | -0.12817 | -0.036621 | -0.10071 | -0.12817 | -0.073242 | 7.2968 | 1.0712 | 8.5373 | 1.1719 | 8.638 | 0.6958 | 121.6507 | 7.3975 | 121.7606 | 121.5225 | 121.7056 | 121.5225 | 121.6049 | -121.7331 | -121.8338 | 121.6507 | 121.6599 | 102.3743 | 59.0927
1199.2812 | 121.9299 | -121.582 | 0.07782 | -0.009308 | 6.9737 | 0.066969 | 0.063006 | -0.00092703 | -0.0052595 | -0.0010852 | -0.00054933 | -0.0005448 | 0.075702 | 0.057424 | -0.0074811 | 0.030657 | 0.0016214 | -19.1391 | -0.15106 | -121.6049 | 0.14648 | -120.7626 | -121.4859 | -121.6187 | -62.4344 | -0.045776 | -121.6827 | 0.14191 | -113.7497 | -112.4405 | -120.4468 | -0.022888 | -0.22888 | 0.068664 | 0.8194 | -0.036621 | 0.09613 | -0.013733 | 0.11902 | -0.10071 | -0.1236 | 0.064087 | 7.8323 | 1.1353 | 9.1415 | 1.236 | 9.2422 | 0.84228 | 121.7514 | 7.933 | 121.8246 | 121.4539 | 121.637 | 121.431 | 121.5363 | -121.6827 | -121.7606 | 121.7285 | 121.7239 | 102.4429 | 59.1476
1201.0312 | 121.9116 | -121.6003 | 0.082397 | 0.036468 | 6.975 | 0.06825 | 0.06386 | 0.0020636 | -0.0024823 | 0.00083737 | 0.020813 | 0.0003098 | 0.077624 | 0.06661 | -0.0034223 | 0.032793 | 0.0048258 | -19.1299 | -0.1236 | -121.6278 | 0.16479 | -120.7626 | -121.5225 | -121.6507 | -62.5168 | -0.027466 | -121.7239 | 0.11902 | -113.3377 | -111.9507 | -120.3873 | -0.027466 | -0.20599 | 0.082398 | 0.83771 | -0.050354 | 0.07782 | -0.022888 | 0.10529 | -0.1236 | -0.10986 | 0.036622 | 8.2626 | 1.2131 | 9.6497 | 1.3367 | 9.7733 | 0.86517 | 121.7926 | 8.3862 | 121.843 | 121.5042 | 121.6965 | 121.4767 | 121.5729 | -121.7102 | -121.8063 | 121.7651 | 121.7194 | 102.4704 | 59.0836
1202.7812 | 121.9254 | -121.582 | 0.10529 | -0.0016785 | 6.9733 | 0.064405 | 0.062151 | -0.001568 | -0.0061139 | -0.0012988 | -0.00054933 | 0.0020188 | 0.078052 | 0.057424 | -0.0059857 | 0.032152 | 0.0061074 | -19.1254 | -0.14648 | -121.6095 | 0.15564 | -120.7855 | -121.5042 | -121.6415 | -62.1689 | -0.050354 | -121.6919 | 0.11902 | -112.6053 | -111.3876 | -120.2957 | -0.027466 | -0.25177 | 0.050354 | 0.79651 | -0.05951 | 0.07782 | -0.032044 | 0.10529 | -0.10986 | -0.15564 | 0.013733 | 8.9767 | 1.2863 | 10.1944 | 1.3962 | 10.3043 | 0.82398 | 121.7651 | 9.0866 | 121.8109 | 121.463 | 121.6415 | 121.4355 | 121.5317 | -121.7148 | -121.7972 | 121.7377 | 121.701 | 102.4567 | 59.4131
1204.5312 | 121.9116 | -121.6003 | 0.082397 | -0.0016785 | 6.9731 | 0.066969 | 0.062579 | -7.2628e-05 | -0.0084637 | -0.0010852 | -0.00054933 | 0.0009506 | 0.078479 | 0.073018 | -0.0070539 | 0.03258 | 0.0054666 | -19.2123 | -0.15106 | -121.6232 | 0.10071 | -120.8496 | -121.5729 | -121.6782 | -62.1735 | -0.059509 | -121.7102 | 0.10071 | -111.9324 | -110.8978 | -120.1767 | -0.022888 | -0.23346 | 0.018311 | 0.75073 | -0.07782 | 0.027466 | -0.054932 | 0.050354 | -0.10986 | -0.14191 | 0.018311 | 9.668 | 1.4236 | 10.7025 | 1.5335 | 10.8124 | 0.77362 | 121.7239 | 9.7778 | 121.8109 | 121.4722 | 121.6507 | 121.4493 | 121.5408 | -121.7056 | -121.7926 | 121.701 | 121.701 | 102.388 | 59.4269
1206.2188 | 121.8567 | -121.6187 | 0.09613 | 0.036468 | 6.9774 | 0.069532 | 0.064715 | -0.0030634 | -0.0026959 | 0.00041017 | 0.014709 | 0.0030868 | 0.080829 | 0.063405 | -0.0070539 | 0.031084 | 0.006962 | -19.1162 | -0.091553 | -121.6599 | 0.073242 | -120.8725 | -121.5775 | -121.7148 | -62.5305 | -0.004578 | -121.7239 | 0.050354 | -111.3831 | -110.4538 | -120.1492 | -0.041199 | -0.18768 | -0.022888 | 0.74615 | -0.096131 | 0.041198 | -0.054932 | 0.082397 | -0.10529 | -0.10071 | -0.045776 | 10.2356 | 1.4694 | 11.1649 | 1.5747 | 11.2701 | 0.78735 | 121.7331 | 10.3409 | 121.7743 | 121.5683 | 121.7194 | 121.5271 | 121.6141 | -121.756 | -121.8201 | 121.6919 | 121.669 | 102.5024 | 59.0881
1207.9062 | 121.843 | -121.6553 | 0.12817 | 0.028839 | 6.9776 | 0.069105 | 0.064288 | -0.0039178 | -0.0071821 | -0.0015124 | 0.014709 | 0.004155 | 0.082965 | 0.055929 | -0.0081219 | 0.032793 | 0.0026896 | -19.1208 | -0.073242 | -121.6599 | 0.068665 | -120.9137 | -121.6003 | -121.7285 | -62.4344 | 0.032043 | -121.7514 | 0.018311 | -110.9482 | -109.9319 | -120.076 | -0.004578 | -0.20142 | -0.059509 | 0.74158 | -0.073243 | 0.054931 | -0.068665 | 0.059509 | -0.096131 | -0.096131 | -0.10986 | 10.7071 | 1.5793 | 11.7233 | 1.6754 | 11.8195 | 0.74616 | 121.7285 | 10.8032 | 121.7697 | 121.5866 | 121.7834 | 121.582 | 121.6873 | -121.788 | -121.8796 | 121.7239 | 121.6736 | 102.5345 | 59.2209
1209.6406 | 121.8567 | -121.637 | 0.11444 | 0.028839 | 6.9739 | 0.069532 | 0.063647 | 0.0012092 | -0.0046185 | 0.001051 | 0.011658 | 0.0030868 | 0.082751 | 0.058065 | -0.0085491 | 0.032152 | 0.0084574 | -19.1299 | -0.068665 | -121.669 | 0.059509 | -120.8817 | -121.5729 | -121.7056 | -62.439 | 0.018311 | -121.7468 | 0.050354 | -110.376 | -109.3964 | -119.9432 | -0.032043 | -0.18311 | -0.054932 | 0.75531 | -0.068664 | 0.064087 | -0.036621 | 0.09613 | -0.10986 | -0.09613 | -0.064087 | 11.261 | 1.6937 | 12.2406 | 1.8036 | 12.3505 | 0.78735 | 121.7285 | 11.3708 | 121.7972 | 121.6003 | 121.7651 | 121.5683 | 121.6553 | -121.7834 | -121.8613 | 121.6965 | 121.6873 | 102.507 | 59.198
1211.375 | 121.9162 | -121.6095 | 0.10529 | -0.0016785 | 6.9739 | 0.066541 | 0.061297 | 0.00035457 | -0.0065411 | -0.0019396 | -0.00054933 | 0.0005234 | 0.079974 | 0.060628 | -0.0059857 | 0.034075 | 0.0029032 | -19.0704 | -0.15564 | -121.6095 | 0.15106 | -120.7764 | -121.5088 | -121.6507 | -62.1506 | -0.054932 | -121.6873 | 0.1236 | -109.7122 | -108.7006 | -119.7556 | 0 | -0.26093 | 0.045776 | 0.83313 | -0.041199 | 0.10071 | -0.041199 | 0.10071 | -0.07782 | -0.16022 | 0.01831 | 11.8973 | 1.8539 | 12.9089 | 1.9318 | 12.9868 | 0.83313 | 121.7606 | 11.9751 | 121.8109 | 121.4539 | 121.6324 | 121.4539 | 121.5546 | -121.7148 | -121.7926 | 121.7606 | 121.7331 | 102.5391 | 59.4589
1213.1094 | 121.8613 | -121.6278 | 0.10986 | 0.028839 | 6.9752 | 0.069532 | 0.063433 | 0.0033454 | -0.0052595 | -0.0027942 | 0.0086061 | 0.0056504 | 0.083178 | 0.062551 | -0.0083355 | 0.034929 | 0.0095254 | -19.0659 | -0.10071 | -121.6324 | 0.091553 | -120.8817 | -121.5866 | -121.6965 | -62.2421 | -0.004578 | -121.7239 | 0.054932 | -109.2911 | -108.3023 | -119.7052 | -0.004577 | -0.21057 | -0.01831 | 0.74616 | -0.068664 | 0.041199 | -0.064087 | 0.045776 | -0.09613 | -0.11444 | -0.054931 | 12.3367 | 1.9226 | 13.3255 | 2.0187 | 13.4216 | 0.75073 | 121.7239 | 12.4329 | 121.7789 | 121.5317 | 121.7194 | 121.5271 | 121.6232 | -121.7422 | -121.8338 | 121.7194 | 121.6827 | 102.562 | 59.3857
1214.8594 | 121.9299 | -121.582 | 0.09613 | -0.009308 | 6.9724 | 0.067396 | 0.06322 | 0.00056817 | -0.0088911 | -0.0019396 | -0.0036011 | 0.0009506 | 0.082538 | 0.06191 | -0.0066265 | 0.034289 | 0.01038 | -19.1757 | -0.14648 | -121.5866 | 0.10071 | -120.8359 | -121.5408 | -121.6644 | -61.1755 | -0.036621 | -121.701 | 0.12817 | -108.7601 | -107.6248 | -119.5404 | -0.004578 | -0.24261 | 0.004578 | 0.74616 | -0.082398 | 0.041198 | -0.07782 | 0.045776 | -0.11902 | -0.13275 | 0.032044 | 12.822 | 2.0416 | 13.9572 | 2.1606 | 14.0762 | 0.75073 | 121.6873 | 12.941 | 121.8292 | 121.4401 | 121.6644 | 121.4355 | 121.5454 | -121.6827 | -121.7972 | 121.6827 | 121.7102 | 102.4063 | 60.4065
1216.5938 | 121.8109 | -121.6461 | 0.12817 | -0.009308 | 6.9752 | 0.067823 | 0.064501 | 0.00099557 | -0.0061139 | -0.0012988 | -0.00054933 | 0.003514 | 0.084887 | 0.05422 | -0.0059857 | 0.034929 | 0.010166 | -19.1849 | -0.10529 | -121.6415 | 0 | -120.9732 | -121.6644 | -121.7697 | -60.4477 | -0.009155 | -121.7148 | 0.018311 | -108.4442 | -107.135 | -119.5221 | 0.004577 | -0.23346 | -0.12817 | 0.67291 | -0.1236 | -0.018311 | -0.12817 | -0.022888 | -0.068665 | -0.13733 | -0.10986 | 13.2019 | 2.124 | 14.5111 | 2.1927 | 14.5798 | 0.66833 | 121.6415 | 13.2706 | 121.7331 | 121.5363 | 121.7056 | 121.5408 | 121.637 | -121.7697 | -121.843 | 121.6461 | 121.6644 | 102.4612 | 61.1984
1218.2656 | 121.8155 | -121.6324 | 0.13733 | 0.005951 | 6.9748 | 0.067182 | 0.065356 | 0.0020636 | -0.0065411 | -0.0025806 | 0.0025025 | 0.0018052 | 0.087451 | 0.055929 | -0.0074811 | 0.034929 | 0.013371 | -19.1574 | -0.10529 | -121.637 | 0.022888 | -120.9686 | -121.669 | -121.7972 | -59.9304 | -0.004578 | -121.7514 | 0.004578 | -107.8674 | -106.5125 | -119.4397 | -0.004578 | -0.24262 | -0.11444 | 0.66376 | -0.16479 | -0.036621 | -0.16022 | -0.032043 | -0.11902 | -0.14191 | -0.13275 | 13.765 | 2.1927 | 15.1199 | 2.3117 | 15.239 | 0.66833 | 121.6599 | 13.884 | 121.756 | 121.5317 | 121.7468 | 121.5271 | 121.6278 | -121.7743 | -121.8887 | 121.6553 | 121.637 | 102.475 | 61.702
1219.9531 | 121.8979 | -121.5958 | 0.091553 | 0.005951 | 6.9744 | 0.065901 | 0.06386 | -0.0034906 | -0.0061139 | -0.0030078 | -0.0036011 | -0.0001174 | 0.085528 | 0.063192 | -0.0057721 | 0.037707 | 0.011234 | -19.0567 | -0.13733 | -121.6049 | 0.15564 | -120.7855 | -121.5042 | -121.6553 | -59.7336 | -0.036621 | -121.6827 | 0.091553 | -107.1991 | -105.8258 | -119.2337 | -0.009155 | -0.22888 | 0.064087 | 0.81024 | -0.059509 | 0.091553 | -0.050354 | 0.10071 | -0.086975 | -0.12817 | 0 | 14.3967 | 2.3621 | 15.77 | 2.449 | 15.8569 | 0.8194 | 121.7606 | 14.4836 | 121.7743 | 121.4676 | 121.6461 | 121.4584 | 121.5591 | -121.6965 | -121.7743 | 121.7514 | 121.6873 | 102.5391 | 61.8622
1221.7031 | 121.7972 | -121.6003 | 0.12817 | -0.0016785 | 6.975 | 0.067396 | 0.065569 | 0.0031318 | -0.0080365 | -0.0010852 | -0.0066527 | 0.0033004 | 0.089587 | 0.063833 | -0.0059857 | 0.037493 | 0.01038 | -19.0979 | -0.1236 | -121.6324 | 0.050354 | -120.9183 | -121.6461 | -121.7606 | -59.7519 | -0.013733 | -121.6873 | 0.013733 | -106.7459 | -105.4596 | -119.1742 | -0.032043 | -0.25177 | -0.07782 | 0.68207 | -0.16022 | -0.045776 | -0.12817 | -0.013733 | -0.086975 | -0.14191 | -0.11444 | 14.8544 | 2.4261 | 16.1407 | 2.5131 | 16.2277 | 0.71411 | 121.6827 | 14.9414 | 121.701 | 121.5088 | 121.6736 | 121.4767 | 121.5866 | -121.7606 | -121.8155 | 121.6507 | 121.6141 | 102.5024 | 61.8484
1223.4375 | 121.9437 | -121.5912 | 0.09613 | -0.0016785 | 6.9739 | 0.066969 | 0.061938 | -0.00049983 | -0.0059003 | -0.0021532 | -0.0036011 | 0.0003098 | 0.087024 | 0.071523 | -0.0057721 | 0.037279 | 0.014652 | -19.1208 | -0.14191 | -121.5958 | 0.15564 | -120.7489 | -121.4859 | -121.6187 | -59.3536 | -0.054932 | -121.6553 | 0.11902 | -106.041 | -104.599 | -118.9407 | -0.004577 | -0.23804 | 0.05951 | 0.84229 | -0.027465 | 0.10529 | -0.022888 | 0.10986 | -0.064086 | -0.15106 | 0.022889 | 15.5502 | 2.6505 | 16.9922 | 2.7145 | 17.0563 | 0.84686 | 121.7514 | 15.6143 | 121.7743 | 121.4539 | 121.6003 | 121.4493 | 121.5363 | -121.6919 | -121.7514 | 121.7468 | 121.7102 | 102.4704 | 62.2375
1225.1875 | 121.8887 | -121.6095 | 0.10529 | 0.01358 | 6.9733 | 0.069105 | 0.061724 | 0.003559 | -0.0071821 | 0.0014784 | -0.00054933 | 0.0015914 | 0.089801 | 0.070669 | -0.0072675 | 0.038347 | 0.013798 | -19.194 | -0.11444 | -121.6187 | 0.091553 | -120.8405 | -121.5683 | -121.6919 | -58.9188 | -0.045776 | -121.7194 | 0.09613 | -105.5237 | -103.7796 | -118.8629 | -0.009155 | -0.21973 | -0.013733 | 0.76904 | -0.082398 | 0.041199 | -0.073243 | 0.050354 | -0.10986 | -0.15106 | -0.009156 | 16.0858 | 2.7466 | 17.8299 | 2.8564 | 17.9398 | 0.7782 | 121.7102 | 16.1957 | 121.8155 | 121.5042 | 121.6736 | 121.4951 | 121.5637 | -121.7239 | -121.8246 | 121.7011 | 121.7056 | 102.4155 | 62.6907
1226.9219 | 121.8155 | -121.637 | 0.13733 | -0.009308 | 6.9737 | 0.065473 | 0.066424 | -0.0041314 | -0.0071821 | -0.0021532 | -0.0036011 | 0.004155 | 0.091083 | 0.064901 | -0.0040631 | 0.040484 | 0.018711 | -19.1528 | -0.10529 | -121.6415 | 0.018311 | -120.9595 | -121.6644 | -121.7651 | -58.6624 | 0 | -121.701 | 0.009155 | -105.1209 | -103.1525 | -118.808 | -0.004578 | -0.24262 | -0.11902 | 0.67749 | -0.12817 | -0.027466 | -0.1236 | -0.022888 | -0.064087 | -0.13733 | -0.12817 | 16.5161 | 2.829 | 18.4845 | 2.8931 | 18.5486 | 0.68207 | 121.6599 | 16.5802 | 121.7102 | 121.5363 | 121.701 | 121.5317 | 121.637 | -121.7789 | -121.8384 | 121.6553 | 121.6461 | 102.4841 | 62.9745
1228.6562 | 121.7972 | -121.637 | 0.11902 | -0.0016785 | 6.9748 | 0.067396 | 0.06386 | 0.0016364 | -0.0080365 | -0.002367 | -0.00054933 | 0.0018052 | 0.091296 | 0.065114 | -0.0094037 | 0.035784 | 0.020634 | -19.162 | -0.09613 | -121.6324 | 0.045776 | -120.9274 | -121.6003 | -121.7377 | -58.6212 | -0.013733 | -121.7285 | 0.004578 | -104.5395 | -102.4475 | -118.7073 | 0.004578 | -0.21515 | -0.073243 | 0.70953 | -0.10071 | 0.036621 | -0.10529 | 0.032043 | -0.091553 | -0.13275 | -0.11444 | 17.0975 | 2.9297 | 19.1895 | 3.0212 | 19.281 | 0.70496 | 121.6782 | 17.189 | 121.7331 | 121.5363 | 121.7148 | 121.5408 | 121.6232 | -121.7514 | -121.8475 | 121.6827 | 121.6415 | 102.475 | 63.0157
1230.4062 | 121.8155 | -121.6324 | 0.14191 | -0.0016785 | 6.9746 | 0.066328 | 0.062365 | -0.0037042 | -0.0063275 | -0.00044443 | -0.00054933 | 0.0015914 | 0.092578 | 0.067464 | -0.0091901 | 0.041338 | 0.018711 | -19.0704 | -0.12817 | -121.6003 | 0.064087 | -120.8817 | -121.5775 | -121.7194 | -58.6807 | -0.018311 | -121.7056 | 0.018311 | -104.0588 | -101.8662 | -118.5196 | 0.032043 | -0.27008 | -0.07782 | 0.75073 | -0.086975 | 0.054931 | -0.11902 | 0.022888 | -0.073242 | -0.16022 | -0.1236 | 17.5735 | 3.1128 | 19.7662 | 3.186 | 19.8395 | 0.71869 | 121.6644 | 17.6468 | 121.7239 | 121.4722 | 121.6873 | 121.5042 | 121.6141 | -121.7422 | -121.8475 | 121.6965 | 121.6507 | 102.5619 | 62.9517
1232.0938 | 121.8796 | -121.5958 | 0.10071 | 0.02121 | 6.9731 | 0.06825 | 0.064715 | -0.00049983 | -0.0063275 | -0.0015124 | -0.00054933 | 0.0028732 | 0.097064 | 0.066396 | -0.0055585 | 0.039843 | 0.019993 | -19.1437 | -0.12817 | -121.5866 | 0.10529 | -120.8313 | -121.5591 | -121.6782 | -58.58 | -0.041199 | -121.701 | 0.086975 | -103.7064 | -101.12 | -118.3685 | 0.009155 | -0.22888 | 0.004578 | 0.76447 | -0.082398 | 0.036621 | -0.091553 | 0.027466 | -0.10529 | -0.14191 | -0.013733 | 17.8894 | 3.2272 | 20.4758 | 3.3325 | 20.5811 | 0.75531 | 121.6919 | 17.9947 | 121.788 | 121.4584 | 121.6599 | 121.4676 | 121.5546 | -121.6873 | -121.8018 | 121.7011 | 121.6827 | 102.4521 | 63.0157
1233.8281 | 121.8842 | -121.5775 | 0.10986 | 0.028839 | 6.9748 | 0.06825 | 0.06087 | -0.0034906 | -0.0041913 | 0.00019657 | 0.0025025 | 0.003514 | 0.093432 | 0.067251 | -0.0053449 | 0.04027 | 0.018711 | -19.1208 | -0.12817 | -121.5912 | 0.10529 | -120.845 | -121.5546 | -121.6736 | -57.9437 | -0.050354 | -121.6873 | 0.091553 | -103.1433 | -100.3326 | -118.2449 | -0.013733 | -0.23804 | -0.004577 | 0.73242 | -0.09613 | 0.022889 | -0.082397 | 0.036622 | -0.10986 | -0.16022 | -0.01831 | 18.4341 | 3.3325 | 21.2448 | 3.4424 | 21.3547 | 0.74616 | 121.6965 | 18.544 | 121.7789 | 121.463 | 121.637 | 121.4493 | 121.5271 | -121.7011 | -121.7972 | 121.6827 | 121.669 | 102.4567 | 63.6337
1235.5625 | 121.8933 | -121.5912 | 0.10529 | -0.016937 | 6.9756 | 0.067396 | 0.062151 | 0.00099557 | -0.0054731 | -0.0019396 | -0.0066527 | 0.0030868 | 0.094501 | 0.067464 | -0.0089765 | 0.041125 | 0.019138 | -19.0475 | -0.14191 | -121.6187 | 0.16479 | -120.7809 | -121.4996 | -121.6278 | -57.7606 | -0.022888 | -121.669 | 0.091553 | -102.2598 | -99.7147 | -118.103 | -0.027465 | -0.24719 | 0.059509 | 0.81024 | -0.036621 | 0.091553 | -0.009156 | 0.11902 | -0.077819 | -0.12817 | -0.013733 | 19.3314 | 3.4882 | 21.8765 | 3.566 | 21.9543 | 0.83771 | 121.7834 | 19.4092 | 121.7606 | 121.4767 | 121.6461 | 121.4493 | 121.5683 | -121.7239 | -121.7743 | 121.756 | 121.6827 | 102.5436 | 63.8306
1237.2344 | 121.8704 | -121.5866 | 0.10986 | 0.036468 | 6.9739 | 0.068891 | 0.064501 | 0.0039862 | -0.0026959 | -0.0027942 | 0.011658 | 0.0028732 | 0.098773 | 0.073018 | -0.0068403 | 0.04262 | 0.019138 | -19.0842 | -0.10986 | -121.6278 | 0.17395 | -120.7809 | -121.5408 | -121.6461 | -58.0765 | -0.004578 | -121.6873 | 0.10529 | -101.889 | -99.1562 | -117.9886 | -0.041199 | -0.21973 | 0.064087 | 0.80566 | -0.059509 | 0.045776 | -0.01831 | 0.086975 | -0.10071 | -0.11444 | -0.004577 | 19.6976 | 3.598 | 22.4304 | 3.6987 | 22.5311 | 0.84686 | 121.8018 | 19.7983 | 121.7926 | 121.5179 | 121.6827 | 121.4767 | 121.582 | -121.7377 | -121.7972 | 121.7606 | 121.6919 | 102.5024 | 63.5101
1238.9219 | 121.9299 | -121.5683 | 0.086975 | -0.0016785 | 6.9763 | 0.067396 | 0.061511 | 0.00099557 | -0.0056867 | -0.00044443 | -0.0036011 | 0.0020188 | 0.098773 | 0.067251 | -0.0053449 | 0.041765 | 0.023838 | -19.0155 | -0.14648 | -121.6095 | 0.16022 | -120.7626 | -121.4996 | -121.6095 | -58.3557 | -0.054932 | -121.6599 | 0.15106 | -101.4542 | -98.4238 | -117.8009 | -0.041199 | -0.23346 | 0.073242 | 0.80566 | -0.041199 | 0.068664 | 0 | 0.10986 | -0.091553 | -0.14191 | 0.064087 | 20.1141 | 3.7674 | 23.1445 | 3.8589 | 23.2361 | 0.84686 | 121.7697 | 20.2057 | 121.8109 | 121.463 | 121.6049 | 121.4218 | 121.5134 | -121.6965 | -121.7468 | 121.7285 | 121.7194 | 102.5528 | 63.2126
1240.6719 | 121.843 | -121.5912 | 0.1236 | 0.028839 | 6.9752 | 0.068678 | 0.065569 | 0.00035457 | -0.0044049 | 0.001051 | 0.017761 | 0.0047958 | 0.10027 | 0.066396 | -0.0087629 | 0.042193 | 0.024693 | -19.0155 | -0.07782 | -121.6461 | 0.054932 | -120.8817 | -121.5637 | -121.7148 | -58.9279 | 0.041199 | -121.7377 | 0.022888 | -101.1566 | -97.9385 | -117.6956 | -0.054931 | -0.20142 | -0.068664 | 0.70953 | -0.1236 | 0.027466 | -0.068665 | 0.082397 | -0.14648 | -0.082397 | -0.10071 | 20.4346 | 3.8956 | 23.6526 | 4.0421 | 23.7991 | 0.76447 | 121.701 | 20.5811 | 121.7606 | 121.5683 | 121.7789 | 121.5134 | 121.6324 | -121.7697 | -121.8613 | 121.6461 | 121.6141 | 102.5757 | 62.6633
1242.3438 | 121.8063 | -121.6278 | 0.12817 | -0.0016785 | 6.9789 | 0.067823 | 0.065142 | 0.00078177 | -0.0076093 | -0.002367 | -0.00054933 | 0.0039414 | 0.10005 | 0.06426 | -0.0066265 | 0.042406 | 0.023197 | -19.1162 | -0.07782 | -121.6095 | 0.027466 | -120.9274 | -121.6644 | -121.756 | -59.3079 | -0.004578 | -121.701 | 0.022888 | -100.8957 | -97.3343 | -117.5766 | 0.018311 | -0.20599 | -0.10071 | 0.70038 | -0.12817 | -0.036621 | -0.14648 | -0.054932 | -0.073242 | -0.13275 | -0.10529 | 20.7321 | 4.0512 | 24.2935 | 4.1245 | 24.3668 | 0.68207 | 121.637 | 20.8054 | 121.7239 | 121.5317 | 121.6965 | 121.55 | 121.6232 | -121.7377 | -121.8292 | 121.6553 | 121.6507 | 102.5116 | 62.3199
1244.0781 | 121.8842 | -121.5683 | 0.091553 | 0.044098 | 6.9754 | 0.066969 | 0.063647 | 0.00185 | -0.0041913 | -0.0019396 | 0.020813 | 0.0039414 | 0.10283 | 0.068746 | -0.0047039 | 0.045824 | 0.02277 | -19.043 | -0.11902 | -121.6003 | 0.17395 | -120.7626 | -121.5179 | -121.6324 | -59.5551 | -0.009155 | -121.6965 | 0.11902 | -100.1038 | -96.5515 | -117.334 | -0.032044 | -0.21057 | 0.082397 | 0.80566 | -0.064087 | 0.050354 | -0.032043 | 0.082398 | -0.12817 | -0.10071 | 0.027466 | 21.4645 | 4.2343 | 25.0168 | 4.3625 | 25.145 | 0.83771 | 121.7743 | 21.5927 | 121.8155 | 121.4813 | 121.6873 | 121.4493 | 121.5591 | -121.6919 | -121.788 | 121.7422 | 121.6873 | 102.5253 | 62.0132
1245.8281 | 121.8384 | -121.582 | 0.1236 | 0.02121 | 6.9774 | 0.067823 | 0.064501 | 0.0031318 | -0.0059003 | -0.00087163 | 0.0025025 | 0.0062912 | 0.10305 | 0.070028 | -0.0070539 | 0.043474 | 0.021488 | -19.0338 | -0.07782 | -121.6278 | 0.10986 | -120.8405 | -121.5591 | -121.6599 | -60.1318 | 0.009155 | -121.7102 | 0.068665 | -99.614 | -95.8603 | -117.16 | -0.045777 | -0.20142 | -0.013733 | 0.74158 | -0.07782 | 0.022888 | -0.032043 | 0.068665 | -0.12817 | -0.11444 | -0.054931 | 21.9681 | 4.422 | 25.7217 | 4.5502 | 25.8499 | 0.78735 | 121.7377 | 22.0963 | 121.7789 | 121.55 | 121.7194 | 121.5042 | 121.5912 | -121.7514 | -121.8338 | 121.6919 | 121.6507 | 102.5482 | 61.4502
1247.5625 | 121.8933 | -121.582 | 0.10071 | 0.005951 | 6.9746 | 0.068678 | 0.063006 | -0.0030634 | -0.0037641 | -0.0015124 | -0.0036011 | 0.0013778 | 0.10347 | 0.073659 | -0.0053449 | 0.04497 | 0.028111 | -19.0887 | -0.10529 | -121.6049 | 0.09613 | -120.8359 | -121.5408 | -121.6599 | -60.2829 | -0.045776 | -121.669 | 0.09613 | -98.9227 | -94.9997 | -116.9357 | -0.022888 | -0.20599 | -0.004578 | 0.74616 | -0.07782 | 0.041198 | -0.054932 | 0.064086 | -0.086975 | -0.14648 | -0.004578 | 22.6593 | 4.6463 | 26.5823 | 4.7333 | 26.6693 | 0.76904 | 121.701 | 22.7463 | 121.7651 | 121.4996 | 121.6232 | 121.4767 | 121.5363 | -121.7056 | -121.7697 | 121.6782 | 121.6782 | 102.4933 | 61.2991
1249.2344 | 121.7834 | -121.637 | 0.13733 | -0.009308 | 6.9754 | 0.066541 | 0.064074 | 0.00014097 | -0.0084637 | -0.0010852 | -0.00054933 | 0.0037278 | 0.10582 | 0.067892 | -0.0064129 | 0.045824 | 0.02982 | -19.0796 | -0.091553 | -121.5912 | 0.032043 | -120.9274 | -121.6507 | -121.7697 | -60.6583 | 0.013733 | -121.7056 | 0.027466 | -98.5153 | -94.4046 | -116.8304 | 0.045776 | -0.22888 | -0.10529 | 0.70953 | -0.13275 | -0.013733 | -0.17853 | -0.059509 | -0.068664 | -0.1236 | -0.10986 | 23.1216 | 4.8065 | 27.2324 | 4.8752 | 27.301 | 0.66376 | 121.6232 | 23.1903 | 121.7331 | 121.4996 | 121.7194 | 121.5454 | 121.6507 | -121.7285 | -121.843 | 121.669 | 121.6644 | 102.5574 | 60.9787
1250.9219 | 121.8613 | -121.582 | 0.091553 | 0.074615 | 6.9752 | 0.067823 | 0.064929 | -7.2628e-05 | -0.0024823 | 0.001051 | 0.011658 | 0.0030868 | 0.11074 | 0.075155 | -0.0057721 | 0.04796 | 0.032169 | -19.0338 | -0.10986 | -121.5866 | 0.17395 | -120.7352 | -121.4859 | -121.6141 | -60.9375 | -0.009155 | -121.7102 | 0.11902 | -97.9248 | -93.4433 | -116.5558 | -0.004578 | -0.20142 | 0.082397 | 0.84686 | -0.032044 | 0.09613 | -0.027466 | 0.10071 | -0.12817 | -0.10071 | 0.027466 | 23.6572 | 5.0262 | 28.1387 | 5.1544 | 28.2669 | 0.85144 | 121.7606 | 23.7854 | 121.8292 | 121.4767 | 121.701 | 121.4722 | 121.5729 | -121.6782 | -121.8018 | 121.756 | 121.701 | 102.5482 | 60.6445
1252.6719 | 121.7926 | -121.5591 | 0.14191 | -0.0016785 | 6.9769 | 0.069105 | 0.064715 | 0.0029182 | -0.0069683 | -0.0025806 | -0.0036011 | 0.0028732 | 0.11202 | 0.068319 | -0.0044903 | 0.12166 | 0.03516 | -19.0292 | -0.068665 | -121.6003 | 0.036621 | -120.9183 | -121.6232 | -121.7377 | -37.0468 | 0.022888 | -121.6736 | 0.041199 | -97.2565 | -5.2185 | -116.3544 | -0.041199 | -0.21057 | -0.10529 | 0.64087 | -0.17853 | -0.064087 | -0.13733 | -0.022888 | -0.11444 | -0.11902 | -0.10071 | 24.3027 | 5.2048 | 116.3406 | 5.3192 | 116.4551 | 0.68207 | 121.637 | 24.4171 | 121.7148 | 121.5317 | 121.6965 | 121.4905 | 121.582 | -121.7422 | -121.8155 | 121.5958 | 121.6003 | 102.5299 | 84.5123
1254.3438 | 121.8155 | -121.5958 | 0.14191 | -0.0016785 | 6.9763 | 0.068678 | 0.064501 | 0.00014097 | -0.0063275 | -0.00065803 | -0.00054933 | 0.003514 | 0.11287 | 0.072164 | -0.0053449 | 0.12166 | 0.035374 | -19.0659 | -0.09613 | -121.5729 | 0.054932 | -120.8771 | -121.5958 | -121.7331 | -36.6852 | 0.018311 | -121.6782 | 0.054932 | -96.1761 | -4.5136 | -116.1026 | 0.022888 | -0.23804 | -0.086975 | 0.71869 | -0.13733 | 0 | -0.16022 | -0.022888 | -0.082398 | -0.1236 | -0.086975 | 25.4196 | 5.4932 | 117.0822 | 5.5756 | 117.1646 | 0.6958 | 121.6278 | 25.502 | 121.7331 | 121.4767 | 121.6965 | 121.4996 | 121.6141 | -121.7148 | -121.8201 | 121.6507 | 121.6507 | 102.5299 | 84.9106
1256.0312 | 121.8338 | -121.5546 | 0.13275 | 0.028839 | 6.9769 | 0.068678 | 0.06322 | 0.0024908 | -0.0063275 | -0.00023063 | 0.014709 | 0.0050094 | 0.11629 | 0.067892 | -0.0059857 | 0.12187 | 0.033024 | -18.9468 | -0.059509 | -121.5775 | 0.11444 | -120.7809 | -121.5179 | -121.637 | -36.676 | 0.022888 | -121.6553 | 0.091553 | -95.3201 | -4.248 | -115.8783 | -0.022889 | -0.19226 | -0.01831 | 0.77362 | -0.082398 | 0.036621 | -0.059509 | 0.05951 | -0.10071 | -0.10986 | -0.041198 | 26.2344 | 5.6763 | 117.3065 | 5.777 | 117.4072 | 0.79651 | 121.6919 | 26.3351 | 121.7468 | 121.5179 | 121.6782 | 121.4951 | 121.5775 | -121.7102 | -121.788 | 121.669 | 121.6461 | 102.6077 | 84.8785
1257.7812 | 121.8063 | -121.5546 | 0.15106 | -0.009308 | 6.9767 | 0.067182 | 0.063006 | -0.00049983 | -0.0084637 | -0.0025806 | -0.0036011 | 0.0037278 | 0.11821 | 0.061269 | -0.0068403 | 0.12081 | 0.036656 | -19.0155 | -0.07782 | -121.5866 | 0.064087 | -120.8588 | -121.5958 | -121.6965 | -36.85 | 0.013733 | -121.6736 | 0.091553 | -94.4458 | -4.1702 | -115.6082 | -0.032044 | -0.22888 | -0.086975 | 0.6958 | -0.14191 | -0.041199 | -0.10986 | -0.009155 | -0.11902 | -0.13733 | -0.059509 | 27.1088 | 5.9463 | 117.3843 | 6.0654 | 117.5034 | 0.72784 | 121.6507 | 27.2278 | 121.7651 | 121.5088 | 121.6873 | 121.4767 | 121.5683 | -121.7377 | -121.8246 | 121.6187 | 121.6461 | 102.5391 | 84.7046
1259.5156 | 121.7102 | -121.5591 | 0.15106 | 0.02121 | 6.9793 | 0.070387 | 0.06386 | 0.0020636 | -0.0061139 | -0.0021532 | 0.0025025 | 0.0054368 | 0.12078 | 0.072591 | -0.0070539 | 0.12017 | 0.039005 | -18.9285 | -0.068665 | -121.5775 | 0.13733 | -120.7718 | -121.4951 | -121.6141 | -37.5046 | 0.013733 | -121.6278 | 0.10071 | -93.1503 | -4.0833 | -115.2237 | -0.018311 | -0.21973 | -0.013733 | 0.78735 | -0.054932 | 0.064087 | -0.036621 | 0.082398 | -0.068665 | -0.13733 | -0.050354 | 28.4088 | 6.3354 | 117.4759 | 6.4041 | 117.5446 | 0.80566 | 121.7148 | 28.4775 | 121.7285 | 121.5088 | 121.6415 | 121.4905 | 121.5729 | -121.7285 | -121.7789 | 121.6965 | 121.6599 | 102.6306 | 84.0546
1261.2031 | 121.7834 | -121.5591 | 0.15564 | -0.0016785 | 6.9765 | 0.067823 | 0.064929 | 0.0054816 | -0.0050457 | -0.002367 | -0.0066527 | 0.005223 | 0.12249 | 0.069814 | -0.0057721 | 0.12145 | 0.042637 | -19.0292 | -0.059509 | -121.5683 | 0.022888 | -120.8771 | -121.6003 | -121.6965 | -37.8021 | 0.027466 | -121.6461 | 0.045776 | -92.3904 | -4.1061 | -115.0543 | -0.009155 | -0.21515 | -0.13275 | 0.68207 | -0.13733 | -0.041199 | -0.12817 | -0.032044 | -0.086975 | -0.12817 | -0.10986 | 29.1687 | 6.5048 | 117.453 | 6.5918 | 117.54 | 0.69122 | 121.5912 | 29.2557 | 121.6919 | 121.5088 | 121.6736 | 121.4996 | 121.5866 | -121.7239 | -121.8018 | 121.582 | 121.6049 | 102.5299 | 83.757
1262.9531 | 121.8246 | -121.5637 | 0.15106 | 0.036468 | 6.9786 | 0.068037 | 0.064501 | 0.00035457 | -0.0029095 | -0.0025806 | 0.014709 | 0.0062912 | 0.12505 | 0.079214 | -0.0083355 | 0.11995 | 0.037724 | -19.0018 | -0.036621 | -121.6095 | 0.10986 | -120.7901 | -121.4767 | -121.6324 | -37.8342 | 0.050354 | -121.637 | 0.059509 | -91.4017 | -4.0146 | -114.7247 | -0.045776 | -0.18768 | -0.041199 | 0.77362 | -0.068664 | 0.086975 | -0.022888 | 0.13275 | -0.073242 | -0.10071 | -0.091553 | 30.162 | 6.839 | 117.5491 | 6.9122 | 117.6224 | 0.8194 | 121.7194 | 30.2353 | 121.6965 | 121.5729 | 121.6873 | 121.5271 | 121.6141 | -121.7606 | -121.788 | 121.6736 | 121.6232 | 102.562 | 83.7296
1264.6406 | 121.7514 | -121.55 | 0.17395 | -0.009308 | 6.9759 | 0.066755 | 0.064074 | 0.0029182 | -0.0046185 | -0.00065803 | -0.0036011 | 0.0056504 | 0.12676 | 0.073446 | -0.0042767 | 0.12081 | 0.039646 | -19.0109 | -0.073242 | -121.5729 | 0.036621 | -120.8954 | -121.5912 | -121.7102 | -38.0402 | 0.032043 | -121.6461 | 0.036621 | -90.4404 | -4.0375 | -114.4821 | -0.022888 | -0.24719 | -0.13733 | 0.6546 | -0.16022 | -0.041199 | -0.13733 | -0.018311 | -0.09613 | -0.14191 | -0.13733 | 31.1096 | 7.0679 | 117.5125 | 7.164 | 117.6086 | 0.67749 | 121.6095 | 31.2057 | 121.6827 | 121.4996 | 121.6782 | 121.4767 | 121.582 | -121.7468 | -121.8201 | 121.5866 | 121.5866 | 102.5391 | 83.5098
1266.375 | 121.7651 | -121.5454 | 0.15564 | -0.009308 | 6.9759 | 0.069959 | 0.06386 | 0.00035457 | -0.0059003 | -0.00023063 | -0.0036011 | 0.0056504 | 0.12932 | 0.067892 | -0.0068403 | 0.12081 | 0.045628 | -19.0155 | -0.073242 | -121.5729 | 0.018311 | -120.8908 | -121.6003 | -121.7194 | -37.9578 | 0.022888 | -121.6232 | 0.045776 | -89.296 | -4.0146 | -114.1434 | -0.027466 | -0.22888 | -0.13733 | 0.6546 | -0.17395 | -0.054932 | -0.14648 | -0.027466 | -0.07782 | -0.13275 | -0.10986 | 32.2495 | 7.402 | 117.5308 | 7.4799 | 117.6086 | 0.68207 | 121.5912 | 32.3273 | 121.669 | 121.4996 | 121.6461 | 121.4722 | 121.5683 | -121.7285 | -121.7789 | 121.5637 | 121.5912 | 102.5299 | 83.5876
1268.1094 | 121.7743 | -121.5317 | 0.17395 | -0.009308 | 6.9769 | 0.065901 | 0.064288 | -0.0030634 | -0.0076093 | -0.0010852 | -0.00054933 | 0.0056504 | 0.13509 | 0.074087 | -0.010899 | 0.12316 | 0.047764 | -18.9789 | -0.064087 | -121.582 | 0.041199 | -120.8313 | -121.5225 | -121.6644 | -37.825 | 0.045776 | -121.6232 | 0.032043 | -88.0966 | -3.9505 | -113.8046 | -0.050354 | -0.23804 | -0.13275 | 0.70038 | -0.13275 | 0.009155 | -0.082398 | 0.059509 | -0.091553 | -0.12817 | -0.14191 | 33.4351 | 7.7271 | 117.5812 | 7.8186 | 117.6727 | 0.75073 | 121.6232 | 33.5266 | 121.6553 | 121.5179 | 121.669 | 121.4676 | 121.5775 | -121.756 | -121.7972 | 121.5729 | 121.5637 | 102.5528 | 83.7067
1269.8438 | 121.8796 | -121.5225 | 0.14648 | -0.0016785 | 6.9735 | 0.067182 | 0.059161 | -0.00028623 | -0.0078229 | -0.0038622 | -0.0036011 | 0.0073594 | 0.13552 | 0.075582 | -0.0059857 | 0.12252 | 0.052677 | -19.0338 | -0.10986 | -121.5088 | 0.13733 | -120.7306 | -121.4218 | -121.5546 | -37.6007 | -0.009155 | -121.5866 | 0.17395 | -87.3047 | -3.8361 | -113.3881 | 0.013733 | -0.25635 | -0.009155 | 0.79193 | -0.032043 | 0.10071 | -0.045776 | 0.086975 | -0.064087 | -0.15564 | 0.027466 | 34.2178 | 8.1345 | 117.6865 | 8.1985 | 117.7505 | 0.7782 | 121.6461 | 34.2819 | 121.7606 | 121.3989 | 121.5775 | 121.4127 | 121.5134 | -121.6553 | -121.7331 | 121.6599 | 121.6965 | 102.4887 | 83.9218
1271.5312 | 121.7468 | -121.5042 | 0.17853 | -0.009308 | 6.9746 | 0.067823 | 0.065783 | 0.00056817 | -0.0076093 | -0.0010852 | 0.011658 | 0.0082138 | 0.19789 | 0.069387 | -0.0076947 | 0.12038 | 0.065067 | -18.9331 | -0.013733 | -121.5454 | 0.086975 | -120.7901 | -121.4767 | -121.6141 | -36.5158 | 0.086975 | -121.5958 | 0.050354 | -7.4936 | -3.923 | -111.5616 | -0.041199 | -0.19226 | -0.091553 | 0.71411 | -0.10986 | 0.027465 | -0.068665 | 0.068664 | -0.091553 | -0.091553 | -0.12817 | 114.0106 | 9.9426 | 117.5812 | 10.0342 | 117.6727 | 0.75531 | 121.6324 | 114.1022 | 121.6461 | 121.5317 | 121.6827 | 121.4905 | 121.5912 | -121.7239 | -121.7743 | 121.5912 | 121.5546 | 102.5711 | 84.9884
1273.2656 | 121.7789 | -121.4951 | 0.18768 | 0.01358 | 6.9763 | 0.06825 | 0.063006 | 0.0031318 | -0.0035505 | -0.0010852 | 0.0025025 | 0.0082138 | 0.20388 | 0.067251 | -0.0049175 | 0.12273 | 0.061009 | -18.8965 | -0.036621 | -121.5179 | 0.1236 | -120.7352 | -121.4584 | -121.5912 | -36.2137 | 0.032043 | -121.5729 | 0.10529 | -3.9001 | -3.891 | -111.1267 | -0.022888 | -0.2243 | -0.064087 | 0.75989 | -0.096131 | 0.036621 | -0.073243 | 0.059509 | -0.07782 | -0.15564 | -0.082397 | 117.5949 | 10.3683 | 117.6041 | 10.4462 | 117.6819 | 0.78278 | 121.6415 | 117.6727 | 121.6782 | 121.4813 | 121.6049 | 121.4584 | 121.5271 | -121.7056 | -121.7606 | 121.6187 | 121.6003 | 102.5986 | 85.2814
1275.0156 | 121.8704 | -121.463 | 0.15106 | -0.0016785 | 6.9739 | 0.066541 | 0.060442 | -0.0054132 | -0.0069683 | 0.00019657 | -0.0036011 | 0.0094956 | 0.20836 | 0.076864 | -0.0074811 | 0.12252 | 0.065067 | -18.9102 | -0.082397 | -121.4996 | 0.20599 | -120.6436 | -121.376 | -121.4996 | -36.0123 | 0.013733 | -121.5454 | 0.17395 | -3.3737 | -3.6438 | -110.7971 | -0.036621 | -0.23346 | 0.054932 | 0.8194 | -0.036621 | 0.086975 | 0 | 0.1236 | -0.082397 | -0.13733 | 0.022888 | 118.0893 | 10.6659 | 117.8192 | 10.7483 | 117.9016 | 0.85602 | 121.7056 | 118.1717 | 121.7194 | 121.4172 | 121.5591 | 121.3806 | 121.4767 | -121.6507 | -121.6965 | 121.669 | 121.637 | 102.5528 | 85.4507
1276.7656 | 121.8475 | -121.463 | 0.12817 | -0.009308 | 6.9752 | 0.066755 | 0.064501 | 0.0029182 | -0.0044049 | 0.001051 | -0.00054933 | 0.010991 | 0.20473 | 0.081136 | -0.0021405 | 0.12187 | 0.069767 | -18.9148 | -0.064087 | -121.4996 | 0.16022 | -120.7169 | -121.4493 | -121.5637 | -35.9665 | 0.009155 | -121.5454 | 0.19684 | -3.035 | -3.6163 | -110.5041 | -0.036621 | -0.19226 | 0.032043 | 0.74616 | -0.10071 | 0.013733 | -0.064087 | 0.050354 | -0.082397 | -0.11902 | 0.068664 | 118.428 | 10.9589 | 117.8467 | 11.0413 | 117.9291 | 0.78278 | 121.6599 | 118.5104 | 121.7422 | 121.4355 | 121.5546 | 121.3989 | 121.4722 | -121.6278 | -121.6736 | 121.6232 | 121.6599 | 102.5482 | 85.4965
1278.4375 | 121.6965 | -121.4905 | 0.19684 | 0.005951 | 6.9742 | 0.065687 | 0.064074 | -0.00049983 | -0.0056867 | -0.0027942 | -0.0066527 | 0.014622 | 0.23934 | 0.066823 | -0.0061993 | 0.12316 | 0.070835 | -18.8919 | -0.050354 | -121.5088 | 0.054932 | -120.8038 | -121.5134 | -121.6095 | -36.0489 | 0.036621 | -121.5179 | 0.10529 | -1.8768 | -3.7628 | -110.2249 | -0.01831 | -0.24719 | -0.14191 | 0.68665 | -0.11902 | -0.022888 | -0.10071 | -0.004578 | -0.027465 | -0.16022 | -0.091552 | 119.6136 | 11.2656 | 117.7277 | 11.293 | 117.7551 | 0.70496 | 121.5637 | 119.6411 | 121.6232 | 121.4584 | 121.5546 | 121.4401 | 121.5271 | -121.7056 | -121.7148 | 121.5454 | 121.5958 | 102.5986 | 85.4416
1280.1719 | 121.5591 | -121.3074 | 0.11444 | -0.024567 | 6.9763 | 0.065046 | 0.063647 | -0.0024224 | -0.0091047 | -0.0027942 | -0.0036011 | 0.0022324 | 0.017169 | -0.007731 | -0.010045 | 0.024676 | -0.0056418 | -18.7775 | -0.13275 | -121.3943 | 0.004578 | -120.6711 | -121.3348 | -121.4676 | -0.18768 | 0 | -0.041199 | 0.027466 | -0.013733 | -0.032043 | 0.064087 | -0.086975 | -0.24719 | -0.10986 | 0.63629 | -0.16022 | -0.027466 | -0.073242 | 0.059509 | 121.2662 | -0.11444 | -0.086975 | 121.2936 | 121.3715 | 121.2753 | 0.10529 | 0.009156 | 0.72327 | 121.3989 | 0.027466 | 0.068665 | 121.2616 | 0.041199 | 121.1746 | 121.3074 | -121.5088 | -0.15564 | 121.312 | 121.3348 | 102.5299 | 121.1197
1281.9062 | 121.6873 | -121.5317 | 0.11444 | -0.0016785 | 6.9752 | 0.066755 | 0.063647 | 0.00078177 | -0.0069683 | -0.001726 | 0.0025025 | 0.0018052 | 0.017596 | -0.018839 | -0.0091901 | 0.022967 | -0.0022238 | -18.9011 | -0.11444 | -121.55 | 0.013733 | -120.8084 | -121.5042 | -121.6415 | -0.16022 | 0.009155 | -0.068665 | 0 | -0.054932 | -0.07782 | 0.013733 | -0.018311 | -0.22888 | -0.10071 | 0.72327 | -0.10986 | 0.027466 | -0.091553 | 0.045777 | 121.463 | -0.10529 | -0.11444 | 121.4767 | 121.5454 | 121.4539 | 0.082398 | -0.009155 | 0.74158 | 121.5637 | 0.013733 | 0.068665 | 121.4355 | 0.07782 | 121.4172 | 121.5408 | -121.6644 | -0.18311 | 121.5454 | 121.5317 | 102.6306 | 121.3715
1283.5781 | 121.7239 | -121.55 | 0.13733 | -0.009308 | 6.9744 | 0.064832 | 0.061938 | -0.00049983 | -0.0044049 | -0.0019396 | -0.0036011 | 0.0030868 | 0.018023 | -0.015421 | -0.0087629 | 0.020403 | -0.00072839 | -18.9102 | -0.12817 | -121.5454 | -0.004578 | -120.8496 | -121.5546 | -121.6644 | -0.19226 | 0.009155 | -0.082397 | 0.018311 | -0.041199 | -0.07782 | 0.032043 | 0.004578 | -0.2655 | -0.14191 | 0.70038 | -0.11444 | -0.004577 | -0.11902 | -0.009155 | 121.4676 | -0.12817 | -0.11902 | 121.5088 | 121.582 | 121.4722 | 0.11444 | 0.004577 | 0.6958 | 121.5408 | 0.041198 | 0.10071 | 121.4172 | 0.091552 | 121.4218 | 121.5591 | -121.6827 | -0.21973 | 121.5454 | 121.5683 | 102.6398 | 121.3577
1285.3125 | 121.7285 | -121.5729 | 0.11902 | -0.0016785 | 6.9756 | 0.068891 | 0.064501 | 0.0029182 | -0.0063275 | -0.00065803 | -0.00054933 | 0.0013778 | 0.016101 | -0.0021768 | -0.0059857 | 0.023607 | -0.00436 | -18.9423 | -0.11444 | -121.5546 | -0.004578 | -120.8817 | -121.6003 | -121.7056 | -0.19226 | 0.013733 | -0.059509 | 0.013733 | -0.050354 | -0.10986 | 0.041199 | 0.018311 | -0.23346 | -0.1236 | 0.69122 | -0.13275 | -0.027466 | -0.15106 | -0.045777 | 121.5134 | -0.10529 | -0.10529 | 121.5225 | 121.6141 | 121.463 | 0.10071 | -0.050354 | 0.67291 | 121.55 | 0.009155 | 0.073242 | 121.4401 | 0.073242 | 121.4584 | 121.5866 | -121.6736 | -0.17853 | 121.5683 | 121.5866 | 102.6306 | 121.3806
1287.0469 | 121.8796 | -121.5317 | 0.086975 | 0.005951 | 6.9739 | 0.06526 | 0.059588 | -0.00092703 | -0.0076093 | -0.0038622 | -0.0036011 | 0.0015914 | 0.017383 | -0.0023904 | -0.0040631 | 0.022967 | -0.0052146 | -18.9056 | -0.14191 | -121.5591 | 0.10529 | -120.7764 | -121.4767 | -121.6003 | -0.059509 | -0.036621 | -0.041199 | 0.10986 | 0.10071 | 0.064087 | 0.14191 | -0.027466 | -0.22888 | 0.018311 | 0.75531 | -0.068665 | 0.054931 | -0.041199 | 0.082397 | 121.4905 | -0.1236 | 0.022888 | 121.6324 | 121.6736 | 121.5958 | 0.18311 | 0.10529 | 0.78278 | 121.6644 | 0.14191 | 0.15106 | 121.4172 | 0.004578 | 121.3898 | 121.4951 | -121.6461 | -0.12817 | 121.637 | 121.6415 | 102.626 | 121.4722
1288.7969 | 121.8246 | -121.5775 | 0.091553 | -0.009308 | 6.9744 | 0.064832 | 0.061938 | -7.2628e-05 | -0.0050457 | -0.0025806 | 0.0025025 | 0.0009506 | 0.01546 | -0.0081582 | -0.0076947 | 0.025103 | -0.0028646 | -18.9102 | -0.15564 | -121.5454 | 0.13275 | -120.7443 | -121.4584 | -121.5912 | -0.059509 | -0.027466 | -0.036621 | 0.082397 | 0.07782 | 0.036621 | 0.10986 | 0.032044 | -0.24719 | 0.041198 | 0.83313 | -0.013733 | 0.11902 | -0.045777 | 0.086975 | 121.5408 | -0.11902 | -0.009156 | 121.6553 | 121.6873 | 121.6141 | 0.14648 | 0.073242 | 0.80109 | 121.6782 | 0.11444 | 0.11902 | 121.3898 | 0.009155 | 121.4218 | 121.55 | -121.637 | -0.12817 | 121.7102 | 121.6599 | 102.6672 | 121.5179
1290.4688 | 121.8018 | -121.5775 | 0.10529 | -0.016937 | 6.9739 | 0.065687 | 0.065783 | -0.0017816 | -0.0086773 | -0.001726 | -0.015808 | 0.0030868 | 0.015887 | -0.010508 | -0.0074811 | 0.023394 | -0.00030119 | -18.9514 | -0.11444 | -121.5866 | 0.018311 | -120.8725 | -121.5683 | -121.6827 | -0.17395 | -0.004578 | -0.050354 | 0.036621 | 0.022888 | -0.027466 | 0.082397 | -0.009155 | -0.21973 | -0.086975 | 0.70496 | -0.10528 | 0.009156 | -0.09613 | 0.018311 | 121.5271 | -0.10986 | -0.068665 | 121.6003 | 121.6599 | 121.55 | 0.13275 | 0.022888 | 0.71411 | 121.6049 | 0.073242 | 0.086975 | 121.4722 | 0.045776 | 121.463 | 121.5729 | -121.6919 | -0.15564 | 121.5958 | 121.6141 | 102.626 | 121.4035
1292.2031 | 121.8201 | -121.5866 | 0.10529 | -0.009308 | 6.9761 | 0.066541 | 0.063433 | -0.003277 | -0.0069683 | 0.001051 | -0.00054933 | 0.0028732 | 0.016314 | -0.0098672 | -0.0040631 | 0.024248 | -0.00072839 | -18.9056 | -0.10986 | -121.5912 | 0.059509 | -120.8221 | -121.5546 | -121.6782 | -0.086975 | 0.004578 | -0.027466 | 0.068665 | 0.045776 | 0.004578 | 0.091553 | -0.004578 | -0.21515 | -0.045777 | 0.76447 | -0.091553 | 0.032044 | -0.086975 | 0.036622 | 121.5591 | -0.10071 | -0.036621 | 121.6324 | 121.6782 | 121.5912 | 0.11902 | 0.032044 | 0.76904 | 121.6507 | 0.073242 | 0.096131 | 121.4813 | 0.032044 | 121.4767 | 121.5912 | -121.6965 | -0.13275 | 121.6461 | 121.6553 | 102.681 | 121.4996
1293.9375 | 121.9116 | -121.5637 | 0.09613 | -0.0016785 | 6.9767 | 0.069319 | 0.063647 | -0.00028623 | -0.0048321 | -0.0010852 | -0.00054933 | 0.002446 | 0.016528 | -0.0021768 | -0.0038495 | 0.024035 | 0.00076681 | -18.9285 | -0.17395 | -121.5454 | 0.13275 | -120.7626 | -121.4951 | -121.6461 | -0.004578 | -0.045776 | -0.009155 | 0.13733 | 0.10071 | 0.082397 | 0.15564 | 0.018311 | -0.27008 | 0.036621 | 0.80109 | -0.082397 | 0.068665 | -0.10071 | 0.050354 | 121.5546 | -0.14191 | 0.041199 | 121.6644 | 121.7194 | 121.6461 | 0.16479 | 0.091552 | 0.78278 | 121.6782 | 0.10986 | 0.14648 | 121.3715 | -0.036621 | 121.3898 | 121.5179 | -121.6415 | -0.10528 | 121.6965 | 121.701 | 102.6352 | 121.5591
1295.6875 | 121.8842 | -121.5866 | 0.09613 | -0.0016785 | 6.9748 | 0.06761 | 0.064715 | 0.0056952 | -0.0050457 | -0.0025806 | -0.0036011 | 0.0018052 | 0.014819 | -0.0028178 | -0.0064129 | 0.025103 | -0.0047874 | -18.9743 | -0.11444 | -121.6095 | 0.045776 | -120.8817 | -121.6141 | -121.7239 | -0.082397 | -0.022888 | -0.018311 | 0.091553 | 0.054932 | 0.018311 | 0.15106 | -0.022888 | -0.21057 | -0.050354 | 0.70496 | -0.13733 | -0.027466 | -0.11444 | -0.004578 | 121.5683 | -0.11902 | -0.004577 | 121.6415 | 121.7377 | 121.6049 | 0.16937 | 0.036622 | 0.72784 | 121.6553 | 0.073243 | 0.10986 | 121.4951 | -0.004577 | 121.4722 | 121.5637 | -121.7056 | -0.11444 | 121.6324 | 121.6782 | 102.6123 | 121.5042
1297.375 | 121.9116 | -121.582 | 0.082397 | -0.009308 | 6.9746 | 0.066969 | 0.06322 | -0.004986 | -0.0065411 | -0.0021532 | -0.00054933 | 0.0020188 | 0.015246 | -0.00068137 | -0.0066265 | 0.025957 | -0.0011558 | -18.9743 | -0.16022 | -121.6187 | 0.086975 | -120.8313 | -121.5225 | -121.6507 | -0.054932 | -0.041199 | -0.013733 | 0.10529 | 0.10986 | 0.068665 | 0.15106 | -0.036621 | -0.24261 | 0.004578 | 0.75073 | -0.068665 | 0.059509 | -0.032044 | 0.09613 | 121.5683 | -0.1236 | 0.022889 | 121.6919 | 121.7331 | 121.6507 | 0.16479 | 0.082398 | 0.78735 | 121.7056 | 0.1236 | 0.11902 | 121.4584 | -0.027466 | 121.4218 | 121.5408 | -121.701 | -0.09613 | 121.669 | 121.6873 | 102.6077 | 121.5271
1299.125 | 121.9116 | -121.5866 | 0.082397 | -0.0016785 | 6.9759 | 0.068678 | 0.063433 | -0.00028623 | -0.0071821 | -0.0021532 | -0.0036011 | 0.0039414 | 0.014819 | -0.013926 | -0.0049175 | 0.024248 | -0.0047874 | -18.869 | -0.16022 | -121.6095 | 0.14191 | -120.7855 | -121.5317 | -121.6553 | 0.009155 | -0.022888 | 0.013733 | 0.15564 | 0.11902 | 0.086975 | 0.17395 | -0.022888 | -0.24261 | 0.05951 | 0.80109 | -0.068664 | 0.054932 | -0.045776 | 0.07782 | 121.6003 | -0.10528 | 0.073243 | 121.7056 | 121.7606 | 121.6736 | 0.16022 | 0.073242 | 0.82398 | 121.7514 | 0.10529 | 0.14191 | 121.4493 | -0.036621 | 121.4264 | 121.5637 | -121.6919 | -0.068664 | 121.7285 | 121.7422 | 102.7176 | 121.5958
1300.875 | 121.8704 | -121.6003 | 0.082397 | -0.032196 | 6.9742 | 0.066541 | 0.062365 | 0.0031318 | -0.0067547 | -0.002367 | -0.0097045 | 0.0037278 | 0.014605 | -0.0028178 | -0.0072675 | 0.023607 | -0.0039328 | -18.9194 | -0.16937 | -121.6141 | 0.11902 | -120.7901 | -121.5408 | -121.669 | 0.009155 | -0.045776 | 0.022888 | 0.11444 | 0.082397 | 0.054932 | 0.14191 | -0.013733 | -0.25177 | 0.036622 | 0.81024 | -0.068664 | 0.059509 | -0.054931 | 0.073242 | 121.6232 | -0.12817 | 0.032044 | 121.6827 | 121.7422 | 121.6553 | 0.11902 | 0.032044 | 0.82398 | 121.7331 | 0.059509 | 0.091553 | 121.4447 | -0.068664 | 121.431 | 121.5546 | -121.6965 | -0.059509 | 121.7194 | 121.7148 | 102.681 | 121.6095
1302.5625 | 121.9162 | -121.5958 | 0.091553 | -0.0016785 | 6.9752 | 0.066328 | 0.06087 | 0.0037726 | -0.0069683 | -0.00087163 | -0.0066527 | 0.0030868 | 0.015674 | -0.010081 | -0.0096173 | 0.024676 | -0.0041464 | -18.8507 | -0.16937 | -121.6415 | 0.13733 | -120.7718 | -121.5042 | -121.6324 | 0.009155 | -0.032043 | 0.009155 | 0.11444 | 0.1236 | 0.091553 | 0.16937 | -0.045777 | -0.26093 | 0.045776 | 0.82397 | -0.036621 | 0.091553 | 0.009156 | 0.13733 | 121.6049 | -0.1236 | 0.022888 | 121.7194 | 121.7651 | 121.6873 | 0.16022 | 0.082398 | 0.86975 | 121.7789 | 0.11444 | 0.10529 | 121.4722 | -0.041198 | 121.4264 | 121.5637 | -121.7331 | -0.082398 | 121.7331 | 121.7102 | 102.7451 | 121.6049
1304.2969 | 121.8246 | -121.6187 | 0.10071 | -0.0016785 | 6.9767 | 0.066755 | 0.066851 | 0.00078177 | -0.0054731 | -0.0027942 | -0.0036011 | 0.0022324 | 0.016742 | -0.006022 | -0.0059857 | 0.026812 | -0.0013694 | -18.9102 | -0.11444 | -121.6736 | 0.004578 | -120.9457 | -121.6599 | -121.788 | -0.12817 | 0.013733 | -0.041199 | 0.013733 | -0.032043 | -0.050354 | 0.07782 | -0.054932 | -0.21515 | -0.09613 | 0.67291 | -0.16937 | -0.041199 | -0.11444 | 0.013733 | 121.5775 | -0.086975 | -0.086975 | 121.5866 | 121.6965 | 121.5683 | 0.11902 | -0.009155 | 0.72784 | 121.6782 | 0.009156 | 0.054932 | 121.5591 | 0.054932 | 121.5042 | 121.6324 | -121.7743 | -0.14191 | 121.6232 | 121.6324 | 102.7084 | 121.4905
1305.9688 | 121.8979 | -121.6187 | 0.10986 | -0.009308 | 6.9733 | 0.065046 | 0.063006 | 0.00099557 | -0.0063275 | -0.00065803 | -0.00054933 | 0.0011642 | 0.016314 | -0.0070902 | -0.0068403 | 0.024248 | -0.0030784 | -18.7683 | -0.15106 | -121.6415 | 0.13733 | -120.7993 | -121.4905 | -121.6461 | -0.004578 | -0.027466 | 0.004578 | 0.09613 | 0.09613 | 0.082397 | 0.14191 | -0.022889 | -0.26093 | 0.027466 | 0.8194 | -0.027466 | 0.12817 | -0.004577 | 0.15106 | 121.6232 | -0.13733 | -0.013733 | 121.7148 | 121.7606 | 121.701 | 0.13733 | 0.077819 | 0.84229 | 121.7789 | 0.091552 | 0.091552 | 121.4905 | -0.032044 | 121.4676 | 121.5912 | -121.7514 | -0.10529 | 121.756 | 121.7148 | 102.8503 | 121.6141
1307.6562 | 121.8155 | -121.6644 | 0.11902 | -0.0016785 | 6.9765 | 0.069319 | 0.065783 | 0.0039862 | -0.0054731 | -0.002367 | -0.0036011 | 0.003514 | 0.015887 | -0.010508 | -0.0070539 | 0.02553 | -0.0020102 | -18.8324 | -0.11902 | -121.6415 | 0.041199 | -120.9183 | -121.6553 | -121.7697 | -0.10071 | 0.009155 | -0.013733 | 0.013733 | -0.022888 | -0.054932 | 0.064087 | 0.022888 | -0.23804 | -0.07782 | 0.74616 | -0.10528 | 0.009156 | -0.12817 | -0.013732 | 121.6507 | -0.10986 | -0.10529 | 121.6415 | 121.7285 | 121.6095 | 0.07782 | -0.041199 | 0.72327 | 121.6827 | -0.009155 | 0.027466 | 121.5225 | 0.022888 | 121.5454 | 121.6736 | -121.7606 | -0.13275 | 121.7056 | 121.6782 | 102.832 | 121.5637
1309.3906 | 121.9208 | -121.6187 | 0.091553 | -0.009308 | 6.9767 | 0.067823 | 0.062792 | 0.0044134 | -0.0054731 | -0.00044443 | -0.0066527 | 0.0015914 | 0.016314 | -0.0085856 | -0.0085491 | 0.023821 | 0.00055321 | -18.8187 | -0.14648 | -121.6461 | 0.14191 | -120.7993 | -121.5225 | -121.6644 | 0.009155 | -0.045776 | 0.009155 | 0.10529 | 0.1236 | 0.086975 | 0.14648 | -0.027466 | -0.23804 | 0.050354 | 0.8194 | -0.045777 | 0.09613 | -0.018311 | 0.1236 | 121.6278 | -0.13733 | 0.013733 | 121.7422 | 121.7651 | 121.7056 | 0.13733 | 0.07782 | 0.84686 | 121.788 | 0.11444 | 0.096131 | 121.4996 | -0.054931 | 121.4722 | 121.5729 | -121.7377 | -0.082398 | 121.7606 | 121.7239 | 102.8 | 121.6278
1311.125 | 121.843 | -121.6553 | 0.11902 | -0.024567 | 6.9748 | 0.065687 | 0.061297 | -7.2628e-05 | -0.0073957 | 0.001692 | -0.0036011 | 0.002446 | 0.012256 | -0.014994 | -0.0089765 | 0.021685 | -0.003292 | -18.9056 | -0.1236 | -121.6415 | -0.004578 | -120.9595 | -121.637 | -121.7606 | -0.13733 | -0.009155 | -0.009155 | 0.018311 | 0.018311 | -0.022888 | 0.07782 | 0.013732 | -0.24261 | -0.1236 | 0.6958 | -0.10529 | 0.01831 | -0.11902 | 0.004578 | 121.6461 | -0.12817 | -0.10071 | 121.6736 | 121.7331 | 121.6324 | 0.086975 | -0.013733 | 0.68207 | 121.637 | 0.027466 | 0.027466 | 121.5179 | 0 | 121.5317 | 121.6461 | -121.7606 | -0.12817 | 121.6507 | 121.6736 | 102.7496 | 121.5179
1312.8594 | 121.8201 | -121.6461 | 0.10986 | -0.009308 | 6.9744 | 0.066969 | 0.061724 | -0.0022088 | -0.0052595 | -0.0021532 | -0.00054933 | 0.0011642 | 0.016742 | -0.0068766 | -0.0072675 | 0.024035 | -0.00030119 | -18.8324 | -0.13275 | -121.6507 | 0.059509 | -120.9 | -121.5912 | -121.7102 | -0.10071 | -0.004578 | -0.022888 | 0.013733 | 0 | -0.045776 | 0.050354 | -0.004578 | -0.24261 | -0.050354 | 0.74616 | -0.064087 | 0.054931 | -0.059509 | 0.059509 | 121.6232 | -0.11444 | -0.09613 | 121.6461 | 121.6965 | 121.6003 | 0.073242 | -0.022888 | 0.75073 | 121.7102 | 0.022888 | 0.036621 | 121.5179 | 0.01831 | 121.5134 | 121.6415 | -121.7606 | -0.13275 | 121.7056 | 121.6599 | 102.8137 | 121.5454
1314.5938 | 121.8613 | -121.669 | 0.11902 | -0.009308 | 6.975 | 0.067182 | 0.062579 | 0.0014228 | -0.0099591 | -0.0010852 | -0.0036011 | 0.0011642 | 0.015033 | -0.011363 | -0.0076947 | 0.02083 | -0.00436 | -18.8919 | -0.11444 | -121.669 | 0.009155 | -120.9641 | -121.6415 | -121.7651 | -0.14648 | -0.013733 | -0.004578 | 0.018311 | 0.009155 | -0.013733 | 0.10986 | 0 | -0.23346 | -0.10986 | 0.70496 | -0.096131 | 0.027465 | -0.096131 | 0.027465 | 121.6644 | -0.13275 | -0.10071 | 121.6782 | 121.7789 | 121.6553 | 0.11444 | -0.009155 | 0.70496 | 121.6782 | 0.013733 | 0.022889 | 121.5546 | -0.009155 | 121.5546 | 121.6553 | -121.788 | -0.1236 | 121.6782 | 121.6873 | 102.7771 | 121.5225
1316.3281 | 121.8384 | -121.6736 | 0.09613 | -0.0016785 | 6.978 | 0.06825 | 0.064288 | -0.0022088 | -0.0063275 | -0.0032214 | -0.0036011 | 0.0030868 | 0.018237 | -0.0011088 | -0.0042767 | 0.023394 | -0.0011558 | -18.9102 | -0.11902 | -121.669 | 0 | -120.9641 | -121.669 | -121.7972 | -0.13275 | 0.009155 | -0.018311 | 0.027466 | -0.013733 | -0.036621 | 0.068665 | 0.004578 | -0.21515 | -0.09613 | 0.70953 | -0.1236 | 0.004578 | -0.12817 | 0 | 121.6553 | -0.086975 | -0.068664 | 121.6599 | 121.7422 | 121.637 | 0.086976 | -0.01831 | 0.70496 | 121.669 | 0.004578 | 0.045777 | 121.55 | 0.027466 | 121.5546 | 121.6827 | -121.7651 | -0.11444 | 121.6736 | 121.7011 | 102.7634 | 121.5408
1318 | 121.9437 | -121.6324 | 0.07782 | -0.016937 | 6.9733 | 0.066969 | 0.061511 | 0.0031318 | -0.0056867 | -0.0030078 | -0.0097045 | 0.000737 | 0.01781 | -0.0040994 | -0.0021405 | 0.02553 | -0.0035056 | -18.8919 | -0.16937 | -121.6095 | 0.13275 | -120.8176 | -121.5729 | -121.6827 | 0.027466 | -0.041199 | 0.027466 | 0.13733 | 0.11444 | 0.07782 | 0.16022 | 0.022888 | -0.24719 | 0.054931 | 0.81482 | -0.050354 | 0.059509 | -0.073242 | 0.036621 | 121.6599 | -0.11902 | 0.059509 | 121.7468 | 121.7926 | 121.7102 | 0.13275 | 0.050354 | 0.79193 | 121.7422 | 0.086975 | 0.10986 | 121.4401 | -0.068665 | 121.463 | 121.5912 | -121.6873 | -0.050354 | 121.7651 | 121.7697 | 102.7405 | 121.6599
1319.75 | 121.9803 | -121.6324 | 0.082397 | -0.0016785 | 6.9739 | 0.066114 | 0.061724 | 0.0020636 | -0.0067547 | -0.0015124 | -0.00054933 | 9.6204e-05 | 0.016314 | -0.006022 | -0.0083355 | 0.022967 | -0.0039328 | -18.8599 | -0.16022 | -121.6415 | 0.14648 | -120.7901 | -121.5179 | -121.6553 | 0.045776 | -0.036621 | -0.009155 | 0.1236 | 0.13275 | 0.11444 | 0.16479 | -0.009156 | -0.24261 | 0.064087 | 0.84229 | -0.022888 | 0.11444 | -0.013732 | 0.1236 | 121.6232 | -0.11902 | 0.041199 | 121.7651 | 121.7972 | 121.7468 | 0.17395 | 0.1236 | 0.85144 | 121.788 | 0.14191 | 0.13275 | 121.4813 | -0.027466 | 121.4722 | 121.5958 | -121.7239 | -0.091552 | 121.7789 | 121.756 | 102.7725 | 121.6782
1321.5 | 121.8475 | -121.6599 | 0.10986 | -0.009308 | 6.9759 | 0.06526 | 0.061511 | 0.00099557 | -0.0041913 | -0.0021532 | 0.0025025 | 0.0018052 | 0.015674 | -0.004954 | -0.0068403 | 0.021471 | 0.00012601 | -18.837 | -0.14191 | -121.669 | 0.082397 | -120.8725 | -121.5683 | -121.7194 | -0.054932 | -0.009155 | -0.013733 | 0.013733 | 0.032043 | -0.009155 | 0.059509 | -0.009155 | -0.25177 | -0.027466 | 0.78735 | -0.059509 | 0.091553 | -0.050354 | 0.10071 | 121.6461 | -0.11902 | -0.09613 | 121.6919 | 121.7194 | 121.6507 | 0.073242 | 0.004578 | 0.79651 | 121.7514 | 0.045776 | 0.027466 | 121.5271 | 0.004578 | 121.5179 | 121.6507 | -121.7789 | -0.1236 | 121.7422 | 121.6736 | 102.8229 | 121.6049
1323.1875 | 121.9757 | -121.6278 | 0.09613 | -0.0016785 | 6.9733 | 0.068464 | 0.062579 | 0.00078177 | -0.0056867 | -0.00087163 | -0.0036011 | 0.0015914 | 0.014819 | -0.004954 | -0.0053449 | 0.022753 | -0.0039328 | -18.8416 | -0.14648 | -121.6461 | 0.10986 | -120.8359 | -121.5454 | -121.6782 | -0.009155 | -0.036621 | 0.009155 | 0.12817 | 0.11902 | 0.10071 | 0.16937 | -0.01831 | -0.24261 | 0.013733 | 0.79193 | -0.050354 | 0.082398 | -0.032044 | 0.10071 | 121.637 | -0.13275 | 0.032044 | 121.7468 | 121.7972 | 121.7285 | 0.16022 | 0.091553 | 0.81024 | 121.756 | 0.10986 | 0.11902 | 121.4996 | -0.045776 | 121.4813 | 121.5912 | -121.7422 | -0.086975 | 121.7377 | 121.756 | 102.7863 | 121.6187
1324.9375 | 121.9162 | -121.6507 | 0.091553 | -0.009308 | 6.9761 | 0.065046 | 0.062579 | 0.00056817 | -0.0054731 | 0.0012646 | -0.0036011 | 9.6204e-05 | 0.016742 | -0.016917 | -0.0076947 | 0.024035 | -0.001583 | -18.7729 | -0.15564 | -121.6553 | 0.14648 | -120.8313 | -121.5408 | -121.669 | 0.018311 | -0.018311 | 0.004578 | 0.091553 | 0.086975 | 0.064087 | 0.14191 | -0.004577 | -0.24719 | 0.054931 | 0.8194 | -0.01831 | 0.10986 | -0.013733 | 0.11444 | 121.6553 | -0.10986 | 0 | 121.7377 | 121.7926 | 121.7148 | 0.13733 | 0.059509 | 0.82397 | 121.8018 | 0.082397 | 0.086975 | 121.4996 | -0.022889 | 121.4951 | 121.6324 | -121.7468 | -0.086975 | 121.7972 | 121.7422 | 102.8778 | 121.669
1326.6875 | 121.8384 | -121.6965 | 0.1236 | -0.009308 | 6.9776 | 0.070387 | 0.064715 | 0.0016364 | -0.0048321 | -0.0036486 | -0.0066527 | 0.0030868 | 0.016528 | -0.012217 | -0.0055585 | 0.023607 | -0.0035056 | -18.8232 | -0.10986 | -121.6827 | 0.009155 | -121.0144 | -121.701 | -121.8338 | -0.16937 | 0.009155 | -0.032043 | 0.009155 | -0.041199 | -0.07782 | 0.054932 | 0.013733 | -0.23346 | -0.11444 | 0.68207 | -0.13733 | -0.004578 | -0.15106 | -0.018311 | 121.6644 | -0.11444 | -0.11444 | 121.6553 | 121.7514 | 121.6187 | 0.086975 | -0.045777 | 0.66833 | 121.6919 | -0.009156 | 0.041198 | 121.5729 | 0.041198 | 121.5866 | 121.7056 | -121.8063 | -0.15564 | 121.7056 | 121.7056 | 102.8732 | 121.5271
1328.3594 | 121.8613 | -121.6827 | 0.11902 | -0.009308 | 6.9756 | 0.067396 | 0.063647 | 0.0044134 | -0.0041913 | -0.00065803 | -0.0036011 | 0.0022324 | 0.01781 | -0.0051676 | -0.0047039 | 0.025744 | -0.0058554 | -18.8461 | -0.10071 | -121.6919 | -0.004578 | -120.9915 | -121.6919 | -121.7972 | -0.1236 | -0.004578 | -0.022888 | 0.018311 | -0.032043 | -0.054932 | 0.073242 | -0.009156 | -0.21973 | -0.1236 | 0.69122 | -0.11444 | -0.009156 | -0.10528 | 0 | 121.6599 | -0.1236 | -0.10071 | 121.6507 | 121.756 | 121.6278 | 0.09613 | -0.032044 | 0.70038 | 121.6873 | -0.009155 | 0.041199 | 121.5912 | 0.01831 | 121.582 | 121.6782 | -121.8109 | -0.14191 | 121.6782 | 121.701 | 102.8366 | 121.5591
1330.0938 | 121.8796 | -121.6827 | 0.13275 | 0.01358 | 6.9752 | 0.066969 | 0.062365 | 0.0020636 | -0.0067547 | -0.0025806 | -0.0066527 | -0.0001174 | 0.015674 | -0.006663 | -0.0085491 | 0.022326 | -0.003292 | -18.7454 | -0.14191 | -121.6782 | 0.073242 | -120.8862 | -121.5958 | -121.7377 | -0.07782 | -0.009155 | -0.018311 | 0.013733 | 0.013733 | -0.027466 | 0.068665 | 0.004577 | -0.27466 | -0.059509 | 0.79651 | -0.054932 | 0.086975 | -0.059509 | 0.082398 | 121.6644 | -0.14191 | -0.11902 | 121.6965 | 121.7514 | 121.6553 | 0.086976 | -0.009155 | 0.79193 | 121.7514 | 0.032044 | 0.032044 | 121.5363 | 0.009156 | 121.5408 | 121.6736 | -121.8109 | -0.15106 | 121.756 | 121.6965 | 102.9373 | 121.6049
1331.7812 | 121.8567 | -121.7056 | 0.10986 | 0.005951 | 6.9782 | 0.067823 | 0.064929 | -0.0019952 | -0.0048321 | -0.0032214 | -0.00054933 | 0.002446 | 0.017169 | -0.0085856 | -0.0032087 | 0.023821 | -0.0030784 | -18.8278 | -0.09613 | -121.7102 | 0 | -120.9961 | -121.7056 | -121.8201 | -0.13733 | -0.004578 | -0.004578 | 0.004578 | -0.018311 | -0.07782 | 0.064087 | -0.004578 | -0.20599 | -0.10986 | 0.70953 | -0.11444 | 0 | -0.10986 | 0.004578 | 121.701 | -0.11444 | -0.10529 | 121.6873 | 121.7697 | 121.6278 | 0.068665 | -0.073242 | 0.71411 | 121.7102 | -0.013733 | 0.009156 | 121.6141 | 0 | 121.6095 | 121.701 | -121.8201 | -0.11444 | 121.7056 | 121.7102 | 102.8778 | 121.5683
1333.5156 | 121.8384 | -121.701 | 0.10071 | 0.01358 | 6.9774 | 0.068678 | 0.064074 | 0.0027044 | -0.0050457 | -0.003435 | 0.0025025 | 0.003514 | 0.017169 | -0.007731 | -0.0064129 | 0.023394 | -0.0037192 | -18.7363 | -0.10986 | -121.6782 | 0.050354 | -120.9595 | -121.6644 | -121.7972 | -0.10071 | -0.013733 | -0.013733 | 0.018311 | -0.027466 | -0.059509 | 0.059509 | 0.022888 | -0.21057 | -0.050354 | 0.74158 | -0.09613 | 0.036621 | -0.11902 | 0.013733 | 121.6873 | -0.11444 | -0.082397 | 121.6736 | 121.7606 | 121.6415 | 0.073242 | -0.045776 | 0.71869 | 121.7285 | -0.013733 | 0.032044 | 121.5683 | 0 | 121.5912 | 121.6873 | -121.7789 | -0.11444 | 121.7514 | 121.7194 | 102.9648 | 121.6003
1335.25 | 121.8246 | -121.6736 | 0.11902 | 0.005951 | 6.9759 | 0.066969 | 0.06322 | 0.0014228 | -0.0041913 | -0.002367 | -0.0066527 | 0.002446 | 0.016528 | -0.01713 | -0.0091901 | 0.024889 | -0.0082052 | -18.8095 | -0.10529 | -121.6736 | -0.013733 | -121.0007 | -121.7056 | -121.8292 | -0.17395 | 0 | -0.032043 | 0.013733 | -0.032043 | -0.073242 | 0.054932 | 0 | -0.22431 | -0.13275 | 0.67291 | -0.15564 | -0.032043 | -0.15564 | -0.032043 | 121.6415 | -0.11902 | -0.10529 | 121.6415 | 121.7285 | 121.6003 | 0.086975 | -0.041199 | 0.67291 | 121.6599 | 0 | 0.045776 | 121.5683 | 0.032043 | 121.5683 | 121.6736 | -121.7926 | -0.15106 | 121.6599 | 121.6873 | 102.8641 | 121.4996
1336.9375 | 121.962 | -121.6553 | 0.068665 | -0.009308 | 6.9735 | 0.066541 | 0.062151 | 0.0014228 | -0.0071821 | -0.00065803 | 0.0025025 | 0.000737 | 0.016528 | -0.003245 | -0.0070539 | 0.024889 | 0.0026896 | -18.7363 | -0.13275 | -121.6736 | 0.09613 | -120.8908 | -121.5958 | -121.7239 | -0.032043 | -0.036621 | -0.004578 | 0.10529 | 0.10071 | 0.068665 | 0.15106 | -0.018311 | -0.20142 | 0.027465 | 0.76446 | -0.068665 | 0.059509 | -0.050354 | 0.07782 | 121.6507 | -0.10529 | 0.036621 | 121.756 | 121.8063 | 121.7239 | 0.15564 | 0.073243 | 0.78278 | 121.7697 | 0.10529 | 0.10986 | 121.5408 | -0.032043 | 121.5225 | 121.6187 | -121.7422 | -0.073243 | 121.7514 | 121.7606 | 102.919 | 121.6232
1338.6719 | 121.8613 | -121.6782 | 0.11444 | -0.0016785 | 6.9767 | 0.066328 | 0.064501 | 0.00056817 | -0.0054731 | -0.0019396 | -0.0036011 | 0.0015914 | 0.016314 | -0.01179 | -0.0057721 | 0.024462 | -0.00051479 | -18.7912 | -0.11444 | -121.6965 | -0.009155 | -120.9961 | -121.7102 | -121.8246 | -0.12817 | 0.009155 | -0.027466 | 0.027466 | -0.018311 | -0.050354 | 0.07782 | -0.01831 | -0.22888 | -0.1236 | 0.68207 | -0.14648 | -0.032043 | -0.12817 | -0.013733 | 121.6507 | -0.10529 | -0.086975 | 121.6599 | 121.756 | 121.6278 | 0.10529 | -0.022888 | 0.70038 | 121.6873 | 0.009155 | 0.054932 | 121.582 | 0.036621 | 121.5637 | 121.6873 | -121.8109 | -0.14191 | 121.669 | 121.7056 | 102.887 | 121.55
1340.4062 | 121.9574 | -121.6324 | 0.086975 | -0.016937 | 6.9774 | 0.067823 | 0.061511 | 0.00078177 | -0.0076093 | -0.0012988 | -0.0097045 | -0.0001174 | 0.014605 | -0.0070902 | -0.0038495 | 0.025744 | -0.010769 | -18.7363 | -0.16479 | -121.6415 | 0.11902 | -120.845 | -121.5912 | -121.7194 | 0.027466 | -0.054932 | 0.018311 | 0.1236 | 0.10071 | 0.064087 | 0.15564 | -0.009156 | -0.25177 | 0.032044 | 0.78735 | -0.086975 | 0.041198 | -0.077819 | 0.050354 | 121.6507 | -0.14191 | 0.036621 | 121.7331 | 121.788 | 121.6965 | 0.13733 | 0.045776 | 0.79651 | 121.7606 | 0.082397 | 0.10528 | 121.4767 | -0.073243 | 121.4676 | 121.5775 | -121.7285 | -0.068664 | 121.7514 | 121.756 | 102.8961 | 121.6599
1342.0781 | 121.8521 | -121.6827 | 0.1236 | -0.009308 | 6.9759 | 0.068037 | 0.063433 | -0.0037042 | -0.0097455 | -0.0021532 | -0.0036011 | 0.0020188 | 0.016742 | -0.012217 | -0.010472 | 0.024889 | -0.0017966 | -18.75 | -0.1236 | -121.6827 | 0.050354 | -120.9137 | -121.637 | -121.7606 | -0.09613 | 0.027466 | -0.004578 | 0 | 0 | -0.022888 | 0.036621 | 0 | -0.24719 | -0.073242 | 0.76904 | -0.07782 | 0.045776 | -0.07782 | 0.045776 | 121.6782 | -0.09613 | -0.1236 | 121.6827 | 121.7194 | 121.6599 | 0.041199 | -0.01831 | 0.76904 | 121.7331 | 0.004578 | 0.004578 | 121.5591 | 0.032044 | 121.5591 | 121.7102 | -121.8063 | -0.12817 | 121.7331 | 121.6827 | 102.9327 | 121.5866
1343.8125 | 121.9849 | -121.6324 | 0.091553 | -0.0016785 | 6.9739 | 0.066541 | 0.060229 | -7.2628e-05 | -0.0067547 | -0.0027942 | -0.00054933 | 0.0009506 | 0.016314 | -0.004954 | -0.0057721 | 0.023821 | -0.00051479 | -18.7637 | -0.15564 | -121.6782 | 0.11444 | -120.8542 | -121.5775 | -121.701 | 0.009155 | -0.036621 | -0.013733 | 0.13275 | 0.1236 | 0.091553 | 0.16937 | -0.045777 | -0.24719 | 0.022888 | 0.7782 | -0.068665 | 0.054931 | -0.022888 | 0.10071 | 121.6187 | -0.12817 | 0.041198 | 121.756 | 121.8018 | 121.7239 | 0.18311 | 0.10529 | 0.82398 | 121.7926 | 0.13733 | 0.14648 | 121.5225 | -0.022888 | 121.4767 | 121.5958 | -121.7697 | -0.10529 | 121.7468 | 121.7651 | 102.8687 | 121.6415
1345.4844 | 121.8475 | -121.6919 | 0.12817 | 0.005951 | 6.9765 | 0.064832 | 0.062792 | -0.0011408 | -0.0073957 | -0.001726 | -0.0036011 | 0.0020188 | 0.017169 | -0.012644 | -0.0089765 | 0.02083 | -0.0058554 | -18.8278 | -0.10986 | -121.7102 | 0.009155 | -120.9595 | -121.669 | -121.7972 | -0.13733 | 0.018311 | -0.036621 | 0 | -0.027466 | -0.064087 | 0.041199 | -0.01831 | -0.23804 | -0.11902 | 0.73242 | -0.10528 | 0.022889 | -0.086975 | 0.041199 | 121.6553 | -0.10986 | -0.12817 | 121.6644 | 121.7331 | 121.6278 | 0.07782 | -0.027466 | 0.75073 | 121.7194 | 0.009155 | 0.036621 | 121.6003 | 0.054932 | 121.582 | 121.7102 | -121.8384 | -0.1648 | 121.7011 | 121.6919 | 102.8641 | 121.5546
1347.2188 | 121.9437 | -121.6599 | 0.10986 | -0.009308 | 6.975 | 0.066328 | 0.063006 | -0.0062676 | -0.0069683 | -0.0032214 | -0.0066527 | 0.0015914 | 0.017383 | -0.0092264 | -0.0059857 | 0.025103 | 0.001835 | -18.8507 | -0.15106 | -121.6827 | 0.073242 | -120.9091 | -121.637 | -121.7514 | -0.07782 | -0.027466 | -0.009155 | 0.064087 | 0.032043 | 0.004578 | 0.091553 | -0.022888 | -0.26093 | -0.036621 | 0.75073 | -0.091553 | 0.022888 | -0.068665 | 0.045776 | 121.6507 | -0.13733 | -0.045776 | 121.6919 | 121.7514 | 121.6644 | 0.10071 | 0.013733 | 0.77362 | 121.756 | 0.041198 | 0.073242 | 121.5317 | -0.018311 | 121.5088 | 121.6324 | -121.7926 | -0.11902 | 121.7331 | 121.7239 | 102.8091 | 121.582
1348.9531 | 121.8521 | -121.6873 | 0.11444 | -0.0016785 | 6.9776 | 0.067182 | 0.064288 | 0.0027044 | -0.0048321 | -0.003435 | -0.0036011 | 0.0026596 | 0.015674 | -0.0098672 | -0.0053449 | 0.025316 | -0.0020102 | -18.8141 | -0.10986 | -121.6965 | -0.009155 | -121.019 | -121.7239 | -121.8201 | -0.14191 | 0.004578 | -0.045776 | 0 | -0.059509 | -0.086975 | 0.064087 | -0.009155 | -0.2243 | -0.1236 | 0.66833 | -0.13275 | -0.036621 | -0.1236 | -0.027466 | 121.6415 | -0.10986 | -0.11444 | 121.6278 | 121.7514 | 121.6003 | 0.10986 | -0.041199 | 0.67749 | 121.6873 | -0.013733 | 0.045776 | 121.5866 | 0.050354 | 121.5775 | 121.6919 | -121.8109 | -0.16022 | 121.6782 | 121.6873 | 102.8732 | 121.5454
1350.6875 | 121.9574 | -121.6553 | 0.091553 | 0.005951 | 6.9752 | 0.067823 | 0.062151 | 0.0041998 | -0.0067547 | -0.0021532 | -0.0066527 | 0.0022324 | 0.016528 | -0.0034586 | -0.0047039 | 0.022326 | -0.00051479 | -18.7775 | -0.1236 | -121.6919 | 0.059509 | -120.9503 | -121.6827 | -121.7834 | -0.054932 | -0.018311 | -0.004578 | 0.09613 | 0.054932 | 0.022888 | 0.14648 | -0.036622 | -0.21515 | -0.032044 | 0.70496 | -0.12817 | -0.027466 | -0.091552 | 0.009156 | 121.6507 | -0.10986 | 0.004577 | 121.7102 | 121.8018 | 121.6782 | 0.15106 | 0.027466 | 0.74158 | 121.7514 | 0.05951 | 0.10071 | 121.5683 | -0.013733 | 121.5317 | 121.637 | -121.7834 | -0.096131 | 121.7148 | 121.7514 | 102.8778 | 121.6003
1352.375 | 121.9711 | -121.6553 | 0.09613 | -0.009308 | 6.9759 | 0.06761 | 0.062365 | 0.0037726 | -0.0046185 | -0.00023063 | -0.00054933 | 0.0026596 | 0.016955 | -0.00046777 | -0.0036359 | 0.025957 | -0.0013694 | -18.7546 | -0.13275 | -121.701 | 0.086975 | -120.9137 | -121.6232 | -121.7331 | -0.018311 | -0.027466 | -0.013733 | 0.12817 | 0.064087 | 0.041199 | 0.15106 | -0.045777 | -0.22888 | -0.009155 | 0.74158 | -0.07782 | 0.032043 | -0.032043 | 0.07782 | 121.6415 | -0.1236 | 0.032044 | 121.7194 | 121.8063 | 121.6965 | 0.16479 | 0.054932 | 0.78735 | 121.788 | 0.07782 | 0.14191 | 121.5683 | -0.013733 | 121.5225 | 121.6278 | -121.7972 | -0.10986 | 121.7422 | 121.7834 | 102.9007 | 121.637
1354.1094 | 122.0032 | -121.6415 | 0.086975 | -0.009308 | 6.9767 | 0.064832 | 0.063006 | 0.0029182 | -0.0065411 | -0.0040758 | -0.00054933 | 9.6204e-05 | 0.015033 | -0.00944 | -0.0057721 | 0.02553 | -0.0017966 | -18.7592 | -0.14648 | -121.7056 | 0.10529 | -120.8817 | -121.6095 | -121.7422 | 0 | -0.027466 | 0.004578 | 0.14191 | 0.082397 | 0.050354 | 0.15564 | -0.064086 | -0.23346 | 0.018311 | 0.75989 | -0.10071 | 0.032044 | -0.036622 | 0.09613 | 121.6461 | -0.11444 | 0.054932 | 121.7239 | 121.7972 | 121.6919 | 0.15106 | 0.045776 | 0.82397 | 121.8109 | 0.077819 | 0.13733 | 121.5591 | -0.032044 | 121.4951 | 121.6141 | -121.7926 | -0.082397 | 121.7468 | 121.7834 | 102.8824 | 121.6415
1355.8438 | 121.9711 | -121.6461 | 0.073242 | -0.016937 | 6.9782 | 0.068891 | 0.062579 | 0.00185 | -0.0050457 | -0.0030078 | -0.0036011 | 0.0018052 | 0.015246 | -0.004313 | -0.0072675 | 0.026385 | -0.0062826 | -18.7363 | -0.16022 | -121.6278 | 0.13275 | -120.845 | -121.6095 | -121.7148 | 0.013733 | -0.032043 | 0.018311 | 0.12817 | 0.09613 | 0.050354 | 0.16022 | 0.01831 | -0.23346 | 0.059509 | 0.80109 | -0.068665 | 0.036621 | -0.086975 | 0.018311 | 121.6644 | -0.10529 | 0.054932 | 121.7422 | 121.8063 | 121.6965 | 0.14191 | 0.032043 | 0.78278 | 121.7606 | 0.077819 | 0.10986 | 121.4676 | -0.050354 | 121.4859 | 121.6141 | -121.701 | -0.054931 | 121.7789 | 121.7743 | 102.9099 | 121.6599
1357.5156 | 121.8521 | -121.6965 | 0.12817 | -0.0016785 | 6.9742 | 0.064405 | 0.061938 | -0.00071343 | -0.0091047 | -0.0015124 | -0.0097045 | 0.0037278 | 0.01546 | -0.0068766 | -0.0091901 | 0.024462 | -0.001583 | -18.75 | -0.11444 | -121.7285 | 0 | -120.9824 | -121.6736 | -121.8155 | -0.15106 | -0.004578 | -0.018311 | -0.004578 | -0.032043 | -0.064087 | 0.059509 | -0.032044 | -0.24262 | -0.12817 | 0.71411 | -0.11902 | 0.022888 | -0.086975 | 0.054932 | 121.6782 | -0.13275 | -0.13275 | 121.6644 | 121.756 | 121.6324 | 0.07782 | -0.045776 | 0.74616 | 121.7285 | -0.013732 | 0.013733 | 121.6141 | 0.013733 | 121.582 | 121.6919 | -121.8567 | -0.14649 | 121.6965 | 121.6919 | 102.9465 | 121.5454
1359.25 | 122.0215 | -121.6507 | 0.068665 | -0.016937 | 6.9744 | 0.066114 | 0.063647 | -0.0011408 | -0.0052595 | -0.0030078 | -0.0036011 | 0.0026596 | 0.013965 | -0.003245 | -0.0066265 | 0.022326 | -0.0039328 | -18.6493 | -0.14648 | -121.6919 | 0.15564 | -120.8313 | -121.55 | -121.6873 | 0.050354 | -0.018311 | 0.009155 | 0.1236 | 0.1236 | 0.086975 | 0.15106 | -0.041199 | -0.21515 | 0.086975 | 0.8194 | -0.036621 | 0.10071 | 0.004578 | 0.14191 | 121.6599 | -0.086976 | 0.054931 | 121.7743 | 121.8018 | 121.7377 | 0.14191 | 0.07782 | 0.8606 | 121.8475 | 0.11444 | 0.11444 | 121.5454 | -0.027466 | 121.5042 | 121.6324 | -121.7606 | -0.05951 | 121.8063 | 121.7743 | 103.0014 | 121.701
1360.9844 | 121.8658 | -121.7056 | 0.13275 | -0.009308 | 6.9759 | 0.066969 | 0.065783 | -0.0013544 | -0.0059003 | -0.0019396 | -0.00054933 | 0.0050094 | 0.015674 | 0.00038663 | -0.0057721 | 0.024676 | -0.0030784 | -18.6722 | -0.10071 | -121.7194 | 0.004578 | -121.0236 | -121.7194 | -121.8384 | -0.15564 | 0.022888 | -0.045776 | 0.018311 | -0.045776 | -0.086975 | 0.050354 | -0.013733 | -0.23346 | -0.12817 | 0.68207 | -0.13275 | -0.013733 | -0.11902 | 0 | 121.6599 | -0.10986 | -0.11444 | 121.6599 | 121.756 | 121.6187 | 0.09613 | -0.041199 | 0.6958 | 121.7239 | 0 | 0.064087 | 121.6187 | 0.068664 | 121.6049 | 121.7285 | -121.8521 | -0.17853 | 121.7102 | 121.7239 | 103.0334 | 121.55
1362.7344 | 121.8704 | -121.7056 | 0.10071 | -0.0016785 | 6.9778 | 0.066541 | 0.065997 | 0.0022772 | -0.0031231 | -0.0010852 | -0.00054933 | 0.0005234 | 0.01781 | -0.0023904 | -0.0064129 | 0.023821 | 0.0020486 | -18.6905 | -0.11902 | -121.7148 | 0 | -121.0236 | -121.7468 | -121.843 | -0.14648 | 0 | -0.027466 | -0.004578 | -0.064087 | -0.10529 | 0.050354 | -0.009156 | -0.21973 | -0.10071 | 0.68207 | -0.13733 | -0.041199 | -0.12817 | -0.032043 | 121.6782 | -0.10071 | -0.10529 | 121.6415 | 121.756 | 121.6003 | 0.07782 | -0.07782 | 0.69122 | 121.7148 | -0.036621 | 0.022888 | 121.5958 | 0.027466 | 121.5866 | 121.7056 | -121.8155 | -0.12817 | 121.7056 | 121.701 | 103.0151 | 121.5591
1364.4062 | 121.9894 | -121.6553 | 0.082397 | -0.009308 | 6.9776 | 0.06825 | 0.061724 | 0.00056817 | -0.0067547 | -0.00065803 | -0.0036011 | 0.0015914 | 0.016528 | -0.0047404 | -0.0051313 | 0.02553 | -0.00671 | -18.663 | -0.14191 | -121.6919 | 0.10071 | -120.8908 | -121.6232 | -121.7514 | -0.013733 | -0.022888 | 0 | 0.14648 | 0.091553 | 0.050354 | 0.15106 | -0.036622 | -0.2243 | 0.018311 | 0.76446 | -0.096131 | 0.032043 | -0.059509 | 0.068665 | 121.6553 | -0.10528 | 0.064087 | 121.7468 | 121.8063 | 121.7056 | 0.15106 | 0.050354 | 0.80109 | 121.7926 | 0.091553 | 0.14648 | 121.55 | -0.022888 | 121.5134 | 121.6324 | -121.7743 | -0.082397 | 121.756 | 121.8018 | 102.9922 | 121.6415
1366.1406 | 122.0032 | -121.6553 | 0.068665 | -0.024567 | 6.9752 | 0.066328 | 0.062365 | 0.00099557 | -0.0056867 | -0.0036486 | -0.0097045 | 0.0003098 | 0.014605 | -0.0070902 | -0.0040631 | 0.024676 | 0.001835 | -18.6539 | -0.16937 | -121.6599 | 0.12817 | -120.8496 | -121.6095 | -121.7239 | 0 | -0.032043 | 0.009155 | 0.13275 | 0.082397 | 0.041199 | 0.15106 | -0.004578 | -0.23804 | 0.059509 | 0.80566 | -0.068665 | 0.045776 | -0.064087 | 0.050354 | 121.6644 | -0.10071 | 0.064086 | 121.7377 | 121.8063 | 121.6965 | 0.14191 | 0.032044 | 0.81024 | 121.788 | 0.073242 | 0.1236 | 121.4905 | -0.041198 | 121.4859 | 121.6232 | -121.7285 | -0.05951 | 121.7834 | 121.788 | 103.0014 | 121.6553
1367.8906 | 121.962 | -121.6553 | 0.086975 | -0.009308 | 6.9733 | 0.068464 | 0.063647 | -0.001568 | -0.0063275 | -0.00044443 | -0.0066527 | 0.0013778 | 0.015033 | -0.0085856 | -0.0061993 | 0.023821 | -0.0024374 | -18.6676 | -0.16022 | -121.6782 | 0.11902 | -120.8725 | -121.6324 | -121.7422 | -0.022888 | -0.027466 | 0.004578 | 0.10071 | 0.050354 | 0.018311 | 0.10529 | -0.022889 | -0.24719 | 0.032044 | 0.78278 | -0.086976 | 0.022888 | -0.064087 | 0.045777 | 121.6599 | -0.11444 | 0.013733 | 121.7056 | 121.7606 | 121.6736 | 0.10071 | 0.013733 | 0.80566 | 121.7972 | 0.045776 | 0.09613 | 121.5179 | -0.032044 | 121.4951 | 121.6278 | -121.7651 | -0.082397 | 121.7743 | 121.756 | 102.9877 | 121.6324
1369.5625 | 121.9986 | -121.6507 | 0.091553 | -0.0016785 | 6.9746 | 0.065046 | 0.059588 | 0.00014097 | -0.0076093 | -0.0010852 | -0.0036011 | 0.0011642 | 0.01311 | -0.0079446 | -0.0081219 | 0.024035 | -0.00030119 | -18.6172 | -0.14191 | -121.6919 | 0.15564 | -120.8176 | -121.5363 | -121.6782 | 0.013733 | -0.027466 | 0.004578 | 0.11444 | 0.11902 | 0.082397 | 0.15106 | -0.041199 | -0.23346 | 0.064087 | 0.83313 | -0.027466 | 0.11444 | 0.013733 | 0.15564 | 121.6553 | -0.11902 | 0.022888 | 121.7697 | 121.8018 | 121.7331 | 0.14648 | 0.077819 | 0.87433 | 121.8475 | 0.11444 | 0.10986 | 121.55 | -0.032044 | 121.5088 | 121.6232 | -121.7834 | -0.086975 | 121.8063 | 121.7651 | 103.0334 | 121.6644
1371.2969 | 121.8704 | -121.6965 | 0.14191 | 0.005951 | 6.9759 | 0.068037 | 0.063006 | 0.0039862 | -0.0071821 | 0.0014784 | -0.00054933 | 0.0043686 | 0.015246 | -0.0023904 | -0.0068403 | 0.024676 | -0.00072839 | -18.6951 | -0.10529 | -121.6965 | 0.032043 | -120.9915 | -121.7102 | -121.8292 | -0.15106 | 0.018311 | -0.036621 | 0.013733 | -0.045776 | -0.086975 | 0.041199 | 0 | -0.24719 | -0.10986 | 0.70496 | -0.13275 | -0.013733 | -0.13275 | -0.013733 | 121.6599 | -0.1236 | -0.12817 | 121.6507 | 121.7377 | 121.6095 | 0.07782 | -0.050354 | 0.70496 | 121.7285 | -0.009155 | 0.050354 | 121.5912 | 0.054932 | 121.5912 | 121.7148 | -121.8384 | -0.17853 | 121.7285 | 121.7102 | 103.0014 | 121.5454
1372.9844 | 122.0078 | -121.6782 | 0.091553 | -0.009308 | 6.9748 | 0.065687 | 0.061297 | 0.0022772 | -0.0063275 | -0.0032214 | -0.00054933 | -0.0003312 | 0.016101 | -0.0090128 | -0.0087629 | 0.022967 | -0.002651 | -18.5806 | -0.15106 | -121.6919 | 0.14191 | -120.8359 | -121.5546 | -121.6965 | -0.009155 | -0.018311 | 0.009155 | 0.1236 | 0.10071 | 0.064087 | 0.12817 | -0.013733 | -0.24261 | 0.050354 | 0.84229 | -0.01831 | 0.1236 | -0.004577 | 0.13733 | 121.6873 | -0.10986 | 0.032043 | 121.7789 | 121.8063 | 121.7422 | 0.11902 | 0.054932 | 0.85602 | 121.8338 | 0.091553 | 0.11444 | 121.5408 | -0.027466 | 121.5271 | 121.6599 | -121.7834 | -0.082398 | 121.8201 | 121.8018 | 103.0975 | 121.669
1374.7188 | 122.0078 | -121.669 | 0.059509 | -0.009308 | 6.9716 | 0.065687 | 0.060656 | -0.0024224 | -0.0050457 | -0.001726 | -0.0066527 | 0.0018052 | 0.015887 | -0.0081582 | -0.0085491 | 0.023607 | -0.00072839 | -18.6539 | -0.13275 | -121.6736 | 0.15564 | -120.813 | -121.55 | -121.6736 | 0.027466 | -0.032043 | 0 | 0.1236 | 0.12817 | 0.091553 | 0.14191 | -0.004578 | -0.19226 | 0.096131 | 0.85602 | -0.004578 | 0.11902 | 0 | 0.1236 | 121.669 | -0.091552 | 0.064087 | 121.7972 | 121.8109 | 121.7606 | 0.14191 | 0.091553 | 0.8606 | 121.8292 | 0.12817 | 0.1236 | 121.5408 | -0.032043 | 121.5363 | 121.637 | -121.7331 | -0.059509 | 121.8246 | 121.7926 | 103.0151 | 121.6965
1376.4531 | 121.994 | -121.6599 | 0.068665 | -0.009308 | 6.9771 | 0.066969 | 0.062365 | -0.0019952 | -0.0044049 | -0.003435 | -0.0036011 | 0.0011642 | 0.01546 | -0.0040994 | -0.0012861 | 0.024676 | -0.0022238 | -18.6356 | -0.13733 | -121.6827 | 0.13275 | -120.8542 | -121.5866 | -121.7331 | 0.013733 | -0.032043 | -0.004578 | 0.14648 | 0.09613 | 0.045776 | 0.14648 | -0.022888 | -0.20599 | 0.064086 | 0.80566 | -0.073242 | 0.073242 | -0.050354 | 0.09613 | 121.6553 | -0.10071 | 0.077819 | 121.756 | 121.8063 | 121.7056 | 0.15106 | 0.050354 | 0.82855 | 121.8155 | 0.10071 | 0.15106 | 121.5454 | -0.027465 | 121.5225 | 121.6278 | -121.7514 | -0.073243 | 121.7926 | 121.8063 | 103.0243 | 121.6736
1378.1406 | 121.8567 | -121.7239 | 0.11444 | -0.009308 | 6.9784 | 0.067396 | 0.06386 | -0.0075494 | -0.0052595 | 0.00083737 | -0.0066527 | 0.0050094 | 0.016101 | -0.006022 | -0.0072675 | 0.025316 | -0.00072839 | -18.6768 | -0.10529 | -121.7514 | 0.022888 | -121.019 | -121.7239 | -121.843 | -0.17853 | 0.013733 | -0.032043 | -0.004578 | -0.068665 | -0.10986 | 0.032043 | -0.027466 | -0.21973 | -0.091553 | 0.70496 | -0.11902 | 0 | -0.091553 | 0.027466 | 121.6919 | -0.10071 | -0.11902 | 121.6553 | 121.756 | 121.6141 | 0.064086 | -0.07782 | 0.73242 | 121.7743 | -0.036622 | 0.027465 | 121.6461 | 0.045776 | 121.6187 | 121.7377 | -121.8658 | -0.14648 | 121.7468 | 121.7194 | 103.0472 | 121.5454
1379.875 | 121.9986 | -121.6599 | 0.086975 | -0.016937 | 6.9776 | 0.064192 | 0.061297 | 0.0016364 | -0.0082501 | -0.0036486 | -0.0036011 | 0.000737 | 0.014819 | -0.010722 | -0.0053449 | 0.024248 | -0.0052146 | -18.6905 | -0.14191 | -121.6827 | 0.10529 | -120.8862 | -121.5729 | -121.7056 | -0.004578 | -0.022888 | 0.004578 | 0.13275 | 0.10071 | 0.082397 | 0.14648 | -0.022888 | -0.22888 | 0.018311 | 0.77362 | -0.045776 | 0.086975 | -0.022888 | 0.10986 | 121.6644 | -0.10986 | 0.045776 | 121.7606 | 121.8063 | 121.7422 | 0.14191 | 0.077819 | 0.79651 | 121.788 | 0.09613 | 0.12817 | 121.5408 | -0.027466 | 121.5179 | 121.637 | -121.7697 | -0.082397 | 121.7651 | 121.7926 | 102.9694 | 121.6553
1381.5625 | 121.8842 | -121.7194 | 0.10529 | -0.0016785 | 6.9763 | 0.067823 | 0.063433 | -0.00071343 | -0.0063275 | -0.0027942 | -0.0036011 | 0.0005234 | 0.016314 | -0.013499 | -0.0074811 | 0.024462 | -0.003292 | -18.6676 | -0.13733 | -121.7194 | 0.054932 | -120.9412 | -121.6415 | -121.7789 | -0.1236 | 0.009155 | -0.027466 | 0.013733 | -0.018311 | -0.045776 | 0.027466 | 0 | -0.24262 | -0.050354 | 0.7782 | -0.05951 | 0.077819 | -0.05951 | 0.077819 | 121.6919 | -0.096131 | -0.091553 | 121.701 | 121.7468 | 121.6736 | 0.054932 | -0.01831 | 0.7782 | 121.7743 | 0.009155 | 0.041199 | 121.582 | 0.036621 | 121.582 | 121.7285 | -121.8246 | -0.13275 | 121.7743 | 121.7331 | 103.0518 | 121.5958
1383.3125 | 122.0215 | -121.6736 | 0.082397 | 0.005951 | 6.9756 | 0.069105 | 0.063433 | -0.0022088 | -0.0063275 | -0.002367 | -0.00054933 | 0.0003098 | 0.014819 | -0.0034586 | -0.0036359 | 0.025103 | -0.002651 | -18.6401 | -0.15564 | -121.6782 | 0.14648 | -120.8679 | -121.6278 | -121.7331 | -0.004578 | -0.041199 | -0.013733 | 0.14191 | 0.091553 | 0.045776 | 0.14648 | -0.004578 | -0.23804 | 0.064087 | 0.80566 | -0.059509 | 0.045776 | -0.054931 | 0.050354 | 121.6599 | -0.1236 | 0.05951 | 121.7651 | 121.8201 | 121.7194 | 0.16022 | 0.059509 | 0.81024 | 121.8246 | 0.10529 | 0.15564 | 121.5225 | -0.027466 | 121.5179 | 121.6324 | -121.7606 | -0.09613 | 121.8201 | 121.8155 | 103.0334 | 121.669
1385.0469 | 121.9986 | -121.669 | 0.059509 | -0.0016785 | 6.9791 | 0.066969 | 0.065569 | -0.00071343 | -0.0059003 | -0.0027942 | -0.0036011 | 0.000737 | 0.014819 | -0.0058084 | -0.0044903 | 0.026598 | -0.0075644 | -18.6447 | -0.14648 | -121.6965 | 0.11902 | -120.8725 | -121.6232 | -121.7422 | -0.004578 | -0.050354 | 0 | 0.15106 | 0.086975 | 0.036621 | 0.15106 | -0.027466 | -0.20599 | 0.05951 | 0.79651 | -0.073243 | 0.045776 | -0.045777 | 0.073242 | 121.669 | -0.10986 | 0.091553 | 121.756 | 121.8201 | 121.7056 | 0.15106 | 0.036621 | 0.82397 | 121.8155 | 0.086975 | 0.15106 | 121.55 | -0.050354 | 121.5225 | 121.6187 | -121.756 | -0.059509 | 121.788 | 121.8201 | 103.0243 | 121.6644
1386.7969 | 122.0078 | -121.6736 | 0.068665 | -0.0016785 | 6.9731 | 0.063764 | 0.063433 | 0.0014228 | -0.0065411 | -0.0021532 | -0.0036011 | 9.6204e-05 | 0.013965 | -0.0023904 | -0.0051313 | 0.024889 | -0.00072839 | -18.5944 | -0.14648 | -121.6827 | 0.15106 | -120.8725 | -121.6187 | -121.7422 | -0.009155 | -0.036621 | -0.004578 | 0.14648 | 0.10071 | 0.045776 | 0.16022 | -0.009155 | -0.21515 | 0.082397 | 0.80109 | -0.068665 | 0.054932 | -0.05951 | 0.064087 | 121.669 | -0.10529 | 0.077819 | 121.7743 | 121.8338 | 121.7194 | 0.16479 | 0.050354 | 0.81024 | 121.8338 | 0.10529 | 0.15106 | 121.5363 | -0.032043 | 121.5271 | 121.637 | -121.7514 | -0.073243 | 121.8246 | 121.8201 | 103.0792 | 121.6644
1388.4688 | 121.9757 | -121.6736 | 0.091553 | -0.009308 | 6.978 | 0.06825 | 0.065356 | 0.0020636 | -0.0067547 | -0.0032214 | -0.00054933 | 0.0037278 | 0.017596 | 0.0016684 | -0.0049175 | 0.02553 | -0.0017966 | -18.6584 | -0.1236 | -121.7148 | 0.054932 | -120.9549 | -121.6873 | -121.8063 | -0.07782 | -0.018311 | -0.022888 | 0.11444 | 0.054932 | 0.018311 | 0.14648 | -0.041199 | -0.21515 | -0.036621 | 0.71869 | -0.13275 | -0.013733 | -0.091552 | 0.027466 | 121.6507 | -0.10986 | 0.022888 | 121.7285 | 121.8201 | 121.6919 | 0.16937 | 0.041199 | 0.75989 | 121.7697 | 0.07782 | 0.13733 | 121.5912 | 0.004577 | 121.55 | 121.6553 | -121.8063 | -0.11444 | 121.7285 | 121.788 | 103.0151 | 121.5958
1390.2188 | 122.0032 | -121.669 | 0.09613 | -0.016937 | 6.9752 | 0.065901 | 0.060015 | -0.00071343 | -0.0086773 | -1.7026e-05 | -0.00054933 | 9.6204e-05 | 0.014819 | -0.0047404 | -0.0089765 | 0.025957 | -0.0024374 | -18.5577 | -0.16022 | -121.701 | 0.16022 | -120.8405 | -121.5729 | -121.7056 | 0.004578 | -0.018311 | 0.009155 | 0.11444 | 0.10986 | 0.059509 | 0.13733 | -0.032044 | -0.25635 | 0.064087 | 0.82855 | -0.036621 | 0.09613 | -0.004577 | 0.12817 | 121.6782 | -0.11444 | 0.018311 | 121.7789 | 121.8063 | 121.7285 | 0.12817 | 0.050354 | 0.8606 | 121.8613 | 0.10071 | 0.10529 | 121.5408 | -0.027466 | 121.5088 | 121.6507 | -121.7972 | -0.086975 | 121.8292 | 121.7834 | 103.1113 | 121.6736
1391.9531 | 121.875 | -121.7422 | 0.12817 | -0.009308 | 6.9746 | 0.065687 | 0.064501 | -0.00071343 | -0.0069683 | -0.0027942 | -0.0036011 | 0.0028732 | 0.017169 | -0.0092264 | -0.01154 | 0.023394 | -0.0047874 | -18.6172 | -0.09613 | -121.7285 | 0.018311 | -120.9869 | -121.701 | -121.8292 | -0.15106 | 0.018311 | -0.045776 | -0.013733 | -0.036621 | -0.07782 | 0.009155 | 0.013733 | -0.2243 | -0.10986 | 0.75531 | -0.086975 | 0.041199 | -0.10071 | 0.027466 | 121.6965 | -0.10986 | -0.14191 | 121.7056 | 121.7514 | 121.6644 | 0.054931 | -0.032044 | 0.74158 | 121.7468 | 0.009155 | 0.032043 | 121.6324 | 0.064087 | 121.6461 | 121.7606 | -121.8567 | -0.17395 | 121.7606 | 121.7285 | 103.125 | 121.5912
1393.625 | 121.9391 | -121.7102 | 0.10529 | -0.032196 | 6.9752 | 0.066755 | 0.064074 | -0.00028623 | -0.0041913 | -0.0021532 | -0.0097045 | 0.003514 | 0.015246 | -0.016062 | -0.0070539 | 0.020403 | -0.0039328 | -18.6081 | -0.1236 | -121.7285 | 0.064087 | -120.9549 | -121.6736 | -121.8018 | -0.10529 | -0.004578 | -0.018311 | 0.064087 | 0.032043 | -0.036621 | 0.082397 | -0.018311 | -0.22888 | -0.041199 | 0.75531 | -0.091553 | 0.036621 | -0.073242 | 0.054932 | 121.6919 | -0.10986 | -0.041199 | 121.7422 | 121.7926 | 121.6736 | 0.10071 | -0.01831 | 0.77362 | 121.7926 | 0.050354 | 0.082398 | 121.6049 | 0.013733 | 121.5866 | 121.7056 | -121.8338 | -0.1236 | 121.7743 | 121.7743 | 103.1021 | 121.6049
1395.3594 | 121.907 | -121.7148 | 0.10986 | -0.0016785 | 6.9763 | 0.068464 | 0.064929 | -0.002636 | -0.0059003 | -0.0012988 | -0.0066527 | 0.0037278 | 0.014819 | -0.011363 | -0.0070539 | 0.025316 | -0.0037192 | -18.6218 | -0.13275 | -121.7331 | 0.07782 | -120.9457 | -121.669 | -121.7834 | -0.09613 | -0.013733 | -0.027466 | 0.068665 | 0 | -0.054932 | 0.064087 | -0.01831 | -0.24261 | -0.032043 | 0.76904 | -0.068664 | 0.045777 | -0.050354 | 0.064087 | 121.6873 | -0.1236 | -0.041198 | 121.7148 | 121.7789 | 121.6599 | 0.091553 | -0.027466 | 0.78735 | 121.8109 | 0.027466 | 0.096131 | 121.6003 | 0.013733 | 121.582 | 121.701 | -121.843 | -0.13733 | 121.7926 | 121.7834 | 103.093 | 121.6187
1397.0781 | 121.9025 | -121.7194 | 0.10529 | -0.009308 | 6.9778 | 0.067396 | 0.065783 | -0.0034906 | -0.0073957 | -0.0030078 | -0.00054933 | 0.0026596 | 0.017169 | -0.0064494 | -0.0066265 | 0.024462 | -0.0013694 | -18.5806 | -0.12817 | -121.7194 | 0.059509 | -120.932 | -121.6507 | -121.7972 | -0.091553 | -0.013733 | -0.036621 | 0.050354 | 0.004578 | -0.064087 | 0.054932 | 0 | -0.23346 | -0.045777 | 0.78735 | -0.07782 | 0.068664 | -0.07782 | 0.068664 | 121.6827 | -0.11902 | -0.054932 | 121.7239 | 121.7743 | 121.6553 | 0.091553 | -0.027466 | 0.78735 | 121.7789 | 0.041199 | 0.086975 | 121.5912 | 0.022888 | 121.5912 | 121.7056 | -121.8246 | -0.14191 | 121.7789 | 121.7697 | 103.1387 | 121.6278
1398.7656 | 121.9803 | -121.6736 | 0.10529 | -0.016937 | 6.9744 | 0.067182 | 0.061511 | -0.0034906 | -0.0080365 | -0.0015124 | -0.0036011 | -0.0005448 | 0.01546 | -0.0055948 | -0.0068403 | 0.025316 | -0.0011558 | -18.6905 | -0.15106 | -121.7194 | 0.073242 | -120.9274 | -121.6324 | -121.7606 | -0.082397 | -0.022888 | -0.018311 | 0.091553 | 0.050354 | 0.027466 | 0.10529 | -0.045776 | -0.25635 | -0.032044 | 0.74616 | -0.086975 | 0.041199 | -0.041199 | 0.086975 | 121.6553 | -0.12817 | -0.013733 | 121.7239 | 121.7789 | 121.7011 | 0.1236 | 0.045777 | 0.79193 | 121.7926 | 0.068665 | 0.10986 | 121.5683 | -0.004577 | 121.5225 | 121.6507 | -121.8246 | -0.1236 | 121.7468 | 121.7651 | 102.9831 | 121.5912
1400.5 | 121.8842 | -121.7102 | 0.10529 | -0.0016785 | 6.9767 | 0.067396 | 0.064501 | 0.0071906 | -0.0061139 | -0.003435 | -0.00054933 | 0.003514 | 0.01781 | -0.01414 | -0.0059857 | 0.024462 | -0.002651 | -18.6447 | -0.11444 | -121.7651 | -0.009155 | -121.0419 | -121.7606 | -121.8521 | -0.16479 | -0.009155 | -0.050354 | 0.013733 | -0.054932 | -0.10529 | 0.032043 | -0.054932 | -0.21973 | -0.11444 | 0.66833 | -0.14191 | -0.050354 | -0.086975 | 0.004578 | 121.6599 | -0.11444 | -0.091553 | 121.6553 | 121.7422 | 121.6049 | 0.082397 | -0.054932 | 0.72327 | 121.756 | -0.004578 | 0.064087 | 121.6507 | 0.041199 | 121.5958 | 121.701 | -121.8704 | -0.15564 | 121.701 | 121.7239 | 103.0655 | 121.5454
1402.25 | 121.875 | -121.7468 | 0.11444 | -0.009308 | 6.9735 | 0.065901 | 0.06386 | 0.0027044 | -0.0071821 | -0.00087163 | -0.0097045 | 0.0018052 | 0.015674 | -0.0085856 | -0.012181 | 0.022112 | -0.0037192 | -18.6218 | -0.10071 | -121.756 | -0.018311 | -121.0327 | -121.7056 | -121.843 | -0.1831 | -0.004578 | -0.032043 | -0.004578 | -0.041199 | -0.07782 | 0.032043 | -0.009155 | -0.21515 | -0.13275 | 0.71411 | -0.096131 | 0.041199 | -0.086976 | 0.050354 | 121.7148 | -0.11902 | -0.11902 | 121.7056 | 121.7789 | 121.669 | 0.064086 | -0.045777 | 0.72327 | 121.7377 | -0.009156 | 0.027465 | 121.6553 | 0.027465 | 121.6461 | 121.7422 | -121.8704 | -0.14648 | 121.7285 | 121.7422 | 103.125 | 121.5637
1403.9375 | 121.875 | -121.7285 | 0.11444 | -0.016937 | 6.9748 | 0.066755 | 0.063006 | 0.0014228 | -0.0059003 | -0.00065803 | -0.0097045 | 0.0018052 | 0.016955 | 0.0014548 | -0.010472 | 0.02318 | -0.0037192 | -18.5852 | -0.10986 | -121.7331 | 0 | -121.0052 | -121.701 | -121.8246 | -0.19226 | 0.013733 | -0.022888 | -0.004578 | -0.064087 | -0.073242 | 0.018311 | -0.004577 | -0.2243 | -0.11444 | 0.72327 | -0.09613 | 0.027466 | -0.091553 | 0.032043 | 121.7056 | -0.10071 | -0.11902 | 121.6644 | 121.7468 | 121.6553 | 0.041199 | -0.050354 | 0.72784 | 121.7331 | -0.041199 | 0.01831 | 121.6232 | 0.036621 | 121.6187 | 121.7422 | -121.8475 | -0.13733 | 121.7285 | 121.7239 | 103.1433 | 121.5363
1405.6719 | 121.9803 | -121.6873 | 0.10529 | -0.0016785 | 6.9754 | 0.066541 | 0.060442 | 0.00035457 | -0.0082501 | -0.0012988 | -0.00054933 | 0.0020188 | 0.013751 | -0.01414 | -0.0096173 | 0.024676 | -0.0024374 | -18.5165 | -0.15564 | -121.7056 | 0.12817 | -120.8771 | -121.6049 | -121.7239 | -0.027466 | -0.022888 | -0.013733 | 0.10071 | 0.082397 | 0.041199 | 0.10986 | -0.01831 | -0.26093 | 0.022888 | 0.81024 | -0.036621 | 0.082398 | -0.018311 | 0.10071 | 121.6736 | -0.12817 | -0.004578 | 121.7697 | 121.7972 | 121.7285 | 0.1236 | 0.054932 | 0.82855 | 121.8338 | 0.09613 | 0.11444 | 121.55 | -0.009155 | 121.5317 | 121.6644 | -121.8109 | -0.11902 | 121.8155 | 121.788 | 103.1708 | 121.6599
1407.4062 | 121.8933 | -121.7422 | 0.10529 | -0.009308 | 6.9782 | 0.066114 | 0.06322 | -0.0022088 | -0.0076093 | -0.00065803 | -0.0066527 | 0.0043686 | 0.015033 | -0.0085856 | -0.010899 | 0.019976 | -0.0024374 | -18.5303 | -0.09613 | -121.7606 | 0.004578 | -121.0144 | -121.7056 | -121.8246 | -0.18768 | 0.013733 | -0.032043 | -0.009155 | -0.036621 | -0.07782 | 0.027466 | -0.01831 | -0.20142 | -0.10071 | 0.72785 | -0.082397 | 0.036622 | -0.064087 | 0.054932 | 121.7102 | -0.091553 | -0.11444 | 121.7056 | 121.7697 | 121.6644 | 0.059509 | -0.045777 | 0.74616 | 121.7651 | -0.004578 | 0.022888 | 121.6644 | 0.045776 | 121.6461 | 121.756 | -121.8658 | -0.13733 | 121.7468 | 121.7331 | 103.212 | 121.5546
1409.1406 | 122.0032 | -121.7056 | 0.09613 | -0.009308 | 6.9744 | 0.06761 | 0.062365 | -0.002636 | -0.0067547 | -0.0030078 | -0.00054933 | 0.0020188 | 0.016314 | -0.013712 | -0.0051313 | 0.025744 | 0.00012601 | -18.5394 | -0.13733 | -121.7194 | 0.064087 | -120.9457 | -121.637 | -121.7697 | -0.09613 | -0.041199 | -0.013733 | 0.10071 | 0.059509 | 0.018311 | 0.10986 | -0.013733 | -0.23346 | -0.032043 | 0.75989 | -0.064087 | 0.068664 | -0.050354 | 0.082397 | 121.6919 | -0.13733 | 0.004578 | 121.7651 | 121.8155 | 121.7239 | 0.1236 | 0.032044 | 0.77362 | 121.7834 | 0.073242 | 0.11444 | 121.582 | -0.027466 | 121.5683 | 121.6644 | -121.8155 | -0.10986 | 121.7697 | 121.8063 | 103.1662 | 121.6095
1410.875 | 121.8796 | -121.7194 | 0.10071 | -0.0016785 | 6.9782 | 0.066541 | 0.065997 | 0.00099557 | -0.0056867 | -0.002367 | -0.0066527 | 0.0030868 | 0.017596 | -0.012644 | -0.0049175 | 0.02318 | -0.0075644 | -18.5623 | -0.11444 | -121.7285 | 0.032043 | -121.0052 | -121.7331 | -121.8521 | -0.15106 | 0.004578 | -0.027466 | 0.013733 | -0.054932 | -0.11444 | 0.018311 | -0.009156 | -0.21515 | -0.068665 | 0.71411 | -0.13275 | -0.013733 | -0.1236 | -0.004577 | 121.6919 | -0.09613 | -0.086975 | 121.6644 | 121.7377 | 121.6049 | 0.045777 | -0.086975 | 0.72327 | 121.7606 | -0.027466 | 0.041199 | 121.6141 | 0.032044 | 121.6049 | 121.7239 | -121.8292 | -0.12817 | 121.7514 | 121.7331 | 103.157 | 121.5683
1412.5625 | 121.962 | -121.6919 | 0.07782 | -0.024567 | 6.9742 | 0.066328 | 0.062792 | -0.00092703 | -0.0082501 | -0.0030078 | -0.0066527 | 0.0003098 | 0.013537 | -0.006663 | -0.0051313 | 0.024889 | -0.0011558 | -18.5349 | -0.15564 | -121.7194 | 0.082397 | -120.932 | -121.6644 | -121.7834 | -0.07782 | -0.045776 | -0.009155 | 0.073242 | 0.027466 | 0 | 0.086975 | -0.027465 | -0.23346 | 0.004577 | 0.75989 | -0.091552 | 0.027466 | -0.064087 | 0.054931 | 121.6827 | -0.1236 | -0.004578 | 121.7194 | 121.7789 | 121.6919 | 0.09613 | 0.009155 | 0.78735 | 121.8018 | 0.036621 | 0.082397 | 121.5637 | -0.036621 | 121.5363 | 121.6461 | -121.7972 | -0.086975 | 121.7743 | 121.7651 | 103.157 | 121.6141
1414.3125 | 122.0078 | -121.6827 | 0.091553 | -0.016937 | 6.9759 | 0.06761 | 0.063647 | 0.0039862 | -0.0097455 | -0.0042896 | -0.00054933 | 0.0022324 | 0.016742 | -0.003245 | -0.0049175 | 0.027239 | 0.0011942 | -18.512 | -0.13733 | -121.7468 | 0.10529 | -120.9274 | -121.6644 | -121.7789 | -0.041199 | -0.013733 | -0.004578 | 0.13275 | 0.073242 | 0.027466 | 0.14191 | -0.064087 | -0.22888 | 0.013733 | 0.75531 | -0.096131 | 0.01831 | -0.032044 | 0.082397 | 121.6782 | -0.10529 | 0.041198 | 121.756 | 121.8246 | 121.7102 | 0.14649 | 0.032044 | 0.8194 | 121.8521 | 0.07782 | 0.13733 | 121.6095 | -0.009155 | 121.5454 | 121.669 | -121.8384 | -0.096131 | 121.788 | 121.8155 | 103.1708 | 121.6415
1416.0625 | 121.9803 | -121.701 | 0.086975 | -0.024567 | 6.9746 | 0.066328 | 0.060656 | -0.0028498 | -0.0078229 | -0.0030078 | -0.0066527 | 0.0013778 | 0.01546 | -0.004954 | -0.0064129 | 0.027666 | -0.0017966 | -18.5394 | -0.15564 | -121.6873 | 0.10986 | -120.9229 | -121.669 | -121.7789 | -0.045776 | -0.041199 | -0.009155 | 0.09613 | 0.045776 | 0 | 0.10071 | 0.013733 | -0.24261 | 0.022888 | 0.7782 | -0.07782 | 0.032044 | -0.091553 | 0.018311 | 121.6919 | -0.12817 | 0.009155 | 121.7468 | 121.8018 | 121.701 | 0.10986 | 0.009155 | 0.76446 | 121.7972 | 0.054931 | 0.10528 | 121.5317 | -0.032044 | 121.5454 | 121.6599 | -121.7743 | -0.09613 | 121.8109 | 121.7972 | 103.1616 | 121.6553
1417.7656 | 121.9894 | -121.6827 | 0.082397 | -0.024567 | 6.9752 | 0.06761 | 0.063647 | 0.0050544 | -0.0035505 | 0.00041017 | -0.0036011 | 0.002446 | 0.014605 | -0.0075174 | -0.0042767 | 0.026812 | -0.0035056 | -18.4845 | -0.15564 | -121.701 | 0.12817 | -120.8862 | -121.637 | -121.7606 | -0.032043 | -0.036621 | 0.004578 | 0.1236 | 0.068665 | 0.018311 | 0.11444 | -0.018311 | -0.23804 | 0.045777 | 0.79651 | -0.07782 | 0.045776 | -0.059509 | 0.064087 | 121.6873 | -0.11902 | 0.041199 | 121.7514 | 121.7972 | 121.701 | 0.10986 | 0.013733 | 0.81482 | 121.8292 | 0.064087 | 0.11902 | 121.5454 | -0.041199 | 121.5271 | 121.6461 | -121.7834 | -0.077819 | 121.8109 | 121.8063 | 103.1982 | 121.6507
1419.5 | 121.9986 | -121.6965 | 0.086975 | -0.0016785 | 6.9761 | 0.068891 | 0.067492 | 0.0024908 | -0.0063275 | -0.00087163 | -0.00054933 | 0.0033004 | 0.015246 | -0.0045266 | -0.0053449 | 0.024248 | 0.00055321 | -18.4891 | -0.11902 | -121.7377 | 0.059509 | -120.9595 | -121.7056 | -121.8201 | -0.086975 | -0.009155 | -0.027466 | 0.11444 | 0.036621 | 0.009155 | 0.12817 | -0.041199 | -0.20599 | -0.027466 | 0.737 | -0.1236 | -0.009155 | -0.082397 | 0.032044 | 121.669 | -0.09613 | 0.027466 | 121.7331 | 121.8246 | 121.7056 | 0.15564 | 0.036621 | 0.7782 | 121.7972 | 0.064087 | 0.14191 | 121.6187 | 0.018311 | 121.5775 | 121.6873 | -121.8246 | -0.11444 | 121.756 | 121.8109 | 103.2074 | 121.6095
1421.25 | 121.9894 | -121.7102 | 0.091553 | -0.009308 | 6.975 | 0.06761 | 0.06322 | 0.006336 | -0.0054731 | -0.00087163 | -0.0036011 | 9.6204e-05 | 0.016742 | -0.014567 | -0.0066265 | 0.024035 | -0.0022238 | -18.5303 | -0.15564 | -121.7102 | 0.1236 | -120.9137 | -121.6461 | -121.7697 | -0.018311 | -0.032043 | -0.004578 | 0.10529 | 0.050354 | 0.013733 | 0.10529 | 0 | -0.24719 | 0.032043 | 0.79651 | -0.059509 | 0.064087 | -0.059509 | 0.064087 | 121.7056 | -0.1236 | 0.013733 | 121.7606 | 121.8155 | 121.7239 | 0.10986 | 0.018311 | 0.79651 | 121.8338 | 0.054932 | 0.10986 | 121.5546 | -0.027465 | 121.5546 | 121.6782 | -121.8018 | -0.096131 | 121.8338 | 121.8155 | 103.1799 | 121.6919
1422.9375 | 122.0123 | -121.7056 | 0.086975 | -0.0016785 | 6.9782 | 0.066328 | 0.061724 | 0.00078177 | -0.0080365 | -0.0036486 | -0.0036011 | 0.0003098 | 0.015033 | -0.0017496 | -0.0085491 | 0.02318 | -0.002651 | -18.4616 | -0.13733 | -121.7285 | 0.15564 | -120.8725 | -121.6095 | -121.7377 | -0.036621 | -0.027466 | 0.004578 | 0.11902 | 0.091553 | 0.050354 | 0.11902 | -0.022889 | -0.2243 | 0.068665 | 0.83313 | -0.032044 | 0.09613 | -0.009155 | 0.11902 | 121.7102 | -0.11444 | 0.032044 | 121.7972 | 121.8246 | 121.756 | 0.11444 | 0.045776 | 0.85602 | 121.8842 | 0.086975 | 0.11444 | 121.5912 | -0.032044 | 121.5683 | 121.6782 | -121.8155 | -0.082397 | 121.8613 | 121.8246 | 103.244 | 121.669
1424.6719 | 122.0215 | -121.6873 | 0.07782 | -0.009308 | 6.9763 | 0.066755 | 0.061724 | 0.0027044 | -0.0048321 | -0.00044443 | -0.0097045 | 0.0011642 | 0.016101 | 0.0023092 | -0.0061993 | 0.024889 | -0.006069 | -18.4616 | -0.15564 | -121.6919 | 0.13275 | -120.8908 | -121.6553 | -121.756 | -0.018311 | -0.059509 | -0.009155 | 0.14191 | 0.082397 | 0.041199 | 0.13275 | -0.004578 | -0.23346 | 0.054931 | 0.79651 | -0.068664 | 0.032044 | -0.064086 | 0.036622 | 121.6782 | -0.13733 | 0.064087 | 121.7697 | 121.8201 | 121.7285 | 0.14191 | 0.050354 | 0.80109 | 121.8246 | 0.091552 | 0.15106 | 121.5363 | -0.050354 | 121.5317 | 121.6278 | -121.7697 | -0.086975 | 121.8201 | 121.8292 | 103.2257 | 121.669
1426.4062 | 121.907 | -121.7148 | 0.12817 | -0.016937 | 6.9771 | 0.063978 | 0.061297 | 0.0037726 | -0.0071821 | -0.003435 | -0.0066527 | 0.0030868 | 0.01546 | -0.0036722 | -0.010045 | 0.025103 | -0.0024374 | -18.5349 | -0.091553 | -121.7651 | -0.009155 | -121.0464 | -121.7422 | -121.843 | -0.19684 | 0.004578 | -0.041199 | -0.004578 | -0.022888 | -0.07782 | 0.032043 | -0.050354 | -0.21973 | -0.13733 | 0.66833 | -0.12817 | -0.027466 | -0.07782 | 0.022888 | 121.6736 | -0.1236 | -0.13275 | 121.6919 | 121.7468 | 121.637 | 0.073242 | -0.036621 | 0.71869 | 121.756 | 0.018311 | 0.036621 | 121.6736 | 0.045777 | 121.6232 | 121.7194 | -121.8933 | -0.16937 | 121.7056 | 121.7102 | 103.1799 | 121.5179
1428.1562 | 121.9116 | -121.7239 | 0.11444 | 0.005951 | 6.9782 | 0.066328 | 0.062579 | 0.00014097 | -0.0050457 | -0.0010852 | -0.00054933 | 0.0028732 | 0.016314 | -0.014353 | -0.0072675 | 0.024462 | -0.0024374 | -18.5715 | -0.10529 | -121.7285 | -0.009155 | -121.0373 | -121.7651 | -121.8658 | -0.17853 | -0.004578 | -0.059509 | 0.013733 | -0.068665 | -0.10986 | 0.027466 | -0.004578 | -0.21973 | -0.1236 | 0.68665 | -0.14191 | -0.041199 | -0.13733 | -0.036621 | 121.6644 | -0.11902 | -0.10071 | 121.6553 | 121.7514 | 121.6141 | 0.086975 | -0.050354 | 0.69122 | 121.7194 | -0.009156 | 0.073242 | 121.6232 | 0.054931 | 121.6187 | 121.7194 | -121.843 | -0.17395 | 121.7148 | 121.7377 | 103.1525 | 121.5454
1429.8906 | 121.9025 | -121.7285 | 0.10071 | -0.009308 | 6.9752 | 0.064405 | 0.063006 | 0.0012092 | -0.0093183 | -0.0025806 | -0.012756 | 0.0033004 | 0.014605 | -0.011576 | -0.012181 | 0.022753 | -0.0054282 | -18.544 | -0.11902 | -121.7514 | 0.004578 | -121.0373 | -121.7331 | -121.8475 | -0.19226 | 0 | -0.045776 | -0.013733 | -0.041199 | -0.07782 | 0.027466 | -0.022888 | -0.21973 | -0.09613 | 0.69122 | -0.11902 | -0.004577 | -0.09613 | 0.018311 | 121.6827 | -0.10071 | -0.11444 | 121.6873 | 121.756 | 121.6507 | 0.073242 | -0.032044 | 0.71411 | 121.756 | 0.004577 | 0.032043 | 121.6324 | 0.045776 | 121.6095 | 121.7285 | -121.8521 | -0.14648 | 121.7331 | 121.7148 | 103.1845 | 121.5363
1431.5781 | 121.9528 | -121.7468 | 0.11902 | -0.009308 | 6.9774 | 0.066541 | 0.061297 | 0.0041998 | -0.0095319 | -0.0019396 | -0.0036011 | -0.0003312 | 0.015887 | -0.011149 | -0.0074811 | 0.024676 | -0.0041464 | -18.5028 | -0.1236 | -121.7331 | 0.064087 | -120.9641 | -121.6919 | -121.8109 | -0.091553 | -0.009155 | -0.013733 | 0.041199 | 0.018311 | -0.036621 | 0.07782 | 0.013733 | -0.24261 | -0.054932 | 0.78278 | -0.064087 | 0.054931 | -0.07782 | 0.041198 | 121.7331 | -0.12817 | -0.07782 | 121.7651 | 121.8246 | 121.7102 | 0.091553 | -0.022888 | 0.76904 | 121.7972 | 0.032044 | 0.054932 | 121.6095 | 0.004578 | 121.6232 | 121.7377 | -121.8521 | -0.13275 | 121.8109 | 121.788 | 103.244 | 121.6553
1433.3125 | 121.9757 | -121.701 | 0.11444 | -0.009308 | 6.9769 | 0.067823 | 0.064074 | 0.00185 | -0.0061139 | -0.0025806 | -0.0066527 | 0.000737 | 0.016314 | -0.0075174 | -0.0059857 | 0.025957 | -0.0052146 | -18.5074 | -0.15106 | -121.7194 | 0.073242 | -120.9457 | -121.6919 | -121.7926 | -0.09613 | -0.027466 | -0.022888 | 0.091553 | 0.027466 | -0.009155 | 0.07782 | -0.01831 | -0.2655 | -0.041199 | 0.75531 | -0.091553 | 0.009155 | -0.073243 | 0.027465 | 121.6782 | -0.14191 | -0.022888 | 121.7285 | 121.7789 | 121.6919 | 0.10071 | 0.013733 | 0.77362 | 121.7926 | 0.050354 | 0.11444 | 121.5683 | -0.004578 | 121.55 | 121.6736 | -121.8338 | -0.13733 | 121.7743 | 121.7926 | 103.1937 | 121.6049
1434.9844 | 121.9894 | -121.7056 | 0.086975 | -0.009308 | 6.9746 | 0.066328 | 0.061938 | 0.00056817 | -0.0086773 | -0.0036486 | -0.0066527 | 0.0009506 | 0.015887 | -0.0062356 | -0.0079083 | 0.026171 | 0.0016214 | -18.5349 | -0.14648 | -121.7331 | 0.064087 | -120.9686 | -121.6827 | -121.8018 | -0.10986 | -0.027466 | -0.022888 | 0.064087 | 0.050354 | 0.013733 | 0.09613 | -0.027466 | -0.23346 | -0.022888 | 0.737 | -0.096131 | 0.022888 | -0.068665 | 0.050354 | 121.6827 | -0.11444 | -0.022888 | 121.756 | 121.8018 | 121.7194 | 0.11902 | 0.036621 | 0.76447 | 121.7972 | 0.073242 | 0.086975 | 121.5866 | -0.004578 | 121.5591 | 121.6782 | -121.8201 | -0.10986 | 121.7697 | 121.7697 | 103.1708 | 121.5958
1436.7344 | 122.0123 | -121.6644 | 0.07782 | -0.0016785 | 6.9754 | 0.066541 | 0.064501 | -7.2628e-05 | -0.0050457 | -0.0010852 | -0.0036011 | 0.0030868 | 0.012683 | -0.0096536 | -0.0029949 | 0.024462 | -0.0028646 | -18.4296 | -0.14191 | -121.7239 | 0.12817 | -120.9137 | -121.669 | -121.7606 | -0.041199 | -0.022888 | -0.004578 | 0.14191 | 0.091553 | 0.032043 | 0.14191 | -0.059509 | -0.21973 | 0.050354 | 0.75073 | -0.09613 | -0.004577 | -0.036621 | 0.054932 | 121.6599 | -0.10071 | 0.064087 | 121.756 | 121.8063 | 121.6965 | 0.14649 | 0.036621 | 0.81024 | 121.8521 | 0.096131 | 0.14649 | 121.582 | -0.01831 | 121.5225 | 121.6415 | -121.8018 | -0.082398 | 121.7926 | 121.8063 | 103.2349 | 121.6232
1438.4844 | 121.9345 | -121.7239 | 0.091553 | -0.009308 | 6.9735 | 0.065901 | 0.064501 | 0.0039862 | -0.0054731 | -0.0021532 | 0.0025025 | 0.0020188 | 0.014819 | 0.0023092 | -0.0076947 | 0.023607 | -0.0022238 | -18.4937 | -0.10529 | -121.7606 | 0 | -121.0464 | -121.7743 | -121.8521 | -0.16479 | 0 | -0.041199 | 0.032043 | -0.032043 | -0.07782 | 0.054932 | -0.036621 | -0.19684 | -0.091553 | 0.67749 | -0.12817 | -0.050354 | -0.091553 | -0.013733 | 121.6827 | -0.091553 | -0.05951 | 121.6919 | 121.7789 | 121.6461 | 0.096131 | -0.036621 | 0.71411 | 121.7606 | 0.009156 | 0.073242 | 121.6553 | 0.041199 | 121.6187 | 121.7239 | -121.8521 | -0.13275 | 121.7239 | 121.756 | 103.2303 | 121.5591
1440.2344 | 122.0398 | -121.6827 | 0.10071 | -0.009308 | 6.9746 | 0.06761 | 0.063433 | 0.00035457 | -0.0054731 | -0.0012988 | -0.0036011 | 0.0026596 | 0.015674 | -0.0034586 | -0.0040631 | 0.026598 | -0.001583 | -18.4341 | -0.13733 | -121.7468 | 0.1236 | -120.9137 | -121.6599 | -121.7789 | -0.013733 | -0.032043 | -0.018311 | 0.13733 | 0.068665 | 0.027466 | 0.13275 | -0.064087 | -0.23804 | 0.022888 | 0.76904 | -0.096131 | 0.022888 | -0.032044 | 0.086975 | 121.6644 | -0.13275 | 0.036621 | 121.7514 | 121.8155 | 121.7102 | 0.15106 | 0.045777 | 0.83313 | 121.8704 | 0.086976 | 0.15564 | 121.6095 | -0.013732 | 121.5454 | 121.6507 | -121.8475 | -0.11902 | 121.8063 | 121.8201 | 103.2486 | 121.669
1441.9219 | 122.0169 | -121.7148 | 0.07782 | -0.016937 | 6.9752 | 0.064192 | 0.061511 | -0.001568 | -0.0050457 | -0.0040758 | -0.0066527 | 0.0020188 | 0.016742 | -0.0092264 | -0.0055585 | 0.025103 | 0.0011942 | -18.4296 | -0.16479 | -121.7102 | 0.1236 | -120.9 | -121.6644 | -121.7606 | -0.004578 | -0.022888 | -0.004578 | 0.1236 | 0.091553 | 0.027466 | 0.13275 | 0.004578 | -0.24261 | 0.045776 | 0.81482 | -0.045776 | 0.050354 | -0.050354 | 0.045776 | 121.7102 | -0.10071 | 0.045776 | 121.8063 | 121.8475 | 121.7422 | 0.13733 | 0.032044 | 0.81024 | 121.8338 | 0.096131 | 0.12817 | 121.5454 | -0.01831 | 121.55 | 121.6919 | -121.788 | -0.082398 | 121.8384 | 121.8384 | 103.2852 | 121.7102
1443.6719 | 122.0352 | -121.701 | 0.091553 | -0.009308 | 6.9739 | 0.068037 | 0.060229 | -0.00028623 | -0.0056867 | -0.00087163 | -0.00054933 | 0.004155 | 0.016314 | -0.004313 | -0.0089765 | 0.023607 | -8.7586e-05 | -18.3929 | -0.12817 | -121.756 | 0.10986 | -120.9091 | -121.6232 | -121.7377 | -0.036621 | -0.013733 | -0.018311 | 0.1236 | 0.091553 | 0.050354 | 0.14191 | -0.054931 | -0.21973 | 0.01831 | 0.79193 | -0.036621 | 0.07782 | 0.01831 | 0.13275 | 121.6827 | -0.10529 | 0.032043 | 121.7926 | 121.843 | 121.7514 | 0.16022 | 0.068665 | 0.84686 | 121.8658 | 0.10986 | 0.14191 | 121.6278 | 0.004578 | 121.5729 | 121.6873 | -121.8475 | -0.10986 | 121.8109 | 121.8246 | 103.3081 | 121.6644
1445.4219 | 121.9757 | -121.7285 | 0.086975 | -0.009308 | 6.9744 | 0.066114 | 0.062151 | 0.00099557 | -0.0063275 | -0.0036486 | -0.00054933 | 0.0015914 | 0.014178 | -0.0092264 | -0.0066265 | 0.025957 | -0.0088462 | -18.4067 | -0.14191 | -121.7056 | 0.09613 | -120.932 | -121.6873 | -121.8018 | -0.050354 | -0.045776 | -0.018311 | 0.086975 | 0.036621 | -0.004578 | 0.086975 | 0.022889 | -0.22888 | 0.009155 | 0.79651 | -0.073242 | 0.041199 | -0.096131 | 0.01831 | 121.7102 | -0.13275 | 0 | 121.7651 | 121.8155 | 121.7239 | 0.10529 | 0.013733 | 0.77362 | 121.8018 | 0.054932 | 0.10529 | 121.5637 | -0.027465 | 121.5866 | 121.6827 | -121.7926 | -0.10529 | 121.8246 | 121.8155 | 103.3218 | 121.6782
1447.0938 | 122.0215 | -121.701 | 0.073242 | -0.009308 | 6.9763 | 0.066541 | 0.065356 | 0.00078177 | -0.0041913 | -0.0021532 | -0.0036011 | 0.0030868 | 0.015033 | -0.008372 | -0.0023541 | 0.024035 | -0.0037192 | -18.306 | -0.15564 | -121.7606 | 0.13275 | -120.9137 | -121.6553 | -121.7651 | -0.027466 | -0.036621 | -0.013733 | 0.13733 | 0.086975 | 0.027466 | 0.15564 | -0.059509 | -0.22888 | 0.059509 | 0.78735 | -0.064087 | 0.045777 | -0.004578 | 0.10529 | 121.6873 | -0.10986 | 0.064087 | 121.788 | 121.8567 | 121.7285 | 0.16937 | 0.041199 | 0.84686 | 121.8933 | 0.10071 | 0.15106 | 121.6049 | -0.022888 | 121.5454 | 121.6644 | -121.8338 | -0.086975 | 121.8338 | 121.8384 | 103.3951 | 121.6736
1448.8438 | 122.0169 | -121.7148 | 0.073242 | -0.0016785 | 6.9761 | 0.06526 | 0.059374 | 0.0031318 | -0.0076093 | -0.0025806 | -0.0036011 | 0.0013778 | 0.015674 | -0.010722 | -0.0089765 | 0.022967 | -0.00051479 | -18.3014 | -0.15106 | -121.7377 | 0.15106 | -120.8862 | -121.6232 | -121.7331 | -0.027466 | -0.022888 | -0.013733 | 0.1236 | 0.09613 | 0.059509 | 0.13275 | -0.022888 | -0.2243 | 0.07782 | 0.82855 | -0.01831 | 0.091553 | 0.004578 | 0.11444 | 121.701 | -0.09613 | 0.050354 | 121.8109 | 121.8475 | 121.7743 | 0.14648 | 0.073242 | 0.85144 | 121.8887 | 0.10986 | 0.13733 | 121.5866 | -0.009155 | 121.5637 | 121.6919 | -121.8109 | -0.086975 | 121.8658 | 121.8384 | 103.4134 | 121.6873
1450.5781 | 122.0123 | -121.6827 | 0.086975 | -0.0016785 | 6.9748 | 0.066541 | 0.065356 | 0.0022772 | -0.0065411 | -0.0032214 | -0.0036011 | 0.0028732 | 0.015246 | -0.0045266 | -0.0053449 | 0.024462 | -0.0028646 | -18.3655 | -0.13733 | -121.7239 | 0.10529 | -120.9549 | -121.6782 | -121.7789 | -0.045776 | -0.027466 | -0.009155 | 0.14191 | 0.068665 | 0.027466 | 0.15564 | -0.041199 | -0.2243 | 0.018311 | 0.72784 | -0.096131 | 0.004577 | -0.054932 | 0.045776 | 121.6736 | -0.11444 | 0.054932 | 121.7514 | 121.8384 | 121.7102 | 0.16479 | 0.036621 | 0.76904 | 121.8292 | 0.07782 | 0.15106 | 121.5866 | -0.018311 | 121.5454 | 121.6553 | -121.8109 | -0.09613 | 121.788 | 121.8246 | 103.3173 | 121.637
1452.3125 | 122.0261 | -121.7468 | 0.091553 | 0.005951 | 6.975 | 0.06761 | 0.064074 | -0.0013544 | -0.0067547 | -0.005144 | -0.0066527 | 0.0009506 | 0.015887 | -0.0055948 | -0.0085491 | 0.026598 | -0.0013694 | -18.4204 | -0.13275 | -121.7468 | 0.073242 | -120.9641 | -121.669 | -121.7789 | -0.073242 | -0.027466 | -0.032043 | 0.10071 | 0.064087 | 0.032043 | 0.11902 | 0 | -0.2243 | -0.018311 | 0.78278 | -0.032044 | 0.07782 | -0.032044 | 0.07782 | 121.7148 | -0.11902 | 0.009155 | 121.8109 | 121.8658 | 121.7789 | 0.15106 | 0.064086 | 0.78278 | 121.8201 | 0.09613 | 0.13275 | 121.6141 | 0.004577 | 121.6141 | 121.7194 | -121.8384 | -0.1236 | 121.8201 | 121.8475 | 103.3264 | 121.6736
1453.9844 | 121.9574 | -121.7148 | 0.11902 | -0.024567 | 6.975 | 0.064619 | 0.062792 | 0.003559 | -0.0078229 | -0.00087163 | -0.0066527 | 0.004155 | 0.017383 | -0.013712 | -0.0066265 | 0.02318 | -0.0024374 | -18.3243 | -0.10071 | -121.7468 | 0.068665 | -120.9778 | -121.7194 | -121.8201 | -0.091553 | -0.013733 | -0.027466 | 0.050354 | 0.036621 | -0.032043 | 0.082397 | -0.032043 | -0.21973 | -0.050354 | 0.737 | -0.10529 | -0.004577 | -0.073242 | 0.027466 | 121.6873 | -0.13275 | -0.068665 | 121.7514 | 121.7972 | 121.6827 | 0.10986 | -0.004577 | 0.76904 | 121.8155 | 0.064087 | 0.07782 | 121.6461 | 0.013733 | 121.6141 | 121.701 | -121.8658 | -0.14649 | 121.7834 | 121.7651 | 103.3905 | 121.6232
1455.7188 | 121.962 | -121.7514 | 0.10986 | -0.009308 | 6.9742 | 0.066755 | 0.063433 | 0.0037726 | -0.0082501 | -0.0025806 | -0.00054933 | 0.002446 | 0.015887 | -0.012217 | -0.010258 | 0.023607 | -0.0062826 | -18.3151 | -0.10071 | -121.756 | 0.07782 | -120.9732 | -121.7056 | -121.8201 | -0.09613 | -0.013733 | -0.032043 | 0.068665 | 0.032043 | -0.018311 | 0.086975 | -0.004577 | -0.21057 | -0.032043 | 0.7782 | -0.068664 | 0.045777 | -0.064087 | 0.050354 | 121.7194 | -0.1236 | -0.041198 | 121.7834 | 121.8384 | 121.7331 | 0.11902 | 0.013732 | 0.78278 | 121.8338 | 0.064086 | 0.10071 | 121.6553 | 0.01831 | 121.6507 | 121.7377 | -121.8658 | -0.14191 | 121.8292 | 121.8201 | 103.4363 | 121.6553
1457.4531 | 121.907 | -121.7606 | 0.11902 | -0.009308 | 6.9746 | 0.065901 | 0.062151 | 0.0022772 | -0.0063275 | -0.00087163 | -0.00054933 | 0.0011642 | 0.015887 | -0.006663 | -0.011326 | 0.024035 | -0.0041464 | -18.3792 | -0.10071 | -121.7743 | 0 | -121.019 | -121.7606 | -121.8475 | -0.17853 | 0.009155 | -0.045776 | -0.018311 | -0.032043 | -0.073242 | 0.022888 | -0.013733 | -0.21973 | -0.11902 | 0.74158 | -0.086975 | 0 | -0.073242 | 0.013733 | 121.7148 | -0.10986 | -0.13733 | 121.7285 | 121.7834 | 121.6873 | 0.068664 | -0.027466 | 0.75531 | 121.7743 | 0.013733 | 0.027465 | 121.6736 | 0.054931 | 121.6599 | 121.7697 | -121.8933 | -0.16479 | 121.7606 | 121.7422 | 103.3813 | 121.582
1459.1875 | 121.9025 | -121.7697 | 0.13733 | -0.009308 | 6.9771 | 0.063337 | 0.061938 | -0.00028623 | -0.0084637 | -0.0042896 | -0.0036011 | 0.0033004 | 0.014819 | -0.01414 | -0.0089765 | 0.021898 | -0.0045736 | -18.3701 | -0.1236 | -121.7606 | 0.004578 | -121.0327 | -121.7422 | -121.8475 | -0.19226 | 0 | -0.027466 | -0.004578 | -0.032043 | -0.07782 | 0.027466 | 0.009155 | -0.26093 | -0.13275 | 0.737 | -0.07782 | 0.027465 | -0.086975 | 0.01831 | 121.7422 | -0.13733 | -0.14191 | 121.7377 | 121.7972 | 121.6919 | 0.054932 | -0.050354 | 0.72784 | 121.7651 | -0.004577 | 0.022888 | 121.637 | 0.027466 | 121.6461 | 121.7697 | -121.8979 | -0.16479 | 121.7743 | 121.7651 | 103.3997 | 121.5775
1460.8594 | 121.9254 | -121.7422 | 0.1236 | -0.009308 | 6.9756 | 0.066114 | 0.065569 | -0.00028623 | -0.0059003 | -0.0010852 | 0.0025025 | 0.0045822 | 0.017596 | -0.00944 | -0.0040631 | 0.025103 | -0.0039328 | -18.3655 | -0.10986 | -121.7651 | -0.013733 | -121.0739 | -121.7743 | -121.8658 | -0.1831 | 0.013733 | -0.027466 | 0 | -0.054932 | -0.10986 | 0.032043 | -0.022888 | -0.23346 | -0.13733 | 0.66833 | -0.1236 | -0.032043 | -0.10071 | -0.009155 | 121.7148 | -0.10986 | -0.1236 | 121.6873 | 121.7743 | 121.6324 | 0.059509 | -0.082397 | 0.69122 | 121.7514 | -0.027466 | 0.027466 | 121.6553 | 0.041199 | 121.6324 | 121.756 | -121.8887 | -0.15106 | 121.7285 | 121.7422 | 103.3768 | 121.5591
1462.6094 | 121.9574 | -121.7743 | 0.12817 | -0.009308 | 6.9748 | 0.066541 | 0.063006 | 0.0022772 | -0.0076093 | -0.0012988 | -0.0036011 | 0.0026596 | 0.01546 | -0.011576 | -0.0083355 | 0.022967 | -8.7586e-05 | -18.3014 | -0.10529 | -121.756 | 0.07782 | -120.9778 | -121.701 | -121.8338 | -0.086975 | -0.009155 | -0.027466 | 0.041199 | 0.009155 | -0.050354 | 0.07782 | 0.018311 | -0.23346 | -0.050354 | 0.79651 | -0.059509 | 0.073242 | -0.07782 | 0.054931 | 121.7468 | -0.13733 | -0.086975 | 121.7834 | 121.8521 | 121.7239 | 0.10529 | -0.022888 | 0.7782 | 121.8338 | 0.036621 | 0.068665 | 121.6507 | 0.018311 | 121.669 | 121.7651 | -121.8842 | -0.15564 | 121.8521 | 121.8155 | 103.4729 | 121.6873
1464.3438 | 121.9208 | -121.7377 | 0.13733 | -0.009308 | 6.9748 | 0.068464 | 0.06386 | 0.0020636 | -0.0059003 | -0.0010852 | -0.0066527 | 0.0022324 | 0.014605 | -0.011363 | -0.0061993 | 0.023394 | -0.0037192 | -18.4158 | -0.10071 | -121.7697 | -0.032043 | -121.0876 | -121.8063 | -121.907 | -0.20599 | 0.018311 | -0.036621 | 0.018311 | -0.054932 | -0.10986 | 0.027466 | -0.032043 | -0.23804 | -0.16937 | 0.65002 | -0.16937 | -0.068664 | -0.13733 | -0.036621 | 121.7011 | -0.11902 | -0.11902 | 121.6827 | 121.7651 | 121.6278 | 0.064087 | -0.073242 | 0.68207 | 121.7377 | -0.018311 | 0.054932 | 121.669 | 0.054932 | 121.637 | 121.756 | -121.907 | -0.17395 | 121.7056 | 121.756 | 103.3218 | 121.5317
1466.0156 | 122.0398 | -121.701 | 0.086975 | -0.016937 | 6.9774 | 0.066755 | 0.063006 | -0.0019952 | -0.0048321 | -0.00044443 | -0.0066527 | 0.0011642 | 0.016528 | -0.0064494 | -0.0047039 | 0.02553 | -0.0024374 | -18.3014 | -0.13275 | -121.7239 | 0.11444 | -120.9274 | -121.6736 | -121.7834 | -0.009155 | -0.045776 | 0.004578 | 0.14191 | 0.086975 | 0.045776 | 0.15106 | -0.022888 | -0.21973 | 0.027466 | 0.77362 | -0.082397 | 0.027466 | -0.059509 | 0.050354 | 121.7056 | -0.13275 | 0.054932 | 121.788 | 121.8521 | 121.7468 | 0.14648 | 0.041198 | 0.79651 | 121.8384 | 0.082397 | 0.13733 | 121.5912 | -0.050354 | 121.5683 | 121.6553 | -121.8109 | -0.082397 | 121.8155 | 121.843 | 103.3997 | 121.6919
1467.75 | 121.907 | -121.7606 | 0.11902 | 0.005951 | 6.9771 | 0.066969 | 0.063006 | -0.0051996 | -0.0063275 | -0.0012988 | -0.0036011 | 0.0011642 | 0.014605 | -0.013285 | -0.0089765 | 0.022539 | -0.00030119 | -18.2968 | -0.1236 | -121.7697 | 0.027466 | -120.9961 | -121.7102 | -121.8292 | -0.15564 | 0.004578 | -0.032043 | 0 | -0.022888 | -0.054932 | 0.027466 | -0.009155 | -0.24261 | -0.091553 | 0.76447 | -0.068665 | 0.050354 | -0.05951 | 0.059509 | 121.7285 | -0.11444 | -0.11902 | 121.7377 | 121.788 | 121.7056 | 0.059509 | -0.022889 | 0.77362 | 121.7972 | 0.009155 | 0.032043 | 121.6461 | 0.036621 | 121.637 | 121.7651 | -121.8887 | -0.15106 | 121.788 | 121.7606 | 103.4637 | 121.6049
1469.4844 | 121.9986 | -121.7331 | 0.091553 | -0.016937 | 6.9759 | 0.066755 | 0.061511 | -0.00092703 | -0.0065411 | -0.00044443 | -0.0036011 | 0.0020188 | 0.017383 | -0.0087992 | -0.0098309 | 0.024676 | -0.0039328 | -18.2739 | -0.14191 | -121.7422 | 0.1236 | -120.9137 | -121.6415 | -121.7514 | -0.041199 | -0.032043 | -0.009155 | 0.07782 | 0.07782 | 0.036621 | 0.10986 | -0.009156 | -0.23346 | 0.032043 | 0.8194 | -0.018311 | 0.091552 | -0.009155 | 0.10071 | 121.7239 | -0.1236 | -0.013733 | 121.8109 | 121.843 | 121.7697 | 0.11902 | 0.045776 | 0.82855 | 121.8658 | 0.086975 | 0.086975 | 121.6003 | -0.022888 | 121.5912 | 121.701 | -121.8338 | -0.10071 | 121.8567 | 121.8109 | 103.4592 | 121.6919
1471.2188 | 121.9437 | -121.7606 | 0.11444 | -0.024567 | 6.9778 | 0.065046 | 0.063006 | 0.0037726 | -0.0097455 | -0.0010852 | -0.0036011 | 0.0033004 | 0.013751 | -0.016703 | -0.0068403 | 0.023821 | 0.0011942 | -18.251 | -0.10529 | -121.7514 | 0.004578 | -121.0373 | -121.7377 | -121.843 | -0.16022 | 0.009155 | -0.032043 | 0.032043 | 0 | -0.050354 | 0.059509 | 0.009155 | -0.21973 | -0.10986 | 0.72327 | -0.082398 | 0.022888 | -0.091553 | 0.013733 | 121.7285 | -0.10529 | -0.082398 | 121.7606 | 121.8201 | 121.7102 | 0.091552 | -0.018311 | 0.71411 | 121.756 | 0.032043 | 0.064086 | 121.6461 | 0.041198 | 121.6553 | 121.7697 | -121.8658 | -0.14648 | 121.7651 | 121.7926 | 103.5095 | 121.6003
1472.9062 | 122.0444 | -121.6827 | 0.064087 | -0.009308 | 6.9759 | 0.066328 | 0.061724 | -0.0017816 | -0.0031231 | -0.0019396 | -0.0036011 | -0.0016128 | 0.016742 | -0.010508 | -0.0025677 | 0.026385 | -0.001583 | -18.2785 | -0.15106 | -121.7102 | 0.12817 | -120.9091 | -121.6599 | -121.7789 | -0.009155 | -0.018311 | 0.009155 | 0.15106 | 0.09613 | 0.032043 | 0.15106 | -0.027466 | -0.21515 | 0.064087 | 0.77362 | -0.096131 | 0.022888 | -0.068665 | 0.050354 | 121.6919 | -0.082398 | 0.086975 | 121.7789 | 121.8338 | 121.7148 | 0.14191 | 0.022888 | 0.80109 | 121.8384 | 0.086975 | 0.14191 | 121.5591 | -0.027466 | 121.5317 | 121.6644 | -121.7743 | -0.054932 | 121.8109 | 121.8338 | 103.4042 | 121.6736
1474.6406 | 121.9025 | -121.7834 | 0.12817 | -0.0016785 | 6.9754 | 0.065687 | 0.064288 | 0.0033454 | -0.0069683 | -0.0042896 | -0.0036011 | 0.004155 | 0.017383 | -0.010295 | -0.0049175 | 0.025316 | 0.00033961 | -18.2922 | -0.11444 | -121.7651 | -0.022888 | -121.0876 | -121.8109 | -121.9025 | -0.1831 | 0 | -0.045776 | 0.009155 | -0.054932 | -0.11444 | 0.036621 | 0.01831 | -0.24262 | -0.15106 | 0.6958 | -0.11902 | -0.027466 | -0.13733 | -0.045776 | 121.7377 | -0.12817 | -0.11902 | 121.7285 | 121.8201 | 121.669 | 0.082397 | -0.068665 | 0.67749 | 121.7422 | -0.009156 | 0.054931 | 121.6507 | 0.045776 | 121.669 | 121.7834 | -121.8933 | -0.17395 | 121.7606 | 121.7926 | 103.4912 | 121.6003
1476.3125 | 121.9208 | -121.756 | 0.1236 | -0.0016785 | 6.9784 | 0.065901 | 0.062365 | 0.00185 | -0.0054731 | -0.00087163 | -0.0036011 | 0.0037278 | 0.017383 | -0.0090128 | -0.0055585 | 0.024462 | -0.0073508 | -18.3105 | -0.091553 | -121.7651 | -0.009155 | -121.0693 | -121.7926 | -121.875 | -0.18768 | 0.013733 | -0.041199 | 0.013733 | -0.054932 | -0.082397 | 0.050354 | -0.009156 | -0.21515 | -0.13275 | 0.68664 | -0.11902 | -0.036622 | -0.10986 | -0.027466 | 121.7148 | -0.10986 | -0.10986 | 121.701 | 121.8063 | 121.6736 | 0.091553 | -0.041198 | 0.6958 | 121.756 | -0.013733 | 0.054932 | 121.6736 | 0.054932 | 121.6644 | 121.7697 | -121.8887 | -0.16479 | 121.7468 | 121.7697 | 103.4454 | 121.5683
1478.0625 | 121.9711 | -121.7377 | 0.091553 | -0.009308 | 6.9774 | 0.065046 | 0.06322 | 0.0012092 | -0.0061139 | -0.0021532 | -0.00054933 | 0.003514 | 0.015246 | -0.017558 | -0.0068403 | 0.024462 | -0.0047874 | -18.2053 | -0.10986 | -121.7606 | 0.073242 | -120.9778 | -121.701 | -121.8246 | -0.07782 | 0.004578 | -0.004578 | 0.054932 | 0.009155 | -0.032043 | 0.073242 | -0.022888 | -0.20142 | -0.018311 | 0.75989 | -0.086975 | 0.036621 | -0.064087 | 0.059509 | 121.7331 | -0.086975 | -0.036621 | 121.7468 | 121.8109 | 121.7056 | 0.07782 | -0.027465 | 0.78278 | 121.8338 | 0.013733 | 0.05951 | 121.6507 | 0.009156 | 121.6278 | 121.7422 | -121.8521 | -0.096131 | 121.8109 | 121.7926 | 103.5324 | 121.6599
1479.8125 | 122.0123 | -121.7148 | 0.091553 | -0.009308 | 6.9767 | 0.067823 | 0.061724 | 0.0014228 | -0.0056867 | -0.00044443 | 0.0025025 | 0.0009506 | 0.013324 | -0.013499 | -0.0061993 | 0.024462 | -0.0020102 | -18.2053 | -0.15106 | -121.7285 | 0.11902 | -120.9 | -121.6415 | -121.756 | -0.022888 | -0.036621 | -0.004578 | 0.11902 | 0.11444 | 0.059509 | 0.13733 | -0.013733 | -0.24261 | 0.027466 | 0.81482 | -0.041198 | 0.073242 | -0.027465 | 0.086975 | 121.7102 | -0.12817 | 0.027466 | 121.8292 | 121.8521 | 121.7743 | 0.14191 | 0.064087 | 0.82855 | 121.8475 | 0.11902 | 0.1236 | 121.5775 | -0.032043 | 121.5637 | 121.6782 | -121.8201 | -0.096131 | 121.8338 | 121.8338 | 103.5095 | 121.6919
1481.5 | 121.9391 | -121.7606 | 0.1236 | -0.009308 | 6.9769 | 0.066969 | 0.061724 | -0.001568 | -0.0071821 | -0.0025806 | -0.0066527 | 0.0033004 | 0.015887 | -0.006663 | -0.0096173 | 0.023607 | -0.002651 | -18.1778 | -0.1236 | -121.7468 | 0.059509 | -120.9732 | -121.6965 | -121.8109 | -0.12817 | -0.009155 | -0.018311 | 0.018311 | -0.004578 | -0.064087 | 0.032043 | 0.013733 | -0.24719 | -0.064087 | 0.78735 | -0.050354 | 0.064087 | -0.064087 | 0.050354 | 121.7422 | -0.13275 | -0.10528 | 121.756 | 121.7926 | 121.6965 | 0.050354 | -0.045776 | 0.77362 | 121.8063 | 0.013733 | 0.036622 | 121.6232 | 0.009156 | 121.637 | 121.7514 | -121.8704 | -0.14191 | 121.8201 | 121.7789 | 103.5828 | 121.6324
1483.25 | 121.9345 | -121.7606 | 0.11444 | -0.016937 | 6.9784 | 0.066541 | 0.061511 | -0.0017816 | -0.0073957 | -0.0045032 | -0.0036011 | -0.0001174 | 0.015033 | -0.012858 | -0.0091901 | 0.023607 | -0.0041464 | -18.2281 | -0.10071 | -121.7972 | -0.004578 | -121.0648 | -121.7514 | -121.8704 | -0.18768 | 0.018311 | -0.036621 | 0 | -0.013733 | -0.082397 | 0.050354 | -0.036621 | -0.21515 | -0.11902 | 0.6958 | -0.10986 | 0.009155 | -0.073242 | 0.045776 | 121.7239 | -0.09613 | -0.11444 | 121.7468 | 121.8109 | 121.6782 | 0.086975 | -0.045776 | 0.73242 | 121.7926 | 0.022888 | 0.036621 | 121.6965 | 0.054932 | 121.6599 | 121.7789 | -121.9116 | -0.15106 | 121.756 | 121.7606 | 103.5324 | 121.5729
1484.9375 | 121.9757 | -121.7697 | 0.10071 | -0.0016785 | 6.9739 | 0.066114 | 0.06621 | 0.0031318 | -0.0078229 | -0.002367 | -0.0036011 | 0.0030868 | 0.01546 | -0.011149 | -0.0057721 | 0.024889 | -0.0056418 | -18.2327 | -0.10529 | -121.7697 | 0.009155 | -121.0419 | -121.788 | -121.8704 | -0.13275 | 0.004578 | -0.027466 | 0.050354 | -0.013733 | -0.050354 | 0.073242 | 0 | -0.20599 | -0.091553 | 0.72784 | -0.10071 | -0.018311 | -0.10071 | -0.018311 | 121.7422 | -0.09613 | -0.050354 | 121.756 | 121.843 | 121.7194 | 0.10071 | -0.022888 | 0.72784 | 121.7789 | 0.013733 | 0.07782 | 121.6644 | 0.032044 | 121.6644 | 121.7743 | -121.8704 | -0.12817 | 121.7789 | 121.8201 | 103.537 | 121.637
1486.6875 | 121.994 | -121.7148 | 0.091553 | -0.024567 | 6.9752 | 0.066328 | 0.061511 | -7.2628e-05 | -0.0052595 | -0.0019396 | -0.0036011 | 0.0003098 | 0.017169 | -0.006663 | -0.0061993 | 0.025103 | -0.00094199 | -18.2373 | -0.1236 | -121.7422 | 0.064087 | -120.9824 | -121.7102 | -121.7972 | -0.09613 | -0.027466 | -0.022888 | 0.07782 | 0.050354 | -0.004578 | 0.10071 | -0.027466 | -0.21515 | -0.027466 | 0.73242 | -0.082397 | 0.004578 | -0.054931 | 0.032044 | 121.6919 | -0.11902 | -0.013733 | 121.7651 | 121.8155 | 121.7102 | 0.1236 | 0.01831 | 0.75989 | 121.8063 | 0.073242 | 0.10071 | 121.6187 | -0.004578 | 121.5912 | 121.6873 | -121.8338 | -0.11444 | 121.7789 | 121.7926 | 103.4775 | 121.6187
1488.4219 | 122.0673 | -121.701 | 0.086975 | -0.009308 | 6.9765 | 0.067182 | 0.060656 | -0.0058404 | -0.0093183 | -0.002367 | -0.00054933 | 0.0005234 | 0.016101 | -0.0036722 | -0.0085491 | 0.026598 | -0.001583 | -18.1961 | -0.15106 | -121.7606 | 0.13275 | -120.8908 | -121.6324 | -121.7468 | 0.022888 | -0.027466 | -0.004578 | 0.14191 | 0.13275 | 0.086975 | 0.16479 | -0.059509 | -0.23804 | 0.045776 | 0.81024 | -0.045776 | 0.068665 | 0.013733 | 0.12817 | 121.6965 | -0.11444 | 0.054932 | 121.8338 | 121.8658 | 121.788 | 0.16937 | 0.091553 | 0.86975 | 121.8933 | 0.13733 | 0.14649 | 121.6095 | -0.022888 | 121.55 | 121.6736 | -121.8475 | -0.091553 | 121.8338 | 121.843 | 103.5049 | 121.7239
1490.0938 | 121.9025 | -121.7606 | 0.11902 | -0.009308 | 6.9799 | 0.067182 | 0.065569 | 0.006336 | -0.0061139 | -0.0036486 | -0.0036011 | 0.0020188 | 0.014819 | -0.006022 | -0.0076947 | 0.024889 | -0.0028646 | -18.2465 | -0.11444 | -121.7926 | 0.009155 | -121.0464 | -121.7926 | -121.8933 | -0.16937 | 0.018311 | -0.018311 | 0.018311 | -0.050354 | -0.10071 | 0.050354 | -0.032044 | -0.23346 | -0.10986 | 0.71411 | -0.13275 | -0.032044 | -0.10071 | 0 | 121.7422 | -0.10071 | -0.10071 | 121.7102 | 121.8109 | 121.6599 | 0.068665 | -0.082397 | 0.74616 | 121.8018 | -0.032043 | 0.036622 | 121.6782 | 0.036622 | 121.6461 | 121.7789 | -121.9116 | -0.13733 | 121.7697 | 121.7789 | 103.5141 | 121.5912
1491.8281 | 121.9391 | -121.7514 | 0.10986 | -0.016937 | 6.9791 | 0.066541 | 0.064501 | -0.0013544 | -0.0093183 | -0.00065803 | -0.0036011 | 0.002446 | 0.015887 | -0.0096536 | -0.0044903 | 0.024462 | -0.0028646 | -18.1778 | -0.13733 | -121.7514 | 0.054932 | -121.0052 | -121.7285 | -121.843 | -0.10529 | 0.018311 | -0.013733 | 0.032043 | -0.018311 | -0.064087 | 0.054932 | 0 | -0.24719 | -0.054931 | 0.74615 | -0.091553 | 0.022888 | -0.091553 | 0.022888 | 121.7377 | -0.091552 | -0.07782 | 121.7331 | 121.8063 | 121.6873 | 0.068665 | -0.050354 | 0.74615 | 121.8063 | -0.004578 | 0.045776 | 121.6141 | 0.032044 | 121.6141 | 121.7697 | -121.8613 | -0.1236 | 121.8063 | 121.7834 | 103.5736 | 121.6461
1493.5625 | 121.9757 | -121.7102 | 0.10986 | -0.009308 | 6.9765 | 0.066755 | 0.063433 | 0.0041998 | -0.0067547 | -0.0012988 | -0.00054933 | 0.0020188 | 0.016528 | -0.0096536 | -0.0074811 | 0.023821 | -0.0024374 | -18.1503 | -0.11444 | -121.7789 | 0.068665 | -120.9824 | -121.7285 | -121.8246 | -0.07782 | 0.004578 | -0.004578 | 0.073242 | 0.050354 | -0.013733 | 0.09613 | -0.068665 | -0.2243 | -0.041198 | 0.72784 | -0.11444 | -0.018311 | -0.045776 | 0.050354 | 121.7056 | -0.10529 | -0.036621 | 121.7606 | 121.8063 | 121.6965 | 0.10071 | -0.009155 | 0.79651 | 121.8475 | 0.054932 | 0.07782 | 121.6644 | 0.009156 | 121.5958 | 121.7148 | -121.8887 | -0.11444 | 121.7789 | 121.7834 | 103.5599 | 121.6324
1495.2969 | 122.0673 | -121.7468 | 0.073242 | -0.016937 | 6.9763 | 0.065901 | 0.060229 | 0.0024908 | -0.0069683 | -0.0021532 | -0.00054933 | -0.0007584 | 0.016314 | -0.012644 | -0.0059857 | 0.024248 | -0.002651 | -18.132 | -0.14191 | -121.7697 | 0.13275 | -120.8908 | -121.6232 | -121.7422 | 0 | -0.018311 | 0.004578 | 0.1236 | 0.12817 | 0.086975 | 0.12817 | -0.022888 | -0.21515 | 0.059509 | 0.85602 | 0.004577 | 0.1236 | 0.027465 | 0.14648 | 121.7514 | -0.091553 | 0.050354 | 121.875 | 121.875 | 121.8338 | 0.1236 | 0.082397 | 0.87891 | 121.9025 | 0.1236 | 0.11902 | 121.6278 | -0.022889 | 121.6049 | 121.7285 | -121.843 | -0.068664 | 121.8796 | 121.8704 | 103.6148 | 121.7468
1496.9844 | 122.0352 | -121.7468 | 0.10071 | -0.009308 | 6.975 | 0.066969 | 0.060656 | -0.00092703 | -0.0071821 | -0.0015124 | -0.0036011 | 0.000737 | 0.016101 | -0.0028178 | -0.0044903 | 0.024889 | -0.0024374 | -18.2373 | -0.14648 | -121.7697 | 0.07782 | -120.9641 | -121.6919 | -121.7926 | -0.068665 | -0.013733 | -0.018311 | 0.10529 | 0.073242 | 0.059509 | 0.13733 | -0.022888 | -0.24719 | -0.022888 | 0.78278 | -0.045777 | 0.054931 | -0.022889 | 0.077819 | 121.7285 | -0.11444 | 0.004578 | 121.8201 | 121.8842 | 121.8063 | 0.15564 | 0.07782 | 0.80566 | 121.8475 | 0.091553 | 0.1236 | 121.6232 | 0.004578 | 121.6003 | 121.7331 | -121.8704 | -0.11902 | 121.8246 | 121.8521 | 103.5095 | 121.6782
1498.7344 | 122.081 | -121.7239 | 0.091553 | -0.009308 | 6.9761 | 0.066541 | 0.061083 | -0.001568 | -0.0080365 | -0.0025806 | -0.0036011 | -0.0007584 | 0.015674 | -0.0053812 | -0.0081219 | 0.023607 | -0.0022238 | -18.1503 | -0.13733 | -121.7285 | 0.13733 | -120.9 | -121.6187 | -121.7285 | 0.032043 | -0.027466 | -0.004578 | 0.13275 | 0.1236 | 0.068665 | 0.13733 | -0.004578 | -0.22888 | 0.045776 | 0.82398 | -0.004578 | 0.10529 | 0 | 0.10986 | 121.7194 | -0.11902 | 0.041198 | 121.8475 | 121.8613 | 121.7926 | 0.14191 | 0.073243 | 0.82855 | 121.8658 | 0.12817 | 0.13733 | 121.5912 | -0.022888 | 121.5866 | 121.6965 | -121.8201 | -0.096131 | 121.8613 | 121.8567 | 103.5736 | 121.756
1500.4844 | 122.0581 | -121.7148 | 0.10071 | -0.009308 | 6.9744 | 0.066541 | 0.061511 | 0.0033454 | -0.0078229 | -1.7026e-05 | -0.0066527 | -0.0007584 | 0.015674 | -0.0073038 | -0.0089765 | 0.025744 | -0.00436 | -18.1549 | -0.13275 | -121.7514 | 0.15564 | -120.8817 | -121.6141 | -121.7285 | 0.004578 | -0.022888 | 0.013733 | 0.12817 | 0.12817 | 0.073242 | 0.14648 | -0.036621 | -0.23346 | 0.054932 | 0.83313 | -0.013733 | 0.10071 | 0.022888 | 0.13733 | 121.7285 | -0.1236 | 0.027466 | 121.843 | 121.8613 | 121.788 | 0.13275 | 0.059509 | 0.86975 | 121.907 | 0.11444 | 0.11444 | 121.6187 | -0.036621 | 121.582 | 121.6919 | -121.8521 | -0.086975 | 121.8704 | 121.843 | 103.5599 | 121.7194
1502.2344 | 122.0032 | -121.7514 | 0.09613 | -0.009308 | 6.9742 | 0.064405 | 0.060656 | 0.00014097 | -0.0050457 | -0.0025806 | -0.0066527 | -0.0005448 | 0.013751 | -0.00944 | -0.0083355 | 0.024676 | -0.0024374 | -18.2053 | -0.15564 | -121.7651 | 0.064087 | -120.9915 | -121.7194 | -121.8246 | -0.10529 | -0.009155 | -0.004578 | 0.068665 | 0.032043 | 0 | 0.082397 | -0.013733 | -0.25177 | -0.032043 | 0.75989 | -0.073242 | 0.032044 | -0.059509 | 0.045777 | 121.7468 | -0.10528 | -0.027465 | 121.7834 | 121.8338 | 121.7514 | 0.086975 | 0.004578 | 0.77362 | 121.8292 | 0.036621 | 0.073243 | 121.6095 | -0.004577 | 121.5958 | 121.7422 | -121.8613 | -0.10071 | 121.8155 | 121.8201 | 103.5461 | 121.6461
1503.9219 | 121.9254 | -121.7651 | 0.1236 | -0.0016785 | 6.9784 | 0.066541 | 0.064929 | -0.0051996 | -0.0073957 | -0.005144 | -0.0097045 | 0.0020188 | 0.014819 | -0.013926 | -0.0089765 | 0.023394 | -0.0039328 | -18.1686 | -0.13275 | -121.788 | 0.004578 | -121.0739 | -121.756 | -121.8704 | -0.18768 | 0.004578 | -0.041199 | 0.018311 | -0.032043 | -0.07782 | 0.041199 | -0.022888 | -0.25635 | -0.11902 | 0.69122 | -0.10529 | 0.009156 | -0.082397 | 0.032044 | 121.7239 | -0.11902 | -0.10528 | 121.7331 | 121.8063 | 121.6873 | 0.082398 | -0.036621 | 0.71411 | 121.7926 | 0.009156 | 0.05951 | 121.6553 | 0.045777 | 121.6324 | 121.7697 | -121.9116 | -0.16479 | 121.7697 | 121.7834 | 103.5965 | 121.5775
1505.6719 | 121.9299 | -121.7743 | 0.14191 | -0.009308 | 6.9737 | 0.065473 | 0.06386 | -0.00049983 | -0.0076093 | -0.0025806 | -0.0066527 | 0.0030868 | 0.015887 | -0.012431 | -0.0087629 | 0.02083 | -0.0017966 | -18.1732 | -0.11444 | -121.7834 | 0.022888 | -121.0373 | -121.7697 | -121.843 | -0.16022 | 0.018311 | -0.027466 | -0.004578 | -0.041199 | -0.073242 | 0.013733 | -0.009155 | -0.25635 | -0.11902 | 0.737 | -0.068665 | 0.004578 | -0.05951 | 0.013733 | 121.7468 | -0.1236 | -0.14649 | 121.7331 | 121.788 | 121.7011 | 0.041199 | -0.045776 | 0.74616 | 121.8063 | -0.013733 | 0.022888 | 121.669 | 0.045777 | 121.6599 | 121.7926 | -121.9254 | -0.16937 | 121.7972 | 121.7697 | 103.6011 | 121.6141
1507.4219 | 121.9528 | -121.7789 | 0.11444 | -0.016937 | 6.975 | 0.064832 | 0.06322 | 0.0012092 | -0.0091047 | -0.0019396 | -0.0097045 | 0.0022324 | 0.015246 | -0.010722 | -0.0059857 | 0.022753 | -0.00094199 | -18.1274 | -0.11902 | -121.7743 | 0.004578 | -121.0602 | -121.7697 | -121.875 | -0.17853 | 0 | -0.022888 | 0.013733 | -0.022888 | -0.041199 | 0.041199 | 0.004578 | -0.23346 | -0.10986 | 0.71869 | -0.09613 | 0.009156 | -0.10071 | 0.004578 | 121.756 | -0.11444 | -0.10071 | 121.756 | 121.8201 | 121.7377 | 0.064087 | -0.018311 | 0.71411 | 121.7789 | 0 | 0.036621 | 121.6553 | 0.022888 | 121.6599 | 121.7789 | -121.8887 | -0.13733 | 121.7834 | 121.7926 | 103.6514 | 121.6003
1509.1094 | 121.9116 | -121.7285 | 0.12817 | -0.016937 | 6.9771 | 0.065901 | 0.064501 | 0.0039862 | -0.0048321 | -0.0012988 | -0.0036011 | 0.0039414 | 0.015887 | -0.007731 | -0.0066265 | 0.022539 | -0.003292 | -18.1686 | -0.10986 | -121.788 | -0.009155 | -121.0876 | -121.8109 | -121.9162 | -0.19684 | 0.022888 | -0.050354 | 0.013733 | -0.050354 | -0.09613 | 0.041199 | -0.059509 | -0.23804 | -0.13733 | 0.64087 | -0.18768 | -0.082397 | -0.12817 | -0.022888 | 121.6782 | -0.10529 | -0.11444 | 121.6782 | 121.7697 | 121.6324 | 0.091553 | -0.045776 | 0.70038 | 121.7789 | 0 | 0.064087 | 121.6782 | 0.073242 | 121.6187 | 121.7514 | -121.9162 | -0.17853 | 121.7194 | 121.7422 | 103.5599 | 121.5317
1510.8438 | 121.9528 | -121.7468 | 0.11444 | -0.009308 | 6.9746 | 0.066969 | 0.059802 | -0.00071343 | -0.0095319 | -0.0049304 | -0.0066527 | 0.0015914 | 0.016742 | -0.0090128 | -0.0074811 | 0.023607 | -0.00072839 | -18.1458 | -0.13275 | -121.7606 | 0.086975 | -120.9549 | -121.6827 | -121.7834 | -0.086975 | -0.013733 | -0.013733 | 0.041199 | 0.018311 | -0.041199 | 0.050354 | -0.013733 | -0.24719 | -0.027466 | 0.79193 | -0.036621 | 0.064087 | -0.022888 | 0.07782 | 121.7331 | -0.12817 | -0.073242 | 121.7651 | 121.7972 | 121.7056 | 0.064087 | -0.027466 | 0.80566 | 121.8475 | 0.032044 | 0.054932 | 121.6278 | 0 | 121.6141 | 121.7331 | -121.875 | -0.12817 | 121.8338 | 121.788 | 103.6011 | 121.6599
1512.5781 | 122.0535 | -121.7239 | 0.07782 | 0.005951 | 6.9761 | 0.067823 | 0.060015 | -0.0037042 | -0.0067547 | -0.0027942 | 0.0055543 | -0.0011856 | 0.01546 | -0.00944 | -0.0085491 | 0.024676 | 0.00012601 | -18.1229 | -0.15106 | -121.7468 | 0.13275 | -120.9045 | -121.6324 | -121.7468 | 0 | -0.013733 | 0 | 0.1236 | 0.10529 | 0.064087 | 0.13733 | -0.022888 | -0.22888 | 0.054931 | 0.8194 | -0.022888 | 0.091553 | 0 | 0.11444 | 121.7239 | -0.091553 | 0.045776 | 121.8292 | 121.8613 | 121.788 | 0.13733 | 0.064087 | 0.84229 | 121.8796 | 0.10529 | 0.1236 | 121.5958 | -0.013733 | 121.5729 | 121.7102 | -121.8246 | -0.07782 | 121.8567 | 121.8475 | 103.6011 | 121.7239
1514.3281 | 121.9666 | -121.7422 | 0.13275 | -0.016937 | 6.9754 | 0.066328 | 0.062579 | 0.0044134 | -0.0059003 | -0.0021532 | -0.0066527 | 0.002446 | 0.015033 | -0.013072 | -0.0076947 | 0.023821 | -0.0047874 | -18.1549 | -0.11902 | -121.7972 | 0.004578 | -121.0648 | -121.756 | -121.8658 | -0.1831 | 0.018311 | -0.036621 | 0.013733 | -0.027466 | -0.059509 | 0.045776 | -0.054931 | -0.25177 | -0.12817 | 0.67749 | -0.1236 | -0.013732 | -0.068665 | 0.041199 | 121.7056 | -0.11444 | -0.11902 | 121.7148 | 121.788 | 121.6827 | 0.082397 | -0.022888 | 0.73242 | 121.8018 | 0.009155 | 0.050354 | 121.6782 | 0.054932 | 121.6232 | 121.7606 | -121.9299 | -0.16937 | 121.7468 | 121.756 | 103.5873 | 121.5591
1516 | 121.9528 | -121.7697 | 0.10071 | -0.0016785 | 6.9765 | 0.068464 | 0.062579 | -0.00071343 | -0.0086773 | 0.00062377 | -0.00054933 | 0.0033004 | 0.016528 | -0.015208 | -0.0040631 | 0.024035 | -0.001583 | -18.1595 | -0.10986 | -121.7651 | 0.041199 | -120.9961 | -121.7331 | -121.8384 | -0.09613 | 0.027466 | 0.009155 | 0.045776 | 0.004578 | -0.064087 | 0.059509 | 0.004577 | -0.21057 | -0.059509 | 0.77362 | -0.068665 | 0.036621 | -0.073242 | 0.032044 | 121.7789 | -0.073242 | -0.054932 | 121.7743 | 121.8292 | 121.7056 | 0.050354 | -0.073242 | 0.76904 | 121.8063 | -0.004577 | 0.036621 | 121.6553 | 0.018311 | 121.6599 | 121.7972 | -121.8658 | -0.091553 | 121.8109 | 121.8155 | 103.6102 | 121.6736
1517.75 | 121.9254 | -121.7651 | 0.13733 | -0.009308 | 6.9769 | 0.068037 | 0.063006 | 0.0039862 | -0.0063275 | -0.002367 | -0.0097045 | 0.0028732 | 0.015674 | -0.0038858 | -0.0053449 | 0.026598 | 0.0011942 | -18.1824 | -0.10986 | -121.7697 | -0.022888 | -121.0968 | -121.8063 | -121.9025 | -0.16937 | 0.022888 | -0.027466 | 0.018311 | -0.036621 | -0.086975 | 0.045776 | -0.004577 | -0.24719 | -0.16022 | 0.66833 | -0.13733 | -0.041198 | -0.13275 | -0.036621 | 121.7377 | -0.11444 | -0.11902 | 121.7285 | 121.8109 | 121.6782 | 0.073242 | -0.059509 | 0.67291 | 121.7468 | -0.009155 | 0.045777 | 121.6599 | 0.050354 | 121.6553 | 121.788 | -121.907 | -0.16479 | 121.7422 | 121.7834 | 103.5828 | 121.5958
1519.5 | 122.0352 | -121.7285 | 0.091553 | -0.0016785 | 6.9765 | 0.066328 | 0.06386 | 0.0016364 | -0.0048321 | -0.0015124 | 0.0025025 | 0.0003098 | 0.017596 | -0.0070902 | -0.0047039 | 0.024248 | -0.0028646 | -18.1549 | -0.11902 | -121.756 | 0.050354 | -121.0052 | -121.7331 | -121.8246 | -0.041199 | -0.018311 | 0 | 0.1236 | 0.064087 | 0.027466 | 0.14191 | -0.027465 | -0.21057 | -0.041199 | 0.72327 | -0.09613 | -0.004577 | -0.068665 | 0.022888 | 121.7285 | -0.10986 | 0.032043 | 121.7926 | 121.8704 | 121.756 | 0.14191 | 0.027466 | 0.75073 | 121.8063 | 0.064087 | 0.1236 | 121.637 | -0.018311 | 121.6095 | 121.7102 | -121.8475 | -0.091553 | 121.7789 | 121.8521 | 103.5736 | 121.6873
1521.1719 | 122.0581 | -121.7056 | 0.073242 | 0.005951 | 6.9765 | 0.06761 | 0.061297 | 0.0029182 | -0.0044049 | -0.00065803 | -0.00054933 | 0.0013778 | 0.014605 | -0.0053812 | -0.0059857 | 0.026171 | -0.0054282 | -18.0862 | -0.14191 | -121.7468 | 0.1236 | -120.9229 | -121.6827 | -121.7789 | 0 | -0.032043 | 0.013733 | 0.16479 | 0.091553 | 0.054932 | 0.14191 | -0.041199 | -0.21515 | 0.050354 | 0.78278 | -0.073243 | 0.022888 | -0.032044 | 0.064087 | 121.7194 | -0.10529 | 0.091553 | 121.7972 | 121.8475 | 121.7606 | 0.12817 | 0.041199 | 0.82397 | 121.8704 | 0.07782 | 0.15106 | 121.6049 | -0.045776 | 121.5637 | 121.6736 | -121.8201 | -0.059509 | 121.8292 | 121.8704 | 103.6194 | 121.7056
1522.9062 | 121.9162 | -121.7468 | 0.13275 | -0.0016785 | 6.9782 | 0.068037 | 0.065783 | 0.0014228 | -0.0069683 | -0.0049304 | -0.00054933 | 0.0026596 | 0.014819 | -0.013499 | -0.0072675 | 0.024889 | -0.001583 | -18.1 | -0.11902 | -121.7606 | -0.009155 | -121.0968 | -121.8201 | -121.9162 | -0.17853 | 0.022888 | -0.036621 | 0.004578 | -0.036621 | -0.086975 | 0.045776 | -0.013733 | -0.25177 | -0.14191 | 0.65002 | -0.16937 | -0.073242 | -0.15564 | -0.059509 | 121.7102 | -0.10986 | -0.12817 | 121.7102 | 121.7926 | 121.6599 | 0.082397 | -0.050354 | 0.66376 | 121.7514 | 0 | 0.041199 | 121.6415 | 0.059509 | 121.6278 | 121.7697 | -121.8933 | -0.16937 | 121.7377 | 121.7514 | 103.6469 | 121.5683
1524.6406 | 122.0627 | -121.7377 | 0.07782 | -0.024567 | 6.9761 | 0.067182 | 0.064288 | 0.005268 | -0.0039777 | -0.0025806 | -0.0036011 | 0.0022324 | 0.015246 | -0.011363 | -0.0036359 | 0.027666 | -0.0039328 | -18.0908 | -0.13733 | -121.7285 | 0.12817 | -120.9183 | -121.6736 | -121.7743 | 0.009155 | -0.027466 | 0.018311 | 0.15106 | 0.10986 | 0.050354 | 0.15106 | 0.009155 | -0.21515 | 0.050354 | 0.8194 | -0.036621 | 0.064087 | -0.045776 | 0.054932 | 121.756 | -0.10529 | 0.073242 | 121.8475 | 121.8887 | 121.788 | 0.13275 | 0.032043 | 0.81024 | 121.8567 | 0.091552 | 0.13275 | 121.5912 | -0.045777 | 121.6003 | 121.7102 | -121.8063 | -0.059509 | 121.8658 | 121.8887 | 103.6469 | 121.7468
1526.375 | 122.049 | -121.7102 | 0.10071 | -0.016937 | 6.9778 | 0.068037 | 0.063647 | -0.0017816 | -0.0050457 | -0.0019396 | -0.0036011 | 0.0013778 | 0.016528 | -0.0030314 | -0.0044903 | 0.02788 | -0.00030119 | -18.1229 | -0.1236 | -121.7834 | 0.082397 | -120.9686 | -121.7056 | -121.8063 | -0.027466 | -0.013733 | 0.004578 | 0.13733 | 0.09613 | 0.032043 | 0.15106 | -0.073242 | -0.2243 | -0.018311 | 0.74158 | -0.09613 | 0.004578 | -0.022888 | 0.07782 | 121.7148 | -0.11444 | 0.036621 | 121.8063 | 121.8613 | 121.7422 | 0.14648 | 0.027465 | 0.81482 | 121.8658 | 0.091552 | 0.13275 | 121.6599 | -0.018311 | 121.5866 | 121.6965 | -121.8842 | -0.09613 | 121.7926 | 121.8475 | 103.5873 | 121.6827
1528.0469 | 121.9894 | -121.7239 | 0.086975 | -0.009308 | 6.9746 | 0.066328 | 0.063006 | 0.00099557 | -0.0061139 | -0.003435 | -0.0066527 | 0.0022324 | 0.016742 | -0.01649 | -0.0070539 | 0.027025 | -0.005001 | -18.1274 | -0.091553 | -121.788 | 0.022888 | -121.0556 | -121.788 | -121.8613 | -0.12817 | 0.009155 | -0.022888 | 0.082397 | 0 | -0.032043 | 0.10071 | -0.064087 | -0.17853 | -0.064087 | 0.66833 | -0.13733 | -0.064087 | -0.073242 | 0 | 121.7011 | -0.07782 | -0.004578 | 121.7239 | 121.8246 | 121.6919 | 0.1236 | -0.009155 | 0.73242 | 121.8109 | 0.022888 | 0.10528 | 121.6965 | 0.032043 | 121.6324 | 121.7331 | -121.875 | -0.10986 | 121.7468 | 121.8063 | 103.5965 | 121.5958
1529.7969 | 122.0398 | -121.7285 | 0.10071 | -0.0016785 | 6.9752 | 0.066114 | 0.061724 | -0.0054132 | -0.0054731 | 0.00041017 | -0.00054933 | 0.0005234 | 0.015246 | -0.010935 | -0.0083355 | 0.027239 | -0.0030784 | -18.0954 | -0.12817 | -121.756 | 0.086975 | -120.9641 | -121.6827 | -121.7789 | -0.068665 | -0.027466 | -0.009155 | 0.10986 | 0.091553 | 0.068665 | 0.13733 | -0.027465 | -0.22888 | -0.013733 | 0.76447 | -0.050354 | 0.045777 | -0.022889 | 0.073242 | 121.7194 | -0.12817 | 0.009155 | 121.8201 | 121.8658 | 121.7972 | 0.14648 | 0.07782 | 0.79193 | 121.843 | 0.10071 | 0.11902 | 121.6278 | -0.018311 | 121.6003 | 121.701 | -121.8567 | -0.10986 | 121.8155 | 121.8384 | 103.6331 | 121.6599
1531.4688 | 121.9254 | -121.7514 | 0.11902 | -0.024567 | 6.9756 | 0.063551 | 0.062151 | -0.0017816 | -0.0071821 | -0.001726 | -0.00054933 | 0.0026596 | 0.014819 | -0.013499 | -0.012181 | 0.022326 | -0.00030119 | -18.0908 | -0.1236 | -121.7651 | 0.022888 | -121.0281 | -121.7422 | -121.8613 | -0.14648 | 0.018311 | -0.032043 | -0.004578 | -0.013733 | -0.059509 | 0.036621 | -0.013733 | -0.24261 | -0.096131 | 0.72327 | -0.10986 | 0.009155 | -0.09613 | 0.022888 | 121.7194 | -0.10071 | -0.1236 | 121.7377 | 121.788 | 121.6919 | 0.068664 | -0.027466 | 0.737 | 121.788 | 0.01831 | 0.027465 | 121.6415 | 0.050354 | 121.6278 | 121.7697 | -121.8842 | -0.15106 | 121.7743 | 121.7468 | 103.6606 | 121.6049
1533.2031 | 121.9757 | -121.7377 | 0.13733 | -0.009308 | 6.9776 | 0.066328 | 0.064074 | 0.0033454 | -0.0073957 | -0.0032214 | -0.0036011 | 0.0030868 | 0.016314 | -0.012217 | -0.0083355 | 0.023394 | -0.0054282 | -18.0313 | -0.10529 | -121.7834 | 0.073242 | -120.9869 | -121.7148 | -121.8246 | -0.064087 | 0.004578 | -0.004578 | 0.068665 | 0.032043 | -0.013733 | 0.086975 | -0.045776 | -0.24262 | -0.064087 | 0.75073 | -0.086975 | 0.022888 | -0.041199 | 0.068664 | 121.7331 | -0.13275 | -0.068664 | 121.7697 | 121.8246 | 121.7239 | 0.091553 | -0.009155 | 0.79651 | 121.8567 | 0.036621 | 0.073243 | 121.6782 | 0.009156 | 121.6324 | 121.7422 | -121.9208 | -0.14191 | 121.8109 | 121.8063 | 103.7064 | 121.6736
1534.9531 | 122.0581 | -121.701 | 0.073242 | -0.0016785 | 6.9763 | 0.06825 | 0.063006 | 0.00035457 | -0.0033369 | -0.0045032 | -0.0036011 | 0.0020188 | 0.015033 | -0.010295 | -0.0042767 | 0.023607 | -0.0011558 | -18.1 | -0.11902 | -121.7331 | 0.10986 | -120.9229 | -121.6965 | -121.7834 | -0.018311 | -0.018311 | 0.013733 | 0.13733 | 0.09613 | 0.050354 | 0.16022 | -0.032043 | -0.19226 | 0.036621 | 0.7782 | -0.082397 | 0.004578 | -0.050354 | 0.036621 | 121.7148 | -0.091553 | 0.064087 | 121.7972 | 121.8613 | 121.7514 | 0.14648 | 0.036621 | 0.81024 | 121.843 | 0.082397 | 0.1236 | 121.6141 | -0.032044 | 121.582 | 121.6827 | -121.8063 | -0.059509 | 121.8109 | 121.8384 | 103.6011 | 121.6827
1536.6875 | 121.9299 | -121.7606 | 0.1236 | -0.009308 | 6.9786 | 0.066969 | 0.06386 | 0.0014228 | -0.0065411 | -0.003435 | -0.0036011 | 0.004155 | 0.016528 | -0.0090128 | -0.0061993 | 0.02553 | -0.0047874 | -18.0954 | -0.10071 | -121.7697 | 0 | -121.0602 | -121.788 | -121.8979 | -0.14648 | 0.013733 | -0.041199 | 0.027466 | -0.036621 | -0.086975 | 0.073242 | -0.009155 | -0.2243 | -0.1236 | 0.70038 | -0.13733 | -0.027466 | -0.12817 | -0.018311 | 121.7194 | -0.10986 | -0.09613 | 121.7239 | 121.8338 | 121.6736 | 0.11444 | -0.045776 | 0.70953 | 121.7697 | 0.004578 | 0.068665 | 121.669 | 0.054932 | 121.6599 | 121.7743 | -121.8933 | -0.16479 | 121.7606 | 121.788 | 103.6652 | 121.6141
1538.4219 | 121.9254 | -121.756 | 0.10529 | 0.005951 | 6.9756 | 0.068037 | 0.06322 | 0.0037726 | -0.0080365 | -0.0027942 | -0.0036011 | 0.0045822 | 0.014819 | -0.012431 | -0.0051313 | 0.024248 | -0.00030119 | -18.1091 | -0.10071 | -121.788 | -0.013733 | -121.0831 | -121.8018 | -121.875 | -0.16479 | 0.022888 | -0.018311 | 0.018311 | -0.041199 | -0.086975 | 0.045776 | -0.032044 | -0.20599 | -0.11902 | 0.67291 | -0.11902 | -0.045777 | -0.086975 | -0.013733 | 121.7377 | -0.082398 | -0.086975 | 121.7148 | 121.8018 | 121.669 | 0.064087 | -0.068664 | 0.70496 | 121.7743 | -0.022888 | 0.036622 | 121.6873 | 0.041199 | 121.6553 | 121.7789 | -121.8933 | -0.1236 | 121.7422 | 121.7743 | 103.6469 | 121.5912
1540.1094 | 122.049 | -121.7102 | 0.09613 | -0.009308 | 6.9756 | 0.065687 | 0.061511 | 0.006336 | -0.0054731 | -0.00065803 | -0.0097045 | 0.0003098 | 0.017169 | -0.0096536 | -0.0072675 | 0.02553 | -0.0056418 | -18.0725 | -0.16022 | -121.701 | 0.11444 | -120.9137 | -121.6736 | -121.7697 | -0.009155 | -0.022888 | 0.004578 | 0.13275 | 0.10986 | 0.050354 | 0.14191 | 0.009155 | -0.25635 | 0.018311 | 0.79651 | -0.059509 | 0.036621 | -0.068664 | 0.027466 | 121.7148 | -0.11902 | 0.036621 | 121.8201 | 121.8521 | 121.7606 | 0.13733 | 0.045776 | 0.78735 | 121.8155 | 0.10529 | 0.12817 | 121.5408 | -0.027466 | 121.55 | 121.6873 | -121.7972 | -0.091552 | 121.8246 | 121.843 | 103.6377 | 121.701
1541.8438 | 121.9757 | -121.7377 | 0.10529 | -0.016937 | 6.9799 | 0.067396 | 0.062792 | 0.0037726 | -0.0073957 | -0.0019396 | -0.0036011 | 0.0020188 | 0.015887 | -0.01948 | -0.0098309 | 0.02083 | -0.0028646 | -17.9901 | -0.10529 | -121.756 | 0.082397 | -120.9686 | -121.7102 | -121.8292 | -0.068665 | 0.018311 | 0 | 0.064087 | 0.032043 | 0.009155 | 0.086975 | -0.01831 | -0.21057 | -0.022889 | 0.76904 | -0.091553 | 0.027466 | -0.073243 | 0.045776 | 121.7377 | -0.086975 | -0.041199 | 121.7697 | 121.8246 | 121.7468 | 0.086975 | 0.009155 | 0.78735 | 121.8384 | 0.032043 | 0.064087 | 121.6507 | 0.018311 | 121.6324 | 121.756 | -121.8613 | -0.10529 | 121.8201 | 121.8018 | 103.7476 | 121.669
1543.5938 | 122.0535 | -121.7102 | 0.10986 | -0.0016785 | 6.9748 | 0.066328 | 0.061724 | -0.0024224 | -0.0063275 | -0.0012988 | -0.00054933 | 0.0013778 | 0.018237 | -0.0023904 | -0.0055585 | 0.024676 | -0.00094199 | -18.0038 | -0.13733 | -121.7468 | 0.11444 | -120.9274 | -121.6324 | -121.7514 | -0.018311 | -0.013733 | -0.009155 | 0.1236 | 0.10529 | 0.073242 | 0.16022 | -0.036621 | -0.24719 | 0.004578 | 0.78278 | -0.041199 | 0.07782 | -0.004578 | 0.11444 | 121.701 | -0.1236 | 0.013733 | 121.8155 | 121.8704 | 121.7834 | 0.16937 | 0.082397 | 0.8194 | 121.8613 | 0.11444 | 0.13275 | 121.6095 | -0.004578 | 121.5729 | 121.6965 | -121.8567 | -0.11902 | 121.8246 | 121.8338 | 103.7064 | 121.6919
1545.2812 | 121.962 | -121.7468 | 0.13275 | -0.016937 | 6.9774 | 0.067396 | 0.063006 | -7.2628e-05 | -0.0069683 | -0.00065803 | -0.0066527 | 0.005223 | 0.016101 | -0.014353 | -0.0091901 | 0.02553 | 0.0014078 | -18.013 | -0.09613 | -121.7285 | 0.07782 | -120.9732 | -121.7102 | -121.8063 | -0.068665 | 0 | -0.013733 | 0.054932 | 0.036621 | -0.032043 | 0.07782 | 0.01831 | -0.22888 | -0.054931 | 0.77362 | -0.059509 | 0.036621 | -0.077819 | 0.018311 | 121.7331 | -0.13275 | -0.077819 | 121.7834 | 121.8246 | 121.7148 | 0.091553 | -0.01831 | 0.75531 | 121.8063 | 0.050354 | 0.068665 | 121.6324 | 0.013733 | 121.6507 | 121.7468 | -121.8613 | -0.14648 | 121.8246 | 121.8018 | 103.7338 | 121.6782
1546.9688 | 122.0581 | -121.6965 | 0.10529 | -0.0016785 | 6.9756 | 0.065901 | 0.060229 | 0.00014097 | -0.0056867 | -0.0025806 | 0.0025025 | 0.0013778 | 0.01546 | -0.0058084 | -0.0057721 | 0.026171 | -0.006069 | -18.0222 | -0.10529 | -121.7285 | 0.086975 | -120.9457 | -121.6873 | -121.8018 | -0.022888 | -0.009155 | -0.004578 | 0.13733 | 0.086975 | 0.036621 | 0.15564 | -0.032044 | -0.21057 | -0.018311 | 0.75073 | -0.10529 | 0.009155 | -0.073242 | 0.041199 | 121.6919 | -0.11444 | 0.032043 | 121.7834 | 121.8521 | 121.7331 | 0.16022 | 0.041199 | 0.78278 | 121.8155 | 0.091553 | 0.14191 | 121.6232 | -0.004577 | 121.5912 | 121.6873 | -121.8338 | -0.10986 | 121.7834 | 121.8338 | 103.6743 | 121.6736
1548.7188 | 122.0398 | -121.7285 | 0.10529 | -0.016937 | 6.9763 | 0.066755 | 0.060442 | -0.0017816 | -0.0067547 | 0.001051 | -0.00054933 | -0.0005448 | 0.013965 | -0.0051676 | -0.0083355 | 0.025744 | -0.0022238 | -18.045 | -0.1236 | -121.7377 | 0.09613 | -120.9457 | -121.6644 | -121.7606 | -0.064087 | 0.009155 | 0.018311 | 0.11444 | 0.082397 | 0.064087 | 0.14191 | -0.009155 | -0.22888 | -0.009156 | 0.78278 | -0.032043 | 0.064087 | -0.022888 | 0.073242 | 121.7468 | -0.096131 | 0.009155 | 121.8109 | 121.8704 | 121.7926 | 0.1236 | 0.045776 | 0.79193 | 121.8338 | 0.064086 | 0.09613 | 121.6141 | -0.009156 | 121.6049 | 121.7377 | -121.843 | -0.086975 | 121.8246 | 121.843 | 103.6835 | 121.6644
1550.4688 | 121.9711 | -121.7285 | 0.13275 | -0.016937 | 6.9765 | 0.064192 | 0.06087 | -0.00049983 | -0.0065411 | -0.002367 | -0.0066527 | 0.0009506 | 0.016955 | -0.019053 | -0.0094037 | 0.02318 | -0.0024374 | -17.9443 | -0.11902 | -121.7377 | 0.10986 | -120.9229 | -121.637 | -121.7789 | -0.068665 | 0.004578 | -0.004578 | 0.045776 | 0.027466 | -0.009155 | 0.064087 | -0.009155 | -0.25177 | -0.022888 | 0.80566 | -0.050354 | 0.091553 | -0.041199 | 0.10071 | 121.7239 | -0.12817 | -0.086975 | 121.756 | 121.7926 | 121.7194 | 0.068665 | -0.004577 | 0.81482 | 121.8475 | 0.032044 | 0.050354 | 121.6187 | 0.009156 | 121.6095 | 121.7331 | -121.8704 | -0.13733 | 121.8384 | 121.7743 | 103.7842 | 121.6599
1552.1406 | 122.0306 | -121.6644 | 0.11902 | -0.0016785 | 6.9752 | 0.066114 | 0.061083 | -0.00071343 | -0.0084637 | 0.00019657 | -0.0066527 | 0.002446 | 0.015246 | -0.008372 | -0.0089765 | 0.022539 | -0.00072839 | -17.9123 | -0.10986 | -121.7102 | 0.15564 | -120.8725 | -121.5912 | -121.7056 | -0.013733 | 0.013733 | 0.013733 | 0.13733 | 0.10071 | 0.07782 | 0.14648 | -0.045776 | -0.22888 | 0.036621 | 0.79193 | -0.041198 | 0.073242 | 0.004578 | 0.11902 | 121.6782 | -0.10529 | 0.01831 | 121.7651 | 121.8109 | 121.7422 | 0.13275 | 0.064087 | 0.83771 | 121.8658 | 0.086975 | 0.1236 | 121.6003 | 0 | 121.5546 | 121.6782 | -121.8292 | -0.10529 | 121.8201 | 121.8018 | 103.7521 | 121.6507
1553.8906 | 122.0444 | -121.6782 | 0.10529 | -0.009308 | 6.9735 | 0.067182 | 0.061297 | -0.0028498 | -0.0084637 | -0.0042896 | -0.0036011 | 0.0015914 | 0.014605 | -0.0051676 | -0.0079083 | 0.022967 | 0.0016214 | -17.9123 | -0.10529 | -121.6965 | 0.16022 | -120.845 | -121.5866 | -121.6827 | 0.018311 | 0.013733 | 0.027466 | 0.17395 | 0.13275 | 0.09613 | 0.16479 | -0.01831 | -0.21057 | 0.054931 | 0.83313 | -0.004577 | 0.091553 | 0.013733 | 0.10986 | 121.7056 | -0.091553 | 0.068664 | 121.8109 | 121.843 | 121.7743 | 0.13733 | 0.068664 | 0.85144 | 121.8567 | 0.10529 | 0.14648 | 121.5912 | -0.013733 | 121.5729 | 121.6919 | -121.8018 | -0.07782 | 121.8384 | 121.8521 | 103.7659 | 121.6965
1555.625 | 121.8796 | -121.7102 | 0.15106 | -0.009308 | 6.9786 | 0.067182 | 0.062792 | 0.00035457 | -0.0084637 | -0.0053576 | 0.0025025 | 0.003514 | 0.012897 | -0.013072 | -0.0053449 | 0.023821 | -0.0045736 | -17.9352 | -0.050354 | -121.7285 | 0.022888 | -121.0419 | -121.7422 | -121.8567 | -0.18768 | 0.050354 | -0.018311 | 0.032043 | -0.041199 | -0.091553 | 0.059509 | -0.018311 | -0.20142 | -0.12817 | 0.66833 | -0.14648 | -0.032044 | -0.12817 | -0.013733 | 121.6919 | -0.10071 | -0.11902 | 121.669 | 121.7697 | 121.6187 | 0.07782 | -0.073242 | 0.68665 | 121.7514 | -0.022888 | 0.050354 | 121.6782 | 0.068665 | 121.6599 | 121.7606 | -121.8796 | -0.16937 | 121.7331 | 121.7422 | 103.775 | 121.5225
1557.2969 | 121.8979 | -121.6873 | 0.13733 | -0.009308 | 6.9789 | 0.06825 | 0.063433 | 0.0022772 | -0.0059003 | -0.0036486 | 0.0025025 | 0.0033004 | 0.017169 | -0.0036722 | -0.0068403 | 0.024248 | -0.0045736 | -17.981 | -0.054932 | -121.7056 | 0.032043 | -121.0556 | -121.7422 | -121.8475 | -0.19684 | 0.045776 | -0.022888 | 0.036621 | -0.054932 | -0.09613 | 0.050354 | -0.01831 | -0.19226 | -0.10529 | 0.63171 | -0.16022 | -0.054932 | -0.14191 | -0.036622 | 121.6644 | -0.091553 | -0.10071 | 121.6324 | 121.7377 | 121.5912 | 0.073242 | -0.073242 | 0.65002 | 121.7377 | -0.032044 | 0.059509 | 121.6507 | 0.068664 | 121.6324 | 121.7331 | -121.843 | -0.16022 | 121.7194 | 121.7239 | 103.7064 | 121.4905
1558.9844 | 121.9986 | -121.6599 | 0.12817 | -0.009308 | 6.9744 | 0.068891 | 0.063006 | 0.0024908 | -0.0088911 | -0.0032214 | -0.00054933 | 0.0009506 | 0.01546 | -0.011149 | -0.0089765 | 0.024035 | -0.0052146 | -17.9031 | -0.10071 | -121.6965 | 0.16937 | -120.8542 | -121.5729 | -121.6919 | -0.022888 | 0.013733 | 0.009155 | 0.13275 | 0.10529 | 0.073242 | 0.13733 | -0.036621 | -0.22888 | 0.041199 | 0.80566 | -0.032044 | 0.086975 | 0.004577 | 0.1236 | 121.669 | -0.11444 | 0.004577 | 121.7651 | 121.7972 | 121.7331 | 0.12817 | 0.064087 | 0.84229 | 121.8658 | 0.096131 | 0.1236 | 121.5958 | 0.004578 | 121.5591 | 121.6736 | -121.8246 | -0.11902 | 121.8292 | 121.7926 | 103.7567 | 121.637
1560.7188 | 122.0078 | -121.6507 | 0.12817 | 0.005951 | 6.9744 | 0.06526 | 0.061083 | -7.2628e-05 | -0.0063275 | -0.0015124 | -0.0066527 | 0.000737 | 0.015674 | -0.0070902 | -0.0079083 | 0.024462 | -0.003292 | -17.8986 | -0.10071 | -121.6827 | 0.16022 | -120.8405 | -121.5637 | -121.6965 | -0.004578 | 0 | 0.036621 | 0.14191 | 0.10071 | 0.068665 | 0.14648 | -0.032043 | -0.22888 | 0.032043 | 0.81024 | -0.045776 | 0.086975 | -0.013733 | 0.11902 | 121.6873 | -0.12817 | 0.013733 | 121.7514 | 121.7972 | 121.7194 | 0.10986 | 0.032044 | 0.84229 | 121.843 | 0.064087 | 0.10529 | 121.582 | -0.036621 | 121.55 | 121.6507 | -121.8109 | -0.091553 | 121.8109 | 121.7926 | 103.7521 | 121.6461
1562.4531 | 121.9299 | -121.6599 | 0.15564 | -0.016937 | 6.9767 | 0.064405 | 0.062365 | -7.2628e-05 | -0.0082501 | -0.00087163 | -0.00054933 | 0.0020188 | 0.011401 | -0.0090128 | -0.010045 | 0.023394 | -0.0037192 | -17.981 | -0.068665 | -121.7194 | 0.050354 | -120.9961 | -121.6782 | -121.8018 | -0.16937 | 0.050354 | -0.013733 | 0.050354 | 0.004578 | -0.032043 | 0.064087 | -0.059509 | -0.22431 | -0.10529 | 0.66376 | -0.14191 | -0.018311 | -0.082398 | 0.041198 | 121.6461 | -0.10529 | -0.10529 | 121.6644 | 121.7239 | 121.6278 | 0.07782 | -0.01831 | 0.72327 | 121.7697 | 0.018311 | 0.064087 | 121.6507 | 0.064087 | 121.5912 | 121.7102 | -121.875 | -0.16937 | 121.7102 | 121.7102 | 103.6789 | 121.4905
1564.125 | 121.994 | -121.669 | 0.1236 | -0.009308 | 6.9793 | 0.066328 | 0.061938 | -7.2628e-05 | -0.0061139 | 0.00083737 | -0.0066527 | 0.0009506 | 0.01311 | -0.0053812 | -0.0044903 | 0.025103 | 0.00012601 | -17.8619 | -0.10071 | -121.6415 | 0.15564 | -120.8542 | -121.5958 | -121.701 | 0.009155 | 0.013733 | 0.027466 | 0.17853 | 0.11444 | 0.082397 | 0.16022 | 0.027465 | -0.2243 | 0.032044 | 0.81482 | -0.032044 | 0.073242 | -0.059509 | 0.045777 | 121.6965 | -0.10986 | 0.054932 | 121.7834 | 121.8292 | 121.7514 | 0.13275 | 0.054931 | 0.78735 | 121.7972 | 0.086975 | 0.15106 | 121.5408 | -0.013733 | 121.5683 | 121.6827 | -121.7651 | -0.09613 | 121.8246 | 121.8475 | 103.8071 | 121.6782
1565.8594 | 121.8933 | -121.6782 | 0.16022 | -0.016937 | 6.9786 | 0.06761 | 0.063006 | 0.0022772 | -0.0044049 | -0.00087163 | -0.00054933 | 0.002446 | 0.016101 | -0.012217 | -0.0083355 | 0.025103 | -0.006069 | -17.8299 | -0.068665 | -121.6965 | 0.10529 | -120.9229 | -121.6599 | -121.756 | -0.091553 | 0.059509 | 0.013733 | 0.09613 | -0.009155 | -0.041199 | 0.073242 | -0.01831 | -0.22888 | -0.054931 | 0.75531 | -0.077819 | 0.018311 | -0.059509 | 0.036621 | 121.6919 | -0.10071 | -0.064087 | 121.669 | 121.7514 | 121.637 | 0.059509 | -0.054932 | 0.77362 | 121.8018 | -0.022888 | 0.082397 | 121.6278 | 0.045776 | 121.6095 | 121.7377 | -121.8567 | -0.14648 | 121.7834 | 121.7743 | 103.8483 | 121.5866
1567.6094 | 121.9391 | -121.637 | 0.13733 | -0.009308 | 6.9729 | 0.065901 | 0.060656 | -0.0037042 | -0.0063275 | -0.0030078 | -0.0036011 | 0.0005234 | 0.012683 | -0.0038858 | -0.0055585 | 0.025744 | -0.0073508 | -17.9443 | -0.082397 | -121.6599 | 0.10071 | -120.9 | -121.6461 | -121.7239 | -0.10986 | 0.022888 | 0.009155 | 0.10986 | 0.054932 | 0.022888 | 0.11444 | -0.022888 | -0.21973 | -0.036621 | 0.737 | -0.086975 | -0.009155 | -0.064087 | 0.013733 | 121.6461 | -0.11444 | -0.027466 | 121.6919 | 121.7514 | 121.6599 | 0.10529 | 0.013733 | 0.75989 | 121.7606 | 0.045777 | 0.10071 | 121.5775 | 0.013733 | 121.5546 | 121.6599 | -121.7972 | -0.12817 | 121.7377 | 121.7468 | 103.6926 | 121.5271
1569.2969 | 121.8979 | -121.6782 | 0.16022 | -0.0016785 | 6.9763 | 0.065687 | 0.059374 | 0.00035457 | -0.0097455 | 0.001051 | -0.0097045 | 0.0018052 | 0.016955 | -0.016703 | -0.0096173 | 0.025103 | -0.0028646 | -17.8757 | -0.082397 | -121.6599 | 0.09613 | -120.9137 | -121.6049 | -121.7331 | -0.10529 | 0.045776 | 0.004578 | 0.041199 | 0.013733 | -0.036621 | 0.050354 | 0.018311 | -0.24261 | -0.064087 | 0.76447 | -0.054931 | 0.073243 | -0.073242 | 0.054932 | 121.6827 | -0.11444 | -0.11902 | 121.6919 | 121.7285 | 121.6415 | 0.045776 | -0.041199 | 0.74616 | 121.756 | 0.009155 | 0.036621 | 121.5775 | 0.041198 | 121.5958 | 121.7239 | -121.8201 | -0.15564 | 121.7743 | 121.7194 | 103.8025 | 121.5729
1570.9844 | 121.8979 | -121.6599 | 0.16479 | -0.024567 | 6.9763 | 0.063337 | 0.06322 | -7.2628e-05 | -0.0071821 | -0.0053576 | -0.0066527 | 0.0028732 | 0.015033 | -0.012644 | -0.0085491 | 0.024035 | -0.003292 | -17.8986 | -0.050354 | -121.6827 | 0.045776 | -120.9686 | -121.6644 | -121.7743 | -0.16937 | 0.041199 | -0.013733 | 0.054932 | 0.004578 | -0.054932 | 0.07782 | -0.022888 | -0.21515 | -0.11902 | 0.69122 | -0.11444 | -0.004578 | -0.091553 | 0.01831 | 121.6461 | -0.1236 | -0.10986 | 121.6644 | 121.7377 | 121.6049 | 0.091553 | -0.041199 | 0.71411 | 121.7285 | 0.018311 | 0.068665 | 121.6324 | 0.054932 | 121.6095 | 121.7011 | -121.8475 | -0.17853 | 121.7056 | 121.7148 | 103.7613 | 121.4905
1572.6562 | 121.9116 | -121.637 | 0.17395 | -0.024567 | 6.9771 | 0.065687 | 0.06322 | 0.0016364 | -0.0076093 | -0.00087163 | -0.0066527 | 0.0015914 | 0.016528 | -0.014567 | -0.0070539 | 0.022967 | -0.0056418 | -17.8757 | -0.064087 | -121.6782 | 0.050354 | -120.932 | -121.6187 | -121.7422 | -0.11902 | 0.041199 | 0.009155 | 0.09613 | 0.036621 | 0.004578 | 0.10986 | -0.041199 | -0.23804 | -0.1236 | 0.70496 | -0.10529 | 0.018311 | -0.064087 | 0.05951 | 121.6461 | -0.13275 | -0.07782 | 121.6736 | 121.7468 | 121.6415 | 0.10071 | -0.004577 | 0.74616 | 121.7285 | 0.027466 | 0.086975 | 121.6141 | 0.032044 | 121.5729 | 121.6782 | -121.8521 | -0.16479 | 121.6873 | 121.7331 | 103.7613 | 121.5179
1574.3438 | 121.9986 | -121.6187 | 0.15106 | -0.0016785 | 6.9776 | 0.065046 | 0.060442 | -0.0011408 | -0.0080365 | -0.0015124 | -0.00054933 | -0.0007584 | 0.015674 | -0.0038858 | -0.0072675 | 0.026812 | -0.0017966 | -17.807 | -0.09613 | -121.6278 | 0.18768 | -120.7809 | -121.4996 | -121.6324 | 0.013733 | 0.022888 | 0.018311 | 0.16022 | 0.11902 | 0.10071 | 0.15564 | -0.009156 | -0.24719 | 0.036621 | 0.83771 | -0.013733 | 0.11902 | -0.004577 | 0.12817 | 121.637 | -0.12817 | 0.009155 | 121.7377 | 121.7743 | 121.7194 | 0.13733 | 0.082397 | 0.84686 | 121.8155 | 0.10071 | 0.14191 | 121.5317 | 0.004577 | 121.5225 | 121.6415 | -121.7789 | -0.13275 | 121.8063 | 121.7789 | 103.8116 | 121.6324
1576.0312 | 121.8521 | -121.637 | 0.16937 | 0.005951 | 6.9774 | 0.066969 | 0.064715 | 0.0029182 | -0.0063275 | -0.0045032 | -0.0036011 | 0.0030868 | 0.013324 | -0.012431 | -0.0044903 | 0.023821 | -0.0028646 | -17.8162 | -0.068665 | -121.6599 | 0.068665 | -120.9641 | -121.6782 | -121.7789 | -0.16022 | 0.073242 | 0.009155 | 0.041199 | -0.027466 | -0.086975 | 0.059509 | -0.022888 | -0.23804 | -0.10071 | 0.67291 | -0.14191 | -0.041199 | -0.11902 | -0.018311 | 121.6461 | -0.096131 | -0.12817 | 121.6095 | 121.6965 | 121.55 | 0.050354 | -0.09613 | 0.6958 | 121.7285 | -0.036621 | 0.032044 | 121.5912 | 0.064087 | 121.5683 | 121.7102 | -121.8292 | -0.16022 | 121.7056 | 121.6782 | 103.8208 | 121.4767
1577.7656 | 121.9803 | -121.6003 | 0.15106 | -0.0016785 | 6.975 | 0.068037 | 0.061938 | -0.0011408 | -0.0076093 | -0.0027942 | -0.0036011 | -0.0001174 | 0.014605 | -0.010508 | -0.0081219 | 0.024889 | -0.001583 | -17.8848 | -0.073242 | -121.6232 | 0.13733 | -120.8313 | -121.5317 | -121.6461 | -0.027466 | 0.041199 | 0.027466 | 0.15106 | 0.11902 | 0.086975 | 0.16022 | -0.022888 | -0.2243 | -0.013733 | 0.76904 | -0.045776 | 0.068665 | -0.022888 | 0.091553 | 121.6278 | -0.10986 | 0 | 121.7194 | 121.7606 | 121.6873 | 0.13275 | 0.059509 | 0.79193 | 121.7606 | 0.091553 | 0.1236 | 121.55 | 0.013733 | 121.5271 | 121.6415 | -121.7743 | -0.1236 | 121.7377 | 121.7514 | 103.7155 | 121.5729
1579.5 | 121.9528 | -121.6278 | 0.14648 | -0.0016785 | 6.9748 | 0.066969 | 0.061724 | 0.00014097 | -0.0071821 | -0.0015124 | -0.0036011 | 0.0011642 | 0.014392 | -0.0073038 | -0.0068403 | 0.024889 | -8.7586e-05 | -17.8711 | -0.07782 | -121.6095 | 0.16022 | -120.8267 | -121.5225 | -121.6232 | -0.027466 | 0.041199 | 0.027466 | 0.17395 | 0.1236 | 0.07782 | 0.16937 | 0.018311 | -0.2243 | 0.013733 | 0.80109 | 0.004578 | 0.10529 | -0.013733 | 0.086975 | 121.6553 | -0.10529 | 0.027466 | 121.7514 | 121.7972 | 121.7056 | 0.14191 | 0.050354 | 0.78278 | 121.7697 | 0.09613 | 0.14648 | 121.5317 | 0.013733 | 121.55 | 121.669 | -121.756 | -0.11902 | 121.788 | 121.8018 | 103.7567 | 121.6003
1581.1719 | 121.8704 | -121.6599 | 0.10986 | -0.009308 | 6.975 | 0.063764 | 0.061724 | -0.00028623 | -0.0080365 | -0.00023063 | -0.0066527 | 0.0026596 | 0.013965 | -0.0034586 | -0.0079083 | 0.024462 | -8.7586e-05 | -17.8299 | -0.14191 | -121.6553 | 0.12817 | -120.8496 | -121.5591 | -121.6736 | -0.041199 | 0.004578 | 0.013733 | 0.045776 | 0.050354 | 0.013733 | 0.091553 | 0.004578 | -0.25177 | 0.018311 | 0.81024 | -0.013733 | 0.10071 | -0.018311 | 0.09613 | 121.6736 | -0.10529 | -0.064087 | 121.7102 | 121.7514 | 121.6736 | 0.07782 | 0 | 0.80566 | 121.7834 | 0.036621 | 0.032043 | 121.5134 | -0.009155 | 121.5179 | 121.6644 | -121.7651 | -0.09613 | 121.788 | 121.7056 | 103.83 | 121.6187
1582.9062 | 121.9208 | -121.6553 | 0.09613 | -0.016937 | 6.9754 | 0.064405 | 0.061083 | 0.0065498 | -0.0076093 | -0.0015124 | -0.0097045 | -0.0005448 | 0.017169 | -0.0038858 | -0.0061993 | 0.027453 | -0.0030784 | -17.9581 | -0.1236 | -121.6827 | 0.064087 | -120.9457 | -121.6461 | -121.7285 | -0.091553 | 0.004578 | 0 | 0.073242 | 0.041199 | 0.027466 | 0.10529 | -0.027466 | -0.21973 | -0.032043 | 0.70953 | -0.073243 | 0.009155 | -0.045777 | 0.036621 | 121.6553 | -0.091552 | -0.022888 | 121.6965 | 121.7606 | 121.6827 | 0.10529 | 0.027466 | 0.737 | 121.7468 | 0.041199 | 0.073242 | 121.5591 | 0.004578 | 121.5317 | 121.6599 | -121.7789 | -0.09613 | 121.7194 | 121.7285 | 103.6972 | 121.5637
1584.6406 | 121.9803 | -121.6553 | 0.07782 | -0.0016785 | 6.9754 | 0.065046 | 0.061724 | 0.00056817 | -0.010814 | -0.0042896 | -0.0036011 | -0.0013992 | 0.01546 | -0.0092264 | -0.0068403 | 0.024462 | -0.0047874 | -17.8299 | -0.13733 | -121.6827 | 0.15106 | -120.8267 | -121.5546 | -121.669 | 0.018311 | -0.022888 | -0.004578 | 0.14648 | 0.13275 | 0.091553 | 0.14191 | -0.027466 | -0.21515 | 0.073242 | 0.82855 | -0.013733 | 0.10071 | 0.013733 | 0.12817 | 121.6507 | -0.10071 | 0.068664 | 121.788 | 121.7972 | 121.7468 | 0.14649 | 0.096131 | 0.85602 | 121.8338 | 0.13733 | 0.15106 | 121.5454 | -0.01831 | 121.5179 | 121.6324 | -121.7606 | -0.082398 | 121.8063 | 121.8018 | 103.8254 | 121.6736
1586.375 | 122.0078 | -121.6461 | 0.1236 | -0.0016785 | 6.978 | 0.064832 | 0.063433 | -0.0034906 | -0.0069683 | -0.0027942 | -0.00054933 | 0.0009506 | 0.014605 | -0.002604 | -0.0068403 | 0.025957 | -0.0041464 | -17.8711 | -0.12817 | -121.7056 | 0.15106 | -120.8542 | -121.5683 | -121.6919 | 0.018311 | -0.013733 | 0.018311 | 0.15564 | 0.13733 | 0.086975 | 0.15564 | -0.059509 | -0.25177 | 0.027466 | 0.79193 | -0.045777 | 0.07782 | 0.013732 | 0.13733 | 121.6644 | -0.13733 | 0.032044 | 121.7834 | 121.8018 | 121.7331 | 0.13733 | 0.068664 | 0.85144 | 121.8567 | 0.11902 | 0.13733 | 121.5775 | -0.032044 | 121.5179 | 121.6324 | -121.8292 | -0.10528 | 121.7972 | 121.8018 | 103.775 | 121.6644
1588.0938 | 121.875 | -121.6919 | 0.12817 | -0.009308 | 6.9765 | 0.066541 | 0.065356 | 0.00056817 | -0.0056867 | -0.0030078 | -0.0036011 | 0.0037278 | 0.017169 | -0.011363 | -0.0049175 | 0.027239 | -0.00094199 | -17.9031 | -0.091553 | -121.7194 | 0.013733 | -121.0464 | -121.756 | -121.8475 | -0.17853 | 0.041199 | -0.022888 | 0.018311 | -0.050354 | -0.091553 | 0.045776 | -0.027465 | -0.21973 | -0.11444 | 0.64545 | -0.15564 | -0.064086 | -0.12817 | -0.036621 | 121.669 | -0.086975 | -0.10986 | 121.6415 | 121.7377 | 121.6003 | 0.068664 | -0.068665 | 0.67291 | 121.7331 | -0.027466 | 0.041199 | 121.6278 | 0.064087 | 121.6003 | 121.7331 | -121.8475 | -0.15106 | 121.7056 | 121.7102 | 103.7888 | 121.5134
1589.7812 | 121.9208 | -121.6782 | 0.13733 | -0.016937 | 6.9778 | 0.067823 | 0.062151 | 0.0022772 | -0.0056867 | -0.0027942 | -0.0066527 | 0.005223 | 0.01781 | -0.014994 | -0.0079083 | 0.025316 | -0.0028646 | -17.8253 | -0.09613 | -121.7239 | 0.07782 | -120.9229 | -121.6507 | -121.7697 | -0.054932 | 0.032043 | 0 | 0.086975 | 0.041199 | -0.009155 | 0.091553 | -0.045776 | -0.23346 | -0.059509 | 0.75531 | -0.091552 | 0.027466 | -0.045776 | 0.073242 | 121.6782 | -0.10529 | -0.050354 | 121.7194 | 121.7697 | 121.669 | 0.091553 | -0.009155 | 0.80109 | 121.8018 | 0.041199 | 0.086975 | 121.6278 | 0.032043 | 121.582 | 121.7102 | -121.8613 | -0.13733 | 121.756 | 121.7651 | 103.8528 | 121.6232
1591.5156 | 122.0352 | -121.6599 | 0.10071 | -0.016937 | 6.9759 | 0.065901 | 0.059161 | -0.0013544 | -0.0063275 | -0.0019396 | -0.0036011 | -0.0013992 | 0.019732 | -0.002604 | -0.0076947 | 0.024676 | -0.001583 | -17.8436 | -0.12817 | -121.6965 | 0.15564 | -120.8267 | -121.5637 | -121.6782 | 0.027466 | -0.009155 | 0.027466 | 0.16479 | 0.12817 | 0.10071 | 0.14191 | -0.036621 | -0.22888 | 0.054932 | 0.83313 | -0.018311 | 0.09613 | 0.01831 | 0.13275 | 121.6873 | -0.10986 | 0.064087 | 121.788 | 121.8018 | 121.7606 | 0.11444 | 0.073242 | 0.86975 | 121.8521 | 0.10071 | 0.13733 | 121.5683 | -0.036621 | 121.5317 | 121.6507 | -121.7972 | -0.073242 | 121.8155 | 121.8246 | 103.8162 | 121.6873
1593.2031 | 121.8842 | -121.7056 | 0.13275 | -0.009308 | 6.9763 | 0.066328 | 0.062151 | -0.00049983 | -0.0071821 | -0.0027942 | -0.0036011 | 0.0033004 | 0.014392 | -0.0079446 | -0.0083355 | 0.024889 | -0.001583 | -17.8024 | -0.11444 | -121.701 | 0.091553 | -120.9091 | -121.6415 | -121.7514 | -0.11902 | 0.018311 | -0.004578 | 0.032043 | 0.013733 | -0.050354 | 0.059509 | 0.004577 | -0.24719 | -0.041198 | 0.79651 | -0.045777 | 0.064086 | -0.050354 | 0.059509 | 121.701 | -0.11444 | -0.10071 | 121.7194 | 121.7651 | 121.6553 | 0.064087 | -0.045776 | 0.79193 | 121.7926 | 0.018311 | 0.036621 | 121.5866 | 0.022889 | 121.5912 | 121.7239 | -121.8338 | -0.13733 | 121.7972 | 121.7377 | 103.9032 | 121.5866
1594.9531 | 121.9116 | -121.6736 | 0.15106 | -0.0016785 | 6.9771 | 0.064832 | 0.065997 | 0.00056817 | -0.0078229 | -0.0040758 | -0.00054933 | 0.0043686 | 0.017383 | -0.011149 | -0.0076947 | 0.025103 | -0.0052146 | -17.807 | -0.086975 | -121.6782 | 0.082397 | -120.9457 | -121.669 | -121.788 | -0.091553 | 0.027466 | 0 | 0.054932 | 0 | -0.07782 | 0.059509 | -0.004578 | -0.23804 | -0.068665 | 0.72784 | -0.11444 | 0.004578 | -0.10986 | 0.009156 | 121.6736 | -0.1236 | -0.09613 | 121.6736 | 121.7331 | 121.5958 | 0.059509 | -0.07782 | 0.73242 | 121.7606 | 0 | 0.054932 | 121.5912 | 0.027466 | 121.5866 | 121.7011 | -121.8292 | -0.15106 | 121.756 | 121.7285 | 103.8666 | 121.582
1596.7031 | 121.962 | -121.6644 | 0.11444 | -0.009308 | 6.9765 | 0.066969 | 0.06087 | 0.0024908 | -0.0078229 | -0.0025806 | -0.0066527 | 0.0013778 | 0.015674 | -0.010935 | -0.0083355 | 0.024889 | -0.0058554 | -17.8024 | -0.1236 | -121.7102 | 0.15106 | -120.8633 | -121.5683 | -121.7056 | -0.041199 | -0.009155 | 0.013733 | 0.09613 | 0.082397 | 0.050354 | 0.10986 | -0.045776 | -0.23804 | 0.036621 | 0.80109 | -0.041198 | 0.096131 | 0.004578 | 0.14191 | 121.6782 | -0.1236 | -0.018311 | 121.7468 | 121.7743 | 121.7148 | 0.09613 | 0.036621 | 0.84686 | 121.8613 | 0.068664 | 0.082397 | 121.5866 | -0.022888 | 121.5408 | 121.6553 | -121.8246 | -0.10071 | 121.8155 | 121.7606 | 103.862 | 121.6232
1598.3906 | 121.8842 | -121.701 | 0.16479 | -0.0016785 | 6.9786 | 0.066328 | 0.066851 | 0.006336 | -0.0063275 | -1.7026e-05 | -0.00054933 | 0.0043686 | 0.017169 | -0.018839 | -0.0064129 | 0.025744 | -0.0030784 | -17.8345 | -0.050354 | -121.7194 | 0.009155 | -121.0236 | -121.7331 | -121.8246 | -0.16937 | 0.054932 | -0.022888 | 0.022888 | -0.059509 | -0.07782 | 0.054932 | -0.01831 | -0.21515 | -0.15564 | 0.67749 | -0.1236 | -0.032043 | -0.10529 | -0.013733 | 121.6782 | -0.10986 | -0.14191 | 121.6415 | 121.756 | 121.6232 | 0.07782 | -0.054932 | 0.6958 | 121.7285 | -0.036621 | 0.045776 | 121.669 | 0.07782 | 121.6507 | 121.756 | -121.8842 | -0.18768 | 121.7102 | 121.7239 | 103.8666 | 121.5317
1600.1562 | 121.875 | -121.6873 | 0.15106 | 0.005951 | 6.9782 | 0.066328 | 0.062365 | 0.0024908 | -0.0069683 | -0.0036486 | -0.00054933 | 0.0026596 | 0.016955 | -0.013926 | -0.0057721 | 0.026385 | -0.00030119 | -17.8757 | -0.082397 | -121.7239 | 0.036621 | -121.0327 | -121.7148 | -121.8201 | -0.17853 | 0.041199 | -0.009155 | 0.041199 | -0.041199 | -0.091553 | 0.050354 | -0.036621 | -0.23346 | -0.11444 | 0.6546 | -0.13275 | -0.027466 | -0.09613 | 0.009155 | 121.6782 | -0.10986 | -0.10986 | 121.6461 | 121.7377 | 121.5958 | 0.059509 | -0.082398 | 0.69122 | 121.7606 | -0.032044 | 0.050354 | 121.6415 | 0.050354 | 121.6049 | 121.7285 | -121.875 | -0.16022 | 121.7239 | 121.7285 | 103.8116 | 121.5088
1601.8906 | 121.2296 | -46.4996 | 74.2218 | 0.074615 | 6.9865 | 0.065901 | 0.06087 | 0.006336 | -0.0031231 | -0.0010852 | 0.014709 | 0.016331 | 0.023791 | 0.50539 | -0.0079083 | 0.021471 | -0.0041464 | 3.8223 | 76.1261 | -44.545 | 76.3458 | -45.9915 | -45.8313 | -45.5978 | 15.5777 | 75.174 | 8.9539 | 73.97 | 16.5939 | 22.1054 | 26.7334 | 1.9547 | 1.9043 | 2.124 | 0.50812 | 0.90179 | 0.66833 | -1.0529 | -1.2863 | 55.4535 | 0.95215 | -0.25177 | 63.0936 | 73.233 | 68.605 | 17.7795 | 13.1516 | -1.4465 | 120.8908 | 7.6401 | 65.0162 | 120.6711 | 66.2201 | 122.6257 | 121.6736 | -118.7668 | -65.2679 | 122.8455 | 120.4697 | 50.322 | 62.0773
1603.5625 | 121.3669 | -31.6132 | 79.0329 | 0.005951 | 6.9776 | 0.066541 | 0.061938 | -0.00028623 | -0.0084637 | -0.0015124 | -0.0066527 | 0.019322 | 0.012897 | 0.53167 | -0.024571 | 0.021258 | -0.014614 | 1.1993 | 88.8702 | -32.0618 | 88.6642 | -32.515 | -32.4371 | -32.4509 | 13.1424 | 87.9959 | 9.2422 | 88.2523 | 11.2244 | 15.4312 | 16.983 | -0.44861 | 9.8373 | 9.6313 | -0.9018 | -0.83771 | -0.82398 | -0.3891 | -0.37537 | 40.8554 | 8.963 | 9.2194 | 42.8375 | 48.5962 | 47.0444 | 7.7408 | 6.189 | -0.45319 | 120.726 | 1.9821 | 79.01 | 120.932 | 78.7537 | 120.4834 | 119.6091 | -111.0947 | -69.7906 | 120.2774 | 119.8654 | 32.8125 | 44.7556
1605.2969 | 120.6848 | -0.51727 | 112.1887 | -0.0016785 | 6.9765 | 0.065687 | 0.06386 | 0.00014097 | -0.0041913 | -0.0021532 | 0.0025025 | 0.0045822 | 0.018878 | 0.012777 | -0.0053449 | 0.025744 | -0.011623 | 5.7678 | 120.5063 | -0.71411 | 120.639 | -0.66834 | -0.79193 | -0.79193 | -0.27008 | -0.09613 | 0.1831 | -0.086975 | -0.13275 | -0.16479 | -0.054932 | -0.19684 | 8.3176 | 8.4503 | -0.15106 | -0.27466 | -0.27466 | -0.07782 | -0.07782 | 0.70038 | -112.2849 | -112.2757 | 0.38452 | 0.46234 | 0.35248 | -0.23804 | -0.3479 | 0.045776 | 121.3531 | -0.31586 | -0.27008 | 121.2204 | -0.27924 | 121.0236 | 0.42114 | -112.9028 | -112.0056 | 121.1563 | 0.4303 | 6.2851 | 0.24719
1607.0312 | 121.3852 | -0.76446 | 120.0165 | -0.0016785 | 6.9763 | 0.067823 | 0.063006 | 0.00035457 | -0.0054731 | -0.0021532 | 0.0025025 | 0.003514 | 0.014178 | 0.010213 | -0.0055585 | 0.02788 | -0.00051479 | 5.6442 | 120.5475 | -0.75531 | 120.7901 | -0.51727 | -0.66834 | -0.68207 | -0.11902 | -0.13275 | -0.082397 | 0.027466 | 0.013733 | -0.032043 | 0.064087 | 0.009155 | 0.53101 | 0.77362 | 0.24719 | 0.082397 | 0.09613 | 0.073242 | 0.086975 | 0.68207 | -120.1492 | -119.989 | 0.7782 | 0.82855 | 0.73242 | 0.14648 | 0.050354 | 0.23804 | 121.5454 | 0.09613 | 0.10986 | 121.3028 | -0.050354 | 121.3119 | 0.63171 | -120.7718 | -120.0989 | 121.5546 | 0.79193 | 6.4087 | 0.64545
1608.7812 | 121.6232 | -0.79193 | 120.4697 | -0.0016785 | 6.9789 | 0.066541 | 0.063006 | -0.001568 | -0.0050457 | -0.00044443 | 0.0025025 | 0.0018052 | 0.017383 | 0.017904 | -0.0066265 | 0.028094 | -0.0013694 | 5.5527 | 120.5795 | -0.75989 | 120.7764 | -0.54932 | -0.69122 | -0.70953 | -0.17853 | -0.13733 | -0.10071 | -0.045776 | -0.036621 | -0.068665 | 0.004578 | 0.032043 | 0.10986 | 0.3067 | 0.24262 | 0.082397 | 0.10071 | 0.050354 | 0.068665 | 0.69122 | -120.607 | -120.5154 | 0.75531 | 0.79651 | 0.72327 | 0.10529 | 0.032043 | 0.21057 | 121.5363 | 0.064087 | 0.054932 | 121.3394 | -0.036621 | 121.3715 | 0.6546 | -121.2296 | -120.5704 | 121.5683 | 0.74616 | 6.3446 | 0.6134
1610.4688 | 121.669 | -0.80109 | 120.7535 | -0.009308 | 6.9767 | 0.066755 | 0.063647 | 0.00035457 | -0.0041913 | -0.00065803 | -0.00054933 | 0.003514 | 0.017596 | 0.021749 | -0.0029949 | 0.026385 | -0.0035056 | 5.5069 | 120.6207 | -0.81482 | 120.7626 | -0.63171 | -0.76446 | -0.7782 | -0.17395 | -0.1236 | -0.10986 | -0.013733 | -0.022888 | -0.086975 | 0.036621 | -0.013733 | -0.13275 | 0.009155 | 0.16937 | 0.022888 | 0.036621 | 0.036621 | 0.050354 | 0.69122 | -120.8771 | -120.7672 | 0.7782 | 0.83771 | 0.71411 | 0.14648 | 0.022888 | 0.1831 | 121.5775 | 0.086975 | 0.09613 | 121.4355 | -0.013733 | 121.4218 | 0.67749 | -121.5683 | -120.8633 | 121.5637 | 0.78735 | 6.308 | 0.62714
1612.2031 | 121.5866 | -0.83771 | 120.8176 | -0.009308 | 6.9778 | 0.064192 | 0.066638 | 0.00035457 | -0.0044049 | -0.00087163 | -0.00054933 | 0.0043686 | 0.018664 | 0.015981 | -0.0061993 | 0.026812 | -0.00094199 | 5.4932 | 120.639 | -0.82855 | 120.6985 | -0.70496 | -0.83313 | -0.82855 | -0.27466 | -0.09613 | -0.12817 | -0.09613 | -0.13275 | -0.18768 | -0.036621 | 0.009156 | -0.17853 | -0.11902 | 0.13275 | 0.009156 | 0.004578 | 0 | -0.004578 | 0.70953 | -120.9137 | -120.9137 | 0.70496 | 0.80109 | 0.65003 | 0.091553 | -0.059509 | 0.1236 | 121.5271 | -0.004577 | 0.032044 | 121.4676 | 0.032044 | 121.4767 | 0.74158 | -121.6461 | -120.9457 | 121.5363 | 0.74158 | 6.3309 | 0.56305
1613.875 | 121.6965 | -0.84228 | 120.7855 | 0.005951 | 6.9784 | 0.066114 | 0.064288 | 0.003559 | -0.0052595 | -0.0012988 | -0.00054933 | 0.0018052 | 0.016314 | 0.017049 | -0.0059857 | 0.028307 | 0.0016214 | 5.5206 | 120.6162 | -0.84686 | 120.7169 | -0.68207 | -0.80566 | -0.8194 | -0.19684 | -0.11902 | -0.09613 | -0.041199 | -0.059509 | -0.086975 | 0.032043 | -0.004578 | -0.16937 | -0.068664 | 0.16022 | 0.022888 | 0.036621 | 0.027466 | 0.041199 | 0.74615 | -120.9045 | -120.8267 | 0.78278 | 0.87433 | 0.75531 | 0.12817 | 0.009155 | 0.1648 | 121.5637 | 0.036621 | 0.054931 | 121.463 | -0.022889 | 121.4584 | 0.72327 | -121.6324 | -120.8817 | 121.5591 | 0.80109 | 6.3629 | 0.64545
1615.625 | 121.7148 | -0.85144 | 120.7809 | -0.0016785 | 6.978 | 0.065687 | 0.062792 | -0.0039178 | -0.0076093 | -0.0038622 | 0.0025025 | 0.0028732 | 0.018023 | 0.016408 | -0.0070539 | 0.025957 | 0.00098061 | 5.571 | 120.5887 | -0.82855 | 120.7764 | -0.60425 | -0.75989 | -0.77362 | -0.14648 | -0.13275 | -0.091553 | -0.032043 | -0.045776 | -0.086975 | 0.013733 | 0.022888 | -0.19226 | -0.004578 | 0.24719 | 0.077819 | 0.091552 | 0.054931 | 0.068664 | 0.75989 | -120.9137 | -120.813 | 0.80566 | 0.86517 | 0.76446 | 0.10529 | 0.004578 | 0.2243 | 121.6049 | 0.045777 | 0.05951 | 121.4172 | -0.041198 | 121.4401 | 0.71869 | -121.6095 | -120.8725 | 121.6278 | 0.8194 | 6.4224 | 0.70496
1617.3594 | 121.7239 | -0.90179 | 120.7672 | 0.005951 | 6.9778 | 0.065473 | 0.06386 | 0.0029182 | -0.0078229 | -0.00065803 | -0.0036011 | 0.002446 | 0.014178 | 0.015981 | -0.0059857 | 0.025957 | -0.0037192 | 5.5573 | 120.5795 | -0.87433 | 120.7581 | -0.68207 | -0.79651 | -0.81024 | -0.20142 | -0.13733 | -0.10071 | -0.068665 | -0.059509 | -0.086975 | -0.013733 | 0.027465 | -0.18768 | -0.009155 | 0.21973 | 0.091552 | 0.10528 | 0.064087 | 0.07782 | 0.80109 | -120.9045 | -120.8359 | 0.84228 | 0.88806 | 0.81482 | 0.086975 | 0.013733 | 0.19226 | 121.6324 | 0.041199 | 0.032043 | 121.4539 | -0.036621 | 121.4813 | 0.76446 | -121.6415 | -120.8679 | 121.6599 | 0.83313 | 6.459 | 0.70038
1619.0938 | 121.6415 | -0.96588 | 120.7626 | -0.009308 | 6.9795 | 0.065046 | 0.065783 | -0.0019952 | -0.0084637 | 0.00062377 | -0.00054933 | 0.0033004 | 0.016742 | 0.016408 | -0.011326 | 0.023821 | -0.005001 | 5.5847 | 120.5933 | -0.90637 | 120.6757 | -0.77362 | -0.85602 | -0.88806 | -0.26093 | -0.10986 | -0.1236 | -0.14648 | -0.12817 | -0.17853 | -0.059509 | 0.059509 | -0.16937 | -0.086975 | 0.19226 | 0.077819 | 0.10986 | 0.01831 | 0.050354 | 0.84228 | -120.8725 | -120.9091 | 0.83771 | 0.90637 | 0.78735 | 0.064087 | -0.054932 | 0.13275 | 121.582 | -0.004578 | -0.022888 | 121.4996 | 0.013733 | 121.5591 | 0.85602 | -121.669 | -120.8862 | 121.6415 | 0.8194 | 6.5506 | 0.70496
1620.8438 | 121.6599 | -0.98877 | 120.7718 | -0.0016785 | 6.9771 | 0.064405 | 0.064715 | 0.00078177 | -0.0071821 | -0.0030078 | -0.0036011 | 0.0037278 | 0.018878 | 0.01299 | -0.010472 | 0.025316 | -0.0035056 | 5.5664 | 120.575 | -0.94757 | 120.6528 | -0.81024 | -0.90637 | -0.90179 | -0.27466 | -0.10986 | -0.15564 | -0.14191 | -0.14191 | -0.16479 | -0.064087 | 0.041199 | -0.19684 | -0.11902 | 0.17853 | 0.086976 | 0.082398 | 0.045777 | 0.041199 | 0.83313 | -120.8817 | -120.9137 | 0.84686 | 0.92468 | 0.82398 | 0.091553 | -0.009155 | 0.13733 | 121.6003 | 0.013733 | 0.013733 | 121.5225 | 0.045777 | 121.5637 | 0.87891 | -121.7194 | -120.9274 | 121.6415 | 0.84686 | 6.5552 | 0.71411
1622.5781 | 121.7148 | -0.98419 | 120.7214 | 0.005951 | 6.9774 | 0.064619 | 0.06386 | -7.2628e-05 | -0.0076093 | -0.0015124 | 0.0055543 | 0.0011642 | 0.016101 | 0.013204 | -0.010472 | 0.024035 | -0.0047874 | 5.6488 | 120.5154 | -0.92468 | 120.7169 | -0.72784 | -0.85144 | -0.87891 | -0.19226 | -0.11902 | -0.10529 | -0.09613 | -0.10529 | -0.10986 | -0.041199 | 0.059509 | -0.20599 | -0.004578 | 0.25635 | 0.10529 | 0.13275 | 0.045777 | 0.073243 | 0.87891 | -120.8405 | -120.8176 | 0.87891 | 0.94299 | 0.87433 | 0.064087 | -0.004577 | 0.19684 | 121.6415 | 0 | 0.009156 | 121.4401 | -0.013733 | 121.4996 | 0.86517 | -121.6461 | -120.8267 | 121.701 | 0.88806 | 6.633 | 0.79193
1624.25 | 121.7285 | -1.0071 | 120.7123 | -0.0016785 | 6.9784 | 0.064405 | 0.064501 | 0.0059088 | -0.0088911 | -0.0015124 | -0.0036011 | 0.0045822 | 0.012897 | 0.006368 | -0.0057721 | 0.027239 | -0.005001 | 5.6808 | 120.5154 | -0.99792 | 120.6985 | -0.78278 | -0.9201 | -0.92468 | -0.18768 | -0.11444 | -0.11902 | -0.068665 | -0.082397 | -0.13275 | -0.036621 | 0.009155 | -0.19684 | -0.013733 | 0.2243 | 0.082397 | 0.086975 | 0.073242 | 0.07782 | 0.88806 | -120.8267 | -120.7809 | 0.92468 | 0.97046 | 0.87433 | 0.082398 | -0.013732 | 0.21515 | 121.6965 | 0.036622 | 0.050354 | 121.5134 | 0.004578 | 121.5225 | 0.89264 | -121.7102 | -120.8313 | 121.7056 | 0.93841 | 6.6879 | 0.8194
1626 | 121.701 | -1.0757 | 120.6894 | -0.009308 | 6.9797 | 0.065046 | 0.064074 | 0.00078177 | -0.0082501 | -0.00065803 | -0.0036011 | 0.005223 | 0.016955 | 0.0089316 | -0.0049175 | 0.025103 | -0.0030784 | 5.69 | 120.5475 | -1.03 | 120.5933 | -0.87433 | -1.0162 | -1.0254 | -0.24719 | -0.10986 | -0.10986 | -0.10529 | -0.15106 | -0.17853 | -0.064087 | 0.045777 | -0.14191 | -0.09613 | 0.20142 | 0.050354 | 0.05951 | 0.004577 | 0.013733 | 0.96588 | -120.7993 | -120.7947 | 0.92468 | 1.0117 | 0.89722 | 0.045776 | -0.068665 | 0.15564 | 121.6232 | -0.041199 | 0.004577 | 121.5775 | 0 | 121.6232 | 0.96588 | -121.7194 | -120.7993 | 121.669 | 0.97046 | 6.7657 | 0.82855
1627.75 | 121.8063 | -1.062 | 120.607 | -0.0016785 | 6.9774 | 0.066541 | 0.064074 | -7.2628e-05 | -0.0069683 | -0.0021532 | 0.0025025 | 0.0018052 | 0.015033 | 0.016408 | -0.0040631 | 0.026171 | -0.0041464 | 5.6763 | 120.4468 | -1.0529 | 120.6573 | -0.81024 | -0.95673 | -0.9613 | -0.11444 | -0.14648 | -0.086975 | -0.013733 | -0.036621 | -0.068665 | 0.032043 | 0.009156 | -0.16022 | 0.050354 | 0.25177 | 0.10071 | 0.10529 | 0.091552 | 0.09613 | 0.97504 | -120.7535 | -120.6207 | 1.0254 | 1.0941 | 0.99335 | 0.11902 | 0.01831 | 0.24261 | 121.7102 | 0.050354 | 0.073242 | 121.4996 | -0.059509 | 121.5088 | 0.91553 | -121.6599 | -120.694 | 121.7194 | 1.0483 | 6.7383 | 0.94757
1629.5 | 121.7102 | -1.1673 | 120.6482 | 0.005951 | 6.9799 | 0.06761 | 0.066424 | -0.00071343 | -0.0082501 | -0.00065803 | -0.0036011 | 0.0020188 | 0.014392 | 0.012563 | -0.0051313 | 0.025103 | -0.00072839 | 5.6442 | 120.4605 | -1.1169 | 120.4788 | -1.0162 | -1.1398 | -1.1307 | -0.27008 | -0.10071 | -0.1236 | -0.12817 | -0.18768 | -0.20599 | -0.041199 | 0.050354 | -0.18768 | -0.16937 | 0.15106 | 0.036621 | 0.027465 | -0.013733 | -0.022889 | 1.0437 | -120.7489 | -120.7764 | 0.97961 | 1.1261 | 0.9613 | 0.082397 | -0.082398 | 0.10071 | 121.5958 | -0.064087 | -0.004578 | 121.5775 | 0.022888 | 121.6278 | 1.0666 | -121.7651 | -120.7718 | 121.6461 | 1.0391 | 6.8115 | 0.89722
1631.1719 | 121.8155 | -1.1856 | 120.5154 | -0.0016785 | 6.9771 | 0.067396 | 0.063433 | 0.0031318 | -0.0088911 | -0.0027942 | -0.00054933 | 0.004155 | 0.015674 | 0.017476 | -0.0047039 | 0.026812 | -0.0024374 | 5.5893 | 120.3781 | -1.181 | 120.4651 | -1.0254 | -1.149 | -1.1581 | -0.17395 | -0.1236 | -0.11902 | -0.032043 | -0.050354 | -0.10529 | 0.013733 | 0.004578 | -0.13733 | -0.050354 | 0.16022 | 0.027466 | 0.036621 | 0.022888 | 0.032043 | 1.0666 | -120.639 | -120.5475 | 1.1353 | 1.1993 | 1.0803 | 0.13275 | 0.013733 | 0.15564 | 121.6461 | 0.068665 | 0.086976 | 121.5591 | -0.004577 | 121.5637 | 1.062 | -121.6965 | -120.6345 | 121.6507 | 1.1536 | 6.7749 | 1.0117
1632.9062 | 121.7468 | -1.2726 | 120.52 | -0.009308 | 6.9786 | 0.066114 | 0.065997 | 0.0061224 | -0.0056867 | -0.00023063 | -0.00054933 | 0.0043686 | 0.012897 | 0.013418 | -0.0051313 | 0.028734 | -0.0020102 | 5.6213 | 120.3323 | -1.2543 | 120.3827 | -1.1307 | -1.2451 | -1.236 | -0.27466 | -0.10529 | -0.13275 | -0.11444 | -0.16479 | -0.19684 | -0.059509 | 0.018311 | -0.18768 | -0.13733 | 0.14191 | 0.036621 | 0.027466 | 0.01831 | 0.009155 | 1.1398 | -120.6253 | -120.6345 | 1.1078 | 1.2131 | 1.0757 | 0.073242 | -0.064087 | 0.1236 | 121.637 | -0.032044 | 0.01831 | 121.5866 | 0.027465 | 121.6049 | 1.1673 | -121.7743 | -120.6528 | 121.6553 | 1.1581 | 6.8939 | 0.99792
1634.6562 | 121.8063 | -1.2863 | 120.4468 | 0.005951 | 6.9765 | 0.066114 | 0.061938 | 0.00056817 | -0.0082501 | -0.0032214 | -0.0036011 | 0.000737 | 0.01781 | 0.018117 | -0.0059857 | 0.025316 | -0.00030119 | 5.603 | 120.282 | -1.2497 | 120.4193 | -1.0666 | -1.1856 | -1.2039 | -0.21973 | -0.12817 | -0.09613 | -0.07782 | -0.086975 | -0.091553 | -0.009155 | 0.036621 | -0.16479 | -0.027465 | 0.21973 | 0.082398 | 0.10071 | 0.045777 | 0.064087 | 1.1902 | -120.575 | -120.5246 | 1.1993 | 1.2772 | 1.1948 | 0.086975 | 0.004577 | 0.18311 | 121.669 | 0.009155 | 0.01831 | 121.5317 | -0.032044 | 121.5683 | 1.1581 | -121.6965 | -120.5429 | 121.7056 | 1.2085 | 6.8893 | 1.0666
1636.3438 | 121.8704 | -1.2863 | 120.4239 | -0.0016785 | 6.9767 | 0.066755 | 0.063647 | -0.00028623 | -0.0082501 | -0.0019396 | -0.00054933 | 0.0020188 | 0.014819 | 0.023672 | -0.0074811 | 0.024889 | 0.00076681 | 5.6808 | 120.2133 | -1.2589 | 120.4742 | -1.0117 | -1.1307 | -1.1719 | -0.11444 | -0.13733 | -0.10529 | -0.009155 | 0 | -0.032043 | 0.036621 | 0.027466 | -0.21057 | 0.050354 | 0.27466 | 0.11444 | 0.15564 | 0.086975 | 0.12817 | 1.181 | -120.5612 | -120.433 | 1.2863 | 1.3229 | 1.2543 | 0.14191 | 0.073243 | 0.24719 | 121.7331 | 0.10529 | 0.096131 | 121.4722 | -0.032043 | 121.4996 | 1.149 | -121.6827 | -120.5292 | 121.7606 | 1.2772 | 6.9672 | 1.1719
1638.0781 | 121.8521 | -1.7578 | 119.9661 | -0.0016785 | 6.9754 | 0.066541 | 0.064501 | -0.00028623 | -0.0054731 | -0.0019396 | 0.0025025 | 0.0028732 | 0.017383 | 0.015981 | -0.0061993 | 0.025103 | -0.0017966 | 5.5344 | 119.7968 | -1.7258 | 119.9478 | -1.5564 | -1.6479 | -1.6754 | -0.19226 | -0.12817 | -0.11444 | -0.036621 | -0.073242 | -0.082397 | 0.022888 | 0.032043 | -0.16937 | -0.01831 | 0.20142 | 0.082397 | 0.10986 | 0.050354 | 0.07782 | 1.6434 | -120.0943 | -120.0027 | 1.6846 | 1.7807 | 1.6754 | 0.13733 | 0.032044 | 0.16937 | 121.6736 | 0.041199 | 0.07782 | 121.5225 | -0.013733 | 121.5546 | 1.6296 | -121.6919 | -120.0806 | 121.7056 | 1.7212 | 7.2922 | 1.5656
1639.8281 | 121.8613 | -1.9547 | 119.7464 | -0.0016785 | 6.9778 | 0.064405 | 0.062365 | 0.0031318 | -0.0078229 | -0.0012988 | 0.0025025 | 0.0015914 | 0.013751 | 0.01235 | -0.0089765 | 0.024035 | -0.0013694 | 5.5984 | 119.545 | -1.9089 | 119.8288 | -1.6617 | -1.7853 | -1.8082 | -0.10071 | -0.15106 | -0.091553 | 0.004578 | 0.004578 | -0.022888 | 0.045776 | 0.045776 | -0.20142 | 0.082397 | 0.29297 | 0.14648 | 0.16937 | 0.10071 | 0.1236 | 1.8631 | -119.8975 | -119.7418 | 1.9592 | 2.0004 | 1.9318 | 0.13733 | 0.068665 | 0.24719 | 121.7377 | 0.096131 | 0.096131 | 121.4539 | -0.059509 | 121.4996 | 1.8036 | -121.6553 | -119.838 | 121.7834 | 1.9592 | 7.5531 | 1.8539
1641.5781 | 121.8292 | -2.005 | 119.6915 | 0.005951 | 6.9769 | 0.065901 | 0.062365 | -0.0030634 | -0.0071821 | -0.0030078 | -0.00054933 | 0.0011642 | 0.016955 | 0.022176 | -0.0083355 | 0.024676 | 0.00055321 | 5.4932 | 119.5633 | -1.9638 | 119.7006 | -1.7944 | -1.9226 | -1.9363 | -0.2243 | -0.1236 | -0.11444 | -0.07782 | -0.086975 | -0.11444 | -0.027466 | 0.041199 | -0.12817 | 0.009156 | 0.21057 | 0.068665 | 0.082398 | 0.027466 | 0.041199 | 1.8906 | -119.8151 | -119.7693 | 1.918 | 1.9775 | 1.8906 | 0.086975 | 0 | 0.16937 | 121.6644 | 0.027466 | 0.036621 | 121.5271 | -0.009155 | 121.5683 | 1.8814 | -121.6553 | -119.8059 | 121.7056 | 1.9272 | 7.4982 | 1.7807
1643.25 | 121.8384 | -2.0187 | 119.7098 | -0.0016785 | 6.9769 | 0.066541 | 0.062579 | 0.0027044 | -0.0069683 | 0.00019657 | 0.0025025 | 0.0018052 | 0.017169 | 0.014486 | -0.0068403 | 0.024889 | -0.0013694 | 5.5252 | 119.5175 | -2.0004 | 119.6869 | -1.8356 | -1.9501 | -1.9501 | -0.19226 | -0.1236 | -0.11902 | -0.045776 | -0.073242 | -0.086975 | -0.004578 | 0.018311 | -0.19226 | -0.022888 | 0.18311 | 0.068665 | 0.068665 | 0.050354 | 0.050354 | 1.8997 | -119.8334 | -119.7556 | 1.9455 | 2.0142 | 1.9318 | 0.11444 | 0.032044 | 0.1648 | 121.6873 | 0.045777 | 0.073243 | 121.5179 | -0.004577 | 121.5363 | 1.8951 | -121.7102 | -119.8288 | 121.7056 | 1.973 | 7.5439 | 1.8265
1644.9375 | 121.7377 | -2.0874 | 119.7281 | -0.009308 | 6.9789 | 0.068464 | 0.063433 | -0.00049983 | -0.0059003 | -0.0019396 | -0.00054933 | 0.0045822 | 0.015033 | 0.017049 | -0.0057721 | 0.025957 | -0.002651 | 5.5115 | 119.5633 | -2.0233 | 119.6091 | -1.9501 | -2.0645 | -2.0645 | -0.29297 | -0.082397 | -0.13275 | -0.14648 | -0.17853 | -0.21515 | -0.07782 | 0.064087 | -0.16479 | -0.11902 | 0.13733 | 0.022888 | 0.022888 | -0.041199 | -0.041199 | 1.9547 | -119.8105 | -119.8746 | 1.9089 | 2.0096 | 1.8723 | 0.054931 | -0.082398 | 0.073242 | 121.6324 | -0.045777 | -0.013733 | 121.5866 | 0.050354 | 121.6507 | 2.005 | -121.7514 | -119.8608 | 121.6965 | 1.9409 | 7.5989 | 1.7944
1646.6719 | 121.8063 | -2.0737 | 119.6777 | 0.005951 | 6.9801 | 0.066114 | 0.065356 | 0.0039862 | -0.0073957 | 0.00062377 | 0.0025025 | 0.0037278 | 0.01781 | 0.0095724 | -0.0083355 | 0.025103 | -0.0041464 | 5.5893 | 119.5358 | -2.0462 | 119.6503 | -1.8814 | -1.9913 | -2.0233 | -0.17395 | -0.1236 | -0.11902 | -0.045776 | -0.073242 | -0.11902 | -0.022888 | 0.027465 | -0.14191 | -0.027465 | 0.19226 | 0.050354 | 0.082397 | 0.022889 | 0.054932 | 1.9547 | -119.8013 | -119.7235 | 2.0004 | 2.0508 | 1.9547 | 0.096131 | 0 | 0.16479 | 121.6965 | 0.045777 | 0.073243 | 121.582 | -0.004577 | 121.6095 | 1.9501 | -121.7239 | -119.7968 | 121.7239 | 2.0279 | 7.663 | 1.8997
1648.4062 | 121.8155 | -2.1103 | 119.6915 | -0.0016785 | 6.9806 | 0.065046 | 0.064288 | -0.00049983 | -0.0052595 | -1.7026e-05 | -0.00054933 | 0.002446 | 0.01311 | 0.013204 | -0.0068403 | 0.025744 | -0.0037192 | 5.571 | 119.5267 | -2.0645 | 119.664 | -1.8814 | -2.0142 | -2.0233 | -0.19684 | -0.11444 | -0.12817 | -0.050354 | -0.073242 | -0.12817 | -0.018311 | 0.045777 | -0.16479 | -0.027466 | 0.22888 | 0.086976 | 0.096131 | 0.041199 | 0.050354 | 1.9821 | -119.8059 | -119.7418 | 2.037 | 2.092 | 1.9821 | 0.10986 | 0 | 0.1831 | 121.7285 | 0.054932 | 0.07782 | 121.5912 | 0.013733 | 121.637 | 1.9959 | -121.756 | -119.8196 | 121.7743 | 2.0599 | 7.6813 | 1.9135
1650.1562 | 121.8521 | -2.1103 | 119.6228 | -0.009308 | 6.9765 | 0.065901 | 0.061724 | 0.0016364 | -0.0071821 | -0.0049304 | -0.00054933 | 0.0022324 | 0.017383 | 0.015981 | -0.0044903 | 0.026171 | -0.0020102 | 5.4932 | 119.5084 | -2.0874 | 119.5953 | -1.9363 | -2.0691 | -2.0828 | -0.19226 | -0.12817 | -0.10529 | -0.032043 | -0.045776 | -0.09613 | 0.045776 | 0.022889 | -0.11444 | -0.027466 | 0.17395 | 0.027466 | 0.041199 | 0.004577 | 0.01831 | 2.005 | -119.751 | -119.6548 | 2.0645 | 2.1561 | 2.0142 | 0.15106 | 0.009156 | 0.15106 | 121.6827 | 0.05951 | 0.073243 | 121.5958 | -0.022888 | 121.6187 | 1.9821 | -121.7102 | -119.7281 | 121.7056 | 2.0782 | 7.6035 | 1.918
1651.8906 | 121.7514 | -2.1103 | 119.7052 | 0.005951 | 6.9791 | 0.064619 | 0.064074 | -0.003277 | -0.0086773 | -0.0040758 | 0.0086061 | 0.0018052 | 0.016955 | 0.0078634 | -0.011113 | 0.024889 | -0.006069 | 5.5481 | 119.5267 | -2.0554 | 119.5816 | -1.9318 | -2.0187 | -2.0508 | -0.27466 | -0.09613 | -0.14648 | -0.13733 | -0.14648 | -0.17395 | -0.059509 | 0.054932 | -0.17853 | -0.1236 | 0.17853 | 0.05951 | 0.091553 | 0.004578 | 0.036621 | 1.9638 | -119.8013 | -119.8425 | 1.9638 | 2.0508 | 1.9363 | 0.086975 | -0.027466 | 0.1236 | 121.637 | 0 | 0.009155 | 121.582 | 0.050354 | 121.637 | 2.0142 | -121.7606 | -119.8517 | 121.6919 | 1.973 | 7.6584 | 1.8356
1653.5625 | 121.8201 | -2.0325 | 119.7052 | 0.005951 | 6.9799 | 0.065901 | 0.063433 | 0.00056817 | -0.0056867 | -0.006853 | 0.0025025 | 0.0020188 | 0.016101 | 0.015981 | -0.0059857 | 0.025957 | 0.00055321 | 5.5344 | 119.5908 | -2.0233 | 119.6274 | -1.8951 | -2.0233 | -2.0233 | -0.21515 | -0.11444 | -0.12817 | -0.054932 | -0.10529 | -0.13733 | -0.009155 | 0.009156 | -0.11444 | -0.07782 | 0.13733 | 0.009156 | 0.009156 | 0 | 0 | 1.9043 | -119.8196 | -119.7601 | 1.9272 | 2.0233 | 1.8951 | 0.11902 | -0.009155 | 0.12817 | 121.6507 | 0.022888 | 0.073242 | 121.6141 | 0.013733 | 121.6232 | 1.918 | -121.7285 | -119.8334 | 121.6599 | 1.9775 | 7.5668 | 1.8173
1655.3125 | 121.788 | -2.0599 | 119.7464 | 0.005951 | 6.978 | 0.064832 | 0.06386 | 0.0029182 | -0.0076093 | -0.00065803 | -0.00054933 | 0.0020188 | 0.01311 | 0.010854 | -0.0083355 | 0.023394 | -0.0011558 | 5.5618 | 119.5908 | -2.0279 | 119.6365 | -1.9089 | -1.9913 | -2.0187 | -0.25635 | -0.082397 | -0.13733 | -0.11902 | -0.13733 | -0.14191 | -0.050354 | 0.032044 | -0.15564 | -0.10986 | 0.15106 | 0.041199 | 0.068665 | 0.009155 | 0.036621 | 1.9226 | -119.8288 | -119.8654 | 1.9226 | 2.0096 | 1.918 | 0.086975 | -0.004578 | 0.11902 | 121.6644 | 0 | 0.01831 | 121.6187 | 0.054932 | 121.6507 | 1.9775 | -121.7743 | -119.8837 | 121.6965 | 1.9409 | 7.6218 | 1.8036
1656.9844 | 121.8887 | -2.0325 | 119.7144 | -0.0016785 | 6.9769 | 0.066755 | 0.062579 | 0.0046272 | -0.0073957 | -0.0055712 | -0.0036011 | 0.000737 | 0.015033 | 0.022817 | -0.0053449 | 0.026812 | -0.0045736 | 5.5984 | 119.545 | -2.0096 | 119.7235 | -1.7899 | -1.9272 | -1.9547 | -0.11444 | -0.13275 | -0.086975 | 0.009155 | -0.009155 | -0.050354 | 0.032043 | 0.022888 | -0.16937 | 0.009156 | 0.24262 | 0.07782 | 0.10529 | 0.054932 | 0.082398 | 1.9455 | -119.8471 | -119.7052 | 2.0233 | 2.0645 | 1.9821 | 0.11902 | 0.036621 | 0.21973 | 121.7331 | 0.07782 | 0.09613 | 121.5546 | -0.045776 | 121.5775 | 1.8997 | -121.7239 | -119.8013 | 121.756 | 2.0416 | 7.6309 | 1.918
1658.7188 | 121.8475 | -2.0325 | 119.7235 | -0.0016785 | 6.9801 | 0.066114 | 0.064501 | 0.0056952 | -0.0067547 | -0.00065803 | -0.0036011 | 0.0015914 | 0.016314 | 0.012777 | -0.0042767 | 0.026171 | -0.0041464 | 5.5573 | 119.5953 | -2.0233 | 119.6503 | -1.8814 | -2.0187 | -2.0233 | -0.2243 | -0.10986 | -0.13275 | -0.059509 | -0.091553 | -0.13733 | -0.013733 | 0.009156 | -0.12817 | -0.073242 | 0.15106 | 0.009156 | 0.013733 | 0 | 0.004577 | 1.8997 | -119.8334 | -119.783 | 1.9409 | 2.0187 | 1.8951 | 0.11902 | -0.004578 | 0.14191 | 121.6736 | 0.041198 | 0.073242 | 121.6187 | 0.022888 | 121.6278 | 1.9226 | -121.7468 | -119.8563 | 121.6827 | 1.973 | 7.5897 | 1.8082
1660.4688 | 121.8933 | -1.9913 | 119.7418 | 0.01358 | 6.9784 | 0.06825 | 0.063433 | -7.2628e-05 | -0.0039777 | -0.0019396 | 0.0055543 | 0.0026596 | 0.018878 | 0.021749 | -0.0066265 | 0.027453 | -0.0028646 | 5.6763 | 119.5999 | -1.9455 | 119.7922 | -1.7166 | -1.8768 | -1.8768 | -0.10986 | -0.13733 | -0.09613 | 0 | -0.032043 | -0.068665 | 0.022888 | 0.045776 | -0.14191 | 0.050354 | 0.27466 | 0.11444 | 0.11444 | 0.068665 | 0.068665 | 1.8951 | -119.8791 | -119.7418 | 1.9592 | 2.0142 | 1.9226 | 0.11902 | 0.027465 | 0.22888 | 121.7377 | 0.064087 | 0.09613 | 121.5454 | -0.041199 | 121.5912 | 1.8539 | -121.6873 | -119.838 | 121.7834 | 1.9913 | 7.6675 | 1.8814
1662.1406 | 121.8521 | -1.9684 | 119.7922 | -0.009308 | 6.9769 | 0.06526 | 0.062151 | 0.00035457 | -0.0059003 | -0.0032214 | -0.00054933 | 0.0011642 | 0.014605 | 0.015554 | -0.0087629 | 0.027025 | 0.0011942 | 5.658 | 119.6457 | -1.9272 | 119.7876 | -1.7212 | -1.8768 | -1.886 | -0.13733 | -0.1236 | -0.10529 | -0.050354 | -0.059509 | -0.073242 | 0.004578 | 0.041199 | -0.14648 | -0.004577 | 0.24719 | 0.082398 | 0.091553 | 0.041199 | 0.050354 | 1.8631 | -119.9158 | -119.8425 | 1.9089 | 1.973 | 1.8951 | 0.10986 | 0.032044 | 0.20599 | 121.7148 | 0.045777 | 0.054932 | 121.5729 | -0.01831 | 121.6141 | 1.8448 | -121.7194 | -119.8975 | 121.756 | 1.918 | 7.6263 | 1.8311
1663.875 | 121.7697 | -1.9547 | 119.8563 | -0.0016785 | 6.9797 | 0.066541 | 0.063647 | 0.0091132 | -0.0069683 | 0.00019657 | -0.0036011 | 0.0043686 | 0.014178 | 0.016836 | -0.0096173 | 0.027453 | 0.00033961 | 5.7312 | 119.7006 | -1.9089 | 119.7601 | -1.799 | -1.9135 | -1.9363 | -0.25177 | -0.091553 | -0.13275 | -0.11444 | -0.13733 | -0.19226 | -0.068665 | 0.045776 | -0.15564 | -0.09613 | 0.15564 | 0.018311 | 0.041199 | -0.027465 | -0.004577 | 1.8219 | -119.9478 | -119.9707 | 1.8173 | 1.886 | 1.7624 | 0.064086 | -0.05951 | 0.10986 | 121.669 | -0.004578 | 0.01831 | 121.6095 | 0.041198 | 121.6553 | 1.8631 | -121.7651 | -119.989 | 121.7148 | 1.8402 | 7.6859 | 1.7029
1665.625 | 121.8933 | -1.9501 | 119.838 | 0.005951 | 6.9761 | 0.064405 | 0.06322 | -0.0019952 | -0.0046185 | -0.0019396 | -0.00054933 | -0.000972 | 0.016742 | 0.0095724 | -0.0072675 | 0.025316 | -0.0020102 | 5.7083 | 119.6548 | -1.8997 | 119.7968 | -1.7303 | -1.8448 | -1.8539 | -0.18768 | -0.11902 | -0.11902 | -0.045776 | -0.041199 | -0.059509 | 0.013733 | 0.050354 | -0.18311 | -0.041199 | 0.21973 | 0.09613 | 0.10528 | 0.045776 | 0.054931 | 1.8311 | -119.957 | -119.8837 | 1.9089 | 1.9638 | 1.8906 | 0.13275 | 0.05951 | 0.16937 | 121.6965 | 0.07782 | 0.073243 | 121.5546 | 0 | 121.6049 | 1.8311 | -121.7377 | -119.957 | 121.7468 | 1.9043 | 7.6584 | 1.7624
1667.2969 | 121.8521 | -1.7532 | 119.9982 | -0.0016785 | 6.9767 | 0.065046 | 0.063006 | -0.0022088 | -0.0073957 | -0.0015124 | -0.00054933 | 9.6204e-05 | 0.013965 | 0.023458 | -0.0072675 | 0.026385 | -0.0030784 | 5.7266 | 119.8563 | -1.6983 | 119.9799 | -1.561 | -1.6708 | -1.7075 | -0.20142 | -0.12817 | -0.11902 | -0.068665 | -0.082397 | -0.10071 | -0.013733 | 0.054932 | -0.14191 | -0.018311 | 0.19226 | 0.045777 | 0.082398 | -0.009155 | 0.027466 | 1.6342 | -120.1263 | -120.0668 | 1.6708 | 1.7395 | 1.6525 | 0.10529 | 0.018311 | 0.13733 | 121.6782 | 0.036622 | 0.050354 | 121.5546 | -0.009155 | 121.6095 | 1.6251 | -121.6965 | -120.1172 | 121.7331 | 1.6846 | 7.4799 | 1.5518
1669.0469 | 121.7972 | -1.5656 | 120.2728 | -0.009308 | 6.9801 | 0.064405 | 0.064929 | 0.0033454 | -0.0071821 | -0.001726 | 0.0025025 | 0.003514 | 0.01546 | 0.01299 | -0.0064129 | 0.025103 | -0.0024374 | 5.7175 | 120.1401 | -1.506 | 120.1401 | -1.4145 | -1.5289 | -1.5472 | -0.2655 | -0.10071 | -0.13733 | -0.10986 | -0.16937 | -0.19684 | -0.068665 | 0.05951 | -0.13275 | -0.13275 | 0.15106 | 0.018311 | 0.036621 | -0.041199 | -0.022889 | 1.4282 | -120.3735 | -120.3827 | 1.3962 | 1.4969 | 1.3687 | 0.068664 | -0.059509 | 0.091552 | 121.6461 | -0.032044 | 0.027466 | 121.6461 | 0.036621 | 121.7056 | 1.4648 | -121.7789 | -120.4102 | 121.7056 | 1.4557 | 7.283 | 1.3
1670.7969 | 121.907 | -1.7258 | 119.9982 | -0.0016785 | 6.9803 | 0.068678 | 0.061511 | 0.0024908 | -0.0052595 | 0.00019657 | -0.00054933 | 0.0033004 | 0.014392 | 0.020254 | -0.0025677 | 0.029375 | -0.002651 | 5.7175 | 119.838 | -1.7166 | 120.0394 | -1.4969 | -1.6251 | -1.6388 | -0.10529 | -0.14191 | -0.11902 | 0 | -0.018311 | -0.068665 | 0.045776 | 0.009155 | -0.16022 | 0.041199 | 0.22888 | 0.086975 | 0.10071 | 0.07782 | 0.091553 | 1.6068 | -120.1401 | -119.9982 | 1.7075 | 1.7715 | 1.6571 | 0.16479 | 0.050354 | 0.21973 | 121.756 | 0.10071 | 0.11902 | 121.5546 | -0.022888 | 121.5637 | 1.5839 | -121.7148 | -120.1172 | 121.7651 | 1.7258 | 7.4432 | 1.6205
1672.5469 | 121.7743 | -1.5884 | 120.2682 | -0.0016785 | 6.9808 | 0.06761 | 0.064501 | 0.0056952 | -0.0078229 | -0.0030078 | 0.0025025 | 0.002446 | 0.018878 | 0.012777 | -0.0087629 | 0.024676 | -0.0011558 | 5.7358 | 120.0989 | -1.5518 | 120.1355 | -1.4328 | -1.5564 | -1.5701 | -0.28381 | -0.09613 | -0.14191 | -0.12817 | -0.1831 | -0.21057 | -0.073242 | 0.036621 | -0.16937 | -0.13275 | 0.15564 | 0.018311 | 0.032044 | -0.01831 | -0.004577 | 1.4465 | -120.3644 | -120.3964 | 1.4053 | 1.5152 | 1.3779 | 0.068665 | -0.068664 | 0.11902 | 121.6873 | -0.041198 | 0.013733 | 121.6507 | 0.045777 | 121.6873 | 1.4923 | -121.8201 | -120.4102 | 121.7239 | 1.4603 | 7.3242 | 1.3046
1674.2188 | 121.8887 | -1.5198 | 120.2637 | 0.02121 | 6.9791 | 0.065687 | 0.065997 | 0.0024908 | -0.0061139 | -0.0019396 | 0.0025025 | 0.0020188 | 0.015674 | 0.01534 | -0.0076947 | 0.026171 | -0.0037192 | 5.7999 | 120.0806 | -1.5427 | 120.1813 | -1.3824 | -1.5106 | -1.5106 | -0.19226 | -0.10071 | -0.1236 | -0.050354 | -0.073242 | -0.10986 | 0.004578 | -0.022889 | -0.18311 | -0.082398 | 0.13733 | 0.009155 | 0.009155 | 0.032044 | 0.032044 | 1.3962 | -120.3644 | -120.314 | 1.4465 | 1.5244 | 1.4099 | 0.12817 | 0.013733 | 0.16022 | 121.7239 | 0.050354 | 0.073242 | 121.6232 | 0.022888 | 121.6003 | 1.4191 | -121.8063 | -120.3873 | 121.701 | 1.4694 | 7.3196 | 1.3275
1675.9062 | 121.8567 | -1.4832 | 120.3461 | -0.009308 | 6.9795 | 0.06761 | 0.061511 | 0.003559 | -0.0078229 | -0.002367 | 0.0025025 | 0.000737 | 0.01546 | 0.010427 | -0.010258 | 0.026598 | -0.0024374 | 5.8319 | 120.0623 | -1.4694 | 120.3003 | -1.2543 | -1.3275 | -1.3504 | -0.14648 | -0.11902 | -0.11444 | -0.050354 | -0.045776 | -0.073242 | -0.004578 | 0.013733 | -0.28381 | -0.045776 | 0.22888 | 0.13275 | 0.15564 | 0.11902 | 0.14191 | 1.3687 | -120.4651 | -120.3964 | 1.4374 | 1.4786 | 1.4099 | 0.10986 | 0.041199 | 0.21515 | 121.7697 | 0.068665 | 0.064087 | 121.5317 | -0.004578 | 121.5454 | 1.3641 | -121.8155 | -120.4605 | 121.7834 | 1.4328 | 7.3151 | 1.3367
1677.6562 | 121.9162 | -0.93384 | 120.8267 | 0.005951 | 6.9782 | 0.065473 | 0.062792 | 0.0031318 | -0.0046185 | -0.002367 | 0.0025025 | 0.0037278 | 0.014605 | 0.017263 | -0.0040631 | 0.024676 | -0.006069 | 5.9601 | 120.6757 | -0.90179 | 120.8633 | -0.70496 | -0.82398 | -0.85144 | -0.11902 | -0.15106 | -0.10071 | 0.009155 | -0.032043 | -0.068665 | 0.045776 | 0.032044 | -0.15106 | 0.036621 | 0.22888 | 0.082398 | 0.10986 | 0.050354 | 0.077819 | 0.83313 | -120.9778 | -120.8176 | 0.90179 | 0.97961 | 0.86517 | 0.14648 | 0.032043 | 0.19684 | 121.7651 | 0.068665 | 0.10986 | 121.5775 | -0.050354 | 121.6095 | 0.78278 | -121.7285 | -120.9274 | 121.7972 | 0.94299 | 6.8939 | 0.81482
1679.3906 | 121.8979 | -0.87433 | 120.8862 | 0.01358 | 6.9801 | 0.066541 | 0.06322 | 0.0037726 | -0.0039777 | -0.0032214 | 0.0025025 | 0.0020188 | 0.017383 | 0.012563 | -0.0072675 | 0.027239 | -0.003292 | 5.9692 | 120.7535 | -0.81482 | 120.9503 | -0.60425 | -0.737 | -0.76904 | -0.11444 | -0.1236 | -0.11444 | -0.009155 | -0.022888 | -0.064087 | 0.013733 | 0.05951 | -0.13275 | 0.064087 | 0.27008 | 0.10529 | 0.13733 | 0.045776 | 0.077819 | 0.75989 | -121.0098 | -120.8954 | 0.85144 | 0.88806 | 0.81024 | 0.12817 | 0.050354 | 0.21057 | 121.7651 | 0.091553 | 0.10529 | 121.5683 | -0.009155 | 121.6278 | 0.75073 | -121.701 | -121.0007 | 121.8246 | 0.86517 | 6.8436 | 0.75989
1681.0625 | 121.9162 | -0.97504 | 120.7855 | -0.009308 | 6.9771 | 0.067182 | 0.061938 | 0.00078177 | -0.0076093 | -0.0045032 | -0.00054933 | 0.0020188 | 0.016955 | 0.014486 | -0.0089765 | 0.025744 | -0.0039328 | 5.9052 | 120.575 | -0.96588 | 120.7947 | -0.70953 | -0.81482 | -0.84686 | -0.10529 | -0.13733 | -0.10529 | -0.018311 | 0.004578 | -0.036621 | 0.022888 | 0.009156 | -0.21057 | 0.009156 | 0.2655 | 0.12817 | 0.16022 | 0.11902 | 0.15106 | 0.86975 | -120.9229 | -120.8038 | 0.97962 | 0.99793 | 0.93842 | 0.12817 | 0.068665 | 0.25635 | 121.7606 | 0.10986 | 0.086975 | 121.5408 | -0.032043 | 121.55 | 0.83771 | -121.7514 | -120.8908 | 121.7697 | 0.95673 | 6.8802 | 0.86975
1682.8125 | 121.9254 | -0.98419 | 120.8038 | 0.005951 | 6.9761 | 0.066114 | 0.064715 | -0.0047724 | -0.0071821 | -0.0036486 | -0.0036011 | 0.0020188 | 0.015887 | 0.017476 | -0.0098309 | 0.026812 | -0.002651 | 5.9647 | 120.6116 | -0.9613 | 120.8038 | -0.75073 | -0.83313 | -0.86517 | -0.12817 | -0.14648 | -0.09613 | -0.004578 | -0.013733 | -0.045776 | 0.036621 | 0.022888 | -0.19226 | 0 | 0.23346 | 0.11902 | 0.15106 | 0.096131 | 0.12817 | 0.88806 | -120.9503 | -120.8084 | 0.97046 | 1.0208 | 0.93842 | 0.13275 | 0.050354 | 0.21057 | 121.7651 | 0.082397 | 0.091552 | 121.5729 | -0.050354 | 121.5958 | 0.83771 | -121.7651 | -120.9 | 121.788 | 0.97961 | 6.9489 | 0.85602
1684.4844 | 121.843 | -0.90637 | 120.9412 | -0.0016785 | 6.9754 | 0.064405 | 0.062365 | 0.00035457 | -0.0063275 | -0.0015124 | 0.0025025 | 0.0037278 | 0.013965 | 0.013845 | -0.0083355 | 0.024462 | -0.0071372 | 5.9692 | 120.8267 | -0.8194 | 120.9045 | -0.68665 | -0.77362 | -0.79651 | -0.25177 | -0.09613 | -0.14648 | -0.091553 | -0.10986 | -0.16022 | -0.041199 | 0.086975 | -0.11444 | -0.036621 | 0.21973 | 0.10986 | 0.13275 | 0.022888 | 0.045776 | 0.75989 | -121.0373 | -121.0327 | 0.79651 | 0.86517 | 0.74615 | 0.10529 | -0.013733 | 0.13275 | 121.7239 | 0.036621 | 0.054931 | 121.6461 | 0.050354 | 121.7331 | 0.81024 | -121.7606 | -121.0876 | 121.8109 | 0.81482 | 6.8756 | 0.6546
1686.2188 | 121.8292 | -0.66376 | 121.1792 | 0.005951 | 6.9782 | 0.066969 | 0.062151 | 0.0027044 | -0.0054731 | 0.00019657 | -0.00054933 | 0.0028732 | 0.015033 | 0.013418 | -0.0079083 | 0.024035 | -0.003292 | 6.0333 | 121.0419 | -0.59052 | 121.1014 | -0.48981 | -0.55847 | -0.59052 | -0.2655 | -0.086975 | -0.1236 | -0.09613 | -0.11444 | -0.16937 | -0.050354 | 0.073242 | -0.13733 | -0.07782 | 0.17395 | 0.073242 | 0.10529 | 0 | 0.032043 | 0.54016 | -121.2662 | -121.2753 | 0.54932 | 0.6134 | 0.49438 | 0.073242 | -0.045777 | 0.10071 | 121.6919 | 0.009155 | 0.027466 | 121.6324 | 0.036621 | 121.7056 | 0.57678 | -121.7697 | -121.3028 | 121.7651 | 0.56763 | 6.6971 | 0.39825
1687.9531 | 121.8246 | -0.92468 | 120.9457 | -0.0016785 | 6.9776 | 0.065046 | 0.064074 | 0.00035457 | -0.0091047 | -0.0010852 | 0.0025025 | 0.0022324 | 0.015674 | 0.011922 | -0.0087629 | 0.024035 | -0.0045736 | 5.9418 | 120.8496 | -0.8194 | 120.8542 | -0.71869 | -0.78278 | -0.81024 | -0.27466 | -0.086975 | -0.14648 | -0.10071 | -0.1236 | -0.16937 | -0.041199 | 0.10529 | -0.096131 | -0.091553 | 0.20599 | 0.11444 | 0.14191 | 0.009155 | 0.036621 | 0.7782 | -121.0327 | -121.0464 | 0.80109 | 0.88348 | 0.75531 | 0.10529 | -0.022889 | 0.10071 | 121.6736 | 0.022888 | 0.045776 | 121.669 | 0.059509 | 121.7743 | 0.83771 | -121.7651 | -121.0922 | 121.7789 | 0.82398 | 6.8665 | 0.65003
1689.6875 | 121.788 | -0.83313 | 121.0327 | -0.009308 | 6.9784 | 0.064405 | 0.063006 | -0.002636 | -0.0082501 | -0.00087163 | 0.0025025 | 0.0030868 | 0.018237 | 0.0078634 | -0.0089765 | 0.024462 | -0.0024374 | 5.9601 | 120.9137 | -0.76446 | 120.9183 | -0.63171 | -0.71411 | -0.72327 | -0.29755 | -0.10071 | -0.15106 | -0.13733 | -0.15564 | -0.17395 | -0.091553 | 0.068665 | -0.11902 | -0.11444 | 0.20142 | 0.10986 | 0.11902 | 0.041198 | 0.050354 | 0.68207 | -121.1334 | -121.17 | 0.67749 | 0.74158 | 0.65918 | 0.059509 | -0.022888 | 0.13275 | 121.6827 | -0.004578 | 0.013733 | 121.6782 | 0.050354 | 121.7468 | 0.73242 | -121.7972 | -121.1838 | 121.7514 | 0.6958 | 6.7932 | 0.53558
1691.4219 | 121.7926 | -0.73242 | 121.0922 | 0.005951 | 6.9793 | 0.064405 | 0.06386 | -0.0011408 | -0.0080365 | -0.0042896 | 0.0055543 | 0.0037278 | 0.016314 | 0.010641 | -0.0074811 | 0.024462 | -0.0039328 | 6.0516 | 120.9778 | -0.64545 | 121.0464 | -0.53101 | -0.65918 | -0.6546 | -0.25177 | -0.09613 | -0.1236 | -0.11902 | -0.14648 | -0.20142 | -0.073242 | 0.086975 | -0.11444 | -0.045776 | 0.20142 | 0.07782 | 0.073242 | -0.009155 | -0.013733 | 0.60883 | -121.1884 | -121.2112 | 0.58594 | 0.65918 | 0.53101 | 0.050354 | -0.07782 | 0.11444 | 121.6919 | -0.022888 | 0.004577 | 121.6232 | 0.027466 | 121.7102 | 0.63629 | -121.7377 | -121.2158 | 121.7789 | 0.6134 | 6.7841 | 0.48065
1693.1562 | 121.8567 | -0.74616 | 121.0464 | 0.005951 | 6.9759 | 0.065046 | 0.062792 | 0.0039862 | -0.0071821 | -0.00087163 | 0.0055543 | -0.000972 | 0.013537 | 0.0074362 | -0.0051313 | 0.02318 | -0.0030784 | 6.0287 | 120.9366 | -0.65918 | 121.0556 | -0.50812 | -0.62256 | -0.64545 | -0.23804 | -0.13733 | -0.1236 | -0.068665 | -0.073242 | -0.13275 | -0.018311 | 0.086975 | -0.10986 | 0.009155 | 0.23804 | 0.10071 | 0.1236 | 0.013733 | 0.036621 | 0.62256 | -121.1838 | -121.1151 | 0.67291 | 0.72784 | 0.6134 | 0.10528 | -0.009155 | 0.15106 | 121.7148 | 0.050354 | 0.054931 | 121.5958 | -0.013733 | 121.6827 | 0.60883 | -121.7056 | -121.17 | 121.8018 | 0.67749 | 6.7749 | 0.50812
1694.8438 | 121.9208 | -1.1124 | 120.6802 | 0.005951 | 6.9765 | 0.063978 | 0.06087 | -0.00049983 | -0.0076093 | -0.0036486 | -0.00054933 | 0.0011642 | 0.01311 | 0.008718 | -0.0061993 | 0.025744 | -0.0073508 | 5.8365 | 120.2774 | -1.2268 | 120.5841 | -0.84228 | -0.93384 | -1.0666 | -0.11444 | -0.14191 | -0.091553 | -0.013733 | -0.004578 | -0.041199 | 0.018311 | -0.11444 | -0.40283 | -0.096131 | 0.27008 | 0.045777 | 0.17853 | 0.16022 | 0.29297 | 1.0208 | -120.8221 | -120.694 | 1.1078 | 1.1307 | 1.0712 | 0.10986 | 0.050354 | 0.38452 | 121.8109 | 0.086975 | 0.07782 | 121.5042 | -0.050354 | 121.3898 | 0.97046 | -121.907 | -120.7718 | 121.6965 | 1.0986 | 6.9489 | 0.99792
1696.5938 | 121.8658 | -0.60883 | 121.225 | -0.016937 | 6.9784 | 0.064405 | 0.062579 | 0.0031318 | -0.0071821 | -0.0025806 | -0.00054933 | 0.000737 | 0.012683 | 0.011495 | -0.0085491 | 0.025957 | -0.00072839 | 6.102 | 121.0464 | -0.54474 | 121.2296 | -0.33875 | -0.4303 | -0.49896 | -0.17395 | -0.1236 | -0.10529 | -0.068665 | -0.068665 | -0.10986 | -0.022888 | 0.064087 | -0.17853 | 0.004577 | 0.27008 | 0.10986 | 0.17853 | 0.045777 | 0.11444 | 0.50354 | -121.3486 | -121.2936 | 0.54016 | 0.58594 | 0.49896 | 0.082398 | -0.004577 | 0.20599 | 121.7743 | 0.036621 | 0.036621 | 121.5912 | -0.01831 | 121.6553 | 0.48523 | -121.7697 | -121.3303 | 121.8384 | 0.54016 | 6.7108 | 0.43488
1698.3281 | 121.8796 | -0.9201 | 120.9183 | -0.009308 | 6.9782 | 0.065046 | 0.06386 | -0.0013544 | -0.0069683 | -0.0012988 | 0.0025025 | 0.0028732 | 0.014178 | 0.024312 | -0.0059857 | 0.02553 | -0.0037192 | 6.102 | 120.6162 | -0.98877 | 120.845 | -0.70038 | -0.83313 | -0.85144 | -0.1831 | -0.15106 | -0.12817 | -0.036621 | -0.07782 | -0.12817 | -0.018311 | -0.068665 | -0.30212 | -0.073242 | 0.21973 | 0.068665 | 0.086975 | 0.13733 | 0.15564 | 0.79193 | -121.0693 | -120.9549 | 0.84228 | 0.90179 | 0.79193 | 0.10986 | 0 | 0.28839 | 121.8338 | 0.050354 | 0.091553 | 121.6049 | -0.022888 | 121.5363 | 0.76904 | -121.907 | -121.0464 | 121.7651 | 0.88348 | 7.0221 | 0.737
1700.0625 | 121.8796 | -0.60883 | 121.2021 | 0.01358 | 6.9801 | 0.067182 | 0.062579 | -7.2628e-05 | -0.0056867 | -0.0025806 | -0.0036011 | 0.004155 | 0.012897 | 0.012136 | -0.0072675 | 0.028948 | -0.0035056 | 6.0745 | 121.0419 | -0.55389 | 121.17 | -0.38452 | -0.50354 | -0.51727 | -0.1831 | -0.13733 | -0.10986 | -0.041199 | -0.07782 | -0.09613 | -0.018311 | 0.054932 | -0.16022 | -0.032043 | 0.2243 | 0.091553 | 0.10529 | 0.036621 | 0.050354 | 0.49896 | -121.3394 | -121.2433 | 0.53101 | 0.59052 | 0.5127 | 0.091552 | 0.013733 | 0.16937 | 121.7239 | 0.032043 | 0.068664 | 121.5958 | -0.027466 | 121.6507 | 0.4715 | -121.756 | -121.312 | 121.7789 | 0.56763 | 6.6833 | 0.42572
1701.8125 | 121.9254 | -0.68207 | 121.1197 | 0.005951 | 6.9748 | 0.065901 | 0.063006 | -0.004345 | -0.0091047 | -0.0030078 | -0.0036011 | 0.0022324 | 0.018237 | 0.014272 | -0.0083355 | 0.025957 | -0.00072839 | 6.0287 | 120.8725 | -0.70953 | 121.0556 | -0.50812 | -0.59967 | -0.61798 | -0.16479 | -0.14648 | -0.12817 | -0.027466 | -0.036621 | -0.050354 | 0.027466 | -0.027466 | -0.24719 | -0.064087 | 0.17395 | 0.064087 | 0.082398 | 0.091553 | 0.10986 | 0.55389 | -121.2662 | -121.1472 | 0.64545 | 0.70953 | 0.63171 | 0.15564 | 0.07782 | 0.20142 | 121.7651 | 0.091553 | 0.10071 | 121.582 | -0.01831 | 121.5546 | 0.53558 | -121.8292 | -121.2479 | 121.7377 | 0.6546 | 6.7108 | 0.51727
1703.5 | 121.7926 | -0.62256 | 121.2982 | 0.005951 | 6.9769 | 0.064619 | 0.06322 | 0.00014097 | -0.0084637 | -0.0057848 | -0.00054933 | 0.0033004 | 0.012683 | 0.010213 | -0.0094037 | 0.024035 | -0.0037192 | 6.1203 | 121.1472 | -0.55389 | 121.1472 | -0.43488 | -0.50812 | -0.54016 | -0.28839 | -0.07782 | -0.16479 | -0.13275 | -0.15106 | -0.19684 | -0.064087 | 0.068665 | -0.15106 | -0.15106 | 0.18768 | 0.082398 | 0.11444 | 0.013733 | 0.045776 | 0.45776 | -121.376 | -121.431 | 0.4715 | 0.55847 | 0.42572 | 0.10071 | -0.032043 | 0.11902 | 121.701 | 0.013733 | 0.032044 | 121.701 | 0.086975 | 121.7697 | 0.54474 | -121.8521 | -121.463 | 121.7697 | 0.48981 | 6.7429 | 0.33417
1705.2344 | 121.8842 | -0.59967 | 121.2296 | -0.0016785 | 6.9767 | 0.066114 | 0.063433 | 0.0033454 | -0.0061139 | -0.00023063 | -0.00054933 | 0.002446 | 0.019305 | 0.016408 | -0.0042767 | 0.02553 | 0.00098061 | 6.0745 | 121.0556 | -0.54016 | 121.1838 | -0.36621 | -0.48981 | -0.50812 | -0.18768 | -0.13733 | -0.10986 | -0.050354 | -0.09613 | -0.11902 | -0.009155 | 0.059509 | -0.17395 | -0.045776 | 0.23346 | 0.091552 | 0.10986 | 0.032043 | 0.050354 | 0.48981 | -121.3669 | -121.2799 | 0.50354 | 0.59052 | 0.48065 | 0.10071 | -0.009156 | 0.17395 | 121.7239 | 0.013733 | 0.059509 | 121.5958 | -0.027466 | 121.6553 | 0.46234 | -121.7697 | -121.3394 | 121.7834 | 0.54932 | 6.6742 | 0.41199
1706.9062 | 121.8109 | -0.6134 | 121.2662 | -0.016937 | 6.9793 | 0.063978 | 0.062151 | 0.0014228 | -0.0073957 | -0.00023063 | -0.00054933 | 0.0039414 | 0.014392 | 0.014059 | -0.0098309 | 0.024035 | -0.0056418 | 6.102 | 121.1288 | -0.54932 | 121.1288 | -0.42572 | -0.51727 | -0.55847 | -0.30212 | -0.068665 | -0.16022 | -0.14191 | -0.16022 | -0.18768 | -0.068665 | 0.064087 | -0.13733 | -0.13733 | 0.18768 | 0.054931 | 0.09613 | -0.009156 | 0.032043 | 0.45319 | -121.3348 | -121.4081 | 0.45319 | 0.54474 | 0.42572 | 0.091552 | -0.027466 | 0.1236 | 121.6782 | 0 | 0.01831 | 121.6782 | 0.091552 | 121.7422 | 0.54474 | -121.8155 | -121.4264 | 121.7422 | 0.4715 | 6.7154 | 0.31128
1708.6406 | 121.9482 | -0.75531 | 121.051 | -0.009308 | 6.9754 | 0.066541 | 0.061297 | 0.0048408 | -0.011454 | -0.00023063 | -0.0036011 | 0.0011642 | 0.016955 | 0.012136 | -0.0074811 | 0.02553 | -0.0054282 | 6.1157 | 120.8954 | -0.66834 | 121.0785 | -0.46692 | -0.56305 | -0.62714 | -0.10529 | -0.14648 | -0.10529 | 0 | 0 | -0.032043 | 0.018311 | 0.086975 | -0.15564 | 0.027466 | 0.28839 | 0.12817 | 0.19226 | 0.041199 | 0.10529 | 0.65002 | -121.1975 | -121.051 | 0.75531 | 0.77362 | 0.72327 | 0.1236 | 0.073243 | 0.20142 | 121.7468 | 0.10529 | 0.10529 | 121.5637 | -0.041198 | 121.6507 | 0.60883 | -121.7194 | -121.1563 | 121.8338 | 0.75531 | 6.871 | 0.65002
1710.375 | 121.8155 | -0.67291 | 121.1792 | -0.0016785 | 6.9786 | 0.065046 | 0.064288 | -0.0011408 | -0.0088911 | -0.0025806 | -0.00054933 | 0.000737 | 0.017169 | 0.019613 | -0.0089765 | 0.025316 | -0.00094199 | 6.0928 | 121.0785 | -0.63171 | 121.0785 | -0.49439 | -0.56305 | -0.60425 | -0.29755 | -0.082397 | -0.16937 | -0.12817 | -0.16937 | -0.19684 | -0.068665 | 0.041199 | -0.10071 | -0.10071 | 0.17853 | 0.068665 | 0.10986 | 0.027466 | 0.068665 | 0.50354 | -121.2616 | -121.3074 | 0.50354 | 0.60425 | 0.47607 | 0.10071 | -0.027465 | 0.13733 | 121.7102 | 0 | 0.041199 | 121.7102 | 0.086976 | 121.7514 | 0.59052 | -121.8109 | -121.3486 | 121.7514 | 0.54474 | 6.7657 | 0.37537
1712.0625 | 121.9345 | -0.58594 | 121.1838 | -0.0016785 | 6.9782 | 0.066541 | 0.062579 | -0.0034906 | -0.0052595 | 0.00019657 | 0.0055543 | 0.0003098 | 0.014605 | 0.019613 | -0.0049175 | 0.025744 | -0.003292 | 6.1249 | 121.0327 | -0.53101 | 121.2341 | -0.33417 | -0.46234 | -0.49439 | -0.12817 | -0.13733 | -0.10986 | 0.013733 | -0.027466 | -0.073242 | 0.022888 | 0.054931 | -0.15106 | 0.050354 | 0.25177 | 0.091552 | 0.1236 | 0.036621 | 0.068665 | 0.47607 | -121.3211 | -121.17 | 0.55847 | 0.60883 | 0.5127 | 0.13275 | 0.036621 | 0.19684 | 121.7651 | 0.082397 | 0.1236 | 121.5637 | -0.027466 | 121.6187 | 0.44861 | -121.7148 | -121.2936 | 121.8201 | 0.59967 | 6.7108 | 0.45776
1713.7969 | 121.8567 | -0.56305 | 121.2845 | 0.005951 | 6.9793 | 0.064405 | 0.062579 | 0.00185 | -0.0084637 | -0.001726 | 0.0025025 | 0.003514 | 0.014178 | 0.017476 | -0.0066265 | 0.024889 | 0.001835 | 6.1661 | 121.1563 | -0.53558 | 121.2067 | -0.39368 | -0.47607 | -0.51727 | -0.25177 | -0.09613 | -0.13733 | -0.09613 | -0.091553 | -0.13733 | -0.032043 | 0.027466 | -0.12817 | -0.07782 | 0.16937 | 0.045776 | 0.086975 | 0.01831 | 0.059509 | 0.42572 | -121.3806 | -121.3806 | 0.4715 | 0.53101 | 0.42572 | 0.10529 | 0 | 0.14191 | 121.7422 | 0.045776 | 0.041199 | 121.6919 | 0.041199 | 121.7194 | 0.46692 | -121.8201 | -121.4218 | 121.7697 | 0.46692 | 6.7291 | 0.31128
1715.5312 | 121.8842 | -0.6134 | 121.2067 | 0.005951 | 6.9789 | 0.065473 | 0.063006 | 0.0037726 | -0.0071821 | -0.0025806 | -0.0036011 | 0.0013778 | 0.016955 | 0.020467 | -0.0068403 | 0.025957 | -0.0020102 | 6.0562 | 121.0693 | -0.58136 | 121.1517 | -0.41199 | -0.50812 | -0.54474 | -0.22888 | -0.11902 | -0.13275 | -0.068665 | -0.086975 | -0.14648 | -0.022888 | 0.032043 | -0.13733 | -0.054932 | 0.20142 | 0.068664 | 0.10529 | 0.036621 | 0.073242 | 0.48065 | -121.3257 | -121.2753 | 0.52643 | 0.59052 | 0.46692 | 0.10986 | -0.013733 | 0.16937 | 121.7331 | 0.045776 | 0.064086 | 121.6507 | 0.013732 | 121.6827 | 0.49438 | -121.788 | -121.3394 | 121.7651 | 0.54474 | 6.6696 | 0.38452
1717.2031 | 121.9391 | -0.52643 | 121.2616 | -0.016937 | 6.9778 | 0.064405 | 0.063006 | -0.00049983 | -0.0082501 | -0.0049304 | -0.00054933 | 0.0028732 | 0.016528 | 0.02004 | -0.010258 | 0.024462 | -0.00030119 | 6.1203 | 121.106 | -0.49439 | 121.3165 | -0.26093 | -0.35706 | -0.42114 | -0.11444 | -0.13733 | -0.091553 | 0 | -0.009155 | -0.041199 | 0.041199 | 0.032043 | -0.15564 | 0.054931 | 0.2655 | 0.10529 | 0.16937 | 0.073242 | 0.13733 | 0.43488 | -121.3989 | -121.2616 | 0.51727 | 0.56763 | 0.48523 | 0.13275 | 0.050354 | 0.23346 | 121.8109 | 0.082398 | 0.091553 | 121.6003 | -0.045776 | 121.6324 | 0.3891 | -121.756 | -121.3531 | 121.843 | 0.52643 | 6.6467 | 0.41199
1718.8906 | 121.8567 | -0.5722 | 121.2799 | -0.0016785 | 6.9816 | 0.063764 | 0.061511 | 0.00035457 | -0.0073957 | -0.0015124 | 0.0055543 | 0.003514 | 0.015033 | 0.0074362 | -0.0076947 | 0.025957 | -0.0064962 | 6.1066 | 121.1563 | -0.54016 | 121.1975 | -0.42572 | -0.50812 | -0.52643 | -0.2655 | -0.10529 | -0.1236 | -0.07782 | -0.1236 | -0.16479 | -0.036621 | 0.032044 | -0.1236 | -0.082397 | 0.14648 | 0.045777 | 0.064087 | 0.013733 | 0.032043 | 0.44861 | -121.3852 | -121.3577 | 0.44861 | 0.53558 | 0.40741 | 0.086975 | -0.041199 | 0.11444 | 121.7377 | 0 | 0.045776 | 121.6965 | 0.01831 | 121.7285 | 0.46692 | -121.8201 | -121.4035 | 121.7697 | 0.49438 | 6.6788 | 0.3067
1720.6406 | 121.9437 | -0.52185 | 121.257 | -0.016937 | 6.9767 | 0.066755 | 0.063006 | 0.00185 | -0.0052595 | -0.0025806 | -0.0036011 | 0.0011642 | 0.016314 | 0.013418 | -0.0044903 | 0.026385 | -0.0022238 | 6.1523 | 121.1426 | -0.46692 | 121.3165 | -0.25177 | -0.41657 | -0.4303 | -0.14191 | -0.13275 | -0.10071 | 0.018311 | -0.041199 | -0.068665 | 0.027466 | 0.054932 | -0.11444 | 0.059509 | 0.27008 | 0.091553 | 0.10529 | 0.036621 | 0.050354 | 0.42114 | -121.3898 | -121.2387 | 0.48065 | 0.54932 | 0.45319 | 0.12817 | 0.032043 | 0.21515 | 121.7834 | 0.059509 | 0.11902 | 121.6095 | -0.032043 | 121.6644 | 0.3891 | -121.7239 | -121.3577 | 121.8384 | 0.54016 | 6.6742 | 0.37994
1722.3281 | 121.9528 | -0.88348 | 120.9183 | -0.009308 | 6.9763 | 0.064619 | 0.061511 | -0.002636 | -0.0065411 | -0.00087163 | -0.00054933 | 0.0009506 | 0.014178 | 0.02239 | -0.0076947 | 0.025957 | -0.00072839 | 6.1249 | 120.7626 | -0.8606 | 120.9137 | -0.66376 | -0.75531 | -0.77362 | -0.15564 | -0.13275 | -0.10986 | -0.013733 | -0.032043 | -0.050354 | 0.027466 | 0.022888 | -0.15564 | -0.004578 | 0.21973 | 0.10986 | 0.12817 | 0.086975 | 0.10529 | 0.77362 | -121.051 | -120.932 | 0.85144 | 0.91095 | 0.83313 | 0.13733 | 0.059509 | 0.19684 | 121.7743 | 0.07782 | 0.09613 | 121.6232 | -0.022888 | 121.6461 | 0.75073 | -121.7789 | -121.0281 | 121.7972 | 0.86975 | 7.0084 | 0.72784
1724.0781 | 121.9345 | -0.53558 | 121.3074 | -0.009308 | 6.9767 | 0.062696 | 0.060656 | 0.00014097 | -0.0061139 | -0.0021532 | -0.0036011 | 0.0015914 | 0.015033 | 0.016622 | -0.0070539 | 0.024248 | -0.0039328 | 6.134 | 121.106 | -0.48523 | 121.2479 | -0.32044 | -0.41199 | -0.43945 | -0.17395 | -0.11902 | -0.10986 | -0.022888 | -0.045776 | -0.064087 | 0.022888 | 0.050354 | -0.20142 | -0.059509 | 0.21515 | 0.09613 | 0.1236 | 0.045776 | 0.073242 | 0.42572 | -121.4264 | -121.3303 | 0.48981 | 0.55847 | 0.4715 | 0.13275 | 0.045776 | 0.16479 | 121.7331 | 0.064087 | 0.086975 | 121.5912 | -0.009156 | 121.6415 | 0.41656 | -121.7926 | -121.4172 | 121.7834 | 0.5127 | 6.6696 | 0.36163
1725.8281 | 121.8292 | -0.53558 | 121.3715 | -0.009308 | 6.9769 | 0.063337 | 0.06322 | -0.0019952 | -0.0082501 | -0.0036486 | -0.0036011 | 0.0028732 | 0.013751 | 0.015767 | -0.010686 | 0.026385 | -0.003292 | 6.1386 | 121.1884 | -0.4715 | 121.2479 | -0.3479 | -0.44403 | -0.46234 | -0.3067 | -0.09613 | -0.13733 | -0.14191 | -0.14191 | -0.17395 | -0.07782 | 0.064086 | -0.18311 | -0.1236 | 0.18768 | 0.073242 | 0.091552 | 0.009156 | 0.027466 | 0.39825 | -121.4676 | -121.5134 | 0.39368 | 0.45776 | 0.36163 | 0.059509 | -0.036621 | 0.1236 | 121.7194 | -0.004578 | -0.004578 | 121.6599 | 0.041199 | 121.7239 | 0.43945 | -121.843 | -121.5088 | 121.7834 | 0.39368 | 6.6742 | 0.22888
1727.5156 | 121.9391 | -0.49896 | 121.3074 | -0.016937 | 6.9754 | 0.065046 | 0.063006 | -0.00071343 | -0.010173 | -0.0036486 | -0.0036011 | 0.0033004 | 0.017596 | 0.019185 | -0.0076947 | 0.025957 | -0.002651 | 6.1615 | 121.1884 | -0.44861 | 121.3348 | -0.2243 | -0.33417 | -0.37079 | -0.11444 | -0.16022 | -0.11444 | 0.004578 | -0.013733 | -0.036621 | 0.036621 | 0.050354 | -0.11902 | 0.027466 | 0.27466 | 0.12817 | 0.1648 | 0.077819 | 0.11444 | 0.38452 | -121.4676 | -121.3028 | 0.48523 | 0.53558 | 0.46234 | 0.15106 | 0.07782 | 0.2243 | 121.7834 | 0.10071 | 0.11902 | 121.637 | -0.045776 | 121.6873 | 0.33875 | -121.756 | -121.4218 | 121.8338 | 0.50354 | 6.6605 | 0.38452
1729.2656 | 121.9391 | -0.60883 | 121.1884 | -0.0016785 | 6.9784 | 0.064832 | 0.063433 | -0.0041314 | -0.0061139 | -0.002367 | -0.0036011 | 0.0026596 | 0.014178 | 0.019399 | -0.0072675 | 0.024248 | -0.0028646 | 6.1203 | 121.0373 | -0.54474 | 121.1975 | -0.37079 | -0.46234 | -0.48981 | -0.17395 | -0.1236 | -0.1236 | -0.013733 | -0.032043 | -0.050354 | 0.013733 | 0.064087 | -0.15106 | 0.009156 | 0.23804 | 0.11902 | 0.14648 | 0.054932 | 0.082398 | 0.48523 | -121.312 | -121.2021 | 0.57678 | 0.62256 | 0.55847 | 0.13733 | 0.073242 | 0.17395 | 121.7422 | 0.091553 | 0.10986 | 121.582 | 0 | 121.6461 | 0.48523 | -121.7331 | -121.312 | 121.8063 | 0.59509 | 6.7291 | 0.43488
1730.9531 | 121.9254 | -0.53101 | 121.2616 | -0.009308 | 6.9782 | 0.06526 | 0.064288 | -0.0039178 | -0.0065411 | -0.0038622 | -0.00054933 | 0.0003098 | 0.012042 | 0.017904 | -0.0044903 | 0.026171 | -0.00671 | 6.1066 | 121.1609 | -0.52185 | 121.2479 | -0.33417 | -0.44861 | -0.47607 | -0.17853 | -0.13733 | -0.13275 | 0 | -0.054932 | -0.09613 | 0.022888 | 0.009155 | -0.10071 | -0.013733 | 0.19684 | 0.054932 | 0.082398 | 0.045777 | 0.073243 | 0.39825 | -121.3989 | -121.2616 | 0.47607 | 0.55389 | 0.43488 | 0.15564 | 0.036621 | 0.18768 | 121.7697 | 0.077819 | 0.13275 | 121.6827 | -0.004578 | 121.6919 | 0.39368 | -121.7834 | -121.3943 | 121.7789 | 0.53101 | 6.6376 | 0.35248
1732.6875 | 121.9025 | -0.51727 | 121.3303 | -0.009308 | 6.9786 | 0.064405 | 0.062579 | 0.00014097 | -0.0041913 | -0.0010852 | -0.00054933 | 0.0009506 | 0.01781 | 0.018117 | -0.0057721 | 0.024676 | -0.001583 | 6.1066 | 121.17 | -0.45776 | 121.2891 | -0.29297 | -0.41657 | -0.42114 | -0.21515 | -0.1236 | -0.12817 | -0.045776 | -0.09613 | -0.13733 | -0.027466 | 0.059509 | -0.16022 | -0.041199 | 0.2243 | 0.09613 | 0.10071 | 0.036621 | 0.041199 | 0.3891 | -121.4539 | -121.376 | 0.42114 | 0.48981 | 0.37994 | 0.10071 | -0.009155 | 0.1648 | 121.7468 | 0.032044 | 0.082398 | 121.6278 | 0.004578 | 121.6873 | 0.39368 | -121.788 | -121.4584 | 121.8063 | 0.4715 | 6.6238 | 0.30212
1734.4375 | 121.8246 | -0.55389 | 121.3623 | -0.009308 | 6.9808 | 0.06291 | 0.062579 | 0.0033454 | -0.0093183 | -0.0019396 | -0.00054933 | 0.005223 | 0.015887 | 0.012777 | -0.010686 | 0.026385 | -0.0041464 | 6.0608 | 121.2296 | -0.4715 | 121.2341 | -0.37079 | -0.45319 | -0.48523 | -0.31128 | -0.091553 | -0.16479 | -0.14191 | -0.16479 | -0.20142 | -0.07782 | 0.082397 | -0.13275 | -0.12817 | 0.18311 | 0.068665 | 0.10071 | -0.013732 | 0.018311 | 0.3891 | -121.4539 | -121.5042 | 0.3891 | 0.47607 | 0.35248 | 0.086975 | -0.036621 | 0.10071 | 121.7056 | 0 | 0.022888 | 121.701 | 0.073242 | 121.7834 | 0.46234 | -121.8338 | -121.5271 | 121.788 | 0.41199 | 6.6147 | 0.24262
1736.125 | 121.9391 | -0.53558 | 121.2753 | -0.0016785 | 6.9776 | 0.063551 | 0.064074 | -0.00071343 | -0.0065411 | -0.0012988 | 0.0025025 | 0.0011642 | 0.016101 | 0.017904 | -0.0021405 | 0.025957 | -0.001583 | 6.1157 | 121.1884 | -0.48523 | 121.2479 | -0.35706 | -0.46234 | -0.47607 | -0.19226 | -0.13275 | -0.13275 | -0.009155 | -0.050354 | -0.10071 | 0.013733 | 0.050354 | -0.086976 | -0.027466 | 0.17853 | 0.059509 | 0.073242 | 0.009155 | 0.022888 | 0.40283 | -121.4081 | -121.2845 | 0.48523 | 0.54932 | 0.43488 | 0.14648 | 0.032043 | 0.12817 | 121.7331 | 0.082397 | 0.1236 | 121.6736 | 0 | 121.7239 | 0.40283 | -121.7606 | -121.4081 | 121.7834 | 0.52643 | 6.6513 | 0.34332
1737.8125 | 121.8018 | -0.56305 | 121.3257 | -0.0016785 | 6.9797 | 0.065046 | 0.064715 | 0.0016364 | -0.0106 | -0.0042896 | -0.00054933 | 0.004155 | 0.015033 | 0.014486 | -0.0074811 | 0.024248 | -0.0024374 | 6.1249 | 121.1884 | -0.53101 | 121.1975 | -0.39825 | -0.5127 | -0.53101 | -0.30212 | -0.09613 | -0.14191 | -0.13733 | -0.17853 | -0.23804 | -0.086975 | 0.032043 | -0.13733 | -0.12817 | 0.1648 | 0.032043 | 0.050354 | 0 | 0.018311 | 0.42114 | -121.4218 | -121.463 | 0.38452 | 0.47607 | 0.32501 | 0.054932 | -0.09613 | 0.13275 | 121.7285 | -0.036621 | 0.004578 | 121.7194 | 0.045777 | 121.7514 | 0.46692 | -121.8567 | -121.4676 | 121.7606 | 0.42572 | 6.6879 | 0.26093
1739.5469 | 121.8338 | -0.62256 | 121.2433 | -0.009308 | 6.9795 | 0.06526 | 0.062365 | -7.2628e-05 | -0.0065411 | -0.0012988 | -0.0036011 | 0.0033004 | 0.016528 | 0.0091452 | -0.0059857 | 0.024248 | -0.0084188 | 6.0562 | 121.1609 | -0.5722 | 121.1014 | -0.48981 | -0.59509 | -0.60425 | -0.3067 | -0.082397 | -0.17853 | -0.11902 | -0.18768 | -0.21973 | -0.09613 | 0.050354 | -0.082397 | -0.14191 | 0.13275 | 0.018311 | 0.027466 | -0.032043 | -0.022888 | 0.44403 | -121.3257 | -121.3623 | 0.43488 | 0.52643 | 0.40283 | 0.082398 | -0.041199 | 0.082398 | 121.6736 | -0.009155 | 0.059509 | 121.7331 | 0.096131 | 121.7834 | 0.54016 | -121.8155 | -121.4218 | 121.7239 | 0.50354 | 6.6788 | 0.31586
1741.2969 | 121.907 | -0.53558 | 121.2936 | 0.005951 | 6.9786 | 0.066755 | 0.06386 | 0.0012092 | -0.0059003 | -0.00044443 | 0.0025025 | 0.0005234 | 0.015887 | 0.021322 | -0.0064129 | 0.027666 | -0.00094199 | 6.0379 | 121.1334 | -0.48523 | 121.2662 | -0.27008 | -0.43488 | -0.43945 | -0.17395 | -0.14191 | -0.13275 | -0.045776 | -0.082397 | -0.11444 | -0.036621 | 0.050354 | -0.16022 | -0.027466 | 0.2655 | 0.09613 | 0.10071 | 0.045776 | 0.050354 | 0.40283 | -121.4355 | -121.3394 | 0.45319 | 0.49896 | 0.42114 | 0.09613 | 0.01831 | 0.21515 | 121.7514 | 0.050354 | 0.086975 | 121.6187 | -0.009156 | 121.669 | 0.39368 | -121.7789 | -121.4264 | 121.8018 | 0.48981 | 6.5735 | 0.36163
1742.9844 | 121.9162 | -0.59967 | 121.2158 | 0.01358 | 6.9776 | 0.065473 | 0.064501 | -0.0030634 | -0.0084637 | -0.0032214 | 0.0025025 | 0.0022324 | 0.017596 | 0.017263 | -0.0074811 | 0.026171 | 0.00076681 | 6.1386 | 121.0739 | -0.53101 | 121.2021 | -0.33875 | -0.49439 | -0.51727 | -0.1831 | -0.16022 | -0.13733 | -0.045776 | -0.10071 | -0.1236 | -0.018311 | 0.068664 | -0.14191 | -0.013733 | 0.26093 | 0.082397 | 0.10529 | 0.013733 | 0.036621 | 0.46234 | -121.376 | -121.2616 | 0.49896 | 0.58136 | 0.47607 | 0.11902 | 0.013733 | 0.19226 | 121.7331 | 0.036621 | 0.091553 | 121.6049 | -0.022888 | 121.6736 | 0.43945 | -121.7468 | -121.3531 | 121.8018 | 0.55389 | 6.7383 | 0.41657
1744.7344 | 121.9482 | -1.6983 | 120.1904 | -0.009308 | 6.9771 | 0.064832 | 0.06322 | -0.00028623 | -0.0073957 | -0.0019396 | -0.00054933 | 0.0015914 | 0.014819 | 0.015767 | -0.010258 | 0.026171 | -0.00094199 | 6.2027 | 120.3644 | -1.2634 | 120.2179 | -1.3321 | -1.4557 | -1.3229 | -0.16937 | -0.12817 | -0.14191 | -0.032043 | -0.036621 | -0.07782 | 0.009155 | 0.43487 | 0.17395 | 0.027466 | 0.36621 | 0.37537 | 0.24261 | -0.059509 | -0.19226 | 1.5564 | -120.3186 | -120.2225 | 1.6617 | 1.7075 | 1.6205 | 0.15106 | 0.064087 | -0.068664 | 121.4813 | 0.10529 | 0.10986 | 121.6278 | 0.013733 | 122.0627 | 1.5701 | -121.4539 | -120.3323 | 121.9162 | 1.6663 | 7.901 | 1.5289
1746.4219 | 121.8475 | -0.86517 | 120.9869 | 0.005951 | 6.9776 | 0.065901 | 0.064501 | 0.003559 | -0.0071821 | -0.00065803 | -0.00054933 | 0.0037278 | 0.015674 | 0.0095724 | -0.0070539 | 0.026171 | 0.0011942 | 6.0196 | 120.9366 | -0.75989 | 120.9091 | -0.69122 | -0.81024 | -0.83771 | -0.29297 | -0.11444 | -0.15106 | -0.10986 | -0.16937 | -0.21515 | -0.068665 | 0.10528 | -0.050354 | -0.077819 | 0.17395 | 0.027465 | 0.054931 | -0.07782 | -0.050354 | 0.71411 | -121.1014 | -121.0968 | 0.6958 | 0.79651 | 0.65002 | 0.082397 | -0.064087 | 0.068665 | 121.669 | -0.018311 | 0.041199 | 121.6965 | 0.036621 | 121.8018 | 0.75073 | -121.7468 | -121.138 | 121.7743 | 0.75531 | 6.8848 | 0.5722
1748.1562 | 121.8613 | -0.62256 | 121.2936 | -0.0016785 | 6.9795 | 0.065901 | 0.064929 | 0.00014097 | -0.0093183 | 0.00019657 | 0.0055543 | 0.003514 | 0.016314 | 0.0025228 | -0.0083355 | 0.025103 | -0.003292 | 6.1432 | 121.1517 | -0.56763 | 121.1884 | -0.41657 | -0.49896 | -0.54016 | -0.27008 | -0.1236 | -0.16479 | -0.09613 | -0.11444 | -0.17853 | -0.054932 | 0.054932 | -0.14191 | -0.10529 | 0.20599 | 0.082398 | 0.1236 | 0.027466 | 0.068665 | 0.45776 | -121.4172 | -121.3898 | 0.50812 | 0.56763 | 0.44403 | 0.10986 | -0.013733 | 0.15106 | 121.756 | 0.050354 | 0.068665 | 121.7194 | 0.041199 | 121.7743 | 0.49896 | -121.8613 | -121.4584 | 121.8109 | 0.52643 | 6.7657 | 0.35248
1749.8438 | 121.8704 | -0.68665 | 121.1929 | 0.01358 | 6.9793 | 0.064405 | 0.066851 | -0.00028623 | -0.0086773 | -0.0030078 | 0.0025025 | 0.0028732 | 0.014178 | 0.01299 | -0.0066265 | 0.024035 | -0.0030784 | 6.1478 | 121.0556 | -0.66376 | 121.106 | -0.4715 | -0.59509 | -0.6134 | -0.21515 | -0.11444 | -0.13733 | -0.068665 | -0.10071 | -0.16479 | -0.036621 | 0.022889 | -0.13733 | -0.086975 | 0.21515 | 0.073243 | 0.091553 | 0.050354 | 0.068664 | 0.54932 | -121.3074 | -121.2616 | 0.58594 | 0.65002 | 0.52185 | 0.10071 | -0.027466 | 0.19226 | 121.7697 | 0.036621 | 0.068664 | 121.7194 | 0.022888 | 121.7422 | 0.5722 | -121.8567 | -121.3303 | 121.7926 | 0.61798 | 6.8344 | 0.4715
1751.5938 | 121.907 | -0.78278 | 121.051 | -0.0016785 | 6.9748 | 0.066541 | 0.061511 | 0.0012092 | -0.0080365 | -0.003435 | -0.0036011 | 0.0022324 | 0.014178 | 0.016195 | -0.0070539 | 0.027453 | 0.00076681 | 5.9875 | 120.9457 | -0.69122 | 121.0236 | -0.56305 | -0.68207 | -0.69122 | -0.24261 | -0.14191 | -0.13733 | -0.054932 | -0.086975 | -0.13275 | -0.036621 | 0.091553 | -0.10528 | -0.027465 | 0.21973 | 0.091553 | 0.10071 | 0 | 0.009155 | 0.64545 | -121.1929 | -121.106 | 0.6958 | 0.74616 | 0.65003 | 0.10071 | 0.004578 | 0.12817 | 121.7148 | 0.050354 | 0.082397 | 121.637 | -0.004578 | 121.7285 | 0.64087 | -121.7422 | -121.1884 | 121.8063 | 0.72784 | 6.7703 | 0.54016
1753.3281 | 121.843 | -0.95673 | 120.9549 | -0.0016785 | 6.9778 | 0.06291 | 0.06322 | 0.00185 | -0.0093183 | -0.0021532 | -0.00054933 | 0.0028732 | 0.014392 | 0.0076498 | -0.0098309 | 0.024248 | -0.0062826 | 6.0699 | 120.8267 | -0.87433 | 120.8221 | -0.78735 | -0.85602 | -0.89722 | -0.32501 | -0.10071 | -0.15564 | -0.11902 | -0.16937 | -0.18768 | -0.086975 | 0.082397 | -0.12817 | -0.13275 | 0.16937 | 0.059509 | 0.10071 | -0.022888 | 0.018311 | 0.80109 | -121.0556 | -121.0739 | 0.78735 | 0.86975 | 0.76904 | 0.068665 | -0.032043 | 0.086975 | 121.6965 | -0.013733 | 0.036621 | 121.7011 | 0.054932 | 121.7834 | 0.85602 | -121.8292 | -121.1105 | 121.7789 | 0.83771 | 7.0267 | 0.63171
1755.0625 | 121.8979 | -0.64545 | 121.2296 | -0.009308 | 6.9769 | 0.064192 | 0.06322 | -0.0017816 | -0.0078229 | -0.0019396 | -0.0036011 | 0.000737 | 0.01546 | 0.016195 | -0.0091901 | 0.025744 | -0.0045736 | 6.134 | 121.0464 | -0.56763 | 121.1746 | -0.38452 | -0.4715 | -0.52185 | -0.1831 | -0.11902 | -0.11444 | -0.064087 | -0.07782 | -0.12817 | -0.041199 | 0.07782 | -0.1831 | -0.054931 | 0.26093 | 0.1236 | 0.17395 | 0.045776 | 0.09613 | 0.53101 | -121.3486 | -121.2936 | 0.56763 | 0.60425 | 0.51727 | 0.073242 | -0.013733 | 0.18311 | 121.7422 | 0.036621 | 0.050354 | 121.6141 | -0.004578 | 121.6919 | 0.52643 | -121.7972 | -121.344 | 121.8201 | 0.58136 | 6.7795 | 0.46234
1756.8125 | 121.875 | -0.62714 | 121.2387 | -0.0016785 | 6.9793 | 0.064832 | 0.063006 | 0.005268 | -0.0073957 | -0.0036486 | -0.00054933 | 0.0037278 | 0.018023 | 0.016622 | -0.0094037 | 0.026171 | -0.003292 | 6.189 | 121.1197 | -0.6134 | 121.1563 | -0.45319 | -0.52185 | -0.55847 | -0.26093 | -0.09613 | -0.16022 | -0.082397 | -0.11902 | -0.16937 | -0.050354 | 0.013733 | -0.11902 | -0.082397 | 0.17395 | 0.068664 | 0.10529 | 0.054931 | 0.091552 | 0.46692 | -121.3348 | -121.3211 | 0.50812 | 0.57678 | 0.45776 | 0.10986 | -0.009156 | 0.16022 | 121.7697 | 0.041198 | 0.07782 | 121.7331 | 0.064087 | 121.7468 | 0.53101 | -121.8521 | -121.3989 | 121.7834 | 0.54474 | 6.8161 | 0.36621
1758.5469 | 121.9986 | -0.5127 | 121.3211 | -0.0016785 | 6.9752 | 0.06526 | 0.063647 | 0.0027044 | -0.0061139 | -0.0015124 | -0.0036011 | 0.0018052 | 0.015246 | 0.013631 | -0.0083355 | 0.026812 | -8.7586e-05 | 6.1523 | 121.1517 | -0.45776 | 121.3348 | -0.21057 | -0.32501 | -0.37079 | -0.12817 | -0.15106 | -0.1236 | -0.009155 | -0.027466 | -0.045776 | 0.004578 | 0.054931 | -0.16937 | 0.013733 | 0.30212 | 0.14191 | 0.18768 | 0.086975 | 0.13275 | 0.3891 | -121.4722 | -121.3303 | 0.48523 | 0.51727 | 0.46692 | 0.12817 | 0.07782 | 0.24719 | 121.7926 | 0.09613 | 0.11444 | 121.6095 | -0.027466 | 121.6644 | 0.36163 | -121.7789 | -121.4447 | 121.8475 | 0.50354 | 6.665 | 0.38452
1760.2812 | 121.8338 | -0.56305 | 121.3486 | 0.005951 | 6.9761 | 0.063551 | 0.064501 | 0.0031318 | -0.0084637 | -0.003435 | 0.0086061 | 0.0022324 | 0.016314 | 0.007009 | -0.0076947 | 0.024462 | -0.0039328 | 6.134 | 121.2296 | -0.50812 | 121.1929 | -0.3891 | -0.47607 | -0.49896 | -0.3067 | -0.09613 | -0.17395 | -0.1236 | -0.16937 | -0.20599 | -0.082397 | 0.054931 | -0.11902 | -0.15564 | 0.17395 | 0.064087 | 0.086975 | 0.009156 | 0.032044 | 0.3891 | -121.4447 | -121.4722 | 0.39368 | 0.48065 | 0.35706 | 0.091553 | -0.032044 | 0.11902 | 121.701 | 0.004577 | 0.050354 | 121.7377 | 0.07782 | 121.7926 | 0.46692 | -121.8567 | -121.5225 | 121.756 | 0.43945 | 6.6971 | 0.25635
1761.9688 | 121.962 | -0.53101 | 121.2936 | -0.0016785 | 6.9763 | 0.066541 | 0.06322 | 0.006977 | -0.0054731 | -0.0012988 | 0.0055543 | 0.0013778 | 0.016528 | 0.024526 | -0.0036359 | 0.027025 | -0.00030119 | 6.1432 | 121.1288 | -0.50354 | 121.2662 | -0.3067 | -0.42572 | -0.45776 | -0.13275 | -0.14191 | -0.12817 | 0.009155 | -0.041199 | -0.07782 | 0.013733 | 0.027466 | -0.16479 | -0.027466 | 0.2243 | 0.073242 | 0.10529 | 0.045776 | 0.07782 | 0.40283 | -121.4355 | -121.2845 | 0.48981 | 0.54474 | 0.45319 | 0.14191 | 0.050354 | 0.19684 | 121.7697 | 0.086975 | 0.13733 | 121.6324 | -0.013733 | 121.6599 | 0.3891 | -121.7972 | -121.4218 | 121.7972 | 0.54016 | 6.6742 | 0.39825
1763.7188 | 121.8475 | -0.77362 | 121.1563 | 0.005951 | 6.9778 | 0.064405 | 0.061938 | -0.0024224 | -0.0078229 | -0.00044443 | -0.00054933 | 0.0054368 | 0.015887 | 0.010427 | -0.011326 | 0.02553 | 0.001835 | 6.0425 | 121.0144 | -0.69122 | 121.0098 | -0.55847 | -0.65918 | -0.6958 | -0.31586 | -0.09613 | -0.16479 | -0.13275 | -0.16937 | -0.21515 | -0.10986 | 0.082398 | -0.14191 | -0.14648 | 0.21515 | 0.07782 | 0.11444 | -0.004578 | 0.032043 | 0.60883 | -121.2524 | -121.2891 | 0.60425 | 0.66376 | 0.55847 | 0.054932 | -0.050354 | 0.13275 | 121.701 | -0.004578 | 0.032044 | 121.7056 | 0.068665 | 121.788 | 0.67749 | -121.8475 | -121.3211 | 121.7834 | 0.64087 | 6.8161 | 0.45776
1765.4688 | 121.843 | -0.74158 | 121.1609 | -0.0016785 | 6.9784 | 0.065901 | 0.064501 | -0.0017816 | -0.0059003 | -0.0012988 | 0.0025025 | 0.0026596 | 0.015674 | 0.008077 | -0.0074811 | 0.024889 | -0.0037192 | 6.1249 | 121.0327 | -0.69122 | 121.0602 | -0.54932 | -0.6546 | -0.69122 | -0.27924 | -0.11444 | -0.15564 | -0.10529 | -0.17395 | -0.22888 | -0.073242 | 0.050354 | -0.12817 | -0.10071 | 0.19226 | 0.050354 | 0.086975 | 0 | 0.036621 | 0.58594 | -121.2753 | -121.2662 | 0.56763 | 0.66834 | 0.5127 | 0.082398 | -0.073242 | 0.14191 | 121.7514 | -0.01831 | 0.050354 | 121.7239 | 0.041199 | 121.7743 | 0.62714 | -121.8521 | -121.3165 | 121.8018 | 0.63629 | 6.8665 | 0.46234
1767.1406 | 121.962 | -0.70038 | 121.138 | -0.0016785 | 6.9771 | 0.066755 | 0.061083 | -0.00071343 | -0.0054731 | -1.7026e-05 | -0.00054933 | 0.0047958 | 0.016101 | 0.0072226 | -0.0055585 | 0.027453 | -0.0017966 | 6.1066 | 120.9869 | -0.66834 | 121.1288 | -0.46234 | -0.59052 | -0.6134 | -0.13275 | -0.13733 | -0.12817 | 0.013733 | -0.032043 | -0.091553 | 0.018311 | 0.032043 | -0.15106 | -0.009155 | 0.23804 | 0.086975 | 0.10986 | 0.054932 | 0.07782 | 0.5722 | -121.2753 | -121.1243 | 0.66833 | 0.71869 | 0.60882 | 0.14649 | 0.036621 | 0.20599 | 121.7972 | 0.096131 | 0.14191 | 121.6553 | -0.009155 | 121.6873 | 0.56305 | -121.8063 | -121.2662 | 121.8292 | 0.71411 | 6.8069 | 0.56763
1768.875 | 121.9666 | -0.58136 | 121.2616 | 0.005951 | 6.9789 | 0.066328 | 0.064715 | 0.0076178 | -0.0061139 | -0.0019396 | -0.00054933 | 0.0022324 | 0.015887 | 0.015127 | -0.0049175 | 0.028734 | -0.0020102 | 6.134 | 121.1288 | -0.52643 | 121.2524 | -0.31128 | -0.43488 | -0.48065 | -0.12817 | -0.15106 | -0.13275 | 0.004578 | -0.045776 | -0.09613 | 0 | 0.054932 | -0.13275 | -0.009156 | 0.27008 | 0.10071 | 0.14648 | 0.045776 | 0.091553 | 0.44861 | -121.4127 | -121.257 | 0.53558 | 0.58136 | 0.48523 | 0.13275 | 0.036621 | 0.21515 | 121.7789 | 0.086975 | 0.13733 | 121.6553 | -0.018311 | 121.7102 | 0.4303 | -121.788 | -121.3943 | 121.8338 | 0.58594 | 6.7154 | 0.45319
1770.625 | 121.8246 | -0.56305 | 121.3303 | 0.005951 | 6.9791 | 0.066969 | 0.065356 | -0.00092703 | -0.0067547 | 0.00041017 | -0.00054933 | 0.0037278 | 0.015246 | 0.0076498 | -0.0072675 | 0.025103 | -0.00671 | 6.0928 | 121.2112 | -0.50812 | 121.1975 | -0.44861 | -0.53558 | -0.55847 | -0.34332 | -0.09613 | -0.16937 | -0.11902 | -0.19684 | -0.25177 | -0.10529 | 0.054931 | -0.11902 | -0.13275 | 0.11444 | 0.004577 | 0.027466 | -0.050354 | -0.027465 | 0.39368 | -121.4264 | -121.4493 | 0.36621 | 0.45776 | 0.31128 | 0.064087 | -0.082397 | 0.05951 | 121.7056 | -0.027465 | 0.050354 | 121.7194 | 0.073243 | 121.7743 | 0.46692 | -121.8384 | -121.4996 | 121.7606 | 0.44403 | 6.6559 | 0.21973
1772.375 | 121.9849 | -0.5127 | 121.2799 | -0.016937 | 6.9752 | 0.065901 | 0.061297 | -0.0011408 | -0.0086773 | -0.002367 | -0.0036011 | 9.6204e-05 | 0.014819 | 0.014059 | -0.0087629 | 0.025316 | -0.0069236 | 6.1203 | 121.1609 | -0.44861 | 121.3303 | -0.2243 | -0.3479 | -0.38452 | -0.11444 | -0.11444 | -0.15106 | -0.018311 | -0.013733 | -0.054932 | 0.009155 | 0.064087 | -0.11902 | 0.050354 | 0.28839 | 0.12817 | 0.1648 | 0.064087 | 0.10071 | 0.36163 | -121.3943 | -121.2982 | 0.49896 | 0.52185 | 0.45776 | 0.16022 | 0.09613 | 0.2243 | 121.7789 | 0.13733 | 0.13275 | 121.6095 | 0.036621 | 121.6736 | 0.39825 | -121.7285 | -121.431 | 121.843 | 0.49438 | 6.633 | 0.39825
1774.0625 | 121.9757 | -0.59509 | 121.225 | -0.009308 | 6.9761 | 0.065046 | 0.06087 | -0.004345 | -0.0084637 | -0.0066394 | -0.0036011 | 0.0018052 | 0.015246 | 0.01235 | -0.010045 | 0.026385 | -0.0037192 | 6.189 | 121.0785 | -0.53558 | 121.2616 | -0.28381 | -0.40741 | -0.42114 | -0.13275 | -0.14648 | -0.13733 | 0.004578 | -0.018311 | -0.073242 | 0.009155 | 0.05951 | -0.14648 | 0.036621 | 0.31128 | 0.17395 | 0.18768 | 0.11444 | 0.12817 | 0.45776 | -121.3715 | -121.2204 | 0.57678 | 0.60425 | 0.52185 | 0.14648 | 0.064087 | 0.25177 | 121.7972 | 0.11902 | 0.14191 | 121.6141 | -0.009155 | 121.6736 | 0.44861 | -121.7606 | -121.3623 | 121.8567 | 0.59967 | 6.7841 | 0.46234
1775.8125 | 121.9528 | -0.56763 | 121.2982 | -0.009308 | 6.9763 | 0.065046 | 0.063006 | 0.00014097 | -0.0073957 | -0.002367 | -0.00054933 | 0.0005234 | 0.015887 | 0.011922 | -0.0076947 | 0.02788 | -0.00436 | 6.0654 | 121.1151 | -0.53101 | 121.2341 | -0.35706 | -0.45319 | -0.48523 | -0.20599 | -0.14648 | -0.13275 | -0.032043 | -0.064087 | -0.10071 | -0.018311 | 0.036621 | -0.18311 | -0.064087 | 0.21057 | 0.082398 | 0.11444 | 0.045777 | 0.07782 | 0.43488 | -121.4447 | -121.3303 | 0.50354 | 0.54932 | 0.46692 | 0.11444 | 0.032043 | 0.17395 | 121.7651 | 0.068664 | 0.10071 | 121.6461 | -0.013733 | 121.6827 | 0.42114 | -121.8292 | -121.431 | 121.8018 | 0.53558 | 6.633 | 0.36163
1777.5625 | 121.843 | -0.69122 | 121.225 | -0.009308 | 6.9799 | 0.064405 | 0.065356 | -0.0037042 | -0.0039777 | -0.0032214 | -0.00054933 | 0.003514 | 0.016101 | 0.010641 | -0.0066265 | 0.024889 | 0.00033961 | 6.0837 | 121.0785 | -0.65002 | 121.0785 | -0.54016 | -0.65918 | -0.67291 | -0.30212 | -0.09613 | -0.16022 | -0.13733 | -0.19226 | -0.24719 | -0.10529 | 0.041199 | -0.14648 | -0.14648 | 0.15106 | 0.01831 | 0.032043 | -0.022889 | -0.009156 | 0.53101 | -121.3211 | -121.3623 | 0.49896 | 0.58594 | 0.44403 | 0.054931 | -0.086975 | 0.10986 | 121.7285 | -0.032044 | 0.022888 | 121.7285 | 0.064087 | 121.7697 | 0.59509 | -121.875 | -121.3852 | 121.7697 | 0.55389 | 6.7749 | 0.3891
1779.2188 | 121.8567 | -0.55389 | 121.3669 | -0.009308 | 6.9761 | 0.06526 | 0.061938 | -0.0022088 | -0.0078229 | -0.0036486 | -0.00054933 | 0.002446 | 0.016528 | 0.017049 | -0.010686 | 0.025316 | -0.0052146 | 6.0745 | 121.2479 | -0.48065 | 121.225 | -0.37079 | -0.44403 | -0.48065 | -0.32044 | -0.10529 | -0.16479 | -0.12817 | -0.17853 | -0.2243 | -0.09613 | 0.073242 | -0.11902 | -0.14191 | 0.18311 | 0.073242 | 0.10986 | 0 | 0.036621 | 0.3891 | -121.4722 | -121.4951 | 0.37537 | 0.45776 | 0.32959 | 0.068665 | -0.059509 | 0.10986 | 121.7056 | -0.013733 | 0.036621 | 121.7285 | 0.059509 | 121.8018 | 0.44861 | -121.8475 | -121.5317 | 121.7789 | 0.42572 | 6.6284 | 0.23346
1780.9062 | 121.8658 | -0.52185 | 121.3623 | -0.009308 | 6.9797 | 0.065687 | 0.064501 | -0.0013544 | -0.0065411 | -0.0021532 | 0.0025025 | 0.0033004 | 0.01781 | 0.0095724 | -0.0068403 | 0.027453 | -0.0024374 | 6.0974 | 121.2433 | -0.4715 | 121.2341 | -0.37537 | -0.48523 | -0.49439 | -0.27466 | -0.10529 | -0.15106 | -0.086975 | -0.16937 | -0.21973 | -0.073242 | 0.050354 | -0.11902 | -0.12817 | 0.14648 | 0.027466 | 0.036622 | -0.022888 | -0.013732 | 0.37079 | -121.4676 | -121.4493 | 0.35248 | 0.44861 | 0.30212 | 0.07782 | -0.068665 | 0.096131 | 121.7056 | -0.018311 | 0.064087 | 121.7148 | 0.045776 | 121.7651 | 0.41656 | -121.8338 | -121.5134 | 121.756 | 0.43488 | 6.6193 | 0.24719
1782.6562 | 121.9391 | -0.54016 | 121.3257 | -0.0016785 | 6.9778 | 0.063123 | 0.061297 | -0.00071343 | -0.0082501 | -0.0021532 | 0.0025025 | 0.0013778 | 0.015887 | 0.013631 | -0.010045 | 0.025957 | -0.0041464 | 6.134 | 121.1838 | -0.47607 | 121.3257 | -0.25177 | -0.36163 | -0.40741 | -0.16937 | -0.13733 | -0.14191 | -0.027466 | -0.059509 | -0.091553 | -0.013733 | 0.064087 | -0.14191 | 0 | 0.28839 | 0.13275 | 0.17853 | 0.068664 | 0.11444 | 0.39825 | -121.463 | -121.3531 | 0.48065 | 0.52643 | 0.44861 | 0.12817 | 0.050354 | 0.2243 | 121.8018 | 0.082398 | 0.11444 | 121.6599 | 0.004578 | 121.7239 | 0.40283 | -121.8018 | -121.4676 | 121.8658 | 0.5127 | 6.6742 | 0.37079
1784.3906 | 121.9986 | -0.51727 | 121.3303 | 0.005951 | 6.9744 | 0.064405 | 0.062579 | 0.006336 | -0.0097455 | -0.0019396 | -0.0036011 | 0.0005234 | 0.015246 | 0.025594 | -0.0049175 | 0.026598 | -0.003292 | 6.0883 | 121.1609 | -0.48523 | 121.2799 | -0.29297 | -0.38452 | -0.42572 | -0.19684 | -0.13275 | -0.13275 | -0.013733 | -0.059509 | -0.07782 | 0 | 0.032044 | -0.16937 | -0.050354 | 0.2243 | 0.091553 | 0.13275 | 0.059509 | 0.10071 | 0.38452 | -121.463 | -121.344 | 0.45776 | 0.51727 | 0.43945 | 0.13275 | 0.054931 | 0.19226 | 121.7651 | 0.073242 | 0.11902 | 121.6461 | 0 | 121.6782 | 0.38452 | -121.8155 | -121.463 | 121.7972 | 0.50354 | 6.6055 | 0.32043
1786.0781 | 121.9482 | -0.52643 | 121.2982 | -0.0016785 | 6.9771 | 0.065046 | 0.061724 | 0.0050544 | -0.0061139 | -0.0012988 | -0.0036011 | 0.0011642 | 0.014392 | 0.015981 | -0.0079083 | 0.025744 | -0.003292 | 6.1707 | 121.1472 | -0.48523 | 121.3165 | -0.27466 | -0.37537 | -0.43945 | -0.15106 | -0.13733 | -0.14191 | -0.018311 | -0.036621 | -0.091553 | -0.018311 | 0.041199 | -0.15106 | 0.01831 | 0.25177 | 0.086975 | 0.15106 | 0.045776 | 0.10986 | 0.38452 | -121.4355 | -121.3165 | 0.48981 | 0.50812 | 0.43488 | 0.1236 | 0.050354 | 0.21057 | 121.8018 | 0.10529 | 0.1236 | 121.6324 | 0.004578 | 121.6736 | 0.3891 | -121.7834 | -121.4401 | 121.843 | 0.50812 | 6.6971 | 0.37537
1787.8438 | 121.9574 | -0.54474 | 121.3028 | -0.0016785 | 6.9776 | 0.065473 | 0.064074 | -0.00049983 | -0.0063275 | 0.00041017 | -0.00054933 | 0.0018052 | 0.016742 | 0.011068 | -0.00085871 | 0.025316 | -0.001583 | 6.0791 | 121.1472 | -0.46692 | 121.2982 | -0.28381 | -0.43488 | -0.45319 | -0.15106 | -0.14648 | -0.12817 | -0.018311 | -0.086975 | -0.13275 | -0.018311 | 0.07782 | -0.15564 | -0.004577 | 0.26093 | 0.091553 | 0.10986 | 0.013733 | 0.032044 | 0.41656 | -121.4493 | -121.3211 | 0.45776 | 0.52643 | 0.41199 | 0.10986 | -0.004577 | 0.18311 | 121.7651 | 0.041199 | 0.10986 | 121.6141 | -0.01831 | 121.6919 | 0.39825 | -121.7697 | -121.431 | 121.843 | 0.52643 | 6.6238 | 0.39368
1789.5312 | 121.9299 | -0.52643 | 121.3623 | -0.009308 | 6.975 | 0.065473 | 0.064074 | 0.00014097 | -0.0071821 | -0.0021532 | -0.00054933 | 0.004155 | 0.013751 | 0.01534 | -0.0094037 | 0.022753 | -0.0047874 | 6.1935 | 121.2067 | -0.44403 | 121.3623 | -0.24719 | -0.36163 | -0.3891 | -0.16937 | -0.13275 | -0.12817 | -0.041199 | -0.054932 | -0.09613 | -0.032043 | 0.082397 | -0.15564 | 0 | 0.27924 | 0.13733 | 0.1648 | 0.054932 | 0.082398 | 0.39825 | -121.4951 | -121.4035 | 0.4715 | 0.49439 | 0.4303 | 0.096131 | 0.032044 | 0.19684 | 121.8063 | 0.073242 | 0.086975 | 121.6507 | -0.004577 | 121.7331 | 0.39368 | -121.8063 | -121.4905 | 121.8887 | 0.48523 | 6.72 | 0.35706
1791.2656 | 121.9162 | -0.54474 | 121.3074 | 0.005951 | 6.9759 | 0.066541 | 0.065783 | -0.0017816 | -0.0084637 | -0.00087163 | -0.00054933 | 0.0050094 | 0.017169 | 0.015127 | -0.0083355 | 0.024676 | 0.00055321 | 6.1111 | 121.2067 | -0.47607 | 121.2662 | -0.3479 | -0.44861 | -0.46234 | -0.22888 | -0.12817 | -0.15106 | -0.059509 | -0.10529 | -0.15564 | -0.036621 | 0.068665 | -0.10071 | -0.041199 | 0.19684 | 0.082398 | 0.096131 | 0.013733 | 0.027466 | 0.39368 | -121.4355 | -121.3669 | 0.43945 | 0.50812 | 0.3891 | 0.11444 | -0.004578 | 0.12817 | 121.7422 | 0.045776 | 0.091553 | 121.6827 | 0.022888 | 121.7514 | 0.41656 | -121.7834 | -121.4584 | 121.8109 | 0.48523 | 6.6559 | 0.31586
1793 | 121.962 | -0.5127 | 121.3669 | -0.0016785 | 6.9808 | 0.06526 | 0.06322 | -0.0028498 | -0.0076093 | -0.0066394 | -0.00054933 | 0.0026596 | 0.014178 | 0.013845 | -0.0096173 | 0.023394 | -0.0030784 | 6.1707 | 121.1884 | -0.43488 | 121.376 | -0.21515 | -0.32959 | -0.36621 | -0.12817 | -0.12817 | -0.12817 | -0.004578 | -0.013733 | -0.082397 | 0 | 0.07782 | -0.17853 | 0.009156 | 0.29755 | 0.14648 | 0.18311 | 0.068664 | 0.10529 | 0.38452 | -121.4951 | -121.3715 | 0.49896 | 0.5127 | 0.4303 | 0.12817 | 0.045777 | 0.21973 | 121.8109 | 0.11444 | 0.1236 | 121.6232 | 0 | 121.701 | 0.38452 | -121.8018 | -121.4951 | 121.8887 | 0.50812 | 6.6833 | 0.38452
1794.75 | 121.962 | -0.49896 | 121.3531 | 0.005951 | 6.9789 | 0.064832 | 0.062792 | -0.0013544 | -0.0061139 | -0.00087163 | -0.00054933 | 0.0039414 | 0.014819 | 0.019399 | -0.0070539 | 0.024676 | -0.0022238 | 6.1523 | 121.1929 | -0.43945 | 121.3669 | -0.21973 | -0.33875 | -0.38452 | -0.16479 | -0.1236 | -0.14191 | -0.027466 | -0.036621 | -0.10071 | -0.027466 | 0.059509 | -0.16022 | 0.013733 | 0.27924 | 0.11444 | 0.16022 | 0.054932 | 0.10071 | 0.35706 | -121.4767 | -121.3806 | 0.46234 | 0.4715 | 0.39825 | 0.11444 | 0.041199 | 0.21973 | 121.8063 | 0.10529 | 0.11444 | 121.6324 | 0.018311 | 121.6919 | 0.37537 | -121.7926 | -121.4951 | 121.8658 | 0.4715 | 6.6513 | 0.33417
1796.4375 | 121.843 | -0.58594 | 121.3303 | -0.0016785 | 6.9763 | 0.064192 | 0.06621 | -0.0022088 | -0.0069683 | -0.0019396 | -0.0036011 | 0.0033004 | 0.018451 | 0.01534 | -0.011113 | 0.02553 | -0.0028646 | 6.0745 | 121.2021 | -0.52185 | 121.1975 | -0.41657 | -0.50354 | -0.54016 | -0.3067 | -0.07782 | -0.18768 | -0.14191 | -0.16937 | -0.21515 | -0.086975 | 0.064086 | -0.12817 | -0.13275 | 0.16937 | 0.045776 | 0.082397 | -0.01831 | 0.018311 | 0.39825 | -121.4081 | -121.4722 | 0.41656 | 0.49896 | 0.37079 | 0.10071 | -0.027466 | 0.10529 | 121.7194 | 0.01831 | 0.045776 | 121.7239 | 0.10986 | 121.788 | 0.50812 | -121.8521 | -121.5179 | 121.7834 | 0.44403 | 6.6605 | 0.27924
1798.1875 | 121.8796 | -0.53101 | 121.4218 | -0.016937 | 6.9786 | 0.065473 | 0.063433 | -7.2628e-05 | -0.0091047 | 0.0014784 | 0.0025025 | 0.0033004 | 0.014178 | 0.0099996 | -0.0076947 | 0.024248 | -0.0011558 | 6.0974 | 121.2891 | -0.46234 | 121.3028 | -0.32959 | -0.41657 | -0.4303 | -0.27466 | -0.10071 | -0.16022 | -0.082397 | -0.1236 | -0.19226 | -0.059509 | 0.068665 | -0.13275 | -0.11902 | 0.20142 | 0.10071 | 0.11444 | 0.032043 | 0.045776 | 0.37079 | -121.5225 | -121.5042 | 0.40741 | 0.4715 | 0.33874 | 0.10071 | -0.032044 | 0.13275 | 121.7651 | 0.036621 | 0.07782 | 121.7514 | 0.059509 | 121.8201 | 0.4303 | -121.8842 | -121.582 | 121.8338 | 0.44861 | 6.6284 | 0.25635
1799.9219 | 121.9254 | -0.46234 | 121.4081 | -0.0016785 | 6.9765 | 0.065687 | 0.063006 | 0.0020636 | -0.0073957 | -0.0049304 | -0.00054933 | 0.0018052 | 0.01546 | 0.014486 | -0.0040631 | 0.027453 | -0.001583 | 6.0745 | 121.2662 | -0.41657 | 121.3303 | -0.26093 | -0.36621 | -0.39368 | -0.25635 | -0.12817 | -0.15106 | -0.073242 | -0.086975 | -0.15106 | -0.036621 | 0.045776 | -0.14191 | -0.07782 | 0.20142 | 0.068664 | 0.09613 | 0.022888 | 0.050354 | 0.31128 | -121.5363 | -121.4813 | 0.37537 | 0.42572 | 0.31128 | 0.11444 | 0 | 0.15564 | 121.7468 | 0.064087 | 0.07782 | 121.6827 | 0.022888 | 121.7285 | 0.33417 | -121.8246 | -121.5591 | 121.7926 | 0.3891 | 6.5369 | 0.20599
1801.5938 | 121.8979 | -0.49896 | 121.4264 | -0.0016785 | 6.9786 | 0.064619 | 0.06621 | 0.0022772 | -0.0071821 | -0.0015124 | -0.00054933 | 0.003514 | 0.012683 | 0.017049 | -0.0081219 | 0.026598 | -0.0056418 | 6.1615 | 121.2799 | -0.4303 | 121.3531 | -0.27924 | -0.37537 | -0.41199 | -0.23346 | -0.10986 | -0.11444 | -0.059509 | -0.07782 | -0.17853 | -0.059509 | 0.068664 | -0.14649 | -0.073243 | 0.21973 | 0.086975 | 0.1236 | 0.018311 | 0.054932 | 0.38452 | -121.5363 | -121.4859 | 0.42114 | 0.43945 | 0.32043 | 0.054932 | -0.064087 | 0.15106 | 121.7834 | 0.036621 | 0.054932 | 121.7102 | 0.004578 | 121.7789 | 0.3891 | -121.8567 | -121.5408 | 121.8521 | 0.43945 | 6.6605 | 0.2655
1803.3438 | 121.9208 | -0.48523 | 121.3715 | -0.0016785 | 6.9778 | 0.063978 | 0.063006 | -0.0013544 | -0.0061139 | -0.0019396 | -0.0036011 | 0.0015914 | 0.011828 | 0.010427 | -0.0057721 | 0.026385 | 0.0048258 | 6.0654 | 121.2204 | -0.42572 | 121.312 | -0.28839 | -0.38452 | -0.41657 | -0.23804 | -0.11902 | -0.14648 | -0.041199 | -0.064087 | -0.1236 | -0.018311 | 0.059509 | -0.15106 | -0.059509 | 0.19684 | 0.068664 | 0.10071 | 0.009155 | 0.041199 | 0.33875 | -121.4905 | -121.4127 | 0.42114 | 0.46692 | 0.36163 | 0.12817 | 0.022888 | 0.13733 | 121.7377 | 0.082397 | 0.10529 | 121.6461 | 0.027465 | 121.7056 | 0.36621 | -121.7972 | -121.5179 | 121.7972 | 0.44403 | 6.5506 | 0.24719
1805.0312 | 121.9803 | -0.40283 | 121.4172 | -0.0016785 | 6.9782 | 0.064832 | 0.063647 | 0.0033454 | -0.0067547 | -0.002367 | -0.00054933 | 0.0033004 | 0.015887 | 0.008077 | -0.0042767 | 0.028307 | -0.0037192 | 6.0745 | 121.2845 | -0.35248 | 121.4493 | -0.16022 | -0.30212 | -0.31586 | -0.14648 | -0.13275 | -0.13275 | 0.018311 | -0.013733 | -0.082397 | 0.018311 | 0.050354 | -0.13275 | 0.032044 | 0.24262 | 0.086975 | 0.10071 | 0.036621 | 0.050354 | 0.27008 | -121.55 | -121.3989 | 0.3891 | 0.42114 | 0.32044 | 0.15106 | 0.050354 | 0.19226 | 121.8018 | 0.11902 | 0.15106 | 121.637 | 0 | 121.6873 | 0.27008 | -121.7697 | -121.55 | 121.8521 | 0.42114 | 6.4774 | 0.25635
1806.7812 | 121.9025 | -0.44403 | 121.4401 | 0.005951 | 6.978 | 0.063978 | 0.06386 | 0.0048408 | -0.0046185 | -0.0040758 | -0.0036011 | 0.0037278 | 0.014819 | 0.018331 | -0.0081219 | 0.025316 | -0.0011558 | 6.102 | 121.3257 | -0.40283 | 121.3486 | -0.29297 | -0.36163 | -0.41199 | -0.26093 | -0.091553 | -0.15106 | -0.082397 | -0.09613 | -0.16937 | -0.050354 | 0.041199 | -0.11444 | -0.091553 | 0.15106 | 0.032044 | 0.082398 | -0.009155 | 0.041199 | 0.29297 | -121.5317 | -121.5225 | 0.3479 | 0.39368 | 0.27466 | 0.10071 | -0.018311 | 0.10986 | 121.7514 | 0.054932 | 0.068665 | 121.7285 | 0.059509 | 121.7697 | 0.35248 | -121.843 | -121.5912 | 121.7926 | 0.36163 | 6.546 | 0.18311
1808.4531 | 121.8796 | -0.45319 | 121.4584 | 0.005951 | 6.9791 | 0.063337 | 0.064288 | 0.0029182 | -0.0080365 | -0.0010852 | -0.00054933 | 0.002446 | 0.015674 | 0.014699 | -0.0064129 | 0.025103 | -0.0069236 | 6.0791 | 121.3623 | -0.39368 | 121.3028 | -0.31586 | -0.40741 | -0.42572 | -0.29755 | -0.086975 | -0.15564 | -0.09613 | -0.11902 | -0.21515 | -0.073242 | 0.059509 | -0.09613 | -0.15564 | 0.13733 | 0.027466 | 0.045776 | -0.032043 | -0.013733 | 0.29755 | -121.5454 | -121.5546 | 0.33417 | 0.37994 | 0.23804 | 0.082398 | -0.059509 | 0.07782 | 121.6965 | 0.036621 | 0.05951 | 121.756 | 0.068665 | 121.8155 | 0.36621 | -121.8521 | -121.6141 | 121.756 | 0.35706 | 6.5323 | 0.15564
1810.1875 | 121.8842 | -0.46234 | 121.4401 | 0.02121 | 6.978 | 0.063978 | 0.06322 | -0.002636 | -0.0069683 | -0.0027942 | 0.0025025 | 0.0030868 | 0.017383 | 0.012777 | -0.0094037 | 0.025103 | -0.0047874 | 6.0883 | 121.312 | -0.42114 | 121.3394 | -0.30212 | -0.3479 | -0.40741 | -0.26093 | -0.09613 | -0.14648 | -0.086975 | -0.082397 | -0.17395 | -0.059509 | 0.041198 | -0.12817 | -0.10071 | 0.16022 | 0.054931 | 0.11444 | 0.013733 | 0.073243 | 0.31586 | -121.5363 | -121.5271 | 0.37994 | 0.40283 | 0.28839 | 0.086975 | -0.027466 | 0.11902 | 121.7606 | 0.064087 | 0.059509 | 121.7331 | 0.050354 | 121.7743 | 0.36621 | -121.8613 | -121.5866 | 121.8018 | 0.37537 | 6.5506 | 0.20142
1811.875 | 121.9803 | -1.4328 | 120.401 | -0.0016785 | 6.9756 | 0.062483 | 0.059802 | 0.00014097 | -0.0069683 | -0.0015124 | -0.00054933 | 0.0013778 | 0.014819 | 0.01769 | -0.0066265 | 0.028521 | 0.0011942 | 5.8273 | 120.2545 | -1.4008 | 120.3598 | -1.2039 | -1.3046 | -1.355 | -0.19226 | -0.13275 | -0.13733 | -0.004578 | 0 | -0.068665 | 0.018311 | 0.032043 | -0.14648 | -0.041199 | 0.22888 | 0.07782 | 0.12817 | 0.045777 | 0.096131 | 1.2955 | -120.5338 | -120.4056 | 1.4328 | 1.4511 | 1.3641 | 0.15564 | 0.068664 | 0.19684 | 121.7606 | 0.13733 | 0.13275 | 121.6553 | 0.004578 | 121.6873 | 1.3 | -121.8018 | -120.5383 | 121.7926 | 1.4282 | 7.2601 | 1.2405
1813.6094 | 121.9711 | -1.9821 | 119.8837 | -0.0016785 | 6.9767 | 0.066541 | 0.064074 | -0.0051996 | -0.0048321 | -0.0012988 | -0.00054933 | 0.0009506 | 0.015033 | 0.017049 | -0.0081219 | 0.026598 | -0.0028646 | 5.7816 | 119.7601 | -1.9135 | 119.8746 | -1.7258 | -1.8448 | -1.8951 | -0.17853 | -0.12817 | -0.1236 | -0.018311 | 0.004578 | -0.068665 | 0.013733 | 0.068665 | -0.1236 | -0.009155 | 0.25635 | 0.086975 | 0.13733 | 0.01831 | 0.068664 | 1.8585 | -120.0119 | -119.902 | 1.9867 | 1.9958 | 1.9135 | 0.13733 | 0.054931 | 0.18768 | 121.788 | 0.12817 | 0.10528 | 121.6736 | -0.004578 | 121.7422 | 1.8539 | -121.7972 | -120.0073 | 121.8567 | 1.9638 | 7.7637 | 1.8036
1815.2812 | 121.9345 | -1.7395 | 120.0943 | 0.005951 | 6.9765 | 0.06526 | 0.062151 | -0.0011408 | -0.0073957 | -0.0036486 | 0.0025025 | 0.0033004 | 0.01311 | 0.01769 | -0.0066265 | 0.025744 | -0.0041464 | 5.7999 | 119.957 | -1.6708 | 120.076 | -1.5152 | -1.6342 | -1.6525 | -0.20142 | -0.12817 | -0.10529 | -0.054932 | -0.073242 | -0.1236 | -0.032043 | 0.068665 | -0.13733 | -0.01831 | 0.2243 | 0.086975 | 0.10529 | 0.01831 | 0.036621 | 1.6342 | -120.2225 | -120.1492 | 1.6663 | 1.7075 | 1.6159 | 0.073243 | -0.01831 | 0.15564 | 121.7468 | 0.032044 | 0.050354 | 121.6278 | -0.022888 | 121.6965 | 1.6113 | -121.7651 | -120.1996 | 121.8155 | 1.6846 | 7.5394 | 1.5381
1817.0312 | 121.9391 | -1.8539 | 119.9982 | 0.005951 | 6.9776 | 0.063978 | 0.063647 | 0.0012092 | -0.0056867 | -0.00087163 | -0.00054933 | 0.0015914 | 0.016528 | 0.016836 | -0.0068403 | 0.027453 | -0.0035056 | 5.7999 | 119.8654 | -1.7853 | 119.9799 | -1.5701 | -1.7349 | -1.7532 | -0.14191 | -0.1236 | -0.11902 | -0.027466 | 0.009155 | -0.11444 | 0 | 0.068665 | -0.13275 | -0.018311 | 0.28381 | 0.10071 | 0.11902 | 0.032043 | 0.050354 | 1.7349 | -120.1218 | -120.0256 | 1.8631 | 1.8539 | 1.7395 | 0.11902 | 0.004578 | 0.21515 | 121.7651 | 0.12817 | 0.091553 | 121.6507 | -0.004577 | 121.7194 | 1.7303 | -121.7834 | -120.1172 | 121.8338 | 1.8265 | 7.6538 | 1.712
1818.7812 | 121.9528 | -2.0325 | 119.8151 | -0.0016785 | 6.9765 | 0.066969 | 0.064715 | 0.00185 | -0.0056867 | -0.0025806 | 0.0025025 | 0.0015914 | 0.016314 | 0.020467 | -0.0083355 | 0.027453 | -0.00051479 | 5.7358 | 119.6365 | -2.0004 | 119.7784 | -1.7761 | -1.9363 | -1.9455 | -0.17395 | -0.14191 | -0.10529 | -0.045776 | 0.004578 | -0.1236 | -0.027466 | 0.032044 | -0.17853 | -0.036621 | 0.25635 | 0.086975 | 0.096131 | 0.054931 | 0.064087 | 1.9272 | -119.957 | -119.8608 | 2.037 | 2.005 | 1.9089 | 0.07782 | -0.01831 | 0.2243 | 121.7789 | 0.10986 | 0.05951 | 121.637 | -0.036621 | 121.669 | 1.8906 | -121.8155 | -119.9203 | 121.8109 | 1.9867 | 7.7683 | 1.8585
1820.4688 | 121.9116 | -1.918 | 119.9844 | -0.016937 | 6.978 | 0.065473 | 0.064074 | 0.0029182 | -0.0059003 | -0.003435 | -0.00054933 | 0.003514 | 0.013965 | 0.0023092 | -0.0091901 | 0.024889 | -0.005001 | 5.8136 | 119.8563 | -1.8539 | 119.9066 | -1.6983 | -1.8173 | -1.8448 | -0.21057 | -0.10529 | -0.12817 | -0.068665 | -0.009155 | -0.15564 | -0.018311 | 0.064087 | -0.12817 | -0.07782 | 0.21973 | 0.073242 | 0.10071 | 0.009155 | 0.036621 | 1.7899 | -120.0897 | -120.0531 | 1.9089 | 1.8997 | 1.7624 | 0.10986 | -0.027466 | 0.15564 | 121.7606 | 0.11902 | 0.059509 | 121.7102 | 0.022888 | 121.7743 | 1.8127 | -121.8384 | -120.1126 | 121.8246 | 1.8494 | 7.7316 | 1.7075
1822.2031 | 121.9757 | -1.6891 | 120.1126 | -0.0016785 | 6.9793 | 0.066328 | 0.060442 | 0.00014097 | -0.0082501 | -0.003435 | -0.00054933 | 0.0018052 | 0.014819 | 0.01769 | -0.0040631 | 0.025957 | -0.0011558 | 5.8273 | 120.0073 | -1.6388 | 120.1172 | -1.4603 | -1.6159 | -1.6342 | -0.1236 | -0.13733 | -0.07782 | 0.027466 | 0.068665 | -0.09613 | 0.050354 | 0.050354 | -0.10529 | 0.004577 | 0.22888 | 0.054932 | 0.073242 | 0.004578 | 0.022888 | 1.6113 | -120.2499 | -120.0851 | 1.7578 | 1.7395 | 1.593 | 0.12817 | -0.01831 | 0.17853 | 121.756 | 0.14649 | 0.10529 | 121.6461 | -0.059509 | 121.6965 | 1.5518 | -121.7514 | -120.1904 | 121.8063 | 1.7166 | 7.5165 | 1.5656
1823.9375 | 121.843 | -1.7807 | 120.1584 | -0.016937 | 6.9784 | 0.060987 | 0.064501 | -0.002636 | -0.0097455 | -0.0062122 | 0.0025025 | 0.003514 | 0.013965 | 0.011709 | -0.010472 | 0.023607 | -0.0039328 | 5.7632 | 120.0394 | -1.7166 | 119.989 | -1.6022 | -1.6891 | -1.7212 | -0.30212 | -0.073242 | -0.14191 | -0.12817 | -0.064087 | -0.20142 | -0.068665 | 0.064087 | -0.11902 | -0.16937 | 0.17853 | 0.05951 | 0.091553 | -0.004577 | 0.027466 | 1.6388 | -120.2316 | -120.2866 | 1.7166 | 1.712 | 1.5793 | 0.073242 | -0.059509 | 0.11444 | 121.7056 | 0.07782 | 0.013733 | 121.756 | 0.068665 | 121.8201 | 1.7075 | -121.875 | -120.3003 | 121.7697 | 1.6525 | 7.5439 | 1.4786
1825.6875 | 121.8475 | -1.8631 | 120.0668 | 0.005951 | 6.9803 | 0.065687 | 0.06322 | 0.0037726 | -0.0076093 | -0.0027942 | -0.00054933 | 0.0033004 | 0.016955 | 0.011709 | -0.0079083 | 0.023821 | -0.003292 | 5.7449 | 119.9478 | -1.7853 | 119.8837 | -1.7395 | -1.8265 | -1.8311 | -0.31128 | -0.09613 | -0.14648 | -0.11902 | -0.086975 | -0.2243 | -0.068665 | 0.07782 | -0.11902 | -0.1831 | 0.1236 | 0.032043 | 0.036621 | -0.045777 | -0.041199 | 1.7166 | -120.163 | -120.1859 | 1.7761 | 1.7944 | 1.6388 | 0.077819 | -0.07782 | 0.045776 | 121.669 | 0.059509 | 0.027465 | 121.7331 | 0.050354 | 121.8109 | 1.767 | -121.8521 | -120.2133 | 121.7468 | 1.7441 | 7.608 | 1.5518
1827.375 | 121.875 | -1.8173 | 120.1126 | -0.009308 | 6.9793 | 0.063764 | 0.062365 | 0.0012092 | -0.0084637 | -0.0015124 | -0.0036011 | 0.0045822 | 0.013965 | 0.011495 | -0.011326 | 0.02553 | -0.002651 | 5.7541 | 119.9661 | -1.7761 | 119.9387 | -1.6479 | -1.7578 | -1.7761 | -0.29297 | -0.09613 | -0.13733 | -0.12817 | -0.050354 | -0.18768 | -0.059509 | 0.041199 | -0.14648 | -0.17395 | 0.16937 | 0.041199 | 0.05951 | 0 | 0.018311 | 1.68 | -120.2087 | -120.2408 | 1.767 | 1.7578 | 1.6296 | 0.07782 | -0.050354 | 0.12817 | 121.7148 | 0.086975 | 0.009155 | 121.7422 | 0.041199 | 121.7834 | 1.7212 | -121.8887 | -120.2499 | 121.756 | 1.6891 | 7.5714 | 1.5244
1829.1094 | 121.9711 | -1.7487 | 120.0851 | -0.0016785 | 6.9759 | 0.065046 | 0.061938 | -7.2628e-05 | -0.0078229 | -1.7026e-05 | -0.00054933 | 0.000737 | 0.016528 | 0.013845 | -0.0081219 | 0.026812 | -0.0017966 | 5.7312 | 119.9387 | -1.7029 | 120.0348 | -1.5381 | -1.6342 | -1.6846 | -0.16937 | -0.15106 | -0.11902 | -0.018311 | 0.054932 | -0.059509 | 0.036621 | 0.045776 | -0.14648 | -0.050354 | 0.21057 | 0.064087 | 0.11444 | 0.018311 | 0.068665 | 1.6296 | -120.2362 | -120.1035 | 1.8036 | 1.7853 | 1.6891 | 0.15564 | 0.05951 | 0.1648 | 121.7377 | 0.17395 | 0.10071 | 121.6415 | -0.032043 | 121.6873 | 1.5976 | -121.788 | -120.2042 | 121.7834 | 1.7303 | 7.4799 | 1.5793
1830.8438 | 121.994 | -1.68 | 120.1401 | -0.009308 | 6.9789 | 0.06825 | 0.064288 | -0.001568 | -0.0073957 | 0.00062377 | -0.00054933 | 0.002446 | 0.013751 | 0.011922 | -0.0044903 | 0.026598 | -0.0024374 | 5.8044 | 119.989 | -1.6388 | 120.1401 | -1.4557 | -1.6067 | -1.6159 | -0.11902 | -0.14191 | -0.086975 | 0.022888 | 0.059509 | -0.07782 | 0.045776 | 0.041199 | -0.15106 | 0 | 0.2243 | 0.064087 | 0.073243 | 0.022888 | 0.032044 | 1.593 | -120.282 | -120.1172 | 1.7395 | 1.7258 | 1.6022 | 0.13275 | 0.009155 | 0.18311 | 121.7789 | 0.14648 | 0.10986 | 121.6278 | -0.054932 | 121.669 | 1.5381 | -121.7789 | -120.2271 | 121.8201 | 1.7029 | 7.4844 | 1.561
1832.5312 | 121.907 | -1.6113 | 120.282 | -0.0016785 | 6.978 | 0.062055 | 0.062792 | 0.003559 | -0.0071821 | -0.001726 | 0.0025025 | 0.004155 | 0.014605 | 0.0078634 | -0.0089765 | 0.025316 | -0.0024374 | 5.8548 | 120.1447 | -1.561 | 120.1904 | -1.3962 | -1.5198 | -1.5518 | -0.18768 | -0.10986 | -0.12817 | -0.073242 | -0.009155 | -0.12817 | -0.022888 | 0.050354 | -0.13733 | -0.091552 | 0.21515 | 0.059509 | 0.091553 | 0.009155 | 0.041199 | 1.4832 | -120.3918 | -120.3552 | 1.6022 | 1.5884 | 1.4832 | 0.10529 | 0 | 0.1648 | 121.7514 | 0.11902 | 0.054932 | 121.7056 | 0.018311 | 121.756 | 1.5015 | -121.843 | -120.4102 | 121.8018 | 1.5381 | 7.4661 | 1.4236
1834.2812 | 121.8384 | -1.8448 | 120.108 | -0.0016785 | 6.9789 | 0.06526 | 0.065356 | 0.0039862 | -0.0044049 | 0.00019657 | -0.0036011 | 0.0039414 | 0.016528 | 0.015554 | -0.0066265 | 0.024462 | -0.0024374 | 5.69 | 119.9203 | -1.7761 | 119.8746 | -1.7532 | -1.8539 | -1.8494 | -0.32044 | -0.091553 | -0.13733 | -0.11902 | -0.07782 | -0.2243 | -0.059509 | 0.068665 | -0.18768 | -0.23346 | 0.091553 | -0.004577 | -0.009155 | -0.073242 | -0.07782 | 1.7075 | -120.1996 | -120.2271 | 1.767 | 1.7853 | 1.6205 | 0.07782 | -0.086975 | 0.022888 | 121.6507 | 0.059509 | 0.01831 | 121.6965 | 0.045776 | 121.7651 | 1.7532 | -121.8842 | -120.2454 | 121.7194 | 1.7258 | 7.5348 | 1.5244
1835.9688 | 121.9482 | -1.7258 | 120.1126 | -0.0016785 | 6.9808 | 0.063764 | 0.062579 | 0.0037726 | -0.0088911 | -0.0027942 | -0.0036011 | 0.0037278 | 0.015887 | 0.014699 | -0.0072675 | 0.027025 | -0.0035056 | 5.69 | 120.0439 | -1.6937 | 120.0302 | -1.5564 | -1.6937 | -1.6937 | -0.21057 | -0.12817 | -0.11902 | -0.022888 | 0.027466 | -0.10986 | 0.004578 | 0.032043 | -0.068665 | -0.082398 | 0.16937 | 0.032043 | 0.032043 | 0 | 0 | 1.6068 | -120.2408 | -120.1355 | 1.7532 | 1.7303 | 1.6159 | 0.1236 | 0.009156 | 0.13733 | 121.7239 | 0.14649 | 0.096131 | 121.7377 | -0.009155 | 121.7697 | 1.5976 | -121.8063 | -120.2316 | 121.756 | 1.7029 | 7.4158 | 1.5152
1837.7344 | 121.9254 | -1.7441 | 120.1492 | 0.005951 | 6.9771 | 0.064619 | 0.065142 | 0.00185 | -0.0069683 | -0.0012988 | -0.00054933 | 0.0037278 | 0.016528 | 0.009786 | -0.0049175 | 0.024676 | -0.001583 | 5.7358 | 120.0165 | -1.6937 | 119.9982 | -1.593 | -1.7166 | -1.7441 | -0.23804 | -0.11444 | -0.12817 | -0.064087 | 0 | -0.16022 | -0.013733 | 0.050354 | -0.13275 | -0.15106 | 0.15106 | 0 | 0.027466 | -0.050354 | -0.022888 | 1.6159 | -120.2637 | -120.2133 | 1.7441 | 1.7303 | 1.5839 | 0.11444 | -0.032043 | 0.10071 | 121.6919 | 0.12817 | 0.064087 | 121.7102 | 0.013733 | 121.7606 | 1.6296 | -121.843 | -120.2774 | 121.7422 | 1.68 | 7.4799 | 1.506
1839.4062 | 121.9391 | -1.6846 | 120.2133 | -0.0016785 | 6.9778 | 0.066328 | 0.062792 | 0.00099557 | -0.0095319 | -0.0010852 | -0.0066527 | 0.0015914 | 0.015674 | 0.015981 | -0.0085491 | 0.026598 | -0.0013694 | 5.7587 | 120.0714 | -1.6388 | 120.0989 | -1.4694 | -1.5884 | -1.6022 | -0.21057 | -0.1236 | -0.10071 | -0.054932 | 0.027466 | -0.10071 | -0.004578 | 0.045776 | -0.14191 | -0.11444 | 0.21515 | 0.082397 | 0.09613 | 0.036621 | 0.050354 | 1.5839 | -120.3369 | -120.2682 | 1.712 | 1.68 | 1.5839 | 0.09613 | 0 | 0.16937 | 121.7377 | 0.12817 | 0.045776 | 121.7102 | -0.022888 | 121.756 | 1.561 | -121.8521 | -120.314 | 121.7834 | 1.6296 | 7.4432 | 1.474
1841.1406 | 121.8704 | -1.6846 | 120.2316 | 0.005951 | 6.9782 | 0.063978 | 0.06386 | 0.0031318 | -0.0071821 | -0.00087163 | -0.0066527 | 0.0039414 | 0.016101 | 0.0076498 | -0.0081219 | 0.025744 | 0.0029032 | 5.7678 | 120.0851 | -1.6251 | 120.1263 | -1.474 | -1.6022 | -1.6388 | -0.22888 | -0.09613 | -0.13733 | -0.091553 | -0.045776 | -0.19684 | -0.068665 | 0.059509 | -0.14648 | -0.10528 | 0.21057 | 0.045776 | 0.082397 | -0.013733 | 0.022888 | 1.5472 | -120.3278 | -120.3232 | 1.6388 | 1.6159 | 1.4877 | 0.068664 | -0.059509 | 0.15106 | 121.7514 | 0.091553 | 0.045776 | 121.7102 | 0.041199 | 121.7697 | 1.5884 | -121.8567 | -120.369 | 121.8109 | 1.593 | 7.4524 | 1.4557
1842.8906 | 121.962 | -1.5976 | 120.2362 | 0.01358 | 6.9784 | 0.065687 | 0.064288 | -0.00028623 | -0.0067547 | -0.0030078 | 0.0025025 | 0.002446 | 0.016101 | 0.019399 | -0.0059857 | 0.025316 | -0.0022238 | 5.7632 | 120.1263 | -1.5152 | 120.2499 | -1.3184 | -1.4786 | -1.4969 | -0.13733 | -0.11902 | -0.11444 | 0 | 0.045776 | -0.086975 | 0.032043 | 0.082397 | -0.10986 | 0.013733 | 0.27924 | 0.10071 | 0.11902 | 0.018311 | 0.036621 | 1.4832 | -120.3552 | -120.2362 | 1.6434 | 1.6296 | 1.5106 | 0.14648 | 0.027466 | 0.19684 | 121.7651 | 0.16022 | 0.11444 | 121.6415 | -0.004578 | 121.7239 | 1.4786 | -121.7514 | -120.3506 | 121.8475 | 1.5976 | 7.3608 | 1.4603
1844.5625 | 121.9986 | -1.5381 | 120.3003 | -0.0016785 | 6.9754 | 0.066328 | 0.058306 | -0.0030634 | -0.0069683 | -0.0032214 | -0.00054933 | 0.003514 | 0.016101 | 0.011281 | -0.0079083 | 0.024676 | -0.0054282 | 5.7678 | 120.1447 | -1.4923 | 120.282 | -1.268 | -1.387 | -1.4053 | -0.11444 | -0.14648 | -0.10071 | 0.009155 | 0.07782 | -0.036621 | 0.041199 | 0.045776 | -0.15564 | -0.018311 | 0.27008 | 0.13275 | 0.15106 | 0.086976 | 0.10529 | 1.4374 | -120.4468 | -120.2911 | 1.6159 | 1.5793 | 1.5015 | 0.14191 | 0.064087 | 0.2243 | 121.7743 | 0.17853 | 0.10986 | 121.637 | -0.045776 | 121.6827 | 1.3916 | -121.7926 | -120.401 | 121.8201 | 1.5472 | 7.3059 | 1.4236
1846.2969 | 121.9345 | -1.5244 | 120.3552 | -0.0016785 | 6.9767 | 0.06825 | 0.062579 | 0.0016364 | -0.0061139 | -0.0015124 | -0.0036011 | 0.0009506 | 0.016742 | 0.014486 | -0.0070539 | 0.024676 | -0.0037192 | 5.7587 | 120.2133 | -1.4465 | 120.314 | -1.2497 | -1.4053 | -1.4236 | -0.1831 | -0.13275 | -0.11902 | -0.059509 | 0.018311 | -0.1236 | -0.018311 | 0.07782 | -0.14191 | -0.041199 | 0.27466 | 0.10071 | 0.11902 | 0.022888 | 0.041199 | 1.4053 | -120.488 | -120.4147 | 1.5427 | 1.506 | 1.4008 | 0.10071 | -0.004577 | 0.19684 | 121.7606 | 0.13733 | 0.05951 | 121.6599 | -0.013732 | 121.7377 | 1.3916 | -121.8018 | -120.4742 | 121.8384 | 1.4648 | 7.283 | 1.3412
1847.9844 | 121.8384 | -1.4511 | 120.5063 | -0.0016785 | 6.9793 | 0.065473 | 0.064715 | 0.00099557 | -0.0097455 | -0.0015124 | -0.00054933 | 0.0047958 | 0.015674 | 0.011495 | -0.0066265 | 0.025957 | -0.0011558 | 5.7999 | 120.3506 | -1.387 | 120.3323 | -1.2817 | -1.4099 | -1.4236 | -0.32044 | -0.15106 | -0.14191 | -0.1831 | -0.10529 | -0.23804 | -0.09613 | 0.064087 | -0.15564 | -0.17395 | 0.16937 | 0.027466 | 0.041199 | -0.036621 | -0.022888 | 1.3092 | -120.6573 | -120.6894 | 1.3458 | 1.355 | 1.2131 | 0.045777 | -0.09613 | 0.10529 | 121.7194 | 0.036621 | -0.041198 | 121.7377 | -0.009155 | 121.8018 | 1.3 | -121.8933 | -120.6482 | 121.7834 | 1.268 | 7.251 | 1.1307
1849.7188 | 121.8796 | -1.5701 | 120.3827 | 0.01358 | 6.9771 | 0.063764 | 0.064074 | 0.00056817 | -0.0069683 | -0.001726 | -0.00054933 | 0.0047958 | 0.015246 | 0.0095724 | -0.011113 | 0.024462 | -0.0035056 | 5.7404 | 120.2316 | -1.5152 | 120.2179 | -1.4099 | -1.5015 | -1.506 | -0.29755 | -0.1831 | -0.16937 | -0.18768 | -0.054932 | -0.20142 | -0.082397 | 0.054931 | -0.15106 | -0.16479 | 0.16022 | 0.064087 | 0.068664 | 0.009156 | 0.013733 | 1.4008 | -120.5658 | -120.5704 | 1.5152 | 1.4877 | 1.3687 | 0.086976 | -0.032043 | 0.10529 | 121.7331 | 0.11444 | -0.01831 | 121.7468 | -0.013732 | 121.8018 | 1.387 | -121.8979 | -120.5521 | 121.788 | 1.3824 | 7.3105 | 1.2726
1851.4531 | 121.8567 | -1.6434 | 120.2637 | -0.016937 | 6.9778 | 0.062055 | 0.062365 | 0.00099557 | -0.0073957 | -0.0021532 | -0.00054933 | 0.0037278 | 0.016101 | 0.01299 | -0.011967 | 0.024462 | -0.005001 | 5.6854 | 120.1172 | -1.6113 | 120.0989 | -1.5152 | -1.6067 | -1.6205 | -0.29297 | -0.14648 | -0.15564 | -0.1831 | -0.068665 | -0.19684 | -0.10071 | 0.032044 | -0.14648 | -0.16479 | 0.12817 | 0.022889 | 0.036622 | -0.009155 | 0.004578 | 1.4877 | -120.4102 | -120.4468 | 1.5747 | 1.5427 | 1.4465 | 0.054932 | -0.041198 | 0.09613 | 121.7102 | 0.086975 | -0.027465 | 121.7285 | 0.009156 | 121.7606 | 1.4969 | -121.875 | -120.4193 | 121.7422 | 1.4603 | 7.3288 | 1.3504
1853.1875 | 121.8567 | -1.5701 | 120.3415 | -0.0016785 | 6.9782 | 0.060987 | 0.06386 | -0.00071343 | -0.0082501 | -0.003435 | -0.00054933 | 0.0033004 | 0.016101 | 0.0085044 | -0.011754 | 0.024248 | 0.00076681 | 5.7541 | 120.1904 | -1.5106 | 120.2042 | -1.3824 | -1.4786 | -1.5198 | -0.28381 | -0.12817 | -0.14648 | -0.17853 | -0.068665 | -0.14648 | -0.082397 | 0.059509 | -0.15106 | -0.13733 | 0.18768 | 0.050354 | 0.091552 | -0.009155 | 0.032043 | 1.4236 | -120.4697 | -120.52 | 1.5015 | 1.4877 | 1.4236 | 0.064087 | 0 | 0.12817 | 121.7148 | 0.077819 | -0.032044 | 121.7011 | 0.01831 | 121.7606 | 1.442 | -121.8521 | -120.488 | 121.7743 | 1.3916 | 7.3242 | 1.2863
1854.8594 | 121.8384 | -1.8814 | 120.0302 | -0.0016785 | 6.9799 | 0.065687 | 0.064288 | 0.00056817 | -0.0067547 | -0.0038622 | -0.00054933 | 0.0028732 | 0.015246 | 0.012563 | -0.0066265 | 0.025316 | -0.0035056 | 5.7678 | 119.957 | -1.7807 | 119.8929 | -1.7075 | -1.8311 | -1.8494 | -0.25635 | -0.11444 | -0.13733 | -0.15564 | -0.091553 | -0.23804 | -0.086975 | 0.10071 | -0.073242 | -0.13733 | 0.17395 | 0.032044 | 0.050354 | -0.068664 | -0.050354 | 1.7441 | -120.1447 | -120.1859 | 1.7899 | 1.7944 | 1.6434 | 0.050354 | -0.10071 | 0.073243 | 121.6736 | 0.045776 | -0.018311 | 121.7377 | 0.022888 | 121.8384 | 1.767 | -121.8109 | -120.1675 | 121.7743 | 1.7258 | 7.6492 | 1.6251
1856.5938 | 121.8475 | -1.7807 | 120.1492 | -0.009308 | 6.9791 | 0.066541 | 0.063433 | 0.006336 | -0.0061139 | -0.0032214 | -0.00054933 | 0.0022324 | 0.016742 | 0.013204 | -0.0064129 | 0.025744 | -0.0039328 | 5.7678 | 119.9707 | -1.7578 | 119.9478 | -1.6663 | -1.7715 | -1.7853 | -0.25635 | -0.16937 | -0.12817 | -0.17395 | -0.07782 | -0.23804 | -0.10071 | 0.022889 | -0.17853 | -0.20142 | 0.11444 | -0.004577 | 0.009156 | -0.027466 | -0.013733 | 1.6525 | -120.3186 | -120.3232 | 1.7029 | 1.68 | 1.5427 | 0.027466 | -0.10986 | 0.091552 | 121.7056 | 0.050354 | -0.045776 | 121.7285 | -0.041199 | 121.7514 | 1.6113 | -121.907 | -120.2774 | 121.7285 | 1.6068 | 7.5485 | 1.5244
1858.2812 | 121.9666 | -1.5793 | 120.2957 | -0.0016785 | 6.9789 | 0.064832 | 0.059161 | -0.0022088 | -0.0052595 | -0.00044443 | -0.00054933 | 0.0022324 | 0.014819 | 0.014699 | -0.0089765 | 0.024889 | -0.0020102 | 5.8182 | 120.1263 | -1.474 | 120.2637 | -1.3 | -1.442 | -1.4923 | -0.11902 | -0.17395 | -0.10529 | -0.068665 | 0.045776 | -0.041199 | 0.004578 | 0.10529 | -0.16937 | -0.032043 | 0.27924 | 0.086975 | 0.13733 | -0.018311 | 0.032043 | 1.474 | -120.4697 | -120.3644 | 1.6251 | 1.5839 | 1.5381 | 0.10986 | 0.064087 | 0.17395 | 121.7377 | 0.15106 | 0.036621 | 121.6003 | -0.068664 | 121.7056 | 1.4053 | -121.7697 | -120.401 | 121.843 | 1.5106 | 7.3975 | 1.4603
1860.0156 | 121.9711 | -1.4648 | 120.4102 | 0.005951 | 6.9789 | 0.064192 | 0.062579 | -0.0030634 | -0.0067547 | -0.00044443 | -0.0036011 | 0.000737 | 0.014605 | 0.01235 | -0.0059857 | 0.027239 | -0.0022238 | 5.7953 | 120.314 | -1.3824 | 120.369 | -1.2177 | -1.3184 | -1.3504 | -0.14191 | -0.14648 | -0.11444 | -0.054932 | 0.032043 | -0.068665 | -0.009155 | 0.082398 | -0.09613 | -0.041198 | 0.24719 | 0.11444 | 0.14648 | 0.032043 | 0.064087 | 1.3504 | -120.5566 | -120.4651 | 1.4969 | 1.4557 | 1.3962 | 0.10529 | 0.045776 | 0.1648 | 121.7514 | 0.14648 | 0.059509 | 121.6965 | -0.032043 | 121.7789 | 1.3184 | -121.7926 | -120.5246 | 121.8338 | 1.4099 | 7.2601 | 1.3229
1861.75 | 121.9849 | -1.4877 | 120.3644 | -0.009308 | 6.9761 | 0.063764 | 0.060656 | -0.00049983 | -0.0091047 | -0.0042896 | -0.00054933 | 0.0018052 | 0.014605 | 0.01235 | -0.0074811 | 0.027666 | -0.00072839 | 5.8868 | 120.2087 | -1.4282 | 120.3506 | -1.2131 | -1.3275 | -1.3733 | -0.059509 | -0.13733 | -0.10529 | 0.004578 | 0.082397 | -0.032043 | 0.022888 | 0.059509 | -0.15564 | -0.013733 | 0.27466 | 0.11444 | 0.16022 | 0.054932 | 0.10071 | 1.3824 | -120.5017 | -120.3598 | 1.5701 | 1.5106 | 1.4557 | 0.12817 | 0.073243 | 0.21515 | 121.7789 | 0.18768 | 0.10986 | 121.637 | -0.032043 | 121.6965 | 1.3504 | -121.7926 | -120.4697 | 121.8384 | 1.4923 | 7.3746 | 1.4282
1863.5 | 121.8613 | -1.3229 | 120.6116 | -0.009308 | 6.9808 | 0.065687 | 0.06386 | 0.00099557 | -0.0076093 | -0.0038622 | 0.0025025 | 0.0033004 | 0.012683 | 0.007009 | -0.0076947 | 0.024462 | -0.006069 | 5.8456 | 120.4926 | -1.2085 | 120.4239 | -1.1902 | -1.2955 | -1.2955 | -0.2243 | -0.10071 | -0.11902 | -0.15106 | -0.09613 | -0.21515 | -0.07782 | 0.11444 | -0.11902 | -0.18768 | 0.13275 | 0.027466 | 0.027466 | -0.086975 | -0.086975 | 1.2039 | -120.7123 | -120.7626 | 1.2268 | 1.2451 | 1.1078 | 0.041199 | -0.09613 | 0.01831 | 121.6324 | 0.022889 | -0.032043 | 121.701 | 0.018311 | 121.8155 | 1.2222 | -121.8201 | -120.7306 | 121.7468 | 1.1719 | 7.1686 | 1.0986
1865.1875 | 121.994 | -1.799 | 120.0485 | 0.01358 | 6.978 | 0.066755 | 0.06386 | -0.0013544 | -0.0054731 | -0.00065803 | 0.0055543 | 0.0022324 | 0.014178 | 0.009786 | -0.0044903 | 0.028094 | -0.003292 | 5.7312 | 119.8334 | -1.7944 | 120.0256 | -1.5518 | -1.712 | -1.6846 | 0.004578 | -0.13275 | -0.10986 | 0.009155 | 0.054932 | -0.050354 | 0.036621 | 0.004577 | -0.21515 | -0.022888 | 0.24719 | 0.11444 | 0.086975 | 0.10986 | 0.082398 | 1.6891 | -120.1813 | -120.0394 | 1.8539 | 1.8356 | 1.7487 | 0.14648 | 0.059509 | 0.24262 | 121.8201 | 0.16479 | 0.11902 | 121.6278 | -0.022888 | 121.6324 | 1.6663 | -121.843 | -120.1584 | 121.8246 | 1.8082 | 7.5302 | 1.8036
1866.9375 | 121.9116 | -1.8723 | 120.0073 | -0.0016785 | 6.9791 | 0.064619 | 0.063433 | 0.00099557 | -0.0073957 | -0.0012988 | -0.0036011 | 0.0037278 | 0.014178 | 0.0067954 | -0.0076947 | 0.026385 | -0.0058554 | 5.722 | 119.9341 | -1.7761 | 119.9753 | -1.6205 | -1.7395 | -1.7715 | -0.10071 | -0.11902 | -0.11444 | -0.064087 | 0.009155 | -0.11902 | -0.009155 | 0.09613 | -0.073242 | -0.032043 | 0.25177 | 0.10071 | 0.13275 | 0.004578 | 0.036621 | 1.7578 | -120.1263 | -120.0714 | 1.8814 | 1.8631 | 1.7532 | 0.10529 | -0.004578 | 0.15564 | 121.7514 | 0.1236 | 0.050354 | 121.7102 | -0.004578 | 121.8063 | 1.7532 | -121.7834 | -120.1218 | 121.8475 | 1.8082 | 7.5943 | 1.7715
1868.625 | 121.8658 | -1.7761 | 120.163 | -0.0016785 | 6.9797 | 0.065473 | 0.063433 | 0.0037726 | -0.0052595 | -0.0012988 | -0.0036011 | 0.0020188 | 0.016955 | 0.020254 | -0.0072675 | 0.027239 | -0.00051479 | 5.6442 | 120.0165 | -1.7258 | 119.9615 | -1.6434 | -1.767 | -1.7761 | -0.20599 | -0.086975 | -0.11902 | -0.13275 | -0.082397 | -0.16022 | -0.064087 | 0.050354 | -0.14648 | -0.20142 | 0.13275 | 0 | 0.009155 | -0.050354 | -0.041199 | 1.6571 | -120.2499 | -120.2957 | 1.6937 | 1.712 | 1.6159 | 0.054932 | -0.041198 | 0.082397 | 121.6873 | 0.036622 | -0.013732 | 121.7422 | 0.032044 | 121.7926 | 1.6891 | -121.8887 | -120.282 | 121.7377 | 1.6434 | 7.4203 | 1.5701
1870.3594 | 121.8521 | -1.6479 | 120.2682 | -0.009308 | 6.9806 | 0.066541 | 0.064288 | 0.0027044 | -0.0088911 | -0.001726 | -0.00054933 | 0.0026596 | 0.014819 | 0.0099996 | -0.0079083 | 0.02553 | -0.0030784 | 5.69 | 120.1355 | -1.6067 | 120.1218 | -1.5015 | -1.6296 | -1.6434 | -0.19684 | -0.11444 | -0.1236 | -0.14191 | -0.10071 | -0.17395 | -0.086975 | 0.041199 | -0.13275 | -0.14648 | 0.14648 | 0.004577 | 0.01831 | -0.036622 | -0.022889 | 1.5244 | -120.3827 | -120.4102 | 1.5472 | 1.561 | 1.474 | 0.036621 | -0.050354 | 0.10528 | 121.7285 | 0.022888 | -0.018311 | 121.7422 | 0.009155 | 121.7834 | 1.5335 | -121.875 | -120.3918 | 121.7697 | 1.506 | 7.338 | 1.4511
1872.0312 | 121.9803 | -1.8677 | 119.989 | -0.009308 | 6.9769 | 0.066541 | 0.063006 | -0.00028623 | -0.0088911 | -0.0025806 | -0.00054933 | 0.0018052 | 0.014392 | 0.015767 | -0.0053449 | 0.028307 | -0.0011558 | 5.69 | 119.9295 | -1.767 | 119.9615 | -1.6342 | -1.767 | -1.799 | -0.032043 | -0.16479 | -0.086975 | -0.004578 | 0.054932 | -0.009155 | 0.059509 | 0.10071 | -0.05951 | -0.027466 | 0.23346 | 0.068665 | 0.10071 | -0.032043 | 0 | 1.7807 | -120.1538 | -119.9936 | 1.9226 | 1.9272 | 1.8585 | 0.14648 | 0.07782 | 0.13275 | 121.7285 | 0.14191 | 0.082397 | 121.6965 | -0.07782 | 121.7972 | 1.7029 | -121.756 | -120.076 | 121.8292 | 1.8631 | 7.5577 | 1.8356
1873.7656 | 121.9345 | -1.8585 | 120.0256 | 0.01358 | 6.9774 | 0.065473 | 0.061297 | 0.0016364 | -0.0073957 | -0.0010852 | -0.00054933 | 0.0015914 | 0.01546 | 0.021749 | -0.0064129 | 0.02553 | -0.00072839 | 5.6488 | 119.8608 | -1.8036 | 119.9478 | -1.5839 | -1.7578 | -1.7624 | -0.045776 | -0.14191 | -0.091553 | -0.059509 | 0.013733 | -0.045776 | 0.009155 | 0.054932 | -0.16479 | -0.07782 | 0.27466 | 0.096131 | 0.10071 | 0.041199 | 0.045777 | 1.767 | -120.1675 | -120.0851 | 1.8723 | 1.8677 | 1.8127 | 0.10071 | 0.045777 | 0.21973 | 121.7514 | 0.10529 | 0.032044 | 121.6644 | -0.050354 | 121.7194 | 1.7166 | -121.8292 | -120.1172 | 121.8063 | 1.799 | 7.5073 | 1.8127
1875.5 | 121.9437 | -1.886 | 119.9661 | 0.01358 | 6.9774 | 0.065473 | 0.062792 | 0.00014097 | -0.0071821 | -0.0021532 | 0.0025025 | 0.0003098 | 0.013537 | 0.014699 | -0.010472 | 0.026385 | -0.0037192 | 5.6213 | 119.8288 | -1.8219 | 119.9478 | -1.6251 | -1.7395 | -1.7807 | -0.073242 | -0.13275 | -0.091553 | -0.064087 | 0.009155 | -0.036621 | 0.004578 | 0.064087 | -0.13733 | -0.01831 | 0.26092 | 0.10528 | 0.14648 | 0.041198 | 0.082397 | 1.7944 | -120.0989 | -120.0302 | 1.8951 | 1.8906 | 1.8494 | 0.096131 | 0.054932 | 0.19684 | 121.7697 | 0.10071 | 0.027466 | 121.6507 | -0.041198 | 121.7148 | 1.7532 | -121.788 | -120.0577 | 121.8338 | 1.8219 | 7.5073 | 1.8127
1877.1719 | 121.9986 | -1.8082 | 119.9982 | -0.0016785 | 6.9799 | 0.065901 | 0.062792 | -0.0039178 | -0.0054731 | -0.0027942 | 0.0025025 | 0.0005234 | 0.017596 | 0.012563 | -0.0051313 | 0.026812 | -0.003292 | 5.6213 | 119.8563 | -1.7578 | 120.0302 | -1.5381 | -1.6891 | -1.6937 | 0.004578 | -0.14648 | -0.082397 | -0.009155 | 0.07782 | 0.004578 | 0.050354 | 0.050355 | -0.14191 | 0.032043 | 0.27008 | 0.11444 | 0.11902 | 0.064086 | 0.068664 | 1.7258 | -120.1447 | -120.0073 | 1.886 | 1.8585 | 1.8127 | 0.13275 | 0.086975 | 0.21973 | 121.788 | 0.16022 | 0.073242 | 121.6141 | -0.064087 | 121.6644 | 1.6617 | -121.756 | -120.0806 | 121.8384 | 1.799 | 7.4295 | 1.8127
1878.9219 | 121.9894 | -1.8448 | 120.0119 | -0.0016785 | 6.9756 | 0.064405 | 0.064074 | 0.0014228 | -0.0061139 | -0.00023063 | -0.00054933 | 0.0020188 | 0.015674 | 0.015767 | -0.0094037 | 0.026171 | -0.0020102 | 5.6808 | 119.8151 | -1.7944 | 120.0256 | -1.561 | -1.68 | -1.7395 | 0.009155 | -0.15564 | -0.09613 | -0.036621 | 0.091553 | 0.018311 | 0.036621 | 0.050354 | -0.19684 | 0.013733 | 0.28381 | 0.10529 | 0.1648 | 0.054932 | 0.11444 | 1.7487 | -120.1675 | -120.0485 | 1.9363 | 1.8814 | 1.8631 | 0.13275 | 0.11444 | 0.23346 | 121.8201 | 0.18768 | 0.059509 | 121.6095 | -0.05951 | 121.6599 | 1.6891 | -121.8063 | -120.108 | 121.8704 | 1.8082 | 7.5256 | 1.8539
1880.5938 | 121.8384 | -1.9272 | 119.9936 | -0.009308 | 6.9782 | 0.065901 | 0.063006 | -0.00049983 | -0.0076093 | -0.001726 | -0.00054933 | 0.004155 | 0.016314 | 0.013845 | -0.0091901 | 0.025103 | -0.003292 | 5.6351 | 119.902 | -1.8356 | 119.7922 | -1.8082 | -1.9272 | -1.9501 | -0.18768 | -0.1236 | -0.13733 | -0.14648 | -0.091553 | -0.16022 | -0.068665 | 0.091553 | -0.091552 | -0.20142 | 0.11902 | -0.022888 | 0 | -0.11444 | -0.091553 | 1.7899 | -120.1172 | -120.1401 | 1.8356 | 1.8585 | 1.767 | 0.068664 | -0.022888 | 0.027465 | 121.6278 | 0.045776 | -0.009155 | 121.7377 | 0.013733 | 121.8292 | 1.8036 | -121.8292 | -120.1309 | 121.7194 | 1.7807 | 7.5623 | 1.7395
1882.3281 | 121.907 | -1.7899 | 120.1309 | 0.005951 | 6.9767 | 0.063337 | 0.064074 | 0.00078177 | -0.0073957 | -0.002367 | -0.00054933 | 0.0028732 | 0.015887 | 0.0076498 | -0.0094037 | 0.025316 | -0.002651 | 5.69 | 120.0256 | -1.7166 | 119.989 | -1.6113 | -1.6937 | -1.7578 | -0.14191 | -0.11444 | -0.12817 | -0.1236 | -0.022888 | -0.10529 | -0.036621 | 0.073242 | -0.10529 | -0.14191 | 0.17853 | 0.032044 | 0.09613 | -0.041198 | 0.022888 | 1.6617 | -120.2454 | -120.2545 | 1.767 | 1.7532 | 1.6846 | 0.091553 | 0.022888 | 0.10529 | 121.7056 | 0.10529 | 0.004578 | 121.7422 | 0.013733 | 121.8155 | 1.6754 | -121.8475 | -120.2591 | 121.7789 | 1.6663 | 7.4799 | 1.6479
1884.0625 | 121.8338 | -1.8585 | 120.0851 | -0.016937 | 6.9776 | 0.063764 | 0.062579 | 0.0050544 | -0.0099591 | -0.0015124 | -0.0036011 | 0.0026596 | 0.014178 | 0.0040182 | -0.0091901 | 0.025103 | -0.002651 | 5.6442 | 119.9707 | -1.7715 | 119.9203 | -1.6891 | -1.8219 | -1.8356 | -0.20599 | -0.15106 | -0.14191 | -0.21515 | -0.10071 | -0.16022 | -0.091553 | 0.086976 | -0.11444 | -0.16479 | 0.16937 | 0.022889 | 0.036622 | -0.064087 | -0.050354 | 1.7166 | -120.2362 | -120.3003 | 1.7578 | 1.767 | 1.6983 | 0.050354 | -0.01831 | 0.082397 | 121.6919 | 0.041199 | -0.073242 | 121.7422 | -0.009155 | 121.8292 | 1.7075 | -121.8567 | -120.2271 | 121.7789 | 1.6434 | 7.5027 | 1.6525
1885.8125 | 121.9894 | -1.7395 | 120.1218 | 0.005951 | 6.978 | 0.066114 | 0.060229 | 0.0024908 | -0.0080365 | 0.00083737 | -0.00054933 | 0.000737 | 0.014605 | 0.010854 | -0.0059857 | 0.027666 | -0.0045736 | 5.6808 | 119.9615 | -1.6754 | 120.0989 | -1.4694 | -1.6342 | -1.6342 | -0.009155 | -0.19226 | -0.10529 | -0.07782 | 0.068665 | 0.004578 | 0.041199 | 0.064087 | -0.16022 | -0.022888 | 0.27008 | 0.10529 | 0.10529 | 0.041199 | 0.041199 | 1.6342 | -120.314 | -120.1996 | 1.8082 | 1.7807 | 1.7441 | 0.14649 | 0.10986 | 0.20599 | 121.7743 | 0.17395 | 0.027466 | 121.637 | -0.086975 | 121.701 | 1.5472 | -121.7972 | -120.2271 | 121.8384 | 1.6617 | 7.4203 | 1.7303
1887.5625 | 121.9666 | -1.799 | 120.0668 | -0.0016785 | 6.978 | 0.063337 | 0.061297 | 0.00099557 | -0.0080365 | 0.00019657 | -0.00054933 | 0.0009506 | 0.015033 | 0.016622 | -0.010045 | 0.02553 | -0.00030119 | 5.6351 | 119.9249 | -1.7212 | 119.9753 | -1.5839 | -1.7029 | -1.7075 | -0.054932 | -0.2243 | -0.09613 | -0.09613 | 0.054932 | -0.004578 | 0.027466 | 0.07782 | -0.14191 | -0.091552 | 0.21515 | 0.091553 | 0.09613 | 0.013733 | 0.01831 | 1.7029 | -120.2911 | -120.163 | 1.8539 | 1.8265 | 1.7944 | 0.1236 | 0.091552 | 0.13733 | 121.6965 | 0.15106 | 0 | 121.6461 | -0.12817 | 121.7239 | 1.5747 | -121.788 | -120.163 | 121.7743 | 1.7029 | 7.4341 | 1.7441
1889.25 | 121.9757 | -1.7029 | 120.0989 | -0.009308 | 6.9793 | 0.063123 | 0.062365 | 0.00014097 | -0.0063275 | -0.0047168 | -0.00054933 | 0.0003098 | 0.012256 | 0.010427 | -0.010472 | 0.025957 | 0.00033961 | 5.7404 | 119.9295 | -1.6571 | 120.1218 | -1.4236 | -1.5747 | -1.6067 | -0.013733 | -0.19684 | -0.086975 | -0.068665 | 0.10071 | 0.032043 | 0.022888 | 0.045777 | -0.16937 | 0.022888 | 0.27924 | 0.096131 | 0.12817 | 0.050354 | 0.082397 | 1.6159 | -120.2957 | -120.1675 | 1.8036 | 1.7258 | 1.7349 | 0.10986 | 0.11902 | 0.23346 | 121.7789 | 0.18768 | 0.01831 | 121.5866 | -0.10986 | 121.6324 | 1.506 | -121.756 | -120.1859 | 121.8246 | 1.6342 | 7.4432 | 1.6891
1890.9844 | 121.9849 | -1.5289 | 120.2866 | 0.005951 | 6.9761 | 0.063551 | 0.063006 | 0.0024908 | -0.0071821 | -0.0027942 | -0.00054933 | 0.0015914 | 0.014605 | 0.016622 | -0.0079083 | 0.024035 | -0.005001 | 5.7404 | 120.1401 | -1.5106 | 120.2866 | -1.2817 | -1.4008 | -1.4191 | -0.032043 | -0.20142 | -0.091553 | -0.07782 | 0.07782 | 0.004578 | 0.022888 | 0.018311 | -0.14648 | 0 | 0.24719 | 0.10986 | 0.12817 | 0.091553 | 0.10986 | 1.4374 | -120.488 | -120.3644 | 1.6068 | 1.5518 | 1.5335 | 0.11444 | 0.096131 | 0.22888 | 121.7972 | 0.16937 | 0.013733 | 121.6507 | -0.10986 | 121.669 | 1.3275 | -121.7972 | -120.3781 | 121.8155 | 1.4511 | 7.2693 | 1.4969
1892.7344 | 121.9025 | -1.5152 | 120.3644 | -0.009308 | 6.981 | 0.063123 | 0.063006 | 0.0024908 | -0.0078229 | -0.0010852 | -0.0066527 | 0.003514 | 0.015887 | 0.01235 | -0.0055585 | 0.024889 | -8.7586e-05 | 5.7449 | 120.2637 | -1.4557 | 120.2225 | -1.3687 | -1.4832 | -1.4832 | -0.16479 | -0.15106 | -0.1236 | -0.15106 | -0.045776 | -0.13733 | -0.054932 | 0.05951 | -0.10071 | -0.14191 | 0.14648 | 0.032044 | 0.032044 | -0.027466 | -0.027466 | 1.3916 | -120.5154 | -120.5154 | 1.4694 | 1.4603 | 1.3779 | 0.068664 | -0.013733 | 0.086975 | 121.6782 | 0.07782 | -0.027466 | 121.7194 | -0.027466 | 121.7789 | 1.3641 | -121.8201 | -120.488 | 121.7377 | 1.3641 | 7.2601 | 1.3504
1894.4219 | 121.8979 | -1.3962 | 120.488 | -0.009308 | 6.9784 | 0.065473 | 0.064501 | 0.0014228 | -0.0071821 | -0.0025806 | -0.00054933 | 0.0009506 | 0.016528 | 0.0095724 | -0.0068403 | 0.024035 | -0.0017966 | 5.7632 | 120.3644 | -1.355 | 120.3918 | -1.1856 | -1.3046 | -1.3367 | -0.13275 | -0.18768 | -0.10986 | -0.14191 | 0 | -0.10529 | -0.032043 | 0.041199 | -0.1236 | -0.09613 | 0.21057 | 0.059509 | 0.091553 | 0.01831 | 0.050354 | 1.2863 | -120.6757 | -120.6299 | 1.3962 | 1.3641 | 1.2909 | 0.07782 | 0.004577 | 0.16937 | 121.7468 | 0.10986 | -0.032044 | 121.7194 | -0.07782 | 121.7606 | 1.2085 | -121.843 | -120.5978 | 121.788 | 1.2543 | 7.1594 | 1.2634
1896.1719 | 121.9391 | -1.474 | 120.4056 | 0.005951 | 6.9767 | 0.066328 | 0.061724 | 0.0033454 | -0.0067547 | -0.0027942 | -0.0036011 | 0.0009506 | 0.012683 | 0.015767 | -0.0091901 | 0.029375 | -0.00051479 | 5.6992 | 120.282 | -1.4236 | 120.3278 | -1.236 | -1.3596 | -1.3824 | -0.17853 | -0.19684 | -0.11902 | -0.11444 | 0.027466 | -0.07782 | -0.013733 | 0.050354 | -0.1236 | -0.07782 | 0.23804 | 0.091553 | 0.11444 | 0.041199 | 0.064087 | 1.355 | -120.6024 | -120.52 | 1.5015 | 1.4603 | 1.3962 | 0.10529 | 0.041199 | 0.18768 | 121.7514 | 0.14649 | 0.004578 | 121.7056 | -0.077819 | 121.756 | 1.2772 | -121.8292 | -120.5246 | 121.8018 | 1.3596 | 7.1732 | 1.2955
1897.9062 | 121.9666 | -1.4191 | 120.4697 | 0.02121 | 6.9763 | 0.064405 | 0.062792 | 0.0029182 | -0.0052595 | 0.00083737 | 0.0025025 | 0.004155 | 0.016528 | 0.011709 | -0.0059857 | 0.027025 | -0.0047874 | 5.7541 | 120.2957 | -1.3733 | 120.4147 | -1.1627 | -1.3138 | -1.3367 | -0.050354 | -0.19226 | -0.10986 | -0.064087 | 0.050354 | -0.045776 | 0.018311 | 0.045776 | -0.17395 | -0.054932 | 0.25635 | 0.082397 | 0.10529 | 0.036621 | 0.059509 | 1.3092 | -120.6619 | -120.5338 | 1.4694 | 1.4374 | 1.3733 | 0.12817 | 0.064087 | 0.21057 | 121.788 | 0.16022 | 0.045776 | 121.669 | -0.082398 | 121.7148 | 1.2268 | -121.843 | -120.5795 | 121.8338 | 1.355 | 7.1732 | 1.3687
1899.6094 | 121.9849 | -1.4511 | 120.3873 | -0.0016785 | 6.9774 | 0.065687 | 0.063647 | 0.0016364 | -0.0080365 | -0.00023063 | 0.0025025 | 0.0011642 | 0.017169 | 0.014913 | -0.0061993 | 0.02788 | -0.0024374 | 5.809 | 120.2545 | -1.4099 | 120.369 | -1.1902 | -1.3596 | -1.3779 | -0.064087 | -0.18768 | -0.11902 | -0.050354 | 0.068665 | -0.050354 | 0.027466 | 0.041199 | -0.13275 | -0.01831 | 0.26093 | 0.073242 | 0.091553 | 0.032043 | 0.050354 | 1.3321 | -120.575 | -120.4376 | 1.5198 | 1.4786 | 1.4008 | 0.14649 | 0.068665 | 0.21973 | 121.7789 | 0.18768 | 0.068665 | 121.6644 | -0.068664 | 121.7056 | 1.2634 | -121.7972 | -120.5063 | 121.8201 | 1.4008 | 7.2601 | 1.387
1901.3594 | 121.9254 | -1.4236 | 120.4605 | -0.0016785 | 6.9808 | 0.065687 | 0.062579 | 0.00078177 | -0.0069683 | -0.0019396 | -0.00054933 | 0.0013778 | 0.01311 | 0.013845 | -0.0074811 | 0.024889 | -0.0037192 | 5.7037 | 120.3094 | -1.3733 | 120.3369 | -1.2314 | -1.3321 | -1.3596 | -0.16479 | -0.14648 | -0.11444 | -0.11444 | 0.018311 | -0.10071 | -0.022888 | 0.050354 | -0.15106 | -0.1236 | 0.19226 | 0.064087 | 0.091553 | 0.013733 | 0.041199 | 1.3092 | -120.607 | -120.575 | 1.442 | 1.4008 | 1.3229 | 0.091553 | 0.013733 | 0.14191 | 121.7102 | 0.13275 | 0 | 121.6827 | -0.032043 | 121.7331 | 1.2772 | -121.8338 | -120.575 | 121.7606 | 1.3092 | 7.1274 | 1.2589
1903.0469 | 121.8933 | -1.5289 | 120.3918 | -0.0016785 | 6.9756 | 0.066541 | 0.065356 | 0.003559 | -0.0082501 | -0.002367 | 0.0025025 | 0.005223 | 0.018023 | 0.013631 | -0.0087629 | 0.02553 | -0.0047874 | 5.7587 | 120.2637 | -1.4603 | 120.2866 | -1.2955 | -1.4145 | -1.4603 | -0.15564 | -0.10986 | -0.10071 | -0.068665 | -0.027466 | -0.12817 | -0.027466 | 0.068665 | -0.12817 | -0.10529 | 0.23346 | 0.068665 | 0.11444 | 0 | 0.045776 | 1.4282 | -120.5017 | -120.4605 | 1.5015 | 1.5015 | 1.4008 | 0.073242 | -0.027466 | 0.1648 | 121.7468 | 0.073242 | 0.032043 | 121.7239 | -0.009155 | 121.7926 | 1.4191 | -121.8521 | -120.4926 | 121.8155 | 1.4603 | 7.2876 | 1.3733
1904.7812 | 121.8292 | -1.4694 | 120.4559 | 0.005951 | 6.981 | 0.062269 | 0.06621 | 0.0039862 | -0.0059003 | -0.00065803 | -0.0066527 | 0.003514 | 0.014178 | 0.0093588 | -0.0070539 | 0.025103 | -0.0011558 | 5.69 | 120.3049 | -1.4236 | 120.2866 | -1.3458 | -1.442 | -1.4511 | -0.27008 | -0.09613 | -0.13733 | -0.14191 | -0.10071 | -0.2243 | -0.086975 | 0.045776 | -0.15106 | -0.16937 | 0.1236 | 0.01831 | 0.027465 | -0.027466 | -0.018311 | 1.3321 | -120.5521 | -120.5978 | 1.3687 | 1.3824 | 1.2451 | 0.050354 | -0.086975 | 0.07782 | 121.7102 | 0.036621 | -0.004578 | 121.7285 | 0.041199 | 121.7743 | 1.3733 | -121.8796 | -120.5933 | 121.756 | 1.3275 | 7.1594 | 1.1993
1906.4531 | 121.9711 | -1.4145 | 120.4559 | -0.0016785 | 6.978 | 0.064192 | 0.063006 | 0.0020636 | -0.0088911 | -0.0027942 | -0.0036011 | 0.0028732 | 0.015674 | 0.0072226 | -0.0047039 | 0.026385 | -0.0037192 | 5.7175 | 120.3186 | -1.3824 | 120.3461 | -1.2268 | -1.3824 | -1.3779 | -0.16937 | -0.14648 | -0.11902 | -0.013733 | 0.022888 | -0.086975 | 0.032043 | 0.032044 | -0.13733 | -0.10986 | 0.18768 | 0.036621 | 0.032044 | 0.004577 | 0 | 1.2955 | -120.6024 | -120.4697 | 1.4374 | 1.4465 | 1.3275 | 0.15106 | 0.032044 | 0.15564 | 121.7285 | 0.14191 | 0.10529 | 121.701 | -0.027465 | 121.7331 | 1.268 | -121.8384 | -120.575 | 121.7606 | 1.4008 | 7.132 | 1.2451
1908.1875 | 121.9528 | -1.3412 | 120.5292 | -0.009308 | 6.9784 | 0.063978 | 0.062579 | -0.00028623 | -0.0067547 | -0.0012988 | -0.0036011 | -0.0003312 | 0.014392 | 0.013845 | -0.0081219 | 0.027666 | -8.7586e-05 | 5.7495 | 120.3873 | -1.2726 | 120.4468 | -1.1078 | -1.2177 | -1.2451 | -0.16022 | -0.12817 | -0.091553 | -0.045776 | 0.036621 | -0.064087 | 0.009155 | 0.068665 | -0.14191 | -0.082398 | 0.23346 | 0.096131 | 0.1236 | 0.027466 | 0.054932 | 1.2497 | -120.6573 | -120.575 | 1.3779 | 1.3504 | 1.2772 | 0.10071 | 0.027466 | 0.1648 | 121.7194 | 0.12817 | 0.045777 | 121.6599 | -0.036621 | 121.7285 | 1.2131 | -121.8018 | -120.6207 | 121.788 | 1.2955 | 7.0908 | 1.181
1909.9219 | 121.9666 | -1.2772 | 120.5475 | -0.016937 | 6.9795 | 0.066328 | 0.062365 | 0.00014097 | -0.0061139 | -1.7026e-05 | 0.0025025 | 0.0030868 | 0.01781 | 0.016408 | -0.0051313 | 0.02788 | -8.7586e-05 | 5.7083 | 120.4468 | -1.236 | 120.4742 | -1.1032 | -1.236 | -1.2497 | -0.1236 | -0.11902 | -0.10071 | -0.004578 | 0.036621 | -0.059509 | 0.036621 | 0.041199 | -0.10071 | -0.073242 | 0.17395 | 0.027466 | 0.041199 | -0.013733 | 0 | 1.1765 | -120.6665 | -120.5521 | 1.3138 | 1.3138 | 1.2177 | 0.13733 | 0.041199 | 0.13275 | 121.7102 | 0.13733 | 0.09613 | 121.6827 | -0.018311 | 121.7239 | 1.1581 | -121.7834 | -120.6482 | 121.7514 | 1.2726 | 6.9855 | 1.1536
1911.5938 | 121.9849 | -1.3092 | 120.5841 | -0.0016785 | 6.9776 | 0.063764 | 0.064288 | 0.0022772 | -0.0091047 | -0.00087163 | -0.00054933 | 0.0022324 | 0.015033 | 0.018545 | -0.0070539 | 0.026598 | 0.00012601 | 5.6992 | 120.4285 | -1.236 | 120.5292 | -1.0483 | -1.1307 | -1.1581 | -0.10529 | -0.1236 | -0.10529 | -0.009155 | 0.073242 | -0.018311 | 0.045776 | 0.073242 | -0.15564 | -0.054931 | 0.26093 | 0.15106 | 0.17853 | 0.07782 | 0.10529 | 1.2039 | -120.7077 | -120.5933 | 1.3824 | 1.355 | 1.2909 | 0.15106 | 0.086975 | 0.18768 | 121.7651 | 0.17853 | 0.096131 | 121.6644 | -0.01831 | 121.7377 | 1.1856 | -121.8201 | -120.6894 | 121.8384 | 1.3 | 7.0084 | 1.2039
1913.3281 | 121.8521 | -1.3367 | 120.5841 | -0.0016785 | 6.9797 | 0.061628 | 0.064715 | -0.0028498 | -0.0082501 | -0.001726 | 0.0025025 | 0.0026596 | 0.016101 | 0.014913 | -0.010472 | 0.024889 | -0.0013694 | 5.7587 | 120.4239 | -1.2497 | 120.4605 | -1.1353 | -1.2222 | -1.268 | -0.21057 | -0.091553 | -0.11902 | -0.12817 | -0.045776 | -0.12817 | -0.07782 | 0.086975 | -0.16022 | -0.1236 | 0.20142 | 0.068665 | 0.11444 | -0.01831 | 0.027466 | 1.2177 | -120.6757 | -120.7123 | 1.2909 | 1.2589 | 1.2085 | 0.041199 | -0.009155 | 0.11444 | 121.7102 | 0.073243 | -0.009155 | 121.6736 | 0.027466 | 121.7606 | 1.2451 | -121.8338 | -120.7031 | 121.7972 | 1.2085 | 7.0953 | 1.1261
1915.0625 | 121.9299 | -1.268 | 120.6162 | 0.005951 | 6.9767 | 0.065473 | 0.061724 | 0.0050544 | -0.0095319 | -0.0019396 | -0.0066527 | 0.0013778 | 0.011615 | 0.017476 | -0.0076947 | 0.025103 | -0.0041464 | 5.6488 | 120.4239 | -1.2405 | 120.4971 | -1.0803 | -1.1948 | -1.2314 | -0.14191 | -0.13275 | -0.09613 | -0.082397 | 0.013733 | -0.064087 | 0.009155 | 0.027465 | -0.19226 | -0.11902 | 0.18768 | 0.036621 | 0.073242 | 0.009156 | 0.045777 | 1.1719 | -120.7489 | -120.6985 | 1.2817 | 1.2772 | 1.2039 | 0.10528 | 0.032043 | 0.16022 | 121.7377 | 0.10986 | 0.013733 | 121.6644 | -0.036621 | 121.6919 | 1.1353 | -121.8567 | -120.7123 | 121.7651 | 1.1856 | 6.9168 | 1.1261
1916.7969 | 121.9803 | -1.2634 | 120.5612 | 0.005951 | 6.978 | 0.06526 | 0.060442 | -7.2628e-05 | -0.0065411 | -0.003435 | 0.0025025 | 0.0018052 | 0.014178 | 0.010854 | -0.0047039 | 0.025316 | -0.0041464 | 5.7037 | 120.4239 | -1.2268 | 120.5429 | -1.0391 | -1.181 | -1.2039 | -0.064087 | -0.13275 | -0.07782 | 0.027466 | 0.064087 | -0.009155 | 0.059509 | 0.036621 | -0.13733 | -0.01831 | 0.2243 | 0.05951 | 0.082398 | 0.022889 | 0.045777 | 1.1856 | -120.694 | -120.5338 | 1.3275 | 1.3229 | 1.2543 | 0.13733 | 0.068665 | 0.18768 | 121.7697 | 0.14191 | 0.10529 | 121.6507 | -0.054931 | 121.6873 | 1.1307 | -121.788 | -120.639 | 121.8063 | 1.2909 | 6.9672 | 1.1993
1918.4844 | 121.8704 | -2.2659 | 119.5862 | -0.024567 | 6.9759 | 0.064192 | 0.061724 | 0.00099557 | -0.0069683 | -0.0015124 | -0.0036011 | 0.000737 | 0.012683 | 0.014059 | -0.010686 | 0.02553 | -0.00671 | 4.9347 | 118.8309 | -2.7786 | 119.5633 | -2.0416 | -2.504 | -2.4307 | -0.10529 | -0.10529 | -0.09613 | -0.054932 | 0.041199 | -0.027466 | 0.013733 | -0.51269 | -0.75531 | -0.022889 | 0.2243 | -0.16479 | -0.23804 | 0.3479 | 0.27466 | 2.1698 | -119.6915 | -119.6411 | 2.3071 | 2.2797 | 2.2385 | 0.10986 | 0.068664 | 0.737 | 122.3419 | 0.13733 | 0.041198 | 121.6095 | -0.009156 | 121.0968 | 2.1606 | -122.3648 | -119.6823 | 121.8292 | 2.211 | 7.2006 | 2.1606
1920.2344 | 119.7235 | -72.5052 | 46.8842 | 0.005951 | 6.9761 | 0.064192 | 0.064288 | 0.00078177 | -0.0078229 | -0.0038622 | -0.00054933 | 0.0020188 | 0.016101 | 0.014272 | -0.0072675 | 0.027453 | -0.0047874 | -6.9855 | 48.3353 | -71.1273 | 47.9324 | -70.7703 | -72.3587 | -72.3862 | 0 | -0.068665 | -0.036621 | 0.064087 | 0.1236 | 0.041199 | 0.11902 | 1.3779 | 1.4511 | 1.0483 | 1.7349 | 0.11902 | 0.14648 | -1.2588 | -1.2314 | 72.4686 | -46.9528 | -46.8201 | 72.6288 | 72.6242 | 72.5464 | 0.15564 | 0.07782 | 0.35706 | 119.0598 | 0.16022 | 0.10071 | 119.4626 | -0.032044 | 120.8405 | 72.4365 | -118.0115 | -46.9208 | 120.4376 | 72.5693 | 65.5197 | 72.5052
1921.9844 | 121.5546 | -0.37994 | 121.257 | -0.016937 | 6.9803 | 0.062483 | 0.061724 | 0.0016364 | -0.0059003 | -0.0015124 | 0.0025025 | 0.0037278 | 0.01546 | 0.016195 | -0.0055585 | 0.025957 | -0.0024374 | 5.8365 | 121.1151 | -0.3067 | 121.1563 | -0.14191 | -0.26093 | -0.2655 | -0.1236 | -0.07782 | -0.10529 | -0.054932 | 0.027466 | -0.059509 | 0.004578 | 0.073242 | -0.14191 | -0.10071 | 0.23804 | 0.11444 | 0.11902 | 0.041199 | 0.045777 | 0.27466 | -121.3348 | -121.312 | 0.40741 | 0.38452 | 0.32044 | 0.10986 | 0.045777 | 0.16479 | 121.463 | 0.13275 | 0.050354 | 121.4218 | 0.027466 | 121.4951 | 0.30212 | -121.5637 | -121.3623 | 121.5363 | 0.32501 | 6.2164 | 0.25635
1923.7344 | 121.6644 | -0.33875 | 121.3303 | -0.009308 | 6.9776 | 0.064192 | 0.062365 | 0.0014228 | -0.0067547 | -0.00044443 | 0.0025025 | 0.002446 | 0.013965 | 0.012563 | -0.0055585 | 0.027025 | -0.002651 | 5.7907 | 121.1609 | -0.27466 | 121.2112 | -0.13733 | -0.2243 | -0.25177 | -0.14648 | -0.10071 | -0.10071 | -0.054932 | 0.018311 | -0.045776 | 0.018311 | 0.064087 | -0.16937 | -0.11902 | 0.20142 | 0.086975 | 0.11444 | 0.022888 | 0.050354 | 0.23804 | -121.431 | -121.3852 | 0.35706 | 0.35706 | 0.29297 | 0.11902 | 0.054932 | 0.13733 | 121.4859 | 0.11902 | 0.045776 | 121.4355 | 0 | 121.4996 | 0.23804 | -121.6049 | -121.431 | 121.55 | 0.28381 | 6.1295 | 0.19226
1925.4062 | 121.6187 | -0.35706 | 121.4035 | -0.009308 | 6.9782 | 0.061842 | 0.063647 | -0.0028498 | -0.0065411 | -0.0032214 | -0.0036011 | 0.0050094 | 0.015033 | 0.0031638 | -0.0091901 | 0.024676 | -0.0020102 | 5.8365 | 121.2158 | -0.28839 | 121.2021 | -0.19684 | -0.2655 | -0.29755 | -0.20599 | -0.086975 | -0.1236 | -0.13733 | -0.054932 | -0.11444 | -0.054932 | 0.068665 | -0.18768 | -0.20142 | 0.16022 | 0.05951 | 0.091553 | -0.009155 | 0.022888 | 0.23346 | -121.4905 | -121.5408 | 0.30212 | 0.30212 | 0.24261 | 0.068664 | 0.009155 | 0.091553 | 121.4905 | 0.068664 | -0.013733 | 121.5042 | 0.036621 | 121.5729 | 0.27008 | -121.6919 | -121.5271 | 121.5591 | 0.21973 | 6.1935 | 0.15106
1927.1406 | 121.7377 | -0.29755 | 121.3806 | 0.005951 | 6.9771 | 0.065046 | 0.061938 | 0.00035457 | -0.0044049 | -0.00044443 | -0.0036011 | 0.0028732 | 0.017383 | 0.017904 | -0.0061993 | 0.028307 | -0.001583 | 5.8136 | 121.2387 | -0.25177 | 121.344 | -0.027466 | -0.18768 | -0.20599 | -0.050354 | -0.13275 | -0.073242 | -0.013733 | 0.041199 | -0.032043 | 0.036621 | 0.045776 | -0.14191 | -0.036621 | 0.27008 | 0.091552 | 0.10986 | 0.045776 | 0.064087 | 0.2243 | -121.5134 | -121.3943 | 0.33874 | 0.33417 | 0.2655 | 0.10986 | 0.041199 | 0.2243 | 121.5958 | 0.11444 | 0.059509 | 121.4905 | -0.059509 | 121.5363 | 0.16479 | -121.6324 | -121.4539 | 121.6415 | 0.28381 | 6.1111 | 0.24719
1928.8906 | 121.701 | -0.32044 | 121.4584 | 0.005951 | 6.9786 | 0.064832 | 0.06087 | 0.00035457 | -0.0086773 | -0.0025806 | -0.00054933 | -0.0003312 | 0.015246 | 0.01235 | -0.0096173 | 0.025744 | -0.0030784 | 5.9326 | 121.2433 | -0.24719 | 121.3486 | -0.073242 | -0.17395 | -0.21515 | -0.13275 | -0.10986 | -0.091553 | -0.086975 | 0.004578 | -0.054932 | -0.009155 | 0.073243 | -0.21515 | -0.10986 | 0.24719 | 0.10529 | 0.14649 | 0.032043 | 0.073242 | 0.22888 | -121.5683 | -121.5454 | 0.32501 | 0.31128 | 0.2655 | 0.082398 | 0.036621 | 0.17395 | 121.5958 | 0.096131 | 0.004578 | 121.4905 | -0.01831 | 121.5637 | 0.21057 | -121.7056 | -121.55 | 121.669 | 0.23346 | 6.2531 | 0.18768
1930.5625 | 121.788 | -0.27466 | 121.4081 | 0.005951 | 6.9784 | 0.066541 | 0.061938 | 0.00056817 | -0.0044049 | -0.0045032 | 0.0025025 | 0.0033004 | 0.014392 | 0.009786 | -0.0047039 | 0.025744 | -0.007778 | 5.8685 | 121.2708 | -0.23804 | 121.376 | -0.032043 | -0.17853 | -0.20142 | -0.041199 | -0.10529 | -0.073242 | -0.009155 | 0.041199 | 0 | 0.064087 | 0.036621 | -0.13733 | -0.032043 | 0.24262 | 0.073242 | 0.09613 | 0.036621 | 0.059509 | 0.20142 | -121.5134 | -121.4172 | 0.31586 | 0.33875 | 0.27466 | 0.13733 | 0.073242 | 0.20599 | 121.6141 | 0.11444 | 0.064087 | 121.5088 | -0.032044 | 121.5454 | 0.16937 | -121.6461 | -121.4813 | 121.6507 | 0.2655 | 6.1432 | 0.23346
1932.2969 | 121.8201 | -0.28839 | 121.4447 | 0.005951 | 6.9786 | 0.068037 | 0.062579 | 0.0044134 | -0.0044049 | -0.0030078 | 0.0055543 | 0.002446 | 0.016742 | 0.015127 | -0.0059857 | 0.026812 | -0.0017966 | 5.8411 | 121.2799 | -0.24261 | 121.3852 | -0.018311 | -0.18768 | -0.19226 | -0.054932 | -0.11444 | -0.064087 | 0.009155 | 0.064087 | 0.009155 | 0.045776 | 0.045776 | -0.1648 | -0.059509 | 0.27008 | 0.09613 | 0.10071 | 0.050354 | 0.054932 | 0.2243 | -121.5591 | -121.4355 | 0.35248 | 0.33417 | 0.29755 | 0.10986 | 0.073242 | 0.2243 | 121.6278 | 0.12817 | 0.073242 | 121.5225 | -0.050354 | 121.5683 | 0.17395 | -121.6873 | -121.5088 | 121.6736 | 0.29755 | 6.1295 | 0.23346
1933.9844 | 121.138 | -0.23346 | 120.9457 | 0.005951 | 6.9799 | 0.061628 | 0.062579 | 0.00056817 | -0.0099591 | -0.0027942 | 0.0025025 | 0.0037278 | 0.013324 | 0.011068 | -0.011113 | 0.027453 | -0.0047874 | 5.6808 | 120.7947 | -0.19226 | 120.7718 | -0.07782 | -0.16022 | -0.1831 | -0.21515 | -0.068665 | -0.11902 | -0.11444 | -0.068665 | -0.10529 | -0.032043 | 0.041198 | -0.15106 | -0.17395 | 0.15564 | 0.050354 | 0.073242 | 0.009156 | 0.032044 | 0.11444 | -121.0144 | -121.0602 | 0.16479 | 0.20142 | 0.12817 | 0.086976 | 0.013733 | 0.11444 | 120.9641 | 0.050354 | 0.004578 | 120.9869 | 0.050354 | 121.0281 | 0.16479 | -121.138 | -121.0648 | 121.0052 | 0.11902 | 5.9143 | 0.01831
1935.75 | 121.4676 | -0.20142 | 121.17 | 0.005951 | 6.9778 | 0.064832 | 0.064929 | -0.0011408 | -0.0073957 | -0.0045032 | 0.0025025 | 0.0009506 | 0.016314 | 0.016408 | -0.0076947 | 0.02788 | -0.0028646 | 5.7266 | 121.0464 | -0.13733 | 121.1151 | 0 | -0.11444 | -0.1236 | -0.15106 | -0.10529 | -0.064087 | -0.064087 | 0.013733 | -0.050354 | 0.009155 | 0.064087 | -0.1236 | -0.054932 | 0.20142 | 0.07782 | 0.086975 | 0.013733 | 0.022888 | 0.13733 | -121.2753 | -121.2341 | 0.21515 | 0.21057 | 0.15106 | 0.073242 | 0.013733 | 0.13733 | 121.2524 | 0.07782 | 0 | 121.1838 | -0.041199 | 121.2479 | 0.09613 | -121.3074 | -121.2341 | 121.3165 | 0.13733 | 5.928 | 0.050354
1937.4375 | 121.4813 | -0.21973 | 121.2524 | -0.0016785 | 6.9791 | 0.066328 | 0.062151 | 0.00056817 | -0.0067547 | -0.002367 | -0.00054933 | 0.0033004 | 0.017383 | 0.0099996 | -0.0098309 | 0.026171 | -0.0017966 | 5.7678 | 121.1517 | -0.18768 | 121.1243 | -0.064087 | -0.14648 | -0.16937 | -0.21057 | -0.064087 | -0.12817 | -0.07782 | -0.027466 | -0.09613 | -0.013733 | 0.032044 | -0.10071 | -0.12817 | 0.15564 | 0.050354 | 0.073243 | 0.01831 | 0.041199 | 0.091553 | -121.3165 | -121.3303 | 0.19226 | 0.20599 | 0.1236 | 0.11444 | 0.032044 | 0.1236 | 121.312 | 0.10071 | 0.050354 | 121.3394 | 0.064087 | 121.3715 | 0.15564 | -121.4401 | -121.3806 | 121.344 | 0.14191 | 5.9875 | 0.009156
1939.1875 | 121.4584 | -0.21515 | 121.312 | -0.009308 | 6.9784 | 0.064619 | 0.06322 | 0.0029182 | -0.0082501 | -0.0036486 | -0.0036011 | 0.0060776 | 0.014178 | 0.0023092 | -0.0089765 | 0.027025 | -0.00072839 | 5.7449 | 121.2021 | -0.14191 | 121.138 | -0.091553 | -0.20599 | -0.21515 | -0.23804 | -0.091553 | -0.11444 | -0.11444 | -0.082397 | -0.17853 | -0.059509 | 0.073242 | -0.10986 | -0.17395 | 0.1236 | 0 | 0.009155 | -0.073242 | -0.064087 | 0.10071 | -121.4035 | -121.4264 | 0.13275 | 0.15564 | 0.036621 | 0.054932 | -0.064087 | 0.050354 | 121.2799 | 0.032044 | 0 | 121.344 | 0.022888 | 121.4172 | 0.1236 | -121.4539 | -121.4264 | 121.3531 | 0.10071 | 5.9601 | -0.022888
1940.9375 | 121.6141 | -0.18768 | 121.3074 | -0.0016785 | 6.9784 | 0.066114 | 0.061938 | 0.0031318 | -0.0054731 | -0.00023063 | -0.00054933 | 0.0026596 | 0.015887 | 0.019613 | -0.0066265 | 0.025744 | -0.0024374 | 5.809 | 121.17 | -0.1236 | 121.3028 | 0.064087 | -0.064087 | -0.086975 | -0.064087 | -0.11902 | -0.082397 | 0.018311 | 0.064087 | -0.009155 | 0.054932 | 0.064087 | -0.13733 | -0.004578 | 0.25177 | 0.10071 | 0.1236 | 0.036621 | 0.059509 | 0.10529 | -121.4264 | -121.2891 | 0.25177 | 0.24261 | 0.17853 | 0.13733 | 0.073242 | 0.18768 | 121.4264 | 0.14648 | 0.10071 | 121.2936 | -0.036622 | 121.3577 | 0.068664 | -121.431 | -121.3898 | 121.4905 | 0.20599 | 5.9967 | 0.1236
1942.6094 | 121.5454 | -0.23804 | 121.3623 | -0.0016785 | 6.9786 | 0.064192 | 0.061724 | 0.0012092 | -0.0099591 | 0.0012646 | 0.0025025 | 0.0028732 | 0.015674 | 0.0093588 | -0.010899 | 0.025744 | -0.001583 | 5.8182 | 121.2341 | -0.1831 | 121.1746 | -0.07782 | -0.14648 | -0.17395 | -0.22888 | -0.068665 | -0.11902 | -0.11444 | -0.032043 | -0.13275 | -0.027466 | 0.054932 | -0.12817 | -0.18768 | 0.16022 | 0.064087 | 0.091553 | 0.009155 | 0.036621 | 0.11902 | -121.431 | -121.4767 | 0.20599 | 0.21057 | 0.10529 | 0.091553 | -0.013732 | 0.10528 | 121.3577 | 0.086976 | 0.004578 | 121.4172 | 0.050354 | 121.4722 | 0.16937 | -121.5454 | -121.4813 | 121.4127 | 0.1236 | 6.0562 | 0.009155
1944.3594 | 121.6324 | -0.19226 | 121.3165 | -0.0016785 | 6.9801 | 0.065473 | 0.061938 | 0.0050544 | -0.0065411 | -1.7026e-05 | -0.0036011 | 0.0013778 | 0.014605 | 0.019399 | -0.0070539 | 0.025744 | -0.0030784 | 5.7816 | 121.2158 | -0.14648 | 121.3074 | 0.068665 | -0.07782 | -0.10986 | -0.082397 | -0.11444 | -0.073242 | 0.004578 | 0.054932 | -0.041199 | 0.054932 | 0.045777 | -0.10071 | -0.009155 | 0.26093 | 0.082398 | 0.11444 | 0.036621 | 0.068664 | 0.11902 | -121.431 | -121.312 | 0.24719 | 0.24719 | 0.15106 | 0.12817 | 0.032043 | 0.21515 | 121.4539 | 0.12817 | 0.07782 | 121.3623 | -0.041199 | 121.4081 | 0.07782 | -121.463 | -121.3898 | 121.4996 | 0.19684 | 5.9738 | 0.10986
1946.0938 | 121.55 | -0.24261 | 121.3898 | -0.0016785 | 6.978 | 0.065901 | 0.06386 | 0.00056817 | -0.010814 | 0.0012646 | -0.00054933 | 0.0033004 | 0.014178 | 0.013845 | -0.0057721 | 0.024462 | -0.0054282 | 5.777 | 121.2616 | -0.17853 | 121.225 | -0.086975 | -0.19684 | -0.21515 | -0.23346 | -0.09613 | -0.11902 | -0.10071 | -0.082397 | -0.19226 | -0.050354 | 0.064087 | -0.12817 | -0.16479 | 0.15564 | 0.027466 | 0.045777 | -0.036621 | -0.01831 | 0.1236 | -121.4859 | -121.4905 | 0.16022 | 0.19226 | 0.050354 | 0.068665 | -0.073242 | 0.091553 | 121.4035 | 0.036622 | 0.018311 | 121.4401 | 0.022889 | 121.5042 | 0.14649 | -121.5683 | -121.5088 | 121.4676 | 0.14191 | 6.0196 | 0.009156
1947.7812 | 121.5729 | -0.22888 | 121.4127 | 0.005951 | 6.9795 | 0.066328 | 0.064288 | -0.0011408 | -0.0067547 | -0.002367 | -0.0036011 | 0.0022324 | 0.015033 | 0.010213 | -0.0064129 | 0.027239 | -0.0020102 | 5.7953 | 121.3074 | -0.16479 | 121.2112 | -0.10529 | -0.21057 | -0.2243 | -0.23804 | -0.086975 | -0.10986 | -0.10986 | -0.082397 | -0.16479 | -0.050354 | 0.064087 | -0.10529 | -0.20142 | 0.1236 | 0.004578 | 0.018311 | -0.059509 | -0.045776 | 0.11902 | -121.4996 | -121.5225 | 0.14649 | 0.17853 | 0.064087 | 0.059509 | -0.054932 | 0.059509 | 121.376 | 0.027466 | 0 | 121.4722 | 0.022888 | 121.5363 | 0.14191 | -121.5775 | -121.5225 | 121.4401 | 0.11902 | 6.0242 | -0.009155
1949.5312 | 121.6461 | -0.21057 | 121.3989 | 0.01358 | 6.9752 | 0.065687 | 0.060656 | 0.0016364 | -0.0056867 | -0.0012988 | -0.0036011 | 0.0022324 | 0.014392 | 0.02004 | -0.0076947 | 0.028948 | -0.0017966 | 5.7907 | 121.2616 | -0.16022 | 121.2982 | -0.013733 | -0.10986 | -0.13733 | -0.16022 | -0.11444 | -0.091553 | -0.073242 | 0.018311 | -0.068665 | 0.004578 | 0.050354 | -0.13733 | -0.10071 | 0.19684 | 0.073242 | 0.10071 | 0.022888 | 0.050354 | 0.11902 | -121.5134 | -121.4722 | 0.22888 | 0.21515 | 0.14191 | 0.096131 | 0.022888 | 0.14648 | 121.4584 | 0.10986 | 0.018311 | 121.4218 | -0.022888 | 121.4722 | 0.09613 | -121.5591 | -121.4905 | 121.5088 | 0.13733 | 6.0013 | 0.050354
1951.2031 | 121.6873 | -0.19684 | 121.3943 | -0.009308 | 6.9784 | 0.067396 | 0.062151 | 0.0054816 | -0.0054731 | -1.7026e-05 | 0.0025025 | 0.003514 | 0.017596 | 0.0095724 | -0.0076947 | 0.026598 | -0.0035056 | 5.8319 | 121.2662 | -0.1236 | 121.344 | 0.054932 | -0.07782 | -0.09613 | -0.073242 | -0.1236 | -0.059509 | -0.032043 | 0.027466 | -0.041199 | 0.045776 | 0.073242 | -0.12817 | -0.050354 | 0.25177 | 0.10071 | 0.11902 | 0.027466 | 0.045776 | 0.13733 | -121.5179 | -121.4264 | 0.2243 | 0.24261 | 0.15564 | 0.10528 | 0.01831 | 0.17853 | 121.4676 | 0.086975 | 0.027466 | 121.3898 | -0.064087 | 121.463 | 0.073242 | -121.5179 | -121.4539 | 121.5408 | 0.1648 | 6.0287 | 0.1236
1952.9375 | 121.7239 | -0.19684 | 121.4081 | 0.005951 | 6.9801 | 0.063978 | 0.062579 | 0.00014097 | -0.0071821 | -0.0036486 | -0.00054933 | 0.0020188 | 0.016101 | 0.014699 | -0.0051313 | 0.028307 | -0.0047874 | 5.8365 | 121.2708 | -0.15106 | 121.3852 | 0.059509 | -0.082397 | -0.091553 | -0.041199 | -0.13275 | -0.050354 | 0.013733 | 0.068665 | -0.013733 | 0.10529 | 0.045776 | -0.13733 | -0.022888 | 0.25635 | 0.10529 | 0.11444 | 0.059509 | 0.068665 | 0.14648 | -121.5408 | -121.3943 | 0.2655 | 0.30212 | 0.18311 | 0.15564 | 0.036621 | 0.21057 | 121.5363 | 0.11902 | 0.064087 | 121.4218 | -0.082397 | 121.4676 | 0.064087 | -121.5591 | -121.4584 | 121.582 | 0.21057 | 6.0333 | 0.15564
1954.6875 | 121.7148 | -0.21057 | 121.4447 | -0.0016785 | 6.9793 | 0.065046 | 0.062151 | -7.2628e-05 | -0.010173 | -0.0027942 | -0.0036011 | 0.0011642 | 0.015246 | 0.010427 | -0.011754 | 0.02553 | -0.003292 | 5.8731 | 121.2662 | -0.13733 | 121.3852 | 0.054932 | -0.054932 | -0.10071 | -0.07782 | -0.13733 | -0.050354 | -0.027466 | 0.068665 | 0.009155 | 0.073242 | 0.073242 | -0.17853 | -0.059509 | 0.2655 | 0.10986 | 0.15564 | 0.036621 | 0.082397 | 0.16022 | -121.582 | -121.4722 | 0.27924 | 0.28381 | 0.21973 | 0.1236 | 0.059509 | 0.19226 | 121.5225 | 0.11902 | 0.022888 | 121.4035 | -0.086975 | 121.4767 | 0.073242 | -121.582 | -121.4951 | 121.5958 | 0.18311 | 6.0837 | 0.13275
1956.3594 | 121.669 | -0.25635 | 121.4493 | -0.009308 | 6.9771 | 0.064405 | 0.061724 | 0.0044134 | -0.0099591 | -0.00044443 | -0.00054933 | 0.0026596 | 0.01546 | 0.011495 | -0.0094037 | 0.027025 | 0.001835 | 5.7632 | 121.3394 | -0.18768 | 121.3211 | -0.064087 | -0.14191 | -0.17395 | -0.17395 | -0.086975 | -0.091553 | -0.10529 | -0.027466 | -0.073242 | 0.032043 | 0.068665 | -0.10986 | -0.12817 | 0.19226 | 0.082398 | 0.11444 | 0.013733 | 0.045776 | 0.1648 | -121.5363 | -121.5546 | 0.22888 | 0.28839 | 0.18311 | 0.1236 | 0.018311 | 0.1236 | 121.5088 | 0.064087 | -0.013733 | 121.5271 | 0.004578 | 121.5958 | 0.16937 | -121.637 | -121.5408 | 121.5775 | 0.15106 | 6.0196 | 0.082398
1958.1094 | 121.6278 | -0.25635 | 121.4539 | -0.009308 | 6.9803 | 0.066328 | 0.065569 | -0.00028623 | -0.0088911 | -0.0055712 | 0.0025025 | 0.003514 | 0.015674 | 0.010213 | -0.0081219 | 0.026385 | -0.0022238 | 5.777 | 121.3211 | -0.17395 | 121.3303 | -0.054932 | -0.16479 | -0.1831 | -0.15564 | -0.082397 | -0.064087 | -0.09613 | -0.045776 | -0.11902 | 0 | 0.082398 | -0.13275 | -0.1236 | 0.20142 | 0.073243 | 0.091553 | -0.009155 | 0.009155 | 0.19226 | -121.5363 | -121.55 | 0.21057 | 0.25635 | 0.13733 | 0.064087 | -0.054932 | 0.11902 | 121.5042 | 0.018311 | -0.032043 | 121.4951 | -0.01831 | 121.5775 | 0.17395 | -121.6278 | -121.5179 | 121.5866 | 0.16022 | 6.0333 | 0.10071
1959.8594 | 121.6461 | -0.22888 | 121.4767 | 0.005951 | 6.9774 | 0.063123 | 0.061511 | 0.0033454 | -0.0073957 | -0.00023063 | -0.0036011 | 0.0011642 | 0.015674 | 0.0089316 | -0.011967 | 0.023607 | -0.0028646 | 5.8182 | 121.312 | -0.16022 | 121.3394 | -0.032043 | -0.11444 | -0.17395 | -0.18768 | -0.11444 | -0.091553 | -0.1236 | -0.054932 | -0.10529 | -0.018311 | 0.068665 | -0.1648 | -0.13733 | 0.19684 | 0.054932 | 0.11444 | -0.013733 | 0.045776 | 0.13733 | -121.5912 | -121.6003 | 0.17395 | 0.21057 | 0.1236 | 0.073242 | -0.013733 | 0.12817 | 121.4996 | 0.036621 | -0.032043 | 121.4722 | -0.022888 | 121.5408 | 0.11444 | -121.637 | -121.5683 | 121.5683 | 0.10529 | 6.0471 | 0.041199
1961.5469 | 121.6278 | -0.25177 | 121.4767 | -0.0016785 | 6.9761 | 0.065687 | 0.064288 | 0.0020636 | -0.0063275 | -0.0047168 | -0.00054933 | 0.0033004 | 0.016314 | 0.00017303 | -0.0061993 | 0.025957 | -0.0028646 | 5.7495 | 121.3486 | -0.17853 | 121.2799 | -0.13275 | -0.21057 | -0.23346 | -0.2243 | -0.11444 | -0.10071 | -0.13275 | -0.11444 | -0.15564 | -0.018311 | 0.073242 | -0.12817 | -0.19684 | 0.11902 | 0.018311 | 0.041199 | -0.054931 | -0.032043 | 0.15106 | -121.5912 | -121.6095 | 0.13733 | 0.23346 | 0.09613 | 0.082397 | -0.054932 | 0.045777 | 121.4584 | -0.013733 | -0.032043 | 121.5271 | -0.013733 | 121.6003 | 0.13733 | -121.6553 | -121.5775 | 121.5317 | 0.11902 | 6.0013 | 0.027466
1963.2812 | 121.6553 | -0.24719 | 121.4676 | -0.009308 | 6.9769 | 0.063123 | 0.06322 | -0.0013544 | -0.0039777 | -0.0040758 | -0.0036011 | 0.0018052 | 0.015674 | 0.01299 | -0.0076947 | 0.02318 | -0.0041464 | 5.8548 | 121.3074 | -0.16022 | 121.3531 | -0.018311 | -0.10529 | -0.14191 | -0.14191 | -0.11902 | -0.073242 | -0.1236 | -0.059509 | -0.10529 | -0.032043 | 0.086975 | -0.16022 | -0.11444 | 0.22888 | 0.10528 | 0.14191 | 0.01831 | 0.054931 | 0.17395 | -121.5866 | -121.5912 | 0.18768 | 0.21515 | 0.14191 | 0.041199 | -0.032044 | 0.14191 | 121.5134 | 0.013733 | -0.050354 | 121.4676 | -0.045777 | 121.5546 | 0.12817 | -121.6278 | -121.5408 | 121.6003 | 0.1236 | 6.102 | 0.10528
1965.0312 | 121.669 | -0.24261 | 121.4813 | 0.005951 | 6.9806 | 0.064619 | 0.065356 | -0.0022088 | -0.0052595 | -0.0015124 | -0.00054933 | 0.0030868 | 0.017169 | 0.011495 | -0.0049175 | 0.026812 | -0.001583 | 5.8411 | 121.376 | -0.16479 | 121.3623 | -0.018311 | -0.13275 | -0.17395 | -0.10529 | -0.10986 | -0.068665 | -0.086975 | -0.036621 | -0.09613 | 0.004578 | 0.07782 | -0.10529 | -0.11902 | 0.2243 | 0.068665 | 0.10986 | -0.009155 | 0.032044 | 0.17395 | -121.5912 | -121.5683 | 0.20599 | 0.24719 | 0.14649 | 0.073243 | -0.027465 | 0.14648 | 121.5271 | 0.032044 | -0.01831 | 121.5408 | -0.041198 | 121.6187 | 0.13275 | -121.6461 | -121.55 | 121.6049 | 0.15564 | 6.0837 | 0.13733
1966.7812 | 121.701 | -0.24719 | 121.4951 | -0.009308 | 6.978 | 0.064192 | 0.06322 | 0.00035457 | -0.0076093 | -0.0015124 | -0.0066527 | 0.0039414 | 0.019305 | 0.020681 | -0.0066265 | 0.026598 | -0.0017966 | 5.7312 | 121.376 | -0.1831 | 121.3074 | -0.086975 | -0.21057 | -0.21973 | -0.16937 | -0.1236 | -0.09613 | -0.10071 | -0.073242 | -0.11902 | 0.004578 | 0.064087 | -0.11902 | -0.18768 | 0.16022 | 0.027465 | 0.036621 | -0.036622 | -0.027466 | 0.15106 | -121.6187 | -121.5958 | 0.17395 | 0.25177 | 0.12817 | 0.10071 | -0.022889 | 0.09613 | 121.4905 | 0.022888 | -0.004578 | 121.5591 | -0.027466 | 121.6232 | 0.1236 | -121.6782 | -121.5912 | 121.5546 | 0.14648 | 5.9784 | 0.077819
1968.4688 | 121.5729 | -0.21515 | 121.3898 | -0.0016785 | 6.9771 | 0.063764 | 0.062151 | 0.0029182 | -0.0067547 | -0.0010852 | 0.0025025 | 0.0028732 | 0.013751 | 0.015127 | -0.010258 | 0.023821 | -0.0030784 | 5.7861 | 121.2753 | -0.1831 | 121.2387 | -0.050354 | -0.11444 | -0.15564 | -0.15564 | -0.10529 | -0.09613 | -0.10071 | -0.027466 | -0.07782 | 0.013733 | 0.032044 | -0.11444 | -0.15106 | 0.16479 | 0.059509 | 0.10071 | 0.027465 | 0.068664 | 0.11902 | -121.4951 | -121.4905 | 0.18768 | 0.22888 | 0.13733 | 0.10986 | 0.01831 | 0.13275 | 121.4218 | 0.068664 | -0.004578 | 121.4584 | -0.009156 | 121.4905 | 0.10986 | -121.5729 | -121.4859 | 121.4539 | 0.11444 | 6.0013 | 0.059509
1970.2031 | 121.6644 | -0.21973 | 121.4539 | -0.0016785 | 6.9789 | 0.066541 | 0.061297 | 0.003559 | -0.0086773 | -0.0019396 | -0.00054933 | 0.0033004 | 0.013965 | 0.012777 | -0.0079083 | 0.026598 | -0.0041464 | 5.8365 | 121.3028 | -0.16022 | 121.3211 | 0 | -0.10529 | -0.1236 | -0.10071 | -0.10986 | -0.082397 | -0.064087 | -0.004578 | -0.068665 | 0.032043 | 0.05951 | -0.15106 | -0.13275 | 0.21973 | 0.096131 | 0.11444 | 0.036621 | 0.054931 | 0.13733 | -121.5637 | -121.5179 | 0.21515 | 0.25177 | 0.15106 | 0.11444 | 0.013732 | 0.16022 | 121.4813 | 0.077819 | 0.01831 | 121.463 | -0.027466 | 121.5225 | 0.10986 | -121.6141 | -121.5363 | 121.5408 | 0.15564 | 6.0562 | 0.11902
1971.9375 | 121.7651 | -0.20599 | 121.4401 | -0.009308 | 6.9769 | 0.063978 | 0.060229 | -0.0034906 | -0.0065411 | -0.0040758 | -0.0066527 | 0.0005234 | 0.01546 | 0.011709 | -0.0055585 | 0.02788 | -0.0030784 | 5.7587 | 121.3165 | -0.13275 | 121.3715 | 0.059509 | -0.050354 | -0.073242 | -0.050354 | -0.14191 | -0.064087 | -0.032043 | 0.054932 | 0.009155 | 0.082397 | 0.073243 | -0.1236 | -0.068665 | 0.2655 | 0.13275 | 0.15564 | 0.059509 | 0.082397 | 0.14191 | -121.582 | -121.4722 | 0.26093 | 0.28839 | 0.21515 | 0.14648 | 0.073242 | 0.19226 | 121.5042 | 0.11902 | 0.032044 | 121.4493 | -0.07782 | 121.5225 | 0.064087 | -121.5729 | -121.5042 | 121.5775 | 0.17395 | 5.9647 | 0.15564
1973.6719 | 121.7285 | -0.1831 | 121.4722 | 0.005951 | 6.9771 | 0.066114 | 0.062365 | -0.00028623 | -0.0059003 | -0.0042896 | 0.0025025 | 0.0009506 | 0.015033 | 0.014699 | -0.0049175 | 0.028094 | -0.0013694 | 5.7816 | 121.3257 | -0.13275 | 121.4081 | 0.082397 | -0.073242 | -0.091553 | -0.032043 | -0.15106 | -0.073242 | -0.027466 | 0.018311 | -0.022888 | 0.050354 | 0.050354 | -0.14648 | -0.064087 | 0.2655 | 0.091552 | 0.10986 | 0.041198 | 0.059509 | 0.10986 | -121.6232 | -121.4996 | 0.20142 | 0.23346 | 0.16022 | 0.1236 | 0.050354 | 0.21515 | 121.5408 | 0.091553 | 0.045776 | 121.4584 | -0.07782 | 121.5088 | 0.032043 | -121.6049 | -121.5454 | 121.5912 | 0.15564 | 5.9647 | 0.15106
1975.3594 | 121.7926 | -0.16937 | 121.4493 | -0.009308 | 6.9782 | 0.065901 | 0.06087 | 0.0024908 | -0.0054731 | -0.002367 | 0.0025025 | 0.0013778 | 0.012683 | 0.017263 | -0.0057721 | 0.027025 | -0.003292 | 5.7953 | 121.3531 | -0.11902 | 121.431 | 0.073242 | -0.068665 | -0.082397 | -0.004578 | -0.14191 | -0.054932 | 0.027466 | 0.064087 | 0.004578 | 0.091553 | 0.050354 | -0.096131 | -0.018311 | 0.24261 | 0.086976 | 0.10071 | 0.036622 | 0.050354 | 0.11444 | -121.5912 | -121.4218 | 0.23346 | 0.26093 | 0.17395 | 0.14649 | 0.05951 | 0.19226 | 121.55 | 0.11902 | 0.082398 | 121.4722 | -0.086975 | 121.5225 | 0.027466 | -121.5683 | -121.5042 | 121.6003 | 0.19684 | 5.9647 | 0.16479
1977.0938 | 121.7697 | -0.20142 | 121.4676 | -0.009308 | 6.9774 | 0.062055 | 0.061724 | 0.00099557 | -0.0106 | -0.0040758 | -0.00054933 | 0.0022324 | 0.014178 | 0.0093588 | -0.0096173 | 0.026171 | -0.0020102 | 5.8136 | 121.3394 | -0.13275 | 121.4584 | 0.091553 | -0.027466 | -0.054932 | -0.004578 | -0.11902 | -0.036621 | -0.004578 | 0.091553 | 0.041199 | 0.10071 | 0.068665 | -0.12817 | -0.009155 | 0.29297 | 0.14648 | 0.17395 | 0.077819 | 0.10529 | 0.1648 | -121.5866 | -121.4722 | 0.29297 | 0.30212 | 0.24262 | 0.13733 | 0.07782 | 0.2243 | 121.5912 | 0.12817 | 0.032043 | 121.4722 | -0.082398 | 121.5408 | 0.082397 | -121.6003 | -121.5042 | 121.6599 | 0.19684 | 6.015 | 0.19684
1978.8281 | 121.7377 | -0.19226 | 121.4951 | -0.009308 | 6.9763 | 0.064619 | 0.061724 | -0.002636 | -0.0054731 | -0.0012988 | -0.00054933 | 0.0009506 | 0.017383 | 0.012136 | -0.0070539 | 0.025957 | -0.0045736 | 5.7175 | 121.3623 | -0.14191 | 121.3852 | -0.004578 | -0.10529 | -0.1236 | -0.09613 | -0.11444 | -0.050354 | -0.059509 | 0.022888 | -0.018311 | 0.045776 | 0.050354 | -0.13275 | -0.10986 | 0.18768 | 0.068665 | 0.086975 | 0.018311 | 0.036621 | 0.14191 | -121.6095 | -121.5546 | 0.21515 | 0.23804 | 0.17395 | 0.09613 | 0.032043 | 0.13733 | 121.5271 | 0.073242 | -0.009155 | 121.5042 | -0.064087 | 121.5546 | 0.07782 | -121.637 | -121.5454 | 121.5775 | 0.13275 | 5.9097 | 0.096131
1980.5156 | 121.7285 | -0.20142 | 121.4996 | 0.01358 | 6.9795 | 0.064619 | 0.065142 | 0.00099557 | -0.0080365 | -0.0021532 | 0.0025025 | 0.002446 | 0.014605 | 0.01769 | -0.0053449 | 0.027666 | -0.0035056 | 5.658 | 121.3531 | -0.14191 | 121.4081 | 0 | -0.11902 | -0.11902 | -0.082397 | -0.1236 | -0.045776 | -0.036621 | 0.004578 | -0.041199 | 0.050354 | 0.059509 | -0.14648 | -0.091553 | 0.20142 | 0.082397 | 0.082397 | 0.022888 | 0.022888 | 0.15564 | -121.6232 | -121.5363 | 0.20599 | 0.25177 | 0.16022 | 0.09613 | 0.004577 | 0.14191 | 121.55 | 0.050354 | 0.009155 | 121.4951 | -0.07782 | 121.5546 | 0.07782 | -121.6415 | -121.5454 | 121.6095 | 0.1648 | 5.8594 | 0.11902
1982.25 | 121.6919 | -0.25177 | 121.5179 | -0.016937 | 6.9789 | 0.06291 | 0.06322 | -0.001568 | -0.01295 | -0.0012988 | 0.0025025 | 0.0047958 | 0.011188 | 0.012563 | -0.0094037 | 0.026171 | -0.005001 | 5.7404 | 121.3989 | -0.1831 | 121.3348 | -0.068665 | -0.16022 | -0.17853 | -0.15564 | -0.064087 | -0.082397 | -0.10529 | -0.036621 | -0.07782 | 0.018311 | 0.068665 | -0.11902 | -0.1831 | 0.1831 | 0.073242 | 0.091553 | 0.004577 | 0.022888 | 0.16937 | -121.582 | -121.6232 | 0.21515 | 0.27008 | 0.17395 | 0.10071 | 0.004577 | 0.11444 | 121.5179 | 0.045776 | -0.022889 | 121.582 | 0.01831 | 121.6507 | 0.18768 | -121.701 | -121.6003 | 121.5866 | 0.14648 | 5.9921 | 0.09613
1983.9375 | 121.6827 | -0.25635 | 121.5317 | -0.0016785 | 6.9806 | 0.063551 | 0.064074 | 0.00099557 | -0.0056867 | -0.0010852 | 0.0025025 | 0.0015914 | 0.013751 | 0.019185 | -0.0074811 | 0.02553 | -0.0028646 | 5.6992 | 121.4172 | -0.17853 | 121.3303 | -0.10986 | -0.21973 | -0.21973 | -0.19226 | -0.073242 | -0.07782 | -0.1236 | -0.10071 | -0.14648 | -0.013733 | 0.07782 | -0.11444 | -0.20142 | 0.14649 | 0.036621 | 0.036621 | -0.041199 | -0.041199 | 0.17853 | -121.6049 | -121.6553 | 0.15564 | 0.24262 | 0.10986 | 0.064087 | -0.068664 | 0.068665 | 121.5088 | -0.022888 | -0.045776 | 121.5958 | 0.004578 | 121.6736 | 0.18311 | -121.7102 | -121.6095 | 121.5866 | 0.13275 | 5.9555 | 0.064087
1985.6875 | 121.756 | -0.2243 | 121.4859 | -0.0016785 | 6.9774 | 0.066114 | 0.060015 | -0.002636 | -0.0076093 | -0.0027942 | -0.00054933 | -0.000972 | 0.01311 | 0.014272 | -0.0053449 | 0.025957 | -0.0020102 | 5.6351 | 121.3623 | -0.14191 | 121.4035 | -0.009155 | -0.11902 | -0.14191 | -0.11444 | -0.13275 | -0.064087 | -0.041199 | 0.018311 | -0.045776 | 0.059509 | 0.082397 | -0.1236 | -0.082398 | 0.21515 | 0.082397 | 0.10529 | 0 | 0.022888 | 0.16022 | -121.6187 | -121.5271 | 0.24261 | 0.28381 | 0.17853 | 0.1236 | 0.018311 | 0.13275 | 121.5454 | 0.082398 | 0.022888 | 121.5042 | -0.068664 | 121.5866 | 0.091553 | -121.6278 | -121.55 | 121.6278 | 0.18311 | 5.8594 | 0.10986
1987.4375 | 121.756 | -0.22888 | 121.5225 | -0.0016785 | 6.978 | 0.066114 | 0.061083 | 0.0012092 | -0.0086773 | -0.0010852 | -0.0036011 | 0.0033004 | 0.014392 | 0.014699 | -0.0066265 | 0.026598 | -0.003292 | 5.6717 | 121.4127 | -0.16937 | 121.3577 | -0.068665 | -0.19226 | -0.18768 | -0.09613 | -0.091553 | -0.064087 | -0.036621 | -0.009155 | -0.041199 | 0.059509 | 0.059509 | -0.10986 | -0.16479 | 0.16022 | 0.041199 | 0.036621 | -0.01831 | -0.022888 | 0.16479 | -121.6141 | -121.5591 | 0.21973 | 0.28839 | 0.18768 | 0.1236 | 0.022888 | 0.10071 | 121.5271 | 0.054932 | 0.027466 | 121.582 | -0.027466 | 121.6415 | 0.13733 | -121.6919 | -121.5866 | 121.5866 | 0.19226 | 5.9006 | 0.13275
1989.1875 | 121.7743 | -0.19684 | 121.4767 | -0.0016785 | 6.9756 | 0.063123 | 0.062365 | -0.0028498 | -0.0065411 | -0.0015124 | -0.00054933 | -0.0011856 | 0.015033 | 0.019399 | -0.0085491 | 0.026812 | -0.00094199 | 5.6854 | 121.376 | -0.14191 | 121.3898 | -0.022888 | -0.12817 | -0.14648 | -0.086975 | -0.091553 | -0.054932 | -0.032043 | 0.032043 | -0.018311 | 0.059509 | 0.054931 | -0.10071 | -0.086975 | 0.17395 | 0.050354 | 0.068664 | -0.004577 | 0.013733 | 0.14191 | -121.5683 | -121.5088 | 0.22888 | 0.25635 | 0.17853 | 0.11444 | 0.036621 | 0.11902 | 121.5317 | 0.086975 | 0.022889 | 121.5179 | -0.036621 | 121.5729 | 0.10529 | -121.6187 | -121.5317 | 121.5866 | 0.1648 | 5.8823 | 0.10986
1990.8594 | 121.6827 | -0.24719 | 121.5591 | 0.005951 | 6.9799 | 0.066114 | 0.066638 | -0.00071343 | -0.0065411 | -0.0045032 | -0.0066527 | 0.003514 | 0.015674 | 0.014059 | -0.0070539 | 0.025957 | -0.00030119 | 5.7037 | 121.3989 | -0.17395 | 121.3394 | -0.12817 | -0.23804 | -0.23804 | -0.17853 | -0.09613 | -0.073242 | -0.09613 | -0.091553 | -0.12817 | -0.013733 | 0.073242 | -0.16022 | -0.21973 | 0.11902 | 0.009155 | 0.009155 | -0.064087 | -0.064087 | 0.17395 | -121.6553 | -121.6553 | 0.15564 | 0.23346 | 0.11902 | 0.059509 | -0.054932 | 0.045776 | 121.5134 | -0.018311 | -0.022888 | 121.5729 | -0.022888 | 121.6461 | 0.15106 | -121.7331 | -121.6324 | 121.5866 | 0.15106 | 5.9509 | 0.068664
1992.6094 | 121.8018 | -0.20142 | 121.5088 | 0.005951 | 6.9774 | 0.064832 | 0.062792 | -0.00049983 | -0.0061139 | -0.00065803 | -0.0036011 | 0.003514 | 0.016742 | 0.010213 | -0.0072675 | 0.026812 | -0.0047874 | 5.6351 | 121.4035 | -0.17853 | 121.3898 | -0.041199 | -0.17395 | -0.16937 | -0.064087 | -0.11444 | -0.032043 | -0.009155 | 0.022888 | -0.027466 | 0.068665 | 0.022888 | -0.10529 | -0.11902 | 0.16022 | 0.032043 | 0.027466 | 0.009155 | 0.004578 | 0.16937 | -121.6232 | -121.5179 | 0.2243 | 0.27008 | 0.17395 | 0.10071 | 0.004577 | 0.13733 | 121.5683 | 0.054931 | 0.022888 | 121.582 | -0.082398 | 121.6049 | 0.086975 | -121.6873 | -121.5408 | 121.5912 | 0.19226 | 5.8365 | 0.13733
1994.2969 | 121.8384 | -0.18768 | 121.5134 | -0.0016785 | 6.9789 | 0.065901 | 0.06087 | -0.003277 | -0.0071821 | -0.0010852 | -0.0066527 | 0.0005234 | 0.014605 | 0.0095724 | -0.0096173 | 0.026385 | -0.001583 | 5.7037 | 121.344 | -0.16022 | 121.4951 | 0.07782 | -0.045776 | -0.091553 | 0.009155 | -0.12817 | -0.045776 | 0.013733 | 0.09613 | 0.045776 | 0.091553 | 0.027466 | -0.16937 | -0.018311 | 0.2655 | 0.09613 | 0.14191 | 0.068664 | 0.11444 | 0.14191 | -121.6415 | -121.4996 | 0.28381 | 0.27924 | 0.23346 | 0.13733 | 0.091552 | 0.23804 | 121.6553 | 0.14191 | 0.059509 | 121.5042 | -0.082398 | 121.5317 | 0.059509 | -121.6736 | -121.5591 | 121.6827 | 0.20142 | 5.8914 | 0.19684
1996.0312 | 121.8246 | -0.20142 | 121.4996 | -0.0016785 | 6.9797 | 0.064192 | 0.063647 | 0.0020636 | -0.0071821 | -0.003435 | -0.0036011 | 0.0037278 | 0.015033 | 0.020681 | -0.0068403 | 0.026812 | -0.0071372 | 5.6671 | 121.431 | -0.16479 | 121.4172 | -0.018311 | -0.14648 | -0.15106 | -0.054932 | -0.11444 | -0.032043 | 0.004578 | 0.054932 | -0.004578 | 0.091553 | 0.036621 | -0.068665 | -0.082398 | 0.18311 | 0.050354 | 0.054932 | 0.013733 | 0.018311 | 0.16937 | -121.6141 | -121.4951 | 0.25635 | 0.29297 | 0.19684 | 0.1236 | 0.027465 | 0.14648 | 121.582 | 0.086975 | 0.036621 | 121.5958 | -0.082398 | 121.6324 | 0.086975 | -121.6644 | -121.5317 | 121.6187 | 0.20599 | 5.8685 | 0.14648
1997.8125 | 121.7651 | -0.23804 | 121.5454 | -0.009308 | 6.9776 | 0.065473 | 0.061724 | 0.0056952 | -0.0082501 | -0.0019396 | -0.00054933 | 0.0043686 | 0.016528 | 0.011709 | -0.0098309 | 0.024248 | -0.001583 | 5.7358 | 121.4355 | -0.17395 | 121.3989 | -0.032043 | -0.16022 | -0.17395 | -0.09613 | -0.10071 | -0.068665 | -0.059509 | -0.013733 | -0.050354 | 0.041199 | 0.064087 | -0.10986 | -0.14648 | 0.20599 | 0.064087 | 0.07782 | 0 | 0.013733 | 0.16937 | -121.6461 | -121.6049 | 0.2243 | 0.27924 | 0.18768 | 0.10986 | 0.018311 | 0.14191 | 121.5729 | 0.054932 | 0.009156 | 121.6095 | -0.032043 | 121.6736 | 0.13733 | -121.7194 | -121.6141 | 121.637 | 0.17853 | 5.9738 | 0.14191
1999.5469 | 121.7285 | -0.25635 | 121.5546 | -0.0016785 | 6.9759 | 0.06291 | 0.062579 | -0.00028623 | -0.0088911 | -0.0015124 | 0.0025025 | 0.0030868 | 0.014605 | 0.010213 | -0.0098309 | 0.025744 | -0.002651 | 5.6992 | 121.4401 | -0.19226 | 121.3303 | -0.10529 | -0.20142 | -0.21515 | -0.17395 | -0.086975 | -0.059509 | -0.10529 | -0.050354 | -0.086975 | 0 | 0.064087 | -0.11444 | -0.2243 | 0.15106 | 0.041199 | 0.054932 | -0.022888 | -0.009155 | 0.19684 | -121.6415 | -121.6599 | 0.20599 | 0.25635 | 0.16937 | 0.059509 | -0.027466 | 0.086975 | 121.5225 | 0.009155 | -0.045777 | 121.6324 | -0.027466 | 121.6965 | 0.16937 | -121.7468 | -121.6141 | 121.5866 | 0.15106 | 5.9555 | 0.082398
2001.2812 | 121.8109 | -0.21973 | 121.4951 | 0.005951 | 6.9786 | 0.064832 | 0.060229 | 0.0012092 | -0.0061139 | -0.0025806 | -0.0036011 | 0.0018052 | 0.014605 | 0.0089316 | -0.0074811 | 0.026812 | -0.0020102 | 5.6488 | 121.3989 | -0.12817 | 121.4767 | 0.050354 | -0.10071 | -0.11444 | -0.009155 | -0.13275 | -0.054932 | 0 | 0.064087 | 0 | 0.086975 | 0.091553 | -0.09613 | -0.01831 | 0.27008 | 0.10529 | 0.11902 | 0.013733 | 0.027466 | 0.16479 | -121.6278 | -121.4951 | 0.28381 | 0.3067 | 0.21973 | 0.14191 | 0.054932 | 0.17853 | 121.6049 | 0.11902 | 0.054932 | 121.5271 | -0.077819 | 121.6187 | 0.086976 | -121.6232 | -121.55 | 121.6965 | 0.21973 | 5.8685 | 0.21057
2002.9531 | 121.8155 | -0.2243 | 121.5225 | -0.0016785 | 6.9769 | 0.063764 | 0.058947 | 0.0014228 | -0.0063275 | -0.0036486 | -0.00054933 | 0.0013778 | 0.015033 | 0.015554 | -0.0061993 | 0.025744 | -0.00436 | 5.6076 | 121.3943 | -0.16937 | 121.3989 | -0.013733 | -0.13275 | -0.14648 | -0.07782 | -0.11444 | -0.054932 | -0.050354 | 0.027466 | 0 | 0.054932 | 0.054931 | -0.12817 | -0.1236 | 0.21057 | 0.07782 | 0.091553 | 0.022889 | 0.036622 | 0.16937 | -121.637 | -121.5729 | 0.25177 | 0.27924 | 0.2243 | 0.10986 | 0.054932 | 0.15564 | 121.5683 | 0.082398 | 0.004578 | 121.5637 | -0.059509 | 121.6187 | 0.10986 | -121.6919 | -121.5775 | 121.6232 | 0.17395 | 5.8319 | 0.14648
2004.7031 | 121.8292 | -0.22888 | 121.5134 | -0.0016785 | 6.9763 | 0.063978 | 0.061083 | -0.0037042 | -0.0093183 | -0.0021532 | -0.00054933 | 0.0015914 | 0.014819 | 0.0089316 | -0.0098309 | 0.02553 | -0.0037192 | 5.7037 | 121.3715 | -0.14648 | 121.4859 | 0.050354 | -0.07782 | -0.09613 | -0.022888 | -0.1236 | -0.036621 | -0.013733 | 0.054932 | 0.032043 | 0.07782 | 0.082398 | -0.14191 | -0.027466 | 0.27924 | 0.13275 | 0.15106 | 0.050354 | 0.068664 | 0.19226 | -121.637 | -121.5271 | 0.28381 | 0.3067 | 0.26093 | 0.11444 | 0.068664 | 0.19684 | 121.6324 | 0.091553 | 0.022888 | 121.5179 | -0.086975 | 121.6003 | 0.10529 | -121.6599 | -121.55 | 121.7148 | 0.21515 | 5.9326 | 0.20599
2006.4531 | 121.788 | -0.25177 | 121.5363 | -0.009308 | 6.9795 | 0.064405 | 0.062579 | 0.00056817 | -0.0065411 | -0.0021532 | -0.00054933 | 0.0037278 | 0.013324 | 0.008718 | -0.0079083 | 0.026812 | -0.005001 | 5.6259 | 121.3898 | -0.18768 | 121.4218 | -0.032043 | -0.16479 | -0.16479 | -0.064087 | -0.091553 | -0.064087 | -0.045776 | 0.009155 | -0.054932 | 0.045776 | 0.064087 | -0.14648 | -0.11444 | 0.21973 | 0.086975 | 0.086975 | 0.022888 | 0.022888 | 0.18768 | -121.6278 | -121.582 | 0.26093 | 0.29755 | 0.19684 | 0.10986 | 0.009155 | 0.15564 | 121.6095 | 0.073242 | 0.018311 | 121.5775 | -0.027466 | 121.6415 | 0.16022 | -121.7239 | -121.6003 | 121.6736 | 0.20599 | 5.8777 | 0.18768
2008.125 | 121.8658 | -0.25177 | 121.4218 | -0.0016785 | 6.9786 | 0.065473 | 0.06386 | 0.00014097 | -0.0048321 | -0.0030078 | -0.0066527 | 0.0015914 | 0.011615 | 0.019185 | -0.0070539 | 0.028094 | -0.0017966 | 5.6351 | 121.3669 | -0.20599 | 121.431 | -0.013733 | -0.15564 | -0.16479 | -0.013733 | -0.14191 | -0.018311 | 0.022888 | 0.054932 | 0.018311 | 0.12817 | 0.045776 | -0.054932 | 0.009155 | 0.23804 | 0.086975 | 0.09613 | 0.041199 | 0.050354 | 0.23346 | -121.5637 | -121.3989 | 0.3067 | 0.37994 | 0.27008 | 0.14649 | 0.036622 | 0.19226 | 121.637 | 0.073243 | 0.041199 | 121.5729 | -0.1236 | 121.6187 | 0.10986 | -121.6278 | -121.4401 | 121.6827 | 0.27466 | 5.8868 | 0.23804
2009.8125 | 117.5766 | -27.4841 | 89.6439 | -0.009308 | 6.9797 | 0.062696 | 0.062579 | -0.00092703 | -0.0076093 | -0.0025806 | -0.00054933 | 0.002446 | 0.016742 | 0.015127 | -0.0057721 | 0.028948 | 0.0020486 | 1.2314 | 89.6301 | -27.5299 | 90.2573 | -26.7792 | -27.0309 | -28.038 | 0.013733 | -0.10986 | -0.018311 | 0.050354 | 0.091553 | 0.032043 | 0.13275 | -0.045776 | -0.013733 | 0.6134 | 0.70496 | -0.55389 | 0.45319 | -0.50812 | 0.49896 | 27.4658 | -89.7537 | -89.5935 | 27.5757 | 27.6169 | 27.5162 | 0.15106 | 0.050354 | 0.75073 | 117.7872 | 0.10986 | 0.068665 | 117.16 | -0.091552 | 117.1143 | 27.3743 | -117.1738 | -89.6622 | 117.7414 | 27.5345 | 28.7155 | 27.4979
2011.5625 | 120.8908 | -0.19226 | 120.8176 | 0.005951 | 6.9818 | 0.064832 | 0.060656 | 0.0031318 | -0.0050457 | -0.002367 | -0.00054933 | 0.0030868 | 0.013324 | 0.0072226 | -0.0085491 | 0.026385 | -0.0039328 | 5.5069 | 120.6665 | -0.12817 | 120.4651 | -0.009155 | -0.16479 | -0.11444 | -0.11902 | -0.09613 | -0.054932 | -0.10529 | -0.068665 | -0.11902 | 0.013733 | 0.064087 | -0.15106 | -0.35248 | 0.18311 | 0.07782 | 0.027466 | 0.013733 | -0.036621 | 0.13733 | -120.9137 | -120.9229 | 0.1236 | 0.20599 | 0.073242 | 0.068665 | -0.064087 | 0.11902 | 120.5933 | -0.013733 | -0.050354 | 120.7947 | -0.041198 | 120.8588 | 0.096131 | -120.9457 | -120.8725 | 120.6573 | 0.086975 | 5.6992 | 0.073242
2013.2344 | 121.0464 | -0.17853 | 120.9183 | -0.009308 | 6.9784 | 0.064192 | 0.063433 | 0.0048408 | -0.0071821 | -0.002367 | -0.0036011 | 0.0043686 | 0.013751 | 0.0099996 | -0.010258 | 0.027239 | -0.0054282 | 5.5573 | 120.7993 | -0.12817 | 120.7764 | 0.013733 | -0.10529 | -0.13733 | -0.10071 | -0.091553 | -0.059509 | -0.082397 | -0.027466 | -0.10529 | 0.032043 | 0.050354 | -0.11902 | -0.14191 | 0.19226 | 0.041199 | 0.073242 | -0.009155 | 0.022888 | 0.11902 | -121.0098 | -121.0007 | 0.15106 | 0.21057 | 0.073242 | 0.091552 | -0.045777 | 0.14191 | 120.9045 | 0.032043 | -0.022888 | 120.9274 | -0.032044 | 120.9778 | 0.086975 | -121.0464 | -120.9778 | 120.9549 | 0.096131 | 5.7358 | 0.07782
2014.9219 | 121.1655 | -0.13275 | 120.9778 | 0.005951 | 6.9765 | 0.062483 | 0.06087 | 0.0024908 | -0.0086773 | -0.003435 | -0.0066527 | 0.0009506 | 0.016742 | 0.0076498 | -0.0074811 | 0.025744 | -0.003292 | 5.4749 | 120.8313 | -0.082397 | 120.8633 | 0.041199 | -0.082397 | -0.086975 | -0.086975 | -0.1236 | -0.059509 | -0.059509 | 0.013733 | -0.018311 | 0.059509 | 0.050354 | -0.14648 | -0.11444 | 0.17395 | 0.045776 | 0.050354 | -0.004578 | 0 | 0.073242 | -121.1014 | -121.0373 | 0.14648 | 0.19226 | 0.11444 | 0.11902 | 0.041198 | 0.1236 | 120.9457 | 0.073242 | 0 | 120.9137 | -0.064087 | 120.9641 | 0.009155 | -121.0602 | -121.0373 | 120.9961 | 0.073242 | 5.6076 | 0.045776
2016.6562 | 121.2753 | -0.16479 | 120.9915 | -0.009308 | 6.9803 | 0.064405 | 0.06087 | 0.0014228 | -0.0061139 | -0.0038622 | -0.0036011 | 0.0011642 | 0.014605 | 0.016408 | -0.0038495 | 0.027666 | -0.0035056 | 5.5069 | 120.9137 | -0.10986 | 120.9137 | 0.041199 | -0.086975 | -0.10071 | -0.036621 | -0.11444 | -0.050354 | 0.004578 | 0.068665 | 0.009155 | 0.10529 | 0.054932 | -0.07782 | -0.07782 | 0.20599 | 0.064087 | 0.07782 | 0.009155 | 0.022888 | 0.11444 | -121.106 | -120.9869 | 0.23346 | 0.27008 | 0.17395 | 0.15564 | 0.059509 | 0.15106 | 121.0236 | 0.11902 | 0.054932 | 121.0236 | -0.064087 | 121.0785 | 0.050354 | -121.1014 | -121.0419 | 121.0785 | 0.16937 | 5.6717 | 0.12817
2018.4062 | 121.257 | -0.14648 | 121.0373 | -0.0016785 | 6.9776 | 0.064405 | 0.062151 | 0.0050544 | -0.0071821 | -0.003435 | -0.0036011 | 0.0018052 | 0.015033 | 0.015554 | -0.0081219 | 0.027025 | 0.00076681 | 5.4703 | 120.9137 | -0.07782 | 120.9641 | 0.086975 | -0.064087 | -0.064087 | -0.022888 | -0.10986 | -0.036621 | -0.027466 | 0.032043 | 0.004578 | 0.068665 | 0.068664 | -0.1236 | -0.073242 | 0.23346 | 0.082397 | 0.082397 | 0.013733 | 0.013733 | 0.10986 | -121.1472 | -121.0648 | 0.17853 | 0.21515 | 0.15106 | 0.10529 | 0.041199 | 0.16479 | 121.0419 | 0.068664 | 0.009155 | 120.9915 | -0.073242 | 121.0602 | 0.036621 | -121.1151 | -121.0739 | 121.1105 | 0.11902 | 5.6168 | 0.1236
2020.0938 | 121.2753 | -0.16479 | 121.0602 | -0.0016785 | 6.9797 | 0.063764 | 0.060442 | 0.0029182 | -0.0088911 | -0.0025806 | -0.0036011 | 0.000737 | 0.014819 | 0.022817 | -0.0085491 | 0.025316 | -0.0013694 | 5.4611 | 120.9366 | -0.091553 | 120.9595 | 0.032043 | -0.073242 | -0.073242 | -0.082397 | -0.09613 | -0.041199 | -0.045776 | 0 | -0.022888 | 0.059509 | 0.073242 | -0.1236 | -0.10071 | 0.19684 | 0.091553 | 0.091553 | 0.018311 | 0.018311 | 0.1236 | -121.1563 | -121.106 | 0.16479 | 0.2243 | 0.14191 | 0.10071 | 0.018311 | 0.1236 | 121.051 | 0.041199 | -0.004577 | 121.0281 | -0.054931 | 121.1014 | 0.068665 | -121.1517 | -121.1014 | 121.1243 | 0.11902 | 5.6259 | 0.082398
2021.8438 | 118.0115 | -12.5839 | 104.7821 | 0.005951 | 6.9791 | 0.063764 | 0.061724 | 0.00056817 | -0.0091047 | -0.0027942 | -0.00054933 | 0.004155 | 0.015246 | 0.0085044 | -0.0081219 | 0.027453 | -0.0039328 | 3.3463 | 105.0064 | -13.0737 | 105.2353 | -12.616 | -13.1607 | -13.8474 | -0.068665 | -0.07782 | -0.054932 | -0.027466 | 0 | -0.045776 | 0.064087 | -0.48981 | 0.22431 | 0.45319 | -0.032044 | -1.2634 | -0.57678 | -0.77362 | -0.086976 | 12.529 | -104.8599 | -104.8096 | 12.5839 | 12.648 | 12.5381 | 0.11902 | 0.009156 | 0.45776 | 118.309 | 0.054932 | 0.027466 | 118.0801 | -0.022888 | 117.5903 | 12.5061 | -117.8558 | -104.837 | 117.8192 | 12.5565 | 15.9302 | 12.5153
2023.5938 | 120.5658 | -0.17853 | 120.4422 | -0.009308 | 6.9784 | 0.06056 | 0.061724 | 0.00078177 | -0.0082501 | -0.0064258 | -0.00054933 | 0.0018052 | 0.015033 | 0.01299 | -0.010045 | 0.023821 | -0.001583 | 5.4428 | 120.2866 | -0.10986 | 120.3232 | 0.064087 | -0.054932 | -0.086975 | -0.091553 | -0.10071 | -0.045776 | -0.082397 | -0.018311 | -0.064087 | 0.013733 | 0.068665 | -0.15564 | -0.11902 | 0.24261 | 0.091553 | 0.1236 | 0.022888 | 0.054931 | 0.13275 | -120.5429 | -120.5246 | 0.16022 | 0.19226 | 0.11444 | 0.059509 | -0.018311 | 0.17395 | 120.433 | 0.027465 | -0.036621 | 120.3964 | -0.054932 | 120.4651 | 0.07782 | -120.5521 | -120.488 | 120.5017 | 0.096131 | 5.6213 | 0.086975
2025.2812 | 120.6573 | -0.19226 | 120.5292 | -0.009308 | 6.9782 | 0.067182 | 0.06322 | 0.0056952 | -0.0056867 | 0.00041017 | 0.0025025 | 0.0033004 | 0.016742 | 0.0093588 | -0.0064129 | 0.027239 | -0.0017966 | 5.3375 | 120.4651 | -0.14648 | 120.3506 | -0.059509 | -0.16937 | -0.17395 | -0.16479 | -0.068665 | -0.059509 | -0.10529 | -0.073242 | -0.12817 | 0 | 0.045777 | -0.064087 | -0.17853 | 0.13275 | 0.018311 | 0.022888 | -0.027466 | -0.022889 | 0.13275 | -120.5978 | -120.6345 | 0.11902 | 0.19226 | 0.064087 | 0.059509 | -0.068665 | 0.086975 | 120.4971 | -0.013733 | -0.045777 | 120.6116 | -0.009156 | 120.6573 | 0.1236 | -120.6757 | -120.5887 | 120.5429 | 0.086975 | 5.5298 | 0.027466
2026.9688 | 120.8542 | -0.16937 | 120.6116 | -0.009308 | 6.9765 | 0.062269 | 0.060442 | 0.00056817 | -0.0091047 | -0.0042896 | -0.0036011 | -0.0003312 | 0.01546 | 0.01235 | -0.0083355 | 0.027025 | -0.003292 | 5.4291 | 120.4697 | -0.10986 | 120.5338 | 0.082397 | -0.018311 | -0.036621 | -0.018311 | -0.11444 | -0.054932 | 0.004578 | 0.086975 | 0.054932 | 0.10529 | 0.05951 | -0.14191 | -0.07782 | 0.25177 | 0.13275 | 0.15106 | 0.073242 | 0.091552 | 0.11444 | -120.726 | -120.607 | 0.25635 | 0.27466 | 0.22431 | 0.16022 | 0.10986 | 0.19226 | 120.6436 | 0.14191 | 0.05951 | 120.5795 | -0.059509 | 120.639 | 0.054932 | -120.7214 | -120.6665 | 120.7031 | 0.17395 | 5.5985 | 0.15106
2028.7031 | 115.4297 | -37.8525 | 77.3941 | -0.009308 | 6.9803 | 0.064619 | 0.058947 | 0.0031318 | -0.0073957 | -0.00023063 | -0.00054933 | 0.0022324 | 0.013537 | 0.010854 | -0.0087629 | 0.026812 | -0.0017966 | -0.70953 | 78.0258 | -37.2162 | 78.5339 | -36.3693 | -36.9049 | -36.8637 | -0.16937 | -0.041199 | -0.041199 | -0.07782 | -0.050354 | -0.091553 | 0.036621 | 0.63629 | 0.63171 | 1.1398 | 1.4832 | 0.98877 | 0.94757 | 0.35248 | 0.31128 | 37.8113 | -77.4353 | -77.4719 | 37.8021 | 37.8891 | 37.7609 | 0.07782 | -0.050354 | 0.84686 | 115.7501 | -0.009155 | -0.036621 | 115.242 | 0 | 115.8783 | 37.8113 | -114.6103 | -77.4353 | 116.3864 | 37.7747 | 37.1429 | 37.6831
2030.4531 | 120.0302 | -0.20599 | 119.9066 | -0.0016785 | 6.9793 | 0.063764 | 0.061938 | 0.00099557 | -0.0076093 | -0.0025806 | -0.0066527 | 0.0028732 | 0.014605 | 0.013204 | -0.0070539 | 0.025744 | -0.002651 | 5.2368 | 119.8242 | -0.16937 | 119.7098 | -0.068665 | -0.19226 | -0.17395 | -0.14191 | -0.073242 | -0.054932 | -0.068665 | -0.050354 | -0.086975 | 0.027466 | 0.036621 | -0.082397 | -0.19684 | 0.13733 | 0.032044 | 0.013733 | -0.004577 | -0.022888 | 0.15106 | -119.9799 | -119.9753 | 0.15564 | 0.23346 | 0.11902 | 0.082398 | -0.032043 | 0.10071 | 119.8792 | 0.004578 | -0.013733 | 119.9936 | -0.01831 | 120.0302 | 0.13275 | -120.076 | -119.9615 | 119.9158 | 0.13733 | 5.4428 | 0.064087
2032.1875 | 120.2362 | -0.3067 | 119.9844 | -0.009308 | 6.9778 | 0.062269 | 0.061297 | 0.0029182 | -0.0076093 | -0.00087163 | -0.0066527 | 0.0020188 | 0.016742 | 0.012136 | -0.010258 | 0.02553 | -0.0024374 | 5.2826 | 119.8975 | -0.22888 | 119.8151 | -0.13733 | -0.22888 | -0.25177 | -0.16022 | -0.07782 | -0.082397 | -0.13275 | -0.050354 | -0.10986 | -0.009155 | 0.07782 | -0.086975 | -0.16937 | 0.16937 | 0.054932 | 0.07782 | -0.022888 | 0 | 0.2243 | -120.0623 | -120.1172 | 0.25635 | 0.29755 | 0.19684 | 0.073242 | -0.027466 | 0.091553 | 120.0439 | 0.032043 | -0.050354 | 120.1263 | 0.004577 | 120.2042 | 0.22888 | -120.2133 | -120.0668 | 120.1218 | 0.17395 | 5.5893 | 0.14648
2033.9219 | 120.4376 | -0.46692 | 119.8334 | -0.009308 | 6.9761 | 0.064192 | 0.061297 | -0.00049983 | -0.0063275 | -0.003435 | -0.0036011 | -0.0001174 | 0.01781 | 0.013845 | -0.0087629 | 0.02553 | -0.0039328 | 5.1636 | 119.7281 | -0.39825 | 119.371 | -0.29297 | -0.31586 | -0.52643 | -0.10071 | -0.11444 | -0.041199 | -0.059509 | 0 | -0.027466 | 0.050354 | 0.068665 | -0.10529 | -0.46234 | 0.17395 | -0.059509 | 0.15106 | -0.12817 | 0.082397 | 0.42572 | -119.9478 | -119.8929 | 0.46692 | 0.51727 | 0.43945 | 0.091553 | 0.013733 | 0.10529 | 119.7693 | 0.041199 | -0.01831 | 120.1263 | -0.073242 | 120.195 | 0.35248 | -120.2316 | -119.8746 | 119.838 | 0.40741 | 5.6305 | 0.36621
2035.6719 | 120.3461 | -0.26093 | 120.2362 | -0.0016785 | 6.9782 | 0.064192 | 0.060442 | 0.003559 | -0.0071821 | -0.0025806 | -0.00054933 | 0.0037278 | 0.013324 | 0.0027364 | -0.0064129 | 0.025957 | -0.0045736 | 5.4337 | 120.1172 | -0.14648 | 120.1447 | 0.027466 | -0.15564 | -0.13733 | -0.068665 | -0.082397 | -0.045776 | -0.054932 | -0.009155 | -0.059509 | 0.032043 | 0.11444 | -0.11902 | -0.091553 | 0.28839 | 0.1236 | 0.10529 | 0.009155 | -0.009156 | 0.21515 | -120.3186 | -120.2911 | 0.25177 | 0.29297 | 0.20142 | 0.077819 | -0.013733 | 0.17395 | 120.2911 | 0.036621 | -0.009156 | 120.2637 | -0.036621 | 120.3781 | 0.17853 | -120.3827 | -120.282 | 120.4056 | 0.20599 | 5.6946 | 0.19226
2037.3438 | 119.6732 | -2.7054 | 116.9678 | -0.0016785 | 6.9765 | 0.063978 | 0.058947 | -0.00049983 | -0.0073957 | -0.003435 | -0.0036011 | 0.002446 | 0.014392 | 0.019185 | -0.0089765 | 0.027666 | -0.0017966 | 5.1682 | 116.2994 | -2.6917 | 117.2653 | -2.6642 | -2.5726 | -1.973 | 0.009155 | -0.10986 | -0.032043 | 0.004578 | 0.10986 | 0.068665 | 0.10071 | 0.013733 | -0.66833 | 0.29755 | 0.041198 | 0.73242 | 0.13275 | 0.71869 | 0.11902 | 2.6733 | -117.0776 | -116.9632 | 2.8152 | 2.8061 | 2.774 | 0.13275 | 0.10071 | 0.027465 | 119.957 | 0.14191 | 0.036621 | 118.9911 | -0.07782 | 119.0048 | 2.5955 | -119.6594 | -116.9998 | 119.9707 | 2.71 | 7.8735 | 2.7145
2039.0781 | 120.2637 | -0.18768 | 120.0806 | -0.0016785 | 6.9786 | 0.063337 | 0.061297 | 0.00185 | -0.0059003 | -0.003435 | -0.00054933 | 0.0056504 | 0.014605 | 0.01235 | -0.0047039 | 0.026598 | -0.00094199 | 5.246 | 119.9844 | -0.10986 | 119.8883 | -0.018311 | -0.14648 | -0.13733 | -0.10986 | -0.082397 | -0.050354 | -0.045776 | -0.009155 | -0.050354 | 0.059509 | 0.07782 | -0.09613 | -0.19226 | 0.16937 | 0.050354 | 0.041199 | -0.027466 | -0.036621 | 0.13733 | -120.163 | -120.1263 | 0.17853 | 0.24719 | 0.13733 | 0.10986 | 0 | 0.091552 | 119.9982 | 0.041199 | 0.004578 | 120.0943 | -0.032043 | 120.1721 | 0.10529 | -120.1904 | -120.1309 | 120.076 | 0.14191 | 5.4337 | 0.07782
2040.8281 | 120.2728 | -0.21515 | 120.1859 | -0.009308 | 6.9791 | 0.061842 | 0.058093 | -0.0041314 | -0.0084637 | -0.0021532 | -0.0036011 | 0.0015914 | 0.016314 | 0.010213 | -0.010258 | 0.023821 | -0.0058554 | 5.2734 | 120.0668 | -0.14191 | 120.0073 | -0.018311 | -0.11902 | -0.13275 | -0.16022 | -0.09613 | -0.068665 | -0.13733 | -0.045776 | -0.07782 | 0 | 0.073242 | -0.11902 | -0.17853 | 0.19684 | 0.082398 | 0.09613 | 0.009156 | 0.022888 | 0.14648 | -120.282 | -120.3232 | 0.16937 | 0.21515 | 0.13733 | 0.068665 | -0.009155 | 0.1236 | 120.1492 | 0.022889 | -0.068664 | 120.2087 | -0.027465 | 120.282 | 0.11902 | -120.3278 | -120.2545 | 120.2225 | 0.07782 | 5.4886 | 0.054932
2042.5156 | 120.3506 | -0.20142 | 120.2728 | 0.01358 | 6.9784 | 0.060987 | 0.063433 | -0.00092703 | -0.0065411 | -0.0025806 | 0.0055543 | 0.0039414 | 0.015887 | 0.008718 | -0.0098309 | 0.025103 | -0.002651 | 5.246 | 120.1584 | -0.15106 | 120.0439 | -0.036621 | -0.13733 | -0.14648 | -0.17853 | -0.059509 | -0.086975 | -0.11444 | -0.050354 | -0.082397 | 0 | 0.050354 | -0.11444 | -0.22888 | 0.1648 | 0.054932 | 0.064087 | 0.004578 | 0.013733 | 0.11444 | -120.3323 | -120.3873 | 0.15106 | 0.20142 | 0.11902 | 0.086975 | 0.004578 | 0.11444 | 120.195 | 0.036621 | -0.027466 | 120.3094 | 0.027466 | 120.3598 | 0.14191 | -120.4239 | -120.3598 | 120.2454 | 0.086975 | 5.4474 | 0.022888
2044.25 | 120.4559 | -0.1831 | 120.2637 | -0.0016785 | 6.9748 | 0.064192 | 0.06087 | -0.001568 | -0.0069683 | -0.002367 | -0.0036011 | 0.000737 | 0.016528 | 0.017263 | -0.0057721 | 0.027453 | -0.0039328 | 5.3055 | 120.1813 | -0.10529 | 120.1401 | 0.022888 | -0.082397 | -0.091553 | -0.086975 | -0.11444 | -0.050354 | -0.050354 | 0.018311 | -0.018311 | 0.054932 | 0.077819 | -0.082398 | -0.1236 | 0.20599 | 0.091552 | 0.10071 | 0.013733 | 0.022889 | 0.13275 | -120.3781 | -120.314 | 0.20142 | 0.23804 | 0.16479 | 0.10529 | 0.032043 | 0.12817 | 120.2454 | 0.068665 | 0 | 120.2866 | -0.064087 | 120.3644 | 0.068664 | -120.369 | -120.314 | 120.3232 | 0.13275 | 5.4886 | 0.09613
2045.9844 | 120.4468 | -0.17395 | 120.2362 | -0.009308 | 6.9776 | 0.063123 | 0.062365 | -0.00028623 | -0.0073957 | -0.0047168 | -0.00054933 | 0.0015914 | 0.016101 | 0.013418 | -0.0064129 | 0.025316 | -0.002651 | 5.3192 | 120.1218 | -0.09613 | 120.1309 | 0.032043 | -0.082397 | -0.086975 | -0.10529 | -0.10986 | -0.064087 | -0.059509 | 0.013733 | -0.018311 | 0.059509 | 0.07782 | -0.11444 | -0.10529 | 0.20599 | 0.086975 | 0.091553 | 0.009155 | 0.013733 | 0.10986 | -120.3461 | -120.2957 | 0.18768 | 0.23346 | 0.15564 | 0.1236 | 0.045776 | 0.12817 | 120.2271 | 0.07782 | 0.004578 | 120.2179 | -0.045776 | 120.2957 | 0.064087 | -120.3323 | -120.3003 | 120.3049 | 0.11444 | 5.4932 | 0.068664
2047.7188 | 120.5429 | -0.14191 | 120.2682 | -0.009308 | 6.9765 | 0.06056 | 0.062151 | -0.0022088 | -0.0078229 | -0.0021532 | -0.00054933 | 9.6204e-05 | 0.016528 | 0.016622 | -0.0068403 | 0.026171 | -0.0013694 | 5.3284 | 120.1538 | -0.091553 | 120.2591 | 0.12817 | -0.013733 | -0.027466 | -0.009155 | -0.11444 | -0.041199 | 0.004578 | 0.091553 | 0.045776 | 0.10986 | 0.050354 | -0.11444 | -0.009156 | 0.27008 | 0.11444 | 0.12817 | 0.064087 | 0.07782 | 0.10071 | -120.3827 | -120.2637 | 0.23346 | 0.25177 | 0.18768 | 0.15106 | 0.086975 | 0.21973 | 120.3506 | 0.13275 | 0.045777 | 120.2454 | -0.073242 | 120.2957 | 0.027466 | -120.3598 | -120.3094 | 120.401 | 0.14649 | 5.4703 | 0.13275
2049.4062 | 120.4742 | -0.19226 | 120.3186 | -0.0016785 | 6.9782 | 0.065046 | 0.062579 | 0.0014228 | -0.0084637 | -0.0019396 | -0.00054933 | 0.0039414 | 0.013751 | 0.0061544 | -0.0072675 | 0.026385 | -0.002651 | 5.3604 | 120.2637 | -0.11444 | 120.1996 | 0.013733 | -0.11902 | -0.13275 | -0.10529 | -0.10071 | -0.054932 | -0.07782 | -0.027466 | -0.10071 | 0.018311 | 0.07782 | -0.054932 | -0.11902 | 0.20599 | 0.05951 | 0.073242 | -0.01831 | -0.004578 | 0.13733 | -120.4193 | -120.3964 | 0.16479 | 0.21057 | 0.091553 | 0.073243 | -0.045776 | 0.12817 | 120.314 | 0.027466 | -0.022888 | 120.3781 | -0.045776 | 120.4559 | 0.091553 | -120.433 | -120.3735 | 120.3918 | 0.11444 | 5.5527 | 0.086975
2051.1562 | 120.4834 | -0.21057 | 120.3506 | -0.0016785 | 6.9765 | 0.06526 | 0.062365 | 0.0061224 | -0.0056867 | -0.0042896 | -0.0036011 | 0.0028732 | 0.015033 | 0.012136 | -0.0074811 | 0.025957 | 0.00012601 | 5.3009 | 120.3003 | -0.13733 | 120.1813 | -0.082397 | -0.18768 | -0.19226 | -0.21057 | -0.07782 | -0.082397 | -0.10986 | -0.07782 | -0.11902 | 0.013733 | 0.073242 | -0.050354 | -0.16937 | 0.12817 | 0.01831 | 0.022888 | -0.054932 | -0.050354 | 0.12817 | -120.4285 | -120.4605 | 0.13275 | 0.2243 | 0.091552 | 0.09613 | -0.036622 | 0.054932 | 120.3186 | 0.004577 | -0.027466 | 120.4376 | 0.004577 | 120.5109 | 0.13275 | -120.488 | -120.433 | 120.3918 | 0.10071 | 5.5115 | 0
2052.8906 | 120.5154 | -0.1831 | 120.3827 | -0.0016785 | 6.9767 | 0.065473 | 0.061511 | 0.005268 | -0.0071821 | -0.0019396 | -0.00054933 | 0.003514 | 0.013537 | 0.010641 | -0.010686 | 0.025316 | -0.0022238 | 5.3329 | 120.2728 | -0.11444 | 120.2454 | 0.018311 | -0.091553 | -0.10986 | -0.13733 | -0.082397 | -0.068665 | -0.10071 | -0.032043 | -0.086975 | 0 | 0.068664 | -0.10986 | -0.13733 | 0.20142 | 0.073242 | 0.091552 | 0.004578 | 0.022888 | 0.11444 | -120.4651 | -120.4834 | 0.15106 | 0.1831 | 0.09613 | 0.068665 | -0.01831 | 0.13275 | 120.3598 | 0.036622 | -0.032043 | 120.3873 | -0.013732 | 120.4559 | 0.10071 | -120.4971 | -120.4514 | 120.4285 | 0.082397 | 5.5161 | 0.045776
2054.5781 | 120.6482 | -0.14648 | 120.3735 | -0.0016785 | 6.9763 | 0.06291 | 0.062365 | -0.00049983 | -0.0080365 | -0.0019396 | -0.0066527 | 0.0009506 | 0.013751 | 0.0099996 | -0.0055585 | 0.027453 | -0.003292 | 5.3238 | 120.282 | -0.086975 | 120.3369 | 0.09613 | -0.045776 | -0.050354 | 0 | -0.12817 | -0.013733 | 0.027466 | 0.059509 | 0.022888 | 0.12817 | 0.059509 | -0.091553 | -0.036621 | 0.24261 | 0.09613 | 0.10071 | 0.036621 | 0.041199 | 0.13275 | -120.5017 | -120.3461 | 0.20599 | 0.27466 | 0.16937 | 0.14191 | 0.036621 | 0.1831 | 120.4239 | 0.073242 | 0.041199 | 120.369 | -0.11444 | 120.4285 | 0.01831 | -120.4605 | -120.3873 | 120.4834 | 0.17395 | 5.4703 | 0.14648
2056.3281 | 120.6665 | -0.13275 | 120.3781 | -0.009308 | 6.9769 | 0.065687 | 0.062365 | 0.0033454 | -0.0071821 | -0.0010852 | -0.0036011 | 0.0043686 | 0.016314 | 0.018117 | -0.0053449 | 0.026385 | -0.00051479 | 5.2643 | 120.2499 | -0.11902 | 120.3598 | 0.10986 | -0.064087 | -0.054932 | 0 | -0.11902 | -0.022888 | 0.041199 | 0.082397 | 0.032043 | 0.11444 | 0.013732 | -0.12817 | -0.018311 | 0.24261 | 0.077819 | 0.068664 | 0.064087 | 0.054932 | 0.10986 | -120.4971 | -120.3369 | 0.21515 | 0.24719 | 0.16479 | 0.13733 | 0.054931 | 0.22888 | 120.4788 | 0.10528 | 0.064087 | 120.369 | -0.096131 | 120.3827 | 0.013732 | -120.4971 | -120.401 | 120.4926 | 0.17395 | 5.397 | 0.13275
2058.0156 | 120.6573 | -0.16022 | 120.4239 | 0.005951 | 6.9759 | 0.062483 | 0.061938 | -0.00071343 | -0.0061139 | -0.0012988 | -0.00054933 | -0.0001174 | 0.015033 | 0.015981 | -0.0083355 | 0.027666 | 0.0031168 | 5.2368 | 120.3186 | -0.10529 | 120.3369 | 0.054932 | -0.073242 | -0.086975 | -0.054932 | -0.10986 | -0.041199 | -0.036621 | 0.009155 | -0.013733 | 0.064087 | 0.054931 | -0.10529 | -0.086975 | 0.21515 | 0.073242 | 0.086975 | 0.018311 | 0.032044 | 0.11902 | -120.5338 | -120.4605 | 0.16937 | 0.2243 | 0.14648 | 0.10529 | 0.027466 | 0.16022 | 120.4422 | 0.050354 | 0.004578 | 120.4239 | -0.068664 | 120.4788 | 0.050354 | -120.5292 | -120.4651 | 120.4971 | 0.1236 | 5.397 | 0.10528
2059.7656 | 120.6573 | -0.16937 | 120.4514 | 0.005951 | 6.9793 | 0.065046 | 0.062151 | 0.00078177 | -0.0065411 | -0.0021532 | -0.00054933 | 0.0028732 | 0.013965 | 0.013845 | -0.0081219 | 0.027666 | 0.00076681 | 5.278 | 120.3644 | -0.082397 | 120.3735 | 0.10986 | -0.050354 | -0.059509 | 0.004578 | -0.10986 | -0.036621 | -0.022888 | 0.041199 | 0.004578 | 0.086975 | 0.086976 | -0.086975 | -0.07782 | 0.27924 | 0.10986 | 0.11902 | 0.022888 | 0.032043 | 0.13275 | -120.5612 | -120.4742 | 0.21057 | 0.25635 | 0.17395 | 0.1236 | 0.041199 | 0.19226 | 120.4559 | 0.07782 | 0.013733 | 120.4468 | -0.073242 | 120.5338 | 0.05951 | -120.5338 | -120.488 | 120.5429 | 0.14649 | 5.4474 | 0.17395
2061.4531 | 120.7077 | -0.14191 | 120.4651 | 0.005951 | 6.9795 | 0.064405 | 0.063006 | -0.00092703 | -0.0084637 | -0.00023063 | 0.0025025 | -0.0003312 | 0.015246 | 0.012563 | -0.0064129 | 0.02788 | -0.0013694 | 5.1819 | 120.3781 | -0.10071 | 120.3598 | 0.027466 | -0.07782 | -0.086975 | -0.068665 | -0.10071 | -0.045776 | -0.032043 | 0.018311 | 0 | 0.073242 | 0.041199 | -0.086975 | -0.10529 | 0.16937 | 0.054932 | 0.064087 | 0.013733 | 0.022888 | 0.096131 | -120.5658 | -120.4971 | 0.16022 | 0.21515 | 0.14191 | 0.11902 | 0.045776 | 0.12817 | 120.4605 | 0.064087 | 0.013733 | 120.4788 | -0.054932 | 120.52 | 0.041199 | -120.5658 | -120.5109 | 120.5017 | 0.10986 | 5.3238 | 0.073242
2063.1875 | 120.7123 | -0.16022 | 120.488 | -0.0016785 | 6.9774 | 0.064619 | 0.062365 | -0.00092703 | -0.0071821 | -0.0070666 | -0.00054933 | 0.0011642 | 0.017383 | 0.009786 | -0.0072675 | 0.027239 | -0.0058554 | 5.2689 | 120.369 | -0.086975 | 120.4102 | 0.09613 | -0.054932 | -0.073242 | -0.027466 | -0.10071 | -0.045776 | -0.022888 | 0.022888 | -0.022888 | 0.073242 | 0.073242 | -0.11902 | -0.07782 | 0.25635 | 0.086975 | 0.10528 | 0.013733 | 0.032043 | 0.11444 | -120.5887 | -120.5109 | 0.1831 | 0.23346 | 0.13733 | 0.11902 | 0.022888 | 0.1831 | 120.4971 | 0.068664 | 0.022888 | 120.4559 | -0.054932 | 120.5292 | 0.059509 | -120.575 | -120.5338 | 120.5704 | 0.13733 | 5.4291 | 0.13275
2064.9219 | 120.7626 | -0.13275 | 120.4971 | -0.0016785 | 6.9789 | 0.064405 | 0.061083 | 0.0048408 | -0.0067547 | -0.0049304 | -0.00054933 | 0.0030868 | 0.017383 | 0.01534 | -0.0057721 | 0.026385 | -0.007778 | 5.246 | 120.4102 | -0.082397 | 120.4559 | 0.086975 | -0.068665 | -0.064087 | 0.004578 | -0.13275 | -0.036621 | 0.022888 | 0.068665 | 0.013733 | 0.11902 | 0.050354 | -0.086975 | -0.041198 | 0.21973 | 0.068664 | 0.064086 | 0.01831 | 0.013732 | 0.09613 | -120.6299 | -120.4742 | 0.20142 | 0.25177 | 0.14648 | 0.15564 | 0.050354 | 0.16937 | 120.5383 | 0.10529 | 0.059509 | 120.4926 | -0.09613 | 120.5429 | 0 | -120.5795 | -120.5338 | 120.5887 | 0.15564 | 5.3787 | 0.13733
2066.6719 | 120.6757 | -0.17853 | 120.5154 | -0.0016785 | 6.9803 | 0.064405 | 0.063647 | 0.0056952 | -0.0086773 | -0.0010852 | 0.0025025 | 0.0033004 | 0.016101 | 0.015554 | -0.0098309 | 0.026171 | -0.0022238 | 5.246 | 120.433 | -0.1236 | 120.401 | 0.041199 | -0.086975 | -0.10529 | -0.064087 | -0.07782 | -0.050354 | -0.045776 | 0 | -0.041199 | 0.059509 | 0.054932 | -0.082398 | -0.11444 | 0.21973 | 0.073242 | 0.091553 | 0.01831 | 0.036621 | 0.12817 | -120.5933 | -120.5612 | 0.17853 | 0.23804 | 0.13733 | 0.10986 | 0.009155 | 0.16479 | 120.5246 | 0.050354 | 0.004578 | 120.5566 | -0.027466 | 120.6116 | 0.10071 | -120.639 | -120.5658 | 120.5795 | 0.13275 | 5.4245 | 0.11444
2068.4219 | 120.7077 | -0.19226 | 120.5658 | 0.005951 | 6.9769 | 0.062269 | 0.06322 | -0.0011408 | -0.0088911 | -0.00065803 | 0.0055543 | 0.0033004 | 0.013751 | 0.01534 | -0.012822 | 0.025957 | -0.0039328 | 5.2551 | 120.4697 | -0.13275 | 120.3644 | -0.032043 | -0.10529 | -0.13733 | -0.14648 | -0.068665 | -0.082397 | -0.086975 | -0.013733 | -0.073242 | 0.032043 | 0.05951 | -0.09613 | -0.20142 | 0.16022 | 0.054932 | 0.086975 | -0.004578 | 0.027465 | 0.10986 | -120.6345 | -120.6528 | 0.17853 | 0.2243 | 0.11902 | 0.11444 | 0.009155 | 0.10071 | 120.4971 | 0.068664 | -0.004578 | 120.6024 | 0.013732 | 120.6619 | 0.1236 | -120.6985 | -120.6482 | 120.5566 | 0.10529 | 5.4474 | 0.045777
2070.1094 | 120.694 | -0.17853 | 120.5383 | -0.0016785 | 6.9782 | 0.064192 | 0.063006 | 0.003559 | -0.0082501 | -0.0025806 | -0.00054933 | 0.0039414 | 0.016955 | 0.01299 | -0.0072675 | 0.025957 | -0.005001 | 5.2277 | 120.4422 | -0.14191 | 120.4056 | 0.022888 | -0.11444 | -0.12817 | -0.086975 | -0.082397 | -0.054932 | -0.07782 | -0.032043 | -0.07782 | 0.018311 | 0.036621 | -0.09613 | -0.13275 | 0.20142 | 0.050354 | 0.064087 | 0.013733 | 0.027466 | 0.1236 | -120.6207 | -120.6162 | 0.14648 | 0.19684 | 0.10071 | 0.073243 | -0.022888 | 0.16479 | 120.5475 | 0.022889 | -0.022888 | 120.5841 | -0.027465 | 120.6207 | 0.096131 | -120.6802 | -120.5933 | 120.5841 | 0.10071 | 5.4062 | 0.091553
2071.875 | 120.7031 | -0.20142 | 120.5475 | -0.016937 | 6.9801 | 0.062269 | 0.05852 | 0.0024908 | -0.0069683 | -0.0010852 | 0.0055543 | 0.0047958 | 0.016314 | 0.017263 | -0.010258 | 0.024035 | -0.0039328 | 5.2002 | 120.5063 | -0.13733 | 120.369 | -0.032043 | -0.13275 | -0.15106 | -0.1831 | -0.064087 | -0.07782 | -0.10529 | -0.068665 | -0.091553 | 0 | 0.064087 | -0.041198 | -0.17853 | 0.16937 | 0.050354 | 0.068665 | -0.013733 | 0.004578 | 0.1236 | -120.6116 | -120.6528 | 0.13275 | 0.20142 | 0.10986 | 0.07782 | -0.013733 | 0.10529 | 120.5063 | 0.009155 | -0.027466 | 120.6436 | 0.013733 | 120.7077 | 0.13733 | -120.6848 | -120.6253 | 120.5704 | 0.09613 | 5.4016 | 0.018311
2073.5469 | 120.3094 | -0.19226 | 120.2087 | -0.016937 | 6.9803 | 0.063764 | 0.062792 | 0.0027044 | -0.0063275 | -0.0019396 | -0.00054933 | 0.0026596 | 0.015887 | 0.012136 | -0.0076947 | 0.02553 | -0.0037192 | 5.04 | 120.1218 | -0.12817 | 120.0073 | -0.082397 | -0.19226 | -0.1831 | -0.20142 | -0.091553 | -0.064087 | -0.10071 | -0.073242 | -0.11902 | 0.009155 | 0.064087 | -0.086975 | -0.20142 | 0.10986 | 0.009156 | 0 | -0.054931 | -0.064087 | 0.12817 | -120.3003 | -120.3094 | 0.11902 | 0.20142 | 0.073242 | 0.073242 | -0.054932 | 0.045777 | 120.1355 | -0.009155 | -0.036621 | 120.2499 | -0.027466 | 120.314 | 0.10071 | -120.3369 | -120.2728 | 120.1996 | 0.091553 | 5.2322 | -0.009155
2075.2969 | 120.7214 | -0.14191 | 120.4559 | -0.0016785 | 6.9774 | 0.065473 | 0.061511 | 0.0012092 | -0.0056867 | 0.00062377 | -0.0036011 | 0.0013778 | 0.01311 | 0.011068 | -0.0044903 | 0.02788 | -0.0028646 | 5.1453 | 120.4056 | -0.082397 | 120.4376 | 0.10529 | -0.032043 | -0.041199 | -0.004578 | -0.10529 | -0.036621 | 0.018311 | 0.073242 | 0.027466 | 0.10529 | 0.05951 | -0.050354 | -0.018311 | 0.24719 | 0.10071 | 0.10986 | 0.041198 | 0.050354 | 0.10529 | -120.5612 | -120.4376 | 0.21515 | 0.24719 | 0.16937 | 0.14191 | 0.064087 | 0.18768 | 120.52 | 0.10986 | 0.054932 | 120.488 | -0.068665 | 120.5475 | 0.036621 | -120.5383 | -120.4926 | 120.5795 | 0.16022 | 5.2872 | 0.13733
2076.9844 | 120.7443 | -0.16479 | 120.5338 | 0.005951 | 6.9793 | 0.063764 | 0.062579 | 0.0024908 | -0.0061139 | -0.0012988 | 0.0025025 | 0.0013778 | 0.014605 | 0.011709 | -0.0049175 | 0.02788 | -0.0090598 | 5.1819 | 120.4422 | -0.091553 | 120.4559 | 0.10529 | -0.050354 | -0.050354 | -0.009155 | -0.11902 | -0.032043 | -0.004578 | 0.036621 | 0 | 0.086975 | 0.073242 | -0.091552 | -0.077819 | 0.27008 | 0.11444 | 0.11444 | 0.041199 | 0.041199 | 0.13275 | -120.6528 | -120.5383 | 0.20142 | 0.25177 | 0.16479 | 0.11902 | 0.032043 | 0.19684 | 120.5475 | 0.068664 | 0.027465 | 120.5338 | -0.086976 | 120.607 | 0.045776 | -120.6253 | -120.5658 | 120.6207 | 0.16022 | 5.3467 | 0.15564
2078.7188 | 120.7993 | -0.14648 | 120.5338 | -0.0016785 | 6.9782 | 0.064192 | 0.060656 | -0.00028623 | -0.0065411 | -0.0032214 | 0.0025025 | -0.0005448 | 0.014178 | 0.010641 | -0.0057721 | 0.027666 | -0.0028646 | 5.1773 | 120.4559 | -0.10529 | 120.4651 | 0.073242 | -0.059509 | -0.059509 | -0.013733 | -0.1236 | -0.036621 | 0.032043 | 0.059509 | 0.013733 | 0.11902 | 0.041198 | -0.077819 | -0.068664 | 0.21973 | 0.086975 | 0.086975 | 0.045777 | 0.045777 | 0.10986 | -120.6573 | -120.5017 | 0.20599 | 0.2655 | 0.16022 | 0.15564 | 0.050354 | 0.17853 | 120.5704 | 0.09613 | 0.068664 | 120.5612 | -0.086975 | 120.6024 | 0.022888 | -120.639 | -120.5704 | 120.6116 | 0.17853 | 5.3238 | 0.13275
2080.4062 | 120.6848 | -0.20599 | 120.5841 | -0.009308 | 6.9793 | 0.06291 | 0.062151 | 0.00014097 | -0.0080365 | -0.00023063 | 0.0055543 | 0.0020188 | 0.016101 | 0.0055136 | -0.012395 | 0.02553 | -0.0024374 | 5.1682 | 120.5246 | -0.13733 | 120.3964 | -0.027466 | -0.11902 | -0.14648 | -0.17395 | -0.045776 | -0.091553 | -0.1236 | -0.059509 | -0.10529 | -0.004578 | 0.068665 | -0.059509 | -0.18768 | 0.17853 | 0.05951 | 0.086975 | -0.009155 | 0.01831 | 0.11444 | -120.6299 | -120.7077 | 0.14649 | 0.20142 | 0.10071 | 0.086975 | -0.013733 | 0.10986 | 120.5338 | 0.032044 | -0.032043 | 120.6619 | 0.045777 | 120.7306 | 0.16022 | -120.7214 | -120.6757 | 120.6024 | 0.082398 | 5.3741 | 0.032044
2082.1562 | 120.7214 | -0.21515 | 120.6207 | 0.01358 | 6.9776 | 0.063551 | 0.061724 | 0.0012092 | -0.0063275 | -0.0021532 | -0.00054933 | 0.0037278 | 0.013324 | 0.0089316 | -0.010258 | 0.026171 | -0.0039328 | 5.159 | 120.5063 | -0.11902 | 120.4147 | -0.004578 | -0.11902 | -0.13275 | -0.15564 | -0.068665 | -0.068665 | -0.11444 | -0.041199 | -0.091553 | 0.009155 | 0.09613 | -0.11444 | -0.20599 | 0.21057 | 0.082398 | 0.09613 | -0.013732 | 0 | 0.14648 | -120.6894 | -120.7352 | 0.17395 | 0.2243 | 0.1236 | 0.07782 | -0.022888 | 0.11444 | 120.5338 | 0.027466 | -0.045776 | 120.6253 | 0 | 120.7214 | 0.14648 | -120.7397 | -120.6894 | 120.6299 | 0.10071 | 5.3741 | 0.059509
2083.8906 | 120.7672 | -0.15106 | 120.575 | -0.0016785 | 6.9754 | 0.063978 | 0.059802 | -0.0037042 | -0.0071821 | -0.0010852 | 0.0055543 | 9.6204e-05 | 0.015246 | 0.014486 | -0.0076947 | 0.025957 | -0.0011558 | 5.1956 | 120.4834 | -0.10071 | 120.5338 | 0.11902 | 0 | -0.027466 | 0.036621 | -0.11902 | -0.036621 | 0.018311 | 0.10986 | 0.068665 | 0.11902 | 0.050354 | -0.091553 | -0.041199 | 0.27008 | 0.1236 | 0.15106 | 0.073242 | 0.10071 | 0.11444 | -120.694 | -120.5566 | 0.26093 | 0.27008 | 0.21973 | 0.15564 | 0.10529 | 0.21973 | 120.6345 | 0.14648 | 0.054932 | 120.5841 | -0.082398 | 120.6345 | 0.032043 | -120.6757 | -120.6116 | 120.6848 | 0.16937 | 5.3467 | 0.18768
2085.5781 | 120.7718 | -0.19226 | 120.6299 | 0.01358 | 6.9782 | 0.065687 | 0.064715 | 0.00035457 | -0.0080365 | -0.00087163 | -0.00054933 | 0.0030868 | 0.014819 | -0.001536 | -0.0076947 | 0.027453 | -0.00094199 | 5.127 | 120.5612 | -0.1236 | 120.3873 | -0.07782 | -0.1831 | -0.15106 | -0.16479 | -0.07782 | -0.073242 | -0.082397 | -0.09613 | -0.13275 | 0.009155 | 0.068665 | -0.068665 | -0.24262 | 0.11444 | 0.041199 | 0.009156 | -0.027466 | -0.059509 | 0.11902 | -120.7077 | -120.7123 | 0.096131 | 0.20142 | 0.05951 | 0.082397 | -0.059509 | 0.045776 | 120.5109 | -0.022888 | -0.009155 | 120.6848 | -0.004578 | 120.7535 | 0.11444 | -120.7535 | -120.7031 | 120.5795 | 0.10986 | 5.3192 | 0.027466
2087.3281 | 120.7718 | -0.17853 | 120.639 | -0.0016785 | 6.9791 | 0.064405 | 0.063647 | 0.0022772 | -0.0067547 | -0.0036486 | -0.0036011 | 0.0022324 | 0.016528 | 0.014059 | -0.0057721 | 0.025957 | -0.00051479 | 5.1819 | 120.5566 | -0.10986 | 120.5063 | 0.013733 | -0.11902 | -0.11902 | -0.09613 | -0.086975 | -0.07782 | -0.068665 | -0.032043 | -0.091553 | 0.027466 | 0.068665 | -0.082397 | -0.13275 | 0.19226 | 0.059509 | 0.059509 | -0.009156 | -0.009156 | 0.10071 | -120.726 | -120.7077 | 0.14648 | 0.20599 | 0.086975 | 0.10529 | -0.013733 | 0.1236 | 120.6162 | 0.045777 | 0.009155 | 120.6665 | -0.009155 | 120.7352 | 0.091553 | -120.7489 | -120.7169 | 120.6848 | 0.10986 | 5.3604 | 0.082398
2089.0156 | 120.7672 | -0.20599 | 120.6665 | 0.01358 | 6.9797 | 0.065473 | 0.063006 | 0.0027044 | -0.0067547 | -0.0040758 | 0.0025025 | 0.0020188 | 0.018023 | 0.014699 | -0.0085491 | 0.027239 | -0.0047874 | 5.0629 | 120.5978 | -0.10986 | 120.4285 | -0.073242 | -0.17853 | -0.17853 | -0.1831 | -0.07782 | -0.064087 | -0.10529 | -0.082397 | -0.11902 | 0.013733 | 0.096131 | -0.068665 | -0.23804 | 0.13275 | 0.027466 | 0.027466 | -0.068665 | -0.068665 | 0.14191 | -120.7443 | -120.7718 | 0.1236 | 0.21973 | 0.086975 | 0.07782 | -0.054932 | 0.036621 | 120.5383 | -0.01831 | -0.041199 | 120.7077 | -0.013733 | 120.8038 | 0.12817 | -120.7764 | -120.7306 | 120.6345 | 0.10071 | 5.2689 | 0.022889
2090.7656 | 120.7809 | -0.21057 | 120.6848 | -0.009308 | 6.9786 | 0.062483 | 0.060015 | -0.0034906 | -0.0084637 | -0.001726 | -0.0036011 | 0.0037278 | 0.011828 | 0.014699 | -0.011326 | 0.024462 | -0.0062826 | 5.0858 | 120.5795 | -0.12817 | 120.4605 | -0.036621 | -0.1236 | -0.15564 | -0.16479 | -0.07782 | -0.064087 | -0.11444 | -0.054932 | -0.10071 | -0.004578 | 0.082397 | -0.10529 | -0.2243 | 0.17395 | 0.054931 | 0.086975 | -0.027466 | 0.004578 | 0.14648 | -120.7626 | -120.7993 | 0.15564 | 0.20599 | 0.10986 | 0.059509 | -0.036621 | 0.091553 | 120.5887 | 0.009155 | -0.050354 | 120.7077 | -0.013733 | 120.7901 | 0.13275 | -120.813 | -120.7489 | 120.6711 | 0.09613 | 5.2963 | 0.045776
2092.4375 | 120.7993 | -0.20599 | 120.6985 | -0.0016785 | 6.9786 | 0.063764 | 0.063647 | 0.0041998 | -0.0071821 | -0.00044443 | -0.0036011 | 0.002446 | 0.015033 | 0.013204 | -0.0064129 | 0.02553 | -0.001583 | 5.0812 | 120.607 | -0.11902 | 120.4971 | -0.027466 | -0.16937 | -0.16022 | -0.16022 | -0.082397 | -0.054932 | -0.10071 | -0.073242 | -0.1236 | 0.009155 | 0.086975 | -0.091552 | -0.20142 | 0.17853 | 0.045777 | 0.036621 | -0.041198 | -0.050354 | 0.15106 | -120.7809 | -120.7993 | 0.13275 | 0.21515 | 0.082398 | 0.064087 | -0.068664 | 0.091553 | 120.6161 | -0.01831 | -0.045776 | 120.726 | -0.027465 | 120.813 | 0.1236 | -120.8176 | -120.7535 | 120.7031 | 0.10529 | 5.2872 | 0.045777
2094.1719 | 120.8542 | -0.21057 | 120.6985 | -0.0016785 | 6.9786 | 0.061415 | 0.062151 | 0.0048408 | -0.0078229 | 0.001051 | 0.0086061 | 0.0030868 | 0.013751 | 0.0038046 | -0.010258 | 0.024248 | -0.0020102 | 5.0858 | 120.6024 | -0.12817 | 120.5017 | -0.027466 | -0.11444 | -0.1236 | -0.14191 | -0.082397 | -0.054932 | -0.073242 | -0.018311 | -0.068665 | 0.032043 | 0.082397 | -0.09613 | -0.19684 | 0.18311 | 0.086975 | 0.09613 | 0.004578 | 0.013733 | 0.15564 | -120.7809 | -120.7718 | 0.19226 | 0.24261 | 0.14191 | 0.086975 | -0.013733 | 0.10071 | 120.6299 | 0.036621 | -0.01831 | 120.7306 | -0.027465 | 120.813 | 0.12817 | -120.8267 | -120.7535 | 120.7123 | 0.13733 | 5.2963 | 0.068664
2095.9062 | 120.8908 | -0.17853 | 120.694 | -0.0016785 | 6.9784 | 0.06526 | 0.062151 | 0.0044134 | -0.0084637 | -0.0019396 | -0.00054933 | 0.0018052 | 0.015246 | 0.019399 | -0.0066265 | 0.026812 | -0.00436 | 5.1315 | 120.6207 | -0.11902 | 120.575 | 0.041199 | -0.09613 | -0.10071 | -0.073242 | -0.09613 | -0.045776 | -0.045776 | -0.004578 | -0.064087 | 0.054932 | 0.059509 | -0.073242 | -0.11902 | 0.21973 | 0.07782 | 0.082398 | 0.018311 | 0.022889 | 0.13275 | -120.7901 | -120.7397 | 0.17395 | 0.23346 | 0.11444 | 0.10071 | -0.018311 | 0.16022 | 120.694 | 0.041198 | 0 | 120.7397 | -0.050354 | 120.7993 | 0.082398 | -120.813 | -120.7397 | 120.7535 | 0.13275 | 5.3101 | 0.10529
2097.5781 | 120.932 | -0.16479 | 120.6985 | 0.005951 | 6.9769 | 0.065901 | 0.058947 | 0.003559 | -0.0084637 | -0.0040758 | -0.00054933 | 0.000737 | 0.014819 | 0.016622 | -0.0055585 | 0.027239 | -0.0041464 | 5.0125 | 120.6207 | -0.10986 | 120.5795 | 0.050354 | -0.073242 | -0.10986 | -0.073242 | -0.11902 | -0.036621 | -0.045776 | 0.018311 | -0.022888 | 0.059509 | 0.054932 | -0.077819 | -0.11902 | 0.21515 | 0.054932 | 0.091553 | 0 | 0.036621 | 0.12817 | -120.8176 | -120.7443 | 0.18311 | 0.2243 | 0.14191 | 0.09613 | 0.013733 | 0.16022 | 120.6894 | 0.054932 | -0.009155 | 120.7306 | -0.082398 | 120.7855 | 0.045776 | -120.8084 | -120.7352 | 120.7443 | 0.11902 | 5.1773 | 0.091553
2099.3125 | 118.1122 | -23.1949 | 94.3771 | -0.0016785 | 6.978 | 0.063123 | 0.061724 | 0.00078177 | -0.0048321 | -0.0027942 | -0.0036011 | 0.0020188 | 0.014178 | 0.013845 | -0.0059857 | 0.027453 | -0.0035056 | -2.7237 | 94.8853 | -23.5245 | 95.1416 | -23.1766 | -23.5016 | -24.2477 | -0.10529 | -0.073242 | -0.036621 | -0.041199 | -0.009155 | -0.050354 | 0.07782 | -0.32959 | 0.50812 | 0.76447 | 0.01831 | -1.0529 | -0.3067 | -0.72327 | 0.022888 | 23.1583 | -94.4504 | -94.4183 | 23.1857 | 23.2727 | 23.1445 | 0.11444 | -0.013733 | 0.3479 | 118.6661 | 0.027466 | -0.004578 | 118.4097 | -0.036621 | 118.0801 | 23.1216 | -117.9016 | -94.4138 | 118.3365 | 23.1537 | 20.4712 | 23.0896
2101.0469 | 120.9137 | -0.16479 | 120.639 | -0.0016785 | 6.9776 | 0.063337 | 0.062792 | 0.0029182 | -0.0073957 | -0.00087163 | -0.00054933 | 0.0030868 | 0.01311 | 0.014913 | -0.0059857 | 0.026812 | -0.0035056 | 5.0308 | 120.607 | -0.09613 | 120.5566 | 0.050354 | -0.068665 | -0.091553 | -0.036621 | -0.11444 | -0.036621 | 0.022888 | 0.059509 | 0.018311 | 0.12817 | 0.068665 | -0.032043 | -0.082397 | 0.21515 | 0.073242 | 0.09613 | 0.004577 | 0.027465 | 0.12817 | -120.7535 | -120.6162 | 0.2243 | 0.29297 | 0.18311 | 0.1648 | 0.054932 | 0.14648 | 120.6528 | 0.09613 | 0.059509 | 120.7031 | -0.07782 | 120.7718 | 0.050354 | -120.7352 | -120.6757 | 120.7214 | 0.18768 | 5.1956 | 0.12817
2102.7812 | 120.9137 | -0.15106 | 120.6985 | -0.0016785 | 6.9769 | 0.06526 | 0.06087 | 0.0033454 | -0.0067547 | -0.0021532 | -0.00054933 | 0.0022324 | 0.016742 | 0.018117 | -0.0059857 | 0.028094 | -0.0030784 | 4.9988 | 120.5978 | -0.082397 | 120.6299 | 0.10071 | -0.064087 | -0.054932 | -0.009155 | -0.12817 | -0.045776 | 0 | 0.059509 | 0.009155 | 0.10071 | 0.068665 | -0.10071 | -0.068664 | 0.25177 | 0.09613 | 0.086975 | 0.027465 | 0.01831 | 0.10529 | -120.8267 | -120.6985 | 0.21057 | 0.25177 | 0.16022 | 0.14648 | 0.054931 | 0.18311 | 120.7123 | 0.10528 | 0.045776 | 120.6802 | -0.082398 | 120.7489 | 0.022888 | -120.7809 | -120.7443 | 120.7809 | 0.15106 | 5.1498 | 0.14191
2104.4531 | 120.845 | -0.21057 | 120.7306 | -0.009308 | 6.9786 | 0.062055 | 0.060442 | 0.00056817 | -0.0061139 | -0.003435 | -0.0036011 | 0.0013778 | 0.013537 | 0.0091452 | -0.012822 | 0.023607 | -0.005001 | 5.0491 | 120.6162 | -0.12817 | 120.5521 | -0.013733 | -0.1236 | -0.13275 | -0.15564 | -0.073242 | -0.068665 | -0.11444 | -0.050354 | -0.07782 | -0.013733 | 0.082397 | -0.11444 | -0.17853 | 0.19684 | 0.07782 | 0.086975 | -0.004577 | 0.004578 | 0.14191 | -120.8038 | -120.845 | 0.16022 | 0.19684 | 0.13275 | 0.054932 | -0.009155 | 0.11444 | 120.6802 | 0.018311 | -0.045776 | 120.7443 | -0.004577 | 120.8267 | 0.13733 | -120.8588 | -120.7993 | 120.7626 | 0.09613 | 5.2597 | 0.054931
2106.2031 | 120.8496 | -0.19226 | 120.7626 | -0.0016785 | 6.9776 | 0.064832 | 0.062151 | 0.00185 | -0.0069683 | -0.0015124 | -0.0036011 | 0.002446 | 0.014819 | 0.01235 | -0.0079083 | 0.027239 | -0.0041464 | 5.0034 | 120.6802 | -0.11902 | 120.5566 | -0.054932 | -0.16479 | -0.16937 | -0.1831 | -0.059509 | -0.050354 | -0.10986 | -0.068665 | -0.13275 | 0.009155 | 0.073242 | -0.082397 | -0.20599 | 0.13733 | 0.022888 | 0.027466 | -0.050354 | -0.045776 | 0.14191 | -120.8221 | -120.8725 | 0.1236 | 0.20142 | 0.05951 | 0.059509 | -0.082397 | 0.064087 | 120.6757 | -0.018311 | -0.059509 | 120.7993 | -0.009155 | 120.8725 | 0.13275 | -120.8817 | -120.813 | 120.7489 | 0.082398 | 5.1956 | 0.009156
2107.9531 | 120.8679 | -0.18768 | 120.7626 | -0.0016785 | 6.9782 | 0.065046 | 0.062151 | 0.0071906 | -0.0084637 | -0.0015124 | 0.0055543 | 0.002446 | 0.017383 | 0.0067954 | -0.0068403 | 0.026598 | -0.001583 | 4.9759 | 120.7077 | -0.13275 | 120.5566 | -0.073242 | -0.17853 | -0.16479 | -0.16022 | -0.07782 | -0.07782 | -0.09613 | -0.07782 | -0.11444 | 0.009155 | 0.054932 | -0.054931 | -0.20599 | 0.11444 | 0.022888 | 0.009155 | -0.032044 | -0.045777 | 0.10986 | -120.8405 | -120.8588 | 0.10986 | 0.19684 | 0.073242 | 0.086975 | -0.036621 | 0.059509 | 120.6894 | 0 | -0.01831 | 120.8405 | 0 | 120.8954 | 0.10986 | -120.8954 | -120.8405 | 120.7443 | 0.091553 | 5.1636 | 0.027466
2109.6406 | 120.9137 | -0.19684 | 120.7993 | 0.01358 | 6.9763 | 0.064405 | 0.060229 | -0.00071343 | -0.0071821 | -0.0030078 | -0.00054933 | 0.0033004 | 0.013751 | 0.0072226 | -0.010258 | 0.026812 | -0.0028646 | 5.0354 | 120.6619 | -0.1236 | 120.5704 | -0.036621 | -0.13733 | -0.13733 | -0.15564 | -0.073242 | -0.07782 | -0.10529 | -0.054932 | -0.082397 | 0 | 0.073242 | -0.13733 | -0.22888 | 0.16022 | 0.059509 | 0.059509 | -0.013733 | -0.013733 | 0.11902 | -120.8725 | -120.9045 | 0.14191 | 0.19684 | 0.11444 | 0.07782 | -0.004577 | 0.086975 | 120.694 | 0.022888 | -0.027466 | 120.7855 | 0.004578 | 120.8588 | 0.1236 | -120.9229 | -120.8771 | 120.7672 | 0.091552 | 5.2322 | 0.041198
2111.375 | 120.9549 | -0.16937 | 120.7672 | -0.0016785 | 6.9778 | 0.064405 | 0.061724 | 0.0044134 | -0.0069683 | -0.0055712 | -0.00054933 | 0.0018052 | 0.014178 | 0.009786 | -0.0064129 | 0.028307 | -0.0035056 | 4.9576 | 120.7077 | -0.1236 | 120.5887 | -0.018311 | -0.16479 | -0.16022 | -0.11902 | -0.082397 | -0.064087 | -0.068665 | -0.032043 | -0.064087 | 0.045776 | 0.045777 | -0.059509 | -0.17853 | 0.15106 | 0.009156 | 0.004578 | -0.036621 | -0.041199 | 0.10529 | -120.8496 | -120.8359 | 0.13733 | 0.21515 | 0.10529 | 0.10986 | 0 | 0.10528 | 120.7123 | 0.032044 | -0.004578 | 120.8313 | -0.01831 | 120.8771 | 0.086976 | -120.8908 | -120.8313 | 120.7581 | 0.10071 | 5.127 | 0.050354
2113.1094 | 120.9091 | -0.20599 | 120.7901 | -0.0016785 | 6.9778 | 0.063551 | 0.062365 | -0.00049983 | -0.0076093 | -0.0027942 | -0.0036011 | -0.0003312 | 0.014819 | 0.0033774 | -0.012181 | 0.024462 | -0.0030784 | 5.0034 | 120.6848 | -0.11902 | 120.5841 | -0.018311 | -0.12817 | -0.14191 | -0.16479 | -0.07782 | -0.054932 | -0.1236 | -0.050354 | -0.086975 | 0.004578 | 0.086975 | -0.10529 | -0.20599 | 0.18768 | 0.064087 | 0.07782 | -0.022888 | -0.009155 | 0.15106 | -120.8679 | -120.9137 | 0.15564 | 0.21057 | 0.11902 | 0.05951 | -0.032043 | 0.10071 | 120.7031 | 0.004578 | -0.068664 | 120.8038 | -0.022888 | 120.8908 | 0.12817 | -120.9091 | -120.845 | 120.7901 | 0.082398 | 5.2094 | 0.041199
2114.8594 | 121.0327 | -0.15106 | 120.7809 | -0.0016785 | 6.9791 | 0.067182 | 0.061297 | 0.00035457 | -0.0052595 | 0.0036146 | -0.00054933 | 0.0022324 | 0.013965 | 0.008077 | -0.0070539 | 0.027453 | -0.0011558 | 5.0491 | 120.6757 | -0.086975 | 120.726 | 0.11444 | -0.036621 | -0.064087 | 0.027466 | -0.10529 | -0.032043 | 0.018311 | 0.059509 | 0.027466 | 0.10986 | 0.064087 | -0.10529 | -0.054932 | 0.2655 | 0.086975 | 0.11444 | 0.022888 | 0.050354 | 0.11902 | -120.8862 | -120.7626 | 0.21057 | 0.26093 | 0.17853 | 0.14191 | 0.059509 | 0.20142 | 120.813 | 0.091552 | 0.050354 | 120.7626 | -0.073243 | 120.8267 | 0.045776 | -120.8679 | -120.813 | 120.8771 | 0.16937 | 5.2002 | 0.17853
2116.5469 | 121.0464 | -0.15106 | 120.7764 | -0.0016785 | 6.9812 | 0.063764 | 0.063433 | 0.0031318 | -0.0052595 | -0.0012988 | 0.0055543 | 0.0020188 | 0.016742 | 0.010213 | -0.0081219 | 0.02788 | 0.00098061 | 5.0354 | 120.6711 | -0.068665 | 120.7352 | 0.10529 | -0.032043 | -0.045776 | 0.009155 | -0.10986 | -0.022888 | 0.027466 | 0.086975 | 0.018311 | 0.12817 | 0.082397 | -0.10528 | -0.041199 | 0.25635 | 0.10529 | 0.11902 | 0.022889 | 0.036622 | 0.12817 | -120.8862 | -120.7489 | 0.23804 | 0.27924 | 0.16937 | 0.15106 | 0.041199 | 0.17395 | 120.8038 | 0.10986 | 0.050354 | 120.7397 | -0.086975 | 120.8221 | 0.041199 | -120.845 | -120.7993 | 120.8862 | 0.17853 | 5.1865 | 0.16022
2118.2812 | 121.0648 | -0.15564 | 120.7809 | 0.01358 | 6.9806 | 0.064405 | 0.060442 | 0.0016364 | -0.0052595 | -0.001726 | -0.00054933 | 0.0013778 | 0.015887 | 0.01299 | -0.0040631 | 0.028734 | -0.0030784 | 5.0446 | 120.6985 | -0.09613 | 120.7535 | 0.11902 | -0.041199 | -0.032043 | 0.018311 | -0.10529 | -0.036621 | 0.027466 | 0.068665 | 0.022888 | 0.10986 | 0.05951 | -0.082398 | -0.027466 | 0.27466 | 0.1236 | 0.11444 | 0.064087 | 0.054931 | 0.11902 | -120.8862 | -120.7535 | 0.22431 | 0.2655 | 0.17853 | 0.14648 | 0.059509 | 0.21515 | 120.8496 | 0.10529 | 0.064087 | 120.7947 | -0.068665 | 120.8542 | 0.050354 | -120.8771 | -120.8176 | 120.9091 | 0.18311 | 5.2002 | 0.17395
2120.0156 | 121.0373 | -0.14648 | 120.8176 | -0.0016785 | 6.9791 | 0.065687 | 0.06386 | 0.0029182 | -0.0039777 | -0.0040758 | 0.0025025 | 0.002446 | 0.015033 | 0.0091452 | -0.0066265 | 0.027239 | -0.0024374 | 4.9484 | 120.7169 | -0.10071 | 120.7123 | 0.091553 | -0.07782 | -0.073242 | -0.013733 | -0.10071 | -0.022888 | -0.022888 | 0.022888 | -0.009155 | 0.073242 | 0.045776 | -0.10071 | -0.10529 | 0.23804 | 0.073242 | 0.068664 | 0.027466 | 0.022888 | 0.1236 | -120.9183 | -120.8405 | 0.16937 | 0.21973 | 0.13733 | 0.09613 | 0.013733 | 0.19226 | 120.813 | 0.045776 | 0 | 120.8176 | -0.07782 | 120.8633 | 0.045776 | -120.9183 | -120.8405 | 120.8588 | 0.1236 | 5.0949 | 0.13275
2121.7031 | 121.1014 | -0.13275 | 120.8176 | -0.0016785 | 6.9795 | 0.065046 | 0.062579 | 0.0031318 | -0.0059003 | -0.0025806 | -0.00054933 | 0.0026596 | 0.014819 | 0.016836 | -0.0055585 | 0.026812 | -0.0028646 | 4.9805 | 120.7306 | -0.09613 | 120.7443 | 0.07782 | -0.068665 | -0.059509 | 0.004578 | -0.11902 | -0.027466 | 0.032043 | 0.064087 | 0.013733 | 0.10529 | 0.036621 | -0.086975 | -0.073242 | 0.21057 | 0.073242 | 0.064086 | 0.036621 | 0.027465 | 0.10529 | -120.9366 | -120.7855 | 0.19684 | 0.23804 | 0.14648 | 0.13275 | 0.041199 | 0.17395 | 120.8405 | 0.091553 | 0.059509 | 120.8267 | -0.091553 | 120.8633 | 0.013732 | -120.9137 | -120.845 | 120.8771 | 0.16479 | 5.1132 | 0.13733
2123.4375 | 120.9595 | -0.18768 | 120.8588 | 0.005951 | 6.9761 | 0.063764 | 0.064501 | 0.0039862 | -0.0065411 | -1.7026e-05 | -0.0036011 | 0.002446 | 0.014819 | 0.0061544 | -0.010258 | 0.025957 | -0.00072839 | 4.8569 | 120.7764 | -0.14648 | 120.6162 | -0.064087 | -0.18768 | -0.17853 | -0.17853 | -0.082397 | -0.068665 | -0.10071 | -0.082397 | -0.13275 | 0 | 0.041199 | -0.082398 | -0.24262 | 0.1236 | 0.009155 | 0 | -0.032044 | -0.041199 | 0.11902 | -120.9412 | -120.9595 | 0.10529 | 0.18768 | 0.054932 | 0.068665 | -0.064086 | 0.082397 | 120.7626 | -0.013732 | -0.032043 | 120.9229 | -0.013732 | 120.9641 | 0.10529 | -121.0052 | -120.9274 | 120.8038 | 0.086975 | 5.0446 | 0.009155
2125.1719 | 120.9686 | -0.21057 | 120.8588 | -0.009308 | 6.9786 | 0.061201 | 0.061938 | 0.00035457 | -0.0080365 | -0.00044443 | -0.00054933 | 0.0054368 | 0.015674 | 0.0065816 | -0.010899 | 0.02788 | 0.0016214 | 4.953 | 120.7535 | -0.14191 | 120.6665 | -0.032043 | -0.1236 | -0.14191 | -0.16022 | -0.059509 | -0.073242 | -0.13275 | -0.059509 | -0.09613 | -0.009155 | 0.068664 | -0.10529 | -0.19226 | 0.17853 | 0.068664 | 0.086975 | 0 | 0.018311 | 0.13733 | -120.9183 | -120.9915 | 0.15106 | 0.20142 | 0.11444 | 0.064087 | -0.022888 | 0.10986 | 120.8084 | 0.013733 | -0.059509 | 120.8954 | 0.013733 | 120.9641 | 0.15106 | -121.0007 | -120.932 | 120.8771 | 0.07782 | 5.1636 | 0.050354
2126.9219 | 120.9915 | -0.19684 | 120.8954 | -0.009308 | 6.9786 | 0.06526 | 0.064288 | -0.0011408 | -0.0082501 | -0.0012988 | -0.00054933 | 0.002446 | 0.016101 | 0.018331 | -0.0072675 | 0.026385 | -0.0045736 | 4.9347 | 120.7901 | -0.10986 | 120.6253 | -0.07782 | -0.19226 | -0.17395 | -0.16479 | -0.064087 | -0.07782 | -0.10529 | -0.086975 | -0.11444 | 0.009155 | 0.086975 | -0.10529 | -0.27008 | 0.11902 | 0.022888 | 0.004577 | -0.064087 | -0.082398 | 0.11902 | -120.9595 | -121.0007 | 0.10986 | 0.20599 | 0.082397 | 0.086975 | -0.036621 | 0.032043 | 120.7352 | -0.009155 | -0.027466 | 120.9 | 0.013733 | 120.9869 | 0.13275 | -121.0052 | -120.9732 | 120.8221 | 0.091552 | 5.1315 | 0.032043
2128.6094 | 121.1288 | -0.15106 | 120.845 | -0.0016785 | 6.9767 | 0.063551 | 0.061083 | 0.0012092 | -0.0078229 | -0.00065803 | 0.0025025 | 0.0011642 | 0.014819 | 0.0074362 | -0.0042767 | 0.027453 | -0.0047874 | 4.9759 | 120.7626 | -0.10529 | 120.7901 | 0.07782 | -0.050354 | -0.073242 | -0.009155 | -0.10986 | -0.036621 | 0.027466 | 0.07782 | 0.013733 | 0.11902 | 0.045776 | -0.082398 | -0.054932 | 0.22888 | 0.07782 | 0.10071 | 0.032044 | 0.054932 | 0.11444 | -120.9549 | -120.8176 | 0.22888 | 0.27008 | 0.16479 | 0.15564 | 0.050354 | 0.18311 | 120.8954 | 0.11444 | 0.064087 | 120.8679 | -0.073242 | 120.9137 | 0.041199 | -120.9503 | -120.8817 | 120.9412 | 0.17853 | 5.127 | 0.14191
2130.3594 | 121.0144 | -0.22888 | 120.8862 | -0.0016785 | 6.9784 | 0.064832 | 0.064074 | 0.003559 | -0.0067547 | -0.0012988 | -0.00054933 | 0.0043686 | 0.016528 | 0.010427 | -0.010258 | 0.024462 | -0.0037192 | 4.8935 | 120.8038 | -0.14648 | 120.6665 | -0.073242 | -0.18768 | -0.1831 | -0.16937 | -0.086975 | -0.050354 | -0.082397 | -0.07782 | -0.11902 | 0.013733 | 0.082398 | -0.082397 | -0.21973 | 0.15564 | 0.045777 | 0.041199 | -0.036621 | -0.041199 | 0.17853 | -120.9732 | -120.9686 | 0.15106 | 0.24261 | 0.10986 | 0.064087 | -0.068665 | 0.073242 | 120.813 | -0.027466 | -0.032043 | 120.9503 | -0.036621 | 121.0327 | 0.14191 | -121.0327 | -120.9366 | 120.8954 | 0.14649 | 5.1224 | 0.059509
2132.1094 | 121.1517 | -0.14648 | 120.8725 | -0.0016785 | 6.9765 | 0.065687 | 0.060015 | 0.0071906 | -0.0078229 | -0.0015124 | -0.0036011 | 0.0020188 | 0.013324 | 0.012136 | -0.0059857 | 0.027025 | -0.0041464 | 5.0034 | 120.7901 | -0.09613 | 120.8176 | 0.10071 | -0.059509 | -0.054932 | 0.018311 | -0.11444 | -0.013733 | 0.027466 | 0.064087 | 0.027466 | 0.11444 | 0.050354 | -0.082398 | -0.054932 | 0.24719 | 0.091552 | 0.086975 | 0.041198 | 0.036621 | 0.13275 | -120.9869 | -120.845 | 0.21057 | 0.26093 | 0.17395 | 0.12817 | 0.041199 | 0.19684 | 120.9137 | 0.07782 | 0.041199 | 120.8862 | -0.10071 | 120.9366 | 0.032043 | -120.9686 | -120.8862 | 120.9641 | 0.17395 | 5.1498 | 0.16479
2133.8594 | 121.0373 | -0.20142 | 120.9045 | -0.009308 | 6.9793 | 0.06526 | 0.062579 | 0.00078177 | -0.0071821 | -0.0010852 | -0.0036011 | 0.0030868 | 0.014605 | 0.014059 | -0.0074811 | 0.026171 | -0.001583 | 4.9026 | 120.8496 | -0.12817 | 120.6757 | -0.07782 | -0.18768 | -0.18768 | -0.16937 | -0.068665 | -0.064087 | -0.10529 | -0.086975 | -0.1236 | 0.013733 | 0.073242 | -0.054932 | -0.22888 | 0.1236 | 0.013733 | 0.013733 | -0.059509 | -0.059509 | 0.13733 | -120.9732 | -121.0098 | 0.11444 | 0.21515 | 0.07782 | 0.07782 | -0.059509 | 0.050354 | 120.8038 | -0.022888 | -0.041199 | 120.9778 | -0.004578 | 121.051 | 0.13275 | -121.0327 | -120.9686 | 120.8771 | 0.09613 | 5.1041 | 0.032043
2135.6094 | 121.1243 | -0.15564 | 120.8771 | 0.01358 | 6.978 | 0.063978 | 0.060229 | 0.0044134 | -0.0063275 | -0.0030078 | 0.0086061 | 0.0005234 | 0.018451 | 0.018331 | -0.0087629 | 0.027666 | -0.0022238 | 4.9484 | 120.7901 | -0.082397 | 120.8221 | 0.10071 | -0.054932 | -0.054932 | -0.013733 | -0.1236 | -0.045776 | 0.018311 | 0.050354 | 0.009155 | 0.10529 | 0.073243 | -0.086975 | -0.054931 | 0.25635 | 0.10071 | 0.10071 | 0.027465 | 0.027465 | 0.10986 | -121.0007 | -120.8588 | 0.20599 | 0.26093 | 0.16479 | 0.15106 | 0.054931 | 0.18311 | 120.9045 | 0.09613 | 0.064087 | 120.8725 | -0.07782 | 120.9457 | 0.032044 | -120.9595 | -120.9229 | 120.9778 | 0.17395 | 5.1041 | 0.14191
2137.2969 | 121.0556 | -0.20599 | 120.9137 | 0.005951 | 6.9782 | 0.062055 | 0.062151 | 0.0012092 | -0.010173 | -0.002367 | -0.00054933 | 0.0039414 | 0.016314 | 0.011922 | -0.013249 | 0.024248 | -0.001583 | 4.9713 | 120.8542 | -0.15106 | 120.7077 | -0.041199 | -0.15564 | -0.14648 | -0.15564 | -0.064087 | -0.068665 | -0.11902 | -0.050354 | -0.091553 | 0.004578 | 0.054932 | -0.059509 | -0.20599 | 0.1648 | 0.05951 | 0.050354 | 0.004578 | -0.004578 | 0.13733 | -120.9778 | -121.0327 | 0.15564 | 0.21057 | 0.11444 | 0.073243 | -0.022888 | 0.10986 | 120.8588 | 0.018311 | -0.050354 | 121.0052 | 0.004578 | 121.0602 | 0.14191 | -121.0648 | -120.9824 | 120.9137 | 0.086975 | 5.1773 | 0.050354
2139.0312 | 121.1609 | -0.16479 | 120.9045 | -0.0016785 | 6.9763 | 0.063551 | 0.059802 | 0.00056817 | -0.0084637 | -0.0027942 | -0.0066527 | 0.0026596 | 0.015887 | 0.015127 | -0.0091901 | 0.027025 | -0.0041464 | 4.9393 | 120.7901 | -0.11444 | 120.7809 | 0.041199 | -0.073242 | -0.091553 | -0.064087 | -0.11444 | -0.050354 | -0.027466 | 0.036621 | 0 | 0.073242 | 0.050354 | -0.11444 | -0.1236 | 0.20599 | 0.073242 | 0.091553 | 0.022888 | 0.041199 | 0.11444 | -121.019 | -120.932 | 0.20142 | 0.23804 | 0.16479 | 0.1236 | 0.050354 | 0.15564 | 120.8954 | 0.086975 | 0.022888 | 120.9045 | -0.064087 | 120.9549 | 0.050354 | -121.019 | -120.9549 | 120.9457 | 0.13733 | 5.1041 | 0.10071
2140.7969 | 121.138 | -0.16937 | 120.9183 | -0.009308 | 6.9784 | 0.064619 | 0.062151 | 0.0024908 | -0.0080365 | -0.002367 | -0.0036011 | 0.0020188 | 0.015674 | 0.014059 | -0.0079083 | 0.024676 | -0.002651 | 4.921 | 120.8221 | -0.10071 | 120.7947 | 0.022888 | -0.086975 | -0.091553 | -0.059509 | -0.10986 | -0.064087 | -0.045776 | 0.004578 | -0.018311 | 0.064087 | 0.068665 | -0.09613 | -0.1236 | 0.19226 | 0.07782 | 0.082398 | 0.009155 | 0.013733 | 0.10529 | -121.0281 | -120.9641 | 0.17395 | 0.23346 | 0.15106 | 0.12817 | 0.045776 | 0.1236 | 120.8954 | 0.068665 | 0.018311 | 120.9229 | -0.045776 | 120.9915 | 0.05951 | -121.019 | -120.9824 | 120.9641 | 0.1236 | 5.0903 | 0.10986
2142.4844 | 117.9474 | -22.4075 | 95.2744 | -0.009308 | 6.9789 | 0.063551 | 0.061511 | -0.0017816 | -0.0063275 | -0.001726 | -0.00054933 | 0.0050094 | 0.014819 | 0.0091452 | -0.0081219 | 0.026598 | -0.0028646 | -1.3046 | 94.9768 | -22.6456 | 95.0226 | -22.3755 | -22.4213 | -23.0164 | -0.15564 | -0.050354 | -0.050354 | -0.10071 | -0.068665 | -0.09613 | 0.009155 | -0.23804 | -0.29755 | -0.25177 | 0.032044 | -0.60882 | -0.013733 | -0.37079 | 0.2243 | 22.3572 | -95.3247 | -95.3751 | 22.3389 | 22.4167 | 22.3114 | 0.059509 | -0.045776 | 0.27008 | 117.6682 | -0.018311 | -0.050354 | 117.6224 | 0 | 117.3843 | 22.3572 | -117.9199 | -95.3247 | 117.4301 | 22.3068 | 21.1029 | 22.2519
2144.2188 | 120.8542 | -0.19684 | 120.7031 | 0.005951 | 6.9767 | 0.064832 | 0.062579 | 0.0044134 | -0.0073957 | -0.0045032 | -0.0036011 | 0.0022324 | 0.015033 | 0.011709 | -0.0079083 | 0.026598 | -0.0092734 | 4.8065 | 120.6116 | -0.11444 | 120.5017 | -0.045776 | -0.1831 | -0.15564 | -0.14191 | -0.073242 | -0.07782 | -0.07782 | -0.027466 | -0.082397 | 0.036621 | 0.082397 | -0.091553 | -0.20142 | 0.15106 | 0.041198 | 0.013733 | -0.041199 | -0.068664 | 0.11902 | -120.7764 | -120.7809 | 0.16937 | 0.23346 | 0.11444 | 0.11444 | -0.004577 | 0.068665 | 120.6162 | 0.050354 | 0 | 120.726 | 0.004578 | 120.8084 | 0.1236 | -120.8176 | -120.7809 | 120.6985 | 0.11902 | 5.0034 | 0.054931
2145.9688 | 120.9869 | -0.17395 | 120.7626 | -0.0016785 | 6.9765 | 0.065687 | 0.063647 | -7.2628e-05 | -0.0091047 | -0.00065803 | -0.0036011 | 0.0013778 | 0.013751 | 0.0085044 | -0.011113 | 0.029162 | -0.00094199 | 4.8203 | 120.6345 | -0.10071 | 120.6345 | 0.032043 | -0.07782 | -0.07782 | -0.068665 | -0.091553 | -0.027466 | -0.027466 | 0.041199 | 0.018311 | 0.086975 | 0.073242 | -0.12817 | -0.12817 | 0.20599 | 0.09613 | 0.09613 | 0.022888 | 0.022888 | 0.14648 | -120.8542 | -120.7901 | 0.21515 | 0.26092 | 0.19226 | 0.11444 | 0.045777 | 0.13275 | 120.7352 | 0.068665 | 0 | 120.7352 | -0.064087 | 120.8084 | 0.082397 | -120.8633 | -120.7901 | 120.8084 | 0.14648 | 4.9942 | 0.10528
2147.6562 | 121.0007 | -0.17853 | 120.7809 | -0.0016785 | 6.9801 | 0.064405 | 0.062365 | 0.00056817 | -0.0052595 | -0.0030078 | -0.00054933 | 0.0033004 | 0.015033 | 0.018545 | -0.0096173 | 0.02788 | -0.002651 | 4.8386 | 120.6711 | -0.086975 | 120.6894 | 0.086975 | -0.073242 | -0.064087 | -0.022888 | -0.10986 | -0.036621 | -0.022888 | 0.027466 | -0.013733 | 0.073242 | 0.091553 | -0.10986 | -0.091553 | 0.2655 | 0.11444 | 0.10529 | 0.022888 | 0.013733 | 0.14191 | -120.8908 | -120.8038 | 0.20599 | 0.25177 | 0.16479 | 0.10986 | 0.022888 | 0.17395 | 120.7764 | 0.064087 | 0.013733 | 120.7581 | -0.073242 | 120.8496 | 0.068665 | -120.8679 | -120.8176 | 120.8679 | 0.15564 | 5.0171 | 0.15564
2149.3906 | 121.0648 | -0.15564 | 120.813 | 0.005951 | 6.9767 | 0.065473 | 0.061724 | -0.00028623 | -0.0050457 | -0.0027942 | -0.00054933 | 0.0003098 | 0.016101 | 0.014699 | -0.0049175 | 0.028307 | -0.006069 | 4.8431 | 120.7031 | -0.086975 | 120.7535 | 0.09613 | -0.054932 | -0.059509 | 0.013733 | -0.10986 | -0.022888 | 0 | 0.091553 | 0.022888 | 0.10529 | 0.068665 | -0.10986 | -0.059509 | 0.25177 | 0.096131 | 0.10071 | 0.027466 | 0.032043 | 0.13275 | -120.9229 | -120.813 | 0.24719 | 0.26093 | 0.17853 | 0.12817 | 0.045776 | 0.1831 | 120.8405 | 0.11444 | 0.022888 | 120.7901 | -0.086975 | 120.8588 | 0.045777 | -120.9 | -120.8359 | 120.9091 | 0.15564 | 4.9988 | 0.16937
2151.125 | 121.0144 | -0.20599 | 120.8817 | 0.005951 | 6.9786 | 0.065046 | 0.061511 | 0.0016364 | -0.0084637 | -0.0042896 | -0.00054933 | 0.0033004 | 0.016528 | 0.014059 | -0.011967 | 0.026385 | -0.0022238 | 4.8935 | 120.7581 | -0.14648 | 120.6528 | -0.045776 | -0.13733 | -0.15106 | -0.16022 | -0.082397 | -0.068665 | -0.10529 | -0.050354 | -0.068665 | 0.018311 | 0.05951 | -0.1236 | -0.22888 | 0.16022 | 0.054932 | 0.068665 | -0.004578 | 0.009155 | 0.13733 | -120.9641 | -120.9869 | 0.15564 | 0.22431 | 0.13733 | 0.086976 | 0 | 0.10071 | 120.7993 | 0.018311 | -0.036621 | 120.9045 | -0.013732 | 120.9641 | 0.1236 | -121.0281 | -120.9503 | 120.8588 | 0.10071 | 5.0995 | 0.045777
2152.875 | 121.0373 | -0.20142 | 120.8817 | -0.0016785 | 6.9808 | 0.063337 | 0.064501 | 0.00185 | -0.0059003 | -0.0021532 | -0.0036011 | 0.0030868 | 0.015674 | 0.011068 | -0.0070539 | 0.022753 | -0.0035056 | 4.9484 | 120.7947 | -0.1236 | 120.7306 | 0.032043 | -0.091553 | -0.13275 | -0.07782 | -0.086975 | -0.068665 | -0.059509 | -0.004578 | -0.064087 | 0.050354 | 0.07782 | -0.086975 | -0.15106 | 0.23346 | 0.068665 | 0.10986 | -0.009155 | 0.032043 | 0.13275 | -120.9686 | -120.9412 | 0.19684 | 0.25177 | 0.13733 | 0.11902 | 0.004578 | 0.15564 | 120.8542 | 0.064087 | 0.009156 | 120.9183 | -0.01831 | 120.9961 | 0.11444 | -121.0052 | -120.9503 | 120.932 | 0.14191 | 5.1498 | 0.1236
2154.5625 | 121.0785 | -0.19226 | 120.8679 | -0.009308 | 6.9771 | 0.062696 | 0.061938 | 0.0024908 | -0.0061139 | -0.0015124 | -0.00054933 | 0.0026596 | 0.015246 | 0.016836 | -0.0044903 | 0.026812 | -0.00094199 | 4.8477 | 120.7947 | -0.1236 | 120.694 | -0.045776 | -0.16479 | -0.15106 | -0.11444 | -0.091553 | -0.050354 | -0.041199 | 0.004578 | -0.045776 | 0.064087 | 0.068665 | -0.073242 | -0.17395 | 0.14648 | 0.041199 | 0.027466 | -0.027466 | -0.041199 | 0.14191 | -120.9595 | -120.9091 | 0.19684 | 0.25635 | 0.14648 | 0.11444 | 0.004578 | 0.07782 | 120.8176 | 0.054932 | 0.009155 | 120.9183 | -0.041199 | 120.9869 | 0.10071 | -120.9915 | -120.9183 | 120.8862 | 0.15106 | 5.04 | 0.07782
2156.3125 | 120.6024 | -1.7761 | 118.84 | -0.0016785 | 6.9782 | 0.064405 | 0.062151 | 0.0041998 | -0.0091047 | -0.00065803 | 0.0055543 | 0.004155 | 0.015033 | 0.0099996 | -0.010472 | 0.025957 | -0.0037192 | 4.2984 | 119.5633 | -1.1627 | 117.9657 | -1.9043 | -1.5976 | -1.2268 | -0.16022 | -0.068665 | -0.073242 | -0.10986 | -0.022888 | -0.064087 | 0.009155 | 0.6134 | 0.72327 | -0.87433 | -0.12817 | 0.54932 | 0.17853 | -0.064087 | -0.43488 | 1.7029 | -118.9087 | -118.9499 | 1.7532 | 1.7853 | 1.712 | 0.082397 | 0.009155 | -0.74158 | 119.1284 | 0.050354 | -0.036621 | 120.726 | 0.004577 | 121.3394 | 1.7075 | -120.0027 | -118.9133 | 119.7418 | 1.6663 | 6.0745 | 1.6159
2158.0469 | 120.6894 | -0.16022 | 120.369 | -0.009308 | 6.9752 | 0.061842 | 0.060442 | 0.00014097 | -0.0061139 | -0.002367 | -0.00054933 | 0.0013778 | 0.015674 | 0.012136 | -0.010258 | 0.026385 | -0.0045736 | 4.8477 | 120.3003 | -0.091553 | 120.3506 | 0.10071 | -0.027466 | -0.036621 | 0.009155 | -0.10986 | -0.036621 | 0.013733 | 0.09613 | 0.041199 | 0.10071 | 0.068664 | -0.068665 | -0.018311 | 0.26093 | 0.1236 | 0.13275 | 0.054932 | 0.064087 | 0.1236 | -120.4788 | -120.3552 | 0.25635 | 0.26093 | 0.20142 | 0.13733 | 0.07782 | 0.19226 | 120.4422 | 0.13275 | 0.050354 | 120.3918 | -0.073242 | 120.4605 | 0.050354 | -120.4605 | -120.4056 | 120.5109 | 0.17395 | 5.0079 | 0.16937
2159.7969 | 120.7031 | -0.20142 | 120.5612 | -0.009308 | 6.9782 | 0.064405 | 0.063433 | 0.00014097 | -0.0091047 | -0.0027942 | -0.0036011 | 0.0022324 | 0.016528 | 0.01534 | -0.011967 | 0.02553 | 0.00055321 | 4.8065 | 120.4559 | -0.12817 | 120.3644 | -0.027466 | -0.1236 | -0.16022 | -0.16022 | -0.082397 | -0.07782 | -0.11444 | -0.064087 | -0.09613 | -0.009155 | 0.073242 | -0.10528 | -0.19684 | 0.17395 | 0.041199 | 0.07782 | -0.032043 | 0.004578 | 0.1236 | -120.6436 | -120.6757 | 0.13733 | 0.19226 | 0.10529 | 0.068665 | -0.01831 | 0.10071 | 120.4926 | 0.013733 | -0.036621 | 120.5841 | -0.004577 | 120.6573 | 0.11902 | -120.6894 | -120.639 | 120.5658 | 0.086975 | 5.0079 | 0.041199
2161.4844 | 120.8038 | -0.20142 | 120.6116 | -0.0016785 | 6.9774 | 0.063337 | 0.062365 | 0.00078177 | -0.0071821 | -0.0038622 | 0.0025025 | 0.0026596 | 0.017596 | 0.004659 | -0.0070539 | 0.025744 | -0.0041464 | 4.8203 | 120.5521 | -0.13275 | 120.4468 | -0.032043 | -0.1236 | -0.14191 | -0.16022 | -0.064087 | -0.082397 | -0.064087 | -0.022888 | -0.064087 | 0.032043 | 0.068665 | -0.059509 | -0.16479 | 0.16937 | 0.059509 | 0.07782 | -0.009156 | 0.009155 | 0.11902 | -120.6757 | -120.6757 | 0.17853 | 0.23346 | 0.13733 | 0.11444 | 0.01831 | 0.10071 | 120.5795 | 0.059509 | 0.01831 | 120.6848 | 0.01831 | 120.7535 | 0.13733 | -120.7443 | -120.694 | 120.6482 | 0.13733 | 5.0217 | 0.041199
2163.2188 | 120.8679 | -0.19226 | 120.6802 | -0.009308 | 6.9799 | 0.06526 | 0.061938 | 0.003559 | -0.0061139 | -0.005144 | -0.00054933 | -0.0001174 | 0.015246 | 0.013204 | -0.0051313 | 0.026385 | -0.0028646 | 4.7607 | 120.6162 | -0.14191 | 120.4742 | -0.022888 | -0.16937 | -0.15106 | -0.11444 | -0.082397 | -0.064087 | -0.045776 | -0.013733 | -0.059509 | 0.059509 | 0.050354 | -0.064087 | -0.20599 | 0.16937 | 0.041199 | 0.022888 | -0.009155 | -0.027466 | 0.12817 | -120.7626 | -120.726 | 0.17853 | 0.25177 | 0.13275 | 0.1236 | 0.004578 | 0.11902 | 120.6162 | 0.050354 | 0.018311 | 120.7581 | -0.01831 | 120.8084 | 0.10986 | -120.8221 | -120.7443 | 120.6665 | 0.14648 | 4.953 | 0.07782
2164.9531 | 120.8862 | -0.17853 | 120.7031 | 0.005951 | 6.9789 | 0.063764 | 0.06322 | -0.0024224 | -0.0088911 | -0.0027942 | -0.0036011 | 0.0028732 | 0.016955 | 0.011709 | -0.010899 | 0.023821 | -0.0052146 | 4.8065 | 120.5887 | -0.1236 | 120.5566 | 0.004578 | -0.09613 | -0.11902 | -0.082397 | -0.07782 | -0.059509 | -0.041199 | 0.018311 | -0.036621 | 0.041199 | 0.054932 | -0.11444 | -0.14648 | 0.18311 | 0.059509 | 0.082398 | 0.004577 | 0.027466 | 0.11902 | -120.7809 | -120.7443 | 0.19684 | 0.21973 | 0.14191 | 0.10071 | 0.022888 | 0.12817 | 120.6802 | 0.07782 | 0.01831 | 120.7123 | -0.018311 | 120.7672 | 0.10071 | -120.8267 | -120.7626 | 120.7352 | 0.13733 | 4.985 | 0.096131
2166.7031 | 120.8588 | -0.20599 | 120.7581 | 0.005951 | 6.9791 | 0.06526 | 0.061938 | 0.0016364 | -0.0071821 | -0.0030078 | -0.0036011 | 0.002446 | 0.016742 | 0.012563 | -0.0070539 | 0.024676 | -0.00030119 | 4.8065 | 120.6711 | -0.14191 | 120.5429 | -0.054932 | -0.17395 | -0.17395 | -0.15564 | -0.082397 | -0.045776 | -0.091553 | -0.073242 | -0.11444 | -0.013733 | 0.064087 | -0.086975 | -0.21515 | 0.15106 | 0.032044 | 0.032044 | -0.032043 | -0.032043 | 0.16022 | -120.8405 | -120.8496 | 0.13275 | 0.19226 | 0.091553 | 0.032043 | -0.068665 | 0.086975 | 120.6848 | -0.027466 | -0.045777 | 120.813 | -0.036621 | 120.8771 | 0.1236 | -120.9 | -120.8038 | 120.7489 | 0.11444 | 5.0125 | 0.050354
2168.4531 | 120.8954 | -0.20599 | 120.7672 | -0.009308 | 6.9771 | 0.064832 | 0.062792 | 0.0027044 | -0.0086773 | -0.0010852 | -0.0036011 | 0.0030868 | 0.014605 | 0.014486 | -0.0068403 | 0.028094 | -0.0056418 | 4.8523 | 120.694 | -0.11902 | 120.607 | 0.018311 | -0.11444 | -0.11902 | -0.09613 | -0.064087 | -0.054932 | -0.059509 | -0.018311 | -0.073242 | 0.036621 | 0.086975 | -0.073242 | -0.16022 | 0.22431 | 0.086975 | 0.091553 | 0 | 0.004578 | 0.15106 | -120.8313 | -120.8267 | 0.18768 | 0.24262 | 0.13275 | 0.091553 | -0.01831 | 0.13733 | 120.726 | 0.036621 | -0.004577 | 120.813 | -0.009155 | 120.9 | 0.14191 | -120.8862 | -120.8221 | 120.813 | 0.14649 | 5.0583 | 0.10986
2170.125 | 121.0236 | -0.15564 | 120.7581 | 0.005951 | 6.9786 | 0.065046 | 0.061511 | 0.0027044 | -0.0073957 | -0.00065803 | 0.0025025 | 0.0033004 | 0.013965 | 0.014059 | -0.0061993 | 0.027666 | -0.00030119 | 4.7745 | 120.7031 | -0.10529 | 120.6665 | 0.07782 | -0.064087 | -0.059509 | -0.009155 | -0.13275 | -0.022888 | 0.032043 | 0.086975 | 0.018311 | 0.11444 | 0.050354 | -0.054932 | -0.091553 | 0.23346 | 0.096131 | 0.091553 | 0.045777 | 0.041199 | 0.13275 | -120.8908 | -120.726 | 0.24261 | 0.27008 | 0.17395 | 0.13733 | 0.041199 | 0.18311 | 120.7718 | 0.10986 | 0.054931 | 120.8084 | -0.10986 | 120.8588 | 0.022889 | -120.8633 | -120.7809 | 120.8221 | 0.18768 | 4.9301 | 0.14649
2171.875 | 120.9549 | -0.21057 | 120.8084 | -0.0016785 | 6.9793 | 0.063551 | 0.064501 | 0.0037726 | -0.0097455 | -0.00044443 | 0.0025025 | 0.003514 | 0.015674 | 0.011922 | -0.010899 | 0.024462 | -0.00072839 | 4.8157 | 120.7214 | -0.13733 | 120.575 | -0.041199 | -0.13733 | -0.13733 | -0.17395 | -0.068665 | -0.07782 | -0.082397 | -0.036621 | -0.068665 | 0.018311 | 0.073242 | -0.086975 | -0.23346 | 0.16937 | 0.073242 | 0.073242 | 0 | 0 | 0.13275 | -120.8771 | -120.8908 | 0.17395 | 0.22888 | 0.14191 | 0.096131 | 0.009155 | 0.09613 | 120.7123 | 0.041199 | -0.004577 | 120.8588 | 0.009155 | 120.932 | 0.14191 | -120.9457 | -120.8862 | 120.7855 | 0.12817 | 5.0262 | 0.036621
2173.5469 | 120.932 | -0.21973 | 120.813 | 0.005951 | 6.9799 | 0.065046 | 0.064501 | -7.2628e-05 | -0.010173 | -0.0019396 | -0.00054933 | 0.002446 | 0.014392 | 0.0082906 | -0.0044903 | 0.027453 | -0.001583 | 4.7562 | 120.7443 | -0.13275 | 120.5795 | -0.068665 | -0.1831 | -0.18768 | -0.17395 | -0.07782 | -0.07782 | -0.091553 | -0.082397 | -0.11902 | 0.004578 | 0.086976 | -0.068664 | -0.23346 | 0.15106 | 0.032044 | 0.036622 | -0.054932 | -0.050354 | 0.14191 | -120.8908 | -120.9045 | 0.13733 | 0.22431 | 0.10071 | 0.082398 | -0.041199 | 0.064086 | 120.7123 | -0.004577 | -0.013733 | 120.8771 | 0 | 120.9641 | 0.14191 | -120.9457 | -120.8908 | 120.7993 | 0.12817 | 4.9759 | 0.045777
2175.2812 | 121.0739 | -0.16022 | 120.8038 | -0.0016785 | 6.9756 | 0.063551 | 0.058306 | -7.2628e-05 | -0.0095319 | -1.7026e-05 | -0.0066527 | 0.0003098 | 0.012256 | 0.008718 | -0.0087629 | 0.025316 | -0.0052146 | 4.8203 | 120.6848 | -0.082397 | 120.7443 | 0.12817 | 0 | -0.032043 | 0.004578 | -0.10529 | -0.050354 | 0.009155 | 0.091553 | 0.054932 | 0.10986 | 0.07782 | -0.11902 | -0.059509 | 0.28839 | 0.12817 | 0.16022 | 0.050354 | 0.082397 | 0.10986 | -120.9091 | -120.7947 | 0.25177 | 0.27008 | 0.21515 | 0.16022 | 0.10529 | 0.21057 | 120.8267 | 0.14191 | 0.059509 | 120.7672 | -0.054932 | 120.845 | 0.054931 | -120.8862 | -120.8542 | 120.9045 | 0.16937 | 4.9805 | 0.16479
2177.0312 | 121.1243 | -0.16479 | 120.8176 | -0.016937 | 6.978 | 0.063978 | 0.06386 | 0.00035457 | -0.0063275 | -0.005144 | -0.0066527 | 0.0028732 | 0.014178 | 0.01299 | -0.0066265 | 0.027666 | 0.00076681 | 4.7287 | 120.7397 | -0.10071 | 120.694 | 0.036621 | -0.09613 | -0.10529 | -0.032043 | -0.10986 | -0.050354 | 0 | 0.050354 | 0.004578 | 0.1236 | 0.064087 | -0.07782 | -0.1236 | 0.20142 | 0.059509 | 0.068665 | -0.004578 | 0.004578 | 0.11444 | -120.9274 | -120.8176 | 0.21515 | 0.28839 | 0.16937 | 0.17395 | 0.054932 | 0.13733 | 120.7947 | 0.10071 | 0.050354 | 120.8405 | -0.059509 | 120.9045 | 0.054932 | -120.9183 | -120.8679 | 120.8588 | 0.16479 | 4.8935 | 0.13275
2178.7812 | 121.0739 | -0.1831 | 120.8084 | -0.0016785 | 6.9786 | 0.063551 | 0.061297 | 0.00056817 | -0.0078229 | -0.0049304 | -0.0036011 | -0.0007584 | 0.014819 | 0.0061544 | -0.0066265 | 0.028734 | 0.00055321 | 4.7653 | 120.7626 | -0.11902 | 120.7077 | 0.027466 | -0.082397 | -0.09613 | -0.07782 | -0.10071 | -0.054932 | -0.022888 | 0.036621 | 0 | 0.082397 | 0.064086 | -0.045777 | -0.10071 | 0.21057 | 0.086975 | 0.10071 | 0.022889 | 0.036622 | 0.12817 | -120.9091 | -120.8313 | 0.21973 | 0.2655 | 0.1831 | 0.13733 | 0.054932 | 0.14649 | 120.8267 | 0.091553 | 0.032044 | 120.8817 | -0.045776 | 120.9457 | 0.082397 | -120.9274 | -120.8633 | 120.8908 | 0.16022 | 4.9484 | 0.10528
2180.4688 | 120.9824 | -0.21973 | 120.8771 | -0.009308 | 6.978 | 0.061201 | 0.061297 | -0.0022088 | -0.0091047 | -0.00023063 | -0.0066527 | 0.0018052 | 0.012042 | 0.014486 | -0.0091901 | 0.02788 | -0.0028646 | 4.7287 | 120.7947 | -0.15564 | 120.6619 | -0.050354 | -0.13733 | -0.15564 | -0.16022 | -0.050354 | -0.073242 | -0.11444 | -0.064087 | -0.086975 | 0 | 0.064087 | -0.082397 | -0.21515 | 0.16937 | 0.064087 | 0.082398 | 0 | 0.018311 | 0.14649 | -120.9274 | -120.9915 | 0.15564 | 0.21973 | 0.13275 | 0.073242 | -0.013733 | 0.10529 | 120.8176 | 0.009155 | -0.041199 | 120.9503 | 0.022888 | 121.0144 | 0.16937 | -121.0327 | -120.9503 | 120.8817 | 0.10529 | 4.9484 | 0.05951
2182.2188 | 120.9869 | -0.21515 | 120.8633 | -0.0016785 | 6.9767 | 0.063337 | 0.061083 | 0.0014228 | -0.0082501 | -0.0042896 | 0.0025025 | 0.0022324 | 0.014605 | 0.015127 | -0.010258 | 0.026385 | 0.00012601 | 4.6875 | 120.8038 | -0.13733 | 120.6665 | -0.045776 | -0.15106 | -0.14648 | -0.16022 | -0.050354 | -0.068665 | -0.10986 | -0.054932 | -0.091553 | 0.009155 | 0.07782 | -0.059509 | -0.19684 | 0.16937 | 0.068665 | 0.064087 | -0.009155 | -0.013733 | 0.14648 | -120.9137 | -120.9732 | 0.16022 | 0.2243 | 0.1236 | 0.07782 | -0.022888 | 0.091553 | 120.8038 | 0.013733 | -0.041198 | 120.9412 | 0.018311 | 121.019 | 0.16479 | -121.0007 | -120.932 | 120.8817 | 0.10529 | 4.9026 | 0.054932
2183.9688 | 121.0464 | -0.1831 | 120.9183 | -0.016937 | 6.9793 | 0.063978 | 0.061724 | 0.0022772 | -0.0091047 | -0.0025806 | -0.0036011 | 0.002446 | 0.012683 | 0.011922 | -0.0087629 | 0.024462 | -0.0020102 | 4.8157 | 120.7397 | -0.11902 | 120.7626 | 0.064087 | -0.027466 | -0.068665 | -0.091553 | -0.10529 | -0.050354 | -0.07782 | 0 | -0.032043 | 0.018311 | 0.064086 | -0.17853 | -0.15564 | 0.24719 | 0.11444 | 0.15564 | 0.050354 | 0.091553 | 0.13275 | -121.0236 | -120.9961 | 0.1831 | 0.20142 | 0.15106 | 0.068665 | 0.018311 | 0.18311 | 120.8817 | 0.050354 | -0.027466 | 120.8588 | -0.054932 | 120.9229 | 0.077819 | -121.0373 | -120.9686 | 120.9457 | 0.10528 | 4.9988 | 0.091552
2185.7188 | 121.0876 | -0.17853 | 120.8862 | 0.005951 | 6.978 | 0.064405 | 0.062151 | 0.00078177 | -0.0086773 | -0.001726 | -0.0036011 | 0.0020188 | 0.015887 | 0.011068 | -0.0051313 | 0.028521 | -0.001583 | 4.6509 | 120.8221 | -0.1236 | 120.6848 | -0.036621 | -0.18768 | -0.17853 | -0.10529 | -0.082397 | -0.054932 | -0.041199 | -0.018311 | -0.050354 | 0.059509 | 0.054932 | -0.064086 | -0.20142 | 0.14191 | 0 | -0.009155 | -0.054932 | -0.064087 | 0.1236 | -120.9686 | -120.9274 | 0.16022 | 0.23804 | 0.12817 | 0.11444 | 0.004578 | 0.086975 | 120.8084 | 0.036621 | 0.013733 | 120.9457 | -0.027465 | 121.0007 | 0.096131 | -121.0098 | -120.9412 | 120.8633 | 0.13733 | 4.8294 | 0.073242
2187.4062 | 120.5795 | -0.21057 | 120.4788 | -0.009308 | 6.9771 | 0.063551 | 0.062792 | 0.00078177 | -0.0046185 | -0.0019396 | -0.0036011 | 0.004155 | 0.016528 | 0.0053 | -0.0064129 | 0.025957 | -0.0030784 | 4.628 | 120.3735 | -0.13733 | 120.2591 | -0.022888 | -0.16937 | -0.1831 | -0.16479 | -0.091553 | -0.054932 | -0.082397 | -0.07782 | -0.14191 | 0 | 0.073242 | -0.10529 | -0.21973 | 0.18768 | 0.027466 | 0.041198 | -0.045776 | -0.032044 | 0.15564 | -120.5704 | -120.5612 | 0.13275 | 0.21057 | 0.068664 | 0.054932 | -0.086975 | 0.11444 | 120.3964 | -0.022888 | -0.027465 | 120.5109 | -0.036621 | 120.5841 | 0.11902 | -120.6161 | -120.5338 | 120.4697 | 0.12817 | 4.8386 | 0.045776
2189.1406 | 120.9183 | -0.16479 | 120.6528 | -0.016937 | 6.9774 | 0.063978 | 0.061297 | -0.001568 | -0.0084637 | -0.003435 | -0.00054933 | 9.6204e-05 | 0.013324 | 0.0050864 | -0.0096173 | 0.026171 | 0.0026896 | 4.7241 | 120.5429 | -0.09613 | 120.5841 | 0.11902 | -0.018311 | -0.045776 | -0.013733 | -0.10529 | -0.041199 | 0.009155 | 0.091553 | 0.054932 | 0.09613 | 0.068665 | -0.10986 | -0.068665 | 0.28381 | 0.11902 | 0.14648 | 0.050354 | 0.077819 | 0.1236 | -120.7581 | -120.6436 | 0.25635 | 0.26092 | 0.21973 | 0.13733 | 0.096131 | 0.21515 | 120.6802 | 0.13275 | 0.050354 | 120.639 | -0.064087 | 120.7077 | 0.059509 | -120.7489 | -120.694 | 120.7489 | 0.17395 | 4.8889 | 0.15106
2190.875 | 120.8405 | -0.16479 | 120.6024 | -0.009308 | 6.9789 | 0.063551 | 0.059588 | 0.0014228 | -0.0084637 | -0.0045032 | -0.00054933 | -0.0003312 | 0.014178 | 0.01299 | -0.0083355 | 0.027239 | -0.00436 | 4.66 | 120.4742 | -0.10071 | 120.52 | 0.10529 | -0.013733 | -0.041199 | -0.009155 | -0.091553 | -0.032043 | 0.013733 | 0.082397 | 0.045776 | 0.09613 | 0.064087 | -0.12817 | -0.082397 | 0.27008 | 0.1236 | 0.15106 | 0.059509 | 0.086975 | 0.13275 | -120.694 | -120.5887 | 0.24719 | 0.26092 | 0.21057 | 0.12817 | 0.077819 | 0.20599 | 120.6207 | 0.11444 | 0.045776 | 120.575 | -0.05951 | 120.639 | 0.073242 | -120.7031 | -120.6345 | 120.6848 | 0.17853 | 4.8248 | 0.15564
2192.5469 | 120.8588 | -0.20599 | 120.7489 | -0.0016785 | 6.9782 | 0.063978 | 0.063647 | 0.0046272 | -0.0067547 | -0.0030078 | -0.00054933 | 0.003514 | 0.017383 | 0.014486 | -0.0049175 | 0.026171 | 0.00033961 | 4.6875 | 120.6802 | -0.14191 | 120.5246 | -0.07782 | -0.19226 | -0.18768 | -0.17395 | -0.068665 | -0.068665 | -0.10986 | -0.064087 | -0.1236 | 0 | 0.064087 | -0.068664 | -0.2243 | 0.12817 | 0.018311 | 0.013733 | -0.045776 | -0.050354 | 0.13733 | -120.8176 | -120.8588 | 0.14191 | 0.20599 | 0.082398 | 0.068665 | -0.054931 | 0.064087 | 120.6665 | 0.004578 | -0.041198 | 120.8221 | 0 | 120.8862 | 0.13733 | -120.8908 | -120.8176 | 120.7306 | 0.096131 | 4.8935 | 0.032044
2194.2812 | 120.9045 | -0.21057 | 120.7855 | -0.009308 | 6.9797 | 0.065687 | 0.061724 | 0.00185 | -0.0080365 | -0.0025806 | -0.00054933 | 0.0054368 | 0.015033 | 0.011709 | -0.0068403 | 0.028094 | 0.00033961 | 4.6829 | 120.7169 | -0.14191 | 120.5429 | -0.064087 | -0.17853 | -0.16937 | -0.14191 | -0.068665 | -0.054932 | -0.086975 | -0.059509 | -0.10529 | 0.018311 | 0.068664 | -0.068664 | -0.24261 | 0.14648 | 0.041198 | 0.032043 | -0.027466 | -0.036621 | 0.15564 | -120.8542 | -120.8725 | 0.15106 | 0.22888 | 0.10529 | 0.073243 | -0.050354 | 0.07782 | 120.6848 | -0.004577 | -0.032043 | 120.8588 | -0.013733 | 120.9274 | 0.14191 | -120.9274 | -120.8405 | 120.7535 | 0.1236 | 4.8935 | 0.068664
2195.9531 | 120.9961 | -0.17853 | 120.7901 | -0.0016785 | 6.9769 | 0.064192 | 0.058734 | -0.0028498 | -0.0071821 | -0.0055712 | -0.00054933 | 0.0003098 | 0.013751 | 0.018545 | -0.0091901 | 0.02788 | -0.0024374 | 4.66 | 120.6894 | -0.11444 | 120.639 | 0.027466 | -0.10071 | -0.10986 | -0.086975 | -0.09613 | -0.050354 | -0.050354 | 0.018311 | -0.022888 | 0.064087 | 0.064087 | -0.10071 | -0.15106 | 0.20599 | 0.068665 | 0.07782 | 0.004578 | 0.013733 | 0.12817 | -120.8862 | -120.8405 | 0.19684 | 0.24261 | 0.15564 | 0.11444 | 0.027466 | 0.14191 | 120.7535 | 0.068665 | 0 | 120.8038 | -0.045776 | 120.8679 | 0.082398 | -120.9045 | -120.8405 | 120.8176 | 0.12817 | 4.8386 | 0.091553
2197.7031 | 120.9732 | -0.19684 | 120.8542 | -0.009308 | 6.9801 | 0.062696 | 0.06386 | 0.0046272 | -0.0080365 | -0.002367 | 0.0025025 | 0.0047958 | 0.016101 | 0.018758 | -0.0098309 | 0.027025 | 0.00012601 | 4.7333 | 120.7306 | -0.14191 | 120.6116 | -0.045776 | -0.13733 | -0.15106 | -0.13275 | -0.064087 | -0.086975 | -0.064087 | -0.009155 | -0.054932 | 0.041199 | 0.054931 | -0.1236 | -0.24262 | 0.15106 | 0.045776 | 0.059509 | -0.009155 | 0.004578 | 0.10986 | -120.9183 | -120.9183 | 0.18768 | 0.23804 | 0.14191 | 0.12817 | 0.032043 | 0.096131 | 120.7535 | 0.07782 | 0.022888 | 120.8725 | 0.022888 | 120.9274 | 0.13275 | -120.9961 | -120.9412 | 120.8084 | 0.13275 | 4.9301 | 0.064087
2199.4531 | 120.9686 | -0.21515 | 120.8359 | -0.009308 | 6.9793 | 0.065687 | 0.061938 | -0.0013544 | -0.010814 | -0.0025806 | 0.0025025 | 0.0037278 | 0.016528 | 0.011709 | -0.010258 | 0.027025 | -0.00436 | 4.7424 | 120.7077 | -0.1236 | 120.6711 | 0.013733 | -0.11444 | -0.10529 | -0.11444 | -0.082397 | -0.059509 | -0.10071 | -0.022888 | -0.086975 | -0.004578 | 0.091553 | -0.12817 | -0.16479 | 0.22888 | 0.10986 | 0.10071 | 0.01831 | 0.009155 | 0.15564 | -120.9183 | -120.9366 | 0.19226 | 0.21057 | 0.12817 | 0.054931 | -0.027466 | 0.13733 | 120.7947 | 0.036621 | -0.041199 | 120.8313 | -0.022888 | 120.9229 | 0.13275 | -120.9595 | -120.8954 | 120.8862 | 0.11444 | 4.9576 | 0.10071
2201.1875 | 121.0464 | -0.16937 | 120.8588 | 0.005951 | 6.9763 | 0.062696 | 0.060015 | 0.0029182 | -0.0073957 | -0.002367 | -0.0036011 | 0.0022324 | 0.015246 | 0.012563 | -0.0064129 | 0.027025 | -0.002651 | 4.6326 | 120.7397 | -0.10986 | 120.6848 | 0.018311 | -0.09613 | -0.10529 | -0.086975 | -0.1236 | -0.064087 | -0.050354 | 0.022888 | -0.027466 | 0.054932 | 0.05951 | -0.11902 | -0.17395 | 0.18768 | 0.064087 | 0.073243 | 0.004577 | 0.013733 | 0.10529 | -120.9824 | -120.9091 | 0.19226 | 0.22431 | 0.14191 | 0.11902 | 0.036621 | 0.12817 | 120.7947 | 0.086975 | 0.013733 | 120.8496 | -0.059509 | 120.9091 | 0.045777 | -120.9686 | -120.9229 | 120.8542 | 0.11902 | 4.8019 | 0.082398
2202.875 | 121.0419 | -0.20599 | 120.8588 | 0.02121 | 6.9801 | 0.063978 | 0.063433 | 0.00099557 | -0.0078229 | -0.0032214 | -0.0036011 | 0.0026596 | 0.014392 | 0.004659 | -0.0076947 | 0.026171 | -0.0041464 | 4.715 | 120.7809 | -0.13275 | 120.7123 | 0.027466 | -0.10986 | -0.13275 | -0.073242 | -0.059509 | -0.059509 | -0.054932 | 0.018311 | -0.036621 | 0.050354 | 0.073243 | -0.07782 | -0.14648 | 0.23346 | 0.073243 | 0.096131 | 0 | 0.022888 | 0.14649 | -120.9183 | -120.9137 | 0.22431 | 0.25635 | 0.16937 | 0.10986 | 0.022888 | 0.16022 | 120.845 | 0.07782 | 0.004577 | 120.9137 | 0 | 120.9869 | 0.14649 | -120.9915 | -120.9183 | 120.9183 | 0.15106 | 4.921 | 0.13275
2204.6094 | 121.0602 | -0.20142 | 120.9091 | 0.01358 | 6.9774 | 0.063123 | 0.063433 | -0.00028623 | -0.0097455 | -0.0038622 | -0.00054933 | 0.004155 | 0.016742 | 0.0057272 | -0.0083355 | 0.028094 | -0.00436 | 4.7195 | 120.8176 | -0.13733 | 120.6985 | -0.027466 | -0.11444 | -0.12817 | -0.1236 | -0.064087 | -0.068665 | -0.073242 | 0.004578 | -0.054932 | 0.036621 | 0.064087 | -0.091553 | -0.21057 | 0.17395 | 0.073242 | 0.086975 | 0.009155 | 0.022888 | 0.13275 | -120.9732 | -120.9824 | 0.20599 | 0.23804 | 0.14648 | 0.10529 | 0.013733 | 0.10986 | 120.8359 | 0.073243 | -0.004577 | 120.9549 | 0.004578 | 121.019 | 0.13733 | -121.0464 | -120.9778 | 120.9 | 0.12817 | 4.921 | 0.07782
2206.3438 | 121.0648 | -0.19226 | 120.845 | -0.0016785 | 6.9769 | 0.064832 | 0.06386 | 0.0024908 | -0.0082501 | -0.00087163 | 0.0025025 | 0.003514 | 0.01546 | 0.0040182 | -0.010258 | 0.027453 | -0.0017966 | 4.7241 | 120.8267 | -0.13275 | 120.7352 | 0.009155 | -0.10529 | -0.10986 | -0.07782 | -0.091553 | -0.050354 | -0.041199 | 0.018311 | -0.041199 | 0.068665 | 0.05951 | -0.018311 | -0.10986 | 0.20142 | 0.082398 | 0.086975 | 0.022888 | 0.027465 | 0.14191 | -120.9366 | -120.8862 | 0.21057 | 0.26093 | 0.15106 | 0.11902 | 0.009155 | 0.14191 | 120.8679 | 0.068665 | 0.009155 | 120.9595 | -0.041199 | 121.019 | 0.10071 | -120.9778 | -120.8954 | 120.9274 | 0.15106 | 4.9164 | 0.11444
2208.0938 | 121.0098 | -0.20599 | 120.9183 | -0.0016785 | 6.9786 | 0.065901 | 0.062365 | 0.0050544 | -0.0078229 | -0.003435 | -0.0036011 | 0.0022324 | 0.015887 | 0.006368 | -0.0081219 | 0.026171 | -0.005001 | 4.6463 | 120.8496 | -0.14191 | 120.6711 | -0.073242 | -0.18768 | -0.20599 | -0.19226 | -0.082397 | -0.064087 | -0.11902 | -0.068665 | -0.11444 | -0.004578 | 0.064087 | -0.068665 | -0.24719 | 0.13275 | 0 | 0.018311 | -0.064087 | -0.045776 | 0.14191 | -121.0007 | -121.0373 | 0.13733 | 0.20142 | 0.091553 | 0.059509 | -0.050354 | 0.068665 | 120.813 | -0.004578 | -0.054932 | 120.9915 | -0.01831 | 121.0556 | 0.1236 | -121.0602 | -120.9824 | 120.8771 | 0.086975 | 4.8523 | 0.013733
2209.7812 | 121.0556 | -0.19684 | 120.9137 | -0.009308 | 6.9791 | 0.064405 | 0.06386 | 0.0022772 | -0.0076093 | -0.0036486 | -0.0036011 | 0.0026596 | 0.014819 | 0.01235 | -0.0068403 | 0.028948 | -0.0028646 | 4.66 | 120.8496 | -0.15106 | 120.694 | -0.082397 | -0.20142 | -0.19684 | -0.16479 | -0.068665 | -0.064087 | -0.10986 | -0.07782 | -0.11902 | 0.013733 | 0.045776 | -0.064087 | -0.21973 | 0.11444 | 0 | -0.004578 | -0.045776 | -0.050354 | 0.13275 | -120.9824 | -121.0236 | 0.11902 | 0.21057 | 0.077819 | 0.07782 | -0.054932 | 0.068665 | 120.845 | -0.013733 | -0.045776 | 121.0007 | -0.004578 | 121.0464 | 0.12817 | -121.0648 | -120.9778 | 120.8908 | 0.086975 | 4.8569 | 0.032043
2211.5312 | 121.1655 | -0.16937 | 120.8817 | -0.0016785 | 6.9799 | 0.069105 | 0.061297 | 0.0020636 | -0.0052595 | -0.0019396 | 0.0055543 | 0.0018052 | 0.01311 | 0.0085044 | -0.0064129 | 0.028307 | -0.0052146 | 4.6875 | 120.8038 | -0.091553 | 120.8267 | 0.091553 | -0.059509 | -0.059509 | 0.004578 | -0.10986 | -0.041199 | 0.022888 | 0.073242 | 0.032043 | 0.10529 | 0.07782 | -0.07782 | -0.054932 | 0.26093 | 0.10986 | 0.10986 | 0.032044 | 0.032044 | 0.12817 | -120.9915 | -120.8588 | 0.24261 | 0.27466 | 0.20142 | 0.14649 | 0.073242 | 0.18311 | 120.9183 | 0.11444 | 0.064087 | 120.8954 | -0.068664 | 120.9732 | 0.05951 | -120.9732 | -120.9229 | 120.9961 | 0.19226 | 4.8569 | 0.17395
2213.2812 | 121.1426 | -0.16937 | 120.9045 | 0.02121 | 6.9791 | 0.065046 | 0.060656 | 0.0041998 | -0.0050457 | -0.0030078 | -0.00054933 | 0.0028732 | 0.015246 | 0.007009 | -0.0076947 | 0.028307 | -0.0017966 | 4.6692 | 120.845 | -0.10986 | 120.8405 | 0.10071 | -0.045776 | -0.064087 | 0.018311 | -0.10986 | -0.045776 | 0.004578 | 0.068665 | 0.022888 | 0.10529 | 0.05951 | -0.059509 | -0.064087 | 0.27008 | 0.10529 | 0.1236 | 0.045776 | 0.064087 | 0.1236 | -121.0144 | -120.9 | 0.23804 | 0.27466 | 0.19226 | 0.15106 | 0.068664 | 0.21057 | 120.9503 | 0.11444 | 0.050354 | 120.9549 | -0.064087 | 121.0144 | 0.05951 | -121.0144 | -120.9503 | 121.0098 | 0.17395 | 4.8386 | 0.18768
2214.9531 | 121.1426 | -0.19226 | 120.932 | 0.005951 | 6.9797 | 0.063978 | 0.059802 | 0.0048408 | -0.0069683 | -0.0047168 | -0.0066527 | 0.0005234 | 0.014178 | 0.012136 | -0.010258 | 0.027453 | 0.0016214 | 4.66 | 120.8633 | -0.10529 | 120.7809 | 0.027466 | -0.09613 | -0.091553 | -0.07782 | -0.11444 | -0.050354 | -0.045776 | 0.022888 | -0.013733 | 0.054932 | 0.086975 | -0.068665 | -0.15106 | 0.21973 | 0.10071 | 0.096131 | 0.013733 | 0.009156 | 0.14191 | -121.0464 | -120.9778 | 0.21515 | 0.24719 | 0.17853 | 0.10529 | 0.036621 | 0.13275 | 120.8862 | 0.073242 | 0.004578 | 120.9686 | -0.064087 | 121.0556 | 0.07782 | -121.0373 | -120.9824 | 120.9732 | 0.14648 | 4.8523 | 0.11444
2216.7031 | 121.0831 | -0.21973 | 120.9549 | -0.009308 | 6.9786 | 0.061415 | 0.06087 | 0.0016364 | -0.0097455 | -0.0012988 | -0.00054933 | 0.0026596 | 0.012897 | 0.011495 | -0.010686 | 0.026171 | -0.002651 | 4.7058 | 120.8267 | -0.09613 | 120.8176 | 0.050354 | -0.064087 | -0.082397 | -0.091553 | -0.073242 | -0.054932 | -0.10071 | -0.004578 | -0.068665 | 0 | 0.1236 | -0.12817 | -0.13733 | 0.27008 | 0.13733 | 0.15564 | 0.013733 | 0.032043 | 0.16479 | -121.0281 | -121.0556 | 0.21515 | 0.21973 | 0.15106 | 0.054932 | -0.013733 | 0.14648 | 120.9137 | 0.050354 | -0.045776 | 120.9229 | -0.01831 | 121.0464 | 0.14649 | -121.051 | -121.0098 | 121.0373 | 0.11902 | 4.9255 | 0.12817
2218.3906 | 121.1609 | -0.1831 | 120.9503 | -0.0016785 | 6.978 | 0.068037 | 0.061083 | -0.00071343 | -0.0065411 | -0.0049304 | -0.00054933 | 0.0013778 | 0.015887 | 0.010854 | -0.0081219 | 0.028094 | -0.0028646 | 4.5914 | 120.8542 | -0.10529 | 120.7809 | 0.032043 | -0.082397 | -0.10986 | -0.082397 | -0.09613 | -0.050354 | -0.041199 | 0.018311 | -0.027466 | 0.073242 | 0.077819 | -0.09613 | -0.16937 | 0.21515 | 0.073242 | 0.10071 | -0.004577 | 0.022889 | 0.13275 | -121.0464 | -120.9915 | 0.20142 | 0.25635 | 0.15564 | 0.1236 | 0.022888 | 0.13733 | 120.8862 | 0.068665 | 0.009155 | 120.9595 | -0.045776 | 121.0373 | 0.086975 | -121.0556 | -121.0007 | 120.9641 | 0.14191 | 4.7745 | 0.10071
2220.125 | 121.2067 | -0.15106 | 120.9549 | -0.0016785 | 6.9789 | 0.063123 | 0.064715 | 0.0020636 | -0.0035505 | -0.0010852 | -0.0036011 | 0.0026596 | 0.014392 | 0.013418 | -0.0040631 | 0.027239 | -0.0013694 | 4.5776 | 120.8588 | -0.10529 | 120.845 | 0.059509 | -0.07782 | -0.073242 | -0.004578 | -0.10986 | -0.036621 | 0.004578 | 0.054932 | 0.018311 | 0.11444 | 0.045776 | -0.09613 | -0.10986 | 0.21057 | 0.07782 | 0.073242 | 0.032044 | 0.027466 | 0.11444 | -121.0648 | -120.9503 | 0.20599 | 0.2655 | 0.16937 | 0.15106 | 0.054932 | 0.16479 | 120.9503 | 0.091553 | 0.041199 | 120.9641 | -0.073242 | 121.0098 | 0.041199 | -121.0602 | -120.9915 | 120.9961 | 0.15564 | 4.7287 | 0.14648
2221.8594 | 121.2021 | -0.19684 | 120.9503 | -0.0016785 | 6.978 | 0.063123 | 0.061938 | 0.0027044 | -0.0076093 | -0.0042896 | -0.0036011 | 0.003514 | 0.017596 | 0.016836 | -0.0081219 | 0.028734 | 0.00055321 | 4.6005 | 120.8725 | -0.10529 | 120.845 | 0.068665 | -0.082397 | -0.086975 | -0.054932 | -0.10071 | -0.045776 | -0.027466 | 0.013733 | -0.032043 | 0.054932 | 0.091552 | -0.077819 | -0.10528 | 0.2655 | 0.10986 | 0.11444 | 0.018311 | 0.022889 | 0.15106 | -121.051 | -120.9778 | 0.21057 | 0.25177 | 0.1648 | 0.10071 | 0.013733 | 0.17395 | 120.9503 | 0.059509 | 0.01831 | 120.9778 | -0.054932 | 121.0693 | 0.09613 | -121.0556 | -120.9961 | 121.0419 | 0.16937 | 4.7974 | 0.14191
2223.5938 | 121.2433 | -0.15106 | 120.9457 | -0.0016785 | 6.9774 | 0.062055 | 0.061297 | 0.00014097 | -0.0099591 | -0.0038622 | -0.0036011 | 0.0015914 | 0.015674 | 0.015554 | -0.0074811 | 0.024889 | -0.0022238 | 4.6921 | 120.8588 | -0.091553 | 120.9137 | 0.1236 | -0.013733 | -0.050354 | 0.009155 | -0.10986 | -0.036621 | 0.022888 | 0.09613 | 0.064087 | 0.10529 | 0.059509 | -0.086975 | -0.032044 | 0.27466 | 0.10071 | 0.13733 | 0.041199 | 0.07782 | 0.11444 | -121.0556 | -120.9229 | 0.24719 | 0.25635 | 0.21515 | 0.14191 | 0.10071 | 0.21515 | 121.0052 | 0.13275 | 0.059509 | 120.9503 | -0.073242 | 121.0098 | 0.041199 | -121.0373 | -120.9824 | 121.0648 | 0.17395 | 4.8431 | 0.16022
2225.2656 | 121.2479 | -0.17853 | 120.9412 | -0.009308 | 6.9776 | 0.062483 | 0.062792 | -0.0030634 | -0.0056867 | -0.0036486 | -0.0036011 | 0.0033004 | 0.016101 | 0.013418 | -0.0074811 | 0.026385 | -0.0020102 | 4.6555 | 120.8496 | -0.11444 | 120.9229 | 0.11902 | -0.018311 | -0.036621 | 0.013733 | -0.10529 | -0.022888 | 0.009155 | 0.10071 | 0.045776 | 0.10986 | 0.064087 | -0.091553 | -0.01831 | 0.29755 | 0.14191 | 0.16022 | 0.07782 | 0.09613 | 0.15564 | -121.0464 | -120.932 | 0.27924 | 0.28839 | 0.2243 | 0.13275 | 0.068664 | 0.23346 | 121.0373 | 0.1236 | 0.032043 | 120.9641 | -0.082398 | 121.0281 | 0.073242 | -121.0556 | -120.9641 | 121.1014 | 0.18768 | 4.834 | 0.19226
2227 | 121.2067 | -0.17853 | 120.9641 | 0.005951 | 6.9793 | 0.063123 | 0.06087 | 0.0014228 | -0.0082501 | -0.0038622 | 0.0025025 | 0.0020188 | 0.011615 | 0.020681 | -0.0085491 | 0.027453 | -0.0054282 | 4.5364 | 120.9045 | -0.10529 | 120.8405 | 0.022888 | -0.10071 | -0.10529 | -0.07782 | -0.10071 | -0.050354 | -0.027466 | 0.032043 | 0 | 0.07782 | 0.073242 | -0.059509 | -0.1236 | 0.20142 | 0.073242 | 0.07782 | 0 | 0.004578 | 0.12817 | -121.0648 | -120.9915 | 0.21057 | 0.25635 | 0.17853 | 0.12817 | 0.050354 | 0.12817 | 120.9457 | 0.082397 | 0.022888 | 121.0098 | -0.050354 | 121.0831 | 0.07782 | -121.0693 | -121.0144 | 121.019 | 0.15106 | 4.715 | 0.10071
2228.6875 | 121.1792 | -0.20142 | 120.9915 | -0.0016785 | 6.9793 | 0.063123 | 0.064501 | 0.0022772 | -0.0078229 | -0.002367 | 0.0025025 | 0.0028732 | 0.016314 | 0.01299 | -0.0064129 | 0.028948 | -0.0013694 | 4.5547 | 120.9412 | -0.13275 | 120.8038 | -0.036621 | -0.18768 | -0.16937 | -0.10529 | -0.073242 | -0.059509 | -0.064087 | -0.022888 | -0.068665 | 0.054932 | 0.068665 | -0.050354 | -0.18768 | 0.1648 | 0.032043 | 0.013733 | -0.036622 | -0.054932 | 0.14191 | -121.0648 | -121.0556 | 0.17853 | 0.25635 | 0.13275 | 0.11444 | -0.009156 | 0.09613 | 120.9366 | 0.036621 | -0.004578 | 121.0739 | -0.013733 | 121.1426 | 0.12817 | -121.1243 | -121.051 | 121.0052 | 0.13733 | 4.7562 | 0.09613
2230.4375 | 121.1472 | -0.18768 | 121.019 | -0.009308 | 6.9767 | 0.065473 | 0.064074 | -0.003277 | -0.0063275 | -0.0036486 | -0.0066527 | 0.0033004 | 0.014605 | 0.006368 | -0.0079083 | 0.027239 | -0.0022238 | 4.5822 | 120.9549 | -0.13275 | 120.7855 | -0.059509 | -0.20599 | -0.17853 | -0.15564 | -0.068665 | -0.064087 | -0.10071 | -0.064087 | -0.1236 | 0.004578 | 0.054932 | -0.064087 | -0.23346 | 0.12817 | 0.009155 | -0.018311 | -0.045777 | -0.073243 | 0.1236 | -121.0876 | -121.1197 | 0.1236 | 0.19226 | 0.064087 | 0.068665 | -0.059509 | 0.073242 | 120.9183 | 0 | -0.036621 | 121.0876 | -0.004578 | 121.1426 | 0.11902 | -121.1517 | -121.0831 | 120.9732 | 0.086975 | 4.7699 | 0.032043
2232.1875 | 121.2296 | -0.15564 | 120.9961 | -0.0016785 | 6.9767 | 0.066114 | 0.060229 | 0.0020636 | -0.0067547 | -0.0019396 | -0.00054933 | 0.0033004 | 0.013751 | 0.0072226 | -0.010258 | 0.028948 | 0.0011942 | 4.6097 | 120.9457 | -0.10529 | 120.8954 | 0.09613 | -0.091553 | -0.059509 | -0.027466 | -0.11444 | -0.041199 | -0.022888 | 0.027466 | -0.018311 | 0.059509 | 0.050354 | -0.050354 | -0.10071 | 0.25177 | 0.096131 | 0.064087 | 0.045777 | 0.013733 | 0.11444 | -121.1105 | -121.019 | 0.18311 | 0.21515 | 0.13733 | 0.10071 | 0.022888 | 0.20142 | 121.0007 | 0.068665 | 0.018311 | 121.051 | -0.073242 | 121.1014 | 0.041199 | -121.1014 | -121.0373 | 121.051 | 0.13275 | 4.7653 | 0.12817
2233.875 | 121.1472 | -0.21057 | 121.0236 | -0.009308 | 6.9784 | 0.063123 | 0.062792 | -0.0013544 | -0.0076093 | -0.0042896 | -0.0036011 | 0.0030868 | 0.013537 | 0.013204 | -0.013249 | 0.024889 | -0.00051479 | 4.5822 | 120.9641 | -0.12817 | 120.813 | -0.036621 | -0.14191 | -0.15106 | -0.16022 | -0.086975 | -0.091553 | -0.1236 | -0.050354 | -0.09613 | -0.013733 | 0.082397 | -0.05951 | -0.21057 | 0.17395 | 0.059509 | 0.068664 | -0.022888 | -0.013733 | 0.11902 | -121.1105 | -121.1472 | 0.16022 | 0.19684 | 0.11444 | 0.07782 | -0.004577 | 0.091553 | 120.9412 | 0.041199 | -0.032043 | 121.0922 | 0.004578 | 121.1746 | 0.1236 | -121.1517 | -121.1151 | 121.0236 | 0.086975 | 4.7928 | 0.050354
2235.6094 | 121.3028 | -0.16022 | 121.0327 | -0.0016785 | 6.9774 | 0.064192 | 0.05852 | -0.00071343 | -0.0082501 | -0.003435 | -0.0066527 | -0.0001174 | 0.010974 | 0.003591 | -0.010045 | 0.026385 | -0.002651 | 4.6097 | 120.9229 | -0.086975 | 120.9457 | 0.13733 | -0.013733 | -0.027466 | 0.032043 | -0.10529 | -0.027466 | 0.032043 | 0.11444 | 0.041199 | 0.10986 | 0.073242 | -0.10986 | -0.086975 | 0.29755 | 0.13275 | 0.14648 | 0.059509 | 0.073242 | 0.13275 | -121.138 | -121.0007 | 0.27466 | 0.27008 | 0.20142 | 0.13733 | 0.068665 | 0.2243 | 121.0327 | 0.14191 | 0.059509 | 121.0098 | -0.07782 | 121.0831 | 0.054931 | -121.1197 | -121.0602 | 121.106 | 0.19226 | 4.7699 | 0.19226
2237.2969 | 121.2936 | -0.14191 | 121.019 | -0.0016785 | 6.9763 | 0.062269 | 0.063006 | -0.004345 | -0.0069683 | -0.0032214 | -0.0066527 | 0.0015914 | 0.017169 | 0.011068 | -0.0068403 | 0.026171 | -0.0020102 | 4.5731 | 120.9183 | -0.10071 | 120.9549 | 0.09613 | -0.004578 | -0.022888 | 0 | -0.10529 | -0.027466 | 0.027466 | 0.10071 | 0.054932 | 0.11902 | 0.041199 | -0.10071 | -0.064087 | 0.23804 | 0.11902 | 0.13733 | 0.07782 | 0.09613 | 0.11444 | -121.1243 | -120.9915 | 0.24262 | 0.26093 | 0.19684 | 0.14649 | 0.082398 | 0.19684 | 121.0556 | 0.12817 | 0.054932 | 121.019 | -0.07782 | 121.0602 | 0.036621 | -121.1197 | -121.0464 | 121.0968 | 0.16937 | 4.715 | 0.14191
2239.0469 | 121.2708 | -0.16479 | 121.019 | -0.0016785 | 6.9778 | 0.062483 | 0.058947 | -0.0019952 | -0.010386 | -0.0030078 | -0.0036011 | 0.0005234 | 0.012469 | 0.012563 | -0.0081219 | 0.027453 | -0.0028646 | 4.5502 | 120.9412 | -0.10071 | 120.9091 | 0.045776 | -0.082397 | -0.073242 | -0.054932 | -0.10071 | -0.059509 | -0.027466 | 0.045776 | 0.018311 | 0.10986 | 0.064087 | -0.07782 | -0.10986 | 0.21057 | 0.091553 | 0.082398 | 0.027466 | 0.018311 | 0.10529 | -121.1197 | -121.0464 | 0.21057 | 0.27466 | 0.18311 | 0.16937 | 0.07782 | 0.14648 | 121.0098 | 0.10528 | 0.032043 | 121.0419 | -0.041199 | 121.106 | 0.064087 | -121.1197 | -121.0785 | 121.0739 | 0.13733 | 4.715 | 0.10986
2240.7969 | 121.2158 | -0.1831 | 121.051 | 0.005951 | 6.9786 | 0.066114 | 0.063006 | 0.0016364 | -0.0067547 | -1.7026e-05 | 0.0025025 | 0.0043686 | 0.012897 | 0.0048728 | -0.0053449 | 0.026812 | -0.0037192 | 4.6005 | 120.9595 | -0.14191 | 120.9229 | 0.032043 | -0.10071 | -0.11444 | -0.086975 | -0.068665 | -0.064087 | -0.045776 | -0.009155 | -0.07782 | 0.045776 | 0.041198 | -0.091552 | -0.12817 | 0.21515 | 0.068664 | 0.082397 | 0.027466 | 0.041199 | 0.11902 | -121.1197 | -121.0968 | 0.17395 | 0.22888 | 0.10528 | 0.10986 | -0.013733 | 0.17395 | 121.0648 | 0.054932 | 0.018311 | 121.1014 | -0.004578 | 121.1426 | 0.11444 | -121.1929 | -121.1151 | 121.106 | 0.13733 | 4.7836 | 0.09613
2242.5469 | 121.3486 | -0.15564 | 121.0281 | -0.009308 | 6.9774 | 0.062055 | 0.060015 | 0.0029182 | -0.010173 | -0.003435 | -0.0036011 | 0.0020188 | 0.012897 | 0.011922 | -0.0081219 | 0.02553 | -0.0028646 | 4.5914 | 120.9549 | -0.07782 | 120.9824 | 0.13275 | 0 | -0.032043 | 0.032043 | -0.11444 | -0.032043 | 0.009155 | 0.10071 | 0.050354 | 0.091553 | 0.07782 | -0.073242 | -0.045776 | 0.28839 | 0.1236 | 0.15564 | 0.045777 | 0.07782 | 0.1236 | -121.1426 | -121.019 | 0.25635 | 0.24719 | 0.20599 | 0.1236 | 0.082397 | 0.21057 | 121.0602 | 0.13275 | 0.041198 | 121.0327 | -0.082398 | 121.1105 | 0.041199 | -121.106 | -121.0602 | 121.138 | 0.16479 | 4.747 | 0.18768
2244.2969 | 121.2296 | -0.20142 | 121.0968 | 0.005951 | 6.9782 | 0.063764 | 0.062579 | -0.00071343 | -0.0082501 | -0.0021532 | -0.0066527 | 0.0050094 | 0.013324 | 0.0078634 | -0.0094037 | 0.027239 | -0.0022238 | 4.5547 | 121.0144 | -0.13733 | 120.8954 | -0.013733 | -0.11444 | -0.13733 | -0.14648 | -0.07782 | -0.054932 | -0.068665 | 0.004578 | -0.068665 | 0.036621 | 0.064087 | -0.082398 | -0.20142 | 0.18768 | 0.064087 | 0.086975 | 0 | 0.022888 | 0.14648 | -121.1746 | -121.1655 | 0.20599 | 0.23804 | 0.13275 | 0.091553 | -0.013733 | 0.1236 | 121.0327 | 0.05951 | -0.013733 | 121.1517 | -0.022888 | 121.2158 | 0.1236 | -121.2341 | -121.1517 | 121.0968 | 0.13275 | 4.7562 | 0.054932
2245.9844 | 121.3257 | -0.15564 | 121.0419 | -0.0016785 | 6.9774 | 0.062269 | 0.057879 | -0.0024224 | -0.0097455 | -0.0012988 | -0.00054933 | 0.000737 | 0.014178 | 0.015981 | -0.0098309 | 0.026385 | -0.0058554 | 4.5593 | 120.9366 | -0.10529 | 120.9961 | 0.14191 | -0.004578 | -0.018311 | 0.022888 | -0.11902 | -0.041199 | 0.009155 | 0.10529 | 0.054932 | 0.10529 | 0.050354 | -0.10529 | -0.045776 | 0.29755 | 0.13733 | 0.15106 | 0.086975 | 0.10071 | 0.11444 | -121.1609 | -121.0327 | 0.26093 | 0.26093 | 0.21057 | 0.14649 | 0.096131 | 0.24719 | 121.1014 | 0.14649 | 0.050354 | 121.0419 | -0.07782 | 121.0922 | 0.036621 | -121.1472 | -121.0831 | 121.1517 | 0.16479 | 4.715 | 0.17853
2247.7344 | 121.1838 | -0.20599 | 121.1151 | -0.0016785 | 6.9797 | 0.064832 | 0.065783 | 0.0014228 | -0.0095319 | -0.001726 | -0.0066527 | 0.0050094 | 0.01546 | 0.0048728 | -0.0061993 | 0.025744 | -0.0024374 | 4.4861 | 120.9961 | -0.13733 | 120.8817 | -0.045776 | -0.17853 | -0.17853 | -0.19684 | -0.07782 | -0.082397 | -0.11902 | -0.073242 | -0.13275 | -0.004578 | 0.068665 | -0.11902 | -0.23346 | 0.16022 | 0.027466 | 0.027466 | -0.041199 | -0.041199 | 0.1236 | -121.1929 | -121.2341 | 0.13275 | 0.20142 | 0.073243 | 0.077819 | -0.050354 | 0.091553 | 121.019 | 0.009155 | -0.036622 | 121.1334 | 0.004577 | 121.2021 | 0.12817 | -121.2524 | -121.1975 | 121.0876 | 0.086975 | 4.6921 | 0.009156
2249.4062 | 121.3211 | -0.16022 | 121.0419 | 0.005951 | 6.9786 | 0.066541 | 0.061511 | -7.2628e-05 | -0.0048321 | -1.7026e-05 | -0.00054933 | 0.0020188 | 0.012256 | 0.01299 | -0.0068403 | 0.028948 | -0.0069236 | 4.5227 | 121.0007 | -0.10529 | 120.9961 | 0.10071 | -0.050354 | -0.054932 | -0.009155 | -0.09613 | -0.022888 | 0.009155 | 0.068665 | 0.018311 | 0.10529 | 0.054931 | -0.041199 | -0.045776 | 0.26093 | 0.10528 | 0.10986 | 0.050354 | 0.054932 | 0.13733 | -121.138 | -121.0327 | 0.22888 | 0.2655 | 0.17853 | 0.12817 | 0.041199 | 0.20599 | 121.1014 | 0.091553 | 0.032043 | 121.106 | -0.073242 | 121.1609 | 0.064087 | -121.1472 | -121.0648 | 121.1563 | 0.16937 | 4.6829 | 0.15106
2251.1406 | 121.2067 | -0.19684 | 121.0922 | -0.009308 | 6.9821 | 0.062269 | 0.064715 | 0.0039862 | -0.0069683 | -0.0021532 | -0.00054933 | 0.0028732 | 0.013751 | 0.011068 | -0.0081219 | 0.027453 | -0.0013694 | 4.4403 | 121.0648 | -0.13733 | 120.8633 | -0.10529 | -0.18768 | -0.1831 | -0.16937 | -0.073242 | -0.068665 | -0.091553 | -0.059509 | -0.11902 | 0.018311 | 0.059509 | -0.027466 | -0.22888 | 0.091552 | 0.013733 | 0.009155 | -0.045776 | -0.050354 | 0.12817 | -121.1655 | -121.1838 | 0.13733 | 0.21515 | 0.077819 | 0.086976 | -0.050354 | 0.032043 | 121.0007 | 0.009156 | -0.022888 | 121.2021 | -0.004577 | 121.2616 | 0.1236 | -121.2296 | -121.1609 | 121.0602 | 0.10529 | 4.6371 | 0.027465
2252.8281 | 121.2982 | -0.16479 | 121.0876 | 0.005951 | 6.9759 | 0.061842 | 0.06087 | -0.00092703 | -0.0099591 | -0.002367 | -0.00054933 | 0.0015914 | 0.014178 | 0.011495 | -0.0098309 | 0.025957 | -0.0011558 | 4.4952 | 120.9961 | -0.091553 | 121.0007 | 0.11444 | -0.013733 | -0.041199 | -0.004578 | -0.1236 | -0.036621 | -0.027466 | 0.086975 | 0.027466 | 0.082397 | 0.073242 | -0.091552 | -0.086975 | 0.27924 | 0.1236 | 0.15106 | 0.050354 | 0.07782 | 0.12817 | -121.2112 | -121.1151 | 0.25177 | 0.24719 | 0.19226 | 0.11902 | 0.064087 | 0.20599 | 121.0922 | 0.1236 | 0.009155 | 121.0876 | -0.086975 | 121.1609 | 0.041199 | -121.1792 | -121.1243 | 121.1655 | 0.13733 | 4.66 | 0.16022
2254.5781 | 121.2433 | -0.19226 | 121.1105 | -0.0016785 | 6.9801 | 0.065687 | 0.062792 | -7.2628e-05 | -0.0067547 | -0.0027942 | -0.00054933 | 0.0039414 | 0.015674 | 0.012777 | -0.0094037 | 0.023821 | -0.0013694 | 4.5136 | 121.0373 | -0.12817 | 120.9549 | 0.032043 | -0.10529 | -0.11444 | -0.082397 | -0.086975 | -0.064087 | -0.068665 | 0.004578 | -0.064087 | 0.041199 | 0.064087 | -0.073243 | -0.15564 | 0.2243 | 0.07782 | 0.086975 | 0.013733 | 0.022888 | 0.12817 | -121.1975 | -121.1792 | 0.19684 | 0.23346 | 0.12817 | 0.10529 | 0 | 0.16022 | 121.0831 | 0.068665 | -0.004578 | 121.1655 | -0.022888 | 121.2296 | 0.10529 | -121.2387 | -121.1746 | 121.1472 | 0.1236 | 4.7058 | 0.10986
2256.3125 | 121.2799 | -0.18768 | 121.1014 | -0.0016785 | 6.9784 | 0.063978 | 0.062579 | -0.001568 | -0.0086773 | -0.0030078 | 0.0055543 | 0.0039414 | 0.014819 | 0.008077 | -0.011113 | 0.026385 | -8.7586e-05 | 4.4495 | 121.0419 | -0.14191 | 120.9091 | -0.041199 | -0.13275 | -0.15564 | -0.16479 | -0.07782 | -0.082397 | -0.09613 | -0.022888 | -0.082397 | 0.022888 | 0.045776 | -0.059509 | -0.19226 | 0.14648 | 0.032043 | 0.054932 | -0.013733 | 0.009156 | 0.10529 | -121.1792 | -121.1975 | 0.16479 | 0.21057 | 0.10529 | 0.10528 | 0 | 0.10071 | 121.051 | 0.059509 | -0.013733 | 121.1838 | 0.004577 | 121.2296 | 0.10986 | -121.2433 | -121.1838 | 121.0968 | 0.091553 | 4.6371 | 0.022888
2258 | 121.2296 | -0.21057 | 121.1197 | -0.009308 | 6.9771 | 0.06291 | 0.061297 | 0.00185 | -0.0086773 | -0.0027942 | -0.0036011 | 0.002446 | 0.016101 | 0.010427 | -0.010899 | 0.024889 | -0.002651 | 4.4449 | 121.051 | -0.14191 | 120.8908 | -0.036621 | -0.14648 | -0.16479 | -0.17853 | -0.068665 | -0.09613 | -0.1236 | -0.036621 | -0.09613 | -0.004578 | 0.068664 | -0.068665 | -0.22888 | 0.17395 | 0.045776 | 0.064087 | -0.022888 | -0.004577 | 0.11444 | -121.1884 | -121.2433 | 0.17395 | 0.20599 | 0.11444 | 0.091552 | 0 | 0.10529 | 121.0327 | 0.059509 | -0.027466 | 121.1929 | 0.027465 | 121.2616 | 0.14191 | -121.2616 | -121.2158 | 121.1014 | 0.086975 | 4.6555 | 0.032043
2259.75 | 121.3806 | -0.14191 | 121.0831 | 0.005951 | 6.9782 | 0.065473 | 0.060442 | 0.0071906 | -0.0076093 | -0.002367 | 0.0025025 | 0.0033004 | 0.0099057 | 0.010427 | -0.0044903 | 0.025744 | -0.0069236 | 4.4998 | 121.0007 | -0.10071 | 121.0373 | 0.10986 | -0.050354 | -0.050354 | 0.018311 | -0.10986 | -0.032043 | 0.022888 | 0.073242 | 0.022888 | 0.10529 | 0.041199 | -0.082398 | -0.045777 | 0.25177 | 0.091553 | 0.091553 | 0.050354 | 0.050354 | 0.10986 | -121.1929 | -121.0602 | 0.21515 | 0.24719 | 0.16479 | 0.13733 | 0.054931 | 0.21057 | 121.138 | 0.10529 | 0.054931 | 121.1014 | -0.07782 | 121.1426 | 0.032044 | -121.1838 | -121.1151 | 121.1792 | 0.16479 | 4.6417 | 0.16022
2261.5 | 121.3715 | -0.15564 | 121.1014 | 0.005951 | 6.9795 | 0.065046 | 0.061083 | 0.0044134 | -0.0078229 | 0.00019657 | 0.0025025 | 0.0013778 | 0.011828 | 0.013845 | -0.0044903 | 0.028094 | -0.0052146 | 4.4724 | 121.0373 | -0.11902 | 121.051 | 0.10071 | -0.045776 | -0.045776 | 0 | -0.10071 | -0.036621 | 0.027466 | 0.073242 | 0.022888 | 0.10071 | 0.036621 | -0.064087 | -0.050354 | 0.25635 | 0.10986 | 0.10986 | 0.073243 | 0.073243 | 0.11902 | -121.2021 | -121.0739 | 0.22888 | 0.25635 | 0.17853 | 0.13733 | 0.059509 | 0.21973 | 121.17 | 0.10986 | 0.064087 | 121.1563 | -0.064087 | 121.1929 | 0.054932 | -121.2204 | -121.138 | 121.2067 | 0.18311 | 4.628 | 0.15564
2263.25 | 121.2616 | -0.21515 | 121.1609 | -0.009308 | 6.9789 | 0.063123 | 0.06322 | 0.0020636 | -0.0056867 | -0.0036486 | -0.00054933 | 0.0037278 | 0.018023 | 0.0074362 | -0.012608 | 0.026171 | -0.0011558 | 4.454 | 121.0876 | -0.14648 | 120.9274 | -0.041199 | -0.15106 | -0.15106 | -0.15106 | -0.059509 | -0.059509 | -0.13275 | -0.059509 | -0.091553 | -0.004578 | 0.068665 | -0.073243 | -0.23346 | 0.17395 | 0.064087 | 0.064087 | -0.004578 | -0.004578 | 0.15564 | -121.2204 | -121.2936 | 0.15564 | 0.21057 | 0.1236 | 0.054931 | -0.032044 | 0.10529 | 121.0739 | 0 | -0.073242 | 121.2341 | 0 | 121.3028 | 0.15564 | -121.3074 | -121.2204 | 121.1426 | 0.082398 | 4.6692 | 0.064087
2264.9219 | 121.3852 | -0.15564 | 121.1334 | -0.009308 | 6.9771 | 0.066328 | 0.062365 | 0.0014228 | -0.0071821 | -0.002367 | -0.00054933 | 0.0009506 | 0.014392 | 0.0057272 | -0.0076947 | 0.027025 | -0.002651 | 4.3671 | 121.0785 | -0.1236 | 120.9778 | 0.009155 | -0.13733 | -0.12817 | -0.068665 | -0.082397 | -0.054932 | -0.004578 | 0.050354 | -0.022888 | 0.10986 | 0.032044 | -0.054932 | -0.15564 | 0.16479 | 0.027466 | 0.018311 | -0.004578 | -0.013733 | 0.10071 | -121.2158 | -121.138 | 0.20599 | 0.2655 | 0.13275 | 0.16479 | 0.032044 | 0.13275 | 121.1014 | 0.10529 | 0.050354 | 121.2021 | -0.027465 | 121.2341 | 0.073243 | -121.257 | -121.1884 | 121.1334 | 0.15106 | 4.5227 | 0.086975
2266.6562 | 121.3806 | -0.16022 | 121.0968 | -0.016937 | 6.9782 | 0.062696 | 0.062365 | -0.001568 | -0.0063275 | -0.0032214 | -0.0066527 | 0.0013778 | 0.015674 | 0.01299 | -0.0055585 | 0.027453 | -0.002651 | 4.3808 | 121.0602 | -0.10986 | 121.0373 | 0.07782 | -0.07782 | -0.07782 | -0.027466 | -0.10529 | -0.027466 | 0.027466 | 0.064087 | 0.018311 | 0.10986 | 0.050354 | -0.036621 | -0.05951 | 0.23804 | 0.082397 | 0.082397 | 0.032043 | 0.032043 | 0.13275 | -121.2021 | -121.0693 | 0.2243 | 0.27008 | 0.17853 | 0.13733 | 0.045777 | 0.18768 | 121.1472 | 0.091553 | 0.054932 | 121.17 | -0.07782 | 121.2204 | 0.054931 | -121.2067 | -121.1243 | 121.1975 | 0.18768 | 4.541 | 0.13275
2268.3438 | 121.3074 | -0.19684 | 121.1517 | -0.009308 | 6.9793 | 0.062269 | 0.061511 | -0.00092703 | -0.0093183 | -0.0021532 | -0.0066527 | 0.0015914 | 0.014178 | 0.014913 | -0.011754 | 0.025744 | -0.0041464 | 4.4312 | 121.0693 | -0.11902 | 121.0052 | 0.050354 | -0.073242 | -0.09613 | -0.086975 | -0.10071 | -0.073242 | -0.09613 | -0.009155 | -0.07782 | 0.027466 | 0.077819 | -0.082397 | -0.14648 | 0.24719 | 0.10071 | 0.1236 | 0.022889 | 0.045777 | 0.1236 | -121.2524 | -121.2479 | 0.18768 | 0.2243 | 0.11902 | 0.10071 | -0.004578 | 0.16937 | 121.1243 | 0.064087 | -0.022888 | 121.1884 | -0.027466 | 121.2662 | 0.09613 | -121.2708 | -121.225 | 121.2021 | 0.10071 | 4.628 | 0.10986
2270.0781 | 121.3531 | -0.16937 | 121.1563 | -0.0016785 | 6.9784 | 0.06291 | 0.062365 | 0.0033454 | -0.0065411 | -0.0012988 | -0.0036011 | 0.0003098 | 0.015887 | 0.009786 | -0.0087629 | 0.027025 | -0.0022238 | 4.3671 | 121.0831 | -0.09613 | 121.019 | 0.064087 | -0.09613 | -0.082397 | -0.050354 | -0.086975 | -0.041199 | -0.036621 | 0.022888 | -0.009155 | 0.068665 | 0.073243 | -0.073242 | -0.13733 | 0.23346 | 0.086976 | 0.073243 | 0.013733 | 0 | 0.12817 | -121.2433 | -121.1929 | 0.19226 | 0.23804 | 0.16022 | 0.10986 | 0.032044 | 0.16022 | 121.1151 | 0.064087 | 0.004578 | 121.1792 | -0.045776 | 121.2524 | 0.082398 | -121.2524 | -121.1975 | 121.1884 | 0.13275 | 4.5364 | 0.11902
2271.8281 | 121.4172 | -0.17395 | 121.1472 | -0.0016785 | 6.9767 | 0.061842 | 0.061297 | 0.0014228 | -0.0091047 | -0.0021532 | -0.0036011 | 0.0020188 | 0.015033 | 0.013631 | -0.0074811 | 0.027453 | -0.003292 | 4.3533 | 121.0419 | -0.10529 | 121.0327 | 0.064087 | -0.036621 | -0.050354 | -0.036621 | -0.091553 | -0.041199 | -0.004578 | 0.082397 | 0.041199 | 0.10529 | 0.068664 | -0.10529 | -0.11444 | 0.23804 | 0.1236 | 0.13733 | 0.054932 | 0.068665 | 0.13275 | -121.2387 | -121.1517 | 0.25635 | 0.27924 | 0.21515 | 0.14649 | 0.082398 | 0.16937 | 121.138 | 0.1236 | 0.036621 | 121.1472 | -0.050354 | 121.2158 | 0.082397 | -121.2524 | -121.1884 | 121.2067 | 0.16937 | 4.5273 | 0.13733
2273.5156 | 121.3028 | -0.20142 | 121.1929 | -0.009308 | 6.9791 | 0.063764 | 0.063647 | -0.00028623 | -0.0050457 | -0.0038622 | 0.0055543 | 0.002446 | 0.014178 | 0.0099996 | -0.0061993 | 0.026598 | -0.0039328 | 4.2892 | 121.1517 | -0.10986 | 120.9366 | -0.054932 | -0.20142 | -0.17853 | -0.18768 | -0.064087 | -0.091553 | -0.10529 | -0.073242 | -0.13275 | -0.009155 | 0.091553 | -0.041199 | -0.25635 | 0.14648 | 0.022888 | 0 | -0.068665 | -0.091553 | 0.10986 | -121.257 | -121.2982 | 0.12817 | 0.19226 | 0.068665 | 0.082398 | -0.041198 | 0.054931 | 121.0464 | 0.018311 | -0.013733 | 121.2616 | 0.027466 | 121.3531 | 0.13733 | -121.3028 | -121.2845 | 121.138 | 0.09613 | 4.4907 | 0.013733
2275.2656 | 121.2799 | -0.21057 | 121.1929 | -0.0016785 | 6.9784 | 0.063337 | 0.064288 | 0.0041998 | -0.0076093 | -0.0036486 | -0.00054933 | 0.0015914 | 0.018023 | 0.011922 | -0.0094037 | 0.027025 | 0.00098061 | 4.3259 | 121.1151 | -0.11902 | 120.9549 | -0.064087 | -0.19226 | -0.1831 | -0.17395 | -0.082397 | -0.073242 | -0.11444 | -0.086975 | -0.14648 | 0.004578 | 0.091552 | -0.07782 | -0.23804 | 0.14648 | 0.027466 | 0.01831 | -0.064086 | -0.073242 | 0.13733 | -121.2753 | -121.3074 | 0.1236 | 0.21515 | 0.064087 | 0.07782 | -0.073242 | 0.054932 | 121.0739 | -0.013733 | -0.041199 | 121.2341 | -0.009155 | 121.3257 | 0.12817 | -121.312 | -121.2662 | 121.1655 | 0.09613 | 4.5364 | 0.036621
2276.9531 | 121.3303 | -0.19684 | 121.1838 | -0.016937 | 6.9776 | 0.066114 | 0.059161 | -0.00092703 | -0.0069683 | -0.0021532 | -0.00054933 | 0.0047958 | 0.014605 | 0.012136 | -0.0098309 | 0.028307 | -0.00436 | 4.3533 | 121.0831 | -0.10529 | 121.051 | 0.07782 | -0.064087 | -0.073242 | -0.064087 | -0.09613 | -0.059509 | -0.073242 | 0.018311 | -0.041199 | 0.032043 | 0.091552 | -0.10071 | -0.13275 | 0.27466 | 0.1236 | 0.13275 | 0.032044 | 0.041199 | 0.13733 | -121.2799 | -121.257 | 0.21515 | 0.22888 | 0.15564 | 0.091552 | 0.01831 | 0.18311 | 121.1563 | 0.07782 | -0.013733 | 121.1884 | -0.036621 | 121.2799 | 0.10071 | -121.2891 | -121.2433 | 121.2479 | 0.1236 | 4.5502 | 0.13275
2278.6875 | 121.3577 | -0.17395 | 121.2021 | -0.016937 | 6.9782 | 0.062055 | 0.059374 | -0.00028623 | -0.0088911 | -0.0010852 | 0.0025025 | -0.0003312 | 0.012469 | 0.016408 | -0.012181 | 0.024676 | -0.0056418 | 4.3854 | 121.0968 | -0.091553 | 121.0602 | 0.073242 | -0.068665 | -0.07782 | -0.086975 | -0.09613 | -0.054932 | -0.082397 | 0.009155 | -0.054932 | 0.018311 | 0.082397 | -0.10529 | -0.14191 | 0.24719 | 0.09613 | 0.10528 | 0.013733 | 0.022888 | 0.11902 | -121.2982 | -121.2845 | 0.1831 | 0.19226 | 0.11902 | 0.073243 | 0 | 0.16479 | 121.1517 | 0.064087 | -0.027465 | 121.1884 | -0.041198 | 121.2708 | 0.07782 | -121.2936 | -121.257 | 121.2341 | 0.091553 | 4.5593 | 0.086975
2280.4219 | 121.3394 | -0.2243 | 121.2204 | 0.005951 | 6.9791 | 0.062483 | 0.062151 | -0.0017816 | -0.0097455 | -0.002367 | -0.00054933 | 0.0039414 | 0.014819 | 0.0091452 | -0.010472 | 0.025103 | -0.0030784 | 4.2847 | 121.138 | -0.15106 | 120.9732 | -0.036621 | -0.13733 | -0.15564 | -0.16479 | -0.059509 | -0.091553 | -0.11902 | -0.022888 | -0.07782 | 0.009155 | 0.073242 | -0.082398 | -0.24719 | 0.18768 | 0.068664 | 0.086975 | -0.004578 | 0.013733 | 0.13275 | -121.2799 | -121.3394 | 0.20142 | 0.23346 | 0.14648 | 0.10071 | 0.013733 | 0.11444 | 121.1243 | 0.068665 | -0.027466 | 121.2891 | 0.032044 | 121.3623 | 0.16479 | -121.3715 | -121.312 | 121.1975 | 0.10529 | 4.509 | 0.059509
2282.1094 | 121.4722 | -0.15106 | 121.1792 | -0.0016785 | 6.9791 | 0.066969 | 0.06087 | -0.00071343 | -0.0071821 | -0.0015124 | 0.0025025 | 9.6204e-05 | 0.013324 | 0.009786 | -0.0051313 | 0.026812 | -0.0041464 | 4.2984 | 121.1151 | -0.09613 | 121.0739 | 0.064087 | -0.050354 | -0.086975 | -0.013733 | -0.10986 | -0.036621 | 0.041199 | 0.064087 | 0.018311 | 0.11902 | 0.054932 | -0.064087 | -0.10528 | 0.21515 | 0.064087 | 0.10071 | 0.009155 | 0.045776 | 0.11444 | -121.2891 | -121.138 | 0.21515 | 0.27008 | 0.16937 | 0.15564 | 0.054932 | 0.16022 | 121.17 | 0.10071 | 0.07782 | 121.2112 | -0.073242 | 121.2662 | 0.041199 | -121.2753 | -121.2158 | 121.225 | 0.19226 | 4.4495 | 0.13733
2283.8594 | 121.3577 | -0.19226 | 121.1929 | -0.009308 | 6.9774 | 0.06291 | 0.063433 | -0.0011408 | -0.0076093 | -0.0036486 | -0.00054933 | 0.004155 | 0.012256 | 0.014272 | -0.0057721 | 0.027453 | -0.0030784 | 4.2847 | 121.1792 | -0.13733 | 120.9869 | -0.045776 | -0.19684 | -0.17853 | -0.14648 | -0.07782 | -0.050354 | -0.07782 | -0.036621 | -0.10986 | 0.013733 | 0.054932 | -0.013733 | -0.20599 | 0.14648 | 0.013733 | -0.004577 | -0.041199 | -0.059509 | 0.14191 | -121.2708 | -121.2708 | 0.15564 | 0.20599 | 0.082398 | 0.064087 | -0.059509 | 0.091553 | 121.1243 | 0.013733 | -0.027466 | 121.3165 | -0.027466 | 121.3715 | 0.11444 | -121.3303 | -121.2433 | 121.1792 | 0.11444 | 4.4769 | 0.045777
2285.5938 | 121.3211 | -0.20599 | 121.2341 | -0.009308 | 6.9795 | 0.06291 | 0.063006 | 0.0014228 | -0.0080365 | -0.0012988 | -0.00054933 | 0.0026596 | 0.013965 | 0.010854 | -0.0089765 | 0.028094 | -0.0035056 | 4.2938 | 121.1472 | -0.1236 | 120.9961 | -0.032043 | -0.17395 | -0.16937 | -0.15106 | -0.064087 | -0.073242 | -0.10529 | -0.064087 | -0.12817 | 0 | 0.082398 | -0.086975 | -0.23804 | 0.17395 | 0.036621 | 0.032044 | -0.045777 | -0.050354 | 0.13275 | -121.2982 | -121.3394 | 0.14191 | 0.20599 | 0.07782 | 0.073242 | -0.054932 | 0.091553 | 121.1197 | 0.009155 | -0.032044 | 121.2708 | 0.009155 | 121.3531 | 0.14191 | -121.3577 | -121.3074 | 121.2021 | 0.10071 | 4.4998 | 0.054932
2287.2656 | 121.4676 | -0.15564 | 121.1655 | -0.0016785 | 6.9786 | 0.066328 | 0.062365 | 0.00185 | -0.0063275 | -0.0038622 | -0.0066527 | 0.0015914 | 0.013537 | 0.023031 | -0.0053449 | 0.028307 | -0.00030119 | 4.3076 | 121.138 | -0.091553 | 121.106 | 0.09613 | -0.064087 | -0.073242 | 0.004578 | -0.13733 | -0.041199 | 0.045776 | 0.07782 | 0.018311 | 0.1236 | 0.064087 | -0.027466 | -0.059509 | 0.25177 | 0.082398 | 0.091553 | 0.018311 | 0.027466 | 0.11444 | -121.3028 | -121.1197 | 0.23346 | 0.27924 | 0.17395 | 0.16479 | 0.05951 | 0.18768 | 121.1975 | 0.11902 | 0.086975 | 121.2296 | -0.09613 | 121.2936 | 0.018311 | -121.257 | -121.2067 | 121.2616 | 0.20142 | 4.4632 | 0.16022
2289.0156 | 121.4767 | -0.16479 | 121.2067 | -0.0016785 | 6.9784 | 0.061628 | 0.061297 | 0.00078177 | -0.0095319 | -0.0036486 | -0.0097045 | 0.0011642 | 0.016314 | 0.0050864 | -0.0072675 | 0.026812 | -0.0028646 | 4.216 | 121.1426 | -0.09613 | 121.0922 | 0.091553 | -0.032043 | -0.054932 | -0.032043 | -0.10529 | -0.036621 | 0.004578 | 0.082397 | 0.045776 | 0.10071 | 0.068665 | -0.064087 | -0.11444 | 0.25635 | 0.10986 | 0.13275 | 0.041198 | 0.064087 | 0.12817 | -121.312 | -121.2021 | 0.24719 | 0.2655 | 0.21057 | 0.13733 | 0.082397 | 0.18768 | 121.1884 | 0.11902 | 0.041199 | 121.2387 | -0.068665 | 121.3074 | 0.059509 | -121.3028 | -121.2433 | 121.257 | 0.16937 | 4.3808 | 0.13275
2290.7656 | 121.3486 | -0.19684 | 121.2204 | -0.009308 | 6.9774 | 0.061842 | 0.061083 | 0.00078177 | -0.0076093 | -0.0027942 | 0.0025025 | 0.004155 | 0.012042 | 0.019185 | -0.010258 | 0.024889 | -0.0030784 | 4.248 | 121.1838 | -0.13733 | 121.0007 | -0.036621 | -0.14648 | -0.14648 | -0.15106 | -0.068665 | -0.068665 | -0.11902 | -0.059509 | -0.10986 | -0.004578 | 0.059509 | -0.036621 | -0.21973 | 0.16022 | 0.050354 | 0.050354 | -0.009155 | -0.009155 | 0.12817 | -121.2891 | -121.3394 | 0.13733 | 0.19226 | 0.086975 | 0.064087 | -0.041198 | 0.10071 | 121.138 | 0.009156 | -0.050354 | 121.3211 | 0 | 121.3806 | 0.12817 | -121.3577 | -121.2891 | 121.1975 | 0.077819 | 4.4449 | 0.045776
2292.5156 | 121.3531 | -0.2243 | 121.2341 | -0.016937 | 6.9791 | 0.061201 | 0.064715 | -0.0024224 | -0.0080365 | -0.001726 | 0.0025025 | 0.0022324 | 0.016955 | 0.014486 | -0.011326 | 0.026171 | -8.7586e-05 | 4.2068 | 121.1609 | -0.13275 | 121.0098 | -0.022888 | -0.13275 | -0.14191 | -0.15564 | -0.059509 | -0.068665 | -0.12817 | -0.027466 | -0.082397 | -0.009155 | 0.091553 | -0.073242 | -0.2243 | 0.20142 | 0.082397 | 0.091553 | -0.009156 | 0 | 0.15564 | -121.2936 | -121.3623 | 0.19684 | 0.21515 | 0.14191 | 0.05951 | -0.013732 | 0.10986 | 121.1426 | 0.041199 | -0.059509 | 121.2936 | 0.009156 | 121.3852 | 0.16479 | -121.3669 | -121.3028 | 121.2341 | 0.09613 | 4.4312 | 0.068664
2294.2656 | 121.3989 | -0.18768 | 121.2296 | -0.009308 | 6.9795 | 0.063337 | 0.061938 | 0.0012092 | -0.0061139 | -0.0015124 | 0.0025025 | 0.0030868 | 0.016101 | 0.007009 | -0.0049175 | 0.02788 | -0.0071372 | 4.1519 | 121.1929 | -0.12817 | 121.0052 | -0.036621 | -0.18768 | -0.16937 | -0.13733 | -0.07782 | -0.050354 | -0.086975 | -0.036621 | -0.10071 | 0.027466 | 0.059509 | -0.036621 | -0.2243 | 0.15106 | 0.01831 | 0 | -0.041199 | -0.059509 | 0.13733 | -121.3074 | -121.3165 | 0.15106 | 0.21515 | 0.086975 | 0.07782 | -0.050354 | 0.091553 | 121.1334 | 0.013733 | -0.036621 | 121.3211 | -0.027466 | 121.3806 | 0.10986 | -121.3577 | -121.2799 | 121.1929 | 0.10071 | 4.3396 | 0.050354
2295.9375 | 121.4447 | -0.18768 | 121.225 | -0.0016785 | 6.9793 | 0.065046 | 0.062151 | 0.00056817 | -0.0054731 | -0.001726 | -0.00054933 | 0.002446 | 0.01311 | 0.006368 | -0.0072675 | 0.028307 | -0.006069 | 4.184 | 121.1655 | -0.091553 | 121.0968 | 0.068665 | -0.09613 | -0.10071 | -0.050354 | -0.09613 | -0.050354 | -0.027466 | 0.018311 | -0.009155 | 0.082397 | 0.09613 | -0.05951 | -0.12817 | 0.25635 | 0.086975 | 0.091553 | -0.009155 | -0.004577 | 0.13733 | -121.3211 | -121.2524 | 0.20599 | 0.27008 | 0.17853 | 0.13275 | 0.041199 | 0.16022 | 121.1884 | 0.068665 | 0.022888 | 121.257 | -0.045776 | 121.3531 | 0.091553 | -121.3165 | -121.2753 | 121.2845 | 0.16022 | 4.3716 | 0.13733
2297.6719 | 121.4859 | -0.15564 | 121.225 | -0.009308 | 6.9776 | 0.062696 | 0.060442 | 0.00078177 | -0.0082501 | -0.0038622 | -0.00054933 | 0.0011642 | 0.013537 | 0.0072226 | -0.010472 | 0.027453 | -0.00072839 | 4.248 | 121.1151 | -0.086975 | 121.1517 | 0.11444 | -0.009155 | -0.032043 | 0.018311 | -0.10986 | -0.022888 | 0 | 0.10529 | 0.059509 | 0.10529 | 0.068665 | -0.10986 | -0.073243 | 0.27008 | 0.1236 | 0.14649 | 0.054932 | 0.07782 | 0.13275 | -121.3348 | -121.225 | 0.26093 | 0.26093 | 0.21515 | 0.12817 | 0.082397 | 0.20142 | 121.2387 | 0.12817 | 0.022888 | 121.2021 | -0.086975 | 121.2708 | 0.045777 | -121.312 | -121.2479 | 121.3074 | 0.15564 | 4.4037 | 0.17395
2299.4219 | 121.5134 | -0.14191 | 121.2433 | -0.0016785 | 6.9767 | 0.062269 | 0.05852 | 0.00099557 | -0.0076093 | -0.0025806 | -0.0036011 | 0.0011642 | 0.012469 | 0.014272 | -0.0087629 | 0.02553 | -0.0028646 | 4.2343 | 121.1288 | -0.091553 | 121.1609 | 0.14191 | -0.009155 | -0.018311 | 0.036621 | -0.11902 | -0.027466 | 0.009155 | 0.10071 | 0.059509 | 0.11444 | 0.050354 | -0.11444 | -0.082397 | 0.28381 | 0.1236 | 0.13275 | 0.073242 | 0.082398 | 0.11444 | -121.3623 | -121.2341 | 0.24262 | 0.25635 | 0.20142 | 0.14191 | 0.086975 | 0.23346 | 121.2524 | 0.12817 | 0.036621 | 121.2204 | -0.091553 | 121.2708 | 0.022888 | -121.3348 | -121.2708 | 121.3028 | 0.15106 | 4.3762 | 0.17853
2301.0938 | 121.4172 | -0.21057 | 121.257 | -0.0016785 | 6.9786 | 0.062696 | 0.061297 | -0.0017816 | -0.0091047 | -0.002367 | -0.00054933 | 0.0028732 | 0.014392 | 0.01299 | -0.010472 | 0.027025 | -0.0022238 | 4.1794 | 121.2021 | -0.12817 | 121.0464 | -0.045776 | -0.13733 | -0.14648 | -0.14648 | -0.073242 | -0.073242 | -0.091553 | -0.018311 | -0.064087 | 0.036621 | 0.082397 | -0.054932 | -0.21057 | 0.1648 | 0.064087 | 0.073242 | -0.01831 | -0.009155 | 0.13733 | -121.3303 | -121.3486 | 0.19226 | 0.24719 | 0.14648 | 0.10986 | 0.009155 | 0.082398 | 121.1746 | 0.054931 | -0.018311 | 121.3303 | 0 | 121.4127 | 0.13733 | -121.3852 | -121.3303 | 121.257 | 0.11902 | 4.39 | 0.064087
2302.7812 | 121.5042 | -0.15106 | 121.225 | -0.0016785 | 6.978 | 0.065046 | 0.063647 | 0.0016364 | -0.0067547 | -0.00065803 | -0.00054933 | 0.0009506 | 0.013537 | 0.012777 | -0.0027813 | 0.029375 | -0.005001 | 4.1977 | 121.1929 | -0.09613 | 121.1472 | 0.091553 | -0.068665 | -0.082397 | -0.004578 | -0.10529 | -0.036621 | 0.027466 | 0.07782 | 0.027466 | 0.13275 | 0.054932 | -0.032044 | -0.07782 | 0.24261 | 0.068665 | 0.082397 | 0.013733 | 0.027465 | 0.11444 | -121.3303 | -121.1975 | 0.22888 | 0.28381 | 0.17853 | 0.16937 | 0.064087 | 0.18768 | 121.2433 | 0.11444 | 0.064087 | 121.2891 | -0.068665 | 121.344 | 0.045776 | -121.3211 | -121.2616 | 121.2982 | 0.17853 | 4.3488 | 0.14648
2304.5312 | 121.3669 | -0.21973 | 121.2708 | 0.005951 | 6.9816 | 0.066969 | 0.06322 | 0.0046272 | -0.0061139 | -0.001726 | -0.00054933 | 0.002446 | 0.013537 | 0.0044454 | -0.0091901 | 0.027453 | -0.00051479 | 4.1382 | 121.2067 | -0.1236 | 121.0464 | -0.036621 | -0.16937 | -0.17853 | -0.15564 | -0.064087 | -0.050354 | -0.10071 | -0.073242 | -0.13275 | -0.004578 | 0.096131 | -0.064087 | -0.2243 | 0.18311 | 0.041199 | 0.050354 | -0.054932 | -0.045777 | 0.16937 | -121.3348 | -121.3715 | 0.14649 | 0.21515 | 0.086976 | 0.045776 | -0.082397 | 0.086975 | 121.17 | -0.022888 | -0.050354 | 121.3303 | -0.013733 | 121.4264 | 0.15564 | -121.3943 | -121.3211 | 121.2662 | 0.11902 | 4.3579 | 0.064087
2306.2031 | 117.8558 | -25.1404 | 92.4408 | 0.005951 | 6.9761 | 0.06526 | 0.059802 | 0.005268 | -0.0093183 | -0.0047168 | -0.00054933 | 0.000737 | 0.014605 | 0.014913 | -0.0076947 | 0.029162 | -0.0030784 | -5.3238 | 93.8324 | -23.8174 | 90.1154 | -26.7105 | -26.4725 | -26.8341 | -0.013733 | -0.082397 | -0.018311 | -0.013733 | 0.050354 | 0.009155 | 0.091553 | 1.3229 | 1.3916 | -2.3254 | -1.5701 | -1.6937 | -1.3321 | -3.0167 | -2.655 | 25.1221 | -92.5232 | -92.4545 | 25.1907 | 25.2319 | 25.1495 | 0.10986 | 0.027466 | -2.8931 | 113.9328 | 0.068665 | 0.004578 | 117.6498 | -0.064086 | 118.9728 | 25.058 | -116.2582 | -92.4591 | 115.2557 | 25.1266 | 19.8166 | 25.1266
2307.9375 | 115.3336 | -37.6053 | 77.1286 | -0.0016785 | 6.9763 | 0.059919 | 0.060656 | 0.00078177 | -0.0067547 | -0.0019396 | -0.0066527 | 0.0030868 | 0.013537 | 0.0074362 | -0.0072675 | 0.026812 | -0.0028646 | -12.5198 | 77.9572 | -37.5458 | 77.2751 | -38.1821 | -38.0676 | -38.1638 | -0.09613 | -0.050354 | -0.045776 | -0.009155 | 0.022888 | -0.022888 | 0.10071 | 0.05951 | 0.82855 | 0.14648 | -0.57678 | -0.55847 | -0.46234 | -0.61798 | -0.52185 | 37.5595 | -77.179 | -77.1378 | 37.6282 | 37.706 | 37.5824 | 0.14648 | 0.022888 | -0.63629 | 114.8209 | 0.068664 | 0.036621 | 115.5029 | -0.004578 | 115.5624 | 37.5549 | -114.6744 | -77.1744 | 114.8804 | 37.5961 | 25.0855 | 37.5092
2309.6875 | 120.1538 | -0.3479 | 119.902 | -0.0016785 | 6.9806 | 0.065473 | 0.062151 | 0.0067634 | -0.0063275 | -0.001726 | -0.0036011 | 0.0030868 | 0.015674 | 0.010854 | -0.0066265 | 0.027453 | -0.001583 | 3.9139 | 119.8242 | -0.27466 | 119.6503 | -0.19226 | -0.33417 | -0.32501 | -0.15564 | -0.082397 | -0.073242 | -0.10071 | -0.050354 | -0.11444 | 0.009155 | 0.073242 | -0.07782 | -0.25177 | 0.15564 | 0.022888 | 0.013733 | -0.050354 | -0.059509 | 0.27466 | -119.9844 | -120.0027 | 0.29755 | 0.35706 | 0.23346 | 0.082397 | -0.041199 | 0.082397 | 119.9249 | 0.022888 | -0.027466 | 120.0989 | -0.009155 | 120.1721 | 0.2655 | -120.1767 | -119.9753 | 119.9982 | 0.24719 | 4.2618 | 0.19226
2311.375 | 120.3186 | -0.21057 | 120.2362 | -0.009308 | 6.9789 | 0.064619 | 0.061083 | 0.00014097 | -0.010814 | -0.00065803 | -0.0036011 | 0.004155 | 0.015033 | 0.015767 | -0.0091901 | 0.02788 | -0.0020102 | 4.0421 | 120.1447 | -0.12817 | 120.0165 | 0.009155 | -0.15564 | -0.16479 | -0.11444 | -0.07782 | -0.059509 | -0.082397 | -0.036621 | -0.11444 | 0.009155 | 0.082397 | -0.091553 | -0.21973 | 0.21973 | 0.045776 | 0.054931 | -0.036621 | -0.027466 | 0.15106 | -120.314 | -120.3186 | 0.17395 | 0.21973 | 0.09613 | 0.068664 | -0.054932 | 0.13733 | 120.1447 | 0.022888 | -0.022888 | 120.2728 | -0.018311 | 120.3552 | 0.13275 | -120.3644 | -120.2957 | 120.2271 | 0.12817 | 4.2526 | 0.09613
2313.125 | 120.4147 | -0.20142 | 120.3186 | -0.0016785 | 6.9789 | 0.064192 | 0.061724 | 0.0012092 | -0.0093183 | -0.0038622 | -0.00054933 | 0.000737 | 0.014605 | 0.014486 | -0.014958 | 0.025316 | -8.7586e-05 | 4.0558 | 120.195 | -0.10529 | 120.108 | 0.041199 | -0.10071 | -0.10986 | -0.1236 | -0.07782 | -0.068665 | -0.10071 | -0.022888 | -0.073242 | 0.013733 | 0.09613 | -0.1236 | -0.21057 | 0.24262 | 0.091553 | 0.10071 | -0.004577 | 0.004578 | 0.13275 | -120.3964 | -120.4193 | 0.17853 | 0.21515 | 0.12817 | 0.082398 | -0.004577 | 0.14649 | 120.2133 | 0.045777 | -0.032043 | 120.3003 | -0.009155 | 120.3964 | 0.1236 | -120.4239 | -120.3873 | 120.3094 | 0.10071 | 4.2572 | 0.07782
2314.875 | 120.5795 | -0.16479 | 120.3049 | -0.009308 | 6.9803 | 0.06291 | 0.058947 | 0.0031318 | -0.0080365 | -0.0025806 | 0.0055543 | 0.0028732 | 0.01311 | 0.006368 | -0.0076947 | 0.029803 | -0.003292 | 4.0009 | 120.2637 | -0.091553 | 120.2408 | 0.10071 | -0.068665 | -0.064087 | 0.009155 | -0.10071 | -0.054932 | 0.027466 | 0.086975 | 0.045776 | 0.10529 | 0.073242 | -0.041199 | -0.064087 | 0.2655 | 0.10071 | 0.09613 | 0.027466 | 0.022888 | 0.10986 | -120.4056 | -120.2774 | 0.25177 | 0.27008 | 0.21057 | 0.16022 | 0.10071 | 0.19226 | 120.3323 | 0.14191 | 0.082398 | 120.3552 | -0.045776 | 120.4285 | 0.064087 | -120.3964 | -120.3598 | 120.4056 | 0.19226 | 4.1656 | 0.17395
2316.5469 | 120.6162 | -0.15106 | 120.3827 | -0.016937 | 6.9799 | 0.062269 | 0.05852 | 0.0024908 | -0.010386 | -0.0047168 | -0.0036011 | 0.002446 | 0.012683 | 0.011495 | -0.010686 | 0.026812 | -0.0054282 | 4.0192 | 120.282 | -0.091553 | 120.2911 | 0.13733 | -0.009155 | -0.041199 | 0.022888 | -0.11444 | -0.032043 | 0.009155 | 0.10986 | 0.050354 | 0.10986 | 0.059509 | -0.10071 | -0.091552 | 0.28839 | 0.10986 | 0.14191 | 0.050354 | 0.082398 | 0.11902 | -120.4971 | -120.3735 | 0.26093 | 0.26093 | 0.20142 | 0.14191 | 0.082397 | 0.22888 | 120.3827 | 0.14191 | 0.041198 | 120.3735 | -0.082398 | 120.433 | 0.036621 | -120.4742 | -120.4147 | 120.4422 | 0.16022 | 4.1702 | 0.17395
2318.2812 | 120.6436 | -0.16022 | 120.401 | 0.005951 | 6.9789 | 0.064832 | 0.061938 | 0.0033454 | -0.0095319 | -0.001726 | -0.0036011 | 0.0030868 | 0.012897 | 0.0076498 | -0.0076947 | 0.027239 | -0.0028646 | 3.9093 | 120.3735 | -0.13275 | 120.2499 | 0.009155 | -0.13733 | -0.13275 | -0.064087 | -0.086975 | -0.045776 | -0.022888 | 0.054932 | -0.027466 | 0.10071 | 0.027466 | -0.027466 | -0.15106 | 0.16937 | 0.027466 | 0.022888 | 0 | -0.004578 | 0.11444 | -120.488 | -120.4239 | 0.21515 | 0.26093 | 0.13275 | 0.14648 | 0.01831 | 0.14191 | 120.3827 | 0.10071 | 0.022888 | 120.5063 | -0.041199 | 120.5338 | 0.073242 | -120.5338 | -120.4468 | 120.4102 | 0.13733 | 4.0695 | 0.09613
2319.9844 | 120.607 | -0.19226 | 120.4422 | -0.009308 | 6.9791 | 0.06291 | 0.06386 | -0.00071343 | -0.0093183 | -0.001726 | -0.0036011 | 0.0026596 | 0.016101 | 0.0085044 | -0.0096173 | 0.028521 | -0.00094199 | 3.9001 | 120.4147 | -0.12817 | 120.2408 | -0.054932 | -0.18768 | -0.1831 | -0.14648 | -0.07782 | -0.045776 | -0.082397 | -0.041199 | -0.10529 | 0.022888 | 0.064087 | -0.027466 | -0.20142 | 0.13733 | 0.009156 | 0.004578 | -0.054931 | -0.059509 | 0.14648 | -120.52 | -120.5246 | 0.15106 | 0.21515 | 0.086975 | 0.068664 | -0.05951 | 0.073242 | 120.369 | 0.004577 | -0.036621 | 120.5429 | -0.032044 | 120.607 | 0.11444 | -120.5704 | -120.488 | 120.433 | 0.10986 | 4.0924 | 0.045777
2321.7344 | 120.6848 | -0.1831 | 120.4971 | -0.009308 | 6.9776 | 0.062696 | 0.060015 | 0.0039862 | -0.0091047 | -0.0038622 | -0.00054933 | 0.0018052 | 0.012683 | 0.009786 | -0.010258 | 0.025957 | -0.003292 | 3.9185 | 120.4147 | -0.10529 | 120.3369 | 0.045776 | -0.09613 | -0.086975 | -0.082397 | -0.086975 | -0.045776 | -0.041199 | 0.027466 | -0.032043 | 0.068665 | 0.077819 | -0.082397 | -0.16022 | 0.22888 | 0.09613 | 0.086975 | 0.018311 | 0.009156 | 0.13733 | -120.5841 | -120.5383 | 0.21057 | 0.25177 | 0.15106 | 0.11444 | 0.013733 | 0.15106 | 120.4422 | 0.073242 | 0.004577 | 120.52 | -0.041199 | 120.5978 | 0.09613 | -120.6024 | -120.5429 | 120.52 | 0.14191 | 4.1016 | 0.10071
2323.5 | 116.1255 | -37.0743 | 78.891 | -0.009308 | 6.9771 | 0.064192 | 0.061083 | 0.00185 | -0.0054731 | -0.00044443 | -0.00054933 | 0.0039414 | 0.015033 | 0.010641 | -0.0091901 | 0.025957 | -0.0037192 | -13.0096 | 79.1016 | -36.8774 | 78.9001 | -37.0285 | -37.3261 | -37.3398 | -0.068665 | -0.027466 | -0.027466 | -0.064087 | -0.009155 | -0.064087 | 0.045776 | 0.19684 | 0.21057 | 0.009155 | 0.045777 | -0.2655 | -0.25177 | -0.46234 | -0.44861 | 37.0468 | -78.9185 | -78.9551 | 37.0651 | 37.1201 | 37.0102 | 0.073242 | -0.036621 | -0.15106 | 115.7776 | 0.018311 | -0.036621 | 115.979 | 0 | 116.1758 | 37.0468 | -115.7684 | -78.9185 | 115.9744 | 37.0102 | 24.0646 | 37.0056
2325.25 | 115.4114 | -38.9969 | 76.149 | 0.005951 | 6.9782 | 0.059706 | 0.060229 | 0.0050544 | -0.0080365 | -0.002367 | -0.00054933 | 0.0047958 | 0.014605 | 0.0089316 | -0.0076947 | 0.026598 | -0.0054282 | -14.5111 | 76.2405 | -38.9191 | 76.268 | -38.8229 | -39.1754 | -39.0015 | -0.054932 | -0.050354 | -0.009155 | -0.018311 | 0.041199 | -0.013733 | 0.082397 | 0.07782 | 0.091553 | 0.11902 | 0.17395 | -0.004578 | -0.17853 | -0.082398 | -0.25635 | 38.9877 | -76.1993 | -76.1673 | 39.0381 | 39.0793 | 38.9832 | 0.091552 | -0.004578 | 0.09613 | 115.1871 | 0.050354 | -0.009156 | 115.1596 | -0.041199 | 115.2374 | 38.9465 | -115.0681 | -76.1581 | 115.2649 | 38.9786 | 24.4858 | 38.942
2326.9375 | 119.8791 | -0.16022 | 119.6274 | 0.005951 | 6.9793 | 0.064832 | 0.059374 | 0.00078177 | -0.0061139 | -0.0036486 | 0.0025025 | 0.0011642 | 0.013751 | 0.011281 | -0.0076947 | 0.027453 | 0.0011942 | 3.8452 | 119.5633 | -0.091553 | 119.5587 | 0.10986 | -0.059509 | -0.059509 | 0.013733 | -0.091553 | -0.022888 | 0.022888 | 0.082397 | 0.013733 | 0.11444 | 0.068664 | -0.064087 | -0.068664 | 0.27008 | 0.10071 | 0.10071 | 0.032044 | 0.032044 | 0.13733 | -119.7189 | -119.6045 | 0.24261 | 0.27466 | 0.17395 | 0.13733 | 0.036621 | 0.20142 | 119.6503 | 0.10528 | 0.045776 | 119.6548 | -0.068665 | 119.7235 | 0.068664 | -119.7189 | -119.6503 | 119.7189 | 0.1831 | 4.0054 | 0.17395
2328.6875 | 119.9661 | -0.21057 | 119.87 | -0.009308 | 6.9793 | 0.061415 | 0.059374 | -0.003277 | -0.0099591 | -0.0021532 | 0.0025025 | 0.0011642 | 0.015887 | 0.0078634 | -0.011754 | 0.026812 | -0.0022238 | 3.8452 | 119.7327 | -0.11902 | 119.6503 | 0.041199 | -0.091553 | -0.09613 | -0.13275 | -0.068665 | -0.041199 | -0.10071 | -0.027466 | -0.068665 | 0.004578 | 0.091552 | -0.13733 | -0.21973 | 0.25177 | 0.11444 | 0.11902 | 0.022889 | 0.027466 | 0.16937 | -119.9387 | -119.9707 | 0.18311 | 0.21515 | 0.14191 | 0.045777 | -0.027466 | 0.16022 | 119.7693 | 0.013733 | -0.059509 | 119.8517 | -0.027466 | 119.9432 | 0.14191 | -119.989 | -119.9112 | 119.8608 | 0.10986 | 4.0558 | 0.07782
2330.4219 | 120.0531 | -0.20599 | 119.9478 | -0.0016785 | 6.9784 | 0.059919 | 0.060656 | 0.0016364 | -0.0088911 | -0.0030078 | -0.0036011 | 0.0022324 | 0.013324 | 0.011281 | -0.01154 | 0.026598 | -8.7586e-05 | 3.7765 | 119.8883 | -0.14191 | 119.696 | -0.036621 | -0.15106 | -0.16022 | -0.15564 | -0.050354 | -0.082397 | -0.10986 | -0.050354 | -0.091553 | -0.004578 | 0.064087 | -0.059509 | -0.25177 | 0.16937 | 0.045777 | 0.054932 | -0.01831 | -0.009155 | 0.1236 | -119.9982 | -120.0577 | 0.15564 | 0.20142 | 0.11444 | 0.077819 | -0.009156 | 0.10529 | 119.838 | 0.032043 | -0.027466 | 120.0302 | 0.032043 | 120.0943 | 0.15564 | -120.0897 | -120.0302 | 119.902 | 0.096131 | 3.9825 | 0.050354
2332.1719 | 120.2133 | -0.16937 | 119.9799 | -0.009308 | 6.9771 | 0.062483 | 0.059161 | -0.00071343 | -0.0063275 | -0.00065803 | -0.0066527 | 0.0026596 | 0.013324 | 0.003591 | -0.0047039 | 0.026385 | -8.7586e-05 | 3.7628 | 119.9432 | -0.1236 | 119.8059 | 0.013733 | -0.14648 | -0.14648 | -0.07782 | -0.073242 | -0.050354 | -0.013733 | 0.032043 | -0.009155 | 0.086975 | 0.045777 | -0.036621 | -0.17395 | 0.18311 | 0.022889 | 0.022889 | -0.022888 | -0.022888 | 0.11902 | -120.0531 | -119.9936 | 0.20142 | 0.25635 | 0.16022 | 0.13733 | 0.041199 | 0.13733 | 119.9295 | 0.082397 | 0.036621 | 120.0668 | -0.022888 | 120.1126 | 0.096131 | -120.1035 | -120.0302 | 119.9753 | 0.15564 | 3.9322 | 0.091553
2333.8594 | 119.8563 | -0.20599 | 119.7418 | -0.0016785 | 6.9784 | 0.063123 | 0.062151 | 0.003559 | -0.0076093 | -0.003435 | -0.0066527 | 0.0030868 | 0.012256 | 0.0091452 | -0.0076947 | 0.026812 | -0.0017966 | 3.7491 | 119.6823 | -0.11902 | 119.5358 | -0.009155 | -0.15106 | -0.15106 | -0.1236 | -0.064087 | -0.054932 | -0.07782 | -0.045776 | -0.09613 | 0.009155 | 0.086975 | -0.059509 | -0.20599 | 0.19684 | 0.054932 | 0.054932 | -0.032043 | -0.032043 | 0.15106 | -119.8059 | -119.8196 | 0.16022 | 0.21515 | 0.10986 | 0.064087 | -0.041198 | 0.10986 | 119.6548 | 0.009156 | -0.022888 | 119.8013 | -0.009155 | 119.8883 | 0.14191 | -119.8608 | -119.7968 | 119.7418 | 0.12817 | 3.9551 | 0.082398
2335.5938 | 120.0668 | -0.19226 | 119.9432 | -0.0016785 | 6.9793 | 0.062483 | 0.063006 | 0.0054816 | -0.0091047 | -0.00087163 | -0.0036011 | 0.0015914 | 0.014819 | 0.003591 | -0.0089765 | 0.024676 | -0.0020102 | 3.7949 | 119.8929 | -0.13733 | 119.751 | 0.009155 | -0.14191 | -0.13733 | -0.10986 | -0.059509 | -0.045776 | -0.059509 | -0.041199 | -0.091553 | 0.018311 | 0.054932 | -0.050354 | -0.19226 | 0.20142 | 0.054932 | 0.050354 | 0 | -0.004578 | 0.14648 | -120.0027 | -120.0027 | 0.15106 | 0.21057 | 0.10071 | 0.064087 | -0.045777 | 0.14648 | 119.8883 | 0.004577 | -0.013733 | 120.0302 | -0.013733 | 120.0851 | 0.13275 | -120.0806 | -119.989 | 119.9432 | 0.13275 | 3.9871 | 0.082398
2337.3281 | 116.391 | -27.5208 | 88.6414 | -0.009308 | 6.9765 | 0.061842 | 0.059588 | 0.0037726 | -0.0080365 | 0.0012646 | -0.0036011 | 0.000737 | 0.015033 | 0.011281 | -0.010045 | 0.026171 | 0.0026896 | -9.8694 | 88.3713 | -27.7771 | 87.1536 | -28.6697 | -28.8025 | -28.5919 | -0.041199 | -0.050354 | -0.018311 | -0.018311 | 0.013733 | -0.027466 | 0.054932 | -0.25635 | -0.27008 | -1.4877 | -1.149 | -1.0712 | -1.2817 | -0.81482 | -1.0254 | 27.5024 | -88.6917 | -88.6597 | 27.5345 | 27.5757 | 27.4933 | 0.073243 | -0.009155 | -0.89264 | 114.9307 | 0.032044 | 0 | 116.1484 | -0.032043 | 115.892 | 27.4704 | -116.4185 | -88.6597 | 114.6744 | 27.5024 | 17.6514 | 27.4796
2339.0156 | 119.7968 | -0.17853 | 119.6091 | -0.024567 | 6.9778 | 0.063337 | 0.060229 | 0.0016364 | -0.0065411 | -0.0012988 | 0.0055543 | 0.0005234 | 0.014392 | 0.013845 | -0.0049175 | 0.027453 | -0.00072839 | 3.7079 | 119.5175 | -0.11444 | 119.458 | 0.059509 | -0.09613 | -0.082397 | -0.050354 | -0.086975 | -0.036621 | 0 | 0.022888 | -0.018311 | 0.059509 | 0.064087 | -0.091553 | -0.15106 | 0.23804 | 0.096131 | 0.082398 | 0.032044 | 0.018311 | 0.14191 | -119.696 | -119.6091 | 0.20142 | 0.23804 | 0.16022 | 0.09613 | 0.01831 | 0.17395 | 119.5724 | 0.059509 | 0.036621 | 119.632 | -0.050354 | 119.696 | 0.091553 | -119.7235 | -119.6457 | 119.6365 | 0.17853 | 3.8864 | 0.12817
2340.75 | 120.0119 | -0.16022 | 119.7464 | -0.016937 | 6.9784 | 0.064619 | 0.061938 | 0.0022772 | -0.0076093 | -0.0021532 | -0.00054933 | 0.0018052 | 0.015033 | 0.0093588 | -0.0040631 | 0.027239 | -0.0030784 | 3.7354 | 119.664 | -0.11444 | 119.6732 | 0.10529 | -0.054932 | -0.064087 | 0.018311 | -0.10986 | -0.041199 | 0.027466 | 0.082397 | 0.013733 | 0.10986 | 0.045776 | -0.082398 | -0.073242 | 0.2655 | 0.09613 | 0.10528 | 0.050354 | 0.059509 | 0.11902 | -119.8563 | -119.7189 | 0.24261 | 0.27008 | 0.17395 | 0.15106 | 0.054932 | 0.21973 | 119.7876 | 0.1236 | 0.068665 | 119.7784 | -0.068664 | 119.8242 | 0.050354 | -119.8608 | -119.7876 | 119.8334 | 0.18768 | 3.8956 | 0.17853
2342.5 | 120.0531 | -0.17395 | 119.8288 | 0.005951 | 6.9754 | 0.062696 | 0.059802 | -0.0024224 | -0.0076093 | -0.0021532 | -0.0066527 | 0.0005234 | 0.014819 | 0.014272 | -0.0083355 | 0.027666 | -0.001583 | 3.6575 | 119.7693 | -0.09613 | 119.696 | 0.027466 | -0.091553 | -0.09613 | -0.091553 | -0.09613 | -0.041199 | -0.027466 | 0.018311 | -0.036621 | 0.050354 | 0.07782 | -0.059509 | -0.13275 | 0.20142 | 0.07782 | 0.082397 | 0 | 0.004577 | 0.13275 | -119.9249 | -119.8563 | 0.19226 | 0.2243 | 0.13733 | 0.091553 | 0.004578 | 0.1236 | 119.7922 | 0.05951 | 0.013733 | 119.8654 | -0.054931 | 119.9432 | 0.07782 | -119.9249 | -119.87 | 119.87 | 0.14648 | 3.8315 | 0.082397
2344.25 | 120.0577 | -0.18768 | 119.9112 | -0.0016785 | 6.9797 | 0.061628 | 0.063006 | 0.0027044 | -0.0054731 | -0.0045032 | -0.00054933 | 0.0030868 | 0.015246 | 0.010427 | -0.0070539 | 0.026812 | -0.0037192 | 3.7033 | 119.8425 | -0.11902 | 119.7418 | 0.018311 | -0.13733 | -0.14648 | -0.082397 | -0.073242 | -0.073242 | -0.050354 | -0.018311 | -0.086975 | 0.032043 | 0.068664 | -0.068665 | -0.16937 | 0.20599 | 0.041199 | 0.050354 | -0.027465 | -0.01831 | 0.11444 | -119.9844 | -119.9615 | 0.16937 | 0.21973 | 0.10071 | 0.10529 | -0.013733 | 0.13733 | 119.8608 | 0.054931 | 0.022888 | 119.9615 | 0 | 120.0302 | 0.11444 | -120.0302 | -119.9844 | 119.9295 | 0.13733 | 3.891 | 0.10529
2345.9219 | 120.0943 | -0.19684 | 119.9524 | -0.009308 | 6.9795 | 0.063978 | 0.062151 | 0.0014228 | -0.0082501 | -0.002367 | -0.00054933 | 0.004155 | 0.013537 | 0.003591 | -0.0087629 | 0.025957 | -0.0013694 | 3.6896 | 119.9066 | -0.12817 | 119.7876 | 0.032043 | -0.10529 | -0.11444 | -0.082397 | -0.068665 | -0.054932 | -0.050354 | -0.009155 | -0.059509 | 0.032043 | 0.068664 | -0.045777 | -0.16479 | 0.22888 | 0.082397 | 0.091552 | 0.013733 | 0.022888 | 0.14191 | -120.0211 | -120.0027 | 0.18768 | 0.22888 | 0.13733 | 0.086975 | -0.004577 | 0.16022 | 119.9158 | 0.045777 | 0.004578 | 120.0348 | -0.013733 | 120.1035 | 0.12817 | -120.0806 | -120.0073 | 119.9844 | 0.14648 | 3.8864 | 0.11444
2347.6719 | 120.1492 | -0.20142 | 120.0073 | -0.009308 | 6.9789 | 0.064192 | 0.061083 | -0.00049983 | -0.0076093 | -0.0015124 | -0.0066527 | 0.0037278 | 0.016742 | 0.0085044 | -0.0066265 | 0.02553 | -0.0017966 | 3.6804 | 119.9432 | -0.13275 | 119.8151 | 0.013733 | -0.1236 | -0.14648 | -0.086975 | -0.073242 | -0.054932 | -0.059509 | -0.004578 | -0.064087 | 0.018311 | 0.068665 | -0.064087 | -0.19226 | 0.21515 | 0.054932 | 0.07782 | -0.013733 | 0.009155 | 0.14648 | -120.0806 | -120.0668 | 0.19684 | 0.21973 | 0.13733 | 0.073243 | -0.009155 | 0.14648 | 119.9478 | 0.050354 | -0.004577 | 120.076 | -0.01831 | 120.1447 | 0.12817 | -120.1401 | -120.0623 | 120.0165 | 0.14191 | 3.8818 | 0.11444
2349.4375 | 120.2545 | -0.16479 | 120.0073 | -0.0016785 | 6.9791 | 0.062269 | 0.057665 | -0.0017816 | -0.0091047 | -0.0030078 | -0.0036011 | -0.0003312 | 0.013751 | 0.014699 | -0.012395 | 0.026385 | 0.00055321 | 3.6484 | 119.9295 | -0.10986 | 119.9158 | 0.10071 | -0.032043 | -0.054932 | -0.004578 | -0.11902 | -0.045776 | -0.018311 | 0.086975 | 0.036621 | 0.091553 | 0.054932 | -0.07782 | -0.091553 | 0.2655 | 0.10986 | 0.13275 | 0.054931 | 0.07782 | 0.11902 | -120.1263 | -120.0256 | 0.25177 | 0.25635 | 0.20142 | 0.13733 | 0.082397 | 0.21057 | 120.0256 | 0.13275 | 0.027465 | 120.0394 | -0.073243 | 120.0943 | 0.045776 | -120.1172 | -120.0531 | 120.0806 | 0.14648 | 3.8132 | 0.16022
2351.1094 | 120.1996 | -0.21515 | 120.0668 | -0.0016785 | 6.9778 | 0.059492 | 0.062365 | 0.00185 | -0.0069683 | -0.0032214 | 0.0025025 | 0.0013778 | 0.013965 | 0.0078634 | -0.012608 | 0.024676 | -0.0017966 | 3.5889 | 120.0256 | -0.16022 | 119.8242 | -0.041199 | -0.14648 | -0.15564 | -0.16937 | -0.054932 | -0.059509 | -0.07782 | -0.032043 | -0.082397 | 0.018311 | 0.054932 | -0.041198 | -0.24261 | 0.17395 | 0.059509 | 0.068665 | 0.004577 | 0.013733 | 0.15564 | -120.1218 | -120.1447 | 0.18311 | 0.23346 | 0.13275 | 0.07782 | -0.022888 | 0.11902 | 119.9844 | 0.027466 | -0.018311 | 120.1859 | 0.004577 | 120.2408 | 0.16022 | -120.2271 | -120.1263 | 120.0394 | 0.13733 | 3.804 | 0.045776
2352.8438 | 120.2408 | -0.20599 | 120.0897 | -0.0016785 | 6.9806 | 0.062696 | 0.06322 | 0.0027044 | -0.0080365 | -0.003435 | -0.00054933 | 0.0033004 | 0.013965 | 0.0048728 | -0.010686 | 0.024889 | -0.00094199 | 3.598 | 120.0531 | -0.13733 | 119.8425 | -0.027466 | -0.14648 | -0.16479 | -0.16022 | -0.059509 | -0.07782 | -0.10071 | -0.036621 | -0.07782 | 0.004578 | 0.068665 | -0.036621 | -0.24719 | 0.17853 | 0.041199 | 0.05951 | -0.027466 | -0.009155 | 0.12817 | -120.1492 | -120.1904 | 0.16937 | 0.21057 | 0.12817 | 0.082398 | 0 | 0.10986 | 119.9799 | 0.041199 | -0.022888 | 120.1904 | 0.018311 | 120.2591 | 0.14649 | -120.2271 | -120.1675 | 120.0485 | 0.10529 | 3.804 | 0.045777
2354.5938 | 120.369 | -0.16479 | 120.0943 | -0.016937 | 6.9776 | 0.064619 | 0.059374 | 0.00078177 | -0.0084637 | -0.0049304 | -0.0036011 | 0.0005234 | 0.013324 | 0.009786 | -0.0091901 | 0.027666 | -0.0035056 | 3.5889 | 120.0485 | -0.10071 | 119.989 | 0.09613 | -0.027466 | -0.036621 | 0 | -0.10529 | -0.032043 | 0.027466 | 0.10071 | 0.041199 | 0.11902 | 0.064087 | -0.045776 | -0.10529 | 0.26092 | 0.12817 | 0.13733 | 0.064087 | 0.073242 | 0.13275 | -120.1996 | -120.0668 | 0.2655 | 0.28381 | 0.20599 | 0.15106 | 0.073242 | 0.19684 | 120.0897 | 0.13275 | 0.059509 | 120.1492 | -0.073243 | 120.2133 | 0.059509 | -120.195 | -120.1263 | 120.1538 | 0.19226 | 3.7537 | 0.16479
2356.3281 | 120.2728 | -0.22888 | 120.1401 | -0.0016785 | 6.9774 | 0.063337 | 0.060656 | 0.00078177 | -0.0095319 | -0.003435 | 0.0025025 | 0.0018052 | 0.01311 | 0.0074362 | -0.012181 | 0.025957 | -0.0020102 | 3.5385 | 120.0897 | -0.13275 | 119.9066 | -0.041199 | -0.14648 | -0.13733 | -0.16022 | -0.068665 | -0.073242 | -0.11902 | -0.054932 | -0.082397 | 0.009155 | 0.096131 | -0.050354 | -0.23346 | 0.18768 | 0.091553 | 0.082398 | -0.004578 | -0.013733 | 0.15564 | -120.2087 | -120.2591 | 0.17395 | 0.23804 | 0.14649 | 0.082397 | -0.009155 | 0.091552 | 120.0394 | 0.01831 | -0.045777 | 120.2225 | 0.004577 | 120.3186 | 0.16022 | -120.2728 | -120.2133 | 120.1355 | 0.10986 | 3.7674 | 0.068665
2358.0156 | 120.282 | -0.21057 | 120.1859 | -0.0016785 | 6.9795 | 0.062696 | 0.064288 | 0.00185 | -0.0078229 | -0.00065803 | -0.00054933 | 0.0033004 | 0.016314 | 0.011922 | -0.0085491 | 0.025957 | -0.0022238 | 3.511 | 120.1675 | -0.15564 | 119.9341 | -0.07782 | -0.20142 | -0.20142 | -0.19226 | -0.045776 | -0.064087 | -0.086975 | -0.073242 | -0.12817 | 0.022888 | 0.054931 | -0.01831 | -0.25177 | 0.13275 | 0.009155 | 0.009155 | -0.045776 | -0.045776 | 0.14648 | -120.2316 | -120.2728 | 0.13733 | 0.23346 | 0.082397 | 0.086975 | -0.064087 | 0.07782 | 120.0897 | -0.009155 | -0.022888 | 120.3232 | 0.018311 | 120.3781 | 0.1648 | -120.3415 | -120.2499 | 120.1447 | 0.1236 | 3.7216 | 0.01831
2359.7656 | 120.3186 | -0.20142 | 120.2133 | -0.016937 | 6.9793 | 0.063764 | 0.061938 | 0.0039862 | -0.0061139 | 0.0014784 | 0.0025025 | 0.0039414 | 0.016955 | 0.0076498 | -0.0066265 | 0.025103 | -0.0058554 | 3.5294 | 120.1721 | -0.14191 | 119.9936 | -0.045776 | -0.17853 | -0.16937 | -0.15564 | -0.050354 | -0.064087 | -0.07782 | -0.054932 | -0.11902 | 0.004578 | 0.059509 | -0.041199 | -0.21973 | 0.15564 | 0.032043 | 0.022888 | -0.027466 | -0.036621 | 0.13733 | -120.2637 | -120.2911 | 0.14648 | 0.20599 | 0.082397 | 0.068665 | -0.054932 | 0.096131 | 120.1355 | 0.009155 | -0.013733 | 120.314 | 0.013733 | 120.3735 | 0.15106 | -120.3552 | -120.2774 | 120.195 | 0.1236 | 3.7308 | 0.045776
2361.5 | 120.3964 | -0.20142 | 120.2362 | -0.016937 | 6.9782 | 0.061415 | 0.062792 | 0.0037726 | -0.0080365 | -0.001726 | 0.0025025 | 0.0026596 | 0.01546 | 0.012136 | -0.0089765 | 0.025103 | -0.0028646 | 3.4927 | 120.2042 | -0.15106 | 120.0165 | -0.041199 | -0.1236 | -0.13733 | -0.14648 | -0.050354 | -0.068665 | -0.068665 | -0.009155 | -0.07782 | 0.032043 | 0.050354 | -0.032043 | -0.21973 | 0.16022 | 0.064087 | 0.07782 | 0.013733 | 0.027466 | 0.13275 | -120.2866 | -120.3049 | 0.19226 | 0.23346 | 0.1236 | 0.10071 | -0.009155 | 0.10986 | 120.1675 | 0.05951 | 0 | 120.3552 | 0.018311 | 120.4056 | 0.15106 | -120.3873 | -120.3049 | 120.2179 | 0.13275 | 3.6942 | 0.054932
2363.2344 | 120.3644 | -0.22888 | 120.2454 | -0.016937 | 6.9791 | 0.061628 | 0.06087 | -0.0024224 | -0.0099591 | -1.7026e-05 | -0.00054933 | 0.0013778 | 0.013965 | 0.008718 | -0.0094037 | 0.026385 | -0.0030784 | 3.4653 | 120.1904 | -0.11902 | 120.0485 | 0.009155 | -0.13275 | -0.14648 | -0.15106 | -0.068665 | -0.050354 | -0.10071 | -0.022888 | -0.082397 | 0 | 0.10986 | -0.054931 | -0.19684 | 0.23804 | 0.082398 | 0.096131 | -0.027465 | -0.013732 | 0.17853 | -120.314 | -120.3461 | 0.20599 | 0.22888 | 0.14649 | 0.050354 | -0.032043 | 0.12817 | 120.1675 | 0.027466 | -0.050354 | 120.3094 | -0.018311 | 120.4193 | 0.16022 | -120.3644 | -120.2957 | 120.2774 | 0.12817 | 3.6942 | 0.07782
2364.9062 | 120.4926 | -0.16022 | 120.2637 | 0.005951 | 6.9765 | 0.06291 | 0.061297 | 0.0033454 | -0.0073957 | -0.0025806 | 0.0025025 | 0.0015914 | 0.01546 | 0.01235 | -0.0083355 | 0.027239 | -0.0017966 | 3.4607 | 120.2087 | -0.11444 | 120.1309 | 0.07782 | -0.09613 | -0.07782 | -0.032043 | -0.091553 | -0.050354 | -0.009155 | 0.036621 | -0.004578 | 0.073242 | 0.045776 | -0.054932 | -0.13275 | 0.23804 | 0.082397 | 0.064087 | 0.036621 | 0.018311 | 0.10986 | -120.3552 | -120.2728 | 0.19684 | 0.23346 | 0.15564 | 0.1236 | 0.045776 | 0.19226 | 120.2454 | 0.086975 | 0.041199 | 120.3232 | -0.041199 | 120.369 | 0.068664 | -120.3781 | -120.314 | 120.2911 | 0.15106 | 3.6209 | 0.12817
2366.6406 | 120.5566 | -0.15106 | 120.2728 | -0.016937 | 6.9771 | 0.063123 | 0.06386 | 0.0046272 | -0.0067547 | -0.0010852 | -0.0036011 | 0.0005234 | 0.016528 | 0.012136 | -0.0042767 | 0.027453 | -0.0024374 | 3.4561 | 120.2271 | -0.10071 | 120.1859 | 0.086975 | -0.068665 | -0.082397 | 0.013733 | -0.10986 | -0.032043 | 0.036621 | 0.082397 | 0.032043 | 0.12817 | 0.050354 | -0.045776 | -0.086975 | 0.23804 | 0.068665 | 0.082397 | 0.018311 | 0.032043 | 0.11902 | -120.3827 | -120.2362 | 0.23346 | 0.27924 | 0.18311 | 0.16022 | 0.064086 | 0.18768 | 120.2866 | 0.11444 | 0.068664 | 120.3278 | -0.07782 | 120.3781 | 0.041199 | -120.3735 | -120.3049 | 120.3369 | 0.18768 | 3.6072 | 0.16479
2368.3125 | 120.5612 | -0.19684 | 120.3186 | 0.005951 | 6.9759 | 0.063337 | 0.061083 | -0.003277 | -0.0054731 | -0.002367 | -0.0036011 | 0.0005234 | 0.012897 | 0.020894 | -0.0094037 | 0.028521 | 0.00055321 | 3.3783 | 120.2682 | -0.11444 | 120.1492 | 0.018311 | -0.091553 | -0.10986 | -0.082397 | -0.091553 | -0.045776 | -0.027466 | 0.036621 | 0.004578 | 0.082397 | 0.082397 | -0.050354 | -0.16937 | 0.21515 | 0.086975 | 0.10529 | 0.004578 | 0.022888 | 0.15106 | -120.4102 | -120.3461 | 0.23346 | 0.27924 | 0.20142 | 0.12817 | 0.050354 | 0.13275 | 120.2637 | 0.082397 | 0.01831 | 120.3827 | -0.045777 | 120.4651 | 0.10529 | -120.433 | -120.3644 | 120.3461 | 0.16937 | 3.5751 | 0.11444
2369.9844 | 118.483 | -26.4542 | 91.6534 | -0.0016785 | 6.9795 | 0.063764 | 0.06386 | 0.00099557 | -0.0069683 | -0.003435 | -0.0036011 | 0.0054368 | 0.015674 | 0.012136 | -0.0085491 | 0.026812 | -0.001583 | -15.2344 | 92.2119 | -26.1795 | 91.7221 | -26.5961 | -26.825 | -26.857 | -0.041199 | -0.036621 | -0.032043 | -0.032043 | 0.054932 | -0.027466 | 0.068665 | 0.27466 | 0.55847 | 0.068665 | -0.14191 | -0.40283 | -0.37079 | -0.67749 | -0.64545 | 26.4221 | -91.6901 | -91.6855 | 26.5091 | 26.5228 | 26.4267 | 0.10071 | 0.004577 | -0.41656 | 117.9016 | 0.086975 | 0 | 118.3914 | -0.004578 | 118.6661 | 26.4175 | -117.8329 | -91.6855 | 118.1763 | 26.4221 | 11.2198 | 26.413
2371.7344 | 115.9882 | -33.7189 | 81.9443 | 0.02121 | 6.9803 | 0.062055 | 0.058306 | 0.0031318 | -0.0063275 | -0.001726 | -0.00054933 | 0.0022324 | 0.014605 | 0.011709 | -0.0066265 | 0.030443 | -0.0022238 | -15.4587 | 81.5369 | -33.9386 | 81.7886 | -33.9935 | -34.4467 | -34.4376 | 0.022888 | -0.073242 | -0.022888 | 0.054932 | 0.10529 | 0.054932 | 0.12817 | -0.21973 | -0.40741 | -0.15564 | -0.27466 | -0.71869 | -0.72784 | -0.49896 | -0.50812 | 33.696 | -82.0175 | -81.8893 | 33.8242 | 33.847 | 33.7738 | 0.15106 | 0.07782 | -0.054931 | 115.7272 | 0.12817 | 0.07782 | 115.4755 | -0.050354 | 115.2557 | 33.6456 | -115.8829 | -81.9672 | 115.5075 | 33.7738 | 18.2602 | 33.7418
2373.4844 | 119.7784 | -2.8427 | 117.0502 | -0.0016785 | 6.9784 | 0.06291 | 0.060015 | 0.0012092 | -0.0080365 | -0.003435 | -0.00054933 | 0.0020188 | 0.012683 | 0.012777 | -0.0091901 | 0.028307 | -0.0045736 | 1.7899 | 117.0181 | -2.742 | 116.8121 | -2.6596 | -2.8015 | -2.8107 | -0.17395 | -0.064087 | -0.054932 | -0.10071 | -0.054932 | -0.11444 | 0.027466 | 0.10071 | -0.032044 | -0.23804 | 0.18311 | 0.032043 | 0.041198 | -0.068665 | -0.05951 | 2.7878 | -117.1143 | -117.1509 | 2.7878 | 2.8702 | 2.7283 | 0.082398 | -0.059509 | 0.082397 | 119.5541 | 0 | -0.045776 | 119.7601 | -0.009155 | 119.8608 | 2.7786 | -119.7922 | -117.1051 | 119.6548 | 2.742 | 4.6326 | 2.6688
2375.2344 | 119.9112 | -1.8082 | 118.2312 | -0.016937 | 6.9782 | 0.064832 | 0.060229 | -0.001568 | -0.0080365 | -0.0025806 | -0.0036011 | 0.0020188 | 0.017596 | 0.018117 | -0.0076947 | 0.025744 | -0.0030784 | 2.3392 | 118.1717 | -1.7303 | 117.9657 | -1.6342 | -1.7899 | -1.767 | -0.14191 | -0.073242 | -0.073242 | -0.09613 | -0.045776 | -0.09613 | 0.022888 | 0.07782 | -0.059509 | -0.2655 | 0.17395 | 0.041199 | 0.018311 | -0.036621 | -0.059509 | 1.7349 | -118.3044 | -118.3273 | 1.7624 | 1.8311 | 1.712 | 0.09613 | -0.022888 | 0.096131 | 119.696 | 0.027466 | -0.022888 | 119.902 | 0 | 119.9799 | 1.7349 | -119.9615 | -118.3044 | 119.7739 | 1.712 | 4.1473 | 1.6663
2376.9219 | 119.8746 | -0.99792 | 118.8446 | -0.009308 | 6.9791 | 0.06291 | 0.059588 | 0.0014228 | -0.0061139 | -0.0038622 | -0.00054933 | 0.0005234 | 0.015033 | 0.015127 | -0.011326 | 0.028948 | -0.0017966 | 2.7786 | 118.7622 | -0.92468 | 118.7073 | -0.72327 | -0.91095 | -0.9201 | -0.045776 | -0.086975 | -0.027466 | -0.013733 | 0.041199 | -0.009155 | 0.07782 | 0.073242 | -0.082397 | -0.13733 | 0.27466 | 0.07782 | 0.086975 | 0.004578 | 0.013733 | 0.97046 | -118.9316 | -118.8583 | 1.0391 | 1.0757 | 0.98877 | 0.10529 | 0.018311 | 0.20142 | 119.632 | 0.068665 | 0.013733 | 119.6869 | -0.059509 | 119.7601 | 0.91095 | -119.7693 | -118.8721 | 119.7052 | 0.98419 | 3.7765 | 0.95215
2378.6562 | 120.0302 | -1.0025 | 119.0186 | -0.009308 | 6.978 | 0.065687 | 0.061297 | -0.0019952 | -0.0078229 | -0.0045032 | -0.00054933 | 0.0018052 | 0.012469 | 0.015127 | -0.0064129 | 0.03023 | -0.0022238 | 2.6825 | 119.0002 | -0.94757 | 118.7897 | -0.83771 | -0.98877 | -0.98419 | -0.10071 | -0.07782 | -0.07782 | -0.036621 | 0.004578 | -0.041199 | 0.064087 | 0.054931 | -0.018311 | -0.22888 | 0.16479 | 0.01831 | 0.013732 | -0.036621 | -0.041199 | 0.92468 | -119.0964 | -119.0552 | 1.0071 | 1.0666 | 0.9613 | 0.14191 | 0.036621 | 0.10986 | 119.7372 | 0.082398 | 0.041199 | 119.9478 | 0 | 120.0027 | 0.92468 | -119.9661 | -119.0964 | 119.7922 | 0.96588 | 3.685 | 0.90179
2380.4062 | 120.0256 | -1.1536 | 118.9453 | -0.009308 | 6.9801 | 0.061415 | 0.06087 | -0.0019952 | -0.0091047 | -0.0049304 | -0.00054933 | 0.0020188 | 0.017169 | 0.012777 | -0.01154 | 0.025744 | 0.00033961 | 2.6093 | 118.895 | -1.0941 | 118.7073 | -0.97961 | -1.0986 | -1.1078 | -0.15564 | -0.045776 | -0.068665 | -0.12817 | -0.041199 | -0.082397 | -0.009155 | 0.059509 | -0.050354 | -0.23804 | 0.17395 | 0.045776 | 0.054931 | -0.013733 | -0.004578 | 1.0849 | -118.9911 | -119.0735 | 1.1124 | 1.1444 | 1.0712 | 0.05951 | -0.013732 | 0.11444 | 119.8013 | 0.027466 | -0.059509 | 119.989 | 0.022889 | 120.0485 | 1.1078 | -120.0394 | -119.014 | 119.8608 | 1.0254 | 3.7628 | 0.99792
2382.0781 | 117.6178 | -48.3902 | 69.223 | -0.016937 | 6.978 | 0.065473 | 0.059588 | 0.006336 | -0.0080365 | -0.0042896 | -0.0036011 | 0.0013778 | 0.015246 | 0.009786 | -0.0068403 | 0.02788 | -0.0020102 | -23.8174 | 68.4677 | -47.4152 | 71.022 | -46.5729 | -48.0515 | -48.4955 | 0.045776 | -0.054932 | 0.009155 | 0.068665 | 0.11444 | 0.068665 | 0.15564 | 0.97504 | -0.75531 | 1.799 | 1.8173 | -0.10529 | 0.33874 | -1.0803 | -0.63629 | 48.3994 | -69.278 | -69.1544 | 48.5046 | 48.5458 | 48.4589 | 0.14649 | 0.05951 | 0.84228 | 118.4372 | 0.10529 | 0.05951 | 115.8829 | -0.064087 | 116.8579 | 48.3353 | -116.6382 | -69.2139 | 119.4122 | 48.4589 | 24.5728 | 48.436
2383.8125 | 119.9203 | -4.3716 | 115.4709 | -0.0016785 | 6.9771 | 0.061842 | 0.060015 | 0.0024908 | -0.010386 | -0.0019396 | -0.00054933 | 0.000737 | 0.012897 | 0.014699 | -0.0094037 | 0.025744 | -0.0024374 | 0.67291 | 115.4251 | -4.3076 | 115.3564 | -4.1519 | -4.3121 | -4.3304 | -0.054932 | -0.09613 | -0.045776 | -0.022888 | 0.036621 | -0.004578 | 0.059509 | 0.064087 | -0.045776 | -0.11444 | 0.21973 | 0.041199 | 0.059509 | -0.022888 | -0.004578 | 4.3259 | -115.567 | -115.4938 | 4.4083 | 4.4312 | 4.3671 | 0.10528 | 0.041198 | 0.15564 | 119.664 | 0.082397 | 0.022888 | 119.7327 | -0.050354 | 119.7968 | 4.2755 | -119.7784 | -115.5167 | 119.7281 | 4.3488 | 5.0446 | 4.3167
2385.5625 | 120.0119 | -4.2068 | 115.8417 | -0.009308 | 6.9789 | 0.06291 | 0.059374 | 0.0024908 | -0.0071821 | -0.003435 | -0.0036011 | 0.0028732 | 0.015246 | 0.0048728 | -0.010045 | 0.027666 | -0.0047874 | 0.78278 | 115.7318 | -4.1199 | 115.7318 | -3.9139 | -4.0558 | -4.1016 | -0.064087 | -0.07782 | -0.054932 | -0.045776 | 0.032043 | -0.022888 | 0.050354 | 0.086975 | -0.10986 | -0.10986 | 0.29297 | 0.10529 | 0.15106 | 0.018311 | 0.064087 | 4.1519 | -115.9195 | -115.8875 | 4.2389 | 4.2572 | 4.184 | 0.10529 | 0.032044 | 0.20599 | 119.8517 | 0.086975 | 0.009156 | 119.8517 | -0.022888 | 119.9387 | 4.129 | -119.9615 | -115.8966 | 119.9387 | 4.1611 | 4.9896 | 4.1428
2387.3125 | 119.8929 | -3.891 | 116.0568 | 0.005951 | 6.9791 | 0.062483 | 0.061511 | 0.00185 | -0.0067547 | -0.002367 | -0.00054933 | 0.0060776 | 0.017383 | 0.0023092 | -0.0094037 | 0.027453 | -0.0056418 | 0.91553 | 116.0294 | -3.8498 | 115.892 | -3.653 | -3.8086 | -3.8177 | -0.07782 | -0.064087 | -0.068665 | -0.045776 | 0.022888 | -0.050354 | 0.059509 | 0.041199 | -0.027466 | -0.1648 | 0.23804 | 0.073242 | 0.082397 | 0.032043 | 0.041198 | 3.8223 | -116.1209 | -116.1026 | 3.9139 | 3.9505 | 3.8406 | 0.12817 | 0.018311 | 0.19684 | 119.7418 | 0.091553 | 0.022889 | 119.8791 | 0.004578 | 119.9203 | 3.8269 | -119.9066 | -116.1255 | 119.783 | 3.8452 | 4.8065 | 3.8132
2388.9844 | 120.0806 | -4.216 | 115.8005 | -0.009308 | 6.9797 | 0.065046 | 0.060656 | -0.00028623 | -0.0099591 | -0.00065803 | 0.0025025 | 0.0030868 | 0.014819 | 0.01299 | -0.0074811 | 0.026812 | -0.0028646 | 0.68207 | 115.7867 | -4.1382 | 115.7227 | -3.9276 | -4.1199 | -4.1336 | 0.004578 | -0.086975 | -0.036621 | -0.004578 | 0.068665 | 0.004578 | 0.09613 | 0.077819 | -0.013733 | -0.07782 | 0.28839 | 0.082397 | 0.09613 | 0.004578 | 0.018311 | 4.1794 | -115.8875 | -115.8051 | 4.2847 | 4.3121 | 4.2206 | 0.13275 | 0.041199 | 0.21057 | 119.8608 | 0.10529 | 0.032043 | 119.9249 | -0.050354 | 120.0027 | 4.129 | -119.9387 | -115.8371 | 119.9387 | 4.2114 | 4.8981 | 4.2206
2390.7344 | 120.1859 | -3.8315 | 116.2354 | -0.0016785 | 6.9806 | 0.063123 | 0.058947 | -0.003277 | -0.0061139 | -0.0019396 | -0.00054933 | 0.0022324 | 0.015246 | 0.018545 | -0.0096173 | 0.027025 | 0.00098061 | 0.87433 | 116.1713 | -3.7765 | 116.153 | -3.5431 | -3.7079 | -3.7537 | -0.004578 | -0.086975 | -0.045776 | 0.004578 | 0.09613 | 0.041199 | 0.10529 | 0.054932 | -0.064087 | -0.082398 | 0.28839 | 0.07782 | 0.1236 | 0.022888 | 0.068664 | 3.7857 | -116.3223 | -116.2308 | 3.9276 | 3.9368 | 3.8727 | 0.15106 | 0.086975 | 0.23346 | 119.9295 | 0.14191 | 0.050354 | 119.9478 | -0.041199 | 120.0027 | 3.7445 | -120.0119 | -116.2811 | 119.9844 | 3.8361 | 4.7058 | 3.8269
2392.4844 | 119.7601 | -73.114 | 46.2662 | -0.0016785 | 6.9818 | 0.066541 | 0.062792 | 0.00035457 | -0.0091047 | -0.0012988 | 0.0025025 | 0.004155 | 0.014605 | 0.013204 | -0.0068403 | 0.026812 | -0.0022238 | -40.567 | 47.9645 | -71.846 | 47.8729 | -71.9101 | -73.1232 | -73.4528 | -0.11902 | 0.004578 | -0.004578 | -0.032043 | -0.009155 | -0.068665 | 0.073242 | 1.268 | 1.6983 | 1.6068 | 1.2039 | -0.33875 | -0.009155 | -1.6068 | -1.2772 | 73.1094 | -46.2616 | -46.2982 | 73.1049 | 73.1873 | 73.0453 | 0.07782 | -0.064087 | -0.064087 | 119.7189 | -0.004577 | -0.027465 | 119.8105 | 0.009156 | 121.0785 | 73.1186 | -118.1122 | -46.2708 | 120.9869 | 73.082 | 32.547 | 72.995
2394.1562 | 120.0302 | -5.7724 | 114.3356 | -0.0016785 | 6.9791 | 0.061842 | 0.060229 | 0.00185 | -0.0084637 | -0.002367 | 0.0025025 | 0.0030868 | 0.013537 | 0.011709 | -0.0064129 | 0.025957 | -0.0071372 | -0.29755 | 114.267 | -5.7175 | 114.1205 | -5.603 | -5.7037 | -5.7404 | -0.13733 | -0.032043 | -0.064087 | -0.073242 | -0.004578 | -0.059509 | 0.045776 | 0.054932 | -0.068664 | -0.21515 | 0.16937 | 0.032044 | 0.068665 | -0.022888 | 0.013733 | 5.7083 | -114.3677 | -114.4089 | 5.7678 | 5.8182 | 5.7129 | 0.10986 | 0.004578 | 0.11444 | 119.838 | 0.059509 | -0.009155 | 119.9844 | 0.032044 | 120.0394 | 5.7404 | -120.0531 | -114.3997 | 119.8929 | 5.6992 | 5.4749 | 5.6351
2395.9062 | 120.0897 | -2.9343 | 117.2699 | 0.005951 | 6.9818 | 0.063123 | 0.062579 | 0.0024908 | -0.0063275 | 0.00041017 | -0.00054933 | 0.003514 | 0.015033 | 0.0044454 | -0.0061993 | 0.025957 | -0.0020102 | 1.268 | 117.2379 | -2.8656 | 117.0547 | -2.7191 | -2.8931 | -2.8976 | -0.14191 | -0.059509 | -0.050354 | -0.10071 | -0.054932 | -0.11444 | 0.013733 | 0.068664 | -0.032043 | -0.21515 | 0.21515 | 0.036621 | 0.041199 | -0.032043 | -0.027465 | 2.8839 | -117.3294 | -117.3706 | 2.8793 | 2.948 | 2.8198 | 0.064087 | -0.064087 | 0.14648 | 119.9203 | -0.004578 | -0.050354 | 120.1035 | -0.009155 | 120.1721 | 2.8748 | -120.1355 | -117.3203 | 119.989 | 2.8336 | 4.2023 | 2.7924
2397.5938 | 120.2499 | -2.3895 | 117.7597 | 0.01358 | 6.9786 | 0.063764 | 0.061083 | -0.0011408 | -0.0061139 | -0.0040758 | -0.00054933 | 0.0020188 | 0.018878 | 0.0091452 | -0.0047039 | 0.029589 | -0.0047874 | 1.5793 | 117.7277 | -2.3163 | 117.7094 | -2.0782 | -2.2751 | -2.2797 | 0.032043 | -0.09613 | -0.032043 | 0.036621 | 0.07782 | 0.013733 | 0.11444 | 0.073242 | -0.032044 | -0.050354 | 0.31128 | 0.10986 | 0.11444 | 0.036621 | 0.041199 | 2.3575 | -117.8558 | -117.7231 | 2.4673 | 2.504 | 2.4033 | 0.14648 | 0.045776 | 0.23804 | 120.0256 | 0.10986 | 0.068664 | 120.0439 | -0.064087 | 120.1172 | 2.2934 | -120.076 | -117.7917 | 120.0989 | 2.4261 | 3.9688 | 2.4216
2399.3281 | 120.2499 | -1.9501 | 118.2541 | 0.01358 | 6.9776 | 0.063337 | 0.062151 | -0.0013544 | -0.0078229 | -0.0019396 | -0.0036011 | 0.004155 | 0.016742 | 0.0072226 | -0.0027813 | 0.027239 | -0.0054282 | 1.767 | 118.2312 | -1.9043 | 118.071 | -1.7899 | -1.9501 | -1.9501 | -0.10529 | -0.073242 | -0.064087 | -0.045776 | 0.009155 | -0.041199 | 0.064087 | 0.045776 | -0.022888 | -0.1831 | 0.16022 | 0 | 0 | -0.045776 | -0.045776 | 1.886 | -118.3273 | -118.2999 | 1.9592 | 2.0142 | 1.9089 | 0.12817 | 0.022888 | 0.11444 | 119.9753 | 0.073242 | 0.018311 | 120.1355 | -0.009155 | 120.1813 | 1.8768 | -120.1584 | -118.3182 | 120.0211 | 1.9043 | 3.717 | 1.8448
2401.0781 | 117.009 | -53.9612 | 63.0981 | -0.009308 | 6.9765 | 0.065687 | 0.064074 | 0.0067634 | -0.0063275 | -0.0021532 | -0.00054933 | 0.0043686 | 0.014605 | 0.011922 | -0.010258 | 0.028094 | -0.0054282 | -31.4667 | 62.6907 | -54.126 | 62.9242 | -53.7827 | -54.2404 | -54.4098 | -0.15106 | -0.022888 | -0.027466 | -0.073242 | -0.013733 | -0.059509 | 0.073242 | -0.16479 | -0.40741 | -0.17395 | 0.17853 | -0.44861 | -0.27923 | -0.28381 | -0.11444 | 53.9337 | -63.121 | -63.1714 | 53.9474 | 54.0344 | 53.9017 | 0.10071 | -0.032043 | 0.34332 | 117.0502 | 0.013733 | -0.045776 | 116.8167 | 0.004578 | 116.6519 | 53.9383 | -117.2241 | -63.1256 | 116.8854 | 53.8879 | 22.4945 | 53.8101
2402.8281 | 120.1218 | -2.4078 | 117.5812 | 0.005951 | 6.9791 | 0.06291 | 0.060656 | 0.00078177 | -0.0059003 | -0.0019396 | 0.0055543 | 0.0005234 | 0.01546 | 0.011281 | -0.0055585 | 0.029589 | -0.0028646 | 1.4282 | 117.5446 | -2.3392 | 117.485 | -2.1606 | -2.3254 | -2.33 | 0 | -0.09613 | -0.027466 | 0.050354 | 0.09613 | 0.036621 | 0.13275 | 0.068665 | -0.036621 | -0.096131 | 0.24719 | 0.07782 | 0.082398 | 0.009155 | 0.013733 | 2.3804 | -117.6773 | -117.5308 | 2.504 | 2.5406 | 2.4445 | 0.16022 | 0.064087 | 0.17853 | 119.8242 | 0.1236 | 0.07782 | 119.8837 | -0.068664 | 119.9524 | 2.3117 | -119.9203 | -117.6086 | 119.8929 | 2.4582 | 3.8361 | 2.4078
2404.5156 | 120.1263 | -2.2751 | 117.9108 | 0.005951 | 6.9786 | 0.063551 | 0.06322 | 0.0054816 | -0.0050457 | -0.00087163 | -0.00054933 | 0.0050094 | 0.017169 | 0.010641 | -0.010258 | 0.02788 | -0.0052146 | 1.4832 | 117.8879 | -2.2064 | 117.6819 | -2.1103 | -2.2522 | -2.2614 | -0.15106 | -0.054932 | -0.073242 | -0.09613 | -0.064087 | -0.11444 | 0.027466 | 0.068664 | -0.022889 | -0.22888 | 0.16479 | 0.013732 | 0.022888 | -0.054932 | -0.045776 | 2.2018 | -117.9657 | -118.0069 | 2.211 | 2.3026 | 2.1606 | 0.10071 | -0.041199 | 0.09613 | 119.8883 | 0.009155 | -0.022888 | 120.0943 | 0.01831 | 120.163 | 2.2202 | -120.1172 | -117.984 | 119.957 | 2.179 | 3.7582 | 2.124
2406.25 | 120.1904 | -2.5452 | 117.7277 | -0.0016785 | 6.9778 | 0.061628 | 0.060442 | -0.001568 | -0.0095319 | -0.0045032 | 0.0025025 | 0.0018052 | 0.015674 | 0.014913 | -0.011967 | 0.027025 | -0.0047874 | 1.2772 | 117.6407 | -2.4673 | 117.485 | -2.3346 | -2.4628 | -2.4811 | -0.13275 | -0.054932 | -0.064087 | -0.10071 | -0.032043 | -0.073242 | 0 | 0.07782 | -0.086975 | -0.24262 | 0.21057 | 0.064087 | 0.082397 | -0.013733 | 0.004577 | 2.4811 | -117.7826 | -117.8284 | 2.5131 | 2.5452 | 2.4719 | 0.064087 | -0.009155 | 0.13275 | 119.9524 | 0.032044 | -0.036621 | 120.108 | 0.009155 | 120.1859 | 2.4902 | -120.195 | -117.7917 | 120.0302 | 2.4445 | 3.8223 | 2.4124
2407.9219 | 117.9565 | -63.2629 | 54.6204 | -0.009308 | 6.9756 | 0.066969 | 0.063006 | 0.00014097 | -0.0061139 | -0.0030078 | -0.00054933 | 0.0013778 | 0.016314 | 0.011709 | -0.0083355 | 0.026171 | -0.00051479 | -37.9623 | 56.1356 | -61.8027 | 52.3865 | -65.0391 | -64.9246 | -64.8743 | -0.13275 | 0.013733 | -0.004578 | -0.054932 | -0.027466 | -0.086975 | 0.054932 | 1.4603 | 1.5152 | -2.2339 | -1.7761 | -1.6113 | -1.6617 | -3.0716 | -3.1219 | 63.2584 | -54.6066 | -54.6753 | 63.2355 | 63.3179 | 63.176 | 0.05951 | -0.082397 | -3.2364 | 114.1891 | -0.022888 | -0.050354 | 117.9382 | 0.018311 | 119.3985 | 63.2767 | -116.423 | -54.6249 | 115.6494 | 63.208 | 25.3006 | 63.1302
2409.6562 | 120.0119 | -8.0978 | 111.0992 | 0.005951 | 6.9791 | 0.064619 | 0.060442 | 0.0016364 | -0.0073957 | -0.0025806 | -0.00054933 | 0.0018052 | 0.013537 | 0.015981 | -0.0079083 | 0.027239 | 0.0016214 | -2.2064 | 112.2528 | -7.5668 | 111.9278 | -7.7408 | -7.9285 | -7.9147 | -0.054932 | -0.07782 | 0.14191 | -0.013733 | 0.027466 | -0.004578 | 0.086975 | 0.53101 | 1.1536 | 0.82855 | 0.35706 | 0.18311 | 0.16937 | -0.3479 | -0.36163 | 8.2397 | -111.1771 | -111.113 | 8.1253 | 8.1848 | 8.0933 | -0.054932 | -0.14649 | -0.17395 | 119.4946 | -0.11444 | -0.15564 | 119.8196 | -0.21973 | 120.3506 | 8.02 | -118.6661 | -110.9573 | 120.0256 | 8.0841 | 5.8914 | 8.0429
2411.3906 | 120.1904 | -7.2922 | 112.0148 | -0.0016785 | 6.9797 | 0.063123 | 0.061724 | -7.2628e-05 | -0.0073957 | -0.001726 | -0.00054933 | 0.0056504 | 0.013751 | 0.015127 | -0.0068403 | 0.02788 | -0.0028646 | -2.1286 | 112.6053 | -7.3563 | 112.175 | -7.3746 | -7.4066 | -7.37 | -0.036621 | -0.07782 | 0.018311 | 0.027466 | 0.059509 | 0.009155 | 0.13733 | -0.064087 | 0.59052 | 0.16022 | -0.082398 | -0.07782 | -0.11444 | -0.013733 | -0.050354 | 7.3105 | -112.0926 | -111.9873 | 7.3517 | 7.4295 | 7.3013 | 0.11902 | -0.009156 | -0.018311 | 119.5312 | 0.041198 | 0.009155 | 119.9615 | -0.096131 | 119.8975 | 7.2144 | -119.371 | -111.9965 | 119.4672 | 7.3196 | 5.1636 | 7.2556
2413.0625 | 116.1758 | -41.9678 | 78.0029 | 0.01358 | 6.975 | 0.061842 | 0.06087 | -0.0039178 | -0.0099591 | -0.0010852 | 0.0025025 | 0.0030868 | 0.014392 | 0.0078634 | -0.011113 | 0.027666 | -8.7586e-05 | -22.9202 | 77.8702 | -41.9632 | 78.5706 | -41.0614 | -41.4368 | -41.716 | 0.064087 | -0.054932 | -0.022888 | 0.059509 | 0.11902 | 0.09613 | 0.16022 | 0.004577 | -0.13275 | 0.56763 | 0.90637 | 0.25177 | 0.53101 | 0.24719 | 0.52643 | 41.9449 | -78.0579 | -77.9434 | 42.0868 | 42.128 | 42.0639 | 0.1831 | 0.11902 | 0.9018 | 120.5338 | 0.14191 | 0.082397 | 119.8334 | -0.032044 | 119.838 | 41.9128 | -119.9661 | -78.0258 | 120.5383 | 42.0273 | 19.0475 | 42.0319
2414.8125 | 119.8608 | -31.8008 | 87.7762 | 0.005951 | 6.9793 | 0.063764 | 0.057879 | -0.0011408 | -0.0067547 | -0.001726 | -0.0036011 | 0.0028732 | 0.013324 | 0.013418 | -0.01154 | 0.028094 | -0.0054282 | -18.2648 | 88.1012 | -31.4346 | 88.1836 | -31.366 | -31.7322 | -32.1213 | -0.004578 | -0.064087 | 0.14191 | -0.004578 | 0.068665 | 0.013733 | 0.082397 | 0.36621 | 0.32501 | 0.40741 | 0.43487 | -0.32043 | 0.068664 | -0.68665 | -0.29755 | 31.9427 | -87.8403 | -87.7808 | 31.8695 | 31.8832 | 31.8146 | -0.05951 | -0.12817 | 0.068664 | 119.6182 | -0.073242 | -0.14649 | 119.5358 | -0.20599 | 119.902 | 31.7368 | -119.2108 | -87.6343 | 119.9844 | 31.7963 | 13.5361 | 31.7963
2416.5469 | 119.8105 | -35.376 | 83.7021 | -0.009308 | 6.981 | 0.063123 | 0.061724 | 0.00014097 | -0.0093183 | -0.0045032 | 0.0025025 | 0.0030868 | 0.014392 | 0.010213 | -0.011113 | 0.027025 | -0.0022238 | -21.2814 | 83.1985 | -36.0626 | 83.5236 | -35.7513 | -36.0123 | -36.1084 | 0 | -0.086975 | 0 | -0.009155 | 0.09613 | 0.036621 | 0.10529 | -0.68664 | -0.50354 | -0.17853 | -0.37537 | -0.73242 | -0.63629 | -0.045776 | 0.050354 | 35.376 | -83.7891 | -83.7112 | 35.4721 | 35.4813 | 35.4126 | 0.10529 | 0.036621 | 0.31128 | 119.5862 | 0.09613 | -0.009155 | 119.2612 | -0.086975 | 118.5745 | 35.289 | -119.7647 | -83.7021 | 118.8995 | 35.3668 | 14.0945 | 35.376
2418.2812 | 119.458 | -2.7008 | 99.9619 | -0.009308 | 6.9767 | 0.060774 | 0.050616 | -0.0024224 | -0.0086773 | -0.0040758 | 0.0055543 | 0.005864 | 0.012469 | 0.0076498 | -0.011326 | 0.026171 | -0.0079916 | 0.95673 | 116.9586 | -3.1265 | 116.8579 | -2.7878 | -2.9572 | -2.9434 | -0.15564 | -0.17395 | -0.004578 | -0.091553 | -0.041199 | -0.16479 | -0.064087 | -0.42572 | 16.9968 | 16.8961 | -0.086975 | -0.24261 | -0.25635 | 0.18311 | 0.16937 | 2.6962 | -100.1358 | -100.0534 | 2.6596 | 2.6367 | 2.536 | -0.059509 | -0.16022 | 0.33875 | 119.9844 | -0.036621 | -0.086975 | 120.0851 | -0.16937 | 119.6594 | 2.5269 | -103.0884 | -99.9664 | 119.5587 | 2.6093 | 3.6575 | 2.5452
2419.9688 | 120.4971 | -51.0635 | 68.9621 | -0.0016785 | 6.9759 | 0.063551 | 0.059588 | -0.0071222 | -0.0071821 | -0.0032214 | 0.0055543 | 0.0018052 | 0.013537 | 0.014699 | -0.0074811 | 0.027025 | -0.00436 | -32.2449 | 68.9117 | -51.1093 | 69.0948 | -50.7431 | -51.2421 | -51.3153 | 0.054932 | -0.045776 | 0.14191 | 0.068665 | 0.14191 | 0.10529 | 0.16022 | -0.045776 | -0.050354 | 0.13275 | 0.32044 | -0.25177 | -0.17853 | -0.20599 | -0.13275 | 51.2054 | -69.0079 | -68.8934 | 51.2054 | 51.2238 | 51.1688 | 0.01831 | -0.036621 | 0.36621 | 120.2042 | 0 | -0.073242 | 120.0211 | -0.18768 | 119.9753 | 51.0178 | -120.0714 | -68.8202 | 120.1584 | 51.1322 | 18.8187 | 51.1185
2421.7031 | 119.8654 | -119.4031 | 0.24719 | -0.0016785 | 6.978 | 0.065473 | 0.059588 | -0.0051996 | -0.0069683 | -0.0070666 | 0.0025025 | -0.0033218 | 0.01311 | 0.0074362 | -0.020726 | 0.015276 | -0.018032 | -78.9825 | 0.091553 | -119.4397 | 0.022888 | -118.2449 | -119.1742 | -119.3436 | -0.17853 | -0.027466 | -0.082397 | -0.1236 | -0.18768 | -0.23804 | 0.064087 | -0.036621 | -0.15564 | -0.2243 | 1.1581 | 0.059509 | 0.22888 | 0.09613 | 0.2655 | 119.3207 | -0.27466 | -0.37079 | 119.2154 | 119.4672 | 119.165 | 0.14648 | -0.15564 | 1.1948 | 119.4626 | -0.10529 | -0.041199 | 119.5312 | 0.054931 | 119.4946 | 119.3756 | -119.6869 | -0.32959 | 119.426 | 119.2795 | 40.4205 | 119.2245
2423.3906 | 120.4102 | -119.8608 | 0.19226 | -0.0016785 | 6.9776 | 0.06761 | 0.06322 | 0.00078177 | -0.0078229 | 0.001051 | -0.0036011 | 0.0022324 | 0.012469 | 0.012136 | -0.0057721 | 0.029375 | -0.0017966 | -79.7699 | 0.059509 | -119.8563 | 0.13733 | -118.8675 | -119.8471 | -119.9524 | 0.082397 | -0.022888 | 0.25635 | 0.15106 | 0.15106 | 0.1236 | 0.18768 | 0.004578 | -0.13275 | -0.054932 | 0.99335 | -0.091553 | 0.013733 | -0.096131 | 0.009155 | 120.1172 | -0.21515 | -0.041199 | 120.0119 | 120.0485 | 119.9844 | -0.068665 | -0.13275 | 0.98877 | 119.9936 | -0.10529 | -0.10529 | 119.9158 | -0.27924 | 119.9203 | 119.838 | -120.0485 | 0.064087 | 119.9982 | 120.0119 | 40.0909 | 119.9432
2425.0781 | 120.4239 | -120.0027 | 0.20142 | 0.01358 | 6.9769 | 0.063551 | 0.061083 | 0.0029182 | -0.0065411 | -0.003435 | 0.0055543 | 0.0003098 | 0.015674 | 0.016836 | -0.0087629 | 0.029162 | -0.0028646 | -80.3421 | 0.064087 | -119.9799 | 0.086975 | -119.0002 | -119.9524 | -120.0668 | 0.009155 | -0.013733 | 0.032043 | 0.068665 | 0.091553 | 0.059509 | 0.1831 | 0.022889 | -0.13733 | -0.11444 | 1.0025 | -0.064086 | 0.050354 | -0.086975 | 0.027465 | 120.0348 | -0.21515 | -0.13275 | 120.0943 | 120.1859 | 120.0623 | 0.15106 | 0.027466 | 0.97961 | 120.0668 | 0.05951 | 0.036622 | 120.0439 | -0.045776 | 120.0668 | 119.989 | -120.1813 | -0.16937 | 120.0897 | 120.0714 | 39.6606 | 120.0119
2426.8125 | 120.5383 | -120.0394 | 0.18768 | -0.009308 | 6.9763 | 0.064192 | 0.060015 | -0.0034906 | -0.0054731 | -0.001726 | 0.0025025 | 0.0015914 | 0.012469 | 0.008077 | -0.0096173 | 0.027666 | -0.00051479 | -80.9967 | 0.036621 | -120.0119 | 0.091553 | -119.0231 | -119.9707 | -120.0714 | 0.036621 | 0.009155 | 0.032043 | 0.10986 | 0.15106 | 0.11902 | 0.18768 | 0.027466 | -0.15106 | -0.09613 | 1.0162 | -0.032043 | 0.068665 | -0.059509 | 0.041199 | 120.0714 | -0.17853 | -0.07782 | 120.1904 | 120.2271 | 120.1584 | 0.15564 | 0.086976 | 0.98877 | 120.1035 | 0.11902 | 0.07782 | 120.0485 | -0.022888 | 120.076 | 120.0485 | -120.1996 | -0.15564 | 120.1309 | 120.1492 | 39.0427 | 120.076
2428.5625 | 119.989 | -119.4534 | 0.27008 | 0.005951 | 6.9739 | 0.06761 | 0.059802 | 0.0020636 | -0.0106 | 0.00062377 | 0.0025025 | 0.0003098 | 0.012042 | 0.015554 | -0.0083355 | 0.025744 | 0.00033961 | -81.2027 | 0.10529 | -119.4214 | 0.21973 | -118.3685 | -119.3298 | -119.4717 | 0.091553 | 0.009155 | 0.045776 | 0.12817 | 0.17395 | 0.13275 | 0.18768 | 0.032043 | -0.1648 | -0.050354 | 1.0849 | -0.018311 | 0.1236 | -0.050354 | 0.091553 | 119.4992 | -0.26093 | -0.14191 | 119.6274 | 119.6411 | 119.5862 | 0.14191 | 0.086975 | 1.0529 | 119.6411 | 0.12817 | 0.082398 | 119.5267 | -0.036621 | 119.5587 | 119.4626 | -119.6915 | -0.22431 | 119.6732 | 119.5816 | 38.2507 | 119.545
2430.25 | 120.3827 | -119.9524 | 0.20142 | -0.0016785 | 6.9761 | 0.063978 | 0.062579 | -7.2628e-05 | -0.0091047 | -0.0012988 | 0.0025025 | 0.0005234 | 0.011188 | 0.0085044 | -0.0081219 | 0.027666 | -0.0037192 | -82.132 | 0.050354 | -119.9158 | 0.082397 | -118.9362 | -119.9249 | -120.0256 | -0.004578 | -0.004578 | 0.036621 | 0.082397 | 0.10529 | 0.064087 | 0.16937 | 0.036622 | -0.15106 | -0.11902 | 1.0162 | -0.073242 | 0.027466 | -0.10986 | -0.009156 | 119.989 | -0.20599 | -0.11902 | 120.0577 | 120.1218 | 120.0165 | 0.13275 | 0.027466 | 0.97961 | 119.9982 | 0.068665 | 0.045776 | 119.9661 | -0.041199 | 120.0027 | 119.9478 | -120.1172 | -0.1648 | 120.0348 | 120.0348 | 37.8204 | 119.9478
2431.9219 | 120.4056 | -120.0668 | 0.2243 | 0.005951 | 6.9771 | 0.064405 | 0.06621 | -0.00092703 | -0.0080365 | -0.0015124 | 0.0055543 | -0.007167 | 0.01076 | 0.0076498 | -0.014531 | 0.020189 | -0.003292 | -82.7179 | 0.073242 | -120.0073 | 0.07782 | -118.8629 | -119.7372 | -119.8151 | 0.027466 | 0.032043 | 0.032043 | 0.064087 | 0.10529 | -0.013733 | -0.20599 | 0.059509 | -0.15106 | -0.14648 | 1.2039 | 0.25177 | 0.32959 | 0.19226 | 0.27008 | 120.0989 | -0.19226 | -0.16022 | 120.1721 | 119.8608 | 120.0531 | -0.23804 | -0.045776 | 1.1444 | 120.0851 | 0.073243 | 0.032044 | 120.0806 | 0 | 120.1401 | 120.0989 | -120.2316 | -0.19226 | 120.1447 | 120.1309 | 37.3489 | 120.0943
2433.6562 | 116.0477 | -87.4512 | 29.2419 | 0.11276 | 6.9742 | 0.064619 | 0.062579 | -0.0056268 | -0.0106 | -0.0053576 | -0.043274 | -0.01144 | 0.01311 | 0.0089316 | -0.020299 | 0.012285 | -0.014187 | -59.5688 | 30.4459 | -86.3388 | 29.9515 | -85.8078 | -86.6684 | -87.1857 | -0.086975 | 0.013733 | -0.009155 | -0.004578 | -0.013733 | -0.16022 | -0.23346 | 1.1124 | 1.2039 | 0.70953 | 1.6434 | 0.2655 | 0.78278 | -0.84686 | -0.32959 | 87.442 | -29.2282 | -29.2465 | 87.4374 | 87.2177 | 87.291 | -0.2243 | -0.15106 | 0.53101 | 116.2903 | -0.004578 | 0.004577 | 116.7847 | 0.022888 | 117.897 | 87.4649 | -115.5807 | -29.2511 | 117.4026 | 87.4466 | 27.8824 | 87.3642
2435.4062 | 120.3552 | -119.8654 | 0.20142 | -0.0016785 | 6.9774 | 0.065687 | 0.065356 | 0.0029182 | -0.0061139 | -0.00023063 | 0.0025025 | 0.0033004 | 0.014392 | 0.0089316 | -0.0051313 | 0.028948 | -0.0035056 | -83.9676 | 0.045776 | -119.87 | 0.041199 | -118.8538 | -119.7556 | -119.7647 | 0.004578 | 0.009155 | 0.041199 | 0.10071 | 0.09613 | 0.045776 | 0.07782 | -0.004578 | -0.15564 | -0.16022 | 1.0117 | 0.10071 | 0.10986 | 0.10529 | 0.11444 | 119.9066 | -0.19226 | -0.10071 | 119.9615 | 119.9432 | 119.9112 | 0.036621 | 0.004577 | 1.0162 | 119.9112 | 0.054931 | 0.059509 | 119.9158 | -0.032044 | 119.9112 | 119.8746 | -120.0714 | -0.16022 | 119.9066 | 119.9661 | 35.8978 | 119.87
2437.1562 | 120.4651 | -119.9844 | 0.21057 | -0.0016785 | 6.9778 | 0.06526 | 0.064074 | 0.005268 | -0.0080365 | -0.0015124 | 0.0025025 | 0.0018052 | 0.013965 | 0.014272 | -0.0042767 | 0.029162 | -0.002651 | -84.6359 | 0.068665 | -119.989 | 0.073242 | -118.9224 | -119.9112 | -119.9112 | 0.073242 | 0.018311 | 0.054932 | 0.1236 | 0.14648 | 0.09613 | 0.19684 | -0.004578 | -0.14191 | -0.13733 | 1.062 | 0.073242 | 0.073242 | 0.07782 | 0.07782 | 120.0394 | -0.19226 | -0.086975 | 120.1309 | 120.1813 | 120.0806 | 0.14191 | 0.041198 | 1.0666 | 120.0623 | 0.091552 | 0.068664 | 120.0577 | -0.036621 | 120.0531 | 120.0027 | -120.1996 | -0.15564 | 120.0577 | 120.108 | 35.3485 | 120.0577
2438.8438 | 119.8837 | -119.4992 | 0.11444 | 0.005951 | 6.9752 | 0.066755 | 0.058947 | -7.2628e-05 | -0.0071821 | -0.002367 | -0.20807 | -0.0052444 | 0.012042 | 0.0074362 | -0.014317 | 0.026171 | -0.006069 | -84.4666 | 0.027466 | -114.0701 | -0.31586 | -105.9448 | -111.0855 | -111.1862 | -0.43945 | 0.082397 | -0.082397 | -0.09613 | 0.07782 | 0.082397 | 0.086975 | 5.4291 | -0.086975 | -0.4303 | 13.5544 | 8.313 | 8.4137 | 2.8839 | 2.9846 | 119.4168 | -0.032044 | -0.21057 | 119.577 | 119.5862 | 119.5816 | 0.16937 | 0.16479 | 8.1253 | 113.7543 | 0.16022 | -0.013733 | 114.0976 | 0.16479 | 119.5267 | 119.5816 | -114.1846 | -0.19684 | 119.1834 | 119.4031 | 35.0327 | 119.0598
2440.6094 | 119.902 | -119.4305 | 0.18768 | 0.005951 | 6.9776 | 0.060346 | 0.05382 | 0.011463 | -0.026835 | 0.052748 | -0.23859 | 0.030217 | 0.0041379 | 0.0072226 | 0.03503 | 0.045183 | 0.031529 | -81.9077 | 0.045776 | -118.9545 | 0 | -88.2477 | -92.6788 | -92.9764 | -0.16479 | 0.086975 | -0.082397 | 0.082397 | 0.086975 | 0.086975 | 0.082397 | 0.47607 | -0.14191 | -0.18768 | 31.1829 | 26.4542 | 26.7517 | 25.9781 | 26.2756 | 119.3481 | -0.10071 | -0.10529 | 119.5175 | 119.5129 | 119.5175 | 0.16479 | 0.16937 | 30.7068 | 118.9545 | 0.16937 | 0.16479 | 119.0002 | 0.16937 | 119.4763 | 119.5175 | -119.1422 | -0.27008 | 119.4305 | 119.5129 | 37.5229 | 119.2657
2442.3594 | 120.2133 | -119.7876 | 0.22888 | 0.005951 | 6.9761 | 0.065046 | 0.05852 | -0.0079766 | -0.0071821 | -0.0059984 | -0.19586 | -0.010371 | 0.013537 | 0.0076498 | -0.024144 | 0.01314 | -0.019741 | -86.2976 | 0.082397 | -119.4305 | -0.23804 | -101.8753 | -105.9036 | -105.2216 | -0.14648 | -0.35706 | 0.091553 | -0.13733 | 0.091553 | 0.073242 | 0.07782 | 0.35706 | -0.14649 | -0.46692 | 17.9123 | 14.566 | 13.884 | 14.209 | 13.5269 | 119.8792 | -0.58594 | -0.36621 | 119.8792 | 119.8654 | 119.8608 | -0.013733 | -0.018311 | 17.5552 | 119.1925 | 0 | -0.22888 | 119.5129 | -0.44861 | 119.87 | 119.4305 | -119.6594 | -0.13733 | 119.5496 | 119.6503 | 33.49 | 119.6411
2444.0312 | 120.2499 | -119.9295 | 0.2243 | -0.0016785 | 6.9784 | 0.064832 | 0.062365 | -0.0019952 | -0.0061139 | -0.0032214 | -0.11957 | -0.0018264 | 0.015246 | 0.0089316 | -0.0044903 | 0.028094 | -0.0035056 | -87.0575 | 0.054932 | -119.902 | -0.16022 | -107.8949 | -113.6078 | -110.8932 | -0.064087 | -0.07782 | 0.3067 | -0.004578 | -0.26093 | -0.28839 | 0.045776 | 0.027465 | -0.16937 | -0.38452 | 12.0346 | 9.0363 | 6.3217 | 9.0088 | 6.2943 | 120.2362 | -0.30212 | -0.22888 | 119.6686 | 119.9753 | 119.6411 | -0.26093 | -0.59509 | 12.0071 | 119.7418 | -0.56763 | -0.31128 | 119.957 | -0.38452 | 119.9844 | 119.8517 | -120.1263 | 0.082398 | 119.7693 | 119.9249 | 32.872 | 119.8654
2445.7812 | 120.4285 | -119.9707 | 0.20599 | 0.005951 | 6.9759 | 0.066114 | 0.058093 | -0.0039178 | -0.0088911 | -0.00065803 | 0.0055543 | 0.0028732 | 0.012469 | 0.013845 | -0.010472 | 0.028094 | 0.00012601 | -87.6617 | 0.027466 | -119.957 | 0.1236 | -118.3914 | -119.5862 | -119.6823 | 0.091553 | -0.013733 | 0.091553 | 0.10986 | 0.19684 | 0.086975 | 0.10986 | 0.013733 | -0.17853 | -0.082398 | 1.5793 | 0.28839 | 0.38452 | 0.27466 | 0.37079 | 120.0623 | -0.21973 | -0.096131 | 120.1675 | 120.0806 | 120.0577 | 0.01831 | -0.004578 | 1.5656 | 120.0806 | 0.10529 | 0.01831 | 119.9844 | -0.10529 | 119.9982 | 119.957 | -120.163 | -0.11444 | 120.0943 | 120.0806 | 32.309 | 120.0623
2447.5312 | 120.369 | -120.0531 | 0.2243 | -0.016937 | 6.9782 | 0.065901 | 0.062365 | 0.00056817 | -0.0067547 | -0.0015124 | -0.0066527 | 0.0020188 | 0.012256 | 0.0089316 | -0.0096173 | 0.028521 | -0.0041464 | -87.8357 | 0.027466 | -119.9936 | 0.10071 | -118.4052 | -119.5816 | -119.6548 | 0.022888 | 0.022888 | 0.036621 | 0.022888 | 0.091553 | -0.073242 | -0.068665 | 0.05951 | -0.19684 | -0.1236 | 1.6479 | 0.39825 | 0.4715 | 0.33874 | 0.41199 | 120.0897 | -0.20142 | -0.20142 | 120.1447 | 119.9844 | 119.9799 | -0.10529 | -0.10986 | 1.5884 | 120.0943 | 0.054932 | -0.013733 | 120.0211 | -0.013733 | 120.0806 | 120.076 | -120.2179 | -0.18768 | 120.1538 | 120.076 | 32.2174 | 120.076
2449.2188 | 120.3873 | -120.0943 | 0.2243 | -0.009308 | 6.978 | 0.065687 | 0.061938 | 0.00056817 | -0.0059003 | -1.7026e-05 | -0.0036011 | 0.0045822 | 0.013324 | 0.013845 | -0.0070539 | 0.027666 | -0.0020102 | -88.0737 | 0.064087 | -120.0531 | 0 | -118.5516 | -119.9387 | -120.5933 | -0.068665 | 0.036621 | 0.018311 | 0.032043 | 0.032043 | -0.1831 | -0.18768 | 0.041198 | -0.16022 | -0.2243 | 1.5427 | -0.49896 | 0.15564 | -0.54016 | 0.11444 | 120.1126 | -0.18768 | -0.19226 | 120.1263 | 119.9066 | 119.9112 | -0.20599 | -0.20142 | 1.5015 | 120.0531 | 0.013732 | 0.013732 | 120.1172 | 0.01831 | 120.1584 | 120.1309 | -120.2774 | -0.20599 | 120.0943 | 120.1263 | 32.0206 | 120.0256
2450.9062 | 120.3964 | -120.1492 | 0.23804 | -0.009308 | 6.9797 | 0.06761 | 0.06322 | 0.0027044 | -0.0073957 | -0.0019396 | -0.040222 | -0.0018264 | 0.012256 | 0.013418 | -0.0057721 | 0.028521 | -0.0028646 | -88.0005 | 0.073242 | -120.1172 | 0 | -118.7439 | -120.3827 | -115.7089 | -0.073242 | 0.041199 | 0.018311 | -0.009155 | 0.004578 | -0.21057 | -0.26093 | 0.032044 | -0.16479 | -0.23804 | 1.4053 | 4.4403 | -0.23346 | 4.4083 | -0.2655 | 120.1675 | -0.19684 | -0.24719 | 120.1538 | 119.8883 | 119.9387 | -0.27924 | -0.22888 | 1.3733 | 120.1172 | -0.013733 | -0.027466 | 120.1904 | 0.022888 | 120.2225 | 120.1904 | -120.3552 | -0.21973 | 120.1492 | 120.1401 | 32.1487 | 120.076
2452.6562 | 120.1355 | -120.1447 | 0.23804 | 0.01358 | 6.9782 | 0.064619 | 0.064288 | -0.00071343 | -0.0067547 | -0.0012988 | -0.10431 | -0.006099 | 0.015033 | 0.015981 | -0.011967 | 0.019121 | -0.0088462 | -87.854 | 0.086975 | -120.0806 | 0.11902 | -118.8629 | -116.3177 | -110.1059 | 0.018311 | 0.027466 | 0.032043 | 0.07782 | 0.10529 | -0.20142 | 0.086975 | 0.064087 | -0.15106 | -0.11902 | 1.2817 | 10.0388 | 3.8269 | 9.9747 | 3.7628 | 120.1767 | -0.21057 | -0.16022 | 120.2499 | 120.2316 | 119.9432 | 0.054932 | -0.23346 | 1.2177 | 120.1996 | 0.073243 | 0.045777 | 120.1675 | -0.004577 | 120.2316 | 120.1721 | -120.3186 | -0.20599 | 120.2637 | 120.2225 | 32.2906 | 120.163
2454.4062 | 120.3598 | -120.1401 | 0.28381 | -0.0016785 | 6.9765 | 0.063978 | 0.060656 | -0.0041314 | -0.0080365 | 0.00083737 | -0.00054933 | 0.0013778 | 0.014178 | 0.011922 | -0.011113 | 0.028521 | -0.0045736 | -88.0554 | 0.10071 | -120.1401 | 0.036621 | -118.5013 | -119.751 | -119.7876 | -0.059509 | 0.032043 | 0.009155 | -0.009155 | 0.041199 | 0 | -0.068665 | 0 | -0.1831 | -0.24719 | 1.6388 | 0.35248 | 0.3891 | 0.35248 | 0.3891 | 120.1492 | -0.25177 | -0.29297 | 120.1813 | 120.0714 | 120.1401 | -0.07782 | -0.009155 | 1.6388 | 120.1767 | 0.032044 | -0.01831 | 120.2408 | 0.022888 | 120.2408 | 120.1721 | -120.4239 | -0.27466 | 120.1767 | 120.1309 | 32.0847 | 120.0806
2456.0938 | 120.607 | -120.1126 | 0.24719 | -0.0016785 | 6.978 | 0.065901 | 0.058734 | 0.0022772 | -0.0091047 | -0.003435 | -0.00054933 | -0.0007584 | 0.01311 | 0.011495 | -0.0094037 | 0.026598 | -0.00072839 | -88.0692 | 0.07782 | -120.1126 | 0.19684 | -118.5516 | -119.9249 | -119.9524 | 0.10071 | -0.004578 | 0.045776 | 0.10529 | 0.19684 | 0.14191 | 0.20599 | 0 | -0.16937 | -0.050354 | 1.561 | 0.16022 | 0.18768 | 0.16022 | 0.18768 | 120.1584 | -0.25177 | -0.14191 | 120.3094 | 120.3186 | 120.2545 | 0.16022 | 0.096131 | 1.561 | 120.3094 | 0.15106 | 0.05951 | 120.1904 | -0.050354 | 120.1904 | 120.108 | -120.3598 | -0.20142 | 120.3094 | 120.2179 | 32.0435 | 120.2133
2457.8281 | 120.1996 | -120.076 | 0.28839 | -0.0016785 | 6.9769 | 0.066541 | 0.062579 | 0.0044134 | -0.0095319 | -0.0053576 | 0.0055543 | 0.0015914 | 0.013324 | 0.011922 | -0.0066265 | 0.026171 | -0.0030784 | -88.7558 | 0.1236 | -120.1675 | 0.068665 | -118.3731 | -119.6594 | -120.1126 | -0.032043 | 0.018311 | 0.022888 | 0.027466 | 0.091553 | -0.004578 | -0.10529 | -0.091553 | -0.1648 | -0.21973 | 1.7029 | -0.036621 | 0.41657 | 0.054932 | 0.50812 | 120.0989 | -0.27008 | -0.26093 | 120.1675 | 119.9707 | 120.0714 | -0.12817 | -0.027466 | 1.7944 | 120.2362 | 0.068665 | 0.004578 | 120.2911 | -0.004577 | 120.1996 | 120.0943 | -120.4559 | -0.2655 | 120.1447 | 120.1035 | 31.3202 | 120.0439
2459.5156 | 120.6345 | -120.1584 | 0.27466 | -0.016937 | 6.9771 | 0.066328 | 0.063006 | 0.0014228 | -0.0088911 | -0.0025806 | -0.00054933 | 0.0026596 | 0.014392 | 0.0044454 | -0.0064129 | 0.030657 | -0.0017966 | -89.0945 | 0.091553 | -120.1813 | 0.10986 | -118.5196 | -119.9295 | -119.9249 | 0.045776 | 0.022888 | 0.032043 | 0.10071 | 0.12817 | 0.073242 | 0.20599 | -0.022888 | -0.18311 | -0.1648 | 1.6388 | 0.23346 | 0.22888 | 0.25635 | 0.25177 | 120.1904 | -0.25177 | -0.17395 | 120.2866 | 120.3644 | 120.2316 | 0.17395 | 0.041199 | 1.6617 | 120.2911 | 0.096131 | 0.068665 | 120.2728 | -0.009155 | 120.2499 | 120.1813 | -120.4559 | -0.24262 | 120.2682 | 120.2591 | 31.0638 | 120.2042
2461.2656 | 120.1172 | -119.9203 | 0.2655 | 0.005951 | 6.9778 | 0.065687 | 0.061724 | -0.0034906 | -0.0078229 | -0.0030078 | 0.0055543 | 0.0020188 | 0.014605 | 0.0067954 | -0.0059857 | 0.026171 | -0.0022238 | -89.2502 | 0.10529 | -120.2316 | 0.13275 | -118.2632 | -119.6915 | -120.4193 | 0.013733 | 0.041199 | 0.036621 | 0.032043 | 0.091553 | 0.009155 | -0.064087 | -0.31128 | -0.16022 | -0.13275 | 1.6571 | -0.49896 | 0.22888 | -0.18768 | 0.54016 | 119.957 | -0.2243 | -0.23346 | 120.0119 | 119.8563 | 119.9295 | -0.10071 | -0.027466 | 1.9684 | 120.3644 | 0.054932 | -0.004578 | 120.3369 | 0.004578 | 120.0256 | 119.9615 | -120.4971 | -0.22888 | 120.0531 | 119.9524 | 30.6702 | 119.9341
2462.9375 | 120.6619 | -120.2408 | 0.25635 | -0.0016785 | 6.9806 | 0.065901 | 0.060442 | 0.00014097 | -0.0080365 | -0.0047168 | 0.0055543 | 0.0018052 | 0.012469 | 0.011068 | -0.0085491 | 0.027239 | -0.005001 | -89.2914 | 0.054932 | -120.1904 | 0.19684 | -118.4052 | -120.1218 | -120.2225 | 0.082397 | 0 | 0.064087 | 0.07782 | 0.14191 | 0.07782 | 0.1831 | 0.050354 | -0.20142 | -0.05951 | 1.8356 | 0.018311 | 0.11902 | -0.032043 | 0.068665 | 120.3049 | -0.25635 | -0.17853 | 120.3827 | 120.4239 | 120.3186 | 0.11902 | 0.013733 | 1.7853 | 120.3873 | 0.07782 | 0.013733 | 120.2454 | -0.064087 | 120.2957 | 120.2408 | -120.4468 | -0.19226 | 120.4376 | 120.3186 | 30.9494 | 120.3232
2464.6875 | 120.7535 | -120.2362 | 0.25177 | -0.009308 | 6.9756 | 0.065046 | 0.059161 | -0.002636 | -0.0082501 | -0.0012988 | 0.0025025 | 0.0015914 | 0.011615 | 0.011068 | -0.0094037 | 0.029162 | -0.0039328 | -89.2319 | 0.064087 | -120.2591 | 0.17395 | -118.2907 | -120.0394 | -120.1996 | 0.11444 | -0.013733 | 0.059509 | 0.09613 | 0.19684 | 0.14191 | 0.19226 | -0.022888 | -0.18768 | -0.07782 | 1.9455 | 0.036621 | 0.19684 | 0.059509 | 0.21973 | 120.2957 | -0.2655 | -0.15564 | 120.433 | 120.4285 | 120.3781 | 0.13275 | 0.082398 | 1.9684 | 120.433 | 0.13733 | 0.036621 | 120.3232 | -0.073242 | 120.3003 | 120.2225 | -120.5109 | -0.19226 | 120.4102 | 120.3323 | 31.0043 | 120.3506
2466.4375 | 120.6024 | -120.2591 | 0.28839 | 0.005951 | 6.9786 | 0.065901 | 0.062579 | -0.00071343 | -0.0086773 | -0.00044443 | -0.00054933 | 0.003514 | 0.013537 | 0.009786 | -0.0066265 | 0.028734 | -0.0030784 | -88.9847 | 0.10071 | -120.2911 | 0.045776 | -118.4189 | -120.0989 | -120.0531 | -0.059509 | 0.036621 | 0.013733 | -0.004578 | 0.036621 | -0.027466 | 0.082397 | -0.032044 | -0.18768 | -0.24262 | 1.8402 | 0.20599 | 0.16022 | 0.23804 | 0.19226 | 120.2728 | -0.25177 | -0.29297 | 120.2957 | 120.3415 | 120.2316 | 0.068664 | -0.041199 | 1.8723 | 120.3369 | 0.022888 | -0.018311 | 120.3918 | 0.022888 | 120.3598 | 120.2957 | -120.5795 | -0.27466 | 120.3049 | 120.2545 | 31.2744 | 120.1996
2468.1094 | 120.7855 | -120.2499 | 0.26093 | -0.009308 | 6.9776 | 0.065901 | 0.06087 | -0.00071343 | -0.0084637 | -0.0030078 | -0.00054933 | 0.0003098 | 0.012469 | 0.017263 | -0.0091901 | 0.028307 | -0.002651 | -88.6505 | 0.073242 | -120.2774 | 0.20142 | -118.1717 | -120.0989 | -120.2454 | 0.1236 | -0.004578 | 0.036621 | 0.11444 | 0.21057 | 0.15106 | 0.23346 | -0.027466 | -0.18768 | -0.059509 | 2.0782 | 0.004578 | 0.15106 | 0.032044 | 0.17853 | 120.2866 | -0.2655 | -0.14648 | 120.4605 | 120.4834 | 120.401 | 0.19684 | 0.11444 | 2.1057 | 120.4788 | 0.17395 | 0.07782 | 120.3506 | -0.041199 | 120.3232 | 120.2454 | -120.5383 | -0.2243 | 120.4514 | 120.3644 | 31.5994 | 120.3735
2469.8594 | 120.639 | -120.2637 | 0.27466 | 0.005951 | 6.9791 | 0.067182 | 0.063647 | 0.00099557 | -0.0071821 | -0.0010852 | -0.00054933 | 0.0043686 | 0.016314 | 0.0085044 | -0.0085491 | 0.028948 | -0.002651 | -88.5269 | 0.09613 | -120.3278 | 0.073242 | -118.2953 | -120.1584 | -120.1218 | -0.10986 | 0.045776 | 0.009155 | -0.004578 | 0.027466 | -0.032043 | 0.10986 | -0.064087 | -0.17853 | -0.20142 | 1.9684 | 0.14191 | 0.10529 | 0.20599 | 0.16937 | 120.2728 | -0.22888 | -0.27924 | 120.2911 | 120.3735 | 120.2316 | 0.10071 | -0.041198 | 2.0325 | 120.401 | 0.018311 | -0.013733 | 120.4239 | 0.036621 | 120.3598 | 120.3094 | -120.6024 | -0.2655 | 120.3369 | 120.2591 | 31.7368 | 120.1538
2471.5312 | 120.7077 | -120.3461 | 0.29755 | -0.0016785 | 6.9778 | 0.066328 | 0.061938 | -0.0017816 | -0.0086773 | -0.00044443 | -0.00054933 | 0.0028732 | 0.013537 | 0.016408 | -0.011326 | 0.028094 | -0.0058554 | -88.4949 | 0.07782 | -120.3278 | 0.16022 | -118.0984 | -120.1538 | -120.3186 | 0.022888 | 0.027466 | 0.022888 | -0.004578 | 0.091553 | 0.041199 | 0.11902 | 0.01831 | -0.21973 | -0.13733 | 2.2476 | 0.027465 | 0.19226 | 0.009155 | 0.17395 | 120.369 | -0.27008 | -0.30212 | 120.4376 | 120.4651 | 120.3873 | 0.096131 | 0.018311 | 2.2293 | 120.488 | 0.068665 | -0.027466 | 120.4056 | 0.004578 | 120.4239 | 120.3735 | -120.6253 | -0.27466 | 120.5063 | 120.3415 | 31.8512 | 120.369
2473.2812 | 120.694 | -120.2454 | 0.28381 | -0.0016785 | 6.9765 | 0.068037 | 0.062151 | 0.00035457 | -0.0080365 | -0.0038622 | -0.00054933 | 0.005864 | 0.016314 | 0.0089316 | -0.0081219 | 0.026598 | -0.00030119 | -88.1149 | 0.10529 | -120.3598 | 0.11902 | -118.0847 | -120.1904 | -120.1263 | -0.018311 | 0.036621 | 0.027466 | 0 | 0.068665 | -0.009155 | 0.10986 | -0.11444 | -0.17853 | -0.16479 | 2.1606 | 0.11902 | 0.054931 | 0.23346 | 0.16937 | 120.2728 | -0.24719 | -0.28381 | 120.314 | 120.3552 | 120.2362 | 0.082397 | -0.036621 | 2.2751 | 120.4788 | 0.041199 | -0.027466 | 120.4651 | 0.009155 | 120.3506 | 120.282 | -120.6436 | -0.25635 | 120.3644 | 120.2454 | 32.1304 | 120.2271
2474.9688 | 120.8405 | -120.3323 | 0.27466 | -0.009308 | 6.9767 | 0.067823 | 0.063433 | 0.006977 | -0.0037641 | -0.0027942 | -0.0036011 | 0.0020188 | 0.013537 | 0.015127 | -0.0044903 | 0.030443 | -0.0052146 | -87.6572 | 0.073242 | -120.3506 | 0.19684 | -117.9474 | -120.1859 | -120.314 | 0.086975 | 0 | 0.045776 | 0.11902 | 0.16937 | 0.11444 | 0.21515 | -0.018311 | -0.20142 | -0.07782 | 2.3849 | 0.01831 | 0.14648 | 0.036621 | 0.16479 | 120.3781 | -0.27466 | -0.15564 | 120.5017 | 120.5475 | 120.4468 | 0.16937 | 0.068665 | 2.4033 | 120.5475 | 0.1236 | 0.073243 | 120.4239 | -0.045776 | 120.4056 | 120.3323 | -120.6253 | -0.22888 | 120.5292 | 120.4514 | 32.6752 | 120.4193
2476.7188 | 120.845 | -120.3415 | 0.27008 | -0.0016785 | 6.9765 | 0.066541 | 0.05852 | -0.0024224 | -0.0069683 | -0.0012988 | -0.00054933 | 0.0003098 | 0.011828 | 0.0089316 | -0.0083355 | 0.027025 | -0.0037192 | -86.879 | 0.082397 | -120.369 | 0.2243 | -117.8192 | -120.1218 | -120.2957 | 0.10071 | 0.004578 | 0.054932 | 0.086975 | 0.18768 | 0.12817 | 0.19684 | -0.027466 | -0.18768 | -0.045777 | 2.5223 | 0.045777 | 0.21973 | 0.073243 | 0.24719 | 120.3964 | -0.2655 | -0.18311 | 120.5292 | 120.5383 | 120.4697 | 0.14191 | 0.073242 | 2.5497 | 120.5933 | 0.13275 | 0.032043 | 120.4514 | -0.050354 | 120.4239 | 120.3461 | -120.639 | -0.21515 | 120.5658 | 120.4285 | 33.4625 | 120.4422
2478.4531 | 120.8679 | -120.3598 | 0.27466 | -0.009308 | 6.9771 | 0.06526 | 0.060442 | -0.0011408 | -0.0073957 | -0.0036486 | 0.0025025 | 0.0013778 | 0.012042 | 0.013204 | -0.0096173 | 0.028948 | -0.0064962 | -86.3525 | 0.07782 | -120.3964 | 0.23346 | -117.7094 | -120.1355 | -120.2866 | 0.10071 | 0 | 0.068665 | 0.10071 | 0.19226 | 0.11902 | 0.18768 | -0.036621 | -0.19684 | -0.041199 | 2.6505 | 0.073242 | 0.2243 | 0.10986 | 0.26093 | 120.4285 | -0.27466 | -0.17395 | 120.5521 | 120.5475 | 120.4788 | 0.11902 | 0.050354 | 2.6871 | 120.6299 | 0.1236 | 0.032043 | 120.4742 | -0.068665 | 120.4376 | 120.3598 | -120.6711 | -0.20599 | 120.5933 | 120.4605 | 34.0073 | 120.4605
2480.125 | 120.8359 | -120.3918 | 0.29755 | 0.005951 | 6.9767 | 0.067182 | 0.062792 | 0.0012092 | -0.0067547 | -0.0025806 | 0.0055543 | 0.0033004 | 0.014605 | 0.012777 | -0.010045 | 0.029375 | -0.003292 | -85.8444 | 0.11902 | -120.4147 | 0.15564 | -117.7368 | -120.2271 | -120.3415 | 0.036621 | 0.027466 | 0.032043 | 0.041199 | 0.11444 | 0.041199 | 0.15106 | -0.022888 | -0.17853 | -0.14191 | 2.655 | 0.050354 | 0.16479 | 0.073242 | 0.18768 | 120.4239 | -0.27008 | -0.25635 | 120.5063 | 120.5429 | 120.433 | 0.11902 | 0.009156 | 2.6779 | 120.5704 | 0.082398 | 0.009156 | 120.5338 | -0.004577 | 120.5109 | 120.4193 | -120.7123 | -0.2655 | 120.5475 | 120.433 | 34.5474 | 120.4285
2481.875 | 120.9091 | -120.3827 | 0.28839 | -0.009308 | 6.9763 | 0.066541 | 0.063006 | 0.0012092 | -0.0039777 | -1.7026e-05 | 0.0055543 | 0.0022324 | 0.014605 | 0.008077 | -0.0059857 | 0.029803 | -0.0035056 | -85.2997 | 0.10986 | -120.4193 | 0.19684 | -117.6453 | -120.2087 | -120.3552 | 0.068665 | 0.004578 | 0.050354 | 0.12817 | 0.16022 | 0.091553 | 0.21515 | -0.036622 | -0.17853 | -0.091553 | 2.7374 | 0.027465 | 0.17395 | 0.064087 | 0.21057 | 120.433 | -0.28381 | -0.16022 | 120.5429 | 120.5978 | 120.4742 | 0.16479 | 0.041199 | 2.774 | 120.6162 | 0.10986 | 0.07782 | 120.5292 | -0.045776 | 120.4926 | 120.3873 | -120.7077 | -0.23804 | 120.5795 | 120.5109 | 35.083 | 120.4514
2483.5469 | 120.9366 | -120.4102 | 0.28839 | 0.005951 | 6.9765 | 0.066969 | 0.06087 | -0.0013544 | -0.0071821 | -0.001726 | -0.00054933 | 0.002446 | 0.013537 | 0.012563 | -0.0091901 | 0.029162 | 0.0022622 | -84.7183 | 0.10986 | -120.4193 | 0.19226 | -117.5812 | -120.1721 | -120.3461 | 0.068665 | 0.004578 | 0.045776 | 0.086975 | 0.17395 | 0.12817 | 0.20599 | -0.009156 | -0.17853 | -0.09613 | 2.829 | 0.064087 | 0.23804 | 0.073243 | 0.24719 | 120.4559 | -0.28381 | -0.20142 | 120.5841 | 120.6162 | 120.5383 | 0.16022 | 0.082398 | 2.8381 | 120.6116 | 0.12817 | 0.041199 | 120.5292 | -0.041198 | 120.52 | 120.4147 | -120.7077 | -0.24262 | 120.6024 | 120.4971 | 35.6918 | 120.4788
2485.2812 | 120.9137 | -120.4376 | 0.28381 | -0.0016785 | 6.9763 | 0.067182 | 0.062579 | 0.0033454 | -0.0067547 | -0.00087163 | -0.00054933 | 0.0013778 | 0.013537 | 0.012136 | -0.010045 | 0.028521 | -0.0024374 | -84.2377 | 0.091553 | -120.4468 | 0.16937 | -117.54 | -120.2225 | -120.3781 | 0.009155 | 0.004578 | 0.032043 | 0.041199 | 0.12817 | 0.07782 | 0.15564 | -0.009155 | -0.19226 | -0.11444 | 2.8976 | 0.059509 | 0.21515 | 0.068664 | 0.2243 | 120.4697 | -0.27923 | -0.24261 | 120.5658 | 120.5933 | 120.5154 | 0.1236 | 0.045777 | 2.9068 | 120.6161 | 0.096131 | 0.009156 | 120.5383 | -0.027465 | 120.5292 | 120.4422 | -120.7306 | -0.25177 | 120.607 | 120.4788 | 36.2 | 120.4468
2487.0312 | 120.8633 | -120.4926 | 0.31128 | -0.0016785 | 6.978 | 0.065687 | 0.062365 | 0.00056817 | -0.0052595 | -0.00065803 | -0.00054933 | 0.0026596 | 0.013751 | 0.0057272 | -0.0059857 | 0.02553 | -0.0013694 | -83.7296 | 0.13275 | -120.4697 | 0.10986 | -117.6086 | -120.3094 | -120.4422 | -0.027466 | 0.032043 | 0.027466 | 0.013733 | 0.059509 | 0.004578 | 0.12817 | 0.022888 | -0.17853 | -0.20142 | 2.8839 | 0.050354 | 0.18311 | 0.027466 | 0.16022 | 120.52 | -0.27924 | -0.29755 | 120.5521 | 120.6207 | 120.4971 | 0.10071 | -0.022888 | 2.861 | 120.5795 | 0.032043 | -0.013733 | 120.6024 | 0.004577 | 120.6253 | 120.5246 | -120.7809 | -0.28381 | 120.6024 | 120.5063 | 36.763 | 120.4651
2488.7812 | 121.0098 | -120.4605 | 0.28839 | 0.005951 | 6.9765 | 0.065473 | 0.061511 | -0.001568 | -0.0078229 | -0.0019396 | -0.00054933 | 0.0011642 | 0.012256 | 0.015554 | -0.010899 | 0.028307 | -0.0047874 | -83.2672 | 0.10986 | -120.4651 | 0.23346 | -117.3981 | -120.1584 | -120.3323 | 0.10071 | 0.004578 | 0.032043 | 0.11902 | 0.20142 | 0.13733 | 0.19684 | -0.004578 | -0.17853 | -0.054932 | 3.0624 | 0.12817 | 0.30212 | 0.13275 | 0.3067 | 120.4926 | -0.28381 | -0.16937 | 120.6619 | 120.6573 | 120.5978 | 0.1648 | 0.10529 | 3.067 | 120.6985 | 0.16937 | 0.086976 | 120.575 | -0.027465 | 120.5704 | 120.4651 | -120.7535 | -0.25635 | 120.694 | 120.5795 | 37.1933 | 120.5612
2490.5312 | 121.0327 | -120.4651 | 0.27924 | -0.0016785 | 6.9776 | 0.06526 | 0.060442 | 0.00056817 | -0.0054731 | -0.002367 | -0.00054933 | 0.0026596 | 0.01311 | 0.018117 | -0.010899 | 0.027453 | -0.0011558 | -83.0887 | 0.10071 | -120.4971 | 0.22888 | -117.3523 | -120.1675 | -120.3323 | 0.12817 | -0.004578 | 0.050354 | 0.10986 | 0.20142 | 0.15564 | 0.22888 | -0.032043 | -0.17853 | -0.050354 | 3.1128 | 0.13275 | 0.29755 | 0.16479 | 0.32959 | 120.5154 | -0.28381 | -0.16937 | 120.6665 | 120.694 | 120.6207 | 0.17853 | 0.10529 | 3.1448 | 120.726 | 0.15106 | 0.059509 | 120.5978 | -0.054932 | 120.5658 | 120.4605 | -120.7764 | -0.22888 | 120.694 | 120.575 | 37.3764 | 120.5933
2492.2188 | 120.8954 | -120.5383 | 0.31128 | -0.0016785 | 6.9784 | 0.066755 | 0.063006 | -0.00028623 | -0.0052595 | -0.0012988 | 0.0025025 | 0.0033004 | 0.01076 | 0.0042318 | -0.012395 | 0.02318 | -0.0024374 | -82.9514 | 0.13275 | -120.5566 | 0.10986 | -117.4393 | -120.2682 | -120.4376 | -0.045776 | 0.050354 | -0.004578 | -0.032043 | 0.041199 | -0.013733 | 0.10071 | -0.018311 | -0.17853 | -0.20142 | 3.0991 | 0.10071 | 0.27008 | 0.11902 | 0.28839 | 120.5338 | -0.26092 | -0.34332 | 120.5795 | 120.639 | 120.5246 | 0.10529 | -0.009155 | 3.1174 | 120.6665 | 0.045777 | -0.027465 | 120.6894 | 0.054932 | 120.6711 | 120.5887 | -120.8679 | -0.31586 | 120.6482 | 120.5063 | 37.587 | 120.4926
2493.9531 | 121.0327 | -120.5109 | 0.3067 | -0.016937 | 6.9746 | 0.066541 | 0.060442 | 0.00014097 | -0.0046185 | -0.001726 | 0.0025025 | -0.0007584 | 0.01311 | 0.011281 | -0.0085491 | 0.026812 | -0.0028646 | -82.5714 | 0.10071 | -120.5017 | 0.25635 | -117.1829 | -120.1355 | -120.3323 | 0.11902 | -0.009155 | 0.045776 | 0.10071 | 0.19684 | 0.13733 | 0.19226 | 0.009155 | -0.20599 | -0.050354 | 3.3279 | 0.17853 | 0.37537 | 0.16937 | 0.36621 | 120.5566 | -0.31586 | -0.20599 | 120.7077 | 120.7031 | 120.6482 | 0.14648 | 0.091553 | 3.3188 | 120.7581 | 0.15106 | 0.054932 | 120.6024 | -0.054931 | 120.6116 | 120.5017 | -120.8084 | -0.26093 | 120.7672 | 120.6116 | 37.9395 | 120.6299
2495.7031 | 120.9686 | -120.52 | 0.3067 | 0.005951 | 6.9816 | 0.06761 | 0.06386 | -0.00071343 | -0.0073957 | -0.00065803 | -0.00054933 | 0.004155 | 0.013751 | 0.010427 | -0.0087629 | 0.026812 | -0.003292 | -82.7271 | 0.13275 | -120.5475 | 0.17853 | -117.2516 | -120.2362 | -120.4285 | 0.032043 | 0.050354 | 0.032043 | 0.041199 | 0.10529 | 0.036621 | 0.16022 | -0.027465 | -0.17395 | -0.12817 | 3.2684 | 0.091553 | 0.28381 | 0.11902 | 0.31128 | 120.5521 | -0.25635 | -0.2655 | 120.6253 | 120.6802 | 120.5566 | 0.12817 | 0.004578 | 3.2959 | 120.726 | 0.073243 | 0.009156 | 120.6802 | 0.018311 | 120.6528 | 120.5704 | -120.8542 | -0.27466 | 120.6985 | 120.5612 | 37.793 | 120.5521
2497.3906 | 121.0144 | -120.52 | 0.30212 | -0.0016785 | 6.9791 | 0.068464 | 0.062579 | 0.0014228 | -0.0041913 | 0.00062377 | -0.00054933 | 0.0005234 | 0.012683 | 0.017476 | -0.0087629 | 0.029589 | -0.0013694 | -84.7137 | 0.10986 | -120.5338 | 0.17395 | -117.2241 | -120.2225 | -120.3873 | 0.009155 | 0.009155 | 0.036621 | 0.036621 | 0.10986 | 0.054932 | 0.16022 | -0.013732 | -0.19226 | -0.12817 | 3.2959 | 0.13275 | 0.29755 | 0.14648 | 0.31128 | 120.5566 | -0.29297 | -0.2655 | 120.6299 | 120.6802 | 120.575 | 0.1236 | 0.018311 | 3.3096 | 120.7077 | 0.073242 | 0 | 120.6436 | -0.027466 | 120.6299 | 120.5292 | -120.8359 | -0.2655 | 120.694 | 120.5566 | 35.8063 | 120.5292
2499.125 | 121.0693 | -120.5429 | 0.28381 | -0.0016785 | 6.9791 | 0.068037 | 0.063433 | -0.0019952 | -0.0067547 | -0.0045032 | -0.0036011 | 0.0030868 | 0.013965 | 0.011709 | -0.0074811 | 0.027666 | -0.0037192 | -85.6842 | 0.09613 | -120.5338 | 0.25177 | -117.1188 | -120.195 | -120.3506 | 0.11444 | 0 | 0.036621 | 0.12817 | 0.17395 | 0.10986 | 0.21057 | 0.009156 | -0.18768 | -0.032043 | 3.4241 | 0.19226 | 0.3479 | 0.18311 | 0.33875 | 120.5795 | -0.28381 | -0.15564 | 120.7169 | 120.7535 | 120.6528 | 0.17395 | 0.073242 | 3.4149 | 120.7855 | 0.13733 | 0.091553 | 120.6299 | -0.036621 | 120.639 | 120.5429 | -120.8176 | -0.24719 | 120.7947 | 120.6711 | 34.8587 | 120.6573
2500.875 | 121.0968 | -120.5566 | 0.31128 | -0.0016785 | 6.9756 | 0.068464 | 0.062151 | -0.00092703 | -0.0073957 | -1.7026e-05 | -0.00054933 | 0.0018052 | 0.010547 | 0.013845 | -0.0079083 | 0.027025 | -0.0054282 | -86.0046 | 0.091553 | -120.575 | 0.25177 | -117.0181 | -120.1492 | -120.3461 | 0.10071 | -0.009155 | 0.054932 | 0.086975 | 0.20599 | 0.13733 | 0.19684 | -0.01831 | -0.21973 | -0.059509 | 3.5385 | 0.21057 | 0.40741 | 0.22888 | 0.42572 | 120.6116 | -0.32043 | -0.2243 | 120.7626 | 120.7535 | 120.694 | 0.14191 | 0.082397 | 3.5568 | 120.8267 | 0.15106 | 0.032043 | 120.6665 | -0.064087 | 120.6482 | 120.5475 | -120.8862 | -0.25635 | 120.8084 | 120.6436 | 34.552 | 120.6573
2502.5625 | 121.0602 | -120.5566 | 0.31586 | 0.005951 | 6.9789 | 0.067823 | 0.062792 | 0.0029182 | -0.0084637 | -0.0010852 | 0.0025025 | 0.000737 | 0.013965 | 0.010641 | -0.010472 | 0.02788 | -0.0064962 | -86.3709 | 0.082397 | -120.575 | 0.26093 | -116.9815 | -120.1538 | -120.3415 | 0.082397 | 0.004578 | 0.050354 | 0.064087 | 0.15106 | 0.10986 | 0.16937 | -0.01831 | -0.23346 | -0.054932 | 3.5751 | 0.21515 | 0.40283 | 0.23346 | 0.42114 | 120.607 | -0.31128 | -0.25177 | 120.7077 | 120.726 | 120.6665 | 0.11902 | 0.059509 | 3.5934 | 120.8359 | 0.10071 | 0.013733 | 120.6573 | -0.045776 | 120.639 | 120.5612 | -120.8908 | -0.2655 | 120.8176 | 120.6207 | 34.1858 | 120.639
2504.3125 | 121.0602 | -120.5933 | 0.29755 | -0.0016785 | 6.9767 | 0.068037 | 0.060015 | -0.00028623 | -0.0063275 | 0.001692 | -0.00054933 | 0.0003098 | 0.014605 | 0.014699 | -0.0085491 | 0.028734 | 0.00076681 | -86.3937 | 0.11902 | -120.5887 | 0.21515 | -116.9632 | -120.2271 | -120.3827 | 0.027466 | 0.022888 | 0.041199 | 0.050354 | 0.11444 | 0.059509 | 0.16022 | 0.004578 | -0.17853 | -0.082397 | 3.6301 | 0.21057 | 0.36621 | 0.20599 | 0.36163 | 120.6345 | -0.27466 | -0.24719 | 120.7077 | 120.7535 | 120.6528 | 0.11902 | 0.01831 | 3.6255 | 120.8038 | 0.073242 | 0.009155 | 120.7077 | -0.018311 | 120.7123 | 120.6161 | -120.8862 | -0.25635 | 120.8084 | 120.6436 | 34.1995 | 120.6207
2506 | 120.9869 | -120.6116 | 0.32501 | -0.009308 | 6.9816 | 0.06825 | 0.06386 | 0.00078177 | -0.0041913 | -0.00023063 | -0.00054933 | 0.0054368 | 0.014392 | 0.0085044 | -0.0072675 | 0.028094 | -0.0041464 | -86.4487 | 0.13733 | -120.6436 | 0.15106 | -116.9586 | -120.3094 | -120.488 | -0.064087 | 0.041199 | 0.018311 | -0.009155 | 0.036621 | -0.032043 | 0.082397 | -0.032044 | -0.18768 | -0.17395 | 3.653 | 0.1236 | 0.30212 | 0.15564 | 0.33417 | 120.6299 | -0.28381 | -0.33417 | 120.6482 | 120.694 | 120.5795 | 0.064086 | -0.050354 | 3.685 | 120.7947 | 0.01831 | -0.027466 | 120.7809 | 0.022888 | 120.7489 | 120.6528 | -120.9686 | -0.3067 | 120.7626 | 120.6024 | 34.1629 | 120.5475
2507.7344 | 121.0098 | -120.6345 | 0.32959 | -0.0016785 | 6.9803 | 0.067823 | 0.061083 | 0.0033454 | -0.0071821 | -0.0015124 | -0.00054933 | 0.0026596 | 0.01546 | 0.0089316 | -0.0076947 | 0.025744 | -0.0037192 | -86.5311 | 0.15564 | -120.6482 | 0.14648 | -116.835 | -120.3094 | -120.4514 | -0.050354 | 0.036621 | 0.027466 | 0.004578 | 0.045776 | -0.036621 | 0.09613 | -0.013733 | -0.17395 | -0.18311 | 3.7994 | 0.1831 | 0.32501 | 0.19684 | 0.33875 | 120.6619 | -0.29297 | -0.32501 | 120.6802 | 120.7306 | 120.5978 | 0.068664 | -0.064087 | 3.8132 | 120.7947 | 0.01831 | -0.022888 | 120.8038 | 0.009155 | 120.7901 | 120.6711 | -120.9778 | -0.30212 | 120.7809 | 120.639 | 34.1034 | 120.5841
2509.4688 | 121.1288 | -120.6116 | 0.29755 | -0.0016785 | 6.9786 | 0.068678 | 0.062151 | 0.0037726 | -0.0059003 | -0.00065803 | -0.0066527 | 0.0039414 | 0.014392 | 0.021535 | -0.0061993 | 0.029375 | -0.0041464 | -86.7188 | 0.15564 | -120.6299 | 0.18768 | -116.684 | -120.2591 | -120.401 | 0.027466 | 0.027466 | 0.036621 | 0.073242 | 0.13275 | 0.082397 | 0.19684 | -0.018311 | -0.14191 | -0.10986 | 3.9276 | 0.21057 | 0.35248 | 0.22888 | 0.37079 | 120.6482 | -0.27008 | -0.2243 | 120.7443 | 120.8084 | 120.694 | 0.16022 | 0.045776 | 3.9459 | 120.8176 | 0.09613 | 0.036621 | 120.7855 | -0.009155 | 120.7672 | 120.639 | -120.9274 | -0.26092 | 120.7993 | 120.6848 | 33.8928 | 120.639
2511.1562 | 121.1609 | -120.607 | 0.3067 | -0.016937 | 6.9786 | 0.069105 | 0.061511 | 0.00056817 | -0.0050457 | -1.7026e-05 | -0.0036011 | 0.0020188 | 0.01311 | 0.0095724 | -0.0089765 | 0.027239 | -0.0020102 | -86.7462 | 0.11902 | -120.6436 | 0.27008 | -116.4459 | -120.1218 | -120.3003 | 0.082397 | 0.004578 | 0.041199 | 0.10529 | 0.18768 | 0.13733 | 0.20599 | -0.036621 | -0.18768 | -0.036621 | 4.1611 | 0.3067 | 0.48523 | 0.34332 | 0.52185 | 120.6482 | -0.30212 | -0.20142 | 120.7947 | 120.813 | 120.7443 | 0.1648 | 0.09613 | 4.1977 | 120.9137 | 0.14648 | 0.064087 | 120.7626 | -0.036621 | 120.726 | 120.6116 | -120.9503 | -0.2655 | 120.8771 | 120.7123 | 33.8608 | 120.6894
2512.8906 | 121.1746 | -120.6116 | 0.29297 | -0.016937 | 6.9782 | 0.069746 | 0.06087 | 0.00056817 | -0.0071821 | 0.0021192 | -0.0036011 | 0.0015914 | 0.014605 | 0.015554 | -0.0098309 | 0.027025 | -0.00051479 | -86.6364 | 0.12817 | -120.6482 | 0.27466 | -116.3132 | -120.0897 | -120.2957 | 0.10986 | -0.004578 | 0.050354 | 0.10071 | 0.21057 | 0.13733 | 0.20142 | -0.036621 | -0.16479 | -0.018311 | 4.2984 | 0.31586 | 0.52185 | 0.35248 | 0.55847 | 120.6619 | -0.29755 | -0.19226 | 120.8221 | 120.813 | 120.7489 | 0.15106 | 0.086975 | 4.335 | 120.9229 | 0.16022 | 0.050354 | 120.7764 | -0.054932 | 120.7397 | 120.607 | -120.9412 | -0.24261 | 120.8862 | 120.7123 | 33.9752 | 120.7214
2514.5781 | 121.1792 | -120.6116 | 0.33875 | -0.0016785 | 6.978 | 0.069959 | 0.061511 | -0.00071343 | -0.0048321 | 0.0012646 | -0.0036011 | 0.0026596 | 0.016101 | 0.011495 | -0.0064129 | 0.026598 | -0.0039328 | -86.8195 | 0.13733 | -120.6802 | 0.19226 | -116.3544 | -120.2179 | -120.3873 | 0.027466 | 0.018311 | 0.036621 | 0.09613 | 0.14648 | 0.07782 | 0.20599 | -0.068665 | -0.20142 | -0.14648 | 4.2572 | 0.2243 | 0.39368 | 0.29297 | 0.46234 | 120.6482 | -0.32043 | -0.24262 | 120.7581 | 120.8176 | 120.6894 | 0.16937 | 0.041199 | 4.3259 | 120.8725 | 0.10986 | 0.059509 | 120.8176 | -0.01831 | 120.7489 | 120.6299 | -121.019 | -0.30212 | 120.8038 | 120.7077 | 33.7921 | 120.639
2516.3281 | 121.1517 | -120.6711 | 0.33417 | -0.0016785 | 6.9767 | 0.069319 | 0.061938 | 0.0014228 | -0.0044049 | -0.00023063 | -0.0036011 | 0.0013778 | 0.012683 | 0.006368 | -0.010258 | 0.028734 | -0.0041464 | -86.6638 | 0.11902 | -120.7031 | 0.25635 | -116.1072 | -120.108 | -120.3232 | 0.054932 | 0.004578 | 0.045776 | 0.054932 | 0.14648 | 0.091553 | 0.16022 | -0.032043 | -0.21515 | -0.077819 | 4.5639 | 0.3479 | 0.56305 | 0.37994 | 0.59509 | 120.7169 | -0.32959 | -0.27924 | 120.8176 | 120.8313 | 120.7626 | 0.11444 | 0.045777 | 4.5959 | 120.9595 | 0.10071 | 0.009156 | 120.8221 | -0.041198 | 120.7901 | 120.6757 | -121.0373 | -0.28839 | 120.9274 | 120.726 | 34.0073 | 120.726
2518.0156 | 121.0831 | -120.6985 | 0.33417 | -0.0016785 | 6.9795 | 0.070387 | 0.061083 | 0.0033454 | -0.0026959 | 0.00019657 | 0.0025025 | 0.003514 | 0.015887 | 0.0055136 | -0.0057721 | 0.026812 | -0.001583 | -86.7279 | 0.15106 | -120.7214 | 0.12817 | -116.2216 | -120.282 | -120.4422 | -0.082397 | 0.027466 | 0.009155 | -0.004578 | 0.027466 | -0.032043 | 0.11444 | -0.022889 | -0.1831 | -0.20599 | 4.4769 | 0.25635 | 0.41657 | 0.27924 | 0.43945 | 120.7077 | -0.3067 | -0.33875 | 120.726 | 120.813 | 120.6665 | 0.10529 | -0.041198 | 4.4998 | 120.8496 | 0.018311 | -0.013733 | 120.8725 | 0.018311 | 120.8496 | 120.726 | -121.0556 | -0.32501 | 120.8267 | 120.694 | 33.9706 | 120.6162
2519.7656 | 121.2341 | -120.6802 | 0.29297 | -0.0016785 | 6.9771 | 0.070173 | 0.062151 | -0.00092703 | -0.0022687 | 0.0021192 | -0.00054933 | 0.0003098 | 0.012469 | 0.012563 | -0.0070539 | 0.027239 | -0.003292 | -86.792 | 0.12817 | -120.6802 | 0.25635 | -115.9149 | -120.1492 | -120.3003 | 0.09613 | 0.004578 | 0.064087 | 0.1236 | 0.17395 | 0.11902 | 0.21057 | 0 | -0.16479 | -0.036621 | 4.7653 | 0.37994 | 0.53101 | 0.37994 | 0.53101 | 120.7443 | -0.28839 | -0.16937 | 120.8542 | 120.8908 | 120.7993 | 0.14648 | 0.054932 | 4.7653 | 120.9366 | 0.10986 | 0.059509 | 120.8084 | -0.059509 | 120.8084 | 120.6848 | -120.9732 | -0.22888 | 120.9366 | 120.8038 | 33.8882 | 120.7764
2521.5156 | 121.225 | -120.7031 | 0.31586 | -0.016937 | 6.9784 | 0.0706 | 0.059374 | -0.00049983 | -0.0052595 | 0.0014784 | -0.0066527 | 0.0020188 | 0.012469 | 0.0091452 | -0.010472 | 0.028307 | -0.006069 | -86.7599 | 0.11444 | -120.7169 | 0.26093 | -115.773 | -120.0714 | -120.2591 | 0.068665 | 0.018311 | 0.041199 | 0.073242 | 0.16937 | 0.10986 | 0.17853 | -0.013733 | -0.20142 | -0.054932 | 4.9301 | 0.44403 | 0.63171 | 0.45776 | 0.64545 | 120.7443 | -0.29755 | -0.24261 | 120.8725 | 120.8817 | 120.813 | 0.13733 | 0.068664 | 4.9438 | 120.9778 | 0.12817 | 0.032043 | 120.8313 | -0.022888 | 120.8176 | 120.7214 | -121.0327 | -0.27466 | 120.9641 | 120.7764 | 33.9432 | 120.7718
2523.25 | 121.1517 | -120.7397 | 0.34332 | 0.005951 | 6.9786 | 0.071455 | 0.061297 | 0.0016364 | -0.0039777 | 0.00062377 | -0.00054933 | 0.0043686 | 0.011188 | 0.017263 | -0.01154 | 0.027025 | -0.001583 | -86.8057 | 0.1236 | -120.7443 | 0.21057 | -115.6586 | -120.1126 | -120.3003 | -0.004578 | 0.022888 | 0.013733 | 0.009155 | 0.082397 | 0.027466 | 0.11444 | -0.004578 | -0.21973 | -0.13275 | 5.0812 | 0.43945 | 0.62714 | 0.44403 | 0.63171 | 120.7535 | -0.32043 | -0.33417 | 120.8221 | 120.8542 | 120.7672 | 0.10071 | 0.013733 | 5.0858 | 120.9549 | 0.068664 | -0.004578 | 120.8679 | 0.009155 | 120.8633 | 120.7626 | -121.0876 | -0.32959 | 120.9503 | 120.7489 | 33.934 | 120.7352
2524.9219 | 121.1472 | -120.7581 | 0.32044 | -0.009308 | 6.9776 | 0.070387 | 0.064501 | 0.00078177 | -0.0026959 | 0.00062377 | 0.0025025 | 0.004155 | 0.012683 | 0.009786 | -0.0061993 | 0.027453 | -0.0011558 | -86.8744 | 0.17395 | -120.7718 | 0.12817 | -115.5945 | -120.1859 | -120.3644 | -0.064087 | 0.032043 | 0 | 0.013733 | 0.032043 | -0.027466 | 0.10986 | -0.013733 | -0.14649 | -0.19226 | 5.1636 | 0.39368 | 0.5722 | 0.40741 | 0.58594 | 120.7581 | -0.28839 | -0.3067 | 120.7901 | 120.8679 | 120.7306 | 0.10986 | -0.027466 | 5.1773 | 120.9 | 0.032043 | 0.013733 | 120.9457 | 0.032043 | 120.932 | 120.7901 | -121.0922 | -0.32044 | 120.8862 | 120.7718 | 33.8837 | 120.694
2526.6875 | 121.2708 | -120.7214 | 0.30212 | -0.0016785 | 6.9763 | 0.0706 | 0.060015 | -7.2628e-05 | -0.0059003 | 0.00062377 | -0.00054933 | 0.0028732 | 0.013537 | 0.012563 | -0.010045 | 0.027239 | -0.0013694 | -86.8973 | 0.12817 | -120.7535 | 0.27466 | -115.21 | -120.0027 | -120.2087 | 0.10071 | 0.009155 | 0.036621 | 0.10071 | 0.20142 | 0.14191 | 0.19684 | -0.032043 | -0.17395 | -0.027466 | 5.5115 | 0.5127 | 0.71869 | 0.54474 | 0.75073 | 120.7581 | -0.29297 | -0.20142 | 120.9229 | 120.9183 | 120.8633 | 0.16022 | 0.10529 | 5.5435 | 121.0281 | 0.1648 | 0.064087 | 120.8817 | -0.027466 | 120.8496 | 120.7306 | -121.0556 | -0.2655 | 120.9961 | 120.8221 | 33.8242 | 120.8221
2528.4219 | 121.2296 | -120.7535 | 0.32501 | -0.009308 | 6.9771 | 0.071882 | 0.060229 | 0.003559 | -0.0035505 | 0.0019056 | -0.0036011 | 0.0020188 | 0.014392 | 0.0059408 | -0.0085491 | 0.026812 | -0.0045736 | -87.1445 | 0.13733 | -120.7443 | 0.21515 | -115.1093 | -120.0668 | -120.2362 | 0.027466 | 0.004578 | 0.054932 | 0.041199 | 0.12817 | 0.064087 | 0.14648 | 0.009155 | -0.18768 | -0.10986 | 5.6442 | 0.51727 | 0.68665 | 0.50812 | 0.67749 | 120.8084 | -0.32043 | -0.28381 | 120.8817 | 120.9 | 120.8176 | 0.091552 | 0.009155 | 5.6351 | 120.9595 | 0.073242 | -0.013733 | 120.8817 | -0.050354 | 120.8908 | 120.7581 | -121.0693 | -0.27008 | 120.9686 | 120.7947 | 33.609 | 120.7809
2530.1094 | 121.1655 | -120.7672 | 0.35248 | -0.0016785 | 6.9806 | 0.071241 | 0.065142 | 0.0022772 | -0.0050457 | 0.00083737 | -0.00054933 | 0.0033004 | 0.01311 | 0.012136 | -0.0070539 | 0.026171 | -0.0035056 | -87.2131 | 0.15106 | -120.7947 | 0.13275 | -115.0131 | -120.1401 | -120.314 | -0.07782 | 0.032043 | 0.022888 | -0.018311 | 0.022888 | -0.036621 | 0.10071 | -0.027466 | -0.20142 | -0.21973 | 5.7541 | 0.45319 | 0.62714 | 0.48065 | 0.6546 | 120.7901 | -0.32044 | -0.37079 | 120.7901 | 120.8679 | 120.7306 | 0.07782 | -0.059509 | 5.7816 | 120.9274 | 0 | -0.041199 | 120.9457 | 0.009155 | 120.9183 | 120.7993 | -121.1472 | -0.32959 | 120.9 | 120.7489 | 33.5541 | 120.6894
2531.8594 | 121.2524 | -120.7581 | 0.32501 | -0.009308 | 6.9771 | 0.070387 | 0.06087 | -0.00071343 | -0.0039777 | 0.0029736 | -0.00054933 | 0.000737 | 0.01311 | 0.012563 | -0.0085491 | 0.029162 | 0.00098061 | -87.0987 | 0.14191 | -120.7581 | 0.20599 | -114.6927 | -120.0165 | -120.1859 | 0.009155 | 0 | 0.032043 | 0.064087 | 0.11444 | 0.068665 | 0.17395 | 0 | -0.18311 | -0.11902 | 6.0654 | 0.5722 | 0.74158 | 0.5722 | 0.74158 | 120.7901 | -0.32501 | -0.26093 | 120.8725 | 120.932 | 120.8267 | 0.14191 | 0.036622 | 6.0654 | 120.9641 | 0.082398 | 0.032044 | 120.9 | -0.032043 | 120.9 | 120.7581 | -121.0831 | -0.29297 | 120.9641 | 120.8221 | 33.6594 | 120.7672
2533.6094 | 121.1884 | -120.7764 | 0.33875 | -0.0016785 | 6.9771 | 0.071028 | 0.060229 | -0.00049983 | -0.0016279 | 0.0055372 | -0.0066527 | 0.002446 | 0.01311 | 0.008718 | -0.013676 | 0.026171 | -0.0011558 | -87.0987 | 0.14648 | -120.8038 | 0.15106 | -114.4775 | -120.0165 | -120.1859 | -0.027466 | 0.036621 | 0.013733 | -0.018311 | 0.054932 | -0.004578 | 0.10071 | -0.027466 | -0.19226 | -0.18768 | 6.2988 | 0.59051 | 0.75989 | 0.61798 | 0.78735 | 120.7901 | -0.30212 | -0.35706 | 120.8313 | 120.8771 | 120.7718 | 0.086975 | -0.018311 | 6.3263 | 120.9549 | 0.041199 | -0.032044 | 120.9503 | 0.022888 | 120.9229 | 120.813 | -121.1426 | -0.32501 | 120.9274 | 120.7581 | 33.6777 | 120.7489
2535.3438 | 121.2158 | -120.7718 | 0.32044 | -0.0016785 | 6.9799 | 0.071241 | 0.060229 | 0.0050544 | -0.0041913 | 0.0040418 | -0.00054933 | 0.005864 | 0.013965 | 0.012777 | -0.0079083 | 0.027025 | -0.0075644 | -87.03 | 0.14648 | -120.8313 | 0.21973 | -114.2349 | -119.989 | -120.163 | 0.027466 | 0.032043 | 0.027466 | 0.045776 | 0.11444 | 0.027466 | 0.15106 | -0.059509 | -0.17395 | -0.10071 | 6.5369 | 0.60883 | 0.78278 | 0.66833 | 0.84229 | 120.7993 | -0.28839 | -0.27466 | 120.8862 | 120.9229 | 120.7993 | 0.1236 | 0 | 6.5964 | 121.051 | 0.086975 | 0.01831 | 120.9778 | 0.004577 | 120.9183 | 120.8038 | -121.1517 | -0.29297 | 120.9915 | 120.8176 | 33.7418 | 120.7993
2537.0312 | 121.344 | -120.7581 | 0.31128 | -0.0016785 | 6.9774 | 0.07295 | 0.061511 | -0.00028623 | -0.0016279 | 0.0029736 | -0.00054933 | 0.0003098 | 0.013965 | 0.010427 | -0.011326 | 0.026812 | -0.0030784 | -87.0209 | 0.13733 | -120.8221 | 0.25177 | -113.9511 | -119.8791 | -120.0623 | 0.07782 | -0.004578 | 0.036621 | 0.11902 | 0.21057 | 0.14191 | 0.21515 | -0.064087 | -0.17395 | -0.059509 | 6.8069 | 0.6958 | 0.87891 | 0.75989 | 0.94299 | 120.7947 | -0.31586 | -0.19226 | 120.9686 | 120.9732 | 120.9 | 0.17853 | 0.10529 | 6.871 | 121.0739 | 0.17395 | 0.082398 | 120.9595 | -0.041199 | 120.8954 | 120.7535 | -121.1334 | -0.27466 | 121.0098 | 120.8771 | 33.7372 | 120.8359
2538.7188 | 121.2204 | -120.8221 | 0.37079 | 0.005951 | 6.9801 | 0.071882 | 0.061724 | 0.00035457 | -0.00034609 | 0.00276 | -0.0066527 | 0.0045822 | 0.016955 | 0.0085044 | -0.011326 | 0.027239 | -0.0041464 | -87.0712 | 0.17395 | -120.8405 | 0.15564 | -113.8275 | -119.9478 | -120.1309 | -0.064087 | 0.045776 | 0 | -0.013733 | 0.045776 | -0.018311 | 0.10071 | -0.01831 | -0.19684 | -0.21515 | 6.9946 | 0.69122 | 0.87433 | 0.70953 | 0.89264 | 120.8221 | -0.32501 | -0.38452 | 120.8679 | 120.9229 | 120.8038 | 0.10071 | -0.018311 | 7.0129 | 120.9961 | 0.045776 | -0.013733 | 121.0144 | 0.045776 | 120.9961 | 120.8679 | -121.2112 | -0.37079 | 120.9778 | 120.8084 | 33.7509 | 120.7581
2540.4688 | 121.2067 | -120.6802 | 0.27008 | -0.009308 | 6.9786 | 0.074446 | 0.062792 | 0.00035457 | -0.00034609 | 0.0042554 | -0.0066527 | 0.0009506 | 0.012042 | 0.011068 | -0.0089765 | 0.027453 | -0.0037192 | -86.5036 | 0.064087 | -120.6985 | 0.23346 | -113.3377 | -119.6823 | -119.902 | 0.086975 | 0.009155 | 0.064087 | 0.10986 | 0.16937 | 0.1236 | 0.19684 | -0.01831 | -0.20599 | -0.036622 | 7.3425 | 0.7782 | 0.99793 | 0.79651 | 1.0162 | 120.7443 | -0.26093 | -0.16022 | 120.8496 | 120.8771 | 120.8038 | 0.13275 | 0.059509 | 7.3608 | 120.932 | 0.10529 | 0.045776 | 120.7626 | -0.054932 | 120.7443 | 120.6894 | -120.9686 | -0.20599 | 120.9137 | 120.7901 | 34.1766 | 120.7672
2542.1562 | 120.7901 | -120.2911 | 0.28839 | -0.0016785 | 6.9791 | 0.076582 | 0.064074 | 0.0020636 | -0.0039777 | 0.0046826 | -0.0036011 | 0.0037278 | 0.013324 | 0.010854 | -0.0053449 | 0.029162 | -0.0011558 | -85.8719 | 0.12817 | -120.3461 | 0.12817 | -112.8983 | -119.4443 | -119.6228 | -0.036621 | 0.027466 | 0.31586 | 0.068665 | 0.073242 | 0.018311 | 0.14191 | -0.054931 | -0.16022 | -0.16022 | 7.3929 | 0.66833 | 0.84686 | 0.72327 | 0.90179 | 120.607 | -0.26093 | -0.21973 | 120.3644 | 120.433 | 120.3094 | -0.17395 | -0.29755 | 7.4478 | 120.4742 | -0.24261 | -0.24719 | 120.4742 | -0.28839 | 120.4193 | 120.3186 | -120.6345 | 0.027466 | 120.4193 | 120.3598 | 34.4193 | 120.2545
2543.9062 | 121.0373 | -120.4559 | 0.29755 | -0.0016785 | 6.9774 | 0.079145 | 0.060015 | -0.00071343 | -0.00013249 | 0.0051098 | 0.0025025 | 0.0018052 | 0.01311 | 0.014059 | -0.0068403 | 0.027666 | -0.002651 | -85.1715 | 0.091553 | -120.4605 | 0.22888 | -112.4039 | -119.0872 | -119.2703 | 0.082397 | -0.16022 | 0.37079 | 0.10986 | 0.1236 | 0.045776 | 0.1236 | -0.004577 | -0.20599 | -0.068664 | 8.0521 | 1.1856 | 1.3687 | 1.1902 | 1.3733 | 120.8267 | -0.45776 | -0.18768 | 120.5795 | 120.5795 | 120.5017 | -0.24719 | -0.32501 | 8.0566 | 120.6894 | -0.24719 | -0.26093 | 120.5521 | -0.53101 | 120.5475 | 120.2957 | -120.7581 | 0.073243 | 120.6848 | 120.5658 | 35.2844 | 120.5383
2545.5781 | 120.7993 | -120.3323 | 0.18768 | 0.01358 | 6.9797 | 0.077223 | 0.049334 | -0.0075494 | -0.0054731 | 0.053602 | -0.20197 | -0.0028946 | 0.018237 | 0.0078634 | 0.035243 | 0.045397 | 0.031529 | -72.8577 | -0.018311 | -119.6228 | -0.1831 | -85.762 | -94.9631 | -95.755 | -0.42114 | 0.07782 | -0.07782 | -0.018311 | 0.07782 | 0.086975 | 0.082397 | 0.70953 | -0.20599 | -0.37079 | 34.5703 | 24.5773 | 25.3693 | 23.8678 | 24.6597 | 120.2545 | -0.10986 | -0.20599 | 120.4102 | 120.4147 | 120.4193 | 0.16022 | 0.16479 | 33.8608 | 119.4397 | 0.15564 | 0.059509 | 119.6045 | 0.15564 | 120.314 | 120.4102 | -119.8105 | -0.2655 | 120.1492 | 120.314 | 47.4747 | 119.9112
2547.3281 | 120.9183 | -120.3827 | 0.28381 | -0.0016785 | 6.9789 | 0.076154 | -0.014326 | 0.010609 | 0.02123 | 0.052534 | -0.1684 | 0.028508 | 0.017596 | 0.0074362 | 0.034816 | 0.045397 | 0.031529 | -64.9521 | -0.21515 | -120.1492 | 0.11444 | -82.251 | -92.0197 | -92.8574 | 0.086975 | 0.086975 | -0.082397 | 0.073242 | 0.086975 | 0.086975 | 0.082397 | 0.23346 | -0.49896 | -0.16937 | 38.1317 | 27.5253 | 28.363 | 27.2919 | 28.1296 | 120.3003 | -0.19684 | -0.21057 | 120.4697 | 120.4651 | 120.4697 | 0.16479 | 0.16937 | 37.8983 | 120.2637 | 0.16937 | 0.15564 | 119.9341 | 0.16937 | 120.1675 | 120.4697 | -120.433 | -0.36621 | 120.4971 | 120.4559 | 55.4306 | 120.4697
2549.0625 | 121.0098 | -120.5841 | 0.31586 | -0.0016785 | 6.9795 | 0.076154 | 0.061511 | -0.0039178 | -0.00077329 | 0.0051098 | 0.0025025 | 0.0026596 | 0.014392 | 0.0010276 | -0.011113 | 0.025316 | -0.0028646 | -83.4961 | 0.12817 | -119.8334 | 0.050354 | -111.8546 | -119.2154 | -119.577 | -0.068665 | -0.26093 | 0.082397 | -0.032043 | -0.30212 | -0.19226 | 0.018311 | 0.75073 | -0.18768 | -0.2655 | 8.7296 | 1.0071 | 1.3687 | 0.25635 | 0.61798 | 120.6665 | -0.57678 | -0.3479 | 120.282 | 120.6024 | 120.3918 | -0.064086 | -0.27466 | 7.9788 | 119.8837 | -0.38452 | -0.11444 | 119.9615 | -0.34332 | 120.7123 | 120.3232 | -120.1492 | -0.23346 | 120.6345 | 120.5521 | 37.088 | 120.5154
2550.7969 | 120.9824 | -120.4514 | 0.29755 | -0.0016785 | 6.9784 | 0.077223 | 0.061511 | -0.00049983 | -0.0016279 | 0.0068188 | -0.024963 | 0.002446 | 0.013324 | 0.0048728 | -0.012822 | 0.02788 | 0.0022622 | -82.9147 | 0.1236 | -119.8059 | 0.018311 | -111.7905 | -119.3848 | -119.6365 | -0.068665 | -0.30212 | -0.091553 | -0.018311 | -0.29297 | -0.050354 | -0.027466 | 0.64545 | -0.17395 | -0.27923 | 8.6609 | 0.81482 | 1.0666 | 0.16937 | 0.42114 | 120.3598 | -0.59967 | -0.31586 | 120.1584 | 120.4239 | 120.401 | 0.064087 | 0.041199 | 8.0154 | 119.8242 | -0.20142 | 0.073242 | 119.9295 | -0.21057 | 120.575 | 120.1492 | -120.1035 | -0.3891 | 120.4697 | 120.433 | 37.5366 | 120.3827
2552.4844 | 121.0464 | -120.4147 | 0.29297 | -0.0016785 | 6.9793 | 0.077436 | 0.06087 | -0.00028623 | -0.00013249 | 0.0031872 | -0.00054933 | 0.0028732 | 0.013537 | 0.01299 | -0.0064129 | 0.029162 | -0.001583 | -82.6401 | 0.082397 | -120.2957 | 0.21973 | -111.0764 | -118.927 | -119.1193 | 0.082397 | -0.14191 | 0.36163 | 0.082397 | 0.11902 | 0.041199 | 0.11444 | 0.11902 | -0.21057 | -0.073242 | 9.3384 | 1.2955 | 1.4877 | 1.1765 | 1.3687 | 120.7764 | -0.43488 | -0.21057 | 120.5338 | 120.5292 | 120.4559 | -0.24719 | -0.32043 | 9.2194 | 120.5154 | -0.24261 | -0.27924 | 120.3781 | -0.50354 | 120.4971 | 120.2728 | -120.5887 | 0.068664 | 120.6345 | 120.4971 | 37.7747 | 120.4971
2554.2344 | 120.6848 | -119.7922 | 0.43488 | -0.0016785 | 6.9776 | 0.075941 | 0.060442 | -0.0019952 | 0.0013629 | 0.0085278 | -0.00054933 | 0.0013778 | 0.014605 | 0.0091452 | -0.0091901 | 0.028307 | -0.0020102 | -82.1915 | 0.21057 | -119.7784 | 0.36621 | -110.289 | -118.2404 | -118.4418 | 0.1236 | -0.10529 | 0.2655 | 0.11902 | 0.20599 | 0.10986 | 0.16937 | 0.013733 | -0.2243 | -0.068664 | 9.5032 | 1.3504 | 1.5518 | 1.3367 | 1.5381 | 120.0577 | -0.54016 | -0.31586 | 119.9982 | 119.9615 | 119.902 | -0.09613 | -0.15564 | 9.4894 | 120.1447 | -0.059509 | -0.14648 | 119.989 | -0.37079 | 120.0027 | 119.6869 | -120.2133 | -0.16937 | 120.1584 | 119.9112 | 37.6007 | 119.9158
2555.9219 | 120.4788 | -119.9203 | 0.25635 | 0.01358 | 6.9776 | 0.081495 | 0.061511 | 0.0029182 | 0.0020037 | 0.0042554 | -0.049377 | 0.0033004 | 0.012683 | 0.0099996 | -0.0059857 | 0.028948 | -0.0035056 | -81.4911 | 0.14648 | -119.8288 | 0.050354 | -109.3689 | -118.7668 | -117.5674 | -0.1831 | -0.3067 | 0.16022 | -0.14191 | -0.2243 | -0.27924 | -0.16022 | 0.091553 | -0.10986 | -0.20599 | 10.5515 | 2.3529 | 1.1536 | 2.2614 | 1.062 | 120.0806 | -0.56305 | -0.39826 | 119.696 | 119.7601 | 119.6411 | -0.32043 | -0.43945 | 10.4599 | 119.8791 | -0.38452 | -0.30212 | 119.9753 | -0.46692 | 120.0668 | 119.6136 | -120.0851 | -0.096131 | 119.9707 | 119.7784 | 38.4293 | 119.7372
2557.6562 | 116.7252 | -71.8506 | 44.8196 | -0.0016785 | 6.9812 | 0.069105 | 0.060656 | -0.0028498 | -0.0018415 | 0.003401 | -0.0066527 | 0.0013778 | 0.012469 | 0.010427 | -0.010045 | 0.027025 | -0.00030119 | -46.8063 | 46.3898 | -69.2871 | 45.7581 | -65.8173 | -69.7723 | -69.4977 | 0.086975 | -0.36621 | 0.29297 | 0.07782 | 0.082397 | 0.022888 | 0.064087 | 2.5635 | 1.5701 | 0.93842 | 6.0333 | 2.3529 | 2.0782 | -0.21057 | -0.48523 | 72.1436 | -45.1859 | -44.7418 | 71.933 | 71.9147 | 71.8735 | -0.22888 | -0.27008 | 3.4698 | 115.0452 | -0.21057 | -0.21515 | 115.6769 | -0.65918 | 118.2404 | 71.4844 | -114.1068 | -44.5267 | 117.6086 | 71.9284 | 25.0443 | 71.9376
2559.4062 | 120.7443 | -120.3873 | 0.25635 | -0.0016785 | 6.9793 | 0.08 | 0.054888 | -0.007763 | 0.0026447 | -0.005144 | -0.15924 | -0.009517 | 0.012042 | 0.0048728 | -0.0053449 | 0.02553 | -0.00436 | -80.7312 | 0.091553 | -120.3827 | -0.041199 | -98.4375 | -107.2861 | -106.2469 | -0.082397 | -0.3067 | 0.086975 | -0.054932 | -0.091553 | 0.10986 | 0.082397 | 0.004578 | -0.1648 | -0.29755 | 21.9498 | 14.1403 | 13.1012 | 14.1357 | 13.0966 | 120.4742 | -0.56305 | -0.31128 | 120.2957 | 120.4697 | 120.4971 | -0.004578 | 0.022888 | 21.9452 | 120.3415 | -0.17853 | -0.14191 | 120.4742 | -0.39368 | 120.4788 | 120.0806 | -120.639 | -0.16937 | 120.3461 | 120.3323 | 39.6561 | 120.3049
2561.0781 | 120.9595 | -120.4559 | 0.24261 | 0.01358 | 6.9799 | 0.080641 | 0.063006 | -0.0011408 | 0.0011493 | 0.007887 | 0.0025025 | 0.0028732 | 0.013537 | 0.01534 | -0.010472 | 0.02788 | -0.0017966 | -80.5801 | 0.054932 | -120.4697 | 0.19684 | -109.845 | -118.4189 | -118.7439 | 0.086975 | -0.004578 | 0.21057 | 0.09613 | 0.15564 | 0.009155 | 0.032043 | -0.013733 | -0.18768 | -0.045777 | 10.611 | 1.712 | 2.037 | 1.7258 | 2.0508 | 120.6665 | -0.24719 | -0.14649 | 120.6116 | 120.488 | 120.4651 | -0.17853 | -0.20142 | 10.6247 | 120.6665 | -0.054931 | -0.11444 | 120.5246 | -0.21515 | 120.5109 | 120.4514 | -120.7123 | -0.032044 | 120.6528 | 120.5521 | 39.8758 | 120.5429
2562.8281 | 120.9961 | -120.52 | 0.24719 | -0.0016785 | 6.9816 | 0.081068 | 0.063006 | -0.00049983 | 0.0049945 | 0.0074598 | 0.0025025 | 0.002446 | 0.012683 | 0.022603 | -0.0061993 | 0.029162 | -0.0017966 | -80.2551 | 0.07782 | -120.5246 | 0.14191 | -109.5657 | -118.364 | -118.9362 | 0.041199 | 0.018311 | 0.036621 | 0.11444 | 0.10986 | -0.09613 | -0.059509 | -0.004577 | -0.16937 | -0.10528 | 10.9543 | 1.5839 | 2.1561 | 1.5884 | 2.1606 | 120.5566 | -0.22888 | -0.13275 | 120.6299 | 120.4605 | 120.4239 | -0.09613 | -0.13275 | 10.9589 | 120.6665 | 0.073242 | 0.07782 | 120.6024 | -0.01831 | 120.5978 | 120.5383 | -120.7718 | -0.21057 | 120.6619 | 120.6345 | 40.2649 | 120.5612
2564.5781 | 121.051 | -120.5795 | 0.24261 | -0.009308 | 6.9782 | 0.080427 | 0.062579 | -0.003277 | 0.0028583 | 0.0068188 | -0.00054933 | 0.0020188 | 0.013537 | 0.022176 | -0.0094037 | 0.029375 | -0.003292 | -79.7379 | 0.059509 | -120.575 | 0.21973 | -109.5749 | -118.4784 | -118.8263 | 0.11902 | -0.009155 | 0.054932 | 0.09613 | 0.1831 | 0.15106 | 0.15564 | 0.004578 | -0.18311 | -0.022888 | 11.0046 | 1.7532 | 2.1011 | 1.7487 | 2.0966 | 120.6345 | -0.25177 | -0.14649 | 120.7626 | 120.7352 | 120.7306 | 0.10071 | 0.09613 | 11.0001 | 120.7947 | 0.12817 | 0.041198 | 120.6345 | -0.064087 | 120.639 | 120.5704 | -120.8176 | -0.18768 | 120.7993 | 120.6757 | 40.8417 | 120.6985
2566.3125 | 121.0968 | -120.5841 | 0.24719 | -0.0016785 | 6.9778 | 0.081068 | 0.061938 | -0.0030634 | 0.0034991 | 0.010237 | -0.00054933 | 0.0013778 | 0.013537 | 0.01769 | -0.0094037 | 0.026812 | -0.0052146 | -79.2938 | 0.050354 | -120.5795 | 0.18768 | -109.52 | -118.5333 | -118.8858 | 0.07782 | -0.009155 | 0.027466 | 0.12817 | 0.17853 | 0.14191 | 0.21515 | 0.004577 | -0.19684 | -0.059509 | 11.0641 | 1.6983 | 2.0508 | 1.6937 | 2.0462 | 120.6116 | -0.25635 | -0.11902 | 120.7626 | 120.7993 | 120.726 | 0.18768 | 0.11444 | 11.0596 | 120.7672 | 0.15106 | 0.10071 | 120.6299 | -0.036621 | 120.6345 | 120.575 | -120.8267 | -0.21973 | 120.7718 | 120.7123 | 41.2903 | 120.6619
2568 | 121.1105 | -120.5978 | 0.25177 | 0.005951 | 6.9795 | 0.085554 | 0.061938 | 0.0016364 | 0.0054217 | 0.0089552 | -0.0036011 | 0.002446 | 0.012897 | 0.017263 | -0.0044903 | 0.032152 | -0.002651 | -78.978 | 0.041199 | -120.6116 | 0.20142 | -109.1721 | -118.3273 | -118.689 | 0.10071 | -0.009155 | 0.073242 | 0.14191 | 0.16937 | 0.10986 | 0.17853 | -0.013733 | -0.21057 | -0.050354 | 11.4258 | 1.9089 | 2.2705 | 1.9226 | 2.2842 | 120.6711 | -0.26093 | -0.10986 | 120.7672 | 120.7764 | 120.7077 | 0.10529 | 0.036621 | 11.4395 | 120.813 | 0.096131 | 0.068665 | 120.6528 | -0.082397 | 120.639 | 120.5887 | -120.8633 | -0.17853 | 120.7993 | 120.7397 | 41.6199 | 120.6985
2569.75 | 121.0785 | -120.6299 | 0.27466 | 0.01358 | 6.9797 | 0.085768 | 0.062365 | -7.2628e-05 | 0.0064899 | 0.0098096 | -0.00054933 | 0.0011642 | 0.012256 | 0.014272 | -0.0098309 | 0.028948 | -0.0013694 | -79.2572 | 0.064087 | -120.6528 | 0.19226 | -109.0942 | -118.4738 | -118.8263 | 0.073242 | 0.018311 | 0.027466 | 0.073242 | 0.13275 | 0.091553 | 0.16022 | -0.022888 | -0.21057 | -0.082397 | 11.5356 | 1.8036 | 2.1561 | 1.8265 | 2.179 | 120.6573 | -0.25635 | -0.20142 | 120.7626 | 120.7901 | 120.7214 | 0.13275 | 0.064087 | 11.5585 | 120.845 | 0.10529 | 0.045776 | 120.7169 | -0.009155 | 120.694 | 120.6482 | -120.9274 | -0.24719 | 120.8221 | 120.7031 | 41.3727 | 120.7031
2571.5 | 120.2316 | -120.2408 | 0.27924 | -0.0016785 | 6.9816 | 0.083418 | 0.065356 | -0.00028623 | 0.0047809 | 0.0070326 | -0.021912 | -0.013789 | 0.012469 | 0.01299 | -0.010258 | 0.02788 | -0.0056418 | -79.2023 | 0.086975 | -120.726 | 0.091553 | -108.6456 | -118.3823 | -115.0635 | -0.050354 | 0.036621 | 0.022888 | -0.013733 | 0.032043 | -0.16937 | -0.25177 | -0.48523 | -0.19226 | -0.18768 | 11.5952 | 5.1773 | 1.8585 | 5.6625 | 2.3438 | 120.2637 | -0.24261 | -0.29297 | 120.2728 | 119.989 | 120.0714 | -0.27466 | -0.19226 | 12.0804 | 120.8176 | 0.009155 | -0.036621 | 120.813 | 0.013733 | 120.3278 | 120.2774 | -121.0052 | -0.25635 | 120.3323 | 120.2271 | 41.0385 | 120.1904
2573.2344 | 120.2362 | -120.1767 | 0.28381 | -0.009308 | 6.9831 | 0.084059 | 0.063433 | -0.0019952 | 0.0090533 | 0.0089552 | -0.0066527 | 0.000737 | 0.012897 | 0.014486 | -0.0094037 | 0.028094 | -0.0073508 | -79.1336 | 0.10529 | -120.7169 | 0.09613 | -108.4305 | -118.0161 | -119.4534 | -0.091553 | 0.036621 | 0.022888 | -0.022888 | 0.022888 | -0.082397 | -0.20142 | -0.54016 | -0.17853 | -0.18768 | 11.7462 | 0.72327 | 2.1606 | 1.2634 | 2.7008 | 120.1996 | -0.24719 | -0.3067 | 120.1996 | 119.9753 | 120.0943 | -0.2243 | -0.10528 | 12.2864 | 120.813 | 0 | -0.045776 | 120.8221 | 0.013733 | 120.282 | 120.2133 | -121.0007 | -0.26092 | 120.2728 | 120.1538 | 41.0431 | 120.0851
2574.9844 | 121.1563 | -120.6757 | 0.25177 | 0.01358 | 6.9821 | 0.08534 | 0.062365 | 0.0046272 | 0.0088397 | 0.014509 | 0.0086061 | 0.0018052 | 0.013751 | 0.012136 | -0.0083355 | 0.030443 | -0.0035056 | -79.1061 | 0.059509 | -120.6802 | 0.21057 | -108.2428 | -118.1763 | -118.6981 | 0.091553 | -0.009155 | 0.045776 | 0.09613 | 0.16479 | 0.11444 | 0.19684 | -0.004578 | -0.19226 | -0.041199 | 12.4329 | 1.9775 | 2.4994 | 1.9821 | 2.504 | 120.7214 | -0.26093 | -0.15564 | 120.8405 | 120.8725 | 120.7901 | 0.15106 | 0.068665 | 12.4374 | 120.8908 | 0.11902 | 0.050354 | 120.7397 | -0.054931 | 120.7352 | 120.6665 | -120.932 | -0.20599 | 120.8862 | 120.7718 | 41.5695 | 120.7672
2576.75 | 121.0876 | -120.6528 | 0.25635 | -0.009308 | 6.9833 | 0.086408 | 0.060015 | 0.0050544 | 0.0092669 | 0.011732 | 0.0055543 | 0.0015914 | 0.012897 | 0.018117 | -0.0066265 | 0.029803 | -0.0037192 | -79.1382 | 0.073242 | -120.7169 | 0.20142 | -107.8949 | -118.1122 | -118.5471 | 0.09613 | 0.009155 | 0.041199 | 0.1236 | 0.17853 | 0.10529 | 0.21973 | -0.064087 | -0.18311 | -0.054932 | 12.7579 | 2.1057 | 2.5406 | 2.1698 | 2.6047 | 120.694 | -0.24719 | -0.13275 | 120.8313 | 120.8725 | 120.7581 | 0.17853 | 0.064087 | 12.822 | 120.9183 | 0.13733 | 0.082397 | 120.7901 | -0.032044 | 120.726 | 120.6619 | -120.9732 | -0.21515 | 120.8542 | 120.7764 | 41.5146 | 120.7489
2578.4375 | 121.2479 | -120.7214 | 0.25177 | -0.009308 | 6.9795 | 0.086195 | 0.061083 | 0.00035457 | 0.0079853 | 0.013868 | 0.0025025 | 0.0009506 | 0.016742 | 0.01235 | -0.010258 | 0.028521 | -0.0045736 | -79.1382 | 0.073242 | -120.7169 | 0.20142 | -107.4417 | -117.9245 | -118.6203 | 0.12817 | 0.009155 | 0.054932 | 0.10986 | 0.2243 | 0.14191 | 0.19226 | 0.004578 | -0.17853 | -0.050354 | 13.2797 | 2.1011 | 2.7969 | 2.0966 | 2.7924 | 120.7764 | -0.24261 | -0.14191 | 120.9457 | 120.9137 | 120.8633 | 0.13733 | 0.086975 | 13.2751 | 120.9183 | 0.16937 | 0.054931 | 120.7901 | -0.045777 | 120.7947 | 120.7306 | -120.9686 | -0.19684 | 120.9229 | 120.8313 | 41.5833 | 120.8496
2580.1875 | 121.2341 | -120.7443 | 0.2655 | -0.0016785 | 6.9795 | 0.087049 | 0.060442 | 0.00099557 | 0.012258 | 0.011946 | 0.0025025 | 0.0018052 | 0.011188 | 0.0089316 | -0.0074811 | 0.026812 | -0.0022238 | -79.1199 | 0.073242 | -120.7397 | 0.1831 | -107.0572 | -117.7917 | -118.5471 | 0.09613 | 0.009155 | 0.054932 | 0.10529 | 0.19226 | 0.12817 | 0.21057 | 0.004578 | -0.19226 | -0.082398 | 13.6871 | 2.1973 | 2.9526 | 2.1927 | 2.948 | 120.7993 | -0.25635 | -0.16022 | 120.9366 | 120.9549 | 120.8725 | 0.15564 | 0.073242 | 13.6826 | 120.9229 | 0.13733 | 0.050354 | 120.813 | -0.045777 | 120.8176 | 120.7535 | -121.0052 | -0.21057 | 120.9274 | 120.8496 | 41.6245 | 120.8405
2581.8906 | 121.2524 | -120.7077 | 0.25177 | -0.0016785 | 6.9825 | 0.087477 | 0.063006 | -0.001568 | 0.013753 | 0.013655 | -0.00054933 | 0.0028732 | 0.012256 | 0.012136 | -0.0066265 | 0.028307 | -0.0020102 | -79.0375 | 0.064087 | -120.7397 | 0.21057 | -106.6727 | -117.7094 | -118.4326 | 0.11902 | 0.004578 | 0.064087 | 0.11902 | 0.16479 | 0.10986 | 0.21515 | -0.032043 | -0.18768 | -0.041199 | 14.035 | 2.2751 | 2.9984 | 2.3071 | 3.0304 | 120.7718 | -0.24719 | -0.13275 | 120.8725 | 120.9229 | 120.8176 | 0.15106 | 0.045776 | 14.0671 | 120.9503 | 0.10071 | 0.054932 | 120.8038 | -0.059509 | 120.7718 | 120.7123 | -120.9915 | -0.18768 | 120.9183 | 120.8267 | 41.6702 | 120.8267
2583.6406 | 120.9915 | -120.6802 | 0.33417 | -0.0016785 | 6.9814 | 0.088758 | 0.063433 | -0.0019952 | 0.012899 | 0.013014 | 0.0025025 | 0.0028732 | 0.013751 | 0.011281 | -0.012822 | 0.026598 | -0.00030119 | -78.7354 | 0.091553 | -120.7947 | 0.16937 | -106.3568 | -117.5949 | -118.3411 | -0.013733 | 0.032043 | 0.027466 | -0.022888 | 0.059509 | 0.018311 | 0.091553 | -0.11444 | -0.24261 | -0.16479 | 14.3234 | 2.3392 | 3.0853 | 2.4536 | 3.1998 | 120.7077 | -0.30212 | -0.35706 | 120.7397 | 120.7718 | 120.6985 | 0.064087 | -0.009155 | 14.4379 | 120.9641 | 0.032043 | -0.050354 | 120.8862 | 0.004577 | 120.7718 | 120.7123 | -121.1288 | -0.3067 | 120.8496 | 120.6573 | 41.9449 | 120.6665
2585.3906 | 121.1929 | -120.7535 | 0.31128 | -0.0016785 | 6.9844 | 0.089826 | 0.06322 | -0.0017816 | 0.014821 | 0.01515 | -0.00054933 | 0.0028732 | 0.01311 | 0.012777 | -0.010686 | 0.025103 | -0.0035056 | -78.6072 | 0.10986 | -120.7718 | 0.2243 | -105.8441 | -117.4118 | -118.222 | 0.045776 | 0 | 0.036621 | 0.032043 | 0.1236 | 0.064087 | 0.14648 | -0.018311 | -0.20142 | -0.086975 | 14.9094 | 2.5314 | 3.3417 | 2.5497 | 3.36 | 120.7901 | -0.31128 | -0.27924 | 120.8771 | 120.9 | 120.8176 | 0.10986 | 0.027466 | 14.9277 | 120.9961 | 0.086975 | -0.004578 | 120.8817 | -0.036621 | 120.8633 | 120.7535 | -121.0831 | -0.27466 | 120.9778 | 120.7855 | 42.1463 | 120.7993
2587.1406 | 121.2753 | -120.7214 | 0.28839 | 0.005951 | 6.9833 | 0.093458 | 0.062579 | 0.0022772 | 0.015035 | 0.019423 | 0.0025025 | 0.0020188 | 0.01311 | 0.016408 | -0.0051313 | 0.027239 | -0.003292 | -78.6896 | 0.10529 | -120.7581 | 0.24719 | -105.3864 | -117.2836 | -118.0756 | 0.11444 | -0.004578 | 0.045776 | 0.10071 | 0.18768 | 0.1236 | 0.19684 | -0.036621 | -0.18311 | -0.041199 | 15.3351 | 2.6459 | 3.4378 | 2.6825 | 3.4744 | 120.7672 | -0.29297 | -0.18768 | 120.9091 | 120.9183 | 120.845 | 0.15106 | 0.07782 | 15.3717 | 121.0052 | 0.14191 | 0.054932 | 120.8633 | -0.050354 | 120.8267 | 120.7169 | -121.0464 | -0.24262 | 120.9686 | 120.8221 | 42.0319 | 120.8359
2588.8281 | 121.2616 | -120.7764 | 0.3067 | -0.009308 | 6.9842 | 0.091322 | 0.062151 | 0.00014097 | 0.013753 | 0.017073 | -0.0036011 | 0.0015914 | 0.011615 | 0.0050864 | -0.010686 | 0.029375 | -0.0037192 | -79.2847 | 0.091553 | -120.7809 | 0.26093 | -105.0934 | -117.1417 | -117.9382 | 0.086975 | 0.004578 | 0.041199 | 0.073242 | 0.16479 | 0.10529 | 0.19684 | -0.004578 | -0.21515 | -0.045777 | 15.683 | 2.8381 | 3.6346 | 2.8427 | 3.6392 | 120.8176 | -0.30212 | -0.23346 | 120.9412 | 120.9732 | 120.8817 | 0.15564 | 0.064087 | 15.6876 | 121.0419 | 0.1236 | 0.032043 | 120.8725 | -0.036621 | 120.8679 | 120.7809 | -121.0876 | -0.2655 | 121.0373 | 120.8496 | 41.4917 | 120.8633
2590.5781 | 121.1014 | -120.5841 | 0.32044 | 0.005951 | 6.9848 | 0.093672 | 0.06322 | -7.2628e-05 | 0.017385 | 0.014723 | 0.0025025 | 0.002446 | 0.01311 | 0.004659 | -0.010899 | 0.026385 | -0.0056418 | -80.0583 | 0.15106 | -120.8221 | 0.10986 | -104.9332 | -117.1555 | -117.8696 | -0.068665 | 0.050354 | 0.018311 | -0.027466 | 0.050354 | -0.018311 | 0.10071 | -0.23804 | -0.16937 | -0.21057 | 15.6509 | 2.7145 | 3.4286 | 2.9526 | 3.6667 | 120.6024 | -0.27008 | -0.3479 | 120.6345 | 120.6848 | 120.5658 | 0.082397 | -0.036622 | 15.889 | 120.932 | 0.032043 | -0.045777 | 120.9732 | 0.032043 | 120.7352 | 120.6345 | -121.1426 | -0.30212 | 120.694 | 120.5566 | 40.5258 | 120.5154
2592.3281 | 121.3074 | -120.7718 | 0.3067 | 0.005951 | 6.9829 | 0.095167 | 0.064288 | 0.0037726 | 0.015035 | 0.021345 | 0.0055543 | 0.0011642 | 0.013751 | 0.017904 | -0.011967 | 0.028948 | -0.0022238 | -80.5023 | 0.09613 | -120.7993 | 0.2655 | -104.3106 | -116.9083 | -117.6041 | 0.11444 | -0.009155 | 0.059509 | 0.086975 | 0.20142 | 0.15106 | 0.20142 | -0.027465 | -0.21057 | -0.041199 | 16.4612 | 3.1677 | 3.8635 | 3.1952 | 3.891 | 120.8313 | -0.31586 | -0.21973 | 120.9732 | 120.9732 | 120.9229 | 0.14191 | 0.091553 | 16.4886 | 121.0648 | 0.14191 | 0.027466 | 120.8954 | -0.068664 | 120.8679 | 120.7626 | -121.106 | -0.24719 | 121.0373 | 120.8588 | 40.2695 | 120.8862
2594.0156 | 121.0098 | -120.5429 | 0.30212 | 0.005951 | 6.9842 | 0.094312 | 0.063647 | -0.00092703 | 0.018239 | 0.0222 | -0.00054933 | 0.0022324 | 0.012256 | 0.0085044 | -0.0070539 | 0.027453 | -0.0011558 | -81.0013 | 0.11444 | -120.5978 | 0.09613 | -104.0176 | -116.8442 | -117.247 | -0.09613 | 0.041199 | 0.004578 | 0 | 0.027466 | -0.032043 | 0.10071 | -0.054931 | -0.18768 | -0.20599 | 16.5253 | 3.2959 | 3.6987 | 3.3508 | 3.7537 | 120.5475 | -0.26093 | -0.30212 | 120.5704 | 120.6436 | 120.5109 | 0.09613 | -0.036621 | 16.5802 | 120.694 | 0.022888 | -0.004578 | 120.7123 | 0.036621 | 120.6573 | 120.5841 | -120.9 | -0.29755 | 120.639 | 120.5429 | 39.5416 | 120.4468
2595.7656 | 121.17 | -120.694 | 0.31586 | -0.0016785 | 6.9842 | 0.098371 | 0.062365 | -0.00071343 | 0.014821 | 0.020491 | -0.00054933 | 0.0005234 | 0.012469 | 0.0089316 | -0.010258 | 0.028521 | -0.0030784 | -81.134 | 0.091553 | -120.694 | 0.21057 | -103.5233 | -116.6565 | -117.2562 | 0.059509 | 0.009155 | 0.027466 | 0.059509 | 0.13733 | 0.068665 | 0.15106 | 0 | -0.2243 | -0.10529 | 17.1707 | 3.4378 | 4.0375 | 3.4378 | 4.0375 | 120.7214 | -0.3067 | -0.25635 | 120.8313 | 120.845 | 120.7626 | 0.1236 | 0.041199 | 17.1707 | 120.9045 | 0.10986 | 0.032043 | 120.7855 | -0.018311 | 120.7855 | 120.7031 | -121.0098 | -0.28839 | 120.9045 | 120.7535 | 39.5599 | 120.7535
2597.4688 | 121.2296 | -120.7214 | 0.28839 | 0.005951 | 6.9846 | 0.10072 | 0.06322 | -0.0034906 | 0.020375 | 0.021132 | 0.0025025 | 9.6204e-05 | 0.013537 | 0.011922 | -0.010258 | 0.02788 | -0.0028646 | -81.1478 | 0.086975 | -120.7489 | 0.20142 | -103.1387 | -116.597 | -117.1371 | 0.07782 | 0.009155 | 0.027466 | 0.091553 | 0.1236 | 0.068665 | 0.16937 | -0.027465 | -0.20142 | -0.086975 | 17.5827 | 3.5843 | 4.1245 | 3.6118 | 4.1519 | 120.7489 | -0.27924 | -0.19684 | 120.845 | 120.8908 | 120.7901 | 0.14191 | 0.041199 | 17.6102 | 120.9503 | 0.09613 | 0.064087 | 120.8359 | -0.018311 | 120.8084 | 120.7306 | -121.0373 | -0.26093 | 120.9229 | 120.813 | 39.5737 | 120.7993
2599.2031 | 121.1563 | -120.7352 | 0.3067 | 0.005951 | 6.9861 | 0.10093 | 0.063647 | 0.0039862 | 0.020589 | 0.023909 | 0.0025025 | 0.0037278 | 0.012469 | 0.0067954 | -0.0072675 | 0.027239 | -0.0054282 | -81.2393 | 0.11902 | -120.7993 | 0.13733 | -102.8 | -116.5558 | -116.954 | -0.027466 | 0.036621 | 0.036621 | 0.013733 | 0.036621 | -0.027466 | 0.09613 | -0.064087 | -0.18768 | -0.16937 | 17.9352 | 3.7811 | 4.1794 | 3.8452 | 4.2435 | 120.7718 | -0.27008 | -0.29297 | 120.7718 | 120.8313 | 120.7077 | 0.059509 | -0.064087 | 17.9993 | 120.9366 | 0 | -0.022888 | 120.9183 | 0 | 120.8542 | 120.7718 | -121.106 | -0.27008 | 120.8725 | 120.7489 | 39.4958 | 120.7077
2600.8906 | 121.3028 | -120.7855 | 0.29755 | -0.016937 | 6.9844 | 0.102 | 0.06386 | -0.001568 | 0.019521 | 0.022841 | -0.00054933 | 0.0015914 | 0.014819 | 0.0091452 | -0.010686 | 0.028734 | -0.001583 | -81.4682 | 0.10986 | -120.7993 | 0.20599 | -102.356 | -116.3361 | -116.7847 | 0.036621 | -0.004578 | 0.036621 | 0.086975 | 0.16479 | 0.11444 | 0.1831 | -0.013733 | -0.18768 | -0.091552 | 18.4296 | 4.0009 | 4.4495 | 4.0146 | 4.4632 | 120.8221 | -0.30212 | -0.21057 | 120.9503 | 120.9686 | 120.9 | 0.14648 | 0.07782 | 18.4433 | 121.0052 | 0.12817 | 0.050354 | 120.9091 | -0.041199 | 120.8954 | 120.7809 | -121.0968 | -0.26092 | 120.9915 | 120.8725 | 39.3173 | 120.8221
2602.6406 | 121.1792 | -120.8221 | 0.32501 | -0.0016785 | 6.9853 | 0.10179 | 0.06621 | 0.0037726 | 0.021444 | 0.026259 | -0.00054933 | 0.0020188 | 0.011615 | 0.01299 | -0.010045 | 0.026812 | -0.00094199 | -81.5598 | 0.14191 | -120.8038 | 0.10071 | -102.0355 | -116.3773 | -116.684 | -0.082397 | 0.036621 | 0.004578 | -0.004578 | 0.027466 | -0.041199 | 0.091553 | 0.018311 | -0.18311 | -0.2243 | 18.7866 | 4.1382 | 4.4449 | 4.1199 | 4.4266 | 120.8267 | -0.28839 | -0.32959 | 120.8496 | 120.9137 | 120.7809 | 0.086975 | -0.045777 | 18.7683 | 120.9045 | 0.022888 | -0.009156 | 120.9457 | 0.032043 | 120.9641 | 120.8588 | -121.1288 | -0.32043 | 120.9229 | 120.8176 | 39.2624 | 120.7397
2604.3906 | 120.9869 | -119.5221 | 1.3916 | -0.0016785 | 6.9863 | 0.10264 | 0.063006 | 0.00035457 | 0.021444 | 0.026259 | -0.00054933 | 0.0033004 | 0.010974 | 0.018758 | -0.0076947 | 0.02788 | -0.003292 | -81.3263 | 0.082397 | -120.7718 | 0.44861 | -100.8728 | -115.2374 | -115.7043 | 0.013733 | 0.022888 | 0.036621 | 0.045776 | 0.11902 | 0.068665 | 0.15106 | -1.2497 | -1.3092 | -0.94299 | 18.6493 | 3.8177 | 4.2847 | 5.0674 | 5.5344 | 119.5587 | -1.3687 | -1.3458 | 119.6411 | 119.6732 | 119.5908 | 0.11444 | 0.032044 | 19.899 | 121.2204 | 0.082398 | 0.009155 | 120.8542 | -0.013733 | 119.6045 | 119.545 | -122.1634 | -1.355 | 119.9707 | 119.5679 | 38.1958 | 119.5358
2606.1406 | 118.2587 | -86.2015 | 31.6498 | 0.005951 | 6.9902 | 0.092176 | 0.065142 | 0.0014228 | 0.015889 | 0.021132 | -0.00054933 | 0.0020188 | 0.014605 | 0.014272 | -0.0094037 | 0.029162 | -0.00051479 | -57.3212 | 31.4255 | -86.2747 | 31.9244 | -71.8781 | -82.6263 | -82.9285 | 0 | -0.018311 | 0.027466 | 0.036621 | 0.09613 | 0.036621 | 0.1236 | -0.073242 | -0.2243 | 0.27466 | 14.3234 | 3.273 | 3.5751 | 3.3463 | 3.6484 | 86.2289 | -31.6681 | -31.6132 | 86.2976 | 86.3251 | 86.2381 | 0.09613 | 0.009155 | 14.3967 | 118.1992 | 0.068664 | 0.009155 | 117.7002 | -0.045777 | 117.627 | 86.1832 | -117.9245 | -31.6223 | 118.1259 | 86.2381 | 28.8803 | 86.2015
2607.8906 | 121.0556 | -120.5338 | 0.27924 | 0.005951 | 6.9878 | 0.10585 | 0.065783 | 0.0061224 | 0.024434 | 0.033308 | -0.00054933 | 0.003514 | 0.013324 | 0.0082906 | -0.0081219 | 0.027453 | 0.00098061 | -81.5964 | 0.13733 | -120.6207 | 0.15564 | -100.3143 | -115.6265 | -115.48 | -0.018311 | 0.027466 | 0.018311 | 0.050354 | 0.086975 | 0.036621 | 0.13733 | -0.086976 | -0.14191 | -0.1236 | 20.2194 | 5.0537 | 4.9072 | 5.1407 | 4.9942 | 120.5521 | -0.25177 | -0.22888 | 120.6207 | 120.6711 | 120.5704 | 0.11902 | 0.01831 | 20.3064 | 120.7764 | 0.068664 | 0.032043 | 120.7581 | 0.009155 | 120.6711 | 120.5612 | -120.9 | -0.26092 | 120.6894 | 120.5841 | 38.9374 | 120.5154
2609.6406 | 121.0785 | -120.6528 | 0.31128 | 0.005951 | 6.9876 | 0.11012 | 0.064501 | 0.0020636 | 0.025716 | 0.034376 | 0.0025025 | 0.0026596 | 0.011615 | 0.010427 | -0.0068403 | 0.028094 | -0.0052146 | -81.3721 | 0.13733 | -120.694 | 0.11902 | -99.9481 | -115.6265 | -114.9765 | -0.086975 | 0.054932 | 0.018311 | -0.004578 | -0.018311 | -0.050354 | 0.086975 | -0.041199 | -0.17395 | -0.19226 | 20.7047 | 5.6763 | 5.0262 | 5.7175 | 5.0674 | 120.6711 | -0.25635 | -0.31586 | 120.6345 | 120.7397 | 120.6024 | 0.068664 | -0.068665 | 20.7458 | 120.813 | -0.036622 | -0.022889 | 120.8313 | 0.036621 | 120.7901 | 120.7077 | -121.0052 | -0.29297 | 120.7718 | 120.6482 | 39.2807 | 120.5658
2611.3906 | 120.845 | -120.3323 | 0.39825 | -0.0016785 | 6.9863 | 0.11247 | 0.068774 | -0.00092703 | 0.027639 | 0.24095 | 0.0025025 | 0.002446 | 0.011828 | 0.011495 | -0.010045 | 0.028521 | -0.0052146 | -81.1569 | 0.21515 | -120.3415 | 0.24261 | -96.7209 | -115.1093 | -83.345 | -0.027466 | 0.036621 | 0.018311 | 0.027466 | 0.045776 | -0.036621 | 0.11444 | -0.009156 | -0.1831 | -0.15564 | 23.6115 | 36.9873 | 5.2231 | 36.9965 | 5.2322 | 120.3506 | -0.36163 | -0.37079 | 120.3781 | 120.4468 | 120.2957 | 0.09613 | -0.054932 | 23.6206 | 120.5841 | 0.027465 | 0.009155 | 120.5566 | 0.01831 | 120.5475 | 120.369 | -120.7397 | -0.37994 | 120.575 | 120.3598 | 39.1754 | 120.3049
2613.0781 | 121.0785 | -120.5154 | 0.31128 | -0.0016785 | 6.9808 | 0.13148 | 0.064501 | 0.00035457 | -0.0088911 | 0.079023 | -0.0036011 | 0.0011642 | 0.013751 | 0.018545 | -0.0085491 | 0.028094 | 0.00033961 | -52.121 | 0.11444 | -120.5292 | 0.21515 | -84.5627 | -26.4908 | -26.358 | 0.036621 | 0.013733 | 0.032043 | 0.091553 | 0.15106 | 0.10529 | 0.17395 | -0.013733 | -0.19684 | -0.09613 | 35.9528 | 94.1574 | 94.0247 | 94.1711 | 94.0384 | 120.5475 | -0.29755 | -0.21973 | 120.6665 | 120.6894 | 120.6207 | 0.14191 | 0.073243 | 35.9665 | 120.7443 | 0.11902 | 0.05951 | 120.6436 | -0.01831 | 120.6299 | 120.5292 | -120.8405 | -0.27924 | 120.7306 | 120.607 | 68.3945 | 120.5521
2614.8281 | 120.9869 | -120.6253 | 0.33875 | 0.005951 | 6.9814 | 0.13362 | 0.06621 | 0.0024908 | -0.0073957 | 0.080946 | 0.0025025 | 0.003514 | 0.011828 | 0.001882 | -0.0094037 | 0.029589 | -0.0011558 | -51.7136 | 0.16022 | -120.6207 | 0.12817 | -84.201 | -26.1932 | -27.2186 | -0.091553 | 0.041199 | 0.013733 | 0 | 0.036621 | -0.036621 | 0.09613 | 0.004577 | -0.17853 | -0.21057 | 36.4243 | 93.4067 | 94.4321 | 93.4021 | 94.4275 | 120.639 | -0.29755 | -0.33875 | 120.6619 | 120.7214 | 120.5887 | 0.082397 | -0.050354 | 36.4197 | 120.7489 | 0.022888 | -0.013733 | 120.7809 | 0.027466 | 120.7855 | 120.6665 | -120.9595 | -0.32501 | 120.7535 | 120.6253 | 68.9117 | 120.5338
2616.5 | 121.1517 | -120.5933 | 0.28381 | -0.0016785 | 6.984 | 0.13768 | 0.065783 | 0.0041998 | -0.0084637 | 0.077528 | 0.0055543 | 0.0015914 | 0.013324 | 0.010854 | -0.0051313 | 0.029375 | 0.00012601 | -51.6724 | 0.11444 | -120.6207 | 0.28381 | -83.6929 | -26.0925 | -28.1891 | 0.10986 | -0.004578 | 0.054932 | 0.13275 | 0.18768 | 0.12817 | 0.1831 | -0.027466 | -0.16937 | 0 | 36.9003 | 92.4042 | 94.5007 | 92.4316 | 94.5282 | 120.6482 | -0.28839 | -0.15106 | 120.7809 | 120.7764 | 120.7214 | 0.12817 | 0.073242 | 36.9278 | 120.9045 | 0.13275 | 0.077819 | 120.7352 | -0.05951 | 120.7077 | 120.5887 | -120.9045 | -0.22888 | 120.8771 | 120.726 | 68.9209 | 120.7031
2618.25 | 121.1105 | -120.6802 | 0.33417 | 0.005951 | 6.9844 | 0.13704 | 0.065997 | 0.00014097 | -0.0082501 | 0.079023 | -0.00054933 | 0.0045822 | 0.015674 | 0.0091452 | -0.010686 | 0.028521 | -0.0035056 | -51.7822 | 0.16937 | -120.6894 | 0.17395 | -83.3267 | -26.1749 | -27.9968 | -0.036621 | 0.027466 | 0.013733 | 0.027466 | 0.10071 | 0.018311 | 0.13275 | -0.009155 | -0.16479 | -0.16022 | 37.3535 | 92.6834 | 94.5053 | 92.6926 | 94.5145 | 120.694 | -0.3067 | -0.3067 | 120.7809 | 120.813 | 120.6985 | 0.11902 | 0.004578 | 37.3627 | 120.8633 | 0.086975 | 0.013733 | 120.8588 | 0.013733 | 120.8496 | 120.7077 | -121.0236 | -0.32043 | 120.8542 | 120.7077 | 68.898 | 120.6436
2619.9531 | 121.1975 | -120.6482 | 0.33417 | -0.009308 | 6.9836 | 0.13939 | 0.063006 | 0.00035457 | -0.0071821 | 0.078596 | -0.00054933 | 0.0013778 | 0.012469 | 0.014486 | -0.012181 | 0.028734 | 0.0014078 | -52.1027 | 0.12817 | -120.6894 | 0.28381 | -82.8598 | -26.0376 | -27.713 | 0.064087 | -0.004578 | 0.045776 | 0.10071 | 0.1831 | 0.12817 | 0.19684 | -0.041199 | -0.20599 | -0.050354 | 37.7884 | 92.9352 | 94.6106 | 92.9764 | 94.6518 | 120.694 | -0.33875 | -0.23346 | 120.8313 | 120.845 | 120.7764 | 0.15106 | 0.082398 | 37.8296 | 120.9732 | 0.13733 | 0.054932 | 120.8176 | -0.050354 | 120.7764 | 120.6436 | -121.0236 | -0.28839 | 120.932 | 120.7489 | 68.5455 | 120.7123
2621.7031 | 121.0327 | -118.7393 | 2.4261 | -0.009308 | 6.9825 | 0.38142 | 0.064288 | 0.003559 | -0.0106 | 0.07411 | 0.0025025 | 0.0030868 | 0.012683 | 0.017049 | -0.0083355 | 0.029375 | -0.0013694 | -58.9508 | 1.8448 | -118.6569 | 2.1744 | -84.2102 | -32.8949 | -29.9881 | 0.064087 | 0.004578 | 0.032043 | 0.07782 | 0.16022 | 0.10529 | 0.16479 | 0.082398 | -0.58136 | -0.25177 | 34.5291 | 88.7512 | 85.8444 | 88.6688 | 85.762 | 118.7714 | -2.4216 | -2.3483 | 118.8995 | 118.9041 | 118.8446 | 0.13275 | 0.073243 | 34.4467 | 120.8313 | 0.12817 | 0.045777 | 120.5017 | -0.027465 | 120.5841 | 118.7439 | -121.0831 | -2.3941 | 120.9137 | 118.8171 | 59.7885 | 118.8034
2623.4531 | 121.0373 | -120.3415 | 0.48065 | -0.0016785 | 6.9827 | 0.56172 | 0.06322 | 0.003559 | -0.0078229 | 0.074965 | -0.0036011 | 0.0015914 | 0.01076 | 0.021535 | -0.0081219 | 0.028307 | 0.00055321 | -62.2971 | 0.29755 | -120.3598 | 0.37079 | -85.675 | -35.6918 | -31.3065 | 0.004578 | 0.013733 | 0.022888 | 0.064087 | 0.1236 | 0.064087 | 0.15106 | -0.01831 | -0.18311 | -0.10986 | 34.6664 | 89.035 | 84.6497 | 89.0533 | 84.668 | 120.3644 | -0.46692 | -0.41657 | 120.4651 | 120.4926 | 120.4056 | 0.12817 | 0.041199 | 34.6848 | 120.7306 | 0.10071 | 0.041199 | 120.6573 | -0.009155 | 120.639 | 120.3552 | -120.8405 | -0.45776 | 120.7123 | 120.4056 | 58.0444 | 120.3461
2625.125 | 121.0556 | -120.2866 | 0.60425 | -0.009308 | 6.9836 | 0.78602 | 0.065569 | 0.0037726 | -0.0088911 | 0.07411 | 0.0055543 | 0.0033004 | 0.011615 | 0.0065816 | -0.0089765 | 0.027666 | -0.0020102 | -61.1298 | 0.42114 | -120.3049 | 0.4303 | -82.7454 | -34.3689 | -30.2994 | -0.022888 | 0.050354 | 0.009155 | 0.036621 | 0.10986 | 0.018311 | 0.13275 | -0.018311 | -0.18311 | -0.17395 | 37.5412 | 89.9872 | 85.9177 | 90.0055 | 85.936 | 120.2957 | -0.55389 | -0.56763 | 120.3964 | 120.4193 | 120.3049 | 0.1236 | 0.009156 | 37.5595 | 120.7352 | 0.10071 | 0.027466 | 120.726 | 0.041199 | 120.7077 | 120.3369 | -120.9091 | -0.59509 | 120.7169 | 120.3232 | 59.1568 | 120.2637
2626.875 | 120.9915 | -119.9753 | 0.88348 | -0.0016785 | 6.9848 | 1.5587 | 0.066851 | 0.00035457 | -0.0069683 | 0.075392 | -0.00054933 | 0.0045822 | 0.012897 | 0.0055136 | -0.0059857 | 0.027239 | -0.0024374 | -63.1851 | 0.79193 | -119.8471 | 1.4236 | -82.0404 | -35.9482 | -31.6406 | -0.050354 | 0.036621 | 0.036621 | 0.013733 | 0.045776 | -0.027466 | 0.10986 | 0.12817 | -0.091553 | 0.54016 | 37.9349 | 88.3347 | 84.0271 | 88.2065 | 83.8989 | 120.0119 | -0.84686 | -0.86975 | 120.0211 | 120.0851 | 119.9478 | 0.073242 | -0.064087 | 37.8067 | 121.2708 | 0.009155 | -0.022888 | 120.639 | 0 | 120.7672 | 120.0119 | -120.7306 | -0.84686 | 121.3989 | 119.989 | 56.7902 | 119.9249
2628.6406 | 120.7031 | -119.5358 | 1.0345 | -0.009308 | 6.9855 | 1.9868 | 0.067492 | -0.00092703 | -0.0091047 | 0.063215 | 0.0025025 | 0.0030868 | 0.012042 | 0.0067954 | -0.010045 | 0.028094 | 0.00012601 | -69.072 | 0.85602 | -119.4077 | 0.85602 | -93.4525 | -41.8991 | -42.0593 | -0.068665 | 0.050354 | 0.009155 | 0.018311 | 0.073242 | 0.009155 | 0.10529 | 0.12817 | -0.17853 | -0.17853 | 26.0834 | 77.4765 | 77.6367 | 77.3483 | 77.5085 | 119.545 | -0.98419 | -1.0162 | 119.6091 | 119.6411 | 119.545 | 0.096131 | 0 | 25.9552 | 120.2637 | 0.064087 | 0.009156 | 120.2637 | 0.041199 | 120.3918 | 119.5862 | -120.4422 | -1.0254 | 120.3918 | 119.5541 | 50.4639 | 119.4672
2630.3281 | 120.7901 | -119.0781 | 1.4465 | -0.0016785 | 6.9859 | 3.0705 | 0.067706 | 0.0033454 | -0.0082501 | 0.061079 | -0.0036011 | 0.0039414 | 0.012256 | 0.012136 | -0.0074811 | 0.030443 | -0.0054282 | -70.3857 | 1.2817 | -118.8904 | 1.3275 | -94.281 | -43.5379 | -43.8446 | 0.036621 | 0.009155 | 0.041199 | 0.10529 | 0.15106 | 0.091553 | 0.19226 | 0.18768 | -0.1648 | -0.11902 | 24.7971 | 75.2335 | 75.5402 | 75.0458 | 75.3525 | 119.1193 | -1.4374 | -1.3412 | 119.2291 | 119.2703 | 119.1696 | 0.15106 | 0.050354 | 24.6094 | 120.2179 | 0.10986 | 0.064087 | 120.1721 | -0.032044 | 120.3598 | 119.0872 | -120.3369 | -1.4053 | 120.4056 | 119.1834 | 48.6923 | 119.1147
2632.0781 | 120.6619 | -118.5562 | 1.9409 | 0.005951 | 6.9883 | 4.2931 | 0.068774 | 0.0016364 | -0.0084637 | 0.042494 | -0.00054933 | 0.0037278 | 0.012469 | 0.011709 | -0.0053449 | 0.028734 | -0.002651 | -75.7919 | 1.7853 | -118.2129 | 1.7899 | -97.8241 | -51.2466 | -68.6554 | -0.018311 | 0.022888 | 0.032043 | 0.059509 | 0.086975 | 0.032043 | 0.15564 | 0.34332 | -0.15564 | -0.15106 | 20.7321 | 49.9008 | 67.3096 | 49.5575 | 66.9662 | 118.5883 | -1.918 | -1.8814 | 118.6432 | 118.7119 | 118.5883 | 0.1236 | 0 | 20.3888 | 120.0027 | 0.054932 | 0.027466 | 119.9982 | -0.009155 | 120.3415 | 118.5791 | -120.1538 | -1.9089 | 120.3461 | 118.6157 | 42.7643 | 118.5379
2633.8281 | 120.7031 | -116.8671 | 3.3096 | -0.009308 | 6.9857 | 7.1195 | 0.06621 | -0.0037042 | -0.0086773 | 0.05467 | 0.0025025 | 0.0022324 | 0.013537 | 0.0053 | -0.0091901 | 0.026385 | -0.003292 | -64.4302 | 2.9984 | -116.7297 | 2.9755 | -87.41 | -40.2695 | -51.5533 | -0.045776 | 0.041199 | 0.018311 | -0.022888 | 0.12817 | 0.004578 | 0.041199 | 0.13733 | -0.31128 | -0.33417 | 29.4571 | 65.3137 | 76.5976 | 65.1764 | 76.4603 | 116.8854 | -3.2684 | -3.3325 | 116.9952 | 116.9083 | 116.8716 | 0.022888 | -0.013733 | 29.3198 | 119.7052 | 0.10986 | -0.041199 | 119.7281 | 0.022888 | 119.8654 | 116.9083 | -120.0394 | -3.2913 | 119.8425 | 116.8442 | 52.4368 | 116.8213
2635.5625 | 120.3827 | -116.7252 | 3.4195 | 0.005951 | 6.9964 | 7.1195 | 0.071978 | 0.0048408 | 0.030202 | 0.10209 | -0.00054933 | 0.0037278 | 0.013324 | 0.0050864 | -0.0085491 | 0.030016 | -0.0039328 | -86.4075 | 3.2776 | -116.011 | 3.0853 | -104.3793 | -108.9294 | -100.5798 | 0.032043 | 0.054932 | 0.054932 | 0.064087 | 0.14191 | 0.068665 | 0.16937 | 0.71411 | -0.14191 | -0.33417 | 12.3459 | 16.1453 | 7.7957 | 15.4312 | 7.0816 | 116.7801 | -3.3646 | -3.3554 | 116.8671 | 116.8945 | 116.7938 | 0.11444 | 0.013733 | 11.6318 | 119.0964 | 0.086975 | 0.009155 | 119.2886 | 0 | 120.0027 | 116.7801 | -119.4305 | -3.3646 | 119.8105 | 116.7892 | 30.3177 | 116.7572
2637.2344 | 119.7739 | -110.4584 | 9.0271 | -0.0016785 | 6.997 | 7.1195 | 0.070056 | -0.0028498 | 0.032979 | 0.1775 | 0.0025025 | -0.0001174 | 0.012683 | 0.017904 | -0.0040631 | 0.028948 | -0.00436 | -80.0171 | 8.7433 | -108.8745 | 8.8211 | -95.8649 | -102.887 | -81.5598 | 0.073242 | 0.059509 | 0.10529 | 0.11902 | 0.17395 | 0.10529 | 0.19226 | 1.5839 | -0.28381 | -0.20599 | 14.5935 | 28.8986 | 7.5714 | 27.3148 | 5.9875 | 110.5637 | -8.9676 | -8.9081 | 110.6323 | 110.6506 | 110.5637 | 0.086975 | 0 | 13.0096 | 117.6956 | 0.068664 | 0.013733 | 117.6178 | -0.045777 | 119.2017 | 110.5179 | -117.9016 | -8.9218 | 119.2795 | 110.5774 | 30.4413 | 110.5316
2638.9219 | 120.8267 | -120.314 | 0.23804 | 0.005951 | 6.9769 | 0.019117 | -0.0059942 | -0.00028623 | -0.0073957 | -0.0015124 | -0.0066527 | 0.0015914 | 0.012042 | 0.0085044 | -0.0081219 | 0.028521 | -0.0013694 | 0.082397 | 0.082397 | 0.022888 | 0.19684 | 0.21057 | 0.050354 | 0.086975 | 0.10071 | 0.004578 | 0.059509 | 0.09613 | 0.14648 | 0.10071 | 0.17395 | 120.3369 | -0.15564 | -0.041199 | 120.5246 | 120.401 | 120.3644 | 0.064087 | 0.027466 | 120.3735 | -0.23346 | -0.14191 | 120.4605 | 120.488 | 120.4147 | 0.11444 | 0.041199 | 0.18768 | 0.17395 | 0.086975 | 0.036621 | 0.059509 | -0.054931 | 120.3964 | 120.3186 | -0.21515 | -0.17853 | 120.5109 | 120.4102 | 120.3964 | 120.4147
2640.6562 | 120.9686 | -120.4468 | 0.23804 | -0.009308 | 6.9765 | 0.016126 | -0.0049262 | 0.0044134 | -0.0091047 | -0.002367 | 0.0025025 | 0.0020188 | 0.014178 | 0.0082906 | -0.0089765 | 0.029803 | 0.0016214 | 0.045776 | 0.086975 | 0.022888 | 0.19684 | 0.19226 | 0.091553 | 0.091553 | 0.09613 | -0.009155 | 0.027466 | 0.10986 | 0.19226 | 0.14648 | 0.20599 | 120.4697 | -0.15106 | -0.041199 | 120.639 | 120.5383 | 120.5383 | 0.068665 | 0.068665 | 120.4742 | -0.24719 | -0.12817 | 120.639 | 120.6528 | 120.5933 | 0.17853 | 0.11902 | 0.16937 | 0.17395 | 0.16479 | 0.082397 | 0.064087 | -0.036621 | 120.5338 | 120.4376 | -0.21515 | -0.21057 | 120.6436 | 120.5566 | 120.4926 | 120.5429
2642.4062 | 117.4393 | -90.8981 | 26.6327 | -0.0016785 | 6.9968 | 0.015913 | 0.016863 | 0.00185 | -0.0082501 | -0.0012988 | -0.015808 | -0.010585 | 0.012683 | 0.00081383 | -0.01389 | 0.024035 | -0.0041464 | 0.33417 | 28.0472 | 0.064087 | 28.1479 | 0.17395 | 0.42114 | 0.10986 | -0.041199 | 0.004578 | -0.009155 | 0.022888 | 0.059509 | 0.018311 | 0.10986 | 90.9622 | 1.4145 | 1.5152 | 91.0721 | 91.008 | 91.3193 | 0.045776 | 0.35706 | 90.889 | -26.6281 | -26.6098 | 90.9576 | 91.008 | 90.9164 | 0.11902 | 0.027466 | 0.10986 | 28.0838 | 0.068664 | 0.032043 | 27.9831 | 0.013733 | 118.9453 | 90.9027 | -26.5686 | -26.6418 | 119.046 | 90.921 | 91.2323 | 90.8569
2644.0938 | 120.7581 | -120.2087 | 0.22888 | -0.009308 | 6.9771 | 0.015486 | -0.005567 | -0.0024224 | -0.0093183 | -0.0012988 | -0.00054933 | 0.0005234 | 0.013751 | 0.018331 | -0.0083355 | 0.026171 | -0.00030119 | 0.068665 | 0.064087 | 0.018311 | 0.21515 | 0.21057 | 0.11902 | 0.091553 | 0.10529 | -0.009155 | 0.041199 | 0.11444 | 0.17853 | 0.14191 | 0.18768 | 120.2271 | -0.16479 | -0.013733 | 120.4193 | 120.3003 | 120.3278 | 0.073242 | 0.10071 | 120.2499 | -0.23804 | -0.11444 | 120.3873 | 120.3964 | 120.3506 | 0.14648 | 0.10071 | 0.19226 | 0.19684 | 0.13733 | 0.073242 | 0.045776 | -0.050354 | 120.2728 | 120.1996 | -0.21057 | -0.18768 | 120.4239 | 120.3232 | 120.2774 | 120.314
2645.8281 | 120.7764 | -120.3461 | 0.27008 | 0.005951 | 6.9782 | 0.016981 | -0.0023626 | 0.0020636 | -0.0086773 | -0.0012988 | -0.00054933 | 0.0003098 | 0.011615 | -0.001536 | -0.0091901 | 0.027453 | 0.00098061 | 0.027466 | 0.13275 | -0.018311 | 0.12817 | 0.091553 | 0.018311 | 0.022888 | -0.004578 | 0.050354 | 0.027466 | 0.050354 | 0.086975 | 0.032043 | 0.13733 | 120.3278 | -0.13733 | -0.14191 | 120.4376 | 120.369 | 120.3644 | 0.041199 | 0.036622 | 120.3735 | -0.21973 | -0.21973 | 120.433 | 120.4834 | 120.3781 | 0.10986 | 0.004577 | 0.10986 | 0.14649 | 0.059509 | 0.022888 | 0.15106 | 0.022888 | 120.4788 | 120.3964 | -0.28839 | -0.24262 | 120.4742 | 120.3964 | 120.3735 | 120.3415
2647.5938 | 119.4031 | -116.8076 | 3.3508 | -0.0016785 | 6.9818 | 0.01869 | -0.011121 | -0.0096856 | -0.014659 | -0.0077074 | -0.031067 | -0.0013992 | 0.0084103 | 0.0038046 | 0.036312 | 0.045611 | 0.029179 | 0.10529 | 2.8931 | 0.009155 | 2.71 | 0.13275 | 0.16937 | -0.009155 | 0.013733 | 0.027466 | 0.022888 | 0.045776 | 0.068665 | -0.013733 | 0.09613 | 116.8167 | -0.45776 | -0.64087 | 116.9403 | 116.7984 | 116.9769 | -0.01831 | 0.16022 | 116.8304 | -3.3234 | -3.3051 | 116.8762 | 116.9037 | 116.7938 | 0.073242 | -0.036621 | 0.1236 | 2.7008 | 0.045777 | 0.022888 | 2.8839 | 0.004578 | 119.7006 | 116.835 | -3.3417 | -3.3279 | 119.5175 | 116.8533 | 116.9128 | 116.8213
2649.2812 | 116.6382 | -86.6592 | 29.7867 | 0.11276 | 6.9746 | 0.014631 | 0.009173 | -0.014385 | -0.0069683 | -0.0083484 | -0.18671 | -0.0093032 | 0.01311 | 0.011281 | -0.0074811 | 0.023394 | -0.01205 | 0.27466 | 30.7571 | 0.091553 | 30.9174 | 0.14191 | 0.41199 | -0.1236 | -0.09613 | -0.082397 | 0.3067 | -0.018311 | -0.013733 | -0.091553 | -0.068665 | 86.7508 | 0.97046 | 1.1307 | 86.8011 | 86.5356 | 87.0712 | -0.21515 | 0.32043 | 86.9659 | -29.8691 | -29.805 | 86.6455 | 86.5906 | 86.5677 | -0.37537 | -0.39825 | 0.050354 | 30.8258 | -0.32043 | -0.32501 | 30.6656 | -0.3891 | 117.4164 | 86.5768 | -29.6951 | -29.48 | 117.5766 | 86.6409 | 86.9339 | 86.5631
2651.0312 | 119.5953 | -119.1238 | 0.22888 | -0.016937 | 6.9812 | 0.021467 | -0.0040716 | 0.011677 | -0.01295 | -0.015825 | 0.054382 | 0.030858 | 0.0062741 | 0.010854 | -0.016453 | 0.015063 | -0.016109 | -0.064087 | 0.09613 | 0.036621 | -0.10986 | -0.20142 | -0.46234 | 0.082397 | -0.091553 | -0.3067 | -0.09613 | -0.027466 | -0.27466 | -0.19226 | 0.07782 | 119.1605 | -0.13275 | -0.33875 | 118.9224 | 119.2062 | 118.6615 | 0.045776 | -0.49896 | 119.0277 | -0.53558 | -0.25635 | 118.8492 | 119.2017 | 118.9316 | 0.17395 | -0.096131 | -0.23804 | -0.14648 | -0.17853 | 0.068664 | 0.059509 | -0.21057 | 119.22 | 118.8171 | -0.19226 | -0.32501 | 119.014 | 119.0964 | 119.0598 | 119.0323
2652.7969 | 120.5658 | -120.1721 | 0.24261 | -0.0016785 | 6.9786 | 0.019117 | -0.020734 | -0.032971 | -0.0086773 | -0.013689 | 0.039123 | -0.03622 | 0.011828 | 0.0033774 | -0.020085 | 0.011645 | -0.0082052 | -0.036621 | 0.10071 | 0.004578 | -0.20599 | -0.29755 | -0.24719 | 0.07782 | -0.091553 | -0.09613 | 0.17395 | 0.004578 | -0.3067 | 0.10529 | 0.07782 | 120.1767 | -0.14191 | -0.44861 | 119.8746 | 120.2499 | 119.9249 | 0.073242 | -0.25177 | 120.3461 | -0.33874 | -0.23804 | 119.8654 | 120.2499 | 120.2774 | -0.09613 | -0.068664 | -0.30212 | -0.21057 | -0.48065 | -0.16937 | 0.09613 | -0.27008 | 120.2728 | 120.076 | -0.23804 | -0.068665 | 119.9661 | 120.1767 | 120.1355 | 120.0806
2654.4844 | 120.7626 | -120.1447 | 0.32959 | -0.0016785 | 6.9784 | 0.017835 | -0.0036444 | -0.0011408 | -0.010173 | -0.0021532 | -0.024963 | 0.0005234 | 0.013324 | 0.010641 | -0.0087629 | 0.028521 | 0.001835 | -0.013733 | 0.33875 | 0.022888 | 0.54474 | 0.14648 | 0.054932 | 0.027466 | 0.027466 | -0.009155 | 0.032043 | 0.082397 | 0.14191 | 0.11902 | 0.16022 | 120.1675 | 0.009155 | 0.21515 | 120.2911 | 120.1721 | 120.1996 | 0.004578 | 0.032044 | 120.1767 | -0.33875 | -0.24719 | 120.2866 | 120.3049 | 120.2637 | 0.12817 | 0.086976 | 0.1236 | 0.52185 | 0.10986 | 0.050354 | 0.31586 | -0.041198 | 120.4834 | 120.1355 | -0.3067 | -0.29755 | 120.6894 | 120.2271 | 120.1309 | 120.1721
2656.2344 | 120.6528 | -120.2682 | 0.24719 | -0.0016785 | 6.9776 | 0.016554 | -0.0049262 | -0.00028623 | -0.011882 | -0.0012988 | -0.21417 | 0.0013778 | 0.012683 | 0.006368 | -0.011326 | 0.030016 | -0.0047874 | -0.013733 | 0.07782 | 0.018311 | 0.082397 | 0.036621 | -0.16937 | -0.35248 | -0.045776 | 0.018311 | 0.19684 | 0.004578 | 0.041199 | -0.28381 | -0.24719 | 120.2866 | -0.16937 | -0.16479 | 120.3049 | 119.9158 | 120.0989 | -0.37079 | -0.18768 | 120.4651 | -0.22888 | -0.24261 | 120.3094 | 120.0211 | 119.9844 | -0.44403 | -0.48065 | 0.01831 | 0.064086 | -0.15564 | -0.19226 | 0.059509 | -0.17853 | 120.3461 | 120.2866 | -0.22888 | -0.050354 | 120.3506 | 120.2728 | 120.2545 | 120.2225
2657.9688 | 120.726 | -120.3552 | 0.25635 | -0.0016785 | 6.9786 | 0.017622 | -0.011335 | -0.013531 | -0.011668 | -0.0040758 | 0.042175 | 0.028294 | 0.012256 | 0.001882 | 0.034389 | 0.045611 | 0.031101 | 0.018311 | 0.10529 | 0.009155 | 0.10529 | -0.1831 | -0.050354 | 0.082397 | 0.032043 | 0.032043 | 0.018311 | 0.064087 | -0.018311 | -0.10986 | 0.086975 | 120.3644 | -0.15106 | -0.15106 | 120.1721 | 120.4376 | 120.3049 | 0.073242 | -0.059509 | 120.3735 | -0.22431 | -0.19226 | 120.3369 | 120.4422 | 120.2454 | 0.068664 | -0.12817 | -0.19226 | 0.096131 | -0.036622 | 0.045776 | 0.096131 | 0.013732 | 120.4605 | 120.3873 | -0.24719 | -0.23804 | 120.4605 | 120.4193 | 120.3735 | 120.3873
2659.7031 | 120.639 | -120.1355 | 0.21515 | -0.0016785 | 6.9791 | 0.018904 | -0.0030036 | -0.0011408 | -0.0095319 | 0.00041017 | -0.10736 | 0.0022324 | 0.012469 | 0.018758 | -0.0044903 | 0.029589 | -0.0013694 | 0.045776 | 0.07782 | 0.045776 | 0.19684 | 0.19684 | -0.068665 | -0.25635 | 0.10529 | -0.004578 | 0.045776 | 0.15106 | 0.16937 | 0.073242 | 0.050354 | 120.1813 | -0.13733 | -0.018311 | 120.3323 | 119.8791 | 120.0668 | -0.30212 | -0.11444 | 120.1813 | -0.21973 | -0.064087 | 120.3049 | 120.1859 | 120.2087 | 0.004578 | 0.027466 | 0.15106 | 0.15106 | 0.1236 | 0.10529 | 0.032044 | -0.050354 | 120.2133 | 120.1309 | -0.16937 | -0.16937 | 120.3323 | 120.2866 | 120.1813 | 120.2408
2661.3906 | 120.7077 | -120.314 | 0.24261 | -0.009308 | 6.9765 | 0.016767 | -0.0042852 | 0.0046272 | -0.0078229 | -0.0040758 | -0.11652 | -0.0001174 | 0.011615 | 0.010854 | -0.01154 | 0.02788 | -0.0047874 | 0.041199 | 0.073242 | 0.036621 | 0.18768 | 0.19226 | 0.045776 | -0.15564 | 0.054932 | -0.004578 | 0.027466 | 0.054932 | 0.1236 | 0.004578 | -0.068665 | 120.3506 | -0.16937 | -0.054932 | 120.5063 | 120.1584 | 120.3598 | -0.19226 | 0.009155 | 120.3415 | -0.24719 | -0.18768 | 120.4376 | 120.2454 | 120.3186 | -0.096131 | -0.022888 | 0.15564 | 0.15106 | 0.09613 | 0.027466 | 0.036621 | -0.032044 | 120.3873 | 120.3094 | -0.20599 | -0.21515 | 120.5017 | 120.369 | 120.3552 | 120.369
2663.1406 | 120.694 | -120.3873 | 0.24719 | 0.005951 | 6.9799 | 0.017622 | -0.0017218 | 0.00078177 | -0.0088911 | -0.0047168 | 0.057434 | -0.0003312 | 0.011188 | 0.011709 | -0.011113 | 0.02083 | -0.0088462 | -0.009155 | 0.11444 | 0.009155 | 0.07782 | -0.082397 | -0.40283 | 0.082397 | -0.050354 | 0.032043 | 0.013733 | -0.009155 | 0.018311 | -0.33417 | 0.091553 | 120.3964 | -0.13275 | -0.16937 | 120.3049 | 120.4697 | 119.9844 | 0.073242 | -0.41199 | 120.401 | -0.21515 | -0.25635 | 120.4056 | 120.4788 | 120.0531 | 0.07782 | -0.3479 | -0.091552 | 0.068665 | 0.004578 | -0.022888 | 0.10529 | 0.01831 | 120.5017 | 120.4193 | -0.23804 | -0.23346 | 120.4651 | 120.3781 | 120.3781 | 120.3369
2664.8281 | 120.8679 | -120.3598 | 0.21515 | -0.0016785 | 6.9799 | 0.018263 | -0.00279 | -0.0022088 | -0.0084637 | -0.0021532 | -0.08905 | -0.0003312 | 0.013751 | 0.010213 | -0.0051313 | 0.029162 | -0.00072839 | 0.073242 | 0.07782 | 0.050354 | 0.19684 | 0.19226 | 0.07782 | -0.086975 | 0.11444 | 0.004578 | 0.041199 | 0.13275 | 0.1831 | 0.11444 | 0.19226 | 120.4102 | -0.13733 | -0.018311 | 120.5521 | 120.2728 | 120.4376 | -0.13733 | 0.027466 | 120.401 | -0.21057 | -0.082398 | 120.5429 | 120.5521 | 120.4742 | 0.15106 | 0.073242 | 0.14191 | 0.14648 | 0.14191 | 0.091552 | 0.027466 | -0.036621 | 120.4376 | 120.3644 | -0.16479 | -0.17395 | 120.5566 | 120.4926 | 120.433 | 120.4742
2666.5625 | 120.5338 | -120.1813 | 0.24261 | -0.009308 | 6.981 | 0.01869 | -0.0079168 | -0.013744 | -0.011882 | -0.016039 | 0.045227 | 0.02979 | 0.011188 | 0.003591 | -0.023076 | 0.020403 | 0.0065348 | -0.018311 | 0.086975 | 0 | 0.013733 | -0.30212 | 0.082397 | 0.082397 | -0.073242 | 0.013733 | 0.14648 | 0.004578 | -0.11902 | 0.10071 | 0.073242 | 120.1813 | -0.15564 | -0.22888 | 119.8791 | 120.2637 | 120.2637 | 0.082397 | 0.082397 | 120.3278 | -0.22888 | -0.23804 | 120.0623 | 120.2545 | 120.282 | -0.073242 | -0.045776 | -0.30212 | 0.013733 | -0.2655 | -0.14191 | 0.086975 | -0.13275 | 120.2682 | 120.195 | -0.24261 | -0.096131 | 120.195 | 120.1859 | 120.163 | 120.108
2668.25 | 120.6985 | -120.3186 | 0.2655 | 0.005951 | 6.9795 | 0.018476 | -0.0034308 | -7.2628e-05 | -0.0080365 | -0.001726 | 0.039123 | -0.008876 | 0.013537 | -0.0011088 | -0.014103 | 0.020403 | -0.015682 | -0.036621 | 0.091553 | 0.004578 | 0.068665 | -0.16937 | -0.068665 | 0.082397 | -0.054932 | 0.045776 | 0.013733 | 0.027466 | 0.013733 | -0.21057 | 0.07782 | 120.3232 | -0.17395 | -0.19684 | 120.1492 | 120.401 | 120.2499 | 0.077819 | -0.073243 | 120.3323 | -0.21973 | -0.23804 | 120.3323 | 120.3964 | 120.108 | 0.064087 | -0.2243 | -0.17395 | 0.064087 | 0 | 0.013733 | 0.086975 | 0.032043 | 120.4102 | 120.3644 | -0.26092 | -0.25177 | 120.3873 | 120.3461 | 120.282 | 120.2637
2669.9844 | 120.7397 | -120.4102 | 0.2655 | -0.0016785 | 6.9767 | 0.016981 | -0.0049262 | 0.0027044 | -0.010814 | -0.00023063 | -0.20197 | 0.0030868 | 0.013965 | 0.0067954 | -0.0096173 | 0.02788 | -0.0024374 | 0.004578 | 0.07782 | 0.009155 | 0.11902 | 0.1236 | -0.10986 | -0.27924 | -0.032043 | 0.027466 | 0.022888 | 0.009155 | 0.059509 | -0.073242 | -0.13733 | 120.4193 | -0.18768 | -0.14648 | 120.5338 | 120.1309 | 120.3003 | -0.28839 | -0.11902 | 120.433 | -0.23804 | -0.25635 | 120.4697 | 120.2728 | 120.3369 | -0.16022 | -0.09613 | 0.11444 | 0.10986 | 0.036621 | -0.013733 | 0.068665 | 0.004578 | 120.488 | 120.4376 | -0.25635 | -0.24261 | 120.5292 | 120.4193 | 120.4147 | 120.3781
2671.7344 | 120.6253 | -120.4193 | 0.25635 | -0.0016785 | 6.9778 | 0.017622 | -0.003858 | 0.0039862 | -0.0082501 | -0.00087163 | 0.042175 | 0.02979 | 0.012042 | 0.010427 | -0.010258 | 0.018694 | -0.012905 | 0.018311 | 0.082397 | 0 | 0.11902 | -0.036621 | -0.10071 | 0.082397 | 0.045776 | 0.018311 | 0.032043 | 0.059509 | 0.064087 | -0.32959 | 0.07782 | 120.4193 | -0.17395 | -0.13733 | 120.3827 | 120.5017 | 120.3186 | 0.082397 | -0.10071 | 120.4514 | -0.23804 | -0.19684 | 120.4834 | 120.4971 | 120.0897 | 0.045777 | -0.36163 | -0.036621 | 0.11902 | 0.032044 | 0.027466 | 0.082397 | -0.013732 | 120.5017 | 120.4376 | -0.25635 | -0.22431 | 120.5383 | 120.4788 | 120.4376 | 120.4651
2673.4844 | 120.9045 | -120.4651 | 0.21973 | 0.01358 | 6.9761 | 0.017622 | -0.0057806 | -0.0037042 | -0.0095319 | -0.0012988 | -0.01886 | 0.0009506 | 0.010119 | 0.0091452 | -0.0085491 | 0.02788 | -0.0017966 | -0.004578 | 0.091553 | 0.022888 | 0.17853 | 0.19684 | 0.10529 | 0.082397 | 0.07782 | 0.004578 | 0.050354 | 0.10986 | 0.20142 | 0.12817 | 0.21973 | 120.488 | -0.12817 | -0.041199 | 120.6619 | 120.5475 | 120.5704 | 0.059509 | 0.082398 | 120.5154 | -0.21515 | -0.10986 | 120.6665 | 120.6848 | 120.5933 | 0.16937 | 0.07782 | 0.17395 | 0.15564 | 0.15106 | 0.059509 | 0.068665 | -0.045776 | 120.5566 | 120.4697 | -0.19684 | -0.16937 | 120.6436 | 120.575 | 120.4605 | 120.5429
2675.1562 | 120.369 | -120.4056 | 0.25177 | -0.0016785 | 6.9782 | 0.016767 | -0.003858 | 0.0031318 | -0.0093183 | -0.0021532 | -0.21417 | -0.0046036 | 0.013324 | 0.007009 | -0.0089765 | 0.029375 | -0.0045736 | -0.036621 | 0.11902 | -0.018311 | 0.09613 | 0.059509 | -0.19226 | -0.28381 | -0.054932 | 0.027466 | 0.013733 | 0.022888 | 0.068665 | -0.10529 | -0.24261 | 120.3873 | -0.13275 | -0.15564 | 120.4651 | 120.1218 | 120.2133 | -0.2655 | -0.17395 | 120.4193 | -0.2243 | -0.22888 | 120.4742 | 120.163 | 120.3003 | -0.25635 | -0.11902 | 0.07782 | 0.11444 | 0.054932 | 0.009155 | 0.13733 | 0.013733 | 120.5246 | 120.433 | -0.27008 | -0.23804 | 120.5017 | 120.4285 | 120.369 | 120.3506
2676.9062 | 119.783 | -119.2978 | 0.20142 | 0.005951 | 6.9707 | 0.020826 | -0.0091986 | -0.00049983 | -0.0093183 | 0.00041017 | -0.14703 | 0.0003098 | 0.015246 | 0.011068 | -0.0089765 | 0.031725 | -0.0030784 | -0.23346 | 0.086975 | 0.07782 | -0.059509 | -0.1236 | -0.10071 | -0.15106 | -0.16022 | -0.28839 | 0.15564 | -0.13275 | -0.23346 | -0.27924 | -0.17853 | 119.3756 | -0.11444 | -0.26093 | 119.1742 | 119.1467 | 119.1971 | -0.22888 | -0.17853 | 119.4534 | -0.48981 | -0.33417 | 119.0643 | 119.1193 | 119.0186 | -0.33417 | -0.43488 | -0.20142 | -0.13733 | -0.3891 | -0.28839 | 0.009155 | -0.44403 | 119.3848 | 119.0094 | -0.1236 | -0.045776 | 119.2383 | 119.165 | 119.0643 | 119.1376
2678.6562 | 120.1813 | -119.7693 | 0.091553 | 0.005951 | 6.9756 | 0.016981 | -0.018384 | 0.011463 | -0.0153 | -0.01668 | 0.036072 | 0.028508 | 0.0017881 | 0.0072226 | 0.034816 | 0.045397 | 0.031529 | -0.086975 | 0.091553 | 0.32501 | -0.032043 | 0.07782 | 0.07782 | 0.082397 | -0.32044 | 0.07782 | -0.086975 | 0.082397 | 0.086975 | 0.082397 | 0.082397 | 120.0943 | 0 | -0.1236 | 119.8471 | 119.8517 | 119.8471 | -0.24262 | -0.24719 | 119.6823 | -0.013733 | -0.009156 | 119.8563 | 119.8517 | 119.8517 | 0.16937 | 0.16937 | -0.24719 | -0.35706 | 0.17395 | 0.16937 | -0.23346 | 0.16479 | 119.8608 | 119.8471 | 0.23346 | -0.17853 | 119.7372 | 119.8517 | 119.6823 | 119.4489
2680.3438 | 120.5658 | -120.0714 | 0.21515 | -0.009308 | 6.9774 | 0.016554 | -0.0062078 | -0.00071343 | -0.0091047 | -0.00023063 | -0.085999 | 0.0009506 | 0.011828 | 0.017476 | -0.010045 | 0.028307 | -8.7586e-05 | 0.004578 | 0.064087 | 0.045776 | 0.17853 | 0.19226 | 0.059509 | -0.022888 | 0.082397 | -0.013733 | 0.25177 | 0.10986 | 0.19226 | 0.11444 | 0.16022 | 120.1172 | -0.15106 | -0.036621 | 120.2637 | 120.0485 | 120.1309 | -0.068664 | 0.013733 | 120.3232 | -0.22888 | -0.10529 | 120.2637 | 120.2316 | 120.1859 | -0.091553 | -0.13733 | 0.14648 | 0.13275 | -0.059509 | -0.14191 | 0.018311 | -0.2655 | 120.1355 | 120.0577 | -0.16937 | 0.036621 | 120.2499 | 120.1813 | 120.076 | 120.1538
2682.0312 | 120.5841 | -120.1767 | 0.22888 | 0.01358 | 6.9799 | 0.01634 | -0.0066352 | -0.00071343 | -0.0091047 | 0.00019657 | -0.092102 | -0.000972 | 0.012683 | 0.0099996 | -0.0055585 | 0.029375 | -0.00094199 | 0.013733 | 0.07782 | 0.045776 | 0.18768 | 0.18768 | -0.009155 | -0.086975 | 0.068665 | 0.004578 | 0.050354 | 0.064087 | 0.12817 | 0.068665 | 0.11444 | 120.2225 | -0.15106 | -0.041199 | 120.3644 | 120.0897 | 120.1675 | -0.13275 | -0.054931 | 120.2271 | -0.2243 | -0.16479 | 120.3049 | 120.2911 | 120.2454 | 0.064087 | 0.018311 | 0.14191 | 0.14191 | 0.07782 | 0.013733 | 0.032044 | -0.045776 | 120.2545 | 120.1813 | -0.18311 | -0.17853 | 120.3644 | 120.2408 | 120.1904 | 120.2454
2683.7812 | 120.6665 | -120.195 | 0.23804 | -0.009308 | 6.9763 | 0.016981 | -0.0064216 | 0.00056817 | -0.011241 | -0.0030078 | -0.14398 | 0.0018052 | 0.01076 | 0.010854 | -0.0098309 | 0.028307 | -0.0020102 | 0.032043 | 0.068665 | 0.036621 | 0.19226 | 0.13733 | -0.07782 | -0.16937 | 0.059509 | 0 | 0.19684 | 0.082397 | 0.1236 | -0.091553 | -0.068665 | 120.2316 | -0.16937 | -0.045776 | 120.3323 | 120.0256 | 120.1172 | -0.20599 | -0.11444 | 120.3918 | -0.23804 | -0.15564 | 120.3186 | 120.1263 | 120.1035 | -0.2655 | -0.28839 | 0.10071 | 0.15564 | -0.073242 | -0.11444 | 0.032044 | -0.19684 | 120.2637 | 120.195 | -0.20142 | -0.041199 | 120.3873 | 120.2774 | 120.2271 | 120.2545
2685.5312 | 120.4376 | -119.9524 | 0.25635 | -0.0016785 | 6.9756 | 0.016767 | -0.012617 | -0.015453 | -0.0080365 | -0.012621 | 0.042175 | 0.028722 | 0.013537 | -0.010081 | 0.03503 | 0.04497 | -0.010982 | 0.009155 | 0.11444 | 0 | 0.10986 | -0.036621 | 0.086975 | 0.082397 | 0.027466 | 0.004578 | 0.10529 | 0.054932 | -0.27008 | 0.082397 | 0.07782 | 119.9524 | -0.14191 | -0.14649 | 119.9158 | 120.0348 | 120.0394 | 0.082397 | 0.086975 | 120.0577 | -0.25177 | -0.20142 | 119.6823 | 120.0302 | 120.0348 | -0.027466 | -0.022889 | -0.036621 | 0.10986 | -0.37537 | -0.050354 | 0.11444 | -0.10071 | 120.0668 | 119.957 | -0.25635 | -0.15106 | 120.0623 | 120.0073 | 119.9615 | 119.9799
2687.2031 | 120.1813 | -119.9615 | 0.2655 | -0.0016785 | 6.9797 | 0.017622 | -0.0081306 | -0.00092703 | -0.0082501 | -0.0032214 | 0.036072 | -0.0024674 | 0.011615 | -0.0028178 | -0.026066 | 0.018267 | -0.019741 | 0.013733 | 0.09613 | 0.004578 | 0.09613 | -0.21057 | 0.10071 | 0.091553 | 0.018311 | 0.027466 | 0.032043 | 0.050354 | -0.17395 | 0.091553 | 0.07782 | 119.9661 | -0.16937 | -0.16937 | 119.751 | 120.0531 | 120.0623 | 0.086975 | 0.09613 | 119.9936 | -0.23804 | -0.21515 | 119.7876 | 120.0394 | 120.0531 | 0.045777 | 0.05951 | -0.21515 | 0.091552 | -0.20599 | 0.018311 | 0.091552 | -0.004577 | 120.0577 | 119.989 | -0.26092 | -0.23346 | 120.0577 | 120.0119 | 119.9753 | 119.9799
2688.9531 | 120.3827 | -120.3094 | 0.26093 | -0.0016785 | 6.9806 | 0.019331 | -0.0040716 | 0.00099557 | -0.0093183 | -0.0040758 | -0.095154 | 0.0013778 | 0.013965 | 0.014699 | -0.0068403 | 0.028948 | 0.00033961 | -0.041199 | 0.12817 | 0.013733 | 0.068665 | -0.041199 | -0.34332 | -0.1236 | -0.054932 | 0.032043 | 0.032043 | 0.013733 | 0.045776 | -0.18768 | -0.20142 | 120.3232 | -0.13275 | -0.19226 | 120.2682 | 120.1859 | 119.9661 | -0.13733 | -0.35706 | 120.3415 | -0.22888 | -0.24719 | 120.3552 | 120.108 | 120.1218 | -0.23346 | -0.21973 | -0.054932 | 0.054932 | 0.013733 | -0.01831 | 0.11444 | 0 | 120.4376 | 120.3415 | -0.24719 | -0.22888 | 120.3781 | 120.3232 | 120.2682 | 120.2545
2690.6875 | 120.8267 | -120.401 | 0.22888 | -0.0016785 | 6.9793 | 0.017835 | -0.0040716 | 0.0024908 | -0.0095319 | -0.0036486 | -0.03717 | 0.0003098 | 0.014392 | 0.011495 | -0.0066265 | 0.030016 | -0.00030119 | 0.009155 | 0.086975 | 0.045776 | 0.20599 | 0.18768 | 0.059509 | 0.009155 | 0.064087 | -0.009155 | 0.064087 | 0.07782 | 0.1236 | 0.073242 | 0.16022 | 120.4468 | -0.14191 | -0.022888 | 120.5887 | 120.4102 | 120.4605 | -0.036621 | 0.013733 | 120.4651 | -0.23804 | -0.15106 | 120.5246 | 120.5612 | 120.4742 | 0.09613 | 0.009155 | 0.14191 | 0.16022 | 0.059509 | 0.013733 | 0.041199 | -0.073242 | 120.488 | 120.3918 | -0.18311 | -0.16479 | 120.607 | 120.4788 | 120.4102 | 120.4651
2692.4375 | 120.5338 | -120.0302 | 0.12817 | -0.0016785 | 6.9799 | 0.019331 | -0.012617 | -0.0073358 | -0.017009 | -0.005144 | 0.042175 | 0.028935 | 0.017383 | 0.0074362 | 0.037166 | 0.04027 | 0.031101 | -0.10071 | 0.12817 | 0.39825 | 0.054932 | 0.073242 | 0.07782 | 0.07782 | 0.082397 | 0.086975 | -0.086975 | 0.082397 | 0.082397 | 0.086975 | 0.07782 | 120.4285 | 0 | -0.073242 | 120.1035 | 120.108 | 120.108 | -0.32043 | -0.32043 | 119.9432 | -0.041199 | -0.045777 | 120.1126 | 120.108 | 120.1172 | 0.16479 | 0.17395 | -0.32501 | -0.34332 | 0.16937 | 0.16937 | -0.27008 | 0.17395 | 120.1584 | 120.1172 | 0.27008 | -0.21515 | 120.0851 | 120.1126 | 119.9295 | 120.1126
2694.125 | 120.4102 | -119.9066 | 0.2243 | 0.005951 | 6.9786 | 0.016554 | -0.017957 | 0.01189 | -0.015086 | -0.011125 | 0.039123 | 0.028722 | 0.0073423 | 0.0076498 | 0.034603 | 0.045397 | 0.031529 | -0.37994 | 0.19226 | 0.35248 | 0.091553 | 0.082397 | 0.07782 | 0.082397 | -0.1236 | 0.082397 | -0.082397 | -0.15106 | 0.086975 | 0.07782 | 0.07782 | 120.2591 | -0.032043 | -0.13275 | 119.989 | 119.989 | 119.9844 | -0.27008 | -0.27466 | 119.8242 | -0.14191 | -0.37537 | 119.9936 | 119.9844 | 119.9844 | 0.16022 | 0.16022 | -0.27008 | -0.26093 | 0.16937 | -0.068665 | -0.16022 | 0.16479 | 120.0989 | 119.989 | 0.12817 | -0.3067 | 119.9982 | 119.7556 | 119.5267 | 119.783
2695.8594 | 120.4285 | -119.1925 | 1.0025 | -0.009308 | 6.9786 | 0.016554 | -0.0057806 | -0.012249 | -0.0086773 | -0.012194 | 0.039123 | 0.027867 | 0.0067013 | 0.0072226 | -0.015385 | 0.020403 | 0.033665 | -0.09613 | 0.81482 | 0.23804 | 0.46692 | 0.082397 | 0.082397 | 0.082397 | -0.064087 | -0.16937 | -0.07782 | -0.2243 | 0.082397 | 0.07782 | 0.082397 | 119.4305 | -0.18768 | -0.53558 | 119.2749 | 119.2749 | 119.2749 | -0.15564 | -0.15564 | 119.1147 | -1.1719 | -1.2268 | 119.2749 | 119.2749 | 119.2703 | 0.16022 | 0.15564 | -0.15564 | 0.22888 | 0.16022 | -0.14648 | 0.57678 | -0.091553 | 120.0073 | 119.0231 | -0.76446 | -1.0803 | 119.6594 | 118.9682 | 119.0964 | 119.1284
2697.5469 | 120.4468 | -120.1263 | 0.13275 | 0.005951 | 6.9803 | 0.015486 | -0.0049262 | 0.011249 | -0.011241 | -0.01198 | 0.042175 | 0.028294 | 0.0043515 | 0.0074362 | 0.034603 | 0.045611 | 0.031101 | -0.022888 | 0 | 0.068665 | -0.26093 | 0.07782 | 0.082397 | 0.07782 | 0.004578 | -0.18768 | 0.082397 | -0.32044 | 0.082397 | 0.086975 | 0.07782 | 120.195 | -0.13275 | -0.39368 | 120.2042 | 120.2042 | 120.2087 | 0.009155 | 0.013732 | 120.2087 | -0.32043 | -0.45319 | 120.2087 | 120.2042 | 120.2133 | -0.004577 | 0.004578 | 0.009155 | -0.32959 | 0 | -0.40283 | -0.068665 | -0.27008 | 120.1263 | 119.9387 | -0.064086 | -0.050354 | 119.8654 | 119.8059 | 120.1035 | 120.1309
2699.2812 | 120.7443 | -120.3323 | 0.10986 | 0.005951 | 6.9789 | 0.018049 | -0.0049262 | -0.002636 | -0.0063275 | -0.00044443 | -0.13788 | 0.0020188 | 0.011615 | 0.0072226 | -0.0081219 | 0.029375 | -0.0039328 | 0.032043 | -0.045776 | 0.064087 | 0.10071 | 0.091553 | -0.068665 | -0.16479 | 0.09613 | 0 | 0.07782 | 0.11444 | 0.14648 | 0.027466 | 0.082397 | 120.3964 | -0.15564 | -0.009155 | 120.4239 | 120.1675 | 120.2637 | -0.22888 | -0.13275 | 120.4102 | -0.10986 | 0.004578 | 120.4788 | 120.4147 | 120.3598 | 0.004577 | -0.050354 | 0.027466 | 0.036621 | 0.068664 | 0.036621 | -0.10986 | -0.07782 | 120.2866 | 120.3323 | -0.045776 | -0.032043 | 120.433 | 120.4468 | 120.3644 | 120.4285
2701.0312 | 120.7535 | -120.4605 | 0.11444 | -0.0016785 | 6.9784 | 0.019544 | -0.0030036 | -0.00028623 | -0.010173 | -0.00044443 | -0.052429 | 0.0026596 | 0.010333 | 0.0078634 | -0.0085491 | 0.030443 | -0.0017966 | -0.013733 | -0.041199 | 0.045776 | 0.032043 | 0.16022 | 0.041199 | -0.050354 | 0.018311 | 0.004578 | 0.013733 | 0.054932 | 0.11902 | 0.059509 | 0.15564 | 120.5063 | -0.15564 | -0.082398 | 120.6207 | 120.4102 | 120.5017 | -0.09613 | -0.004577 | 120.4742 | -0.10986 | -0.059509 | 120.5795 | 120.6162 | 120.52 | 0.14191 | 0.045776 | 0.11444 | -0.013733 | 0.10529 | 0.041199 | -0.086975 | -0.009155 | 120.4193 | 120.4651 | -0.068665 | -0.10071 | 120.4926 | 120.5154 | 120.4468 | 120.4788
2702.7812 | 120.7077 | -120.2591 | 0.12817 | -0.0016785 | 6.9799 | 0.015913 | -0.0049262 | -7.2628e-05 | -0.0054731 | -0.0027942 | -0.19281 | -0.0003312 | 0.014605 | 0.010427 | -0.012822 | 0.027666 | -0.0013694 | 0.018311 | -0.054932 | 0.10986 | 0.091553 | 0.027466 | -0.11902 | -0.19684 | 0.064087 | -0.059509 | 0.3891 | 0.068665 | 0.022888 | -0.13275 | -0.10529 | 120.369 | -0.18311 | -0.036621 | 120.2866 | 120.0623 | 120.1401 | -0.3067 | -0.22888 | 120.6482 | -0.18768 | -0.059509 | 120.282 | 120.1538 | 120.1263 | -0.49438 | -0.52185 | -0.082397 | -0.01831 | -0.36621 | -0.32043 | -0.16479 | -0.44861 | 120.2042 | 120.1996 | -0.018311 | 0.26092 | 120.3506 | 120.3278 | 120.2774 | 120.3232
2704.4844 | 120.7031 | -120.4559 | 0.13733 | -0.0016785 | 6.9776 | 0.017408 | -0.018598 | -0.015881 | -0.015513 | -0.014971 | 0.042175 | -0.0090896 | 0.010974 | 0.015767 | -0.0074811 | 0.024462 | -0.0062826 | -0.050354 | 0 | 0.009155 | -0.15564 | -0.041199 | 0.07782 | 0.091553 | -0.068665 | 0.032043 | 0.21057 | 0.004578 | -0.21973 | -0.11444 | 0.073242 | 120.4651 | -0.13733 | -0.29297 | 120.4147 | 120.5475 | 120.5338 | 0.082398 | 0.068665 | 120.6665 | -0.10529 | -0.13275 | 120.2362 | 120.5292 | 120.3415 | -0.13733 | -0.32501 | -0.050354 | -0.16479 | -0.4303 | -0.20599 | -0.009155 | -0.17853 | 120.4559 | 120.488 | -0.12817 | 0.073242 | 120.3003 | 120.4605 | 120.4056 | 120.3873
2706.2188 | 120.3232 | -120.0851 | 0.10986 | -0.0016785 | 6.9776 | 0.020613 | -0.013257 | -0.015026 | -0.02299 | -0.023302 | 0.057434 | -0.010799 | -0.0029117 | 0.013204 | -0.0091901 | 0.023821 | -0.0090598 | -0.13733 | 0 | 0.23346 | -0.35248 | 0.091553 | 0.082397 | 0.073242 | -0.2655 | -0.064087 | -0.10529 | -0.07782 | -0.059509 | 0.086975 | 0.073242 | 120.3186 | -0.10986 | -0.46234 | 120.1767 | 120.1584 | 120.1675 | -0.16022 | -0.15106 | 119.9799 | -0.17395 | -0.18768 | 120.0256 | 120.1584 | 120.1721 | 0.17853 | 0.19226 | -0.14191 | -0.58594 | 0.045777 | 0.027466 | -0.23346 | 0.041199 | 120.0851 | 120.0211 | 0.1236 | -0.21515 | 119.7327 | 120.0073 | 119.9478 | 119.8196
2707.8906 | 120.4468 | -120.0394 | 0.12817 | 0.005951 | 6.9776 | 0.016981 | -0.005567 | -0.0037042 | -0.0080365 | -0.00087163 | -0.19891 | 0.0011642 | 0.011828 | 0.011709 | -0.011967 | 0.028307 | -0.0088462 | 0.004578 | -0.050354 | 0.32959 | 0.036621 | -0.091553 | -0.2243 | -0.3067 | -0.004578 | -0.31128 | 0.37079 | 0.032043 | -0.13733 | -0.29755 | -0.23804 | 120.369 | -0.17853 | -0.091553 | 119.9478 | 119.7327 | 119.8151 | -0.63629 | -0.55389 | 120.4102 | -0.43945 | -0.096131 | 119.902 | 119.8013 | 119.7418 | -0.60883 | -0.66833 | -0.42114 | -0.29297 | -0.50812 | -0.33875 | -0.37994 | -0.68207 | 119.989 | 119.7281 | 0.20142 | 0.24261 | 120.076 | 120.0714 | 120.0439 | 120.0348
2709.6406 | 120.6528 | -120.2637 | 0.12817 | 0.01358 | 6.9776 | 0.016767 | -0.0036444 | -0.00028623 | -0.0073957 | -0.0010852 | -0.058533 | 0.0026596 | 0.01546 | 0.012563 | -0.010258 | 0.028094 | -0.0035056 | -0.032043 | -0.027466 | 0.032043 | 0.018311 | 0.14648 | 0.013733 | -0.022888 | 0 | 0 | 0.09613 | 0.073242 | 0.11444 | 0.091553 | 0.17853 | 120.2957 | -0.15564 | -0.10986 | 120.4102 | 120.2408 | 120.2774 | -0.054931 | -0.01831 | 120.3598 | -0.12817 | -0.054932 | 120.3781 | 120.4422 | 120.3552 | 0.082398 | -0.004577 | 0.11444 | -0.013732 | 0.018311 | -0.022888 | -0.059509 | -0.09613 | 120.2362 | 120.2637 | -0.096131 | -0.032044 | 120.282 | 120.3369 | 120.2316 | 120.2637
2711.375 | 120.7535 | -120.3278 | 0.1236 | -0.016937 | 6.9776 | 0.016126 | -0.0034308 | 0.0016364 | -0.0080365 | -0.0030078 | -0.098206 | 0.0003098 | 0.014178 | 0.011068 | -0.0094037 | 0.028094 | -0.0024374 | 0.018311 | -0.045776 | 0.050354 | 0.11444 | 0.23804 | 0.050354 | -0.045776 | 0.10986 | -0.027466 | 0.045776 | 0.10986 | 0.16937 | 0.10986 | 0.10986 | 120.3781 | -0.16937 | -0.009155 | 120.5658 | 120.282 | 120.3781 | -0.09613 | 0 | 120.3735 | -0.15106 | -0.013733 | 120.4971 | 120.4376 | 120.4376 | 0.064087 | 0.064087 | 0.18768 | 0.064087 | 0.1236 | 0.064087 | -0.09613 | -0.073242 | 120.282 | 120.3003 | -0.073242 | -0.07782 | 120.4422 | 120.4376 | 120.3461 | 120.4376
2713.0469 | 120.3461 | -119.3115 | -3.1677 | -0.0016785 | 7.0038 | 0.015486 | 0.011736 | -0.0034906 | -0.0097455 | 0.0012646 | -0.0066527 | 0.011205 | 0.021228 | 0.0074362 | -0.015172 | 0.024462 | -0.0099142 | 0.56305 | 21.8216 | 0.4715 | 14.3875 | -0.018311 | 0.07782 | 20.9518 | -0.054932 | -0.24719 | -0.082397 | 0.009155 | -0.27924 | 0.082397 | 0.07782 | 119.783 | 24.9893 | 17.5552 | 119.2932 | 140.2634 | 119.3893 | 20.4803 | -0.39368 | 119.2291 | 2.9205 | 3.1769 | 119.0323 | 119.3893 | 119.3939 | 0.16022 | 0.16479 | -0.48981 | 13.916 | -0.19684 | 0.091552 | 21.3501 | -0.16479 | 141.1331 | 119.0643 | 3.6392 | 3.0853 | 133.699 | 119.3207 | 119.8746 | 119.2566
2714.8125 | 120.3781 | -120.0348 | 0.11902 | -0.0016785 | 6.978 | 0.018049 | -0.0087714 | 0.0020636 | -0.0054731 | -0.0015124 | -0.18671 | 0.0030868 | 0.013965 | 0.01299 | -0.0064129 | 0.027453 | -0.00072839 | -0.059509 | -0.009155 | 0.041199 | -0.16937 | -0.2243 | -0.20142 | -0.068665 | -0.004578 | -0.19226 | 0.32044 | 0.068665 | -0.14648 | -0.29297 | -0.19684 | 120.076 | -0.12817 | -0.28839 | 119.8105 | 119.9661 | 119.8334 | -0.10986 | -0.24262 | 120.3552 | -0.31128 | -0.050354 | 119.8883 | 119.838 | 119.7418 | -0.51727 | -0.6134 | -0.2655 | -0.21057 | -0.46692 | -0.25177 | -0.050354 | -0.5127 | 120.0256 | 119.8425 | -0.07782 | 0.20142 | 119.8654 | 120.1035 | 119.9753 | 120.0302
2716.5625 | 120.4742 | -120.3049 | 0.14648 | 0.005951 | 6.9767 | 0.015058 | -0.0051398 | 0.00185 | -0.0084637 | -0.002367 | -0.1745 | 0.0018052 | 0.011828 | 0.019613 | -0.0098309 | 0.02788 | -0.002651 | 0.009155 | -0.050354 | 0.032043 | 0.018311 | -0.041199 | -0.21973 | -0.28381 | -0.032043 | -0.004578 | 0.28839 | -0.009155 | -0.022888 | -0.24719 | -0.22888 | 120.3369 | -0.19684 | -0.12817 | 120.2637 | 120.0211 | 120.0851 | -0.31586 | -0.25177 | 120.5933 | -0.15106 | -0.15564 | 120.282 | 120.076 | 120.0577 | -0.51727 | -0.53558 | -0.073242 | -0.013732 | -0.31128 | -0.29755 | -0.082397 | -0.29297 | 120.2545 | 120.3003 | -0.11444 | 0.14191 | 120.3232 | 120.2957 | 120.314 | 120.2728
2718.2344 | 120.4147 | -120.3552 | 0.13733 | -0.009308 | 6.9791 | 0.019544 | -0.018171 | -0.00071343 | -0.011882 | -0.01967 | 0.039123 | 0.028508 | 0.012683 | 0.0072226 | -0.021794 | 0.011004 | -0.01675 | -0.018311 | -0.004578 | 0.013733 | -0.24261 | -0.009155 | 0.082397 | 0.082397 | -0.068665 | 0.032043 | 0.16479 | 0 | -0.26093 | 0.10071 | 0.082397 | 120.369 | -0.14191 | -0.37994 | 120.3461 | 120.4376 | 120.4376 | 0.068664 | 0.068664 | 120.52 | -0.10529 | -0.13733 | 120.0943 | 120.4376 | 120.4559 | -0.082398 | -0.064087 | -0.022888 | -0.25635 | -0.42572 | -0.16479 | -0.018311 | -0.13275 | 120.3506 | 120.3873 | -0.1236 | 0.027466 | 120.1126 | 120.3552 | 120.3369 | 120.2866
2719.9219 | 120.3415 | -120.4193 | 0.15564 | 0.005951 | 6.9786 | 0.015699 | -0.0025764 | -0.00028623 | -0.0099591 | -0.00023063 | -0.043274 | -0.0011856 | 0.01311 | -0.00944 | -0.010899 | 0.026812 | -0.0017966 | -0.041199 | -0.009155 | -0.004578 | -0.064087 | -0.18768 | -0.36621 | -0.07782 | -0.064087 | 0.041199 | 0.022888 | 0 | -0.054932 | -0.36621 | 0.036621 | 120.4147 | -0.16479 | -0.21973 | 120.2316 | 120.3415 | 120.0531 | -0.073242 | -0.36163 | 120.4422 | -0.11444 | -0.15564 | 120.3644 | 120.4559 | 120.0531 | 0.013733 | -0.3891 | -0.1831 | -0.059509 | -0.07782 | -0.022888 | -0.004577 | 0.018311 | 120.4102 | 120.4605 | -0.16022 | -0.13275 | 120.3552 | 120.4193 | 120.3781 | 120.3552
2721.6719 | 120.369 | -120.4697 | 0.14191 | 0.01358 | 6.9776 | 0.015699 | -0.00279 | 0.0022772 | -0.0091047 | -0.00044443 | -0.21722 | 0.000737 | 0.014392 | 0.0067954 | -0.013249 | 0.029162 | -0.0039328 | -0.041199 | -0.032043 | 0.013733 | -0.036621 | 0.004578 | -0.19684 | -0.34332 | -0.064087 | 0.032043 | 0.009155 | -0.032043 | 0.045776 | -0.16937 | -0.24261 | 120.4834 | -0.17395 | -0.17853 | 120.4742 | 120.1263 | 120.2728 | -0.35706 | -0.21057 | 120.4788 | -0.10986 | -0.17395 | 120.5154 | 120.2271 | 120.3003 | -0.25177 | -0.17853 | -0.009155 | -0.050354 | 0.036621 | -0.041198 | -0.045776 | 0.022888 | 120.4376 | 120.5017 | -0.12817 | -0.13275 | 120.433 | 120.4376 | 120.4285 | 120.4056
2723.4219 | 120.0668 | -120.0302 | 0.14648 | -0.009308 | 6.9797 | 0.017195 | -0.0062078 | -0.0054132 | -0.0073957 | -0.0081348 | 0.039123 | 0.028294 | 0.0071285 | 0.00081383 | 0.036739 | 0.04497 | -0.021877 | 0.009155 | -0.018311 | 0.018311 | -0.032043 | -0.20142 | -0.045776 | 0.082397 | 0.013733 | 0.018311 | 0 | 0.036621 | -0.054932 | -0.35248 | 0.073242 | 120.0485 | -0.16479 | -0.17853 | 119.8288 | 120.1126 | 119.9844 | 0.064086 | -0.064087 | 120.0302 | -0.12817 | -0.10986 | 119.9753 | 120.1035 | 119.6777 | 0.073242 | -0.35248 | -0.21973 | -0.050354 | -0.054932 | 0.036621 | -0.036622 | 0.018311 | 120.0119 | 120.0485 | -0.12817 | -0.14648 | 119.9982 | 120.0668 | 120.0394 | 120.0439
2725.1562 | 120.5658 | -120.4926 | 0.1236 | -0.0016785 | 6.9771 | 0.019544 | -0.00065359 | -0.0024224 | -0.0095319 | -0.0025806 | -0.18976 | 0.0022324 | 0.011615 | 0.0085044 | -0.0057721 | 0.031725 | -0.0071372 | -0.027466 | -0.022888 | 0.027466 | -0.013733 | 0.086975 | -0.1236 | -0.27924 | 0.022888 | 0.004578 | 0.022888 | 0.09613 | 0.1236 | 0.045776 | 0.073242 | 120.52 | -0.14648 | -0.13733 | 120.5795 | 120.2133 | 120.369 | -0.3067 | -0.15106 | 120.5154 | -0.11902 | -0.027466 | 120.6162 | 120.5658 | 120.5383 | 0.050354 | 0.022888 | 0.059509 | -0.041199 | 0.10071 | 0.073242 | -0.050354 | -0.01831 | 120.4697 | 120.4971 | -0.09613 | -0.10071 | 120.4788 | 120.5887 | 120.4651 | 120.5154
2726.8906 | 117.9657 | -89.4333 | 28.1754 | 0.005951 | 7.0209 | 0.005018 | 0.041216 | -0.001568 | -0.0029095 | 0.0012646 | -0.18365 | 0.0026596 | 0.01311 | 0.0095724 | -0.0098309 | 0.027239 | -0.00436 | 0.66834 | 29.3701 | 0.23346 | 28.8666 | 0.52643 | 0.87433 | 0.54474 | 0.041199 | -0.009155 | 0.013733 | 0.022888 | 0.10529 | 0 | -0.082397 | 89.6667 | 1.1948 | 0.69122 | 89.9597 | 89.978 | 90.3076 | 0.31128 | 0.64087 | 89.447 | -28.1845 | -28.1525 | 89.5386 | 89.3509 | 89.4333 | -0.09613 | -0.013733 | 0.29297 | 28.6331 | 0.091553 | 0.009155 | 29.1367 | -0.022888 | 118.8034 | 89.4241 | -27.9419 | -28.1616 | 118.2999 | 89.4562 | 90.1016 | 89.4745
2728.5781 | 120.7397 | -120.3094 | 0.10529 | 0.005951 | 6.9784 | 0.017408 | -0.0032172 | 0.0020636 | -0.0084637 | 0.00019657 | -0.07074 | 0.0028732 | 0.016528 | 0.015554 | -0.0061993 | 0.02788 | 0.0016214 | 0.036621 | -0.041199 | 0.054932 | 0.054932 | -0.068665 | -0.21057 | -0.27008 | 0.068665 | -0.11444 | 0.22888 | 0.11902 | 0.036621 | -0.068665 | 0.009155 | 120.3644 | -0.14649 | -0.050354 | 120.2408 | 120.0394 | 120.0989 | -0.32501 | -0.2655 | 120.5383 | -0.21973 | 0.013733 | 120.3461 | 120.3186 | 120.2408 | -0.21973 | -0.29755 | -0.1236 | 0 | -0.19226 | -0.10986 | -0.096131 | -0.34332 | 120.2682 | 120.195 | -0.050354 | 0.1236 | 120.3644 | 120.4285 | 120.3461 | 120.3781
2730.3281 | 118.0435 | -94.7159 | 22.5815 | -0.0016785 | 7.0115 | 0.011854 | 0.022418 | 0.00014097 | -0.0041913 | 0.0055372 | -0.19586 | 0.000737 | 0.014605 | 0.012777 | -0.012822 | 0.02788 | -8.7586e-05 | 0.46692 | 19.5282 | 0.50812 | 15.4266 | 0.16022 | 0.17853 | 0.13275 | 0.032043 | -0.27008 | 0.086975 | 0.036621 | -0.07782 | -0.21973 | -0.16937 | 95.224 | -3.0533 | -7.1548 | 94.8761 | 94.8486 | 94.8944 | -0.37537 | -0.32959 | 94.8029 | -22.8516 | -22.5449 | 94.6381 | 94.5465 | 94.4962 | -0.25635 | -0.3067 | -0.3479 | 14.9185 | -0.16479 | -0.050354 | 19.0201 | -0.35706 | 114.2441 | 94.4458 | -22.0734 | -22.4945 | 110.1425 | 94.7525 | 95.1828 | 94.7479
2732.0781 | 120.7306 | -120.2545 | 0.10529 | -0.0016785 | 6.9767 | 0.016126 | -0.0074896 | -7.2628e-05 | -0.0086773 | -0.0036486 | -0.061585 | 0.000737 | 0.012469 | 0.0095724 | -0.010258 | 0.029162 | -0.0017966 | -0.022888 | -0.036621 | 0.045776 | 0.041199 | 0.15106 | 0.050354 | -0.018311 | 0.045776 | -0.004578 | 0.15106 | 0.10071 | 0.15564 | 0.11444 | 0.16479 | 120.3003 | -0.14191 | -0.064087 | 120.4056 | 120.2362 | 120.3049 | -0.064087 | 0.004578 | 120.4056 | -0.10986 | -0.004578 | 120.4102 | 120.4193 | 120.369 | 0.013733 | -0.036621 | 0.10529 | -0.004577 | 0.004578 | -0.050354 | -0.082397 | -0.15564 | 120.2179 | 120.2499 | -0.05951 | 0.045776 | 120.2957 | 120.3552 | 120.2316 | 120.3003
2733.8281 | 120.8313 | -120.3918 | 0.11444 | -0.0016785 | 6.9765 | 0.01869 | -0.0053534 | 0.0041998 | -0.0065411 | -0.0012988 | -0.14398 | 0.003514 | 0.013324 | 0.012563 | -0.0072675 | 0.028948 | -0.0030784 | 0.050354 | -0.068665 | 0.059509 | 0.091553 | 0.14648 | -0.07782 | -0.16937 | 0.10986 | 0.004578 | 0.022888 | 0.12817 | 0.15106 | 0.054932 | 0.07782 | 120.4514 | -0.18311 | -0.022888 | 120.5383 | 120.2225 | 120.314 | -0.22888 | -0.13733 | 120.4147 | -0.10986 | 0.013733 | 120.5429 | 120.4697 | 120.4468 | 0.054932 | 0.032044 | 0.086975 | 0.032044 | 0.12817 | 0.10529 | -0.12817 | -0.01831 | 120.3232 | 120.3964 | -0.054932 | -0.091553 | 120.4834 | 120.52 | 120.4422 | 120.5017
2735.5625 | 120.8176 | -120.5017 | 0.09613 | -0.0016785 | 6.978 | 0.015058 | -0.0064216 | 0.00185 | -0.0052595 | -0.0036486 | -0.043274 | 0.0013778 | 0.01546 | 0.015767 | -0.0070539 | 0.029803 | -0.0028646 | 0 | -0.036621 | 0.041199 | 0.036621 | 0.13733 | 0.036621 | -0.022888 | 0.013733 | 0 | 0.022888 | 0.064087 | 0.086975 | 0.054932 | 0.16022 | 120.5429 | -0.13275 | -0.059509 | 120.639 | 120.4788 | 120.5383 | -0.064087 | -0.004578 | 120.5246 | -0.09613 | -0.032043 | 120.5887 | 120.6619 | 120.5566 | 0.13733 | 0.032044 | 0.09613 | -0.004578 | 0.064087 | 0.041199 | -0.07782 | -0.022888 | 120.4651 | 120.5017 | -0.054931 | -0.073242 | 120.5383 | 120.5658 | 120.5017 | 120.5154
2737.3125 | 120.8817 | -120.5521 | 0.1236 | 0.02121 | 6.9767 | 0.01634 | -0.0047126 | -0.0024224 | -0.0106 | -0.002367 | -0.10126 | 0.0026596 | 0.011828 | 0.016836 | -0.0085491 | 0.026171 | -0.0041464 | 0.018311 | -0.059509 | 0.054932 | 0.09613 | 0.19226 | 0.041199 | -0.082397 | 0.07782 | 0 | 0.036621 | 0.091553 | 0.14191 | 0.091553 | 0.022888 | 120.607 | -0.1831 | -0.027466 | 120.7443 | 120.4697 | 120.5933 | -0.13733 | -0.013733 | 120.5887 | -0.1236 | -0.032043 | 120.694 | 120.575 | 120.6436 | -0.013733 | 0.054932 | 0.13733 | 0.041198 | 0.10529 | 0.054932 | -0.11444 | -0.036621 | 120.4926 | 120.5521 | -0.068664 | -0.086975 | 120.6482 | 120.6436 | 120.5704 | 120.6299
2739 | 120.9412 | -120.5704 | 0.11444 | 0.005951 | 6.9771 | 0.015486 | -0.003858 | -0.00049983 | -0.0063275 | -1.7026e-05 | -0.015808 | 0.0011642 | 0.012256 | 0.010213 | -0.0094037 | 0.026598 | -0.001583 | 0.032043 | -0.050354 | 0.045776 | 0.086975 | 0.21057 | 0.13275 | 0.073242 | 0.091553 | 0.004578 | 0.027466 | 0.13275 | 0.16479 | 0.13733 | 0.19684 | 120.6162 | -0.16479 | -0.027466 | 120.7809 | 120.6436 | 120.7031 | 0.027466 | 0.086975 | 120.5978 | -0.10986 | 0.01831 | 120.7352 | 120.7672 | 120.7077 | 0.16937 | 0.10986 | 0.1648 | 0.041199 | 0.13733 | 0.10529 | -0.09613 | -0.022888 | 120.52 | 120.575 | -0.068665 | -0.086975 | 120.6573 | 120.7031 | 120.6024 | 120.6619
2740.75 | 120.9274 | -120.6024 | 0.10071 | -0.0016785 | 6.9789 | 0.019758 | -0.00279 | 0.00014097 | -0.0099591 | -0.0010852 | -0.01886 | 0.0013778 | 0.014819 | 0.010641 | -0.0070539 | 0.02788 | -0.002651 | 0.041199 | -0.045776 | 0.050354 | 0.091553 | 0.20599 | 0.07782 | 0.018311 | 0.09613 | -0.004578 | 0.032043 | 0.11902 | 0.14191 | 0.073242 | 0.17853 | 120.6528 | -0.14648 | -0.009155 | 120.8084 | 120.6207 | 120.6802 | -0.032043 | 0.027466 | 120.6345 | -0.10529 | 0.018311 | 120.7443 | 120.7809 | 120.6757 | 0.14648 | 0.041199 | 0.15564 | 0.041199 | 0.10986 | 0.086976 | -0.09613 | -0.036621 | 120.5566 | 120.5978 | -0.050354 | -0.068665 | 120.694 | 120.7214 | 120.6436 | 120.6985
2742.4219 | 120.8588 | -120.6848 | 0.16022 | 0.005951 | 6.9765 | 0.015272 | -0.00065359 | 0.0033454 | -0.0073957 | -0.0021532 | -0.20197 | 0.000737 | 0.012256 | 0.0053 | -0.010899 | 0.028521 | -0.005001 | -0.045776 | -0.009155 | -0.013733 | -0.036621 | 0.054932 | -0.12817 | -0.33875 | -0.073242 | 0.036621 | -0.022888 | -0.027466 | 0.027466 | -0.013733 | -0.15106 | 120.6711 | -0.16937 | -0.19684 | 120.7397 | 120.3461 | 120.5566 | -0.32501 | -0.11444 | 120.6619 | -0.1236 | -0.18768 | 120.7123 | 120.5338 | 120.6711 | -0.12817 | 0.009155 | 0.068665 | -0.022888 | 0.050354 | -0.004578 | 0.004578 | 0.059509 | 120.6757 | 120.7214 | -0.17395 | -0.1831 | 120.6482 | 120.6573 | 120.639 | 120.6116
2744.1719 | 121.0281 | -120.6482 | 0.11444 | -0.009308 | 6.9761 | 0.018049 | -0.002149 | 0.00014097 | -0.0099591 | -0.00065803 | -0.00054933 | -0.0001174 | 0.012256 | 0.014272 | -0.0096173 | 0.027453 | -0.0024374 | 0.041199 | -0.054932 | 0.064087 | 0.10986 | 0.24719 | 0.13733 | 0.13733 | 0.10986 | 0.004578 | 0.054932 | 0.10986 | 0.18768 | 0.1236 | 0.1831 | 120.7123 | -0.16937 | -0.004578 | 120.8954 | 120.7855 | 120.7855 | 0.073242 | 0.073242 | 120.7031 | -0.10986 | -0.004578 | 120.8359 | 120.8313 | 120.7718 | 0.12817 | 0.068664 | 0.1831 | 0.045776 | 0.13275 | 0.054931 | -0.11902 | -0.050354 | 120.5933 | 120.6528 | -0.050354 | -0.059509 | 120.7581 | 120.7581 | 120.6894 | 120.7581
2745.9062 | 120.9778 | -120.6802 | 0.11902 | -0.0016785 | 6.9759 | 0.016554 | -0.0032172 | -0.004345 | -0.0095319 | -1.7026e-05 | 0.0025025 | 0.0028732 | 0.012469 | 0.014272 | -0.0094037 | 0.028734 | -0.00072839 | -0.013733 | -0.059509 | 0.041199 | 0.013733 | 0.12817 | 0.045776 | 0.036621 | 0 | 0.027466 | 0.018311 | 0.045776 | 0.11444 | 0.050354 | 0.14191 | 120.7214 | -0.17853 | -0.10529 | 120.8084 | 120.7169 | 120.726 | -0.004578 | 0.004577 | 120.6985 | -0.091553 | -0.073243 | 120.7947 | 120.8221 | 120.7306 | 0.1236 | 0.032043 | 0.086975 | -0.027466 | 0.09613 | 0.027465 | -0.10071 | 0.009155 | 120.6207 | 120.7077 | -0.07782 | -0.10071 | 120.694 | 120.726 | 120.6665 | 120.6802
2747.6094 | 121.0419 | -120.7031 | 0.091553 | 0.005951 | 6.9782 | 0.015272 | -0.003858 | 0.0020636 | -0.0106 | -0.00023063 | 0.0025025 | 0.002446 | 0.012042 | 0.012136 | -0.0089765 | 0.02788 | -0.0039328 | 0.041199 | -0.050354 | 0.059509 | 0.10529 | 0.24261 | 0.12817 | 0.11902 | 0.11902 | -0.013733 | 0.032043 | 0.091553 | 0.19226 | 0.13733 | 0.19684 | 120.7626 | -0.14191 | 0.013733 | 120.9457 | 120.8221 | 120.8313 | 0.05951 | 0.068665 | 120.7352 | -0.10529 | 0 | 120.8954 | 120.9 | 120.8405 | 0.1648 | 0.10529 | 0.18311 | 0.045777 | 0.16022 | 0.05951 | -0.10986 | -0.045776 | 120.6528 | 120.6894 | -0.032044 | -0.05951 | 120.8084 | 120.7947 | 120.7443 | 120.8221
2749.375 | 121.0785 | -120.7214 | 0.11444 | -0.0016785 | 6.9765 | 0.016767 | -0.0032172 | 0.00099557 | -0.0071821 | 0.001051 | 0.0025025 | 0.0028732 | 0.015033 | 0.014486 | -0.0070539 | 0.032152 | -0.00030119 | 0.045776 | -0.054932 | 0.059509 | 0.091553 | 0.1831 | 0.07782 | 0.07782 | 0.10071 | -0.004578 | 0.045776 | 0.11444 | 0.16479 | 0.10071 | 0.19226 | 120.7809 | -0.16937 | -0.022888 | 120.9045 | 120.7993 | 120.7993 | 0.018311 | 0.018311 | 120.7672 | -0.11902 | 0 | 120.8862 | 120.9137 | 120.8221 | 0.14648 | 0.054932 | 0.1236 | 0.032044 | 0.11902 | 0.068665 | -0.11444 | -0.050354 | 120.6665 | 120.7169 | -0.054932 | -0.068665 | 120.813 | 120.8359 | 120.7672 | 120.8221
2751.0625 | 120.8679 | -120.813 | 0.15564 | -0.0016785 | 6.9765 | 0.017195 | -0.0032172 | -0.0039178 | -0.010173 | -0.0021532 | -0.015808 | 0.0039414 | 0.012897 | 0.011709 | -0.011754 | 0.028307 | -0.0037192 | -0.050354 | -0.018311 | 0.009155 | -0.050354 | 0.059509 | 0 | -0.018311 | -0.068665 | 0.032043 | -0.009155 | -0.036621 | 0.045776 | -0.027466 | 0.064087 | 120.8221 | -0.17395 | -0.20599 | 120.8725 | 120.7947 | 120.813 | -0.027466 | -0.009155 | 120.8038 | -0.1236 | -0.19226 | 120.8588 | 120.8771 | 120.7855 | 0.073242 | -0.018311 | 0.050354 | -0.059509 | 0.054931 | -0.027466 | -0.027466 | 0.041198 | 120.7947 | 120.845 | -0.14649 | -0.16479 | 120.7626 | 120.7764 | 120.7626 | 120.7443
2752.8125 | 121.0373 | -120.7993 | 0.11902 | 0.005951 | 6.9797 | 0.016981 | -0.003858 | 0.0033454 | -0.0084637 | -0.00065803 | -0.00054933 | 0.0018052 | 0.012897 | 0.011495 | -0.012608 | 0.027453 | -0.0030784 | 0.032043 | -0.041199 | 0.054932 | 0.073242 | 0.19226 | 0.10071 | 0.059509 | 0.036621 | 0.009155 | 0.022888 | 0.036621 | 0.11902 | 0.045776 | 0.13275 | 120.8542 | -0.16022 | -0.045777 | 120.9915 | 120.8588 | 120.9 | 0.004577 | 0.045776 | 120.8221 | -0.10986 | -0.082398 | 120.9183 | 120.932 | 120.845 | 0.10986 | 0.022888 | 0.13733 | 0.01831 | 0.096131 | 0.013733 | -0.096131 | -0.013733 | 120.7581 | 120.8084 | -0.064087 | -0.096131 | 120.8725 | 120.8359 | 120.8313 | 120.8359
2754.5156 | 120.9274 | -120.8084 | 0.16022 | -0.016937 | 6.978 | 0.014204 | -0.0051398 | 0.00078177 | -0.010814 | -0.0012988 | 0.0055543 | 0.003514 | 0.01076 | -0.00089517 | -0.011113 | 0.028094 | -0.0041464 | -0.07782 | -0.018311 | 0.013733 | -0.045776 | 0.064087 | -0.004578 | -0.013733 | -0.068665 | 0.036621 | -0.013733 | -0.032043 | 0.045776 | -0.009155 | 0.082397 | 120.8221 | -0.17853 | -0.20599 | 120.8725 | 120.7947 | 120.8038 | -0.027466 | -0.018311 | 120.7947 | -0.1236 | -0.19226 | 120.8542 | 120.8908 | 120.7993 | 0.09613 | 0.004578 | 0.050354 | -0.059509 | 0.059509 | -0.01831 | -0.032044 | 0.050354 | 120.7901 | 120.845 | -0.14648 | -0.17395 | 120.7626 | 120.7764 | 120.7306 | 120.7397
2756.2656 | 121.1655 | -120.7993 | 0.11444 | -0.0016785 | 6.9759 | 0.01634 | -0.0047126 | -0.00092703 | -0.0084637 | -0.0019396 | -0.00054933 | 0.0022324 | 0.010974 | 0.014699 | -0.0079083 | 0.031298 | -0.0035056 | 0.022888 | -0.045776 | 0.050354 | 0.082397 | 0.21515 | 0.10986 | 0.10986 | 0.11902 | 0 | 0.036621 | 0.10986 | 0.20599 | 0.12817 | 0.20599 | 120.8496 | -0.16022 | -0.032044 | 121.0144 | 120.9091 | 120.9091 | 0.059509 | 0.059509 | 120.8359 | -0.11444 | -0.004578 | 121.0052 | 121.0052 | 120.9274 | 0.16937 | 0.091553 | 0.16479 | 0.032043 | 0.16937 | 0.073242 | -0.09613 | -0.036621 | 120.7535 | 120.7993 | -0.064087 | -0.07782 | 120.8817 | 120.9091 | 120.8221 | 120.9183
2758.0156 | 121.138 | -120.8267 | 0.11902 | 0.005951 | 6.9782 | 0.016126 | -0.0068488 | 0.0037726 | -0.0071821 | -0.0036486 | -0.0036011 | 0.0013778 | 0.014178 | 0.01235 | -0.0079083 | 0.027453 | -0.0017966 | -0.009155 | -0.036621 | 0.036621 | 0.027466 | 0.14648 | 0.032043 | 0.041199 | 0.018311 | 0.004578 | 0.022888 | 0.045776 | 0.10529 | 0.064087 | 0.14648 | 120.8633 | -0.15564 | -0.091553 | 120.9732 | 120.8679 | 120.8588 | 0.004578 | -0.004578 | 120.8496 | -0.11444 | -0.073243 | 120.932 | 120.9732 | 120.8908 | 0.1236 | 0.041199 | 0.10986 | -0.009155 | 0.082398 | 0.022888 | -0.073242 | -0.01831 | 120.7901 | 120.8313 | -0.082398 | -0.096131 | 120.8542 | 120.8725 | 120.8176 | 120.845
2759.7812 | 120.9915 | -120.726 | 0.14648 | 0.005951 | 6.9799 | 0.01634 | -0.0030036 | 0.00035457 | -0.0082501 | -0.001726 | 0.0025025 | 0.0026596 | 0.0099057 | 0.0016684 | -0.0091901 | 0.027239 | -0.0028646 | -0.018311 | -0.018311 | 0.013733 | -0.045776 | 0.013733 | -0.059509 | -0.050354 | -0.086975 | 0.045776 | -0.004578 | -0.009155 | 0.009155 | -0.050354 | 0.09613 | 120.7397 | -0.16479 | -0.19226 | 120.7397 | 120.6757 | 120.6665 | -0.064087 | -0.073242 | 120.7214 | -0.10071 | -0.15564 | 120.7352 | 120.8221 | 120.6757 | 0.10071 | -0.045776 | 0 | -0.059509 | 0.013733 | -0.004577 | -0.032044 | 0.050354 | 120.7077 | 120.7718 | -0.13275 | -0.15106 | 120.6802 | 120.7169 | 120.7077 | 120.639
2761.4531 | 121.2112 | -120.8725 | 0.12817 | -0.009308 | 6.9746 | 0.01634 | -0.0062078 | 0.00056817 | -0.0097455 | -0.00065803 | -0.00054933 | 0.0013778 | 0.012042 | 0.010427 | -0.0094037 | 0.028734 | -0.0030784 | 0.054932 | -0.050354 | 0.036621 | 0.10071 | 0.23346 | 0.13275 | 0.09613 | 0.09613 | 0.004578 | 0.059509 | 0.091553 | 0.19684 | 0.13275 | 0.19226 | 120.9091 | -0.17853 | -0.027466 | 121.106 | 120.9686 | 121.0052 | 0.059509 | 0.09613 | 120.932 | -0.1236 | -0.036621 | 121.0693 | 121.0648 | 121.0052 | 0.13275 | 0.073242 | 0.19684 | 0.064087 | 0.13733 | 0.032044 | -0.086975 | -0.054931 | 120.8221 | 120.8771 | -0.091553 | -0.068665 | 120.9732 | 120.9641 | 120.9274 | 120.9686
2763.125 | 121.0236 | -120.607 | 0.12817 | -0.009308 | 6.9791 | 0.016981 | -0.0015082 | -0.0013544 | -0.0093183 | -0.00023063 | 0.0055543 | 0.0013778 | 0.013537 | 0.011922 | -0.0089765 | 0.029162 | -0.002651 | 0 | -0.018311 | 0.032043 | 0.036621 | 0.13733 | 0.022888 | 0.018311 | 0.036621 | 0.027466 | 0.009155 | 0.041199 | 0.10071 | 0.022888 | 0.1236 | 120.639 | -0.14649 | -0.091553 | 120.7443 | 120.6253 | 120.6299 | -0.013732 | -0.009155 | 120.6162 | -0.10071 | -0.086975 | 120.7077 | 120.7306 | 120.6299 | 0.11444 | 0.013733 | 0.10529 | 0.004578 | 0.091553 | 0.032044 | -0.050354 | 0.018311 | 120.5887 | 120.6345 | -0.096131 | -0.11902 | 120.6436 | 120.6482 | 120.607 | 120.6436
2764.875 | 91.4658 | -108.9569 | 0.36621 | -0.0016785 | 6.9778 | 0.016554 | -0.017957 | -0.0024224 | -0.0091047 | -0.001726 | 0.039123 | -0.008876 | 0.0094785 | 0.0074362 | -0.015385 | 0.025103 | -0.017605 | -0.054932 | 0.37994 | 0.2243 | 0.35248 | 0.036621 | -0.31128 | 0.073242 | -0.07782 | -0.1831 | -0.082397 | -0.11444 | -0.091553 | -0.33875 | 0.082397 | 109.1812 | 0.013733 | -0.013733 | 108.9935 | 109.0302 | 108.6456 | -0.15106 | -0.53558 | 108.8745 | -0.54932 | -0.48065 | 108.8654 | 109.0393 | 108.6182 | 0.16479 | -0.25635 | -0.18768 | 0.12817 | -0.009156 | -0.032044 | 0.15564 | -0.10071 | 109.3369 | 108.7738 | -0.14191 | -0.44861 | 109.3094 | 108.8425 | 108.902 | 108.8791
2766.625 | 120.8496 | -120.3964 | 0.10529 | -0.0016785 | 6.9763 | 0.018904 | -0.0036444 | -0.0011408 | -0.0063275 | -0.0015124 | -0.24164 | 0.0013778 | 0.015033 | 0.014272 | -0.0053449 | 0.031084 | -0.00072839 | -0.11444 | -0.027466 | 0.086975 | -0.022888 | -0.15564 | -0.28381 | -0.24719 | 0.073242 | -0.2243 | 0.40283 | 0.13275 | -0.018311 | -0.1236 | -0.041199 | 120.4834 | -0.13275 | -0.12817 | 120.2408 | 120.1492 | 120.1126 | -0.33417 | -0.37079 | 120.7993 | -0.32959 | 0.027465 | 120.3781 | 120.3552 | 120.2728 | -0.44403 | -0.52643 | -0.24261 | -0.10986 | -0.42114 | -0.27008 | -0.11444 | -0.62714 | 120.369 | 120.1721 | -0.018311 | 0.29755 | 120.3735 | 120.5292 | 120.282 | 120.4697
2768.3125 | 120.9549 | -120.6299 | 0.1236 | 0.02121 | 6.9778 | 0.015272 | -0.021162 | -0.013104 | -0.0088911 | -0.011125 | 0.045227 | 0.028081 | 0.0092649 | 0.0082906 | -0.022221 | 0.013994 | -0.022518 | -0.045776 | -0.018311 | 0.022888 | -0.3479 | 0.082397 | 0.082397 | 0.07782 | -0.018311 | -0.13275 | 0.25177 | 0.022888 | -0.059509 | 0.073242 | 0.07782 | 120.6528 | -0.14191 | -0.4715 | 120.7123 | 120.7077 | 120.7123 | 0.054932 | 0.059509 | 120.8817 | -0.25635 | -0.10071 | 120.5704 | 120.7077 | 120.7031 | -0.17395 | -0.17853 | 0.059509 | -0.37079 | -0.31128 | -0.22888 | -0.041199 | -0.38452 | 120.6116 | 120.4971 | -0.10071 | 0.12817 | 120.282 | 120.6528 | 120.5841 | 120.6116
2770 | 121.0556 | -120.6894 | 0.1236 | -0.0016785 | 6.9756 | 0.018049 | -0.0042852 | -0.0024224 | -0.0099591 | -0.00065803 | -0.058533 | -0.0001174 | 0.013324 | 0.013204 | -0.010899 | 0.028734 | -0.0020102 | -0.032043 | -0.059509 | 0.059509 | 0.027466 | 0.15564 | 0.054932 | 0 | 0.032043 | 0.013733 | 0.018311 | 0.07782 | 0.13275 | 0.10529 | 0.19226 | 120.7489 | -0.1831 | -0.09613 | 120.845 | 120.6894 | 120.7443 | -0.059509 | -0.004577 | 120.7077 | -0.10986 | -0.045776 | 120.8221 | 120.8817 | 120.7947 | 0.17395 | 0.086975 | 0.096131 | -0.032043 | 0.11444 | 0.059509 | -0.11902 | -0.004578 | 120.6299 | 120.7031 | -0.064087 | -0.10528 | 120.7169 | 120.7672 | 120.6573 | 120.7214
2771.75 | 121.0693 | -120.7809 | 0.10986 | -0.0016785 | 6.9763 | 0.017622 | -0.003858 | -0.0017816 | -0.0078229 | -0.00087163 | -0.043274 | 0.0013778 | 0.01311 | 0.020254 | -0.0081219 | 0.029162 | 0.00055321 | -0.027466 | -0.045776 | 0.041199 | 0.018311 | 0.11444 | 0.036621 | -0.022888 | 0.004578 | 0.013733 | 0.018311 | 0.032043 | 0.082397 | 0.064087 | 0.15564 | 120.8221 | -0.15564 | -0.091552 | 120.8954 | 120.7581 | 120.8176 | -0.064087 | -0.004578 | 120.7993 | -0.09613 | -0.07782 | 120.8633 | 120.9366 | 120.845 | 0.13733 | 0.045776 | 0.073242 | -0.022888 | 0.064086 | 0.013732 | -0.086975 | -0.004578 | 120.7352 | 120.7947 | -0.068664 | -0.091552 | 120.7993 | 120.813 | 120.7535 | 120.7855
2773.4375 | 120.726 | -120.4514 | 0.12817 | 0.01358 | 6.9771 | 0.017622 | -0.016248 | 0.011249 | -0.0080365 | -0.013048 | 0.045227 | 0.028508 | 0.0094785 | -0.0023904 | 0.034389 | 0.04497 | -0.020168 | 0.004578 | -0.013733 | 0.027466 | -0.14191 | 0.091553 | 0.073242 | 0.086975 | -0.027466 | 0.036621 | 0.27466 | 0.022888 | -0.15106 | 0.082397 | 0.073242 | 120.4788 | -0.14191 | -0.27008 | 120.5429 | 120.5383 | 120.5246 | 0.059509 | 0.045776 | 120.726 | -0.091553 | -0.10529 | 120.3003 | 120.5246 | 120.5338 | -0.20142 | -0.19226 | 0.064087 | -0.16937 | -0.42572 | -0.25177 | -0.041199 | -0.23804 | 120.4376 | 120.488 | -0.10071 | 0.14648 | 120.3094 | 120.4742 | 120.4559 | 120.4239
2775.1875 | 120.8908 | -120.6528 | 0.14648 | -0.009308 | 6.978 | 0.016981 | -0.0030036 | -0.006695 | -0.0099591 | -0.0070666 | 0.036072 | -0.0041764 | 0.012897 | -0.0036722 | -0.024571 | 0.009722 | -0.017605 | 0.018311 | -0.013733 | 0.022888 | -0.082397 | -0.21973 | 0.082397 | 0.07782 | 0.018311 | 0.027466 | 0.027466 | 0.050354 | -0.004578 | -0.045776 | 0.07782 | 120.6757 | -0.16022 | -0.22888 | 120.433 | 120.7306 | 120.7352 | 0.054932 | 0.059509 | 120.6802 | -0.11902 | -0.09613 | 120.6482 | 120.7306 | 120.607 | 0.050354 | -0.073242 | -0.24261 | -0.10528 | -0.032044 | 0.022888 | -0.036621 | 0 | 120.639 | 120.6802 | -0.1236 | -0.11902 | 120.5704 | 120.7031 | 120.6711 | 120.6711
2776.875 | 121.0052 | -120.7169 | 0.12817 | -0.0016785 | 6.9774 | 0.017835 | -0.0023626 | 0.0024908 | -0.0086773 | -0.003435 | -0.046326 | 0.0009506 | 0.010974 | 0.013204 | -0.0087629 | 0.03023 | -0.00030119 | -0.018311 | -0.059509 | 0.059509 | 0.027466 | 0.14191 | 0.050354 | -0.013733 | 0.013733 | 0.004578 | 0.004578 | 0.059509 | 0.09613 | 0.045776 | 0.15106 | 120.7764 | -0.18768 | -0.10071 | 120.8588 | 120.7031 | 120.7672 | -0.073242 | -0.009155 | 120.7214 | -0.1236 | -0.068665 | 120.813 | 120.8679 | 120.7626 | 0.14648 | 0.041198 | 0.082398 | -0.032043 | 0.091552 | 0.054931 | -0.11902 | 0 | 120.6573 | 120.7214 | -0.068665 | -0.1236 | 120.7443 | 120.7764 | 120.6985 | 120.7306
2778.625 | 121.0876 | -120.7123 | 0.11902 | -0.0016785 | 6.9771 | 0.015486 | -0.0030036 | 0.0031318 | -0.0078229 | -0.0012988 | -0.18976 | 0.000737 | 0.011401 | 0.01235 | -0.0047039 | 0.029162 | 0.00012601 | -0.022888 | -0.032043 | 0.036621 | 0.018311 | 0.091553 | -0.16022 | -0.32044 | 0.036621 | -0.009155 | 0.022888 | 0.09613 | 0.13275 | 0.064087 | 0.036621 | 120.7489 | -0.15106 | -0.10071 | 120.8038 | 120.3918 | 120.5521 | -0.35706 | -0.19684 | 120.7352 | -0.12817 | -0.022889 | 120.845 | 120.7489 | 120.7764 | 0.013733 | 0.041199 | 0.054932 | -0.01831 | 0.10986 | 0.073242 | -0.068664 | -0.032043 | 120.6802 | 120.7031 | -0.082398 | -0.096131 | 120.7306 | 120.8084 | 120.6894 | 120.7489
2780.375 | 121.1655 | -120.7764 | 0.11902 | -0.0016785 | 6.9754 | 0.014631 | -0.0051398 | -0.0013544 | -0.0093183 | -0.003435 | -0.012756 | 0.000737 | 0.016101 | 0.013204 | -0.0098309 | 0.029375 | -0.00030119 | 0.027466 | -0.045776 | 0.041199 | 0.082397 | 0.22888 | 0.12817 | 0.082397 | 0.13275 | 0 | 0.041199 | 0.10529 | 0.19684 | 0.15106 | 0.20599 | 120.8176 | -0.16479 | -0.036622 | 121.0052 | 120.8588 | 120.9045 | 0.041198 | 0.086975 | 120.8176 | -0.11902 | -0.013733 | 120.9732 | 120.9824 | 120.9274 | 0.1648 | 0.10986 | 0.18768 | 0.041198 | 0.15564 | 0.064087 | -0.086975 | -0.041199 | 120.7306 | 120.7764 | -0.07782 | -0.07782 | 120.8588 | 120.8817 | 120.8038 | 120.9091
2782.1094 | 121.019 | -120.6894 | 0.13733 | -0.0016785 | 6.9795 | 0.019972 | -0.0025764 | -0.0081902 | -0.0091047 | -0.010057 | -0.17755 | 0.028722 | 0.010119 | 0.01235 | -0.01154 | 0.022326 | -0.0037192 | -0.027466 | -0.018311 | 0.013733 | -0.027466 | -0.10071 | -0.12817 | 0.082397 | -0.045776 | 0.027466 | 0.004578 | -0.018311 | 0.027466 | -0.29297 | 0.10071 | 120.7031 | -0.15564 | -0.16479 | 120.5887 | 120.7718 | 120.5612 | 0.068664 | -0.14191 | 120.694 | -0.10986 | -0.15564 | 120.7169 | 120.7901 | 120.3964 | 0.09613 | -0.29755 | -0.11444 | -0.041199 | 0.022888 | -0.022889 | -0.032044 | 0.022888 | 120.6711 | 120.7169 | -0.1236 | -0.13275 | 120.6619 | 120.6711 | 120.6619 | 120.6436
2783.7969 | 120.9915 | -120.8588 | 0.14191 | -0.0016785 | 6.9769 | 0.014631 | -0.0023626 | -0.00071343 | -0.0086773 | 0.00083737 | -0.23859 | 0.0033004 | 0.013324 | 0.011068 | -0.012395 | 0.028521 | -0.0020102 | -0.068665 | -0.027466 | 0.009155 | -0.054932 | 0.064087 | -0.17395 | -0.37994 | -0.073242 | 0.036621 | -0.013733 | -0.036621 | 0.022888 | -0.064087 | -0.21057 | 120.8679 | -0.16937 | -0.19684 | 120.9229 | 120.4788 | 120.6848 | -0.3891 | -0.1831 | 120.845 | -0.10529 | -0.17853 | 120.8817 | 120.6482 | 120.7947 | -0.19684 | -0.050354 | 0.054932 | -0.064087 | 0.036621 | -0.022888 | -0.036621 | 0.050354 | 120.8313 | 120.8954 | -0.13275 | -0.15564 | 120.8038 | 120.8221 | 120.7901 | 120.7855
2785.5469 | 121.1929 | -120.8313 | 0.10529 | 0.005951 | 6.9774 | 0.016554 | -0.0030036 | 0.00014097 | -0.0088911 | -0.002367 | -0.11041 | 0.0015914 | 0.011828 | 0.016836 | -0.0059857 | 0.031725 | -0.0024374 | 0.036621 | -0.073242 | 0.045776 | 0.07782 | 0.18768 | 0.073242 | -0.10071 | 0.082397 | -0.013733 | 0.018311 | 0.12817 | 0.15564 | 0.09613 | 0.21515 | 120.8771 | -0.17853 | -0.027466 | 121.019 | 120.7306 | 120.9045 | -0.14648 | 0.027466 | 120.8496 | -0.11902 | 0.022888 | 120.9869 | 121.0464 | 120.9274 | 0.19684 | 0.077819 | 0.14191 | 0.032044 | 0.13733 | 0.10986 | -0.11902 | -0.032044 | 120.7581 | 120.8176 | -0.05951 | -0.086975 | 120.9091 | 120.9595 | 120.8679 | 120.9137
2787.2969 | 121.2341 | -120.8771 | 0.10071 | -0.016937 | 6.9754 | 0.015272 | -0.0057806 | -0.0013544 | -0.0091047 | -0.002367 | 0.0025025 | -0.0007584 | 0.013324 | 0.015127 | -0.011967 | 0.028307 | -0.0037192 | 0.018311 | -0.050354 | 0.054932 | 0.086975 | 0.21057 | 0.11444 | 0.1236 | 0.12817 | -0.013733 | 0.018311 | 0.091553 | 0.17853 | 0.11902 | 0.21057 | 120.932 | -0.15106 | -0.013733 | 121.0876 | 121.0007 | 120.9915 | 0.068664 | 0.059509 | 120.8954 | -0.11444 | -0.009155 | 121.0556 | 121.0876 | 120.9961 | 0.19226 | 0.10071 | 0.15564 | 0.032043 | 0.16022 | 0.073242 | -0.10529 | -0.032044 | 120.8267 | 120.8633 | -0.045776 | -0.082397 | 120.9641 | 120.9686 | 120.8954 | 121.0052
2788.9688 | 120.9778 | -120.8633 | 0.10986 | -0.0016785 | 6.9776 | 0.01399 | -0.0015082 | 0.00035457 | -0.0080365 | 0.00062377 | -0.13177 | 0.0026596 | 0.012683 | 0.0059408 | -0.0081219 | 0.029589 | -0.002651 | -0.036621 | -0.018311 | 0.032043 | -0.036621 | 0.059509 | -0.054932 | -0.26093 | -0.032043 | 0.027466 | 0.009155 | 0.027466 | 0.068665 | 0 | 0.09613 | 120.8954 | -0.12817 | -0.14648 | 120.9229 | 120.6024 | 120.8084 | -0.29297 | -0.086975 | 120.8725 | -0.082397 | -0.082397 | 120.932 | 120.9595 | 120.8633 | 0.086975 | -0.009155 | 0.027466 | -0.068664 | 0.05951 | 0.018311 | -0.050354 | 0.018311 | 120.845 | 120.8908 | -0.07782 | -0.10071 | 120.8267 | 120.8908 | 120.8267 | 120.8313
2790.7188 | 121.2799 | -120.9091 | 0.09613 | -0.009308 | 6.9791 | 0.015486 | -0.0042852 | -0.0011408 | -0.0095319 | -0.0012988 | -0.00054933 | 0.0015914 | 0.013324 | 0.018117 | -0.0094037 | 0.028521 | -0.0028646 | 0.013733 | -0.050354 | 0.032043 | 0.064087 | 0.19684 | 0.10529 | 0.091553 | 0.07782 | -0.004578 | 0.018311 | 0.10529 | 0.17853 | 0.14191 | 0.20142 | 120.9412 | -0.14648 | -0.032043 | 121.106 | 121.0007 | 121.0144 | 0.05951 | 0.073243 | 120.9274 | -0.10071 | 0.009156 | 121.0876 | 121.1105 | 121.051 | 0.18311 | 0.1236 | 0.1648 | 0.032044 | 0.16022 | 0.086975 | -0.082397 | -0.022889 | 120.8588 | 120.9045 | -0.064087 | -0.077819 | 120.9732 | 121.0144 | 120.9229 | 120.9869
2792.4062 | 121.1746 | -120.9 | 0.10529 | -0.009308 | 6.9789 | 0.018263 | -0.00279 | 0.0024908 | -0.0082501 | -0.0010852 | -0.028015 | 0.002446 | 0.012256 | 0.010427 | -0.0053449 | 0.028734 | -0.0030784 | -0.018311 | -0.027466 | 0.032043 | 0.045776 | 0.1236 | 0.036621 | -0.013733 | 0.050354 | -0.004578 | 0.032043 | 0.086975 | 0.13733 | 0.07782 | 0.19684 | 120.932 | -0.13275 | -0.05951 | 121.0236 | 120.8862 | 120.9366 | -0.045776 | 0.004578 | 120.932 | -0.10986 | -0.018311 | 121.0373 | 121.0968 | 120.9778 | 0.1648 | 0.045777 | 0.091553 | 0.013733 | 0.10529 | 0.054932 | -0.059509 | -0.036621 | 120.8725 | 120.8954 | -0.073243 | -0.073243 | 120.9457 | 120.9869 | 120.8817 | 120.9503
2794.0781 | 121.2891 | -120.9549 | 0.11444 | -0.009308 | 6.9761 | 0.015913 | -0.005567 | 0.0016364 | -0.0086773 | -0.0025806 | -0.00054933 | 0.0015914 | 0.013324 | 0.013204 | -0.01154 | 0.029375 | -0.0041464 | 0.041199 | -0.064087 | 0.045776 | 0.086975 | 0.21515 | 0.12817 | 0.10529 | 0.11444 | 0.004578 | 0.027466 | 0.073242 | 0.19226 | 0.13275 | 0.1831 | 121.0007 | -0.17853 | -0.027466 | 121.17 | 121.0602 | 121.0831 | 0.05951 | 0.082398 | 120.9824 | -0.10986 | -0.041199 | 121.1472 | 121.138 | 121.0876 | 0.15564 | 0.10529 | 0.16937 | 0.041199 | 0.16479 | 0.045776 | -0.10986 | -0.022888 | 120.8908 | 120.9595 | -0.068665 | -0.086975 | 121.0419 | 121.0281 | 120.9961 | 121.0693
2795.8281 | 120.9457 | -120.8862 | 0.15564 | -0.009308 | 6.9784 | 0.015058 | -0.0051398 | -0.00071343 | -0.0091047 | -0.0019396 | -0.00054933 | 0.0009506 | 0.012683 | 0.0048728 | -0.012395 | 0.02788 | 0.00076681 | -0.018311 | -0.022888 | 0.032043 | -0.018311 | 0.082397 | 0.013733 | 0.009155 | -0.045776 | 0.027466 | -0.013733 | -0.036621 | 0.041199 | -0.004578 | 0.068665 | 120.9183 | -0.17853 | -0.17395 | 120.9686 | 120.8954 | 120.9 | -0.022888 | -0.01831 | 120.8725 | -0.12817 | -0.19226 | 120.9274 | 120.9549 | 120.8817 | 0.082398 | 0.009155 | 0.050354 | -0.050354 | 0.054932 | -0.022888 | -0.054931 | 0.041199 | 120.8633 | 120.9137 | -0.1236 | -0.16937 | 120.8679 | 120.8496 | 120.8679 | 120.8405
2797.5781 | 121.3531 | -120.9824 | 0.10986 | 0.005951 | 6.9744 | 0.017195 | -0.0032172 | -0.0028498 | -0.0099591 | -1.7026e-05 | 0.0025025 | 0.002446 | 0.011615 | 0.013845 | -0.0076947 | 0.028307 | -8.7586e-05 | 0.013733 | -0.045776 | 0.045776 | 0.07782 | 0.19684 | 0.1236 | 0.10529 | 0.10529 | 0 | 0.013733 | 0.091553 | 0.20142 | 0.14191 | 0.18768 | 121.0281 | -0.15564 | -0.032043 | 121.1792 | 121.0876 | 121.106 | 0.05951 | 0.07782 | 120.9961 | -0.10986 | -0.01831 | 121.1838 | 121.17 | 121.1243 | 0.17395 | 0.12817 | 0.15106 | 0.032044 | 0.18768 | 0.07782 | -0.091552 | -0.013733 | 120.9366 | 120.9824 | -0.064087 | -0.09613 | 121.0602 | 121.0739 | 120.9961 | 121.0876
2799.2656 | 120.8862 | -120.6619 | 0.15564 | 0.005951 | 6.9791 | 0.013136 | -0.0047126 | 0.00099557 | -0.0080365 | -0.001726 | 0.0025025 | 0.0039414 | 0.013751 | 0.007009 | -0.011967 | 0.028307 | -0.003292 | -0.059509 | -0.013733 | -0.009155 | -0.036621 | 0.054932 | -0.004578 | -0.009155 | -0.068665 | 0.054932 | -0.004578 | -0.041199 | 0.022888 | -0.032043 | 0.082397 | 120.6528 | -0.16937 | -0.19226 | 120.7169 | 120.6528 | 120.6573 | 0 | 0.004577 | 120.6573 | -0.10071 | -0.19684 | 120.6848 | 120.7443 | 120.6299 | 0.086975 | -0.027465 | 0.064087 | -0.027466 | 0.027466 | -0.036621 | -0.004578 | 0.05951 | 120.6482 | 120.7169 | -0.16479 | -0.16022 | 120.6253 | 120.6207 | 120.6024 | 120.5933
2800.9531 | 121.1975 | -121.0373 | 0.14191 | -0.0016785 | 6.9754 | 0.015913 | -0.005567 | 0.0031318 | -0.0086773 | -0.0030078 | -0.00054933 | 0.0018052 | 0.012897 | 0.0072226 | -0.011326 | 0.025744 | -0.0013694 | -0.004578 | -0.059509 | 0.027466 | 0.013733 | 0.11902 | 0.032043 | 0.027466 | -0.027466 | 0.027466 | 0 | -0.022888 | 0.059509 | 0.004578 | 0.082397 | 121.0648 | -0.20142 | -0.12817 | 121.1563 | 121.0648 | 121.0693 | 0 | 0.004577 | 121.0373 | -0.11444 | -0.16479 | 121.0968 | 121.1197 | 121.0419 | 0.082397 | 0.004578 | 0.091553 | -0.013733 | 0.059509 | -0.022888 | -0.086975 | 0.027466 | 120.9778 | 121.0648 | -0.11444 | -0.14191 | 121.051 | 121.0144 | 121.0327 | 121.0098
2802.7188 | 120.7993 | -120.3415 | 0.1236 | -0.0016785 | 6.9806 | 0.017408 | -0.004499 | -0.0028498 | -0.0088911 | -0.0015124 | -0.0036011 | 0.0011642 | 0.012042 | 0.011068 | -0.0085491 | 0.027025 | -0.0028646 | 0.009155 | -0.027466 | 0.027466 | 0.018311 | 0.1236 | 0.018311 | 0.013733 | 0.018311 | 0.022888 | 0.009155 | 0.041199 | 0.10529 | 0.036621 | 0.14191 | 120.369 | -0.15106 | -0.10528 | 120.4651 | 120.3552 | 120.3598 | -0.013733 | -0.009155 | 120.3506 | -0.10071 | -0.082397 | 120.4468 | 120.4834 | 120.3781 | 0.13275 | 0.027466 | 0.09613 | -0.009155 | 0.096131 | 0.032044 | -0.054932 | 0.013733 | 120.314 | 120.3644 | -0.09613 | -0.11444 | 120.3598 | 120.3827 | 120.3506 | 120.3598
2804.4062 | 121.225 | -121.0281 | 0.16022 | -0.0016785 | 6.9803 | 0.016126 | -0.0049262 | 0.0012092 | -0.0097455 | 0.00062377 | 0.0025025 | 0.0013778 | 0.012683 | 0.0085044 | -0.010899 | 0.027666 | -0.0020102 | -0.050354 | -0.027466 | 0.009155 | -0.045776 | 0.068665 | -0.004578 | -0.027466 | -0.059509 | 0.027466 | -0.004578 | -0.041199 | 0.045776 | -0.018311 | 0.059509 | 121.0373 | -0.18768 | -0.20599 | 121.0968 | 121.0007 | 121.0236 | -0.036621 | -0.013733 | 121.0236 | -0.13275 | -0.20142 | 121.0739 | 121.0876 | 121.0098 | 0.064087 | -0.013733 | 0.05951 | -0.054931 | 0.050354 | -0.036621 | -0.036621 | 0.032044 | 121.0007 | 121.0556 | -0.15106 | -0.16479 | 120.9824 | 120.9869 | 120.9778 | 120.9686
2806.0938 | 121.3852 | -121.0602 | 0.10986 | -0.009308 | 6.9771 | 0.015272 | -0.003858 | -0.0075494 | -0.0097455 | -0.0019396 | -0.00054933 | -0.0003312 | 0.012897 | 0.01299 | -0.0091901 | 0.027239 | -0.0028646 | 0.032043 | -0.059509 | 0.036621 | 0.082397 | 0.21057 | 0.10986 | 0.082397 | 0.073242 | -0.009155 | 0.027466 | 0.059509 | 0.18768 | 0.1236 | 0.17395 | 121.0968 | -0.16937 | -0.027466 | 121.2708 | 121.1426 | 121.17 | 0.045776 | 0.073242 | 121.0876 | -0.11902 | -0.050354 | 121.2479 | 121.2341 | 121.1838 | 0.14648 | 0.09613 | 0.17395 | 0.045776 | 0.16022 | 0.032043 | -0.09613 | -0.036621 | 121.0007 | 121.051 | -0.073242 | -0.082397 | 121.1426 | 121.1197 | 121.0922 | 121.1334
2807.8438 | 121.376 | -121.1197 | 0.11444 | -0.009308 | 6.9774 | 0.016554 | -0.0057806 | -7.2628e-05 | -0.0080365 | -0.001726 | 0.0055543 | 0.0003098 | 0.013965 | 0.013204 | -0.010258 | 0.029375 | -0.0017966 | 0.032043 | -0.073242 | 0.050354 | 0.073242 | 0.20599 | 0.10071 | 0.082397 | 0.064087 | -0.004578 | 0.018311 | 0.054932 | 0.14648 | 0.10071 | 0.16022 | 121.17 | -0.18768 | -0.041199 | 121.3257 | 121.2021 | 121.2204 | 0.032043 | 0.050354 | 121.138 | -0.11902 | -0.059509 | 121.2662 | 121.2799 | 121.2204 | 0.14191 | 0.082397 | 0.15564 | 0.022888 | 0.12817 | 0.036621 | -0.1236 | -0.022889 | 121.0464 | 121.1151 | -0.064087 | -0.09613 | 121.1929 | 121.1746 | 121.1517 | 121.1838
2809.6094 | 121.3989 | -121.0922 | 0.11444 | -0.0016785 | 6.9769 | 0.016767 | -0.0062078 | 0.0014228 | -0.0099591 | 0.00019657 | -0.00054933 | 0.0009506 | 0.013324 | 0.0095724 | -0.0081219 | 0.02788 | -0.00436 | 0.027466 | -0.073242 | 0.050354 | 0.082397 | 0.21515 | 0.10529 | 0.086975 | 0.073242 | -0.004578 | 0.027466 | 0.082397 | 0.15564 | 0.10986 | 0.17853 | 121.1426 | -0.18768 | -0.032044 | 121.3074 | 121.1792 | 121.1975 | 0.036621 | 0.054932 | 121.1197 | -0.11902 | -0.032044 | 121.2479 | 121.2708 | 121.2021 | 0.15106 | 0.082397 | 0.16479 | 0.032043 | 0.12817 | 0.054931 | -0.1236 | -0.032044 | 121.019 | 121.0876 | -0.064087 | -0.086975 | 121.1746 | 121.1746 | 121.1197 | 121.1655
2811.2969 | 121.2936 | -120.9732 | 0.14648 | -0.0016785 | 6.9784 | 0.016767 | -0.0036444 | 0.00014097 | -0.0065411 | -0.001726 | 0.0025025 | 0.0033004 | 0.014178 | 0.0076498 | -0.0076947 | 0.03023 | -0.0035056 | -0.036621 | -0.032043 | 0.032043 | -0.059509 | 0.027466 | -0.036621 | -0.054932 | -0.10071 | 0.032043 | -0.018311 | -0.036621 | 0.018311 | -0.050354 | 0.064087 | 121.0052 | -0.17853 | -0.20599 | 121.0007 | 120.9183 | 120.9366 | -0.086975 | -0.068664 | 120.9549 | -0.11444 | -0.18311 | 120.9915 | 121.0373 | 120.9229 | 0.082398 | -0.032043 | -0.004577 | -0.091552 | 0.036622 | -0.01831 | -0.064086 | 0.050354 | 120.9412 | 121.0052 | -0.11444 | -0.16479 | 120.9137 | 120.9366 | 120.9366 | 120.8725
2813.0469 | 121.4264 | -121.1472 | 0.12817 | 0.005951 | 6.9763 | 0.015699 | -0.0049262 | -0.0056268 | -0.0091047 | -0.0012988 | -0.00054933 | 0.000737 | 0.011188 | 0.016622 | -0.0079083 | 0.028094 | -0.00094199 | -0.032043 | -0.054932 | 0.036621 | 0.027466 | 0.14191 | 0.050354 | 0.041199 | 0.027466 | 0 | 0.013733 | 0.059509 | 0.14191 | 0.09613 | 0.16937 | 121.1838 | -0.18311 | -0.10071 | 121.2891 | 121.1884 | 121.1975 | 0.004578 | 0.013733 | 121.1609 | -0.12817 | -0.068665 | 121.2891 | 121.3165 | 121.2433 | 0.15564 | 0.082397 | 0.10529 | -0.009155 | 0.12817 | 0.045776 | -0.091553 | -0.013733 | 121.0922 | 121.1472 | -0.091553 | -0.11444 | 121.1746 | 121.2067 | 121.1151 | 121.1746
2814.8125 | 121.3486 | -121.0098 | 0.13275 | 0.01358 | 6.9797 | 0.014845 | -0.00279 | 0.00035457 | -0.0063275 | -0.0036486 | 0.0025025 | 0.0033004 | 0.015887 | 0.0078634 | -0.0089765 | 0.028948 | -0.0052146 | 0.004578 | -0.018311 | 0.022888 | 0.022888 | 0.09613 | -0.004578 | 0 | -0.018311 | 0.027466 | 0.009155 | 0.004578 | 0.050354 | -0.018311 | 0.091553 | 121.0327 | -0.15106 | -0.10986 | 121.106 | 121.0098 | 121.0052 | -0.022888 | -0.027466 | 121.019 | -0.10529 | -0.12817 | 121.0602 | 121.1014 | 120.9915 | 0.082398 | -0.027466 | 0.073242 | 0 | 0.041199 | -0.004577 | -0.041199 | 0.018311 | 120.9915 | 121.0373 | -0.10986 | -0.1236 | 121.0327 | 121.0144 | 121.0144 | 120.9915
2816.4844 | 121.4813 | -121.138 | 0.10529 | -0.0016785 | 6.9767 | 0.016554 | -0.0059942 | -0.0019952 | -0.0084637 | -0.0025806 | -0.0036011 | 0.0003098 | 0.013537 | 0.01235 | -0.0087629 | 0.029162 | 0.00076681 | -0.009155 | -0.059509 | 0.036621 | 0.041199 | 0.16022 | 0.091553 | 0.073242 | 0.082397 | -0.009155 | 0.036621 | 0.091553 | 0.16022 | 0.11902 | 0.19226 | 121.1746 | -0.16479 | -0.064087 | 121.2982 | 121.2112 | 121.2296 | 0.036621 | 0.054932 | 121.1746 | -0.11444 | -0.013733 | 121.2982 | 121.3303 | 121.257 | 0.15564 | 0.082398 | 0.1236 | 0.004578 | 0.1236 | 0.054932 | -0.09613 | -0.045776 | 121.0785 | 121.1288 | -0.068665 | -0.068665 | 121.1792 | 121.2296 | 121.1288 | 121.2204
2818.2344 | 121.4218 | -121.1563 | 0.14191 | -0.0016785 | 6.9759 | 0.015058 | -0.0030036 | 0.0024908 | -0.0088911 | -0.00044443 | -0.0036011 | 0.0028732 | 0.012256 | 0.0093588 | -0.010045 | 0.025957 | -0.0064962 | 0.004578 | -0.009155 | 0.018311 | 0.018311 | 0.10529 | 0.032043 | 0.018311 | 0.004578 | 0.041199 | 0.013733 | 0.027466 | 0.091553 | 0.009155 | 0.13275 | 121.1746 | -0.15106 | -0.1236 | 121.2616 | 121.1746 | 121.1884 | 0 | 0.013732 | 121.17 | -0.10071 | -0.11444 | 121.2479 | 121.2891 | 121.1655 | 0.11902 | -0.004578 | 0.086975 | 0 | 0.07782 | 0.013733 | -0.027466 | 0.027466 | 121.1472 | 121.1975 | -0.1236 | -0.12817 | 121.1746 | 121.1838 | 121.1609 | 121.1609
2819.9375 | 121.3806 | -121.2021 | 0.15564 | -0.009308 | 6.9769 | 0.014631 | -0.004499 | -7.2628e-05 | -0.0093183 | -0.00044443 | -0.00054933 | 0.000737 | 0.014605 | 0.008718 | -0.012822 | 0.027453 | -0.002651 | -0.027466 | -0.022888 | 0.032043 | -0.032043 | 0.091553 | -0.004578 | -0.004578 | -0.054932 | 0.027466 | 0.009155 | -0.041199 | 0.032043 | -0.009155 | 0.073242 | 121.2341 | -0.17853 | -0.18768 | 121.2936 | 121.1975 | 121.1975 | -0.036621 | -0.036621 | 121.2112 | -0.12817 | -0.19684 | 121.2341 | 121.2753 | 121.1929 | 0.064087 | -0.01831 | 0.05951 | -0.064086 | 0.022888 | -0.050354 | -0.054931 | 0.018311 | 121.1792 | 121.2296 | -0.1236 | -0.14649 | 121.17 | 121.1609 | 121.1746 | 121.1472
2821.6719 | 121.3898 | -121.2433 | 0.14648 | -0.0016785 | 6.9782 | 0.018049 | -0.0049262 | 0.0027044 | -0.0091047 | -0.0012988 | 0.0025025 | 0.0018052 | 0.01546 | 0.0093588 | -0.012608 | 0.026171 | -0.0017966 | -0.032043 | -0.027466 | 0.022888 | -0.018311 | 0.086975 | -0.004578 | 0 | -0.050354 | 0.036621 | 0.004578 | -0.027466 | 0.054932 | 0.009155 | 0.068665 | 121.2662 | -0.17395 | -0.16479 | 121.3303 | 121.2433 | 121.2387 | -0.022888 | -0.027466 | 121.2479 | -0.10986 | -0.17395 | 121.2982 | 121.312 | 121.2524 | 0.064087 | 0.004577 | 0.064087 | -0.041199 | 0.050354 | -0.032044 | -0.050354 | 0.032043 | 121.2158 | 121.2799 | -0.1236 | -0.14191 | 121.225 | 121.2158 | 121.2112 | 121.1929
2823.3438 | 121.4172 | -121.1929 | 0.14648 | -0.009308 | 6.9791 | 0.016981 | -0.0042852 | 0.0046272 | -0.0073957 | -0.0019396 | -0.00054933 | 0.0030868 | 0.013751 | 0.0061544 | -0.0055585 | 0.02788 | -0.0017966 | -0.041199 | -0.018311 | 0.009155 | -0.050354 | 0.032043 | -0.054932 | -0.054932 | -0.07782 | 0.032043 | -0.009155 | 0 | 0.036621 | -0.022888 | 0.086975 | 121.2021 | -0.16479 | -0.19684 | 121.225 | 121.138 | 121.138 | -0.064087 | -0.064087 | 121.1838 | -0.11444 | -0.14648 | 121.2296 | 121.2799 | 121.17 | 0.09613 | -0.013733 | 0.022888 | -0.059509 | 0.045776 | 0.009155 | -0.027466 | 0.041198 | 121.1746 | 121.225 | -0.13733 | -0.15564 | 121.1426 | 121.1929 | 121.1517 | 121.1151
2825.0312 | 121.5683 | -121.1975 | 0.11902 | -0.0016785 | 6.9769 | 0.014631 | -0.0064216 | -0.00049983 | -0.0076093 | -0.0010852 | -0.0066527 | -0.0005448 | 0.012683 | 0.0072226 | -0.010258 | 0.029803 | -0.0030784 | 0.032043 | -0.054932 | 0.041199 | 0.086975 | 0.2243 | 0.11444 | 0.091553 | 0.10529 | 0 | 0.032043 | 0.09613 | 0.18768 | 0.1236 | 0.19684 | 121.2387 | -0.17395 | -0.032044 | 121.4218 | 121.2891 | 121.312 | 0.050354 | 0.073242 | 121.2296 | -0.11902 | -0.022889 | 121.3852 | 121.3943 | 121.3211 | 0.1648 | 0.091553 | 0.18311 | 0.045776 | 0.15564 | 0.064087 | -0.096131 | -0.032043 | 121.1426 | 121.1975 | -0.07782 | -0.086976 | 121.2845 | 121.2936 | 121.2296 | 121.3028
2826.7812 | 121.4676 | -121.2204 | 0.14648 | 0.005951 | 6.9806 | 0.016126 | -0.0023626 | 0.00035457 | -0.0091047 | -0.001726 | 0.0025025 | 0.0015914 | 0.013965 | 0.0029502 | -0.0091901 | 0.028734 | -0.0030784 | -0.009155 | -0.013733 | 0.004578 | 0 | 0.091553 | 0.009155 | 0.009155 | -0.022888 | 0.041199 | 0.009155 | 0.004578 | 0.082397 | 0.032043 | 0.1236 | 121.225 | -0.16022 | -0.14648 | 121.312 | 121.2296 | 121.2296 | 0.004577 | 0.004577 | 121.2296 | -0.10529 | -0.14191 | 121.3028 | 121.344 | 121.2524 | 0.11444 | 0.022888 | 0.086975 | -0.004578 | 0.073242 | -0.004577 | -0.018311 | 0.032044 | 121.2067 | 121.2616 | -0.14191 | -0.13733 | 121.2204 | 121.225 | 121.2112 | 121.1975
2828.5156 | 121.55 | -121.2204 | 0.1236 | -0.0016785 | 6.978 | 0.014631 | -0.0032172 | 0.0048408 | -0.0067547 | -0.0027942 | -0.00054933 | 0.002446 | 0.01311 | 0.012777 | -0.0055585 | 0.02788 | 0.0014078 | -0.027466 | -0.022888 | 0.027466 | -0.009155 | 0.10071 | -0.018311 | 0.009155 | 0.009155 | 0.018311 | 0.018311 | 0.07782 | 0.11444 | 0.064087 | 0.17395 | 121.2479 | -0.14648 | -0.13275 | 121.3211 | 121.2296 | 121.2021 | -0.018311 | -0.045777 | 121.2387 | -0.10528 | -0.045776 | 121.3348 | 121.3943 | 121.2845 | 0.15564 | 0.045776 | 0.073242 | -0.036621 | 0.09613 | 0.059509 | -0.050354 | 0 | 121.1975 | 121.2387 | -0.09613 | -0.10528 | 121.2112 | 121.2982 | 121.1929 | 121.2296
2830.2656 | 121.2387 | -121.0373 | 0.15106 | -0.0016785 | 6.9784 | 0.019758 | -0.0040716 | 0.0033454 | -0.0084637 | -0.0010852 | -0.00054933 | 0.002446 | 0.014178 | 0.00017303 | -0.0085491 | 0.027666 | -0.0017966 | -0.054932 | -0.022888 | 0 | -0.045776 | 0.036621 | -0.073242 | -0.054932 | -0.091553 | 0.027466 | -0.009155 | -0.050354 | 0.004578 | -0.050354 | 0.10071 | 121.0373 | -0.17395 | -0.19684 | 121.0739 | 120.9824 | 120.9641 | -0.054932 | -0.073242 | 121.0281 | -0.1236 | -0.20142 | 121.0419 | 121.138 | 120.9869 | 0.10986 | -0.041199 | 0.036621 | -0.045776 | 0.013733 | -0.041199 | -0.022888 | 0.036621 | 121.0144 | 121.0648 | -0.15106 | -0.16022 | 120.9915 | 120.9869 | 120.9824 | 120.9457
2831.9375 | 121.5042 | -121.1197 | 0.10071 | -0.0016785 | 6.9761 | 0.016767 | -0.0047126 | 0.0020636 | -0.0099591 | -0.003435 | -0.0036011 | 0.0005234 | 0.013751 | 0.015981 | -0.010258 | 0.029589 | -0.0013694 | 0.022888 | -0.064087 | 0.059509 | 0.091553 | 0.22888 | 0.1236 | 0.10529 | 0.091553 | -0.009155 | 0.022888 | 0.10071 | 0.19226 | 0.13275 | 0.17853 | 121.1792 | -0.1648 | -0.009155 | 121.3486 | 121.225 | 121.2433 | 0.045777 | 0.064087 | 121.1426 | -0.10986 | 0 | 121.312 | 121.2982 | 121.2524 | 0.15564 | 0.10986 | 0.16937 | 0.032044 | 0.16937 | 0.07782 | -0.1236 | -0.032043 | 121.0556 | 121.1105 | -0.041199 | -0.07782 | 121.2112 | 121.2204 | 121.1426 | 121.2112
2833.625 | 121.2936 | -120.8908 | 0.11444 | 0.005951 | 6.9795 | 0.016981 | -0.0012946 | 0.0046272 | -0.0088911 | -0.00023063 | -0.00054933 | 0.000737 | 0.012469 | 0.014272 | -0.0079083 | 0.028094 | 0.0020486 | 0.027466 | -0.054932 | 0.059509 | 0.10071 | 0.21057 | 0.07782 | 0.082397 | 0.082397 | -0.018311 | 0.045776 | 0.09613 | 0.16022 | 0.086975 | 0.18768 | 120.9503 | -0.16937 | -0.013733 | 121.1014 | 120.9732 | 120.9686 | 0.022888 | 0.018311 | 120.9366 | -0.13275 | -0.018311 | 121.051 | 121.0785 | 120.9778 | 0.14191 | 0.041199 | 0.15106 | 0.041199 | 0.11444 | 0.050354 | -0.11444 | -0.064087 | 120.8359 | 120.8725 | -0.054932 | -0.068665 | 120.9915 | 120.9869 | 120.9183 | 120.9732
2835.375 | 121.1563 | -120.8633 | 0.12817 | -0.009308 | 6.9774 | 0.016767 | -0.001081 | 0.00035457 | -0.0084637 | -0.00087163 | 0.0025025 | 0.0018052 | 0.01076 | 0.004659 | -0.010045 | 0.029589 | -0.0013694 | -0.027466 | -0.018311 | 0.004578 | 0 | 0.09613 | 0.013733 | 0 | -0.036621 | 0.018311 | 0 | 0.022888 | 0.082397 | 0.022888 | 0.1236 | 120.8679 | -0.14649 | -0.12817 | 120.9595 | 120.8633 | 120.8771 | -0.004578 | 0.009155 | 120.8633 | -0.10986 | -0.10529 | 120.9457 | 120.9869 | 120.8862 | 0.1236 | 0.022888 | 0.091552 | -0.004578 | 0.082397 | 0.022888 | -0.022889 | 0.018311 | 120.845 | 120.8817 | -0.1236 | -0.12817 | 120.8633 | 120.8862 | 120.8359 | 120.8267
2837.0469 | 121.2982 | -120.9869 | 0.11902 | -0.009308 | 6.9767 | 0.018263 | -0.0040716 | 0.00035457 | -0.0088911 | -0.00065803 | -0.0036011 | 0.0045822 | 0.012897 | 0.0065816 | -0.0053449 | 0.029803 | -0.00072839 | -0.036621 | -0.027466 | 0.018311 | -0.018311 | 0.09613 | -0.032043 | -0.004578 | -0.013733 | 0.013733 | 0.009155 | 0.054932 | 0.10529 | 0.041199 | 0.14648 | 121.0052 | -0.14649 | -0.13733 | 121.0831 | 120.9824 | 120.9549 | -0.022889 | -0.050354 | 120.9961 | -0.10529 | -0.064087 | 121.0922 | 121.1334 | 121.0281 | 0.13733 | 0.032044 | 0.077819 | -0.036622 | 0.096131 | 0.045777 | -0.045777 | 0.004578 | 120.9595 | 121.0007 | -0.10071 | -0.10986 | 120.9686 | 121.0419 | 120.9503 | 120.9732
2838.7969 | 120.9778 | -120.7214 | 0.13733 | -0.016937 | 6.9791 | 0.016981 | -0.0030036 | 0.0044134 | -0.0063275 | 0.001692 | -0.00054933 | 0.0037278 | 0.014178 | 0.0072226 | -0.0096173 | 0.030657 | -8.7586e-05 | -0.050354 | -0.027466 | 0.022888 | -0.073242 | 0.036621 | -0.064087 | -0.045776 | -0.073242 | 0.027466 | -0.009155 | -0.022888 | 0.013733 | -0.027466 | 0.09613 | 120.7443 | -0.16479 | -0.21057 | 120.7581 | 120.6757 | 120.6573 | -0.068664 | -0.086975 | 120.7123 | -0.10986 | -0.16022 | 120.7352 | 120.8176 | 120.694 | 0.10528 | -0.018311 | 0.013733 | -0.09613 | 0.022888 | -0.013733 | -0.050354 | 0.036621 | 120.694 | 120.7489 | -0.11444 | -0.14648 | 120.6482 | 120.6985 | 120.6711 | 120.6482
2840.5469 | 120.9137 | -120.6802 | 0.12817 | -0.0016785 | 6.9767 | 0.016767 | -0.003858 | -0.0017816 | -0.0086773 | 0.00019657 | -0.0036011 | 0.0015914 | 0.012469 | 0.00038663 | -0.010258 | 0.027239 | -0.003292 | -0.004578 | -0.059509 | 0.018311 | -0.009155 | 0.11444 | 0.032043 | 0.013733 | -0.041199 | 0.013733 | 0 | -0.018311 | 0.073242 | -0.009155 | 0.086975 | 120.6985 | -0.18768 | -0.13733 | 120.7947 | 120.694 | 120.7123 | -0.004578 | 0.013732 | 120.6802 | -0.11444 | -0.14649 | 120.7535 | 120.7672 | 120.6711 | 0.086975 | -0.009155 | 0.09613 | -0.027466 | 0.073242 | -0.018311 | -0.07782 | 0.013733 | 120.6207 | 120.694 | -0.10986 | -0.12817 | 120.6711 | 120.6619 | 120.6757 | 120.639
2842.25 | 121.2433 | -120.8862 | 0.10529 | -0.009308 | 6.9774 | 0.016126 | -0.0062078 | 0.00014097 | -0.0080365 | -0.0045032 | 0.0025025 | -0.0003312 | 0.010547 | 0.016408 | -0.0098309 | 0.027025 | 0.00098061 | 0.032043 | -0.054932 | 0.045776 | 0.091553 | 0.23346 | 0.10071 | 0.09613 | 0.086975 | -0.018311 | 0.027466 | 0.10071 | 0.19226 | 0.13275 | 0.1831 | 120.932 | -0.16022 | -0.013733 | 121.1197 | 120.9824 | 120.9869 | 0.050354 | 0.054932 | 120.9137 | -0.1236 | -0.004578 | 121.0785 | 121.0693 | 121.019 | 0.15564 | 0.10529 | 0.18768 | 0.045777 | 0.16479 | 0.073242 | -0.10071 | -0.045777 | 120.8313 | 120.8679 | -0.05951 | -0.07782 | 120.9778 | 120.9869 | 120.9183 | 120.9732
2844 | 121.1838 | -120.9961 | 0.11902 | 0.005951 | 6.9793 | 0.018476 | -0.0032172 | 0.0054816 | -0.0106 | -0.0015124 | 0.0025025 | 0.002446 | 0.014178 | 0.0029502 | -0.0072675 | 0.031084 | -0.0039328 | -0.032043 | -0.036621 | 0.022888 | -0.054932 | 0.032043 | -0.054932 | -0.054932 | -0.082397 | 0.027466 | -0.027466 | -0.013733 | 0.013733 | -0.054932 | 0.09613 | 121.019 | -0.15564 | -0.17395 | 121.0281 | 120.9412 | 120.9412 | -0.07782 | -0.07782 | 120.9686 | -0.091553 | -0.13275 | 121.0098 | 121.0922 | 120.9412 | 0.1236 | -0.027466 | 0.009155 | -0.07782 | 0.041199 | 0.013733 | -0.059509 | 0.054932 | 120.9595 | 121.0236 | -0.096131 | -0.14649 | 120.9412 | 120.9824 | 120.9641 | 120.9137
2845.6875 | 121.312 | -121.0144 | 0.082397 | 0.005951 | 6.9786 | 0.017408 | -0.00279 | 0.00035457 | -0.0052595 | -0.00044443 | 0.0025025 | 0.0020188 | 0.012683 | 0.01769 | -0.0074811 | 0.030871 | -0.0020102 | 0.045776 | -0.073242 | 0.054932 | 0.073242 | 0.20599 | 0.068665 | 0.07782 | 0.082397 | 0 | 0.032043 | 0.091553 | 0.13275 | 0.086975 | 0.16937 | 121.0693 | -0.15564 | -0.009155 | 121.2204 | 121.0922 | 121.0831 | 0.022888 | 0.013733 | 121.0464 | -0.082397 | 0.009156 | 121.1472 | 121.1838 | 121.1014 | 0.13733 | 0.054932 | 0.15106 | 0.01831 | 0.10071 | 0.05951 | -0.12817 | -0.032043 | 120.9412 | 121.0144 | -0.027465 | -0.050354 | 121.0876 | 121.106 | 121.0602 | 121.0968
2847.4219 | 121.2662 | -121.0648 | 0.13275 | -0.009308 | 6.9789 | 0.016554 | -0.003858 | -0.0034906 | -0.0106 | -0.0036486 | 0.0055543 | 0.0043686 | 0.015033 | -0.0021768 | -0.0081219 | 0.029803 | -0.00051479 | -0.036621 | -0.027466 | 0.009155 | -0.027466 | 0.054932 | 0 | 0.004578 | -0.064087 | 0.036621 | -0.013733 | -0.004578 | 0.073242 | 0.013733 | 0.10529 | 121.0739 | -0.16022 | -0.16022 | 121.1197 | 121.0693 | 121.0648 | -0.004577 | -0.009155 | 121.051 | -0.09613 | -0.13733 | 121.138 | 121.17 | 121.0785 | 0.11902 | 0.027466 | 0.045777 | -0.036621 | 0.086975 | 0.009155 | -0.036621 | 0.050354 | 121.0373 | 121.1014 | -0.1236 | -0.14648 | 121.0373 | 121.0602 | 121.0281 | 121.0007
2849.1562 | 121.2662 | -121.0739 | 0.11902 | -0.0016785 | 6.9769 | 0.015272 | -0.0023626 | 0.003559 | -0.0073957 | -0.00065803 | -0.00054933 | 0.0020188 | 0.013324 | 0.0027364 | -0.0094037 | 0.028734 | -0.002651 | -0.004578 | -0.036621 | 0.022888 | -0.004578 | 0.10529 | -0.009155 | -0.013733 | -0.022888 | 0.022888 | -0.009155 | 0.009155 | 0.050354 | -0.013733 | 0.10529 | 121.0968 | -0.15564 | -0.1236 | 121.1792 | 121.0602 | 121.0648 | -0.036621 | -0.032043 | 121.0648 | -0.096131 | -0.10986 | 121.1243 | 121.1792 | 121.0602 | 0.11444 | -0.004578 | 0.082398 | -0.027466 | 0.059509 | 0.01831 | -0.059509 | 0.032043 | 121.0373 | 121.0968 | -0.096131 | -0.12817 | 121.0693 | 121.0831 | 121.0693 | 121.051
2850.9062 | 121.4127 | -121.0602 | 0.091553 | 0.005951 | 6.9774 | 0.016126 | -0.0053534 | 0.0014228 | -0.0093183 | -0.0021532 | -0.0036011 | -0.000972 | 0.014392 | 0.011709 | -0.012395 | 0.026385 | -0.003292 | 0.013733 | -0.045776 | 0.045776 | 0.086975 | 0.21057 | 0.10986 | 0.10071 | 0.082397 | -0.009155 | 0.027466 | 0.09613 | 0.17395 | 0.11902 | 0.19226 | 121.106 | -0.13733 | -0.004578 | 121.2708 | 121.1609 | 121.17 | 0.054932 | 0.064087 | 121.0876 | -0.10071 | 0.004577 | 121.2341 | 121.2524 | 121.1792 | 0.16479 | 0.091553 | 0.1648 | 0.041199 | 0.14648 | 0.068664 | -0.091552 | -0.036621 | 121.0144 | 121.051 | -0.045777 | -0.064087 | 121.1472 | 121.1563 | 121.0739 | 121.1426
2852.6562 | 121.3303 | -121.1014 | 0.13275 | -0.009308 | 6.9761 | 0.018263 | -0.00279 | 0.0048408 | -0.0063275 | -0.005144 | -0.0036011 | 0.0037278 | 0.011401 | 0.015981 | -0.0070539 | 0.029162 | -0.00072839 | -0.027466 | -0.018311 | 0.009155 | -0.054932 | 0.032043 | -0.054932 | -0.054932 | -0.07782 | 0.027466 | -0.009155 | -0.009155 | 0.018311 | -0.032043 | 0.09613 | 121.1105 | -0.15106 | -0.18768 | 121.1334 | 121.0464 | 121.0464 | -0.064087 | -0.064087 | 121.0922 | -0.10529 | -0.14191 | 121.1197 | 121.1975 | 121.0693 | 0.10528 | -0.022888 | 0.022888 | -0.064087 | 0.027466 | 0 | -0.027466 | 0.036621 | 121.0831 | 121.1288 | -0.1236 | -0.14191 | 121.0464 | 121.0922 | 121.0739 | 121.0236
2854.3438 | 121.3715 | -121.0327 | 0.11444 | 0.005951 | 6.9756 | 0.017195 | -0.007276 | 0.0022772 | -0.0080365 | -0.0012988 | -0.0066527 | 0.0015914 | 0.013965 | 0.014059 | -0.0089765 | 0.027453 | -0.0035056 | -0.013733 | -0.064087 | 0.050354 | 0.022888 | 0.16022 | 0.054932 | 0.064087 | 0.045776 | 0 | 0.027466 | 0.07782 | 0.16479 | 0.10529 | 0.17395 | 121.0831 | -0.17853 | -0.091553 | 121.1929 | 121.0968 | 121.0876 | 0.013733 | 0.004578 | 121.0602 | -0.11444 | -0.036621 | 121.1975 | 121.2067 | 121.138 | 0.14648 | 0.07782 | 0.10986 | -0.027466 | 0.13733 | 0.050354 | -0.11444 | -0.027466 | 120.9686 | 121.0327 | -0.064087 | -0.086975 | 121.0556 | 121.1105 | 121.019 | 121.0785
2856.0938 | 121.2936 | -121.0922 | 0.15106 | -0.016937 | 6.978 | 0.015699 | -0.0017218 | -0.00049983 | -0.0086773 | -0.0010852 | -0.0036011 | 0.0026596 | 0.014392 | 0.0053 | -0.0061993 | 0.028521 | -0.003292 | -0.036621 | -0.027466 | -0.004578 | -0.054932 | 0.041199 | -0.041199 | -0.036621 | -0.073242 | 0.032043 | -0.009155 | -0.009155 | 0.036621 | -0.027466 | 0.086975 | 121.0876 | -0.17853 | -0.20599 | 121.1334 | 121.0556 | 121.051 | -0.032043 | -0.036621 | 121.0831 | -0.11902 | -0.16022 | 121.1288 | 121.1792 | 121.0648 | 0.09613 | -0.018311 | 0.045777 | -0.050354 | 0.045776 | 0 | -0.022888 | 0.041198 | 121.0648 | 121.1243 | -0.15564 | -0.16022 | 121.0373 | 121.0831 | 121.0556 | 121.019
2857.8438 | 121.3165 | -121.1655 | 0.14648 | -0.016937 | 6.9795 | 0.015486 | -0.0066352 | 0.00035457 | -0.0088911 | -0.00023063 | 0.0025025 | 0.0045822 | 0.012256 | 0.008077 | -0.012608 | 0.028734 | -0.0020102 | -0.045776 | -0.009155 | 0.009155 | -0.054932 | 0.068665 | -0.018311 | -0.018311 | -0.082397 | 0.036621 | -0.013733 | -0.041199 | 0.018311 | -0.032043 | 0.082397 | 121.1746 | -0.15564 | -0.20142 | 121.2341 | 121.1472 | 121.1472 | -0.027466 | -0.027466 | 121.1517 | -0.10986 | -0.18768 | 121.1838 | 121.2479 | 121.1334 | 0.09613 | -0.01831 | 0.05951 | -0.064087 | 0.032044 | -0.027466 | -0.01831 | 0.050354 | 121.1563 | 121.2021 | -0.13733 | -0.16022 | 121.1105 | 121.1243 | 121.1197 | 121.0831
2859.5156 | 121.4218 | -121.1197 | 0.11444 | -0.0016785 | 6.9765 | 0.016981 | -0.0051398 | 0.0020636 | -0.0073957 | -0.0030078 | 0.0025025 | 0.0015914 | 0.013537 | 0.0095724 | -0.0070539 | 0.027666 | -0.00436 | -0.022888 | -0.064087 | 0.022888 | 0.009155 | 0.1236 | 0.022888 | 0.027466 | -0.018311 | 0 | 0.022888 | 0.041199 | 0.10071 | 0.064087 | 0.14191 | 121.1426 | -0.17853 | -0.10529 | 121.2433 | 121.1472 | 121.1426 | 0.004578 | 0 | 121.1426 | -0.11444 | -0.073242 | 121.2204 | 121.2616 | 121.1838 | 0.11902 | 0.041199 | 0.10071 | -0.013733 | 0.07782 | 0.018311 | -0.086975 | -0.022888 | 121.0556 | 121.1197 | -0.091553 | -0.091553 | 121.1288 | 121.1609 | 121.0968 | 121.1014
2861.2656 | 121.3577 | -121.17 | 0.15564 | 0.005951 | 6.9793 | 0.014204 | -0.003858 | -0.0011408 | -0.0097455 | 0.001692 | -0.0036011 | 0.0037278 | 0.013965 | 0.011922 | -0.0081219 | 0.028094 | -0.0079916 | -0.032043 | -0.009155 | 0.004578 | -0.054932 | 0.032043 | -0.059509 | -0.041199 | -0.059509 | 0.041199 | -0.004578 | 0.004578 | 0.022888 | -0.027466 | 0.10986 | 121.1746 | -0.16479 | -0.21057 | 121.2021 | 121.1288 | 121.1105 | -0.045777 | -0.064087 | 121.1655 | -0.11444 | -0.15106 | 121.1929 | 121.2799 | 121.1426 | 0.11444 | -0.022888 | 0.027465 | -0.05951 | 0.027466 | 0.009156 | -0.013733 | 0.045777 | 121.1609 | 121.2112 | -0.15106 | -0.16022 | 121.1151 | 121.1746 | 121.138 | 121.1105
2863 | 121.4859 | -121.1563 | 0.10529 | -0.0016785 | 6.9776 | 0.016767 | -0.0087714 | -0.0019952 | -0.010173 | -1.7026e-05 | -0.00054933 | 0.0009506 | 0.013537 | 0.014059 | -0.010686 | 0.028521 | -0.0052146 | 0.036621 | -0.054932 | 0.050354 | 0.082397 | 0.22888 | 0.10529 | 0.091553 | 0.10071 | 0.004578 | 0.041199 | 0.09613 | 0.1831 | 0.11902 | 0.19226 | 121.2067 | -0.16022 | -0.022889 | 121.3852 | 121.2479 | 121.2616 | 0.041199 | 0.054932 | 121.1975 | -0.10071 | -0.009156 | 121.3394 | 121.3486 | 121.2753 | 0.15106 | 0.07782 | 0.17853 | 0.032043 | 0.14191 | 0.054931 | -0.10529 | -0.036621 | 121.1014 | 121.1609 | -0.054932 | -0.064087 | 121.2387 | 121.2524 | 121.1929 | 121.257
2864.75 | 121.4539 | -121.1792 | 0.11902 | 0.005951 | 6.9763 | 0.016767 | -0.0051398 | -0.0011408 | -0.0059003 | -0.0021532 | 0.0055543 | 0.0011642 | 0.01076 | 0.015127 | -0.0087629 | 0.030871 | -0.0041464 | -0.027466 | -0.054932 | 0.032043 | 0.013733 | 0.11902 | 0.041199 | 0.045776 | 0.004578 | -0.004578 | 0.018311 | 0.041199 | 0.1236 | 0.073242 | 0.14648 | 121.2112 | -0.17395 | -0.10529 | 121.2982 | 121.225 | 121.2204 | 0.013733 | 0.009156 | 121.1975 | -0.1236 | -0.07782 | 121.3028 | 121.3257 | 121.2524 | 0.12817 | 0.054931 | 0.086976 | -0.01831 | 0.10528 | 0.022888 | -0.086975 | -0.022889 | 121.1243 | 121.1746 | -0.086976 | -0.10071 | 121.1929 | 121.2204 | 121.1517 | 121.1838
2866.4375 | 121.4081 | -121.2204 | 0.1236 | -0.009308 | 6.9806 | 0.015699 | -0.0023626 | 0.0061224 | -0.0080365 | -0.0012988 | -0.00054933 | 0.005223 | 0.013537 | 0.0095724 | -0.0081219 | 0.028734 | -0.0024374 | -0.041199 | -0.036621 | 0.013733 | -0.032043 | 0.050354 | -0.059509 | -0.036621 | -0.054932 | 0.032043 | 0 | 0 | 0.032043 | -0.032043 | 0.10071 | 121.2341 | -0.16022 | -0.15564 | 121.2708 | 121.1838 | 121.1609 | -0.050354 | -0.073242 | 121.2204 | -0.091553 | -0.1236 | 121.2524 | 121.3211 | 121.1884 | 0.10071 | -0.032043 | 0.036621 | -0.045776 | 0.032043 | 0 | -0.050354 | 0.032043 | 121.1838 | 121.2524 | -0.10986 | -0.1236 | 121.1884 | 121.2204 | 121.1792 | 121.1655
2868.1875 | 121.3943 | -121.2387 | 0.15564 | -0.0016785 | 6.978 | 0.014631 | -0.0032172 | 0.005268 | -0.0088911 | -0.00044443 | 0.0086061 | 0.0020188 | 0.011615 | 0.010213 | -0.012822 | 0.027025 | -0.0056418 | -0.064087 | -0.009155 | 0.004578 | -0.050354 | 0.054932 | -0.009155 | -0.027466 | -0.09613 | 0.054932 | -0.022888 | -0.045776 | 0.027466 | -0.022888 | 0.07782 | 121.2433 | -0.16479 | -0.20599 | 121.2936 | 121.2112 | 121.2296 | -0.032044 | -0.013733 | 121.2158 | -0.10071 | -0.20142 | 121.2662 | 121.3165 | 121.2158 | 0.10071 | 0 | 0.050354 | -0.054932 | 0.050354 | -0.022888 | -0.013733 | 0.07782 | 121.2296 | 121.2936 | -0.15106 | -0.17853 | 121.1884 | 121.1929 | 121.1746 | 121.1426
2869.9219 | 121.4584 | -121.225 | 0.1236 | -0.0016785 | 6.9786 | 0.017622 | -0.003858 | 0.0031318 | -0.0093183 | -0.0027942 | -0.00054933 | 0.0030868 | 0.01311 | 0.01235 | -0.0079083 | 0.027453 | -0.0045736 | 0.013733 | -0.041199 | 0.013733 | 0.022888 | 0.11902 | 0.027466 | 0.004578 | 0.018311 | 0.032043 | 0 | 0.032043 | 0.10986 | 0.027466 | 0.13275 | 121.2387 | -0.16479 | -0.10071 | 121.344 | 121.2296 | 121.2524 | -0.009155 | 0.013733 | 121.225 | -0.091553 | -0.091553 | 121.3348 | 121.3577 | 121.2524 | 0.13275 | 0.027466 | 0.10529 | 0.009155 | 0.10986 | 0.032043 | -0.054932 | 0.032043 | 121.1838 | 121.257 | -0.10986 | -0.1236 | 121.2479 | 121.257 | 121.2387 | 121.2433
2871.6719 | 121.5591 | -121.2158 | 0.11444 | -0.0016785 | 6.9771 | 0.015486 | -0.0064216 | -0.0013544 | -0.0091047 | -0.0019396 | -0.00054933 | 0.0015914 | 0.013965 | 0.0040182 | -0.0094037 | 0.027453 | -0.0024374 | 0.027466 | -0.059509 | 0.059509 | 0.082397 | 0.23804 | 0.1236 | 0.10529 | 0.11902 | -0.022888 | 0.032043 | 0.086975 | 0.19226 | 0.13733 | 0.18768 | 121.2753 | -0.17395 | -0.032044 | 121.4539 | 121.3211 | 121.3394 | 0.045777 | 0.064087 | 121.2479 | -0.13733 | -0.027466 | 121.4081 | 121.4035 | 121.3531 | 0.15564 | 0.10529 | 0.17853 | 0.022888 | 0.16022 | 0.054932 | -0.11902 | -0.054931 | 121.1563 | 121.1929 | -0.054932 | -0.082398 | 121.2982 | 121.3028 | 121.2433 | 121.3348
2873.3438 | 121.4401 | -121.2524 | 0.12817 | -0.0016785 | 6.9791 | 0.017408 | -0.0036444 | -0.00028623 | -0.0069683 | -0.0015124 | -0.0036011 | 0.0050094 | 0.012042 | 0.006368 | -0.0081219 | 0.027239 | 0.00012601 | -0.045776 | -0.036621 | 0.013733 | -0.045776 | 0.022888 | -0.054932 | -0.050354 | -0.073242 | 0.032043 | -0.013733 | -0.013733 | 0.018311 | -0.045776 | 0.091553 | 121.2662 | -0.1648 | -0.17395 | 121.2753 | 121.2021 | 121.1975 | -0.064087 | -0.068665 | 121.2387 | -0.096131 | -0.14191 | 121.2708 | 121.344 | 121.2067 | 0.10529 | -0.032043 | 0.009155 | -0.059509 | 0.032044 | 0 | -0.050354 | 0.045776 | 121.2158 | 121.2845 | -0.11444 | -0.14191 | 121.2067 | 121.2387 | 121.2067 | 121.1792
2875.0781 | 121.5271 | -121.2662 | 0.13733 | -0.0016785 | 6.9789 | 0.01634 | -0.0019354 | 0.00014097 | -0.0086773 | -0.00087163 | -0.0036011 | 0.0026596 | 0.012897 | 0.0093588 | -0.0083355 | 0.029803 | -0.0024374 | -0.041199 | -0.036621 | 0.004578 | -0.027466 | 0.082397 | -0.018311 | -0.013733 | -0.018311 | 0.004578 | 0.013733 | 0.045776 | 0.091553 | 0.018311 | 0.14191 | 121.2708 | -0.17395 | -0.16479 | 121.3486 | 121.2524 | 121.2479 | -0.018311 | -0.022889 | 121.2799 | -0.13275 | -0.091553 | 121.3577 | 121.4081 | 121.2845 | 0.12817 | 0.004578 | 0.077819 | -0.032044 | 0.07782 | 0.032043 | -0.041199 | -0.009155 | 121.2296 | 121.2708 | -0.13275 | -0.1236 | 121.2387 | 121.312 | 121.225 | 121.2479
2876.8281 | 121.6324 | -121.225 | 0.10071 | 0.005951 | 6.9786 | 0.016767 | -0.0053534 | 0.00078177 | -0.0093183 | -0.0027942 | -0.00054933 | 0.0011642 | 0.015887 | 0.011068 | -0.01154 | 0.027239 | -0.0020102 | 0.018311 | -0.064087 | 0.059509 | 0.07782 | 0.23346 | 0.1236 | 0.10529 | 0.11444 | -0.013733 | 0.027466 | 0.09613 | 0.1831 | 0.11444 | 0.17853 | 121.2845 | -0.1648 | -0.022888 | 121.4584 | 121.3303 | 121.3486 | 0.045777 | 0.064087 | 121.2524 | -0.11444 | -0.004578 | 121.4081 | 121.4035 | 121.3394 | 0.15106 | 0.086975 | 0.17395 | 0.018311 | 0.15564 | 0.068664 | -0.1236 | -0.041199 | 121.1609 | 121.2112 | -0.041199 | -0.073242 | 121.3028 | 121.3211 | 121.2433 | 121.3394
2878.5156 | 121.6095 | -121.2616 | 0.086975 | -0.0016785 | 6.9801 | 0.016554 | -0.0019354 | 0.00185 | -0.0076093 | -0.0038622 | -0.00054933 | 0.002446 | 0.013751 | 0.0074362 | -0.0061993 | 0.029162 | -0.00436 | 0.050354 | -0.059509 | 0.054932 | 0.082397 | 0.19226 | 0.07782 | 0.068665 | 0.091553 | -0.013733 | 0.018311 | 0.10529 | 0.17853 | 0.11902 | 0.19684 | 121.3165 | -0.14648 | -0.004578 | 121.4539 | 121.3303 | 121.3394 | 0.013733 | 0.022888 | 121.2799 | -0.10071 | 0.018311 | 121.4401 | 121.4584 | 121.3806 | 0.17853 | 0.10071 | 0.13733 | 0.027465 | 0.16022 | 0.086975 | -0.11444 | -0.032044 | 121.2021 | 121.2479 | -0.032043 | -0.068664 | 121.344 | 121.3669 | 121.312 | 121.3531
2880.25 | 121.5775 | -121.2708 | 0.1236 | -0.009308 | 6.9789 | 0.017622 | -0.004499 | -0.002636 | -0.0071821 | -0.0012988 | -0.00054933 | 0.0015914 | 0.013537 | 0.01235 | -0.010045 | 0.028734 | -0.00051479 | -0.027466 | -0.064087 | 0.022888 | 0.022888 | 0.10986 | 0.022888 | 0.022888 | 0.004578 | 0 | 0.036621 | 0.032043 | 0.10071 | 0.059509 | 0.14191 | 121.2936 | -0.18768 | -0.10071 | 121.3806 | 121.2936 | 121.2936 | 0 | 0 | 121.3074 | -0.1236 | -0.091553 | 121.3715 | 121.4127 | 121.3303 | 0.10529 | 0.022888 | 0.086975 | 0 | 0.064087 | -0.004578 | -0.086975 | -0.036621 | 121.2067 | 121.2708 | -0.10071 | -0.086975 | 121.2936 | 121.3028 | 121.2433 | 121.2753
2881.9531 | 121.4996 | -121.3165 | 0.16022 | -0.0016785 | 6.9774 | 0.015058 | -0.0053534 | 0.00078177 | -0.0106 | -0.002367 | -0.0036011 | 0.0026596 | 0.014605 | 0.008077 | -0.013249 | 0.026812 | -0.0056418 | -0.059509 | -0.022888 | 0.009155 | -0.045776 | 0.059509 | -0.018311 | -0.022888 | -0.064087 | 0.045776 | -0.013733 | -0.054932 | 0.022888 | -0.018311 | 0.073242 | 121.3257 | -0.1831 | -0.20599 | 121.376 | 121.2936 | 121.2982 | -0.032043 | -0.027466 | 121.3028 | -0.11444 | -0.21515 | 121.3394 | 121.3898 | 121.2982 | 0.086975 | -0.004578 | 0.050354 | -0.054931 | 0.036621 | -0.041199 | -0.032043 | 0.059509 | 121.2936 | 121.3623 | -0.15106 | -0.17395 | 121.2708 | 121.2616 | 121.257 | 121.2524
2883.7031 | 121.6095 | -121.312 | 0.11444 | -0.009308 | 6.9782 | 0.016126 | -0.0032172 | 0.00035457 | -0.0088911 | -0.00065803 | -0.0036011 | 0.0015914 | 0.014819 | 0.01534 | -0.0083355 | 0.029803 | 0.00012601 | 0.018311 | -0.059509 | 0.064087 | 0.091553 | 0.20599 | 0.068665 | 0.073242 | 0.073242 | -0.009155 | 0.027466 | 0.064087 | 0.12817 | 0.068665 | 0.14191 | 121.376 | -0.17395 | -0.022888 | 121.5179 | 121.3852 | 121.3806 | 0.009155 | 0.004578 | 121.3394 | -0.1236 | -0.050354 | 121.4401 | 121.4539 | 121.3806 | 0.11444 | 0.041199 | 0.14191 | 0.027466 | 0.10071 | 0.036621 | -0.1236 | -0.036621 | 121.2524 | 121.3028 | -0.050354 | -0.086975 | 121.4035 | 121.376 | 121.3303 | 121.3852
2885.4375 | 121.6095 | -121.344 | 0.10986 | -0.009308 | 6.9789 | 0.015058 | -0.0059942 | 0.0033454 | -0.010173 | -0.00044443 | -0.00054933 | 0.0022324 | 0.012683 | 0.010427 | -0.0096173 | 0.029162 | -0.0047874 | -0.022888 | -0.045776 | 0.041199 | 0.018311 | 0.1236 | 0.022888 | 0.050354 | 0.009155 | 0.022888 | 0.018311 | 0.050354 | 0.10529 | 0.068665 | 0.15564 | 121.3852 | -0.15564 | -0.091552 | 121.4676 | 121.3943 | 121.3669 | 0.009155 | -0.018311 | 121.3623 | -0.086975 | -0.059509 | 121.4493 | 121.4996 | 121.4127 | 0.13733 | 0.050354 | 0.082397 | -0.022888 | 0.086975 | 0.032043 | -0.086975 | 0.004577 | 121.2982 | 121.3669 | -0.068664 | -0.091552 | 121.3623 | 121.3943 | 121.3211 | 121.3531
2887.1875 | 121.5546 | -121.3531 | 0.14648 | -0.0016785 | 6.9795 | 0.015486 | -0.0023626 | 0.0044134 | -0.0080365 | -0.00023063 | 0.0025025 | 0.0043686 | 0.014392 | -0.0036722 | -0.013249 | 0.027025 | -0.0047874 | -0.036621 | -0.027466 | 0.013733 | -0.027466 | 0.064087 | -0.013733 | -0.013733 | -0.068665 | 0.027466 | -0.009155 | -0.022888 | 0.041199 | -0.018311 | 0.091553 | 121.3669 | -0.17395 | -0.17395 | 121.4172 | 121.3394 | 121.3394 | -0.027466 | -0.027466 | 121.344 | -0.11902 | -0.16937 | 121.3943 | 121.4447 | 121.3348 | 0.10071 | -0.009156 | 0.050354 | -0.041199 | 0.050354 | -0.013733 | -0.041199 | 0.036621 | 121.3257 | 121.3806 | -0.13275 | -0.15564 | 121.3257 | 121.3303 | 121.3165 | 121.2845
2888.9375 | 121.5775 | -121.3806 | 0.14191 | -0.009308 | 6.9808 | 0.017835 | -0.002149 | 0.0039862 | -0.0086773 | -1.7026e-05 | 0.0025025 | 0.005223 | 0.010119 | 0.010213 | -0.0087629 | 0.025744 | -0.0022238 | 0.004578 | -0.022888 | 0.036621 | 0.022888 | 0.14191 | 0.022888 | 0.018311 | 0.013733 | 0.022888 | 0.009155 | 0.041199 | 0.073242 | 0.018311 | 0.13275 | 121.4172 | -0.16479 | -0.11902 | 121.5225 | 121.3989 | 121.4035 | -0.01831 | -0.013733 | 121.3898 | -0.11902 | -0.10071 | 121.4539 | 121.5134 | 121.3989 | 0.1236 | 0.009156 | 0.10529 | -0.013733 | 0.064087 | 0.032044 | -0.059509 | 0.013733 | 121.3577 | 121.4035 | -0.10529 | -0.13275 | 121.4035 | 121.4218 | 121.3852 | 121.3943
2890.7031 | 121.6782 | -121.3394 | 0.09613 | -0.0016785 | 6.9771 | 0.014631 | -0.0047126 | 0.00078177 | -0.0106 | -0.00044443 | 0.0025025 | 0.0013778 | 0.011615 | 0.011495 | -0.010472 | 0.025744 | 0.00055321 | 0.041199 | -0.059509 | 0.054932 | 0.11444 | 0.21515 | 0.1236 | 0.10529 | 0.086975 | -0.009155 | 0.036621 | 0.09613 | 0.1831 | 0.11902 | 0.17395 | 121.3943 | -0.15564 | 0.018311 | 121.5546 | 121.4447 | 121.463 | 0.050354 | 0.068664 | 121.376 | -0.10528 | 0 | 121.5225 | 121.5134 | 121.4584 | 0.13733 | 0.082398 | 0.16022 | 0.059509 | 0.14648 | 0.059509 | -0.11444 | -0.045776 | 121.2799 | 121.3303 | -0.041198 | -0.059509 | 121.4539 | 121.4355 | 121.3806 | 121.4264
2892.3906 | 121.5729 | -121.3806 | 0.14191 | -0.0016785 | 6.9793 | 0.016126 | -0.0015082 | -0.002636 | -0.0082501 | -0.0012988 | -0.0036011 | 0.0045822 | 0.01311 | 0.008077 | -0.0081219 | 0.028094 | -0.00051479 | -0.059509 | -0.036621 | 0.009155 | -0.059509 | 0.041199 | -0.064087 | -0.041199 | -0.091553 | 0.050354 | -0.013733 | -0.027466 | 0.018311 | -0.064087 | 0.07782 | 121.3898 | -0.17853 | -0.20142 | 121.4218 | 121.3394 | 121.3165 | -0.050354 | -0.073242 | 121.3669 | -0.091553 | -0.16937 | 121.3989 | 121.4584 | 121.3165 | 0.091553 | -0.050354 | 0.032044 | -0.068664 | 0.032044 | -0.013733 | -0.045776 | 0.064087 | 121.344 | 121.431 | -0.13275 | -0.15564 | 121.3211 | 121.3531 | 121.3211 | 121.2891
2894.1406 | 121.701 | -121.344 | 0.11444 | -0.0016785 | 6.9793 | 0.01634 | -0.0032172 | 0.00185 | -0.0082501 | -0.0032214 | 0.0025025 | 0.0028732 | 0.014605 | 0.012777 | -0.0047039 | 0.029803 | -0.0069236 | 0.036621 | -0.064087 | 0.050354 | 0.082397 | 0.18768 | 0.064087 | 0.064087 | 0.10071 | 0 | 0.032043 | 0.10986 | 0.17853 | 0.10529 | 0.18768 | 121.3943 | -0.17853 | -0.032044 | 121.5317 | 121.4081 | 121.4081 | 0.013733 | 0.013733 | 121.376 | -0.11444 | -0.004578 | 121.5225 | 121.5317 | 121.4493 | 0.15564 | 0.073243 | 0.13733 | 0.032043 | 0.14648 | 0.07782 | -0.11444 | -0.032043 | 121.2799 | 121.344 | -0.064087 | -0.082398 | 121.4264 | 121.4539 | 121.3806 | 121.4447
2895.8906 | 121.6278 | -121.3943 | 0.14648 | 0.005951 | 6.9791 | 0.013777 | -0.0040716 | 0.0012092 | -0.0073957 | -0.002367 | 0.0025025 | 0.003514 | 0.014178 | 0.0082906 | -0.010686 | 0.028734 | -0.0039328 | -0.027466 | -0.018311 | 0 | -0.018311 | 0.064087 | 0 | 0 | -0.059509 | 0.050354 | -0.009155 | -0.013733 | 0.068665 | 0.009155 | 0.12817 | 121.3943 | -0.16479 | -0.16479 | 121.4584 | 121.3943 | 121.3943 | 0 | 0 | 121.3852 | -0.09613 | -0.16022 | 121.463 | 121.5225 | 121.4035 | 0.13733 | 0.01831 | 0.064087 | -0.018311 | 0.07782 | -0.004578 | -0.018311 | 0.059509 | 121.376 | 121.4447 | -0.14648 | -0.15564 | 121.376 | 121.3806 | 121.3669 | 121.3348
2897.5781 | 121.6049 | -121.4355 | 0.13733 | -0.009308 | 6.9776 | 0.013563 | -0.0059942 | 0.0016364 | -0.0093183 | -0.00044443 | 0.0025025 | 0.0022324 | 0.015246 | 0.009786 | -0.012395 | 0.028521 | -0.00051479 | -0.059509 | -0.004578 | -0.009155 | -0.054932 | 0.073242 | -0.009155 | -0.022888 | -0.086975 | 0.032043 | -0.004578 | -0.022888 | 0.041199 | -0.013733 | 0.086975 | 121.4264 | -0.14191 | -0.19226 | 121.5088 | 121.4127 | 121.4264 | -0.013733 | 0 | 121.431 | -0.10529 | -0.16022 | 121.4767 | 121.5225 | 121.4218 | 0.091553 | -0.009155 | 0.082397 | -0.045777 | 0.045777 | -0.01831 | 0.004577 | 0.036621 | 121.431 | 121.4676 | -0.14648 | -0.14191 | 121.3806 | 121.4127 | 121.376 | 121.3486
2899.3281 | 121.6507 | -121.4264 | 0.12817 | -0.0016785 | 6.9806 | 0.015486 | -0.0023626 | 0.0041998 | -0.0097455 | -0.00087163 | 0.0025025 | 0.0033004 | 0.013751 | 0.0067954 | -0.010899 | 0.028521 | -0.0039328 | 0.004578 | -0.022888 | 0.036621 | 0.022888 | 0.12817 | 0.018311 | 0.027466 | 0.027466 | 0.013733 | 0 | 0.041199 | 0.10071 | 0.036621 | 0.1236 | 121.463 | -0.15106 | -0.10529 | 121.5546 | 121.4539 | 121.4447 | -0.009155 | -0.01831 | 121.4264 | -0.11444 | -0.086975 | 121.5271 | 121.55 | 121.463 | 0.1236 | 0.036621 | 0.091553 | -0.013733 | 0.10071 | 0.041199 | -0.059509 | 0.013733 | 121.4035 | 121.4401 | -0.091553 | -0.12817 | 121.4493 | 121.4676 | 121.431 | 121.4539
2901.0156 | 121.6599 | -121.4172 | 0.12817 | -0.009308 | 6.9797 | 0.016767 | -0.0057806 | 0.003559 | -0.0073957 | -0.0042896 | -0.00054933 | 0.0045822 | 0.011615 | 0.0042318 | -0.0087629 | 0.02553 | -0.0022238 | 0.018311 | -0.036621 | 0.022888 | 0.009155 | 0.11444 | 0.036621 | 0.013733 | 0.013733 | 0.013733 | 0.013733 | 0.027466 | 0.11444 | 0.022888 | 0.13275 | 121.4401 | -0.1648 | -0.11902 | 121.5317 | 121.431 | 121.4539 | -0.009155 | 0.013733 | 121.431 | -0.11444 | -0.10071 | 121.5317 | 121.55 | 121.4401 | 0.11902 | 0.009155 | 0.091553 | -0.013733 | 0.10071 | 0.013733 | -0.059509 | 0 | 121.3806 | 121.431 | -0.10529 | -0.11444 | 121.4264 | 121.4447 | 121.4355 | 121.431
2902.7656 | 121.6324 | -121.4355 | 0.13733 | 0.005951 | 6.9793 | 0.01634 | -0.0025764 | -0.0011408 | -0.0065411 | -0.001726 | 0.0055543 | 0.0050094 | 0.016742 | 0.0055136 | -0.0083355 | 0.027025 | -0.00051479 | 0.004578 | -0.022888 | 0.027466 | 0.009155 | 0.11444 | 0 | 0.004578 | -0.009155 | 0.018311 | -0.009155 | 0 | 0.059509 | -0.032043 | 0.091553 | 121.463 | -0.16022 | -0.12817 | 121.55 | 121.4401 | 121.4355 | -0.022888 | -0.027466 | 121.4264 | -0.11902 | -0.13733 | 121.4951 | 121.5271 | 121.4035 | 0.10071 | -0.022888 | 0.086975 | -0.018311 | 0.068664 | 0.009155 | -0.050354 | 0.027466 | 121.4127 | 121.4539 | -0.10986 | -0.14648 | 121.4447 | 121.4355 | 121.4401 | 121.4264
2904.5156 | 121.6965 | -121.4218 | 0.10529 | -0.0016785 | 6.9801 | 0.016767 | -0.0051398 | -0.00028623 | -0.0069683 | -0.003435 | -0.00054933 | 0.0018052 | 0.012897 | -0.00025417 | -0.010045 | 0.029162 | -0.006069 | -0.009155 | -0.068665 | 0.045776 | 0.032043 | 0.15564 | 0.045776 | 0.054932 | 0.018311 | -0.009155 | 0.013733 | 0.045776 | 0.11444 | 0.059509 | 0.14191 | 121.4676 | -0.17395 | -0.073243 | 121.5775 | 121.4767 | 121.4676 | 0.009156 | 0 | 121.4355 | -0.11444 | -0.05951 | 121.5363 | 121.5637 | 121.4813 | 0.12817 | 0.045776 | 0.10986 | -0.013733 | 0.10071 | 0.032043 | -0.11444 | -0.022888 | 121.3531 | 121.4127 | -0.05951 | -0.091553 | 121.4539 | 121.4676 | 121.4127 | 121.4401
2906.2812 | 121.7194 | -121.4218 | 0.11444 | -0.009308 | 6.9782 | 0.016981 | -0.0040716 | 0.0014228 | -0.0086773 | -0.00065803 | -0.00054933 | 0.0018052 | 0.013324 | 0.0076498 | -0.0089765 | 0.02788 | -0.0041464 | -0.009155 | -0.045776 | 0.07782 | 0.045776 | 0.16479 | 0.045776 | 0.041199 | 0.018311 | -0.004578 | 0.013733 | 0.036621 | 0.11902 | 0.050354 | 0.14648 | 121.4996 | -0.16022 | -0.068665 | 121.5866 | 121.463 | 121.4676 | -0.036621 | -0.032044 | 121.4355 | -0.11902 | -0.07782 | 121.5408 | 121.5683 | 121.4722 | 0.13275 | 0.036621 | 0.086975 | -0.032044 | 0.10529 | 0.022888 | -0.1236 | -0.018311 | 121.376 | 121.4172 | -0.036621 | -0.10071 | 121.4676 | 121.4584 | 121.4127 | 121.4401
2907.9688 | 121.7468 | -121.4264 | 0.11902 | -0.016937 | 6.9812 | 0.015272 | -0.005567 | -0.0030634 | -0.0067547 | -0.00087163 | -0.00054933 | 0.0028732 | 0.011828 | 0.0093588 | -0.010472 | 0.030016 | -0.0041464 | 0.013733 | -0.064087 | 0.050354 | 0.10071 | 0.20599 | 0.10071 | 0.091553 | 0.07782 | 0 | 0.032043 | 0.086975 | 0.16022 | 0.11902 | 0.16022 | 121.4767 | -0.18311 | -0.018311 | 121.6324 | 121.5179 | 121.5271 | 0.041199 | 0.050354 | 121.4584 | -0.11902 | -0.032044 | 121.5866 | 121.5866 | 121.5454 | 0.12817 | 0.086976 | 0.15564 | 0.050354 | 0.12817 | 0.054932 | -0.11444 | -0.032043 | 121.3623 | 121.4264 | -0.068665 | -0.086976 | 121.5271 | 121.5134 | 121.4401 | 121.5042
2909.6719 | 121.8018 | -121.4447 | 0.11902 | -0.009308 | 6.9748 | 0.015486 | -0.0059942 | 0.0014228 | -0.010814 | -0.0032214 | -0.0066527 | -0.0001174 | 0.013537 | 0.010427 | -0.0089765 | 0.025103 | -0.00072839 | 0.018311 | -0.045776 | 0.041199 | 0.10071 | 0.24261 | 0.11444 | 0.10529 | 0.10986 | -0.009155 | 0.022888 | 0.091553 | 0.18768 | 0.13275 | 0.16937 | 121.4859 | -0.16479 | -0.018311 | 121.6873 | 121.55 | 121.5591 | 0.064087 | 0.073242 | 121.4676 | -0.12817 | -0.027466 | 121.6324 | 121.6141 | 121.5775 | 0.14649 | 0.10986 | 0.20142 | 0.059509 | 0.16479 | 0.068665 | -0.086975 | -0.032043 | 121.3989 | 121.4355 | -0.07782 | -0.096131 | 121.5454 | 121.5363 | 121.463 | 121.5546
2911.4219 | 121.7743 | -121.4493 | 0.09613 | -0.0016785 | 6.9778 | 0.019117 | -0.0053534 | 0.00185 | -0.0061139 | -0.0038622 | 0.0025025 | 0.0020188 | 0.014392 | 0.013418 | -0.0066265 | 0.028307 | -0.00094199 | 0.068665 | -0.054932 | 0.068665 | 0.11444 | 0.20599 | 0.073242 | 0.082397 | 0.10071 | 0.004578 | 0.032043 | 0.07782 | 0.15564 | 0.091553 | 0.18768 | 121.5179 | -0.15106 | 0.018311 | 121.6553 | 121.5317 | 121.5225 | 0.013732 | 0.004577 | 121.4813 | -0.091552 | -0.01831 | 121.6049 | 121.637 | 121.5408 | 0.15564 | 0.05951 | 0.13733 | 0.045776 | 0.1236 | 0.045777 | -0.1236 | -0.027465 | 121.3943 | 121.4539 | -0.027465 | -0.064087 | 121.5637 | 121.5271 | 121.5179 | 121.55
2913.1719 | 121.7651 | -121.4172 | 0.1236 | -0.009308 | 6.9797 | 0.015486 | -0.0066352 | -0.001568 | -0.0069683 | -0.0012988 | -0.0066527 | 0.0022324 | 0.014392 | 0.010427 | -0.010472 | 0.029162 | -0.0058554 | 0.036621 | -0.054932 | 0.041199 | 0.10071 | 0.21057 | 0.11444 | 0.07782 | 0.082397 | -0.018311 | 0.013733 | 0.082397 | 0.17395 | 0.11444 | 0.1831 | 121.4584 | -0.17853 | -0.022888 | 121.6278 | 121.4951 | 121.5317 | 0.036621 | 0.073242 | 121.431 | -0.14191 | -0.041199 | 121.5912 | 121.6003 | 121.5317 | 0.16937 | 0.10071 | 0.16937 | 0.059509 | 0.16022 | 0.068664 | -0.096131 | -0.032044 | 121.3623 | 121.3989 | -0.082397 | -0.10986 | 121.5179 | 121.4996 | 121.4539 | 121.4996
2914.9219 | 121.6782 | -121.5042 | 0.13733 | -0.0016785 | 6.9816 | 0.014204 | -0.0047126 | 0.0033454 | -0.0086773 | -0.0027942 | -0.00054933 | 0.005223 | 0.014605 | 0.0048728 | -0.0076947 | 0.028521 | 0.00012601 | 0.004578 | -0.027466 | 0.036621 | 0.009155 | 0.10071 | -0.004578 | 0 | -0.032043 | 0.027466 | 0.009155 | 0 | 0.036621 | -0.027466 | 0.09613 | 121.5408 | -0.16479 | -0.12817 | 121.6049 | 121.5042 | 121.4996 | -0.036621 | -0.041199 | 121.5134 | -0.10986 | -0.13733 | 121.5408 | 121.6003 | 121.4767 | 0.086975 | -0.036621 | 0.064087 | -0.027466 | 0.027466 | -0.009155 | -0.064087 | 0.018311 | 121.4767 | 121.5317 | -0.10071 | -0.12817 | 121.5134 | 121.5042 | 121.5088 | 121.4722
2916.6094 | 121.6736 | -121.4905 | 0.14191 | -0.016937 | 6.9793 | 0.01634 | -0.0017218 | -0.002636 | -0.0056867 | -0.0030078 | 0.0025025 | 0.0043686 | 0.013537 | 0.0095724 | -0.0094037 | 0.028521 | -0.0054282 | 0 | -0.036621 | 0.027466 | -0.018311 | 0.082397 | -0.027466 | -0.022888 | -0.036621 | 0.036621 | 0 | -0.009155 | 0.032043 | -0.036621 | 0.091553 | 121.5179 | -0.17853 | -0.16022 | 121.5729 | 121.4676 | 121.463 | -0.050354 | -0.054932 | 121.4905 | -0.10529 | -0.15106 | 121.5225 | 121.582 | 121.4539 | 0.091553 | -0.036621 | 0.054931 | -0.045777 | 0.032043 | -0.009155 | -0.064087 | 0.036621 | 121.4539 | 121.5271 | -0.11444 | -0.14191 | 121.4722 | 121.4813 | 121.4905 | 121.4539
2918.3594 | 121.7468 | -121.4951 | 0.13275 | -0.0016785 | 6.9786 | 0.016981 | -0.0030036 | -0.001568 | -0.0097455 | -0.001726 | -0.00054933 | 0.0043686 | 0.014605 | 0.0074362 | -0.012395 | 0.029162 | -0.0035056 | -0.022888 | -0.004578 | 0.013733 | -0.013733 | 0.086975 | 0.004578 | -0.013733 | -0.054932 | 0.054932 | -0.009155 | 0.009155 | 0.082397 | 0.004578 | 0.13275 | 121.5088 | -0.13733 | -0.14648 | 121.582 | 121.4813 | 121.4996 | -0.027466 | -0.009155 | 121.4859 | -0.077819 | -0.1236 | 121.5775 | 121.6278 | 121.4996 | 0.14191 | 0.013733 | 0.073242 | -0.027466 | 0.091552 | 0.01831 | -0.018311 | 0.064087 | 121.4905 | 121.55 | -0.11902 | -0.14191 | 121.4813 | 121.5042 | 121.4722 | 121.4401
2920.0469 | 121.6873 | -121.5271 | 0.16937 | 0.01358 | 6.9797 | 0.015272 | -0.0030036 | 0.0024908 | -0.0067547 | -0.00087163 | -0.0036011 | 0.002446 | 0.013965 | 0.0067954 | -0.0081219 | 0.027666 | -0.006069 | -0.036621 | -0.013733 | 0.018311 | -0.050354 | 0 | -0.064087 | -0.050354 | -0.086975 | 0.041199 | 0 | -0.018311 | 0.018311 | -0.045776 | 0.086975 | 121.5454 | -0.18311 | -0.21973 | 121.5271 | 121.4767 | 121.463 | -0.068665 | -0.082398 | 121.5271 | -0.12817 | -0.18768 | 121.5454 | 121.6141 | 121.4813 | 0.086975 | -0.045776 | -0.018311 | -0.068665 | 0.018311 | -0.018311 | -0.032044 | 0.041199 | 121.5134 | 121.5683 | -0.15106 | -0.16937 | 121.4767 | 121.5088 | 121.4905 | 121.4401
2921.8125 | 121.7926 | -121.4951 | 0.13275 | -0.0016785 | 6.9784 | 0.016126 | -0.0051398 | 0.00078177 | -0.0063275 | -0.00087163 | -0.0066527 | 0.0018052 | 0.013537 | 0.006368 | -0.0066265 | 0.029589 | 0.0014078 | 0.022888 | -0.059509 | 0.054932 | 0.082397 | 0.19684 | 0.086975 | 0.073242 | 0.091553 | 0.013733 | 0.032043 | 0.091553 | 0.14648 | 0.086975 | 0.16022 | 121.55 | -0.19226 | -0.050354 | 121.6919 | 121.5683 | 121.582 | 0.01831 | 0.032043 | 121.5271 | -0.11902 | -0.041198 | 121.6415 | 121.6553 | 121.582 | 0.12817 | 0.054932 | 0.14191 | 0.027465 | 0.11444 | 0.05951 | -0.11444 | -0.01831 | 121.4355 | 121.5088 | -0.077819 | -0.10071 | 121.5775 | 121.5866 | 121.5179 | 121.5866
2923.4844 | 121.7468 | -121.5317 | 0.12817 | -0.009308 | 6.9795 | 0.015699 | -0.0019354 | 0.005268 | -0.0084637 | -0.0010852 | -0.00054933 | 0.0039414 | 0.014178 | 0.0057272 | -0.010899 | 0.028948 | -0.0071372 | -0.018311 | -0.009155 | 0.009155 | -0.032043 | 0.064087 | -0.004578 | -0.009155 | -0.068665 | 0.045776 | -0.004578 | 0.018311 | 0.068665 | 0.009155 | 0.1236 | 121.5408 | -0.13733 | -0.16022 | 121.5958 | 121.5225 | 121.5271 | -0.01831 | -0.013733 | 121.5271 | -0.082398 | -0.10986 | 121.6003 | 121.6553 | 121.5408 | 0.12817 | 0.013733 | 0.054932 | -0.041198 | 0.073243 | 0.022889 | -0.01831 | 0.050354 | 121.5225 | 121.5775 | -0.11902 | -0.13275 | 121.4996 | 121.55 | 121.5134 | 121.463
2925.2188 | 121.7651 | -121.5408 | 0.13275 | -0.024567 | 6.9795 | 0.01399 | -0.0034308 | 0.0039862 | -0.0093183 | 0.0031872 | 0.0025025 | 0.0045822 | 0.015674 | 0.01299 | -0.0072675 | 0.029803 | -0.0020102 | 0.004578 | -0.022888 | 0.032043 | 0.013733 | 0.10986 | 0.027466 | 0.018311 | -0.009155 | 0.041199 | -0.004578 | 0.027466 | 0.091553 | 0.032043 | 0.13733 | 121.5729 | -0.15564 | -0.11902 | 121.6507 | 121.5591 | 121.5683 | -0.013732 | -0.004577 | 121.5363 | -0.091552 | -0.10529 | 121.6324 | 121.6782 | 121.5729 | 0.14191 | 0.036621 | 0.07782 | -0.01831 | 0.096131 | 0.032044 | -0.054931 | 0.045777 | 121.5179 | 121.582 | -0.10071 | -0.13733 | 121.5546 | 121.5683 | 121.5454 | 121.5317
2926.9062 | 121.7331 | -121.5317 | 0.12817 | 0.005951 | 6.9816 | 0.016981 | -0.0040716 | 0.0012092 | -0.0099591 | -0.0027942 | -0.0036011 | 0.004155 | 0.013965 | -0.00025417 | -0.0072675 | 0.028521 | -0.0035056 | -0.004578 | -0.013733 | 0.022888 | 0.004578 | 0.091553 | -0.004578 | 0.004578 | -0.041199 | 0.027466 | -0.013733 | -0.004578 | 0.050354 | -0.032043 | 0.09613 | 121.5546 | -0.14191 | -0.1236 | 121.6232 | 121.5363 | 121.5271 | -0.01831 | -0.027466 | 121.5179 | -0.10071 | -0.13275 | 121.582 | 121.6278 | 121.4996 | 0.10986 | -0.01831 | 0.068665 | -0.01831 | 0.064087 | 0.009155 | -0.036621 | 0.041199 | 121.5179 | 121.5591 | -0.10529 | -0.14191 | 121.5363 | 121.5271 | 121.5271 | 121.4905
2928.6562 | 121.8658 | -121.5317 | 0.11444 | -0.0016785 | 6.9774 | 0.015272 | -0.0057806 | -0.0011408 | -0.011027 | -1.7026e-05 | -0.00054933 | 0.0030868 | 0.01311 | 0.017476 | -0.011754 | 0.027453 | -0.00030119 | 0.027466 | -0.059509 | 0.064087 | 0.07782 | 0.20599 | 0.11902 | 0.10529 | 0.086975 | 0.009155 | 0.027466 | 0.11444 | 0.21515 | 0.14648 | 0.19684 | 121.5958 | -0.17395 | -0.036621 | 121.7377 | 121.637 | 121.6507 | 0.041199 | 0.054932 | 121.5591 | -0.10529 | 0 | 121.7468 | 121.7285 | 121.6782 | 0.16937 | 0.11902 | 0.14191 | 0.013733 | 0.18768 | 0.086975 | -0.1236 | -0.018311 | 121.4722 | 121.5408 | -0.050354 | -0.086975 | 121.6095 | 121.6461 | 121.5591 | 121.6187
2930.4062 | 121.8521 | -121.5408 | 0.11444 | -0.009308 | 6.9776 | 0.014631 | -0.0053534 | -7.2628e-05 | -0.011027 | -0.0027942 | -0.0036011 | 9.6204e-05 | 0.012469 | 0.013418 | -0.0089765 | 0.027453 | -0.0024374 | -0.009155 | -0.045776 | 0.050354 | 0.022888 | 0.13733 | 0.045776 | 0.064087 | 0.009155 | -0.004578 | 0.018311 | 0.073242 | 0.11902 | 0.07782 | 0.16022 | 121.5912 | -0.16022 | -0.091553 | 121.6782 | 121.6049 | 121.5866 | 0.013733 | -0.004578 | 121.5591 | -0.11902 | -0.041199 | 121.6599 | 121.7011 | 121.6187 | 0.14191 | 0.059509 | 0.086975 | -0.027466 | 0.10071 | 0.054931 | -0.09613 | -0.022889 | 121.4951 | 121.5363 | -0.064087 | -0.09613 | 121.5637 | 121.6141 | 121.5317 | 121.55
2932.1562 | 121.3028 | -121.1609 | 0.11902 | -0.0016785 | 6.9818 | 0.017195 | -0.0015082 | 0.0027044 | -0.0095319 | -0.0032214 | -0.0066527 | 0.0022324 | 0.015674 | 0.016195 | -0.0091901 | 0.028307 | -0.002651 | -0.041199 | -0.022888 | 0.018311 | -0.041199 | 0.032043 | -0.045776 | -0.050354 | -0.10529 | 0.050354 | -0.013733 | -0.036621 | 0.004578 | -0.068665 | 0.091553 | 121.1792 | -0.14191 | -0.16022 | 121.1929 | 121.1105 | 121.1151 | -0.068665 | -0.064087 | 121.1472 | -0.068665 | -0.15564 | 121.1655 | 121.2524 | 121.0922 | 0.10529 | -0.054932 | 0.013732 | -0.05951 | 0.018311 | -0.022888 | -0.041199 | 0.064087 | 121.138 | 121.2112 | -0.10071 | -0.13275 | 121.1197 | 121.1243 | 121.1197 | 121.0556
2933.9062 | 121.5454 | -121.3531 | 0.13275 | -0.009308 | 6.9838 | 0.013777 | -0.00279 | 0.0033454 | -0.0099591 | -0.0015124 | 0.0055543 | 0.005223 | 0.013965 | 0.0065816 | -0.011326 | 0.027025 | -0.0028646 | -0.041199 | -0.013733 | 0.018311 | -0.050354 | 0.059509 | -0.004578 | -0.009155 | -0.086975 | 0.041199 | 0 | -0.032043 | 0.050354 | -0.004578 | 0.10529 | 121.3715 | -0.14648 | -0.18311 | 121.4127 | 121.344 | 121.3486 | -0.027466 | -0.022889 | 121.3531 | -0.091552 | -0.16479 | 121.4035 | 121.4584 | 121.3486 | 0.10529 | -0.004578 | 0.041198 | -0.068665 | 0.050354 | -0.032043 | -0.032044 | 0.041199 | 121.3394 | 121.3943 | -0.11444 | -0.13275 | 121.3028 | 121.3211 | 121.3119 | 121.2662
2935.5781 | 121.6919 | -121.3623 | 0.10529 | -0.009308 | 6.9821 | 0.017408 | -0.0023626 | 0.0029182 | -0.0069683 | -0.0012988 | -0.00054933 | 0.0003098 | 0.01311 | 0.0078634 | -0.0055585 | 0.030016 | -0.001583 | 0.036621 | -0.064087 | 0.054932 | 0.059509 | 0.19226 | 0.054932 | 0.068665 | 0.091553 | -0.022888 | 0.032043 | 0.11444 | 0.16479 | 0.10529 | 0.21515 | 121.4172 | -0.16937 | -0.045777 | 121.5546 | 121.431 | 121.4172 | 0.013733 | 0 | 121.3943 | -0.12817 | 0.009155 | 121.5271 | 121.5775 | 121.4676 | 0.18311 | 0.073243 | 0.13733 | 0.004577 | 0.13275 | 0.082398 | -0.11902 | -0.054931 | 121.2982 | 121.3394 | -0.050354 | -0.073243 | 121.4218 | 121.4767 | 121.3989 | 121.4539
2937.3281 | 121.6141 | -121.4401 | 0.14648 | -0.009308 | 6.9812 | 0.016981 | 0.00041441 | 0.00099557 | -0.0088911 | -0.002367 | -0.0066527 | 0.0026596 | 0.01311 | -4.0566e-05 | -0.010899 | 0.028307 | -0.0024374 | -0.013733 | -0.041199 | 0.027466 | -0.009155 | 0.091553 | -0.036621 | -0.009155 | -0.050354 | 0.009155 | 0.004578 | -0.013733 | 0.036621 | -0.041199 | 0.086975 | 121.4676 | -0.18768 | -0.15564 | 121.5317 | 121.431 | 121.4035 | -0.036621 | -0.064087 | 121.4447 | -0.13733 | -0.16022 | 121.4767 | 121.5271 | 121.3989 | 0.082397 | -0.045777 | 0.064087 | -0.036621 | 0.032043 | -0.018311 | -0.068665 | 0.004577 | 121.3989 | 121.4493 | -0.11902 | -0.14191 | 121.431 | 121.4264 | 121.4264 | 121.3898
2939.0625 | 120.8817 | -120.5933 | 0.10986 | -0.0016785 | 6.9445 | -0.059923 | -0.019025 | 0.0059088 | 0.028707 | 0.03929 | -0.00054933 | 0.002446 | 0.012469 | 0.006368 | -0.0066265 | 0.027666 | -0.00051479 | -0.064087 | -0.068665 | 0.2243 | -0.10986 | -0.032043 | -0.3891 | -0.55389 | 0.009155 | 0.032043 | 0.009155 | 0.032043 | 0.082397 | 0.018311 | 0.12817 | 120.8176 | -0.17853 | -0.21973 | 120.5612 | 120.0394 | 120.2042 | -0.7782 | -0.6134 | 120.6024 | -0.07782 | -0.07782 | 120.6757 | 120.7214 | 120.6116 | 0.11902 | 0.009156 | -0.25635 | -0.33417 | 0.073242 | 0.022888 | -0.29297 | 0.022888 | 120.5246 | 120.6253 | 0.11444 | -0.10071 | 120.4834 | 120.6253 | 120.5292 | 120.6024
2940.7969 | 120.9091 | -120.5933 | 0.11902 | -0.009308 | 6.9752 | 0.019544 | -0.0059942 | -0.00028623 | -0.0099591 | -0.00065803 | -0.00054933 | 0.0037278 | 0.014819 | 0.012136 | -0.0076947 | 0.029162 | -0.0039328 | -0.064087 | -0.027466 | 0.013733 | -0.032043 | 0.064087 | -0.041199 | -0.022888 | -0.032043 | 0.022888 | 0.009155 | 0.041199 | 0.082397 | 0.036621 | 0.14191 | 120.607 | -0.14649 | -0.15106 | 120.6573 | 120.5704 | 120.5521 | -0.036621 | -0.054932 | 120.6024 | -0.096131 | -0.07782 | 120.6757 | 120.7352 | 120.6299 | 0.13275 | 0.027466 | 0.050354 | -0.045776 | 0.073242 | 0.032044 | -0.041199 | 0.013733 | 120.5658 | 120.6161 | -0.10529 | -0.10986 | 120.5612 | 120.6345 | 120.5292 | 120.5612
2942.5625 | 121.4035 | -121.138 | 0.10986 | -0.0016785 | 6.9767 | 0.015058 | -0.0087714 | 0.00185 | -0.0093183 | -0.001726 | -0.00054933 | 0.0028732 | 0.01311 | 0.009786 | -0.010045 | 0.030016 | -0.0028646 | -0.022888 | -0.054932 | 0.036621 | 0.009155 | 0.13275 | 0.022888 | 0.041199 | -0.004578 | -0.009155 | 0.013733 | 0.050354 | 0.10986 | 0.045776 | 0.13275 | 121.1746 | -0.16479 | -0.10071 | 121.2708 | 121.1792 | 121.1609 | 0.004578 | -0.013733 | 121.1517 | -0.11902 | -0.059509 | 121.2479 | 121.2708 | 121.1838 | 0.11902 | 0.032043 | 0.09613 | -0.027466 | 0.09613 | 0.036621 | -0.091553 | -0.022888 | 121.0831 | 121.1288 | -0.073242 | -0.09613 | 121.1472 | 121.1884 | 121.1151 | 121.1334
2944.25 | 121.3989 | -121.2662 | 0.1236 | -0.009308 | 6.9774 | 0.015486 | -0.007276 | -0.0045586 | -0.0086773 | -0.001726 | -0.0036011 | 0.0026596 | 0.011615 | 0.011922 | -0.011754 | 0.027666 | -0.00030119 | -0.068665 | -0.036621 | -0.004578 | -0.054932 | 0.050354 | -0.022888 | -0.022888 | -0.082397 | 0.036621 | -0.018311 | -0.032043 | 0.041199 | -0.027466 | 0.068665 | 121.2616 | -0.16022 | -0.17853 | 121.3165 | 121.2433 | 121.2433 | -0.01831 | -0.01831 | 121.2479 | -0.086975 | -0.15564 | 121.3074 | 121.3348 | 121.2387 | 0.086976 | -0.009155 | 0.054932 | -0.050354 | 0.05951 | -0.013732 | -0.032043 | 0.054932 | 121.2296 | 121.3028 | -0.12817 | -0.14191 | 121.2112 | 121.2341 | 121.1975 | 121.1838
2946 | 121.4767 | -121.2982 | 0.13733 | 0.005951 | 6.9795 | 0.014631 | -0.0064216 | -0.001568 | -0.010386 | -0.0021532 | -0.0036011 | 0.0043686 | 0.012683 | 0.01235 | -0.011754 | 0.027239 | -0.006069 | -0.054932 | -0.036621 | 0.004578 | -0.059509 | 0.054932 | -0.022888 | -0.027466 | -0.086975 | 0.045776 | -0.004578 | -0.022888 | 0.027466 | -0.022888 | 0.07782 | 121.3028 | -0.17395 | -0.19684 | 121.3531 | 121.2708 | 121.2753 | -0.032044 | -0.027466 | 121.2936 | -0.091553 | -0.16022 | 121.3257 | 121.376 | 121.2753 | 0.082398 | -0.01831 | 0.050354 | -0.064087 | 0.032044 | -0.01831 | -0.041199 | 0.050354 | 121.2616 | 121.344 | -0.13275 | -0.14191 | 121.2387 | 121.2753 | 121.2433 | 121.2112
2947.7812 | 121.1655 | -120.8084 | 0.11902 | -0.009308 | 6.9795 | 0.018476 | -0.0064216 | -0.0013544 | -0.0059003 | -0.0032214 | -0.0036011 | 0.0022324 | 0.012897 | 0.015554 | -0.0047039 | 0.028734 | -0.00094199 | -0.009155 | -0.027466 | 0.027466 | -0.004578 | 0.11902 | 0.009155 | 0.022888 | 0.022888 | 0 | 0.027466 | 0.091553 | 0.14648 | 0.082397 | 0.16937 | 120.8359 | -0.14649 | -0.1236 | 120.9274 | 120.8313 | 120.8176 | -0.004578 | -0.018311 | 120.8359 | -0.11902 | -0.027466 | 120.9549 | 120.9778 | 120.8908 | 0.14191 | 0.054931 | 0.091553 | -0.032044 | 0.11902 | 0.064087 | -0.054932 | -0.027466 | 120.7809 | 120.8084 | -0.091553 | -0.091553 | 120.8038 | 120.9 | 120.7993 | 120.8313
2949.4688 | 121.3074 | -121.0876 | 0.11902 | -0.009308 | 6.9806 | 0.015058 | -0.0053534 | -0.0041314 | -0.0073957 | -0.0025806 | -0.00054933 | 0.0054368 | 0.01311 | 0.0065816 | -0.010045 | 0.02788 | -0.0047874 | 0.036621 | -0.073242 | 0.032043 | 0.036621 | 0.14648 | 0.068665 | 0.054932 | -0.009155 | 0.018311 | 0.027466 | 0 | 0.073242 | 0.013733 | 0.10071 | 121.1197 | -0.19226 | -0.082398 | 121.2341 | 121.1426 | 121.1563 | 0.022889 | 0.036622 | 121.1151 | -0.10071 | -0.11902 | 121.1609 | 121.1884 | 121.1014 | 0.073242 | -0.013733 | 0.11444 | 0.004578 | 0.045776 | -0.027466 | -0.10529 | -0.009155 | 121.0144 | 121.106 | -0.086976 | -0.091553 | 121.1243 | 121.0876 | 121.1243 | 121.0785
2951.2188 | 121.4676 | -121.1426 | 0.07782 | 0.005951 | 6.9799 | 0.016126 | -0.0040716 | 0.0059088 | -0.0044049 | -0.0059984 | -0.00054933 | 0.002446 | 0.010333 | 0.0050864 | -0.0053449 | 0.030871 | -0.0056418 | 0.036621 | -0.073242 | 0.045776 | 0.068665 | 0.1831 | 0.050354 | 0.059509 | 0.082397 | -0.009155 | 0.036621 | 0.11444 | 0.16937 | 0.091553 | 0.20142 | 121.1884 | -0.15106 | -0.009155 | 121.3257 | 121.2021 | 121.1929 | 0.013733 | 0.004578 | 121.1792 | -0.086975 | 0.036621 | 121.312 | 121.344 | 121.2341 | 0.1648 | 0.054932 | 0.13733 | 0.022889 | 0.13275 | 0.07782 | -0.11902 | -0.045776 | 121.0693 | 121.1334 | -0.032044 | -0.041199 | 121.2112 | 121.257 | 121.1792 | 121.225
2952.9688 | 118.3456 | -85.4507 | 32.0663 | 0.005951 | 10.6688 | -0.10393 | 2.4509 | -0.00049983 | 0.049215 | 0.057234 | -0.00054933 | 0.0030868 | 0.014392 | 0.006368 | -0.013249 | 0.028094 | -0.0071372 | 9.494 | 31.3248 | 5.0995 | 32.4692 | 10.4187 | 14.6896 | 14.621 | -0.064087 | -0.041199 | -0.036621 | -0.045776 | 0.018311 | -0.032043 | 0.045776 | 90.5502 | -0.74158 | 0.40283 | 95.8694 | 100.0717 | 100.1404 | 9.5215 | 9.5901 | 85.4141 | -32.1075 | -32.1121 | 85.4691 | 85.4965 | 85.4187 | 0.082397 | 0.004578 | 5.3192 | 27.3697 | 0.054932 | -0.009155 | 26.2253 | -0.004578 | 116.7755 | 85.4095 | -26.9669 | -32.103 | 117.9199 | 85.405 | 94.9448 | 85.3867
2954.7188 | 121.3028 | -121.0007 | 0.09613 | -0.0016785 | 6.9784 | 0.016981 | -0.0034308 | 0.00056817 | -0.0084637 | -0.001726 | -0.0036011 | -0.0005448 | 0.014178 | 0.011495 | -0.0070539 | 0.029162 | -8.7586e-05 | -0.013733 | -0.059509 | 0.045776 | 0.027466 | 0.16022 | 0.045776 | 0.032043 | 0.018311 | 0.009155 | 0.018311 | 0.050354 | 0.09613 | 0.045776 | 0.13733 | 121.0464 | -0.15564 | -0.068664 | 121.1609 | 121.0327 | 121.0464 | -0.013733 | 0 | 121.019 | -0.086975 | -0.045776 | 121.0968 | 121.138 | 121.0464 | 0.11902 | 0.027465 | 0.11444 | -0.01831 | 0.077819 | 0.032043 | -0.10528 | -0.009156 | 120.9412 | 121.0098 | -0.050354 | -0.077819 | 121.0281 | 121.051 | 120.9869 | 121.019
2956.3906 | 121.3348 | -121.1334 | 0.10986 | -0.009308 | 6.9816 | 0.015058 | -0.004499 | 0.0016364 | -0.0080365 | -0.0012988 | -0.00054933 | 0.0030868 | 0.013965 | 0.011709 | -0.010472 | 0.026171 | -0.00051479 | -0.022888 | -0.041199 | 0.004578 | -0.027466 | 0.064087 | 0 | -0.009155 | -0.045776 | 0.036621 | -0.004578 | 0.013733 | 0.073242 | 0.009155 | 0.1236 | 121.138 | -0.15106 | -0.13733 | 121.1975 | 121.1243 | 121.1334 | -0.013733 | -0.004578 | 121.1288 | -0.073242 | -0.09613 | 121.2067 | 121.257 | 121.1426 | 0.12817 | 0.013733 | 0.059509 | -0.032044 | 0.07782 | 0.018311 | -0.045777 | 0.041199 | 121.0922 | 121.17 | -0.10529 | -0.11444 | 121.106 | 121.1472 | 121.1105 | 121.0876
2958.1406 | 121.4722 | -121.138 | 0.091553 | -0.009308 | 6.9791 | 0.014845 | -0.0053534 | 0.0041998 | -0.0065411 | -0.0040758 | -0.00054933 | 0.0009506 | 0.014605 | 0.0078634 | -0.010258 | 0.026812 | -0.0028646 | 0.054932 | -0.068665 | 0.045776 | 0.068665 | 0.21515 | 0.10071 | 0.09613 | 0.10071 | -0.018311 | 0.022888 | 0.09613 | 0.17395 | 0.13733 | 0.19226 | 121.1838 | -0.16022 | -0.022888 | 121.3531 | 121.2341 | 121.2387 | 0.050354 | 0.054932 | 121.1609 | -0.10986 | 0.004577 | 121.312 | 121.3303 | 121.2753 | 0.16937 | 0.11444 | 0.16937 | 0.022889 | 0.15106 | 0.073242 | -0.11444 | -0.041199 | 121.0693 | 121.1197 | -0.045777 | -0.068665 | 121.2067 | 121.2341 | 121.1929 | 121.2387
2959.875 | 121.4127 | -121.225 | 0.12817 | 0.005951 | 6.9814 | 0.013563 | -0.0032172 | 0.0016364 | -0.0099591 | -0.0010852 | -0.00054933 | 0.0039414 | 0.012042 | 0.0048728 | -0.01154 | 0.026812 | -0.003292 | -0.041199 | -0.018311 | 0.009155 | -0.022888 | 0.054932 | -0.004578 | -0.009155 | -0.045776 | 0.032043 | -0.022888 | 0.004578 | 0.064087 | 0.009155 | 0.1236 | 121.2341 | -0.14649 | -0.15106 | 121.2799 | 121.2158 | 121.2204 | -0.01831 | -0.013733 | 121.2021 | -0.096131 | -0.1236 | 121.2891 | 121.3486 | 121.2341 | 0.14648 | 0.032043 | 0.045777 | -0.032043 | 0.086975 | 0.027466 | -0.027466 | 0.054931 | 121.2067 | 121.257 | -0.11902 | -0.15106 | 121.2021 | 121.2296 | 121.1838 | 121.1792
2961.5625 | 121.3898 | -121.2433 | 0.10529 | -0.009308 | 6.9814 | 0.016767 | -0.0051398 | 0.00185 | -0.0099591 | -0.0021532 | -0.0036011 | 0.0033004 | 0.014178 | -0.00046777 | -0.011754 | 0.025744 | -8.7586e-05 | -0.041199 | -0.050354 | 0 | -0.050354 | 0.064087 | -0.013733 | -0.013733 | -0.073242 | 0.041199 | -0.018311 | -0.027466 | 0.041199 | -0.022888 | 0.07782 | 121.2433 | -0.15564 | -0.15564 | 121.3074 | 121.2296 | 121.2296 | -0.013733 | -0.013733 | 121.225 | -0.064087 | -0.13275 | 121.2845 | 121.3211 | 121.2204 | 0.096131 | -0.004577 | 0.064087 | -0.050354 | 0.05951 | -0.009155 | -0.050354 | 0.05951 | 121.1929 | 121.2845 | -0.10529 | -0.1236 | 121.1929 | 121.2158 | 121.2021 | 121.17
2963.2969 | 121.4905 | -121.2067 | 0.11902 | -0.009308 | 6.9825 | 0.016554 | -0.0012946 | 0.0031318 | -0.0063275 | -0.0045032 | -0.0036011 | 0.003514 | 0.014605 | 0.0078634 | -0.0066265 | 0.029803 | -0.0056418 | -0.045776 | -0.036621 | 0.004578 | -0.032043 | 0.059509 | -0.045776 | -0.018311 | -0.018311 | 0 | 0.004578 | 0.068665 | 0.091553 | 0.032043 | 0.14648 | 121.2112 | -0.15564 | -0.15106 | 121.2662 | 121.1884 | 121.1609 | -0.022889 | -0.050354 | 121.2112 | -0.11902 | -0.050354 | 121.2982 | 121.3531 | 121.2387 | 0.14191 | 0.027465 | 0.054931 | -0.036621 | 0.086975 | 0.064087 | -0.041199 | -0.004578 | 121.17 | 121.2067 | -0.11444 | -0.11444 | 121.1746 | 121.2753 | 121.1609 | 121.1884
2965.0469 | 121.5271 | -121.2524 | 0.11444 | -0.0016785 | 6.9797 | 0.015699 | -0.0049262 | -0.003277 | -0.0078229 | -0.0036486 | -0.0036011 | 0.0015914 | 0.012683 | 0.018972 | -0.0087629 | 0.031511 | 0.00033961 | -0.018311 | -0.07782 | 0.027466 | 0.009155 | 0.10529 | 0.018311 | 0.027466 | -0.013733 | 0 | 0.022888 | 0.045776 | 0.10071 | 0.068665 | 0.15564 | 121.2799 | -0.19226 | -0.10529 | 121.3577 | 121.2799 | 121.2708 | 0 | -0.009155 | 121.2753 | -0.11444 | -0.068665 | 121.3531 | 121.4081 | 121.3211 | 0.13275 | 0.045777 | 0.07782 | -0.018311 | 0.07782 | 0.022888 | -0.10529 | -0.022888 | 121.1746 | 121.2524 | -0.086975 | -0.091553 | 121.2616 | 121.2982 | 121.2341 | 121.2387
2966.8125 | 121.1243 | -120.813 | 0.10071 | -0.0016785 | 6.9872 | 0.018049 | 0.0010552 | 0.00056817 | -0.0088911 | -0.0032214 | -0.0036011 | 0.0022324 | 0.012683 | 0.011922 | -0.0074811 | 0.029803 | -0.0013694 | 0.018311 | -0.054932 | 0.064087 | 0.082397 | 0.18768 | 0.059509 | 0.07782 | 0.086975 | 0 | 0.009155 | 0.07782 | 0.13733 | 0.086975 | 0.17395 | 120.8771 | -0.15564 | -0.018311 | 121.0007 | 120.8908 | 120.8725 | 0.013733 | -0.004578 | 120.8221 | -0.10071 | -0.022888 | 120.9503 | 120.9869 | 120.9 | 0.16479 | 0.07782 | 0.1236 | 0.01831 | 0.12817 | 0.068665 | -0.11902 | -0.009155 | 120.7581 | 120.813 | -0.036621 | -0.091553 | 120.8954 | 120.8908 | 120.8313 | 120.9
2968.5 | 121.2296 | -121.0419 | 0.13275 | -0.016937 | 6.9868 | 0.016554 | 0.0034052 | 0.0020636 | -0.0082501 | -0.00044443 | -0.00054933 | 0.0047958 | 0.013751 | 0.006368 | -0.0085491 | 0.028948 | -0.0035056 | -0.041199 | -0.036621 | 0.022888 | -0.032043 | 0.032043 | -0.064087 | -0.059509 | -0.073242 | 0.027466 | 0 | -0.018311 | 0 | -0.050354 | 0.091553 | 121.0648 | -0.16937 | -0.16479 | 121.0739 | 120.9824 | 120.9778 | -0.082397 | -0.086975 | 121.0419 | -0.10529 | -0.15106 | 121.0419 | 121.1334 | 120.9915 | 0.091553 | -0.050354 | 0.009155 | -0.054931 | 0 | -0.018311 | -0.059509 | 0.027466 | 121.0052 | 121.0693 | -0.10986 | -0.13275 | 121.0098 | 121.0236 | 121.0007 | 120.9686
2970.2344 | 121.2845 | -121.138 | 0.11444 | -0.016937 | 6.9895 | 0.015913 | 0.0053278 | 0.0033454 | -0.0093183 | -0.0032214 | -0.0036011 | 0.003514 | 0.013965 | 0.0082906 | -0.0087629 | 0.029589 | 0.0011942 | -0.059509 | -0.032043 | 0.018311 | -0.059509 | 0.009155 | -0.054932 | -0.054932 | -0.11902 | 0.022888 | -0.009155 | -0.027466 | 0 | -0.054932 | 0.073242 | 121.1563 | -0.14648 | -0.17395 | 121.1472 | 121.0831 | 121.0831 | -0.073243 | -0.073243 | 121.1288 | -0.091553 | -0.14191 | 121.138 | 121.2112 | 121.0831 | 0.082397 | -0.045777 | -0.009156 | -0.07782 | 0.009155 | -0.018311 | -0.050354 | 0.032043 | 121.106 | 121.1609 | -0.09613 | -0.1236 | 121.0785 | 121.1105 | 121.0785 | 121.019
2971.9844 | 121.4355 | -121.1288 | 0.09613 | -0.016937 | 6.9863 | 0.015272 | -0.00086739 | -0.00092703 | -0.0097455 | -0.0059984 | -0.00054933 | 0.0022324 | 0.0099057 | 0.0053 | -0.011754 | 0.028094 | -0.003292 | -0.022888 | -0.073242 | 0.059509 | 0.009155 | 0.13733 | 0.050354 | 0.054932 | 0.032043 | -0.004578 | 0.032043 | 0.07782 | 0.14648 | 0.09613 | 0.17395 | 121.1884 | -0.16937 | -0.086975 | 121.2662 | 121.1838 | 121.1792 | -0.004577 | -0.009155 | 121.1609 | -0.10071 | -0.01831 | 121.2753 | 121.3028 | 121.225 | 0.14191 | 0.064087 | 0.07782 | -0.050354 | 0.11444 | 0.045777 | -0.13275 | -0.036621 | 121.0556 | 121.1243 | -0.036621 | -0.064087 | 121.138 | 121.2067 | 121.106 | 121.1609
2973.7344 | 121.0693 | -120.8313 | 0.10071 | 0.005951 | 6.9816 | 0.015486 | -0.00022639 | 0.00099557 | -0.0086773 | -0.0032214 | -0.0036011 | 0.0022324 | 0.015033 | 0.0038046 | -0.0085491 | 0.029162 | -0.0020102 | -0.050354 | -0.027466 | 0.013733 | -0.059509 | 0.054932 | -0.050354 | -0.027466 | -0.054932 | 0.027466 | 0 | 0.018311 | 0.059509 | -0.041199 | 0.10529 | 120.845 | -0.12817 | -0.16022 | 120.8862 | 120.8038 | 120.7809 | -0.041199 | -0.064087 | 120.8313 | -0.073242 | -0.082397 | 120.8908 | 120.9366 | 120.7901 | 0.10529 | -0.041199 | 0.041199 | -0.073242 | 0.059509 | 0.018311 | -0.041199 | 0.027466 | 120.8038 | 120.8588 | -0.086975 | -0.10071 | 120.7718 | 120.8496 | 120.7809 | 120.7764
2975.4219 | 121.1929 | -121.0144 | 0.13733 | -0.0016785 | 6.9833 | 0.017195 | 0.0019098 | -0.00071343 | -0.0067547 | -0.00087163 | -0.00054933 | 0.0033004 | 0.013324 | 0.009786 | -0.0098309 | 0.028307 | -0.003292 | -0.036621 | -0.032043 | 0.027466 | -0.068665 | 0.027466 | -0.082397 | -0.068665 | -0.082397 | 0.032043 | -0.018311 | -0.027466 | 0.013733 | -0.054932 | 0.091553 | 121.0419 | -0.16937 | -0.20599 | 121.0419 | 120.9457 | 120.932 | -0.096131 | -0.10986 | 120.9961 | -0.10529 | -0.16479 | 121.0281 | 121.106 | 120.9595 | 0.10986 | -0.036621 | 0 | -0.096131 | 0.032044 | -0.009155 | -0.059509 | 0.050354 | 120.9824 | 121.0464 | -0.10986 | -0.15564 | 120.9457 | 120.9869 | 120.9778 | 120.932
2977.1562 | 121.257 | -121.0693 | 0.12817 | -0.009308 | 6.9812 | 0.015699 | -0.00043999 | -0.00092703 | -0.0080365 | -0.0036486 | 0.0025025 | 0.0030868 | 0.012683 | 0.010641 | -0.012608 | 0.027666 | -0.0020102 | 0 | -0.064087 | 0.045776 | 0.018311 | 0.15564 | 0.054932 | 0.045776 | -0.004578 | 0.013733 | -0.004578 | 0 | 0.091553 | 0.036621 | 0.091553 | 121.1151 | -0.19226 | -0.10986 | 121.225 | 121.1151 | 121.1243 | 0 | 0.009156 | 121.0648 | -0.11444 | -0.12817 | 121.1609 | 121.1609 | 121.106 | 0.096131 | 0.041199 | 0.10986 | -0.027465 | 0.096131 | 0.004578 | -0.10986 | 0.018311 | 121.0052 | 121.0831 | -0.082398 | -0.13275 | 121.0876 | 121.0693 | 121.0693 | 121.0648
2978.8438 | 121.4127 | -121.0831 | 0.091553 | -0.0016785 | 6.9803 | 0.015486 | -0.0012946 | -0.001568 | -0.0080365 | -0.0021532 | -0.00054933 | 0.0015914 | 0.01311 | 0.010213 | -0.010899 | 0.029375 | -0.0013694 | -0.004578 | -0.059509 | 0.059509 | 0.027466 | 0.16479 | 0.073242 | 0.082397 | 0.064087 | -0.013733 | 0.004578 | 0.07782 | 0.15106 | 0.11444 | 0.19226 | 121.1426 | -0.15106 | -0.064087 | 121.2479 | 121.1655 | 121.1563 | 0.022888 | 0.013733 | 121.0876 | -0.10529 | -0.013733 | 121.2341 | 121.2753 | 121.1975 | 0.18768 | 0.10986 | 0.10529 | -0.032043 | 0.14648 | 0.073242 | -0.11902 | -0.018311 | 121.0236 | 121.0693 | -0.032044 | -0.086975 | 121.1105 | 121.1609 | 121.0785 | 121.1472
2980.5938 | 120.9366 | -120.6299 | 0.10071 | 0.005951 | 6.9818 | 0.018476 | -0.00022639 | 0.00185 | -0.0093183 | -0.0053576 | -0.00054933 | 0.0003098 | 0.012042 | 0.0099996 | -0.0096173 | 0.028307 | -0.0022238 | -0.032043 | -0.082397 | 0.045776 | 0.018311 | 0.13275 | 0.027466 | 0.036621 | 0.004578 | -0.009155 | 0.004578 | 0.045776 | 0.091553 | 0.036621 | 0.13733 | 120.6757 | -0.18311 | -0.082397 | 120.7626 | 120.6665 | 120.6573 | -0.009155 | -0.01831 | 120.6345 | -0.10986 | -0.054932 | 120.7214 | 120.7672 | 120.6665 | 0.13275 | 0.032043 | 0.086975 | -0.027465 | 0.086975 | 0.041198 | -0.12817 | -0.013733 | 120.5475 | 120.6207 | -0.054932 | -0.09613 | 120.6482 | 120.6757 | 120.5978 | 120.6345
2982.3438 | 121.1334 | -120.9183 | 0.11902 | -0.0016785 | 6.9848 | 0.015913 | 0.0021234 | 0.0014228 | -0.0093183 | -0.00023063 | -0.00054933 | 0.0037278 | 0.012683 | 0.0091452 | -0.0074811 | 0.028734 | -0.0054282 | 0.013733 | -0.059509 | 0.013733 | 0.009155 | 0.10986 | 0.018311 | 0.004578 | 0.009155 | 0.018311 | 0 | 0.022888 | 0.073242 | -0.009155 | 0.10986 | 120.932 | -0.17853 | -0.10986 | 121.0281 | 120.9229 | 120.9366 | -0.009155 | 0.004578 | 120.9183 | -0.10071 | -0.096131 | 120.9915 | 121.0281 | 120.9091 | 0.10986 | -0.009155 | 0.09613 | -0.004578 | 0.073242 | 0.022888 | -0.073242 | 0.018311 | 120.8588 | 120.9366 | -0.10529 | -0.11902 | 120.9274 | 120.9412 | 120.932 | 120.9274
2984.0938 | 121.2891 | -120.9641 | 0.064087 | -0.009308 | 6.985 | 0.017195 | -0.0023626 | 0.005268 | -0.0078229 | -0.0036486 | -0.0036011 | 0.000737 | 0.01311 | 0.014486 | -0.0094037 | 0.030443 | -0.006069 | 0.032043 | -0.07782 | 0.059509 | 0.068665 | 0.18768 | 0.064087 | 0.073242 | 0.086975 | -0.018311 | 0.041199 | 0.11444 | 0.15564 | 0.09613 | 0.19684 | 121.0236 | -0.14191 | 0.004578 | 121.1517 | 121.0373 | 121.0281 | 0.013733 | 0.004578 | 121.0052 | -0.082398 | 0.050354 | 121.1197 | 121.1609 | 121.0602 | 0.15564 | 0.054931 | 0.12817 | 0.009156 | 0.11444 | 0.073242 | -0.13733 | -0.05951 | 120.8862 | 120.9457 | -0.004578 | -0.022888 | 121.0327 | 121.0785 | 120.9961 | 121.051
2985.8281 | 121.2158 | -121.0693 | 0.11444 | -0.0016785 | 6.9848 | 0.014631 | 0.00020081 | 0.00056817 | -0.011241 | -0.00023063 | 0.0025025 | 0.0013778 | 0.013965 | 0.006368 | -0.01389 | 0.027239 | -0.00094199 | -0.050354 | -0.045776 | 0.004578 | -0.059509 | 0.059509 | 0 | -0.004578 | -0.064087 | 0.041199 | -0.013733 | -0.022888 | 0.027466 | -0.022888 | 0.068665 | 121.0739 | -0.16022 | -0.17395 | 121.1288 | 121.0648 | 121.0693 | -0.009156 | -0.004578 | 121.0556 | -0.073242 | -0.13733 | 121.0968 | 121.138 | 121.0464 | 0.082398 | -0.009155 | 0.054931 | -0.064087 | 0.041199 | -0.009155 | -0.050354 | 0.054932 | 121.0236 | 121.1105 | -0.10986 | -0.12817 | 121.0098 | 121.0464 | 121.019 | 121.0052
2987.5156 | 121.3531 | -121.0556 | 0.1236 | 0.005951 | 6.9844 | 0.01634 | -0.00022639 | 0.0065498 | -0.0059003 | 0.00041017 | -0.0036011 | 0.0028732 | 0.013324 | 0.008077 | -0.0094037 | 0.024462 | -0.0069236 | -0.004578 | -0.027466 | 0.032043 | -0.004578 | 0.11444 | 0.022888 | 0.032043 | 0.013733 | 0.022888 | -0.009155 | 0.045776 | 0.091553 | 0.036621 | 0.12817 | 121.0876 | -0.15106 | -0.12817 | 121.17 | 121.0876 | 121.0785 | 0 | -0.009155 | 121.0464 | -0.10071 | -0.07782 | 121.1472 | 121.1838 | 121.0922 | 0.13733 | 0.045776 | 0.082398 | -0.036621 | 0.10071 | 0.054931 | -0.059509 | 0.032043 | 121.0281 | 121.0785 | -0.091553 | -0.13275 | 121.051 | 121.1014 | 121.051 | 121.0693
2989.2656 | 121.1563 | -120.8771 | 0.073242 | 0.005951 | 6.9821 | 0.017195 | 0.00084161 | -0.0017816 | -0.0086773 | -0.0030078 | -0.00054933 | 0.0022324 | 0.013324 | 0.0038046 | -0.0089765 | 0.027453 | 0.0014078 | -0.013733 | -0.082397 | 0.054932 | 0.032043 | 0.16937 | 0.036621 | 0.045776 | 0.027466 | -0.004578 | 0.022888 | 0.041199 | 0.10986 | 0.050354 | 0.14648 | 120.932 | -0.15564 | -0.041199 | 121.0464 | 120.9229 | 120.9137 | -0.009156 | -0.018311 | 120.9 | -0.07782 | -0.032043 | 120.9869 | 121.0236 | 120.9274 | 0.1236 | 0.027466 | 0.11444 | -0.022889 | 0.086975 | 0.018311 | -0.13733 | -0.027466 | 120.7947 | 120.8725 | -0.01831 | -0.050354 | 120.9091 | 120.9183 | 120.8633 | 120.9045
2990.9531 | 121.2112 | -120.9732 | 0.11444 | 0.005951 | 6.9844 | 0.015058 | 0.0014826 | 0.003559 | -0.0071821 | -0.0015124 | -0.00054933 | 0.0047958 | 0.012897 | 0.008077 | -0.0089765 | 0.026171 | -0.0017966 | -0.009155 | -0.045776 | 0.004578 | -0.013733 | 0.10986 | 0.009155 | 0.009155 | -0.013733 | 0.036621 | 0 | 0.032043 | 0.086975 | 0.018311 | 0.12817 | 120.9778 | -0.16022 | -0.12817 | 121.0831 | 120.9824 | 120.9824 | 0.004577 | 0.004577 | 120.9732 | -0.07782 | -0.082398 | 121.0602 | 121.1014 | 120.9915 | 0.12817 | 0.018311 | 0.10529 | -0.018311 | 0.086975 | 0.032043 | -0.050354 | 0.036621 | 120.9274 | 121.0098 | -0.10986 | -0.11444 | 120.9595 | 121.0052 | 120.9641 | 120.9595
2992.7031 | 121.0373 | -120.8176 | 0.1236 | -0.0016785 | 6.9827 | 0.015913 | 0.00041441 | 0.0027044 | -0.010386 | 0.00062377 | -0.00054933 | 0.0026596 | 0.013324 | 0.0072226 | -0.011967 | 0.028521 | -0.003292 | -0.036621 | -0.036621 | 0.018311 | -0.032043 | 0.059509 | 0.004578 | 0 | -0.036621 | 0.036621 | 0 | 0.027466 | 0.082397 | 0.009155 | 0.1236 | 120.8359 | -0.16022 | -0.15564 | 120.8771 | 120.8176 | 120.8221 | -0.018311 | -0.013733 | 120.8176 | -0.086975 | -0.09613 | 120.9 | 120.9412 | 120.8267 | 0.1236 | 0.009155 | 0.041198 | -0.050354 | 0.082397 | 0.027466 | -0.054932 | 0.036621 | 120.7809 | 120.8542 | -0.10528 | -0.1236 | 120.7855 | 120.845 | 120.7809 | 120.7809
2994.4375 | 121.1197 | -120.9366 | 0.12817 | -0.016937 | 6.9859 | 0.017195 | 0.0027642 | -0.0022088 | -0.0095319 | -0.0032214 | 0.0025025 | 0.003514 | 0.01311 | 0.007009 | -0.0066265 | 0.027453 | -0.00094199 | -0.041199 | -0.041199 | 0.018311 | -0.073242 | 0.032043 | -0.07782 | -0.059509 | -0.086975 | 0.036621 | -0.022888 | -0.013733 | 0.018311 | -0.050354 | 0.091553 | 120.9549 | -0.16937 | -0.20142 | 120.9686 | 120.8771 | 120.8588 | -0.07782 | -0.096131 | 120.9137 | -0.091553 | -0.14191 | 120.9549 | 121.0281 | 120.8862 | 0.11444 | -0.027466 | 0.013732 | -0.091553 | 0.041199 | 0.009155 | -0.05951 | 0.059509 | 120.8954 | 120.9732 | -0.10986 | -0.15106 | 120.8633 | 120.9229 | 120.8954 | 120.8496
2996.125 | 121.1563 | -121.0052 | 0.11444 | -0.016937 | 6.9846 | 0.015058 | 0.0021234 | -0.00028623 | -0.011882 | -0.0038622 | 0.0055543 | 0.0020188 | 0.012897 | 0.007009 | -0.01389 | 0.027239 | -0.00094199 | -0.064087 | -0.036621 | -0.004578 | -0.068665 | 0.041199 | -0.018311 | -0.018311 | -0.07782 | 0.022888 | -0.018311 | -0.036621 | 0.032043 | -0.032043 | 0.086975 | 121.0007 | -0.15106 | -0.18311 | 121.0464 | 120.9869 | 120.9869 | -0.013733 | -0.013733 | 120.9869 | -0.091553 | -0.15106 | 121.0373 | 121.0922 | 120.9732 | 0.10529 | -0.013732 | 0.045777 | -0.064087 | 0.050354 | -0.01831 | -0.032043 | 0.041199 | 120.9686 | 121.0281 | -0.11902 | -0.13275 | 120.9366 | 120.9686 | 120.9412 | 120.9274
2997.8906 | 121.2662 | -121.0144 | 0.10071 | -0.0016785 | 6.9833 | 0.017195 | 0.00062801 | -0.0013544 | -0.010386 | -0.001726 | -0.0036011 | 0.0013778 | 0.011828 | 0.0040182 | -0.0096173 | 0.030443 | -0.00072839 | -0.027466 | -0.068665 | 0.050354 | 0 | 0.11444 | 0.036621 | 0.036621 | 0.004578 | 0.004578 | 0.018311 | 0.032043 | 0.091553 | 0.041199 | 0.14648 | 121.0648 | -0.16937 | -0.10071 | 121.1288 | 121.051 | 121.051 | -0.013733 | -0.013733 | 121.0327 | -0.09613 | -0.068665 | 121.106 | 121.1609 | 121.0556 | 0.12817 | 0.022888 | 0.064087 | -0.050354 | 0.073242 | 0.013732 | -0.11902 | -0.013733 | 120.9457 | 121.019 | -0.050354 | -0.082397 | 121.0144 | 121.0464 | 120.9869 | 121.019
2999.6406 | 121.312 | -121.0419 | 0.10529 | -0.016937 | 6.9838 | 0.01634 | -1.2792e-05 | 0.0020636 | -0.0065411 | -0.00087163 | -0.00054933 | 0.002446 | 0.012683 | 0.009786 | -0.0094037 | 0.028521 | -0.0011558 | -0.013733 | -0.054932 | 0.041199 | -0.004578 | 0.11444 | 0.027466 | 0.032043 | 0 | 0.022888 | 0.013733 | 0.032043 | 0.10071 | 0.041199 | 0.13733 | 121.0831 | -0.16022 | -0.10986 | 121.1563 | 121.0739 | 121.0693 | -0.009156 | -0.013733 | 121.0556 | -0.082398 | -0.073243 | 121.1426 | 121.1792 | 121.0831 | 0.1236 | 0.027466 | 0.073242 | -0.045777 | 0.086975 | 0.01831 | -0.096131 | 0.009155 | 120.9869 | 121.0648 | -0.064087 | -0.091553 | 121.0373 | 121.0739 | 121.0281 | 121.0419
3001.3906 | 121.3165 | -121.1014 | 0.12817 | 0.005951 | 6.987 | 0.01634 | 0.0038324 | 0.0012092 | -0.010173 | -0.0015124 | -0.0036011 | 0.0028732 | 0.013537 | 0.0053 | -0.0094037 | 0.02788 | -0.0024374 | 0 | -0.045776 | 0.027466 | 0.004578 | 0.11444 | 0.009155 | 0.009155 | 0.022888 | 0.022888 | 0.009155 | 0.036621 | 0.10986 | 0.022888 | 0.1236 | 121.1288 | -0.17395 | -0.1236 | 121.2158 | 121.1105 | 121.1105 | -0.018311 | -0.018311 | 121.1105 | -0.10529 | -0.091553 | 121.2112 | 121.225 | 121.1243 | 0.11444 | 0.013733 | 0.086975 | -0.022888 | 0.10071 | 0.027466 | -0.073242 | 0.013733 | 121.0556 | 121.1243 | -0.10071 | -0.11902 | 121.106 | 121.138 | 121.1014 | 121.1243
3003.125 | 120.7809 | -120.4056 | 0.10071 | -0.009308 | 6.988 | 0.017408 | 0.0025506 | 0.0067634 | -0.0078229 | 0.00019657 | -0.0036011 | 0.0009506 | 0.011401 | 0.011281 | -0.0061993 | 0.030016 | -0.003292 | 0.018311 | -0.086975 | 0.027466 | 0.064087 | 0.16937 | 0.059509 | 0.045776 | 0.073242 | -0.022888 | 0.036621 | 0.1236 | 0.16022 | 0.09613 | 0.20142 | 120.433 | -0.18768 | -0.036621 | 120.575 | 120.4514 | 120.4651 | 0.01831 | 0.032043 | 120.4422 | -0.1236 | 0.022888 | 120.5658 | 120.607 | 120.5017 | 0.1648 | 0.059509 | 0.14191 | 0.036621 | 0.1236 | 0.086975 | -0.11444 | -0.059509 | 120.3186 | 120.3827 | -0.073242 | -0.064087 | 120.4697 | 120.5292 | 120.4239 | 120.4788
3004.8125 | 121.1838 | -120.8908 | 0.10071 | -0.009308 | 6.9912 | 0.015272 | 0.0044732 | 0.0012092 | -0.0093183 | -0.0025806 | -0.0036011 | 0.002446 | 0.014178 | 0.015127 | -0.0094037 | 0.029375 | -0.0011558 | -0.004578 | -0.068665 | 0.027466 | 0 | 0.10986 | 0.018311 | 0.032043 | -0.009155 | 0.013733 | 0.018311 | 0.041199 | 0.10071 | 0.054932 | 0.13733 | 120.9183 | -0.16937 | -0.10071 | 121.0007 | 120.9229 | 120.9091 | 0.004577 | -0.009155 | 120.9091 | -0.086975 | -0.059509 | 120.9915 | 121.0281 | 120.9457 | 0.11902 | 0.036621 | 0.082397 | -0.027466 | 0.082397 | 0.022888 | -0.096131 | -0.004578 | 120.8221 | 120.9045 | -0.073242 | -0.082397 | 120.8908 | 120.932 | 120.8862 | 120.8817
3006.5469 | 121.2616 | -120.9778 | 0.10071 | -0.0016785 | 6.9906 | 0.017195 | 0.0046868 | -0.00049983 | -0.0084637 | -0.0021532 | -0.00054933 | 0.0022324 | 0.01311 | 0.008077 | -0.0098309 | 0.029162 | -0.0024374 | -0.013733 | -0.054932 | 0.032043 | 0.004578 | 0.11444 | 0.018311 | 0.022888 | -0.004578 | 0.004578 | 0 | 0.036621 | 0.10986 | 0.064087 | 0.15106 | 121.0098 | -0.15564 | -0.09613 | 121.0922 | 121.0007 | 120.9961 | -0.009155 | -0.013732 | 120.9778 | -0.09613 | -0.064087 | 121.0876 | 121.1288 | 121.0419 | 0.15106 | 0.064087 | 0.082398 | -0.027465 | 0.10986 | 0.036621 | -0.086975 | 0.004578 | 120.9229 | 120.9824 | -0.068665 | -0.10071 | 120.9824 | 121.0144 | 120.9641 | 120.9732
3008.2969 | 117.6178 | -92.6102 | 24.7971 | 0.005951 | 10.5479 | -0.083849 | 1.5735 | 0.0022772 | 0.04067 | 0.046766 | -0.0036011 | 0.005864 | 0.015033 | 0.0031638 | -0.0089765 | 0.03023 | -8.7586e-05 | 12.5473 | 26.7975 | 5.9692 | 25.0351 | 9.668 | 11.7828 | 12.4558 | -0.11444 | 0 | -0.041199 | -0.082397 | -0.022888 | -0.068665 | 0.064087 | 98.5794 | 2.0004 | 0.23804 | 102.2781 | 105.0659 | 104.393 | 6.4865 | 5.8136 | 92.569 | -24.7971 | -24.8795 | 92.5873 | 92.6743 | 92.5415 | 0.10529 | -0.027466 | 3.6987 | 19.0659 | 0.018311 | -0.041198 | 20.8282 | 0.041199 | 119.4077 | 92.6102 | -18.8278 | -24.8383 | 117.6453 | 92.5278 | 105.1575 | 92.4957
3010.0469 | 121.1472 | -120.8038 | 0.10071 | -0.016937 | 6.984 | 0.01869 | 0.002337 | 0.0048408 | -0.0065411 | -0.0019396 | 0.0025025 | 0.0020188 | 0.012256 | 0.014059 | -0.0079083 | 0.030871 | -0.00094199 | 0.054932 | -0.073242 | 0.050354 | 0.082397 | 0.1831 | 0.054932 | 0.082397 | 0.086975 | -0.022888 | 0.045776 | 0.11444 | 0.16937 | 0.09613 | 0.17853 | 120.8542 | -0.17395 | -0.018311 | 120.9869 | 120.8862 | 120.8588 | 0.032043 | 0.004578 | 120.8496 | -0.1236 | 0.013733 | 120.9732 | 120.9824 | 120.9 | 0.13275 | 0.050354 | 0.13275 | 0.032043 | 0.1236 | 0.068665 | -0.1236 | -0.068664 | 120.7306 | 120.7809 | -0.050354 | -0.054932 | 120.8862 | 120.9183 | 120.8588 | 120.8908
3011.7969 | 121.2296 | -120.8862 | 0.086975 | -0.0016785 | 6.9812 | 0.016981 | 0.0027642 | 0.0037726 | -0.0069683 | -0.0012988 | 0.0055543 | 0.0013778 | 0.014178 | 0.009786 | -0.010258 | 0.029375 | -0.0041464 | 0.022888 | -0.064087 | 0.050354 | 0.073242 | 0.21515 | 0.11444 | 0.086975 | 0.091553 | -0.009155 | 0.036621 | 0.07782 | 0.17853 | 0.11444 | 0.17395 | 120.9366 | -0.15106 | -0.013733 | 121.1014 | 120.9732 | 121.0007 | 0.036621 | 0.064087 | 120.9229 | -0.09613 | -0.009155 | 121.0648 | 121.0602 | 121.0007 | 0.13733 | 0.07782 | 0.16479 | 0.022888 | 0.14191 | 0.041199 | -0.11444 | -0.045776 | 120.8221 | 120.8771 | -0.036621 | -0.050354 | 120.9595 | 120.9641 | 120.9091 | 120.9778
3013.5 | 121.2112 | -120.9778 | 0.10986 | -0.0016785 | 6.9878 | 0.016981 | 0.002337 | -0.00071343 | -0.0082501 | -0.0012988 | -0.0036011 | 0.0037278 | 0.01311 | 0.010641 | -0.0089765 | 0.029162 | -0.00436 | 0.009155 | -0.045776 | 0.032043 | 0.022888 | 0.11444 | 0.022888 | 0.013733 | 0.013733 | 0.027466 | 0 | 0.032043 | 0.073242 | 0.013733 | 0.1236 | 121.0098 | -0.15564 | -0.086975 | 121.0922 | 120.9915 | 121.0007 | -0.01831 | -0.009155 | 120.9778 | -0.082397 | -0.07782 | 121.051 | 121.1014 | 120.9915 | 0.1236 | 0.013733 | 0.082398 | -0.009155 | 0.073242 | 0.032043 | -0.077819 | 0.027466 | 120.932 | 121.0052 | -0.07782 | -0.10986 | 121.0007 | 121.0098 | 120.9869 | 120.9915
3015.25 | 121.3211 | -121.0281 | 0.07782 | -0.0016785 | 6.9808 | 0.013136 | 0.0021234 | 0.00056817 | -0.0067547 | -0.001726 | -0.0036011 | 0.0015914 | 0.013965 | 0.01299 | -0.0087629 | 0.028094 | -0.00094199 | -0.022888 | -0.073242 | 0.050354 | 0.032043 | 0.15564 | 0.073242 | 0.073242 | 0.054932 | 0.004578 | 0 | 0.073242 | 0.15106 | 0.11444 | 0.18768 | 121.0785 | -0.15106 | -0.045777 | 121.1838 | 121.1014 | 121.1014 | 0.022888 | 0.022888 | 121.0281 | -0.073242 | -0.004578 | 121.1792 | 121.2158 | 121.1426 | 0.18768 | 0.11444 | 0.10529 | -0.018311 | 0.15106 | 0.073242 | -0.1236 | 0.004578 | 120.9549 | 121.0327 | -0.027466 | -0.07782 | 121.0602 | 121.1014 | 121.0052 | 121.0831
3016.9219 | 121.2204 | -121.0739 | 0.11444 | -0.0016785 | 6.9863 | 0.016126 | 0.0036188 | 0.0020636 | -0.0073957 | -0.0021532 | 0.0025025 | 0.005864 | 0.01311 | 0.0082906 | -0.010045 | 0.028094 | -0.0037192 | -0.036621 | -0.045776 | 0.027466 | -0.045776 | 0.041199 | -0.059509 | -0.045776 | -0.09613 | 0.045776 | -0.013733 | -0.022888 | 0.004578 | -0.054932 | 0.068665 | 121.1014 | -0.16022 | -0.16022 | 121.1151 | 121.0281 | 121.0144 | -0.073242 | -0.086975 | 121.0602 | -0.068665 | -0.13733 | 121.0785 | 121.1426 | 121.019 | 0.082398 | -0.041199 | 0.013733 | -0.073242 | 0.018311 | -0.009155 | -0.073242 | 0.059509 | 121.0281 | 121.1197 | -0.086975 | -0.12817 | 121.0281 | 121.051 | 121.0373 | 120.9778
3018.6719 | 121.2845 | -121.106 | 0.1236 | -0.0016785 | 6.984 | 0.013349 | 0.0027642 | 0.0024908 | -0.0088911 | 0.0021192 | -0.00054933 | 0.004155 | 0.014392 | 0.011281 | -0.011967 | 0.027453 | -0.0056418 | -0.045776 | -0.013733 | 0.009155 | -0.054932 | 0.045776 | -0.022888 | -0.022888 | -0.091553 | 0.045776 | -0.018311 | -0.018311 | 0.045776 | -0.022888 | 0.10071 | 121.1151 | -0.13733 | -0.17853 | 121.1517 | 121.0831 | 121.0831 | -0.032043 | -0.032043 | 121.0876 | -0.07782 | -0.14191 | 121.1517 | 121.2067 | 121.0831 | 0.11902 | -0.004577 | 0.036621 | -0.064087 | 0.064087 | 0 | -0.022888 | 0.064087 | 121.0922 | 121.1517 | -0.11444 | -0.14191 | 121.051 | 121.0876 | 121.0602 | 121.0144
3020.4219 | 121.3257 | -121.1014 | 0.10071 | -0.0016785 | 6.9842 | 0.015913 | 0.0021234 | 0.0031318 | -0.0063275 | -0.0021532 | -0.0066527 | 0.0022324 | 0.012897 | 0.010641 | -0.0079083 | 0.029589 | 0.00033961 | -0.045776 | -0.054932 | 0 | -0.050354 | 0.050354 | -0.050354 | -0.041199 | -0.050354 | 0.009155 | -0.018311 | 0.032043 | 0.059509 | 0.004578 | 0.1236 | 121.1014 | -0.15564 | -0.15106 | 121.1517 | 121.0602 | 121.051 | -0.041199 | -0.050354 | 121.0831 | -0.091553 | -0.068665 | 121.1609 | 121.225 | 121.106 | 0.14191 | 0.022889 | 0.050354 | -0.050354 | 0.07782 | 0.050354 | -0.054932 | 0.027466 | 121.0464 | 121.1105 | -0.10071 | -0.11902 | 121.051 | 121.1334 | 121.0556 | 121.051
3022.1094 | 121.3028 | -121.1472 | 0.10986 | -0.0016785 | 6.9848 | 0.016981 | 0.0025506 | 0.00185 | -0.011027 | -0.0070666 | -0.0036011 | 0.0018052 | 0.014392 | 0.0027364 | -0.013676 | 0.027239 | -0.0011558 | -0.027466 | -0.07782 | 0.022888 | -0.018311 | 0.086975 | -0.004578 | -0.004578 | -0.064087 | 0.036621 | -0.004578 | -0.036621 | 0.041199 | -0.004578 | 0.086975 | 121.17 | -0.18768 | -0.12817 | 121.2341 | 121.1426 | 121.1426 | -0.027466 | -0.027466 | 121.1426 | -0.073242 | -0.14648 | 121.1884 | 121.2341 | 121.1426 | 0.091553 | 0 | 0.064087 | -0.041199 | 0.045777 | -0.032043 | -0.10071 | 0.041199 | 121.0693 | 121.1838 | -0.086975 | -0.11444 | 121.1288 | 121.1105 | 121.1197 | 121.0831
3023.8594 | 121.4355 | -121.1288 | 0.07782 | -0.009308 | 6.9827 | 0.015913 | 0.0025506 | -0.00092703 | -0.0097455 | -0.0042896 | 0.0025025 | 0.0015914 | 0.01311 | 0.008718 | -0.0066265 | 0.029589 | -0.00051479 | -0.022888 | -0.064087 | 0.027466 | 0.027466 | 0.13733 | 0.018311 | 0.036621 | 0.041199 | -0.004578 | 0.004578 | 0.10529 | 0.15564 | 0.07782 | 0.19226 | 121.1563 | -0.14191 | -0.050354 | 121.2662 | 121.1655 | 121.1472 | 0.009155 | -0.009155 | 121.1334 | -0.082398 | 0.027466 | 121.2845 | 121.3211 | 121.2067 | 0.18768 | 0.073242 | 0.10986 | 0 | 0.15106 | 0.10071 | -0.091553 | -0.009156 | 121.0648 | 121.1243 | -0.050354 | -0.073242 | 121.1563 | 121.2341 | 121.106 | 121.17
3025.5469 | 121.4172 | -121.1426 | 0.10986 | -0.009308 | 6.9846 | 0.015913 | 0.00041441 | -0.0011408 | -0.0082501 | -0.002367 | -0.00054933 | 0.002446 | 0.014178 | 0.011281 | -0.012822 | 0.028094 | -0.00671 | 0.022888 | -0.086975 | 0.054932 | 0.059509 | 0.18768 | 0.091553 | 0.07782 | 0.064087 | 0 | 0.009155 | 0.045776 | 0.13733 | 0.091553 | 0.14191 | 121.1975 | -0.19684 | -0.050354 | 121.3303 | 121.2204 | 121.2341 | 0.022888 | 0.036621 | 121.1517 | -0.10986 | -0.064087 | 121.2799 | 121.2845 | 121.2341 | 0.13275 | 0.082398 | 0.13275 | 0.004577 | 0.12817 | 0.036621 | -0.14191 | -0.009155 | 121.0556 | 121.1426 | -0.054931 | -0.10071 | 121.2021 | 121.1884 | 121.1655 | 121.2067
3027.2812 | 121.4813 | -121.1472 | 0.10986 | -0.009308 | 6.9838 | 0.01634 | 0.002337 | -0.004345 | -0.0091047 | -0.0040758 | -0.00054933 | 0.0011642 | 0.013537 | 0.013631 | -0.011113 | 0.028094 | 0.0016214 | -0.032043 | -0.068665 | 0.041199 | 0.022888 | 0.13733 | 0.064087 | 0.068665 | 0.036621 | 0.004578 | 0.004578 | 0.07782 | 0.16022 | 0.10986 | 0.1831 | 121.1884 | -0.17853 | -0.086975 | 121.2845 | 121.2158 | 121.2112 | 0.027466 | 0.022888 | 121.1517 | -0.10529 | -0.032043 | 121.3074 | 121.3303 | 121.257 | 0.17853 | 0.10529 | 0.09613 | -0.018311 | 0.15564 | 0.073242 | -0.10986 | 0 | 121.0785 | 121.1517 | -0.068664 | -0.10529 | 121.17 | 121.225 | 121.1151 | 121.1838
3029.0312 | 121.4676 | -121.1838 | 0.09613 | -0.009308 | 6.984 | 0.016126 | 0.0027642 | -0.00092703 | -0.0082501 | -0.0021532 | -0.0036011 | 0.0030868 | 0.012897 | 0.011068 | -0.0087629 | 0.030871 | -0.0054282 | -0.032043 | -0.064087 | 0.013733 | -0.022888 | 0.091553 | -0.027466 | -0.018311 | 0.009155 | 0.022888 | 0.004578 | 0.064087 | 0.10986 | 0.045776 | 0.16937 | 121.1975 | -0.16022 | -0.11902 | 121.2753 | 121.1655 | 121.1563 | -0.032044 | -0.041199 | 121.1884 | -0.073242 | -0.032043 | 121.2936 | 121.3531 | 121.2296 | 0.16479 | 0.041198 | 0.07782 | -0.036621 | 0.10529 | 0.059509 | -0.07782 | 0.01831 | 121.1197 | 121.2067 | -0.082397 | -0.091552 | 121.1609 | 121.2479 | 121.1517 | 121.1929
3030.7812 | 121.4172 | -121.2433 | 0.13733 | -0.0016785 | 6.984 | 0.014845 | 0.0031916 | 0.0059088 | -0.0091047 | -0.0040758 | 0.0025025 | 0.004155 | 0.012469 | 0.0038046 | -0.0098309 | 0.028094 | 0.00033961 | -0.027466 | -0.036621 | 0 | -0.045776 | 0.050354 | -0.004578 | -0.009155 | -0.064087 | 0.032043 | 0 | -0.013733 | 0.059509 | 0.004578 | 0.1236 | 121.2433 | -0.17395 | -0.18311 | 121.2936 | 121.2341 | 121.2387 | -0.009155 | -0.004578 | 121.2433 | -0.10529 | -0.15106 | 121.3028 | 121.3669 | 121.2479 | 0.1236 | 0.004578 | 0.050354 | -0.045776 | 0.059509 | -0.013733 | -0.036621 | 0.032043 | 121.2067 | 121.2753 | -0.13733 | -0.13733 | 121.1975 | 121.2296 | 121.2158 | 121.1792
3032.4688 | 121.5134 | -121.1975 | 0.10986 | -0.009308 | 6.985 | 0.014845 | 0.0014826 | 0.00078177 | -0.0082501 | -0.002367 | -0.0036011 | 0.0013778 | 0.014819 | 0.010213 | -0.012395 | 0.027453 | -0.0028646 | 0.004578 | -0.073242 | 0.045776 | 0.086975 | 0.21515 | 0.09613 | 0.091553 | 0.073242 | -0.018311 | 0.018311 | 0.07782 | 0.16937 | 0.12817 | 0.18768 | 121.2433 | -0.18311 | -0.022888 | 121.4127 | 121.2891 | 121.2936 | 0.045777 | 0.050354 | 121.2158 | -0.12817 | -0.032043 | 121.3669 | 121.3852 | 121.3257 | 0.16937 | 0.10986 | 0.16937 | 0.041199 | 0.15106 | 0.059509 | -0.11902 | -0.036622 | 121.1243 | 121.1792 | -0.064087 | -0.091552 | 121.2845 | 121.2753 | 121.2021 | 121.2708
3034.2188 | 121.4172 | -121.2662 | 0.10529 | -0.009308 | 6.9844 | 0.014631 | 0.001269 | -0.0039178 | -0.0095319 | 0.00083737 | -0.0036011 | 0.0050094 | 0.013324 | 0.008718 | -0.010045 | 0.027453 | -0.0028646 | -0.054932 | -0.041199 | -0.004578 | -0.059509 | 0.050354 | -0.032043 | -0.022888 | -0.086975 | 0.032043 | -0.022888 | -0.045776 | 0.036621 | -0.013733 | 0.091553 | 121.2616 | -0.14649 | -0.16479 | 121.3165 | 121.2433 | 121.2341 | -0.01831 | -0.027465 | 121.2433 | -0.073243 | -0.15106 | 121.3028 | 121.3577 | 121.2524 | 0.11444 | 0.009155 | 0.054932 | -0.054931 | 0.059509 | -0.022888 | -0.036621 | 0.054931 | 121.225 | 121.2982 | -0.10986 | -0.12817 | 121.2067 | 121.2204 | 121.2112 | 121.1792
3035.9688 | 121.4218 | -121.2662 | 0.10986 | -0.009308 | 6.988 | 0.017195 | 0.0042596 | 0.0076178 | -0.0086773 | -0.00087163 | -0.0036011 | 0.005864 | 0.013751 | 0.0082906 | -0.0085491 | 0.028734 | -0.0041464 | -0.045776 | -0.032043 | 0.018311 | -0.027466 | 0.064087 | -0.064087 | -0.041199 | -0.064087 | 0.032043 | -0.022888 | -0.022888 | 0.018311 | -0.054932 | 0.07782 | 121.2845 | -0.14191 | -0.13733 | 121.3303 | 121.225 | 121.2021 | -0.05951 | -0.082398 | 121.2433 | -0.07782 | -0.13275 | 121.2845 | 121.344 | 121.2112 | 0.10071 | -0.032044 | 0.045776 | -0.045777 | 0.041199 | 0 | -0.050354 | 0.054931 | 121.2341 | 121.2982 | -0.091552 | -0.13275 | 121.2387 | 121.2433 | 121.2204 | 121.2021
3037.7344 | 121.5683 | -121.2204 | 0.09613 | 0.005951 | 6.9859 | 0.015058 | 0.0031916 | 0.0033454 | -0.0078229 | -0.0015124 | -0.0036011 | 0.0013778 | 0.012683 | 0.015554 | -0.0061993 | 0.027453 | -0.0039328 | -0.027466 | -0.059509 | 0.032043 | 0.018311 | 0.13733 | 0.009155 | 0.050354 | 0.032043 | 0 | 0.022888 | 0.091553 | 0.14648 | 0.082397 | 0.20142 | 121.2524 | -0.15564 | -0.077819 | 121.3577 | 121.2708 | 121.2296 | 0.018311 | -0.022888 | 121.2433 | -0.09613 | -0.004577 | 121.3669 | 121.4218 | 121.3028 | 0.17853 | 0.059509 | 0.10529 | -0.013732 | 0.1236 | 0.068665 | -0.091552 | -0.022888 | 121.1609 | 121.2204 | -0.064087 | -0.073242 | 121.2387 | 121.312 | 121.1929 | 121.2524
3039.4219 | 121.5042 | -121.2799 | 0.11444 | -0.009308 | 6.9859 | 0.015486 | 0.001269 | 0.0022772 | -0.0095319 | -0.0040758 | -0.0036011 | 0.0030868 | 0.014178 | 0.010427 | -0.0087629 | 0.027453 | -0.0022238 | 0.004578 | -0.059509 | 0.013733 | 0.004578 | 0.12817 | 0.013733 | 0.022888 | 0.004578 | 0.027466 | 0 | 0.022888 | 0.082397 | 0.013733 | 0.13275 | 121.2936 | -0.17395 | -0.10986 | 121.4081 | 121.3028 | 121.2936 | 0.009155 | 0 | 121.2799 | -0.086975 | -0.091553 | 121.3623 | 121.4127 | 121.2936 | 0.13275 | 0.013733 | 0.11444 | -0.009155 | 0.082397 | 0.022888 | -0.073242 | 0.027466 | 121.2204 | 121.3074 | -0.10071 | -0.11444 | 121.2845 | 121.3028 | 121.2845 | 121.2845
3041.1562 | 121.2708 | -121.0876 | 0.11902 | -0.0016785 | 6.9827 | 0.015913 | 0.00084161 | 0.0056952 | -0.0084637 | -0.005144 | -0.0036011 | 0.003514 | 0.014605 | 0.0012412 | -0.010472 | 0.029162 | -0.0035056 | -0.054932 | -0.050354 | 0.022888 | -0.07782 | 0.018311 | -0.073242 | -0.054932 | -0.091553 | 0.032043 | -0.018311 | -0.022888 | 0.004578 | -0.050354 | 0.086975 | 121.1105 | -0.16937 | -0.19684 | 121.106 | 121.0327 | 121.0144 | -0.07782 | -0.09613 | 121.0693 | -0.086976 | -0.14191 | 121.0922 | 121.1746 | 121.0373 | 0.10529 | -0.032043 | -0.004577 | -0.10071 | 0.022889 | -0.004577 | -0.073242 | 0.050354 | 121.0373 | 121.1197 | -0.096131 | -0.13733 | 121.0098 | 121.0648 | 121.0327 | 120.9961
3042.9062 | 121.4127 | -121.1563 | 0.12817 | -0.0016785 | 6.9818 | 0.014845 | 0.0019098 | 0.0016364 | -0.0082501 | -0.0012988 | -0.00054933 | 0.0009506 | 0.012469 | 0.012136 | -0.0098309 | 0.028094 | -0.0037192 | -0.054932 | -0.027466 | 0.004578 | -0.064087 | 0.041199 | 0 | -0.013733 | -0.073242 | 0.050354 | -0.018311 | -0.004578 | 0.073242 | 0 | 0.11444 | 121.1609 | -0.15564 | -0.19226 | 121.1975 | 121.1426 | 121.1563 | -0.018311 | -0.004578 | 121.138 | -0.07782 | -0.13275 | 121.2296 | 121.2708 | 121.1563 | 0.13275 | 0.018311 | 0.036621 | -0.068665 | 0.091553 | 0.013733 | -0.032044 | 0.068665 | 121.1288 | 121.2067 | -0.1236 | -0.14649 | 121.0922 | 121.1517 | 121.1014 | 121.0831
3044.5938 | 121.4859 | -121.1884 | 0.10986 | -0.009308 | 6.9825 | 0.013563 | 0.00041441 | 0.0016364 | -0.0082501 | -1.7026e-05 | -0.0036011 | 0.0009506 | 0.011828 | 0.011281 | -0.010686 | 0.027025 | 0.001835 | 0.004578 | -0.07782 | 0.032043 | 0.064087 | 0.21057 | 0.086975 | 0.091553 | 0.059509 | 0.004578 | 0.018311 | 0.068665 | 0.16479 | 0.10529 | 0.17395 | 121.2204 | -0.18768 | -0.045776 | 121.3989 | 121.2799 | 121.2753 | 0.05951 | 0.054932 | 121.2067 | -0.10529 | -0.041198 | 121.3531 | 121.3623 | 121.2936 | 0.15564 | 0.086975 | 0.17853 | 0.032044 | 0.14648 | 0.050354 | -0.10986 | -0.013733 | 121.1105 | 121.1929 | -0.07782 | -0.091552 | 121.2524 | 121.257 | 121.1929 | 121.2479
3046.3438 | 121.4172 | -121.257 | 0.13733 | -0.009308 | 6.9827 | 0.01399 | 0.0031916 | 0.0020636 | -0.0095319 | -0.005144 | -0.00054933 | 0.0026596 | 0.014392 | 0.012563 | -0.012181 | 0.026385 | -0.0056418 | -0.054932 | -0.032043 | 0.018311 | -0.054932 | 0.073242 | -0.009155 | -0.018311 | -0.07782 | 0.032043 | -0.009155 | -0.022888 | 0.032043 | -0.018311 | 0.091553 | 121.2753 | -0.16937 | -0.19226 | 121.3303 | 121.2387 | 121.2479 | -0.036622 | -0.027466 | 121.2479 | -0.10529 | -0.16022 | 121.2891 | 121.3486 | 121.2387 | 0.10071 | -0.009156 | 0.054931 | -0.073243 | 0.041198 | -0.013733 | -0.050354 | 0.041198 | 121.225 | 121.2891 | -0.11902 | -0.14648 | 121.2021 | 121.2341 | 121.2021 | 121.1792
3048.0938 | 121.4493 | -121.2524 | 0.10529 | -0.0016785 | 6.9855 | 0.014631 | 0.0031916 | 0.0029182 | -0.0093183 | -0.00044443 | -0.0036011 | 0.0037278 | 0.012897 | 0.010213 | -0.0068403 | 0.025957 | -0.0047874 | -0.009155 | -0.036621 | 0.036621 | -0.022888 | 0.086975 | -0.022888 | -0.022888 | -0.022888 | 0.032043 | 0 | -0.009155 | 0.041199 | -0.036621 | 0.082397 | 121.2891 | -0.14191 | -0.12817 | 121.3394 | 121.2296 | 121.2296 | -0.059509 | -0.059509 | 121.2524 | -0.073243 | -0.11444 | 121.2936 | 121.3348 | 121.2158 | 0.082397 | -0.036621 | 0.050354 | -0.059509 | 0.041199 | -0.009155 | -0.073242 | 0.032043 | 121.2158 | 121.2845 | -0.068665 | -0.10529 | 121.2296 | 121.2433 | 121.2433 | 121.2296
3049.8438 | 121.5591 | -121.2524 | 0.10529 | 0.005951 | 6.9829 | 0.016981 | 0.00020081 | 0.0067634 | -0.0076093 | -0.0030078 | 0.0025025 | 0.0003098 | 0.012469 | 0.010213 | -0.0083355 | 0.030016 | -0.00094199 | 0.013733 | -0.059509 | 0.050354 | 0.041199 | 0.19684 | 0.064087 | 0.064087 | 0.07782 | 0.018311 | 0.018311 | 0.082397 | 0.13733 | 0.082397 | 0.16479 | 121.3028 | -0.16479 | -0.064087 | 121.4493 | 121.3165 | 121.3165 | 0.013733 | 0.013733 | 121.2708 | -0.086975 | -0.022889 | 121.3898 | 121.4172 | 121.3348 | 0.14648 | 0.064086 | 0.14648 | -0.009155 | 0.11902 | 0.064086 | -0.10986 | 0 | 121.1929 | 121.2708 | -0.054932 | -0.086975 | 121.2936 | 121.3348 | 121.2662 | 121.3303
3051.5156 | 121.5088 | -121.2799 | 0.12817 | -0.016937 | 6.9814 | 0.015486 | 0.0010552 | 0.0048408 | -0.0056867 | -0.0012988 | -0.00054933 | 0.0009506 | 0.014605 | 0.010213 | -0.011113 | 0.028521 | -0.005001 | 0.027466 | -0.07782 | 0.054932 | 0.036621 | 0.15106 | 0.064087 | 0.054932 | 0.009155 | 0.018311 | 0.004578 | 0.004578 | 0.091553 | 0.027466 | 0.11444 | 121.3348 | -0.20599 | -0.091553 | 121.431 | 121.3348 | 121.344 | 0 | 0.009155 | 121.2845 | -0.10986 | -0.1236 | 121.3715 | 121.3943 | 121.3074 | 0.10986 | 0.022888 | 0.09613 | -0.018311 | 0.086975 | 0 | -0.13275 | 0.013733 | 121.2021 | 121.2982 | -0.073242 | -0.1236 | 121.3165 | 121.2845 | 121.3074 | 121.2891
3053.2656 | 121.4813 | -121.3348 | 0.10986 | 0.005951 | 6.9833 | 0.018263 | 0.00084161 | 0.0022772 | -0.0073957 | -0.0019396 | -0.0036011 | 0.0047958 | 0.014178 | 0.011709 | -0.0098309 | 0.028307 | -0.0054282 | -0.050354 | -0.036621 | 0.027466 | -0.073242 | 0.004578 | -0.082397 | -0.064087 | -0.082397 | 0.027466 | -0.018311 | -0.018311 | 0.004578 | -0.064087 | 0.086975 | 121.3623 | -0.14648 | -0.18311 | 121.3394 | 121.2708 | 121.2524 | -0.091553 | -0.10986 | 121.3165 | -0.082397 | -0.12817 | 121.3394 | 121.4218 | 121.2708 | 0.10529 | -0.045776 | -0.022888 | -0.10071 | 0.022889 | 0 | -0.064087 | 0.045777 | 121.2982 | 121.3623 | -0.082397 | -0.12817 | 121.2616 | 121.3165 | 121.2845 | 121.2524
3054.9688 | 121.6232 | -121.2753 | 0.082397 | -0.016937 | 6.9816 | 0.016554 | 0.0034052 | 0.005268 | -0.0086773 | -0.0059984 | -0.0066527 | 0.0020188 | 0.013537 | 0.0057272 | -0.0047039 | 0.031298 | -0.003292 | 0.004578 | -0.068665 | 0.036621 | 0.032043 | 0.15564 | 0.022888 | 0.050354 | 0.059509 | -0.009155 | 0.027466 | 0.10529 | 0.14648 | 0.07782 | 0.19226 | 121.312 | -0.15106 | -0.050354 | 121.431 | 121.3257 | 121.2982 | 0.013733 | -0.013733 | 121.3028 | -0.091552 | 0.022889 | 121.4218 | 121.4676 | 121.3531 | 0.16479 | 0.050354 | 0.11902 | -0.004578 | 0.11902 | 0.07782 | -0.10529 | -0.036621 | 121.2067 | 121.2662 | -0.045776 | -0.054931 | 121.3074 | 121.3806 | 121.2799 | 121.3348
3056.7188 | 121.6232 | -121.3348 | 0.10529 | -0.009308 | 6.9838 | 0.014845 | -1.2792e-05 | 0.0033454 | -0.0097455 | -0.0015124 | -0.00054933 | 0.0003098 | 0.011615 | -0.0053812 | -0.012395 | 0.031511 | -0.0052146 | 0.027466 | -0.091553 | 0.045776 | 0.068665 | 0.20599 | 0.086975 | 0.082397 | 0.064087 | 0.013733 | 0.013733 | 0.07782 | 0.16022 | 0.11444 | 0.16022 | 121.3806 | -0.19684 | -0.036621 | 121.5408 | 121.4172 | 121.4218 | 0.036621 | 0.041199 | 121.3486 | -0.091553 | -0.027466 | 121.4951 | 121.4951 | 121.4493 | 0.14648 | 0.10071 | 0.16022 | 0.022889 | 0.14648 | 0.064087 | -0.13733 | 0 | 121.2433 | 121.3486 | -0.05951 | -0.091553 | 121.4035 | 121.4127 | 121.3623 | 121.3989
3058.4688 | 121.6599 | -121.3165 | 0.10986 | -0.009308 | 6.9833 | 0.015272 | 0.0014826 | 0.0029182 | -0.0061139 | -0.002367 | -0.0097045 | 0.0011642 | 0.013751 | 0.015554 | -0.0094037 | 0.026171 | -0.0013694 | -0.018311 | -0.082397 | 0.045776 | 0.027466 | 0.15106 | 0.050354 | 0.041199 | 0.032043 | 0.009155 | 0.013733 | 0.068665 | 0.14191 | 0.10071 | 0.17395 | 121.3623 | -0.19226 | -0.082397 | 121.4676 | 121.3577 | 121.3669 | -0.004577 | 0.004578 | 121.3303 | -0.10071 | -0.041198 | 121.4584 | 121.4905 | 121.4172 | 0.16022 | 0.086975 | 0.10529 | -0.01831 | 0.12817 | 0.054932 | -0.12817 | -0.004578 | 121.2341 | 121.3257 | -0.064087 | -0.09613 | 121.344 | 121.3852 | 121.2982 | 121.3486
3060.1406 | 121.5317 | -121.376 | 0.12817 | -0.016937 | 6.9833 | 0.015699 | 0.001269 | 0.00185 | -0.0095319 | -0.0027942 | 0.0025025 | 0.003514 | 0.011828 | 0.0029502 | -0.0094037 | 0.030657 | -0.0041464 | -0.050354 | -0.032043 | -0.004578 | -0.07782 | 0.013733 | -0.07782 | -0.073242 | -0.11444 | 0.022888 | -0.009155 | -0.009155 | -0.013733 | -0.050354 | 0.086975 | 121.3715 | -0.16022 | -0.20599 | 121.3898 | 121.3028 | 121.2982 | -0.068664 | -0.073242 | 121.3669 | -0.10529 | -0.13733 | 121.3623 | 121.463 | 121.3257 | 0.09613 | -0.041199 | 0.018311 | -0.073242 | -0.004578 | 0 | -0.027465 | 0.032043 | 121.344 | 121.3989 | -0.13275 | -0.13733 | 121.2982 | 121.3669 | 121.3257 | 121.2616
3061.8906 | 121.6187 | -121.3623 | 0.11902 | -0.0016785 | 6.9842 | 0.015486 | 0.00062801 | 0.0012092 | -0.0091047 | -0.001726 | -0.00054933 | 0.0013778 | 0.014605 | 0.0067954 | -0.0096173 | 0.026812 | -0.006069 | 0.018311 | -0.086975 | 0.041199 | 0.054932 | 0.17853 | 0.082397 | 0.07782 | 0.036621 | 0.009155 | 0.004578 | 0.027466 | 0.11902 | 0.050354 | 0.13733 | 121.4035 | -0.20599 | -0.064087 | 121.5408 | 121.4401 | 121.4447 | 0.036621 | 0.041198 | 121.3669 | -0.10986 | -0.091553 | 121.4813 | 121.4996 | 121.4127 | 0.13275 | 0.045776 | 0.13733 | 0.013733 | 0.11444 | 0.022888 | -0.12817 | 0.004577 | 121.2753 | 121.3715 | -0.07782 | -0.11444 | 121.4172 | 121.3898 | 121.3806 | 121.3989
3063.625 | 121.5317 | -121.3852 | 0.11902 | -0.009308 | 6.9855 | 0.015272 | 0.0044732 | 0.00099557 | -0.0071821 | -0.0036486 | -0.00054933 | 0.0043686 | 0.013751 | 0.0029502 | -0.0070539 | 0.026385 | 0.00012601 | -0.032043 | -0.045776 | 0.027466 | -0.041199 | 0.059509 | -0.050354 | -0.050354 | -0.09613 | 0.045776 | -0.022888 | -0.022888 | 0.018311 | -0.059509 | 0.086975 | 121.4127 | -0.16479 | -0.16022 | 121.4447 | 121.3348 | 121.3348 | -0.07782 | -0.07782 | 121.3623 | -0.073243 | -0.14191 | 121.4035 | 121.4722 | 121.3257 | 0.10986 | -0.036621 | 0.032043 | -0.068665 | 0.041199 | 0 | -0.073242 | 0.068664 | 121.3394 | 121.431 | -0.091553 | -0.14191 | 121.344 | 121.3623 | 121.3531 | 121.2891
3065.375 | 121.669 | -121.376 | 0.086975 | 0.005951 | 6.9825 | 0.01634 | 0.0010552 | -0.001568 | -0.010173 | -0.0027942 | -0.0036011 | 0.0013778 | 0.013965 | 0.0074362 | -0.0089765 | 0.030016 | -0.002651 | -0.036621 | -0.064087 | 0.041199 | 0.004578 | 0.11902 | 0.036621 | 0.041199 | -0.004578 | -0.004578 | 0.009155 | 0.050354 | 0.11902 | 0.082397 | 0.15564 | 121.4172 | -0.15106 | -0.082397 | 121.4951 | 121.4172 | 121.4127 | 0 | -0.004578 | 121.3852 | -0.091553 | -0.036621 | 121.4951 | 121.5317 | 121.4584 | 0.14649 | 0.073242 | 0.07782 | -0.036621 | 0.10986 | 0.041199 | -0.10529 | -0.013733 | 121.312 | 121.3715 | -0.045776 | -0.07782 | 121.3806 | 121.4264 | 121.3394 | 121.3715
3067.0625 | 121.5729 | -121.431 | 0.12817 | -0.016937 | 6.9829 | 0.015699 | 0.0010552 | -0.0019952 | -0.0088911 | -1.7026e-05 | -0.0036011 | 0.0030868 | 0.014819 | 0.0078634 | -0.012395 | 0.026385 | 0.00012601 | -0.013733 | -0.059509 | 0.022888 | -0.018311 | 0.10986 | 0.009155 | 0.009155 | -0.045776 | 0.041199 | -0.009155 | -0.045776 | 0.059509 | -0.004578 | 0.068665 | 121.4539 | -0.18768 | -0.14649 | 121.5408 | 121.4401 | 121.4401 | -0.013733 | -0.013733 | 121.4218 | -0.086975 | -0.17395 | 121.4905 | 121.4996 | 121.4264 | 0.07782 | 0.004577 | 0.086975 | -0.041199 | 0.068664 | -0.036621 | -0.082397 | 0.050354 | 121.3715 | 121.4722 | -0.10529 | -0.13733 | 121.4127 | 121.3852 | 121.4172 | 121.3852
3068.8281 | 121.7148 | -121.3852 | 0.082397 | -0.009308 | 6.9823 | 0.014845 | 0.0025506 | 0.00035457 | -0.0069683 | -0.0036486 | -0.00054933 | 0.0030868 | 0.014178 | 0.0099996 | -0.0079083 | 0.028521 | -0.006069 | 0.027466 | -0.064087 | 0.064087 | 0.073242 | 0.19684 | 0.059509 | 0.050354 | 0.10986 | 0 | 0.032043 | 0.10071 | 0.17853 | 0.10071 | 0.18768 | 121.4493 | -0.14648 | -0.009155 | 121.582 | 121.4355 | 121.4447 | -0.013733 | -0.004578 | 121.4172 | -0.082397 | 0.018311 | 121.5637 | 121.5729 | 121.4859 | 0.15564 | 0.068665 | 0.13275 | 0.009155 | 0.14648 | 0.068665 | -0.12817 | -0.032043 | 121.3211 | 121.3852 | -0.01831 | -0.050354 | 121.4584 | 121.4859 | 121.4127 | 121.4951
3070.5156 | 121.6324 | -121.4447 | 0.13275 | 0.005951 | 6.985 | 0.014417 | 0.0016962 | 0.00035457 | -0.0080365 | -0.0038622 | -0.0036011 | 0.0037278 | 0.014605 | 0.010213 | -0.010899 | 0.026598 | -0.0020102 | -0.045776 | -0.032043 | 0.013733 | -0.054932 | 0.045776 | -0.004578 | -0.013733 | -0.082397 | 0.041199 | -0.022888 | -0.018311 | 0.054932 | -0.018311 | 0.10529 | 121.4584 | -0.16479 | -0.18768 | 121.4905 | 121.431 | 121.4401 | -0.027466 | -0.018311 | 121.4218 | -0.091552 | -0.15106 | 121.4996 | 121.55 | 121.4264 | 0.12817 | 0.004577 | 0.032043 | -0.068665 | 0.07782 | 0.004577 | -0.045776 | 0.064087 | 121.4127 | 121.4859 | -0.11902 | -0.15564 | 121.3898 | 121.4264 | 121.3989 | 121.3623
3072.2656 | 121.6599 | -121.431 | 0.12817 | -0.016937 | 6.9861 | 0.015913 | 0.0034052 | 0.00185 | -0.011241 | -0.0021532 | -0.0036011 | 0.0033004 | 0.014819 | 0.011068 | -0.010258 | 0.027239 | -0.0047874 | -0.018311 | -0.027466 | 0.032043 | -0.036621 | 0.073242 | -0.022888 | -0.009155 | -0.059509 | 0.045776 | -0.004578 | 0.013733 | 0.07782 | 0.013733 | 0.1236 | 121.463 | -0.15564 | -0.1648 | 121.5042 | 121.4218 | 121.4081 | -0.041198 | -0.054931 | 121.4264 | -0.082398 | -0.11444 | 121.5088 | 121.5546 | 121.4447 | 0.12817 | 0.018311 | 0.041199 | -0.068664 | 0.082398 | 0.018311 | -0.059509 | 0.050354 | 121.4035 | 121.4767 | -0.096131 | -0.13275 | 121.3943 | 121.4447 | 121.4127 | 121.3715
3073.9688 | 121.6049 | -121.463 | 0.13275 | -0.009308 | 6.9816 | 0.014631 | 0.00084161 | 0.00035457 | -0.0084637 | -0.0045032 | -0.00054933 | 0.004155 | 0.016314 | 0.008077 | -0.013249 | 0.025957 | -0.0028646 | -0.059509 | -0.036621 | 0 | -0.059509 | 0.050354 | -0.018311 | -0.018311 | -0.10071 | 0.032043 | -0.009155 | -0.036621 | 0.041199 | -0.013733 | 0.068665 | 121.463 | -0.16937 | -0.19226 | 121.5134 | 121.4447 | 121.4447 | -0.018311 | -0.018311 | 121.4539 | -0.10071 | -0.16937 | 121.5042 | 121.5317 | 121.4493 | 0.07782 | -0.004578 | 0.050354 | -0.059509 | 0.050354 | -0.027466 | -0.036621 | 0.041198 | 121.4264 | 121.4951 | -0.13275 | -0.14191 | 121.4035 | 121.4264 | 121.4035 | 121.3623
3075.7188 | 121.637 | -121.4722 | 0.11902 | -0.0016785 | 6.9842 | 0.012068 | 0.001269 | -0.003277 | -0.0097455 | -0.0021532 | -0.00054933 | 0.0028732 | 0.012042 | 0.0078634 | -0.010258 | 0.025744 | -0.0045736 | -0.054932 | -0.027466 | 0.018311 | -0.064087 | 0.050354 | -0.013733 | -0.027466 | -0.073242 | 0.032043 | -0.013733 | -0.032043 | 0.054932 | -0.027466 | 0.064087 | 121.4905 | -0.14649 | -0.18311 | 121.5225 | 121.4447 | 121.4584 | -0.045777 | -0.032044 | 121.4584 | -0.086976 | -0.15106 | 121.5271 | 121.5363 | 121.4447 | 0.07782 | -0.013733 | 0.032043 | -0.082398 | 0.068665 | -0.01831 | -0.045777 | 0.045776 | 121.4447 | 121.5042 | -0.10071 | -0.13275 | 121.4081 | 121.4401 | 121.4172 | 121.3989
3077.4688 | 121.7651 | -121.4172 | 0.10071 | -0.0016785 | 6.9833 | 0.016981 | 0.0029778 | 0.003559 | -0.0091047 | -0.00087163 | 0.0055543 | 0.0013778 | 0.011188 | 0.011281 | -0.0066265 | 0.029589 | -0.0054282 | 0.050354 | -0.082397 | 0.059509 | 0.068665 | 0.19226 | 0.064087 | 0.059509 | 0.09613 | 0 | 0.027466 | 0.10071 | 0.16937 | 0.09613 | 0.20599 | 121.4767 | -0.18311 | -0.032043 | 121.6095 | 121.4767 | 121.4813 | 0 | 0.004578 | 121.4447 | -0.10071 | 0 | 121.5866 | 121.6232 | 121.5134 | 0.17853 | 0.068664 | 0.13275 | 0.009156 | 0.14191 | 0.073242 | -0.14191 | -0.027466 | 121.3348 | 121.4172 | -0.041199 | -0.073242 | 121.4859 | 121.5179 | 121.4676 | 121.5134
3079.1562 | 121.7102 | -121.4767 | 0.11444 | -0.0016785 | 6.9863 | 0.015913 | 0.0034052 | -0.0017816 | -0.0065411 | -0.0025806 | -0.00054933 | 0.0037278 | 0.011615 | 0.011068 | -0.0089765 | 0.028734 | -0.0041464 | -0.009155 | -0.032043 | 0.009155 | -0.013733 | 0.091553 | 0.022888 | -0.004578 | -0.032043 | 0.027466 | -0.009155 | 0.027466 | 0.091553 | 0.018311 | 0.13733 | 121.4859 | -0.14648 | -0.12817 | 121.5683 | 121.4722 | 121.4996 | -0.013733 | 0.013733 | 121.4676 | -0.086975 | -0.086975 | 121.5683 | 121.6141 | 121.4951 | 0.14648 | 0.027466 | 0.082398 | -0.022888 | 0.10071 | 0.036621 | -0.041198 | 0.036621 | 121.4447 | 121.5042 | -0.10529 | -0.1236 | 121.463 | 121.5042 | 121.4676 | 121.4447
3080.9062 | 121.6553 | -121.5042 | 0.11902 | -0.016937 | 6.9836 | 0.016981 | 0.004046 | 0.0022772 | -0.0082501 | -0.0010852 | -0.00054933 | 0.0030868 | 0.012683 | 0.012777 | -0.010472 | 0.028094 | -0.0020102 | -0.022888 | -0.059509 | 0.027466 | -0.041199 | 0.064087 | -0.041199 | -0.036621 | -0.059509 | 0.027466 | -0.022888 | -0.004578 | 0.036621 | -0.045776 | 0.07782 | 121.5317 | -0.17853 | -0.16022 | 121.5683 | 121.4676 | 121.463 | -0.064087 | -0.068665 | 121.4813 | -0.091553 | -0.1236 | 121.5408 | 121.582 | 121.4584 | 0.10071 | -0.022888 | 0.036621 | -0.068665 | 0.059509 | 0.01831 | -0.086975 | 0.050354 | 121.4447 | 121.5317 | -0.091553 | -0.14191 | 121.463 | 121.4996 | 121.4813 | 121.4447
3082.5938 | 121.6873 | -121.4996 | 0.13733 | -0.009308 | 6.9848 | 0.014204 | 0.0010552 | -0.0013544 | -0.0067547 | -0.0049304 | -0.0036011 | 0.0015914 | 0.011615 | 0.006368 | -0.014317 | 0.027666 | -0.0064962 | -0.018311 | -0.059509 | 0.013733 | -0.022888 | 0.091553 | 0.004578 | 0.009155 | -0.054932 | 0.018311 | -0.009155 | -0.027466 | 0.059509 | -0.009155 | 0.073242 | 121.5134 | -0.19684 | -0.16022 | 121.5912 | 121.5088 | 121.5042 | -0.004578 | -0.009155 | 121.4905 | -0.11902 | -0.16479 | 121.5591 | 121.5729 | 121.4905 | 0.082397 | 0 | 0.07782 | -0.036621 | 0.068664 | -0.018311 | -0.073242 | 0.027466 | 121.4401 | 121.5179 | -0.1236 | -0.14648 | 121.4767 | 121.4722 | 121.4813 | 121.4447
3084.3438 | 121.7972 | -121.4767 | 0.082397 | -0.0016785 | 6.9831 | 0.016126 | 0.00084161 | 0.00078177 | -0.0078229 | -0.0040758 | -0.00054933 | 0.0009506 | 0.010119 | 0.014486 | -0.0087629 | 0.028521 | -0.00436 | 0.027466 | -0.091553 | 0.064087 | 0.068665 | 0.21515 | 0.10986 | 0.10071 | 0.086975 | 0.009155 | 0.022888 | 0.091553 | 0.16937 | 0.13275 | 0.17853 | 121.5408 | -0.17395 | -0.013732 | 121.6919 | 121.5775 | 121.5866 | 0.036621 | 0.045776 | 121.4996 | -0.073242 | 0.009156 | 121.6461 | 121.6553 | 121.6095 | 0.15564 | 0.10986 | 0.15106 | 0.004578 | 0.14649 | 0.068665 | -0.15564 | -0.013733 | 121.3852 | 121.4859 | -0.01831 | -0.059509 | 121.5454 | 121.5683 | 121.5042 | 121.5637
3086.0156 | 121.669 | -121.5042 | 0.12817 | -0.009308 | 6.984 | 0.016554 | 0.0029778 | 0.0065498 | -0.0097455 | -0.0019396 | -0.0066527 | 0.0026596 | 0.013537 | -0.0013224 | -0.0068403 | 0.028734 | -0.0045736 | -0.013733 | -0.045776 | 0.022888 | -0.036621 | 0.059509 | -0.050354 | -0.032043 | -0.064087 | 0.054932 | -0.009155 | -0.018311 | 0.032043 | -0.032043 | 0.082397 | 121.5271 | -0.17395 | -0.1648 | 121.5637 | 121.4722 | 121.4539 | -0.054931 | -0.073242 | 121.4951 | -0.073242 | -0.14649 | 121.5363 | 121.5866 | 121.4722 | 0.091552 | -0.022888 | 0.036621 | -0.059509 | 0.041198 | -0.009156 | -0.068664 | 0.064087 | 121.4584 | 121.5591 | -0.10529 | -0.13733 | 121.4676 | 121.4859 | 121.4905 | 121.4401
3087.7812 | 121.7789 | -121.4905 | 0.09613 | -0.0016785 | 6.9838 | 0.015272 | 0.0019098 | 0.00078177 | -0.0097455 | -0.0021532 | -0.0036011 | 0.0039414 | 0.013537 | 0.0053 | -0.0055585 | 0.029589 | -0.003292 | -0.045776 | -0.036621 | 0.022888 | -0.022888 | 0.068665 | -0.041199 | -0.022888 | -0.022888 | 0.027466 | -0.009155 | 0.050354 | 0.10986 | 0.022888 | 0.13733 | 121.5134 | -0.13275 | -0.11902 | 121.5591 | 121.4676 | 121.4493 | -0.045776 | -0.064087 | 121.4813 | -0.068664 | -0.045776 | 121.6003 | 121.6278 | 121.5134 | 0.14648 | 0.032043 | 0.045777 | -0.045776 | 0.11902 | 0.059509 | -0.059509 | 0.036621 | 121.4539 | 121.5179 | -0.073242 | -0.10528 | 121.4676 | 121.5408 | 121.4447 | 121.4676
3089.5312 | 121.701 | -121.5363 | 0.1236 | -0.016937 | 6.9848 | 0.016767 | 0.0034052 | 0.0024908 | -0.0076093 | -0.0045032 | -0.0036011 | 0.004155 | 0.010974 | 0.010641 | -0.0074811 | 0.027453 | -0.0028646 | -0.041199 | -0.032043 | 0.013733 | -0.086975 | 0.004578 | -0.068665 | -0.050354 | -0.091553 | 0.032043 | -0.022888 | -0.022888 | 0.013733 | -0.041199 | 0.07782 | 121.55 | -0.15564 | -0.21057 | 121.5408 | 121.4859 | 121.4676 | -0.064087 | -0.082398 | 121.5134 | -0.091553 | -0.14648 | 121.55 | 121.6141 | 121.4951 | 0.10071 | -0.018311 | -0.009155 | -0.10071 | 0.036621 | 0 | -0.045776 | 0.054931 | 121.5042 | 121.5683 | -0.10986 | -0.14648 | 121.4493 | 121.5134 | 121.4951 | 121.4447
3091.2031 | 121.7926 | -121.5317 | 0.10529 | -0.0016785 | 6.9848 | 0.016126 | 0.00062801 | -0.001568 | -0.0056867 | -0.0019396 | -0.00054933 | 0.0003098 | 0.016528 | 0.007009 | -0.0083355 | 0.028307 | -0.0017966 | -0.004578 | -0.073242 | 0.050354 | 0.013733 | 0.17853 | 0.032043 | 0.050354 | 0.027466 | 0.004578 | 0.013733 | 0.036621 | 0.10986 | 0.059509 | 0.16022 | 121.582 | -0.17853 | -0.091553 | 121.7102 | 121.582 | 121.5637 | 0 | -0.018311 | 121.5454 | -0.10071 | -0.068665 | 121.6415 | 121.6919 | 121.5912 | 0.14648 | 0.045776 | 0.12817 | -0.036621 | 0.09613 | 0.022888 | -0.1236 | -0.009155 | 121.4584 | 121.5363 | -0.054932 | -0.091553 | 121.5454 | 121.5683 | 121.5271 | 121.5591
3092.9531 | 121.7789 | -121.5591 | 0.11444 | 0.005951 | 6.9836 | 0.015699 | 0.0038324 | 0.0031318 | -0.0088911 | -0.00065803 | -0.0066527 | 0.003514 | 0.016314 | 0.0067954 | -0.0076947 | 0.029589 | -0.0028646 | -0.050354 | -0.036621 | 0.018311 | -0.050354 | 0.041199 | -0.064087 | -0.022888 | -0.041199 | 0.036621 | 0.004578 | 0.032043 | 0.059509 | -0.004578 | 0.13733 | 121.5775 | -0.15106 | -0.16479 | 121.6003 | 121.5363 | 121.4951 | -0.041199 | -0.082398 | 121.5637 | -0.07782 | -0.082398 | 121.6187 | 121.6965 | 121.5546 | 0.13275 | -0.009156 | 0.022888 | -0.068665 | 0.054931 | 0.027465 | -0.054932 | 0.032043 | 121.5225 | 121.5958 | -0.09613 | -0.10986 | 121.5088 | 121.5912 | 121.5088 | 121.5179
3094.6406 | 121.8613 | -121.5134 | 0.10986 | -0.009308 | 6.9831 | 0.016981 | -0.00065359 | 0.0012092 | -0.0067547 | -0.0036486 | -0.0036011 | 0.0030868 | 0.012683 | 0.011709 | -0.0072675 | 0.030871 | -0.0011558 | -0.004578 | -0.064087 | 0.032043 | 0.041199 | 0.16022 | 0.036621 | 0.064087 | 0.068665 | 0 | 0 | 0.11902 | 0.16022 | 0.09613 | 0.19684 | 121.5454 | -0.17395 | -0.068664 | 121.6736 | 121.5775 | 121.55 | 0.032044 | 0.004578 | 121.5134 | -0.10986 | 0.009156 | 121.6736 | 121.7102 | 121.6095 | 0.19684 | 0.09613 | 0.12817 | 0.009156 | 0.16022 | 0.11902 | -0.09613 | 0 | 121.4493 | 121.5134 | -0.07782 | -0.10986 | 121.5546 | 121.6324 | 121.5088 | 121.582
3096.375 | 121.7422 | -121.5546 | 0.12817 | -0.0016785 | 6.9842 | 0.016126 | 0.00020081 | -0.00092703 | -0.010173 | -0.00087163 | -0.0036011 | 0.0028732 | 0.013324 | 0.0040182 | -0.015172 | 0.026812 | -0.0054282 | -0.036621 | -0.050354 | 0.022888 | -0.032043 | 0.10071 | -0.004578 | -0.004578 | -0.068665 | 0.032043 | -0.018311 | -0.036621 | 0.045776 | -0.022888 | 0.082397 | 121.5775 | -0.17853 | -0.16022 | 121.6553 | 121.55 | 121.55 | -0.027466 | -0.027466 | 121.5363 | -0.096131 | -0.1648 | 121.6003 | 121.637 | 121.5317 | 0.10071 | -0.004577 | 0.07782 | -0.054931 | 0.064087 | -0.01831 | -0.073242 | 0.050354 | 121.5042 | 121.5866 | -0.10529 | -0.14649 | 121.5225 | 121.5179 | 121.5179 | 121.4859
3098.0625 | 121.7285 | -121.5683 | 0.12817 | -0.009308 | 6.9844 | 0.016126 | 0.0051142 | 0.0022772 | -0.0084637 | -0.00065803 | -0.0036011 | 0.0043686 | 0.013537 | 0.0095724 | -0.0091901 | 0.028734 | -0.007778 | -0.036621 | -0.045776 | 0.018311 | -0.054932 | 0.045776 | -0.059509 | -0.045776 | -0.086975 | 0.027466 | -0.018311 | -0.036621 | 0.009155 | -0.045776 | 0.091553 | 121.5866 | -0.17395 | -0.18311 | 121.6141 | 121.5225 | 121.5088 | -0.064087 | -0.07782 | 121.55 | -0.10071 | -0.1648 | 121.5775 | 121.6599 | 121.5225 | 0.10986 | -0.027465 | 0.027465 | -0.073243 | 0.027466 | -0.01831 | -0.064087 | 0.045777 | 121.5225 | 121.5958 | -0.10986 | -0.14649 | 121.5134 | 121.5317 | 121.5317 | 121.4813
3099.8281 | 121.7834 | -121.5866 | 0.11444 | -0.009308 | 6.9838 | 0.015058 | 0.0010552 | 0.00099557 | -0.0088911 | 0.0014784 | 0.0025025 | 0.0037278 | 0.011615 | 0.0020956 | -0.011754 | 0.028948 | -0.0035056 | 0 | -0.045776 | 0.027466 | 0 | 0.11902 | 0.009155 | 0.009155 | 0.013733 | 0.036621 | -0.009155 | 0.022888 | 0.07782 | 0.004578 | 0.11902 | 121.6141 | -0.16022 | -0.11444 | 121.7056 | 121.5958 | 121.5958 | -0.018311 | -0.018311 | 121.5775 | -0.07782 | -0.091553 | 121.6644 | 121.7056 | 121.5912 | 0.12817 | 0.013733 | 0.091553 | -0.027466 | 0.086975 | 0.032043 | -0.073242 | 0.045776 | 121.5408 | 121.6232 | -0.086975 | -0.1236 | 121.5866 | 121.6095 | 121.5866 | 121.6003
3101.5156 | 121.8018 | -121.5683 | 0.10529 | 0.01358 | 6.9816 | 0.014631 | 0.00062801 | 0.0046272 | -0.0091047 | -0.0019396 | -0.00054933 | 0.002446 | 0.013324 | 0.0038046 | -0.013035 | 0.028307 | -0.0011558 | -0.027466 | -0.032043 | 0.022888 | -0.022888 | 0.082397 | 0 | -0.013733 | -0.041199 | 0.027466 | -0.032043 | 0.018311 | 0.07782 | 0.004578 | 0.1236 | 121.5912 | -0.13733 | -0.12817 | 121.6507 | 121.5546 | 121.5683 | -0.036621 | -0.022888 | 121.5363 | -0.07782 | -0.086975 | 121.6461 | 121.6919 | 121.5729 | 0.15564 | 0.036621 | 0.059509 | -0.045776 | 0.10986 | 0.050354 | -0.054931 | 0.059509 | 121.5363 | 121.5958 | -0.082398 | -0.13733 | 121.5454 | 121.5866 | 121.5408 | 121.5271
3103.2656 | 121.8979 | -121.5775 | 0.073242 | -0.009308 | 6.9844 | 0.016981 | 0.0014826 | 0.0020636 | -0.0073957 | -0.0027942 | -0.0036011 | 0.0020188 | 0.012683 | 0.008077 | -0.0051313 | 0.029589 | -0.0035056 | 0.022888 | -0.064087 | 0.054932 | 0.054932 | 0.17853 | 0.068665 | 0.064087 | 0.068665 | -0.004578 | 0.032043 | 0.10529 | 0.15564 | 0.10071 | 0.19226 | 121.6324 | -0.13733 | -0.01831 | 121.756 | 121.6415 | 121.6461 | 0.009155 | 0.013733 | 121.6095 | -0.07782 | 0.032044 | 121.7331 | 121.7697 | 121.6782 | 0.16022 | 0.068665 | 0.1236 | 0 | 0.1236 | 0.073243 | -0.11902 | -0.036621 | 121.5134 | 121.5729 | -0.01831 | -0.041199 | 121.6324 | 121.6827 | 121.6003 | 121.6461
3104.9688 | 121.8201 | -121.6049 | 0.10529 | -0.016937 | 6.9838 | 0.016126 | 0.0010552 | -7.2628e-05 | -0.0095319 | 0.00062377 | -0.0036011 | 0.0030868 | 0.013537 | 0.004659 | -0.011326 | 0.029803 | -0.00671 | 0 | -0.050354 | 0.022888 | 0 | 0.1236 | 0.009155 | 0.013733 | 0.027466 | 0.036621 | -0.004578 | 0.032043 | 0.10529 | 0.032043 | 0.11902 | 121.6278 | -0.15564 | -0.10529 | 121.7285 | 121.6187 | 121.6141 | -0.009155 | -0.013733 | 121.6003 | -0.068665 | -0.073243 | 121.7102 | 121.7239 | 121.637 | 0.1236 | 0.036621 | 0.10071 | -0.022888 | 0.10986 | 0.036621 | -0.073242 | 0.041199 | 121.5546 | 121.6415 | -0.082398 | -0.10986 | 121.6049 | 121.637 | 121.6049 | 121.6324
3106.7031 | 121.8201 | -121.6278 | 0.11444 | -0.009308 | 6.9844 | 0.015699 | 0.0025506 | 0.0016364 | -0.0086773 | -0.0032214 | -0.00054933 | 0.005223 | 0.012256 | 0.0040182 | -0.011113 | 0.027453 | -0.0017966 | -0.013733 | -0.041199 | 0.027466 | 0.004578 | 0.14191 | 0.022888 | 0.032043 | 0.013733 | 0.041199 | 0 | 0.022888 | 0.091553 | 0.004578 | 0.12817 | 121.6553 | -0.15564 | -0.10986 | 121.7697 | 121.6599 | 121.6507 | 0.004577 | -0.004578 | 121.6278 | -0.073242 | -0.091553 | 121.7194 | 121.756 | 121.6324 | 0.12817 | 0.004578 | 0.11444 | -0.022888 | 0.091553 | 0.022888 | -0.068665 | 0.041199 | 121.5866 | 121.669 | -0.086975 | -0.11444 | 121.6324 | 121.6507 | 121.6141 | 121.6415
3108.4375 | 121.8796 | -121.6095 | 0.09613 | -0.0016785 | 6.984 | 0.018904 | -0.002149 | 0.005268 | -0.0086773 | -0.0045032 | -0.00054933 | 9.6204e-05 | 0.012683 | 0.007009 | -0.0074811 | 0.029589 | -0.0056418 | 0.009155 | -0.086975 | 0.064087 | 0.054932 | 0.20599 | 0.073242 | 0.073242 | 0.082397 | -0.022888 | 0.013733 | 0.086975 | 0.14191 | 0.082397 | 0.1831 | 121.6736 | -0.1831 | -0.041198 | 121.8155 | 121.6827 | 121.6827 | 0.009155 | 0.009155 | 121.6232 | -0.11902 | -0.009155 | 121.7514 | 121.7926 | 121.6919 | 0.16937 | 0.068664 | 0.14191 | -0.009155 | 0.12817 | 0.073242 | -0.15106 | -0.036621 | 121.5225 | 121.5866 | -0.032043 | -0.082397 | 121.6644 | 121.6965 | 121.6187 | 121.6919
3110.125 | 121.9208 | -121.5866 | 0.086975 | -0.0016785 | 6.9855 | 0.015486 | 0.0014826 | -0.00049983 | -0.0067547 | -0.00065803 | 0.0025025 | 0.0030868 | 0.015887 | 0.008077 | -0.0081219 | 0.03023 | 0.00033961 | 0.032043 | -0.064087 | 0.041199 | 0.073242 | 0.19226 | 0.045776 | 0.064087 | 0.09613 | -0.022888 | 0.032043 | 0.10986 | 0.15564 | 0.091553 | 0.19226 | 121.6278 | -0.15106 | -0.013733 | 121.7789 | 121.6507 | 121.6324 | 0.022888 | 0.004577 | 121.6187 | -0.10986 | 0.022888 | 121.7422 | 121.7789 | 121.6782 | 0.16022 | 0.05951 | 0.15106 | 0.032043 | 0.1236 | 0.07782 | -0.10529 | -0.054931 | 121.5225 | 121.5637 | -0.045776 | -0.054932 | 121.6599 | 121.6965 | 121.6187 | 121.6827
3111.8594 | 121.8018 | -121.6461 | 0.10529 | -0.0016785 | 6.9833 | 0.016126 | 0.0019098 | 0.00099557 | -0.0097455 | -0.0049304 | -0.0036011 | 0.0020188 | 0.014178 | 0.00060023 | -0.016026 | 0.027666 | -0.00051479 | -0.027466 | -0.041199 | 0.018311 | -0.032043 | 0.09613 | -0.009155 | -0.009155 | -0.064087 | 0.032043 | -0.009155 | -0.022888 | 0.050354 | -0.022888 | 0.07782 | 121.6644 | -0.14649 | -0.13733 | 121.7422 | 121.637 | 121.637 | -0.027466 | -0.027466 | 121.637 | -0.073243 | -0.12817 | 121.6965 | 121.7239 | 121.6232 | 0.086975 | -0.013733 | 0.077819 | -0.050354 | 0.059509 | -0.013733 | -0.05951 | 0.041198 | 121.6049 | 121.6782 | -0.086975 | -0.11444 | 121.6141 | 121.6232 | 121.6187 | 121.582
3113.5469 | 121.9208 | -121.582 | 0.07782 | -0.0016785 | 6.985 | 0.016554 | 0.002337 | 0.00099557 | -0.0071821 | -0.0015124 | 0.0025025 | 0.0026596 | 0.013324 | 0.0053 | -0.0079083 | 0.029803 | -0.0088462 | 0.022888 | -0.07782 | 0.050354 | 0.07782 | 0.20599 | 0.064087 | 0.082397 | 0.073242 | -0.004578 | 0.009155 | 0.10071 | 0.17395 | 0.10529 | 0.19226 | 121.6324 | -0.15564 | 0 | 121.788 | 121.6644 | 121.6461 | 0.032043 | 0.013733 | 121.5912 | -0.082398 | 0.022888 | 121.756 | 121.7743 | 121.6873 | 0.18311 | 0.096131 | 0.15564 | 0.027466 | 0.16479 | 0.091553 | -0.12817 | -0.013733 | 121.5042 | 121.5775 | -0.027466 | -0.068665 | 121.6599 | 121.6827 | 121.6049 | 121.6553
3115.2969 | 121.7972 | -121.6736 | 0.1236 | -0.009308 | 6.9857 | 0.013777 | 0.0027642 | 0.0012092 | -0.010173 | -0.003435 | -0.0066527 | 0.0033004 | 0.014605 | 0.0048728 | -0.010472 | 0.027666 | -0.00094199 | -0.068665 | -0.041199 | 0.013733 | -0.073242 | 0.018311 | -0.054932 | -0.059509 | -0.10071 | 0.050354 | -0.004578 | -0.027466 | 0.004578 | -0.054932 | 0.091553 | 121.6873 | -0.16479 | -0.19684 | 121.6919 | 121.6141 | 121.6187 | -0.073242 | -0.068665 | 121.669 | -0.073242 | -0.15106 | 121.6782 | 121.7651 | 121.6187 | 0.096131 | -0.050354 | 0.004578 | -0.086975 | 0.009156 | -0.022888 | -0.054932 | 0.054932 | 121.6324 | 121.7239 | -0.10986 | -0.12817 | 121.6003 | 121.6461 | 121.6049 | 121.5729
3116.9844 | 121.9345 | -121.6003 | 0.10071 | -0.009308 | 6.9816 | 0.015058 | -0.001081 | -0.0028498 | -0.0080365 | -0.0032214 | -0.0036011 | 0.0009506 | 0.010333 | 0.013204 | -0.011754 | 0.028734 | -0.002651 | 0.018311 | -0.082397 | 0.050354 | 0.086975 | 0.23346 | 0.10071 | 0.091553 | 0.09613 | -0.004578 | 0.022888 | 0.086975 | 0.18768 | 0.12817 | 0.17853 | 121.6507 | -0.18311 | -0.013733 | 121.8338 | 121.6919 | 121.701 | 0.041199 | 0.050354 | 121.6232 | -0.10529 | -0.013733 | 121.788 | 121.7789 | 121.7285 | 0.15564 | 0.10529 | 0.1831 | 0.036621 | 0.16479 | 0.064087 | -0.13275 | -0.027466 | 121.5179 | 121.5958 | -0.050354 | -0.07782 | 121.6873 | 121.6873 | 121.6187 | 121.6965
3118.75 | 121.9528 | -121.6049 | 0.09613 | -0.0016785 | 6.9846 | 0.017835 | 0.00041441 | 0.0029182 | -0.0078229 | -0.0030078 | -0.00054933 | 0.0030868 | 0.011615 | 0.010641 | -0.0074811 | 0.029589 | -0.0041464 | 0 | -0.064087 | 0.045776 | 0.041199 | 0.15106 | 0.027466 | 0.041199 | 0.054932 | 0.009155 | 0.018311 | 0.10986 | 0.15564 | 0.086975 | 0.19684 | 121.6507 | -0.16022 | -0.054931 | 121.756 | 121.6461 | 121.6324 | -0.004577 | -0.01831 | 121.6232 | -0.086975 | 0.013733 | 121.7606 | 121.8018 | 121.6919 | 0.17853 | 0.068664 | 0.10529 | -0.004577 | 0.13733 | 0.091552 | -0.10986 | -0.009156 | 121.5408 | 121.6141 | -0.050354 | -0.077819 | 121.6461 | 121.7148 | 121.6049 | 121.6599
3120.5 | 121.9162 | -121.6461 | 0.091553 | 0.005951 | 6.9838 | 0.016554 | 0.00084161 | 0.0033454 | -0.0073957 | -0.003435 | -0.0036011 | 0.0018052 | 0.014178 | 0.012136 | -0.010899 | 0.027666 | -0.002651 | -0.036621 | -0.064087 | 0.050354 | -0.004578 | 0.11444 | 0.032043 | 0.018311 | -0.027466 | 0.018311 | -0.004578 | 0.027466 | 0.09613 | 0.036621 | 0.13733 | 121.6965 | -0.15564 | -0.096131 | 121.7606 | 121.6644 | 121.6782 | -0.032043 | -0.018311 | 121.6415 | -0.073242 | -0.064087 | 121.7422 | 121.7834 | 121.6827 | 0.14191 | 0.041199 | 0.064087 | -0.054932 | 0.10071 | 0.032044 | -0.11444 | 0.022889 | 121.582 | 121.6644 | -0.041199 | -0.096131 | 121.6415 | 121.6736 | 121.6095 | 121.6187
3122.25 | 121.8979 | -121.6782 | 0.10986 | -0.016937 | 6.9833 | 0.017408 | 0.0025506 | 0.0039862 | -0.0076093 | -0.0030078 | -0.00054933 | 0.0030868 | 0.014392 | 0.0053 | -0.010258 | 0.028094 | -0.00072839 | -0.004578 | -0.050354 | 0.013733 | 0.013733 | 0.1236 | 0.013733 | 0.018311 | 0.022888 | 0.027466 | 0 | 0.036621 | 0.082397 | 0.036621 | 0.13275 | 121.6919 | -0.16022 | -0.09613 | 121.8018 | 121.6965 | 121.6919 | 0.004578 | 0 | 121.6782 | -0.082397 | -0.073242 | 121.7606 | 121.8109 | 121.7148 | 0.13275 | 0.036621 | 0.10986 | 0 | 0.082397 | 0.036621 | -0.064087 | 0.027466 | 121.6278 | 121.7056 | -0.09613 | -0.10986 | 121.6919 | 121.7148 | 121.6736 | 121.701
3123.9375 | 121.8201 | -121.7056 | 0.12817 | 0.005951 | 6.9857 | 0.015699 | 0.00062801 | -0.00071343 | -0.0069683 | -0.0040758 | -0.0036011 | 0.0003098 | 0.012897 | -0.002604 | -0.012395 | 0.029589 | 0.00055321 | -0.054932 | -0.041199 | 0.004578 | -0.07782 | 0.009155 | -0.073242 | -0.068665 | -0.11444 | 0.050354 | -0.022888 | -0.027466 | 0.013733 | -0.059509 | 0.07782 | 121.7102 | -0.16937 | -0.20599 | 121.7148 | 121.637 | 121.6324 | -0.073243 | -0.07782 | 121.6827 | -0.07782 | -0.15564 | 121.7194 | 121.7834 | 121.6461 | 0.10071 | -0.036621 | 0.004577 | -0.082398 | 0.036621 | -0.004578 | -0.045777 | 0.073242 | 121.6644 | 121.756 | -0.1236 | -0.15106 | 121.6278 | 121.6782 | 121.6507 | 121.5912
3125.6719 | 121.9437 | -121.6644 | 0.10529 | 0.005951 | 6.9842 | 0.016126 | 0.00084161 | -0.0013544 | -0.0078229 | -0.0021532 | -0.00054933 | 0.0026596 | 0.015033 | 0.011922 | -0.0087629 | 0.028948 | 0.0014078 | 0.013733 | -0.064087 | 0.059509 | 0.059509 | 0.19684 | 0.054932 | 0.073242 | 0.091553 | 0 | 0.004578 | 0.082397 | 0.15106 | 0.082397 | 0.1831 | 121.7239 | -0.16937 | -0.045777 | 121.8613 | 121.7377 | 121.7194 | 0.013733 | -0.004577 | 121.669 | -0.10529 | -0.022889 | 121.8155 | 121.8475 | 121.7468 | 0.17853 | 0.077819 | 0.13733 | 0 | 0.14648 | 0.077819 | -0.1236 | -0.004578 | 121.6003 | 121.6644 | -0.045777 | -0.10071 | 121.7239 | 121.7468 | 121.6782 | 121.756
3127.3594 | 121.9254 | -121.6873 | 0.10071 | -0.016937 | 6.9846 | 0.015058 | 0.0029778 | 0.0022772 | -0.0093183 | -0.0040758 | -0.0036011 | 0.0011642 | 0.012469 | 0.0027364 | -0.011113 | 0.027453 | -0.0058554 | -0.022888 | -0.045776 | 0.004578 | -0.004578 | 0.091553 | -0.009155 | 0.009155 | -0.018311 | 0.027466 | -0.004578 | 0.018311 | 0.091553 | 0.018311 | 0.12817 | 121.6919 | -0.14648 | -0.10529 | 121.7789 | 121.6965 | 121.6782 | 0.004577 | -0.013733 | 121.6827 | -0.073242 | -0.082397 | 121.7789 | 121.8155 | 121.7056 | 0.13275 | 0.022889 | 0.086975 | -0.009156 | 0.096131 | 0.022889 | -0.050354 | 0.032044 | 121.6415 | 121.7148 | -0.09613 | -0.10529 | 121.6827 | 121.7056 | 121.6644 | 121.669
3129.1094 | 121.994 | -121.6461 | 0.068665 | -0.0016785 | 6.9844 | 0.018049 | 0.001269 | 0.0048408 | -0.0071821 | -0.0042896 | -0.00054933 | 0.0015914 | 0.013537 | 0.01299 | -0.0064129 | 0.031298 | -0.0037192 | 0.018311 | -0.086975 | 0.073242 | 0.054932 | 0.19684 | 0.050354 | 0.07782 | 0.082397 | -0.009155 | 0.022888 | 0.11444 | 0.16022 | 0.10071 | 0.20142 | 121.7194 | -0.15564 | -0.013733 | 121.843 | 121.7239 | 121.6965 | 0.004578 | -0.022888 | 121.669 | -0.07782 | 0.045776 | 121.8063 | 121.8475 | 121.7468 | 0.17853 | 0.07782 | 0.1236 | -0.01831 | 0.13733 | 0.091553 | -0.16022 | -0.032043 | 121.5591 | 121.637 | 0.004577 | -0.045777 | 121.701 | 121.7606 | 121.6644 | 121.7285
3130.8438 | 121.9025 | -121.7148 | 0.11444 | -0.009308 | 6.9829 | 0.015913 | 0.002337 | 0.00014097 | -0.010173 | -0.0015124 | -0.0036011 | 0.0018052 | 0.012683 | 0.0085044 | -0.014317 | 0.028094 | -0.0041464 | 0.022888 | -0.082397 | 0.050354 | 0.036621 | 0.16479 | 0.073242 | 0.054932 | -0.004578 | 0.022888 | 0 | 0 | 0.09613 | 0.022888 | 0.10986 | 121.7651 | -0.19684 | -0.07782 | 121.8796 | 121.7697 | 121.788 | 0.004578 | 0.022888 | 121.7148 | -0.091553 | -0.11444 | 121.8109 | 121.8246 | 121.7377 | 0.10986 | 0.022888 | 0.11444 | -0.013733 | 0.09613 | 0 | -0.13275 | 0.022888 | 121.6324 | 121.7377 | -0.064087 | -0.11444 | 121.7514 | 121.7148 | 121.7377 | 121.7102
3132.5312 | 122.0078 | -121.6736 | 0.09613 | -0.016937 | 6.9842 | 0.018476 | 0.00041441 | 0.0020636 | -0.010173 | -0.0049304 | -0.00054933 | 0.0020188 | 0.013965 | 0.0078634 | -0.0098309 | 0.028094 | 0.00033961 | 0.004578 | -0.082397 | 0.064087 | 0.091553 | 0.25635 | 0.10529 | 0.086975 | 0.086975 | 0 | 0.009155 | 0.09613 | 0.18768 | 0.12817 | 0.1831 | 121.7377 | -0.17853 | -0.004577 | 121.9299 | 121.7606 | 121.7789 | 0.022888 | 0.041199 | 121.6827 | -0.09613 | 0 | 121.8613 | 121.8567 | 121.8018 | 0.17395 | 0.11902 | 0.19226 | 0.027466 | 0.17853 | 0.086975 | -0.14648 | -0.009155 | 121.5912 | 121.6736 | -0.032043 | -0.086975 | 121.7651 | 121.7697 | 121.6782 | 121.7606
3134.2812 | 121.9482 | -121.7056 | 0.11444 | -0.009308 | 6.984 | 0.01399 | 0.0036188 | 0.0078314 | -0.0071821 | -0.0036486 | 0.0025025 | 0.0047958 | 0.01311 | 0.0085044 | -0.010258 | 0.027025 | -0.0045736 | 0.004578 | -0.050354 | 0.032043 | 0.004578 | 0.13275 | -0.013733 | 0.004578 | 0.018311 | 0.004578 | -0.009155 | 0.036621 | 0.091553 | 0.022888 | 0.13275 | 121.7377 | -0.16479 | -0.10986 | 121.8384 | 121.7102 | 121.6919 | -0.027465 | -0.045776 | 121.6965 | -0.10986 | -0.07782 | 121.7972 | 121.8384 | 121.7285 | 0.14191 | 0.032043 | 0.10071 | -0.027465 | 0.10071 | 0.045776 | -0.082397 | 0.013733 | 121.6553 | 121.7102 | -0.082398 | -0.1236 | 121.7102 | 121.7422 | 121.7102 | 121.7239
3136.0156 | 121.9299 | -121.7056 | 0.12817 | -0.0016785 | 6.9838 | 0.01399 | 0.0021234 | 0.00035457 | -0.0080365 | -1.7026e-05 | -0.0066527 | 0.003514 | 0.012683 | 0.0053 | -0.0096173 | 0.026171 | -0.0062826 | -0.027466 | -0.036621 | 0.009155 | -0.013733 | 0.086975 | 0.022888 | -0.004578 | -0.032043 | 0.032043 | -0.013733 | 0.027466 | 0.091553 | 0.022888 | 0.1236 | 121.7148 | -0.1648 | -0.14191 | 121.7926 | 121.701 | 121.7285 | -0.013733 | 0.013733 | 121.6919 | -0.096131 | -0.10071 | 121.7972 | 121.8292 | 121.7285 | 0.13733 | 0.036621 | 0.07782 | -0.022888 | 0.10529 | 0.041199 | -0.045776 | 0.045776 | 121.669 | 121.7377 | -0.11902 | -0.14191 | 121.6919 | 121.7331 | 121.6782 | 121.6736
3137.7812 | 121.9482 | -121.7056 | 0.10986 | -0.009308 | 6.9829 | 0.01634 | 0.0027642 | -0.00049983 | -0.0078229 | -0.0040758 | -0.0066527 | 0.0047958 | 0.013537 | 0.0040182 | -0.0068403 | 0.029162 | -0.0020102 | -0.041199 | -0.027466 | 0.041199 | -0.045776 | 0.050354 | -0.064087 | -0.032043 | -0.050354 | 0.032043 | -0.009155 | 0.036621 | 0.068665 | 0.004578 | 0.14648 | 121.7468 | -0.13733 | -0.15564 | 121.756 | 121.6736 | 121.6415 | -0.073242 | -0.10529 | 121.6965 | -0.07782 | -0.073242 | 121.7743 | 121.8521 | 121.7102 | 0.15564 | 0.013733 | 0.009155 | -0.086975 | 0.07782 | 0.045776 | -0.068665 | 0.041198 | 121.6782 | 121.7377 | -0.068664 | -0.11902 | 121.6599 | 121.7422 | 121.6644 | 121.6553
3139.4844 | 121.994 | -121.7056 | 0.10529 | -0.0016785 | 6.9825 | 0.016126 | 0.00041441 | -0.0022088 | -0.0084637 | -0.003435 | -0.0036011 | 0.0020188 | 0.014605 | 0.010427 | -0.0096173 | 0.03023 | 0.00098061 | -0.027466 | -0.073242 | 0.045776 | 0.018311 | 0.16022 | 0.018311 | 0.054932 | 0.013733 | 0.004578 | 0.022888 | 0.041199 | 0.10071 | 0.054932 | 0.14191 | 121.7514 | -0.17853 | -0.086975 | 121.8658 | 121.7606 | 121.7239 | 0.009156 | -0.027465 | 121.7285 | -0.10071 | -0.064087 | 121.8063 | 121.8475 | 121.7606 | 0.11902 | 0.032044 | 0.11444 | -0.027465 | 0.07782 | 0.018311 | -0.11902 | -0.01831 | 121.6324 | 121.7102 | -0.05951 | -0.082398 | 121.7239 | 121.7468 | 121.6782 | 121.7194
3141.1719 | 121.9116 | -121.7743 | 0.086975 | 0.005951 | 6.9857 | 0.015272 | 0.0019098 | 0.0065498 | -0.0097455 | -0.0047168 | -0.0036011 | 0.003514 | 0.010974 | 0.004659 | -0.0098309 | 0.028734 | -0.0069236 | 0 | -0.050354 | 0.032043 | 0 | 0.09613 | -0.009155 | -0.004578 | -0.018311 | 0.027466 | -0.009155 | 0.009155 | 0.059509 | -0.027466 | 0.091553 | 121.8063 | -0.13733 | -0.086975 | 121.8704 | 121.7697 | 121.7651 | -0.036621 | -0.041198 | 121.7651 | -0.059509 | -0.07782 | 121.8338 | 121.8658 | 121.7468 | 0.10071 | -0.018311 | 0.064087 | -0.032043 | 0.068664 | 0.01831 | -0.082397 | 0.036621 | 121.7239 | 121.8018 | -0.054932 | -0.09613 | 121.7743 | 121.7834 | 121.7743 | 121.756
3142.9062 | 122.0078 | -121.7239 | 0.091553 | -0.009308 | 6.985 | 0.01634 | 0.0027642 | 0.0031318 | -0.0086773 | -0.0025806 | -0.0036011 | 0.0028732 | 0.014605 | 0.0023092 | -0.0098309 | 0.029375 | -0.0037192 | -0.045776 | -0.041199 | 0.032043 | -0.032043 | 0.07782 | -0.027466 | -0.013733 | -0.018311 | 0.032043 | -0.009155 | 0.073242 | 0.10529 | 0.054932 | 0.16022 | 121.756 | -0.13275 | -0.1236 | 121.8018 | 121.7102 | 121.6965 | -0.045776 | -0.059509 | 121.7148 | -0.05951 | -0.018311 | 121.8292 | 121.8842 | 121.7789 | 0.16937 | 0.064087 | 0.045777 | -0.064086 | 0.11444 | 0.082397 | -0.073242 | 0.041198 | 121.6827 | 121.756 | -0.05951 | -0.10071 | 121.6919 | 121.7972 | 121.6782 | 121.7056
3144.5938 | 121.9986 | -121.7606 | 0.10529 | -0.009308 | 6.9827 | 0.015272 | 0.0016962 | 0.0031318 | -0.0080365 | -0.001726 | -0.00054933 | 0.0018052 | 0.013324 | 0.0089316 | -0.0083355 | 0.027025 | -0.0039328 | -0.018311 | -0.082397 | 0.045776 | 0.009155 | 0.13733 | 0.027466 | 0.032043 | 0.004578 | 0.013733 | 0.009155 | 0.032043 | 0.11444 | 0.054932 | 0.13733 | 121.8063 | -0.18768 | -0.096131 | 121.8979 | 121.7926 | 121.788 | -0.013733 | -0.01831 | 121.7697 | -0.091553 | -0.073243 | 121.875 | 121.8979 | 121.8155 | 0.12817 | 0.045777 | 0.091553 | -0.036621 | 0.10529 | 0.022888 | -0.12817 | 0.004578 | 121.6782 | 121.7743 | -0.05951 | -0.096131 | 121.7697 | 121.7926 | 121.7422 | 121.7651
3146.3438 | 121.9208 | -121.7697 | 0.11902 | -0.024567 | 6.9829 | 0.013563 | 0.00020081 | 0.00099557 | -0.0084637 | -0.0021532 | -0.0066527 | 0.0026596 | 0.014819 | 0.006368 | -0.013463 | 0.02788 | -0.0020102 | -0.07782 | -0.045776 | 0 | -0.073242 | 0.054932 | -0.032043 | -0.013733 | -0.082397 | 0.064087 | -0.013733 | -0.045776 | 0.036621 | -0.009155 | 0.068665 | 121.7697 | -0.16479 | -0.19226 | 121.8246 | 121.756 | 121.7377 | -0.013733 | -0.032043 | 121.756 | -0.054932 | -0.16479 | 121.8063 | 121.8384 | 121.7606 | 0.082398 | 0.004578 | 0.054932 | -0.073242 | 0.050354 | -0.032043 | -0.045776 | 0.07782 | 121.7239 | 121.8338 | -0.11902 | -0.13275 | 121.6965 | 121.7239 | 121.6919 | 121.6873
3148.0312 | 122.0352 | -121.7331 | 0.07782 | -0.016937 | 6.9853 | 0.014845 | 0.0014826 | -0.00049983 | -0.0065411 | 0.00041017 | -0.00054933 | 0.0026596 | 0.013324 | 0.0095724 | -0.0061993 | 0.03023 | -0.001583 | -0.032043 | -0.064087 | 0.032043 | 0.018311 | 0.14648 | 0.032043 | 0.036621 | 0.064087 | 0 | 0.018311 | 0.10529 | 0.15564 | 0.07782 | 0.19684 | 121.7651 | -0.14191 | -0.059509 | 121.8796 | 121.7697 | 121.7651 | 0.004578 | 0 | 121.7514 | -0.07782 | 0.027466 | 121.8887 | 121.9299 | 121.8109 | 0.17853 | 0.059509 | 0.11444 | -0.013732 | 0.13733 | 0.086975 | -0.09613 | -0.018311 | 121.669 | 121.7331 | -0.045777 | -0.059509 | 121.7514 | 121.8384 | 121.701 | 121.7972
3149.7969 | 121.9208 | -121.7789 | 0.11902 | -0.016937 | 6.9848 | 0.014845 | 0.0029778 | 0.0029182 | -0.010386 | 0.00062377 | -0.00054933 | 0.0003098 | 0.014392 | 0.0044454 | -0.014531 | 0.027453 | -0.0024374 | -0.07782 | -0.032043 | 0.009155 | -0.068665 | 0.045776 | -0.013733 | -0.022888 | -0.086975 | 0.050354 | -0.036621 | -0.045776 | 0.041199 | -0.022888 | 0.068665 | 121.788 | -0.15106 | -0.18768 | 121.8246 | 121.756 | 121.7651 | -0.032043 | -0.022888 | 121.7422 | -0.068665 | -0.16479 | 121.8201 | 121.8475 | 121.756 | 0.10529 | 0.013733 | 0.036621 | -0.07782 | 0.07782 | -0.009155 | -0.041198 | 0.086975 | 121.7468 | 121.8292 | -0.10986 | -0.15564 | 121.7102 | 121.7331 | 121.701 | 121.6919
3151.4844 | 122.0123 | -121.7651 | 0.09613 | -0.0016785 | 6.981 | 0.014845 | 0.0014826 | -0.0024224 | -0.0095319 | -0.0040758 | -0.0036011 | 0.0013778 | 0.013537 | 0.0082906 | -0.010045 | 0.028948 | -0.00094199 | -0.041199 | -0.073242 | 0.041199 | 0.004578 | 0.11902 | 0.018311 | 0.022888 | -0.013733 | 0.004578 | 0.018311 | 0.041199 | 0.10071 | 0.041199 | 0.14191 | 121.8063 | -0.16937 | -0.091552 | 121.8842 | 121.788 | 121.7834 | -0.018311 | -0.022888 | 121.7834 | -0.091552 | -0.054931 | 121.8658 | 121.907 | 121.8063 | 0.1236 | 0.022888 | 0.07782 | -0.036621 | 0.082397 | 0.022888 | -0.11444 | -0.013733 | 121.6919 | 121.7697 | -0.054931 | -0.077819 | 121.7697 | 121.8063 | 121.7239 | 121.7514
3153.2344 | 121.9437 | -121.7789 | 0.11444 | -0.009308 | 6.9825 | 0.014417 | 0.00041441 | -0.0011408 | -0.0084637 | -0.0032214 | -0.0036011 | 0.0013778 | 0.013751 | 0.010641 | -0.012395 | 0.026598 | -0.0045736 | -0.013733 | -0.054932 | 0.045776 | 0.004578 | 0.1236 | 0.027466 | 0.022888 | -0.036621 | 0.022888 | -0.004578 | -0.032043 | 0.050354 | 0.004578 | 0.082397 | 121.8246 | -0.16937 | -0.10986 | 121.9025 | 121.8018 | 121.8063 | -0.022888 | -0.01831 | 121.7743 | -0.091553 | -0.14648 | 121.8292 | 121.8613 | 121.7834 | 0.086975 | 0.009156 | 0.07782 | -0.041198 | 0.054932 | -0.027465 | -0.10071 | 0.027466 | 121.7239 | 121.8018 | -0.068665 | -0.11902 | 121.7834 | 121.7468 | 121.7651 | 121.7422
3154.9219 | 121.9528 | -121.7926 | 0.12817 | -0.009308 | 6.9846 | 0.016126 | 0.0025506 | -7.2628e-05 | -0.0082501 | -0.0042896 | 0.0025025 | 0.005223 | 0.015033 | 0.011709 | -0.0083355 | 0.029162 | -0.00436 | -0.045776 | -0.050354 | 0.018311 | -0.064087 | 0.032043 | -0.059509 | -0.059509 | -0.073242 | 0.022888 | -0.018311 | -0.022888 | 0.018311 | -0.050354 | 0.086975 | 121.8109 | -0.17853 | -0.19226 | 121.8246 | 121.7331 | 121.7331 | -0.07782 | -0.07782 | 121.7743 | -0.10529 | -0.15106 | 121.8109 | 121.8796 | 121.7422 | 0.10529 | -0.032043 | 0.013732 | -0.082398 | 0.036622 | -0.004577 | -0.068665 | 0.041199 | 121.7422 | 121.8155 | -0.10986 | -0.14649 | 121.7285 | 121.7697 | 121.7468 | 121.7194
3156.6719 | 122.0947 | -121.7422 | 0.082397 | -0.009308 | 6.9846 | 0.01399 | -1.2792e-05 | -0.003277 | -0.0093183 | -0.0047168 | -0.00054933 | 0.0003098 | 0.01311 | 0.014059 | -0.010686 | 0.028094 | -0.0024374 | 0.004578 | -0.059509 | 0.059509 | 0.036621 | 0.19684 | 0.10529 | 0.10986 | 0.091553 | 0 | 0.018311 | 0.086975 | 0.19226 | 0.14191 | 0.20142 | 121.8018 | -0.14191 | -0.045776 | 121.9391 | 121.8521 | 121.8475 | 0.050354 | 0.045777 | 121.7606 | -0.082397 | 0.004578 | 121.9345 | 121.9437 | 121.8842 | 0.18311 | 0.1236 | 0.13733 | -0.022888 | 0.17395 | 0.068664 | -0.11902 | -0.018311 | 121.6827 | 121.7422 | -0.022888 | -0.064086 | 121.7789 | 121.8292 | 121.7468 | 121.8338
3158.3594 | 122.0673 | -121.7697 | 0.10529 | -0.009308 | 6.9848 | 0.016767 | -0.0012946 | 0.0027044 | -0.0095319 | -0.0019396 | 0.0025025 | 0.0022324 | 0.013537 | 0.010213 | -0.010472 | 0.03023 | 0.0011942 | -0.022888 | -0.082397 | 0.032043 | 0.022888 | 0.13733 | 0.050354 | 0.041199 | 0.009155 | 0.022888 | 0.009155 | 0.054932 | 0.12817 | 0.082397 | 0.16479 | 121.8018 | -0.18768 | -0.082398 | 121.907 | 121.8109 | 121.8201 | 0.009156 | 0.018311 | 121.7789 | -0.082398 | -0.050354 | 121.8979 | 121.9345 | 121.8521 | 0.15564 | 0.073242 | 0.10529 | -0.009155 | 0.11902 | 0.045777 | -0.11444 | 0.013733 | 121.6873 | 121.7926 | -0.073243 | -0.096131 | 121.7926 | 121.8246 | 121.7468 | 121.7789
3160.1094 | 121.9803 | -121.788 | 0.11902 | -0.016937 | 6.9833 | 0.016981 | 0.0038324 | 0.003559 | -0.0086773 | -0.0012988 | -0.0036011 | 0.0065048 | 0.012469 | 0.0095724 | -0.0096173 | 0.027025 | -0.0017966 | -0.045776 | -0.032043 | 0.009155 | -0.064087 | 0.036621 | -0.068665 | -0.036621 | -0.07782 | 0.027466 | -0.022888 | -0.013733 | 0.027466 | -0.041199 | 0.10986 | 121.7972 | -0.15106 | -0.18311 | 121.8246 | 121.7514 | 121.7194 | -0.045776 | -0.07782 | 121.7651 | -0.091553 | -0.13275 | 121.8155 | 121.8979 | 121.7468 | 0.13275 | -0.018311 | 0.027466 | -0.073242 | 0.050354 | 0.009155 | -0.041198 | 0.050354 | 121.756 | 121.8155 | -0.10986 | -0.14191 | 121.7239 | 121.7743 | 121.7422 | 121.7102
3161.8594 | 122.1039 | -121.7697 | 0.086975 | -0.009308 | 6.9812 | 0.015913 | 0.00062801 | 0.0050544 | -0.010173 | -0.0036486 | -0.0066527 | 0.0013778 | 0.012256 | 0.014913 | -0.01154 | 0.027239 | -0.003292 | 0 | -0.086975 | 0.054932 | 0.073242 | 0.18768 | 0.09613 | 0.091553 | 0.082397 | -0.013733 | 0.018311 | 0.10071 | 0.18768 | 0.11902 | 0.19684 | 121.8246 | -0.17395 | -0.013733 | 121.9574 | 121.8613 | 121.8658 | 0.036621 | 0.041198 | 121.788 | -0.10071 | 0.013733 | 121.9574 | 121.9666 | 121.8887 | 0.17853 | 0.10071 | 0.13275 | 0.01831 | 0.16937 | 0.082397 | -0.14191 | -0.032044 | 121.6827 | 121.756 | -0.032043 | -0.068664 | 121.843 | 121.8704 | 121.7697 | 121.8521
3163.5312 | 121.9574 | -121.8155 | 0.11444 | -0.016937 | 6.9859 | 0.014631 | 0.0044732 | 0.0020636 | -0.0091047 | -0.0021532 | -0.00054933 | 0.0050094 | 0.01311 | -0.00046777 | -0.010899 | 0.027666 | -0.0035056 | -0.041199 | -0.045776 | 0.004578 | -0.041199 | 0.045776 | -0.054932 | -0.041199 | -0.07782 | 0.041199 | -0.004578 | -0.022888 | 0.009155 | -0.050354 | 0.059509 | 121.8201 | -0.16022 | -0.15564 | 121.8613 | 121.7743 | 121.7606 | -0.045777 | -0.05951 | 121.8109 | -0.073242 | -0.13733 | 121.8246 | 121.875 | 121.7651 | 0.064087 | -0.045776 | 0.041198 | -0.045777 | 0.013733 | -0.01831 | -0.050354 | 0.045777 | 121.7697 | 121.8567 | -0.10986 | -0.11902 | 121.7743 | 121.7926 | 121.7743 | 121.7377
3165.2656 | 122.0032 | -121.8521 | 0.11902 | -0.009308 | 6.9861 | 0.016554 | 0.0044732 | 0.0027044 | -0.0093183 | -0.00087163 | -0.00054933 | 0.0045822 | 0.013324 | 0.0042318 | -0.0087629 | 0.02788 | -0.0011558 | -0.064087 | -0.036621 | 0.022888 | -0.07782 | 0.032043 | -0.07782 | -0.045776 | -0.091553 | 0.032043 | -0.032043 | -0.004578 | 0.022888 | -0.045776 | 0.086975 | 121.875 | -0.15564 | -0.19684 | 121.8842 | 121.8063 | 121.7743 | -0.068664 | -0.10071 | 121.8201 | -0.086976 | -0.1236 | 121.875 | 121.9391 | 121.8063 | 0.11902 | -0.013733 | 0.009155 | -0.10071 | 0.054931 | 0.027465 | -0.059509 | 0.064086 | 121.8155 | 121.8842 | -0.096131 | -0.15106 | 121.7743 | 121.8475 | 121.788 | 121.7606
3166.9531 | 122.0673 | -121.8109 | 0.10071 | -0.009308 | 6.9833 | 0.015913 | 0.00020081 | 0.0012092 | -0.0071821 | -0.0021532 | -0.0066527 | 0.0011642 | 0.013751 | 0.011068 | -0.0098309 | 0.028734 | -0.001583 | -0.036621 | -0.068665 | 0.036621 | 0 | 0.11902 | 0.022888 | 0.022888 | 0.004578 | 0.009155 | -0.018311 | 0.027466 | 0.1236 | 0.064087 | 0.15106 | 121.8475 | -0.16937 | -0.10071 | 121.9299 | 121.8338 | 121.8338 | -0.013733 | -0.013733 | 121.7926 | -0.091553 | -0.073242 | 121.9345 | 121.962 | 121.875 | 0.16937 | 0.082398 | 0.082398 | -0.036621 | 0.14191 | 0.045777 | -0.10529 | 0.027466 | 121.7422 | 121.8201 | -0.064087 | -0.11902 | 121.8109 | 121.8384 | 121.7743 | 121.8155
3168.7031 | 122.1085 | -121.8018 | 0.091553 | -0.016937 | 6.9814 | 0.014417 | -0.00022639 | 0.0033454 | -0.0061139 | -0.003435 | -0.00054933 | -0.0003312 | 0.014605 | 0.004659 | -0.011113 | 0.028948 | -0.0013694 | -0.027466 | -0.073242 | 0.036621 | 0.027466 | 0.14191 | 0.036621 | 0.054932 | 0.027466 | 0.009155 | -0.004578 | 0.064087 | 0.15564 | 0.1236 | 0.18768 | 121.8384 | -0.16479 | -0.064087 | 121.9437 | 121.8567 | 121.8384 | 0.018311 | 0 | 121.7972 | -0.082398 | -0.027466 | 121.9574 | 121.9894 | 121.9254 | 0.19226 | 0.12817 | 0.10529 | -0.009155 | 0.16022 | 0.068665 | -0.10986 | 0.013733 | 121.7285 | 121.8109 | -0.054932 | -0.096131 | 121.8292 | 121.8658 | 121.7743 | 121.8292
3170.4531 | 122.1085 | -121.7651 | 0.091553 | -0.024567 | 6.985 | 0.01869 | 0.0027642 | 0.0014228 | -0.0078229 | -0.0030078 | -0.0066527 | 0.0039414 | 0.012469 | 0.010854 | -0.0057721 | 0.030871 | -0.0030784 | 0.022888 | -0.086975 | 0.059509 | 0.082397 | 0.19684 | 0.059509 | 0.07782 | 0.086975 | 0 | 0.022888 | 0.10071 | 0.16479 | 0.10071 | 0.1831 | 121.8246 | -0.17853 | -0.009156 | 121.962 | 121.843 | 121.8246 | 0.018311 | 0 | 121.788 | -0.091553 | 0.009155 | 121.9299 | 121.9482 | 121.8658 | 0.16022 | 0.07782 | 0.13733 | 0.022888 | 0.14191 | 0.07782 | -0.14648 | -0.022888 | 121.6782 | 121.7651 | -0.032044 | -0.068665 | 121.8475 | 121.8658 | 121.788 | 121.8521
3172.1875 | 122.1176 | -121.8109 | 0.086975 | 0.01358 | 6.9853 | 0.018049 | 0.0016962 | -0.0024224 | -0.0063275 | -0.00044443 | -0.0036011 | 0.0009506 | 0.012683 | 0.0076498 | -0.0079083 | 0.030016 | 0.0029032 | 0.045776 | -0.068665 | 0.059509 | 0.073242 | 0.20599 | 0.064087 | 0.068665 | 0.09613 | 0.009155 | 0.009155 | 0.10071 | 0.16022 | 0.07782 | 0.18768 | 121.8704 | -0.15564 | -0.013733 | 122.0169 | 121.8796 | 121.875 | 0.009156 | 0.004578 | 121.8201 | -0.07782 | 0.013733 | 121.9711 | 121.9986 | 121.8887 | 0.17853 | 0.068665 | 0.14649 | 0.013733 | 0.15106 | 0.091553 | -0.12817 | 0 | 121.7422 | 121.8201 | -0.027466 | -0.07782 | 121.8842 | 121.9116 | 121.8567 | 121.907
3173.875 | 122.0078 | -121.8658 | 0.12817 | -0.016937 | 6.9827 | 0.014204 | -0.00043999 | 0.0012092 | -0.0088911 | -0.00065803 | -0.00054933 | 0.0020188 | 0.012683 | 0.003591 | -0.013249 | 0.025316 | -0.0064962 | -0.032043 | -0.045776 | 0.022888 | -0.032043 | 0.091553 | -0.013733 | 0 | -0.045776 | 0.045776 | -0.004578 | -0.041199 | 0.045776 | -0.022888 | 0.073242 | 121.8887 | -0.17395 | -0.16022 | 121.9574 | 121.8658 | 121.8521 | -0.022888 | -0.036621 | 121.8613 | -0.082398 | -0.16937 | 121.9116 | 121.9391 | 121.843 | 0.07782 | -0.01831 | 0.068665 | -0.054931 | 0.050354 | -0.036621 | -0.068664 | 0.050354 | 121.8201 | 121.9116 | -0.10529 | -0.13275 | 121.8338 | 121.8246 | 121.8338 | 121.8201
3175.6406 | 122.049 | -121.8567 | 0.11902 | 0.005951 | 6.985 | 0.015058 | 0.0014826 | 0.00185 | -0.0084637 | -0.00044443 | -0.0036011 | 0.0037278 | 0.013751 | 0.0061544 | -0.01154 | 0.02788 | -0.0035056 | -0.054932 | -0.032043 | 0.009155 | -0.054932 | 0.050354 | -0.027466 | -0.022888 | -0.068665 | 0.032043 | -0.022888 | -0.009155 | 0.064087 | 0 | 0.09613 | 121.8658 | -0.15106 | -0.17395 | 121.907 | 121.8338 | 121.8292 | -0.032043 | -0.036621 | 121.8338 | -0.086976 | -0.12817 | 121.9208 | 121.9528 | 121.8567 | 0.11902 | 0.022888 | 0.041199 | -0.064087 | 0.086975 | 0.013733 | -0.041198 | 0.054931 | 121.8246 | 121.8887 | -0.10986 | -0.14191 | 121.8018 | 121.8475 | 121.8018 | 121.788
3177.3906 | 122.0123 | -121.8384 | 0.14191 | -0.024567 | 6.9829 | 0.014204 | 0.0027642 | -0.0047724 | -0.010386 | -0.0042896 | -0.0066527 | 0.0028732 | 0.012469 | -0.00068137 | -0.013035 | 0.028094 | -0.002651 | -0.059509 | -0.027466 | 0.022888 | -0.045776 | 0.050354 | -0.032043 | -0.036621 | -0.082397 | 0.050354 | -0.032043 | -0.027466 | 0.045776 | -0.032043 | 0.091553 | 121.8613 | -0.16937 | -0.18768 | 121.8887 | 121.8018 | 121.8063 | -0.059509 | -0.054931 | 121.8063 | -0.091553 | -0.16937 | 121.8842 | 121.9299 | 121.8063 | 0.1236 | 0 | 0.027466 | -0.068664 | 0.077819 | 0.004577 | -0.050354 | 0.082397 | 121.8109 | 121.8887 | -0.11902 | -0.17395 | 121.7926 | 121.8109 | 121.7789 | 121.756
3179.125 | 122.1451 | -121.8155 | 0.07782 | -0.016937 | 6.9846 | 0.015272 | -0.00022639 | 0.00014097 | -0.0097455 | -0.0047168 | -0.0066527 | 0.0011642 | 0.012683 | 0.0093588 | -0.010258 | 0.026385 | -0.0030784 | 0.004578 | -0.086975 | 0.064087 | 0.073242 | 0.21057 | 0.11444 | 0.091553 | 0.073242 | 0.009155 | 0 | 0.086975 | 0.17853 | 0.11902 | 0.17853 | 121.8796 | -0.16479 | -0.004578 | 122.0261 | 121.907 | 121.9299 | 0.027466 | 0.050354 | 121.8155 | -0.068665 | 0.009155 | 121.994 | 121.994 | 121.9345 | 0.17853 | 0.11902 | 0.14648 | 0.009155 | 0.17853 | 0.086975 | -0.15106 | 0.009155 | 121.7285 | 121.8246 | -0.013733 | -0.07782 | 121.8887 | 121.9025 | 121.8201 | 121.8887
3180.875 | 122.1313 | -121.7926 | 0.082397 | -0.009308 | 6.985 | 0.017622 | 0.0014826 | 0.00035457 | -0.011454 | -0.005144 | 0.0025025 | 0.0020188 | 0.013965 | 0.013204 | -0.0064129 | 0.028948 | -0.0054282 | 0.027466 | -0.10071 | 0.073242 | 0.082397 | 0.21057 | 0.050354 | 0.073242 | 0.086975 | 0.009155 | -0.004578 | 0.10071 | 0.17395 | 0.086975 | 0.18768 | 121.8658 | -0.18311 | 0 | 122.0032 | 121.8658 | 121.843 | 0 | -0.022888 | 121.788 | -0.073242 | 0.018311 | 121.9666 | 121.9803 | 121.8796 | 0.19226 | 0.091553 | 0.13733 | 0.009155 | 0.17853 | 0.10529 | -0.17395 | 0.013733 | 121.6919 | 121.8018 | -0.009155 | -0.086975 | 121.875 | 121.8933 | 121.8201 | 121.8796
3182.5625 | 122.168 | -121.8109 | 0.07782 | -0.016937 | 6.9818 | 0.015699 | -0.0012946 | -0.00092703 | -0.0076093 | -0.0038622 | -0.0066527 | 0.002446 | 0.01311 | 0.01769 | -0.011326 | 0.029375 | -0.003292 | 0.013733 | -0.073242 | 0.041199 | 0.082397 | 0.21515 | 0.10071 | 0.086975 | 0.10071 | 0 | 0.009155 | 0.082397 | 0.19684 | 0.12817 | 0.18768 | 121.8521 | -0.15106 | 0.004577 | 122.0261 | 121.8979 | 121.9116 | 0.045776 | 0.059509 | 121.8201 | -0.07782 | 0.004577 | 122.0078 | 121.9986 | 121.9391 | 0.17853 | 0.11902 | 0.17395 | 0.041198 | 0.18768 | 0.073242 | -0.11444 | -0.009155 | 121.7377 | 121.8109 | -0.036621 | -0.068665 | 121.8933 | 121.8933 | 121.8246 | 121.9116
3184.2969 | 122.0215 | -121.8796 | 0.13275 | -0.009308 | 6.985 | 0.016126 | 0.004046 | 0.0014228 | -0.012095 | -0.0042896 | -0.0036011 | 0.0028732 | 0.01546 | 0.006368 | -0.01389 | 0.028094 | -0.002651 | -0.032043 | -0.064087 | 0.009155 | -0.036621 | 0.091553 | 0 | 0 | -0.059509 | 0.050354 | -0.022888 | -0.032043 | 0.054932 | -0.009155 | 0.082397 | 121.8887 | -0.19684 | -0.16937 | 121.9711 | 121.8796 | 121.8796 | -0.009155 | -0.009155 | 121.8567 | -0.082397 | -0.16479 | 121.9345 | 121.962 | 121.8704 | 0.10528 | 0.013733 | 0.082398 | -0.045776 | 0.07782 | -0.009155 | -0.073242 | 0.073242 | 121.8155 | 121.9299 | -0.1236 | -0.15564 | 121.843 | 121.8475 | 121.8475 | 121.8201
3185.9844 | 122.1542 | -121.8201 | 0.07782 | -0.024567 | 6.9829 | 0.015913 | 0.002337 | 0.0046272 | -0.0080365 | -0.0025806 | 0.0025025 | 0.004155 | 0.013537 | 0.014699 | -0.0081219 | 0.028307 | -0.0045736 | 0.032043 | -0.064087 | 0.045776 | 0.073242 | 0.18768 | 0.054932 | 0.064087 | 0.086975 | 0.009155 | 0.022888 | 0.10986 | 0.17395 | 0.082397 | 0.18768 | 121.8658 | -0.14191 | -0.004578 | 122.0078 | 121.8842 | 121.875 | 0.018311 | 0.009156 | 121.843 | -0.068665 | 0.032043 | 121.994 | 122.0078 | 121.9025 | 0.16479 | 0.059509 | 0.14191 | 0.027466 | 0.15106 | 0.086975 | -0.10986 | -0.013733 | 121.756 | 121.8292 | -0.032044 | -0.054932 | 121.8933 | 121.9299 | 121.8521 | 121.907
3187.7344 | 122.0718 | -121.8704 | 0.10529 | -0.0016785 | 6.9836 | 0.016767 | 0.0031916 | 0.003559 | -0.0093183 | -0.0015124 | -0.00054933 | 0.0039414 | 0.016101 | 0.011922 | -0.0096173 | 0.029589 | -0.0020102 | -0.022888 | -0.045776 | 0.018311 | 0 | 0.10529 | 0.004578 | 0.022888 | 0 | 0.045776 | -0.004578 | 0.027466 | 0.086975 | 0.036621 | 0.13733 | 121.8887 | -0.15106 | -0.10529 | 121.9757 | 121.8933 | 121.875 | 0.004577 | -0.013733 | 121.8658 | -0.05951 | -0.07782 | 121.9574 | 122.0078 | 121.907 | 0.14191 | 0.041199 | 0.086975 | -0.018311 | 0.091553 | 0.032044 | -0.064087 | 0.050354 | 121.8246 | 121.9162 | -0.086975 | -0.10986 | 121.8704 | 121.8979 | 121.8475 | 121.8704
3189.4844 | 122.1268 | -121.8567 | 0.09613 | -0.009308 | 6.9821 | 0.016126 | -0.0015082 | 0.0012092 | -0.0082501 | -0.0012988 | -0.00054933 | 0.0011642 | 0.013324 | 0.011922 | -0.010899 | 0.028307 | -0.0020102 | -0.036621 | -0.050354 | 0.027466 | 0.018311 | 0.13275 | 0.022888 | 0.027466 | -0.018311 | 0.018311 | 0 | 0.050354 | 0.10529 | 0.054932 | 0.15106 | 121.8842 | -0.14648 | -0.077819 | 121.9894 | 121.8842 | 121.8796 | 0 | -0.004578 | 121.8567 | -0.077819 | -0.045776 | 121.962 | 122.0078 | 121.9116 | 0.15106 | 0.054932 | 0.10529 | -0.009155 | 0.10529 | 0.050354 | -0.07782 | 0.018311 | 121.8063 | 121.875 | -0.068664 | -0.09613 | 121.875 | 121.907 | 121.8201 | 121.8384
3191.1719 | 122.1359 | -121.8704 | 0.10071 | -0.009308 | 6.9848 | 0.015913 | 0.0034052 | 0.00014097 | -0.0073957 | -0.0025806 | -0.00054933 | 0.0037278 | 0.013537 | 0.0033774 | -0.0066265 | 0.028521 | -0.00072839 | -0.041199 | -0.036621 | 0.022888 | -0.018311 | 0.073242 | -0.032043 | -0.013733 | -0.009155 | 0.027466 | 0.013733 | 0.064087 | 0.11444 | 0.045776 | 0.15106 | 121.8933 | -0.13733 | -0.11902 | 121.9437 | 121.8567 | 121.8384 | -0.036621 | -0.054931 | 121.8842 | -0.073242 | -0.036621 | 121.9849 | 122.0215 | 121.9162 | 0.13733 | 0.032043 | 0.050354 | -0.041199 | 0.10071 | 0.050354 | -0.059509 | 0.013733 | 121.8338 | 121.8979 | -0.07782 | -0.086975 | 121.8521 | 121.9345 | 121.8292 | 121.8613
3192.9062 | 122.1497 | -121.8338 | 0.091553 | -0.0016785 | 6.9829 | 0.016981 | 0.0016962 | 0.00099557 | -0.0063275 | -0.003435 | -0.00054933 | 0.0011642 | 0.012469 | 0.006368 | -0.0079083 | 0.032152 | -0.0054282 | 0.013733 | -0.064087 | 0.073242 | 0.07782 | 0.20142 | 0.059509 | 0.059509 | 0.07782 | 0 | 0.027466 | 0.086975 | 0.15564 | 0.09613 | 0.16479 | 121.907 | -0.15564 | -0.013733 | 122.0352 | 121.8933 | 121.8933 | -0.013733 | -0.013733 | 121.8613 | -0.091553 | -0.004578 | 121.9894 | 121.9986 | 121.9299 | 0.13733 | 0.068664 | 0.12817 | 0.004578 | 0.12817 | 0.059509 | -0.13733 | -0.027466 | 121.7697 | 121.8338 | -0.018311 | -0.064087 | 121.9116 | 121.9208 | 121.8475 | 121.9116
3194.6562 | 122.0718 | -121.907 | 0.11444 | -0.009308 | 6.9857 | 0.015913 | 0.0034052 | 0.0012092 | -0.0078229 | -0.00044443 | -0.00054933 | 0.0054368 | 0.013537 | 0.0055136 | -0.01154 | 0.02788 | -0.00436 | -0.022888 | -0.050354 | 0.013733 | -0.027466 | 0.10071 | -0.018311 | -0.027466 | -0.054932 | 0.041199 | -0.004578 | -0.013733 | 0.036621 | -0.041199 | 0.086975 | 121.9208 | -0.16479 | -0.14191 | 122.0078 | 121.8796 | 121.8887 | -0.041199 | -0.032044 | 121.9025 | -0.073242 | -0.12817 | 121.9437 | 121.994 | 121.8658 | 0.091553 | -0.036621 | 0.086975 | -0.041199 | 0.041199 | -0.009155 | -0.064087 | 0.045777 | 121.8567 | 121.9482 | -0.10071 | -0.11902 | 121.8796 | 121.8933 | 121.8842 | 121.8521
3196.3438 | 122.0673 | -121.9162 | 0.11444 | 0.005951 | 6.985 | 0.013136 | 0.0019098 | 0.00185 | -0.010386 | -0.00065803 | -0.0066527 | 0.005223 | 0.014178 | 0.011495 | -0.013463 | 0.027666 | -0.0030784 | -0.059509 | -0.045776 | 0.009155 | -0.073242 | 0.054932 | -0.013733 | -0.032043 | -0.07782 | 0.036621 | -0.018311 | -0.027466 | 0.054932 | -0.004578 | 0.086975 | 121.9254 | -0.16022 | -0.18768 | 121.9711 | 121.8842 | 121.9025 | -0.041198 | -0.022888 | 121.8979 | -0.07782 | -0.14191 | 121.9711 | 122.0032 | 121.9116 | 0.10529 | 0.013733 | 0.045777 | -0.082397 | 0.073243 | -0.009155 | -0.054931 | 0.054932 | 121.8704 | 121.9528 | -0.10529 | -0.13275 | 121.843 | 121.8887 | 121.8567 | 121.8384
3198.0312 | 122.1085 | -121.9208 | 0.10529 | -0.024567 | 6.9825 | 0.01399 | 0.0019098 | 0.003559 | -0.0086773 | -0.0047168 | -0.00054933 | 0.0054368 | 0.013537 | 0.001882 | -0.012608 | 0.027239 | -0.0064962 | -0.059509 | -0.045776 | -0.009155 | -0.068665 | 0.050354 | -0.004578 | -0.018311 | -0.086975 | 0.050354 | -0.027466 | -0.013733 | 0.054932 | 0.004578 | 0.086975 | 121.9116 | -0.15106 | -0.17395 | 121.9711 | 121.9025 | 121.9162 | -0.009156 | 0.004577 | 121.8933 | -0.054932 | -0.11902 | 121.9757 | 122.0078 | 121.9254 | 0.11444 | 0.032044 | 0.059509 | -0.05951 | 0.082398 | 0.013733 | -0.036621 | 0.07782 | 121.875 | 121.9711 | -0.11444 | -0.13275 | 121.8521 | 121.907 | 121.8613 | 121.8338
3199.7812 | 122.1909 | -121.8658 | 0.10071 | -0.0016785 | 6.9842 | 0.017195 | 0.00084161 | 0.0014228 | -0.0091047 | -0.0030078 | -0.0036011 | 0.0037278 | 0.014605 | 0.011709 | -0.0055585 | 0.028307 | -0.0035056 | 0.009155 | -0.073242 | 0.041199 | 0.050354 | 0.17395 | 0.050354 | 0.045776 | 0.054932 | 0.018311 | 0.013733 | 0.10529 | 0.15564 | 0.10529 | 0.19684 | 121.907 | -0.17395 | -0.050354 | 122.0398 | 121.9116 | 121.9162 | 0.004577 | 0.009155 | 121.8796 | -0.082397 | 0.004578 | 122.0215 | 122.0627 | 121.9711 | 0.18311 | 0.091553 | 0.13275 | 0.009155 | 0.14191 | 0.091553 | -0.11444 | 0.004578 | 121.7926 | 121.8842 | -0.059509 | -0.086975 | 121.9162 | 121.9711 | 121.875 | 121.9208
3201.5312 | 122.2046 | -121.8613 | 0.091553 | -0.0016785 | 6.9829 | 0.013136 | 0.00062801 | 0.0014228 | -0.0106 | -0.002367 | -0.0066527 | 0.0015914 | 0.015246 | 0.012136 | -0.013463 | 0.026812 | -0.002651 | 0.013733 | -0.073242 | 0.045776 | 0.082397 | 0.23346 | 0.11444 | 0.11902 | 0.12817 | -0.009155 | 0.018311 | 0.10071 | 0.17395 | 0.13275 | 0.17853 | 121.907 | -0.16479 | -0.009156 | 122.0947 | 121.9803 | 121.9757 | 0.073243 | 0.068665 | 121.8796 | -0.10071 | 0.009155 | 122.0352 | 122.0398 | 121.994 | 0.16022 | 0.11444 | 0.18768 | 0.036621 | 0.15564 | 0.082397 | -0.11902 | -0.027466 | 121.788 | 121.8521 | -0.045777 | -0.073242 | 121.9437 | 121.962 | 121.875 | 121.9894
3203.2656 | 122.113 | -121.9116 | 0.12817 | -0.016937 | 6.9842 | 0.013563 | 0.0016962 | 0.00014097 | -0.0084637 | -0.003435 | 0.0025025 | 0.0030868 | 0.011401 | 0.010854 | -0.011326 | 0.027025 | -0.0017966 | -0.045776 | -0.050354 | 0.004578 | -0.054932 | 0.064087 | -0.013733 | -0.013733 | -0.073242 | 0.027466 | -0.022888 | -0.009155 | 0.082397 | -0.004578 | 0.10529 | 121.9162 | -0.17853 | -0.18311 | 121.9757 | 121.8979 | 121.8979 | -0.018311 | -0.018311 | 121.8887 | -0.10071 | -0.13733 | 121.994 | 122.0169 | 121.907 | 0.12817 | 0.01831 | 0.059509 | -0.05951 | 0.10528 | 0.013733 | -0.054932 | 0.050354 | 121.8613 | 121.9391 | -0.1236 | -0.15106 | 121.8567 | 121.9025 | 121.8658 | 121.8384
3204.9688 | 122.2092 | -121.8567 | 0.10071 | -0.009308 | 6.9838 | 0.018049 | 0.002337 | 0.0014228 | -0.0080365 | -0.0019396 | -0.0097045 | 0.0018052 | 0.01311 | 0.012136 | -0.0081219 | 0.028734 | -0.0020102 | 0.027466 | -0.086975 | 0.064087 | 0.068665 | 0.18768 | 0.059509 | 0.068665 | 0.086975 | -0.009155 | 0.032043 | 0.11902 | 0.16479 | 0.09613 | 0.19226 | 121.9208 | -0.18768 | -0.032043 | 122.0444 | 121.9254 | 121.9162 | 0.004578 | -0.004578 | 121.8887 | -0.10986 | 0.018311 | 122.0215 | 122.049 | 121.9528 | 0.16022 | 0.064087 | 0.1236 | 0.004578 | 0.13275 | 0.086976 | -0.15106 | -0.041198 | 121.7697 | 121.8475 | -0.036621 | -0.068665 | 121.9254 | 121.9757 | 121.8842 | 121.9437
3206.7188 | 122.1725 | -121.8567 | 0.10071 | -0.016937 | 6.9833 | 0.017408 | 0.0019098 | 0.0041998 | -0.0080365 | -0.001726 | -0.00054933 | 0.0030868 | 0.012683 | 0.010213 | -0.010686 | 0.031511 | -0.0039328 | -0.041199 | -0.022888 | 0.018311 | -0.027466 | 0.086975 | -0.027466 | -0.013733 | -0.009155 | 0.013733 | 0 | 0.064087 | 0.10986 | 0.050354 | 0.16479 | 121.875 | -0.1236 | -0.12817 | 121.9437 | 121.843 | 121.8292 | -0.032044 | -0.045777 | 121.8567 | -0.086975 | -0.036621 | 121.9666 | 122.0215 | 121.907 | 0.16479 | 0.050354 | 0.068664 | -0.045777 | 0.10986 | 0.064087 | -0.041199 | 0.013733 | 121.8338 | 121.8704 | -0.082397 | -0.10071 | 121.8292 | 121.9208 | 121.8155 | 121.8475
3208.4062 | 122.1039 | -121.9299 | 0.1236 | -0.009308 | 6.9842 | 0.014204 | 0.00041441 | 0.0016364 | -0.0071821 | -0.00044443 | 0.0025025 | 0.0022324 | 0.012469 | 0.0016684 | -0.011754 | 0.025744 | -0.0024374 | -0.018311 | -0.073242 | 0.036621 | 0.004578 | 0.11902 | 0.027466 | 0.018311 | -0.041199 | 0.036621 | -0.004578 | -0.013733 | 0.064087 | -0.009155 | 0.073242 | 121.9666 | -0.19684 | -0.11902 | 122.049 | 121.9482 | 121.9574 | -0.01831 | -0.009155 | 121.9254 | -0.086975 | -0.13733 | 121.994 | 122.0032 | 121.9208 | 0.07782 | -0.004577 | 0.082398 | -0.032043 | 0.068665 | -0.009155 | -0.10986 | 0.041199 | 121.8567 | 121.9666 | -0.086975 | -0.12817 | 121.9345 | 121.9162 | 121.9116 | 121.8887
3210.1094 | 122.1497 | -121.9208 | 0.10986 | -0.0016785 | 6.9848 | 0.013563 | 0.0014826 | -0.00092703 | -0.0097455 | -0.0015124 | -0.0066527 | 0.0037278 | 0.011401 | 0.0085044 | -0.010045 | 0.027453 | -0.006069 | -0.009155 | -0.036621 | 0.036621 | 0 | 0.13275 | 0.036621 | 0.009155 | 0.009155 | 0.036621 | 0.004578 | 0.032043 | 0.09613 | 0.022888 | 0.11444 | 121.9574 | -0.14648 | -0.10986 | 122.0535 | 121.9299 | 121.9574 | -0.027466 | 0 | 121.9254 | -0.073242 | -0.07782 | 122.0169 | 122.0352 | 121.9437 | 0.10986 | 0.01831 | 0.09613 | -0.036621 | 0.091552 | 0.027465 | -0.073242 | 0.032043 | 121.8842 | 121.9574 | -0.073242 | -0.10529 | 121.9208 | 121.9528 | 121.9116 | 121.9299
3211.8594 | 122.1817 | -121.8979 | 0.086975 | 0.005951 | 6.9859 | 0.016126 | 0.00041441 | 0.0027044 | -0.0082501 | -0.0019396 | 0.0055543 | 0.0022324 | 0.014819 | 0.0048728 | -0.010686 | 0.028307 | -0.0039328 | -0.009155 | -0.082397 | 0.068665 | 0.054932 | 0.19226 | 0.036621 | 0.054932 | 0.050354 | -0.004578 | 0.018311 | 0.045776 | 0.12817 | 0.068665 | 0.15106 | 121.9666 | -0.16937 | -0.032043 | 122.0901 | 121.9528 | 121.9345 | -0.013733 | -0.032044 | 121.9162 | -0.091553 | -0.041199 | 122.0261 | 122.0489 | 121.9666 | 0.13275 | 0.050354 | 0.1236 | -0.013733 | 0.10986 | 0.027465 | -0.15106 | -0.022889 | 121.8155 | 121.8933 | -0.01831 | -0.068664 | 121.9528 | 121.9437 | 121.8887 | 121.9482
3213.6094 | 122.1405 | -121.9299 | 0.13733 | -0.016937 | 6.9853 | 0.01399 | 0.0036188 | 0.0024908 | -0.0076093 | -0.0040758 | -0.00054933 | 0.0039414 | 0.013751 | 0.0012412 | -0.012822 | 0.027666 | -0.0017966 | -0.041199 | -0.027466 | 0 | -0.045776 | 0.045776 | -0.018311 | -0.022888 | -0.086975 | 0.027466 | -0.027466 | -0.013733 | 0.054932 | -0.013733 | 0.091553 | 121.9299 | -0.16479 | -0.18311 | 121.9757 | 121.907 | 121.9116 | -0.022888 | -0.018311 | 121.9025 | -0.10986 | -0.15106 | 121.9849 | 122.0215 | 121.9162 | 0.11902 | 0.013733 | 0.045776 | -0.045776 | 0.082398 | 0.013733 | -0.027466 | 0.054932 | 121.9025 | 121.9574 | -0.13733 | -0.16479 | 121.8842 | 121.9162 | 121.8887 | 121.843
3215.2969 | 122.2183 | -121.9162 | 0.091553 | -0.016937 | 6.9829 | 0.015913 | -0.00065359 | -0.0011408 | -0.0099591 | -0.0019396 | -0.0066527 | 0.0028732 | 0.011188 | 0.0076498 | -0.011754 | 0.029375 | -0.0011558 | 0.009155 | -0.086975 | 0.045776 | 0.073242 | 0.21057 | 0.10529 | 0.10071 | 0.064087 | 0 | 0.018311 | 0.082397 | 0.17853 | 0.10529 | 0.17395 | 121.962 | -0.17853 | -0.018311 | 122.1268 | 122.0169 | 122.0215 | 0.054932 | 0.05951 | 121.9345 | -0.091553 | -0.009156 | 122.0947 | 122.0901 | 122.0215 | 0.15564 | 0.086975 | 0.1648 | 0.027466 | 0.16022 | 0.064086 | -0.13275 | -0.018311 | 121.8292 | 121.9162 | -0.045777 | -0.073242 | 121.9894 | 121.9986 | 121.9254 | 121.9803
3216.9688 | 122.2549 | -121.9025 | 0.07782 | -0.016937 | 6.9848 | 0.019331 | -0.00022639 | 0.003559 | -0.0093183 | -0.0038622 | -0.0036011 | 0.0013778 | 0.011401 | 0.0016684 | -0.0074811 | 0.028948 | -8.7586e-05 | 0.036621 | -0.07782 | 0.045776 | 0.054932 | 0.17395 | 0.059509 | 0.064087 | 0.073242 | 0 | 0.009155 | 0.10071 | 0.15564 | 0.091553 | 0.19684 | 121.9482 | -0.15564 | -0.022888 | 122.0764 | 121.9666 | 121.962 | 0.018311 | 0.013733 | 121.9116 | -0.07782 | 0.022888 | 122.0581 | 122.0993 | 121.994 | 0.18768 | 0.082398 | 0.12817 | 0.009156 | 0.14649 | 0.091553 | -0.1236 | -0.009155 | 121.8246 | 121.9025 | -0.032044 | -0.068665 | 121.9574 | 122.0032 | 121.9391 | 121.9757
3218.7188 | 122.1085 | -121.962 | 0.11902 | -0.009308 | 6.9823 | 0.017835 | 0.0055414 | -0.00028623 | -0.0065411 | -0.0015124 | 0.0025025 | 0.003514 | 0.014605 | 0.0027364 | -0.011326 | 0.028307 | -0.0022238 | -0.054932 | -0.027466 | 0.022888 | -0.073242 | 0.009155 | -0.064087 | -0.073242 | -0.12817 | 0.050354 | -0.013733 | -0.018311 | 0.013733 | -0.050354 | 0.07782 | 121.9849 | -0.14649 | -0.19226 | 121.9711 | 121.8887 | 121.8979 | -0.09613 | -0.086975 | 121.9482 | -0.068665 | -0.13733 | 121.9757 | 122.0398 | 121.9116 | 0.091553 | -0.036621 | -0.013733 | -0.09613 | 0.027466 | -0.004578 | -0.050354 | 0.064087 | 121.9345 | 122.0123 | -0.096131 | -0.13275 | 121.8887 | 121.9437 | 121.907 | 121.8338
3220.4062 | 122.2458 | -121.9391 | 0.09613 | -0.016937 | 6.9838 | 0.01634 | 0.001269 | 0.0029182 | -0.010173 | -0.0019396 | -0.00054933 | 0.0018052 | 0.013324 | 0.007009 | -0.0081219 | 0.029162 | -0.002651 | 0 | -0.073242 | 0.032043 | 0.041199 | 0.16937 | 0.064087 | 0.059509 | 0.073242 | 0.004578 | 0.018311 | 0.09613 | 0.14191 | 0.082397 | 0.20142 | 121.9711 | -0.16937 | -0.054931 | 122.1085 | 121.9986 | 122.0032 | 0.027466 | 0.032044 | 121.9574 | -0.091552 | 0 | 122.081 | 122.1405 | 122.0215 | 0.18311 | 0.064086 | 0.13733 | 0.009156 | 0.1236 | 0.077819 | -0.10529 | -0.013733 | 121.8658 | 121.9437 | -0.064087 | -0.077819 | 121.9803 | 122.0352 | 121.9391 | 122.0123
3222.1562 | 122.2458 | -121.907 | 0.091553 | -0.0016785 | 6.9855 | 0.015058 | 0.00020081 | -0.0013544 | -0.0093183 | -0.0025806 | -0.0036011 | 0.0028732 | 0.012683 | 0.003591 | -0.011754 | 0.030657 | 0.0024758 | 0.022888 | -0.07782 | 0.054932 | 0.073242 | 0.21515 | 0.091553 | 0.10071 | 0.082397 | 0 | 0.022888 | 0.09613 | 0.17853 | 0.13275 | 0.18768 | 121.962 | -0.16937 | -0.018311 | 122.1222 | 122.0078 | 121.9986 | 0.045776 | 0.036621 | 121.9299 | -0.091553 | 0.004577 | 122.0856 | 122.0947 | 122.0398 | 0.16479 | 0.10986 | 0.16022 | 0.01831 | 0.15564 | 0.073242 | -0.13275 | -0.022888 | 121.8292 | 121.907 | -0.036621 | -0.068665 | 121.9803 | 122.0032 | 121.9299 | 121.9894
3223.8438 | 122.2046 | -121.9574 | 0.10529 | 0.005951 | 6.9823 | 0.014204 | 0.0021234 | -0.0011408 | -0.0097455 | -0.0027942 | -0.0036011 | 0.0018052 | 0.01311 | 0.0082906 | -0.0098309 | 0.027666 | -0.0035056 | -0.032043 | -0.073242 | 0.036621 | 0.009155 | 0.14191 | 0.036621 | 0.032043 | -0.013733 | 0.004578 | -0.009155 | 0.036621 | 0.10071 | 0.050354 | 0.14648 | 121.994 | -0.17853 | -0.096131 | 122.0993 | 121.9894 | 121.994 | -0.004578 | 0 | 121.9482 | -0.10071 | -0.068665 | 122.0581 | 122.1039 | 122.0078 | 0.15564 | 0.059509 | 0.10529 | -0.027466 | 0.10986 | 0.045776 | -0.10986 | 0.013733 | 121.8842 | 121.962 | -0.068665 | -0.11444 | 121.9666 | 121.994 | 121.9254 | 121.9437
3225.5938 | 122.2 | -121.9391 | 0.10529 | -0.009308 | 6.9827 | 0.014845 | 0.00084161 | 0.00014097 | -0.0082501 | -0.003435 | -0.00054933 | 0.0033004 | 0.013751 | 0.011709 | -0.0091901 | 0.028307 | -0.003292 | -0.036621 | -0.086975 | 0.041199 | 0.004578 | 0.12817 | 0.018311 | 0.045776 | -0.009155 | 0.013733 | 0.009155 | 0.036621 | 0.10071 | 0.041199 | 0.12817 | 121.9803 | -0.19226 | -0.10071 | 122.0673 | 121.9849 | 121.9574 | 0.004577 | -0.022888 | 121.9482 | -0.091553 | -0.068665 | 122.0398 | 122.0673 | 121.9803 | 0.11902 | 0.032044 | 0.086975 | -0.036621 | 0.091553 | 0.027466 | -0.12817 | 0.004578 | 121.8521 | 121.9528 | -0.064087 | -0.096131 | 121.9437 | 121.9757 | 121.9025 | 121.9299
3227.2656 | 122.1771 | -121.9666 | 0.11902 | -0.0016785 | 6.9853 | 0.014845 | 0.0051142 | 0.0059088 | -0.011668 | -0.002367 | -0.0036011 | 0.0039414 | 0.013751 | 0.007009 | -0.011754 | 0.027666 | -0.0017966 | 0 | -0.054932 | 0.022888 | 0.009155 | 0.10529 | -0.004578 | 0.013733 | 0.013733 | 0.036621 | -0.018311 | 0.018311 | 0.068665 | 0.004578 | 0.1236 | 121.9894 | -0.17395 | -0.10986 | 122.0718 | 121.9803 | 121.962 | -0.009155 | -0.027466 | 121.9482 | -0.082398 | -0.10071 | 122.0352 | 122.0901 | 121.9711 | 0.14191 | 0.022889 | 0.082398 | -0.013733 | 0.086976 | 0.036622 | -0.07782 | 0.054932 | 121.9116 | 122.0032 | -0.096131 | -0.13733 | 121.9757 | 121.9849 | 121.9666 | 121.9803
3229 | 122.2641 | -121.9299 | 0.091553 | -0.016937 | 6.9831 | 0.016767 | 0.00084161 | -0.00071343 | -0.0078229 | -0.0053576 | -0.00054933 | 0.0015914 | 0.012256 | 0.009786 | -0.0081219 | 0.029803 | -8.7586e-05 | 0.027466 | -0.07782 | 0.050354 | 0.068665 | 0.19226 | 0.064087 | 0.064087 | 0.07782 | 0.009155 | 0.013733 | 0.10986 | 0.16022 | 0.10071 | 0.20599 | 121.9803 | -0.16937 | -0.022888 | 122.1222 | 121.994 | 121.994 | 0.013733 | 0.013733 | 121.9437 | -0.082398 | 0.01831 | 122.0901 | 122.1359 | 122.0306 | 0.19226 | 0.086975 | 0.14191 | 0.018311 | 0.14648 | 0.09613 | -0.12817 | -0.004578 | 121.8521 | 121.9391 | -0.041199 | -0.07782 | 121.9986 | 122.0398 | 121.9574 | 122.0078
3230.7656 | 122.2321 | -121.9437 | 0.091553 | -0.009308 | 6.9842 | 0.016767 | 0.0010552 | 0.0024908 | -0.0067547 | -0.0019396 | -0.0036011 | 0.0018052 | 0.013324 | 0.012563 | -0.0079083 | 0.030871 | -0.0047874 | 0.009155 | -0.09613 | 0.059509 | 0.054932 | 0.20142 | 0.041199 | 0.073242 | 0.082397 | 0.013733 | 0.022888 | 0.091553 | 0.13733 | 0.091553 | 0.15564 | 122.0032 | -0.18768 | -0.036621 | 122.1451 | 122.0169 | 121.9849 | 0.013733 | -0.01831 | 121.9666 | -0.07782 | 0 | 122.081 | 122.0993 | 122.0352 | 0.13275 | 0.068665 | 0.14191 | -0.004577 | 0.11444 | 0.068665 | -0.15564 | -0.009155 | 121.8475 | 121.9574 | -0.032044 | -0.068665 | 121.9986 | 122.0352 | 121.9528 | 122.0261
3232.4531 | 122.1909 | -121.9574 | 0.1236 | -0.009308 | 6.9848 | 0.014204 | 0.0010552 | 0.00185 | -0.0080365 | -0.0012988 | -0.0066527 | 0.0037278 | 0.012897 | 0.0048728 | -0.012395 | 0.028094 | -8.7586e-05 | -0.027466 | -0.036621 | 0 | -0.041199 | 0.068665 | -0.009155 | -0.009155 | -0.054932 | 0.027466 | -0.013733 | 0.009155 | 0.082397 | 0 | 0.1236 | 121.9574 | -0.16022 | -0.16479 | 122.0261 | 121.9482 | 121.9482 | -0.009155 | -0.009155 | 121.9437 | -0.09613 | -0.11444 | 122.0398 | 122.081 | 121.9574 | 0.13733 | 0.013733 | 0.068665 | -0.041199 | 0.09613 | 0.022888 | -0.036621 | 0.041199 | 121.9208 | 121.9849 | -0.1236 | -0.13733 | 121.9162 | 121.9666 | 121.9299 | 121.9025
3234.2031 | 122.1497 | -121.9803 | 0.10986 | -0.016937 | 6.9814 | 0.012922 | 0.0014826 | -0.0013544 | -0.011454 | -0.0030078 | -0.00054933 | 0.0028732 | 0.014178 | -0.0030314 | -0.01389 | 0.027666 | 0.00076681 | -0.059509 | -0.013733 | 0.004578 | -0.073242 | 0.032043 | -0.036621 | -0.022888 | -0.086975 | 0.050354 | -0.022888 | -0.045776 | 0.036621 | -0.013733 | 0.09613 | 121.9849 | -0.1236 | -0.18311 | 122.0123 | 121.9574 | 121.9437 | -0.027466 | -0.041199 | 121.9574 | -0.059509 | -0.15564 | 122.0169 | 122.0764 | 121.9666 | 0.11902 | 0.009155 | 0.027465 | -0.07782 | 0.059509 | -0.022888 | -0.018311 | 0.073242 | 121.9666 | 122.0306 | -0.10529 | -0.13275 | 121.907 | 121.9345 | 121.9208 | 121.8933
3235.9531 | 122.2275 | -121.9574 | 0.11444 | -0.0016785 | 6.9801 | 0.014631 | 0.0016962 | 0.0031318 | -0.0099591 | -0.0032214 | -0.0036011 | 0.002446 | 0.013537 | 0.0050864 | -0.012395 | 0.027239 | -0.0030784 | -0.041199 | -0.082397 | 0.036621 | -0.009155 | 0.11444 | 0.009155 | 0.027466 | -0.018311 | 0.022888 | 0.013733 | 0.027466 | 0.10071 | 0.041199 | 0.14648 | 121.994 | -0.19684 | -0.1236 | 122.0718 | 121.9849 | 121.9666 | -0.009155 | -0.027466 | 121.9711 | -0.091553 | -0.086975 | 122.0581 | 122.1039 | 121.9986 | 0.13275 | 0.027466 | 0.07782 | -0.045776 | 0.086975 | 0.013733 | -0.11902 | 0.009155 | 121.875 | 121.9803 | -0.07782 | -0.10071 | 121.9482 | 121.9849 | 121.9162 | 121.9391
3237.7031 | 122.1725 | -122.0078 | 0.13275 | -0.009308 | 6.9844 | 0.015272 | 0.00020081 | 0.0039862 | -0.0082501 | -0.0047168 | 0.0025025 | 0.0022324 | 0.014819 | 0.012777 | -0.011967 | 0.026171 | -0.003292 | -0.068665 | -0.027466 | 0.013733 | -0.068665 | 0.041199 | -0.027466 | -0.027466 | -0.091553 | 0.059509 | -0.032043 | -0.032043 | 0.032043 | -0.022888 | 0.091553 | 122.0215 | -0.16022 | -0.20142 | 122.049 | 121.9803 | 121.9803 | -0.041199 | -0.041199 | 121.9757 | -0.073242 | -0.16479 | 122.0398 | 122.0993 | 121.9849 | 0.1236 | 0.009155 | 0.027466 | -0.082398 | 0.064086 | 0 | -0.041199 | 0.091552 | 121.9803 | 122.0673 | -0.11902 | -0.16479 | 121.9391 | 121.9757 | 121.9391 | 121.9162
3239.3906 | 122.2321 | -121.962 | 0.091553 | -0.016937 | 6.9833 | 0.015913 | -1.2792e-05 | 0.0046272 | -0.0082501 | -0.0036486 | -0.0036011 | 0.0009506 | 0.012042 | 0.0076498 | -0.0085491 | 0.028307 | -0.0052146 | -0.004578 | -0.064087 | 0.054932 | 0.054932 | 0.1831 | 0.045776 | 0.050354 | 0.054932 | -0.004578 | 0.004578 | 0.073242 | 0.12817 | 0.068665 | 0.14191 | 122.0169 | -0.15564 | -0.036621 | 122.1451 | 122.0123 | 122.0078 | -0.004578 | -0.009156 | 121.9666 | -0.096131 | -0.018311 | 122.0901 | 122.1039 | 122.0306 | 0.13733 | 0.064087 | 0.12817 | 0 | 0.1236 | 0.068664 | -0.11902 | -0.009156 | 121.8979 | 121.9574 | -0.036621 | -0.086975 | 122.0169 | 122.0352 | 121.9574 | 122.0169
3241.125 | 122.1542 | -122.0261 | 0.12817 | -0.009308 | 6.9859 | 0.015272 | 0.00084161 | 0.0037726 | -0.0091047 | -0.0032214 | -0.0036011 | 0.0028732 | 0.013537 | 0.0038046 | -0.012822 | 0.025103 | -0.0024374 | -0.054932 | -0.054932 | 0.009155 | -0.054932 | 0.059509 | -0.022888 | -0.018311 | -0.073242 | 0.032043 | -0.013733 | -0.036621 | 0.036621 | -0.018311 | 0.068665 | 122.0352 | -0.18311 | -0.18311 | 122.0856 | 122.0078 | 122.0032 | -0.027466 | -0.032043 | 122.0123 | -0.096131 | -0.1648 | 122.0627 | 122.0947 | 122.0078 | 0.082398 | -0.004578 | 0.050354 | -0.064087 | 0.050354 | -0.022888 | -0.064087 | 0.045776 | 121.9711 | 122.0581 | -0.11902 | -0.14191 | 121.9711 | 121.9894 | 121.9711 | 121.9528
3242.875 | 122.2275 | -121.994 | 0.11444 | -0.016937 | 6.9855 | 0.015486 | 0.0021234 | 0.0022772 | -0.0086773 | -0.002367 | -0.00054933 | 0.005223 | 0.013751 | 0.0057272 | -0.011113 | 0.027025 | -0.0069236 | -0.013733 | -0.032043 | 0.018311 | 0 | 0.11902 | -0.004578 | 0.009155 | 0.009155 | 0.041199 | 0 | 0.027466 | 0.091553 | 0.027466 | 0.13733 | 122.0123 | -0.14648 | -0.11444 | 122.113 | 122.0032 | 121.9894 | -0.009156 | -0.022889 | 121.994 | -0.073242 | -0.086975 | 122.0856 | 122.1313 | 122.0215 | 0.13733 | 0.027466 | 0.10071 | -0.018311 | 0.091553 | 0.027466 | -0.050354 | 0.041199 | 121.962 | 122.0352 | -0.09613 | -0.11444 | 121.994 | 122.0215 | 121.9803 | 122.0032
3244.5625 | 122.2183 | -122.0032 | 0.11444 | -0.016937 | 6.9833 | 0.015058 | 0.00084161 | 0.0031318 | -0.0099591 | -0.0038622 | -0.0066527 | 0.0009506 | 0.013537 | 0.0065816 | -0.012822 | 0.02788 | 0.00012601 | 0.009155 | -0.064087 | 0.041199 | 0.041199 | 0.16479 | 0.045776 | 0.050354 | 0.022888 | 0.018311 | -0.009155 | 0.022888 | 0.10529 | 0.036621 | 0.10529 | 122.0444 | -0.17853 | -0.073242 | 122.168 | 122.0535 | 122.049 | 0.009155 | 0.004577 | 121.994 | -0.09613 | -0.091553 | 122.1085 | 122.1085 | 122.0398 | 0.11444 | 0.045776 | 0.1236 | 0 | 0.11444 | 0.032043 | -0.10529 | 0.027466 | 121.9391 | 122.0215 | -0.073242 | -0.1236 | 122.0444 | 122.0261 | 122.0123 | 122.0261
3246.2969 | 122.2275 | -122.0078 | 0.11902 | -0.009308 | 6.9844 | 0.015058 | 0.0034052 | 0.00185 | -0.0095319 | 0.00019657 | -0.00054933 | 0.0043686 | 0.010974 | 0.0067954 | -0.010045 | 0.028094 | -0.0017966 | -0.009155 | -0.050354 | 0.041199 | -0.004578 | 0.11444 | 0.022888 | 0.022888 | 0.013733 | 0.036621 | 0 | 0.041199 | 0.10071 | 0.036621 | 0.12817 | 122.049 | -0.16937 | -0.1236 | 122.1222 | 122.0306 | 122.0306 | -0.018311 | -0.018311 | 122.0078 | -0.082398 | -0.07782 | 122.1085 | 122.1359 | 122.0444 | 0.12817 | 0.036621 | 0.073242 | -0.045777 | 0.10071 | 0.041199 | -0.091553 | 0.036621 | 121.9574 | 122.0444 | -0.07782 | -0.11902 | 122.0032 | 122.049 | 121.9986 | 122.0215
3248.0312 | 122.2549 | -122.0032 | 0.09613 | -0.009308 | 6.987 | 0.016767 | 0.0014826 | 0.0044134 | -0.0078229 | -0.0030078 | -0.0066527 | 0.0045822 | 0.01311 | 0.01299 | -0.0079083 | 0.029589 | -0.0073508 | -0.045776 | -0.036621 | 0.032043 | -0.050354 | 0.07782 | -0.064087 | -0.018311 | -0.013733 | 0.009155 | -0.009155 | 0.054932 | 0.086975 | 0.022888 | 0.15106 | 122.0352 | -0.13275 | -0.14648 | 122.081 | 121.9849 | 121.9391 | -0.050354 | -0.09613 | 121.994 | -0.086975 | -0.041198 | 122.0901 | 122.1542 | 122.0261 | 0.16022 | 0.032043 | 0.045777 | -0.082397 | 0.09613 | 0.064087 | -0.068664 | 0.01831 | 121.9666 | 122.0123 | -0.064087 | -0.10528 | 121.9528 | 122.0581 | 121.9574 | 121.9894
3249.7188 | 122.2275 | -122.0261 | 0.11444 | -0.009308 | 6.9844 | 0.014204 | 0.0016962 | -7.2628e-05 | -0.0097455 | -0.0047168 | -0.00054933 | 0.0071456 | 0.013324 | 0.0055136 | -0.0098309 | 0.028094 | -0.0028646 | -0.004578 | -0.041199 | 0.032043 | -0.004578 | 0.13733 | 0.018311 | 0.027466 | 0.027466 | 0.036621 | -0.004578 | 0.045776 | 0.10529 | 0.022888 | 0.12817 | 122.0581 | -0.15564 | -0.11902 | 122.1634 | 122.0535 | 122.0444 | -0.004577 | -0.013732 | 122.0215 | -0.07782 | -0.068665 | 122.1313 | 122.1542 | 122.0489 | 0.13275 | 0.027466 | 0.10529 | -0.036621 | 0.10986 | 0.050354 | -0.073242 | 0.041199 | 121.9849 | 122.0627 | -0.082398 | -0.11902 | 122.0215 | 122.0718 | 122.0215 | 122.0535
3251.4531 | 122.2961 | -121.9803 | 0.091553 | 0.005951 | 6.9838 | 0.015699 | 0.00041441 | 0.008686 | -0.0076093 | -0.0012988 | -0.0036011 | 0.0009506 | 0.014819 | 0.0020956 | -0.0074811 | 0.029803 | -0.00436 | 0.022888 | -0.07782 | 0.064087 | 0.059509 | 0.18768 | 0.050354 | 0.082397 | 0.082397 | 0.013733 | 0.027466 | 0.10529 | 0.16022 | 0.09613 | 0.17395 | 122.0444 | -0.16937 | -0.032044 | 122.168 | 122.0627 | 122.0306 | 0.01831 | -0.013733 | 122.0078 | -0.07782 | 0.013733 | 122.1405 | 122.1542 | 122.0764 | 0.14648 | 0.068664 | 0.1236 | -0.004578 | 0.13275 | 0.07782 | -0.14191 | -0.013733 | 121.9025 | 121.994 | -0.027466 | -0.064087 | 122.0398 | 122.0856 | 122.0032 | 122.0627
3253.1875 | 122.3099 | -121.9803 | 0.086975 | -0.009308 | 6.9831 | 0.018476 | 0.0019098 | 0.0014228 | -0.0088911 | -0.0045032 | -0.0036011 | 0.002446 | 0.011828 | 0.006368 | -0.0079083 | 0.031298 | -0.0013694 | 0.036621 | -0.064087 | 0.07782 | 0.068665 | 0.19684 | 0.059509 | 0.068665 | 0.09613 | -0.004578 | 0.018311 | 0.10529 | 0.16479 | 0.09613 | 0.19684 | 122.0581 | -0.15106 | -0.01831 | 122.1771 | 122.049 | 122.0398 | -0.009155 | -0.018311 | 121.9986 | -0.091553 | 0.018311 | 122.1451 | 122.1771 | 122.0764 | 0.17853 | 0.077819 | 0.11902 | -0.009155 | 0.14648 | 0.086975 | -0.14191 | -0.022889 | 121.9162 | 121.9757 | -0.009155 | -0.068664 | 122.049 | 122.0856 | 122.0169 | 122.0764
3254.875 | 122.2641 | -121.9757 | 0.10071 | 0.005951 | 6.9833 | 0.015272 | -0.00022639 | -0.00028623 | -0.0069683 | -0.0036486 | -0.0066527 | 0.0018052 | 0.014819 | 0.010854 | -0.012395 | 0.030016 | -0.00051479 | -0.032043 | -0.068665 | 0.054932 | 0.018311 | 0.14648 | 0.032043 | 0.036621 | 0.009155 | 0.009155 | 0.013733 | 0.032043 | 0.10986 | 0.050354 | 0.12817 | 122.0306 | -0.16937 | -0.082397 | 122.1222 | 122.0123 | 122.0078 | -0.018311 | -0.022889 | 121.9894 | -0.091553 | -0.068665 | 122.0856 | 122.1039 | 122.0261 | 0.11444 | 0.036621 | 0.091552 | -0.036621 | 0.09613 | 0.01831 | -0.1236 | -0.004578 | 121.907 | 121.9849 | -0.045776 | -0.086975 | 121.994 | 122.0078 | 121.9437 | 121.9849
3256.625 | 122.2092 | -122.0306 | 0.12817 | -0.0016785 | 6.9848 | 0.013777 | 0.0025506 | 0.00078177 | -0.010814 | -0.003435 | -0.0036011 | 0.0022324 | 0.012683 | 0.0061544 | -0.012822 | 0.029589 | -0.00051479 | -0.050354 | -0.032043 | -0.009155 | -0.059509 | 0.050354 | -0.041199 | -0.013733 | -0.10071 | 0.036621 | -0.018311 | -0.027466 | 0.045776 | -0.018311 | 0.086975 | 122.0215 | -0.16022 | -0.18768 | 122.081 | 122.0169 | 121.9894 | -0.004578 | -0.032044 | 122.0123 | -0.091553 | -0.15564 | 122.0764 | 122.1176 | 122.0123 | 0.10529 | 0 | 0.059509 | -0.050354 | 0.064087 | -0.009155 | -0.022888 | 0.054932 | 121.9986 | 122.0673 | -0.13733 | -0.14649 | 121.9711 | 122.0032 | 121.9803 | 121.9299
3258.375 | 122.2458 | -122.0032 | 0.10071 | -0.009308 | 6.9857 | 0.013563 | 0.0021234 | -0.00028623 | -0.0088911 | -0.0010852 | -0.00054933 | 0.0030868 | 0.012469 | 0.008077 | -0.012395 | 0.029162 | -0.0011558 | -0.027466 | -0.041199 | 0.018311 | -0.032043 | 0.07782 | -0.004578 | -0.009155 | -0.032043 | 0.045776 | -0.013733 | 0.009155 | 0.082397 | 0.032043 | 0.1236 | 122.0215 | -0.14191 | -0.13275 | 122.081 | 121.994 | 121.9986 | -0.027466 | -0.022889 | 121.9894 | -0.054932 | -0.091553 | 122.0856 | 122.1268 | 122.0352 | 0.13733 | 0.045776 | 0.059509 | -0.050354 | 0.09613 | 0.022888 | -0.05951 | 0.059509 | 121.962 | 122.049 | -0.082397 | -0.11444 | 121.9711 | 122.0123 | 121.9757 | 121.9711
3260.1406 | 122.2046 | -122.0306 | 0.10986 | -0.016937 | 6.9803 | 0.015699 | -0.00022639 | -0.00028623 | -0.010173 | -0.0021532 | -0.0036011 | 0.0018052 | 0.015033 | 0.0042318 | -0.013035 | 0.026171 | 0.00012601 | -0.013733 | -0.059509 | 0.027466 | -0.004578 | 0.12817 | 0.018311 | 0.018311 | -0.041199 | 0.036621 | -0.018311 | -0.013733 | 0.064087 | 0.018311 | 0.073242 | 122.0581 | -0.16937 | -0.11444 | 122.1588 | 122.049 | 122.049 | -0.009155 | -0.009155 | 122.0123 | -0.073242 | -0.1236 | 122.0947 | 122.1039 | 122.049 | 0.091553 | 0.036622 | 0.10071 | -0.032044 | 0.082398 | 0.004578 | -0.086975 | 0.054932 | 121.9711 | 122.0673 | -0.082397 | -0.12817 | 122.0261 | 122.0169 | 122.0169 | 121.9894
3261.8906 | 122.2916 | -122.0261 | 0.10071 | -0.016937 | 6.9829 | 0.017408 | 0.00084161 | -0.0028498 | -0.0076093 | -0.0032214 | -0.0036011 | 0.0020188 | 0.012256 | 0.006368 | -0.0087629 | 0.028948 | -0.0024374 | 0 | -0.086975 | 0.054932 | 0.054932 | 0.17853 | 0.041199 | 0.07782 | 0.059509 | -0.022888 | 0.009155 | 0.07782 | 0.1236 | 0.073242 | 0.14648 | 122.081 | -0.18768 | -0.045776 | 122.2046 | 122.1039 | 122.0673 | 0.022888 | -0.013733 | 122.0352 | -0.1236 | -0.022888 | 122.1497 | 122.1725 | 122.0993 | 0.13733 | 0.064087 | 0.1236 | 0 | 0.11444 | 0.068665 | -0.14191 | -0.032043 | 121.9391 | 122.0032 | -0.045776 | -0.091553 | 122.081 | 122.1039 | 122.0261 | 122.0856
3263.5781 | 122.2321 | -122.0261 | 0.13733 | -0.009308 | 6.985 | 0.015272 | 0.0016962 | 0.0050544 | -0.0082501 | -0.0025806 | -0.0036011 | 0.004155 | 0.012897 | 0.008077 | -0.014103 | 0.027666 | -0.0024374 | -0.041199 | -0.032043 | 0.004578 | -0.064087 | 0.054932 | -0.027466 | -0.009155 | -0.073242 | 0.054932 | -0.027466 | -0.027466 | 0.041199 | -0.013733 | 0.10071 | 122.0306 | -0.16937 | -0.20142 | 122.081 | 122.0169 | 121.9986 | -0.013733 | -0.032044 | 121.9986 | -0.082397 | -0.16479 | 122.0673 | 122.1268 | 122.0123 | 0.12817 | 0.013733 | 0.050354 | -0.068665 | 0.068665 | 0 | -0.036621 | 0.082398 | 121.994 | 122.081 | -0.13275 | -0.16479 | 121.962 | 121.9986 | 121.9849 | 121.9528
3265.3281 | 122.2412 | -122.049 | 0.11902 | -0.009308 | 6.9838 | 0.012495 | 0.0014826 | -0.0039178 | -0.0078229 | 0.00062377 | -0.0036011 | 0.005864 | 0.015674 | 0.014699 | -0.010899 | 0.027453 | -0.0020102 | -0.050354 | -0.027466 | 0 | -0.059509 | 0.041199 | -0.022888 | -0.027466 | -0.082397 | 0.050354 | -0.027466 | -0.013733 | 0.059509 | -0.013733 | 0.082397 | 122.049 | -0.14649 | -0.17853 | 122.0901 | 122.0215 | 122.0261 | -0.027466 | -0.022888 | 122.0215 | -0.068665 | -0.13275 | 122.1085 | 122.1313 | 122.0352 | 0.10986 | 0.013733 | 0.041199 | -0.059509 | 0.086975 | 0.013733 | -0.027466 | 0.07782 | 122.0215 | 122.0993 | -0.11902 | -0.14649 | 121.9894 | 122.0352 | 121.9986 | 121.9666
3267.0156 | 122.3328 | -121.9986 | 0.09613 | -0.024567 | 6.9818 | 0.013563 | -1.2792e-05 | -0.0039178 | -0.0073957 | -0.0015124 | -0.0097045 | 0.0015914 | 0.014392 | 0.01769 | -0.011113 | 0.029375 | 0.00055321 | -0.018311 | -0.073242 | 0.045776 | 0.032043 | 0.16022 | 0.064087 | 0.068665 | 0.050354 | 0.004578 | 0.004578 | 0.073242 | 0.16479 | 0.1236 | 0.1831 | 122.0444 | -0.16937 | -0.064087 | 122.1588 | 122.0673 | 122.0627 | 0.022889 | 0.018311 | 122.0032 | -0.091552 | -0.022888 | 122.1634 | 122.1817 | 122.1222 | 0.17853 | 0.11902 | 0.11444 | -0.013733 | 0.16022 | 0.068664 | -0.11902 | 0 | 121.9254 | 122.0032 | -0.050354 | -0.091552 | 122.0306 | 122.0718 | 121.9803 | 122.049
3268.75 | 122.2778 | -122.0398 | 0.10071 | -0.009308 | 6.9842 | 0.013349 | 0.0014826 | 0.00185 | -0.0093183 | -0.0038622 | -0.0066527 | 0.0022324 | 0.012042 | 0.0089316 | -0.012608 | 0.026385 | -0.0028646 | 0.018311 | -0.07782 | 0.036621 | 0.050354 | 0.18768 | 0.086975 | 0.082397 | 0.032043 | 0.009155 | 0 | 0.032043 | 0.10071 | 0.050354 | 0.13733 | 122.0764 | -0.17853 | -0.050354 | 122.2275 | 122.1222 | 122.1268 | 0.045776 | 0.050354 | 122.0398 | -0.091553 | -0.068665 | 122.1405 | 122.1771 | 122.0901 | 0.13733 | 0.050354 | 0.15106 | 0.013733 | 0.10071 | 0.032043 | -0.11444 | 0.009155 | 121.962 | 122.049 | -0.064087 | -0.10071 | 122.0901 | 122.0718 | 122.0581 | 122.0718
3270.5156 | 122.2046 | -122.0764 | 0.12817 | -0.024567 | 6.9836 | 0.013777 | 0.0027642 | 0.00014097 | -0.0093183 | -0.0021532 | -0.0066527 | 0.0047958 | 0.014605 | 0.00038663 | -0.010686 | 0.029162 | -0.0069236 | -0.068665 | -0.036621 | 0.022888 | -0.059509 | 0.050354 | -0.022888 | -0.013733 | -0.068665 | 0.045776 | -0.009155 | -0.050354 | 0.045776 | -0.013733 | 0.054932 | 122.0993 | -0.1648 | -0.18768 | 122.1268 | 122.0627 | 122.0535 | -0.036621 | -0.045776 | 122.0673 | -0.082398 | -0.17853 | 122.1222 | 122.1313 | 122.0627 | 0.064087 | -0.004578 | 0.027466 | -0.082397 | 0.054931 | -0.041199 | -0.059509 | 0.054931 | 122.0398 | 122.1222 | -0.10529 | -0.13733 | 122.0169 | 122.0261 | 122.0078 | 122.0078
3272.2656 | 122.3007 | -122.0398 | 0.09613 | -0.016937 | 6.9827 | 0.015058 | 0.0016962 | 0.00056817 | -0.0097455 | -0.0019396 | -0.0066527 | -0.0001174 | 0.01311 | 0.0038046 | -0.0091901 | 0.03023 | -0.001583 | -0.032043 | -0.064087 | 0.036621 | 0.009155 | 0.13275 | 0.013733 | 0.041199 | -0.009155 | -0.009155 | 0 | 0.032043 | 0.09613 | 0.036621 | 0.1236 | 122.0764 | -0.16022 | -0.086975 | 122.1725 | 122.081 | 122.0535 | 0.004578 | -0.022888 | 122.0398 | -0.10528 | -0.064087 | 122.1359 | 122.1634 | 122.0764 | 0.1236 | 0.036621 | 0.09613 | -0.027466 | 0.09613 | 0.032043 | -0.10071 | -0.009155 | 121.9757 | 122.0306 | -0.059509 | -0.09613 | 122.049 | 122.0718 | 122.0078 | 122.0306
3273.9375 | 122.2321 | -122.0627 | 0.11444 | -0.009308 | 6.9844 | 0.016126 | 0.0025506 | 0.0059088 | -0.0099591 | -0.0036486 | -0.0097045 | 0.005223 | 0.014605 | 0.0053 | -0.011113 | 0.029162 | -0.0030784 | -0.009155 | -0.064087 | 0.018311 | -0.009155 | 0.073242 | -0.022888 | 0 | -0.018311 | 0.022888 | -0.027466 | 0.013733 | 0.036621 | -0.036621 | 0.07782 | 122.081 | -0.17853 | -0.1236 | 122.1359 | 122.0627 | 122.0398 | -0.018311 | -0.041199 | 122.0352 | -0.091553 | -0.10071 | 122.0993 | 122.1405 | 122.0261 | 0.10529 | -0.009155 | 0.054931 | -0.027466 | 0.064087 | 0.041199 | -0.082398 | 0.050354 | 121.9986 | 122.0856 | -0.09613 | -0.14191 | 122.0535 | 122.0764 | 122.0535 | 122.0444
3275.6719 | 122.3053 | -122.0398 | 0.07782 | -0.009308 | 6.985 | 0.014204 | 0.0034052 | 0.0024908 | -0.0095319 | -0.0038622 | -0.00054933 | 0.0022324 | 0.013965 | 0.0050864 | -0.010258 | 0.029589 | -0.0030784 | -0.009155 | -0.073242 | 0.045776 | 0.050354 | 0.16937 | 0.041199 | 0.036621 | 0.054932 | 0.013733 | 0.004578 | 0.054932 | 0.11444 | 0.054932 | 0.16022 | 122.0856 | -0.15106 | -0.027466 | 122.2092 | 122.0764 | 122.081 | -0.009155 | -0.004577 | 122.0444 | -0.064087 | -0.022888 | 122.1542 | 122.2 | 122.0947 | 0.15564 | 0.050354 | 0.1236 | 0.004578 | 0.10986 | 0.050354 | -0.11902 | 0.009155 | 121.9666 | 122.0535 | -0.032044 | -0.073242 | 122.0901 | 122.0947 | 122.0306 | 122.0947
3277.375 | 122.3511 | -122.0215 | 0.091553 | -0.024567 | 6.9838 | 0.012281 | 0.0016962 | 0.0041998 | -0.0080365 | -0.001726 | -0.0066527 | 0.0037278 | 0.014605 | 0.0038046 | -0.0053449 | 0.029162 | -0.005001 | -0.032043 | -0.041199 | 0.018311 | 0 | 0.10986 | -0.004578 | 0.004578 | 0.032043 | 0.018311 | -0.004578 | 0.086975 | 0.13733 | 0.068665 | 0.1831 | 122.0398 | -0.13275 | -0.091553 | 122.1313 | 122.0261 | 122.0169 | -0.013733 | -0.022889 | 122.0169 | -0.073242 | -0.004578 | 122.1588 | 122.2046 | 122.0901 | 0.18768 | 0.073243 | 0.091552 | -0.018311 | 0.14191 | 0.091553 | -0.05951 | 0.022889 | 121.9803 | 122.0398 | -0.073242 | -0.096131 | 122.0215 | 122.1085 | 121.9894 | 122.0535
3279.0625 | 122.2366 | -122.081 | 0.11902 | -0.024567 | 6.984 | 0.013777 | 0.001269 | 0.0031318 | -0.0073957 | -0.0040758 | -0.0066527 | 0.0015914 | 0.012897 | -4.0566e-05 | -0.014317 | 0.027453 | -0.003292 | -0.068665 | -0.045776 | 0.004578 | -0.064087 | 0.059509 | -0.032043 | -0.018311 | -0.07782 | 0.045776 | -0.027466 | -0.036621 | 0.032043 | -0.032043 | 0.073242 | 122.0856 | -0.16479 | -0.18311 | 122.1405 | 122.0627 | 122.049 | -0.022889 | -0.036621 | 122.0535 | -0.073243 | -0.15564 | 122.113 | 122.1542 | 122.049 | 0.10071 | -0.004577 | 0.054931 | -0.068665 | 0.059509 | -0.009155 | -0.050354 | 0.073242 | 122.0352 | 122.1268 | -0.11444 | -0.14649 | 122.0169 | 122.0444 | 122.0123 | 122.0032
3280.8281 | 122.3831 | -122.0398 | 0.082397 | -0.016937 | 6.9831 | 0.016554 | 0.00084161 | 0.0014228 | -0.0095319 | -0.0019396 | -0.00054933 | 0.0022324 | 0.012042 | 0.0076498 | -0.010258 | 0.029589 | -0.0030784 | 0.009155 | -0.07782 | 0.045776 | 0.082397 | 0.21515 | 0.091553 | 0.11444 | 0.10071 | 0 | 0.013733 | 0.09613 | 0.16937 | 0.12817 | 0.19226 | 122.0856 | -0.16022 | 0 | 122.2549 | 122.1542 | 122.1313 | 0.068665 | 0.045777 | 122.0535 | -0.082397 | 0.013733 | 122.2092 | 122.2321 | 122.168 | 0.17853 | 0.11444 | 0.16937 | 0.036621 | 0.15564 | 0.082397 | -0.1236 | -0.013733 | 121.962 | 122.0398 | -0.036621 | -0.068664 | 122.1222 | 122.1359 | 122.049 | 122.1405
3282.5938 | 122.319 | -122.0581 | 0.091553 | -0.016937 | 6.9831 | 0.016554 | 0.00062801 | 0.00099557 | -0.0078229 | -0.0030078 | -0.0036011 | 0.0026596 | 0.012042 | 0.0076498 | -0.0081219 | 0.027025 | 0.00033961 | -0.009155 | -0.07782 | 0.041199 | 0.027466 | 0.16479 | 0.036621 | 0.045776 | 0.036621 | 0.004578 | 0 | 0.045776 | 0.11444 | 0.045776 | 0.13733 | 122.0993 | -0.16937 | -0.064087 | 122.2229 | 122.1039 | 122.0947 | 0.004577 | -0.004578 | 122.0581 | -0.086975 | -0.045777 | 122.1725 | 122.1954 | 122.1039 | 0.13733 | 0.045776 | 0.1236 | -0.013733 | 0.11444 | 0.045776 | -0.11902 | 0.004578 | 121.9803 | 122.0627 | -0.050354 | -0.091553 | 122.0856 | 122.1039 | 122.0489 | 122.0947
3284.3438 | 122.287 | -122.081 | 0.11444 | -0.016937 | 6.9833 | 0.014204 | 0.0046868 | 0.005268 | -0.0097455 | -0.0010852 | -0.00054933 | 0.004155 | 0.01546 | 0.013418 | -0.01154 | 0.027453 | -0.0073508 | -0.041199 | -0.032043 | 0.009155 | -0.027466 | 0.068665 | -0.004578 | -0.009155 | -0.036621 | 0.050354 | -0.013733 | 0.018311 | 0.091553 | 0.013733 | 0.11902 | 122.0901 | -0.14648 | -0.14191 | 122.1497 | 122.0718 | 122.0764 | -0.01831 | -0.013733 | 122.0673 | -0.064087 | -0.09613 | 122.1725 | 122.2 | 122.0947 | 0.13275 | 0.027466 | 0.05951 | -0.036621 | 0.10529 | 0.032044 | -0.041198 | 0.064087 | 122.049 | 122.1313 | -0.10529 | -0.12817 | 122.0535 | 122.0993 | 122.0398 | 122.0444
3286.0312 | 122.2549 | -122.0901 | 0.11902 | -0.024567 | 6.9818 | 0.013349 | 0.00062801 | -0.0024224 | -0.0080365 | -0.0045032 | -0.00054933 | 0.0011642 | 0.012042 | -0.0017496 | -0.01389 | 0.028521 | -8.7586e-05 | -0.004578 | -0.045776 | 0.041199 | -0.013733 | 0.10071 | 0.018311 | 0.009155 | -0.045776 | 0.027466 | -0.009155 | -0.013733 | 0.054932 | -0.013733 | 0.073242 | 122.1313 | -0.16479 | -0.13275 | 122.1909 | 122.0993 | 122.1085 | -0.032044 | -0.022888 | 122.081 | -0.091553 | -0.13275 | 122.1451 | 122.1634 | 122.0764 | 0.082397 | -0.004578 | 0.059509 | -0.054932 | 0.064087 | -0.004578 | -0.086975 | 0.036621 | 122.0444 | 122.1176 | -0.07782 | -0.12817 | 122.0764 | 122.0764 | 122.0856 | 122.0444
3287.7969 | 122.2549 | -122.0947 | 0.13275 | -0.0016785 | 6.985 | 0.015486 | 0.0031916 | -0.0013544 | -0.0084637 | -0.0030078 | -0.0036011 | 0.0047958 | 0.01311 | 0.0027364 | -0.0079083 | 0.028948 | -0.0047874 | -0.064087 | -0.032043 | 0.004578 | -0.07782 | 0.027466 | -0.068665 | -0.059509 | -0.082397 | 0.032043 | -0.013733 | -0.009155 | 0.009155 | -0.064087 | 0.10986 | 122.0993 | -0.16479 | -0.21057 | 122.1222 | 122.0352 | 122.0261 | -0.064087 | -0.073243 | 122.081 | -0.10071 | -0.14191 | 122.1039 | 122.2046 | 122.0306 | 0.1236 | -0.050354 | 0.022888 | -0.082398 | 0.022888 | 0.004578 | -0.036621 | 0.045776 | 122.0627 | 122.1268 | -0.12817 | -0.14648 | 122.0169 | 122.0856 | 122.0306 | 122.0123
3289.4688 | 122.2549 | -122.0993 | 0.13733 | -0.009308 | 6.985 | 0.012495 | 0.001269 | -0.002636 | -0.0076093 | -0.0072802 | -0.0036011 | 0.002446 | 0.012897 | 0.011709 | -0.010472 | 0.027453 | -0.0039328 | -0.050354 | -0.022888 | 0.009155 | -0.059509 | 0.045776 | -0.018311 | -0.022888 | -0.073242 | 0.022888 | -0.059509 | -0.027466 | 0.045776 | -0.013733 | 0.091553 | 122.1085 | -0.16022 | -0.19684 | 122.1451 | 122.0764 | 122.081 | -0.032043 | -0.027466 | 122.0398 | -0.11444 | -0.16479 | 122.1451 | 122.1909 | 122.0856 | 0.15106 | 0.045776 | 0.036621 | -0.068664 | 0.10528 | 0.032043 | -0.032043 | 0.082397 | 122.0764 | 122.1222 | -0.12817 | -0.19684 | 122.0398 | 122.0718 | 122.049 | 122.0261
3291.2188 | 122.2778 | -122.1039 | 0.09613 | -0.009308 | 6.9848 | 0.01399 | 0.0025506 | 0.0039862 | -0.0076093 | -0.0015124 | -0.0066527 | 0.0026596 | 0.014178 | 0.0055136 | -0.0096173 | 0.028307 | -0.0045736 | -0.009155 | -0.027466 | 0.032043 | -0.004578 | 0.11444 | 0.009155 | -0.004578 | -0.004578 | 0.041199 | 0.013733 | 0.032043 | 0.082397 | -0.013733 | 0.10986 | 122.1359 | -0.1236 | -0.10071 | 122.2183 | 122.0993 | 122.113 | -0.036621 | -0.022888 | 122.1176 | -0.054931 | -0.064087 | 122.1863 | 122.2137 | 122.0901 | 0.09613 | -0.027466 | 0.082398 | -0.036621 | 0.068664 | 0.01831 | -0.059509 | 0.027466 | 122.0764 | 122.1451 | -0.064087 | -0.082397 | 122.0993 | 122.1359 | 122.0947 | 122.0993
3292.9062 | 122.2641 | -122.1268 | 0.11444 | -0.016937 | 6.9816 | 0.012495 | 0.001269 | 0.0041998 | -0.0073957 | -0.001726 | -0.0036011 | 0.0028732 | 0.012897 | 0.013845 | -0.016026 | 0.027666 | -8.7586e-05 | -0.050354 | -0.041199 | 0.018311 | -0.059509 | 0.064087 | -0.009155 | -0.018311 | -0.082397 | 0.054932 | 0.013733 | -0.041199 | 0.036621 | -0.032043 | 0.068665 | 122.1451 | -0.15564 | -0.17395 | 122.1909 | 122.1085 | 122.1176 | -0.036622 | -0.027466 | 122.1405 | -0.059509 | -0.15564 | 122.1634 | 122.1954 | 122.0947 | 0.054932 | -0.045776 | 0.045776 | -0.07782 | 0.022888 | -0.054932 | -0.05951 | 0.041199 | 122.0856 | 122.1817 | -0.09613 | -0.10071 | 122.0673 | 122.0856 | 122.0764 | 122.0444
3294.6562 | 122.4106 | -122.0673 | 0.068665 | -0.016937 | 6.9827 | 0.015699 | 0.00084161 | 0.00035457 | -0.0088911 | -0.0040758 | -0.0036011 | 0.0013778 | 0.011401 | 0.011068 | -0.0087629 | 0.027025 | -0.003292 | 0.004578 | -0.054932 | 0.036621 | 0.050354 | 0.20142 | 0.091553 | 0.09613 | 0.09613 | -0.013733 | 0.022888 | 0.10071 | 0.1831 | 0.1236 | 0.19684 | 122.1039 | -0.1236 | -0.018311 | 122.2687 | 122.1634 | 122.1588 | 0.059509 | 0.054932 | 122.0901 | -0.082398 | 0.032043 | 122.2504 | 122.2641 | 122.1909 | 0.17395 | 0.10071 | 0.1648 | 0.013733 | 0.16022 | 0.07782 | -0.091553 | -0.036621 | 122.0123 | 122.0535 | -0.032044 | -0.045777 | 122.1176 | 122.168 | 122.0718 | 122.1634
3296.3438 | 122.3923 | -122.0581 | 0.064087 | -0.009308 | 6.9831 | 0.014631 | 0.0019098 | -7.2628e-05 | -0.0071821 | -0.0047168 | -0.0036011 | 0.0037278 | 0.01311 | 0.0053 | -0.0044903 | 0.029375 | -0.0017966 | -0.013733 | -0.050354 | 0.041199 | 0.036621 | 0.14648 | 0.041199 | 0.059509 | 0.054932 | 0.022888 | 0.013733 | 0.10529 | 0.15106 | 0.086975 | 0.18768 | 122.0993 | -0.11444 | -0.027466 | 122.2046 | 122.1176 | 122.0993 | 0.01831 | 0 | 122.0718 | -0.041199 | 0.041199 | 122.2092 | 122.2458 | 122.1451 | 0.17395 | 0.073242 | 0.10529 | -0.004578 | 0.13733 | 0.091553 | -0.091553 | 0.009155 | 122.0078 | 122.081 | -0.022888 | -0.050354 | 122.0947 | 122.1634 | 122.0444 | 122.113
3298.0938 | 122.2687 | -122.0993 | 0.1236 | -0.0016785 | 6.9857 | 0.012922 | 0.0016962 | 0.00185 | -0.0093183 | -0.001726 | -0.00054933 | 0.0026596 | 0.012256 | 0.0023092 | -0.012181 | 0.028094 | -0.00671 | -0.022888 | -0.045776 | 0.022888 | -0.036621 | 0.10071 | 0.013733 | -0.009155 | -0.045776 | 0.032043 | -0.022888 | -0.022888 | 0.054932 | -0.004578 | 0.073242 | 122.1222 | -0.16937 | -0.16022 | 122.2 | 122.0901 | 122.113 | -0.032043 | -0.009155 | 122.0764 | -0.091553 | -0.14648 | 122.1542 | 122.1725 | 122.0947 | 0.09613 | 0.01831 | 0.07782 | -0.059509 | 0.07782 | 0 | -0.068664 | 0.054931 | 122.0535 | 122.1313 | -0.10071 | -0.14648 | 122.0627 | 122.0764 | 122.0764 | 122.0535
3299.8438 | 122.3602 | -122.0947 | 0.082397 | -0.009308 | 6.9836 | 0.014204 | 0.0016962 | -0.00049983 | -0.0082501 | -0.0047168 | -0.0036011 | 0.0039414 | 0.013751 | 0.0061544 | -0.0061993 | 0.028734 | -0.00436 | -0.013733 | -0.073242 | 0.064087 | 0.045776 | 0.17853 | 0.027466 | 0.050354 | 0.032043 | 0 | 0.022888 | 0.064087 | 0.10986 | 0.054932 | 0.15106 | 122.1588 | -0.15564 | -0.036621 | 122.2733 | 122.1451 | 122.1222 | -0.013733 | -0.036621 | 122.1176 | -0.082397 | -0.01831 | 122.2046 | 122.2458 | 122.1497 | 0.12817 | 0.032044 | 0.11444 | -0.018311 | 0.086975 | 0.041199 | -0.13733 | -0.022888 | 122.0215 | 122.0947 | -0.01831 | -0.059509 | 122.1405 | 122.1588 | 122.081 | 122.1268
3301.5312 | 122.4106 | -122.0627 | 0.091553 | -0.0016785 | 6.9806 | 0.014845 | 0.0021234 | 0.0067634 | -0.0078229 | -0.003435 | -0.0036011 | 0.0018052 | 0.014178 | 0.008077 | -0.0079083 | 0.031084 | 0.00012601 | 0.041199 | -0.073242 | 0.068665 | 0.073242 | 0.17395 | 0.050354 | 0.07782 | 0.10529 | -0.004578 | 0.027466 | 0.10986 | 0.15106 | 0.086975 | 0.19226 | 122.1313 | -0.16479 | -0.018311 | 122.2366 | 122.1405 | 122.113 | 0.009155 | -0.018311 | 122.0901 | -0.096131 | 0.01831 | 122.2137 | 122.2549 | 122.1497 | 0.16479 | 0.059509 | 0.10528 | 0.004577 | 0.1236 | 0.082397 | -0.14191 | -0.032044 | 121.9894 | 122.0581 | -0.022888 | -0.064087 | 122.1359 | 122.1725 | 122.1039 | 122.168

## Thermal Data
Fire Time | B Position - Middle | B Position - Kerite 10c w/o | D Position - 3' | D Position - Middle | D Position - 7' | D Position - Armored 3' | D Position - Armored 5' | D Position - Armored 7'
-0.6833 | 9.5457 | 9.0147 | 10.3604 | 14.6612 | 9.9468 | 9.4625 | 9.0433 | 9.0386
0.3167 | 9.5449 | 9.016 | 10.3598 | 14.6642 | 9.936 | 9.4706 | 9.0437 | 9.0371
1.3167 | 9.558 | 9.0131 | 10.3629 | 14.6601 | 9.9393 | 9.4679 | 9.042 | 9.0313
2.3167 | 9.5731 | 9.0112 | 10.3612 | 14.6761 | 9.9359 | 9.4703 | 9.0408 | 9.0392
3.3167 | 9.5847 | 9.014 | 10.3559 | 14.6579 | 9.9399 | 9.473 | 9.0373 | 9.0274
4.3167 | 9.5792 | 9.0167 | 10.3511 | 14.6744 | 9.9395 | 9.4599 | 9.041 | 9.0298
5.3167 | 9.5795 | 9.0177 | 10.372 | 14.713 | 9.9474 | 9.4619 | 9.0403 | 9.0409
6.3167 | 9.6007 | 9.014 | 10.8384 | 15.0893 | 9.9512 | 9.4523 | 9.0386 | 9.0169
7.3167 | 9.6274 | 9.0161 | 11.3981 | 15.7038 | 10.1291 | 9.4274 | 9.0354 | 9.0346
8.3167 | 9.7009 | 9.022 | 13.6391 | 16.6607 | 11.3313 | 9.3433 | 9.0233 | 9.0636
9.3167 | 9.8371 | 9.0214 | 16.2096 | 23.7718 | 13.6734 | 9.2572 | 9.0146 | 9.0761
10.3167 | 10.1031 | 9.0169 | 19.7706 | 23.8915 | 15.6148 | 9.2711 | 9.0268 | 9.0965
11.3167 | 10.8565 | 9.0157 | 24.4203 | 23.8991 | 16.906 | 9.2752 | 9.0261 | 9.0776
12.3167 | 11.677 | 9.0218 | 32.072 | 23.9037 | 19.8416 | 9.1465 | 9.0124 | 9.105
13.3167 | 12.901 | 9.022 | 39.1357 | 23.9164 | 24.4956 | 9.0799 | 9.0108 | 9.1556
14.3167 | 13.5505 | 9.0248 | 44.4399 | 23.9188 | 27.1696 | 9.1218 | 9.0252 | 9.1714
15.3167 | 14.5821 | 9.0256 | 49.2618 | 23.9167 | 28.8317 | 9.211 | 9.0221 | 9.1643
16.3167 | 16.1696 | 9.0252 | 50.9169 | 23.9282 | 30.5283 | 9.2505 | 9.0352 | 9.1261
17.3167 | 17.9136 | 9.0339 | 54.7357 | 23.9249 | 32.1452 | 9.2513 | 9.0354 | 9.1539
18.3167 | 19.079 | 9.0314 | 56.8385 | 23.9303 | 34.3156 | 9.2457 | 9.0356 | 9.1916
19.3167 | 20.0216 | 9.038 | 59.3208 | 23.9385 | 35.4197 | 9.2318 | 9.0475 | 9.2157
20.3167 | 20.7805 | 9.0319 | 61.8536 | 23.9307 | 37.976 | 9.2056 | 9.0488 | 9.237
21.3167 | 22.0379 | 9.0351 | 65.7431 | 23.9358 | 41.5309 | 9.1449 | 9.0448 | 9.2794
22.3167 | 23.2429 | 9.043 | 70.2154 | 23.9498 | 46.4228 | 9.1352 | 9.0675 | 9.2984
23.3167 | 24.6636 | 9.0463 | 73.744 | 23.9521 | 50.4616 | 9.1328 | 9.056 | 9.3263
24.3167 | 25.6395 | 9.0488 | 76.7188 | 23.9453 | 53.2801 | 9.2528 | 9.0506 | 9.2774
25.3167 | 27.5491 | 9.0496 | 80.0903 | 23.9568 | 56.0681 | 9.3134 | 9.0517 | 9.2959
26.3167 | 29.5115 | 9.0518 | 83.6435 | 23.9602 | 58.6156 | 9.3596 | 9.0775 | 9.2892
27.3167 | 30.0407 | 9.0458 | 87.0025 | 23.9769 | 62.2601 | 9.3992 | 9.0892 | 9.3193
28.3167 | 30.2874 | 9.0584 | 88.6989 | 23.9742 | 64.5767 | 9.4032 | 9.0781 | 9.335
29.3167 | 31.796 | 9.0549 | 91.2468 | 23.9758 | 67.939 | 9.5532 | 9.1108 | 9.3098
30.3167 | 32.3244 | 9.0605 | 92.906 | 23.9796 | 70.0996 | 9.6517 | 9.1276 | 9.3158
31.3167 | 33.7142 | 9.0479 | 94.2814 | 23.9827 | 72.065 | 9.6278 | 9.1181 | 9.346
32.3167 | 34.5068 | 9.0504 | 94.999 | 23.9841 | 73.4983 | 9.6392 | 9.15 | 9.3727
33.3167 | 35.4438 | 9.057 | 96.3639 | 23.9906 | 74.9267 | 9.7524 | 9.1607 | 9.3494
34.3167 | 36.6241 | 9.0557 | 97.7332 | 23.9838 | 77.3002 | 9.8851 | 9.1947 | 9.3311
35.3167 | 37.7731 | 9.0521 | 99.8871 | 23.9987 | 79.498 | 9.9009 | 9.2055 | 9.3636
36.3167 | 39.0229 | 9.0615 | 101.6225 | 24.0045 | 81.8595 | 9.9117 | 9.208 | 9.3732
37.3167 | 39.8403 | 9.0642 | 104.3262 | 24.0084 | 83.7373 | 9.9433 | 9.2341 | 9.3697
38.3167 | 40.5508 | 9.0614 | 105.7444 | 24.0129 | 85.2177 | 10.0461 | 9.271 | 9.3898
39.3167 | 42.1702 | 9.0652 | 106.7416 | 24.0136 | 86.8987 | 10.1158 | 9.2666 | 9.4132
40.3167 | 43.06 | 9.0616 | 107.2293 | 24.0201 | 88.8537 | 10.2174 | 9.2943 | 9.3862
41.3167 | 44.3791 | 9.0604 | 108.3987 | 24.0308 | 89.9017 | 10.2917 | 9.3192 | 9.3977
42.3167 | 45.2886 | 9.0624 | 109.5592 | 24.0186 | 91.0565 | 10.3747 | 9.3404 | 9.4124
43.3167 | 46.0827 | 9.0664 | 109.7306 | 24.0242 | 92.4942 | 10.4171 | 9.3791 | 9.4293
44.3167 | 47.1983 | 9.0646 | 111.228 | 24.03 | 93.7177 | 10.5441 | 9.3687 | 9.4272
45.3167 | 48.384 | 9.0703 | 112.7311 | 24.0422 | 96.0917 | 10.5275 | 9.4107 | 9.4874
46.3167 | 48.7227 | 9.0732 | 114.0054 | 24.0494 | 97.8841 | 10.6394 | 9.4318 | 9.4659
47.3167 | 49.4085 | 9.0791 | 116.2567 | 24.0384 | 99.8806 | 10.7071 | 9.4719 | 9.4867
48.3167 | 49.5093 | 9.0715 | 116.6098 | 24.0529 | 101.9395 | 10.7071 | 9.4955 | 9.4991
49.3167 | 50.8997 | 9.0782 | 118.3171 | 24.0505 | 105.4964 | 10.6991 | 9.4996 | 9.5591
50.3167 | 51.9384 | 9.0767 | 119.5038 | 24.0498 | 106.8769 | 10.9873 | 9.5642 | 9.5287
51.3167 | 52.4962 | 9.0799 | 121.3088 | 24.064 | 108.1422 | 11.1323 | 9.597 | 9.5113
52.3167 | 53.8271 | 9.0804 | 122.251 | 24.0686 | 108.8896 | 11.1925 | 9.624 | 9.535
53.3167 | 54.0083 | 9.0869 | 122.8688 | 24.0728 | 111.177 | 11.2332 | 9.6697 | 9.5776
54.3167 | 54.9344 | 9.0932 | 123.4652 | 24.0661 | 113.3448 | 11.3145 | 9.6828 | 9.6169
55.3167 | 55.9298 | 9.0926 | 122.7712 | 24.0676 | 114.9923 | 11.3673 | 9.735 | 9.6414
56.3167 | 56.479 | 9.0924 | 122.2807 | 24.0691 | 116.5485 | 11.4813 | 9.7857 | 9.6307
57.3167 | 57.1225 | 9.0928 | 122.5654 | 24.0863 | 117.8386 | 11.5676 | 9.8112 | 9.689
58.3167 | 57.9187 | 9.0944 | 123.1375 | 24.082 | 118.7676 | 11.6487 | 9.8325 | 9.7035
59.3167 | 58.5971 | 9.094 | 123.2165 | 24.0884 | 119.0811 | 11.7262 | 9.8753 | 9.6794
60.3167 | 59.3734 | 9.1003 | 123.834 | 24.088 | 120.1472 | 11.8704 | 9.9139 | 9.679
61.3167 | 60.1787 | 9.0978 | 123.6488 | 24.0952 | 121.142 | 11.945 | 9.9716 | 9.7023
62.3167 | 60.7607 | 9.1029 | 123.2558 | 24.0908 | 121.5507 | 11.9986 | 10.0167 | 9.754
63.3167 | 61.652 | 9.1065 | 123.6987 | 24.0961 | 122.2534 | 12.1 | 10.0552 | 9.7457
64.3167 | 62.3323 | 9.1138 | 123.6651 | 24.1023 | 122.5236 | 12.2221 | 10.0873 | 9.7601
65.3167 | 63.1386 | 9.1139 | 124.3362 | 24.1069 | 122.7165 | 12.2394 | 10.1527 | 9.814
66.3167 | 63.7126 | 9.1168 | 124.6379 | 24.1173 | 123.857 | 12.3088 | 10.2002 | 9.8917
67.3167 | 64.1701 | 9.1239 | 124.7982 | 24.1142 | 124.8052 | 12.3916 | 10.2383 | 9.8757
68.3167 | 65.5313 | 9.1328 | 125.1903 | 24.118 | 125.0526 | 12.5276 | 10.3042 | 9.8804
69.3167 | 66.18 | 9.1365 | 125.4524 | 24.1224 | 126.1897 | 12.6158 | 10.3543 | 9.9078
70.3167 | 66.7141 | 9.1408 | 125.7732 | 24.1297 | 127.3386 | 12.6637 | 10.3858 | 9.9637
71.3167 | 66.8634 | 9.1494 | 126.0909 | 24.1281 | 128.6299 | 12.7432 | 10.4399 | 10.006
72.3167 | 67.1586 | 9.1509 | 126.5367 | 24.135 | 130.148 | 12.7989 | 10.4992 | 10.0319
73.3167 | 67.6307 | 9.1621 | 126.858 | 24.1397 | 130.7665 | 12.8589 | 10.5591 | 10.0524
74.3167 | 69.1264 | 9.1624 | 127.4187 | 24.1433 | 131.2657 | 12.9661 | 10.6436 | 10.1268
75.3167 | 69.9039 | 9.1707 | 129.0225 | 24.1421 | 133.0479 | 12.9954 | 10.6725 | 10.1425
76.3167 | 70.3769 | 9.1745 | 129.0375 | 24.1442 | 135.6374 | 13.0632 | 10.7425 | 10.2128
77.3167 | 71.2971 | 9.1837 | 128.813 | 24.1551 | 135.9598 | 13.2047 | 10.813 | 10.2317
78.3167 | 71.3881 | 9.1842 | 128.46 | 24.161 | 136.4288 | 13.359 | 10.8797 | 10.2386
79.3167 | 71.9881 | 9.2003 | 128.2703 | 24.1597 | 136.6855 | 13.4292 | 10.908 | 10.2466
80.3167 | 73.0633 | 9.2002 | 128.5345 | 24.1696 | 136.7798 | 13.5095 | 10.9887 | 10.2847
81.3167 | 73.5313 | 9.2106 | 129.0466 | 24.1772 | 136.9122 | 13.5935 | 11.0442 | 10.3549
82.3167 | 74.312 | 9.2229 | 129.7698 | 24.1762 | 137.4993 | 13.5483 | 11.117 | 10.4245
83.3323 | 74.5614 | 9.2297 | 130.4433 | 24.1817 | 137.8357 | 13.7335 | 11.1752 | 10.4342
84.3167 | 74.7218 | 9.2331 | 131.898 | 24.182 | 138.5081 | 13.822 | 11.2247 | 10.4502
85.3167 | 74.909 | 9.2405 | 131.9851 | 24.1837 | 138.4727 | 13.9233 | 11.2761 | 10.5045
86.3167 | 75.3774 | 9.2551 | 131.9439 | 24.1835 | 138.5932 | 13.983 | 11.3526 | 10.5604
87.3167 | 75.805 | 9.2623 | 132.0343 | 24.1798 | 139.6988 | 14.0879 | 11.4052 | 10.5794
88.3167 | 76.2508 | 9.2719 | 131.8111 | 24.1897 | 140.0376 | 14.1993 | 11.5156 | 10.6202
89.3167 | 76.1505 | 9.2784 | 131.7827 | 24.2108 | 140.7166 | 14.2777 | 11.5794 | 10.6996
90.3167 | 76.48 | 9.2906 | 131.8192 | 24.2108 | 141.3168 | 14.3376 | 11.6265 | 10.7391
91.3167 | 77.0571 | 9.3032 | 132.3149 | 24.212 | 141.1724 | 14.4922 | 11.7186 | 10.7521
92.3167 | 78.0233 | 9.3063 | 133.4588 | 24.2164 | 141.5829 | 14.5434 | 11.7623 | 10.8054
93.3167 | 78.3281 | 9.3231 | 133.6066 | 24.2098 | 142.4054 | 14.6218 | 11.8591 | 10.8417
94.3167 | 79.1057 | 9.3275 | 133.9699 | 24.2165 | 142.7552 | 14.7048 | 11.9143 | 10.8681
95.3167 | 79.443 | 9.3445 | 134.1203 | 24.2165 | 143.5624 | 14.8288 | 11.9924 | 10.9407
96.3167 | 80.3175 | 9.3573 | 134.3523 | 24.23 | 143.3117 | 14.9269 | 12.0671 | 10.9581
97.3167 | 80.3762 | 9.3647 | 135.493 | 24.2151 | 143.6138 | 14.9681 | 12.1271 | 11.0288
98.3167 | 80.5497 | 9.3762 | 135.8214 | 24.2397 | 144.2935 | 15.0801 | 12.2198 | 11.0845
99.3167 | 81.6164 | 9.3896 | 135.6633 | 24.2324 | 144.7124 | 15.1596 | 12.2916 | 11.1267
100.3167 | 82.2528 | 9.4044 | 136.365 | 24.2425 | 145.391 | 15.2073 | 12.3492 | 11.2079
101.3167 | 82.4767 | 9.4182 | 137.0594 | 24.2434 | 146.9557 | 15.2675 | 12.4301 | 11.2745
102.3167 | 83.3324 | 9.4186 | 138.5938 | 24.239 | 147.4167 | 15.4024 | 12.502 | 11.3162
103.3167 | 84.1909 | 9.4352 | 139.4801 | 24.2557 | 147.5262 | 15.4997 | 12.5707 | 11.3624
104.3167 | 84.7018 | 9.4595 | 140.9229 | 24.2479 | 147.4665 | 15.6133 | 12.6788 | 11.3973
105.3167 | 85.4888 | 9.4655 | 142.223 | 24.2488 | 148.1812 | 15.6652 | 12.7299 | 11.4803
106.3167 | 85.9335 | 9.4835 | 144.7071 | 24.2541 | 147.5537 | 15.8012 | 12.8152 | 11.4769
107.3167 | 86.9472 | 9.4971 | 145.1341 | 24.2572 | 148.3581 | 15.8008 | 12.9157 | 11.592
108.3167 | 87.709 | 9.5158 | 146.1795 | 24.2617 | 148.8595 | 15.9193 | 12.9995 | 11.6376
109.3167 | 87.7463 | 9.5245 | 146.7074 | 24.2708 | 149.9374 | 15.9975 | 13.0762 | 11.7038
110.3167 | 88.3451 | 9.5466 | 146.3559 | 24.2627 | 152.6238 | 16.065 | 13.136 | 11.7837
111.3167 | 88.5991 | 9.5699 | 146.9917 | 24.2715 | 154.2774 | 16.1578 | 13.2235 | 11.8445
112.3167 | 88.6762 | 9.5775 | 147.3327 | 24.2772 | 155.0583 | 16.302 | 13.3426 | 11.9108
113.3167 | 89.8799 | 9.6018 | 147.1789 | 24.2771 | 155.5892 | 16.4376 | 13.4475 | 11.9649
114.3167 | 89.8362 | 9.6223 | 148.0821 | 24.2751 | 155.5118 | 16.5493 | 13.5245 | 11.9782
115.3167 | 89.8972 | 9.6377 | 148.1272 | 24.2866 | 156.2348 | 16.6623 | 13.6162 | 12.0462
116.3167 | 90.7025 | 9.6573 | 148.1049 | 24.2876 | 156.1952 | 16.791 | 13.7222 | 12.0796
117.3167 | 91.1527 | 9.6718 | 147.1289 | 24.2955 | 156.072 | 16.9069 | 13.8265 | 12.1616
118.3167 | 90.979 | 9.6908 | 147.245 | 24.2917 | 155.8441 | 16.9809 | 13.8873 | 12.2338
119.3167 | 90.8645 | 9.7227 | 148.0294 | 24.3055 | 155.6436 | 17.0995 | 13.9831 | 12.3077
120.3167 | 91.2106 | 9.745 | 147.9968 | 24.3068 | 156.5153 | 17.1302 | 14.1055 | 12.3715
121.3167 | 91.1813 | 9.7659 | 148.5459 | 24.3147 | 156.8283 | 17.2331 | 14.1562 | 12.4482
122.3167 | 91.5592 | 9.7868 | 148.7285 | 24.3091 | 156.828 | 17.359 | 14.2744 | 12.5176
123.3167 | 91.379 | 9.8086 | 149.777 | 24.3105 | 157.1284 | 17.472 | 14.3616 | 12.5892
124.3167 | 92.0045 | 9.8322 | 149.4822 | 24.319 | 156.6897 | 17.5984 | 14.4522 | 12.602
125.3167 | 92.7451 | 9.8508 | 149.1697 | 24.3185 | 155.8544 | 17.712 | 14.5275 | 12.6762
126.3167 | 93.118 | 9.8815 | 148.7916 | 24.3274 | 154.5765 | 17.7802 | 14.6393 | 12.7479
127.3167 | 93.0496 | 9.9053 | 150.1768 | 24.3282 | 154.6504 | 17.8296 | 14.7162 | 12.8332
128.3167 | 93.1773 | 9.9295 | 150.2967 | 24.3309 | 155.5353 | 17.9236 | 14.8357 | 12.9266
129.3167 | 93.585 | 9.9525 | 150.8908 | 24.3312 | 155.7586 | 18.0165 | 14.9058 | 12.9856
130.3167 | 93.2278 | 9.9836 | 151.9688 | 24.3285 | 156.3528 | 18.159 | 15.0411 | 13.0599
131.3167 | 92.8996 | 10.0027 | 151.703 | 24.3397 | 156.0179 | 18.3148 | 15.1208 | 13.0913
132.3167 | 92.899 | 10.0285 | 152.6986 | 24.3431 | 155.5681 | 18.4213 | 15.2332 | 13.167
133.3167 | 93.5374 | 10.0611 | 152.3123 | 24.351 | 155.2034 | 18.5229 | 15.3386 | 13.2463
134.3167 | 94.024 | 10.0897 | 152.2769 | 24.358 | 155.304 | 18.6157 | 15.4455 | 13.3266
135.3167 | 94.5104 | 10.1144 | 152.8156 | 24.3638 | 155.0236 | 18.6472 | 15.5462 | 13.4195
136.3167 | 94.7747 | 10.1538 | 152.7717 | 24.3623 | 155.3603 | 18.8101 | 15.6381 | 13.4688
137.3167 | 96.0748 | 10.175 | 152.6322 | 24.3509 | 155.0868 | 18.9307 | 15.7262 | 13.5169
138.3167 | 96.1775 | 10.2061 | 152.4457 | 24.3609 | 155.1049 | 19.0526 | 15.8487 | 13.6124
139.3167 | 96.8873 | 10.2323 | 152.1228 | 24.3755 | 154.2598 | 19.1597 | 15.9468 | 13.6937
140.3167 | 97.306 | 10.2652 | 151.6007 | 24.3757 | 153.897 | 19.2425 | 16.0553 | 13.7572
141.3167 | 97.4192 | 10.2892 | 150.9355 | 24.3774 | 152.9758 | 19.3539 | 16.1536 | 13.8475
142.3167 | 97.5792 | 10.318 | 150.9681 | 24.3818 | 152.4083 | 19.4967 | 16.2528 | 13.9003
143.3167 | 97.6982 | 10.3559 | 150.3746 | 24.3891 | 152.2852 | 19.556 | 16.3544 | 13.9949
144.3167 | 97.0527 | 10.3797 | 151.1191 | 24.3878 | 151.801 | 19.6789 | 16.4391 | 14.0597
145.3167 | 97.0737 | 10.4062 | 151.7954 | 24.3909 | 151.4432 | 19.7858 | 16.5418 | 14.1308
146.3167 | 97.5164 | 10.4399 | 151.2021 | 24.3966 | 151.1766 | 19.923 | 16.6773 | 14.2395
147.3167 | 98.0403 | 10.4736 | 151.1014 | 24.4013 | 150.8976 | 20.039 | 16.7853 | 14.3005
148.3167 | 98.1381 | 10.5088 | 150.572 | 24.3979 | 150.9304 | 20.1236 | 16.8745 | 14.3726
149.3167 | 97.8606 | 10.5376 | 150.2488 | 24.4065 | 151.6892 | 20.2298 | 16.9803 | 14.4645
150.3167 | 98.2194 | 10.5682 | 149.6625 | 24.4125 | 151.8494 | 20.3292 | 17.1053 | 14.5563
151.3167 | 98.3124 | 10.6046 | 149.8753 | 24.4081 | 151.837 | 20.4039 | 17.213 | 14.6213
152.3167 | 98.7618 | 10.6345 | 151.3736 | 24.4174 | 152.7975 | 20.5009 | 17.288 | 14.7119
153.3167 | 98.8059 | 10.6717 | 151.8941 | 24.422 | 153.2599 | 20.6654 | 17.4161 | 14.789
154.3167 | 99.5408 | 10.702 | 152.0149 | 24.4232 | 153.1247 | 20.7717 | 17.5263 | 14.8659
155.3167 | 99.8504 | 10.7307 | 152.1634 | 24.4266 | 153.9599 | 20.8365 | 17.6506 | 14.9685
156.3167 | 99.5653 | 10.7645 | 151.9002 | 24.4262 | 155.1017 | 20.9642 | 17.7532 | 15.0363
157.3167 | 99.8698 | 10.8053 | 151.2992 | 24.4404 | 155.6179 | 21.1086 | 17.8645 | 15.1249
158.3167 | 99.7594 | 10.835 | 150.7174 | 24.4281 | 156.2727 | 21.1871 | 17.9997 | 15.1776
159.3167 | 100.4036 | 10.8615 | 150.6014 | 24.4355 | 156.0688 | 21.2987 | 18.0881 | 15.2581
160.3167 | 100.7307 | 10.9028 | 150.0543 | 24.4492 | 156.6539 | 21.4028 | 18.2275 | 15.3563
161.3167 | 101.7029 | 10.9389 | 149.908 | 24.4523 | 156.8175 | 21.4861 | 18.312 | 15.4445
162.3167 | 102.4509 | 10.9725 | 149.6856 | 24.4416 | 157.6449 | 21.5992 | 18.4358 | 15.5341
163.3167 | 103.1458 | 11.0009 | 149.7076 | 24.4543 | 158.5869 | 21.6919 | 18.5537 | 15.6089
164.3167 | 103.593 | 11.0479 | 149.231 | 24.4548 | 158.7347 | 21.7853 | 18.664 | 15.7311
165.3167 | 103.8468 | 11.0893 | 149.4683 | 24.4601 | 159.0387 | 21.9308 | 18.7708 | 15.8036
166.3167 | 104.0072 | 11.1238 | 149.0498 | 24.4573 | 158.4903 | 22.037 | 18.874 | 15.8496
167.3167 | 104.3604 | 11.1549 | 149.1591 | 24.465 | 158.0018 | 22.1222 | 19.0322 | 15.9543
168.3167 | 104.6952 | 11.1985 | 148.9525 | 24.4739 | 157.8817 | 22.2512 | 19.1193 | 16.0287
169.3167 | 104.8672 | 11.2329 | 149.6732 | 24.4628 | 158.8836 | 22.3222 | 19.2255 | 16.1315
170.3167 | 105.2411 | 11.2752 | 151.6703 | 24.4796 | 160.3424 | 22.4483 | 19.3334 | 16.228
171.3167 | 105.7399 | 11.3102 | 152.1106 | 24.4907 | 161.103 | 22.5818 | 19.5163 | 16.3384
172.3167 | 106.205 | 11.3489 | 151.8589 | 24.4923 | 161.7002 | 22.659 | 19.6163 | 16.3822
173.3167 | 106.1888 | 11.3835 | 151.4224 | 24.4949 | 160.9819 | 22.8216 | 19.7264 | 16.4864
174.3167 | 106.765 | 11.4289 | 150.7944 | 24.5092 | 160.409 | 22.8794 | 19.8415 | 16.5965
175.3167 | 107.3577 | 11.4683 | 150.4195 | 24.4981 | 159.5741 | 22.9815 | 19.9507 | 16.6707
176.3167 | 107.5781 | 11.5048 | 151.3239 | 24.5136 | 159.7595 | 23.123 | 20.0901 | 16.7695
177.3167 | 107.0678 | 11.541 | 151.6757 | 24.5088 | 160.3328 | 23.2177 | 20.1837 | 16.8321
178.3167 | 107.6716 | 11.5897 | 151.5061 | 24.5247 | 161.3175 | 23.2848 | 20.3353 | 16.9905
179.3167 | 108.0933 | 11.6235 | 151.3681 | 24.5308 | 162.6038 | 23.4314 | 20.4263 | 17.0394
180.3167 | 108.4628 | 11.668 | 151.4933 | 24.5689 | 162.592 | 23.5207 | 20.561 | 17.1394
181.3167 | 108.6474 | 11.704 | 151.8829 | 24.5923 | 163.6584 | 23.6489 | 20.7179 | 17.2257
182.3167 | 108.5775 | 11.7456 | 152.2983 | 24.6351 | 164.2286 | 23.7809 | 20.8327 | 17.2859
183.3167 | 108.9362 | 11.7865 | 151.8152 | 24.7085 | 165.0102 | 23.8666 | 20.9424 | 17.4052
184.3167 | 109.2106 | 11.8333 | 151.8776 | 24.822 | 165.2773 | 24.0052 | 21.0744 | 17.5089
185.3167 | 110.1006 | 11.8794 | 151.8411 | 24.8705 | 165.8031 | 24.1077 | 21.1691 | 17.5867
186.3167 | 109.9436 | 11.9111 | 151.9192 | 24.933 | 166.2106 | 24.201 | 21.303 | 17.6932
187.3167 | 109.4688 | 11.9527 | 152.2509 | 24.9596 | 166.8092 | 24.3139 | 21.4352 | 17.7969
188.3167 | 109.0635 | 11.9959 | 152.1544 | 25.0352 | 167.024 | 24.381 | 21.5585 | 17.8823
189.3167 | 108.592 | 12.0376 | 151.8719 | 25.1625 | 166.957 | 24.5403 | 21.65 | 17.9631
190.3167 | 109.0738 | 12.0924 | 152.0028 | 25.3717 | 166.7647 | 24.6262 | 21.8254 | 18.0819
191.3167 | 108.9093 | 12.1323 | 152.2902 | 25.5409 | 166.9989 | 24.6988 | 21.9193 | 18.1711
192.3167 | 109.5704 | 12.1802 | 151.8424 | 25.8498 | 167.2196 | 24.8356 | 22.0312 | 18.2773
193.3167 | 109.2715 | 12.2091 | 152.0598 | 26.0399 | 167.2923 | 24.9413 | 22.1983 | 18.3781
194.3167 | 109.8703 | 12.2563 | 152.147 | 26.6176 | 166.8874 | 25.0109 | 22.2779 | 18.4546
195.3167 | 109.9615 | 12.2992 | 151.8215 | 26.9315 | 167.3389 | 25.111 | 22.4482 | 18.5486
196.3167 | 110.0535 | 12.3471 | 152.7273 | 27.1881 | 167.1895 | 25.26 | 22.5384 | 18.6626
197.3167 | 110.8075 | 12.3914 | 153.0367 | 28.0791 | 167.9814 | 25.3783 | 22.6867 | 18.7578
198.3167 | 111.2742 | 12.4357 | 153.3601 | 27.9452 | 168.0705 | 25.4779 | 22.8011 | 18.844
199.3167 | 111.6681 | 12.472 | 154.3173 | 28.267 | 168.3285 | 25.5806 | 22.9218 | 18.9668
200.3167 | 112.375 | 12.5197 | 155.427 | 28.8768 | 168.4431 | 25.6836 | 23.0976 | 19.0833
201.3167 | 112.5528 | 12.566 | 158.11 | 29.646 | 169.0192 | 25.8234 | 23.1904 | 19.1521
202.3167 | 113.1026 | 12.6149 | 158.0556 | 30.9035 | 169.5808 | 25.9088 | 23.3123 | 19.2454
203.3167 | 113.6655 | 12.6608 | 157.9143 | 32.2288 | 169.6807 | 25.9873 | 23.4485 | 19.3842
204.3167 | 113.8839 | 12.7065 | 157.8894 | 44.5193 | 170.5227 | 26.1036 | 23.591 | 19.4526
205.3167 | 113.9434 | 12.7524 | 158.3838 | 148.9101 | 170.2406 | 26.2123 | 23.7462 | 19.599
206.3167 | 114.2882 | 12.7977 | 159.6914 | 180.9841 | 170.9918 | 26.3019 | 23.842 | 19.7164
207.3167 | 114.4139 | 12.8359 | 161.6897 | 182.3466 | 172.0729 | 26.4272 | 23.993 | 19.7848
208.3167 | 114.8654 | 12.8813 | 163.5571 | 184.3577 | 173.3676 | 26.547 | 24.1171 | 19.8799
209.3167 | 115.2882 | 12.9315 | 163.7523 | 184.5883 | 173.5022 | 26.6641 | 24.2286 | 19.9698
210.3167 | 115.877 | 12.9809 | 164.5159 | 184.9801 | 174.7242 | 26.7844 | 24.3632 | 20.1141
211.3167 | 116.2623 | 13.0254 | 165.0495 | 185.2751 | 175.8486 | 26.8933 | 24.4939 | 20.238
212.3167 | 116.1196 | 13.0727 | 165.2512 | 185.248 | 176.2232 | 26.9811 | 24.639 | 20.3407
213.3167 | 116.249 | 13.1178 | 166.261 | 184.8791 | 176.5722 | 27.1212 | 24.7813 | 20.4299
214.3167 | 117.0699 | 13.1662 | 166.8055 | 185.5121 | 178.2157 | 27.2483 | 24.8896 | 20.5253
215.3167 | 116.8316 | 13.2134 | 166.5909 | 185.9547 | 179.0304 | 27.3223 | 25.056 | 20.6661
216.3167 | 117.4678 | 13.2616 | 167.1153 | 186.0653 | 179.8978 | 27.4631 | 25.1511 | 20.7355
217.3167 | 118.5417 | 13.3049 | 167.251 | 186.9248 | 180.6931 | 27.5361 | 25.2971 | 20.8642
218.3167 | 119.7608 | 13.3552 | 167.1255 | 187.8061 | 181.0284 | 27.6612 | 25.4391 | 20.9536
219.3167 | 120.7109 | 13.3962 | 167.3961 | 188.406 | 181.6077 | 27.774 | 25.5697 | 21.0536
220.3167 | 121.4551 | 13.4426 | 167.0982 | 189.1754 | 182.3833 | 27.9055 | 25.7046 | 21.1553
221.3167 | 122.5446 | 13.4933 | 166.7512 | 190.0198 | 182.0758 | 28.0237 | 25.8824 | 21.2681
222.3167 | 123.0704 | 13.5475 | 166.4751 | 190.5227 | 181.9928 | 28.1236 | 25.9864 | 21.4004
223.3167 | 124.0431 | 13.595 | 166.036 | 190.7013 | 182.26 | 28.2365 | 26.1095 | 21.5105
224.3167 | 125.267 | 13.643 | 166.0746 | 191.1399 | 182.492 | 28.3643 | 26.2444 | 21.621
225.3167 | 126.4618 | 13.6978 | 166.1808 | 191.2189 | 182.4354 | 28.4512 | 26.361 | 21.7177
226.3167 | 127.6 | 13.7448 | 166.1424 | 191.9869 | 183.2399 | 28.5781 | 26.5239 | 21.8165
227.3167 | 128.6136 | 13.798 | 165.6004 | 191.9251 | 183.8271 | 28.7036 | 26.6519 | 21.9346
228.3167 | 130.0295 | 13.8421 | 165.3382 | 192.1412 | 183.8947 | 28.8195 | 26.7997 | 22.0626
229.3167 | 130.9397 | 13.8856 | 165.2702 | 191.8789 | 184.0744 | 28.9286 | 26.9189 | 22.1666
230.3167 | 131.7762 | 13.9458 | 165.4003 | 190.9065 | 184.6009 | 29.0433 | 27.0453 | 22.2535
231.3167 | 132.21 | 13.9856 | 165.1849 | 190.4106 | 184.4058 | 29.1488 | 27.1864 | 22.3677
232.3167 | 133.2238 | 14.0422 | 164.7571 | 191.5581 | 184.7105 | 29.2631 | 27.3359 | 22.4959
233.3167 | 134.0992 | 14.0873 | 164.8919 | 191.3037 | 184.7257 | 29.3697 | 27.4796 | 22.6339
234.3167 | 135.04 | 14.1293 | 165.2594 | 191.965 | 184.3897 | 29.4898 | 27.628 | 22.6993
235.3167 | 135.9993 | 14.1811 | 165.5287 | 192.5024 | 185.0871 | 29.6289 | 27.7419 | 22.803
236.3167 | 136.9439 | 14.233 | 166.5295 | 193.4171 | 186.6879 | 29.7009 | 27.8875 | 22.961
237.3167 | 137.7841 | 14.2803 | 167.8085 | 194.2956 | 189.9977 | 29.7939 | 28.0132 | 23.1182
238.3167 | 138.9304 | 14.3245 | 167.8734 | 195.3351 | 191.8513 | 29.9301 | 28.192 | 23.1962
239.3167 | 139.9332 | 14.3871 | 168.3384 | 196.6 | 192.6463 | 30.0665 | 28.3385 | 23.297
240.3167 | 140.9218 | 14.4271 | 168.194 | 197.2561 | 192.7834 | 30.1908 | 28.4951 | 23.4415
241.3167 | 141.6965 | 14.4787 | 167.7686 | 197.5829 | 192.8599 | 30.2356 | 28.6087 | 23.5751
242.3167 | 141.9734 | 14.5284 | 168.5254 | 198.3023 | 193.7064 | 30.3855 | 28.7708 | 23.6604
243.3167 | 141.934 | 14.5814 | 170.5839 | 199.8501 | 194.3373 | 30.4942 | 28.8779 | 23.7961
244.3167 | 141.7283 | 14.6394 | 172.7324 | 201.5413 | 195.8308 | 30.601 | 29.0323 | 23.8773
245.3167 | 141.6703 | 14.6817 | 173.6529 | 202.5497 | 196.6958 | 30.7445 | 29.2109 | 24.0499
246.3167 | 141.3396 | 14.7372 | 173.856 | 203.2342 | 196.4327 | 30.8782 | 29.3423 | 24.1386
247.3167 | 141.6949 | 14.7772 | 174.0914 | 203.6575 | 195.6992 | 30.9943 | 29.5012 | 24.2672
248.3167 | 142.002 | 14.831 | 174.4179 | 204.1177 | 195.6641 | 31.1135 | 29.6334 | 24.3778
249.3167 | 142.8519 | 14.8894 | 173.9593 | 203.961 | 194.5795 | 31.2302 | 29.7835 | 24.4983
250.3167 | 143.4025 | 14.9402 | 174.2135 | 204.1159 | 194.2374 | 31.3305 | 29.9397 | 24.6174
251.3167 | 144.6278 | 14.9907 | 175.0985 | 205.435 | 195.2992 | 31.4289 | 30.087 | 24.7254
252.3167 | 146.3041 | 15.0385 | 175.7787 | 206.2171 | 196.3983 | 31.5558 | 30.2415 | 24.8407
253.3167 | 146.5484 | 15.0975 | 177.0596 | 207.87 | 197.1861 | 31.6619 | 30.3664 | 24.9808
254.3167 | 147.3634 | 15.1463 | 177.6215 | 209.0891 | 197.3783 | 31.8077 | 30.5277 | 25.0987
255.3167 | 147.5188 | 15.201 | 178.7189 | 211.3846 | 198.7159 | 31.903 | 30.6782 | 25.2203
256.3167 | 147.8638 | 15.2639 | 180.2884 | 212.633 | 198.7515 | 32.0584 | 30.8299 | 25.338
257.3167 | 147.8988 | 15.3117 | 181.4342 | 212.8967 | 199.3785 | 32.1503 | 30.9704 | 25.443
258.3167 | 148.6597 | 15.363 | 180.955 | 212.7955 | 199.2918 | 32.2696 | 31.147 | 25.5875
259.3167 | 148.881 | 15.4154 | 181.1854 | 212.8247 | 199.3163 | 32.4 | 31.2708 | 25.6982
260.3167 | 149.6115 | 15.4668 | 180.829 | 213.1199 | 199.5138 | 32.5256 | 31.4443 | 25.8314
261.3167 | 149.6385 | 15.5182 | 181.1437 | 213.8914 | 201.4405 | 32.6417 | 31.5763 | 25.9636
262.3167 | 150.6533 | 15.5748 | 182.1525 | 214.4313 | 202.0079 | 32.7722 | 31.7035 | 26.0834
263.3167 | 151.7214 | 15.6263 | 181.7907 | 214.4742 | 201.5029 | 32.9145 | 31.8582 | 26.206
264.3167 | 152.1423 | 15.6811 | 181.6459 | 214.8346 | 201.7399 | 33.0165 | 32.0299 | 26.3333
265.3167 | 152.8029 | 15.7322 | 182.1673 | 214.9634 | 201.4733 | 33.1369 | 32.1554 | 26.4431
266.3167 | 153.4297 | 15.7836 | 183.0382 | 215.3409 | 201.7 | 33.2678 | 32.3349 | 26.5904
267.3167 | 153.731 | 15.8332 | 182.8682 | 215.3407 | 201.4248 | 33.3651 | 32.4774 | 26.7094
268.3167 | 153.3014 | 15.894 | 182.6434 | 216.2127 | 201.5584 | 33.4839 | 32.6217 | 26.8221
269.3167 | 152.9507 | 15.9493 | 182.9764 | 216.4798 | 203.6069 | 33.6113 | 32.786 | 26.9648
270.3167 | 153.6557 | 16.0071 | 183.2498 | 217.3722 | 205.331 | 33.7433 | 32.9401 | 27.1086
271.3167 | 153.8288 | 16.0543 | 183.0352 | 217.9369 | 204.6813 | 33.9093 | 33.081 | 27.208
272.3167 | 154.1839 | 16.1156 | 184.874 | 219.0254 | 204.7602 | 33.9843 | 33.2531 | 27.3555
273.3167 | 154.4949 | 16.1693 | 187.4075 | 220.1649 | 204.8262 | 34.1403 | 33.4031 | 27.4568
274.3167 | 154.2113 | 16.2313 | 189.3997 | 221.1098 | 205.7931 | 34.2428 | 33.5555 | 27.6024
275.3167 | 154.5009 | 16.2852 | 190.4477 | 221.7045 | 206.3531 | 34.3779 | 33.712 | 27.7251
276.3167 | 153.9088 | 16.3447 | 191.1994 | 222.6775 | 206.9749 | 34.4952 | 33.8808 | 27.8618
277.3167 | 153.7497 | 16.4024 | 190.8443 | 222.9914 | 207.8321 | 34.6224 | 34.0621 | 27.9986
278.3167 | 153.759 | 16.469 | 190.7455 | 223.0654 | 208.1963 | 34.7516 | 34.1969 | 28.1313
279.3167 | 154.3661 | 16.5177 | 192.6294 | 224.5297 | 207.9403 | 34.8651 | 34.3498 | 28.2614
280.3167 | 154.909 | 16.5829 | 194.5844 | 225.9029 | 210.2134 | 34.9873 | 34.5007 | 28.3969
281.3167 | 155.6823 | 16.6431 | 195.3839 | 227.4449 | 211.2395 | 35.1242 | 34.7013 | 28.5267
282.3167 | 156.6591 | 16.6956 | 196.2929 | 228.2882 | 211.9922 | 35.2367 | 34.8355 | 28.6901
283.3167 | 157.6543 | 16.7565 | 196.2316 | 229.6324 | 212.1096 | 35.3752 | 34.9982 | 28.7913
284.3167 | 158.4328 | 16.8221 | 196.2244 | 230.0831 | 214.5037 | 35.505 | 35.1378 | 28.9126
285.3167 | 158.7669 | 16.8819 | 196.4916 | 231.1155 | 215.0473 | 35.6251 | 35.3172 | 29.0509
286.3167 | 159.5205 | 16.9426 | 196.2537 | 231.4946 | 216.2327 | 35.7801 | 35.4844 | 29.219
287.3167 | 159.6571 | 17.0042 | 196.2813 | 232.3538 | 215.6136 | 35.8995 | 35.6408 | 29.3397
288.3167 | 160.1234 | 17.0614 | 196.5137 | 232.9069 | 216.4326 | 36.0257 | 35.8167 | 29.4843
289.3167 | 160.0607 | 17.1169 | 197.5401 | 234.0982 | 218.542 | 36.1537 | 35.9599 | 29.6218
290.3167 | 161.5857 | 17.1826 | 197.4205 | 233.9933 | 218.4808 | 36.3008 | 36.1093 | 29.7569
291.3167 | 162.2876 | 17.2433 | 197.8983 | 233.6737 | 218.7448 | 36.4322 | 36.2778 | 29.8532
292.3167 | 161.8783 | 17.3068 | 198.3092 | 233.7604 | 218.0491 | 36.5648 | 36.4597 | 29.9979
293.3167 | 162.1286 | 17.371 | 198.5691 | 234.0713 | 218.7285 | 36.7198 | 36.6179 | 30.1421
294.3167 | 162.6399 | 17.4316 | 199.2935 | 234.0004 | 218.4018 | 36.8443 | 36.8028 | 30.2862
295.3167 | 163.1098 | 17.5032 | 200.7548 | 234.919 | 219.7201 | 36.9777 | 36.9412 | 30.4308
296.3167 | 163.4828 | 17.5576 | 201.4679 | 235.5555 | 221.0527 | 37.1179 | 37.1301 | 30.5676
297.3167 | 164.2538 | 17.6223 | 201.7083 | 235.5142 | 222.784 | 37.2433 | 37.3056 | 30.7019
298.3167 | 164.4619 | 17.6795 | 203.3598 | 236.7929 | 223.9085 | 37.3875 | 37.4506 | 30.8392
299.3167 | 164.2649 | 17.7454 | 206.1512 | 238.7487 | 225.9424 | 37.5254 | 37.6499 | 30.9544
300.3167 | 164.2024 | 17.8172 | 207.4309 | 239.8249 | 227.216 | 37.68 | 37.8103 | 31.114
301.3167 | 164.8188 | 17.8759 | 206.8036 | 240.2188 | 228.4902 | 37.7983 | 37.999 | 31.2432
302.3167 | 165.3232 | 17.9506 | 206.2114 | 240.4931 | 228.8934 | 37.9144 | 38.1557 | 31.3826
303.3167 | 165.7139 | 18.0115 | 208.7521 | 241.6326 | 229.5449 | 38.0805 | 38.3256 | 31.5428
304.3167 | 165.8899 | 18.0813 | 209.3424 | 243.1659 | 230.806 | 38.2144 | 38.4799 | 31.6661
305.3167 | 166.2 | 18.1492 | 209.0796 | 243.937 | 230.5854 | 38.3646 | 38.6593 | 31.7667
306.3167 | 166.2603 | 18.2068 | 208.416 | 243.5056 | 230.1289 | 38.5105 | 38.8279 | 31.934
307.3167 | 166.4646 | 18.2799 | 207.465 | 242.573 | 229.1004 | 38.636 | 38.9958 | 32.0814
308.3167 | 166.0121 | 18.3544 | 208.3716 | 243.0855 | 230.2366 | 38.808 | 39.1395 | 32.2214
309.3167 | 166.0819 | 18.4217 | 208.5002 | 242.0614 | 230.8827 | 38.9687 | 39.3187 | 32.3505
310.3167 | 166.7923 | 19.0367 | 209.9493 | 244.098 | 233.524 | 39.0787 | 39.5327 | 32.5374
311.3167 | 167.5464 | 19.3747 | 211.309 | 244.1723 | 235.892 | 39.244 | 39.6765 | 32.6981
312.3167 | 169.8077 | 19.2803 | 212.0011 | 244.4268 | 237.8664 | 39.4108 | 39.8758 | 32.8352
313.3167 | 171.229 | 19.1324 | 212.6584 | 245.1269 | 238.4379 | 39.5544 | 40.0378 | 32.9775
314.3167 | 171.9605 | 19.1151 | 215.0549 | 247.5278 | 240.0567 | 39.7071 | 40.233 | 33.1321
315.3167 | 175.0875 | 19.1323 | 215.8565 | 248.6762 | 239.6574 | 39.8659 | 40.4522 | 33.2649
316.3167 | 175.1344 | 19.1773 | 215.4466 | 248.2084 | 239.2902 | 40.0118 | 40.6149 | 33.3919
317.3167 | 176.3315 | 19.2252 | 214.5891 | 248.1289 | 239.6232 | 40.145 | 40.7795 | 33.5613
318.3167 | 177.1987 | 19.27 | 214.6979 | 247.8907 | 238.8506 | 40.3024 | 40.9824 | 33.7124
319.3167 | 178.0844 | 19.3258 | 213.7869 | 247.9695 | 239.6543 | 40.4592 | 41.1129 | 33.8566
320.3167 | 179.0672 | 19.3813 | 213.8918 | 248.4303 | 238.6505 | 40.6086 | 41.33 | 33.9935
321.3167 | 179.5501 | 19.4373 | 213.3095 | 248.6026 | 240.1034 | 40.7686 | 41.48 | 34.1453
322.3167 | 179.4921 | 20.0737 | 212.6131 | 247.5027 | 240.1729 | 40.9414 | 41.6828 | 34.2815
323.3167 | 179.4886 | 20.2346 | 212.4239 | 247.0107 | 238.8816 | 41.11 | 41.8381 | 34.4371
324.3167 | 178.7667 | 20.1231 | 212.0371 | 246.7135 | 237.4353 | 41.2532 | 42.0229 | 34.58
325.3167 | 178.3269 | 20.1055 | 211.5588 | 246.1073 | 235.7909 | 41.4169 | 42.1999 | 34.7349
326.3167 | 177.7379 | 20.0912 | 211.9554 | 246.9224 | 235.9088 | 41.5599 | 42.3602 | 34.8655
327.3167 | 177.5958 | 20.078 | 212.5304 | 247.1729 | 235.0937 | 41.725 | 42.541 | 35.0299
328.3167 | 177.4282 | 20.0902 | 213.3427 | 248.1768 | 234.1541 | 41.8819 | 42.7307 | 35.1653
329.3167 | 176.996 | 20.117 | 213.8749 | 248.5152 | 234.6593 | 42.0268 | 42.9003 | 35.353
330.3167 | 178.2107 | 20.1512 | 213.0794 | 248.1524 | 234.0807 | 42.1743 | 43.0745 | 35.4794
331.3167 | 179.2631 | 20.1921 | 212.43 | 247.9794 | 234.2845 | 42.3374 | 43.2933 | 35.6196
332.3167 | 179.9509 | 20.2385 | 213.3385 | 248.1382 | 233.2851 | 42.482 | 43.4581 | 35.7828
333.3167 | 180.6931 | 20.2992 | 213.737 | 248.7232 | 232.6412 | 42.6407 | 43.6582 | 35.9573
334.3167 | 180.9528 | 20.3579 | 213.6994 | 249.1224 | 233.5813 | 42.7924 | 43.8024 | 36.1019
335.3167 | 181.0685 | 20.5692 | 214.9072 | 249.331 | 233.6159 | 42.9374 | 43.9866 | 36.2363
336.3167 | 180.9236 | 20.8863 | 214.5262 | 249.3757 | 233.894 | 43.0933 | 44.1687 | 36.4041
337.3167 | 181.6341 | 20.8334 | 214.2963 | 249.7975 | 234.6767 | 43.2342 | 44.37 | 36.5758
338.3167 | 182.4866 | 20.8398 | 214.0561 | 250.2159 | 235.3542 | 43.3957 | 44.5242 | 36.7327
339.3167 | 181.7831 | 20.8674 | 214.3656 | 250.536 | 236.078 | 43.5378 | 44.7016 | 36.8742
340.3167 | 181.4356 | 20.9218 | 215.283 | 250.5028 | 235.8554 | 43.7042 | 44.9074 | 37.0185
341.3167 | 180.9814 | 20.9585 | 216.4719 | 251.4408 | 236.2872 | 43.836 | 45.0984 | 37.1873
342.3167 | 181.3717 | 21.0053 | 216.9273 | 251.889 | 235.5141 | 43.9962 | 45.265 | 37.3489
343.3167 | 182.059 | 21.0526 | 219.1194 | 252.7386 | 234.8216 | 44.1526 | 45.4408 | 37.487
344.3167 | 181.847 | 21.1208 | 220.5567 | 254.6743 | 234.6416 | 44.3131 | 45.6352 | 37.6623
345.3167 | 182.5453 | 21.1794 | 221.2301 | 256.1751 | 235.5123 | 44.4788 | 45.8142 | 37.811
346.3167 | 182.9682 | 21.2422 | 221.9506 | 257.2552 | 235.2586 | 44.6252 | 46.0028 | 37.9849
347.3167 | 183.0069 | 21.3021 | 221.758 | 256.1256 | 234.8621 | 44.7885 | 46.185 | 38.1267
348.3167 | 183.5968 | 21.3606 | 220.3359 | 255.6103 | 234.3728 | 44.9317 | 46.365 | 38.2735
349.3167 | 183.5048 | 21.4181 | 219.5181 | 255.8744 | 233.3364 | 45.0837 | 46.5383 | 38.4174
350.3167 | 183.3649 | 21.4838 | 219.7628 | 255.8642 | 232.3775 | 45.2395 | 46.7399 | 38.5848
351.3167 | 183.9991 | 21.555 | 220.6553 | 256.2841 | 233.2599 | 45.4076 | 46.9049 | 38.7433
352.3167 | 183.9702 | 21.6257 | 221.8501 | 256.9292 | 233.7478 | 45.538 | 47.1027 | 38.9078
353.3167 | 185.2113 | 21.6965 | 222.2055 | 256.9839 | 234.1146 | 45.6991 | 47.2728 | 39.0559
354.3167 | 186.2417 | 21.7576 | 222.6191 | 257.9322 | 233.8193 | 45.8515 | 47.4704 | 39.2208
355.3167 | 187.3117 | 21.8331 | 222.7261 | 259.2924 | 235.0379 | 45.9926 | 47.646 | 39.3958
356.3167 | 187.98 | 21.8898 | 224.3718 | 260.363 | 236.4425 | 46.1571 | 47.8195 | 39.5503
357.3167 | 186.77 | 21.9657 | 225.4828 | 261.2857 | 236.4582 | 46.3266 | 48.0201 | 39.7119
358.3167 | 186.9404 | 22.032 | 225.57 | 260.9114 | 235.8291 | 46.4669 | 48.2256 | 39.8594
359.3167 | 187.2186 | 22.107 | 226.2738 | 260.6569 | 235.1044 | 46.6323 | 48.4002 | 40.0344
360.3167 | 188.1653 | 22.1736 | 227.2195 | 261.2393 | 233.8928 | 46.8101 | 48.575 | 40.1831
361.3167 | 187.7246 | 22.2414 | 227.9633 | 261.7849 | 233.0106 | 46.9677 | 48.7855 | 40.3283
362.3167 | 187.8974 | 22.3139 | 227.9666 | 261.6106 | 234.3894 | 47.1185 | 48.9724 | 40.5114
363.3167 | 188.0402 | 22.3852 | 228.8412 | 262.4769 | 234.871 | 47.2664 | 49.1502 | 40.6678
364.3167 | 187.7261 | 22.4515 | 231.1006 | 264.0396 | 237.2476 | 47.4331 | 49.3321 | 40.8301
365.3167 | 187.1133 | 22.5181 | 232.1449 | 264.8539 | 237.6237 | 47.6134 | 49.5328 | 40.9938
366.3167 | 187.6317 | 22.5917 | 233.6254 | 265.2206 | 237.7098 | 47.7676 | 49.7091 | 41.1552
367.3167 | 188.4773 | 22.6702 | 232.0302 | 265.224 | 240.0335 | 47.9162 | 49.9126 | 41.2841
368.3167 | 189.3153 | 22.7317 | 232.5073 | 266.7903 | 242.1837 | 48.0784 | 50.0877 | 41.4884
369.3167 | 189.6807 | 22.8212 | 235.1444 | 269.4037 | 242.8133 | 48.2585 | 50.3032 | 41.6646
370.3167 | 189.1025 | 22.8915 | 235.1407 | 269.016 | 243.0778 | 48.4296 | 50.4848 | 41.791
371.3167 | 189.5678 | 22.9625 | 233.3714 | 268.6511 | 242.3257 | 48.5978 | 50.6777 | 41.9548
372.3167 | 190.4898 | 23.0339 | 232.3604 | 268.0814 | 243.0008 | 48.7466 | 50.8563 | 42.1131
373.3167 | 190.4241 | 23.1013 | 231.6446 | 267.8788 | 244.7135 | 48.9332 | 51.0486 | 42.2526
374.3167 | 191.4843 | 23.1828 | 231.7109 | 268.9564 | 246.8782 | 49.0904 | 51.2331 | 42.4527
375.3167 | 191.6044 | 23.2632 | 231.1037 | 269.2722 | 248.7098 | 49.2569 | 51.4324 | 42.5978
376.3167 | 190.856 | 23.3416 | 231.5014 | 270.0141 | 248.9309 | 49.4238 | 51.6486 | 42.7677
377.3167 | 191.6727 | 23.7091 | 231.9845 | 270.5634 | 248.7805 | 49.6078 | 51.8264 | 42.9152
378.3167 | 192.2962 | 23.7695 | 233.2761 | 269.76 | 249.5201 | 49.7716 | 52.0154 | 43.0929
379.3167 | 192.9098 | 23.7487 | 232.1319 | 268.9361 | 250.2588 | 49.9489 | 52.2049 | 43.2232
380.3167 | 194.5064 | 23.7971 | 232.3575 | 269.6651 | 249.5182 | 50.1045 | 52.3963 | 43.3866
381.3167 | 194.7089 | 23.8652 | 232.0041 | 270.1115 | 249.7369 | 50.2644 | 52.5842 | 43.5675
382.3167 | 195.751 | 24.3043 | 232.7199 | 271.7257 | 250.9896 | 50.4335 | 52.8036 | 43.7238
383.3167 | 196.8297 | 24.2698 | 231.3702 | 272.3823 | 250.2749 | 50.6135 | 52.97 | 43.8822
384.3167 | 197.8937 | 24.263 | 231.8467 | 272.4937 | 250.4109 | 50.7852 | 53.1674 | 44.04
385.3167 | 199 | 24.3194 | 231.2295 | 272.9955 | 249.9486 | 50.9538 | 53.3882 | 44.1966
386.3167 | 198.8628 | 24.3805 | 232.7124 | 272.9006 | 249.8207 | 51.1185 | 53.5689 | 44.3749
387.3167 | 199.4389 | 24.4298 | 231.8811 | 272.8554 | 249.7523 | 51.3103 | 53.737 | 44.5212
388.3167 | 199.9383 | 24.5521 | 232.0864 | 272.5869 | 249.4504 | 51.4687 | 53.9559 | 44.6918
389.3167 | 200.4683 | 24.9361 | 231.7146 | 272.5317 | 249.0176 | 51.6394 | 54.1337 | 44.8335
390.3167 | 200.8592 | 25.0372 | 232.017 | 271.8347 | 248.6082 | 51.8089 | 54.3699 | 45.0117
391.3167 | 200.6358 | 25.2133 | 233.4095 | 271.7358 | 248.241 | 51.9903 | 54.5311 | 45.1597
392.3167 | 200.6333 | 25.348 | 234.7224 | 271.7892 | 247.7005 | 52.1562 | 54.7328 | 45.3171
393.3167 | 200.351 | 25.4 | 235.6139 | 272.8615 | 248.5518 | 52.3471 | 54.9325 | 45.4714
394.3167 | 200.7654 | 25.4258 | 236.1232 | 273.6688 | 249.2389 | 52.511 | 55.1339 | 45.6533
395.3167 | 201.4974 | 25.4521 | 236.1455 | 274.283 | 249.6467 | 52.6948 | 55.3256 | 45.7932
396.3167 | 201.315 | 25.4848 | 237.6145 | 274.808 | 251.3195 | 52.8536 | 55.5173 | 45.9516
397.3167 | 201.1557 | 25.5046 | 237.9471 | 274.7475 | 252.4454 | 53.0304 | 55.692 | 46.1228
398.3167 | 201.8226 | 25.5473 | 238.0782 | 275.2197 | 251.7868 | 53.2067 | 55.9195 | 46.2866
399.3167 | 201.7149 | 25.6163 | 238.9436 | 276.8027 | 251.2196 | 53.3634 | 56.121 | 46.4586
400.3167 | 202.262 | 25.6816 | 240.1863 | 278.2989 | 251.3067 | 53.5361 | 56.3087 | 46.633
401.3167 | 202.3585 | 25.7364 | 241.5882 | 280.5451 | 250.9181 | 53.7181 | 56.4862 | 46.7909
402.3167 | 202.7212 | 25.8483 | 242.2687 | 281.4845 | 250.8108 | 53.878 | 56.7084 | 46.9453
403.3167 | 202.7643 | 25.9317 | 245.3198 | 282.5499 | 251.5209 | 54.07 | 56.9108 | 47.1204
404.3167 | 203.2926 | 25.9906 | 245.4733 | 282.0972 | 253.3983 | 54.2566 | 57.1085 | 47.288
405.3167 | 203.1304 | 26.0511 | 246.2514 | 282.1389 | 254.555 | 54.4423 | 57.2885 | 47.4419
406.3167 | 202.9855 | 26.11 | 247.6449 | 283.0469 | 254.223 | 54.5955 | 57.4962 | 47.6132
407.3167 | 202.5186 | 26.1677 | 247.7213 | 283.998 | 253.5164 | 54.7846 | 57.6987 | 47.7833
408.3167 | 203.1364 | 26.2342 | 247.2169 | 283.9179 | 254.6266 | 54.9605 | 57.9032 | 47.9372
409.3167 | 203.8824 | 26.2961 | 247.7146 | 283.9354 | 254.2372 | 55.1286 | 58.0925 | 48.098
410.3167 | 203.9067 | 26.3626 | 247.6486 | 283.1806 | 253.8642 | 55.315 | 58.3069 | 48.2855
411.3167 | 204.4798 | 26.4326 | 247.9915 | 284.0485 | 255.2026 | 55.4862 | 58.4795 | 48.4364
412.3167 | 205.4211 | 26.5053 | 246.4752 | 284.2294 | 256.4175 | 55.6809 | 58.691 | 48.6014
413.3167 | 205.544 | 26.5815 | 245.7171 | 284.2829 | 257.0866 | 55.8548 | 58.8879 | 48.7744
414.3167 | 206.3038 | 26.7734 | 245.2479 | 284.8645 | 258.7004 | 56.037 | 59.0968 | 48.9798
415.3167 | 207.3992 | 26.7981 | 244.0787 | 284.3815 | 259.0819 | 56.2223 | 59.2815 | 49.1121
416.3167 | 208.094 | 26.8599 | 243.9957 | 284.4574 | 259.2949 | 56.3978 | 59.4582 | 49.2754
417.3167 | 209.3182 | 26.9092 | 243.2961 | 284.5367 | 259.1319 | 56.5795 | 59.6663 | 49.4265
418.3167 | 208.6577 | 26.9826 | 243.8654 | 285.1663 | 259.1677 | 56.7733 | 59.8757 | 49.5878
419.3167 | 209.475 | 27.0577 | 246.8257 | 285.7931 | 259.1849 | 56.9523 | 60.0709 | 49.7422
420.3167 | 210.1054 | 27.1347 | 247.4904 | 285.362 | 258.4372 | 57.155 | 60.2673 | 49.9229
421.3167 | 210.788 | 27.2045 | 247.4929 | 284.9364 | 258.1547 | 57.3404 | 60.4674 | 50.0732
422.3167 | 211.021 | 27.2903 | 246.7188 | 285.1913 | 260.1171 | 57.518 | 60.6651 | 50.2653
423.3167 | 211.7622 | 27.3691 | 248.4077 | 285.8967 | 261.127 | 57.7138 | 60.8357 | 50.4321
424.3167 | 211.6569 | 27.4592 | 248.6236 | 286.8054 | 260.532 | 57.9078 | 61.0319 | 50.5994
425.3167 | 212.0003 | 27.5567 | 250.1033 | 288.0767 | 260.5932 | 58.0922 | 61.2152 | 50.7508
426.3167 | 212.7284 | 27.9432 | 250.3594 | 288.6935 | 262.169 | 58.2865 | 61.4151 | 50.9145
427.3167 | 212.8702 | 28.1371 | 250.3046 | 288.7952 | 261.6826 | 58.4469 | 61.6315 | 51.0882
428.3167 | 212.8657 | 28.1807 | 252.0257 | 289.6227 | 262.1497 | 58.6514 | 61.8363 | 51.2445
429.3167 | 213.2552 | 28.1796 | 256.1368 | 291.2111 | 262.6754 | 58.8418 | 62.0327 | 51.4017
430.3167 | 212.9798 | 28.2303 | 257.3993 | 292.7449 | 262.7329 | 59.0456 | 62.2367 | 51.5661
431.3167 | 212.1414 | 28.2863 | 256.7116 | 292.3375 | 262.3384 | 59.2216 | 62.4166 | 51.7455
432.3167 | 212.9714 | 28.3391 | 256.4731 | 291.7121 | 261.974 | 59.4299 | 62.6198 | 51.9032
433.3167 | 212.8379 | 28.3952 | 257.5393 | 291.8402 | 261.2607 | 59.6241 | 62.8147 | 52.0644
434.3167 | 212.6751 | 28.4612 | 257.4518 | 291.7628 | 260.4708 | 59.8047 | 63.0272 | 52.2269
435.3167 | 212.5763 | 28.5369 | 256.3759 | 290.8969 | 259.95 | 59.9919 | 63.2074 | 52.4006
436.3167 | 212.2727 | 28.6193 | 255.46 | 290.1832 | 260.0271 | 60.18 | 63.445 | 52.5516
437.3167 | 212.4375 | 28.6904 | 256.1872 | 291.3189 | 259.7228 | 60.3609 | 63.6047 | 52.7247
438.3167 | 212.5724 | 28.7655 | 256.8698 | 291.4243 | 261.636 | 60.5522 | 63.8363 | 52.881
439.3167 | 212.4542 | 28.8479 | 256.5081 | 292.2336 | 263.1801 | 60.7486 | 64.0098 | 53.0587
440.3167 | 211.9588 | 28.9194 | 255.6521 | 291.7467 | 263.4806 | 60.9362 | 64.2005 | 53.2305
441.3167 | 212.264 | 29.0117 | 257.5773 | 292.715 | 262.4475 | 61.1454 | 64.4087 | 53.3968
442.3167 | 213.1352 | 29.0963 | 258.6751 | 292.9374 | 262.0134 | 61.3259 | 64.6484 | 53.5311
443.3167 | 214.0455 | 29.1891 | 259.8936 | 295.1364 | 263.9313 | 61.5149 | 64.8093 | 53.7043
444.3167 | 215.1504 | 29.2785 | 259.696 | 295.3811 | 265.5314 | 61.7187 | 65.0144 | 53.8712
445.3167 | 216.2195 | 29.3692 | 259.1602 | 295.4217 | 266.6328 | 61.9162 | 65.2244 | 54.0464
446.3167 | 216.4424 | 29.5299 | 261.2347 | 298.2394 | 269.536 | 62.1143 | 65.4164 | 54.2278
447.3167 | 216.6158 | 29.6753 | 261.925 | 299.2304 | 269.9632 | 62.3018 | 65.6316 | 54.3846
448.3167 | 216.2309 | 29.7095 | 260.4336 | 300.0859 | 270.4687 | 62.4992 | 65.8421 | 54.566
449.3167 | 215.7122 | 29.7888 | 261.093 | 299.8579 | 270.1262 | 62.6984 | 66.0177 | 54.7272
450.3167 | 215.408 | 29.8661 | 262.1833 | 300.5074 | 269.4254 | 62.8931 | 66.2337 | 54.8944
451.3167 | 215.547 | 29.9566 | 261.9993 | 301.729 | 271.4065 | 63.0926 | 66.4102 | 55.0574
452.3167 | 216.4386 | 30.0404 | 261.5419 | 301.5948 | 271.689 | 63.3066 | 66.6032 | 55.2246
453.3167 | 216.7259 | 30.1353 | 263.9262 | 302.6691 | 271.4042 | 63.4837 | 66.834 | 55.3916
454.3167 | 217.1394 | 30.2324 | 266.1757 | 303.9435 | 272.1437 | 63.6914 | 67.0124 | 55.565
455.3167 | 217.1435 | 30.3366 | 266.143 | 304.2619 | 270.8972 | 63.888 | 67.1982 | 55.7326
456.3167 | 217.7738 | 30.4353 | 266.9231 | 305.3952 | 271.63 | 64.0856 | 67.4031 | 55.9019
457.3167 | 218.353 | 30.5398 | 266.4786 | 305.8844 | 272.1973 | 64.2963 | 67.6087 | 56.0509
458.3167 | 218.6692 | 30.6416 | 265.472 | 305.2249 | 271.8505 | 64.4867 | 67.8272 | 56.2184
459.3167 | 219.5785 | 30.7313 | 265.9261 | 304.5955 | 272.6134 | 64.6866 | 67.9984 | 56.3992
460.3167 | 220.1762 | 30.8248 | 265.2283 | 304.1454 | 273.5199 | 64.8863 | 68.1882 | 56.5363
461.3167 | 220.9028 | 30.9275 | 265.0774 | 305.4232 | 273.7446 | 65.0763 | 68.3849 | 56.7258
462.3167 | 221.2933 | 31.0293 | 264.9622 | 306.1813 | 275.9005 | 65.2717 | 68.5623 | 56.8947
463.3167 | 221.2299 | 31.1323 | 268.1894 | 307.0691 | 276.7454 | 65.4794 | 68.8003 | 57.031
464.3167 | 222.0101 | 31.2299 | 266.9416 | 306.1855 | 276.9887 | 65.6649 | 68.9577 | 57.2339
465.3167 | 223.1742 | 31.3289 | 265.3064 | 306.1631 | 277.6561 | 65.8603 | 69.132 | 57.401
466.3167 | 224.1227 | 31.4345 | 265.864 | 306.7621 | 277.131 | 66.0812 | 69.3644 | 57.538
467.3167 | 225.0741 | 31.5304 | 263.7004 | 305.756 | 276.2193 | 66.278 | 69.5446 | 57.7188
468.3167 | 225.7842 | 31.6347 | 263.0426 | 305.8027 | 277.37 | 66.4756 | 69.7221 | 57.8791
469.3167 | 225.9646 | 31.7281 | 262.5085 | 305.9861 | 277.0312 | 66.6621 | 69.9324 | 58.044
470.3167 | 227.1374 | 31.8318 | 262.3175 | 305.474 | 276.3278 | 66.8515 | 70.1227 | 58.2209
471.3167 | 227.1196 | 31.9356 | 262.319 | 305.8941 | 276.3805 | 67.0746 | 70.3142 | 58.384
472.3167 | 227.4501 | 32.0333 | 262.2694 | 305.5993 | 276.1478 | 67.2713 | 70.5088 | 58.5861
473.3167 | 227.9081 | 32.1295 | 262.0049 | 306.6539 | 276.0617 | 67.4784 | 70.6822 | 58.7443
474.3167 | 228.6854 | 32.234 | 262.6611 | 307.1214 | 274.7702 | 67.6627 | 70.8741 | 58.9247
475.3167 | 229.4482 | 32.3331 | 264.4174 | 308.8669 | 274.5115 | 67.8919 | 71.0769 | 59.0593
476.3167 | 230.2361 | 32.4377 | 266.5556 | 309.9554 | 274.5948 | 68.0857 | 71.2813 | 59.2452
477.3167 | 230.673 | 32.5495 | 267.9727 | 310.7109 | 275.9709 | 68.2902 | 71.4517 | 59.4116
478.3167 | 231.3088 | 32.6565 | 270.4384 | 310.5943 | 279.2621 | 68.5072 | 71.6586 | 59.5869
479.3167 | 231.4946 | 32.7665 | 274.7579 | 313.8436 | 281.597 | 68.7049 | 71.8371 | 59.773
480.3167 | 231.1247 | 32.8739 | 276.5761 | 315.5373 | 282.2837 | 68.9292 | 72.0175 | 59.9199
481.3167 | 232.4205 | 32.9811 | 274.264 | 315.9441 | 282.9487 | 69.1361 | 72.2227 | 60.0716
482.3167 | 233.3086 | 33.0776 | 274.3762 | 315.4245 | 282.969 | 69.3433 | 72.4143 | 60.2501
483.3167 | 234.1778 | 33.1928 | 274.5996 | 314.9132 | 282.8202 | 69.5432 | 72.5954 | 60.4276
484.3167 | 233.9819 | 33.2952 | 275.4897 | 314.8018 | 283.6987 | 69.7527 | 72.7807 | 60.5631
485.3167 | 235.148 | 33.4039 | 274.6051 | 314.4424 | 284.5397 | 69.9528 | 72.9784 | 60.7535
486.3167 | 237.1203 | 33.5108 | 273.7609 | 314.5923 | 284.9006 | 70.1544 | 73.1681 | 60.9181
487.3167 | 238.3223 | 33.6181 | 272.6292 | 313.6303 | 285.1595 | 70.3589 | 73.3678 | 61.0891
488.3167 | 238.8427 | 33.7327 | 271.9853 | 314.1195 | 284.3807 | 70.5433 | 73.5786 | 61.2501
489.3167 | 239.6154 | 33.8363 | 271.6115 | 313.1712 | 286.6806 | 70.7542 | 73.7717 | 61.4171
490.3167 | 240.5597 | 33.947 | 270.5816 | 313.0884 | 286.2021 | 70.9697 | 73.9515 | 61.5876
491.3167 | 240.4883 | 34.0569 | 269.1388 | 312.4079 | 284.6168 | 71.1508 | 74.1329 | 61.7694
492.3167 | 241.0824 | 34.168 | 269.8504 | 311.2688 | 282.4859 | 71.3682 | 74.3346 | 61.9253
493.3167 | 242.1565 | 34.2795 | 270.2366 | 311.3654 | 282.0222 | 71.5702 | 74.5248 | 62.0837
494.3167 | 242.2431 | 34.3912 | 269.5487 | 311.7083 | 283.1782 | 71.7921 | 74.7114 | 62.2601
495.3167 | 242.7741 | 34.5002 | 268.8895 | 310.5372 | 282.9356 | 71.9967 | 74.8945 | 62.4339
496.3167 | 241.8994 | 34.6139 | 269.1706 | 309.1204 | 281.7314 | 72.2023 | 75.0839 | 62.5788
497.3167 | 240.7889 | 34.7273 | 268.9664 | 308.6595 | 279.6882 | 72.4188 | 75.2965 | 62.7458
498.3167 | 241.1123 | 34.841 | 270.4243 | 308.6438 | 278.2808 | 72.639 | 75.4578 | 62.9322
499.3167 | 241.2282 | 34.9495 | 274.2453 | 310.7258 | 278.8953 | 72.8482 | 75.6486 | 63.0854
500.3167 | 240.2784 | 35.0794 | 273.6739 | 311.1889 | 278.5278 | 73.0609 | 75.847 | 63.2684
501.3167 | 240.5492 | 35.1578 | 272.8528 | 311.517 | 278.9116 | 73.2576 | 76.074 | 63.4405
502.3167 | 240.9419 | 35.1939 | 273.095 | 311.9459 | 280.8461 | 73.4695 | 76.2644 | 63.619
503.3167 | 241.4593 | 35.2744 | 272.1015 | 311.8961 | 280.443 | 73.7007 | 76.4518 | 63.749
504.3167 | 242.1784 | 35.3663 | 272.0602 | 312.4082 | 280.191 | 73.8983 | 76.6529 | 63.9388
505.3167 | 242.8877 | 35.4429 | 272.307 | 312.2822 | 280.7909 | 74.1072 | 76.8312 | 64.1201
506.3167 | 242.8198 | 35.5376 | 274.1021 | 311.8868 | 281.0914 | 74.3185 | 77.033 | 64.2847
507.3167 | 243.0934 | 35.6472 | 272.7112 | 313.3746 | 279.8272 | 74.5515 | 77.242 | 64.4277
508.3167 | 243.6205 | 35.7651 | 272.0291 | 312.2945 | 279.817 | 74.7527 | 77.4476 | 64.6173
509.3167 | 243.1301 | 35.8779 | 271.8353 | 312.7631 | 279.8016 | 74.9658 | 77.6392 | 64.7825
510.3167 | 242.9457 | 36.0063 | 272.7151 | 313.1662 | 279.1723 | 75.1719 | 77.8355 | 64.9534
511.3167 | 242.4921 | 36.1102 | 271.6884 | 312.8704 | 279.1553 | 75.3833 | 78.0258 | 65.1286
512.3167 | 241.9756 | 36.2282 | 272.9636 | 313.1594 | 279.4438 | 75.595 | 78.2317 | 65.2766
513.3167 | 242.4915 | 36.3373 | 274.3482 | 313.2061 | 278.9165 | 75.8003 | 78.4339 | 65.4661
514.3167 | 242.1849 | 36.452 | 274.7714 | 314.0077 | 279.3189 | 76.0377 | 78.6121 | 65.6208
515.3167 | 241.583 | 36.5749 | 275.232 | 314.5375 | 280.072 | 76.2349 | 78.8257 | 65.8054
516.3167 | 242.2982 | 36.681 | 275.8168 | 314.7346 | 279.697 | 76.4375 | 79.036 | 65.9936
517.3167 | 241.961 | 36.7904 | 275.0258 | 314.1731 | 280.3539 | 76.6498 | 79.2216 | 66.1478
518.3167 | 241.1092 | 36.9059 | 274.4389 | 314.2364 | 281.9615 | 76.8541 | 79.4426 | 66.3301
519.3167 | 241.2664 | 37.0222 | 275.3876 | 314.9697 | 284.1454 | 77.0606 | 79.6179 | 66.5048
520.3167 | 241.1969 | 37.137 | 276.8408 | 315.2594 | 285.1926 | 77.2847 | 79.8513 | 66.6738
521.3167 | 241.7019 | 37.2471 | 277.8437 | 316.2464 | 285.9635 | 77.4931 | 80.02 | 66.851
522.3167 | 241.3198 | 37.3556 | 277.5696 | 315.951 | 286.3086 | 77.6833 | 80.2043 | 67.0207
523.3167 | 241.8036 | 37.4711 | 276.7747 | 316.4785 | 287.2061 | 77.903 | 80.4162 | 67.1792
524.3167 | 242.2696 | 37.5895 | 276.0908 | 315.8025 | 286.4584 | 78.1106 | 80.6028 | 67.3557
525.3167 | 243.1208 | 37.6987 | 275.5798 | 315.6187 | 286.508 | 78.3154 | 80.8262 | 67.5247
526.3167 | 243.6255 | 37.821 | 274.8516 | 315.0786 | 287.4228 | 78.522 | 81.0292 | 67.7236
527.3167 | 244.8009 | 37.9354 | 272.8065 | 313.7491 | 287.4965 | 78.7315 | 81.2185 | 67.8785
528.3167 | 245.5669 | 38.0479 | 274.0478 | 313.8405 | 288.1687 | 78.9332 | 81.4243 | 68.0565
529.3167 | 245.9039 | 38.1539 | 275.4252 | 314.1198 | 289.2195 | 79.1765 | 81.5976 | 68.208
530.3167 | 246.2855 | 38.2625 | 275.7044 | 313.6454 | 290.185 | 79.3852 | 81.8265 | 68.3973
531.3167 | 246.3356 | 38.3807 | 274.6471 | 313.8244 | 290.0674 | 79.5866 | 81.9868 | 68.577
532.3167 | 245.5546 | 38.4985 | 273.0358 | 313.3601 | 290.4299 | 79.7989 | 82.2073 | 68.708
533.3167 | 245.6522 | 38.6141 | 273.8211 | 314.3473 | 289.4338 | 80.009 | 82.391 | 68.9072
534.3167 | 245.9404 | 38.7217 | 273.7414 | 314.1093 | 288.0405 | 80.2109 | 82.6002 | 69.0599
535.3167 | 246.1519 | 38.8413 | 272.7139 | 313.1398 | 287.3062 | 80.4261 | 82.8238 | 69.2469
536.3167 | 246.0487 | 38.9633 | 272.3685 | 312.4209 | 286.6242 | 80.6303 | 83.0014 | 69.4159
537.3167 | 246.5119 | 39.0866 | 272.4723 | 311.8757 | 285.2222 | 80.8316 | 83.2251 | 69.5821
538.3167 | 246.0954 | 39.2078 | 271.9984 | 311.7098 | 284.3509 | 81.0388 | 83.4201 | 69.7602
539.3167 | 245.4192 | 39.3184 | 272.065 | 311.9437 | 284.4898 | 81.248 | 83.6392 | 69.9163
540.3167 | 246.641 | 39.4379 | 271.5295 | 312.0051 | 283.2974 | 81.4594 | 83.8317 | 70.0948
541.3167 | 246.681 | 39.5521 | 273.0835 | 311.9017 | 283.5046 | 81.6777 | 84.0564 | 70.2189
542.3167 | 246.9505 | 39.6653 | 273.47 | 312.5703 | 283.1699 | 81.8838 | 84.2322 | 70.4305
543.3167 | 248.0272 | 39.773 | 273.4167 | 312.5842 | 282.5782 | 82.1084 | 84.4582 | 70.5799
544.3167 | 248.6394 | 39.889 | 272.9196 | 312.9813 | 283.1274 | 82.3179 | 84.6772 | 70.7415
545.3167 | 249.229 | 39.9987 | 273.2676 | 313.3366 | 282.8044 | 82.5117 | 84.8867 | 70.929
546.3167 | 249.3467 | 40.1186 | 272.1704 | 313.0296 | 281.9049 | 82.7307 | 85.1145 | 71.078
547.3167 | 249.6013 | 40.2443 | 272.1694 | 314.2298 | 282.0046 | 82.9182 | 85.3311 | 71.2566
548.3167 | 249.4355 | 40.3645 | 273.2729 | 315.1099 | 282.4695 | 83.1169 | 85.538 | 71.4288
549.3167 | 249.6382 | 40.4752 | 273.3331 | 314.3383 | 283.333 | 83.3234 | 85.7461 | 71.6104
550.3167 | 250.2064 | 40.5862 | 273.753 | 314.2427 | 282.4612 | 83.5506 | 85.9626 | 71.7649
551.3167 | 250.7005 | 40.7041 | 275.3602 | 313.9572 | 281.5243 | 83.746 | 86.1752 | 71.9195
552.3167 | 250.5811 | 40.813 | 275.2481 | 313.9079 | 280.132 | 83.9514 | 86.3857 | 72.0742
553.3167 | 249.554 | 40.91 | 275.7816 | 314.1698 | 280.983 | 84.1636 | 86.6084 | 72.247
554.3167 | 249.7184 | 41.0328 | 276.093 | 313.8076 | 279.4278 | 84.3726 | 86.8234 | 72.4242
555.3167 | 249.9815 | 41.1368 | 275.7451 | 314.1665 | 278.5925 | 84.5746 | 87.0402 | 72.5858
556.3167 | 249.7935 | 41.2519 | 275.8522 | 314.1105 | 278.6138 | 84.781 | 87.273 | 72.7524
557.3167 | 250.3561 | 41.358 | 275.2695 | 313.5572 | 278.0323 | 84.9894 | 87.4609 | 72.9214
558.3167 | 250.6351 | 41.4651 | 276.5921 | 313.1188 | 278.1918 | 85.1741 | 87.6822 | 73.0944
559.3167 | 250.839 | 41.595 | 278.0454 | 314.634 | 279.1005 | 85.3826 | 87.8953 | 73.2234
560.3167 | 250.9085 | 41.7168 | 278.7733 | 315.4231 | 281.1595 | 85.5872 | 88.1234 | 73.4216
561.3167 | 250.2359 | 41.8287 | 277.5772 | 315.1474 | 282.3059 | 85.8066 | 88.3393 | 73.5848
562.3167 | 250.1292 | 41.9333 | 278.9254 | 315.105 | 281.4755 | 86.0099 | 88.5447 | 73.7519
563.3167 | 250.5217 | 42.053 | 281.4794 | 316.6142 | 281.9118 | 86.2158 | 88.7589 | 73.908
564.3167 | 250.6427 | 42.1717 | 281.4066 | 316.5227 | 283.4553 | 86.4261 | 89.0042 | 74.1073
565.3167 | 251.7419 | 42.2886 | 281.8784 | 317.5678 | 285.9408 | 86.6705 | 89.186 | 74.2452
566.3167 | 251.7402 | 42.3977 | 279.5868 | 316.8817 | 285.9666 | 86.8673 | 89.4212 | 74.4384
567.3167 | 252.3353 | 42.5249 | 278.7884 | 316.4549 | 286.3421 | 87.0666 | 89.6143 | 74.5814
568.3167 | 252.0803 | 42.6417 | 277.2754 | 315.4518 | 286.7925 | 87.2699 | 89.8365 | 74.7564
569.3167 | 252.3975 | 42.7547 | 277.4609 | 315.0141 | 286.1667 | 87.4748 | 90.06 | 74.936
570.3167 | 252.2589 | 42.8688 | 276.3182 | 314.2516 | 286.187 | 87.6754 | 90.2971 | 75.093
571.3167 | 252.7421 | 42.9942 | 276.5943 | 315.9975 | 287.4465 | 87.8912 | 90.5147 | 75.2568
572.3167 | 253.2407 | 43.1151 | 277.7722 | 314.8301 | 286.3633 | 88.1181 | 90.7448 | 75.4511
573.3167 | 253.4846 | 43.2348 | 278.5186 | 315.5143 | 287.0503 | 88.3217 | 90.9647 | 75.5841
574.3167 | 253.9401 | 43.3467 | 278.8799 | 315.7941 | 288.2827 | 88.528 | 91.1817 | 75.7357
575.3167 | 253.8126 | 43.4574 | 278.0754 | 315.1424 | 288.5938 | 88.7351 | 91.4226 | 75.9037
576.3167 | 253.3407 | 43.5776 | 278.901 | 315.952 | 289.845 | 88.9426 | 91.6477 | 76.0659
577.3167 | 253.4901 | 43.6911 | 278.8607 | 317.5972 | 291.0542 | 89.1611 | 91.9058 | 76.2332
578.3167 | 253.9737 | 43.8006 | 278.2721 | 318.9428 | 292.5904 | 89.3624 | 92.1088 | 76.4105
579.3167 | 254.0685 | 43.9171 | 278.8144 | 320.0753 | 294.6087 | 89.5974 | 92.3768 | 76.5704
580.3167 | 254.0618 | 44.0405 | 279.4348 | 320.4153 | 295.1002 | 89.7783 | 92.5868 | 76.7789
581.3167 | 253.7408 | 44.1549 | 280.9819 | 320.5533 | 294.2721 | 89.9961 | 92.8208 | 76.9357
582.3167 | 253.635 | 44.2693 | 280.8111 | 321.6008 | 294.7177 | 90.1951 | 93.0643 | 77.0845
583.3167 | 253.5208 | 44.3813 | 282.0418 | 321.1766 | 293.7797 | 90.4054 | 93.3164 | 77.2544
584.3167 | 253.6879 | 44.4931 | 282.0834 | 320.6646 | 293.399 | 90.6101 | 93.5511 | 77.4394
585.3167 | 254.7244 | 44.6149 | 282.8782 | 320.8053 | 293.273 | 90.8155 | 93.799 | 77.6149
586.3167 | 254.5642 | 44.728 | 283.9163 | 320.0556 | 292.4373 | 91.0242 | 94.0195 | 77.7788
587.3167 | 254.7138 | 44.8429 | 283.8433 | 320.5153 | 291.8492 | 91.2352 | 94.2869 | 77.9508
588.3167 | 255.6143 | 44.9447 | 284.511 | 321.0333 | 291.2904 | 91.4169 | 94.5228 | 78.1324
589.3167 | 255.6824 | 45.0704 | 286.0464 | 321.87 | 291.3431 | 91.6411 | 94.7329 | 78.2845
590.3167 | 255.7306 | 45.1834 | 285.9027 | 321.4476 | 291.1472 | 91.8356 | 94.9919 | 78.4516
591.3167 | 255.7304 | 45.2971 | 285.9492 | 321.8041 | 291.1392 | 92.0198 | 95.2233 | 78.6204
592.3167 | 255.4008 | 45.4156 | 286.6149 | 321.784 | 292.4223 | 92.2106 | 95.4545 | 78.8047
593.3167 | 255.0047 | 45.5322 | 286.7071 | 322.5594 | 293.3235 | 92.3967 | 95.6996 | 78.9656
594.3167 | 254.8011 | 45.6391 | 287.5625 | 323.5263 | 294.4779 | 92.577 | 95.9098 | 79.1199
595.3167 | 255.095 | 45.7448 | 288.1362 | 323.4339 | 295.6479 | 92.7538 | 96.154 | 79.3015
596.3167 | 255.6666 | 45.8675 | 286.7042 | 322.7763 | 295.4508 | 92.9439 | 96.4041 | 79.4412
597.3167 | 255.8734 | 45.9859 | 288.0342 | 324.371 | 296.3321 | 93.1218 | 96.6564 | 79.6312
598.3167 | 256.1365 | 46.1004 | 289.5489 | 324.9667 | 297.1384 | 93.3144 | 96.8565 | 79.7858
599.3167 | 256.2667 | 46.2165 | 288.6447 | 323.8088 | 296.6597 | 93.4997 | 97.1065 | 79.9517
600.3167 | 256.669 | 46.3278 | 288.3133 | 324.5812 | 297.0438 | 93.6698 | 97.3448 | 80.154
601.3167 | 256.5629 | 46.4395 | 287.6955 | 325.2155 | 295.799 | 93.8624 | 97.5894 | 80.2886
602.3167 | 256.4189 | 46.552 | 287.2911 | 325.9904 | 294.6948 | 94.0257 | 97.8224 | 80.4687
603.3167 | 257.1226 | 46.6726 | 287.089 | 325.5002 | 292.798 | 94.2145 | 98.0633 | 80.6436
604.3167 | 257.541 | 46.792 | 286.8438 | 325.9283 | 292.9093 | 94.3748 | 98.3028 | 80.8114
605.3167 | 258.0411 | 46.8995 | 286.9889 | 325.7738 | 292.614 | 94.5775 | 98.5111 | 80.9891
606.3167 | 258.5194 | 47.0151 | 285.8325 | 325.1251 | 292.2059 | 94.7693 | 98.7663 | 81.1551
607.3167 | 258.9028 | 47.133 | 285.1075 | 324.4073 | 291.4303 | 94.953 | 98.9705 | 81.3099
608.3167 | 259.0732 | 47.2503 | 285.3421 | 324.2677 | 291.4625 | 95.1435 | 99.2237 | 81.4915
609.3167 | 259.0135 | 47.3699 | 284.7987 | 323.9737 | 290.4711 | 95.3231 | 99.4469 | 81.6707
610.3167 | 259.304 | 47.4957 | 285.2961 | 324.1051 | 289.9742 | 95.5205 | 99.6896 | 81.8318
611.3167 | 259.8594 | 47.6226 | 286.432 | 324.4615 | 290.0841 | 95.7 | 99.9096 | 82.0357
612.3167 | 259.949 | 47.7666 | 285.8281 | 324.2165 | 290.6475 | 95.8731 | 100.1376 | 82.2293
613.3167 | 260.2182 | 47.8899 | 287.2176 | 324.7383 | 289.7776 | 96.0487 | 100.3699 | 82.432
614.3167 | 260.4063 | 48.0167 | 287.5865 | 324.1946 | 289.267 | 96.2363 | 100.5715 | 82.6617
615.3167 | 260.2057 | 48.1457 | 287.6008 | 323.7811 | 288.0385 | 96.3848 | 100.8225 | 82.8959
616.3167 | 260.7524 | 48.2714 | 288.1877 | 324.0114 | 287.3628 | 96.538 | 101.0495 | 83.1622
617.3167 | 260.1868 | 48.4024 | 289.2667 | 324.4156 | 287.3464 | 96.6942 | 101.2856 | 83.427
618.3167 | 260.5129 | 48.5255 | 289.4128 | 324.1836 | 288.6269 | 96.7882 | 101.529 | 83.7339
619.3167 | 260.2869 | 48.649 | 290.0823 | 324.4073 | 288.3542 | 96.7751 | 101.7464 | 84.0462
620.3167 | 260.3651 | 48.7767 | 290.139 | 324.9828 | 290.0733 | 96.2642 | 101.9887 | 84.3433
621.3167 | 260.2047 | 48.901 | 290.3622 | 324.4751 | 288.7586 | 95.8597 | 102.237 | 84.6782
622.3167 | 260.633 | 49.0231 | 291.5956 | 324.9752 | 287.3525 | 95.6156 | 102.4505 | 85.019
623.3167 | 261.5198 | 49.1392 | 292.3052 | 324.9294 | 289.0875 | 95.4981 | 102.692 | 85.3774
624.3167 | 261.738 | 49.2587 | 293.0718 | 325.4162 | 290.3371 | 95.4781 | 102.9056 | 85.7141
625.3167 | 262.226 | 49.3914 | 292.5845 | 324.7197 | 289.8456 | 95.4926 | 103.1476 | 86.0565
626.3167 | 263.0588 | 49.5216 | 290.691 | 325.4804 | 290.2471 | 95.5653 | 103.3727 | 86.3981
627.3167 | 263.4216 | 49.6382 | 291.3519 | 326.3866 | 290.5188 | 95.6136 | 103.5953 | 86.7479
628.3167 | 263.598 | 49.7642 | 290.6118 | 325.6264 | 290.5259 | 95.7653 | 103.8418 | 87.067
629.3167 | 263.0157 | 49.8857 | 290.0365 | 325.03 | 290.431 | 95.8879 | 104.0763 | 87.3608
630.3167 | 262.9886 | 50.0132 | 289.6788 | 324.6774 | 289.7844 | 96.0585 | 104.2948 | 87.659
631.3167 | 263.0138 | 50.1322 | 289.2909 | 324.6382 | 288.633 | 96.2121 | 104.5418 | 87.9125
632.3167 | 263.7786 | 50.2522 | 291.0223 | 325.6023 | 289.6972 | 96.3803 | 104.7388 | 88.1708
633.3167 | 265.0964 | 50.3716 | 290.4906 | 325.4296 | 289.2882 | 96.5269 | 104.9645 | 88.382
634.3167 | 265.2471 | 50.5 | 292.1411 | 326.2805 | 290.7724 | 96.6662 | 105.1864 | 88.6302
635.3167 | 265.179 | 50.6205 | 293.4764 | 327.3117 | 292.404 | 96.8278 | 105.4256 | 88.8557
636.3167 | 264.7337 | 50.7439 | 296.5548 | 328.0476 | 293.4369 | 97.0958 | 105.6552 | 89.1302
637.3167 | 264.6567 | 50.8951 | 296.3447 | 328.5745 | 295.3258 | 97.3743 | 105.9186 | 89.3803
638.3167 | 265.7899 | 51.1182 | 297.5812 | 329.6827 | 297.8031 | 98.7118 | 106.3229 | 89.9571
639.3167 | 265.1165 | 51.1492 | 299.0806 | 330.8057 | 300.2597 | 97.9484 | 106.3897 | 89.8579
640.3167 | 264.4127 | 51.2828 | 297.8872 | 331.8505 | 301.3684 | 98.318 | 106.6763 | 90.1384
641.3167 | 264.6836 | 51.3455 | 296.8395 | 331.4203 | 301.8881 | 97.6628 | 106.7848 | 90.0463
642.3167 | 265.7815 | 51.4733 | 296.4609 | 331.9299 | 302.8721 | 97.7779 | 106.9896 | 90.1893
643.3167 | 266.5627 | 51.6078 | 297.0869 | 332.7134 | 304.3085 | 97.8741 | 107.2149 | 90.3462
644.3167 | 267.0735 | 51.7205 | 298.356 | 333.042 | 306.5856 | 97.9781 | 107.4591 | 90.4828
645.3167 | 267.95 | 51.8331 | 299.2483 | 333.4228 | 309.2112 | 98.0919 | 107.6827 | 90.6404
646.3167 | 268.5787 | 51.9469 | 300.0436 | 334.9454 | 309.7317 | 98.1971 | 107.8821 | 90.8057
647.3167 | 268.6754 | 52.0602 | 300.2796 | 335.682 | 310.9925 | 98.2954 | 108.1351 | 90.9176
648.3167 | 269.9805 | 52.1776 | 298.0821 | 335.2502 | 312.3591 | 98.4032 | 108.3485 | 91.0524
649.3167 | 270.249 | 52.2814 | 297.0955 | 335.4884 | 312.5539 | 98.4993 | 108.5835 | 91.166
650.3167 | 270.2398 | 52.3909 | 296.0494 | 334.9232 | 311.4915 | 98.6104 | 108.8009 | 91.2491
651.3167 | 270.5401 | 52.5062 | 295.9098 | 334.3023 | 310.978 | 98.6736 | 109.0236 | 91.3694
652.3167 | 270.6512 | 52.6354 | 298.227 | 335.1002 | 310.6276 | 98.7762 | 109.2477 | 91.4973
653.3167 | 270.9777 | 52.7224 | 298.1421 | 336.5512 | 310.1733 | 98.865 | 109.4875 | 91.5941
654.3167 | 271.3604 | 52.8159 | 298.1089 | 336.6227 | 310.8972 | 98.9629 | 109.7148 | 91.699
655.3167 | 271.1421 | 52.7863 | 299.6256 | 337.4228 | 310.5724 | 99.0822 | 109.9351 | 91.8123
656.3167 | 270.949 | 52.8424 | 300.6144 | 339.2447 | 310.7547 | 99.1625 | 110.1801 | 91.9045
657.3167 | 271.0792 | 52.9666 | 298.7142 | 339.2665 | 310.4771 | 99.286 | 110.3856 | 91.9881
658.3167 | 271.9395 | 53.0961 | 297.6269 | 338.1673 | 309.3181 | 99.3654 | 110.6214 | 92.076
659.3167 | 272.2264 | 53.2204 | 298.6883 | 338.0765 | 308.6652 | 99.4597 | 110.8469 | 92.1604
660.3167 | 272.3652 | 53.3405 | 299.2584 | 338.9407 | 310.5555 | 99.5525 | 111.0552 | 92.2433
661.3167 | 271.4645 | 53.4461 | 299.4659 | 339.8033 | 311.362 | 99.6693 | 111.2935 | 92.3356
662.3167 | 272.7757 | 53.5624 | 301.2028 | 340.1407 | 311.5846 | 99.7563 | 111.5299 | 92.3931
663.3167 | 273.3527 | 53.7014 | 300.3593 | 339.6948 | 312.2043 | 99.8728 | 111.758 | 92.4709
664.3167 | 274.6198 | 53.8894 | 299.8078 | 339.5348 | 312.6997 | 99.9786 | 111.9753 | 92.5706
665.3167 | 274.938 | 54.0302 | 301.1943 | 340.0442 | 313.8537 | 100.0746 | 112.1993 | 92.6411
666.3167 | 274.7164 | 54.1447 | 301.8886 | 341.6553 | 315.554 | 100.175 | 112.4318 | 92.7162
667.3167 | 274.4666 | 54.256 | 302.7771 | 342.31 | 316.3232 | 100.288 | 112.6558 | 92.8034
668.3167 | 274.2529 | 54.3893 | 304.674 | 342.7179 | 314.6379 | 100.4073 | 112.907 | 92.8492
669.3167 | 274.4979 | 54.5404 | 305.6952 | 342.9924 | 313.934 | 100.4898 | 113.135 | 92.8953
670.3167 | 274.5831 | 54.6835 | 307.5133 | 343.7539 | 314.1704 | 100.5897 | 113.3525 | 92.9678
671.3167 | 276.1707 | 54.7803 | 309.816 | 345.107 | 314.4193 | 100.695 | 113.5946 | 92.9938
672.3167 | 276.547 | 54.8959 | 310.1493 | 344.4106 | 312.3632 | 100.8059 | 113.8301 | 93.0557
673.3167 | 276.5501 | 55.0358 | 309.5533 | 345.5948 | 313.055 | 100.8944 | 114.0594 | 93.0969
674.3167 | 276.7221 | 55.139 | 308.8236 | 346.3476 | 312.2812 | 100.9881 | 114.3157 | 93.1199
675.3167 | 277.8062 | 55.2106 | 308.2424 | 346.245 | 311.4872 | 101.1057 | 114.534 | 93.1683
676.3167 | 277.0166 | 55.3056 | 309.6875 | 346.4235 | 311.8409 | 101.1917 | 114.795 | 93.2211
677.3167 | 277.3269 | 55.3829 | 310.8836 | 347.6927 | 313.6486 | 101.2963 | 115.0347 | 93.2663
678.3167 | 278.7498 | 55.4915 | 311.4887 | 348.6542 | 313.8092 | 101.3863 | 115.2887 | 93.2158
679.3167 | 279.3072 | 55.5824 | 310.5766 | 348.2202 | 313.2668 | 101.466 | 115.5465 | 93.2635
680.3167 | 278.9482 | 55.6951 | 309.9686 | 347.9642 | 313.796 | 101.5323 | 115.8047 | 93.3032
681.3167 | 279.1213 | 55.7966 | 308.5244 | 347.6451 | 312.7905 | 101.6057 | 116.0587 | 93.3349
682.3167 | 279.5076 | 55.9009 | 307.854 | 347.4569 | 313.7792 | 101.7073 | 116.3302 | 93.3871
683.3167 | 277.9951 | 56.0167 | 307.2647 | 346.5388 | 313.3974 | 101.7857 | 116.594 | 93.4119
684.3167 | 277.3406 | 56.1335 | 306.5706 | 346.3094 | 313.3395 | 101.8506 | 116.8838 | 93.4899
685.3167 | 277.0255 | 56.2539 | 306.5293 | 346.9209 | 314.0045 | 101.9137 | 117.1615 | 93.547
686.3167 | 276.8888 | 56.3967 | 306.4687 | 346.1286 | 312.707 | 101.9782 | 117.4425 | 93.583
687.3167 | 277.1654 | 56.5247 | 306.0762 | 345.1582 | 310.9372 | 102.0749 | 117.7611 | 93.6492
688.3167 | 276.8693 | 56.6513 | 306.8859 | 345.4332 | 308.7084 | 102.1608 | 118.0598 | 93.7299
689.3167 | 277.1874 | 56.7805 | 307.408 | 345.3389 | 306.9264 | 102.2386 | 118.3469 | 93.7753
690.3167 | 278.1311 | 56.8989 | 308.1233 | 345.9407 | 305.6048 | 102.2951 | 118.6802 | 93.8403
691.3167 | 277.4537 | 57.0246 | 308.7932 | 345.5742 | 304.7215 | 102.3739 | 118.9985 | 93.9326
692.3167 | 277.1472 | 57.1376 | 309.4486 | 345.7983 | 305.0959 | 102.4471 | 119.3314 | 94.003
693.3167 | 276.4415 | 57.3278 | 310.2334 | 344.7268 | 305.9162 | 102.5488 | 119.694 | 94.0802
694.3167 | 277.1213 | 57.4125 | 310.5579 | 344.1865 | 305.1045 | 102.6163 | 120.0532 | 94.1812
695.3167 | 277.6862 | 57.5218 | 310.382 | 343.7024 | 306.1934 | 102.6973 | 120.4011 | 94.2622
696.3167 | 278.3736 | 57.6228 | 310.8309 | 343.7111 | 307.2852 | 102.7849 | 120.7593 | 94.3573
697.3167 | 278.4024 | 57.7521 | 312.288 | 344.5297 | 308.1552 | 102.8674 | 121.1579 | 94.4644
698.3167 | 279.2083 | 57.867 | 312.8182 | 344.8548 | 309.4493 | 102.9518 | 121.5492 | 94.5538
699.3167 | 279.655 | 57.9924 | 313.7694 | 346.1874 | 310.9058 | 103.0289 | 121.9381 | 94.6453
700.3167 | 280.0089 | 58.0812 | 314.1556 | 346.5679 | 311.6237 | 103.0922 | 122.3633 | 94.7257
701.3167 | 280.1213 | 58.2569 | 314.1297 | 346.6256 | 311.5974 | 103.1812 | 122.7158 | 94.8143
702.3167 | 280.2098 | 58.3507 | 313.4873 | 345.5829 | 310.5751 | 103.2971 | 123.1141 | 94.9171
703.3167 | 280.7295 | 58.4286 | 311.0686 | 344.708 | 310.9405 | 103.3652 | 123.492 | 95.0177
704.3167 | 280.9929 | 58.5603 | 310.7061 | 344.1412 | 311.3984 | 103.4825 | 123.8629 | 95.1129
705.3167 | 281.4009 | 58.66 | 309.5239 | 343.5879 | 312.1238 | 103.5956 | 124.238 | 95.235
706.3167 | 281.3609 | 58.7787 | 308.3721 | 342.5351 | 311.7257 | 103.711 | 124.56 | 95.3357
707.3167 | 281.4462 | 58.8715 | 307.1367 | 342.1465 | 310.2209 | 103.8812 | 124.9225 | 95.4187
708.3167 | 282.1004 | 58.9957 | 306.1838 | 342.5995 | 310.4608 | 104.071 | 125.3177 | 95.5463
709.3167 | 283.0793 | 59.1369 | 305.8687 | 341.8553 | 309.6833 | 104.2973 | 125.6513 | 95.6617
710.3167 | 283.088 | 59.2743 | 306.1537 | 342.9361 | 309.9656 | 104.5446 | 126.0135 | 95.7668
711.3167 | 283.0892 | 59.3882 | 306.1549 | 343.0153 | 311.4636 | 104.7981 | 126.3736 | 95.8931
712.3167 | 282.6967 | 59.4816 | 305.0073 | 342.7674 | 313.7318 | 105.0965 | 126.7095 | 96.0327
713.3167 | 281.7778 | 59.6242 | 304.0443 | 343.421 | 314.5288 | 105.3769 | 127.0627 | 96.1427
714.3167 | 281.7439 | 59.7857 | 303.7084 | 343.2037 | 313.6361 | 105.7053 | 127.4172 | 96.2479
715.3167 | 282.2439 | 59.9489 | 302.8756 | 343.4003 | 313.2127 | 106.0706 | 127.7324 | 96.3715
716.3167 | 282.9784 | 60.1073 | 302.0312 | 342.6828 | 312.5804 | 106.4458 | 128.0836 | 96.5088
717.3167 | 283.6547 | 60.2454 | 301.663 | 342.1755 | 312.5884 | 106.8501 | 128.4149 | 96.6237
718.3167 | 284.0941 | 60.3964 | 300.456 | 342.3008 | 312.1165 | 107.2542 | 128.7473 | 96.7446
719.3167 | 283.9177 | 60.5031 | 300.6268 | 342.524 | 310.9883 | 107.6826 | 129.0978 | 96.8877
720.3167 | 284.1363 | 60.6729 | 299.2128 | 342.2899 | 310.1527 | 108.1054 | 129.4347 | 97.0112
721.3167 | 284.6933 | 61.0476 | 299.4681 | 342.1694 | 309.3266 | 108.4977 | 129.7604 | 97.1593
722.3167 | 284.2067 | 61.3812 | 299.4361 | 342.3432 | 308.5171 | 108.8878 | 130.1104 | 97.2759
723.3167 | 284.3408 | 61.6077 | 298.8494 | 342.3142 | 308.3537 | 109.2593 | 130.4397 | 97.4148
724.3167 | 284.8638 | 61.8478 | 300.563 | 342.0734 | 307.9554 | 109.612 | 130.757 | 97.5553
725.3167 | 285.1202 | 62.0407 | 301.4949 | 341.82 | 306.4141 | 109.9498 | 131.0909 | 97.6565
726.3167 | 285.4727 | 62.2101 | 303.1308 | 342.2321 | 306.4489 | 110.3047 | 131.3961 | 97.784
727.3167 | 285.0983 | 62.3406 | 304.9942 | 342.8656 | 306.5003 | 110.636 | 131.7101 | 97.9173
728.3167 | 285.097 | 62.4529 | 306.587 | 343.9116 | 306.2995 | 110.9699 | 132.0294 | 98.0294
729.3167 | 285.2163 | 62.5563 | 309.158 | 345.073 | 307.616 | 111.2923 | 132.3728 | 98.1288
730.3167 | 285.2842 | 62.6936 | 310.8193 | 345.6752 | 308.3363 | 111.6125 | 132.6934 | 98.2581
731.3167 | 284.8696 | 62.8507 | 311.8834 | 347.208 | 309.5397 | 111.9164 | 133.003 | 98.3305
732.3167 | 285.8377 | 62.9533 | 313.231 | 348.1444 | 310.8081 | 112.2237 | 133.3383 | 98.455
733.3167 | 285.5999 | 63.0285 | 312.1524 | 348.9873 | 312.8017 | 112.5286 | 133.6449 | 98.5476
734.3167 | 287.0563 | 63.1101 | 312.3742 | 349.0979 | 313.3806 | 112.8484 | 133.9733 | 98.6645
735.3167 | 285.6803 | 63.2395 | 312.1127 | 349.2575 | 314.6126 | 113.1517 | 134.2805 | 98.7775
736.3167 | 285.5209 | 63.3516 | 312.9751 | 348.6651 | 314.9776 | 113.4585 | 134.5994 | 98.8797
737.3167 | 285.2141 | 63.4902 | 311.531 | 348.5953 | 315.2029 | 113.7718 | 134.934 | 98.9853
738.3167 | 285.061 | 63.6323 | 312.2496 | 348.5774 | 314.9123 | 114.0917 | 135.2586 | 99.1177
739.3167 | 285.4895 | 63.8162 | 312.8177 | 349.0039 | 314.8566 | 114.4283 | 135.5326 | 99.2648
740.3167 | 287.4461 | 63.9903 | 313.6689 | 349.273 | 315.3321 | 114.7507 | 135.8692 | 99.3815
741.3167 | 287.5354 | 64.1893 | 313.0726 | 349.3832 | 315.7047 | 115.0879 | 136.1714 | 99.5321
742.3167 | 287.7106 | 64.3292 | 312.452 | 349.4612 | 315.6744 | 115.4459 | 136.4918 | 99.6766
743.3167 | 288.0845 | 64.4313 | 312.1014 | 349.4285 | 315.9809 | 115.7975 | 136.8153 | 99.8195
744.3167 | 287.9404 | 64.6021 | 313.043 | 349.9566 | 315.2679 | 116.1403 | 137.1233 | 99.9402
745.3167 | 288.6118 | 64.7584 | 314.8108 | 350.9101 | 316.2365 | 116.5084 | 137.4395 | 100.0809
746.3167 | 289.8855 | 64.8953 | 316.1668 | 351.2113 | 317.1478 | 116.8536 | 137.7489 | 100.1718
747.3167 | 291.1493 | 65.1203 | 316.4806 | 351.8575 | 319.522 | 117.1809 | 138.0644 | 100.2651
748.3167 | 292.0171 | 65.4398 | 317.8566 | 352.9413 | 319.8649 | 119.5003 | 138.7351 | 101.0947
749.3167 | 292.0748 | 65.4203 | 316.7973 | 351.5812 | 320.423 | 117.8293 | 138.7276 | 100.4748
750.3167 | 292.4157 | 65.7418 | 317.7244 | 352.2725 | 320.2108 | 119.4997 | 139.2846 | 101.0759
751.3167 | 292.226 | 65.6811 | 317.9799 | 352.9221 | 322.4111 | 118.4434 | 139.3797 | 100.6644
752.3167 | 292.0896 | 65.8491 | 319.4159 | 353.9209 | 324.5092 | 119.0912 | 139.708 | 100.8884
753.3167 | 292.2205 | 66.0674 | 320.1213 | 354.2599 | 325.4742 | 119.9126 | 140.1657 | 101.1261
754.3167 | 293.0707 | 66.0546 | 318.82 | 355.9815 | 326.8067 | 119.377 | 140.3267 | 100.9526
755.3167 | 293.1819 | 66.2024 | 318.8137 | 356.4803 | 325.9711 | 119.6638 | 140.6628 | 101.0773
756.3167 | 293.8478 | 66.3493 | 318.3729 | 356.1054 | 324.1272 | 119.9678 | 140.9604 | 101.1413
757.3167 | 294.1188 | 66.4717 | 317.1044 | 355.6385 | 324.5655 | 120.2541 | 141.2913 | 101.2156
758.3167 | 293.6906 | 66.6796 | 316.1899 | 355.1656 | 323.4376 | 121.3325 | 141.7543 | 101.5867
759.3167 | 293.5786 | 66.8013 | 314.8464 | 354.3589 | 322.1431 | 121.1229 | 142.0205 | 101.5047
760.3167 | 293.4346 | 66.8945 | 313.8102 | 353.9916 | 321.6612 | 121.4109 | 142.3221 | 101.6112
761.3167 | 294.2091 | 66.9943 | 313.3551 | 353.1489 | 321.7269 | 121.3825 | 142.5954 | 101.608
762.3167 | 295.0729 | 67.0784 | 313.6043 | 353.325 | 321.1397 | 121.6533 | 142.9148 | 101.7751
763.3167 | 295.1081 | 67.044 | 312.9244 | 352.9968 | 319.5312 | 121.9149 | 143.2352 | 101.9346
764.3167 | 295.7563 | 67.1626 | 315.0345 | 352.8721 | 318.4366 | 122.148 | 143.551 | 102.0906
765.3167 | 295.2638 | 67.4244 | 315.0354 | 352.6529 | 316.6252 | 122.4121 | 143.8956 | 102.2546
766.3167 | 295.4319 | 67.6931 | 315.7323 | 352.8537 | 315.9441 | 124.3839 | 144.5567 | 103.0647
767.3167 | 295.6417 | 67.8889 | 314.4364 | 353.0916 | 316.4399 | 123.2778 | 144.6289 | 102.7031
768.3167 | 295.7685 | 68.2146 | 313.6943 | 353.1573 | 317.3783 | 124.135 | 145.0353 | 103.0646
769.3167 | 295.022 | 68.3531 | 313.147 | 352.7942 | 317.0727 | 123.4523 | 145.248 | 102.9366
770.3167 | 295.2606 | 68.4867 | 314.5196 | 353.9392 | 316.2625 | 123.7668 | 145.6276 | 103.1366
771.3167 | 295.4345 | 68.6568 | 313.2282 | 354.1636 | 316.9151 | 123.9538 | 145.9409 | 103.2653
772.3167 | 295.8562 | 68.7847 | 311.7729 | 354.223 | 317.3309 | 124.1937 | 146.2699 | 103.4491
773.3167 | 295.8484 | 68.9813 | 312.4007 | 354.2818 | 316.8186 | 124.4573 | 146.6213 | 103.6091
774.3167 | 296.1489 | 69.1351 | 312.3702 | 354.4895 | 315.5949 | 124.6873 | 146.932 | 103.7692
775.3167 | 296.3559 | 69.3512 | 311.4814 | 353.5972 | 314.149 | 124.9577 | 147.2765 | 103.9264
776.3167 | 296.5381 | 69.5217 | 311.9755 | 354.585 | 314.5313 | 125.1932 | 147.6288 | 104.1201
777.3167 | 296.4017 | 69.7136 | 313.0771 | 355.753 | 314.9322 | 125.8339 | 148.0351 | 104.3874
778.3167 | 297.1668 | 69.908 | 313.3412 | 356.1302 | 315.5388 | 125.6864 | 148.3247 | 104.444
779.3167 | 296.8655 | 70.0452 | 314.3526 | 356.4268 | 315.6049 | 125.9216 | 148.6727 | 104.5793
780.3167 | 297.3195 | 70.1652 | 314.1483 | 356.3097 | 315.9845 | 126.203 | 149.0242 | 104.7412
781.3167 | 298.4979 | 70.2676 | 312.8342 | 356.5051 | 315.6963 | 126.4838 | 149.3659 | 104.9227
782.3167 | 299.1206 | 70.4261 | 313.6264 | 356.5994 | 315.7638 | 126.753 | 149.7455 | 105.0934
783.3167 | 299.5429 | 70.631 | 314.5792 | 356.734 | 316.2653 | 127.0019 | 150.0794 | 105.261
784.3167 | 300.1172 | 70.7944 | 314.5813 | 356.5525 | 317.3949 | 127.2595 | 150.4339 | 105.4181
785.3167 | 300.139 | 70.9433 | 314.2052 | 356.3034 | 318.3792 | 127.5087 | 150.7744 | 105.5608
786.3167 | 300.0775 | 71.0942 | 313.4555 | 356.1308 | 318.5331 | 127.766 | 151.1307 | 105.7167
787.3167 | 300.3107 | 71.2373 | 311.8268 | 355.6419 | 318.9101 | 127.9721 | 151.4806 | 105.8815
788.3167 | 299.6414 | 71.3347 | 312.4563 | 355.3791 | 318.8929 | 128.2183 | 151.8065 | 106.0251
789.3167 | 299.5303 | 71.4403 | 312.8181 | 356.7334 | 318.8888 | 128.4707 | 152.1491 | 106.1767
790.3167 | 299.3613 | 71.56 | 311.8946 | 356.4928 | 318.2848 | 128.71 | 152.523 | 106.3057
791.3167 | 300.4432 | 71.7644 | 313.4432 | 357.3795 | 316.8001 | 128.9508 | 152.8617 | 106.4723
792.3167 | 299.8236 | 71.9543 | 313.9831 | 357.3992 | 316.9871 | 129.1643 | 153.2253 | 106.6179
793.3167 | 299.752 | 72.1016 | 315.7437 | 358.6265 | 317.1645 | 129.3849 | 153.5692 | 106.7695
794.3167 | 298.9832 | 72.243 | 319.2827 | 358.6703 | 318.0139 | 129.6403 | 153.9098 | 106.9267
795.3167 | 299.1552 | 72.3139 | 322.3803 | 360.3816 | 318.8169 | 129.8524 | 154.2519 | 107.0567
796.3167 | 299.6515 | 72.4112 | 324.1511 | 360.7253 | 320.4667 | 130.0888 | 154.6272 | 107.2298
797.3167 | 300.1041 | 72.5762 | 325.1315 | 361.5609 | 321.6732 | 130.319 | 154.9698 | 107.373
798.3167 | 300.3851 | 72.7286 | 325.0584 | 362.0548 | 323.3966 | 130.5559 | 155.3215 | 107.5154
799.3167 | 300.5017 | 72.8684 | 325.2375 | 362.7099 | 324.2013 | 130.7789 | 155.6772 | 107.6757
800.3167 | 300.8454 | 73.0775 | 325.7397 | 363.0499 | 323.9576 | 131.0271 | 156.0351 | 107.8125
801.3167 | 300.4444 | 73.2789 | 326.85 | 362.919 | 324.8838 | 131.2398 | 156.3583 | 107.9663
802.3167 | 300.4027 | 73.3802 | 326.7839 | 363.7262 | 325.8202 | 131.4388 | 156.6998 | 108.1011
803.3167 | 300.9655 | 73.5375 | 327.0899 | 364.2974 | 325.8178 | 131.6545 | 157.0419 | 108.2396
804.3167 | 301.0323 | 73.709 | 324.9483 | 364.2912 | 326.1575 | 131.8584 | 157.3997 | 108.3896
805.3167 | 301.789 | 73.7947 | 323.2182 | 364.6759 | 325.2648 | 132.0968 | 157.7369 | 108.5284
806.3167 | 300.7948 | 73.9388 | 322.4325 | 364.4346 | 324.7245 | 132.295 | 158.0681 | 108.6823
807.3167 | 300.8162 | 74.0731 | 323.2786 | 364.2262 | 324.4719 | 132.5388 | 158.4236 | 108.8357
808.3167 | 301.2515 | 74.2177 | 325.3328 | 364.9659 | 325.2919 | 132.7517 | 158.7775 | 108.9862
809.3167 | 301.2358 | 74.4152 | 326.6426 | 365.8825 | 326.5757 | 132.9892 | 159.1076 | 109.1262
810.3167 | 301.3239 | 74.5583 | 327.6618 | 366.7108 | 327.4737 | 133.2133 | 159.4347 | 109.2665
811.3167 | 301.4662 | 74.7173 | 325.8723 | 366.8842 | 327.9445 | 133.4118 | 159.7799 | 109.424
812.3167 | 302.1537 | 74.8556 | 325.8663 | 368.1502 | 329.7041 | 133.6569 | 160.1082 | 109.566
813.3167 | 303.0719 | 74.9755 | 323.9902 | 367.243 | 330.3165 | 133.8704 | 160.4574 | 109.7281
814.3167 | 303.8389 | 75.1449 | 323.7318 | 367.9973 | 330.6577 | 134.0858 | 160.7945 | 109.8871
815.3167 | 303.9855 | 75.289 | 322.67 | 367.9117 | 331.1306 | 134.2937 | 161.1237 | 110.0328
816.3167 | 302.9952 | 75.4651 | 322.9362 | 367.614 | 331.3873 | 134.5052 | 161.446 | 110.1899
817.3167 | 302.4795 | 75.6463 | 322.3815 | 368.189 | 330.8665 | 134.7112 | 161.7849 | 110.365
818.3167 | 302.9771 | 75.8354 | 323.5756 | 368.718 | 330.8997 | 134.922 | 162.0983 | 110.5228
819.3167 | 303.1911 | 76.0021 | 324.7528 | 369.617 | 330.247 | 135.1176 | 162.4196 | 110.7048
820.3167 | 303.2328 | 76.1814 | 325.0764 | 370.0497 | 330.4873 | 135.3363 | 162.7471 | 110.8773
821.3167 | 303.5478 | 76.3353 | 323.8421 | 369.1752 | 330.77 | 135.5174 | 163.1007 | 111.0643
822.3167 | 303.7067 | 76.4973 | 322.9449 | 367.5224 | 329.1142 | 135.7569 | 163.4333 | 111.2484
823.3167 | 303.1289 | 76.6419 | 323.1358 | 367.7571 | 328.7887 | 136.009 | 163.7384 | 111.4334
824.3167 | 303.2039 | 76.795 | 323.0549 | 367.1813 | 327.5822 | 136.2357 | 164.0664 | 111.6184
825.3167 | 302.9385 | 76.9878 | 324.5712 | 367.6606 | 327.8541 | 136.4643 | 164.399 | 111.7858
826.3167 | 303.0074 | 77.1593 | 324.2743 | 367.3975 | 326.9201 | 136.6521 | 164.7329 | 111.9796
827.3167 | 302.9921 | 77.3162 | 325.6147 | 367.8556 | 325.7308 | 136.8891 | 165.0899 | 112.1418
828.3167 | 303.4839 | 77.495 | 326.6102 | 368.3088 | 326.1875 | 137.1553 | 165.41 | 112.3136
829.3167 | 303.4799 | 77.6514 | 327.2652 | 368.7806 | 327.0038 | 137.3737 | 165.7559 | 112.5051
830.3167 | 302.8132 | 77.8045 | 327.1335 | 368.4972 | 325.541 | 137.6162 | 166.0924 | 112.6916
831.3167 | 302.6807 | 77.9866 | 327.1016 | 368.2339 | 324.8113 | 137.7736 | 166.4245 | 112.8592
832.3167 | 302.5453 | 78.152 | 326.2941 | 367.1256 | 323.0573 | 138.0207 | 166.7567 | 113.0481
833.3167 | 301.9161 | 78.2902 | 326.2539 | 366.7602 | 322.3686 | 138.243 | 167.1036 | 113.2435
834.3167 | 302.7579 | 78.458 | 325.9146 | 365.9487 | 320.1676 | 138.4392 | 167.4342 | 113.4324
835.3167 | 302.5986 | 78.6451 | 326.9572 | 365.7073 | 318.8528 | 138.6758 | 167.7638 | 113.6013
836.3167 | 302.8803 | 78.8126 | 327.0527 | 365.9968 | 318.5294 | 138.9148 | 168.0985 | 113.777
837.3167 | 303.3321 | 78.9701 | 326.568 | 365.6244 | 318.7121 | 139.1587 | 168.4457 | 113.9936
838.3167 | 304.671 | 79.154 | 325.8963 | 365.5212 | 318.4188 | 139.3879 | 168.7721 | 114.1882
839.3167 | 303.6646 | 79.3116 | 324.4637 | 364.8074 | 317.4033 | 139.5851 | 169.1122 | 114.3883
840.3167 | 303.5446 | 79.5116 | 324.749 | 364.2795 | 315.7279 | 139.8522 | 169.4465 | 114.5584
841.3167 | 302.9538 | 79.7044 | 324.8855 | 364.0275 | 315.6964 | 140.0619 | 169.801 | 114.7547
842.3167 | 303.2371 | 79.8926 | 326.4918 | 365.2408 | 316.1897 | 140.2846 | 170.1132 | 114.9527
843.3167 | 302.6535 | 80.0713 | 327.181 | 365.5846 | 316.9949 | 140.5215 | 170.4835 | 115.1498
844.3167 | 302.3648 | 80.2501 | 325.6967 | 365.8444 | 317.1819 | 140.7599 | 170.8018 | 115.3686
845.3167 | 302.0044 | 80.4442 | 325.289 | 365.3466 | 317.009 | 140.9465 | 171.1259 | 115.5688
846.3167 | 302.117 | 80.6232 | 324.8761 | 364.8626 | 317.7805 | 141.2209 | 171.4847 | 115.7692
847.3167 | 301.8447 | 80.7991 | 323.968 | 364.4118 | 318.4854 | 141.4603 | 171.7935 | 115.981
848.3167 | 302.2072 | 80.9633 | 323.5457 | 364.3228 | 318.6409 | 141.7235 | 172.1402 | 116.2103
849.3167 | 302.5431 | 81.1369 | 323.1176 | 365.3743 | 319.2953 | 141.9651 | 172.4827 | 116.4104
850.3167 | 303.1961 | 81.315 | 323.926 | 366.124 | 320.5718 | 142.2436 | 172.8155 | 116.5604
851.3167 | 303.5911 | 81.5037 | 324.1192 | 366.4303 | 319.7854 | 142.4916 | 173.1728 | 116.7719
852.3167 | 304.2497 | 81.6493 | 323.8221 | 366.3878 | 319.8028 | 142.7034 | 173.4857 | 116.985
853.3167 | 305.3575 | 81.8328 | 322.5996 | 365.7778 | 319.0591 | 143.0114 | 173.8565 | 117.235
854.3167 | 306.0173 | 82.0059 | 322.7154 | 365.4572 | 320.0666 | 143.2917 | 174.188 | 117.4909
855.3167 | 306.6562 | 82.1396 | 322.2234 | 365.0116 | 320.7985 | 143.566 | 174.5181 | 117.7202
856.3167 | 307.1235 | 82.2859 | 321.5393 | 364.0107 | 321.0836 | 143.8167 | 174.8599 | 117.9241
857.3167 | 307.1926 | 82.4278 | 319.9822 | 363.8164 | 322.5998 | 144.0097 | 175.2048 | 118.1576
858.3167 | 307.1952 | 82.5764 | 320.5706 | 364.2114 | 323.8608 | 144.3995 | 175.5269 | 118.3797
859.3167 | 307.712 | 82.7411 | 320.8899 | 363.7992 | 323.9034 | 144.59 | 175.864 | 118.5634
860.3167 | 308.8733 | 82.8941 | 321.3639 | 363.5397 | 324.8451 | 144.8279 | 176.2102 | 118.7791
861.3167 | 308.6623 | 83.0615 | 321.8821 | 364.3429 | 325.4209 | 145.0275 | 176.5536 | 118.9966
862.3167 | 308.7713 | 83.2115 | 322.0287 | 364.9161 | 326.8963 | 145.3417 | 176.876 | 119.2051
863.3167 | 309.2998 | 83.3784 | 322.6199 | 366.7413 | 328.7502 | 145.7695 | 177.2197 | 119.4308
864.3167 | 309.3649 | 83.5376 | 322.2578 | 366.7943 | 329.284 | 146.0928 | 177.5504 | 119.6647
865.3167 | 309.9162 | 83.7304 | 320.5246 | 366.2731 | 330.1869 | 146.2214 | 177.8968 | 119.8899
866.3167 | 310.4501 | 83.8989 | 320.4946 | 366.5611 | 331.7695 | 146.694 | 178.2182 | 120.0954
867.3167 | 310.4893 | 84.0506 | 320.6643 | 366.5959 | 331.5785 | 146.8826 | 178.5785 | 120.3253
868.3167 | 310.3033 | 84.2216 | 320.6915 | 365.9721 | 331.8848 | 147.2113 | 178.888 | 120.5677
869.3167 | 310.5015 | 84.393 | 322.1389 | 365.2928 | 332.4918 | 147.4712 | 179.2001 | 120.7808
870.3167 | 310.2785 | 84.556 | 321.2422 | 365.2724 | 332.8852 | 147.8107 | 179.521 | 120.9919
871.3167 | 310.6248 | 84.7074 | 321.0224 | 364.6524 | 332.5746 | 148.0013 | 179.8513 | 121.223
872.3167 | 310.1556 | 84.8704 | 320.9807 | 364.2751 | 332.4706 | 148.1466 | 180.1953 | 121.4531
873.3167 | 311.1378 | 85.0261 | 323.3765 | 365.6941 | 333.1914 | 148.5204 | 180.5256 | 121.691
874.3167 | 310.8274 | 85.181 | 324.7076 | 365.4773 | 334.184 | 148.7444 | 180.8427 | 121.9243
875.3167 | 310.3534 | 85.2418 | 327.2452 | 366.2945 | 335.4222 | 149.1493 | 181.1964 | 122.1653
876.3167 | 310.5456 | 85.4026 | 327.486 | 365.8531 | 337.0666 | 149.1361 | 181.5294 | 122.4466
877.3167 | 310.5718 | 85.544 | 326.1027 | 365.9091 | 336.3617 | 149.4386 | 181.8373 | 122.6539
878.3167 | 311.5404 | 85.7149 | 326.5001 | 365.631 | 336.2604 | 149.6736 | 182.1635 | 122.879
879.3167 | 311.6447 | 85.8745 | 325.8351 | 364.8541 | 335.7537 | 149.9794 | 182.5043 | 123.1132
880.3167 | 311.6546 | 86.0271 | 325.1875 | 364.6648 | 336.3664 | 150.2419 | 182.8351 | 123.3693
881.3167 | 311.6482 | 86.1873 | 325.2687 | 364.5412 | 336.8839 | 150.5298 | 183.1567 | 123.5839
882.3167 | 311.7515 | 86.3678 | 326.962 | 365.6543 | 338 | 150.8386 | 183.4781 | 123.8158
883.3167 | 312.2084 | 86.5193 | 326.6477 | 366.2253 | 338.7058 | 151.094 | 183.8095 | 124.0756
884.3167 | 312.6557 | 86.6698 | 325.0959 | 365.8172 | 338.3744 | 151.5414 | 184.1369 | 124.3236
885.3167 | 313.1323 | 86.8162 | 324.2635 | 365.5679 | 338.1545 | 151.6876 | 184.4641 | 124.5509
886.3167 | 312.9913 | 86.9622 | 324.7812 | 366.0247 | 337.0949 | 152.0384 | 184.7952 | 124.786
887.3167 | 312.4396 | 87.1007 | 323.2635 | 365.584 | 336.7374 | 152.3636 | 185.1135 | 125.0208
888.3167 | 311.5269 | 87.2515 | 322.8459 | 365.0685 | 335.4215 | 152.5835 | 185.4355 | 125.2396
889.3167 | 311.1142 | 87.392 | 323.0217 | 364.3296 | 333.5752 | 152.8302 | 185.7491 | 125.4472
890.3167 | 311.6684 | 87.5305 | 322.9961 | 364.4119 | 331.8124 | 153.2814 | 186.0743 | 125.6665
891.3167 | 311.7324 | 87.6701 | 324.7457 | 365.3429 | 329.653 | 153.5 | 186.3861 | 125.9353
892.3167 | 312.7397 | 87.8324 | 326.8682 | 366.3344 | 328.6501 | 153.8566 | 186.7037 | 126.1778
893.3167 | 313.3274 | 87.9788 | 329.2019 | 366.7669 | 327.7494 | 154.1949 | 187.0135 | 126.4069
894.3167 | 313.614 | 88.1155 | 329.3254 | 366.2063 | 325.8835 | 154.5928 | 187.3454 | 126.6527
895.3167 | 313.8266 | 88.2656 | 329.8384 | 365.3457 | 324.3094 | 155.0018 | 187.6604 | 126.9234
896.3167 | 314.2611 | 88.4272 | 331.8718 | 365.6589 | 324.6281 | 155.4273 | 187.9692 | 127.1692
897.3167 | 316.1999 | 88.5705 | 333.2091 | 366.3226 | 325.1174 | 155.7781 | 188.2996 | 127.4251
898.3167 | 314.8216 | 88.7323 | 333.4896 | 367.4775 | 325.9561 | 156.1287 | 188.6217 | 127.6528
899.3167 | 314.8702 | 88.9001 | 334.8613 | 368.0178 | 327.5847 | 156.4144 | 188.9148 | 127.8875
900.3167 | 314.9975 | 89.0758 | 336.368 | 368.5778 | 327.8794 | 156.7395 | 189.2324 | 128.1218
901.3167 | 314.5421 | 89.2602 | 336.641 | 367.7284 | 328.8979 | 157.1008 | 189.542 | 128.371
902.3167 | 313.8061 | 89.4346 | 336.4707 | 367.2206 | 328.8726 | 157.4516 | 189.8418 | 128.6085
903.3167 | 313.3364 | 89.6183 | 337.2478 | 367.3503 | 329.6498 | 157.7923 | 190.1527 | 128.8385
904.3167 | 314.5379 | 89.7851 | 339.4573 | 368.2087 | 329.6042 | 158.0333 | 190.4712 | 129.0759
905.3167 | 316.1559 | 89.9801 | 340.1954 | 369.2252 | 331.9658 | 158.1948 | 190.7455 | 129.2991
906.3167 | 317.3375 | 90.1521 | 342.1516 | 370.1305 | 334.5529 | 158.6276 | 191.078 | 129.5735
907.3167 | 317.5889 | 90.3373 | 343.8876 | 371.3459 | 335.7415 | 159.0117 | 191.3869 | 129.7943
908.3167 | 317.3862 | 90.5104 | 343.3581 | 371.1315 | 335.0016 | 159.4086 | 191.6876 | 129.9894
909.3167 | 317.7014 | 90.6829 | 343.1706 | 370.3599 | 333.5978 | 159.5695 | 191.9932 | 130.2509
910.3167 | 316.9113 | 90.8219 | 344.3285 | 370.4982 | 334.5379 | 159.9092 | 192.3096 | 130.4609
911.3167 | 317.0735 | 90.9242 | 342.9046 | 369.7801 | 335.3634 | 160.2279 | 192.6116 | 130.7063
912.3167 | 317.2826 | 91.1091 | 343.5617 | 369.3694 | 335.4263 | 160.4668 | 192.925 | 130.9594
913.3167 | 318.9995 | 91.3617 | 345.4784 | 371.0323 | 336.2188 | 160.7958 | 193.2336 | 131.2285
914.3167 | 319.7881 | 91.5018 | 346.4073 | 372.1672 | 335.8072 | 161.1229 | 193.5188 | 131.5017
915.3167 | 319.7038 | 91.6405 | 347.6397 | 373.3227 | 334.9815 | 161.4621 | 193.8578 | 131.7374
916.3167 | 320.8541 | 91.8048 | 348.3487 | 374.2626 | 334.6511 | 161.8144 | 194.1455 | 131.9849
917.3167 | 321.5109 | 91.9652 | 349.5949 | 375.1489 | 335.2378 | 162.1464 | 194.4761 | 132.2326
918.3167 | 321.968 | 92.1095 | 349.6868 | 376.2211 | 336.4975 | 162.4978 | 194.7798 | 132.4636
919.3167 | 324.8034 | 92.2873 | 350.796 | 376.6531 | 337.1619 | 162.8563 | 195.0915 | 132.6854
920.3167 | 326.0508 | 92.4688 | 352.0975 | 378.422 | 338.541 | 163.2122 | 195.398 | 132.9246
921.3167 | 326.4593 | 92.6288 | 352.8924 | 378.6948 | 339.882 | 163.5718 | 195.7049 | 133.1518
922.3167 | 326.6009 | 92.7781 | 354.7863 | 379.8349 | 341.4715 | 163.958 | 196.0259 | 133.3869
923.3167 | 327.3235 | 92.9324 | 356.4389 | 380.7633 | 342.7287 | 164.351 | 196.3312 | 133.6425
924.3167 | 328.9136 | 93.0244 | 356.9845 | 383.3596 | 343.4058 | 164.7914 | 196.6387 | 133.9389
925.3167 | 329.1175 | 93.1893 | 357.5606 | 384.5776 | 343.2168 | 165.0525 | 196.9417 | 134.1878
926.3167 | 328.3418 | 93.3236 | 356.5442 | 384.7723 | 341.8922 | 165.4649 | 197.2525 | 134.4244
927.3167 | 329.1705 | 93.4657 | 355.647 | 384.1238 | 340.0114 | 165.8302 | 197.5465 | 134.6626
928.3167 | 329.8607 | 93.5785 | 356.9058 | 385.6342 | 339.5918 | 166.1661 | 197.8488 | 134.9069
929.3167 | 330.6622 | 93.7542 | 357.9727 | 386.0179 | 340.1516 | 166.5643 | 198.1587 | 135.1552
930.3167 | 331.3448 | 93.9203 | 358.916 | 386.4037 | 340.2013 | 166.9802 | 198.4612 | 135.3986
931.3167 | 330.2623 | 94.0756 | 360.7825 | 387.2645 | 341.8916 | 167.441 | 198.743 | 135.6511
932.3167 | 330.87 | 94.2057 | 362.3428 | 389.6553 | 342.0882 | 167.8707 | 199.0487 | 135.8968
933.3167 | 332.1757 | 94.3669 | 362.4174 | 391.8679 | 343.4527 | 168.2714 | 199.3459 | 136.1462
934.3167 | 332.6693 | 94.5207 | 361.5655 | 391.7332 | 343.7546 | 168.7 | 199.6396 | 136.387
935.3167 | 332.4989 | 94.7065 | 359.6899 | 391.1701 | 343.6614 | 169.1019 | 199.9606 | 136.6651
936.3167 | 331.8376 | 94.8565 | 358.9678 | 390.845 | 343.3082 | 169.5139 | 200.2643 | 136.9203
937.3167 | 330.7656 | 95.0048 | 358.1234 | 389.8012 | 342.5899 | 169.8966 | 200.5934 | 137.1658
938.3167 | 332.0567 | 95.1604 | 359.2898 | 391.1971 | 342.2093 | 170.3047 | 200.8962 | 137.3993
939.3167 | 331.7169 | 95.3232 | 360.6669 | 391.7463 | 342.2264 | 170.7126 | 201.2358 | 137.6585
940.3167 | 332.647 | 95.4714 | 361.8213 | 391.3079 | 341.7383 | 171.1931 | 201.5109 | 137.91
941.3167 | 332.6298 | 95.6269 | 362.8741 | 391.665 | 341.7049 | 171.6147 | 201.8335 | 138.1752
942.3167 | 333.0467 | 95.7888 | 363.1556 | 391.5659 | 340.4772 | 171.9751 | 202.1281 | 138.4227
943.3167 | 332.8739 | 95.9736 | 362.9088 | 391.1733 | 341.8083 | 172.4512 | 202.4262 | 138.6517
944.3167 | 332.9089 | 96.1114 | 362.4962 | 391.4199 | 342.8877 | 172.9242 | 202.7421 | 138.9255
945.3167 | 333.426 | 96.2435 | 361.7264 | 392.4246 | 343.0759 | 173.4859 | 203.0371 | 139.1841
946.3167 | 334.6054 | 96.4193 | 362.2107 | 392.6084 | 345.1659 | 173.5861 | 203.3467 | 139.4641
947.3167 | 335.829 | 96.5726 | 361.576 | 393.2443 | 344.911 | 173.9655 | 203.6796 | 139.7138
948.3167 | 337.2327 | 96.7331 | 362.2355 | 394.2321 | 344.649 | 174.1902 | 204.006 | 139.9605
949.3167 | 337.7425 | 96.912 | 362.0901 | 394.8802 | 344.5592 | 174.5916 | 204.3245 | 140.2133
950.3167 | 337.7295 | 97.0823 | 361.9309 | 395.425 | 343.8827 | 174.8562 | 204.6465 | 140.4835
951.3167 | 338.97 | 97.2571 | 362.9476 | 395.8441 | 343.0292 | 175.2021 | 204.9497 | 140.7312
952.3167 | 339.4878 | 97.3993 | 363.0329 | 397.231 | 342.3421 | 175.5687 | 205.2299 | 140.9853
953.3167 | 340.3877 | 97.5695 | 363.5887 | 398.2956 | 343.847 | 175.9399 | 205.5462 | 141.2437
954.3167 | 340.4347 | 97.774 | 364.5783 | 398.9429 | 345.5951 | 176.3248 | 205.8412 | 141.5279
955.3167 | 340.5064 | 97.9618 | 364.7509 | 399.6481 | 347.5036 | 176.8529 | 206.134 | 141.8177
956.3167 | 340.68 | 98.1517 | 364.6742 | 400.2916 | 349.3668 | 177.2254 | 206.4243 | 142.0496
957.3167 | 340.8956 | 98.3303 | 365.7718 | 400.3682 | 350.2651 | 177.3194 | 206.7135 | 142.3258
958.3167 | 342.199 | 98.4831 | 365.9374 | 400.3273 | 350.9243 | 177.6671 | 207.0269 | 142.626
959.3167 | 342.1756 | 98.6645 | 364.7121 | 400.1085 | 352.7843 | 178.1303 | 207.3287 | 142.8766
960.3167 | 342.7807 | 98.8219 | 365.0761 | 400.53 | 354.0514 | 178.3579 | 207.6519 | 143.1458
961.3167 | 343.0981 | 98.9958 | 366.5604 | 400.7758 | 354.6998 | 178.678 | 207.9808 | 143.4245
962.3167 | 344.44 | 99.1751 | 366.0026 | 402.0731 | 353.9528 | 179.0106 | 208.3043 | 143.6919
963.3167 | 344.1481 | 99.3594 | 364.7185 | 402.9398 | 353.8174 | 179.3307 | 208.6459 | 143.9524
964.3167 | 344.5273 | 99.5749 | 365.1895 | 402.9486 | 354.3934 | 179.6677 | 208.9551 | 144.2192
965.3167 | 345.1306 | 99.7379 | 365.7417 | 403.4899 | 354.4036 | 180.0161 | 209.2621 | 144.504
966.3167 | 345.478 | 99.911 | 364.7275 | 403.4599 | 353.5522 | 180.3403 | 209.589 | 144.7653
967.3167 | 345.9667 | 100.0773 | 363.3885 | 402.0169 | 354.2411 | 180.6814 | 209.9176 | 145.0306
968.3167 | 346.1309 | 100.2274 | 363.3128 | 401.3839 | 355.6383 | 180.9535 | 210.2119 | 145.3282
969.3167 | 346.9242 | 100.4339 | 363.0153 | 401.3137 | 355.9752 | 181.2691 | 210.5165 | 145.6152
970.3167 | 347.1739 | 100.6207 | 362.0496 | 401.1699 | 356.0333 | 181.5619 | 210.8367 | 145.8816
971.3167 | 347.3543 | 100.7676 | 362.4399 | 401.038 | 355.7904 | 181.8987 | 211.1545 | 146.1364
972.3167 | 347.3552 | 100.9682 | 363.7319 | 401.4732 | 354.4815 | 182.2267 | 211.485 | 146.4294
973.3167 | 347.8578 | 101.2049 | 364.6527 | 401.8578 | 354.9557 | 182.6059 | 211.7746 | 146.6971
974.3167 | 348.0491 | 101.3528 | 364.5971 | 402.3075 | 354.653 | 182.9796 | 212.0903 | 146.9726
975.3167 | 347.293 | 101.5467 | 364.038 | 401.8397 | 353.5891 | 183.313 | 212.4225 | 147.2557
976.3167 | 346.434 | 101.7564 | 364.0288 | 402.198 | 354.619 | 183.6581 | 212.7491 | 147.5256
977.3167 | 346.6724 | 101.9396 | 363.8196 | 403.2982 | 355.4334 | 184.0187 | 213.0675 | 147.8078
978.3167 | 347.7134 | 102.1837 | 363.9298 | 404.0697 | 356.5915 | 184.3819 | 213.3567 | 148.0832
979.3167 | 348.5668 | 102.4101 | 363.9479 | 404.1977 | 357.9571 | 184.7413 | 213.7016 | 148.3717
980.3167 | 349.1739 | 102.5979 | 364.1129 | 404.3866 | 358.194 | 185.0828 | 214.0123 | 148.6486
981.3167 | 349.5935 | 102.726 | 364.7584 | 404.202 | 358.5295 | 185.4178 | 214.3307 | 148.9469
982.3167 | 349.5648 | 102.8821 | 364.6938 | 404.5281 | 359.4517 | 185.7369 | 214.6456 | 149.2243
983.3167 | 349.1109 | 103.0453 | 364.5167 | 405.2767 | 361.4412 | 186.0866 | 214.9585 | 149.5016
984.3167 | 348.87 | 103.22 | 363.7401 | 405.7019 | 361.6311 | 186.4047 | 215.2631 | 149.7946
985.3167 | 350.0856 | 103.381 | 364.3728 | 406.3696 | 361.3282 | 186.7022 | 215.572 | 150.0502
986.3167 | 349.763 | 103.5288 | 364.1851 | 406.8208 | 361.808 | 187.0255 | 215.9233 | 150.3153
987.3167 | 349.3148 | 103.7053 | 364.6159 | 407.6413 | 362.5158 | 187.3427 | 216.2235 | 150.5916
988.3167 | 350.4826 | 103.8846 | 364.3702 | 408.3243 | 362.3712 | 187.6464 | 216.5328 | 150.8907
989.3167 | 352.0496 | 104.1008 | 364.0265 | 408.2516 | 362.3071 | 187.9526 | 216.8801 | 151.156
990.3167 | 352.4366 | 104.2721 | 364.2445 | 408.1171 | 362.328 | 188.2536 | 217.208 | 151.4222
991.3167 | 351.5116 | 104.5056 | 363.5431 | 407.3981 | 361.0483 | 188.612 | 217.5465 | 151.6905
992.3167 | 350.7336 | 104.7601 | 364.1175 | 407.7743 | 361.6819 | 188.962 | 217.88 | 151.9644
993.3167 | 349.7219 | 104.8582 | 363.7146 | 407.0246 | 361.9499 | 189.3072 | 218.1989 | 152.2746
994.3167 | 350.363 | 105.1274 | 363.5287 | 406.4001 | 360.8825 | 189.6484 | 218.5092 | 152.5491
995.3167 | 351.3722 | 105.2987 | 362.6163 | 405.9803 | 359.424 | 189.989 | 218.8162 | 152.8084
996.3167 | 351.719 | 105.4431 | 362.4291 | 405.9178 | 358.4891 | 190.2244 | 219.1222 | 153.0713
997.3167 | 352.8376 | 105.5713 | 362.3123 | 405.9206 | 358.3878 | 190.4899 | 219.4289 | 153.3419
998.3167 | 352.6996 | 105.7277 | 362.3578 | 406.088 | 358.7975 | 190.7912 | 219.7382 | 153.6136
999.3167 | 351.039 | 105.8877 | 362.2184 | 405.7957 | 358.4856 | 191.1413 | 220.0338 | 153.918
1000.3167 | 350.2308 | 106.0675 | 361.5654 | 404.701 | 358.2381 | 191.4252 | 220.3623 | 154.2146
1001.3167 | 350.9819 | 106.3226 | 362.407 | 404.8529 | 358.12 | 191.7545 | 220.6609 | 154.449
1002.3167 | 352.1647 | 106.4595 | 363.8024 | 405.4181 | 359.3736 | 192.0451 | 220.9986 | 154.742
1003.3167 | 352.1368 | 106.6404 | 364.5421 | 405.8507 | 360.8414 | 192.2887 | 221.3252 | 155.0013
1004.3167 | 353.6512 | 106.8394 | 366.1011 | 407.5561 | 362.3283 | 192.5899 | 221.6649 | 155.2803
1005.3167 | 356.7137 | 107.001 | 367.204 | 409.7792 | 363.9343 | 192.9069 | 221.9974 | 155.5859
1006.3167 | 356.8723 | 107.2147 | 368.2585 | 409.9086 | 364.1025 | 193.1963 | 222.3255 | 155.8512
1007.3167 | 357.4378 | 107.4004 | 367.3106 | 410.4136 | 364.8712 | 193.502 | 222.6311 | 156.1239
1008.3167 | 358.9423 | 107.492 | 366.7915 | 409.7729 | 364.2037 | 193.7768 | 222.9451 | 156.3632
1009.3167 | 358.1474 | 107.7249 | 365.7592 | 409.0999 | 363.2235 | 194.0579 | 223.2696 | 156.657
1010.3167 | 356.6247 | 107.8984 | 366.1244 | 409.0934 | 362.359 | 194.377 | 223.579 | 156.9408
1011.3167 | 357.3743 | 108.0477 | 366.2637 | 408.9719 | 361.7389 | 194.7137 | 223.898 | 157.2392
1012.3167 | 357.2172 | 108.2391 | 367.5069 | 409.311 | 360.7886 | 195.0256 | 224.1992 | 157.4987
1013.3167 | 358.6362 | 108.365 | 369.3882 | 409.7944 | 360.5877 | 195.3792 | 224.5511 | 157.7812
1014.3167 | 358.7537 | 108.549 | 370.0543 | 410.1354 | 361.5058 | 195.6696 | 224.8479 | 158.0507
1015.3167 | 358.6931 | 108.704 | 369.376 | 409.7888 | 361.9544 | 195.996 | 225.1822 | 158.3155
1016.3167 | 356.9026 | 108.8724 | 369.4606 | 411.1428 | 361.3249 | 196.2682 | 225.5005 | 158.591
1017.3167 | 355.2742 | 109.062 | 370.1645 | 410.2145 | 360.4453 | 196.5663 | 225.8507 | 158.87
1018.3167 | 355.4501 | 109.3127 | 371.126 | 410.8264 | 359.8864 | 196.8518 | 226.1744 | 159.1492
1019.3167 | 354.9631 | 109.5054 | 371.6554 | 410.9876 | 360.0133 | 197.1947 | 226.5003 | 159.4111
1020.3167 | 356.2921 | 109.6279 | 371.6802 | 413.166 | 359.8191 | 197.4315 | 226.8262 | 159.7047
1021.3167 | 355.8717 | 109.8193 | 373.7616 | 412.4164 | 360.7305 | 197.7404 | 227.1477 | 160.0009
1022.3167 | 354.8647 | 109.9787 | 371.5322 | 410.7414 | 359.6803 | 198.0571 | 227.4674 | 160.2753
1023.3167 | 354.202 | 110.1965 | 369.4752 | 408.9059 | 358.3349 | 198.3453 | 227.7792 | 160.5513
1024.3167 | 354.185 | 110.448 | 369.6165 | 407.7105 | 356.4394 | 198.6431 | 228.0938 | 160.8199
1025.3167 | 354.1024 | 110.5395 | 369.5689 | 406.9566 | 356.8141 | 198.939 | 228.4219 | 161.0986
1026.3167 | 355.2362 | 110.7926 | 368.5639 | 406.2261 | 356.68 | 199.2358 | 228.7284 | 161.3926
1027.3167 | 354.6663 | 110.963 | 368.5968 | 406.0483 | 358.0105 | 199.576 | 229.0853 | 161.6671
1028.3167 | 354.9733 | 111.1326 | 366.4705 | 404.9058 | 357.2359 | 199.9161 | 229.4406 | 161.9243
1029.3167 | 355.7723 | 111.316 | 364.3401 | 403.3487 | 356.89 | 200.2429 | 229.7842 | 162.2035
1030.3167 | 354.5265 | 111.4007 | 363.3594 | 402.4758 | 355.7602 | 200.531 | 230.1098 | 162.5051
1031.3167 | 354.0633 | 111.598 | 363.4645 | 400.8733 | 353.7171 | 200.8334 | 230.463 | 162.7955
1032.3167 | 354.3424 | 111.9169 | 367.5809 | 401.6276 | 352.2307 | 201.187 | 230.7774 | 163.0635
1033.3167 | 354.5404 | 112.0082 | 368.9002 | 402.3791 | 351.6217 | 201.4914 | 231.0659 | 163.3353
1034.3167 | 356.6395 | 112.1607 | 371.496 | 402.6802 | 351.149 | 201.7271 | 231.393 | 163.6052
1035.3167 | 354.4824 | 112.3455 | 373.6963 | 404.3996 | 351.8222 | 202.053 | 231.727 | 163.8868
1036.3167 | 357.5563 | 112.4758 | 377.5597 | 407.0483 | 352.9474 | 202.4495 | 232.0229 | 164.1433
1037.3167 | 356.4585 | 112.6483 | 379.5488 | 408.169 | 352.8319 | 202.7726 | 232.3273 | 164.4255
1038.3167 | 356.289 | 112.8611 | 379.7877 | 407.8213 | 351.4975 | 203.1031 | 232.6494 | 164.6881
1039.3167 | 355.4838 | 112.9417 | 379.5224 | 407.5872 | 351.0235 | 203.4034 | 232.9688 | 164.9677
1040.3167 | 358.6234 | 113.1394 | 379.5174 | 408.4227 | 351.4395 | 203.7339 | 233.2959 | 165.2539
1041.3167 | 356.8936 | 113.258 | 380.0402 | 409.9941 | 353.1087 | 204.063 | 233.584 | 165.5345
1042.3167 | 359.2888 | 113.3748 | 379.5627 | 409.6572 | 352.5631 | 204.3699 | 233.8909 | 165.7971
1043.3167 | 357.6947 | 113.5474 | 379.2339 | 409.8831 | 351.2128 | 204.6873 | 234.2158 | 166.0846
1044.3167 | 356.708 | 113.7302 | 380.7717 | 410.2769 | 351.6001 | 205.0089 | 234.525 | 166.3672
1045.3167 | 356.5466 | 113.9368 | 380.7824 | 409.3045 | 351.155 | 205.3194 | 234.8317 | 166.6183
1046.3167 | 356.1422 | 114.1167 | 379.6863 | 407.8701 | 350.2174 | 205.6454 | 235.1581 | 166.9097
1047.3167 | 355.7668 | 114.2918 | 378.5294 | 406.7772 | 349.0247 | 205.9537 | 235.4737 | 167.1857
1048.3167 | 355.3355 | 114.4222 | 377.9756 | 404.5688 | 347.4405 | 206.2558 | 235.7987 | 167.4524
1049.3167 | 356.322 | 114.4048 | 375.2561 | 402.7878 | 345.8915 | 206.5634 | 236.1203 | 167.7081
1050.3167 | 357.1254 | 114.5626 | 373.5933 | 402.1737 | 344.8961 | 206.7984 | 236.4014 | 167.9783
1051.3167 | 355.6711 | 114.7013 | 372.8818 | 401.0557 | 344.2606 | 207.0846 | 236.746 | 168.2768
1052.3167 | 354.5347 | 114.8331 | 372.5917 | 400.1815 | 343.8961 | 207.3732 | 237.0538 | 168.5416
1053.3167 | 356.6626 | 115.0375 | 373.2157 | 400.2668 | 343.2094 | 207.6914 | 237.3823 | 168.8329
1054.3167 | 356.9297 | 115.2489 | 372.0986 | 399.7226 | 342.7545 | 207.9587 | 237.6747 | 169.1014
1055.3167 | 355.3575 | 115.4464 | 369.7452 | 398.4232 | 342.4241 | 208.2033 | 238.0103 | 169.3972
1056.3167 | 355.5022 | 115.4728 | 367.5522 | 397.2842 | 342.6396 | 208.5005 | 238.3119 | 169.682
1057.3167 | 355.6431 | 115.64 | 365.9283 | 396.0708 | 342.0653 | 208.788 | 238.629 | 169.942
1058.3167 | 354.7258 | 115.8401 | 364.8096 | 395.4278 | 342.1082 | 209.0581 | 238.9428 | 170.2074
1059.3167 | 353.299 | 116.0205 | 363.7476 | 394.324 | 341.4147 | 209.3096 | 239.2655 | 170.4751
1060.3167 | 352.437 | 116.2225 | 362.8795 | 393.9679 | 341.0783 | 209.5324 | 239.5956 | 170.7917
1061.3167 | 353.2894 | 116.4058 | 363.3047 | 394.6426 | 340.0414 | 209.7414 | 239.8954 | 171.0724
1062.3167 | 353.6197 | 116.7301 | 363.9179 | 394.7364 | 339.1625 | 210.0272 | 240.2235 | 171.3826
1063.3167 | 352.6208 | 116.853 | 364.1845 | 393.9898 | 338.2708 | 210.3008 | 240.5421 | 171.6632
1064.3167 | 350.79 | 116.9509 | 364.2982 | 393.0885 | 337.7419 | 210.553 | 240.8594 | 171.9502
1065.3167 | 351.0457 | 116.9917 | 364.3029 | 393.6839 | 337.812 | 210.8815 | 241.1651 | 172.2201
1066.3167 | 351.2354 | 117.23 | 363.7182 | 393.9735 | 337.5946 | 210.9569 | 241.5135 | 172.4965
1067.3167 | 350.4193 | 117.5035 | 363.4694 | 393.2614 | 336.7113 | 211.2547 | 241.8295 | 172.7566
1068.3167 | 350.4053 | 117.7045 | 363.8675 | 392.8066 | 335.9 | 211.4237 | 242.1257 | 173.036
1069.3167 | 347.7307 | 118.0442 | 364.3141 | 391.0674 | 335.7375 | 211.637 | 242.4439 | 173.2775
1070.3167 | 349.3936 | 118.0934 | 363.2733 | 390.0812 | 334.5932 | 211.8625 | 242.7732 | 173.5617
1071.3167 | 349.0225 | 118.2331 | 362.5175 | 390.3238 | 334.6046 | 212.1472 | 243.1427 | 173.8168
1072.3167 | 348.4538 | 118.4405 | 363.7895 | 390.2603 | 334.0853 | 212.407 | 243.4542 | 174.0903
1073.3167 | 348.5774 | 118.5679 | 364.9588 | 391.165 | 333.872 | 212.691 | 243.7762 | 174.3623
1074.3167 | 347.5854 | 118.7958 | 365.3985 | 391.406 | 333.8641 | 212.8735 | 244.1017 | 174.6334
1075.3167 | 347.1371 | 119.0124 | 366.7753 | 391.0701 | 333.9234 | 213.0947 | 244.4545 | 174.9264
1076.3167 | 348.6798 | 119.1593 | 366.9832 | 391.024 | 333.77 | 213.3982 | 244.7762 | 175.2061
1077.3167 | 349.0216 | 119.2132 | 365.5146 | 390.5938 | 333.4458 | 213.6233 | 245.096 | 175.4773
1078.3167 | 348.4862 | 119.2775 | 364.0701 | 389.9436 | 333.7915 | 213.7907 | 245.4167 | 175.7433
1079.3167 | 348.2215 | 119.3505 | 364.3113 | 389.2219 | 333.9837 | 214.022 | 245.7173 | 176.0168
1080.3167 | 349.2043 | 119.525 | 364.8689 | 390.3012 | 333.6737 | 214.2885 | 246.0419 | 176.2728
1081.3167 | 349.5601 | 119.8041 | 365.3574 | 391.1885 | 333.6042 | 214.542 | 246.3406 | 176.5423
1082.3167 | 350.001 | 119.9191 | 365.9628 | 391.0373 | 333.9851 | 214.7664 | 246.6394 | 176.8201
1083.3167 | 350.4503 | 120.0633 | 364.8263 | 390.4588 | 333.7894 | 215.0016 | 246.9329 | 177.0865
1084.3167 | 351.301 | 120.2318 | 364.7755 | 390.6737 | 334.8213 | 215.2275 | 247.2559 | 177.3253
1085.3167 | 349.6743 | 120.3407 | 364.044 | 389.6921 | 334.7161 | 215.4603 | 247.5625 | 177.5851
1086.3167 | 350.6334 | 120.4753 | 363.3767 | 388.5711 | 334.3079 | 215.6446 | 247.8896 | 177.847
1087.3167 | 350.6891 | 120.7036 | 363.1251 | 387.6829 | 334.0289 | 215.8503 | 248.2278 | 178.1042
1088.3167 | 350.2923 | 120.7496 | 363.3402 | 388.4056 | 333.5071 | 216.0526 | 248.5321 | 178.3628
1089.3167 | 348.7381 | 120.8906 | 363.0722 | 387.7618 | 332.6878 | 216.2672 | 248.8527 | 178.6247
1090.3167 | 349.2791 | 120.9808 | 362.64 | 386.457 | 332.0135 | 216.5034 | 249.149 | 178.8593
1091.3167 | 348.7688 | 121.2279 | 361.4848 | 385.3331 | 331.7724 | 216.6777 | 249.4624 | 179.0886
1092.3167 | 348.83 | 121.4813 | 362.3619 | 385.319 | 332.1232 | 216.9597 | 249.7469 | 179.3335
1093.3167 | 348.991 | 121.6266 | 362.936 | 386.0434 | 332.8512 | 217.2629 | 250.0653 | 179.589
1094.3167 | 348.7449 | 121.8058 | 361.595 | 385.1165 | 332.1313 | 217.5015 | 250.3671 | 179.8212
1095.3167 | 348.7141 | 122.0522 | 362.8478 | 385.8793 | 331.5437 | 217.7352 | 250.6573 | 180.0468
1096.3167 | 348.8319 | 122.3126 | 365.1991 | 386.8581 | 332.2799 | 217.9699 | 250.9472 | 180.2738
1097.3167 | 349.3962 | 122.4091 | 366.795 | 388.2273 | 333.5421 | 218.2373 | 251.2579 | 180.5384
1098.3167 | 349.7956 | 122.6077 | 367.3582 | 388.5846 | 334.1246 | 218.4935 | 251.574 | 180.7742
1099.3167 | 349.4199 | 122.7372 | 367.7081 | 388.7244 | 333.8563 | 218.7547 | 251.8771 | 181.0247
1100.3167 | 348.8472 | 122.7664 | 368.8518 | 388.764 | 334.0478 | 218.9969 | 252.1677 | 181.2546
1101.3167 | 348.276 | 122.7824 | 369.5673 | 388.7632 | 334.1814 | 219.3085 | 252.483 | 181.5069
1102.3167 | 347.8966 | 122.8442 | 369.4543 | 388.9266 | 333.9138 | 219.5585 | 252.7965 | 181.7449
1103.3167 | 348.7047 | 122.8446 | 370.8104 | 389.0026 | 334.328 | 219.8144 | 253.1102 | 181.9636
1104.3167 | 348.7872 | 123.061 | 373.7097 | 390.4612 | 334.5902 | 220.141 | 253.43 | 182.1809
1105.3167 | 349.3635 | 123.1504 | 374.6956 | 391.0452 | 335.6702 | 220.4078 | 253.7438 | 182.4402
1106.3167 | 348.9827 | 123.2562 | 374.6887 | 391.0243 | 335.2983 | 220.7057 | 254.0376 | 182.6593
1107.3167 | 348.1999 | 123.4198 | 372.9436 | 389.8074 | 334.6121 | 220.9644 | 254.3279 | 182.894
1108.3167 | 348.3015 | 123.6344 | 371.498 | 390.138 | 334.1062 | 221.1958 | 254.6291 | 183.136
1109.3167 | 348.5837 | 123.7035 | 370.4948 | 389.7535 | 334.4871 | 221.436 | 254.9534 | 183.3601
1110.3167 | 348.1882 | 123.7873 | 368.6718 | 389.023 | 334.2052 | 221.6696 | 255.2613 | 183.5763
1111.3167 | 347.5791 | 123.9864 | 366.9318 | 388.5274 | 334.725 | 221.9083 | 255.5648 | 183.8364
1112.3167 | 346.6783 | 124.2061 | 366.2977 | 387.9675 | 335.3526 | 222.1421 | 255.8527 | 184.0734
1113.3167 | 345.9233 | 124.3929 | 366.5937 | 387.2442 | 334.6427 | 222.4004 | 256.1349 | 184.294
1114.3167 | 346.4559 | 124.5093 | 365.3772 | 386.6358 | 333.8527 | 222.6422 | 256.4443 | 184.5652
1115.3167 | 345.6524 | 124.6377 | 363.4906 | 385.7756 | 332.7184 | 222.8766 | 256.7464 | 184.8282
1116.3167 | 344.3738 | 124.8274 | 363.0755 | 385.6032 | 332.1564 | 223.0812 | 257.0415 | 185.0854
1117.3167 | 345.1987 | 124.9865 | 362.9264 | 386.2274 | 332.231 | 223.3341 | 257.332 | 185.3343
1118.3167 | 344.8737 | 125.0633 | 362.5159 | 385.6178 | 331.7272 | 223.5759 | 257.6418 | 185.5657
1119.3167 | 343.7802 | 125.1761 | 362.0544 | 384.4742 | 331.3047 | 223.8071 | 257.9296 | 185.7983
1120.3167 | 343.0149 | 125.3301 | 362.8131 | 384.2518 | 330.8191 | 224.0294 | 258.2383 | 186.0267
1121.3167 | 343.1758 | 125.5172 | 360.4106 | 383.3714 | 330.7533 | 224.273 | 258.5374 | 186.2581
1122.3167 | 343.8306 | 125.6301 | 358.4021 | 383.6034 | 331.124 | 224.4955 | 258.8395 | 186.4915
1123.3167 | 343.0019 | 125.7796 | 357.2281 | 382.9084 | 330.1744 | 224.7166 | 259.1399 | 186.7556
1124.3167 | 342.6513 | 125.9694 | 357.9946 | 382.5673 | 329.0491 | 224.9202 | 259.4156 | 187.0068
1125.3167 | 342.0811 | 126.0769 | 357.6637 | 381.8856 | 328.2644 | 225.1456 | 259.7081 | 187.228
1126.3167 | 341.9758 | 126.169 | 358.5635 | 381.6713 | 328.1967 | 225.3492 | 260.0161 | 187.4736
1127.3167 | 340.6166 | 126.4226 | 358.9268 | 381.8303 | 328.4561 | 225.5715 | 260.3116 | 187.7165
1128.3167 | 340.4839 | 126.5492 | 359.9246 | 381.4399 | 328.3222 | 225.7795 | 260.602 | 187.9416
1129.3167 | 340.2584 | 126.6949 | 359.1285 | 380.4503 | 328.0992 | 225.9968 | 260.9082 | 188.197
1130.3167 | 339.2503 | 126.9777 | 357.8349 | 378.9282 | 327.9788 | 226.1792 | 261.2173 | 188.4707
1131.3167 | 338.4148 | 127.206 | 356.6048 | 377.6352 | 327.2962 | 226.4031 | 261.4971 | 188.6421
1132.3167 | 339.557 | 127.4274 | 356.62 | 376.894 | 326.633 | 226.5497 | 261.8188 | 188.8829
1133.3167 | 339.9683 | 127.6584 | 356.7215 | 377.2072 | 326.5498 | 226.8023 | 262.1146 | 189.1363
1134.3167 | 339.9636 | 127.9204 | 356.5792 | 377.4009 | 326.8759 | 227.0187 | 262.3936 | 189.5465
1135.3167 | 340.7481 | 128.1469 | 357.965 | 378.6568 | 327.0562 | 227.1537 | 262.6827 | 189.7872
1136.3167 | 341.2882 | 128.2519 | 360.0247 | 379.9507 | 329.086 | 227.395 | 262.9586 | 190.031
1137.3167 | 340.5286 | 128.3636 | 360.3685 | 379.8133 | 330.1472 | 227.6537 | 263.2373 | 190.2522
1138.3167 | 340.7519 | 128.4976 | 362.1542 | 379.9139 | 330.2154 | 227.8442 | 263.5257 | 190.4873
1139.3167 | 341.1438 | 128.6109 | 362.1995 | 379.546 | 330.348 | 228.1168 | 263.8053 | 190.7119
1140.3167 | 341.2073 | 128.7563 | 362.5194 | 380.5957 | 329.919 | 228.3542 | 264.0901 | 190.9641
1141.3167 | 341.5182 | 128.8802 | 364.0379 | 380.8209 | 329.6568 | 228.5915 | 264.3715 | 191.1993
1142.3167 | 341.7103 | 128.9962 | 363.1415 | 380.0601 | 329.3476 | 228.8283 | 264.6407 | 191.4431
1143.3167 | 341.3868 | 129.112 | 362.1666 | 378.8295 | 329.0386 | 229.0647 | 264.9325 | 191.679
1144.3167 | 341.0622 | 129.2509 | 360.6673 | 377.5339 | 328.1747 | 229.2792 | 265.2123 | 191.9298
1145.3167 | 340.3198 | 129.4225 | 358.5948 | 376.2671 | 327.9997 | 229.4537 | 265.4988 | 192.1651
1146.3167 | 339.5726 | 129.575 | 356.5977 | 375.2713 | 328.5434 | 229.6774 | 265.7659 | 192.3872
1147.3167 | 338.2963 | 129.7111 | 356.0941 | 374.9465 | 328.4063 | 229.9017 | 266.0458 | 192.6224
1148.3167 | 338.1276 | 129.8528 | 355.5927 | 373.9773 | 328.1546 | 230.0713 | 266.3082 | 192.8399
1149.3167 | 337.2346 | 129.972 | 354.6883 | 372.4493 | 327.5126 | 230.2696 | 266.5958 | 193.0675
1150.3167 | 336.71 | 130.0894 | 353.9022 | 371.1786 | 326.5092 | 230.4809 | 266.8589 | 193.3407
1151.3167 | 337.0966 | 130.2238 | 353.111 | 370.6515 | 325.5316 | 230.6425 | 267.1405 | 193.567
1152.3167 | 336.9892 | 130.3433 | 352.2208 | 369.236 | 325.1166 | 230.8565 | 267.419 | 193.8103
1153.3167 | 337.0548 | 130.4709 | 350.7114 | 370.3078 | 325.1916 | 231.0502 | 267.6711 | 194.0373
1154.3167 | 337.5789 | 130.5647 | 351.9228 | 371.7358 | 326.382 | 231.2645 | 267.9757 | 194.2845
1155.3167 | 338.3682 | 130.7275 | 352.3602 | 372.6231 | 327.3571 | 231.4654 | 268.2882 | 194.5083
1156.3167 | 338.7065 | 130.9094 | 353.0279 | 373.6314 | 328.4657 | 231.6414 | 268.5308 | 194.744
1157.3167 | 338.7702 | 131.0269 | 351.9353 | 374.046 | 329.3408 | 231.8044 | 268.7894 | 194.9559
1158.3167 | 340.4179 | 131.0812 | 352.8633 | 376.3534 | 330.4258 | 231.9882 | 269.0729 | 195.1114
1159.3167 | 340.8096 | 131.279 | 353.5495 | 377.7158 | 333.1728 | 232.1235 | 269.3652 | 195.3185
1160.3167 | 340.7616 | 131.4326 | 353.2031 | 377.9095 | 334.1495 | 232.3058 | 269.6215 | 195.5087
1161.3167 | 340.7304 | 131.6178 | 351.8902 | 376.9686 | 334.7166 | 232.4757 | 269.8785 | 195.7679
1162.3167 | 339.6696 | 131.8391 | 350.8962 | 376.357 | 334.1681 | 232.6673 | 270.1478 | 195.9215
1163.3167 | 338.8442 | 132.022 | 350.6018 | 376.3366 | 333.5259 | 232.8046 | 270.4198 | 196.1318
1164.3167 | 338.6983 | 132.1943 | 350.1116 | 376.4239 | 333.1293 | 232.9484 | 270.6829 | 196.388
1165.3167 | 338.6237 | 132.3281 | 350.0092 | 375.6507 | 332.5979 | 233.1126 | 270.9637 | 196.6657
1166.3167 | 338.5138 | 132.4732 | 349.1555 | 374.9993 | 332.5967 | 233.2996 | 271.2135 | 196.9281
1167.3167 | 337.5171 | 132.6472 | 348.7497 | 373.7874 | 331.3204 | 233.4724 | 271.4678 | 197.2041
1168.3167 | 337.2457 | 132.818 | 349.535 | 373.6621 | 329.9591 | 233.6537 | 271.7352 | 197.4488
1169.3167 | 336.7388 | 132.9285 | 349.3997 | 373.4173 | 329.4638 | 233.8439 | 271.9848 | 197.6636
1170.3167 | 336.0127 | 133.0646 | 348.9425 | 372.8347 | 329.1407 | 234.0484 | 272.2699 | 197.8784
1171.3167 | 335.3298 | 133.2184 | 348.5508 | 372.1902 | 329.3099 | 234.2378 | 272.5182 | 198.1047
1172.3167 | 335.0908 | 133.3978 | 347.9276 | 371.3892 | 329.1734 | 234.439 | 272.7556 | 198.3028
1173.3167 | 334.4279 | 133.5202 | 349.0857 | 371.9504 | 328.9053 | 234.614 | 273.0227 | 198.5326
1174.3167 | 334.1529 | 133.6705 | 349.2126 | 372.2615 | 328.4062 | 234.8132 | 273.2634 | 198.7512
1175.3167 | 333.7252 | 133.791 | 348.5338 | 371.6222 | 327.6913 | 235.0092 | 273.5382 | 198.9169
1176.3167 | 333.993 | 133.939 | 349.1469 | 371.2909 | 327.2371 | 235.2266 | 273.7861 | 199.1618
1177.3167 | 333.9014 | 134.1085 | 348.7749 | 370.1614 | 326.9109 | 235.4242 | 274.0401 | 199.3675
1178.3167 | 333.6302 | 134.2614 | 348.6942 | 369.2203 | 326.4743 | 235.5895 | 274.2961 | 199.5706
1179.3167 | 333.7584 | 134.4219 | 349.5699 | 368.3716 | 325.7609 | 235.7736 | 274.5409 | 199.755
1180.3167 | 333.6443 | 134.5648 | 349.2308 | 367.7265 | 325.456 | 235.9625 | 274.808 | 199.9491
1181.3167 | 333.5713 | 134.6396 | 349.1758 | 367.4445 | 325.2234 | 236.1487 | 275.0556 | 200.1767
1182.3167 | 333.9844 | 134.8114 | 348.0463 | 367.2633 | 325.2541 | 236.3303 | 275.3017 | 200.3798
1183.3167 | 334.0074 | 135.0099 | 346.6194 | 365.8303 | 324.3912 | 236.5112 | 275.5255 | 200.6208
1184.3167 | 334.4271 | 135.1284 | 346.7777 | 364.7419 | 323.3085 | 236.6679 | 275.7621 | 200.8386
1185.3167 | 334.2982 | 135.2609 | 346.5036 | 364.4475 | 322.8073 | 236.8385 | 276.0059 | 200.9963
1186.3167 | 334.5925 | 135.4041 | 346.6632 | 363.6853 | 322.1761 | 237.0295 | 276.2536 | 201.2008
1187.3167 | 334.2805 | 135.5371 | 347.7044 | 362.8533 | 321.5767 | 237.1469 | 276.4845 | 201.4229
1188.3167 | 335.121 | 135.6605 | 348.7749 | 362.5258 | 321.4115 | 237.3675 | 276.7287 | 201.6508
1189.3167 | 335.783 | 135.8023 | 348.8211 | 361.9808 | 321.1956 | 237.5991 | 276.965 | 201.8787
1190.3167 | 334.9607 | 135.9591 | 349.4245 | 361.1158 | 321.4589 | 237.7658 | 277.2194 | 202.059
1191.3167 | 334.5525 | 136.1592 | 348.8108 | 360.9329 | 321.0701 | 237.9678 | 277.4362 | 202.2761
1192.3167 | 333.6581 | 136.3387 | 347.606 | 360.5823 | 320.7061 | 238.1186 | 277.6905 | 202.4844
1193.3167 | 333.0283 | 136.5072 | 346.9388 | 360.2246 | 319.9927 | 238.2791 | 277.8967 | 202.7443
1194.3167 | 332.9787 | 136.6509 | 347.7489 | 359.9257 | 319.2249 | 238.4301 | 278.1174 | 202.9499
1195.3167 | 333.0314 | 136.7802 | 347.9966 | 359.8359 | 319.5854 | 238.6541 | 278.3631 | 203.1766
1196.3167 | 333.2518 | 136.9164 | 348.3859 | 359.7693 | 319.524 | 238.8299 | 278.6107 | 203.3739
1197.3167 | 334.8305 | 137.0057 | 349.8312 | 361.0758 | 320.9143 | 239.0216 | 278.8249 | 203.5902
1198.3167 | 334.8212 | 137.1459 | 351.3478 | 361.4499 | 321.5418 | 239.2123 | 279.0534 | 203.7939
1199.3167 | 335.1401 | 137.2977 | 349.5903 | 361.2323 | 321.3469 | 239.4034 | 279.2894 | 203.9967
1200.3167 | 335.6524 | 137.4521 | 348.1036 | 360.2075 | 320.9625 | 239.5751 | 279.5177 | 204.193
1201.3167 | 335.4547 | 137.5641 | 348.0873 | 360.1256 | 320.439 | 239.7354 | 279.7496 | 204.3893
1202.3167 | 335.5282 | 137.6938 | 347.6111 | 359.8061 | 320.422 | 239.9192 | 280 | 204.5668
1203.3167 | 335.119 | 137.8208 | 346.7325 | 359.0669 | 320.1485 | 240.094 | 280.2105 | 204.7387
1204.3167 | 334.1956 | 138.0227 | 346.4545 | 358.3316 | 319.5776 | 240.2571 | 280.4203 | 204.9077
1205.3167 | 334.7502 | 138.2048 | 348.1746 | 360.0779 | 319.9748 | 240.4415 | 280.6647 | 205.1188
1206.3167 | 334.3053 | 138.3359 | 348.1192 | 359.978 | 319.7998 | 240.6426 | 280.8723 | 205.3013
1207.3167 | 334.2419 | 138.4877 | 346.8097 | 359.8487 | 320.0563 | 240.5626 | 281.077 | 205.4865
1208.3167 | 334.2031 | 138.6198 | 345.4781 | 359.4211 | 320.7257 | 240.6704 | 281.2817 | 205.6885
1209.3167 | 333.7831 | 138.8162 | 343.5575 | 358.5045 | 321.3517 | 240.8297 | 281.5163 | 205.9259
1210.3167 | 333.6176 | 138.9509 | 341.7154 | 357.8055 | 320.6791 | 241.2304 | 281.7432 | 206.0921
1211.3167 | 333.1683 | 139.1842 | 340.7527 | 356.9771 | 319.781 | 241.3893 | 281.935 | 206.296
1212.3167 | 332.3095 | 139.2906 | 340.8045 | 356.674 | 319.4793 | 241.2321 | 282.1473 | 206.5101
1213.3167 | 332.6283 | 139.4784 | 340.82 | 357.3761 | 319.8296 | 241.1299 | 282.3772 | 206.7182
1214.3167 | 332.3326 | 139.6766 | 339.6741 | 357.8931 | 321.172 | 241.2522 | 282.6066 | 206.9561
1215.3167 | 331.9027 | 139.7995 | 338.2151 | 357.6894 | 322.1449 | 241.4195 | 282.7982 | 207.2358
1216.3167 | 332.323 | 139.9165 | 337.2682 | 357.7861 | 323.5698 | 241.5453 | 283.0069 | 207.4072
1217.3167 | 332.9525 | 140.0673 | 339.3411 | 359.111 | 323.6639 | 241.7156 | 283.1991 | 207.5725
1218.3167 | 333.5125 | 140.2491 | 340.7685 | 359.9244 | 323.3255 | 241.9226 | 283.4286 | 207.79
1219.3167 | 333.8526 | 140.4075 | 341.5306 | 359.8023 | 323.1373 | 242.0931 | 283.5975 | 207.9936
1220.3167 | 333.4702 | 140.5881 | 341.9213 | 359.6881 | 322.6033 | 242.2663 | 283.8146 | 208.2316
1221.3167 | 332.6591 | 140.7487 | 341.7752 | 358.9678 | 321.9986 | 242.4635 | 284.0194 | 208.4164
1222.3167 | 331.8821 | 140.877 | 341.6776 | 358.5927 | 321.5334 | 242.6274 | 284.2261 | 208.6729
1223.3167 | 331.6895 | 141.0474 | 341.4203 | 358.7534 | 321.008 | 242.7422 | 284.4057 | 208.9267
1224.3167 | 331.3152 | 141.2022 | 340.5935 | 358.8127 | 320.6672 | 242.9206 | 284.6228 | 209.1006
1225.3167 | 330.8362 | 141.3019 | 340.4335 | 358.6134 | 320.2583 | 243.062 | 284.822 | 209.342
1226.3167 | 330.8005 | 141.5122 | 340.8278 | 358.3199 | 319.9454 | 243.1997 | 285.016 | 209.508
1227.3167 | 330.8313 | 141.6902 | 341.2692 | 358.5055 | 320.6689 | 243.3823 | 285.2253 | 209.7123
1228.3167 | 330.2953 | 141.8726 | 341.1109 | 358.1091 | 320.479 | 243.527 | 285.3954 | 209.8828
1229.3167 | 329.6597 | 142.064 | 340.1173 | 357.0396 | 319.8178 | 243.6869 | 285.5941 | 210.0708
1230.3167 | 329.9764 | 142.2012 | 338.547 | 355.6382 | 319.3668 | 243.8573 | 285.8032 | 210.2227
1231.3167 | 329.7381 | 142.2652 | 337.1839 | 355.066 | 320.494 | 243.9747 | 286.0008 | 210.4272
1232.3167 | 329.8865 | 142.3481 | 337.7227 | 356.3269 | 322.6546 | 244.0986 | 286.187 | 210.6209
1233.3167 | 329.5947 | 142.485 | 338.7597 | 357.4225 | 324.1045 | 244.2087 | 286.3778 | 210.8554
1234.3167 | 329.6714 | 142.688 | 339.8496 | 358.2877 | 324.6382 | 244.3361 | 286.587 | 211.0379
1235.3167 | 330.0938 | 142.7951 | 339.7044 | 358.5369 | 324.6009 | 244.4755 | 286.7761 | 211.2206
1236.3167 | 330.2486 | 142.9869 | 338.6336 | 358.0682 | 324.4213 | 244.6192 | 286.9468 | 211.3922
1237.3167 | 330.8754 | 143.2075 | 338.7963 | 359.6905 | 325.2047 | 244.7578 | 287.1572 | 211.5657
1238.3167 | 331.2414 | 143.4319 | 340.1602 | 360.9734 | 325.9866 | 244.9029 | 287.3233 | 211.7614
1239.3167 | 331.0036 | 143.6243 | 340.2302 | 362.4175 | 326.561 | 245.0429 | 287.5388 | 211.9487
1240.3167 | 330.7267 | 143.7819 | 339.2673 | 362.3434 | 326.7847 | 245.1835 | 287.718 | 212.1269
1241.3167 | 330.5717 | 143.9786 | 340.0866 | 362.4838 | 326.1818 | 245.3318 | 287.9151 | 212.3565
1242.3167 | 331.5551 | 144.191 | 341.6984 | 364.1882 | 326.8781 | 245.4813 | 288.0988 | 212.4831
1243.3167 | 331.9538 | 144.3598 | 342.351 | 365.031 | 328.4621 | 245.63 | 288.2862 | 212.6854
1244.3167 | 331.5442 | 144.4266 | 341.9796 | 365.1165 | 328.9321 | 245.7864 | 288.4615 | 212.8889
1245.3167 | 332.1765 | 144.571 | 342.5681 | 365.3526 | 328.7128 | 245.9347 | 288.6579 | 213.0552
1246.3167 | 332.0421 | 144.753 | 344.7383 | 365.6408 | 328.5259 | 246.0962 | 288.8409 | 213.2729
1247.3167 | 331.6367 | 144.8948 | 345.7821 | 365.2014 | 328.2433 | 246.2872 | 289.02 | 213.4001
1248.3167 | 332.1689 | 145.0462 | 347.7518 | 365.2351 | 327.4448 | 246.5023 | 289.1876 | 213.6533
1249.3167 | 332.5545 | 145.1922 | 349.4186 | 365.2959 | 327.4739 | 246.6798 | 289.3617 | 213.7826
1250.3167 | 332.932 | 145.3482 | 350.8909 | 365.5311 | 327.2601 | 246.8713 | 289.5358 | 214.0584
1251.3167 | 332.5747 | 145.4906 | 350.9941 | 364.7368 | 326.8467 | 247.0532 | 289.7235 | 214.2233
1252.3167 | 334.9457 | 145.5888 | 351.9841 | 364.9401 | 327.3122 | 247.2884 | 289.8754 | 214.4227
1253.3167 | 336.0508 | 145.706 | 352.012 | 366.9378 | 327.4812 | 247.4868 | 290.0727 | 214.5952
1254.3167 | 337.0485 | 145.9162 | 353.0725 | 368.7773 | 328.1976 | 247.651 | 290.2464 | 214.7926
1255.3167 | 337.6453 | 146.1151 | 355.1327 | 370.7804 | 328.6931 | 247.8316 | 290.4083 | 215.0096
1256.3167 | 339.0849 | 146.2464 | 356.0894 | 373.1293 | 328.7336 | 248.0108 | 290.5943 | 215.1783
1257.3167 | 339.4503 | 146.4249 | 357.692 | 375.9705 | 329.7889 | 248.1596 | 290.7681 | 215.3798
1258.3167 | 339.7279 | 146.4822 | 359.2014 | 378.1452 | 331.849 | 248.3155 | 290.96 | 215.6004
1259.3167 | 340.7755 | 146.5894 | 360.6394 | 380.5086 | 332.7981 | 248.5027 | 291.1304 | 215.7818
1260.3167 | 341.4062 | 146.7099 | 361.0892 | 382.3236 | 334.7598 | 248.6685 | 291.3053 | 215.9509
1261.3167 | 341.7792 | 146.7943 | 361.3027 | 383.8719 | 335.8895 | 248.856 | 291.4724 | 216.1436
1262.3167 | 342.5251 | 146.8792 | 361.862 | 384.7712 | 336.7304 | 249.0261 | 291.6505 | 216.3305
1263.3167 | 343.7836 | 147.1356 | 363.112 | 387.5788 | 338.407 | 249.2201 | 291.8543 | 216.5508
1264.3167 | 344.0231 | 147.3181 | 363.585 | 389.5904 | 338.8169 | 249.4129 | 292.0052 | 216.7689
1265.3167 | 344.5485 | 147.4673 | 364.2463 | 391.184 | 340.0699 | 249.6024 | 292.1585 | 216.9519
1266.3167 | 344.6322 | 147.5309 | 365.3987 | 391.1199 | 340.384 | 249.7807 | 292.3537 | 217.1184
1267.3167 | 344.8826 | 147.7491 | 365.759 | 390.7347 | 340.4481 | 249.9498 | 292.5062 | 217.3363
1268.3167 | 344.8896 | 147.9474 | 365.7302 | 390.4019 | 340.8805 | 250.125 | 292.6654 | 217.514
1269.3167 | 344.2977 | 148.1372 | 364.9863 | 388.9697 | 340.301 | 250.292 | 292.8436 | 217.6845
1270.3167 | 344.9316 | 148.2406 | 364.7054 | 387.7559 | 339.5848 | 250.4694 | 293.0168 | 217.8527
1271.3167 | 344.5134 | 148.4523 | 364.6944 | 387.8905 | 338.3615 | 250.6306 | 293.1996 | 218.0333
1272.3167 | 345.0834 | 148.5806 | 364.8479 | 388.3679 | 339.4265 | 250.8382 | 293.3754 | 218.2134
1273.3167 | 345.995 | 148.7845 | 365.3251 | 390.2001 | 341.1366 | 250.9576 | 293.5303 | 218.377
1274.3167 | 346.1583 | 149.0137 | 366.1774 | 389.9663 | 341.5819 | 251.1241 | 293.7125 | 218.5754
1275.3167 | 346.3101 | 149.2329 | 366.5311 | 389.7419 | 342.3938 | 251.306 | 293.8836 | 218.761
1276.3167 | 346.0715 | 149.3411 | 366.0114 | 388.3138 | 341.4816 | 251.4944 | 294.0543 | 218.9464
1277.3167 | 345.5241 | 149.5117 | 363.6087 | 387.1672 | 340.2566 | 251.6713 | 294.2278 | 219.1341
1278.3167 | 345.2456 | 149.6109 | 361.8872 | 385.7435 | 339.5474 | 251.7929 | 294.4055 | 219.3983
1279.3167 | 344.9757 | 149.7937 | 360.1293 | 384.2525 | 338.9302 | 252.246 | 294.6428 | 219.649
1280.3167 | 344.2816 | 150.1022 | 358.71 | 382.2936 | 337.3446 | 253.7333 | 295.0434 | 220.3446
1281.3167 | 342.9528 | 150.0005 | 356.1181 | 380.8201 | 336.9583 | 252.2383 | 294.9226 | 219.8608
1282.3167 | 342.6023 | 150.1047 | 356.6389 | 379.4771 | 335.9124 | 252.4048 | 295.1012 | 220.0233
1283.3167 | 342.3452 | 150.2707 | 357.6556 | 378.6867 | 334.2444 | 252.573 | 295.2777 | 220.2079
1284.3167 | 342.2785 | 150.5016 | 358.0989 | 379.4736 | 333.8104 | 252.6747 | 295.458 | 220.3487
1285.3167 | 341.2908 | 150.7486 | 357.5696 | 378.7408 | 333.0588 | 252.8224 | 295.6245 | 220.5061
1286.3167 | 340.8674 | 150.982 | 356.6324 | 378.4437 | 332.7502 | 252.9553 | 295.8066 | 220.7883
1287.3167 | 340.6321 | 151.2302 | 357.0496 | 380.1815 | 333.045 | 253.1304 | 295.9651 | 220.9308
1288.3167 | 340.5012 | 151.4135 | 357.4146 | 382.0202 | 333.7069 | 253.316 | 296.1622 | 221.0806
1289.3167 | 340.9352 | 151.6374 | 357.8743 | 382.7141 | 334.5654 | 253.5321 | 296.3573 | 221.2502
1290.3167 | 342.1148 | 151.7655 | 359.3301 | 383.4741 | 335.3656 | 253.7381 | 296.5049 | 221.4823
1291.3167 | 342.49 | 151.9095 | 359.7043 | 383.3406 | 335.7732 | 253.8858 | 296.6878 | 221.6407
1292.3167 | 342.6186 | 152.1806 | 360.3351 | 383.0595 | 335.6612 | 254.0237 | 296.861 | 221.7733
1293.3167 | 342.3655 | 152.3586 | 362.2307 | 383.7237 | 336.0028 | 254.2007 | 297.043 | 221.9478
1294.3167 | 342.7296 | 152.5766 | 362.634 | 384.038 | 336.6249 | 254.4384 | 297.2237 | 222.1118
1295.3167 | 343.335 | 152.7595 | 363.703 | 384.0227 | 335.5091 | 254.677 | 297.4074 | 222.2788
1296.3167 | 343.4038 | 152.9216 | 364.4542 | 383.9415 | 335.5497 | 254.8823 | 297.6006 | 222.4667
1297.3167 | 343.5986 | 153.114 | 365.5933 | 383.9697 | 336.4264 | 255.0952 | 297.7525 | 222.6532
1298.3167 | 343.3787 | 153.2314 | 366.0001 | 383.2966 | 336.4811 | 255.3071 | 297.9423 | 222.8082
1299.3167 | 343.8014 | 153.4442 | 366.1292 | 383.0409 | 336.7344 | 255.5137 | 298.1053 | 222.9829
1300.3167 | 343.3295 | 153.7065 | 364.8446 | 382.0294 | 336.2393 | 255.7052 | 298.2691 | 223.1537
1301.3167 | 343.5899 | 153.8329 | 363.8776 | 380.8327 | 335.0975 | 255.8793 | 298.4589 | 223.3256
1302.3167 | 342.5094 | 153.9008 | 361.9154 | 379.0186 | 333.9191 | 256.0223 | 298.6395 | 223.4879
1303.3167 | 342.0646 | 154.0675 | 360.706 | 378.0384 | 332.8757 | 256.1765 | 298.8257 | 223.6507
1304.3167 | 341.5226 | 154.2647 | 359.4936 | 377.2959 | 332.1744 | 256.3218 | 298.9987 | 223.8274
1305.3167 | 340.8127 | 154.4849 | 360.662 | 377.5256 | 331.6208 | 256.4945 | 299.1578 | 224.0177
1306.3167 | 340.0891 | 154.6429 | 360.7192 | 377.1499 | 331.4621 | 256.6734 | 299.321 | 224.2365
1307.3167 | 340.9269 | 154.7585 | 360.5227 | 376.488 | 330.9537 | 256.8556 | 299.4855 | 224.4489
1308.3167 | 340.6384 | 154.894 | 359.8828 | 375.1388 | 330.2144 | 257.0315 | 299.6567 | 224.6077
1309.3167 | 340.5928 | 155.0432 | 359.5227 | 374.3428 | 328.9047 | 257.5688 | 299.8393 | 224.748
1310.3167 | 340.3475 | 155.2171 | 360.0753 | 373.9241 | 328.5523 | 257.3107 | 300.0434 | 224.8979
1311.3167 | 340.622 | 155.3962 | 359.0488 | 373.8304 | 328.1843 | 257.4531 | 300.1959 | 225.0634
1312.3167 | 340.953 | 155.6193 | 360.7707 | 374.1026 | 328.9117 | 257.6365 | 300.3957 | 225.2113
1313.3167 | 341.019 | 155.7959 | 360.859 | 373.0774 | 328.3294 | 257.8698 | 300.5573 | 225.3831
1314.3167 | 340.4949 | 156.0618 | 361.4305 | 371.6269 | 327.4449 | 258.0776 | 300.7479 | 225.5606
1315.3167 | 340.7666 | 156.3562 | 359.9641 | 370.3033 | 326.1547 | 258.5187 | 300.8853 | 225.7487
1316.3167 | 340.1904 | 156.5851 | 359.6502 | 369.5948 | 325.2133 | 258.4909 | 301.0725 | 225.9419
1317.3167 | 340.7489 | 156.7899 | 360.8426 | 371.0166 | 325.1657 | 258.6483 | 301.2372 | 226.111
1318.3167 | 342.0609 | 156.9411 | 362.2434 | 372.7608 | 325.9813 | 258.7808 | 301.427 | 226.3192
1319.3167 | 342.1766 | 157.1555 | 363.3232 | 372.8641 | 326.68 | 258.9511 | 301.6053 | 226.461
1320.3167 | 342.0742 | 157.2872 | 362.0796 | 371.5415 | 326.3602 | 259.1059 | 301.7701 | 226.6657
1321.3167 | 342.4728 | 157.4678 | 360.9085 | 369.7553 | 325.2731 | 259.2323 | 301.9427 | 226.8242
1322.3167 | 342.8905 | 157.6411 | 359.4101 | 368.5928 | 324.262 | 259.3813 | 302.1085 | 226.9686
1323.3167 | 342.1867 | 157.8106 | 358.776 | 368.3447 | 324.1842 | 259.4906 | 302.286 | 227.1288
1324.3167 | 342.4031 | 158.0026 | 358.2244 | 369.2229 | 324.3278 | 259.6403 | 302.4473 | 227.3003
1325.3167 | 342.7661 | 158.1907 | 358.4192 | 369.9462 | 325.8101 | 259.8048 | 302.606 | 227.4719
1326.3167 | 342.0878 | 158.3815 | 358.8992 | 370.0922 | 326.5658 | 259.9617 | 302.7944 | 227.6059
1327.3167 | 341.4857 | 158.5377 | 358.3561 | 369.9899 | 326.6754 | 260.1184 | 302.9769 | 227.776
1328.3167 | 341.7981 | 158.7544 | 358.6 | 369.9279 | 326.5008 | 260.2611 | 303.1572 | 227.9413
1329.3167 | 342.301 | 158.9619 | 358.9361 | 370.751 | 326.3934 | 260.4096 | 303.309 | 228.0951
1330.3167 | 342.671 | 159.1396 | 359.4402 | 371.1876 | 326.2108 | 261.1292 | 303.4897 | 228.2658
1331.3167 | 342.6853 | 159.3162 | 359.1156 | 370.6081 | 325.8927 | 261.2487 | 303.6598 | 228.4222
1332.3167 | 342.1413 | 159.5194 | 358.8943 | 370.2996 | 325.6345 | 261.439 | 303.8367 | 228.559
1333.3167 | 340.9842 | 159.6221 | 358.7223 | 369.7717 | 324.7777 | 261.612 | 304.0154 | 228.7304
1334.3167 | 342.0292 | 159.7954 | 358.7023 | 368.9676 | 323.8774 | 261.7467 | 304.2085 | 228.9079
1335.3167 | 342.517 | 159.9703 | 358.4784 | 368.3864 | 324.1304 | 261.9338 | 304.3901 | 229.0113
1336.3167 | 342.3606 | 160.1439 | 359.8439 | 367.354 | 324.0275 | 262.1073 | 304.5514 | 229.1621
1337.3167 | 341.8737 | 160.337 | 359.0947 | 367.0726 | 323.5481 | 262.2668 | 304.7415 | 229.3197
1338.3167 | 341.887 | 160.519 | 358.8709 | 366.5292 | 323.1519 | 262.4288 | 304.9158 | 229.4894
1339.3167 | 340.7455 | 160.6635 | 360.179 | 366.2857 | 322.9479 | 262.5972 | 305.063 | 229.639
1340.3167 | 339.7086 | 160.7891 | 361.5164 | 366.9114 | 323.2606 | 262.7874 | 305.2412 | 229.8089
1341.3167 | 339.219 | 160.9509 | 361.6019 | 367.5512 | 324.1503 | 262.9765 | 305.3927 | 229.9845
1342.3167 | 339.4348 | 161.1434 | 363.1683 | 368.2648 | 324.8248 | 263.1899 | 305.5744 | 230.1491
1343.3167 | 339.2962 | 161.3251 | 364.1733 | 369.0819 | 325.2184 | 263.4306 | 305.7404 | 230.2948
1344.3167 | 339.8548 | 161.4765 | 364.3649 | 369.5859 | 325.0258 | 263.6572 | 305.88 | 230.4692
1345.3167 | 339.9989 | 161.6097 | 364.9301 | 369.7203 | 325.3239 | 264.0293 | 306.0417 | 230.5976
1346.3167 | 339.4606 | 161.788 | 366.1618 | 370.9702 | 325.6648 | 264.5993 | 306.211 | 230.7524
1347.3167 | 339.7496 | 162.0025 | 366.7602 | 372.3164 | 326.3117 | 264.5687 | 306.3902 | 230.9182
1348.3167 | 339.4644 | 162.1851 | 366.8215 | 372.2553 | 326.3818 | 264.7554 | 306.5356 | 231.077
1349.3167 | 339.2045 | 162.4236 | 366.9923 | 373.0519 | 326.895 | 264.9287 | 306.6909 | 231.2422
1350.3167 | 340.0954 | 162.5962 | 367.0884 | 374.7084 | 326.8962 | 265.1155 | 306.8913 | 231.3849
1351.3167 | 341.5394 | 162.7494 | 368.59 | 376.1454 | 328.3551 | 265.2964 | 307.048 | 231.5445
1352.3167 | 342.7248 | 162.8956 | 370.4954 | 378.3455 | 330.8946 | 265.4985 | 307.2316 | 231.746
1353.3167 | 343.7034 | 163.073 | 370.8078 | 380.5119 | 332.7961 | 265.6586 | 307.3882 | 231.8712
1354.3167 | 343.8199 | 163.2994 | 370.9212 | 381.4744 | 333.7771 | 265.8458 | 307.5669 | 232.0347
1355.3167 | 344.5177 | 163.4958 | 371.2003 | 383.2087 | 334.5445 | 266.286 | 307.7335 | 232.1839
1356.3167 | 344.6935 | 163.567 | 373.4263 | 385.1796 | 336.0523 | 266.4043 | 307.8733 | 232.2978
1357.3167 | 345.5454 | 163.8874 | 373.9574 | 385.7991 | 335.329 | 266.4277 | 308.0083 | 232.5556
1358.3167 | 346.1012 | 164.1155 | 375.8922 | 387.918 | 335.2317 | 266.6177 | 308.1595 | 232.6592
1359.3167 | 345.8483 | 164.3112 | 375.6203 | 388.5922 | 335.9231 | 266.7888 | 308.3176 | 232.8859
1360.3167 | 346.0991 | 164.4896 | 375.2208 | 388.3208 | 336.0632 | 266.9868 | 308.4783 | 233.003
1361.3167 | 345.2423 | 164.6878 | 373.9456 | 387.0955 | 335.6671 | 267.1542 | 308.6341 | 233.1222
1362.3167 | 344.7983 | 164.8795 | 371.0794 | 385.0647 | 334.7013 | 267.3286 | 308.7483 | 233.2872
1363.3167 | 344.8211 | 165.0987 | 368.7662 | 383.557 | 333.9502 | 267.4495 | 308.9008 | 233.4372
1364.3167 | 344.0969 | 165.2793 | 368.23 | 382.6631 | 333.5753 | 267.5912 | 309.0729 | 233.594
1365.3167 | 343.526 | 165.3756 | 367.4189 | 382.452 | 333.2871 | 267.705 | 309.2395 | 233.7685
1366.3167 | 342.6087 | 165.5498 | 366.8434 | 381.7062 | 332.6502 | 267.8513 | 309.4052 | 233.9304
1367.3167 | 342.5715 | 165.7573 | 366.7349 | 380.6571 | 332.373 | 267.9126 | 309.5455 | 234.0739
1368.3167 | 341.938 | 165.8875 | 365.0377 | 378.2881 | 331.5117 | 268.0851 | 309.7239 | 234.2269
1369.3167 | 342.4916 | 166.1831 | 363.7254 | 376.2089 | 330.3406 | 268.1739 | 309.8817 | 234.3951
1370.3167 | 342.2403 | 166.4109 | 363.0027 | 375.5593 | 329.2484 | 268.2486 | 310.0697 | 234.5198
1371.3167 | 341.5304 | 166.6435 | 364.5757 | 376.0502 | 328.9861 | 268.3817 | 310.2278 | 234.6328
1372.3167 | 341.7641 | 166.8215 | 366.0328 | 377.6096 | 330.0246 | 268.5549 | 310.3699 | 234.7609
1373.3167 | 341.6804 | 167.0729 | 366.1477 | 378.1394 | 331.3148 | 269.081 | 310.5322 | 234.8987
1374.3167 | 343.0241 | 167.1874 | 366.2272 | 377.9159 | 331.6749 | 269.2035 | 310.7166 | 235.0249
1375.3167 | 343.6193 | 167.3462 | 364.6309 | 377.3409 | 331.3397 | 269.1995 | 310.8955 | 235.2073
1376.3167 | 343.4104 | 167.5731 | 362.3254 | 375.84 | 330.4433 | 269.3793 | 311.0715 | 235.3065
1377.3167 | 343.1699 | 167.7461 | 360.5877 | 374.8671 | 329.5369 | 269.5362 | 311.2297 | 235.4534
1378.3167 | 342.9655 | 167.9661 | 359.4715 | 374.3039 | 328.7608 | 269.8894 | 311.3932 | 235.6433
1379.3167 | 342.4376 | 168.1308 | 359.6497 | 375.2662 | 329.3174 | 269.7004 | 311.5314 | 235.8817
1380.3167 | 341.8941 | 168.2128 | 360.1979 | 376.1174 | 330.8264 | 269.837 | 311.6841 | 235.9795
1381.3167 | 341.6079 | 168.2814 | 359.7993 | 375.8844 | 331.4497 | 270.0057 | 311.8165 | 236.0791
1382.3167 | 341.4094 | 168.5094 | 359.3793 | 374.9573 | 331.0698 | 270.1291 | 311.9507 | 236.198
1383.3167 | 342.2683 | 168.8942 | 358.938 | 373.9385 | 330.1008 | 270.2708 | 312.1088 | 236.3843
1384.3167 | 342.2086 | 169.0837 | 357.6084 | 372.9038 | 329.2523 | 270.3436 | 312.2396 | 236.499
1385.3167 | 342.2694 | 169.2351 | 357.4077 | 371.7397 | 328.1154 | 270.4659 | 312.3949 | 236.6398
1386.3167 | 342.3557 | 169.3735 | 356.8532 | 371.0194 | 327.2055 | 270.5926 | 312.5268 | 236.7431
1387.3167 | 341.8124 | 169.5724 | 356.5139 | 370.3765 | 326.7797 | 270.7241 | 312.6622 | 236.8871
1388.3167 | 342.3616 | 169.7736 | 356.9957 | 369.5934 | 326.185 | 270.8081 | 312.808 | 237.0106
1389.3167 | 341.4424 | 169.9944 | 357.7979 | 368.891 | 325.7933 | 270.9355 | 312.9852 | 237.1589
1390.3167 | 340.5638 | 170.232 | 358.0929 | 368.9911 | 325.5816 | 271.0508 | 313.134 | 237.3143
1391.3167 | 340.5354 | 170.355 | 358.4107 | 370.0952 | 326.2508 | 271.1699 | 313.2944 | 237.4455
1392.3167 | 340.3602 | 170.5124 | 358.1324 | 370.0281 | 326.2863 | 271.1388 | 313.4762 | 237.5659
1393.3167 | 340.4064 | 170.7733 | 358.5025 | 370.0485 | 326.1203 | 271.2652 | 313.6376 | 237.7153
1394.3167 | 340.4191 | 171.0232 | 358.2444 | 370.4666 | 325.5149 | 271.4013 | 313.7854 | 237.8931
1395.3167 | 340.8258 | 171.1714 | 356.8653 | 370.3596 | 325.5159 | 271.5114 | 313.9424 | 238.0774
1396.3167 | 340.9924 | 171.2891 | 356.2199 | 369.8517 | 325.8151 | 271.8647 | 314.0951 | 238.2457
1397.3167 | 340.891 | 171.5046 | 357.7591 | 369.6328 | 325.4369 | 272.0367 | 314.2444 | 238.3752
1398.3167 | 340.9044 | 171.7058 | 357.7998 | 369.056 | 325.1571 | 272.1252 | 314.4143 | 238.5383
1399.3167 | 341.0968 | 171.8952 | 357.2544 | 368.9637 | 324.5196 | 272.1605 | 314.6057 | 238.6901
1400.3167 | 340.5332 | 172.0335 | 355.2554 | 367.7501 | 323.6555 | 272.3681 | 314.7596 | 238.8384
1401.3167 | 340.5642 | 172.2133 | 355.614 | 367.1608 | 322.8522 | 272.5577 | 314.9217 | 238.9634
1402.3167 | 340.351 | 172.3753 | 357.5487 | 368.2017 | 323.7034 | 272.6245 | 315.0814 | 239.0948
1403.3167 | 340.274 | 172.606 | 358.6438 | 369.4217 | 324.8393 | 272.6923 | 315.2437 | 239.2534
1404.3167 | 340.9269 | 172.817 | 358.9659 | 368.9544 | 325.0686 | 272.8387 | 315.4269 | 239.4118
1405.3167 | 341.442 | 173.0453 | 358.9248 | 367.9052 | 324.8378 | 272.9821 | 315.5787 | 239.5535
1406.3167 | 341.3402 | 173.2396 | 359.0064 | 366.8269 | 324.457 | 273.0987 | 315.7346 | 239.6807
1407.3167 | 341.7757 | 173.4431 | 359.3222 | 366.5064 | 323.9667 | 273.2537 | 315.8775 | 239.8491
1408.3167 | 341.0458 | 173.5902 | 360.6036 | 366.7073 | 323.8588 | 274.0717 | 316.0207 | 239.9834
1409.3167 | 340.5924 | 173.8371 | 361.6395 | 367.0143 | 323.4409 | 274.1869 | 316.159 | 240.11
1410.3167 | 341.2302 | 174.1246 | 361.6369 | 367.1998 | 323.985 | 274.1743 | 316.3162 | 240.2708
1411.3167 | 340.8288 | 174.4691 | 362.4169 | 366.6395 | 324.1224 | 274.3092 | 316.4699 | 240.4093
1412.3167 | 340.9561 | 174.7051 | 361.8339 | 366.3684 | 324.0095 | 274.4544 | 316.6215 | 240.5564
1413.3167 | 340.6071 | 174.9232 | 361.4308 | 366.5426 | 323.8181 | 274.5876 | 316.7683 | 240.708
1414.3167 | 340.9916 | 175.1318 | 360.7705 | 366.0564 | 323.605 | 275.0295 | 316.9473 | 240.8257
1415.3167 | 341.6689 | 175.2939 | 360.4757 | 365.313 | 323.2292 | 275.1405 | 317.0924 | 240.9641
1416.3167 | 341.665 | 175.4839 | 360.2689 | 363.7592 | 322.8475 | 275.0094 | 317.2438 | 241.0971
1417.3167 | 341.1339 | 175.719 | 359.8457 | 363.2354 | 322.0893 | 275.0805 | 317.3901 | 241.2166
1418.3167 | 340.8403 | 176.0062 | 359.6928 | 363.5382 | 321.6697 | 275.2131 | 317.541 | 241.358
1419.3167 | 340.8819 | 176.1686 | 359.1573 | 363.1352 | 321.5127 | 275.2871 | 317.672 | 241.4771
1420.3167 | 340.5898 | 176.344 | 357.9224 | 362.7202 | 321.2349 | 275.5977 | 317.8345 | 241.6154
1421.3167 | 340.4152 | 176.4771 | 355.9571 | 362.5125 | 322.5937 | 275.6383 | 317.9807 | 241.7644
1422.3167 | 339.3333 | 176.6944 | 354.7905 | 362.7182 | 323.177 | 275.8479 | 318.0973 | 241.8958
1423.3167 | 338.455 | 176.9259 | 354.5379 | 362.4969 | 323.1851 | 275.853 | 318.2568 | 242.036
1424.3167 | 337.2766 | 177.0372 | 356.1023 | 362.3041 | 323.1092 | 275.9542 | 318.3906 | 242.1927
1425.3167 | 336.9168 | 177.1942 | 356.1651 | 361.6511 | 322.285 | 276.0795 | 318.5359 | 242.3349
1426.3167 | 336.7948 | 177.4912 | 356.298 | 361.4932 | 321.8104 | 276.1423 | 318.6829 | 242.4648
1427.3167 | 335.9332 | 177.6544 | 356.6475 | 361.2043 | 321.2864 | 276.2697 | 318.8297 | 242.5924
1428.3167 | 335.846 | 177.7954 | 355.7944 | 360.334 | 320.7447 | 276.376 | 318.977 | 242.7306
1429.3167 | 336.4062 | 178.0907 | 355.0541 | 359.8483 | 320.6701 | 276.5263 | 319.1202 | 242.8927
1430.3167 | 336.7574 | 178.3019 | 354.9825 | 359.8591 | 320.8001 | 276.8536 | 319.2799 | 243.0389
1431.3167 | 336.6964 | 178.5706 | 354.5728 | 360.4989 | 321.7973 | 276.8212 | 319.4242 | 243.2095
1432.3167 | 336.3304 | 178.8536 | 354.2319 | 360.6752 | 322.3954 | 276.8778 | 319.5829 | 243.3512
1433.3167 | 335.6263 | 179.0304 | 353.3322 | 360.6177 | 322.5939 | 276.9985 | 319.7355 | 243.4795
1434.3167 | 335.1565 | 179.1311 | 352.5166 | 360.1652 | 322.2006 | 277.0947 | 319.8603 | 243.6355
1435.3167 | 335.5874 | 179.2515 | 352.3045 | 359.3099 | 321.3425 | 277.1878 | 320.0072 | 243.7478
1436.3167 | 335.2606 | 179.3195 | 351.9276 | 360.1927 | 321.1962 | 277.2658 | 320.1597 | 243.8725
1437.3167 | 335.0154 | 179.497 | 351.9353 | 360.4975 | 321.4146 | 277.7822 | 320.2898 | 243.9816
1438.3167 | 334.546 | 179.7694 | 351.2342 | 359.9979 | 321.2946 | 277.7804 | 320.4252 | 244.0904
1439.3167 | 334.145 | 179.9835 | 350.8749 | 359.0973 | 320.5037 | 277.7091 | 320.5795 | 244.2075
1440.3167 | 333.6437 | 180.1614 | 350.7699 | 358.6394 | 319.8085 | 277.8021 | 320.7335 | 244.364
1441.3167 | 333.0042 | 180.355 | 351.9301 | 358.3161 | 319.3949 | 277.9072 | 320.8698 | 244.4737
1442.3167 | 332.6919 | 180.6112 | 353.293 | 358.0472 | 318.9048 | 278.0849 | 321.0414 | 244.6051
1443.3167 | 332.5663 | 180.8848 | 354.1393 | 357.6677 | 318.516 | 278.3089 | 321.1764 | 244.7575
1444.3167 | 332.764 | 181.0813 | 355.4372 | 358.006 | 318.135 | 278.4289 | 321.3328 | 244.8715
1445.3167 | 331.6152 | 181.2978 | 355.5278 | 357.5396 | 318.0956 | 278.5593 | 321.449 | 245.0084
1446.3167 | 331.0429 | 181.4913 | 355.5389 | 358.2915 | 318.2598 | 278.736 | 321.6097 | 245.124
1447.3167 | 330.6938 | 181.69 | 355.3779 | 357.9298 | 318.4978 | 278.8723 | 321.7332 | 245.2425
1448.3167 | 331.0693 | 181.9121 | 357.1989 | 359.8808 | 319.4057 | 279.0293 | 321.8414 | 245.4048
1449.3167 | 331.5121 | 182.0652 | 358.2333 | 360.9464 | 321.0898 | 279.1699 | 321.9865 | 245.5075
1450.3167 | 332.4267 | 182.2715 | 358.9675 | 361.2593 | 321.6365 | 279.3403 | 322.1143 | 245.5943
1451.3167 | 333.2667 | 182.472 | 361.45 | 363.5747 | 322.7099 | 279.5262 | 322.2707 | 245.7163
1452.3167 | 333.7964 | 182.6632 | 363.8744 | 364.0482 | 323.666 | 279.7198 | 322.4019 | 245.8535
1453.3167 | 334.161 | 182.926 | 364.4942 | 364.3718 | 323.5185 | 279.9361 | 322.5324 | 246.0107
1454.3167 | 333.7221 | 183.1616 | 365.3687 | 365.2158 | 323.4996 | 280.0933 | 322.6583 | 246.3633
1455.3167 | 333.8139 | 183.4068 | 365.3602 | 365.7818 | 323.7462 | 280.2439 | 322.7877 | 246.4181
1456.3167 | 333.9536 | 183.6485 | 365.5185 | 366.6352 | 324.0521 | 280.3292 | 322.9191 | 246.5011
1457.3167 | 334.5821 | 183.9494 | 366.774 | 368.6815 | 325.3962 | 280.4522 | 323.0493 | 246.6094
1458.3167 | 334.5538 | 184.1847 | 367.8193 | 369.486 | 327.2491 | 280.6166 | 323.1756 | 246.7379
1459.3167 | 334.573 | 184.4205 | 368.387 | 369.7411 | 328.1266 | 280.7669 | 323.3068 | 246.866
1460.3167 | 335.7864 | 184.6264 | 370.5031 | 371.1246 | 328.8186 | 280.9076 | 323.4137 | 246.9688
1461.3167 | 335.9415 | 184.8419 | 372.0676 | 372.5171 | 331.0048 | 281.0477 | 323.5593 | 247.1019
1462.3167 | 336.6967 | 185.0577 | 372.1651 | 372.4421 | 331.4511 | 281.1944 | 323.6727 | 247.2188
1463.3167 | 337.7134 | 185.2609 | 371.6908 | 372.2447 | 330.8347 | 281.37 | 323.7956 | 247.3427
1464.3167 | 337.8989 | 185.5043 | 370.6679 | 371.2685 | 330.1803 | 281.4887 | 323.9111 | 247.4345
1465.3167 | 338.4322 | 185.7606 | 370.9405 | 370.7325 | 329.5135 | 281.6461 | 324.0392 | 247.5576
1466.3167 | 338.5182 | 185.9991 | 369.7765 | 370.0452 | 328.8487 | 281.787 | 324.1445 | 247.6971
1467.3167 | 338.8018 | 186.2052 | 368.4599 | 369.183 | 328.0865 | 281.9186 | 324.2765 | 247.7971
1468.3167 | 339.8337 | 186.361 | 368.1959 | 370.1223 | 327.9722 | 282.0447 | 324.3945 | 247.9171
1469.3167 | 339.9857 | 186.5693 | 369.0917 | 371.8003 | 329.1302 | 282.2009 | 324.5196 | 248.018
1470.3167 | 340.6088 | 186.7795 | 368.7052 | 373.6318 | 329.9404 | 282.3807 | 324.6349 | 248.1415
1471.3167 | 340.931 | 186.9893 | 369.8769 | 374.8561 | 331.3261 | 282.5708 | 324.761 | 248.2673
1472.3167 | 342.3278 | 187.1864 | 370.6002 | 377.1207 | 333.7514 | 282.7242 | 324.9121 | 248.3657
1473.3167 | 343.4328 | 187.3625 | 370.8559 | 378.5747 | 335.2739 | 282.8859 | 325.0379 | 248.4739
1474.3167 | 344.1354 | 187.6073 | 372.3781 | 379.5532 | 335.7501 | 283.0339 | 325.1767 | 248.6083
1475.3167 | 344.4215 | 187.8199 | 372.9052 | 379.5568 | 336.216 | 283.1489 | 325.303 | 248.7391
1476.3167 | 344.5619 | 188.0365 | 373.0698 | 382.6326 | 336.5561 | 283.3084 | 325.4369 | 248.865
1477.3167 | 345.7722 | 188.2658 | 373.4264 | 383.221 | 337.0972 | 283.4896 | 325.5506 | 248.993
1478.3167 | 346.9867 | 188.5035 | 375.1576 | 384.4267 | 338.6936 | 283.6247 | 325.6892 | 249.0769
1479.3167 | 348.2532 | 188.7434 | 375.3381 | 385.4497 | 339.7412 | 283.7769 | 325.8084 | 249.1878
1480.3167 | 348.7551 | 188.9261 | 374.6966 | 386.3468 | 340.6671 | 283.9078 | 325.9138 | 249.299
1481.3167 | 348.0543 | 189.1658 | 373.6462 | 386.0759 | 340.7766 | 284.0462 | 326.0385 | 249.4106
1482.3167 | 347.9364 | 189.3507 | 372.6137 | 384.6726 | 340.0957 | 284.1771 | 326.1517 | 249.5553
1483.3167 | 348.7174 | 189.566 | 372.2821 | 383.7782 | 339.3359 | 284.3004 | 326.2569 | 249.6663
1484.3167 | 349.355 | 189.9279 | 371.612 | 383.6177 | 338.9557 | 284.4039 | 326.3999 | 249.8236
1485.3167 | 348.8317 | 190.1263 | 371.5942 | 383.2439 | 338.7244 | 284.4919 | 326.4933 | 249.9326
1486.3167 | 349.1666 | 190.3163 | 370.0524 | 382.5727 | 338.3016 | 284.5757 | 326.6405 | 250.0371
1487.3167 | 349.2719 | 190.5046 | 368.19 | 381.0471 | 337.4309 | 284.6866 | 326.742 | 250.1652
1488.3167 | 349.4427 | 190.733 | 367.6934 | 380.2518 | 336.8095 | 284.7949 | 326.858 | 250.2755
1489.3167 | 349.2141 | 190.9985 | 366.8367 | 380.0794 | 336.2611 | 284.8554 | 326.9848 | 250.423
1490.3167 | 349.8049 | 191.1242 | 366.4416 | 379.1098 | 335.9467 | 284.9883 | 327.1343 | 250.5268
1491.3167 | 349.2026 | 191.4396 | 367.0708 | 378.1974 | 335.0622 | 285.1006 | 327.2387 | 250.6297
1492.3167 | 349.3853 | 191.6715 | 368.3063 | 378.562 | 334.0434 | 285.2127 | 327.3613 | 250.7409
1493.3167 | 349.2514 | 191.9472 | 369.5562 | 379.8586 | 334.47 | 285.3632 | 327.4904 | 250.8775
1494.3167 | 348.9712 | 192.229 | 369.6559 | 380.9024 | 334.4007 | 285.5009 | 327.6074 | 250.9819
1495.3167 | 348.5669 | 192.4971 | 369.2594 | 381.8046 | 334.3417 | 285.6504 | 327.7361 | 251.0967
1496.3167 | 349.0967 | 192.7426 | 369.7313 | 382.1463 | 333.8734 | 285.7789 | 327.8531 | 251.2137
1497.3167 | 349.3148 | 192.979 | 370.1166 | 382.3721 | 333.3632 | 285.9167 | 327.9914 | 251.3222
1498.3167 | 349.8483 | 193.2804 | 371.5225 | 382.6194 | 333.695 | 286.0697 | 328.1215 | 251.4229
1499.3167 | 349.3355 | 193.5101 | 371.5803 | 382.3548 | 333.8179 | 286.224 | 328.2598 | 251.5625
1500.3167 | 350.2388 | 193.7301 | 371.5158 | 382.6171 | 333.6347 | 286.374 | 328.3855 | 251.6432
1501.3167 | 350.5479 | 193.9408 | 373.1925 | 383.5045 | 334.488 | 286.5348 | 328.5132 | 251.7894
1502.3167 | 350.5333 | 194.172 | 373.6876 | 383.6495 | 335.3239 | 286.7402 | 328.6542 | 251.8815
1503.3167 | 351.1613 | 194.478 | 374.1559 | 384.0324 | 335.466 | 286.9402 | 328.8283 | 251.9916
1504.3167 | 352.5444 | 194.7558 | 373.8554 | 385.3379 | 335.8765 | 287.1421 | 328.964 | 252.0956
1505.3167 | 354.5492 | 194.9013 | 372.1465 | 387.0382 | 336.6014 | 287.2948 | 329.1012 | 252.2053
1506.3167 | 355.7354 | 195.1396 | 371.7696 | 388.6563 | 336.72 | 287.4646 | 329.2481 | 252.3269
1507.3167 | 357.3031 | 195.3998 | 371.625 | 389.1718 | 336.8333 | 287.9546 | 329.3806 | 252.4208
1508.3167 | 356.4754 | 195.6189 | 372.487 | 390.0549 | 336.6017 | 288.1666 | 329.4849 | 252.5367
1509.3167 | 355.7331 | 195.911 | 372.7219 | 390.4732 | 337.1266 | 287.9344 | 329.6104 | 252.6206
1510.3167 | 354.8011 | 196.1503 | 372.3718 | 390.7447 | 338.2986 | 288.1338 | 329.7403 | 252.7667
1511.3167 | 354.9663 | 196.3854 | 371.7083 | 391.7931 | 339.368 | 288.2683 | 329.8677 | 252.8678
1512.3167 | 355.009 | 196.5798 | 371.7006 | 393.3326 | 340.9999 | 288.4085 | 330.0317 | 252.9868
1513.3167 | 355.1057 | 196.8081 | 371.4919 | 393.6259 | 342.4234 | 288.5383 | 330.1682 | 253.0836
1514.3167 | 355.9295 | 196.9959 | 370.6378 | 394.9303 | 343.7026 | 288.7553 | 330.2972 | 253.1997
1515.3167 | 356.6976 | 197.3069 | 370.8437 | 395.4205 | 344.5759 | 288.8479 | 330.4305 | 253.2977
1516.3167 | 356.9074 | 197.3841 | 372.3949 | 396.4208 | 345.6493 | 288.916 | 330.586 | 253.4037
1517.3167 | 357.1769 | 197.6811 | 372.4873 | 397.2446 | 345.7954 | 289.0373 | 330.7258 | 253.5111
1518.3167 | 356.8234 | 197.9813 | 372.0604 | 397.6 | 346.6892 | 289.1335 | 330.8798 | 253.6126
1519.3167 | 357.3651 | 198.271 | 373.4161 | 398.6351 | 347.5192 | 289.4348 | 331.0205 | 253.7446
1520.3167 | 357.8771 | 198.5079 | 374.2215 | 399.1546 | 348.5285 | 289.6654 | 331.1663 | 253.8841
1521.3167 | 357.9 | 198.7312 | 374.7836 | 398.6992 | 348.7939 | 289.1761 | 331.311 | 253.957
1522.3167 | 357.8747 | 198.9461 | 374.937 | 398.2485 | 348.7603 | 289.4942 | 331.4439 | 254.0654
1523.3167 | 357.1557 | 199.1272 | 373.5437 | 396.2761 | 347.765 | 289.5224 | 331.5793 | 254.2081
1524.3167 | 356.341 | 199.4702 | 372.4849 | 395.5746 | 347.3888 | 289.6486 | 331.7352 | 254.3026
1525.3167 | 355.6699 | 199.8435 | 370.9851 | 393.4618 | 346.7983 | 289.8 | 331.8842 | 254.3934
1526.3167 | 355.0807 | 200.21 | 370.5606 | 393.2125 | 346.2313 | 289.9577 | 332.0215 | 254.4893
1527.3167 | 354.5802 | 200.4322 | 370.1767 | 392.0246 | 346.0801 | 289.8755 | 332.1487 | 254.5963
1528.3167 | 354.4388 | 200.6988 | 370.0028 | 392.063 | 345.9334 | 290.1907 | 332.3189 | 254.7233
1529.3167 | 354.4325 | 200.9811 | 369.7048 | 391.1217 | 344.8135 | 290.3246 | 332.4507 | 254.7948
1530.3167 | 354.5527 | 201.0994 | 368.4105 | 389.4199 | 343.9097 | 290.2398 | 332.6123 | 254.9307
1531.3167 | 353.9751 | 201.2887 | 367.3353 | 388.035 | 343.1878 | 290.8415 | 332.7647 | 255.042
1532.3167 | 354.6375 | 201.4963 | 366.3547 | 387.1778 | 342.6381 | 290.7212 | 332.9074 | 255.1409
1533.3167 | 354.5569 | 201.6153 | 365.8996 | 387.6086 | 342.8292 | 290.8249 | 333.0702 | 255.2511
1534.3167 | 354.2777 | 201.8926 | 367.2753 | 388.6 | 343.0444 | 290.8929 | 333.2493 | 255.3869
1535.3167 | 354.8653 | 202.1534 | 370.0613 | 390.5164 | 344.7606 | 290.809 | 333.4002 | 255.4704
1536.3167 | 357.1375 | 202.5778 | 370.8954 | 392.2094 | 344.6663 | 291.0072 | 333.5338 | 255.5991
1537.3167 | 357.8343 | 202.8719 | 370.5641 | 393.0017 | 344.6155 | 291.476 | 333.7064 | 255.7023
1538.3167 | 358.2493 | 203.1324 | 371.0337 | 393.5904 | 343.8126 | 291.5635 | 333.8429 | 255.8166
1539.3167 | 359.6537 | 203.3921 | 372.417 | 395.2233 | 343.4523 | 291.8015 | 334.0031 | 255.9008
1540.3167 | 361.365 | 203.5657 | 372.9772 | 397.5048 | 344.1726 | 291.9779 | 334.1556 | 256.0804
1541.3167 | 363.2664 | 203.7977 | 372.9327 | 399.6541 | 344.9271 | 292.1407 | 334.2999 | 256.1693
1542.3167 | 363.7237 | 204.0255 | 373.2537 | 401.6555 | 345.5856 | 292.3276 | 334.4607 | 256.2845
1543.3167 | 363.6812 | 204.2531 | 372.2278 | 403.0534 | 346.4326 | 292.3663 | 334.6058 | 256.3833
1544.3167 | 363.0338 | 204.4208 | 372.7944 | 404.0474 | 347.3291 | 292.6193 | 334.7934 | 256.4633
1545.3167 | 361.9847 | 204.685 | 373.927 | 404.3774 | 347.6404 | 292.6595 | 334.9631 | 256.6217
1546.3167 | 361.5308 | 204.8743 | 374.6476 | 403.7644 | 347.4751 | 292.6701 | 335.1008 | 256.6945
1547.3167 | 360.7981 | 205.1015 | 375.402 | 403.3021 | 348.1075 | 292.7334 | 335.261 | 256.8158
1548.3167 | 360.5958 | 205.4242 | 375.3357 | 403.6976 | 347.8479 | 292.9651 | 335.4144 | 256.9444
1549.3167 | 360.4687 | 205.7058 | 375.3104 | 403.0973 | 348.4899 | 292.8799 | 335.581 | 257.0461
1550.3167 | 361.4767 | 205.9747 | 375.878 | 403.7699 | 349.3208 | 293.1527 | 335.7264 | 257.1457
1551.3167 | 362.2479 | 206.233 | 376.9398 | 404.9169 | 349.5433 | 293.524 | 335.8923 | 257.2501
1552.3167 | 362.9901 | 206.4925 | 376.4133 | 405.7942 | 349.0641 | 293.5696 | 336.0598 | 257.3755
1553.3167 | 364.0988 | 206.7344 | 376.2111 | 406.0781 | 348.4975 | 293.9018 | 336.2146 | 257.4837
1554.3167 | 364.8288 | 207.0387 | 375.9756 | 406.446 | 348.0934 | 293.9131 | 336.3781 | 257.5881
1555.3167 | 365.7519 | 207.4091 | 376.1336 | 406.2036 | 347.9319 | 294.0654 | 336.5556 | 257.6905
1556.3167 | 366.2136 | 207.6751 | 375.7146 | 406.1804 | 347.7366 | 294.2293 | 336.7469 | 257.8289
1557.3167 | 367.1609 | 208.0227 | 376.6068 | 407.1347 | 347.8068 | 294.255 | 336.9004 | 257.9113
1558.3167 | 367.1393 | 208.2674 | 376.364 | 407.4916 | 348.1884 | 294.357 | 337.0855 | 258.0319
1559.3167 | 367.5299 | 208.4824 | 376.0117 | 407.5851 | 348.1124 | 294.3688 | 337.2517 | 258.1299
1560.3167 | 367.0548 | 208.6569 | 375.6702 | 408.4419 | 348.5054 | 294.4662 | 337.41 | 258.2154
1561.3167 | 367.7357 | 208.8562 | 375.1498 | 408.7245 | 348.8208 | 294.3932 | 337.5922 | 258.308
1562.3167 | 367.688 | 209.0513 | 374.819 | 408.3128 | 349.2867 | 294.1548 | 337.7603 | 258.4242
1563.3167 | 368.4974 | 208.5357 | 374.2403 | 408.0835 | 349.3583 | 294.1024 | 337.948 | 258.5273
1564.3167 | 370.4053 | 208.8173 | 375.342 | 408.4001 | 349.8887 | 294.1972 | 338.1275 | 258.648
1565.3167 | 369.3756 | 209.0807 | 376.3185 | 408.0095 | 349.8257 | 294.5618 | 338.3036 | 258.7544
1566.3167 | 369.3345 | 209.4804 | 377.1924 | 407.4591 | 349.035 | 294.7431 | 338.485 | 258.8803
1567.3167 | 370.5446 | 209.8343 | 378.6757 | 407.7422 | 348.6811 | 295.0298 | 338.6621 | 258.9913
1568.3167 | 371.2152 | 210.1139 | 378.9533 | 407.8974 | 348.7729 | 295.1692 | 338.852 | 259.1003
1569.3167 | 372.586 | 210.5411 | 379.2631 | 408.7207 | 349.3233 | 295.4693 | 339.0254 | 259.2215
1570.3167 | 372.057 | 210.729 | 378.1906 | 408.801 | 350.4726 | 295.5815 | 339.2137 | 259.3376
1571.3167 | 371.3323 | 210.9031 | 377.973 | 409.2077 | 350.3741 | 295.774 | 339.4022 | 259.4429
1572.3167 | 371.4208 | 211.2304 | 377.1502 | 408.8003 | 349.9503 | 295.8413 | 339.5961 | 259.55
1573.3167 | 372.2725 | 211.4377 | 376.8694 | 408.2219 | 349.6939 | 295.9258 | 339.7754 | 259.6503
1574.3167 | 373.0101 | 211.7265 | 376.7385 | 408.4771 | 350.1005 | 296.0855 | 339.9527 | 259.7602
1575.3167 | 372.3458 | 211.8749 | 376.709 | 408.7707 | 351.375 | 296.1122 | 340.1508 | 259.8862
1576.3167 | 373.0059 | 212.0061 | 376.0132 | 408.324 | 352.4266 | 296.3284 | 340.3683 | 259.9959
1577.3167 | 372.1064 | 212.0439 | 375.5556 | 408.0693 | 352.9042 | 296.4223 | 340.549 | 260.1241
1578.3167 | 370.3772 | 211.9105 | 376.2737 | 408.4084 | 354.3101 | 296.6287 | 340.7468 | 260.2222
1579.3167 | 370.5228 | 212.4104 | 377.6544 | 409.7287 | 354.6697 | 297.3186 | 341.0513 | 260.5709
1580.3167 | 369.6825 | 212.4875 | 377.8995 | 409.4047 | 355.6228 | 296.7317 | 341.1472 | 260.4561
1581.3167 | 370.4052 | 212.8339 | 378.7905 | 408.8468 | 357.41 | 297.5918 | 341.4695 | 260.841
1582.3167 | 370.0954 | 212.9645 | 379.2974 | 409.9434 | 357.9643 | 296.9675 | 341.5418 | 260.7065
1583.3167 | 370.437 | 213.1754 | 380.0675 | 410.2059 | 358.7587 | 297.1426 | 341.7432 | 260.8341
1584.3167 | 370.6256 | 213.2401 | 379.5776 | 409.5676 | 358.8067 | 297.3388 | 341.9422 | 260.9441
1585.3167 | 370.4552 | 213.462 | 379.9792 | 409.0034 | 358.4121 | 297.4407 | 342.1689 | 261.0672
1586.3167 | 369.7978 | 213.5366 | 380.3564 | 408.6865 | 358.1179 | 297.5857 | 342.3719 | 261.1818
1587.3167 | 370.8022 | 213.9305 | 381.3533 | 409.0467 | 359.0067 | 297.7602 | 342.6038 | 261.2913
1588.3167 | 371.1631 | 213.9677 | 382.1131 | 409.9731 | 359.5238 | 297.8515 | 342.8053 | 261.4232
1589.3167 | 372.4104 | 214.2613 | 382.6475 | 410.5946 | 360.0926 | 297.9715 | 343.0093 | 261.5234
1590.3167 | 371.7543 | 214.4149 | 382.9125 | 410.3489 | 360.5529 | 298.0524 | 343.2284 | 261.6222
1591.3167 | 371.6688 | 214.5128 | 381.7976 | 409.3873 | 360.524 | 298.1033 | 343.4492 | 261.6909
1592.3167 | 369.9823 | 214.7948 | 380.7883 | 408.6244 | 361.3044 | 298.2261 | 343.6764 | 261.8084
1593.3167 | 371.8668 | 215.0959 | 379.9973 | 407.7815 | 362.1338 | 298.2726 | 343.8946 | 261.9268
1594.3167 | 372.5889 | 215.3486 | 378.7536 | 406.882 | 362.6208 | 298.4251 | 344.1219 | 262.0394
1595.3167 | 372.2712 | 215.4281 | 377.191 | 405.5849 | 362.5829 | 298.5026 | 344.3434 | 262.1421
1596.3167 | 372.6678 | 215.6064 | 375.4111 | 404.4497 | 361.9487 | 298.6334 | 344.5776 | 262.2868
1597.3167 | 373.0371 | 215.7517 | 375.1958 | 403.9082 | 361.0138 | 298.7088 | 344.8032 | 262.3757
1598.3167 | 374.3141 | 216.0071 | 374.8605 | 404.5919 | 360.2443 | 298.8119 | 345.0538 | 262.49
1599.3167 | 376.4676 | 216.0663 | 373.8816 | 404.1131 | 359.1533 | 298.8815 | 345.2994 | 262.5671
1600.3167 | 378.1988 | 216.2079 | 374.5229 | 404.3582 | 358.7209 | 299.0139 | 345.5255 | 262.6591
1601.3167 | 376.7335 | 216.4112 | 376.7832 | 405.6679 | 358.4279 | 299.2398 | 345.7621 | 262.7398
1602.3167 | 377.4949 | 216.9413 | 378.5193 | 407.6614 | 356.7418 | 301.0105 | 346.558 | 263.568
1603.3167 | 376.8674 | 216.9335 | 379.2196 | 409.8939 | 356.2754 | 301.1778 | 346.5273 | 263.5051
1604.3167 | 376.0584 | 216.9889 | 380.2567 | 411.4402 | 355.9161 | 300.0558 | 346.538 | 263.1521
1605.3167 | 376.2823 | 217.1122 | 379.9899 | 413.4245 | 356.2482 | 300.037 | 346.722 | 263.1855
1606.3167 | 378.4819 | 217.3474 | 380.554 | 415.6632 | 356.7086 | 300.2756 | 346.9448 | 263.3091
1607.3167 | 378.7257 | 217.5567 | 381.2973 | 415.7037 | 356.5168 | 300.3377 | 347.179 | 263.4272
1608.3167 | 380.0093 | 217.7105 | 380.6021 | 416.2097 | 356.7375 | 300.4839 | 347.4077 | 263.5797
1609.3167 | 379.3982 | 217.9141 | 380.0616 | 415.6525 | 356.6514 | 300.5707 | 347.6414 | 263.6806
1610.3167 | 379.9626 | 218.1324 | 380.2684 | 415.401 | 356.1792 | 300.7284 | 347.8842 | 263.8057
1611.3167 | 378.0574 | 218.3416 | 379.7864 | 415.5959 | 355.595 | 300.8434 | 348.1064 | 263.9515
1612.3167 | 379.0993 | 218.5501 | 380.0723 | 414.651 | 354.8807 | 301.0406 | 348.3535 | 264.0552
1613.3167 | 378.6215 | 218.7393 | 379.5819 | 413.7942 | 354.3426 | 301.1628 | 348.5955 | 264.1636
1614.3167 | 378.433 | 218.9179 | 379.5748 | 412.656 | 353.5924 | 301.3731 | 348.8239 | 264.257
1615.3167 | 377.896 | 219.1386 | 379.4274 | 412.1586 | 353.1551 | 301.5878 | 349.071 | 264.2786
1616.3167 | 378.5583 | 219.354 | 379.412 | 412.1156 | 352.9053 | 301.7473 | 349.3136 | 264.4183
1617.3167 | 377.9273 | 219.5645 | 378.6372 | 411.4953 | 352.3511 | 301.8998 | 349.5651 | 264.5214
1618.3167 | 380.3914 | 219.7681 | 378.1635 | 411.3126 | 351.7875 | 302.0615 | 349.8235 | 264.5778
1619.3167 | 379.1704 | 219.9433 | 378.5101 | 411.0699 | 351.3215 | 302.174 | 350.1001 | 264.7033
1620.3167 | 380.0676 | 220.0999 | 377.8071 | 411.105 | 351.4908 | 302.2779 | 350.3937 | 264.7644
1621.3167 | 379.3534 | 220.3202 | 378.0227 | 411.0957 | 350.9343 | 302.4589 | 350.6633 | 264.8771
1622.3167 | 380.7857 | 220.531 | 378.8159 | 412.4923 | 350.4344 | 302.5211 | 350.9297 | 264.9917
1623.3167 | 383.7487 | 220.7387 | 379.139 | 414.6788 | 351.0197 | 302.6986 | 351.185 | 265.1157
1624.3167 | 383.6593 | 220.945 | 378.0284 | 414.7504 | 351.5476 | 302.7883 | 351.44 | 265.2037
1625.3167 | 385.1223 | 221.1167 | 377.6022 | 414.4367 | 351.1657 | 302.9202 | 351.6834 | 265.3512
1626.3167 | 381.8038 | 221.3112 | 377.2369 | 414.7964 | 352.27 | 303.0494 | 351.9339 | 265.5493
1627.3167 | 382.2228 | 221.506 | 377.6504 | 414.9357 | 353.7692 | 303.1206 | 352.1834 | 265.6855
1628.3167 | 380.726 | 221.6864 | 378.4171 | 415.414 | 354.4484 | 303.1993 | 352.4343 | 265.8055
1629.3167 | 379.6325 | 221.8861 | 379.6412 | 416.3511 | 354.6116 | 303.3594 | 352.7169 | 265.8803
1630.3167 | 381.3779 | 222.0608 | 379.0807 | 416.3646 | 355.3753 | 303.4089 | 352.9874 | 266.0585
1631.3167 | 381.1359 | 222.275 | 379.1221 | 416.3873 | 355.8339 | 303.4523 | 353.2756 | 266.1214
1632.3167 | 380.3725 | 222.4757 | 379.4451 | 416.7956 | 356.1412 | 303.6257 | 353.5825 | 266.2924
1633.3167 | 380.2087 | 222.6701 | 379.2271 | 416.1737 | 355.4795 | 303.6914 | 353.8961 | 266.3775
1634.3167 | 379.0552 | 222.8714 | 379.965 | 415.9058 | 354.3374 | 303.8424 | 354.2207 | 266.4653
1635.3167 | 381.7259 | 223.0645 | 381.2257 | 415.3243 | 354.616 | 303.9361 | 354.5715 | 266.6698
1636.3167 | 379.9245 | 223.2553 | 382.2531 | 415.3642 | 355.3207 | 304.0901 | 354.8984 | 266.6705
1637.3167 | 381.1297 | 223.4004 | 383.0169 | 415.801 | 355.8745 | 304.1742 | 355.2433 | 266.741
1638.3167 | 380.1794 | 223.6017 | 382.3147 | 414.5066 | 355.9065 | 304.3352 | 355.6145 | 266.9614
1639.3167 | 379.1113 | 223.7709 | 380.9108 | 412.47 | 354.9567 | 304.5034 | 355.9921 | 267.0518
1640.3167 | 379.5633 | 223.9615 | 378.5979 | 410.6555 | 354.1658 | 304.576 | 356.3885 | 267.1662
1641.3167 | 378.3787 | 224.1078 | 377.5578 | 409.2125 | 353.0019 | 304.7462 | 356.8193 | 267.2637
1642.3167 | 377.2699 | 224.297 | 377.2893 | 408.4274 | 352.3111 | 304.9381 | 357.2484 | 267.3856
1643.3167 | 375.8772 | 224.4681 | 376.7828 | 407.5912 | 351.8355 | 305.0343 | 357.698 | 267.4804
1644.3167 | 376.2806 | 224.6677 | 376.3609 | 406.7242 | 351.8113 | 305.1921 | 358.1517 | 267.6196
1645.3167 | 376.9917 | 224.8237 | 375.6915 | 406.2384 | 351.3593 | 305.3921 | 358.6538 | 267.7357
1646.3167 | 375.5291 | 225.0109 | 375.2456 | 405.2602 | 350.5102 | 305.4452 | 359.1404 | 267.8724
1647.3167 | 374.3706 | 225.1648 | 374.5933 | 403.9856 | 349.3302 | 305.6603 | 359.6586 | 267.9766
1648.3167 | 373.1924 | 225.354 | 373.5002 | 402.082 | 347.7632 | 305.7993 | 360.1326 | 268.0606
1649.3167 | 372.8727 | 225.5102 | 372.0899 | 400.3341 | 346.4121 | 305.9484 | 360.6261 | 268.1483
1650.3167 | 371.8692 | 225.7195 | 370.7051 | 400.1498 | 346.5405 | 305.979 | 361.1126 | 268.2481
1651.3167 | 371.9885 | 225.9068 | 369.9607 | 399.103 | 346.0636 | 306.195 | 361.6418 | 268.3635
1652.3167 | 370.634 | 226.0295 | 369.8008 | 397.9222 | 345.2667 | 306.2803 | 362.2065 | 268.4483
1653.3167 | 370.9737 | 226.1872 | 369.2962 | 397.3547 | 344.3641 | 306.4966 | 362.7723 | 268.5059
1654.3167 | 370.1335 | 226.3687 | 370.1722 | 397.239 | 344.1744 | 306.5784 | 363.3434 | 268.671
1655.3167 | 368.9975 | 226.5581 | 369.6612 | 396.0569 | 343.1193 | 306.7263 | 363.9472 | 268.7815
1656.3167 | 368.4523 | 226.732 | 368.7406 | 395.5165 | 342.1737 | 306.7529 | 364.5535 | 268.8983
1657.3167 | 366.8138 | 226.8927 | 369.0472 | 394.6695 | 341.1556 | 306.8394 | 365.1854 | 268.9658
1658.3167 | 365.871 | 227.0742 | 368.7905 | 394.1859 | 340.5483 | 306.9395 | 365.8079 | 269.1076
1659.3167 | 365.7198 | 227.2486 | 369.6642 | 394.2238 | 340.8488 | 307.105 | 366.4603 | 269.2045
1660.3167 | 364.5229 | 227.3981 | 368.8764 | 394.0479 | 341.7132 | 307.2877 | 367.1092 | 269.3254
1661.3167 | 365.0865 | 227.5819 | 369.1244 | 394.8222 | 342.7905 | 307.2846 | 367.772 | 269.4193
1662.3167 | 368.456 | 227.7216 | 370.4812 | 396.0365 | 344.5455 | 307.3623 | 368.4505 | 269.5332
1663.3167 | 368.3618 | 227.9112 | 370.4021 | 395.8819 | 344.8488 | 307.5104 | 369.1338 | 269.6086
1664.3167 | 368.3328 | 228.0546 | 370.0486 | 395.5571 | 344.4759 | 307.5437 | 369.7987 | 269.7396
1665.3167 | 367.6179 | 228.2228 | 368.9008 | 394.6603 | 343.9505 | 307.7032 | 370.4836 | 269.9883
1666.3167 | 367.7055 | 228.3532 | 369.0819 | 394.4104 | 343.4659 | 307.8132 | 371.1305 | 270.0236
1667.3167 | 366.7531 | 228.5198 | 368.0531 | 393.9819 | 343.4819 | 307.9431 | 371.8293 | 270.1465
1668.3167 | 367.9384 | 228.7115 | 368.8948 | 394.7599 | 343.4857 | 308.0592 | 372.5355 | 270.2776
1669.3167 | 367.6573 | 228.8543 | 369.3257 | 395.943 | 343.8898 | 308.0302 | 373.2638 | 270.362
1670.3167 | 368.0847 | 229.0515 | 371.6285 | 397.4222 | 343.5762 | 308.25 | 373.9789 | 270.4247
1671.3167 | 369.2026 | 229.1639 | 372.8932 | 397.5645 | 344.4358 | 308.1032 | 374.6975 | 270.5289
1672.3167 | 369.8652 | 229.37 | 373.8991 | 398.4862 | 345.3397 | 308.3325 | 375.4067 | 270.6443
1673.3167 | 370.0871 | 229.5494 | 375.0866 | 399.3343 | 346.4765 | 308.6221 | 376.1356 | 270.7189
1674.3167 | 370.4206 | 229.6952 | 375.4462 | 400.3053 | 346.9959 | 308.7606 | 376.8675 | 270.8172
1675.3167 | 371.1766 | 229.8632 | 375.6014 | 400.9889 | 346.5215 | 309.0623 | 377.5259 | 270.9885
1676.3167 | 371.6867 | 230.0058 | 376.273 | 400.9882 | 346.2728 | 309.1307 | 378.2232 | 271.0894
1677.3167 | 374.1634 | 230.1949 | 375.2873 | 401.1398 | 346.0594 | 309.1017 | 378.9485 | 271.2893
1678.3167 | 376.5217 | 230.3324 | 374.8256 | 401.8364 | 345.7664 | 309.2046 | 379.6566 | 271.3922
1679.3167 | 377.9289 | 230.499 | 375.3384 | 403.3908 | 345.4962 | 309.6465 | 380.387 | 271.4861
1680.3167 | 379.3579 | 230.6419 | 376.0106 | 405.2878 | 347.4088 | 309.7982 | 381.102 | 271.5359
1681.3167 | 379.5372 | 230.8025 | 377.1473 | 406.9152 | 348.7763 | 309.757 | 381.8706 | 271.6643
1682.3167 | 380.1751 | 230.932 | 377.2255 | 407.9307 | 349.8632 | 310.033 | 382.6286 | 271.7052
1683.3167 | 381.7449 | 231.0842 | 377.3033 | 409.9043 | 350.4493 | 310.1729 | 383.37 | 271.7696
1684.3167 | 380.8304 | 231.2106 | 378.8635 | 411.9473 | 351.4281 | 310.2243 | 384.0125 | 271.9162
1685.3167 | 381.7431 | 231.3683 | 379.0857 | 413.9954 | 352.833 | 309.9447 | 384.6982 | 272.0771
1686.3167 | 384.4508 | 231.5317 | 380.5329 | 414.7679 | 352.8938 | 310.2653 | 385.3639 | 272.1247
1687.3167 | 385.7627 | 231.6821 | 380.5225 | 415.4612 | 353.1981 | 310.3526 | 386.0099 | 272.3072
1688.3167 | 384.9035 | 231.8258 | 382.0129 | 417.3292 | 353.8844 | 310.5155 | 386.6674 | 272.4268
1689.3167 | 384.8806 | 231.9804 | 382.4057 | 418.7557 | 353.2982 | 310.6479 | 387.2774 | 272.5063
1690.3167 | 386.3543 | 232.1263 | 384.9164 | 420.0463 | 353.6299 | 310.8379 | 387.85 | 272.679
1691.3167 | 387.4001 | 232.3223 | 385.248 | 419.9863 | 353.2281 | 311.0729 | 388.4028 | 272.8723
1692.3167 | 387.4677 | 232.4956 | 385.355 | 419.6554 | 353.2792 | 311.1861 | 388.947 | 272.9612
1693.3167 | 387.6293 | 232.5867 | 387.0895 | 420.259 | 353.569 | 311.3593 | 389.4639 | 273.1407
1694.3167 | 387.7589 | 232.7361 | 387.4 | 419.5569 | 354.5109 | 311.4539 | 389.9845 | 273.1755
1695.3167 | 388.3748 | 232.8412 | 386.4366 | 419.2116 | 354.5484 | 311.9294 | 390.4701 | 273.3084
1696.3167 | 387.9227 | 232.9746 | 385.149 | 417.1234 | 353.9737 | 311.5125 | 390.9087 | 273.4214
1697.3167 | 388.768 | 233.1124 | 383.1056 | 415.8449 | 353.8383 | 311.8203 | 391.339 | 273.4968
1698.3167 | 391.6834 | 233.2591 | 382.7463 | 414.7575 | 354.0824 | 311.8282 | 391.7679 | 273.6759
1699.3167 | 390.1845 | 233.3834 | 381.5497 | 412.7594 | 353.7657 | 312.1002 | 392.1421 | 273.7555
1700.3167 | 387.8865 | 233.5317 | 379.9188 | 410.7362 | 353.0568 | 312.5842 | 392.5247 | 273.8493
1701.3167 | 386.4146 | 233.6714 | 379.5034 | 410.1194 | 352.0754 | 312.6428 | 392.8889 | 273.961
1702.3167 | 383.9801 | 233.7786 | 381.8656 | 410.0826 | 351.9188 | 312.4934 | 393.2515 | 274.0471
1703.3167 | 383.2943 | 233.9578 | 381.4323 | 409.3034 | 352.3068 | 312.6502 | 393.5707 | 274.1031
1704.3167 | 384.4253 | 234.0684 | 380.4013 | 408.4232 | 353.1044 | 312.8113 | 393.8885 | 274.0633
1705.3167 | 384.6318 | 234.1985 | 378.6863 | 406.9876 | 352.7501 | 312.8156 | 394.2012 | 274.2012
1706.3167 | 385.6441 | 234.3069 | 376.6303 | 405.9263 | 352.1848 | 313.0149 | 394.486 | 274.3019
1707.3167 | 382.9804 | 234.467 | 375.5848 | 404.914 | 351.6128 | 313.0888 | 394.7597 | 274.4979
1708.3167 | 382.274 | 234.6192 | 375.082 | 404.1485 | 350.6504 | 313.168 | 395.0181 | 274.6277
1709.3167 | 382.6137 | 234.7446 | 374.3113 | 403.3095 | 349.9726 | 313.1908 | 395.273 | 274.7426
1710.3167 | 380.5864 | 234.8608 | 372.8211 | 401.8281 | 349.52 | 313.3399 | 395.5052 | 274.8686
1711.3167 | 378.348 | 235.0312 | 371.7715 | 399.8306 | 347.9638 | 313.4286 | 395.7065 | 274.9638
1712.3167 | 377.2085 | 235.1995 | 371.5617 | 398.3958 | 346.9032 | 313.747 | 395.9034 | 275.0774
1713.3167 | 375.3225 | 235.3496 | 371.0953 | 397.291 | 346.1593 | 313.7943 | 396.1134 | 275.1819
1714.3167 | 374.8642 | 235.5048 | 372.1936 | 396.9497 | 345.8091 | 313.8686 | 396.2909 | 275.2744
1715.3167 | 374.622 | 235.587 | 373.5974 | 396.2214 | 345.4043 | 313.9479 | 396.4698 | 275.4208
1716.3167 | 372.8716 | 235.7501 | 373.5167 | 396.0604 | 344.8659 | 314.1212 | 396.6674 | 275.6624
1717.3167 | 373.6366 | 235.8847 | 372.6438 | 395.2797 | 344.5546 | 314.2205 | 396.8329 | 275.7268
1718.3167 | 374.6488 | 236.0323 | 371.615 | 395.4545 | 344.6008 | 314.2917 | 397.0083 | 275.8186
1719.3167 | 376.8727 | 236.1708 | 371.5737 | 395.0983 | 345.1229 | 314.5182 | 397.1801 | 275.918
1720.3167 | 377.506 | 236.3312 | 372.5164 | 395.4521 | 345.248 | 314.4733 | 397.3485 | 276.0355
1721.3167 | 379.058 | 236.4758 | 373.6682 | 396.4152 | 345.8366 | 314.6613 | 397.5335 | 276.1323
1722.3167 | 378.6428 | 236.6263 | 373.399 | 397.2305 | 346.9989 | 314.7878 | 397.707 | 276.2386
1723.3167 | 378.7399 | 236.7601 | 374.2282 | 397.714 | 347.5013 | 314.684 | 397.8908 | 276.3883
1724.3167 | 380.6936 | 236.8994 | 376.8175 | 398.8894 | 348.2201 | 314.9887 | 398.0584 | 276.4799
1725.3167 | 379.9485 | 237.0272 | 379.5484 | 400.0837 | 348.9138 | 315.3003 | 398.202 | 276.5757
1726.3167 | 378.9327 | 237.1446 | 382.74 | 402.1837 | 349.6733 | 315.3931 | 398.3718 | 276.6912
1727.3167 | 378.8333 | 237.2636 | 383.8522 | 402.0521 | 350.0281 | 315.6118 | 398.5371 | 276.7974
1728.3167 | 379.0479 | 237.3776 | 385.7031 | 402.3747 | 350.482 | 315.851 | 398.6652 | 276.9079
1729.3167 | 378.9918 | 237.5006 | 386.9692 | 402.9033 | 351.3256 | 316.0757 | 398.8262 | 277.0468
1730.3167 | 380.2512 | 237.6154 | 387.4321 | 403.5034 | 351.4442 | 316.3701 | 398.9831 | 277.1333
1731.3167 | 381.8396 | 237.7432 | 391.2538 | 406.2299 | 353.8417 | 316.4808 | 399.1316 | 277.2104
1732.3167 | 383.2478 | 237.8604 | 393.0245 | 409.0097 | 354.4452 | 316.6155 | 399.2911 | 277.3262
1733.3167 | 385.6993 | 237.9841 | 394.6498 | 411.2701 | 354.697 | 317.0533 | 399.4314 | 277.4521
1734.3167 | 386.9176 | 238.1251 | 396.0759 | 413.6199 | 354.8016 | 317.2285 | 399.5678 | 277.5455
1735.3167 | 391.5624 | 238.2509 | 397.3736 | 415.5222 | 355.1776 | 317.2892 | 399.725 | 277.6645
1736.3167 | 392.9536 | 238.3828 | 398.9961 | 418.3978 | 357.8822 | 317.6843 | 399.9171 | 277.7943
1737.3167 | 395.2824 | 238.5178 | 401.4097 | 421.0027 | 358.6799 | 317.7296 | 400.0678 | 277.9073
1738.3167 | 396.8074 | 238.6411 | 402.2749 | 422.0708 | 358.7138 | 318.1095 | 400.2113 | 278.0085
1739.3167 | 398.0473 | 238.7839 | 403.9923 | 423.2877 | 358.7052 | 318.33 | 400.3512 | 278.1184
1740.3167 | 397.1876 | 238.9055 | 405.1959 | 424.6645 | 358.8614 | 318.77 | 400.4856 | 278.2098
1741.3167 | 397.6296 | 239.0213 | 405.8172 | 426.3959 | 360.3408 | 318.9954 | 400.6299 | 278.3729
1742.3167 | 399.6775 | 239.1422 | 407.2569 | 428.7586 | 363.6325 | 319.3839 | 400.7822 | 278.4745
1743.3167 | 402.897 | 239.2406 | 407.5317 | 430.0801 | 366.1629 | 319.6041 | 400.9042 | 278.5704
1744.3167 | 405.3465 | 239.3389 | 407.0092 | 430.1016 | 367.5788 | 319.819 | 401.0449 | 278.688
1745.3167 | 405.2415 | 239.455 | 404.6468 | 429.7588 | 368.0678 | 320.2707 | 401.1687 | 278.7976
1746.3167 | 407.6911 | 239.5698 | 403.7192 | 429.7018 | 368.5408 | 320.3223 | 401.2995 | 278.8865
1747.3167 | 408.8501 | 239.6815 | 403.3043 | 430.6005 | 369.9464 | 320.2949 | 401.4383 | 278.9996
1748.3167 | 407.781 | 239.7954 | 403.4064 | 432.4743 | 372.2218 | 320.3334 | 401.5668 | 279.168
1749.3167 | 408.7044 | 239.9034 | 404.2421 | 434.6074 | 374.2808 | 320.6954 | 401.7113 | 279.2658
1750.3167 | 407.4569 | 240.0148 | 405.7712 | 435.7261 | 375.3842 | 320.7128 | 401.8062 | 279.377
1751.3167 | 408.9446 | 240.1246 | 405.887 | 437.5282 | 375.8233 | 321.0716 | 401.9287 | 279.4653
1752.3167 | 408.9099 | 240.1846 | 405.4063 | 436.8463 | 375.3832 | 321.3581 | 402.0693 | 279.5833
1753.3167 | 410.446 | 240.3027 | 404.8645 | 437.3163 | 375.7445 | 321.4039 | 402.1917 | 279.7024
1754.3167 | 409.7111 | 240.3777 | 404.2274 | 436.677 | 375.7038 | 321.3928 | 402.3326 | 279.7987
1755.3167 | 408.6146 | 240.4811 | 403.4037 | 435.1611 | 375.0081 | 321.7784 | 402.4618 | 279.92
1756.3167 | 410.0562 | 240.5849 | 402.5466 | 434.5239 | 374.387 | 321.8097 | 402.5729 | 280.0302
1757.3167 | 408.967 | 240.6723 | 401.9291 | 434.0524 | 372.8305 | 322.0549 | 402.6982 | 280.1415
1758.3167 | 407.0163 | 240.79 | 405.2332 | 434.5775 | 371.5097 | 322.3006 | 402.8037 | 280.2445
1759.3167 | 406.4126 | 240.8841 | 407.8452 | 436.3256 | 371.5049 | 322.5661 | 402.9237 | 280.3552
1760.3167 | 406.7414 | 240.9788 | 410.1526 | 438.3877 | 372.3613 | 322.9447 | 403.0374 | 280.4783
1761.3167 | 407.6606 | 241.099 | 410.7411 | 438.2929 | 373.2372 | 323.1065 | 403.1528 | 280.5942
1762.3167 | 409.4797 | 241.2036 | 410.6 | 438.2951 | 374.2556 | 323.2678 | 403.2591 | 280.706
1763.3167 | 407.2332 | 241.3105 | 411.5124 | 440.3881 | 374.9255 | 323.5675 | 403.3801 | 280.8193
1764.3167 | 408.2126 | 241.4329 | 414.7776 | 442.1497 | 374.7311 | 323.8103 | 403.5041 | 280.939
1765.3167 | 409.9953 | 241.5441 | 414.764 | 443.3388 | 375.1259 | 324.2843 | 403.6245 | 281.0529
1766.3167 | 411.4567 | 241.6348 | 415.5306 | 444.1788 | 375.6056 | 324.0493 | 403.7482 | 281.1574
1767.3167 | 414.208 | 241.7602 | 415.6394 | 444.9873 | 376.5268 | 324.8362 | 403.8474 | 281.2664
1768.3167 | 415.9072 | 241.8675 | 417.682 | 446.1735 | 377.9096 | 324.6578 | 403.9748 | 281.3861
1769.3167 | 418.9392 | 241.9619 | 418.0317 | 445.9326 | 379.1534 | 324.8829 | 404.0976 | 281.5018
1770.3167 | 419.5277 | 242.0497 | 419.986 | 446.3597 | 378.8583 | 325.1897 | 404.1952 | 281.6083
1771.3167 | 416.8487 | 242.1197 | 419.9565 | 446.4085 | 378.1515 | 325.3811 | 404.306 | 281.7394
1772.3167 | 415.8985 | 242.2093 | 420.3857 | 446.5093 | 377.3842 | 325.8934 | 404.4026 | 281.8547
1773.3167 | 420.5253 | 242.3422 | 424.1402 | 449.242 | 379.4862 | 326.3645 | 404.515 | 281.9765
1774.3167 | 423.5993 | 242.4532 | 425.7409 | 451.3621 | 379.6017 | 326.3854 | 404.659 | 282.0924
1775.3167 | 424.2148 | 242.5684 | 426.1617 | 453.1645 | 379.697 | 327.1701 | 404.7905 | 282.1923
1776.3167 | 423.1698 | 242.6909 | 426.6528 | 452.8613 | 379.3321 | 327.3545 | 404.893 | 282.3115
1777.3167 | 424.7663 | 242.8007 | 425.4779 | 453.2711 | 379.2157 | 327.9704 | 405.0145 | 282.4171
1778.3167 | 425.4594 | 242.9051 | 427.1752 | 454.0933 | 380.4217 | 328.2168 | 405.1216 | 282.5415
1779.3167 | 423.8065 | 243.0144 | 426.5385 | 453.1665 | 380.2271 | 328.4526 | 405.2552 | 282.6575
1780.3167 | 419.6922 | 243.1224 | 425.8846 | 453.9837 | 380.387 | 328.7355 | 405.3786 | 282.7719
1781.3167 | 423.6074 | 243.2351 | 426.8254 | 455.0867 | 382.3306 | 329.0145 | 405.4839 | 282.8715
1782.3167 | 421.398 | 243.3435 | 427.1892 | 455.6713 | 383.0683 | 329.2763 | 405.6208 | 282.993
1783.3167 | 421.4707 | 243.4566 | 429.6782 | 456.2865 | 383.8919 | 329.5557 | 405.7458 | 283.1136
1784.3167 | 423.9776 | 243.5578 | 429.3742 | 456.671 | 385.313 | 329.8351 | 405.8613 | 283.2479
1785.3167 | 427.2864 | 243.6657 | 430.011 | 457.912 | 388.0626 | 330.1174 | 405.981 | 283.3388
1786.3167 | 429.6756 | 243.7681 | 429.658 | 459.7486 | 388.6815 | 330.3517 | 406.1118 | 283.4642
1787.3167 | 428.3398 | 243.8684 | 427.8318 | 459.712 | 389.1712 | 330.4499 | 406.2279 | 283.5896
1788.3167 | 433.4885 | 243.9673 | 429.3654 | 461.7737 | 390.4258 | 330.583 | 406.3516 | 283.6918
1789.3167 | 439.0693 | 244.072 | 429.1077 | 460.8885 | 390.2985 | 330.715 | 406.4834 | 283.7999
1790.3167 | 436.4127 | 244.1793 | 429.2811 | 459.5314 | 389.8036 | 331.032 | 406.6011 | 283.9198
1791.3167 | 442.9224 | 244.2196 | 427.0746 | 457.8623 | 388.8677 | 331.2441 | 406.7487 | 284.0388
1792.3167 | 440.2004 | 244.3059 | 424.367 | 455.3288 | 387.833 | 331.6354 | 406.8675 | 284.1439
1793.3167 | 437.417 | 244.4198 | 420.9787 | 452.2052 | 386.522 | 331.7983 | 407.0075 | 284.2698
1794.3167 | 433.589 | 244.5281 | 419.3956 | 450.0605 | 384.8671 | 331.9218 | 407.1432 | 284.3598
1795.3167 | 437.3192 | 244.6221 | 418.0576 | 448.7266 | 383.7599 | 331.8947 | 407.2757 | 284.4766
1796.3167 | 430.5668 | 244.7267 | 417.6994 | 446.8141 | 382.2216 | 332.1168 | 407.4162 | 284.6135
1797.3167 | 433.1507 | 244.759 | 416.653 | 444.7355 | 380.6974 | 332.5326 | 407.5583 | 284.7183
1798.3167 | 427.4845 | 244.8759 | 415.3066 | 443.5516 | 378.9375 | 332.5642 | 407.6957 | 284.834
1799.3167 | 425.5425 | 244.9916 | 419.5199 | 445.3138 | 378.8392 | 333.1121 | 407.8342 | 285.0295
1800.3167 | 427.0459 | 245.1042 | 420.5507 | 444.9105 | 379.3914 | 333.4358 | 407.974 | 285.1444
1801.3167 | 425.4011 | 245.2105 | 421.5902 | 445.7114 | 379.7744 | 333.5868 | 408.1207 | 285.2674
1802.3167 | 423.4628 | 245.3237 | 421.7086 | 445.3923 | 380.1163 | 333.8324 | 408.2596 | 285.3929
1803.3167 | 421.8779 | 245.4317 | 419.7479 | 443.795 | 379.0776 | 334.0746 | 408.4093 | 285.5111
1804.3167 | 423.7617 | 245.537 | 419.1742 | 444.1872 | 378.0655 | 334.0952 | 408.5677 | 285.6041
1805.3167 | 430.1881 | 245.6317 | 421.5592 | 445.462 | 379.157 | 334.3818 | 408.7129 | 285.7562
1806.3167 | 427.1778 | 245.7481 | 421.2257 | 446.6388 | 379.9262 | 334.5143 | 408.8724 | 286.0164
1807.3167 | 429.0504 | 245.8979 | 421.1338 | 447.1419 | 380.4986 | 335.1578 | 409.0257 | 286.107
1808.3167 | 428.6953 | 246.0751 | 421.9218 | 450.012 | 380.8184 | 335.4059 | 409.1844 | 286.1789
1809.3167 | 432.14 | 246.2107 | 424.6311 | 456.2241 | 382.9366 | 335.2138 | 409.3358 | 286.3045
1810.3167 | 431.746 | 246.2427 | 424.9163 | 457.4532 | 384.3375 | 335.5523 | 409.4923 | 286.5232
1811.3167 | 431.4567 | 246.2804 | 425.3421 | 457.7329 | 385.1262 | 335.9886 | 409.6572 | 286.6137
1812.3167 | 429.8031 | 246.2427 | 427.568 | 458.4597 | 386.5559 | 336.111 | 409.8147 | 286.7326
1813.3167 | 430.4689 | 246.1655 | 429.9637 | 459.1627 | 387.2624 | 336.6432 | 409.9692 | 286.8284
1814.3167 | 429.3931 | 246.23 | 432.1786 | 460.2744 | 387.9668 | 337.0317 | 410.1447 | 286.938
1815.3167 | 429.0772 | 246.3156 | 432.4388 | 459.5712 | 387.8809 | 337.4496 | 410.2842 | 287.0408
1816.3167 | 426.7423 | 246.5116 | 431.784 | 459.5158 | 387.3233 | 337.5652 | 410.4465 | 287.1638
1817.3167 | 427.3727 | 246.6595 | 432.2963 | 459.3799 | 386.1573 | 337.6017 | 410.6 | 287.3202
1818.3167 | 428.1009 | 246.8056 | 433.9101 | 459.5989 | 385.8063 | 338.5456 | 410.7587 | 287.4249
1819.3167 | 429.595 | 246.9275 | 436.9629 | 459.4038 | 385.1967 | 338.7324 | 410.9208 | 287.5356
1820.3167 | 426.3131 | 247.045 | 437.22 | 471.8568 | 383.7331 | 339.0993 | 411.0956 | 287.6673
1821.3167 | 426.9327 | 247.1509 | 437.1847 | 493.5206 | 382.1022 | 339.4211 | 411.2522 | 287.7761
1822.3167 | 426.6155 | 247.2608 | 437.4072 | 491.0053 | 383.2607 | 339.6482 | 411.4067 | 287.9106
1823.3167 | 426.598 | 247.3693 | 438.0552 | 492.2079 | 386.1117 | 340.1585 | 411.5737 | 288.0007
1824.3167 | 430.0262 | 247.2126 | 438.7356 | 492.2591 | 386.6825 | 340.5381 | 411.7262 | 288.1132
1825.3167 | 430.4791 | 247.1075 | 440.5522 | 492.3024 | 386.723 | 340.7102 | 411.9018 | 288.2158
1826.3167 | 434.381 | 247.0605 | 441.9317 | 492.4804 | 385.8092 | 340.9631 | 412.0654 | 288.3403
1827.3167 | 436.5979 | 247.0725 | 443.5303 | 490.4635 | 385.075 | 341.3144 | 412.2291 | 288.4532
1828.3167 | 435.6445 | 247.0377 | 443.8581 | 490.2892 | 384.9751 | 341.6556 | 412.3996 | 288.5747
1829.3167 | 435.1498 | 246.9489 | 445.25 | 490.0575 | 384.932 | 342.2042 | 412.5533 | 288.6931
1830.3167 | 434.5695 | 246.8465 | 446.1075 | 490.5212 | 384.7189 | 342.6208 | 412.7403 | 288.8139
1831.3167 | 433.6388 | 246.8289 | 449.0766 | 491.8536 | 385.3455 | 342.9663 | 412.896 | 288.9448
1832.3167 | 436.7288 | 246.8995 | 448.4361 | 490.2878 | 385.011 | 342.9471 | 413.0688 | 289.075
1833.3167 | 437.1889 | 246.9172 | 449.76 | 493.3199 | 387.0567 | 343.4322 | 413.2298 | 289.1899
1834.3167 | 438.1921 | 247.1022 | 450.3438 | 493.2694 | 390.3423 | 344.03 | 413.4044 | 289.332
1835.3167 | 439.329 | 247.2689 | 449.7481 | 492.2376 | 391.242 | 344.3304 | 413.5712 | 289.4919
1836.3167 | 447.1168 | 247.3843 | 447.9652 | 492.1606 | 391.6887 | 344.8156 | 413.7412 | 289.6231
1837.3167 | 441.7167 | 247.4392 | 444.7756 | 489.5472 | 390.4736 | 345.1144 | 413.9245 | 289.741
1838.3167 | 447.1254 | 247.4139 | 444.5121 | 489.245 | 391.8955 | 345.5965 | 414.0807 | 289.8586
1839.3167 | 443.9554 | 247.5205 | 447.5418 | 490.1202 | 394.1009 | 345.9974 | 414.2657 | 290.0116
1840.3167 | 447.611 | 247.6097 | 448.1596 | 490.4173 | 395.3263 | 346.0687 | 414.4162 | 290.1633
1841.3167 | 445.7012 | 247.7007 | 447.3253 | 490.5192 | 394.9902 | 346.6208 | 414.5878 | 290.283
1842.3167 | 450.9343 | 247.7832 | 444.9443 | 490.439 | 395.8484 | 346.6968 | 414.772 | 290.3867
1843.3167 | 456.2236 | 247.8593 | 443.0442 | 490.7017 | 396.7639 | 347.2098 | 414.9329 | 290.5276
1844.3167 | 453.5837 | 247.9449 | 443.5063 | 490.2971 | 396.8915 | 347.6727 | 415.1191 | 290.6335
1845.3167 | 459.0508 | 247.9348 | 442.769 | 490.361 | 397.99 | 347.8166 | 415.2921 | 290.7615
1848.4729 | 453.7509 | 248.0228 | 443.0048 | 488.6717 | 401.5932 | 349.3151 | 415.8397 | 291.1824
1849.3167 | 457.6097 | 248.0751 | 444.9591 | 490.612 | 403.595 | 349.5464 | 415.9899 | 291.2996
1850.3167 | 465.585 | 248.0613 | 446.7946 | 490.893 | 403.1333 | 350.0813 | 416.1494 | 291.4231
1851.3167 | 465.4421 | 248.1604 | 446.7864 | 489.9225 | 401.9441 | 350.4966 | 416.3405 | 291.5653
1854.4729 | 468.3191 | 248.3564 | 452.1613 | 495.053 | 405.854 | 351.8316 | 416.9127 | 292.1624
1855.3167 | 469.4947 | 248.4052 | 455.0242 | 495.7212 | 406.989 | 352.3152 | 417.064 | 292.2652
1856.3167 | 466.7517 | 248.4613 | 455.4535 | 496.3432 | 406.3715 | 352.6916 | 417.2455 | 292.3819
1860.4885 | 471.4377 | 248.6539 | 455.4923 | 508.7249 | 405.3649 | 355.16 | 418.0475 | 292.8279
1861.3167 | 472.0334 | 248.6982 | 455.0313 | 508.3777 | 404.9229 | 355.4281 | 418.1975 | 292.9739
1862.3167 | 472.9418 | 248.7637 | 455.7648 | 508.2287 | 404.6496 | 355.6606 | 418.3914 | 293.1201
1863.3167 | 470.6066 | 248.8562 | 455.163 | 507.3485 | 404.2366 | 355.9576 | 418.6087 | 293.2153
1864.3167 | 475.1744 | 248.996 | 455.831 | 507.8919 | 405.7665 | 356.4296 | 418.7915 | 293.346
1865.3167 | 477.1024 | 249.0943 | 454.7973 | 507.6023 | 407.4819 | 356.7001 | 419.0012 | 293.5423
1869.4729 | 480.7523 | 249.5496 | 450.746 | 508.2267 | 410.554 | 359.0214 | 419.8693 | 294.0924
1870.3167 | 478.7257 | 249.642 | 451.2694 | 508.4007 | 412.0625 | 359.3386 | 420.032 | 294.2196
1871.3167 | 478.3718 | 249.7454 | 450.9448 | 508.4583 | 412.3116 | 359.7882 | 420.249 | 294.389
1872.3167 | 480.7374 | 249.8542 | 449.7658 | 509.9834 | 412.3483 | 360.1701 | 420.4728 | 294.5305
1873.3167 | 479.6378 | 249.9524 | 448.9616 | 509.5836 | 411.9494 | 360.8836 | 420.6747 | 294.6466
1874.3167 | 481.6459 | 250.0608 | 447.3394 | 537.4103 | 411.3087 | 361.2592 | 420.8886 | 294.8015
1875.3167 | 482.7783 | 250.16 | 447.0083 | 554.1903 | 410.58 | 361.9279 | 421.1019 | 294.923
1876.3167 | 483.0957 | 250.2736 | 446.497 | 559.4689 | 409.4266 | 362.2278 | 421.3222 | 295.0379
1877.3167 | 484.1337 | 250.356 | 447.7415 | 564.3653 | 409.5162 | 362.4074 | 421.5566 | 295.1815
1878.3167 | 484.1771 | 250.4056 | 449.679 | 578.8165 | 411.0979 | 362.6334 | 421.7827 | 295.3339
1879.3167 | 488.3013 | 250.529 | 447.5798 | 592.5585 | 412.6366 | 362.9752 | 422.0122 | 295.4847
1880.3167 | 493.9016 | 250.6321 | 446.6557 | 600.7326 | 415.262 | 363.4801 | 422.2474 | 295.595
1881.3167 | 497.1278 | 250.5934 | 448.408 | 591.5923 | 415.8665 | 364.1591 | 422.4924 | 295.7499
1882.3167 | 497.8393 | 250.6545 | 463.8292 | 586.6684 | 417.8833 | 364.51 | 422.7297 | 296.0271
1883.3167 | 499.6133 | 250.9289 | 465.411 | 577.6611 | 419.4963 | 365.0258 | 423.0061 | 296.1975
1884.3167 | 499.7773 | 251.1045 | 465.3373 | 570.8962 | 419.2038 | 365.2946 | 423.2382 | 296.3781
1885.3167 | 500.9532 | 251.2391 | 464.276 | 568.059 | 419.6079 | 365.6613 | 423.4858 | 296.4973
1889.4729 | 502.6166 | 251.7179 | 468.9343 | 621.6555 | 417.7221 | 367.4899 | 424.4874 | 297.2743
1890.3167 | 502.0104 | 251.8023 | 468.2149 | 629.4704 | 417.9216 | 367.8992 | 424.6935 | 297.3405
1891.3167 | 501.9289 | 251.9009 | 467.2243 | 616.9024 | 418.4618 | 368.4258 | 424.9373 | 297.4607
1895.4885 | 501.9805 | 252.2226 | 464.8056 | 582.9547 | 437.8781 | 369.4346 | 426.0796 | 298.1143
1896.3167 | 501.8303 | 252.1755 | 466.9913 | 578.4123 | 435.9314 | 369.6294 | 426.2971 | 298.2165
1897.3167 | 501.7633 | 252.1829 | 470.0136 | 573.2522 | 435.3745 | 370.0769 | 426.5555 | 298.3784
1898.3167 | 504.0003 | 252.3583 | 468.9469 | 568.0319 | 434.217 | 370.3652 | 426.8618 | 298.5729
1899.3167 | 505.7543 | 252.4688 | 467.1291 | 563.5046 | 433.3037 | 370.6669 | 427.1517 | 298.7432
1900.3167 | 507.4627 | 252.5909 | 467.1675 | 558.9776 | 432.2067 | 370.9329 | 427.474 | 298.8945
1901.3167 | 506.8256 | 252.4724 | 466.4433 | 555.5938 | 431.5474 | 371.2255 | 427.733 | 299.0397
1902.3167 | 507.5717 | 252.5176 | 468.4886 | 552.583 | 431.7313 | 371.5614 | 427.9961 | 299.2066
1903.3167 | 506.896 | 252.7762 | 467.8656 | 551.6114 | 432.6112 | 371.7834 | 428.2132 | 299.3485
1904.3167 | 507.7779 | 253.0287 | 467.4691 | 551.6527 | 431.9817 | 372.1382 | 428.4859 | 299.4609
1905.3167 | 508.2307 | 253.1602 | 468.7255 | 562.5735 | 430.5809 | 372.4605 | 428.741 | 299.6271
1906.3167 | 510.6083 | 253.2258 | 469.0727 | 584.0012 | 429.7747 | 373.0595 | 429.0301 | 299.7947
1907.3167 | 510.0338 | 253.5027 | 469.4294 | 595.716 | 428.7486 | 373.4948 | 429.3645 | 299.9558
1908.3167 | 507.5071 | 253.6401 | 471.7803 | 598.7251 | 427.1912 | 374.1783 | 429.6501 | 300.1019
1909.3167 | 508.1035 | 253.7589 | 469.7355 | 604.4585 | 426.2173 | 374.6258 | 430.8173 | 300.2628
1910.3167 | 507.8341 | 253.9064 | 470.5509 | 611.8222 | 425.3326 | 375.0771 | 431.1642 | 300.4595
1911.3167 | 507.491 | 254.0946 | 472.9551 | 622.1542 | 424.3354 | 375.4194 | 431.5481 | 300.641
1912.3167 | 506.4209 | 254.2457 | 473.4888 | 624.3062 | 423.7691 | 376.0415 | 431.8233 | 300.8712
1913.3167 | 505.2998 | 254.384 | 471.1843 | 625.5414 | 427.5537 | 376.5335 | 432.1743 | 301.0412
1914.3167 | 502.3302 | 254.4457 | 469.826 | 621.3264 | 428.3288 | 376.943 | 432.507 | 301.2142
1915.3167 | 499.0767 | 254.5697 | 468.8838 | 616.9878 | 426.9645 | 377.516 | 432.8061 | 301.4585
1916.3167 | 496.8536 | 254.6843 | 469.6155 | 616.4748 | 427.3313 | 379.1501 | 433.2409 | 301.7596
1917.3167 | 495.5051 | 254.8077 | 471.2586 | 616.9194 | 431.4405 | 382.3968 | 433.6761 | 301.8839
1918.3167 | 495.6316 | 254.9387 | 474.96 | 607.6114 | 437.2285 | 382.6825 | 434.0766 | 302.1636
1919.3167 | 496.6597 | 255.0917 | 474.1672 | 603.7041 | 440.7352 | 384.3882 | 434.6219 | 302.5394
1920.3167 | 497.1409 | 255.131 | 473.1792 | 601.2229 | 445.2731 | 384.3154 | 434.8194 | 302.5259
1921.3167 | 498.3591 | 255.2078 | 471.6755 | 601.6036 | 446.9511 | 384.306 | 435.0458 | 302.5921
1922.3167 | 498.721 | 255.2945 | 471.503 | 598.916 | 453.8504 | 384.7009 | 435.3372 | 302.7652
1923.3167 | 497.8047 | 255.3836 | 470.0504 | 609.8582 | 460.7362 | 384.9261 | 435.6256 | 302.9211
1924.3167 | 496.2773 | 255.5277 | 470.8151 | 605.7566 | 466.2127 | 385.1999 | 435.9351 | 303.0847
1925.3167 | 496.0231 | 255.6509 | 472.8656 | 600.6854 | 467.9126 | 385.6007 | 436.2322 | 303.3148
1926.3167 | 496.8564 | 255.749 | 471.3033 | 597.5568 | 473.0552 | 385.6727 | 436.5666 | 303.3951
1927.3167 | 496.2279 | 255.8507 | 470.0925 | 593.8595 | 470.3056 | 385.9025 | 436.8726 | 303.6536
1928.3167 | 494.7172 | 255.9528 | 467.1327 | 589.5583 | 468.26 | 386.919 | 437.1912 | 303.7988
1929.3167 | 492.3051 | 256.0623 | 469.8049 | 587.0623 | 468.5772 | 387.8271 | 437.5181 | 304.0089
1930.3167 | 490.6636 | 256.166 | 470.067 | 588.1746 | 468.9339 | 388.5652 | 437.8656 | 304.2267
1931.3167 | 489.8194 | 256.2763 | 471.5895 | 587.6098 | 468.3281 | 389.3152 | 438.2854 | 304.4675
1932.3167 | 489.4385 | 256.3889 | 473.3176 | 594.4564 | 469.2375 | 389.8366 | 438.7657 | 304.64
1933.3167 | 491.357 | 256.5164 | 473.5764 | 598.6405 | 482.2955 | 390.7785 | 439.4523 | 304.9389
1934.3167 | 493.1105 | 256.6052 | 473.5101 | 595.7993 | 502.2669 | 390.904 | 439.7592 | 305.0671
1935.3167 | 493.143 | 256.6971 | 472.6219 | 599.5541 | 513.1785 | 391.238 | 440.1475 | 305.2658
1936.3167 | 492.9608 | 256.8048 | 473.2944 | 602.6688 | 527.1966 | 391.5912 | 440.5384 | 305.6802
1937.3167 | 493.979 | 256.9026 | 471.1285 | 598.8948 | 536.2669 | 391.9026 | 440.7557 | 305.8371
1938.3167 | 496.4983 | 256.9964 | 469.5281 | 595.2515 | 536.0463 | 391.8882 | 440.7124 | 305.8966
1939.3167 | 497.2503 | 257.0855 | 468.3797 | 593.5413 | 532.4466 | 392.0726 | 440.7494 | 306.0528
1940.3167 | 497.3232 | 257.1925 | 467.1053 | 588.9447 | 528.4559 | 392.35 | 440.8735 | 306.2597
1941.3167 | 497.9187 | 257.2238 | 465.1412 | 582.1249 | 521.4634 | 392.481 | 441.0615 | 306.4675
1942.3167 | 498.0353 | 257.2862 | 466.1077 | 585.5201 | 514.2471 | 392.7597 | 441.2005 | 306.7593
1943.3167 | 499.2962 | 257.3762 | 470.1091 | 584.3514 | 508.6362 | 393.0606 | 441.3415 | 306.828
1944.3167 | 498.414 | 257.4731 | 470.0958 | 586.7087 | 502.3732 | 393.5819 | 441.4932 | 307.0242
1945.3167 | 500.3213 | 257.5647 | 472.7018 | 606.603 | 497.454 | 394.3214 | 441.6985 | 307.2162
1946.3167 | 513.2046 | 257.6874 | 474.4145 | 611.6208 | 494.4494 | 395.0203 | 441.9955 | 307.3925
1947.3167 | 523.3102 | 257.7646 | 475.0516 | 615.6236 | 490.6393 | 395.5733 | 442.2871 | 307.7181
1948.3167 | 522.0617 | 257.8582 | 475.9512 | 619.3254 | 489.1806 | 396.1162 | 442.5756 | 307.887
1949.3167 | 521.4975 | 257.932 | 478.7543 | 628.958 | 498.142 | 396.5535 | 442.9158 | 308.1532
1950.3167 | 521.7301 | 258.0352 | 482.9583 | 627.9743 | 497.424 | 397.0229 | 443.2746 | 308.3595
1951.3167 | 521.4457 | 258.1107 | 486.3023 | 637.4132 | 502.8887 | 397.2597 | 443.6287 | 308.5117
1952.3167 | 521.4452 | 258.2109 | 489.4185 | 634.7324 | 502.596 | 397.5402 | 443.915 | 308.7134
1953.3167 | 521.118 | 258.3254 | 489.6202 | 631.4109 | 499.5107 | 397.8651 | 444.2246 | 308.9144
1954.3167 | 521.4413 | 258.3778 | 488.9588 | 628.2409 | 498.0541 | 398.1249 | 444.5592 | 309.0917
1955.3167 | 521.1239 | 258.4811 | 490.466 | 622.6095 | 497.5778 | 398.4074 | 444.8889 | 309.2998
1956.3167 | 519.8767 | 258.5609 | 488.3095 | 613.7688 | 494.268 | 398.6852 | 445.239 | 309.4902
1957.3167 | 520.6874 | 258.5523 | 490.2856 | 606.2312 | 489.5705 | 398.9992 | 445.6136 | 309.7512
1958.3167 | 519.9242 | 258.6807 | 493.7237 | 622.2188 | 499.9049 | 399.4902 | 445.9306 | 309.9916
1959.3167 | 519.2262 | 258.7678 | 495.9753 | 624.4375 | 498.7789 | 399.9284 | 446.309 | 310.1477
1960.3167 | 520.9598 | 258.9485 | 498.9666 | 621.2719 | 503.8013 | 400.4451 | 446.7341 | 310.3509
1961.3167 | 521.4042 | 259.076 | 497.7132 | 615.9749 | 507.1986 | 400.873 | 447.1702 | 310.581
1962.3167 | 520.194 | 259.1817 | 497.5106 | 617.2836 | 521.5885 | 401.2903 | 447.6285 | 310.7568
1963.3167 | 521.798 | 259.2757 | 496.32 | 624.4391 | 531.654 | 401.7946 | 448.0626 | 310.9819
1964.3167 | 521.0214 | 259.382 | 499.1957 | 623.4755 | 534.1317 | 401.8438 | 448.4747 | 311.1714
1965.3167 | 521.8856 | 259.4906 | 495.5895 | 624.5291 | 536.9292 | 402.1545 | 448.9159 | 311.4283
1966.3167 | 521.951 | 259.576 | 493.1689 | 617.8894 | 538.112 | 402.3659 | 449.317 | 311.6461
1967.3167 | 523.0431 | 259.6876 | 493.0434 | 619.0575 | 538.5662 | 402.4765 | 449.7506 | 311.8878
1968.3167 | 520.8252 | 259.7639 | 491.0206 | 611.1822 | 542.2644 | 402.865 | 450.2164 | 312.2092
1969.3167 | 518.2186 | 259.8692 | 492.0224 | 614.2603 | 551.2415 | 403.2297 | 450.6438 | 312.6102
1970.3167 | 517.2231 | 259.9462 | 490.644 | 613.5569 | 550.3779 | 403.1516 | 451.0579 | 312.7506
1971.3167 | 515.7368 | 260.0768 | 490.0566 | 625.2715 | 548.9442 | 403.0457 | 451.4443 | 312.9574
1972.3167 | 515.8275 | 260.2005 | 497.426 | 630.8379 | 549.3195 | 403.2725 | 451.8716 | 313.1938
1973.3167 | 516.5359 | 260.2999 | 498.0098 | 629.0079 | 548.8389 | 403.4129 | 452.4351 | 313.3707
1974.3167 | 518.6924 | 260.412 | 495.3463 | 630.8455 | 542.1169 | 403.4436 | 452.8629 | 313.6086
1975.3167 | 519.3505 | 260.4806 | 494.6465 | 621.9608 | 535.6412 | 403.4305 | 453.3242 | 313.7682
1976.3167 | 520.0895 | 260.5708 | 492.5928 | 619.4564 | 528.1299 | 403.6417 | 453.7238 | 314.0433
1977.3167 | 519.3841 | 260.6156 | 493.5704 | 617.5739 | 529.6676 | 403.9663 | 454.1594 | 314.2473
1978.3167 | 516.867 | 260.7418 | 490.8104 | 620.2672 | 534.9206 | 404.2588 | 454.7138 | 314.5
1979.3167 | 515.4054 | 260.8433 | 492.5067 | 619.5012 | 528.8294 | 404.8292 | 455.2427 | 314.6998
1980.3167 | 515.6507 | 260.9095 | 490.7019 | 619.2143 | 530.9076 | 404.9193 | 455.7253 | 314.9284
1981.3167 | 516.3938 | 261.0315 | 491.2331 | 614.4644 | 527.3785 | 405.1696 | 456.3873 | 315.163
1982.3167 | 514.4465 | 261.097 | 491.787 | 617.3004 | 522.1524 | 405.1727 | 457.0861 | 315.3991
1983.3167 | 513.9671 | 261.2346 | 494.6145 | 634.1072 | 516.3319 | 405.4311 | 457.7192 | 315.6777
1984.3167 | 514.2203 | 261.3293 | 497.1078 | 647.0117 | 510.6718 | 405.7036 | 458.2595 | 315.9253
1985.3167 | 516.2988 | 261.4044 | 503.7034 | 638.0828 | 516.4421 | 406.0707 | 459.0725 | 316.1931
1986.3167 | 516.6734 | 261.507 | 503.0592 | 648.2381 | 519.6564 | 406.3961 | 459.7031 | 316.473
1987.3167 | 517.2417 | 261.6138 | 504.8651 | 645.7145 | 523.6956 | 406.9654 | 460.3098 | 316.7079
1988.3167 | 515.9584 | 261.8166 | 504.8765 | 647.4437 | 528.7664 | 407.1406 | 460.7816 | 316.9077
1989.3167 | 516.2325 | 261.9488 | 509.868 | 641.7757 | 524.1575 | 407.3292 | 461.2385 | 317.2999
1990.3167 | 516.1841 | 262.0701 | 511.0061 | 642.7902 | 518.6369 | 407.7932 | 461.5644 | 317.457
1991.3167 | 517.1198 | 262.1824 | 510.9427 | 637.0264 | 520.1243 | 407.9823 | 461.8357 | 317.6884
1992.3167 | 519.0489 | 262.2973 | 520.3589 | 633.6846 | 525.2625 | 408.0205 | 462.1108 | 317.8924
1993.3167 | 521.2275 | 262.4081 | 519.3942 | 631.772 | 526.2452 | 408.2996 | 462.3309 | 318.1987
1994.3167 | 521.8417 | 262.5262 | 514.2877 | 629.9211 | 520.6733 | 408.3672 | 462.6366 | 318.4798
1995.3167 | 522.2274 | 262.6282 | 510.7803 | 631.7891 | 516.978 | 408.4614 | 462.9626 | 318.7826
1996.3167 | 523.8051 | 262.747 | 508.4101 | 631.5755 | 513.2054 | 408.7695 | 463.3435 | 319.0377
1997.3167 | 523.5001 | 262.7291 | 506.5245 | 631.5645 | 509.2883 | 408.9939 | 463.7239 | 319.3118
1998.3167 | 522.8782 | 262.8247 | 507.6145 | 633.8524 | 504.4941 | 409.2271 | 464.0851 | 319.5894
1999.3167 | 524.0822 | 262.9541 | 510.2524 | 635.4158 | 497.1428 | 409.5496 | 464.4867 | 319.7746
2000.3167 | 526.3665 | 263.0724 | 515.1327 | 633.2631 | 491.1632 | 409.8239 | 464.9178 | 320.0574
2001.3167 | 529.5342 | 263.1965 | 513.6829 | 639.4522 | 486.1066 | 410.1789 | 465.2628 | 320.1386
2002.3167 | 533.5401 | 263.2605 | 511.3662 | 638.4945 | 486.6016 | 410.3792 | 465.7372 | 320.4123
2003.3167 | 535.3765 | 263.3463 | 510.4422 | 631.7835 | 490.4744 | 410.6386 | 466.3161 | 320.869
2004.3167 | 535.4752 | 263.4891 | 513.1142 | 630.7847 | 489.2268 | 410.9819 | 466.8101 | 321.2706
2005.3167 | 537.9248 | 263.6066 | 511.0099 | 626.2781 | 483.9668 | 412.0966 | 467.4343 | 321.8263
2006.3167 | 538.5375 | 263.6593 | 512.0197 | 625.8946 | 480.9026 | 411.3582 | 467.4513 | 321.7706
2007.3167 | 539.0939 | 263.7866 | 512.7011 | 621.7145 | 478.3623 | 411.5751 | 467.9192 | 322.0764
2008.3167 | 538.5877 | 263.8779 | 508.6582 | 609.9707 | 475.2028 | 412.0187 | 468.3113 | 322.3191
2009.3167 | 536.0941 | 263.8673 | 503.3809 | 601.499 | 470.9424 | 412.4629 | 468.9908 | 322.8467
2010.3167 | 537.061 | 263.9829 | 507.4653 | 607.547 | 467.3672 | 412.029 | 469.3463 | 323.0234
2011.3167 | 536.97 | 264.0701 | 517.4852 | 615.073 | 466.3906 | 412.7896 | 469.9702 | 323.3
2012.3167 | 536.9258 | 264.2316 | 522.5545 | 620.7754 | 464.0611 | 413.1893 | 470.4862 | 323.479
2013.3167 | 536.2643 | 264.3334 | 520.5411 | 621.7727 | 461.8214 | 413.4873 | 470.7759 | 323.7065
2014.3167 | 535.8534 | 264.4512 | 518.5516 | 616.7127 | 460.3645 | 413.7712 | 471.2986 | 324.0465
2015.3167 | 536.2772 | 264.5658 | 519.1785 | 624.114 | 459.0543 | 414.0011 | 471.9339 | 324.3543
2016.3167 | 536.2882 | 264.7025 | 513.3381 | 623.8404 | 457.241 | 414.451 | 472.3758 | 324.688
2017.3167 | 535.7225 | 264.7603 | 508.9779 | 622.8292 | 456.0029 | 414.5166 | 472.8782 | 324.9107
2018.3167 | 536.8484 | 264.9261 | 505.972 | 616.8252 | 456.5087 | 414.8266 | 473.4007 | 325.2127
2019.3167 | 537.7179 | 265.0312 | 501.1772 | 624.685 | 455.9607 | 415.2035 | 473.921 | 325.5063
2020.3167 | 536.0116 | 265.135 | 497.9173 | 633.9677 | 457.3279 | 415.613 | 474.2364 | 325.8769
2021.3167 | 536.0908 | 265.2447 | 495.5878 | 631.8895 | 458.754 | 416.1102 | 474.7089 | 326.2157
2022.3167 | 534.4981 | 265.3981 | 507.4562 | 632.8464 | 458.445 | 415.9455 | 475.2678 | 326.4201
2023.3167 | 533.5322 | 265.5298 | 514.7839 | 632.3437 | 458.6719 | 416.311 | 475.58 | 326.7138
2024.3167 | 535.1639 | 265.673 | 514.8131 | 635.4304 | 458.509 | 416.7004 | 475.8697 | 326.9174
2025.3167 | 538.022 | 265.8143 | 534.2361 | 636.1335 | 460.7797 | 416.9637 | 476.3503 | 327.1924
2026.3167 | 539.2426 | 265.9469 | 533.1109 | 634.5993 | 463.1274 | 417.5554 | 476.5887 | 327.4738
2027.3167 | 539.943 | 266.0664 | 528.2966 | 630.5611 | 464.5056 | 417.8131 | 477.028 | 327.9122
2028.3167 | 539.1591 | 266.22 | 526.5314 | 626.5548 | 464.4202 | 418.331 | 477.4181 | 328.2398
2029.3167 | 538.6929 | 266.3628 | 522.9127 | 625.8205 | 464.8891 | 418.206 | 477.5394 | 328.5429
2030.3167 | 539.5864 | 266.5211 | 520.4298 | 627.4429 | 464.4576 | 418.6994 | 477.916 | 328.9116
2031.3167 | 540.9612 | 266.6565 | 517.5389 | 632.2594 | 462.6233 | 418.7072 | 478.1682 | 329.1543
2032.3167 | 539.1388 | 266.8502 | 516.3176 | 633.9252 | 462.109 | 420.1105 | 478.7021 | 329.7707
2033.3167 | 539.3346 | 267.0043 | 516.4152 | 635.8739 | 462.078 | 420.4112 | 478.7993 | 330.1112
2034.3167 | 538.1399 | 267.105 | 523.9421 | 637.0942 | 464.3545 | 420.4205 | 478.8426 | 330.3363
2035.3167 | 535.8049 | 267.273 | 525.9669 | 651.1841 | 464.2161 | 421.3041 | 479.081 | 330.9774
2036.3167 | 537.2106 | 267.3682 | 519.3218 | 643.1722 | 461.7961 | 421.2403 | 479.1547 | 331.0957
2037.3167 | 541.0248 | 267.5603 | 516.049 | 633.3152 | 459.4598 | 421.6598 | 479.4104 | 331.4057
2038.3167 | 540.8232 | 267.6167 | 520.6105 | 624.9453 | 456.9386 | 420.6033 | 479.1914 | 331.2989
2039.3167 | 539.1133 | 267.7543 | 520.2025 | 644.6829 | 455.0031 | 420.7652 | 479.2568 | 331.5695
2040.3167 | 538.9808 | 267.8537 | 523.6681 | 636.6536 | 454.5792 | 421.4995 | 479.435 | 331.9068
2041.3167 | 538.937 | 267.9856 | 521.3545 | 639.499 | 455.7473 | 421.7092 | 479.7391 | 332.2637
2042.3167 | 536.8294 | 268.1297 | 522.6707 | 632.6016 | 455.2068 | 421.8976 | 480.0058 | 332.6011
2043.3167 | 536.4115 | 268.2531 | 523.7957 | 647.1349 | 454.8555 | 422.3408 | 480.08 | 332.8897
2044.3167 | 537.9052 | 268.3901 | 525.4563 | 642.454 | 455.614 | 423.1073 | 480.3191 | 333.3047
2045.3167 | 539.8878 | 268.5243 | 526.7557 | 647.049 | 456.9961 | 422.9705 | 480.4362 | 333.6898
2046.3167 | 541.1953 | 268.6755 | 529.9766 | 650.3894 | 458.4326 | 423.6235 | 480.8328 | 334.1002
2047.3167 | 543.5814 | 268.798 | 528.5887 | 651.5355 | 458.6267 | 423.5471 | 480.9233 | 334.3827
2048.3167 | 543.6229 | 268.9124 | 527.8281 | 640.9112 | 457.4027 | 423.8035 | 481.1074 | 334.78
2049.3167 | 542.8483 | 269.0207 | 527.5921 | 645.238 | 457.5117 | 424.0364 | 481.2926 | 335.1323
2050.3167 | 541.9038 | 269.1937 | 529.1257 | 653.3679 | 456.0703 | 424.049 | 481.4875 | 335.5294
2051.3167 | 542.958 | 269.3469 | 531.7887 | 656.2668 | 455.1699 | 424.3557 | 481.7252 | 335.906
2052.3167 | 541.745 | 269.497 | 529.9997 | 654.6165 | 453.4436 | 424.6672 | 482 | 336.2836
2053.3167 | 540.9699 | 269.6618 | 531.3674 | 659.3095 | 453.2026 | 424.9483 | 482.3119 | 336.6862
2054.3167 | 544.5349 | 269.8077 | 533.0813 | 660.1385 | 457.6684 | 425.5595 | 482.6506 | 337.0767
2055.3167 | 550.6949 | 269.9582 | 535.6845 | 667.676 | 460.7014 | 426.3089 | 483.0661 | 337.5421
2056.3167 | 551.109 | 270.1131 | 532.119 | 672.7067 | 465.8039 | 426.787 | 483.299 | 337.9749
2057.3167 | 552.8153 | 270.2652 | 537.4549 | 669.9904 | 466.6311 | 427.4794 | 483.7393 | 338.3924
2058.3167 | 553.078 | 270.4094 | 535.5732 | 670.3345 | 464.5906 | 427.6114 | 484.095 | 338.7818
2059.3167 | 565.4018 | 270.55 | 543.0486 | 676.8 | 464.449 | 428.0369 | 484.4947 | 339.1957
2060.3167 | 567.941 | 270.6881 | 543.1761 | 664.9086 | 464.7246 | 428.2387 | 485.049 | 339.5825
2061.3167 | 571.758 | 270.841 | 542.9256 | 662.4323 | 465.5195 | 428.3706 | 485.3779 | 340.0153
2062.3167 | 571.9608 | 270.9854 | 540.2603 | 657.4498 | 466.9185 | 428.5362 | 485.7338 | 340.4505
2063.3167 | 570.4101 | 271.1263 | 537.5631 | 660.838 | 465.3903 | 428.6629 | 486.066 | 340.8566
2064.3167 | 571.6438 | 271.2769 | 535.648 | 660.7763 | 463.9732 | 428.8877 | 486.3929 | 341.2896
2065.3167 | 571.3286 | 271.4104 | 533.4471 | 673.2274 | 462.6841 | 429.2274 | 486.6469 | 341.6942
2066.3167 | 570.1492 | 271.5851 | 532.6211 | 662.5259 | 460.611 | 429.8365 | 487.0203 | 342.1783
2067.3167 | 570.6839 | 271.7191 | 527.5835 | 656.6983 | 460.0923 | 429.5392 | 487.2617 | 342.5031
2068.3167 | 571.7297 | 271.8536 | 529.6883 | 652.4653 | 466.8229 | 429.8785 | 487.5719 | 343.0018
2069.3167 | 572.1843 | 272.0041 | 531.3463 | 673.6994 | 472.9718 | 430.3922 | 487.9371 | 343.4959
2070.3167 | 575.5302 | 272.1267 | 531.2109 | 682.6565 | 475.4492 | 431.3293 | 488.2584 | 344.0469
2071.3167 | 578.1448 | 272.2781 | 533.169 | 691.933 | 478.4495 | 431.7505 | 488.522 | 344.5575
2072.3167 | 583.4315 | 272.4303 | 538.2211 | 695.4132 | 483.6879 | 432.6615 | 488.832 | 344.996
2073.3167 | 588.5175 | 272.5518 | 541.4606 | 700.7586 | 485.1302 | 433.2203 | 489.1535 | 345.5057
2074.3167 | 589.7661 | 272.6872 | 544.3193 | 702.7004 | 484.2243 | 434.2048 | 489.5836 | 346.035
2075.3167 | 594.1419 | 272.7758 | 544.4965 | 703.0057 | 487.1354 | 435.0213 | 489.9332 | 346.4153
2076.3167 | 593.9985 | 272.9152 | 547.5287 | 703.6601 | 489.8374 | 435.8644 | 490.4702 | 346.9589
2077.3167 | 598.5126 | 272.9485 | 546.744 | 698.5797 | 497.3505 | 436.2964 | 490.8335 | 347.2937
2078.3167 | 599.4305 | 273.0998 | 546.7903 | 688.6539 | 500.3616 | 435.7495 | 491.3267 | 347.7247
2079.3167 | 597.8586 | 273.2469 | 542.7295 | 678.766 | 501.8798 | 435.5904 | 491.7551 | 348.2475
2080.3167 | 593.0807 | 273.3639 | 539.3763 | 671.1988 | 501.3 | 435.0729 | 492.0066 | 348.831
2081.3167 | 589.0479 | 273.49 | 547.1384 | 671.553 | 503.3725 | 435.5841 | 492.308 | 349.0134
2082.3167 | 586.6724 | 273.6216 | 555.8784 | 672.6677 | 505.2807 | 435.538 | 492.777 | 349.3547
2083.3167 | 583.7588 | 273.7558 | 555.866 | 672.3413 | 507.6957 | 435.7993 | 493.0778 | 349.776
2084.3167 | 580.7347 | 273.8916 | 552.2796 | 664.3257 | 506.7543 | 436.2219 | 493.5605 | 350.1929
2085.3167 | 578.7018 | 274.0342 | 551.2379 | 662.6775 | 519.6166 | 436.233 | 494.0109 | 350.5498
2086.3167 | 577.8075 | 274.1568 | 547.7173 | 658.5355 | 524.6687 | 436.2991 | 494.4623 | 350.9646
2087.3167 | 576.5801 | 274.2949 | 550.6348 | 655.2277 | 521.4047 | 436.3616 | 494.8868 | 351.4558
2088.801 | 575.6669 | 274.4949 | 553.8759 | 664.3708 | 530.3361 | 436.8051 | 495.4568 | 352.342
2089.3792 | 575.333 | 274.5653 | 558.4569 | 663.1707 | 530.7129 | 437.0733 | 495.6948 | 352.6138
2090.3948 | 574.3869 | 274.717 | 554.616 | 659.1456 | 531.2633 | 437.2773 | 496.1481 | 353.3015
2091.426 | 573.3813 | 274.836 | 550.4478 | 657.7082 | 533.6447 | 437.387 | 496.545 | 353.5093
2092.4104 | 572.1787 | 274.995 | 549.0267 | 665.4268 | 542.9739 | 437.7995 | 496.9415 | 353.8821
2093.3167 | 571.8684 | 275.1444 | 548.8646 | 659.518 | 550.8712 | 438.2767 | 497.443 | 354.3103
2095.1604 | 570.7773 | 275.4467 | 547.1677 | 648.3994 | 572.886 | 438.5531 | 498.2474 | 355.3452
2095.6448 | 569.5301 | 275.5086 | 544.9506 | 645.2307 | 574.2593 | 438.4272 | 498.4999 | 355.5569
2096.3167 | 568.0758 | 275.6272 | 544.1152 | 642.9162 | 573.5543 | 438.3261 | 498.8721 | 355.992
2097.3167 | 568.4074 | 275.6031 | 542.6572 | 638.6156 | 581.9064 | 438.14 | 499.2518 | 357.8034
2098.3167 | 568.5282 | 275.7784 | 541.8078 | 640.7349 | 586.634 | 438.2438 | 499.6325 | 360.3323
2099.3167 | 569.434 | 275.968 | 543.0471 | 638.415 | 583.8665 | 438.7166 | 499.9931 | 361.4359
2100.3167 | 570.6472 | 276.038 | 546.3758 | 644.3622 | 581.0688 | 438.6268 | 500.3411 | 362.881
2101.3167 | 568.3756 | 276.2278 | 548.8126 | 639.4877 | 589.232 | 439.107 | 500.8105 | 364.0947
2102.3167 | 572.4837 | 276.4099 | 550.6787 | 646.5886 | 596.6182 | 438.9706 | 501.1873 | 365.0162
2103.3167 | 573.8935 | 276.5784 | 553.6123 | 646.7679 | 599.1262 | 439.6213 | 501.6107 | 365.8517
2104.3167 | 573.7221 | 276.7553 | 553.7101 | 645.322 | 595.8083 | 440.0737 | 502.181 | 366.7245
2105.3167 | 575.2568 | 276.8701 | 557.5346 | 651.9616 | 591.4374 | 440.4492 | 502.6496 | 367.5335
2106.3167 | 575.6622 | 277.0642 | 558.5799 | 648.0175 | 582.6595 | 440.5796 | 503.1584 | 368.3305
2107.3167 | 580.8192 | 277.2143 | 553.5253 | 644.1036 | 585.677 | 441.0709 | 503.5962 | 369.1522
2108.3167 | 580.5973 | 277.3967 | 550.3588 | 639.0344 | 590.9786 | 441.2403 | 504.1012 | 369.9413
2109.3167 | 579.3788 | 277.5739 | 552.3231 | 637.5876 | 601.9749 | 442.1401 | 504.5722 | 370.6338
2110.3167 | 579.0162 | 277.739 | 547.8617 | 636.7826 | 612.1733 | 442.541 | 505.1184 | 371.1726
2111.3167 | 577.7561 | 277.8039 | 552.3464 | 648.4197 | 616.6818 | 442.96 | 505.5914 | 371.6342
2112.3167 | 578.4856 | 278.0025 | 553.0138 | 647.1602 | 622.7738 | 443.8678 | 506.1605 | 372.1423
2113.3167 | 580.1237 | 278.1703 | 552.2095 | 650.9521 | 627.3534 | 443.9469 | 506.7261 | 372.6662
2114.3167 | 583.3417 | 278.3239 | 549.5402 | 649.8965 | 629.7493 | 444.8363 | 507.2704 | 373.385
2115.3167 | 582.1005 | 278.4805 | 549.8235 | 645.1892 | 631.2589 | 445.0206 | 507.8423 | 374.1152
2116.3167 | 583.547 | 278.6531 | 550.8366 | 650.0354 | 623.8408 | 444.7788 | 508.3426 | 374.6308
2117.3167 | 585.4088 | 278.8036 | 553.4976 | 654.9431 | 633.4735 | 445.4449 | 508.9351 | 375.3933
2118.3167 | 589.6563 | 278.9626 | 558.3432 | 663.7116 | 643.4525 | 445.9158 | 509.5444 | 375.6746
2119.3167 | 591.3797 | 279.1634 | 556.4271 | 678.444 | 639.6112 | 446.954 | 510.1202 | 376.2753
2120.3167 | 595.5218 | 279.3409 | 558.6337 | 680.7338 | 638.6995 | 447.6014 | 510.7571 | 376.7729
2121.3167 | 595.3947 | 279.5248 | 555.1979 | 676.5467 | 637.6654 | 448.5414 | 511.4002 | 377.4175
2122.3167 | 596.0927 | 279.6868 | 549.552 | 669.6033 | 629.7402 | 449.0418 | 512.0156 | 378.078
2123.3167 | 594.4689 | 279.8466 | 550.3178 | 666.7462 | 618.5775 | 448.5625 | 512.6497 | 378.576
2124.3167 | 593.45 | 280.0007 | 556.891 | 669.662 | 607.8351 | 447.9085 | 513.1453 | 379.0781
2125.3167 | 590.7301 | 280.1732 | 558.6799 | 668.9298 | 615.4019 | 447.9134 | 513.7103 | 379.7463
2126.3323 | 590.7431 | 280.3351 | 570.7819 | 671.7399 | 614.5 | 448.0799 | 514.2732 | 380.2906
2127.3167 | 590.0826 | 280.5372 | 567.3057 | 668.9712 | 618.0839 | 448.3433 | 514.8911 | 380.9935
2128.3323 | 591.2696 | 280.7442 | 560.8612 | 666.5419 | 621.7771 | 448.8309 | 515.4857 | 382.7867
2129.3167 | 589.8256 | 280.9466 | 555.5864 | 653.0895 | 614.0532 | 448.935 | 516.1481 | 383.4316
2130.3167 | 590.2951 | 281.1911 | 553.3627 | 647.8398 | 613.776 | 449.4641 | 516.6179 | 384.1576
2131.3167 | 592.0464 | 281.3758 | 549.9715 | 648.5313 | 605.5551 | 449.6242 | 517.1897 | 385.0231
2132.3323 | 592.4577 | 281.5615 | 542.3664 | 638.3662 | 595.4701 | 449.4563 | 517.6826 | 385.7991
2133.3167 | 591.312 | 281.7338 | 540.7137 | 640.7041 | 586.2101 | 449.3855 | 518.1483 | 386.1066
2134.3167 | 589.6882 | 281.9027 | 542.1151 | 640.6689 | 580.9861 | 449.264 | 518.7023 | 386.6899
2135.3167 | 586.082 | 282.0664 | 543.6664 | 642.7779 | 575.6765 | 449.5138 | 519.1039 | 387.1871
2136.3167 | 585.0006 | 282.2234 | 543.1199 | 637.8259 | 570.7016 | 449.4135 | 519.641 | 387.6698
2137.3167 | 583.5007 | 282.3947 | 539.6245 | 638.9091 | 564.6073 | 449.2705 | 520.0953 | 388.3237
2138.3167 | 584.3728 | 282.5803 | 542.1579 | 646.6604 | 566.534 | 449.2867 | 520.4803 | 389.2598
2139.3167 | 584.5245 | 282.7206 | 541.5536 | 641.4424 | 576.4715 | 449.606 | 521.0693 | 390.8056
2140.3167 | 585.4981 | 282.8753 | 539.8481 | 636.6825 | 572.0014 | 449.3753 | 521.5001 | 391.5292
2141.3167 | 586.5064 | 283.0368 | 540.9379 | 647.2086 | 568.6424 | 450.9071 | 520.8127 | 392.8117
2142.3167 | 586.4151 | 283.1983 | 541.5388 | 647.6035 | 563.4251 | 452.1394 | 518.4547 | 394.6919
2143.3167 | 586.55 | 283.3892 | 537.9068 | 644.3093 | 556.7894 | 452.2814 | 516.4501 | 395.8311
2144.3167 | 584.2894 | 283.5039 | 536.8864 | 639.8208 | 557.7995 | 452.5699 | 514.5867 | 396.8565
2145.3167 | 581.7516 | 283.6895 | 533.9951 | 629.4616 | 552.7229 | 453.5482 | 513.102 | 396.9672
2146.3167 | 581.2174 | 283.8625 | 535.0539 | 627.4835 | 547.4407 | 453.8986 | 511.8069 | 397.4419
2147.3167 | 581.1623 | 284.0225 | 539.8798 | 622.1993 | 541.0787 | 454.2978 | 510.8735 | 397.8633
2148.3167 | 582.2087 | 284.2332 | 540.8561 | 619.845 | 536.2659 | 454.6727 | 510.204 | 398.5125
2149.3167 | 583.9541 | 284.4101 | 538.8434 | 614.4891 | 531.2858 | 455.2659 | 509.8125 | 399.1172
2150.3167 | 584.2782 | 284.581 | 536.2076 | 608.7563 | 526.9279 | 455.9638 | 509.4181 | 400.2922
2151.3167 | 582.7509 | 284.7253 | 537.0337 | 603.8283 | 523.1789 | 456.4669 | 509.1762 | 401.0758
2152.3167 | 582.5537 | 284.8778 | 534.711 | 598.8955 | 519.6855 | 457.0562 | 509.0388 | 401.9563
2153.3167 | 584.0228 | 285.0386 | 535.7609 | 598.43 | 517.1401 | 457.8243 | 508.9666 | 402.7269
2154.3167 | 584.2711 | 285.2106 | 535.4985 | 595.2604 | 515.7007 | 458.4999 | 508.9366 | 403.5827
2155.3167 | 581.8815 | 285.3376 | 535.0453 | 589.0983 | 512.2616 | 459.115 | 508.9748 | 404.0442
2156.3167 | 582.8193 | 285.5567 | 535.7364 | 590.7576 | 508.1115 | 459.8773 | 509.2152 | 405.2144
2157.3167 | 590.1705 | 285.759 | 538.3232 | 592.2231 | 507.3019 | 460.151 | 509.4374 | 405.8343
2158.3167 | 590.6514 | 285.9411 | 549.777 | 593.0744 | 506.7805 | 460.0698 | 509.6687 | 406.244
2159.3167 | 593.4922 | 285.9978 | 552.4345 | 597.9712 | 506.3986 | 459.7518 | 509.6851 | 406.6449
2160.3167 | 591.2499 | 286.1578 | 558.253 | 598.9315 | 505.3265 | 459.8836 | 510.0819 | 407.0184
2161.3167 | 591.4838 | 286.3176 | 556.1586 | 604.8564 | 504.3915 | 460.0721 | 510.2192 | 407.7043
2162.3479 | 589.9999 | 286.4881 | 552.5379 | 604.3153 | 504.2306 | 460.6471 | 510.5291 | 408.2912
2163.3167 | 588.7787 | 286.5783 | 549.7644 | 609.0981 | 505.0234 | 461.8101 | 510.7419 | 409.0073
2164.3167 | 588.9896 | 286.686 | 548.0308 | 612.1907 | 503.7301 | 462.2201 | 510.9764 | 409.614
2165.3167 | 589.8458 | 286.8149 | 543.5956 | 611.2724 | 503.1458 | 462.7211 | 511.3099 | 410.1005
2166.3323 | 588.1808 | 286.9635 | 542.9718 | 612.5985 | 501.8778 | 463.1605 | 511.6124 | 410.2531
2167.3167 | 588.1935 | 287.0744 | 543.3492 | 614.2708 | 501.3954 | 463.8635 | 511.9359 | 410.4278
2168.3167 | 591.9265 | 287.2242 | 542.3727 | 615.0373 | 501.1047 | 464.7833 | 512.2744 | 410.8066
2169.3167 | 591.7949 | 287.3667 | 543.0714 | 614.4066 | 500.4817 | 465.4205 | 512.6187 | 411.572
2170.3167 | 591.336 | 287.5124 | 541.2821 | 612.3293 | 499.0175 | 465.2204 | 513.0773 | 412.1297
2171.3167 | 590.7212 | 287.6867 | 539.1269 | 609.9978 | 497.0022 | 464.1761 | 513.3769 | 412.3554
2172.3167 | 589.1647 | 287.8442 | 539.1939 | 612.8079 | 494.9967 | 462.9482 | 513.8525 | 412.7793
2173.3167 | 589.2227 | 287.996 | 539.0116 | 616.3235 | 495.8496 | 462.4379 | 514.2153 | 413.257
2174.3167 | 588.6895 | 288.134 | 540.3842 | 617.9788 | 497.8812 | 461.435 | 514.7403 | 413.8287
2175.3167 | 588.5836 | 288.2761 | 542.9129 | 621.7066 | 497.2993 | 461.0559 | 515.2334 | 414.2121
2176.3167 | 589.0111 | 288.4202 | 540.7228 | 622.066 | 499.4959 | 461.1117 | 515.6847 | 414.5189
2177.3167 | 589.6999 | 288.5875 | 538.6284 | 623.0943 | 499.144 | 461.6316 | 516.1096 | 414.7926
2178.3167 | 589.1263 | 288.7303 | 535.6473 | 629.8616 | 498.5385 | 461.7999 | 516.6571 | 415.0704
2179.3167 | 590.4586 | 288.9286 | 539.259 | 631.1093 | 497.0043 | 462.1502 | 517.1584 | 415.6899
2180.3167 | 591.5138 | 289.0982 | 539.0392 | 631.2598 | 495.027 | 462.563 | 517.5431 | 416.0606
2181.3167 | 592.1234 | 289.2703 | 540.9196 | 629.3895 | 494.5222 | 462.7426 | 518.0059 | 416.5345
2182.3167 | 590.4625 | 289.4561 | 538.0912 | 621.1165 | 493.2114 | 463.0733 | 518.5884 | 416.4258
2183.3167 | 592.405 | 289.6443 | 538.412 | 621.6907 | 495.6396 | 463.0629 | 519.0296 | 415.2389
2184.3167 | 591.3766 | 289.8364 | 533.254 | 617.8247 | 497.6099 | 463.3315 | 519.4433 | 415.3497
2185.3167 | 591.0593 | 290.0073 | 529.9071 | 615.9279 | 500.5506 | 463.5676 | 519.7831 | 415.6238
2186.3167 | 591.7534 | 290.1998 | 526.6389 | 619.2691 | 503.4278 | 463.6635 | 520.18 | 416.0357
2187.3167 | 593.055 | 290.3511 | 527.0562 | 618.6031 | 504.6043 | 463.6231 | 520.4241 | 416.1527
2188.3167 | 597.2083 | 290.6207 | 526.8407 | 623.9048 | 504.2564 | 464.3552 | 521.0994 | 416.6213
2189.3167 | 596.676 | 290.7312 | 529.8442 | 627.1152 | 505.1432 | 463.4421 | 521.1607 | 416.5625
2190.3167 | 595.2852 | 290.9008 | 531.5808 | 626.4393 | 503.9809 | 463.5339 | 521.505 | 416.8253
2191.3167 | 594.5397 | 291.0644 | 531.8407 | 622.522 | 503.0398 | 463.552 | 521.9321 | 417.132
2192.3167 | 596.441 | 291.1904 | 531.8933 | 622.8109 | 502.4182 | 463.3533 | 522.3141 | 417.354
2193.3167 | 595.3908 | 291.3819 | 531.1473 | 627.1782 | 503.0494 | 463.079 | 522.7497 | 417.5926
2194.3167 | 598.7111 | 291.5822 | 533.9683 | 627.2042 | 506.1066 | 463.5946 | 523.1658 | 417.9173
2195.3167 | 599.6721 | 291.7675 | 530.6977 | 630.3982 | 506.6639 | 463.9126 | 523.7564 | 418.1709
2196.3167 | 600.6053 | 291.9466 | 531.807 | 629.2369 | 508.7755 | 463.9133 | 524.1374 | 418.4929
2197.3167 | 609.1218 | 292.1488 | 530.8122 | 626.7976 | 507.4592 | 463.9431 | 524.5428 | 418.7119
2198.3167 | 605.028 | 292.3453 | 534.2288 | 629.4237 | 506.3294 | 464.0363 | 524.9483 | 418.9368
2199.3167 | 602.1385 | 292.5367 | 535.7888 | 627.0342 | 506.8494 | 464.278 | 525.2885 | 419.2242
2200.3167 | 599.484 | 292.7361 | 538.2745 | 620.3845 | 505.1689 | 464.6527 | 525.6813 | 419.4939
2201.3167 | 599.1518 | 292.9143 | 541.9109 | 634.859 | 502.6243 | 465.0494 | 526.0236 | 419.7069
2202.3167 | 599.0059 | 293.0951 | 543.8814 | 629.5778 | 500.6583 | 465.5033 | 526.3514 | 420.0271
2203.3167 | 598.4746 | 293.2856 | 541.1057 | 630.1512 | 499.526 | 465.5325 | 526.6825 | 420.3113
2204.3167 | 598.5596 | 293.4635 | 536.5416 | 627.9793 | 498.3868 | 465.7939 | 527.0491 | 420.6441
2205.3167 | 596.8728 | 293.6418 | 534.978 | 627.5903 | 497.4332 | 466.0289 | 527.4705 | 421.2682
2206.3167 | 596.0128 | 293.7607 | 537.54 | 626.716 | 495.4505 | 466.2947 | 527.8514 | 422.1746
2207.3167 | 597.9648 | 293.934 | 539.9512 | 624.7443 | 494.3189 | 466.8037 | 528.1095 | 423.4383
2208.3167 | 602.2188 | 294.1079 | 542.0089 | 622.7953 | 491.4802 | 467.3376 | 528.4722 | 423.6616
2209.3167 | 602.2161 | 294.3084 | 543.6463 | 633.9389 | 489.1809 | 467.9575 | 528.8386 | 423.8447
2210.3167 | 601.9641 | 294.4421 | 548.0473 | 632.3315 | 487.308 | 468.2575 | 529.1686 | 423.7051
2211.3167 | 604.6695 | 294.5854 | 549.3847 | 642.3735 | 485.5349 | 468.4628 | 529.5564 | 424.0141
2212.3167 | 606.9087 | 294.7661 | 548.8535 | 643.4649 | 484.3189 | 468.8517 | 529.9322 | 424.3463
2213.3167 | 606.7073 | 294.9606 | 549.7686 | 638.7539 | 483.1809 | 469.3349 | 530.3503 | 424.6956
2214.3167 | 610.6876 | 295.1144 | 548.8571 | 636.0554 | 482.4083 | 469.7695 | 530.7853 | 425.1526
2215.3167 | 613.7185 | 295.2821 | 550.5737 | 636.0372 | 480.7 | 470.1575 | 531.187 | 425.6281
2216.3167 | 616.1149 | 295.4443 | 550.5702 | 637.5608 | 483.0634 | 470.4984 | 531.6425 | 426.0356
2217.3167 | 611.0892 | 295.593 | 549.6749 | 631.2308 | 484.4669 | 470.7261 | 532.069 | 426.4505
2218.3167 | 609.7946 | 295.7589 | 551.5226 | 645.1896 | 483.5839 | 471.1397 | 532.4579 | 427.0141
2219.3167 | 611.5605 | 295.9428 | 556.425 | 654.9094 | 484.2515 | 471.4733 | 532.8823 | 427.2898
2220.3167 | 611.1223 | 296.1051 | 556.9933 | 649.5118 | 483.2133 | 471.8126 | 533.2516 | 429.9485
2221.3167 | 611.7574 | 296.2281 | 556.5755 | 646.9413 | 483.5948 | 472.1598 | 533.4761 | 429.6754
2222.3323 | 612.0913 | 296.4085 | 555.5094 | 644.5088 | 485.72 | 472.4228 | 533.6596 | 429.4161
2223.3167 | 617.5489 | 296.5573 | 556.9465 | 639.72 | 488.9036 | 472.7442 | 533.8642 | 429.7172
2224.3167 | 621.0587 | 296.7082 | 554.5655 | 638.0459 | 493.0215 | 472.9903 | 534.1273 | 430.2328
2225.3167 | 626.6904 | 296.8749 | 550.2177 | 640.0017 | 495.1568 | 473.0999 | 534.4509 | 430.6519
2226.3167 | 623 | 297.0297 | 548.9592 | 639.2151 | 493.4546 | 473.2561 | 534.7738 | 430.9
2227.3167 | 618.7696 | 297.2065 | 549.6228 | 638.1175 | 492.7638 | 473.483 | 535.1501 | 431.1396
2228.3167 | 621.3765 | 297.3811 | 547.8936 | 633.2668 | 494.5437 | 473.7816 | 535.5447 | 431.4173
2229.3167 | 624.9502 | 297.547 | 547.673 | 634.4787 | 496.1266 | 473.9796 | 535.946 | 431.8884
2230.3167 | 630.0408 | 297.7048 | 549.3057 | 630.7259 | 501.0602 | 474.2395 | 536.3629 | 432.1398
2231.3167 | 627.2306 | 297.8783 | 548.6214 | 630.2951 | 503.6247 | 474.2623 | 536.7832 | 432.5025
2232.3167 | 624.0678 | 298.0357 | 545.5799 | 627.4486 | 503.1286 | 474.6184 | 537.2231 | 432.8284
2233.3167 | 620.1377 | 298.2184 | 545.4167 | 623.138 | 501.021 | 474.7953 | 537.6502 | 433.1076
2234.3167 | 622.0476 | 298.408 | 542.7224 | 618.39 | 499.7023 | 474.9677 | 538.0799 | 433.3351
2235.3167 | 623.5089 | 298.5739 | 541.0736 | 621.0536 | 499.2953 | 475.1563 | 538.4961 | 433.5673
2236.3167 | 619.6436 | 298.7564 | 540.0054 | 621.9389 | 499.2797 | 475.377 | 538.9095 | 433.8304
2237.3167 | 617.4254 | 298.9339 | 540.7247 | 622.5127 | 497.494 | 475.484 | 539.375 | 434.0813
2238.3167 | 615.5897 | 299.1159 | 540.4167 | 621.4232 | 496.8437 | 475.6809 | 539.8358 | 434.2664
2239.3167 | 625.5404 | 299.3053 | 539.9289 | 621.0277 | 495.6863 | 475.7459 | 540.3394 | 434.5229
2240.3167 | 631.6821 | 299.4798 | 536.1695 | 616.5629 | 495.1934 | 475.9916 | 540.8268 | 434.8243
2241.3167 | 636.343 | 299.6562 | 536.7536 | 618.8193 | 494.2014 | 476.0392 | 541.3291 | 435.1396
2242.3167 | 635.9762 | 299.8221 | 535.8433 | 618.1097 | 493.947 | 476.2119 | 541.7799 | 435.5116
2243.3167 | 631.5855 | 300.009 | 534.6402 | 611.9869 | 492.7294 | 476.5562 | 542.2543 | 435.86
2244.3167 | 630.0742 | 300.2051 | 537.1712 | 608.5145 | 490.7313 | 476.8271 | 542.7021 | 436.1475
2245.3167 | 628.0666 | 300.3731 | 536.6109 | 602.6763 | 489.2523 | 477.1492 | 543.1744 | 436.3523
2246.3167 | 627.0505 | 300.5558 | 530.8755 | 597.1013 | 487.2764 | 477.3799 | 543.6137 | 436.5945
2247.3167 | 625.6617 | 300.7513 | 525.8747 | 595.8641 | 485.83 | 477.5485 | 544.0815 | 436.7634
2248.3167 | 621.9096 | 300.9246 | 530.275 | 598.571 | 486.3115 | 477.6366 | 544.52 | 436.9315
2249.3167 | 617.7151 | 301.0959 | 533.8662 | 594.9625 | 487.3497 | 477.8966 | 544.9928 | 437.0536
2250.3167 | 614.6345 | 301.2709 | 537.1766 | 591.8136 | 486.9826 | 478.1387 | 545.4675 | 437.3407
2251.3167 | 611.199 | 301.4447 | 540.3157 | 590.5907 | 486.8552 | 478.4906 | 545.9739 | 437.4884
2252.3167 | 611.4223 | 301.689 | 541.4912 | 588.3576 | 486.68 | 479.1888 | 546.6394 | 437.8409
2253.3167 | 608.6708 | 301.8108 | 541.5665 | 595.2685 | 485.3525 | 479.0196 | 546.963 | 437.8657
2254.3167 | 607.8366 | 301.9813 | 541.9449 | 600.5853 | 484.5763 | 479.3231 | 547.4215 | 437.9956
2255.3167 | 611.9656 | 302.1582 | 542.1129 | 599.1246 | 484.7483 | 479.5895 | 547.8879 | 438.1835
2256.3167 | 609.8744 | 302.3383 | 544.6085 | 601.7225 | 484.1277 | 479.8507 | 548.3878 | 438.3756
2257.3167 | 609.0946 | 302.5103 | 548.5917 | 608.1654 | 485.1723 | 480.0645 | 548.8977 | 438.6408
2258.3167 | 609.0315 | 302.6857 | 548.9292 | 604.2722 | 485.1487 | 480.157 | 549.3527 | 438.7426
2259.3167 | 614.1549 | 302.859 | 544.935 | 598.8807 | 484.4565 | 480.2498 | 549.8783 | 438.9146
2260.3167 | 621.1598 | 303.0376 | 541.0484 | 599.4072 | 483.9199 | 480.2224 | 550.4546 | 439.1311
2261.3167 | 626.9948 | 303.2018 | 542.7435 | 605.3677 | 483.5285 | 480.1253 | 550.9601 | 439.2574
2262.3167 | 630.0938 | 303.3817 | 539.5187 | 609.7816 | 485.8201 | 480.2632 | 551.4811 | 439.4165
2263.3167 | 629.7257 | 303.5732 | 541.6205 | 614.3461 | 488.6984 | 480.3852 | 552.0153 | 439.5929
2264.3167 | 628.8361 | 303.731 | 541.3572 | 612.033 | 491.2298 | 480.3066 | 552.4675 | 439.7398
2265.3167 | 629.9239 | 303.9023 | 540.0104 | 617.4042 | 493.1486 | 480.2337 | 553.0121 | 439.9035
2266.3167 | 623.8144 | 304.0916 | 541.5586 | 618.635 | 492.2289 | 480.3904 | 553.5701 | 440.1189
2267.3167 | 624.4441 | 304.307 | 545.2594 | 621.993 | 492.3928 | 480.9026 | 554.1851 | 440.3908
2268.3167 | 633.9046 | 304.4394 | 542.8786 | 623.604 | 493.5372 | 480.5173 | 554.5291 | 440.3304
2269.3167 | 632.1815 | 304.6021 | 544.5447 | 624.1014 | 493.3169 | 480.4657 | 555.0211 | 440.4469
2270.3167 | 630.7834 | 304.7791 | 541.5141 | 625.9959 | 493.8663 | 480.4387 | 555.5897 | 440.5322
2271.3167 | 632.3735 | 304.9542 | 540.621 | 629.3719 | 494.0429 | 480.4723 | 556.1823 | 440.6546
2272.3167 | 626.1633 | 305.1285 | 542.5028 | 626.6556 | 493.0865 | 480.4467 | 556.7795 | 440.7792
2273.3167 | 623.1466 | 305.3162 | 541.3289 | 622.1516 | 491.8732 | 480.4089 | 557.3635 | 440.9031
2274.3167 | 620.1518 | 305.4883 | 541.142 | 618.2243 | 491.6701 | 480.4025 | 557.9538 | 441.0295
2275.3167 | 620.0997 | 305.6771 | 547.2139 | 617.9416 | 489.761 | 480.4059 | 558.491 | 441.1916
2276.3167 | 624.4891 | 305.8482 | 548.311 | 621.4529 | 489.8312 | 480.5136 | 559.1052 | 441.2939
2277.3167 | 623.846 | 306.0177 | 543.7085 | 613.4936 | 489.0162 | 480.5842 | 559.7647 | 441.3897
2278.3167 | 622.6514 | 306.2025 | 543.7009 | 609.3485 | 487.4054 | 480.2964 | 560.4141 | 441.5247
2279.3167 | 624.8213 | 306.3803 | 542.7472 | 604.3162 | 485.1089 | 480.1483 | 561.072 | 441.6268
2280.3167 | 627.2757 | 306.5537 | 539.5728 | 603.3743 | 483.7675 | 479.99 | 561.728 | 441.7254
2281.3167 | 627.6073 | 306.7306 | 540.6366 | 606.35 | 485.9128 | 479.8881 | 562.358 | 441.8289
2282.3167 | 632.3207 | 306.9164 | 540.8828 | 608.5733 | 488.5843 | 479.7897 | 563.0131 | 442.0058
2283.3167 | 632.1272 | 307.1006 | 540.2007 | 607.8417 | 490.4476 | 479.7158 | 563.6998 | 442.1349
2284.3167 | 637.8774 | 307.2865 | 539.7897 | 609.9371 | 493.5787 | 479.6134 | 564.424 | 442.261
2285.3167 | 636.4808 | 307.4552 | 538.5895 | 616.2591 | 495.6748 | 479.4511 | 565.1308 | 442.4257
2286.3167 | 640.5933 | 307.6351 | 549.6489 | 622.1339 | 499.0412 | 479.494 | 565.795 | 442.5563
2287.3167 | 643.2117 | 307.8245 | 554.4731 | 627.854 | 503.3056 | 479.5939 | 566.5708 | 442.7019
2288.3167 | 635.8568 | 307.993 | 556.1038 | 632.8396 | 502.1815 | 479.7487 | 567.4105 | 442.854
2289.3167 | 630.2147 | 308.1647 | 559.602 | 635.8191 | 504.5329 | 479.8367 | 568.2302 | 442.9897
2290.3167 | 628.09 | 308.35 | 559.8446 | 641.4066 | 508.1837 | 479.8974 | 569.1123 | 443.113
2291.3167 | 625.5335 | 308.526 | 560.9102 | 644.4888 | 510.2427 | 479.9857 | 569.9171 | 443.2635
2292.3167 | 628.3126 | 308.6995 | 561.1749 | 646.0465 | 510.9865 | 480.131 | 570.5925 | 443.4164
2293.3167 | 632.8902 | 308.8634 | 569.575 | 643.0868 | 512.7964 | 480.1989 | 571.3129 | 443.5138
2294.3167 | 634.0893 | 309.0389 | 570.9725 | 640.0399 | 511.9316 | 480.4849 | 572.0272 | 443.6556
2295.3167 | 634.9558 | 309.2151 | 574.0529 | 644.208 | 511.6256 | 480.8222 | 572.6887 | 443.7653
2296.3167 | 635.5671 | 309.3942 | 577.1262 | 645.9073 | 512.0954 | 481.1869 | 573.3494 | 443.9059
2297.3167 | 641.0068 | 309.5726 | 578.5678 | 650.4319 | 511.9685 | 481.5498 | 574.1711 | 443.9998
2298.3167 | 643.6062 | 309.752 | 580.1751 | 650.2017 | 512.078 | 481.7723 | 574.9595 | 444.1317
2299.3167 | 642.8517 | 309.9366 | 579.8003 | 650.5044 | 512.7056 | 481.9691 | 575.7303 | 444.2456
2300.3167 | 649.0283 | 310.1079 | 579.5536 | 652.2685 | 517.2174 | 482.1965 | 576.3919 | 444.3674
2301.3167 | 652.4619 | 310.2917 | 578.259 | 648.1353 | 521.8002 | 482.4039 | 577.1228 | 444.5056
2302.3167 | 652.5108 | 310.4787 | 575.9999 | 645.5688 | 522.8863 | 482.5577 | 577.921 | 444.6592
2303.3167 | 646.9078 | 310.6513 | 576.2282 | 643.9003 | 519.8694 | 482.785 | 578.5206 | 444.7753
2304.3167 | 642.1272 | 310.8286 | 580.5407 | 652.1067 | 518.6151 | 483.04 | 579.0082 | 444.8614
2305.3167 | 641.5881 | 311.0063 | 582.5992 | 653.25 | 517.602 | 483.4121 | 579.5298 | 444.9614
2306.3167 | 642.2825 | 311.2032 | 582.6238 | 654.0501 | 516.8061 | 483.8528 | 580.1133 | 445.0768
2307.3167 | 646.6916 | 311.4418 | 582.0024 | 652.6648 | 518.9264 | 484.5295 | 580.8417 | 445.4234
2308.3167 | 649.19 | 311.5812 | 584.8773 | 659.3929 | 526.772 | 484.2692 | 581.1925 | 445.3214
2309.3167 | 648.349 | 311.7623 | 585.0625 | 662.6921 | 530.736 | 484.5686 | 581.6183 | 445.4459
2310.3167 | 649.1325 | 311.9843 | 584.9325 | 660.3606 | 531.0625 | 485.1801 | 582.475 | 445.6869
2311.3167 | 648.8114 | 312.1068 | 582.0447 | 661.0396 | 531.5635 | 485.0146 | 582.934 | 445.6869
2312.3167 | 648.2714 | 312.2877 | 583.9138 | 659.4892 | 531.6265 | 485.1456 | 583.3798 | 445.7952
2313.3167 | 651.4439 | 312.4669 | 584.0425 | 661.5184 | 533.614 | 485.602 | 583.8379 | 445.9505
2314.3167 | 650.2996 | 312.6462 | 585.7177 | 658.4944 | 532.356 | 486.2405 | 584.3899 | 446.059
2315.3167 | 646.3044 | 312.8538 | 587.9762 | 655.5084 | 530.1632 | 486.6609 | 585.0087 | 446.2216
2316.3167 | 643.929 | 313.038 | 587.8993 | 651.3484 | 528.141 | 487.0779 | 585.6036 | 446.358
2317.3167 | 642.8813 | 313.2283 | 585.8333 | 651.3781 | 525.3294 | 487.3723 | 586.0458 | 446.5093
2318.3167 | 641.1029 | 313.4237 | 581.2238 | 650.5132 | 525.4771 | 487.6694 | 586.4678 | 446.5908
2319.3167 | 639.206 | 313.6009 | 582.2476 | 650.1055 | 527.5858 | 487.9283 | 586.9005 | 446.7526
2320.3167 | 638.8128 | 313.7696 | 582.5853 | 650.3953 | 529.3344 | 488.1811 | 587.514 | 446.9081
2321.3167 | 638.638 | 313.9531 | 584.9358 | 648.9105 | 530.4942 | 488.4267 | 587.8687 | 447.0532
2322.3167 | 645.2178 | 314.1545 | 585.7478 | 654.9509 | 532.72 | 488.7554 | 588.4725 | 447.1671
2323.3167 | 648.3936 | 314.338 | 586.5352 | 660.0038 | 533.9165 | 488.9041 | 589.0686 | 447.3345
2324.3167 | 650.8231 | 314.543 | 586.5879 | 659.2925 | 534.5447 | 489.2323 | 589.4257 | 447.4867
2325.3167 | 658.1983 | 314.743 | 588.2062 | 658.8157 | 535.7937 | 489.5036 | 589.8576 | 447.6496
2326.3167 | 653.3545 | 314.9323 | 590.3903 | 663.3531 | 535.9402 | 489.7594 | 590.4002 | 447.7729
2327.3167 | 652.2966 | 315.1121 | 591.1796 | 665.3651 | 537.7423 | 489.8822 | 590.8655 | 447.8878
2328.3167 | 653.3894 | 315.3008 | 593.5723 | 668.6854 | 538.7058 | 490.1433 | 591.3651 | 448.0194
2329.3167 | 654.6836 | 315.4996 | 590.8241 | 672.0875 | 540.0882 | 490.3626 | 591.9152 | 448.1436
2330.3167 | 657.9122 | 315.6983 | 589.5056 | 674.2827 | 542.0411 | 490.5037 | 592.4673 | 448.2622
2331.3167 | 663.8149 | 315.8923 | 590.9549 | 678.2973 | 542.7369 | 490.7182 | 592.9179 | 448.4493
2332.3167 | 661.5271 | 316.0897 | 592.5096 | 678.1272 | 538.9937 | 491.1641 | 593.4437 | 448.6329
2333.3167 | 665.0584 | 316.2857 | 593.3412 | 678.7301 | 536.7389 | 491.5943 | 593.8872 | 448.7615
2334.3167 | 665.4743 | 316.4765 | 595.7748 | 679.6198 | 536.9088 | 492.1069 | 594.4865 | 448.9143
2335.3167 | 663.8717 | 316.6647 | 594.8208 | 677.0168 | 537.7683 | 492.4385 | 595.0495 | 449.0794
2336.3167 | 661.4879 | 316.8613 | 594.1084 | 675.4471 | 539.6938 | 492.7976 | 595.6702 | 449.2204
2337.3167 | 660.7128 | 317.0699 | 593.0823 | 672.9846 | 541.2241 | 493.4255 | 596.0823 | 449.3617
2338.3167 | 661.5639 | 317.2548 | 595.026 | 677.0129 | 542.7972 | 493.9945 | 596.5265 | 449.5221
2339.3167 | 658.4548 | 317.3917 | 595.0838 | 683.0171 | 544.1734 | 494.7925 | 596.8749 | 449.6067
2340.3167 | 657.9838 | 317.5998 | 594.2462 | 680.4904 | 543.9808 | 495.5709 | 597.1937 | 449.7402
2341.3167 | 661.919 | 317.8058 | 597.565 | 683.2936 | 544.2788 | 496.484 | 597.41 | 449.8979
2342.3167 | 661.8787 | 318.0162 | 598.4537 | 679.8041 | 544.5394 | 497.7716 | 597.5805 | 449.9989
2343.3167 | 659.9954 | 318.2149 | 599.4184 | 677.1025 | 543.3654 | 498.9477 | 597.6109 | 450.1657
2344.3167 | 658.5839 | 318.4202 | 598.9521 | 672.3608 | 545.1104 | 499.9901 | 597.9077 | 450.2714
2345.3167 | 652.7091 | 318.6199 | 599.8675 | 671.0884 | 544.1655 | 501.0556 | 597.9502 | 450.4029
2346.3167 | 653.5706 | 318.8338 | 602.876 | 681.821 | 540.7811 | 502.179 | 597.9189 | 450.5428
2347.3167 | 660.7743 | 319.0297 | 602.8933 | 687.9482 | 538.1499 | 503.1598 | 597.9654 | 450.694
2348.3167 | 671.6074 | 319.2229 | 607.4641 | 690.0049 | 544.8591 | 503.8952 | 598.0803 | 450.8355
2349.3167 | 670.1965 | 319.4316 | 615.8618 | 690.2559 | 544.8582 | 504.8923 | 598.1719 | 450.92
2350.3167 | 673.3637 | 319.6458 | 620.0058 | 689.8138 | 548.688 | 505.9196 | 598.2911 | 451.0388
2351.3167 | 669.1804 | 319.8372 | 620.5988 | 692.1632 | 548.5283 | 506.8852 | 598.4599 | 451.1885
2352.3167 | 674.8714 | 320.0436 | 620.8368 | 694.5906 | 546.7303 | 507.676 | 598.6237 | 451.3204
2353.3167 | 674.4347 | 320.2409 | 620.3258 | 690.9422 | 543.9013 | 508.5672 | 598.7982 | 451.4319
2354.3167 | 672.3166 | 320.4562 | 623.1074 | 692.4193 | 541.6386 | 509.1291 | 599.0738 | 451.5429
2355.3167 | 667.6934 | 320.662 | 622.2798 | 694.2227 | 539.1797 | 509.8148 | 599.2647 | 451.7085
2356.3167 | 664.1796 | 320.8564 | 619.0601 | 693.8286 | 536.2096 | 510.453 | 599.4966 | 451.874
2357.3167 | 663.2101 | 321.0799 | 616.4672 | 688.7018 | 537.0175 | 511.2032 | 599.7599 | 452.0424
2358.3167 | 667.7383 | 321.2692 | 620.04 | 689.5555 | 539.2071 | 511.7191 | 599.9943 | 452.1792
2359.3167 | 669.7023 | 321.4803 | 622.1764 | 686.7649 | 542.447 | 512.5361 | 600.223 | 452.3247
2360.3167 | 670.0743 | 321.6866 | 622.1967 | 686.8144 | 544.8272 | 513.468 | 600.5164 | 452.5064
2361.3167 | 672.2088 | 321.8941 | 625.0855 | 689.0791 | 544.2097 | 514.2914 | 600.8555 | 452.7194
2362.3167 | 681.7437 | 322.1046 | 624.2941 | 687.5394 | 549.2476 | 515.3065 | 601.1036 | 452.8409
2363.3167 | 687.9744 | 322.314 | 621.9354 | 683.8177 | 552.607 | 516.2528 | 601.5271 | 452.9734
2364.3167 | 690.969 | 322.5153 | 621.2429 | 681.7467 | 555.7004 | 517.3842 | 601.8028 | 453.1599
2365.3167 | 689.6144 | 322.7181 | 623.4966 | 684.0596 | 555.9425 | 518.6904 | 602.0933 | 453.358
2366.3167 | 685.7355 | 322.9264 | 622.2687 | 680.5689 | 554.0894 | 520.0223 | 602.3819 | 453.4918
2367.3167 | 687.4077 | 323.1329 | 622.2299 | 680.0829 | 555.7076 | 520.8746 | 602.6917 | 453.6149
2368.3167 | 684.8375 | 323.3429 | 616.9495 | 678.8679 | 556.0811 | 521.765 | 602.9715 | 453.7929
2369.3167 | 688.6925 | 323.5632 | 614.5985 | 677.342 | 553.7722 | 522.3949 | 603.2732 | 454.0097
2370.3167 | 683.595 | 323.7618 | 614.9465 | 681.696 | 555.2665 | 522.882 | 603.4309 | 454.1873
2371.3167 | 683.7213 | 323.9895 | 614.2689 | 682.4552 | 558.3417 | 523.5124 | 603.7219 | 454.3991
2372.3167 | 683.6101 | 324.209 | 612.4312 | 686.1984 | 560.7205 | 524.0305 | 604.065 | 454.5638
2373.3167 | 684.4021 | 324.4059 | 612.5677 | 690.0815 | 564.4179 | 524.4485 | 604.2835 | 454.7954
2374.3167 | 681.3378 | 324.6133 | 614.7561 | 688.5192 | 565.6444 | 525.0303 | 604.5974 | 454.9787
2375.3167 | 679.1885 | 324.8538 | 613.7494 | 688.9341 | 565.3052 | 525.9526 | 604.9291 | 455.3096
2376.3167 | 674.7132 | 325.0311 | 615.5835 | 688.9434 | 564.5088 | 526.2645 | 604.9719 | 455.3964
2377.3167 | 674.597 | 325.2485 | 615.2375 | 691.428 | 564.6628 | 526.9776 | 605.062 | 455.5797
2378.3167 | 673.2432 | 325.4596 | 613.9812 | 689.7926 | 564.8191 | 527.4624 | 605.211 | 455.722
2379.3167 | 672.4965 | 325.6756 | 613.8766 | 686.9565 | 563.2737 | 528.0135 | 605.3575 | 455.8708
2380.3167 | 671.7249 | 325.8971 | 607.2817 | 684.0196 | 563.8775 | 528.3705 | 605.433 | 455.9881
2381.3167 | 677.0118 | 326.1069 | 607.2721 | 680.3904 | 563.1096 | 528.7026 | 605.4095 | 456.1327
2382.3167 | 673.9846 | 326.3573 | 607.451 | 677.9143 | 562.4703 | 529.2673 | 605.618 | 456.4098
2383.3167 | 672 | 326.5557 | 608.3466 | 676.9218 | 559.7583 | 529.6057 | 605.6228 | 456.5545
2384.3167 | 671.6165 | 326.7663 | 607.0964 | 680.79 | 559.479 | 530.0266 | 605.5849 | 456.6657
2385.3167 | 671.8047 | 326.9783 | 609.4503 | 678.2054 | 558.9087 | 530.2843 | 605.6794 | 456.7941
2386.3167 | 672.458 | 327.1975 | 608.0749 | 676.1293 | 557.7405 | 530.6436 | 605.7601 | 456.9121
2387.3167 | 668.7053 | 327.4195 | 608.226 | 675.8507 | 557.5761 | 531.1064 | 605.9122 | 457.0523
2388.3167 | 669.0754 | 327.638 | 606.9772 | 674.8557 | 556.7557 | 531.2271 | 606.1091 | 457.1724
2389.3167 | 667.6813 | 327.854 | 606.191 | 674.0037 | 555.5709 | 531.3006 | 606.2634 | 457.3353
2390.3167 | 666.2713 | 328.0639 | 605.4828 | 676.9989 | 555.0214 | 531.4853 | 606.4155 | 457.5588
2391.3167 | 666.7029 | 328.2815 | 604.2045 | 677.9632 | 555.5545 | 531.838 | 606.6226 | 457.7695
2392.3167 | 665.3518 | 328.4976 | 604.0352 | 680.0106 | 555.6227 | 531.8727 | 606.8201 | 457.9782
2393.3167 | 665.3199 | 328.7507 | 605.5878 | 677.0313 | 555.706 | 532.3485 | 607.1619 | 458.2376
2394.3167 | 673.5431 | 329.1506 | 607.24 | 676.441 | 554.6143 | 533.6987 | 607.6549 | 458.8049
2395.3167 | 679.7322 | 329.1755 | 607.1406 | 674.4019 | 555.3684 | 533.0864 | 607.5718 | 458.7162
2396.3167 | 689.9012 | 329.3805 | 608.3867 | 677.57 | 553.8527 | 533.3116 | 607.7452 | 458.9275
2397.3167 | 694.5151 | 329.594 | 608.0299 | 673.2871 | 549.9747 | 533.5818 | 608.0151 | 459.106
2398.3167 | 695.5757 | 329.8208 | 612.6494 | 674.7052 | 549.0063 | 533.8903 | 608.3008 | 459.2758
2399.3167 | 694.5758 | 330.0425 | 611.9302 | 678.1627 | 548.4834 | 534.0958 | 608.5389 | 459.4278
2400.3167 | 694.7267 | 330.2525 | 609.366 | 674.6387 | 551.3574 | 534.3366 | 608.7868 | 459.6278
2401.3167 | 700.8233 | 330.484 | 618.7919 | 673.2172 | 554.071 | 534.4351 | 609.0638 | 459.8454
2402.3167 | 692.9538 | 330.7585 | 621.4548 | 670.2594 | 554.9646 | 534.8519 | 609.3469 | 460.0851
2403.3167 | 691.0788 | 330.936 | 618.6777 | 669.1417 | 557.2462 | 534.8816 | 609.5712 | 460.2727
2404.3167 | 687.5042 | 331.1539 | 614.533 | 668.7027 | 558.1195 | 535.0704 | 609.8611 | 460.4606
2405.3167 | 685.0138 | 331.371 | 610.4738 | 669.1217 | 557.7238 | 535.4987 | 610.0577 | 460.645
2406.3167 | 680.5593 | 331.5983 | 605.4354 | 666.464 | 558.1423 | 535.7238 | 610.2978 | 460.8607
2407.3167 | 680.2079 | 331.8224 | 599.6122 | 667.259 | 561.1908 | 535.7228 | 610.5464 | 461.0982
2408.3167 | 684.0494 | 332.0411 | 599.0244 | 665.1878 | 563.0287 | 535.6884 | 610.6868 | 461.3187
2409.3167 | 677.4435 | 332.3414 | 601.906 | 665.1171 | 561.4786 | 535.9809 | 610.9591 | 461.6134
2410.3167 | 678.8984 | 332.5024 | 604.3054 | 667.3426 | 560.2402 | 536.0528 | 611.1917 | 461.7567
2411.3167 | 677.2736 | 332.7271 | 606.5497 | 665.5623 | 559.9072 | 536.315 | 611.4592 | 461.9326
2412.3167 | 686.7613 | 332.9321 | 605.6406 | 664.297 | 559.6885 | 536.4915 | 611.5804 | 462.091
2413.3167 | 690.4385 | 333.2541 | 607.9567 | 668.9173 | 560.6345 | 537.3999 | 611.9417 | 462.46
2414.3167 | 686.456 | 333.4283 | 608.9595 | 670.5016 | 562.4041 | 537.2455 | 612.0993 | 462.4736
2415.3167 | 689.6501 | 333.6456 | 612.8762 | 675.6648 | 563.481 | 537.8172 | 612.3886 | 462.7945
2416.3167 | 689.8862 | 333.8339 | 616.0272 | 678.9411 | 564.8227 | 537.9862 | 612.4888 | 463.1595
2417.3167 | 687.8928 | 334.0594 | 616.6785 | 683.3992 | 565.2922 | 538.3041 | 612.7754 | 463.7447
2418.3167 | 688.2934 | 334.2973 | 619.0766 | 685.3701 | 567.0722 | 538.49 | 612.9371 | 464.2742
2419.3167 | 690.8145 | 334.5154 | 619.6351 | 688.7319 | 568.9439 | 538.898 | 613.1529 | 464.6669
2420.3167 | 689.8744 | 334.744 | 625.8537 | 696.4679 | 569.5553 | 539.2676 | 613.4275 | 464.9923
2421.3167 | 691.4689 | 335.0432 | 627.0838 | 699.871 | 567.7938 | 539.8144 | 613.838 | 465.4121
2422.3167 | 693.057 | 335.259 | 629.1536 | 702.7619 | 565.1104 | 540.1958 | 613.9877 | 465.6574
2423.3167 | 695.8017 | 335.4786 | 626.2286 | 703.1466 | 564.639 | 540.3844 | 614.2512 | 465.6378
2424.3167 | 696.5659 | 335.7102 | 627.7233 | 705.817 | 564.2258 | 540.4612 | 614.5322 | 465.7525
2425.3167 | 697.3395 | 335.9467 | 633.5757 | 709.6759 | 562.57 | 540.5639 | 614.9075 | 465.9449
2426.3167 | 700.2049 | 336.1842 | 635.0649 | 711.3596 | 560.3555 | 541.0268 | 615.1883 | 466.1408
2427.3167 | 699.5994 | 336.4091 | 633.064 | 708.5001 | 558.5563 | 541.5865 | 615.5384 | 466.2981
2428.3167 | 698.7402 | 336.6453 | 632.2503 | 708.7314 | 561.2575 | 542.1041 | 615.8793 | 466.6168
2429.3167 | 703.0167 | 336.8403 | 634.7664 | 712.8086 | 560.9335 | 542.4612 | 616.2082 | 466.8832
2430.3167 | 699.5116 | 337.082 | 634.8783 | 712.8358 | 559.6614 | 543.0731 | 616.5508 | 467.096
2431.3167 | 704.5376 | 337.3168 | 632.9375 | 706.4007 | 560.1223 | 543.5637 | 616.9834 | 467.3018
2432.3167 | 703.3572 | 337.5565 | 635.9034 | 709.3424 | 560.9257 | 543.8174 | 617.3619 | 467.5024
2433.3167 | 700.2198 | 337.7973 | 638.0487 | 707.5317 | 560.9834 | 544.7668 | 617.8014 | 467.8839
2434.3167 | 703.9868 | 338.5022 | 638.0299 | 708.0109 | 557.2317 | 550.5424 | 619.7101 | 470.1207
2435.3167 | 707.2354 | 338.2542 | 638.4635 | 703.9037 | 556.5304 | 545.9157 | 618.3285 | 468.1136
2436.3167 | 703.3877 | 338.4792 | 638.0525 | 699.5854 | 554.7532 | 546.2758 | 618.5581 | 468.3375
2437.3167 | 701.3394 | 338.7175 | 636.3721 | 699.1839 | 554.012 | 546.7218 | 618.9044 | 468.5654
2438.3167 | 697.8358 | 338.9808 | 635.7101 | 701.2567 | 553.469 | 547.4682 | 619.2639 | 468.88
2439.3167 | 696.7785 | 339.2104 | 637.3636 | 704.0534 | 552.5549 | 547.8386 | 619.6175 | 468.9663
2440.3167 | 695.0329 | 339.4388 | 638.8633 | 701.3743 | 554.6963 | 548.4226 | 619.8347 | 469.1181
2441.3167 | 696.9973 | 339.6891 | 638.4144 | 702.8686 | 553.4283 | 548.7603 | 620.1267 | 469.2892
2442.3167 | 697.6403 | 339.9462 | 637.4957 | 701.2068 | 553.0687 | 549.3938 | 620.4705 | 469.4032
2443.3167 | 696.2762 | 340.1824 | 634.2709 | 699.7977 | 554.2002 | 549.7658 | 620.647 | 469.5904
2444.3167 | 696.9807 | 340.4463 | 636.3172 | 699.5802 | 556.2315 | 550.4306 | 620.9524 | 469.7031
2445.3167 | 694.0593 | 340.7022 | 634.2249 | 703.4049 | 556.1093 | 550.4623 | 621.1953 | 469.7886
2446.3167 | 693.7987 | 340.9415 | 635.1568 | 702.1083 | 558.9202 | 550.8375 | 621.4825 | 469.9091
2447.3167 | 696.3598 | 341.1979 | 636.2588 | 702.6844 | 562.1331 | 551.2848 | 621.7122 | 470.0232
2448.3167 | 695.6635 | 341.4532 | 638.9241 | 705.6862 | 563.8327 | 551.5353 | 621.9881 | 470.1095
2449.3167 | 693.3886 | 341.6982 | 639.168 | 715.5193 | 561.7382 | 551.8671 | 622.2054 | 470.156
2450.3167 | 693.89 | 341.9599 | 640.4501 | 713.0091 | 560.0216 | 552.2837 | 622.4624 | 470.2787
2451.3167 | 701.3618 | 342.2086 | 639.4579 | 706.7765 | 561.8742 | 552.8678 | 622.7178 | 470.3929
2452.3167 | 700.2729 | 342.4749 | 640.5693 | 708.7081 | 561.028 | 553.1268 | 622.9178 | 470.4184
2453.3167 | 701.9334 | 342.7364 | 643.4499 | 712.1023 | 560.9246 | 553.5931 | 623.1126 | 470.4615
2454.3167 | 700.2345 | 342.9935 | 641.4533 | 708.979 | 563.0838 | 554.0582 | 623.4272 | 470.575
2455.3167 | 700.9602 | 343.2617 | 639.8433 | 709.7752 | 566.2242 | 554.3811 | 623.7252 | 470.7209
2456.3167 | 699.7666 | 343.5271 | 639.8764 | 707.2674 | 566.8479 | 554.8336 | 623.9731 | 470.8911
2457.3167 | 697.5355 | 343.8059 | 637.3638 | 706.098 | 566.5143 | 555.3004 | 624.0872 | 470.9067
2458.3167 | 697.2444 | 344.0697 | 635.6314 | 708.5806 | 565.1399 | 555.6327 | 624.3161 | 471.041
2459.3167 | 694.3424 | 344.3401 | 636.7963 | 714.2314 | 562.5944 | 555.9874 | 624.5125 | 471.2682
2460.3167 | 694.3581 | 344.6218 | 639.9271 | 716.7329 | 561.051 | 556.0549 | 624.67 | 471.3755
2461.3167 | 698.2466 | 344.8804 | 639.5449 | 715.4674 | 561.7814 | 556.6276 | 624.8762 | 471.535
2462.3167 | 695.1541 | 345.1555 | 638.3175 | 712.0852 | 561.3603 | 557.0937 | 625.1431 | 471.6093
2463.3167 | 696.2689 | 345.4203 | 635.2992 | 707.9547 | 562.2428 | 557.6817 | 625.3534 | 471.6346
2464.3167 | 694.9958 | 345.6934 | 632.9696 | 704.7291 | 564.4518 | 558.0704 | 625.5482 | 471.7155
2465.3167 | 695.9039 | 345.9666 | 632.7671 | 702.8672 | 565.2265 | 558.4196 | 625.7857 | 471.7465
2466.3167 | 694.0932 | 346.2474 | 632.3249 | 702.6172 | 566.4606 | 558.5563 | 625.9678 | 471.6745
2467.3167 | 691.3116 | 346.523 | 628.1755 | 702.4945 | 566.9664 | 558.9156 | 626.1099 | 471.7134
2468.3167 | 689.3264 | 346.7942 | 625.8313 | 701.622 | 565.7469 | 559.2115 | 626.265 | 471.7649
2469.3167 | 688.3013 | 347.0799 | 628.2931 | 704.3683 | 566.9491 | 559.2799 | 626.4099 | 471.8241
2470.3167 | 686.8448 | 347.3568 | 632.3225 | 702.3907 | 567.3038 | 559.8297 | 626.601 | 472.0094
2471.3167 | 690.5353 | 347.6506 | 633.9665 | 701.0674 | 565.4822 | 560.2418 | 626.7349 | 472.2125
2472.3167 | 694.7092 | 347.9154 | 633.5129 | 703.2717 | 564.1222 | 560.3344 | 626.8145 | 472.5454
2473.3167 | 695.8906 | 348.1946 | 631.1581 | 707.5454 | 561.087 | 560.7488 | 627.0861 | 472.7257
2474.3167 | 694.1021 | 348.4811 | 632.7066 | 709.6952 | 558.4193 | 561.3113 | 627.2839 | 472.9706
2475.3167 | 698.1932 | 348.7724 | 632.4051 | 707.0082 | 558.2483 | 561.6715 | 627.4202 | 472.9938
2476.3167 | 698.3404 | 349.0473 | 630.3218 | 705.9658 | 561.8405 | 561.8489 | 627.5725 | 473.2479
2477.3167 | 695.9145 | 349.3518 | 630.8427 | 709.769 | 564.3916 | 561.905 | 627.7069 | 473.3503
2478.3167 | 695.2917 | 349.6427 | 632.0638 | 707.2646 | 567.3542 | 562.236 | 627.8336 | 473.4163
2479.3167 | 696.0187 | 349.9283 | 633.4622 | 706.0537 | 565.7021 | 562.5692 | 627.911 | 473.5874
2480.3167 | 697.3369 | 350.2273 | 633.1873 | 703.7398 | 566.2682 | 562.9894 | 628.0744 | 473.7743
2481.3167 | 694.5272 | 350.5213 | 631.1385 | 702.1635 | 567.8207 | 562.9498 | 628.1874 | 473.9405
2482.3167 | 693.099 | 350.8306 | 628.4515 | 702.7805 | 570.4389 | 563.3135 | 628.359 | 474.0802
2483.3167 | 690.5191 | 351.1206 | 626.7316 | 705.2257 | 570.1478 | 563.604 | 628.4775 | 474.2586
2484.3167 | 690.9248 | 351.4109 | 628.0469 | 704.9965 | 569.8982 | 563.984 | 628.4881 | 474.391
2485.3167 | 689.0778 | 351.7035 | 627.4688 | 707.0823 | 571.0435 | 564.4239 | 628.5877 | 474.5623
2486.3167 | 687.4599 | 351.9979 | 630.1168 | 704.1111 | 571.9318 | 564.4702 | 628.7345 | 474.6882
2487.3167 | 692.9502 | 352.3007 | 632.3312 | 703.6729 | 573.787 | 564.8847 | 628.8076 | 474.8065
2488.3167 | 693.7791 | 352.5936 | 632.6131 | 708.8637 | 574.3678 | 564.9376 | 628.9149 | 474.9472
2489.3167 | 695.821 | 352.9048 | 631.9724 | 709.3198 | 571.884 | 565.3219 | 629.0122 | 475.1046
2490.3167 | 696.1154 | 353.2077 | 632.9534 | 709.2571 | 568.8128 | 565.7653 | 629.0944 | 475.2533
2491.3167 | 696.4193 | 353.5212 | 634.7878 | 714.2441 | 565.556 | 565.8871 | 629.2318 | 475.3791
2492.3167 | 699.1071 | 353.8203 | 634.2788 | 716.606 | 563.6149 | 566.4226 | 629.3279 | 475.5358
2493.3167 | 701.2421 | 354.1234 | 635.4556 | 718.5418 | 563.0411 | 566.602 | 629.4104 | 475.6295
2494.3167 | 701.2675 | 354.4333 | 636.8582 | 722.8533 | 561.0311 | 566.9211 | 629.4955 | 475.7727
2495.3167 | 700.3373 | 354.7342 | 638.6471 | 724.1635 | 558.5485 | 567.3561 | 629.6643 | 475.8656
2496.3167 | 700.4217 | 355.0516 | 640.5179 | 723.5088 | 558.3426 | 567.9544 | 629.8624 | 475.9313
2497.3167 | 705.0166 | 355.3704 | 644.9224 | 722.1877 | 556.5805 | 568.5296 | 630.093 | 475.9912
2498.3167 | 705.0237 | 355.6832 | 642.8284 | 721.529 | 554.2046 | 568.9341 | 630.257 | 476.0701
2499.3167 | 702.7537 | 355.9953 | 643.6465 | 718.6339 | 555.6807 | 569.5606 | 630.461 | 476.1527
2500.3167 | 701.9071 | 356.3208 | 641.4856 | 717.1008 | 558.4419 | 569.2649 | 630.7155 | 476.1936
2501.3167 | 700.3518 | 356.6519 | 641.8288 | 718.4369 | 561.1234 | 569.6918 | 630.9811 | 476.2145
2502.3167 | 699.531 | 356.9804 | 645.0254 | 716.0092 | 563.3816 | 570.2138 | 631.1999 | 476.3038
2503.3167 | 700.2894 | 357.3222 | 644.1267 | 717.5545 | 563.7772 | 570.7607 | 631.4986 | 476.4107
2504.3167 | 699.1089 | 357.6658 | 643.6823 | 721.4287 | 563.7614 | 571.1874 | 631.8236 | 476.4625
2505.3167 | 704.8869 | 358.0003 | 646.029 | 721.634 | 566.9978 | 571.719 | 632.0061 | 476.5551
2506.3167 | 706.4323 | 358.3493 | 647.7045 | 718.3914 | 569.1361 | 572.1291 | 632.2807 | 476.5825
2507.3167 | 704.8932 | 358.709 | 647.8228 | 713.8921 | 570.8554 | 572.6587 | 632.5807 | 476.6816
2508.3167 | 705.3488 | 359.0623 | 644.7228 | 713.6525 | 569.1962 | 573.1353 | 632.7652 | 476.7441
2509.3167 | 706.3879 | 359.4019 | 646.1732 | 708.9557 | 571.1974 | 573.7532 | 633.079 | 476.8006
2510.3167 | 708.5499 | 359.7454 | 645.0274 | 706.8084 | 570.2937 | 574.0452 | 633.3123 | 476.8366
2511.3167 | 705.3892 | 360.0977 | 645.8182 | 705.9596 | 571.0413 | 574.6435 | 633.6075 | 476.8998
2512.3167 | 706.2187 | 360.4652 | 644.7958 | 704.7871 | 572.0363 | 575.0212 | 633.7789 | 476.9335
2513.3167 | 703.5996 | 360.8276 | 642.9893 | 700.255 | 572.5551 | 575.5106 | 634.0612 | 477.0102
2514.3167 | 699.4816 | 361.1962 | 643.9388 | 695.8808 | 571.9698 | 575.7483 | 634.3066 | 477.0605
2515.3167 | 695.4072 | 361.5763 | 642.17 | 690.6827 | 571.1477 | 576.287 | 634.5388 | 477.1139
2516.3167 | 694.6679 | 361.9638 | 645.2789 | 688.8839 | 568.4936 | 576.7968 | 634.7474 | 477.156
2517.3167 | 693.9876 | 362.342 | 646.5242 | 694.4216 | 568.104 | 577.2169 | 634.9478 | 477.1702
2518.3167 | 695.8267 | 362.7066 | 645.7707 | 696.5101 | 568.5961 | 577.6634 | 635.0848 | 477.2367
2519.3167 | 698.8764 | 363.0651 | 645.2622 | 692.6225 | 566.4819 | 578.1885 | 635.2707 | 477.3105
2520.3167 | 702.0979 | 363.4596 | 645.9491 | 691.394 | 562.6719 | 578.6027 | 635.4584 | 477.3075
2521.3167 | 701.784 | 363.8568 | 646.8386 | 693.9633 | 559.9081 | 579.3057 | 635.6816 | 477.3556
2522.3167 | 701.2087 | 364.2184 | 646.4311 | 694.448 | 558.9033 | 579.5678 | 635.8928 | 477.4055
2523.3167 | 707.1035 | 364.5957 | 646.9987 | 697.4048 | 558.4022 | 580.006 | 636.0794 | 477.4219
2524.3167 | 706.4599 | 365.0029 | 646.6735 | 694.8693 | 560.5696 | 580.5132 | 636.3077 | 477.4708
2525.3167 | 703.3874 | 365.4032 | 645.6999 | 691.912 | 560.3183 | 580.8809 | 636.5539 | 477.5001
2526.3167 | 701.5964 | 365.8306 | 645.0353 | 691.6571 | 559.5583 | 581.2227 | 636.7305 | 477.49
2527.3167 | 700.5772 | 366.2308 | 646.0549 | 691.4755 | 559.1697 | 581.8383 | 636.9521 | 477.5233
2528.3167 | 695.8865 | 366.6242 | 647.8303 | 689.5721 | 560.1332 | 582.2373 | 637.0748 | 477.5484
2529.3167 | 692.5947 | 367.0574 | 652.252 | 688.6421 | 558.6629 | 583.2961 | 637.2745 | 477.756
2530.3167 | 691.9991 | 367.4431 | 656.0116 | 693.6799 | 556.8654 | 583.1885 | 637.4289 | 477.6523
2531.3167 | 698.7578 | 367.8865 | 653.8586 | 697.6279 | 557.2448 | 583.7935 | 637.5801 | 477.7
2532.3167 | 700.9824 | 368.3034 | 652.4181 | 696.986 | 559.6455 | 583.8686 | 637.7207 | 477.7363
2533.3167 | 702.2121 | 368.7305 | 654.7599 | 699.7521 | 561.2171 | 584.5117 | 637.9877 | 477.8053
2534.3167 | 702.7513 | 369.17 | 654.7688 | 704.7053 | 559.7531 | 584.7268 | 638.147 | 477.8739
2535.3167 | 705.8764 | 369.609 | 653.8602 | 704.4561 | 563.6887 | 585.2395 | 638.2405 | 477.8781
2536.3167 | 704.2184 | 370.1042 | 653.3272 | 700.857 | 564.3682 | 585.1065 | 638.427 | 477.9327
2537.3167 | 703.3545 | 370.5658 | 647.7397 | 700.6895 | 565.6317 | 585.05 | 638.5131 | 477.8934
2538.3167 | 701.7843 | 371.021 | 647.11 | 704.0602 | 567.8332 | 585.1292 | 638.7563 | 477.9158
2539.3167 | 700.0062 | 371.481 | 646.9614 | 705.1786 | 570.055 | 585.4687 | 638.8698 | 477.938
2540.3167 | 699.6887 | 371.9585 | 645.927 | 703.7738 | 573.6807 | 585.896 | 638.9968 | 477.9929
2541.3167 | 703.8038 | 372.444 | 643.5008 | 701.5155 | 577.3115 | 585.9532 | 639.2232 | 478.0131
2542.3167 | 703.8451 | 372.9763 | 642.971 | 699.2389 | 579.4768 | 586.3789 | 639.3969 | 478.0603
2543.3167 | 701.8579 | 373.4818 | 639.4417 | 696.8331 | 578.7236 | 586.5503 | 639.67 | 478.123
2544.3167 | 697.0922 | 373.9823 | 638.1633 | 695.461 | 576.0555 | 586.4294 | 639.7841 | 478.0916
2545.3167 | 697.5786 | 374.5249 | 640.9085 | 694.4057 | 575.608 | 586.6704 | 639.8702 | 478.1003
2546.3167 | 698.9678 | 375.0597 | 641.9593 | 695.2005 | 579.341 | 586.9849 | 639.9834 | 478.0915
2547.3167 | 701.8946 | 375.6036 | 643.4489 | 699.8061 | 581.0836 | 587.0123 | 640.1781 | 478.13
2548.3167 | 703.5763 | 376.1531 | 644.8917 | 703.2649 | 579.6846 | 587.4369 | 640.4275 | 478.1778
2549.3167 | 700.571 | 376.7344 | 643.4039 | 700.9416 | 578.9909 | 587.567 | 640.6613 | 478.2393
2550.3167 | 700.5326 | 377.3032 | 638.1585 | 698.5382 | 578.8987 | 587.7246 | 640.7656 | 478.247
2551.3167 | 700.3173 | 377.9365 | 635.1117 | 694.3283 | 578.0682 | 588.2452 | 640.9964 | 478.3874
2552.3167 | 697.107 | 378.5475 | 633.5798 | 694.4552 | 577.5419 | 587.9755 | 641.0125 | 478.3255
2553.3167 | 696.497 | 379.2137 | 631.9237 | 696.0066 | 576.5109 | 588.0162 | 641.1748 | 478.3763
2554.3167 | 695.5271 | 379.9001 | 631.8858 | 695.6885 | 575.4964 | 588.4285 | 641.3186 | 478.4718
2555.3167 | 695.1576 | 380.6689 | 634.0232 | 698.106 | 572.9231 | 589.6226 | 641.832 | 478.9313
2556.3167 | 695.2862 | 381.3955 | 633.7186 | 696.4121 | 572.6569 | 588.8648 | 641.5277 | 478.5361
2557.3167 | 702.1173 | 382.1723 | 635.9794 | 698.1786 | 572.0215 | 588.8492 | 641.6926 | 478.5763
2558.3167 | 710.2175 | 383.08 | 637.5428 | 694.1416 | 572.1005 | 589.3209 | 641.7508 | 478.6495
2559.3167 | 712.6867 | 383.7843 | 640.7244 | 697.1497 | 570.4132 | 589.578 | 642.0662 | 478.6329
2560.3167 | 708.1247 | 384.6242 | 640.6441 | 697.5296 | 570.5548 | 589.9263 | 642.2763 | 478.6811
2561.3167 | 710.6148 | 385.4746 | 640.034 | 699.2561 | 569.8145 | 590.3248 | 642.4184 | 478.7031
2562.3167 | 709.2575 | 386.3452 | 640.0608 | 697.4984 | 568.9448 | 590.4286 | 642.5161 | 478.7394
2563.3167 | 705.4634 | 387.156 | 641.1565 | 698.4468 | 568.3437 | 590.797 | 642.7014 | 478.7837
2564.3167 | 704.481 | 387.9478 | 646.7053 | 699.9048 | 566.999 | 591.0588 | 642.8997 | 478.8587
2565.3167 | 711.0347 | 388.701 | 649.1188 | 705.8862 | 566.0105 | 591.6643 | 643.064 | 478.9331
2566.3167 | 708.9922 | 389.3891 | 650.0483 | 699.5224 | 565.2556 | 591.9024 | 643.2169 | 478.9956
2567.3167 | 708.0792 | 390.0182 | 652.5855 | 700.639 | 564.5813 | 592.1624 | 643.4055 | 479.0587
2568.3167 | 707.7523 | 390.6745 | 656.0917 | 702.1985 | 563.2314 | 592.4898 | 643.5475 | 479.0936
2569.3167 | 708.984 | 391.2285 | 659.3507 | 701.7116 | 560.6202 | 593.0464 | 643.7209 | 479.172
2570.3167 | 716.3495 | 391.7652 | 662.7118 | 706.5815 | 559.7449 | 593.3951 | 643.8618 | 479.2278
2571.3167 | 718.1682 | 392.2898 | 663.7257 | 703.9989 | 557.8259 | 594.0454 | 643.9956 | 479.3161
2572.3167 | 717.9835 | 392.9604 | 663.8549 | 704.5888 | 561.3832 | 594.239 | 644.1092 | 479.3732
2573.3167 | 718.931 | 393.5815 | 664.9145 | 701.2633 | 562.6344 | 594.6469 | 644.247 | 479.4252
2574.3167 | 720.3141 | 394.1501 | 667.3321 | 705.7119 | 564.1195 | 594.961 | 644.4232 | 479.4827
2575.3167 | 722.5534 | 394.68 | 666.7062 | 703.3552 | 564.5024 | 595.3949 | 644.5533 | 479.5483
2576.3167 | 721.1984 | 395.1557 | 660.133 | 700.0375 | 566.3381 | 595.6045 | 644.632 | 479.6352
2577.3167 | 721.2304 | 395.7127 | 660.7981 | 701.5456 | 568.9189 | 595.8004 | 644.7475 | 479.6677
2578.3167 | 717.6302 | 396.1066 | 664.2411 | 705.2112 | 570.2937 | 595.7509 | 644.939 | 479.7232
2579.3167 | 715.8535 | 396.5368 | 666.8304 | 705.9359 | 572.8183 | 595.9484 | 645.0902 | 479.8173
2580.3167 | 714.6475 | 396.9548 | 664.747 | 707.901 | 575.3858 | 596.2247 | 645.1511 | 479.9033
2581.3167 | 714.6193 | 397.3692 | 662.918 | 709.7911 | 574.9827 | 596.577 | 645.3142 | 479.9828
2582.3167 | 716.3682 | 397.7821 | 665.0586 | 708.829 | 572.9001 | 596.7947 | 645.4717 | 480.028
2583.3167 | 717.4979 | 398.1864 | 666.8408 | 711.664 | 570.4101 | 597.2395 | 645.6247 | 480.0903
2584.3167 | 720.8779 | 398.6421 | 669.0355 | 710.6392 | 574.7419 | 597.7052 | 645.7338 | 480.1558
2585.3167 | 718.1865 | 399.0549 | 667.025 | 706.1317 | 577.2895 | 597.8933 | 645.8667 | 480.2287
2586.3167 | 717.5649 | 399.5008 | 663.2921 | 704.9716 | 576.4979 | 598.272 | 645.9073 | 480.2488
2587.3167 | 711.4739 | 399.9458 | 656.911 | 701.5107 | 574.4909 | 598.4369 | 646.0184 | 480.2783
2588.3167 | 708.0565 | 400.4448 | 655.7817 | 698.2275 | 572.9874 | 598.4689 | 646.0829 | 480.3575
2589.3167 | 706.5162 | 401.009 | 654.5772 | 698.6027 | 571.676 | 598.5631 | 646.1113 | 480.4178
2590.3167 | 706.5297 | 401.5488 | 656.5422 | 700.3912 | 571.9366 | 598.8303 | 646.1577 | 480.4831
2591.3167 | 708.6938 | 402.0626 | 663.0363 | 700.2115 | 571.4284 | 599.4419 | 646.3378 | 480.5605
2592.3167 | 716.5298 | 402.6793 | 669.0693 | 710.1989 | 568.6576 | 599.8242 | 646.5953 | 480.6356
2593.3167 | 727.8676 | 403.8133 | 675.9486 | 720.3601 | 565.858 | 602.7231 | 647.6371 | 481.7987
2594.3167 | 728.9209 | 404.3482 | 678.0046 | 719.471 | 564.9142 | 600.4639 | 647.0073 | 480.8182
2595.3167 | 730.9741 | 405.1729 | 677.318 | 724.6748 | 564.0622 | 601.084 | 647.1704 | 480.9256
2596.3167 | 727.0043 | 406.0013 | 675.0298 | 724.409 | 563.6388 | 601.5627 | 647.2787 | 481.0077
2597.3167 | 726.3144 | 406.8833 | 670.9943 | 717.9878 | 564.2718 | 601.7424 | 647.4318 | 481.074
2598.3167 | 722.2988 | 407.7405 | 669.9428 | 714.6669 | 568.4229 | 602.0117 | 647.5175 | 481.1623
2599.3167 | 717.7685 | 408.7684 | 668.7816 | 710.1291 | 569.3919 | 602.245 | 647.5507 | 481.2463
2600.3167 | 715.3126 | 409.8048 | 667.8009 | 704.7179 | 570.4794 | 602.615 | 647.6731 | 481.3245
2601.3167 | 711.8288 | 410.8138 | 666.8167 | 705.8205 | 569.5572 | 603.0622 | 647.7452 | 481.4177
2602.3167 | 712.2618 | 411.8176 | 665.1334 | 704.6811 | 571.1216 | 603.271 | 647.7742 | 481.4999
2603.3167 | 711.5754 | 412.7647 | 665.5026 | 702.6274 | 572.1213 | 603.6119 | 647.747 | 481.5901
2604.3167 | 714.1405 | 413.6766 | 667.2151 | 706.8538 | 575.2724 | 603.9684 | 647.8906 | 481.6904
2605.3167 | 713.7513 | 414.8457 | 668.7422 | 708.6904 | 573.1625 | 605.1611 | 648.3156 | 482.0873
2606.3167 | 720.4511 | 415.4689 | 671.9873 | 711.8511 | 572.0728 | 604.9354 | 648.1705 | 481.8914
2607.3167 | 721.8397 | 416.3563 | 669.9675 | 709.0852 | 573.3918 | 605.4255 | 648.3364 | 482.0872
2608.3167 | 718.5293 | 416.8536 | 665.3118 | 707.4912 | 574.2994 | 605.7089 | 648.321 | 482.1379
2609.3167 | 716.9489 | 417.3961 | 662.4066 | 704.9996 | 577.0646 | 605.7785 | 648.384 | 482.2227
2610.3167 | 714.5927 | 417.8741 | 661.0782 | 703.1966 | 578.431 | 605.965 | 648.4301 | 482.3273
2611.3167 | 714.4505 | 418.3388 | 658.4936 | 701.7807 | 577.785 | 606.2665 | 648.437 | 482.4138
2612.3167 | 713.8873 | 418.0257 | 655.7406 | 702.1773 | 577.3894 | 606.3141 | 648.5526 | 482.5726
2613.3167 | 716.6478 | 419.5212 | 656.1912 | 700.7304 | 579.1458 | 606.4272 | 648.5908 | 482.6289
2614.3167 | 713.1446 | 419.8018 | 655.1965 | 707.8597 | 577.6805 | 606.6648 | 648.6733 | 482.743
2615.3167 | 708.903 | 420.06 | 656.9718 | 706.1284 | 576.1903 | 606.8461 | 648.7722 | 482.8465
2616.3167 | 706.6772 | 420.2653 | 658.5361 | 704.3823 | 574.1104 | 607.1636 | 648.7755 | 482.9304
2617.3167 | 704.3155 | 420.4167 | 659.4933 | 701.1381 | 572.7159 | 607.5491 | 648.8759 | 483.0286
2618.3167 | 704.549 | 420.5786 | 660.6994 | 699.9747 | 571.9556 | 607.6156 | 648.9809 | 483.1227
2619.3167 | 714.4074 | 420.8198 | 660.6893 | 701.0261 | 572.7179 | 607.7782 | 649.0928 | 483.2581
2620.3167 | 711.1483 | 420.9532 | 663.0806 | 702.784 | 570.8207 | 608.0658 | 649.2369 | 483.3717
2621.3167 | 714.47 | 421.1176 | 666.0512 | 702.3063 | 570.1912 | 608.4011 | 649.3462 | 483.4947
2622.3167 | 717.6357 | 420.874 | 666.5401 | 704.5753 | 570.2422 | 608.7877 | 649.4673 | 483.6206
2623.3167 | 725.8801 | 419.3309 | 668.8836 | 713.1787 | 567.9757 | 609.1 | 649.5987 | 483.7221
2624.3167 | 727.7787 | 419.1347 | 670.763 | 716.2204 | 568.2984 | 609.4633 | 649.7512 | 483.84
2625.3167 | 726.9007 | 419.3926 | 668.0173 | 714.3073 | 566.473 | 609.732 | 649.8623 | 483.9508
2626.3167 | 727.9369 | 420.1985 | 667.9409 | 713.9647 | 564.5496 | 609.9539 | 650.0103 | 484.0752
2627.3167 | 731.2839 | 419.2082 | 670.7958 | 715.8411 | 563.1216 | 610.3194 | 650.2093 | 484.213
2628.3167 | 733.125 | 419.5106 | 674.2759 | 714.5914 | 562.8732 | 610.6561 | 650.3589 | 484.3227
2629.3167 | 736.649 | 415.9895 | 676.3733 | 713.0255 | 562.8966 | 610.9786 | 650.4774 | 484.4195
2630.3167 | 736.9875 | 415.5652 | 671.5895 | 711.8941 | 562.0818 | 611.32 | 650.6015 | 484.5192
2631.3167 | 735.5567 | 416.8376 | 670.5736 | 712.4744 | 561.8838 | 611.4717 | 650.7446 | 484.6154
2632.3167 | 736.0817 | 416.6195 | 668.7714 | 717.9514 | 561.3422 | 611.9749 | 650.8446 | 484.752
2633.3167 | 735.2722 | 417.3121 | 665.9375 | 717.0098 | 562.1282 | 612.3085 | 650.8874 | 484.8796
2634.3167 | 734.0406 | 417.8336 | 667.5419 | 714.522 | 571.6596 | 612.4968 | 651.016 | 485.0181
2635.3167 | 731.7744 | 416.0227 | 665.7464 | 714.0984 | 573.1231 | 612.5473 | 651.0675 | 485.1031
2636.3167 | 732.2139 | 414.5228 | 664.5617 | 714.2323 | 572.5013 | 612.9378 | 651.1671 | 485.2364
2637.3167 | 734.0008 | 415.7898 | 666.5856 | 714.2041 | 572.8857 | 613.3474 | 651.3701 | 485.421
2638.3167 | 732.9677 | 422.5668 | 664.7349 | 713.8094 | 572.5903 | 613.3279 | 651.3959 | 485.4752
2639.3167 | 730.211 | 424.6415 | 663.886 | 711.9647 | 571.9868 | 613.3215 | 651.4308 | 485.5612
2640.3167 | 727.4937 | 424.749 | 661.6874 | 714.0798 | 575.3175 | 613.7402 | 651.4964 | 485.697
2641.3167 | 726.4362 | 424.8551 | 659.323 | 711.7986 | 576.3811 | 613.9959 | 651.5554 | 485.8419
2642.3167 | 725.2181 | 424.9686 | 659.0479 | 713.5972 | 574.8346 | 614.2566 | 651.6254 | 485.9685
2643.3167 | 725.3059 | 425.1266 | 658.8265 | 714.1015 | 573.8036 | 614.6137 | 651.7995 | 486.1637
2644.3167 | 733.1196 | 425.2336 | 659.2064 | 710.509 | 576.9465 | 614.5851 | 651.8855 | 486.2179
2645.3167 | 731.039 | 425.3661 | 658.3692 | 708.1823 | 579.7502 | 614.6852 | 651.8823 | 486.3399
2646.3167 | 727.5365 | 425.5094 | 658.9223 | 708.2029 | 580.5898 | 615.4225 | 652.1272 | 486.7132
2647.3167 | 726.8589 | 425.6456 | 659.7826 | 712.3386 | 582.2657 | 615.4791 | 652.214 | 486.6646
2648.3167 | 729.3546 | 425.7824 | 660.2431 | 707.6154 | 578.7498 | 615.9527 | 652.2675 | 486.7816
2649.3167 | 728.8478 | 425.9194 | 658.7339 | 708.3975 | 578.1603 | 616.2117 | 652.3147 | 486.9019
2650.3167 | 728.2254 | 426.0695 | 660.9873 | 709.6653 | 579.1616 | 616.2904 | 652.4128 | 487.0262
2651.3167 | 728.0436 | 426.2124 | 665.9277 | 715.3832 | 578.4239 | 616.8148 | 652.6252 | 487.1355
2652.3167 | 729.7649 | 426.3576 | 663.4362 | 716.4271 | 576.375 | 617.4225 | 652.8727 | 487.3332
2653.3167 | 734.875 | 426.4932 | 668.0375 | 718.6752 | 575.6942 | 617.5048 | 652.9944 | 487.4706
2654.3167 | 735.1807 | 426.6222 | 667.8314 | 721.0153 | 593.6638 | 617.9325 | 653.1831 | 487.6286
2655.3167 | 738.2274 | 426.8064 | 670.8492 | 721.9807 | 606.1951 | 618.5406 | 653.4041 | 487.887
2656.3167 | 736.0211 | 426.9044 | 667.2524 | 720.047 | 610.4697 | 618.8963 | 653.4695 | 487.9454
2657.3167 | 732.6148 | 427.0326 | 664.9638 | 718.976 | 608.0146 | 619.2332 | 653.5879 | 488.0836
2658.3167 | 733.6294 | 427.1666 | 662.3873 | 718.7756 | 603.6687 | 619.3965 | 653.6023 | 488.2394
2659.3167 | 728.833 | 427.3104 | 660.3319 | 712.9059 | 600.3622 | 619.7111 | 653.6787 | 488.3899
2660.3167 | 729.0071 | 427.434 | 659.6495 | 713.7636 | 596.101 | 619.8391 | 653.7644 | 488.5405
2661.3167 | 728.5677 | 427.5537 | 662.0892 | 713.1682 | 594.3105 | 620.3631 | 653.917 | 488.6751
2662.3167 | 728.8657 | 427.6701 | 662.4677 | 716.9191 | 592.0222 | 620.4673 | 654.0759 | 488.8432
2663.3167 | 727.6236 | 427.7931 | 666.3151 | 721.3648 | 589.258 | 621.0366 | 654.2761 | 488.9882
2664.3167 | 733.7146 | 427.911 | 666.2306 | 719.7305 | 585.3359 | 621.6634 | 654.4224 | 489.182
2665.3167 | 734.0733 | 428.031 | 670.6335 | 727.0035 | 582.5542 | 622.0156 | 654.545 | 489.346
2666.3167 | 733.401 | 428.4286 | 668.3325 | 722.9074 | 580.0526 | 623.8987 | 655.3102 | 490.061
2667.3167 | 732.4589 | 428.2508 | 667.6049 | 718.6721 | 581.2675 | 622.4948 | 654.7785 | 489.6383
2668.3167 | 734.2323 | 428.365 | 668.7456 | 714.3565 | 579.1249 | 623.071 | 654.9285 | 489.8391
2669.3167 | 733.3837 | 428.4739 | 667.5076 | 714.5441 | 576.8369 | 623.4095 | 655.0057 | 490.0067
2670.3167 | 729.8194 | 428.5801 | 667.6386 | 713.9995 | 573.8073 | 623.7038 | 655.1022 | 490.1587
2671.3167 | 724.4954 | 428.6812 | 665.7711 | 713.9004 | 571.7498 | 623.954 | 655.1649 | 490.3289
2672.3167 | 718.7172 | 428.7913 | 663.1229 | 710.7986 | 570.3267 | 624.1324 | 655.1627 | 490.4826
2673.3167 | 714.8052 | 428.8888 | 663.4841 | 714.175 | 568.5698 | 624.4029 | 655.3238 | 490.639
2674.3167 | 713.8103 | 428.9922 | 662.1467 | 715.7319 | 568.0217 | 624.4572 | 655.4198 | 490.7914
2675.3167 | 711.7965 | 429.0919 | 661.6567 | 710.3102 | 567.6491 | 624.8396 | 655.461 | 490.9593
2676.3167 | 713.8082 | 429.2476 | 659.1021 | 709.4832 | 568.0359 | 625.3339 | 655.5859 | 491.239
2677.3167 | 709.4228 | 429.2823 | 657.668 | 708.0569 | 568.4079 | 625.4245 | 655.5726 | 491.3175
2678.3167 | 708.0826 | 429.3659 | 656.8863 | 710.2578 | 567.542 | 625.6015 | 655.6267 | 491.4817
2679.3167 | 709.1476 | 429.4516 | 657.5818 | 707.6283 | 569.9224 | 625.7738 | 655.6948 | 491.6475
2680.3167 | 712.1449 | 429.5414 | 657.104 | 707.8917 | 571.8857 | 626.0652 | 655.7023 | 491.8328
2681.3167 | 716.1675 | 429.6289 | 653.6863 | 705.6256 | 573.6449 | 626.2318 | 655.8034 | 492.0168
2682.3167 | 719.6675 | 429.7227 | 652.5044 | 703.4907 | 574.8622 | 626.1828 | 655.913 | 492.1994
2683.3167 | 719.6211 | 429.8054 | 651.1383 | 699.5606 | 577.7191 | 626.1934 | 655.9593 | 492.378
2684.3167 | 717.1727 | 429.8741 | 648.6334 | 700.355 | 577.5072 | 626.2452 | 656.0899 | 492.5697
2685.3167 | 716.5466 | 429.9588 | 649.2466 | 698.3656 | 575.9115 | 626.2986 | 656.132 | 492.7387
2686.3167 | 722.5438 | 430.0331 | 649.1289 | 702.0685 | 576.03 | 626.3779 | 656.2567 | 492.9212
2687.3167 | 726.7662 | 430.1148 | 647.5438 | 703.1343 | 573.9492 | 626.454 | 656.3727 | 493.0877
2688.3167 | 726.5474 | 430.1899 | 647.1549 | 703.2503 | 575.2269 | 626.5999 | 656.4453 | 493.2808
2689.3167 | 724.0168 | 430.2624 | 646.2438 | 699.5701 | 575.1824 | 626.4565 | 656.4983 | 493.4407
2690.3167 | 722.6997 | 430.3504 | 645.9095 | 697.2061 | 575.3941 | 626.5439 | 656.5266 | 493.6081
2691.3167 | 719.6153 | 430.4177 | 644.3373 | 696.4752 | 576.0867 | 626.6677 | 656.5586 | 493.7988
2692.3167 | 722.8043 | 430.5728 | 644.5157 | 693.1244 | 577.384 | 627.0699 | 656.7582 | 494.1983
2693.3167 | 721.6561 | 430.5756 | 644.7102 | 698.87 | 578.3161 | 626.7132 | 656.7217 | 494.1868
2694.3167 | 726.0082 | 430.668 | 646.2633 | 705.2798 | 577.8027 | 626.7415 | 656.9418 | 494.389
2695.3167 | 729.9391 | 430.7693 | 646.5311 | 708.9536 | 576.5276 | 627.041 | 657.1812 | 494.6513
2696.3167 | 728.4253 | 430.815 | 645.2597 | 711.4927 | 578.3912 | 626.9326 | 657.2335 | 494.7748
2697.3167 | 728.2837 | 430.9074 | 643.799 | 711.3641 | 579.4179 | 626.8556 | 657.2965 | 494.9543
2698.3167 | 728.7708 | 430.9595 | 644.5501 | 711.5465 | 578.2156 | 626.9431 | 657.4656 | 495.1414
2699.3167 | 731.0756 | 431.0153 | 644.1658 | 713.6248 | 580.086 | 626.9879 | 657.6068 | 495.3206
2700.3167 | 730.9075 | 431.0837 | 640.9181 | 708.7788 | 581.359 | 627.026 | 657.74 | 495.5346
2701.3167 | 728.3256 | 431.1619 | 638.7841 | 706.6762 | 581.2787 | 626.8092 | 657.8014 | 495.7497
2702.3167 | 723.3547 | 431.2288 | 638.9937 | 699.7874 | 579.8862 | 626.93 | 657.8742 | 495.9399
2703.3167 | 721.6608 | 431.3158 | 639.1729 | 699.1329 | 577.7638 | 626.9846 | 657.927 | 496.1367
2704.3167 | 722.4194 | 431.3849 | 640.2498 | 701.7352 | 578.7022 | 626.8557 | 658.046 | 496.291
2705.3167 | 727.2061 | 431.453 | 644.6289 | 709.1903 | 580.4049 | 626.8973 | 658.1647 | 496.5074
2706.3167 | 732.9324 | 431.5841 | 645.558 | 710.2379 | 580.2153 | 627.2728 | 658.4583 | 496.7878
2707.3167 | 736.7518 | 431.6713 | 646.6101 | 714.7243 | 579.4948 | 627.5955 | 658.6829 | 497.0945
2708.3167 | 734.3033 | 431.6618 | 644.3394 | 715.7515 | 579.8724 | 627.3243 | 658.8063 | 497.1745
2709.3167 | 735.7652 | 431.7335 | 646.3347 | 717.0412 | 580.0965 | 627.4037 | 659.0171 | 497.4061
2710.3167 | 731.5534 | 431.8031 | 644.1267 | 709.9329 | 579.3376 | 627.6405 | 659.1124 | 497.6546
2711.3167 | 730.6693 | 431.8762 | 642.9395 | 706.5982 | 577.8689 | 627.5915 | 659.1654 | 497.8515
2712.3167 | 731.6223 | 431.9501 | 647.0163 | 708.5727 | 579.0897 | 627.6433 | 659.2582 | 498.0544
2713.3167 | 736.536 | 432.0898 | 648.3832 | 710.6963 | 578.325 | 629.032 | 659.7146 | 498.5749
2714.3167 | 740.4233 | 432.1879 | 646.069 | 712.8553 | 578.2558 | 628.9056 | 659.9124 | 498.796
2715.3167 | 739.9767 | 432.156 | 645.0132 | 715.3862 | 577.6935 | 628.1937 | 659.8945 | 498.7634
2716.3167 | 738.6348 | 432.2313 | 644.7435 | 716.6048 | 576.3498 | 628.3034 | 660.0861 | 498.9744
2717.3167 | 745.5583 | 432.3138 | 646.2748 | 714.7327 | 574.9585 | 628.3563 | 660.3537 | 499.1807
2718.3167 | 744.0384 | 432.3893 | 646.5772 | 718.3018 | 573.5821 | 628.5252 | 660.5971 | 499.4158
2719.3167 | 745.4722 | 432.4509 | 646.3183 | 715.5905 | 572.4648 | 628.8679 | 660.8401 | 499.6524
2720.3167 | 742.9747 | 432.5201 | 646.6382 | 714.2325 | 570.5603 | 629.0286 | 661.0034 | 499.8731
2721.3167 | 743.2693 | 432.5915 | 646.4683 | 712.4201 | 568.0267 | 629.1221 | 661.209 | 499.9554
2722.3167 | 743.1061 | 432.6608 | 646.3593 | 707.2548 | 567.5255 | 629.2662 | 661.3553 | 500.1698
2723.3167 | 740.6209 | 432.7286 | 649.3281 | 707.6646 | 565.9428 | 629.3344 | 661.5436 | 500.3897
2724.3167 | 738.5764 | 432.8022 | 650.6054 | 707.3015 | 567.2961 | 629.6179 | 661.717 | 500.6155
2725.3167 | 735.8633 | 432.8652 | 652.103 | 703.8657 | 565.5234 | 629.8225 | 661.9185 | 500.8156
2726.3167 | 732.8328 | 432.9239 | 651.8502 | 715.8926 | 563.1742 | 630.2053 | 662.1529 | 501.0378
2727.3167 | 728.5163 | 432.998 | 651.464 | 710.143 | 562.0632 | 630.4332 | 662.3337 | 501.2496
2728.3167 | 729.0761 | 433.0891 | 651.0927 | 712.8016 | 562.2591 | 630.6193 | 662.5198 | 501.4737
2729.3167 | 730.1831 | 433.143 | 652.186 | 711.789 | 565.8248 | 630.7734 | 662.6587 | 501.6631
2730.3167 | 728.1213 | 433.2178 | 651.0314 | 710.8549 | 567.187 | 631.2314 | 662.8424 | 501.9024
2731.3167 | 728.7632 | 433.2934 | 648.3472 | 703.1216 | 567.6409 | 631.53 | 663.0392 | 502.1203
2732.3167 | 727.1409 | 433.3624 | 649.2456 | 702.9395 | 567.2222 | 631.411 | 663.1681 | 502.3162
2733.3167 | 725.5851 | 433.434 | 650.2418 | 703.7178 | 566.3453 | 631.6599 | 663.3702 | 502.538
2734.3167 | 724.8647 | 433.501 | 653.2555 | 703.9712 | 564.9853 | 632.1027 | 663.6424 | 502.7912
2735.3167 | 728.9702 | 433.5719 | 648.8107 | 696.1544 | 562.5038 | 632.4464 | 663.8167 | 503.0078
2736.3167 | 725.7056 | 433.6472 | 649.8929 | 695.1536 | 561.0946 | 632.3748 | 663.9844 | 503.2334
2737.3167 | 726.0987 | 433.7166 | 651.4344 | 699.223 | 560.7234 | 632.5024 | 664.2196 | 503.4293
2738.3167 | 728.5219 | 433.7858 | 651.4747 | 702.8236 | 561.6914 | 632.5005 | 664.5025 | 503.649
2739.3167 | 726.5908 | 433.8601 | 648.5803 | 698.3396 | 563.2909 | 632.826 | 664.645 | 503.8666
2740.3167 | 725.6844 | 433.9306 | 647.0986 | 693.9299 | 564.3057 | 632.9695 | 664.7825 | 504.0981
2741.3167 | 723.624 | 434.0083 | 645.7677 | 694.1117 | 565.5167 | 633.0026 | 664.8955 | 504.3017
2742.3167 | 723.3434 | 434.1101 | 642.2943 | 691.4609 | 567.7617 | 633.1637 | 665.0376 | 504.5162
2743.3167 | 719.7599 | 434.1831 | 637.3895 | 688.2745 | 567.7527 | 633.2876 | 665.1669 | 504.7304
2744.3167 | 718.1093 | 434.263 | 635.5842 | 685.8669 | 567.1557 | 633.1248 | 665.3426 | 504.9499
2745.3167 | 718.985 | 434.333 | 637.2888 | 691.4698 | 568.5903 | 633.1243 | 665.4947 | 505.1691
2746.3167 | 721.7515 | 434.4046 | 636.6059 | 693.8646 | 571.0116 | 633.0919 | 665.627 | 505.4136
2747.3167 | 723.7484 | 434.4808 | 637.3028 | 695.4274 | 571.0269 | 633.1197 | 665.8404 | 505.6614
2748.3167 | 728.3195 | 434.5564 | 638.7875 | 698.6151 | 568.7925 | 633.1897 | 666.082 | 505.8894
2749.3167 | 731.5512 | 434.6098 | 643.3748 | 698.1678 | 567.35 | 633.3745 | 666.3762 | 506.1471
2750.3167 | 737.9502 | 434.6897 | 643.0931 | 699.2341 | 565.8056 | 633.6182 | 666.6625 | 506.387
2751.3167 | 740.0491 | 434.7534 | 642.7675 | 695.6638 | 564.0185 | 633.7284 | 666.9536 | 506.6288
2752.3167 | 740.0414 | 434.8333 | 643.6721 | 694.7249 | 562.2536 | 633.8211 | 667.1836 | 506.8681
2753.3167 | 738.1517 | 434.9051 | 644.444 | 697.8537 | 561.6508 | 633.9038 | 667.4458 | 507.0827
2754.3167 | 737.4458 | 434.9823 | 642.938 | 695.7727 | 560.0935 | 634.1462 | 667.6792 | 507.3148
2755.3167 | 733.3147 | 435.0519 | 641.6836 | 694.2893 | 559.2859 | 634.3871 | 667.8454 | 507.5609
2756.3167 | 733.1601 | 435.1229 | 641.4848 | 701.7651 | 559.3203 | 634.3816 | 668.0496 | 507.7731
2757.3167 | 734.301 | 435.1967 | 641.4149 | 698.7271 | 558.8267 | 634.6277 | 668.2603 | 508.0328
2758.3167 | 732.7574 | 435.2759 | 639.1179 | 694.8019 | 559.5245 | 634.7631 | 668.4465 | 508.2711
2759.3167 | 733.4406 | 435.3543 | 638.4189 | 695.1375 | 561.1148 | 634.7511 | 668.577 | 508.4815
2760.3167 | 735.1526 | 435.4375 | 638.0008 | 693.8986 | 565.2144 | 634.7996 | 668.8185 | 508.7445
2761.3167 | 736.3312 | 435.5175 | 637.1914 | 697.5827 | 566.0996 | 634.7534 | 669.0596 | 509.0059
2762.3167 | 735.0798 | 435.5936 | 637.6155 | 698.5412 | 568.0367 | 634.7632 | 669.2373 | 509.2774
2763.3167 | 731.9595 | 435.6676 | 637.1911 | 698.3989 | 569.3257 | 634.8205 | 669.4284 | 509.5229
2764.3167 | 729.0025 | 435.7577 | 635.5759 | 694.8824 | 571.212 | 634.9935 | 669.6476 | 509.8044
2765.3167 | 729.8557 | 436.0344 | 632.2966 | 697.5981 | 571.466 | 635.5752 | 670.0468 | 510.3013
2766.3167 | 730.0481 | 436.132 | 630.5259 | 693.0894 | 573.5865 | 635.8188 | 670.3739 | 510.6492
2767.3167 | 724.8617 | 435.9951 | 627.0276 | 687.6471 | 575.7913 | 634.8486 | 670.346 | 510.5735
2768.3167 | 721.5918 | 436.082 | 625.1463 | 687.1244 | 576.3037 | 634.7128 | 670.4583 | 510.8642
2769.3167 | 722.6797 | 436.1591 | 626.3757 | 692.2527 | 578.5758 | 634.4525 | 670.6732 | 511.1457
2770.3167 | 722.6359 | 436.2449 | 627.6243 | 691.6463 | 580.9072 | 634.5794 | 670.8916 | 511.4423
2771.3167 | 719.8091 | 436.3261 | 623.7438 | 687.0299 | 584.226 | 634.6527 | 671.025 | 511.7241
2772.3167 | 718.7634 | 436.4094 | 618.4435 | 681.8636 | 586.1862 | 634.6274 | 671.2844 | 512.0333
2773.3167 | 720.0016 | 436.7624 | 613.9749 | 678.5256 | 585.6802 | 634.7123 | 671.5128 | 512.4156
2774.3167 | 712.5781 | 436.5706 | 612.3652 | 676.4897 | 585.836 | 634.2174 | 671.5755 | 512.6196
2775.3167 | 712.3639 | 436.655 | 612.2086 | 675.2973 | 583.9135 | 634.14 | 671.7152 | 512.9141
2776.3167 | 714.3894 | 436.7329 | 614.8366 | 676.3614 | 583.7824 | 633.8389 | 671.8095 | 513.2089
2777.3167 | 716.3787 | 436.819 | 617.9259 | 680.4982 | 583.4154 | 633.7966 | 671.9251 | 513.5206
2778.3167 | 714.9821 | 436.8983 | 618.2576 | 687.3074 | 582.9442 | 633.9251 | 672.1139 | 513.8518
2779.3167 | 715.5153 | 436.9841 | 619.0179 | 689.3906 | 581.8741 | 633.9023 | 672.2413 | 514.1705
2780.3167 | 715.4995 | 437.0619 | 619.6687 | 685.792 | 582.2683 | 633.957 | 672.3841 | 514.4972
2781.3167 | 717.595 | 437.1512 | 618.5984 | 682.8949 | 582.4475 | 633.9808 | 672.5298 | 514.8379
2782.3167 | 715.1757 | 437.2634 | 615.5959 | 679.4153 | 581.6059 | 634.0482 | 672.7945 | 515.1671
2783.3167 | 713.8053 | 437.3203 | 613.3109 | 680.9698 | 579.9236 | 633.8309 | 672.9208 | 515.4606
2784.3167 | 716.0017 | 437.4011 | 613.1187 | 678.7187 | 579.5763 | 633.7361 | 673.0164 | 515.7636
2785.3167 | 716.8271 | 437.4851 | 614.9228 | 679.9711 | 579.9971 | 633.5466 | 673.1378 | 516.0915
2786.3167 | 715.4192 | 437.5608 | 616.1657 | 681.5114 | 579.3677 | 633.5635 | 673.2852 | 516.4105
2787.3167 | 713.2203 | 437.6489 | 615.3584 | 681.3784 | 577.8936 | 633.5423 | 673.4187 | 516.7676
2788.3167 | 712.6339 | 437.7298 | 618.1514 | 682.8583 | 575.6333 | 633.485 | 673.4941 | 517.1003
2789.3167 | 713.1283 | 437.8213 | 618.867 | 682.9929 | 574.9141 | 633.4957 | 673.6626 | 517.4071
2790.3167 | 713.0726 | 437.8916 | 618.5249 | 684.2948 | 574.3661 | 633.4104 | 673.7848 | 517.7305
2791.3167 | 712.5905 | 437.9754 | 618.796 | 682.5023 | 574.8375 | 633.3061 | 673.9167 | 518.1265
2792.3167 | 709.256 | 438.0608 | 617.4182 | 679.3067 | 574.6479 | 633.2465 | 674.0483 | 518.5293
2793.3167 | 705.5342 | 438.1427 | 615.6832 | 678.7128 | 574.2981 | 633.129 | 674.1985 | 518.8714
2794.3167 | 702.8423 | 438.2168 | 616.8802 | 676.7668 | 573.0227 | 633.1135 | 674.4015 | 519.2381
2795.3167 | 703.1293 | 438.2967 | 617.5961 | 678.2651 | 571.2789 | 632.9828 | 674.5157 | 519.5598
2796.3167 | 703.9248 | 438.3828 | 618.624 | 678.5181 | 571.7899 | 632.9585 | 674.6543 | 519.8964
2797.3167 | 702.5683 | 438.4584 | 615.994 | 676.3537 | 571.9487 | 632.9706 | 674.8499 | 520.2385
2798.3167 | 701.2076 | 438.5428 | 614.1673 | 671.9243 | 570.1619 | 632.9805 | 675.1011 | 520.568
2799.3167 | 699.8502 | 438.6314 | 612.6269 | 669.3441 | 568.0687 | 632.7103 | 675.2346 | 520.867
2800.3167 | 698.4502 | 438.714 | 611.1247 | 669.6315 | 567.3171 | 632.7298 | 675.3876 | 521.1183
2801.3167 | 699.049 | 438.8002 | 609.8458 | 670.6786 | 568.7564 | 632.4381 | 675.5377 | 521.4617
2802.3167 | 698.6083 | 438.8854 | 606.7421 | 668.3262 | 569.5112 | 632.3377 | 675.7398 | 521.9713
2803.3167 | 700.9358 | 438.9776 | 604.9174 | 670.206 | 572.187 | 632.1352 | 675.9112 | 522.2353
2804.3167 | 706.0114 | 439.0805 | 602.1159 | 671.1078 | 575.6656 | 631.9853 | 676.0697 | 522.6588
2805.3167 | 712.6152 | 439.1623 | 600.7672 | 668.9631 | 577.3008 | 631.7414 | 676.2047 | 522.9784
2806.3167 | 711.7535 | 439.2462 | 600.7754 | 666.5202 | 579.3056 | 631.5049 | 676.3001 | 523.3908
2807.3167 | 708.8919 | 439.3341 | 602.4329 | 667.1452 | 578.0951 | 631.2731 | 676.5134 | 523.7264
2808.3167 | 707.8255 | 439.4174 | 605.3957 | 670.3626 | 576.455 | 631.1506 | 676.6204 | 524.0438
2809.3167 | 706.4607 | 439.5081 | 605.0555 | 671.0006 | 576.1804 | 631.1348 | 676.7031 | 524.3757
2810.3167 | 703.9628 | 439.5985 | 602.6826 | 667.4078 | 574.5914 | 631.1214 | 676.8056 | 524.6845
2811.3167 | 704.2967 | 439.6867 | 603.5767 | 670.2087 | 573.0317 | 630.7814 | 677.2062 | 525.0149
2812.3167 | 703.6961 | 439.7755 | 604.7788 | 669.3953 | 573.9422 | 630.7227 | 677.4538 | 525.3484
2813.3167 | 703.9922 | 439.8666 | 607.4533 | 670.5677 | 572.2957 | 630.4869 | 677.7348 | 525.672
2814.3167 | 707.4836 | 439.9554 | 608.7843 | 671.447 | 571.7554 | 630.5608 | 677.9382 | 526.0757
2815.3167 | 713.3174 | 440.0512 | 610.2271 | 671.402 | 571.5209 | 630.5201 | 678.3048 | 526.4319
2816.3167 | 716.8277 | 440.1489 | 610.9179 | 667.3186 | 570.9932 | 630.5098 | 678.6936 | 526.7323
2817.3167 | 715.7715 | 440.2477 | 610.2358 | 668.734 | 570.5252 | 630.4488 | 678.8815 | 527.0505
2818.3167 | 714.8076 | 440.3403 | 609.1351 | 667.9145 | 572.4914 | 630.2834 | 678.9371 | 527.3819
2819.3167 | 714.4123 | 440.4351 | 606.4865 | 667.8377 | 573.6815 | 630.1472 | 679.0181 | 527.7198
2820.3167 | 713.7803 | 440.5186 | 607.9476 | 670.8411 | 574.3453 | 629.7955 | 679.0875 | 528.0272
2821.3167 | 713.2576 | 440.6198 | 609.4899 | 671.9005 | 576.4391 | 629.7491 | 679.2102 | 528.3658
2822.3167 | 712.193 | 440.7153 | 608.5432 | 672.372 | 576.1682 | 629.6901 | 679.3493 | 528.7068
2823.3167 | 709.0669 | 440.8156 | 607.2245 | 668.9582 | 575.0352 | 629.6563 | 679.5274 | 529.0044
2824.3167 | 706.4901 | 440.9021 | 603.2818 | 669.9018 | 574.9632 | 629.526 | 679.5345 | 529.3222
2825.3167 | 704.634 | 441.0026 | 600.3227 | 669.3469 | 573.6484 | 629.3084 | 679.6915 | 529.6698
2826.3167 | 703.3139 | 441.096 | 602.7079 | 671.4684 | 571.6431 | 628.798 | 679.7384 | 529.9826
2827.3167 | 705.4498 | 441.1933 | 604.8055 | 671.8207 | 569.8907 | 628.9415 | 679.9463 | 530.2871
2828.3167 | 709.568 | 441.2874 | 605.6159 | 668.0442 | 567.8773 | 628.9384 | 679.8448 | 530.5885
2829.3167 | 712.11 | 441.3881 | 606.0062 | 667.0468 | 567.1756 | 628.8138 | 679.9205 | 530.8837
2830.3167 | 715.2649 | 441.9323 | 607.7325 | 671.2173 | 566.6539 | 628.8551 | 680.0069 | 531.2108
2831.3167 | 713.7742 | 441.582 | 608.4039 | 672.642 | 566.5918 | 628.6016 | 679.9516 | 531.457
2832.3167 | 716.027 | 441.6859 | 609.8672 | 672.5456 | 568.6303 | 628.4755 | 679.9831 | 531.705
2833.3167 | 717.471 | 441.7812 | 609.362 | 672.8033 | 568.6915 | 628.3043 | 679.9773 | 531.9828
2834.3167 | 720.1128 | 441.8772 | 609.7655 | 674.6575 | 567.6764 | 628.2614 | 680.1292 | 532.239
2835.3167 | 721.3733 | 441.9913 | 609.9271 | 676.3447 | 566.2446 | 628.1602 | 680.1635 | 532.5048
2836.3167 | 721.1971 | 442.0678 | 608.9832 | 675.1213 | 565.4378 | 628.098 | 680.3884 | 532.6883
2837.3167 | 721.8663 | 442.1588 | 610.0894 | 680.6668 | 565.1187 | 627.9209 | 680.5223 | 533.0604
2838.3167 | 720.4532 | 442.2664 | 611.435 | 678.4922 | 563.8746 | 627.9074 | 680.5215 | 533.3526
2839.3167 | 721.8841 | 442.4455 | 611.9385 | 677.2657 | 563.0247 | 628.6424 | 680.7513 | 533.9214
2840.3167 | 722.2694 | 442.4552 | 612.8492 | 680.6077 | 564.1913 | 627.8227 | 680.6103 | 533.9252
2841.3167 | 719.9834 | 442.5503 | 612.9371 | 681.7543 | 564.0442 | 627.7092 | 680.8066 | 534.1116
2842.3167 | 718.4499 | 442.6476 | 614.3158 | 683.0788 | 564.0593 | 627.6022 | 680.9995 | 534.2953
2843.3167 | 717.3381 | 442.7503 | 614.422 | 683.3878 | 564.5941 | 627.4805 | 681.0267 | 534.6488
2844.3167 | 719.0692 | 442.8633 | 619.2504 | 684.3057 | 564.8178 | 627.402 | 681.1192 | 534.9242
2845.3167 | 722.6908 | 442.9528 | 621.9733 | 687.1372 | 565.082 | 627.3294 | 681.2782 | 535.1321
2846.3167 | 728.3729 | 443.0557 | 622.7334 | 687.5095 | 563.771 | 627.3654 | 681.6043 | 535.3968
2847.3167 | 735.2626 | 443.1652 | 622.7094 | 689.2 | 562.6396 | 627.282 | 681.9884 | 535.6247
2848.3167 | 736.4577 | 443.2701 | 621.7509 | 688.382 | 562.133 | 627.3275 | 682.054 | 535.8679
2849.3167 | 737.0171 | 443.373 | 622.4299 | 688.9287 | 561.9414 | 627.2812 | 682.1164 | 536.0273
2850.3167 | 737.9576 | 443.4982 | 622.3235 | 688.3351 | 561.9316 | 627.3083 | 682.3383 | 536.3171
2851.3167 | 740.2339 | 443.5816 | 622.2339 | 688.2567 | 563.6673 | 626.9781 | 682.3268 | 536.4678
2852.3167 | 739.8345 | 443.6784 | 620.3643 | 685.0273 | 564.4347 | 627.1346 | 682.5187 | 536.7956
2853.3167 | 738.0973 | 443.8618 | 618.3098 | 681.9745 | 565.4586 | 627.8219 | 682.7674 | 537.3026
2854.3167 | 734.1392 | 443.8611 | 615.951 | 678.4928 | 567.7113 | 626.894 | 682.5808 | 537.1015
2855.3167 | 731.5438 | 443.9769 | 615.0816 | 682.8885 | 570.6311 | 626.7335 | 682.5073 | 537.4324
2856.3167 | 730.1045 | 444.0725 | 615.4786 | 680.3162 | 572.9272 | 626.6288 | 682.5171 | 537.656
2857.3167 | 727.0147 | 444.1686 | 614.3299 | 679.3493 | 571.8347 | 626.4493 | 682.6077 | 537.817
2858.3167 | 725.5265 | 444.2764 | 612.6658 | 679.4189 | 571.2055 | 626.3521 | 682.574 | 537.9598
2859.3167 | 723.5367 | 444.3859 | 613.4811 | 682.7498 | 570.9125 | 626.0946 | 682.591 | 538.2838
2860.3167 | 722.3051 | 444.4858 | 615.5622 | 687.1955 | 571.553 | 625.8951 | 682.5976 | 538.4806
2861.3167 | 722.0675 | 444.5971 | 616.1576 | 686.9786 | 572.95 | 625.9074 | 682.7389 | 538.7265
2862.3167 | 720.0771 | 444.6935 | 616.6725 | 685.9568 | 572.6255 | 625.7968 | 682.8338 | 538.9189
2863.3167 | 720.1861 | 444.8044 | 618.3857 | 684.0413 | 570.8721 | 625.7457 | 682.848 | 539.0377
2864.3167 | 725.6382 | 444.8999 | 619.6871 | 682.9242 | 569.8809 | 625.5332 | 683.0288 | 539.2304
2865.3167 | 724.7642 | 445.0004 | 619.2159 | 679.9724 | 567.798 | 625.6316 | 683.2157 | 539.4426
2866.3167 | 724.5396 | 445.1005 | 615.6913 | 674.7689 | 566.2866 | 625.671 | 683.4025 | 539.6448
2867.3167 | 722.3112 | 445.2119 | 615.2449 | 674.0187 | 565.0196 | 625.4614 | 683.3558 | 539.9331
2868.3167 | 722.1989 | 445.3071 | 615.6563 | 675.3779 | 565.7341 | 625.295 | 683.2751 | 540.0245
2869.3167 | 721.4518 | 445.4121 | 614.9273 | 675.0765 | 565.6721 | 625.0894 | 683.2489 | 540.2988
2870.3167 | 720.4559 | 445.5143 | 616.9051 | 677.1961 | 565.6996 | 624.8784 | 683.2726 | 540.4614
2871.3167 | 723.7479 | 445.616 | 618.5251 | 679.2916 | 566.6485 | 624.6089 | 683.2993 | 540.6827
2872.3167 | 726.4813 | 445.7193 | 616.3305 | 681.0935 | 566.6107 | 624.7586 | 683.5155 | 540.8886
2873.3167 | 728.7279 | 445.8297 | 615.8908 | 679.8014 | 565.8243 | 624.5153 | 683.5712 | 541.1059
2874.3167 | 729.2515 | 445.9244 | 614.3002 | 678.0856 | 564.6353 | 624.3631 | 683.6199 | 541.2812
2875.3167 | 731.2251 | 446.0318 | 615.7034 | 677.4733 | 565.204 | 624.0411 | 683.6345 | 541.4947
2876.3167 | 731.9254 | 446.1315 | 615.0967 | 674.0145 | 564.0385 | 623.996 | 683.642 | 541.6735
2877.3167 | 730.6306 | 446.2424 | 613.3019 | 675.8257 | 565.0559 | 623.7061 | 683.5652 | 541.8481
2878.3167 | 729.4755 | 446.3488 | 612.1881 | 678.6532 | 567.4275 | 623.6488 | 683.5428 | 542.0404
2879.3167 | 726.2143 | 446.4403 | 611.8509 | 678.9884 | 569.2803 | 623.5729 | 683.441 | 542.247
2880.3167 | 724.5525 | 446.5454 | 612.072 | 679.4597 | 572.6018 | 623.2237 | 683.4901 | 542.4471
2881.3167 | 726.0893 | 446.6515 | 613.6666 | 682.7275 | 573.9711 | 622.8609 | 683.4704 | 542.6393
2882.3167 | 724.094 | 446.7515 | 613.3975 | 678.7076 | 575.8824 | 622.7468 | 683.3994 | 542.8724
2883.3167 | 721.1244 | 446.8512 | 612.735 | 678.3681 | 575.9833 | 622.7317 | 683.458 | 543.0668
2884.3167 | 719.3574 | 446.9628 | 614.4792 | 678.8761 | 574.4039 | 622.6287 | 683.4446 | 543.258
2885.3167 | 717.0697 | 447.0604 | 611.0533 | 674.8742 | 572.5236 | 622.6154 | 683.4293 | 543.4649
2886.3167 | 715.4235 | 447.1639 | 611.6859 | 673.4111 | 570.2883 | 622.4577 | 683.3686 | 543.6634
2887.3167 | 715.5102 | 447.2725 | 612.6345 | 675.769 | 568.0761 | 622.2762 | 683.3297 | 543.8553
2888.3167 | 720.2388 | 447.377 | 613.6086 | 674.8329 | 569.9325 | 622.3131 | 683.2959 | 544.0435
2889.3167 | 720.1169 | 447.4771 | 613.8425 | 679.3803 | 572.4953 | 622.2674 | 683.374 | 544.2296
2890.3167 | 722.2006 | 447.58 | 615.7082 | 680.3473 | 575.5133 | 621.8938 | 683.3659 | 544.4399
2891.3167 | 722.4799 | 447.6935 | 613.516 | 679.6228 | 575.5609 | 622.1401 | 683.5252 | 544.6917
2892.3167 | 723.303 | 447.7844 | 612.3574 | 677.9207 | 573.7797 | 621.9651 | 683.7233 | 544.8907
2893.3167 | 722.3223 | 447.8866 | 612.7476 | 679.0585 | 572.565 | 621.7356 | 683.876 | 545.0823
2894.3167 | 724.2748 | 447.9979 | 610.1776 | 676.3454 | 570.5321 | 621.8147 | 683.8612 | 545.2716
2895.3167 | 723.8992 | 448.1043 | 610.6477 | 677.351 | 568.9709 | 621.4579 | 683.9021 | 545.4435
2896.3167 | 725.6255 | 448.2073 | 611.8323 | 679.393 | 567.2649 | 621.4479 | 684.0301 | 545.6292
2897.3167 | 728.2331 | 448.3147 | 612.0159 | 676.8388 | 565.5464 | 621.3491 | 683.9884 | 545.7993
2898.3167 | 728.2921 | 448.4184 | 611.7371 | 677.3901 | 567.3325 | 621.36 | 684.0122 | 545.9911
2899.3167 | 726.9593 | 448.5158 | 611.2805 | 677.4719 | 568.1643 | 621.2667 | 683.8747 | 546.1614
2900.3167 | 726.2237 | 448.6285 | 609.9772 | 679.0649 | 568.1674 | 620.9288 | 683.9337 | 546.3482
2901.3167 | 726.7712 | 448.7307 | 610.4665 | 678.0779 | 570.0287 | 620.859 | 683.8218 | 546.5278
2902.3167 | 728.3658 | 448.8378 | 609.2603 | 674.7476 | 572.1793 | 620.747 | 683.8407 | 546.7259
2903.3167 | 726.3391 | 448.9436 | 611.0889 | 677.5807 | 573.4913 | 620.6868 | 683.9604 | 546.9186
2904.3167 | 726.3252 | 449.0508 | 612.4741 | 680.6569 | 574.3807 | 620.4346 | 683.9909 | 547.1181
2905.3167 | 729.6136 | 449.1607 | 612.2455 | 684.2752 | 573.7486 | 620.3571 | 684.0413 | 547.2989
2906.3167 | 730.4437 | 449.2723 | 612.3196 | 686.8678 | 571.7867 | 620.1891 | 684.1885 | 547.4625
2907.3167 | 733.3377 | 449.3752 | 611.9731 | 685.4736 | 570.913 | 620.2186 | 684.2218 | 547.6264
2908.3167 | 734.5437 | 449.4811 | 610.7208 | 683.8137 | 572.2945 | 620.1675 | 684.253 | 547.8012
2909.3167 | 733.3191 | 449.5856 | 610.9949 | 682.8235 | 572.5482 | 620.0118 | 684.264 | 547.9705
2910.3167 | 730.506 | 449.6781 | 610.1378 | 680.7835 | 571.9974 | 620.1357 | 684.3317 | 548.1745
2911.3167 | 727.4172 | 449.7837 | 607.7322 | 679.9432 | 571.9739 | 620.0465 | 684.3497 | 548.3202
2912.3167 | 725.1501 | 449.8903 | 606.5008 | 675.0206 | 572.8471 | 619.9285 | 684.3477 | 548.5042
2913.3167 | 727.9374 | 449.9988 | 604.5532 | 675.2655 | 574.058 | 619.5107 | 684.3684 | 548.6645
2914.3167 | 731.7114 | 450.1033 | 601.9848 | 671.5017 | 575.7739 | 619.3582 | 684.4051 | 548.8788
2915.3167 | 729.7204 | 450.2121 | 599.7837 | 669.5466 | 577.0133 | 619.2697 | 684.4318 | 549.0612
2916.3167 | 727.495 | 450.3124 | 598.917 | 666.7253 | 579.1419 | 619.1171 | 684.3924 | 549.2398
2917.3167 | 726.047 | 450.4198 | 597.25 | 663.4223 | 582.2609 | 618.9418 | 684.4754 | 549.4733
2918.3167 | 725.3566 | 450.5182 | 593.1651 | 658.607 | 583.4859 | 618.7974 | 684.5173 | 549.6668
2919.3167 | 722.8982 | 450.6229 | 590.2555 | 657.6197 | 583.1922 | 618.4883 | 684.4747 | 549.8822
2920.3167 | 722.9123 | 450.7225 | 590.0859 | 656.8346 | 584.6069 | 618.2551 | 684.2674 | 550.1171
2921.3167 | 719.718 | 450.8333 | 588.4279 | 657.2418 | 584.8903 | 618.0726 | 684.1381 | 550.3433
2922.3167 | 718.923 | 450.9406 | 587.5962 | 658.7708 | 583.2916 | 617.6152 | 684.1021 | 550.548
2923.3167 | 719.1289 | 451.0425 | 589.5653 | 660.8848 | 584.2815 | 617.4302 | 684.0539 | 550.7793
2924.3167 | 717.49 | 451.1434 | 588.9529 | 662.0824 | 586.5069 | 617.0987 | 683.9268 | 551.0322
2925.3167 | 713.7385 | 451.2495 | 588.8406 | 663.2843 | 587.2045 | 616.8166 | 683.792 | 551.2661
2926.3167 | 712.1015 | 451.3438 | 587.7541 | 664.8597 | 586.2816 | 616.4704 | 683.8072 | 551.4861
2927.3167 | 711.1798 | 451.4565 | 588.3413 | 667.7589 | 585.7631 | 616.1158 | 683.6157 | 551.7057
2928.3167 | 709.6279 | 451.5695 | 588.6657 | 665.9374 | 585.92 | 615.9463 | 683.4171 | 551.9381
2929.3167 | 709.8883 | 451.6817 | 591.5443 | 667.4627 | 585.6921 | 615.6074 | 683.396 | 552.1658
2930.3167 | 709.5072 | 451.7848 | 592.5265 | 667.9176 | 584.7056 | 615.5068 | 683.3421 | 552.434
2931.3167 | 709.2778 | 451.883 | 590.3114 | 665.4238 | 584.1204 | 615.3894 | 683.3233 | 552.6995
2932.3167 | 708.0861 | 453.7856 | 587.4888 | 660.6975 | 581.03 | 615.6396 | 683.4357 | 553.0979
2933.3167 | 704.6182 | 452.0768 | 585.5865 | 661.2806 | 577.75 | 614.8532 | 683.3322 | 553.1751
2934.3167 | 701.7379 | 452.1844 | 583.7021 | 662.2993 | 576.078 | 614.5676 | 683.1842 | 553.3857
2935.3167 | 700.0142 | 452.2943 | 582.814 | 663.307 | 574.4458 | 614.1858 | 683.0639 | 553.6017
2936.3167 | 697.9055 | 452.4022 | 583.0723 | 663.3559 | 573.3924 | 613.8495 | 683.0393 | 553.8217
2937.3167 | 696.9867 | 452.5026 | 582.2494 | 660.7726 | 572.2606 | 613.6038 | 683.0033 | 554.0507
2938.3167 | 697.8835 | 452.6124 | 583.6772 | 661.7547 | 571.6514 | 613.2535 | 682.9213 | 554.27
2939.3167 | 697.208 | 452.7019 | 580.126 | 659.4892 | 572.019 | 612.9742 | 682.9591 | 554.506
2940.3167 | 698.743 | 452.859 | 580.3905 | 660.4075 | 571.6445 | 612.9699 | 683.1045 | 554.8518
2941.3167 | 700.6055 | 454.6122 | 584.6076 | 664.0535 | 570.5235 | 612.9599 | 683.0198 | 555.1258
2942.3167 | 699.5662 | 453.0147 | 585.1086 | 664.087 | 570.5703 | 612.0405 | 682.7087 | 555.1766
2943.3167 | 698.1885 | 453.1212 | 583.6248 | 664.6051 | 569.569 | 611.8546 | 682.6359 | 555.3902
2944.3167 | 698.9294 | 453.2176 | 582.8321 | 663.631 | 568.1598 | 611.4314 | 682.5044 | 555.6163
2945.3167 | 701.3694 | 453.328 | 585.6137 | 664.1659 | 566.8176 | 611.1237 | 682.3036 | 555.8139
2946.3167 | 703.6468 | 453.4391 | 590.3885 | 666.3635 | 566.3301 | 610.9002 | 682.3079 | 556.0218
2947.3167 | 704.3673 | 453.6115 | 591.2331 | 666.6019 | 567.0979 | 611.3435 | 682.4714 | 556.434
2948.3167 | 706.2485 | 453.6571 | 594.9307 | 669.5953 | 569.2993 | 610.5365 | 682.3356 | 556.432
2949.3167 | 710.5615 | 453.7415 | 594.4621 | 662.837 | 567.8675 | 610.6493 | 682.3577 | 556.6357
2950.3167 | 713.0729 | 453.838 | 594.0193 | 656.5963 | 566.227 | 610.5738 | 682.327 | 556.7899
2951.3167 | 710.8533 | 453.9422 | 590.9286 | 651.1425 | 566.6481 | 610.5457 | 682.2423 | 556.9325
2952.3167 | 709.2431 | 454.0637 | 591.6131 | 652.9073 | 565.6811 | 610.32 | 682.1561 | 557.1414
2953.3167 | 708.8201 | 454.1628 | 591.6358 | 654.7462 | 565.3466 | 610.0183 | 681.9306 | 557.2623
2954.3167 | 709.4194 | 454.2532 | 591.5507 | 657.3714 | 566.1378 | 609.6343 | 681.7676 | 557.3981
2955.3167 | 709.1114 | 454.3611 | 591.8281 | 657.3412 | 567.3373 | 609.4588 | 681.7713 | 557.5663
2956.3167 | 709.415 | 454.4673 | 592.425 | 658.1345 | 567.5699 | 609.2122 | 681.7185 | 557.7434
2957.3167 | 712.9618 | 454.5742 | 592.0793 | 662.5004 | 570.7936 | 608.91 | 681.5826 | 557.8855
2958.3167 | 710.4917 | 454.6817 | 592.4111 | 663.1599 | 572.7361 | 608.633 | 681.4459 | 558.0545
2959.3167 | 709.6799 | 454.7877 | 591.0419 | 668.0384 | 572.179 | 608.2411 | 681.3072 | 558.2074
2960.3167 | 709.3033 | 454.8856 | 592.1656 | 668.768 | 573.2916 | 608.147 | 681.2954 | 558.3667
2961.3167 | 709.4347 | 454.9945 | 592.0576 | 667.8546 | 573.2355 | 608.005 | 681.2923 | 558.5147
2962.3167 | 709.5837 | 455.1054 | 589.4607 | 665.9936 | 573.2434 | 607.6569 | 681.3041 | 558.6625
2963.3167 | 707.9984 | 455.2152 | 588.8723 | 662.285 | 573.3479 | 607.5053 | 681.3479 | 558.8274
2964.3167 | 706.6177 | 455.3254 | 584.5096 | 658.7616 | 573.621 | 607.3577 | 681.4561 | 558.9797
2965.3167 | 705.2739 | 455.4279 | 581.7144 | 655.6135 | 572.5819 | 606.9908 | 681.3973 | 559.1051
2966.3167 | 702.9709 | 455.5366 | 582.3922 | 656.323 | 571.8385 | 606.5597 | 681.2987 | 559.2464
2967.3167 | 703.5758 | 455.6227 | 585.5052 | 662.2156 | 569.7807 | 606.1278 | 681.3167 | 559.3985
2968.3167 | 707.0074 | 455.7368 | 589.0906 | 661.2473 | 569.1662 | 605.935 | 681.1912 | 559.5433
2969.3167 | 707.5817 | 455.8377 | 590.5991 | 658.5952 | 570.155 | 605.8208 | 681.1378 | 559.6878
2970.3167 | 707.6854 | 455.9425 | 588.9053 | 653.3863 | 569.0063 | 605.7283 | 681.0653 | 559.8197
2971.3167 | 705.9596 | 456.0511 | 587.5871 | 653.1506 | 567.1979 | 605.5552 | 680.9551 | 559.9396
2972.3167 | 703.0549 | 456.2798 | 585.8058 | 651.256 | 564.8243 | 606.028 | 681.0623 | 560.3261
2973.3167 | 704.229 | 456.2804 | 587.9595 | 654.4555 | 565.6745 | 604.8123 | 680.6451 | 560.1333
2974.3167 | 703.4699 | 456.3608 | 589.2491 | 654.3909 | 566.0809 | 604.6377 | 680.4757 | 560.2631
2975.3167 | 699.4779 | 456.475 | 589.131 | 654.1855 | 564.6624 | 604.4348 | 680.3897 | 560.3911
2976.3167 | 696.9098 | 456.5789 | 587.6192 | 656.0114 | 563.2451 | 604.065 | 680.2822 | 560.487
2977.3167 | 699.656 | 456.6901 | 588.6719 | 656.9817 | 563.7757 | 603.7436 | 680.085 | 560.5933
2978.3167 | 700.2172 | 456.7936 | 589.5824 | 659.9494 | 565.7996 | 603.3372 | 679.9972 | 560.7228
2979.3167 | 701.7734 | 456.8949 | 592.7575 | 658.4854 | 565.424 | 603.1392 | 680.0045 | 560.8565
2980.3167 | 705.8984 | 457.019 | 594.4112 | 661.9933 | 565.5168 | 602.9089 | 680.0489 | 560.969
2981.3167 | 710.3608 | 457.0924 | 593.6869 | 665.033 | 566.2464 | 602.7854 | 680.0093 | 561.0866
2982.3167 | 712.3934 | 457.2179 | 593.2661 | 664.2755 | 565.407 | 602.5107 | 679.9929 | 561.1889
2983.3167 | 713.3567 | 457.3241 | 593.5075 | 662.9655 | 564.3775 | 602.2889 | 679.9882 | 561.2883
2984.3167 | 713.8603 | 457.4375 | 594.51 | 664.4224 | 564.6973 | 602.0085 | 679.9365 | 561.3691
2985.3167 | 716.9704 | 457.5431 | 596.0153 | 665.5712 | 564.6126 | 601.7996 | 679.9534 | 561.4669
2986.3167 | 718.8117 | 457.6492 | 597.23 | 663.6201 | 565.2764 | 601.6732 | 679.9181 | 561.5561
2987.3167 | 721.4665 | 457.771 | 599.1 | 668.8451 | 568.0791 | 601.2101 | 679.8792 | 561.658
2988.3167 | 724.6595 | 458.1934 | 598.0011 | 667.0718 | 568.7172 | 601.3819 | 679.8696 | 561.8608
2989.3167 | 726.7105 | 457.9503 | 598.3436 | 666.9529 | 568.0367 | 600.9175 | 679.9103 | 561.9114
2990.3167 | 725.3482 | 458.0726 | 597.3938 | 660.1388 | 566.0983 | 600.902 | 679.8459 | 562.0474
2991.3167 | 721.825 | 458.184 | 595.1931 | 654.0185 | 564.4034 | 600.669 | 679.7112 | 562.1406
2992.3167 | 721.495 | 458.3685 | 594.1623 | 655.6382 | 563.2982 | 600.4216 | 679.4978 | 562.2137
2993.3167 | 721.6833 | 458.4072 | 593.2691 | 653.5891 | 564.8951 | 600.1117 | 679.302 | 562.279
2994.3167 | 718.9937 | 458.5302 | 592.4956 | 653.3602 | 567.0902 | 599.8452 | 679.188 | 562.3602
2995.3167 | 715.8326 | 458.6465 | 592.0781 | 655.8855 | 566.95 | 599.6156 | 679.1275 | 562.4762
2996.3167 | 713.4396 | 458.7569 | 592.4194 | 657.9076 | 566.151 | 599.3513 | 678.9947 | 562.5688
2997.3167 | 713.7911 | 458.8703 | 594.4794 | 662.7114 | 564.8418 | 599.0474 | 678.9286 | 562.6595
2998.3167 | 711.7379 | 458.997 | 594.3303 | 662.8398 | 563.2559 | 598.8498 | 678.7878 | 562.7292
2999.3167 | 711.9963 | 459.1151 | 594.5437 | 663.3319 | 562.299 | 598.517 | 678.6401 | 562.7968
3000.3167 | 713.3163 | 459.2353 | 596.6147 | 662.7345 | 562.4378 | 598.291 | 678.4831 | 562.8867
3001.3167 | 712.8484 | 459.3619 | 594.7686 | 661.639 | 563.7605 | 598.1494 | 678.3926 | 562.9608
3002.3167 | 709.4688 | 459.4695 | 591.9141 | 661.5705 | 563.5978 | 597.8525 | 678.4201 | 563.0459
3003.3167 | 710.7969 | 459.6064 | 593.661 | 665.2026 | 563.1501 | 597.654 | 678.4226 | 563.2102
3004.3167 | 709.1055 | 459.6904 | 594.2904 | 665.4614 | 563.2197 | 597.1793 | 678.2458 | 563.208
3005.3167 | 709.6703 | 459.8115 | 596.2213 | 666.8559 | 562.9867 | 596.8498 | 678.1699 | 563.2632
3006.3167 | 711.3051 | 459.9468 | 595.2581 | 666.9958 | 565.2615 | 596.6782 | 678.0421 | 563.3475
3007.3167 | 713.8882 | 460.0748 | 597.8506 | 668.2919 | 569.0398 | 596.2249 | 677.9473 | 563.4078
3008.3167 | 714.7388 | 460.1983 | 597.8932 | 669.8121 | 569.4812 | 595.8824 | 677.9313 | 563.4894
3009.3167 | 716.4122 | 460.4726 | 596.7868 | 667.0704 | 568.5173 | 595.7718 | 677.9199 | 563.6126
3010.3167 | 717.6363 | 460.4461 | 596.6511 | 668.9874 | 566.5204 | 595.4284 | 677.9392 | 563.6747
3011.3167 | 717.4871 | 460.5878 | 596.5749 | 667.4823 | 566.1529 | 595.1726 | 677.9844 | 563.7398
3012.3167 | 717.7832 | 460.7245 | 596.9982 | 665.2038 | 569.1191 | 594.9952 | 678.0157 | 563.8135
3013.3167 | 719.3186 | 460.8608 | 596.1881 | 664.5409 | 569.9772 | 594.6348 | 678.0019 | 563.9073
3014.3167 | 719.6539 | 460.9828 | 596.203 | 664.4728 | 570.5306 | 594.4361 | 678.0515 | 563.9775
3015.3167 | 717.6939 | 461.1225 | 594.3231 | 665.4111 | 569.2451 | 594.1565 | 678.0155 | 564.0559
3016.3167 | 717.4782 | 461.2628 | 594.5714 | 668.6215 | 568.3589 | 593.7903 | 677.9756 | 564.0957
3017.3167 | 719.8934 | 461.3973 | 594.0004 | 667.0561 | 568.7319 | 593.5989 | 677.9843 | 564.1693
3018.3167 | 716.1631 | 461.527 | 592.2473 | 665.6667 | 569.5045 | 593.2886 | 677.9459 | 564.2272
3019.3167 | 712.4407 | 461.6536 | 590.5797 | 661.7269 | 568.6746 | 593.0717 | 677.8915 | 564.308
3020.3167 | 710.5484 | 461.7809 | 590.493 | 661.8516 | 566.9338 | 592.5873 | 677.8584 | 564.3752
3021.3167 | 711.2944 | 461.9089 | 593.2845 | 660.5128 | 566.1882 | 592.4068 | 677.7721 | 564.4573
3022.3167 | 709.8701 | 462.0323 | 593.1874 | 656.4805 | 564.0915 | 592.1757 | 677.7115 | 564.5095
3023.3167 | 708.7693 | 462.1635 | 593.4309 | 656.7189 | 561.8573 | 591.9096 | 677.595 | 564.5911
3024.3167 | 708.395 | 462.3038 | 591.5041 | 657.0786 | 562.3155 | 591.6092 | 677.4763 | 564.6441
3025.3167 | 708.0771 | 462.4373 | 590.0133 | 655.3378 | 566.0254 | 591.4445 | 677.386 | 564.7366
3026.3167 | 707.734 | 462.5786 | 585.4072 | 651.9459 | 567.8183 | 591.1438 | 677.3586 | 564.8192
3027.3167 | 704.5154 | 462.7156 | 582.4155 | 646.6117 | 567.5879 | 590.9621 | 677.3281 | 564.9084
3028.3167 | 702.9163 | 462.8594 | 581.5816 | 649.2529 | 566.6426 | 590.4169 | 677.2758 | 564.9544
3029.3167 | 703.909 | 462.9995 | 585.5886 | 650.7407 | 566.2837 | 589.9782 | 677.1731 | 565.0214
3030.3167 | 707.782 | 463.1169 | 584.5362 | 653.2015 | 568.1386 | 589.6013 | 677.1386 | 565.0705
3031.3167 | 706.3824 | 463.255 | 583.5593 | 656.0044 | 568.0115 | 589.3732 | 677.0883 | 565.1444
3032.3167 | 703.9538 | 463.3905 | 583.2731 | 653.2258 | 567.1973 | 589.125 | 676.9817 | 565.183
3033.3167 | 702.2078 | 463.5223 | 582.3362 | 652.7262 | 567.8123 | 588.8759 | 676.8157 | 565.2482
3034.3167 | 706.0221 | 463.6636 | 581.6492 | 649.0621 | 570.376 | 588.697 | 676.729 | 565.3363
3035.3167 | 708.8199 | 463.7981 | 579.7641 | 645.1405 | 573.5909 | 588.4631 | 676.6807 | 565.4203
3036.3167 | 706.1595 | 463.9244 | 579.6479 | 640.6558 | 573.4981 | 588.1787 | 676.5885 | 565.5209
3037.3167 | 702.454 | 464.0554 | 579.9597 | 643.7028 | 573.0104 | 587.7867 | 676.4739 | 565.5701
3038.3167 | 700.7385 | 464.1893 | 581.9064 | 642.9967 | 571.0784 | 587.4009 | 676.3886 | 565.663
3039.3167 | 701.885 | 464.3872 | 585.0895 | 643.404 | 568.5213 | 587.6643 | 676.4169 | 565.9553
3040.3167 | 705.8339 | 464.498 | 586.7884 | 644.6452 | 566.5012 | 587.2408 | 676.2424 | 565.96
3041.3167 | 707.4155 | 464.5651 | 588.0071 | 644.7724 | 565.3436 | 586.4116 | 675.9819 | 565.9029
3042.3167 | 707.1821 | 464.7194 | 590.2982 | 650.2944 | 564.2133 | 586.0925 | 675.8963 | 565.9789
3043.3167 | 708.005 | 464.8613 | 590.7988 | 651.3286 | 562.7786 | 585.9957 | 675.8582 | 566.081
3044.3167 | 711.0518 | 465.0032 | 591.595 | 652.044 | 563.2293 | 585.7894 | 675.7709 | 566.154
3045.3167 | 712.2938 | 465.1423 | 588.7837 | 649.3412 | 566.1459 | 585.5706 | 675.6329 | 566.2531
3046.3167 | 709.7907 | 465.2726 | 586.6856 | 645.3048 | 565.8196 | 585.4225 | 675.5188 | 566.3587
3047.3167 | 708.2182 | 465.4092 | 584.718 | 647.4726 | 565.3813 | 584.9604 | 675.348 | 566.3981
3048.3167 | 707.4938 | 465.5409 | 585.1457 | 644.7795 | 567.709 | 584.8132 | 675.1741 | 566.4756
3049.3167 | 704.9257 | 465.6681 | 582.4893 | 644.3129 | 570.9682 | 584.5239 | 675.0663 | 566.5487
3050.3167 | 701.9899 | 465.8092 | 583.0446 | 647.0274 | 571.2085 | 584.1148 | 674.9686 | 566.6252
3051.3167 | 699.7479 | 465.9367 | 583.2455 | 647.277 | 571.0738 | 584.0306 | 674.877 | 566.7309
3052.3167 | 697.6054 | 466.0695 | 583.1272 | 644.9218 | 568.5273 | 583.9243 | 674.7998 | 566.8107
3053.3167 | 697.3903 | 466.2089 | 585.5303 | 646.7807 | 565.7041 | 583.6319 | 674.6641 | 566.8765
3054.3167 | 699.1594 | 466.3432 | 585.3759 | 644.9336 | 563.3465 | 583.5543 | 674.4726 | 566.9547
3055.3167 | 700.0785 | 466.4773 | 586.8826 | 645.3788 | 561.6524 | 583.4005 | 674.3176 | 567.0197
3056.3167 | 701.1142 | 466.6177 | 588.8516 | 648.2309 | 560.3521 | 583.3011 | 674.1775 | 567.0849
3057.3167 | 701.858 | 466.7466 | 588.1172 | 653.7064 | 561.3075 | 583.2441 | 674.0234 | 567.1512
3058.3167 | 704.6656 | 466.8876 | 587.8306 | 655.1384 | 563.4231 | 583.092 | 673.8919 | 567.2131
3059.3167 | 704.8375 | 467.0299 | 586.203 | 655.1402 | 565.2416 | 582.9975 | 673.7815 | 567.285
3060.3167 | 700.7622 | 467.1602 | 585.871 | 651.5942 | 565.9945 | 582.9361 | 673.6896 | 567.3523
3061.3167 | 697.2363 | 467.2945 | 586.4416 | 651.4406 | 564.6647 | 582.7253 | 673.6104 | 567.3977
3062.3167 | 694.7096 | 467.4435 | 586.7117 | 651.9544 | 563.1597 | 582.6498 | 673.493 | 567.4432
3063.3167 | 695.9677 | 467.5923 | 586.1386 | 652.9551 | 561.8275 | 582.5219 | 673.3839 | 567.4682
3064.3167 | 696.3606 | 467.7292 | 587.2581 | 655.4151 | 561.9371 | 582.3911 | 673.3172 | 567.4884
3065.3167 | 698.9021 | 467.8707 | 588.1247 | 657.2894 | 562.0838 | 582.2915 | 673.2305 | 567.5171
3066.3167 | 696.9339 | 468.0131 | 587.5398 | 654.3475 | 562.5727 | 582.3216 | 673.156 | 567.566
3067.3167 | 698.2446 | 468.1669 | 586.8456 | 655.9358 | 561.4619 | 582.1393 | 673.1154 | 567.5853
3068.3167 | 701.0839 | 468.3182 | 586.9981 | 655.8501 | 561.0423 | 582.161 | 673.0911 | 567.6112
3069.3167 | 701.0325 | 468.4552 | 587.7314 | 653.5398 | 561.046 | 582.0843 | 673.0658 | 567.6359
3070.3167 | 700.0401 | 468.6066 | 588.9046 | 653.2898 | 560.2608 | 582.0447 | 673.075 | 567.6615
3071.3167 | 701.7046 | 468.7408 | 588.9579 | 652.1568 | 560.1377 | 582.0969 | 673.0215 | 567.6819
3072.3167 | 702.9495 | 468.8768 | 587.331 | 650.1019 | 561.1534 | 582.0028 | 672.9173 | 567.7076
3073.3167 | 706.5337 | 469.0286 | 587.6536 | 651.3577 | 561.8292 | 581.9399 | 672.8367 | 567.7343
3074.3167 | 705.8795 | 469.1788 | 586.8935 | 648.5679 | 564.7275 | 582.0501 | 672.7021 | 567.7769
3075.3167 | 707.2407 | 469.3169 | 586.7813 | 648.9738 | 565.0128 | 581.824 | 672.6597 | 567.783
3076.3167 | 704.7284 | 469.4627 | 586.9302 | 647.4695 | 565.8855 | 581.8504 | 672.5867 | 567.8172
3077.3167 | 700.3304 | 469.6088 | 586.4319 | 646.8542 | 564.7771 | 581.84 | 672.5141 | 567.8335
3078.3167 | 697.6657 | 469.7503 | 583.0748 | 644.7654 | 564.0268 | 581.915 | 672.4383 | 567.8553
3079.3167 | 696.9429 | 469.9096 | 580.318 | 643.8623 | 564.3374 | 581.7966 | 672.3647 | 567.8832
3080.3167 | 696.1236 | 470.0514 | 580.9608 | 642.1446 | 565.7683 | 581.6726 | 672.2907 | 567.9473
3081.3167 | 698.394 | 470.1991 | 583.2074 | 642.2824 | 565.4891 | 581.4821 | 672.2864 | 567.9884
3082.3167 | 702.2638 | 470.3572 | 585.3219 | 641.154 | 563.3642 | 581.5942 | 672.3101 | 568.0411
3083.3167 | 704.7521 | 470.5067 | 585.4041 | 638.5828 | 560.8996 | 581.5926 | 672.3097 | 568.0773
3084.3167 | 707.4483 | 470.6678 | 587.2164 | 637.081 | 558.7902 | 581.7549 | 672.2641 | 568.0813
3085.3167 | 707.8877 | 470.8202 | 586.2053 | 636.1241 | 558.6629 | 581.7986 | 672.1849 | 568.0847
3086.3167 | 706.7828 | 470.982 | 585.4622 | 637.2238 | 558.7798 | 581.7181 | 672.0697 | 568.0933
3087.3167 | 706.0412 | 471.1465 | 589.6629 | 639.8408 | 559.6557 | 581.6188 | 671.9441 | 568.1161
3088.3167 | 704.0141 | 471.309 | 589.6798 | 640.3499 | 560.8109 | 581.7752 | 671.8038 | 568.1477
3089.3167 | 704.0228 | 471.4579 | 589.8586 | 641.0355 | 561.4806 | 581.829 | 671.7111 | 568.1787
3090.3167 | 700.7483 | 471.6105 | 590.0637 | 642.2589 | 561.5519 | 581.8364 | 671.5565 | 568.1784
3091.3167 | 699.5872 | 471.7588 | 591.7518 | 643.4178 | 560.6482 | 581.8444 | 671.4542 | 568.1732
3092.3167 | 699.0419 | 471.9181 | 591.5313 | 645.1054 | 561.0998 | 581.9832 | 671.3397 | 568.1807
3093.3323 | 697.1685 | 472.0851 | 590.8942 | 642.6321 | 561.6923 | 582.1387 | 671.2452 | 568.2233
3094.3167 | 697.4245 | 472.2441 | 591.1369 | 642.7708 | 561.8933 | 582.2086 | 671.1233 | 568.2321
3095.3167 | 700.9178 | 472.3964 | 593.7469 | 642.5526 | 564.3034 | 582.318 | 671.0985 | 568.2486
3096.3167 | 701.8878 | 472.5608 | 591.8266 | 641.7184 | 564.939 | 582.3387 | 671.0009 | 568.2578
3097.3167 | 700.7235 | 472.7164 | 591.5193 | 642.3609 | 565.7893 | 582.3645 | 670.9237 | 568.2693
3098.3167 | 699.5635 | 472.8705 | 592.2079 | 644.0958 | 565.4015 | 582.345 | 670.8044 | 568.2549
3099.3167 | 701.8521 | 473.032 | 590.9951 | 645.8221 | 565.9301 | 582.4082 | 670.654 | 568.2449
3100.3167 | 704.3323 | 473.1942 | 590.6404 | 647.518 | 566.1533 | 582.5272 | 670.573 | 568.262
3101.3167 | 706.7037 | 473.3503 | 589.4288 | 647.1684 | 564.712 | 582.5758 | 670.5122 | 568.2656
3102.3167 | 709.4138 | 473.5094 | 589.9053 | 646.6748 | 563.1573 | 582.6281 | 670.4713 | 568.2628
3103.3167 | 714.2572 | 473.6699 | 590.4479 | 648.5563 | 561.7359 | 582.6351 | 670.3807 | 568.2369
3104.3167 | 715.0767 | 473.8318 | 591.1712 | 648.5024 | 560.493 | 582.6952 | 670.3213 | 568.2483
3105.3167 | 714.1946 | 473.9984 | 591.0058 | 648.4147 | 559.2999 | 582.7309 | 670.2551 | 568.252
3106.3167 | 712.7237 | 474.1636 | 591.0358 | 647.4995 | 557.8761 | 582.9645 | 670.1712 | 568.2352
3107.3167 | 711.908 | 474.3301 | 589.1235 | 646.1758 | 556.2337 | 583.089 | 670.0345 | 568.2094
3108.3167 | 714.0735 | 474.4958 | 588.2095 | 645.4184 | 556.4149 | 583.2243 | 669.9731 | 568.2094
3109.3167 | 713.0807 | 474.6556 | 587.7609 | 650.728 | 557.8419 | 583.3558 | 669.8884 | 568.2045
3110.3167 | 713.659 | 474.8134 | 589.8813 | 649.4576 | 559.3398 | 583.4587 | 669.7994 | 568.2028
3111.3167 | 714.8876 | 474.9814 | 588.9643 | 649.4987 | 558.5006 | 583.4083 | 669.6761 | 568.1777
3112.3167 | 712.2835 | 475.1441 | 586.9242 | 647.0733 | 558.3467 | 583.738 | 669.5447 | 568.1956
3113.3167 | 710.0864 | 475.3056 | 585.9722 | 646.3121 | 558.0224 | 583.7767 | 669.4533 | 568.1913
3114.3167 | 706.0444 | 475.4763 | 585.4868 | 643.9098 | 557.5927 | 583.9656 | 669.3544 | 568.1954
3115.3167 | 707.4276 | 475.6533 | 585.2722 | 643.6154 | 556.5794 | 583.9425 | 669.2705 | 568.1705
3116.3167 | 707.6169 | 475.8299 | 586.362 | 643.0869 | 556.8096 | 584.018 | 669.2115 | 568.1568
3117.3167 | 706.7606 | 476.0057 | 586.2273 | 646.9126 | 557.6383 | 584.0557 | 669.1128 | 568.1455
3118.3167 | 702.8315 | 476.1705 | 584.187 | 643.8025 | 557.4552 | 584.1998 | 669.0268 | 568.137
3119.3167 | 700.6362 | 476.3533 | 581.1367 | 640.5324 | 557.1273 | 584.1833 | 668.9657 | 568.098
3120.3167 | 700.8514 | 476.5163 | 580.2457 | 641.455 | 558.458 | 584.0688 | 668.8889 | 568.0753
3121.3167 | 700.7122 | 476.6969 | 581.2557 | 642.5838 | 558.6321 | 583.9823 | 668.8141 | 568.0489
3122.3167 | 702.6833 | 476.8711 | 583.9873 | 641.6044 | 558.3774 | 584.0533 | 668.747 | 568.0209
3123.3323 | 702.347 | 477.0556 | 583.0907 | 642.8793 | 558.5997 | 584.1777 | 668.6717 | 568.0084
3124.3167 | 703.9529 | 477.2445 | 581.6905 | 643.3564 | 559.8281 | 584.2005 | 668.6297 | 567.9788
3125.3167 | 706.3824 | 477.4255 | 585.0389 | 644.5727 | 560.5927 | 584.1782 | 668.5677 | 567.9608
3126.3167 | 712.9407 | 477.6101 | 584.2192 | 644.8189 | 560.2283 | 584.1713 | 668.5057 | 567.9326
3127.3167 | 715.2884 | 477.799 | 582.5088 | 644.8139 | 559.4678 | 584.2714 | 668.4619 | 567.9257
3128.3167 | 715.792 | 477.9815 | 581.4356 | 645.6882 | 558.3239 | 584.3857 | 668.4301 | 567.9092
3129.3167 | 713.4336 | 478.1694 | 580.4386 | 644.3439 | 557.9208 | 584.4906 | 668.3535 | 567.8779
3130.3167 | 715.3563 | 478.3432 | 579.282 | 641.9042 | 559.3353 | 584.4391 | 668.2741 | 567.8441
3131.3167 | 717.605 | 478.5365 | 577.4801 | 639.8664 | 560.4938 | 584.5799 | 668.2098 | 567.8366
3132.3167 | 722.1471 | 478.7231 | 576.535 | 638.8095 | 562.1578 | 584.491 | 668.0862 | 567.833
3133.3167 | 718.3994 | 478.9045 | 574.9649 | 635.9087 | 563.3754 | 584.5552 | 667.9076 | 567.8188
3134.3167 | 717.8538 | 479.0962 | 577.4133 | 635.2432 | 563.2848 | 584.4914 | 667.7979 | 567.7947
3135.3167 | 717.3372 | 479.289 | 577.4498 | 635.8361 | 564.2986 | 584.4712 | 667.6498 | 567.7803
3136.3167 | 717.6109 | 479.4867 | 577.2769 | 637.8596 | 564.2246 | 584.3976 | 667.5239 | 567.7851
3137.3167 | 716.9506 | 479.6862 | 577.0543 | 637.7928 | 563.8164 | 584.4408 | 667.3961 | 567.7539
3138.3167 | 715.3539 | 479.8798 | 576.5682 | 637.1835 | 564.1328 | 584.564 | 667.2616 | 567.7631
3139.3167 | 719.1414 | 480.0825 | 577.8433 | 638.1376 | 565.9607 | 584.341 | 667.1646 | 567.7398
3140.3167 | 719.2763 | 480.2802 | 578.2977 | 634.6915 | 565.2453 | 584.5534 | 667.1134 | 567.7824
3141.3167 | 723.3987 | 480.4783 | 579.1329 | 634.2049 | 563.4444 | 584.5811 | 667.0282 | 567.7617
3142.3167 | 724.6328 | 480.6742 | 579.8287 | 635.4891 | 562.198 | 584.6735 | 666.9247 | 567.7423
3143.3167 | 723.096 | 480.8888 | 580.8224 | 636.3904 | 562.2421 | 584.6599 | 666.8401 | 567.7249
3144.3167 | 719.7217 | 481.0851 | 580.5038 | 635.2425 | 560.8059 | 584.7996 | 666.7309 | 567.7183
3145.3167 | 718.1856 | 481.2997 | 580.4464 | 634.5087 | 558.7304 | 584.8291 | 666.6103 | 567.6848
3146.3167 | 718.0174 | 481.5135 | 581.198 | 634.7933 | 557.6019 | 584.9419 | 666.4227 | 567.6584
3147.3167 | 715.4409 | 481.6982 | 582.3141 | 640.3928 | 557.9174 | 584.9307 | 666.2911 | 567.621
3148.3167 | 715.6151 | 481.8987 | 581.0332 | 640.3435 | 557.7978 | 584.8999 | 666.1386 | 567.614
3149.3167 | 716.4566 | 482.1028 | 582.5438 | 640.1216 | 558.8159 | 585.0083 | 665.9897 | 567.5989
3150.3167 | 712.1167 | 482.3009 | 581.8027 | 637.7426 | 558.1075 | 585.0757 | 665.8588 | 567.5957
3151.3167 | 710.9592 | 482.4933 | 582.6713 | 640.488 | 558.002 | 584.9481 | 665.724 | 567.562
3152.3167 | 714.3594 | 482.6946 | 584.9204 | 643.228 | 559.8783 | 584.9475 | 665.6178 | 567.554
3153.3167 | 717.9834 | 482.8995 | 585.3084 | 643.3801 | 559.5412 | 585.0518 | 665.5376 | 567.5476
3154.3167 | 719.5274 | 483.1096 | 585.7773 | 643.3623 | 558.1101 | 585.1316 | 665.4609 | 567.5519
3155.3167 | 719.7101 | 483.3203 | 585.4027 | 640.9462 | 557.2544 | 585.2248 | 665.3837 | 567.5144
3156.3167 | 719.3984 | 483.5402 | 586.1698 | 640.8944 | 557.018 | 585.275 | 665.2916 | 567.505
3157.3167 | 720.6297 | 483.7484 | 585.4106 | 642.2219 | 556.327 | 585.3133 | 665.1772 | 567.4841
3158.3167 | 724.2382 | 483.9629 | 585.238 | 644.18 | 555.521 | 585.3982 | 665.1378 | 567.4808
3159.3167 | 724.5613 | 484.1693 | 583.9082 | 642.8002 | 554.8313 | 585.608 | 665.0899 | 567.465
3160.3167 | 719.5211 | 484.3811 | 580.9269 | 640.668 | 555.0279 | 585.7908 | 665.0097 | 567.4591
3161.3167 | 716.03 | 484.5952 | 577.6796 | 639.4353 | 554.4584 | 585.7931 | 664.9335 | 567.4451
3162.3167 | 714.9135 | 484.8078 | 575.7121 | 637.4042 | 554.1305 | 585.7286 | 664.8072 | 567.4371
3163.3167 | 714.8513 | 485.0197 | 575.1181 | 634.4024 | 555.324 | 585.7856 | 664.6851 | 567.4312
3164.3167 | 711.2091 | 485.244 | 575.0206 | 632.8852 | 556.0221 | 585.7538 | 664.531 | 567.4166
3165.3167 | 710.3665 | 485.4586 | 576.439 | 635.0384 | 556.5306 | 585.682 | 664.3811 | 567.408
3166.3167 | 709.2702 | 485.6775 | 576.082 | 634.9872 | 557.7468 | 585.6215 | 664.2272 | 567.3986
3167.3167 | 708.172 | 485.9033 | 575.715 | 635.5956 | 558.4356 | 585.5863 | 664.0933 | 567.3775
3168.3167 | 709.5149 | 486.126 | 578.3125 | 635.4113 | 560.6095 | 585.638 | 663.9647 | 567.3735
3169.3167 | 707.1686 | 486.3589 | 577.2685 | 632.2788 | 561.0292 | 585.741 | 663.8745 | 567.3783
3170.3167 | 704.9527 | 486.5774 | 575.054 | 631.1168 | 560.3244 | 585.7094 | 663.7415 | 567.3754
3171.3167 | 705.6506 | 486.8084 | 573.8987 | 629.3954 | 561.9332 | 585.6992 | 663.6064 | 567.3544
3172.3167 | 708.4531 | 487.0299 | 573.615 | 628.1115 | 563.1679 | 585.6717 | 663.4449 | 567.3503
3173.3167 | 706.9176 | 487.2648 | 571.8931 | 626.0531 | 563.7393 | 585.6286 | 663.3486 | 567.3614
3174.3167 | 706.4446 | 487.5075 | 574.3951 | 628.5701 | 563.7499 | 585.5113 | 663.2237 | 567.3485
3175.3167 | 705.8715 | 487.7243 | 573.4375 | 627.8326 | 562.8018 | 585.5426 | 663.0997 | 567.3469
3176.3167 | 705.7538 | 487.9616 | 571.8509 | 628.0685 | 563.1917 | 585.5251 | 662.976 | 567.3566
3177.3167 | 707.8058 | 488.1906 | 570.5711 | 627.6972 | 563.2566 | 585.4662 | 662.861 | 567.3392
3178.3167 | 711.4603 | 488.4246 | 569.9002 | 629.1175 | 565.5514 | 585.4094 | 662.7588 | 567.3257
3179.3167 | 715.3016 | 488.6629 | 567.9162 | 630.465 | 566.0549 | 585.3783 | 662.6471 | 567.3291
3180.3167 | 714.6328 | 488.9024 | 566.3618 | 629.1603 | 565.1502 | 585.3116 | 662.5172 | 567.3425
3181.3167 | 715.1331 | 489.1362 | 568.2755 | 629.224 | 563.658 | 585.1518 | 662.3653 | 567.3311
3182.3167 | 717.4205 | 489.3825 | 572.3999 | 629.6847 | 561.3889 | 585.1258 | 662.2645 | 567.3207
3183.3167 | 719.0955 | 489.6222 | 575.7988 | 628.9778 | 558.7266 | 585.1859 | 662.2323 | 567.3177
3184.3167 | 722.4974 | 489.8599 | 576.9292 | 629.5132 | 556.5488 | 585.1852 | 662.1141 | 567.306
3185.3167 | 725.8261 | 490.0976 | 579.5219 | 630.4683 | 554.7551 | 585.2942 | 661.957 | 567.3055
3186.3167 | 728.6873 | 490.34 | 582.3623 | 631.6553 | 553.5943 | 585.3171 | 661.8235 | 567.2776
3187.3167 | 726.1037 | 490.5842 | 584.4559 | 632.4568 | 552.2893 | 585.4974 | 661.6999 | 567.2529
3188.3167 | 725.9684 | 490.8376 | 585.5932 | 634.5912 | 551.9347 | 585.6063 | 661.5472 | 567.2083
3189.3167 | 725.1168 | 491.0882 | 585.7483 | 634.7346 | 550.7607 | 585.7851 | 661.3753 | 567.1954
3190.3167 | 724.4013 | 491.3271 | 587.2588 | 635.8679 | 552.799 | 585.9053 | 661.2233 | 567.1605
3191.3167 | 726.1226 | 491.5667 | 587.7146 | 638.2756 | 554.692 | 585.9613 | 661.1231 | 567.1485
3192.3167 | 729.4016 | 491.8161 | 586.5425 | 637.7197 | 555.2375 | 586.1066 | 661.0401 | 567.1484
3193.3167 | 729.6963 | 492.0658 | 584.5967 | 635.7871 | 554.3694 | 586.3148 | 660.9507 | 567.1476
3194.3167 | 729.1397 | 492.3185 | 583.794 | 634.4652 | 552.7785 | 586.3428 | 660.7932 | 567.1256
3195.3167 | 728.2892 | 492.5642 | 583.1017 | 631.3454 | 551.5765 | 586.5432 | 660.6206 | 567.1364
3196.3167 | 724.8836 | 492.8108 | 580.8989 | 628.7241 | 551.0728 | 586.6591 | 660.4232 | 567.0985
3197.3167 | 725.1159 | 493.0468 | 580.1777 | 629.1354 | 552.5393 | 586.5653 | 660.2701 | 567.064
3198.3167 | 725.5194 | 493.2997 | 581.1081 | 631.4546 | 554.2186 | 586.5118 | 660.1298 | 567.0489
3199.3167 | 726.1256 | 493.5532 | 582.0443 | 634.6696 | 554.4436 | 586.4648 | 659.9867 | 567.02
3200.3167 | 726.9524 | 493.8055 | 581.9937 | 635.8727 | 554.8497 | 586.6467 | 659.8512 | 566.9916
3201.3167 | 727.9246 | 494.0504 | 579.8443 | 636.2856 | 555.9232 | 586.6351 | 659.7352 | 566.9749
3202.3167 | 729.2061 | 494.3087 | 578.8671 | 636.9983 | 556.8333 | 586.6779 | 659.6192 | 566.9474
3203.3167 | 726.6601 | 494.5647 | 578.0206 | 635.6276 | 557.0565 | 586.7997 | 659.4978 | 566.9686
3204.3167 | 723.0619 | 494.8319 | 578.1663 | 634.1341 | 557.1104 | 586.7932 | 659.3754 | 566.9567
3205.3167 | 718.2217 | 495.0943 | 578.0052 | 633.0734 | 555.9491 | 586.9041 | 659.2305 | 566.9392
3206.3167 | 716.9228 | 495.3682 | 577.1121 | 634.1125 | 555.5759 | 586.9467 | 659.1257 | 566.9195
3207.3167 | 714.0199 | 495.6344 | 576.4901 | 632.4443 | 556.438 | 586.9784 | 658.9596 | 566.9223
3208.3167 | 711.0143 | 495.9055 | 575.0141 | 630.488 | 558.0963 | 587.0367 | 658.799 | 566.9035
3209.3167 | 710.0754 | 496.178 | 572.8629 | 628.6694 | 558.9453 | 587.0779 | 658.6615 | 566.8878
3210.3167 | 712.0415 | 496.4406 | 571.5129 | 628.7279 | 561.256 | 586.9891 | 658.5273 | 566.8929
3211.3167 | 717.3872 | 496.72 | 572.3722 | 633.18 | 563.3561 | 586.8251 | 658.4075 | 566.8744
3212.3167 | 721.0501 | 496.9904 | 571.8036 | 632.4909 | 563.9153 | 586.8128 | 658.3623 | 566.9077
3213.3167 | 724.1125 | 497.2777 | 570.6126 | 632.672 | 564.0124 | 586.7953 | 658.2673 | 566.9344
3214.3167 | 726.1268 | 497.5564 | 569.6092 | 633.9974 | 563.8075 | 586.6738 | 658.1319 | 566.9392
3215.3167 | 728.8698 | 497.8451 | 569.2905 | 632.2846 | 563.1876 | 586.6264 | 658.0033 | 566.9606
3216.3167 | 729.7627 | 498.1263 | 570.5116 | 632.5109 | 561.8225 | 586.5853 | 657.899 | 566.9639
3217.3167 | 730.4197 | 498.4234 | 571.3937 | 631.3761 | 560.5329 | 586.6281 | 657.7916 | 566.9758
3218.3167 | 730.1201 | 498.7254 | 571.9376 | 628.7584 | 558.6725 | 586.6825 | 657.6484 | 566.9625
3219.3167 | 728.6254 | 499.02 | 571.6886 | 627.3929 | 561.8037 | 586.7213 | 657.4759 | 566.9605
3220.3167 | 724.8078 | 499.3201 | 569.3635 | 626.2478 | 562.9652 | 586.7776 | 657.3349 | 566.978
3221.3167 | 720.4981 | 499.6322 | 568.383 | 625.259 | 563.3542 | 586.7087 | 657.1781 | 566.9869
3222.3167 | 719.0042 | 499.9406 | 567.2028 | 625.4558 | 563.7565 | 586.5777 | 657.0162 | 566.9941
3223.3167 | 720.935 | 500.1221 | 568.4397 | 626.9722 | 564.0999 | 586.5111 | 656.8669 | 567.0157
3224.3167 | 722.3271 | 500.4213 | 569.4184 | 628.0574 | 562.7091 | 586.3346 | 656.6992 | 567.0413
3225.3167 | 724.2935 | 500.7483 | 570.1374 | 629.4869 | 561.1113 | 586.3638 | 656.5519 | 567.0548
3226.3167 | 724.81 | 501.0753 | 569.4063 | 627.6946 | 559.8368 | 586.3998 | 656.4336 | 567.0753
3227.3167 | 726.5142 | 501.3937 | 570.0289 | 628.9495 | 560.699 | 586.2613 | 656.2994 | 567.0806
3228.3167 | 727.8319 | 501.7335 | 571.8768 | 630.7401 | 563.6119 | 586.2769 | 656.2015 | 567.1023
3229.3167 | 728.7606 | 502.0605 | 572.6383 | 631.4676 | 565.6535 | 586.1635 | 656.1206 | 567.1213
3230.3167 | 727.4852 | 502.4004 | 573.0043 | 630.6437 | 564.1674 | 586.1935 | 656.0092 | 567.1499
3231.3167 | 728.0472 | 502.733 | 572.9407 | 631.2828 | 563.2643 | 586.1623 | 655.855 | 567.1591
3232.3167 | 727.4521 | 503.0736 | 575.1006 | 632.2424 | 564.1611 | 586.0072 | 655.7689 | 567.1642
3233.3167 | 726.5658 | 503.4166 | 576.8571 | 633.7286 | 564.5263 | 585.9925 | 655.6437 | 567.1864
3234.3167 | 725.3032 | 503.7657 | 576.3315 | 633.5405 | 564.9109 | 586.1346 | 655.5035 | 567.2216
3235.3167 | 723.6745 | 504.1134 | 575.6364 | 631.533 | 563.2218 | 586.1668 | 655.3706 | 567.2466
3236.3167 | 720.6041 | 504.4748 | 574.802 | 630.2401 | 561.6819 | 586.1855 | 655.2464 | 567.2463
3237.3167 | 717.7356 | 504.8167 | 572.4071 | 628.1887 | 561.0759 | 586.2287 | 655.1232 | 567.2521
3238.3167 | 713.7535 | 505.1719 | 570.0457 | 626.1845 | 560.2343 | 586.1443 | 655.0242 | 567.2689
3239.3167 | 712.81 | 505.5269 | 570.701 | 626.4589 | 559.5547 | 586.0945 | 654.8955 | 567.2892
3240.3167 | 712.1643 | 505.8816 | 571.5588 | 626.3722 | 559.4733 | 586.0683 | 654.7544 | 567.314
3241.3167 | 716.7311 | 506.2437 | 572.6855 | 628.8344 | 559.4178 | 586.0788 | 654.6835 | 567.3217
3242.3167 | 720.6936 | 506.6005 | 569.8979 | 627.768 | 560.1865 | 586.1222 | 654.6455 | 567.3489
3243.3167 | 720.8459 | 506.9614 | 568.5081 | 627.5831 | 559.7391 | 586.0407 | 654.57 | 567.3707
3244.3167 | 723.5349 | 507.3268 | 569.1587 | 628.3744 | 561.0538 | 585.9173 | 654.4961 | 567.3608
3245.3167 | 728.1396 | 507.6897 | 570.162 | 631.0605 | 561.3594 | 585.732 | 654.4331 | 567.3555
3246.3167 | 726.884 | 508.0621 | 573.8848 | 631.891 | 559.4059 | 585.7541 | 654.3826 | 567.378
3247.3167 | 724.2683 | 508.4343 | 574.0669 | 630.6487 | 557.6336 | 585.8042 | 654.3371 | 567.3625
3248.3167 | 723.9277 | 508.8076 | 572.758 | 627.8516 | 555.5942 | 585.9584 | 654.2428 | 567.3672
3249.3167 | 721.0137 | 509.1788 | 571.1772 | 625.2866 | 554.434 | 585.9815 | 654.1643 | 567.348
3250.3167 | 719.0618 | 509.541 | 570.3818 | 623.2829 | 555.9876 | 585.9896 | 654.0567 | 567.3232
3251.3167 | 721.042 | 509.9105 | 568.8212 | 621.0107 | 558.0369 | 586.0794 | 653.9699 | 567.3377
3252.3167 | 720.1365 | 510.2847 | 565.778 | 617.6342 | 559.1902 | 586.1112 | 653.8298 | 567.3556
3253.3167 | 718.725 | 510.6534 | 562.6407 | 614.6634 | 559.6696 | 586.0798 | 653.6742 | 567.3484
3254.3167 | 714.7378 | 511.0298 | 560.01 | 612.3983 | 558.8829 | 585.9373 | 653.535 | 567.3374
3255.3167 | 712.3681 | 511.41 | 559.4199 | 612.0325 | 557.202 | 585.7744 | 653.3799 | 567.3481
3256.3167 | 710.4123 | 511.7764 | 559.6399 | 612.8038 | 555.894 | 585.6418 | 653.2031 | 567.3415
3257.3167 | 709.344 | 512.1483 | 561.1348 | 614.6556 | 556.6885 | 585.5164 | 653.0321 | 567.3422
3258.3167 | 707.1196 | 512.5261 | 561.2755 | 615.054 | 555.944 | 585.3729 | 652.9135 | 567.3454
3259.3167 | 708.0379 | 512.9019 | 563.4201 | 617.9036 | 555.638 | 585.2065 | 652.7864 | 567.3479
3260.3167 | 708.0257 | 513.2785 | 564.8445 | 617.3378 | 555.8842 | 585.3269 | 652.6699 | 567.3516
3261.3167 | 705.3857 | 513.6614 | 562.8096 | 615.6222 | 554.77 | 585.3562 | 652.5638 | 567.3477
3262.3167 | 705.2756 | 514.0279 | 562.5553 | 615.1935 | 554.2438 | 585.315 | 652.4753 | 567.3265
3263.3167 | 708.2455 | 514.4027 | 563.7242 | 618.7176 | 555.5253 | 585.123 | 652.3863 | 567.2909
3264.3167 | 708.8728 | 514.7742 | 562.8406 | 618.95 | 555.3369 | 585.1452 | 652.2672 | 567.2855
3265.3167 | 707.0317 | 515.141 | 562.5265 | 618.497 | 556.0504 | 585.0571 | 652.1818 | 567.2671
3266.3167 | 709.5069 | 515.52 | 564.247 | 619.8857 | 555.8905 | 584.8925 | 652.0876 | 567.2509
3267.3167 | 710.6728 | 515.8949 | 565.9317 | 620.276 | 555.7234 | 584.8809 | 651.9751 | 567.2348
3268.3167 | 711.8274 | 516.2767 | 565.2098 | 619.3744 | 554.8401 | 584.8627 | 651.8264 | 567.2087
3269.3167 | 711.5251 | 516.6498 | 565.8221 | 618.4066 | 553.877 | 584.8585 | 651.7059 | 567.203
3270.3167 | 710.4485 | 517.0183 | 566.8439 | 619.9 | 554.2512 | 584.7594 | 651.678 | 567.1834
3271.3167 | 710.6915 | 517.3857 | 567.9368 | 620.4733 | 552.7216 | 584.7217 | 651.5646 | 567.1545
3272.3167 | 710.4074 | 517.7455 | 569.5179 | 620.9518 | 552.6174 | 584.6592 | 651.473 | 567.1404
3273.3167 | 711.781 | 518.1199 | 569.7871 | 620.4841 | 550.8518 | 584.6942 | 651.3703 | 567.1167
3274.3167 | 712.7885 | 518.4722 | 570.7043 | 619.2199 | 548.8241 | 584.6835 | 651.269 | 567.0615
3275.3167 | 716.6756 | 518.8369 | 571.5512 | 618.1452 | 546.8254 | 584.7658 | 651.1558 | 567.013
3276.3167 | 716.0148 | 519.2048 | 571.1944 | 615.0535 | 545.162 | 584.9209 | 651.0377 | 566.9604
3277.3167 | 715.0481 | 519.5709 | 569.5768 | 612.4954 | 543.8767 | 584.959 | 650.8532 | 566.8902
3278.3167 | 712.6748 | 519.9336 | 570.3702 | 612.4364 | 542.7878 | 584.9214 | 650.708 | 566.8135
3279.3167 | 711.8413 | 520.3011 | 572.3259 | 611.8873 | 542.8163 | 584.9305 | 650.5731 | 566.7541
3280.3167 | 714.012 | 520.6581 | 573.5949 | 610.836 | 542.6318 | 584.8709 | 650.4193 | 566.6701
3281.3167 | 717.7949 | 521.023 | 574.4288 | 614.2629 | 543.0341 | 584.819 | 650.2872 | 566.5927
3282.3167 | 721.1002 | 521.3909 | 573.5331 | 617.0511 | 542.5948 | 585.0104 | 650.1963 | 566.5422
3283.3167 | 722.8792 | 521.7514 | 571.9886 | 616.8343 | 541.7932 | 585.0417 | 650.0954 | 566.4823
3284.3167 | 722.5169 | 522.1277 | 572.0767 | 615.533 | 542.049 | 585.1112 | 649.9556 | 566.4199
3285.3167 | 722.2405 | 522.4863 | 571.429 | 613.906 | 543.7331 | 585.1881 | 649.8272 | 566.3401
3286.3167 | 721.4608 | 522.8545 | 573.984 | 614.2911 | 544.1355 | 585.1756 | 649.71 | 566.2761
3287.3167 | 720.2111 | 523.2271 | 574.0693 | 614.571 | 543.3237 | 585.2905 | 649.5716 | 566.1984
3288.3167 | 718.7107 | 523.5857 | 573.2416 | 613.4406 | 542.6636 | 585.3773 | 649.428 | 566.1181
3289.3167 | 718.5358 | 523.9603 | 573.6025 | 613.8269 | 543.3175 | 585.2654 | 649.2762 | 566.0216
3290.3167 | 715.9461 | 524.3246 | 576.2338 | 615.3599 | 544.5022 | 585.3477 | 649.1434 | 565.9547
3291.3167 | 714.0138 | 524.6782 | 576.1007 | 613.6252 | 543.1754 | 585.5332 | 648.9831 | 565.8806
3292.3167 | 713.8484 | 525.0449 | 575.6832 | 610.7479 | 541.7063 | 585.6185 | 648.8184 | 565.7793
3293.3167 | 714.1424 | 525.3988 | 575.6335 | 610.7761 | 542.1881 | 585.6547 | 648.6603 | 565.6817
3294.3167 | 714.0969 | 525.7562 | 574.9547 | 610.655 | 542.8475 | 585.74 | 648.5013 | 565.6098
3295.3167 | 714.1532 | 526.118 | 575.4437 | 612.9903 | 543.7647 | 585.7497 | 648.3634 | 565.5279
3296.3167 | 713.5088 | 526.4669 | 577.7642 | 614.9995 | 545.0279 | 585.7168 | 648.2302 | 565.4353
3297.3167 | 715.6617 | 526.827 | 578.1978 | 617.8976 | 543.3775 | 585.8132 | 648.112 | 565.3711
3298.3167 | 718.8976 | 527.174 | 577.0447 | 616.8676 | 542.0973 | 585.9329 | 647.9898 | 565.2682
3299.3167 | 718.5042 | 527.5298 | 575.636 | 616.1355 | 543.2816 | 586.0755 | 647.859 | 565.1942
3300.3167 | 719.9213 | 527.8874 | 576.7942 | 620.6291 | 546.4614 | 585.8963 | 647.7484 | 565.111
3301.3167 | 861.0705 | 578.8955 | 578.3597 | 621.3512 | 549.4722 | 586.0109 | 647.6121 | 565.0432