## Test Conditions
DESIREE-FIRE Intermediate Scale Test 9 - Circuit Simulator Data Only
Test Date: | 2010-03-17
DCSim DAQ Start Time | 13:14
DCSim Time for Synchronization | 13:15
Heat Source Synchronization | 0:00 | hour:minutes:seconds
Heat Source DAQ Start Time | 13:14
Fire Time | 13:41
Offset | 0:27 | hour:minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 1620 | seconds
Heat Source Offset | 0:26 | hour:minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 1590 | seconds
Heat Source Stop Time | 14:36
Test Duration | 0:55 | hour:minutes:seconds
| 3300 | seconds
CT500 turns | 2 | 1 or 2 | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 turns | 5 | 1 or 5
Pre-Test Baseline: | Gathered | Gathered or Not Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit Number | Cable Type |  | Cable TC Channel | Air TC Channel
SOV 1 | Kerite, 10c, 12AWG, with zinc wrap |  | Channel 4 represented as "B-Position - Kerite 10c w" in the Temperature Data File is monitoring the center of the cable sample sitting within the tray | Channel 1 represented as "B-Position - Tray - Middle" in the Temperature Data File is monitoring the air temperature in the middle of the tray at B Position.
SOV 2 | Armored Cable, 8c, 12AWG |  | There are three cable TCs monitoring internal temperatures for the armored cables in D Position. Channels 11, 12, and 13 are represented as "D Position - Armored 3'", "D Position - Armored 5'", and "D Position - Armored 7'" in the raw temperature files. | There are three cable TCs monitoring air temperatures for the armored cables in D Position. Channels 8, 9, and 10 are represented as "D Position - 3'", "D Position - Middle", and "D Position - 7'" in the raw temperature files.
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | SOV-1_CT500 | SOV-1_CT35_1_P | SOV-1_CT35_2_S1 | SOV-1_CT35_3_G | SOV-1_CT35_4_S2 | SOV-1_CT35_5_N | SOV-2_CT500 | SOV-2_CT35_1_P | SOV-2_CT35_2_S1 | SOV-2_CT35_3_G | SOV-2_CT35_4_S2 | SOV-2_CT35_5_N | SOV-1_VT7_1_R | SOV-1_VT7_2_SP | SOV-1_VT7_3_S | SOV-1_VTU_1_P | SOV-1_VTU_2_S1 | SOV-1_VTU_3_G | SOV-1_VTU_4_N | SOV-2_VT7_1_R | SOV-2_VT7_2_SP | SOV-2_VT7_3_S | SOV-2_VTU_1_P | SOV-2_VTU_2_S1 | SOV-2_VTU_3_G | SOV-2_VTU_4_N | {SOV1} V(N) - V(Batt -) | {SOV1} V(P) - V(Batt +) | {SOV1} V(R) - V(Batt -) | {SOV1} V(S) - V(Batt -) | {SOV1} V(S) - V(N) | {SOV1} V(S1) - V(Batt +) | {SOV1} V(G) - V(Batt +) | {SOV2} V(N) - V(Batt -) | {SOV2} V(P) - V(Batt +) | {SOV2} V(R) - V(Batt -) | {SOV2} V(S) - V(Batt -) | {SOV2} V(S) - V(N) | {SOV2} V(S1) - V(Batt +) | {SOV2} V(G) - V(Batt +) | {SOV1} V(P) - V(Batt -) | {SOV1} V(S1) - V(Batt -) | {SOV1} V(G) - V(Batt -) | {SOV1} V(SP) - V(Batt -) | {SOV1} V(N) - V(Batt +) | {SOV2} V(P) - V(Batt -) | {SOV2} V(S1) - V(Batt -) | {SOV1} V(G) - V(Batt -) | {SOV2} V(SP) - V(Batt -) | {SOV2} V(N) - V(Batt +)
-0.6875 | 122.1451 | -61.0107 | 61.0153 | 1.4211e-13 | -0.0038056 | 0.0021197 | 0.064218 | -0.0030042 | 0.060823 | -0.0069437 | -0.00097422 | -0.0013203 | 0.063842 | 0.0098246 | 0.062686 | -60.832 | -0.07643 | -60.8904 | 60.8806 | 60.5017 | 60.5063 | -60.9353 | -60.9324 | 0.036989 | -61.0493 | 60.7221 | 60.7763 | 60.6834 | -61.0304 | 0.075462 | -0.13473 | 0.17875 | 0.12036 | 0.044896 | -0.51363 | -0.50906 | -0.019624 | -0.29322 | 0.078319 | -0.038603 | -0.018979 | -0.23898 | -0.33193 | 121.8913 | 121.5124 | 121.517 | 60.9343 | -121.9506 | 121.7328 | 121.7871 | 121.6941 | 61.0477 | -122.0457
1.0469 | 122.1405 | -61.0794 | 60.9558 | 1.4211e-13 | -0.0038056 | 0.0019059 | 0.064218 | -0.0027904 | 0.061037 | 0.0083173 | -0.0014014 | -0.0011067 | 0.063842 | 0.0098246 | 0.062472 | -60.832 | -0.081008 | -60.895 | 60.8806 | 60.4971 | 60.5063 | -60.9307 | -60.9233 | 0.046146 | -61.0493 | 60.7221 | 60.7718 | 60.6788 | -61.0258 | 0.14871 | -0.075222 | 0.24742 | 0.18445 | 0.035739 | -0.4587 | -0.44955 | 0.05362 | -0.23371 | 0.15614 | 0.030062 | -0.023558 | -0.18405 | -0.277 | 121.96 | 121.5765 | 121.5857 | 60.9984 | -121.8865 | 121.8015 | 121.8512 | 121.7582 | 61.1256 | -121.9816
2.7812 | 122.1451 | -60.9833 | 61.0153 | 1.4211e-13 | -0.0040192 | 0.0019059 | 0.064432 | -0.0032178 | 0.061037 | 0.00068675 | -0.00097422 | -0.0013203 | 0.064056 | 0.0098246 | 0.062472 | -60.8274 | -0.07643 | -60.8904 | 60.876 | 60.4925 | 60.5017 | -60.9353 | -60.9324 | 0.03241 | -61.0539 | 60.7221 | 60.7718 | 60.6742 | -61.0304 | 0.047996 | -0.13931 | 0.15586 | 0.092892 | 0.044896 | -0.52279 | -0.51364 | -0.04709 | -0.29322 | 0.050853 | -0.070648 | -0.023558 | -0.24356 | -0.34109 | 121.8593 | 121.4758 | 121.485 | 60.9068 | -121.9506 | 121.7054 | 121.755 | 121.6575 | 61.0157 | -122.0457
4.4375 | 122.168 | -61.0199 | 60.9924 | 1.4211e-13 | -0.0040192 | 0.0023333 | 0.064218 | -0.0032178 | 0.060823 | 0.00068675 | -0.001615 | -0.0013203 | 0.063842 | 0.0098246 | 0.0629 | -60.8274 | -0.081008 | -60.8904 | 60.8806 | 60.4971 | 60.5063 | -60.9353 | -60.9278 | 0.036989 | -61.0448 | 60.7129 | 60.7763 | 60.6834 | -61.0304 | 0.084617 | -0.11184 | 0.19248 | 0.12951 | 0.044896 | -0.49532 | -0.48617 | -0.010469 | -0.27949 | 0.092053 | -0.024869 | -0.0144 | -0.21609 | -0.30904 | 121.9005 | 121.517 | 121.5262 | 60.9389 | -121.9277 | 121.7328 | 121.7962 | 121.7033 | 61.0569 | -122.0228
6.1719 | 122.1268 | -61.0794 | 60.9558 | 1.4211e-13 | -0.0033782 | 0.0021197 | 0.064218 | -0.0032178 | 0.061251 | -0.0069437 | -0.0011878 | -0.0013203 | 0.063842 | 0.009611 | 0.062472 | -60.832 | -0.081008 | -60.8858 | 60.876 | 60.4834 | 60.5063 | -60.9353 | -60.9278 | 0.041567 | -61.0448 | 60.7175 | 60.7718 | 60.6742 | -61.0349 | 0.14413 | -0.079801 | 0.24742 | 0.1936 | 0.049474 | -0.47244 | -0.44955 | 0.044462 | -0.23829 | 0.15156 | 0.034641 | -0.009821 | -0.18405 | -0.28158 | 121.9554 | 121.5628 | 121.5857 | 60.9984 | -121.8911 | 121.7969 | 121.8512 | 121.7536 | 61.121 | -121.9908
7.8906 | 122.1817 | -61.0382 | 60.9695 | 1.4211e-13 | -0.0038056 | 0.0019059 | 0.064646 | -0.0030042 | 0.061251 | -0.0069437 | -0.0014014 | -0.0011067 | 0.063629 | 0.009611 | 0.062472 | -60.8228 | -0.085587 | -60.8904 | 60.8806 | 60.4971 | 60.4971 | -60.9307 | -60.9187 | 0.041567 | -61.0448 | 60.7221 | 60.7672 | 60.6788 | -61.0349 | 0.10751 | -0.088954 | 0.21537 | 0.14782 | 0.040317 | -0.47243 | -0.47244 | 0.003263 | -0.24744 | 0.11952 | -0.006558 | -0.009821 | -0.20236 | -0.29073 | 121.9188 | 121.5353 | 121.5353 | 60.9526 | -121.9002 | 121.7603 | 121.8054 | 121.717 | 61.0798 | -122.0045
9.5625 | 122.1634 | -61.0428 | 60.9375 | 1.4211e-13 | -0.0038056 | 0.0021197 | 0.064218 | -0.0030042 | 0.061037 | -0.0069437 | -0.001615 | -0.0011067 | 0.063842 | 0.0098246 | 0.062686 | -60.8228 | -0.081008 | -60.8904 | 60.876 | 60.4971 | 60.5063 | -60.9307 | -60.9187 | 0.046146 | -61.0402 | 60.7129 | 60.7718 | 60.6697 | -61.0258 | 0.11209 | -0.06149 | 0.21995 | 0.1524 | 0.040317 | -0.44039 | -0.43124 | 0.016999 | -0.22456 | 0.1241 | 0.002598 | -0.014401 | -0.16574 | -0.26785 | 121.9188 | 121.5399 | 121.549 | 60.9618 | -121.8682 | 121.7557 | 121.8145 | 121.7124 | 61.0889 | -121.9633
11.2969 | 122.1222 | -61.0336 | 60.9558 | 1.4211e-13 | -0.0038056 | 0.0016923 | 0.064432 | -0.0030042 | 0.061037 | -0.0069437 | -0.001615 | -0.0015341 | 0.063842 | 0.0098246 | 0.062686 | -60.8274 | -0.081008 | -60.8812 | 60.876 | 60.4925 | 60.5017 | -60.9261 | -60.9233 | 0.036989 | -61.0402 | 60.7221 | 60.7763 | 60.6788 | -61.0304 | 0.10751 | -0.079801 | 0.20622 | 0.1524 | 0.044895 | -0.46328 | -0.45413 | 0.003264 | -0.23371 | 0.11036 | -0.006558 | -0.009822 | -0.17947 | -0.277 | 121.9096 | 121.5262 | 121.5353 | 60.9526 | -121.8819 | 121.7557 | 121.81 | 121.7124 | 61.0706 | -121.9862
13.0156 | 122.1176 | -60.9879 | 61.0153 | 1.4211e-13 | -0.0038056 | 0.0021197 | 0.064646 | -0.0032178 | 0.061037 | 0.0083173 | -0.0011878 | -0.0013203 | 0.063842 | 0.010038 | 0.0629 | -60.8274 | -0.081008 | -60.8858 | 60.8669 | 60.4925 | 60.5063 | -60.9261 | -60.9233 | 0.041567 | -61.0402 | 60.7129 | 60.7718 | 60.6742 | -61.0304 | 0.061732 | -0.14847 | 0.16044 | 0.10205 | 0.040316 | -0.52279 | -0.50906 | -0.042512 | -0.30238 | 0.064588 | -0.052334 | -0.009822 | -0.24356 | -0.34109 | 121.8547 | 121.4804 | 121.4941 | 60.9068 | -121.9414 | 121.7008 | 121.7596 | 121.6621 | 61.0294 | -122.0457
14.7344 | 122.113 | -61.0199 | 60.9238 | 1.4211e-13 | -0.0038056 | 0.0019059 | 0.064005 | -0.0030042 | 0.060823 | -0.014574 | -0.001615 | -0.0011067 | 0.063629 | 0.010038 | 0.062472 | -60.8228 | -0.085587 | -60.8721 | 60.876 | 60.488 | 60.5017 | -60.9215 | -60.9141 | 0.036989 | -61.0402 | 60.7129 | 60.7718 | 60.6788 | -61.0258 | 0.098354 | -0.047757 | 0.19706 | 0.14783 | 0.049472 | -0.43581 | -0.42208 | -0.00589 | -0.21083 | 0.10579 | -0.020291 | -0.014401 | -0.152 | -0.24495 | 121.8959 | 121.5078 | 121.5216 | 60.9343 | -121.8453 | 121.7328 | 121.7917 | 121.6987 | 61.0569 | -121.9496
16.4062 | 122.2549 | -60.9467 | 60.9375 | 1.4211e-13 | -0.0042328 | 0.0019059 | 0.064432 | -0.0030042 | 0.061037 | 0.00068675 | -0.00097422 | -0.0013203 | 0.063842 | 0.010038 | 0.062472 | -60.8228 | -0.081008 | -60.8766 | 60.8714 | 60.4925 | 60.5017 | -60.9261 | -60.9141 | 0.036989 | -61.0448 | 60.7129 | 60.7718 | 60.6742 | -61.0166 | 0.020533 | -0.066068 | 0.12382 | 0.070006 | 0.049473 | -0.44497 | -0.43582 | -0.069974 | -0.22456 | 0.032547 | -0.098111 | -0.028137 | -0.16574 | -0.26327 | 121.8181 | 121.4392 | 121.4483 | 60.8656 | -121.8636 | 121.6596 | 121.7184 | 121.6209 | 60.9836 | -121.9541
18.125 | 122.2 | -61.0062 | 60.91 | 1.4211e-13 | -0.0040192 | 0.0019059 | 0.064218 | -0.0030042 | 0.060823 | 0.0083173 | -0.00097422 | -0.0011067 | 0.063629 | 0.009611 | 0.062472 | -60.8228 | -0.081008 | -60.8721 | 60.8714 | 60.4834 | 60.5063 | -60.9261 | -60.9141 | 0.036989 | -61.0402 | 60.7175 | 60.7718 | 60.6651 | -61.0304 | 0.080043 | -0.038602 | 0.18333 | 0.13409 | 0.054051 | -0.42666 | -0.40377 | -0.024201 | -0.19251 | 0.092057 | -0.034023 | -0.009822 | -0.13827 | -0.24496 | 121.8776 | 121.4895 | 121.5124 | 60.9252 | -121.8362 | 121.7237 | 121.7779 | 121.6712 | 61.0432 | -121.9404
19.8438 | 122.2183 | -60.9421 | 60.9741 | 1.4211e-13 | -0.0038056 | 0.0023333 | 0.064432 | -0.0027904 | 0.060396 | -0.0069437 | -0.0014014 | -0.00089313 | 0.063629 | 0.010252 | 0.062472 | -60.8274 | -0.090166 | -60.8721 | 60.876 | 60.488 | 60.5063 | -60.9215 | -60.9141 | 0.036989 | -61.0448 | 60.7084 | 60.7718 | 60.6697 | -61.0304 | 0.020535 | -0.098111 | 0.11466 | 0.070007 | 0.049472 | -0.48617 | -0.46786 | -0.088288 | -0.26576 | 0.02797 | -0.10269 | -0.0144 | -0.20236 | -0.30447 | 121.8181 | 121.43 | 121.4483 | 60.8519 | -121.8957 | 121.6504 | 121.7138 | 121.6117 | 60.9791 | -122.0045
21.5156 | 122.1817 | -60.9879 | 60.965 | 1.4211e-13 | -0.0035918 | 0.0019059 | 0.064218 | -0.0030042 | 0.060823 | 0.00068675 | -0.0011878 | -0.0013203 | 0.063629 | 0.0098246 | 0.062472 | -60.8183 | -0.090166 | -60.8721 | 60.8669 | 60.4925 | 60.4971 | -60.9215 | -60.9095 | 0.036989 | -61.0356 | 60.7129 | 60.7672 | 60.6742 | -61.0258 | 0.066311 | -0.098112 | 0.1696 | 0.11578 | 0.049472 | -0.47243 | -0.46786 | -0.037933 | -0.25202 | 0.078324 | -0.047755 | -0.009822 | -0.19778 | -0.29073 | 121.8547 | 121.4804 | 121.485 | 60.8977 | -121.8865 | 121.7008 | 121.755 | 121.6621 | 61.0248 | -121.9908
23.25 | 122.1085 | -61.0519 | 60.9467 | 1.4211e-13 | -0.0042328 | 0.0019059 | 0.064218 | -0.0032178 | 0.06061 | -0.014574 | -0.0011878 | -0.0013203 | 0.063415 | 0.0098246 | 0.062686 | -60.8183 | -0.081008 | -60.8721 | 60.8669 | 60.4925 | 60.4971 | -60.9261 | -60.9141 | 0.036989 | -61.0356 | 60.7084 | 60.7626 | 60.6651 | -61.0212 | 0.12582 | -0.079801 | 0.23368 | 0.17987 | 0.054051 | -0.45412 | -0.44955 | 0.030733 | -0.23829 | 0.13783 | 0.016332 | -0.014401 | -0.18405 | -0.28158 | 121.9188 | 121.5445 | 121.549 | 60.9709 | -121.8728 | 121.7603 | 121.8145 | 121.717 | 61.0889 | -121.9679
24.9062 | 122.1451 | -61.0565 | 60.9146 | 1.4211e-13 | -0.0040192 | 0.0021197 | 0.064218 | -0.0030042 | 0.061037 | 0.00068675 | -0.0014014 | -0.0011067 | 0.063629 | 0.010252 | 0.062259 | -60.8228 | -0.085587 | -60.8675 | 60.8806 | 60.4834 | 60.4971 | -60.9215 | -60.9141 | 0.041567 | -61.031 | 60.7129 | 60.7763 | 60.6651 | -61.0258 | 0.13498 | -0.034023 | 0.23368 | 0.18903 | 0.05405 | -0.43124 | -0.41751 | 0.030732 | -0.20167 | 0.14241 | 0.025489 | -0.005243 | -0.13827 | -0.24954 | 121.9371 | 121.5399 | 121.5536 | 60.9709 | -121.8362 | 121.7695 | 121.8329 | 121.7216 | 61.0981 | -121.9404
26.6406 | 122.1863 | -60.9879 | 60.9467 | 1.4211e-13 | -0.0040192 | 0.0019059 | 0.064005 | -0.0032178 | 0.06061 | -0.0069437 | -0.00097422 | -0.0013203 | 0.063629 | 0.0098246 | 0.0629 | -60.8228 | -0.090166 | -60.8675 | 60.8714 | 60.4834 | 60.5017 | -60.917 | -60.9141 | 0.036989 | -61.031 | 60.7038 | 60.7672 | 60.6651 | -61.0212 | 0.07089 | -0.075223 | 0.16502 | 0.12036 | 0.049471 | -0.46328 | -0.44497 | -0.033354 | -0.24287 | 0.073746 | -0.043176 | -0.009822 | -0.17947 | -0.28158 | 121.8593 | 121.4712 | 121.4895 | 60.8977 | -121.8636 | 121.6916 | 121.755 | 121.6529 | 61.0248 | -121.9679
28.375 | 122.113 | -60.9924 | 61.0199 | 1.4211e-13 | -0.0035918 | 0.0021197 | 0.064218 | -0.0032178 | 0.060823 | 0.0083173 | -0.0014014 | -0.0011067 | 0.063629 | 0.0098246 | 0.062472 | -60.8228 | -0.085587 | -60.8675 | 60.8669 | 60.488 | 60.4971 | -60.917 | -60.905 | 0.036989 | -61.031 | 60.7084 | 60.7672 | 60.6697 | -61.0212 | 0.075468 | -0.15304 | 0.1696 | 0.12494 | 0.049471 | -0.53195 | -0.52279 | -0.028776 | -0.31153 | 0.087481 | -0.038598 | -0.009822 | -0.25271 | -0.35024 | 121.8593 | 121.4804 | 121.4895 | 60.9068 | -121.9369 | 121.7008 | 121.7596 | 121.6621 | 61.0294 | -122.0411
30.0312 | 122.2183 | -61.0153 | 60.8963 | 1.4211e-13 | -0.0040192 | 0.0019059 | 0.064646 | -0.0032178 | 0.060823 | -0.0069437 | -0.0014014 | -0.0011067 | 0.063415 | 0.0098246 | 0.062472 | -60.8137 | -0.085587 | -60.8675 | 60.8669 | 60.4788 | 60.4925 | -60.9078 | -60.905 | 0.036989 | -61.0356 | 60.7129 | 60.7672 | 60.6651 | -61.0212 | 0.10751 | -0.029447 | 0.20164 | 0.14783 | 0.040314 | -0.41751 | -0.40378 | -0.005888 | -0.18336 | 0.11037 | -0.020289 | -0.014401 | -0.12912 | -0.23122 | 121.8822 | 121.4941 | 121.5078 | 60.9297 | -121.8041 | 121.7283 | 121.7825 | 121.6804 | 61.0523 | -121.9175
31.7656 | 122.2183 | -61.0016 | 60.8871 | 1.4211e-13 | -0.0038056 | 0.0021197 | 0.064218 | -0.0027904 | 0.060823 | 0.00068675 | -0.0011878 | -0.0013203 | 0.063415 | 0.010038 | 0.062686 | -60.8183 | -0.081008 | -60.8675 | 60.8669 | 60.4742 | 60.4971 | -60.9124 | -60.905 | 0.036989 | -61.031 | 60.7084 | 60.7672 | 60.6605 | -61.0258 | 0.089201 | -0.020292 | 0.18333 | 0.13409 | 0.044893 | -0.41293 | -0.39004 | -0.0242 | -0.17878 | 0.096636 | -0.029443 | -0.005243 | -0.11996 | -0.22665 | 121.8684 | 121.4758 | 121.4987 | 60.9206 | -121.7995 | 121.7099 | 121.7688 | 121.6621 | 61.0386 | -121.9129
33.4844 | 122.1634 | -61.0062 | 60.9604 | 1.4211e-13 | -0.0042328 | 0.0021197 | 0.064218 | -0.0032178 | 0.06061 | 0.00068675 | -0.0011878 | -0.0013203 | 0.063629 | 0.0098246 | 0.062472 | -60.8183 | -0.094744 | -60.8629 | 60.8577 | 60.488 | 60.4971 | -60.9215 | -60.9095 | 0.03241 | -61.0265 | 60.6992 | 60.7626 | 60.6697 | -61.0304 | 0.084622 | -0.10269 | 0.18791 | 0.14325 | 0.058629 | -0.47244 | -0.46328 | -0.024201 | -0.26118 | 0.096635 | -0.020287 | 0.003914 | -0.19778 | -0.29073 | 121.8639 | 121.4941 | 121.5033 | 60.9114 | -121.8819 | 121.7054 | 121.7688 | 121.6758 | 61.0386 | -121.9908
35.1562 | 122.113 | -61.0657 | 60.9375 | 1.4211e-13 | -0.0042328 | 0.0021197 | 0.064218 | -0.0032178 | 0.061037 | -0.0069437 | -0.0014014 | -0.00089313 | 0.063842 | 0.010252 | 0.062472 | -60.8137 | -0.085587 | -60.8629 | 60.8669 | 60.4788 | 60.4925 | -60.9124 | -60.9095 | 0.027831 | -61.0219 | 60.7038 | 60.7672 | 60.6605 | -61.0212 | 0.15329 | -0.070646 | 0.252 | 0.20276 | 0.049472 | -0.45871 | -0.44497 | 0.044466 | -0.23372 | 0.15614 | 0.043801 | -0.000665 | -0.17032 | -0.277 | 121.9325 | 121.5445 | 121.5582 | 60.9801 | -121.8499 | 121.7695 | 121.8329 | 121.7262 | 61.0935 | -121.9587
36.875 | 122.1359 | -61.0016 | 60.9833 | 1.4211e-13 | -0.0042328 | 0.0019059 | 0.064218 | -0.0030042 | 0.060823 | 0.00068675 | -0.0011878 | -0.0013203 | 0.063629 | 0.010038 | 0.062686 | -60.8183 | -0.085587 | -60.8675 | 60.8669 | 60.4834 | 60.4879 | -60.917 | -60.9095 | 0.03241 | -61.0219 | 60.7038 | 60.7626 | 60.6605 | -61.0304 | 0.084623 | -0.11642 | 0.18333 | 0.13409 | 0.049471 | -0.4999 | -0.49533 | -0.028779 | -0.27949 | 0.092057 | -0.020286 | 0.008493 | -0.22067 | -0.32278 | 121.8684 | 121.485 | 121.4895 | 60.916 | -121.9002 | 121.7054 | 121.7642 | 121.6621 | 61.034 | -122.0136
38.5469 | 122.2183 | -60.9238 | 60.9741 | 1.4211e-13 | -0.0042328 | 0.0023333 | 0.064218 | -0.0032178 | 0.061037 | 0.00068675 | -0.0011878 | -0.0013203 | 0.063629 | 0.010466 | 0.062472 | -60.8183 | -0.090166 | -60.8675 | 60.8623 | 60.4742 | 60.4879 | -60.917 | -60.905 | 0.03241 | -61.0265 | 60.7038 | 60.7672 | 60.6605 | -61.0258 | 0.006803 | -0.11185 | 0.10551 | 0.056274 | 0.049471 | -0.49991 | -0.48617 | -0.10202 | -0.27034 | 0.018816 | -0.10269 | -0.000665 | -0.20694 | -0.31362 | 121.786 | 121.398 | 121.4117 | 60.8336 | -121.8911 | 121.6276 | 121.691 | 121.5843 | 60.9562 | -121.9999
40.2812 | 122.2275 | -60.9741 | 60.9741 | 1.4211e-13 | -0.0042328 | 0.0021197 | 0.063791 | -0.0030042 | 0.060823 | 0.00068675 | -0.00097422 | -0.0017477 | 0.063629 | 0.010038 | 0.062472 | -60.8137 | -0.085587 | -60.8583 | 60.8623 | 60.4834 | 60.4971 | -60.9124 | -60.905 | 0.036989 | -61.0265 | 60.7038 | 60.758 | 60.6605 | -61.0212 | 0.061735 | -0.11185 | 0.16044 | 0.11578 | 0.05405 | -0.49075 | -0.47702 | -0.047087 | -0.27034 | 0.06917 | -0.052331 | -0.005244 | -0.21609 | -0.31362 | 121.8364 | 121.4575 | 121.4712 | 60.8885 | -121.8865 | 121.6779 | 121.7321 | 121.6346 | 61.0111 | -121.9953
42 | 122.1909 | -60.997 | 60.9055 | 1.4211e-13 | -0.0042328 | 0.0021197 | 0.064218 | -0.0030042 | 0.061037 | 0.0083173 | -0.0011878 | -0.0013203 | 0.063629 | 0.010252 | 0.062686 | -60.8137 | -0.071851 | -60.8629 | 60.8577 | 60.4742 | 60.4971 | -60.9124 | -60.9004 | 0.036989 | -61.0265 | 60.6992 | 60.7534 | 60.6651 | -61.0212 | 0.084623 | -0.04776 | 0.18333 | 0.13409 | 0.049472 | -0.43124 | -0.40835 | -0.024199 | -0.20625 | 0.096637 | -0.029443 | -0.005244 | -0.15201 | -0.24038 | 121.8547 | 121.4712 | 121.4941 | 60.9252 | -121.8178 | 121.6962 | 121.7505 | 121.6621 | 61.034 | -121.9267
43.6562 | 122.2137 | -60.965 | 60.965 | 1.4211e-13 | -0.0042328 | 0.0021197 | 0.064005 | -0.0034314 | 0.06061 | 0.0083173 | -0.0011878 | -0.0013203 | 0.063415 | 0.010038 | 0.062472 | -60.8091 | -0.085587 | -60.8629 | 60.8669 | 60.4696 | 60.4879 | -60.9032 | -60.9095 | 0.036989 | -61.031 | 60.7038 | 60.7672 | 60.6559 | -61.0258 | 0.061738 | -0.098112 | 0.15587 | 0.10205 | 0.040314 | -0.49533 | -0.47702 | -0.060821 | -0.26118 | 0.055436 | -0.066064 | -0.005243 | -0.19778 | -0.30905 | 121.8318 | 121.4346 | 121.4529 | 60.8794 | -121.8682 | 121.6687 | 121.7321 | 121.6209 | 61.002 | -121.9908
45.375 | 122.0901 | -60.965 | 61.0199 | 1.4211e-13 | -0.0040192 | 0.0016923 | 0.064218 | -0.0032178 | 0.060823 | 0.0083173 | -0.0014014 | -0.0017477 | 0.063415 | 0.010466 | 0.062259 | -60.8137 | -0.085587 | -60.8675 | 60.8623 | 60.4834 | 60.4925 | -60.917 | -60.8958 | 0.041567 | -61.031 | 60.6992 | 60.7626 | 60.6559 | -61.0258 | 0.048002 | -0.15762 | 0.15129 | 0.097473 | 0.049471 | -0.53652 | -0.52737 | -0.060821 | -0.32069 | 0.069173 | -0.066064 | -0.005243 | -0.25729 | -0.36398 | 121.8272 | 121.4483 | 121.4575 | 60.8794 | -121.9369 | 121.6642 | 121.7276 | 121.6209 | 61.0065 | -122.0457
47.0312 | 122.2137 | -60.9283 | 60.9375 | 1.4211e-13 | -0.0044466 | 0.0021197 | 0.063791 | -0.0032178 | 0.06061 | 0.00068675 | -0.0014014 | -0.0011067 | 0.063415 | 0.010252 | 0.062045 | -60.8137 | -0.07643 | -60.8583 | 60.8623 | 60.4834 | 60.4971 | -60.917 | -60.905 | 0.027831 | -61.0265 | 60.6992 | 60.7718 | 60.6559 | -61.0212 | 0.011381 | -0.075225 | 0.11467 | 0.070009 | 0.058628 | -0.45413 | -0.4404 | -0.092863 | -0.23829 | 0.023394 | -0.098107 | -0.005244 | -0.16574 | -0.28158 | 121.7906 | 121.4117 | 121.4254 | 60.8519 | -121.8545 | 121.6276 | 121.7001 | 121.5843 | 60.9562 | -121.9587
48.75 | 122.168 | -60.9695 | 60.9375 | 1.4211e-13 | -0.0044466 | 0.0021197 | 0.064218 | -0.0032178 | 0.060396 | 0.00068675 | -0.0011878 | -0.0015341 | 0.063415 | 0.010466 | 0.062472 | -60.7999 | -0.081008 | -60.8629 | 60.8577 | 60.4788 | 60.4879 | -60.917 | -60.9004 | 0.041567 | -61.0219 | 60.7084 | 60.7626 | 60.6651 | -61.0166 | 0.052579 | -0.079803 | 0.1696 | 0.10663 | 0.05405 | -0.45871 | -0.44955 | -0.047086 | -0.22914 | 0.069171 | -0.05233 | -0.005244 | -0.17489 | -0.27242 | 121.8272 | 121.4483 | 121.4575 | 60.8885 | -121.8545 | 121.6779 | 121.7321 | 121.6346 | 61.0111 | -121.9541
50.4219 | 122.0901 | -61.0291 | 60.9055 | 1.4211e-13 | -0.0042328 | 0.0021197 | 0.064005 | -0.0032178 | 0.06061 | 0.00068675 | -0.0011878 | -0.0013203 | 0.063629 | 0.010038 | 0.062259 | -60.8045 | -0.085587 | -60.8629 | 60.8669 | 60.4742 | 60.4925 | -60.9078 | -60.905 | 0.036989 | -61.0219 | 60.6992 | 60.7672 | 60.6559 | -61.0166 | 0.12125 | -0.038603 | 0.22453 | 0.16614 | 0.044893 | -0.43124 | -0.41293 | 0.012424 | -0.20625 | 0.1241 | 0.00718 | -0.005244 | -0.13827 | -0.24954 | 121.8959 | 121.5033 | 121.5216 | 60.9435 | -121.8133 | 121.7283 | 121.7962 | 121.685 | 61.066 | -121.9221
52.0938 | 122.1405 | -61.0245 | 60.8871 | 1.4211e-13 | -0.0042328 | 0.0016923 | 0.064218 | -0.0032178 | 0.060182 | 0.00068675 | -0.0014014 | -0.0015341 | 0.063629 | 0.010466 | 0.0629 | -60.7999 | -0.081008 | -60.8583 | 60.8669 | 60.4696 | 60.4971 | -60.9078 | -60.905 | 0.03241 | -61.0173 | 60.69 | 60.7626 | 60.6559 | -61.0304 | 0.11667 | -0.020292 | 0.22453 | 0.16614 | 0.049471 | -0.41751 | -0.39004 | -0.005891 | -0.1971 | 0.11952 | 0.007181 | 0.013072 | -0.12454 | -0.23123 | 121.8913 | 121.4941 | 121.5216 | 60.9435 | -121.795 | 121.7145 | 121.7871 | 121.6804 | 61.0569 | -121.9175
53.8281 | 122.1451 | -60.9741 | 60.9375 | 1.4211e-13 | -0.0046602 | 0.0019059 | 0.064218 | -0.0030042 | 0.06061 | -0.0069437 | -0.0014014 | -0.0013203 | 0.063842 | 0.010252 | 0.062472 | -60.7999 | -0.071851 | -60.8583 | 60.8577 | 60.4742 | 60.4879 | -60.9124 | -60.8958 | 0.03241 | -61.0127 | 60.6946 | 60.7626 | 60.6605 | -61.0212 | 0.061735 | -0.079803 | 0.17418 | 0.11578 | 0.05405 | -0.46328 | -0.44955 | -0.047087 | -0.24287 | 0.078328 | -0.038594 | 0.008493 | -0.17489 | -0.277 | 121.8318 | 121.4483 | 121.4621 | 60.9023 | -121.8499 | 121.6687 | 121.7367 | 121.6346 | 61.0065 | -121.9587
55.4844 | 122.2092 | -60.9375 | 60.9375 | 1.4211e-13 | -0.0044466 | 0.0021197 | 0.064432 | -0.0032178 | 0.06061 | -0.0069437 | -0.0014014 | -0.0017477 | 0.063629 | 0.010038 | 0.062472 | -60.7999 | -0.07643 | -60.8629 | 60.8577 | 60.4742 | 60.4925 | -60.9078 | -60.9004 | 0.03241 | -61.0081 | 60.7038 | 60.7672 | 60.6559 | -61.0212 | 0.029693 | -0.079803 | 0.13756 | 0.074586 | 0.044893 | -0.46328 | -0.44497 | -0.083708 | -0.23372 | 0.037128 | -0.070637 | 0.013071 | -0.17032 | -0.28158 | 121.7952 | 121.4117 | 121.43 | 60.8611 | -121.8453 | 121.6413 | 121.7047 | 121.5934 | 60.9699 | -121.9587
57.2031 | 122.1771 | -60.9879 | 60.9421 | 1.4211e-13 | -0.0044466 | 0.0023333 | 0.064218 | -0.0032178 | 0.06061 | -0.0069437 | -0.0011878 | -0.0017477 | 0.063415 | 0.010252 | 0.062045 | -60.8045 | -0.081008 | -60.8538 | 60.8669 | 60.4696 | 60.4925 | -60.9078 | -60.9004 | 0.03241 | -61.0173 | 60.6946 | 60.7626 | 60.6559 | -61.0166 | 0.080047 | -0.075224 | 0.18333 | 0.1341 | 0.054049 | -0.47244 | -0.44955 | -0.028775 | -0.24745 | 0.087482 | -0.02944 | -0.000665 | -0.17947 | -0.28616 | 121.8547 | 121.4575 | 121.4804 | 60.9068 | -121.8499 | 121.6825 | 121.7505 | 121.6438 | 61.0203 | -121.9587
58.9219 | 122.0993 | -61.0336 | 60.9375 | 1.4211e-13 | -0.0044466 | 0.0019059 | 0.064218 | -0.0034314 | 0.060396 | 0.00068675 | -0.00097422 | -0.0011067 | 0.063415 | 0.010466 | 0.062686 | -60.8091 | -0.081008 | -60.8583 | 60.8577 | 60.4788 | 60.4925 | -60.9124 | -60.8958 | 0.03241 | -61.0127 | 60.6992 | 60.7626 | 60.6559 | -61.0212 | 0.12124 | -0.079803 | 0.22453 | 0.17529 | 0.05405 | -0.45871 | -0.44497 | 0.012422 | -0.23829 | 0.13784 | 0.020915 | 0.008493 | -0.17489 | -0.28158 | 121.8913 | 121.5124 | 121.5262 | 60.9526 | -121.8499 | 121.7328 | 121.7962 | 121.6895 | 61.066 | -121.9587
60.6562 | 122.1909 | -60.997 | 60.9009 | 1.4211e-13 | -0.004874 | 0.0021197 | 0.064432 | -0.0034314 | 0.06061 | -0.0069437 | -0.001615 | -0.0013203 | 0.063415 | 0.010466 | 0.062686 | -60.8045 | -0.07643 | -60.8583 | 60.8577 | 60.4834 | 60.4879 | -60.9124 | -60.8958 | 0.036989 | -61.0173 | 60.7038 | 60.7672 | 60.6513 | -61.0212 | 0.084623 | -0.043182 | 0.19249 | 0.13867 | 0.05405 | -0.41751 | -0.41293 | -0.024199 | -0.1971 | 0.10122 | -0.020285 | 0.003914 | -0.1337 | -0.24954 | 121.8547 | 121.4804 | 121.485 | 60.9206 | -121.8133 | 121.7008 | 121.7642 | 121.6483 | 61.034 | -121.9221
62.3281 | 122.0993 | -60.9741 | 60.9924 | 1.4211e-13 | -0.0046602 | 0.0019059 | 0.064646 | -0.0036452 | 0.060823 | 0.00068675 | -0.0011878 | -0.0011067 | 0.063201 | 0.010466 | 0.062045 | -60.7908 | -0.081008 | -60.8583 | 60.8485 | 60.4788 | 60.4834 | -60.9078 | -60.9004 | 0.036989 | -61.0173 | 60.6946 | 60.758 | 60.6605 | -61.0166 | 0.066314 | -0.14389 | 0.18333 | 0.11578 | 0.049471 | -0.51364 | -0.50906 | -0.042508 | -0.29781 | 0.073749 | -0.043173 | -0.000665 | -0.23441 | -0.33193 | 121.8227 | 121.4529 | 121.4575 | 60.8931 | -121.9002 | 121.6687 | 121.7321 | 121.6346 | 61.0111 | -122.0091
64.0469 | 122.168 | -60.9329 | 60.9558 | 1.4211e-13 | -0.0046602 | 0.0021197 | 0.064859 | -0.0034314 | 0.061037 | -0.0069437 | -0.00097422 | -0.0013203 | 0.063629 | 0.010252 | 0.062259 | -60.7954 | -0.081008 | -60.8583 | 60.8531 | 60.4788 | 60.4879 | -60.9078 | -60.905 | 0.036989 | -61.0127 | 60.6946 | 60.7534 | 60.6422 | -61.0212 | 0.025115 | -0.10269 | 0.13756 | 0.074586 | 0.049471 | -0.47702 | -0.46786 | -0.088286 | -0.26118 | 0.027971 | -0.079793 | 0.008493 | -0.20236 | -0.31363 | 121.786 | 121.4117 | 121.4209 | 60.8519 | -121.8636 | 121.6275 | 121.6864 | 121.5751 | 60.9699 | -121.977
65.7969 | 122.0535 | -61.0016 | 60.9192 | 1.4211e-13 | -0.004874 | 0.0023333 | 0.064646 | -0.0032178 | 0.060823 | 0.00068675 | -0.0011878 | -0.0013203 | 0.063415 | 0.010466 | 0.062686 | -60.7999 | -0.07643 | -60.8675 | 60.8577 | 60.4834 | 60.4925 | -60.9032 | -60.8912 | 0.036989 | -61.0127 | 60.6946 | 60.7534 | 60.6559 | -61.0121 | 0.098359 | -0.061492 | 0.20164 | 0.13409 | 0.035735 | -0.43582 | -0.42666 | -0.010463 | -0.22456 | 0.11037 | -0.011128 | -0.000665 | -0.16574 | -0.26327 | 121.8593 | 121.485 | 121.4941 | 60.9252 | -121.8224 | 121.6962 | 121.755 | 121.6575 | 61.0386 | -121.9312
67.4531 | 122.081 | -61.0016 | 60.9146 | 1.4211e-13 | -0.0042328 | 0.0025471 | 0.064859 | -0.0036452 | 0.06061 | 0.00068675 | -0.0011878 | -0.0011067 | 0.063415 | 0.010893 | 0.062686 | -60.7954 | -0.07643 | -60.8583 | 60.8531 | 60.4788 | 60.4925 | -60.9124 | -60.8912 | 0.036989 | -61.0081 | 60.6946 | 60.758 | 60.6559 | -61.0121 | 0.089201 | -0.061494 | 0.20622 | 0.14325 | 0.05405 | -0.43582 | -0.42209 | -0.010463 | -0.21999 | 0.11037 | -0.00655 | 0.003913 | -0.15659 | -0.25869 | 121.8547 | 121.4804 | 121.4941 | 60.9252 | -121.827 | 121.6962 | 121.7596 | 121.6575 | 61.0386 | -121.9267
69.1719 | 122.2092 | -60.9283 | 60.9467 | 1.4211e-13 | -0.004874 | 0.0016923 | 0.064432 | -0.0034314 | 0.060823 | 0.00068675 | -0.0011878 | -0.0013203 | 0.063629 | 0.010679 | 0.062259 | -60.7908 | -0.081008 | -60.8583 | 60.8485 | 60.4696 | 60.4879 | -60.9032 | -60.8866 | 0.027831 | -61.0127 | 60.69 | 60.7534 | 60.6468 | -61.0212 | 0.025117 | -0.098115 | 0.13756 | 0.070009 | 0.044892 | -0.47702 | -0.45871 | -0.092863 | -0.25661 | 0.041709 | -0.08437 | 0.008493 | -0.19321 | -0.29989 | 121.7769 | 121.398 | 121.4163 | 60.8473 | -121.8499 | 121.6184 | 121.6818 | 121.5751 | 60.9562 | -121.9679
70.8906 | 122.0535 | -61.0336 | 60.9238 | 1.4211e-13 | -0.0042328 | 0.0021197 | 0.064218 | -0.0038588 | 0.061037 | -0.0069437 | -0.0014014 | -0.0011067 | 0.063629 | 0.010679 | 0.062259 | -60.7999 | -0.085587 | -60.8492 | 60.8623 | 60.4742 | 60.4879 | -60.9032 | -60.8958 | 0.041567 | -61.0127 | 60.6855 | 60.7534 | 60.6513 | -61.0121 | 0.1304 | -0.061492 | 0.23369 | 0.18445 | 0.054049 | -0.44955 | -0.43582 | 0.02158 | -0.2383 | 0.13784 | 0.020915 | -0.000665 | -0.17032 | -0.27243 | 121.8959 | 121.5078 | 121.5216 | 60.948 | -121.827 | 121.7191 | 121.7871 | 121.685 | 61.0752 | -121.9358
72.6094 | 122.0718 | -61.0474 | 60.9192 | 1.4211e-13 | -0.0042328 | 0.0019059 | 0.064218 | -0.0038588 | 0.060823 | -0.014574 | -0.0011878 | -0.0011067 | 0.063629 | 0.010679 | 0.062045 | -60.7908 | -0.085587 | -60.8538 | 60.8531 | 60.4742 | 60.4834 | -60.9032 | -60.8912 | 0.041567 | -61.0036 | 60.6855 | 60.7626 | 60.6513 | -61.0166 | 0.14413 | -0.066071 | 0.25658 | 0.1936 | 0.04947 | -0.44497 | -0.43582 | 0.030734 | -0.23372 | 0.15615 | 0.043805 | 0.013071 | -0.15658 | -0.26785 | 121.9005 | 121.5216 | 121.5307 | 60.9618 | -121.8224 | 121.7328 | 121.81 | 121.6987 | 61.0889 | -121.9358
74.2656 | 122.1405 | -60.9833 | 60.91 | 1.4211e-13 | -0.004874 | 0.0019059 | 0.064646 | -0.0032178 | 0.06061 | 0.0083173 | -0.00076062 | -0.0011067 | 0.063201 | 0.010893 | 0.062259 | -60.7908 | -0.081008 | -60.8492 | 60.8531 | 60.4605 | 60.4834 | -60.9078 | -60.8912 | 0.03241 | -61.0127 | 60.6946 | 60.7534 | 60.6422 | -61.0121 | 0.075469 | -0.056916 | 0.19249 | 0.1341 | 0.058628 | -0.44956 | -0.42666 | -0.028774 | -0.21541 | 0.092061 | -0.029439 | -0.000665 | -0.15659 | -0.26785 | 121.8364 | 121.4438 | 121.4666 | 60.9023 | -121.8178 | 121.6779 | 121.7367 | 121.6255 | 61.0157 | -121.9221
76 | 122.1909 | -60.8917 | 60.965 | 1.4211e-13 | -0.004874 | 0.0023333 | 0.064432 | -0.0036452 | 0.061037 | 0.00068675 | -0.0011878 | -0.0011067 | 0.063842 | 0.010893 | 0.062045 | -60.7908 | -0.081008 | -60.8446 | 60.8485 | 60.4651 | 60.4879 | -60.8986 | -60.8866 | 0.036989 | -61.0127 | 60.6855 | 60.7534 | 60.6422 | -61.0166 | -0.006925 | -0.11643 | 0.10094 | 0.047123 | 0.054048 | -0.49991 | -0.47702 | -0.1249 | -0.2795 | 0.005088 | -0.12099 | 0.003914 | -0.21152 | -0.32278 | 121.7403 | 121.3568 | 121.3797 | 60.8107 | -121.8636 | 121.5772 | 121.6452 | 121.5339 | 60.9287 | -121.9816
77.7344 | 122.1863 | -60.9833 | 60.8231 | 1.4211e-13 | -0.004874 | 0.0019059 | 0.064646 | -0.0036452 | 0.060823 | 0.00068675 | -0.00097422 | -0.0013203 | 0.063415 | 0.010466 | 0.062045 | -60.7862 | -0.07643 | -60.8538 | 60.8485 | 60.4742 | 60.4879 | -60.8941 | -60.8866 | 0.036989 | -61.0127 | 60.6855 | 60.758 | 60.6376 | -61.0166 | 0.089206 | 0.025481 | 0.19707 | 0.12952 | 0.040312 | -0.34884 | -0.33511 | -0.033353 | -0.13759 | 0.09664 | -0.029439 | 0.003914 | -0.065033 | -0.18545 | 121.8318 | 121.4575 | 121.4712 | 60.9068 | -121.7171 | 121.6687 | 121.7413 | 121.6209 | 61.0203 | -121.8397
79.3906 | 122.1817 | -61.0016 | 60.8688 | 1.4211e-13 | -0.004874 | 0.0016923 | 0.064432 | -0.0034314 | 0.06061 | 0.00068675 | -0.0014014 | -0.00089313 | 0.063201 | 0.010893 | 0.062259 | -60.7908 | -0.07643 | -60.8492 | 60.8531 | 60.4651 | 60.4879 | -60.8986 | -60.8866 | 0.027831 | -61.0081 | 60.6855 | 60.7443 | 60.6376 | -61.0166 | 0.10294 | -0.015717 | 0.2108 | 0.15241 | 0.04947 | -0.40378 | -0.38089 | -0.015042 | -0.18336 | 0.11495 | -0.00655 | 0.008492 | -0.12454 | -0.23123 | 121.8547 | 121.4666 | 121.4895 | 60.9252 | -121.7675 | 121.6871 | 121.7459 | 121.6392 | 61.0294 | -121.8855
81.0625 | 122.1451 | -60.9787 | 60.9283 | 1.4211e-13 | -0.004874 | 0.0021197 | 0.064859 | -0.0036452 | 0.060823 | 0.0083173 | -0.0011878 | -0.0013203 | 0.063201 | 0.010679 | 0.062472 | -60.7954 | -0.090166 | -60.8492 | 60.8485 | 60.4651 | 60.4925 | -60.8986 | -60.8866 | 0.041567 | -61.0036 | 60.69 | 60.7534 | 60.6422 | -61.0166 | 0.08005 | -0.079805 | 0.18333 | 0.12952 | 0.04947 | -0.46329 | -0.43582 | -0.03793 | -0.2383 | 0.092063 | -0.024859 | 0.013071 | -0.1749 | -0.28616 | 121.8272 | 121.4438 | 121.4712 | 60.8885 | -121.827 | 121.6687 | 121.7321 | 121.6209 | 61.0203 | -121.945
82.7812 | 122.1909 | -60.997 | 60.8688 | 1.4211e-13 | -0.0050876 | 0.0021197 | 0.064646 | -0.0034314 | 0.061037 | 0.0083173 | -0.0011878 | -0.0011067 | 0.063415 | 0.010679 | 0.062259 | -60.7862 | -0.07643 | -60.8354 | 60.844 | 60.4742 | 60.4834 | -60.8941 | -60.8866 | 0.041567 | -61.0036 | 60.6855 | 60.7489 | 60.633 | -61.0075 | 0.10294 | -0.024873 | 0.2108 | 0.16156 | 0.058625 | -0.39462 | -0.38547 | -0.010463 | -0.18336 | 0.11037 | -0.006549 | 0.003914 | -0.11997 | -0.23581 | 121.841 | 121.4712 | 121.4804 | 60.9206 | -121.7629 | 121.6825 | 121.7459 | 121.63 | 61.0386 | -121.8763
84.4375 | 122.1588 | -60.9375 | 60.9375 | 1.4211e-13 | -0.0050876 | 0.0021197 | 0.064646 | -0.0032178 | 0.06061 | -0.0069437 | -0.0011878 | -0.0013203 | 0.063629 | 0.010679 | 0.062259 | -60.7862 | -0.081008 | -60.8492 | 60.844 | 60.4651 | 60.4834 | -60.8895 | -60.8866 | 0.036989 | -60.9944 | 60.6809 | 60.7489 | 60.6422 | -61.0075 | 0.048009 | -0.093538 | 0.15129 | 0.088321 | 0.040312 | -0.47244 | -0.45413 | -0.069972 | -0.25661 | 0.050864 | -0.056901 | 0.013071 | -0.18863 | -0.29532 | 121.7815 | 121.4026 | 121.4209 | 60.8565 | -121.827 | 121.6184 | 121.6864 | 121.5797 | 60.9745 | -121.945
86.1562 | 122.1954 | -60.9009 | 60.9283 | 1.4211e-13 | -0.0053012 | 0.0023333 | 0.064646 | -0.0034314 | 0.06061 | -0.0069437 | -0.0011878 | -0.0013203 | 0.063629 | 0.011107 | 0.062472 | -60.7908 | -0.07643 | -60.8446 | 60.844 | 60.4605 | 60.4879 | -60.8941 | -60.8821 | 0.036989 | -60.9944 | 60.6809 | 60.7489 | 60.6422 | -61.0075 | 0.006809 | -0.084383 | 0.11009 | 0.056278 | 0.049469 | -0.46787 | -0.4404 | -0.10659 | -0.24745 | 0.018822 | -0.093522 | 0.013071 | -0.17948 | -0.28616 | 121.7448 | 121.3614 | 121.3888 | 60.8244 | -121.8224 | 121.5818 | 121.6497 | 121.5431 | 60.9379 | -121.9358
87.875 | 122.0947 | -61.0428 | 60.878 | 1.4211e-13 | -0.0050876 | 0.0019059 | 0.064432 | -0.0034314 | 0.06061 | -0.014574 | -0.0011878 | -0.0011067 | 0.063629 | 0.011107 | 0.062045 | -60.7771 | -0.07643 | -60.8446 | 60.8485 | 60.4651 | 60.4879 | -60.8941 | -60.8866 | 0.041567 | -61.0036 | 60.6855 | 60.7489 | 60.6422 | -61.0121 | 0.14872 | -0.029451 | 0.26573 | 0.19819 | 0.049469 | -0.41293 | -0.39004 | 0.030736 | -0.19252 | 0.15615 | 0.039228 | 0.008492 | -0.12912 | -0.23581 | 121.8913 | 121.5078 | 121.5307 | 60.9664 | -121.7721 | 121.7283 | 121.7917 | 121.685 | 61.0844 | -121.89
89.5469 | 122.168 | -61.0016 | 60.8826 | 1.4211e-13 | -0.0050876 | 0.0021197 | 0.064859 | -0.0034314 | 0.06061 | -0.0069437 | -0.0011878 | -0.0017477 | 0.063629 | 0.010893 | 0.062045 | -60.7862 | -0.071851 | -60.8446 | 60.844 | 60.4559 | 60.4788 | -60.8895 | -60.8729 | 0.041567 | -61.0081 | 60.6809 | 60.7489 | 60.6376 | -61.0166 | 0.1121 | -0.038606 | 0.21538 | 0.15699 | 0.04489 | -0.42667 | -0.40378 | -0.015042 | -0.20168 | 0.12869 | -0.00655 | 0.008492 | -0.1337 | -0.24496 | 121.8455 | 121.4575 | 121.4804 | 60.9297 | -121.7721 | 121.6825 | 121.7505 | 121.6392 | 61.0432 | -121.8992
91.2812 | 122.1542 | -60.9924 | 60.8505 | 1.4211e-13 | -0.005515 | 0.0019059 | 0.064646 | -0.0036452 | 0.06061 | -0.0069437 | -0.0011878 | -0.0013203 | 0.063629 | 0.010679 | 0.062259 | -60.7862 | -0.07643 | -60.8446 | 60.8531 | 60.4513 | 60.4742 | -60.8849 | -60.8729 | 0.03241 | -61.0036 | 60.6809 | 60.7443 | 60.6376 | -61.0166 | 0.10752 | 0.002593 | 0.20622 | 0.14783 | 0.040311 | -0.3992 | -0.37631 | -0.024197 | -0.16963 | 0.11953 | -0.011126 | 0.013071 | -0.10623 | -0.21292 | 121.8456 | 121.4438 | 121.4666 | 60.916 | -121.7354 | 121.6733 | 121.7367 | 121.63 | 61.0248 | -121.8672
93 | 122.0718 | -61.0016 | 60.9055 | 1.4211e-13 | -0.005515 | 0.0019059 | 0.064859 | -0.0032178 | 0.060396 | 0.00068675 | -0.0011878 | -0.0015341 | 0.063415 | 0.011107 | 0.062259 | -60.7816 | -0.071851 | -60.8446 | 60.844 | 60.4742 | 60.4834 | -60.8986 | -60.8821 | 0.036989 | -61.0036 | 60.6855 | 60.7443 | 60.6422 | -61.0075 | 0.10294 | -0.061495 | 0.21996 | 0.15699 | 0.054048 | -0.43124 | -0.42209 | -0.005885 | -0.21999 | 0.11953 | -0.001971 | 0.003914 | -0.16117 | -0.26327 | 121.8455 | 121.4758 | 121.485 | 60.9297 | -121.8041 | 121.6871 | 121.7459 | 121.6438 | 61.0386 | -121.9129
94.7188 | 122.1725 | -60.9787 | 60.8597 | 1.4211e-13 | -0.0053012 | 0.0021197 | 0.064432 | -0.0032178 | 0.061037 | 0.00068675 | -0.0014014 | -0.00089313 | 0.063415 | 0.01132 | 0.062686 | -60.7771 | -0.071851 | -60.84 | 60.8485 | 60.4651 | 60.4834 | -60.8895 | -60.8775 | 0.041567 | -61.0036 | 60.69 | 60.7534 | 60.6422 | -61.0029 | 0.089208 | -0.01114 | 0.20165 | 0.13868 | 0.049468 | -0.39462 | -0.37631 | -0.024194 | -0.16963 | 0.10122 | -0.024859 | -0.000665 | -0.10623 | -0.2175 | 121.8272 | 121.4438 | 121.4621 | 60.9068 | -121.7492 | 121.6687 | 121.7321 | 121.6209 | 61.0203 | -121.8626
96.3906 | 122.0444 | -60.9695 | 60.965 | 1.4211e-13 | -0.0053012 | 0.0023333 | 0.064432 | -0.0034314 | 0.060823 | 0.00068675 | -0.0014014 | -0.0015341 | 0.063415 | 0.011107 | 0.062259 | -60.7816 | -0.071851 | -60.8446 | 60.8394 | 60.4696 | 60.4834 | -60.8895 | -60.8866 | 0.046146 | -60.999 | 60.6809 | 60.7351 | 60.6468 | -61.0121 | 0.080052 | -0.12558 | 0.18791 | 0.12494 | 0.04489 | -0.49533 | -0.4816 | -0.042507 | -0.28407 | 0.082907 | -0.029436 | 0.013071 | -0.22983 | -0.3182 | 121.8089 | 121.4392 | 121.4529 | 60.8977 | -121.8545 | 121.6504 | 121.7047 | 121.6163 | 61.0157 | -121.977
98.1094 | 122.0901 | -60.9787 | 60.9238 | 1.4211e-13 | -0.0050876 | 0.0016923 | 0.064859 | -0.0032178 | 0.06061 | -0.014574 | -0.0011878 | -0.0013203 | 0.063415 | 0.010893 | 0.062686 | -60.7771 | -0.07643 | -60.84 | 60.8485 | 60.4605 | 60.4834 | -60.8895 | -60.8821 | 0.041567 | -60.999 | 60.6809 | 60.7489 | 60.6422 | -61.0121 | 0.089208 | -0.075227 | 0.20165 | 0.13868 | 0.049468 | -0.46329 | -0.4404 | -0.033351 | -0.24287 | 0.096642 | -0.02028 | 0.013071 | -0.1749 | -0.28158 | 121.8272 | 121.4392 | 121.4621 | 60.9023 | -121.8133 | 121.6596 | 121.7276 | 121.6209 | 61.0203 | -121.9358
99.8281 | 122.0947 | -60.9558 | 60.9375 | 1.4211e-13 | -0.0050876 | 0.0019059 | 0.064432 | -0.0034314 | 0.06061 | 0.0083173 | -0.0011878 | -0.0013203 | 0.063201 | 0.011107 | 0.062259 | -60.7862 | -0.071851 | -60.8309 | 60.8485 | 60.4651 | 60.4788 | -60.8849 | -60.8821 | 0.041567 | -60.9944 | 60.6855 | 60.7489 | 60.6468 | -61.0121 | 0.070899 | -0.08896 | 0.1696 | 0.12494 | 0.054046 | -0.47244 | -0.45871 | -0.056239 | -0.25203 | 0.073754 | -0.03859 | 0.017649 | -0.18863 | -0.29074 | 121.8044 | 121.4209 | 121.4346 | 60.884 | -121.8224 | 121.6413 | 121.7047 | 121.6026 | 60.9974 | -121.9496
101.5 | 122.0901 | -60.9741 | 60.9695 | 1.4211e-13 | -0.0053012 | 0.0019059 | 0.064432 | -0.0034314 | 0.06061 | 0.00068675 | -0.0014014 | -0.0013203 | 0.062988 | 0.010893 | 0.062045 | -60.7771 | -0.07643 | -60.84 | 60.8394 | 60.4651 | 60.4834 | -60.8849 | -60.8729 | 0.036989 | -60.999 | 60.6717 | 60.7351 | 60.6422 | -61.0029 | 0.089209 | -0.13016 | 0.19707 | 0.1341 | 0.044889 | -0.50449 | -0.48617 | -0.028772 | -0.29781 | 0.10122 | -0.024858 | 0.003914 | -0.23441 | -0.32736 | 121.8135 | 121.4392 | 121.4575 | 60.8977 | -121.8545 | 121.6459 | 121.7093 | 121.6163 | 61.0111 | -121.9724
103.2031 | 122.0901 | -60.9741 | 60.91 | 1.4211e-13 | -0.005515 | 0.0016923 | 0.064432 | -0.0032178 | 0.060182 | 0.00068675 | -0.0014014 | -0.0015341 | 0.063415 | 0.011107 | 0.062259 | -60.7816 | -0.067272 | -60.8354 | 60.8485 | 60.4605 | 60.4834 | -60.8895 | -60.8729 | 0.041567 | -60.9898 | 60.6855 | 60.7397 | 60.6284 | -61.0075 | 0.08463 | -0.061494 | 0.19249 | 0.13868 | 0.054046 | -0.44956 | -0.42666 | -0.033351 | -0.22456 | 0.10122 | -0.015701 | 0.01765 | -0.17032 | -0.28159 | 121.8227 | 121.4346 | 121.4575 | 60.9068 | -121.7995 | 121.6596 | 121.7138 | 121.6026 | 61.0157 | -121.9175
104.9219 | 122.1725 | -60.9879 | 60.8459 | 1.4211e-13 | -0.0053012 | 0.0021197 | 0.064432 | -0.0036452 | 0.060396 | -0.0069437 | -0.0014014 | -0.0013203 | 0.063201 | 0.010893 | 0.062259 | -60.7771 | -0.07643 | -60.8263 | 60.8394 | 60.4651 | 60.4788 | -60.8803 | -60.8821 | 0.050725 | -60.9898 | 60.6855 | 60.7443 | 60.633 | -61.0075 | 0.10752 | -0.006564 | 0.2108 | 0.16157 | 0.054045 | -0.38089 | -0.36716 | -0.019618 | -0.16048 | 0.1058 | -0.001968 | 0.01765 | -0.10166 | -0.21292 | 121.8272 | 121.4529 | 121.4666 | 60.9114 | -121.7263 | 121.6733 | 121.7321 | 121.6209 | 61.0386 | -121.8534
106.6562 | 122.1725 | -60.9192 | 60.9238 | 1.4211e-13 | -0.005515 | 0.0023333 | 0.064432 | -0.0036452 | 0.060823 | -0.0069437 | -0.001615 | -0.00089313 | 0.063201 | 0.011107 | 0.062045 | -60.7771 | -0.081008 | -60.84 | 60.8394 | 60.4605 | 60.4742 | -60.8849 | -60.8729 | 0.036989 | -60.9898 | 60.6809 | 60.7306 | 60.6376 | -61.0029 | 0.034277 | -0.084384 | 0.14214 | 0.079166 | 0.044889 | -0.46329 | -0.44956 | -0.083704 | -0.24287 | 0.046289 | -0.070633 | 0.013071 | -0.19321 | -0.28616 | 121.7586 | 121.3797 | 121.3934 | 60.8382 | -121.8087 | 121.6001 | 121.6497 | 121.5568 | 60.9562 | -121.9267
108.3906 | 122.1359 | -60.9055 | 60.9238 | 1.4211e-13 | -0.005515 | 0.0019059 | 0.064432 | -0.0036452 | 0.06061 | -0.0069437 | -0.001615 | -0.0013203 | 0.063629 | 0.010893 | 0.062259 | -60.7771 | -0.07643 | -60.8309 | 60.8394 | 60.4605 | 60.4834 | -60.8895 | -60.8775 | 0.041567 | -60.9944 | 60.6717 | 60.7443 | 60.6284 | -61.0075 | 0.015966 | -0.084384 | 0.12841 | 0.074591 | 0.058625 | -0.46329 | -0.4404 | -0.10202 | -0.25203 | 0.027978 | -0.088944 | 0.013071 | -0.17948 | -0.29532 | 121.7448 | 121.3659 | 121.3888 | 60.829 | -121.8133 | 121.5772 | 121.6497 | 121.5339 | 60.947 | -121.9312
110.0469 | 122.081 | -60.9421 | 60.9695 | 1.4211e-13 | -0.0050876 | 0.0019059 | 0.064646 | -0.0036452 | 0.06061 | 0.00068675 | -0.001615 | -0.0013203 | 0.063415 | 0.011534 | 0.062045 | -60.7725 | -0.071851 | -60.8309 | 60.8394 | 60.4605 | 60.4742 | -60.8849 | -60.8729 | 0.036989 | -60.9898 | 60.6763 | 60.7443 | 60.6376 | -61.0029 | 0.057166 | -0.13016 | 0.16961 | 0.11121 | 0.054046 | -0.50906 | -0.49533 | -0.060815 | -0.29323 | 0.069178 | -0.047744 | 0.013071 | -0.22525 | -0.33194 | 121.7815 | 121.4026 | 121.4163 | 60.8702 | -121.8545 | 121.6184 | 121.6864 | 121.5797 | 60.9791 | -121.9724
111.7812 | 122.1359 | -60.9512 | 60.8643 | 1.4211e-13 | -0.0057286 | 0.0019059 | 0.064218 | -0.0034314 | 0.06061 | 0.00068675 | -0.00097422 | -0.0011067 | 0.063201 | 0.01132 | 0.062259 | -60.7771 | -0.07643 | -60.8309 | 60.8302 | 60.4513 | 60.4788 | -60.8895 | -60.8775 | 0.036989 | -60.9944 | 60.6763 | 60.7397 | 60.6239 | -61.0029 | 0.061742 | -0.034031 | 0.17418 | 0.12037 | 0.058625 | -0.41294 | -0.38547 | -0.05166 | -0.18794 | 0.073754 | -0.043168 | 0.008492 | -0.12455 | -0.24039 | 121.7815 | 121.4026 | 121.43 | 60.8748 | -121.7537 | 121.6275 | 121.6909 | 121.5751 | 60.9882 | -121.8672
113.4531 | 122.1634 | -60.9192 | 60.9146 | 1.4211e-13 | -0.005515 | 0.0021197 | 0.064432 | -0.0034314 | 0.060396 | 0.00068675 | -0.00097422 | -0.0011067 | 0.063201 | 0.011107 | 0.062472 | -60.7771 | -0.085587 | -60.8354 | 60.8348 | 60.4513 | 60.4788 | -60.8849 | -60.8637 | 0.041567 | -60.9898 | 60.6763 | 60.7351 | 60.6376 | -61.0075 | 0.034277 | -0.079807 | 0.14214 | 0.083744 | 0.049467 | -0.46329 | -0.43582 | -0.088283 | -0.2383 | 0.055447 | -0.070633 | 0.01765 | -0.17948 | -0.27701 | 121.754 | 121.3705 | 121.398 | 60.8336 | -121.7995 | 121.5955 | 121.6543 | 121.5568 | 60.9608 | -121.9221
115.1719 | 122.049 | -60.997 | 60.8734 | 1.4211e-13 | -0.005515 | 0.0019059 | 0.064859 | -0.0034314 | 0.060182 | 0.00068675 | -0.0014014 | -0.0013203 | 0.063201 | 0.01132 | 0.062259 | -60.7771 | -0.07643 | -60.8309 | 60.844 | 60.4513 | 60.4788 | -60.8849 | -60.8729 | 0.050725 | -60.9898 | 60.6672 | 60.7397 | 60.633 | -60.9937 | 0.1121 | -0.029451 | 0.21996 | 0.16614 | 0.054046 | -0.42209 | -0.39462 | 0.003274 | -0.20626 | 0.12411 | 0.007187 | 0.003913 | -0.1337 | -0.24039 | 121.841 | 121.4483 | 121.4758 | 60.9206 | -121.7583 | 121.6642 | 121.7367 | 121.63 | 61.0477 | -121.8671
116.8906 | 122.1085 | -60.9558 | 60.9329 | 1.4211e-13 | -0.0057286 | 0.0021197 | 0.064432 | -0.0036452 | 0.060396 | 0.0083173 | -0.0014014 | -0.0011067 | 0.063415 | 0.011534 | 0.062045 | -60.7633 | -0.085587 | -60.8354 | 60.8394 | 60.4605 | 60.4788 | -60.8849 | -60.8683 | 0.036989 | -60.9944 | 60.6763 | 60.7397 | 60.633 | -60.9983 | 0.070899 | -0.093539 | 0.19249 | 0.12037 | 0.049467 | -0.47244 | -0.45413 | -0.042503 | -0.25661 | 0.08749 | -0.03859 | 0.003913 | -0.19321 | -0.29989 | 121.7952 | 121.4163 | 121.4346 | 60.8702 | -121.8178 | 121.6321 | 121.6955 | 121.5888 | 60.9928 | -121.9312
118.6094 | 122.0993 | -60.9467 | 60.8871 | 1.4211e-13 | -0.005515 | 0.0016923 | 0.064432 | -0.0036452 | 0.060396 | 0.00068675 | -0.0011878 | -0.0013203 | 0.063629 | 0.01132 | 0.062259 | -60.7725 | -0.090166 | -60.8263 | 60.8256 | 60.4513 | 60.4788 | -60.8803 | -60.8729 | 0.041567 | -60.9944 | 60.6717 | 60.7351 | 60.6193 | -60.9937 | 0.066322 | -0.061498 | 0.17418 | 0.12037 | 0.054045 | -0.43583 | -0.40836 | -0.04708 | -0.21541 | 0.073755 | -0.047746 | -0.000666 | -0.15201 | -0.26786 | 121.7723 | 121.398 | 121.4254 | 60.8565 | -121.7675 | 121.6184 | 121.6818 | 121.5659 | 60.9882 | -121.8809
120.2656 | 122.0261 | -60.9192 | 60.9512 | 1.4211e-13 | -0.005515 | 0.0023333 | 0.064432 | -0.0038588 | 0.060182 | 0.00068675 | -0.00097422 | -0.0011067 | 0.063415 | 0.011534 | 0.062045 | -60.7633 | -0.081008 | -60.8309 | 60.8394 | 60.4651 | 60.4834 | -60.8803 | -60.8729 | 0.03241 | -60.9807 | 60.6855 | 60.7306 | 60.633 | -60.9983 | 0.038856 | -0.11185 | 0.15587 | 0.088323 | 0.049467 | -0.48618 | -0.46786 | -0.079125 | -0.26576 | 0.046289 | -0.061475 | 0.01765 | -0.22068 | -0.31821 | 121.7586 | 121.3842 | 121.4026 | 60.8382 | -121.8316 | 121.6047 | 121.6497 | 121.5522 | 60.9516 | -121.9495
121.9219 | 122.1085 | -60.9558 | 60.8688 | 1.4211e-13 | -0.0057286 | 0.0019059 | 0.064432 | -0.0038588 | 0.060182 | 0.00068675 | -0.0011878 | -0.0015341 | 0.063629 | 0.011534 | 0.062472 | -60.7679 | -0.07643 | -60.8309 | 60.8348 | 60.4513 | 60.4788 | -60.8849 | -60.8729 | 0.03241 | -60.9807 | 60.6763 | 60.7397 | 60.6284 | -61.0029 | 0.070899 | -0.03403 | 0.18792 | 0.12494 | 0.054046 | -0.41751 | -0.39005 | -0.047082 | -0.19252 | 0.082911 | -0.024853 | 0.022229 | -0.12912 | -0.24039 | 121.7906 | 121.4071 | 121.4346 | 60.8794 | -121.7537 | 121.6321 | 121.6955 | 121.5843 | 60.9882 | -121.8717
123.6406 | 122.1313 | -60.9375 | 60.9238 | 1.4211e-13 | -0.005515 | 0.0019059 | 0.064432 | -0.0036452 | 0.060396 | 0.00068675 | -0.001615 | -0.0013203 | 0.062988 | 0.01132 | 0.061831 | -60.7679 | -0.085587 | -60.8217 | 60.8211 | 60.4513 | 60.4742 | -60.8849 | -60.8683 | 0.036989 | -60.9944 | 60.6672 | 60.7351 | 60.6284 | -60.9983 | 0.052588 | -0.1027 | 0.1696 | 0.11579 | 0.063202 | -0.47245 | -0.44956 | -0.060814 | -0.25661 | 0.069179 | -0.056901 | 0.003913 | -0.18863 | -0.29532 | 121.7586 | 121.3888 | 121.4117 | 60.8519 | -121.8087 | 121.6047 | 121.6726 | 121.5659 | 60.9745 | -121.9221
125.2969 | 122.1634 | -60.9924 | 60.8231 | 1.4211e-13 | -0.0057286 | 0.0019059 | 0.064646 | -0.0036452 | 0.06061 | 0.015947 | -0.0011878 | -0.0015341 | 0.062774 | 0.011107 | 0.062045 | -60.7633 | -0.07643 | -60.8263 | 60.8348 | 60.4513 | 60.4788 | -60.8758 | -60.8637 | 0.041567 | -60.9852 | 60.6717 | 60.7397 | 60.6284 | -60.9892 | 0.11668 | 0.011746 | 0.22912 | 0.16614 | 0.049466 | -0.37174 | -0.34427 | 0.003276 | -0.15132 | 0.12869 | 0.007189 | 0.003913 | -0.083347 | -0.19461 | 121.8272 | 121.4438 | 121.4712 | 60.916 | -121.6988 | 121.6642 | 121.7321 | 121.6209 | 61.034 | -121.8122
127.0312 | 122.1634 | -60.8826 | 60.9329 | 1.4211e-13 | -0.0057286 | 0.0019059 | 0.064218 | -0.0036452 | 0.060396 | -0.0069437 | -0.0014014 | -0.0015341 | 0.063415 | 0.011748 | 0.062259 | -60.7542 | -0.085587 | -60.84 | 60.8302 | 60.4559 | 60.4742 | -60.8849 | -60.8637 | 0.036989 | -60.9807 | 60.6717 | 60.7306 | 60.6284 | -60.9937 | -0.002344 | -0.10269 | 0.12841 | 0.042545 | 0.044889 | -0.47702 | -0.45871 | -0.11117 | -0.26119 | 0.018826 | -0.098096 | 0.013071 | -0.20237 | -0.30447 | 121.7128 | 121.3385 | 121.3568 | 60.797 | -121.8178 | 121.5543 | 121.6131 | 121.511 | 60.9196 | -121.9267
128.7656 | 122.1497 | -60.9558 | 60.8322 | 1.4211e-13 | -0.005515 | 0.0016923 | 0.064432 | -0.0038588 | 0.06061 | -0.0069437 | -0.0011878 | -0.0013203 | 0.063415 | 0.011748 | 0.062259 | -60.7587 | -0.081008 | -60.8354 | 60.8302 | 60.4559 | 60.4788 | -60.8758 | -60.8683 | 0.036989 | -60.9898 | 60.6717 | 60.7351 | 60.6193 | -60.9892 | 0.080057 | -0.001987 | 0.19707 | 0.12037 | 0.040309 | -0.37631 | -0.35342 | -0.033345 | -0.16048 | 0.08749 | -0.034011 | -0.000666 | -0.097081 | -0.21292 | 121.786 | 121.4117 | 121.4346 | 60.8748 | -121.708 | 121.6275 | 121.6909 | 121.5751 | 60.9928 | -121.8214
130.4375 | 122.1451 | -60.9238 | 60.8826 | 1.4211e-13 | -0.005515 | 0.0021197 | 0.064005 | -0.0034314 | 0.060182 | -0.0069437 | -0.0014014 | -0.0013203 | 0.063415 | 0.01132 | 0.061831 | -60.7679 | -0.081008 | -60.84 | 60.8302 | 60.4513 | 60.4742 | -60.8758 | -60.8637 | 0.041567 | -60.9807 | 60.6672 | 60.7351 | 60.6284 | -60.9983 | 0.048013 | -0.052341 | 0.15587 | 0.083744 | 0.035731 | -0.43125 | -0.40836 | -0.074547 | -0.21541 | 0.060025 | -0.056897 | 0.01765 | -0.14744 | -0.25412 | 121.754 | 121.3751 | 121.398 | 60.8428 | -121.7583 | 121.5909 | 121.6589 | 121.5522 | 60.9653 | -121.8809
132.1719 | 122.1268 | -60.9192 | 60.8917 | 1.4211e-13 | -0.005515 | 0.0021197 | 0.064218 | -0.0036452 | 0.06061 | 0.0083173 | -0.0011878 | -0.0013203 | 0.063415 | 0.011748 | 0.062045 | -60.7633 | -0.085587 | -60.8354 | 60.8302 | 60.4559 | 60.4742 | -60.8803 | -60.8637 | 0.03241 | -60.9807 | 60.6672 | 60.7306 | 60.6193 | -60.9983 | 0.038856 | -0.061497 | 0.15587 | 0.083744 | 0.044888 | -0.43582 | -0.41751 | -0.079125 | -0.22457 | 0.055447 | -0.061475 | 0.01765 | -0.16117 | -0.27243 | 121.7494 | 121.3751 | 121.3934 | 60.8336 | -121.7721 | 121.5863 | 121.6497 | 121.5385 | 60.9516 | -121.89
133.8906 | 122.0856 | -60.9375 | 60.8871 | 1.4211e-13 | -0.0057286 | 0.0021197 | 0.064218 | -0.0036452 | 0.060396 | 0.0083173 | -0.001615 | -0.0011067 | 0.063415 | 0.011748 | 0.062045 | -60.7542 | -0.081008 | -60.8309 | 60.8302 | 60.4559 | 60.4696 | -60.8712 | -60.8592 | 0.036989 | -60.9852 | 60.6672 | 60.7306 | 60.6239 | -60.9937 | 0.066325 | -0.056919 | 0.18334 | 0.10663 | 0.040309 | -0.43125 | -0.41751 | -0.056235 | -0.21999 | 0.078336 | -0.047743 | 0.008492 | -0.15659 | -0.26328 | 121.7677 | 121.3934 | 121.4071 | 60.8565 | -121.7583 | 121.6047 | 121.6681 | 121.5614 | 60.9745 | -121.8809
135.5625 | 122.0261 | -61.0062 | 60.8917 | 1.4211e-13 | -0.0057286 | 0.0016923 | 0.064432 | -0.0034314 | 0.060396 | 0.0083173 | -0.0018288 | -0.0015341 | 0.063201 | 0.011107 | 0.062045 | -60.7587 | -0.085587 | -60.8309 | 60.8348 | 60.4559 | 60.4742 | -60.8803 | -60.8637 | 0.041567 | -60.9852 | 60.6717 | 60.7306 | 60.633 | -60.9846 | 0.12583 | -0.056919 | 0.24743 | 0.1753 | 0.049467 | -0.43582 | -0.41751 | 0.021587 | -0.21999 | 0.14242 | 0.020922 | -0.000665 | -0.16117 | -0.2587 | 121.841 | 121.4621 | 121.4804 | 60.9206 | -121.7721 | 121.6779 | 121.7367 | 121.6392 | 61.0477 | -121.8763
137.2969 | 121.9986 | -60.9833 | 60.8597 | 1.4211e-13 | -0.0057286 | 0.0016923 | 0.064218 | -0.0038588 | 0.06061 | 0.00068675 | -0.0011878 | -0.0013203 | 0.063629 | 0.011748 | 0.061831 | -60.7587 | -0.081008 | -60.8354 | 60.8302 | 60.4559 | 60.4788 | -60.8849 | -60.8683 | 0.036989 | -60.9807 | 60.6672 | 60.726 | 60.6284 | -60.9846 | 0.098364 | -0.029453 | 0.22454 | 0.14783 | 0.049467 | -0.40378 | -0.38089 | -0.001302 | -0.19252 | 0.11495 | 0.002612 | 0.003914 | -0.1337 | -0.23123 | 121.8135 | 121.4392 | 121.4621 | 60.9023 | -121.7446 | 121.6504 | 121.7093 | 121.6117 | 61.0203 | -121.8443
139.0156 | 122.0306 | -60.9283 | 60.9512 | 1.4211e-13 | -0.0059422 | 0.0019059 | 0.063791 | -0.0036452 | 0.06061 | 0.00068675 | -0.0011878 | -0.0013203 | 0.063415 | 0.011748 | 0.061831 | -60.7542 | -0.07643 | -60.8354 | 60.8302 | 60.4559 | 60.4696 | -60.8803 | -60.8637 | 0.03241 | -60.9807 | 60.6717 | 60.7306 | 60.633 | -60.9892 | 0.048012 | -0.12101 | 0.17419 | 0.0929 | 0.044888 | -0.49533 | -0.4816 | -0.060811 | -0.2795 | 0.064603 | -0.052319 | 0.008492 | -0.22068 | -0.31821 | 121.7586 | 121.3842 | 121.398 | 60.8519 | -121.8316 | 121.6001 | 121.6589 | 121.5614 | 60.9608 | -121.9404
140.75 | 122.0123 | -60.9879 | 60.8871 | 1.4211e-13 | -0.0059422 | 0.0023333 | 0.064218 | -0.0038588 | 0.06061 | 0.00068675 | -0.0011878 | -0.0015341 | 0.063201 | 0.011748 | 0.061831 | -60.7542 | -0.07643 | -60.8309 | 60.8256 | 60.4467 | 60.4696 | -60.8712 | -60.8637 | 0.036989 | -60.9761 | 60.6534 | 60.7351 | 60.633 | -60.9937 | 0.11668 | -0.061498 | 0.23369 | 0.15699 | 0.040309 | -0.4404 | -0.41751 | -0.005881 | -0.23372 | 0.12411 | 0.011768 | 0.017649 | -0.15201 | -0.25412 | 121.8135 | 121.4346 | 121.4575 | 60.9114 | -121.7583 | 121.6413 | 121.723 | 121.6209 | 61.0248 | -121.8809
142.4219 | 122.0718 | -60.9192 | 60.9238 | 1.4211e-13 | -0.0059422 | 0.0019059 | 0.064005 | -0.0036452 | 0.060396 | 0.00068675 | -0.0018288 | -0.0013203 | 0.063415 | 0.01132 | 0.062045 | -60.7587 | -0.07643 | -60.8354 | 60.8348 | 60.4513 | 60.4742 | -60.8849 | -60.8546 | 0.036989 | -60.9852 | 60.658 | 60.726 | 60.6284 | -60.9846 | 0.034277 | -0.088962 | 0.16045 | 0.083744 | 0.049467 | -0.47245 | -0.44956 | -0.065389 | -0.26577 | 0.064604 | -0.066054 | -0.000665 | -0.19779 | -0.29532 | 121.754 | 121.3705 | 121.3934 | 60.8428 | -121.8087 | 121.5772 | 121.6452 | 121.5476 | 60.9562 | -121.9083
144.1406 | 122.1451 | -60.9283 | 60.8826 | 1.4211e-13 | -0.0059422 | 0.0021197 | 0.064218 | -0.0034314 | 0.060182 | 0.00068675 | -0.00097422 | -0.0011067 | 0.063201 | 0.011748 | 0.061404 | -60.7542 | -0.071851 | -60.8354 | 60.8256 | 60.4513 | 60.4742 | -60.8712 | -60.8592 | 0.036989 | -60.9761 | 60.658 | 60.7306 | 60.6284 | -60.9892 | 0.05717 | -0.05692 | 0.17419 | 0.0929 | 0.03573 | -0.43125 | -0.40836 | -0.060811 | -0.22457 | 0.069181 | -0.047741 | 0.01307 | -0.15201 | -0.25412 | 121.754 | 121.3797 | 121.4026 | 60.8565 | -121.7537 | 121.5863 | 121.6589 | 121.5568 | 60.9653 | -121.8717
145.875 | 122.0627 | -61.0153 | 60.8414 | 1.4211e-13 | -0.006156 | 0.0021197 | 0.064432 | -0.0038588 | 0.06061 | -0.0069437 | -0.0014014 | -0.0013203 | 0.063201 | 0.011961 | 0.061831 | -60.7542 | -0.071851 | -60.8309 | 60.8211 | 60.4559 | 60.4696 | -60.8803 | -60.8592 | 0.03241 | -60.9669 | 60.658 | 60.726 | 60.6147 | -60.9892 | 0.13499 | -0.0203 | 0.26116 | 0.18445 | 0.049467 | -0.38547 | -0.37174 | 0.026164 | -0.18337 | 0.15616 | 0.048392 | 0.022228 | -0.11539 | -0.22666 | 121.8364 | 121.4712 | 121.485 | 60.9435 | -121.7217 | 121.6733 | 121.7413 | 121.63 | 61.0477 | -121.8305
147.5469 | 122.0627 | -60.9375 | 60.9055 | 1.4211e-13 | -0.0059422 | 0.0021197 | 0.064005 | -0.0036452 | 0.060396 | 0.0083173 | -0.0014014 | -0.0013203 | 0.063201 | 0.011534 | 0.061831 | -60.7496 | -0.081008 | -60.8354 | 60.8256 | 60.4422 | 60.4696 | -60.8758 | -60.8546 | 0.036989 | -60.9807 | 60.658 | 60.7306 | 60.6284 | -60.9892 | 0.061746 | -0.079809 | 0.18792 | 0.10206 | 0.040309 | -0.46329 | -0.43582 | -0.051656 | -0.24746 | 0.082915 | -0.043164 | 0.008492 | -0.1749 | -0.27701 | 121.7631 | 121.3797 | 121.4071 | 60.8565 | -121.7812 | 121.5955 | 121.6681 | 121.5659 | 60.9745 | -121.8946
149.2656 | 122.1222 | -60.9512 | 60.8551 | 1.4211e-13 | -0.0059422 | 0.0019059 | 0.063791 | -0.0036452 | 0.060182 | -0.0069437 | -0.0011878 | -0.0015341 | 0.063415 | 0.011748 | 0.061831 | -60.7542 | -0.081008 | -60.8354 | 60.8211 | 60.4467 | 60.4696 | -60.8712 | -60.8592 | 0.036989 | -60.9807 | 60.6717 | 60.7306 | 60.6193 | -60.9937 | 0.080058 | -0.034033 | 0.19707 | 0.11579 | 0.03573 | -0.40836 | -0.38547 | -0.042502 | -0.18337 | 0.092069 | -0.029431 | 0.013071 | -0.12455 | -0.23581 | 121.7723 | 121.398 | 121.4209 | 60.8702 | -121.7263 | 121.623 | 121.6818 | 121.5705 | 60.9882 | -121.8488
151 | 122.0581 | -60.9558 | 60.9238 | 1.4211e-13 | -0.0059422 | 0.0019059 | 0.063791 | -0.0034314 | 0.060396 | -0.0069437 | -0.0014014 | -0.0015341 | 0.063415 | 0.011534 | 0.061618 | -60.7496 | -0.07643 | -60.8263 | 60.8256 | 60.4559 | 60.4651 | -60.8803 | -60.8592 | 0.036989 | -60.9807 | 60.6626 | 60.7214 | 60.6284 | -60.98 | 0.075478 | -0.098119 | 0.20623 | 0.12952 | 0.054045 | -0.46787 | -0.45871 | -0.024188 | -0.26119 | 0.096647 | -0.024853 | -0.000665 | -0.20237 | -0.29532 | 121.7815 | 121.4117 | 121.4209 | 60.8794 | -121.8041 | 121.6184 | 121.6772 | 121.5843 | 60.9928 | -121.9038
152.7344 | 122.1405 | -60.8917 | 60.9055 | 1.4211e-13 | -0.0059422 | 0.0019059 | 0.064005 | -0.0038588 | 0.060396 | -0.0069437 | -0.0014014 | -0.0011067 | 0.062988 | 0.01132 | 0.061618 | -60.7542 | -0.07643 | -60.8309 | 60.8256 | 60.4559 | 60.4696 | -60.8712 | -60.8546 | 0.036989 | -60.9761 | 60.6626 | 60.726 | 60.6239 | -60.9846 | 0.020549 | -0.079809 | 0.13757 | 0.060858 | 0.040309 | -0.44956 | -0.43582 | -0.092854 | -0.24288 | 0.037139 | -0.084362 | 0.008492 | -0.17948 | -0.28159 | 121.7174 | 121.3476 | 121.3614 | 60.8153 | -121.7766 | 121.5543 | 121.6177 | 121.5156 | 60.9287 | -121.89
154.3906 | 122.0901 | -60.9055 | 60.9283 | 1.4211e-13 | -0.006156 | 0.0023333 | 0.064005 | -0.0036452 | 0.060182 | 0.00068675 | -0.0014014 | -0.0013203 | 0.063415 | 0.011534 | 0.061831 | -60.745 | -0.07643 | -60.8354 | 60.8256 | 60.4467 | 60.4696 | -60.8712 | -60.8546 | 0.036989 | -60.9669 | 60.658 | 60.7306 | 60.6239 | -60.9846 | 0.034282 | -0.1027 | 0.16045 | 0.070012 | 0.03573 | -0.4816 | -0.45871 | -0.079121 | -0.27035 | 0.050872 | -0.061471 | 0.01765 | -0.19779 | -0.30448 | 121.7311 | 121.3522 | 121.3751 | 60.829 | -121.7995 | 121.5635 | 121.636 | 121.5293 | 60.9424 | -121.9129
156.125 | 122.0627 | -60.9421 | 60.8963 | 1.4211e-13 | -0.0065834 | 0.0019059 | 0.063791 | -0.0038588 | 0.060182 | 0.00068675 | -0.001615 | -0.0013203 | 0.063201 | 0.011961 | 0.061831 | -60.7496 | -0.071851 | -60.8217 | 60.8165 | 60.4467 | 60.4696 | -60.8666 | -60.8592 | 0.03241 | -60.9669 | 60.658 | 60.7306 | 60.6101 | -60.9846 | 0.075482 | -0.07981 | 0.1925 | 0.12037 | 0.044886 | -0.44956 | -0.42667 | -0.0425 | -0.2383 | 0.082914 | -0.02485 | 0.01765 | -0.16575 | -0.28617 | 121.7586 | 121.3888 | 121.4117 | 60.8702 | -121.7629 | 121.6001 | 121.6726 | 121.5522 | 60.9745 | -121.8809
157.8594 | 122.0215 | -60.965 | 60.8505 | 1.4211e-13 | -0.006156 | 0.0021197 | 0.064005 | -0.0040724 | 0.060396 | 0.00068675 | -0.001615 | -0.0013203 | 0.063415 | 0.011748 | 0.061618 | -60.7496 | -0.067272 | -60.8309 | 60.8119 | 60.4422 | 60.4742 | -60.8803 | -60.85 | 0.027831 | -60.9761 | 60.6626 | 60.7351 | 60.6147 | -60.9846 | 0.084633 | -0.038612 | 0.21538 | 0.1341 | 0.049467 | -0.40836 | -0.37631 | -0.019612 | -0.18795 | 0.11496 | -0.01112 | 0.008492 | -0.11539 | -0.23581 | 121.7769 | 121.4071 | 121.4392 | 60.8977 | -121.7309 | 121.6275 | 121.7001 | 121.5797 | 60.9928 | -121.8351
159.5156 | 122.113 | -60.965 | 60.8276 | 1.4211e-13 | -0.006156 | 0.0016923 | 0.063791 | -0.0036452 | 0.060396 | -0.0069437 | -0.0014014 | -0.0017477 | 0.063415 | 0.011961 | 0.061618 | -60.745 | -0.071851 | -60.8263 | 60.8211 | 60.4422 | 60.4696 | -60.8758 | -60.8454 | 0.03241 | -60.9669 | 60.6626 | 60.726 | 60.6101 | -60.9937 | 0.089212 | -0.006567 | 0.21996 | 0.13868 | 0.049466 | -0.38547 | -0.358 | -0.028769 | -0.16506 | 0.11954 | -0.001962 | 0.026807 | -0.10166 | -0.2175 | 121.786 | 121.4071 | 121.4346 | 60.8931 | -121.7034 | 121.6275 | 121.6909 | 121.5751 | 60.9974 | -121.8214
161.2344 | 122.0306 | -60.9375 | 60.9009 | 1.4211e-13 | -0.0063696 | 0.0016923 | 0.064218 | -0.0036452 | 0.060182 | 0.00068675 | -0.0011878 | -0.00089313 | 0.063629 | 0.012175 | 0.061618 | -60.7496 | -0.071851 | -60.8217 | 60.8211 | 60.4422 | 60.4696 | -60.8712 | -60.8546 | 0.03241 | -60.9715 | 60.6626 | 60.726 | 60.6193 | -60.9846 | 0.066325 | -0.079809 | 0.18792 | 0.11579 | 0.049465 | -0.45872 | -0.43125 | -0.047078 | -0.2383 | 0.082915 | -0.034007 | 0.013071 | -0.1749 | -0.28159 | 121.7586 | 121.3797 | 121.4071 | 60.8656 | -121.7721 | 121.6001 | 121.6635 | 121.5568 | 60.9699 | -121.8855
162.9531 | 122.0215 | -60.9375 | 60.9512 | 1.4211e-13 | -0.0065834 | 0.0014787 | 0.063791 | -0.0036452 | 0.060182 | 0.00068675 | -0.001615 | -0.0015341 | 0.063201 | 0.011748 | 0.061404 | -60.7358 | -0.071851 | -60.8263 | 60.8165 | 60.4376 | 60.4696 | -60.8758 | -60.85 | 0.03241 | -60.9624 | 60.6626 | 60.7214 | 60.6193 | -60.9846 | 0.061746 | -0.13474 | 0.20165 | 0.11121 | 0.049466 | -0.51365 | -0.4816 | -0.047078 | -0.28865 | 0.087494 | -0.02485 | 0.022228 | -0.22984 | -0.33194 | 121.754 | 121.3751 | 121.4071 | 60.8656 | -121.827 | 121.6001 | 121.6589 | 121.5568 | 60.9699 | -121.9358
164.6719 | 122.049 | -60.9146 | 60.9238 | 1.4211e-13 | -0.0063696 | 0.0019059 | 0.064218 | -0.0036452 | 0.059969 | 0.015947 | -0.0014014 | -0.0013203 | 0.063201 | 0.011961 | 0.06119 | -60.745 | -0.067272 | -60.8217 | 60.8165 | 60.4559 | 60.4651 | -60.8758 | -60.85 | 0.036989 | -60.9624 | 60.6626 | 60.7168 | 60.6193 | -60.9846 | 0.038858 | -0.10728 | 0.16961 | 0.092902 | 0.054044 | -0.46787 | -0.45871 | -0.069966 | -0.26119 | 0.064606 | -0.047738 | 0.022228 | -0.20695 | -0.30448 | 121.7311 | 121.3705 | 121.3797 | 60.8473 | -121.7995 | 121.5772 | 121.6314 | 121.5339 | 60.9516 | -121.9083
166.4219 | 122.0444 | -60.9329 | 60.9238 | 1.4211e-13 | -0.0063696 | 0.0021197 | 0.063577 | -0.0040724 | 0.060182 | 0.00068675 | -0.0014014 | -0.0015341 | 0.062988 | 0.011961 | 0.061404 | -60.745 | -0.07643 | -60.8217 | 60.8165 | 60.4513 | 60.4742 | -60.8666 | -60.85 | 0.036989 | -60.9669 | 60.658 | 60.7306 | 60.6101 | -60.9846 | 0.066326 | -0.10728 | 0.18792 | 0.11121 | 0.044886 | -0.47245 | -0.44956 | -0.051656 | -0.26577 | 0.082916 | -0.034006 | 0.01765 | -0.19321 | -0.31363 | 121.7494 | 121.3842 | 121.4071 | 60.8565 | -121.7904 | 121.5909 | 121.6635 | 121.5431 | 60.9699 | -121.9083
168.1406 | 122.0947 | -60.9604 | 60.8459 | 1.4211e-13 | -0.0063696 | 0.0021197 | 0.063791 | -0.0038588 | 0.059755 | 0.0083173 | -0.00097422 | -0.0015341 | 0.063201 | 0.011961 | 0.061618 | -60.745 | -0.067272 | -60.8217 | 60.8165 | 60.4467 | 60.4696 | -60.8712 | -60.85 | 0.041567 | -60.9624 | 60.6626 | 60.726 | 60.6147 | -60.9846 | 0.089213 | -0.029456 | 0.21539 | 0.13868 | 0.049465 | -0.39921 | -0.37631 | -0.02419 | -0.18337 | 0.11038 | -0.001962 | 0.022228 | -0.11997 | -0.23124 | 121.7769 | 121.4071 | 121.43 | 60.8931 | -121.7171 | 121.623 | 121.6864 | 121.5751 | 61.002 | -121.8305
169.7969 | 122.113 | -60.965 | 60.8139 | 1.4211e-13 | -0.0065834 | 0.0014787 | 0.063791 | -0.0038588 | 0.059755 | 0.00068675 | -0.0018288 | -0.0017477 | 0.062988 | 0.012389 | 0.061404 | -60.7358 | -0.071851 | -60.8217 | 60.8119 | 60.4376 | 60.4651 | -60.8666 | -60.8454 | 0.036989 | -60.9669 | 60.658 | 60.7214 | 60.6101 | -60.98 | 0.09837 | -0.001991 | 0.22912 | 0.14326 | 0.044886 | -0.37632 | -0.34885 | -0.015033 | -0.15591 | 0.11954 | -0.001962 | 0.013071 | -0.092507 | -0.20377 | 121.7769 | 121.4025 | 121.43 | 60.8931 | -121.6805 | 121.623 | 121.6864 | 121.5751 | 61.002 | -121.7939
171.4531 | 122.1222 | -60.9055 | 60.8963 | 1.4211e-13 | -0.0065834 | 0.0019059 | 0.063791 | -0.0040724 | 0.059969 | 0.00068675 | -0.00097422 | -0.0017477 | 0.063415 | 0.011961 | 0.061618 | -60.7404 | -0.071851 | -60.8309 | 60.8165 | 60.4422 | 60.4651 | -60.8574 | -60.8454 | 0.027831 | -60.9669 | 60.6534 | 60.7168 | 60.6101 | -60.9846 | 0.048019 | -0.07981 | 0.16503 | 0.074591 | 0.026572 | -0.45414 | -0.43125 | -0.079121 | -0.24288 | 0.060029 | -0.061471 | 0.01765 | -0.17948 | -0.28617 | 121.7219 | 121.3476 | 121.3705 | 60.8336 | -121.7537 | 121.5589 | 121.6223 | 121.5156 | 60.9333 | -121.8809
173.125 | 122.1039 | -60.8734 | 60.8871 | 1.4211e-13 | -0.0063696 | 0.0019059 | 0.063791 | -0.0038588 | 0.059969 | 0.00068675 | -0.0014014 | -0.0015341 | 0.063415 | 0.011961 | 0.061404 | -60.7404 | -0.067272 | -60.8171 | 60.8165 | 60.4376 | 60.4651 | -60.8666 | -60.8454 | 0.027831 | -60.9624 | 60.658 | 60.726 | 60.6101 | -60.9846 | 0.006817 | -0.070655 | 0.13299 | 0.056281 | 0.049464 | -0.44956 | -0.42209 | -0.11116 | -0.22915 | 0.027985 | -0.088937 | 0.022228 | -0.16117 | -0.27701 | 121.6899 | 121.311 | 121.3385 | 60.8061 | -121.7537 | 121.5314 | 121.5994 | 121.4835 | 60.9012 | -121.8717
174.7969 | 122.1039 | -60.8597 | 60.8871 | 1.4211e-13 | -0.0065834 | 0.0019059 | 0.063791 | -0.0038588 | 0.059755 | -0.0069437 | -0.0014014 | -0.0015341 | 0.063201 | 0.011961 | 0.06119 | -60.7404 | -0.071851 | -60.8217 | 60.8119 | 60.4376 | 60.4605 | -60.8666 | -60.85 | 0.036989 | -60.9669 | 60.658 | 60.7168 | 60.6147 | -60.9892 | -0.006916 | -0.075233 | 0.11926 | 0.03797 | 0.044886 | -0.44956 | -0.42667 | -0.12948 | -0.22915 | 0.009674 | -0.10725 | 0.022228 | -0.17033 | -0.27243 | 121.6716 | 121.2973 | 121.3202 | 60.7878 | -121.7537 | 121.5177 | 121.5765 | 121.4744 | 60.8967 | -121.8763
176.4844 | 121.9849 | -60.9055 | 60.965 | 1.4211e-13 | -0.0065834 | 0.0019059 | 0.063363 | -0.0038588 | 0.059541 | -0.0069437 | -0.001615 | -0.0017477 | 0.063201 | 0.012175 | 0.061404 | -60.7358 | -0.085587 | -60.8217 | 60.8119 | 60.4513 | 60.4696 | -60.8666 | -60.8454 | 0.03241 | -60.9761 | 60.658 | 60.7214 | 60.6101 | -60.9846 | 0.038861 | -0.15305 | 0.16961 | 0.083747 | 0.044886 | -0.51364 | -0.49533 | -0.079121 | -0.30697 | 0.060029 | -0.070629 | 0.008492 | -0.24357 | -0.35483 | 121.7174 | 121.3568 | 121.3751 | 60.8199 | -121.8316 | 121.5635 | 121.6269 | 121.5156 | 60.9379 | -121.9495
178.25 | 122.0673 | -60.8734 | 60.9238 | 1.4211e-13 | -0.0063696 | 0.0014787 | 0.063791 | -0.0034314 | 0.059755 | 0.00068675 | -0.001615 | -0.0015341 | 0.063201 | 0.012175 | 0.061404 | -60.7358 | -0.071851 | -60.8171 | 60.8119 | 60.4467 | 60.4696 | -60.8712 | -60.8408 | 0.027831 | -60.9669 | 60.6534 | 60.7168 | 60.6101 | -60.9846 | 0.002238 | -0.11185 | 0.13757 | 0.056281 | 0.054043 | -0.47702 | -0.45413 | -0.11116 | -0.27035 | 0.032564 | -0.093515 | 0.01765 | -0.20695 | -0.31363 | 121.6853 | 121.3202 | 121.343 | 60.8016 | -121.7949 | 121.5268 | 121.5902 | 121.4835 | 60.9012 | -121.9083
179.9219 | 121.9711 | -60.9421 | 60.878 | 1.4211e-13 | -0.006797 | 0.0019059 | 0.063791 | -0.0036452 | 0.059969 | -0.0069437 | -0.00097422 | -0.0015341 | 0.062988 | 0.012389 | 0.061404 | -60.7358 | -0.081008 | -60.8263 | 60.8165 | 60.4467 | 60.4651 | -60.862 | -60.8408 | 0.036989 | -60.9578 | 60.658 | 60.7168 | 60.6056 | -60.9846 | 0.080061 | -0.0615 | 0.20623 | 0.11579 | 0.035729 | -0.43125 | -0.41294 | -0.0425 | -0.21999 | 0.10123 | -0.015693 | 0.026807 | -0.16117 | -0.27244 | 121.7586 | 121.3888 | 121.4071 | 60.8611 | -121.74 | 121.6001 | 121.6589 | 121.5476 | 60.9791 | -121.8626
181.6094 | 122.0993 | -60.9329 | 60.8231 | 1.4211e-13 | -0.0065834 | 0.0021197 | 0.064005 | -0.0036452 | 0.059755 | 0.00068675 | -0.001615 | -0.0011067 | 0.062988 | 0.011961 | 0.061618 | -60.745 | -0.07643 | -60.8126 | 60.8165 | 60.433 | 60.4651 | -60.8574 | -60.8454 | 0.036989 | -60.9624 | 60.6534 | 60.7168 | 60.601 | -60.9754 | 0.075484 | -0.006568 | 0.18792 | 0.12037 | 0.044885 | -0.39005 | -0.358 | -0.042498 | -0.16964 | 0.087494 | -0.029428 | 0.01307 | -0.10624 | -0.22208 | 121.7494 | 121.3659 | 121.398 | 60.8565 | -121.6805 | 121.5863 | 121.6497 | 121.5339 | 60.9699 | -121.7985
183.2812 | 122.113 | -60.9009 | 60.91 | 1.4211e-13 | -0.0070106 | 0.0016923 | 0.064005 | -0.0036452 | 0.059969 | 0.00068675 | -0.0011878 | -0.0013203 | 0.063415 | 0.011961 | 0.061404 | -60.7404 | -0.071851 | -60.8171 | 60.8119 | 60.4376 | 60.4651 | -60.8529 | -60.85 | 0.027831 | -60.9624 | 60.6534 | 60.7168 | 60.6101 | -60.98 | 0.04802 | -0.098121 | 0.16046 | 0.083747 | 0.035727 | -0.47245 | -0.44498 | -0.07912 | -0.25661 | 0.050873 | -0.061471 | 0.017649 | -0.19322 | -0.2999 | 121.7128 | 121.3385 | 121.3659 | 60.829 | -121.7629 | 121.5543 | 121.6177 | 121.511 | 60.9287 | -121.89
184.9688 | 122.0764 | -60.9375 | 60.8551 | 1.4211e-13 | -0.0065834 | 0.0016923 | 0.063363 | -0.0038588 | 0.059755 | 0.015947 | -0.001615 | -0.0015341 | 0.062774 | 0.012175 | 0.061618 | -60.7313 | -0.062694 | -60.8217 | 60.8028 | 60.433 | 60.4605 | -60.862 | -60.8408 | 0.027831 | -60.9532 | 60.6534 | 60.7168 | 60.601 | -60.98 | 0.075483 | -0.052347 | 0.20623 | 0.11579 | 0.040307 | -0.4221 | -0.39463 | -0.042499 | -0.20168 | 0.096651 | -0.015692 | 0.026807 | -0.13828 | -0.25413 | 121.7403 | 121.3705 | 121.398 | 60.8748 | -121.7171 | 121.5909 | 121.6543 | 121.5385 | 60.9653 | -121.8351
186.6406 | 122.0444 | -60.9146 | 60.8505 | 1.4211e-13 | -0.0063696 | 0.0016923 | 0.063791 | -0.0038588 | 0.059969 | -0.0069437 | -0.001615 | -0.0013203 | 0.062988 | 0.012389 | 0.061618 | -60.7404 | -0.071851 | -60.8171 | 60.8073 | 60.4422 | 60.4651 | -60.862 | -60.8363 | 0.03241 | -60.9624 | 60.6534 | 60.726 | 60.6056 | -60.9754 | 0.052595 | -0.04319 | 0.17419 | 0.09748 | 0.044885 | -0.40836 | -0.38547 | -0.060808 | -0.1971 | 0.078342 | -0.047738 | 0.01307 | -0.12455 | -0.24497 | 121.7219 | 121.3568 | 121.3797 | 60.8428 | -121.7125 | 121.568 | 121.6406 | 121.5202 | 60.947 | -121.8259
188.3281 | 122.0947 | -60.9329 | 60.8093 | 1.4211e-13 | -0.006797 | 0.0019059 | 0.063791 | -0.0038588 | 0.060182 | 0.00068675 | -0.0014014 | -0.0013203 | 0.062988 | 0.012175 | 0.061618 | -60.7358 | -0.071851 | -60.8171 | 60.8211 | 60.4467 | 60.4651 | -60.8574 | -60.8454 | 0.036989 | -60.9532 | 60.6534 | 60.726 | 60.601 | -60.9754 | 0.075484 | 0.011744 | 0.19708 | 0.11579 | 0.040306 | -0.36258 | -0.34427 | -0.042498 | -0.1559 | 0.087494 | -0.02027 | 0.022228 | -0.08335 | -0.20835 | 121.754 | 121.3797 | 121.398 | 60.8611 | -121.6668 | 121.5863 | 121.6589 | 121.5339 | 60.9699 | -121.7847
189.9844 | 122.0535 | -60.9146 | 60.8643 | 1.4211e-13 | -0.0070106 | 0.0021197 | 0.063363 | -0.0038588 | 0.059755 | 0.00068675 | -0.0014014 | -0.0013203 | 0.062988 | 0.012389 | 0.061404 | -60.7313 | -0.071851 | -60.8217 | 60.8073 | 60.4376 | 60.4651 | -60.862 | -60.8363 | 0.041567 | -60.9624 | 60.6534 | 60.7214 | 60.6056 | -60.98 | 0.052595 | -0.056923 | 0.18334 | 0.092902 | 0.040307 | -0.42667 | -0.3992 | -0.065387 | -0.21084 | 0.078342 | -0.047738 | 0.017649 | -0.14286 | -0.2587 | 121.7219 | 121.3522 | 121.3797 | 60.8428 | -121.7263 | 121.568 | 121.636 | 121.5202 | 60.9562 | -121.8443
191.6562 | 122.081 | -60.8688 | 60.9055 | 1.4211e-13 | -0.006797 | 0.0016923 | 0.063577 | -0.0036452 | 0.059755 | -0.0069437 | -0.0018288 | -0.0013203 | 0.063201 | 0.011748 | 0.061404 | -60.7404 | -0.071851 | -60.8126 | 60.8073 | 60.4422 | 60.4696 | -60.8574 | -60.8408 | 0.036989 | -60.9578 | 60.6534 | 60.726 | 60.601 | -60.9846 | 0.011397 | -0.098122 | 0.12841 | 0.056282 | 0.044885 | -0.46329 | -0.43582 | -0.11574 | -0.25204 | 0.027986 | -0.088936 | 0.026807 | -0.17948 | -0.30448 | 121.6762 | 121.311 | 121.3385 | 60.797 | -121.7629 | 121.5223 | 121.5948 | 121.4698 | 60.9058 | -121.89
193.3125 | 122.0535 | -60.9146 | 60.878 | 1.4211e-13 | -0.0072244 | 0.0019059 | 0.063363 | -0.0038588 | 0.060182 | -0.0069437 | -0.0014014 | -0.0013203 | 0.063201 | 0.012389 | 0.06119 | -60.7313 | -0.067272 | -60.8126 | 60.8119 | 60.4284 | 60.4651 | -60.8529 | -60.8363 | 0.036989 | -60.9624 | 60.6488 | 60.7306 | 60.6056 | -60.98 | 0.061753 | -0.066078 | 0.18334 | 0.10206 | 0.040306 | -0.44956 | -0.41294 | -0.065387 | -0.22915 | 0.078342 | -0.047738 | 0.017649 | -0.14744 | -0.27244 | 121.7265 | 121.343 | 121.3797 | 60.8473 | -121.7309 | 121.5635 | 121.6452 | 121.5202 | 60.9516 | -121.858
195 | 122.0169 | -60.9146 | 60.9009 | 1.4211e-13 | -0.0070106 | 0.0019059 | 0.063363 | -0.0036452 | 0.060182 | 0.00068675 | -0.001615 | -0.0017477 | 0.063201 | 0.012602 | 0.06119 | -60.7358 | -0.071851 | -60.8171 | 60.8073 | 60.4376 | 60.4651 | -60.8574 | -60.8363 | 0.03241 | -60.9578 | 60.6534 | 60.7168 | 60.6101 | -60.9754 | 0.057174 | -0.093544 | 0.17877 | 0.09748 | 0.040306 | -0.4633 | -0.43583 | -0.060808 | -0.24746 | 0.078342 | -0.043159 | 0.017649 | -0.18406 | -0.29075 | 121.7219 | 121.3522 | 121.3797 | 60.8428 | -121.7583 | 121.568 | 121.6314 | 121.5247 | 60.947 | -121.8763
196.75 | 122.0169 | -60.9833 | 60.8231 | 1.4211e-13 | -0.006797 | 0.0019059 | 0.063791 | -0.0038588 | 0.059969 | 0.00068675 | -0.0014014 | -0.0013203 | 0.063201 | 0.012175 | 0.061404 | -60.7313 | -0.062694 | -60.8171 | 60.8073 | 60.4376 | 60.4605 | -60.862 | -60.8363 | 0.03241 | -60.9532 | 60.658 | 60.7214 | 60.6056 | -60.9754 | 0.12126 | -0.015724 | 0.25201 | 0.16614 | 0.044885 | -0.38547 | -0.36258 | 0.007856 | -0.16506 | 0.14701 | 0.030084 | 0.022228 | -0.10166 | -0.2175 | 121.7906 | 121.4209 | 121.4438 | 60.9206 | -121.6851 | 121.6413 | 121.7047 | 121.5888 | 61.0157 | -121.7985
198.4062 | 122.0764 | -60.9375 | 60.8231 | 1.4211e-13 | -0.0065834 | 0.0021197 | 0.063791 | -0.0038588 | 0.059755 | 0.0083173 | -0.0014014 | -0.0015341 | 0.062988 | 0.012602 | 0.060977 | -60.7267 | -0.067272 | -60.8126 | 60.8073 | 60.4376 | 60.4696 | -60.8529 | -60.8408 | 0.036989 | -60.9578 | 60.6534 | 60.726 | 60.601 | -60.9754 | 0.084641 | -0.015724 | 0.21081 | 0.12495 | 0.040306 | -0.38547 | -0.35343 | -0.03792 | -0.16964 | 0.096651 | -0.020271 | 0.017649 | -0.097083 | -0.22208 | 121.7448 | 121.3751 | 121.4071 | 60.8702 | -121.6759 | 121.5909 | 121.6635 | 121.5385 | 60.9745 | -121.7985
200.0781 | 122.0947 | -60.878 | 60.9055 | 1.4211e-13 | -0.0065834 | 0.0016923 | 0.063577 | -0.0042862 | 0.059755 | 0.0083173 | -0.0014014 | -0.0015341 | 0.062988 | 0.012175 | 0.061404 | -60.7358 | -0.067272 | -60.8217 | 60.8073 | 60.4376 | 60.4559 | -60.8529 | -60.8317 | 0.027831 | -60.9532 | 60.6534 | 60.7122 | 60.601 | -60.9754 | 0.025132 | -0.098122 | 0.14214 | 0.056281 | 0.031149 | -0.46787 | -0.44956 | -0.097429 | -0.25204 | 0.046299 | -0.075201 | 0.022228 | -0.19322 | -0.30448 | 121.6853 | 121.3156 | 121.3339 | 60.8107 | -121.7583 | 121.5314 | 121.5902 | 121.479 | 60.9058 | -121.8809
201.7812 | 122.0993 | -60.8643 | 60.9055 | 1.4211e-13 | -0.0070106 | 0.0019059 | 0.063791 | -0.0042862 | 0.059541 | 0.0083173 | -0.0014014 | -0.0013203 | 0.063415 | 0.012602 | 0.06119 | -60.7313 | -0.07643 | -60.8171 | 60.8028 | 60.4422 | 60.4605 | -60.8574 | -60.8363 | 0.027831 | -60.9486 | 60.6488 | 60.7214 | 60.6056 | -60.98 | 0.00682 | -0.1027 | 0.13299 | 0.047126 | 0.040306 | -0.46329 | -0.44498 | -0.11574 | -0.25661 | 0.027988 | -0.084355 | 0.031386 | -0.18406 | -0.2999 | 121.667 | 121.3064 | 121.3247 | 60.7878 | -121.7629 | 121.5131 | 121.5857 | 121.4698 | 60.8921 | -121.8855
203.4531 | 121.962 | -60.9787 | 60.8597 | 1.4211e-13 | -0.0070106 | 0.0019059 | 0.063791 | -0.0038588 | 0.059755 | 0.00068675 | -0.0014014 | -0.0017477 | 0.062988 | 0.012602 | 0.06119 | -60.7404 | -0.071851 | -60.8217 | 60.8028 | 60.4422 | 60.4651 | -60.862 | -60.8408 | 0.036989 | -60.9578 | 60.6397 | 60.7168 | 60.6056 | -60.9708 | 0.11668 | -0.056924 | 0.23828 | 0.15699 | 0.040307 | -0.41752 | -0.39463 | 0.007858 | -0.21999 | 0.13785 | 0.020928 | 0.01307 | -0.14286 | -0.25412 | 121.7815 | 121.4209 | 121.4438 | 60.9068 | -121.7217 | 121.6184 | 121.6955 | 121.5843 | 61.0157 | -121.8305
205.125 | 122.0901 | -60.9604 | 60.8185 | 1.4211e-13 | -0.0070106 | 0.0021197 | 0.063577 | -0.0040724 | 0.059969 | 0.00068675 | -0.001615 | -0.0015341 | 0.062774 | 0.011961 | 0.060977 | -60.7267 | -0.062694 | -60.8217 | 60.8119 | 60.4422 | 60.4605 | -60.8574 | -60.8363 | 0.03241 | -60.9486 | 60.6534 | 60.7168 | 60.601 | -60.98 | 0.10295 | -0.006568 | 0.2337 | 0.13868 | 0.035728 | -0.37632 | -0.358 | -0.019611 | -0.16506 | 0.12412 | 0.011775 | 0.031386 | -0.10166 | -0.2175 | 121.7723 | 121.4026 | 121.4209 | 60.8977 | -121.6759 | 121.6138 | 121.6772 | 121.5614 | 60.9928 | -121.7985
206.8125 | 121.9574 | -60.8917 | 60.9741 | 1.4211e-13 | -0.0065834 | 0.0016923 | 0.063577 | -0.0040724 | 0.059755 | 0.015947 | -0.0014014 | -0.0015341 | 0.063201 | 0.012389 | 0.061618 | -60.7267 | -0.067272 | -60.8126 | 60.8073 | 60.433 | 60.4605 | -60.8574 | -60.8317 | 0.03241 | -60.944 | 60.6443 | 60.7168 | 60.6101 | -60.98 | 0.034286 | -0.16679 | 0.16504 | 0.079171 | 0.044885 | -0.54112 | -0.51364 | -0.088275 | -0.32986 | 0.060032 | -0.052311 | 0.035964 | -0.2573 | -0.36399 | 121.6991 | 121.3247 | 121.3522 | 60.8245 | -121.8316 | 121.536 | 121.6085 | 121.5019 | 60.9241 | -121.9541
208.5312 | 121.9574 | -60.9146 | 60.9192 | 1.4211e-13 | -0.0065834 | 0.0016923 | 0.063791 | -0.0036452 | 0.059969 | 0.00068675 | -0.0018288 | -0.0013203 | 0.063201 | 0.012389 | 0.061404 | -60.7267 | -0.067272 | -60.8126 | 60.7982 | 60.4376 | 60.4559 | -60.8529 | -60.8271 | 0.023253 | -60.9532 | 60.6488 | 60.7168 | 60.5964 | -60.98 | 0.061753 | -0.12101 | 0.18792 | 0.10206 | 0.040306 | -0.48161 | -0.46329 | -0.065387 | -0.27035 | 0.087499 | -0.03858 | 0.026807 | -0.20237 | -0.32279 | 121.7128 | 121.3522 | 121.3705 | 60.8473 | -121.772 | 121.5635 | 121.6314 | 121.511 | 60.9379 | -121.8992
210.2344 | 122.0718 | -60.8505 | 60.878 | 1.4211e-13 | -0.0070106 | 0.0021197 | 0.063791 | -0.0040724 | 0.059969 | 0.00068675 | -0.0014014 | -0.0011067 | 0.063201 | 0.012389 | 0.060977 | -60.7267 | -0.062694 | -60.8171 | 60.8028 | 60.433 | 60.4651 | -60.8483 | -60.8225 | 0.03241 | -60.9486 | 60.6443 | 60.7214 | 60.5964 | -60.98 | 0.002244 | -0.075235 | 0.12384 | 0.033393 | 0.031149 | -0.44499 | -0.41294 | -0.12947 | -0.23373 | 0.027991 | -0.098088 | 0.031386 | -0.15659 | -0.28159 | 121.6533 | 121.2835 | 121.3156 | 60.7878 | -121.7263 | 121.4948 | 121.5719 | 121.4469 | 60.8829 | -121.858
211.8906 | 121.9894 | -60.9329 | 60.9146 | 1.4211e-13 | -0.006797 | 0.0016923 | 0.063791 | -0.0038588 | 0.059755 | 0.00068675 | -0.001615 | -0.0013203 | 0.063201 | 0.012602 | 0.06119 | -60.7267 | -0.062694 | -60.8217 | 60.8028 | 60.4422 | 60.4559 | -60.8574 | -60.8317 | 0.036989 | -60.9486 | 60.6397 | 60.7168 | 60.6056 | -60.9708 | 0.075484 | -0.11186 | 0.20623 | 0.11121 | 0.035728 | -0.47245 | -0.45871 | -0.037919 | -0.27493 | 0.10123 | -0.015691 | 0.022228 | -0.19779 | -0.30906 | 121.7357 | 121.3751 | 121.3888 | 60.8702 | -121.7721 | 121.5726 | 121.6497 | 121.5385 | 60.9699 | -121.8855
213.5781 | 121.9986 | -60.9009 | 60.8963 | 1.4211e-13 | -0.006797 | 0.0019059 | 0.063577 | -0.0036452 | 0.059755 | 0.0083173 | -0.0014014 | -0.0015341 | 0.063201 | 0.012816 | 0.06119 | -60.7267 | -0.067272 | -60.808 | 60.8028 | 60.4376 | 60.4605 | -60.8574 | -60.8271 | 0.036989 | -60.944 | 60.6443 | 60.7077 | 60.6056 | -60.98 | 0.043441 | -0.093545 | 0.17419 | 0.092904 | 0.049463 | -0.45872 | -0.43583 | -0.07912 | -0.25204 | 0.073766 | -0.043156 | 0.035964 | -0.18864 | -0.29075 | 121.7036 | 121.3385 | 121.3614 | 60.8336 | -121.7537 | 121.5451 | 121.6085 | 121.5064 | 60.9379 | -121.8763
215.3438 | 122.0444 | -60.9192 | 60.8231 | 1.4211e-13 | -0.006797 | 0.0019059 | 0.063577 | -0.0038588 | 0.059328 | -0.0069437 | -0.0014014 | -0.0015341 | 0.063415 | 0.012602 | 0.061404 | -60.7221 | -0.067272 | -60.8217 | 60.8073 | 60.433 | 60.4605 | -60.8529 | -60.8225 | 0.03241 | -60.944 | 60.6443 | 60.7122 | 60.601 | -60.9754 | 0.06633 | -0.015724 | 0.19708 | 0.097479 | 0.031149 | -0.39005 | -0.36258 | -0.056231 | -0.1788 | 0.096655 | -0.024846 | 0.031385 | -0.11082 | -0.22208 | 121.7265 | 121.3522 | 121.3797 | 60.8519 | -121.6759 | 121.5635 | 121.6314 | 121.5202 | 60.9516 | -121.7985
217.0156 | 122.0581 | -60.8734 | 60.9009 | 1.4211e-13 | -0.006797 | 0.0016923 | 0.063791 | -0.0036452 | 0.059755 | 0.00068675 | -0.0011878 | -0.0015341 | 0.063201 | 0.012389 | 0.061404 | -60.7221 | -0.058115 | -60.8171 | 60.7982 | 60.433 | 60.4559 | -60.8529 | -60.8271 | 0.036989 | -60.944 | 60.6488 | 60.7077 | 60.601 | -60.9846 | 0.020554 | -0.1027 | 0.1513 | 0.056281 | 0.035727 | -0.46787 | -0.44498 | -0.11116 | -0.25204 | 0.0463 | -0.070622 | 0.040543 | -0.19322 | -0.2999 | 121.6716 | 121.3064 | 121.3293 | 60.8153 | -121.7537 | 121.5223 | 121.5811 | 121.4744 | 60.9104 | -121.8855
218.75 | 122.0215 | -60.9421 | 60.8231 | 1.4211e-13 | -0.006797 | 0.0019059 | 0.063577 | -0.0038588 | 0.059541 | 0.0083173 | -0.0011878 | -0.0013203 | 0.062988 | 0.012816 | 0.061404 | -60.7175 | -0.062694 | -60.8171 | 60.8028 | 60.433 | 60.4559 | -60.8529 | -60.8317 | 0.036989 | -60.9395 | 60.6397 | 60.7122 | 60.5964 | -60.9754 | 0.089219 | -0.020303 | 0.22455 | 0.12495 | 0.035727 | -0.39005 | -0.36716 | -0.033342 | -0.18337 | 0.11039 | 0.002622 | 0.035964 | -0.11082 | -0.22666 | 121.7448 | 121.3751 | 121.398 | 60.8794 | -121.6759 | 121.5818 | 121.6543 | 121.5385 | 60.9791 | -121.7985
220.4375 | 122.0947 | -60.8963 | 60.9009 | 1.4211e-13 | -0.0070106 | 0.0019059 | 0.063577 | -0.0036452 | 0.059969 | 0.00068675 | -0.001615 | -0.0015341 | 0.062774 | 0.012816 | 0.06119 | -60.7267 | -0.058115 | -60.8126 | 60.7936 | 60.433 | 60.4605 | -60.8529 | -60.8317 | 0.046146 | -60.9486 | 60.6443 | 60.7077 | 60.5964 | -60.9708 | 0.043442 | -0.10728 | 0.16961 | 0.083748 | 0.040306 | -0.46787 | -0.4404 | -0.07454 | -0.25662 | 0.064609 | -0.052312 | 0.022228 | -0.19322 | -0.30448 | 121.6899 | 121.3293 | 121.3568 | 60.8382 | -121.7537 | 121.5406 | 121.604 | 121.4927 | 60.9424 | -121.8717
222.125 | 122.0123 | -60.8963 | 60.8643 | 1.4211e-13 | -0.0070106 | 0.0014787 | 0.063791 | -0.0042862 | 0.059541 | 0.00068675 | -0.0014014 | -0.0015341 | 0.062988 | 0.012602 | 0.061404 | -60.7175 | -0.062694 | -60.8171 | 60.8028 | 60.4376 | 60.4559 | -60.8437 | -60.8271 | 0.036989 | -60.9395 | 60.6397 | 60.7031 | 60.5872 | -60.9754 | 0.052599 | -0.061502 | 0.17877 | 0.079169 | 0.02657 | -0.42667 | -0.40836 | -0.079119 | -0.22457 | 0.069188 | -0.043155 | 0.035964 | -0.16118 | -0.27702 | 121.6991 | 121.3339 | 121.3522 | 60.8336 | -121.708 | 121.536 | 121.5994 | 121.4835 | 60.9333 | -121.8397
223.7969 | 121.962 | -60.9283 | 60.8551 | 1.4211e-13 | -0.006797 | 0.0023333 | 0.063577 | -0.0040724 | 0.059755 | 0.00068675 | -0.0014014 | -0.0013203 | 0.062988 | 0.012816 | 0.061404 | -60.7221 | -0.062694 | -60.8171 | 60.7982 | 60.433 | 60.4559 | -60.8483 | -60.8363 | 0.036989 | -60.944 | 60.6443 | 60.7077 | 60.601 | -60.9754 | 0.080064 | -0.056925 | 0.20623 | 0.11121 | 0.031149 | -0.4221 | -0.39921 | -0.047075 | -0.21084 | 0.092075 | -0.01569 | 0.031385 | -0.14744 | -0.25413 | 121.7265 | 121.3614 | 121.3842 | 60.8657 | -121.7034 | 121.5726 | 121.636 | 121.5293 | 60.9653 | -121.8305
225.5 | 121.9711 | -60.8826 | 60.9238 | 1.4211e-13 | -0.0072244 | 0.0016923 | 0.063791 | -0.0040724 | 0.059328 | -0.0069437 | -0.001615 | -0.0015341 | 0.062988 | 0.012816 | 0.061404 | -60.7175 | -0.071851 | -60.8171 | 60.7982 | 60.433 | 60.4605 | -60.8529 | -60.8225 | 0.03241 | -60.944 | 60.6488 | 60.7122 | 60.601 | -60.9754 | 0.029709 | -0.12559 | 0.16504 | 0.065436 | 0.035727 | -0.49076 | -0.46329 | -0.092852 | -0.27492 | 0.060034 | -0.061467 | 0.031385 | -0.21153 | -0.32279 | 121.6807 | 121.3156 | 121.343 | 60.8107 | -121.7766 | 121.5314 | 121.5948 | 121.4835 | 60.915 | -121.8992
227.1875 | 121.9391 | -60.9741 | 60.8597 | 1.4211e-13 | -0.0070106 | 0.0016923 | 0.063791 | -0.0038588 | 0.059541 | 0.0083173 | -0.001615 | -0.0015341 | 0.063201 | 0.012602 | 0.060977 | -60.7221 | -0.058115 | -60.8034 | 60.8028 | 60.4376 | 60.4651 | -60.8483 | -60.8225 | 0.041567 | -60.9486 | 60.6443 | 60.7168 | 60.6101 | -60.9708 | 0.12584 | -0.056924 | 0.25201 | 0.17072 | 0.044884 | -0.4221 | -0.39463 | 0.00328 | -0.21542 | 0.15159 | 0.025508 | 0.022228 | -0.14286 | -0.24955 | 121.7769 | 121.4117 | 121.4392 | 60.916 | -121.708 | 121.6184 | 121.6909 | 121.5843 | 61.0157 | -121.8305
228.8594 | 122.0215 | -60.9055 | 60.8643 | 1.4211e-13 | -0.0072244 | 0.0019059 | 0.063791 | -0.0038588 | 0.059755 | 0.00068675 | -0.001615 | -0.0015341 | 0.062774 | 0.012602 | 0.06119 | -60.7175 | -0.062694 | -60.808 | 60.7982 | 60.433 | 60.4605 | -60.8391 | -60.8317 | 0.036989 | -60.944 | 60.6443 | 60.7077 | 60.5918 | -60.9708 | 0.066334 | -0.06608 | 0.18792 | 0.097482 | 0.031148 | -0.43125 | -0.40378 | -0.065384 | -0.21999 | 0.073765 | -0.038578 | 0.026806 | -0.1566 | -0.27244 | 121.7036 | 121.3385 | 121.3659 | 60.8428 | -121.7034 | 121.5497 | 121.6131 | 121.4973 | 60.9424 | -121.8351
230.5625 | 122.0627 | -60.8826 | 60.8917 | 1.4211e-13 | -0.0070106 | 0.0016923 | 0.063791 | -0.0038588 | 0.059541 | -0.0069437 | -0.001615 | -0.0013203 | 0.062774 | 0.012602 | 0.06119 | -60.7221 | -0.067272 | -60.8126 | 60.789 | 60.4238 | 60.4559 | -60.8437 | -60.8271 | 0.036989 | -60.944 | 60.6443 | 60.7122 | 60.5872 | -60.9708 | 0.038866 | -0.1027 | 0.16046 | 0.070015 | 0.031149 | -0.46788 | -0.43583 | -0.088273 | -0.24746 | 0.055455 | -0.061467 | 0.026806 | -0.17948 | -0.30448 | 121.6716 | 121.3064 | 121.3385 | 60.8153 | -121.7354 | 121.5268 | 121.5948 | 121.4698 | 60.9196 | -121.8626
232.2344 | 122.0261 | -60.9467 | 60.7956 | 1.4211e-13 | -0.0072244 | 0.0019059 | 0.063791 | -0.0036452 | 0.059328 | 0.00068675 | -0.0014014 | -0.0013203 | 0.062774 | 0.012389 | 0.06119 | -60.7175 | -0.062694 | -60.8034 | 60.7982 | 60.433 | 60.4605 | -60.8483 | -60.8225 | 0.03241 | -60.9395 | 60.6351 | 60.7122 | 60.5918 | -60.9708 | 0.098374 | 0.002585 | 0.22912 | 0.14326 | 0.044884 | -0.36259 | -0.33512 | -0.024186 | -0.16049 | 0.12412 | 0.007199 | 0.031385 | -0.083353 | -0.20377 | 121.7448 | 121.3797 | 121.4071 | 60.884 | -121.6439 | 121.5818 | 121.6589 | 121.5385 | 60.9791 | -121.7664
233.8906 | 122.0627 | -60.9055 | 60.8002 | 1.4211e-13 | -0.0072244 | 0.0019059 | 0.063577 | -0.0036452 | 0.059541 | 0.0083173 | -0.0014014 | -0.0015341 | 0.063201 | 0.012602 | 0.061404 | -60.7084 | -0.053537 | -60.808 | 60.789 | 60.4284 | 60.4559 | -60.8483 | -60.8225 | 0.036989 | -60.9395 | 60.6397 | 60.7077 | 60.5918 | -60.9708 | 0.057176 | -0.01115 | 0.19708 | 0.097482 | 0.040306 | -0.37174 | -0.34427 | -0.065384 | -0.16049 | 0.082923 | -0.033999 | 0.031385 | -0.09251 | -0.20835 | 121.6945 | 121.3339 | 121.3614 | 60.8519 | -121.6485 | 121.5451 | 121.6131 | 121.4973 | 60.9424 | -121.771
235.5625 | 122.0215 | -60.9238 | 60.8688 | 1.4211e-13 | -0.0072244 | 0.0016923 | 0.063791 | -0.0040724 | 0.059755 | 0.00068675 | -0.0011878 | -0.0017477 | 0.062774 | 0.012816 | 0.060977 | -60.7175 | -0.067272 | -60.8126 | 60.7936 | 60.4238 | 60.4513 | -60.8437 | -60.818 | 0.03241 | -60.9395 | 60.6443 | 60.7031 | 60.5918 | -60.9663 | 0.080065 | -0.075236 | 0.20623 | 0.11121 | 0.031149 | -0.44499 | -0.41752 | -0.042495 | -0.22457 | 0.10581 | -0.015689 | 0.026806 | -0.16575 | -0.27702 | 121.7174 | 121.3476 | 121.3751 | 60.8565 | -121.7125 | 121.568 | 121.6268 | 121.5156 | 60.9562 | -121.8351
237.2188 | 122.0352 | -60.9421 | 60.8276 | 1.4211e-13 | -0.0072244 | 0.0016923 | 0.063577 | -0.0040724 | 0.059755 | 0.0083173 | -0.001615 | -0.0017477 | 0.062774 | 0.01303 | 0.060977 | -60.713 | -0.067272 | -60.808 | 60.7936 | 60.433 | 60.4559 | -60.8483 | -60.8134 | 0.041567 | -60.944 | 60.6397 | 60.7122 | 60.5964 | -60.9708 | 0.093797 | -0.034038 | 0.22912 | 0.1341 | 0.040306 | -0.39463 | -0.37174 | -0.028763 | -0.18795 | 0.1287 | -0.001957 | 0.026806 | -0.1154 | -0.23124 | 121.7357 | 121.3751 | 121.398 | 60.8748 | -121.6759 | 121.5818 | 121.6543 | 121.5385 | 60.9836 | -121.7985
238.9062 | 121.9391 | -60.9467 | 60.8643 | 1.4211e-13 | -0.0070106 | 0.0019059 | 0.063363 | -0.0036452 | 0.059969 | 0.00068675 | -0.001615 | -0.0013203 | 0.062774 | 0.012602 | 0.060977 | -60.7084 | -0.067272 | -60.8126 | 60.789 | 60.4284 | 60.4651 | -60.8483 | -60.818 | 0.03241 | -60.9349 | 60.6443 | 60.7031 | 60.5918 | -60.9617 | 0.098374 | -0.075237 | 0.23828 | 0.1341 | 0.035728 | -0.43583 | -0.3992 | -0.015028 | -0.21999 | 0.1287 | 0.011778 | 0.026806 | -0.16118 | -0.27244 | 121.7357 | 121.3751 | 121.4117 | 60.8794 | -121.7125 | 121.5909 | 121.6497 | 121.5385 | 60.9791 | -121.8259
240.5781 | 121.9574 | -60.965 | 60.8551 | 1.4211e-13 | -0.0072244 | 0.0019059 | 0.063577 | -0.0038588 | 0.059755 | -0.0069437 | -0.001615 | -0.0015341 | 0.062774 | 0.012816 | 0.060977 | -60.713 | -0.062694 | -60.8217 | 60.7936 | 60.433 | 60.4559 | -60.8437 | -60.8225 | 0.03241 | -60.944 | 60.6305 | 60.7077 | 60.5918 | -60.9708 | 0.12126 | -0.061504 | 0.25201 | 0.14326 | 0.021992 | -0.4221 | -0.39921 | -0.005875 | -0.22458 | 0.14243 | 0.020931 | 0.026806 | -0.14744 | -0.26328 | 121.7586 | 121.398 | 121.4209 | 60.9023 | -121.6988 | 121.5955 | 121.6726 | 121.5568 | 60.9974 | -121.8259
242.25 | 121.9391 | -60.9329 | 60.8597 | 1.4211e-13 | -0.007438 | 0.0014787 | 0.063791 | -0.0040724 | 0.059541 | 0.00068675 | -0.001615 | -0.0015341 | 0.063201 | 0.012816 | 0.060977 | -60.7175 | -0.062694 | -60.808 | 60.789 | 60.4238 | 60.4559 | -60.8437 | -60.818 | 0.036989 | -60.9486 | 60.6397 | 60.7122 | 60.5827 | -60.9663 | 0.08922 | -0.070659 | 0.21539 | 0.12495 | 0.035727 | -0.43583 | -0.40378 | -0.03334 | -0.21999 | 0.11497 | -0.015691 | 0.017649 | -0.14744 | -0.27702 | 121.7219 | 121.3568 | 121.3888 | 60.8702 | -121.7034 | 121.5726 | 121.6452 | 121.5156 | 60.9699 | -121.8259
243.9375 | 121.962 | -60.9238 | 60.8643 | 1.4211e-13 | -0.007438 | 0.0019059 | 0.063577 | -0.0042862 | 0.059755 | 0.00068675 | -0.0014014 | -0.0017477 | 0.06256 | 0.01303 | 0.06119 | -60.713 | -0.058115 | -60.8034 | 60.789 | 60.4238 | 60.4559 | -60.8483 | -60.818 | 0.041567 | -60.9395 | 60.6397 | 60.7122 | 60.5918 | -60.9663 | 0.075486 | -0.075237 | 0.21081 | 0.12037 | 0.044884 | -0.44041 | -0.40836 | -0.042495 | -0.22457 | 0.10581 | -0.015689 | 0.026806 | -0.15202 | -0.27244 | 121.7128 | 121.3476 | 121.3797 | 60.8657 | -121.7125 | 121.5635 | 121.636 | 121.5156 | 60.9653 | -121.8305
245.6094 | 122.0581 | -60.9238 | 60.7956 | 1.4211e-13 | -0.007438 | 0.0019059 | 0.063363 | -0.0038588 | 0.059328 | 0.00068675 | -0.0018288 | -0.0015341 | 0.062988 | 0.013243 | 0.060977 | -60.7084 | -0.062694 | -60.8034 | 60.789 | 60.4193 | 60.4605 | -60.8437 | -60.8134 | 0.041567 | -60.9395 | 60.6397 | 60.7122 | 60.5872 | -60.9663 | 0.080065 | -0.006572 | 0.21539 | 0.12037 | 0.040305 | -0.37632 | -0.33512 | -0.042495 | -0.15591 | 0.11039 | -0.015689 | 0.026806 | -0.083353 | -0.20835 | 121.7128 | 121.343 | 121.3842 | 60.8611 | -121.6393 | 121.5635 | 121.636 | 121.511 | 60.9653 | -121.7619
247.2656 | 122.0261 | -60.9192 | 60.8185 | 1.4211e-13 | -0.0072244 | 0.0021197 | 0.063577 | -0.0038588 | 0.059969 | 0.00068675 | -0.001615 | -0.0017477 | 0.062988 | 0.012816 | 0.060977 | -60.7084 | -0.067272 | -60.808 | 60.7982 | 60.4238 | 60.4513 | -60.8437 | -60.8134 | 0.036989 | -60.9395 | 60.6397 | 60.7077 | 60.5781 | -60.9617 | 0.075487 | -0.020303 | 0.21081 | 0.11121 | 0.035727 | -0.39463 | -0.36716 | -0.042494 | -0.1788 | 0.10581 | -0.020267 | 0.022227 | -0.11082 | -0.2404 | 121.7174 | 121.343 | 121.3705 | 60.8519 | -121.6622 | 121.5589 | 121.6269 | 121.4973 | 60.9562 | -121.7802
248.9531 | 121.9711 | -60.965 | 60.8231 | 1.4211e-13 | -0.0072244 | 0.0019059 | 0.063791 | -0.0040724 | 0.059541 | 0.00068675 | -0.001615 | -0.0015341 | 0.062774 | 0.012602 | 0.060977 | -60.7084 | -0.067272 | -60.8126 | 60.7844 | 60.4238 | 60.4605 | -60.8391 | -60.8225 | 0.036989 | -60.9395 | 60.6351 | 60.7122 | 60.5827 | -60.9663 | 0.12584 | -0.038616 | 0.25659 | 0.15241 | 0.02657 | -0.39921 | -0.36258 | -0.001296 | -0.18795 | 0.14243 | 0.02551 | 0.026806 | -0.11082 | -0.2404 | 121.7494 | 121.3888 | 121.4254 | 60.8977 | -121.6622 | 121.6001 | 121.6772 | 121.5476 | 61.002 | -121.7893
250.6094 | 121.9666 | -60.878 | 60.91 | 1.4211e-13 | -0.007438 | 0.0019059 | 0.063791 | -0.0042862 | 0.059328 | 0.00068675 | -0.001615 | -0.0015341 | 0.06256 | 0.013457 | 0.060977 | -60.7084 | -0.062694 | -60.8034 | 60.789 | 60.4238 | 60.4559 | -60.8391 | -60.8225 | 0.036989 | -60.9349 | 60.6305 | 60.7168 | 60.5872 | -60.9663 | 0.038868 | -0.12101 | 0.16962 | 0.074594 | 0.035726 | -0.48619 | -0.45414 | -0.088271 | -0.27951 | 0.055457 | -0.056886 | 0.031385 | -0.19322 | -0.32279 | 121.667 | 121.3018 | 121.3339 | 60.8153 | -121.7492 | 121.5085 | 121.5948 | 121.4652 | 60.915 | -121.8763
252.2812 | 122.0581 | -60.8505 | 60.8505 | 1.4211e-13 | -0.0072244 | 0.0021197 | 0.063577 | -0.0040724 | 0.059328 | 0.00068675 | -0.001615 | -0.0015341 | 0.062774 | 0.013243 | 0.060763 | -60.7084 | -0.062694 | -60.808 | 60.7844 | 60.4284 | 60.4559 | -60.8483 | -60.818 | 0.036989 | -60.944 | 60.6305 | 60.7077 | 60.5827 | -60.9708 | 0.002244 | -0.066082 | 0.14215 | 0.04255 | 0.040306 | -0.4221 | -0.39463 | -0.12032 | -0.22 | 0.03257 | -0.09351 | 0.026806 | -0.14286 | -0.26786 | 121.635 | 121.279 | 121.3064 | 60.7878 | -121.6988 | 121.4811 | 121.5582 | 121.4332 | 60.8875 | -121.8214
253.9531 | 122.0535 | -60.8414 | 60.8551 | 1.4211e-13 | -0.007438 | 0.0021197 | 0.063577 | -0.0038588 | 0.059541 | -0.0069437 | -0.0014014 | -0.0015341 | 0.062988 | 0.01303 | 0.060977 | -60.7038 | -0.062694 | -60.808 | 60.789 | 60.4284 | 60.4559 | -60.8437 | -60.8134 | 0.03241 | -60.9395 | 60.6351 | 60.7077 | 60.5872 | -60.9663 | -0.002332 | -0.066082 | 0.13757 | 0.033395 | 0.035727 | -0.42668 | -0.39921 | -0.12489 | -0.22 | 0.027993 | -0.098086 | 0.026806 | -0.14744 | -0.26786 | 121.6304 | 121.2698 | 121.2973 | 60.7787 | -121.6988 | 121.4765 | 121.549 | 121.4286 | 60.8738 | -121.8214
255.625 | 121.9711 | -60.8871 | 60.9146 | 1.4211e-13 | -0.007438 | 0.0019059 | 0.063577 | -0.0044998 | 0.059541 | -0.0069437 | -0.0020424 | -0.0015341 | 0.062774 | 0.01303 | 0.060763 | -60.7084 | -0.062694 | -60.808 | 60.7844 | 60.4238 | 60.4559 | -60.8437 | -60.818 | 0.041567 | -60.9257 | 60.6351 | 60.7168 | 60.5872 | -60.9617 | 0.043444 | -0.13017 | 0.17877 | 0.079171 | 0.035727 | -0.49076 | -0.45871 | -0.074537 | -0.27951 | 0.069191 | -0.038574 | 0.035963 | -0.19779 | -0.32737 | 121.6716 | 121.311 | 121.343 | 60.8245 | -121.7583 | 121.5223 | 121.604 | 121.4744 | 60.9287 | -121.8763
257.2969 | 122.0581 | -60.8643 | 60.8963 | 1.4211e-13 | -0.0076516 | 0.0023333 | 0.063363 | -0.0042862 | 0.059541 | -0.0069437 | -0.0018288 | -0.0015341 | 0.06256 | 0.012816 | 0.060763 | -60.7038 | -0.071851 | -60.8034 | 60.7844 | 60.4284 | 60.4513 | -60.8345 | -60.8088 | 0.036989 | -60.9257 | 60.6305 | 60.7168 | 60.5781 | -60.9663 | 0.029714 | -0.11186 | 0.16046 | 0.060861 | 0.031147 | -0.46787 | -0.44498 | -0.102 | -0.26577 | 0.05546 | -0.061462 | 0.040542 | -0.17948 | -0.31822 | 121.6487 | 121.2927 | 121.3156 | 60.7924 | -121.7308 | 121.4948 | 121.5811 | 121.4423 | 60.9012 | -121.8626
258.9844 | 122.0078 | -60.9009 | 60.8551 | 1.4211e-13 | -0.0072244 | 0.0021197 | 0.06315 | -0.0042862 | 0.059328 | 0.0083173 | -0.0014014 | -0.0013203 | 0.062774 | 0.013457 | 0.060977 | -60.6992 | -0.067272 | -60.808 | 60.7844 | 60.4193 | 60.4559 | -60.8345 | -60.8134 | 0.036989 | -60.9303 | 60.6397 | 60.7122 | 60.5781 | -60.9617 | 0.066335 | -0.07066 | 0.20166 | 0.092904 | 0.026569 | -0.43583 | -0.39921 | -0.060804 | -0.21542 | 0.087502 | -0.02942 | 0.031384 | -0.14286 | -0.27702 | 121.6853 | 121.3201 | 121.3568 | 60.8336 | -121.6896 | 121.5406 | 121.6131 | 121.479 | 60.9379 | -121.8168
260.7188 | 122.0535 | -60.8505 | 60.8551 | 1.4211e-13 | -0.007438 | 0.0019059 | 0.063577 | -0.0040724 | 0.059541 | 0.0083173 | -0.0014014 | -0.0015341 | 0.062774 | 0.013243 | 0.06119 | -60.7038 | -0.07643 | -60.808 | 60.7844 | 60.4284 | 60.4467 | -60.8437 | -60.8134 | 0.03241 | -60.9257 | 60.6351 | 60.7077 | 60.5781 | -60.9571 | 0.006823 | -0.07066 | 0.14673 | 0.04255 | 0.035727 | -0.42668 | -0.40836 | -0.10658 | -0.22 | 0.037148 | -0.075195 | 0.031385 | -0.14744 | -0.27702 | 121.635 | 121.279 | 121.2973 | 60.7741 | -121.6988 | 121.4856 | 121.5582 | 121.4286 | 60.8829 | -121.8122
262.4531 | 122.0581 | -60.8505 | 60.8826 | 1.4211e-13 | -0.0072244 | 0.0019059 | 0.063791 | -0.0044998 | 0.059328 | 0.00068675 | -0.0014014 | -0.0017477 | 0.062774 | 0.013457 | 0.060977 | -60.6992 | -0.071851 | -60.7988 | 60.789 | 60.4193 | 60.4559 | -60.8391 | -60.818 | 0.03241 | -60.9257 | 60.6351 | 60.7031 | 60.5781 | -60.9617 | 0.011402 | -0.093547 | 0.15131 | 0.051707 | 0.040305 | -0.4633 | -0.42667 | -0.11116 | -0.24746 | 0.03257 | -0.075195 | 0.035963 | -0.17948 | -0.30448 | 121.6395 | 121.2698 | 121.3064 | 60.7787 | -121.7217 | 121.4856 | 121.5536 | 121.4286 | 60.8829 | -121.8443
264.1406 | 121.9116 | -60.9558 | 60.8276 | 1.4211e-13 | -0.0076516 | 0.0021197 | 0.063791 | -0.0040724 | 0.059114 | -0.0069437 | -0.0014014 | -0.0015341 | 0.063415 | 0.01303 | 0.060549 | -60.6992 | -0.071851 | -60.8034 | 60.7844 | 60.4238 | 60.4467 | -60.8391 | -60.8134 | 0.041567 | -60.9303 | 60.6351 | 60.7031 | 60.5918 | -60.9571 | 0.11669 | -0.043194 | 0.25659 | 0.15241 | 0.035726 | -0.40379 | -0.3809 | -0.001294 | -0.19253 | 0.14243 | 0.025512 | 0.026806 | -0.12455 | -0.23582 | 121.7403 | 121.3797 | 121.4026 | 60.884 | -121.6668 | 121.5909 | 121.6589 | 121.5476 | 60.9974 | -121.7847
265.8438 | 122.0352 | -60.9329 | 60.7864 | 1.4211e-13 | -0.0072244 | 0.0019059 | 0.064005 | -0.0044998 | 0.059328 | 0.015947 | -0.0018288 | -0.0015341 | 0.062774 | 0.013243 | 0.060977 | -60.6992 | -0.07643 | -60.8034 | 60.7844 | 60.4193 | 60.4513 | -60.8391 | -60.818 | 0.036989 | -60.9349 | 60.626 | 60.7077 | 60.5781 | -60.9617 | 0.093799 | -0.001995 | 0.2337 | 0.12953 | 0.035726 | -0.36717 | -0.33512 | -0.028761 | -0.16049 | 0.11497 | -0.001955 | 0.026806 | -0.078777 | -0.20835 | 121.7174 | 121.3522 | 121.3842 | 60.8565 | -121.6256 | 121.5589 | 121.6406 | 121.511 | 60.9699 | -121.7481
267.5156 | 122.0673 | -60.8459 | 60.8734 | 1.4211e-13 | -0.0076516 | 0.0019059 | 0.063363 | -0.0042862 | 0.059328 | 0.015947 | -0.0014014 | -0.0019613 | 0.062774 | 0.013243 | 0.060763 | -60.7038 | -0.067272 | -60.808 | 60.7844 | 60.4238 | 60.4605 | -60.8345 | -60.8088 | 0.03241 | -60.9303 | 60.6305 | 60.7122 | 60.5781 | -60.9663 | 0.011403 | -0.08897 | 0.14215 | 0.037972 | 0.026569 | -0.44957 | -0.41294 | -0.12031 | -0.24289 | 0.037149 | -0.084352 | 0.035963 | -0.16117 | -0.29533 | 121.6304 | 121.2698 | 121.3064 | 60.7787 | -121.708 | 121.4765 | 121.5582 | 121.424 | 60.8784 | -121.8397
269.1875 | 121.9162 | -60.9787 | 60.8597 | 1.4211e-13 | -0.007438 | 0.0021197 | 0.063577 | -0.0042862 | 0.059541 | 0.00068675 | -0.0014014 | -0.0011067 | 0.06256 | 0.013243 | 0.060977 | -60.6992 | -0.071851 | -60.808 | 60.7799 | 60.4238 | 60.4513 | -60.8437 | -60.8134 | 0.036989 | -60.9257 | 60.6351 | 60.7031 | 60.5735 | -60.9571 | 0.135 | -0.079816 | 0.27948 | 0.17072 | 0.035727 | -0.43583 | -0.40836 | 0.021594 | -0.22457 | 0.16532 | 0.052979 | 0.031385 | -0.1566 | -0.28618 | 121.7586 | 121.4025 | 121.43 | 60.9068 | -121.7034 | 121.6138 | 121.6818 | 121.5522 | 61.0157 | -121.8168
270.9375 | 121.9574 | -60.8917 | 60.8734 | 1.4211e-13 | -0.0076516 | 0.0021197 | 0.06315 | -0.0044998 | 0.059541 | 0.00068675 | -0.001615 | -0.0015341 | 0.062988 | 0.013243 | 0.060977 | -60.7038 | -0.07643 | -60.8034 | 60.7844 | 60.4238 | 60.4605 | -60.8437 | -60.818 | 0.03241 | -60.9257 | 60.6305 | 60.7077 | 60.5872 | -60.9617 | 0.048022 | -0.08897 | 0.18793 | 0.088327 | 0.040305 | -0.44957 | -0.41294 | -0.069959 | -0.24289 | 0.073769 | -0.033996 | 0.035963 | -0.16575 | -0.28617 | 121.6762 | 121.3156 | 121.3522 | 60.8153 | -121.7171 | 121.5223 | 121.5994 | 121.479 | 60.9241 | -121.8351
272.6875 | 121.9391 | -60.8643 | 60.9329 | 1.4211e-13 | -0.007438 | 0.0019059 | 0.063363 | -0.0044998 | 0.059328 | 0.00068675 | -0.0011878 | -0.0017477 | 0.062988 | 0.013457 | 0.060977 | -60.7084 | -0.067272 | -60.808 | 60.7799 | 60.4193 | 60.4513 | -60.8345 | -60.8088 | 0.036989 | -60.9257 | 60.626 | 60.7031 | 60.5827 | -60.9617 | 0.029714 | -0.15306 | 0.15588 | 0.056283 | 0.026569 | -0.51365 | -0.4816 | -0.097425 | -0.30697 | 0.05546 | -0.061462 | 0.035963 | -0.22984 | -0.35026 | 121.6441 | 121.2835 | 121.3156 | 60.797 | -121.7675 | 121.4902 | 121.5673 | 121.4469 | 60.9012 | -121.8946
274.4375 | 122.0535 | -60.8414 | 60.8826 | 1.4211e-13 | -0.0078654 | 0.0016923 | 0.06315 | -0.0044998 | 0.059541 | 0.0083173 | -0.0018288 | -0.0015341 | 0.062774 | 0.013243 | 0.060977 | -60.6992 | -0.067272 | -60.7988 | 60.7844 | 60.4193 | 60.4513 | -60.8345 | -60.818 | 0.03241 | -60.9303 | 60.626 | 60.7077 | 60.5872 | -60.9617 | 0.006826 | -0.098125 | 0.14215 | 0.042552 | 0.035726 | -0.4633 | -0.43125 | -0.12031 | -0.25662 | 0.023415 | -0.088929 | 0.031384 | -0.17491 | -0.29533 | 121.6258 | 121.2606 | 121.2927 | 60.7741 | -121.7171 | 121.4673 | 121.549 | 121.4286 | 60.8738 | -121.8443
276.1875 | 121.907 | -60.8414 | 60.91 | 1.4211e-13 | -0.008079 | 0.0019059 | 0.06315 | -0.0047134 | 0.059541 | 0.00068675 | -0.0018288 | -0.0011067 | 0.06256 | 0.013243 | 0.060977 | -60.6946 | -0.067272 | -60.7942 | 60.7799 | 60.4238 | 60.4559 | -60.8391 | -60.8088 | 0.027831 | -60.9257 | 60.626 | 60.6985 | 60.5872 | -60.9617 | 0.002247 | -0.13017 | 0.14673 | 0.04713 | 0.044883 | -0.48619 | -0.45414 | -0.12031 | -0.28408 | 0.032572 | -0.08435 | 0.035963 | -0.21153 | -0.32279 | 121.6212 | 121.2652 | 121.2973 | 60.7741 | -121.7492 | 121.4673 | 121.5399 | 121.4286 | 60.8692 | -121.8717
277.875 | 121.9254 | -60.9283 | 60.8322 | 1.4211e-13 | -0.0072244 | 0.0021197 | 0.063363 | -0.0042862 | 0.059328 | -0.0069437 | -0.001615 | -0.0015341 | 0.062988 | 0.013243 | 0.060977 | -60.6901 | -0.067272 | -60.7942 | 60.7844 | 60.4147 | 60.4467 | -60.8345 | -60.8134 | 0.036989 | -60.9211 | 60.6305 | 60.7122 | 60.5872 | -60.9571 | 0.093801 | -0.047771 | 0.23828 | 0.1341 | 0.040304 | -0.41752 | -0.38547 | -0.02876 | -0.20169 | 0.11497 | 0.007204 | 0.035964 | -0.11997 | -0.24497 | 121.7128 | 121.343 | 121.3751 | 60.8611 | -121.6668 | 121.5589 | 121.6406 | 121.5156 | 60.9653 | -121.7893
279.6094 | 121.9254 | -60.8826 | 60.8963 | 1.4211e-13 | -0.0082926 | 0.0016923 | 0.063577 | -0.0044998 | 0.059541 | -0.0069437 | -0.0018288 | -0.0013203 | 0.062774 | 0.013457 | 0.060763 | -60.6992 | -0.07643 | -60.8034 | 60.7799 | 60.4193 | 60.4467 | -60.8391 | -60.8042 | 0.03241 | -60.9257 | 60.6305 | 60.7077 | 60.5827 | -60.9571 | 0.043445 | -0.11644 | 0.18335 | 0.079171 | 0.035726 | -0.47703 | -0.44956 | -0.074537 | -0.26577 | 0.078349 | -0.043152 | 0.031385 | -0.18864 | -0.31364 | 121.6624 | 121.3018 | 121.3293 | 60.8061 | -121.7354 | 121.5131 | 121.5902 | 121.4652 | 60.915 | -121.8534
281.3281 | 122.0352 | -60.8963 | 60.7773 | 1.4211e-13 | -0.0078654 | 0.0016923 | 0.063791 | -0.0044998 | 0.059541 | 0.00068675 | -0.001615 | -0.0017477 | 0.062988 | 0.013457 | 0.060763 | -60.6992 | -0.062694 | -60.7942 | 60.7799 | 60.4147 | 60.4559 | -60.83 | -60.8088 | 0.027831 | -60.9166 | 60.626 | 60.6985 | 60.5781 | -60.9617 | 0.066336 | 0.002581 | 0.19708 | 0.10206 | 0.035725 | -0.36259 | -0.32139 | -0.065382 | -0.15133 | 0.087503 | -0.020261 | 0.045121 | -0.078779 | -0.1992 | 121.6762 | 121.311 | 121.3522 | 60.8336 | -121.6072 | 121.5223 | 121.5948 | 121.4744 | 60.9241 | -121.739
283 | 122.0078 | -60.9009 | 60.7681 | 1.4211e-13 | -0.0078654 | 0.0014787 | 0.06315 | -0.0042862 | 0.059541 | -0.014574 | -0.001615 | -0.0015341 | 0.062774 | 0.013457 | 0.060549 | -60.6946 | -0.07643 | -60.7988 | 60.7799 | 60.4101 | 60.4559 | -60.83 | -60.7996 | 0.036989 | -60.9211 | 60.626 | 60.7077 | 60.5781 | -60.9617 | 0.070914 | 0.011737 | 0.20624 | 0.10206 | 0.031147 | -0.35802 | -0.31223 | -0.060804 | -0.14218 | 0.10124 | -0.020262 | 0.040542 | -0.060466 | -0.19004 | 121.6807 | 121.311 | 121.3568 | 60.8244 | -121.5981 | 121.5268 | 121.6085 | 121.479 | 60.9379 | -121.7298
284.7344 | 121.9391 | -60.8917 | 60.8643 | 1.4211e-13 | -0.0078654 | 0.0021197 | 0.063577 | -0.0047134 | 0.059328 | -0.0069437 | -0.001615 | -0.0017477 | 0.062988 | 0.013457 | 0.06119 | -60.6901 | -0.062694 | -60.7988 | 60.7799 | 60.4284 | 60.4467 | -60.83 | -60.7951 | 0.03241 | -60.9211 | 60.626 | 60.7077 | 60.5781 | -60.9571 | 0.061759 | -0.084394 | 0.20166 | 0.092906 | 0.031147 | -0.43583 | -0.41752 | -0.065381 | -0.23831 | 0.096662 | -0.029417 | 0.035964 | -0.1566 | -0.28618 | 121.6716 | 121.3202 | 121.3385 | 60.829 | -121.6942 | 121.5177 | 121.5994 | 121.4698 | 60.9241 | -121.8214
286.4219 | 121.9437 | -60.8871 | 60.9009 | 1.4211e-13 | -0.0078654 | 0.0014787 | 0.063363 | -0.0044998 | 0.059328 | 0.00068675 | -0.0014014 | -0.0015341 | 0.062774 | 0.013243 | 0.060977 | -60.6901 | -0.071851 | -60.7942 | 60.7844 | 60.4284 | 60.4467 | -60.8345 | -60.8042 | 0.041567 | -60.9211 | 60.6214 | 60.7031 | 60.5781 | -60.9525 | 0.052602 | -0.11644 | 0.19708 | 0.092906 | 0.040304 | -0.47245 | -0.45414 | -0.06538 | -0.27951 | 0.082927 | -0.033995 | 0.031385 | -0.1978 | -0.3228 | 121.6716 | 121.3156 | 121.3339 | 60.8153 | -121.7354 | 121.5085 | 121.5902 | 121.4652 | 60.9287 | -121.8534
288.1562 | 121.907 | -60.8688 | 60.9055 | 1.4211e-13 | -0.0076516 | 0.0016923 | 0.063363 | -0.0042862 | 0.059114 | 0.00068675 | -0.001615 | -0.0017477 | 0.06256 | 0.013884 | 0.060977 | -60.6901 | -0.067272 | -60.7942 | 60.7753 | 60.4238 | 60.4559 | -60.8345 | -60.8042 | 0.03241 | -60.9257 | 60.626 | 60.7031 | 60.5735 | -60.9617 | 0.034291 | -0.13017 | 0.17877 | 0.074595 | 0.040304 | -0.48161 | -0.44956 | -0.092848 | -0.27951 | 0.064616 | -0.056885 | 0.035963 | -0.20237 | -0.33195 | 121.6441 | 121.2927 | 121.3247 | 60.8016 | -121.74 | 121.4948 | 121.5719 | 121.4423 | 60.9012 | -121.8671
289.8281 | 121.9345 | -60.878 | 60.9146 | 1.4211e-13 | -0.0082926 | 0.0016923 | 0.063577 | -0.0040724 | 0.059328 | -0.0069437 | -0.001615 | -0.0015341 | 0.062774 | 0.013671 | 0.060763 | -60.6946 | -0.067272 | -60.7942 | 60.7799 | 60.4238 | 60.4559 | -60.8345 | -60.7996 | 0.03241 | -60.9211 | 60.626 | 60.7031 | 60.5827 | -60.9571 | 0.043447 | -0.13475 | 0.18335 | 0.083751 | 0.040304 | -0.49076 | -0.45871 | -0.079114 | -0.28866 | 0.07835 | -0.04315 | 0.035964 | -0.21153 | -0.33195 | 121.6579 | 121.3018 | 121.3339 | 60.8107 | -121.7492 | 121.5039 | 121.5811 | 121.4607 | 60.9104 | -121.8717
291.5625 | 121.9894 | -60.9055 | 60.8047 | 1.4211e-13 | -0.0082926 | 0.0019059 | 0.06315 | -0.0047134 | 0.059114 | 0.00068675 | -0.001615 | -0.0015341 | 0.06256 | 0.013457 | 0.060977 | -60.6901 | -0.071851 | -60.7897 | 60.7799 | 60.4147 | 60.4513 | -60.83 | -60.8088 | 0.036989 | -60.9166 | 60.6214 | 60.6985 | 60.5689 | -60.9525 | 0.075492 | -0.024885 | 0.2154 | 0.11579 | 0.040303 | -0.39006 | -0.35343 | -0.047069 | -0.18338 | 0.096659 | -0.011105 | 0.035964 | -0.10625 | -0.23582 | 121.6853 | 121.3201 | 121.3568 | 60.8336 | -121.6347 | 121.5268 | 121.604 | 121.4744 | 60.9424 | -121.7573
293.2969 | 121.8796 | -60.9192 | 60.8505 | 1.4211e-13 | -0.008079 | 0.0016923 | 0.063363 | -0.0044998 | 0.059114 | 0.00068675 | -0.0018288 | -0.0013203 | 0.062774 | 0.013671 | 0.060977 | -60.6901 | -0.071851 | -60.7942 | 60.7844 | 60.4284 | 60.4513 | -60.8254 | -60.7996 | 0.036989 | -60.9211 | 60.626 | 60.7031 | 60.5735 | -60.9617 | 0.093803 | -0.066082 | 0.22913 | 0.12495 | 0.031146 | -0.4221 | -0.39921 | -0.042494 | -0.22457 | 0.11955 | -0.001952 | 0.040542 | -0.14744 | -0.27702 | 121.7036 | 121.3476 | 121.3705 | 60.8473 | -121.6759 | 121.5451 | 121.6223 | 121.4927 | 60.9562 | -121.8122
294.9688 | 121.8979 | -60.8688 | 60.9192 | 1.4211e-13 | -0.0078654 | 0.0016923 | 0.063577 | -0.004927 | 0.059328 | 0.00068675 | -0.001615 | -0.0015341 | 0.063201 | 0.013671 | 0.060549 | -60.6809 | -0.071851 | -60.7851 | 60.7844 | 60.4238 | 60.4513 | -60.83 | -60.7905 | 0.03241 | -60.912 | 60.6305 | 60.6985 | 60.5781 | -60.9479 | 0.03887 | -0.13475 | 0.18793 | 0.083751 | 0.044881 | -0.49534 | -0.46787 | -0.079112 | -0.28866 | 0.078352 | -0.043149 | 0.035963 | -0.22069 | -0.34111 | 121.6533 | 121.2927 | 121.3202 | 60.797 | -121.7492 | 121.4994 | 121.5673 | 121.4469 | 60.9012 | -121.8671
296.7031 | 122.0398 | -60.8871 | 60.7819 | 1.4211e-13 | -0.0082926 | 0.0019059 | 0.062936 | -0.0042862 | 0.059114 | 0.00068675 | -0.0014014 | -0.0017477 | 0.062988 | 0.013671 | 0.060549 | -60.6901 | -0.067272 | -60.7897 | 60.7844 | 60.4193 | 60.4559 | -60.8254 | -60.7951 | 0.036989 | -60.9257 | 60.626 | 60.6939 | 60.5781 | -60.9479 | 0.06176 | 0.002583 | 0.19708 | 0.097484 | 0.035724 | -0.36259 | -0.32596 | -0.060801 | -0.15591 | 0.092084 | -0.038574 | 0.022227 | -0.087934 | -0.20378 | 121.6716 | 121.3064 | 121.343 | 60.8199 | -121.6072 | 121.5131 | 121.5811 | 121.4652 | 60.9241 | -121.7298
298.4375 | 121.9711 | -60.9375 | 60.8185 | 1.4211e-13 | -0.0078654 | 0.0016923 | 0.06315 | -0.0051408 | 0.059114 | 0.00068675 | -0.001615 | -0.0013203 | 0.06256 | 0.013243 | 0.060977 | -60.6992 | -0.062694 | -60.7942 | 60.7799 | 60.4238 | 60.4422 | -60.8254 | -60.8042 | 0.041567 | -60.9166 | 60.6214 | 60.7031 | 60.5827 | -60.9525 | 0.11211 | -0.038617 | 0.23828 | 0.14326 | 0.031146 | -0.39463 | -0.37632 | -0.015026 | -0.19711 | 0.13328 | 0.020938 | 0.035964 | -0.1154 | -0.23582 | 121.7174 | 121.3613 | 121.3797 | 60.8748 | -121.6439 | 121.5589 | 121.6406 | 121.5202 | 60.9791 | -121.771
300.1719 | 121.9849 | -60.8963 | 60.8551 | 1.4211e-13 | -0.0082926 | 0.0014787 | 0.06315 | -0.0042862 | 0.0589 | -0.0069437 | -0.001615 | -0.0013203 | 0.06256 | 0.013671 | 0.060763 | -60.6855 | -0.071851 | -60.7897 | 60.7799 | 60.4101 | 60.4513 | -60.8254 | -60.7996 | 0.036989 | -60.9211 | 60.626 | 60.6985 | 60.5735 | -60.9525 | 0.070915 | -0.075239 | 0.21082 | 0.10664 | 0.035724 | -0.44499 | -0.40378 | -0.056225 | -0.22915 | 0.09666 | -0.02484 | 0.031385 | -0.1566 | -0.2816 | 121.6762 | 121.3064 | 121.3476 | 60.8244 | -121.6805 | 121.5223 | 121.5948 | 121.4698 | 60.9333 | -121.8076
301.8594 | 121.9574 | -60.8551 | 60.9055 | 1.4211e-13 | -0.008079 | 0.0021197 | 0.063363 | -0.0047134 | 0.0589 | 0.00068675 | -0.001615 | -0.0015341 | 0.062988 | 0.013884 | 0.060549 | -60.6901 | -0.067272 | -60.7851 | 60.7799 | 60.4101 | 60.4422 | -60.8254 | -60.8042 | 0.041567 | -60.9166 | 60.6214 | 60.6939 | 60.5643 | -60.9525 | 0.029717 | -0.12559 | 0.16504 | 0.070019 | 0.040302 | -0.49535 | -0.4633 | -0.097423 | -0.28409 | 0.050884 | -0.061459 | 0.035964 | -0.21153 | -0.34111 | 121.635 | 121.2652 | 121.2973 | 60.7878 | -121.7308 | 121.4765 | 121.549 | 121.4195 | 60.8967 | -121.858
303.6094 | 122.0032 | -60.8963 | 60.8139 | 1.4211e-13 | -0.0082926 | 0.0019059 | 0.06315 | -0.0044998 | 0.059114 | 0.00068675 | -0.0018288 | -0.0017477 | 0.06256 | 0.013671 | 0.060763 | -60.6901 | -0.067272 | -60.7897 | 60.7707 | 60.4101 | 60.4513 | -60.8254 | -60.7996 | 0.036989 | -60.9211 | 60.626 | 60.7031 | 60.5689 | -60.9571 | 0.070915 | -0.043197 | 0.20624 | 0.10664 | 0.035724 | -0.40379 | -0.36259 | -0.060804 | -0.18795 | 0.09666 | -0.02484 | 0.035964 | -0.11082 | -0.24498 | 121.667 | 121.3064 | 121.3476 | 60.829 | -121.6393 | 121.5223 | 121.5994 | 121.4652 | 60.9333 | -121.771
305.2656 | 122.0306 | -60.8414 | 60.8597 | 1.4211e-13 | -0.008079 | 0.0016923 | 0.062936 | -0.0044998 | 0.0589 | 0.00068675 | -0.0018288 | -0.0013203 | 0.063201 | 0.013671 | 0.060549 | -60.6946 | -0.067272 | -60.7851 | 60.7707 | 60.4147 | 60.4513 | -60.8208 | -60.8042 | 0.027831 | -60.9166 | 60.6214 | 60.6893 | 60.5689 | -60.9479 | 0.020563 | -0.088973 | 0.14673 | 0.056286 | 0.035723 | -0.44499 | -0.40836 | -0.10658 | -0.23831 | 0.037151 | -0.075192 | 0.031385 | -0.17033 | -0.29075 | 121.6121 | 121.2561 | 121.2927 | 60.7741 | -121.6805 | 121.4627 | 121.5307 | 121.4103 | 60.8692 | -121.8076
307 | 121.8887 | -60.9421 | 60.8551 | 1.4211e-13 | -0.008079 | 0.0014787 | 0.06315 | -0.0047134 | 0.0589 | -0.0069437 | -0.0020424 | -0.0015341 | 0.062774 | 0.013884 | 0.060763 | -60.6855 | -0.067272 | -60.7942 | 60.7661 | 60.4193 | 60.4513 | -60.8345 | -60.7996 | 0.036989 | -60.9166 | 60.626 | 60.6985 | 60.5689 | -60.9525 | 0.10753 | -0.088974 | 0.25659 | 0.14784 | 0.040304 | -0.43583 | -0.40378 | -0.010448 | -0.22915 | 0.14244 | 0.025516 | 0.035964 | -0.1566 | -0.28618 | 121.7082 | 121.3613 | 121.3934 | 60.8748 | -121.6896 | 121.568 | 121.6406 | 121.511 | 60.9791 | -121.8076
308.75 | 122.0123 | -60.8963 | 60.7956 | 1.4211e-13 | -0.0085064 | 0.0016923 | 0.063363 | -0.004927 | 0.0589 | -0.0069437 | -0.0018288 | -0.0013203 | 0.062774 | 0.013884 | 0.060549 | -60.6855 | -0.067272 | -60.7897 | 60.7753 | 60.4193 | 60.4513 | -60.8254 | -60.8042 | 0.041567 | -60.912 | 60.6168 | 60.6985 | 60.5689 | -60.9571 | 0.070915 | -0.020307 | 0.21082 | 0.10664 | 0.035724 | -0.37632 | -0.34427 | -0.060804 | -0.1788 | 0.092082 | -0.015683 | 0.045121 | -0.097089 | -0.22667 | 121.6716 | 121.3156 | 121.3476 | 60.829 | -121.621 | 121.5131 | 121.5948 | 121.4652 | 60.9379 | -121.7527
310.4219 | 122.0123 | -60.8688 | 60.7636 | 1.4211e-13 | -0.0082926 | 0.0016923 | 0.062936 | -0.0044998 | 0.058687 | 0.00068675 | -0.001615 | -0.0015341 | 0.062774 | 0.013884 | 0.060549 | -60.6809 | -0.058115 | -60.7942 | 60.7753 | 60.4147 | 60.4467 | -60.83 | -60.7951 | 0.036989 | -60.912 | 60.626 | 60.6893 | 60.5689 | -60.9479 | 0.03887 | 0.011736 | 0.18793 | 0.074595 | 0.035725 | -0.34886 | -0.31681 | -0.079112 | -0.1376 | 0.073773 | -0.043149 | 0.035963 | -0.074203 | -0.19462 | 121.6441 | 121.2835 | 121.3156 | 60.8107 | -121.5935 | 121.4948 | 121.5582 | 121.4378 | 60.9058 | -121.7115
312.1562 | 121.8979 | -60.878 | 60.9146 | 1.4211e-13 | -0.0085064 | 0.0016923 | 0.06315 | -0.004927 | 0.059328 | 0.00068675 | -0.0014014 | -0.0017477 | 0.062774 | 0.013457 | 0.060549 | -60.6855 | -0.062694 | -60.7897 | 60.7661 | 60.4193 | 60.4513 | -60.8254 | -60.7951 | 0.036989 | -60.9166 | 60.626 | 60.6939 | 60.5735 | -60.9525 | 0.052605 | -0.14848 | 0.19251 | 0.088329 | 0.035724 | -0.49534 | -0.46329 | -0.074535 | -0.28866 | 0.082929 | -0.038571 | 0.035964 | -0.22069 | -0.34111 | 121.6441 | 121.2973 | 121.3293 | 60.8153 | -121.74 | 121.5039 | 121.5719 | 121.4515 | 60.915 | -121.8671
313.8906 | 121.9757 | -60.8917 | 60.8185 | 1.4211e-13 | -0.0085064 | 0.0016923 | 0.06315 | -0.0044998 | 0.0589 | 0.00068675 | -0.0018288 | -0.0013203 | 0.062774 | 0.013884 | 0.060763 | -60.6901 | -0.067272 | -60.7851 | 60.7753 | 60.4147 | 60.4467 | -60.8254 | -60.7905 | 0.036989 | -60.912 | 60.6214 | 60.6939 | 60.5689 | -60.9525 | 0.066338 | -0.043195 | 0.20166 | 0.10664 | 0.040302 | -0.40379 | -0.37174 | -0.060802 | -0.19711 | 0.10124 | -0.02026 | 0.040542 | -0.12456 | -0.24956 | 121.667 | 121.3064 | 121.3385 | 60.8245 | -121.6439 | 121.5131 | 121.5857 | 121.4607 | 60.9287 | -121.771
315.5781 | 122.0352 | -60.8414 | 60.8551 | 1.4211e-13 | -0.0085064 | 0.0016923 | 0.06315 | -0.0042862 | 0.0589 | -0.0069437 | -0.0018288 | -0.0015341 | 0.062774 | 0.013671 | 0.060763 | -60.6809 | -0.067272 | -60.7851 | 60.7707 | 60.4193 | 60.4422 | -60.8254 | -60.7905 | 0.03241 | -60.9211 | 60.6214 | 60.6939 | 60.5643 | -60.9479 | 0.015984 | -0.084396 | 0.16046 | 0.056286 | 0.040302 | -0.43583 | -0.41294 | -0.10658 | -0.23373 | 0.050887 | -0.079771 | 0.026806 | -0.16118 | -0.29075 | 121.6121 | 121.2606 | 121.2835 | 60.7741 | -121.6805 | 121.4627 | 121.5353 | 121.4057 | 60.8738 | -121.803
317.2969 | 121.9803 | -60.8414 | 60.8414 | 1.4211e-13 | -0.00872 | 0.0016923 | 0.06315 | -0.0047134 | 0.059114 | 0.00068675 | -0.001615 | -0.0019613 | 0.062774 | 0.013884 | 0.060549 | -60.6809 | -0.062694 | -60.7805 | 60.7753 | 60.4147 | 60.4467 | -60.8208 | -60.7996 | 0.041567 | -60.912 | 60.6168 | 60.6939 | 60.5689 | -60.9479 | 0.020563 | -0.066084 | 0.16046 | 0.060865 | 0.040302 | -0.42668 | -0.39463 | -0.10658 | -0.22458 | 0.041729 | -0.070614 | 0.035963 | -0.14744 | -0.27244 | 121.6167 | 121.2561 | 121.2881 | 60.7787 | -121.6622 | 121.4582 | 121.5353 | 121.4103 | 60.8829 | -121.7893
319.0312 | 121.9711 | -60.8734 | 60.8414 | 1.4211e-13 | -0.00872 | 0.0014787 | 0.06315 | -0.0042862 | 0.058473 | 0.00068675 | -0.0014014 | -0.0013203 | 0.062774 | 0.013671 | 0.060763 | -60.6809 | -0.067272 | -60.7805 | 60.7661 | 60.4147 | 60.4513 | -60.83 | -60.7905 | 0.046146 | -60.912 | 60.6168 | 60.6939 | 60.5598 | -60.9479 | 0.043448 | -0.075241 | 0.19251 | 0.092908 | 0.04946 | -0.42668 | -0.39005 | -0.074534 | -0.22458 | 0.08293 | -0.038571 | 0.035963 | -0.14744 | -0.2816 | 121.6395 | 121.2881 | 121.3247 | 60.8061 | -121.6713 | 121.4902 | 121.5673 | 121.4332 | 60.9196 | -121.7893
320.7031 | 121.9894 | -60.8826 | 60.7956 | 1.4211e-13 | -0.00872 | 0.0019059 | 0.062722 | -0.0044998 | 0.059114 | 0.00068675 | -0.0014014 | -0.0013203 | 0.062774 | 0.013884 | 0.060763 | -60.6809 | -0.062694 | -60.7805 | 60.7753 | 60.4147 | 60.4422 | -60.8254 | -60.7951 | 0.036989 | -60.912 | 60.6168 | 60.6893 | 60.5598 | -60.9525 | 0.057182 | -0.020307 | 0.20166 | 0.10206 | 0.044881 | -0.3809 | -0.35343 | -0.069958 | -0.1788 | 0.087506 | -0.029416 | 0.040542 | -0.10625 | -0.23582 | 121.6579 | 121.2973 | 121.3247 | 60.8199 | -121.621 | 121.4994 | 121.5719 | 121.4423 | 60.9196 | -121.7481
322.4375 | 122.0032 | -60.8505 | 60.8459 | 1.4211e-13 | -0.00872 | 0.0014787 | 0.062936 | -0.0042862 | 0.0589 | -0.0069437 | -0.0018288 | -0.0028161 | 0.062774 | 0.014098 | 0.060549 | -60.6855 | -0.067272 | -60.7805 | 60.7707 | 60.4147 | 60.433 | -60.8254 | -60.7905 | 0.041567 | -60.912 | 60.6122 | 60.6939 | 60.5689 | -60.9479 | 0.025139 | -0.07524 | 0.16504 | 0.07002 | 0.044881 | -0.43126 | -0.41294 | -0.097422 | -0.23373 | 0.060042 | -0.061459 | 0.035963 | -0.15202 | -0.27702 | 121.6212 | 121.2652 | 121.2835 | 60.7833 | -121.6713 | 121.4627 | 121.5445 | 121.4195 | 60.8921 | -121.7939
324.1094 | 121.9711 | -60.878 | 60.8139 | 1.4211e-13 | -0.0085064 | 0.0019059 | 0.062936 | -0.0047134 | 0.0589 | 0.00068675 | -0.0018288 | -0.0030297 | 0.062774 | 0.013884 | 0.060763 | -60.6763 | -0.07643 | -60.7805 | 60.7707 | 60.4147 | 60.4422 | -60.8254 | -60.7951 | 0.03241 | -60.912 | 60.6168 | 60.6939 | 60.5689 | -60.9525 | 0.052605 | -0.043197 | 0.20166 | 0.097486 | 0.044881 | -0.39921 | -0.37174 | -0.074535 | -0.19711 | 0.082929 | -0.033993 | 0.040542 | -0.11998 | -0.24498 | 121.6487 | 121.2927 | 121.3202 | 60.8016 | -121.6393 | 121.4948 | 121.5719 | 121.4469 | 60.9104 | -121.7664
325.8438 | 121.9391 | -60.8917 | 60.8322 | 1.4211e-13 | -0.00872 | 0.0019059 | 0.062722 | -0.004927 | 0.058687 | -0.0069437 | -0.0018288 | -0.0026023 | 0.062988 | 0.013671 | 0.060763 | -60.6763 | -0.062694 | -60.7805 | 60.7707 | 60.4101 | 60.4513 | -60.8254 | -60.7951 | 0.041567 | -60.912 | 60.6122 | 60.6893 | 60.5735 | -60.9479 | 0.066338 | -0.061507 | 0.2154 | 0.11122 | 0.044881 | -0.4221 | -0.3809 | -0.056223 | -0.22 | 0.096662 | -0.02026 | 0.035963 | -0.14287 | -0.25871 | 121.6624 | 121.3018 | 121.343 | 60.829 | -121.6576 | 121.5039 | 121.5811 | 121.4652 | 60.9333 | -121.7802
327.5156 | 122.0123 | -60.8231 | 60.8322 | 1.4211e-13 | -0.00872 | 0.0019059 | 0.06315 | -0.0047134 | 0.059114 | 0.0083173 | -0.001615 | -0.0026023 | 0.062774 | 0.014098 | 0.060763 | -60.6855 | -0.071851 | -60.7759 | 60.7707 | 60.4101 | 60.4422 | -60.8208 | -60.7951 | 0.041567 | -60.9074 | 60.6168 | 60.6893 | 60.5689 | -60.9479 | 0.002252 | -0.061507 | 0.13757 | 0.047132 | 0.04488 | -0.4221 | -0.39005 | -0.12489 | -0.21542 | 0.027997 | -0.084346 | 0.040542 | -0.14287 | -0.26329 | 121.5938 | 121.2332 | 121.2652 | 60.7512 | -121.653 | 121.4399 | 121.5124 | 121.392 | 60.8646 | -121.7802
329.25 | 121.9254 | -60.8597 | 60.9055 | 1.4211e-13 | -0.0085064 | 0.0012649 | 0.062936 | -0.0047134 | 0.059114 | 0.00068675 | -0.0014014 | -0.0026023 | 0.062774 | 0.014098 | 0.060763 | -60.6763 | -0.071851 | -60.7805 | 60.7707 | 60.4193 | 60.4422 | -60.8254 | -60.7905 | 0.036989 | -60.9074 | 60.6122 | 60.6893 | 60.5689 | -60.9479 | 0.034294 | -0.13475 | 0.18335 | 0.079175 | 0.044881 | -0.48619 | -0.4633 | -0.088267 | -0.29324 | 0.069197 | -0.047725 | 0.040542 | -0.21611 | -0.33653 | 121.6304 | 121.2789 | 121.3018 | 60.7878 | -121.7308 | 121.4719 | 121.549 | 121.4286 | 60.8967 | -121.8534
330.9844 | 122.0261 | -60.8505 | 60.8505 | 1.4211e-13 | -0.0085064 | 0.0019059 | 0.06315 | -0.0044998 | 0.058473 | -0.0069437 | -0.001615 | -0.0028161 | 0.062774 | 0.013671 | 0.060763 | -60.6763 | -0.062694 | -60.7759 | 60.7707 | 60.4101 | 60.4467 | -60.8208 | -60.7859 | 0.041567 | -60.9074 | 60.6122 | 60.6893 | 60.5598 | -60.9479 | 0.029718 | -0.079818 | 0.1742 | 0.074598 | 0.04488 | -0.44041 | -0.40378 | -0.097422 | -0.23831 | 0.064621 | -0.05688 | 0.040542 | -0.16118 | -0.29076 | 121.6212 | 121.2606 | 121.2973 | 60.7878 | -121.6713 | 121.4627 | 121.5399 | 121.4103 | 60.8921 | -121.7985
332.6562 | 121.8704 | -60.91 | 60.8231 | 1.4211e-13 | -0.0089338 | 0.0016923 | 0.06315 | -0.0047134 | 0.058687 | 0.00068675 | -0.0018288 | -0.0023887 | 0.06256 | 0.013884 | 0.060549 | -60.6763 | -0.067272 | -60.7759 | 60.7661 | 60.4193 | 60.4467 | -60.8208 | -60.7905 | 0.041567 | -60.9074 | 60.6122 | 60.6893 | 60.5735 | -60.9525 | 0.089227 | -0.05693 | 0.23371 | 0.13411 | 0.04488 | -0.40379 | -0.37632 | -0.042492 | -0.21084 | 0.11955 | 0.002629 | 0.045121 | -0.13371 | -0.24955 | 121.6762 | 121.3293 | 121.3568 | 60.8428 | -121.6439 | 121.5222 | 121.5994 | 121.4835 | 60.9516 | -121.7756
334.3906 | 121.9025 | -60.8688 | 60.8871 | 1.4211e-13 | -0.00872 | 0.0016923 | 0.063363 | -0.0044998 | 0.058687 | 0.00068675 | -0.001615 | -0.0026023 | 0.06256 | 0.013884 | 0.060549 | -60.6717 | -0.067272 | -60.7805 | 60.7616 | 60.4101 | 60.4467 | -60.8254 | -60.7905 | 0.036989 | -60.8982 | 60.6122 | 60.6893 | 60.5689 | -60.9479 | 0.043449 | -0.1256 | 0.19709 | 0.08833 | 0.044881 | -0.47704 | -0.44041 | -0.079112 | -0.27493 | 0.078352 | -0.029413 | 0.049699 | -0.1978 | -0.31822 | 121.6304 | 121.2789 | 121.3156 | 60.8016 | -121.7125 | 121.481 | 121.5582 | 121.4378 | 60.9058 | -121.8351
336.125 | 121.9254 | -60.8826 | 60.8597 | 1.4211e-13 | -0.0085064 | 0.0016923 | 0.06315 | -0.0042862 | 0.058687 | -0.0069437 | -0.0018288 | -0.0026023 | 0.06256 | 0.013884 | 0.060763 | -60.6763 | -0.062694 | -60.7759 | 60.7616 | 60.4147 | 60.4467 | -60.8254 | -60.7859 | 0.041567 | -60.8982 | 60.6076 | 60.6893 | 60.5735 | -60.9479 | 0.057182 | -0.098129 | 0.20624 | 0.10664 | 0.049459 | -0.44499 | -0.41294 | -0.065379 | -0.25204 | 0.096664 | -0.01568 | 0.049699 | -0.17033 | -0.28618 | 121.6441 | 121.2973 | 121.3293 | 60.8199 | -121.6851 | 121.4902 | 121.5719 | 121.4561 | 60.9241 | -121.8076
337.8594 | 121.9254 | -60.9146 | 60.8002 | 1.4211e-13 | -0.00872 | 0.0016923 | 0.063363 | -0.0047134 | 0.0589 | 0.00068675 | -0.001615 | -0.0026023 | 0.06256 | 0.014098 | 0.060549 | -60.6763 | -0.058115 | -60.7805 | 60.7707 | 60.4101 | 60.4376 | -60.8208 | -60.7859 | 0.036989 | -60.9028 | 60.6122 | 60.6893 | 60.5689 | -60.9434 | 0.093805 | -0.029464 | 0.23828 | 0.13411 | 0.040302 | -0.39006 | -0.36259 | -0.028756 | -0.18796 | 0.12871 | 0.011786 | 0.040542 | -0.11082 | -0.23125 | 121.6853 | 121.3247 | 121.3522 | 60.8565 | -121.621 | 121.5268 | 121.604 | 121.4835 | 60.9516 | -121.7435
339.5469 | 121.9986 | -60.8505 | 60.8368 | 1.4211e-13 | -0.0089338 | 0.0014787 | 0.06315 | -0.0047134 | 0.058687 | -0.014574 | -0.001615 | -0.0030297 | 0.06256 | 0.014098 | 0.060549 | -60.6717 | -0.067272 | -60.7805 | 60.7616 | 60.401 | 60.4422 | -60.8116 | -60.7905 | 0.036989 | -60.9028 | 60.6168 | 60.6848 | 60.5643 | -60.9479 | 0.038876 | -0.075241 | 0.17878 | 0.07002 | 0.031144 | -0.43584 | -0.39463 | -0.097422 | -0.22 | 0.060042 | -0.052301 | 0.045121 | -0.15202 | -0.27244 | 121.6121 | 121.2515 | 121.2927 | 60.7833 | -121.6484 | 121.4673 | 121.5353 | 121.4149 | 60.8875 | -121.7847
341.2812 | 121.9162 | -60.8688 | 60.8368 | 1.4211e-13 | -0.0085064 | 0.0016923 | 0.06315 | -0.004927 | 0.059114 | 0.00068675 | -0.0018288 | -0.0028161 | 0.062774 | 0.014098 | 0.060763 | -60.6717 | -0.062694 | -60.7759 | 60.7661 | 60.4101 | 60.4467 | -60.8254 | -60.7905 | 0.036989 | -60.912 | 60.6168 | 60.6893 | 60.5689 | -60.9479 | 0.043449 | -0.070663 | 0.19709 | 0.092908 | 0.049459 | -0.42668 | -0.39005 | -0.079112 | -0.22 | 0.078352 | -0.043149 | 0.035963 | -0.14745 | -0.26787 | 121.635 | 121.2789 | 121.3156 | 60.8061 | -121.6622 | 121.4856 | 121.5582 | 121.4378 | 60.9058 | -121.7847
342.9375 | 121.8796 | -60.8643 | 60.8963 | 1.4211e-13 | -0.0089338 | 0.0021197 | 0.063363 | -0.0047134 | 0.059328 | 0.00068675 | -0.001615 | -0.0030297 | 0.062774 | 0.014098 | 0.060336 | -60.6809 | -0.071851 | -60.7759 | 60.7707 | 60.4101 | 60.4422 | -60.8254 | -60.7905 | 0.046146 | -60.9028 | 60.6076 | 60.6893 | 60.5643 | -60.9479 | 0.038872 | -0.12559 | 0.18335 | 0.088331 | 0.049459 | -0.48619 | -0.45414 | -0.083689 | -0.28867 | 0.073775 | -0.038568 | 0.045121 | -0.20695 | -0.33195 | 121.635 | 121.2744 | 121.3064 | 60.7924 | -121.7217 | 121.4719 | 121.5536 | 121.4286 | 60.9104 | -121.8442
344.6719 | 121.8567 | -60.8688 | 60.8963 | 1.4211e-13 | -0.00872 | 0.0019059 | 0.062722 | -0.0047134 | 0.058687 | 0.0083173 | -0.001615 | -0.0026023 | 0.06256 | 0.014098 | 0.060122 | -60.6763 | -0.053537 | -60.7713 | 60.7661 | 60.4101 | 60.4422 | -60.8208 | -60.7859 | 0.036989 | -60.8982 | 60.6076 | 60.6893 | 60.5643 | -60.9479 | 0.048028 | -0.13017 | 0.19251 | 0.097486 | 0.049458 | -0.48619 | -0.45414 | -0.079112 | -0.28867 | 0.082931 | -0.029413 | 0.049699 | -0.20695 | -0.33195 | 121.635 | 121.2789 | 121.311 | 60.8153 | -121.7171 | 121.4765 | 121.5582 | 121.4332 | 60.9058 | -121.8442
346.4062 | 121.9574 | -60.8734 | 60.8231 | 1.4211e-13 | -0.0089338 | 0.0014787 | 0.06315 | -0.004927 | 0.058687 | -0.0069437 | -0.0018288 | -0.0028161 | 0.06256 | 0.014312 | 0.060122 | -60.6717 | -0.058115 | -60.7759 | 60.7661 | 60.4147 | 60.4422 | -60.8162 | -60.7905 | 0.041567 | -60.912 | 60.6122 | 60.6802 | 60.5552 | -60.9479 | 0.057185 | -0.05693 | 0.20166 | 0.097486 | 0.040301 | -0.40837 | -0.3809 | -0.074534 | -0.21084 | 0.08293 | -0.038571 | 0.035963 | -0.14287 | -0.26787 | 121.6395 | 121.2881 | 121.3156 | 60.8153 | -121.6393 | 121.4856 | 121.5536 | 121.4286 | 60.915 | -121.771
348.0781 | 121.9208 | -60.9238 | 60.8047 | 1.4211e-13 | -0.0089338 | 0.0014787 | 0.06315 | -0.0047134 | 0.0589 | 0.0083173 | -0.001615 | -0.0028161 | 0.06256 | 0.014098 | 0.060763 | -60.6672 | -0.062694 | -60.7668 | 60.7707 | 60.4055 | 60.4467 | -60.8116 | -60.7859 | 0.036989 | -60.9074 | 60.6122 | 60.6893 | 60.5643 | -60.9479 | 0.11212 | -0.034042 | 0.2566 | 0.157 | 0.044879 | -0.39922 | -0.35801 | -0.02418 | -0.19253 | 0.13786 | 0.016362 | 0.040542 | -0.1154 | -0.2404 | 121.6945 | 121.3293 | 121.3705 | 60.8611 | -121.6164 | 121.536 | 121.6131 | 121.4881 | 60.9608 | -121.7527
349.8281 | 121.8887 | -60.9329 | 60.8002 | 1.4211e-13 | -0.0091474 | 0.0019059 | 0.062936 | -0.0047134 | 0.058687 | -0.0069437 | -0.0020424 | -0.0026023 | 0.06256 | 0.014525 | 0.060549 | -60.6763 | -0.067272 | -60.7713 | 60.7616 | 60.4101 | 60.4376 | -60.8208 | -60.7813 | 0.041567 | -60.9028 | 60.6168 | 60.6939 | 60.5552 | -60.9479 | 0.11211 | -0.03862 | 0.25659 | 0.16157 | 0.049458 | -0.39006 | -0.36259 | -0.015025 | -0.18338 | 0.1516 | 0.030096 | 0.045121 | -0.10625 | -0.24498 | 121.6945 | 121.343 | 121.3705 | 60.8656 | -121.621 | 121.5497 | 121.6268 | 121.4881 | 60.9745 | -121.7481
351.5 | 121.8842 | -60.9192 | 60.7956 | 1.4211e-13 | -0.00872 | 0.0016923 | 0.06315 | -0.0047134 | 0.058687 | 0.0083173 | -0.0018288 | -0.0026023 | 0.06256 | 0.014098 | 0.060763 | -60.6763 | -0.062694 | -60.7759 | 60.7661 | 60.4101 | 60.4422 | -60.8162 | -60.7813 | 0.046146 | -60.8982 | 60.6076 | 60.6848 | 60.5598 | -60.9434 | 0.10296 | -0.029464 | 0.24286 | 0.14326 | 0.040301 | -0.38548 | -0.35343 | -0.024179 | -0.18796 | 0.13786 | 0.020941 | 0.04512 | -0.11082 | -0.23582 | 121.6853 | 121.3293 | 121.3614 | 60.8565 | -121.6118 | 121.5268 | 121.604 | 121.479 | 60.9653 | -121.739
353.2188 | 121.9803 | -60.9055 | 60.759 | 1.4211e-13 | -0.0089338 | 0.0014787 | 0.06315 | -0.0044998 | 0.058687 | 0.00068675 | -0.001615 | -0.0028161 | 0.06256 | 0.014525 | 0.060336 | -60.6763 | -0.058115 | -60.7668 | 60.7707 | 60.4101 | 60.4513 | -60.8071 | -60.7859 | 0.036989 | -60.8982 | 60.6076 | 60.6893 | 60.5598 | -60.9434 | 0.098387 | 0.011735 | 0.22913 | 0.13869 | 0.0403 | -0.34886 | -0.30765 | -0.037911 | -0.15134 | 0.11955 | 0.007209 | 0.04512 | -0.069625 | -0.1992 | 121.6762 | 121.3156 | 121.3568 | 60.8473 | -121.566 | 121.5131 | 121.5948 | 121.4652 | 60.9424 | -121.7023
354.9531 | 121.8567 | -60.8459 | 60.9055 | 1.4211e-13 | -0.0091474 | 0.0014787 | 0.062936 | -0.004927 | 0.0589 | 0.0083173 | -0.0018288 | -0.0026023 | 0.062774 | 0.014525 | 0.060336 | -60.6717 | -0.067272 | -60.7713 | 60.757 | 60.4147 | 60.4422 | -60.8208 | -60.7859 | 0.041567 | -60.9028 | 60.6031 | 60.6848 | 60.5552 | -60.9479 | 0.02514 | -0.14849 | 0.1742 | 0.074598 | 0.049458 | -0.49077 | -0.4633 | -0.102 | -0.3024 | 0.060043 | -0.056879 | 0.045121 | -0.22069 | -0.35027 | 121.6029 | 121.2606 | 121.2881 | 60.7787 | -121.7263 | 121.449 | 121.5307 | 121.4011 | 60.8875 | -121.8534
356.6875 | 121.9437 | -60.8826 | 60.8002 | 1.4211e-13 | -0.0089338 | 0.0016923 | 0.06315 | -0.0047134 | 0.058687 | -0.0069437 | -0.0020424 | -0.0026023 | 0.06256 | 0.014312 | 0.060549 | -60.6717 | -0.058115 | -60.7713 | 60.7616 | 60.4193 | 60.4422 | -60.8162 | -60.7813 | 0.036989 | -60.9028 | 60.6031 | 60.6802 | 60.5598 | -60.9525 | 0.06634 | -0.03862 | 0.21082 | 0.11122 | 0.044879 | -0.3809 | -0.35801 | -0.069958 | -0.19711 | 0.10124 | -0.020258 | 0.0497 | -0.11998 | -0.2404 | 121.6441 | 121.3018 | 121.3247 | 60.8245 | -121.6164 | 121.4856 | 121.5628 | 121.4423 | 60.9196 | -121.7527
358.3594 | 122.0123 | -60.8826 | 60.7864 | 1.4211e-13 | -0.0089338 | 0.0019059 | 0.06315 | -0.0044998 | 0.058473 | 0.0083173 | -0.0018288 | -0.0026023 | 0.062347 | 0.014525 | 0.060549 | -60.6626 | -0.058115 | -60.7668 | 60.7661 | 60.4055 | 60.4422 | -60.8116 | -60.7859 | 0.036989 | -60.9028 | 60.6122 | 60.6893 | 60.5598 | -60.9434 | 0.070919 | -0.020309 | 0.21998 | 0.1158 | 0.044879 | -0.38091 | -0.34428 | -0.0608 | -0.17422 | 0.096664 | -0.020258 | 0.040542 | -0.097091 | -0.22667 | 121.6487 | 121.2881 | 121.3247 | 60.8245 | -121.5981 | 121.4948 | 121.5719 | 121.4423 | 60.9196 | -121.7298
360.1094 | 121.8658 | -60.9283 | 60.8231 | 1.4211e-13 | -0.0091474 | 0.0016923 | 0.06315 | -0.0044998 | 0.0589 | -0.0069437 | -0.001615 | -0.0028161 | 0.06256 | 0.014525 | 0.060763 | -60.6672 | -0.058115 | -60.7713 | 60.7616 | 60.4055 | 60.4422 | -60.8116 | -60.7813 | 0.036989 | -60.9074 | 60.6076 | 60.6848 | 60.5506 | -60.9388 | 0.1167 | -0.061508 | 0.26118 | 0.157 | 0.0403 | -0.41753 | -0.3809 | -0.010444 | -0.21542 | 0.14702 | 0.02094 | 0.031384 | -0.13829 | -0.27245 | 121.6899 | 121.3339 | 121.3705 | 60.8702 | -121.6347 | 121.536 | 121.6131 | 121.479 | 60.9653 | -121.7618
361.8438 | 121.9574 | -60.8597 | 60.8047 | 1.4211e-13 | -0.0091474 | 0.0019059 | 0.062722 | -0.0047134 | 0.058473 | 0.0083173 | -0.0018288 | -0.0028161 | 0.06256 | 0.014098 | 0.060763 | -60.6626 | -0.062694 | -60.7713 | 60.757 | 60.4147 | 60.4467 | -60.8116 | -60.7813 | 0.041567 | -60.8982 | 60.6076 | 60.6848 | 60.5643 | -60.9434 | 0.048031 | -0.047777 | 0.19709 | 0.088331 | 0.0403 | -0.39006 | -0.35801 | -0.083688 | -0.19711 | 0.078354 | -0.038568 | 0.04512 | -0.11998 | -0.2404 | 121.6167 | 121.2744 | 121.3064 | 60.797 | -121.6164 | 121.4673 | 121.5444 | 121.424 | 60.9012 | -121.7481
363.5938 | 121.8613 | -60.9192 | 60.8414 | 1.4211e-13 | -0.0091474 | 0.0016923 | 0.063363 | -0.004927 | 0.0589 | 0.0083173 | -0.0018288 | -0.0030297 | 0.062774 | 0.014312 | 0.060336 | -60.6717 | -0.058115 | -60.7622 | 60.7661 | 60.4101 | 60.4467 | -60.8116 | -60.7859 | 0.041567 | -60.8982 | 60.6076 | 60.6893 | 60.5552 | -60.9434 | 0.10754 | -0.075241 | 0.24744 | 0.157 | 0.049457 | -0.43126 | -0.39463 | -0.024179 | -0.23373 | 0.13329 | 0.020941 | 0.04512 | -0.15202 | -0.28618 | 121.6853 | 121.3293 | 121.3659 | 60.8611 | -121.653 | 121.5268 | 121.6085 | 121.4744 | 60.9608 | -121.7847
365.2656 | 121.9162 | -60.8734 | 60.8597 | 1.4211e-13 | -0.0089338 | 0.0019059 | 0.06315 | -0.0042862 | 0.059114 | 0.00068675 | -0.001615 | -0.0028161 | 0.06256 | 0.014525 | 0.060549 | -60.6717 | -0.067272 | -60.7713 | 60.7661 | 60.4101 | 60.4422 | -60.8162 | -60.7767 | 0.041567 | -60.8982 | 60.6076 | 60.6848 | 60.5598 | -60.9434 | 0.057185 | -0.093551 | 0.20166 | 0.10206 | 0.044879 | -0.44957 | -0.41752 | -0.069955 | -0.25204 | 0.096666 | -0.024835 | 0.04512 | -0.17491 | -0.29991 | 121.6395 | 121.2835 | 121.3156 | 60.8061 | -121.6759 | 121.481 | 121.5582 | 121.4332 | 60.915 | -121.803
367 | 121.9849 | -60.8826 | 60.759 | 1.4211e-13 | -0.009361 | 0.0019059 | 0.06315 | -0.0051408 | 0.058259 | 0.00068675 | -0.0014014 | -0.0026023 | 0.06256 | 0.014525 | 0.060122 | -60.6626 | -0.062694 | -60.7668 | 60.7661 | 60.4055 | 60.4422 | -60.8116 | -60.7767 | 0.041567 | -60.8937 | 60.6076 | 60.6848 | 60.5506 | -60.9479 | 0.070919 | 0.007157 | 0.21998 | 0.1158 | 0.044879 | -0.35344 | -0.31681 | -0.065379 | -0.15134 | 0.10582 | -0.011101 | 0.054278 | -0.074204 | -0.20836 | 121.6487 | 121.2881 | 121.3247 | 60.8199 | -121.5706 | 121.4902 | 121.5673 | 121.4332 | 60.9241 | -121.7069
368.7344 | 121.9574 | -60.8963 | 60.791 | 1.4211e-13 | -0.0091474 | 0.0021197 | 0.06315 | -0.004927 | 0.058687 | 0.00068675 | -0.001615 | -0.0028161 | 0.06256 | 0.014312 | 0.060549 | -60.6626 | -0.062694 | -60.7713 | 60.7661 | 60.401 | 60.4376 | -60.8116 | -60.7813 | 0.050725 | -60.8937 | 60.6076 | 60.6893 | 60.5552 | -60.9479 | 0.084652 | -0.024887 | 0.23371 | 0.12495 | 0.0403 | -0.39006 | -0.35343 | -0.051646 | -0.18338 | 0.11498 | 0.002632 | 0.054278 | -0.10167 | -0.23583 | 121.6624 | 121.2973 | 121.3339 | 60.8336 | -121.6027 | 121.5039 | 121.5856 | 121.4515 | 60.947 | -121.739
370.4062 | 121.8613 | -60.9283 | 60.8231 | 1.4211e-13 | -0.0091474 | 0.0016923 | 0.06315 | -0.004927 | 0.058473 | 0.00068675 | -0.001615 | -0.0032433 | 0.062347 | 0.014739 | 0.060763 | -60.6626 | -0.053537 | -60.7713 | 60.7616 | 60.4101 | 60.4422 | -60.8071 | -60.7813 | 0.041567 | -60.8937 | 60.6122 | 60.6893 | 60.5552 | -60.9479 | 0.12127 | -0.061508 | 0.26575 | 0.157 | 0.035721 | -0.41295 | -0.3809 | -0.019602 | -0.21084 | 0.14702 | 0.034676 | 0.054278 | -0.13371 | -0.26787 | 121.6899 | 121.3385 | 121.3705 | 60.8748 | -121.6301 | 121.5406 | 121.6177 | 121.4835 | 60.9699 | -121.771
372.1406 | 121.9757 | -60.8322 | 60.8185 | 1.4211e-13 | -0.009361 | 0.0016923 | 0.063363 | -0.004927 | 0.058473 | -0.0069437 | -0.001615 | -0.0028161 | 0.06256 | 0.014525 | 0.060549 | -60.6672 | -0.062694 | -60.7668 | 60.7616 | 60.401 | 60.4422 | -60.8071 | -60.7859 | 0.027831 | -60.9074 | 60.6031 | 60.6802 | 60.5552 | -60.9434 | 0.025144 | -0.05693 | 0.16504 | 0.065444 | 0.0403 | -0.41753 | -0.37632 | -0.11115 | -0.21542 | 0.04631 | -0.075191 | 0.035963 | -0.13829 | -0.26329 | 121.5938 | 121.2332 | 121.2744 | 60.7695 | -121.6256 | 121.4353 | 121.5124 | 121.3874 | 60.86 | -121.7618
373.875 | 121.9803 | -60.8322 | 60.8368 | 1.4211e-13 | -0.009361 | 0.0019059 | 0.06315 | -0.0044998 | 0.058473 | -0.0069437 | -0.0018288 | -0.0023887 | 0.06256 | 0.014525 | 0.060336 | -60.658 | -0.058115 | -60.7622 | 60.757 | 60.3964 | 60.4376 | -60.8116 | -60.7813 | 0.041567 | -60.9028 | 60.6031 | 60.6802 | 60.5506 | -60.9525 | 0.020565 | -0.07982 | 0.1742 | 0.070022 | 0.049457 | -0.44042 | -0.39921 | -0.12031 | -0.23374 | 0.050888 | -0.070612 | 0.0497 | -0.1566 | -0.28618 | 121.5892 | 121.2286 | 121.2698 | 60.7741 | -121.6484 | 121.4353 | 121.5124 | 121.3828 | 60.8738 | -121.7893
375.5469 | 121.9849 | -60.9009 | 60.7773 | 1.4211e-13 | -0.0091474 | 0.0016923 | 0.062936 | -0.0047134 | 0.058473 | -0.0069437 | -0.0018288 | -0.0026023 | 0.06256 | 0.01538 | 0.060122 | -60.6626 | -0.058115 | -60.7622 | 60.757 | 60.401 | 60.4422 | -60.8162 | -60.7813 | 0.041567 | -60.9028 | 60.6031 | 60.6893 | 60.5552 | -60.9525 | 0.084651 | -0.020311 | 0.23829 | 0.13869 | 0.054036 | -0.37633 | -0.33512 | -0.051647 | -0.17423 | 0.11955 | -0.001947 | 0.0497 | -0.087936 | -0.22209 | 121.6579 | 121.3018 | 121.343 | 60.8428 | -121.5935 | 121.5039 | 121.5902 | 121.4561 | 60.9424 | -121.7298
377.2812 | 122.0032 | -60.9009 | 60.7407 | 1.4211e-13 | -0.009361 | 0.0019059 | 0.062936 | -0.004927 | 0.058259 | 0.00068675 | -0.001615 | -0.0026023 | 0.062347 | 0.014953 | 0.060336 | -60.658 | -0.058115 | -60.7668 | 60.7616 | 60.4101 | 60.4422 | -60.8116 | -60.7767 | 0.036989 | -60.8982 | 60.6031 | 60.6848 | 60.546 | -60.9479 | 0.08923 | 0.020889 | 0.24287 | 0.13411 | 0.044879 | -0.33055 | -0.2985 | -0.047068 | -0.13761 | 0.12413 | 0.002631 | 0.049699 | -0.055894 | -0.19463 | 121.6624 | 121.311 | 121.343 | 60.8428 | -121.5523 | 121.5039 | 121.5856 | 121.4469 | 60.9379 | -121.6886
379.0156 | 121.8384 | -60.9192 | 60.8139 | 1.4211e-13 | -0.009361 | 0.0014787 | 0.063363 | -0.0047134 | 0.058687 | 0.00068675 | -0.0020424 | -0.0028161 | 0.06256 | 0.014525 | 0.060122 | -60.6626 | -0.058115 | -60.7713 | 60.7707 | 60.4055 | 60.4467 | -60.8116 | -60.7813 | 0.03241 | -60.8937 | 60.5985 | 60.6756 | 60.5689 | -60.9479 | 0.10754 | -0.043197 | 0.2566 | 0.14784 | 0.0403 | -0.40837 | -0.36716 | -0.028758 | -0.21543 | 0.13786 | 0.02552 | 0.054278 | -0.13829 | -0.24498 | 121.6899 | 121.3247 | 121.3659 | 60.8611 | -121.6256 | 121.5177 | 121.5948 | 121.4881 | 60.9516 | -121.7619
380.75 | 121.8475 | -60.9238 | 60.8276 | 1.4211e-13 | -0.0095748 | 0.0016923 | 0.06315 | -0.0047134 | 0.0589 | -0.0069437 | -0.001615 | -0.0026023 | 0.062988 | 0.014525 | 0.060336 | -60.6534 | -0.048958 | -60.7668 | 60.7616 | 60.4101 | 60.4422 | -60.8071 | -60.7767 | 0.041567 | -60.8937 | 60.5985 | 60.6848 | 60.5506 | -60.9434 | 0.1167 | -0.066086 | 0.27033 | 0.157 | 0.0403 | -0.41753 | -0.38548 | -0.019601 | -0.22916 | 0.14702 | 0.030098 | 0.049699 | -0.14287 | -0.27703 | 121.6853 | 121.3339 | 121.3659 | 60.8748 | -121.6347 | 121.5222 | 121.6085 | 121.4744 | 60.9653 | -121.771
382.4062 | 121.8613 | -60.8459 | 60.9009 | 1.4211e-13 | -0.0097884 | 0.0016923 | 0.063363 | -0.0047134 | 0.058259 | -0.0069437 | -0.0018288 | -0.0028161 | 0.062988 | 0.014739 | 0.060122 | -60.658 | -0.058115 | -60.7576 | 60.7524 | 60.4055 | 60.4467 | -60.8071 | -60.7813 | 0.03241 | -60.8982 | 60.5985 | 60.6802 | 60.5643 | -60.9434 | 0.038877 | -0.14849 | 0.18793 | 0.088333 | 0.049456 | -0.49535 | -0.45414 | -0.097421 | -0.3024 | 0.064621 | -0.052301 | 0.04512 | -0.22069 | -0.33653 | 121.5983 | 121.2515 | 121.2927 | 60.7878 | -121.7079 | 121.4444 | 121.5261 | 121.4103 | 60.8784 | -121.8442
384.1562 | 121.8658 | -60.8688 | 60.8688 | 1.4211e-13 | -0.009361 | 0.0014787 | 0.062936 | -0.0047134 | 0.058687 | 0.0083173 | -0.001615 | -0.0028161 | 0.06256 | 0.014525 | 0.060122 | -60.6534 | -0.058115 | -60.7668 | 60.7661 | 60.4055 | 60.4467 | -60.8071 | -60.7767 | 0.041567 | -60.8982 | 60.5985 | 60.6802 | 60.5598 | -60.9388 | 0.061765 | -0.10271 | 0.2154 | 0.10206 | 0.0403 | -0.4633 | -0.42209 | -0.069954 | -0.27036 | 0.092088 | -0.029413 | 0.040541 | -0.18864 | -0.30907 | 121.635 | 121.2744 | 121.3156 | 60.8107 | -121.6759 | 121.4673 | 121.549 | 121.4286 | 60.9104 | -121.8076
385.9062 | 121.843 | -60.8368 | 60.8917 | 1.4211e-13 | -0.009361 | 0.0016923 | 0.063363 | -0.0044998 | 0.058473 | 0.00068675 | -0.001615 | -0.0026023 | 0.06256 | 0.014953 | 0.059908 | -60.658 | -0.062694 | -60.7622 | 60.7616 | 60.4055 | 60.4422 | -60.8071 | -60.7767 | 0.03241 | -60.8982 | 60.5939 | 60.6756 | 60.546 | -60.9434 | 0.029722 | -0.13017 | 0.17878 | 0.0746 | 0.044878 | -0.48619 | -0.44956 | -0.10658 | -0.29782 | 0.060045 | -0.061456 | 0.04512 | -0.21611 | -0.34569 | 121.5983 | 121.2423 | 121.279 | 60.7741 | -121.6988 | 121.4307 | 121.5124 | 121.3828 | 60.8692 | -121.8351
387.5781 | 121.8475 | -60.8551 | 60.9055 | 1.4211e-13 | -0.0095748 | 0.0021197 | 0.062936 | -0.0047134 | 0.058259 | 0.0083173 | -0.001615 | -0.0026023 | 0.06256 | 0.014739 | 0.060122 | -60.658 | -0.053537 | -60.7668 | 60.757 | 60.401 | 60.4422 | -60.8025 | -60.7813 | 0.036989 | -60.8937 | 60.6076 | 60.6848 | 60.546 | -60.9434 | 0.052612 | -0.14849 | 0.19709 | 0.088333 | 0.035721 | -0.5045 | -0.4633 | -0.088265 | -0.29782 | 0.073777 | -0.038566 | 0.049699 | -0.22069 | -0.35942 | 121.6121 | 121.2561 | 121.2973 | 60.8016 | -121.7079 | 121.4627 | 121.5399 | 121.4011 | 60.8921 | -121.8488
389.2969 | 121.8613 | -60.91 | 60.8093 | 1.4211e-13 | -0.010216 | 0.0014787 | 0.062936 | -0.004927 | 0.058473 | 0.00068675 | -0.001615 | -0.0026023 | 0.062774 | 0.014525 | 0.060122 | -60.6534 | -0.058115 | -60.7668 | 60.757 | 60.4055 | 60.4422 | -60.8071 | -60.7722 | 0.041567 | -60.8937 | 60.5985 | 60.6756 | 60.5598 | -60.9434 | 0.10296 | -0.052354 | 0.2566 | 0.14326 | 0.0403 | -0.40379 | -0.36716 | -0.033334 | -0.21085 | 0.13787 | 0.016365 | 0.049699 | -0.13371 | -0.24956 | 121.667 | 121.3156 | 121.3522 | 60.8519 | -121.6164 | 121.5085 | 121.5856 | 121.4698 | 60.9516 | -121.7527
391.0312 | 121.8475 | -60.91 | 60.8368 | 1.4211e-13 | -0.0097884 | 0.0016923 | 0.06315 | -0.004927 | 0.058687 | -0.0069437 | -0.0018288 | -0.0026023 | 0.062347 | 0.014953 | 0.060122 | -60.6534 | -0.053537 | -60.7622 | 60.757 | 60.4055 | 60.4376 | -60.8116 | -60.7767 | 0.036989 | -60.8982 | 60.6031 | 60.6756 | 60.5506 | -60.9388 | 0.098385 | -0.07982 | 0.2566 | 0.14784 | 0.049457 | -0.43126 | -0.39921 | -0.028755 | -0.23374 | 0.13329 | 0.011786 | 0.040541 | -0.16118 | -0.28618 | 121.667 | 121.3156 | 121.3476 | 60.8565 | -121.6484 | 121.5131 | 121.5856 | 121.4606 | 60.947 | -121.7756
392.7656 | 121.875 | -60.9009 | 60.7773 | 1.4211e-13 | -0.0097884 | 0.0016923 | 0.06315 | -0.004927 | 0.058687 | -0.0069437 | -0.002256 | -0.0026023 | 0.062347 | 0.014739 | 0.060122 | -60.6489 | -0.048958 | -60.7668 | 60.757 | 60.4101 | 60.4422 | -60.7979 | -60.7676 | 0.036989 | -60.8845 | 60.5985 | 60.6893 | 60.5552 | -60.9388 | 0.10297 | -0.020311 | 0.25202 | 0.13411 | 0.031142 | -0.36717 | -0.33512 | -0.03791 | -0.1788 | 0.13329 | 0.016367 | 0.054277 | -0.087936 | -0.22209 | 121.6579 | 121.311 | 121.343 | 60.8519 | -121.5752 | 121.4994 | 121.5902 | 121.4561 | 60.9379 | -121.7161
394.4375 | 121.9254 | -60.8231 | 60.8276 | 1.4211e-13 | -0.010216 | 0.0014787 | 0.062936 | -0.004927 | 0.058687 | 0.00068675 | -0.001615 | -0.0026023 | 0.062347 | 0.014739 | 0.060336 | -60.6534 | -0.058115 | -60.7622 | 60.757 | 60.401 | 60.4422 | -60.8071 | -60.7722 | 0.046146 | -60.8937 | 60.6031 | 60.6848 | 60.546 | -60.9479 | 0.015989 | -0.070665 | 0.16962 | 0.060867 | 0.044878 | -0.42668 | -0.38548 | -0.12489 | -0.22458 | 0.050891 | -0.07061 | 0.054278 | -0.14287 | -0.2816 | 121.58 | 121.224 | 121.2652 | 60.7649 | -121.6347 | 121.4261 | 121.5078 | 121.3691 | 60.8692 | -121.7756
396.1875 | 121.9025 | -60.8734 | 60.8688 | 1.4211e-13 | -0.0097884 | 0.0023333 | 0.06315 | -0.004927 | 0.058473 | -0.0069437 | -0.0018288 | -0.0028161 | 0.06256 | 0.014953 | 0.060122 | -60.658 | -0.053537 | -60.7622 | 60.7524 | 60.4055 | 60.4422 | -60.8116 | -60.7676 | 0.041567 | -60.8891 | 60.5985 | 60.6848 | 60.5598 | -60.9388 | 0.061764 | -0.11644 | 0.2154 | 0.11122 | 0.049457 | -0.4633 | -0.42667 | -0.065376 | -0.27036 | 0.10582 | -0.015677 | 0.049699 | -0.18407 | -0.30907 | 121.6258 | 121.2789 | 121.3156 | 60.8199 | -121.6805 | 121.4719 | 121.5582 | 121.4332 | 60.915 | -121.8076
397.9375 | 121.8613 | -60.8459 | 60.9055 | 1.4211e-13 | -0.010002 | 0.0019059 | 0.062936 | -0.004927 | 0.058473 | 0.0083173 | -0.001615 | -0.0026023 | 0.062347 | 0.014739 | 0.059908 | -60.6534 | -0.048958 | -60.7668 | 60.7524 | 60.4055 | 60.4467 | -60.8025 | -60.7722 | 0.036989 | -60.8937 | 60.6031 | 60.6756 | 60.5506 | -60.9434 | 0.043456 | -0.15306 | 0.19251 | 0.079177 | 0.035721 | -0.49992 | -0.45872 | -0.097421 | -0.3024 | 0.073779 | -0.047722 | 0.049699 | -0.22985 | -0.35484 | 121.5983 | 121.2515 | 121.2927 | 60.797 | -121.7079 | 121.449 | 121.5216 | 121.3966 | 60.8829 | -121.8488
399.625 | 121.843 | -60.91 | 60.8139 | 1.4211e-13 | -0.0095748 | 0.0016923 | 0.06315 | -0.0051408 | 0.058687 | 0.0083173 | -0.001615 | -0.0028161 | 0.062347 | 0.014953 | 0.059908 | -60.6489 | -0.058115 | -60.7576 | 60.7524 | 60.4055 | 60.4467 | -60.8071 | -60.7767 | 0.041567 | -60.8845 | 60.6031 | 60.6848 | 60.5506 | -60.9434 | 0.10296 | -0.06151 | 0.26118 | 0.15242 | 0.049456 | -0.40837 | -0.36716 | -0.033334 | -0.21085 | 0.13329 | 0.025522 | 0.058856 | -0.12914 | -0.26329 | 121.6624 | 121.3156 | 121.3568 | 60.8519 | -121.621 | 121.5131 | 121.5948 | 121.4606 | 60.9516 | -121.7573
401.3594 | 121.9482 | -60.8414 | 60.7864 | 1.4211e-13 | -0.010216 | 0.0019059 | 0.062936 | -0.0047134 | 0.058473 | 0.015947 | -0.0018288 | -0.0026023 | 0.062133 | 0.014953 | 0.060122 | -60.6534 | -0.048958 | -60.7576 | 60.757 | 60.401 | 60.4467 | -60.8071 | -60.7676 | 0.041567 | -60.8937 | 60.5985 | 60.6756 | 60.5506 | -60.9434 | 0.0343 | -0.029466 | 0.18793 | 0.083756 | 0.049456 | -0.38548 | -0.3397 | -0.102 | -0.18796 | 0.07378 | -0.052299 | 0.049699 | -0.11083 | -0.23583 | 121.5983 | 121.2423 | 121.2881 | 60.7924 | -121.5935 | 121.4398 | 121.517 | 121.392 | 60.8829 | -121.7298
403.0938 | 121.8292 | -60.8597 | 60.9009 | 1.4211e-13 | -0.010216 | 0.0016923 | 0.062722 | -0.004927 | 0.058473 | 0.00068675 | -0.0018288 | -0.0030297 | 0.06256 | 0.014953 | 0.060122 | -60.6489 | -0.062694 | -60.7622 | 60.7616 | 60.4055 | 60.4376 | -60.8071 | -60.7676 | 0.036989 | -60.8937 | 60.5939 | 60.6756 | 60.5552 | -60.9388 | 0.05261 | -0.13933 | 0.21082 | 0.097488 | 0.044878 | -0.49535 | -0.4633 | -0.079109 | -0.30698 | 0.09209 | -0.033989 | 0.04512 | -0.22527 | -0.34569 | 121.6212 | 121.2652 | 121.2973 | 60.797 | -121.7079 | 121.4536 | 121.5353 | 121.4149 | 60.8967 | -121.8397
404.8281 | 121.8475 | -60.8505 | 60.8963 | 1.4211e-13 | -0.0097884 | 0.0016923 | 0.062936 | -0.004927 | 0.058473 | 0.00068675 | -0.0018288 | -0.0026023 | 0.062347 | 0.015166 | 0.059908 | -60.6489 | -0.048958 | -60.7622 | 60.7524 | 60.4055 | 60.4422 | -60.8025 | -60.7722 | 0.041567 | -60.8845 | 60.5939 | 60.671 | 60.5506 | -60.9434 | 0.048034 | -0.14391 | 0.20167 | 0.088333 | 0.040299 | -0.49077 | -0.45414 | -0.092843 | -0.3024 | 0.078357 | -0.033987 | 0.058856 | -0.22527 | -0.34569 | 121.6029 | 121.2561 | 121.2927 | 60.8016 | -121.6988 | 121.4444 | 121.5216 | 121.4011 | 60.8921 | -121.8397
406.5 | 121.9208 | -60.8047 | 60.8597 | 1.4211e-13 | -0.010216 | 0.0016923 | 0.062936 | -0.0047134 | 0.058473 | -0.0069437 | -0.0020424 | -0.0028161 | 0.062133 | 0.015166 | 0.060122 | -60.6397 | -0.053537 | -60.7668 | 60.7524 | 60.4055 | 60.4467 | -60.8071 | -60.7767 | 0.036989 | -60.8845 | 60.5985 | 60.6756 | 60.5506 | -60.9434 | -0.002321 | -0.10729 | 0.16505 | 0.037979 | 0.0403 | -0.45415 | -0.41294 | -0.13862 | -0.2612 | 0.028002 | -0.079763 | 0.058856 | -0.18407 | -0.30907 | 121.5571 | 121.2103 | 121.2515 | 60.7512 | -121.6668 | 121.4032 | 121.4804 | 121.3554 | 60.8417 | -121.803
408.2344 | 121.9803 | -60.8917 | 60.7452 | 1.4211e-13 | -0.010002 | 0.0012649 | 0.062936 | -0.0053544 | 0.058473 | 0.00068675 | -0.0018288 | -0.0028161 | 0.062133 | 0.01538 | 0.060122 | -60.6489 | -0.039801 | -60.7576 | 60.7524 | 60.401 | 60.433 | -60.8071 | -60.7722 | 0.036989 | -60.8845 | 60.5939 | 60.6802 | 60.546 | -60.9342 | 0.084654 | 0.007155 | 0.24287 | 0.13411 | 0.049456 | -0.34429 | -0.31224 | -0.042487 | -0.15134 | 0.11956 | 0.007212 | 0.049699 | -0.065049 | -0.19921 | 121.6441 | 121.2927 | 121.3247 | 60.8519 | -121.5523 | 121.4856 | 121.5719 | 121.4378 | 60.9287 | -121.6795
409.9688 | 121.962 | -60.8047 | 60.8368 | 1.4211e-13 | -0.010429 | 0.0016923 | 0.062722 | -0.0051408 | 0.058473 | 0.0083173 | -0.0018288 | -0.0028161 | 0.06256 | 0.014739 | 0.060336 | -60.6489 | -0.044379 | -60.7668 | 60.757 | 60.401 | 60.433 | -60.7979 | -60.7722 | 0.036989 | -60.8891 | 60.5939 | 60.6756 | 60.5506 | -60.9388 | 0.006837 | -0.07982 | 0.15589 | 0.037979 | 0.031142 | -0.43584 | -0.40379 | -0.13404 | -0.24289 | 0.032581 | -0.084341 | 0.049699 | -0.16118 | -0.28618 | 121.5617 | 121.2057 | 121.2378 | 60.7604 | -121.6347 | 121.3986 | 121.4804 | 121.3554 | 60.8417 | -121.7756
411.7031 | 121.9437 | -60.8734 | 60.759 | 1.4211e-13 | -0.010216 | 0.0016923 | 0.062936 | -0.0051408 | 0.058259 | 0.0083173 | -0.001615 | -0.0028161 | 0.062347 | 0.015166 | 0.060122 | -60.6443 | -0.048958 | -60.7622 | 60.7478 | 60.3872 | 60.4422 | -60.8025 | -60.7722 | 0.041567 | -60.8799 | 60.6031 | 60.6802 | 60.546 | -60.9342 | 0.070922 | -0.011156 | 0.22913 | 0.11122 | 0.040299 | -0.37176 | -0.31681 | -0.060798 | -0.15592 | 0.10124 | -0.00652 | 0.054278 | -0.078782 | -0.21294 | 121.6212 | 121.2606 | 121.3156 | 60.8245 | -121.5615 | 121.4765 | 121.5536 | 121.4194 | 60.915 | -121.6932
413.375 | 121.843 | -60.9238 | 60.8139 | 1.4211e-13 | -0.010429 | 0.0016923 | 0.06315 | -0.004927 | 0.058687 | 0.00068675 | -0.0018288 | -0.0028161 | 0.062347 | 0.014739 | 0.059695 | -60.6443 | -0.058115 | -60.7576 | 60.7524 | 60.4055 | 60.4422 | -60.8071 | -60.763 | 0.050725 | -60.8891 | 60.5985 | 60.6802 | 60.546 | -60.9342 | 0.1167 | -0.06151 | 0.27949 | 0.16615 | 0.049456 | -0.40837 | -0.37174 | -0.010444 | -0.21543 | 0.16076 | 0.034677 | 0.045121 | -0.13371 | -0.26787 | 121.6762 | 121.3293 | 121.3659 | 60.8657 | -121.621 | 121.5222 | 121.604 | 121.4698 | 60.9745 | -121.7481
415.125 | 121.8658 | -60.8505 | 60.8871 | 1.4211e-13 | -0.010002 | 0.0019059 | 0.062722 | -0.004927 | 0.058473 | 0.0083173 | -0.0018288 | -0.0028161 | 0.062133 | 0.015166 | 0.059908 | -60.6489 | -0.053537 | -60.7576 | 60.7524 | 60.4055 | 60.4376 | -60.7979 | -60.7722 | 0.041567 | -60.8754 | 60.5893 | 60.6848 | 60.5552 | -60.9388 | 0.052613 | -0.13475 | 0.20167 | 0.092911 | 0.040298 | -0.48161 | -0.44956 | -0.088264 | -0.29782 | 0.078357 | -0.024829 | 0.063435 | -0.20238 | -0.33196 | 121.6029 | 121.2561 | 121.2881 | 60.797 | -121.6851 | 121.4398 | 121.5353 | 121.4057 | 60.8921 | -121.8259
416.8594 | 121.9528 | -60.8414 | 60.8093 | 1.4211e-13 | -0.010216 | 0.0014787 | 0.062936 | -0.0047134 | 0.058473 | 0.0083173 | -0.0018288 | -0.0032433 | 0.06256 | 0.015166 | 0.059695 | -60.6397 | -0.048958 | -60.753 | 60.7524 | 60.401 | 60.4422 | -60.8025 | -60.7722 | 0.046146 | -60.8845 | 60.5893 | 60.671 | 60.5506 | -60.9434 | 0.038879 | -0.056932 | 0.20167 | 0.088334 | 0.049455 | -0.40837 | -0.36716 | -0.102 | -0.22 | 0.069202 | -0.043142 | 0.058856 | -0.13829 | -0.25871 | 121.5938 | 121.2423 | 121.2835 | 60.7924 | -121.6118 | 121.4307 | 121.5124 | 121.392 | 60.8875 | -121.7527
418.5312 | 121.9803 | -60.8185 | 60.8414 | 1.4211e-13 | -0.010002 | 0.0016923 | 0.062936 | -0.004927 | 0.058687 | -0.0069437 | -0.0018288 | -0.0026023 | 0.062347 | 0.014953 | 0.059695 | -60.6489 | -0.053537 | -60.7576 | 60.7432 | 60.401 | 60.433 | -60.8025 | -60.7676 | 0.046146 | -60.8845 | 60.5939 | 60.6802 | 60.5415 | -60.9434 | 0.01599 | -0.098133 | 0.16962 | 0.060867 | 0.044877 | -0.44042 | -0.40837 | -0.12489 | -0.24747 | 0.050891 | -0.066031 | 0.058856 | -0.16118 | -0.29991 | 121.5617 | 121.2194 | 121.2515 | 60.7649 | -121.6439 | 121.4124 | 121.4987 | 121.3599 | 60.8646 | -121.7847
420.2656 | 121.9528 | -60.8322 | 60.8368 | 1.4211e-13 | -0.010002 | 0.0016923 | 0.062936 | -0.0051408 | 0.058259 | -0.0069437 | -0.0018288 | -0.0028161 | 0.062347 | 0.01538 | 0.059695 | -60.6489 | -0.053537 | -60.7668 | 60.7432 | 60.3964 | 60.4422 | -60.7979 | -60.763 | 0.041567 | -60.8891 | 60.5893 | 60.6802 | 60.5369 | -60.9434 | 0.034302 | -0.093555 | 0.18336 | 0.065444 | 0.031142 | -0.44042 | -0.39463 | -0.11115 | -0.24747 | 0.069203 | -0.056876 | 0.054278 | -0.1566 | -0.29992 | 121.5755 | 121.2286 | 121.2744 | 60.7787 | -121.6347 | 121.4215 | 121.5124 | 121.3691 | 60.8738 | -121.7802
421.9531 | 121.843 | -60.9009 | 60.8047 | 1.4211e-13 | -0.010429 | 0.0016923 | 0.062722 | -0.005568 | 0.058046 | 0.00068675 | -0.0018288 | -0.0026023 | 0.062347 | 0.014953 | 0.059695 | -60.6489 | -0.048958 | -60.7622 | 60.757 | 60.3964 | 60.433 | -60.8025 | -60.7676 | 0.041567 | -60.8845 | 60.5893 | 60.6848 | 60.546 | -60.9342 | 0.098388 | -0.047777 | 0.25202 | 0.13869 | 0.040299 | -0.40837 | -0.37175 | -0.033332 | -0.21543 | 0.13329 | 0.016367 | 0.049699 | -0.11998 | -0.25872 | 121.6579 | 121.2973 | 121.3339 | 60.8519 | -121.6072 | 121.4902 | 121.5856 | 121.4469 | 60.9424 | -121.739
423.6875 | 121.9208 | -60.8734 | 60.7681 | 1.4211e-13 | -0.010216 | 0.0012649 | 0.062722 | -0.0051408 | 0.058473 | 0.00068675 | -0.0018288 | -0.0030297 | 0.062347 | 0.01538 | 0.059695 | -60.6397 | -0.053537 | -60.7576 | 60.7432 | 60.3964 | 60.4376 | -60.7979 | -60.763 | 0.041567 | -60.8845 | 60.5893 | 60.6756 | 60.546 | -60.9342 | 0.075501 | -0.02489 | 0.23371 | 0.1158 | 0.040298 | -0.37175 | -0.33054 | -0.060798 | -0.1788 | 0.1104 | -0.011099 | 0.049699 | -0.092516 | -0.22209 | 121.6166 | 121.2698 | 121.311 | 60.8199 | -121.566 | 121.4627 | 121.549 | 121.4194 | 60.915 | -121.7023
425.4219 | 121.8475 | -60.9009 | 60.8276 | 1.4211e-13 | -0.010002 | 0.0016923 | 0.062936 | -0.0047134 | 0.058046 | 0.00068675 | -0.0018288 | -0.0026023 | 0.06256 | 0.01538 | 0.059908 | -60.6397 | -0.048958 | -60.7576 | 60.7478 | 60.401 | 60.4422 | -60.8025 | -60.763 | 0.046146 | -60.8799 | 60.5939 | 60.6756 | 60.5598 | -60.9434 | 0.098388 | -0.079821 | 0.26118 | 0.14327 | 0.044877 | -0.42668 | -0.38548 | -0.042489 | -0.23374 | 0.13787 | 0.020946 | 0.063435 | -0.15203 | -0.26787 | 121.6487 | 121.3018 | 121.343 | 60.8519 | -121.6301 | 121.4948 | 121.5765 | 121.4606 | 60.947 | -121.771
427.1406 | 121.9528 | -60.8826 | 60.759 | 1.4211e-13 | -0.010429 | 0.0019059 | 0.062936 | -0.004927 | 0.058473 | 0.00068675 | -0.0018288 | -0.0026023 | 0.062774 | 0.015594 | 0.059908 | -60.6443 | -0.053537 | -60.7576 | 60.7432 | 60.3918 | 60.4376 | -60.7979 | -60.763 | 0.036989 | -60.8799 | 60.5939 | 60.6802 | 60.5415 | -60.9434 | 0.084656 | -0.015735 | 0.23829 | 0.12495 | 0.040298 | -0.36718 | -0.32139 | -0.0608 | -0.16507 | 0.11956 | 0.002635 | 0.063435 | -0.078782 | -0.21752 | 121.6258 | 121.2744 | 121.3202 | 60.829 | -121.5569 | 121.4765 | 121.5628 | 121.424 | 60.9196 | -121.7023
428.875 | 121.9299 | -60.7956 | 60.8597 | 1.4211e-13 | -0.010429 | 0.0014787 | 0.06315 | -0.0047134 | 0.058046 | -0.014574 | -0.001615 | -0.0026023 | 0.062347 | 0.015166 | 0.060122 | -60.6397 | -0.062694 | -60.7576 | 60.7478 | 60.401 | 60.4284 | -60.8025 | -60.7676 | 0.046146 | -60.8845 | 60.5985 | 60.6756 | 60.5552 | -60.9434 | -0.006898 | -0.11186 | 0.15589 | 0.037979 | 0.044877 | -0.45873 | -0.43126 | -0.14778 | -0.2612 | 0.028003 | -0.088919 | 0.058856 | -0.18407 | -0.30449 | 121.5434 | 121.1965 | 121.224 | 60.7329 | -121.6622 | 121.3941 | 121.4712 | 121.3508 | 60.8417 | -121.803
430.5625 | 121.8521 | -60.91 | 60.8093 | 1.4211e-13 | -0.010857 | 0.0019059 | 0.062722 | -0.004927 | 0.058259 | 0.00068675 | -0.001615 | -0.0028161 | 0.06256 | 0.01538 | 0.059908 | -60.6443 | -0.058115 | -60.7576 | 60.7524 | 60.4055 | 60.4376 | -60.8071 | -60.7676 | 0.046146 | -60.8754 | 60.5939 | 60.6802 | 60.5415 | -60.9434 | 0.10296 | -0.056932 | 0.26576 | 0.15242 | 0.049456 | -0.40379 | -0.37174 | -0.033334 | -0.21543 | 0.14244 | 0.03468 | 0.068014 | -0.12914 | -0.26787 | 121.6624 | 121.3156 | 121.3476 | 60.8519 | -121.6164 | 121.5039 | 121.5902 | 121.4515 | 60.9562 | -121.7527
432.2969 | 121.9574 | -60.8643 | 60.7498 | 1.4211e-13 | -0.010643 | 0.0014787 | 0.062936 | -0.0051408 | 0.058259 | -0.0069437 | -0.0020424 | -0.0030297 | 0.062133 | 0.015594 | 0.059908 | -60.6351 | -0.048958 | -60.7576 | 60.7432 | 60.401 | 60.4376 | -60.7933 | -60.763 | 0.046146 | -60.8754 | 60.5985 | 60.671 | 60.5506 | -60.9388 | 0.070925 | -0.00658 | 0.22914 | 0.10664 | 0.035719 | -0.34886 | -0.31223 | -0.074531 | -0.15134 | 0.10125 | -0.011096 | 0.063435 | -0.078784 | -0.1992 | 121.6075 | 121.2652 | 121.3018 | 60.8153 | -121.5431 | 121.4627 | 121.5353 | 121.4149 | 60.9104 | -121.6886
434.0312 | 121.8384 | -60.8276 | 60.91 | 1.4211e-13 | -0.010429 | 0.0014787 | 0.062722 | -0.0051408 | 0.058046 | -0.0069437 | -0.0020424 | -0.0030297 | 0.06256 | 0.014953 | 0.059908 | -60.6397 | -0.058115 | -60.753 | 60.7478 | 60.3964 | 60.4376 | -60.8025 | -60.7676 | 0.046146 | -60.8799 | 60.5939 | 60.6802 | 60.546 | -60.9434 | 0.025146 | -0.16222 | 0.18794 | 0.074601 | 0.049455 | -0.51366 | -0.47245 | -0.11573 | -0.31613 | 0.060047 | -0.052296 | 0.063435 | -0.22984 | -0.364 | 121.5755 | 121.224 | 121.2652 | 60.7695 | -121.7125 | 121.4215 | 121.5078 | 121.3737 | 60.8738 | -121.8534
435.7812 | 121.8384 | -60.9055 | 60.791 | 1.4211e-13 | -0.010643 | 0.0016923 | 0.062722 | -0.0053544 | 0.058259 | 0.00068675 | -0.0020424 | -0.0026023 | 0.062133 | 0.01538 | 0.059695 | -60.6397 | -0.058115 | -60.753 | 60.7524 | 60.401 | 60.4376 | -60.7979 | -60.763 | 0.055303 | -60.8754 | 60.5939 | 60.6756 | 60.546 | -60.9388 | 0.10755 | -0.038622 | 0.26576 | 0.15242 | 0.044876 | -0.39006 | -0.35343 | -0.033332 | -0.19712 | 0.14245 | 0.030103 | 0.063435 | -0.1154 | -0.24498 | 121.6579 | 121.3064 | 121.343 | 60.8473 | -121.5889 | 121.4994 | 121.5811 | 121.4515 | 60.9608 | -121.7298
437.4531 | 121.8658 | -60.8597 | 60.8185 | 1.4211e-13 | -0.010216 | 0.0016923 | 0.062936 | -0.005568 | 0.058687 | 0.0083173 | -0.0018288 | -0.0026023 | 0.062347 | 0.015807 | 0.060122 | -60.6397 | -0.053537 | -60.7576 | 60.7478 | 60.3964 | 60.4376 | -60.8025 | -60.7676 | 0.046146 | -60.8754 | 60.5985 | 60.6802 | 60.5552 | -60.9434 | 0.057189 | -0.070665 | 0.21998 | 0.10207 | 0.044877 | -0.42211 | -0.3809 | -0.083688 | -0.22 | 0.09209 | -0.015674 | 0.068014 | -0.13829 | -0.26329 | 121.6075 | 121.2561 | 121.2973 | 60.8061 | -121.621 | 121.4582 | 121.5399 | 121.4149 | 60.9058 | -121.7618
439.1875 | 121.843 | -60.9009 | 60.8139 | 1.4211e-13 | -0.010643 | 0.0016923 | 0.062936 | -0.0051408 | 0.058473 | 0.00068675 | -0.001615 | -0.0030297 | 0.06256 | 0.01538 | 0.059695 | -60.6351 | -0.058115 | -60.753 | 60.7432 | 60.401 | 60.433 | -60.7979 | -60.763 | 0.041567 | -60.8845 | 60.5893 | 60.6619 | 60.5506 | -60.9434 | 0.10297 | -0.070667 | 0.26576 | 0.14784 | 0.044876 | -0.41295 | -0.3809 | -0.042489 | -0.22458 | 0.13787 | 0.016367 | 0.058856 | -0.15203 | -0.26329 | 121.6441 | 121.3018 | 121.3339 | 60.8428 | -121.6118 | 121.4902 | 121.5628 | 121.4515 | 60.9424 | -121.7573
440.9375 | 121.907 | -60.8459 | 60.7773 | 1.4211e-13 | -0.010857 | 0.0014787 | 0.062936 | -0.004927 | 0.058259 | -0.022205 | -0.0018288 | -0.0026023 | 0.062133 | 0.015594 | 0.059908 | -60.6305 | -0.053537 | -60.7576 | 60.7478 | 60.3964 | 60.4422 | -60.7979 | -60.7584 | 0.046146 | -60.8754 | 60.5939 | 60.6756 | 60.5415 | -60.9388 | 0.048035 | -0.029467 | 0.2154 | 0.088333 | 0.040298 | -0.38091 | -0.33512 | -0.092842 | -0.18338 | 0.087515 | -0.029407 | 0.063435 | -0.10167 | -0.23583 | 121.5938 | 121.2423 | 121.2881 | 60.7924 | -121.5752 | 121.4398 | 121.5216 | 121.3874 | 60.8921 | -121.7161
442.6094 | 121.8155 | -60.91 | 60.8231 | 1.4211e-13 | -0.010429 | 0.0019059 | 0.062722 | -0.0053544 | 0.058473 | -0.0069437 | -0.0020424 | -0.0028161 | 0.06256 | 0.01538 | 0.059908 | -60.6397 | -0.048958 | -60.753 | 60.7478 | 60.3964 | 60.4422 | -60.7979 | -60.763 | 0.055303 | -60.8799 | 60.5893 | 60.671 | 60.5415 | -60.9434 | 0.11212 | -0.075243 | 0.27033 | 0.157 | 0.044876 | -0.42668 | -0.3809 | -0.033334 | -0.23374 | 0.14702 | 0.030101 | 0.063435 | -0.15203 | -0.2816 | 121.6578 | 121.3064 | 121.3522 | 60.8611 | -121.621 | 121.4994 | 121.5811 | 121.4515 | 60.9653 | -121.7664
444.3281 | 121.907 | -60.8551 | 60.7819 | 1.4211e-13 | -0.010857 | 0.0014787 | 0.062722 | -0.0053544 | 0.058259 | 0.015947 | -0.001615 | -0.0028161 | 0.062133 | 0.015807 | 0.059908 | -60.6351 | -0.053537 | -60.7439 | 60.7478 | 60.3918 | 60.4422 | -60.7979 | -60.7584 | 0.041567 | -60.8845 | 60.5939 | 60.6756 | 60.546 | -60.9388 | 0.057191 | -0.034044 | 0.21998 | 0.11122 | 0.054033 | -0.39006 | -0.3397 | -0.083686 | -0.18796 | 0.096671 | -0.029409 | 0.054277 | -0.10625 | -0.23583 | 121.6029 | 121.2469 | 121.2973 | 60.8016 | -121.5798 | 121.449 | 121.5307 | 121.4011 | 60.8967 | -121.7206
446.0625 | 121.8933 | -60.8368 | 60.8688 | 1.4211e-13 | -0.010857 | 0.0014787 | 0.062295 | -0.0053544 | 0.058046 | 0.00068675 | -0.002256 | -0.0026023 | 0.06256 | 0.01538 | 0.060122 | -60.6351 | -0.053537 | -60.7576 | 60.7432 | 60.3872 | 60.4376 | -60.8025 | -60.763 | 0.046146 | -60.8799 | 60.5893 | 60.6665 | 60.5415 | -60.9388 | 0.034301 | -0.1256 | 0.20167 | 0.079178 | 0.044877 | -0.48162 | -0.43125 | -0.102 | -0.27951 | 0.073781 | -0.043141 | 0.058856 | -0.20238 | -0.32738 | 121.58 | 121.224 | 121.2744 | 60.7833 | -121.6713 | 121.4261 | 121.5032 | 121.3782 | 60.8829 | -121.8076
447.7969 | 121.8063 | -60.8917 | 60.8139 | 1.4211e-13 | -0.010857 | 0.0016923 | 0.062509 | -0.0053544 | 0.058473 | 0.00068675 | -0.0020424 | -0.0026023 | 0.062347 | 0.015594 | 0.059695 | -60.6443 | -0.053537 | -60.7576 | 60.7524 | 60.4055 | 60.433 | -60.7979 | -60.763 | 0.046146 | -60.8754 | 60.5847 | 60.671 | 60.5369 | -60.9388 | 0.093812 | -0.06151 | 0.24745 | 0.13411 | 0.040298 | -0.40837 | -0.3809 | -0.047065 | -0.22916 | 0.12871 | 0.01637 | 0.063435 | -0.14287 | -0.27703 | 121.6441 | 121.2973 | 121.3247 | 60.8382 | -121.6118 | 121.4765 | 121.5628 | 121.4286 | 60.9379 | -121.7527
449.4688 | 121.8384 | -60.8185 | 60.8688 | 1.4211e-13 | -0.010857 | 0.0016923 | 0.062936 | -0.0053544 | 0.058259 | 0.00068675 | -0.001615 | -0.0028161 | 0.06256 | 0.01538 | 0.059908 | -60.6443 | -0.058115 | -60.753 | 60.7478 | 60.401 | 60.4422 | -60.8025 | -60.763 | 0.041567 | -60.8754 | 60.5893 | 60.6756 | 60.546 | -60.9342 | 0.01599 | -0.12102 | 0.1742 | 0.065445 | 0.049455 | -0.46788 | -0.42667 | -0.11573 | -0.27951 | 0.05547 | -0.056873 | 0.058857 | -0.19322 | -0.3228 | 121.5663 | 121.2194 | 121.2606 | 60.7604 | -121.6713 | 121.4078 | 121.4941 | 121.3645 | 60.86 | -121.803
451.2031 | 121.8521 | -60.878 | 60.8002 | 1.4211e-13 | -0.01107 | 0.0014787 | 0.062722 | -0.0053544 | 0.058259 | 0.00068675 | -0.0020424 | -0.0026023 | 0.062133 | 0.01538 | 0.059908 | -60.6443 | -0.053537 | -60.7576 | 60.757 | 60.3964 | 60.4376 | -60.7979 | -60.7584 | 0.041567 | -60.8845 | 60.5893 | 60.6756 | 60.546 | -60.9388 | 0.080079 | -0.043199 | 0.23371 | 0.12038 | 0.040298 | -0.4038 | -0.36259 | -0.060798 | -0.21085 | 0.11956 | -0.006521 | 0.054277 | -0.12456 | -0.25414 | 121.635 | 121.2744 | 121.3156 | 60.8245 | -121.5981 | 121.4673 | 121.5536 | 121.424 | 60.9196 | -121.739
452.9375 | 121.8933 | -60.8459 | 60.8368 | 1.4211e-13 | -0.010643 | 0.0012649 | 0.062722 | -0.0051408 | 0.058046 | 0.00068675 | -0.001615 | -0.0026023 | 0.062347 | 0.015594 | 0.059695 | -60.6397 | -0.058115 | -60.753 | 60.7432 | 60.401 | 60.433 | -60.7979 | -60.7539 | 0.041567 | -60.8799 | 60.5847 | 60.671 | 60.5415 | -60.9434 | 0.048035 | -0.093555 | 0.20625 | 0.092911 | 0.044876 | -0.43584 | -0.40379 | -0.097421 | -0.25205 | 0.092094 | -0.033986 | 0.063435 | -0.16576 | -0.29534 | 121.5892 | 121.2469 | 121.279 | 60.7878 | -121.6347 | 121.4307 | 121.517 | 121.3874 | 60.8875 | -121.7802
454.6719 | 121.9437 | -60.791 | 60.8414 | 1.4211e-13 | -0.010643 | 0.0016923 | 0.062936 | -0.0051408 | 0.058259 | 0.00068675 | -0.0020424 | -0.0026023 | 0.062133 | 0.016021 | 0.059908 | -60.6397 | -0.062694 | -60.7576 | 60.7524 | 60.3918 | 60.4513 | -60.7979 | -60.7584 | 0.046146 | -60.8799 | 60.5893 | 60.6756 | 60.5506 | -60.9388 | -0.006896 | -0.088976 | 0.15132 | 0.033402 | 0.040298 | -0.44957 | -0.39005 | -0.14777 | -0.25205 | 0.032584 | -0.088917 | 0.058856 | -0.16576 | -0.29076 | 121.5434 | 121.1828 | 121.2423 | 60.7283 | -121.6393 | 121.3803 | 121.4666 | 121.3416 | 60.8372 | -121.7802
456.3594 | 121.8704 | -60.8231 | 60.8643 | 1.4211e-13 | -0.010857 | 0.0014787 | 0.062936 | -0.004927 | 0.058259 | 0.00068675 | -0.0018288 | -0.0026023 | 0.06256 | 0.016021 | 0.060122 | -60.6305 | -0.048958 | -60.7576 | 60.7478 | 60.3964 | 60.4422 | -60.7979 | -60.763 | 0.046146 | -60.8708 | 60.5939 | 60.6665 | 60.546 | -60.9434 | 0.025147 | -0.11644 | 0.19252 | 0.065445 | 0.040298 | -0.46788 | -0.4221 | -0.12031 | -0.27036 | 0.060048 | -0.047716 | 0.072593 | -0.1978 | -0.31822 | 121.5709 | 121.2194 | 121.2652 | 60.7741 | -121.6622 | 121.417 | 121.4895 | 121.3691 | 60.8692 | -121.8076
458.0938 | 121.8796 | -60.9009 | 60.7681 | 1.4211e-13 | -0.010643 | 0.0016923 | 0.062936 | -0.0051408 | 0.058473 | -0.0069437 | -0.0018288 | -0.0026023 | 0.062347 | 0.015594 | 0.059908 | -60.6397 | -0.048958 | -60.753 | 60.7432 | 60.3964 | 60.4376 | -60.7933 | -60.7539 | 0.036989 | -60.8754 | 60.5893 | 60.671 | 60.5369 | -60.9388 | 0.10755 | -0.02489 | 0.26118 | 0.14784 | 0.040297 | -0.37175 | -0.33054 | -0.03791 | -0.1788 | 0.14703 | 0.025525 | 0.063435 | -0.097094 | -0.23125 | 121.6441 | 121.2973 | 121.3385 | 60.8519 | -121.5615 | 121.4902 | 121.5719 | 121.4378 | 60.9379 | -121.7069
459.8281 | 121.9116 | -60.8505 | 60.7636 | 1.4211e-13 | -0.010857 | 0.0019059 | 0.062722 | -0.0051408 | 0.058259 | -0.0069437 | -0.0020424 | -0.0028161 | 0.062347 | 0.016021 | 0.059695 | -60.6351 | -0.058115 | -60.7485 | 60.7478 | 60.3918 | 60.433 | -60.7979 | -60.7584 | 0.046146 | -60.8754 | 60.5847 | 60.6665 | 60.5506 | -60.9388 | 0.052613 | -0.015734 | 0.2154 | 0.10207 | 0.049455 | -0.37176 | -0.33055 | -0.088264 | -0.17881 | 0.092093 | -0.024829 | 0.063435 | -0.097096 | -0.21294 | 121.5983 | 121.2423 | 121.2835 | 60.7924 | -121.5615 | 121.4353 | 121.517 | 121.4011 | 60.8967 | -121.7023
461.5625 | 121.8109 | -60.91 | 60.7864 | 1.4211e-13 | -0.011284 | 0.0014787 | 0.062722 | -0.004927 | 0.058259 | 0.015947 | -0.0020424 | -0.0026023 | 0.06256 | 0.015594 | 0.059695 | -60.6305 | -0.058115 | -60.753 | 60.7478 | 60.3964 | 60.4422 | -60.8071 | -60.763 | 0.046146 | -60.8708 | 60.5847 | 60.6665 | 60.5506 | -60.9479 | 0.10296 | -0.038622 | 0.27949 | 0.157 | 0.054034 | -0.39006 | -0.34428 | -0.037913 | -0.20169 | 0.14702 | 0.039259 | 0.077172 | -0.11998 | -0.23583 | 121.6578 | 121.3064 | 121.3522 | 60.8519 | -121.5935 | 121.4948 | 121.5765 | 121.4606 | 60.9562 | -121.7344
463.2969 | 121.9528 | -60.7956 | 60.8414 | 1.4211e-13 | -0.01107 | 0.0016923 | 0.062936 | -0.0051408 | 0.058046 | -0.014574 | -0.001615 | -0.0026023 | 0.062347 | 0.015594 | 0.059695 | -60.6351 | -0.053537 | -60.7485 | 60.7387 | 60.3964 | 60.4422 | -60.7933 | -60.763 | 0.041567 | -60.8708 | 60.5893 | 60.671 | 60.5415 | -60.9434 | 0.00226 | -0.10271 | 0.16047 | 0.047136 | 0.044876 | -0.445 | -0.39921 | -0.14778 | -0.25205 | 0.032582 | -0.075182 | 0.072593 | -0.17034 | -0.29991 | 121.5343 | 121.192 | 121.2378 | 60.7421 | -121.6347 | 121.3849 | 121.4666 | 121.337 | 60.8372 | -121.7847
464.9688 | 121.962 | -60.791 | 60.8185 | 1.4211e-13 | -0.011284 | 0.0016923 | 0.062722 | -0.004927 | 0.058046 | 0.0083173 | -0.0018288 | -0.0028161 | 0.062774 | 0.016021 | 0.059695 | -60.6351 | -0.048958 | -60.7439 | 60.7478 | 60.3964 | 60.4376 | -60.7933 | -60.7539 | 0.036989 | -60.8754 | 60.5847 | 60.6573 | 60.5415 | -60.9434 | -0.002317 | -0.070665 | 0.1559 | 0.047137 | 0.049454 | -0.42211 | -0.3809 | -0.15235 | -0.23374 | 0.037163 | -0.084338 | 0.068014 | -0.16118 | -0.27703 | 121.5388 | 121.1874 | 121.2286 | 60.7421 | -121.6118 | 121.3758 | 121.4483 | 121.3325 | 60.828 | -121.7618
466.7188 | 121.8338 | -60.8368 | 60.8597 | 1.4211e-13 | -0.011284 | 0.0014787 | 0.062936 | -0.0051408 | 0.058046 | -0.0069437 | -0.001615 | -0.0028161 | 0.062133 | 0.016021 | 0.059695 | -60.6351 | -0.053537 | -60.753 | 60.7478 | 60.3964 | 60.433 | -60.7933 | -60.763 | 0.046146 | -60.8708 | 60.5893 | 60.6619 | 60.5552 | -60.9388 | 0.043459 | -0.11186 | 0.20167 | 0.083756 | 0.040297 | -0.46331 | -0.42668 | -0.102 | -0.27036 | 0.073781 | -0.033983 | 0.068014 | -0.1978 | -0.30449 | 121.5846 | 121.2332 | 121.2698 | 60.7833 | -121.653 | 121.4261 | 121.4987 | 121.392 | 60.8829 | -121.7985
468.4531 | 121.9528 | -60.8002 | 60.8276 | 1.4211e-13 | -0.01107 | 0.0016923 | 0.062936 | -0.004927 | 0.058473 | 0.00068675 | -0.0018288 | -0.0030297 | 0.062347 | 0.015594 | 0.059695 | -60.6305 | -0.058115 | -60.7485 | 60.7387 | 60.3964 | 60.433 | -60.7933 | -60.7539 | 0.041567 | -60.8754 | 60.5893 | 60.6573 | 60.5323 | -60.9388 | 0.006838 | -0.088978 | 0.16963 | 0.051714 | 0.044876 | -0.43126 | -0.39463 | -0.13862 | -0.23832 | 0.046318 | -0.075183 | 0.063435 | -0.17034 | -0.29534 | 121.5388 | 121.1965 | 121.2332 | 60.7421 | -121.621 | 121.3895 | 121.4575 | 121.3325 | 60.8417 | -121.7664
470.125 | 121.8338 | -60.791 | 60.878 | 1.4211e-13 | -0.01107 | 0.0014787 | 0.062936 | -0.005568 | 0.058046 | 0.00068675 | -0.001615 | -0.0026023 | 0.062133 | 0.015807 | 0.060122 | -60.6305 | -0.058115 | -60.7439 | 60.7387 | 60.3964 | 60.4376 | -60.7979 | -60.7584 | 0.046146 | -60.8754 | 60.5802 | 60.6665 | 60.5415 | -60.9434 | -0.006896 | -0.13933 | 0.16047 | 0.047137 | 0.054033 | -0.48162 | -0.44041 | -0.15235 | -0.29783 | 0.032584 | -0.084338 | 0.068014 | -0.21154 | -0.33654 | 121.5297 | 121.1874 | 121.2286 | 60.7329 | -121.6759 | 121.3712 | 121.4575 | 121.3325 | 60.8372 | -121.8214
471.8594 | 121.8246 | -60.8917 | 60.7819 | 1.4211e-13 | -0.01107 | 0.0016923 | 0.062509 | -0.005568 | 0.058259 | 0.00068675 | -0.001615 | -0.0026023 | 0.062347 | 0.015807 | 0.059908 | -60.6351 | -0.062694 | -60.7439 | 60.7478 | 60.3872 | 60.4422 | -60.7979 | -60.7539 | 0.046146 | -60.8662 | 60.5893 | 60.6665 | 60.5369 | -60.9434 | 0.093812 | -0.034044 | 0.2566 | 0.14785 | 0.054033 | -0.39464 | -0.3397 | -0.051644 | -0.19254 | 0.13787 | 0.025527 | 0.077171 | -0.11541 | -0.24498 | 121.6395 | 121.2789 | 121.3339 | 60.829 | -121.5798 | 121.481 | 121.5582 | 121.4286 | 60.9379 | -121.7252
473.6094 | 121.7926 | -60.878 | 60.8093 | 1.4211e-13 | -0.011284 | 0.0019059 | 0.062509 | -0.0051408 | 0.058046 | -0.0069437 | -0.001615 | -0.0028161 | 0.062347 | 0.016021 | 0.059481 | -60.6305 | -0.058115 | -60.7439 | 60.7387 | 60.3964 | 60.4376 | -60.7933 | -60.7539 | 0.036989 | -60.8708 | 60.5802 | 60.6665 | 60.5369 | -60.9388 | 0.084658 | -0.070667 | 0.24745 | 0.13411 | 0.049454 | -0.41295 | -0.37174 | -0.060798 | -0.22916 | 0.12414 | 0.007216 | 0.068014 | -0.14287 | -0.27245 | 121.6166 | 121.2744 | 121.3156 | 60.8199 | -121.6027 | 121.4582 | 121.5444 | 121.4149 | 60.915 | -121.7481
475.2812 | 121.8521 | -60.8505 | 60.8276 | 1.4211e-13 | -0.01107 | 0.0014787 | 0.062722 | -0.0053544 | 0.058046 | 0.0083173 | -0.001615 | -0.0023887 | 0.062347 | 0.016021 | 0.059481 | -60.6351 | -0.058115 | -60.7439 | 60.7387 | 60.3964 | 60.4422 | -60.7888 | -60.7584 | 0.050725 | -60.8754 | 60.5847 | 60.6756 | 60.546 | -60.9434 | 0.06177 | -0.088978 | 0.2154 | 0.10665 | 0.044876 | -0.43126 | -0.38548 | -0.092843 | -0.24289 | 0.092093 | -0.024829 | 0.068014 | -0.15203 | -0.2816 | 121.5892 | 121.2469 | 121.2927 | 60.7924 | -121.6164 | 121.4353 | 121.5261 | 121.3966 | 60.9012 | -121.771
477 | 121.8338 | -60.9192 | 60.7681 | 1.4211e-13 | -0.01107 | 0.0016923 | 0.062936 | -0.0053544 | 0.058046 | 0.0083173 | -0.0020424 | -0.0026023 | 0.062347 | 0.015594 | 0.059908 | -60.626 | -0.062694 | -60.7485 | 60.7478 | 60.3918 | 60.4376 | -60.7933 | -60.7584 | 0.046146 | -60.8754 | 60.5802 | 60.6619 | 60.5415 | -60.9388 | 0.12586 | -0.020311 | 0.29322 | 0.17073 | 0.044876 | -0.37633 | -0.33054 | -0.0196 | -0.18796 | 0.16076 | 0.043835 | 0.063435 | -0.10625 | -0.22667 | 121.667 | 121.311 | 121.3568 | 60.8565 | -121.5615 | 121.4994 | 121.5811 | 121.4606 | 60.9653 | -121.7069
478.7344 | 121.9345 | -60.8551 | 60.7315 | 1.4211e-13 | -0.011498 | 0.0016923 | 0.062936 | -0.0051408 | 0.058259 | 0.00068675 | -0.0020424 | -0.0030297 | 0.062347 | 0.016021 | 0.059695 | -60.6305 | -0.053537 | -60.753 | 60.7432 | 60.3872 | 60.4376 | -60.7979 | -60.7539 | 0.046146 | -60.8662 | 60.5893 | 60.6619 | 60.5369 | -60.9479 | 0.057191 | 0.011731 | 0.22456 | 0.10207 | 0.044876 | -0.34429 | -0.29392 | -0.092844 | -0.14218 | 0.10125 | -0.011094 | 0.08175 | -0.069631 | -0.19463 | 121.5983 | 121.2423 | 121.2927 | 60.8016 | -121.5294 | 121.4444 | 121.517 | 121.392 | 60.9012 | -121.6795
480.4062 | 121.8292 | -60.9283 | 60.8002 | 1.4211e-13 | -0.011284 | 0.0016923 | 0.062509 | -0.005568 | 0.057832 | -0.0069437 | -0.001615 | -0.0026023 | 0.06256 | 0.015594 | 0.059695 | -60.626 | -0.058115 | -60.7439 | 60.7524 | 60.3918 | 60.433 | -60.7842 | -60.7584 | 0.036989 | -60.8616 | 60.5847 | 60.6619 | 60.5369 | -60.9296 | 0.14417 | -0.047777 | 0.30238 | 0.18447 | 0.040297 | -0.40838 | -0.36717 | -0.001287 | -0.21543 | 0.16991 | 0.066727 | 0.068014 | -0.1383 | -0.26329 | 121.6807 | 121.3201 | 121.3613 | 60.8702 | -121.5843 | 121.5131 | 121.5902 | 121.4652 | 60.9653 | -121.7298
482.1406 | 121.7972 | -60.8231 | 60.878 | 1.4211e-13 | -0.011284 | 0.0016923 | 0.062509 | -0.0053544 | 0.058046 | -0.0069437 | -0.0020424 | -0.0026023 | 0.062133 | 0.015807 | 0.059481 | -60.6305 | -0.062694 | -60.7393 | 60.7432 | 60.401 | 60.433 | -60.7979 | -60.7493 | 0.041567 | -60.8708 | 60.5756 | 60.6619 | 60.5415 | -60.9342 | 0.025147 | -0.13475 | 0.19252 | 0.083758 | 0.058611 | -0.47704 | -0.44499 | -0.11115 | -0.30241 | 0.073784 | -0.047716 | 0.063436 | -0.21612 | -0.33654 | 121.5663 | 121.224 | 121.2561 | 60.7604 | -121.6759 | 121.3986 | 121.4849 | 121.3645 | 60.8646 | -121.8122
483.875 | 121.9116 | -60.8276 | 60.8047 | 1.4211e-13 | -0.011711 | 0.0014787 | 0.062722 | -0.0051408 | 0.057832 | 0.00068675 | -0.0018288 | -0.0028161 | 0.062774 | 0.016021 | 0.059695 | -60.6305 | -0.058115 | -60.753 | 60.7387 | 60.3918 | 60.4376 | -60.7979 | -60.7539 | 0.046146 | -60.8708 | 60.5847 | 60.6665 | 60.5277 | -60.9434 | 0.029725 | -0.06609 | 0.19709 | 0.074601 | 0.044876 | -0.41295 | -0.36717 | -0.11573 | -0.22001 | 0.073784 | -0.043138 | 0.072593 | -0.13829 | -0.27703 | 121.5663 | 121.2194 | 121.2652 | 60.7695 | -121.6027 | 121.4124 | 121.4941 | 121.3554 | 60.8738 | -121.7481
485.6094 | 121.8384 | -60.878 | 60.8093 | 1.4211e-13 | -0.011498 | 0.0019059 | 0.062722 | -0.0051408 | 0.058259 | 0.00068675 | -0.0018288 | -0.0028161 | 0.062347 | 0.016021 | 0.059908 | -60.6305 | -0.053537 | -60.7439 | 60.7478 | 60.3964 | 60.4376 | -60.8025 | -60.7493 | 0.036989 | -60.8662 | 60.5802 | 60.6665 | 60.5369 | -60.9342 | 0.0755 | -0.06151 | 0.24745 | 0.13411 | 0.058612 | -0.41295 | -0.37174 | -0.05622 | -0.22916 | 0.12872 | 0.011794 | 0.068014 | -0.14287 | -0.27245 | 121.6258 | 121.2744 | 121.3156 | 60.8245 | -121.6118 | 121.4582 | 121.5444 | 121.4149 | 60.915 | -121.7435
487.2812 | 121.9208 | -60.7864 | 60.7956 | 1.4211e-13 | -0.011284 | 0.0016923 | 0.06315 | -0.0051408 | 0.058046 | -0.0069437 | -0.0018288 | -0.0028161 | 0.061919 | 0.015807 | 0.059695 | -60.6305 | -0.053537 | -60.753 | 60.7432 | 60.3918 | 60.4422 | -60.7933 | -60.7493 | 0.041567 | -60.8662 | 60.5893 | 60.6573 | 60.5369 | -60.9434 | -0.006895 | -0.052356 | 0.15589 | 0.033402 | 0.040297 | -0.4038 | -0.35343 | -0.15693 | -0.20627 | 0.037163 | -0.079759 | 0.077171 | -0.1383 | -0.25872 | 121.5297 | 121.1782 | 121.2286 | 60.7329 | -121.5889 | 121.3758 | 121.4437 | 121.3233 | 60.828 | -121.739
488.9531 | 121.9437 | -60.8551 | 60.7452 | 1.4211e-13 | -0.01107 | 0.0014787 | 0.062936 | -0.0053544 | 0.058259 | -0.0069437 | -0.0020424 | -0.0028161 | 0.062347 | 0.015807 | 0.059267 | -60.626 | -0.053537 | -60.7485 | 60.7432 | 60.3918 | 60.4376 | -60.7888 | -60.7539 | 0.046146 | -60.8616 | 60.5802 | 60.6573 | 60.5369 | -60.9342 | 0.066348 | -0.002002 | 0.22914 | 0.10665 | 0.040298 | -0.35344 | -0.30766 | -0.079108 | -0.16507 | 0.10125 | -0.006515 | 0.072593 | -0.087942 | -0.20836 | 121.5983 | 121.2469 | 121.2927 | 60.8016 | -121.534 | 121.4353 | 121.5124 | 121.392 | 60.9012 | -121.6795
490.6875 | 121.8887 | -60.8459 | 60.8139 | 1.4211e-13 | -0.011498 | 0.0014787 | 0.062722 | -0.0051408 | 0.058046 | -0.0069437 | -0.0018288 | -0.0028161 | 0.061919 | 0.016235 | 0.059695 | -60.6305 | -0.067272 | -60.7485 | 60.7341 | 60.3918 | 60.433 | -60.7888 | -60.7539 | 0.046146 | -60.8662 | 60.5847 | 60.6619 | 60.5323 | -60.9434 | 0.057192 | -0.079824 | 0.2154 | 0.09749 | 0.040298 | -0.42211 | -0.3809 | -0.097421 | -0.22916 | 0.092094 | -0.02025 | 0.077171 | -0.15203 | -0.28161 | 121.58 | 121.2377 | 121.279 | 60.7787 | -121.6027 | 121.4307 | 121.5078 | 121.3782 | 60.8921 | -121.7573
492.4219 | 121.8155 | -60.8276 | 60.8459 | 1.4211e-13 | -0.011711 | 0.0014787 | 0.062722 | -0.0051408 | 0.058259 | 0.0083173 | -0.0018288 | -0.0028161 | 0.062347 | 0.016449 | 0.059481 | -60.626 | -0.044379 | -60.7576 | 60.7341 | 60.3918 | 60.433 | -60.7842 | -60.7493 | 0.046146 | -60.8662 | 60.5847 | 60.6619 | 60.5369 | -60.9434 | 0.043461 | -0.11187 | 0.20167 | 0.070023 | 0.026562 | -0.45415 | -0.41294 | -0.11573 | -0.2612 | 0.078362 | -0.03856 | 0.077171 | -0.18407 | -0.30907 | 121.5617 | 121.2194 | 121.2606 | 60.7833 | -121.6301 | 121.4124 | 121.4895 | 121.3645 | 60.8738 | -121.7893
494.0938 | 121.8018 | -60.8276 | 60.9009 | 1.4211e-13 | -0.011711 | 0.0010513 | 0.062936 | -0.0053544 | 0.058473 | 0.0083173 | -0.0018288 | -0.0032433 | 0.06256 | 0.016021 | 0.059267 | -60.6305 | -0.058115 | -60.7439 | 60.7341 | 60.3872 | 60.4467 | -60.7933 | -60.7584 | 0.046146 | -60.8708 | 60.5847 | 60.6619 | 60.5369 | -60.9434 | 0.034304 | -0.1668 | 0.19709 | 0.083758 | 0.049454 | -0.51366 | -0.45414 | -0.11573 | -0.31614 | 0.069205 | -0.043138 | 0.072593 | -0.239 | -0.364 | 121.5617 | 121.2149 | 121.2744 | 60.7695 | -121.6942 | 121.4124 | 121.4895 | 121.3645 | 60.8738 | -121.8442
495.8438 | 121.9345 | -60.7773 | 60.8185 | 1.4211e-13 | -0.011711 | 0.0016923 | 0.062722 | -0.0051408 | 0.058259 | 0.00068675 | -0.0020424 | -0.0030297 | 0.062133 | 0.016449 | 0.059267 | -60.6214 | -0.053537 | -60.7485 | 60.7295 | 60.3918 | 60.4376 | -60.7888 | -60.7493 | 0.041567 | -60.8662 | 60.5847 | 60.6619 | 60.5369 | -60.9479 | -0.011472 | -0.088979 | 0.1559 | 0.028826 | 0.040298 | -0.42669 | -0.3809 | -0.17066 | -0.23374 | 0.028008 | -0.088914 | 0.08175 | -0.15661 | -0.2816 | 121.5068 | 121.1691 | 121.2149 | 60.7237 | -121.6072 | 121.362 | 121.4392 | 121.3142 | 60.8188 | -121.7664
497.5625 | 121.8155 | -60.8276 | 60.8597 | 1.4211e-13 | -0.011711 | 0.0014787 | 0.062722 | -0.0053544 | 0.057832 | -0.0069437 | -0.0018288 | -0.0028161 | 0.061919 | 0.016235 | 0.059695 | -60.6214 | -0.053537 | -60.7485 | 60.7341 | 60.3964 | 60.4376 | -60.7888 | -60.7539 | 0.041567 | -60.8662 | 60.5802 | 60.6665 | 60.546 | -60.9434 | 0.038882 | -0.1256 | 0.20625 | 0.07918 | 0.040298 | -0.46331 | -0.4221 | -0.11573 | -0.27951 | 0.073784 | -0.03856 | 0.077171 | -0.19323 | -0.31365 | 121.5617 | 121.224 | 121.2652 | 60.7741 | -121.6484 | 121.4078 | 121.4941 | 121.3737 | 60.8692 | -121.803
499.2188 | 121.9299 | -60.7956 | 60.791 | 1.4211e-13 | -0.011711 | 0.0012649 | 0.06315 | -0.0053544 | 0.057832 | -0.0069437 | -0.001615 | -0.0028161 | 0.062133 | 0.016449 | 0.059481 | -60.6168 | -0.048958 | -60.7485 | 60.7387 | 60.3918 | 60.4467 | -60.7888 | -60.7493 | 0.041567 | -60.8616 | 60.5802 | 60.6619 | 60.5277 | -60.9434 | 0.006838 | -0.052357 | 0.17878 | 0.047136 | 0.040298 | -0.39922 | -0.34428 | -0.14778 | -0.21085 | 0.046318 | -0.066025 | 0.08175 | -0.12914 | -0.2633 | 121.5343 | 121.1874 | 121.2423 | 60.7466 | -121.5798 | 121.3758 | 121.4575 | 121.3233 | 60.8372 | -121.7344
500.9531 | 121.9254 | -60.8414 | 60.7315 | 1.4211e-13 | -0.011925 | 0.0019059 | 0.062509 | -0.0051408 | 0.058046 | -0.0069437 | -0.0018288 | -0.0028161 | 0.062347 | 0.016235 | 0.059481 | -60.6214 | -0.053537 | -60.7439 | 60.7387 | 60.3918 | 60.4376 | -60.7842 | -60.7539 | 0.046146 | -60.8662 | 60.5847 | 60.6665 | 60.5323 | -60.9434 | 0.057194 | 0.007153 | 0.21998 | 0.097491 | 0.040297 | -0.33971 | -0.29392 | -0.102 | -0.14676 | 0.087517 | -0.024827 | 0.077171 | -0.065052 | -0.19921 | 121.58 | 121.2332 | 121.279 | 60.7878 | -121.5157 | 121.4261 | 121.5078 | 121.3737 | 60.8875 | -121.6749
502.6875 | 121.8338 | -60.8414 | 60.8047 | 1.4211e-13 | -0.011498 | 0.0016923 | 0.062722 | -0.0053544 | 0.058046 | 0.0083173 | -0.0018288 | -0.0023887 | 0.062347 | 0.016235 | 0.059695 | -60.626 | -0.048958 | -60.7393 | 60.7387 | 60.401 | 60.433 | -60.7888 | -60.7493 | 0.041567 | -60.8616 | 60.5756 | 60.6527 | 60.5369 | -60.9342 | 0.052615 | -0.06609 | 0.2154 | 0.10207 | 0.049454 | -0.4038 | -0.37175 | -0.092841 | -0.22916 | 0.092095 | -0.020248 | 0.072593 | -0.15203 | -0.26787 | 121.58 | 121.2423 | 121.2744 | 60.7924 | -121.5935 | 121.417 | 121.4941 | 121.3782 | 60.8829 | -121.739
504.4219 | 121.8246 | -60.8231 | 60.8643 | 1.4211e-13 | -0.011284 | 0.0014787 | 0.062936 | -0.0053544 | 0.058046 | -0.0069437 | -0.0018288 | -0.0026023 | 0.062133 | 0.016449 | 0.059481 | -60.6214 | -0.071851 | -60.7439 | 60.7387 | 60.3918 | 60.433 | -60.7933 | -60.7539 | 0.036989 | -60.857 | 60.5756 | 60.6573 | 60.5369 | -60.9434 | 0.029726 | -0.1256 | 0.20167 | 0.07918 | 0.049454 | -0.47246 | -0.43125 | -0.12031 | -0.28867 | 0.069206 | -0.03398 | 0.086329 | -0.20696 | -0.32738 | 121.5617 | 121.2149 | 121.2561 | 60.7512 | -121.6576 | 121.3986 | 121.4804 | 121.3599 | 60.86 | -121.8076
506.1719 | 121.8155 | -60.791 | 60.878 | 1.4211e-13 | -0.011711 | 0.0016923 | 0.062722 | -0.0057818 | 0.057832 | 0.00068675 | -0.0020424 | -0.0028161 | 0.062133 | 0.016235 | 0.059695 | -60.626 | -0.053537 | -60.7485 | 60.7387 | 60.3872 | 60.433 | -60.7842 | -60.7493 | 0.036989 | -60.8662 | 60.5664 | 60.6619 | 60.5369 | -60.9479 | 0.00684 | -0.13933 | 0.16505 | 0.042559 | 0.035719 | -0.49077 | -0.44499 | -0.15693 | -0.31156 | 0.041741 | -0.075181 | 0.08175 | -0.21612 | -0.34112 | 121.5297 | 121.1782 | 121.224 | 60.7375 | -121.6622 | 121.3574 | 121.4529 | 121.3279 | 60.828 | -121.8259
507.8438 | 121.8063 | -60.8734 | 60.791 | 1.4211e-13 | -0.011925 | 0.0014787 | 0.062936 | -0.0053544 | 0.057832 | -0.0069437 | -0.0020424 | -0.0026023 | 0.062133 | 0.016021 | 0.059695 | -60.6168 | -0.053537 | -60.7576 | 60.7387 | 60.3918 | 60.4422 | -60.7888 | -60.7539 | 0.036989 | -60.8662 | 60.5802 | 60.671 | 60.5277 | -60.9434 | 0.084658 | -0.052357 | 0.25661 | 0.1158 | 0.031141 | -0.39922 | -0.34886 | -0.069955 | -0.21085 | 0.11956 | 0.007216 | 0.077171 | -0.11998 | -0.2633 | 121.6121 | 121.2652 | 121.3156 | 60.8199 | -121.5798 | 121.4536 | 121.5444 | 121.4011 | 60.9104 | -121.7344
509.5781 | 121.8292 | -60.8139 | 60.8734 | 1.4211e-13 | -0.011925 | 0.0016923 | 0.062936 | -0.0051408 | 0.057832 | -0.0069437 | -0.0020424 | -0.0026023 | 0.062133 | 0.016662 | 0.059267 | -60.6168 | -0.058115 | -60.7393 | 60.7341 | 60.3872 | 60.433 | -60.7842 | -60.7447 | 0.041567 | -60.8616 | 60.5802 | 60.6665 | 60.5323 | -60.9479 | 0.029728 | -0.13933 | 0.1971 | 0.074603 | 0.044875 | -0.4862 | -0.44041 | -0.13404 | -0.29325 | 0.069208 | -0.047714 | 0.086329 | -0.20696 | -0.34112 | 121.548 | 121.2011 | 121.2469 | 60.7558 | -121.6576 | 121.3941 | 121.4804 | 121.3462 | 60.8555 | -121.8214
511.3281 | 121.8155 | -60.9009 | 60.791 | 1.4211e-13 | -0.011925 | 0.0012649 | 0.062722 | -0.0051408 | 0.058259 | 0.00068675 | -0.0020424 | -0.0026023 | 0.062347 | 0.016449 | 0.059481 | -60.6168 | -0.053537 | -60.7485 | 60.7387 | 60.3826 | 60.4376 | -60.7933 | -60.7447 | 0.046146 | -60.8662 | 60.5756 | 60.6665 | 60.5277 | -60.9525 | 0.10755 | -0.052357 | 0.28407 | 0.15242 | 0.044876 | -0.40838 | -0.35343 | -0.051647 | -0.21543 | 0.15618 | 0.034682 | 0.086329 | -0.12456 | -0.2633 | 121.6395 | 121.2835 | 121.3385 | 60.8473 | -121.5843 | 121.4765 | 121.5673 | 121.4286 | 60.947 | -121.7435
513 | 121.9208 | -60.7819 | 60.8231 | 1.4211e-13 | -0.012139 | 0.0016923 | 0.062936 | -0.0051408 | 0.057618 | 0.00068675 | -0.001615 | -0.0023887 | 0.062133 | 0.016662 | 0.059481 | -60.626 | -0.053537 | -60.7439 | 60.7341 | 60.3918 | 60.4376 | -60.7933 | -60.7493 | 0.041567 | -60.8616 | 60.5802 | 60.6665 | 60.5369 | -60.9434 | -0.011473 | -0.088979 | 0.1559 | 0.037981 | 0.049454 | -0.43126 | -0.38548 | -0.16151 | -0.24289 | 0.032585 | -0.079758 | 0.08175 | -0.1566 | -0.28618 | 121.5159 | 121.1737 | 121.2194 | 60.7283 | -121.6164 | 121.362 | 121.4483 | 121.3187 | 60.8234 | -121.7664
514.7344 | 121.8842 | -60.8414 | 60.7773 | 1.4211e-13 | -0.011925 | 0.0014787 | 0.062722 | -0.004927 | 0.058046 | 0.00068675 | -0.0020424 | -0.0026023 | 0.062133 | 0.016449 | 0.059481 | -60.6168 | -0.053537 | -60.7485 | 60.7341 | 60.3872 | 60.4422 | -60.7796 | -60.7493 | 0.036989 | -60.8616 | 60.5756 | 60.6665 | 60.5323 | -60.9388 | 0.061773 | -0.043203 | 0.22456 | 0.092913 | 0.03114 | -0.39007 | -0.33512 | -0.097419 | -0.2017 | 0.092095 | -0.020248 | 0.077171 | -0.11083 | -0.24499 | 121.5754 | 121.2286 | 121.2835 | 60.7878 | -121.5569 | 121.417 | 121.5078 | 121.3737 | 60.8784 | -121.7161
516.4062 | 121.7926 | -60.8139 | 60.8734 | 1.4211e-13 | -0.011925 | 0.0016923 | 0.062936 | -0.0047134 | 0.057832 | -0.0069437 | -0.0020424 | -0.0028161 | 0.062347 | 0.016449 | 0.059695 | -60.626 | -0.058115 | -60.7393 | 60.7295 | 60.3918 | 60.433 | -60.7842 | -60.7401 | 0.046146 | -60.8662 | 60.5756 | 60.671 | 60.5415 | -60.9434 | 0.029728 | -0.14391 | 0.18794 | 0.074603 | 0.044875 | -0.48162 | -0.44041 | -0.12946 | -0.29783 | 0.073787 | -0.052293 | 0.077171 | -0.20238 | -0.33196 | 121.5434 | 121.2057 | 121.2469 | 60.7558 | -121.6576 | 121.3895 | 121.4849 | 121.3554 | 60.8601 | -121.8168
518.1406 | 121.9208 | -60.7681 | 60.7864 | 1.4211e-13 | -0.012139 | 0.0016923 | 0.062509 | -0.0044998 | 0.057832 | 0.00068675 | -0.0020424 | -0.0028161 | 0.06256 | 0.016449 | 0.059267 | -60.6168 | -0.053537 | -60.7485 | 60.7295 | 60.3918 | 60.433 | -60.7842 | -60.7447 | 0.041567 | -60.857 | 60.5802 | 60.6619 | 60.5277 | -60.9434 | -0.016049 | -0.056936 | 0.15132 | 0.01967 | 0.035719 | -0.39464 | -0.35343 | -0.17524 | -0.20627 | 0.023431 | -0.088912 | 0.086329 | -0.12456 | -0.25872 | 121.4976 | 121.1599 | 121.2011 | 60.7146 | -121.5706 | 121.3483 | 121.43 | 121.2958 | 60.8097 | -121.7298
519.875 | 121.7926 | -60.8643 | 60.8093 | 1.4211e-13 | -0.011711 | 0.0019059 | 0.062936 | -0.0044998 | 0.058046 | 0.0083173 | -0.001615 | -0.0028161 | 0.062347 | 0.016449 | 0.059481 | -60.6168 | -0.058115 | -60.7439 | 60.7387 | 60.3918 | 60.4376 | -60.7796 | -60.7539 | 0.046146 | -60.8616 | 60.5802 | 60.6665 | 60.5277 | -60.9434 | 0.084661 | -0.070667 | 0.24745 | 0.12038 | 0.035718 | -0.41753 | -0.37174 | -0.07911 | -0.22916 | 0.11041 | 0.00264 | 0.08175 | -0.14287 | -0.28161 | 121.6029 | 121.2561 | 121.3018 | 60.8061 | -121.5889 | 121.4444 | 121.5307 | 121.392 | 60.9104 | -121.7527
521.5469 | 121.7926 | -60.8688 | 60.791 | 1.4211e-13 | -0.012139 | 0.0016923 | 0.062722 | -0.0044998 | 0.057832 | -0.0069437 | -0.001615 | -0.0026023 | 0.062347 | 0.016662 | 0.059695 | -60.6122 | -0.048958 | -60.7439 | 60.7432 | 60.3872 | 60.4376 | -60.7842 | -60.7447 | 0.041567 | -60.8662 | 60.571 | 60.6573 | 60.5323 | -60.9434 | 0.084659 | -0.047779 | 0.25661 | 0.12496 | 0.040297 | -0.4038 | -0.35343 | -0.074533 | -0.22001 | 0.12414 | 0.002638 | 0.077171 | -0.13372 | -0.25872 | 121.6121 | 121.2561 | 121.3064 | 60.8199 | -121.5752 | 121.4398 | 121.5261 | 121.4011 | 60.9104 | -121.7344
523.2812 | 121.8613 | -60.7681 | 60.8597 | 1.4211e-13 | -0.011925 | 0.0016923 | 0.062722 | -0.0047134 | 0.057832 | -0.0069437 | -0.0020424 | -0.0028161 | 0.062133 | 0.016662 | 0.059481 | -60.6122 | -0.053537 | -60.7439 | 60.7295 | 60.3872 | 60.4284 | -60.7842 | -60.7493 | 0.046146 | -60.857 | 60.5756 | 60.6619 | 60.5323 | -60.9388 | -0.016049 | -0.13018 | 0.1559 | 0.024248 | 0.040297 | -0.47246 | -0.43126 | -0.17066 | -0.28409 | 0.018852 | -0.088912 | 0.08175 | -0.1978 | -0.32738 | 121.4976 | 121.1553 | 121.1966 | 60.7146 | -121.6439 | 121.3437 | 121.43 | 121.3004 | 60.8143 | -121.7985
525.0156 | 121.7926 | -60.8917 | 60.7956 | 1.4211e-13 | -0.011925 | 0.0012649 | 0.062936 | -0.0047134 | 0.057832 | -0.0069437 | -0.0020424 | -0.0026023 | 0.062347 | 0.016449 | 0.059267 | -60.6168 | -0.062694 | -60.7393 | 60.7341 | 60.3964 | 60.433 | -60.7888 | -60.7493 | 0.041567 | -60.857 | 60.571 | 60.6573 | 60.5369 | -60.9388 | 0.10297 | -0.061513 | 0.27492 | 0.15242 | 0.049454 | -0.39922 | -0.36259 | -0.047065 | -0.22458 | 0.14245 | 0.034685 | 0.08175 | -0.1383 | -0.25872 | 121.6258 | 121.2881 | 121.3247 | 60.829 | -121.5843 | 121.4627 | 121.549 | 121.4286 | 60.9333 | -121.7344
526.7656 | 121.9025 | -60.8322 | 60.7727 | 1.4211e-13 | -0.011925 | 0.0014787 | 0.062722 | -0.0040724 | 0.057618 | 0.00068675 | -0.0018288 | -0.0030297 | 0.061919 | 0.016662 | 0.059267 | -60.6168 | -0.058115 | -60.7393 | 60.7341 | 60.3872 | 60.433 | -60.7842 | -60.7401 | 0.046146 | -60.8616 | 60.571 | 60.6573 | 60.5277 | -60.9342 | 0.048038 | -0.038625 | 0.21541 | 0.092913 | 0.044875 | -0.38549 | -0.3397 | -0.102 | -0.2017 | 0.092097 | -0.029404 | 0.072593 | -0.11541 | -0.24499 | 121.5663 | 121.2194 | 121.2652 | 60.7741 | -121.5569 | 121.4032 | 121.4895 | 121.3599 | 60.8784 | -121.7069
528.5 | 121.7972 | -60.8917 | 60.7956 | 1.4211e-13 | -0.011925 | 0.0014787 | 0.062722 | -0.0042862 | 0.057832 | 0.00068675 | -0.001615 | -0.0028161 | 0.062133 | 0.016662 | 0.059267 | -60.6214 | -0.058115 | -60.7439 | 60.7295 | 60.3826 | 60.4422 | -60.775 | -60.7447 | 0.046146 | -60.857 | 60.5664 | 60.6619 | 60.5323 | -60.9388 | 0.11671 | -0.066091 | 0.27034 | 0.14785 | 0.031139 | -0.41296 | -0.35343 | -0.047065 | -0.22916 | 0.14703 | 0.034685 | 0.08175 | -0.13372 | -0.2633 | 121.6212 | 121.2744 | 121.3339 | 60.8336 | -121.5706 | 121.4582 | 121.5536 | 121.424 | 60.9379 | -121.7344
530.1719 | 121.7789 | -60.8826 | 60.8139 | 1.4211e-13 | -0.012139 | 0.0016923 | 0.062295 | -0.0042862 | 0.057832 | -0.0069437 | -0.002256 | -0.0028161 | 0.062133 | 0.016449 | 0.059267 | -60.6168 | -0.058115 | -60.7485 | 60.7295 | 60.3918 | 60.433 | -60.7842 | -60.7493 | 0.041567 | -60.857 | 60.571 | 60.6527 | 60.5323 | -60.9434 | 0.098392 | -0.084402 | 0.26576 | 0.13411 | 0.035719 | -0.42211 | -0.3809 | -0.0608 | -0.2429 | 0.13329 | 0.025529 | 0.086329 | -0.16119 | -0.28161 | 121.6121 | 121.2744 | 121.3156 | 60.8245 | -121.5981 | 121.4536 | 121.5353 | 121.4149 | 60.9241 | -121.7573
531.9062 | 121.8155 | -60.8826 | 60.791 | 1.4211e-13 | -0.01278 | 0.0014787 | 0.062509 | -0.0047134 | 0.058046 | 0.00068675 | -0.0020424 | -0.0028161 | 0.062133 | 0.016662 | 0.059481 | -60.6168 | -0.048958 | -60.7393 | 60.7387 | 60.3918 | 60.4376 | -60.7888 | -60.7539 | 0.050725 | -60.857 | 60.5802 | 60.6573 | 60.5277 | -60.9388 | 0.093813 | -0.052357 | 0.26576 | 0.14327 | 0.049454 | -0.39922 | -0.35343 | -0.056221 | -0.21085 | 0.12871 | 0.025529 | 0.08175 | -0.13372 | -0.2633 | 121.6212 | 121.2744 | 121.3202 | 60.8336 | -121.5798 | 121.4627 | 121.5399 | 121.4103 | 60.9333 | -121.7298
533.5781 | 121.8933 | -60.8505 | 60.7498 | 1.4211e-13 | -0.012566 | 0.0014787 | 0.062722 | -0.0044998 | 0.057832 | 0.00068675 | -0.0020424 | -0.0032433 | 0.062347 | 0.016876 | 0.059267 | -60.6077 | -0.058115 | -60.7393 | 60.7295 | 60.3918 | 60.4376 | -60.7796 | -60.7401 | 0.036989 | -60.857 | 60.5802 | 60.6527 | 60.5323 | -60.9388 | 0.070928 | -0.020315 | 0.24287 | 0.11122 | 0.040296 | -0.35802 | -0.31223 | -0.088264 | -0.16965 | 0.11041 | -0.006514 | 0.08175 | -0.097099 | -0.21752 | 121.58 | 121.2423 | 121.2881 | 60.7924 | -121.5294 | 121.4307 | 121.5032 | 121.3828 | 60.8875 | -121.6886
535.2969 | 121.9208 | -60.7864 | 60.7819 | 1.4211e-13 | -0.012352 | 0.0014787 | 0.062722 | -0.0042862 | 0.057832 | 0.00068675 | -0.0020424 | -0.0028161 | 0.062133 | 0.016662 | 0.059481 | -60.6168 | -0.058115 | -60.7347 | 60.7341 | 60.3826 | 60.4284 | -60.7842 | -60.7401 | 0.041567 | -60.8616 | 60.5847 | 60.6527 | 60.5323 | -60.9388 | 0.002262 | -0.04778 | 0.16963 | 0.051716 | 0.049454 | -0.39922 | -0.35344 | -0.15235 | -0.19712 | 0.046321 | -0.07518 | 0.077171 | -0.12914 | -0.24956 | 121.5205 | 121.1691 | 121.2149 | 60.7283 | -121.566 | 121.3712 | 121.4392 | 121.3187 | 60.828 | -121.7206
537.0312 | 121.9162 | -60.7864 | 60.8047 | 1.4211e-13 | -0.012352 | 0.0014787 | 0.062509 | -0.0044998 | 0.057832 | -0.0069437 | -0.0020424 | -0.0028161 | 0.061919 | 0.016876 | 0.059054 | -60.6122 | -0.058115 | -60.7439 | 60.7387 | 60.3826 | 60.433 | -60.7796 | -60.7401 | 0.046146 | -60.8616 | 60.5802 | 60.6527 | 60.5369 | -60.9342 | 0.006841 | -0.06609 | 0.17421 | 0.042559 | 0.035718 | -0.42211 | -0.37175 | -0.14777 | -0.22458 | 0.046321 | -0.07518 | 0.072593 | -0.15203 | -0.26787 | 121.5251 | 121.1691 | 121.2194 | 60.7283 | -121.5843 | 121.3666 | 121.4392 | 121.3233 | 60.8326 | -121.739
538.7812 | 121.7834 | -60.91 | 60.8047 | 1.4211e-13 | -0.012352 | 0.0014787 | 0.062509 | -0.0044998 | 0.057832 | -0.014574 | -0.0018288 | -0.0030297 | 0.062133 | 0.016662 | 0.059054 | -60.6168 | -0.053537 | -60.7393 | 60.7387 | 60.3918 | 60.4376 | -60.7842 | -60.7447 | 0.041567 | -60.8616 | 60.5802 | 60.6619 | 60.5277 | -60.9296 | 0.12586 | -0.06609 | 0.29323 | 0.17073 | 0.044875 | -0.41295 | -0.36717 | -0.019598 | -0.22458 | 0.16534 | 0.048416 | 0.068014 | -0.14287 | -0.27703 | 121.6487 | 121.3018 | 121.3476 | 60.8565 | -121.5889 | 121.4902 | 121.5719 | 121.4378 | 60.9516 | -121.7344
540.4531 | 121.7926 | -60.8231 | 60.8643 | 1.4211e-13 | -0.012352 | 0.0014787 | 0.062509 | -0.0040724 | 0.058046 | -0.0069437 | -0.0014014 | -0.0026023 | 0.062133 | 0.016662 | 0.059054 | -60.6168 | -0.062694 | -60.7347 | 60.7341 | 60.3918 | 60.433 | -60.7933 | -60.7493 | 0.046146 | -60.8616 | 60.5756 | 60.6527 | 60.5323 | -60.9388 | 0.029726 | -0.13018 | 0.20625 | 0.088337 | 0.058611 | -0.47246 | -0.43125 | -0.11573 | -0.28867 | 0.073784 | -0.038559 | 0.077171 | -0.21154 | -0.33196 | 121.5571 | 121.2149 | 121.2561 | 60.7604 | -121.6576 | 121.3986 | 121.4758 | 121.3554 | 60.8692 | -121.803
542.2031 | 121.7926 | -60.8917 | 60.7636 | 1.4211e-13 | -0.012139 | 0.0012649 | 0.062509 | -0.0042862 | 0.057618 | 0.0083173 | -0.0020424 | -0.0028161 | 0.062133 | 0.016876 | 0.059054 | -60.6077 | -0.058115 | -60.7439 | 60.7341 | 60.3918 | 60.433 | -60.7796 | -60.7401 | 0.046146 | -60.857 | 60.5802 | 60.6527 | 60.5277 | -60.9296 | 0.11213 | -0.02947 | 0.28407 | 0.14785 | 0.035718 | -0.37176 | -0.33055 | -0.037908 | -0.18339 | 0.15161 | 0.034685 | 0.072593 | -0.11083 | -0.23583 | 121.6258 | 121.2835 | 121.3247 | 60.8336 | -121.5431 | 121.4719 | 121.5444 | 121.4194 | 60.9379 | -121.6932
543.9375 | 121.7789 | -60.8276 | 60.8597 | 1.4211e-13 | -0.012566 | 0.0012649 | 0.062509 | -0.0042862 | 0.057618 | -0.0069437 | -0.001615 | -0.0030297 | 0.062133 | 0.016876 | 0.059695 | -60.6031 | -0.058115 | -60.7393 | 60.7295 | 60.3872 | 60.4376 | -60.7842 | -60.7447 | 0.036989 | -60.8616 | 60.5756 | 60.6527 | 60.5277 | -60.9342 | 0.043461 | -0.13018 | 0.22456 | 0.088336 | 0.044875 | -0.47246 | -0.4221 | -0.10657 | -0.28409 | 0.082941 | -0.033981 | 0.072593 | -0.20696 | -0.33196 | 121.5571 | 121.2149 | 121.2652 | 60.7695 | -121.6439 | 121.4032 | 121.4804 | 121.3554 | 60.8646 | -121.7939
545.6719 | 121.8796 | -60.8505 | 60.7269 | 1.4211e-13 | -0.01278 | 0.0016923 | 0.062936 | -0.0044998 | 0.057832 | 0.015947 | -0.0018288 | -0.0026023 | 0.062347 | 0.016662 | 0.059695 | -60.6168 | -0.053537 | -60.7439 | 60.7387 | 60.3872 | 60.4422 | -60.7796 | -60.7401 | 0.041567 | -60.8479 | 60.5756 | 60.6527 | 60.5277 | -60.9296 | 0.070928 | 0.01173 | 0.23372 | 0.10665 | 0.035718 | -0.33971 | -0.28477 | -0.079107 | -0.15134 | 0.11041 | 0.002643 | 0.08175 | -0.074211 | -0.19921 | 121.5892 | 121.2377 | 121.2927 | 60.797 | -121.5065 | 121.4261 | 121.5032 | 121.3782 | 60.8921 | -121.6566
547.3438 | 121.9208 | -60.7636 | 60.8002 | 1.4211e-13 | -0.012352 | 0.0016923 | 0.062295 | -0.0042862 | 0.057618 | -0.0069437 | -0.0018288 | -0.0028161 | 0.062133 | 0.016662 | 0.059267 | -60.6168 | -0.062694 | -60.7347 | 60.7295 | 60.3826 | 60.4376 | -60.7888 | -60.7447 | 0.041567 | -60.8525 | 60.5756 | 60.6527 | 60.5277 | -60.9342 | -0.025205 | -0.070669 | 0.14674 | 0.028828 | 0.054033 | -0.41753 | -0.36259 | -0.17066 | -0.22458 | 0.018854 | -0.088911 | 0.08175 | -0.14745 | -0.27245 | 121.4931 | 121.1462 | 121.2011 | 60.7009 | -121.5889 | 121.3391 | 121.4163 | 121.2913 | 60.8051 | -121.7344
549.0781 | 121.843 | -60.791 | 60.8414 | 1.4211e-13 | -0.012566 | 0.0014787 | 0.062509 | -0.0047134 | 0.057832 | 0.0083173 | -0.002256 | -0.0028161 | 0.062347 | 0.016876 | 0.059054 | -60.6077 | -0.062694 | -60.7256 | 60.7341 | 60.3872 | 60.433 | -60.775 | -60.7401 | 0.041567 | -60.8616 | 60.5756 | 60.6619 | 60.5231 | -60.9388 | 0.015998 | -0.10729 | 0.18337 | 0.06545 | 0.049452 | -0.45415 | -0.40837 | -0.14777 | -0.26578 | 0.050899 | -0.070602 | 0.077171 | -0.17949 | -0.31823 | 121.5251 | 121.1782 | 121.224 | 60.7283 | -121.6164 | 121.3666 | 121.4529 | 121.3142 | 60.8326 | -121.7802
550.8281 | 121.7651 | -60.8597 | 60.8002 | 1.4211e-13 | -0.012352 | 0.0014787 | 0.062722 | -0.0042862 | 0.057832 | 0.00068675 | -0.0020424 | -0.0026023 | 0.061919 | 0.016662 | 0.059481 | -60.6214 | -0.062694 | -60.7301 | 60.7341 | 60.3918 | 60.4376 | -60.7933 | -60.7401 | 0.036989 | -60.857 | 60.571 | 60.6573 | 60.5277 | -60.9296 | 0.066347 | -0.066091 | 0.23829 | 0.12954 | 0.063189 | -0.40838 | -0.36259 | -0.069952 | -0.22916 | 0.11956 | 0.002641 | 0.072593 | -0.14287 | -0.27245 | 121.5938 | 121.2515 | 121.2973 | 60.797 | -121.5935 | 121.4307 | 121.517 | 121.3874 | 60.8967 | -121.7298
552.5 | 121.7926 | -60.8047 | 60.8414 | 1.4211e-13 | -0.012566 | 0.0016923 | 0.062509 | -0.0042862 | 0.057618 | -0.0069437 | -0.0018288 | -0.0030297 | 0.061919 | 0.017303 | 0.059695 | -60.6122 | -0.067272 | -60.7347 | 60.7341 | 60.3918 | 60.4376 | -60.7888 | -60.7447 | 0.041567 | -60.8479 | 60.5756 | 60.6619 | 60.5277 | -60.9296 | 0.015994 | -0.10729 | 0.19252 | 0.070027 | 0.054033 | -0.44957 | -0.40379 | -0.12488 | -0.26578 | 0.060053 | -0.043133 | 0.08175 | -0.17949 | -0.31365 | 121.5388 | 121.1965 | 121.2423 | 60.7375 | -121.6301 | 121.3803 | 121.4666 | 121.3325 | 60.8463 | -121.771
554.2344 | 121.7926 | -60.8826 | 60.7773 | 1.4211e-13 | -0.012352 | 0.0014787 | 0.062722 | -0.0042862 | 0.057618 | 0.0083173 | -0.0018288 | -0.0030297 | 0.062347 | 0.017517 | 0.059267 | -60.6122 | -0.062694 | -60.7301 | 60.7341 | 60.3964 | 60.4422 | -60.7842 | -60.7493 | 0.036989 | -60.8479 | 60.571 | 60.6619 | 60.5231 | -60.9296 | 0.098392 | -0.043203 | 0.27034 | 0.15242 | 0.054032 | -0.38091 | -0.33512 | -0.047064 | -0.20627 | 0.13329 | 0.034686 | 0.08175 | -0.11541 | -0.25414 | 121.6166 | 121.2789 | 121.3247 | 60.8199 | -121.5615 | 121.4536 | 121.5444 | 121.4057 | 60.9196 | -121.7069
555.9844 | 121.8796 | -60.8597 | 60.7269 | 1.4211e-13 | -0.012566 | 0.0010513 | 0.062722 | -0.0044998 | 0.057832 | 0.0083173 | -0.0020424 | -0.0026023 | 0.062133 | 0.01709 | 0.059054 | -60.6031 | -0.053537 | -60.7256 | 60.7295 | 60.3918 | 60.433 | -60.7796 | -60.7401 | 0.046146 | -60.8525 | 60.5756 | 60.6619 | 60.5231 | -60.9342 | 0.080083 | 0.002573 | 0.25661 | 0.13411 | 0.054031 | -0.33513 | -0.29393 | -0.074531 | -0.15134 | 0.11956 | 0.007219 | 0.08175 | -0.065054 | -0.20379 | 121.5892 | 121.2515 | 121.2927 | 60.8061 | -121.5065 | 121.4353 | 121.5216 | 121.3828 | 60.9058 | -121.6611
557.7188 | 121.7834 | -60.8643 | 60.7864 | 1.4211e-13 | -0.012566 | 0.0014787 | 0.062509 | -0.0044998 | 0.057618 | 0.00068675 | -0.0020424 | -0.0028161 | 0.062133 | 0.01709 | 0.059481 | -60.5985 | -0.062694 | -60.7301 | 60.7295 | 60.3872 | 60.4422 | -60.7796 | -60.7355 | 0.041567 | -60.8525 | 60.571 | 60.6527 | 60.5277 | -60.9342 | 0.084661 | -0.056936 | 0.26576 | 0.13411 | 0.049453 | -0.39922 | -0.34428 | -0.069953 | -0.21543 | 0.12872 | 0.011797 | 0.08175 | -0.13372 | -0.25872 | 121.5938 | 121.2515 | 121.3064 | 60.8016 | -121.566 | 121.4353 | 121.517 | 121.392 | 60.9058 | -121.7206
559.375 | 121.9162 | -60.7727 | 60.8093 | 1.4211e-13 | -0.012566 | 0.0014787 | 0.062722 | -0.0047134 | 0.057832 | -0.0069437 | -0.0018288 | -0.0030297 | 0.061919 | 0.01709 | 0.059054 | -60.6077 | -0.062694 | -60.7256 | 60.7295 | 60.3872 | 60.4376 | -60.7842 | -60.7401 | 0.036989 | -60.8525 | 60.571 | 60.6619 | 60.5277 | -60.9205 | -0.011471 | -0.079824 | 0.16505 | 0.047139 | 0.05861 | -0.42211 | -0.37174 | -0.14777 | -0.23832 | 0.032588 | -0.079756 | 0.068013 | -0.14745 | -0.28161 | 121.5022 | 121.1599 | 121.2103 | 60.71 | -121.5935 | 121.3437 | 121.4346 | 121.3004 | 60.8097 | -121.7298
561.1094 | 121.8933 | -60.791 | 60.7956 | 1.4211e-13 | -0.012566 | 0.0012649 | 0.062722 | -0.0042862 | 0.057618 | -0.0069437 | -0.0020424 | -0.0028161 | 0.062133 | 0.016876 | 0.059481 | -60.6031 | -0.058115 | -60.7256 | 60.7295 | 60.3918 | 60.4376 | -60.775 | -60.7355 | 0.046146 | -60.8479 | 60.5802 | 60.6665 | 60.5231 | -60.9251 | 0.015998 | -0.066091 | 0.18794 | 0.06545 | 0.049452 | -0.4038 | -0.35801 | -0.13404 | -0.21543 | 0.055477 | -0.056866 | 0.077171 | -0.12914 | -0.27245 | 121.5205 | 121.1828 | 121.2286 | 60.7329 | -121.5706 | 121.3712 | 121.4575 | 121.3142 | 60.8372 | -121.7206
562.8281 | 121.7789 | -60.791 | 60.878 | 1.4211e-13 | -0.01278 | 0.0014787 | 0.062509 | -0.0044998 | 0.057832 | -0.0069437 | -0.0018288 | -0.0026023 | 0.061706 | 0.016876 | 0.059267 | -60.6031 | -0.062694 | -60.7301 | 60.7295 | 60.3964 | 60.4376 | -60.7888 | -60.731 | 0.046146 | -60.8479 | 60.5756 | 60.6619 | 60.5277 | -60.9251 | 0.002261 | -0.14849 | 0.18794 | 0.060872 | 0.058611 | -0.48162 | -0.44041 | -0.13404 | -0.30241 | 0.060056 | -0.056866 | 0.077171 | -0.21612 | -0.35027 | 121.5205 | 121.1874 | 121.2286 | 60.7283 | -121.6667 | 121.3666 | 121.4529 | 121.3187 | 60.8372 | -121.803
564.5 | 121.8842 | -60.7681 | 60.7864 | 1.4211e-13 | -0.01278 | 0.0019059 | 0.062722 | -0.0044998 | 0.057832 | -0.0069437 | -0.002256 | -0.0026023 | 0.062133 | 0.017303 | 0.059267 | -60.6077 | -0.067272 | -60.7347 | 60.7295 | 60.3918 | 60.4376 | -60.7796 | -60.7355 | 0.050725 | -60.8479 | 60.5802 | 60.6619 | 60.5186 | -60.9205 | -0.01147 | -0.056936 | 0.16048 | 0.033405 | 0.044875 | -0.39464 | -0.34886 | -0.15235 | -0.20627 | 0.032588 | -0.079755 | 0.072592 | -0.12456 | -0.26788 | 121.4976 | 121.1599 | 121.2057 | 60.7009 | -121.566 | 121.3483 | 121.43 | 121.2867 | 60.8189 | -121.7069
566.25 | 121.7606 | -60.8917 | 60.791 | 1.4211e-13 | -0.01278 | 0.0014787 | 0.062509 | -0.0044998 | 0.057405 | 0.00068675 | -0.0020424 | -0.0028161 | 0.062133 | 0.016876 | 0.059267 | -60.6031 | -0.062694 | -60.7301 | 60.7387 | 60.3964 | 60.4422 | -60.7796 | -60.731 | 0.041567 | -60.8479 | 60.5756 | 60.6665 | 60.5277 | -60.9251 | 0.11213 | -0.052357 | 0.28865 | 0.16158 | 0.049453 | -0.39464 | -0.34886 | -0.033329 | -0.21543 | 0.16076 | 0.043842 | 0.077171 | -0.12456 | -0.2633 | 121.6304 | 121.2881 | 121.3339 | 60.829 | -121.5706 | 121.4673 | 121.5582 | 121.4194 | 60.9333 | -121.7161
567.9219 | 121.788 | -60.8093 | 60.8734 | 1.4211e-13 | -0.013207 | 0.0010513 | 0.062722 | -0.0044998 | 0.057405 | -0.0069437 | -0.0020424 | -0.0026023 | 0.061919 | 0.017517 | 0.059267 | -60.6031 | -0.067272 | -60.7347 | 60.7341 | 60.3918 | 60.433 | -60.7842 | -60.7401 | 0.036989 | -60.8479 | 60.5802 | 60.6665 | 60.5323 | -60.9251 | 0.02515 | -0.13933 | 0.20625 | 0.074604 | 0.049454 | -0.48162 | -0.44041 | -0.11573 | -0.29325 | 0.069209 | -0.038556 | 0.077171 | -0.20696 | -0.34112 | 121.5434 | 121.2011 | 121.2423 | 60.7421 | -121.6576 | 121.3895 | 121.4758 | 121.3416 | 60.8463 | -121.7985
569.6562 | 121.8109 | -60.8459 | 60.8185 | 1.4211e-13 | -0.012566 | 0.0014787 | 0.062722 | -0.0047134 | 0.057832 | 0.00068675 | -0.0020424 | -0.0026023 | 0.062133 | 0.017303 | 0.059054 | -60.5985 | -0.067272 | -60.7256 | 60.7341 | 60.3918 | 60.4376 | -60.7704 | -60.731 | 0.041567 | -60.8479 | 60.5847 | 60.6619 | 60.5369 | -60.9296 | 0.075508 | -0.084401 | 0.24745 | 0.12038 | 0.044873 | -0.42669 | -0.3809 | -0.083685 | -0.23374 | 0.11499 | -0.001935 | 0.08175 | -0.15661 | -0.2816 | 121.58 | 121.2377 | 121.2835 | 60.7787 | -121.5889 | 121.4307 | 121.5078 | 121.3828 | 60.8875 | -121.7481
571.4219 | 121.9208 | -60.7544 | 60.8002 | 1.4211e-13 | -0.012993 | 0.0016923 | 0.062509 | -0.0047134 | 0.057405 | 0.0083173 | -0.0020424 | -0.0026023 | 0.062133 | 0.01709 | 0.059481 | -60.6031 | -0.067272 | -60.7301 | 60.7295 | 60.3918 | 60.433 | -60.7796 | -60.7355 | 0.036989 | -60.8525 | 60.571 | 60.6619 | 60.5277 | -60.9251 | -0.025202 | -0.070669 | 0.15132 | 0.024251 | 0.049453 | -0.40838 | -0.36717 | -0.17066 | -0.22916 | 0.018856 | -0.098066 | 0.072592 | -0.1383 | -0.27245 | 121.4839 | 121.1462 | 121.1874 | 60.6871 | -121.5798 | 121.3254 | 121.4163 | 121.2821 | 60.7914 | -121.7252
573.0938 | 121.8338 | -60.8231 | 60.8185 | 1.4211e-13 | -0.013421 | 0.0010513 | 0.062722 | -0.0047134 | 0.057405 | -0.0069437 | -0.002256 | -0.0026023 | 0.061919 | 0.017517 | 0.059267 | -60.6031 | -0.062694 | -60.7347 | 60.7341 | 60.401 | 60.4422 | -60.775 | -60.7355 | 0.041567 | -60.8525 | 60.571 | 60.6573 | 60.5369 | -60.9251 | 0.048041 | -0.084401 | 0.21999 | 0.088337 | 0.040296 | -0.41753 | -0.37632 | -0.10199 | -0.24747 | 0.08752 | -0.029402 | 0.072592 | -0.16118 | -0.2816 | 121.5571 | 121.224 | 121.2652 | 60.7604 | -121.5935 | 121.3941 | 121.4804 | 121.3599 | 60.8646 | -121.7435
574.8281 | 121.8842 | -60.8093 | 60.7864 | 1.4211e-13 | -0.012993 | 0.0014787 | 0.062509 | -0.0042862 | 0.057618 | 0.00068675 | -0.0020424 | -0.0028161 | 0.061919 | 0.01709 | 0.059267 | -60.6031 | -0.071851 | -60.721 | 60.7341 | 60.3964 | 60.4376 | -60.775 | -60.731 | 0.046146 | -60.8387 | 60.571 | 60.6573 | 60.5369 | -60.9205 | 0.034308 | -0.052358 | 0.20625 | 0.088338 | 0.05403 | -0.39006 | -0.34886 | -0.11115 | -0.21543 | 0.078366 | -0.029398 | 0.08175 | -0.12914 | -0.24956 | 121.5434 | 121.2057 | 121.2469 | 60.7375 | -121.5615 | 121.3803 | 121.4666 | 121.3462 | 60.8555 | -121.7069
576.5 | 121.7743 | -60.8139 | 60.8459 | 1.4211e-13 | -0.013421 | 0.0014787 | 0.062509 | -0.0044998 | 0.057405 | -0.014574 | -0.0020424 | -0.0026023 | 0.062133 | 0.01709 | 0.059267 | -60.6031 | -0.071851 | -60.7256 | 60.7295 | 60.3872 | 60.433 | -60.7704 | -60.731 | 0.03241 | -60.8433 | 60.571 | 60.6619 | 60.5231 | -60.9205 | 0.043465 | -0.11645 | 0.21083 | 0.088338 | 0.044873 | -0.45873 | -0.41294 | -0.10657 | -0.27494 | 0.082944 | -0.029399 | 0.077171 | -0.18407 | -0.32281 | 121.5434 | 121.2011 | 121.2469 | 60.7421 | -121.6164 | 121.3849 | 121.4758 | 121.337 | 60.8463 | -121.7664
578.2344 | 121.8796 | -60.8139 | 60.8002 | 1.4211e-13 | -0.013635 | 0.0014787 | 0.062936 | -0.0051408 | 0.057832 | -0.0069437 | -0.001615 | -0.0028161 | 0.062133 | 0.017303 | 0.059054 | -60.6077 | -0.067272 | -60.721 | 60.7249 | 60.3826 | 60.4376 | -60.7796 | -60.7264 | 0.050725 | -60.8479 | 60.5756 | 60.6527 | 60.5277 | -60.9251 | 0.034307 | -0.075247 | 0.20625 | 0.092916 | 0.058609 | -0.41753 | -0.36259 | -0.11115 | -0.22458 | 0.087523 | -0.033978 | 0.077171 | -0.14745 | -0.27245 | 121.5388 | 121.1965 | 121.2515 | 60.7466 | -121.5798 | 121.3895 | 121.4666 | 121.3416 | 60.8646 | -121.7252
579.9062 | 121.875 | -60.8322 | 60.759 | 1.4211e-13 | -0.013207 | 0.0014787 | 0.062722 | -0.0047134 | 0.057405 | 0.00068675 | -0.0020424 | -0.0026023 | 0.061706 | 0.01709 | 0.059481 | -60.5985 | -0.062694 | -60.7301 | 60.7249 | 60.3918 | 60.4376 | -60.7796 | -60.7401 | 0.041567 | -60.8433 | 60.571 | 60.6481 | 60.5186 | -60.9205 | 0.052617 | -0.034048 | 0.23372 | 0.10207 | 0.049453 | -0.36718 | -0.32139 | -0.08826 | -0.18796 | 0.092097 | -0.011089 | 0.077171 | -0.11083 | -0.24041 | 121.5571 | 121.224 | 121.2698 | 60.7695 | -121.5386 | 121.4032 | 121.4804 | 121.3508 | 60.8738 | -121.6794
581.6406 | 121.8201 | -60.8276 | 60.7819 | 1.4211e-13 | -0.012993 | 0.0010513 | 0.062722 | -0.0044998 | 0.057405 | -0.014574 | -0.0018288 | -0.0026023 | 0.062133 | 0.017303 | 0.059267 | -60.6077 | -0.067272 | -60.7393 | 60.7249 | 60.3918 | 60.4284 | -60.7842 | -60.7401 | 0.041567 | -60.8479 | 60.5619 | 60.6481 | 60.5277 | -60.9342 | 0.043461 | -0.056936 | 0.21999 | 0.088336 | 0.044875 | -0.39006 | -0.35344 | -0.10657 | -0.22001 | 0.08752 | -0.020245 | 0.086329 | -0.13372 | -0.25414 | 121.5526 | 121.2194 | 121.2561 | 60.7604 | -121.566 | 121.3895 | 121.4758 | 121.3554 | 60.8692 | -121.7161
583.375 | 121.8658 | -60.8368 | 60.7498 | 1.4211e-13 | -0.013421 | 0.0012649 | 0.062722 | -0.004927 | 0.057618 | -0.0069437 | -0.0018288 | -0.0028161 | 0.062133 | 0.017303 | 0.059267 | -60.6122 | -0.067272 | -60.7393 | 60.7249 | 60.3735 | 60.4284 | -60.7888 | -60.7447 | 0.041567 | -60.857 | 60.5664 | 60.6481 | 60.514 | -60.9434 | 0.048037 | -0.024893 | 0.22456 | 0.097491 | 0.049454 | -0.37634 | -0.32139 | -0.10658 | -0.18339 | 0.092096 | -0.020247 | 0.086329 | -0.10168 | -0.23583 | 121.5617 | 121.2103 | 121.2652 | 60.7695 | -121.5386 | 121.4032 | 121.4849 | 121.3508 | 60.8784 | -121.6932
585.0938 | 121.9254 | -60.791 | 60.7727 | 1.4211e-13 | -0.013207 | 0.0019059 | 0.062509 | -0.0044998 | 0.056977 | 0.00068675 | -0.002256 | -0.0028161 | 0.061919 | 0.017517 | 0.059054 | -60.6168 | -0.07643 | -60.7576 | 60.7066 | 60.3735 | 60.4147 | -60.7979 | -60.7539 | 0.041567 | -60.8708 | 60.5527 | 60.639 | 60.5048 | -60.9388 | -0.006896 | -0.066095 | 0.17421 | 0.033402 | 0.040298 | -0.39923 | -0.35802 | -0.14777 | -0.22001 | 0.037163 | -0.079759 | 0.068014 | -0.13372 | -0.26788 | 121.4976 | 121.1645 | 121.2057 | 60.7146 | -121.5706 | 121.3437 | 121.43 | 121.2958 | 60.8326 | -121.7115
586.8438 | 121.8155 | -60.8643 | 60.7636 | 1.4211e-13 | -0.013421 | 0.0014787 | 0.062295 | -0.0044998 | 0.057618 | -0.014574 | -0.002256 | -0.0028161 | 0.062133 | 0.017517 | 0.059481 | -60.6397 | -0.07643 | -60.7576 | 60.702 | 60.3643 | 60.401 | -60.8162 | -60.763 | 0.046146 | -60.8754 | 60.539 | 60.6344 | 60.5002 | -60.9617 | 0.04803 | -0.061518 | 0.22456 | 0.10664 | 0.058614 | -0.39923 | -0.3626 | -0.097425 | -0.22459 | 0.10125 | -0.011096 | 0.086329 | -0.12915 | -0.2633 | 121.5663 | 121.2286 | 121.2652 | 60.7878 | -121.5798 | 121.4032 | 121.4987 | 121.3645 | 60.9104 | -121.7252
588.5156 | 121.8338 | -60.8734 | 60.7681 | 1.4211e-13 | -0.01278 | 0.0014787 | 0.062295 | -0.004927 | 0.057405 | -0.0069437 | -0.0018288 | -0.0030297 | 0.061919 | 0.017731 | 0.059054 | -60.6534 | -0.071851 | -60.7668 | 60.6837 | 60.3414 | 60.3918 | -60.8254 | -60.7813 | 0.041567 | -60.8937 | 60.5206 | 60.6024 | 60.4819 | -60.9754 | 0.048027 | -0.084409 | 0.21998 | 0.10664 | 0.058616 | -0.4267 | -0.37633 | -0.10201 | -0.24748 | 0.092087 | -0.020256 | 0.081751 | -0.16577 | -0.28619 | 121.5571 | 121.2148 | 121.2652 | 60.8016 | -121.5935 | 121.3941 | 121.4758 | 121.3553 | 60.915 | -121.7435
590.25 | 121.7651 | -60.9558 | 60.704 | 1.4211e-13 | -0.013421 | 0.0016923 | 0.062295 | -0.0047134 | 0.057832 | -0.0069437 | -0.002256 | -0.0028161 | 0.062133 | 0.017303 | 0.059267 | -60.6717 | -0.071851 | -60.7897 | 60.6471 | 60.3185 | 60.3689 | -60.8437 | -60.8042 | 0.036989 | -60.9257 | 60.5023 | 60.5886 | 60.459 | -60.9937 | 0.11211 | -0.05695 | 0.28406 | 0.16615 | 0.05404 | -0.38551 | -0.33514 | -0.037924 | -0.20171 | 0.15159 | 0.030091 | 0.068015 | -0.11542 | -0.245 | 121.6029 | 121.2743 | 121.3247 | 60.884 | -121.5477 | 121.4581 | 121.5444 | 121.4149 | 60.9928 | -121.6978
592 | 121.7743 | -60.9833 | 60.6903 | 1.4211e-13 | -0.013635 | 0.0012649 | 0.062722 | -0.0044998 | 0.057618 | 0.00068675 | -0.002256 | -0.0026023 | 0.062133 | 0.017303 | 0.059267 | -60.7084 | -0.081008 | -60.8263 | 60.6334 | 60.2956 | 60.3323 | -60.8803 | -60.8408 | 0.041567 | -60.944 | 60.4703 | 60.5566 | 60.4224 | -61.0304 | 0.10294 | -0.056952 | 0.2749 | 0.15699 | 0.054045 | -0.39467 | -0.35803 | -0.04709 | -0.22003 | 0.14243 | 0.039241 | 0.086331 | -0.13374 | -0.2679 | 121.6166 | 121.2789 | 121.3156 | 60.9023 | -121.5706 | 121.4536 | 121.5398 | 121.4057 | 61.0248 | -121.7207
593.75 | 121.7697 | -60.9879 | 60.64 | 1.4211e-13 | -0.013207 | 0.0014787 | 0.062081 | -0.004927 | 0.057618 | 0.00068675 | -0.002256 | -0.0028161 | 0.061919 | 0.017517 | 0.059267 | -60.7404 | -0.071851 | -60.8721 | 60.5921 | 60.2453 | 60.2865 | -60.9261 | -60.8821 | 0.041567 | -60.9898 | 60.4245 | 60.5108 | 60.3766 | -61.067 | 0.061732 | -0.047804 | 0.24743 | 0.11578 | 0.054051 | -0.39469 | -0.35346 | -0.079142 | -0.21546 | 0.1058 | -0.001968 | 0.077174 | -0.12917 | -0.26333 | 121.58 | 121.2331 | 121.2743 | 60.916 | -121.5661 | 121.4124 | 121.4986 | 121.3645 | 61.0294 | -121.707
595.4844 | 121.8475 | -61.0107 | 60.5804 | 1.4211e-13 | -0.013421 | 0.0012649 | 0.062081 | -0.0044998 | 0.057618 | -0.0069437 | -0.0020424 | -0.0026023 | 0.061919 | 0.017303 | 0.059267 | -60.7954 | -0.07643 | -60.9133 | 60.5235 | 60.1903 | 60.2315 | -60.9719 | -60.9324 | 0.036989 | -61.0493 | 60.365 | 60.4558 | 60.3263 | -61.1265 | 0.03883 | -0.056969 | 0.21538 | 0.097467 | 0.058637 | -0.39012 | -0.3489 | -0.11578 | -0.21547 | 0.078319 | -0.038603 | 0.077176 | -0.12461 | -0.25418 | 121.5342 | 121.2011 | 121.2423 | 60.9343 | -121.5524 | 121.3757 | 121.4666 | 121.337 | 61.0477 | -121.707
597.1719 | 121.8613 | -61.0931 | 60.5072 | 1.4211e-13 | -0.013421 | 0.0016923 | 0.062081 | -0.0047134 | 0.057618 | 0.00068675 | -0.0020424 | -0.0030297 | 0.061706 | 0.017731 | 0.059054 | -60.8595 | -0.081008 | -60.9774 | 60.464 | 60.1262 | 60.1766 | -61.0314 | -60.9874 | 0.041567 | -61.1043 | 60.3055 | 60.3872 | 60.2622 | -61.1769 | 0.061702 | -0.043246 | 0.23368 | 0.11577 | 0.054067 | -0.38099 | -0.3306 | -0.083748 | -0.20175 | 0.10577 | -0.01115 | 0.072598 | -0.12004 | -0.24504 | 121.5571 | 121.2194 | 121.2697 | 61.0121 | -121.5386 | 121.3986 | 121.4803 | 121.3553 | 61.1347 | -121.6841
598.9062 | 121.8201 | -61.1069 | 60.4889 | 1.4211e-13 | -0.013635 | 0.0012649 | 0.062295 | -0.0047134 | 0.057405 | -0.0069437 | -0.0018288 | -0.0028161 | 0.061706 | 0.017303 | 0.059267 | -60.9373 | -0.094744 | -61.0552 | 60.3815 | 60.0392 | 60.0988 | -61.1139 | -61.0698 | 0.036989 | -61.1867 | 60.2322 | 60.3139 | 60.1889 | -61.273 | -0.006985 | -0.10735 | 0.16958 | 0.051671 | 0.058656 | -0.44967 | -0.39013 | -0.16617 | -0.25669 | 0.037089 | -0.079833 | 0.086337 | -0.17499 | -0.29999 | 121.4884 | 121.1461 | 121.2056 | 61.0121 | -121.6028 | 121.3391 | 121.4208 | 121.2958 | 61.1439 | -121.7619
600.5781 | 121.8384 | -61.2534 | 60.3241 | 1.4211e-13 | -0.013848 | 0.0014787 | 0.061868 | -0.004927 | 0.057832 | 0.00068675 | -0.0018288 | -0.0028161 | 0.062133 | 0.017731 | 0.059054 | -61.0426 | -0.081008 | -61.1651 | 60.2808 | 59.9431 | 59.9935 | -61.2238 | -61.1705 | 0.036989 | -61.292 | 60.1223 | 60.204 | 60.0836 | -61.3692 | 0.029605 | -0.043277 | 0.21076 | 0.088276 | 0.058671 | -0.38104 | -0.33064 | -0.11584 | -0.20178 | 0.082841 | -0.03866 | 0.077181 | -0.12008 | -0.2405 | 121.5342 | 121.1964 | 121.2468 | 61.1723 | -121.5478 | 121.3757 | 121.4574 | 121.337 | 61.2903 | -121.6933
602.3281 | 121.9345 | -61.3495 | 60.228 | 1.4211e-13 | -0.013635 | 0.0016923 | 0.062295 | -0.0044998 | 0.057618 | -0.014574 | -0.002256 | -0.0030297 | 0.061706 | 0.017517 | 0.059054 | -61.1754 | -0.085587 | -61.2933 | 60.1572 | 59.8103 | 59.8561 | -61.3474 | -61.3033 | 0.041567 | -61.4248 | 59.9987 | 60.0804 | 59.9508 | -61.502 | 0.002104 | -0.070762 | 0.17412 | 0.056214 | 0.05411 | -0.4177 | -0.37187 | -0.1525 | -0.22927 | 0.046188 | -0.075312 | 0.077185 | -0.14757 | -0.27715 | 121.5067 | 121.1598 | 121.2056 | 61.2639 | -121.5753 | 121.3482 | 121.4299 | 121.3003 | 61.3911 | -121.73
604.0625 | 121.7514 | -61.6104 | 60.0357 | 1.4211e-13 | -0.013635 | 0.0012649 | 0.062295 | -0.0047134 | 0.057405 | 0.0083173 | -0.002256 | -0.0026023 | 0.061492 | 0.017303 | 0.059054 | -61.3219 | -0.090166 | -61.4444 | 59.9878 | 59.6546 | 59.7142 | -61.5076 | -61.4544 | 0.041567 | -61.5713 | 59.843 | 59.911 | 59.7906 | -61.6622 | 0.10277 | -0.047903 | 0.28853 | 0.16606 | 0.06329 | -0.38112 | -0.32154 | -0.05183 | -0.19268 | 0.15602 | 0.039095 | 0.090925 | -0.12472 | -0.24514 | 121.5982 | 121.265 | 121.3246 | 61.5202 | -121.5434 | 121.4534 | 121.5214 | 121.401 | 61.652 | -121.6979
605.7969 | 121.9025 | -61.6882 | 59.8755 | 1.4211e-13 | -0.013635 | 0.0014787 | 0.061868 | -0.0047134 | 0.057618 | 0.0083173 | -0.002256 | -0.0028161 | 0.061706 | 0.017517 | 0.059481 | -61.505 | -0.090166 | -61.6275 | 59.8092 | 59.4806 | 59.5264 | -61.6862 | -61.633 | 0.03241 | -61.7499 | 59.6645 | 59.7462 | 59.6257 | -61.8317 | 0.002008 | -0.066242 | 0.18322 | 0.060745 | 0.058737 | -0.3949 | -0.34905 | -0.14343 | -0.21102 | 0.055266 | -0.061656 | 0.081771 | -0.12933 | -0.24975 | 121.4975 | 121.1688 | 121.2147 | 61.5981 | -121.5617 | 121.3527 | 121.4344 | 121.314 | 61.7206 | -121.7071
607.4688 | 121.8475 | -61.9263 | 59.6329 | 1.4211e-13 | -0.013421 | 0.0012649 | 0.061868 | -0.0047134 | 0.057191 | -0.0069437 | -0.0020424 | -0.0030297 | 0.061706 | 0.017517 | 0.059267 | -61.7019 | -0.094744 | -61.8244 | 59.6124 | 59.27 | 59.325 | -61.8877 | -61.8299 | 0.03241 | -61.9376 | 59.4584 | 59.5401 | 59.4151 | -62.0331 | 0.038574 | -0.020499 | 0.22438 | 0.10192 | 0.063343 | -0.36292 | -0.30789 | -0.10686 | -0.17444 | 0.09642 | -0.011345 | 0.095512 | -0.092756 | -0.21776 | 121.5386 | 121.1962 | 121.2513 | 61.8315 | -121.5206 | 121.3847 | 121.4664 | 121.3414 | 61.9587 | -121.666
609.2031 | 121.9116 | -62.1918 | 59.3903 | 1.4211e-13 | -0.013635 | 0.0014787 | 0.061868 | -0.004927 | 0.057618 | 0.00068675 | -0.0020424 | -0.0026023 | 0.062347 | 0.017944 | 0.059267 | -61.972 | -0.10848 | -62.099 | 59.3285 | 58.9952 | 59.0503 | -62.1624 | -62.1092 | 0.036989 | -62.2261 | 59.1837 | 59.2654 | 59.1358 | -62.317 | 0.02934 | -0.061744 | 0.21976 | 0.092722 | 0.063382 | -0.39504 | -0.33999 | -0.12524 | -0.20654 | 0.08262 | -0.034301 | 0.09094 | -0.12486 | -0.25444 | 121.5203 | 121.187 | 121.242 | 62.0833 | -121.5527 | 121.3755 | 121.4572 | 121.3276 | 62.2288 | -121.7073
610.9375 | 121.9025 | -62.4664 | 59.1064 | 1.4211e-13 | -0.013635 | 0.0016923 | 0.061868 | -0.0047134 | 0.057618 | 0.00068675 | -0.002256 | -0.0028161 | 0.062133 | 0.017944 | 0.059267 | -62.1872 | -0.10848 | -62.3142 | 59.1088 | 58.7846 | 58.8351 | -62.3776 | -62.3198 | 0.036989 | -62.4413 | 58.964 | 59.0456 | 58.9206 | -62.5276 | 0.08879 | 0.002308 | 0.27924 | 0.1522 | 0.063412 | -0.32185 | -0.27137 | -0.061208 | -0.14249 | 0.14666 | 0.025158 | 0.086366 | -0.060816 | -0.18582 | 121.5752 | 121.251 | 121.3015 | 62.358 | -121.4841 | 121.4304 | 121.5121 | 121.3871 | 62.5034 | -121.6341
612.6719 | 121.875 | -62.4115 | 59.1522 | 1.4211e-13 | -0.013635 | 0.0016923 | 0.062081 | -0.004927 | 0.057618 | 0.0083173 | -0.0020424 | -0.0028161 | 0.061919 | 0.017731 | 0.059267 | -61.6149 | -0.13595 | -61.7419 | 59.7177 | 59.5081 | 59.4715 | -61.8282 | -61.7657 | 0.004938 | -61.8781 | 59.5317 | 59.6225 | 59.5616 | -61.969 | 0.58333 | 0.56546 | 0.7966 | 0.66956 | 0.086226 | 0.35584 | 0.31927 | 0.44248 | 0.37947 | 0.64575 | 0.53341 | 0.090931 | 0.47031 | 0.40941 | 122.1292 | 121.9196 | 121.883 | 62.2755 | -120.9804 | 121.9432 | 122.034 | 121.9731 | 62.4164 | -121.1212
614.4375 | 121.7697 | -48.0515 | 73.6908 | 1.4211e-13 | -0.013207 | 0.0016923 | 0.062081 | -0.004927 | 0.057405 | -0.014574 | -0.002256 | -0.0028161 | 0.062347 | 0.017731 | 0.059267 | -47.8752 | 0.092979 | -47.9934 | 73.5902 | 73.2265 | 73.2531 | -47.9174 | -47.993 | 0.13772 | -48.0779 | 73.3862 | 73.4957 | 73.5172 | -48.0586 | 0.13406 | -0.1006 | 0.1763 | 0.058085 | -0.07597 | -0.46428 | -0.43771 | -0.007124 | -0.30458 | 0.058464 | -0.026407 | -0.019283 | -0.1951 | -0.17358 | 121.6416 | 121.278 | 121.3045 | 48.1444 | -121.6082 | 121.4377 | 121.5472 | 121.5687 | 48.1892 | -121.7494
616.1562 | 121.8567 | -49.4568 | 72.1619 | 1.4211e-13 | -0.013635 | 0.0014787 | 0.061654 | -0.004927 | 0.057618 | 0.00068675 | -0.0020424 | -0.0026023 | 0.061706 | 0.017731 | 0.059267 | -49.2029 | 0.042614 | -49.3165 | 72.2396 | 71.8528 | 71.8978 | -49.2957 | -49.3208 | 0.10567 | -49.4423 | 72.0401 | 72.1496 | 72.1574 | -49.4414 | 0.16113 | 0.077704 | 0.2539 | 0.1403 | -0.020837 | -0.30902 | -0.26404 | 0.015408 | -0.12173 | 0.13597 | 0.014471 | -0.000937 | -0.012276 | -0.004496 | 121.6964 | 121.3096 | 121.3546 | 49.4994 | -121.4575 | 121.4969 | 121.6064 | 121.6142 | 49.5625 | -121.6032
617.8281 | 121.8475 | -60.2463 | 61.29 | 1.4211e-13 | -0.013635 | 0.0012649 | 0.062081 | -0.004927 | 0.057618 | -0.0069437 | -0.002256 | -0.0026023 | 0.062347 | 0.017731 | 0.059267 | -62.4115 | 0.10214 | -62.5615 | 58.9165 | 58.693 | 58.629 | -62.6249 | -62.5304 | 0.19267 | -62.6336 | 58.7625 | 58.835 | 58.8657 | -62.7245 | -2.3786 | -2.3735 | -2.1653 | -2.3152 | 0.063447 | -2.597 | -2.6609 | -2.4783 | -2.5275 | -2.2841 | -2.3873 | 0.090949 | -2.455 | -2.4243 | 119.1627 | 118.9393 | 118.8753 | 60.3484 | -123.9149 | 119.0088 | 119.0813 | 119.112 | 60.4389 | -124.0145
619.5 | 121.7834 | -67.9138 | 53.6774 | 1.4211e-13 | -0.013635 | 0.0012649 | 0.062081 | -0.004927 | 0.057618 | 0.00068675 | -0.002256 | -0.0026023 | 0.061919 | 0.017944 | 0.059267 | -66.8526 | -0.37862 | -66.9703 | 54.4663 | 54.2515 | 54.2107 | -67.1443 | -67.013 | -0.10495 | -67.107 | 54.2573 | 54.3526 | 54.3924 | -67.2392 | 0.76952 | 0.7889 | 1.0612 | 0.94348 | 0.17396 | 0.57409 | 0.53332 | 0.67458 | 0.5799 | 0.90087 | 0.80684 | 0.13226 | 0.67519 | 0.71502 | 122.3801 | 122.1653 | 122.1245 | 67.5352 | -120.8217 | 122.1711 | 122.2664 | 122.3062 | 67.8089 | -120.9166
621.2188 | 121.8979 | -71.7087 | 49.8688 | 1.4211e-13 | -0.013848 | 0.0010513 | 0.061868 | -0.0047134 | 0.057405 | -0.0069437 | -0.0018288 | -0.0028161 | 0.061919 | 0.017944 | 0.059481 | -71.3898 | -0.63044 | -71.5395 | 49.8329 | 49.5077 | 49.5909 | -71.65 | -71.5779 | -0.12784 | -71.6491 | 49.7062 | 49.774 | 49.6444 | -71.8043 | 0.058715 | -0.035835 | 0.31893 | 0.16921 | 0.1105 | -0.36108 | -0.2779 | -0.095644 | -0.16254 | 0.13076 | 0.059621 | 0.15526 | -0.094815 | -0.22439 | 121.5416 | 121.2164 | 121.2996 | 71.0782 | -121.5187 | 121.4149 | 121.4826 | 121.3531 | 71.5808 | -121.6731
622.9531 | 121.9528 | -114.4318 | 7.0999 | 1.4211e-13 | -0.014489 | 0.0010513 | 0.061227 | -0.004927 | 0.058046 | 0.00068675 | -0.0026832 | -0.0032433 | 0.061278 | 0.017731 | 0.059481 | -113.7673 | -11.3947 | -114.0488 | 7.1624 | 7.0748 | 7.0831 | -114.4217 | -114.0317 | -4.4273 | -114.1349 | 7.1262 | 7.1289 | 7.1916 | -114.5338 | 0.010065 | 0.062449 | 0.66445 | 0.38296 | 0.3729 | -0.025118 | -0.016788 | -0.10208 | 0.026319 | 0.40004 | 0.29686 | 0.39894 | 0.02894 | 0.091663 | 121.5941 | 121.5066 | 121.5149 | 103.037 | -121.5216 | 121.558 | 121.5606 | 121.6233 | 110.0045 | -121.6338
624.7031 | 121.8018 | -115.7181 | 5.928 | 1.4211e-13 | -0.014489 | 0.0010513 | 0.061654 | -0.0047134 | 0.058046 | 0.00068675 | -0.0024696 | -0.0030297 | 0.061492 | 0.018158 | 0.059695 | -114.9256 | -12.9011 | -115.2071 | 5.972 | 5.9163 | 5.9293 | -115.5435 | -115.1856 | -5.137 | -115.2933 | 5.9633 | 5.9705 | 6.0378 | -115.706 | 0.17455 | 0.043943 | 0.79243 | 0.51098 | 0.33643 | -0.011711 | 0.00128 | 0.012057 | 0.035256 | 0.53252 | 0.42476 | 0.4127 | 0.042428 | 0.10973 | 121.6901 | 121.6344 | 121.6474 | 102.817 | -121.4716 | 121.6814 | 121.6885 | 121.7558 | 110.5811 | -121.6341
626.3906 | 121.8842 | -116.4001 | 5.191 | 1.4211e-13 | -0.014489 | 0.00062391 | 0.06144 | -0.0044998 | 0.057832 | -0.0069437 | -0.002897 | -0.0034569 | 0.061278 | 0.018158 | 0.059695 | -115.4659 | -13.7573 | -115.7519 | 5.4134 | 5.3714 | 5.3936 | -116.061 | -115.735 | -5.604 | -115.8565 | 5.4185 | 5.4302 | 5.4883 | -116.2417 | 0.33919 | 0.22238 | 0.93425 | 0.64823 | 0.30903 | 0.1804 | 0.20258 | 0.1584 | 0.22741 | 0.66515 | 0.54364 | 0.38524 | 0.23915 | 0.2973 | 121.8136 | 121.7716 | 121.7938 | 102.6429 | -121.252 | 121.8186 | 121.8303 | 121.8885 | 110.7962 | -121.4328
628.0781 | 121.843 | -116.4505 | 5.127 | 1.4211e-13 | -0.014276 | 0.00083771 | 0.061013 | -0.004927 | 0.058046 | 0.00068675 | -0.0024696 | -0.0032433 | 0.061278 | 0.018158 | 0.059695 | -115.0309 | -14.1602 | -115.3353 | 5.8255 | 5.7652 | 5.7691 | -115.6488 | -115.3092 | -5.8375 | -115.4261 | 5.8076 | 5.8148 | 5.8867 | -115.8251 | 0.80165 | 0.69852 | 1.4196 | 1.1152 | 0.31355 | 0.63827 | 0.64211 | 0.62543 | 0.68067 | 1.1413 | 1.0244 | 0.39897 | 0.68784 | 0.75972 | 122.276 | 122.2157 | 122.2196 | 102.2903 | -120.7758 | 122.2581 | 122.2653 | 122.3372 | 110.613 | -120.952
629.7812 | 121.8292 | -118.3914 | 3.1082 | 1.4211e-13 | -0.014276 | 0.0010513 | 0.061227 | -0.004927 | 0.058259 | -0.0069437 | -0.002256 | -0.0036707 | 0.061278 | 0.018372 | 0.059481 | -117.7551 | -15.4468 | -118.0731 | 3.0189 | 2.995 | 3.0036 | -118.3733 | -118.0335 | -6.4602 | -118.1596 | 3.0376 | 3.0402 | 3.1075 | -118.5724 | 0.018108 | -0.089292 | 0.63633 | 0.31831 | 0.3002 | -0.11324 | -0.10462 | -0.18094 | -0.070578 | 0.3579 | 0.23183 | 0.41277 | -0.068052 | -0.00075 | 121.4103 | 121.3864 | 121.395 | 102.9446 | -121.4815 | 121.4291 | 121.4316 | 121.4989 | 111.9312 | -121.6806
631.4688 | 121.7377 | -118.9178 | 2.6047 | 1.4211e-13 | -0.014917 | 0.0010513 | 0.061227 | -0.004927 | 0.058046 | 0.00068675 | -0.0026832 | -0.0036707 | 0.061278 | 0.017944 | 0.059481 | -118.245 | -16.01 | -118.5584 | 2.5153 | 2.473 | 2.4862 | -118.877 | -118.528 | -6.7853 | -118.6449 | 2.5203 | 2.5365 | 2.5901 | -119.0577 | 0.040856 | -0.089375 | 0.67287 | 0.35944 | 0.31858 | -0.1317 | -0.11847 | -0.13987 | -0.084408 | 0.38983 | 0.27291 | 0.41278 | -0.068159 | -0.014593 | 121.4331 | 121.3908 | 121.4041 | 102.9079 | -121.4817 | 121.4381 | 121.4544 | 121.5079 | 112.1326 | -121.6624
633.2031 | 121.7056 | -118.9636 | 2.5772 | 1.4211e-13 | -0.014489 | 0.00083771 | 0.061013 | -0.0047134 | 0.057832 | 0.0083173 | -0.0026832 | -0.0034569 | 0.061492 | 0.018372 | 0.059267 | -118.277 | -16.3625 | -118.5721 | 2.4649 | 2.4363 | 2.445 | -118.8953 | -118.5555 | -6.9959 | -118.6724 | 2.4791 | 2.4816 | 2.5443 | -119.0898 | 0.068316 | -0.11227 | 0.6866 | 0.39148 | 0.32317 | -0.14086 | -0.13221 | -0.12615 | -0.098148 | 0.40814 | 0.29121 | 0.41736 | -0.095636 | -0.032913 | 121.4286 | 121.4 | 121.4086 | 102.6011 | -121.4725 | 121.4427 | 121.4452 | 121.5079 | 111.9677 | -121.667
634.9219 | 121.6461 | -119.1788 | 2.3666 | 1.4211e-13 | -0.014276 | 0.0010513 | 0.060799 | -0.0047134 | 0.058046 | -0.0069437 | -0.0024696 | -0.0032433 | 0.061492 | 0.018158 | 0.059481 | -118.4922 | -16.7197 | -118.7873 | 2.236 | 2.212 | 2.2298 | -119.1105 | -118.7753 | -7.2065 | -118.8922 | 2.2593 | 2.2664 | 2.3291 | -119.3096 | 0.068256 | -0.13062 | 0.68656 | 0.39145 | 0.3232 | -0.15466 | -0.13683 | -0.13078 | -0.10735 | 0.40351 | 0.28658 | 0.41736 | -0.10026 | -0.037536 | 121.4148 | 121.3908 | 121.4086 | 102.4591 | -121.4772 | 121.4381 | 121.4452 | 121.5079 | 111.9722 | -121.6762
636.6719 | 121.6278 | -118.959 | 2.5497 | 1.4211e-13 | -0.014276 | 0.0010513 | 0.06144 | -0.004927 | 0.057832 | 0.0083173 | -0.0024696 | -0.0034569 | 0.061278 | 0.018372 | 0.059054 | -118.4235 | -16.9165 | -118.737 | 2.3001 | 2.2669 | 2.2756 | -119.1151 | -118.7112 | -7.353 | -118.8098 | 2.3188 | 2.3213 | 2.3795 | -119.2409 | -0.15605 | -0.24963 | 0.53551 | 0.22209 | 0.37814 | -0.28282 | -0.27415 | -0.28182 | -0.23093 | 0.24788 | 0.14928 | 0.4311 | -0.22842 | -0.17028 | 121.2592 | 121.226 | 121.2346 | 102.0425 | -121.6648 | 121.2779 | 121.2804 | 121.3385 | 111.606 | -121.7906
638.4219 | 121.7239 | -120.0577 | 1.4236 | 1.4211e-13 | -0.014917 | 0.00083771 | 0.061227 | -0.004927 | 0.057832 | -0.0069437 | -0.0026832 | -0.0030297 | 0.061065 | 0.018158 | 0.059695 | -119.3026 | -17.4522 | -119.616 | 1.4531 | 1.3786 | 1.3965 | -119.9988 | -119.5857 | -7.6919 | -119.698 | 1.426 | 1.4285 | 1.4821 | -120.1292 | 0.05885 | 0.029469 | 0.75509 | 0.44169 | 0.38284 | -0.04503 | -0.027142 | -0.071481 | 0.002362 | 0.47198 | 0.35964 | 0.43112 | 0.00485 | 0.058416 | 121.5108 | 121.4363 | 121.4542 | 102.6055 | -121.4225 | 121.4837 | 121.4862 | 121.5397 | 112.3658 | -121.5528
640.1094 | 121.431 | -121.2616 | 0.15564 | 1.4211e-13 | -0.014703 | 0.0010513 | 0.061013 | -0.0047134 | 0.057618 | -0.0069437 | -0.0024696 | -0.0034569 | 0.062347 | 0.018158 | 0.059054 | -117.7917 | -17.2508 | -117.9678 | 2.8541 | 2.6149 | 2.8159 | -118.4328 | -118.1434 | -7.7468 | -118.2374 | 2.6668 | 2.7609 | 2.6908 | -118.5769 | 2.8288 | 2.6985 | 3.4699 | 3.2938 | 0.46503 | 2.4593 | 2.6602 | 2.6847 | 2.5111 | 3.1182 | 3.0242 | 0.33951 | 2.6052 | 2.5352 | 124.1157 | 123.8765 | 124.0775 | 104.0108 | -118.5885 | 123.9284 | 124.0225 | 123.9524 | 113.5148 | -118.7326
641.8438 | 121.6141 | -121.4447 | 0.13275 | 1.4211e-13 | -0.014703 | 0.0010513 | 0.06144 | -0.004927 | 0.058259 | 0.0083173 | -0.0026832 | -0.0030297 | 0.061706 | 0.018585 | 0.059695 | -120.7173 | -18.4275 | -121.049 | 0.042971 | -0.027115 | -0.004549 | -121.432 | -121.0097 | -8.2322 | -121.1266 | 0.024988 | 0.027442 | 0.085587 | -121.5715 | 0.012671 | -0.08978 | 0.7274 | 0.39571 | 0.38304 | -0.15987 | -0.1373 | -0.12678 | -0.10776 | 0.43503 | 0.31811 | 0.44489 | -0.10531 | -0.047164 | 121.4877 | 121.4176 | 121.4402 | 103.0172 | -121.5648 | 121.4697 | 121.4721 | 121.5303 | 113.2125 | -121.7042
643.5156 | 121.7697 | -121.4218 | 0.09613 | 1.4211e-13 | -0.014917 | 0.00062391 | 0.061227 | -0.0047134 | 0.058046 | -0.0069437 | -0.002897 | -0.0032433 | 0.061278 | 0.018585 | 0.059481 | -120.7631 | -18.6564 | -121.0856 | 0.042971 | -0.022536 | -0.013707 | -121.4229 | -121.0509 | -8.3649 | -121.1678 | 0.029566 | 0.022864 | 0.085587 | -121.6035 | -0.001059 | -0.053159 | 0.65873 | 0.3362 | 0.33726 | -0.11867 | -0.10984 | -0.18172 | -0.066564 | 0.37093 | 0.25401 | 0.43573 | -0.073266 | -0.010543 | 121.4648 | 121.3993 | 121.4081 | 102.7654 | -121.519 | 121.4514 | 121.4447 | 121.5074 | 113.0569 | -121.6997
645.25 | 121.6644 | -121.4493 | 0.14648 | 1.4211e-13 | -0.014703 | 0.0010513 | 0.061227 | -0.004927 | 0.058259 | -0.0069437 | -0.0026832 | -0.0032433 | 0.061492 | 0.018158 | 0.059267 | -120.786 | -18.8579 | -121.1177 | 0.038393 | -0.027115 | -0.013707 | -121.432 | -121.0784 | -8.4382 | -121.1999 | 0.029566 | 0.018285 | 0.081008 | -121.631 | 0.017249 | -0.10809 | 0.6633 | 0.33162 | 0.31437 | -0.1736 | -0.16019 | -0.18173 | -0.11692 | 0.37092 | 0.24942 | 0.43116 | -0.1282 | -0.065476 | 121.4877 | 121.4222 | 121.4356 | 102.5914 | -121.5785 | 121.4788 | 121.4676 | 121.5303 | 113.0111 | -121.7775
646.9219 | 121.7468 | -121.4767 | 0.14648 | 1.4211e-13 | -0.014917 | 0.00083771 | 0.060799 | -0.0047134 | 0.058046 | -0.014574 | -0.0026832 | -0.0034569 | 0.061065 | 0.018585 | 0.059695 | -120.8043 | -19.0318 | -121.1268 | 0.042971 | -0.027115 | -0.013707 | -121.4458 | -121.0921 | -8.5572 | -121.2136 | 0.024988 | 0.032021 | 0.081008 | -121.6402 | 0.030978 | -0.10351 | 0.67245 | 0.34992 | 0.31895 | -0.1736 | -0.16019 | -0.16342 | -0.1215 | 0.38465 | 0.26315 | 0.42658 | -0.11446 | -0.065476 | 121.5197 | 121.4496 | 121.463 | 102.4449 | -121.5923 | 121.5017 | 121.5088 | 121.5578 | 112.9195 | -121.7867
648.6562 | 121.7422 | -121.4951 | 0.13275 | 1.4211e-13 | -0.01513 | 0.00083771 | 0.060799 | -0.0047134 | 0.058046 | 0.015947 | -0.0026832 | -0.0028161 | 0.061492 | 0.018585 | 0.059481 | -120.8135 | -19.1555 | -121.1314 | 0.042971 | -0.036272 | -0.013707 | -121.4641 | -121.1012 | -8.6534 | -121.2273 | 0.020409 | 0.027442 | 0.085587 | -121.6493 | 0.030972 | -0.08978 | 0.68161 | 0.36366 | 0.33268 | -0.16902 | -0.14646 | -0.15427 | -0.11234 | 0.39381 | 0.26773 | 0.422 | -0.10531 | -0.047164 | 121.538 | 121.4588 | 121.4813 | 102.3396 | -121.5968 | 121.5155 | 121.5225 | 121.5806 | 112.8417 | -121.7821
650.3906 | 121.7972 | -121.4813 | 0.10529 | 1.4211e-13 | -0.014917 | 0.0010513 | 0.061013 | -0.0047134 | 0.058259 | -0.0069437 | -0.002897 | -0.0030297 | 0.061278 | 0.018585 | 0.059481 | -120.818 | -19.3203 | -121.1406 | 0.038393 | -0.036272 | -0.018285 | -121.4687 | -121.1104 | -8.7404 | -121.2319 | 0.024988 | 0.0366 | 0.085587 | -121.6631 | 0.01266 | -0.066893 | 0.66329 | 0.34077 | 0.32811 | -0.14156 | -0.12357 | -0.18174 | -0.080298 | 0.37092 | 0.24942 | 0.43116 | -0.068686 | -0.019699 | 121.5197 | 121.4451 | 121.463 | 102.161 | -121.5739 | 121.5063 | 121.5179 | 121.5669 | 112.7409 | -121.7683
652.1406 | 121.8063 | -121.4767 | 0.10986 | 1.4211e-13 | -0.014917 | 0.00062391 | 0.061227 | -0.0051408 | 0.057832 | 0.00068675 | -0.0024696 | -0.0032433 | 0.061278 | 0.018799 | 0.059481 | -120.8226 | -19.4531 | -121.1543 | 0.033814 | -0.031693 | -0.009128 | -121.4778 | -121.115 | -8.8274 | -121.2365 | 0.024988 | 0.032021 | 0.081008 | -121.6722 | -0.001074 | -0.076049 | 0.65414 | 0.32246 | 0.32353 | -0.14156 | -0.11899 | -0.19547 | -0.084875 | 0.36176 | 0.24026 | 0.43573 | -0.077842 | -0.028855 | 121.5106 | 121.4451 | 121.4676 | 102.0237 | -121.5877 | 121.5017 | 121.5088 | 121.5578 | 112.6494 | -121.7821
653.875 | 121.8063 | -121.4859 | 0.10986 | 1.4211e-13 | -0.014703 | 0.00083771 | 0.061013 | -0.004927 | 0.057832 | 0.00068675 | -0.0031106 | -0.0030297 | 0.061278 | 0.018158 | 0.059481 | -120.8272 | -19.5859 | -121.1589 | 0.038393 | -0.036272 | -0.018285 | -121.4824 | -121.1196 | -8.9098 | -121.2365 | 0.034145 | 0.022864 | 0.085587 | -121.6722 | 0.003502 | -0.07147 | 0.65872 | 0.32703 | 0.32353 | -0.14614 | -0.12815 | -0.18632 | -0.075718 | 0.36634 | 0.24941 | 0.43573 | -0.086999 | -0.024276 | 121.5243 | 121.4496 | 121.4676 | 101.9 | -121.5923 | 121.52 | 121.5088 | 121.5715 | 112.5761 | -121.7821
655.5469 | 121.7422 | -121.5454 | 0.13733 | 1.4211e-13 | -0.015344 | 0.0010513 | 0.061227 | -0.0044998 | 0.058259 | 0.0083173 | -0.0024696 | -0.0030297 | 0.061706 | 0.018372 | 0.059908 | -120.8363 | -19.6866 | -121.1634 | 0.033814 | -0.027115 | -0.013707 | -121.487 | -121.1241 | -8.9693 | -121.2411 | 0.029566 | 0.022864 | 0.081008 | -121.6814 | 0.058432 | -0.10352 | 0.70907 | 0.38196 | 0.32353 | -0.16444 | -0.15104 | -0.13597 | -0.10776 | 0.42127 | 0.30434 | 0.44031 | -0.11447 | -0.056321 | 121.5792 | 121.5183 | 121.5317 | 101.8588 | -121.6243 | 121.575 | 121.5683 | 121.6264 | 112.5761 | -121.8187
657.2812 | 121.8155 | -121.5042 | 0.10071 | 1.4211e-13 | -0.014703 | 0.00083771 | 0.061013 | -0.0053544 | 0.058259 | -0.0069437 | -0.002897 | -0.0030297 | 0.061278 | 0.018158 | 0.059267 | -120.8363 | -19.8102 | -121.1634 | 0.033814 | -0.027115 | -0.013707 | -121.4916 | -121.1333 | -9.0289 | -121.2502 | 0.038723 | 0.022864 | 0.081008 | -121.686 | 0.012654 | -0.066894 | 0.66787 | 0.34076 | 0.32811 | -0.12782 | -0.11442 | -0.18175 | -0.061985 | 0.37091 | 0.25399 | 0.43574 | -0.077844 | -0.0197 | 121.538 | 121.4771 | 121.4905 | 101.694 | -121.5923 | 121.5429 | 121.5271 | 121.5852 | 112.4754 | -121.7867
659.0156 | 121.7697 | -121.5408 | 0.1236 | 1.4211e-13 | -0.01513 | 0.0010513 | 0.061013 | -0.0047134 | 0.058259 | 0.00068675 | -0.0026832 | -0.0030297 | 0.061278 | 0.018158 | 0.059481 | -120.8363 | -19.888 | -121.168 | 0.033814 | -0.036272 | -0.022864 | -121.5007 | -121.1333 | -9.1021 | -121.2548 | 0.029566 | 0.013707 | 0.07643 | -121.6905 | 0.040118 | -0.089782 | 0.70449 | 0.37281 | 0.33269 | -0.15987 | -0.14646 | -0.1497 | -0.09403 | 0.40753 | 0.28603 | 0.43573 | -0.10989 | -0.047166 | 121.5746 | 121.5046 | 121.518 | 101.6528 | -121.6243 | 121.5704 | 121.5545 | 121.6173 | 112.4387 | -121.8141
660.75 | 121.7651 | -121.5454 | 0.11902 | 1.4211e-13 | -0.01513 | 0.00083771 | 0.061227 | -0.004927 | 0.057618 | 0.00068675 | -0.0026832 | -0.0034569 | 0.061278 | 0.018585 | 0.059481 | -120.8363 | -20.0071 | -121.1818 | 0.024657 | -0.040851 | -0.018285 | -121.5007 | -121.1425 | -9.1571 | -121.2502 | 0.024988 | 0.013707 | 0.081008 | -121.6997 | 0.044695 | -0.094362 | 0.70907 | 0.36365 | 0.31896 | -0.15987 | -0.1373 | -0.15428 | -0.094031 | 0.40295 | 0.29519 | 0.44947 | -0.10531 | -0.038011 | 121.5701 | 121.5046 | 121.5271 | 101.5383 | -121.6197 | 121.5704 | 121.5591 | 121.6264 | 112.3883 | -121.8187
662.4531 | 121.7102 | -121.5317 | 0.13733 | 1.4211e-13 | -0.015344 | 0.00062391 | 0.061013 | -0.0051408 | 0.058259 | -0.0069437 | -0.002897 | -0.0032433 | 0.061065 | 0.018585 | 0.059695 | -120.8501 | -20.117 | -121.1772 | 0.020079 | -0.040851 | -0.018285 | -121.5099 | -121.1379 | -9.2303 | -121.2502 | 0.029566 | 0.013707 | 0.07643 | -121.6951 | 0.021804 | -0.11725 | 0.6816 | 0.3545 | 0.33269 | -0.17818 | -0.15561 | -0.16344 | -0.10776 | 0.3938 | 0.28146 | 0.44489 | -0.12362 | -0.060899 | 121.5518 | 121.4908 | 121.5134 | 101.4147 | -121.6472 | 121.5612 | 121.5454 | 121.6081 | 112.3014 | -121.8324
664.1719 | 121.8704 | -121.5225 | 0.09613 | 1.4211e-13 | -0.015558 | 0.0014787 | 0.061013 | -0.0047134 | 0.057832 | 0.00068675 | -0.0026832 | -0.0032433 | 0.061492 | 0.018799 | 0.059267 | -120.8501 | -20.1902 | -121.168 | 0.024657 | -0.036272 | -0.027442 | -121.4961 | -121.1425 | -9.299 | -121.264 | 0.024988 | 0.018285 | 0.071851 | -121.6997 | 0.026386 | -0.071473 | 0.67244 | 0.3545 | 0.32811 | -0.1324 | -0.12357 | -0.17717 | -0.071142 | 0.38006 | 0.25856 | 0.43574 | -0.077845 | -0.024279 | 121.5472 | 121.4862 | 121.4951 | 101.3323 | -121.5923 | 121.5475 | 121.5408 | 121.5944 | 112.2235 | -121.7958
665.9062 | 121.7514 | -121.5546 | 0.13733 | 1.4211e-13 | -0.015344 | 0.0010513 | 0.061227 | -0.004927 | 0.057832 | 0.0083173 | -0.0026832 | -0.0030297 | 0.061492 | 0.018158 | 0.059054 | -120.8501 | -20.2498 | -121.1772 | 0.015501 | -0.040851 | -0.027442 | -121.5099 | -121.1379 | -9.3402 | -121.2594 | 0.020409 | 0.013707 | 0.07643 | -121.7089 | 0.044692 | -0.12183 | 0.70449 | 0.37738 | 0.33269 | -0.17818 | -0.16477 | -0.15429 | -0.11692 | 0.41669 | 0.29519 | 0.44947 | -0.12362 | -0.060899 | 121.5701 | 121.5137 | 121.5271 | 101.3048 | -121.6472 | 121.575 | 121.5683 | 121.631 | 112.2144 | -121.8462
667.5938 | 121.7789 | -121.5683 | 0.11444 | 1.4211e-13 | -0.014703 | 0.00083771 | 0.061227 | -0.004927 | 0.058046 | -0.0069437 | -0.0026832 | -0.0032433 | 0.061278 | 0.019013 | 0.059267 | -120.8501 | -20.3367 | -121.1818 | 0.020079 | -0.036272 | -0.027442 | -121.5053 | -121.147 | -9.4043 | -121.264 | 0.024988 | 0.018285 | 0.07643 | -121.6997 | 0.063004 | -0.094362 | 0.71822 | 0.38654 | 0.32353 | -0.15071 | -0.14188 | -0.1314 | -0.089453 | 0.42126 | 0.30434 | 0.43574 | -0.096156 | -0.038011 | 121.5884 | 121.532 | 121.5409 | 101.2316 | -121.6197 | 121.5933 | 121.5866 | 121.6447 | 112.164 | -121.8141
669.3281 | 121.7514 | -121.5775 | 0.11902 | 1.4211e-13 | -0.01513 | 0.00062391 | 0.061227 | -0.004927 | 0.058046 | -0.0069437 | -0.0026832 | -0.0030297 | 0.061065 | 0.018799 | 0.05884 | -120.8501 | -20.4146 | -121.1772 | 0.015501 | -0.04543 | -0.022864 | -121.5053 | -121.1425 | -9.4684 | -121.2548 | 0.034145 | 0.027442 | 0.07643 | -121.7043 | 0.07216 | -0.10352 | 0.72738 | 0.40027 | 0.32811 | -0.16445 | -0.14188 | -0.12682 | -0.084874 | 0.435 | 0.32265 | 0.44947 | -0.091577 | -0.042589 | 121.593 | 121.532 | 121.5546 | 101.1629 | -121.6243 | 121.6116 | 121.6049 | 121.6539 | 112.109 | -121.8233
671.0625 | 121.8155 | -121.5271 | 0.1236 | 1.4211e-13 | -0.015344 | 0.00062391 | 0.06144 | -0.0047134 | 0.057832 | -0.0069437 | -0.0026832 | -0.0034569 | 0.061492 | 0.019226 | 0.059267 | -120.8409 | -20.4924 | -121.1909 | 0.020079 | -0.036272 | -0.018285 | -121.5099 | -121.1425 | -9.5188 | -121.2594 | 0.034145 | 0.018285 | 0.081008 | -121.7043 | 0.017227 | -0.10352 | 0.68618 | 0.33618 | 0.31896 | -0.15987 | -0.14188 | -0.17717 | -0.089451 | 0.38464 | 0.26772 | 0.44489 | -0.10531 | -0.042588 | 121.5472 | 121.4908 | 121.5088 | 101.0347 | -121.6335 | 121.5612 | 121.5454 | 121.6081 | 112.0083 | -121.8279
672.7969 | 121.8613 | -121.5363 | 0.11444 | 1.4211e-13 | -0.015344 | 0.00083771 | 0.061227 | -0.0051408 | 0.057832 | -0.014574 | -0.0026832 | -0.0034569 | 0.061278 | 0.018585 | 0.059481 | -120.8363 | -20.5657 | -121.1909 | 0.020079 | -0.036272 | -0.022864 | -121.5053 | -121.1425 | -9.5829 | -121.2685 | 0.024988 | 0.018285 | 0.081008 | -121.7134 | 0.030961 | -0.094362 | 0.69991 | 0.34534 | 0.31438 | -0.15071 | -0.13731 | -0.17718 | -0.089453 | 0.3938 | 0.26772 | 0.44489 | -0.096156 | -0.033433 | 121.5563 | 121.5 | 121.5134 | 100.9706 | -121.6197 | 121.5612 | 121.5545 | 121.6173 | 111.9534 | -121.8279
674.4688 | 121.8475 | -121.4905 | 0.10071 | 1.4211e-13 | -0.015344 | 0.00083771 | 0.060799 | -0.0051408 | 0.058259 | -0.0069437 | -0.0031106 | -0.0034569 | 0.061065 | 0.018585 | 0.059481 | -120.8501 | -20.6298 | -121.1863 | 0.015501 | -0.040851 | -0.027442 | -121.5053 | -121.1516 | -9.6287 | -121.264 | 0.024988 | 0.013707 | 0.071851 | -121.7089 | -0.014815 | -0.085207 | 0.6404 | 0.30414 | 0.31896 | -0.14156 | -0.12815 | -0.21837 | -0.07572 | 0.33886 | 0.22652 | 0.44489 | -0.087001 | -0.028857 | 121.506 | 121.4496 | 121.463 | 100.8607 | -121.606 | 121.5155 | 121.5042 | 121.5623 | 111.8618 | -121.8096
676.2031 | 121.8979 | -121.5454 | 0.10529 | 1.4211e-13 | -0.015344 | 0.00083771 | 0.061013 | -0.004927 | 0.058046 | 0.0083173 | -0.0026832 | -0.0030297 | 0.061278 | 0.019013 | 0.059481 | -120.8455 | -20.6756 | -121.1863 | 0.020079 | -0.04543 | -0.027442 | -121.5053 | -121.147 | -9.6653 | -121.264 | 0.034145 | 0.009128 | 0.071851 | -121.7134 | 0.040116 | -0.085207 | 0.69991 | 0.35907 | 0.31896 | -0.15072 | -0.13273 | -0.16802 | -0.071141 | 0.39837 | 0.28145 | 0.44947 | -0.096158 | -0.033435 | 121.5655 | 121.5 | 121.518 | 100.8698 | -121.6106 | 121.5796 | 121.5545 | 121.6173 | 111.8801 | -121.8187
677.8906 | 121.7789 | -121.5591 | 0.11902 | 1.4211e-13 | -0.01513 | 0.0012649 | 0.061227 | -0.0047134 | 0.057832 | 0.0083173 | -0.0026832 | -0.0030297 | 0.061492 | 0.018585 | 0.059481 | -120.8501 | -20.7488 | -121.1909 | 0.020079 | -0.040851 | -0.027442 | -121.519 | -121.1516 | -9.7248 | -121.2823 | 0.029566 | 0.013707 | 0.07643 | -121.7134 | 0.040112 | -0.09894 | 0.70907 | 0.36823 | 0.32811 | -0.15987 | -0.14646 | -0.15429 | -0.089453 | 0.40753 | 0.27687 | 0.43116 | -0.10531 | -0.042589 | 121.5792 | 121.5183 | 121.5317 | 100.8103 | -121.638 | 121.5887 | 121.5729 | 121.6356 | 111.8343 | -121.8324
679.625 | 121.8567 | -121.5317 | 0.091553 | 1.4211e-13 | -0.015344 | 0.00083771 | 0.061227 | -0.004927 | 0.057832 | -0.0069437 | -0.002897 | -0.0032433 | 0.061492 | 0.018799 | 0.059054 | -120.8592 | -20.8129 | -121.1818 | 0.024657 | -0.04543 | -0.022864 | -121.5099 | -121.1562 | -9.7798 | -121.2685 | 0.029566 | 0.004549 | 0.071851 | -121.718 | 0.021804 | -0.066896 | 0.67244 | 0.34992 | 0.32811 | -0.13698 | -0.11442 | -0.18633 | -0.061987 | 0.37548 | 0.26314 | 0.44947 | -0.087004 | -0.019702 | 121.5563 | 121.4862 | 121.5088 | 100.7188 | -121.6014 | 121.5612 | 121.5362 | 121.6035 | 111.7519 | -121.8096
681.3594 | 121.8796 | -121.5225 | 0.10529 | 1.4211e-13 | -0.015558 | 0.00083771 | 0.061227 | -0.0051408 | 0.058046 | 0.0083173 | -0.002897 | -0.0030297 | 0.061278 | 0.019013 | 0.059267 | -120.8501 | -20.8953 | -121.1955 | 0.010922 | -0.040851 | -0.022864 | -121.5099 | -121.147 | -9.8118 | -121.2777 | 0.029566 | 0.009128 | 0.071851 | -121.7134 | 0.012649 | -0.094364 | 0.67244 | 0.32703 | 0.31438 | -0.14614 | -0.12815 | -0.19091 | -0.07572 | 0.37549 | 0.24483 | 0.43574 | -0.096158 | -0.033435 | 121.5334 | 121.4817 | 121.4997 | 100.6272 | -121.6152 | 121.5521 | 121.5316 | 121.5944 | 111.7107 | -121.8187
683.0625 | 121.8338 | -121.5179 | 0.11444 | 1.4211e-13 | -0.015344 | 0.00083771 | 0.061013 | -0.004927 | 0.058046 | -0.0069437 | -0.0026832 | -0.0030297 | 0.061065 | 0.019013 | 0.059695 | -120.8455 | -20.9457 | -121.1863 | 0.020079 | -0.036272 | -0.027442 | -121.5145 | -121.1516 | -9.8622 | -121.2685 | 0.024988 | 0.009128 | 0.07643 | -121.718 | 0.003492 | -0.094362 | 0.67244 | 0.3316 | 0.32811 | -0.15071 | -0.14188 | -0.20006 | -0.089453 | 0.36633 | 0.24941 | 0.44947 | -0.10531 | -0.038011 | 121.538 | 121.4817 | 121.4905 | 100.5722 | -121.6289 | 121.5429 | 121.5271 | 121.5944 | 111.6558 | -121.8324
684.7656 | 121.8796 | -121.5317 | 0.082397 | 1.4211e-13 | -0.015344 | 0.00083771 | 0.061227 | -0.004927 | 0.058046 | -0.0069437 | -0.002897 | -0.0032433 | 0.061065 | 0.018799 | 0.059481 | -120.8501 | -21.0006 | -121.1818 | 0.015501 | -0.040851 | -0.032021 | -121.5145 | -121.1516 | -9.908 | -121.2731 | 0.029566 | 0.022864 | 0.081008 | -121.7134 | 0.017225 | -0.066896 | 0.6816 | 0.34992 | 0.33269 | -0.12325 | -0.11442 | -0.18175 | -0.052831 | 0.38006 | 0.25856 | 0.44031 | -0.059533 | -0.001389 | 121.5472 | 121.4908 | 121.4997 | 100.531 | -121.5968 | 121.5612 | 121.5545 | 121.6127 | 111.6237 | -121.7958
686.5 | 121.756 | -121.5454 | 0.12817 | 1.4211e-13 | -0.015558 | 0.00041031 | 0.06144 | -0.0047134 | 0.058046 | 0.00068675 | -0.0026832 | -0.0034569 | 0.061492 | 0.018585 | 0.059695 | -120.8501 | -20.9961 | -121.1863 | 0.020079 | -0.036272 | -0.032021 | -121.5099 | -121.147 | -9.94 | -121.2731 | 0.029566 | 0.018285 | 0.081008 | -121.7226 | 0.035537 | -0.1081 | 0.69533 | 0.35907 | 0.32353 | -0.16445 | -0.1602 | -0.17718 | -0.098608 | 0.39837 | 0.27229 | 0.44947 | -0.10989 | -0.047166 | 121.5655 | 121.5091 | 121.5134 | 100.5493 | -121.638 | 121.575 | 121.5637 | 121.6264 | 111.6054 | -121.8508
688.1719 | 121.8842 | -121.5225 | 0.091553 | 1.4211e-13 | -0.015771 | 0.0010513 | 0.061227 | -0.004927 | 0.057618 | 0.0083173 | -0.0024696 | -0.0034569 | 0.061065 | 0.018799 | 0.059267 | -120.8547 | -21.0556 | -121.1909 | 0.010922 | -0.040851 | -0.027442 | -121.519 | -121.147 | -9.9675 | -121.2777 | 0.029566 | 0.013707 | 0.085587 | -121.7226 | 0.003491 | -0.080631 | 0.66786 | 0.3316 | 0.32811 | -0.1324 | -0.11899 | -0.20007 | -0.061987 | 0.37549 | 0.24483 | 0.44489 | -0.077846 | -0.005966 | 121.5334 | 121.4817 | 121.4951 | 100.4669 | -121.6106 | 121.5521 | 121.5362 | 121.6081 | 111.555 | -121.8141
689.9062 | 121.8842 | -121.5134 | 0.091553 | 1.4211e-13 | -0.015558 | 0.00062391 | 0.061227 | -0.0051408 | 0.057832 | -0.0069437 | -0.0026832 | -0.0034569 | 0.061492 | 0.018799 | 0.059267 | -120.8501 | -21.1014 | -121.1818 | 0.024657 | -0.050009 | -0.022864 | -121.5145 | -121.1608 | -10.0133 | -121.2685 | 0.024988 | 0.009128 | 0.067272 | -121.7134 | -0.001085 | -0.066896 | 0.66329 | 0.33161 | 0.33269 | -0.14156 | -0.11442 | -0.20006 | -0.066565 | 0.35259 | 0.24483 | 0.44489 | -0.082425 | -0.024281 | 121.538 | 121.4634 | 121.4905 | 100.412 | -121.606 | 121.5384 | 121.5225 | 121.5806 | 111.5001 | -121.805
691.6406 | 121.7514 | -121.5317 | 0.12817 | 1.4211e-13 | -0.015558 | 0.0012649 | 0.06144 | -0.004927 | 0.057618 | 0.00068675 | -0.002897 | -0.0030297 | 0.061065 | 0.018585 | 0.059267 | -120.8592 | -21.1563 | -121.1909 | 0.015501 | -0.04543 | -0.027442 | -121.519 | -121.1654 | -10.0545 | -121.2777 | 0.024988 | 0.022864 | 0.07643 | -121.7226 | 0.012646 | -0.11267 | 0.67244 | 0.34076 | 0.32811 | -0.1736 | -0.15562 | -0.19091 | -0.10319 | 0.36633 | 0.25398 | 0.44489 | -0.10531 | -0.051744 | 121.5472 | 121.4862 | 121.5042 | 100.3754 | -121.6472 | 121.5567 | 121.5545 | 121.6081 | 111.4772 | -121.8508
693.3281 | 121.756 | -121.582 | 0.11902 | 1.4211e-13 | -0.015558 | 0.00062391 | 0.06144 | -0.004927 | 0.058046 | -0.0069437 | -0.0026832 | -0.0032433 | 0.061278 | 0.019013 | 0.059267 | -120.8547 | -21.2158 | -121.1955 | 0.015501 | -0.04543 | -0.022864 | -121.5236 | -121.1608 | -10.082 | -121.2777 | 0.024988 | 0.013707 | 0.067272 | -121.7226 | 0.058421 | -0.10352 | 0.72737 | 0.38654 | 0.32812 | -0.16445 | -0.14188 | -0.14056 | -0.094031 | 0.42126 | 0.30434 | 0.44489 | -0.10531 | -0.051747 | 121.5975 | 121.5366 | 121.5592 | 100.3662 | -121.6426 | 121.607 | 121.5957 | 121.6493 | 111.5001 | -121.8416
695.0625 | 121.8933 | -121.5225 | 0.09613 | 1.4211e-13 | -0.015985 | 0.00083771 | 0.06144 | -0.0057818 | 0.058046 | 0.00068675 | -0.0031106 | -0.0030297 | 0.060851 | 0.019013 | 0.059267 | -120.8547 | -21.2525 | -121.1909 | 0.024657 | -0.04543 | -0.022864 | -121.519 | -121.1516 | -10.1094 | -121.2731 | 0.024988 | 0.009128 | 0.07643 | -121.7226 | 0.003491 | -0.071473 | 0.66786 | 0.3316 | 0.32811 | -0.14156 | -0.11899 | -0.20007 | -0.071142 | 0.37091 | 0.24941 | 0.44947 | -0.087002 | -0.0197 | 121.5472 | 121.4771 | 121.4997 | 100.2701 | -121.6152 | 121.5475 | 121.5316 | 121.599 | 111.4131 | -121.8187
696.7969 | 121.7468 | -121.5546 | 0.13733 | 1.4211e-13 | -0.015985 | 0.00083771 | 0.061013 | -0.0047134 | 0.058259 | -0.0069437 | -0.002897 | -0.0028161 | 0.060851 | 0.018799 | 0.059267 | -120.8592 | -21.2937 | -121.1955 | 0.020079 | -0.04543 | -0.0366 | -121.5236 | -121.1608 | -10.1506 | -121.2685 | 0.024988 | 0.009128 | 0.07643 | -121.7272 | 0.030955 | -0.11725 | 0.69533 | 0.35907 | 0.32812 | -0.18276 | -0.17393 | -0.1726 | -0.11234 | 0.39379 | 0.28603 | 0.45863 | -0.1282 | -0.060899 | 121.5746 | 121.5091 | 121.518 | 100.2609 | -121.6609 | 121.5796 | 121.5637 | 121.631 | 111.4039 | -121.8645
698.4844 | 121.8658 | -121.5317 | 0.086975 | 1.4211e-13 | -0.015771 | 0.0010513 | 0.061227 | -0.004927 | 0.057832 | -0.0069437 | -0.0031106 | -0.0030297 | 0.061278 | 0.018799 | 0.059267 | -120.8547 | -21.3303 | -121.1909 | 0.020079 | -0.04543 | -0.032021 | -121.519 | -121.1654 | -10.1735 | -121.2777 | 0.015831 | 0.013707 | 0.071851 | -121.718 | 0.012646 | -0.066896 | 0.67702 | 0.34076 | 0.32811 | -0.1324 | -0.119 | -0.18633 | -0.071144 | 0.36633 | 0.25398 | 0.44031 | -0.073268 | -0.015124 | 121.5518 | 121.4862 | 121.4997 | 100.2014 | -121.606 | 121.5475 | 121.5454 | 121.6035 | 111.3581 | -121.805
700.2344 | 121.8704 | -121.4859 | 0.082397 | 1.4211e-13 | -0.015771 | 0.00083771 | 0.061227 | -0.004927 | 0.058046 | -0.0069437 | -0.002897 | -0.0032433 | 0.061065 | 0.019226 | 0.059267 | -120.8547 | -21.3761 | -121.1909 | 0.010922 | -0.04543 | -0.032021 | -121.519 | -121.1562 | -10.201 | -121.2731 | 0.034145 | 0.013707 | 0.07643 | -121.7272 | -0.03313 | -0.071475 | 0.63124 | 0.29498 | 0.32811 | -0.12783 | -0.11442 | -0.24126 | -0.048252 | 0.32971 | 0.21278 | 0.45405 | -0.06869 | -0.005967 | 121.4968 | 121.4405 | 121.4539 | 100.1098 | -121.6014 | 121.52 | 121.4996 | 121.5623 | 111.2849 | -121.8096
701.9688 | 121.8338 | -121.5454 | 0.09613 | 1.4211e-13 | -0.015771 | 0.00083771 | 0.061227 | -0.0051408 | 0.057618 | 0.0083173 | -0.002897 | -0.0032433 | 0.061065 | 0.01944 | 0.059054 | -120.8501 | -21.3807 | -121.1955 | 0.015501 | -0.04543 | -0.027442 | -121.5236 | -121.1562 | -10.2422 | -121.2777 | 0.024988 | 0.009128 | 0.067272 | -121.7272 | 0.0218 | -0.080629 | 0.69533 | 0.34992 | 0.32812 | -0.14156 | -0.12357 | -0.18176 | -0.071142 | 0.38922 | 0.26772 | 0.44947 | -0.087002 | -0.028858 | 121.5609 | 121.5 | 121.518 | 100.1647 | -121.6197 | 121.5704 | 121.5545 | 121.6127 | 111.3032 | -121.8233
703.7188 | 121.7697 | -121.5866 | 0.10529 | 1.4211e-13 | -0.015771 | 0.00083771 | 0.061227 | -0.004927 | 0.058046 | -0.0069437 | -0.002897 | -0.0030297 | 0.061278 | 0.019226 | 0.059267 | -120.8638 | -21.4631 | -121.2047 | 0.010922 | -0.059167 | -0.041178 | -121.5282 | -121.1654 | -10.2834 | -121.2914 | 0.020409 | 0.004549 | 0.062694 | -121.7409 | 0.05842 | -0.094364 | 0.72279 | 0.38196 | 0.32354 | -0.16445 | -0.14646 | -0.15429 | -0.084877 | 0.42126 | 0.29518 | 0.44947 | -0.10074 | -0.042592 | 121.5975 | 121.5274 | 121.5454 | 100.1235 | -121.6335 | 121.607 | 121.5912 | 121.6493 | 111.3032 | -121.8462
705.3906 | 121.875 | -121.5591 | 0.07782 | 1.4211e-13 | -0.015985 | 0.00062391 | 0.06144 | -0.004927 | 0.058046 | -0.0069437 | -0.002897 | -0.0032433 | 0.061492 | 0.019226 | 0.059481 | -120.8638 | -21.5043 | -121.2047 | 0.015501 | -0.054588 | -0.0366 | -121.5328 | -121.1654 | -10.3017 | -121.2869 | 0.011252 | -2.9e-05 | 0.058115 | -121.7409 | 0.026375 | -0.062319 | 0.69533 | 0.35449 | 0.32812 | -0.13241 | -0.11442 | -0.18176 | -0.066568 | 0.39379 | 0.27229 | 0.45405 | -0.077849 | -0.019705 | 121.5746 | 121.5046 | 121.5225 | 100.0549 | -121.6106 | 121.5704 | 121.5591 | 121.6173 | 111.2574 | -121.8187
707.0625 | 121.8292 | -121.5637 | 0.086975 | 1.4211e-13 | -0.015985 | 0.00062391 | 0.061227 | -0.0051408 | 0.057832 | 0.0083173 | -0.002897 | -0.0034569 | 0.061278 | 0.019226 | 0.059481 | -120.8684 | -21.5363 | -121.2001 | 0.010922 | -0.050009 | -0.041178 | -121.5328 | -121.1699 | -10.3292 | -121.2869 | 0.006674 | -2.9e-05 | 0.058115 | -121.7501 | 0.030953 | -0.076053 | 0.69533 | 0.36365 | 0.33269 | -0.13698 | -0.12815 | -0.18634 | -0.080301 | 0.39379 | 0.27687 | 0.46321 | -0.087004 | -0.02886 | 121.5746 | 121.5137 | 121.5225 | 100.0274 | -121.6197 | 121.5704 | 121.5637 | 121.6218 | 111.2345 | -121.837
708.8125 | 121.8613 | -121.5317 | 0.086975 | 1.4211e-13 | -0.015985 | 0.00062391 | 0.061227 | -0.004927 | 0.058046 | -0.0069437 | -0.0031106 | -0.0030297 | 0.061065 | 0.019226 | 0.059267 | -120.8684 | -21.5775 | -121.2001 | 0.006344 | -0.054588 | -0.032021 | -121.5328 | -121.1608 | -10.3704 | -121.2823 | 0.015831 | -0.009187 | 0.067272 | -121.7409 | -0.001091 | -0.080631 | 0.66329 | 0.3316 | 0.33269 | -0.14156 | -0.119 | -0.20923 | -0.071144 | 0.3709 | 0.2494 | 0.45863 | -0.096162 | -0.019703 | 121.538 | 121.4771 | 121.4997 | 99.9541 | -121.6197 | 121.5475 | 121.5225 | 121.5989 | 111.1613 | -121.8279
710.4844 | 121.8292 | -121.5408 | 0.07782 | 1.4211e-13 | -0.015985 | 0.00083771 | 0.06144 | -0.0053544 | 0.058046 | -0.0069437 | -0.002897 | -0.0032433 | 0.061065 | 0.01944 | 0.059267 | -120.8638 | -21.6096 | -121.2047 | 0.010922 | -0.04543 | -0.032021 | -121.5282 | -121.1699 | -10.3933 | -121.2914 | 0.011252 | -2.9e-05 | 0.067272 | -121.7409 | 0.012644 | -0.066898 | 0.67702 | 0.33618 | 0.32354 | -0.12325 | -0.10984 | -0.20007 | -0.066568 | 0.3709 | 0.2494 | 0.44947 | -0.077849 | -0.010548 | 121.5518 | 121.4954 | 121.5088 | 99.9312 | -121.606 | 121.5521 | 121.5408 | 121.6081 | 111.1475 | -121.8187
712.1562 | 121.8338 | -121.5088 | 0.10071 | 1.4211e-13 | -0.016199 | 0.0010513 | 0.061227 | -0.004927 | 0.057832 | 0.0083173 | -0.002897 | -0.0028161 | 0.060851 | 0.019226 | 0.059695 | -120.873 | -21.6462 | -121.2001 | 0.006344 | -0.050009 | -0.0366 | -121.5373 | -121.1745 | -10.4254 | -121.2823 | 0.006674 | -2.9e-05 | 0.062694 | -121.7363 | -0.028557 | -0.094364 | 0.63582 | 0.30871 | 0.33727 | -0.15072 | -0.13731 | -0.22754 | -0.094034 | 0.33428 | 0.22652 | 0.45405 | -0.10074 | -0.038014 | 121.5151 | 121.4588 | 121.4722 | 99.8626 | -121.6381 | 121.5155 | 121.5088 | 121.5715 | 111.0834 | -121.837
713.8906 | 121.8704 | -121.5363 | 0.07782 | 1.4211e-13 | -0.015771 | 0.00083771 | 0.06144 | -0.004927 | 0.057832 | -0.0069437 | -0.002897 | -0.0032433 | 0.061278 | 0.019013 | 0.059481 | -120.8638 | -21.6691 | -121.2092 | 0.006344 | -0.054588 | -0.041178 | -121.5328 | -121.1608 | -10.462 | -121.2914 | 0.011252 | 0.004549 | 0.062694 | -121.7501 | 0.003487 | -0.071476 | 0.67244 | 0.32702 | 0.32354 | -0.13241 | -0.119 | -0.21381 | -0.066568 | 0.37548 | 0.24482 | 0.45863 | -0.073271 | -0.015126 | 121.5426 | 121.4817 | 121.4951 | 99.8671 | -121.6106 | 121.5475 | 121.5408 | 121.5989 | 111.0743 | -121.8279
715.625 | 121.756 | -121.5591 | 0.11444 | 1.4211e-13 | -0.016199 | 0.00062391 | 0.06144 | -0.004927 | 0.057832 | 0.0083173 | -0.002897 | -0.0032433 | 0.061492 | 0.01944 | 0.05884 | -120.8592 | -21.6829 | -121.1955 | 0.006344 | -0.054588 | -0.041178 | -121.5328 | -121.1745 | -10.4895 | -121.2869 | 0.006674 | 0.004549 | 0.062694 | -121.7409 | 0.026375 | -0.1081 | 0.69991 | 0.36365 | 0.33727 | -0.16903 | -0.15562 | -0.18176 | -0.10777 | 0.38463 | 0.27229 | 0.45405 | -0.10989 | -0.051747 | 121.5655 | 121.5046 | 121.518 | 99.8763 | -121.6472 | 121.5658 | 121.5637 | 121.6218 | 111.0697 | -121.8553
717.3594 | 121.843 | -121.55 | 0.07782 | 1.4211e-13 | -0.015985 | 0.00062391 | 0.06144 | -0.0051408 | 0.057618 | 0.00068675 | -0.0031106 | -0.0030297 | 0.061278 | 0.01944 | 0.059267 | -120.8592 | -21.7286 | -121.2047 | 0.006344 | -0.054588 | -0.041178 | -121.5373 | -121.1699 | -10.5215 | -121.2823 | 0.015831 | -0.004608 | 0.062694 | -121.7409 | 0.012642 | -0.071476 | 0.69075 | 0.34534 | 0.33269 | -0.13241 | -0.119 | -0.19092 | -0.061989 | 0.38006 | 0.26771 | 0.45863 | -0.082428 | -0.015126 | 121.5563 | 121.4954 | 121.5088 | 99.8213 | -121.6152 | 121.5658 | 121.5454 | 121.6127 | 111.0285 | -121.8187
719.0312 | 121.8567 | -121.5408 | 0.086975 | 1.4211e-13 | -0.016199 | 0.00083771 | 0.061227 | -0.0047134 | 0.057618 | -0.0069437 | -0.0026832 | -0.0030297 | 0.060638 | 0.019013 | 0.059481 | -120.8638 | -21.747 | -121.2001 | 0.001765 | -0.059167 | -0.041178 | -121.5282 | -121.1654 | -10.5398 | -121.2869 | 0.011252 | 0.004549 | 0.058115 | -121.7455 | 0.012644 | -0.08521 | 0.67702 | 0.34076 | 0.32811 | -0.14614 | -0.12815 | -0.20465 | -0.075723 | 0.37548 | 0.25398 | 0.45863 | -0.082426 | -0.02886 | 121.5426 | 121.4817 | 121.4997 | 99.7939 | -121.6152 | 121.5521 | 121.5454 | 121.5989 | 111.001 | -121.8325
720.7656 | 121.7972 | -121.5546 | 0.10071 | 1.4211e-13 | -0.015985 | 0.00062391 | 0.061227 | -0.004927 | 0.057832 | 0.0083173 | -0.002897 | -0.0032433 | 0.060851 | 0.01944 | 0.059054 | -120.8592 | -21.7561 | -121.2047 | 0.006344 | -0.050009 | -0.041178 | -121.5328 | -121.1699 | -10.5536 | -121.2869 | 0.006674 | -0.004608 | 0.058115 | -121.7409 | 0.021797 | -0.094364 | 0.69533 | 0.34991 | 0.32812 | -0.15072 | -0.14189 | -0.18634 | -0.094034 | 0.38464 | 0.26771 | 0.45405 | -0.10532 | -0.042593 | 121.5609 | 121.5046 | 121.5134 | 99.7985 | -121.6335 | 121.5612 | 121.55 | 121.6127 | 111.001 | -121.8416
722.5 | 121.7377 | -121.582 | 0.11444 | 1.4211e-13 | -0.015771 | 0.0010513 | 0.061227 | -0.0051408 | 0.057618 | 0.0083173 | -0.0026832 | -0.0032433 | 0.061278 | 0.019226 | 0.059267 | -120.8638 | -21.8248 | -121.2047 | 0.006344 | -0.054588 | -0.0366 | -121.5373 | -121.1654 | -10.5856 | -121.2869 | 0.020409 | 0.009128 | 0.062694 | -121.7455 | 0.044685 | -0.1081 | 0.71822 | 0.37738 | 0.33269 | -0.16903 | -0.15104 | -0.16345 | -0.094032 | 0.41668 | 0.29518 | 0.45863 | -0.10531 | -0.051747 | 121.5884 | 121.5274 | 121.5454 | 99.7572 | -121.6518 | 121.6024 | 121.5912 | 121.6447 | 110.9964 | -121.8599
724.1719 | 121.7789 | -121.55 | 0.11902 | 1.4211e-13 | -0.016199 | 0.00062391 | 0.061654 | -0.0047134 | 0.057405 | -0.014574 | -0.002897 | -0.0034569 | 0.061492 | 0.01944 | 0.059267 | -120.8592 | -21.8477 | -121.2092 | 0.010922 | -0.054588 | -0.032021 | -121.5282 | -121.1699 | -10.6177 | -121.2869 | 0.011252 | 0.009128 | 0.067272 | -121.7501 | 0.021799 | -0.1081 | 0.69075 | 0.34076 | 0.31896 | -0.17361 | -0.15104 | -0.20007 | -0.10777 | 0.38006 | 0.26314 | 0.46321 | -0.10989 | -0.051747 | 121.5609 | 121.4954 | 121.518 | 99.7023 | -121.6472 | 121.5612 | 121.5591 | 121.6173 | 110.9323 | -121.8691
725.9062 | 121.8155 | -121.5225 | 0.10071 | 1.4211e-13 | -0.016199 | 0.0010513 | 0.06144 | -0.0051408 | 0.057618 | -0.0069437 | -0.002897 | -0.0034569 | 0.061278 | 0.01944 | 0.059481 | -120.8638 | -21.8477 | -121.2047 | 0.006344 | -0.050009 | -0.0366 | -121.5328 | -121.1654 | -10.6314 | -121.2869 | 0.015831 | 0.004549 | 0.062694 | -121.7501 | -0.010246 | -0.094364 | 0.65871 | 0.31787 | 0.32812 | -0.15072 | -0.13731 | -0.22754 | -0.084877 | 0.35717 | 0.23567 | 0.46321 | -0.096159 | -0.038014 | 121.5289 | 121.4725 | 121.4859 | 99.6748 | -121.6335 | 121.5384 | 121.5271 | 121.5852 | 110.8911 | -121.8508
727.6406 | 121.7422 | -121.5729 | 0.10529 | 1.4211e-13 | -0.016412 | 0.0010513 | 0.06144 | -0.004927 | 0.057618 | 0.00068675 | -0.0033242 | -0.0034569 | 0.061278 | 0.019226 | 0.059267 | -120.8592 | -21.8797 | -121.2092 | 0.010922 | -0.054588 | -0.032021 | -121.5328 | -121.1654 | -10.6543 | -121.2777 | 0.002095 | -2.9e-05 | 0.062694 | -121.7455 | 0.040108 | -0.094364 | 0.71364 | 0.36365 | 0.32354 | -0.15987 | -0.13731 | -0.17261 | -0.10319 | 0.40752 | 0.29518 | 0.46779 | -0.10532 | -0.042592 | 121.5838 | 121.5183 | 121.5409 | 99.6931 | -121.6381 | 121.575 | 121.5728 | 121.6356 | 110.9186 | -121.8508
729.3125 | 121.8063 | -121.5317 | 0.11902 | 1.4211e-13 | -0.016199 | 0.00083771 | 0.06144 | -0.0047134 | 0.058046 | -0.0069437 | -0.002897 | -0.0034569 | 0.061065 | 0.019654 | 0.059267 | -120.8318 | -21.9026 | -121.1772 | 0.029236 | -0.027115 | -0.013707 | -121.519 | -121.1333 | -10.6543 | -121.2548 | 0.038723 | 0.027442 | 0.081008 | -121.7226 | 0.012646 | -0.089783 | 0.69991 | 0.3545 | 0.34185 | -0.14613 | -0.13273 | -0.19091 | -0.080296 | 0.39838 | 0.27688 | 0.46779 | -0.091577 | -0.038011 | 121.5609 | 121.5046 | 121.518 | 99.629 | -121.638 | 121.5704 | 121.5591 | 121.6127 | 110.8774 | -121.8416
731 | 121.8704 | -121.5179 | 0.091553 | 1.4211e-13 | -0.016199 | 0.00062391 | 0.06144 | -0.0051408 | 0.057832 | -0.0069437 | -0.0033242 | -0.0032433 | 0.061065 | 0.01944 | 0.059267 | -120.8318 | -21.8843 | -121.1772 | 0.029236 | -0.022536 | -0.013707 | -121.5007 | -121.1333 | -10.6726 | -121.2548 | 0.043302 | 0.0366 | 0.085587 | -121.718 | 0.017229 | -0.062317 | 0.68618 | 0.34076 | 0.32353 | -0.11409 | -0.10526 | -0.20006 | -0.048251 | 0.38464 | 0.26314 | 0.46321 | -0.054953 | -0.005966 | 121.5472 | 121.4954 | 121.5042 | 99.6336 | -121.5923 | 121.5612 | 121.5545 | 121.6035 | 110.8453 | -121.8096
732.7344 | 121.8018 | -121.5363 | 0.14191 | 1.4211e-13 | -0.016412 | 0.00083771 | 0.06144 | -0.004927 | 0.057832 | 0.00068675 | -0.002897 | -0.0034569 | 0.061065 | 0.019654 | 0.059054 | -120.8226 | -21.9164 | -121.168 | 0.029236 | -0.022536 | -0.009128 | -121.5007 | -121.1333 | -10.6955 | -121.2411 | 0.043302 | 0.027442 | 0.085587 | -121.718 | 0.03554 | -0.11267 | 0.71365 | 0.36823 | 0.33269 | -0.16444 | -0.15104 | -0.18175 | -0.098605 | 0.40295 | 0.29519 | 0.47694 | -0.11447 | -0.05632 | 121.5655 | 121.5137 | 121.5271 | 99.6199 | -121.6426 | 121.5796 | 121.5637 | 121.6218 | 110.8407 | -121.8599
734.4688 | 121.7834 | -121.5317 | 0.13275 | 1.4211e-13 | -0.016412 | 0.00062391 | 0.06144 | -0.005568 | 0.058046 | 0.0083173 | -0.0031106 | -0.0030297 | 0.061492 | 0.01944 | 0.059267 | -120.8226 | -21.985 | -121.1726 | 0.038393 | -0.027115 | -0.018285 | -121.5007 | -121.1287 | -10.7092 | -121.2456 | 0.043302 | 0.022864 | 0.094744 | -121.7272 | 0.030962 | -0.094358 | 0.70907 | 0.35907 | 0.32811 | -0.15987 | -0.15104 | -0.19549 | -0.089449 | 0.40296 | 0.28603 | 0.48152 | -0.10989 | -0.038007 | 121.5701 | 121.5046 | 121.5134 | 99.5466 | -121.6335 | 121.575 | 121.5545 | 121.6264 | 110.8224 | -121.8599
736.1406 | 121.7468 | -121.5454 | 0.13733 | 1.4211e-13 | -0.016199 | 0.00083771 | 0.061013 | -0.0051408 | 0.057618 | 0.00068675 | -0.0031106 | -0.0028161 | 0.061278 | 0.01944 | 0.059054 | -120.8226 | -22.0171 | -121.168 | 0.033814 | -0.027115 | -0.013707 | -121.5007 | -121.1333 | -10.7413 | -121.2456 | 0.043302 | 0.022864 | 0.090166 | -121.718 | 0.044695 | -0.10352 | 0.7228 | 0.37738 | 0.33269 | -0.16444 | -0.15104 | -0.1726 | -0.094027 | 0.41211 | 0.29977 | 0.47236 | -0.11447 | -0.047163 | 121.5792 | 121.5183 | 121.5317 | 99.5283 | -121.638 | 121.5887 | 121.5683 | 121.6356 | 110.8041 | -121.8553
737.875 | 121.7743 | -121.5271 | 0.14191 | 1.4211e-13 | -0.016412 | 0.0012649 | 0.061013 | -0.004927 | 0.057618 | 0.0083173 | -0.0033242 | -0.0032433 | 0.060851 | 0.019867 | 0.059481 | -120.818 | -22.0537 | -121.1634 | 0.033814 | -0.022536 | -0.004549 | -121.4961 | -121.1241 | -10.7688 | -121.2411 | 0.038723 | 0.032021 | 0.094744 | -121.718 | 0.030964 | -0.10809 | 0.70907 | 0.36365 | 0.33269 | -0.16444 | -0.14646 | -0.19091 | -0.10318 | 0.40296 | 0.28603 | 0.47694 | -0.10989 | -0.047163 | 121.5609 | 121.5046 | 121.5226 | 99.4734 | -121.638 | 121.5658 | 121.5591 | 121.6218 | 110.7583 | -121.8599
739.5625 | 121.7834 | -121.5225 | 0.11902 | 1.4211e-13 | -0.016199 | 0.0010513 | 0.061013 | -0.0053544 | 0.057618 | 0.0083173 | -0.002897 | -0.0034569 | 0.061492 | 0.019226 | 0.059267 | -120.8226 | -22.0766 | -121.1589 | 0.033814 | -0.022536 | -0.009128 | -121.4961 | -121.1241 | -10.8008 | -121.2411 | 0.043302 | 0.027442 | 0.090166 | -121.7272 | 0.026386 | -0.085205 | 0.69991 | 0.36365 | 0.33727 | -0.14155 | -0.12815 | -0.20464 | -0.075717 | 0.39838 | 0.28146 | 0.4861 | -0.091577 | -0.028853 | 121.5563 | 121.5 | 121.5134 | 99.4459 | -121.6152 | 121.5658 | 121.55 | 121.6127 | 110.7217 | -121.8462
741.2969 | 121.8842 | -121.4996 | 0.10986 | 1.4211e-13 | -0.016626 | 0.00083771 | 0.060799 | -0.0053544 | 0.057832 | 0.00068675 | -0.0031106 | -0.0034569 | 0.061065 | 0.01944 | 0.05884 | -120.818 | -22.0949 | -121.168 | 0.033814 | -0.027115 | -0.018285 | -121.4961 | -121.1287 | -10.8237 | -121.2365 | 0.043302 | 0.032021 | 0.085587 | -121.7226 | 0.003498 | -0.076049 | 0.6816 | 0.33161 | 0.32811 | -0.13698 | -0.12815 | -0.22295 | -0.066561 | 0.37091 | 0.26315 | 0.4861 | -0.077842 | -0.024276 | 121.5334 | 121.4725 | 121.4813 | 99.4047 | -121.606 | 121.5429 | 121.5317 | 121.5852 | 110.6759 | -121.8325
743.0312 | 121.7514 | -121.5408 | 0.11902 | 1.4211e-13 | -0.016626 | 0.00083771 | 0.061013 | -0.0051408 | 0.057832 | 0.0083173 | -0.002897 | -0.0028161 | 0.060851 | 0.019867 | 0.059054 | -120.818 | -22.1041 | -121.1589 | 0.038393 | -0.031693 | -0.009128 | -121.4916 | -121.1241 | -10.8329 | -121.2456 | 0.043302 | 0.032021 | 0.094744 | -121.7134 | 0.049276 | -0.080626 | 0.7228 | 0.38196 | 0.33269 | -0.15071 | -0.12815 | -0.1726 | -0.075717 | 0.41669 | 0.29519 | 0.46779 | -0.086998 | -0.024275 | 121.5792 | 121.5091 | 121.5317 | 99.4367 | -121.6106 | 121.5841 | 121.5729 | 121.6356 | 110.708 | -121.8324
744.7812 | 121.7697 | -121.5134 | 0.14191 | 1.4211e-13 | -0.016626 | 0.00083771 | 0.061013 | -0.0053544 | 0.057618 | -0.014574 | -0.002897 | -0.0032433 | 0.061278 | 0.019654 | 0.059054 | -120.8043 | -22.0995 | -121.1451 | 0.047549 | -0.017957 | 2.9e-05 | -121.5099 | -121.115 | -10.8558 | -121.2273 | 0.052459 | 0.041178 | 0.1039 | -121.7043 | 0.003494 | -0.094358 | 0.70907 | 0.36823 | 0.36474 | -0.15986 | -0.14188 | -0.19091 | -0.089448 | 0.39838 | 0.28604 | 0.47694 | -0.10073 | -0.038006 | 121.5609 | 121.4954 | 121.5134 | 99.4139 | -121.6518 | 121.5658 | 121.5545 | 121.6173 | 110.6576 | -121.8462
746.5312 | 121.7102 | -121.4813 | 0.17853 | 1.4211e-13 | -0.01684 | 0.0010513 | 0.061227 | -0.004927 | 0.058046 | 0.00068675 | -0.002897 | -0.0032433 | 0.061278 | 0.01944 | 0.059267 | -120.7997 | -22.1407 | -121.1497 | 0.047549 | -0.00422 | -0.004549 | -121.4732 | -121.1058 | -10.8878 | -121.2273 | 0.061616 | 0.050335 | 0.099323 | -121.6447 | 0.008082 | -0.13098 | 0.68161 | 0.33161 | 0.32353 | -0.18275 | -0.18308 | -0.16343 | -0.11691 | 0.3755 | 0.25399 | 0.41742 | -0.12819 | -0.079205 | 121.5289 | 121.4771 | 121.4768 | 99.3406 | -121.6518 | 121.5429 | 121.5317 | 121.5806 | 110.5935 | -121.8233
748.2031 | 121.7377 | -121.4859 | 0.1236 | 1.4211e-13 | -0.016412 | 0.00083771 | 0.061013 | -0.0051408 | 0.058046 | 0.00068675 | -0.0031106 | -0.0032433 | 0.061278 | 0.019654 | 0.059267 | -120.8318 | -22.1545 | -121.1726 | 0.029236 | -0.040851 | -0.018285 | -121.5053 | -121.1287 | -10.9107 | -121.2456 | 0.020409 | 0.027442 | 0.071851 | -121.7363 | -0.019393 | -0.09436 | 0.65414 | 0.3133 | 0.33269 | -0.16445 | -0.14188 | -0.25042 | -0.10319 | 0.35718 | 0.24026 | 0.49068 | -0.096154 | -0.051745 | 121.5151 | 121.445 | 121.4676 | 99.3314 | -121.6289 | 121.5063 | 121.5133 | 121.5578 | 110.5752 | -121.8599
749.9375 | 121.7743 | -121.4859 | 0.10529 | 1.4211e-13 | -0.016626 | 0.00062391 | 0.061013 | -0.0051408 | 0.058259 | 0.00068675 | -0.002897 | -0.0036707 | 0.061278 | 0.019867 | 0.059267 | -120.7997 | -22.1911 | -121.1406 | 0.038393 | -0.013378 | -0.009128 | -121.5282 | -121.115 | -10.9061 | -121.2273 | 0.052459 | 0.050335 | 0.099323 | -121.7134 | -0.042288 | -0.066893 | 0.68618 | 0.34534 | 0.38763 | -0.11866 | -0.11441 | -0.22753 | -0.052827 | 0.37092 | 0.25857 | 0.4861 | -0.054951 | -0.005963 | 121.5243 | 121.4725 | 121.4768 | 99.2948 | -121.6335 | 121.5384 | 121.5362 | 121.5852 | 110.5798 | -121.8187
751.9062 | 121.6919 | -120.5933 | 0.92468 | 1.4211e-13 | -0.016412 | 0.00083771 | 0.061013 | -0.0053544 | 0.058046 | 0.0083173 | -0.0026832 | -0.0032433 | 0.061065 | 0.019654 | 0.059481 | -119.9481 | -21.9209 | -120.2936 | 0.75262 | 0.72841 | 0.74176 | -120.6811 | -120.2496 | -10.7321 | -120.3665 | 0.7896 | 0.78291 | 0.85021 | -120.8526 | -0.087826 | -0.17206 | 0.64513 | 0.29969 | 0.38751 | -0.19627 | -0.18292 | -0.25935 | -0.13509 | 0.34365 | 0.22673 | 0.48608 | -0.14177 | -0.074469 | 121.3459 | 121.3217 | 121.335 | 98.6723 | -121.6058 | 121.3829 | 121.3762 | 121.4435 | 109.8611 | -121.7773
755.4531 | 121.463 | -119.7418 | 1.4648 | 1.4211e-13 | -0.01684 | 0.00041031 | 0.060586 | -0.005568 | 0.057832 | -0.0069437 | -0.002897 | -0.0034569 | 0.060851 | 0.019654 | 0.059054 | -119.0645 | -21.6233 | -119.4054 | 1.3524 | 1.3374 | 1.337 | -119.7287 | -119.3568 | -10.5994 | -119.4874 | 1.4031 | 1.3827 | 1.4546 | -119.9643 | 0.01315 | -0.11245 | 0.67731 | 0.33643 | 0.32328 | -0.12744 | -0.12786 | -0.2225 | -0.061729 | 0.38506 | 0.2544 | 0.4769 | -0.082135 | -0.010255 | 121.0942 | 121.0792 | 121.0788 | 98.1185 | -121.1935 | 121.1449 | 121.1245 | 121.1964 | 109.1425 | -121.4292
759.0781 | 121.2982 | -119.7052 | 1.4557 | 1.4211e-13 | -0.01684 | 0.00062391 | 0.060799 | -0.0051408 | 0.057618 | -0.0069437 | -0.0031106 | -0.0034569 | 0.060851 | 0.019867 | 0.05884 | -119.0554 | -21.6325 | -119.355 | 1.3936 | 1.3054 | 1.3232 | -119.7378 | -119.3522 | -10.6543 | -119.4325 | 1.3802 | 1.369 | 1.4317 | -119.9231 | -0.032629 | -0.062093 | 0.64985 | 0.35017 | 0.3828 | -0.15034 | -0.13244 | -0.21791 | -0.075466 | 0.35302 | 0.27273 | 0.49064 | -0.086715 | -0.023992 | 121.0988 | 121.0106 | 121.0284 | 98.0727 | -121.1935 | 121.0854 | 121.0742 | 121.1369 | 109.0509 | -121.3788
764.7344 | 121.7377 | -1.3138 | 120.1126 | 1.4211e-13 | -0.016412 | 0.0010513 | 0.06144 | -0.0057818 | 0.058046 | -0.0069437 | -0.0020424 | -0.0028161 | 0.061919 | 0.019867 | 0.058199 | -1.0566 | 21.2095 | -1.2308 | 120.331 | 119.9544 | 119.7946 | -0.10427 | -1.1528 | 12.1385 | -1.2834 | 119.9312 | 120.1196 | 120.1915 | -0.008469 | 1.2095 | 0.21834 | 0.25722 | 0.082972 | -1.1265 | -0.15816 | -0.31802 | 1.3053 | -0.18141 | 0.16099 | 0.030337 | -1.275 | 0.006998 | 0.078878 | 121.6447 | 121.2682 | 121.1084 | 22.5233 | -120.2169 | 121.245 | 121.4334 | 121.5053 | 13.4523 | -120.1211
766.4844 | 121.6965 | -0.5127 | 120.8679 | 1.4211e-13 | -0.01684 | 0.0010513 | 0.06144 | -0.0057818 | 0.058473 | -0.22823 | -0.0024696 | -0.0026023 | 0.061919 | 0.019867 | 0.057986 | -0.44763 | 21.6536 | -0.63106 | 120.8117 | 120.4581 | 120.2479 | -0.88269 | -0.53466 | 12.4544 | -0.66532 | 120.4165 | 120.5958 | 120.7134 | -0.95171 | -0.36999 | -0.056234 | 0.065061 | -0.11836 | 0.25163 | -0.40979 | -0.62005 | -0.43901 | -0.4514 | -0.021966 | -0.15263 | 0.28639 | -0.27214 | -0.15447 | 121.3244 | 120.9708 | 120.7606 | 22.1663 | -121.7506 | 120.9292 | 121.1085 | 121.2261 | 12.9671 | -121.8196
768.1719 | 121.6232 | -0.22888 | 119.4626 | 1.4211e-13 | -0.016626 | 0.00083771 | 0.061654 | -0.0053544 | 0.058473 | -0.23586 | -0.002256 | -0.0026023 | 0.061919 | 0.019654 | 0.058627 | -0.085942 | 21.7223 | -0.24648 | 121.2512 | 120.9298 | 120.7652 | -0.30574 | -0.17294 | 12.4224 | -0.29444 | 120.9018 | 121.0857 | 121.1576 | -0.36562 | -0.076858 | 1.7886 | 0.14294 | -0.017598 | 0.05926 | 1.4672 | 1.3027 | -0.13674 | 1.4393 | 0.055939 | -0.065562 | 0.071173 | 1.6231 | 1.695 | 121.4801 | 121.1586 | 120.9941 | 21.9512 | -119.7683 | 121.1307 | 121.3146 | 121.3865 | 12.6513 | -119.8282
769.9062 | 121.7468 | -0.59052 | 120.5795 | 1.4211e-13 | -0.016626 | 0.00083771 | 0.061227 | -0.0057818 | 0.058259 | -0.23586 | -0.0024696 | -0.0021751 | 0.061919 | 0.019867 | 0.057986 | -0.031001 | 21.7635 | -0.19612 | 121.3245 | 121.003 | 120.8431 | -0.25079 | -0.12716 | 12.4499 | -0.24866 | 120.9751 | 121.1681 | 121.2354 | -0.31525 | 0.33972 | 0.74494 | 0.55951 | 0.3944 | 0.054674 | 0.42349 | 0.26356 | 0.27527 | 0.39557 | 0.46336 | 0.34186 | 0.066593 | 0.58858 | 0.65588 | 121.915 | 121.5935 | 121.4336 | 22.354 | -120.8303 | 121.5656 | 121.7586 | 121.8259 | 13.0404 | -120.8948
771.6406 | 121.6324 | -0.29755 | 120.7169 | 1.4211e-13 | -0.016626 | 0.00083771 | 0.061227 | -0.0057818 | 0.058473 | -0.2206 | -0.002256 | -0.0026023 | 0.061492 | 0.019867 | 0.058199 | -0.026423 | 21.7406 | -0.17781 | 121.2695 | 120.9481 | 120.7836 | -0.24163 | -0.11342 | 12.4132 | -0.23492 | 120.9202 | 121.104 | 121.1805 | -0.29236 | 0.055911 | 0.55267 | 0.27112 | 0.11974 | 0.063829 | 0.23121 | 0.066706 | 0.00519 | 0.20329 | 0.18413 | 0.062625 | 0.057435 | 0.38715 | 0.46361 | 121.5671 | 121.2456 | 121.0811 | 22.0382 | -120.9585 | 121.2177 | 121.4016 | 121.478 | 12.7108 | -121.0092
773.375 | 121.7743 | -0.1831 | 121.3028 | 1.4211e-13 | -0.017053 | 0.0010513 | 0.06144 | -0.0059954 | 0.058046 | -0.2206 | -0.0020424 | -0.0023887 | 0.061706 | 0.019654 | 0.057986 | 0.05141 | 21.8322 | -0.10913 | 121.4069 | 121.0305 | 120.9301 | -0.1409 | -0.035582 | 12.4773 | -0.15708 | 121.0529 | 121.2459 | 121.24 | -0.23283 | 0.042206 | 0.10408 | 0.23451 | 0.073973 | 0.031767 | -0.2723 | -0.37272 | -0.049726 | -0.24987 | 0.14752 | 0.026022 | 0.075748 | -0.056851 | -0.062807 | 121.59 | 121.2136 | 121.1132 | 22.0153 | -121.4437 | 121.236 | 121.429 | 121.4231 | 12.6604 | -121.5356
775.0469 | 121.7102 | -0.18768 | 121.3531 | 1.4211e-13 | -0.016626 | 0.0010513 | 0.061227 | -0.005568 | 0.058259 | -0.21297 | -0.0024696 | -0.0023887 | 0.061706 | 0.019867 | 0.058413 | 0.060567 | 21.878 | -0.095397 | 121.4252 | 121.0534 | 120.9576 | -0.13632 | -0.031003 | 12.4361 | -0.1525 | 121.0804 | 121.2734 | 121.2766 | -0.20994 | 0.051363 | 0.072041 | 0.24825 | 0.092286 | 0.040923 | -0.29976 | -0.3956 | -0.022254 | -0.27275 | 0.15668 | 0.035179 | 0.057433 | -0.079733 | -0.076532 | 121.6129 | 121.2411 | 121.1452 | 22.0657 | -121.4895 | 121.2681 | 121.4611 | 121.4643 | 12.6238 | -121.5631
776.7969 | 121.7331 | -0.1831 | 121.2891 | 1.4211e-13 | -0.016626 | 0.00062391 | 0.06144 | -0.0059954 | 0.058259 | -0.22823 | -0.0024696 | -0.0023887 | 0.061706 | 0.019867 | 0.058413 | -0.67655 | 21.5437 | -0.85081 | 120.6194 | 120.2521 | 120.1242 | -0.86895 | -0.74986 | 12.3217 | -0.87594 | 120.2792 | 120.463 | 120.5074 | -0.92423 | -0.68584 | -0.66967 | -0.49345 | -0.66771 | 0.018135 | -1.037 | -1.1648 | -0.74113 | -1.0099 | -0.56676 | -0.69284 | 0.048292 | -0.82606 | -0.78165 | 120.8025 | 120.4352 | 120.3073 | 21.7268 | -122.158 | 120.4623 | 120.6461 | 120.6905 | 12.5048 | -122.2133
778.4688 | 121.5317 | -121.0556 | 0.21515 | 1.4211e-13 | -0.018122 | -1.7092e-05 | 0.060158 | -0.0053544 | 0.059328 | -0.21297 | -0.0033242 | -0.0026023 | 0.061278 | 0.019867 | 0.059695 | -120.4014 | -25.8494 | -120.6965 | 0.17117 | 0.087359 | 0.11449 | -121.0978 | -120.7075 | -13.255 | -120.7786 | 0.15776 | 0.14649 | 0.20463 | -121.2464 | -0.042167 | -0.043983 | 0.65421 | 0.35914 | 0.40131 | -0.12779 | -0.10066 | -0.19079 | -0.057385 | 0.34812 | 0.27699 | 0.46778 | -0.068663 | -0.010518 | 121.2268 | 121.143 | 121.1701 | 95.2062 | -121.3129 | 121.2134 | 121.2021 | 121.2602 | 107.8006 | -121.4615
780.1406 | 121.5591 | -121.1975 | 0.19226 | 1.4211e-13 | -0.017694 | 0.00019651 | 0.060158 | -0.005568 | 0.059541 | -0.23586 | -0.0035378 | -0.0023887 | 0.061492 | 0.020295 | 0.059695 | -120.5113 | -26.353 | -120.8247 | 0.1208 | 0.050727 | 0.077866 | -121.2214 | -120.8265 | -13.5664 | -120.9068 | 0.11656 | 0.10528 | 0.15884 | -121.3746 | -0.023891 | -0.071457 | 0.68623 | 0.37285 | 0.39675 | -0.14153 | -0.11439 | -0.17709 | -0.075704 | 0.37098 | 0.29069 | 0.46778 | -0.086982 | -0.033416 | 121.3183 | 121.2482 | 121.2754 | 94.8445 | -121.4137 | 121.3141 | 121.3028 | 121.3564 | 107.6312 | -121.5669
781.8906 | 121.701 | -121.2662 | 0.10986 | 1.4211e-13 | -0.017908 | 0.00019651 | 0.060158 | -0.0053544 | 0.059114 | -0.22823 | -0.0035378 | -0.0032433 | 0.060638 | 0.020295 | 0.059481 | -120.5937 | -26.6277 | -120.8979 | 0.084176 | 0.014096 | 0.027501 | -121.3038 | -120.9135 | -13.7816 | -120.9892 | 0.066194 | 0.059493 | 0.11306 | -121.4524 | -0.037647 | -0.025687 | 0.67249 | 0.36827 | 0.40591 | -0.095767 | -0.082362 | -0.18626 | -0.043669 | 0.35265 | 0.27694 | 0.4632 | -0.05037 | 0.003196 | 121.3504 | 121.2803 | 121.2937 | 94.6384 | -121.4137 | 121.3324 | 121.3257 | 121.3792 | 107.4846 | -121.5623
783.6406 | 121.7239 | -121.3394 | 0.086975 | 1.4211e-13 | -0.018122 | -1.7092e-05 | 0.060372 | -0.005568 | 0.059755 | -0.22823 | -0.0033242 | -0.0034569 | 0.060851 | 0.020295 | 0.059695 | -120.6441 | -26.8017 | -120.9437 | 0.047549 | -0.017957 | 0.013765 | -121.345 | -120.9547 | -13.951 | -121.0304 | 0.04788 | 0.032021 | 0.094744 | -121.4982 | -0.005615 | -0.039426 | 0.69537 | 0.39573 | 0.40134 | -0.10493 | -0.07321 | -0.15881 | -0.039095 | 0.38469 | 0.30897 | 0.46778 | -0.054954 | 0.007769 | 121.387 | 121.3215 | 121.3532 | 94.5377 | -121.432 | 121.3873 | 121.3714 | 121.4342 | 107.3884 | -121.5852
785.375 | 121.5958 | -121.3989 | 0.11902 | 1.4211e-13 | -0.018122 | 0.00019651 | 0.060372 | -0.0053544 | 0.059755 | -0.2206 | -0.0031106 | -0.0036707 | 0.060851 | 0.020295 | 0.059481 | -120.6853 | -26.9391 | -120.9895 | 0.020079 | -0.036272 | -0.009128 | -121.3862 | -121.0005 | -14.1158 | -121.0717 | 0.029566 | 0.022864 | 0.085587 | -121.5394 | 0.012684 | -0.09894 | 0.71367 | 0.40945 | 0.39677 | -0.15529 | -0.12815 | -0.14051 | -0.089453 | 0.39841 | 0.32727 | 0.46778 | -0.096155 | -0.033432 | 121.419 | 121.3627 | 121.3898 | 94.4598 | -121.5053 | 121.4285 | 121.4218 | 121.4845 | 107.2831 | -121.6585
787.0469 | 121.6782 | -121.3989 | 0.10071 | 1.4211e-13 | -0.017694 | -1.7092e-05 | 0.060158 | -0.0051408 | 0.059755 | -0.21297 | -0.0035378 | -0.0034569 | 0.060638 | 0.020508 | 0.059481 | -120.7081 | -27.0307 | -121.0032 | 0.015501 | -0.040851 | -0.018285 | -121.345 | -121.0097 | -14.2348 | -121.09 | 0.020409 | 0.018285 | 0.071851 | -121.5669 | 0.053894 | -0.085207 | 0.69078 | 0.39572 | 0.34183 | -0.14156 | -0.11899 | -0.16798 | -0.080299 | 0.38925 | 0.30896 | 0.47694 | -0.082423 | -0.028857 | 121.4144 | 121.3581 | 121.3806 | 94.3683 | -121.4457 | 121.4193 | 121.4172 | 121.4708 | 107.1641 | -121.6676
788.7812 | 121.6415 | -121.4264 | 0.10986 | 1.4211e-13 | -0.017908 | -1.7092e-05 | 0.060586 | -0.005568 | 0.059328 | -0.23586 | -0.0033242 | -0.0036707 | 0.060851 | 0.020508 | 0.059481 | -120.7173 | -27.1589 | -121.0215 | 0.015501 | -0.040851 | -0.022864 | -121.3542 | -121.0234 | -14.3081 | -121.1037 | 0.020409 | 0.013707 | 0.071851 | -121.5761 | 0.072203 | -0.094362 | 0.70909 | 0.40487 | 0.33267 | -0.15071 | -0.13273 | -0.14967 | -0.089454 | 0.40298 | 0.32269 | 0.47236 | -0.096156 | -0.038012 | 121.4419 | 121.3855 | 121.4035 | 94.2675 | -121.4641 | 121.4468 | 121.4401 | 121.4982 | 107.1183 | -121.6859
790.5312 | 121.7514 | -121.3669 | 0.086975 | 1.4211e-13 | -0.017908 | -0.00023069 | 0.060372 | -0.0053544 | 0.059755 | -0.2206 | -0.0035378 | -0.0034569 | 0.060424 | 0.020295 | 0.059695 | -120.7265 | -27.2092 | -121.0307 | 0.015501 | -0.040851 | -0.022864 | -121.3679 | -120.9914 | -14.4043 | -121.1083 | 0.011252 | 0.013707 | 0.067272 | -121.5898 | -0.001044 | -0.071474 | 0.64042 | 0.33621 | 0.33725 | -0.12783 | -0.10984 | -0.22292 | -0.075723 | 0.37552 | 0.2586 | 0.48152 | -0.073268 | -0.019703 | 121.3824 | 121.326 | 121.344 | 94.1577 | -121.4549 | 121.3781 | 121.3806 | 121.4342 | 106.9626 | -121.6768
792.2031 | 121.6187 | -121.4493 | 0.12817 | 1.4211e-13 | -0.018549 | -1.7092e-05 | 0.060372 | -0.0051408 | 0.059541 | -0.22823 | -0.0033242 | -0.0034569 | 0.060851 | 0.020295 | 0.059481 | -120.7356 | -27.2642 | -121.0398 | 0.006344 | -0.040851 | -0.027442 | -121.3771 | -121.0051 | -14.4638 | -121.122 | 0.015831 | 0.022864 | 0.067272 | -121.5898 | 0.072196 | -0.12183 | 0.71366 | 0.40945 | 0.33725 | -0.16903 | -0.15562 | -0.14052 | -0.11234 | 0.44418 | 0.32726 | 0.46778 | -0.10531 | -0.060902 | 121.4556 | 121.4084 | 121.4218 | 94.1851 | -121.5053 | 121.4651 | 121.4721 | 121.5166 | 106.9855 | -121.718
793.9375 | 121.701 | -121.4081 | 0.091553 | 1.4211e-13 | -0.018122 | 0.00019651 | 0.060372 | -0.005568 | 0.059541 | -0.2206 | -0.0033242 | -0.0034569 | 0.060851 | 0.020081 | 0.059481 | -120.7402 | -27.3283 | -121.0444 | 0.015501 | -0.050009 | -0.022864 | -121.3771 | -121.0143 | -14.5142 | -121.122 | 0.020409 | 0.013707 | 0.071851 | -121.6035 | 0.030997 | -0.076052 | 0.66788 | 0.36367 | 0.33267 | -0.14156 | -0.11442 | -0.19546 | -0.071144 | 0.39383 | 0.28606 | 0.48152 | -0.077846 | -0.019702 | 121.4236 | 121.3581 | 121.3852 | 94.0798 | -121.4686 | 121.4285 | 121.4218 | 121.4799 | 106.8939 | -121.6951
795.6719 | 121.669 | -121.4584 | 0.10986 | 1.4211e-13 | -0.018549 | -1.7092e-05 | 0.060372 | -0.005568 | 0.059541 | -0.23586 | -0.0035378 | -0.0034569 | 0.060851 | 0.020295 | 0.059481 | -120.7494 | -27.3649 | -121.0627 | 0.006344 | -0.040851 | -0.022864 | -121.3908 | -121.0188 | -14.5737 | -121.1312 | 0.011252 | 0.013707 | 0.067272 | -121.6081 | 0.067614 | -0.10352 | 0.70908 | 0.39571 | 0.3281 | -0.15071 | -0.13273 | -0.14968 | -0.098611 | 0.4396 | 0.32726 | 0.47694 | -0.096156 | -0.042591 | 121.4648 | 121.4176 | 121.4356 | 94.0935 | -121.5007 | 121.4697 | 121.4721 | 121.5257 | 106.8848 | -121.718
797.3438 | 121.7148 | -121.4218 | 0.086975 | 1.4211e-13 | -0.017908 | -1.7092e-05 | 0.060158 | -0.0053544 | 0.059541 | -0.24349 | -0.0033242 | -0.0032433 | 0.060424 | 0.020081 | 0.059267 | -120.7494 | -27.4061 | -121.0719 | 0.020079 | -0.050009 | -0.013707 | -121.3908 | -121.0188 | -14.6057 | -121.1449 | 0.011252 | 0.009128 | 0.071851 | -121.631 | 0.030993 | -0.066896 | 0.67246 | 0.34993 | 0.31894 | -0.13698 | -0.10068 | -0.2092 | -0.075723 | 0.40298 | 0.2769 | 0.4861 | -0.077847 | -0.015124 | 121.4419 | 121.3718 | 121.4081 | 94.0157 | -121.4778 | 121.4331 | 121.4309 | 121.4937 | 106.8161 | -121.718
799.0781 | 121.6141 | -121.463 | 0.11902 | 1.4211e-13 | -0.017908 | -0.00023069 | 0.060586 | -0.0051408 | 0.059755 | -0.22823 | -0.0035378 | -0.0038843 | 0.060851 | 0.020081 | 0.059481 | -120.7585 | -27.4061 | -121.0673 | 0.010922 | -0.050009 | -0.027442 | -121.4046 | -121.028 | -14.6332 | -121.1449 | 0.011252 | 0.018285 | 0.062694 | -121.6219 | 0.058455 | -0.1081 | 0.7045 | 0.39571 | 0.33725 | -0.16903 | -0.14646 | -0.15884 | -0.10777 | 0.43502 | 0.3181 | 0.47694 | -0.10073 | -0.056325 | 121.4739 | 121.413 | 121.4356 | 94.0569 | -121.5236 | 121.4743 | 121.4813 | 121.5257 | 106.8298 | -121.7409
800.8281 | 121.669 | -121.4447 | 0.11444 | 1.4211e-13 | -0.018549 | 0.00019651 | 0.060586 | -0.005568 | 0.059755 | -0.2206 | -0.0033242 | -0.0032433 | 0.061065 | 0.020081 | 0.059908 | -120.7631 | -27.4794 | -121.0673 | 0.010922 | -0.04543 | -0.027442 | -121.4 | -121.0234 | -14.6607 | -121.1541 | 0.020409 | 0.009128 | 0.062694 | -121.6264 | 0.044723 | -0.10352 | 0.68161 | 0.3774 | 0.33268 | -0.15987 | -0.14188 | -0.18173 | -0.094032 | 0.42129 | 0.29063 | 0.47236 | -0.10531 | -0.051747 | 121.4556 | 121.3993 | 121.4173 | 93.9653 | -121.5144 | 121.4651 | 121.4538 | 121.5074 | 106.784 | -121.7409
802.5 | 121.6141 | -121.463 | 0.10986 | 1.4211e-13 | -0.018122 | 0.00019651 | 0.060372 | -0.0051408 | 0.059328 | -0.23586 | -0.0037514 | -0.0032433 | 0.061065 | 0.020508 | 0.059908 | -120.7585 | -27.4839 | -121.0719 | 0.015501 | -0.050009 | -0.022864 | -121.4046 | -121.0326 | -14.7248 | -121.1541 | 0.015831 | 0.013707 | 0.067272 | -121.6356 | 0.058455 | -0.094362 | 0.7045 | 0.39113 | 0.33268 | -0.15987 | -0.13273 | -0.17258 | -0.094032 | 0.43044 | 0.30894 | 0.48152 | -0.096156 | -0.042591 | 121.4785 | 121.413 | 121.4401 | 93.9791 | -121.5144 | 121.4788 | 121.4767 | 121.5303 | 106.7382 | -121.7455
804.2344 | 121.756 | -121.3989 | 0.086975 | 1.4211e-13 | -0.018122 | -1.7092e-05 | 0.060372 | -0.0053544 | 0.059541 | -0.21297 | -0.0035378 | -0.0034569 | 0.060851 | 0.020936 | 0.059695 | -120.7631 | -27.5114 | -121.081 | 0.010922 | -0.040851 | -0.032021 | -121.4137 | -121.0463 | -14.7385 | -121.1632 | 0.015831 | 0.004549 | 0.067272 | -121.6356 | -0.014789 | -0.076053 | 0.63584 | 0.31789 | 0.33268 | -0.12783 | -0.119 | -0.23666 | -0.071144 | 0.35262 | 0.2357 | 0.47236 | -0.082426 | -0.019703 | 121.4098 | 121.3581 | 121.3669 | 93.8875 | -121.5007 | 121.4148 | 121.4035 | 121.4662 | 106.6604 | -121.7226
805.9688 | 121.6461 | -121.4767 | 0.11444 | 1.4211e-13 | -0.018122 | -1.7092e-05 | 0.060158 | -0.005568 | 0.059541 | -0.2206 | -0.0035378 | -0.0034569 | 0.060638 | 0.020722 | 0.059267 | -120.7677 | -27.5572 | -121.0765 | 0.006344 | -0.050009 | -0.027442 | -121.4137 | -121.0417 | -14.7751 | -121.1632 | 0.020409 | 0.004549 | 0.058115 | -121.6447 | 0.063031 | -0.1081 | 0.70908 | 0.40029 | 0.33725 | -0.16445 | -0.14188 | -0.168 | -0.094032 | 0.43502 | 0.31352 | 0.48152 | -0.10989 | -0.056326 | 121.4831 | 121.4267 | 121.4493 | 93.9195 | -121.5282 | 121.4972 | 121.4813 | 121.5349 | 106.7016 | -121.7592
807.7031 | 121.7148 | -121.431 | 0.09613 | 1.4211e-13 | -0.018549 | -1.7092e-05 | 0.060586 | -0.0051408 | 0.059755 | -0.2206 | -0.0031106 | -0.0038843 | 0.060851 | 0.020508 | 0.059267 | -120.7722 | -27.5938 | -121.0902 | 0.010922 | -0.04543 | -0.032021 | -121.4183 | -121.0463 | -14.798 | -121.1724 | 0.020409 | 0.009128 | 0.067272 | -121.6447 | 0.012675 | -0.085208 | 0.65872 | 0.34077 | 0.3281 | -0.14156 | -0.12815 | -0.21378 | -0.075721 | 0.38466 | 0.25859 | 0.47236 | -0.087002 | -0.028858 | 121.4419 | 121.3855 | 121.3989 | 93.8371 | -121.5144 | 121.4514 | 121.4401 | 121.4982 | 106.6329 | -121.7409
809.4375 | 121.7239 | -121.4355 | 0.086975 | 1.4211e-13 | -0.018335 | 0.00019651 | 0.060372 | -0.0053544 | 0.059755 | -0.2206 | -0.0037514 | -0.0034569 | 0.060638 | 0.020295 | 0.059695 | -120.7768 | -27.5893 | -121.0902 | 0.010922 | -0.040851 | -0.032021 | -121.4183 | -121.0463 | -14.8163 | -121.1724 | 0.015831 | -2.9e-05 | 0.058115 | -121.6493 | 0.017253 | -0.076053 | 0.65872 | 0.34535 | 0.3281 | -0.12783 | -0.119 | -0.21378 | -0.071144 | 0.38924 | 0.26316 | 0.47694 | -0.087004 | -0.02886 | 121.4465 | 121.3947 | 121.4035 | 93.8463 | -121.5053 | 121.4514 | 121.4355 | 121.4937 | 106.6192 | -121.7363
811.1094 | 121.7148 | -121.4355 | 0.10071 | 1.4211e-13 | -0.018335 | 0.00019651 | 0.060586 | -0.005568 | 0.059541 | -0.2206 | -0.0035378 | -0.0036707 | 0.060851 | 0.020295 | 0.059267 | -120.7768 | -27.5938 | -121.0948 | 0.006344 | -0.050009 | -0.027442 | -121.4275 | -121.0463 | -14.853 | -121.1724 | 0.011252 | 0.004549 | 0.07643 | -121.6539 | 0.008095 | -0.094364 | 0.65872 | 0.34077 | 0.33268 | -0.15072 | -0.12815 | -0.21836 | -0.089456 | 0.38924 | 0.26316 | 0.48152 | -0.096159 | -0.024278 | 121.4419 | 121.3855 | 121.4081 | 93.8417 | -121.5282 | 121.4468 | 121.4401 | 121.512 | 106.5826 | -121.7546
812.8438 | 121.6507 | -121.4447 | 0.11902 | 1.4211e-13 | -0.018549 | -1.7092e-05 | 0.060372 | -0.005568 | 0.059114 | -0.22823 | -0.0035378 | -0.0036707 | 0.060638 | 0.020081 | 0.059481 | -120.786 | -27.6259 | -121.0948 | 0.001765 | -0.04543 | -0.032021 | -121.432 | -121.0555 | -14.8713 | -121.177 | 0.020409 | 0.004549 | 0.067272 | -121.6585 | 0.012671 | -0.11725 | 0.65872 | 0.34993 | 0.33726 | -0.16445 | -0.15104 | -0.21378 | -0.09861 | 0.38924 | 0.26774 | 0.48152 | -0.11447 | -0.051747 | 121.4465 | 121.3993 | 121.4127 | 93.8188 | -121.551 | 121.4651 | 121.4493 | 121.512 | 106.5734 | -121.7775
814.5156 | 121.7789 | -121.4218 | 0.091553 | 1.4211e-13 | -0.018335 | 0.00062391 | 0.060799 | -0.0057818 | 0.059541 | -0.22823 | -0.0037514 | -0.0036707 | 0.060424 | 0.020936 | 0.059481 | -120.7768 | -27.6213 | -121.0994 | 0.001765 | -0.059167 | -0.022864 | -121.432 | -121.06 | -14.8988 | -121.1815 | 0.020409 | 0.013707 | 0.067272 | -121.6585 | -0.010217 | -0.089788 | 0.64499 | 0.32246 | 0.33268 | -0.15072 | -0.11442 | -0.23667 | -0.071144 | 0.36177 | 0.24027 | 0.47694 | -0.077846 | -0.024281 | 121.4236 | 121.3626 | 121.3989 | 93.8005 | -121.5236 | 121.4422 | 121.4355 | 121.4891 | 106.5231 | -121.75
816.25 | 121.6553 | -121.4996 | 0.09613 | 1.4211e-13 | -0.018549 | 0.00019651 | 0.060586 | -0.0053544 | 0.059328 | -0.22823 | -0.0035378 | -0.0034569 | 0.060851 | 0.020722 | 0.059481 | -120.7906 | -27.6488 | -121.1039 | 0.006344 | -0.04543 | -0.032021 | -121.4458 | -121.06 | -14.94 | -121.1815 | 0.015831 | -2.9e-05 | 0.067272 | -121.6585 | 0.053866 | -0.089786 | 0.70907 | 0.3957 | 0.34184 | -0.14156 | -0.12815 | -0.15885 | -0.080299 | 0.43959 | 0.31809 | 0.47694 | -0.096159 | -0.028858 | 121.506 | 121.4542 | 121.4676 | 93.8509 | -121.5419 | 121.5155 | 121.4996 | 121.5669 | 106.5597 | -121.7546
817.9844 | 121.7239 | -121.4447 | 0.086975 | 1.4211e-13 | -0.018763 | -1.7092e-05 | 0.060799 | -0.0053544 | 0.059541 | -0.2206 | -0.0031106 | -0.0030297 | 0.060638 | 0.020081 | 0.059267 | -120.7951 | -27.6534 | -121.1085 | 0.015501 | -0.050009 | -0.032021 | -121.4412 | -121.0646 | -14.9354 | -121.1861 | 0.015831 | 0.009128 | 0.067272 | -121.6722 | 0.003513 | -0.071474 | 0.64956 | 0.33619 | 0.33268 | -0.13698 | -0.119 | -0.22752 | -0.071144 | 0.38008 | 0.25858 | 0.4861 | -0.077847 | -0.019703 | 121.4602 | 121.3947 | 121.4127 | 93.7913 | -121.5282 | 121.4605 | 121.4538 | 121.512 | 106.5093 | -121.7592
819.7188 | 121.756 | -121.4447 | 0.07782 | 1.4211e-13 | -0.018335 | 0.00019651 | 0.060586 | -0.005568 | 0.059755 | -0.22823 | -0.0033242 | -0.0032433 | 0.060851 | 0.020508 | 0.059054 | -120.7906 | -27.6625 | -121.1085 | 0.010922 | -0.04543 | -0.027442 | -121.4458 | -121.0646 | -14.9583 | -121.1861 | 0.015831 | 0.009128 | 0.058115 | -121.6631 | -0.001066 | -0.066898 | 0.65414 | 0.33619 | 0.33726 | -0.12325 | -0.10526 | -0.21836 | -0.061989 | 0.38008 | 0.25858 | 0.47694 | -0.068692 | -0.019705 | 121.4556 | 121.3993 | 121.4173 | 93.7822 | -121.5236 | 121.4605 | 121.4538 | 121.5028 | 106.4864 | -121.7409
821.3906 | 121.7743 | -121.4539 | 0.09613 | 1.4211e-13 | -0.018549 | -1.7092e-05 | 0.060372 | -0.0057818 | 0.059541 | -0.2206 | -0.0035378 | -0.0034569 | 0.060638 | 0.020508 | 0.059481 | -120.7997 | -27.6762 | -121.1085 | 0.015501 | -0.054588 | -0.032021 | -121.4503 | -121.0646 | -14.972 | -121.1953 | 0.011252 | 0.009128 | 0.058115 | -121.6631 | 0.00351 | -0.080629 | 0.65414 | 0.34535 | 0.34184 | -0.15072 | -0.12815 | -0.20921 | -0.084878 | 0.38924 | 0.25858 | 0.46778 | -0.087002 | -0.038015 | 121.4694 | 121.3993 | 121.4218 | 93.7776 | -121.5465 | 121.4651 | 121.463 | 121.512 | 106.4818 | -121.7592
823.125 | 121.788 | -121.4493 | 0.10986 | 1.4211e-13 | -0.018763 | 0.00019651 | 0.060586 | -0.0057818 | 0.059328 | -0.23586 | -0.0033242 | -0.0036707 | 0.060424 | 0.020722 | 0.059054 | -120.8043 | -27.7129 | -121.1177 | 0.010922 | -0.054588 | -0.032021 | -121.4503 | -121.0738 | -14.9674 | -121.1999 | 0.011252 | 0.009128 | 0.058115 | -121.6814 | -0.001067 | -0.098941 | 0.64499 | 0.33162 | 0.33268 | -0.16445 | -0.14188 | -0.2321 | -0.098611 | 0.3755 | 0.24942 | 0.48152 | -0.10074 | -0.051748 | 121.4602 | 121.3947 | 121.4173 | 93.7364 | -121.5602 | 121.4605 | 121.4584 | 121.5074 | 106.4818 | -121.7912
824.7969 | 121.7377 | -121.4722 | 0.091553 | 1.4211e-13 | -0.018549 | -1.7092e-05 | 0.060586 | -0.0057818 | 0.059328 | -0.22823 | -0.0033242 | -0.0036707 | 0.06021 | 0.020508 | 0.059054 | -120.7997 | -27.7129 | -121.1131 | 0.010922 | -0.054588 | -0.022864 | -121.4458 | -121.0784 | -14.9995 | -121.1953 | 0.015831 | 0.004549 | 0.058115 | -121.6905 | 0.0264 | -0.080631 | 0.67245 | 0.35908 | 0.33268 | -0.14614 | -0.11442 | -0.21837 | -0.075722 | 0.39381 | 0.27689 | 0.49526 | -0.087004 | -0.033438 | 121.4831 | 121.4176 | 121.4493 | 93.7593 | -121.5373 | 121.488 | 121.4767 | 121.5303 | 106.4727 | -121.7821
826.5469 | 121.7789 | -121.4401 | 0.082397 | 1.4211e-13 | -0.018763 | 0.00041031 | 0.060799 | -0.005568 | 0.059328 | -0.21297 | -0.0035378 | -0.0034569 | 0.060638 | 0.020936 | 0.05884 | -120.7951 | -27.7632 | -121.1085 | 0.006344 | -0.04543 | -0.027442 | -121.4595 | -121.0829 | -15.0087 | -121.1999 | 0.011252 | 0.009128 | 0.071851 | -121.6768 | -0.01938 | -0.076053 | 0.64499 | 0.33162 | 0.351 | -0.12783 | -0.10984 | -0.23667 | -0.071145 | 0.35719 | 0.24027 | 0.47694 | -0.073269 | -0.010546 | 121.4465 | 121.3947 | 121.4127 | 93.6769 | -121.5419 | 121.4514 | 121.4493 | 121.512 | 106.4315 | -121.7592
828.2969 | 121.7422 | -121.431 | 0.086975 | 1.4211e-13 | -0.018763 | 0.00019651 | 0.060372 | -0.005568 | 0.059541 | -0.21297 | -0.0035378 | -0.0038843 | 0.060638 | 0.020508 | 0.059054 | -120.7997 | -27.7358 | -121.1177 | 0.020079 | -0.050009 | -0.0366 | -121.4503 | -121.0784 | -15.0087 | -121.1999 | 0.006674 | 0.009128 | 0.067272 | -121.686 | -0.019378 | -0.066896 | 0.63125 | 0.3133 | 0.33268 | -0.13698 | -0.12357 | -0.25499 | -0.080301 | 0.35261 | 0.23111 | 0.4861 | -0.077847 | -0.019703 | 121.451 | 121.381 | 121.3944 | 93.6952 | -121.5373 | 121.4376 | 121.4401 | 121.4982 | 106.4223 | -121.7729
830.0312 | 121.6507 | -121.4813 | 0.13275 | 1.4211e-13 | -0.018549 | -1.7092e-05 | 0.060372 | -0.0053544 | 0.059328 | -0.22823 | -0.0033242 | -0.0034569 | 0.060424 | 0.020508 | 0.059267 | -120.8043 | -27.7449 | -121.1222 | 0.015501 | -0.050009 | -0.032021 | -121.4641 | -121.0875 | -15.0132 | -121.2044 | 0.015831 | 0.009128 | 0.062694 | -121.686 | 0.017239 | -0.11725 | 0.67703 | 0.35908 | 0.34184 | -0.18276 | -0.16477 | -0.20463 | -0.11692 | 0.39381 | 0.27689 | 0.48152 | -0.12362 | -0.070057 | 121.4968 | 121.4313 | 121.4493 | 93.7364 | -121.5968 | 121.4972 | 121.4905 | 121.544 | 106.4681 | -121.8187
831.7656 | 121.6599 | -121.4859 | 0.13733 | 1.4211e-13 | -0.018763 | -1.7092e-05 | 0.060799 | -0.0057818 | 0.059755 | -0.2206 | -0.0035378 | -0.0034569 | 0.060638 | 0.020936 | 0.059481 | -120.8043 | -27.7129 | -121.1222 | 0.006344 | -0.054588 | -0.032021 | -121.4687 | -121.0921 | -15.0315 | -121.1999 | 0.011252 | 0.009128 | 0.071851 | -121.6814 | 0.017238 | -0.13099 | 0.68161 | 0.36366 | 0.34642 | -0.19192 | -0.16935 | -0.19548 | -0.12608 | 0.39381 | 0.28605 | 0.48152 | -0.1282 | -0.065478 | 121.4922 | 121.4313 | 121.4539 | 93.773 | -121.606 | 121.4972 | 121.495 | 121.5578 | 106.4544 | -121.8187
833.5 | 121.669 | -121.4722 | 0.11444 | 1.4211e-13 | -0.018335 | -0.00023069 | 0.060372 | -0.005568 | 0.059755 | -0.23586 | -0.0037514 | -0.0034569 | 0.060638 | 0.020722 | 0.059267 | -120.8089 | -27.7129 | -121.1268 | 0.010922 | -0.04543 | -0.032021 | -121.4687 | -121.0875 | -15.0407 | -121.1999 | 0.011252 | 0.009128 | 0.058115 | -121.6905 | 0.003505 | -0.10352 | 0.66329 | 0.34535 | 0.34184 | -0.15987 | -0.14646 | -0.21837 | -0.10319 | 0.38465 | 0.27231 | 0.49068 | -0.10531 | -0.056326 | 121.4831 | 121.4267 | 121.4401 | 93.7593 | -121.5831 | 121.4834 | 121.4813 | 121.5303 | 106.4315 | -121.805
835.2344 | 121.7056 | -121.4859 | 0.10986 | 1.4211e-13 | -0.018549 | 0.00019651 | 0.060158 | -0.0057818 | 0.059541 | -0.24349 | -0.0033242 | -0.0034569 | 0.060638 | 0.020722 | 0.059267 | -120.8043 | -27.7312 | -121.1314 | 0.015501 | -0.04543 | -0.032021 | -121.4641 | -121.0875 | -15.027 | -121.2044 | 0.011252 | -2.9e-05 | 0.062694 | -121.6905 | 0.021817 | -0.094362 | 0.68161 | 0.3545 | 0.33268 | -0.15529 | -0.14188 | -0.20463 | -0.098611 | 0.39839 | 0.28147 | 0.4861 | -0.10989 | -0.047169 | 121.5014 | 121.4405 | 121.4539 | 93.7547 | -121.5739 | 121.4972 | 121.4859 | 121.5486 | 106.4589 | -121.8004
836.9062 | 121.7834 | -121.4584 | 0.10529 | 1.4211e-13 | -0.018976 | -0.00023069 | 0.060586 | -0.0057818 | 0.059328 | -0.22823 | -0.0033242 | -0.0034569 | 0.060424 | 0.020722 | 0.059054 | -120.8135 | -27.722 | -121.1268 | 0.006344 | -0.050009 | -0.027442 | -121.4641 | -121.0967 | -15.0453 | -121.209 | 0.020409 | 0.004549 | 0.062694 | -121.7043 | -0.005649 | -0.098942 | 0.64498 | 0.33161 | 0.33726 | -0.1553 | -0.13273 | -0.24584 | -0.084877 | 0.36176 | 0.24942 | 0.49526 | -0.10074 | -0.042592 | 121.4648 | 121.4084 | 121.431 | 93.7364 | -121.5694 | 121.4788 | 121.463 | 121.5211 | 106.4132 | -121.8096
838.6562 | 121.7972 | -121.4493 | 0.082397 | 1.4211e-13 | -0.018763 | -0.00023069 | 0.060586 | -0.005568 | 0.059541 | -0.22823 | -0.0037514 | -0.0034569 | 0.060424 | 0.020936 | 0.059267 | -120.8089 | -27.722 | -121.1314 | 0.006344 | -0.050009 | -0.032021 | -121.4732 | -121.0921 | -15.0453 | -121.2136 | 0.011252 | -2.9e-05 | 0.053537 | -121.7043 | -0.023961 | -0.076053 | 0.64041 | 0.31788 | 0.34184 | -0.13241 | -0.11442 | -0.25499 | -0.071145 | 0.35719 | 0.23569 | 0.49068 | -0.082426 | -0.02886 | 121.4556 | 121.3993 | 121.4173 | 93.7272 | -121.5556 | 121.4605 | 121.4493 | 121.5028 | 106.404 | -121.7867
840.3906 | 121.6599 | -121.4996 | 0.1236 | 1.4211e-13 | -0.018976 | -1.7092e-05 | 0.060372 | -0.0057818 | 0.059969 | -0.22823 | -0.0037514 | -0.0034569 | 0.060424 | 0.020936 | 0.059267 | -120.8135 | -27.7358 | -121.136 | 0.010922 | -0.04543 | -0.032021 | -121.4732 | -121.0921 | -15.059 | -121.2136 | 0.006674 | 0.009128 | 0.058115 | -121.6951 | 0.026393 | -0.11267 | 0.68618 | 0.36366 | 0.33726 | -0.16903 | -0.15562 | -0.19548 | -0.11692 | 0.40754 | 0.28604 | 0.48152 | -0.11447 | -0.065481 | 121.5106 | 121.4542 | 121.4676 | 93.7639 | -121.5968 | 121.5063 | 121.5088 | 121.5577 | 106.4406 | -121.8187
842.125 | 121.6873 | -121.5042 | 0.13275 | 1.4211e-13 | -0.018763 | 0.00019651 | 0.060372 | -0.005568 | 0.059755 | -0.22823 | -0.0033242 | -0.0032433 | 0.060638 | 0.020722 | 0.059481 | -120.818 | -27.7083 | -121.1406 | 0.006344 | -0.054588 | -0.0366 | -121.4732 | -121.0967 | -15.0636 | -121.2136 | 0.015831 | 0.013707 | 0.067272 | -121.6951 | 0.03097 | -0.12641 | 0.68618 | 0.36365 | 0.33268 | -0.18734 | -0.16935 | -0.1909 | -0.11692 | 0.40754 | 0.29062 | 0.48152 | -0.11904 | -0.065479 | 121.5106 | 121.4496 | 121.4676 | 93.7959 | -121.606 | 121.52 | 121.5179 | 121.5715 | 106.4406 | -121.8279
843.8594 | 121.8018 | -121.4676 | 0.082397 | 1.4211e-13 | -0.018549 | -1.7092e-05 | 0.060586 | -0.0053544 | 0.059541 | -0.22823 | -0.0033242 | -0.0032433 | 0.060424 | 0.020936 | 0.059267 | -120.8135 | -27.7403 | -121.1406 | 0.001765 | -0.054588 | -0.032021 | -121.4824 | -121.0967 | -15.0499 | -121.2182 | 0.011252 | 0.009128 | 0.071851 | -121.7043 | -0.014809 | -0.080632 | 0.65414 | 0.32703 | 0.34184 | -0.13698 | -0.11442 | -0.23668 | -0.071145 | 0.37092 | 0.24942 | 0.4861 | -0.073269 | -0.010546 | 121.4694 | 121.413 | 121.4356 | 93.7272 | -121.5648 | 121.4788 | 121.4767 | 121.5394 | 106.4177 | -121.7867
845.6094 | 121.7239 | -121.4813 | 0.11444 | 1.4211e-13 | -0.01919 | -0.00023069 | 0.060372 | -0.0053544 | 0.059541 | -0.2206 | -0.0035378 | -0.0034569 | 0.060638 | 0.020936 | 0.059481 | -120.8318 | -27.7312 | -121.1406 | 0.015501 | -0.050009 | -0.0366 | -121.4778 | -121.0967 | -15.0544 | -121.2182 | 0.020409 | 0.009128 | 0.067272 | -121.7043 | 0.003503 | -0.09894 | 0.64956 | 0.34077 | 0.33726 | -0.16445 | -0.15104 | -0.22295 | -0.094032 | 0.38465 | 0.26315 | 0.4861 | -0.10531 | -0.047169 | 121.4968 | 121.4313 | 121.4447 | 93.7501 | -121.5923 | 121.5017 | 121.4905 | 121.5486 | 106.4269 | -121.8187
847.2812 | 121.7926 | -121.4539 | 0.068665 | 1.4211e-13 | -0.018976 | 0.00019651 | 0.060158 | -0.0057818 | 0.059755 | -0.22823 | -0.0035378 | -0.0036707 | 0.060851 | 0.020936 | 0.059267 | -120.8135 | -27.7175 | -121.1406 | 0.010922 | -0.040851 | -0.027442 | -121.4824 | -121.0967 | -15.0636 | -121.2136 | 0.006674 | 0.004549 | 0.067272 | -121.7089 | -0.028542 | -0.057743 | 0.64041 | 0.3133 | 0.34184 | -0.10952 | -0.096107 | -0.25499 | -0.061991 | 0.35719 | 0.24026 | 0.49526 | -0.064116 | -0.001393 | 121.4648 | 121.413 | 121.4264 | 93.7364 | -121.5511 | 121.4605 | 121.4584 | 121.5211 | 106.3903 | -121.7775
849.0156 | 121.7194 | -121.4905 | 0.10529 | 1.4211e-13 | -0.019404 | -1.7092e-05 | 0.060586 | -0.005568 | 0.060182 | -0.22823 | -0.0033242 | -0.0036707 | 0.060638 | 0.020936 | 0.058627 | -120.8226 | -27.7449 | -121.136 | 0.015501 | -0.050009 | -0.022864 | -121.4778 | -121.1058 | -15.0499 | -121.2228 | 0.020409 | 0.004549 | 0.067272 | -121.7134 | 0.012659 | -0.089785 | 0.66787 | 0.3545 | 0.34184 | -0.1553 | -0.12815 | -0.22295 | -0.084877 | 0.38465 | 0.26773 | 0.49068 | -0.10074 | -0.038014 | 121.506 | 121.4405 | 121.4676 | 93.7456 | -121.5831 | 121.5109 | 121.495 | 121.5578 | 106.4406 | -121.8187
850.7656 | 121.788 | -121.463 | 0.091553 | 1.4211e-13 | -0.01919 | -0.00023069 | 0.060586 | -0.0059954 | 0.059541 | -0.22823 | -0.0035378 | -0.0036707 | 0.060638 | 0.020936 | 0.059267 | -120.818 | -27.7403 | -121.136 | 0.006344 | -0.04543 | -0.027442 | -121.4824 | -121.1012 | -15.0636 | -121.2228 | 0.015831 | 0.009128 | 0.067272 | -121.7089 | -0.019386 | -0.085209 | 0.64498 | 0.32704 | 0.34642 | -0.13698 | -0.11899 | -0.24584 | -0.075722 | 0.36176 | 0.24026 | 0.4861 | -0.082425 | -0.024281 | 121.4694 | 121.4176 | 121.4356 | 93.7227 | -121.574 | 121.4788 | 121.4721 | 121.5303 | 106.3994 | -121.8004
852.5 | 121.6644 | -121.5042 | 0.10986 | 1.4211e-13 | -0.018976 | -1.7092e-05 | 0.060372 | -0.005568 | 0.059969 | -0.22823 | -0.0035378 | -0.0034569 | 0.060851 | 0.020722 | 0.059481 | -120.818 | -27.7403 | -121.136 | 0.010922 | -0.050009 | -0.027442 | -121.4824 | -121.1104 | -15.0544 | -121.2182 | 0.011252 | 0.004549 | 0.067272 | -121.7134 | 0.021812 | -0.098941 | 0.68618 | 0.36823 | 0.34642 | -0.15987 | -0.13731 | -0.20922 | -0.098611 | 0.3938 | 0.28604 | 0.49526 | -0.10531 | -0.042591 | 121.5151 | 121.4542 | 121.4768 | 93.7639 | -121.5923 | 121.5155 | 121.5088 | 121.5715 | 106.4498 | -121.8233
854.1719 | 121.7148 | -121.5363 | 0.10986 | 1.4211e-13 | -0.01919 | -1.7092e-05 | 0.060586 | -0.0059954 | 0.059541 | -0.2206 | -0.0033242 | -0.0036707 | 0.060638 | 0.020722 | 0.059054 | -120.8272 | -27.7358 | -121.1314 | 0.015501 | -0.050009 | -0.0366 | -121.487 | -121.1058 | -15.0682 | -121.2273 | 0.006674 | 0.004549 | 0.067272 | -121.7134 | 0.049277 | -0.094362 | 0.70907 | 0.40486 | 0.35558 | -0.15987 | -0.14646 | -0.17718 | -0.10319 | 0.43043 | 0.30893 | 0.4861 | -0.10531 | -0.042591 | 121.5518 | 121.4862 | 121.4997 | 93.8005 | -121.5968 | 121.5429 | 121.5408 | 121.6035 | 106.4681 | -121.8233
855.9062 | 121.6827 | -121.5271 | 0.10986 | 1.4211e-13 | -0.01919 | 0.00019651 | 0.060799 | -0.005568 | 0.059755 | -0.23586 | -0.0037514 | -0.0036707 | 0.060851 | 0.021577 | 0.059054 | -120.8226 | -27.7129 | -121.1406 | 0.006344 | -0.054588 | -0.0366 | -121.4824 | -121.1058 | -15.0407 | -121.2273 | 0.015831 | 0.013707 | 0.062694 | -121.7043 | 0.044701 | -0.10352 | 0.70449 | 0.38654 | 0.34184 | -0.16445 | -0.14646 | -0.17717 | -0.094032 | 0.42127 | 0.29977 | 0.47694 | -0.096156 | -0.047169 | 121.5334 | 121.4725 | 121.4905 | 93.8142 | -121.5923 | 121.5429 | 121.5408 | 121.5898 | 106.4864 | -121.8141
857.5781 | 121.8063 | -121.4859 | 0.09613 | 1.4211e-13 | -0.01919 | 0.00019651 | 0.060799 | -0.0057818 | 0.059969 | -0.22823 | -0.0033242 | -0.0034569 | 0.060424 | 0.021149 | 0.059267 | -120.8318 | -27.6991 | -121.136 | 0.006344 | -0.04543 | -0.027442 | -121.487 | -121.1058 | -15.0453 | -121.2365 | 0.011252 | 0.004549 | 0.062694 | -121.7226 | -0.001077 | -0.089786 | 0.65414 | 0.34992 | 0.351 | -0.14156 | -0.12357 | -0.23669 | -0.084878 | 0.38007 | 0.24941 | 0.4861 | -0.091581 | -0.033436 | 121.4922 | 121.4405 | 121.4585 | 93.7868 | -121.5831 | 121.4972 | 121.4904 | 121.5486 | 106.4406 | -121.8187
859.3125 | 121.7422 | -121.5134 | 0.09613 | 1.4211e-13 | -0.018976 | -1.7092e-05 | 0.060586 | -0.0057818 | 0.059755 | -0.2206 | -0.0035378 | -0.0034569 | 0.060638 | 0.021363 | 0.059267 | -120.8318 | -27.722 | -121.136 | 0.010922 | -0.054588 | -0.022864 | -121.4824 | -121.1104 | -15.0407 | -121.2228 | 0.011252 | 0.009128 | 0.053537 | -121.7226 | 0.030968 | -0.085208 | 0.6816 | 0.37739 | 0.34642 | -0.15072 | -0.11899 | -0.20922 | -0.084878 | 0.40296 | 0.29062 | 0.49984 | -0.087002 | -0.042593 | 121.5243 | 121.4588 | 121.4905 | 93.7913 | -121.5785 | 121.5246 | 121.5225 | 121.5669 | 106.4727 | -121.8187
861 | 121.7606 | -121.4996 | 0.10529 | 1.4211e-13 | -0.019404 | -1.7092e-05 | 0.060586 | -0.0051408 | 0.059969 | -0.2206 | -0.003965 | -0.0034569 | 0.060638 | 0.020936 | 0.059054 | -120.8318 | -27.7403 | -121.1406 | 0.006344 | -0.050009 | -0.022864 | -121.487 | -121.1196 | -15.0361 | -121.2365 | 0.020409 | 0.004549 | 0.062694 | -121.7226 | 0.012656 | -0.098942 | 0.66787 | 0.35908 | 0.34642 | -0.1553 | -0.12815 | -0.22295 | -0.084877 | 0.38007 | 0.26315 | 0.4861 | -0.10074 | -0.042592 | 121.506 | 121.4496 | 121.4768 | 93.7593 | -121.5923 | 121.52 | 121.5042 | 121.5623 | 106.4635 | -121.8279
862.7344 | 121.8109 | -121.4813 | 0.082397 | 1.4211e-13 | -0.01919 | 0.00019651 | 0.060586 | -0.005568 | 0.059755 | -0.22823 | -0.0035378 | -0.0034569 | 0.060638 | 0.021149 | 0.05884 | -120.8318 | -27.7312 | -121.136 | 0.020079 | -0.040851 | -0.032021 | -121.4961 | -121.1012 | -15.0315 | -121.2273 | 0.006674 | 0.009128 | 0.062694 | -121.7226 | -0.014813 | -0.062318 | 0.64956 | 0.34535 | 0.36016 | -0.12325 | -0.11442 | -0.24126 | -0.075723 | 0.38007 | 0.25399 | 0.49526 | -0.073269 | -0.019703 | 121.5014 | 121.4405 | 121.4493 | 93.7501 | -121.5785 | 121.488 | 121.4905 | 121.544 | 106.4498 | -121.805
864.4062 | 121.6644 | -121.5363 | 0.12817 | 1.4211e-13 | -0.019617 | 0.00019651 | 0.060372 | -0.0057818 | 0.060182 | -0.22823 | -0.0033242 | -0.0032433 | 0.06021 | 0.021149 | 0.059054 | -120.8363 | -27.7861 | -121.1451 | 0.015501 | -0.050009 | -0.022864 | -121.5007 | -121.1196 | -15.0453 | -121.2319 | 0.015831 | 0.004549 | 0.067272 | -121.7272 | 0.03554 | -0.11267 | 0.69991 | 0.39112 | 0.35558 | -0.17818 | -0.15104 | -0.19091 | -0.11234 | 0.41669 | 0.30435 | 0.49526 | -0.12363 | -0.060902 | 121.5518 | 121.4862 | 121.5134 | 93.7501 | -121.6289 | 121.5521 | 121.5408 | 121.6035 | 106.491 | -121.8553
866.1562 | 121.6919 | -121.5363 | 0.10529 | 1.4211e-13 | -0.019617 | 0.00041031 | 0.060586 | -0.0057818 | 0.059541 | -0.22823 | -0.0033242 | -0.0036707 | 0.060638 | 0.021363 | 0.05884 | -120.8272 | -27.7678 | -121.1543 | 0.010922 | -0.054588 | -0.0366 | -121.5007 | -121.115 | -15.027 | -121.2319 | 0.020409 | 0.004549 | 0.062694 | -121.7317 | 0.03554 | -0.094364 | 0.70907 | 0.38196 | 0.34642 | -0.15987 | -0.14189 | -0.19549 | -0.084877 | 0.42127 | 0.30435 | 0.49984 | -0.10074 | -0.042592 | 121.5472 | 121.4817 | 121.4997 | 93.7684 | -121.606 | 121.5567 | 121.5408 | 121.5989 | 106.5093 | -121.837
867.8906 | 121.8246 | -121.463 | 0.086975 | 1.4211e-13 | -0.019617 | 0.00041031 | 0.060158 | -0.0057818 | 0.059541 | -0.23586 | -0.0037514 | -0.0036707 | 0.060638 | 0.021363 | 0.059481 | -120.8363 | -27.7678 | -121.1543 | 0.001765 | -0.054588 | -0.027442 | -121.4961 | -121.1241 | -15.0636 | -121.2411 | 0.006674 | 0.004549 | 0.062694 | -121.7317 | -0.033123 | -0.08521 | 0.62667 | 0.30872 | 0.34185 | -0.14156 | -0.11442 | -0.26873 | -0.080301 | 0.33887 | 0.22195 | 0.49068 | -0.082426 | -0.024281 | 121.4648 | 121.4084 | 121.4356 | 93.6952 | -121.5831 | 121.4697 | 121.4676 | 121.5257 | 106.3994 | -121.8187
869.5625 | 121.7789 | -121.5088 | 0.086975 | 1.4211e-13 | -0.019404 | -1.7092e-05 | 0.060372 | -0.0057818 | 0.059541 | -0.22823 | -0.0033242 | -0.0036707 | 0.060424 | 0.021363 | 0.05884 | -120.8318 | -27.777 | -121.1543 | 0.001765 | -0.050009 | -0.0366 | -121.4916 | -121.1196 | -15.0361 | -121.2319 | 0.015831 | -2.9e-05 | 0.062694 | -121.7409 | 0.017232 | -0.08521 | 0.67702 | 0.3545 | 0.33727 | -0.13698 | -0.12357 | -0.23211 | -0.071144 | 0.38922 | 0.27688 | 0.509 | -0.087004 | -0.024281 | 121.5106 | 121.4588 | 121.4722 | 93.7318 | -121.5785 | 121.5246 | 121.5088 | 121.5715 | 106.4727 | -121.8279
871.3125 | 121.8201 | -121.4859 | 0.073242 | 1.4211e-13 | -0.019617 | 0.00019651 | 0.060372 | -0.005568 | 0.059541 | -0.23586 | -0.0031106 | -0.0032433 | 0.060424 | 0.021577 | 0.059481 | -120.8409 | -27.7816 | -121.1451 | 0.001765 | -0.054588 | -0.022864 | -121.5007 | -121.1241 | -15.0544 | -121.2319 | 0.011252 | 0.004549 | 0.058115 | -121.7272 | -0.014814 | -0.071477 | 0.64498 | 0.34077 | 0.35558 | -0.12783 | -0.096106 | -0.24126 | -0.06199 | 0.36176 | 0.25399 | 0.49526 | -0.068693 | -0.015127 | 121.4877 | 121.4313 | 121.463 | 93.7043 | -121.574 | 121.4972 | 121.4904 | 121.544 | 106.4315 | -121.8004
873.0469 | 121.7422 | -121.5271 | 0.11444 | 1.4211e-13 | -0.019404 | -1.7092e-05 | 0.060372 | -0.005568 | 0.059755 | -0.2206 | -0.0035378 | -0.0032433 | 0.060424 | 0.021577 | 0.058627 | -120.8363 | -27.7632 | -121.1543 | 0.006344 | -0.050009 | -0.032021 | -121.5007 | -121.1196 | -15.0544 | -121.2411 | 0.015831 | 0.009128 | 0.058115 | -121.7272 | 0.026385 | -0.1081 | 0.69076 | 0.37281 | 0.34642 | -0.16445 | -0.14646 | -0.20007 | -0.09861 | 0.40754 | 0.28603 | 0.4861 | -0.10531 | -0.056326 | 121.5334 | 121.4771 | 121.4951 | 93.7639 | -121.6152 | 121.5429 | 121.5362 | 121.5852 | 106.4727 | -121.8416
874.7812 | 121.701 | -121.5408 | 0.10529 | 1.4211e-13 | -0.019404 | -0.00023069 | 0.060158 | -0.0057818 | 0.059541 | -0.23586 | -0.0035378 | -0.0032433 | 0.060424 | 0.021363 | 0.059267 | -120.8409 | -27.7632 | -121.1543 | 0.001765 | -0.050009 | -0.032021 | -121.5007 | -121.1241 | -15.0315 | -121.2411 | 0.015831 | 0.018285 | 0.067272 | -121.7317 | 0.040118 | -0.10352 | 0.69991 | 0.38654 | 0.34642 | -0.1553 | -0.13731 | -0.19091 | -0.089455 | 0.41669 | 0.29977 | 0.49068 | -0.087001 | -0.038014 | 121.5426 | 121.4908 | 121.5088 | 93.7776 | -121.606 | 121.5567 | 121.5591 | 121.6081 | 106.5093 | -121.837
876.4688 | 121.8475 | -121.5088 | 0.064087 | 1.4211e-13 | -0.019404 | -1.7092e-05 | 0.060372 | -0.005568 | 0.059755 | -0.22823 | -0.0035378 | -0.0036707 | 0.060424 | 0.021577 | 0.059054 | -120.8409 | -27.7678 | -121.1589 | 0.015501 | -0.050009 | -0.027442 | -121.5007 | -121.1333 | -15.059 | -121.2502 | 0.015831 | 0.004549 | 0.062694 | -121.7409 | 0.008074 | -0.048586 | 0.66787 | 0.34992 | 0.34185 | -0.1141 | -0.091529 | -0.23211 | -0.048256 | 0.37549 | 0.25857 | 0.49068 | -0.059538 | -0.001393 | 121.5243 | 121.4588 | 121.4813 | 93.741 | -121.5648 | 121.5246 | 121.5133 | 121.5715 | 106.4498 | -121.805
878.1406 | 121.6965 | -121.5546 | 0.11444 | 1.4211e-13 | -0.019617 | 0.00019651 | 0.060586 | -0.005568 | 0.059755 | -0.22823 | -0.0035378 | -0.0034569 | 0.060424 | 0.021577 | 0.059267 | -120.8363 | -27.7449 | -121.1634 | 0.010922 | -0.04543 | -0.027442 | -121.5053 | -121.1241 | -15.0544 | -121.2411 | 0.015831 | 0.004549 | 0.062694 | -121.7363 | 0.049271 | -0.10352 | 0.71822 | 0.39112 | 0.34185 | -0.15987 | -0.14188 | -0.18176 | -0.09861 | 0.43042 | 0.3135 | 0.49526 | -0.10989 | -0.051747 | 121.5655 | 121.5091 | 121.5271 | 93.8096 | -121.6197 | 121.5704 | 121.5591 | 121.6173 | 106.5001 | -121.8508
879.875 | 121.7422 | -121.5317 | 0.13275 | 1.4211e-13 | -0.01919 | -0.00023069 | 0.060372 | -0.005568 | 0.060182 | -0.23586 | -0.0037514 | -0.0034569 | 0.060424 | 0.021577 | 0.059267 | -120.8363 | -27.7541 | -121.1634 | 0.006344 | -0.04543 | -0.032021 | -121.5007 | -121.1196 | -15.0819 | -121.2502 | 0.011252 | -2.9e-05 | 0.058115 | -121.7409 | 0.030962 | -0.12641 | 0.69533 | 0.36823 | 0.33727 | -0.17818 | -0.16477 | -0.20923 | -0.1215 | 0.41211 | 0.28146 | 0.49068 | -0.13278 | -0.074636 | 121.538 | 121.4862 | 121.4997 | 93.7776 | -121.6335 | 121.5429 | 121.5316 | 121.5898 | 106.4498 | -121.8737
881.5469 | 121.6782 | -121.5454 | 0.1236 | 1.4211e-13 | -0.019617 | 0.00019651 | 0.059945 | -0.0057818 | 0.060182 | -0.22823 | -0.0033242 | -0.0036707 | 0.060638 | 0.021149 | 0.059267 | -120.8409 | -27.7816 | -121.1589 | 0.006344 | -0.04543 | -0.022864 | -121.5099 | -121.1333 | -15.0636 | -121.2456 | 0.011252 | -2.9e-05 | 0.067272 | -121.7455 | 0.035537 | -0.11725 | 0.70449 | 0.38654 | 0.351 | -0.16903 | -0.14646 | -0.20007 | -0.11234 | 0.41211 | 0.29977 | 0.49984 | -0.12362 | -0.056324 | 121.5518 | 121.5 | 121.5225 | 93.7639 | -121.6335 | 121.5567 | 121.5454 | 121.6127 | 106.4818 | -121.8691
883.2812 | 121.7331 | -121.5271 | 0.11902 | 1.4211e-13 | -0.020045 | -0.00023069 | 0.060372 | -0.0057818 | 0.059541 | -0.2206 | -0.0033242 | -0.0034569 | 0.060851 | 0.021577 | 0.059054 | -120.8409 | -27.7449 | -121.1726 | 0.010922 | -0.050009 | -0.032021 | -121.5145 | -121.1241 | -15.0773 | -121.2411 | 0.011252 | 0.004549 | 0.062694 | -121.7363 | 0.012648 | -0.1081 | 0.68618 | 0.3545 | 0.34185 | -0.16903 | -0.15104 | -0.20922 | -0.10777 | 0.40296 | 0.28603 | 0.49526 | -0.11447 | -0.056325 | 121.538 | 121.4771 | 121.4951 | 93.7822 | -121.6335 | 121.5384 | 121.5316 | 121.5898 | 106.4498 | -121.8553
884.9531 | 121.701 | -121.5363 | 0.11444 | 1.4211e-13 | -0.019404 | -0.00023069 | 0.060372 | -0.0057818 | 0.059755 | -0.21297 | -0.0033242 | -0.0034569 | 0.060424 | 0.02179 | 0.059267 | -120.8501 | -27.7358 | -121.1726 | 0.010922 | -0.050009 | -0.032021 | -121.5053 | -121.1287 | -15.0636 | -121.2502 | 0.015831 | 0.004549 | 0.058115 | -121.7363 | 0.030961 | -0.10352 | 0.68618 | 0.36365 | 0.33269 | -0.16445 | -0.14646 | -0.20007 | -0.09861 | 0.40753 | 0.28603 | 0.4861 | -0.10989 | -0.056326 | 121.5472 | 121.4862 | 121.5042 | 93.8005 | -121.6197 | 121.5521 | 121.5408 | 121.5944 | 106.4727 | -121.8508
886.7031 | 121.8521 | -121.4859 | 0.068665 | 1.4211e-13 | -0.020045 | 0.00041031 | 0.060158 | -0.0057818 | 0.060182 | -0.23586 | -0.0031106 | -0.0034569 | 0.060424 | 0.021577 | 0.059267 | -120.8455 | -27.7587 | -121.168 | 0.010922 | -0.050009 | -0.027442 | -121.5053 | -121.1287 | -15.0499 | -121.2456 | 0.015831 | 0.009128 | 0.062694 | -121.7501 | -0.019393 | -0.057743 | 0.6404 | 0.31788 | 0.33727 | -0.11867 | -0.096107 | -0.26416 | -0.052834 | 0.35718 | 0.24026 | 0.50442 | -0.059537 | -0.005971 | 121.4968 | 121.4359 | 121.4585 | 93.7272 | -121.574 | 121.5017 | 121.495 | 121.5486 | 106.436 | -121.8187
888.375 | 121.7377 | -121.5317 | 0.11444 | 1.4211e-13 | -0.019617 | -1.7092e-05 | 0.060372 | -0.0057818 | 0.059755 | -0.2206 | -0.0033242 | -0.0036707 | 0.060638 | 0.021577 | 0.059054 | -120.8501 | -27.7495 | -121.168 | 0.010922 | -0.050009 | -0.027442 | -121.5099 | -121.1333 | -15.0499 | -121.2456 | 0.011252 | -2.9e-05 | 0.062694 | -121.7455 | 0.021804 | -0.10352 | 0.6816 | 0.36365 | 0.34185 | -0.16445 | -0.14188 | -0.2138 | -0.10319 | 0.39838 | 0.28603 | 0.49984 | -0.11447 | -0.051747 | 121.5426 | 121.4817 | 121.5042 | 93.7822 | -121.6243 | 121.5429 | 121.5316 | 121.5944 | 106.4818 | -121.8599
890.0469 | 121.7285 | -121.5363 | 0.11902 | 1.4211e-13 | -0.019617 | -1.7092e-05 | 0.060158 | -0.005568 | 0.059755 | -0.22823 | -0.0031106 | -0.0034569 | 0.060424 | 0.021577 | 0.059267 | -120.8455 | -27.7816 | -121.168 | 0.001765 | -0.050009 | -0.032021 | -121.5099 | -121.1333 | -15.059 | -121.2548 | 0.002095 | -2.9e-05 | 0.062694 | -121.7501 | 0.026382 | -0.11725 | 0.69075 | 0.36823 | 0.34185 | -0.16903 | -0.15104 | -0.21381 | -0.11692 | 0.40295 | 0.28145 | 0.49526 | -0.11905 | -0.056325 | 121.538 | 121.4862 | 121.5042 | 93.7547 | -121.6289 | 121.5383 | 121.5362 | 121.5989 | 106.4772 | -121.8691
891.7812 | 121.8338 | -121.4905 | 0.082397 | 1.4211e-13 | -0.019404 | -0.00023069 | 0.060372 | -0.0059954 | 0.059755 | -0.22823 | -0.0033242 | -0.0036707 | 0.060638 | 0.02179 | 0.059054 | -120.8501 | -27.7495 | -121.168 | 0.010922 | -0.054588 | -0.032021 | -121.5099 | -121.1379 | -15.0636 | -121.2502 | 0.015831 | 0.004549 | 0.062694 | -121.7455 | -0.019394 | -0.071475 | 0.6404 | 0.32245 | 0.34185 | -0.13698 | -0.11442 | -0.255 | -0.066566 | 0.3526 | 0.24026 | 0.49526 | -0.077848 | -0.019703 | 121.5014 | 121.4359 | 121.4585 | 93.741 | -121.5923 | 121.5063 | 121.495 | 121.5532 | 106.4269 | -121.8279
893.4688 | 121.7377 | -121.5179 | 0.11902 | 1.4211e-13 | -0.020258 | 0.00019651 | 0.060586 | -0.005568 | 0.059755 | -0.2206 | -0.0035378 | -0.0032433 | 0.060638 | 0.021577 | 0.059267 | -120.8501 | -27.722 | -121.168 | 0.010922 | -0.050009 | -0.022864 | -121.5099 | -121.1379 | -15.0773 | -121.2502 | 0.020409 | 0.004549 | 0.067272 | -121.7455 | 0.008071 | -0.1081 | 0.66787 | 0.34992 | 0.34185 | -0.16903 | -0.14188 | -0.22754 | -0.09861 | 0.38007 | 0.26772 | 0.49526 | -0.11447 | -0.051747 | 121.5289 | 121.4679 | 121.4951 | 93.7959 | -121.6289 | 121.5384 | 121.5225 | 121.5852 | 106.4406 | -121.8645
895.2188 | 121.6873 | -121.5363 | 0.10529 | 1.4211e-13 | -0.019617 | -0.00023069 | 0.060372 | -0.0057818 | 0.059541 | -0.2206 | -0.0037514 | -0.0034569 | 0.060638 | 0.021149 | 0.05884 | -120.8409 | -27.7083 | -121.1726 | 0.010922 | -0.050009 | -0.022864 | -121.5145 | -121.1379 | -15.0865 | -121.2411 | 0.015831 | -2.9e-05 | 0.062694 | -121.7501 | 0.021803 | -0.094364 | 0.69533 | 0.36365 | 0.34185 | -0.1553 | -0.12815 | -0.21381 | -0.089455 | 0.39838 | 0.29519 | 0.509 | -0.10532 | -0.042592 | 121.5472 | 121.4862 | 121.5134 | 93.828 | -121.6197 | 121.5521 | 121.5362 | 121.5989 | 106.4498 | -121.8553
896.9062 | 121.756 | -121.5408 | 0.086975 | 1.4211e-13 | -0.020472 | 0.00019651 | 0.059945 | -0.0057818 | 0.059755 | -0.2206 | -0.0033242 | -0.0036707 | 0.060638 | 0.02179 | 0.059054 | -120.8501 | -27.7083 | -121.1726 | 0.010922 | -0.050009 | -0.022864 | -121.5099 | -121.1379 | -15.0956 | -121.2502 | 0.011252 | 0.004549 | 0.067272 | -121.7546 | 0.03096 | -0.076053 | 0.69076 | 0.36823 | 0.33727 | -0.13698 | -0.10984 | -0.21381 | -0.075723 | 0.40295 | 0.29061 | 0.50442 | -0.082426 | -0.019703 | 121.5518 | 121.4908 | 121.518 | 93.8325 | -121.5968 | 121.5521 | 121.5454 | 121.6081 | 106.4452 | -121.8416
898.6562 | 121.7102 | -121.5134 | 0.10071 | 1.4211e-13 | -0.020045 | 0.00041031 | 0.060158 | -0.0059954 | 0.059541 | -0.2206 | -0.0033242 | -0.0032433 | 0.060638 | 0.02179 | 0.059054 | -120.8501 | -27.722 | -121.1726 | 0.010922 | -0.04543 | -0.027442 | -121.5236 | -121.1425 | -15.0865 | -121.2548 | 0.011252 | 0.009128 | 0.062694 | -121.7455 | -0.010243 | -0.089786 | 0.66329 | 0.34076 | 0.35101 | -0.14614 | -0.12815 | -0.23211 | -0.089456 | 0.37091 | 0.25857 | 0.49068 | -0.09158 | -0.038014 | 121.5243 | 121.4679 | 121.4859 | 93.7913 | -121.6243 | 121.5246 | 121.5225 | 121.5761 | 106.4269 | -121.8462
900.3438 | 121.7148 | -121.5317 | 0.11902 | 1.4211e-13 | -0.019831 | -1.7092e-05 | 0.060372 | -0.0057818 | 0.059328 | -0.2206 | -0.0035378 | -0.0034569 | 0.060638 | 0.02179 | 0.059267 | -120.8501 | -27.7129 | -121.1772 | 0.010922 | -0.050009 | -0.027442 | -121.5236 | -121.1425 | -15.0956 | -121.2502 | 0.011252 | -2.9e-05 | 0.067272 | -121.7501 | 0.008067 | -0.1081 | 0.6816 | 0.3545 | 0.34643 | -0.16903 | -0.14646 | -0.21838 | -0.10777 | 0.38922 | 0.28146 | 0.49984 | -0.11905 | -0.051747 | 121.5426 | 121.4817 | 121.5042 | 93.8188 | -121.6426 | 121.5429 | 121.5316 | 121.5989 | 106.436 | -121.8691
902.1094 | 121.7697 | -121.5546 | 0.10071 | 1.4211e-13 | -0.019831 | 0.00019651 | 0.060158 | -0.0059954 | 0.059755 | -0.2206 | -0.0035378 | -0.0034569 | 0.06021 | 0.02179 | 0.059054 | -120.8547 | -27.7266 | -121.1726 | 0.006344 | -0.050009 | -0.032021 | -121.5236 | -121.147 | -15.0865 | -121.2502 | 0.015831 | 0.004549 | 0.062694 | -121.7592 | 0.030955 | -0.094364 | 0.69991 | 0.38196 | 0.35101 | -0.15072 | -0.13273 | -0.20465 | -0.084877 | 0.40753 | 0.30434 | 0.509 | -0.096159 | -0.038014 | 121.5609 | 121.5046 | 121.5225 | 93.828 | -121.6243 | 121.5704 | 121.5591 | 121.6173 | 106.4681 | -121.8599
903.8438 | 121.7606 | -121.5225 | 0.11902 | 1.4211e-13 | -0.020045 | -1.7092e-05 | 0.060372 | -0.0059954 | 0.059541 | -0.2206 | -0.0035378 | -0.0034569 | 0.060424 | 0.021577 | 0.059054 | -120.8547 | -27.7266 | -121.1726 | 0.010922 | -0.050009 | -0.027442 | -121.5145 | -121.1425 | -15.0819 | -121.2548 | 0.015831 | 0.004549 | 0.062694 | -121.7592 | 0.00807 | -0.1081 | 0.66786 | 0.34992 | 0.34185 | -0.16903 | -0.14646 | -0.2367 | -0.10319 | 0.38006 | 0.26772 | 0.50442 | -0.11447 | -0.056325 | 121.5334 | 121.4725 | 121.4951 | 93.7959 | -121.6335 | 121.5384 | 121.5271 | 121.5852 | 106.4406 | -121.8782
905.5156 | 121.7285 | -121.5363 | 0.11902 | 1.4211e-13 | -0.020045 | 0.00019651 | 0.060586 | -0.0059954 | 0.059541 | -0.23586 | -0.0035378 | -0.0038843 | 0.06021 | 0.022004 | 0.059054 | -120.8547 | -27.7403 | -121.1772 | 0.006344 | -0.04543 | -0.032021 | -121.519 | -121.1425 | -15.0773 | -121.2594 | 0.015831 | 0.004549 | 0.058115 | -121.7546 | 0.017224 | -0.11267 | 0.6816 | 0.35907 | 0.34185 | -0.16445 | -0.15104 | -0.21838 | -0.10319 | 0.3938 | 0.27688 | 0.49526 | -0.11447 | -0.060904 | 121.5426 | 121.4908 | 121.5042 | 93.7959 | -121.638 | 121.5521 | 121.5408 | 121.5944 | 106.4589 | -121.8737
907.25 | 121.6919 | -121.55 | 0.13275 | 1.4211e-13 | -0.020045 | -0.00023069 | 0.060372 | -0.0057818 | 0.059328 | -0.22823 | -0.0033242 | -0.0032433 | 0.060424 | 0.021577 | 0.059054 | -120.8547 | -27.7495 | -121.1818 | 0.010922 | -0.050009 | -0.032021 | -121.519 | -121.147 | -15.0544 | -121.2548 | 0.015831 | 0.009128 | 0.062694 | -121.7592 | 0.030957 | -0.12183 | 0.69533 | 0.36823 | 0.33727 | -0.18276 | -0.16477 | -0.20923 | -0.11692 | 0.40295 | 0.29519 | 0.50442 | -0.12362 | -0.070057 | 121.5609 | 121.5 | 121.518 | 93.8005 | -121.6518 | 121.5658 | 121.5591 | 121.6127 | 106.4955 | -121.892
908.9219 | 121.7148 | -121.5408 | 0.12817 | 1.4211e-13 | -0.020258 | -1.7092e-05 | 0.060586 | -0.0059954 | 0.059541 | -0.23586 | -0.0035378 | -0.0034569 | 0.060851 | 0.022004 | 0.059481 | -120.8547 | -27.7266 | -121.1818 | 0.020079 | -0.050009 | -0.032021 | -121.5282 | -121.147 | -15.0819 | -121.264 | 0.015831 | 0.004549 | 0.062694 | -121.7546 | 0.012644 | -0.1081 | 0.68618 | 0.35907 | 0.34643 | -0.17818 | -0.1602 | -0.21381 | -0.11234 | 0.3938 | 0.27688 | 0.49068 | -0.12363 | -0.06548 | 121.5609 | 121.4908 | 121.5088 | 93.8142 | -121.6564 | 121.5567 | 121.5454 | 121.6035 | 106.4589 | -121.8828
910.6562 | 121.8658 | -121.5408 | 0.07782 | 1.4211e-13 | -0.020045 | -0.00023069 | 0.059945 | -0.0057818 | 0.059328 | -0.23586 | -0.0031106 | -0.0034569 | 0.060638 | 0.021577 | 0.059267 | -120.8547 | -27.7312 | -121.1818 | 0.015501 | -0.04543 | -0.022864 | -121.5236 | -121.1425 | -15.0865 | -121.264 | 0.015831 | 0.009128 | 0.062694 | -121.7684 | 0.017223 | -0.062319 | 0.68618 | 0.35907 | 0.34185 | -0.12325 | -0.10068 | -0.22754 | -0.061989 | 0.39838 | 0.27688 | 0.50442 | -0.068692 | -0.015126 | 121.5563 | 121.4954 | 121.518 | 93.8096 | -121.6014 | 121.5567 | 121.55 | 121.6035 | 106.4543 | -121.8462
912.3438 | 121.7697 | -121.55 | 0.12817 | 1.4211e-13 | -0.020258 | 0.00019651 | 0.060372 | -0.0057818 | 0.059114 | -0.24349 | -0.0035378 | -0.0032433 | 0.060638 | 0.02179 | 0.059054 | -120.8501 | -27.7495 | -121.1818 | 0.001765 | -0.054588 | -0.027442 | -121.5236 | -121.1425 | -15.0865 | -121.2548 | 0.011252 | 0.004549 | 0.062694 | -121.7592 | 0.026378 | -0.12641 | 0.69991 | 0.36823 | 0.34185 | -0.18276 | -0.15562 | -0.20923 | -0.11692 | 0.40753 | 0.29519 | 0.50442 | -0.12363 | -0.06548 | 121.5518 | 121.4954 | 121.5225 | 93.8005 | -121.6518 | 121.5612 | 121.5545 | 121.6127 | 106.4635 | -121.8874
914.0156 | 121.7468 | -121.5546 | 0.12817 | 1.4211e-13 | -0.020045 | 0.00019651 | 0.060158 | -0.0057818 | 0.059328 | -0.23586 | -0.0035378 | -0.0034569 | 0.06021 | 0.022004 | 0.059267 | -120.8547 | -27.7266 | -121.1818 | 0.006344 | -0.040851 | -0.027442 | -121.5236 | -121.1425 | -15.0682 | -121.2594 | 0.015831 | 0.004549 | 0.058115 | -121.7546 | 0.030955 | -0.12183 | 0.69991 | 0.3728 | 0.34185 | -0.16903 | -0.15562 | -0.20007 | -0.11234 | 0.41211 | 0.29519 | 0.49526 | -0.12363 | -0.070059 | 121.5609 | 121.5137 | 121.5271 | 93.828 | -121.6518 | 121.5704 | 121.5591 | 121.6127 | 106.4864 | -121.8828
915.75 | 121.7285 | -121.5591 | 0.10986 | 1.4211e-13 | -0.019831 | -0.00023069 | 0.060586 | -0.0057818 | 0.059114 | -0.23586 | -0.0035378 | -0.0034569 | 0.060638 | 0.02179 | 0.059054 | -120.8547 | -27.7312 | -121.1818 | 0.010922 | -0.050009 | -0.027442 | -121.5282 | -121.147 | -15.0682 | -121.264 | 0.015831 | 0.004549 | 0.067272 | -121.7684 | 0.030954 | -0.098941 | 0.70449 | 0.37738 | 0.34643 | -0.15987 | -0.13731 | -0.20923 | -0.094032 | 0.41211 | 0.29519 | 0.50442 | -0.10531 | -0.042591 | 121.5701 | 121.5091 | 121.5317 | 93.828 | -121.6381 | 121.575 | 121.5637 | 121.6264 | 106.491 | -121.8782
917.4219 | 121.7056 | -121.5363 | 0.11902 | 1.4211e-13 | -0.019831 | -1.7092e-05 | 0.060799 | -0.005568 | 0.0589 | -0.22823 | -0.0035378 | -0.0032433 | 0.060424 | 0.022004 | 0.059054 | -120.8547 | -27.7587 | -121.1772 | 0.010922 | -0.054588 | -0.027442 | -121.5282 | -121.1516 | -15.0544 | -121.2685 | 0.011252 | 0.009128 | 0.058115 | -121.7592 | 0.008066 | -0.1081 | 0.6816 | 0.35907 | 0.35101 | -0.17361 | -0.14646 | -0.22296 | -0.10777 | 0.38464 | 0.26772 | 0.49068 | -0.10989 | -0.060904 | 121.5472 | 121.4817 | 121.5088 | 93.7776 | -121.6472 | 121.5475 | 121.5454 | 121.5944 | 106.4818 | -121.8782
919.1562 | 121.788 | -121.5408 | 0.11444 | 1.4211e-13 | -0.020258 | 0.00019651 | 0.060372 | -0.0057818 | 0.059328 | -0.23586 | -0.0035378 | -0.0036707 | 0.060851 | 0.02179 | 0.05884 | -120.8638 | -27.7861 | -121.1818 | 0.010922 | -0.050009 | -0.022864 | -121.5328 | -121.147 | -15.0682 | -121.2685 | 0.011252 | -2.9e-05 | 0.058115 | -121.7638 | 0.008065 | -0.10352 | 0.67702 | 0.35907 | 0.35101 | -0.16445 | -0.13731 | -0.22296 | -0.10319 | 0.3938 | 0.2723 | 0.49526 | -0.11447 | -0.056326 | 121.5518 | 121.4908 | 121.518 | 93.7547 | -121.6472 | 121.5521 | 121.5408 | 121.5989 | 106.4727 | -121.8782
920.8906 | 121.7789 | -121.5408 | 0.10529 | 1.4211e-13 | -0.020258 | 0.00019651 | 0.060372 | -0.0059954 | 0.059114 | -0.22823 | -0.0033242 | -0.0032433 | 0.060638 | 0.022218 | 0.059054 | -120.8547 | -27.7449 | -121.1818 | 0.001765 | -0.04543 | -0.027442 | -121.5282 | -121.1516 | -15.0956 | -121.2594 | 0.011252 | 0.013707 | 0.062694 | -121.7684 | 0.012644 | -0.10352 | 0.68618 | 0.35907 | 0.34643 | -0.15072 | -0.13273 | -0.22754 | -0.094034 | 0.38922 | 0.28145 | 0.509 | -0.091579 | -0.042592 | 121.5426 | 121.4954 | 121.5134 | 93.7959 | -121.6335 | 121.5521 | 121.5545 | 121.6035 | 106.4452 | -121.8737
922.5625 | 121.7972 | -121.5271 | 0.09613 | 1.4211e-13 | -0.020258 | 0.00019651 | 0.060158 | -0.005568 | 0.059328 | -0.22823 | -0.0033242 | -0.0036707 | 0.060424 | 0.02179 | 0.059267 | -120.8638 | -27.7587 | -121.1818 | 0.010922 | -0.050009 | -0.027442 | -121.5328 | -121.1516 | -15.0819 | -121.264 | 0.015831 | 0.004549 | 0.067272 | -121.7638 | -0.005668 | -0.085208 | 0.66329 | 0.34534 | 0.35101 | -0.14614 | -0.12357 | -0.2367 | -0.080299 | 0.37548 | 0.26314 | 0.49984 | -0.091581 | -0.028858 | 121.538 | 121.4771 | 121.4997 | 93.7684 | -121.6289 | 121.5429 | 121.5316 | 121.5944 | 106.4452 | -121.8599
924.2969 | 121.8246 | -121.5454 | 0.086975 | 1.4211e-13 | -0.020472 | -1.7092e-05 | 0.060586 | -0.0057818 | 0.0589 | -0.22823 | -0.0037514 | -0.0036707 | 0.060638 | 0.021577 | 0.05884 | -120.8638 | -27.7678 | -121.1818 | 0.006344 | -0.050009 | -0.022864 | -121.5328 | -121.1562 | -15.0728 | -121.264 | 0.011252 | 0.009128 | 0.071851 | -121.773 | 0.012642 | -0.080631 | 0.6816 | 0.36365 | 0.35101 | -0.13698 | -0.10984 | -0.22754 | -0.075723 | 0.38922 | 0.28145 | 0.509 | -0.077847 | -0.015124 | 121.5518 | 121.4954 | 121.5225 | 93.7776 | -121.6197 | 121.5567 | 121.5545 | 121.6173 | 106.4727 | -121.8599
926.0312 | 121.7239 | -121.5637 | 0.13275 | 1.4211e-13 | -0.020258 | -1.7092e-05 | 0.060372 | -0.005568 | 0.059541 | -0.21297 | -0.0035378 | -0.0036707 | 0.060638 | 0.022004 | 0.058627 | -120.8592 | -27.7861 | -121.1818 | 0.010922 | -0.040851 | -0.018285 | -121.5373 | -121.1562 | -15.0865 | -121.264 | 0.015831 | 0.009128 | 0.062694 | -121.7775 | 0.026375 | -0.12183 | 0.70449 | 0.38196 | 0.35559 | -0.1736 | -0.15104 | -0.21381 | -0.11692 | 0.40753 | 0.29976 | 0.51358 | -0.12362 | -0.070057 | 121.5746 | 121.5229 | 121.5454 | 93.7776 | -121.6701 | 121.5796 | 121.5728 | 121.6264 | 106.4772 | -121.9103
927.7812 | 121.7651 | -121.5637 | 0.11444 | 1.4211e-13 | -0.020472 | 0.00019651 | 0.060372 | -0.005568 | 0.059114 | -0.22823 | -0.0037514 | -0.0032433 | 0.060424 | 0.022004 | 0.05884 | -120.8684 | -27.7861 | -121.1818 | 0.010922 | -0.040851 | -0.027442 | -121.5328 | -121.1562 | -15.059 | -121.264 | 0.006674 | -2.9e-05 | 0.062694 | -121.7775 | 0.030953 | -0.10352 | 0.69533 | 0.38196 | 0.35101 | -0.15529 | -0.14188 | -0.21381 | -0.10777 | 0.40753 | 0.29976 | 0.51358 | -0.11447 | -0.051747 | 121.5746 | 121.5229 | 121.5363 | 93.7776 | -121.6472 | 121.5704 | 121.5637 | 121.6264 | 106.5047 | -121.892
929.4531 | 121.756 | -121.5729 | 0.11444 | 1.4211e-13 | -0.020258 | -1.7092e-05 | 0.060372 | -0.005568 | 0.059114 | -0.2206 | -0.0033242 | -0.0036707 | 0.060851 | 0.022004 | 0.058627 | -120.8638 | -27.7861 | -121.1909 | 0.020079 | -0.050009 | -0.022864 | -121.5328 | -121.1562 | -15.0728 | -121.2685 | 0.011252 | 0.009128 | 0.067272 | -121.773 | 0.040108 | -0.094362 | 0.70906 | 0.38196 | 0.34185 | -0.16445 | -0.13731 | -0.20008 | -0.10319 | 0.41668 | 0.30434 | 0.50442 | -0.10531 | -0.047169 | 121.593 | 121.5229 | 121.55 | 93.7867 | -121.6472 | 121.5841 | 121.582 | 121.6401 | 106.5001 | -121.8874
931.1875 | 121.8201 | -121.5179 | 0.082397 | 1.4211e-13 | -0.020258 | -1.7092e-05 | 0.060372 | -0.0059954 | 0.0589 | -0.23586 | -0.0033242 | -0.0034569 | 0.060638 | 0.022004 | 0.05884 | -120.8684 | -27.7816 | -121.1863 | 0.015501 | -0.04543 | -0.022864 | -121.5328 | -121.1608 | -15.0544 | -121.2594 | 0.015831 | 0.009128 | 0.067272 | -121.773 | -0.014824 | -0.066896 | 0.64955 | 0.3316 | 0.34643 | -0.12783 | -0.10526 | -0.25501 | -0.066566 | 0.35717 | 0.25856 | 0.51358 | -0.073269 | -0.015125 | 121.5334 | 121.4725 | 121.4951 | 93.7364 | -121.6152 | 121.5338 | 121.5271 | 121.5852 | 106.4635 | -121.8554
932.9219 | 121.7789 | -121.5775 | 0.11902 | 1.4211e-13 | -0.020472 | 0.00041031 | 0.059945 | -0.0057818 | 0.059114 | -0.2206 | -0.0035378 | -0.0034569 | 0.060851 | 0.022431 | 0.058627 | -120.873 | -27.7632 | -121.1863 | 0.006344 | -0.04543 | -0.0366 | -121.5373 | -121.1516 | -15.0544 | -121.2685 | 0.015831 | -2.9e-05 | 0.067272 | -121.7775 | 0.040108 | -0.11267 | 0.70448 | 0.39111 | 0.35101 | -0.16445 | -0.15562 | -0.20008 | -0.10319 | 0.42584 | 0.30892 | 0.509 | -0.11905 | -0.051747 | 121.5838 | 121.532 | 121.5409 | 93.8142 | -121.6564 | 121.5933 | 121.5774 | 121.6447 | 106.523 | -121.8966
934.6562 | 121.8796 | -121.5134 | 0.082397 | 1.4211e-13 | -0.020472 | -1.7092e-05 | 0.060372 | -0.0057818 | 0.059114 | -0.23586 | -0.0031106 | -0.0038843 | 0.06021 | 0.022004 | 0.059267 | -120.8684 | -27.7907 | -121.1909 | 0.006344 | -0.050009 | -0.027442 | -121.5373 | -121.1562 | -15.0728 | -121.2731 | 0.011252 | 0.009128 | 0.062694 | -121.7775 | -0.023979 | -0.076053 | 0.64498 | 0.32245 | 0.34643 | -0.13241 | -0.10984 | -0.26417 | -0.071145 | 0.35717 | 0.24025 | 0.50442 | -0.073269 | -0.019703 | 121.5197 | 121.4634 | 121.4859 | 93.7227 | -121.6197 | 121.5246 | 121.5225 | 121.5761 | 106.4406 | -121.8599
936.3906 | 121.7697 | -121.5637 | 0.11902 | 1.4211e-13 | -0.020258 | -1.7092e-05 | 0.060158 | -0.0057818 | 0.059114 | -0.21297 | -0.0035378 | -0.0034569 | 0.060424 | 0.022004 | 0.05884 | -120.8684 | -27.7495 | -121.1909 | 0.010922 | -0.040851 | -0.022864 | -121.5328 | -121.1608 | -15.0499 | -121.2777 | 0.011252 | 0.004549 | 0.058115 | -121.7775 | 0.030953 | -0.1081 | 0.69533 | 0.3728 | 0.34185 | -0.15987 | -0.14188 | -0.21381 | -0.10777 | 0.40295 | 0.28603 | 0.49984 | -0.11447 | -0.060904 | 121.5746 | 121.5229 | 121.5409 | 93.8142 | -121.6518 | 121.575 | 121.5683 | 121.6218 | 106.5139 | -121.8966
938.125 | 121.8292 | -121.5454 | 0.086975 | 1.4211e-13 | -0.020472 | -1.7092e-05 | 0.060372 | -0.006209 | 0.059328 | -0.2206 | -0.0033242 | -0.0036707 | 0.060424 | 0.022004 | 0.058627 | -120.873 | -27.7678 | -121.1772 | 0.006344 | -0.04543 | -0.018285 | -121.5373 | -121.1654 | -15.0773 | -121.2731 | 0.011252 | 0.004549 | 0.067272 | -121.7821 | 0.008064 | -0.080631 | 0.67244 | 0.36823 | 0.36016 | -0.1324 | -0.10526 | -0.2367 | -0.075723 | 0.38006 | 0.27229 | 0.509 | -0.082426 | -0.019703 | 121.5518 | 121.5 | 121.5271 | 93.7776 | -121.6243 | 121.5567 | 121.55 | 121.6127 | 106.4681 | -121.8691
939.8125 | 121.8246 | -121.5546 | 0.091553 | 1.4211e-13 | -0.020472 | -0.00023069 | 0.060158 | -0.0059954 | 0.059114 | -0.22823 | -0.0033242 | -0.0034569 | 0.060424 | 0.022004 | 0.05884 | -120.8684 | -27.7861 | -121.1909 | 0.010922 | -0.050009 | -0.022864 | -121.5373 | -121.1654 | -15.0544 | -121.264 | 0.011252 | 0.009128 | 0.062694 | -121.7775 | 0.017219 | -0.080631 | 0.68617 | 0.36365 | 0.34643 | -0.14156 | -0.11442 | -0.22297 | -0.080301 | 0.38921 | 0.29061 | 0.51358 | -0.082425 | -0.028859 | 121.5655 | 121.5046 | 121.5317 | 93.7684 | -121.6289 | 121.5658 | 121.5637 | 121.6173 | 106.5001 | -121.8691
941.5625 | 121.7834 | -121.5591 | 0.11902 | 1.4211e-13 | -0.020686 | -0.00023069 | 0.060586 | -0.0057818 | 0.059328 | -0.2206 | -0.0031106 | -0.0034569 | 0.061065 | 0.022431 | 0.05884 | -120.8638 | -27.7953 | -121.1955 | 0.010922 | -0.050009 | -0.032021 | -121.5465 | -121.1654 | -15.0544 | -121.2685 | 0.015831 | 0.009128 | 0.067272 | -121.7821 | 0.012639 | -0.1081 | 0.69533 | 0.36365 | 0.35101 | -0.16903 | -0.15104 | -0.22297 | -0.10319 | 0.39379 | 0.29061 | 0.51358 | -0.10989 | -0.051747 | 121.5701 | 121.5091 | 121.5271 | 93.7639 | -121.6655 | 121.575 | 121.5683 | 121.6264 | 106.5047 | -121.9011
943.2969 | 121.8704 | -121.5179 | 0.091553 | 1.4211e-13 | -0.020472 | 0.00019651 | 0.059945 | -0.005568 | 0.059328 | -0.22823 | -0.0031106 | -0.0034569 | 0.060424 | 0.022004 | 0.058413 | -120.8684 | -27.7999 | -121.1909 | 0.010922 | -0.04543 | -0.022864 | -121.5419 | -121.1654 | -15.0682 | -121.2777 | 0.015831 | 0.004549 | 0.067272 | -121.7958 | -0.023981 | -0.080631 | 0.64955 | 0.32703 | 0.35101 | -0.13698 | -0.11442 | -0.27791 | -0.075722 | 0.35259 | 0.24025 | 0.51816 | -0.087004 | -0.024281 | 121.5289 | 121.4725 | 121.4951 | 93.7181 | -121.6335 | 121.5338 | 121.5225 | 121.5852 | 106.4498 | -121.8874
944.9688 | 121.8704 | -121.5408 | 0.091553 | 1.4211e-13 | -0.020899 | -1.7092e-05 | 0.060158 | -0.005568 | 0.059328 | -0.2206 | -0.0035378 | -0.0036707 | 0.060638 | 0.022218 | 0.05884 | -120.8684 | -27.7999 | -121.1955 | 0.010922 | -0.04543 | -0.022864 | -121.5511 | -121.1699 | -15.0544 | -121.264 | 0.011252 | -2.9e-05 | 0.062694 | -121.7913 | -0.01025 | -0.080631 | 0.67244 | 0.34534 | 0.35559 | -0.13698 | -0.11442 | -0.25044 | -0.080301 | 0.3709 | 0.27688 | 0.52731 | -0.091582 | -0.028859 | 121.5518 | 121.4954 | 121.518 | 93.741 | -121.6426 | 121.5521 | 121.5408 | 121.6035 | 106.4864 | -121.8828
946.7031 | 121.8613 | -121.5271 | 0.091553 | 1.4211e-13 | -0.020686 | -1.7092e-05 | 0.059945 | -0.0057818 | 0.059114 | -0.2206 | -0.0035378 | -0.0032433 | 0.060638 | 0.022431 | 0.058413 | -120.873 | -27.7861 | -121.1909 | 0.006344 | -0.04543 | -0.022864 | -121.5419 | -121.1699 | -15.0773 | -121.2685 | 0.015831 | 0.004549 | 0.067272 | -121.7913 | -0.014825 | -0.085209 | 0.65413 | 0.33618 | 0.35101 | -0.13698 | -0.11442 | -0.26417 | -0.075722 | 0.35717 | 0.25856 | 0.52273 | -0.087004 | -0.024281 | 121.5334 | 121.4817 | 121.5042 | 93.741 | -121.6335 | 121.5429 | 121.5316 | 121.5944 | 106.4498 | -121.8828
948.375 | 121.7422 | -121.5729 | 0.12817 | 1.4211e-13 | -0.020258 | -1.7092e-05 | 0.060372 | -0.0057818 | 0.059541 | -0.2206 | -0.0033242 | -0.0036707 | 0.060638 | 0.022004 | 0.05884 | -120.8684 | -27.7587 | -121.1863 | 0.015501 | -0.050009 | -0.032021 | -121.5511 | -121.1699 | -15.0819 | -121.2685 | 0.006674 | 0.004549 | 0.067272 | -121.8004 | 0.021793 | -0.11267 | 0.70448 | 0.38654 | 0.36474 | -0.17818 | -0.1602 | -0.22755 | -0.1215 | 0.40295 | 0.30434 | 0.53189 | -0.12363 | -0.060902 | 121.5884 | 121.5229 | 121.5409 | 93.8142 | -121.6793 | 121.5795 | 121.5774 | 121.6401 | 106.491 | -121.9286
950.1094 | 121.7377 | -121.5958 | 0.10986 | 1.4211e-13 | -0.020686 | -0.00023069 | 0.060586 | -0.0059954 | 0.059114 | -0.22823 | -0.0031106 | -0.0034569 | 0.060424 | 0.022218 | 0.05884 | -120.873 | -27.777 | -121.1909 | 0.006344 | -0.04543 | -0.027442 | -121.5419 | -121.1608 | -15.0956 | -121.2685 | 0.011252 | 0.004549 | 0.067272 | -121.7958 | 0.053839 | -0.10352 | 0.72279 | 0.40485 | 0.35101 | -0.15529 | -0.13731 | -0.20009 | -0.098611 | 0.43499 | 0.32723 | 0.52731 | -0.10531 | -0.042591 | 121.6021 | 121.5503 | 121.5683 | 93.8188 | -121.6518 | 121.607 | 121.6003 | 121.663 | 106.5001 | -121.9057
951.8438 | 121.7468 | -121.5775 | 0.11444 | 1.4211e-13 | -0.020686 | 0.00019651 | 0.060372 | -0.005568 | 0.059114 | -0.23586 | -0.0033242 | -0.0036707 | 0.06021 | 0.022645 | 0.05884 | -120.8684 | -27.8044 | -121.1863 | 0.010922 | -0.050009 | -0.032021 | -121.5511 | -121.1699 | -15.1094 | -121.2731 | 0.020409 | -2.9e-05 | 0.071851 | -121.7958 | 0.026371 | -0.10352 | 0.70906 | 0.39111 | 0.36474 | -0.16445 | -0.14646 | -0.2184 | -0.094032 | 0.40752 | 0.30434 | 0.52273 | -0.11447 | -0.04259 | 121.5884 | 121.5274 | 121.5454 | 93.773 | -121.6655 | 121.5979 | 121.5774 | 121.6493 | 106.4681 | -121.9103
953.5938 | 121.843 | -121.5454 | 0.07782 | 1.4211e-13 | -0.020686 | -1.7092e-05 | 0.059945 | -0.0057818 | 0.059328 | -0.22823 | -0.0031106 | -0.0032433 | 0.060424 | 0.022431 | 0.058627 | -120.8684 | -27.8136 | -121.1955 | 0.010922 | -0.050009 | -0.022864 | -121.5511 | -121.1654 | -15.0682 | -121.2731 | 0.020409 | 0.013707 | 0.062694 | -121.7958 | -0.005673 | -0.066898 | 0.67702 | 0.34992 | 0.35559 | -0.12783 | -0.10068 | -0.25044 | -0.057411 | 0.38006 | 0.27229 | 0.52273 | -0.064113 | -0.015126 | 121.5563 | 121.4954 | 121.5225 | 93.7318 | -121.6289 | 121.5658 | 121.5591 | 121.6081 | 106.4772 | -121.8737
955.3438 | 121.8658 | -121.5546 | 0.091553 | 1.4211e-13 | -0.020686 | -0.00044449 | 0.060372 | -0.0053544 | 0.0589 | -0.22823 | -0.0031106 | -0.0034569 | 0.06021 | 0.022218 | 0.05884 | -120.873 | -27.7999 | -121.1955 | 0.015501 | -0.050009 | -0.022864 | -121.5511 | -121.1745 | -15.0865 | -121.2777 | 0.006674 | 0.004549 | 0.067272 | -121.8004 | 0.003482 | -0.076052 | 0.6816 | 0.35907 | 0.35559 | -0.14156 | -0.11442 | -0.24586 | -0.084879 | 0.38006 | 0.27687 | 0.52273 | -0.087004 | -0.024281 | 121.5701 | 121.5046 | 121.5317 | 93.7547 | -121.6426 | 121.5612 | 121.5591 | 121.6218 | 106.4681 | -121.892
957.0312 | 121.875 | -121.5408 | 0.07782 | 1.4211e-13 | -0.020899 | -0.00023069 | 0.059945 | -0.006209 | 0.0589 | -0.23586 | -0.0037514 | -0.0034569 | 0.060424 | 0.022004 | 0.058627 | -120.8684 | -27.8182 | -121.1909 | 0.015501 | -0.04543 | -0.027442 | -121.5465 | -121.1745 | -15.0636 | -121.2777 | 0.011252 | 0.013707 | 0.071851 | -121.7958 | -0.005671 | -0.062319 | 0.67244 | 0.34992 | 0.35559 | -0.12325 | -0.10526 | -0.25502 | -0.066568 | 0.36632 | 0.26314 | 0.51816 | -0.064113 | -0.005969 | 121.5563 | 121.4954 | 121.5134 | 93.7227 | -121.6243 | 121.5521 | 121.5545 | 121.6127 | 106.4772 | -121.8737
958.7969 | 121.8338 | -121.5729 | 0.10071 | 1.4211e-13 | -0.021113 | -0.00044449 | 0.060586 | -0.0057818 | 0.059114 | -0.23586 | -0.0033242 | -0.0032433 | 0.060424 | 0.022645 | 0.058199 | -120.8684 | -27.8228 | -121.2047 | 0.010922 | -0.04543 | -0.022864 | -121.5511 | -121.1608 | -15.1048 | -121.2777 | 0.015831 | 0.013707 | 0.067272 | -121.8004 | 0.021793 | -0.089786 | 0.70448 | 0.36822 | 0.34643 | -0.14614 | -0.12357 | -0.22755 | -0.084877 | 0.4121 | 0.29518 | 0.52273 | -0.087001 | -0.033436 | 121.5838 | 121.5274 | 121.55 | 93.7501 | -121.6518 | 121.5887 | 121.5866 | 121.6401 | 106.4681 | -121.9011
960.5469 | 121.8704 | -121.5454 | 0.082397 | 1.4211e-13 | -0.020899 | -1.7092e-05 | 0.060158 | -0.0059954 | 0.059114 | -0.2206 | -0.0035378 | -0.0032433 | 0.06021 | 0.022004 | 0.05884 | -120.8775 | -27.8136 | -121.2001 | 0.015501 | -0.040851 | -0.027442 | -121.5465 | -121.1791 | -15.0819 | -121.2777 | 0.015831 | 0.009128 | 0.062694 | -121.8004 | -0.001094 | -0.066896 | 0.66786 | 0.34534 | 0.34643 | -0.12325 | -0.10984 | -0.25502 | -0.066566 | 0.36632 | 0.26772 | 0.52273 | -0.073269 | -0.019703 | 121.5609 | 121.5046 | 121.518 | 93.7318 | -121.6289 | 121.5612 | 121.5545 | 121.6081 | 106.4635 | -121.8828
962.2969 | 121.8796 | -121.4996 | 0.07782 | 1.4211e-13 | -0.020899 | -0.00023069 | 0.060372 | -0.0057818 | 0.0589 | -0.22823 | -0.0035378 | -0.0036707 | 0.060424 | 0.022218 | 0.05884 | -120.8684 | -27.7999 | -121.2001 | 0.010922 | -0.04543 | -0.032021 | -121.5602 | -121.1608 | -15.0911 | -121.2777 | 0.006674 | -0.004608 | 0.062694 | -121.805 | -0.060607 | -0.066898 | 0.63124 | 0.29956 | 0.36017 | -0.12325 | -0.10984 | -0.30537 | -0.071146 | 0.33886 | 0.22194 | 0.52731 | -0.082428 | -0.015126 | 121.5106 | 121.4542 | 121.4676 | 93.6998 | -121.6381 | 121.5063 | 121.495 | 121.5623 | 106.4086 | -121.8828
963.9688 | 121.843 | -121.5454 | 0.091553 | 1.4211e-13 | -0.020899 | -1.7092e-05 | 0.059945 | -0.0059954 | 0.059114 | -0.22823 | -0.0035378 | -0.0038843 | 0.060424 | 0.022645 | 0.058627 | -120.8775 | -27.7999 | -121.2001 | 0.006344 | -0.040851 | -0.022864 | -121.5511 | -121.1791 | -15.1002 | -121.2869 | 0.015831 | 0.004549 | 0.067272 | -121.805 | -0.005673 | -0.085209 | 0.66786 | 0.34534 | 0.35101 | -0.1324 | -0.11442 | -0.2596 | -0.075722 | 0.36632 | 0.25856 | 0.51815 | -0.087004 | -0.024281 | 121.5518 | 121.5046 | 121.5225 | 93.7455 | -121.6426 | 121.5612 | 121.55 | 121.6127 | 106.4452 | -121.8966
965.6562 | 121.7743 | -121.5637 | 0.10529 | 1.4211e-13 | -0.021113 | -0.00044449 | 0.060372 | -0.0059954 | 0.0589 | -0.23586 | -0.0035378 | -0.0034569 | 0.06021 | 0.022431 | 0.05884 | -120.8775 | -27.8044 | -121.1909 | 0.010922 | -0.040851 | -0.022864 | -121.5511 | -121.1745 | -15.1094 | -121.2823 | 0.015831 | 0.009128 | 0.067272 | -121.805 | 0.012638 | -0.094364 | 0.68617 | 0.3728 | 0.36017 | -0.14614 | -0.12815 | -0.24129 | -0.089455 | 0.38921 | 0.28145 | 0.52273 | -0.096158 | -0.038014 | 121.5746 | 121.5229 | 121.5409 | 93.7593 | -121.6564 | 121.5796 | 121.5728 | 121.631 | 106.4543 | -121.9103
967.4062 | 121.7972 | -121.5775 | 0.09613 | 1.4211e-13 | -0.020686 | -1.7092e-05 | 0.060158 | -0.0059954 | 0.059328 | -0.2206 | -0.0033242 | -0.0032433 | 0.060638 | 0.022859 | 0.059054 | -120.8775 | -27.8365 | -121.2092 | 0.001765 | -0.050009 | -0.018285 | -121.5511 | -121.1745 | -15.0865 | -121.2869 | 0.015831 | 0.009128 | 0.071851 | -121.805 | 0.026371 | -0.094365 | 0.69991 | 0.36822 | 0.34185 | -0.14614 | -0.11441 | -0.22755 | -0.080299 | 0.40295 | 0.2906 | 0.51815 | -0.087002 | -0.024279 | 121.5792 | 121.5274 | 121.5592 | 93.741 | -121.6472 | 121.5933 | 121.5866 | 121.6493 | 106.491 | -121.9011
969.0781 | 121.7972 | -121.5591 | 0.11444 | 1.4211e-13 | -0.021113 | -1.7092e-05 | 0.060158 | -0.0059954 | 0.059328 | -0.2206 | -0.0031106 | -0.0034569 | 0.060424 | 0.022218 | 0.05884 | -120.8821 | -27.7861 | -121.2001 | 0.006344 | -0.04543 | -0.027442 | -121.5557 | -121.1791 | -15.0728 | -121.2823 | 0.015831 | -2.9e-05 | 0.067272 | -121.805 | 0.003481 | -0.1081 | 0.67702 | 0.35907 | 0.35559 | -0.15987 | -0.14188 | -0.24586 | -0.09861 | 0.38006 | 0.27687 | 0.52273 | -0.11447 | -0.047169 | 121.5655 | 121.5137 | 121.5317 | 93.773 | -121.6701 | 121.575 | 121.5591 | 121.6264 | 106.4864 | -121.9194
970.8125 | 121.8338 | -121.5729 | 0.086975 | 1.4211e-13 | -0.020899 | -1.7092e-05 | 0.060372 | -0.0059954 | 0.0589 | -0.22823 | -0.0035378 | -0.0032433 | 0.060424 | 0.022645 | 0.058627 | -120.873 | -27.8136 | -121.2047 | 0.010922 | -0.050009 | -0.018285 | -121.5557 | -121.1791 | -15.0819 | -121.2777 | 0.015831 | 0.004549 | 0.067272 | -121.8096 | 0.017214 | -0.076053 | 0.69991 | 0.36822 | 0.35101 | -0.13698 | -0.10526 | -0.23671 | -0.071144 | 0.39379 | 0.29518 | 0.53189 | -0.082426 | -0.019703 | 121.5838 | 121.5229 | 121.5546 | 93.7593 | -121.6426 | 121.5887 | 121.5774 | 121.6401 | 106.491 | -121.8966
972.5 | 121.8933 | -121.55 | 0.082397 | 1.4211e-13 | -0.021113 | -0.00065809 | 0.059945 | -0.005568 | 0.059328 | -0.23586 | -0.0031106 | -0.0036707 | 0.060424 | 0.022645 | 0.058199 | -120.8775 | -27.7907 | -121.2047 | 0.010922 | -0.040851 | -0.027442 | -121.5602 | -121.1837 | -15.0819 | -121.2869 | 0.006674 | 0.009128 | 0.067272 | -121.805 | -0.010253 | -0.071475 | 0.67244 | 0.34534 | 0.35559 | -0.12325 | -0.10984 | -0.25502 | -0.075723 | 0.36632 | 0.26314 | 0.51815 | -0.073269 | -0.015125 | 121.5609 | 121.5091 | 121.5225 | 93.7593 | -121.6426 | 121.5567 | 121.5591 | 121.6173 | 106.4681 | -121.8874
974.1719 | 121.8613 | -121.5271 | 0.10986 | 1.4211e-13 | -0.021113 | -1.7092e-05 | 0.060158 | -0.0059954 | 0.059114 | -0.2206 | -0.0033242 | -0.0036707 | 0.060424 | 0.022645 | 0.058413 | -120.8821 | -27.809 | -121.2047 | 0.010922 | -0.050009 | -0.022864 | -121.5648 | -121.1745 | -15.0819 | -121.2914 | 0.020409 | -2.9e-05 | 0.071851 | -121.8096 | -0.03772 | -0.098941 | 0.64497 | 0.32245 | 0.36017 | -0.15987 | -0.13273 | -0.28248 | -0.089454 | 0.35259 | 0.23567 | 0.51815 | -0.10989 | -0.038012 | 121.538 | 121.4771 | 121.5042 | 93.7181 | -121.6747 | 121.5475 | 121.5271 | 121.599 | 106.4452 | -121.9194
975.9062 | 121.8155 | -121.5591 | 0.091553 | 1.4211e-13 | -0.021327 | -1.7092e-05 | 0.059945 | -0.0059954 | 0.0589 | -0.22823 | -0.0033242 | -0.0036707 | 0.06021 | 0.022859 | 0.058627 | -120.873 | -27.7907 | -121.1955 | 0.010922 | -0.04543 | -0.022864 | -121.5557 | -121.1699 | -15.059 | -121.2869 | 0.020409 | 0.004549 | 0.071851 | -121.8096 | 0.003481 | -0.080631 | 0.68617 | 0.36365 | 0.36017 | -0.13698 | -0.11442 | -0.25044 | -0.071144 | 0.38921 | 0.27229 | 0.52273 | -0.087004 | -0.019702 | 121.5701 | 121.5137 | 121.5363 | 93.7684 | -121.6472 | 121.5796 | 121.5637 | 121.631 | 106.5001 | -121.9011
977.5781 | 121.7697 | -121.6049 | 0.13275 | 1.4211e-13 | -0.021113 | -1.7092e-05 | 0.059945 | -0.0059954 | 0.059328 | -0.23586 | -0.0033242 | -0.0036707 | 0.060424 | 0.022859 | 0.058413 | -120.8821 | -27.7999 | -121.2047 | 0.010922 | -0.040851 | -0.032021 | -121.5602 | -121.1745 | -15.059 | -121.2914 | 0.011252 | 0.009128 | 0.067272 | -121.8142 | 0.044678 | -0.12183 | 0.72279 | 0.40027 | 0.35559 | -0.1736 | -0.16477 | -0.20925 | -0.1215 | 0.43041 | 0.31349 | 0.52273 | -0.12362 | -0.065479 | 121.6158 | 121.5641 | 121.5729 | 93.8051 | -121.693 | 121.6162 | 121.614 | 121.6722 | 106.5459 | -121.9469
979.3125 | 121.8384 | -121.5546 | 0.082397 | 1.4211e-13 | -0.021327 | -1.7092e-05 | 0.060158 | -0.0059954 | 0.059114 | -0.2206 | -0.0033242 | -0.0032433 | 0.060638 | 0.022645 | 0.058627 | -120.8867 | -27.8044 | -121.2092 | 0.006344 | -0.054588 | -0.022864 | -121.5602 | -121.1745 | -15.0728 | -121.2869 | 0.011252 | 0.013707 | 0.071851 | -121.805 | -0.005676 | -0.076053 | 0.66786 | 0.34533 | 0.35101 | -0.13698 | -0.10526 | -0.25044 | -0.071145 | 0.38006 | 0.26771 | 0.51815 | -0.06869 | -0.010546 | 121.5609 | 121.5 | 121.5317 | 93.7501 | -121.6426 | 121.5658 | 121.5683 | 121.6264 | 106.4818 | -121.8874
980.9844 | 121.8338 | -121.5591 | 0.09613 | 1.4211e-13 | -0.021113 | -0.00023069 | 0.059945 | -0.0059954 | 0.059114 | -0.22823 | -0.0033242 | -0.0032433 | 0.060424 | 0.022645 | 0.058413 | -120.8775 | -27.7724 | -121.2092 | 0.010922 | -0.050009 | -0.022864 | -121.5602 | -121.1837 | -15.0728 | -121.2914 | 0.011252 | 0.013707 | 0.067272 | -121.8187 | -0.001098 | -0.085208 | 0.68159 | 0.34991 | 0.35101 | -0.14614 | -0.11899 | -0.2596 | -0.084878 | 0.37548 | 0.26771 | 0.52731 | -0.082423 | -0.028858 | 121.5701 | 121.5091 | 121.5363 | 93.7867 | -121.6564 | 121.5704 | 121.5729 | 121.6264 | 106.4864 | -121.9149
982.7344 | 121.8567 | -121.5637 | 0.10071 | 1.4211e-13 | -0.021327 | -0.00023069 | 0.060372 | -0.0057818 | 0.059114 | -0.21297 | -0.0033242 | -0.0034569 | 0.060424 | 0.022645 | 0.058627 | -120.8775 | -27.8136 | -121.2092 | 0.001765 | -0.050009 | -0.018285 | -121.5602 | -121.1791 | -15.059 | -121.2914 | 0.015831 | -2.9e-05 | 0.067272 | -121.8096 | 0.00348 | -0.098943 | 0.68617 | 0.35449 | 0.35101 | -0.15072 | -0.11899 | -0.24586 | -0.084877 | 0.38463 | 0.27229 | 0.51815 | -0.10074 | -0.033436 | 121.5655 | 121.5137 | 121.5454 | 93.7501 | -121.6609 | 121.5796 | 121.5637 | 121.631 | 106.5047 | -121.9103
984.4062 | 121.875 | -121.5363 | 0.086975 | 1.4211e-13 | -0.021113 | -0.00023069 | 0.060158 | -0.006209 | 0.059114 | -0.22823 | -0.0033242 | -0.0034569 | 0.060424 | 0.022859 | 0.058627 | -120.8775 | -27.8182 | -121.2092 | 0.015501 | -0.050009 | -0.022864 | -121.5602 | -121.1837 | -15.0728 | -121.2869 | 0.002095 | -2.9e-05 | 0.058115 | -121.8187 | -0.023986 | -0.071474 | 0.65871 | 0.32702 | 0.35101 | -0.13698 | -0.10984 | -0.28249 | -0.08488 | 0.35259 | 0.2494 | 0.53189 | -0.087004 | -0.02886 | 121.5518 | 121.4862 | 121.5134 | 93.7181 | -121.6472 | 121.5383 | 121.5362 | 121.5944 | 106.4635 | -121.9057
986.1406 | 121.7926 | -121.5591 | 0.10986 | 1.4211e-13 | -0.021327 | -0.00023069 | 0.059945 | -0.006209 | 0.0589 | -0.23586 | -0.0031106 | -0.0034569 | 0.060424 | 0.023072 | 0.058627 | -120.8867 | -27.7816 | -121.2092 | 0.010922 | -0.050009 | -0.022864 | -121.5602 | -121.1837 | -15.0636 | -121.3006 | 0.020409 | -0.004608 | 0.067272 | -121.8142 | -0.001098 | -0.098941 | 0.67244 | 0.34991 | 0.35101 | -0.15987 | -0.13273 | -0.25502 | -0.089454 | 0.37548 | 0.25856 | 0.51358 | -0.11447 | -0.042591 | 121.5701 | 121.5091 | 121.5363 | 93.7776 | -121.6701 | 121.5796 | 121.5545 | 121.6264 | 106.4955 | -121.924
987.8906 | 121.7789 | -121.5775 | 0.11444 | 1.4211e-13 | -0.021327 | -0.00023069 | 0.060158 | -0.0059954 | 0.059114 | -0.22823 | -0.0033242 | -0.0036707 | 0.060424 | 0.022859 | 0.058627 | -120.8821 | -27.777 | -121.2092 | 0.006344 | -0.050009 | -0.032021 | -121.5648 | -121.1837 | -15.0453 | -121.2869 | 0.015831 | 0.009128 | 0.067272 | -121.8096 | 0.012634 | -0.1081 | 0.69533 | 0.36822 | 0.35559 | -0.16445 | -0.14646 | -0.23213 | -0.09861 | 0.39379 | 0.2906 | 0.52273 | -0.10531 | -0.047169 | 121.5838 | 121.5274 | 121.5454 | 93.8005 | -121.6793 | 121.5933 | 121.5866 | 121.6447 | 106.5322 | -121.924
989.5781 | 121.7514 | -121.5729 | 0.1236 | 1.4211e-13 | -0.02154 | -0.00023069 | 0.060158 | -0.0064228 | 0.058687 | -0.2206 | -0.0035378 | -0.0034569 | 0.060424 | 0.022859 | 0.05884 | -120.8867 | -27.7724 | -121.2184 | 0.010922 | -0.04543 | -0.022864 | -121.5602 | -121.1791 | -15.027 | -121.2914 | 0.015831 | -2.9e-05 | 0.067272 | -121.8233 | 0.012635 | -0.11267 | 0.68617 | 0.35449 | 0.34185 | -0.16903 | -0.14646 | -0.25045 | -0.10776 | 0.39379 | 0.28144 | 0.53189 | -0.12362 | -0.056324 | 121.5838 | 121.5274 | 121.55 | 93.8005 | -121.6838 | 121.5887 | 121.5728 | 121.6401 | 106.5459 | -121.9469
991.3125 | 121.8613 | -121.5591 | 0.07782 | 1.4211e-13 | -0.021113 | -1.7092e-05 | 0.059731 | -0.006209 | 0.0589 | -0.22823 | -0.0033242 | -0.0036707 | 0.06021 | 0.023072 | 0.058627 | -120.8959 | -27.7816 | -121.2138 | 0.010922 | -0.050009 | -0.027442 | -121.574 | -121.1928 | -15.0361 | -121.2914 | 0.015831 | -0.004608 | 0.058115 | -121.8233 | -0.014835 | -0.066898 | 0.66328 | 0.34534 | 0.36017 | -0.12783 | -0.10526 | -0.26418 | -0.061989 | 0.36632 | 0.26771 | 0.53189 | -0.082428 | -0.019705 | 121.5701 | 121.5091 | 121.5317 | 93.7776 | -121.6518 | 121.575 | 121.5545 | 121.6173 | 106.523 | -121.9011
993 | 121.7651 | -121.582 | 0.11444 | 1.4211e-13 | -0.021327 | 0.00019651 | 0.059945 | -0.0057818 | 0.059328 | -0.2206 | -0.0035378 | -0.0034569 | 0.060424 | 0.023072 | 0.05884 | -120.8775 | -27.8182 | -121.2184 | 0.010922 | -0.050009 | -0.022864 | -121.5694 | -121.1791 | -15.0407 | -121.3006 | 0.006674 | 0.004549 | 0.062694 | -121.8142 | 0.012632 | -0.10352 | 0.70448 | 0.36364 | 0.35101 | -0.16445 | -0.13731 | -0.23213 | -0.10777 | 0.40294 | 0.28144 | 0.51358 | -0.10989 | -0.051747 | 121.593 | 121.532 | 121.5592 | 93.7638 | -121.6838 | 121.5887 | 121.5866 | 121.6447 | 106.5413 | -121.9286
994.7344 | 121.8018 | -121.5775 | 0.091553 | 1.4211e-13 | -0.021754 | -1.7092e-05 | 0.060158 | -0.0053544 | 0.059114 | -0.22823 | -0.0033242 | -0.0030297 | 0.06021 | 0.023072 | 0.058627 | -120.8867 | -27.7953 | -121.2184 | 0.010922 | -0.04543 | -0.022864 | -121.5648 | -121.1837 | -15.0315 | -121.296 | 0.015831 | 0.004549 | 0.067272 | -121.8187 | 0.012634 | -0.080631 | 0.69075 | 0.35907 | 0.34643 | -0.13698 | -0.11442 | -0.24129 | -0.075722 | 0.39379 | 0.28145 | 0.52273 | -0.087004 | -0.024281 | 121.5884 | 121.532 | 121.5546 | 93.7822 | -121.6564 | 121.5933 | 121.582 | 121.6447 | 106.5459 | -121.9103
996.4688 | 121.8521 | -121.5683 | 0.073242 | 1.4211e-13 | -0.021754 | -0.00023069 | 0.060158 | -0.006209 | 0.059114 | -0.22823 | -0.0035378 | -0.0032433 | 0.060638 | 0.022645 | 0.05884 | -120.8867 | -27.809 | -121.2184 | 0.010922 | -0.050009 | -0.027442 | -121.5648 | -121.1882 | -15.0682 | -121.296 | 0.020409 | 0.004549 | 0.067272 | -121.8187 | 0.003478 | -0.06232 | 0.68159 | 0.34991 | 0.34643 | -0.12325 | -0.10068 | -0.25044 | -0.052833 | 0.38005 | 0.27229 | 0.52273 | -0.068693 | -0.00597 | 121.5792 | 121.5183 | 121.5409 | 93.7593 | -121.6381 | 121.5887 | 121.5728 | 121.6356 | 106.5001 | -121.892
998.2188 | 121.7422 | -121.5866 | 0.11444 | 1.4211e-13 | -0.02154 | -0.00044449 | 0.059945 | -0.006209 | 0.059114 | -0.2206 | -0.0035378 | -0.0034569 | 0.060424 | 0.023072 | 0.058627 | -120.8867 | -27.809 | -121.2184 | 0.010922 | -0.04543 | -0.022864 | -121.5694 | -121.1928 | -15.0544 | -121.296 | 0.015831 | 0.004549 | 0.067272 | -121.8279 | 0.01721 | -0.10352 | 0.6999 | 0.36822 | 0.35101 | -0.15987 | -0.13731 | -0.24129 | -0.09861 | 0.39378 | 0.2906 | 0.53189 | -0.10989 | -0.047169 | 121.5975 | 121.5412 | 121.5637 | 93.7776 | -121.6838 | 121.6024 | 121.5912 | 121.6539 | 106.5322 | -121.9423
999.9531 | 121.7239 | -121.5866 | 0.1236 | 1.4211e-13 | -0.02154 | 0.00019651 | 0.059945 | -0.0064228 | 0.059328 | -0.2206 | -0.0035378 | -0.0030297 | 0.060424 | 0.023072 | 0.058199 | -120.8821 | -27.7861 | -121.2184 | 0.010922 | -0.050009 | -0.022864 | -121.574 | -121.1928 | -15.0544 | -121.296 | 0.015831 | 0.004549 | 0.058115 | -121.8233 | 0.012631 | -0.11267 | 0.70448 | 0.36822 | 0.35559 | -0.17361 | -0.14646 | -0.23671 | -0.10776 | 0.39378 | 0.2906 | 0.52731 | -0.11905 | -0.065481 | 121.5975 | 121.5366 | 121.5637 | 93.8005 | -121.6976 | 121.6024 | 121.5912 | 121.6447 | 106.5322 | -121.9469
1001.625 | 121.8887 | -121.5546 | 0.082397 | 1.4211e-13 | -0.021327 | -1.7092e-05 | 0.059945 | -0.0059954 | 0.0589 | -0.22823 | -0.0031106 | -0.0036707 | 0.060424 | 0.023286 | 0.058413 | -120.8867 | -27.809 | -121.2275 | 0.010922 | -0.040851 | -0.027442 | -121.5648 | -121.1882 | -15.0453 | -121.3052 | 0.011252 | -2.9e-05 | 0.058115 | -121.8233 | -0.010255 | -0.071475 | 0.66786 | 0.32702 | 0.33728 | -0.12325 | -0.10984 | -0.26876 | -0.071145 | 0.36632 | 0.2494 | 0.51816 | -0.082426 | -0.024282 | 121.5655 | 121.5137 | 121.5271 | 93.7455 | -121.6472 | 121.5658 | 121.5545 | 121.6127 | 106.5093 | -121.9057
1003.375 | 121.7468 | -121.6003 | 0.10529 | 1.4211e-13 | -0.021327 | -0.00023069 | 0.059731 | -0.006209 | 0.059114 | -0.2206 | -0.0035378 | -0.0032433 | 0.060424 | 0.022859 | 0.05884 | -120.8913 | -27.7999 | -121.223 | 0.010922 | -0.04543 | -0.022864 | -121.574 | -121.1837 | -15.0819 | -121.3052 | 0.011252 | -2.9e-05 | 0.062694 | -121.8279 | 0.026364 | -0.094364 | 0.70906 | 0.37738 | 0.35101 | -0.15072 | -0.12815 | -0.22756 | -0.094034 | 0.41668 | 0.29518 | 0.52273 | -0.10532 | -0.042592 | 121.6113 | 121.5549 | 121.5775 | 93.8005 | -121.6793 | 121.6116 | 121.6003 | 121.663 | 106.5184 | -121.9332
1005.0469 | 121.7651 | -121.6049 | 0.11444 | 1.4211e-13 | -0.021754 | -0.00023069 | 0.059945 | -0.0057818 | 0.059114 | -0.2206 | -0.0035378 | -0.0034569 | 0.06021 | 0.022859 | 0.058413 | -120.8959 | -27.8136 | -121.2275 | 0.015501 | -0.04543 | -0.022864 | -121.574 | -121.1882 | -15.0682 | -121.3097 | 0.015831 | 0.004549 | 0.067272 | -121.8325 | 0.030941 | -0.09894 | 0.70906 | 0.37738 | 0.34643 | -0.15987 | -0.13731 | -0.22756 | -0.09861 | 0.41667 | 0.29517 | 0.52273 | -0.10989 | -0.047169 | 121.6204 | 121.5595 | 121.5821 | 93.7913 | -121.6884 | 121.6208 | 121.6095 | 121.6722 | 106.5367 | -121.9469
1006.7969 | 121.8887 | -121.5729 | 0.073242 | 1.4211e-13 | -0.021754 | 0.00019651 | 0.059731 | -0.0059954 | 0.059114 | -0.22823 | -0.0037514 | -0.0034569 | 0.06021 | 0.022859 | 0.058627 | -120.8867 | -27.8044 | -121.2321 | 0.006344 | -0.04543 | -0.018285 | -121.574 | -121.1882 | -15.0682 | -121.3052 | 0.011252 | 0.009128 | 0.058115 | -121.8279 | -0.001102 | -0.066898 | 0.68617 | 0.34075 | 0.34186 | -0.11867 | -0.091527 | -0.25502 | -0.06199 | 0.38463 | 0.26771 | 0.52273 | -0.064114 | -0.015127 | 121.5792 | 121.5274 | 121.5546 | 93.7684 | -121.6472 | 121.5841 | 121.582 | 121.631 | 106.5047 | -121.9011
1008.4688 | 121.7514 | -121.6003 | 0.12817 | 1.4211e-13 | -0.02154 | -1.7092e-05 | 0.059945 | -0.006209 | 0.059114 | -0.2206 | -0.0035378 | -0.0034569 | 0.06021 | 0.023072 | 0.058627 | -120.9004 | -27.8182 | -121.2275 | 0.010922 | -0.050009 | -0.018285 | -121.5786 | -121.1928 | -15.0773 | -121.3006 | 0.011252 | -2.9e-05 | 0.067272 | -121.8233 | 0.021785 | -0.11725 | 0.6999 | 0.3728 | 0.35101 | -0.17818 | -0.14646 | -0.22298 | -0.11692 | 0.40752 | 0.29975 | 0.52273 | -0.1282 | -0.060902 | 121.6113 | 121.5503 | 121.5821 | 93.7822 | -121.7067 | 121.6116 | 121.6003 | 121.6676 | 106.523 | -121.9515
1010.2031 | 121.8887 | -121.5546 | 0.082397 | 1.4211e-13 | -0.021754 | 0.00019651 | 0.059945 | -0.0059954 | 0.059114 | -0.24349 | -0.0035378 | -0.0032433 | 0.06021 | 0.022859 | 0.057986 | -120.8867 | -27.8273 | -121.2321 | 0.010922 | -0.050009 | -0.022864 | -121.574 | -121.1928 | -15.0636 | -121.3006 | 0.011252 | 0.013707 | 0.067272 | -121.8325 | -0.019413 | -0.071475 | 0.66786 | 0.32244 | 0.34186 | -0.13241 | -0.10526 | -0.27791 | -0.071145 | 0.36174 | 0.25398 | 0.53189 | -0.06869 | -0.015125 | 121.5655 | 121.5046 | 121.5317 | 93.7272 | -121.6564 | 121.5658 | 121.5683 | 121.6218 | 106.491 | -121.9149
1011.875 | 121.7926 | -121.6278 | 0.10529 | 1.4211e-13 | -0.02154 | -0.00023069 | 0.059945 | -0.006209 | 0.059114 | -0.22823 | -0.0037514 | -0.0036707 | 0.06021 | 0.023286 | 0.058627 | -120.8867 | -27.8548 | -121.223 | 0.006344 | -0.050009 | -0.022864 | -121.574 | -121.1928 | -15.0499 | -121.3052 | 0.011252 | 0.009128 | 0.067272 | -121.8233 | 0.05383 | -0.098942 | 0.7411 | 0.40484 | 0.35101 | -0.1553 | -0.12815 | -0.19551 | -0.094034 | 0.43498 | 0.32264 | 0.51816 | -0.096158 | -0.038014 | 121.6342 | 121.5778 | 121.6049 | 93.773 | -121.6793 | 121.6391 | 121.6369 | 121.6951 | 106.5779 | -121.9286
1013.6094 | 121.8979 | -121.5546 | 0.082397 | 1.4211e-13 | -0.02154 | -0.00023069 | 0.059945 | -0.0059954 | 0.059114 | -0.22823 | -0.0035378 | -0.0034569 | 0.060638 | 0.0235 | 0.058199 | -120.8867 | -27.8044 | -121.2275 | 0.010922 | -0.050009 | -0.022864 | -121.574 | -121.1974 | -15.0682 | -121.3097 | 0.011252 | 0.013707 | 0.062694 | -121.8371 | -0.019413 | -0.071475 | 0.66786 | 0.32702 | 0.34643 | -0.13241 | -0.10526 | -0.28249 | -0.071145 | 0.35716 | 0.24482 | 0.52731 | -0.06869 | -0.019703 | 121.5655 | 121.5046 | 121.5317 | 93.7501 | -121.6564 | 121.5658 | 121.5683 | 121.6173 | 106.4864 | -121.9195
1015.3438 | 121.8704 | -121.5775 | 0.07782 | 1.4211e-13 | -0.02154 | 0.00019651 | 0.059945 | -0.006209 | 0.059114 | -0.2206 | -0.0033242 | -0.0032433 | 0.06021 | 0.023286 | 0.058413 | -120.8913 | -27.7999 | -121.2275 | 0.010922 | -0.036272 | -0.013707 | -121.5694 | -121.1837 | -15.0865 | -121.3052 | 0.006674 | 0.009128 | 0.062694 | -121.8325 | 0.008055 | -0.066898 | 0.68617 | 0.34991 | 0.34186 | -0.11409 | -0.091527 | -0.25503 | -0.071146 | 0.39379 | 0.27229 | 0.52731 | -0.068692 | -0.015126 | 121.5884 | 121.5412 | 121.5637 | 93.7776 | -121.6472 | 121.5841 | 121.5866 | 121.6401 | 106.491 | -121.9103
1017.0156 | 121.8933 | -121.5546 | 0.086975 | 1.4211e-13 | -0.021968 | -0.00023069 | 0.059731 | -0.0059954 | 0.059114 | -0.22823 | -0.0033242 | -0.0036707 | 0.059997 | 0.023286 | 0.058413 | -120.8959 | -27.8136 | -121.2321 | 0.015501 | -0.04543 | -0.018285 | -121.574 | -121.1837 | -15.0682 | -121.3006 | 0.011252 | 0.013707 | 0.062694 | -121.8279 | -0.019413 | -0.071474 | 0.6587 | 0.32244 | 0.34186 | -0.1324 | -0.10526 | -0.27334 | -0.075723 | 0.3709 | 0.25398 | 0.52731 | -0.073268 | -0.024281 | 121.5701 | 121.5091 | 121.5363 | 93.741 | -121.661 | 121.5658 | 121.5683 | 121.6173 | 106.4864 | -121.9149
1018.75 | 121.8796 | -121.5591 | 0.082397 | 1.4211e-13 | -0.021754 | 0.00019651 | 0.059945 | -0.0059954 | 0.059114 | -0.2206 | -0.0037514 | -0.0034569 | 0.060424 | 0.0235 | 0.058199 | -120.8913 | -27.809 | -121.2321 | 0.010922 | -0.050009 | -0.018285 | -121.5786 | -121.1974 | -15.0407 | -121.3052 | 0.020409 | 0.009128 | 0.067272 | -121.8279 | -0.019414 | -0.071475 | 0.66786 | 0.32702 | 0.34643 | -0.13241 | -0.10068 | -0.26876 | -0.061988 | 0.36174 | 0.25398 | 0.52273 | -0.073269 | -0.015125 | 121.5701 | 121.5091 | 121.5409 | 93.7501 | -121.661 | 121.5796 | 121.5683 | 121.6264 | 106.5184 | -121.9103
1020.4844 | 121.8063 | -121.582 | 0.11444 | 1.4211e-13 | -0.021968 | -0.00023069 | 0.059945 | -0.006209 | 0.059114 | -0.2206 | -0.0033242 | -0.0036707 | 0.060424 | 0.023072 | 0.058199 | -120.8913 | -27.8273 | -121.2321 | 0.006344 | -0.050009 | -0.018285 | -121.5786 | -121.1882 | -15.0315 | -121.3006 | 0.015831 | 0.009128 | 0.071851 | -121.8371 | 0.003474 | -0.1081 | 0.69075 | 0.34991 | 0.34643 | -0.16445 | -0.13273 | -0.25503 | -0.09861 | 0.39379 | 0.28144 | 0.53647 | -0.10531 | -0.04259 | 121.5884 | 121.532 | 121.5637 | 93.7547 | -121.693 | 121.5979 | 121.5912 | 121.6539 | 106.5505 | -121.9515
1022.1719 | 121.8475 | -121.582 | 0.091553 | 1.4211e-13 | -0.021754 | -1.7092e-05 | 0.059731 | -0.006209 | 0.059328 | -0.2206 | -0.0033242 | -0.0034569 | 0.060424 | 0.023286 | 0.058199 | -120.8959 | -27.809 | -121.2367 | 0.010922 | -0.04543 | -0.018285 | -121.574 | -121.1974 | -15.0407 | -121.3052 | 0.002095 | 0.009128 | 0.058115 | -121.8325 | 0.008053 | -0.080631 | 0.68617 | 0.34533 | 0.33728 | -0.13698 | -0.10984 | -0.25045 | -0.089458 | 0.38463 | 0.27686 | 0.52731 | -0.082425 | -0.033438 | 121.593 | 121.5366 | 121.5637 | 93.773 | -121.6655 | 121.5841 | 121.5912 | 121.6401 | 106.5413 | -121.924
1023.9062 | 121.875 | -121.5775 | 0.086975 | 1.4211e-13 | -0.022181 | -1.7092e-05 | 0.059945 | -0.0057818 | 0.059114 | -0.21297 | -0.0035378 | -0.0034569 | 0.059997 | 0.023713 | 0.058413 | -120.8959 | -27.8136 | -121.2321 | 0.010922 | -0.036272 | -0.022864 | -121.5831 | -121.202 | -15.0499 | -121.3052 | 0.011252 | 0.018285 | 0.067272 | -121.8325 | -0.005682 | -0.076053 | 0.68159 | 0.34533 | 0.35101 | -0.12325 | -0.10984 | -0.25503 | -0.075723 | 0.37547 | 0.27229 | 0.52731 | -0.06869 | -0.019703 | 121.5884 | 121.5412 | 121.5546 | 93.7639 | -121.6701 | 121.5887 | 121.5957 | 121.6447 | 106.5276 | -121.9195
1025.5781 | 121.9025 | -121.5866 | 0.07782 | 1.4211e-13 | -0.021968 | -1.7092e-05 | 0.059945 | -0.0059954 | 0.0589 | -0.22823 | -0.0033242 | -0.0036707 | 0.06021 | 0.023286 | 0.058199 | -120.8959 | -27.8182 | -121.2321 | 0.006344 | -0.040851 | -0.013707 | -121.5786 | -121.1974 | -15.0361 | -121.3052 | 0.015831 | 0.009128 | 0.067272 | -121.8371 | 0.008052 | -0.071476 | 0.69075 | 0.35449 | 0.34643 | -0.11867 | -0.091527 | -0.25045 | -0.061989 | 0.38921 | 0.28144 | 0.53189 | -0.068692 | -0.010548 | 121.593 | 121.5458 | 121.5729 | 93.7684 | -121.6564 | 121.6024 | 121.5957 | 121.6539 | 106.5505 | -121.9149
1027.3125 | 121.9025 | -121.5591 | 0.068665 | 1.4211e-13 | -0.021968 | 0.00041031 | 0.059945 | -0.0059954 | 0.058687 | -0.22823 | -0.0035378 | -0.0034569 | 0.060424 | 0.023286 | 0.058199 | -120.8959 | -27.8136 | -121.2367 | 0.015501 | -0.04543 | -0.018285 | -121.5831 | -121.1974 | -15.0224 | -121.3006 | 0.015831 | 0.013707 | 0.067272 | -121.8371 | -0.023993 | -0.053164 | 0.66328 | 0.32244 | 0.34644 | -0.1141 | -0.08695 | -0.27791 | -0.052834 | 0.36174 | 0.25856 | 0.53647 | -0.054958 | -0.001393 | 121.5746 | 121.5137 | 121.5409 | 93.7455 | -121.6518 | 121.575 | 121.5729 | 121.6264 | 106.5368 | -121.9057
1029.0469 | 121.843 | -121.5775 | 0.073242 | 1.4211e-13 | -0.021754 | -0.00023069 | 0.059945 | -0.006209 | 0.0589 | -0.2206 | -0.0035378 | -0.0036707 | 0.060424 | 0.023286 | 0.058413 | -120.8959 | -27.7953 | -121.2275 | 0.006344 | -0.04543 | -0.022864 | -121.5877 | -121.202 | -15.0361 | -121.3097 | 0.020409 | 0.009128 | 0.067272 | -121.8371 | -0.010261 | -0.066898 | 0.68159 | 0.34991 | 0.36017 | -0.11867 | -0.096106 | -0.2596 | -0.052833 | 0.37547 | 0.26771 | 0.52731 | -0.064114 | -0.00597 | 121.5838 | 121.532 | 121.5546 | 93.7822 | -121.661 | 121.5979 | 121.5866 | 121.6447 | 106.5413 | -121.9103
1030.7188 | 121.8842 | -121.582 | 0.07782 | 1.4211e-13 | -0.02154 | -0.00023069 | 0.059945 | -0.0059954 | 0.059114 | -0.23586 | -0.0035378 | -0.0034569 | 0.06021 | 0.023286 | 0.058199 | -120.8913 | -27.8411 | -121.2367 | 0.001765 | -0.04543 | -0.027442 | -121.5786 | -121.1974 | -15.0499 | -121.3052 | 0.020409 | 0.004549 | 0.071851 | -121.8371 | 0.003474 | -0.076055 | 0.69075 | 0.34533 | 0.34186 | -0.12325 | -0.10526 | -0.25503 | -0.057411 | 0.38463 | 0.27686 | 0.53189 | -0.073271 | -0.005969 | 121.5838 | 121.5366 | 121.5546 | 93.741 | -121.6564 | 121.6024 | 121.5866 | 121.6539 | 106.5322 | -121.9149
1032.4531 | 121.8613 | -121.5729 | 0.07782 | 1.4211e-13 | -0.021968 | -1.7092e-05 | 0.059731 | -0.0059954 | 0.059328 | -0.22823 | -0.0035378 | -0.0032433 | 0.06021 | 0.023286 | 0.058413 | -120.8913 | -27.8228 | -121.2321 | 0.010922 | -0.04543 | -0.022864 | -121.5831 | -121.202 | -15.0544 | -121.3052 | 0.015831 | 0.013707 | 0.062694 | -121.8371 | -0.01026 | -0.066898 | 0.68159 | 0.34075 | 0.35101 | -0.12325 | -0.10068 | -0.26418 | -0.061989 | 0.37089 | 0.26771 | 0.53189 | -0.064113 | -0.015126 | 121.5838 | 121.5274 | 121.55 | 93.7501 | -121.661 | 121.5887 | 121.5866 | 121.6356 | 106.5184 | -121.9149
1034.125 | 121.8018 | -121.5912 | 0.10071 | 1.4211e-13 | -0.021754 | -0.00023069 | 0.059945 | -0.006209 | 0.0589 | -0.2206 | -0.0037514 | -0.0034569 | 0.060424 | 0.0235 | 0.058199 | -120.8959 | -27.8182 | -121.2321 | 0.010922 | -0.04543 | -0.022864 | -121.5923 | -121.1974 | -15.059 | -121.3097 | 0.015831 | 0.009128 | 0.067272 | -121.8279 | -0.001107 | -0.089786 | 0.69533 | 0.35907 | 0.36017 | -0.14614 | -0.12357 | -0.23671 | -0.084877 | 0.39379 | 0.28144 | 0.51815 | -0.09158 | -0.033436 | 121.6021 | 121.5458 | 121.5683 | 93.773 | -121.693 | 121.607 | 121.6003 | 121.6585 | 106.5322 | -121.9286
1035.8438 | 121.8933 | -121.5454 | 0.068665 | 1.4211e-13 | -0.022181 | -0.00023069 | 0.059945 | -0.0059954 | 0.058687 | -0.2206 | -0.0035378 | -0.0036707 | 0.060424 | 0.023713 | 0.058199 | -120.8913 | -27.8182 | -121.2413 | 0.010922 | -0.040851 | -0.018285 | -121.5923 | -121.1974 | -15.0728 | -121.3006 | 0.015831 | 0.009128 | 0.067272 | -121.8279 | -0.046884 | -0.057743 | 0.65413 | 0.30413 | 0.35102 | -0.10952 | -0.08695 | -0.28249 | -0.052834 | 0.34801 | 0.24482 | 0.52731 | -0.059537 | -0.001393 | 121.5563 | 121.5046 | 121.5271 | 93.7272 | -121.661 | 121.5612 | 121.5545 | 121.6127 | 106.4727 | -121.8966
1037.5156 | 121.8887 | -121.5637 | 0.082397 | 1.4211e-13 | -0.021754 | -0.00023069 | 0.060158 | -0.006209 | 0.0589 | -0.21297 | -0.0037514 | -0.0038843 | 0.059997 | 0.0235 | 0.058199 | -120.8959 | -27.8319 | -121.2367 | 0.015501 | -0.040851 | -0.018285 | -121.5786 | -121.1974 | -15.0682 | -121.3052 | 0.015831 | 0.013707 | 0.067272 | -121.8462 | -0.014836 | -0.066896 | 0.66786 | 0.32702 | 0.34186 | -0.12325 | -0.10068 | -0.28249 | -0.066566 | 0.36632 | 0.25855 | 0.54105 | -0.06869 | -0.015125 | 121.5792 | 121.5229 | 121.5454 | 93.7318 | -121.661 | 121.5796 | 121.5774 | 121.631 | 106.4955 | -121.9286
1039.25 | 121.8109 | -121.6141 | 0.10529 | 1.4211e-13 | -0.022609 | -0.00023069 | 0.060158 | -0.0064228 | 0.0589 | -0.22823 | -0.0031106 | -0.0030297 | 0.059997 | 0.023286 | 0.058199 | -120.8913 | -27.8548 | -121.2367 | 0.015501 | -0.054588 | -0.022864 | -121.5831 | -121.2066 | -15.1185 | -121.3097 | 0.011252 | 0.009128 | 0.067272 | -121.8416 | 0.030939 | -0.089785 | 0.72279 | 0.37738 | 0.34644 | -0.15987 | -0.12815 | -0.22756 | -0.094034 | 0.40752 | 0.30433 | 0.53189 | -0.096158 | -0.038014 | 121.6296 | 121.5595 | 121.5912 | 93.7593 | -121.6884 | 121.6253 | 121.6232 | 121.6813 | 106.4955 | -121.9469
1040.9844 | 121.8658 | -121.5591 | 0.07782 | 1.4211e-13 | -0.022609 | -0.00065809 | 0.059945 | -0.006209 | 0.0589 | -0.22823 | -0.0035378 | -0.0034569 | 0.06021 | 0.023927 | 0.058199 | -120.905 | -27.8457 | -121.2459 | 0.015501 | -0.040851 | -0.018285 | -121.5831 | -121.1974 | -15.114 | -121.3143 | 0.015831 | 0.018285 | 0.067272 | -121.8371 | -0.023993 | -0.062319 | 0.65412 | 0.31329 | 0.33728 | -0.11867 | -0.096105 | -0.27791 | -0.061989 | 0.36174 | 0.24482 | 0.52273 | -0.059535 | -0.010548 | 121.5746 | 121.5183 | 121.5409 | 93.7135 | -121.661 | 121.575 | 121.5774 | 121.6264 | 106.4452 | -121.9149
1042.7344 | 121.8658 | -121.582 | 0.09613 | 1.4211e-13 | -0.022822 | -1.7092e-05 | 0.059945 | -0.0064228 | 0.0589 | -0.22823 | -0.0031106 | -0.0032433 | 0.060424 | 0.023713 | 0.057986 | -120.905 | -27.864 | -121.2413 | 0.015501 | -0.04543 | -0.013707 | -121.5923 | -121.202 | -15.1002 | -121.3235 | 0.015831 | 0.009128 | 0.062694 | -121.8371 | -0.010263 | -0.080629 | 0.67701 | 0.34075 | 0.35102 | -0.14156 | -0.10984 | -0.25503 | -0.080299 | 0.38005 | 0.25855 | 0.51358 | -0.087002 | -0.033436 | 121.5975 | 121.5366 | 121.5683 | 93.7181 | -121.6884 | 121.5979 | 121.5912 | 121.6447 | 106.4818 | -121.9332
1044.4062 | 121.8842 | -121.5775 | 0.07782 | 1.4211e-13 | -0.022181 | -1.7092e-05 | 0.059945 | -0.0059954 | 0.059114 | -0.22823 | -0.0033242 | -0.0034569 | 0.059997 | 0.023286 | 0.057986 | -120.9004 | -27.8914 | -121.2459 | 0.015501 | -0.050009 | -0.022864 | -121.5877 | -121.1928 | -15.1185 | -121.3189 | 0.015831 | 0.009128 | 0.067272 | -121.8462 | -0.010261 | -0.062319 | 0.67701 | 0.3316 | 0.34186 | -0.12783 | -0.10068 | -0.26876 | -0.061989 | 0.38463 | 0.25855 | 0.52731 | -0.068692 | -0.010548 | 121.593 | 121.5274 | 121.5546 | 93.686 | -121.6655 | 121.5933 | 121.5866 | 121.6447 | 106.4589 | -121.924
1046.1406 | 121.907 | -121.5546 | 0.082397 | 1.4211e-13 | -0.022181 | -0.00023069 | 0.059945 | -0.006209 | 0.059114 | -0.22823 | -0.0033242 | -0.0036707 | 0.060424 | 0.023713 | 0.058199 | -120.8959 | -27.8777 | -121.2367 | 0.006344 | -0.04543 | -0.032021 | -121.5831 | -121.2066 | -15.1002 | -121.3097 | 0.020409 | 0.018285 | 0.071851 | -121.8416 | -0.028571 | -0.076053 | 0.6587 | 0.31786 | 0.34644 | -0.12783 | -0.11442 | -0.28707 | -0.061988 | 0.34801 | 0.24482 | 0.53189 | -0.064112 | -0.010546 | 121.5609 | 121.5091 | 121.5225 | 93.6769 | -121.6655 | 121.575 | 121.5729 | 121.6264 | 106.4543 | -121.924
1047.8906 | 121.7697 | -121.6049 | 0.09613 | 1.4211e-13 | -0.022181 | -1.7092e-05 | 0.060158 | -0.006209 | 0.0589 | -0.22823 | -0.0035378 | -0.0030297 | 0.060424 | 0.0235 | 0.058413 | -120.8959 | -27.8869 | -121.2413 | 0.006344 | -0.04543 | -0.022864 | -121.5923 | -121.202 | -15.1277 | -121.3097 | 0.015831 | 0.013707 | 0.067272 | -121.8462 | 0.012625 | -0.089786 | 0.70906 | 0.36364 | 0.35102 | -0.14156 | -0.11899 | -0.2413 | -0.080299 | 0.40294 | 0.29517 | 0.53647 | -0.082423 | -0.028858 | 121.6113 | 121.5595 | 121.5821 | 93.7181 | -121.6884 | 121.6208 | 121.6186 | 121.6722 | 106.4772 | -121.9423
1049.625 | 121.8063 | -121.5912 | 0.10071 | 1.4211e-13 | -0.022395 | -0.00023069 | 0.059731 | -0.0064228 | 0.0589 | -0.23586 | -0.0033242 | -0.0032433 | 0.06021 | 0.0235 | 0.058199 | -120.9096 | -27.8869 | -121.2413 | 0.006344 | -0.04543 | -0.018285 | -121.5877 | -121.202 | -15.1643 | -121.3189 | 0.015831 | 0.009128 | 0.062694 | -121.8554 | 0.003472 | -0.094364 | 0.68159 | 0.34991 | 0.34644 | -0.14614 | -0.11899 | -0.26419 | -0.084877 | 0.38921 | 0.27228 | 0.53647 | -0.09158 | -0.038014 | 121.5975 | 121.5458 | 121.5729 | 93.7043 | -121.6884 | 121.607 | 121.6003 | 121.6539 | 106.4269 | -121.9561
1051.2969 | 121.8155 | -121.6049 | 0.11902 | 1.4211e-13 | -0.022181 | -0.00023069 | 0.059731 | -0.006209 | 0.059114 | -0.2206 | -0.0035378 | -0.0034569 | 0.060424 | 0.0235 | 0.058199 | -120.8913 | -27.864 | -121.2459 | 0.015501 | -0.04543 | -0.022864 | -121.5923 | -121.2111 | -15.1506 | -121.3097 | 0.015831 | 0.013707 | 0.062694 | -121.8371 | 0.012625 | -0.10352 | 0.71363 | 0.35906 | 0.34644 | -0.16445 | -0.14188 | -0.23214 | -0.10319 | 0.39378 | 0.29517 | 0.52731 | -0.10531 | -0.056325 | 121.6204 | 121.5595 | 121.5821 | 93.741 | -121.7113 | 121.6208 | 121.6186 | 121.6676 | 106.4543 | -121.9561
1053.0312 | 121.788 | -121.6049 | 0.11444 | 1.4211e-13 | -0.022609 | -0.00044449 | 0.060158 | -0.0064228 | 0.0589 | -0.22823 | -0.0031106 | -0.0036707 | 0.059997 | 0.023713 | 0.057986 | -120.8959 | -27.8685 | -121.2504 | 0.010922 | -0.036272 | -0.022864 | -121.5923 | -121.1974 | -15.1689 | -121.3189 | 0.011252 | 0.013707 | 0.062694 | -121.8416 | 0.012625 | -0.10352 | 0.70906 | 0.35448 | 0.34186 | -0.15071 | -0.13731 | -0.23672 | -0.10319 | 0.40752 | 0.28602 | 0.52273 | -0.10073 | -0.051747 | 121.6158 | 121.5686 | 121.5821 | 93.7364 | -121.7067 | 121.6162 | 121.6186 | 121.6676 | 106.436 | -121.9561
1054.7812 | 121.8155 | -121.6095 | 0.082397 | 1.4211e-13 | -0.022395 | -0.00023069 | 0.059945 | -0.0059954 | 0.0589 | -0.22823 | -0.0037514 | -0.0032433 | 0.06021 | 0.023713 | 0.058199 | -120.8913 | -27.8777 | -121.255 | 0.010922 | -0.040851 | -0.018285 | -121.5877 | -121.2066 | -15.1735 | -121.3052 | 0.011252 | 0.013707 | 0.062694 | -121.8462 | 0.021782 | -0.071475 | 0.71821 | 0.35448 | 0.3327 | -0.12325 | -0.10068 | -0.23672 | -0.071145 | 0.40294 | 0.30433 | 0.54105 | -0.06869 | -0.019703 | 121.6204 | 121.5686 | 121.5912 | 93.7318 | -121.6701 | 121.6207 | 121.6232 | 121.6722 | 106.436 | -121.9286
1056.4531 | 121.7606 | -121.6141 | 0.10529 | 1.4211e-13 | -0.022609 | -0.00023069 | 0.060158 | -0.006209 | 0.058687 | -0.22823 | -0.0031106 | -0.0034569 | 0.060424 | 0.023286 | 0.057986 | -120.9004 | -27.9006 | -121.2504 | 0.010922 | -0.04543 | -0.018285 | -121.5969 | -121.2157 | -15.1826 | -121.3143 | 0.011252 | 0.013707 | 0.062694 | -121.8462 | 0.017203 | -0.094364 | 0.71363 | 0.36364 | 0.34644 | -0.15072 | -0.12357 | -0.23214 | -0.094034 | 0.39836 | 0.29975 | 0.53189 | -0.091579 | -0.042592 | 121.625 | 121.5686 | 121.5958 | 93.7135 | -121.7022 | 121.6253 | 121.6278 | 121.6768 | 106.4314 | -121.9515
1058.2031 | 121.8246 | -121.5912 | 0.11444 | 1.4211e-13 | -0.022181 | -0.00023069 | 0.059517 | -0.0064228 | 0.058687 | -0.23586 | -0.0035378 | -0.0032433 | 0.06021 | 0.023927 | 0.058199 | -120.8959 | -27.8823 | -121.2459 | 0.015501 | -0.040851 | -0.013707 | -121.5969 | -121.2066 | -15.1872 | -121.3143 | 0.020409 | 0.013707 | 0.071851 | -121.8554 | -0.005685 | -0.09894 | 0.69533 | 0.34533 | 0.35102 | -0.15529 | -0.12815 | -0.26419 | -0.094032 | 0.38463 | 0.27686 | 0.54105 | -0.10073 | -0.04259 | 121.6067 | 121.5503 | 121.5775 | 93.7089 | -121.7113 | 121.6116 | 121.6049 | 121.663 | 106.404 | -121.9698
1059.9375 | 121.8246 | -121.5912 | 0.086975 | 1.4211e-13 | -0.022609 | 0.00019651 | 0.060158 | -0.006209 | 0.0589 | -0.22823 | -0.003965 | -0.0034569 | 0.060424 | 0.023286 | 0.057772 | -120.9096 | -27.8869 | -121.2459 | 0.006344 | -0.04543 | -0.018285 | -121.5969 | -121.2066 | -15.2284 | -121.3143 | 0.011252 | 0.018285 | 0.062694 | -121.8508 | -0.005685 | -0.080631 | 0.68159 | 0.34533 | 0.35102 | -0.1324 | -0.10526 | -0.25961 | -0.075723 | 0.38463 | 0.27686 | 0.53647 | -0.06869 | -0.024281 | 121.5975 | 121.5458 | 121.5729 | 93.7043 | -121.6838 | 121.6024 | 121.6095 | 121.6539 | 106.3628 | -121.9378
1061.6719 | 121.7743 | -121.6324 | 0.11444 | 1.4211e-13 | -0.022609 | -0.00023069 | 0.060158 | -0.006209 | 0.059114 | -0.22823 | -0.0033242 | -0.0032433 | 0.060424 | 0.023713 | 0.057772 | -120.9096 | -27.8869 | -121.2504 | 0.010922 | -0.036272 | -0.018285 | -121.5877 | -121.2111 | -15.233 | -121.3189 | 0.015831 | 0.009128 | 0.062694 | -121.8508 | 0.04467 | -0.10352 | 0.72279 | 0.38195 | 0.33728 | -0.15071 | -0.13273 | -0.21841 | -0.09861 | 0.42125 | 0.31348 | 0.53189 | -0.10531 | -0.051747 | 121.6433 | 121.5961 | 121.6141 | 93.7455 | -121.7022 | 121.6482 | 121.6415 | 121.6951 | 106.3994 | -121.9652
1063.3438 | 121.8933 | -121.5683 | 0.068665 | 1.4211e-13 | -0.022395 | -0.00023069 | 0.059731 | -0.0066364 | 0.058259 | -0.22823 | -0.003965 | -0.0036707 | 0.06021 | 0.023927 | 0.058199 | -120.905 | -27.9372 | -121.2504 | 0.006344 | -0.040851 | -0.018285 | -121.5969 | -121.2066 | -15.2467 | -121.3143 | 0.011252 | 0.013707 | 0.071851 | -121.8554 | -0.028574 | -0.062321 | 0.66328 | 0.31786 | 0.34644 | -0.10952 | -0.08695 | -0.28708 | -0.057413 | 0.36174 | 0.25397 | 0.54105 | -0.054958 | 0.003186 | 121.5746 | 121.5274 | 121.55 | 93.6311 | -121.6655 | 121.5795 | 121.582 | 121.6401 | 106.3216 | -121.924
1065.0781 | 121.8979 | -121.5683 | 0.082397 | 1.4211e-13 | -0.023036 | -1.7092e-05 | 0.059517 | -0.0064228 | 0.058687 | -0.22823 | -0.0035378 | -0.0032433 | 0.06021 | 0.023713 | 0.058199 | -120.9004 | -27.9281 | -121.2596 | 0.015501 | -0.050009 | -0.022864 | -121.606 | -121.2066 | -15.2605 | -121.3281 | 0.024988 | -2.9e-05 | 0.062694 | -121.86 | -0.037732 | -0.066896 | 0.66786 | 0.30871 | 0.34644 | -0.13241 | -0.10526 | -0.29165 | -0.057409 | 0.36174 | 0.24024 | 0.53189 | -0.082426 | -0.019703 | 121.5838 | 121.5183 | 121.5454 | 93.6402 | -121.6884 | 121.5933 | 121.5683 | 121.631 | 106.3078 | -121.9423
1066.8125 | 121.7972 | -121.6278 | 0.12817 | 1.4211e-13 | -0.022395 | -0.00023069 | 0.059945 | -0.0064228 | 0.0589 | -0.22823 | -0.0037514 | -0.0036707 | 0.059997 | 0.023927 | 0.058199 | -120.9004 | -27.9098 | -121.255 | 0.010922 | -0.050009 | -0.018285 | -121.5969 | -121.2111 | -15.2742 | -121.3097 | 0.006674 | 0.004549 | 0.062694 | -121.8554 | 0.030936 | -0.11725 | 0.72737 | 0.37279 | 0.34186 | -0.17818 | -0.14646 | -0.22756 | -0.1215 | 0.41667 | 0.31806 | 0.54563 | -0.12363 | -0.06548 | 121.6387 | 121.5778 | 121.6095 | 93.7181 | -121.725 | 121.6345 | 121.6324 | 121.6905 | 106.3536 | -121.9835
1068.4844 | 121.7514 | -121.6049 | 0.10986 | 1.4211e-13 | -0.022609 | -0.00023069 | 0.059945 | -0.0059954 | 0.0589 | -0.21297 | -0.0035378 | -0.0034569 | 0.06021 | 0.023927 | 0.058199 | -120.9004 | -27.9281 | -121.255 | 0.015501 | -0.04543 | -0.018285 | -121.5969 | -121.2157 | -15.2559 | -121.3189 | 0.011252 | 0.004549 | 0.071851 | -121.86 | 0.008047 | -0.094362 | 0.70448 | 0.34991 | 0.34186 | -0.15529 | -0.12815 | -0.25503 | -0.098611 | 0.3892 | 0.28602 | 0.54105 | -0.10531 | -0.038012 | 121.6204 | 121.5595 | 121.5866 | 93.6769 | -121.7067 | 121.6162 | 121.6095 | 121.6768 | 106.349 | -121.9698
1070.2188 | 121.9025 | -121.5775 | 0.064087 | 1.4211e-13 | -0.022609 | -0.00023069 | 0.059945 | -0.0064228 | 0.058687 | -0.22823 | -0.0037514 | -0.0034569 | 0.06021 | 0.023927 | 0.057558 | -120.9004 | -27.9143 | -121.255 | 0.010922 | -0.040851 | -0.022864 | -121.5969 | -121.2111 | -15.2605 | -121.3189 | 0.015831 | 0.004549 | 0.071851 | -121.8508 | -0.019418 | -0.053165 | 0.67701 | 0.32244 | 0.34186 | -0.10494 | -0.086951 | -0.27334 | -0.048256 | 0.36632 | 0.25855 | 0.53189 | -0.059538 | 0.007764 | 121.5884 | 121.5366 | 121.5546 | 93.6631 | -121.661 | 121.5933 | 121.582 | 121.6493 | 106.317 | -121.9149
1071.9531 | 121.8933 | -121.5958 | 0.082397 | 1.4211e-13 | -0.022822 | -0.00023069 | 0.059945 | -0.0059954 | 0.0589 | -0.24349 | -0.0035378 | -0.0034569 | 0.059997 | 0.024141 | 0.057986 | -120.905 | -27.9372 | -121.2504 | 0.015501 | -0.04543 | -0.013707 | -121.5969 | -121.2066 | -15.2834 | -121.3235 | 0.015831 | -2.9e-05 | 0.067272 | -121.8554 | -0.001108 | -0.066896 | 0.69075 | 0.34533 | 0.34644 | -0.12783 | -0.096104 | -0.25961 | -0.066566 | 0.3892 | 0.27228 | 0.53189 | -0.082426 | -0.015125 | 121.6113 | 121.5503 | 121.5821 | 93.6585 | -121.6793 | 121.6116 | 121.5957 | 121.663 | 106.3124 | -121.9378
1073.6875 | 121.9208 | -121.5683 | 0.091553 | 1.4211e-13 | -0.022822 | -1.7092e-05 | 0.059945 | -0.006209 | 0.0589 | -0.23586 | -0.0035378 | -0.0034569 | 0.06021 | 0.024141 | 0.057772 | -120.9096 | -27.9235 | -121.255 | 0.010922 | -0.04543 | -0.018285 | -121.5969 | -121.2157 | -15.3017 | -121.3189 | 0.020409 | 0.004549 | 0.067272 | -121.8554 | -0.028574 | -0.080631 | 0.6587 | 0.31328 | 0.34186 | -0.13698 | -0.10984 | -0.28708 | -0.071144 | 0.35258 | 0.24939 | 0.53647 | -0.087004 | -0.024281 | 121.5792 | 121.5229 | 121.55 | 93.6448 | -121.6884 | 121.5887 | 121.5728 | 121.6356 | 106.2666 | -121.9469
1075.3594 | 121.8704 | -121.5775 | 0.10529 | 1.4211e-13 | -0.022822 | -1.7092e-05 | 0.059731 | -0.006209 | 0.058687 | -0.23586 | -0.0035378 | -0.0032433 | 0.059783 | 0.023927 | 0.058199 | -120.9096 | -27.9052 | -121.2642 | 0.006344 | -0.036272 | -0.018285 | -121.6015 | -121.2157 | -15.2834 | -121.3189 | 0.015831 | 0.009128 | 0.067272 | -121.8554 | -0.023997 | -0.098942 | 0.66786 | 0.31329 | 0.33728 | -0.14156 | -0.12357 | -0.27792 | -0.089455 | 0.36174 | 0.25855 | 0.53647 | -0.096158 | -0.038014 | 121.5838 | 121.5412 | 121.5592 | 93.6723 | -121.7067 | 121.5933 | 121.5866 | 121.6447 | 106.2941 | -121.9607
1077.0938 | 121.8613 | -121.6049 | 0.09613 | 1.4211e-13 | -0.022822 | -1.7092e-05 | 0.059731 | -0.006209 | 0.058473 | -0.23586 | -0.0035378 | -0.0034569 | 0.060638 | 0.024354 | 0.057986 | -120.905 | -27.9143 | -121.2596 | 0.006344 | -0.040851 | -0.018285 | -121.6015 | -121.2203 | -15.3017 | -121.3281 | 0.020409 | 0.013707 | 0.062694 | -121.8554 | 0.003468 | -0.089786 | 0.6999 | 0.34533 | 0.34186 | -0.13698 | -0.11441 | -0.25045 | -0.075721 | 0.38462 | 0.27686 | 0.52731 | -0.082423 | -0.033436 | 121.6113 | 121.5641 | 121.5866 | 93.6906 | -121.6976 | 121.6253 | 121.6186 | 121.6676 | 106.3032 | -121.9515
1078.7656 | 121.7834 | -121.6324 | 0.10071 | 1.4211e-13 | -0.022822 | -0.00023069 | 0.059945 | -0.006209 | 0.058473 | -0.2206 | -0.0033242 | -0.0034569 | 0.060424 | 0.024141 | 0.058199 | -120.9096 | -27.9235 | -121.2596 | 0.015501 | -0.040851 | -0.013707 | -121.6015 | -121.2157 | -15.3154 | -121.3189 | 0.015831 | 0.009128 | 0.067272 | -121.8554 | 0.030934 | -0.085207 | 0.72279 | 0.37279 | 0.34186 | -0.14156 | -0.11442 | -0.22299 | -0.084877 | 0.41667 | 0.31348 | 0.53647 | -0.09158 | -0.033436 | 121.6479 | 121.5915 | 121.6187 | 93.7089 | -121.7022 | 121.6482 | 121.6415 | 121.6997 | 106.317 | -121.9561
1080.5 | 121.875 | -121.6003 | 0.09613 | 1.4211e-13 | -0.023036 | -0.00023069 | 0.059945 | -0.0059954 | 0.0589 | -0.2206 | -0.0035378 | -0.0034569 | 0.060424 | 0.023927 | 0.058199 | -120.9096 | -27.9006 | -121.2504 | 0.006344 | -0.036272 | -0.018285 | -121.6015 | -121.2157 | -15.3017 | -121.3189 | 0.006674 | 0.004549 | 0.071851 | -121.8554 | -0.001109 | -0.089786 | 0.69074 | 0.34991 | 0.35102 | -0.1324 | -0.11441 | -0.25503 | -0.089456 | 0.38462 | 0.28144 | 0.53647 | -0.091581 | -0.024279 | 121.6067 | 121.5641 | 121.5821 | 93.6997 | -121.6976 | 121.607 | 121.6049 | 121.6722 | 106.2987 | -121.9515
1082.25 | 121.8658 | -121.582 | 0.086975 | 1.4211e-13 | -0.023036 | -1.7092e-05 | 0.059731 | -0.006209 | 0.0589 | -0.23586 | -0.0033242 | -0.0034569 | 0.059997 | 0.024354 | 0.058199 | -120.905 | -27.8869 | -121.2596 | 0.015501 | -0.04543 | -0.013707 | -121.5969 | -121.2203 | -15.32 | -121.3189 | 0.015831 | 0.009128 | 0.067272 | -121.8554 | -0.014841 | -0.071474 | 0.67701 | 0.32244 | 0.33728 | -0.1324 | -0.10068 | -0.27334 | -0.071144 | 0.36173 | 0.26313 | 0.53647 | -0.077847 | -0.019703 | 121.5975 | 121.5366 | 121.5683 | 93.6952 | -121.6838 | 121.5979 | 121.5912 | 121.6493 | 106.262 | -121.9423
1083.9375 | 121.7834 | -121.6232 | 0.09613 | 1.4211e-13 | -0.023036 | -1.7092e-05 | 0.059731 | -0.0064228 | 0.058473 | -0.22823 | -0.0037514 | -0.0032433 | 0.059997 | 0.023927 | 0.057772 | -120.9142 | -27.9326 | -121.2459 | 0.006344 | -0.04543 | -0.013707 | -121.6015 | -121.2157 | -15.3108 | -121.3189 | 0.020409 | 0.013707 | 0.067272 | -121.8645 | 0.021779 | -0.089786 | 0.70905 | 0.37737 | 0.35559 | -0.14156 | -0.10984 | -0.2413 | -0.075721 | 0.40751 | 0.30433 | 0.54563 | -0.082423 | -0.028858 | 121.6296 | 121.5778 | 121.6095 | 93.6906 | -121.6976 | 121.6436 | 121.6369 | 121.6905 | 106.3124 | -121.9607
1085.6875 | 121.8704 | -121.5866 | 0.082397 | 1.4211e-13 | -0.023463 | -1.7092e-05 | 0.060158 | -0.006209 | 0.058473 | -0.23586 | -0.0035378 | -0.0034569 | 0.059997 | 0.024141 | 0.057986 | -120.9096 | -27.9006 | -121.2504 | 0.010922 | -0.040851 | -0.013707 | -121.5969 | -121.2157 | -15.3521 | -121.3189 | 0.020409 | 0.009128 | 0.067272 | -121.86 | -0.010263 | -0.071475 | 0.67701 | 0.33617 | 0.34644 | -0.12325 | -0.096104 | -0.27334 | -0.061988 | 0.37089 | 0.26771 | 0.54105 | -0.073269 | -0.015125 | 121.5975 | 121.5458 | 121.5729 | 93.686 | -121.6793 | 121.607 | 121.5957 | 121.6539 | 106.2346 | -121.9423
1087.4219 | 121.9345 | -121.5958 | 0.068665 | 1.4211e-13 | -0.02325 | -0.00023069 | 0.059945 | -0.0066364 | 0.058687 | -0.23586 | -0.0037514 | -0.0032433 | 0.060424 | 0.024141 | 0.057772 | -120.905 | -27.951 | -121.2459 | 0.015501 | -0.04543 | -0.013707 | -121.6015 | -121.2203 | -15.3612 | -121.3143 | 0.015831 | 0.013707 | 0.062694 | -121.8554 | -0.005687 | -0.053164 | 0.69075 | 0.34991 | 0.35559 | -0.1141 | -0.082372 | -0.25961 | -0.052834 | 0.37547 | 0.28144 | 0.54105 | -0.054958 | -0.005971 | 121.6113 | 121.5503 | 121.5821 | 93.6448 | -121.6701 | 121.6116 | 121.6095 | 121.6585 | 106.2346 | -121.924
1089.1562 | 121.8384 | -121.6003 | 0.11902 | 1.4211e-13 | -0.02325 | -0.00044449 | 0.059945 | -0.0066364 | 0.058687 | -0.21297 | -0.0033242 | -0.0036707 | 0.06021 | 0.023927 | 0.057772 | -120.9004 | -27.9189 | -121.2504 | 0.010922 | -0.040851 | -0.013707 | -121.6015 | -121.2111 | -15.3612 | -121.3143 | 0.015831 | 0.004549 | 0.067272 | -121.8645 | -0.001109 | -0.1081 | 0.6999 | 0.34991 | 0.35102 | -0.15987 | -0.13273 | -0.26419 | -0.10319 | 0.3892 | 0.28602 | 0.55021 | -0.11447 | -0.051747 | 121.6113 | 121.5595 | 121.5866 | 93.6814 | -121.7205 | 121.6162 | 121.6049 | 121.6676 | 106.2391 | -121.9835
1090.8906 | 121.9208 | -121.5866 | 0.086975 | 1.4211e-13 | -0.023036 | -0.00044449 | 0.060158 | -0.0064228 | 0.058687 | -0.22823 | -0.0033242 | -0.0036707 | 0.060424 | 0.024354 | 0.057986 | -120.9188 | -27.9052 | -121.2504 | 0.015501 | -0.040851 | -0.013707 | -121.5969 | -121.2249 | -15.3612 | -121.3189 | 0.020409 | 0.013707 | 0.067272 | -121.86 | -0.010263 | -0.071474 | 0.66785 | 0.33617 | 0.34644 | -0.12783 | -0.10068 | -0.27334 | -0.066566 | 0.36173 | 0.26771 | 0.54105 | -0.073268 | -0.019703 | 121.6021 | 121.5458 | 121.5729 | 93.6814 | -121.6838 | 121.607 | 121.6003 | 121.6539 | 106.2254 | -121.9469
1092.5781 | 121.7926 | -121.637 | 0.10529 | 1.4211e-13 | -0.02325 | 0.00019651 | 0.059945 | -0.0064228 | 0.0589 | -0.22823 | -0.0035378 | -0.0034569 | 0.059997 | 0.023927 | 0.057558 | -120.905 | -27.9098 | -121.255 | 0.020079 | -0.036272 | -0.018285 | -121.606 | -121.2203 | -15.4024 | -121.3189 | 0.015831 | 0.009128 | 0.067272 | -121.8645 | 0.030933 | -0.085207 | 0.73194 | 0.38195 | 0.35102 | -0.14156 | -0.12357 | -0.22757 | -0.089455 | 0.41667 | 0.31806 | 0.54563 | -0.096158 | -0.038014 | 121.657 | 121.6007 | 121.6187 | 93.7272 | -121.7113 | 121.6528 | 121.6461 | 121.7042 | 106.2345 | -121.9698
1094.3125 | 121.8704 | -121.6095 | 0.091553 | 1.4211e-13 | -0.023463 | -0.00023069 | 0.059945 | -0.0064228 | 0.058473 | -0.24349 | -0.0035378 | -0.0034569 | 0.060638 | 0.024141 | 0.057986 | -120.9096 | -27.9189 | -121.2504 | 0.010922 | -0.040851 | -0.009128 | -121.606 | -121.2111 | -15.3978 | -121.3235 | 0.011252 | 0.009128 | 0.062694 | -121.8691 | 0.003467 | -0.080631 | 0.6999 | 0.35906 | 0.3556 | -0.1324 | -0.10068 | -0.25961 | -0.080301 | 0.39836 | 0.28602 | 0.54563 | -0.082425 | -0.028859 | 121.6204 | 121.5686 | 121.6004 | 93.6906 | -121.6976 | 121.6207 | 121.6186 | 121.6722 | 106.2117 | -121.9607
1095.9844 | 121.8018 | -121.6232 | 0.10986 | 1.4211e-13 | -0.023036 | -0.00044449 | 0.059945 | -0.0066364 | 0.0589 | -0.22823 | -0.0035378 | -0.0032433 | 0.06021 | 0.023927 | 0.057772 | -120.9004 | -27.9372 | -121.255 | 0.010922 | -0.040851 | -0.013707 | -121.606 | -121.2203 | -15.4345 | -121.3235 | 0.015831 | 0.009128 | 0.067272 | -121.8645 | 0.0172 | -0.098941 | 0.72279 | 0.36822 | 0.35102 | -0.15071 | -0.12357 | -0.2413 | -0.094032 | 0.40293 | 0.29975 | 0.54105 | -0.10074 | -0.042591 | 121.6342 | 121.5824 | 121.6095 | 93.686 | -121.7159 | 121.6391 | 121.6324 | 121.6905 | 106.1888 | -121.9744
1097.7344 | 121.7651 | -121.6415 | 0.10986 | 1.4211e-13 | -0.023677 | -0.00044449 | 0.059945 | -0.006209 | 0.058687 | -0.2206 | -0.0033242 | -0.0034569 | 0.060424 | 0.024141 | 0.057986 | -120.9142 | -27.9372 | -121.2596 | 0.010922 | -0.050009 | -0.018285 | -121.606 | -121.2203 | -15.4299 | -121.3281 | 0.006674 | 0.009128 | 0.058115 | -121.8691 | 0.035511 | -0.098941 | 0.72737 | 0.38195 | 0.34644 | -0.15987 | -0.12815 | -0.22757 | -0.10319 | 0.42124 | 0.31348 | 0.54105 | -0.10074 | -0.051748 | 121.6525 | 121.5915 | 121.6233 | 93.7043 | -121.7159 | 121.6482 | 121.6507 | 121.6997 | 106.2116 | -121.979
1099.4844 | 121.788 | -121.6187 | 0.11902 | 1.4211e-13 | -0.02325 | -1.7092e-05 | 0.059945 | -0.0064228 | 0.058473 | -0.22823 | -0.0033242 | -0.0032433 | 0.06021 | 0.024354 | 0.057772 | -120.9142 | -27.9281 | -121.255 | 0.020079 | -0.04543 | -0.013707 | -121.6152 | -121.2249 | -15.4299 | -121.3235 | 0.015831 | 0.009128 | 0.067272 | -121.8691 | 0.003464 | -0.09894 | 0.70448 | 0.36364 | 0.36017 | -0.16445 | -0.13273 | -0.25046 | -0.10319 | 0.39378 | 0.29517 | 0.54563 | -0.10989 | -0.051747 | 121.6387 | 121.5732 | 121.6049 | 93.6906 | -121.7342 | 121.6345 | 121.6278 | 121.6859 | 106.1888 | -121.9881
1101.1562 | 121.788 | -121.6232 | 0.11902 | 1.4211e-13 | -0.02325 | -0.00044449 | 0.060158 | -0.006209 | 0.058473 | -0.2206 | -0.0033242 | -0.0034569 | 0.060424 | 0.024354 | 0.058199 | -120.905 | -27.9098 | -121.2504 | 0.010922 | -0.040851 | -0.009128 | -121.606 | -121.2249 | -15.4528 | -121.3235 | 0.020409 | -2.9e-05 | 0.071851 | -121.8645 | 0.0172 | -0.1081 | 0.71821 | 0.3728 | 0.3556 | -0.15987 | -0.12815 | -0.2413 | -0.09861 | 0.39836 | 0.29975 | 0.54105 | -0.11905 | -0.047168 | 121.6342 | 121.5824 | 121.6141 | 93.7135 | -121.725 | 121.6436 | 121.6232 | 121.6951 | 106.1704 | -121.9835
1102.8906 | 121.8658 | -121.6003 | 0.091553 | 1.4211e-13 | -0.023677 | -0.00065809 | 0.059731 | -0.0066364 | 0.058473 | -0.22823 | -0.0035378 | -0.0034569 | 0.060638 | 0.024354 | 0.057772 | -120.9096 | -27.951 | -121.255 | 0.010922 | -0.036272 | -0.018285 | -121.606 | -121.2203 | -15.4665 | -121.3189 | 0.024988 | 0.009128 | 0.071851 | -121.8783 | -0.005688 | -0.080631 | 0.69074 | 0.34533 | 0.35102 | -0.12782 | -0.10984 | -0.27792 | -0.066565 | 0.38005 | 0.28144 | 0.55936 | -0.082425 | -0.019702 | 121.6113 | 121.5641 | 121.5821 | 93.6494 | -121.6976 | 121.6253 | 121.6095 | 121.6722 | 106.1338 | -121.9698
1104.6406 | 121.8109 | -121.6187 | 0.11902 | 1.4211e-13 | -0.023463 | -0.00023069 | 0.059945 | -0.0066364 | 0.058259 | -0.23586 | -0.0033242 | -0.0030297 | 0.059997 | 0.023927 | 0.057772 | -120.9096 | -27.9189 | -121.2596 | 0.010922 | -0.04543 | -0.013707 | -121.606 | -121.2295 | -15.4894 | -121.3281 | 0.024988 | 0.013707 | 0.067272 | -121.8737 | 0.012622 | -0.1081 | 0.70905 | 0.35906 | 0.34644 | -0.16445 | -0.13273 | -0.25504 | -0.094031 | 0.3892 | 0.29059 | 0.54563 | -0.10531 | -0.051747 | 121.6296 | 121.5732 | 121.6049 | 93.6997 | -121.725 | 121.6436 | 121.6324 | 121.6859 | 106.1292 | -121.9927
1106.375 | 121.7972 | -121.6003 | 0.11444 | 1.4211e-13 | -0.023677 | -0.00044449 | 0.059945 | -0.0057818 | 0.058473 | -0.22823 | -0.0033242 | -0.0032433 | 0.059997 | 0.024141 | 0.058199 | -120.9096 | -27.9098 | -121.2596 | 0.010922 | -0.050009 | -0.018285 | -121.6106 | -121.2249 | -15.4711 | -121.3281 | 0.015831 | 0.009128 | 0.071851 | -121.8645 | -0.010267 | -0.10352 | 0.69074 | 0.34075 | 0.35102 | -0.16445 | -0.13273 | -0.26419 | -0.09861 | 0.37547 | 0.27228 | 0.53647 | -0.10531 | -0.04259 | 121.6113 | 121.5503 | 121.5821 | 93.6906 | -121.725 | 121.6162 | 121.6095 | 121.6722 | 106.1292 | -121.979
1108.1094 | 121.7743 | -121.6461 | 0.1236 | 1.4211e-13 | -0.023677 | -0.00023069 | 0.059945 | -0.00685 | 0.058473 | -0.2206 | -0.0031106 | -0.0032433 | 0.059997 | 0.024141 | 0.057558 | -120.9142 | -27.9372 | -121.255 | 0.015501 | -0.04543 | -0.009128 | -121.6106 | -121.2203 | -15.4894 | -121.3281 | 0.011252 | 0.013707 | 0.071851 | -121.8691 | 0.035509 | -0.10809 | 0.73194 | 0.3911 | 0.3556 | -0.16903 | -0.13272 | -0.22299 | -0.11234 | 0.42582 | 0.31806 | 0.54105 | -0.10989 | -0.051745 | 121.6616 | 121.6007 | 121.637 | 93.7089 | -121.7342 | 121.6574 | 121.6598 | 121.718 | 106.1567 | -121.9927
1109.7969 | 121.9254 | -121.5637 | 0.073242 | 1.4211e-13 | -0.02325 | -0.00044449 | 0.059731 | -0.0064228 | 0.058687 | -0.22823 | -0.0037514 | -0.0032433 | 0.060424 | 0.024568 | 0.057558 | -120.9096 | -27.9326 | -121.255 | 0.010922 | -0.04543 | -0.009128 | -121.6152 | -121.2249 | -15.5077 | -121.3235 | 0.015831 | 0.009128 | 0.067272 | -121.8783 | -0.051467 | -0.06232 | 0.65412 | 0.30871 | 0.36017 | -0.11867 | -0.08237 | -0.31455 | -0.057411 | 0.33885 | 0.24024 | 0.55478 | -0.064114 | -0.00597 | 121.5746 | 121.5183 | 121.5546 | 93.6311 | -121.6884 | 121.5796 | 121.5728 | 121.631 | 106.056 | -121.9515
1111.5312 | 121.7789 | -121.6415 | 0.1236 | 1.4211e-13 | -0.023463 | -0.00044449 | 0.059517 | -0.006209 | 0.058473 | -0.2206 | -0.0035378 | -0.0034569 | 0.059997 | 0.024568 | 0.057986 | -120.9096 | -27.9189 | -121.2687 | 0.010922 | -0.040851 | -0.009128 | -121.6152 | -121.2203 | -15.5077 | -121.3281 | 0.011252 | 0.013707 | 0.071851 | -121.8737 | 0.026353 | -0.11267 | 0.73194 | 0.37279 | 0.34644 | -0.16445 | -0.13272 | -0.23215 | -0.11234 | 0.42124 | 0.31348 | 0.54563 | -0.10989 | -0.051745 | 121.6525 | 121.6007 | 121.6324 | 93.7226 | -121.7388 | 121.6528 | 121.6552 | 121.7134 | 106.1338 | -121.9973
1113.2656 | 121.9391 | -121.5866 | 0.086975 | 1.4211e-13 | -0.023677 | -0.00044449 | 0.059731 | -0.006209 | 0.058687 | -0.23586 | -0.0033242 | -0.0034569 | 0.059783 | 0.024354 | 0.057986 | -120.9142 | -27.9281 | -121.2596 | 0.015501 | -0.040851 | -0.013707 | -121.6106 | -121.2157 | -15.5352 | -121.3235 | 0.011252 | 0.009128 | 0.067272 | -121.8737 | -0.024 | -0.071474 | 0.67243 | 0.32702 | 0.35102 | -0.12783 | -0.10068 | -0.28708 | -0.075723 | 0.37089 | 0.26313 | 0.55021 | -0.077847 | -0.019703 | 121.6021 | 121.5458 | 121.5729 | 93.6585 | -121.6976 | 121.5979 | 121.5957 | 121.6539 | 106.0514 | -121.9607
1114.9531 | 121.7926 | -121.6141 | 0.11902 | 1.4211e-13 | -0.023463 | -0.00023069 | 0.059945 | -0.006209 | 0.0589 | -0.23586 | -0.0035378 | -0.0034569 | 0.059997 | 0.024782 | 0.057986 | -120.9096 | -27.9143 | -121.2642 | 0.010922 | -0.040851 | -0.009128 | -121.6152 | -121.2203 | -15.5444 | -121.3281 | 0.011252 | 0.022864 | 0.071851 | -121.8783 | -0.001113 | -0.1081 | 0.70448 | 0.34991 | 0.35102 | -0.15987 | -0.12815 | -0.26419 | -0.10777 | 0.39378 | 0.28602 | 0.55021 | -0.096155 | -0.047168 | 121.625 | 121.5732 | 121.6049 | 93.6997 | -121.7342 | 121.6253 | 121.6369 | 121.6859 | 106.0697 | -121.9973
1116.6875 | 121.9437 | -121.6003 | 0.091553 | 1.4211e-13 | -0.023463 | -0.00023069 | 0.059945 | -0.0064228 | 0.058687 | -0.2206 | -0.0035378 | -0.0036707 | 0.059997 | 0.024782 | 0.057772 | -120.9142 | -27.951 | -121.2642 | 0.020079 | -0.040851 | -0.013707 | -121.6106 | -121.2203 | -15.5306 | -121.3326 | 0.006674 | 0.013707 | 0.067272 | -121.8783 | -0.010267 | -0.071474 | 0.68617 | 0.33617 | 0.34644 | -0.1324 | -0.10526 | -0.27792 | -0.084879 | 0.38005 | 0.2677 | 0.54563 | -0.077846 | -0.024281 | 121.6204 | 121.5595 | 121.5866 | 93.6494 | -121.7022 | 121.607 | 121.614 | 121.6676 | 106.0697 | -121.9698
1118.4375 | 121.9162 | -121.6095 | 0.086975 | 1.4211e-13 | -0.023463 | -0.00023069 | 0.059945 | -0.006209 | 0.0589 | -0.22823 | -0.0033242 | -0.0036707 | 0.059783 | 0.024568 | 0.057558 | -120.9096 | -27.9693 | -121.2596 | 0.015501 | -0.031693 | -0.013707 | -121.6106 | -121.2203 | -15.5306 | -121.3281 | 0.015831 | 0.018285 | 0.07643 | -121.8737 | -0.001112 | -0.071474 | 0.6999 | 0.34991 | 0.35102 | -0.11867 | -0.10068 | -0.26419 | -0.071144 | 0.3892 | 0.28144 | 0.54563 | -0.06869 | -0.010545 | 121.625 | 121.5778 | 121.5958 | 93.6402 | -121.6976 | 121.6253 | 121.6278 | 121.6859 | 106.0789 | -121.9607
1120.1719 | 121.8613 | -121.5866 | 0.086975 | 1.4211e-13 | -0.023677 | -1.7092e-05 | 0.059731 | -0.006209 | 0.058687 | -0.22823 | -0.0041788 | -0.0034569 | 0.06021 | 0.024568 | 0.057772 | -120.9096 | -27.9601 | -121.2642 | 0.010922 | -0.04543 | -0.013707 | -121.6106 | -121.2203 | -15.5581 | -121.3281 | 0.020409 | 0.018285 | 0.071851 | -121.8783 | -0.024 | -0.076053 | 0.67701 | 0.32244 | 0.34644 | -0.1324 | -0.10068 | -0.29166 | -0.066566 | 0.36631 | 0.25855 | 0.55021 | -0.06869 | -0.015124 | 121.5975 | 121.5412 | 121.5729 | 93.6265 | -121.6976 | 121.607 | 121.6049 | 121.6585 | 106.0285 | -121.9652
1121.8438 | 121.8704 | -121.6141 | 0.086975 | 1.4211e-13 | -0.023677 | -0.00023069 | 0.059517 | -0.006209 | 0.058687 | -0.22823 | -0.0035378 | -0.0034569 | 0.059997 | 0.024568 | 0.057772 | -120.9142 | -27.9784 | -121.2642 | 0.015501 | -0.040851 | -0.004549 | -121.6106 | -121.2203 | -15.5581 | -121.3281 | 0.015831 | 0.018285 | 0.07643 | -121.8783 | 0.003466 | -0.071474 | 0.6999 | 0.34991 | 0.34644 | -0.12783 | -0.091524 | -0.26419 | -0.071144 | 0.39378 | 0.28602 | 0.55021 | -0.06869 | -0.010545 | 121.6296 | 121.5732 | 121.6095 | 93.6356 | -121.6976 | 121.6299 | 121.6324 | 121.6905 | 106.056 | -121.9652
1123.5781 | 121.8704 | -121.5958 | 0.10529 | 1.4211e-13 | -0.023891 | -0.00023069 | 0.059517 | -0.0059954 | 0.058687 | -0.24349 | -0.0035378 | -0.0032433 | 0.06021 | 0.024568 | 0.057558 | -120.9096 | -27.9464 | -121.2642 | 0.015501 | -0.040851 | -0.009128 | -121.6106 | -121.2157 | -15.5947 | -121.3235 | 0.015831 | 0.018285 | 0.067272 | -121.8783 | -0.014845 | -0.089785 | 0.68617 | 0.3316 | 0.34644 | -0.14614 | -0.11441 | -0.2825 | -0.089455 | 0.38005 | 0.27228 | 0.55478 | -0.087001 | -0.038014 | 121.6113 | 121.5549 | 121.5866 | 93.6494 | -121.7159 | 121.6116 | 121.614 | 121.663 | 106.001 | -121.9836
1125.3125 | 121.8979 | -121.6141 | 0.086975 | 1.4211e-13 | -0.023463 | -1.7092e-05 | 0.059731 | -0.0064228 | 0.058259 | -0.2206 | -0.0037514 | -0.0032433 | 0.06021 | 0.024782 | 0.058199 | -120.9142 | -27.9784 | -121.255 | 0.015501 | -0.040851 | -0.013707 | -121.6152 | -121.2249 | -15.5718 | -121.3326 | 0.020409 | 0.013707 | 0.062694 | -121.8828 | -0.001113 | -0.071474 | 0.6999 | 0.35906 | 0.36017 | -0.12783 | -0.10068 | -0.26877 | -0.066566 | 0.3892 | 0.28144 | 0.55021 | -0.073268 | -0.024281 | 121.6296 | 121.5732 | 121.6004 | 93.6356 | -121.7022 | 121.6345 | 121.6278 | 121.6768 | 106.0422 | -121.9698
1126.9844 | 121.8658 | -121.6049 | 0.073242 | 1.4211e-13 | -0.023891 | -0.00044449 | 0.059731 | -0.006209 | 0.058687 | -0.22823 | -0.0035378 | -0.0034569 | 0.059997 | 0.024568 | 0.057772 | -120.9142 | -27.9876 | -121.2642 | 0.020079 | -0.040851 | -0.009128 | -121.6243 | -121.2249 | -15.613 | -121.3326 | 0.015831 | 0.013707 | 0.067272 | -121.8874 | -0.019427 | -0.053163 | 0.69074 | 0.34075 | 0.36018 | -0.11409 | -0.08237 | -0.28251 | -0.057411 | 0.38004 | 0.27228 | 0.55479 | -0.059535 | -0.00597 | 121.625 | 121.5641 | 121.5958 | 93.6173 | -121.6976 | 121.6208 | 121.6186 | 121.6722 | 105.9919 | -121.9607
1128.7344 | 121.9116 | -121.6141 | 0.07782 | 1.4211e-13 | -0.023463 | -0.00044449 | 0.060158 | -0.006209 | 0.058259 | -0.22823 | -0.0035378 | -0.0034569 | 0.06021 | 0.024782 | 0.057986 | -120.9096 | -27.983 | -121.2687 | 0.010922 | -0.04543 | -0.004549 | -121.6198 | -121.2249 | -15.613 | -121.3281 | 0.015831 | 0.013707 | 0.067272 | -121.8737 | -0.005692 | -0.066898 | 0.70448 | 0.34533 | 0.35102 | -0.12325 | -0.082369 | -0.25961 | -0.061989 | 0.3892 | 0.28602 | 0.54563 | -0.064113 | -0.010548 | 121.625 | 121.5686 | 121.6095 | 93.6311 | -121.6976 | 121.6299 | 121.6278 | 121.6813 | 106.001 | -121.9515
1130.4688 | 121.9345 | -121.582 | 0.082397 | 1.4211e-13 | -0.023891 | -0.00023069 | 0.059731 | -0.0064228 | 0.058473 | -0.2206 | -0.0033242 | -0.0034569 | 0.06021 | 0.024568 | 0.057558 | -120.9096 | -28.0059 | -121.2687 | 0.010922 | -0.040851 | -0.009128 | -121.6243 | -121.2203 | -15.5856 | -121.3326 | 0.020409 | 0.022864 | 0.071851 | -121.8828 | -0.042315 | -0.071475 | 0.67243 | 0.31328 | 0.3556 | -0.12325 | -0.091525 | -0.30082 | -0.061988 | 0.36173 | 0.24939 | 0.55021 | -0.059533 | -0.010546 | 121.593 | 121.5412 | 121.5729 | 93.5761 | -121.7067 | 121.6024 | 121.6049 | 121.6539 | 105.9965 | -121.9652
1132.2188 | 121.8842 | -121.582 | 0.07782 | 1.4211e-13 | -0.023891 | -0.00044449 | 0.059731 | -0.0064228 | 0.058473 | -0.22823 | -0.0037514 | -0.0032433 | 0.060424 | 0.024568 | 0.057986 | -120.9142 | -28.0288 | -121.2642 | 0.001765 | -0.040851 | -0.009128 | -121.606 | -121.2203 | -15.613 | -121.3281 | 0.015831 | 0.013707 | 0.067272 | -121.8828 | -0.023999 | -0.076055 | 0.66786 | 0.31786 | 0.34186 | -0.11867 | -0.086948 | -0.30082 | -0.061989 | 0.36173 | 0.25397 | 0.55479 | -0.064113 | -0.010548 | 121.5838 | 121.5412 | 121.5729 | 93.5532 | -121.6839 | 121.5979 | 121.5957 | 121.6493 | 105.969 | -121.9607
1133.9062 | 121.7972 | -121.6187 | 0.11444 | 1.4211e-13 | -0.023677 | -0.00023069 | 0.059945 | -0.006209 | 0.058687 | -0.22823 | -0.0037514 | -0.0034569 | 0.060424 | 0.024995 | 0.057772 | -120.9142 | -28.0151 | -121.2687 | 0.010922 | -0.040851 | -0.004549 | -121.6152 | -121.2249 | -15.6451 | -121.3281 | 0.011252 | 0.013707 | 0.071851 | -121.8828 | 0.003464 | -0.10352 | 0.70448 | 0.3499 | 0.34644 | -0.15529 | -0.11899 | -0.26419 | -0.10319 | 0.39378 | 0.29059 | 0.55479 | -0.10073 | -0.04259 | 121.6296 | 121.5778 | 121.6141 | 93.6036 | -121.7296 | 121.6299 | 121.6324 | 121.6905 | 105.9736 | -121.9973
1135.6406 | 121.9208 | -121.5866 | 0.07782 | 1.4211e-13 | -0.024104 | -0.00044449 | 0.059517 | -0.006209 | 0.058473 | -0.2206 | -0.0033242 | -0.0034569 | 0.059997 | 0.024568 | 0.057772 | -120.9142 | -28.038 | -121.2687 | 0.015501 | -0.036272 | -0.013707 | -121.6152 | -121.2295 | -15.6634 | -121.3326 | 0.015831 | 0.022864 | 0.062694 | -121.892 | -0.028579 | -0.062319 | 0.67243 | 0.31786 | 0.34644 | -0.11409 | -0.091527 | -0.3054 | -0.061989 | 0.35716 | 0.25397 | 0.55936 | -0.054956 | -0.015126 | 121.6021 | 121.5503 | 121.5729 | 93.5487 | -121.693 | 121.6024 | 121.6095 | 121.6493 | 105.9232 | -121.9698
1137.3125 | 121.8887 | -121.6187 | 0.09613 | 1.4211e-13 | -0.023677 | -0.00065809 | 0.059731 | -0.006209 | 0.058473 | -0.22823 | -0.0035378 | -0.0034569 | 0.059997 | 0.024354 | 0.057558 | -120.9188 | -28.0196 | -121.2687 | 0.020079 | -0.040851 | -0.013707 | -121.6198 | -121.2295 | -15.668 | -121.3281 | 0.020409 | 0.022864 | 0.067272 | -121.8783 | -0.001115 | -0.076051 | 0.6999 | 0.3499 | 0.35102 | -0.13698 | -0.10984 | -0.25961 | -0.075721 | 0.3892 | 0.29059 | 0.55021 | -0.073266 | -0.028858 | 121.6387 | 121.5778 | 121.6049 | 93.599 | -121.7159 | 121.6391 | 121.6415 | 121.6859 | 105.9507 | -121.9744
1138.9844 | 121.8979 | -121.6141 | 0.09613 | 1.4211e-13 | -0.023891 | -0.00044449 | 0.059731 | -0.0059954 | 0.058687 | -0.23586 | -0.0033242 | -0.0034569 | 0.059997 | 0.024782 | 0.057772 | -120.9188 | -28.0105 | -121.2687 | 0.010922 | -0.040851 | -0.013707 | -121.6198 | -121.2295 | -15.6726 | -121.3281 | 0.015831 | 0.022864 | 0.071851 | -121.8874 | -0.005692 | -0.085208 | 0.69532 | 0.34533 | 0.35102 | -0.13698 | -0.10984 | -0.27335 | -0.080299 | 0.38462 | 0.28602 | 0.55936 | -0.073266 | -0.024279 | 121.625 | 121.5732 | 121.6004 | 93.6036 | -121.7159 | 121.6299 | 121.6369 | 121.6859 | 105.9415 | -121.9836
1140.7188 | 121.8292 | -121.6553 | 0.10529 | 1.4211e-13 | -0.023891 | -0.00023069 | 0.059731 | -0.006209 | 0.058473 | -0.22823 | -0.0033242 | -0.0034569 | 0.06021 | 0.025423 | 0.057772 | -120.9142 | -28.0517 | -121.2687 | 0.015501 | -0.040851 | -0.009128 | -121.6198 | -121.2203 | -15.6634 | -121.3281 | 0.006674 | 0.013707 | 0.062694 | -121.892 | 0.035506 | -0.089785 | 0.7411 | 0.38652 | 0.35102 | -0.14614 | -0.11441 | -0.23673 | -0.098612 | 0.43498 | 0.32721 | 0.56394 | -0.091579 | -0.042592 | 121.6708 | 121.6144 | 121.6461 | 93.6036 | -121.7251 | 121.6619 | 121.669 | 121.718 | 105.9919 | -121.9973
1142.4531 | 121.8155 | -121.6644 | 0.10071 | 1.4211e-13 | -0.023677 | -0.00044449 | 0.059517 | -0.006209 | 0.058473 | -0.22823 | -0.0035378 | -0.0032433 | 0.06021 | 0.024995 | 0.057772 | -120.905 | -28.0608 | -121.2687 | 0.015501 | -0.040851 | -0.009128 | -121.6289 | -121.234 | -15.6909 | -121.3281 | 0.015831 | 0.013707 | 0.071851 | -121.892 | 0.035504 | -0.085207 | 0.75941 | 0.39568 | 0.36018 | -0.14156 | -0.10984 | -0.22758 | -0.084877 | 0.4304 | 0.33637 | 0.56394 | -0.087001 | -0.028857 | 121.6799 | 121.6236 | 121.6553 | 93.6036 | -121.7296 | 121.6803 | 121.6781 | 121.7363 | 105.9735 | -121.9927
1144.1875 | 121.8567 | -121.6187 | 0.073242 | 1.4211e-13 | -0.024104 | -0.00044449 | 0.060158 | -0.0064228 | 0.058259 | -0.23586 | -0.0033242 | -0.0032433 | 0.06021 | 0.024995 | 0.057772 | -120.9233 | -28.0334 | -121.2687 | 0.006344 | -0.040851 | -0.018285 | -121.6198 | -121.2249 | -15.7 | -121.3235 | 0.024988 | 0.013707 | 0.071851 | -121.892 | -0.001115 | -0.066898 | 0.69532 | 0.3499 | 0.35102 | -0.11409 | -0.091527 | -0.27335 | -0.048254 | 0.39378 | 0.29517 | 0.56852 | -0.059535 | -0.001391 | 121.625 | 121.5778 | 121.6004 | 93.5853 | -121.693 | 121.6436 | 121.6324 | 121.6905 | 105.9186 | -121.9652
1145.8594 | 121.8613 | -121.6141 | 0.091553 | 1.4211e-13 | -0.023891 | -0.00044449 | 0.059517 | -0.006209 | 0.058473 | -0.22823 | -0.0035378 | -0.0034569 | 0.059783 | 0.024782 | 0.057986 | -120.9142 | -27.9189 | -121.2687 | 0.015501 | -0.036272 | -0.009128 | -121.6243 | -121.234 | -15.7092 | -121.3326 | 0.024988 | 0.018285 | 0.07643 | -121.8966 | -0.010271 | -0.076052 | 0.6999 | 0.34533 | 0.3556 | -0.12782 | -0.10068 | -0.28251 | -0.066565 | 0.38004 | 0.28144 | 0.56394 | -0.073268 | -0.015123 | 121.6296 | 121.5778 | 121.6049 | 93.6952 | -121.7159 | 121.6391 | 121.6324 | 121.6905 | 105.9049 | -121.9881
1147.5938 | 121.9254 | -121.5958 | 0.086975 | 1.4211e-13 | -0.024318 | -0.00044449 | 0.059945 | -0.0059954 | 0.058473 | -0.22823 | -0.0037514 | -0.0034569 | 0.060424 | 0.024782 | 0.057558 | -120.9096 | -27.9189 | -121.2687 | 0.010922 | -0.036272 | -0.009128 | -121.6289 | -121.2249 | -15.7046 | -121.3235 | 0.015831 | 0.022864 | 0.071851 | -121.892 | -0.033161 | -0.076053 | 0.68617 | 0.32702 | 0.36018 | -0.12325 | -0.096103 | -0.29624 | -0.071144 | 0.37089 | 0.27228 | 0.56852 | -0.064111 | -0.015124 | 121.6067 | 121.5595 | 121.5866 | 93.6769 | -121.7159 | 121.6116 | 121.6186 | 121.6676 | 105.8911 | -121.979
1149.3281 | 121.9437 | -121.5958 | 0.086975 | 1.4211e-13 | -0.024104 | -0.00044449 | 0.059731 | -0.006209 | 0.058473 | -0.22823 | -0.0033242 | -0.0032433 | 0.06021 | 0.024568 | 0.057772 | -120.9188 | -27.9372 | -121.2642 | 0.006344 | -0.036272 | -0.004549 | -121.6243 | -121.2295 | -15.6955 | -121.3281 | 0.015831 | 0.022864 | 0.067272 | -121.8828 | -0.028582 | -0.080631 | 0.67701 | 0.3316 | 0.36018 | -0.12325 | -0.091524 | -0.28708 | -0.071144 | 0.36631 | 0.2677 | 0.55479 | -0.064111 | -0.019703 | 121.6021 | 121.5595 | 121.5912 | 93.6585 | -121.7113 | 121.6116 | 121.6186 | 121.663 | 105.9003 | -121.9698
1151.0625 | 121.8613 | -121.6187 | 0.10071 | 1.4211e-13 | -0.023891 | -0.00023069 | 0.059945 | -0.0059954 | 0.058687 | -0.2206 | -0.0037514 | -0.0032433 | 0.059997 | 0.024782 | 0.057772 | -120.9142 | -27.9372 | -121.2733 | 0.015501 | -0.031693 | -0.004549 | -121.6243 | -121.2249 | -15.7229 | -121.3281 | 0.011252 | 0.018285 | 0.071851 | -121.892 | -0.005694 | -0.085207 | 0.70448 | 0.34533 | 0.35102 | -0.1324 | -0.10526 | -0.27335 | -0.089456 | 0.39378 | 0.29059 | 0.56394 | -0.082423 | -0.028857 | 121.6342 | 121.587 | 121.6141 | 93.6814 | -121.7251 | 121.6299 | 121.6369 | 121.6905 | 105.8957 | -121.9927
1152.8125 | 121.843 | -121.637 | 0.11444 | 1.4211e-13 | -0.023891 | -0.00023069 | 0.059731 | -0.0059954 | 0.058687 | -0.2206 | -0.0035378 | -0.0034569 | 0.059783 | 0.025209 | 0.057558 | -120.9096 | -27.9418 | -121.2642 | 0.010922 | -0.031693 | -0.013707 | -121.6198 | -121.2249 | -15.7275 | -121.3326 | 0.011252 | 0.013707 | 0.067272 | -121.892 | 0.017196 | -0.10352 | 0.72737 | 0.37279 | 0.3556 | -0.14613 | -0.12815 | -0.25504 | -0.10319 | 0.41209 | 0.30432 | 0.55936 | -0.10073 | -0.047169 | 121.6479 | 121.6053 | 121.6233 | 93.6952 | -121.7342 | 121.6482 | 121.6507 | 121.7042 | 105.9095 | -122.0064
1154.5 | 121.8796 | -121.6187 | 0.091553 | 1.4211e-13 | -0.024532 | -0.00023069 | 0.059731 | -0.0064228 | 0.058259 | -0.22823 | -0.0037514 | -0.0034569 | 0.059997 | 0.024995 | 0.057986 | -120.9142 | -27.9372 | -121.2687 | 0.010922 | -0.036272 | -0.004549 | -121.6243 | -121.2249 | -15.7412 | -121.3372 | 0.020409 | 0.027442 | 0.07643 | -121.8966 | -0.005694 | -0.080631 | 0.70448 | 0.3499 | 0.3556 | -0.12782 | -0.096102 | -0.27793 | -0.071144 | 0.39378 | 0.28143 | 0.55937 | -0.064111 | -0.015123 | 121.6296 | 121.5824 | 121.6141 | 93.6814 | -121.7159 | 121.6391 | 121.6461 | 121.6951 | 105.8774 | -121.9881
1156.2344 | 121.8018 | -121.6324 | 0.10986 | 1.4211e-13 | -0.024104 | -0.00023069 | 0.059517 | -0.0064228 | 0.058687 | -0.23586 | -0.0035378 | -0.0034569 | 0.059783 | 0.024995 | 0.057772 | -120.9188 | -27.9189 | -121.2687 | 0.015501 | -0.040851 | -0.004549 | -121.6289 | -121.2249 | -15.755 | -121.3281 | 0.015831 | 0.022864 | 0.071851 | -121.892 | 0.00346 | -0.094362 | 0.71363 | 0.36364 | 0.36018 | -0.15071 | -0.11441 | -0.25962 | -0.094032 | 0.40751 | 0.30433 | 0.56394 | -0.086999 | -0.038012 | 121.6479 | 121.5915 | 121.6278 | 93.7135 | -121.7388 | 121.6482 | 121.6552 | 121.7042 | 105.8774 | -122.0019
1157.9688 | 121.8887 | -121.6095 | 0.09613 | 1.4211e-13 | -0.024318 | -0.00023069 | 0.059731 | -0.0064228 | 0.058687 | -0.22823 | -0.0033242 | -0.0032433 | 0.06021 | 0.024782 | 0.057772 | -120.9188 | -27.9418 | -121.2733 | 0.015501 | -0.031693 | -0.013707 | -121.6289 | -121.2295 | -15.7367 | -121.3281 | 0.015831 | 0.018285 | 0.067272 | -121.8966 | -0.019428 | -0.080629 | 0.69074 | 0.33617 | 0.3556 | -0.12782 | -0.10984 | -0.28709 | -0.080299 | 0.38004 | 0.28144 | 0.56852 | -0.077845 | -0.028858 | 121.625 | 121.5778 | 121.5958 | 93.6677 | -121.7251 | 121.6253 | 121.6278 | 121.6768 | 105.8728 | -121.9927
1159.7344 | 121.8796 | -121.6187 | 0.09613 | 1.4211e-13 | -0.024104 | -1.7092e-05 | 0.059945 | -0.0064228 | 0.058473 | -0.2206 | -0.0035378 | -0.0034569 | 0.06021 | 0.024995 | 0.057986 | -120.9233 | -27.9281 | -121.2687 | 0.020079 | -0.040851 | -0.009128 | -121.6198 | -121.2249 | -15.7367 | -121.3372 | 0.024988 | 0.018285 | 0.067272 | -121.8966 | -0.001115 | -0.076051 | 0.69532 | 0.3499 | 0.35102 | -0.13698 | -0.10526 | -0.27793 | -0.071142 | 0.39378 | 0.28143 | 0.55937 | -0.077845 | -0.028858 | 121.6387 | 121.5778 | 121.6095 | 93.6906 | -121.7159 | 121.6436 | 121.6369 | 121.6859 | 105.882 | -121.9927
1161.4219 | 121.9162 | -121.5912 | 0.068665 | 1.4211e-13 | -0.024318 | -0.00044449 | 0.059731 | -0.0064228 | 0.058259 | -0.22823 | -0.0033242 | -0.0030297 | 0.059569 | 0.025423 | 0.057986 | -120.9188 | -27.9601 | -121.2733 | 0.020079 | -0.036272 | -0.004549 | -121.6198 | -121.2249 | -15.7138 | -121.3372 | 0.020409 | 0.018285 | 0.071851 | -121.892 | -0.02858 | -0.048586 | 0.67243 | 0.31786 | 0.34644 | -0.10494 | -0.073214 | -0.30082 | -0.048256 | 0.36631 | 0.25397 | 0.55479 | -0.05038 | 0.003186 | 121.6113 | 121.5549 | 121.5866 | 93.6311 | -121.6884 | 121.6116 | 121.6095 | 121.663 | 105.8774 | -121.9607
1163.1562 | 121.9345 | -121.6141 | 0.082397 | 1.4211e-13 | -0.024104 | -0.00044449 | 0.059731 | -0.0059954 | 0.058473 | -0.22823 | -0.0035378 | -0.0034569 | 0.059997 | 0.025209 | 0.058199 | -120.9142 | -27.9647 | -121.2779 | 0.015501 | -0.036272 | 2.9e-05 | -121.6289 | -121.2249 | -15.7184 | -121.3372 | 0.020409 | 0.009128 | 0.062694 | -121.8966 | -0.01485 | -0.066896 | 0.6999 | 0.33617 | 0.35102 | -0.11867 | -0.082368 | -0.28251 | -0.061988 | 0.3892 | 0.27686 | 0.55937 | -0.073269 | -0.019703 | 121.6296 | 121.5778 | 121.6141 | 93.6494 | -121.7113 | 121.6345 | 121.6232 | 121.6768 | 105.8957 | -121.979
1164.9062 | 121.9162 | -121.6049 | 0.091553 | 1.4211e-13 | -0.024318 | -0.00023069 | 0.059731 | -0.006209 | 0.058473 | -0.22823 | -0.0035378 | -0.0034569 | 0.06021 | 0.024995 | 0.057772 | -120.9188 | -27.983 | -121.2733 | 0.015501 | -0.031693 | -0.009128 | -121.6289 | -121.2295 | -15.755 | -121.3326 | 0.020409 | 0.009128 | 0.071851 | -121.8966 | -0.024006 | -0.076052 | 0.68616 | 0.33159 | 0.3556 | -0.12325 | -0.10068 | -0.29166 | -0.071144 | 0.37547 | 0.27228 | 0.56394 | -0.082425 | -0.019702 | 121.6204 | 121.5732 | 121.5958 | 93.6219 | -121.7205 | 121.6253 | 121.614 | 121.6768 | 105.8499 | -121.9881
1166.5781 | 121.8475 | -121.6232 | 0.09613 | 1.4211e-13 | -0.024318 | -0.00023069 | 0.059945 | -0.0064228 | 0.058473 | -0.2206 | -0.0037514 | -0.0034569 | 0.060424 | 0.024782 | 0.057772 | -120.9188 | -28.0013 | -121.2733 | 0.010922 | -0.031693 | -0.004549 | -121.6335 | -121.2249 | -15.7412 | -121.3281 | 0.020409 | 0.013707 | 0.071851 | -121.892 | -0.010274 | -0.085208 | 0.70448 | 0.3499 | 0.36018 | -0.12782 | -0.10068 | -0.26877 | -0.075721 | 0.39836 | 0.29517 | 0.56394 | -0.082423 | -0.024279 | 121.6342 | 121.5915 | 121.6187 | 93.6219 | -121.7296 | 121.6436 | 121.6369 | 121.6951 | 105.882 | -121.9881
1168.2969 | 121.9391 | -121.5958 | 0.073242 | 1.4211e-13 | -0.024532 | -0.00023069 | 0.059517 | -0.006209 | 0.058046 | -0.2206 | -0.0033242 | -0.0034569 | 0.059997 | 0.024995 | 0.057772 | -120.9188 | -27.9555 | -121.2687 | 0.010922 | -0.036272 | 2.9e-05 | -121.6289 | -121.2249 | -15.7687 | -121.3372 | 0.020409 | 0.013707 | 0.071851 | -121.8966 | -0.033161 | -0.06232 | 0.67701 | 0.32702 | 0.36018 | -0.10951 | -0.073213 | -0.30082 | -0.052833 | 0.37089 | 0.25855 | 0.55937 | -0.059535 | -0.001391 | 121.6067 | 121.5595 | 121.5958 | 93.6402 | -121.7022 | 121.6162 | 121.6095 | 121.6676 | 105.827 | -121.9698
1170.0469 | 121.8018 | -121.6507 | 0.13275 | 1.4211e-13 | -0.024104 | -0.00065809 | 0.059731 | -0.0066364 | 0.058687 | -0.22823 | -0.0035378 | -0.0034569 | 0.06021 | 0.024995 | 0.057986 | -120.9188 | -27.9555 | -121.2687 | 0.015501 | -0.031693 | -0.009128 | -121.6335 | -121.2249 | -15.787 | -121.3326 | 0.020409 | 0.009128 | 0.071851 | -121.892 | 0.017192 | -0.11725 | 0.73194 | 0.38195 | 0.36476 | -0.16444 | -0.14188 | -0.24131 | -0.11234 | 0.42582 | 0.31806 | 0.55936 | -0.12362 | -0.0609 | 121.6662 | 121.619 | 121.6416 | 93.6952 | -121.7663 | 121.6711 | 121.6598 | 121.7225 | 105.8637 | -122.0248
1171.7969 | 121.8567 | -121.6232 | 0.09613 | 1.4211e-13 | -0.024318 | -0.00044449 | 0.059731 | -0.0059954 | 0.058687 | -0.2206 | -0.0035378 | -0.0034569 | 0.059997 | 0.025209 | 0.057772 | -120.9142 | -27.9784 | -121.2733 | 0.015501 | -0.036272 | -0.009128 | -121.6289 | -121.2295 | -15.8099 | -121.3281 | 0.024988 | 0.022864 | 0.07643 | -121.892 | -0.005695 | -0.080629 | 0.70905 | 0.3499 | 0.3556 | -0.1324 | -0.10526 | -0.26877 | -0.071142 | 0.39378 | 0.29517 | 0.56394 | -0.073266 | -0.0197 | 121.6387 | 121.587 | 121.6141 | 93.6448 | -121.7251 | 121.6482 | 121.6461 | 121.6997 | 105.8133 | -121.9881
1173.4688 | 121.8292 | -121.6415 | 0.11902 | 1.4211e-13 | -0.024532 | -0.00023069 | 0.059517 | -0.0064228 | 0.058687 | -0.23586 | -0.0037514 | -0.0034569 | 0.059997 | 0.024995 | 0.057986 | -120.9188 | -27.9876 | -121.2733 | 0.020079 | -0.036272 | 2.9e-05 | -121.6335 | -121.2249 | -15.8008 | -121.3281 | 0.015831 | 0.018285 | 0.081008 | -121.8874 | 0.008037 | -0.09894 | 0.72279 | 0.36822 | 0.36018 | -0.15529 | -0.11899 | -0.24588 | -0.10319 | 0.41667 | 0.31348 | 0.55936 | -0.10073 | -0.038011 | 121.6616 | 121.6053 | 121.6416 | 93.654 | -121.7525 | 121.6574 | 121.6598 | 121.7225 | 105.8408 | -122.0064
1175.2031 | 121.843 | -121.6415 | 0.10529 | 1.4211e-13 | -0.024532 | -0.00065809 | 0.059731 | -0.0064228 | 0.058473 | -0.22823 | -0.0035378 | -0.0032433 | 0.060638 | 0.025209 | 0.057986 | -120.9188 | -28.0334 | -121.2733 | 0.020079 | -0.036272 | -0.004549 | -121.6289 | -121.2295 | -15.8237 | -121.3281 | 0.015831 | 0.018285 | 0.071851 | -121.8874 | 0.012616 | -0.085207 | 0.72279 | 0.36822 | 0.3556 | -0.14156 | -0.10984 | -0.24588 | -0.089455 | 0.41209 | 0.31348 | 0.55936 | -0.087001 | -0.033435 | 121.6616 | 121.6053 | 121.637 | 93.6082 | -121.7342 | 121.6574 | 121.6598 | 121.7134 | 105.8179 | -121.9927
1176.9375 | 121.8063 | -121.6553 | 0.13733 | 1.4211e-13 | -0.024532 | -0.00044449 | 0.059517 | -0.006209 | 0.058473 | -0.22823 | -0.0035378 | -0.0030297 | 0.06021 | 0.024995 | 0.057986 | -120.9142 | -28.0196 | -121.2687 | 0.015501 | -0.027115 | -0.004549 | -121.6289 | -121.234 | -15.8328 | -121.3326 | 0.020409 | 0.022864 | 0.071851 | -121.892 | 0.026348 | -0.12183 | 0.7411 | 0.38652 | 0.36018 | -0.16444 | -0.14188 | -0.23673 | -0.11692 | 0.42124 | 0.32263 | 0.55936 | -0.11447 | -0.065478 | 121.6708 | 121.6282 | 121.6507 | 93.6356 | -121.7663 | 121.6757 | 121.6781 | 121.7271 | 105.8225 | -122.0293
1178.6719 | 121.8933 | -121.6141 | 0.086975 | 1.4211e-13 | -0.024959 | -0.00044449 | 0.059945 | -0.0066364 | 0.058473 | -0.2206 | -0.0035378 | -0.0032433 | 0.059997 | 0.025423 | 0.057772 | -120.9142 | -28.0196 | -121.2687 | 0.010922 | -0.036272 | -0.009128 | -121.6243 | -121.2295 | -15.8466 | -121.3326 | 0.015831 | 0.022864 | 0.071851 | -121.8966 | -0.010271 | -0.076053 | 0.6999 | 0.34533 | 0.3556 | -0.12325 | -0.096103 | -0.28251 | -0.071144 | 0.38462 | 0.28144 | 0.56394 | -0.064111 | -0.015124 | 121.625 | 121.5778 | 121.6049 | 93.5944 | -121.7113 | 121.6299 | 121.6369 | 121.6859 | 105.7675 | -121.9836
1180.3594 | 121.9299 | -121.6003 | 0.064087 | 1.4211e-13 | -0.024532 | -0.00065809 | 0.059945 | -0.0064228 | 0.0589 | -0.22823 | -0.0037514 | -0.0032433 | 0.059997 | 0.025209 | 0.058199 | -120.9096 | -28.0471 | -121.2733 | 0.015501 | -0.031693 | 2.9e-05 | -121.6289 | -121.2249 | -15.8649 | -121.3326 | 0.015831 | 0.013707 | 0.07643 | -121.8828 | -0.028583 | -0.048586 | 0.69074 | 0.32702 | 0.3556 | -0.09578 | -0.064058 | -0.2825 | -0.048256 | 0.37547 | 0.2677 | 0.55021 | -0.05038 | 0.012343 | 121.6158 | 121.5686 | 121.6004 | 93.5532 | -121.693 | 121.6162 | 121.614 | 121.6768 | 105.7355 | -121.9469
1182.0938 | 121.8246 | -121.6415 | 0.12817 | 1.4211e-13 | -0.024532 | -0.00044449 | 0.059517 | -0.0066364 | 0.058687 | -0.22823 | -0.0037514 | -0.0032433 | 0.059783 | 0.025636 | 0.057558 | -120.9233 | -28.0425 | -121.2779 | 0.015501 | -0.036272 | -0.004549 | -121.6381 | -121.2203 | -15.8923 | -121.3326 | 0.015831 | 0.018285 | 0.071851 | -121.892 | 0.003458 | -0.11267 | 0.71821 | 0.36364 | 0.36018 | -0.16445 | -0.13272 | -0.25046 | -0.11234 | 0.42124 | 0.3089 | 0.55936 | -0.10989 | -0.056323 | 121.657 | 121.6053 | 121.637 | 93.599 | -121.7663 | 121.6574 | 121.6598 | 121.7134 | 105.7492 | -122.0202
1183.8281 | 121.8384 | -121.6278 | 0.1236 | 1.4211e-13 | -0.024532 | -0.00023069 | 0.059517 | -0.0066364 | 0.058473 | -0.2206 | -0.0037514 | -0.0034569 | 0.06021 | 0.025209 | 0.057558 | -120.8684 | -28.038 | -121.2642 | 0.015501 | -0.036272 | 2.9e-05 | -121.6335 | -121.2249 | -15.8923 | -121.3326 | 0.015831 | 0.009128 | 0.07643 | -121.8874 | -0.005696 | -0.10809 | 0.75942 | 0.36364 | 0.36934 | -0.15987 | -0.12357 | -0.25962 | -0.10776 | 0.40293 | 0.29517 | 0.55479 | -0.11447 | -0.047166 | 121.6433 | 121.5915 | 121.6278 | 93.5899 | -121.7571 | 121.6436 | 121.6369 | 121.7042 | 105.7355 | -122.011
1185.5 | 121.8933 | -121.6095 | 0.10071 | 1.4211e-13 | -0.024959 | -0.00044449 | 0.059945 | -0.0066364 | 0.058473 | -0.2206 | -0.003965 | -0.0030297 | 0.06021 | 0.025423 | 0.057772 | -120.8684 | -28.038 | -121.2642 | 0.015501 | -0.036272 | -0.009128 | -121.6289 | -121.2295 | -15.8923 | -121.3326 | 0.020409 | 0.018285 | 0.07643 | -121.8874 | -0.019428 | -0.085207 | 0.74111 | 0.34533 | 0.36476 | -0.13698 | -0.10984 | -0.27793 | -0.080299 | 0.38004 | 0.27686 | 0.55479 | -0.082423 | -0.024278 | 121.625 | 121.5732 | 121.6004 | 93.5715 | -121.7296 | 121.6299 | 121.6278 | 121.6859 | 105.7172 | -121.9881
1187.2344 | 121.9574 | -121.6324 | 0.082397 | 1.4211e-13 | -0.024959 | -0.00087189 | 0.059517 | -0.006209 | 0.058473 | -0.22823 | -0.0037514 | -0.0036707 | 0.059997 | 0.025209 | 0.057558 | -120.873 | -28.0334 | -121.2687 | 0.020079 | -0.027115 | -0.004549 | -121.6289 | -121.2249 | -15.8786 | -121.3281 | 0.020409 | 0.018285 | 0.07643 | -121.8828 | 0.00346 | -0.062318 | 0.75942 | 0.36364 | 0.36018 | -0.10951 | -0.086946 | -0.25046 | -0.061988 | 0.40751 | 0.30433 | 0.55479 | -0.064112 | -0.005967 | 121.6525 | 121.6053 | 121.6278 | 93.599 | -121.7113 | 121.6528 | 121.6507 | 121.7088 | 105.7538 | -121.9652
1188.9688 | 121.907 | -121.5958 | 0.068665 | 1.4211e-13 | -0.024746 | -0.00044449 | 0.059731 | -0.0066364 | 0.058473 | -0.2206 | -0.0035378 | -0.0036707 | 0.06021 | 0.025636 | 0.057986 | -120.8638 | -28.0288 | -121.2642 | 0.015501 | -0.031693 | 0.004608 | -121.6335 | -121.2295 | -15.8923 | -121.3281 | 0.015831 | 0.013707 | 0.07643 | -121.892 | -0.03774 | -0.053164 | 0.73195 | 0.3316 | 0.36934 | -0.10036 | -0.064057 | -0.29624 | -0.052834 | 0.36631 | 0.2677 | 0.56394 | -0.054958 | 0.007765 | 121.6113 | 121.5641 | 121.6004 | 93.567 | -121.7022 | 121.6116 | 121.6095 | 121.6722 | 105.7034 | -121.9607
1190.7188 | 121.8567 | -121.6049 | 0.10529 | 1.4211e-13 | -0.024746 | -0.00065809 | 0.059303 | -0.0064228 | 0.058687 | -0.23586 | -0.0033242 | -0.0032433 | 0.059997 | 0.025636 | 0.057558 | -120.8684 | -28.0334 | -121.2733 | 0.015501 | -0.031693 | -0.009128 | -121.6289 | -121.2249 | -15.9015 | -121.3281 | 0.020409 | 0.018285 | 0.07643 | -121.8874 | -0.024006 | -0.089785 | 0.73653 | 0.33159 | 0.3556 | -0.13698 | -0.11441 | -0.28251 | -0.084877 | 0.38004 | 0.27686 | 0.55936 | -0.087001 | -0.028856 | 121.6204 | 121.5732 | 121.5958 | 93.5715 | -121.7342 | 121.6253 | 121.6232 | 121.6813 | 105.7034 | -121.9927
1192.4062 | 121.8246 | -121.6507 | 0.10071 | 1.4211e-13 | -0.024532 | -0.00023069 | 0.059731 | -0.0066364 | 0.058473 | -0.22823 | -0.0037514 | -0.0034569 | 0.060424 | 0.025636 | 0.058199 | -120.8638 | -28.0151 | -121.2687 | 0.015501 | -0.036272 | 2.9e-05 | -121.6335 | -121.2203 | -15.9473 | -121.3235 | 0.015831 | 0.027442 | 0.07643 | -121.8874 | 0.017192 | -0.085207 | 0.78688 | 0.38195 | 0.36476 | -0.13698 | -0.10068 | -0.23673 | -0.084877 | 0.4304 | 0.32721 | 0.56394 | -0.073266 | -0.024278 | 121.6662 | 121.6144 | 121.6507 | 93.6356 | -121.7342 | 121.6665 | 121.6781 | 121.7271 | 105.7034 | -121.9881
1194.1406 | 121.8109 | -121.6553 | 0.1236 | 1.4211e-13 | -0.024959 | -0.00044449 | 0.059731 | -0.006209 | 0.058473 | -0.22823 | -0.0037514 | -0.0032433 | 0.06021 | 0.025423 | 0.057772 | -120.8684 | -28.038 | -121.2687 | 0.015501 | -0.031693 | -0.009128 | -121.6335 | -121.2203 | -15.9061 | -121.3281 | 0.020409 | 0.018285 | 0.071851 | -121.8874 | 0.021769 | -0.10809 | 0.78688 | 0.38652 | 0.36476 | -0.15529 | -0.13272 | -0.23215 | -0.10319 | 0.43498 | 0.32721 | 0.55936 | -0.10531 | -0.051745 | 121.6708 | 121.6236 | 121.6461 | 93.6173 | -121.7571 | 121.6757 | 121.6736 | 121.7271 | 105.7492 | -122.011
1195.875 | 121.7972 | -121.6507 | 0.11444 | 1.4211e-13 | -0.024959 | -0.00044449 | 0.059945 | -0.0066364 | 0.058687 | -0.23586 | -0.0035378 | -0.0036707 | 0.06021 | 0.025423 | 0.057558 | -120.8684 | -28.0608 | -121.2687 | 0.020079 | -0.022536 | -0.004549 | -121.6289 | -121.2249 | -15.9198 | -121.3326 | 0.029566 | 0.013707 | 0.07643 | -121.8828 | 0.021771 | -0.094362 | 0.7823 | 0.38195 | 0.36018 | -0.13698 | -0.11899 | -0.23215 | -0.084875 | 0.42582 | 0.31806 | 0.55021 | -0.10073 | -0.038011 | 121.6708 | 121.6282 | 121.6461 | 93.5898 | -121.7434 | 121.6803 | 121.6644 | 121.7271 | 105.7309 | -121.9973
1197.5469 | 121.8246 | -121.6415 | 0.091553 | 1.4211e-13 | -0.024746 | -0.00065809 | 0.059517 | -0.006209 | 0.058687 | -0.23586 | -0.0035378 | -0.0032433 | 0.059997 | 0.025636 | 0.057558 | -120.8638 | -28.038 | -121.2596 | 0.015501 | -0.022536 | 0.004608 | -121.6289 | -121.2203 | -15.9381 | -121.3235 | 0.024988 | 0.022864 | 0.081008 | -121.8874 | 0.012616 | -0.076052 | 0.77773 | 0.38195 | 0.36933 | -0.11409 | -0.086945 | -0.24588 | -0.066565 | 0.42124 | 0.31806 | 0.56394 | -0.068689 | -0.010545 | 121.657 | 121.619 | 121.6461 | 93.6036 | -121.7205 | 121.6665 | 121.6644 | 121.7225 | 105.7034 | -121.979
1199.2812 | 121.9299 | -121.582 | 0.07782 | 1.4211e-13 | -0.024746 | -0.00044449 | 0.059517 | -0.0064228 | 0.058473 | -0.22823 | -0.0035378 | -0.0032433 | 0.06021 | 0.02585 | 0.057558 | -120.873 | -28.0334 | -121.2642 | 0.020079 | -0.027115 | -0.004549 | -121.6198 | -121.2249 | -15.9702 | -121.3281 | 0.020409 | 0.022864 | 0.07643 | -121.892 | -0.037736 | -0.057741 | 0.70906 | 0.31786 | 0.3556 | -0.10494 | -0.082369 | -0.30997 | -0.057411 | 0.35716 | 0.25397 | 0.56394 | -0.054956 | -0.00139 | 121.6021 | 121.5549 | 121.5775 | 93.5487 | -121.6976 | 121.6024 | 121.6049 | 121.6585 | 105.6119 | -121.9698
1201.0312 | 121.9116 | -121.6003 | 0.082397 | 1.4211e-13 | -0.024959 | -0.00044449 | 0.059945 | -0.0064228 | 0.058259 | -0.2206 | -0.0035378 | -0.0034569 | 0.06021 | 0.025423 | 0.057986 | -120.8638 | -28.0608 | -121.2642 | 0.015501 | -0.031693 | 0.004608 | -121.6243 | -121.2111 | -15.9748 | -121.3281 | 0.020409 | 0.027442 | 0.07643 | -121.8966 | -0.024004 | -0.066896 | 0.73653 | 0.33617 | 0.36018 | -0.11409 | -0.077789 | -0.29624 | -0.061988 | 0.3892 | 0.27228 | 0.56852 | -0.054955 | -0.005967 | 121.6158 | 121.5686 | 121.605 | 93.5395 | -121.7067 | 121.6208 | 121.6278 | 121.6768 | 105.6256 | -121.979
1202.7812 | 121.9254 | -121.582 | 0.10529 | 1.4211e-13 | -0.024959 | -0.00065809 | 0.059517 | -0.0064228 | 0.058046 | -0.2206 | -0.0035378 | -0.0032433 | 0.059997 | 0.025636 | 0.057558 | -120.8684 | -28.0837 | -121.2733 | 0.010922 | -0.031693 | 2.9e-05 | -121.6198 | -121.2157 | -16.0114 | -121.3235 | 0.020409 | 0.022864 | 0.07643 | -121.8828 | -0.037736 | -0.094364 | 0.71364 | 0.30871 | 0.34644 | -0.13698 | -0.10526 | -0.30082 | -0.084877 | 0.36631 | 0.25855 | 0.55936 | -0.082422 | -0.028856 | 121.593 | 121.5503 | 121.5821 | 93.4983 | -121.7251 | 121.6024 | 121.6049 | 121.6585 | 105.5706 | -121.9881
1204.5312 | 121.9116 | -121.6003 | 0.082397 | 1.4211e-13 | -0.025387 | -0.00044449 | 0.059517 | -0.0064228 | 0.058473 | -0.23586 | -0.003965 | -0.0032433 | 0.059997 | 0.02585 | 0.057772 | -120.8592 | -28.1021 | -121.2642 | 0.024657 | -0.031693 | 0.004608 | -121.6289 | -121.2157 | -15.9839 | -121.3235 | 0.024988 | 0.022864 | 0.07643 | -121.8874 | -0.028583 | -0.05774 | 0.74111 | 0.33617 | 0.36476 | -0.11409 | -0.077789 | -0.28708 | -0.057409 | 0.38462 | 0.27686 | 0.56394 | -0.059533 | -0.005967 | 121.625 | 121.5686 | 121.605 | 93.4983 | -121.7113 | 121.6253 | 121.6232 | 121.6768 | 105.6164 | -121.9698
1206.2188 | 121.8567 | -121.6187 | 0.09613 | 1.4211e-13 | -0.024532 | -0.00087189 | 0.059945 | -0.0066364 | 0.058687 | -0.22823 | -0.0037514 | -0.0034569 | 0.06021 | 0.025636 | 0.057772 | -120.873 | -28.1066 | -121.2596 | 0.010922 | -0.031693 | 0.009187 | -121.6243 | -121.2157 | -16.0068 | -121.3189 | 0.020409 | 0.032021 | 0.081008 | -121.8828 | -0.005694 | -0.085208 | 0.74568 | 0.35906 | 0.36476 | -0.12782 | -0.086943 | -0.26419 | -0.075721 | 0.40293 | 0.29975 | 0.56394 | -0.064109 | -0.015122 | 121.6296 | 121.587 | 121.6278 | 93.512 | -121.7205 | 121.6391 | 121.6507 | 121.6997 | 105.6118 | -121.979
1207.9062 | 121.843 | -121.6553 | 0.12817 | 1.4211e-13 | -0.025387 | -0.00044449 | 0.059517 | -0.0064228 | 0.058687 | -0.2206 | -0.003965 | -0.0032433 | 0.059783 | 0.02585 | 0.057772 | -120.8592 | -28.0746 | -121.255 | 0.015501 | -0.036272 | -0.004549 | -121.6243 | -121.2157 | -15.9931 | -121.3235 | 0.024988 | 0.018285 | 0.081008 | -121.8874 | 0.030927 | -0.11267 | 0.79604 | 0.40026 | 0.36933 | -0.16445 | -0.13272 | -0.23215 | -0.10319 | 0.43956 | 0.33179 | 0.56394 | -0.10989 | -0.047166 | 121.6708 | 121.619 | 121.6507 | 93.5807 | -121.7525 | 121.6803 | 121.6736 | 121.7363 | 105.6622 | -122.0156
1209.6406 | 121.8567 | -121.637 | 0.11444 | 1.4211e-13 | -0.025173 | -0.00065809 | 0.059731 | -0.0066364 | 0.058687 | -0.2206 | -0.0037514 | -0.0034569 | 0.06021 | 0.025636 | 0.057772 | -120.8638 | -28.0883 | -121.255 | 0.029236 | -0.031693 | 2.9e-05 | -121.6289 | -121.2157 | -16.016 | -121.3235 | 0.029566 | 0.027442 | 0.081008 | -121.8783 | 0.008038 | -0.085205 | 0.77315 | 0.38195 | 0.37391 | -0.14613 | -0.11441 | -0.2413 | -0.084875 | 0.42125 | 0.31348 | 0.55478 | -0.086999 | -0.033433 | 121.6662 | 121.6053 | 121.637 | 93.5486 | -121.7434 | 121.6665 | 121.6644 | 121.718 | 105.621 | -121.9927
1211.375 | 121.9162 | -121.6095 | 0.10529 | 1.4211e-13 | -0.024959 | -0.00065809 | 0.059731 | -0.00685 | 0.058046 | -0.23586 | -0.003965 | -0.0032433 | 0.059997 | 0.02585 | 0.057558 | -120.8592 | -28.0746 | -121.255 | 0.020079 | -0.022536 | 0.004608 | -121.6198 | -121.2111 | -16.0114 | -121.3235 | 0.034145 | 0.027442 | 0.090166 | -121.8874 | -0.01027 | -0.085207 | 0.75026 | 0.35448 | 0.36475 | -0.12782 | -0.10068 | -0.27793 | -0.071141 | 0.39836 | 0.28602 | 0.56394 | -0.077844 | -0.01512 | 121.6296 | 121.587 | 121.6141 | 93.5349 | -121.7251 | 121.6436 | 121.6369 | 121.6997 | 105.5981 | -121.9927
1213.1094 | 121.8613 | -121.6278 | 0.10986 | 1.4211e-13 | -0.0256 | -0.00065809 | 0.059945 | -0.00685 | 0.058473 | -0.21297 | -0.0035378 | -0.0032433 | 0.059997 | 0.025636 | 0.057772 | -120.8592 | -28.1204 | -121.2504 | 0.020079 | -0.022536 | 0.004608 | -121.6289 | -121.2111 | -16.0343 | -121.3281 | 0.015831 | 0.027442 | 0.085587 | -121.8828 | -0.001117 | -0.089784 | 0.76857 | 0.37737 | 0.37849 | -0.1324 | -0.10526 | -0.25504 | -0.094032 | 0.41667 | 0.29975 | 0.55479 | -0.082421 | -0.024276 | 121.6479 | 121.6053 | 121.6324 | 93.5074 | -121.7388 | 121.6436 | 121.6552 | 121.7134 | 105.5935 | -121.9927
1214.8594 | 121.9299 | -121.582 | 0.09613 | 1.4211e-13 | -0.024746 | -0.00044449 | 0.060158 | -0.0066364 | 0.058687 | -0.22823 | -0.003965 | -0.0030297 | 0.06021 | 0.025636 | 0.058199 | -120.8547 | -28.1295 | -121.255 | 0.029236 | -0.022536 | 0.004608 | -121.6198 | -121.2066 | -16.048 | -121.3235 | 0.034145 | 0.027442 | 0.081008 | -121.8828 | -0.037736 | -0.066894 | 0.72737 | 0.32702 | 0.36475 | -0.11867 | -0.091522 | -0.30082 | -0.061985 | 0.37547 | 0.25855 | 0.55936 | -0.068688 | -0.015122 | 121.6113 | 121.5595 | 121.5866 | 93.4525 | -121.7159 | 121.6162 | 121.6095 | 121.663 | 105.534 | -121.979
1216.5938 | 121.8109 | -121.6461 | 0.12817 | 1.4211e-13 | -0.0256 | -1.7092e-05 | 0.059945 | -0.0064228 | 0.058473 | -0.2206 | -0.0035378 | -0.0034569 | 0.059783 | 0.025636 | 0.057345 | -120.8592 | -28.1204 | -121.2596 | 0.020079 | -0.017957 | 0.009187 | -121.6335 | -121.2066 | -16.048 | -121.3097 | 0.034145 | 0.027442 | 0.081008 | -121.8828 | 0.012614 | -0.1081 | 0.78688 | 0.38653 | 0.37391 | -0.14613 | -0.11899 | -0.23673 | -0.094029 | 0.43956 | 0.33637 | 0.5731 | -0.10073 | -0.047166 | 121.6662 | 121.6282 | 121.6553 | 93.5257 | -121.7617 | 121.6803 | 121.6736 | 121.7271 | 105.5981 | -122.011
1218.2656 | 121.8155 | -121.6324 | 0.13733 | 1.4211e-13 | -0.025173 | -0.00023069 | 0.059945 | -0.006209 | 0.058259 | -0.22823 | -0.0037514 | -0.0034569 | 0.059997 | 0.025423 | 0.057772 | -120.8501 | -28.1204 | -121.2504 | 0.029236 | -0.022536 | 0.004608 | -121.6152 | -121.2066 | -16.0572 | -121.3097 | 0.029566 | 0.032021 | 0.07643 | -121.8783 | 0.017197 | -0.10809 | 0.78231 | 0.38195 | 0.36475 | -0.15987 | -0.13272 | -0.24588 | -0.10776 | 0.42583 | 0.32264 | 0.56852 | -0.10531 | -0.060899 | 121.6616 | 121.6098 | 121.637 | 93.512 | -121.7525 | 121.662 | 121.6644 | 121.7088 | 105.5752 | -122.0156
1219.9531 | 121.8979 | -121.5958 | 0.091553 | 1.4211e-13 | -0.025387 | -0.00065809 | 0.059731 | -0.0064228 | 0.058473 | -0.22823 | -0.0037514 | -0.0034569 | 0.059997 | 0.025636 | 0.057558 | -120.8592 | -28.1295 | -121.255 | 0.015501 | -0.027115 | 0.004608 | -121.6198 | -121.2157 | -16.0846 | -121.3143 | 0.029566 | 0.027442 | 0.085587 | -121.8737 | -0.024003 | -0.076052 | 0.73653 | 0.34075 | 0.36475 | -0.11867 | -0.086945 | -0.27792 | -0.061987 | 0.38005 | 0.28144 | 0.55936 | -0.064111 | -0.005966 | 121.6113 | 121.5686 | 121.6004 | 93.4662 | -121.7113 | 121.6253 | 121.6232 | 121.6814 | 105.5111 | -121.9652
1221.7031 | 121.7972 | -121.6003 | 0.12817 | 1.4211e-13 | -0.025173 | -0.00023069 | 0.059731 | -0.0066364 | 0.058259 | -0.22823 | -0.0035378 | -0.0032433 | 0.059997 | 0.02585 | 0.057345 | -120.8547 | -28.1845 | -121.255 | 0.020079 | -0.022536 | 0.004608 | -121.6289 | -121.2066 | -16.1259 | -121.3189 | 0.029566 | 0.027442 | 0.085587 | -121.8828 | -0.028583 | -0.1081 | 0.74568 | 0.34533 | 0.37391 | -0.15071 | -0.12357 | -0.2825 | -0.098608 | 0.39378 | 0.28144 | 0.56394 | -0.10073 | -0.042587 | 121.6204 | 121.5778 | 121.605 | 93.4159 | -121.7571 | 121.6299 | 121.6278 | 121.6859 | 105.4745 | -122.011
1223.4375 | 121.9437 | -121.5912 | 0.09613 | 1.4211e-13 | -0.0256 | -0.00044449 | 0.059731 | -0.0066364 | 0.058473 | -0.22823 | -0.0041788 | -0.0032433 | 0.059783 | 0.025636 | 0.057345 | -120.8547 | -28.1662 | -121.255 | 0.024657 | -0.027115 | 0.009187 | -121.6198 | -121.202 | -16.1167 | -121.3143 | 0.029566 | 0.032021 | 0.085587 | -121.8828 | -0.02858 | -0.071473 | 0.73653 | 0.33617 | 0.36475 | -0.12324 | -0.086943 | -0.29166 | -0.066564 | 0.38921 | 0.27686 | 0.56852 | -0.064109 | -0.010543 | 121.6158 | 121.5641 | 121.6004 | 93.425 | -121.7159 | 121.6208 | 121.6232 | 121.6768 | 105.4745 | -121.979
1225.1875 | 121.8887 | -121.6095 | 0.10529 | 1.4211e-13 | -0.025387 | -0.00065809 | 0.059517 | -0.0064228 | 0.058473 | -0.22823 | -0.0037514 | -0.0034569 | 0.059783 | 0.025636 | 0.057558 | -120.8501 | -28.1387 | -121.2504 | 0.024657 | -0.017957 | 0.004608 | -121.6152 | -121.1974 | -16.1121 | -121.3143 | 0.029566 | 0.027442 | 0.071851 | -121.8783 | -0.005691 | -0.080629 | 0.75942 | 0.35906 | 0.36475 | -0.12324 | -0.10068 | -0.26877 | -0.07572 | 0.4121 | 0.29517 | 0.56394 | -0.077844 | -0.033435 | 121.6342 | 121.5915 | 121.6141 | 93.4708 | -121.7205 | 121.6391 | 121.6369 | 121.6813 | 105.4974 | -121.9836
1226.9219 | 121.8155 | -121.637 | 0.13733 | 1.4211e-13 | -0.025387 | -0.00065809 | 0.059731 | -0.006209 | 0.058687 | -0.24349 | -0.0037514 | -0.0030297 | 0.06021 | 0.025636 | 0.057345 | -120.8501 | -28.1478 | -121.2459 | 0.029236 | -0.027115 | 0.009187 | -121.6152 | -121.202 | -16.1304 | -121.3143 | 0.029566 | 0.032021 | 0.090166 | -121.8828 | 0.021775 | -0.10809 | 0.78688 | 0.39111 | 0.36933 | -0.16444 | -0.12814 | -0.24588 | -0.10776 | 0.43498 | 0.32264 | 0.56852 | -0.10531 | -0.047163 | 121.6662 | 121.6098 | 121.6461 | 93.4891 | -121.7525 | 121.6665 | 121.669 | 121.7271 | 105.5065 | -122.0202
1228.6562 | 121.7972 | -121.637 | 0.11902 | 1.4211e-13 | -0.025387 | -0.00087189 | 0.059731 | -0.0066364 | 0.058046 | -0.22823 | -0.003965 | -0.0030297 | 0.059783 | 0.02585 | 0.057558 | -120.8455 | -28.1341 | -121.2504 | 0.029236 | -0.022536 | 0.009187 | -121.606 | -121.1928 | -16.1442 | -121.3052 | 0.029566 | 0.022864 | 0.081008 | -121.8828 | 0.030933 | -0.089783 | 0.79146 | 0.38653 | 0.3556 | -0.14155 | -0.10983 | -0.24588 | -0.089453 | 0.44414 | 0.3318 | 0.57768 | -0.096155 | -0.038011 | 121.6662 | 121.6144 | 121.6461 | 93.5029 | -121.725 | 121.6665 | 121.6598 | 121.718 | 105.4928 | -122.0019
1230.4062 | 121.8155 | -121.6324 | 0.14191 | 1.4211e-13 | -0.025814 | -0.00044449 | 0.059731 | -0.0066364 | 0.058046 | -0.23586 | -0.0037514 | -0.0032433 | 0.059997 | 0.026064 | 0.057558 | -120.8455 | -28.1524 | -121.2504 | 0.024657 | -0.017957 | 0.009187 | -121.6152 | -121.2066 | -16.1488 | -121.296 | 0.029566 | 0.032021 | 0.081008 | -121.8828 | 0.017197 | -0.11725 | 0.78688 | 0.38195 | 0.36475 | -0.15986 | -0.13272 | -0.25046 | -0.11234 | 0.42583 | 0.33638 | 0.58684 | -0.10989 | -0.060899 | 121.657 | 121.6144 | 121.6416 | 93.48 | -121.7571 | 121.662 | 121.6644 | 121.7134 | 105.4836 | -122.0248
1232.0938 | 121.8796 | -121.5958 | 0.10071 | 1.4211e-13 | -0.025387 | -0.00044449 | 0.059731 | -0.00685 | 0.058473 | -0.22823 | -0.0035378 | -0.0032433 | 0.059783 | 0.026064 | 0.057772 | -120.8409 | -28.1616 | -121.2504 | 0.029236 | -0.017957 | 0.009187 | -121.606 | -121.1882 | -16.1625 | -121.3052 | 0.034145 | 0.032021 | 0.081008 | -121.8783 | -0.010266 | -0.071472 | 0.75484 | 0.34533 | 0.3556 | -0.11867 | -0.091521 | -0.2825 | -0.066563 | 0.40752 | 0.2906 | 0.5731 | -0.068687 | -0.0197 | 121.625 | 121.5778 | 121.605 | 93.4342 | -121.7067 | 121.6299 | 121.6278 | 121.6768 | 105.4333 | -121.979
1233.8281 | 121.8842 | -121.5775 | 0.10986 | 1.4211e-13 | -0.025387 | -0.00065809 | 0.059731 | -0.0066364 | 0.058259 | -0.21297 | -0.0037514 | -0.0036707 | 0.059783 | 0.026277 | 0.057772 | -120.8409 | -28.1753 | -121.2459 | 0.029236 | -0.022536 | 0.013765 | -121.606 | -121.1882 | -16.1488 | -121.3006 | 0.024988 | 0.041178 | 0.085587 | -121.8783 | -0.028576 | -0.080627 | 0.73653 | 0.3316 | 0.36017 | -0.1324 | -0.096098 | -0.30081 | -0.084875 | 0.38921 | 0.27687 | 0.57768 | -0.068685 | -0.024276 | 121.6067 | 121.5549 | 121.5912 | 93.4021 | -121.7159 | 121.6024 | 121.6186 | 121.663 | 105.4287 | -121.9881
1235.5625 | 121.8933 | -121.5912 | 0.10529 | 1.4211e-13 | -0.0256 | -0.00044449 | 0.059731 | -0.0066364 | 0.058259 | -0.2206 | -0.0037514 | -0.0034569 | 0.059997 | 0.026064 | 0.057558 | -120.8409 | -28.1524 | -121.2459 | 0.029236 | -0.022536 | 0.009187 | -121.606 | -121.1974 | -16.1716 | -121.3006 | 0.034145 | 0.032021 | 0.085587 | -121.8645 | -0.014843 | -0.07605 | 0.75026 | 0.34533 | 0.36017 | -0.12782 | -0.096099 | -0.27334 | -0.071141 | 0.39379 | 0.2906 | 0.56394 | -0.073265 | -0.019699 | 121.6204 | 121.5687 | 121.6004 | 93.4388 | -121.7113 | 121.6253 | 121.6232 | 121.6768 | 105.4195 | -121.9698
1237.2344 | 121.8704 | -121.5866 | 0.10986 | 1.4211e-13 | -0.025387 | -0.00087189 | 0.060158 | -0.00685 | 0.058473 | -0.22823 | -0.0037514 | -0.0034569 | 0.059783 | 0.025636 | 0.057558 | -120.8409 | -28.1616 | -121.2413 | 0.024657 | -0.017957 | 0.013765 | -121.6015 | -121.1882 | -16.1579 | -121.3006 | 0.029566 | 0.032021 | 0.090166 | -121.8737 | -0.014842 | -0.085206 | 0.74569 | 0.34533 | 0.36017 | -0.12782 | -0.096098 | -0.28708 | -0.080297 | 0.39836 | 0.28602 | 0.5731 | -0.077842 | -0.019697 | 121.6113 | 121.5687 | 121.6004 | 93.425 | -121.7113 | 121.6162 | 121.6186 | 121.6768 | 105.4287 | -121.9836
1238.9219 | 121.9299 | -121.5683 | 0.086975 | 1.4211e-13 | -0.025387 | -0.00023069 | 0.059945 | -0.0064228 | 0.058259 | -0.22823 | -0.0035378 | -0.0034569 | 0.059997 | 0.026064 | 0.057772 | -120.8363 | -28.1341 | -121.2459 | 0.024657 | -0.013378 | 0.013765 | -121.606 | -121.1928 | -16.1671 | -121.2914 | 0.029566 | 0.0366 | 0.081008 | -121.8783 | -0.037732 | -0.062318 | 0.73195 | 0.32244 | 0.36017 | -0.10035 | -0.07321 | -0.30997 | -0.057409 | 0.37547 | 0.27687 | 0.58684 | -0.050375 | -0.005967 | 121.593 | 121.5549 | 121.5821 | 93.4342 | -121.693 | 121.5979 | 121.6049 | 121.6493 | 105.4012 | -121.9652
1240.6719 | 121.843 | -121.5912 | 0.1236 | 1.4211e-13 | -0.0256 | -0.00044449 | 0.059517 | -0.00685 | 0.058473 | -0.2206 | -0.0037514 | -0.0034569 | 0.059997 | 0.026064 | 0.057986 | -120.8318 | -28.189 | -121.2413 | 0.033814 | -0.013378 | 0.009187 | -121.6106 | -121.1928 | -16.1991 | -121.2914 | 0.038723 | 0.032021 | 0.085587 | -121.8691 | -0.019422 | -0.089782 | 0.75942 | 0.34991 | 0.36933 | -0.13697 | -0.11441 | -0.27792 | -0.084873 | 0.39836 | 0.29976 | 0.57768 | -0.091575 | -0.038009 | 121.625 | 121.5778 | 121.6004 | 93.4021 | -121.7342 | 121.6299 | 121.6232 | 121.6768 | 105.3921 | -121.9927
1242.3438 | 121.8063 | -121.6278 | 0.12817 | 1.4211e-13 | -0.025814 | -0.00087189 | 0.059517 | -0.00685 | 0.058259 | -0.22823 | -0.0037514 | -0.0034569 | 0.059997 | 0.02585 | 0.057558 | -120.8363 | -28.1707 | -121.2459 | 0.029236 | -0.022536 | 0.013765 | -121.6015 | -121.1882 | -16.2449 | -121.2914 | 0.029566 | 0.0366 | 0.090166 | -121.8737 | 0.026357 | -0.098938 | 0.79147 | 0.38195 | 0.35559 | -0.15071 | -0.11441 | -0.24588 | -0.098608 | 0.43956 | 0.33638 | 0.58226 | -0.091574 | -0.038008 | 121.657 | 121.6053 | 121.6416 | 93.4571 | -121.7296 | 121.6574 | 121.6644 | 121.718 | 105.3829 | -122.0019
1244.0781 | 121.8842 | -121.5683 | 0.091553 | 1.4211e-13 | -0.0256 | -0.00044449 | 0.059945 | -0.0066364 | 0.058046 | -0.23586 | -0.0037514 | -0.0032433 | 0.059997 | 0.026277 | 0.057558 | -120.8318 | -28.2028 | -121.2413 | 0.024657 | -0.022536 | 0.022922 | -121.6015 | -121.1837 | -16.2678 | -121.2914 | 0.043302 | 0.0366 | 0.094744 | -121.8691 | -0.033153 | -0.066896 | 0.73653 | 0.32702 | 0.36017 | -0.11409 | -0.068631 | -0.30081 | -0.048251 | 0.38463 | 0.27687 | 0.57768 | -0.054953 | 0.003191 | 121.593 | 121.5458 | 121.5912 | 93.3655 | -121.693 | 121.6116 | 121.6049 | 121.663 | 105.3005 | -121.9607
1245.8281 | 121.8384 | -121.582 | 0.1236 | 1.4211e-13 | -0.0256 | -0.00087189 | 0.059945 | -0.00685 | 0.058259 | -0.21297 | -0.0033242 | -0.0034569 | 0.06021 | 0.026064 | 0.057772 | -120.8318 | -28.2165 | -121.2367 | 0.033814 | -0.017957 | 0.018344 | -121.6015 | -121.1882 | -16.2312 | -121.2914 | 0.029566 | 0.0366 | 0.090166 | -121.8691 | -0.01942 | -0.089782 | 0.75027 | 0.34533 | 0.36475 | -0.14155 | -0.10525 | -0.28708 | -0.09403 | 0.39379 | 0.2906 | 0.57768 | -0.086996 | -0.03343 | 121.6158 | 121.5641 | 121.6004 | 93.3655 | -121.725 | 121.6116 | 121.6186 | 121.6722 | 105.3509 | -121.9927
1247.5625 | 121.8933 | -121.582 | 0.10071 | 1.4211e-13 | -0.025814 | -0.00044449 | 0.059731 | -0.006209 | 0.058046 | -0.23586 | -0.0031106 | -0.0032433 | 0.06021 | 0.026064 | 0.057345 | -120.8272 | -28.2028 | -121.2275 | 0.038393 | -0.008799 | 0.022922 | -121.6015 | -121.1837 | -16.2495 | -121.2914 | 0.043302 | 0.041178 | 0.090166 | -121.8691 | -0.01942 | -0.062315 | 0.75485 | 0.35449 | 0.37391 | -0.10951 | -0.077786 | -0.28708 | -0.057406 | 0.39836 | 0.2906 | 0.57768 | -0.05953 | -0.010542 | 121.6204 | 121.5732 | 121.605 | 93.3792 | -121.7022 | 121.6253 | 121.6232 | 121.6722 | 105.3325 | -121.9698
1249.2344 | 121.7834 | -121.637 | 0.13733 | 1.4211e-13 | -0.025814 | -0.00065809 | 0.059945 | -0.00685 | 0.058259 | -0.23586 | -0.003965 | -0.0032433 | 0.059783 | 0.026277 | 0.057558 | -120.8318 | -28.1982 | -121.2413 | 0.038393 | -0.013378 | 0.022922 | -121.6015 | -121.1791 | -16.2495 | -121.2869 | 0.029566 | 0.032021 | 0.090166 | -121.8691 | 0.035512 | -0.098936 | 0.8052 | 0.39569 | 0.36017 | -0.15071 | -0.11441 | -0.23215 | -0.10776 | 0.45788 | 0.35011 | 0.58226 | -0.10531 | -0.047163 | 121.6754 | 121.6236 | 121.6599 | 93.4388 | -121.7388 | 121.6665 | 121.669 | 121.7271 | 105.3875 | -122.0064
1250.9219 | 121.8613 | -121.582 | 0.091553 | 1.4211e-13 | -0.0256 | -0.00044449 | 0.060372 | -0.00685 | 0.058046 | -0.21297 | -0.0041788 | -0.0032433 | 0.059997 | 0.026277 | 0.057772 | -120.8226 | -28.2119 | -121.2275 | 0.033814 | -0.008799 | 0.027501 | -121.5969 | -121.1699 | -16.2815 | -121.2869 | 0.034145 | 0.0366 | 0.099323 | -121.8645 | -0.014841 | -0.057739 | 0.75942 | 0.35449 | 0.36933 | -0.10035 | -0.064052 | -0.2825 | -0.057408 | 0.4121 | 0.29518 | 0.57768 | -0.054953 | 0.00777 | 121.6158 | 121.5732 | 121.6095 | 93.3701 | -121.6884 | 121.6162 | 121.6186 | 121.6814 | 105.3005 | -121.9561
1252.6719 | 121.7926 | -121.5591 | 0.14191 | 1.4211e-13 | -0.025814 | -0.00023069 | 0.060158 | -0.006209 | 0.058046 | -0.2206 | -0.0035378 | -0.0034569 | 0.059997 | 0.026277 | 0.057558 | -120.8043 | -28.2303 | -121.2138 | 0.052128 | -0.00422 | 0.036658 | -121.574 | -121.1516 | -16.2632 | -121.2594 | 0.052459 | 0.054914 | 0.10848 | -121.8325 | -0.014835 | -0.089779 | 0.75485 | 0.34534 | 0.36017 | -0.14613 | -0.10525 | -0.27334 | -0.089448 | 0.40753 | 0.29976 | 0.5731 | -0.086993 | -0.033427 | 121.6113 | 121.5549 | 121.5958 | 93.3289 | -121.7159 | 121.6116 | 121.6141 | 121.6676 | 105.2959 | -121.9744
1254.3438 | 121.8155 | -121.5958 | 0.14191 | 1.4211e-13 | -0.026028 | -0.00065809 | 0.060158 | -0.00685 | 0.058046 | -0.2206 | -0.0041788 | -0.0036707 | 0.059783 | 0.026277 | 0.057558 | -120.7951 | -28.2577 | -121.2047 | 0.052128 | 0.004938 | 0.036658 | -121.5694 | -121.147 | -16.2632 | -121.2548 | 0.057037 | 0.054914 | 0.10848 | -121.8371 | 0.026365 | -0.089779 | 0.80063 | 0.39111 | 0.36475 | -0.13697 | -0.10525 | -0.24129 | -0.08487 | 0.44873 | 0.34096 | 0.58226 | -0.086993 | -0.033427 | 121.6479 | 121.6007 | 121.6324 | 93.338 | -121.7113 | 121.6528 | 121.6507 | 121.7042 | 105.3325 | -121.979
1256.0312 | 121.8338 | -121.5546 | 0.13275 | 1.4211e-13 | -0.025814 | -0.00065809 | 0.059945 | -0.0066364 | 0.058473 | -0.22823 | -0.0035378 | -0.0032433 | 0.059997 | 0.026064 | 0.057772 | -120.786 | -28.2669 | -121.2047 | 0.047549 | 0.004938 | 0.03208 | -121.5602 | -121.1425 | -16.2815 | -121.2548 | 0.057037 | 0.059493 | 0.11306 | -121.8325 | -0.005676 | -0.085202 | 0.76858 | 0.34991 | 0.35559 | -0.12781 | -0.10067 | -0.27791 | -0.075714 | 0.41211 | 0.29976 | 0.57768 | -0.073258 | -0.019692 | 121.6021 | 121.5595 | 121.5866 | 93.2877 | -121.693 | 121.6116 | 121.6141 | 121.6676 | 105.273 | -121.9652
1257.7812 | 121.8063 | -121.5546 | 0.15106 | 1.4211e-13 | -0.025814 | -0.00065809 | 0.060372 | -0.0064228 | 0.058259 | -0.23586 | -0.0037514 | -0.0028161 | 0.059783 | 0.026277 | 0.058199 | -120.7814 | -28.2944 | -121.1955 | 0.042971 | 0.009517 | 0.045815 | -121.5557 | -121.1425 | -16.3044 | -121.2456 | 0.061616 | 0.054914 | 0.11306 | -121.8325 | -0.001097 | -0.10809 | 0.77316 | 0.35907 | 0.36017 | -0.14155 | -0.10525 | -0.27791 | -0.089446 | 0.41211 | 0.30892 | 0.58684 | -0.096148 | -0.038003 | 121.5975 | 121.5641 | 121.6004 | 93.2602 | -121.7067 | 121.6162 | 121.6095 | 121.6676 | 105.2501 | -121.9835
1259.5156 | 121.7102 | -121.5591 | 0.15106 | 1.4211e-13 | -0.025387 | -0.00087189 | 0.060372 | -0.00685 | 0.058046 | -0.23586 | -0.0035378 | -0.0030297 | 0.059783 | 0.026491 | 0.057772 | -120.786 | -28.2989 | -121.1863 | 0.056706 | 0.009517 | 0.041237 | -121.5602 | -121.1333 | -16.2953 | -121.2411 | 0.057037 | 0.059493 | 0.10848 | -121.8279 | -0.001098 | -0.094356 | 0.77316 | 0.3728 | 0.3739 | -0.14155 | -0.10983 | -0.26876 | -0.094025 | 0.42584 | 0.31808 | 0.58683 | -0.091569 | -0.042582 | 121.6158 | 121.5687 | 121.6004 | 93.2602 | -121.7113 | 121.6162 | 121.6186 | 121.6676 | 105.2639 | -121.979
1261.2031 | 121.7834 | -121.5591 | 0.15564 | 1.4211e-13 | -0.026028 | -0.00065809 | 0.059731 | -0.00685 | 0.058259 | -0.2206 | -0.003965 | -0.0034569 | 0.059997 | 0.026491 | 0.057558 | -120.7768 | -28.2852 | -121.1818 | 0.052128 | 0.004938 | 0.041237 | -121.5511 | -121.1196 | -16.2953 | -121.2411 | 0.052459 | 0.059493 | 0.10848 | -121.8279 | 0.00806 | -0.10351 | 0.78232 | 0.37738 | 0.36932 | -0.1507 | -0.1144 | -0.26876 | -0.10318 | 0.43958 | 0.31808 | 0.58683 | -0.096147 | -0.04716 | 121.6113 | 121.5641 | 121.6004 | 93.2739 | -121.7067 | 121.6116 | 121.6186 | 121.6676 | 105.2639 | -121.9835
1262.9531 | 121.8246 | -121.5637 | 0.15106 | 1.4211e-13 | -0.025814 | -0.00087189 | 0.060158 | -0.00685 | 0.058046 | -0.24349 | -0.0033242 | -0.0032433 | 0.059783 | 0.026064 | 0.057345 | -120.7722 | -28.2898 | -121.1772 | 0.047549 | 0.009517 | 0.041237 | -121.5511 | -121.1287 | -16.2953 | -121.2273 | 0.057037 | 0.059493 | 0.12222 | -121.8187 | 0.012638 | -0.10351 | 0.79148 | 0.38654 | 0.3739 | -0.14155 | -0.10983 | -0.25502 | -0.094025 | 0.435 | 0.33639 | 0.59141 | -0.091569 | -0.028846 | 121.6113 | 121.5732 | 121.605 | 93.2739 | -121.7021 | 121.6208 | 121.6232 | 121.6859 | 105.2685 | -121.9698
1264.6406 | 121.7514 | -121.55 | 0.17395 | 1.4211e-13 | -0.026028 | -0.00065809 | 0.060158 | -0.0070638 | 0.058259 | -0.23586 | -0.0037514 | -0.0034569 | 0.059997 | 0.026064 | 0.057558 | -120.7722 | -28.3081 | -121.1772 | 0.061284 | 0.004938 | 0.045815 | -121.5419 | -121.115 | -16.2998 | -121.2273 | 0.061616 | 0.064071 | 0.11764 | -121.8187 | 0.008063 | -0.11267 | 0.77774 | 0.37281 | 0.36474 | -0.16901 | -0.12813 | -0.26875 | -0.11233 | 0.435 | 0.32266 | 0.59141 | -0.10988 | -0.056313 | 121.6113 | 121.5549 | 121.5958 | 93.2419 | -121.7159 | 121.6116 | 121.6141 | 121.6676 | 105.2501 | -121.9927
1266.375 | 121.7651 | -121.5454 | 0.15564 | 1.4211e-13 | -0.026028 | -0.00044449 | 0.060158 | -0.00685 | 0.058473 | -0.22823 | -0.0035378 | -0.0032433 | 0.059783 | 0.026491 | 0.057345 | -120.7768 | -28.331 | -121.168 | 0.056706 | 0.014096 | 0.045815 | -121.5465 | -121.1104 | -16.2907 | -121.2228 | 0.066194 | 0.064071 | 0.11306 | -121.8187 | -0.001094 | -0.098934 | 0.76859 | 0.37738 | 0.37848 | -0.14154 | -0.10983 | -0.27333 | -0.089446 | 0.435 | 0.32266 | 0.59599 | -0.091569 | -0.042581 | 121.6021 | 121.5595 | 121.5912 | 93.2144 | -121.7021 | 121.6116 | 121.6095 | 121.6585 | 105.2547 | -121.9744
1268.1094 | 121.7743 | -121.5317 | 0.17395 | 1.4211e-13 | -0.026028 | -0.00065809 | 0.060372 | -0.0066364 | 0.058046 | -0.2206 | -0.0035378 | -0.0032433 | 0.06021 | 0.026277 | 0.057558 | -120.7631 | -28.3264 | -121.1589 | 0.061284 | 0.004938 | 0.041237 | -121.5373 | -121.1058 | -16.3136 | -121.2182 | 0.066194 | 0.064071 | 0.11306 | -121.8096 | -0.005669 | -0.11267 | 0.76859 | 0.37281 | 0.37848 | -0.16901 | -0.13271 | -0.27791 | -0.10776 | 0.42585 | 0.31351 | 0.59141 | -0.10988 | -0.060891 | 121.593 | 121.5366 | 121.5729 | 93.2053 | -121.7113 | 121.5979 | 121.5957 | 121.6447 | 105.2181 | -121.9835
1269.8438 | 121.8796 | -121.5225 | 0.14648 | 1.4211e-13 | -0.026028 | -0.00065809 | 0.060372 | -0.0072774 | 0.058259 | -0.22823 | -0.0037514 | -0.0032433 | 0.059783 | 0.026705 | 0.057772 | -120.7585 | -28.331 | -121.1634 | 0.047549 | 0.014096 | 0.045815 | -121.5373 | -121.1058 | -16.3502 | -121.2182 | 0.057037 | 0.064071 | 0.11764 | -121.8096 | -0.014824 | -0.098935 | 0.76401 | 0.35907 | 0.3739 | -0.13239 | -0.10067 | -0.28706 | -0.089447 | 0.41669 | 0.30435 | 0.59141 | -0.082413 | -0.028847 | 121.5701 | 121.5366 | 121.5683 | 93.1915 | -121.6838 | 121.5796 | 121.5866 | 121.6402 | 105.1723 | -121.9561
1271.5312 | 121.7468 | -121.5042 | 0.17853 | 1.4211e-13 | -0.026241 | -0.00087189 | 0.059945 | -0.0066364 | 0.058259 | -0.22823 | -0.0035378 | -0.0032433 | 0.059997 | 0.026491 | 0.057345 | -120.7356 | -28.3447 | -121.1451 | 0.070441 | 0.027833 | 0.059551 | -121.519 | -121.0784 | -16.3594 | -121.1907 | 0.075351 | 0.082386 | 0.13595 | -121.7913 | -0.01482 | -0.10809 | 0.76859 | 0.35908 | 0.3739 | -0.15069 | -0.11898 | -0.28706 | -0.10318 | 0.42585 | 0.31351 | 0.60057 | -0.096142 | -0.042576 | 121.5747 | 121.532 | 121.5638 | 93.1595 | -121.6976 | 121.5796 | 121.5866 | 121.6402 | 105.1448 | -121.9698
1273.2656 | 121.7789 | -121.4951 | 0.18768 | 1.4211e-13 | -0.026028 | -0.00065809 | 0.060158 | -0.00685 | 0.058259 | -0.2206 | -0.003965 | -0.0032433 | 0.059783 | 0.026491 | 0.057345 | -120.7356 | -28.3493 | -121.136 | 0.070441 | 0.032411 | 0.059551 | -121.5053 | -121.0738 | -16.3868 | -121.1861 | 0.07993 | 0.077807 | 0.13595 | -121.773 | -0.010238 | -0.11724 | 0.75944 | 0.35908 | 0.36932 | -0.15527 | -0.12813 | -0.2779 | -0.10775 | 0.42128 | 0.30894 | 0.58683 | -0.10988 | -0.051731 | 121.5655 | 121.5275 | 121.5546 | 93.1458 | -121.693 | 121.575 | 121.5729 | 121.631 | 105.1082 | -121.9606
1275.0156 | 121.8704 | -121.463 | 0.15106 | 1.4211e-13 | -0.026241 | -0.00065809 | 0.060158 | -0.0070638 | 0.058046 | -0.22823 | -0.0037514 | -0.0034569 | 0.059569 | 0.026491 | 0.057345 | -120.7219 | -28.3493 | -121.136 | 0.070441 | 0.032411 | 0.06413 | -121.5007 | -121.0646 | -16.3868 | -121.1815 | 0.07993 | 0.086964 | 0.12679 | -121.7638 | -0.037702 | -0.080621 | 0.74113 | 0.32704 | 0.36474 | -0.11865 | -0.086932 | -0.30078 | -0.071132 | 0.39839 | 0.28147 | 0.58226 | -0.064098 | -0.024268 | 121.5335 | 121.4954 | 121.5271 | 93.1137 | -121.6518 | 121.5429 | 121.55 | 121.5898 | 105.0762 | -121.9149
1276.7656 | 121.8475 | -121.463 | 0.12817 | 1.4211e-13 | -0.025814 | -0.00065809 | 0.059731 | -0.0070638 | 0.058046 | -0.22823 | -0.0035378 | -0.0034569 | 0.059569 | 0.026705 | 0.057772 | -120.7173 | -28.3493 | -121.1177 | 0.07502 | 0.023254 | 0.068708 | -121.4961 | -121.0646 | -16.4097 | -121.177 | 0.070773 | 0.086964 | 0.12679 | -121.7638 | -0.033123 | -0.053154 | 0.74571 | 0.34535 | 0.37847 | -0.10492 | -0.059466 | -0.30078 | -0.057401 | 0.39839 | 0.28605 | 0.58683 | -0.04121 | -0.00138 | 121.538 | 121.4863 | 121.5317 | 93.1137 | -121.6243 | 121.5338 | 121.55 | 121.5898 | 105.0533 | -121.892
1278.4375 | 121.6965 | -121.4905 | 0.19684 | 1.4211e-13 | -0.0256 | -0.00087189 | 0.059945 | -0.0070638 | 0.058259 | -0.2206 | -0.0037514 | -0.0032433 | 0.06021 | 0.026491 | 0.057772 | -120.6624 | -28.363 | -121.0719 | 0.11622 | 0.064464 | 0.10992 | -121.5053 | -121.0051 | -16.4235 | -121.1129 | 0.12571 | 0.11901 | 0.18174 | -121.7134 | -0.014815 | -0.080613 | 0.82811 | 0.4186 | 0.43341 | -0.13237 | -0.086922 | -0.22295 | -0.071124 | 0.48538 | 0.37762 | 0.60057 | -0.077824 | -0.0151 | 121.6067 | 121.5549 | 121.6004 | 93.1274 | -121.7021 | 121.6162 | 121.6095 | 121.6722 | 105.067 | -121.9103
1280.1719 | 121.5591 | -121.3074 | 0.11444 | 1.4211e-13 | -0.026455 | -0.00023069 | 0.059731 | -0.0066364 | 0.057618 | -0.22823 | -0.0035378 | -0.0032433 | 0.059569 | 0.026705 | 0.057131 | -119.2476 | -27.7129 | -119.6526 | 1.2562 | 1.1634 | 1.2134 | -120.0355 | -119.5994 | -16.1625 | -119.6706 | 1.2154 | 1.2179 | 1.2623 | -120.2482 | 1.2719 | 1.1418 | 2.0597 | 1.6548 | 0.38284 | 1.049 | 1.0989 | 1.0592 | 1.101 | 1.7079 | 1.6368 | 0.57764 | 1.1034 | 1.1478 | 122.5636 | 122.4708 | 122.5207 | 93.5945 | -120.1499 | 122.5228 | 122.5253 | 122.5697 | 105.1449 | -120.3627
1281.9062 | 121.6873 | -121.5317 | 0.11444 | 1.4211e-13 | -0.026455 | -0.00065809 | 0.060372 | -0.0066364 | 0.058259 | -0.2206 | -0.0033242 | -0.0032433 | 0.059997 | 0.026277 | 0.057558 | -120.7356 | -28.4226 | -121.1497 | 0.010922 | -0.040851 | -0.004549 | -121.5831 | -121.0829 | -16.5105 | -121.1953 | 0.020409 | 0.022864 | 0.067272 | -121.7913 | -0.051459 | -0.10352 | 0.79606 | 0.38197 | 0.43342 | -0.15529 | -0.11899 | -0.25959 | -0.094032 | 0.44874 | 0.3364 | 0.59599 | -0.091577 | -0.047169 | 121.5426 | 121.4908 | 121.5271 | 93.1091 | -121.6976 | 121.5521 | 121.5545 | 121.5989 | 105.0212 | -121.9057
1283.5781 | 121.7239 | -121.55 | 0.13733 | 1.4211e-13 | -0.026241 | -0.00044449 | 0.059945 | -0.0070638 | 0.058259 | -0.22823 | -0.0035378 | -0.0034569 | 0.059997 | 0.026277 | 0.057345 | -120.7585 | -28.4409 | -121.1772 | 0.015501 | -0.036272 | 0.004608 | -121.6015 | -121.115 | -16.5608 | -121.2182 | 0.006674 | 0.013707 | 0.071851 | -121.8187 | -0.051463 | -0.12183 | 0.79148 | 0.37281 | 0.42427 | -0.1736 | -0.13272 | -0.26875 | -0.13065 | 0.435 | 0.33182 | 0.60057 | -0.12362 | -0.065478 | 121.5655 | 121.5137 | 121.5546 | 93.1091 | -121.7388 | 121.5567 | 121.5637 | 121.6218 | 104.9892 | -121.9561
1285.3125 | 121.7285 | -121.5729 | 0.11902 | 1.4211e-13 | -0.026455 | -0.00065809 | 0.060158 | -0.0066364 | 0.058046 | -0.2206 | -0.003965 | -0.0034569 | 0.059997 | 0.026705 | 0.057558 | -120.7768 | -28.3997 | -121.1863 | 0.015501 | -0.031693 | -0.009128 | -121.6243 | -121.1196 | -16.6112 | -121.2365 | 0.034145 | 0.022864 | 0.067272 | -121.8279 | -0.05147 | -0.10352 | 0.79605 | 0.38654 | 0.43801 | -0.15071 | -0.12815 | -0.25502 | -0.084874 | 0.45331 | 0.33639 | 0.59141 | -0.096155 | -0.051747 | 121.5884 | 121.5412 | 121.5637 | 93.1732 | -121.7434 | 121.607 | 121.5957 | 121.6401 | 104.9617 | -121.9469
1287.0469 | 121.8796 | -121.5317 | 0.086975 | 1.4211e-13 | -0.026241 | -0.00065809 | 0.060586 | -0.0070638 | 0.058259 | -0.22823 | -0.0035378 | -0.0030297 | 0.06021 | 0.026918 | 0.057345 | -120.7906 | -28.4271 | -121.2047 | 0.020079 | -0.036272 | -0.004549 | -121.5694 | -121.1241 | -16.6478 | -121.2411 | 0.015831 | 0.013707 | 0.07643 | -121.8462 | -0.037722 | -0.066896 | 0.74112 | 0.32703 | 0.36475 | -0.12325 | -0.091524 | -0.31454 | -0.071144 | 0.40753 | 0.29061 | 0.60515 | -0.073268 | -0.010545 | 121.5518 | 121.4954 | 121.5271 | 93.1045 | -121.6564 | 121.5475 | 121.5454 | 121.6081 | 104.8838 | -121.9332
1288.7969 | 121.8246 | -121.5775 | 0.091553 | 1.4211e-13 | -0.026455 | -0.00044449 | 0.060158 | -0.0070638 | 0.058046 | -0.22823 | -0.0037514 | -0.0030297 | 0.059997 | 0.026918 | 0.057345 | -120.7951 | -28.4683 | -121.2184 | 0.020079 | -0.031693 | 2.9e-05 | -121.5786 | -121.1425 | -16.6707 | -121.2548 | 0.020409 | 0.018285 | 0.071851 | -121.8508 | -0.001103 | -0.071474 | 0.78232 | 0.35907 | 0.36017 | -0.12325 | -0.091524 | -0.27334 | -0.071144 | 0.435 | 0.32265 | 0.59599 | -0.073268 | -0.019702 | 121.5975 | 121.5458 | 121.5775 | 93.1091 | -121.6701 | 121.5979 | 121.5957 | 121.6493 | 104.9067 | -121.9423
1290.4688 | 121.8018 | -121.5775 | 0.10529 | 1.4211e-13 | -0.026455 | -0.00065809 | 0.060158 | -0.00685 | 0.058473 | -0.22823 | -0.003965 | -0.0032433 | 0.059997 | 0.026705 | 0.057345 | -120.8135 | -28.45 | -121.223 | 0.010922 | -0.031693 | 0.004608 | -121.5831 | -121.1425 | -16.7257 | -121.2594 | 0.015831 | 0.013707 | 0.071851 | -121.86 | -0.005682 | -0.094364 | 0.764 | 0.35449 | 0.36017 | -0.13698 | -0.10068 | -0.2825 | -0.089455 | 0.435 | 0.31807 | 0.60057 | -0.091579 | -0.033435 | 121.5884 | 121.5458 | 121.5821 | 93.1274 | -121.6884 | 121.5933 | 121.5912 | 121.6493 | 104.8518 | -121.9652
1292.2031 | 121.8201 | -121.5866 | 0.10529 | 1.4211e-13 | -0.026455 | -1.7092e-05 | 0.060158 | -0.0072774 | 0.058046 | -0.23586 | -0.0037514 | -0.0034569 | 0.059997 | 0.026918 | 0.057345 | -120.8135 | -28.4317 | -121.2275 | 0.010922 | -0.027115 | -0.004549 | -121.5923 | -121.147 | -16.7577 | -121.2685 | 0.020409 | 0.018285 | 0.071851 | -121.8691 | -0.005685 | -0.094364 | 0.77316 | 0.35907 | 0.36475 | -0.1324 | -0.10984 | -0.2825 | -0.084877 | 0.43957 | 0.31807 | 0.60057 | -0.087001 | -0.033435 | 121.5975 | 121.5595 | 121.5821 | 93.1549 | -121.6976 | 121.607 | 121.6049 | 121.6585 | 104.8289 | -121.9744
1293.9375 | 121.9116 | -121.5637 | 0.09613 | 1.4211e-13 | -0.026455 | -0.00044449 | 0.059945 | -0.00685 | 0.058259 | -0.2206 | -0.0033242 | -0.0034569 | 0.059997 | 0.026918 | 0.057345 | -120.8135 | -28.4729 | -121.2275 | 0.020079 | -0.031693 | 2.9e-05 | -121.6015 | -121.1654 | -16.7669 | -121.2731 | 0.015831 | 0.018285 | 0.071851 | -121.8783 | -0.03773 | -0.076051 | 0.75027 | 0.33618 | 0.37391 | -0.12782 | -0.096101 | -0.31455 | -0.080299 | 0.39837 | 0.2906 | 0.60515 | -0.077845 | -0.024279 | 121.5838 | 121.532 | 121.5637 | 93.0908 | -121.6976 | 121.5796 | 121.582 | 121.6356 | 104.7968 | -121.9744
1295.6875 | 121.8842 | -121.5866 | 0.09613 | 1.4211e-13 | -0.026241 | -0.00065809 | 0.060372 | -0.00685 | 0.058259 | -0.2206 | -0.003965 | -0.0034569 | 0.059783 | 0.026064 | 0.057345 | -120.8272 | -28.505 | -121.2413 | 0.010922 | -0.031693 | 0.004608 | -121.6106 | -121.1654 | -16.7989 | -121.2777 | 0.020409 | 0.013707 | 0.081008 | -121.8874 | -0.024 | -0.085208 | 0.75942 | 0.34533 | 0.36933 | -0.12782 | -0.091522 | -0.30082 | -0.075721 | 0.42126 | 0.30891 | 0.60973 | -0.082423 | -0.015122 | 121.5975 | 121.5549 | 121.5912 | 93.0816 | -121.7067 | 121.607 | 121.6003 | 121.6676 | 104.7877 | -121.9836
1297.375 | 121.9116 | -121.582 | 0.082397 | 1.4211e-13 | -0.026455 | -0.00065809 | 0.059731 | -0.0072774 | 0.058046 | -0.22823 | -0.003965 | -0.0034569 | 0.059783 | 0.026705 | 0.057345 | -120.8272 | -28.5508 | -121.2459 | 0.015501 | -0.031693 | 2.9e-05 | -121.6152 | -121.1745 | -16.8356 | -121.2914 | 0.024988 | 0.018285 | 0.071851 | -121.8966 | -0.033157 | -0.066896 | 0.75485 | 0.33617 | 0.36933 | -0.11409 | -0.082368 | -0.31455 | -0.057409 | 0.40752 | 0.2906 | 0.60515 | -0.064112 | -0.010546 | 121.5975 | 121.5503 | 121.5821 | 93.0313 | -121.6976 | 121.607 | 121.6003 | 121.6539 | 104.7465 | -121.979
1299.125 | 121.9116 | -121.5866 | 0.082397 | 1.4211e-13 | -0.026241 | -0.00044449 | 0.060158 | -0.00685 | 0.058259 | -0.23586 | -0.0037514 | -0.0034569 | 0.059783 | 0.026918 | 0.057558 | -120.8363 | -28.5599 | -121.255 | 0.020079 | -0.031693 | 0.004608 | -121.6152 | -121.1745 | -16.8951 | -121.2869 | 0.020409 | 0.022864 | 0.07643 | -121.892 | -0.028579 | -0.062318 | 0.75027 | 0.3316 | 0.36017 | -0.11409 | -0.077789 | -0.3054 | -0.061988 | 0.4121 | 0.29976 | 0.60515 | -0.059533 | -0.005967 | 121.6067 | 121.5549 | 121.5912 | 93.0267 | -121.6976 | 121.607 | 121.6095 | 121.663 | 104.6915 | -121.9744
1300.875 | 121.8704 | -121.6003 | 0.082397 | 1.4211e-13 | -0.026669 | -0.00044449 | 0.059945 | -0.00685 | 0.058046 | -0.22823 | -0.0035378 | -0.0034569 | 0.059569 | 0.026705 | 0.057345 | -120.8363 | -28.5645 | -121.255 | 0.015501 | -0.031693 | -0.004549 | -121.6198 | -121.1837 | -16.9226 | -121.2914 | 0.020409 | 0.013707 | 0.071851 | -121.8966 | -0.019425 | -0.066896 | 0.764 | 0.34533 | 0.36475 | -0.11409 | -0.086946 | -0.29624 | -0.061988 | 0.41668 | 0.30891 | 0.60515 | -0.06869 | -0.010546 | 121.6158 | 121.5686 | 121.5958 | 93.0358 | -121.7022 | 121.6208 | 121.614 | 121.6722 | 104.6778 | -121.979
1302.5625 | 121.9162 | -121.5958 | 0.091553 | 1.4211e-13 | -0.026669 | -0.00044449 | 0.059945 | -0.00685 | 0.058259 | -0.24349 | -0.0037514 | -0.0034569 | 0.06021 | 0.026918 | 0.056917 | -120.8455 | -28.5737 | -121.2642 | 0.015501 | -0.036272 | 0.004608 | -121.6243 | -121.1882 | -16.9729 | -121.3006 | 0.015831 | 0.022864 | 0.07643 | -121.9057 | -0.028582 | -0.076052 | 0.75026 | 0.3316 | 0.36018 | -0.12782 | -0.086945 | -0.30998 | -0.075722 | 0.40752 | 0.29518 | 0.60515 | -0.068689 | -0.015123 | 121.6113 | 121.5595 | 121.6004 | 93.0221 | -121.7159 | 121.6116 | 121.6186 | 121.6722 | 104.6228 | -121.9973
1304.2969 | 121.8246 | -121.6187 | 0.10071 | 1.4211e-13 | -0.026669 | -0.00065809 | 0.059945 | -0.0070638 | 0.058046 | -0.22823 | -0.003965 | -0.0032433 | 0.059783 | 0.026918 | 0.057345 | -120.8455 | -28.5599 | -121.2596 | 0.015501 | -0.022536 | 2.9e-05 | -121.6335 | -121.1837 | -17.0141 | -121.3006 | 0.015831 | 0.018285 | 0.07643 | -121.9103 | -0.014852 | -0.085207 | 0.77315 | 0.35906 | 0.37391 | -0.12324 | -0.10068 | -0.29167 | -0.084877 | 0.43499 | 0.31806 | 0.60973 | -0.082423 | -0.024278 | 121.6342 | 121.5961 | 121.6187 | 93.0587 | -121.7342 | 121.6345 | 121.6369 | 121.6951 | 104.6045 | -122.011
1305.9688 | 121.8979 | -121.6187 | 0.10986 | 1.4211e-13 | -0.026669 | -0.00087189 | 0.059945 | -0.00685 | 0.058259 | -0.22823 | -0.003965 | -0.0032433 | 0.059997 | 0.026705 | 0.057131 | -120.8547 | -28.592 | -121.2642 | 0.015501 | -0.036272 | 2.9e-05 | -121.6335 | -121.1882 | -17.0737 | -121.3052 | 0.024988 | 0.013707 | 0.067272 | -121.9057 | -0.014852 | -0.094362 | 0.76399 | 0.35448 | 0.36934 | -0.14614 | -0.10983 | -0.28709 | -0.084875 | 0.43041 | 0.31349 | 0.60057 | -0.096156 | -0.042591 | 121.6342 | 121.5824 | 121.6187 | 93.0267 | -121.7434 | 121.6436 | 121.6324 | 121.6859 | 104.545 | -122.0156
1307.6562 | 121.8155 | -121.6644 | 0.11902 | 1.4211e-13 | -0.026882 | -0.00044449 | 0.059945 | -0.0070638 | 0.058046 | -0.23586 | -0.003965 | -0.0032433 | 0.059783 | 0.026705 | 0.057131 | -120.8592 | -28.5691 | -121.2779 | 0.010922 | -0.036272 | 0.004608 | -121.6427 | -121.1974 | -17.124 | -121.3006 | 0.024988 | 0.018285 | 0.067272 | -121.9195 | 0.021767 | -0.1081 | 0.80519 | 0.38652 | 0.36476 | -0.15529 | -0.11441 | -0.25505 | -0.094031 | 0.46703 | 0.36384 | 0.61889 | -0.10073 | -0.051747 | 121.6754 | 121.6282 | 121.669 | 93.0954 | -121.7617 | 121.6894 | 121.6827 | 121.7317 | 104.5404 | -122.0385
1309.3906 | 121.9208 | -121.6187 | 0.091553 | 1.4211e-13 | -0.027096 | -0.00065809 | 0.059731 | -0.0066364 | 0.058046 | -0.22823 | -0.003965 | -0.0032433 | 0.059783 | 0.026705 | 0.057345 | -120.8592 | -28.6103 | -121.2779 | 0.010922 | -0.040851 | 0.004608 | -121.6427 | -121.1928 | -17.1606 | -121.3097 | 0.011252 | 0.018285 | 0.067272 | -121.9195 | -0.02401 | -0.080631 | 0.75942 | 0.34075 | 0.36476 | -0.1324 | -0.086945 | -0.30083 | -0.080301 | 0.42583 | 0.30891 | 0.60973 | -0.073268 | -0.024281 | 121.6296 | 121.5778 | 121.6233 | 93.0084 | -121.7342 | 121.6299 | 121.6369 | 121.6859 | 104.458 | -122.011
1311.125 | 121.843 | -121.6553 | 0.11902 | 1.4211e-13 | -0.026669 | -0.00065809 | 0.059945 | -0.0066364 | 0.058046 | -0.24349 | -0.0041788 | -0.0034569 | 0.059997 | 0.026491 | 0.057345 | -120.8638 | -28.6057 | -121.2779 | 0.015501 | -0.027115 | 2.9e-05 | -121.6427 | -121.1928 | -17.2293 | -121.3189 | 0.024988 | 0.027442 | 0.07643 | -121.9241 | 0.012611 | -0.10352 | 0.79146 | 0.37737 | 0.36476 | -0.14613 | -0.11899 | -0.26878 | -0.094031 | 0.46245 | 0.33637 | 0.60515 | -0.091577 | -0.042589 | 121.6708 | 121.6282 | 121.6553 | 93.0496 | -121.7617 | 121.6803 | 121.6827 | 121.7317 | 104.4259 | -122.0431
1312.8594 | 121.8201 | -121.6461 | 0.10986 | 1.4211e-13 | -0.026669 | -0.00065809 | 0.059945 | -0.0070638 | 0.058473 | -0.22823 | -0.003965 | -0.0036707 | 0.059783 | 0.027132 | 0.057345 | -120.8638 | -28.6103 | -121.2733 | 0.020079 | -0.031693 | 0.004608 | -121.6518 | -121.1928 | -17.2751 | -121.3143 | 0.011252 | 0.018285 | 0.071851 | -121.9241 | -0.005702 | -0.089784 | 0.7823 | 0.37279 | 0.37849 | -0.14156 | -0.10526 | -0.27794 | -0.098611 | 0.45329 | 0.33179 | 0.60973 | -0.091578 | -0.038012 | 121.6662 | 121.6144 | 121.6507 | 93.0358 | -121.7617 | 121.6574 | 121.6644 | 121.718 | 104.371 | -122.0339
1314.5938 | 121.8613 | -121.669 | 0.11902 | 1.4211e-13 | -0.026455 | -0.00044449 | 0.059731 | -0.00685 | 0.058046 | -0.22823 | -0.003965 | -0.0030297 | 0.059783 | 0.026705 | 0.057558 | -120.873 | -28.6469 | -121.2825 | 0.015501 | -0.031693 | 2.9e-05 | -121.6472 | -121.1974 | -17.3392 | -121.3189 | 0.020409 | 0.022864 | 0.07643 | -121.9241 | 0.021765 | -0.10352 | 0.79604 | 0.38652 | 0.36476 | -0.15071 | -0.11899 | -0.25505 | -0.09861 | 0.4716 | 0.3501 | 0.60515 | -0.096155 | -0.042589 | 121.6845 | 121.6373 | 121.669 | 93.0221 | -121.7663 | 121.6894 | 121.6919 | 121.7454 | 104.3298 | -122.0431
1316.3281 | 121.8384 | -121.6736 | 0.09613 | 1.4211e-13 | -0.026882 | -0.00065809 | 0.060158 | -0.00685 | 0.058046 | -0.22823 | -0.003965 | -0.0030297 | 0.059569 | 0.026705 | 0.057558 | -120.8684 | -28.6652 | -121.2779 | 0.015501 | -0.031693 | 2.9e-05 | -121.6472 | -121.1974 | -17.3942 | -121.3189 | 0.020409 | 0.018285 | 0.07643 | -121.9286 | 0.026343 | -0.080629 | 0.80519 | 0.39568 | 0.36934 | -0.12782 | -0.096101 | -0.25505 | -0.075721 | 0.47618 | 0.35468 | 0.60973 | -0.077845 | -0.0197 | 121.6891 | 121.6419 | 121.6736 | 93.0084 | -121.7434 | 121.694 | 121.6919 | 121.75 | 104.2794 | -122.0248
1318 | 121.9437 | -121.6324 | 0.07782 | 1.4211e-13 | -0.026882 | -0.00044449 | 0.059945 | -0.00685 | 0.058259 | -0.22823 | -0.003965 | -0.0034569 | 0.059997 | 0.027132 | 0.057131 | -120.8684 | -28.6744 | -121.2916 | 0.010922 | -0.036272 | 0.004608 | -121.6564 | -121.202 | -17.4399 | -121.3189 | 0.020409 | 0.018285 | 0.081008 | -121.9332 | -0.024013 | -0.066898 | 0.76399 | 0.34075 | 0.36476 | -0.11409 | -0.073212 | -0.30083 | -0.057411 | 0.4304 | 0.31348 | 0.61431 | -0.059535 | 0.003188 | 121.6433 | 121.5961 | 121.637 | 92.958 | -121.7342 | 121.6528 | 121.6507 | 121.7134 | 104.1924 | -122.011
1319.75 | 121.9803 | -121.6324 | 0.082397 | 1.4211e-13 | -0.027096 | -0.00065809 | 0.060372 | -0.00685 | 0.058473 | -0.22823 | -0.0037514 | -0.0034569 | 0.059997 | 0.027132 | 0.057558 | -120.873 | -28.6927 | -121.2916 | 0.015501 | -0.031693 | 0.004608 | -121.6564 | -121.202 | -17.4949 | -121.3189 | 0.015831 | 0.013707 | 0.071851 | -121.9286 | -0.024013 | -0.066896 | 0.75942 | 0.34075 | 0.36476 | -0.11409 | -0.077789 | -0.29625 | -0.066566 | 0.4304 | 0.31348 | 0.60973 | -0.06869 | -0.010546 | 121.6479 | 121.6007 | 121.637 | 92.9397 | -121.7388 | 121.6482 | 121.6461 | 121.7042 | 104.1375 | -122.011
1321.5 | 121.8475 | -121.6599 | 0.10986 | 1.4211e-13 | -0.026669 | -0.00065809 | 0.059731 | -0.0070638 | 0.058473 | -0.23586 | -0.003965 | -0.0034569 | 0.059783 | 0.027132 | 0.057558 | -120.873 | -28.7156 | -121.2962 | 0.015501 | -0.027115 | 0.009187 | -121.661 | -121.202 | -17.6002 | -121.3235 | 0.020409 | 0.013707 | 0.071851 | -121.9332 | -0.001126 | -0.094362 | 0.78688 | 0.36363 | 0.36476 | -0.13698 | -0.10068 | -0.27336 | -0.089454 | 0.45787 | 0.33637 | 0.60973 | -0.096156 | -0.038012 | 121.6754 | 121.6327 | 121.669 | 92.9443 | -121.7708 | 121.6803 | 121.6736 | 121.7317 | 104.0596 | -122.0431
1323.1875 | 121.9757 | -121.6278 | 0.09613 | 1.4211e-13 | -0.027096 | -0.00044449 | 0.059731 | -0.00685 | 0.058259 | -0.22823 | -0.0041788 | -0.0032433 | 0.06021 | 0.027132 | 0.056917 | -120.873 | -28.7522 | -121.3008 | 0.015501 | -0.031693 | 2.9e-05 | -121.661 | -121.202 | -17.6872 | -121.3326 | 0.011252 | 0.022864 | 0.071851 | -121.9424 | -0.033169 | -0.080629 | 0.75484 | 0.32701 | 0.36018 | -0.12782 | -0.096101 | -0.31456 | -0.084878 | 0.42583 | 0.29517 | 0.60973 | -0.073266 | -0.024279 | 121.6433 | 121.5961 | 121.6278 | 92.8756 | -121.7571 | 121.6391 | 121.6507 | 121.6997 | 103.9406 | -122.0385
1324.9375 | 121.9162 | -121.6507 | 0.091553 | 1.4211e-13 | -0.026882 | -0.00044449 | 0.060158 | -0.00685 | 0.058473 | -0.23586 | -0.0037514 | -0.0034569 | 0.06021 | 0.027346 | 0.057558 | -120.8775 | -28.7568 | -121.3054 | 0.015501 | -0.031693 | 0.009187 | -121.6564 | -121.1974 | -17.765 | -121.3235 | 0.020409 | 0.022864 | 0.07643 | -121.9424 | -0.005702 | -0.076052 | 0.77315 | 0.34532 | 0.35102 | -0.12325 | -0.082366 | -0.29167 | -0.071144 | 0.45329 | 0.32721 | 0.61889 | -0.068689 | -0.015123 | 121.6662 | 121.619 | 121.6599 | 92.8939 | -121.748 | 121.6711 | 121.6736 | 121.7271 | 103.8857 | -122.0339
1326.6875 | 121.8384 | -121.6965 | 0.1236 | 1.4211e-13 | -0.026882 | -0.0010855 | 0.060158 | -0.0070638 | 0.058473 | -0.22823 | -0.003965 | -0.0032433 | 0.059569 | 0.027132 | 0.056917 | -120.8821 | -28.7431 | -121.31 | 0.010922 | -0.036272 | 0.004608 | -121.6656 | -121.2111 | -17.8383 | -121.3235 | 0.015831 | 0.018285 | 0.071851 | -121.9515 | 0.030916 | -0.11267 | 0.81435 | 0.38652 | 0.3556 | -0.15987 | -0.11899 | -0.25506 | -0.10776 | 0.48533 | 0.37299 | 0.62805 | -0.10531 | -0.051745 | 121.7074 | 121.6602 | 121.7011 | 92.9534 | -121.7892 | 121.7123 | 121.7148 | 121.7683 | 103.8582 | -122.0751
1328.3594 | 121.8613 | -121.6827 | 0.11902 | 1.4211e-13 | -0.026882 | -0.0010855 | 0.059945 | -0.0070638 | 0.058473 | -0.2206 | -0.003965 | -0.0032433 | 0.059783 | 0.026918 | 0.057131 | -120.8775 | -28.7614 | -121.3145 | 0.020079 | -0.022536 | 0.004608 | -121.6701 | -121.2066 | -17.9161 | -121.3281 | 0.020409 | 0.027442 | 0.067272 | -121.9424 | 0.012604 | -0.09894 | 0.80519 | 0.36821 | 0.3556 | -0.14155 | -0.11441 | -0.25963 | -0.09861 | 0.47618 | 0.35468 | 0.61431 | -0.091577 | -0.051747 | 121.7028 | 121.6602 | 121.6873 | 92.9214 | -121.7892 | 121.7031 | 121.7102 | 121.75 | 103.7666 | -122.0614
1330.0938 | 121.8796 | -121.6827 | 0.13275 | 1.4211e-13 | -0.02731 | -0.00065809 | 0.059945 | -0.0070638 | 0.058473 | -0.24349 | -0.0035378 | -0.0032433 | 0.059783 | 0.027132 | 0.057131 | -120.8867 | -28.7797 | -121.3145 | 0.015501 | -0.031693 | 0.004608 | -121.6656 | -121.2066 | -17.9848 | -121.3235 | 0.024988 | 0.018285 | 0.071851 | -121.9515 | 0.017183 | -0.11725 | 0.79603 | 0.36821 | 0.35102 | -0.16444 | -0.12814 | -0.26879 | -0.10776 | 0.47618 | 0.35926 | 0.62805 | -0.11447 | -0.0609 | 121.6982 | 121.651 | 121.6873 | 92.903 | -121.7983 | 121.7077 | 121.701 | 121.7546 | 103.6979 | -122.0843
1331.7812 | 121.8567 | -121.7056 | 0.10986 | 1.4211e-13 | -0.027096 | -0.00065809 | 0.059945 | -0.0070638 | 0.058259 | -0.23586 | -0.0041788 | -0.0032433 | 0.059997 | 0.026918 | 0.057772 | -120.8867 | -28.7751 | -121.3191 | 0.015501 | -0.031693 | 0.004608 | -121.6701 | -121.2066 | -18.1084 | -121.3235 | 0.015831 | 0.027442 | 0.07643 | -121.9561 | 0.035492 | -0.094362 | 0.81892 | 0.38652 | 0.35103 | -0.14156 | -0.10526 | -0.25048 | -0.094032 | 0.49907 | 0.38215 | 0.63263 | -0.082421 | -0.033433 | 121.7211 | 121.6739 | 121.7102 | 92.9305 | -121.78 | 121.7215 | 121.7331 | 121.7821 | 103.5972 | -122.066
1333.5156 | 121.8384 | -121.701 | 0.10071 | 1.4211e-13 | -0.027096 | -0.00087189 | 0.059731 | -0.0070638 | 0.058259 | -0.22823 | -0.0037514 | -0.0030297 | 0.059997 | 0.027132 | 0.057345 | -120.8913 | -28.7843 | -121.3191 | 0.024657 | -0.027115 | 0.009187 | -121.6793 | -121.202 | -18.2092 | -121.3326 | 0.024988 | 0.022864 | 0.062694 | -121.947 | 0.021757 | -0.076051 | 0.80977 | 0.38194 | 0.36018 | -0.12782 | -0.091521 | -0.2459 | -0.07572 | 0.49907 | 0.36841 | 0.61431 | -0.077844 | -0.038014 | 121.7257 | 121.6739 | 121.7102 | 92.9168 | -121.78 | 121.726 | 121.7239 | 121.7637 | 103.4919 | -122.0477
1335.25 | 121.8246 | -121.6736 | 0.11902 | 1.4211e-13 | -0.027096 | -0.00065809 | 0.060158 | -0.0070638 | 0.0589 | -0.23586 | -0.0035378 | -0.0032433 | 0.059783 | 0.027346 | 0.057131 | -120.8959 | -28.8026 | -121.3237 | 0.015501 | -0.031693 | 0.004608 | -121.6747 | -121.2111 | -18.2733 | -121.3235 | 0.024988 | 0.022864 | 0.071851 | -121.9515 | -0.00113 | -0.10352 | 0.77772 | 0.3499 | 0.35103 | -0.15071 | -0.11441 | -0.27794 | -0.094031 | 0.46245 | 0.3501 | 0.62805 | -0.096155 | -0.047168 | 121.6891 | 121.6419 | 121.6782 | 92.871 | -121.7937 | 121.6986 | 121.6964 | 121.7454 | 103.4003 | -122.0705
1336.9375 | 121.962 | -121.6553 | 0.068665 | 1.4211e-13 | -0.02731 | -0.00065809 | 0.059731 | -0.0070638 | 0.057832 | -0.22823 | -0.0035378 | -0.0034569 | 0.059783 | 0.027346 | 0.057558 | -120.8913 | -28.8117 | -121.3145 | 0.010922 | -0.031693 | 0.004608 | -121.6793 | -121.2066 | -18.3877 | -121.3235 | 0.015831 | 0.022864 | 0.07643 | -121.9561 | -0.02402 | -0.057743 | 0.76399 | 0.34074 | 0.36476 | -0.10036 | -0.064057 | -0.30083 | -0.052834 | 0.44871 | 0.33179 | 0.63263 | -0.045801 | 0.007765 | 121.6662 | 121.6236 | 121.6599 | 92.8435 | -121.748 | 121.6711 | 121.6781 | 121.7317 | 103.2675 | -122.0248
1338.6719 | 121.8613 | -121.6782 | 0.11444 | 1.4211e-13 | -0.027523 | -0.00087189 | 0.059945 | -0.0077048 | 0.058473 | -0.22823 | -0.0035378 | -0.0032433 | 0.059997 | 0.027132 | 0.056917 | -120.8867 | -28.8713 | -121.3237 | 0.015501 | -0.022536 | 0.004608 | -121.6793 | -121.2111 | -18.4885 | -121.3372 | 0.024988 | 0.018285 | 0.07643 | -121.9561 | -0.001131 | -0.09894 | 0.79146 | 0.35447 | 0.35561 | -0.13698 | -0.10983 | -0.27795 | -0.089453 | 0.46702 | 0.34094 | 0.61889 | -0.096156 | -0.038011 | 121.6937 | 121.6556 | 121.6828 | 92.8069 | -121.7937 | 121.7031 | 121.6964 | 121.7546 | 103.1897 | -122.0705
1340.4062 | 121.9574 | -121.6324 | 0.086975 | 1.4211e-13 | -0.02731 | -0.00065809 | 0.059945 | -0.007491 | 0.058046 | -0.23586 | -0.0037514 | -0.0032433 | 0.059569 | 0.02756 | 0.057345 | -120.8913 | -28.8621 | -121.3237 | 0.010922 | -0.036272 | 0.004608 | -121.6793 | -121.2066 | -18.5572 | -121.3418 | 0.020409 | 0.032021 | 0.07643 | -121.9515 | -0.046908 | -0.076053 | 0.7411 | 0.3087 | 0.35561 | -0.12325 | -0.082367 | -0.31914 | -0.066566 | 0.42583 | 0.29059 | 0.60973 | -0.054954 | -0.010545 | 121.6433 | 121.5961 | 121.637 | 92.7703 | -121.7663 | 121.6528 | 121.6644 | 121.7088 | 103.0752 | -122.0385
1342.0781 | 121.8521 | -121.6827 | 0.1236 | 1.4211e-13 | -0.027523 | -0.00065809 | 0.059731 | -0.0070638 | 0.058473 | -0.2206 | -0.003965 | -0.0036707 | 0.059783 | 0.027132 | 0.057345 | -120.8959 | -28.9033 | -121.3283 | 0.015501 | -0.031693 | 0.004608 | -121.6839 | -121.2066 | -18.6762 | -121.3372 | 0.024988 | 0.018285 | 0.07643 | -121.9653 | -0.001133 | -0.10809 | 0.78688 | 0.35447 | 0.35561 | -0.15529 | -0.11899 | -0.28253 | -0.098608 | 0.47618 | 0.34552 | 0.62805 | -0.10531 | -0.047166 | 121.6982 | 121.651 | 121.6873 | 92.7794 | -121.8075 | 121.7077 | 121.701 | 121.7592 | 103.0065 | -122.0889
1343.8125 | 121.9849 | -121.6324 | 0.091553 | 1.4211e-13 | -0.027096 | -0.00087189 | 0.059945 | -0.0072774 | 0.058259 | -0.22823 | -0.0041788 | -0.0034569 | 0.059783 | 0.027346 | 0.057558 | -120.8959 | -28.9216 | -121.3237 | 0.010922 | -0.031693 | 0.004608 | -121.6885 | -121.2066 | -18.8044 | -121.3372 | 0.011252 | 0.032021 | 0.071851 | -121.9607 | -0.056066 | -0.080631 | 0.73652 | 0.3087 | 0.36476 | -0.12325 | -0.086945 | -0.3283 | -0.080301 | 0.42583 | 0.29517 | 0.62347 | -0.059532 | -0.019702 | 121.6433 | 121.6007 | 121.637 | 92.7108 | -121.78 | 121.6436 | 121.6644 | 121.7042 | 102.828 | -122.0522
1345.4844 | 121.8475 | -121.6919 | 0.12817 | 1.4211e-13 | -0.027523 | -0.00087189 | 0.060158 | -0.0072774 | 0.058046 | -0.22823 | -0.003965 | -0.0032433 | 0.059783 | 0.02756 | 0.057558 | -120.8913 | -28.9262 | -121.3283 | 0.010922 | -0.027115 | 0.009187 | -121.6839 | -121.2066 | -18.9051 | -121.3326 | 0.020409 | 0.018285 | 0.071851 | -121.9607 | 0.008023 | -0.11725 | 0.80061 | 0.36363 | 0.35561 | -0.15529 | -0.11899 | -0.26879 | -0.10777 | 0.48534 | 0.35926 | 0.62805 | -0.10989 | -0.056323 | 121.7028 | 121.6648 | 121.7011 | 92.7657 | -121.812 | 121.7123 | 121.7102 | 121.7637 | 102.7868 | -122.0889
1347.2188 | 121.9437 | -121.6599 | 0.10986 | 1.4211e-13 | -0.027096 | -0.00065809 | 0.059731 | -0.007491 | 0.058473 | -0.22823 | -0.003965 | -0.0034569 | 0.059997 | 0.027346 | 0.057558 | -120.8959 | -28.9445 | -121.3283 | 0.020079 | -0.027115 | 0.013765 | -121.6839 | -121.2066 | -18.9921 | -121.3372 | 0.020409 | 0.022864 | 0.081008 | -121.9653 | -0.024021 | -0.089784 | 0.76399 | 0.33159 | 0.35561 | -0.13698 | -0.096098 | -0.30541 | -0.089454 | 0.45329 | 0.32263 | 0.62805 | -0.086999 | -0.028855 | 121.6799 | 121.6327 | 121.6736 | 92.7153 | -121.7937 | 121.6803 | 121.6827 | 121.7409 | 102.6677 | -122.0751
1348.9531 | 121.8521 | -121.6873 | 0.11444 | 1.4211e-13 | -0.027096 | -0.00087189 | 0.059731 | -0.007491 | 0.058259 | -0.22823 | -0.003965 | -0.0032433 | 0.059783 | 0.027132 | 0.057345 | -120.8959 | -28.9354 | -121.3283 | 0.015501 | -0.022536 | 0.013765 | -121.6885 | -121.2066 | -19.1249 | -121.3281 | 0.020409 | 0.022864 | 0.071851 | -121.9698 | -0.001134 | -0.09894 | 0.79145 | 0.35905 | 0.36019 | -0.13698 | -0.10068 | -0.28253 | -0.094032 | 0.48076 | 0.35926 | 0.64178 | -0.091577 | -0.04259 | 121.7028 | 121.6648 | 121.7011 | 92.752 | -121.8029 | 121.7077 | 121.7102 | 121.7592 | 102.5624 | -122.0843
1350.6875 | 121.9574 | -121.6553 | 0.091553 | 1.4211e-13 | -0.027096 | -0.0010855 | 0.059945 | -0.0070638 | 0.058259 | -0.24349 | -0.003965 | -0.0032433 | 0.059569 | 0.02756 | 0.057131 | -120.8913 | -28.9262 | -121.3328 | 0.020079 | -0.027115 | 2.9e-05 | -121.6885 | -121.2111 | -19.244 | -121.3372 | 0.020409 | 0.027442 | 0.07643 | -121.9561 | -0.033178 | -0.071474 | 0.76399 | 0.32243 | 0.35561 | -0.11867 | -0.091524 | -0.30083 | -0.071144 | 0.44413 | 0.31806 | 0.61889 | -0.064111 | -0.015123 | 121.6754 | 121.6282 | 121.6553 | 92.7291 | -121.78 | 121.6757 | 121.6827 | 121.7317 | 102.4113 | -122.0477
1352.375 | 121.9711 | -121.6553 | 0.09613 | 1.4211e-13 | -0.027737 | -0.00087189 | 0.059945 | -0.0072774 | 0.058259 | -0.22823 | -0.0037514 | -0.0032433 | 0.059783 | 0.02756 | 0.056917 | -120.905 | -28.9811 | -121.3237 | 0.024657 | -0.027115 | 0.009187 | -121.693 | -121.2066 | -19.3951 | -121.3281 | 0.015831 | 0.022864 | 0.081008 | -121.9698 | -0.037757 | -0.071473 | 0.75025 | 0.33159 | 0.36934 | -0.12324 | -0.086943 | -0.31457 | -0.080299 | 0.44871 | 0.32721 | 0.64178 | -0.073266 | -0.015122 | 121.6799 | 121.6282 | 121.6645 | 92.6741 | -121.7892 | 121.6711 | 121.6781 | 121.7363 | 102.2602 | -122.066
1354.1094 | 122.0032 | -121.6415 | 0.086975 | 1.4211e-13 | -0.027737 | -0.00087189 | 0.059945 | -0.007491 | 0.058046 | -0.23586 | -0.003965 | -0.0030297 | 0.059783 | 0.027346 | 0.057345 | -120.8913 | -29.0132 | -121.3237 | 0.010922 | -0.031693 | 0.004608 | -121.6885 | -121.2157 | -19.4958 | -121.3326 | 0.015831 | 0.022864 | 0.067272 | -121.9744 | -0.04691 | -0.076053 | 0.75026 | 0.31785 | 0.36476 | -0.11867 | -0.082367 | -0.33288 | -0.071144 | 0.42582 | 0.3089 | 0.64178 | -0.064111 | -0.019703 | 121.6525 | 121.6098 | 121.6461 | 92.6283 | -121.7754 | 121.6574 | 121.6644 | 121.7088 | 102.1458 | -122.0614
1355.8438 | 121.9711 | -121.6461 | 0.073242 | 1.4211e-13 | -0.027523 | -0.00065809 | 0.059731 | -0.007491 | 0.058259 | -0.22823 | -0.003965 | -0.0034569 | 0.059569 | 0.027346 | 0.057131 | -120.8959 | -29.0544 | -121.3374 | 0.015501 | -0.027115 | 0.009187 | -121.6885 | -121.1974 | -19.6148 | -121.3326 | 0.015831 | 0.032021 | 0.07643 | -121.9698 | -0.042333 | -0.057741 | 0.75026 | 0.3087 | 0.35103 | -0.10036 | -0.064055 | -0.32373 | -0.057411 | 0.44872 | 0.31348 | 0.6372 | -0.041221 | 0.003188 | 121.6616 | 121.619 | 121.6553 | 92.5917 | -121.7617 | 121.6619 | 121.6781 | 121.7225 | 102.0313 | -122.0431
1357.5156 | 121.8521 | -121.6965 | 0.12817 | 1.4211e-13 | -0.027523 | -0.00065809 | 0.059731 | -0.0070638 | 0.058473 | -0.23586 | -0.0035378 | -0.0030297 | 0.059569 | 0.02756 | 0.057345 | -120.9004 | -29.059 | -121.3328 | 0.015501 | -0.027115 | 0.009187 | -121.693 | -121.202 | -19.7476 | -121.3372 | 0.020409 | 0.022864 | 0.071851 | -121.9653 | 0.003442 | -0.11267 | 0.79603 | 0.36363 | 0.36019 | -0.15529 | -0.11899 | -0.26879 | -0.10777 | 0.49449 | 0.35925 | 0.62805 | -0.10531 | -0.056323 | 121.712 | 121.6694 | 121.7057 | 92.6375 | -121.8212 | 121.7169 | 121.7193 | 121.7683 | 101.9489 | -122.0934
1359.25 | 122.0215 | -121.6507 | 0.068665 | 1.4211e-13 | -0.027737 | -0.00065809 | 0.059517 | -0.0070638 | 0.058046 | -0.22823 | -0.003965 | -0.0032433 | 0.059783 | 0.02756 | 0.057131 | -120.9004 | -29.1093 | -121.3283 | 0.020079 | -0.022536 | 0.004608 | -121.6976 | -121.1928 | -19.8987 | -121.3326 | 0.024988 | 0.027442 | 0.07643 | -121.9698 | -0.046913 | -0.048586 | 0.75025 | 0.32243 | 0.36934 | -0.091201 | -0.064057 | -0.31915 | -0.043677 | 0.45787 | 0.31806 | 0.6372 | -0.041223 | 0.007765 | 121.6708 | 121.6282 | 121.6553 | 92.5413 | -121.7663 | 121.6757 | 121.6781 | 121.7271 | 101.752 | -122.0385
1360.9844 | 121.8658 | -121.7056 | 0.13275 | 1.4211e-13 | -0.027737 | -0.00087189 | 0.059945 | -0.0072774 | 0.058473 | -0.24349 | -0.0035378 | -0.0034569 | 0.059356 | 0.02756 | 0.057345 | -120.905 | -29.1093 | -121.3328 | 0.020079 | -0.031693 | 0.009187 | -121.693 | -121.2066 | -20.0956 | -121.3326 | 0.020409 | 0.032021 | 0.07643 | -121.9744 | 0.012597 | -0.11267 | 0.80061 | 0.37278 | 0.36019 | -0.16444 | -0.12356 | -0.2688 | -0.11234 | 0.49907 | 0.37299 | 0.64178 | -0.10073 | -0.056321 | 121.7257 | 121.6739 | 121.7148 | 92.5963 | -121.8258 | 121.726 | 121.7376 | 121.7821 | 101.61 | -122.1072
1362.7344 | 121.8704 | -121.7056 | 0.10071 | 1.4211e-13 | -0.027737 | -0.00087189 | 0.059517 | -0.0070638 | 0.058259 | -0.22823 | -0.0037514 | -0.0032433 | 0.059997 | 0.027773 | 0.057131 | -120.9096 | -29.1139 | -121.3374 | 0.015501 | -0.022536 | 0.004608 | -121.693 | -121.2066 | -20.2971 | -121.3281 | 0.029566 | 0.022864 | 0.07643 | -121.979 | 0.012597 | -0.085207 | 0.79603 | 0.36821 | 0.35561 | -0.12324 | -0.0961 | -0.27337 | -0.071142 | 0.49907 | 0.37757 | 0.65094 | -0.077844 | -0.024278 | 121.7211 | 121.6831 | 121.7102 | 92.5917 | -121.7937 | 121.7352 | 121.7285 | 121.7821 | 101.4086 | -122.0797
1364.4062 | 121.9894 | -121.6553 | 0.082397 | 1.4211e-13 | -0.02731 | -0.00065809 | 0.059731 | -0.007491 | 0.058046 | -0.23586 | -0.0035378 | -0.0032433 | 0.059569 | 0.027773 | 0.057131 | -120.905 | -29.1185 | -121.3374 | 0.020079 | -0.031693 | 0.009187 | -121.7022 | -121.1928 | -20.4894 | -121.3326 | 0.020409 | 0.022864 | 0.07643 | -121.979 | -0.046915 | -0.062318 | 0.75025 | 0.31785 | 0.36477 | -0.11409 | -0.07321 | -0.32373 | -0.061988 | 0.46245 | 0.32263 | 0.64636 | -0.059533 | -0.005967 | 121.6754 | 121.6236 | 121.6645 | 92.5368 | -121.7846 | 121.6757 | 121.6781 | 121.7317 | 101.1659 | -122.0614
1366.1406 | 122.0032 | -121.6553 | 0.068665 | 1.4211e-13 | -0.027951 | -0.00065809 | 0.059517 | -0.0072774 | 0.058473 | -0.22823 | -0.0035378 | -0.0038843 | 0.059783 | 0.02756 | 0.057131 | -120.905 | -29.1231 | -121.3374 | 0.015501 | -0.027115 | 0.013765 | -121.693 | -121.202 | -20.7 | -121.3281 | 0.020409 | 0.027442 | 0.07643 | -121.979 | -0.037757 | -0.053164 | 0.75025 | 0.31785 | 0.35561 | -0.09578 | -0.0549 | -0.32373 | -0.048256 | 0.45329 | 0.32721 | 0.65094 | -0.041223 | 0.007765 | 121.6708 | 121.6282 | 121.669 | 92.5322 | -121.7617 | 121.6757 | 121.6827 | 121.7317 | 100.9553 | -122.0477
1367.8906 | 121.962 | -121.6553 | 0.086975 | 1.4211e-13 | -0.027951 | -0.00044449 | 0.059731 | -0.0072774 | 0.058046 | -0.2206 | -0.0037514 | -0.0036707 | 0.059783 | 0.027773 | 0.057345 | -120.8959 | -29.1185 | -121.3374 | 0.020079 | -0.031693 | 0.009187 | -121.7022 | -121.2066 | -20.9106 | -121.3326 | 0.020409 | 0.027442 | 0.071851 | -121.9836 | -0.046915 | -0.066896 | 0.75941 | 0.31785 | 0.36477 | -0.11867 | -0.077788 | -0.32831 | -0.066566 | 0.44871 | 0.32263 | 0.65094 | -0.059533 | -0.015124 | 121.6754 | 121.6236 | 121.6645 | 92.5368 | -121.7892 | 121.6757 | 121.6827 | 121.7271 | 100.7447 | -122.0706
1369.5625 | 121.9986 | -121.6507 | 0.091553 | 1.4211e-13 | -0.027737 | -0.00065809 | 0.059731 | -0.007491 | 0.058259 | -0.2206 | -0.0033242 | -0.0032433 | 0.059997 | 0.027773 | 0.057131 | -120.9096 | -29.1506 | -121.3328 | 0.020079 | -0.022536 | 0.004608 | -121.693 | -121.1974 | -21.1167 | -121.3281 | 0.024988 | 0.027442 | 0.081008 | -121.979 | -0.042334 | -0.071474 | 0.7411 | 0.31785 | 0.36019 | -0.11409 | -0.086945 | -0.32831 | -0.066565 | 0.45329 | 0.32264 | 0.65094 | -0.064111 | -0.010545 | 121.6708 | 121.6282 | 121.6553 | 92.5001 | -121.7846 | 121.6757 | 121.6781 | 121.7317 | 100.534 | -122.0706
1371.2969 | 121.8704 | -121.6965 | 0.14191 | 1.4211e-13 | -0.027951 | -0.00087189 | 0.059945 | -0.0072774 | 0.058046 | -0.22823 | -0.0037514 | -0.0028161 | 0.059997 | 0.02756 | 0.057345 | -120.9096 | -29.1506 | -121.3374 | 0.010922 | -0.031693 | 0.009187 | -121.7068 | -121.1974 | -21.3776 | -121.3281 | 0.015831 | 0.032021 | 0.081008 | -121.979 | -0.010295 | -0.13099 | 0.78687 | 0.35905 | 0.36934 | -0.1736 | -0.13272 | -0.28253 | -0.12608 | 0.49907 | 0.36841 | 0.65094 | -0.10989 | -0.060899 | 121.7074 | 121.6648 | 121.7057 | 92.5459 | -121.8487 | 121.7123 | 121.7285 | 121.7775 | 100.3188 | -122.1209
1372.9844 | 122.0078 | -121.6782 | 0.091553 | 1.4211e-13 | -0.027737 | -0.00087189 | 0.059945 | -0.0072774 | 0.058259 | -0.22823 | -0.0033242 | -0.0032433 | 0.059997 | 0.027346 | 0.057558 | -120.905 | -29.178 | -121.3374 | 0.024657 | -0.022536 | 0.013765 | -121.7022 | -121.1882 | -21.6066 | -121.3281 | 0.024988 | 0.032021 | 0.071851 | -121.9882 | -0.024026 | -0.066896 | 0.77314 | 0.34074 | 0.36477 | -0.11409 | -0.077788 | -0.31 | -0.066565 | 0.48992 | 0.3501 | 0.6601 | -0.059532 | -0.019702 | 121.7028 | 121.6556 | 121.6919 | 92.5001 | -121.7937 | 121.7031 | 121.7102 | 121.75 | 100.0716 | -122.0797
1374.7188 | 122.0078 | -121.669 | 0.059509 | 1.4211e-13 | -0.027951 | -0.00087189 | 0.059731 | -0.0072774 | 0.057618 | -0.2206 | -0.0035378 | -0.0032433 | 0.059783 | 0.027773 | 0.057558 | -120.9096 | -29.2147 | -121.3328 | 0.010922 | -0.027115 | 0.009187 | -121.7022 | -121.1974 | -21.8584 | -121.3281 | 0.020409 | 0.032021 | 0.07643 | -121.9882 | -0.033182 | -0.048587 | 0.75941 | 0.33616 | 0.36934 | -0.086624 | -0.050322 | -0.31915 | -0.0391 | 0.4716 | 0.34095 | 0.6601 | -0.027488 | 0.016921 | 121.6799 | 121.6419 | 121.6782 | 92.4543 | -121.7617 | 121.6894 | 121.701 | 121.7454 | 99.8106 | -122.0477
1376.4531 | 121.994 | -121.6599 | 0.068665 | 1.4211e-13 | -0.028164 | -0.00087189 | 0.059945 | -0.007491 | 0.058046 | -0.2206 | -0.0035378 | -0.0030297 | 0.059569 | 0.027773 | 0.057345 | -120.9096 | -29.233 | -121.3374 | 0.020079 | -0.027115 | 0.013765 | -121.7022 | -121.1882 | -22.1011 | -121.3326 | 0.020409 | 0.027442 | 0.071851 | -121.9836 | -0.042337 | -0.048586 | 0.75025 | 0.32243 | 0.36477 | -0.09578 | -0.0549 | -0.32373 | -0.048256 | 0.47161 | 0.32721 | 0.65094 | -0.041223 | 0.003186 | 121.6799 | 121.6327 | 121.6736 | 92.4269 | -121.7709 | 121.6803 | 121.6873 | 121.7317 | 99.5588 | -122.0522
1378.1406 | 121.8567 | -121.7239 | 0.11444 | 1.4211e-13 | -0.027737 | -0.00065809 | 0.059517 | -0.0079184 | 0.058259 | -0.23586 | -0.0035378 | -0.0030297 | 0.059569 | 0.02756 | 0.057131 | -120.9096 | -29.2375 | -121.342 | 0.020079 | -0.031693 | 0.009187 | -121.7159 | -121.1882 | -22.3758 | -121.3143 | 0.020409 | 0.018285 | 0.07643 | -121.9882 | 0.008014 | -0.094362 | 0.81434 | 0.38194 | 0.37392 | -0.14613 | -0.10525 | -0.26422 | -0.094032 | 0.53569 | 0.40961 | 0.67383 | -0.096156 | -0.038011 | 121.744 | 121.6922 | 121.7331 | 92.4864 | -121.8304 | 121.7443 | 121.7422 | 121.8004 | 99.3481 | -122.1026
1379.875 | 121.9986 | -121.6599 | 0.086975 | 1.4211e-13 | -0.028164 | -0.00065809 | 0.059731 | -0.007491 | 0.058259 | -0.22823 | -0.003965 | -0.0032433 | 0.059997 | 0.027987 | 0.057345 | -120.9096 | -29.265 | -121.3466 | 0.010922 | -0.027115 | 0.018344 | -121.7022 | -121.1882 | -22.6734 | -121.3189 | 0.015831 | 0.027442 | 0.071851 | -121.9882 | -0.042337 | -0.076053 | 0.75025 | 0.31327 | 0.35561 | -0.11409 | -0.068631 | -0.32831 | -0.071144 | 0.47161 | 0.34095 | 0.66926 | -0.059533 | -0.015124 | 121.6708 | 121.6327 | 121.6782 | 92.3948 | -121.7892 | 121.6757 | 121.6873 | 121.7317 | 98.9864 | -122.0751
1381.5625 | 121.8842 | -121.7194 | 0.10529 | 1.4211e-13 | -0.028378 | -0.0010855 | 0.059731 | -0.0077048 | 0.058046 | -0.22823 | -0.0035378 | -0.0034569 | 0.059997 | 0.027987 | 0.057131 | -120.9142 | -29.2375 | -121.3374 | 0.015501 | -0.031693 | 0.013765 | -121.7068 | -121.1837 | -22.9848 | -121.3189 | 0.024988 | 0.032021 | 0.081008 | -121.9927 | 0.012593 | -0.089785 | 0.80518 | 0.38194 | 0.36934 | -0.13698 | -0.091521 | -0.27338 | -0.080298 | 0.53569 | 0.40046 | 0.67383 | -0.073265 | -0.024278 | 121.7349 | 121.6877 | 121.7331 | 92.4818 | -121.8121 | 121.7443 | 121.7514 | 121.8004 | 98.7346 | -122.098
1383.3125 | 122.0215 | -121.6736 | 0.082397 | 1.4211e-13 | -0.027951 | -0.00065809 | 0.059731 | -0.0072774 | 0.058259 | -0.23586 | -0.003965 | -0.0032433 | 0.059783 | 0.028201 | 0.056917 | -120.9096 | -29.2742 | -121.3374 | 0.010922 | -0.022536 | 0.013765 | -121.7068 | -121.1791 | -23.3099 | -121.3189 | 0.020409 | 0.022864 | 0.081008 | -121.9882 | -0.033183 | -0.071475 | 0.76399 | 0.33616 | 0.36934 | -0.10493 | -0.068632 | -0.31457 | -0.061988 | 0.4945 | 0.35468 | 0.66926 | -0.059533 | -0.001389 | 121.6845 | 121.651 | 121.6873 | 92.3994 | -121.7892 | 121.694 | 121.6964 | 121.7546 | 98.3637 | -122.0706
1385.0469 | 121.9986 | -121.669 | 0.059509 | 1.4211e-13 | -0.028378 | -0.00087189 | 0.059945 | -0.0077048 | 0.058046 | -0.22823 | -0.0035378 | -0.0034569 | 0.059783 | 0.027773 | 0.057345 | -120.9142 | -29.3108 | -121.3374 | 0.020079 | -0.027115 | 0.013765 | -121.7113 | -121.1837 | -23.6304 | -121.3235 | 0.020409 | 0.027442 | 0.07643 | -121.9973 | -0.04234 | -0.03943 | 0.75483 | 0.33158 | 0.37392 | -0.086624 | -0.045744 | -0.32831 | -0.0391 | 0.48534 | 0.34552 | 0.67383 | -0.032067 | 0.016921 | 121.6891 | 121.6419 | 121.6828 | 92.3582 | -121.7709 | 121.6894 | 121.6964 | 121.7454 | 98.0386 | -122.0568
1386.7969 | 122.0078 | -121.6736 | 0.068665 | 1.4211e-13 | -0.027951 | -0.00065809 | 0.059945 | -0.0079184 | 0.058046 | -0.21297 | -0.0037514 | -0.0034569 | 0.059783 | 0.027987 | 0.057131 | -120.9142 | -29.2833 | -121.3374 | 0.015501 | -0.027115 | 0.009187 | -121.7022 | -121.1791 | -23.9967 | -121.3143 | 0.015831 | 0.027442 | 0.071851 | -121.979 | -0.028604 | -0.053164 | 0.75941 | 0.33616 | 0.36477 | -0.09578 | -0.059478 | -0.30542 | -0.052834 | 0.4945 | 0.35926 | 0.66468 | -0.041223 | 0.003186 | 121.6891 | 121.6465 | 121.6828 | 92.3902 | -121.7709 | 121.6894 | 121.701 | 121.7454 | 97.6769 | -122.0477
1388.4688 | 121.9757 | -121.6736 | 0.091553 | 1.4211e-13 | -0.028164 | -0.00065809 | 0.059517 | -0.007491 | 0.058259 | -0.2206 | -0.0037514 | -0.0032433 | 0.059997 | 0.027987 | 0.057131 | -120.9096 | -29.3016 | -121.3283 | 0.024657 | -0.031693 | 0.013765 | -121.7113 | -121.1699 | -24.3584 | -121.3097 | 0.020409 | 0.022864 | 0.071851 | -122.0019 | -0.037762 | -0.066896 | 0.76399 | 0.34532 | 0.38308 | -0.12325 | -0.077788 | -0.32831 | -0.071144 | 0.50365 | 0.36384 | 0.69215 | -0.068689 | -0.019702 | 121.6982 | 121.6419 | 121.6873 | 92.3719 | -121.8029 | 121.694 | 121.6964 | 121.7454 | 97.3152 | -122.0934
1390.2188 | 122.0032 | -121.669 | 0.09613 | 1.4211e-13 | -0.028164 | -0.00087189 | 0.059945 | -0.0079184 | 0.058687 | -0.23586 | -0.0035378 | -0.0030297 | 0.059569 | 0.028201 | 0.057131 | -120.9096 | -29.3474 | -121.3283 | 0.020079 | -0.022536 | 0.009187 | -121.7159 | -121.1699 | -24.7888 | -121.3235 | 0.020409 | 0.022864 | 0.07643 | -121.9927 | -0.046918 | -0.076051 | 0.75941 | 0.34074 | 0.38766 | -0.11867 | -0.086943 | -0.32373 | -0.075721 | 0.49908 | 0.34552 | 0.66926 | -0.073266 | -0.0197 | 121.6891 | 121.6465 | 121.6782 | 92.3216 | -121.8121 | 121.6894 | 121.6919 | 121.7454 | 96.8802 | -122.0889
1391.9531 | 121.875 | -121.7422 | 0.12817 | 1.4211e-13 | -0.028164 | -0.00087189 | 0.059731 | -0.0079184 | 0.058473 | -0.2206 | -0.003965 | -0.0032433 | 0.059997 | 0.027987 | 0.056704 | -120.905 | -29.352 | -121.3283 | 0.020079 | -0.027115 | 0.013765 | -121.7113 | -121.1562 | -25.1871 | -121.3097 | 0.015831 | 0.022864 | 0.071851 | -121.9973 | 0.030903 | -0.1081 | 0.83723 | 0.41398 | 0.38308 | -0.15529 | -0.11441 | -0.25507 | -0.11234 | 0.58606 | 0.4325 | 0.68757 | -0.10531 | -0.056323 | 121.7623 | 121.7151 | 121.756 | 92.3902 | -121.8395 | 121.7581 | 121.7651 | 121.8141 | 96.5551 | -122.1255
1393.625 | 121.9391 | -121.7102 | 0.10529 | 1.4211e-13 | -0.028164 | -0.00087189 | 0.059731 | -0.0077048 | 0.058473 | -0.22823 | -0.0037514 | -0.0034569 | 0.059997 | 0.027987 | 0.057131 | -120.9142 | -29.3841 | -121.3237 | 0.020079 | -0.027115 | 0.004608 | -121.7159 | -121.1608 | -25.6267 | -121.3052 | 0.020409 | 0.027442 | 0.07643 | -121.9973 | -0.005719 | -0.085207 | 0.79603 | 0.38652 | 0.39224 | -0.1324 | -0.10068 | -0.28711 | -0.084877 | 0.54943 | 0.40504 | 0.69215 | -0.077844 | -0.028856 | 121.7303 | 121.6831 | 121.7148 | 92.3261 | -121.8212 | 121.7306 | 121.7376 | 121.7866 | 96.0835 | -122.1026
1395.3594 | 121.907 | -121.7148 | 0.10986 | 1.4211e-13 | -0.028164 | -0.00087189 | 0.059945 | -0.0077048 | 0.058687 | -0.22823 | -0.0037514 | -0.0034569 | 0.059569 | 0.028201 | 0.057131 | -120.9142 | -29.3886 | -121.3283 | 0.015501 | -0.027115 | 0.013765 | -121.7205 | -121.1699 | -26.1487 | -121.3052 | 0.020409 | 0.027442 | 0.07643 | -121.9973 | -0.00572 | -0.094362 | 0.80061 | 0.38652 | 0.39224 | -0.13698 | -0.096098 | -0.28253 | -0.089454 | 0.54485 | 0.40962 | 0.69215 | -0.082421 | -0.033433 | 121.7303 | 121.6877 | 121.7285 | 92.3261 | -121.8304 | 121.7352 | 121.7422 | 121.7912 | 95.5661 | -122.1072
1397.0781 | 121.9025 | -121.7194 | 0.10529 | 1.4211e-13 | -0.028164 | -0.00087189 | 0.059517 | -0.0079184 | 0.058473 | -0.22823 | -0.003965 | -0.0034569 | 0.059569 | 0.028201 | 0.057131 | -120.9188 | -29.4436 | -121.3328 | 0.020079 | -0.027115 | 0.009187 | -121.7159 | -121.1516 | -26.6248 | -121.3052 | 0.020409 | 0.027442 | 0.07643 | -122.0065 | 0.003436 | -0.085207 | 0.80061 | 0.38652 | 0.38308 | -0.1324 | -0.096099 | -0.28711 | -0.084877 | 0.56774 | 0.41419 | 0.70131 | -0.077844 | -0.028856 | 121.7394 | 121.6922 | 121.7285 | 92.2758 | -121.8212 | 121.7398 | 121.7468 | 121.7958 | 95.0945 | -122.1118
1398.7656 | 121.9803 | -121.6736 | 0.10529 | 1.4211e-13 | -0.028378 | -0.00065809 | 0.059731 | -0.0079184 | 0.058259 | -0.2206 | -0.0041788 | -0.0032433 | 0.059783 | 0.027987 | 0.057345 | -120.9188 | -29.4207 | -121.3328 | 0.015501 | -0.022536 | 0.004608 | -121.7159 | -121.147 | -27.1422 | -121.3006 | 0.024988 | 0.022864 | 0.07643 | -122.0019 | -0.04234 | -0.089785 | 0.75483 | 0.34074 | 0.38308 | -0.12782 | -0.10068 | -0.32831 | -0.080298 | 0.52655 | 0.373 | 0.70131 | -0.082422 | -0.028856 | 121.6891 | 121.651 | 121.6782 | 92.2529 | -121.8212 | 121.6986 | 121.6964 | 121.75 | 94.5314 | -122.1072
1400.5 | 121.8842 | -121.7102 | 0.10529 | 1.4211e-13 | -0.028164 | -0.00087189 | 0.059731 | -0.0072774 | 0.058687 | -0.2206 | -0.003965 | -0.0030297 | 0.059783 | 0.028414 | 0.057131 | -120.9188 | -29.4573 | -121.3328 | 0.020079 | -0.022536 | 0.009187 | -121.7205 | -121.1379 | -27.7375 | -121.3006 | 0.015831 | 0.022864 | 0.07643 | -121.9973 | -0.010298 | -0.085207 | 0.79145 | 0.37736 | 0.38766 | -0.12782 | -0.096099 | -0.28711 | -0.089455 | 0.57233 | 0.40962 | 0.69673 | -0.082422 | -0.028856 | 121.7303 | 121.6877 | 121.7194 | 92.2529 | -121.8258 | 121.726 | 121.7331 | 121.7866 | 93.9727 | -122.1026
1402.25 | 121.875 | -121.7468 | 0.11444 | 1.4211e-13 | -0.028592 | -0.0010855 | 0.059945 | -0.0077048 | 0.058687 | -0.22823 | -0.003965 | -0.0034569 | 0.059997 | 0.028201 | 0.057131 | -120.9142 | -29.4482 | -121.3191 | 0.015501 | -0.031693 | 0.009187 | -121.7159 | -121.1333 | -28.3739 | -121.2869 | 0.020409 | 0.022864 | 0.081008 | -122.0111 | 0.030902 | -0.09894 | 0.83265 | 0.42772 | 0.39682 | -0.14613 | -0.10525 | -0.26423 | -0.094032 | 0.61353 | 0.45997 | 0.7242 | -0.091577 | -0.033433 | 121.7623 | 121.7151 | 121.756 | 92.2987 | -121.8304 | 121.7672 | 121.7697 | 121.8278 | 93.3729 | -122.1255
1403.9375 | 121.875 | -121.7285 | 0.11444 | 1.4211e-13 | -0.028592 | -0.00087189 | 0.059517 | -0.0072774 | 0.058259 | -0.24349 | -0.003965 | -0.0030297 | 0.059569 | 0.028201 | 0.057345 | -120.9188 | -29.4894 | -121.3374 | 0.020079 | -0.027115 | 0.018344 | -121.7205 | -121.1379 | -29.0332 | -121.2869 | 0.020409 | 0.027442 | 0.071851 | -122.0111 | 0.008013 | -0.094362 | 0.80976 | 0.39109 | 0.38308 | -0.14156 | -0.096097 | -0.28254 | -0.094032 | 0.59064 | 0.44166 | 0.7242 | -0.086999 | -0.04259 | 121.7486 | 121.7014 | 121.7469 | 92.2391 | -121.8349 | 121.7489 | 121.756 | 121.8004 | 92.6953 | -122.1255
1405.6719 | 121.9803 | -121.6873 | 0.10529 | 1.4211e-13 | -0.028378 | -0.0010855 | 0.059731 | -0.007491 | 0.058687 | -0.23586 | -0.0035378 | -0.0032433 | 0.059783 | 0.028414 | 0.057131 | -120.9142 | -29.5306 | -121.3374 | 0.024657 | -0.027115 | 0.013765 | -121.7251 | -121.1196 | -29.7933 | -121.2869 | 0.015831 | 0.022864 | 0.071851 | -122.0111 | -0.037765 | -0.080629 | 0.77314 | 0.34989 | 0.38766 | -0.1324 | -0.091521 | -0.32374 | -0.089455 | 0.56775 | 0.40046 | 0.7242 | -0.082422 | -0.033435 | 121.712 | 121.6602 | 121.7011 | 92.1567 | -121.8304 | 121.7031 | 121.7102 | 121.7592 | 91.894 | -122.1163
1407.4062 | 121.8933 | -121.7422 | 0.10529 | 1.4211e-13 | -0.028592 | -0.0012991 | 0.059731 | -0.0077048 | 0.058687 | -0.22823 | -0.0037514 | -0.0030297 | 0.059997 | 0.027987 | 0.056917 | -120.9142 | -29.5214 | -121.3283 | 0.024657 | -0.027115 | 0.013765 | -121.7251 | -121.1196 | -30.5442 | -121.2731 | 0.020409 | 0.027442 | 0.07643 | -122.0111 | 0.017167 | -0.080629 | 0.82807 | 0.41398 | 0.39682 | -0.1324 | -0.091521 | -0.2688 | -0.084877 | 0.62269 | 0.46913 | 0.73794 | -0.077844 | -0.028856 | 121.7669 | 121.7151 | 121.756 | 92.2208 | -121.8304 | 121.7627 | 121.7697 | 121.8187 | 91.198 | -122.1163
1409.1406 | 122.0032 | -121.7056 | 0.09613 | 1.4211e-13 | -0.028592 | -0.00087189 | 0.059517 | -0.0077048 | 0.058473 | -0.22823 | -0.0035378 | -0.0026023 | 0.059997 | 0.028414 | 0.057345 | -120.9142 | -29.5306 | -121.3374 | 0.029236 | -0.027115 | 0.013765 | -121.7251 | -121.1196 | -31.3592 | -121.264 | 0.020409 | 0.027442 | 0.081008 | -122.0111 | -0.019455 | -0.066894 | 0.79145 | 0.36821 | 0.38766 | -0.12324 | -0.082365 | -0.30543 | -0.075721 | 0.58606 | 0.44167 | 0.7471 | -0.068688 | -0.015122 | 121.7349 | 121.6785 | 121.7194 | 92.175 | -121.8212 | 121.726 | 121.7331 | 121.7866 | 90.3464 | -122.1072
1410.875 | 121.8796 | -121.7194 | 0.10071 | 1.4211e-13 | -0.028592 | -0.00065809 | 0.059517 | -0.0079184 | 0.058046 | -0.2206 | -0.0035378 | -0.0032433 | 0.059997 | 0.028414 | 0.057131 | -120.9142 | -29.5443 | -121.3374 | 0.015501 | -0.027115 | 0.013765 | -121.7251 | -121.115 | -32.2246 | -121.264 | 0.020409 | 0.022864 | 0.071851 | -122.0156 | -0.005722 | -0.085207 | 0.80518 | 0.38194 | 0.38766 | -0.12782 | -0.086943 | -0.29627 | -0.080299 | 0.60437 | 0.4554 | 0.75167 | -0.077844 | -0.028857 | 121.7349 | 121.6922 | 121.7331 | 92.175 | -121.8258 | 121.7398 | 121.7422 | 121.7912 | 89.4948 | -122.1163
1412.5625 | 121.962 | -121.6919 | 0.07782 | 1.4211e-13 | -0.028805 | -0.0010855 | 0.059731 | -0.0077048 | 0.058259 | -0.2206 | -0.0037514 | -0.0032433 | 0.06021 | 0.028414 | 0.057345 | -120.9188 | -29.5626 | -121.3328 | 0.015501 | -0.022536 | 0.013765 | -121.7205 | -121.1012 | -33.0946 | -121.2502 | 0.020409 | 0.022864 | 0.081008 | -122.0156 | -0.028608 | -0.062319 | 0.77314 | 0.35905 | 0.38766 | -0.10036 | -0.064055 | -0.32374 | -0.057411 | 0.59065 | 0.44167 | 0.76541 | -0.054956 | 0.003188 | 121.7074 | 121.6694 | 121.7057 | 92.1293 | -121.7983 | 121.7123 | 121.7148 | 121.7729 | 88.5973 | -122.0935
1414.3125 | 122.0078 | -121.6827 | 0.091553 | 1.4211e-13 | -0.028592 | -0.00065809 | 0.059731 | -0.0077048 | 0.058259 | -0.22823 | -0.0037514 | -0.0034569 | 0.059997 | 0.028201 | 0.056917 | -120.9233 | -29.6222 | -121.342 | 0.020079 | -0.031693 | 0.013765 | -121.7251 | -121.0875 | -34.0149 | -121.2502 | 0.024988 | 0.027442 | 0.085587 | -122.0111 | -0.042343 | -0.071474 | 0.75941 | 0.34074 | 0.38308 | -0.12325 | -0.077788 | -0.32831 | -0.066565 | 0.59523 | 0.43252 | 0.76083 | -0.064111 | -0.005966 | 121.7028 | 121.651 | 121.6965 | 92.0606 | -121.8166 | 121.7077 | 121.7102 | 121.7683 | 87.6679 | -122.1026
1416.0625 | 121.9803 | -121.701 | 0.086975 | 1.4211e-13 | -0.028805 | -0.00065809 | 0.059517 | -0.007491 | 0.058259 | -0.23586 | -0.003965 | -0.0034569 | 0.059569 | 0.028414 | 0.057345 | -120.9142 | -29.645 | -121.3374 | 0.015501 | -0.027115 | 0.009187 | -121.7159 | -121.0784 | -35.0222 | -121.2502 | 0.020409 | 0.027442 | 0.07643 | -122.0111 | -0.014874 | -0.071474 | 0.78687 | 0.36363 | 0.3785 | -0.11409 | -0.077788 | -0.31 | -0.066566 | 0.62269 | 0.45083 | 0.76083 | -0.059533 | -0.010545 | 121.7166 | 121.6739 | 121.7102 | 92.056 | -121.8029 | 121.7215 | 121.7285 | 121.7775 | 86.6789 | -122.098
1417.7656 | 121.9894 | -121.6827 | 0.082397 | 1.4211e-13 | -0.029019 | -0.00087189 | 0.059731 | -0.007491 | 0.058473 | -0.2206 | -0.0037514 | -0.0032433 | 0.059783 | 0.028414 | 0.057131 | -120.9233 | -29.6588 | -121.3557 | 0.010922 | -0.022536 | 0.009187 | -121.7251 | -121.0646 | -35.9242 | -121.2456 | 0.015831 | 0.018285 | 0.07643 | -122.0202 | -0.042343 | -0.071475 | 0.75941 | 0.327 | 0.36935 | -0.10493 | -0.07321 | -0.33747 | -0.066566 | 0.61812 | 0.43709 | 0.77457 | -0.064112 | -0.005967 | 121.6937 | 121.6602 | 121.6919 | 92.024 | -121.8075 | 121.6986 | 121.701 | 121.7592 | 85.7585 | -122.1026
1419.5 | 121.9986 | -121.6965 | 0.086975 | 1.4211e-13 | -0.028805 | -0.0010855 | 0.059731 | -0.0077048 | 0.058046 | -0.22823 | -0.0035378 | -0.0036707 | 0.06021 | 0.027987 | 0.057345 | -120.9142 | -29.6908 | -121.3512 | 0.015501 | -0.022536 | 0.013765 | -121.7297 | -121.0646 | -37.0139 | -121.2319 | 0.020409 | 0.027442 | 0.081008 | -122.0202 | -0.033189 | -0.071474 | 0.7823 | 0.34531 | 0.3785 | -0.10951 | -0.07321 | -0.32374 | -0.066566 | 0.63185 | 0.46456 | 0.7883 | -0.059533 | -0.005967 | 121.712 | 121.6739 | 121.7102 | 92.0056 | -121.8166 | 121.7169 | 121.7239 | 121.7775 | 84.6825 | -122.1072
1421.25 | 121.9894 | -121.7102 | 0.091553 | 1.4211e-13 | -0.029019 | -0.0010855 | 0.059731 | -0.0077048 | 0.058259 | -0.23586 | -0.0035378 | -0.0032433 | 0.059569 | 0.028201 | 0.057131 | -120.9142 | -29.6634 | -121.3512 | 0.015501 | -0.027115 | 0.004608 | -121.7297 | -121.0509 | -38.0808 | -121.2319 | 0.024988 | 0.027442 | 0.07643 | -122.0248 | -0.019456 | -0.076052 | 0.79603 | 0.35905 | 0.3785 | -0.11867 | -0.086945 | -0.31458 | -0.066565 | 0.65932 | 0.4783 | 0.79288 | -0.064111 | -0.015123 | 121.7257 | 121.6831 | 121.7148 | 92.0468 | -121.8212 | 121.7352 | 121.7376 | 121.7866 | 83.6294 | -122.1163
1422.9375 | 122.0123 | -121.7056 | 0.086975 | 1.4211e-13 | -0.028592 | -0.0010855 | 0.059303 | -0.007491 | 0.058259 | -0.22823 | -0.003965 | -0.0032433 | 0.059783 | 0.028414 | 0.057131 | -120.9279 | -29.7046 | -121.3603 | 0.015501 | -0.027115 | 0.009187 | -121.7297 | -121.0326 | -39.1293 | -121.2273 | 0.024988 | 0.032021 | 0.067272 | -122.0294 | -0.024034 | -0.071474 | 0.77772 | 0.34531 | 0.36935 | -0.11409 | -0.077788 | -0.32374 | -0.061987 | 0.67306 | 0.4783 | 0.80204 | -0.054954 | -0.019703 | 121.7211 | 121.6785 | 121.7148 | 92.0011 | -121.8166 | 121.7306 | 121.7376 | 121.7729 | 82.5763 | -122.1163
1424.6719 | 122.0215 | -121.6873 | 0.07782 | 1.4211e-13 | -0.029019 | -0.00087189 | 0.059731 | -0.0079184 | 0.058259 | -0.23586 | -0.003965 | -0.0030297 | 0.059569 | 0.028201 | 0.057345 | -120.9188 | -29.7137 | -121.3557 | 0.020079 | -0.022536 | 0.018344 | -121.7251 | -121.028 | -40.448 | -121.2136 | 0.020409 | 0.027442 | 0.07643 | -122.0248 | -0.037765 | -0.057741 | 0.76856 | 0.33158 | 0.36935 | -0.10036 | -0.059476 | -0.33747 | -0.057411 | 0.65933 | 0.47372 | 0.8112 | -0.050378 | -0.00139 | 121.7074 | 121.6648 | 121.7057 | 91.9736 | -121.8029 | 121.7077 | 121.7148 | 121.7637 | 81.2394 | -122.1026
1426.4062 | 121.907 | -121.7148 | 0.12817 | 1.4211e-13 | -0.028592 | -0.00087189 | 0.059731 | -0.0079184 | 0.058473 | -0.22823 | -0.003965 | -0.0032433 | 0.059783 | 0.029055 | 0.057131 | -120.9188 | -29.7275 | -121.3603 | 0.010922 | -0.022536 | 0.018344 | -121.7251 | -121.0143 | -41.7804 | -121.209 | 0.020409 | 0.032021 | 0.07643 | -122.0156 | -0.010299 | -0.11725 | 0.79603 | 0.35447 | 0.36477 | -0.15071 | -0.10983 | -0.30085 | -0.10777 | 0.70053 | 0.50577 | 0.80662 | -0.096153 | -0.051744 | 121.7257 | 121.6922 | 121.7331 | 91.9873 | -121.8533 | 121.7352 | 121.7468 | 121.7912 | 79.9344 | -122.1438
1428.1562 | 121.9116 | -121.7239 | 0.11444 | 1.4211e-13 | -0.028805 | -0.0010855 | 0.059731 | -0.007491 | 0.058046 | -0.2206 | -0.0037514 | -0.0030297 | 0.059569 | 0.028628 | 0.057345 | -120.9279 | -29.7366 | -121.3603 | 0.024657 | -0.027115 | 0.009187 | -121.7434 | -121.0097 | -43.1998 | -121.2044 | 0.024988 | 0.027442 | 0.07643 | -122.0339 | -0.01946 | -0.089784 | 0.79603 | 0.36362 | 0.38308 | -0.14156 | -0.10525 | -0.31001 | -0.089453 | 0.71426 | 0.5195 | 0.82951 | -0.086999 | -0.038011 | 121.7486 | 121.6968 | 121.7331 | 91.9873 | -121.8578 | 121.7489 | 121.7514 | 121.8004 | 78.5242 | -122.1484
1429.8906 | 121.9025 | -121.7285 | 0.10071 | 1.4211e-13 | -0.028805 | -0.00065809 | 0.059517 | -0.0079184 | 0.058259 | -0.2206 | -0.0035378 | -0.0032433 | 0.059997 | 0.028414 | 0.057345 | -120.9233 | -29.7549 | -121.3557 | 0.020079 | -0.017957 | 0.009187 | -121.7251 | -120.9776 | -44.8435 | -121.1953 | 0.020409 | 0.022864 | 0.081008 | -122.0248 | 0.003434 | -0.080629 | 0.80518 | 0.37278 | 0.36935 | -0.11867 | -0.091521 | -0.29627 | -0.080299 | 0.75089 | 0.53324 | 0.82951 | -0.077844 | -0.0197 | 121.7486 | 121.7106 | 121.7377 | 91.9736 | -121.8258 | 121.7489 | 121.7514 | 121.8095 | 76.885 | -122.1255
1431.5781 | 121.9528 | -121.7468 | 0.11902 | 1.4211e-13 | -0.029233 | -0.0010855 | 0.059517 | -0.0079184 | 0.058046 | -0.22823 | -0.0035378 | -0.0036707 | 0.059569 | 0.028628 | 0.057131 | -120.9142 | -29.8007 | -121.3603 | 0.024657 | -0.022536 | 0.013765 | -121.7297 | -120.973 | -46.3133 | -121.1815 | 0.015831 | 0.032021 | 0.07643 | -122.0294 | 0.017165 | -0.094362 | 0.83265 | 0.38651 | 0.36935 | -0.14155 | -0.10525 | -0.28254 | -0.10319 | 0.77378 | 0.56528 | 0.84783 | -0.086998 | -0.042589 | 121.7715 | 121.7243 | 121.7606 | 91.9461 | -121.8487 | 121.7627 | 121.7788 | 121.8233 | 75.4335 | -122.1484
1433.3125 | 121.9757 | -121.701 | 0.11444 | 1.4211e-13 | -0.029233 | -0.00087189 | 0.060158 | -0.007491 | 0.058473 | -0.2206 | -0.0041788 | -0.0030297 | 0.059356 | 0.028628 | 0.057345 | -120.9233 | -29.8694 | -121.3603 | 0.024657 | -0.027115 | 0.009187 | -121.7342 | -120.9502 | -47.9525 | -121.1678 | 0.024988 | 0.022864 | 0.085587 | -122.0339 | -0.03319 | -0.089784 | 0.77772 | 0.34074 | 0.37393 | -0.14156 | -0.10525 | -0.3329 | -0.089453 | 0.7509 | 0.53324 | 0.86614 | -0.091577 | -0.028854 | 121.7257 | 121.6739 | 121.7102 | 91.8317 | -121.8487 | 121.726 | 121.7239 | 121.7866 | 73.7486 | -122.1484
1434.9844 | 121.9894 | -121.7056 | 0.086975 | 1.4211e-13 | -0.029233 | -0.0012991 | 0.059731 | -0.0079184 | 0.058046 | -0.23586 | -0.003965 | -0.0030297 | 0.059997 | 0.028628 | 0.057345 | -120.9325 | -29.8511 | -121.3649 | 0.020079 | -0.027115 | 0.018344 | -121.7388 | -120.9364 | -49.5688 | -121.1632 | 0.024988 | 0.027442 | 0.07643 | -122.0294 | -0.033192 | -0.066896 | 0.77314 | 0.34074 | 0.37393 | -0.11409 | -0.068631 | -0.32374 | -0.061987 | 0.76921 | 0.5424 | 0.86614 | -0.059533 | -0.010545 | 121.7257 | 121.6785 | 121.724 | 91.8545 | -121.8258 | 121.7306 | 121.7331 | 121.7821 | 72.1369 | -122.1163
1436.7344 | 122.0123 | -121.6644 | 0.07782 | 1.4211e-13 | -0.029233 | -0.0010855 | 0.059731 | -0.0077048 | 0.058259 | -0.22823 | -0.0037514 | -0.0030297 | 0.059356 | 0.028628 | 0.057131 | -120.9233 | -29.8465 | -121.3557 | 0.015501 | -0.027115 | 0.018344 | -121.7388 | -120.9135 | -51.4094 | -121.1541 | 0.020409 | 0.0366 | 0.081008 | -122.0339 | -0.07439 | -0.062319 | 0.7411 | 0.30869 | 0.38308 | -0.10494 | -0.059476 | -0.36952 | -0.057411 | 0.75091 | 0.51036 | 0.87988 | -0.04122 | 0.003188 | 121.6799 | 121.6373 | 121.6828 | 91.8179 | -121.8166 | 121.6848 | 121.701 | 121.7454 | 70.255 | -122.1118
1438.4844 | 121.9345 | -121.7239 | 0.091553 | 1.4211e-13 | -0.029233 | -0.00065809 | 0.059517 | -0.007491 | 0.058259 | -0.22823 | -0.003965 | -0.0032433 | 0.059783 | 0.028628 | 0.057131 | -120.9233 | -29.8557 | -121.3649 | 0.024657 | -0.027115 | 0.009187 | -121.7342 | -120.8998 | -53.1173 | -121.1403 | 0.024988 | 0.022864 | 0.081008 | -122.0431 | -0.010302 | -0.066896 | 0.80061 | 0.35905 | 0.36935 | -0.11867 | -0.082366 | -0.31917 | -0.066565 | 0.82415 | 0.58361 | 0.90277 | -0.068689 | -0.010545 | 121.7486 | 121.6968 | 121.7331 | 91.8683 | -121.8258 | 121.7489 | 121.7468 | 121.8049 | 68.6067 | -122.1347
1440.2344 | 122.0398 | -121.6827 | 0.10071 | 1.4211e-13 | -0.029446 | -0.0010855 | 0.059731 | -0.0079184 | 0.058259 | -0.22823 | -0.003965 | -0.0032433 | 0.059783 | 0.028842 | 0.057558 | -120.9233 | -29.9152 | -121.3557 | 0.015501 | -0.027115 | 0.018344 | -121.7342 | -120.8677 | -55.2418 | -121.1358 | 0.011252 | 0.032021 | 0.07643 | -122.0339 | -0.051501 | -0.085207 | 0.75941 | 0.327 | 0.37851 | -0.12782 | -0.082364 | -0.35121 | -0.089456 | 0.815 | 0.54698 | 0.89819 | -0.068687 | -0.024278 | 121.6982 | 121.6556 | 121.7011 | 91.7676 | -121.8349 | 121.694 | 121.7148 | 121.7592 | 66.441 | -122.1347
1441.9219 | 122.0169 | -121.7148 | 0.07782 | 1.4211e-13 | -0.029446 | -0.0010855 | 0.059945 | -0.0077048 | 0.058046 | -0.22823 | -0.0037514 | -0.0032433 | 0.059783 | 0.028414 | 0.056917 | -120.9188 | -29.9152 | -121.3603 | 0.020079 | -0.017957 | 0.018344 | -121.7342 | -120.854 | -57.1923 | -121.1266 | 0.029566 | 0.032021 | 0.081008 | -122.0385 | -0.019457 | -0.057741 | 0.79603 | 0.35447 | 0.37393 | -0.095777 | -0.059476 | -0.32374 | -0.048254 | 0.86078 | 0.58819 | 0.91193 | -0.045799 | 0.003188 | 121.7349 | 121.6968 | 121.7331 | 91.7996 | -121.8121 | 121.7443 | 121.7468 | 121.7958 | 64.5225 | -122.1163
1443.6719 | 122.0352 | -121.701 | 0.091553 | 1.4211e-13 | -0.029233 | -0.00087189 | 0.059517 | -0.0079184 | 0.058687 | -0.22823 | -0.003965 | -0.0030297 | 0.059997 | 0.028842 | 0.057558 | -120.9233 | -29.9289 | -121.3649 | 0.020079 | -0.022536 | 0.018344 | -121.7434 | -120.8174 | -59.358 | -121.122 | 0.015831 | 0.032021 | 0.081008 | -122.0339 | -0.042348 | -0.071474 | 0.77772 | 0.33616 | 0.37851 | -0.11409 | -0.073209 | -0.3329 | -0.075722 | 0.88368 | 0.57903 | 0.91193 | -0.059532 | -0.010545 | 121.7211 | 121.6785 | 121.7194 | 91.7721 | -121.835 | 121.7169 | 121.7331 | 121.7821 | 62.343 | -122.1255
1445.4219 | 121.9757 | -121.7285 | 0.086975 | 1.4211e-13 | -0.029233 | -0.00044449 | 0.059731 | -0.0079184 | 0.058473 | -0.22823 | -0.0041788 | -0.0034569 | 0.059783 | 0.028628 | 0.057345 | -120.9233 | -29.9655 | -121.3603 | 0.015501 | -0.017957 | 0.009187 | -121.7342 | -120.7899 | -61.6611 | -121.1037 | 0.024988 | 0.0366 | 0.07643 | -122.0431 | -0.005724 | -0.071474 | 0.80518 | 0.3682 | 0.37393 | -0.10493 | -0.077788 | -0.31459 | -0.061987 | 0.93862 | 0.62481 | 0.9394 | -0.050375 | -0.010545 | 121.744 | 121.7106 | 121.7377 | 91.763 | -121.8212 | 121.7535 | 121.7651 | 121.8049 | 60.0674 | -122.1301
1447.0938 | 122.0215 | -121.701 | 0.073242 | 1.4211e-13 | -0.029446 | -0.0010855 | 0.059731 | -0.0079184 | 0.058046 | -0.23586 | -0.0037514 | -0.0028161 | 0.059783 | 0.028842 | 0.057345 | -120.9279 | -29.9564 | -121.3649 | 0.015501 | -0.022536 | 0.013765 | -121.7434 | -120.7533 | -63.4468 | -121.0854 | 0.020409 | 0.027442 | 0.081008 | -122.0385 | -0.042348 | -0.057741 | 0.77314 | 0.33616 | 0.37851 | -0.095778 | -0.059477 | -0.33748 | -0.052833 | 0.94778 | 0.61566 | 0.95314 | -0.0458 | 0.007766 | 121.7166 | 121.6785 | 121.7148 | 91.7447 | -121.8166 | 121.7215 | 121.7285 | 121.7821 | 58.2542 | -122.1118
1448.8438 | 122.0169 | -121.7148 | 0.073242 | 1.4211e-13 | -0.02966 | -0.0010855 | 0.059731 | -0.0079184 | 0.058259 | -0.22823 | -0.0035378 | -0.0030297 | 0.059569 | 0.028628 | 0.057558 | -120.9279 | -29.9793 | -121.3603 | 0.020079 | -0.022536 | 0.018344 | -121.7388 | -120.7212 | -64.6098 | -121.0808 | 0.015831 | 0.027442 | 0.081008 | -122.0339 | -0.024036 | -0.053163 | 0.78687 | 0.35447 | 0.37851 | -0.095778 | -0.054898 | -0.31916 | -0.057411 | 0.99357 | 0.63397 | 0.95314 | -0.0458 | 0.007766 | 121.7349 | 121.6922 | 121.7331 | 91.7355 | -121.8121 | 121.7306 | 121.7422 | 121.7958 | 57.105 | -122.1072
1450.5781 | 122.0123 | -121.6827 | 0.086975 | 1.4211e-13 | -0.029446 | -0.0010855 | 0.059731 | -0.0079184 | 0.058259 | -0.2206 | -0.003965 | -0.0032433 | 0.059569 | 0.029055 | 0.057558 | -120.9188 | -30.0296 | -121.3603 | 0.024657 | -0.022536 | 0.018344 | -121.7388 | -120.6846 | -66.162 | -121.0625 | 0.015831 | 0.0366 | 0.07643 | -122.0431 | -0.05608 | -0.062318 | 0.76398 | 0.32243 | 0.37851 | -0.10951 | -0.068631 | -0.36037 | -0.071144 | 0.99815 | 0.62024 | 0.98061 | -0.050375 | -0.010545 | 121.7074 | 121.6602 | 121.7011 | 91.6531 | -121.8258 | 121.6986 | 121.7193 | 121.7592 | 55.5207 | -122.1301
1452.3125 | 122.0261 | -121.7468 | 0.091553 | 1.4211e-13 | -0.029446 | -0.00065809 | 0.059517 | -0.0079184 | 0.058259 | -0.23586 | -0.0035378 | -0.0030297 | 0.059997 | 0.029055 | 0.057558 | -120.9233 | -30.0068 | -121.3649 | 0.015501 | -0.017957 | 0.013765 | -121.7342 | -120.6525 | -68.1675 | -121.0488 | 0.020409 | 0.022864 | 0.07643 | -122.0431 | 0.012586 | -0.076052 | 0.82349 | 0.38193 | 0.36935 | -0.10951 | -0.077788 | -0.29628 | -0.071144 | 1.0943 | 0.69807 | 0.99435 | -0.068689 | -0.015123 | 121.7623 | 121.7289 | 121.7606 | 91.7401 | -121.8258 | 121.7672 | 121.7697 | 121.8233 | 53.5794 | -122.1347
1453.9844 | 121.9574 | -121.7148 | 0.11902 | 1.4211e-13 | -0.02966 | -0.00087189 | 0.059731 | -0.0077048 | 0.058259 | -0.23586 | -0.0037514 | -0.0028161 | 0.059783 | 0.029269 | 0.057131 | -120.9279 | -30.0617 | -121.3649 | 0.029236 | -0.027115 | 0.009187 | -121.748 | -120.6159 | -70.0127 | -121.0304 | 0.020409 | 0.032021 | 0.085587 | -122.0431 | -0.033194 | -0.089783 | 0.78687 | 0.34989 | 0.38309 | -0.14613 | -0.10983 | -0.32832 | -0.09861 | 1.0989 | 0.68434 | 1.0127 | -0.086998 | -0.033432 | 121.744 | 121.6877 | 121.724 | 91.6531 | -121.867 | 121.7352 | 121.7468 | 121.8004 | 51.7021 | -122.1621
1455.7188 | 121.962 | -121.7514 | 0.10986 | 1.4211e-13 | -0.029874 | -0.0010855 | 0.059731 | -0.008132 | 0.058259 | -0.23586 | -0.0037514 | -0.0030297 | 0.059783 | 0.029055 | 0.057345 | -120.9233 | -30.0709 | -121.374 | 0.015501 | -0.017957 | 0.022922 | -121.7388 | -120.5701 | -72.27 | -121.0213 | 0.020409 | 0.032021 | 0.07643 | -122.0431 | 0.012585 | -0.094362 | 0.82807 | 0.37736 | 0.36477 | -0.12782 | -0.086941 | -0.2917 | -0.089454 | 1.1813 | 0.73012 | 1.0218 | -0.077842 | -0.033433 | 121.7669 | 121.7334 | 121.7743 | 91.6805 | -121.8487 | 121.7718 | 121.7834 | 121.8278 | 49.4814 | -122.153
1457.4531 | 121.907 | -121.7606 | 0.11902 | 1.4211e-13 | -0.029874 | -0.0012991 | 0.059303 | -0.008132 | 0.058473 | -0.23586 | -0.0033242 | -0.0023887 | 0.059783 | 0.029055 | 0.057558 | -120.9325 | -30.048 | -121.3649 | 0.020079 | -0.031693 | 0.018344 | -121.748 | -120.5152 | -74.4449 | -120.9892 | 0.020409 | 0.022864 | 0.07643 | -122.0431 | 0.012582 | -0.09894 | 0.82807 | 0.39567 | 0.38309 | -0.15071 | -0.10068 | -0.28255 | -0.09861 | 1.2454 | 0.77132 | 1.0539 | -0.096155 | -0.042589 | 121.7806 | 121.7289 | 121.7789 | 91.7126 | -121.867 | 121.781 | 121.7834 | 121.837 | 47.3157 | -122.1621
1459.1875 | 121.9025 | -121.7697 | 0.13733 | 1.4211e-13 | -0.02966 | -0.0010855 | 0.059945 | -0.008132 | 0.058046 | -0.2206 | -0.003965 | -0.0028161 | 0.059783 | 0.029483 | 0.057558 | -120.9279 | -30.1304 | -121.3649 | 0.015501 | -0.017957 | 0.018344 | -121.7434 | -120.4648 | -76.5374 | -120.9709 | 0.024988 | 0.027442 | 0.071851 | -122.0431 | 0.026316 | -0.12183 | 0.8418 | 0.40482 | 0.37851 | -0.15529 | -0.11899 | -0.27339 | -0.11234 | 1.3049 | 0.79879 | 1.0722 | -0.10989 | -0.065478 | 121.7852 | 121.7518 | 121.7881 | 91.6393 | -121.8807 | 121.7947 | 121.7972 | 121.8416 | 45.2324 | -122.1804
1460.8594 | 121.9254 | -121.7422 | 0.1236 | 1.4211e-13 | -0.029019 | -0.0010855 | 0.059731 | -0.008132 | 0.058046 | -0.2206 | -0.0037514 | -0.0028161 | 0.059569 | 0.029483 | 0.057345 | -120.9233 | -30.1487 | -121.374 | 0.024657 | -0.031693 | 0.018344 | -121.7434 | -120.4099 | -78.0025 | -120.9434 | 0.024988 | 0.027442 | 0.07643 | -122.0568 | -0.001149 | -0.098939 | 0.81892 | 0.3682 | 0.36935 | -0.15529 | -0.10525 | -0.31459 | -0.098608 | 1.3324 | 0.7988 | 1.1134 | -0.096154 | -0.047166 | 121.7669 | 121.7106 | 121.7606 | 91.5936 | -121.867 | 121.7672 | 121.7697 | 121.8187 | 43.7397 | -122.1804
1462.6094 | 121.9574 | -121.7743 | 0.12817 | 1.4211e-13 | -0.029446 | -0.00044449 | 0.059303 | -0.008132 | 0.058473 | -0.23586 | -0.003965 | -0.0028161 | 0.059783 | 0.029055 | 0.057772 | -120.9279 | -30.2036 | -121.3695 | 0.024657 | -0.017957 | 0.022922 | -121.7526 | -120.3366 | -79.8981 | -120.9297 | 0.024988 | 0.032021 | 0.081008 | -122.0523 | 0.021736 | -0.10352 | 0.84638 | 0.40482 | 0.38309 | -0.14613 | -0.10525 | -0.27797 | -0.10319 | 1.4377 | 0.84458 | 1.1225 | -0.096153 | -0.047166 | 121.7989 | 121.7563 | 121.7972 | 91.5707 | -121.8807 | 121.7993 | 121.8063 | 121.8553 | 41.8762 | -122.1804
1464.3438 | 121.9208 | -121.7377 | 0.13733 | 1.4211e-13 | -0.029446 | -0.0012991 | 0.059517 | -0.0077048 | 0.058473 | -0.23586 | -0.003965 | -0.0028161 | 0.059997 | 0.029269 | 0.057558 | -120.9233 | -30.2128 | -121.3695 | 0.020079 | -0.022536 | 0.018344 | -121.748 | -120.2542 | -81.0978 | -120.9068 | 0.024988 | 0.022864 | 0.081008 | -122.0477 | -0.010306 | -0.11725 | 0.81434 | 0.3682 | 0.37851 | -0.15987 | -0.11899 | -0.31001 | -0.11234 | 1.4835 | 0.83085 | 1.1409 | -0.11447 | -0.056321 | 121.7578 | 121.7151 | 121.756 | 91.5249 | -121.8853 | 121.7627 | 121.7605 | 121.8187 | 40.6399 | -122.185
1466.0156 | 122.0398 | -121.701 | 0.086975 | 1.4211e-13 | -0.029874 | -0.00087189 | 0.059303 | -0.0077048 | 0.058473 | -0.22823 | -0.003965 | -0.0026023 | 0.059356 | 0.029483 | 0.057772 | -120.9233 | -30.254 | -121.3649 | 0.024657 | -0.013378 | 0.018344 | -121.7526 | -120.1992 | -85.4063 | -120.8519 | 0.024988 | 0.0366 | 0.07643 | -122.0477 | -0.051506 | -0.062318 | 0.77772 | 0.33616 | 0.38766 | -0.10035 | -0.068631 | -0.34663 | -0.061987 | 1.5018 | 0.84918 | 1.1958 | -0.050375 | -0.010545 | 121.7257 | 121.6877 | 121.7194 | 91.4471 | -121.8395 | 121.726 | 121.7377 | 121.7775 | 36.2947 | -122.1347
1467.75 | 121.907 | -121.7606 | 0.11902 | 1.4211e-13 | -0.030087 | -0.00087189 | 0.059517 | -0.008132 | 0.058046 | -0.23586 | -0.003965 | -0.0026023 | 0.059997 | 0.029483 | 0.057772 | -120.9233 | -30.2723 | -121.3649 | 0.024657 | -0.017957 | 0.022922 | -121.7434 | -120.1077 | -87.8422 | -120.8107 | 0.024988 | 0.0366 | 0.081008 | -122.0477 | 0.017161 | -0.094362 | 0.83723 | 0.39567 | 0.37851 | -0.13698 | -0.096097 | -0.28713 | -0.094031 | 1.6529 | 0.94989 | 1.237 | -0.082419 | -0.038011 | 121.7852 | 121.7426 | 121.7835 | 91.4882 | -121.8624 | 121.7855 | 121.7972 | 121.8416 | 33.9184 | -122.1667
1469.4844 | 121.9986 | -121.7331 | 0.091553 | 1.4211e-13 | -0.030087 | -0.0010855 | 0.059517 | -0.007491 | 0.058259 | -0.2206 | -0.0037514 | -0.0026023 | 0.059783 | 0.029696 | 0.057986 | -120.9325 | -30.286 | -121.374 | 0.020079 | -0.027115 | 0.018344 | -121.748 | -120.0207 | -89.3806 | -120.7878 | 0.024988 | 0.027442 | 0.071851 | -122.0477 | -0.014884 | -0.071474 | 0.8006 | 0.35904 | 0.37393 | -0.11867 | -0.073209 | -0.31459 | -0.066565 | 1.7124 | 0.94532 | 1.2599 | -0.064111 | -0.019702 | 121.7532 | 121.706 | 121.7514 | 91.447 | -121.8395 | 121.7581 | 121.7605 | 121.8049 | 32.3525 | -122.1392
1471.2188 | 121.9437 | -121.7606 | 0.11444 | 1.4211e-13 | -0.030087 | -0.00087189 | 0.059303 | -0.008132 | 0.058259 | -0.23586 | -0.0037514 | -0.0026023 | 0.059997 | 0.029483 | 0.057986 | -120.9325 | -30.3089 | -121.374 | 0.020079 | -0.022536 | 0.018344 | -121.7526 | -119.9383 | -90.5665 | -120.7374 | 0.020409 | 0.0366 | 0.07643 | -122.0477 | 0.008003 | -0.094362 | 0.82807 | 0.38651 | 0.37851 | -0.13698 | -0.096097 | -0.28713 | -0.094032 | 1.8223 | 1.0232 | 1.3103 | -0.077841 | -0.038011 | 121.7806 | 121.738 | 121.7789 | 91.4516 | -121.867 | 121.781 | 121.7972 | 121.837 | 31.194 | -122.1621
1472.9062 | 122.0444 | -121.6827 | 0.064087 | 1.4211e-13 | -0.029233 | -0.0015129 | 0.059945 | -0.0079184 | 0.058473 | -0.2206 | -0.0037514 | -0.0026023 | 0.059569 | 0.029696 | 0.057986 | -120.9188 | -30.3318 | -121.3695 | 0.020079 | -0.022536 | 0.013765 | -121.7526 | -119.8101 | -92.0958 | -120.7054 | 0.024988 | 0.032021 | 0.07643 | -122.0385 | -0.069817 | -0.044008 | 0.76398 | 0.31327 | 0.38309 | -0.086623 | -0.050322 | -0.35579 | -0.039099 | 1.8727 | 0.97738 | 1.3332 | -0.032066 | 0.012343 | 121.7028 | 121.6602 | 121.6965 | 91.3509 | -121.8166 | 121.7077 | 121.7148 | 121.7592 | 29.5869 | -122.1026
1474.6406 | 121.9025 | -121.7834 | 0.12817 | 1.4211e-13 | -0.030087 | -0.0010855 | 0.059517 | -0.008132 | 0.058046 | -0.23586 | -0.0037514 | -0.0026023 | 0.06021 | 0.029696 | 0.057772 | -120.9279 | -30.3273 | -121.3603 | 0.024657 | -0.022536 | 0.022922 | -121.7617 | -119.7047 | -93.6663 | -120.6596 | 0.020409 | 0.032021 | 0.07643 | -122.0477 | 0.021733 | -0.10352 | 0.85554 | 0.42313 | 0.4014 | -0.15071 | -0.10525 | -0.26424 | -0.10777 | 2.0787 | 1.1239 | 1.3881 | -0.096153 | -0.051744 | 121.8081 | 121.7609 | 121.8064 | 91.4562 | -121.8899 | 121.8039 | 121.8155 | 121.8599 | 28.1171 | -122.1759
1476.3125 | 121.9208 | -121.756 | 0.1236 | 1.4211e-13 | -0.029874 | -0.00087189 | 0.059303 | -0.0083458 | 0.058473 | -0.21297 | -0.003965 | -0.0026023 | 0.059997 | 0.02991 | 0.057986 | -120.9188 | -30.3822 | -121.3695 | 0.020079 | -0.022536 | 0.018344 | -121.748 | -119.5949 | -95.0811 | -120.6504 | 0.024988 | 0.032021 | 0.081008 | -122.0568 | 0.008004 | -0.10352 | 0.83723 | 0.38651 | 0.37851 | -0.14613 | -0.10525 | -0.30086 | -0.098608 | 2.1611 | 1.1056 | 1.4064 | -0.091575 | -0.042588 | 121.7761 | 121.7334 | 121.7743 | 91.3738 | -121.8716 | 121.781 | 121.788 | 121.837 | 26.6749 | -122.1804
1478.0625 | 121.9711 | -121.7377 | 0.091553 | 1.4211e-13 | -0.029874 | -0.00087189 | 0.059517 | -0.0083458 | 0.058473 | -0.22823 | -0.0035378 | -0.0023887 | 0.059783 | 0.030124 | 0.058199 | -120.9325 | -30.3868 | -121.3695 | 0.020079 | -0.022536 | 0.013765 | -121.748 | -119.4392 | -96.0427 | -120.5634 | 0.024988 | 0.032021 | 0.081008 | -122.0614 | -0.010306 | -0.071474 | 0.80518 | 0.3682 | 0.37851 | -0.11409 | -0.077788 | -0.32375 | -0.066565 | 2.2985 | 1.1743 | 1.498 | -0.059532 | -0.010545 | 121.7578 | 121.7151 | 121.7514 | 91.3509 | -121.8395 | 121.7627 | 121.7697 | 121.8187 | 25.695 | -122.153
1479.8125 | 122.0123 | -121.7148 | 0.091553 | 1.4211e-13 | -0.02966 | -0.00065809 | 0.060158 | -0.0083458 | 0.058046 | -0.23586 | -0.003965 | -0.0023887 | 0.059997 | 0.029696 | 0.058199 | -120.9233 | -30.4371 | -121.374 | 0.020079 | -0.017957 | 0.027501 | -121.748 | -119.311 | -96.409 | -120.4993 | 0.020409 | 0.027442 | 0.07643 | -122.0523 | -0.033194 | -0.071474 | 0.79145 | 0.34073 | 0.37393 | -0.10951 | -0.064052 | -0.33748 | -0.071144 | 2.4038 | 1.2155 | 1.5529 | -0.064111 | -0.015123 | 121.7349 | 121.6968 | 121.7423 | 91.2776 | -121.8395 | 121.7352 | 121.7422 | 121.7912 | 25.3058 | -122.1438
1481.5 | 121.9391 | -121.7606 | 0.1236 | 1.4211e-13 | -0.029874 | -0.0010855 | 0.059731 | -0.008132 | 0.058046 | -0.23586 | -0.003965 | -0.0021751 | 0.059783 | 0.02991 | 0.057986 | -120.9233 | -30.4692 | -121.3695 | 0.024657 | -0.017957 | 0.027501 | -121.7571 | -119.1645 | -97.2011 | -120.4032 | 0.029566 | 0.032021 | 0.07643 | -122.0477 | 0.003424 | -0.098939 | 0.83723 | 0.39109 | 0.38766 | -0.14155 | -0.096095 | -0.28713 | -0.09403 | 2.5961 | 1.3574 | 1.6445 | -0.091575 | -0.047166 | 121.7852 | 121.7426 | 121.7881 | 91.2914 | -121.8807 | 121.7901 | 121.7926 | 121.837 | 24.5595 | -122.1713
1483.25 | 121.9345 | -121.7606 | 0.11444 | 1.4211e-13 | -0.029874 | -0.00087189 | 0.059731 | -0.0077048 | 0.058046 | -0.22823 | -0.0037514 | -0.0021751 | 0.059997 | 0.02991 | 0.057986 | -120.9325 | -30.4738 | -121.374 | 0.020079 | -0.022536 | 0.013765 | -121.7526 | -119.0088 | -95.9007 | -120.2795 | 0.024988 | 0.032021 | 0.07643 | -122.0523 | 0.008003 | -0.094362 | 0.82807 | 0.38651 | 0.37851 | -0.13698 | -0.10068 | -0.2917 | -0.089453 | 2.7518 | 1.481 | 1.7727 | -0.08242 | -0.038011 | 121.7806 | 121.738 | 121.7743 | 91.2868 | -121.867 | 121.7855 | 121.7926 | 121.837 | 25.8598 | -122.1667
1484.9375 | 121.9757 | -121.7697 | 0.10071 | 1.4211e-13 | -0.029874 | -0.0012991 | 0.059731 | -0.0077048 | 0.058046 | -0.22823 | -0.003965 | -0.0021751 | 0.059997 | 0.030551 | 0.058627 | -120.9279 | -30.5287 | -121.3695 | 0.020079 | -0.022536 | 0.027501 | -121.7571 | -118.8485 | -95.745 | -120.1651 | 0.029566 | 0.032021 | 0.07643 | -122.0523 | 0.012579 | -0.080629 | 0.8418 | 0.40024 | 0.38766 | -0.12324 | -0.073207 | -0.28255 | -0.071142 | 2.9212 | 1.6046 | 1.8872 | -0.068687 | -0.024278 | 121.7898 | 121.7472 | 121.7972 | 91.241 | -121.8578 | 121.7993 | 121.8017 | 121.8461 | 26.0247 | -122.153
1486.6875 | 121.994 | -121.7148 | 0.091553 | 1.4211e-13 | -0.030301 | -0.00087189 | 0.059731 | -0.008132 | 0.058259 | -0.22823 | -0.003965 | -0.0021751 | 0.059783 | 0.030551 | 0.058413 | -120.9325 | -30.5333 | -121.3695 | 0.029236 | -0.027115 | 0.027501 | -121.7571 | -118.67 | -95.745 | -120.0506 | 0.029566 | 0.032021 | 0.07643 | -122.0568 | -0.042352 | -0.062317 | 0.78229 | 0.34531 | 0.38766 | -0.11867 | -0.064052 | -0.34206 | -0.061987 | 3.0448 | 1.6642 | 2.0062 | -0.059532 | -0.015123 | 121.744 | 121.6877 | 121.7423 | 91.1815 | -121.8487 | 121.7443 | 121.7468 | 121.7912 | 25.9697 | -122.1484
1488.4219 | 122.0673 | -121.701 | 0.086975 | 1.4211e-13 | -0.02966 | -0.00087189 | 0.059731 | -0.008132 | 0.058046 | -0.23586 | -0.0035378 | -0.0021751 | 0.060424 | 0.030337 | 0.058627 | -120.9279 | -30.5425 | -121.3695 | 0.020079 | -0.022536 | 0.03208 | -121.7526 | -118.496 | -95.8824 | -119.927 | 0.020409 | 0.032021 | 0.085587 | -122.0568 | -0.051506 | -0.066896 | 0.77314 | 0.33158 | 0.38309 | -0.10951 | -0.054895 | -0.35579 | -0.066566 | 3.2051 | 1.7741 | 2.1299 | -0.054954 | -0.001388 | 121.7211 | 121.6785 | 121.7331 | 91.1586 | -121.8395 | 121.7215 | 121.7331 | 121.7866 | 25.8186 | -122.1438
1490.0938 | 121.9025 | -121.7606 | 0.11902 | 1.4211e-13 | -0.029874 | -0.00087189 | 0.059303 | -0.0079184 | 0.058046 | -0.21297 | -0.0037514 | -0.0017477 | 0.06021 | 0.030337 | 0.059267 | -120.9325 | -30.5745 | -121.374 | 0.024657 | -0.017957 | 0.018344 | -121.7526 | -118.2808 | -96.3586 | -119.7942 | 0.024988 | 0.027442 | 0.07643 | -122.0614 | 0.008003 | -0.094362 | 0.82807 | 0.38651 | 0.37851 | -0.13698 | -0.10068 | -0.30086 | -0.094031 | 3.4798 | 1.9664 | 2.2672 | -0.091577 | -0.042589 | 121.7852 | 121.7426 | 121.7789 | 91.1861 | -121.8716 | 121.7855 | 121.788 | 121.837 | 25.402 | -122.1804
1491.8281 | 121.9391 | -121.7514 | 0.10986 | 1.4211e-13 | -0.030087 | -0.0010855 | 0.059945 | -0.0079184 | 0.058259 | -0.24349 | -0.0037514 | -0.0013203 | 0.06021 | 0.030551 | 0.05884 | -120.9325 | -30.6432 | -121.3786 | 0.015501 | -0.022536 | 0.018344 | -121.7663 | -118.0289 | -96.4135 | -119.6935 | 0.034145 | 0.0366 | 0.07643 | -122.066 | -0.014889 | -0.094362 | 0.81891 | 0.37278 | 0.38767 | -0.1324 | -0.091519 | -0.3146 | -0.075718 | 3.7225 | 2.0579 | 2.3725 | -0.073263 | -0.033433 | 121.7669 | 121.7289 | 121.7697 | 91.1082 | -121.8762 | 121.7855 | 121.788 | 121.8278 | 25.3379 | -122.1759
1493.5625 | 121.9757 | -121.7102 | 0.10986 | 1.4211e-13 | -0.029874 | -0.0010855 | 0.059517 | -0.008132 | 0.058046 | -0.2206 | -0.003965 | -0.0015341 | 0.059997 | 0.030765 | 0.059267 | -120.9325 | -30.6523 | -121.374 | 0.020079 | -0.022536 | 0.027501 | -121.7526 | -117.8229 | -93.5839 | -119.4371 | 0.024988 | 0.041178 | 0.085587 | -122.066 | -0.042351 | -0.089784 | 0.77772 | 0.33616 | 0.37851 | -0.1324 | -0.082362 | -0.35579 | -0.084875 | 3.8873 | 2.2732 | 2.6289 | -0.068685 | -0.024276 | 121.7303 | 121.6877 | 121.7377 | 91.0579 | -121.8624 | 121.7352 | 121.7514 | 121.7958 | 28.1263 | -122.1759
1495.2969 | 122.0673 | -121.7468 | 0.073242 | 1.4211e-13 | -0.030301 | -0.0012991 | 0.059731 | -0.008132 | 0.058259 | -0.2206 | -0.003965 | -0.0015341 | 0.06021 | 0.030978 | 0.059267 | -120.9233 | -30.6981 | -121.374 | 0.020079 | -0.013378 | 0.027501 | -121.7663 | -117.6169 | -91.789 | -119.199 | 0.029566 | 0.027442 | 0.071851 | -122.0614 | -0.019467 | -0.053163 | 0.82349 | 0.37278 | 0.39225 | -0.08662 | -0.045741 | -0.31459 | -0.043676 | 4.13 | 2.5479 | 2.8625 | -0.0458 | -0.001391 | 121.7669 | 121.7334 | 121.7743 | 91.0487 | -121.8395 | 121.7764 | 121.7743 | 121.8187 | 29.9578 | -122.1347
1496.9844 | 122.0352 | -121.7468 | 0.10071 | 1.4211e-13 | -0.030301 | -0.0010855 | 0.059731 | -0.0085594 | 0.058259 | -0.22823 | -0.0035378 | -0.0017477 | 0.059997 | 0.031192 | 0.059481 | -120.9325 | -30.7119 | -121.3695 | 0.020079 | -0.017957 | 0.027501 | -121.7663 | -117.4245 | -90.7497 | -118.9929 | 0.024988 | 0.022864 | 0.07643 | -122.0614 | -0.019467 | -0.080629 | 0.81434 | 0.37736 | 0.39682 | -0.11867 | -0.073207 | -0.31459 | -0.07572 | 4.3223 | 2.7539 | 3.0685 | -0.077844 | -0.024278 | 121.7669 | 121.7289 | 121.7743 | 91.035 | -121.867 | 121.7718 | 121.7697 | 121.8233 | 30.9972 | -122.1621
1498.7344 | 122.081 | -121.7239 | 0.091553 | 1.4211e-13 | -0.030087 | -0.00065809 | 0.059517 | -0.0083458 | 0.058259 | -0.24349 | -0.0035378 | -0.0015341 | 0.060424 | 0.031619 | 0.059695 | -120.9233 | -30.7256 | -121.3649 | 0.024657 | -0.022536 | 0.036658 | -121.7571 | -117.1361 | -90.0949 | -118.7915 | 0.024988 | 0.0366 | 0.07643 | -122.066 | -0.033197 | -0.066896 | 0.80061 | 0.35905 | 0.39224 | -0.11409 | -0.054895 | -0.34206 | -0.066565 | 4.5879 | 2.9325 | 3.2745 | -0.054953 | -0.015123 | 121.7486 | 121.7014 | 121.7606 | 90.9983 | -121.8487 | 121.7489 | 121.7605 | 121.8004 | 31.629 | -122.1576
1500.4844 | 122.0581 | -121.7148 | 0.10071 | 1.4211e-13 | -0.030301 | -0.0010855 | 0.059731 | -0.0079184 | 0.058259 | -0.23586 | -0.0037514 | -0.0015341 | 0.059997 | 0.031619 | 0.060122 | -120.9279 | -30.7302 | -121.374 | 0.020079 | -0.013378 | 0.018344 | -121.7617 | -116.843 | -88.1444 | -118.5396 | 0.024988 | 0.032021 | 0.085587 | -122.066 | -0.046931 | -0.080629 | 0.78687 | 0.34073 | 0.38767 | -0.11409 | -0.082364 | -0.35122 | -0.07572 | 4.8717 | 3.1752 | 3.5264 | -0.068687 | -0.015121 | 121.7349 | 121.7014 | 121.7331 | 90.9846 | -121.8624 | 121.7398 | 121.7468 | 121.8004 | 33.5704 | -122.1667
1502.2344 | 122.0032 | -121.7514 | 0.09613 | 1.4211e-13 | -0.030087 | -0.0010855 | 0.059517 | -0.008132 | 0.058259 | -0.23586 | -0.0035378 | -0.0013203 | 0.06021 | 0.031833 | 0.060336 | -120.9325 | -30.7805 | -121.3695 | 0.020079 | -0.017957 | 0.022922 | -121.7571 | -116.4493 | -87.4805 | -118.2832 | 0.029566 | 0.0366 | 0.085587 | -122.0614 | -0.005731 | -0.076051 | 0.81891 | 0.38193 | 0.38766 | -0.11409 | -0.073208 | -0.31002 | -0.066564 | 5.3021 | 3.4682 | 3.7782 | -0.05953 | -0.010543 | 121.7715 | 121.7334 | 121.7743 | 90.9709 | -121.8533 | 121.781 | 121.788 | 121.837 | 34.2709 | -122.1576
1503.9219 | 121.9254 | -121.7651 | 0.1236 | 1.4211e-13 | -0.030515 | -0.00087189 | 0.059731 | -0.008132 | 0.058046 | -0.23586 | -0.0041788 | -0.0013203 | 0.059997 | 0.03226 | 0.060763 | -120.9188 | -30.7943 | -121.3649 | 0.029236 | -0.027115 | 0.027501 | -121.7571 | -116.0784 | -86.9173 | -118.036 | 0.024988 | 0.032021 | 0.07643 | -122.066 | 0.008002 | -0.09436 | 0.84638 | 0.40024 | 0.39224 | -0.15071 | -0.096095 | -0.30086 | -0.098608 | 5.6867 | 3.7292 | 4.03 | -0.091575 | -0.047166 | 121.7944 | 121.738 | 121.7926 | 90.9709 | -121.8807 | 121.7901 | 121.7972 | 121.8416 | 34.8478 | -122.1896
1505.6719 | 121.9299 | -121.7743 | 0.14191 | 1.4211e-13 | -0.030301 | -0.0010855 | 0.059731 | -0.008132 | 0.058046 | -0.22823 | -0.0037514 | -0.00089313 | 0.06021 | 0.032474 | 0.060763 | -120.9279 | -30.8584 | -121.3695 | 0.024657 | -0.022536 | 0.022922 | -121.7571 | -115.6388 | -86.2625 | -117.7292 | 0.029566 | 0.0366 | 0.085587 | -122.0614 | 0.017157 | -0.11725 | 0.84638 | 0.40482 | 0.38766 | -0.16444 | -0.11899 | -0.28713 | -0.11234 | 6.1354 | 4.0451 | 4.3322 | -0.10531 | -0.05632 | 121.7989 | 121.7518 | 121.7972 | 90.9159 | -121.899 | 121.8039 | 121.8109 | 121.8599 | 35.5118 | -122.2033
1507.4219 | 121.9528 | -121.7789 | 0.11444 | 1.4211e-13 | -0.030301 | -0.00087189 | 0.059517 | -0.0083458 | 0.058259 | -0.23586 | -0.0035378 | -0.0011067 | 0.060424 | 0.032901 | 0.061831 | -120.9279 | -30.8309 | -121.3649 | 0.020079 | -0.013378 | 0.027501 | -121.7571 | -115.1398 | -84.9576 | -117.4041 | 0.015831 | 0.0366 | 0.081008 | -122.0568 | 0.021735 | -0.094362 | 0.85096 | 0.41398 | 0.39224 | -0.12782 | -0.08694 | -0.27797 | -0.09861 | 6.6391 | 4.3748 | 4.6527 | -0.077841 | -0.033433 | 121.7989 | 121.7655 | 121.8064 | 90.948 | -121.8716 | 121.7947 | 121.8155 | 121.8599 | 36.8213 | -122.1713
1509.1094 | 121.9116 | -121.7285 | 0.12817 | 1.4211e-13 | -0.030087 | -0.00087189 | 0.059303 | -0.0085594 | 0.058046 | -0.21297 | -0.0037514 | -0.00089313 | 0.06021 | 0.032901 | 0.062259 | -120.9188 | -30.8584 | -121.3649 | 0.015501 | -0.022536 | 0.018344 | -121.7663 | -114.5766 | -84.138 | -117.0973 | 0.024988 | 0.027442 | 0.081008 | -122.066 | -0.037777 | -0.11267 | 0.80976 | 0.36362 | 0.4014 | -0.15071 | -0.10983 | -0.33748 | -0.10319 | 7.1519 | 4.6312 | 4.9687 | -0.10073 | -0.047166 | 121.744 | 121.706 | 121.7469 | 90.8701 | -121.8945 | 121.7535 | 121.756 | 121.8095 | 37.5905 | -122.1942
1510.8438 | 121.9528 | -121.7468 | 0.11444 | 1.4211e-13 | -0.030301 | -0.0015129 | 0.059517 | -0.008132 | 0.058046 | -0.23586 | -0.0035378 | -0.00046573 | 0.060424 | 0.033329 | 0.062472 | -120.9233 | -30.9042 | -121.374 | 0.024657 | -0.013378 | 0.027501 | -121.7617 | -113.9585 | -83.6893 | -116.7265 | 0.024988 | 0.032021 | 0.081008 | -122.066 | -0.014888 | -0.089784 | 0.82349 | 0.37278 | 0.38767 | -0.12782 | -0.08694 | -0.31917 | -0.089453 | 7.7884 | 5.0204 | 5.3395 | -0.08242 | -0.033433 | 121.7715 | 121.7334 | 121.7743 | 90.8427 | -121.8762 | 121.7718 | 121.7788 | 121.8278 | 38.0575 | -122.1804
1512.5781 | 122.0535 | -121.7239 | 0.07782 | 1.4211e-13 | -0.030515 | -0.0010855 | 0.059517 | -0.0085594 | 0.058046 | -0.23586 | -0.003965 | -3.853e-05 | 0.060424 | 0.033542 | 0.063327 | -120.9279 | -30.9133 | -121.374 | 0.024657 | -0.013378 | 0.022922 | -121.7617 | -113.2854 | -83.1902 | -116.3281 | 0.024988 | 0.032021 | 0.081008 | -122.0706 | -0.037776 | -0.053163 | 0.79603 | 0.34989 | 0.38767 | -0.091198 | -0.054898 | -0.34664 | -0.052832 | 8.4385 | 5.3958 | 5.7425 | -0.045799 | 0.003188 | 121.7486 | 121.7106 | 121.7469 | 90.8106 | -121.8395 | 121.7489 | 121.756 | 121.8049 | 38.5337 | -122.1484
1514.3281 | 121.9666 | -121.7422 | 0.13275 | 1.4211e-13 | -0.030728 | -0.00087189 | 0.059517 | -0.0083458 | 0.058259 | -0.22823 | -0.0037514 | -0.00025213 | 0.060424 | 0.034183 | 0.063968 | -120.9233 | -30.9408 | -121.374 | 0.015501 | -0.013378 | 0.022922 | -121.7663 | -112.5162 | -82.6179 | -115.8657 | 0.024988 | 0.032021 | 0.085587 | -122.0614 | -0.024044 | -0.11725 | 0.81892 | 0.3682 | 0.39225 | -0.14613 | -0.10983 | -0.31917 | -0.10776 | 9.2261 | 5.8766 | 6.1958 | -0.10073 | -0.047164 | 121.7578 | 121.7289 | 121.7652 | 90.8015 | -121.899 | 121.7672 | 121.7743 | 121.8278 | 39.1244 | -122.1942
1516 | 121.9528 | -121.7697 | 0.10071 | 1.4211e-13 | -0.030301 | -0.0010855 | 0.059517 | -0.0085594 | 0.058259 | -0.2206 | -0.0033242 | 0.00038887 | 0.06021 | 0.034611 | 0.064822 | -120.9233 | -30.982 | -121.3695 | 0.033814 | -0.022536 | 0.027501 | -121.7663 | -111.7424 | -82.215 | -115.3941 | 0.029566 | 0.032021 | 0.081008 | -122.0706 | 0.003421 | -0.066894 | 0.84638 | 0.40024 | 0.39682 | -0.12324 | -0.073207 | -0.30086 | -0.071142 | 10.0273 | 6.3757 | 6.6765 | -0.068687 | -0.0197 | 121.8035 | 121.7472 | 121.7972 | 90.7877 | -121.867 | 121.7993 | 121.8017 | 121.8507 | 39.5548 | -122.1713
1517.75 | 121.9254 | -121.7651 | 0.13733 | 1.4211e-13 | -0.030301 | -0.00087189 | 0.059945 | -0.0083458 | 0.058046 | -0.2206 | -0.0035378 | 0.00060247 | 0.060638 | 0.034611 | 0.065677 | -120.9233 | -31.0644 | -121.3695 | 0.024657 | -0.017957 | 0.027501 | -121.7663 | -110.964 | -80.1454 | -114.8996 | 0.024988 | 0.0366 | 0.07643 | -122.0614 | -0.001156 | -0.11267 | 0.8418 | 0.39567 | 0.39682 | -0.15529 | -0.10983 | -0.29628 | -0.11234 | 10.8012 | 6.8656 | 7.1619 | -0.10073 | -0.060899 | 121.7898 | 121.7472 | 121.7926 | 90.7007 | -121.9036 | 121.7901 | 121.8017 | 121.8416 | 41.6198 | -122.1987
1519.5 | 122.0352 | -121.7285 | 0.091553 | 1.4211e-13 | -0.030301 | -0.0012991 | 0.059945 | -0.0083458 | 0.058473 | -0.22823 | -0.0035378 | 0.0010299 | 0.060424 | 0.035252 | 0.066745 | -120.9233 | -31.0553 | -121.3649 | 0.020079 | -0.017957 | 0.027501 | -121.7571 | -110.0025 | -75.7681 | -114.0388 | 0.029566 | 0.0366 | 0.090166 | -122.066 | -0.028619 | -0.071474 | 0.80518 | 0.36362 | 0.39224 | -0.10951 | -0.064052 | -0.33748 | -0.061987 | 11.7261 | 7.6898 | 8.0272 | -0.054953 | -0.001387 | 121.7486 | 121.7106 | 121.756 | 90.6733 | -121.8487 | 121.7581 | 121.7651 | 121.8187 | 45.9604 | -122.1576
1521.1719 | 122.0581 | -121.7056 | 0.073242 | 1.4211e-13 | -0.030515 | -0.0012991 | 0.059517 | -0.008132 | 0.057618 | -0.22823 | -0.0035378 | 0.00060247 | 0.060638 | 0.03632 | 0.067386 | -120.9188 | -31.0461 | -121.3603 | 0.029236 | -0.017957 | 0.027501 | -121.7663 | -109.0821 | -72.2792 | -113.3107 | 0.020409 | 0.0366 | 0.090166 | -122.066 | -0.060666 | -0.044006 | 0.78687 | 0.34531 | 0.40598 | -0.091199 | -0.045741 | -0.36037 | -0.052833 | 12.6235 | 8.3949 | 8.7553 | -0.036642 | 0.016924 | 121.7349 | 121.6877 | 121.7331 | 90.6595 | -121.8395 | 121.726 | 121.7422 | 121.7958 | 49.4265 | -122.1392
1522.9062 | 121.9162 | -121.7468 | 0.13275 | 1.4211e-13 | -0.030301 | -0.0010855 | 0.059303 | -0.008132 | 0.058259 | -0.23586 | -0.0033242 | 0.0012435 | 0.061065 | 0.036961 | 0.068882 | -120.9233 | -31.1056 | -121.374 | 0.029236 | -0.013378 | 0.03208 | -121.7571 | -108.0336 | -70.3927 | -112.5781 | 0.029566 | 0.032021 | 0.090166 | -122.066 | -0.010309 | -0.10352 | 0.82349 | 0.37278 | 0.38309 | -0.14613 | -0.10067 | -0.31917 | -0.10319 | 13.7132 | 9.1687 | 9.4879 | -0.10073 | -0.042585 | 121.7761 | 121.7334 | 121.7789 | 90.6412 | -121.8899 | 121.7764 | 121.7788 | 121.837 | 51.3541 | -122.1988
1524.6406 | 122.0627 | -121.7377 | 0.07782 | 1.4211e-13 | -0.030301 | -0.0010855 | 0.059517 | -0.0083458 | 0.058046 | -0.2206 | -0.0035378 | 0.0012435 | 0.060424 | 0.037388 | 0.069736 | -120.9188 | -31.101 | -121.3649 | 0.020079 | -0.013378 | 0.027501 | -121.7617 | -106.9897 | -68.5155 | -111.9051 | 0.029566 | 0.0366 | 0.085587 | -122.066 | -0.024043 | -0.057741 | 0.81892 | 0.37278 | 0.39682 | -0.091198 | -0.050319 | -0.32833 | -0.048254 | 14.748 | 9.8326 | 10.1609 | -0.04122 | 0.007767 | 121.7578 | 121.7243 | 121.7652 | 90.6366 | -121.8395 | 121.7672 | 121.7743 | 121.8233 | 53.2222 | -122.1438
1526.375 | 122.049 | -121.7102 | 0.10071 | 1.4211e-13 | -0.030087 | -0.00087189 | 0.059945 | -0.0083458 | 0.058046 | -0.2206 | -0.0037514 | 0.0018845 | 0.060638 | 0.03803 | 0.071446 | -120.9188 | -31.1377 | -121.3649 | 0.020079 | -0.017957 | 0.027501 | -121.7663 | -105.7992 | -66.8717 | -111.1633 | 0.034145 | 0.032021 | 0.081008 | -122.0568 | -0.056088 | -0.080629 | 0.79145 | 0.34531 | 0.4014 | -0.11867 | -0.073207 | -0.34664 | -0.066563 | 15.911 | 10.5469 | 10.8935 | -0.068687 | -0.0197 | 121.7303 | 121.6922 | 121.7377 | 90.5725 | -121.867 | 121.7443 | 121.7422 | 121.7912 | 54.8385 | -122.1575
1528.0469 | 121.9894 | -121.7239 | 0.086975 | 1.4211e-13 | -0.030515 | -0.0010855 | 0.059517 | -0.0083458 | 0.057832 | -0.22823 | -0.0035378 | 0.0023117 | 0.060851 | 0.038671 | 0.072728 | -120.9188 | -31.1422 | -121.3557 | 0.029236 | -0.017957 | 0.027501 | -121.7571 | -104.6591 | -65.7911 | -110.3758 | 0.034145 | 0.032021 | 0.081008 | -122.066 | -0.033197 | -0.057739 | 0.80518 | 0.3682 | 0.4014 | -0.10493 | -0.059474 | -0.34206 | -0.05283 | 17.0648 | 11.3482 | 11.6902 | -0.054954 | -0.005967 | 121.7532 | 121.706 | 121.7514 | 90.5817 | -121.8441 | 121.7581 | 121.756 | 121.8049 | 55.9328 | -122.153
1529.7969 | 122.0398 | -121.7285 | 0.10071 | 1.4211e-13 | -0.030515 | -0.0012991 | 0.059517 | -0.0085594 | 0.058473 | -0.23586 | -0.0033242 | 0.0023117 | 0.061065 | 0.039525 | 0.074223 | -120.9142 | -31.1651 | -121.3603 | 0.029236 | -0.013378 | 0.03208 | -121.7571 | -103.4183 | -65.0402 | -109.5379 | 0.034145 | 0.041178 | 0.081008 | -122.0706 | -0.028619 | -0.071472 | 0.81434 | 0.3682 | 0.39682 | -0.11409 | -0.068628 | -0.34206 | -0.066563 | 18.3102 | 12.1906 | 12.5327 | -0.05953 | -0.0197 | 121.7578 | 121.7151 | 121.7606 | 90.5634 | -121.8578 | 121.7627 | 121.7697 | 121.8095 | 56.6883 | -122.1713
1531.4688 | 121.9254 | -121.7514 | 0.11902 | 1.4211e-13 | -0.030728 | -0.00087189 | 0.059517 | -0.0083458 | 0.058259 | -0.23586 | -0.002897 | 0.0027391 | 0.061278 | 0.039953 | 0.075719 | -120.9142 | -31.1926 | -121.3695 | 0.024657 | -0.017957 | 0.03208 | -121.7617 | -102.1271 | -64.3443 | -108.6588 | 0.034145 | 0.0366 | 0.085587 | -122.0614 | -0.01031 | -0.094362 | 0.83723 | 0.38193 | 0.39224 | -0.13698 | -0.086939 | -0.31002 | -0.084874 | 19.6243 | 13.0926 | 13.4026 | -0.082419 | -0.033432 | 121.7761 | 121.7334 | 121.7835 | 90.5588 | -121.8807 | 121.7855 | 121.788 | 121.837 | 57.4072 | -122.1804
1533.2031 | 121.9757 | -121.7377 | 0.13733 | 1.4211e-13 | -0.030515 | -0.0012991 | 0.059731 | -0.008132 | 0.058046 | -0.22823 | -0.0031106 | 0.0027391 | 0.060851 | 0.040807 | 0.077642 | -120.905 | -31.2659 | -121.3649 | 0.020079 | -0.013378 | 0.036658 | -121.7617 | -100.8542 | -63.3644 | -107.7339 | 0.034145 | 0.032021 | 0.085587 | -122.0614 | -0.024043 | -0.11725 | 0.83265 | 0.37278 | 0.39682 | -0.15071 | -0.10067 | -0.32375 | -0.10318 | 20.8835 | 14.0038 | 14.3275 | -0.10531 | -0.051742 | 121.7578 | 121.7243 | 121.7743 | 90.4718 | -121.899 | 121.7718 | 121.7697 | 121.8233 | 58.3733 | -122.1987
1534.9531 | 122.0581 | -121.701 | 0.073242 | 1.4211e-13 | -0.030728 | -0.00087189 | 0.059517 | -0.008132 | 0.058046 | -0.2206 | -0.0033242 | 0.0035937 | 0.060638 | 0.041448 | 0.079351 | -120.9096 | -31.2888 | -121.3512 | 0.024657 | -0.013378 | 0.027501 | -121.7617 | -99.4394 | -62.1465 | -106.6716 | 0.038723 | 0.0366 | 0.085587 | -122.0568 | -0.060664 | -0.048585 | 0.79145 | 0.34989 | 0.41056 | -0.08662 | -0.045741 | -0.35579 | -0.034519 | 22.2617 | 15.0294 | 15.3852 | -0.036642 | 0.012345 | 121.7257 | 121.6877 | 121.7286 | 90.4123 | -121.835 | 121.7398 | 121.7377 | 121.7866 | 59.5546 | -122.1301
1536.6875 | 121.9299 | -121.7606 | 0.1236 | 1.4211e-13 | -0.030942 | -0.00065809 | 0.059303 | -0.0083458 | 0.058046 | -0.23586 | -0.002897 | 0.0033801 | 0.061065 | 0.042089 | 0.081701 | -120.905 | -31.33 | -121.3603 | 0.029236 | -0.008799 | 0.036658 | -121.7617 | -97.9421 | -61.2124 | -105.5773 | 0.034145 | 0.0366 | 0.090166 | -122.0568 | -0.001155 | -0.09436 | 0.85554 | 0.40025 | 0.4014 | -0.13239 | -0.086938 | -0.29628 | -0.089451 | 23.8184 | 16.1833 | 16.4795 | -0.086996 | -0.03343 | 121.7898 | 121.7518 | 121.7972 | 90.4306 | -121.8853 | 121.7947 | 121.7972 | 121.8507 | 60.5481 | -122.1804
1538.4219 | 121.9254 | -121.756 | 0.10529 | 1.4211e-13 | -0.030515 | -0.0012991 | 0.059517 | -0.008132 | 0.058259 | -0.23586 | -0.002897 | 0.0040211 | 0.061065 | 0.043158 | 0.083838 | -120.9096 | -31.3437 | -121.3603 | 0.029236 | 0.000359 | 0.036658 | -121.7571 | -96.39 | -60.2371 | -104.428 | 0.029566 | 0.041178 | 0.085587 | -122.066 | -0.001154 | -0.07605 | 0.84638 | 0.39567 | 0.39682 | -0.10493 | -0.068628 | -0.31002 | -0.07572 | 25.366 | 17.3279 | 17.638 | -0.064108 | -0.019699 | 121.7852 | 121.7563 | 121.7926 | 90.4123 | -121.8624 | 121.7855 | 121.7972 | 121.8416 | 61.5188 | -122.1713
1540.1094 | 122.049 | -121.7102 | 0.09613 | 1.4211e-13 | -0.030728 | -0.00087189 | 0.059731 | -0.0083458 | 0.058259 | -0.23586 | -0.002897 | 0.0042347 | 0.061065 | 0.044226 | 0.086188 | -120.9004 | -31.4078 | -121.3603 | 0.029236 | -0.013378 | 0.03208 | -121.7526 | -94.8561 | -59.0787 | -103.1826 | 0.038723 | 0.041178 | 0.090166 | -122.0523 | -0.042351 | -0.066894 | 0.80976 | 0.34989 | 0.39224 | -0.10951 | -0.06405 | -0.34206 | -0.057407 | 26.8541 | 18.5276 | 18.8696 | -0.054952 | -0.005964 | 121.7394 | 121.6968 | 121.7423 | 90.3024 | -121.8487 | 121.7489 | 121.7514 | 121.8004 | 62.6315 | -122.1484
1541.8438 | 121.9757 | -121.7377 | 0.10529 | 1.4211e-13 | -0.030942 | -0.00044449 | 0.059517 | -0.0083458 | 0.058046 | -0.22823 | -0.002897 | 0.0053031 | 0.061492 | 0.045294 | 0.089179 | -120.9096 | -31.4124 | -121.3557 | 0.033814 | 0.000359 | 0.041237 | -121.7571 | -93.0109 | -57.8242 | -101.7358 | 0.034145 | 0.045757 | 0.094744 | -122.0523 | -0.019464 | -0.071472 | 0.82807 | 0.38194 | 0.4014 | -0.10493 | -0.064049 | -0.31459 | -0.071141 | 28.7268 | 20.0019 | 20.3165 | -0.059529 | -0.010542 | 121.7715 | 121.738 | 121.7789 | 90.3253 | -121.8624 | 121.7718 | 121.7834 | 121.8324 | 63.9135 | -122.1575
1543.5938 | 122.0535 | -121.7102 | 0.10986 | 1.4211e-13 | -0.030942 | -0.0010855 | 0.059517 | -0.008773 | 0.057832 | -0.23586 | -0.0026832 | 0.0050893 | 0.061278 | 0.046576 | 0.092384 | -120.8959 | -31.4856 | -121.3466 | 0.029236 | -0.008799 | 0.03208 | -121.7526 | -91.271 | -56.913 | -100.2477 | 0.043302 | 0.0366 | 0.090166 | -122.0477 | -0.042351 | -0.080627 | 0.81434 | 0.36363 | 0.40598 | -0.11866 | -0.077783 | -0.33748 | -0.066561 | 30.4393 | 21.4625 | 21.8 | -0.073263 | -0.019697 | 121.7394 | 121.7014 | 121.7423 | 90.2246 | -121.8624 | 121.7535 | 121.7468 | 121.8004 | 64.7972 | -122.1575
1545.2812 | 121.962 | -121.7468 | 0.13275 | 1.4211e-13 | -0.031156 | -0.0012991 | 0.059517 | -0.0083458 | 0.058046 | -0.22823 | -0.0024696 | 0.0061577 | 0.061492 | 0.047858 | 0.095375 | -120.8867 | -31.504 | -121.3512 | 0.042971 | -0.00422 | 0.036658 | -121.7526 | -89.4624 | -56.1484 | -98.7184 | 0.034145 | 0.0366 | 0.094744 | -122.0523 | -0.00573 | -0.08978 | 0.86012 | 0.39567 | 0.4014 | -0.13697 | -0.096093 | -0.30544 | -0.098606 | 32.2845 | 23.0284 | 23.3339 | -0.096151 | -0.038007 | 121.7898 | 121.7426 | 121.7835 | 90.2429 | -121.8853 | 121.781 | 121.7834 | 121.8416 | 65.5985 | -122.185
1546.9688 | 122.0581 | -121.6965 | 0.10529 | 1.4211e-13 | -0.030942 | -0.0010855 | 0.059517 | -0.0083458 | 0.057832 | -0.2206 | -0.0024696 | 0.0061577 | 0.061492 | 0.049354 | 0.098366 | -120.8959 | -31.5406 | -121.3512 | 0.033814 | 0.000359 | 0.036658 | -121.7526 | -87.8369 | -55.2921 | -97.038 | 0.038723 | 0.050335 | 0.085587 | -122.0431 | -0.056084 | -0.071472 | 0.80061 | 0.34531 | 0.4014 | -0.10493 | -0.068628 | -0.34663 | -0.066563 | 33.8595 | 24.6585 | 25.0051 | -0.054951 | -0.019699 | 121.7303 | 121.6968 | 121.7331 | 90.1559 | -121.8578 | 121.7352 | 121.7468 | 121.7821 | 66.4043 | -122.1484
1548.7188 | 122.0398 | -121.7285 | 0.10529 | 1.4211e-13 | -0.030942 | -0.0010855 | 0.059517 | -0.0083458 | 0.057832 | -0.23586 | -0.0024696 | 0.0067987 | 0.061919 | 0.05085 | 0.10243 | -120.8913 | -31.5452 | -121.3512 | 0.033814 | -0.00422 | 0.041237 | -121.7434 | -86.0741 | -54.5687 | -95.3164 | 0.034145 | 0.045757 | 0.090166 | -122.0431 | -0.014882 | -0.071472 | 0.83723 | 0.37736 | 0.39224 | -0.10951 | -0.064049 | -0.31459 | -0.071141 | 35.6544 | 26.4121 | 26.7267 | -0.059529 | -0.01512 | 121.7623 | 121.7243 | 121.7698 | 90.1834 | -121.8487 | 121.7627 | 121.7743 | 121.8187 | 67.1598 | -122.1484
1550.4688 | 121.9711 | -121.7285 | 0.13275 | 1.4211e-13 | -0.031156 | -0.0010855 | 0.05909 | -0.0085594 | 0.058259 | -0.22823 | -0.002256 | 0.0074395 | 0.061919 | 0.052132 | 0.10627 | -120.8959 | -31.6138 | -121.342 | 0.038393 | 0.000359 | 0.041237 | -121.7434 | -84.4304 | -53.9323 | -93.4941 | 0.043302 | 0.045757 | 0.090166 | -122.0385 | -0.014882 | -0.094358 | 0.83265 | 0.38652 | 0.4014 | -0.13239 | -0.091514 | -0.31001 | -0.089449 | 37.2982 | 28.2344 | 28.5444 | -0.086994 | -0.042585 | 121.7669 | 121.7289 | 121.7698 | 90.1147 | -121.8761 | 121.7718 | 121.7743 | 121.8187 | 67.7963 | -122.1713
1552.1406 | 122.0306 | -121.6644 | 0.11902 | 1.4211e-13 | -0.031156 | -0.0010855 | 0.059731 | -0.0085594 | 0.058046 | -0.22823 | -0.0031106 | 0.0078669 | 0.06021 | 0.12179 | 0.11225 | -120.8638 | -31.6276 | -121.3191 | 0.052128 | 0.014096 | 0.06413 | -121.7159 | -82.7088 | -34.5552 | -3.8338 | 0.043302 | 0.059493 | 0.11764 | -121.9973 | -0.051495 | -0.066891 | 0.80061 | 0.34532 | 0.39682 | -0.10492 | -0.054889 | -0.33289 | -0.075717 | 38.9557 | 117.8306 | 118.1635 | -0.059526 | -0.001382 | 121.7166 | 121.6785 | 121.7286 | 90.0368 | -121.8349 | 121.7077 | 121.7239 | 121.7821 | 87.1093 | -122.1163
1553.8906 | 122.0444 | -121.6782 | 0.10529 | 1.4211e-13 | -0.031156 | -0.0010855 | 0.059945 | -0.008132 | 0.058046 | -0.23586 | -0.0026832 | 0.0082943 | 0.06021 | 0.122 | 0.11631 | -120.8547 | -31.6551 | -121.3145 | 0.047549 | 0.009517 | 0.059551 | -121.7113 | -81.033 | -34.0607 | -3.4995 | 0.057037 | 0.06865 | 0.11306 | -122.0065 | -0.033184 | -0.057737 | 0.8235 | 0.36363 | 0.39682 | -0.095769 | -0.045735 | -0.32831 | -0.048249 | 40.6452 | 118.1786 | 118.5069 | -0.036636 | 0.007773 | 121.7257 | 121.6877 | 121.7377 | 90.0231 | -121.8166 | 121.7352 | 121.7468 | 121.7912 | 87.6175 | -122.1118
1555.625 | 121.8796 | -121.7102 | 0.15106 | 1.4211e-13 | -0.031156 | -0.00065809 | 0.059303 | -0.0083458 | 0.058046 | -0.22823 | -0.0024696 | 0.0087215 | 0.060851 | 0.122 | 0.12037 | -120.8547 | -31.6734 | -121.31 | 0.061284 | 0.018675 | 0.050394 | -121.7068 | -79.5952 | -33.7814 | -3.2843 | 0.057037 | 0.06865 | 0.11764 | -121.9927 | 0.003438 | -0.089778 | 0.85555 | 0.40025 | 0.39682 | -0.13239 | -0.10067 | -0.28253 | -0.094025 | 42.115 | 118.4259 | 118.7084 | -0.082412 | -0.033425 | 121.7715 | 121.7289 | 121.7606 | 90.0368 | -121.8578 | 121.7672 | 121.7789 | 121.8278 | 87.9288 | -122.1438
1557.2969 | 121.8979 | -121.6873 | 0.13733 | 1.4211e-13 | -0.031156 | -0.0010855 | 0.059731 | -0.0083458 | 0.058046 | -0.22823 | -0.0026832 | 0.0091489 | 0.06021 | 0.122 | 0.12465 | -120.8455 | -31.7375 | -121.3008 | 0.056706 | 0.014096 | 0.06413 | -121.7022 | -78.2995 | -33.5982 | -3.1607 | 0.057037 | 0.073228 | 0.11306 | -121.9927 | -0.014871 | -0.080623 | 0.84182 | 0.38652 | 0.40139 | -0.12323 | -0.073199 | -0.30542 | -0.080292 | 43.3878 | 118.5266 | 118.832 | -0.064101 | -0.02427 | 121.744 | 121.7014 | 121.7514 | 89.9499 | -121.8395 | 121.7444 | 121.7605 | 121.8004 | 88.0891 | -122.1301
1558.9844 | 121.9986 | -121.6599 | 0.12817 | 1.4211e-13 | -0.030728 | -0.0015129 | 0.059945 | -0.0083458 | 0.058259 | -0.23586 | -0.002256 | 0.0091489 | 0.06021 | 0.12179 | 0.1287 | -120.8318 | -31.7833 | -121.2916 | 0.056706 | 0.023254 | 0.068708 | -121.6976 | -76.9945 | -33.47 | -3.3347 | 0.061616 | 0.077807 | 0.11764 | -121.9927 | -0.037758 | -0.071468 | 0.82809 | 0.36821 | 0.40597 | -0.10492 | -0.059466 | -0.33289 | -0.066558 | 44.6653 | 118.3251 | 118.658 | -0.050367 | -0.010537 | 121.7166 | 121.6831 | 121.7286 | 89.8766 | -121.8258 | 121.7215 | 121.7377 | 121.7775 | 88.1898 | -122.1209
1560.7188 | 122.0078 | -121.6507 | 0.12817 | 1.4211e-13 | -0.031369 | -0.0010855 | 0.059517 | -0.0083458 | 0.058046 | -0.2206 | -0.0020424 | 0.0095761 | 0.060851 | 0.12179 | 0.13383 | -120.8318 | -31.7878 | -121.2962 | 0.052128 | 0.018675 | 0.06413 | -121.6976 | -75.74 | -33.3281 | -3.179 | 0.061616 | 0.064071 | 0.12222 | -121.979 | -0.046913 | -0.076046 | 0.81893 | 0.35448 | 0.40139 | -0.1095 | -0.064044 | -0.32831 | -0.066558 | 45.9107 | 118.4717 | 118.8 | -0.064103 | -0.005958 | 121.7028 | 121.6694 | 121.7148 | 89.8629 | -121.8258 | 121.7123 | 121.7148 | 121.7729 | 88.3226 | -122.1072
1562.4531 | 121.9299 | -121.6599 | 0.15564 | 1.4211e-13 | -0.031369 | -0.0010855 | 0.059945 | -0.008132 | 0.057832 | -0.22823 | -0.0014014 | 0.010003 | 0.060851 | 0.12158 | 0.13917 | -120.8226 | -31.829 | -121.2825 | 0.052128 | 0.023254 | 0.073287 | -121.6885 | -74.4717 | -33.4975 | -3.4675 | 0.070773 | 0.077807 | 0.12222 | -121.979 | -0.0286 | -0.10351 | 0.83724 | 0.37737 | 0.40597 | -0.13239 | -0.082353 | -0.31915 | -0.084867 | 47.1882 | 118.1924 | 118.5115 | -0.077833 | -0.033424 | 121.712 | 121.6831 | 121.7331 | 89.8308 | -121.8441 | 121.7306 | 121.7377 | 121.7821 | 88.1624 | -122.1346
1564.125 | 121.994 | -121.669 | 0.1236 | 1.4211e-13 | -0.031369 | -0.00087189 | 0.059731 | -0.008132 | 0.057832 | -0.22823 | -0.0014014 | 0.010644 | 0.060638 | 0.12136 | 0.14473 | -120.818 | -31.8702 | -121.2779 | 0.061284 | 0.023254 | 0.068708 | -121.6793 | -73.2308 | -33.3143 | -3.3484 | 0.061616 | 0.06865 | 0.11764 | -121.9698 | -0.010287 | -0.062312 | 0.85098 | 0.3911 | 0.40139 | -0.10034 | -0.054888 | -0.30084 | -0.06198 | 48.4382 | 118.3206 | 118.6214 | -0.054946 | -0.005959 | 121.7303 | 121.6923 | 121.7377 | 89.7988 | -121.8029 | 121.7306 | 121.7377 | 121.7866 | 88.3547 | -122.0934
1565.8594 | 121.8933 | -121.6782 | 0.16022 | 1.4211e-13 | -0.030942 | -0.0012991 | 0.059303 | -0.0083458 | 0.057832 | -0.22823 | -0.00097422 | 0.010217 | 0.061065 | 0.12179 | 0.14986 | -120.818 | -31.8748 | -121.2687 | 0.061284 | 0.027833 | 0.068708 | -121.6793 | -72.0312 | -32.8702 | -3.2614 | 0.070773 | 0.073228 | 0.11306 | -121.9607 | -0.001131 | -0.098933 | 0.86013 | 0.40941 | 0.41054 | -0.13238 | -0.091509 | -0.28252 | -0.089444 | 49.6469 | 118.4167 | 118.6992 | -0.086989 | -0.047158 | 121.7394 | 121.706 | 121.7469 | 89.8033 | -121.8395 | 121.7489 | 121.7514 | 121.7912 | 88.808 | -122.1209
1567.6094 | 121.9391 | -121.637 | 0.13733 | 1.4211e-13 | -0.031369 | -0.00065809 | 0.059517 | -0.0083458 | 0.058046 | -0.23586 | 0.00030758 | 0.010858 | 0.060851 | 0.12136 | 0.15498 | -120.8135 | -31.9115 | -121.2642 | 0.061284 | 0.032411 | 0.073287 | -121.6701 | -70.827 | -32.5314 | -3.1882 | 0.066194 | 0.077807 | 0.12222 | -121.9607 | -0.033172 | -0.076045 | 0.82351 | 0.37279 | 0.40597 | -0.10492 | -0.064042 | -0.32372 | -0.071135 | 50.8099 | 118.4488 | 118.7725 | -0.059522 | -0.015113 | 121.6982 | 121.6694 | 121.7102 | 89.7255 | -121.8075 | 121.7032 | 121.7148 | 121.7592 | 89.1056 | -122.098
1569.2969 | 121.8979 | -121.6782 | 0.16022 | 1.4211e-13 | -0.031156 | -0.0010855 | 0.059303 | -0.0083458 | 0.057618 | -0.22823 | 0.00073498 | 0.010644 | 0.060851 | 0.12115 | 0.16011 | -120.7951 | -31.9206 | -121.2596 | 0.061284 | 0.023254 | 0.06413 | -121.6656 | -69.6182 | -32.1147 | -3.2386 | 0.070773 | 0.077807 | 0.12222 | -121.9515 | 0.012606 | -0.098933 | 0.88302 | 0.41857 | 0.40596 | -0.13696 | -0.096087 | -0.27337 | -0.089444 | 52.0599 | 118.4396 | 118.713 | -0.08241 | -0.038001 | 121.7394 | 121.7014 | 121.7423 | 89.7576 | -121.8258 | 121.7489 | 121.756 | 121.8004 | 89.5635 | -122.1117
1570.9844 | 121.8979 | -121.6599 | 0.16479 | 1.4211e-13 | -0.031369 | -0.0012991 | 0.059303 | -0.0085594 | 0.057832 | -0.22823 | 0.0018032 | 0.010858 | 0.061492 | 0.12115 | 0.16503 | -120.7997 | -31.971 | -121.2596 | 0.061284 | 0.027833 | 0.082444 | -121.661 | -68.5239 | -31.7118 | -3.005 | 0.070773 | 0.086964 | 0.12679 | -121.9424 | -0.001126 | -0.10351 | 0.86013 | 0.40026 | 0.40139 | -0.13696 | -0.082351 | -0.28252 | -0.094022 | 53.1359 | 118.6548 | 118.9373 | -0.077831 | -0.038001 | 121.7211 | 121.6877 | 121.7423 | 89.6889 | -121.8258 | 121.7306 | 121.7468 | 121.7866 | 89.9481 | -122.1072
1572.6562 | 121.9116 | -121.637 | 0.17395 | 1.4211e-13 | -0.031583 | -0.0010855 | 0.059731 | -0.0083458 | 0.057618 | -0.23586 | 0.0026576 | 0.011072 | 0.061278 | 0.12136 | 0.16951 | -120.786 | -31.971 | -121.2459 | 0.065863 | 0.032411 | 0.087023 | -121.661 | -67.3426 | -31.3363 | -2.9226 | 0.070773 | 0.086964 | 0.12222 | -121.9424 | -0.024014 | -0.10809 | 0.85098 | 0.39111 | 0.41512 | -0.14154 | -0.086927 | -0.30541 | -0.10318 | 54.2943 | 118.7143 | 119.0197 | -0.086986 | -0.051734 | 121.7028 | 121.6694 | 121.724 | 89.666 | -121.8349 | 121.7077 | 121.7239 | 121.7592 | 90.3006 | -122.1163
1574.3438 | 121.9986 | -121.6187 | 0.15106 | 1.4211e-13 | -0.031369 | -0.00065809 | 0.059517 | -0.0085594 | 0.057832 | -0.21297 | 0.0037258 | 0.010644 | 0.061492 | 0.12093 | 0.17379 | -120.7906 | -32.0168 | -121.2367 | 0.065863 | 0.032411 | 0.087023 | -121.6518 | -66.2804 | -30.8556 | -3.1516 | 0.070773 | 0.077807 | 0.13595 | -121.9286 | -0.033168 | -0.085199 | 0.82809 | 0.38195 | 0.41512 | -0.11865 | -0.064039 | -0.30998 | -0.080289 | 55.3383 | 118.4671 | 118.7771 | -0.073255 | -0.01511 | 121.6845 | 121.6511 | 121.7057 | 89.6019 | -121.8029 | 121.6894 | 121.6965 | 121.7546 | 90.7631 | -122.0797
1576.0312 | 121.8521 | -121.637 | 0.16937 | 1.4211e-13 | -0.031369 | -0.0012991 | 0.059303 | -0.0085594 | 0.058046 | -0.22823 | 0.0050078 | 0.010644 | 0.061065 | 0.12136 | 0.1787 | -120.7722 | -32.0213 | -121.2321 | 0.065863 | 0.03699 | 0.077866 | -121.6472 | -65.273 | -30.6083 | -2.7441 | 0.075351 | 0.082386 | 0.13137 | -121.9241 | -0.010278 | -0.10351 | 0.86472 | 0.40484 | 0.41512 | -0.13238 | -0.091507 | -0.28709 | -0.094022 | 56.3639 | 118.8929 | 119.18 | -0.086987 | -0.038 | 121.7028 | 121.674 | 121.7148 | 89.6156 | -121.8166 | 121.7123 | 121.7193 | 121.7683 | 91.0286 | -122.0934
1577.7656 | 121.9803 | -121.6003 | 0.15106 | 1.4211e-13 | -0.031583 | -0.0010855 | 0.059731 | -0.0083458 | 0.057832 | -0.23586 | 0.0058622 | 0.011072 | 0.061492 | 0.12072 | 0.18682 | -120.7722 | -32.0854 | -121.223 | 0.07502 | 0.041569 | 0.087023 | -121.6289 | -64.2291 | -30.2741 | -2.7395 | 0.075351 | 0.091543 | 0.13595 | -121.9195 | -0.028583 | -0.076042 | 0.8281 | 0.37738 | 0.40596 | -0.10949 | -0.064039 | -0.31914 | -0.075711 | 57.3712 | 118.8609 | 119.18 | -0.059519 | -0.01511 | 121.6754 | 121.6419 | 121.6874 | 89.5149 | -121.78 | 121.6757 | 121.6919 | 121.7363 | 91.3263 | -122.0705
1579.5 | 121.9528 | -121.6278 | 0.14648 | 1.4211e-13 | -0.031797 | -0.00087189 | 0.059517 | -0.0085594 | 0.057618 | -0.2206 | 0.0069304 | 0.011072 | 0.061492 | 0.12072 | 0.22058 | -120.7539 | -32.1358 | -121.2047 | 0.07502 | 0.041569 | 0.091601 | -121.7022 | -63.208 | -29.8757 | -2.8768 | 0.07993 | 0.091543 | 0.14511 | -121.892 | -0.07438 | -0.071464 | 0.87388 | 0.42316 | 0.49754 | -0.10492 | -0.054883 | -0.2642 | -0.066554 | 58.4198 | 118.751 | 119.0152 | -0.054941 | -0.001375 | 121.7028 | 121.6694 | 121.7194 | 89.492 | -121.8487 | 121.7077 | 121.7194 | 121.7729 | 91.7521 | -122.0385
1581.1719 | 121.8704 | -121.6599 | 0.10986 | 1.4211e-13 | -0.031583 | -0.0010855 | 0.05909 | -0.0085594 | 0.057832 | -0.23586 | -0.0037514 | -0.0030297 | -0.0034569 | 0.032474 | 0.048371 | -120.7677 | -32.1587 | -121.223 | 0.065863 | 0.009517 | 0.06413 | -121.7022 | -1.3726 | -0.64066 | -0.06093 | 0.066194 | 0.077807 | 0.11764 | -2.8565 | -0.042337 | -0.044 | 0.89218 | 0.43689 | 0.47922 | -0.10035 | -0.045733 | 118.8034 | -0.043669 | 120.2873 | 121.5989 | 2.7956 | -0.032056 | 0.007774 | 121.7257 | 121.6694 | 121.724 | 89.5012 | -121.8121 | 121.726 | 121.7377 | 121.7775 | 121.0192 | -2.9664
1582.9062 | 121.9208 | -121.6553 | 0.09613 | 1.4211e-13 | -0.031156 | -0.0012991 | 0.059517 | -0.0085594 | 0.057618 | -0.24349 | -0.003965 | -0.0034569 | -0.0045251 | 0.030978 | 0.0073497 | -120.8135 | -32.2228 | -121.2733 | 0.038393 | -0.00422 | 0.050394 | -121.7571 | 0.014784 | -0.017956 | 0.007751 | 0.043302 | 0.054914 | 0.099323 | -0.17331 | -0.10186 | -0.057737 | 0.84182 | 0.38195 | 0.48381 | -0.10035 | -0.045736 | 121.482 | -0.052828 | 121.6701 | 121.663 | 0.18106 | -0.041216 | 0.003193 | 121.6937 | 121.6511 | 121.7057 | 89.4325 | -121.8533 | 121.6986 | 121.7102 | 121.7546 | 121.6373 | -0.26944
1584.6406 | 121.9803 | -121.6553 | 0.07782 | 1.4211e-13 | -0.03201 | -0.0015129 | 0.05909 | -0.0083458 | 0.057618 | -0.22823 | -0.0037514 | -0.0032433 | -0.0043115 | 0.030551 | 0.0071361 | -120.818 | -32.232 | -121.2687 | 0.033814 | 0.000359 | 0.045815 | -121.693 | 0.02852 | -0.013377 | 0.01233 | 0.043302 | 0.050335 | 0.1039 | -0.15499 | -0.037757 | -0.044006 | 0.83724 | 0.38652 | 0.42428 | -0.077461 | -0.032005 | 121.5003 | -0.034518 | 121.6838 | 121.6676 | 0.16732 | -0.027485 | 0.026081 | 121.6891 | 121.6556 | 121.7011 | 89.4233 | -121.7708 | 121.6986 | 121.7056 | 121.7592 | 121.6419 | -0.23281
1586.375 | 122.0078 | -121.6461 | 0.1236 | 1.4211e-13 | -0.031369 | -0.0012991 | 0.059303 | -0.0083458 | 0.057618 | -0.23586 | -0.0035378 | -0.0032433 | -0.0047387 | 0.030337 | 0.0071361 | -120.8226 | -32.2869 | -121.2733 | 0.042971 | 0.000359 | 0.045815 | -121.7022 | 0.033099 | -0.008798 | 0.007751 | 0.043302 | 0.054914 | 0.1039 | -0.14125 | -0.05607 | -0.080625 | 0.82351 | 0.37279 | 0.42886 | -0.12324 | -0.077781 | 121.5049 | -0.080294 | 121.6792 | 121.6539 | 0.14901 | -0.068682 | -0.019695 | 121.6891 | 121.6465 | 121.6919 | 89.3592 | -121.8258 | 121.6894 | 121.701 | 121.75 | 121.6373 | -0.26485
1588.0938 | 121.875 | -121.6919 | 0.12817 | 1.4211e-13 | -0.031583 | -0.0010855 | 0.059517 | -0.0085594 | 0.058046 | -0.23586 | -0.003965 | -0.0030297 | -0.0047387 | 0.030765 | 0.0071361 | -120.8363 | -32.2915 | -121.2825 | 0.042971 | 0.004938 | 0.045815 | -121.7113 | 0.033099 | -0.013377 | 0.01233 | 0.04788 | 0.059493 | 0.10848 | -0.14125 | -0.019451 | -0.085203 | 0.85555 | 0.40941 | 0.42886 | -0.12324 | -0.082359 | 121.5506 | -0.080294 | 121.725 | 121.7042 | 0.15358 | -0.068681 | -0.019694 | 121.7349 | 121.6968 | 121.7377 | 89.4004 | -121.8395 | 121.7398 | 121.7514 | 121.8004 | 121.6785 | -0.26943
1589.7812 | 121.9208 | -121.6782 | 0.13733 | 1.4211e-13 | -0.031583 | -0.0012991 | 0.059517 | -0.0085594 | 0.057832 | -0.2206 | -0.003965 | -0.0034569 | -0.0049523 | 0.030765 | 0.0069223 | -120.8272 | -32.3418 | -121.2825 | 0.033814 | 0.004938 | 0.045815 | -121.7022 | 0.033099 | -0.00422 | 0.01233 | 0.04788 | 0.050335 | 0.094744 | -0.15041 | -0.024026 | -0.10352 | 0.85098 | 0.39568 | 0.41971 | -0.13239 | -0.091514 | 121.5277 | -0.089449 | 121.7113 | 121.6905 | 0.16274 | -0.086994 | -0.042585 | 121.712 | 121.6831 | 121.724 | 89.3363 | -121.8395 | 121.726 | 121.7285 | 121.7729 | 121.6739 | -0.28774
1591.5156 | 122.0352 | -121.6599 | 0.10071 | 1.4211e-13 | -0.031797 | -0.0010855 | 0.059517 | -0.0085594 | 0.057832 | -0.22823 | -0.0037514 | -0.0034569 | -0.0045251 | 0.030551 | 0.0073497 | -120.818 | -32.4059 | -121.2733 | 0.038393 | 0.004938 | 0.050394 | -121.7068 | 0.092622 | -0.013377 | 0.007751 | 0.04788 | 0.064071 | 0.11306 | -0.1321 | -0.046916 | -0.062315 | 0.84182 | 0.38653 | 0.43344 | -0.09577 | -0.050314 | 121.5278 | -0.052828 | 121.7525 | 121.6676 | 0.13985 | -0.036637 | 0.012351 | 121.6982 | 121.6648 | 121.7102 | 89.2539 | -121.8075 | 121.7077 | 121.7239 | 121.7729 | 121.6465 | -0.2328
1593.2031 | 121.8842 | -121.7056 | 0.13275 | 1.4211e-13 | -0.031583 | -0.0010855 | 0.059517 | -0.008132 | 0.057618 | -0.22823 | -0.0041788 | -0.0034569 | -0.0045251 | 0.030765 | 0.0069223 | -120.818 | -32.4197 | -121.2779 | 0.042971 | 0.004938 | 0.050394 | -121.7022 | 0.088043 | -0.013377 | -0.005985 | 0.052459 | 0.064071 | 0.11306 | -0.14583 | 0.003439 | -0.08978 | 0.8876 | 0.42772 | 0.42428 | -0.12781 | -0.082357 | 121.5598 | -0.080292 | 121.7937 | 121.6996 | 0.13985 | -0.06868 | -0.019692 | 121.7486 | 121.7106 | 121.756 | 89.2859 | -121.8349 | 121.7581 | 121.7697 | 121.8187 | 121.6923 | -0.27858
1594.9531 | 121.9116 | -121.6736 | 0.15106 | 1.4211e-13 | -0.031583 | -0.0015129 | 0.059517 | -0.0085594 | 0.057832 | -0.21297 | -0.0041788 | -0.0032433 | -0.0045251 | 0.030978 | 0.0073497 | -120.818 | -32.4471 | -121.2733 | 0.047549 | 0.009517 | 0.050394 | -121.7068 | 0.092622 | -0.013377 | -0.010564 | 0.052459 | 0.064071 | 0.11306 | -0.14125 | -0.033183 | -0.10351 | 0.85555 | 0.40026 | 0.43344 | -0.14155 | -0.10067 | 121.5323 | -0.098603 | 121.7662 | 121.663 | 0.13069 | -0.086991 | -0.038003 | 121.7211 | 121.6831 | 121.724 | 89.2264 | -121.8578 | 121.726 | 121.7377 | 121.7866 | 121.6602 | -0.29232
1596.7031 | 121.962 | -121.6644 | 0.11444 | 1.4211e-13 | -0.031583 | -0.0012991 | 0.059517 | -0.008773 | 0.057618 | -0.2206 | -0.003965 | -0.0032433 | -0.0040977 | 0.030765 | 0.0067087 | -120.8135 | -32.5067 | -121.2687 | 0.047549 | 0.009517 | 0.059551 | -121.7068 | 0.092622 | -0.013377 | -0.015143 | 0.066194 | 0.064071 | 0.11764 | -0.1321 | -0.042338 | -0.066892 | 0.85098 | 0.39568 | 0.43802 | -0.10492 | -0.05489 | 121.5323 | -0.048247 | 121.7571 | 121.6493 | 0.11695 | -0.05037 | 0.003196 | 121.712 | 121.6739 | 121.724 | 89.1578 | -121.8212 | 121.7306 | 121.7285 | 121.7821 | 121.6511 | -0.24654
1598.3906 | 121.8842 | -121.701 | 0.16479 | 1.4211e-13 | -0.031583 | -0.0015129 | 0.059731 | -0.0083458 | 0.057832 | -0.22823 | -0.003965 | -0.0032433 | -0.0047387 | 0.030337 | 0.0064951 | -120.8135 | -32.5067 | -121.2687 | 0.052128 | 0.014096 | 0.059551 | -121.6976 | 0.097201 | -0.022535 | -0.028879 | 0.061616 | 0.06865 | 0.11764 | -0.11836 | 0.003441 | -0.11267 | 0.8876 | 0.4323 | 0.42886 | -0.1507 | -0.10524 | 121.5827 | -0.10318 | 121.7983 | 121.6722 | 0.089482 | -0.096145 | -0.047158 | 121.7532 | 121.7151 | 121.7606 | 89.1944 | -121.8624 | 121.7627 | 121.7697 | 121.8187 | 121.6785 | -0.28316
1600.1562 | 121.875 | -121.6873 | 0.15106 | 1.4211e-13 | -0.03201 | -0.0010855 | 0.059303 | -0.0083458 | 0.057832 | -0.22823 | -0.0037514 | -0.0032433 | -0.0045251 | 0.030551 | 0.0073497 | -120.7997 | -32.5754 | -121.2596 | 0.047549 | 0.018675 | 0.06413 | -121.6976 | 0.092622 | -0.022535 | -0.042615 | 0.070773 | 0.073228 | 0.12222 | -0.12294 | -0.010292 | -0.10351 | 0.8876 | 0.42773 | 0.43802 | -0.13239 | -0.086932 | 121.5644 | -0.080289 | 121.7799 | 121.6447 | 0.080324 | -0.077834 | -0.028846 | 121.7349 | 121.706 | 121.7514 | 89.112 | -121.8487 | 121.7581 | 121.7605 | 121.8095 | 121.6648 | -0.274
1601.8906 | 121.2296 | -46.4996 | 74.2218 | 1.4211e-13 | -0.031369 | -0.00065809 | 0.059303 | -0.008773 | 0.056337 | -0.22823 | 0.020603 | 0.032224 | 0.11127 | 0.031619 | 0.0067087 | -52.9022 | -6.111 | -53.4324 | 67.066 | 67.2144 | 66.6645 | -53.2702 | 5.1658 | 7.5323 | 2.0086 | 67.1503 | 67.0536 | 67.5559 | 1.3148 | -6.7705 | -7.1558 | -6.4026 | -6.9327 | -0.16221 | -7.0074 | -7.5573 | 47.8144 | -7.0715 | 51.6655 | 48.5083 | 0.69384 | -7.1682 | -6.6659 | 113.5656 | 113.714 | 113.1641 | 40.3886 | -127.492 | 113.6499 | 113.5532 | 114.0555 | 54.032 | -72.907
1603.5625 | 121.3669 | -31.6132 | 79.0329 | 1.4211e-13 | -0.031369 | -0.00065809 | 0.059945 | -0.0092004 | 0.05655 | -0.22823 | -0.0037514 | 0.049103 | 0.077302 | 0.030765 | 0.0069223 | -47.0877 | -3.8767 | -47.476 | 73.6863 | 73.689 | 73.3309 | -47.3405 | 0.033099 | -0.013377 | -0.083823 | 0.47826 | 0.52651 | 0.48392 | -0.14125 | -15.7273 | -5.3466 | -15.4745 | -15.8629 | -0.13557 | -5.3439 | -5.702 | 31.4719 | -78.5546 | 31.6463 | 31.5293 | 0.057432 | -78.5064 | -78.549 | 105.2995 | 105.3022 | 104.9441 | 27.7365 | -126.3734 | 32.0914 | 32.1397 | 32.0971 | 31.5998 | -79.1742
1605.2969 | 120.6848 | -0.51727 | 112.1887 | 1.4211e-13 | -0.031156 | -0.00044449 | 0.060158 | -0.0089866 | 0.055909 | -0.23586 | -0.0037514 | 0.014918 | 0.024317 | 0.030765 | 0.0071361 | -0.49342 | 15.6831 | -0.67226 | 120.6835 | 120.3711 | 120.2433 | -0.77737 | -0.040161 | -0.137 | -0.13877 | -0.062004 | -0.045815 | -0.001407 | -0.25572 | -0.2601 | 8.4948 | 0.023855 | -0.15499 | 0.10511 | 8.1824 | 8.0546 | 0.26155 | -112.2507 | 0.47711 | 0.3785 | 0.11696 | -112.2345 | -112.1901 | 121.2008 | 120.8884 | 120.7606 | 16.2004 | -112.9661 | 0.45527 | 0.47146 | 0.51587 | 0.38027 | -112.4444
1607.0312 | 121.3852 | -0.76446 | 120.0165 | 1.4211e-13 | -0.030942 | -0.00023069 | 0.060158 | -0.0092004 | 0.055909 | -0.2206 | -0.0037514 | 0.014704 | 0.024745 | 0.030765 | 0.0069223 | -0.47968 | 15.6419 | -0.66768 | 120.7567 | 120.4535 | 120.312 | -0.76821 | -0.026425 | -0.12784 | -0.12045 | -0.075739 | -0.06413 | -0.019721 | -0.25115 | -0.003747 | 0.74027 | 0.28478 | 0.096783 | 0.10053 | 0.43707 | 0.29549 | 0.51332 | -120.0922 | 0.73804 | 0.64401 | 0.13069 | -120.0806 | -120.0362 | 121.5212 | 121.218 | 121.0764 | 16.4064 | -120.7847 | 0.68873 | 0.70033 | 0.74474 | 0.63662 | -120.2676
1608.7812 | 121.6232 | -0.79193 | 120.4697 | 1.4211e-13 | -0.030942 | -0.00044449 | 0.060372 | -0.008773 | 0.056123 | -0.22823 | -0.0035378 | 0.01449 | 0.024745 | 0.030765 | 0.0071361 | -0.48884 | 15.6007 | -0.68142 | 120.7888 | 120.481 | 120.3669 | -0.78195 | -0.017267 | -0.12784 | -0.10214 | -0.084896 | -0.06413 | -0.019721 | -0.24657 | 0.009983 | 0.31913 | 0.30309 | 0.11051 | 0.10053 | 0.011356 | -0.10276 | 0.54536 | -120.5546 | 0.77466 | 0.68979 | 0.14443 | -120.5338 | -120.4894 | 121.5807 | 121.273 | 121.1588 | 16.3926 | -121.2516 | 0.70704 | 0.7278 | 0.77221 | 0.66409 | -120.7162
1610.4688 | 121.669 | -0.80109 | 120.7535 | 1.4211e-13 | -0.030728 | -0.00023069 | 0.060158 | -0.0092004 | 0.055909 | -0.22823 | -0.0037514 | 0.014277 | 0.024745 | 0.030765 | 0.0071361 | -0.50257 | 15.6419 | -0.69515 | 120.798 | 120.4948 | 120.3761 | -0.79111 | -0.00811 | -0.14158 | -0.1754 | -0.094053 | -0.073287 | -0.0243 | -0.23741 | 0.00998 | 0.044472 | 0.29851 | 0.10594 | 0.095955 | -0.25872 | -0.37741 | 0.56368 | -120.8475 | 0.79298 | 0.62569 | 0.062012 | -120.8268 | -120.7778 | 121.599 | 121.2958 | 121.1772 | 16.443 | -121.5446 | 0.70703 | 0.7278 | 0.77679 | 0.65951 | -120.9909
1612.2031 | 121.5866 | -0.83771 | 120.8176 | 1.4211e-13 | -0.031369 | -0.00023069 | 0.060372 | -0.0089866 | 0.056123 | -0.23586 | -0.0037514 | 0.01449 | 0.024958 | 0.030765 | 0.0071361 | -0.51631 | 15.5549 | -0.70431 | 120.8163 | 120.5039 | 120.3852 | -0.80484 | 0.001048 | -0.14158 | -0.16166 | -0.080318 | -0.077866 | -0.033457 | -0.24199 | 0.032865 | -0.001302 | 0.3214 | 0.1334 | 0.10053 | -0.31365 | -0.43234 | 0.59572 | -120.8979 | 0.83876 | 0.67605 | 0.080328 | -120.8954 | -120.851 | 121.654 | 121.3416 | 121.2229 | 16.3926 | -121.6224 | 0.75739 | 0.75984 | 0.80425 | 0.69613 | -121.0596
1613.875 | 121.6965 | -0.84228 | 120.7855 | 1.4211e-13 | -0.030728 | -0.00044449 | 0.060158 | -0.008773 | 0.056123 | -0.22823 | -0.003965 | 0.014704 | 0.024745 | 0.030978 | 0.0069223 | -0.53462 | 15.5687 | -0.72262 | 120.8117 | 120.4993 | 120.3852 | -0.81858 | -0.00811 | -0.14158 | -0.1525 | -0.089475 | -0.077866 | -0.033457 | -0.23741 | 0.023705 | 0.026164 | 0.30766 | 0.11966 | 0.095959 | -0.28619 | -0.4003 | 0.60487 | -120.875 | 0.83417 | 0.68978 | 0.084906 | -120.8634 | -120.819 | 121.654 | 121.3416 | 121.2275 | 16.4109 | -121.6041 | 0.75281 | 0.76442 | 0.80883 | 0.7007 | -121.0229
1615.625 | 121.7148 | -0.85144 | 120.7809 | 1.4211e-13 | -0.031156 | -1.7092e-05 | 0.060586 | -0.008773 | 0.056337 | -0.22823 | -0.0041788 | 0.014918 | 0.024317 | 0.030765 | 0.0071361 | -0.55294 | 15.6007 | -0.73636 | 120.8071 | 120.4993 | 120.3806 | -0.84147 | -0.017267 | -0.14616 | -0.16624 | -0.084896 | -0.077866 | -0.028878 | -0.24199 | 0.009966 | 0.026163 | 0.2985 | 0.11508 | 0.10512 | -0.28161 | -0.4003 | 0.60945 | -120.8658 | 0.83417 | 0.6852 | 0.075749 | -120.8588 | -120.8098 | 121.6585 | 121.3508 | 121.2321 | 16.4521 | -121.6224 | 0.76654 | 0.77357 | 0.82256 | 0.70528 | -121.0229
1617.3594 | 121.7239 | -0.90179 | 120.7672 | 1.4211e-13 | -0.031369 | -0.00044449 | 0.060372 | -0.0089866 | 0.056337 | -0.22823 | -0.003965 | 0.015345 | 0.023676 | 0.030765 | 0.0069223 | -0.57583 | 15.5824 | -0.76383 | 120.798 | 120.4948 | 120.3715 | -0.85521 | -0.00811 | -0.137 | -0.1525 | -0.084896 | -0.073287 | -0.033457 | -0.24199 | 0.046583 | 0.030739 | 0.32596 | 0.13797 | 0.091385 | -0.27245 | -0.39572 | 0.6598 | -120.8521 | 0.89368 | 0.74929 | 0.089485 | -120.8405 | -120.8007 | 121.6997 | 121.3966 | 121.2733 | 16.4842 | -121.6224 | 0.8169 | 0.82851 | 0.86834 | 0.76479 | -121.0092
1619.0938 | 121.6415 | -0.96588 | 120.7626 | 1.4211e-13 | -0.031369 | -0.00023069 | 0.060372 | -0.008773 | 0.055909 | -0.22823 | -0.003965 | 0.015131 | 0.023676 | 0.030978 | 0.0069223 | -0.59872 | 15.5687 | -0.78672 | 120.7888 | 120.481 | 120.3623 | -0.87811 | -0.012689 | -0.15074 | -0.14793 | -0.084896 | -0.082444 | -0.028878 | -0.23741 | 0.087775 | 0.02616 | 0.36716 | 0.17916 | 0.091389 | -0.28161 | -0.4003 | 0.72847 | -120.8475 | 0.95319 | 0.81796 | 0.089485 | -120.8451 | -120.7915 | 121.7547 | 121.4469 | 121.3282 | 16.5345 | -121.6407 | 0.88099 | 0.88344 | 0.937 | 0.81514 | -121
1620.8438 | 121.6599 | -0.98877 | 120.7718 | 1.4211e-13 | -0.031369 | -1.7092e-05 | 0.060372 | -0.0089866 | 0.055909 | -0.22823 | -0.0041788 | 0.015345 | 0.023463 | 0.030978 | 0.0073497 | -0.62619 | 15.5687 | -0.81419 | 120.7751 | 120.4719 | 120.3578 | -0.901 | -0.00811 | -0.15532 | -0.18455 | -0.089475 | -0.077866 | -0.033457 | -0.25115 | 0.08777 | 0.003269 | 0.36258 | 0.17458 | 0.086813 | -0.29993 | -0.41404 | 0.73762 | -120.8613 | 0.98066 | 0.80422 | 0.066591 | -120.8497 | -120.8052 | 121.7638 | 121.4606 | 121.3465 | 16.5574 | -121.6728 | 0.8993 | 0.9109 | 0.95531 | 0.83345 | -121.0229
1622.5781 | 121.7148 | -0.98419 | 120.7214 | 1.4211e-13 | -0.031583 | -0.00023069 | 0.060372 | -0.008773 | 0.055909 | -0.22823 | -0.003965 | 0.015772 | 0.023463 | 0.030978 | 0.0073497 | -0.63993 | 15.5961 | -0.83708 | 120.7522 | 120.449 | 120.3303 | -0.93763 | -0.00811 | -0.15532 | -0.1754 | -0.084896 | -0.073287 | -0.0243 | -0.25572 | 0.04656 | 0.030731 | 0.34426 | 0.14711 | 0.10055 | -0.27247 | -0.39115 | 0.72847 | -120.8063 | 0.97608 | 0.80879 | 0.080327 | -120.7947 | -120.7457 | 121.7364 | 121.4332 | 121.3145 | 16.5803 | -121.6591 | 0.8993 | 0.9109 | 0.95989 | 0.82887 | -120.9772
1624.25 | 121.7285 | -1.0071 | 120.7123 | 1.4211e-13 | -0.030942 | -0.00044449 | 0.060158 | -0.008773 | 0.056123 | -0.22823 | -0.0041788 | 0.015772 | 0.023035 | 0.030765 | 0.0071361 | -0.68571 | 15.5687 | -0.8737 | 120.7293 | 120.4307 | 120.3257 | -0.9651 | -0.021846 | -0.15074 | -0.17998 | -0.084896 | -0.073287 | -0.028878 | -0.24657 | 0.041975 | 0.016995 | 0.32137 | 0.13338 | 0.091401 | -0.28163 | -0.38658 | 0.76051 | -120.7972 | 0.98523 | 0.8271 | 0.066591 | -120.7856 | -120.7412 | 121.7364 | 121.4377 | 121.3328 | 16.5757 | -121.6774 | 0.92218 | 0.93379 | 0.9782 | 0.85634 | -120.9588
1626 | 121.701 | -1.0757 | 120.6894 | 1.4211e-13 | -0.031369 | -0.00044449 | 0.060586 | -0.0092004 | 0.055909 | -0.22823 | -0.0037514 | 0.015986 | 0.023249 | 0.030978 | 0.0069223 | -0.71776 | 15.5549 | -0.90575 | 120.7018 | 120.3986 | 120.2891 | -1.0017 | -0.021846 | -0.15074 | -0.17998 | -0.084896 | -0.068708 | -0.033457 | -0.24657 | 0.074008 | 0.012413 | 0.35799 | 0.16999 | 0.095985 | -0.29079 | -0.40032 | 0.82918 | -120.7743 | 1.0539 | 0.89577 | 0.066591 | -120.7581 | -120.7228 | 121.7775 | 121.4743 | 121.3648 | 16.6307 | -121.6911 | 0.99085 | 1.007 | 1.0423 | 0.92501 | -120.936
1627.75 | 121.8063 | -1.062 | 120.607 | 1.4211e-13 | -0.031583 | -1.7092e-05 | 0.060372 | -0.0089866 | 0.056123 | -0.22823 | -0.003965 | 0.016413 | 0.023249 | 0.030765 | 0.0069223 | -0.76354 | 15.5778 | -0.95611 | 120.6698 | 120.362 | 120.2433 | -1.0475 | -0.012689 | -0.15532 | -0.18913 | -0.084896 | -0.068708 | -0.028878 | -0.24657 | 0.014486 | 0.062761 | 0.29847 | 0.1059 | 0.091413 | -0.24503 | -0.36371 | 0.81544 | -120.6919 | 1.0493 | 0.87288 | 0.057433 | -120.6757 | -120.6359 | 121.7318 | 121.424 | 121.3053 | 16.6398 | -121.6545 | 0.97712 | 0.9933 | 1.0331 | 0.90669 | -120.8536
1629.5 | 121.7102 | -1.1673 | 120.6482 | 1.4211e-13 | -0.031369 | -1.7092e-05 | 0.060586 | -0.0089866 | 0.056123 | -0.24349 | -0.003965 | 0.016199 | 0.023249 | 0.031406 | 0.0071361 | -0.80475 | 15.5366 | -1.0019 | 120.624 | 120.3253 | 120.2158 | -1.0887 | -0.017267 | -0.1599 | -0.18455 | -0.084896 | -0.073287 | -0.033457 | -0.25115 | 0.078561 | -0.024221 | 0.36255 | 0.1654 | 0.08684 | -0.32286 | -0.43238 | 0.91615 | -120.7331 | 1.15 | 0.98274 | 0.066591 | -120.7215 | -120.6817 | 121.7913 | 121.4926 | 121.3831 | 16.7039 | -121.7369 | 1.0824 | 1.094 | 1.1338 | 1.0074 | -120.8993
1631.1719 | 121.8155 | -1.1856 | 120.5154 | 1.4211e-13 | -0.031369 | 0.00019651 | 0.060372 | -0.009414 | 0.056337 | -0.22823 | -0.003965 | 0.015986 | 0.023463 | 0.030978 | 0.0069223 | -0.86885 | 15.4679 | -1.0706 | 120.5645 | 120.2612 | 120.1471 | -1.1574 | 0.001048 | -0.1599 | -0.17998 | -0.080318 | -0.073287 | -0.028878 | -0.24199 | 0.028188 | 0.049011 | 0.31676 | 0.11504 | 0.08685 | -0.25421 | -0.3683 | 0.94362 | -120.5958 | 1.1867 | 1.0056 | 0.062013 | -120.5887 | -120.5443 | 121.7501 | 121.4468 | 121.3327 | 16.6535 | -121.6729 | 1.1053 | 1.1123 | 1.1567 | 1.0257 | -120.7574
1632.9062 | 121.7468 | -1.2726 | 120.52 | 1.4211e-13 | -0.031369 | -0.00023069 | 0.060799 | -0.0092004 | 0.056337 | -0.24349 | -0.003965 | 0.016413 | 0.022822 | 0.030978 | 0.0071361 | -0.91921 | 15.4588 | -1.1118 | 120.5278 | 120.2338 | 120.1105 | -1.1986 | -0.003531 | -0.15074 | -0.18913 | -0.080318 | -0.082444 | -0.0243 | -0.23741 | 0.073952 | 0.007806 | 0.35337 | 0.16081 | 0.086856 | -0.28626 | -0.40951 | 1.0352 | -120.6003 | 1.2691 | 1.0834 | 0.048276 | -120.6025 | -120.5443 | 121.8004 | 121.5063 | 121.3831 | 16.7314 | -121.7187 | 1.1923 | 1.1901 | 1.2483 | 1.1218 | -120.7574
1634.6562 | 121.8063 | -1.2863 | 120.4468 | 1.4211e-13 | -0.031583 | -1.7092e-05 | 0.060372 | -0.0092004 | 0.056123 | -0.23586 | -0.0041788 | 0.016627 | 0.023249 | 0.031192 | 0.0067087 | -0.95584 | 15.4496 | -1.1484 | 120.4912 | 120.1925 | 120.0785 | -1.2398 | -0.012689 | -0.15532 | -0.18455 | -0.084896 | -0.073287 | -0.028878 | -0.24657 | 0.046475 | 0.044422 | 0.33048 | 0.13792 | 0.09144 | -0.25423 | -0.36832 | 1.0397 | -120.5317 | 1.2736 | 1.1018 | 0.062012 | -120.5201 | -120.4757 | 121.7775 | 121.4789 | 121.3648 | 16.7359 | -121.6866 | 1.2014 | 1.213 | 1.2574 | 1.131 | -120.6933
1636.3438 | 121.8704 | -1.2863 | 120.4239 | 1.4211e-13 | -0.031156 | -1.7092e-05 | 0.060586 | -0.0089866 | 0.055909 | -0.2206 | -0.003965 | 0.016413 | 0.022822 | 0.031406 | 0.0069223 | -0.98331 | 15.4038 | -1.185 | 120.4683 | 120.1651 | 120.0556 | -1.2719 | -0.012689 | -0.15532 | -0.17998 | -0.080318 | -0.077866 | -0.028878 | -0.23741 | 0.014423 | 0.044418 | 0.30301 | 0.10129 | 0.086866 | -0.25881 | -0.36832 | 1.0489 | -120.5042 | 1.2736 | 1.1063 | 0.057434 | -120.5018 | -120.4528 | 121.7546 | 121.4514 | 121.3419 | 16.6901 | -121.6958 | 1.206 | 1.2085 | 1.2574 | 1.131 | -120.6613
1638.0781 | 121.8521 | -1.7578 | 119.9661 | 1.4211e-13 | -0.031583 | -0.00023069 | 0.060372 | -0.0089866 | 0.055909 | -0.22823 | -0.003965 | 0.01684 | 0.022822 | 0.030978 | 0.0069223 | -1.1207 | 15.3123 | -1.3178 | 120.3172 | 120.0231 | 119.9182 | -1.4138 | 0.001048 | -0.1599 | -0.1754 | -0.094053 | -0.073287 | -0.028878 | -0.24199 | 0.34397 | 0.3511 | 0.63715 | 0.44001 | 0.096042 | 0.057004 | -0.047917 | 1.5158 | -120.0602 | 1.7589 | 1.5824 | 0.066591 | -120.0394 | -119.995 | 122.075 | 121.7809 | 121.676 | 17.0701 | -121.38 | 1.6638 | 1.6845 | 1.7289 | 1.5979 | -120.2081
1639.8281 | 121.8613 | -1.9547 | 119.7464 | 1.4211e-13 | -0.031369 | -0.00044449 | 0.060372 | -0.008773 | 0.055909 | -0.21297 | -0.0037514 | 0.01684 | 0.022822 | 0.030765 | 0.0069223 | -1.5968 | 15.0238 | -1.7894 | 119.8182 | 119.524 | 119.4191 | -1.9038 | -0.012689 | -0.15532 | -0.17082 | -0.080318 | -0.073287 | -0.0243 | -0.24657 | 0.050866 | 0.071777 | 0.35784 | 0.16529 | 0.11442 | -0.22237 | -0.32726 | 1.7081 | -119.8267 | 1.942 | 1.7838 | 0.075748 | -119.8197 | -119.7707 | 121.7728 | 121.4787 | 121.3738 | 16.9785 | -121.6502 | 1.8743 | 1.8814 | 1.9304 | 1.7993 | -119.993
1641.5781 | 121.8292 | -2.005 | 119.6915 | 1.4211e-13 | -0.031583 | -0.00044449 | 0.060799 | -0.0092004 | 0.056123 | -0.22823 | -0.0037514 | 0.016627 | 0.022608 | 0.031192 | 0.0073497 | -1.6426 | 14.9826 | -1.8397 | 119.777 | 119.4828 | 119.3642 | -1.9542 | -0.00811 | -0.15074 | -0.1754 | -0.080318 | -0.077866 | -0.0243 | -0.24199 | 0.050852 | 0.085503 | 0.36241 | 0.16528 | 0.11443 | -0.20865 | -0.32727 | 1.763 | -119.7718 | 1.9969 | 1.8296 | 0.066591 | -119.7693 | -119.7158 | 121.782 | 121.4878 | 121.3692 | 16.9876 | -121.6456 | 1.9247 | 1.9271 | 1.9807 | 1.8543 | -119.9335
1643.25 | 121.8384 | -2.0187 | 119.7098 | 1.4211e-13 | -0.031583 | -0.00044449 | 0.060372 | -0.0092004 | 0.05655 | -0.23586 | -0.003965 | 0.016627 | 0.022395 | 0.030978 | 0.0067087 | -1.6609 | 14.9368 | -1.8672 | 119.7541 | 119.4599 | 119.355 | -1.9862 | -0.00811 | -0.15074 | -0.1754 | -0.080318 | -0.068708 | -0.0243 | -0.23283 | 0.032532 | 0.0443 | 0.35783 | 0.15155 | 0.11901 | -0.24986 | -0.35474 | 1.7859 | -119.7901 | 2.0106 | 1.8433 | 0.057433 | -119.7785 | -119.7341 | 121.7728 | 121.4787 | 121.3738 | 16.9555 | -121.696 | 1.9384 | 1.95 | 1.9944 | 1.868 | -119.9426
1644.9375 | 121.7377 | -2.0874 | 119.7281 | 1.4211e-13 | -0.031797 | -0.00065809 | 0.060158 | -0.0092004 | 0.056337 | -0.23586 | -0.003965 | 0.015558 | 0.022608 | 0.031192 | 0.0071361 | -1.6746 | 14.9277 | -1.8901 | 119.7358 | 119.4416 | 119.3367 | -2.0045 | -0.003531 | -0.15074 | -0.16166 | -0.080318 | -0.073287 | -0.028878 | -0.23283 | 0.082881 | 0.007677 | 0.41276 | 0.19732 | 0.11444 | -0.28648 | -0.39136 | 1.8546 | -119.8084 | 2.0839 | 1.9257 | 0.07117 | -119.8014 | -119.757 | 121.8232 | 121.529 | 121.4241 | 17.0151 | -121.7326 | 2.0071 | 2.0141 | 2.0585 | 1.9367 | -119.9609
1646.6719 | 121.8063 | -2.0737 | 119.6777 | 1.4211e-13 | -0.031797 | -0.00023069 | 0.060372 | -0.0092004 | 0.056123 | -0.23586 | -0.0041788 | 0.015345 | 0.022822 | 0.030978 | 0.0069223 | -1.7113 | 14.9002 | -1.913 | 119.7129 | 119.4187 | 119.3138 | -2.0274 | -0.003531 | -0.14158 | -0.1525 | -0.084896 | -0.082444 | -0.019721 | -0.22367 | 0.046253 | 0.035139 | 0.3624 | 0.1607 | 0.11444 | -0.25902 | -0.3639 | 1.85 | -119.7626 | 2.0701 | 1.9212 | 0.071169 | -119.7602 | -119.6975 | 121.7865 | 121.4924 | 121.3875 | 16.9738 | -121.7052 | 1.9888 | 1.9912 | 2.0539 | 1.9321 | -119.9014
1648.4062 | 121.8155 | -2.1103 | 119.6915 | 1.4211e-13 | -0.031583 | -1.7092e-05 | 0.060586 | -0.008773 | 0.056337 | -0.22823 | -0.0037514 | 0.015558 | 0.022822 | 0.031619 | 0.0067087 | -1.7158 | 14.8819 | -1.9221 | 119.7083 | 119.4141 | 119.3138 | -2.0412 | -0.003531 | -0.14158 | -0.12503 | -0.084896 | -0.073287 | -0.0243 | -0.22367 | 0.069138 | 0.016827 | 0.39444 | 0.18816 | 0.11902 | -0.27734 | -0.37763 | 1.8866 | -119.7764 | 2.1068 | 1.9853 | 0.098641 | -119.7648 | -119.7158 | 121.8186 | 121.5244 | 121.4241 | 16.9922 | -121.7326 | 2.0254 | 2.037 | 2.086 | 1.9687 | -119.9151
1650.1562 | 121.8521 | -2.1103 | 119.6228 | 1.4211e-13 | -0.031583 | -0.00023069 | 0.060372 | -0.0092004 | 0.056123 | -0.23586 | -0.0043924 | 0.015986 | 0.022822 | 0.030978 | 0.0069223 | -1.7296 | 14.8773 | -1.9359 | 119.6946 | 119.4004 | 119.3001 | -2.0503 | -0.017267 | -0.14616 | -0.16166 | -0.089475 | -0.068708 | -0.019721 | -0.23283 | 0.05998 | 0.071756 | 0.38071 | 0.17443 | 0.11445 | -0.22241 | -0.32271 | 1.8775 | -119.7123 | 2.093 | 1.9486 | 0.07117 | -119.6915 | -119.6425 | 121.8049 | 121.5107 | 121.4104 | 16.9876 | -121.6731 | 2.0208 | 2.0416 | 2.0906 | 1.9641 | -119.8556
1651.8906 | 121.7514 | -2.1103 | 119.7052 | 1.4211e-13 | -0.031797 | -0.00023069 | 0.060586 | -0.0089866 | 0.055909 | -0.2206 | -0.003965 | 0.015986 | 0.022822 | 0.031192 | 0.0069223 | -1.6975 | 14.8452 | -1.9176 | 119.7083 | 119.4279 | 119.323 | -2.0228 | -0.00811 | -0.13242 | -0.10672 | -0.084896 | -0.068708 | -0.019721 | -0.22367 | 0.087454 | 0.003094 | 0.41276 | 0.19274 | 0.10529 | -0.27733 | -0.38221 | 1.8866 | -119.7901 | 2.1022 | 2.0036 | 0.11696 | -119.7739 | -119.7249 | 121.8186 | 121.5382 | 121.4333 | 16.9555 | -121.728 | 2.0254 | 2.0416 | 2.0906 | 1.9779 | -119.9289
1653.5625 | 121.8201 | -2.0325 | 119.7052 | 1.4211e-13 | -0.031797 | -0.00044449 | 0.060372 | -0.0092004 | 0.056123 | -0.23586 | -0.0037514 | 0.015986 | 0.022822 | 0.030978 | 0.0067087 | -1.6746 | 14.8544 | -1.8809 | 119.7541 | 119.4599 | 119.355 | -2.0091 | -0.003531 | -0.137 | -0.092981 | -0.080318 | -0.073287 | -0.028878 | -0.2191 | 0.023371 | 0.048878 | 0.35783 | 0.15155 | 0.12817 | -0.24528 | -0.35016 | 1.8134 | -119.7855 | 2.0289 | 1.9395 | 0.12611 | -119.7785 | -119.7341 | 121.7865 | 121.4924 | 121.3875 | 16.8869 | -121.7143 | 1.9522 | 1.9592 | 2.0036 | 1.8955 | -119.9243
1655.3125 | 121.788 | -2.0599 | 119.7464 | 1.4211e-13 | -0.03201 | -1.7092e-05 | 0.060372 | -0.0089866 | 0.056123 | -0.22823 | -0.003965 | 0.015772 | 0.022608 | 0.031192 | 0.0067087 | -1.6701 | 14.8544 | -1.8809 | 119.7632 | 119.4737 | 119.3825 | -1.9908 | -0.00811 | -0.14158 | -0.11587 | -0.089475 | -0.068708 | -0.019721 | -0.2191 | 0.069152 | 0.016836 | 0.38987 | 0.17901 | 0.10986 | -0.27274 | -0.36389 | 1.8408 | -119.8359 | 2.0518 | 1.9441 | 0.10322 | -119.8151 | -119.7661 | 121.8232 | 121.5336 | 121.4424 | 16.9143 | -121.7372 | 1.9705 | 1.9912 | 2.0402 | 1.9184 | -119.9655
1656.9844 | 121.8887 | -2.0325 | 119.7144 | 1.4211e-13 | -0.031583 | -0.00023069 | 0.060372 | -0.0089866 | 0.055696 | -0.23586 | -0.0041788 | 0.015772 | 0.022395 | 0.031192 | 0.0067087 | -1.6701 | 14.8361 | -1.8763 | 119.7587 | 119.4737 | 119.3688 | -1.9954 | -0.00811 | -0.12784 | -0.11587 | -0.089475 | -0.068708 | -0.0243 | -0.22367 | 0.037108 | 0.044302 | 0.36241 | 0.15612 | 0.11902 | -0.2407 | -0.34558 | 1.8088 | -119.8038 | 2.0244 | 1.9166 | 0.1078 | -119.7831 | -119.7387 | 121.7911 | 121.5061 | 121.4012 | 16.8685 | -121.7097 | 1.943 | 1.9638 | 2.0082 | 1.9046 | -119.938
1658.7188 | 121.8475 | -2.0325 | 119.7235 | 1.4211e-13 | -0.031797 | -0.00023069 | 0.060158 | -0.0089866 | 0.055909 | -0.23586 | -0.0043924 | 0.015986 | 0.022395 | 0.031619 | 0.0071361 | -1.6701 | 14.804 | -1.8718 | 119.7815 | 119.492 | 119.3917 | -1.9862 | -0.012689 | -0.12784 | -0.14793 | -0.089475 | -0.06413 | -0.0243 | -0.22367 | 0.046265 | 0.058038 | 0.36241 | 0.1607 | 0.11444 | -0.23154 | -0.33184 | 1.8088 | -119.813 | 2.0198 | 1.8845 | 0.075748 | -119.7876 | -119.7478 | 121.814 | 121.5244 | 121.4241 | 16.8365 | -121.7097 | 1.943 | 1.9683 | 2.0082 | 1.9046 | -119.9472
1660.4688 | 121.8933 | -1.9913 | 119.7418 | 1.4211e-13 | -0.031583 | -0.00044449 | 0.060372 | -0.0092004 | 0.056123 | -0.23586 | -0.0043924 | 0.015986 | 0.022395 | 0.031192 | 0.0067087 | -1.6197 | 14.8086 | -1.8306 | 119.8182 | 119.524 | 119.4375 | -1.9404 | -0.026425 | -0.12327 | -0.10672 | -0.084896 | -0.073287 | -0.0243 | -0.22367 | 0.050856 | 0.076355 | 0.37157 | 0.16071 | 0.10985 | -0.21779 | -0.30437 | 1.7676 | -119.8267 | 1.9648 | 1.8846 | 0.11696 | -119.8151 | -119.7661 | 121.8094 | 121.5153 | 121.4287 | 16.7999 | -121.6822 | 1.9064 | 1.918 | 1.967 | 1.868 | -119.9655
1662.1406 | 121.8521 | -1.9684 | 119.7922 | 1.4211e-13 | -0.03201 | 0.00019651 | 0.059945 | -0.0092004 | 0.055696 | -0.23586 | -0.003965 | 0.015772 | 0.022608 | 0.031192 | 0.0067087 | -1.6105 | 14.7903 | -1.8214 | 119.8273 | 119.5378 | 119.4329 | -1.9404 | -0.017267 | -0.13242 | -0.14335 | -0.080318 | -0.068708 | -0.019721 | -0.22825 | 0.027968 | 0.035158 | 0.35784 | 0.14698 | 0.11901 | -0.25441 | -0.3593 | 1.7401 | -119.8725 | 1.9511 | 1.825 | 0.084905 | -119.8609 | -119.8119 | 121.7957 | 121.5061 | 121.4013 | 16.7587 | -121.7326 | 1.8881 | 1.8997 | 1.9487 | 1.836 | -120.0204
1663.875 | 121.7697 | -1.9547 | 119.8563 | 1.4211e-13 | -0.032438 | -0.00023069 | 0.060158 | -0.0089866 | 0.055909 | -0.23586 | -0.003965 | 0.015772 | 0.022608 | 0.030978 | 0.0067087 | -1.5877 | 14.7857 | -1.7985 | 119.8456 | 119.5698 | 119.4695 | -1.9129 | -0.00811 | -0.14158 | -0.16624 | -0.084896 | -0.073287 | -0.0243 | -0.23283 | 0.041708 | -0.010616 | 0.367 | 0.15613 | 0.11443 | -0.28645 | -0.38676 | 1.7218 | -119.9412 | 1.9465 | 1.7884 | 0.066591 | -119.9295 | -119.8806 | 121.8003 | 121.5245 | 121.4242 | 16.7404 | -121.7692 | 1.8698 | 1.8814 | 1.9304 | 1.8131 | -120.0891
1665.625 | 121.8933 | -1.9501 | 119.838 | 1.4211e-13 | -0.03201 | -0.00044449 | 0.060158 | -0.0096276 | 0.056123 | -0.2206 | -0.0041788 | 0.015558 | 0.022608 | 0.031406 | 0.0067087 | -1.5785 | 14.7628 | -1.7848 | 119.8594 | 119.5836 | 119.4787 | -1.9129 | -0.00811 | -0.14158 | -0.17082 | -0.080318 | -0.068708 | -0.0243 | -0.22367 | 0.03713 | 0.021429 | 0.37158 | 0.16529 | 0.12816 | -0.2544 | -0.35929 | 1.7264 | -119.9183 | 1.942 | 1.7793 | 0.052854 | -119.9067 | -119.8623 | 121.8095 | 121.5336 | 121.4287 | 16.7129 | -121.7509 | 1.8698 | 1.8814 | 1.9258 | 1.8085 | -120.0616
1667.2969 | 121.8521 | -1.7532 | 119.9982 | 1.4211e-13 | -0.03201 | -0.00023069 | 0.060372 | -0.0092004 | 0.055696 | -0.21297 | -0.003965 | 0.015772 | 0.022608 | 0.031192 | 0.0071361 | -1.3816 | 14.8544 | -1.5925 | 120.0563 | 119.7667 | 119.6847 | -1.716 | -0.012689 | -0.14158 | -0.16166 | -0.080318 | -0.06413 | -0.019721 | -0.2191 | 0.037186 | 0.058083 | 0.37161 | 0.16074 | 0.12355 | -0.23146 | -0.31347 | 1.5341 | -120.0785 | 1.7405 | 1.5916 | 0.057434 | -120.0623 | -120.0179 | 121.8095 | 121.5199 | 121.4379 | 16.6076 | -121.7142 | 1.6729 | 1.6891 | 1.7335 | 1.6117 | -120.2173
1669.0469 | 121.7972 | -1.5656 | 120.2728 | 1.4211e-13 | -0.03201 | -0.00044449 | 0.060372 | -0.0092004 | 0.055696 | -0.23586 | -0.003965 | 0.015772 | 0.022181 | 0.031406 | 0.0069223 | -1.2626 | 14.8819 | -1.4735 | 120.189 | 119.8949 | 119.8037 | -1.5924 | -0.00811 | -0.13242 | -0.16166 | -0.075739 | -0.06413 | -0.019721 | -0.22367 | -0.026866 | -0.083802 | 0.30296 | 0.092093 | 0.11896 | -0.37791 | -0.46908 | 1.3419 | -120.3486 | 1.5574 | 1.4039 | 0.062012 | -120.337 | -120.2925 | 121.7546 | 121.4605 | 121.3693 | 16.4474 | -121.8652 | 1.4898 | 1.5014 | 1.5458 | 1.4331 | -120.4965
1670.7969 | 121.907 | -1.7258 | 119.9982 | 1.4211e-13 | -0.032224 | -1.7092e-05 | 0.060372 | -0.0092004 | 0.055696 | -0.22823 | -0.003965 | 0.015345 | 0.022395 | 0.031406 | 0.0064951 | -1.464 | 14.7491 | -1.6703 | 119.9876 | 119.698 | 119.6069 | -1.7893 | -0.00811 | -0.13242 | -0.16624 | -0.080318 | -0.068708 | -0.028878 | -0.21452 | -0.063543 | -0.010593 | 0.26173 | 0.055444 | 0.11899 | -0.30014 | -0.39131 | 1.5113 | -120.0785 | 1.7177 | 1.5595 | 0.048276 | -120.0669 | -120.027 | 121.7133 | 121.4238 | 121.3326 | 16.4749 | -121.7875 | 1.6455 | 1.6571 | 1.6969 | 1.5933 | -120.2127
1672.5469 | 121.7743 | -1.5884 | 120.2682 | 1.4211e-13 | -0.031797 | -0.00023069 | 0.060586 | -0.008773 | 0.055909 | -0.2206 | -0.0041788 | 0.016199 | 0.022608 | 0.031619 | 0.0067087 | -1.1115 | 14.9093 | -1.327 | 120.3401 | 120.0552 | 119.9548 | -1.4505 | -0.012689 | -0.13242 | -0.16624 | -0.080318 | -0.068708 | -0.0243 | -0.22367 | 0.13797 | 0.071862 | 0.47694 | 0.26149 | 0.12352 | -0.21307 | -0.31341 | 1.3648 | -120.3486 | 1.5758 | 1.4222 | 0.057433 | -120.337 | -120.2925 | 121.9286 | 121.6436 | 121.5433 | 16.4978 | -121.7187 | 1.5081 | 1.5197 | 1.5641 | 1.456 | -120.4919
1674.2188 | 121.8887 | -1.5198 | 120.2637 | 1.4211e-13 | -0.031797 | -0.00023069 | 0.060799 | -0.0089866 | 0.055909 | -0.23586 | -0.003965 | 0.016199 | 0.021967 | 0.031406 | 0.0067087 | -1.2443 | 14.8223 | -1.4506 | 120.2028 | 119.9224 | 119.8266 | -1.5741 | -0.00811 | -0.12784 | -0.15708 | -0.080318 | -0.068708 | -0.0243 | -0.21452 | -0.054327 | -0.060912 | 0.2755 | 0.069207 | 0.12353 | -0.34128 | -0.43704 | 1.3053 | -120.344 | 1.5117 | 1.3627 | 0.057433 | -120.3324 | -120.288 | 121.7225 | 121.4422 | 121.3464 | 16.3421 | -121.8378 | 1.4395 | 1.4511 | 1.4955 | 1.3919 | -120.4782
1675.9062 | 121.8567 | -1.4832 | 120.3461 | 1.4211e-13 | -0.03201 | -0.00023069 | 0.060372 | -0.0092004 | 0.055696 | -0.22823 | -0.003965 | 0.015986 | 0.022395 | 0.031192 | 0.0067087 | -0.92836 | 14.9643 | -1.1484 | 120.5187 | 120.2383 | 120.1426 | -1.2765 | -0.017267 | -0.12784 | -0.16166 | -0.084896 | -0.06413 | -0.0243 | -0.22367 | 0.20668 | 0.1726 | 0.55479 | 0.33475 | 0.12807 | -0.10773 | -0.20351 | 1.2595 | -120.431 | 1.4659 | 1.3215 | 0.062012 | -120.4102 | -120.3704 | 122.0018 | 121.7215 | 121.6257 | 16.4474 | -121.6225 | 1.3983 | 1.419 | 1.4589 | 1.3553 | -120.5697
1677.6562 | 121.9162 | -0.93384 | 120.8267 | 1.4211e-13 | -0.03201 | -0.00023069 | 0.060586 | -0.009414 | 0.055909 | -0.23586 | -0.003965 | 0.015986 | 0.022395 | 0.031619 | 0.0069223 | -0.61704 | 15.0879 | -0.82792 | 120.8392 | 120.5543 | 120.4631 | -0.95137 | -0.017267 | -0.12784 | -0.14793 | -0.080318 | -0.068708 | -0.019721 | -0.21452 | -0.017531 | 0.012435 | 0.3168 | 0.10592 | 0.12345 | -0.27244 | -0.36366 | 0.71932 | -120.907 | 0.91657 | 0.78591 | 0.066591 | -120.8954 | -120.8464 | 121.773 | 121.4881 | 121.3969 | 16.0217 | -121.7781 | 0.85352 | 0.86513 | 0.91412 | 0.80599 | -121.0412
1679.3906 | 121.8979 | -0.87433 | 120.8862 | 1.4211e-13 | -0.032651 | -0.00065809 | 0.060158 | -0.009414 | 0.055268 | -0.22823 | -0.003965 | 0.015345 | 0.022608 | 0.031833 | 0.0069223 | -0.498 | 15.1383 | -0.69057 | 120.9719 | 120.6917 | 120.605 | -0.814 | -0.00811 | -0.12784 | -0.14335 | -0.080318 | -0.06413 | -0.015142 | -0.21452 | 0.060328 | 0.085699 | 0.37633 | 0.18376 | 0.12343 | -0.19458 | -0.28123 | 0.65981 | -120.9665 | 0.86622 | 0.73098 | 0.071169 | -120.9504 | -120.9014 | 121.8463 | 121.566 | 121.4793 | 16.0126 | -121.7002 | 0.79401 | 0.8102 | 0.85919 | 0.74648 | -121.1007
1681.0625 | 121.9162 | -0.97504 | 120.7855 | 1.4211e-13 | -0.03201 | -0.00023069 | 0.060158 | -0.0092004 | 0.055696 | -0.23586 | -0.0037514 | 0.015558 | 0.021967 | 0.031406 | 0.0069223 | -0.73607 | 14.9551 | -0.94696 | 120.7155 | 120.4307 | 120.3394 | -1.0704 | -0.012689 | -0.12784 | -0.14335 | -0.084896 | -0.068708 | -0.0243 | -0.20994 | -0.095384 | -0.069982 | 0.23896 | 0.02808 | 0.12346 | -0.35487 | -0.44608 | 0.7651 | -120.8704 | 0.96235 | 0.83169 | 0.06659 | -120.8542 | -120.8098 | 121.6906 | 121.4057 | 121.3145 | 15.9302 | -121.8559 | 0.89014 | 0.90633 | 0.95074 | 0.84719 | -120.9955
1682.8125 | 121.9254 | -0.98419 | 120.8038 | 1.4211e-13 | -0.032224 | -0.00044449 | 0.060372 | -0.0089866 | 0.055482 | -0.22823 | -0.0041788 | 0.015772 | 0.022608 | 0.031619 | 0.0071361 | -0.55752 | 15.0467 | -0.75925 | 120.9124 | 120.6275 | 120.5363 | -0.88726 | -0.012689 | -0.12327 | -0.1525 | -0.080318 | -0.06413 | -0.019721 | -0.20994 | 0.096928 | 0.10858 | 0.42668 | 0.22494 | 0.12802 | -0.17629 | -0.26751 | 0.77425 | -120.8842 | 0.9715 | 0.83169 | 0.057433 | -120.868 | -120.8236 | 121.8966 | 121.6117 | 121.5205 | 16.0309 | -121.6911 | 0.90387 | 0.92006 | 0.96447 | 0.86093 | -121.0138
1684.4844 | 121.843 | -0.90637 | 120.9412 | 1.4211e-13 | -0.032224 | -1.7092e-05 | 0.060372 | -0.009414 | 0.055909 | -0.22823 | -0.003965 | 0.015772 | 0.022822 | 0.031619 | 0.0067087 | -0.47968 | 15.0604 | -0.66768 | 121.004 | 120.7237 | 120.6279 | -0.79568 | -0.00811 | -0.12784 | -0.1525 | -0.071161 | -0.06413 | -0.0243 | -0.20536 | 0.11069 | 0.062816 | 0.42669 | 0.23869 | 0.128 | -0.21746 | -0.31327 | 0.70101 | -121.0123 | 0.89826 | 0.75387 | 0.052854 | -121.0053 | -120.9655 | 121.9104 | 121.6301 | 121.5343 | 15.9668 | -121.7368 | 0.83521 | 0.84224 | 0.88207 | 0.77853 | -121.1465
1686.2188 | 121.8292 | -0.66376 | 121.1792 | 1.4211e-13 | -0.032224 | -0.00023069 | 0.060372 | -0.0092004 | 0.055909 | -0.2206 | -0.0037514 | 0.015558 | 0.022395 | 0.031619 | 0.0067087 | -0.31486 | 15.0559 | -0.50744 | 121.178 | 120.8931 | 120.7927 | -0.62169 | -0.00811 | -0.12784 | -0.15708 | -0.080318 | -0.068708 | -0.019721 | -0.20536 | 0.042071 | -0.001242 | 0.3489 | 0.15632 | 0.11424 | -0.28607 | -0.38648 | 0.4584 | -121.2595 | 0.65565 | 0.50667 | 0.048275 | -121.2479 | -121.1989 | 121.8417 | 121.5569 | 121.4565 | 15.7196 | -121.8009 | 0.58344 | 0.59505 | 0.64404 | 0.53591 | -121.3846
1687.9531 | 121.8246 | -0.92468 | 120.9457 | 1.4211e-13 | -0.032224 | -1.7092e-05 | 0.060372 | -0.008773 | 0.055482 | -0.22823 | -0.0041788 | 0.015772 | 0.022181 | 0.031833 | 0.0067087 | -0.34233 | 15.0375 | -0.53491 | 121.1551 | 120.8748 | 120.7744 | -0.65374 | -0.00811 | -0.12784 | -0.15708 | -0.080318 | -0.073287 | -0.0243 | -0.20536 | 0.27094 | 0.20932 | 0.58235 | 0.38977 | 0.11883 | -0.070931 | -0.17133 | 0.71932 | -121.0261 | 0.91657 | 0.7676 | 0.048275 | -121.019 | -120.97 | 122.0797 | 121.7995 | 121.6991 | 15.9622 | -121.5995 | 0.84437 | 0.8514 | 0.90038 | 0.79684 | -121.1511
1689.6875 | 121.788 | -0.83313 | 121.0327 | 1.4211e-13 | -0.032224 | -0.00023069 | 0.060586 | -0.0089866 | 0.055696 | -0.22823 | -0.0043924 | 0.015986 | 0.022395 | 0.031619 | 0.0069223 | -0.34233 | 15.0101 | -0.53491 | 121.1459 | 120.8565 | 120.7698 | -0.65832 | -0.012689 | -0.13242 | -0.1525 | -0.075739 | -0.068708 | -0.028878 | -0.20994 | 0.17481 | 0.11319 | 0.4908 | 0.29822 | 0.1234 | -0.17622 | -0.26289 | 0.62319 | -121.1085 | 0.82044 | 0.68063 | 0.057433 | -121.1014 | -121.0616 | 121.979 | 121.6896 | 121.603 | 15.8432 | -121.691 | 0.75739 | 0.76442 | 0.80425 | 0.70071 | -121.2427
1691.4219 | 121.7926 | -0.73242 | 121.0922 | 1.4211e-13 | -0.032438 | -0.00023069 | 0.060372 | -0.009414 | 0.055909 | -0.21297 | -0.0041788 | 0.015772 | 0.022608 | 0.031833 | 0.0064951 | -0.33317 | 14.9734 | -0.53033 | 121.1505 | 120.8702 | 120.779 | -0.64916 | -0.00811 | -0.12327 | -0.15708 | -0.080318 | -0.06413 | -0.0243 | -0.21452 | 0.083262 | 0.058263 | 0.39925 | 0.20209 | 0.11883 | -0.22199 | -0.31324 | 0.51791 | -121.1725 | 0.72431 | 0.57534 | 0.057433 | -121.1564 | -121.1165 | 121.8829 | 121.6027 | 121.5114 | 15.7059 | -121.7414 | 0.6521 | 0.66829 | 0.70812 | 0.60916 | -121.3067
1693.1562 | 121.8567 | -0.74616 | 121.0464 | 1.4211e-13 | -0.032438 | -0.00023069 | 0.060586 | -0.009414 | 0.055909 | -0.22823 | -0.0037514 | 0.015558 | 0.022181 | 0.031833 | 0.0064951 | -0.37896 | 14.9689 | -0.57612 | 121.1093 | 120.8244 | 120.7378 | -0.69495 | -0.017267 | -0.12327 | -0.15708 | -0.080318 | -0.06413 | -0.028878 | -0.20536 | 0.051206 | 0.062833 | 0.3672 | 0.17004 | 0.11883 | -0.22201 | -0.30867 | 0.5408 | -121.1268 | 0.72889 | 0.58907 | 0.048275 | -121.1106 | -121.0753 | 121.8554 | 121.5706 | 121.4839 | 15.715 | -121.7414 | 0.66584 | 0.68202 | 0.71728 | 0.62289 | -121.2518
1694.8438 | 121.9208 | -1.1124 | 120.6802 | 1.4211e-13 | -0.032438 | -1.7092e-05 | 0.060372 | -0.0096276 | 0.055696 | -0.22823 | -0.0041788 | 0.015772 | 0.022395 | 0.03226 | 0.0067087 | -0.58956 | 14.7811 | -0.80045 | 120.8712 | 120.5909 | 120.4997 | -0.93305 | -0.017267 | -0.12327 | -0.1525 | -0.080318 | -0.068708 | -0.0243 | -0.20078 | 0.17931 | 0.19097 | 0.5228 | 0.31191 | 0.1326 | -0.089321 | -0.18055 | 0.91159 | -120.7606 | 1.0951 | 0.95986 | 0.048275 | -120.7489 | -120.7045 | 121.9836 | 121.7033 | 121.6121 | 15.8935 | -121.6133 | 1.032 | 1.0437 | 1.0881 | 0.9891 | -120.881
1696.5938 | 121.8658 | -0.60883 | 121.225 | 1.4211e-13 | -0.032651 | -0.00023069 | 0.060158 | -0.009414 | 0.055909 | -0.22823 | -0.003965 | 0.015772 | 0.022181 | 0.031833 | 0.0067087 | -0.30113 | 14.8864 | -0.50286 | 121.178 | 120.9069 | 120.8156 | -0.62169 | -0.017267 | -0.12327 | -0.15708 | -0.075739 | -0.073287 | -0.015142 | -0.20078 | -0.01286 | -0.047019 | 0.3077 | 0.10596 | 0.11882 | -0.31811 | -0.40936 | 0.40805 | -121.3007 | 0.59156 | 0.45174 | 0.043696 | -121.2983 | -121.2401 | 121.7868 | 121.5157 | 121.4244 | 15.4953 | -121.8467 | 0.53309 | 0.53554 | 0.59368 | 0.48556 | -121.4258
1698.3281 | 121.8796 | -0.9201 | 120.9183 | 1.4211e-13 | -0.032651 | -0.00023069 | 0.060158 | -0.009414 | 0.055696 | -0.23586 | -0.0041788 | 0.015772 | 0.022181 | 0.031833 | 0.0069223 | -0.48884 | 14.7995 | -0.69973 | 120.9857 | 120.7054 | 120.6187 | -0.82316 | -0.012689 | -0.12784 | -0.15708 | -0.080318 | -0.06413 | -0.0243 | -0.20536 | 0.096946 | 0.067391 | 0.43126 | 0.22037 | 0.12343 | -0.21288 | -0.29954 | 0.71475 | -120.9986 | 0.90742 | 0.76302 | 0.048275 | -120.9824 | -120.9426 | 121.9058 | 121.6255 | 121.5388 | 15.7196 | -121.7414 | 0.83979 | 0.85597 | 0.8958 | 0.79226 | -121.1236
1700.0625 | 121.8796 | -0.60883 | 121.2021 | 1.4211e-13 | -0.032224 | -0.00044449 | 0.059945 | -0.009414 | 0.055909 | -0.23586 | -0.0041788 | 0.015772 | 0.021967 | 0.03226 | 0.0067087 | -0.25534 | 14.859 | -0.4525 | 121.2466 | 120.9618 | 120.8614 | -0.5759 | -0.012689 | -0.13242 | -0.1525 | -0.080318 | -0.06413 | -0.0243 | -0.20536 | 0.032929 | 0.044546 | 0.35348 | 0.15632 | 0.12339 | -0.24028 | -0.34069 | 0.40347 | -121.2824 | 0.59614 | 0.45632 | 0.052854 | -121.2662 | -121.2264 | 121.8555 | 121.5706 | 121.4702 | 15.4678 | -121.778 | 0.52851 | 0.5447 | 0.58453 | 0.4764 | -121.4074
1701.8125 | 121.9254 | -0.68207 | 121.1197 | 1.4211e-13 | -0.032651 | -0.00023069 | 0.059945 | -0.0092004 | 0.055696 | -0.22823 | -0.0037514 | 0.015986 | 0.022181 | 0.031833 | 0.0062815 | -0.25992 | 14.8178 | -0.47082 | 121.2237 | 120.9481 | 120.866 | -0.58505 | -0.021846 | -0.12327 | -0.14793 | -0.080318 | -0.059551 | -0.0243 | -0.20536 | 0.097013 | 0.10405 | 0.42215 | 0.21125 | 0.11424 | -0.17162 | -0.25371 | 0.47671 | -121.2 | 0.66022 | 0.53414 | 0.057433 | -121.1792 | -121.144 | 121.9058 | 121.6301 | 121.548 | 15.4998 | -121.7047 | 0.60175 | 0.62252 | 0.65777 | 0.5588 | -121.325
1703.5 | 121.7926 | -0.62256 | 121.2982 | 1.4211e-13 | -0.032438 | -0.00023069 | 0.059945 | -0.009414 | 0.055696 | -0.23586 | -0.0041788 | 0.015558 | 0.022395 | 0.031833 | 0.0064951 | -0.20956 | 14.7766 | -0.4113 | 121.2787 | 120.9939 | 120.9026 | -0.53469 | -0.017267 | -0.12784 | -0.15708 | -0.080318 | -0.06413 | -0.0243 | -0.20536 | 0.087872 | -0.019537 | 0.413 | 0.21126 | 0.12339 | -0.30436 | -0.39561 | 0.4172 | -121.3785 | 0.60529 | 0.46548 | 0.048275 | -121.3623 | -121.3225 | 121.9012 | 121.6164 | 121.5252 | 15.3991 | -121.8329 | 0.54224 | 0.55843 | 0.59826 | 0.49471 | -121.5036
1705.2344 | 121.8842 | -0.59967 | 121.2296 | 1.4211e-13 | -0.032438 | 0.00019651 | 0.059945 | -0.0092004 | 0.055696 | -0.22823 | -0.0043924 | 0.015772 | 0.022395 | 0.031619 | 0.0069223 | -0.23245 | 14.7811 | -0.43877 | 121.2649 | 120.9847 | 120.8935 | -0.54842 | -0.012689 | -0.12784 | -0.15708 | -0.075739 | -0.06413 | -0.019721 | -0.20078 | 0.051247 | 0.035393 | 0.36722 | 0.1609 | 0.10966 | -0.24485 | -0.3361 | 0.39889 | -121.3053 | 0.58698 | 0.44259 | 0.043696 | -121.2937 | -121.2493 | 121.8646 | 121.5844 | 121.4931 | 15.3808 | -121.778 | 0.52393 | 0.53554 | 0.57995 | 0.47183 | -121.4303
1706.9062 | 121.8109 | -0.6134 | 121.2662 | 1.4211e-13 | -0.032438 | -0.00044449 | 0.060372 | -0.0092004 | 0.055696 | -0.23586 | -0.003965 | 0.016199 | 0.022395 | 0.031833 | 0.0064951 | -0.2004 | 14.772 | -0.40672 | 121.2878 | 121.0122 | 120.9255 | -0.53011 | -0.021846 | -0.137 | -0.15708 | -0.080318 | -0.068708 | -0.028878 | -0.20078 | 0.083295 | 0.021664 | 0.413 | 0.20668 | 0.12339 | -0.254 | -0.34067 | 0.41262 | -121.3465 | 0.59156 | 0.45632 | 0.043696 | -121.3349 | -121.2951 | 121.9012 | 121.6256 | 121.5389 | 15.3854 | -121.7963 | 0.53309 | 0.5447 | 0.58453 | 0.4764 | -121.467
1708.6406 | 121.9482 | -0.75531 | 121.051 | 1.4211e-13 | -0.032651 | 0.00019651 | 0.060372 | -0.008773 | 0.055696 | -0.22823 | -0.003965 | 0.015986 | 0.022395 | 0.031833 | 0.0069223 | -0.36064 | 14.6484 | -0.56696 | 121.123 | 120.8473 | 120.7652 | -0.68121 | -0.00811 | -0.12784 | -0.1525 | -0.075739 | -0.059551 | -0.0243 | -0.20078 | 0.074098 | 0.071991 | 0.39467 | 0.18835 | 0.11425 | -0.20369 | -0.28578 | 0.55453 | -121.1268 | 0.7472 | 0.60281 | 0.048275 | -121.1106 | -121.0753 | 121.8783 | 121.6026 | 121.5206 | 15.4037 | -121.7322 | 0.67957 | 0.69576 | 0.73101 | 0.62747 | -121.2518
1710.375 | 121.8155 | -0.67291 | 121.1792 | 1.4211e-13 | -0.032438 | -1.7092e-05 | 0.059945 | -0.009414 | 0.055909 | -0.23586 | -0.0041788 | 0.016199 | 0.022608 | 0.032047 | 0.0064951 | -0.30113 | 14.6163 | -0.50744 | 121.1917 | 120.916 | 120.8294 | -0.64 | -0.003531 | -0.12784 | -0.1525 | -0.075739 | -0.06413 | -0.019721 | -0.1962 | 0.032911 | 0.012493 | 0.37179 | 0.16547 | 0.13256 | -0.26318 | -0.34985 | 0.47671 | -121.2549 | 0.66938 | 0.52041 | 0.043696 | -121.2433 | -121.1989 | 121.8646 | 121.5889 | 121.5023 | 15.2892 | -121.8192 | 0.59717 | 0.60878 | 0.65319 | 0.54507 | -121.3754
1712.0625 | 121.9345 | -0.58594 | 121.1838 | 1.4211e-13 | -0.032438 | -0.00044449 | 0.060158 | -0.0092004 | 0.055909 | -0.22823 | -0.0041788 | 0.015986 | 0.022181 | 0.032047 | 0.0067087 | -0.24618 | 14.6117 | -0.4525 | 121.2466 | 120.971 | 120.8751 | -0.58048 | -0.017267 | -0.12327 | -0.15708 | -0.075739 | -0.059551 | -0.015142 | -0.20078 | 0.005461 | 0.062856 | 0.33975 | 0.13343 | 0.12797 | -0.21281 | -0.30864 | 0.38516 | -121.2595 | 0.56867 | 0.42885 | 0.043696 | -121.2433 | -121.1989 | 121.8326 | 121.5569 | 121.4611 | 15.1977 | -121.7643 | 0.5102 | 0.52639 | 0.5708 | 0.46267 | -121.3846
1713.7969 | 121.8567 | -0.56305 | 121.2845 | 1.4211e-13 | -0.032651 | -0.00044449 | 0.059945 | -0.009414 | 0.055696 | -0.23586 | -0.0043924 | 0.015772 | 0.022181 | 0.031619 | 0.0069223 | -0.20956 | 14.5888 | -0.4113 | 121.2833 | 121.0076 | 120.9209 | -0.53926 | -0.00811 | -0.11869 | -0.14793 | -0.075739 | -0.068708 | -0.010564 | -0.20078 | 0.023784 | -0.001225 | 0.35349 | 0.15175 | 0.12797 | -0.27689 | -0.36356 | 0.36227 | -121.3602 | 0.55494 | 0.41512 | 0.052854 | -121.3532 | -121.295 | 121.8463 | 121.5706 | 121.484 | 15.1519 | -121.8238 | 0.48731 | 0.49434 | 0.55249 | 0.44436 | -121.4853
1715.5312 | 121.8842 | -0.6134 | 121.2067 | 1.4211e-13 | -0.032651 | -0.00044449 | 0.059945 | -0.0092004 | 0.055482 | -0.22823 | -0.0041788 | 0.015772 | 0.022181 | 0.032047 | 0.0067087 | -0.25534 | 14.5202 | -0.46166 | 121.2375 | 120.9572 | 120.8751 | -0.58505 | -0.003531 | -0.12784 | -0.15708 | -0.084896 | -0.068708 | -0.0243 | -0.20536 | 0.028348 | 0.030811 | 0.35806 | 0.15174 | 0.1234 | -0.24944 | -0.33153 | 0.40804 | -121.2916 | 0.60987 | 0.45632 | 0.048275 | -121.2754 | -121.231 | 121.8509 | 121.5706 | 121.4885 | 15.1336 | -121.7917 | 0.52851 | 0.5447 | 0.5891 | 0.48556 | -121.412
1717.2031 | 121.9391 | -0.52643 | 121.2616 | 1.4211e-13 | -0.032865 | -0.00044449 | 0.059945 | -0.0089866 | 0.055482 | -0.22823 | -0.0041788 | 0.015772 | 0.022181 | 0.03226 | 0.0064951 | -0.23245 | 14.5064 | -0.43419 | 121.2604 | 120.9847 | 120.898 | -0.553 | -0.012689 | -0.12327 | -0.15708 | -0.080318 | -0.06413 | -0.0243 | -0.1962 | -0.026574 | -0.001229 | 0.29398 | 0.092239 | 0.11881 | -0.27689 | -0.36357 | 0.33023 | -121.3419 | 0.51374 | 0.36935 | 0.039117 | -121.3257 | -121.2859 | 121.7868 | 121.5111 | 121.4245 | 15.0328 | -121.8146 | 0.44611 | 0.4623 | 0.50213 | 0.40316 | -121.4578
1718.8906 | 121.8567 | -0.5722 | 121.2799 | 1.4211e-13 | -0.032865 | -0.00023069 | 0.059945 | -0.009414 | 0.055696 | -0.23586 | -0.003965 | 0.015772 | 0.022181 | 0.03226 | 0.0069223 | -0.18667 | 14.4744 | -0.40672 | 121.3107 | 121.0396 | 120.9484 | -0.52095 | -0.012689 | -0.13242 | -0.16166 | -0.084896 | -0.059551 | -0.019721 | -0.1962 | 0.051255 | 0.030823 | 0.38554 | 0.16548 | 0.11423 | -0.24026 | -0.33151 | 0.376 | -121.3648 | 0.55952 | 0.41054 | 0.034539 | -121.3395 | -121.2996 | 121.8829 | 121.6119 | 121.5206 | 15.0466 | -121.8009 | 0.48731 | 0.51265 | 0.55248 | 0.43978 | -121.4761
1720.6406 | 121.9437 | -0.52185 | 121.257 | 1.4211e-13 | -0.032651 | -0.00044449 | 0.059945 | -0.0092004 | 0.055909 | -0.25112 | -0.0043924 | 0.015986 | 0.022395 | 0.032047 | 0.0067087 | -0.16377 | 14.4377 | -0.37467 | 121.3336 | 121.0625 | 120.9759 | -0.49348 | -0.049318 | -0.137 | -0.15708 | -0.080318 | -0.068708 | -0.019721 | -0.20994 | 0.028375 | 0.076603 | 0.35808 | 0.14718 | 0.1188 | -0.19447 | -0.28115 | 0.31191 | -121.3373 | 0.47253 | 0.36477 | 0.052854 | -121.3257 | -121.2767 | 121.8555 | 121.5844 | 121.4977 | 14.9596 | -121.7505 | 0.44153 | 0.45314 | 0.50213 | 0.38485 | -121.467
1722.3281 | 121.9528 | -0.88348 | 120.9183 | 1.4211e-13 | -0.032865 | -0.00023069 | 0.060158 | -0.0089866 | 0.055909 | -0.2206 | -0.0043924 | 0.015558 | 0.022395 | 0.03226 | 0.0064951 | -0.3698 | 14.3279 | -0.57612 | 121.123 | 120.8473 | 120.7744 | -0.70869 | -0.049318 | -0.12784 | -0.16624 | -0.071161 | -0.059551 | -0.019721 | -0.20994 | 0.1748 | 0.20474 | 0.51368 | 0.30737 | 0.13257 | -0.070939 | -0.14387 | 0.67355 | -120.9894 | 0.83417 | 0.71724 | 0.043697 | -120.9778 | -120.938 | 122.0065 | 121.7308 | 121.6579 | 15.2113 | -121.627 | 0.81232 | 0.82393 | 0.86376 | 0.75564 | -121.1282
1724.0781 | 121.9345 | -0.53558 | 121.3074 | 1.4211e-13 | -0.032865 | -0.00023069 | 0.059945 | -0.009414 | 0.055909 | -0.22823 | -0.003965 | 0.015558 | 0.022181 | 0.03226 | 0.0064951 | -0.17751 | 14.3645 | -0.38383 | 121.3199 | 121.0488 | 120.953 | -0.50721 | -0.040161 | -0.13242 | -0.16624 | -0.075739 | -0.06413 | -0.0243 | -0.21452 | 0.02837 | 0.012514 | 0.35807 | 0.15176 | 0.12339 | -0.25857 | -0.3544 | 0.32107 | -121.3831 | 0.49542 | 0.36934 | 0.048276 | -121.3715 | -121.3317 | 121.8555 | 121.5844 | 121.4886 | 14.9001 | -121.8146 | 0.45984 | 0.47145 | 0.51128 | 0.40316 | -121.5219
1725.8281 | 121.8292 | -0.53558 | 121.3715 | 1.4211e-13 | -0.032651 | -0.00023069 | 0.060158 | -0.009414 | 0.055696 | -0.22823 | -0.004606 | 0.015772 | 0.022181 | 0.032047 | 0.0062815 | -0.11341 | 14.337 | -0.31515 | 121.4023 | 121.1266 | 121.04 | -0.43853 | -0.040161 | -0.12327 | -0.17082 | -0.080318 | -0.059551 | -0.028878 | -0.20536 | 0.097054 | 0.030838 | 0.42217 | 0.22043 | 0.12338 | -0.24481 | -0.3315 | 0.33022 | -121.4518 | 0.49542 | 0.36476 | 0.034539 | -121.431 | -121.4003 | 121.9379 | 121.6622 | 121.5755 | 14.8726 | -121.81 | 0.45527 | 0.47603 | 0.50671 | 0.41232 | -121.5768
1727.5156 | 121.9391 | -0.49896 | 121.3074 | 1.4211e-13 | -0.033506 | -1.7092e-05 | 0.059945 | -0.009414 | 0.055482 | -0.2206 | -0.0037514 | 0.015986 | 0.022181 | 0.031833 | 0.0064951 | -0.10883 | 14.2912 | -0.32431 | 121.3977 | 121.1175 | 121.0491 | -0.43853 | -0.049318 | -0.12784 | -0.17082 | -0.080318 | -0.06413 | -0.0243 | -0.20536 | 0.060433 | 0.090347 | 0.39013 | 0.17465 | 0.11422 | -0.18988 | -0.25825 | 0.2936 | -121.3877 | 0.44964 | 0.32814 | 0.034539 | -121.3715 | -121.3317 | 121.8967 | 121.6165 | 121.5481 | 14.7902 | -121.7459 | 0.41864 | 0.43483 | 0.47466 | 0.37112 | -121.5127
1729.2656 | 121.9391 | -0.60883 | 121.1884 | 1.4211e-13 | -0.033079 | -0.00044449 | 0.059945 | -0.0096276 | 0.055696 | -0.2206 | -0.0041788 | 0.015986 | 0.022181 | 0.032047 | 0.0064951 | -0.16835 | 14.218 | -0.38841 | 121.3199 | 121.0534 | 120.9621 | -0.51179 | -0.049318 | -0.13242 | -0.15708 | -0.080318 | -0.059551 | -0.019721 | -0.20994 | 0.097034 | 0.13153 | 0.44047 | 0.22042 | 0.12339 | -0.13497 | -0.22622 | 0.39889 | -121.2687 | 0.55951 | 0.45174 | 0.052854 | -121.2479 | -121.2081 | 121.9287 | 121.6622 | 121.571 | 14.8268 | -121.7001 | 0.52851 | 0.54927 | 0.5891 | 0.4764 | -121.3983
1730.9531 | 121.9254 | -0.53101 | 121.2616 | 1.4211e-13 | -0.033079 | -0.00044449 | 0.059731 | -0.0092004 | 0.055696 | -0.22823 | -0.0043924 | 0.015986 | 0.022181 | 0.032474 | 0.0067087 | -0.22329 | 14.1218 | -0.44335 | 121.2695 | 120.9984 | 120.9072 | -0.57132 | -0.040161 | -0.137 | -0.15708 | -0.075739 | -0.059551 | -0.019721 | -0.20994 | -0.040312 | 0.007928 | 0.30771 | 0.08766 | 0.12797 | -0.26316 | -0.35441 | 0.32107 | -121.3373 | 0.49084 | 0.37392 | 0.052854 | -121.3211 | -121.2813 | 121.8005 | 121.5294 | 121.4382 | 14.6528 | -121.8329 | 0.45527 | 0.47145 | 0.51128 | 0.394 | -121.4715
1732.6875 | 121.9025 | -0.51727 | 121.3303 | 1.4211e-13 | -0.033292 | -1.7092e-05 | 0.060158 | -0.009414 | 0.055482 | -0.2206 | -0.003965 | 0.016199 | 0.022181 | 0.032047 | 0.0064951 | -0.12257 | 14.1264 | -0.3472 | 121.3794 | 121.1129 | 121.0217 | -0.45227 | -0.040161 | -0.12784 | -0.16166 | -0.075739 | -0.059551 | -0.019721 | -0.20536 | 0.065007 | 0.049145 | 0.3947 | 0.17007 | 0.10506 | -0.21735 | -0.30861 | 0.31191 | -121.406 | 0.47711 | 0.35561 | 0.043697 | -121.3898 | -121.35 | 121.8967 | 121.6302 | 121.5389 | 14.6437 | -121.7825 | 0.44153 | 0.45772 | 0.49755 | 0.38943 | -121.5356
1734.4375 | 121.8246 | -0.55389 | 121.3623 | 1.4211e-13 | -0.033079 | -0.00044449 | 0.060158 | -0.009414 | 0.055482 | -0.2206 | -0.0048196 | 0.015986 | 0.022181 | 0.03226 | 0.0062815 | -0.14088 | 14.0806 | -0.36551 | 121.3519 | 121.0717 | 120.9988 | -0.4889 | -0.044739 | -0.13242 | -0.16166 | -0.084896 | -0.06413 | -0.019721 | -0.20078 | 0.064997 | -0.010369 | 0.41301 | 0.18838 | 0.12338 | -0.2906 | -0.36355 | 0.35311 | -121.4472 | 0.50916 | 0.39223 | 0.039118 | -121.4264 | -121.382 | 121.9058 | 121.6256 | 121.5527 | 14.6345 | -121.8512 | 0.469 | 0.48976 | 0.53417 | 0.42147 | -121.5631
1736.125 | 121.9391 | -0.53558 | 121.2753 | 1.4211e-13 | -0.033079 | -0.00044449 | 0.059945 | -0.0092004 | 0.055482 | -0.2206 | -0.003965 | 0.015558 | 0.021967 | 0.03226 | 0.0064951 | -0.15004 | 14.0348 | -0.37009 | 121.3428 | 121.0809 | 120.9988 | -0.49348 | -0.044739 | -0.12784 | -0.16166 | -0.075739 | -0.059551 | -0.015142 | -0.20536 | 0.042107 | 0.067449 | 0.38554 | 0.16549 | 0.12338 | -0.19447 | -0.27657 | 0.33022 | -121.3511 | 0.49084 | 0.37392 | 0.043697 | -121.3349 | -121.2905 | 121.8784 | 121.6164 | 121.5343 | 14.5704 | -121.7688 | 0.45984 | 0.47603 | 0.52044 | 0.40774 | -121.4807
1737.8125 | 121.8018 | -0.56305 | 121.3257 | 1.4211e-13 | -0.033079 | -0.00044449 | 0.059945 | -0.009414 | 0.055696 | -0.22823 | -0.0041788 | 0.015772 | 0.021967 | 0.032047 | 0.0064951 | -0.15004 | 14.0211 | -0.36551 | 121.3474 | 121.0809 | 120.9988 | -0.4889 | -0.053897 | -0.137 | -0.16166 | -0.080318 | -0.059551 | -0.0243 | -0.20994 | 0.074152 | 0.021673 | 0.41301 | 0.19753 | 0.12338 | -0.24482 | -0.32693 | 0.35311 | -121.406 | 0.50915 | 0.40139 | 0.048276 | -121.3852 | -121.35 | 121.9104 | 121.6439 | 121.5618 | 14.5841 | -121.8146 | 0.48273 | 0.5035 | 0.53875 | 0.42605 | -121.5356
1739.5469 | 121.8338 | -0.62256 | 121.2433 | 1.4211e-13 | -0.033292 | -1.7092e-05 | 0.060158 | -0.009414 | 0.055696 | -0.23586 | -0.003965 | 0.016199 | 0.021967 | 0.03226 | 0.0067087 | -0.1592 | 13.9845 | -0.38383 | 121.3474 | 121.0763 | 120.9896 | -0.50263 | -0.044739 | -0.14158 | -0.16624 | -0.075739 | -0.059551 | -0.019721 | -0.20078 | 0.11992 | 0.10407 | 0.46336 | 0.23873 | 0.11881 | -0.167 | -0.25369 | 0.42178 | -121.319 | 0.57782 | 0.45632 | 0.034539 | -121.3028 | -121.263 | 121.9699 | 121.6988 | 121.6122 | 14.607 | -121.7459 | 0.54682 | 0.56301 | 0.60284 | 0.48098 | -121.4441
1741.2969 | 121.907 | -0.53558 | 121.2936 | 1.4211e-13 | -0.033079 | -0.00023069 | 0.060372 | -0.0092004 | 0.055482 | -0.22823 | -0.0041788 | 0.015772 | 0.021967 | 0.032474 | 0.0064951 | -0.14088 | 13.9524 | -0.36094 | 121.3519 | 121.0854 | 121.0079 | -0.4889 | -0.044739 | -0.13242 | -0.16624 | -0.080318 | -0.059551 | -0.015142 | -0.20078 | 0.046686 | 0.058296 | 0.3947 | 0.17465 | 0.12796 | -0.2082 | -0.28572 | 0.3348 | -121.374 | 0.49084 | 0.36934 | 0.034539 | -121.3532 | -121.3088 | 121.8875 | 121.621 | 121.5435 | 14.488 | -121.7825 | 0.45527 | 0.47603 | 0.52044 | 0.40316 | -121.4944
1742.9844 | 121.9162 | -0.59967 | 121.2158 | 1.4211e-13 | -0.033506 | -0.00044449 | 0.059517 | -0.0092004 | 0.055696 | -0.22823 | -0.0043924 | 0.015772 | 0.021967 | 0.032474 | 0.0064951 | -0.25534 | 13.8471 | -0.47082 | 121.2421 | 120.9664 | 120.8843 | -0.60337 | -0.053897 | -0.12784 | -0.16624 | -0.075739 | -0.054973 | -0.0243 | -0.20078 | -0.0037 | 0.026234 | 0.34433 | 0.12885 | 0.13255 | -0.24943 | -0.33153 | 0.39889 | -121.2916 | 0.54577 | 0.43343 | 0.034539 | -121.2708 | -121.2401 | 121.8417 | 121.5661 | 121.484 | 14.4468 | -121.8192 | 0.52393 | 0.5447 | 0.57537 | 0.47183 | -121.4166
1744.7344 | 121.9482 | -1.6983 | 120.1904 | 1.4211e-13 | -0.033079 | -0.00044449 | 0.060158 | -0.0096276 | 0.055696 | -0.23586 | -0.0041788 | 0.015772 | 0.022181 | 0.032474 | 0.0067087 | -0.86885 | 13.4717 | -1.1118 | 120.5919 | 120.3208 | 120.2387 | -1.2536 | -0.049318 | -0.13242 | -0.15708 | -0.080318 | -0.045815 | -0.019721 | -0.20994 | 0.44472 | 0.40149 | 0.82946 | 0.58653 | 0.1418 | 0.13033 | 0.04828 | 1.4884 | -120.2707 | 1.649 | 1.5412 | 0.052854 | -120.2362 | -120.2102 | 122.2902 | 122.0191 | 121.937 | 15.17 | -121.444 | 1.618 | 1.6525 | 1.6786 | 1.5659 | -120.4004
1746.4219 | 121.8475 | -0.86517 | 120.9869 | 1.4211e-13 | -0.033079 | -0.00044449 | 0.060158 | -0.009414 | 0.055909 | -0.2206 | -0.0041788 | 0.015772 | 0.021967 | 0.03226 | 0.0062815 | -0.58041 | 13.577 | -0.81419 | 120.8895 | 120.6275 | 120.5317 | -0.95137 | -0.044739 | -0.12327 | -0.15708 | -0.075739 | -0.059551 | -0.019721 | -0.20078 | -0.086196 | -0.09742 | 0.28476 | 0.050986 | 0.13718 | -0.35939 | -0.4552 | 0.66439 | -121.0627 | 0.82043 | 0.70809 | 0.043696 | -121.0465 | -121.0067 | 121.7547 | 121.4927 | 121.3969 | 14.4421 | -121.9383 | 0.78943 | 0.80562 | 0.84545 | 0.74191 | -121.1877
1748.1562 | 121.8613 | -0.62256 | 121.2936 | 1.4211e-13 | -0.033292 | -1.7092e-05 | 0.059945 | -0.009414 | 0.055268 | -0.22823 | -0.003965 | 0.015558 | 0.021967 | 0.032047 | 0.0064951 | -0.22329 | 13.7097 | -0.44792 | 121.2649 | 120.9984 | 120.9118 | -0.58048 | -0.049318 | -0.13242 | -0.16624 | -0.084896 | -0.068708 | -0.019721 | -0.20536 | 0.042083 | -0.028694 | 0.39927 | 0.17463 | 0.13255 | -0.2952 | -0.38187 | 0.4172 | -121.3785 | 0.57324 | 0.45632 | 0.039118 | -121.3623 | -121.3134 | 121.8875 | 121.621 | 121.5343 | 14.3323 | -121.8741 | 0.53766 | 0.55385 | 0.60284 | 0.49013 | -121.499
1749.8438 | 121.8704 | -0.68665 | 121.1929 | 1.4211e-13 | -0.033506 | -0.00044449 | 0.060158 | -0.009414 | 0.055482 | -0.23586 | -0.003965 | 0.015772 | 0.022181 | 0.03226 | 0.0064951 | -0.31486 | 13.6502 | -0.54865 | 121.1642 | 120.8977 | 120.8202 | -0.68121 | -0.053897 | -0.137 | -0.16624 | -0.071161 | -0.054973 | -0.019721 | -0.20536 | 0.005434 | -0.02871 | 0.37178 | 0.138 | 0.13257 | -0.29523 | -0.37274 | 0.48129 | -121.2641 | 0.63275 | 0.52041 | 0.039118 | -121.2479 | -121.2127 | 121.8509 | 121.5844 | 121.5068 | 14.3369 | -121.8741 | 0.61548 | 0.63167 | 0.66692 | 0.54964 | -121.3983
1751.5938 | 121.907 | -0.78278 | 121.051 | 1.4211e-13 | -0.033292 | -0.00023069 | 0.059731 | -0.0092004 | 0.055482 | -0.23586 | -0.0041788 | 0.015986 | 0.021967 | 0.032688 | 0.0064951 | -0.38811 | 13.5495 | -0.61732 | 121.0955 | 120.8199 | 120.7378 | -0.75905 | -0.058476 | -0.13242 | -0.16624 | -0.075739 | -0.059551 | -0.0243 | -0.20078 | 0.023722 | 0.044521 | 0.39466 | 0.16546 | 0.14173 | -0.23116 | -0.31325 | 0.582 | -121.1268 | 0.7243 | 0.61654 | 0.034539 | -121.1106 | -121.0753 | 121.8783 | 121.6026 | 121.5206 | 14.3323 | -121.8101 | 0.70704 | 0.72323 | 0.75848 | 0.65035 | -121.2518
1753.3281 | 121.843 | -0.95673 | 120.9549 | 1.4211e-13 | -0.033079 | -1.7092e-05 | 0.059517 | -0.009414 | 0.055482 | -0.22823 | -0.003965 | 0.015986 | 0.021967 | 0.032474 | 0.0062815 | -0.46137 | 13.4625 | -0.70431 | 121.0086 | 120.7329 | 120.6554 | -0.85063 | -0.053897 | -0.14158 | -0.16624 | -0.075739 | -0.054973 | -0.0243 | -0.20994 | 0.10609 | 0.053662 | 0.49536 | 0.25242 | 0.14632 | -0.22203 | -0.29953 | 0.74679 | -121.0306 | 0.90283 | 0.79049 | 0.043697 | -121.0099 | -120.9792 | 121.9653 | 121.6896 | 121.6121 | 14.4192 | -121.8055 | 0.88099 | 0.90175 | 0.93243 | 0.81515 | -121.1648
1755.0625 | 121.8979 | -0.64545 | 121.2296 | 1.4211e-13 | -0.033292 | -0.00044449 | 0.059731 | -0.0096276 | 0.055696 | -0.23586 | -0.0041788 | 0.015986 | 0.022395 | 0.032474 | 0.0064951 | -0.17293 | 13.5724 | -0.40214 | 121.3199 | 121.0488 | 120.9621 | -0.53011 | -0.053897 | -0.137 | -0.16624 | -0.080318 | -0.059551 | -0.019721 | -0.20536 | 0.11534 | 0.090334 | 0.47252 | 0.2433 | 0.12797 | -0.18075 | -0.26742 | 0.44009 | -121.3099 | 0.59155 | 0.47921 | 0.039118 | -121.2891 | -121.2493 | 121.9653 | 121.6943 | 121.6076 | 14.2178 | -121.7597 | 0.56513 | 0.5859 | 0.62573 | 0.50845 | -121.4349
1756.8125 | 121.875 | -0.62714 | 121.2387 | 1.4211e-13 | -0.03372 | -0.00065809 | 0.059945 | -0.009414 | 0.055482 | -0.23586 | -0.003965 | 0.015772 | 0.021754 | 0.032474 | 0.0067087 | -0.30113 | 13.4625 | -0.53033 | 121.178 | 120.916 | 120.8294 | -0.65832 | -0.049318 | -0.13242 | -0.17082 | -0.075739 | -0.054973 | -0.015142 | -0.20536 | -0.031181 | -0.060751 | 0.32601 | 0.096803 | 0.12798 | -0.32269 | -0.40936 | 0.42178 | -121.3144 | 0.57782 | 0.45632 | 0.034539 | -121.2937 | -121.2538 | 121.8051 | 121.5432 | 121.4565 | 14.0896 | -121.897 | 0.5514 | 0.57216 | 0.61199 | 0.49471 | -121.4441
1758.5469 | 121.9986 | -0.5127 | 121.3211 | 1.4211e-13 | -0.03372 | -0.00023069 | 0.059731 | -0.009414 | 0.055482 | -0.22823 | -0.003965 | 0.015772 | 0.021967 | 0.032688 | 0.0064951 | -0.13173 | 13.4945 | -0.36551 | 121.3519 | 121.0854 | 120.9988 | -0.4889 | -0.053897 | -0.14158 | -0.16166 | -0.084896 | -0.06413 | -0.019721 | -0.20536 | 0.023798 | 0.03083 | 0.38097 | 0.14718 | 0.12338 | -0.23567 | -0.32235 | 0.30734 | -121.406 | 0.4588 | 0.35103 | 0.043697 | -121.3852 | -121.3408 | 121.8646 | 121.5981 | 121.5115 | 14.0072 | -121.81 | 0.4278 | 0.44856 | 0.49297 | 0.37111 | -121.5265
1760.2812 | 121.8338 | -0.56305 | 121.3486 | 1.4211e-13 | -0.033506 | -0.00023069 | 0.059945 | -0.009414 | 0.055696 | -0.23586 | -0.0041788 | 0.015772 | 0.021967 | 0.032688 | 0.0067087 | -0.10426 | 13.4625 | -0.33805 | 121.3886 | 121.1312 | 121.0445 | -0.46142 | -0.053897 | -0.137 | -0.17082 | -0.075739 | -0.068708 | -0.0243 | -0.20536 | 0.10163 | 0.039991 | 0.45879 | 0.225 | 0.12338 | -0.21734 | -0.30403 | 0.35769 | -121.4243 | 0.50915 | 0.39223 | 0.034539 | -121.4173 | -121.3729 | 121.9516 | 121.6943 | 121.6076 | 14.0255 | -121.81 | 0.48731 | 0.49434 | 0.53875 | 0.42605 | -121.5539
1761.9688 | 121.962 | -0.53101 | 121.2936 | 1.4211e-13 | -0.033292 | -0.00023069 | 0.059945 | -0.009414 | 0.055482 | -0.23586 | -0.003965 | 0.015558 | 0.021967 | 0.032688 | 0.0064951 | -0.12715 | 13.4167 | -0.36094 | 121.3565 | 121.09 | 121.0079 | -0.50263 | -0.058476 | -0.13242 | -0.17082 | -0.080318 | -0.068708 | -0.019721 | -0.20078 | 0.028372 | 0.062874 | 0.40386 | 0.17007 | 0.1417 | -0.20362 | -0.28572 | 0.33023 | -121.374 | 0.47253 | 0.36019 | 0.02996 | -121.3623 | -121.3134 | 121.8875 | 121.621 | 121.5389 | 13.9477 | -121.7963 | 0.45069 | 0.4623 | 0.51128 | 0.39858 | -121.4944
1763.7188 | 121.8475 | -0.77362 | 121.1563 | 1.4211e-13 | -0.033506 | -0.00023069 | 0.059945 | -0.0096276 | 0.055482 | -0.23586 | -0.003965 | 0.016199 | 0.02154 | 0.032474 | 0.0064951 | -0.25076 | 13.3114 | -0.48913 | 121.2329 | 120.9618 | 120.8843 | -0.62626 | -0.058476 | -0.137 | -0.17082 | -0.071161 | -0.068708 | -0.019721 | -0.20536 | 0.14736 | 0.076587 | 0.52286 | 0.28449 | 0.13714 | -0.1945 | -0.27202 | 0.56826 | -121.2275 | 0.71515 | 0.6028 | 0.034539 | -121.225 | -121.176 | 122.0065 | 121.7354 | 121.6579 | 14.085 | -121.7826 | 0.70246 | 0.70491 | 0.7539 | 0.63662 | -121.3617
1765.4688 | 121.843 | -0.74158 | 121.1609 | 1.4211e-13 | -0.033506 | -0.00044449 | 0.060158 | -0.009414 | 0.055482 | -0.22823 | -0.0041788 | 0.015772 | 0.02154 | 0.032688 | 0.0062815 | -0.24618 | 13.2244 | -0.49371 | 121.2192 | 120.9527 | 120.8751 | -0.63542 | -0.058476 | -0.13242 | -0.16624 | -0.075739 | -0.06413 | -0.019721 | -0.20536 | 0.10615 | 0.058273 | 0.49539 | 0.24787 | 0.14172 | -0.20824 | -0.28575 | 0.53622 | -121.2366 | 0.6831 | 0.57534 | 0.039118 | -121.225 | -121.1806 | 121.9607 | 121.6942 | 121.6167 | 13.966 | -121.7963 | 0.66584 | 0.67745 | 0.72186 | 0.60915 | -121.3662
1767.1406 | 121.962 | -0.70038 | 121.138 | 1.4211e-13 | -0.033506 | -0.00044449 | 0.060372 | -0.0096276 | 0.055482 | -0.2206 | -0.0041788 | 0.015558 | 0.021967 | 0.032901 | 0.0067087 | -0.29197 | 13.1786 | -0.53033 | 121.1871 | 120.9114 | 120.8339 | -0.6629 | -0.058476 | -0.14158 | -0.16624 | -0.075739 | -0.06413 | -0.015142 | -0.21452 | 0.037482 | 0.049114 | 0.40841 | 0.17004 | 0.13256 | -0.22656 | -0.30407 | 0.48586 | -121.2137 | 0.6419 | 0.53414 | 0.048276 | -121.2021 | -121.1531 | 121.8875 | 121.6118 | 121.5343 | 13.879 | -121.8009 | 0.62464 | 0.63625 | 0.68524 | 0.5588 | -121.3525
1768.875 | 121.9666 | -0.58136 | 121.2616 | 1.4211e-13 | -0.03372 | -0.00044449 | 0.059731 | -0.0096276 | 0.055696 | -0.22823 | -0.0041788 | 0.015772 | 0.021967 | 0.032688 | 0.0067087 | -0.15462 | 13.1969 | -0.39756 | 121.3153 | 121.0488 | 120.9804 | -0.53469 | -0.067633 | -0.137 | -0.1754 | -0.075739 | -0.059551 | -0.019721 | -0.20536 | 0.046673 | 0.053712 | 0.42674 | 0.1838 | 0.13712 | -0.21279 | -0.28115 | 0.376 | -121.3373 | 0.51373 | 0.40596 | 0.02996 | -121.3211 | -121.2813 | 121.8967 | 121.6302 | 121.5618 | 13.7783 | -121.7963 | 0.50562 | 0.52181 | 0.56164 | 0.44436 | -121.467
1770.625 | 121.8246 | -0.56305 | 121.3303 | 1.4211e-13 | -0.03372 | -0.00023069 | 0.059731 | -0.0092004 | 0.055268 | -0.2206 | -0.003965 | 0.015772 | 0.02154 | 0.032901 | 0.0064951 | -0.12715 | 13.1603 | -0.37467 | 121.3565 | 121.0946 | 121.0079 | -0.50263 | -0.035582 | -0.137 | -0.15708 | -0.075739 | -0.068708 | -0.015142 | -0.20536 | 0.060415 | 0.026253 | 0.4359 | 0.18838 | 0.12796 | -0.23566 | -0.32235 | 0.35769 | -121.406 | 0.52747 | 0.40597 | 0.048275 | -121.399 | -121.3454 | 121.9196 | 121.6576 | 121.571 | 13.7234 | -121.8329 | 0.48731 | 0.49434 | 0.54791 | 0.42605 | -121.5356
1772.375 | 121.9849 | -0.5127 | 121.2799 | 1.4211e-13 | -0.033933 | -0.00023069 | 0.059945 | -0.0096276 | 0.055696 | -0.22823 | -0.003965 | 0.015772 | 0.021967 | 0.032688 | 0.0062815 | -0.12715 | 13.1237 | -0.36551 | 121.3519 | 121.0946 | 121.0079 | -0.50263 | -0.067633 | -0.137 | -0.1754 | -0.071161 | -0.059551 | -0.0243 | -0.20994 | 0.010061 | 0.072029 | 0.38555 | 0.14718 | 0.13712 | -0.18531 | -0.27199 | 0.30276 | -121.3511 | 0.44506 | 0.3373 | 0.034539 | -121.3395 | -121.3042 | 121.8646 | 121.6073 | 121.5206 | 13.6364 | -121.7825 | 0.44153 | 0.45314 | 0.4884 | 0.37569 | -121.4898
1774.0625 | 121.9757 | -0.59509 | 121.225 | 1.4211e-13 | -0.033506 | -1.7092e-05 | 0.059945 | -0.0096276 | 0.055268 | -0.22823 | -0.003965 | 0.015986 | 0.021754 | 0.032474 | 0.0064951 | -0.1592 | 13.0733 | -0.4113 | 121.3245 | 121.0534 | 120.9667 | -0.54384 | -0.072212 | -0.137 | -0.17082 | -0.075739 | -0.06413 | -0.019721 | -0.20994 | 0.051249 | 0.099489 | 0.4359 | 0.18379 | 0.13255 | -0.17159 | -0.25827 | 0.38516 | -121.3007 | 0.52288 | 0.42427 | 0.039118 | -121.2891 | -121.2447 | 121.9196 | 121.6485 | 121.5618 | 13.6684 | -121.7688 | 0.51935 | 0.53096 | 0.57537 | 0.45809 | -121.4349
1775.8125 | 121.9528 | -0.56763 | 121.2982 | 1.4211e-13 | -0.034147 | -0.00044449 | 0.059945 | -0.009414 | 0.055482 | -0.22823 | -0.0043924 | 0.015986 | 0.021754 | 0.032688 | 0.0064951 | -0.11341 | 13.0504 | -0.36551 | 121.3611 | 121.0946 | 121.0125 | -0.49348 | -0.063054 | -0.137 | -0.16624 | -0.080318 | -0.045815 | -0.0243 | -0.20994 | 0.074151 | 0.062874 | 0.45421 | 0.20211 | 0.12796 | -0.20362 | -0.28572 | 0.35769 | -121.3785 | 0.50457 | 0.40139 | 0.043697 | -121.344 | -121.3225 | 121.9287 | 121.6622 | 121.5801 | 13.6181 | -121.7917 | 0.48731 | 0.52181 | 0.54333 | 0.43062 | -121.5082
1777.5625 | 121.843 | -0.69122 | 121.225 | 1.4211e-13 | -0.03372 | -1.7092e-05 | 0.059945 | -0.0096276 | 0.055268 | -0.23586 | -0.0043924 | 0.015986 | 0.021754 | 0.032901 | 0.0060677 | -0.24161 | 12.936 | -0.50286 | 121.2329 | 120.9572 | 120.8751 | -0.64458 | -0.058476 | -0.13242 | -0.16624 | -0.075739 | -0.050394 | -0.010564 | -0.20078 | 0.046642 | 0.007922 | 0.44962 | 0.18836 | 0.14172 | -0.26775 | -0.34984 | 0.49044 | -121.3007 | 0.63275 | 0.52498 | 0.034539 | -121.2754 | -121.2355 | 121.9241 | 121.6485 | 121.5664 | 13.6272 | -121.8696 | 0.61548 | 0.64083 | 0.68066 | 0.5588 | -121.4258
1779.2188 | 121.8567 | -0.55389 | 121.3669 | 1.4211e-13 | -0.03372 | -0.00044449 | 0.059945 | -0.0096276 | 0.055482 | -0.22823 | -0.0041788 | 0.015558 | 0.021967 | 0.032688 | 0.0064951 | -0.076785 | 12.968 | -0.31973 | 121.4115 | 121.1541 | 121.0629 | -0.46142 | -0.067633 | -0.137 | -0.16166 | -0.066582 | -0.068708 | -0.019721 | -0.21452 | 0.09247 | 0.044573 | 0.47711 | 0.23416 | 0.14169 | -0.21276 | -0.30402 | 0.33938 | -121.4335 | 0.48626 | 0.39223 | 0.052855 | -121.4356 | -121.3866 | 121.9653 | 121.708 | 121.6168 | 13.5219 | -121.8283 | 0.48731 | 0.48519 | 0.53417 | 0.41689 | -121.5814
1780.9062 | 121.8658 | -0.52185 | 121.3623 | 1.4211e-13 | -0.033933 | -0.00023069 | 0.059731 | -0.009414 | 0.055482 | -0.23586 | -0.003965 | 0.015772 | 0.021967 | 0.032688 | 0.0062815 | -0.10426 | 12.8902 | -0.35178 | 121.3931 | 121.1129 | 121.0262 | -0.4889 | -0.063054 | -0.137 | -0.16624 | -0.075739 | -0.054973 | -0.015142 | -0.20078 | 0.032954 | 0.030836 | 0.4176 | 0.17007 | 0.13712 | -0.24939 | -0.33608 | 0.32107 | -121.438 | 0.4588 | 0.35561 | 0.034539 | -121.4173 | -121.3774 | 121.915 | 121.6348 | 121.5481 | 13.412 | -121.8512 | 0.44611 | 0.46688 | 0.50671 | 0.38485 | -121.5631
1782.6562 | 121.9391 | -0.54016 | 121.3257 | 1.4211e-13 | -0.034147 | 0.00019651 | 0.059945 | -0.0098414 | 0.055482 | -0.22823 | -0.0041788 | 0.016199 | 0.02154 | 0.033115 | 0.0062815 | -0.15004 | 12.8261 | -0.40672 | 121.3336 | 121.058 | 120.9804 | -0.53469 | -0.053897 | -0.13242 | -0.17082 | -0.071161 | -0.059551 | -0.010564 | -0.20536 | 0.005474 | 0.007938 | 0.39012 | 0.13344 | 0.12797 | -0.26772 | -0.34524 | 0.3348 | -121.3968 | 0.48626 | 0.36934 | 0.034539 | -121.3852 | -121.3362 | 121.8738 | 121.5981 | 121.5206 | 13.3662 | -121.8604 | 0.469 | 0.48061 | 0.5296 | 0.40774 | -121.531
1784.3906 | 121.9986 | -0.51727 | 121.3303 | 1.4211e-13 | -0.03372 | -0.00044449 | 0.059945 | -0.009414 | 0.055482 | -0.22823 | -0.003965 | 0.015558 | 0.021967 | 0.032901 | 0.0062815 | -0.12257 | 12.7803 | -0.39298 | 121.3382 | 121.0809 | 120.9942 | -0.52095 | -0.058476 | -0.13242 | -0.16166 | -0.080318 | -0.068708 | -0.015142 | -0.20994 | -0.003677 | 0.00794 | 0.3947 | 0.12429 | 0.12797 | -0.2494 | -0.33608 | 0.30734 | -121.4106 | 0.4588 | 0.35561 | 0.048276 | -121.399 | -121.3454 | 121.8555 | 121.5981 | 121.5115 | 13.2976 | -121.8512 | 0.43695 | 0.44856 | 0.50213 | 0.38485 | -121.5402
1786.0781 | 121.9482 | -0.52643 | 121.2982 | 1.4211e-13 | -0.033933 | -1.7092e-05 | 0.059731 | -0.0098414 | 0.055696 | -0.23586 | -0.0043924 | 0.015772 | 0.02154 | 0.032901 | 0.0062815 | -0.058472 | 12.7803 | -0.306 | 121.4206 | 121.1541 | 121.0766 | -0.44769 | -0.058476 | -0.13242 | -0.16166 | -0.080318 | -0.059551 | -0.019721 | -0.20536 | 0.078741 | 0.12239 | 0.46796 | 0.22043 | 0.14169 | -0.1441 | -0.22162 | 0.32107 | -121.3785 | 0.46795 | 0.36477 | 0.043697 | -121.3578 | -121.3179 | 121.947 | 121.6806 | 121.603 | 13.3067 | -121.7459 | 0.44611 | 0.46688 | 0.50671 | 0.394 | -121.5036
1787.8438 | 121.9574 | -0.54474 | 121.3028 | 1.4211e-13 | -0.034361 | -0.00023069 | 0.059731 | -0.0098414 | 0.055482 | -0.22823 | -0.0041788 | 0.015558 | 0.021326 | 0.032901 | 0.0062815 | -0.19582 | 12.6612 | -0.45708 | 121.2741 | 121.003 | 120.9209 | -0.59421 | -0.053897 | -0.137 | -0.17082 | -0.071161 | -0.054973 | -0.015142 | -0.20536 | -0.049474 | -0.028692 | 0.34892 | 0.087658 | 0.13713 | -0.29978 | -0.38187 | 0.33938 | -121.374 | 0.49084 | 0.37392 | 0.034539 | -121.3578 | -121.3179 | 121.8188 | 121.5478 | 121.4657 | 13.206 | -121.897 | 0.47358 | 0.48977 | 0.5296 | 0.40774 | -121.5082
1789.5312 | 121.9299 | -0.52643 | 121.3623 | 1.4211e-13 | -0.034361 | -0.00044449 | 0.059731 | -0.0096276 | 0.055482 | -0.24349 | -0.004606 | 0.015772 | 0.021326 | 0.032688 | 0.0062815 | -0.072207 | 12.6841 | -0.33347 | 121.4023 | 121.1404 | 121.0583 | -0.45685 | -0.053897 | -0.137 | -0.16624 | -0.075739 | -0.059551 | -0.019721 | -0.21452 | 0.069583 | 0.039993 | 0.45422 | 0.19296 | 0.12338 | -0.22192 | -0.30403 | 0.31191 | -121.438 | 0.47253 | 0.36019 | 0.048276 | -121.4219 | -121.382 | 121.9287 | 121.6668 | 121.5847 | 13.2106 | -121.8192 | 0.45069 | 0.46688 | 0.50671 | 0.38943 | -121.5768
1791.2656 | 121.9162 | -0.54474 | 121.3074 | 1.4211e-13 | -0.03372 | 0.00019651 | 0.059731 | -0.0096276 | 0.055696 | -0.22823 | -0.0041788 | 0.015986 | 0.02154 | 0.032901 | 0.0062815 | -0.09052 | 12.6383 | -0.36551 | 121.3657 | 121.1083 | 121.0217 | -0.50263 | -0.053897 | -0.13242 | -0.17082 | -0.075739 | -0.059551 | -0.015142 | -0.20536 | 0.042105 | 0.058298 | 0.45422 | 0.17922 | 0.13712 | -0.19904 | -0.28572 | 0.33938 | -121.3831 | 0.49084 | 0.37392 | 0.034539 | -121.3669 | -121.3225 | 121.9104 | 121.6531 | 121.5664 | 13.1831 | -121.81 | 0.469 | 0.48519 | 0.5296 | 0.41231 | -121.5127
1793 | 121.962 | -0.5127 | 121.3669 | 1.4211e-13 | -0.033933 | -0.00044449 | 0.059731 | -0.009414 | 0.055696 | -0.22823 | -0.003965 | 0.016199 | 0.021326 | 0.032688 | 0.0060677 | -0.072207 | 12.588 | -0.33347 | 121.3977 | 121.1312 | 121.0583 | -0.47974 | -0.049318 | -0.14158 | -0.17082 | -0.071161 | -0.06413 | -0.010564 | -0.20994 | 0.032956 | 0.030838 | 0.44049 | 0.17923 | 0.14627 | -0.23565 | -0.3086 | 0.30276 | -121.438 | 0.46338 | 0.34188 | 0.039118 | -121.431 | -121.3774 | 121.9104 | 121.6439 | 121.571 | 13.1007 | -121.8466 | 0.44153 | 0.44856 | 0.50213 | 0.37111 | -121.5768
1794.75 | 121.962 | -0.49896 | 121.3531 | 1.4211e-13 | -0.034147 | -0.00044449 | 0.059945 | -0.0096276 | 0.055482 | -0.22823 | -0.0041788 | 0.015986 | 0.02154 | 0.033115 | 0.0060677 | -0.049315 | 12.533 | -0.31058 | 121.4252 | 121.1587 | 121.0812 | -0.44311 | -0.053897 | -0.137 | -0.16624 | -0.071161 | -0.050394 | -0.019721 | -0.2191 | 0.055854 | 0.072041 | 0.44965 | 0.18839 | 0.13253 | -0.19445 | -0.27198 | 0.27987 | -121.4243 | 0.44507 | 0.33272 | 0.052855 | -121.4035 | -121.3729 | 121.9242 | 121.6577 | 121.5801 | 13.032 | -121.7963 | 0.4278 | 0.44857 | 0.47924 | 0.36196 | -121.5722
1796.4375 | 121.843 | -0.58594 | 121.3303 | 1.4211e-13 | -0.033933 | -0.00044449 | 0.060372 | -0.0096276 | 0.055696 | -0.22823 | -0.0041788 | 0.016199 | 0.021326 | 0.032901 | 0.0058541 | -0.076785 | 12.4964 | -0.3472 | 121.3886 | 121.1221 | 121.0445 | -0.49348 | -0.044739 | -0.13242 | -0.17082 | -0.075739 | -0.06413 | -0.015142 | -0.21452 | 0.092461 | 0.058302 | 0.50915 | 0.23874 | 0.14627 | -0.20819 | -0.28572 | 0.37142 | -121.406 | 0.5412 | 0.41512 | 0.043697 | -121.3944 | -121.3454 | 121.9745 | 121.708 | 121.6305 | 13.0823 | -121.8237 | 0.5102 | 0.52181 | 0.5708 | 0.45351 | -121.5448
1798.1875 | 121.8796 | -0.53101 | 121.4218 | 1.4211e-13 | -0.034574 | -0.00023069 | 0.060158 | -0.0096276 | 0.055268 | -0.23586 | -0.0041788 | 0.016199 | 0.02154 | 0.033115 | 0.0060677 | 0.001048 | 12.4781 | -0.26479 | 121.4664 | 121.1999 | 121.1224 | -0.41563 | -0.049318 | -0.137 | -0.17082 | -0.075739 | -0.059551 | -0.019721 | -0.21452 | 0.11537 | 0.044581 | 0.53205 | 0.26621 | 0.15084 | -0.2219 | -0.29943 | 0.31649 | -121.4976 | 0.48169 | 0.36019 | 0.043697 | -121.4814 | -121.4415 | 121.9974 | 121.7309 | 121.6534 | 13.0091 | -121.8374 | 0.45527 | 0.47145 | 0.51128 | 0.394 | -121.6363
1799.9219 | 121.9254 | -0.46234 | 121.4081 | 1.4211e-13 | -0.034147 | -0.00065809 | 0.060158 | -0.0096276 | 0.055268 | -0.22823 | -0.0043924 | 0.015772 | 0.021754 | 0.032688 | 0.0056405 | 0.014783 | 12.4232 | -0.25564 | 121.4801 | 121.2091 | 121.1361 | -0.40648 | -0.053897 | -0.13242 | -0.17082 | -0.075739 | -0.059551 | -0.015142 | -0.20994 | 0.055864 | 0.07205 | 0.47712 | 0.2067 | 0.15084 | -0.19901 | -0.27196 | 0.2524 | -121.4838 | 0.40844 | 0.29152 | 0.039118 | -121.4676 | -121.4232 | 121.9425 | 121.6714 | 121.5985 | 12.8855 | -121.8146 | 0.3866 | 0.40279 | 0.4472 | 0.32992 | -121.618
1801.5938 | 121.8979 | -0.49896 | 121.4264 | 1.4211e-13 | -0.03372 | -0.00023069 | 0.059945 | -0.0096276 | 0.055696 | -0.22823 | -0.0041788 | 0.015986 | 0.02154 | 0.032901 | 0.0062815 | 0.001048 | 12.4003 | -0.27853 | 121.4664 | 121.2045 | 121.1224 | -0.42021 | -0.044739 | -0.13242 | -0.1754 | -0.071161 | -0.059551 | -0.015142 | -0.21452 | 0.078749 | 0.040003 | 0.50001 | 0.22043 | 0.14169 | -0.2219 | -0.30401 | 0.28445 | -121.4976 | 0.45422 | 0.32356 | 0.039118 | -121.4859 | -121.4415 | 121.9654 | 121.7035 | 121.6213 | 12.8992 | -121.8466 | 0.4278 | 0.43941 | 0.48382 | 0.36654 | -121.6409
1803.3438 | 121.9208 | -0.48523 | 121.3715 | 1.4211e-13 | -0.034361 | -0.00044449 | 0.059945 | -0.009414 | 0.055482 | -0.23586 | -0.0041788 | 0.015986 | 0.021754 | 0.032901 | 0.0058541 | -0.003531 | 12.3362 | -0.27853 | 121.4481 | 121.1816 | 121.1086 | -0.43395 | -0.044739 | -0.137 | -0.1754 | -0.080318 | -0.054973 | -0.019721 | -0.20536 | 0.051279 | 0.076622 | 0.4817 | 0.2067 | 0.15542 | -0.18986 | -0.26282 | 0.27987 | -121.4518 | 0.44049 | 0.30983 | 0.02996 | -121.4264 | -121.3912 | 121.9333 | 121.6668 | 121.5939 | 12.8214 | -121.8054 | 0.40491 | 0.43026 | 0.46551 | 0.34823 | -121.5768
1805.0312 | 121.9803 | -0.40283 | 121.4172 | 1.4211e-13 | -0.034574 | -0.00044449 | 0.059945 | -0.0096276 | 0.055696 | -0.22823 | -0.003965 | 0.015772 | 0.021326 | 0.032901 | 0.0060677 | 0.037675 | 12.2995 | -0.22817 | 121.5076 | 121.2457 | 121.1727 | -0.379 | -0.053897 | -0.137 | -0.16624 | -0.075739 | -0.054973 | -0.019721 | -0.20536 | 0.023829 | 0.090365 | 0.44051 | 0.17467 | 0.15084 | -0.17153 | -0.24449 | 0.19747 | -121.493 | 0.34893 | 0.23659 | 0.039118 | -121.4722 | -121.437 | 121.9104 | 121.6485 | 121.5756 | 12.7024 | -121.7962 | 0.32709 | 0.34786 | 0.38311 | 0.26583 | -121.6226
1806.7812 | 121.9025 | -0.44403 | 121.4401 | 1.4211e-13 | -0.034788 | -1.7092e-05 | 0.059731 | -0.0096276 | 0.055696 | -0.22823 | -0.0043924 | 0.015772 | 0.021326 | 0.033115 | 0.0058541 | 0.042253 | 12.2675 | -0.23275 | 121.5076 | 121.2411 | 121.1773 | -0.38358 | -0.040161 | -0.137 | -0.17082 | -0.080318 | -0.06413 | -0.015142 | -0.20994 | 0.060449 | 0.067476 | 0.48628 | 0.21129 | 0.15084 | -0.199 | -0.2628 | 0.23409 | -121.5204 | 0.40387 | 0.27321 | 0.039118 | -121.5043 | -121.4553 | 121.9516 | 121.6852 | 121.6214 | 12.7115 | -121.8237 | 0.36371 | 0.3799 | 0.42889 | 0.30703 | -121.6501
1808.4531 | 121.8796 | -0.45319 | 121.4584 | 1.4211e-13 | -0.034361 | -0.00044449 | 0.059945 | -0.0096276 | 0.055696 | -0.2206 | -0.0041788 | 0.015772 | 0.02154 | 0.032901 | 0.0060677 | 0.046831 | 12.2217 | -0.22817 | 121.5122 | 121.2503 | 121.1727 | -0.379 | -0.044739 | -0.137 | -0.17082 | -0.071161 | -0.06413 | -0.015142 | -0.20994 | 0.074183 | 0.053744 | 0.50002 | 0.22502 | 0.15084 | -0.20815 | -0.28569 | 0.24325 | -121.5296 | 0.40845 | 0.28237 | 0.039118 | -121.5226 | -121.4736 | 121.9654 | 121.7035 | 121.6259 | 12.6749 | -121.8374 | 0.38202 | 0.38906 | 0.43804 | 0.31618 | -121.6684
1810.1875 | 121.8842 | -0.46234 | 121.4401 | 1.4211e-13 | -0.034574 | -0.00044449 | 0.060158 | -0.0096276 | 0.055482 | -0.22823 | -0.0041788 | 0.015772 | 0.02154 | 0.033329 | 0.0058541 | 0.037675 | 12.1484 | -0.23732 | 121.4984 | 121.2274 | 121.1544 | -0.39732 | -0.044739 | -0.137 | -0.1754 | -0.075739 | -0.059551 | -0.015142 | -0.20536 | 0.065022 | 0.058319 | 0.50002 | 0.22502 | 0.16 | -0.21274 | -0.28569 | 0.25698 | -121.5159 | 0.4176 | 0.28694 | 0.02996 | -121.4997 | -121.4553 | 121.9608 | 121.6897 | 121.6168 | 12.6108 | -121.8374 | 0.3866 | 0.40279 | 0.4472 | 0.32534 | -121.6455
1811.875 | 121.9803 | -1.4328 | 120.401 | 1.4211e-13 | -0.034361 | -0.00044449 | 0.060158 | -0.0098414 | 0.055268 | -0.23586 | -0.003965 | 0.015986 | 0.02154 | 0.032688 | 0.0054267 | -0.97873 | 11.5074 | -1.2812 | 120.4134 | 120.1559 | 120.0739 | -1.4596 | -0.049318 | -0.137 | -0.17082 | -0.071161 | -0.050394 | -0.015142 | -0.20536 | -0.026829 | 0.012365 | 0.45407 | 0.15163 | 0.17846 | -0.24508 | -0.32712 | 1.2274 | -120.4722 | 1.3835 | 1.262 | 0.034539 | -120.4514 | -120.4161 | 121.8462 | 121.5887 | 121.5067 | 12.9402 | -121.8606 | 1.3616 | 1.3824 | 1.4177 | 1.2958 | -120.6064
1813.6094 | 121.9711 | -1.9821 | 119.8837 | 1.4211e-13 | -0.034147 | -0.00044449 | 0.059945 | -0.0096276 | 0.055909 | -0.22823 | -0.0041788 | 0.015986 | 0.02154 | 0.033329 | 0.0060677 | -1.0795 | 11.4067 | -1.391 | 120.3081 | 120.046 | 119.9732 | -1.5604 | -0.040161 | -0.137 | -0.17998 | -0.075739 | -0.054973 | -0.010564 | -0.21452 | 0.42175 | 0.42433 | 0.90266 | 0.59107 | 0.16932 | 0.1623 | 0.089423 | 1.7676 | -119.9595 | 1.942 | 1.8021 | 0.03454 | -119.9387 | -119.8943 | 122.2902 | 122.0281 | 121.9553 | 13.3888 | -121.4441 | 1.9064 | 1.9271 | 1.9716 | 1.8451 | -120.0982
1815.2812 | 121.9345 | -1.7395 | 120.0943 | 1.4211e-13 | -0.034574 | -0.00065809 | 0.059945 | -0.009414 | 0.055482 | -0.22823 | -0.0043924 | 0.015986 | 0.021754 | 0.033329 | 0.0060677 | -1.1527 | 11.2739 | -1.4643 | 120.2257 | 119.9682 | 119.8907 | -1.6382 | -0.049318 | -0.137 | -0.1754 | -0.066582 | -0.059551 | -0.019721 | -0.21452 | 0.1013 | 0.13135 | 0.5868 | 0.2752 | 0.1739 | -0.12612 | -0.20356 | 1.525 | -120.1609 | 1.6902 | 1.5641 | 0.039118 | -120.1539 | -120.114 | 121.9652 | 121.7077 | 121.6302 | 13.0134 | -121.7325 | 1.6729 | 1.68 | 1.7198 | 1.6025 | -120.3088
1817.0312 | 121.9391 | -1.8539 | 119.9982 | 1.4211e-13 | -0.034361 | -0.00023069 | 0.059731 | -0.0096276 | 0.055909 | -0.23586 | -0.003965 | 0.015986 | 0.02154 | 0.033115 | 0.0056405 | -1.2901 | 11.1457 | -1.6154 | 120.0837 | 119.8171 | 119.7534 | -1.7847 | -0.021846 | -0.137 | -0.17082 | -0.071161 | -0.059551 | -0.015142 | -0.20536 | 0.06921 | 0.085553 | 0.56388 | 0.23856 | 0.16935 | -0.18109 | -0.24479 | 1.6486 | -120.0693 | 1.8321 | 1.6831 | 0.034539 | -120.0577 | -120.0133 | 121.9377 | 121.671 | 121.6073 | 12.9997 | -121.7829 | 1.7828 | 1.7944 | 1.8388 | 1.7169 | -120.2035
1818.7812 | 121.9528 | -2.0325 | 119.8151 | 1.4211e-13 | -0.034574 | -0.00044449 | 0.060158 | -0.0098414 | 0.055268 | -0.22823 | -0.0041788 | 0.015772 | 0.02154 | 0.033115 | 0.0056405 | -1.3862 | 11.0404 | -1.7024 | 119.9876 | 119.7255 | 119.6481 | -1.8855 | -0.021846 | -0.137 | -0.16624 | -0.075739 | -0.054973 | -0.015142 | -0.20078 | 0.147 | 0.17251 | 0.64627 | 0.3301 | 0.1831 | -0.089564 | -0.16699 | 1.8317 | -119.8908 | 2.0106 | 1.8662 | 0.034539 | -119.87 | -119.8302 | 122.02 | 121.758 | 121.6805 | 13.0729 | -121.7005 | 1.9567 | 1.9775 | 2.0173 | 1.8955 | -120.0158
1820.4688 | 121.9116 | -1.918 | 119.9844 | 1.4211e-13 | -0.034574 | -1.7092e-05 | 0.060158 | -0.0098414 | 0.055268 | -0.22823 | -0.0043924 | 0.015558 | 0.02154 | 0.033329 | 0.0058541 | -1.3496 | 10.9855 | -1.6703 | 120.0242 | 119.7667 | 119.6893 | -1.8443 | -0.058476 | -0.14158 | -0.17082 | -0.071161 | -0.06413 | -0.015142 | -0.20078 | 0.073771 | 0.039767 | 0.56845 | 0.2477 | 0.17393 | -0.21773 | -0.29516 | 1.7173 | -120.0556 | 1.8596 | 1.7472 | 0.02996 | -120.0486 | -119.9996 | 121.9422 | 121.6847 | 121.6073 | 12.9035 | -121.8287 | 1.8469 | 1.8539 | 1.9029 | 1.7764 | -120.1852
1822.2031 | 121.9757 | -1.6891 | 120.1126 | 1.4211e-13 | -0.034574 | -1.7092e-05 | 0.059945 | -0.010055 | 0.055055 | -0.2206 | -0.003965 | 0.015772 | 0.02154 | 0.033329 | 0.0054267 | -1.1756 | 11.0679 | -1.4964 | 120.1982 | 119.9361 | 119.8678 | -1.684 | -0.058476 | -0.137 | -0.16166 | -0.066582 | -0.050394 | -0.015142 | -0.20536 | 0.005151 | 0.085572 | 0.51355 | 0.1928 | 0.18765 | -0.17648 | -0.24477 | 1.4838 | -120.1792 | 1.6307 | 1.5275 | 0.043697 | -120.163 | -120.1278 | 121.8873 | 121.6253 | 121.557 | 12.757 | -121.7966 | 1.6226 | 1.6388 | 1.674 | 1.5521 | -120.318
1823.9375 | 121.843 | -1.7807 | 120.1584 | 1.4211e-13 | -0.034361 | -0.00044449 | 0.059945 | -0.0098414 | 0.055268 | -0.22823 | -0.0041788 | 0.015772 | 0.02154 | 0.032901 | 0.0058541 | -1.171 | 10.9946 | -1.5009 | 120.1753 | 119.9316 | 119.8587 | -1.6794 | -0.063054 | -0.14616 | -0.1754 | -0.066582 | -0.059551 | -0.015142 | -0.20536 | 0.10128 | 0.016904 | 0.60968 | 0.27977 | 0.17849 | -0.22683 | -0.2997 | 1.5753 | -120.225 | 1.7176 | 1.6053 | 0.02996 | -120.2179 | -120.1735 | 121.956 | 121.7123 | 121.6394 | 12.7753 | -121.8378 | 1.7141 | 1.7212 | 1.7656 | 1.6345 | -120.3637
1825.6875 | 121.8475 | -1.8631 | 120.0668 | 1.4211e-13 | -0.034574 | -0.00023069 | 0.059945 | -0.0096276 | 0.055268 | -0.22823 | -0.0041788 | 0.015986 | 0.021326 | 0.033115 | 0.0056405 | -1.2489 | 10.8802 | -1.5833 | 120.1066 | 119.8537 | 119.7854 | -1.7618 | -0.063054 | -0.14616 | -0.1754 | -0.075739 | -0.054973 | -0.010564 | -0.20536 | 0.10126 | 0.039781 | 0.61425 | 0.27976 | 0.1785 | -0.21312 | -0.28141 | 1.6577 | -120.1426 | 1.8 | 1.6877 | 0.02996 | -120.1218 | -120.0774 | 121.9697 | 121.7168 | 121.6485 | 12.7433 | -121.8287 | 1.7874 | 1.8081 | 1.8525 | 1.7169 | -120.2722
1827.375 | 121.875 | -1.8173 | 120.1126 | 1.4211e-13 | -0.034788 | -0.00044449 | 0.059945 | -0.009414 | 0.055268 | -0.2206 | -0.003965 | 0.015558 | 0.021326 | 0.033329 | 0.0056405 | -1.2397 | 10.8527 | -1.5696 | 120.1249 | 119.8583 | 119.7992 | -1.7481 | -0.058476 | -0.14158 | -0.17082 | -0.075739 | -0.054973 | -0.010564 | -0.20078 | 0.06922 | 0.012318 | 0.57763 | 0.24772 | 0.1785 | -0.25432 | -0.31345 | 1.6165 | -120.1883 | 1.7588 | 1.6465 | 0.02996 | -120.1676 | -120.1232 | 121.9423 | 121.6756 | 121.6165 | 12.67 | -121.8607 | 1.7416 | 1.7623 | 1.8068 | 1.6757 | -120.3134
1829.1094 | 121.9711 | -1.7487 | 120.0851 | 1.4211e-13 | -0.034574 | -0.00044449 | 0.059517 | -0.0096276 | 0.055268 | -0.22823 | -0.0041788 | 0.015345 | 0.021754 | 0.033329 | 0.0054267 | -1.2214 | 10.7932 | -1.5513 | 120.1203 | 119.8766 | 119.8037 | -1.7298 | -0.067633 | -0.13242 | -0.15708 | -0.066582 | -0.050394 | -0.019721 | -0.20536 | 0.018871 | 0.035205 | 0.52727 | 0.19737 | 0.1785 | -0.20854 | -0.2814 | 1.5433 | -120.1517 | 1.681 | 1.5916 | 0.048275 | -120.1355 | -120.1049 | 121.869 | 121.6253 | 121.5524 | 12.5418 | -121.8149 | 1.6821 | 1.6983 | 1.7289 | 1.6162 | -120.2905
1830.8438 | 121.994 | -1.68 | 120.1401 | 1.4211e-13 | -0.034788 | -0.00044449 | 0.059945 | -0.0096276 | 0.055696 | -0.2206 | -0.0041788 | 0.015345 | 0.021326 | 0.033329 | 0.0056405 | -1.1802 | 10.7657 | -1.5238 | 120.1616 | 119.9087 | 119.8266 | -1.7069 | -0.053897 | -0.137 | -0.14793 | -0.071161 | -0.050394 | -0.019721 | -0.20078 | -0.026898 | 0.021479 | 0.49982 | 0.15617 | 0.18307 | -0.23142 | -0.31344 | 1.4792 | -120.2112 | 1.6261 | 1.5321 | 0.052854 | -120.1905 | -120.1598 | 121.8415 | 121.5886 | 121.5066 | 12.4457 | -121.847 | 1.6088 | 1.6296 | 1.6603 | 1.543 | -120.3409
1832.5312 | 121.907 | -1.6113 | 120.282 | 1.4211e-13 | -0.034574 | -0.00023069 | 0.059945 | -0.0098414 | 0.055268 | -0.24349 | -0.0041788 | 0.015986 | 0.021326 | 0.033329 | 0.0056405 | -1.0382 | 10.8115 | -1.3819 | 120.3081 | 120.0506 | 119.9777 | -1.5695 | -0.044739 | -0.14158 | -0.15708 | -0.071161 | -0.059551 | -0.015142 | -0.1962 | 0.041805 | 0.026081 | 0.57308 | 0.22943 | 0.18763 | -0.23138 | -0.30425 | 1.4151 | -120.3531 | 1.5666 | 1.4542 | 0.039117 | -120.3415 | -120.2971 | 121.9194 | 121.6619 | 121.5891 | 12.4228 | -121.8515 | 1.5402 | 1.5518 | 1.5962 | 1.4697 | -120.4782
1834.2812 | 121.8384 | -1.8448 | 120.108 | 1.4211e-13 | -0.034788 | -0.00023069 | 0.059945 | -0.0096276 | 0.055696 | -0.22823 | -0.0041788 | 0.015558 | 0.02154 | 0.033115 | 0.0058541 | -1.226 | 10.6283 | -1.5604 | 120.1203 | 119.872 | 119.7946 | -1.7481 | -0.044739 | -0.137 | -0.14335 | -0.075739 | -0.045815 | -0.019721 | -0.1962 | 0.096686 | 0.012317 | 0.61883 | 0.28434 | 0.18766 | -0.23601 | -0.31345 | 1.6486 | -120.1838 | 1.8 | 1.7014 | 0.052853 | -120.1538 | -120.1278 | 121.9651 | 121.7168 | 121.6394 | 12.4731 | -121.8561 | 1.769 | 1.799 | 1.8251 | 1.7078 | -120.3042
1835.9688 | 121.9482 | -1.7258 | 120.1126 | 1.4211e-13 | -0.034574 | -0.00023069 | 0.059945 | -0.0096276 | 0.056123 | -0.22823 | -0.0041788 | 0.015772 | 0.021113 | 0.033115 | 0.0056405 | -1.1893 | 10.5688 | -1.5376 | 120.1524 | 119.8995 | 119.8266 | -1.716 | -0.049318 | -0.13242 | -0.14335 | -0.071161 | -0.050394 | -0.010564 | -0.20078 | 0.00972 | 0.039788 | 0.53644 | 0.18821 | 0.17849 | -0.21311 | -0.28597 | 1.525 | -120.1838 | 1.6765 | 1.5824 | 0.057432 | -120.163 | -120.1232 | 121.8782 | 121.6253 | 121.5524 | 12.2946 | -121.8287 | 1.6546 | 1.6754 | 1.7152 | 1.5933 | -120.3134
1837.7344 | 121.9254 | -1.7441 | 120.1492 | 1.4211e-13 | -0.034574 | -0.00044449 | 0.059945 | -0.0098414 | 0.055482 | -0.22823 | -0.003965 | 0.015558 | 0.02154 | 0.033115 | 0.0056405 | -1.1115 | 10.6054 | -1.4689 | 120.2119 | 119.9682 | 119.8907 | -1.6519 | -0.044739 | -0.13242 | -0.16166 | -0.071161 | -0.050394 | -0.010564 | -0.20536 | 0.092136 | 0.062686 | 0.63258 | 0.2752 | 0.18306 | -0.18105 | -0.25849 | 1.5387 | -120.2204 | 1.6993 | 1.5824 | 0.043697 | -120.1996 | -120.1598 | 121.956 | 121.7123 | 121.6348 | 12.3495 | -121.8012 | 1.6729 | 1.6937 | 1.7335 | 1.6117 | -120.3546
1839.4062 | 121.9391 | -1.6846 | 120.2133 | 1.4211e-13 | -0.034574 | -0.00023069 | 0.059517 | -0.0098414 | 0.055909 | -0.22823 | -0.0041788 | 0.015986 | 0.021113 | 0.033756 | 0.0054267 | -1.084 | 10.578 | -1.4414 | 120.244 | 119.9911 | 119.9182 | -1.6245 | -0.053897 | -0.137 | -0.14793 | -0.066582 | -0.050394 | -0.010564 | -0.20078 | 0.060099 | 0.030648 | 0.60054 | 0.24316 | 0.18306 | -0.22224 | -0.29511 | 1.4838 | -120.2799 | 1.6307 | 1.5366 | 0.052854 | -120.2637 | -120.2239 | 121.9285 | 121.6756 | 121.6028 | 12.2625 | -121.8378 | 1.618 | 1.6342 | 1.674 | 1.5476 | -120.4141
1841.1406 | 121.8704 | -1.6846 | 120.2316 | 1.4211e-13 | -0.034788 | -0.00044449 | 0.059731 | -0.010269 | 0.055696 | -0.22823 | -0.0041788 | 0.016199 | 0.021326 | 0.033329 | 0.0060677 | -1.0474 | 10.491 | -1.4048 | 120.2714 | 120.0277 | 119.9503 | -1.6016 | -0.053897 | -0.12784 | -0.13877 | -0.075739 | -0.054973 | -0.010564 | -0.20078 | 0.082994 | 0.039808 | 0.63717 | 0.27978 | 0.19679 | -0.20392 | -0.28137 | 1.4838 | -120.3074 | 1.6307 | 1.5458 | 0.062011 | -120.2866 | -120.2422 | 121.956 | 121.7123 | 121.6348 | 12.1756 | -121.8332 | 1.6088 | 1.6296 | 1.674 | 1.5567 | -120.4324
1842.8906 | 121.962 | -1.5976 | 120.2362 | 1.4211e-13 | -0.034361 | -1.7092e-05 | 0.060158 | -0.010055 | 0.055268 | -0.22823 | -0.0041788 | 0.015986 | 0.021326 | 0.033329 | 0.0054267 | -1.0062 | 10.4681 | -1.3636 | 120.3172 | 120.0552 | 119.996 | -1.5466 | -0.058476 | -0.137 | -0.13877 | -0.071161 | -0.050394 | -0.015142 | -0.1962 | 0.050966 | 0.081014 | 0.5914 | 0.23402 | 0.18305 | -0.18102 | -0.24016 | 1.4014 | -120.3074 | 1.5391 | 1.4588 | 0.057432 | -120.2866 | -120.2513 | 121.9148 | 121.6528 | 121.5936 | 12.0657 | -121.7828 | 1.5264 | 1.5472 | 1.5825 | 1.4606 | -120.4324
1844.5625 | 121.9986 | -1.5381 | 120.3003 | 1.4211e-13 | -0.034574 | -0.00023069 | 0.059945 | -0.0098414 | 0.055482 | -0.23586 | -0.003965 | 0.015772 | 0.021113 | 0.033756 | 0.0054267 | -0.91463 | 10.4589 | -1.2766 | 120.4042 | 120.1422 | 120.0739 | -1.4779 | -0.049318 | -0.14158 | -0.14335 | -0.062004 | -0.045815 | -0.010564 | -0.20536 | 0.060141 | 0.10392 | 0.62346 | 0.26149 | 0.20135 | -0.15811 | -0.22641 | 1.3327 | -120.3623 | 1.4888 | 1.3947 | 0.062011 | -120.3461 | -120.3109 | 121.9423 | 121.6803 | 121.612 | 11.997 | -121.7782 | 1.4761 | 1.4923 | 1.5275 | 1.3965 | -120.5057
1846.2969 | 121.9345 | -1.5244 | 120.3552 | 1.4211e-13 | -0.034788 | -0.00044449 | 0.059945 | -0.0096276 | 0.055696 | -0.2206 | -0.0041788 | 0.015558 | 0.021326 | 0.03397 | 0.0056405 | -0.89174 | 10.3857 | -1.2583 | 120.4134 | 120.1651 | 120.0922 | -1.4642 | -0.058476 | -0.13242 | -0.12961 | -0.071161 | -0.054973 | -0.005985 | -0.20994 | 0.060145 | 0.058141 | 0.63262 | 0.26607 | 0.20593 | -0.19015 | -0.26303 | 1.3144 | -120.4264 | 1.4659 | 1.3947 | 0.080327 | -120.4102 | -120.3612 | 121.9377 | 121.6894 | 121.6165 | 11.91 | -121.8194 | 1.4532 | 1.4694 | 1.5184 | 1.3919 | -120.5652
1847.9844 | 121.8384 | -1.4511 | 120.5063 | 1.4211e-13 | -0.034574 | -0.00023069 | 0.059731 | -0.0098414 | 0.055909 | -0.2206 | -0.003965 | 0.015345 | 0.021754 | 0.03397 | 0.0056405 | -0.81848 | 10.3994 | -1.1896 | 120.4912 | 120.2429 | 120.17 | -1.3864 | -0.053897 | -0.12784 | -0.092981 | -0.066582 | -0.050394 | -0.010564 | -0.20536 | 0.064745 | -0.015088 | 0.63263 | 0.26151 | 0.19676 | -0.26337 | -0.33626 | 1.2458 | -120.5729 | 1.3972 | 1.3581 | 0.11238 | -120.5567 | -120.5169 | 121.9423 | 121.694 | 121.6211 | 11.8505 | -121.8927 | 1.3845 | 1.4007 | 1.4405 | 1.3233 | -120.7116
1849.7188 | 121.8796 | -1.5701 | 120.3827 | 1.4211e-13 | -0.034788 | -0.00023069 | 0.060158 | -0.0096276 | 0.055482 | -0.23586 | -0.0043924 | 0.015558 | 0.02154 | 0.033542 | 0.0054267 | -0.92836 | 10.2849 | -1.3086 | 120.3722 | 120.1239 | 120.051 | -1.4963 | -0.058476 | -0.12327 | -0.092981 | -0.071161 | -0.054973 | -0.0243 | -0.2191 | 0.073868 | -0.010529 | 0.64176 | 0.26149 | 0.18762 | -0.25883 | -0.3317 | 1.351 | -120.4539 | 1.5117 | 1.4771 | 0.12611 | -120.4377 | -120.407 | 121.9423 | 121.694 | 121.6211 | 11.8551 | -121.879 | 1.499 | 1.5152 | 1.5458 | 1.4469 | -120.6018
1851.4531 | 121.8567 | -1.6434 | 120.2637 | 1.4211e-13 | -0.035002 | 0.00041031 | 0.060158 | -0.010269 | 0.055482 | -0.22823 | -0.003965 | 0.015986 | 0.021113 | 0.033542 | 0.0056405 | -0.94668 | 10.2346 | -1.327 | 120.3401 | 120.0964 | 120.0281 | -1.5375 | -0.063054 | -0.12784 | -0.092981 | -0.071161 | -0.054973 | -0.015142 | -0.20536 | 0.1059 | 0.07644 | 0.69669 | 0.31642 | 0.21052 | -0.16728 | -0.23558 | 1.438 | -120.3348 | 1.5803 | 1.5504 | 0.11238 | -120.3186 | -120.2788 | 121.9835 | 121.7398 | 121.6715 | 11.878 | -121.8011 | 1.5722 | 1.5884 | 1.6282 | 1.5155 | -120.469
1853.1875 | 121.8567 | -1.5701 | 120.3415 | 1.4211e-13 | -0.034788 | -1.7092e-05 | 0.059731 | -0.0098414 | 0.055482 | -0.23586 | -0.0041788 | 0.015772 | 0.020899 | 0.033542 | 0.0056405 | -0.9009 | 10.2071 | -1.2812 | 120.3859 | 120.1376 | 120.0647 | -1.4917 | -0.058476 | -0.137 | -0.092981 | -0.075739 | -0.050394 | -0.010564 | -0.2191 | 0.078447 | 0.044404 | 0.66923 | 0.28896 | 0.21051 | -0.20389 | -0.27677 | 1.351 | -120.4172 | 1.5117 | 1.4771 | 0.12611 | -120.3919 | -120.3521 | 121.956 | 121.7077 | 121.6349 | 11.7772 | -121.8332 | 1.4944 | 1.5197 | 1.5596 | 1.4331 | -120.5606
1854.8594 | 121.8384 | -1.8814 | 120.0302 | 1.4211e-13 | -0.034788 | -0.00023069 | 0.059945 | -0.010055 | 0.055268 | -0.23586 | -0.0043924 | 0.015772 | 0.021326 | 0.033756 | 0.0056405 | -1.1664 | 10.0148 | -1.5467 | 120.1249 | 119.872 | 119.7992 | -1.7573 | -0.012689 | -0.12327 | -0.097559 | -0.075739 | -0.045815 | -0.019721 | -0.20536 | 0.12415 | 0.094716 | 0.71497 | 0.3347 | 0.21055 | -0.15819 | -0.23105 | 1.6761 | -120.106 | 1.8687 | 1.7839 | 0.1078 | -120.076 | -120.0499 | 122.0063 | 121.7534 | 121.6806 | 11.8962 | -121.7875 | 1.8057 | 1.8356 | 1.8617 | 1.7581 | -120.2356
1856.5938 | 121.8475 | -1.7807 | 120.1492 | 1.4211e-13 | -0.034788 | -1.7092e-05 | 0.059945 | -0.0096276 | 0.055482 | -0.22823 | -0.003965 | 0.016199 | 0.02154 | 0.033756 | 0.0056405 | -1.1756 | 9.9187 | -1.5696 | 120.1066 | 119.8583 | 119.7854 | -1.771 | 0.001048 | -0.12327 | -0.088402 | -0.066582 | -0.059551 | -0.015142 | -0.20536 | 0.009705 | -0.042617 | 0.6051 | 0.2111 | 0.20139 | -0.29094 | -0.3638 | 1.5753 | -120.2158 | 1.7817 | 1.6923 | 0.11696 | -120.2088 | -120.1644 | 121.8873 | 121.639 | 121.5661 | 11.6994 | -121.9202 | 1.7141 | 1.7212 | 1.7656 | 1.6574 | -120.3546
1858.2812 | 121.9666 | -1.5793 | 120.2957 | 1.4211e-13 | -0.035002 | -0.00023069 | 0.059731 | -0.010269 | 0.055482 | -0.23586 | -0.0043924 | 0.015772 | 0.021326 | 0.033756 | 0.0056405 | -0.95126 | 10.0102 | -1.3407 | 120.3172 | 120.0735 | 120.0098 | -1.5512 | -0.00811 | -0.12784 | -0.097559 | -0.066582 | -0.050394 | -0.019721 | -0.20536 | 0.028077 | 0.021505 | 0.62803 | 0.2386 | 0.21052 | -0.22222 | -0.28593 | 1.3739 | -120.3623 | 1.5712 | 1.4817 | 0.1078 | -120.3461 | -120.3154 | 121.8965 | 121.6528 | 121.5891 | 11.5895 | -121.8469 | 1.5127 | 1.5289 | 1.5596 | 1.4514 | -120.5011
1860.0156 | 121.9711 | -1.4648 | 120.4102 | 1.4211e-13 | -0.034788 | -0.00023069 | 0.059517 | -0.0098414 | 0.055482 | -0.23586 | -0.0043924 | 0.015986 | 0.021326 | 0.033329 | 0.0052131 | -0.79101 | 10.0148 | -1.1896 | 120.482 | 120.2246 | 120.1655 | -1.3955 | 0.001048 | -0.13242 | -0.092981 | -0.071161 | -0.050394 | -0.010564 | -0.20536 | 0.06932 | 0.071886 | 0.67383 | 0.27524 | 0.20592 | -0.18555 | -0.2447 | 1.2595 | -120.4813 | 1.4659 | 1.3719 | 0.11238 | -120.4605 | -120.4207 | 121.9469 | 121.6894 | 121.6303 | 11.4797 | -121.8057 | 1.3937 | 1.4144 | 1.4543 | 1.3324 | -120.6155
1861.75 | 121.9849 | -1.4877 | 120.3644 | 1.4211e-13 | -0.035216 | -1.7092e-05 | 0.059731 | -0.0098414 | 0.055482 | -0.23586 | -0.0041788 | 0.015772 | 0.021113 | 0.033542 | 0.0054267 | -0.90547 | 9.9232 | -1.2949 | 120.363 | 120.1147 | 120.0418 | -1.5054 | 0.001048 | -0.11869 | -0.088402 | -0.071161 | -0.054973 | -0.010564 | -0.20536 | -0.017687 | -0.001376 | 0.58226 | 0.19283 | 0.21051 | -0.24967 | -0.32255 | 1.2824 | -120.4355 | 1.4888 | 1.3993 | 0.11696 | -120.4194 | -120.3749 | 121.8507 | 121.6024 | 121.5296 | 11.411 | -121.8698 | 1.4166 | 1.4328 | 1.4772 | 1.369 | -120.5697
1863.5 | 121.8613 | -1.3229 | 120.6116 | 1.4211e-13 | -0.034788 | -0.00044449 | 0.059945 | -0.010055 | 0.055696 | -0.23586 | -0.003965 | 0.015558 | 0.021326 | 0.033756 | 0.0052131 | -0.69487 | 9.9782 | -1.1026 | 120.5736 | 120.3299 | 120.257 | -1.3085 | 0.005626 | -0.12784 | -0.092981 | -0.066582 | -0.054973 | -0.015142 | -0.20536 | 0.014412 | -0.037962 | 0.62807 | 0.22032 | 0.20591 | -0.28166 | -0.35455 | 1.1176 | -120.6782 | 1.3286 | 1.23 | 0.11238 | -120.6665 | -120.6267 | 121.8965 | 121.6529 | 121.58 | 11.3011 | -121.9201 | 1.2564 | 1.268 | 1.3078 | 1.1951 | -120.8169
1865.1875 | 121.994 | -1.799 | 120.0485 | 1.4211e-13 | -0.035002 | -0.00023069 | 0.060158 | -0.0098414 | 0.055268 | -0.2206 | -0.0043924 | 0.015345 | 0.020685 | 0.033542 | 0.0058541 | -1.1848 | 9.6119 | -1.5925 | 120.07 | 119.8171 | 119.7534 | -1.8076 | 0.001048 | -0.12784 | -0.088402 | -0.075739 | -0.050394 | -0.015142 | -0.20994 | -0.008617 | 0.021464 | 0.61426 | 0.20652 | 0.21513 | -0.23145 | -0.29515 | 1.5891 | -120.1243 | 1.8001 | 1.7106 | 0.12154 | -120.0989 | -120.0637 | 121.869 | 121.6161 | 121.5524 | 11.4109 | -121.8562 | 1.7233 | 1.7486 | 1.7839 | 1.6712 | -120.2585
1866.9375 | 121.9116 | -1.8723 | 120.0073 | 1.4211e-13 | -0.035216 | -0.00023069 | 0.059945 | -0.0098414 | 0.055696 | -0.22823 | -0.0041788 | 0.015772 | 0.020899 | 0.033756 | 0.0054267 | -1.1664 | 9.5982 | -1.5788 | 120.0746 | 119.8262 | 119.758 | -1.7985 | 0.005626 | -0.12327 | -0.083823 | -0.075739 | -0.050394 | -0.015142 | -0.20994 | 0.073783 | 0.067241 | 0.70581 | 0.29349 | 0.21971 | -0.18109 | -0.24937 | 1.6623 | -120.0831 | 1.8779 | 1.7884 | 0.12611 | -120.0577 | -120.0225 | 121.9468 | 121.6985 | 121.6302 | 11.4704 | -121.8058 | 1.7965 | 1.8219 | 1.8571 | 1.749 | -120.2173
1868.625 | 121.8658 | -1.7761 | 120.163 | 1.4211e-13 | -0.034788 | -0.00023069 | 0.059945 | -0.0098414 | 0.055482 | -0.23586 | -0.0043924 | 0.015772 | 0.021326 | 0.033756 | 0.0054267 | -1.0474 | 9.6256 | -1.4643 | 120.1982 | 119.9636 | 119.8862 | -1.6794 | 0.014784 | -0.12784 | -0.092981 | -0.066582 | -0.045815 | -0.010564 | -0.20536 | 0.096705 | 0.035218 | 0.72872 | 0.31182 | 0.21512 | -0.19936 | -0.27681 | 1.5708 | -120.2295 | 1.7909 | 1.6831 | 0.11238 | -120.2088 | -120.1735 | 121.9743 | 121.7397 | 121.6623 | 11.4018 | -121.8424 | 1.7095 | 1.7303 | 1.7656 | 1.6483 | -120.3683
1870.3594 | 121.8521 | -1.6479 | 120.2682 | 1.4211e-13 | -0.034788 | -0.00044449 | 0.059945 | -0.010055 | 0.055482 | -0.23586 | -0.004606 | 0.015558 | 0.021113 | 0.03397 | 0.0054267 | -0.99246 | 9.6119 | -1.4048 | 120.244 | 120.0002 | 119.9365 | -1.6336 | 0.005626 | -0.12784 | -0.088402 | -0.075739 | -0.059551 | -0.010564 | -0.20994 | 0.014321 | -0.024284 | 0.65549 | 0.24316 | 0.22884 | -0.26802 | -0.33173 | 1.438 | -120.344 | 1.6536 | 1.5595 | 0.12154 | -120.3278 | -120.2788 | 121.8919 | 121.6482 | 121.5845 | 11.2598 | -121.9019 | 1.5722 | 1.5884 | 1.6374 | 1.5201 | -120.4782
1872.0312 | 121.9803 | -1.8677 | 119.989 | 1.4211e-13 | -0.035002 | -1.7092e-05 | 0.059731 | -0.0098414 | 0.055482 | -0.22823 | -0.0041788 | 0.015772 | 0.021113 | 0.03397 | 0.0054267 | -1.0978 | 9.4654 | -1.5101 | 120.1387 | 119.8903 | 119.8266 | -1.7389 | 0.001048 | -0.11869 | -0.088402 | -0.062004 | -0.054973 | -0.005985 | -0.20994 | 0.12873 | 0.14965 | 0.76991 | 0.35759 | 0.22886 | -0.098674 | -0.16238 | 1.6577 | -120.051 | 1.8687 | 1.7793 | 0.12154 | -120.044 | -119.995 | 122.0063 | 121.758 | 121.6943 | 11.3331 | -121.728 | 1.8057 | 1.8127 | 1.8617 | 1.749 | -120.199
1873.7656 | 121.9345 | -1.8585 | 120.0256 | 1.4211e-13 | -0.034788 | -0.00023069 | 0.059731 | -0.0096276 | 0.055696 | -0.23586 | -0.0043924 | 0.015772 | 0.02154 | 0.033756 | 0.0054267 | -1.1481 | 9.4059 | -1.5696 | 120.0746 | 119.8308 | 119.7671 | -1.7939 | 0.001048 | -0.12784 | -0.088402 | -0.066582 | -0.050394 | -0.010564 | -0.21452 | 0.06463 | 0.04893 | 0.71039 | 0.28892 | 0.22429 | -0.19482 | -0.25852 | 1.644 | -120.0922 | 1.8596 | 1.7701 | 0.12611 | -120.076 | -120.0362 | 121.9331 | 121.6893 | 121.6256 | 11.2644 | -121.8195 | 1.7919 | 1.8081 | 1.848 | 1.7307 | -120.2402
1875.5 | 121.9437 | -1.886 | 119.9661 | 1.4211e-13 | -0.035002 | -0.00023069 | 0.059945 | -0.0098414 | 0.055696 | -0.2206 | -0.0043924 | 0.015558 | 0.020899 | 0.033756 | 0.0056405 | -1.1802 | 9.3326 | -1.5971 | 120.0334 | 119.7896 | 119.7305 | -1.8351 | 0.001048 | -0.031692 | -0.092981 | -0.062004 | -0.054973 | -0.015142 | -0.20994 | 0.050885 | 0.067235 | 0.70581 | 0.28891 | 0.23803 | -0.17652 | -0.23564 | 1.676 | -120.0281 | 1.887 | 1.793 | 0.11696 | -120.0211 | -119.9813 | 121.9193 | 121.6756 | 121.6165 | 11.2186 | -121.8012 | 1.824 | 1.831 | 1.8708 | 1.8543 | -120.1761
1877.1719 | 121.9986 | -1.8082 | 119.9982 | 1.4211e-13 | -0.035002 | -0.00023069 | 0.059731 | -0.010055 | 0.055268 | -0.22823 | -0.003965 | 0.015986 | 0.020685 | 0.033756 | 0.0052131 | -1.1161 | 9.3005 | -1.5421 | 120.0975 | 119.8537 | 119.7854 | -1.7802 | 0.005626 | -0.036271 | -0.083823 | -0.071161 | -0.059551 | -0.015142 | -0.20536 | 0.028013 | 0.099288 | 0.69209 | 0.26603 | 0.23802 | -0.14446 | -0.21274 | 1.6028 | -120.0693 | 1.8138 | 1.7243 | 0.12154 | -120.0577 | -120.0133 | 121.9056 | 121.6619 | 121.5936 | 11.1087 | -121.7783 | 1.737 | 1.7486 | 1.793 | 1.7719 | -120.2035
1878.9219 | 121.9894 | -1.8448 | 120.0119 | 1.4211e-13 | -0.035002 | -0.00023069 | 0.059731 | -0.010055 | 0.055696 | -0.22823 | -0.003965 | 0.015986 | 0.021113 | 0.03397 | 0.0049995 | -1.0657 | 9.3005 | -1.5055 | 120.1249 | 119.8903 | 119.8266 | -1.7435 | 0.005626 | -0.031692 | -0.088402 | -0.071161 | -0.054973 | -0.010564 | -0.20994 | 0.10127 | 0.11303 | 0.77907 | 0.33928 | 0.23802 | -0.12156 | -0.18527 | 1.6349 | -120.0831 | 1.8504 | 1.7564 | 0.12154 | -120.0669 | -120.0225 | 121.9697 | 121.7351 | 121.6714 | 11.1453 | -121.7554 | 1.7736 | 1.7898 | 1.8342 | 1.8131 | -120.2218
1880.5938 | 121.8384 | -1.9272 | 119.9936 | 1.4211e-13 | -0.035216 | -0.00023069 | 0.059945 | -0.010055 | 0.055696 | -0.22823 | -0.0041788 | 0.015772 | 0.021113 | 0.033542 | 0.0052131 | -1.139 | 9.1815 | -1.5742 | 120.0563 | 119.8171 | 119.7488 | -1.8259 | 0.005626 | -0.031692 | -0.088402 | -0.066582 | -0.041237 | -0.015142 | -0.20994 | 0.10124 | 0.062661 | 0.78821 | 0.353 | 0.25176 | -0.17651 | -0.24479 | 1.7172 | -120.0602 | 1.9328 | 1.8388 | 0.12154 | -120.0348 | -120.0087 | 121.9834 | 121.7443 | 121.676 | 11.1087 | -121.8195 | 1.8606 | 1.8859 | 1.912 | 1.8955 | -120.2035
1882.3281 | 121.907 | -1.7899 | 120.1309 | 1.4211e-13 | -0.035429 | -0.00044449 | 0.059731 | -0.010055 | 0.055482 | -0.23586 | -0.003965 | 0.015772 | 0.021113 | 0.033542 | 0.0052131 | -1.0199 | 9.1952 | -1.4643 | 120.1707 | 119.9316 | 119.8633 | -1.7115 | 0.005626 | -0.031692 | -0.083823 | -0.071161 | -0.045815 | -0.010564 | -0.20536 | 0.078386 | 0.039792 | 0.76992 | 0.32555 | 0.24717 | -0.19937 | -0.26766 | 1.5845 | -120.2021 | 1.7955 | 1.706 | 0.12154 | -120.1767 | -120.1415 | 121.9606 | 121.7214 | 121.6531 | 10.9851 | -121.8424 | 1.7187 | 1.744 | 1.7793 | 1.7582 | -120.3363
1884.0625 | 121.8338 | -1.8585 | 120.0851 | 1.4211e-13 | -0.035216 | -1.7092e-05 | 0.060158 | -0.010055 | 0.055482 | -0.2206 | -0.0043924 | 0.015558 | 0.021326 | 0.03397 | 0.0047859 | -1.0337 | 9.154 | -1.4918 | 120.1478 | 119.9087 | 119.8312 | -1.7298 | 0.001048 | -0.031692 | -0.083823 | -0.071161 | -0.050394 | -0.019721 | -0.2191 | 0.12874 | 0.062676 | 0.82485 | 0.36675 | 0.23801 | -0.17649 | -0.25393 | 1.6394 | -120.1563 | 1.8596 | 1.7747 | 0.13527 | -120.1355 | -120.1049 | 122.0063 | 121.7672 | 121.6897 | 11.0126 | -121.8149 | 1.7874 | 1.8081 | 1.8388 | 1.8268 | -120.3042
1885.8125 | 121.9894 | -1.7395 | 120.1218 | 1.4211e-13 | -0.035002 | -0.00044449 | 0.059945 | -0.010055 | 0.055696 | -0.22823 | -0.0043924 | 0.015558 | 0.020899 | 0.034397 | 0.0047859 | -1.0199 | 9.0991 | -1.4689 | 120.1478 | 119.9178 | 119.8495 | -1.7252 | 0.005626 | -0.031692 | -0.088402 | -0.071161 | -0.054973 | -0.005985 | -0.20994 | 0.014295 | 0.026055 | 0.71957 | 0.27062 | 0.25633 | -0.20395 | -0.27224 | 1.5296 | -120.1929 | 1.7451 | 1.6511 | 0.12154 | -120.1767 | -120.1277 | 121.8873 | 121.6573 | 121.589 | 10.8386 | -121.847 | 1.6683 | 1.6845 | 1.7335 | 1.7078 | -120.3317
1887.5625 | 121.9666 | -1.799 | 120.0668 | 1.4211e-13 | -0.035002 | -0.00023069 | 0.059731 | -0.0096276 | 0.055268 | -0.2206 | -0.0041788 | 0.015772 | 0.021113 | 0.034183 | 0.0047859 | -1.0062 | 9.0579 | -1.4597 | 120.1616 | 119.9316 | 119.8633 | -1.7023 | 0.005626 | -0.031692 | -0.088402 | -0.066582 | -0.054973 | -0.010564 | -0.20994 | 0.096699 | 0.094722 | 0.79281 | 0.33929 | 0.24259 | -0.13528 | -0.20357 | 1.5891 | -120.1334 | 1.8046 | 1.7106 | 0.12154 | -120.1218 | -120.0774 | 121.9606 | 121.7306 | 121.6623 | 10.8569 | -121.7691 | 1.7324 | 1.744 | 1.7884 | 1.7673 | -120.2768
1889.25 | 121.9757 | -1.7029 | 120.0989 | 1.4211e-13 | -0.035216 | -0.00023069 | 0.059945 | -0.010269 | 0.055482 | -0.23586 | -0.003965 | 0.015772 | 0.020899 | 0.03397 | 0.0054267 | -0.92836 | 9.0487 | -1.391 | 120.2302 | 119.9957 | 119.9274 | -1.6428 | 0.001048 | -0.036271 | -0.088402 | -0.071161 | -0.050394 | -0.005985 | -0.20994 | 0.060095 | 0.13135 | 0.77452 | 0.31183 | 0.25174 | -0.10322 | -0.17151 | 1.4929 | -120.17 | 1.7039 | 1.6145 | 0.12154 | -120.1493 | -120.1049 | 121.9331 | 121.6985 | 121.6302 | 10.7516 | -121.7417 | 1.6317 | 1.6525 | 1.6969 | 1.6666 | -120.3088
1890.9844 | 121.9849 | -1.5289 | 120.2866 | 1.4211e-13 | -0.035216 | -0.00023069 | 0.059731 | -0.010055 | 0.055482 | -0.21297 | -0.0041788 | 0.015772 | 0.020899 | 0.034611 | 0.0054267 | -0.79559 | 9.0579 | -1.2629 | 120.3538 | 120.1239 | 120.0556 | -1.5192 | 0.001048 | -0.031692 | -0.088402 | -0.071161 | -0.054973 | -0.010564 | -0.20994 | 0.009776 | 0.067287 | 0.73334 | 0.26607 | 0.2563 | -0.16269 | -0.23099 | 1.319 | -120.3577 | 1.53 | 1.4405 | 0.12154 | -120.3415 | -120.2971 | 121.8828 | 121.6528 | 121.5845 | 10.5868 | -121.8057 | 1.4578 | 1.474 | 1.5184 | 1.4972 | -120.4965
1892.7344 | 121.9025 | -1.5152 | 120.3644 | 1.4211e-13 | -0.035216 | -0.00044449 | 0.059731 | -0.0098414 | 0.055482 | -0.23586 | -0.004606 | 0.015772 | 0.021113 | 0.034183 | 0.0047859 | -0.74981 | 9.0258 | -1.2217 | 120.3996 | 120.1651 | 120.0922 | -1.4779 | 0.001048 | -0.036271 | -0.088402 | -0.062004 | -0.054973 | -0.015142 | -0.2191 | 0.037253 | 0.035251 | 0.76539 | 0.29354 | 0.25629 | -0.1993 | -0.27218 | 1.2961 | -120.4264 | 1.5162 | 1.4268 | 0.13069 | -120.4194 | -120.3795 | 121.9148 | 121.6803 | 121.6074 | 10.541 | -121.8423 | 1.4532 | 1.4602 | 1.5001 | 1.4789 | -120.5835
1894.4219 | 121.8979 | -1.3962 | 120.488 | 1.4211e-13 | -0.035216 | -1.7092e-05 | 0.059945 | -0.010055 | 0.055482 | -0.23586 | -0.0041788 | 0.015986 | 0.020899 | 0.03397 | 0.0045721 | -0.62619 | 9.0396 | -1.098 | 120.5095 | 120.2704 | 120.2112 | -1.3635 | 0.010205 | -0.031692 | -0.10672 | -0.062004 | -0.054973 | -0.015142 | -0.2191 | 0.032707 | 0.021536 | 0.76999 | 0.29814 | 0.26543 | -0.21758 | -0.27674 | 1.1771 | -120.55 | 1.4064 | 1.2895 | 0.11238 | -120.5429 | -120.5031 | 121.9057 | 121.6666 | 121.6074 | 10.4357 | -121.8514 | 1.3342 | 1.3412 | 1.381 | 1.3645 | -120.7071
1896.1719 | 121.9391 | -1.474 | 120.4056 | 1.4211e-13 | -0.035216 | -1.7092e-05 | 0.059945 | -0.010269 | 0.055268 | -0.2206 | -0.0043924 | 0.015345 | 0.020899 | 0.034397 | 0.0047859 | -0.63993 | 8.9755 | -1.1164 | 120.4958 | 120.2521 | 120.1838 | -1.3818 | 0.005626 | -0.027113 | -0.14793 | -0.066582 | -0.045815 | -0.0243 | -0.21452 | 0.092211 | 0.090198 | 0.83407 | 0.35765 | 0.26544 | -0.1535 | -0.22181 | 1.2595 | -120.4722 | 1.4796 | 1.3261 | 0.066591 | -120.4514 | -120.4299 | 121.9698 | 121.7261 | 121.6578 | 10.4495 | -121.7874 | 1.4074 | 1.4282 | 1.4497 | 1.4469 | -120.6201
1897.9062 | 121.9666 | -1.4191 | 120.4697 | 1.4211e-13 | -0.035216 | -1.7092e-05 | 0.059945 | -0.0096276 | 0.055268 | -0.22823 | -0.0043924 | 0.015345 | 0.021326 | 0.033756 | 0.0052131 | -0.63993 | 8.9159 | -1.1255 | 120.4866 | 120.2475 | 120.1883 | -1.3909 | 0.001048 | -0.027113 | -0.1525 | -0.071161 | -0.050394 | -0.005985 | -0.23283 | 0.028122 | 0.016954 | 0.77914 | 0.29356 | 0.26544 | -0.22217 | -0.28132 | 1.1862 | -120.5408 | 1.4201 | 1.2666 | 0.080327 | -120.5201 | -120.4757 | 121.9057 | 121.6666 | 121.6074 | 10.335 | -121.8606 | 1.3479 | 1.3687 | 1.4131 | 1.392 | -120.7025
1899.6094 | 121.9849 | -1.4511 | 120.3873 | 1.4211e-13 | -0.035429 | -1.7092e-05 | 0.059731 | -0.0096276 | 0.055268 | -0.24349 | -0.0043924 | 0.015772 | 0.021326 | 0.034183 | 0.0049995 | -0.63993 | 8.8793 | -1.1301 | 120.4729 | 120.2338 | 120.17 | -1.4047 | 0.010205 | -0.031692 | -0.1525 | -0.066582 | -0.054973 | -0.015142 | -0.22825 | 0.046429 | 0.085617 | 0.81118 | 0.32102 | 0.27459 | -0.15351 | -0.21724 | 1.2229 | -120.4539 | 1.4613 | 1.2986 | 0.075748 | -120.4422 | -120.4024 | 121.924 | 121.6849 | 121.6211 | 10.3304 | -121.7919 | 1.3845 | 1.3961 | 1.436 | 1.4194 | -120.6155
1901.3594 | 121.9254 | -1.4236 | 120.4605 | 1.4211e-13 | -0.035429 | -1.7092e-05 | 0.059731 | -0.010269 | 0.055268 | -0.23586 | -0.0041788 | 0.015345 | 0.021326 | 0.03397 | 0.0047859 | -0.63077 | 8.8198 | -1.1164 | 120.482 | 120.2429 | 120.1746 | -1.3909 | 0.005626 | -0.027113 | -0.14793 | -0.071161 | -0.054973 | -0.005985 | -0.23283 | 0.0327 | 0.021532 | 0.79287 | 0.30729 | 0.27459 | -0.21759 | -0.2859 | 1.1908 | -120.5317 | 1.4293 | 1.2757 | 0.084906 | -120.5155 | -120.4665 | 121.9057 | 121.6666 | 121.5983 | 10.2434 | -121.8515 | 1.3525 | 1.3687 | 1.4177 | 1.3965 | -120.6933
1903.0469 | 121.8933 | -1.5289 | 120.3918 | 1.4211e-13 | -0.035429 | -1.7092e-05 | 0.059945 | -0.010055 | 0.055055 | -0.23586 | -0.0043924 | 0.015772 | 0.020685 | 0.034183 | 0.0049995 | -0.65366 | 8.7328 | -1.153 | 120.4454 | 120.2017 | 120.138 | -1.4276 | 0.010205 | -0.031692 | -0.14793 | -0.066582 | -0.050394 | -0.015142 | -0.22367 | 0.10135 | 0.053569 | 0.87527 | 0.37595 | 0.2746 | -0.19014 | -0.25387 | 1.3053 | -120.4584 | 1.5391 | 1.381 | 0.075748 | -120.4422 | -120.407 | 121.9743 | 121.7306 | 121.6669 | 10.2617 | -121.8194 | 1.4623 | 1.4785 | 1.5138 | 1.4972 | -120.6155
1904.7812 | 121.8292 | -1.4694 | 120.4559 | 1.4211e-13 | -0.035216 | -0.00023069 | 0.059731 | -0.0098414 | 0.055482 | -0.23586 | -0.0041788 | 0.015772 | 0.020685 | 0.034611 | 0.0049995 | -0.59414 | 8.742 | -1.0935 | 120.4958 | 120.2704 | 120.2021 | -1.3726 | 0.001048 | -0.031692 | -0.1525 | -0.075739 | -0.050394 | -0.010564 | -0.23283 | 0.096791 | 0.039844 | 0.87528 | 0.37596 | 0.27917 | -0.18554 | -0.25385 | 1.2366 | -120.5317 | 1.4705 | 1.3169 | 0.080327 | -120.5063 | -120.4665 | 121.9652 | 121.7398 | 121.6715 | 10.2114 | -121.8286 | 1.3937 | 1.419 | 1.4589 | 1.4377 | -120.6888
1906.4531 | 121.9711 | -1.4145 | 120.4559 | 1.4211e-13 | -0.035216 | -1.7092e-05 | 0.059945 | -0.0098414 | 0.055482 | -0.2206 | -0.0041788 | 0.015772 | 0.020472 | 0.034183 | 0.0049995 | -0.56667 | 8.7008 | -1.0706 | 120.5232 | 120.2887 | 120.2204 | -1.3589 | 0.010205 | -0.022535 | -0.16166 | -0.071161 | -0.045815 | -0.010564 | -0.22825 | 0.055597 | 0.067314 | 0.84782 | 0.34392 | 0.28832 | -0.16723 | -0.23554 | 1.1862 | -120.5271 | 1.4247 | 1.2528 | 0.066591 | -120.5017 | -120.4665 | 121.9377 | 121.7032 | 121.6349 | 10.1152 | -121.8148 | 1.3433 | 1.3687 | 1.4039 | 1.392 | -120.6842
1908.1875 | 121.9528 | -1.3412 | 120.5292 | 1.4211e-13 | -0.035429 | -0.00023069 | 0.059731 | -0.010055 | 0.055055 | -0.22823 | -0.0041788 | 0.015986 | 0.021326 | 0.03397 | 0.0047859 | -0.49342 | 8.6687 | -1.0065 | 120.5828 | 120.3482 | 120.2799 | -1.2856 | 0.010205 | -0.027113 | -0.14793 | -0.066582 | -0.045815 | -0.010564 | -0.22367 | 0.055618 | 0.053592 | 0.84783 | 0.33477 | 0.27916 | -0.18094 | -0.24926 | 1.1176 | -120.5958 | 1.3515 | 1.1933 | 0.075748 | -120.575 | -120.5397 | 121.924 | 121.6895 | 121.6212 | 10.0099 | -121.8148 | 1.2747 | 1.2954 | 1.3307 | 1.3141 | -120.7528
1909.9219 | 121.9666 | -1.2772 | 120.5475 | 1.4211e-13 | -0.035429 | 0.00019651 | 0.060158 | -0.010055 | 0.055482 | -0.24349 | -0.0041788 | 0.015558 | 0.021113 | 0.03397 | 0.0049995 | -0.45679 | 8.6595 | -0.96527 | 120.6194 | 120.3849 | 120.3211 | -1.2536 | 0.005626 | -0.031692 | -0.15708 | -0.066582 | -0.050394 | -0.010564 | -0.23283 | 0.023583 | 0.071909 | 0.82037 | 0.31189 | 0.28831 | -0.16262 | -0.22636 | 1.0443 | -120.6141 | 1.2828 | 1.1201 | 0.075748 | -120.5979 | -120.558 | 121.8966 | 121.662 | 121.5983 | 9.9367 | -121.8011 | 1.2106 | 1.2268 | 1.2666 | 1.2455 | -120.7803
1911.5938 | 121.9849 | -1.3092 | 120.5841 | 1.4211e-13 | -0.035429 | 0.00019651 | 0.060158 | -0.0096276 | 0.055482 | -0.22823 | -0.0043924 | 0.015345 | 0.020685 | 0.034611 | 0.0049995 | -0.42474 | 8.6183 | -0.9378 | 120.6423 | 120.4078 | 120.344 | -1.2307 | 0.001048 | -0.11869 | -0.16166 | -0.066582 | -0.054973 | -0.015142 | -0.23283 | 0.078521 | 0.05818 | 0.88446 | 0.3714 | 0.29288 | -0.17635 | -0.24009 | 1.0764 | -120.6507 | 1.3103 | 1.1475 | 0.07117 | -120.6391 | -120.5992 | 121.9515 | 121.717 | 121.6532 | 9.9275 | -121.8148 | 1.2426 | 1.2542 | 1.2941 | 1.1905 | -120.8169
1913.3281 | 121.8521 | -1.3367 | 120.5841 | 1.4211e-13 | -0.035429 | -1.7092e-05 | 0.059731 | -0.0096276 | 0.055055 | -0.23586 | -0.0043924 | 0.015558 | 0.020685 | 0.034183 | 0.0052131 | -0.42932 | 8.5542 | -0.94238 | 120.6377 | 120.4032 | 120.3394 | -1.2398 | 0.005626 | -0.11411 | -0.1525 | -0.071161 | -0.050394 | -0.010564 | -0.23741 | 0.096829 | 0.053601 | 0.90735 | 0.39429 | 0.29746 | -0.18093 | -0.24467 | 1.0993 | -120.6553 | 1.3423 | 1.1842 | 0.084906 | -120.6345 | -120.5947 | 121.9744 | 121.7399 | 121.6761 | 9.8909 | -121.8239 | 1.2655 | 1.2863 | 1.3261 | 1.2226 | -120.8215
1915.0625 | 121.9299 | -1.268 | 120.6162 | 1.4211e-13 | -0.035643 | -1.7092e-05 | 0.059731 | -0.010055 | 0.055055 | -0.24349 | -0.0041788 | 0.015558 | 0.020685 | 0.034397 | 0.0047859 | -0.41101 | 8.5039 | -0.92864 | 120.6469 | 120.4215 | 120.3486 | -1.2261 | 0.001048 | -0.11869 | -0.1525 | -0.066582 | -0.050394 | -0.010564 | -0.22825 | 0.041901 | 0.030714 | 0.857 | 0.33936 | 0.29746 | -0.19466 | -0.26755 | 1.0398 | -120.6827 | 1.2691 | 1.1155 | 0.075748 | -120.6665 | -120.6267 | 121.9149 | 121.6895 | 121.6166 | 9.7719 | -121.8423 | 1.2014 | 1.2176 | 1.2574 | 1.1493 | -120.8444
1916.7969 | 121.9803 | -1.2634 | 120.5612 | 1.4211e-13 | -0.035857 | 0.00019651 | 0.059945 | -0.0096276 | 0.055482 | -0.22823 | -0.0043924 | 0.015772 | 0.020044 | 0.03397 | 0.0047859 | -0.40185 | 8.4535 | -0.92407 | 120.6469 | 120.4123 | 120.3486 | -1.2307 | 0.005626 | -0.12327 | -0.1525 | -0.066582 | -0.045815 | -0.010564 | -0.23283 | 0.032745 | 0.085646 | 0.86158 | 0.33936 | 0.30662 | -0.14888 | -0.21262 | 1.0306 | -120.6278 | 1.2691 | 1.1109 | 0.080327 | -120.607 | -120.5718 | 121.9103 | 121.6758 | 121.612 | 9.7169 | -121.7919 | 1.1968 | 1.2176 | 1.2529 | 1.1402 | -120.794
1918.4844 | 121.8704 | -2.2659 | 119.5862 | 1.4211e-13 | -0.035429 | -0.00044449 | 0.059303 | -0.0098414 | 0.055268 | -0.22823 | -0.0041788 | 0.015772 | 0.020899 | 0.034397 | 0.0052131 | -3.4556 | 6.5488 | -4.0327 | 117.4695 | 117.2666 | 117.1848 | -4.3306 | 0.019362 | -0.12327 | -0.14793 | -0.066582 | -0.045815 | -0.005985 | -0.22825 | -2.0647 | -2.1167 | -1.1897 | -1.7668 | 0.2979 | -2.3196 | -2.4014 | 2.0377 | -119.6528 | 2.2853 | 2.118 | 0.080327 | -119.632 | -119.5922 | 119.7354 | 119.5325 | 119.4507 | 8.8147 | -123.9168 | 2.1993 | 2.2201 | 2.2599 | 2.1427 | -119.8144
1920.2344 | 119.7235 | -72.5052 | 46.8842 | 1.4211e-13 | -0.036284 | -0.0010855 | 0.057808 | -0.010055 | 0.054627 | -0.24349 | -0.003965 | 0.015772 | 0.020899 | 0.034611 | 0.0054267 | -54.1201 | -23.5372 | -54.3251 | 65.2209 | 64.7189 | 65.3596 | -55.5459 | 0.060571 | -0.0729 | -0.1113 | -0.016219 | -0.009187 | 0.030644 | -0.17331 | 16.9593 | 18.3367 | 18.3851 | 18.1801 | 1.2208 | 17.8347 | 18.4754 | 72.3319 | -46.9004 | 72.5658 | 72.3939 | 0.06201 | -46.8933 | -46.8535 | 137.7261 | 137.2241 | 137.8648 | 48.968 | -102.43 | 72.489 | 72.496 | 72.5358 | 72.4323 | -47.0575
1921.9844 | 121.5546 | -0.37994 | 121.257 | 1.4211e-13 | -0.035429 | -1.7092e-05 | 0.059731 | -0.0098414 | 0.055055 | -0.22823 | -0.0043924 | 0.015772 | 0.020258 | 0.034397 | 0.0049995 | 0.55045 | 8.7969 | -0.012988 | 121.2924 | 121.0625 | 120.9896 | -0.30574 | 0.010205 | -0.10953 | -0.14793 | -0.066582 | -0.045815 | -0.010564 | -0.22367 | 0.074204 | 0.035398 | 0.9304 | 0.36696 | 0.29275 | -0.19447 | -0.26742 | 0.15627 | -121.3236 | 0.39015 | 0.23202 | 0.075748 | -121.3028 | -121.2676 | 121.6724 | 121.4425 | 121.3695 | 9.1768 | -121.5628 | 0.31336 | 0.33413 | 0.36938 | 0.27041 | -121.4807
1923.7344 | 121.6644 | -0.33875 | 121.3303 | 1.4211e-13 | -0.035857 | -0.00023069 | 0.059731 | -0.010482 | 0.055268 | -0.22823 | -0.004606 | 0.015772 | 0.020685 | 0.034397 | 0.0049995 | 0.57335 | 8.8015 | 0.000747 | 121.3702 | 121.145 | 121.0674 | -0.28742 | 0.010205 | -0.10953 | -0.14793 | -0.066582 | -0.045815 | -0.010564 | -0.22367 | 0.05132 | 0.039988 | 0.91209 | 0.33949 | 0.28817 | -0.18529 | -0.26282 | 0.11507 | -121.3968 | 0.34895 | 0.19082 | 0.075748 | -121.3761 | -121.3408 | 121.709 | 121.4837 | 121.4062 | 9.1402 | -121.6177 | 0.27216 | 0.29293 | 0.32818 | 0.22922 | -121.5539
1925.4062 | 121.6187 | -0.35706 | 121.4035 | 1.4211e-13 | -0.035643 | -0.00023069 | 0.060158 | -0.010269 | 0.055268 | -0.23586 | -0.0043924 | 0.015558 | 0.020685 | 0.034397 | 0.0047859 | 0.59166 | 8.7694 | 0.023639 | 121.416 | 121.1816 | 121.1132 | -0.28285 | 0.001048 | -0.10495 | -0.1525 | -0.066582 | -0.041237 | -0.015142 | -0.22825 | 0.07421 | 0.01253 | 0.94872 | 0.3807 | 0.30649 | -0.22191 | -0.29028 | 0.1288 | -121.4701 | 0.3581 | 0.20455 | 0.075748 | -121.4447 | -121.4186 | 121.7731 | 121.5387 | 121.4703 | 9.1265 | -121.6863 | 0.29047 | 0.31582 | 0.34191 | 0.2521 | -121.6318
1927.1406 | 121.7377 | -0.29755 | 121.3806 | 1.4211e-13 | -0.035429 | 0.00019651 | 0.059945 | -0.010055 | 0.055268 | -0.22823 | -0.0043924 | 0.015345 | 0.020899 | 0.034397 | 0.0047859 | 0.61455 | 8.742 | 0.032795 | 121.4481 | 121.2228 | 121.1636 | -0.26453 | 0.005626 | -0.10495 | -0.14793 | -0.071161 | -0.045815 | -0.010564 | -0.22367 | 0.033016 | 0.067467 | 0.9121 | 0.33034 | 0.29733 | -0.15781 | -0.21703 | 0.073873 | -121.4518 | 0.30317 | 0.14962 | 0.075748 | -121.4264 | -121.3912 | 121.7456 | 121.5204 | 121.4611 | 9.0395 | -121.6451 | 0.22638 | 0.25173 | 0.28698 | 0.19259 | -121.6043
1928.8906 | 121.701 | -0.32044 | 121.4584 | 1.4211e-13 | -0.035429 | -1.7092e-05 | 0.060158 | -0.010055 | 0.055268 | -0.22823 | -0.0041788 | 0.015345 | 0.020685 | 0.034397 | 0.0047859 | 0.62371 | 8.6641 | 0.032795 | 121.4801 | 121.2365 | 121.1682 | -0.26911 | 0.005626 | -0.10037 | -0.14335 | -0.066582 | -0.050394 | -0.001407 | -0.22367 | 0.051326 | 0.021696 | 0.94414 | 0.35323 | 0.3019 | -0.22189 | -0.29027 | 0.096762 | -121.525 | 0.32606 | 0.17709 | 0.080326 | -121.5088 | -121.4598 | 121.8006 | 121.557 | 121.4886 | 8.9846 | -121.7275 | 0.25385 | 0.27004 | 0.31903 | 0.22006 | -121.6821
1930.5625 | 121.788 | -0.27466 | 121.4081 | 1.4211e-13 | -0.035857 | -1.7092e-05 | 0.060158 | -0.0096276 | 0.055696 | -0.22823 | -0.0041788 | 0.015558 | 0.021113 | 0.034397 | 0.0047859 | 0.63744 | 8.6229 | 0.04653 | 121.4939 | 121.264 | 121.1911 | -0.26453 | 0.005626 | -0.10037 | -0.14335 | -0.075739 | -0.041237 | -0.005985 | -0.22367 | 0.010128 | 0.085785 | 0.9121 | 0.32119 | 0.31106 | -0.14406 | -0.21702 | 0.050985 | -121.4838 | 0.28028 | 0.13131 | 0.080326 | -121.4493 | -121.4141 | 121.7685 | 121.5387 | 121.4657 | 8.8976 | -121.6726 | 0.19892 | 0.23342 | 0.26867 | 0.17429 | -121.6318
1932.2969 | 121.8201 | -0.28839 | 121.4447 | 1.4211e-13 | -0.035857 | 0.00019651 | 0.060158 | -0.010269 | 0.054841 | -0.22823 | -0.0041788 | 0.015772 | 0.020899 | 0.034611 | 0.0045721 | 0.64202 | 8.5817 | 0.051108 | 121.4939 | 121.2732 | 121.2048 | -0.25995 | -0.003531 | -0.095794 | -0.14335 | -0.066582 | -0.054973 | -0.001407 | -0.2191 | 0.02844 | 0.049164 | 0.93041 | 0.3395 | 0.31106 | -0.17153 | -0.23991 | 0.069296 | -121.5113 | 0.28486 | 0.14504 | 0.075748 | -121.4997 | -121.4461 | 121.7823 | 121.5616 | 121.4932 | 8.8701 | -121.7047 | 0.22181 | 0.23342 | 0.28698 | 0.1926 | -121.6638
1933.9844 | 121.138 | -0.23346 | 120.9457 | 1.4211e-13 | -0.035643 | 0.00019651 | 0.059517 | -0.010055 | 0.054627 | -0.2206 | -0.0043924 | 0.015558 | 0.020685 | 0.034397 | 0.0047859 | 0.23912 | 8.1284 | -0.37009 | 120.2577 | 120.0643 | 119.9411 | -0.69037 | 0.014784 | -0.10495 | -0.13877 | -0.062004 | -0.050394 | -0.010564 | -0.22367 | -0.45691 | -0.68804 | 0.47258 | -0.13663 | 0.32028 | -0.8814 | -1.0046 | 0.009786 | -121.0077 | 0.24824 | 0.094691 | 0.084905 | -120.9961 | -120.9563 | 120.4912 | 120.2978 | 120.1746 | 8.3619 | -121.6361 | 0.17145 | 0.18307 | 0.2229 | 0.12851 | -121.1694
1935.75 | 121.4676 | -0.20142 | 121.17 | 1.4211e-13 | -0.035643 | -1.7092e-05 | 0.060372 | -0.010055 | 0.055055 | -0.22823 | -0.0041788 | 0.015772 | 0.020685 | 0.034611 | 0.0047859 | 0.77022 | 8.5268 | 0.15641 | 121.2512 | 121.0168 | 120.953 | -0.17295 | 0.010205 | -0.086637 | -0.12961 | -0.066582 | -0.041237 | -0.010564 | -0.21452 | 0.028465 | 0.081167 | 0.97163 | 0.35783 | 0.32936 | -0.15329 | -0.21707 | -0.0131 | -121.2366 | 0.21162 | 0.071806 | 0.084906 | -121.2113 | -121.1806 | 121.4526 | 121.2182 | 121.1544 | 8.7282 | -121.343 | 0.13483 | 0.16018 | 0.19085 | 0.11478 | -121.3846
1937.4375 | 121.4813 | -0.21973 | 121.2524 | 1.4211e-13 | -0.035643 | 0.00041031 | 0.060372 | -0.0098414 | 0.055268 | -0.23586 | -0.004606 | 0.015558 | 0.020685 | 0.034824 | 0.0045721 | 0.7748 | 8.4947 | 0.15641 | 121.3107 | 121.0854 | 121.0171 | -0.16379 | 0.014784 | -0.086637 | -0.12503 | -0.066582 | -0.050394 | -0.005985 | -0.20994 | 0.055933 | 0.058289 | 0.99452 | 0.37614 | 0.3202 | -0.167 | -0.23537 | 0.00979 | -121.319 | 0.23451 | 0.094695 | 0.084905 | -121.3028 | -121.2584 | 121.5305 | 121.3052 | 121.2368 | 8.7144 | -121.4162 | 0.15315 | 0.16933 | 0.21374 | 0.13309 | -121.4624
1939.1875 | 121.4584 | -0.21515 | 121.312 | 1.4211e-13 | -0.035216 | 0.00019651 | 0.060372 | -0.010055 | 0.055482 | -0.23586 | -0.0041788 | 0.015772 | 0.020472 | 0.034397 | 0.0045721 | 0.79311 | 8.4535 | 0.16556 | 121.3565 | 121.1221 | 121.0537 | -0.16837 | 0.005626 | -0.095794 | -0.12961 | -0.071161 | -0.041237 | -0.010564 | -0.20994 | 0.046776 | 0.044563 | 1.0083 | 0.38071 | 0.33394 | -0.18988 | -0.25825 | 0.005212 | -121.3831 | 0.22077 | 0.085539 | 0.080327 | -121.3532 | -121.3225 | 121.5717 | 121.3372 | 121.2689 | 8.6687 | -121.4803 | 0.14399 | 0.17391 | 0.20459 | 0.11936 | -121.5219
1940.9375 | 121.6141 | -0.18768 | 121.3074 | 1.4211e-13 | -0.035643 | 0.00019651 | 0.059945 | -0.010482 | 0.055268 | -0.22823 | -0.004606 | 0.015986 | 0.020472 | 0.034824 | 0.0045721 | 0.81142 | 8.4077 | 0.17014 | 121.3748 | 121.145 | 121.0858 | -0.18211 | 0.001048 | -0.091215 | -0.12961 | -0.066582 | -0.045815 | -0.005985 | -0.21452 | 0.005574 | 0.067455 | 0.9991 | 0.35783 | 0.35225 | -0.16241 | -0.22162 | -0.026833 | -121.374 | 0.18873 | 0.058073 | 0.084906 | -121.3532 | -121.3134 | 121.5625 | 121.3326 | 121.2734 | 8.5954 | -121.4895 | 0.1211 | 0.14187 | 0.1817 | 0.096468 | -121.5219
1942.6094 | 121.5454 | -0.23804 | 121.3623 | 1.4211e-13 | -0.035643 | -1.7092e-05 | 0.060158 | -0.010269 | 0.055055 | -0.23586 | -0.0041788 | 0.015986 | 0.020685 | 0.034824 | 0.0047859 | 0.81142 | 8.3711 | 0.17014 | 121.3977 | 121.1724 | 121.1041 | -0.17295 | 0.014784 | -0.082058 | -0.12503 | -0.062004 | -0.050394 | -0.005985 | -0.21452 | 0.065086 | 0.035415 | 1.0495 | 0.40818 | 0.34309 | -0.18987 | -0.25824 | 0.023521 | -121.4243 | 0.25282 | 0.113 | 0.089484 | -121.4127 | -121.3683 | 121.6358 | 121.4105 | 121.3421 | 8.6091 | -121.5353 | 0.17603 | 0.18764 | 0.23205 | 0.15598 | -121.5768
1944.3594 | 121.6324 | -0.19226 | 121.3165 | 1.4211e-13 | -0.035429 | 0.00019651 | 0.060372 | -0.010269 | 0.055268 | -0.24349 | -0.003965 | 0.015558 | 0.020472 | 0.034824 | 0.0045721 | 0.82058 | 8.307 | 0.1793 | 121.4252 | 121.1953 | 121.1224 | -0.17295 | 0.005626 | -0.082058 | -0.12045 | -0.066582 | -0.045815 | -0.010564 | -0.21452 | 0.01931 | 0.10866 | 1.0128 | 0.37156 | 0.35225 | -0.12119 | -0.19415 | -0.022255 | -121.3831 | 0.19789 | 0.071808 | 0.094063 | -121.3623 | -121.3271 | 121.6175 | 121.3876 | 121.3146 | 8.4993 | -121.4895 | 0.12568 | 0.14645 | 0.1817 | 0.1102 | -121.531
1946.0938 | 121.55 | -0.24261 | 121.3898 | 1.4211e-13 | -0.035643 | -1.7092e-05 | 0.060158 | -0.010055 | 0.055482 | -0.22823 | -0.0041788 | 0.015772 | 0.020685 | 0.034397 | 0.0049995 | 0.84347 | 8.2658 | 0.18388 | 121.4389 | 121.2182 | 121.1499 | -0.17295 | 0.010205 | -0.082058 | -0.12045 | -0.062004 | -0.050394 | -0.010564 | -0.20536 | 0.069664 | 0.049154 | 1.0861 | 0.42649 | 0.35683 | -0.17154 | -0.23992 | 0.037257 | -121.4518 | 0.25282 | 0.12216 | 0.084905 | -121.4402 | -121.4003 | 121.6815 | 121.4608 | 121.3925 | 8.5084 | -121.5627 | 0.18061 | 0.19222 | 0.23205 | 0.16056 | -121.5951
1947.7812 | 121.5729 | -0.22888 | 121.4127 | 1.4211e-13 | -0.035857 | 0.00019651 | 0.060158 | -0.010055 | 0.055268 | -0.23586 | -0.0041788 | 0.015986 | 0.020685 | 0.034611 | 0.0047859 | 0.85721 | 8.2337 | 0.19761 | 121.4572 | 121.2274 | 121.1636 | -0.17753 | 0.010205 | -0.077479 | -0.1113 | -0.066582 | -0.045815 | -0.005985 | -0.20536 | 0.051352 | 0.04458 | 1.0861 | 0.4265 | 0.37514 | -0.18527 | -0.24907 | 0.023524 | -121.4792 | 0.23909 | 0.11759 | 0.094062 | -121.4585 | -121.4186 | 121.6861 | 121.4563 | 121.3925 | 8.4626 | -121.5902 | 0.1623 | 0.18307 | 0.2229 | 0.1514 | -121.618
1949.5312 | 121.6461 | -0.21057 | 121.3989 | 1.4211e-13 | -0.035857 | 0.00019651 | 0.060372 | -0.0096276 | 0.054841 | -0.2206 | -0.0043924 | 0.015558 | 0.020685 | 0.034611 | 0.0045721 | 0.85721 | 8.1834 | 0.18846 | 121.4618 | 121.232 | 121.1727 | -0.17753 | 0.010205 | -0.082058 | -0.11587 | -0.071161 | -0.050394 | -0.005985 | -0.20994 | 0.033041 | 0.062891 | 1.0678 | 0.39903 | 0.36599 | -0.16696 | -0.22618 | 0.000634 | -121.4701 | 0.22078 | 0.094697 | 0.094063 | -121.4493 | -121.4049 | 121.6724 | 121.4425 | 121.3833 | 8.3939 | -121.5765 | 0.13941 | 0.16018 | 0.20459 | 0.12851 | -121.6089
1951.2031 | 121.6873 | -0.19684 | 121.3943 | 1.4211e-13 | -0.03607 | 0.00062391 | 0.060158 | -0.010055 | 0.055268 | -0.22823 | -0.003965 | 0.015558 | 0.020044 | 0.034397 | 0.0047859 | 0.87552 | 8.1467 | 0.19304 | 121.4756 | 121.2503 | 121.1865 | -0.17295 | 0.005626 | -0.068322 | -0.11587 | -0.071161 | -0.045815 | -0.005985 | -0.20536 | 0.023887 | 0.081204 | 1.0724 | 0.38987 | 0.36599 | -0.14407 | -0.20787 | -0.00852 | -121.4655 | 0.20246 | 0.080964 | 0.089484 | -121.4402 | -121.4003 | 121.6724 | 121.4471 | 121.3833 | 8.3436 | -121.5673 | 0.12568 | 0.15102 | 0.19085 | 0.12852 | -121.5997
1952.9375 | 121.7239 | -0.19684 | 121.4081 | 1.4211e-13 | -0.03607 | 0.00019651 | 0.060158 | -0.010055 | 0.055055 | -0.23586 | -0.0043924 | 0.015558 | 0.020685 | 0.035038 | 0.0049995 | 0.88468 | 8.0918 | 0.19304 | 121.4847 | 121.2594 | 121.1865 | -0.17753 | 0.010205 | -0.068322 | -0.1113 | -0.066582 | -0.054973 | -0.005985 | -0.20536 | 0.019308 | 0.076628 | 1.0815 | 0.38987 | 0.37057 | -0.14864 | -0.2216 | -0.00852 | -121.4747 | 0.20704 | 0.085542 | 0.094062 | -121.4631 | -121.4141 | 121.6815 | 121.4563 | 121.3833 | 8.2886 | -121.5856 | 0.13026 | 0.14187 | 0.19085 | 0.12852 | -121.6134
1954.6875 | 121.7148 | -0.21057 | 121.4447 | 1.4211e-13 | -0.03607 | 0.00041031 | 0.060158 | -0.010055 | 0.055055 | -0.22823 | -0.0043924 | 0.015558 | 0.020685 | 0.034824 | 0.0041449 | 0.89841 | 8.0414 | 0.19761 | 121.4939 | 121.2594 | 121.1911 | -0.17753 | 0.005626 | -0.0729 | -0.10214 | -0.057425 | -0.050394 | -0.005985 | -0.20536 | 0.033041 | 0.049164 | 1.109 | 0.40818 | 0.37514 | -0.18526 | -0.25364 | 0.005213 | -121.5021 | 0.2162 | 0.10843 | 0.10322 | -121.4951 | -121.4507 | 121.7044 | 121.47 | 121.4016 | 8.252 | -121.6222 | 0.15315 | 0.16018 | 0.20459 | 0.13767 | -121.6501
1956.3594 | 121.669 | -0.25635 | 121.4493 | 1.4211e-13 | -0.035857 | 0.00041031 | 0.060586 | -0.010269 | 0.055482 | -0.23586 | -0.0043924 | 0.015772 | 0.020685 | 0.034824 | 0.0047859 | 0.91215 | 7.9956 | 0.20677 | 121.4984 | 121.2686 | 121.2048 | -0.18669 | 0.001048 | -0.0729 | -0.097559 | -0.062004 | -0.036658 | -0.015142 | -0.20536 | 0.06966 | 0.049164 | 1.1685 | 0.46312 | 0.39346 | -0.18068 | -0.24448 | 0.05099 | -121.5113 | 0.2574 | 0.15879 | 0.1078 | -121.4859 | -121.4644 | 121.7548 | 121.5249 | 121.4611 | 8.252 | -121.636 | 0.19434 | 0.21969 | 0.24121 | 0.18345 | -121.6546
1958.1094 | 121.6278 | -0.25635 | 121.4539 | 1.4211e-13 | -0.036284 | 0.00041031 | 0.059945 | -0.010269 | 0.055055 | -0.22823 | -0.003965 | 0.015345 | 0.020258 | 0.035038 | 0.0045721 | 0.92588 | 7.9407 | 0.21593 | 121.503 | 121.2823 | 121.214 | -0.17753 | 0.001048 | -0.059164 | -0.092981 | -0.062004 | -0.050394 | -0.010564 | -0.20078 | 0.078818 | 0.049165 | 1.1822 | 0.47227 | 0.39346 | -0.17152 | -0.2399 | 0.055569 | -121.5159 | 0.2574 | 0.16337 | 0.1078 | -121.5043 | -121.4644 | 121.7594 | 121.5387 | 121.4703 | 8.1971 | -121.6314 | 0.19434 | 0.20595 | 0.24578 | 0.19718 | -121.6546
1959.8594 | 121.6461 | -0.22888 | 121.4767 | 1.4211e-13 | -0.035857 | 0.00019651 | 0.060158 | -0.010055 | 0.055055 | -0.2206 | -0.0043924 | 0.015558 | 0.020472 | 0.034824 | 0.0045721 | 0.93046 | 7.8858 | 0.22051 | 121.5076 | 121.3006 | 121.2185 | -0.17753 | 0.014784 | -0.059164 | -0.097559 | -0.066582 | -0.050394 | -0.005985 | -0.20078 | 0.051352 | 0.030855 | 1.1593 | 0.44939 | 0.39804 | -0.1761 | -0.25822 | 0.028103 | -121.5433 | 0.24367 | 0.13132 | 0.10322 | -121.5271 | -121.4827 | 121.7365 | 121.5295 | 121.4474 | 8.1146 | -121.6543 | 0.1623 | 0.17849 | 0.2229 | 0.16972 | -121.6775
1961.5469 | 121.6278 | -0.25177 | 121.4767 | 1.4211e-13 | -0.035643 | 0.00041031 | 0.060372 | -0.010055 | 0.055268 | -0.23586 | -0.0041788 | 0.015772 | 0.020685 | 0.034824 | 0.0047859 | 0.95793 | 7.8674 | 0.21593 | 121.5259 | 121.2961 | 121.2277 | -0.18211 | 0.010205 | -0.063743 | -0.097559 | -0.066582 | -0.041237 | -0.001407 | -0.20536 | 0.069661 | 0.049168 | 1.2097 | 0.4677 | 0.39804 | -0.18068 | -0.24906 | 0.046412 | -121.5433 | 0.26198 | 0.15421 | 0.1078 | -121.518 | -121.4782 | 121.7777 | 121.5478 | 121.4795 | 8.1192 | -121.6589 | 0.18519 | 0.21053 | 0.25036 | 0.18803 | -121.6821
1963.2812 | 121.6553 | -0.24719 | 121.4676 | 1.4211e-13 | -0.035857 | 0.00062391 | 0.060158 | -0.010482 | 0.055482 | -0.24349 | -0.003965 | 0.015558 | 0.020472 | 0.034611 | 0.0045721 | 0.96709 | 7.7896 | 0.22966 | 121.5213 | 121.2915 | 121.2368 | -0.18211 | 0.010205 | -0.063743 | -0.092981 | -0.066582 | -0.050394 | -0.005985 | -0.1962 | 0.065083 | 0.053746 | 1.2143 | 0.47685 | 0.41177 | -0.1761 | -0.23074 | 0.050992 | -121.5342 | 0.2574 | 0.15421 | 0.10322 | -121.518 | -121.4736 | 121.7685 | 121.5387 | 121.484 | 8.0368 | -121.6497 | 0.18061 | 0.1968 | 0.24121 | 0.18345 | -121.6638
1965.0312 | 121.669 | -0.24261 | 121.4813 | 1.4211e-13 | -0.035857 | 0.00062391 | 0.060372 | -0.010055 | 0.055268 | -0.21297 | -0.0041788 | 0.015772 | 0.020472 | 0.035038 | 0.0047859 | 0.98082 | 7.7438 | 0.21593 | 121.5259 | 121.3098 | 121.2414 | -0.18669 | 0.005626 | -0.059164 | -0.092981 | -0.066582 | -0.050394 | -0.005985 | -0.20078 | 0.055927 | 0.044591 | 1.2234 | 0.45854 | 0.40261 | -0.17152 | -0.2399 | 0.041836 | -121.5479 | 0.24824 | 0.14963 | 0.1078 | -121.5317 | -121.4873 | 121.7685 | 121.5524 | 121.484 | 7.9864 | -121.668 | 0.17603 | 0.19222 | 0.23663 | 0.18345 | -121.6821
1966.7812 | 121.701 | -0.24719 | 121.4951 | 1.4211e-13 | -0.035857 | 0.00041031 | 0.059945 | -0.010269 | 0.055055 | -0.22823 | -0.0043924 | 0.015558 | 0.020685 | 0.034611 | 0.0043585 | 0.9854 | 7.6889 | 0.22508 | 121.5305 | 121.3098 | 121.246 | -0.18669 | 0.010205 | -0.054586 | -0.092981 | -0.071161 | -0.045815 | -0.010564 | -0.1962 | 0.060504 | 0.035437 | 1.2326 | 0.47228 | 0.41177 | -0.18525 | -0.24905 | 0.050992 | -121.5662 | 0.2574 | 0.15421 | 0.10322 | -121.5409 | -121.5056 | 121.7777 | 121.557 | 121.4932 | 7.9361 | -121.6817 | 0.17603 | 0.20138 | 0.23663 | 0.19261 | -121.6913
1968.4688 | 121.5729 | -0.21515 | 121.3898 | 1.4211e-13 | -0.035857 | 0.00041031 | 0.059945 | -0.010269 | 0.055055 | -0.2206 | -0.0043924 | 0.015772 | 0.019831 | 0.034824 | 0.0047859 | 1.0266 | 7.6477 | 0.26171 | 121.4206 | 121.1953 | 121.1315 | -0.18669 | 0.005626 | -0.054586 | -0.092981 | -0.066582 | -0.045815 | -0.001407 | -0.20536 | 0.028461 | 0.03084 | 1.2418 | 0.47686 | 0.4484 | -0.19444 | -0.25823 | 0.009791 | -121.4564 | 0.22077 | 0.12217 | 0.11238 | -121.4356 | -121.3912 | 121.6358 | 121.4105 | 121.3467 | 7.8628 | -121.5765 | 0.14857 | 0.16933 | 0.21374 | 0.16056 | -121.5951
1970.2031 | 121.6644 | -0.21973 | 121.4539 | 1.4211e-13 | -0.035857 | 0.00041031 | 0.059945 | -0.010269 | 0.055268 | -0.22823 | -0.0043924 | 0.015986 | 0.020472 | 0.035038 | 0.0043585 | 1.0495 | 7.611 | 0.27087 | 121.4939 | 121.2823 | 121.2048 | -0.15921 | 0.005626 | -0.054586 | -0.088402 | -0.066582 | -0.045815 | -0.010564 | -0.1962 | 0.060512 | 0.040009 | 1.2692 | 0.49059 | 0.43008 | -0.17152 | -0.24906 | 0.023527 | -121.5204 | 0.22535 | 0.13133 | 0.1078 | -121.4997 | -121.4644 | 121.7136 | 121.5021 | 121.4245 | 7.8308 | -121.6131 | 0.15315 | 0.17391 | 0.20916 | 0.16514 | -121.6501
1971.9375 | 121.7651 | -0.20599 | 121.4401 | 1.4211e-13 | -0.035857 | 0.00062391 | 0.060158 | -0.010269 | 0.054841 | -0.24349 | -0.003965 | 0.015558 | 0.020472 | 0.034824 | 0.0045721 | 1.0587 | 7.5698 | 0.27087 | 121.5122 | 121.3006 | 121.2323 | -0.16379 | 0.001048 | -0.063743 | -0.088402 | -0.066582 | -0.036658 | -0.001407 | -0.1962 | 0.0422 | 0.072054 | 1.2646 | 0.47686 | 0.43466 | -0.13948 | -0.20786 | 0.009794 | -121.5067 | 0.20704 | 0.11759 | 0.1078 | -121.4768 | -121.4415 | 121.7182 | 121.5066 | 121.4383 | 7.7758 | -121.6039 | 0.13941 | 0.16934 | 0.20459 | 0.14225 | -121.6363
1973.6719 | 121.7285 | -0.1831 | 121.4722 | 1.4211e-13 | -0.03607 | 0.00062391 | 0.060158 | -0.010055 | 0.054627 | -0.23586 | -0.0041788 | 0.015558 | 0.020258 | 0.035038 | 0.0045721 | 1.0724 | 7.5057 | 0.28002 | 121.5396 | 121.3144 | 121.246 | -0.15921 | 0.010205 | -0.059164 | -0.083823 | -0.062004 | -0.041237 | -0.005985 | -0.19162 | 0.02389 | 0.067482 | 1.2555 | 0.46313 | 0.43924 | -0.15778 | -0.22616 | -0.008517 | -121.5342 | 0.19331 | 0.099282 | 0.1078 | -121.5134 | -121.4782 | 121.7228 | 121.4975 | 121.4291 | 7.6888 | -121.6314 | 0.1211 | 0.14187 | 0.17712 | 0.12394 | -121.6638
1975.3594 | 121.7926 | -0.16937 | 121.4493 | 1.4211e-13 | -0.035857 | 0.00019651 | 0.059517 | -0.010269 | 0.054627 | -0.21297 | -0.003965 | 0.015558 | 0.020685 | 0.035252 | 0.0045721 | 1.0953 | 7.4783 | 0.28002 | 121.5488 | 121.3281 | 121.2597 | -0.15921 | 0.010205 | -0.054586 | -0.088402 | -0.071161 | -0.045815 | -0.005985 | -0.18704 | 0.010158 | 0.099526 | 1.2647 | 0.44939 | 0.43924 | -0.12116 | -0.18954 | -0.01767 | -121.5204 | 0.17958 | 0.080971 | 0.098641 | -121.4951 | -121.4553 | 121.7182 | 121.4975 | 121.4291 | 7.6476 | -121.6085 | 0.098212 | 0.12356 | 0.16339 | 0.11479 | -121.6363
1977.0938 | 121.7697 | -0.20142 | 121.4676 | 1.4211e-13 | -0.035857 | 0.00041031 | 0.060372 | -0.010055 | 0.054414 | -0.22823 | -0.0041788 | 0.015345 | 0.020685 | 0.035252 | 0.0047859 | 1.109 | 7.4371 | 0.2846 | 121.558 | 121.3419 | 121.2689 | -0.15464 | -0.003531 | -0.059164 | -0.088402 | -0.062004 | -0.045815 | -0.005985 | -0.1962 | 0.04678 | 0.090373 | 1.3104 | 0.48602 | 0.43924 | -0.12573 | -0.19869 | 0.005216 | -121.5296 | 0.19789 | 0.11301 | 0.1078 | -121.5134 | -121.4736 | 121.7594 | 121.5433 | 121.4703 | 7.6385 | -121.6222 | 0.13941 | 0.1556 | 0.19543 | 0.14225 | -121.6638
1978.8281 | 121.7377 | -0.19226 | 121.4951 | 1.4211e-13 | -0.03607 | 0.00041031 | 0.059945 | -0.010269 | 0.054841 | -0.23586 | -0.003965 | 0.015558 | 0.020685 | 0.034611 | 0.0043585 | 1.1273 | 7.3913 | 0.29376 | 121.5488 | 121.3464 | 121.2781 | -0.16379 | 0.010205 | -0.054586 | -0.097559 | -0.057425 | -0.041237 | -0.005985 | -0.18704 | 0.028467 | 0.05375 | 1.3196 | 0.48602 | 0.45755 | -0.14862 | -0.217 | 0.005218 | -121.5525 | 0.20247 | 0.094702 | 0.089484 | -121.5363 | -121.501 | 121.7411 | 121.5387 | 121.4703 | 7.5835 | -121.6589 | 0.13484 | 0.15102 | 0.18628 | 0.13767 | -121.6821
1980.5156 | 121.7285 | -0.20142 | 121.4996 | 1.4211e-13 | -0.03607 | 0.00041031 | 0.060372 | -0.010269 | 0.054627 | -0.23586 | -0.0041788 | 0.015772 | 0.020472 | 0.035252 | 0.0047859 | 1.109 | 7.3501 | 0.29376 | 121.5625 | 121.3464 | 121.2781 | -0.16837 | 0.014784 | -0.054586 | -0.097559 | -0.057425 | -0.041237 | -0.005985 | -0.19162 | 0.033043 | 0.062908 | 1.3104 | 0.49517 | 0.46213 | -0.1532 | -0.22158 | 0.009794 | -121.5571 | 0.2162 | 0.10386 | 0.094063 | -121.5409 | -121.5056 | 121.764 | 121.5479 | 121.4795 | 7.5515 | -121.668 | 0.14399 | 0.16018 | 0.19543 | 0.14683 | -121.6913
1982.25 | 121.6919 | -0.25177 | 121.5179 | 1.4211e-13 | -0.03607 | 0.00041031 | 0.060158 | -0.010482 | 0.054627 | -0.22823 | -0.0041788 | 0.015558 | 0.020472 | 0.035679 | 0.0043585 | 1.1136 | 7.2997 | 0.29834 | 121.5625 | 121.351 | 121.2781 | -0.16379 | 0.010205 | -0.054586 | -0.10214 | -0.062004 | -0.041237 | -0.001407 | -0.18704 | 0.087976 | 0.044598 | 1.3654 | 0.55011 | 0.46213 | -0.16693 | -0.23989 | 0.064727 | -121.5799 | 0.26198 | 0.14963 | 0.084905 | -121.5592 | -121.5194 | 121.8143 | 121.6028 | 121.5298 | 7.5515 | -121.6817 | 0.18977 | 0.21053 | 0.25036 | 0.19718 | -121.705
1983.9375 | 121.6827 | -0.25635 | 121.5317 | 1.4211e-13 | -0.035857 | 0.00041031 | 0.059517 | -0.010482 | 0.054627 | -0.24349 | -0.0043924 | 0.015772 | 0.020472 | 0.035038 | 0.0043585 | 1.1365 | 7.2448 | 0.30291 | 121.5717 | 121.3556 | 121.2826 | -0.17295 | 0.010205 | -0.054586 | -0.097559 | -0.066582 | -0.036658 | -0.019721 | -0.18704 | 0.083397 | 0.040021 | 1.3928 | 0.55926 | 0.47586 | -0.17608 | -0.24905 | 0.069305 | -121.5983 | 0.26655 | 0.15879 | 0.089484 | -121.5683 | -121.5514 | 121.828 | 121.6119 | 121.539 | 7.5011 | -121.7046 | 0.18977 | 0.21969 | 0.23663 | 0.20176 | -121.7187
1985.6875 | 121.756 | -0.2243 | 121.4859 | 1.4211e-13 | -0.036284 | 0.00041031 | 0.060158 | -0.010055 | 0.054627 | -0.22823 | -0.004606 | 0.015345 | 0.020472 | 0.035038 | 0.0047859 | 1.1502 | 7.1578 | 0.31207 | 121.5671 | 121.3464 | 121.2735 | -0.17295 | 0.005626 | -0.050007 | -0.10214 | -0.062004 | -0.03208 | -0.001407 | -0.19162 | 0.051353 | 0.081219 | 1.3745 | 0.53637 | 0.48502 | -0.13946 | -0.21243 | 0.032682 | -121.5479 | 0.22993 | 0.12217 | 0.089484 | -121.518 | -121.4873 | 121.7914 | 121.5707 | 121.4978 | 7.3821 | -121.6589 | 0.1623 | 0.19222 | 0.2229 | 0.1743 | -121.6775
1987.4375 | 121.756 | -0.22888 | 121.5225 | 1.4211e-13 | -0.035857 | 0.00083771 | 0.059945 | -0.010055 | 0.054841 | -0.22823 | -0.0041788 | 0.015558 | 0.020472 | 0.035252 | 0.0043585 | 1.164 | 7.1211 | 0.32581 | 121.5809 | 121.3648 | 121.2918 | -0.16837 | 0.001048 | -0.063743 | -0.097559 | -0.062004 | -0.041237 | -0.001407 | -0.18704 | 0.060509 | 0.058333 | 1.3928 | 0.55469 | 0.49418 | -0.15777 | -0.23073 | 0.041839 | -121.5845 | 0.22993 | 0.13132 | 0.089484 | -121.5638 | -121.5239 | 121.8097 | 121.5936 | 121.5207 | 7.35 | -121.6909 | 0.16688 | 0.18765 | 0.22748 | 0.16514 | -121.7096
1989.1875 | 121.7743 | -0.19684 | 121.4767 | 1.4211e-13 | -0.035857 | 0.00062391 | 0.060158 | -0.010269 | 0.054841 | -0.24349 | -0.004606 | 0.015558 | 0.020472 | 0.035465 | 0.0043585 | 1.1868 | 7.0891 | 0.32581 | 121.5809 | 121.3648 | 121.3009 | -0.17295 | 0.001048 | -0.063743 | -0.10672 | -0.062004 | -0.050394 | 0.007751 | -0.18246 | 0.023887 | 0.10411 | 1.3837 | 0.52264 | 0.49876 | -0.11199 | -0.1758 | 0.014374 | -121.5388 | 0.19789 | 0.090121 | 0.075747 | -121.5271 | -121.469 | 121.7777 | 121.5616 | 121.4978 | 7.2859 | -121.6497 | 0.13483 | 0.14644 | 0.20459 | 0.1331 | -121.6592
1990.8594 | 121.6827 | -0.24719 | 121.5591 | 1.4211e-13 | -0.03607 | 0.00041031 | 0.059731 | -0.010482 | 0.055055 | -0.22823 | -0.0043924 | 0.015558 | 0.020472 | 0.035038 | 0.0045721 | 1.2052 | 7.0479 | 0.33496 | 121.5809 | 121.3693 | 121.3055 | -0.17753 | 0.005626 | -0.054586 | -0.097559 | -0.062004 | -0.050394 | -0.005985 | -0.18704 | 0.069662 | 0.021712 | 1.4524 | 0.58215 | 0.51249 | -0.18981 | -0.25362 | 0.060149 | -121.6211 | 0.25282 | 0.14963 | 0.089484 | -121.6095 | -121.5651 | 121.828 | 121.6165 | 121.5527 | 7.2951 | -121.7367 | 0.18519 | 0.1968 | 0.24121 | 0.19261 | -121.7462
1992.6094 | 121.8018 | -0.20142 | 121.5088 | 1.4211e-13 | -0.035857 | 0.00062391 | 0.059945 | -0.010269 | 0.054414 | -0.24349 | -0.004606 | 0.016199 | 0.020258 | 0.035252 | 0.0047859 | 1.2235 | 7.0021 | 0.33954 | 121.5854 | 121.3693 | 121.3055 | -0.17295 | 0.005626 | -0.050007 | -0.092981 | -0.066582 | -0.045815 | -0.005985 | -0.19162 | 0.028465 | 0.076644 | 1.4249 | 0.54096 | 0.51249 | -0.13946 | -0.20326 | 0.009794 | -121.5754 | 0.20704 | 0.10844 | 0.098641 | -121.5546 | -121.5148 | 121.7868 | 121.5707 | 121.5069 | 7.2035 | -121.6817 | 0.13483 | 0.1556 | 0.19543 | 0.15141 | -121.7004
1994.2969 | 121.8384 | -0.18768 | 121.5134 | 1.4211e-13 | -0.03607 | 0.00041031 | 0.060372 | -0.010055 | 0.054841 | -0.2206 | -0.0043924 | 0.015558 | 0.020258 | 0.035038 | 0.0045721 | 1.2372 | 6.9609 | 0.33038 | 121.5854 | 121.3739 | 121.3055 | -0.18211 | 0.001048 | -0.054586 | -0.092981 | -0.071161 | -0.041237 | -0.010564 | -0.18704 | 0.005574 | 0.072066 | 1.4249 | 0.51807 | 0.51249 | -0.13945 | -0.20784 | 0.00064 | -121.5845 | 0.18873 | 0.094702 | 0.094062 | -121.5546 | -121.5239 | 121.7731 | 121.5616 | 121.4932 | 7.1486 | -121.6955 | 0.11652 | 0.14645 | 0.17712 | 0.1331 | -121.7004
1996.0312 | 121.8246 | -0.20142 | 121.4996 | 1.4211e-13 | -0.035857 | 0.00062391 | 0.060158 | -0.010482 | 0.054627 | -0.23586 | -0.003965 | 0.015772 | 0.020472 | 0.035679 | 0.0047859 | 1.2601 | 6.9197 | 0.3487 | 121.5854 | 121.3693 | 121.2964 | -0.17753 | 0.005626 | -0.059164 | -0.10214 | -0.057425 | -0.03208 | -0.010564 | -0.18704 | 0.023886 | 0.085799 | 1.4615 | 0.55011 | 0.52623 | -0.1303 | -0.20327 | 0.014373 | -121.5571 | 0.20704 | 0.099278 | 0.084905 | -121.5317 | -121.5102 | 121.7868 | 121.5707 | 121.4978 | 7.1211 | -121.6772 | 0.14399 | 0.16934 | 0.19085 | 0.14225 | -121.6867
1997.8125 | 121.7651 | -0.23804 | 121.5454 | 1.4211e-13 | -0.035643 | 0.00062391 | 0.059945 | -0.010269 | 0.054414 | -0.22823 | -0.0041788 | 0.015558 | 0.020472 | 0.035252 | 0.0047859 | 1.2738 | 6.8693 | 0.35328 | 121.5854 | 121.3739 | 121.3055 | -0.19127 | 0.010205 | -0.045428 | -0.088402 | -0.062004 | -0.03208 | -0.005985 | -0.18246 | 0.04677 | 0.040023 | 1.5119 | 0.59131 | 0.54454 | -0.1715 | -0.23989 | 0.055573 | -121.6074 | 0.24824 | 0.14964 | 0.094062 | -121.5775 | -121.5514 | 121.8235 | 121.6119 | 121.5436 | 7.1073 | -121.7367 | 0.17603 | 0.20596 | 0.23205 | 0.19261 | -121.7279
1999.5469 | 121.7285 | -0.25635 | 121.5546 | 1.4211e-13 | -0.036284 | 0.00041031 | 0.060158 | -0.010055 | 0.054841 | -0.22823 | -0.0041788 | 0.015558 | 0.020258 | 0.035252 | 0.0047859 | 1.2922 | 6.8327 | 0.35785 | 121.59 | 121.3831 | 121.3055 | -0.18211 | 0.010205 | -0.050007 | -0.092981 | -0.066582 | -0.041237 | -0.005985 | -0.18246 | 0.074239 | 0.035447 | 1.5485 | 0.6142 | 0.53996 | -0.17149 | -0.24904 | 0.073884 | -121.6211 | 0.26655 | 0.16337 | 0.089483 | -121.5958 | -121.5605 | 121.8464 | 121.6394 | 121.5619 | 7.089 | -121.7367 | 0.18977 | 0.21511 | 0.25036 | 0.20634 | -121.737
2001.2812 | 121.8109 | -0.21973 | 121.4951 | 1.4211e-13 | -0.03607 | 0.00041031 | 0.059731 | -0.010482 | 0.0542 | -0.21297 | -0.003965 | 0.015772 | 0.020472 | 0.035465 | 0.0045721 | 1.315 | 6.7961 | 0.36701 | 121.59 | 121.3785 | 121.3101 | -0.18669 | 0.001048 | -0.054586 | -0.092981 | -0.071161 | -0.036658 | -0.001407 | -0.18704 | 0.033039 | 0.094956 | 1.5348 | 0.58674 | 0.5537 | -0.11657 | -0.18495 | 0.032684 | -121.5662 | 0.22077 | 0.12675 | 0.094062 | -121.5317 | -121.4965 | 121.8097 | 121.5982 | 121.5298 | 7.0158 | -121.6817 | 0.14857 | 0.18307 | 0.21832 | 0.16514 | -121.6821
2002.9531 | 121.8155 | -0.2243 | 121.5225 | 1.4211e-13 | -0.035857 | 0.00083771 | 0.059945 | -0.010269 | 0.054414 | -0.23586 | -0.0041788 | 0.015558 | 0.020258 | 0.035465 | 0.0043585 | 1.3288 | 6.7503 | 0.37159 | 121.59 | 121.3876 | 121.3055 | -0.18211 | 0.010205 | -0.054586 | -0.088402 | -0.062004 | -0.036658 | -0.001407 | -0.18246 | 0.042195 | 0.06749 | 1.5531 | 0.59589 | 0.5537 | -0.13487 | -0.217 | 0.04184 | -121.5845 | 0.23451 | 0.1359 | 0.094062 | -121.5592 | -121.5239 | 121.8143 | 121.612 | 121.5298 | 6.9746 | -121.7046 | 0.1623 | 0.18765 | 0.2229 | 0.16972 | -121.705
2004.7031 | 121.8292 | -0.22888 | 121.5134 | 1.4211e-13 | -0.035857 | 0.00062391 | 0.059945 | -0.0098414 | 0.054414 | -0.22823 | -0.0041788 | 0.015345 | 0.020258 | 0.035465 | 0.0047859 | 1.3105 | 6.677 | 0.34412 | 121.5442 | 121.3464 | 121.2643 | -0.25079 | 0.005626 | -0.054586 | -0.083823 | -0.062004 | -0.041237 | -0.005985 | -0.2191 | -0.021911 | 0.030861 | 1.5393 | 0.573 | 0.59491 | -0.16693 | -0.24905 | 0.009787 | -121.5754 | 0.23451 | 0.14506 | 0.13527 | -121.5546 | -121.5194 | 121.7731 | 121.5753 | 121.4932 | 6.9059 | -121.7642 | 0.16688 | 0.18765 | 0.2229 | 0.1743 | -121.7325
2006.4531 | 121.788 | -0.25177 | 121.5363 | 1.4211e-13 | -0.036498 | 0.00041031 | 0.060158 | -0.010269 | 0.054841 | -0.2206 | -0.0043924 | 0.015558 | 0.020258 | 0.035465 | 0.0043585 | 1.3746 | 6.6587 | 0.3899 | 121.59 | 121.3785 | 121.3147 | -0.19127 | 0.005626 | -0.050007 | -0.083823 | -0.071161 | -0.03208 | -0.010564 | -0.20994 | 0.060503 | 0.053757 | 1.6263 | 0.64167 | 0.58117 | -0.15776 | -0.22157 | 0.041833 | -121.6074 | 0.2574 | 0.16795 | 0.12611 | -121.5683 | -121.5468 | 121.8418 | 121.6303 | 121.5665 | 6.9105 | -121.7275 | 0.18061 | 0.21969 | 0.24121 | 0.20176 | -121.7462
2008.125 | 121.8658 | -0.25177 | 121.4218 | 1.4211e-13 | -0.035857 | 0.00083771 | 0.060158 | -0.010055 | 0.054414 | -0.24349 | -0.004606 | 0.015772 | 0.020258 | 0.035252 | 0.0043585 | 1.37 | 6.5946 | 0.37159 | 121.5763 | 121.3556 | 121.2826 | -0.24163 | 0.010205 | -0.045428 | -0.092981 | -0.066582 | -0.041237 | -0.001407 | -0.20078 | 0.010135 | 0.15446 | 1.6218 | 0.62336 | 0.61322 | -0.066218 | -0.13918 | 0.050991 | -121.4884 | 0.26198 | 0.15879 | 0.1078 | -121.4631 | -121.4232 | 121.828 | 121.6074 | 121.5344 | 6.8464 | -121.6634 | 0.18519 | 0.21053 | 0.25036 | 0.20634 | -121.6226
2009.8125 | 117.5766 | -27.4841 | 89.6439 | 1.4211e-13 | -0.036925 | -0.00023069 | 0.056739 | -0.009414 | 0.052491 | -0.22823 | -0.0043924 | 0.015345 | 0.020044 | 0.035252 | 0.0045721 | -27.8127 | -12.2738 | -28.7463 | 87.774 | 87.6272 | 87.5933 | -29.62 | 0.02852 | -0.027113 | -0.056351 | -0.039111 | -0.009187 | 0.016908 | -0.17788 | -2.1359 | -1.8698 | -0.32853 | -1.2621 | 0.87374 | -2.0166 | -2.0506 | 27.3062 | -89.683 | 27.5127 | 27.4278 | 0.12153 | -89.653 | -89.627 | 115.2582 | 115.1114 | 115.0774 | 15.2103 | -119.2639 | 27.445 | 27.4749 | 27.501 | 27.457 | -89.8217
2011.5625 | 120.8908 | -0.19226 | 120.8176 | 1.4211e-13 | -0.03607 | 0.00062391 | 0.059945 | -0.010055 | 0.054414 | -0.23586 | -0.0043924 | 0.015345 | 0.020472 | 0.035252 | 0.0045721 | 1.5028 | 6.4481 | 0.43568 | 120.7888 | 120.5818 | 120.5134 | -0.19585 | 0.014784 | -0.054586 | -0.083823 | -0.057425 | -0.03208 | -0.001407 | -0.1962 | -0.003585 | -0.028772 | 1.695 | 0.62794 | 0.63153 | -0.23581 | -0.30414 | -0.003939 | -120.875 | 0.20704 | 0.10844 | 0.11238 | -120.8496 | -120.819 | 120.9811 | 120.774 | 120.7057 | 6.6403 | -121.0134 | 0.13484 | 0.16018 | 0.19085 | 0.13767 | -121.0138
2013.2344 | 121.0464 | -0.17853 | 120.9183 | 1.4211e-13 | -0.036498 | 0.00041031 | 0.059731 | -0.0098414 | 0.0542 | -0.23586 | -0.004606 | 0.015558 | 0.020044 | 0.035038 | 0.0047859 | 1.5531 | 6.4618 | 0.48147 | 120.9628 | 120.7512 | 120.6828 | -0.13632 | 0.005626 | -0.027113 | -0.092981 | -0.066582 | -0.041237 | -0.005985 | -0.19162 | 0.042208 | 0.044499 | 1.7316 | 0.65999 | 0.61779 | -0.1671 | -0.23544 | -0.013094 | -120.9849 | 0.18415 | 0.085547 | 0.098641 | -120.9595 | -120.9243 | 121.1413 | 120.9297 | 120.8614 | 6.6403 | -121.0546 | 0.11195 | 0.13729 | 0.17254 | 0.15141 | -121.1099
2014.9219 | 121.1655 | -0.13275 | 120.9778 | 1.4211e-13 | -0.035857 | 0.00062391 | 0.060158 | -0.010055 | 0.0542 | -0.22823 | -0.004606 | 0.015558 | 0.020258 | 0.035679 | 0.0043585 | 1.5714 | 6.4389 | 0.49062 | 121.0223 | 120.8153 | 120.7515 | -0.13632 | 0.014784 | -0.022535 | -0.088402 | -0.066582 | -0.045815 | -0.001407 | -0.18246 | -0.003569 | 0.044509 | 1.7042 | 0.62337 | 0.62694 | -0.1625 | -0.22627 | -0.049713 | -121.0444 | 0.14753 | 0.044349 | 0.094062 | -121.0236 | -120.9792 | 121.155 | 120.948 | 120.8843 | 6.5717 | -121.1141 | 0.066169 | 0.086936 | 0.13134 | 0.11022 | -121.1602
2016.6562 | 121.2753 | -0.16479 | 120.9915 | 1.4211e-13 | -0.03607 | 0.00062391 | 0.059945 | -0.010055 | 0.0542 | -0.22823 | -0.0041788 | 0.015558 | 0.020685 | 0.035679 | 0.0045721 | 1.5577 | 6.4206 | 0.50436 | 121.0635 | 120.8565 | 120.7881 | -0.13632 | 0.005626 | -0.031692 | -0.097559 | -0.057425 | -0.045815 | -0.001407 | -0.19162 | 0.028475 | 0.071981 | 1.7225 | 0.66915 | 0.64068 | -0.13502 | -0.20337 | -0.026827 | -121.0489 | 0.17042 | 0.067236 | 0.094063 | -121.0373 | -120.9929 | 121.2283 | 121.0213 | 120.9529 | 6.5854 | -121.1278 | 0.10737 | 0.11898 | 0.16339 | 0.1331 | -121.1831
2018.4062 | 121.257 | -0.14648 | 121.0373 | 1.4211e-13 | -0.036284 | 0.00041031 | 0.060158 | -0.010269 | 0.0542 | -0.24349 | -0.0043924 | 0.015772 | 0.020258 | 0.035679 | 0.0047859 | 1.5897 | 6.3794 | 0.50894 | 121.1047 | 120.8885 | 120.8294 | -0.12258 | 0.010205 | -0.027113 | -0.088402 | -0.057425 | -0.036658 | -0.005985 | -0.18246 | 0.023901 | 0.067411 | 1.7362 | 0.65542 | 0.63152 | -0.14875 | -0.20794 | -0.03598 | -121.0947 | 0.15669 | 0.058082 | 0.094062 | -121.0739 | -121.0433 | 121.2512 | 121.035 | 120.9758 | 6.5259 | -121.1599 | 0.089059 | 0.10983 | 0.1405 | 0.11937 | -121.2198
2020.0938 | 121.2753 | -0.16479 | 121.0602 | 1.4211e-13 | -0.035643 | 0.00062391 | 0.060158 | -0.010269 | 0.054414 | -0.23586 | -0.004606 | 0.015558 | 0.020044 | 0.035679 | 0.0045721 | 1.5943 | 6.3336 | 0.4952 | 121.1047 | 120.8885 | 120.8294 | -0.17295 | 0.005626 | -0.022535 | -0.092981 | -0.071161 | -0.045815 | 0.007751 | -0.18246 | -0.008156 | 0.044522 | 1.7591 | 0.66 | 0.66815 | -0.17163 | -0.23083 | -0.017669 | -121.1313 | 0.17042 | 0.071814 | 0.089483 | -121.106 | -121.0524 | 121.2695 | 121.0533 | 120.9941 | 6.4984 | -121.2331 | 0.093634 | 0.11898 | 0.17255 | 0.14226 | -121.2426
2021.8438 | 118.0115 | -12.5839 | 104.7821 | 1.4211e-13 | -0.036498 | 0.00019651 | 0.05738 | -0.0096276 | 0.052063 | -0.22823 | -0.0043924 | 0.015558 | 0.020044 | 0.035465 | 0.0045721 | -19.2557 | -7.3152 | -20.3909 | 96.1479 | 96.0799 | 95.9172 | -21.149 | 0.019362 | -0.013377 | -0.079245 | -0.04369 | -0.022922 | 0.016908 | -0.15957 | -8.5651 | -8.6342 | -6.6717 | -7.807 | 0.75809 | -8.7022 | -8.8649 | 12.4244 | -104.8258 | 12.6033 | 12.5047 | 0.080325 | -104.805 | -104.7652 | 108.7318 | 108.6639 | 108.5011 | 5.2687 | -125.9311 | 12.5402 | 12.561 | 12.6008 | 12.5705 | -104.9417
2023.5938 | 120.5658 | -0.17853 | 120.4422 | 1.4211e-13 | -0.035857 | 0.00083771 | 0.059517 | -0.010055 | 0.053986 | -0.23586 | -0.0043924 | 0.015345 | 0.020258 | 0.035465 | 0.0045721 | 1.6905 | 6.1825 | 0.53183 | 120.4591 | 120.2612 | 120.1883 | -0.15006 | 0.001048 | -0.031692 | -0.088402 | -0.057425 | -0.036658 | -0.005985 | -0.18246 | 0.028471 | 0.01695 | 1.869 | 0.71036 | 0.68188 | -0.18097 | -0.25386 | -0.003936 | -120.4996 | 0.17958 | 0.090126 | 0.094062 | -120.4789 | -120.4482 | 120.6377 | 120.4398 | 120.3669 | 6.361 | -120.5923 | 0.1211 | 0.14187 | 0.17254 | 0.14684 | -120.6247
2025.2812 | 120.6573 | -0.19226 | 120.5292 | 1.4211e-13 | -0.035857 | 0.00062391 | 0.059517 | -0.010482 | 0.054414 | -0.22823 | -0.004606 | 0.015558 | 0.020258 | 0.035679 | 0.0045721 | 1.6859 | 6.1734 | 0.54556 | 120.5965 | 120.3803 | 120.3165 | -0.13632 | 0.010205 | -0.031692 | -0.092981 | -0.062004 | -0.041237 | -0.005985 | -0.17788 | 0.055941 | 0.067327 | 1.8782 | 0.73782 | 0.68188 | -0.14889 | -0.21263 | 0.014376 | -120.5912 | 0.20247 | 0.09928 | 0.084904 | -120.5704 | -120.5352 | 120.7888 | 120.5725 | 120.5088 | 6.3656 | -120.6655 | 0.13026 | 0.15102 | 0.18628 | 0.16057 | -120.7071
2026.9688 | 120.8542 | -0.16937 | 120.6116 | 1.4211e-13 | -0.035857 | 0.00083771 | 0.059945 | -0.010269 | 0.054414 | -0.24349 | -0.0043924 | 0.015772 | 0.020044 | 0.035465 | 0.0043585 | 1.7042 | 6.1459 | 0.56388 | 120.6743 | 120.4444 | 120.3761 | -0.13632 | 0.010205 | -0.027113 | -0.097559 | -0.066582 | -0.036658 | -0.005985 | -0.16415 | 0.033053 | 0.062762 | 1.8736 | 0.73325 | 0.7002 | -0.16718 | -0.2355 | 0.005224 | -120.6782 | 0.17958 | 0.071814 | 0.06659 | -120.6482 | -120.6176 | 120.8437 | 120.6138 | 120.5454 | 6.3153 | -120.7479 | 0.10279 | 0.13271 | 0.16339 | 0.14226 | -120.7757
2028.7031 | 115.4297 | -37.8525 | 77.3941 | 1.4211e-13 | -0.037352 | -0.00023069 | 0.055244 | -0.0092004 | 0.051636 | -0.23586 | -0.0043924 | 0.015345 | 0.020044 | 0.035679 | 0.0047859 | -37.1159 | -18.9632 | -38.1272 | 75.9206 | 75.7999 | 75.7896 | -39.483 | 0.046835 | 0.004938 | -0.051772 | -0.029954 | -0.013765 | 0.026065 | -0.12294 | -1.6305 | -1.4735 | 0.73653 | -0.2747 | 1.3558 | -1.5942 | -1.6045 | 37.7295 | -77.4241 | 37.8993 | 37.8007 | 0.071167 | -77.4079 | -77.368 | 113.7731 | 113.6524 | 113.6421 | 18.8893 | -116.8771 | 37.8225 | 37.8387 | 37.8785 | 37.8574 | -77.517
2030.4531 | 120.0302 | -0.20599 | 119.9066 | 1.4211e-13 | -0.035857 | 0.00062391 | 0.059517 | -0.010696 | 0.053986 | -0.22823 | -0.0048196 | 0.015558 | 0.020044 | 0.035252 | 0.0043585 | 1.7225 | 5.9765 | 0.51352 | 119.8823 | 119.6706 | 119.6023 | -0.21874 | 0.005626 | -0.031692 | -0.079245 | -0.066582 | -0.036658 | -0.010564 | -0.15499 | -0.012747 | -0.024343 | 1.9285 | 0.71951 | 0.73226 | -0.23606 | -0.30433 | 0.051003 | -119.9732 | 0.21162 | 0.12675 | 0.075746 | -119.9433 | -119.9172 | 120.0883 | 119.8765 | 119.8083 | 6.1825 | -120.1254 | 0.13941 | 0.16934 | 0.19543 | 0.1743 | -120.0616
2032.1875 | 120.2362 | -0.3067 | 119.9844 | 1.4211e-13 | -0.035643 | 0.00083771 | 0.059731 | -0.010482 | 0.0542 | -0.22823 | -0.0043924 | 0.015558 | 0.020258 | 0.035893 | 0.0045721 | 1.7179 | 5.9811 | 0.51352 | 120.0791 | 119.8629 | 119.7946 | -0.2279 | 0.010205 | -0.040849 | -0.088402 | -0.066582 | -0.036658 | -0.005985 | -0.16415 | 0.078803 | 0.094708 | 2.0246 | 0.82022 | 0.74141 | -0.12157 | -0.18985 | 0.14255 | -120.051 | 0.31691 | 0.2183 | 0.075747 | -120.0211 | -119.9904 | 120.3858 | 120.1696 | 120.1013 | 6.2878 | -120.2123 | 0.24012 | 0.27004 | 0.30072 | 0.26585 | -120.1486
2033.9219 | 120.4376 | -0.46692 | 119.8334 | 1.4211e-13 | -0.036284 | 0.00083771 | 0.059731 | -0.010269 | 0.0542 | -0.22823 | -0.003965 | 0.015345 | 0.020044 | 0.035893 | 0.0043585 | 1.576 | 5.83 | 0.36701 | 119.9738 | 119.7713 | 119.6847 | -0.40648 | 0.010205 | -0.036271 | -0.079245 | -0.062004 | -0.036658 | -0.001407 | -0.15957 | 0.060442 | 0.14047 | 2.0429 | 0.83393 | 0.77349 | -0.062086 | -0.14868 | 0.30735 | -119.8954 | 0.47712 | 0.38767 | 0.080325 | -119.87 | -119.8348 | 120.4408 | 120.2382 | 120.1516 | 6.2969 | -120.2399 | 0.40491 | 0.43026 | 0.46551 | 0.43065 | -119.9929
2035.6719 | 120.3461 | -0.26093 | 120.2362 | 1.4211e-13 | -0.03607 | 0.00083771 | 0.059517 | -0.010269 | 0.054627 | -0.22823 | -0.0043924 | 0.015986 | 0.020044 | 0.035679 | 0.0043585 | 1.7866 | 5.9124 | 0.56388 | 120.244 | 120.0323 | 119.9457 | -0.2279 | 0.014784 | -0.027113 | -0.088402 | -0.071161 | -0.041237 | -0.001407 | -0.15957 | 0.033026 | 0.00776 | 2.0475 | 0.8248 | 0.79178 | -0.20392 | -0.29053 | 0.10136 | -120.3074 | 0.27571 | 0.17252 | 0.071168 | -120.2774 | -120.2376 | 120.5049 | 120.2932 | 120.2066 | 6.1733 | -120.4641 | 0.18976 | 0.21969 | 0.25952 | 0.23381 | -120.3958
2037.3438 | 119.6732 | -2.7054 | 116.9678 | 1.4211e-13 | -0.036284 | 0.0010513 | 0.058662 | -0.010269 | 0.053345 | -0.25112 | -0.0043924 | 0.015772 | 0.020258 | 0.035679 | 0.0043585 | -4.9757 | 1.3658 | -6.3081 | 111.7602 | 111.6116 | 111.4478 | -7.0825 | 0.019362 | -0.022535 | -0.074666 | -0.052847 | -0.03208 | 0.007751 | -0.15499 | -4.3772 | -5.2076 | -2.2703 | -3.6027 | 0.77443 | -5.3561 | -5.52 | 2.5504 | -117.0206 | 2.7247 | 2.6307 | 0.080325 | -116.9999 | -116.96 | 114.4656 | 114.317 | 114.1532 | 4.0712 | -124.0503 | 2.6525 | 2.6733 | 2.7131 | 2.6828 | -117.1228
2039.0781 | 120.2637 | -0.18768 | 120.0806 | 1.4211e-13 | -0.035643 | 0.0010513 | 0.059517 | -0.010482 | 0.054414 | -0.22823 | -0.0043924 | 0.015345 | 0.020044 | 0.035679 | 0.0041449 | 1.9423 | 5.8666 | 0.62797 | 120.1158 | 119.9041 | 119.8312 | -0.13632 | 0.001048 | -0.031692 | -0.092981 | -0.066582 | -0.03208 | -0.001407 | -0.15957 | 0.051363 | 0.035205 | 2.13 | 0.81566 | 0.76429 | -0.17649 | -0.24935 | 0.028113 | -120.1471 | 0.18873 | 0.094702 | 0.066589 | -120.1126 | -120.082 | 120.3035 | 120.0918 | 120.0189 | 6.0543 | -120.2169 | 0.1211 | 0.1556 | 0.18628 | 0.15599 | -120.2401
2040.8281 | 120.2728 | -0.21515 | 120.1859 | 1.4211e-13 | -0.035857 | 0.0010513 | 0.059517 | -0.0096276 | 0.054414 | -0.23586 | -0.004606 | 0.015772 | 0.020044 | 0.035893 | 0.0043585 | 1.9743 | 5.8483 | 0.65086 | 120.2348 | 120.0277 | 119.9365 | -0.12258 | 0.010205 | -0.022535 | -0.083823 | -0.062004 | -0.03208 | -0.005985 | -0.16415 | 0.092566 | 0.048957 | 2.1895 | 0.86601 | 0.77345 | -0.15814 | -0.24933 | 0.051 | -120.2479 | 0.22535 | 0.13133 | 0.080326 | -120.2179 | -120.1918 | 120.45 | 120.2429 | 120.1517 | 6.0634 | -120.3084 | 0.15315 | 0.18307 | 0.20916 | 0.19261 | -120.35
2042.5156 | 120.3506 | -0.20142 | 120.2728 | 1.4211e-13 | -0.036284 | 0.0010513 | 0.060158 | -0.010269 | 0.0542 | -0.22823 | -0.0041788 | 0.015558 | 0.020258 | 0.035465 | 0.0041449 | 1.9652 | 5.8254 | 0.65544 | 120.2852 | 120.0735 | 119.996 | -0.1409 | 0.001048 | -0.031692 | -0.083823 | -0.057425 | -0.036658 | -0.001407 | -0.16415 | 0.060517 | 0.012344 | 2.1666 | 0.85686 | 0.79634 | -0.19933 | -0.27678 | 0.037267 | -120.3303 | 0.20246 | 0.11759 | 0.080326 | -120.3095 | -120.2742 | 120.4866 | 120.2749 | 120.1975 | 6.0268 | -120.4137 | 0.14399 | 0.16476 | 0.20001 | 0.16972 | -120.437
2044.25 | 120.4559 | -0.1831 | 120.2637 | 1.4211e-13 | -0.036284 | 0.0010513 | 0.059731 | -0.010269 | 0.054414 | -0.2206 | -0.003965 | 0.015558 | 0.020258 | 0.035679 | 0.0041449 | 2.0018 | 5.7933 | 0.68291 | 120.3126 | 120.1101 | 120.0281 | -0.15006 | 0.010205 | -0.031692 | -0.083823 | -0.052847 | -0.03208 | -0.005985 | -0.16873 | 0.033048 | 0.04897 | 2.1849 | 0.86602 | 0.83297 | -0.15354 | -0.23558 | 0.014377 | -120.3165 | 0.19331 | 0.099282 | 0.084905 | -120.2958 | -120.2697 | 120.4957 | 120.2932 | 120.2112 | 5.9764 | -120.4137 | 0.13026 | 0.15102 | 0.17712 | 0.15141 | -120.4324
2045.9844 | 120.4468 | -0.17395 | 120.2362 | 1.4211e-13 | -0.03607 | 0.0012649 | 0.059731 | -0.010269 | 0.054627 | -0.24349 | -0.0041788 | 0.015345 | 0.020258 | 0.036106 | 0.0039313 | 2.0659 | 5.743 | 0.68291 | 120.2897 | 120.0689 | 119.9915 | -0.1409 | 0.005626 | -0.027113 | -0.083823 | -0.057425 | -0.036658 | -0.005985 | -0.15957 | 0.033051 | 0.053544 | 2.2399 | 0.85686 | 0.82381 | -0.16729 | -0.24474 | 0.01438 | -120.2936 | 0.17958 | 0.090127 | 0.075747 | -120.2729 | -120.2422 | 120.4637 | 120.2429 | 120.1654 | 5.9169 | -120.3771 | 0.11652 | 0.13729 | 0.16797 | 0.14684 | -120.3958
2047.7188 | 120.5429 | -0.14191 | 120.2682 | 1.4211e-13 | -0.03607 | 0.0010513 | 0.059731 | -0.010055 | 0.054627 | -0.23586 | -0.0041788 | 0.015558 | 0.020044 | 0.035893 | 0.0041449 | 2.1071 | 5.7247 | 0.69207 | 120.3584 | 120.1422 | 120.0601 | -0.13174 | 0.005626 | -0.031692 | -0.083823 | -0.062004 | -0.027501 | -0.005985 | -0.16415 | 0.010166 | 0.090176 | 2.249 | 0.83398 | 0.82381 | -0.12607 | -0.2081 | -0.022242 | -120.3303 | 0.14753 | 0.058084 | 0.080326 | -120.2958 | -120.2742 | 120.5003 | 120.2841 | 120.2021 | 5.8666 | -120.4 | 0.079903 | 0.11441 | 0.13592 | 0.11022 | -120.4324
2049.4062 | 120.4742 | -0.19226 | 120.3186 | 1.4211e-13 | -0.035857 | 0.0010513 | 0.059731 | -0.010055 | 0.054627 | -0.23586 | -0.0041788 | 0.015345 | 0.020044 | 0.035679 | 0.0043585 | 2.1437 | 5.6926 | 0.71954 | 120.3905 | 120.1788 | 120.1014 | -0.12258 | 0.010205 | -0.027113 | -0.083823 | -0.057425 | -0.036658 | -0.005985 | -0.16415 | 0.069678 | 0.07187 | 2.336 | 0.9118 | 0.84212 | -0.13979 | -0.21725 | 0.028112 | -120.376 | 0.20247 | 0.10844 | 0.080326 | -120.3553 | -120.3246 | 120.5827 | 120.3711 | 120.2936 | 5.8849 | -120.4412 | 0.13484 | 0.1556 | 0.18628 | 0.16515 | -120.4828
2051.1562 | 120.4834 | -0.21057 | 120.3506 | 1.4211e-13 | -0.035857 | 0.0012649 | 0.059945 | -0.010269 | 0.054414 | -0.22823 | -0.004606 | 0.015558 | 0.019831 | 0.035679 | 0.0039313 | 2.1392 | 5.6331 | 0.72869 | 120.4225 | 120.2109 | 120.1334 | -0.12716 | 0.014784 | -0.031692 | -0.079245 | -0.062004 | -0.03208 | -0.001407 | -0.15957 | 0.083409 | 0.071876 | 2.3497 | 0.93927 | 0.85586 | -0.13978 | -0.21724 | 0.051001 | -120.4127 | 0.22535 | 0.13133 | 0.080325 | -120.3827 | -120.3521 | 120.6331 | 120.4214 | 120.344 | 5.8437 | -120.4778 | 0.14857 | 0.17849 | 0.20916 | 0.17888 | -120.5102
2052.8906 | 120.5154 | -0.1831 | 120.3827 | 1.4211e-13 | -0.035857 | 0.0014787 | 0.059731 | -0.0098414 | 0.054627 | -0.23586 | -0.0043924 | 0.015558 | 0.020258 | 0.035893 | 0.0041449 | 2.1712 | 5.601 | 0.74243 | 120.4317 | 120.2338 | 120.1563 | -0.13174 | 0.005626 | -0.031692 | -0.079245 | -0.066582 | -0.027501 | -0.001407 | -0.16415 | 0.051364 | 0.04899 | 2.3543 | 0.92553 | 0.87417 | -0.14893 | -0.22639 | 0.018956 | -120.4493 | 0.18873 | 0.10386 | 0.084904 | -120.4102 | -120.3841 | 120.6148 | 120.4169 | 120.3394 | 5.7841 | -120.5144 | 0.11652 | 0.1556 | 0.1817 | 0.15141 | -120.5468
2054.5781 | 120.6482 | -0.14648 | 120.3735 | 1.4211e-13 | -0.035643 | 0.0014787 | 0.060372 | -0.010055 | 0.054627 | -0.22823 | -0.0041788 | 0.015772 | 0.019617 | 0.036106 | 0.0041449 | 2.2124 | 5.5598 | 0.74701 | 120.4637 | 120.2521 | 120.1609 | -0.13174 | 0.005626 | -0.031692 | -0.088402 | -0.062004 | -0.027501 | -0.001407 | -0.15957 | 0.014743 | 0.090193 | 2.3589 | 0.89349 | 0.87875 | -0.12146 | -0.21266 | -0.013086 | -120.4355 | 0.15211 | 0.058082 | 0.071168 | -120.401 | -120.3749 | 120.6102 | 120.3986 | 120.3074 | 5.7063 | -120.5053 | 0.08448 | 0.11898 | 0.14508 | 0.11479 | -120.5331
2056.3281 | 120.6665 | -0.13275 | 120.3781 | 1.4211e-13 | -0.035857 | 0.0012649 | 0.060372 | -0.010055 | 0.054627 | -0.22823 | -0.0043924 | 0.015558 | 0.019831 | 0.035893 | 0.0039313 | 2.2399 | 5.5003 | 0.76074 | 120.4683 | 120.2567 | 120.1929 | -0.17295 | 0.010205 | -0.036271 | -0.079245 | -0.062004 | -0.03208 | -0.001407 | -0.15957 | -0.0402 | 0.090194 | 2.3726 | 0.89349 | 0.93369 | -0.12146 | -0.18519 | -0.026819 | -120.4401 | 0.14296 | 0.053506 | 0.080325 | -120.4102 | -120.3795 | 120.6011 | 120.3894 | 120.3257 | 5.6331 | -120.5511 | 0.070747 | 0.10067 | 0.13134 | 0.09648 | -120.5377
2058.0156 | 120.6573 | -0.16022 | 120.4239 | 1.4211e-13 | -0.03607 | 0.0019059 | 0.059945 | -0.010055 | 0.054841 | -0.22823 | -0.0043924 | 0.015558 | 0.019831 | 0.035465 | 0.0041449 | 2.2811 | 5.4683 | 0.77448 | 120.5004 | 120.2933 | 120.2112 | -0.14548 | 0.010205 | -0.031692 | -0.088402 | -0.066582 | -0.041237 | -0.005985 | -0.15957 | 0.014739 | 0.076467 | 2.4413 | 0.93469 | 0.91995 | -0.1306 | -0.21265 | 0.000647 | -120.4905 | 0.17042 | 0.071815 | 0.071168 | -120.4651 | -120.4299 | 120.6606 | 120.4535 | 120.3715 | 5.6285 | -120.5694 | 0.093635 | 0.11898 | 0.15423 | 0.12853 | -120.5835
2059.7656 | 120.6573 | -0.16937 | 120.4514 | 1.4211e-13 | -0.035643 | 0.0012649 | 0.059945 | -0.010696 | 0.054627 | -0.23586 | -0.0043924 | 0.015131 | 0.020258 | 0.036106 | 0.0039313 | 2.3223 | 5.4316 | 0.78821 | 120.5141 | 120.307 | 120.2158 | -0.16379 | -0.003531 | -0.031692 | -0.083823 | -0.071161 | -0.036658 | 0.003172 | -0.15957 | 0.005579 | 0.062736 | 2.4917 | 0.95758 | 0.952 | -0.14433 | -0.23554 | 0.009803 | -120.5225 | 0.16584 | 0.08555 | 0.075747 | -120.488 | -120.4482 | 120.6835 | 120.4764 | 120.3852 | 5.601 | -120.6151 | 0.098212 | 0.13271 | 0.17255 | 0.13768 | -120.6109
2061.4531 | 120.7077 | -0.14191 | 120.4651 | 1.4211e-13 | -0.035429 | 0.0014787 | 0.059731 | -0.010055 | 0.054627 | -0.22823 | -0.004606 | 0.015345 | 0.020044 | 0.035893 | 0.0041449 | 2.3635 | 5.4042 | 0.8111 | 120.537 | 120.3345 | 120.2479 | -0.12716 | 0.010205 | -0.031692 | -0.083823 | -0.066582 | -0.041237 | -0.005985 | -0.16415 | 0.014745 | 0.071895 | 2.5054 | 0.95301 | 0.93827 | -0.13059 | -0.21722 | -0.022242 | -120.5317 | 0.15211 | 0.058084 | 0.080326 | -120.5063 | -120.4711 | 120.6789 | 120.4764 | 120.3898 | 5.5461 | -120.5922 | 0.075325 | 0.10067 | 0.13592 | 0.11022 | -120.6292
2063.1875 | 120.7123 | -0.16022 | 120.488 | 1.4211e-13 | -0.035857 | 0.0019059 | 0.060158 | -0.0098414 | 0.054841 | -0.2206 | -0.0043924 | 0.015558 | 0.020258 | 0.035893 | 0.0039313 | 2.391 | 5.3538 | 0.82026 | 120.5461 | 120.3391 | 120.257 | -0.1409 | 0.005626 | -0.031692 | -0.088402 | -0.066582 | -0.041237 | -0.005985 | -0.15957 | 0.019318 | 0.058163 | 2.5512 | 0.98048 | 0.96116 | -0.1489 | -0.23095 | 0.000647 | -120.5546 | 0.16584 | 0.071815 | 0.071168 | -120.5292 | -120.494 | 120.7064 | 120.4993 | 120.4172 | 5.514 | -120.6289 | 0.093635 | 0.11898 | 0.15423 | 0.12853 | -120.6475
2064.9219 | 120.7626 | -0.13275 | 120.4971 | 1.4211e-13 | -0.035643 | 0.0016923 | 0.060372 | -0.010269 | 0.055055 | -0.23586 | -0.0041788 | 0.015345 | 0.020044 | 0.035893 | 0.0043585 | 2.4459 | 5.3309 | 0.84773 | 120.5828 | 120.3711 | 120.2799 | -0.13632 | 0.005626 | -0.027113 | -0.088402 | -0.066582 | -0.041237 | -0.001407 | -0.16415 | -0.003569 | 0.085636 | 2.5787 | 0.98048 | 0.98405 | -0.126 | -0.21721 | -0.031398 | -120.5637 | 0.13838 | 0.044349 | 0.075747 | -120.5384 | -120.4985 | 120.7155 | 120.5039 | 120.4127 | 5.4637 | -120.6335 | 0.066169 | 0.091514 | 0.13134 | 0.10564 | -120.6613
2066.6719 | 120.6757 | -0.17853 | 120.5154 | 1.4211e-13 | -0.035643 | 0.0014787 | 0.059945 | -0.0098414 | 0.055055 | -0.24349 | -0.004606 | 0.015345 | 0.019831 | 0.035679 | 0.0039313 | 2.5283 | 5.276 | 0.8752 | 120.569 | 120.3528 | 120.2753 | -0.13632 | 0.010205 | -0.022535 | -0.083823 | -0.057425 | -0.036658 | 0.003172 | -0.16415 | 0.042208 | 0.053589 | 2.7068 | 1.0537 | 1.0115 | -0.16263 | -0.2401 | 0.014379 | -120.5729 | 0.18873 | 0.094705 | 0.080326 | -120.5521 | -120.5123 | 120.7476 | 120.5313 | 120.4539 | 5.4545 | -120.6518 | 0.1211 | 0.14187 | 0.1817 | 0.15599 | -120.6796
2068.4219 | 120.7077 | -0.19226 | 120.5658 | 1.4211e-13 | -0.035216 | 0.0019059 | 0.060158 | -0.010269 | 0.055055 | -0.22823 | -0.004606 | 0.015345 | 0.020258 | 0.036106 | 0.0037175 | 2.5466 | 5.2393 | 0.88893 | 120.5919 | 120.3803 | 120.2982 | -0.13174 | 0.001048 | -0.031692 | -0.079245 | -0.071161 | -0.036658 | -0.005985 | -0.15957 | 0.06052 | 0.026127 | 2.7389 | 1.0812 | 1.0207 | -0.18551 | -0.26756 | 0.032691 | -120.637 | 0.19331 | 0.11302 | 0.080325 | -120.6025 | -120.5718 | 120.7842 | 120.5725 | 120.4905 | 5.4316 | -120.6975 | 0.1211 | 0.1556 | 0.18628 | 0.16057 | -120.7254
2070.1094 | 120.694 | -0.17853 | 120.5383 | 1.4211e-13 | -0.035643 | 0.0016923 | 0.060158 | -0.010269 | 0.055055 | -0.23586 | -0.004606 | 0.015986 | 0.020472 | 0.035679 | 0.0043585 | 2.5878 | 5.1935 | 0.90725 | 120.6011 | 120.3986 | 120.312 | -0.15006 | 0.005626 | -0.027113 | -0.074666 | -0.062004 | -0.03208 | -0.001407 | -0.16415 | 0.028471 | 0.06275 | 2.7664 | 1.0858 | 1.0573 | -0.13973 | -0.22636 | 0.014379 | -120.6003 | 0.18415 | 0.10386 | 0.089483 | -120.5704 | -120.5397 | 120.7796 | 120.5771 | 120.4905 | 5.3721 | -120.6884 | 0.11652 | 0.14645 | 0.17712 | 0.15141 | -120.7025
2071.875 | 120.7031 | -0.20142 | 120.5475 | 1.4211e-13 | -0.035429 | 0.0016923 | 0.060372 | -0.0098414 | 0.054841 | -0.23586 | -0.0043924 | 0.015345 | 0.020044 | 0.035893 | 0.0039313 | 2.6336 | 5.1478 | 0.93472 | 120.624 | 120.4032 | 120.3257 | -0.13174 | 0.014784 | -0.027113 | -0.088402 | -0.071161 | -0.03208 | -0.005985 | -0.16415 | 0.069675 | 0.076487 | 2.835 | 1.1361 | 1.0665 | -0.1443 | -0.22178 | 0.037267 | -120.6186 | 0.2162 | 0.11301 | 0.075747 | -120.5796 | -120.5535 | 120.8254 | 120.6046 | 120.5271 | 5.3492 | -120.6792 | 0.13026 | 0.16934 | 0.19543 | 0.1743 | -120.7116
2073.5469 | 120.3094 | -0.19226 | 120.2087 | 1.4211e-13 | -0.035429 | 0.0014787 | 0.059945 | -0.010055 | 0.054414 | -0.22823 | -0.0043924 | 0.015558 | 0.020044 | 0.036106 | 0.0039313 | 1.8141 | 4.5022 | 0.028217 | 119.0582 | 118.9013 | 118.7232 | -1.0338 | 0.010205 | -0.031692 | -0.079245 | -0.062004 | -0.027501 | -0.001407 | -0.16415 | -0.84153 | -1.1506 | 2.0063 | 0.22048 | 1.062 | -1.3074 | -1.4855 | 0.028112 | -120.2707 | 0.20247 | 0.11302 | 0.084904 | -120.2362 | -120.2101 | 119.2504 | 119.0936 | 118.9155 | 4.6944 | -121.2425 | 0.13026 | 0.16476 | 0.19085 | 0.16057 | -120.3729
2075.2969 | 120.7214 | -0.14191 | 120.4559 | 1.4211e-13 | -0.035429 | 0.0019059 | 0.060158 | -0.0098414 | 0.055268 | -0.23586 | -0.004606 | 0.015345 | 0.020044 | 0.03632 | 0.0041449 | 2.771 | 5.0653 | 0.97134 | 120.5599 | 120.3528 | 120.2708 | -0.12716 | 0.001048 | -0.031692 | -0.083823 | -0.066582 | -0.03208 | -0.001407 | -0.16415 | 0.014745 | 0.10394 | 2.9129 | 1.1132 | 1.0985 | -0.10312 | -0.18517 | -0.022242 | -120.5225 | 0.14295 | 0.058084 | 0.080326 | -120.488 | -120.4573 | 120.7018 | 120.4947 | 120.4127 | 5.2072 | -120.5831 | 0.075325 | 0.10983 | 0.1405 | 0.11022 | -120.6201
2076.9844 | 120.7443 | -0.16479 | 120.5338 | 1.4211e-13 | -0.035216 | 0.0016923 | 0.060586 | -0.010055 | 0.055055 | -0.22823 | -0.004606 | 0.015558 | 0.019831 | 0.03632 | 0.0039313 | 2.8168 | 5.0287 | 0.99881 | 120.6057 | 120.3894 | 120.3074 | -0.13174 | 0.005626 | -0.031692 | -0.092981 | -0.066582 | -0.03208 | 0.003172 | -0.16415 | 0.033054 | 0.071906 | 2.9816 | 1.1636 | 1.1306 | -0.14431 | -0.22636 | 0.000646 | -120.6003 | 0.17042 | 0.071814 | 0.071168 | -120.5658 | -120.5306 | 120.7705 | 120.5542 | 120.4722 | 5.1935 | -120.6655 | 0.098213 | 0.13271 | 0.16797 | 0.1331 | -120.6979
2078.7188 | 120.7993 | -0.14648 | 120.5338 | 1.4211e-13 | -0.035429 | 0.0019059 | 0.060158 | -0.010055 | 0.055268 | -0.23586 | -0.0043924 | 0.015345 | 0.019831 | 0.03632 | 0.0041449 | 2.8671 | 4.9646 | 1.0125 | 120.624 | 120.4123 | 120.3303 | -0.13632 | 0.010205 | -0.031692 | -0.083823 | -0.066582 | -0.027501 | -0.005985 | -0.15957 | 0.010164 | 0.09022 | 3.0136 | 1.159 | 1.1489 | -0.12141 | -0.20347 | -0.013086 | -120.6003 | 0.15669 | 0.062661 | 0.075747 | -120.5613 | -120.5397 | 120.7705 | 120.5588 | 120.4768 | 5.1111 | -120.6701 | 0.079902 | 0.11898 | 0.1405 | 0.11479 | -120.6933
2080.4062 | 120.6848 | -0.20599 | 120.5841 | 1.4211e-13 | -0.035216 | 0.0021197 | 0.060158 | -0.0098414 | 0.055482 | -0.2206 | -0.004606 | 0.015558 | 0.019831 | 0.036106 | 0.0041449 | 2.9266 | 4.9371 | 1.0492 | 120.6469 | 120.4352 | 120.3486 | -0.12716 | 0.005626 | -0.022535 | -0.079245 | -0.057425 | -0.027501 | -0.005985 | -0.16415 | 0.078832 | 0.062758 | 3.1326 | 1.2552 | 1.1763 | -0.14887 | -0.23551 | 0.041845 | -120.6415 | 0.21162 | 0.12675 | 0.084904 | -120.6116 | -120.5901 | 120.8529 | 120.6412 | 120.5546 | 5.1431 | -120.7113 | 0.14857 | 0.17849 | 0.20001 | 0.18346 | -120.7483
2082.1562 | 120.7214 | -0.21515 | 120.6207 | 1.4211e-13 | -0.035002 | 0.0021197 | 0.060372 | -0.0098414 | 0.055482 | -0.22823 | -0.0043924 | 0.015558 | 0.020258 | 0.03632 | 0.0037175 | 2.9312 | 4.8868 | 1.0492 | 120.6423 | 120.4307 | 120.3532 | -0.14548 | 0.010205 | -0.031692 | -0.083823 | -0.062004 | -0.03208 | -0.001407 | -0.16873 | 0.069671 | 0.021558 | 3.1464 | 1.2643 | 1.1947 | -0.19007 | -0.26755 | 0.046421 | -120.6827 | 0.22535 | 0.13133 | 0.084905 | -120.6528 | -120.6221 | 120.8574 | 120.6458 | 120.5683 | 5.1019 | -120.7662 | 0.15315 | 0.18307 | 0.21374 | 0.18346 | -120.7895
2083.8906 | 120.7672 | -0.15106 | 120.575 | 1.4211e-13 | -0.034788 | 0.0025471 | 0.060158 | -0.0098414 | 0.055268 | -0.23586 | -0.0043924 | 0.015558 | 0.019831 | 0.036106 | 0.0039313 | 3.0045 | 4.8501 | 1.1041 | 120.6743 | 120.4627 | 120.3852 | -0.14548 | 0.001048 | -0.036271 | -0.088402 | -0.057425 | -0.027501 | -0.001407 | -0.15957 | 0.005584 | 0.099383 | 3.1555 | 1.2552 | 1.2496 | -0.11225 | -0.18973 | -0.008508 | -120.6324 | 0.15211 | 0.06266 | 0.071168 | -120.6025 | -120.5764 | 120.8254 | 120.6138 | 120.5363 | 5.0012 | -120.7204 | 0.093637 | 0.12356 | 0.14966 | 0.11479 | -120.7345
2085.5781 | 120.7718 | -0.19226 | 120.6299 | 1.4211e-13 | -0.035216 | 0.0021197 | 0.061013 | -0.0098414 | 0.055696 | -0.2206 | -0.003965 | 0.015772 | 0.019617 | 0.036106 | 0.0041449 | 3.0686 | 4.8227 | 1.1316 | 120.7018 | 120.481 | 120.399 | -0.13174 | 0.001048 | -0.027113 | -0.092981 | -0.066582 | -0.027501 | -0.005985 | -0.15957 | 0.06052 | 0.071922 | 3.2608 | 1.3238 | 1.2633 | -0.14886 | -0.23092 | 0.032691 | -120.6965 | 0.19331 | 0.09928 | 0.066589 | -120.6574 | -120.6359 | 120.8941 | 120.6733 | 120.5912 | 5.0149 | -120.7616 | 0.12568 | 0.16476 | 0.18628 | 0.16515 | -120.7895
2087.3281 | 120.7718 | -0.17853 | 120.639 | 1.4211e-13 | -0.034788 | 0.0025471 | 0.060799 | -0.0098414 | 0.055696 | -0.23586 | -0.0041788 | 0.015772 | 0.019831 | 0.036106 | 0.0037175 | 3.1281 | 4.7677 | 1.1545 | 120.7018 | 120.4993 | 120.4219 | -0.12258 | 0.005626 | -0.036271 | -0.083823 | -0.062004 | -0.027501 | -0.005985 | -0.16415 | 0.055945 | 0.062767 | 3.3066 | 1.333 | 1.2771 | -0.1397 | -0.21718 | 0.014379 | -120.701 | 0.18415 | 0.094705 | 0.080326 | -120.6665 | -120.645 | 120.8803 | 120.6779 | 120.6004 | 4.9463 | -120.7616 | 0.11652 | 0.15103 | 0.17254 | 0.14226 | -120.8032
2089.0156 | 120.7672 | -0.20599 | 120.6665 | 1.4211e-13 | -0.034788 | 0.0023333 | 0.061013 | -0.010055 | 0.056123 | -0.23586 | -0.0048196 | 0.015345 | 0.020044 | 0.03632 | 0.0039313 | 3.1922 | 4.7311 | 1.1865 | 120.7247 | 120.5085 | 120.4264 | -0.13174 | 0.005626 | -0.027113 | -0.079245 | -0.062004 | -0.03208 | -0.001407 | -0.16415 | 0.074253 | 0.058193 | 3.3982 | 1.3925 | 1.3183 | -0.15801 | -0.24007 | 0.041845 | -120.7285 | 0.21162 | 0.12675 | 0.084904 | -120.6986 | -120.6679 | 120.9307 | 120.7145 | 120.6324 | 4.9371 | -120.7982 | 0.14399 | 0.17391 | 0.20459 | 0.17888 | -120.8307
2090.7656 | 120.7809 | -0.21057 | 120.6848 | 1.4211e-13 | -0.034574 | 0.0023333 | 0.061227 | -0.0098414 | 0.055696 | -0.22823 | -0.0043924 | 0.015558 | 0.019831 | 0.036747 | 0.0037175 | 3.2563 | 4.6853 | 1.214 | 120.7293 | 120.5222 | 120.4264 | -0.13174 | 0.010205 | -0.022535 | -0.079245 | -0.066582 | -0.036658 | -0.001407 | -0.16415 | 0.07883 | 0.044461 | 3.4669 | 1.4246 | 1.3457 | -0.16258 | -0.25838 | 0.046422 | -120.7514 | 0.22078 | 0.13133 | 0.084904 | -120.7215 | -120.6862 | 120.9398 | 120.7328 | 120.637 | 4.8959 | -120.8166 | 0.14399 | 0.17391 | 0.20916 | 0.18804 | -120.849
2092.4375 | 120.7993 | -0.20599 | 120.6985 | 1.4211e-13 | -0.034788 | 0.0029743 | 0.060586 | -0.0098414 | 0.056123 | -0.22823 | -0.004606 | 0.015558 | 0.019617 | 0.03632 | 0.0037175 | 3.3341 | 4.6578 | 1.246 | 120.7476 | 120.536 | 120.4447 | -0.1409 | 0.001048 | -0.036271 | -0.083823 | -0.062004 | -0.036658 | -0.001407 | -0.16415 | 0.065095 | 0.049041 | 3.5401 | 1.452 | 1.3869 | -0.16258 | -0.2538 | 0.041845 | -120.7606 | 0.20704 | 0.12217 | 0.080326 | -120.7352 | -120.7 | 120.9536 | 120.742 | 120.6507 | 4.8638 | -120.8394 | 0.14399 | 0.16934 | 0.20459 | 0.16972 | -120.8627
2094.1719 | 120.8542 | -0.21057 | 120.6985 | 1.4211e-13 | -0.034788 | 0.0025471 | 0.060799 | -0.0098414 | 0.05655 | -0.23586 | -0.004606 | 0.015772 | 0.019831 | 0.036106 | 0.0039313 | 3.3845 | 4.6075 | 1.2369 | 120.743 | 120.5177 | 120.431 | -0.18211 | -0.003531 | -0.031692 | -0.088402 | -0.066582 | -0.041237 | -0.001407 | -0.16873 | 0.028462 | 0.044463 | 3.595 | 1.4475 | 1.419 | -0.18089 | -0.26754 | 0.041843 | -120.7651 | 0.20704 | 0.12217 | 0.080326 | -120.7398 | -120.7 | 120.9536 | 120.7282 | 120.6416 | 4.8181 | -120.8807 | 0.14399 | 0.16933 | 0.20916 | 0.17888 | -120.8673
2095.9062 | 120.8908 | -0.17853 | 120.694 | 1.4211e-13 | -0.034361 | 0.0023333 | 0.06144 | -0.010055 | 0.056123 | -0.21297 | -0.004606 | 0.015558 | 0.019831 | 0.036534 | 0.0039313 | 3.4806 | 4.58 | 1.2781 | 120.7613 | 120.5543 | 120.4768 | -0.15464 | -0.00811 | -0.031692 | -0.088402 | -0.062004 | -0.036658 | -0.010564 | -0.16873 | 0.023892 | 0.067354 | 3.6591 | 1.4566 | 1.4327 | -0.13969 | -0.21717 | 0.0098 | -120.756 | 0.17042 | 0.090126 | 0.080326 | -120.7306 | -120.7045 | 120.9399 | 120.7328 | 120.6553 | 4.7585 | -120.8486 | 0.11652 | 0.14187 | 0.16796 | 0.14684 | -120.8627
2097.5781 | 120.932 | -0.16479 | 120.6985 | 1.4211e-13 | -0.034147 | 0.0029743 | 0.061227 | -0.0098414 | 0.055909 | -0.2206 | -0.0043924 | 0.015345 | 0.020044 | 0.03632 | 0.0037175 | 3.5447 | 4.5342 | 1.3056 | 120.7705 | 120.5634 | 120.4814 | -0.15006 | 0.001048 | -0.027113 | -0.088402 | -0.066582 | -0.041237 | -0.010564 | -0.15957 | 0.014738 | 0.071933 | 3.7095 | 1.4704 | 1.4556 | -0.13511 | -0.21717 | 0.005225 | -120.7651 | 0.16584 | 0.076393 | 0.071168 | -120.7398 | -120.7091 | 120.9353 | 120.7282 | 120.6462 | 4.699 | -120.8486 | 0.098213 | 0.12356 | 0.15423 | 0.13768 | -120.8581
2099.3125 | 118.1122 | -23.1949 | 94.3771 | 1.4211e-13 | -0.034574 | 0.0029743 | 0.060799 | -0.0096276 | 0.056123 | -0.23586 | -0.004606 | 0.015345 | 0.019831 | 0.03632 | 0.0035039 | 2.1895 | 3.6368 | 0.005325 | 119.168 | 118.9059 | 118.8789 | -1.6977 | 0.001048 | -0.027113 | -0.092981 | -0.062004 | -0.036658 | -0.005985 | -0.16873 | 21.4972 | 24.7909 | 25.3844 | 23.2002 | 1.7031 | 24.5287 | 24.5017 | 23.0262 | -94.4391 | 23.1959 | 23.1019 | 0.075747 | -94.4138 | -94.3831 | 142.3629 | 142.1008 | 142.0738 | 26.8317 | -96.0749 | 23.1329 | 23.1582 | 23.1889 | 23.1678 | -94.5459
2101.0469 | 120.9137 | -0.16479 | 120.639 | 1.4211e-13 | -0.034147 | 0.0031881 | 0.06144 | -0.0096276 | 0.05655 | -0.2206 | -0.0043924 | 0.015558 | 0.019403 | 0.036534 | 0.0037175 | 3.7599 | 4.4655 | 1.4154 | 120.743 | 120.536 | 120.4493 | -0.13174 | 0.005626 | -0.036271 | -0.088402 | -0.066582 | -0.036658 | -0.005985 | -0.16873 | 0.033054 | 0.10397 | 3.9247 | 1.5802 | 1.5472 | -0.10307 | -0.18971 | -0.003933 | -120.7056 | 0.17042 | 0.076393 | 0.080326 | -120.6757 | -120.645 | 120.9078 | 120.7008 | 120.6141 | 4.6303 | -120.7708 | 0.098213 | 0.12814 | 0.15881 | 0.12852 | -120.8078
2102.7812 | 120.9137 | -0.15106 | 120.6985 | 1.4211e-13 | -0.03372 | 0.0034017 | 0.06144 | -0.009414 | 0.05655 | -0.24349 | -0.0043924 | 0.015345 | 0.019617 | 0.036106 | 0.0037175 | 3.8148 | 4.4289 | 1.4566 | 120.7796 | 120.568 | 120.486 | -0.13174 | 0.001048 | -0.031692 | -0.097559 | -0.066582 | -0.045815 | -0.005985 | -0.16415 | 0.019321 | 0.08109 | 3.9659 | 1.6077 | 1.5884 | -0.13053 | -0.21259 | -0.013087 | -120.7651 | 0.15211 | 0.053503 | 0.06659 | -120.7444 | -120.7045 | 120.9307 | 120.7191 | 120.637 | 4.58 | -120.8303 | 0.08448 | 0.10525 | 0.14508 | 0.11937 | -120.8627
2104.4531 | 120.845 | -0.21057 | 120.7306 | 1.4211e-13 | -0.034147 | 0.0031881 | 0.06144 | -0.0098414 | 0.05655 | -0.22823 | -0.004606 | 0.015772 | 0.019617 | 0.036534 | 0.0037175 | 3.9018 | 4.3923 | 1.5116 | 120.798 | 120.5818 | 120.5043 | -0.12716 | 0.001048 | -0.036271 | -0.088402 | -0.066582 | -0.03208 | -0.001407 | -0.16415 | 0.083409 | 0.06736 | 4.1124 | 1.7222 | 1.6387 | -0.14883 | -0.22632 | 0.046422 | -120.7972 | 0.21162 | 0.12217 | 0.075747 | -120.7627 | -120.732 | 121.0085 | 120.7923 | 120.7148 | 4.6029 | -120.8578 | 0.14399 | 0.17849 | 0.20916 | 0.1743 | -120.8947
2106.2031 | 120.8496 | -0.19226 | 120.7626 | 1.4211e-13 | -0.03372 | 0.0031881 | 0.06144 | -0.0098414 | 0.05655 | -0.22823 | -0.0048196 | 0.015558 | 0.019831 | 0.036534 | 0.0037175 | 4.0071 | 4.3602 | 1.5528 | 120.8163 | 120.6092 | 120.518 | -0.12716 | 0.005626 | -0.031692 | -0.088402 | -0.075739 | -0.045815 | -0.005985 | -0.17788 | 0.065099 | 0.05363 | 4.1994 | 1.745 | 1.6799 | -0.1534 | -0.24463 | 0.014376 | -120.8384 | 0.19789 | 0.10386 | 0.089483 | -120.8084 | -120.7686 | 121.0085 | 120.8015 | 120.7103 | 4.5525 | -120.8898 | 0.11652 | 0.14645 | 0.18628 | 0.16057 | -120.9405
2107.9531 | 120.8679 | -0.18768 | 120.7626 | 1.4211e-13 | -0.033292 | 0.0031881 | 0.06144 | -0.0098414 | 0.056764 | -0.22823 | -0.0043924 | 0.015558 | 0.019831 | 0.036534 | 0.0039313 | 4.1124 | 4.3328 | 1.6077 | 120.83 | 120.6138 | 120.5272 | -0.12716 | 0.005626 | -0.040849 | -0.092981 | -0.066582 | -0.045815 | -0.015142 | -0.16873 | 0.060521 | 0.067365 | 4.3001 | 1.7954 | 1.7349 | -0.14882 | -0.23547 | 0.018955 | -120.8292 | 0.19331 | 0.094702 | 0.075747 | -120.8084 | -120.7778 | 121.0177 | 120.8015 | 120.7148 | 4.5204 | -120.8898 | 0.1211 | 0.14187 | 0.17254 | 0.14683 | -120.9314
2109.6406 | 120.9137 | -0.19684 | 120.7993 | 1.4211e-13 | -0.033292 | 0.0036155 | 0.061227 | -0.0096276 | 0.05655 | -0.2206 | -0.0043924 | 0.015558 | 0.020044 | 0.036534 | 0.0039313 | 4.2177 | 4.2961 | 1.6443 | 120.8437 | 120.6275 | 120.5363 | -0.13174 | -0.003531 | -0.031692 | -0.092981 | -0.062004 | -0.050394 | -0.010564 | -0.16873 | 0.065097 | 0.04448 | 4.4146 | 1.8412 | 1.7761 | -0.17171 | -0.26294 | 0.02811 | -120.8613 | 0.19331 | 0.10386 | 0.075747 | -120.8496 | -120.8098 | 121.0406 | 120.8244 | 120.7332 | 4.493 | -120.931 | 0.13483 | 0.14644 | 0.18627 | 0.16515 | -120.968
2111.375 | 120.9549 | -0.16937 | 120.7672 | 1.4211e-13 | -0.033079 | 0.0038291 | 0.06144 | -0.0092004 | 0.056764 | -0.22823 | -0.003965 | 0.015558 | 0.019831 | 0.03632 | 0.0039313 | 4.3368 | 4.2595 | 1.6718 | 120.8529 | 120.6413 | 120.5546 | -0.13174 | -0.003531 | -0.031692 | -0.088402 | -0.066582 | -0.041237 | -0.010564 | -0.16873 | 0.037632 | 0.085679 | 4.5062 | 1.8412 | 1.8036 | -0.12593 | -0.21258 | 0.000645 | -120.8338 | 0.16584 | 0.080971 | 0.080326 | -120.8084 | -120.7778 | 121.0223 | 120.8107 | 120.724 | 4.4289 | -120.899 | 0.10279 | 0.12814 | 0.15881 | 0.13768 | -120.9359
2113.1094 | 120.9091 | -0.20599 | 120.7901 | 1.4211e-13 | -0.032865 | 0.0040427 | 0.061868 | -0.0096276 | 0.056764 | -0.22823 | -0.0043924 | 0.015345 | 0.019831 | 0.03632 | 0.0039313 | 4.4467 | 4.2137 | 1.7039 | 120.8437 | 120.6367 | 120.5455 | -0.15921 | -0.00811 | -0.036271 | -0.092981 | -0.066582 | -0.041237 | -0.005985 | -0.16415 | 0.046779 | 0.053635 | 4.6527 | 1.9099 | 1.8631 | -0.15339 | -0.24462 | 0.041845 | -120.8567 | 0.19788 | 0.11301 | 0.071168 | -120.8313 | -120.7961 | 121.0497 | 120.8427 | 120.7515 | 4.4197 | -120.9493 | 0.13941 | 0.16476 | 0.20001 | 0.16972 | -120.9542
2114.8594 | 121.0327 | -0.15106 | 120.7809 | 1.4211e-13 | -0.032865 | 0.0038291 | 0.061868 | -0.009414 | 0.056764 | -0.22823 | -0.004606 | 0.015345 | 0.019617 | 0.036747 | 0.0039313 | 4.5794 | 4.2 | 1.7725 | 120.8804 | 120.6596 | 120.5729 | -0.12716 | -0.00811 | -0.040849 | -0.092981 | -0.075739 | -0.045815 | -0.005985 | -0.17331 | 0.0239 | 0.099417 | 4.7305 | 1.9236 | 1.8997 | -0.12135 | -0.208 | -0.022244 | -120.8567 | 0.14295 | 0.058081 | 0.080325 | -120.8268 | -120.7869 | 121.0314 | 120.8107 | 120.724 | 4.351 | -120.9081 | 0.075323 | 0.10525 | 0.14508 | 0.11021 | -120.9543
2116.5469 | 121.0464 | -0.15106 | 120.7764 | 1.4211e-13 | -0.032438 | 0.0042565 | 0.062081 | -0.0092004 | 0.057191 | -0.22823 | -0.0043924 | 0.015345 | 0.019617 | 0.036534 | 0.0041449 | 4.7168 | 4.1771 | 1.8275 | 120.8758 | 120.6642 | 120.5775 | -0.12258 | 0.005626 | -0.036271 | -0.092981 | -0.066582 | -0.050394 | -0.010564 | -0.17788 | 0.028479 | 0.099416 | 4.8678 | 1.9785 | 1.9501 | -0.11219 | -0.19884 | -0.026823 | -120.8429 | 0.15669 | 0.058081 | 0.084904 | -120.8268 | -120.7869 | 121.0268 | 120.8152 | 120.7286 | 4.3282 | -120.8989 | 0.08448 | 0.10067 | 0.1405 | 0.11479 | -120.9543
2118.2812 | 121.0648 | -0.15564 | 120.7809 | 1.4211e-13 | -0.032438 | 0.0040427 | 0.062081 | -0.009414 | 0.057191 | -0.23586 | -0.0050332 | 0.015772 | 0.019403 | 0.036747 | 0.0037175 | 4.8541 | 4.1496 | 1.9007 | 120.8895 | 120.6779 | 120.5913 | -0.12716 | -0.012689 | -0.045428 | -0.092981 | -0.066582 | -0.041237 | -0.010564 | -0.17788 | 0.028478 | 0.10857 | 5.0098 | 2.0564 | 2.0279 | -0.10303 | -0.18968 | -0.022245 | -120.8475 | 0.14295 | 0.062659 | 0.084904 | -120.8222 | -120.7915 | 121.0452 | 120.8336 | 120.7469 | 4.3053 | -120.9081 | 0.089058 | 0.1144 | 0.14508 | 0.11021 | -120.9588
2120.0156 | 121.0373 | -0.14648 | 120.8176 | 1.4211e-13 | -0.032224 | 0.0046839 | 0.062295 | -0.009414 | 0.057191 | -0.22823 | -0.0041788 | 0.015558 | 0.019403 | 0.036961 | 0.0039313 | 5.0052 | 4.1359 | 1.9648 | 120.9078 | 120.6871 | 120.605 | -0.13174 | -0.012689 | -0.040849 | -0.10672 | -0.071161 | -0.050394 | -0.010564 | -0.17331 | 0.014743 | 0.090266 | 5.1517 | 2.1113 | 2.0966 | -0.13049 | -0.21257 | -0.026822 | -120.8887 | 0.13379 | 0.039767 | 0.066589 | -120.868 | -120.8281 | 121.0543 | 120.8336 | 120.7515 | 4.2824 | -120.9493 | 0.075323 | 0.09609 | 0.13592 | 0.10564 | -120.9909
2121.7031 | 121.1014 | -0.13275 | 120.8176 | 1.4211e-13 | -0.03201 | 0.0046839 | 0.062295 | -0.009414 | 0.057191 | -0.22823 | -0.004606 | 0.015345 | 0.019403 | 0.036747 | 0.0037175 | 5.1609 | 4.1221 | 2.0243 | 120.9124 | 120.6962 | 120.605 | -0.12716 | -0.00811 | -0.036271 | -0.097559 | -0.075739 | -0.041237 | -0.015142 | -0.17331 | 0.005589 | 0.094844 | 5.2936 | 2.1571 | 2.1515 | -0.12134 | -0.21257 | -0.040555 | -120.8933 | 0.12464 | 0.035192 | 0.075747 | -120.8588 | -120.8327 | 121.0452 | 120.829 | 120.7377 | 4.2549 | -120.9447 | 0.057012 | 0.091514 | 0.11761 | 0.09648 | -120.9909
2123.4375 | 120.9595 | -0.18768 | 120.8588 | 1.4211e-13 | -0.031797 | 0.0046839 | 0.062509 | -0.0092004 | 0.057618 | -0.22823 | -0.004606 | 0.015345 | 0.019403 | 0.036534 | 0.0035039 | 5.3303 | 4.1084 | 2.1068 | 120.9261 | 120.7054 | 120.6187 | -0.13632 | -0.00811 | -0.036271 | -0.092981 | -0.075739 | -0.045815 | -0.010564 | -0.17331 | 0.051363 | 0.067381 | 5.518 | 2.2944 | 2.2431 | -0.15338 | -0.24003 | 0.014377 | -120.9345 | 0.17957 | 0.094702 | 0.080325 | -120.9046 | -120.8693 | 121.1138 | 120.8931 | 120.8064 | 4.2961 | -120.9951 | 0.11194 | 0.14187 | 0.17712 | 0.15141 | -121.0321
2125.1719 | 120.9686 | -0.21057 | 120.8588 | 1.4211e-13 | -0.031156 | 0.0048975 | 0.062936 | -0.009414 | 0.057618 | -0.22823 | -0.0041788 | 0.015558 | 0.019831 | 0.036534 | 0.0039313 | 5.4814 | 4.0901 | 2.1663 | 120.9261 | 120.7191 | 120.6279 | -0.13174 | -0.00811 | -0.036271 | -0.097559 | -0.075739 | -0.050394 | -0.019721 | -0.17788 | 0.07883 | 0.067381 | 5.6919 | 2.3768 | 2.298 | -0.13964 | -0.23087 | 0.032686 | -120.9345 | 0.20246 | 0.11301 | 0.080326 | -120.9092 | -120.8785 | 121.1367 | 120.9297 | 120.8385 | 4.3007 | -120.9905 | 0.13483 | 0.16018 | 0.19085 | 0.1743 | -121.0367
2126.9219 | 120.9915 | -0.19684 | 120.8954 | 1.4211e-13 | -0.031369 | 0.0053249 | 0.062722 | -0.0092004 | 0.057832 | -0.22823 | -0.0048196 | 0.015345 | 0.019831 | 0.036534 | 0.0035039 | 5.6737 | 4.0901 | 2.2533 | 120.9399 | 120.7283 | 120.637 | -0.12716 | -0.00811 | -0.040849 | -0.097559 | -0.080318 | -0.054973 | -0.010564 | -0.16873 | 0.069676 | 0.044495 | 5.8705 | 2.4501 | 2.3804 | -0.1671 | -0.25834 | 0.02811 | -120.9757 | 0.18873 | 0.099279 | 0.071169 | -120.9504 | -120.906 | 121.1367 | 120.9251 | 120.8339 | 4.2869 | -121.0225 | 0.11652 | 0.14187 | 0.18627 | 0.15599 | -121.0641
2128.6094 | 121.1288 | -0.15106 | 120.845 | 1.4211e-13 | -0.030515 | 0.0055385 | 0.06315 | -0.009414 | 0.057832 | -0.22823 | -0.0043924 | 0.015558 | 0.019403 | 0.036534 | 0.0035039 | 5.8476 | 4.1038 | 2.3311 | 120.949 | 120.7374 | 120.6416 | -0.14548 | 0.001048 | -0.040849 | -0.097559 | -0.071161 | -0.045815 | -0.010564 | -0.16873 | 0.005584 | 0.10401 | 5.9987 | 2.4822 | 2.4766 | -0.10759 | -0.20341 | -0.017666 | -120.9162 | 0.15211 | 0.053503 | 0.071169 | -120.8908 | -120.8556 | 121.1001 | 120.8885 | 120.7927 | 4.2549 | -120.9905 | 0.079901 | 0.10525 | 0.1405 | 0.11021 | -121.0138
2130.3594 | 121.0144 | -0.22888 | 120.8862 | 1.4211e-13 | -0.030515 | 0.0059659 | 0.062936 | -0.0092004 | 0.058259 | -0.22823 | -0.0043924 | 0.015131 | 0.019403 | 0.03632 | 0.0032903 | 6.0354 | 4.113 | 2.4135 | 120.9582 | 120.7512 | 120.6508 | -0.13174 | -0.00811 | -0.040849 | -0.097559 | -0.071161 | -0.045815 | -0.015142 | -0.17331 | 0.097141 | 0.071964 | 6.2642 | 2.6424 | 2.5452 | -0.13505 | -0.23545 | 0.055576 | -120.9574 | 0.22077 | 0.13132 | 0.075747 | -120.932 | -120.9014 | 121.1871 | 120.9801 | 120.8797 | 4.3419 | -121.018 | 0.15772 | 0.18307 | 0.21374 | 0.18803 | -121.0595
2132.1094 | 121.1517 | -0.14648 | 120.8725 | 1.4211e-13 | -0.030301 | 0.0059659 | 0.063363 | -0.008773 | 0.058046 | -0.23586 | -0.004606 | 0.015558 | 0.019403 | 0.036534 | 0.0037175 | 6.2368 | 4.1221 | 2.5005 | 120.9628 | 120.7649 | 120.6599 | -0.1409 | -0.003531 | -0.040849 | -0.10214 | -0.071161 | -0.041237 | -0.015142 | -0.18246 | 0.005585 | 0.090275 | 6.3833 | 2.647 | 2.6414 | -0.10758 | -0.21256 | -0.03598 | -120.9437 | 0.14295 | 0.044346 | 0.080326 | -120.9137 | -120.8876 | 121.1093 | 120.9114 | 120.8064 | 4.2686 | -121.0134 | 0.075323 | 0.10525 | 0.13134 | 0.10564 | -121.055
2133.8594 | 121.0373 | -0.20142 | 120.9045 | 1.4211e-13 | -0.02966 | 0.0063933 | 0.063363 | -0.0089866 | 0.058473 | -0.23586 | -0.0050332 | 0.015131 | 0.01919 | 0.03632 | 0.0037175 | 6.4474 | 4.1313 | 2.5783 | 120.9811 | 120.7603 | 120.6737 | -0.13632 | -0.00811 | -0.045428 | -0.10672 | -0.075739 | -0.050394 | -0.019721 | -0.17331 | 0.065096 | 0.076545 | 6.6488 | 2.7797 | 2.7146 | -0.1442 | -0.23086 | 0.02811 | -120.9803 | 0.19331 | 0.094699 | 0.066589 | -120.9549 | -120.9243 | 121.1825 | 120.9618 | 120.8751 | 4.3327 | -121.0409 | 0.12568 | 0.15102 | 0.1817 | 0.15599 | -121.0778
2135.6094 | 121.1243 | -0.15564 | 120.8771 | 1.4211e-13 | -0.02966 | 0.0066069 | 0.063577 | -0.008773 | 0.058473 | -0.2206 | -0.004606 | 0.015131 | 0.01919 | 0.036747 | 0.0039313 | 6.6534 | 4.1359 | 2.6653 | 120.9857 | 120.7741 | 120.6737 | -0.12716 | -0.00811 | -0.040849 | -0.097559 | -0.075739 | -0.045815 | -0.019721 | -0.17331 | 0.028478 | 0.10859 | 6.8091 | 2.8209 | 2.7925 | -0.103 | -0.2034 | -0.017666 | -120.9528 | 0.14753 | 0.058081 | 0.075747 | -120.9229 | -120.8968 | 121.1413 | 120.9297 | 120.8293 | 4.2915 | -121.0042 | 0.079901 | 0.10983 | 0.13592 | 0.11479 | -121.0504
2137.2969 | 121.0556 | -0.20599 | 120.9137 | 1.4211e-13 | -0.029019 | 0.0066069 | 0.063577 | -0.0089866 | 0.058687 | -0.2206 | -0.004606 | 0.015345 | 0.019403 | 0.036534 | 0.0035039 | 6.8778 | 4.1725 | 2.7523 | 120.9902 | 120.7741 | 120.6874 | -0.13174 | -0.00811 | -0.050007 | -0.092981 | -0.075739 | -0.054973 | -0.015142 | -0.17788 | 0.074253 | 0.076547 | 7.0838 | 2.9583 | 2.884 | -0.13962 | -0.22628 | 0.028109 | -120.9894 | 0.19788 | 0.11301 | 0.084904 | -120.9687 | -120.9288 | 121.1962 | 120.9801 | 120.8934 | 4.3785 | -121.0454 | 0.13026 | 0.15102 | 0.19085 | 0.15599 | -121.0916
2139.0312 | 121.1609 | -0.16479 | 120.9045 | 1.4211e-13 | -0.028805 | 0.0072479 | 0.064005 | -0.008773 | 0.058687 | -0.2206 | -0.004606 | 0.015345 | 0.019831 | 0.03632 | 0.0039313 | 7.1204 | 4.1908 | 2.8576 | 120.9948 | 120.7878 | 120.7011 | -0.12716 | -0.003531 | -0.050007 | -0.10214 | -0.075739 | -0.050394 | -0.010564 | -0.17788 | 0.037633 | 0.09028 | 7.2852 | 3.0224 | 2.9848 | -0.11673 | -0.20339 | -0.01309 | -120.9803 | 0.16126 | 0.062657 | 0.075747 | -120.9549 | -120.9151 | 121.1596 | 120.9526 | 120.8659 | 4.3556 | -121.0317 | 0.089056 | 0.1144 | 0.15423 | 0.11479 | -121.0824
2140.7969 | 121.138 | -0.16937 | 120.9183 | 1.4211e-13 | -0.028378 | 0.0076753 | 0.064218 | -0.0085594 | 0.059114 | -0.22823 | -0.0043924 | 0.015345 | 0.019617 | 0.036961 | 0.0035039 | 7.3677 | 4.232 | 2.9537 | 121.004 | 120.7924 | 120.7011 | -0.12716 | -0.012689 | -0.045428 | -0.10214 | -0.075739 | -0.045815 | -0.015142 | -0.17788 | 0.042211 | 0.085704 | 7.537 | 3.1231 | 3.0809 | -0.12589 | -0.21712 | -0.008512 | -120.994 | 0.15668 | 0.067235 | 0.075747 | -120.9641 | -120.9334 | 121.1734 | 120.9618 | 120.8705 | 4.4014 | -121.0454 | 0.093634 | 0.12356 | 0.15423 | 0.12394 | -121.0962
2142.4844 | 117.9474 | -22.4075 | 95.2744 | 1.4211e-13 | -0.030301 | 0.0068205 | 0.061013 | -0.0064228 | 0.059541 | -0.22823 | -0.004606 | 0.015345 | 0.019403 | 0.036961 | 0.0037175 | -13.725 | -9.5633 | -17.4562 | 94.8293 | 94.6513 | 94.6214 | -22.9668 | 0.010205 | -0.008798 | -0.079245 | -0.048268 | -0.027501 | 0.003172 | -0.15499 | -0.55931 | -0.44502 | 8.6826 | 4.9513 | 5.5106 | -0.62305 | -0.65292 | 22.2525 | -95.3226 | 22.4177 | 22.3283 | 0.075746 | -95.3019 | -95.2712 | 117.2369 | 117.0588 | 117.029 | 12.8442 | -118.2412 | 22.3593 | 22.38 | 22.4107 | 22.3987 | -95.4293
2144.2188 | 120.8542 | -0.19684 | 120.7031 | 1.4211e-13 | -0.027523 | 0.0085301 | 0.064646 | -0.008773 | 0.0589 | -0.22823 | -0.0048196 | 0.015345 | 0.01919 | 0.036747 | 0.0035039 | 7.8759 | 4.2732 | 3.1872 | 120.7613 | 120.5451 | 120.4631 | -0.13632 | -0.00811 | -0.045428 | -0.10214 | -0.071161 | -0.054973 | -0.010564 | -0.17331 | 0.060518 | 0.058199 | 8.0727 | 3.3841 | 3.3236 | -0.158 | -0.24006 | 0.023532 | -120.7743 | 0.18873 | 0.0947 | 0.071168 | -120.7581 | -120.7137 | 120.9582 | 120.742 | 120.6599 | 4.4701 | -120.8394 | 0.12568 | 0.14187 | 0.18627 | 0.15141 | -120.8764
2145.9688 | 120.9869 | -0.17395 | 120.7626 | 1.4211e-13 | -0.027096 | 0.0087437 | 0.064859 | -0.0083458 | 0.058687 | -0.22823 | -0.0041788 | 0.015345 | 0.019403 | 0.037388 | 0.0037175 | 8.1643 | 4.3282 | 3.3017 | 120.8392 | 120.6321 | 120.5272 | -0.1409 | -0.003531 | -0.045428 | -0.10214 | -0.071161 | -0.041237 | -0.015142 | -0.16873 | 0.033051 | 0.076522 | 8.3383 | 3.4756 | 3.4426 | -0.13051 | -0.23547 | 0.005222 | -120.8338 | 0.17042 | 0.071812 | 0.06659 | -120.8039 | -120.7778 | 121.0131 | 120.8061 | 120.7011 | 4.5021 | -120.9035 | 0.10279 | 0.13271 | 0.15881 | 0.12852 | -120.9314
2147.6562 | 121.0007 | -0.17853 | 120.7809 | 1.4211e-13 | -0.026882 | 0.0091711 | 0.0655 | -0.008132 | 0.059328 | -0.22823 | -0.004606 | 0.015772 | 0.019617 | 0.036747 | 0.0035039 | 8.4482 | 4.3557 | 3.4253 | 120.8804 | 120.6596 | 120.5638 | -0.1409 | -0.00811 | -0.045428 | -0.10214 | -0.062004 | -0.045815 | -0.010564 | -0.17788 | 0.037629 | 0.099417 | 8.6267 | 3.6038 | 3.5662 | -0.12135 | -0.21715 | 0.000643 | -120.8429 | 0.17042 | 0.07639 | 0.075747 | -120.8268 | -120.7915 | 121.0589 | 120.8381 | 120.7423 | 4.5342 | -120.9218 | 0.11652 | 0.13271 | 0.16796 | 0.1331 | -120.9588
2149.3906 | 121.0648 | -0.15564 | 120.813 | 1.4211e-13 | -0.026455 | 0.0098121 | 0.0655 | -0.0083458 | 0.059541 | -0.23586 | -0.0043924 | 0.015772 | 0.019617 | 0.037175 | 0.0035039 | 8.7503 | 4.4106 | 3.5489 | 120.8987 | 120.6962 | 120.5913 | -0.13174 | -0.00811 | -0.036271 | -0.097559 | -0.075739 | -0.045815 | -0.010564 | -0.16873 | 0.023899 | 0.085687 | 8.906 | 3.7046 | 3.6807 | -0.11676 | -0.22173 | -0.013088 | -120.8887 | 0.14753 | 0.058081 | 0.071169 | -120.8588 | -120.8236 | 121.0543 | 120.8519 | 120.7469 | 4.5662 | -120.9447 | 0.079901 | 0.10983 | 0.14508 | 0.11937 | -120.9817
2151.125 | 121.0144 | -0.20599 | 120.8817 | 1.4211e-13 | -0.025814 | 0.010453 | 0.066141 | -0.008132 | 0.059969 | -0.22823 | -0.004606 | 0.015345 | 0.019617 | 0.036747 | 0.0032903 | 9.0663 | 4.4564 | 3.7 | 120.9216 | 120.71 | 120.6187 | -0.14548 | -0.00811 | -0.040849 | -0.097559 | -0.071161 | -0.041237 | -0.015142 | -0.16873 | 0.060516 | 0.039914 | 9.2722 | 3.906 | 3.8455 | -0.17168 | -0.26292 | 0.037266 | -120.9528 | 0.19788 | 0.10844 | 0.071169 | -120.9229 | -120.8968 | 121.1276 | 120.916 | 120.8247 | 4.6624 | -121.0271 | 0.13483 | 0.16476 | 0.19085 | 0.16515 | -121.0504
2152.875 | 121.0373 | -0.20142 | 120.8817 | 1.4211e-13 | -0.025173 | 0.011094 | 0.066141 | -0.008132 | 0.059969 | -0.23586 | -0.004606 | 0.015131 | 0.019617 | 0.036961 | 0.0037175 | 9.3822 | 4.5113 | 3.8373 | 120.9399 | 120.7329 | 120.637 | -0.1409 | -0.00811 | -0.036271 | -0.097559 | -0.075739 | -0.041237 | -0.005985 | -0.17331 | 0.060517 | 0.058228 | 9.5836 | 4.0388 | 3.9782 | -0.14879 | -0.24461 | 0.02811 | -120.9574 | 0.19331 | 0.10386 | 0.075747 | -120.9229 | -120.8876 | 121.1413 | 120.9343 | 120.8385 | 4.7127 | -121.0226 | 0.12568 | 0.16018 | 0.19543 | 0.16515 | -121.055
2154.5625 | 121.0785 | -0.19226 | 120.8679 | 1.4211e-13 | -0.024746 | 0.011522 | 0.066569 | -0.0077048 | 0.060396 | -0.2206 | -0.0043924 | 0.015772 | 0.019617 | 0.036961 | 0.0037175 | 9.6935 | 4.5571 | 3.9747 | 120.9536 | 120.7329 | 120.6416 | -0.13632 | 0.001048 | -0.040849 | -0.092981 | -0.071161 | -0.045815 | -0.010564 | -0.17331 | 0.055941 | 0.085696 | 9.8858 | 4.167 | 4.111 | -0.13506 | -0.22629 | 0.018955 | -120.9391 | 0.19331 | 0.09928 | 0.080325 | -120.9137 | -120.8785 | 121.1459 | 120.9251 | 120.8339 | 4.7494 | -121.0042 | 0.1211 | 0.14645 | 0.1817 | 0.15141 | -121.0412
2156.3125 | 120.6024 | -1.7761 | 118.84 | 1.4211e-13 | -0.024532 | 0.011735 | 0.066355 | -0.0077048 | 0.060823 | -0.22823 | -0.0048196 | 0.015131 | 0.01919 | 0.037388 | 0.0035039 | 8.5993 | 3.6689 | 2.7752 | 119.136 | 118.9288 | 118.8422 | -1.7252 | 0.001048 | -0.040849 | -0.092981 | -0.071161 | -0.045815 | -0.010564 | -0.17331 | 0.050916 | 0.29597 | 10.3754 | 4.5513 | 4.5004 | 0.088739 | 0.002209 | 1.6028 | -118.9112 | 1.7772 | 1.6831 | 0.080325 | -118.8858 | -118.8506 | 120.9121 | 120.7049 | 120.6184 | 5.445 | -120.5652 | 1.705 | 1.7303 | 1.7656 | 1.7353 | -119.0133
2158.0469 | 120.6894 | -0.16022 | 120.369 | 1.4211e-13 | -0.024532 | 0.01259 | 0.066782 | -0.007491 | 0.060396 | -0.23586 | -0.004606 | 0.015345 | 0.019617 | 0.036961 | 0.0035039 | 10.2978 | 4.6762 | 4.2677 | 120.4363 | 120.2292 | 120.1288 | -0.17753 | -0.003531 | -0.050007 | -0.097559 | -0.080318 | -0.050394 | -0.005985 | -0.17331 | -0.017313 | 0.0673 | 10.4581 | 4.4279 | 4.4452 | -0.13978 | -0.24013 | -0.013089 | -120.4493 | 0.15669 | 0.062658 | 0.075747 | -120.4194 | -120.3749 | 120.5965 | 120.3894 | 120.289 | 4.8364 | -120.5465 | 0.079899 | 0.10982 | 0.15423 | 0.11021 | -120.5423
2159.7969 | 120.7031 | -0.20142 | 120.5612 | 1.4211e-13 | -0.023677 | 0.013231 | 0.067423 | -0.007491 | 0.060823 | -0.23586 | -0.0043924 | 0.015558 | 0.019403 | 0.036961 | 0.0035039 | 10.6641 | 4.7723 | 4.4142 | 120.6286 | 120.4215 | 120.3211 | -0.14548 | -0.003531 | -0.036271 | -0.10214 | -0.071161 | -0.050394 | -0.005985 | -0.17331 | 0.055938 | 0.067332 | 10.8655 | 4.6156 | 4.5597 | -0.13972 | -0.24009 | 0.02811 | -120.6324 | 0.19789 | 0.099278 | 0.071168 | -120.6116 | -120.5672 | 120.83 | 120.6229 | 120.5225 | 4.9737 | -120.7067 | 0.13026 | 0.15102 | 0.19543 | 0.16515 | -120.7345
2161.4844 | 120.8038 | -0.20142 | 120.6116 | 1.4211e-13 | -0.022822 | 0.013872 | 0.068065 | -0.007491 | 0.061251 | -0.22823 | -0.004606 | 0.015345 | 0.019403 | 0.036961 | 0.0035039 | 10.9983 | 4.8181 | 4.5607 | 120.6926 | 120.4856 | 120.3852 | -0.16837 | -0.003531 | -0.045428 | -0.10214 | -0.071161 | -0.045815 | -0.015142 | -0.17788 | 0.033043 | 0.081076 | 11.1998 | 4.7621 | 4.7291 | -0.12597 | -0.22635 | 0.023531 | -120.6827 | 0.19789 | 0.099278 | 0.075747 | -120.6574 | -120.6267 | 120.8941 | 120.687 | 120.5866 | 5.0195 | -120.7799 | 0.13026 | 0.1556 | 0.18627 | 0.15599 | -120.7895
2163.2188 | 120.8679 | -0.19226 | 120.6802 | 1.4211e-13 | -0.022822 | 0.014513 | 0.068065 | -0.0077048 | 0.061251 | -0.23586 | -0.004606 | 0.015345 | 0.018976 | 0.036961 | 0.0037175 | 11.3371 | 4.9188 | 4.7438 | 120.7476 | 120.5405 | 120.4402 | -0.13174 | -0.00811 | -0.036271 | -0.092981 | -0.075739 | -0.045815 | -0.010564 | -0.17788 | 0.06052 | 0.067351 | 11.5294 | 4.9361 | 4.8756 | -0.13969 | -0.24007 | 0.014376 | -120.756 | 0.18415 | 0.09928 | 0.084904 | -120.7261 | -120.6908 | 120.9398 | 120.7328 | 120.6324 | 5.1111 | -120.812 | 0.11652 | 0.14645 | 0.1817 | 0.15599 | -120.8581
2164.9531 | 120.8862 | -0.17853 | 120.7031 | 1.4211e-13 | -0.021754 | 0.015581 | 0.068065 | -0.007491 | 0.061464 | -0.22823 | -0.004606 | 0.015558 | 0.01919 | 0.037175 | 0.0032903 | 11.6256 | 5.0104 | 4.9087 | 120.7796 | 120.568 | 120.4722 | -0.13174 | -0.00811 | -0.040849 | -0.097559 | -0.075739 | -0.054973 | -0.005985 | -0.17788 | 0.046787 | 0.076512 | 11.8041 | 5.0872 | 5.0404 | -0.1351 | -0.23091 | 0.000643 | -120.7789 | 0.17042 | 0.080969 | 0.080326 | -120.7581 | -120.7091 | 120.9582 | 120.7465 | 120.6507 | 5.1889 | -120.8349 | 0.10279 | 0.12355 | 0.17254 | 0.13768 | -120.881
2166.7031 | 120.8588 | -0.20599 | 120.7581 | 1.4211e-13 | -0.022395 | 0.015795 | 0.068706 | -0.0072774 | 0.061892 | -0.24349 | -0.004606 | 0.015558 | 0.01919 | 0.037388 | 0.0035039 | 11.9094 | 5.1065 | 5.0781 | 120.8071 | 120.5955 | 120.5088 | -0.13632 | 0.001048 | -0.040849 | -0.10214 | -0.066582 | -0.045815 | -0.010564 | -0.17331 | 0.069674 | 0.049051 | 12.1154 | 5.2841 | 5.2144 | -0.16256 | -0.24921 | 0.032688 | -120.8246 | 0.20704 | 0.10386 | 0.071168 | -120.8039 | -120.7686 | 121.0131 | 120.8015 | 120.7148 | 5.3125 | -120.8944 | 0.13941 | 0.16018 | 0.19543 | 0.16515 | -120.9314
2168.4531 | 120.8954 | -0.20599 | 120.7672 | 1.4211e-13 | -0.021754 | 0.01665 | 0.069133 | -0.00685 | 0.062319 | -0.23586 | -0.004606 | 0.015345 | 0.01919 | 0.037175 | 0.0032903 | 12.2574 | 5.1981 | 5.2749 | 120.8163 | 120.6138 | 120.5226 | -0.15921 | -0.003531 | -0.036271 | -0.092981 | -0.075739 | -0.050394 | -0.005985 | -0.17788 | 0.046779 | 0.049052 | 12.4634 | 5.4809 | 5.4341 | -0.1534 | -0.24463 | 0.028109 | -120.843 | 0.20246 | 0.11301 | 0.084904 | -120.8176 | -120.7732 | 121.0223 | 120.8198 | 120.7286 | 5.4041 | -120.9264 | 0.13026 | 0.1556 | 0.20001 | 0.16972 | -120.9451
2170.125 | 121.0236 | -0.15564 | 120.7581 | 1.4211e-13 | -0.021113 | 0.017291 | 0.06956 | -0.00685 | 0.062533 | -0.24349 | -0.0048196 | 0.015131 | 0.019403 | 0.036961 | 0.0035039 | 12.6328 | 5.3126 | 5.4718 | 120.8437 | 120.6459 | 120.5363 | -0.1409 | -0.00811 | -0.045428 | -0.092981 | -0.071161 | -0.045815 | -0.015142 | -0.17331 | 0.014741 | 0.085678 | 12.7885 | 5.6274 | 5.6127 | -0.11219 | -0.22174 | -0.017666 | -120.8292 | 0.14753 | 0.062659 | 0.080325 | -120.8039 | -120.7732 | 120.9994 | 120.8015 | 120.692 | 5.4682 | -120.899 | 0.084479 | 0.10983 | 0.1405 | 0.11021 | -120.9314
2171.875 | 120.9549 | -0.21057 | 120.8084 | 1.4211e-13 | -0.020686 | 0.017718 | 0.069774 | -0.0066364 | 0.062533 | -0.2206 | -0.0048196 | 0.015345 | 0.01919 | 0.037175 | 0.0039313 | 13.0266 | 5.4408 | 5.6824 | 120.8712 | 120.6596 | 120.5638 | -0.13632 | -0.00811 | -0.045428 | -0.097559 | -0.075739 | -0.041237 | -0.010564 | -0.16873 | 0.074251 | 0.062794 | 13.2371 | 5.893 | 5.8187 | -0.14881 | -0.24462 | 0.041843 | -120.8842 | 0.20246 | 0.11301 | 0.071169 | -120.8496 | -120.819 | 121.0818 | 120.8702 | 120.7744 | 5.6514 | -120.9447 | 0.13483 | 0.16933 | 0.20001 | 0.16514 | -120.9771
2173.5469 | 120.932 | -0.21973 | 120.813 | 1.4211e-13 | -0.020258 | 0.018146 | 0.070415 | -0.0066364 | 0.063174 | -0.24349 | -0.0041788 | 0.015131 | 0.018762 | 0.036961 | 0.0035039 | 13.3699 | 5.5553 | 5.8793 | 120.8895 | 120.6733 | 120.5821 | -0.14548 | -0.003531 | -0.036271 | -0.097559 | -0.075739 | -0.036658 | -0.010564 | -0.17331 | 0.074249 | 0.07653 | 13.5897 | 6.099 | 6.0247 | -0.13965 | -0.23088 | 0.046421 | -120.8887 | 0.2162 | 0.12217 | 0.075747 | -120.8496 | -120.8236 | 121.1092 | 120.8931 | 120.8018 | 5.775 | -120.9585 | 0.14399 | 0.18307 | 0.20916 | 0.18346 | -120.9863
2175.2812 | 121.0739 | -0.16022 | 120.8038 | 1.4211e-13 | -0.020472 | 0.018146 | 0.070201 | -0.0064228 | 0.063174 | -0.22823 | -0.0050332 | 0.014918 | 0.01919 | 0.037175 | 0.0039313 | 13.7362 | 5.6743 | 6.0761 | 120.8941 | 120.6917 | 120.5867 | -0.14548 | -0.00811 | -0.050007 | -0.097559 | -0.071161 | -0.045815 | -0.010564 | -0.16873 | 0.014739 | 0.090264 | 13.8964 | 6.2363 | 6.2216 | -0.11218 | -0.21715 | -0.008511 | -120.875 | 0.15211 | 0.062658 | 0.071169 | -120.8496 | -120.8144 | 121.0543 | 120.8519 | 120.7469 | 5.8345 | -120.9493 | 0.089056 | 0.1144 | 0.14965 | 0.11021 | -120.9726
2177.0312 | 121.1243 | -0.16479 | 120.8176 | 1.4211e-13 | -0.019831 | 0.019214 | 0.070842 | -0.0059954 | 0.063601 | -0.23586 | -0.004606 | 0.015345 | 0.01919 | 0.037175 | 0.0037175 | 14.1254 | 5.8071 | 6.2867 | 120.917 | 120.7054 | 120.605 | -0.16379 | -0.00811 | -0.045428 | -0.097559 | -0.075739 | -0.036658 | -0.010564 | -0.17331 | 0.001001 | 0.099423 | 14.2902 | 6.4515 | 6.4505 | -0.11218 | -0.21257 | -0.008511 | -120.8933 | 0.15668 | 0.067236 | 0.075747 | -120.8542 | -120.8281 | 121.0818 | 120.8702 | 120.7698 | 5.9719 | -120.9814 | 0.089056 | 0.12814 | 0.15423 | 0.11937 | -120.9909
2178.7812 | 121.0739 | -0.1831 | 120.8084 | 1.4211e-13 | -0.019831 | 0.019428 | 0.071056 | -0.0059954 | 0.063815 | -0.23586 | -0.0041788 | 0.015131 | 0.01919 | 0.037602 | 0.0039313 | 14.51 | 5.9444 | 6.5019 | 120.917 | 120.7145 | 120.605 | -0.15006 | -0.003531 | -0.040849 | -0.097559 | -0.066582 | -0.041237 | -0.010564 | -0.17788 | 0.033048 | 0.10858 | 14.6931 | 6.685 | 6.652 | -0.093864 | -0.20341 | 0.00522 | -120.875 | 0.17957 | 0.085546 | 0.080326 | -120.8496 | -120.819 | 121.1001 | 120.8977 | 120.7881 | 6.1275 | -120.9585 | 0.11652 | 0.14187 | 0.17254 | 0.14226 | -120.9863
2180.4688 | 120.9824 | -0.21973 | 120.8771 | 1.4211e-13 | -0.019617 | 0.019641 | 0.070842 | -0.0059954 | 0.064242 | -0.23586 | -0.0048196 | 0.015558 | 0.018976 | 0.037175 | 0.0037175 | 14.89 | 6.0909 | 6.7125 | 120.9124 | 120.7191 | 120.6096 | -0.15464 | -0.003531 | -0.045428 | -0.092981 | -0.066582 | -0.045815 | -0.010564 | -0.17788 | 0.065091 | 0.035335 | 15.1097 | 6.9322 | 6.8671 | -0.15795 | -0.2675 | 0.041842 | -120.9437 | 0.2162 | 0.12675 | 0.084904 | -120.9229 | -120.8876 | 121.1321 | 120.9389 | 120.8293 | 6.3107 | -121.0317 | 0.15315 | 0.17391 | 0.20916 | 0.1743 | -121.055
2182.2188 | 120.9869 | -0.21515 | 120.8633 | 1.4211e-13 | -0.019404 | 0.020069 | 0.070842 | -0.005568 | 0.064456 | -0.22823 | -0.0043924 | 0.015772 | 0.019403 | 0.037388 | 0.0037175 | 15.3615 | 6.2466 | 6.9414 | 120.9353 | 120.742 | 120.637 | -0.1409 | -0.00811 | -0.036271 | -0.10214 | -0.080318 | -0.045815 | -0.010564 | -0.17788 | 0.07425 | 0.07196 | 15.5767 | 7.1566 | 7.0823 | -0.12132 | -0.22629 | 0.037264 | -120.9437 | 0.20704 | 0.11301 | 0.075747 | -120.9092 | -120.8739 | 121.1505 | 120.9572 | 120.8522 | 6.4618 | -121.0042 | 0.13483 | 0.16933 | 0.20459 | 0.17888 | -121.0412
2183.9688 | 121.0464 | -0.1831 | 120.9183 | 1.4211e-13 | -0.018763 | 0.02071 | 0.070842 | -0.005568 | 0.06531 | -0.22823 | -0.004606 | 0.014918 | 0.019403 | 0.037175 | 0.0037175 | 15.7736 | 6.3748 | 7.1246 | 120.9307 | 120.7283 | 120.6233 | -0.17753 | -0.00811 | -0.045428 | -0.10214 | -0.066582 | -0.045815 | -0.005985 | -0.17331 | 0.005575 | 0.01245 | 15.9567 | 7.3077 | 7.3021 | -0.18999 | -0.29496 | 0.009799 | -120.9849 | 0.17499 | 0.080967 | 0.071168 | -120.9641 | -120.9243 | 121.1138 | 120.9114 | 120.8064 | 6.5579 | -121.0958 | 0.11652 | 0.13729 | 0.17712 | 0.13768 | -121.0916
2185.7188 | 121.0876 | -0.17853 | 120.8862 | 1.4211e-13 | -0.018763 | 0.020923 | 0.070842 | -0.0057818 | 0.065524 | -0.22823 | -0.004606 | 0.015558 | 0.018976 | 0.037175 | 0.0039313 | 16.2589 | 6.5625 | 7.3718 | 120.9582 | 120.7558 | 120.6508 | -0.16379 | -0.003531 | -0.036271 | -0.10214 | -0.071161 | -0.036658 | -0.005985 | -0.17331 | 0.014734 | 0.071964 | 16.4374 | 7.5503 | 7.5356 | -0.13047 | -0.23545 | 0.005222 | -120.9574 | 0.175 | 0.07639 | 0.071168 | -120.9229 | -120.8922 | 121.1367 | 120.9343 | 120.8293 | 6.7411 | -121.05 | 0.10737 | 0.14187 | 0.17254 | 0.14226 | -121.0595
2187.4062 | 120.5795 | -0.21057 | 120.4788 | 1.4211e-13 | -0.018335 | 0.021137 | 0.070629 | -0.0051408 | 0.065738 | -0.22823 | -0.004606 | 0.015131 | 0.01919 | 0.037175 | 0.0037175 | 16.4741 | 6.6679 | 7.532 | 120.4271 | 120.2246 | 120.1197 | -0.19127 | -0.003531 | -0.036271 | -0.097559 | -0.066582 | -0.041237 | -0.097557 | -0.17331 | 0.019304 | -0.05172 | 16.6847 | 7.7426 | 7.7233 | -0.25422 | -0.35916 | 0.037265 | -120.5454 | 0.20704 | 0.11301 | 0.075747 | -120.5201 | -120.5764 | 120.6377 | 120.4352 | 120.3302 | 6.8784 | -120.6701 | 0.14399 | 0.16933 | 0.11301 | 0.1743 | -120.6521
2189.1406 | 120.9183 | -0.16479 | 120.6528 | 1.4211e-13 | -0.018335 | 0.021351 | 0.071056 | -0.0053544 | 0.065951 | -0.22823 | -0.0043924 | 0.015345 | 0.019403 | 0.037175 | 0.0037175 | 16.8907 | 6.8785 | 7.7838 | 120.6698 | 120.4627 | 120.3715 | -0.21416 | -0.012689 | -0.036271 | -0.10214 | -0.066582 | -0.036658 | -0.092979 | -0.17331 | -0.049367 | 0.016985 | 17.0555 | 7.9486 | 7.998 | -0.19007 | -0.28128 | -0.008511 | -120.7194 | 0.15211 | 0.062657 | 0.071168 | -120.6894 | -120.7458 | 120.8346 | 120.6275 | 120.5363 | 7.0433 | -120.8669 | 0.098213 | 0.12814 | 0.071816 | 0.12852 | -120.8261
2190.875 | 120.8405 | -0.16479 | 120.6024 | 1.4211e-13 | -0.018335 | 0.021564 | 0.070842 | -0.004927 | 0.066379 | -0.22823 | -0.004606 | 0.015345 | 0.01919 | 0.037602 | 0.0037175 | 16.9594 | 6.8693 | 7.7655 | 120.2302 | 120.0506 | 119.9136 | -0.46142 | -0.003531 | -0.040849 | -0.097559 | -0.062004 | -0.036658 | -0.0884 | -0.17331 | -0.29663 | -0.37219 | 17.1242 | 7.9303 | 8.2269 | -0.55181 | -0.68879 | -0.008511 | -120.6644 | 0.16126 | 0.067236 | 0.075747 | -120.6391 | -120.6908 | 120.395 | 120.2154 | 120.0784 | 7.0341 | -121.0638 | 0.10279 | 0.12814 | 0.076395 | 0.12395 | -120.7757
2192.5469 | 120.8588 | -0.20599 | 120.7489 | 1.4211e-13 | -0.018335 | 0.021564 | 0.071056 | -0.0047134 | 0.06702 | -0.23586 | -0.004606 | 0.015558 | 0.01919 | 0.037388 | 0.0037175 | 17.6187 | 7.318 | 8.3057 | 120.8117 | 120.5955 | 120.5043 | -0.13632 | -0.003531 | -0.045428 | -0.092981 | -0.062004 | -0.036658 | -0.097557 | -0.16873 | 0.069674 | 0.062785 | 17.8247 | 8.5117 | 8.4421 | -0.15341 | -0.24463 | 0.037266 | -120.8109 | 0.20246 | 0.11301 | 0.075747 | -120.7856 | -120.8465 | 121.0177 | 120.8015 | 120.7103 | 7.524 | -120.8852 | 0.14399 | 0.16934 | 0.10844 | 0.16057 | -120.9176
2194.2812 | 120.9045 | -0.21057 | 120.7855 | 1.4211e-13 | -0.017908 | 0.021778 | 0.070842 | -0.0047134 | 0.067233 | -0.23586 | -0.0043924 | 0.015345 | 0.018976 | 0.037388 | 0.0039313 | 17.9895 | 7.4966 | 8.5667 | 120.8392 | 120.6413 | 120.5272 | -0.15006 | 0.001048 | -0.040849 | -0.10214 | -0.075739 | -0.045815 | -0.097557 | -0.17788 | 0.060514 | 0.053634 | 18.2001 | 8.7773 | 8.7168 | -0.14424 | -0.25836 | 0.032686 | -120.8613 | 0.21162 | 0.10843 | 0.075747 | -120.8313 | -120.8831 | 121.0497 | 120.8519 | 120.7377 | 7.7071 | -120.9356 | 0.13483 | 0.16476 | 0.11301 | 0.16972 | -120.9634
2195.9531 | 120.9961 | -0.17853 | 120.7901 | 1.4211e-13 | -0.017908 | 0.021992 | 0.070415 | -0.0042862 | 0.067661 | -0.22823 | -0.004606 | 0.015558 | 0.01919 | 0.037175 | 0.0037175 | 18.3283 | 7.6935 | 8.791 | 120.862 | 120.6596 | 120.5546 | -0.14548 | -0.003531 | -0.031692 | -0.10214 | -0.071161 | -0.036658 | -0.092979 | -0.17331 | 0.03305 | 0.071948 | 18.5069 | 8.9696 | 8.9365 | -0.1305 | -0.23547 | 0.005222 | -120.8613 | 0.175 | 0.07639 | 0.071168 | -120.8268 | -120.8831 | 121.0406 | 120.8381 | 120.7332 | 7.872 | -120.9356 | 0.10737 | 0.14187 | 0.085549 | 0.14684 | -120.9634
2197.7031 | 120.9732 | -0.19684 | 120.8542 | 1.4211e-13 | -0.017694 | 0.021778 | 0.070415 | -0.0040724 | 0.067874 | -0.23586 | -0.0048196 | 0.015345 | 0.01919 | 0.037388 | 0.0035039 | 18.7267 | 7.9178 | 9.0383 | 120.8849 | 120.6825 | 120.5775 | -0.1409 | -0.00811 | -0.045428 | -0.097559 | -0.071161 | -0.045815 | -0.097557 | -0.17331 | 0.055939 | 0.030753 | 18.9235 | 9.2351 | 9.1792 | -0.17169 | -0.27666 | 0.023532 | -120.9253 | 0.18873 | 0.099279 | 0.075747 | -120.9 | -120.9517 | 121.0818 | 120.8793 | 120.7744 | 8.1146 | -120.9951 | 0.12568 | 0.15102 | 0.099281 | 0.15141 | -121.0275
2199.4531 | 120.9686 | -0.21515 | 120.8359 | 1.4211e-13 | -0.017908 | 0.022419 | 0.070629 | -0.0040724 | 0.068302 | -0.22823 | -0.0043924 | 0.015345 | 0.01919 | 0.037388 | 0.0037175 | 19.038 | 8.1147 | 9.2809 | 120.8987 | 120.71 | 120.5958 | -0.13632 | -0.00811 | -0.045428 | -0.10214 | -0.066582 | -0.036658 | -0.092979 | -0.18246 | 0.078829 | 0.062799 | 19.2531 | 9.4961 | 9.4172 | -0.12591 | -0.24004 | 0.032685 | -120.9025 | 0.20704 | 0.11301 | 0.080326 | -120.8725 | -120.9289 | 121.1138 | 120.9251 | 120.811 | 8.3298 | -120.9722 | 0.14857 | 0.17849 | 0.12217 | 0.16972 | -121.0183
2201.1875 | 121.0464 | -0.16937 | 120.8588 | 1.4211e-13 | -0.017908 | 0.021992 | 0.070415 | -0.0034314 | 0.068515 | -0.23586 | -0.004606 | 0.015345 | 0.019403 | 0.037602 | 0.0035039 | 19.3218 | 8.2933 | 9.5144 | 120.9261 | 120.7237 | 120.6096 | -0.13632 | -0.003531 | -0.040849 | -0.10214 | -0.071161 | -0.027501 | -0.097557 | -0.18704 | 0.033053 | 0.067381 | 19.4912 | 9.6838 | 9.6507 | -0.13506 | -0.24919 | -0.01767 | -120.9299 | 0.16584 | 0.067235 | 0.084905 | -120.8863 | -120.9563 | 121.0955 | 120.8931 | 120.7789 | 8.4626 | -120.9951 | 0.098212 | 0.14187 | 0.071816 | 0.12852 | -121.0458
2202.875 | 121.0419 | -0.20599 | 120.8588 | 1.4211e-13 | -0.017481 | 0.021992 | 0.069988 | -0.0034314 | 0.068729 | -0.23586 | -0.0043924 | 0.015558 | 0.018762 | 0.037388 | 0.0037175 | 19.592 | 8.4718 | 9.78 | 120.9353 | 120.7329 | 120.637 | -0.1409 | 0.001048 | -0.040849 | -0.088402 | -0.071161 | -0.03208 | -0.097557 | -0.17788 | 0.065095 | 0.076537 | 19.798 | 9.9859 | 9.9209 | -0.1259 | -0.22172 | 0.028109 | -120.9299 | 0.20704 | 0.11759 | 0.089483 | -120.8908 | -120.9563 | 121.1413 | 120.9389 | 120.843 | 8.6778 | -120.9997 | 0.13483 | 0.17391 | 0.10844 | 0.16515 | -121.0367
2204.6094 | 121.0602 | -0.20142 | 120.9091 | 1.4211e-13 | -0.017908 | 0.022206 | 0.070415 | -0.0032178 | 0.06937 | -0.22823 | -0.0048196 | 0.015131 | 0.019403 | 0.037388 | 0.0039313 | 19.9308 | 8.6275 | 9.9997 | 120.949 | 120.7466 | 120.6416 | -0.14548 | -0.00811 | -0.040849 | -0.092981 | -0.066582 | -0.036658 | -0.097557 | -0.18246 | 0.055938 | 0.039919 | 20.1322 | 10.2011 | 10.1452 | -0.16252 | -0.26749 | 0.018952 | -120.9757 | 0.19331 | 0.10844 | 0.089483 | -120.9458 | -121.0067 | 121.1505 | 120.948 | 120.843 | 8.8289 | -121.0546 | 0.13483 | 0.16476 | 0.10386 | 0.16057 | -121.0916
2206.3438 | 121.0648 | -0.19226 | 120.845 | 1.4211e-13 | -0.018122 | 0.022206 | 0.069988 | -0.0034314 | 0.069584 | -0.23586 | -0.0043924 | 0.015131 | 0.018976 | 0.037602 | 0.0039313 | 20.1688 | 8.9159 | 10.2836 | 120.9628 | 120.7558 | 120.6554 | -0.1409 | 0.005626 | -0.036271 | -0.092981 | -0.066582 | -0.027501 | -0.092979 | -0.17331 | 0.051362 | 0.11774 | 20.3611 | 10.4758 | 10.4245 | -0.089275 | -0.18967 | 0.018955 | -120.9116 | 0.19789 | 0.09928 | 0.080325 | -120.8725 | -120.938 | 121.155 | 120.948 | 120.8476 | 9.1082 | -120.9859 | 0.12568 | 0.16476 | 0.099282 | 0.15599 | -121.0183
2208.0938 | 121.0098 | -0.20599 | 120.9183 | 1.4211e-13 | -0.017694 | 0.022419 | 0.070201 | -0.0034314 | 0.069584 | -0.23586 | -0.004606 | 0.015345 | 0.01919 | 0.037388 | 0.0039313 | 20.3245 | 9.154 | 10.5308 | 120.9765 | 120.7741 | 120.6645 | -0.14548 | -0.003531 | -0.040849 | -0.092981 | -0.066582 | -0.03208 | -0.10214 | -0.17788 | 0.060516 | 0.058234 | 20.5305 | 10.7368 | 10.6763 | -0.1442 | -0.25375 | 0.028109 | -120.9849 | 0.20246 | 0.11301 | 0.084904 | -120.9504 | -121.0204 | 121.1825 | 120.9801 | 120.8705 | 9.36 | -121.0638 | 0.13941 | 0.17391 | 0.10386 | 0.16515 | -121.0962
2209.7812 | 121.0556 | -0.19684 | 120.9137 | 1.4211e-13 | -0.017908 | 0.022206 | 0.069774 | -0.0030042 | 0.070652 | -0.23586 | -0.0048196 | 0.015131 | 0.018976 | 0.037602 | 0.0037175 | 20.7503 | 9.3692 | 10.7414 | 120.9857 | 120.7787 | 120.6783 | -0.1409 | 0.005626 | -0.031692 | -0.083823 | -0.052847 | -0.036658 | -0.10214 | -0.15957 | 0.055939 | 0.071969 | 20.9471 | 10.9382 | 10.8823 | -0.13504 | -0.23544 | 0.037268 | -120.9665 | 0.20246 | 0.11302 | 0.075747 | -120.9504 | -121.0158 | 121.1825 | 120.9755 | 120.8751 | 9.5661 | -121.0546 | 0.14399 | 0.16018 | 0.094702 | 0.16515 | -121.0733
2211.5312 | 121.1655 | -0.16937 | 120.8817 | 1.4211e-13 | -0.018122 | 0.022847 | 0.070201 | -0.0023632 | 0.070652 | -0.22823 | -0.0043924 | 0.015131 | 0.018762 | 0.037816 | 0.0035039 | 21.0662 | 9.6348 | 11.0024 | 120.9902 | 120.7878 | 120.6828 | -0.13632 | 0.014784 | -0.022535 | -0.088402 | -0.057425 | -0.03208 | -0.11129 | -0.16415 | 0.033053 | 0.10859 | 21.2356 | 11.1717 | 11.1387 | -0.093844 | -0.19882 | 0.005224 | -120.9391 | 0.18416 | 0.080971 | 0.075747 | -120.9137 | -120.9929 | 121.1596 | 120.9572 | 120.8522 | 9.8042 | -121.018 | 0.11195 | 0.13729 | 0.05808 | 0.14684 | -121.0458
2213.2812 | 121.1426 | -0.16937 | 120.9045 | 1.4211e-13 | -0.018122 | 0.022847 | 0.069774 | -0.0023632 | 0.070652 | -0.22823 | -0.0048196 | 0.015345 | 0.01919 | 0.037388 | 0.0035039 | 21.3272 | 9.8683 | 11.213 | 121.004 | 120.8015 | 120.6966 | -0.13632 | 0.010205 | -0.031692 | -0.079245 | -0.057425 | -0.027501 | -0.10214 | -0.16415 | 0.033053 | 0.099437 | 21.4966 | 11.3823 | 11.3493 | -0.10299 | -0.20797 | 0.005224 | -120.962 | 0.17958 | 0.090128 | 0.084904 | -120.932 | -121.0067 | 121.1734 | 120.9709 | 120.8659 | 10.0377 | -121.0409 | 0.11195 | 0.14187 | 0.067237 | 0.13768 | -121.0687
2214.9531 | 121.1426 | -0.19226 | 120.932 | 1.4211e-13 | -0.018122 | 0.022633 | 0.06956 | -0.0023632 | 0.071079 | -0.24349 | -0.004606 | 0.015558 | 0.018976 | 0.037602 | 0.0035039 | 21.5561 | 10.0881 | 11.2999 | 121.0086 | 120.8107 | 120.7103 | -0.13632 | 0.010205 | -0.027113 | -0.079245 | -0.062004 | -0.03208 | -0.10671 | -0.16873 | 0.055941 | 0.07655 | 21.7484 | 11.4922 | 11.4363 | -0.1213 | -0.2217 | 0.023533 | -120.994 | 0.20247 | 0.11302 | 0.089483 | -120.9641 | -121.0387 | 121.2008 | 121.003 | 120.9026 | 10.2803 | -121.0683 | 0.13026 | 0.16018 | 0.085547 | 0.16515 | -121.1007
2216.7031 | 121.0831 | -0.21973 | 120.9549 | 1.4211e-13 | -0.018549 | 0.022847 | 0.069774 | -0.0019358 | 0.07172 | -0.23586 | -0.0043924 | 0.015131 | 0.018976 | 0.037602 | 0.0035039 | 21.5881 | 10.2941 | 11.5105 | 121.0131 | 120.8199 | 120.7149 | -0.13632 | 0.010205 | -0.027113 | -0.079245 | -0.052847 | -0.027501 | -0.10214 | -0.15957 | 0.083407 | 0.05824 | 21.8079 | 11.7303 | 11.6469 | -0.13503 | -0.24001 | 0.060157 | -121.0077 | 0.22993 | 0.14048 | 0.080325 | -120.9824 | -121.057 | 121.2329 | 121.0396 | 120.9346 | 10.5138 | -121.0912 | 0.16688 | 0.19223 | 0.11759 | 0.19261 | -121.1145
2218.3906 | 121.1609 | -0.1831 | 120.9503 | 1.4211e-13 | -0.018976 | 0.022633 | 0.06956 | -0.0025768 | 0.071507 | -0.24349 | -0.0048196 | 0.015345 | 0.01919 | 0.037388 | 0.0037175 | 21.7255 | 10.4681 | 11.538 | 121.0269 | 120.8244 | 120.7286 | -0.1409 | 0.014784 | -0.031692 | -0.083823 | -0.052847 | -0.036658 | -0.10671 | -0.15957 | 0.042206 | 0.076553 | 21.9086 | 11.7211 | 11.6789 | -0.12588 | -0.2217 | 0.023535 | -121.0032 | 0.19789 | 0.099282 | 0.075747 | -120.987 | -121.057 | 121.21 | 121.0075 | 120.9117 | 10.6512 | -121.0912 | 0.13026 | 0.14645 | 0.076391 | 0.15141 | -121.1099
2220.125 | 121.2067 | -0.15106 | 120.9549 | 1.4211e-13 | -0.018976 | 0.02306 | 0.06956 | -0.0025768 | 0.07172 | -0.24349 | -0.0043924 | 0.015131 | 0.018762 | 0.037388 | 0.0037175 | 21.8583 | 10.6695 | 11.6067 | 121.036 | 120.8336 | 120.7332 | -0.1409 | 0.010205 | -0.036271 | -0.083823 | -0.057425 | -0.027501 | -0.10214 | -0.16415 | 0.010163 | 0.081132 | 22.0093 | 11.7577 | 11.7476 | -0.1213 | -0.2217 | -0.013087 | -121.0123 | 0.16127 | 0.067239 | 0.080326 | -120.9824 | -121.057 | 121.1871 | 120.9847 | 120.8843 | 10.8206 | -121.0958 | 0.093637 | 0.12356 | 0.048926 | 0.11479 | -121.119
2221.8594 | 121.2021 | -0.19684 | 120.9503 | 1.4211e-13 | -0.018976 | 0.022847 | 0.068706 | -0.0019358 | 0.07172 | -0.24349 | -0.004606 | 0.015345 | 0.018976 | 0.037602 | 0.0035039 | 21.8903 | 10.7932 | 11.6662 | 121.0452 | 120.8473 | 120.7424 | -0.1409 | 0.014784 | -0.031692 | -0.074666 | -0.048268 | -0.027501 | -0.10214 | -0.15499 | 0.055939 | 0.094867 | 22.0872 | 11.863 | 11.8071 | -0.10298 | -0.20796 | 0.041847 | -120.9986 | 0.21162 | 0.12217 | 0.080325 | -120.9778 | -121.0525 | 121.242 | 121.0442 | 120.9392 | 10.99 | -121.0912 | 0.14857 | 0.16934 | 0.094702 | 0.16515 | -121.1053
2223.5938 | 121.2433 | -0.15106 | 120.9457 | 1.4211e-13 | -0.01919 | 0.022419 | 0.069133 | -0.0017222 | 0.071934 | -0.22823 | -0.0048196 | 0.015345 | 0.018976 | 0.037388 | 0.0035039 | 21.8949 | 10.958 | 11.7944 | 121.0498 | 120.8428 | 120.7561 | -0.1409 | 0.005626 | -0.017956 | -0.079245 | -0.052847 | -0.027501 | -0.097557 | -0.15957 | 0.010163 | 0.10402 | 22.046 | 11.9455 | 11.9353 | -0.10298 | -0.18965 | -0.008508 | -120.9986 | 0.15669 | 0.071817 | 0.080325 | -120.9732 | -121.0433 | 121.2008 | 120.9938 | 120.9072 | 11.1091 | -121.0866 | 0.098215 | 0.12356 | 0.053505 | 0.13311 | -121.1053
2225.2656 | 121.2479 | -0.17853 | 120.9412 | 1.4211e-13 | -0.01919 | 0.022206 | 0.069347 | -0.0021494 | 0.07172 | -0.22823 | -0.004606 | 0.015345 | 0.018976 | 0.037602 | 0.0035039 | 21.785 | 11.1915 | 11.8722 | 121.0635 | 120.8565 | 120.7515 | -0.13632 | 0.010205 | -0.031692 | -0.092981 | -0.052847 | -0.027501 | -0.10671 | -0.16873 | 0.042208 | 0.12233 | 21.9635 | 12.0508 | 12.0085 | -0.084669 | -0.18965 | 0.0098 | -120.994 | 0.18873 | 0.085547 | 0.075747 | -120.9687 | -121.0479 | 121.242 | 121.035 | 120.93 | 11.37 | -121.0775 | 0.12568 | 0.15103 | 0.071814 | 0.14684 | -121.1099
2227 | 121.2067 | -0.17853 | 120.9641 | 1.4211e-13 | -0.019404 | 0.022633 | 0.068919 | -0.0019358 | 0.072148 | -0.23586 | -0.0043924 | 0.015558 | 0.018976 | 0.037602 | 0.0035039 | 21.8216 | 11.3518 | 12.0004 | 121.0681 | 120.8702 | 120.779 | -0.13632 | 0.005626 | -0.027113 | -0.083823 | -0.048268 | -0.027501 | -0.10214 | -0.16873 | 0.042208 | 0.10403 | 22.0002 | 12.1789 | 12.1367 | -0.09382 | -0.18506 | 0.0098 | -121.0123 | 0.18415 | 0.094705 | 0.084905 | -120.9916 | -121.0662 | 121.2466 | 121.0488 | 120.9575 | 11.5303 | -121.1004 | 0.13026 | 0.15103 | 0.076392 | 0.15141 | -121.1328
2228.6875 | 121.1792 | -0.20142 | 120.9915 | 1.4211e-13 | -0.019404 | 0.022206 | 0.068919 | -0.0015084 | 0.072148 | -0.23586 | -0.0048196 | 0.015772 | 0.018762 | 0.037816 | 0.0035039 | 21.7392 | 11.3792 | 12.0508 | 121.0772 | 120.8702 | 120.7836 | -0.13174 | 0.014784 | -0.022535 | -0.083823 | -0.048268 | -0.022922 | -0.10214 | -0.15957 | 0.069675 | 0.085716 | 21.9406 | 12.2522 | 12.1825 | -0.12129 | -0.20795 | 0.041846 | -121.0398 | 0.2162 | 0.11759 | 0.075747 | -121.0144 | -121.0937 | 121.2786 | 121.0716 | 120.985 | 11.5807 | -121.1233 | 0.15315 | 0.17849 | 0.09928 | 0.17888 | -121.1511
2230.4375 | 121.1472 | -0.18768 | 121.019 | 1.4211e-13 | -0.019404 | 0.021992 | 0.068919 | -0.0021494 | 0.072148 | -0.22823 | -0.0043924 | 0.015345 | 0.018976 | 0.037816 | 0.0032903 | 21.6934 | 11.4571 | 12.0462 | 121.091 | 120.8794 | 120.7881 | -0.13632 | 0.010205 | -0.027113 | -0.092981 | -0.048268 | -0.022922 | -0.10214 | -0.15499 | 0.051363 | 0.071986 | 21.8811 | 12.2339 | 12.1825 | -0.13959 | -0.23084 | 0.032692 | -121.0672 | 0.19789 | 0.094702 | 0.06201 | -121.0419 | -121.1211 | 121.2787 | 121.0671 | 120.9758 | 11.6448 | -121.1553 | 0.13941 | 0.16476 | 0.085547 | 0.16057 | -121.174
2232.1875 | 121.2296 | -0.15564 | 120.9961 | 1.4211e-13 | -0.019617 | 0.022206 | 0.069133 | -0.0019358 | 0.072361 | -0.22823 | -0.0048196 | 0.015345 | 0.018976 | 0.037602 | 0.0030767 | 21.7575 | 11.5303 | 12.0599 | 121.1001 | 120.9023 | 120.7927 | -0.13174 | 0.010205 | -0.022535 | -0.083823 | -0.052847 | -0.018344 | -0.10214 | -0.15957 | 0.023899 | 0.10403 | 21.9132 | 12.2156 | 12.1917 | -0.093811 | -0.20337 | -0.00393 | -121.0489 | 0.16584 | 0.071817 | 0.075747 | -121.0144 | -121.0982 | 121.2558 | 121.0579 | 120.9484 | 11.686 | -121.1278 | 0.10279 | 0.1373 | 0.053504 | 0.13311 | -121.1557
2233.875 | 121.1472 | -0.21057 | 121.0236 | 1.4211e-13 | -0.01919 | 0.022633 | 0.068919 | -0.0019358 | 0.072148 | -0.22823 | -0.004606 | 0.015131 | 0.018976 | 0.037816 | 0.0035039 | 21.8445 | 11.6036 | 12.1103 | 121.1001 | 120.9069 | 120.8019 | -0.13632 | 0.019362 | -0.022535 | -0.083823 | -0.04369 | -0.027501 | -0.10214 | -0.15957 | 0.074251 | 0.076564 | 22.0551 | 12.3209 | 12.2466 | -0.1167 | -0.22168 | 0.051001 | -121.0673 | 0.22993 | 0.12675 | 0.075747 | -121.0511 | -121.1257 | 121.3107 | 121.1174 | 121.0124 | 11.8142 | -121.1599 | 0.16688 | 0.18307 | 0.10844 | 0.18804 | -121.1831
2235.6094 | 121.3028 | -0.16022 | 121.0327 | 1.4211e-13 | -0.019831 | 0.022419 | 0.069133 | -0.0017222 | 0.073002 | -0.22823 | -0.0048196 | 0.015131 | 0.018549 | 0.038243 | 0.0035039 | 21.9453 | 11.6723 | 12.1744 | 121.1139 | 120.916 | 120.811 | -0.13632 | 0.010205 | -0.017956 | -0.079245 | -0.052847 | -0.027501 | -0.10671 | -0.15957 | 0.023897 | 0.081145 | 22.1055 | 12.3346 | 12.3107 | -0.1167 | -0.22168 | 0.000647 | -121.0856 | 0.17042 | 0.080972 | 0.080325 | -121.0602 | -121.1394 | 121.2741 | 121.0762 | 120.9713 | 11.8325 | -121.169 | 0.10737 | 0.13272 | 0.053503 | 0.14226 | -121.1923
2237.2969 | 121.2936 | -0.14191 | 121.019 | 1.4211e-13 | -0.019831 | 0.022419 | 0.069347 | -0.0017222 | 0.072789 | -0.23586 | -0.0041788 | 0.015345 | 0.018976 | 0.03803 | 0.0032903 | 22.0551 | 11.6952 | 12.1744 | 121.1276 | 120.9252 | 120.8248 | -0.13632 | 0.010205 | -0.022535 | -0.088402 | -0.048268 | -0.027501 | -0.10214 | -0.16415 | 0.005587 | 0.10861 | 22.197 | 12.3163 | 12.3107 | -0.093805 | -0.19421 | -0.022242 | -121.0672 | 0.15211 | 0.053505 | 0.075747 | -121.0465 | -121.1211 | 121.2695 | 121.0671 | 120.9667 | 11.8371 | -121.1553 | 0.093639 | 0.11441 | 0.039771 | 0.11937 | -121.1831
2239.0469 | 121.2708 | -0.16479 | 121.019 | 1.4211e-13 | -0.019617 | 0.022847 | 0.069133 | -0.0015084 | 0.073002 | -0.22823 | -0.0048196 | 0.015345 | 0.018976 | 0.038243 | 0.0035039 | 22.1284 | 11.805 | 12.2156 | 121.1276 | 120.9343 | 120.8248 | -0.13632 | 0.014784 | -0.022535 | -0.083823 | -0.057425 | -0.013765 | -0.10214 | -0.16873 | 0.028475 | 0.10861 | 22.2932 | 12.3804 | 12.3519 | -0.084647 | -0.19421 | -0.003933 | -121.0764 | 0.17958 | 0.080972 | 0.084905 | -121.0327 | -121.1211 | 121.2924 | 121.0991 | 120.9896 | 11.9698 | -121.1553 | 0.10737 | 0.15103 | 0.062659 | 0.14226 | -121.1877
2240.7969 | 121.2158 | -0.1831 | 121.051 | 1.4211e-13 | -0.019831 | 0.023274 | 0.06956 | -0.0019358 | 0.073002 | -0.22823 | -0.0048196 | 0.015772 | 0.018762 | 0.037816 | 0.0037175 | 22.1833 | 11.86 | 12.2889 | 121.1368 | 120.9435 | 120.8294 | -0.13174 | 0.010205 | -0.027113 | -0.074666 | -0.048268 | -0.013765 | -0.11129 | -0.15957 | 0.051364 | 0.085726 | 22.3664 | 12.472 | 12.4206 | -0.10753 | -0.22167 | 0.023535 | -121.0993 | 0.19331 | 0.10844 | 0.084904 | -121.0648 | -121.1623 | 121.3199 | 121.1266 | 121.0125 | 12.0431 | -121.1828 | 0.13484 | 0.16934 | 0.071812 | 0.15599 | -121.2106
2242.5469 | 121.3486 | -0.15564 | 121.0281 | 1.4211e-13 | -0.019617 | 0.022633 | 0.06956 | -0.0015084 | 0.073002 | -0.2206 | -0.0048196 | 0.015131 | 0.018549 | 0.037816 | 0.0035039 | 22.2337 | 11.9149 | 12.3209 | 121.1505 | 120.9389 | 120.8385 | -0.13174 | 0.014784 | -0.027113 | -0.083823 | -0.04369 | -0.013765 | -0.10214 | -0.15499 | 0.023899 | 0.12235 | 22.3893 | 12.4765 | 12.4526 | -0.089223 | -0.18963 | 0.000649 | -121.0718 | 0.17042 | 0.071817 | 0.071168 | -121.0419 | -121.1303 | 121.3061 | 121.0946 | 120.9941 | 12.0706 | -121.1599 | 0.11195 | 0.14188 | 0.053504 | 0.12853 | -121.1831
2244.2969 | 121.2296 | -0.20142 | 121.0968 | 1.4211e-13 | -0.019617 | 0.02306 | 0.069988 | -0.0017222 | 0.07343 | -0.2206 | -0.0048196 | 0.015345 | 0.018976 | 0.03803 | 0.0035039 | 22.3482 | 12.0019 | 12.3575 | 121.1505 | 120.9527 | 120.8477 | -0.13174 | 0.014784 | -0.017956 | -0.083823 | -0.052847 | -0.018344 | -0.10214 | -0.15957 | 0.069675 | 0.053685 | 22.5496 | 12.5589 | 12.4893 | -0.14415 | -0.24914 | 0.041846 | -121.1496 | 0.2162 | 0.11759 | 0.075747 | -121.1151 | -121.1989 | 121.3519 | 121.1541 | 121.0491 | 12.2033 | -121.2285 | 0.14857 | 0.18307 | 0.09928 | 0.18346 | -121.2564
2245.9844 | 121.3257 | -0.15564 | 121.0419 | 1.4211e-13 | -0.019617 | 0.02306 | 0.069988 | -0.0019358 | 0.073216 | -0.22823 | -0.0048196 | 0.015131 | 0.018549 | 0.037602 | 0.0035039 | 22.3115 | 12.0477 | 12.385 | 121.1551 | 120.9618 | 120.8522 | -0.13632 | 0.014784 | -0.022535 | -0.083823 | -0.048268 | -0.018344 | -0.10671 | -0.15041 | 0.01932 | 0.11319 | 22.4672 | 12.5406 | 12.5213 | -0.080061 | -0.18963 | 0.005228 | -121.0901 | 0.17042 | 0.071817 | 0.066589 | -121.0602 | -121.1486 | 121.3107 | 121.1174 | 121.0079 | 12.2034 | -121.1782 | 0.10737 | 0.1373 | 0.048926 | 0.13311 | -121.1923
2247.7344 | 121.1838 | -0.20599 | 121.1151 | 1.4211e-13 | -0.019617 | 0.023274 | 0.069988 | -0.0019358 | 0.073643 | -0.22823 | -0.004606 | 0.015131 | 0.018549 | 0.037816 | 0.0032903 | 22.3848 | 12.0843 | 12.385 | 121.1596 | 120.9618 | 120.866 | -0.13632 | 0.014784 | -0.017956 | -0.079245 | -0.052847 | -0.022922 | -0.11129 | -0.15499 | 0.069674 | 0.044531 | 22.5908 | 12.591 | 12.5213 | -0.1533 | -0.24913 | 0.051003 | -121.168 | 0.22078 | 0.12675 | 0.075746 | -121.138 | -121.2264 | 121.3656 | 121.1678 | 121.072 | 12.2903 | -121.2514 | 0.15315 | 0.18307 | 0.094701 | 0.18804 | -121.2701
2249.4062 | 121.3211 | -0.16022 | 121.0419 | 1.4211e-13 | -0.01919 | 0.02306 | 0.069988 | -0.0019358 | 0.073643 | -0.23586 | -0.0048196 | 0.015558 | 0.018335 | 0.03803 | 0.0030767 | 22.4535 | 12.1301 | 12.3392 | 121.1688 | 120.971 | 120.866 | -0.12716 | 0.014784 | -0.008798 | -0.083823 | -0.04369 | -0.013765 | -0.10214 | -0.15499 | 0.033055 | 0.12693 | 22.6137 | 12.4994 | 12.4664 | -0.070904 | -0.17589 | 0.005226 | -121.0856 | 0.175 | 0.076394 | 0.071168 | -121.0556 | -121.144 | 121.329 | 121.1312 | 121.0262 | 12.2903 | -121.169 | 0.11653 | 0.14645 | 0.058081 | 0.15142 | -121.1969
2251.1406 | 121.2067 | -0.19684 | 121.0922 | 1.4211e-13 | -0.018976 | 0.023488 | 0.070201 | -0.0015084 | 0.07343 | -0.23586 | -0.0043924 | 0.015772 | 0.018549 | 0.038243 | 0.0032903 | 22.5084 | 12.1668 | 12.3438 | 121.1734 | 120.971 | 120.8614 | -0.16379 | 0.010205 | -0.017956 | -0.074666 | -0.04369 | -0.018344 | -0.10671 | -0.15499 | 0.033044 | 0.081155 | 22.7052 | 12.5406 | 12.5076 | -0.12126 | -0.23082 | 0.041847 | -121.1359 | 0.20704 | 0.12217 | 0.080325 | -121.1106 | -121.1989 | 121.3702 | 121.1678 | 121.0582 | 12.3636 | -121.256 | 0.15315 | 0.17849 | 0.090124 | 0.17888 | -121.2472
2252.8281 | 121.2982 | -0.16479 | 121.0876 | 1.4211e-13 | -0.019617 | 0.023488 | 0.069988 | -0.0017222 | 0.073002 | -0.22823 | -0.004606 | 0.015345 | 0.018549 | 0.038243 | 0.0035039 | 22.5084 | 12.2675 | 12.3072 | 121.1825 | 120.9755 | 120.8797 | -0.13632 | 0.014784 | -0.017956 | -0.079245 | -0.04369 | -0.018344 | -0.11129 | -0.15041 | 0.028475 | 0.094889 | 22.6732 | 12.472 | 12.4435 | -0.1121 | -0.20793 | 0.014383 | -121.1313 | 0.17958 | 0.08555 | 0.071167 | -121.106 | -121.1989 | 121.3473 | 121.1403 | 121.0445 | 12.4323 | -121.224 | 0.1211 | 0.14645 | 0.053502 | 0.14684 | -121.2381
2254.5781 | 121.2433 | -0.19226 | 121.1105 | 1.4211e-13 | -0.019404 | 0.023488 | 0.070201 | -0.0017222 | 0.073216 | -0.22823 | -0.004606 | 0.015558 | 0.018976 | 0.03803 | 0.0032903 | 22.4809 | 12.327 | 12.2064 | 121.1871 | 120.9893 | 120.8843 | -0.1409 | 0.010205 | -0.022535 | -0.079245 | -0.04369 | -0.022922 | -0.10671 | -0.15041 | 0.051362 | 0.076579 | 22.6732 | 12.3987 | 12.3473 | -0.12125 | -0.22624 | 0.041849 | -121.1542 | 0.20247 | 0.11302 | 0.071167 | -121.1335 | -121.2172 | 121.3794 | 121.1815 | 121.0766 | 12.5193 | -121.2514 | 0.14857 | 0.16934 | 0.085547 | 0.16973 | -121.2609
2256.3125 | 121.2799 | -0.18768 | 121.1014 | 1.4211e-13 | -0.019404 | 0.023488 | 0.070842 | -0.0017222 | 0.073643 | -0.22823 | -0.004606 | 0.015345 | 0.018762 | 0.03803 | 0.0037175 | 22.4351 | 12.3133 | 12.1836 | 121.1917 | 120.9984 | 120.8935 | -0.1409 | 0.023941 | -0.017956 | -0.074666 | -0.04369 | -0.018344 | -0.11129 | -0.15041 | 0.046784 | 0.090313 | 22.6228 | 12.3712 | 12.3245 | -0.10294 | -0.20793 | 0.037271 | -121.1451 | 0.21162 | 0.11302 | 0.075746 | -121.1197 | -121.2127 | 121.3794 | 121.1861 | 121.0811 | 12.501 | -121.2423 | 0.14399 | 0.16934 | 0.07639 | 0.16973 | -121.2518
2258 | 121.2296 | -0.21057 | 121.1197 | 1.4211e-13 | -0.019404 | 0.023915 | 0.070629 | -0.0019358 | 0.073643 | -0.2206 | -0.0048196 | 0.015345 | 0.018762 | 0.037816 | 0.0030767 | 22.4626 | 12.2904 | 12.1744 | 121.2054 | 120.9984 | 120.898 | -0.12258 | 0.023941 | -0.017956 | -0.074666 | -0.04369 | -0.022922 | -0.10671 | -0.15499 | 0.087988 | 0.085737 | 22.6732 | 12.385 | 12.297 | -0.12125 | -0.22166 | 0.05558 | -121.1634 | 0.23451 | 0.1359 | 0.080325 | -121.1426 | -121.2264 | 121.416 | 121.209 | 121.1086 | 12.5009 | -121.2423 | 0.16688 | 0.18765 | 0.10386 | 0.19262 | -121.2747
2259.75 | 121.3806 | -0.14191 | 121.0831 | 1.4211e-13 | -0.019617 | 0.023701 | 0.070629 | -0.0021494 | 0.073643 | -0.23586 | -0.0048196 | 0.015131 | 0.018549 | 0.038243 | 0.0032903 | 22.339 | 12.1942 | 12.1515 | 121.2008 | 121.003 | 120.9026 | -0.15464 | 0.010205 | -0.013377 | -0.079245 | -0.04369 | -0.018344 | -0.10671 | -0.15041 | -0.012729 | 0.11778 | 22.4809 | 12.2934 | 12.3061 | -0.08005 | -0.18046 | -0.008505 | -121.1268 | 0.15211 | 0.062662 | 0.071167 | -121.1014 | -121.1898 | 121.3428 | 121.1449 | 121.0445 | 12.3361 | -121.2377 | 0.098217 | 0.12356 | 0.035193 | 0.12853 | -121.2335
2261.5 | 121.3715 | -0.15564 | 121.1014 | 1.4211e-13 | -0.018976 | 0.023915 | 0.070629 | -0.0019358 | 0.07343 | -0.23586 | -0.0043924 | 0.015131 | 0.018762 | 0.03803 | 0.0032903 | 22.3665 | 12.2034 | 12.1011 | 121.2146 | 121.0213 | 120.9163 | -0.13632 | 0.019362 | -0.013377 | -0.070087 | -0.048268 | -0.022922 | -0.11129 | -0.15499 | 0.01932 | 0.11321 | 22.5221 | 12.2568 | 12.2375 | -0.080044 | -0.18504 | 0.000649 | -121.1496 | 0.175 | 0.085553 | 0.084904 | -121.1243 | -121.2127 | 121.3702 | 121.177 | 121.072 | 12.359 | -121.2377 | 0.10737 | 0.13272 | 0.044347 | 0.14226 | -121.2564
2263.25 | 121.2616 | -0.21515 | 121.1609 | 1.4211e-13 | -0.019404 | 0.023915 | 0.070842 | -0.0012948 | 0.07343 | -0.23586 | -0.0048196 | 0.015345 | 0.018335 | 0.038243 | 0.0030767 | 22.3253 | 12.1668 | 12.092 | 121.2192 | 121.0213 | 120.9209 | -0.13632 | 0.019362 | -0.013377 | -0.074666 | -0.048268 | -0.027501 | -0.11129 | -0.15499 | 0.078829 | 0.058273 | 22.5404 | 12.3071 | 12.2283 | -0.13955 | -0.23997 | 0.060158 | -121.2092 | 0.23451 | 0.14048 | 0.080325 | -121.1884 | -121.2722 | 121.4343 | 121.2365 | 121.1361 | 12.3819 | -121.2972 | 0.16688 | 0.18765 | 0.10386 | 0.20177 | -121.3159
2264.9219 | 121.3852 | -0.15564 | 121.1334 | 1.4211e-13 | -0.01919 | 0.024129 | 0.070842 | -0.0017222 | 0.073643 | -0.23586 | -0.0043924 | 0.015131 | 0.018549 | 0.038243 | 0.0035039 | 22.2566 | 12.1118 | 12.0554 | 121.2192 | 121.0213 | 120.9255 | -0.13632 | 0.010205 | -0.017956 | -0.083823 | -0.04369 | -0.018344 | -0.10214 | -0.15041 | 0.01932 | 0.085739 | 22.4122 | 12.211 | 12.1917 | -0.11209 | -0.20792 | 0.005228 | -121.1771 | 0.16584 | 0.071817 | 0.066589 | -121.1518 | -121.2356 | 121.3748 | 121.177 | 121.0811 | 12.2675 | -121.2697 | 0.11195 | 0.1373 | 0.053504 | 0.13768 | -121.2838
2266.6562 | 121.3806 | -0.16022 | 121.0968 | 1.4211e-13 | -0.019404 | 0.024342 | 0.071056 | -0.0019358 | 0.07343 | -0.22823 | -0.0048196 | 0.014918 | 0.018335 | 0.03803 | 0.0030767 | 22.2841 | 12.066 | 12.0554 | 121.2146 | 121.0168 | 120.9255 | -0.17753 | 0.005626 | -0.022535 | -0.074666 | -0.04369 | -0.013765 | -0.10671 | -0.15957 | -0.017313 | 0.11778 | 22.4443 | 12.2156 | 12.2329 | -0.080046 | -0.1713 | 0.000647 | -121.1405 | 0.16584 | 0.085551 | 0.084904 | -121.1106 | -121.2035 | 121.3748 | 121.177 | 121.0857 | 12.2262 | -121.2743 | 0.11653 | 0.14645 | 0.053503 | 0.13768 | -121.2564
2268.3438 | 121.3074 | -0.19684 | 121.1517 | 1.4211e-13 | -0.019404 | 0.024129 | 0.071056 | -0.0019358 | 0.07343 | -0.23586 | -0.0048196 | 0.015131 | 0.018335 | 0.038457 | 0.0032903 | 22.3756 | 12.066 | 12.0691 | 121.2329 | 121.0351 | 120.9301 | -0.13632 | 0.014784 | -0.022535 | -0.088402 | -0.048268 | -0.018344 | -0.10671 | -0.15957 | 0.060518 | 0.081165 | 22.5725 | 12.2659 | 12.2054 | -0.11666 | -0.22165 | 0.037268 | -121.2 | 0.21162 | 0.10844 | 0.071168 | -121.1701 | -121.2584 | 121.4297 | 121.2319 | 121.1269 | 12.2629 | -121.2881 | 0.14857 | 0.17849 | 0.090124 | 0.1743 | -121.3113
2270.0781 | 121.3531 | -0.16937 | 121.1563 | 1.4211e-13 | -0.018976 | 0.024129 | 0.07127 | -0.0019358 | 0.073643 | -0.22823 | -0.004606 | 0.014918 | 0.018976 | 0.03803 | 0.0032903 | 22.3985 | 12.0614 | 12.0783 | 121.2466 | 121.0442 | 120.9438 | -0.13632 | 0.014784 | -0.017956 | -0.079245 | -0.052847 | -0.009187 | -0.11129 | -0.15499 | 0.033053 | 0.090322 | 22.5679 | 12.2476 | 12.2146 | -0.11208 | -0.2125 | 0.014382 | -121.2092 | 0.18416 | 0.090128 | 0.075746 | -121.1655 | -121.2676 | 121.416 | 121.2136 | 121.1132 | 12.2308 | -121.2926 | 0.11653 | 0.16019 | 0.05808 | 0.15142 | -121.3113
2271.8281 | 121.4172 | -0.17395 | 121.1472 | 1.4211e-13 | -0.018976 | 0.024129 | 0.070842 | -0.0019358 | 0.07343 | -0.23586 | -0.0043924 | 0.015345 | 0.018762 | 0.038243 | 0.0035039 | 22.4718 | 12.066 | 12.092 | 121.2466 | 121.0488 | 120.9484 | -0.13174 | 0.019362 | -0.017956 | -0.074666 | -0.048268 | -0.018344 | -0.10214 | -0.15957 | 0.042209 | 0.099477 | 22.6457 | 12.2659 | 12.2237 | -0.098348 | -0.19876 | 0.01438 | -121.1954 | 0.19331 | 0.099284 | 0.084904 | -121.1655 | -121.2493 | 121.4206 | 121.2228 | 121.1223 | 12.24 | -121.2789 | 0.12568 | 0.15561 | 0.071814 | 0.15599 | -121.3067
2273.5156 | 121.3028 | -0.20142 | 121.1929 | 1.4211e-13 | -0.018549 | 0.024342 | 0.07127 | -0.0021494 | 0.074071 | -0.23586 | -0.004606 | 0.015558 | 0.018762 | 0.038457 | 0.0030767 | 22.5725 | 12.034 | 12.0737 | 121.2649 | 121.058 | 120.9621 | -0.13632 | 0.010205 | -0.017956 | -0.070087 | -0.052847 | -0.018344 | -0.10671 | -0.15499 | 0.065096 | 0.072014 | 22.7739 | 12.2751 | 12.21 | -0.13497 | -0.2308 | 0.046425 | -121.2458 | 0.21162 | 0.13133 | 0.084904 | -121.2113 | -121.2996 | 121.4664 | 121.2594 | 121.1635 | 12.2354 | -121.3293 | 0.14857 | 0.18307 | 0.094702 | 0.18346 | -121.3479
2275.2656 | 121.2799 | -0.21057 | 121.1929 | 1.4211e-13 | -0.018763 | 0.02477 | 0.071483 | -0.0019358 | 0.074071 | -0.22823 | -0.0048196 | 0.015345 | 0.018549 | 0.03803 | 0.0030767 | 22.7007 | 12.0431 | 12.0645 | 121.2558 | 121.0625 | 120.9621 | -0.13174 | 0.019362 | -0.017956 | -0.083823 | -0.048268 | -0.018344 | -0.10671 | -0.15499 | 0.07883 | 0.062858 | 22.9113 | 12.2751 | 12.1963 | -0.13039 | -0.2308 | 0.05558 | -121.2412 | 0.22993 | 0.12675 | 0.071168 | -121.2113 | -121.2996 | 121.4664 | 121.2731 | 121.1727 | 12.2537 | -121.3247 | 0.1623 | 0.19223 | 0.10386 | 0.19262 | -121.3479
2276.9531 | 121.3303 | -0.19684 | 121.1838 | 1.4211e-13 | -0.018976 | 0.024983 | 0.071056 | -0.0021494 | 0.074071 | -0.2206 | -0.004606 | 0.015345 | 0.018549 | 0.03803 | 0.0030767 | 22.7739 | 11.9973 | 12.0142 | 121.2695 | 121.0671 | 120.9713 | -0.1409 | 0.010205 | -0.013377 | -0.079245 | -0.048268 | -0.018344 | -0.11129 | -0.15957 | 0.055939 | 0.085748 | 22.9708 | 12.211 | 12.1551 | -0.11665 | -0.21249 | 0.037268 | -121.232 | 0.20704 | 0.11759 | 0.080325 | -121.2021 | -121.2951 | 121.4664 | 121.264 | 121.1681 | 12.1942 | -121.3247 | 0.14857 | 0.17849 | 0.085545 | 0.18346 | -121.3433
2278.6875 | 121.3577 | -0.17395 | 121.2021 | 1.4211e-13 | -0.018976 | 0.024556 | 0.070842 | -0.0023632 | 0.073857 | -0.22823 | -0.0048196 | 0.015345 | 0.018335 | 0.038243 | 0.0030767 | 22.8518 | 11.9287 | 11.9913 | 121.2695 | 121.0763 | 120.9667 | -0.13632 | 0.019362 | -0.017956 | -0.074666 | -0.048268 | -0.013765 | -0.10671 | -0.15957 | 0.03763 | 0.067438 | 23.0257 | 12.1652 | 12.1276 | -0.1258 | -0.23538 | 0.01438 | -121.2504 | 0.19331 | 0.099284 | 0.084904 | -121.2159 | -121.3088 | 121.4435 | 121.2502 | 121.1407 | 12.1026 | -121.3384 | 0.12568 | 0.16018 | 0.067236 | 0.15599 | -121.3617
2280.4219 | 121.3394 | -0.2243 | 121.2204 | 1.4211e-13 | -0.018549 | 0.024983 | 0.071056 | -0.0021494 | 0.074284 | -0.23586 | -0.0043924 | 0.015131 | 0.018335 | 0.038457 | 0.0030767 | 22.8609 | 11.9241 | 11.9913 | 121.2741 | 121.0763 | 120.985 | -0.12716 | 0.014784 | -0.017956 | -0.083823 | -0.04369 | -0.013765 | -0.10671 | -0.16415 | 0.097142 | 0.053705 | 23.0852 | 12.2156 | 12.1184 | -0.14412 | -0.23538 | 0.060155 | -121.2641 | 0.23909 | 0.14048 | 0.080326 | -121.2342 | -121.3271 | 121.4984 | 121.3006 | 121.2093 | 12.1484 | -121.3476 | 0.18061 | 0.21054 | 0.11759 | 0.20635 | -121.3845
2282.1094 | 121.4722 | -0.15106 | 121.1792 | 1.4211e-13 | -0.018549 | 0.024983 | 0.07127 | -0.0023632 | 0.074284 | -0.22823 | -0.004606 | 0.015131 | 0.018122 | 0.038243 | 0.0030767 | 22.8884 | 11.892 | 12.0233 | 121.2833 | 121.0854 | 120.985 | -0.13174 | 0.019362 | -0.017956 | -0.074666 | -0.04369 | -0.018344 | -0.11129 | -0.16415 | 0.019321 | 0.10406 | 23.0395 | 12.1744 | 12.1551 | -0.093759 | -0.19418 | -0.013087 | -121.2229 | 0.17042 | 0.076396 | 0.089483 | -121.1975 | -121.2905 | 121.4343 | 121.2365 | 121.1361 | 12.0431 | -121.3109 | 0.10737 | 0.13272 | 0.039769 | 0.13311 | -121.3433
2283.8594 | 121.3577 | -0.19226 | 121.1929 | 1.4211e-13 | -0.018549 | 0.025411 | 0.071483 | -0.0019358 | 0.074498 | -0.22823 | -0.0048196 | 0.014918 | 0.018549 | 0.038457 | 0.0032903 | 22.9617 | 11.9012 | 12.0508 | 121.2878 | 121.0809 | 120.9942 | -0.13174 | 0.014784 | -0.013377 | -0.079245 | -0.039111 | -0.018344 | -0.097557 | -0.16415 | 0.06052 | 0.094906 | 23.1539 | 12.243 | 12.1825 | -0.11207 | -0.19875 | 0.028112 | -121.232 | 0.20704 | 0.11302 | 0.084904 | -121.2113 | -121.2905 | 121.4801 | 121.2731 | 121.1864 | 12.0935 | -121.3247 | 0.15315 | 0.17392 | 0.094704 | 0.17888 | -121.3571
2285.5938 | 121.3211 | -0.20599 | 121.2341 | 1.4211e-13 | -0.018335 | 0.025197 | 0.071483 | -0.0023632 | 0.074284 | -0.22823 | -0.0048196 | 0.014918 | 0.018122 | 0.038243 | 0.0032903 | 23.0395 | 11.9149 | 12.0874 | 121.2833 | 121.09 | 121.0033 | -0.13174 | 0.014784 | -0.017956 | -0.079245 | -0.04369 | -0.018344 | -0.10214 | -0.15499 | 0.074253 | 0.049129 | 23.2455 | 12.2934 | 12.2191 | -0.14411 | -0.23079 | 0.051003 | -121.2778 | 0.22078 | 0.12675 | 0.075746 | -121.2525 | -121.3363 | 121.4893 | 121.296 | 121.2093 | 12.1209 | -121.3659 | 0.1623 | 0.18765 | 0.10386 | 0.18804 | -121.3891
2287.2656 | 121.4676 | -0.15564 | 121.1655 | 1.4211e-13 | -0.018335 | 0.025197 | 0.071697 | -0.0019358 | 0.074498 | -0.23586 | -0.004606 | 0.015131 | 0.018549 | 0.03803 | 0.0035039 | 23.0715 | 11.947 | 12.1149 | 121.297 | 121.0946 | 120.9942 | -0.13174 | 0.010205 | -0.017956 | -0.079245 | -0.04369 | -0.018344 | -0.10671 | -0.15957 | 0.023899 | 0.13153 | 23.2272 | 12.2705 | 12.2466 | -0.070869 | -0.17129 | -0.00393 | -121.2092 | 0.16584 | 0.076395 | 0.080325 | -121.1838 | -121.2722 | 121.4526 | 121.2502 | 121.1498 | 12.1026 | -121.2972 | 0.11195 | 0.1373 | 0.048926 | 0.13768 | -121.325
2289.0156 | 121.4767 | -0.16479 | 121.2067 | 1.4211e-13 | -0.018122 | 0.024983 | 0.071483 | -0.0019358 | 0.074071 | -0.23586 | -0.004606 | 0.014704 | 0.018549 | 0.038243 | 0.0035039 | 23.0899 | 11.9653 | 12.1378 | 121.297 | 121.1038 | 121.0033 | -0.1409 | 0.014784 | -0.022535 | -0.074666 | -0.048268 | -0.013765 | -0.10214 | -0.15957 | 0.023896 | 0.09033 | 23.2547 | 12.3026 | 12.2787 | -0.10291 | -0.20333 | 0.005225 | -121.2549 | 0.17958 | 0.090129 | 0.084904 | -121.2204 | -121.3088 | 121.4618 | 121.2686 | 121.1681 | 12.1301 | -121.3476 | 0.11653 | 0.15103 | 0.062659 | 0.14226 | -121.3662
2290.7656 | 121.3486 | -0.19684 | 121.2204 | 1.4211e-13 | -0.018122 | 0.024983 | 0.071697 | -0.0019358 | 0.074712 | -0.2206 | -0.0050332 | 0.015345 | 0.018549 | 0.038243 | 0.0032903 | 23.1127 | 11.9973 | 12.1881 | 121.3016 | 121.1038 | 121.0171 | -0.13174 | 0.014784 | -0.017956 | -0.079245 | -0.052847 | -0.018344 | -0.10671 | -0.16415 | 0.065097 | 0.081175 | 23.3096 | 12.385 | 12.3199 | -0.11664 | -0.20333 | 0.032689 | -121.2732 | 0.21162 | 0.11759 | 0.084904 | -121.2387 | -121.3271 | 121.4984 | 121.3006 | 121.2139 | 12.1942 | -121.3521 | 0.14399 | 0.17849 | 0.090124 | 0.17888 | -121.3845
2292.5156 | 121.3531 | -0.2243 | 121.2341 | 1.4211e-13 | -0.018122 | 0.024983 | 0.071697 | -0.0021494 | 0.074498 | -0.23586 | -0.004606 | 0.014704 | 0.018549 | 0.038457 | 0.0030767 | 23.0624 | 11.9745 | 12.2019 | 121.3153 | 121.1129 | 121.0171 | -0.13174 | 0.014784 | -0.017956 | -0.079245 | -0.048268 | -0.022922 | -0.10214 | -0.16415 | 0.092563 | 0.081178 | 23.2867 | 12.4262 | 12.3336 | -0.12122 | -0.21706 | 0.060155 | -121.2824 | 0.23909 | 0.14506 | 0.084904 | -121.2571 | -121.3363 | 121.5396 | 121.3372 | 121.2414 | 12.1988 | -121.3659 | 0.17604 | 0.20138 | 0.12217 | 0.20635 | -121.3983
2294.2656 | 121.3989 | -0.18768 | 121.2296 | 1.4211e-13 | -0.017908 | 0.025624 | 0.071911 | -0.0021494 | 0.074498 | -0.2206 | -0.0048196 | 0.015345 | 0.018335 | 0.038671 | 0.0030767 | 23.1173 | 11.9745 | 12.2248 | 121.3199 | 121.1175 | 121.0262 | -0.13632 | 0.014784 | -0.013377 | -0.079245 | -0.048268 | -0.022922 | -0.11129 | -0.15957 | 0.051363 | 0.090334 | 23.305 | 12.4124 | 12.3611 | -0.11206 | -0.20332 | 0.028113 | -121.2778 | 0.20247 | 0.10844 | 0.080325 | -121.2525 | -121.3408 | 121.5076 | 121.3052 | 121.2139 | 12.1621 | -121.3659 | 0.13941 | 0.16476 | 0.07639 | 0.17431 | -121.3891
2295.9375 | 121.4447 | -0.18768 | 121.225 | 1.4211e-13 | -0.017908 | 0.025411 | 0.072338 | -0.0017222 | 0.074498 | -0.22823 | -0.004606 | 0.014918 | 0.018335 | 0.038671 | 0.0035039 | 23.1768 | 11.9928 | 12.2568 | 121.3199 | 121.1221 | 121.0308 | -0.13632 | 0.010205 | -0.027113 | -0.079245 | -0.04369 | -0.018344 | -0.10671 | -0.15957 | 0.051363 | 0.094911 | 23.3645 | 12.4445 | 12.3931 | -0.1029 | -0.19417 | 0.028113 | -121.2687 | 0.19789 | 0.10844 | 0.080325 | -121.2433 | -121.3317 | 121.5076 | 121.3098 | 121.2185 | 12.1805 | -121.3613 | 0.14399 | 0.16934 | 0.080969 | 0.16057 | -121.3845
2297.6719 | 121.4859 | -0.15564 | 121.225 | 1.4211e-13 | -0.017908 | 0.025411 | 0.072124 | -0.0023632 | 0.074712 | -0.23586 | -0.0048196 | 0.015345 | 0.018549 | 0.038671 | 0.0032903 | 23.2638 | 11.9836 | 12.2614 | 121.3245 | 121.1266 | 121.0354 | -0.12716 | 0.014784 | -0.017956 | -0.088402 | -0.052847 | -0.018344 | -0.10671 | -0.16415 | 0.028478 | 0.099489 | 23.4195 | 12.417 | 12.3885 | -0.098326 | -0.18959 | -0.008509 | -121.2778 | 0.17042 | 0.067238 | 0.075747 | -121.2433 | -121.3317 | 121.4801 | 121.2823 | 121.191 | 12.1392 | -121.3521 | 0.10279 | 0.1373 | 0.048926 | 0.13768 | -121.3891
2299.4219 | 121.5134 | -0.14191 | 121.2433 | 1.4211e-13 | -0.017481 | 0.025838 | 0.072338 | -0.0021494 | 0.074498 | -0.24349 | -0.0048196 | 0.015345 | 0.018335 | 0.038671 | 0.0032903 | 23.2822 | 11.9836 | 12.2568 | 121.3245 | 121.1266 | 121.0308 | -0.1409 | 0.014784 | -0.017956 | -0.083823 | -0.048268 | -0.013765 | -0.10671 | -0.15957 | 0.001008 | 0.081179 | 23.4241 | 12.3987 | 12.3977 | -0.11664 | -0.21248 | -0.017663 | -121.2916 | 0.15669 | 0.058084 | 0.075747 | -121.2571 | -121.35 | 121.4664 | 121.2686 | 121.1727 | 12.1255 | -121.3842 | 0.093639 | 0.12814 | 0.035193 | 0.12395 | -121.4029
2301.0938 | 121.4172 | -0.21057 | 121.257 | 1.4211e-13 | -0.017053 | 0.025624 | 0.072338 | -0.0019358 | 0.074712 | -0.22823 | -0.0048196 | 0.014918 | 0.018335 | 0.038671 | 0.0032903 | 23.3279 | 11.9836 | 12.2797 | 121.3336 | 121.1358 | 121.0354 | -0.12716 | 0.010205 | -0.022535 | -0.074666 | -0.048268 | -0.018344 | -0.10214 | -0.15499 | 0.083409 | 0.076603 | 23.5385 | 12.4903 | 12.4069 | -0.12121 | -0.22163 | 0.05558 | -121.3053 | 0.22078 | 0.1359 | 0.080325 | -121.2754 | -121.3592 | 121.5442 | 121.3464 | 121.246 | 12.1942 | -121.3842 | 0.1623 | 0.19223 | 0.10844 | 0.18804 | -121.412
2302.7812 | 121.5042 | -0.15106 | 121.225 | 1.4211e-13 | -0.017481 | 0.026052 | 0.072338 | -0.0017222 | 0.074712 | -0.22823 | -0.0048196 | 0.014918 | 0.018335 | 0.038671 | 0.0032903 | 23.3829 | 12.0111 | 12.3072 | 121.3428 | 121.145 | 121.0491 | -0.13174 | 0.014784 | -0.017956 | -0.079245 | -0.052847 | -0.022922 | -0.10671 | -0.15957 | 0.019321 | 0.1178 | 23.5339 | 12.4582 | 12.4389 | -0.08001 | -0.17585 | -0.008508 | -121.2778 | 0.16585 | 0.071817 | 0.080325 | -121.2479 | -121.3317 | 121.4938 | 121.296 | 121.2002 | 12.1621 | -121.3567 | 0.098215 | 0.12814 | 0.044348 | 0.13311 | -121.3845
2304.5312 | 121.3669 | -0.21973 | 121.2708 | 1.4211e-13 | -0.017267 | 0.026052 | 0.072766 | -0.0019358 | 0.074712 | -0.23586 | -0.0048196 | 0.015345 | 0.018335 | 0.038884 | 0.0032903 | 23.447 | 12.0706 | 12.3575 | 121.3519 | 121.145 | 121.0537 | -0.13174 | 0.014784 | -0.017956 | -0.074666 | -0.048268 | -0.022922 | -0.10214 | -0.16415 | 0.087986 | 0.081184 | 23.6667 | 12.5773 | 12.4893 | -0.12579 | -0.21705 | 0.055578 | -121.319 | 0.23451 | 0.14506 | 0.089483 | -121.2937 | -121.3729 | 121.5717 | 121.3647 | 121.2734 | 12.2903 | -121.4025 | 0.17146 | 0.19681 | 0.11759 | 0.20177 | -121.4349
2306.2031 | 117.8558 | -25.1404 | 92.4408 | 1.4211e-13 | -0.021968 | 0.022206 | 0.06721 | 0.00084184 | 0.08048 | -0.23586 | -0.0050332 | 0.015131 | 0.018335 | 0.038671 | 0.0032903 | -1.2992 | -10.0669 | -12.9649 | 88.8088 | 88.6758 | 88.6326 | -28.6447 | 0.033099 | 0.004938 | -0.051772 | -0.025376 | 0.013707 | -0.11129 | -0.1321 | -3.5043 | -3.632 | 23.8412 | 12.1754 | 15.6798 | -3.765 | -3.8082 | 25.0083 | -92.4662 | 25.1735 | 25.0886 | 0.080325 | -92.4271 | -92.5521 | 113.9491 | 113.8162 | 113.773 | 15.0734 | -121.0855 | 25.115 | 25.1541 | 25.0291 | 25.1453 | -92.5729
2307.9375 | 115.3336 | -37.6053 | 77.1286 | 1.4211e-13 | -0.022395 | 0.020923 | 0.065928 | 0.0016964 | 0.081121 | -0.2206 | -0.0048196 | 0.015345 | 0.018549 | 0.038671 | 0.0037175 | -6.427 | -14.554 | -18.0285 | 81.5841 | 81.4182 | 81.4442 | -34.4508 | 0.046835 | 0.009516 | -0.051772 | -0.020797 | 0.013707 | -0.10671 | -0.1321 | 3.1545 | 4.4555 | 31.1783 | 19.5768 | 16.4223 | 4.2896 | 4.3156 | 37.4732 | -77.1494 | 37.6521 | 37.5535 | 0.080325 | -77.1149 | -77.2353 | 119.1893 | 119.0235 | 119.0495 | 23.0513 | -111.5794 | 37.5845 | 37.619 | 37.4986 | 37.6148 | -77.2607
2309.6875 | 120.1538 | -0.3479 | 119.902 | 1.4211e-13 | -0.017267 | 0.026265 | 0.072124 | -0.0021494 | 0.074284 | -0.2206 | -0.0048196 | 0.015131 | 0.018549 | 0.038884 | 0.0037175 | 23.2272 | 11.8554 | 12.1744 | 119.9922 | 119.7988 | 119.7076 | -0.25079 | 0.014784 | -0.008798 | -0.074666 | -0.034533 | -0.009187 | -0.11129 | -0.15041 | 0.097107 | 0.090115 | 23.5751 | 12.5223 | 12.4252 | -0.10328 | -0.19445 | 0.19749 | -119.9366 | 0.36268 | 0.27323 | 0.075746 | -119.9112 | -120.0133 | 120.3401 | 120.1467 | 120.0555 | 12.2033 | -120.1528 | 0.31337 | 0.33871 | 0.23661 | 0.3391 | -120.0525
2311.375 | 120.3186 | -0.21057 | 120.2362 | 1.4211e-13 | -0.017053 | 0.026265 | 0.072338 | -0.0019358 | 0.074284 | -0.2206 | -0.0050332 | 0.014918 | 0.018122 | 0.03803 | 0.0035039 | 23.392 | 11.979 | 12.2934 | 120.2714 | 120.0827 | 119.9869 | -0.13632 | 0.019362 | -0.017956 | -0.065509 | -0.04369 | -0.018344 | -0.10214 | -0.15499 | 0.074251 | 0.03523 | 23.6026 | 12.504 | 12.4298 | -0.15355 | -0.24932 | 0.05558 | -120.2799 | 0.22993 | 0.14506 | 0.089482 | -120.2545 | -120.3383 | 120.482 | 120.2932 | 120.1975 | 12.1896 | -120.3725 | 0.16688 | 0.19223 | 0.10844 | 0.19262 | -120.3912
2313.125 | 120.4147 | -0.20142 | 120.3186 | 1.4211e-13 | -0.01684 | 0.026479 | 0.072338 | -0.0019358 | 0.074498 | -0.22823 | -0.004606 | 0.015131 | 0.018122 | 0.038457 | 0.0030767 | 23.4332 | 11.979 | 12.3346 | 120.3538 | 120.1651 | 120.0693 | -0.13632 | 0.014784 | -0.017956 | -0.079245 | -0.04369 | -0.018344 | -0.10214 | -0.15499 | 0.065096 | 0.035243 | 23.6347 | 12.5361 | 12.471 | -0.15353 | -0.2493 | 0.046425 | -120.3623 | 0.2162 | 0.12217 | 0.075746 | -120.3369 | -120.4207 | 120.5553 | 120.3665 | 120.2707 | 12.1804 | -120.4549 | 0.15773 | 0.18307 | 0.09928 | 0.18346 | -120.4736
2314.875 | 120.5795 | -0.16479 | 120.3049 | 1.4211e-13 | -0.016412 | 0.026479 | 0.072979 | -0.0017222 | 0.074284 | -0.23586 | -0.0048196 | 0.014918 | 0.018122 | 0.038671 | 0.0032903 | 23.3783 | 12.034 | 12.3758 | 120.4179 | 120.22 | 120.1288 | -0.13632 | 0.019362 | -0.017956 | -0.070087 | -0.04369 | -0.018344 | -0.10671 | -0.15499 | 0.028475 | 0.11307 | 23.5431 | 12.5406 | 12.5122 | -0.084848 | -0.17605 | 0.009804 | -120.3486 | 0.18416 | 0.094708 | 0.084904 | -120.3232 | -120.4116 | 120.5827 | 120.3848 | 120.2936 | 12.1988 | -120.4412 | 0.1211 | 0.14645 | 0.058081 | 0.14684 | -120.4599
2316.5469 | 120.6162 | -0.15106 | 120.3827 | 1.4211e-13 | -0.01684 | 0.026265 | 0.072979 | -0.0021494 | 0.074071 | -0.23586 | -0.004606 | 0.014918 | 0.018335 | 0.038671 | 0.0032903 | 23.3783 | 12.066 | 12.3987 | 120.4637 | 120.2704 | 120.1792 | -0.13632 | 0.023941 | -0.013377 | -0.070087 | -0.04369 | -0.013765 | -0.11129 | -0.15957 | 0.014742 | 0.081038 | 23.5294 | 12.5498 | 12.5351 | -0.1123 | -0.2035 | -0.008508 | -120.4264 | 0.175 | 0.080975 | 0.089483 | -120.3965 | -120.494 | 120.6148 | 120.4215 | 120.3302 | 12.2171 | -120.519 | 0.10737 | 0.1373 | 0.039769 | 0.13769 | -120.5423
2318.2812 | 120.6436 | -0.16022 | 120.401 | 1.4211e-13 | -0.016199 | 0.026479 | 0.072766 | -0.0021494 | 0.074284 | -0.24349 | -0.004606 | 0.014918 | 0.018335 | 0.038457 | 0.0035039 | 23.3096 | 12.0843 | 12.417 | 120.5004 | 120.3116 | 120.2067 | -0.13174 | 0.019362 | -0.008798 | -0.074666 | -0.048268 | -0.022922 | -0.10671 | -0.15499 | 0.028476 | 0.099355 | 23.4698 | 12.5773 | 12.5488 | -0.0894 | -0.19434 | 0.005226 | -120.4493 | 0.17958 | 0.085551 | 0.080325 | -120.4239 | -120.5077 | 120.6606 | 120.4718 | 120.3669 | 12.2446 | -120.5327 | 0.11195 | 0.1373 | 0.053503 | 0.15142 | -120.556
2319.9844 | 120.607 | -0.19226 | 120.4422 | 1.4211e-13 | -0.01684 | 0.026693 | 0.073193 | -0.0021494 | 0.074284 | -0.22823 | -0.0048196 | 0.015131 | 0.018549 | 0.038457 | 0.0032903 | 23.2409 | 12.066 | 12.4216 | 120.537 | 120.3299 | 120.2479 | -0.13632 | 0.010205 | -0.017956 | -0.065509 | -0.039111 | -0.013765 | -0.11129 | -0.15499 | 0.055941 | 0.094783 | 23.4332 | 12.6139 | 12.5579 | -0.11228 | -0.19433 | 0.03727 | -120.4813 | 0.20247 | 0.12675 | 0.089482 | -120.456 | -120.5535 | 120.7292 | 120.5222 | 120.4401 | 12.2583 | -120.5785 | 0.15315 | 0.1785 | 0.080968 | 0.1743 | -120.5972
2321.7344 | 120.6848 | -0.1831 | 120.4971 | 1.4211e-13 | -0.016199 | 0.026693 | 0.073193 | -0.0021494 | 0.074284 | -0.23586 | -0.004606 | 0.014918 | 0.018335 | 0.039312 | 0.0032903 | 23.2226 | 12.066 | 12.4537 | 120.569 | 120.3757 | 120.2799 | -0.13632 | 0.023941 | -0.013377 | -0.074666 | -0.034533 | -0.004608 | -0.10671 | -0.15957 | 0.046785 | 0.0719 | 23.4057 | 12.6368 | 12.59 | -0.12143 | -0.21721 | 0.023535 | -120.5317 | 0.20705 | 0.10844 | 0.084904 | -120.5017 | -120.6038 | 120.7521 | 120.5588 | 120.463 | 12.2491 | -120.6335 | 0.14857 | 0.1785 | 0.076391 | 0.16973 | -120.6567
2323.5 | 116.1255 | -37.0743 | 78.891 | 1.4211e-13 | -0.02154 | 0.021564 | 0.067637 | 0.0014828 | 0.081549 | -0.22823 | -0.0048196 | 0.014918 | 0.018122 | 0.038671 | 0.0035039 | -2.9978 | -11.0559 | -13.9905 | 86.9133 | 86.5741 | 86.8973 | -30.6182 | 0.042256 | 0.004938 | -0.051772 | -0.020797 | 0.009128 | -0.11587 | -0.1321 | 6.4561 | 8.0223 | 34.0765 | 23.0838 | 16.6277 | 7.6831 | 8.0063 | 36.9422 | -78.9118 | 37.1165 | 37.0225 | 0.080325 | -78.8819 | -79.0069 | 123.9876 | 123.6484 | 123.9716 | 26.0184 | -109.5092 | 37.0535 | 37.0834 | 36.9584 | 37.0792 | -79.0231
2325.25 | 115.4114 | -38.9969 | 76.149 | 1.4211e-13 | -0.022609 | 0.020923 | 0.065928 | 0.0019102 | 0.08219 | -0.23586 | -0.0048196 | 0.014704 | 0.018122 | 0.038884 | 0.0035039 | -8.2446 | -15.7032 | -19.3288 | 79.2674 | 79.1013 | 79.132 | -36.4151 | 0.042256 | 0.018674 | -0.042615 | -0.016219 | 0.018285 | -0.12045 | -0.12294 | 2.5817 | 3.1184 | 30.7523 | 19.6681 | 17.0864 | 2.9523 | 2.983 | 38.8739 | -76.1652 | 39.0391 | 38.9543 | 0.080324 | -76.1307 | -76.2694 | 118.2643 | 118.0982 | 118.1289 | 23.2937 | -112.5641 | 38.9807 | 39.0152 | 38.8764 | 39.0156 | -76.2719
2326.9375 | 119.8791 | -0.16022 | 119.6274 | 1.4211e-13 | -0.015985 | 0.026479 | 0.073193 | -0.0019358 | 0.073643 | -0.24349 | -0.0048196 | 0.014918 | 0.018335 | 0.038457 | 0.0037175 | 23.0029 | 11.892 | 12.3529 | 119.6991 | 119.5011 | 119.4054 | -0.15921 | 0.023941 | -0.017956 | -0.079245 | -0.04369 | -0.022922 | -0.11129 | -0.15499 | 0.001002 | 0.071758 | 23.1631 | 12.5132 | 12.5122 | -0.12625 | -0.22198 | 0.005226 | -119.6711 | 0.18416 | 0.080972 | 0.075746 | -119.6503 | -119.7387 | 119.8594 | 119.6613 | 119.5656 | 12.0523 | -119.7866 | 0.11653 | 0.1373 | 0.048924 | 0.14226 | -119.7824
2328.6875 | 119.9661 | -0.21057 | 119.87 | 1.4211e-13 | -0.015558 | 0.026052 | 0.072979 | -0.0019358 | 0.073857 | -0.22823 | -0.0048196 | 0.015345 | 0.017908 | 0.038671 | 0.0030767 | 22.9571 | 11.9745 | 12.4033 | 119.9006 | 119.7118 | 119.6206 | -0.13632 | 0.019362 | -0.017956 | -0.079245 | -0.048268 | -0.009187 | -0.10214 | -0.15499 | 0.074251 | 0.030592 | 23.1677 | 12.6139 | 12.5396 | -0.15823 | -0.2494 | 0.05558 | -119.9183 | 0.22993 | 0.13133 | 0.075746 | -119.8792 | -119.9721 | 120.1112 | 119.9223 | 119.8312 | 12.185 | -120.0063 | 0.1623 | 0.20138 | 0.10844 | 0.19262 | -120.025
2330.4219 | 120.0531 | -0.20599 | 119.9478 | 1.4211e-13 | -0.015985 | 0.026693 | 0.073193 | -0.0015084 | 0.074284 | -0.22823 | -0.0048196 | 0.015131 | 0.018335 | 0.038884 | 0.0032903 | 22.9342 | 12.0843 | 12.4537 | 120.0013 | 119.8125 | 119.7213 | -0.13632 | 0.019362 | -0.017956 | -0.065509 | -0.039111 | -0.013765 | -0.11129 | -0.15957 | 0.069674 | 0.053496 | 23.1402 | 12.6597 | 12.59 | -0.13532 | -0.22649 | 0.046424 | -119.9869 | 0.22536 | 0.14049 | 0.094061 | -119.9616 | -120.0591 | 120.2073 | 120.0185 | 119.9273 | 12.2903 | -120.0841 | 0.16688 | 0.19223 | 0.094701 | 0.18804 | -120.1074
2332.1719 | 120.2133 | -0.16937 | 119.9799 | 1.4211e-13 | -0.015771 | 0.026479 | 0.073407 | -0.0023632 | 0.073857 | -0.23586 | -0.0043924 | 0.014918 | 0.018335 | 0.038671 | 0.0032903 | 22.9433 | 12.0111 | 12.4491 | 120.07 | 119.872 | 119.7809 | -0.1409 | 0.010205 | -0.022535 | -0.079245 | -0.04369 | -0.009187 | -0.10671 | -0.15957 | 0.028474 | 0.090129 | 23.1127 | 12.6185 | 12.59 | -0.10783 | -0.19901 | 0.009803 | -120.0235 | 0.17958 | 0.090128 | 0.080325 | -119.989 | -120.0866 | 120.2394 | 120.0414 | 119.9502 | 12.1805 | -120.1208 | 0.12568 | 0.16019 | 0.062659 | 0.14684 | -120.1394
2333.8594 | 119.8563 | -0.20599 | 119.7418 | 1.4211e-13 | -0.015771 | 0.026265 | 0.073407 | -0.0021494 | 0.073643 | -0.23586 | -0.0043924 | 0.015345 | 0.018335 | 0.038457 | 0.0032903 | 22.7144 | 11.9378 | 12.3529 | 119.7266 | 119.5378 | 119.4466 | -0.17753 | 0.010205 | -0.022535 | -0.079245 | -0.04369 | -0.018344 | -0.11587 | -0.15041 | 0.028464 | -0.015213 | 22.9204 | 12.5589 | 12.5305 | -0.20406 | -0.29521 | 0.055582 | -119.7855 | 0.2162 | 0.12675 | 0.071167 | -119.7602 | -119.8577 | 119.9326 | 119.7438 | 119.6526 | 12.1438 | -119.9194 | 0.1623 | 0.18765 | 0.090122 | 0.18346 | -119.8922
2335.5938 | 120.0668 | -0.19226 | 119.9432 | 1.4211e-13 | -0.015344 | 0.026479 | 0.07362 | -0.0021494 | 0.073857 | -0.24349 | -0.0048196 | 0.015131 | 0.018122 | 0.038671 | 0.0035039 | 22.7739 | 11.9836 | 12.4125 | 120.015 | 119.8217 | 119.7351 | -0.1409 | 0.023941 | -0.017956 | -0.074666 | -0.04369 | -0.009187 | -0.10671 | -0.15957 | 0.051362 | 0.071809 | 22.9662 | 12.6047 | 12.5534 | -0.12158 | -0.20817 | 0.032691 | -119.9869 | 0.2162 | 0.11759 | 0.084904 | -119.9524 | -120.05 | 120.2073 | 120.0139 | 119.9273 | 12.1759 | -120.0841 | 0.14857 | 0.18307 | 0.085547 | 0.1743 | -120.1028
2337.3281 | 116.391 | -27.5208 | 88.6414 | 1.4211e-13 | -0.019617 | 0.022847 | 0.068706 | 0.00041444 | 0.078557 | -0.22823 | -0.004606 | 0.015345 | 0.018122 | 0.038457 | 0.0030767 | 2.4322 | -5.9508 | -8.1898 | 93.0117 | 92.8838 | 92.8266 | -23.7636 | 0.037677 | 0.004938 | -0.056351 | -0.020797 | 0.004549 | -0.12045 | -0.13668 | 3.7572 | 4.3704 | 29.9529 | 19.331 | 15.5738 | 4.2425 | 4.1853 | 27.3841 | -88.6622 | 27.5584 | 27.4644 | 0.080325 | -88.6368 | -88.7618 | 120.5325 | 120.4046 | 120.3474 | 21.57 | -112.4049 | 27.5 | 27.5253 | 27.4003 | 27.5257 | -88.778
2339.0156 | 119.7968 | -0.17853 | 119.6091 | 1.4211e-13 | -0.015344 | 0.026265 | 0.07362 | -0.0021494 | 0.07343 | -0.2206 | -0.004606 | 0.014918 | 0.018549 | 0.038671 | 0.0035039 | 22.6458 | 11.9195 | 12.3392 | 119.6671 | 119.4782 | 119.3779 | -0.1409 | 0.023941 | -0.017956 | -0.074666 | -0.04369 | -0.009187 | -0.10671 | -0.15499 | 0.037629 | 0.058019 | 22.8243 | 12.5177 | 12.4801 | -0.13083 | -0.23114 | 0.023537 | -119.6528 | 0.20247 | 0.10386 | 0.080325 | -119.6183 | -119.7158 | 119.8456 | 119.6568 | 119.5565 | 12.098 | -119.75 | 0.13484 | 0.16934 | 0.071814 | 0.16057 | -119.7641
2340.75 | 120.0119 | -0.16022 | 119.7464 | 1.4211e-13 | -0.01513 | 0.026906 | 0.073407 | -0.0023632 | 0.071934 | -0.22823 | -0.0050332 | 0.014704 | 0.018122 | 0.038671 | 0.0030767 | 20.0956 | 11.9012 | 12.3438 | 119.8411 | 119.6614 | 119.5565 | -0.14548 | 0.023941 | -0.008798 | -0.074666 | -0.04369 | -0.013765 | -0.11587 | -0.16415 | 0.014739 | 0.094669 | 20.2558 | 12.504 | 12.4893 | -0.085005 | -0.1899 | -0.003932 | -119.7901 | 0.18416 | 0.085551 | 0.089483 | -119.7602 | -119.8623 | 120.0013 | 119.8216 | 119.7167 | 12.0614 | -119.8919 | 0.11653 | 0.14645 | 0.044345 | 0.15142 | -119.9105
2342.5 | 120.0531 | -0.17395 | 119.8288 | 1.4211e-13 | -0.01513 | 0.026906 | 0.074048 | -0.0019358 | 0.071507 | -0.22823 | -0.0048196 | 0.014918 | 0.018335 | 0.038884 | 0.0030767 | 18.4703 | 11.8875 | 12.3484 | 119.9372 | 119.7392 | 119.6435 | -0.1409 | 0.02852 | -0.017956 | -0.074666 | -0.039111 | -0.013765 | -0.10671 | -0.16415 | 0.033051 | 0.10842 | 18.6442 | 12.5223 | 12.4893 | -0.08956 | -0.1853 | 0.009801 | -119.8679 | 0.20247 | 0.099284 | 0.089483 | -119.8426 | -119.9355 | 120.1112 | 119.9132 | 119.8174 | 12.0614 | -119.9697 | 0.13484 | 0.16018 | 0.067236 | 0.15599 | -119.9929
2344.25 | 120.0577 | -0.18768 | 119.9112 | 1.4211e-13 | -0.01513 | 0.027547 | 0.074048 | -0.0021494 | 0.070652 | -0.22823 | -0.004606 | 0.015131 | 0.017908 | 0.039098 | 0.0032903 | 17.6828 | 11.8875 | 12.3667 | 119.983 | 119.7942 | 119.703 | -0.13632 | 0.019362 | -0.013377 | -0.079245 | -0.04369 | -0.004608 | -0.10671 | -0.15499 | 0.051363 | 0.071804 | 17.8705 | 12.5544 | 12.503 | -0.11701 | -0.20818 | 0.032692 | -119.9549 | 0.20704 | 0.10844 | 0.075746 | -119.9158 | -120.0179 | 120.1707 | 119.9819 | 119.8907 | 12.0751 | -120.0475 | 0.14399 | 0.18307 | 0.080969 | 0.17431 | -120.0662
2345.9219 | 120.0943 | -0.19684 | 119.9524 | 1.4211e-13 | -0.014703 | 0.027761 | 0.074261 | -0.0019358 | 0.070652 | -0.2206 | -0.0048196 | 0.014918 | 0.018335 | 0.038884 | 0.0030767 | 17.5958 | 11.8966 | 12.3804 | 120.0288 | 119.84 | 119.7488 | -0.14548 | 0.023941 | -0.022535 | -0.079245 | -0.04369 | -0.004608 | -0.10214 | -0.15957 | 0.05136 | 0.076389 | 17.7926 | 12.5773 | 12.5259 | -0.11242 | -0.20359 | 0.037268 | -119.9961 | 0.22078 | 0.11759 | 0.080325 | -119.957 | -120.0545 | 120.2256 | 120.0368 | 119.9456 | 12.0935 | -120.0979 | 0.15315 | 0.19223 | 0.094702 | 0.1743 | -120.112
2347.6719 | 120.1492 | -0.20142 | 120.0073 | 1.4211e-13 | -0.014703 | 0.027334 | 0.074261 | -0.0023632 | 0.070866 | -0.22823 | -0.0048196 | 0.014918 | 0.018335 | 0.038884 | 0.0032903 | 17.4996 | 11.9287 | 12.4079 | 120.0746 | 119.8766 | 119.7854 | -0.1409 | 0.019362 | -0.013377 | -0.079245 | -0.04369 | -2.9e-05 | -0.10214 | -0.16415 | 0.060517 | 0.067241 | 17.7011 | 12.6093 | 12.5488 | -0.13072 | -0.2219 | 0.037267 | -120.051 | 0.22078 | 0.12217 | 0.084904 | -120.0074 | -120.1095 | 120.276 | 120.078 | 119.9868 | 12.1301 | -120.1482 | 0.15773 | 0.20139 | 0.09928 | 0.18804 | -120.1715
2349.4375 | 120.2545 | -0.16479 | 120.0073 | 1.4211e-13 | -0.014917 | 0.02712 | 0.074048 | -0.0017222 | 0.071079 | -0.22823 | -0.0048196 | 0.014918 | 0.018122 | 0.039098 | 0.0035039 | 17.8384 | 11.9287 | 12.4125 | 120.1066 | 119.9224 | 119.8221 | -0.13632 | 0.023941 | -0.00422 | -0.065509 | -0.04369 | -0.004608 | -0.11129 | -0.15499 | 0.028475 | 0.09929 | 18.0032 | 12.5773 | 12.5488 | -0.084931 | -0.18527 | 0.009804 | -120.051 | 0.18874 | 0.099286 | 0.089482 | -120.0119 | -120.1186 | 120.2714 | 120.0872 | 119.9869 | 12.0935 | -120.1436 | 0.1211 | 0.16019 | 0.053502 | 0.16057 | -120.1623
2351.1094 | 120.1996 | -0.21515 | 120.0668 | 1.4211e-13 | -0.014703 | 0.027547 | 0.074261 | -0.0021494 | 0.071079 | -0.22823 | -0.0048196 | 0.014704 | 0.018335 | 0.038671 | 0.0030767 | 17.3028 | 11.9241 | 12.4308 | 120.1432 | 119.9499 | 119.8587 | -0.13174 | 0.019362 | -0.008798 | -0.065509 | -0.034533 | -0.004608 | -0.11587 | -0.15499 | 0.083408 | 0.076408 | 17.5179 | 12.6459 | 12.5625 | -0.11697 | -0.20815 | 0.060158 | -120.1014 | 0.23451 | 0.14964 | 0.089482 | -120.0714 | -120.1827 | 120.3584 | 120.165 | 120.0738 | 12.1392 | -120.1986 | 0.18062 | 0.21054 | 0.099277 | 0.20635 | -120.2218
2352.8438 | 120.2408 | -0.20599 | 120.0897 | 1.4211e-13 | -0.014276 | 0.027547 | 0.074261 | -0.0021494 | 0.070438 | -0.22823 | -0.004606 | 0.014918 | 0.018335 | 0.038884 | 0.0028629 | 16.8449 | 11.9516 | 12.4216 | 120.1707 | 119.9865 | 119.8907 | -0.14548 | 0.023941 | -0.017956 | -0.070087 | -0.034533 | -0.009187 | -0.10671 | -0.15957 | 0.060516 | 0.08099 | 17.0509 | 12.6276 | 12.5671 | -0.10322 | -0.19899 | 0.046424 | -120.1243 | 0.22994 | 0.13591 | 0.089483 | -120.0989 | -120.1964 | 120.3767 | 120.1925 | 120.0967 | 12.1576 | -120.2352 | 0.17146 | 0.19681 | 0.09928 | 0.18804 | -120.2493
2354.5938 | 120.369 | -0.16479 | 120.0943 | 1.4211e-13 | -0.014703 | 0.027761 | 0.074261 | -0.0019358 | 0.070438 | -0.22823 | -0.0048196 | 0.014918 | 0.018335 | 0.038671 | 0.0032903 | 16.9548 | 11.9928 | 12.4399 | 120.2028 | 120.0186 | 119.9182 | -0.1409 | 0.019362 | -0.013377 | -0.070087 | -0.029954 | -2.9e-05 | -0.11129 | -0.15499 | 0.023896 | 0.10846 | 17.1196 | 12.6047 | 12.5808 | -0.075749 | -0.17609 | 0.009804 | -120.1243 | 0.18416 | 0.094708 | 0.084904 | -120.0943 | -120.2056 | 120.3676 | 120.1833 | 120.083 | 12.1576 | -120.2352 | 0.13484 | 0.16477 | 0.053502 | 0.15142 | -120.2493
2356.3281 | 120.2728 | -0.22888 | 120.1401 | 1.4211e-13 | -0.014703 | 0.027975 | 0.074475 | -0.0021494 | 0.070225 | -0.22823 | -0.0050332 | 0.015131 | 0.018335 | 0.039098 | 0.0028629 | 16.703 | 11.9836 | 12.4628 | 120.2257 | 120.0414 | 119.9503 | -0.13632 | 0.010205 | -0.008798 | -0.079245 | -0.034533 | -0.004608 | -0.10671 | -0.15041 | 0.092562 | 0.085576 | 16.9319 | 12.6917 | 12.5991 | -0.098631 | -0.18982 | 0.07847 | -120.1746 | 0.23909 | 0.14964 | 0.071167 | -120.1447 | -120.2468 | 120.4545 | 120.2703 | 120.1791 | 12.2125 | -120.2764 | 0.19435 | 0.22427 | 0.12217 | 0.22008 | -120.2905
2358.0156 | 120.282 | -0.21057 | 120.1859 | 1.4211e-13 | -0.014489 | 0.027761 | 0.074689 | -0.0021494 | 0.070225 | -0.22823 | -0.005247 | 0.015131 | 0.017908 | 0.039098 | 0.0032903 | 16.3734 | 12.0065 | 12.4857 | 120.2623 | 120.0598 | 119.9777 | -0.13632 | 0.023941 | -0.00422 | -0.079245 | -0.034533 | -0.013765 | -0.11129 | -0.15499 | 0.074251 | 0.076427 | 16.5839 | 12.6963 | 12.622 | -0.12609 | -0.20812 | 0.05558 | -120.2204 | 0.23451 | 0.13133 | 0.075746 | -120.1996 | -120.2971 | 120.4729 | 120.2703 | 120.1883 | 12.2171 | -120.3222 | 0.17604 | 0.19681 | 0.099278 | 0.20635 | -120.3408
2359.7656 | 120.3186 | -0.20142 | 120.2133 | 1.4211e-13 | -0.014276 | 0.027761 | 0.074475 | -0.0017222 | 0.070652 | -0.22823 | -0.0050332 | 0.014918 | 0.017908 | 0.039098 | 0.0028629 | 16.7854 | 12.0431 | 12.4903 | 120.2852 | 120.0918 | 120.0006 | -0.14548 | 0.019362 | -0.013377 | -0.06093 | -0.039111 | -0.013765 | -0.11129 | -0.14583 | 0.055938 | 0.071853 | 16.9868 | 12.6917 | 12.6358 | -0.1215 | -0.21269 | 0.055583 | -120.2524 | 0.22078 | 0.14049 | 0.084903 | -120.2271 | -120.3246 | 120.4866 | 120.2932 | 120.202 | 12.2445 | -120.3588 | 0.16231 | 0.18765 | 0.090123 | 0.18804 | -120.3592
2361.5 | 120.3964 | -0.20142 | 120.2362 | 1.4211e-13 | -0.014276 | 0.028402 | 0.074689 | -0.0021494 | 0.070225 | -0.22823 | -0.0050332 | 0.014918 | 0.018335 | 0.039312 | 0.0032903 | 16.236 | 12.0569 | 12.504 | 120.3081 | 120.1193 | 120.0327 | -0.1409 | 0.023941 | -0.017956 | -0.074666 | -0.034533 | -0.004608 | -0.10214 | -0.15499 | 0.060517 | 0.071857 | 16.4374 | 12.7054 | 12.6449 | -0.11692 | -0.20353 | 0.046425 | -120.2707 | 0.22536 | 0.12675 | 0.080325 | -120.2408 | -120.3383 | 120.5095 | 120.3207 | 120.2341 | 12.2583 | -120.3771 | 0.16688 | 0.19681 | 0.09928 | 0.18346 | -120.3912
2363.2344 | 120.3644 | -0.22888 | 120.2454 | 1.4211e-13 | -0.014489 | 0.027975 | 0.074902 | -0.0021494 | 0.070225 | -0.23586 | -0.004606 | 0.015131 | 0.018335 | 0.039098 | 0.0026493 | 16.4878 | 12.1118 | 12.559 | 120.3218 | 120.1422 | 120.0556 | -0.13632 | 0.023941 | -0.008798 | -0.074666 | -0.025376 | -2.9e-05 | -0.11129 | -0.15499 | 0.092562 | 0.076437 | 16.7167 | 12.7879 | 12.6953 | -0.10318 | -0.1898 | 0.073891 | -120.2707 | 0.25282 | 0.15422 | 0.080325 | -120.2454 | -120.3567 | 120.5507 | 120.3711 | 120.2844 | 12.3407 | -120.3817 | 0.20351 | 0.22885 | 0.11759 | 0.22008 | -120.4004
2364.9062 | 120.4926 | -0.16022 | 120.2637 | 1.4211e-13 | -0.014062 | 0.028616 | 0.074689 | -0.0017222 | 0.070438 | -0.23586 | -0.0048196 | 0.014704 | 0.018335 | 0.039312 | 0.0032903 | 16.3413 | 12.1439 | 12.5956 | 120.3493 | 120.1697 | 120.0739 | -0.1409 | 0.019362 | -0.017956 | -0.074666 | -0.039111 | -0.009187 | -0.10671 | -0.15957 | 0.019318 | 0.085597 | 16.5015 | 12.7558 | 12.7365 | -0.094017 | -0.18979 | 0.000647 | -120.3028 | 0.17958 | 0.085551 | 0.084904 | -120.2729 | -120.3704 | 120.5095 | 120.3299 | 120.2341 | 12.3041 | -120.4046 | 0.12111 | 0.15103 | 0.053503 | 0.14226 | -120.4232
2366.6406 | 120.5566 | -0.15106 | 120.2728 | 1.4211e-13 | -0.013635 | 0.028616 | 0.07533 | -0.0023632 | 0.070011 | -0.22823 | -0.0048196 | 0.01449 | 0.018122 | 0.039098 | 0.0032903 | 16.3459 | 12.1851 | 12.646 | 120.3813 | 120.1834 | 120.0968 | -0.14548 | 0.019362 | -0.008798 | -0.070087 | -0.039111 | -0.004608 | -0.10214 | -0.15499 | 0.005584 | 0.10849 | 16.497 | 12.797 | 12.7914 | -0.089436 | -0.17605 | -0.003929 | -120.3119 | 0.17042 | 0.080975 | 0.084904 | -120.2774 | -120.375 | 120.5324 | 120.3345 | 120.2478 | 12.3361 | -120.4183 | 0.11195 | 0.14645 | 0.048926 | 0.14226 | -120.4278
2368.3125 | 120.5612 | -0.19684 | 120.3186 | 1.4211e-13 | -0.013635 | 0.029257 | 0.075116 | -0.0015084 | 0.070011 | -0.22823 | -0.004606 | 0.015131 | 0.017908 | 0.039312 | 0.0032903 | 16.4146 | 12.1851 | 12.6917 | 120.3996 | 120.2017 | 120.1242 | -0.13632 | 0.019362 | -0.00422 | -0.070087 | -0.039111 | -2.9e-05 | -0.10671 | -0.15041 | 0.060518 | 0.081027 | 16.6114 | 12.8886 | 12.8281 | -0.1169 | -0.19436 | 0.046426 | -120.3577 | 0.2162 | 0.12675 | 0.080325 | -120.3186 | -120.4253 | 120.5965 | 120.3985 | 120.3211 | 12.3819 | -120.4549 | 0.15773 | 0.19681 | 0.090124 | 0.19262 | -120.469
2369.9844 | 118.483 | -26.4542 | 91.6534 | 1.4211e-13 | -0.013207 | 0.029257 | 0.075116 | -0.0023632 | 0.070011 | -0.2206 | -0.0050332 | 0.014918 | 0.018122 | 0.039098 | 0.0032903 | 16.2314 | 12.208 | 12.7101 | 120.4134 | 120.2338 | 120.1471 | -0.15006 | 0.023941 | -0.008798 | -0.070087 | -0.034533 | 0.009128 | -0.11129 | -0.15499 | 26.3041 | 28.7599 | 42.6856 | 39.1642 | 12.8601 | 28.5803 | 28.4937 | 26.2992 | -91.688 | 26.4781 | 26.3841 | 0.084904 | -91.6443 | -91.7647 | 146.8675 | 146.6879 | 146.6013 | 38.6621 | -91.8035 | 26.4196 | 26.4633 | 26.3429 | 26.4454 | -91.8084
2371.7344 | 115.9882 | -33.7189 | 81.9443 | 1.4211e-13 | -0.019617 | 0.022419 | 0.068065 | 0.0021238 | 0.082617 | -0.2206 | -0.0048196 | 0.014918 | 0.018122 | 0.039098 | 0.0030767 | -2.7826 | -11.3673 | -14.3522 | 84.1892 | 84.106 | 84.0311 | -31.6164 | 0.051413 | 0.014095 | -0.042615 | -0.01164 | 0.018285 | -0.11587 | -0.1321 | 2.1024 | 2.2449 | 30.9363 | 19.3667 | 17.2643 | 2.1618 | 2.0868 | 33.5868 | -81.9559 | 33.7703 | 33.6763 | 0.089482 | -81.926 | -82.0601 | 117.908 | 117.8249 | 117.75 | 22.3516 | -113.5607 | 33.7072 | 33.7372 | 33.603 | 33.733 | -82.0764
2373.4844 | 119.7784 | -2.8427 | 117.0502 | 1.4211e-13 | -0.013421 | 0.02883 | 0.074475 | -0.0017222 | 0.071079 | -0.22823 | -0.005247 | 0.014704 | 0.018335 | 0.039098 | 0.0030767 | 14.8076 | 10.2163 | 10.4301 | 117.1032 | 116.9278 | 116.8368 | -2.7326 | 0.02852 | 0.000359 | -0.065509 | -0.039111 | -0.004608 | -0.11129 | -0.15041 | 0.11014 | 0.053021 | 17.6503 | 13.2728 | 13.1626 | -0.1224 | -0.21336 | 2.6923 | -117.0893 | 2.8712 | 2.7772 | 0.084903 | -117.0548 | -117.1615 | 119.9459 | 119.7705 | 119.6795 | 13.059 | -119.7827 | 2.8036 | 2.8381 | 2.7314 | 2.8431 | -117.2006
2375.2344 | 119.9112 | -1.8082 | 118.2312 | 1.4211e-13 | -0.013207 | 0.02883 | 0.075116 | -0.0015084 | 0.070866 | -0.23586 | -0.0048196 | 0.014918 | 0.017908 | 0.039312 | 0.0030767 | 14.9403 | 10.4589 | 10.7551 | 117.561 | 117.4086 | 117.2718 | -2.3892 | 0.023941 | -0.013377 | -0.079245 | -0.039111 | -2.9e-05 | -0.11129 | -0.15041 | -0.58098 | -0.67017 | 16.7485 | 12.5633 | 13.1443 | -0.82264 | -0.95942 | 1.6578 | -118.2703 | 1.8321 | 1.7289 | 0.071167 | -118.2312 | -118.3425 | 119.3692 | 119.2167 | 119.0799 | 12.2671 | -120.6204 | 1.7691 | 1.8081 | 1.6969 | 1.7948 | -118.3816
2376.9219 | 119.8746 | -0.99792 | 118.8446 | 1.4211e-13 | -0.013207 | 0.029471 | 0.074902 | -0.0021494 | 0.070225 | -0.23586 | -0.0048196 | 0.015131 | 0.017908 | 0.039098 | 0.0030767 | 15.769 | 11.4388 | 11.9775 | 118.8933 | 118.7044 | 118.6133 | -0.94679 | 0.019362 | -0.013377 | -0.079245 | -0.052847 | -2.9e-05 | -0.10671 | -0.15499 | 0.051135 | 0.048737 | 16.7669 | 12.9755 | 12.9243 | -0.14021 | -0.2313 | 0.84293 | -118.8975 | 1.0173 | 0.91868 | 0.075746 | -118.8446 | -118.9513 | 119.8913 | 119.7023 | 119.6112 | 12.4367 | -119.7914 | 0.94508 | 0.9979 | 0.89121 | 0.98455 | -118.9996
2378.6562 | 120.0302 | -1.0025 | 119.0186 | 1.4211e-13 | -0.012993 | 0.029471 | 0.075116 | -0.0017222 | 0.070225 | -0.22823 | -0.0048196 | 0.014918 | 0.017908 | 0.039525 | 0.0028629 | 15.7095 | 11.512 | 12.0096 | 119.0719 | 118.8967 | 118.8056 | -0.93763 | 0.005626 | -0.017956 | -0.083823 | -0.04369 | -0.009187 | -0.11129 | -0.15957 | 0.06487 | 0.053344 | 16.712 | 13.0121 | 12.9472 | -0.12184 | -0.21295 | 0.84293 | -119.0622 | 1.0081 | 0.91868 | 0.075747 | -119.0277 | -119.1298 | 120.0744 | 119.8992 | 119.8081 | 12.5145 | -119.9562 | 0.95881 | 0.99331 | 0.89121 | 0.98455 | -119.1781
2380.4062 | 120.0256 | -1.1536 | 118.9453 | 1.4211e-13 | -0.012566 | 0.029257 | 0.07533 | -0.0017222 | 0.070438 | -0.25112 | -0.004606 | 0.01449 | 0.017694 | 0.039312 | 0.0028629 | 15.5676 | 11.4616 | 11.9638 | 119.0261 | 118.8326 | 118.7461 | -1.0613 | 0.019362 | -0.022535 | -0.083823 | -0.039111 | -0.004608 | -0.11129 | -0.16415 | 0.092301 | 0.080803 | 16.7211 | 13.1174 | 13.0251 | -0.1127 | -0.19923 | 0.98942 | -118.9844 | 1.1729 | 1.0697 | 0.080326 | -118.9499 | -119.0566 | 120.1797 | 119.9862 | 119.8997 | 12.6152 | -120.0066 | 1.1145 | 1.149 | 1.0423 | 1.131 | -119.1095
2382.0781 | 117.6178 | -48.3902 | 69.223 | 1.4211e-13 | -0.021968 | 0.019855 | 0.066782 | 0.0049014 | 0.093728 | -0.22823 | -0.0050332 | 0.014918 | 0.018122 | 0.039525 | 0.0030767 | -13.5281 | -24.9016 | -30.0282 | 66.0679 | 66.1017 | 65.9182 | -50.6373 | 0.055992 | 0.023253 | -0.042615 | -0.007062 | 0.032021 | -0.11587 | -0.12294 | -2.2471 | -3.1551 | 34.8621 | 18.362 | 20.6091 | -3.1213 | -3.3049 | 48.2673 | -69.2301 | 48.4462 | 48.3476 | 0.080324 | -69.191 | -69.3389 | 114.4581 | 114.4919 | 114.3084 | 23.4886 | -119.8603 | 48.3831 | 48.4222 | 48.2743 | 48.4135 | -69.346
2383.8125 | 119.9203 | -4.3716 | 115.4709 | 1.4211e-13 | -0.01278 | 0.02883 | 0.07533 | -0.0012948 | 0.07172 | -0.23586 | -0.0048196 | 0.015131 | 0.017908 | 0.039525 | 0.0030767 | 13.5164 | 9.1037 | 9.226 | 115.5328 | 115.348 | 115.2755 | -4.4039 | 0.019362 | -0.008798 | -0.074666 | -0.04369 | -0.009187 | -0.10214 | -0.15957 | -0.032235 | 0.061919 | 17.8881 | 13.5976 | 13.6299 | -0.12284 | -0.19538 | 4.2121 | -115.5146 | 4.391 | 4.297 | 0.084904 | -115.4801 | -115.573 | 119.9044 | 119.7197 | 119.6471 | 13.4753 | -119.8748 | 4.328 | 4.3625 | 4.2695 | 4.3628 | -115.6305
2385.5625 | 120.0119 | -4.2068 | 115.8417 | 1.4211e-13 | -0.01278 | 0.029257 | 0.075757 | -0.0012948 | 0.072148 | -0.23586 | -0.004606 | 0.015345 | 0.017694 | 0.039739 | 0.0032903 | 13.7408 | 9.3463 | 9.4183 | 115.8716 | 115.696 | 115.6097 | -4.1383 | 0.019362 | -0.022535 | -0.079245 | -0.039111 | -0.004608 | -0.11129 | -0.15499 | 0.068548 | 0.02993 | 17.9476 | 13.6251 | 13.5566 | -0.14563 | -0.23193 | 4.0519 | -115.8808 | 4.2262 | 4.1276 | 0.075746 | -115.8463 | -115.953 | 120.0785 | 119.9029 | 119.8166 | 13.5532 | -119.98 | 4.1677 | 4.2022 | 4.0956 | 4.1843 | -115.9967
2387.3125 | 119.8929 | -3.891 | 116.0568 | 1.4211e-13 | -0.01278 | 0.029471 | 0.07533 | -0.0010812 | 0.07172 | -0.22823 | -0.0050332 | 0.01449 | 0.017908 | 0.039312 | 0.0026493 | 13.7271 | 9.5203 | 9.6609 | 116.0731 | 115.8929 | 115.8112 | -3.8498 | 0.019362 | -0.013377 | -0.074666 | -0.039111 | -0.013765 | -0.10671 | -0.15957 | 0.041163 | 0.01623 | 17.618 | 13.5519 | 13.5107 | -0.16389 | -0.24562 | 3.7314 | -116.0959 | 3.9104 | 3.8163 | 0.084904 | -116.0706 | -116.1635 | 119.964 | 119.7839 | 119.7022 | 13.4113 | -119.9067 | 3.8519 | 3.8772 | 3.7843 | 3.8776 | -116.2164
2388.9844 | 120.0806 | -4.216 | 115.8005 | 1.4211e-13 | -0.012566 | 0.029257 | 0.075757 | -0.0012948 | 0.07172 | -0.23586 | -0.0050332 | 0.015345 | 0.017908 | 0.039312 | 0.0030767 | 13.5989 | 9.4883 | 9.6197 | 116.0959 | 115.9113 | 115.8387 | -3.9414 | 0.014784 | -0.013377 | -0.079245 | -0.04369 | -0.004608 | -0.10214 | -0.15957 | 0.2746 | 0.29547 | 17.8149 | 13.8357 | 13.5611 | 0.11078 | 0.038197 | 4.0564 | -115.8442 | 4.2308 | 4.1368 | 0.080325 | -115.8051 | -115.9026 | 120.3119 | 120.1273 | 120.0547 | 13.7043 | -119.7419 | 4.1723 | 4.2114 | 4.1139 | 4.2026 | -115.96
2390.7344 | 120.1859 | -3.8315 | 116.2354 | 1.4211e-13 | -0.011925 | 0.029684 | 0.075971 | -0.0015084 | 0.071507 | -0.23586 | -0.004606 | 0.015131 | 0.017908 | 0.039312 | 0.0030767 | 13.6446 | 9.6623 | 9.8166 | 116.3386 | 116.1585 | 116.0768 | -3.7628 | 0.014784 | -0.017956 | -0.074666 | -0.039111 | -2.9e-05 | -0.10671 | -0.15499 | 0.068654 | 0.10325 | 17.4761 | 13.6481 | 13.5794 | -0.076835 | -0.15859 | 3.6765 | -116.2745 | 3.8463 | 3.7568 | 0.080325 | -116.2354 | -116.3421 | 120.1701 | 119.99 | 119.9082 | 13.4937 | -119.9982 | 3.7924 | 3.8315 | 3.7248 | 3.8135 | -116.3903
2392.4844 | 119.7601 | -73.114 | 46.2662 | 1.4211e-13 | -0.024318 | 0.016864 | 0.066569 | 0.0078926 | 0.10997 | -0.23586 | -0.004606 | 0.014918 | 0.018122 | 0.039312 | 0.0028629 | -25.8394 | -40.1941 | -47.8789 | 46.0283 | 45.9499 | 46.0379 | -73.3304 | 0.074307 | 0.03241 | -0.019721 | 0.015831 | 0.041178 | -0.12961 | -0.1092 | -0.21641 | -0.23788 | 47.2746 | 25.2351 | 25.4515 | -0.31631 | -0.2283 | 73.0048 | -46.2503 | 73.1883 | 73.0943 | 0.089482 | -46.225 | -46.3958 | 119.1423 | 119.0639 | 119.1519 | 32.9199 | -119.5966 | 73.1298 | 73.1552 | 72.9844 | 73.1464 | -46.3754
2394.1562 | 120.0302 | -5.7724 | 114.3356 | 1.4211e-13 | -0.011925 | 0.029898 | 0.075971 | -0.0010812 | 0.072148 | -0.2206 | -0.0050332 | 0.014918 | 0.017908 | 0.039312 | 0.0028629 | 12.7656 | 8.4947 | 8.5209 | 114.7179 | 114.5467 | 114.4605 | -5.3655 | 0.019362 | -0.017956 | -0.070087 | -0.039111 | -0.009187 | -0.10671 | -0.16415 | 0.40695 | 0.38222 | 18.538 | 14.2933 | 13.8864 | 0.2111 | 0.12488 | 5.6083 | -114.3747 | 5.7918 | 5.7023 | 0.094062 | -114.3448 | -114.4423 | 120.4903 | 120.3191 | 120.2329 | 14.2671 | -119.7011 | 5.7333 | 5.7632 | 5.6657 | 5.7544 | -114.4998
2395.9062 | 120.0897 | -2.9343 | 117.2699 | 1.4211e-13 | -0.011498 | 0.030325 | 0.076398 | -0.0015084 | 0.071079 | -0.22823 | -0.0050332 | 0.014704 | 0.018122 | 0.039525 | 0.0028629 | 13.9651 | 10.2941 | 10.5674 | 117.2772 | 117.0972 | 117.0108 | -2.9386 | 0.010205 | -0.013377 | -0.074666 | -0.039111 | -0.013765 | -0.10214 | -0.16415 | -0.004357 | 0.007273 | 16.8994 | 13.5017 | 13.506 | -0.1727 | -0.2591 | 2.7701 | -117.309 | 2.9445 | 2.8596 | 0.089483 | -117.2837 | -117.372 | 120.2114 | 120.0315 | 119.9451 | 13.2284 | -120.2085 | 2.8952 | 2.9205 | 2.8321 | 2.9209 | -117.434
2397.5938 | 120.2499 | -2.3895 | 117.7597 | 1.4211e-13 | -0.011498 | 0.03118 | 0.076612 | -0.0015084 | 0.071079 | -0.23586 | -0.0050332 | 0.014704 | 0.017908 | 0.039739 | 0.0028629 | 14.281 | 10.6054 | 10.9703 | 117.8128 | 117.6329 | 117.5373 | -2.3983 | 0.014784 | -0.013377 | -0.074666 | -0.039111 | -0.004608 | -0.11129 | -0.15499 | -0.008783 | 0.053137 | 16.6706 | 13.3598 | 13.3686 | -0.12677 | -0.22237 | 2.2345 | -117.7988 | 2.4043 | 2.3149 | 0.080325 | -117.7643 | -117.871 | 120.2024 | 120.0225 | 119.9269 | 12.995 | -120.158 | 2.3504 | 2.3849 | 2.2782 | 2.3761 | -117.9147
2399.3281 | 120.2499 | -1.9501 | 118.2541 | 1.4211e-13 | -0.011284 | 0.03118 | 0.076398 | -0.0012948 | 0.071079 | -0.22823 | -0.0048196 | 0.014704 | 0.018122 | 0.039525 | 0.0026493 | 14.6473 | 10.9855 | 11.4007 | 118.3439 | 118.1549 | 118.0593 | -1.9038 | 0.014784 | -0.017956 | -0.070087 | -0.039111 | -0.004608 | -0.10671 | -0.15499 | 0.046288 | 0.089846 | 16.5974 | 13.3507 | 13.3045 | -0.099161 | -0.19479 | 1.7951 | -118.2932 | 1.9649 | 1.88 | 0.084904 | -118.2587 | -118.3608 | 120.294 | 120.105 | 120.0094 | 12.9355 | -120.1579 | 1.911 | 1.9455 | 1.8434 | 1.9321 | -118.4091
2401.0781 | 117.009 | -53.9612 | 63.0981 | 1.4211e-13 | -0.016412 | 0.025411 | 0.072124 | 0.0014828 | 0.085822 | -0.23586 | -0.0048196 | 0.015131 | 0.017694 | 0.039739 | 0.0028629 | -0.44763 | -7.8967 | -10.337 | 90.8965 | 90.3838 | 90.9585 | -28.979 | 0.042256 | 0.014095 | -0.051772 | -0.01164 | 0.013707 | -0.11129 | -0.13668 | 24.9822 | 27.7984 | 53.5135 | 43.6242 | 18.642 | 27.2856 | 27.8604 | 53.8245 | -63.1098 | 54.0034 | 53.9094 | 0.084904 | -63.0844 | -63.2094 | 144.8577 | 144.3449 | 144.9197 | 46.0645 | -92.0771 | 53.9495 | 53.9749 | 53.8499 | 53.9753 | -63.2348
2402.8281 | 120.1218 | -2.4078 | 117.5812 | 1.4211e-13 | -0.01107 | 0.030753 | 0.076612 | -0.0015084 | 0.070866 | -0.2206 | -0.0048196 | 0.014918 | 0.017694 | 0.039312 | 0.0026493 | 14.2124 | 10.6009 | 10.9016 | 117.6251 | 117.4589 | 117.3588 | -2.4349 | 0.019362 | -0.013377 | -0.074666 | -0.034533 | -0.004608 | -0.10671 | -0.15957 | -0.027103 | 0.043951 | 16.6202 | 13.3095 | 13.3366 | -0.12225 | -0.22241 | 2.2483 | -117.6157 | 2.4272 | 2.3332 | 0.084904 | -117.5858 | -117.6879 | 120.033 | 119.8668 | 119.7666 | 13.0087 | -120.0161 | 2.3733 | 2.4032 | 2.3011 | 2.3945 | -117.7407
2404.5156 | 120.1263 | -2.2751 | 117.9108 | 1.4211e-13 | -0.010857 | 0.03118 | 0.076826 | -0.0015084 | 0.071079 | -0.22823 | -0.0050332 | 0.014918 | 0.017908 | 0.039525 | 0.0028629 | 14.5832 | 10.7932 | 11.1168 | 117.9731 | 117.7886 | 117.693 | -2.206 | 0.019362 | -0.008798 | -0.074666 | -0.048268 | -0.013765 | -0.10671 | -0.15957 | 0.069091 | 0.062318 | 16.8583 | 13.3919 | 13.3228 | -0.12215 | -0.21776 | 2.1155 | -117.959 | 2.2944 | 2.2004 | 0.084904 | -117.9245 | -118.0175 | 120.2482 | 120.0637 | 119.9681 | 13.0683 | -120.1168 | 2.2268 | 2.2613 | 2.1684 | 2.2663 | -118.0703
2406.25 | 120.1904 | -2.5452 | 117.7277 | 1.4211e-13 | -0.01107 | 0.031394 | 0.077039 | -0.0015084 | 0.071293 | -0.23586 | -0.0050332 | 0.014918 | 0.018122 | 0.039953 | 0.0032903 | 14.4504 | 10.6238 | 10.9154 | 117.7625 | 117.5826 | 117.4961 | -2.4716 | 0.014784 | -0.017956 | -0.074666 | -0.04369 | -0.004608 | -0.11129 | -0.15957 | 0.073594 | 0.034819 | 16.9956 | 13.4605 | 13.3869 | -0.1451 | -0.23153 | 2.3856 | -117.7714 | 2.56 | 2.4705 | 0.084904 | -117.7323 | -117.839 | 120.3076 | 120.1277 | 120.0413 | 13.1689 | -120.1992 | 2.5015 | 2.5406 | 2.4339 | 2.5272 | -117.8872
2407.9219 | 117.9565 | -63.2629 | 54.6204 | 1.4211e-13 | -0.013421 | 0.027334 | 0.074261 | 0.00084184 | 0.081976 | -0.23586 | -0.0050332 | 0.015131 | 0.017694 | 0.039525 | 0.0028629 | 3.9751 | -2.1826 | -3.52 | 99.3024 | 98.7998 | 99.2824 | -21.2314 | 0.046835 | 0.000359 | -0.056351 | -0.029954 | 0.009128 | -0.11587 | -0.14583 | 42.0315 | 44.6821 | 67.238 | 59.743 | 17.7115 | 44.1795 | 44.6621 | 63.1171 | -54.6503 | 63.3098 | 63.2066 | 0.089482 | -54.6112 | -54.7362 | 162.5654 | 162.0628 | 162.5454 | 61.0804 | -75.8518 | 63.233 | 63.2721 | 63.1471 | 63.2633 | -54.7662
2409.6562 | 120.0119 | -8.0978 | 111.0992 | 1.4211e-13 | 0.13572 | 0.030325 | 0.076184 | -0.00086736 | 0.074498 | -0.2206 | -0.0048196 | 0.014918 | 0.017908 | 0.039739 | 0.0026493 | 11.5111 | 6.8922 | 6.5568 | 112.1265 | 111.9551 | 111.8644 | -7.8747 | 0.019362 | -0.013377 | -0.079245 | -0.034533 | -0.004608 | -0.10671 | -0.15957 | 0.22314 | 1.0272 | 19.609 | 14.6547 | 14.4315 | 0.85582 | 0.7652 | 7.9383 | -111.1338 | 8.1172 | 8.0186 | 0.080325 | -111.1039 | -111.206 | 120.2243 | 120.0529 | 119.9623 | 14.99 | -118.9739 | 8.0633 | 8.0932 | 7.9911 | 8.0845 | -111.2588
2411.3906 | 120.1904 | -7.2922 | 112.0148 | 1.4211e-13 | 0.88572 | 0.030112 | 0.076184 | -1.2758e-05 | 0.075994 | -0.23586 | -0.0048196 | 0.015131 | 0.018122 | 0.039739 | 0.0028629 | 13.1914 | 8.2383 | 7.5458 | 112.5981 | 112.4175 | 112.3498 | -7.426 | 0.019362 | -0.013377 | -0.079245 | -0.04369 | -0.009187 | -0.11129 | -0.15957 | -0.13379 | 0.58329 | 20.4836 | 14.8379 | 14.9717 | 0.40276 | 0.33501 | 7.1326 | -112.0585 | 7.3115 | 7.2129 | 0.080325 | -112.024 | -112.1261 | 119.8902 | 119.7097 | 119.642 | 15.5305 | -119.4407 | 7.2485 | 7.283 | 7.1809 | 7.2788 | -112.1743
2413.0625 | 116.1758 | -41.9678 | 78.0029 | 1.4211e-13 | 1.7186 | 0.019 | 0.068278 | 0.007038 | 0.10762 | -0.24349 | -0.005247 | 0.015131 | 0.017908 | 0.039525 | 0.0024357 | -13.464 | -26.9711 | -33.9701 | 60.4914 | 60.4788 | 60.3552 | -59.3327 | 0.055992 | 0.014095 | -0.033458 | -0.007062 | 0.022864 | -0.12503 | -0.11836 | -17.3649 | -17.5115 | 28.5038 | 7.9977 | 25.3626 | -17.5241 | -17.6478 | 41.8494 | -78.01 | 42.0238 | 41.9343 | 0.084903 | -77.9801 | -78.128 | 102.4592 | 102.4466 | 102.3229 | 14.9966 | -137.3356 | 41.9607 | 41.9906 | 41.8427 | 41.9819 | -78.1213
2414.8125 | 119.8608 | -31.8008 | 87.7762 | 1.4211e-13 | 3.9977 | 0.023274 | 0.070842 | 0.005115 | 0.096292 | -0.2206 | -0.0048196 | 0.014704 | 0.017908 | 0.039312 | 0.0026493 | 3.8652 | -6.0836 | -11.0878 | 86.7439 | 86.6611 | 86.5951 | -32.7154 | 0.033099 | -0.017956 | -0.070087 | -0.034533 | -0.004608 | -0.11129 | -0.15041 | -0.91453 | -1.0323 | 35.666 | 20.713 | 21.6275 | -1.1151 | -1.181 | 31.6504 | -87.8107 | 31.8339 | 31.7308 | 0.080325 | -87.7808 | -87.8875 | 118.5447 | 118.4619 | 118.396 | 25.7173 | -120.4916 | 31.7663 | 31.7962 | 31.6895 | 31.7829 | -87.9266
2416.5469 | 119.8105 | -35.376 | 83.7021 | 1.4211e-13 | 6.9545 | 0.020923 | 0.069774 | 0.0061834 | 0.10056 | -0.23586 | -0.0048196 | 0.014918 | 0.017694 | 0.040166 | 0.0026493 | 2.5466 | -8.7437 | -14.9885 | 80.0457 | 80.0171 | 79.9791 | -38.1139 | 0.014784 | -0.027113 | -0.079245 | -0.048268 | -0.022922 | -0.10671 | -0.15957 | -2.7379 | -3.6564 | 37.9226 | 20.3874 | 23.1254 | -3.685 | -3.723 | 35.2164 | -83.7504 | 35.3908 | 35.2967 | 0.080325 | -83.725 | -83.8088 | 115.4217 | 115.393 | 115.355 | 26.6323 | -121.816 | 35.3277 | 35.3531 | 35.2693 | 35.3489 | -83.8617
2418.2812 | 119.458 | -2.7008 | 99.9619 | 1.4211e-13 | -0.017053 | -0.0025813 | -0.006511 | -0.011337 | -0.0069078 | -0.2206 | -0.0048196 | 0.015131 | 0.017694 | 0.039525 | 0.0030767 | -1.2397 | -1.8483 | -2.2518 | 0.070441 | 0.050727 | 0.19233 | -3.2454 | 0.02852 | -0.008798 | -0.074666 | -0.034533 | -2.9e-05 | -0.11129 | -0.15499 | -0.5446 | -99.8914 | 1.4611 | 0.44904 | 0.99364 | -99.9111 | -99.7695 | 2.5458 | -99.9964 | 2.7293 | 2.6261 | 0.080325 | -99.9619 | -100.0731 | 2.7712 | 2.7515 | 2.8931 | 0.85246 | -103.2073 | 2.6663 | 2.7008 | 2.5895 | 2.692 | -100.1168
2419.9688 | 120.4971 | -51.0635 | 68.9621 | 1.4211e-13 | -0.047181 | 0.0016923 | 0.018704 | -0.00065376 | 0.048004 | -0.23586 | -0.004606 | 0.014704 | 0.017908 | 0.039739 | 0.0026493 | -19.6998 | -27.8136 | -33.1643 | -0.25005 | -0.27896 | -0.14191 | -47.748 | 0.055992 | 0.009516 | -0.038036 | -0.007062 | 0.032021 | -0.11587 | -0.12294 | 3.3156 | -69.2121 | 31.3638 | 17.8992 | 14.5837 | -69.2411 | -69.104 | 50.9406 | -68.9692 | 51.1195 | 51.0255 | 0.084903 | -68.9301 | -69.078 | 50.8135 | 50.7846 | 50.9216 | 23.2499 | -116.7101 | 51.0565 | 51.0956 | 50.9477 | 51.0731 | -69.085
2421.7031 | 119.8654 | -119.4031 | 0.24719 | 1.4211e-13 | -0.092053 | 0.0066069 | 0.057167 | 0.015371 | 0.13817 | -0.23586 | -0.0050332 | 0.014704 | 0.017908 | 0.039953 | 0.0026493 | -42.4681 | -66.9652 | -80.1283 | -0.94138 | -1.0024 | -0.87448 | -115.7771 | 0.10636 | 0.055303 | 0.016908 | 0.043302 | 0.06865 | -0.12045 | -0.077151 | 3.626 | -1.1886 | 76.935 | 39.2748 | 35.6487 | -1.2496 | -1.1217 | 119.3259 | -0.20389 | 119.5094 | 119.42 | 0.094059 | -0.17854 | -0.36764 | 118.4617 | 118.4007 | 118.5286 | 52.4378 | -116.0243 | 119.4464 | 119.4717 | 119.2826 | 119.4584 | -0.32434
2423.3906 | 120.4102 | -119.8608 | 0.19226 | 1.4211e-13 | -0.095471 | 0.0081027 | 0.060158 | 0.016439 | 0.13774 | -0.23586 | -0.0048196 | 0.01449 | 0.017908 | 0.039525 | 0.0026493 | -51.2403 | -69.5476 | -83.1408 | -1.1886 | -1.2497 | -1.1217 | -119.953 | 0.10636 | 0.064461 | 0.016908 | 0.04788 | 0.082386 | -0.13419 | -0.08173 | -0.092199 | -1.3809 | 68.6206 | 36.72 | 36.8122 | -1.4419 | -1.314 | 119.7791 | -0.14438 | 119.9672 | 119.8777 | 0.098638 | -0.10987 | -0.32645 | 118.6722 | 118.6112 | 118.7391 | 50.3133 | -120.1453 | 119.9087 | 119.9432 | 119.7267 | 119.9253 | -0.27399
2425.0781 | 120.4239 | -120.0027 | 0.20142 | 1.4211e-13 | -0.096326 | 0.0085301 | 0.059731 | 0.016439 | 0.13582 | -0.23586 | -0.0048196 | 0.015131 | 0.017481 | 0.039739 | 0.0026493 | -55.1136 | -69.6437 | -83.1454 | -1.3626 | -1.4237 | -1.2866 | -120.0355 | 0.11094 | 0.059882 | 0.016908 | 0.043302 | 0.082386 | -0.13419 | -0.072572 | -0.032712 | -1.564 | 64.8892 | 36.8573 | 36.8901 | -1.6251 | -1.488 | 119.9302 | -0.15811 | 120.1137 | 120.0197 | 0.08948 | -0.11903 | -0.3356 | 118.6402 | 118.5791 | 118.7162 | 50.359 | -120.2369 | 120.046 | 120.0851 | 119.8686 | 120.0626 | -0.27399
2426.8125 | 120.5383 | -120.0394 | 0.18768 | 1.4211e-13 | -0.095044 | 0.0070343 | 0.059303 | 0.01708 | 0.14073 | -0.23586 | -0.0048196 | 0.014918 | 0.017267 | 0.039739 | 0.0026493 | -47.3532 | -69.3324 | -82.9348 | -1.4999 | -1.5702 | -1.4331 | -120.0904 | 0.10636 | 0.06904 | 0.007751 | 0.04788 | 0.077807 | -0.13419 | -0.072572 | -0.051038 | -1.6876 | 72.6861 | 37.1046 | 37.1556 | -1.7579 | -1.6208 | 119.9668 | -0.1398 | 120.1457 | 120.0471 | 0.080323 | -0.10988 | -0.32187 | 118.5394 | 118.4692 | 118.6063 | 50.707 | -120.2781 | 120.0872 | 120.1172 | 119.9052 | 120.1084 | -0.26026
2428.5625 | 119.989 | -119.4534 | 0.27008 | 1.4211e-13 | -0.087779 | 0.0036155 | 0.057594 | 0.016439 | 0.1512 | -0.2206 | -0.004606 | 0.014918 | 0.017267 | 0.039739 | 0.0030767 | -25.3861 | -67.0431 | -80.6228 | -1.7975 | -1.8678 | -1.7353 | -117.5262 | 0.097201 | 0.064461 | 0.016908 | 0.057037 | 0.077807 | -0.13419 | -0.072572 | 1.9272 | -2.0676 | 94.0673 | 38.8307 | 36.9034 | -2.1379 | -2.0053 | 119.3809 | -0.21304 | 119.5506 | 119.4703 | 0.08948 | -0.19227 | -0.40427 | 117.6559 | 117.5856 | 117.7182 | 52.4104 | -117.7963 | 119.5105 | 119.5312 | 119.3192 | 119.5179 | -0.34265
2430.25 | 120.3827 | -119.9524 | 0.20142 | 1.4211e-13 | -0.08842 | 0.0036155 | 0.058235 | 0.016867 | 0.15548 | -0.22823 | -0.0050332 | 0.014704 | 0.017481 | 0.039739 | 0.0026493 | -23.3442 | -68.2839 | -82.2893 | -2.118 | -2.1792 | -2.0466 | -120.0034 | 0.11094 | 0.06904 | 0.01233 | 0.04788 | 0.082386 | -0.12961 | -0.067994 | -0.051014 | -2.3194 | 96.6082 | 37.6631 | 37.7141 | -2.3806 | -2.248 | 119.8844 | -0.15354 | 120.0633 | 119.9647 | 0.080324 | -0.11903 | -0.33102 | 117.8344 | 117.7732 | 117.9058 | 51.6685 | -120.2048 | 120.0003 | 120.0348 | 119.8228 | 120.0214 | -0.26941
2431.9219 | 120.4056 | -120.0668 | 0.2243 | 1.4211e-13 | -0.088206 | 0.0027607 | 0.058449 | 0.016867 | 0.15633 | -0.22823 | -0.0048196 | 0.015131 | 0.017694 | 0.039525 | 0.0024357 | -22.4102 | -68.2335 | -82.1931 | -2.3241 | -2.3898 | -2.2572 | -120.0355 | 0.11094 | 0.064461 | 0.016908 | 0.04788 | 0.082386 | -0.13876 | -0.063415 | 0.031374 | -2.5484 | 97.6567 | 37.8737 | 37.8423 | -2.6141 | -2.4815 | 120.0034 | -0.17642 | 120.1778 | 120.0837 | 0.080323 | -0.14192 | -0.36307 | 117.7428 | 117.677 | 117.8096 | 51.8333 | -120.2598 | 120.1147 | 120.1492 | 119.9281 | 120.1313 | -0.28772
2433.6562 | 116.0477 | -87.4512 | 29.2419 | 1.4211e-13 | -0.083719 | 0.0027607 | 0.054389 | 0.016439 | 0.1465 | -0.22823 | -0.0050332 | 0.014704 | 0.017481 | 0.040166 | 0.0026493 | -20.7345 | -64.5798 | -78.0452 | -2.4477 | -2.5135 | -2.3763 | -113.4281 | 0.10636 | 0.059882 | 0.016908 | 0.043302 | 0.073228 | -0.12961 | -0.072572 | -25.9769 | -31.6896 | 66.7167 | 9.406 | 35.3829 | -31.7554 | -31.6182 | 87.3786 | -29.1986 | 87.5575 | 87.4681 | 0.08948 | -29.1687 | -29.3715 | 85.0035 | 84.9377 | 85.0749 | 22.8714 | -142.67 | 87.4945 | 87.5244 | 87.3216 | 87.5111 | -29.3145
2435.4062 | 120.3552 | -119.8654 | 0.20142 | 1.4211e-13 | -0.087779 | 0.0027607 | 0.058235 | 0.017508 | 0.15697 | -0.23586 | -0.0050332 | 0.014918 | 0.017481 | 0.039525 | 0.0026493 | -21.055 | -67.8077 | -81.6895 | -2.6857 | -2.5959 | -2.6098 | -119.9622 | 0.11094 | 0.06904 | 0.016908 | 0.052459 | 0.086964 | -0.12961 | -0.072572 | -0.096779 | -2.8872 | 98.8105 | 38.1759 | 38.2727 | -2.7973 | -2.8112 | 119.7928 | -0.14896 | 119.9764 | 119.8823 | 0.08948 | -0.11445 | -0.33102 | 117.1797 | 117.2695 | 117.2556 | 52.0577 | -120.1636 | 119.9179 | 119.9524 | 119.7358 | 119.9345 | -0.27399
2437.1562 | 120.4651 | -119.9844 | 0.21057 | 1.4211e-13 | -0.087779 | 0.0025471 | 0.058021 | 0.018362 | 0.15783 | -0.24349 | -0.0050332 | 0.014704 | 0.017908 | 0.039739 | 0.0028629 | -20.5376 | -67.3269 | -80.6045 | -2.6491 | -2.5593 | -2.5823 | -120.008 | 0.10636 | 0.06904 | 0.021487 | 0.057037 | 0.096121 | -0.13419 | -0.067994 | -0.02355 | -2.8597 | 99.4468 | 39.38 | 39.4035 | -2.7698 | -2.7929 | 119.9164 | -0.15353 | 120.0908 | 120.0059 | 0.089481 | -0.11445 | -0.34476 | 117.3353 | 117.4252 | 117.4021 | 52.6575 | -120.2186 | 120.0415 | 120.0806 | 119.8503 | 120.0535 | -0.27857
2438.8438 | 119.8837 | -119.4992 | 0.11444 | 1.4211e-13 | -0.086924 | 0.0027607 | 0.056953 | 0.018362 | 0.15569 | -0.23586 | -0.0050332 | 0.01449 | 0.017481 | 0.039525 | 0.0028629 | -20.2904 | -66.0175 | -78.645 | -2.5072 | -2.4173 | -2.4266 | -118.442 | 0.11094 | 0.06904 | 0.021487 | 0.052459 | 0.082386 | -0.13419 | -0.072572 | 1.0572 | -2.6216 | 99.2088 | 40.8543 | 39.797 | -2.5318 | -2.5411 | 119.4266 | -0.061982 | 119.6101 | 119.5207 | 0.094059 | -0.032055 | -0.24863 | 116.992 | 117.0819 | 117.0726 | 53.4817 | -118.5564 | 119.5517 | 119.5816 | 119.365 | 119.5682 | -0.18701
2440.6094 | 119.902 | -119.4305 | 0.18768 | 1.4211e-13 | -0.087138 | 0.0021197 | 0.05738 | 0.018149 | 0.15697 | -0.22823 | -0.0043924 | 0.014918 | 0.017481 | 0.039739 | 0.0026493 | -20.1484 | -66.8004 | -80.1924 | -3.0841 | -2.9943 | -3.0081 | -119.3944 | 0.10636 | 0.06904 | 0.01233 | 0.052459 | 0.086964 | -0.12961 | -0.067994 | 0.036132 | -3.2718 | 99.2821 | 39.2381 | 39.202 | -3.1819 | -3.1958 | 119.3625 | -0.13522 | 119.5369 | 119.4429 | 0.080324 | -0.10072 | -0.31729 | 116.3465 | 116.4363 | 116.4224 | 52.6301 | -119.5821 | 119.483 | 119.5175 | 119.3009 | 119.4996 | -0.25568
2442.3594 | 120.2133 | -119.7876 | 0.22888 | 1.4211e-13 | -0.086711 | 0.0019059 | 0.057808 | 0.018149 | 0.15783 | -0.23586 | -0.0048196 | 0.014704 | 0.017694 | 0.04038 | 0.0024357 | -19.6631 | -67.0019 | -80.6823 | -3.4046 | -3.3148 | -3.3378 | -119.8569 | 0.11094 | 0.06904 | 0.021487 | 0.052459 | 0.082386 | -0.13419 | -0.067994 | -0.069283 | -3.6334 | 100.1245 | 39.1053 | 39.1746 | -3.5437 | -3.5667 | 119.7196 | -0.17642 | 119.8985 | 119.8091 | 0.089481 | -0.1465 | -0.36307 | 116.383 | 116.4728 | 116.4498 | 52.7857 | -120.0858 | 119.8401 | 119.87 | 119.6534 | 119.8566 | -0.29688
2444.0312 | 120.2499 | -119.9295 | 0.2243 | 1.4211e-13 | -0.086497 | 0.0019059 | 0.05738 | 0.018149 | 0.15825 | -0.24349 | -0.0050332 | 0.014918 | 0.017481 | 0.039953 | 0.0026493 | -19.3243 | -66.8462 | -80.49 | -3.6838 | -3.5895 | -3.6079 | -119.9027 | 0.11094 | 0.064461 | 0.016908 | 0.061616 | 0.086964 | -0.12961 | -0.063415 | 0.026834 | -3.9081 | 100.6052 | 39.4395 | 39.4127 | -3.8138 | -3.8322 | 119.8661 | -0.16269 | 120.0404 | 119.9464 | 0.080323 | -0.13734 | -0.35391 | 116.2457 | 116.34 | 116.3216 | 53.0833 | -120.127 | 119.9911 | 120.0165 | 119.7999 | 119.994 | -0.28772
2445.7812 | 120.4285 | -119.9707 | 0.20599 | 1.4211e-13 | -0.086283 | 0.0019059 | 0.05738 | 0.018576 | 0.15825 | -0.23586 | -0.0050332 | 0.014704 | 0.017694 | 0.040166 | 0.0024357 | -19.013 | -66.7363 | -80.3069 | -3.8303 | -3.736 | -3.7544 | -119.9622 | 0.10636 | 0.064461 | 0.026066 | 0.052459 | 0.082386 | -0.12961 | -0.067994 | 0.008507 | -4.0363 | 100.9577 | 39.6638 | 39.6553 | -3.942 | -3.9604 | 119.9027 | -0.15354 | 120.0771 | 119.9968 | 0.09406 | -0.12361 | -0.3356 | 116.1404 | 116.2347 | 116.2163 | 53.2344 | -120.1682 | 120.0232 | 120.0531 | 119.8411 | 120.0352 | -0.27399
2447.5312 | 120.369 | -120.0531 | 0.2243 | 1.4211e-13 | -0.086497 | 0.0021197 | 0.056953 | 0.01879 | 0.15847 | -0.23586 | -0.0048196 | 0.01449 | 0.017481 | 0.039953 | 0.0024357 | -18.9947 | -66.4753 | -79.9315 | -3.8395 | -3.736 | -3.7498 | -120.0126 | 0.10636 | 0.06904 | 0.016908 | 0.052459 | 0.086964 | -0.12503 | -0.072572 | 0.040536 | -4.0638 | 101.0584 | 40.1216 | 40.0811 | -3.9603 | -3.9741 | 119.9805 | -0.17184 | 120.1595 | 120.07 | 0.08948 | -0.13734 | -0.34933 | 116.2136 | 116.3171 | 116.3033 | 53.5778 | -120.2369 | 120.1056 | 120.1401 | 119.9281 | 120.1221 | -0.29688
2449.2188 | 120.3873 | -120.0943 | 0.2243 | 1.4211e-13 | -0.08607 | 0.0019059 | 0.05738 | 0.019003 | 0.15847 | -0.22823 | -0.005247 | 0.01449 | 0.017694 | 0.039525 | 0.0026493 | -18.8161 | -66.2098 | -79.5652 | -3.9631 | -3.8643 | -3.8826 | -120.0538 | 0.10636 | 0.064461 | 0.016908 | 0.057037 | 0.082386 | -0.13419 | -0.072572 | 0.040524 | -4.1874 | 101.2782 | 40.5291 | 40.4886 | -4.0886 | -4.1069 | 120.0217 | -0.16727 | 120.2007 | 120.1112 | 0.08948 | -0.14192 | -0.35849 | 116.1312 | 116.23 | 116.2117 | 53.8845 | -120.2781 | 120.1513 | 120.1767 | 119.9601 | 120.1588 | -0.29688
2450.9062 | 120.3964 | -120.1492 | 0.23804 | 1.4211e-13 | -0.08607 | 0.0016923 | 0.056739 | 0.019003 | 0.15868 | -0.23586 | -0.0050332 | 0.015131 | 0.017481 | 0.039739 | 0.0026493 | -18.7383 | -66.1777 | -80.0642 | -4.1188 | -4.0291 | -4.0429 | -120.0904 | 0.11552 | 0.073618 | 0.021487 | 0.057037 | 0.086964 | -0.12503 | -0.067994 | 0.058825 | -4.3568 | 101.4109 | 40.085 | 40.0262 | -4.2671 | -4.2809 | 120.0812 | -0.181 | 120.2647 | 120.1707 | 0.089481 | -0.15107 | -0.36307 | 116.0304 | 116.1201 | 116.1064 | 53.9715 | -120.3284 | 120.2063 | 120.2362 | 120.0242 | 120.2228 | -0.30603
2452.6562 | 120.1355 | -120.1447 | 0.23804 | 1.4211e-13 | -0.085856 | 0.0019059 | 0.056953 | 0.018576 | 0.15889 | -0.23586 | -0.0050332 | 0.014918 | 0.017267 | 0.039953 | 0.0026493 | -18.4544 | -66.1136 | -80.0825 | -4.3569 | -4.2718 | -4.2901 | -120.095 | 0.10178 | 0.06904 | 0.021487 | 0.052459 | 0.082386 | -0.13419 | -0.067994 | 0.049668 | -4.5949 | 101.6902 | 40.0621 | 40.0124 | -4.5098 | -4.5282 | 120.0767 | -0.18558 | 120.2464 | 120.1661 | 0.089481 | -0.15565 | -0.37222 | 115.7878 | 115.8729 | 115.8545 | 54.031 | -120.333 | 120.1971 | 120.227 | 120.0105 | 120.2137 | -0.30603
2454.4062 | 120.3598 | -120.1401 | 0.28381 | 1.4211e-13 | -0.085642 | 0.0016923 | 0.056739 | 0.018576 | 0.15868 | -0.22823 | -0.005247 | 0.014704 | 0.017481 | 0.039953 | 0.0026493 | -18.3858 | -66.0724 | -80.2702 | -4.421 | -4.3405 | -4.3542 | -120.1179 | 0.11094 | 0.06904 | 0.016908 | 0.057037 | 0.082386 | -0.12961 | -0.067994 | 0.022196 | -4.7048 | 101.7543 | 39.8698 | 39.8476 | -4.6243 | -4.638 | 120.0721 | -0.22678 | 120.251 | 120.157 | 0.084902 | -0.20143 | -0.41342 | 115.7191 | 115.7996 | 115.7859 | 54.0677 | -120.4017 | 120.1971 | 120.2225 | 120.0105 | 120.2091 | -0.35181
2456.0938 | 120.607 | -120.1126 | 0.24719 | 1.4211e-13 | -0.085429 | 0.0016923 | 0.056953 | 0.018576 | 0.15868 | -0.24349 | -0.004606 | 0.015131 | 0.017694 | 0.040166 | 0.0024357 | -18.1935 | -65.9534 | -80.1878 | -4.6132 | -4.5236 | -4.5419 | -120.127 | 0.11094 | 0.06904 | 0.016908 | 0.057037 | 0.091543 | -0.13419 | -0.058836 | -0.014428 | -4.8604 | 101.9191 | 39.9248 | 39.9392 | -4.7708 | -4.7891 | 120.0538 | -0.19015 | 120.2235 | 120.1295 | 0.075744 | -0.15565 | -0.38138 | 115.4994 | 115.589 | 115.5707 | 54.1592 | -120.3742 | 120.1696 | 120.2042 | 119.9784 | 120.1817 | -0.30603
2457.8281 | 120.1996 | -120.076 | 0.28839 | 1.4211e-13 | -0.084788 | 0.0012649 | 0.056953 | 0.018576 | 0.15868 | -0.22823 | -0.0048196 | 0.014918 | 0.017267 | 0.040166 | 0.0026493 | -18.1019 | -65.9671 | -80.4168 | -4.8376 | -4.7434 | -4.7114 | -120.1682 | 0.11094 | 0.073618 | 0.021487 | 0.052459 | 0.091543 | -0.12961 | -0.067994 | -0.092259 | -5.126 | 101.9741 | 39.6592 | 39.7515 | -5.0318 | -4.9997 | 120.008 | -0.23593 | 120.1869 | 120.0975 | 0.089481 | -0.19685 | -0.418 | 115.2384 | 115.3326 | 115.3646 | 54.1089 | -120.4566 | 120.1284 | 120.1675 | 119.9464 | 120.1496 | -0.35639
2459.5156 | 120.6345 | -120.1584 | 0.27466 | 1.4211e-13 | -0.086283 | 0.0014787 | 0.05738 | 0.018362 | 0.15889 | -0.23586 | -0.0050332 | 0.014704 | 0.017267 | 0.040166 | 0.0026493 | -18.0744 | -65.8343 | -80.4396 | -4.0959 | -3.9925 | -3.9788 | -120.1774 | 0.11094 | 0.082776 | 0.016908 | 0.057037 | 0.096121 | -0.13876 | -0.067994 | -0.01902 | -4.3705 | 102.084 | 39.7187 | 39.7378 | -4.2671 | -4.2534 | 120.0904 | -0.21762 | 120.2693 | 120.1753 | 0.084902 | -0.17854 | -0.41342 | 116.0625 | 116.1659 | 116.1796 | 54.3241 | -120.4521 | 120.2154 | 120.2545 | 120.0196 | 120.2412 | -0.34265
2461.2656 | 120.1172 | -119.9203 | 0.2655 | 1.4211e-13 | -0.086924 | 0.0012649 | 0.057808 | 0.018576 | 0.15954 | -0.23586 | -0.0050332 | 0.014918 | 0.017481 | 0.040166 | 0.0026493 | -18.0149 | -65.6832 | -80.3847 | -3.6289 | -3.5437 | -3.5163 | -120.2049 | 0.11552 | 0.073618 | 0.01233 | 0.061616 | 0.091543 | -0.12503 | -0.063415 | -0.28453 | -3.8944 | 101.9054 | 39.5356 | 39.8202 | -3.8092 | -3.7818 | 119.8569 | -0.20389 | 120.0359 | 119.9327 | 0.075745 | -0.17396 | -0.39053 | 116.2915 | 116.3766 | 116.404 | 54.2371 | -120.4704 | 119.982 | 120.0119 | 119.7953 | 119.994 | -0.32892
2462.9375 | 120.6619 | -120.2408 | 0.25635 | 1.4211e-13 | -0.086711 | 0.0021197 | 0.057808 | 0.018576 | 0.15996 | -0.22823 | -0.0050332 | 0.01449 | 0.017694 | 0.04038 | 0.0024357 | -17.9279 | -65.6008 | -80.4213 | -3.5419 | -3.4613 | -3.4248 | -120.2324 | 0.11094 | 0.087354 | 0.021487 | 0.061616 | 0.096121 | -0.12503 | -0.067994 | 0.008431 | -3.7983 | 102.3129 | 39.8195 | 39.811 | -3.7177 | -3.6811 | 120.1728 | -0.19473 | 120.3517 | 120.2623 | 0.089481 | -0.16023 | -0.38138 | 116.6989 | 116.7795 | 116.816 | 54.64 | -120.4887 | 120.3024 | 120.3369 | 120.1158 | 120.3281 | -0.32434
2464.6875 | 120.7535 | -120.2362 | 0.25177 | 1.4211e-13 | -0.087138 | 0.0016923 | 0.057808 | 0.018362 | 0.15996 | -0.22823 | -0.0050332 | 0.014918 | 0.017694 | 0.04038 | 0.0024357 | -17.905 | -65.5138 | -80.5816 | -3.5419 | -3.4522 | -3.4248 | -120.2598 | 0.11094 | 0.082776 | 0.021487 | 0.057037 | 0.1007 | -0.12961 | -0.063415 | -0.02362 | -3.7937 | 102.3312 | 39.6546 | 39.6783 | -3.7039 | -3.6765 | 120.1728 | -0.19473 | 120.3471 | 120.2577 | 0.084902 | -0.15107 | -0.38138 | 116.6943 | 116.7841 | 116.8114 | 54.7224 | -120.5116 | 120.2932 | 120.3369 | 120.1066 | 120.319 | -0.31518
2466.4375 | 120.6024 | -120.2591 | 0.28839 | 1.4211e-13 | -0.086924 | 0.0016923 | 0.058235 | 0.018362 | 0.16082 | -0.22823 | -0.0048196 | 0.014704 | 0.017481 | 0.039953 | 0.0028629 | -17.8638 | -65.4268 | -80.6319 | -3.5877 | -3.4888 | -3.4751 | -120.2781 | 0.12009 | 0.087354 | 0.026066 | 0.061616 | 0.1007 | -0.12961 | -0.063415 | -0.019048 | -3.8761 | 102.3953 | 39.6272 | 39.6462 | -3.7772 | -3.7635 | 120.1957 | -0.22678 | 120.3792 | 120.2852 | 0.089481 | -0.18769 | -0.418 | 116.6714 | 116.7703 | 116.784 | 54.8323 | -120.5665 | 120.3207 | 120.3598 | 120.1295 | 120.3464 | -0.35181
2468.1094 | 120.7855 | -120.2499 | 0.26093 | 1.4211e-13 | -0.086924 | 0.0016923 | 0.058021 | 0.018362 | 0.16039 | -0.2206 | -0.0048196 | 0.014704 | 0.017481 | 0.040166 | 0.0026493 | -17.9508 | -65.3444 | -80.6457 | -3.4229 | -3.3285 | -3.3011 | -120.2919 | 0.11094 | 0.082776 | 0.026066 | 0.057037 | 0.10528 | -0.12961 | -0.067994 | -0.04194 | -3.6838 | 102.2991 | 39.6043 | 39.6462 | -3.5894 | -3.5621 | 120.1819 | -0.20389 | 120.3609 | 120.276 | 0.09406 | -0.15565 | -0.39053 | 116.8271 | 116.9214 | 116.9488 | 54.9055 | -120.5528 | 120.307 | 120.3552 | 120.1203 | 120.3327 | -0.32892
2469.8594 | 120.639 | -120.2637 | 0.27466 | 1.4211e-13 | -0.087565 | 0.0016923 | 0.058021 | 0.018576 | 0.16039 | -0.23586 | -0.0048196 | 0.014704 | 0.017481 | 0.040166 | 0.0024357 | -17.9233 | -65.1842 | -80.6869 | -3.2993 | -3.214 | -3.1867 | -120.3194 | 0.11552 | 0.082776 | 0.030644 | 0.057037 | 0.091543 | -0.12961 | -0.067994 | -0.055681 | -3.5739 | 102.3403 | 39.5768 | 39.6325 | -3.4887 | -3.4613 | 120.1957 | -0.21762 | 120.3792 | 120.2943 | 0.098638 | -0.18312 | -0.40426 | 116.9644 | 117.0496 | 117.077 | 55.0795 | -120.594 | 120.3207 | 120.3552 | 120.1341 | 120.3464 | -0.34265
2471.5312 | 120.7077 | -120.3461 | 0.29755 | 1.4211e-13 | -0.087565 | 0.0019059 | 0.058235 | 0.018576 | 0.1606 | -0.23586 | -0.0048196 | 0.014704 | 0.017053 | 0.040594 | 0.0026493 | -17.9096 | -65.0422 | -80.5358 | -2.9421 | -2.8477 | -2.8295 | -120.3331 | 0.11552 | 0.082776 | 0.021487 | 0.057037 | 0.086964 | -0.12961 | -0.058836 | 0.01298 | -3.2397 | 102.4365 | 39.8103 | 39.7973 | -3.1453 | -3.1271 | 120.2872 | -0.24051 | 120.4616 | 120.3676 | 0.080323 | -0.21058 | -0.42715 | 117.4039 | 117.4983 | 117.5165 | 55.3038 | -120.6306 | 120.4031 | 120.433 | 120.2165 | 120.4288 | -0.35638
2473.2812 | 120.694 | -120.2454 | 0.28381 | 1.4211e-13 | -0.088206 | 0.0019059 | 0.058235 | 0.018576 | 0.16103 | -0.23586 | -0.0048196 | 0.01449 | 0.017694 | 0.039953 | 0.0026493 | -17.9645 | -64.9873 | -80.5175 | -3.0245 | -2.9347 | -2.9165 | -120.3468 | 0.11552 | 0.091933 | 0.030644 | 0.057037 | 0.096121 | -0.13419 | -0.063415 | -0.10146 | -3.3084 | 102.2808 | 39.7279 | 39.8294 | -3.2185 | -3.2004 | 120.1819 | -0.22678 | 120.3609 | 120.276 | 0.094059 | -0.18769 | -0.418 | 117.2208 | 117.3106 | 117.3288 | 55.2581 | -120.6306 | 120.3024 | 120.3415 | 120.1112 | 120.3373 | -0.34723
2474.9688 | 120.8405 | -120.3323 | 0.27466 | 1.4211e-13 | -0.087779 | 0.0016923 | 0.058235 | 0.018576 | 0.16082 | -0.23586 | -0.005247 | 0.014918 | 0.017481 | 0.04038 | 0.0028629 | -17.8409 | -64.9278 | -80.5175 | -3.0154 | -2.9256 | -2.9028 | -120.3651 | 0.11552 | 0.078197 | 0.030644 | 0.061616 | 0.10528 | -0.13419 | -0.058836 | -0.032806 | -3.29 | 102.4914 | 39.8149 | 39.8477 | -3.2002 | -3.1775 | 120.2735 | -0.21304 | 120.4479 | 120.363 | 0.08948 | -0.16938 | -0.40884 | 117.3169 | 117.4068 | 117.4295 | 55.4046 | -120.6398 | 120.394 | 120.4376 | 120.1981 | 120.4105 | -0.33349
2476.7188 | 120.845 | -120.3415 | 0.27008 | 1.4211e-13 | -0.087779 | 0.0019059 | 0.058235 | 0.018362 | 0.16082 | -0.23586 | -0.004606 | 0.014918 | 0.017267 | 0.04038 | 0.0026493 | -17.8226 | -64.8453 | -80.4854 | -3.107 | -3.0172 | -2.999 | -120.3789 | 0.11094 | 0.078197 | 0.016908 | 0.061616 | 0.091543 | -0.12503 | -0.063415 | -0.037387 | -3.377 | 102.5189 | 39.8561 | 39.8935 | -3.2872 | -3.269 | 120.2781 | -0.20847 | 120.4524 | 120.3584 | 0.080323 | -0.17854 | -0.39511 | 117.2345 | 117.3243 | 117.3425 | 55.4962 | -120.649 | 120.4031 | 120.433 | 120.2165 | 120.4197 | -0.3335
2478.4531 | 120.8679 | -120.3598 | 0.27466 | 1.4211e-13 | -0.087565 | 0.0021197 | 0.058449 | 0.018576 | 0.16125 | -0.2206 | -0.004606 | 0.015345 | 0.017053 | 0.04038 | 0.0028629 | -17.7768 | -64.7858 | -80.5266 | -3.1482 | -3.0446 | -3.0264 | -120.3926 | 0.12009 | 0.091933 | 0.030644 | 0.066194 | 0.1007 | -0.13419 | -0.054257 | -0.032813 | -3.4228 | 102.583 | 39.8332 | 39.866 | -3.3193 | -3.3011 | 120.3055 | -0.20846 | 120.4799 | 120.3904 | 0.084901 | -0.17396 | -0.40884 | 117.2116 | 117.3152 | 117.3334 | 55.574 | -120.6673 | 120.426 | 120.4605 | 120.2256 | 120.4517 | -0.32892
2480.125 | 120.8359 | -120.3918 | 0.29755 | 1.4211e-13 | -0.087993 | 0.0016923 | 0.058662 | 0.018362 | 0.16189 | -0.22823 | -0.004606 | 0.014704 | 0.017267 | 0.04038 | 0.0028629 | -17.667 | -64.6576 | -80.4717 | -2.9009 | -2.8019 | -2.77 | -120.4109 | 0.11552 | 0.082776 | 0.026066 | 0.066194 | 0.091543 | -0.13419 | -0.058836 | -0.019085 | -3.1985 | 102.7249 | 39.9202 | 39.9392 | -3.0995 | -3.0676 | 120.333 | -0.23135 | 120.5074 | 120.4179 | 0.084902 | -0.206 | -0.43173 | 117.4909 | 117.5899 | 117.6218 | 55.7342 | -120.7085 | 120.458 | 120.4834 | 120.2577 | 120.4746 | -0.35638
2481.875 | 120.9091 | -120.3827 | 0.28839 | 1.4211e-13 | -0.088206 | 0.0016923 | 0.058235 | 0.018576 | 0.16146 | -0.24349 | -0.005247 | 0.014704 | 0.017267 | 0.04038 | 0.0024357 | -17.6257 | -64.5477 | -80.4625 | -3.107 | -3.0172 | -2.9944 | -120.4292 | 0.11552 | 0.082776 | 0.021487 | 0.066194 | 0.096121 | -0.12961 | -0.063415 | -0.046557 | -3.3954 | 102.7569 | 39.9202 | 39.9667 | -3.3055 | -3.2828 | 120.3193 | -0.2222 | 120.4982 | 120.4042 | 0.084902 | -0.19227 | -0.418 | 117.2757 | 117.3655 | 117.3883 | 55.835 | -120.7176 | 120.4489 | 120.4788 | 120.2531 | 120.4655 | -0.35181
2483.5469 | 120.9366 | -120.4102 | 0.28839 | 1.4211e-13 | -0.087993 | 0.0019059 | 0.058449 | 0.019003 | 0.16167 | -0.23586 | -0.0050332 | 0.01449 | 0.017481 | 0.039953 | 0.0024357 | -17.6761 | -64.4058 | -80.4442 | -2.8735 | -2.7836 | -2.7563 | -120.443 | 0.11094 | 0.082776 | 0.021487 | 0.061616 | 0.091543 | -0.12961 | -0.067994 | -0.032827 | -3.1619 | 102.734 | 39.9659 | 39.9988 | -3.072 | -3.0447 | 120.3422 | -0.22678 | 120.5211 | 120.4316 | 0.089481 | -0.19685 | -0.418 | 117.5367 | 117.6265 | 117.6539 | 56.0044 | -120.7314 | 120.4718 | 120.5017 | 120.2805 | 120.4929 | -0.35639
2485.2812 | 120.9137 | -120.4376 | 0.28381 | 1.4211e-13 | -0.087993 | 0.0021197 | 0.058449 | 0.018576 | 0.16167 | -0.22823 | -0.004606 | 0.014704 | 0.017267 | 0.040807 | 0.0028629 | -17.5708 | -64.3005 | -80.3984 | -2.9009 | -2.8157 | -2.7883 | -120.4521 | 0.12009 | 0.082776 | 0.026066 | 0.061616 | 0.1007 | -0.12503 | -0.063415 | -0.014519 | -3.1847 | 102.8668 | 40.0392 | 40.0537 | -3.0995 | -3.0722 | 120.3742 | -0.2222 | 120.5577 | 120.4637 | 0.089481 | -0.18311 | -0.40884 | 117.5367 | 117.6219 | 117.6493 | 56.1371 | -120.736 | 120.4992 | 120.5383 | 120.3126 | 120.5204 | -0.34723
2487.0312 | 120.8633 | -120.4926 | 0.31128 | 1.4211e-13 | -0.087993 | 0.0023333 | 0.058449 | 0.01879 | 0.1621 | -0.23586 | -0.0050332 | 0.014918 | 0.017481 | 0.04038 | 0.0024357 | -17.4609 | -64.1402 | -80.3893 | -2.8414 | -2.747 | -2.7242 | -120.4796 | 0.11094 | 0.087354 | 0.026066 | 0.066194 | 0.1007 | -0.12961 | -0.063415 | 0.012939 | -3.1527 | 103.0316 | 40.1033 | 40.0903 | -3.0583 | -3.0355 | 120.4291 | -0.24508 | 120.6035 | 120.5186 | 0.089481 | -0.21058 | -0.44089 | 117.6511 | 117.7456 | 117.7683 | 56.3523 | -120.7909 | 120.5587 | 120.5933 | 120.3629 | 120.5799 | -0.37469
2488.7812 | 121.0098 | -120.4605 | 0.28839 | 1.4211e-13 | -0.088206 | 0.0021197 | 0.058449 | 0.019003 | 0.16167 | -0.24349 | -0.0048196 | 0.014704 | 0.017267 | 0.040807 | 0.0024357 | -17.4426 | -63.9754 | -80.3298 | -2.7819 | -2.6966 | -2.6693 | -120.4934 | 0.11552 | 0.087354 | 0.021487 | 0.057037 | 0.1007 | -0.13876 | -0.063415 | -0.032842 | -3.0703 | 103.0179 | 40.1307 | 40.1636 | -2.985 | -2.9577 | 120.3971 | -0.23135 | 120.576 | 120.482 | 0.084902 | -0.18769 | -0.42716 | 117.6786 | 117.7639 | 117.7912 | 56.4851 | -120.7817 | 120.5175 | 120.5612 | 120.3217 | 120.5479 | -0.35181
2490.5312 | 121.0327 | -120.4651 | 0.27924 | 1.4211e-13 | -0.088634 | 0.0016923 | 0.058235 | 0.018576 | 0.16189 | -0.23586 | -0.0050332 | 0.01449 | 0.017267 | 0.040594 | 0.0026493 | -17.2732 | -63.8564 | -80.316 | -2.7773 | -2.7012 | -2.6785 | -120.5117 | 0.12009 | 0.087354 | 0.016908 | 0.066194 | 0.10528 | -0.12961 | -0.058836 | -0.046579 | -3.0566 | 103.1919 | 40.1491 | 40.1956 | -2.9804 | -2.9577 | 120.4063 | -0.21304 | 120.5852 | 120.482 | 0.075744 | -0.17396 | -0.40884 | 117.6878 | 117.7639 | 117.7866 | 56.6087 | -120.7909 | 120.5313 | 120.5704 | 120.3355 | 120.5524 | -0.33807
2492.2188 | 120.8954 | -120.5383 | 0.31128 | 1.4211e-13 | -0.08842 | 0.0016923 | 0.058662 | 0.01879 | 0.1621 | -0.22823 | -0.0048196 | 0.014277 | 0.017481 | 0.040594 | 0.0024357 | -17.0992 | -63.7785 | -80.2428 | -2.7361 | -2.66 | -2.6372 | -120.5208 | 0.11094 | 0.082776 | 0.021487 | 0.066194 | 0.091543 | -0.12961 | -0.054257 | 0.017505 | -3.0474 | 103.4391 | 40.2956 | 40.278 | -2.9713 | -2.9485 | 120.4841 | -0.24508 | 120.6493 | 120.5598 | 0.075744 | -0.21974 | -0.44089 | 117.8022 | 117.8783 | 117.9011 | 56.7598 | -120.8321 | 120.6045 | 120.6299 | 120.4087 | 120.6211 | -0.36554
2493.9531 | 121.0327 | -120.5109 | 0.3067 | 1.4211e-13 | -0.087993 | 0.0016923 | 0.058235 | 0.018362 | 0.16167 | -0.22823 | -0.0050332 | 0.014704 | 0.017267 | 0.040166 | 0.0024357 | -17.0855 | -63.6778 | -80.2519 | -3.1436 | -3.0538 | -3.0356 | -120.53 | 0.11094 | 0.087354 | 0.021487 | 0.057037 | 0.096121 | -0.13419 | -0.063415 | -0.019119 | -3.4503 | 103.4254 | 40.2589 | 40.2781 | -3.3605 | -3.3423 | 120.4474 | -0.24966 | 120.6218 | 120.5324 | 0.084902 | -0.21058 | -0.44089 | 117.3673 | 117.4571 | 117.4753 | 56.8331 | -120.8367 | 120.5679 | 120.607 | 120.3767 | 120.5982 | -0.37012
2495.7031 | 120.9686 | -120.52 | 0.3067 | 1.4211e-13 | -0.087565 | 0.0016923 | 0.058235 | 0.019003 | 0.16167 | -0.23586 | -0.005247 | 0.014704 | 0.017053 | 0.040594 | 0.0020083 | -16.9573 | -63.6183 | -80.1924 | -3.2397 | -3.1545 | -3.118 | -120.5483 | 0.11094 | 0.082776 | 0.021487 | 0.070773 | 0.096121 | -0.12045 | -0.058836 | -0.028279 | -3.5464 | 103.5627 | 40.3276 | 40.3559 | -3.4612 | -3.4247 | 120.4612 | -0.23593 | 120.631 | 120.5415 | 0.080323 | -0.21058 | -0.42715 | 117.2803 | 117.3655 | 117.402 | 56.9017 | -120.855 | 120.5908 | 120.6161 | 120.3996 | 120.6028 | -0.36554
2497.3906 | 121.0144 | -120.52 | 0.30212 | 1.4211e-13 | -0.087779 | 0.0014787 | 0.058449 | 0.01879 | 0.16189 | -0.22823 | -0.0050332 | 0.014704 | 0.017267 | 0.04038 | 0.0024357 | -16.8245 | -63.4809 | -80.0459 | -3.0062 | -2.921 | -2.8982 | -120.5575 | 0.11552 | 0.087354 | 0.016908 | 0.066194 | 0.091543 | -0.12961 | -0.058836 | -0.037437 | -3.3084 | 103.6955 | 40.4741 | 40.5115 | -3.2231 | -3.2004 | 120.4612 | -0.23593 | 120.6355 | 120.5369 | 0.075744 | -0.21058 | -0.43173 | 117.5138 | 117.599 | 117.6218 | 57.0391 | -120.8596 | 120.5862 | 120.6116 | 120.3904 | 120.6074 | -0.36096
2499.125 | 121.0693 | -120.5429 | 0.28381 | 1.4211e-13 | -0.08842 | 0.0014787 | 0.058449 | 0.019003 | 0.1621 | -0.23586 | -0.005247 | 0.01449 | 0.017053 | 0.040594 | 0.0022219 | -16.7696 | -63.3665 | -79.9955 | -2.8872 | -2.8019 | -2.77 | -120.5712 | 0.11094 | 0.087354 | 0.016908 | 0.061616 | 0.091543 | -0.12503 | -0.054257 | -0.028285 | -3.171 | 103.7733 | 40.5474 | 40.5756 | -3.0858 | -3.0538 | 120.4887 | -0.2222 | 120.6538 | 120.5598 | 0.071165 | -0.19227 | -0.40884 | 117.6557 | 117.741 | 117.7729 | 57.1765 | -120.855 | 120.6045 | 120.6345 | 120.4179 | 120.6303 | -0.33807
2500.875 | 121.0968 | -120.5566 | 0.31128 | 1.4211e-13 | -0.088634 | 0.0019059 | 0.058449 | 0.01879 | 0.1621 | -0.24349 | -0.004606 | 0.014704 | 0.017267 | 0.040594 | 0.0024357 | -16.7513 | -63.1696 | -79.9498 | -2.7773 | -2.6875 | -2.6693 | -120.5895 | 0.11552 | 0.087354 | 0.021487 | 0.057037 | 0.096121 | -0.12503 | -0.058836 | -0.032868 | -3.0886 | 103.8054 | 40.6069 | 40.6397 | -2.9987 | -2.9806 | 120.4978 | -0.25424 | 120.6722 | 120.5781 | 0.080323 | -0.21516 | -0.43631 | 117.7793 | 117.8692 | 117.8873 | 57.3871 | -120.9008 | 120.6137 | 120.6528 | 120.4316 | 120.644 | -0.37011
2502.5625 | 121.0602 | -120.5566 | 0.31586 | 1.4211e-13 | -0.08842 | 0.0016923 | 0.058449 | 0.019003 | 0.16231 | -0.2206 | -0.0050332 | 0.014704 | 0.017481 | 0.04038 | 0.0024357 | -16.6505 | -63.0047 | -79.8628 | -2.8231 | -2.7287 | -2.7105 | -120.5941 | 0.11552 | 0.082776 | 0.016908 | 0.066194 | 0.10986 | -0.12503 | -0.058836 | -0.037447 | -3.139 | 103.9061 | 40.6939 | 40.7313 | -3.0445 | -3.0264 | 120.4978 | -0.24966 | 120.6722 | 120.5735 | 0.075744 | -0.206 | -0.44089 | 117.7335 | 117.828 | 117.8461 | 57.5519 | -120.9099 | 120.6228 | 120.6665 | 120.4316 | 120.6394 | -0.37469
2504.3125 | 121.0602 | -120.5933 | 0.29755 | 1.4211e-13 | -0.08842 | 0.0019059 | 0.058449 | 0.019003 | 0.16274 | -0.23586 | -0.0048196 | 0.01449 | 0.017481 | 0.040594 | 0.0024357 | -16.559 | -62.872 | -79.7987 | -2.8277 | -2.7333 | -2.7151 | -120.6078 | 0.11552 | 0.082776 | 0.026066 | 0.061616 | 0.1007 | -0.12961 | -0.063415 | -0.014563 | -3.1252 | 104.0343 | 40.7946 | 40.8091 | -3.0308 | -3.0126 | 120.5298 | -0.23593 | 120.7088 | 120.6193 | 0.089481 | -0.19685 | -0.42715 | 117.7656 | 117.86 | 117.8782 | 57.7213 | -120.9054 | 120.6549 | 120.694 | 120.4637 | 120.676 | -0.36096
2506 | 120.9869 | -120.6116 | 0.32501 | 1.4211e-13 | -0.08842 | 0.0014787 | 0.058235 | 0.019003 | 0.16253 | -0.23586 | -0.0054606 | 0.014918 | 0.017481 | 0.04038 | 0.0020083 | -16.504 | -62.8079 | -79.7575 | -2.8277 | -2.7424 | -2.7151 | -120.6216 | 0.11552 | 0.087354 | 0.030644 | 0.070773 | 0.10986 | -0.12961 | -0.063415 | -0.00999 | -3.1527 | 104.1075 | 40.8541 | 40.8641 | -3.0674 | -3.0401 | 120.5482 | -0.25424 | 120.7271 | 120.6422 | 0.094059 | -0.21516 | -0.45462 | 117.7839 | 117.8692 | 117.8965 | 57.8037 | -120.9466 | 120.6823 | 120.7214 | 120.482 | 120.6989 | -0.38843
2507.7344 | 121.0098 | -120.6345 | 0.32959 | 1.4211e-13 | -0.088634 | 0.0019059 | 0.058235 | 0.019431 | 0.16295 | -0.23586 | -0.0048196 | 0.01449 | 0.017053 | 0.040594 | 0.0022219 | -16.4674 | -62.7254 | -79.6705 | -2.7544 | -2.6737 | -2.651 | -120.6307 | 0.12009 | 0.091933 | 0.039802 | 0.066194 | 0.1007 | -0.13419 | -0.063415 | 0.003741 | -3.084 | 104.167 | 40.964 | 40.9602 | -3.0033 | -2.9806 | 120.571 | -0.2634 | 120.7546 | 120.6743 | 0.10322 | -0.22889 | -0.46378 | 117.88 | 117.9607 | 117.9835 | 57.909 | -120.9603 | 120.7007 | 120.7352 | 120.5003 | 120.7264 | -0.393
2509.4688 | 121.1288 | -120.6116 | 0.29755 | 1.4211e-13 | -0.088634 | 0.0014787 | 0.058876 | 0.019217 | 0.16253 | -0.24349 | -0.0050332 | 0.014704 | 0.017481 | 0.040807 | 0.0024357 | -16.4399 | -62.6293 | -79.6018 | -2.8139 | -2.7287 | -2.7059 | -120.6445 | 0.12009 | 0.091933 | 0.026066 | 0.075351 | 0.10528 | -0.12961 | -0.058836 | -0.032884 | -3.1115 | 104.1716 | 41.0098 | 41.0426 | -3.0262 | -3.0035 | 120.5527 | -0.22219 | 120.7317 | 120.6376 | 0.084902 | -0.19227 | -0.42715 | 117.7976 | 117.8829 | 117.9056 | 57.9823 | -120.942 | 120.6869 | 120.7169 | 120.482 | 120.7035 | -0.35638
2511.1562 | 121.1609 | -120.607 | 0.3067 | 1.4211e-13 | -0.088847 | 0.0016923 | 0.058876 | 0.019431 | 0.16253 | -0.23586 | -0.0050332 | 0.014918 | 0.017053 | 0.040807 | 0.0022219 | -16.4308 | -62.5515 | -79.5286 | -2.8002 | -2.7195 | -2.7013 | -120.649 | 0.12009 | 0.091933 | 0.026066 | 0.066194 | 0.096121 | -0.12503 | -0.058836 | -0.04204 | -3.1069 | 104.1762 | 41.0784 | 41.1205 | -3.0262 | -3.008 | 120.5482 | -0.24051 | 120.7271 | 120.6331 | 0.084902 | -0.21058 | -0.43173 | 117.8068 | 117.8875 | 117.9056 | 58.0555 | -120.9557 | 120.6732 | 120.7031 | 120.482 | 120.6989 | -0.36554
2512.8906 | 121.1746 | -120.6116 | 0.29297 | 1.4211e-13 | -0.088847 | 0.0016923 | 0.058876 | 0.019431 | 0.16274 | -0.2206 | -0.0050332 | 0.014704 | 0.017267 | 0.040594 | 0.0022219 | -16.3987 | -62.4782 | -79.4599 | -2.6629 | -2.5776 | -2.5548 | -120.6628 | 0.12467 | 0.091933 | 0.030644 | 0.070773 | 0.1007 | -0.12503 | -0.049678 | -0.0512 | -2.9558 | 104.2128 | 41.1517 | 41.2029 | -2.8705 | -2.8478 | 120.5619 | -0.2222 | 120.7362 | 120.6422 | 0.080322 | -0.19227 | -0.418 | 117.9487 | 118.034 | 118.0567 | 58.1334 | -120.9557 | 120.6823 | 120.7123 | 120.4865 | 120.7035 | -0.34265
2514.5781 | 121.1792 | -120.6116 | 0.33875 | 1.4211e-13 | -0.089061 | 0.0014787 | 0.058662 | 0.019217 | 0.16253 | -0.23586 | -0.0048196 | 0.014704 | 0.017053 | 0.04038 | 0.0022219 | -16.3392 | -62.3683 | -79.405 | -2.4202 | -2.3303 | -2.3213 | -120.6857 | 0.11094 | 0.087354 | 0.021487 | 0.066194 | 0.1007 | -0.13419 | -0.063415 | -0.074094 | -2.7589 | 104.2724 | 41.2066 | 41.2807 | -2.6691 | -2.6601 | 120.5482 | -0.27255 | 120.7225 | 120.6331 | 0.084902 | -0.23805 | -0.47293 | 118.1914 | 118.2813 | 118.2903 | 58.2433 | -121.0244 | 120.6778 | 120.7123 | 120.4774 | 120.6989 | -0.40216
2516.3281 | 121.1517 | -120.6711 | 0.33417 | 1.4211e-13 | -0.089275 | 0.0014787 | 0.058876 | 0.019431 | 0.16274 | -0.23586 | -0.005247 | 0.014704 | 0.017267 | 0.040807 | 0.0020083 | -16.2797 | -62.3592 | -79.3683 | -2.4797 | -2.3898 | -2.3671 | -120.6857 | 0.12467 | 0.087354 | 0.030644 | 0.075351 | 0.1007 | -0.12503 | -0.063415 | -0.014584 | -2.8139 | 104.3914 | 41.3028 | 41.3173 | -2.724 | -2.7013 | 120.6077 | -0.25882 | 120.7958 | 120.7017 | 0.094059 | -0.23347 | -0.4592 | 118.1914 | 118.2812 | 118.304 | 58.3119 | -121.0198 | 120.7464 | 120.7718 | 120.5461 | 120.7584 | -0.39758
2518.0156 | 121.0831 | -120.6985 | 0.33417 | 1.4211e-13 | -0.088847 | 0.0012649 | 0.058662 | 0.019431 | 0.16295 | -0.24349 | -0.0048196 | 0.014918 | 0.017053 | 0.040807 | 0.0020083 | -16.2385 | -62.2859 | -79.3271 | -2.7224 | -2.6325 | -2.6144 | -120.7177 | 0.12009 | 0.096512 | 0.026066 | 0.070773 | 0.10528 | -0.12045 | -0.058836 | -0.019172 | -3.0565 | 104.4601 | 41.3714 | 41.3906 | -2.9667 | -2.9485 | 120.6397 | -0.26339 | 120.8186 | 120.7246 | 0.084902 | -0.22889 | -0.45462 | 117.9762 | 118.066 | 118.0842 | 58.4126 | -121.0519 | 120.7693 | 120.8038 | 120.5781 | 120.7951 | -0.393
2519.7656 | 121.2341 | -120.6802 | 0.29297 | 1.4211e-13 | -0.089061 | 0.0016923 | 0.058662 | 0.019431 | 0.16295 | -0.23586 | -0.0048196 | 0.014704 | 0.017267 | 0.040594 | 0.0017947 | -16.2202 | -62.2126 | -79.2768 | -2.7041 | -2.6005 | -2.5915 | -120.7269 | 0.12009 | 0.091933 | 0.026066 | 0.070773 | 0.1007 | -0.12045 | -0.054257 | -0.04664 | -2.997 | 104.4601 | 41.4035 | 41.4501 | -2.8934 | -2.8844 | 120.626 | -0.2222 | 120.8003 | 120.7063 | 0.080323 | -0.19227 | -0.41342 | 117.9762 | 118.0798 | 118.0888 | 58.4676 | -121.0198 | 120.751 | 120.7809 | 120.5598 | 120.7722 | -0.34723
2521.5156 | 121.225 | -120.7031 | 0.31586 | 1.4211e-13 | -0.089488 | 0.0014787 | 0.058876 | 0.019644 | 0.16317 | -0.22823 | -0.0050332 | 0.01449 | 0.017267 | 0.04038 | 0.0020083 | -16.1744 | -62.1577 | -79.2447 | -2.6629 | -2.5638 | -2.5457 | -120.7315 | 0.12467 | 0.087354 | 0.021487 | 0.066194 | 0.10986 | -0.13419 | -0.058836 | -0.028331 | -2.9787 | 104.5287 | 41.4584 | 41.4867 | -2.8797 | -2.8615 | 120.6443 | -0.24966 | 120.8278 | 120.7246 | 0.080323 | -0.206 | -0.45004 | 118.0403 | 118.1393 | 118.1575 | 58.5454 | -121.0473 | 120.7693 | 120.813 | 120.5689 | 120.7905 | -0.37469
2523.25 | 121.1517 | -120.7397 | 0.34332 | 1.4211e-13 | -0.088634 | 0.0016923 | 0.058235 | 0.019644 | 0.16317 | -0.23586 | -0.0050332 | 0.01449 | 0.017053 | 0.04038 | 0.0020083 | -16.1103 | -62.1165 | -79.2264 | -3.0062 | -2.9256 | -2.8936 | -120.7406 | 0.11552 | 0.087354 | 0.021487 | 0.061616 | 0.1007 | -0.12503 | -0.063415 | -0.000868 | -3.3496 | 104.6294 | 41.5133 | 41.5142 | -3.2689 | -3.237 | 120.6763 | -0.28171 | 120.8553 | 120.7612 | 0.084902 | -0.24262 | -0.46835 | 117.7335 | 117.8142 | 117.8461 | 58.6233 | -121.0839 | 120.8014 | 120.8404 | 120.6147 | 120.8271 | -0.40674
2524.9219 | 121.1472 | -120.7581 | 0.32044 | 1.4211e-13 | -0.08842 | 0.0014787 | 0.058662 | 0.019644 | 0.16317 | -0.22823 | -0.005247 | 0.014704 | 0.017267 | 0.040807 | 0.0022219 | -16.0325 | -61.9975 | -79.2218 | -2.8826 | -2.7974 | -2.7792 | -120.7498 | 0.12009 | 0.091933 | 0.016908 | 0.061616 | 0.10986 | -0.13419 | -0.063415 | 0.008286 | -3.2031 | 104.7256 | 41.5362 | 41.528 | -3.1178 | -3.0996 | 120.6946 | -0.25882 | 120.8782 | 120.775 | 0.080323 | -0.21058 | -0.45462 | 117.8754 | 117.9607 | 117.9789 | 58.7606 | -121.0702 | 120.8197 | 120.8679 | 120.6239 | 120.85 | -0.38385
2526.6875 | 121.2708 | -120.7214 | 0.30212 | 1.4211e-13 | -0.088634 | 0.0012649 | 0.058021 | 0.019431 | 0.16295 | -0.23586 | -0.0048196 | 0.014704 | 0.017053 | 0.040807 | 0.0022219 | -16.0233 | -61.9746 | -79.2218 | -3.2168 | -3.1362 | -3.1043 | -120.7589 | 0.12467 | 0.091933 | 0.021487 | 0.066194 | 0.10528 | -0.12961 | -0.058836 | -0.037493 | -3.519 | 104.6981 | 41.4996 | 41.5371 | -3.4383 | -3.4064 | 120.6626 | -0.23593 | 120.8461 | 120.7429 | 0.080323 | -0.19684 | -0.43173 | 117.5046 | 117.5852 | 117.6172 | 58.7469 | -121.0611 | 120.7876 | 120.8267 | 120.5918 | 120.8134 | -0.36096
2528.4219 | 121.2296 | -120.7535 | 0.32501 | 1.4211e-13 | -0.088847 | 0.0010513 | 0.058021 | 0.019858 | 0.16274 | -0.24349 | -0.0048196 | 0.014704 | 0.017053 | 0.04038 | 0.0022219 | -15.9363 | -61.8189 | -79.0662 | -3.0154 | -2.9256 | -2.9165 | -120.7772 | 0.11552 | 0.091933 | 0.030644 | 0.066194 | 0.10986 | -0.12503 | -0.054257 | -0.023766 | -3.3404 | 104.8172 | 41.6873 | 41.7111 | -3.2506 | -3.2416 | 120.6992 | -0.25882 | 120.869 | 120.7841 | 0.084901 | -0.21516 | -0.45004 | 117.7381 | 117.8279 | 117.8369 | 58.9346 | -121.1023 | 120.8197 | 120.8633 | 120.6285 | 120.8454 | -0.37927
2530.1094 | 121.1655 | -120.7672 | 0.35248 | 1.4211e-13 | -0.088847 | 0.0014787 | 0.058449 | 0.019858 | 0.16274 | -0.23586 | -0.0048196 | 0.014704 | 0.017267 | 0.040594 | 0.0015811 | -15.9088 | -61.6769 | -79.0341 | -2.8918 | -2.7974 | -2.7838 | -120.7727 | 0.12009 | 0.091933 | 0.026066 | 0.061616 | 0.10986 | -0.12045 | -0.058836 | -0.005454 | -3.2443 | 104.8584 | 41.7331 | 41.7386 | -3.1498 | -3.1362 | 120.7084 | -0.29086 | 120.8873 | 120.7933 | 0.084902 | -0.24262 | -0.47293 | 117.8754 | 117.9698 | 117.9835 | 59.0903 | -121.1251 | 120.8288 | 120.8771 | 120.6468 | 120.8591 | -0.41131
2531.8594 | 121.2524 | -120.7581 | 0.32501 | 1.4211e-13 | -0.088847 | 0.0010513 | 0.058235 | 0.020071 | 0.16274 | -0.23586 | -0.005247 | 0.01449 | 0.01684 | 0.040594 | 0.0017947 | -15.8722 | -61.5808 | -78.9425 | -2.9559 | -2.866 | -2.8479 | -120.791 | 0.12009 | 0.091933 | 0.026066 | 0.070773 | 0.10528 | -0.12961 | -0.058836 | -0.032925 | -3.2809 | 104.8858 | 41.8155 | 41.8484 | -3.1911 | -3.1729 | 120.6992 | -0.25424 | 120.8782 | 120.7841 | 0.084902 | -0.21973 | -0.45462 | 117.8022 | 117.892 | 117.9102 | 59.1773 | -121.116 | 120.8288 | 120.8633 | 120.6285 | 120.85 | -0.38385
2533.6094 | 121.1884 | -120.7764 | 0.33875 | 1.4211e-13 | -0.088847 | 0.0012649 | 0.058662 | 0.019858 | 0.16274 | -0.23586 | -0.0050332 | 0.014918 | 0.017053 | 0.040807 | 0.0015811 | -15.8127 | -61.4846 | -78.851 | -3.02 | -2.921 | -2.9028 | -120.8322 | 0.11094 | 0.087354 | 0.026066 | 0.070773 | 0.10528 | -0.12961 | -0.058836 | -0.055825 | -3.3587 | 104.9637 | 41.9254 | 41.9812 | -3.2597 | -3.2415 | 120.7175 | -0.26797 | 120.8873 | 120.8024 | 0.084902 | -0.23347 | -0.46835 | 117.7564 | 117.8554 | 117.8736 | 59.2917 | -121.1709 | 120.8471 | 120.8816 | 120.6468 | 120.8637 | -0.39758
2535.3438 | 121.2158 | -120.7718 | 0.32044 | 1.4211e-13 | -0.088847 | 0.0012649 | 0.058449 | 0.020071 | 0.16295 | -0.2206 | -0.0050332 | 0.01449 | 0.01684 | 0.040807 | 0.0017947 | -15.7532 | -61.3885 | -78.8098 | -3.0749 | -2.9897 | -2.9577 | -120.823 | 0.11552 | 0.096512 | 0.026066 | 0.066194 | 0.11444 | -0.13419 | -0.058836 | -0.051244 | -3.3953 | 105.0186 | 41.962 | 42.0133 | -3.3101 | -3.2782 | 120.713 | -0.25424 | 120.8873 | 120.7979 | 0.084902 | -0.206 | -0.45462 | 117.6969 | 117.7821 | 117.814 | 59.3833 | -121.1435 | 120.838 | 120.8862 | 120.6376 | 120.8683 | -0.37927
2537.0312 | 121.344 | -120.7581 | 0.31128 | 1.4211e-13 | -0.089061 | 0.0012649 | 0.058449 | 0.019644 | 0.16295 | -0.2206 | -0.0050332 | 0.014704 | 0.017267 | 0.040807 | 0.0020083 | -15.7074 | -61.3198 | -78.6999 | -2.9147 | -2.834 | -2.8158 | -120.8185 | 0.12009 | 0.087354 | 0.021487 | 0.066194 | 0.1007 | -0.12503 | -0.063415 | -0.060398 | -3.2259 | 105.0507 | 42.0582 | 42.1186 | -3.1453 | -3.1271 | 120.6946 | -0.24508 | 120.8782 | 120.7795 | 0.084902 | -0.21058 | -0.43631 | 117.8434 | 117.9241 | 117.9422 | 59.4382 | -121.1297 | 120.8243 | 120.8588 | 120.633 | 120.8454 | -0.37469
2538.7188 | 121.2204 | -120.8221 | 0.37079 | 1.4211e-13 | -0.089061 | 0.0014787 | 0.058662 | 0.019858 | 0.1636 | -0.23586 | -0.0050332 | 0.01449 | 0.017053 | 0.041021 | 0.0020083 | -15.6525 | -61.2282 | -78.6175 | -2.7819 | -2.7058 | -2.6785 | -120.8322 | 0.12467 | 0.082776 | 0.016908 | 0.061616 | 0.10528 | -0.12961 | -0.067994 | -0.010048 | -3.1527 | 105.1697 | 42.2047 | 42.2147 | -3.0766 | -3.0492 | 120.7541 | -0.30917 | 120.9468 | 120.8391 | 0.084902 | -0.26551 | -0.5004 | 118.0403 | 118.1164 | 118.1437 | 59.5939 | -121.203 | 120.8838 | 120.9274 | 120.6925 | 120.9049 | -0.43878
2540.4688 | 121.2067 | -120.6802 | 0.27008 | 1.4211e-13 | -0.088634 | 0.0012649 | 0.058021 | 0.020285 | 0.16274 | -0.23586 | -0.0050332 | 0.014704 | 0.017053 | 0.040807 | 0.0022219 | -15.6433 | -61.0451 | -78.4481 | -3.0978 | -3.008 | -2.9944 | -120.7818 | 0.11094 | 0.082776 | 0.016908 | 0.061616 | 0.10528 | -0.12503 | -0.063415 | -0.10159 | -3.3679 | 105.0369 | 42.2321 | 42.3337 | -3.2781 | -3.2645 | 120.6168 | -0.20847 | 120.7912 | 120.6971 | 0.080323 | -0.1648 | -0.39511 | 117.5824 | 117.6722 | 117.6859 | 59.6351 | -121.0519 | 120.7419 | 120.7855 | 120.5552 | 120.763 | -0.3335
2542.1562 | 120.7901 | -120.2911 | 0.28839 | 1.4211e-13 | -0.088634 | 0.0012649 | 0.057808 | 0.019858 | 0.16167 | -0.23586 | -0.0050332 | 0.014918 | 0.017053 | 0.040807 | 0.0020083 | -15.6479 | -60.4774 | -77.7659 | -3.052 | -2.9668 | -2.944 | -119.9118 | 0.11552 | 0.087354 | 0.021487 | 0.057037 | 0.1007 | -0.13876 | -0.067994 | 0.37931 | -3.3404 | 104.6433 | 42.5252 | 42.1459 | -3.2552 | -3.2324 | 120.2231 | -0.23135 | 120.4067 | 120.3126 | 0.089481 | -0.18769 | -0.42716 | 117.2391 | 117.3244 | 117.3471 | 59.8138 | -120.2002 | 120.3482 | 120.3918 | 120.1524 | 120.3785 | -0.35639
2543.9062 | 121.0373 | -120.4559 | 0.29755 | 1.4211e-13 | -0.088847 | 0.0014787 | 0.058021 | 0.019858 | 0.16274 | -0.22823 | -0.0048196 | 0.014063 | 0.01684 | 0.040807 | 0.0020083 | -15.5288 | -60.6468 | -78.1093 | -2.9605 | -2.866 | -2.857 | -120.5849 | 0.11552 | 0.087354 | 0.021487 | 0.066194 | 0.10528 | -0.12961 | -0.067994 | -0.129 | -3.258 | 104.9271 | 42.3466 | 42.4756 | -3.1636 | -3.1546 | 120.3879 | -0.23135 | 120.5714 | 120.4774 | 0.089481 | -0.19227 | -0.42715 | 117.4955 | 117.5899 | 117.5989 | 59.8092 | -120.8825 | 120.5221 | 120.5612 | 120.3263 | 120.5433 | -0.36554
2545.5781 | 120.7993 | -120.3323 | 0.18768 | 1.4211e-13 | -0.088847 | 0.0014787 | 0.058021 | 0.019858 | 0.16231 | -0.22823 | -0.005247 | 0.014704 | 0.017053 | 0.041235 | 0.0017947 | -15.4876 | -60.2988 | -77.798 | -3.0062 | -2.921 | -2.9028 | -120.2415 | 0.11552 | 0.091933 | 0.021487 | 0.061616 | 0.091543 | -0.12503 | -0.067994 | 0.090825 | -3.1939 | 104.8447 | 42.5344 | 42.4435 | -3.1087 | -3.0905 | 120.2643 | -0.12607 | 120.4479 | 120.3538 | 0.089481 | -0.09614 | -0.31271 | 117.3261 | 117.4113 | 117.4295 | 60.0335 | -120.4292 | 120.394 | 120.4239 | 120.2073 | 120.4243 | -0.25568
2547.3281 | 120.9183 | -120.3827 | 0.28381 | 1.4211e-13 | -0.089061 | 0.0012649 | 0.058021 | 0.020071 | 0.16295 | -0.2206 | -0.004606 | 0.015131 | 0.017481 | 0.041235 | 0.0017947 | -15.3274 | -60.2255 | -77.7613 | -2.9879 | -2.9073 | -2.8891 | -120.388 | 0.10636 | 0.082776 | 0.021487 | 0.061616 | 0.096121 | -0.12503 | -0.067994 | -0.005346 | -3.2717 | 105.0553 | 42.6213 | 42.6267 | -3.1911 | -3.1729 | 120.3147 | -0.2222 | 120.489 | 120.4042 | 0.089481 | -0.18769 | -0.40884 | 117.3948 | 117.4754 | 117.4936 | 60.1572 | -120.6718 | 120.4443 | 120.4788 | 120.2577 | 120.4655 | -0.35181
2549.0625 | 121.0098 | -120.5841 | 0.31586 | 1.4211e-13 | -0.089275 | 0.0012649 | 0.058449 | 0.020071 | 0.16317 | -0.22823 | -0.0050332 | 0.014704 | 0.01684 | 0.040807 | 0.0020083 | -15.1855 | -60.2484 | -77.8254 | -2.9055 | -2.8203 | -2.7975 | -120.6261 | 0.12009 | 0.091933 | 0.026066 | 0.052459 | 0.086964 | -0.12961 | -0.072572 | -0.042034 | -3.2214 | 105.3986 | 42.7587 | 42.8007 | -3.1361 | -3.1134 | 120.5115 | -0.2634 | 120.7042 | 120.6102 | 0.098638 | -0.22889 | -0.44546 | 117.6786 | 117.7638 | 117.7866 | 60.3357 | -120.942 | 120.6366 | 120.6711 | 120.4545 | 120.676 | -0.38843
2550.7969 | 120.9824 | -120.4514 | 0.29755 | 1.4211e-13 | -0.088847 | 0.0010513 | 0.058449 | 0.020071 | 0.16317 | -0.22823 | -0.0048196 | 0.014704 | 0.01684 | 0.041021 | 0.0017947 | -15.1122 | -60.0515 | -77.6148 | -2.9284 | -2.8432 | -2.825 | -120.443 | 0.10636 | 0.082776 | 0.021487 | 0.057037 | 0.091543 | -0.12045 | -0.072572 | 0.008372 | -3.2259 | 105.3391 | 42.8365 | 42.8281 | -3.1407 | -3.1225 | 120.3788 | -0.24051 | 120.5577 | 120.4728 | 0.094059 | -0.206 | -0.418 | 117.523 | 117.6082 | 117.6264 | 60.3998 | -120.7405 | 120.5084 | 120.5429 | 120.3309 | 120.5341 | -0.37012
2552.4844 | 121.0464 | -120.4147 | 0.29297 | 1.4211e-13 | -0.088847 | 0.0012649 | 0.058021 | 0.020071 | 0.16317 | -0.24349 | -0.004606 | 0.014704 | 0.01684 | 0.041021 | 0.0020083 | -15.0023 | -59.9737 | -77.6148 | -2.9055 | -2.8157 | -2.8067 | -120.5895 | 0.11094 | 0.091933 | 0.026066 | 0.057037 | 0.096121 | -0.12961 | -0.063415 | -0.17478 | -3.1985 | 105.4124 | 42.7999 | 42.9747 | -3.1086 | -3.0996 | 120.3513 | -0.23593 | 120.5257 | 120.4408 | 0.089481 | -0.19685 | -0.42258 | 117.5092 | 117.5991 | 117.6081 | 60.441 | -120.8825 | 120.4718 | 120.5109 | 120.2851 | 120.5067 | -0.35638
2554.2344 | 120.6848 | -119.7922 | 0.43488 | 1.4211e-13 | -0.080301 | 0.00083771 | 0.049688 | 0.016439 | 0.14095 | -0.22823 | -0.004606 | 0.01449 | 0.017267 | 0.040807 | 0.0020083 | -13.2488 | -52.0573 | -67.126 | -2.5942 | -2.5135 | -2.4816 | -105.0761 | 0.10636 | 0.078197 | 0.007751 | 0.057037 | 0.086964 | -0.12045 | -0.077151 | 14.7161 | -3.0291 | 106.5434 | 52.6662 | 37.9501 | -2.9483 | -2.9164 | 119.715 | -0.37784 | 119.8985 | 119.7999 | 0.084902 | -0.34791 | -0.55533 | 117.198 | 117.2787 | 117.3106 | 67.7349 | -105.511 | 119.8492 | 119.8791 | 119.6717 | 119.8704 | -0.51203
2555.9219 | 120.4788 | -119.9203 | 0.25635 | 1.4211e-13 | -0.079232 | 0.00062391 | 0.048833 | 0.015585 | 0.13924 | -0.22823 | -0.0048196 | 0.014277 | 0.017053 | 0.040807 | 0.0017947 | -13.0977 | -51.311 | -66.1508 | -2.5713 | -2.486 | -2.4633 | -103.7574 | 0.10178 | 0.073618 | 0.016908 | 0.057037 | 0.086964 | -0.12961 | -0.077151 | 16.163 | -2.8276 | 106.8226 | 53.7695 | 37.6066 | -2.7423 | -2.7196 | 119.8432 | -0.19931 | 120.0221 | 119.9373 | 0.094059 | -0.16938 | -0.38596 | 117.3491 | 117.4344 | 117.4571 | 68.6094 | -104.0137 | 119.9774 | 120.0073 | 119.7907 | 119.994 | -0.3335
2557.6562 | 116.7252 | -71.8506 | 44.8196 | 1.4211e-13 | -0.062138 | -0.00023069 | 0.031525 | 0.0081064 | 0.092018 | -0.23586 | -0.004606 | 0.01449 | 0.01684 | 0.041021 | 0.0015811 | -9.3297 | -36.9296 | -47.9018 | -1.8204 | -1.7305 | -1.7261 | -73.8524 | 0.078886 | 0.055303 | -0.010564 | 0.034145 | 0.059493 | -0.13419 | -0.10462 | -2.0018 | -46.6401 | 62.5209 | 23.9488 | 25.9506 | -46.5501 | -46.5457 | 71.746 | -44.7855 | 71.9295 | 71.84 | 0.09406 | -44.7601 | -44.9538 | 70.0302 | 70.1201 | 70.1245 | 34.921 | -118.6721 | 71.8847 | 71.9101 | 71.7164 | 71.9059 | -44.9243
2559.4062 | 120.7443 | -120.3873 | 0.25635 | 1.4211e-13 | -0.089061 | 0.0012649 | 0.058235 | 0.020712 | 0.16317 | -0.23586 | -0.0050332 | 0.01449 | 0.016626 | 0.041021 | 0.0017947 | -14.7597 | -59.5158 | -77.1341 | -2.8735 | -2.779 | -2.7654 | -120.4384 | 0.11094 | 0.082776 | 0.016908 | 0.061616 | 0.091543 | -0.12503 | -0.063415 | -0.051137 | -3.1298 | 105.6276 | 43.2531 | 43.3043 | -3.0354 | -3.0218 | 120.3239 | -0.19473 | 120.4982 | 120.4042 | 0.080323 | -0.16481 | -0.38138 | 117.5138 | 117.6082 | 117.6218 | 60.8714 | -120.6948 | 120.4489 | 120.4788 | 120.2622 | 120.47 | -0.31976
2561.0781 | 120.9595 | -120.4559 | 0.24261 | 1.4211e-13 | -0.089061 | 0.0012649 | 0.058449 | 0.020712 | 0.1636 | -0.23586 | -0.0050332 | 0.014704 | 0.017053 | 0.041021 | 0.0017947 | -14.6727 | -59.4472 | -77.1158 | -2.8735 | -2.7974 | -2.7746 | -120.562 | 0.10636 | 0.078197 | 0.01233 | 0.061616 | 0.096121 | -0.12961 | -0.067994 | -0.1061 | -3.1161 | 105.7832 | 43.3401 | 43.4462 | -3.04 | -3.0172 | 120.3879 | -0.181 | 120.5623 | 120.4683 | 0.080324 | -0.14649 | -0.37222 | 117.5825 | 117.6586 | 117.6813 | 61.0088 | -120.8047 | 120.5175 | 120.5521 | 120.3263 | 120.5341 | -0.31061
2562.8281 | 120.9961 | -120.52 | 0.24719 | 1.4211e-13 | -0.089488 | 0.0010513 | 0.058449 | 0.02114 | 0.1636 | -0.24349 | -0.0048196 | 0.01449 | 0.016412 | 0.041021 | 0.0015811 | -14.5949 | -59.4105 | -77.0654 | -2.9101 | -2.8203 | -2.8067 | -120.5529 | 0.11094 | 0.082776 | 0.016908 | 0.061616 | 0.10528 | -0.12961 | -0.067994 | -0.032858 | -3.1573 | 105.9252 | 43.4546 | 43.4874 | -3.0675 | -3.0538 | 120.452 | -0.18558 | 120.631 | 120.5369 | 0.084902 | -0.14191 | -0.3768 | 117.6099 | 117.6998 | 117.7134 | 61.1095 | -120.8001 | 120.5816 | 120.6253 | 120.3904 | 120.6028 | -0.31519
2564.5781 | 121.051 | -120.5795 | 0.24261 | 1.4211e-13 | -0.089488 | 0.0014787 | 0.058449 | 0.02114 | 0.16424 | -0.24349 | -0.0050332 | 0.01449 | 0.017053 | 0.040807 | 0.0017947 | -14.5399 | -59.4014 | -76.9922 | -2.8826 | -2.7928 | -2.7746 | -120.5849 | 0.11094 | 0.087354 | 0.021487 | 0.057037 | 0.1007 | -0.12503 | -0.067994 | -0.005401 | -3.1252 | 106.0396 | 43.5873 | 43.5927 | -3.0354 | -3.0172 | 120.5115 | -0.18558 | 120.6905 | 120.601 | 0.089481 | -0.14192 | -0.36764 | 117.6969 | 117.7867 | 117.8049 | 61.1781 | -120.8275 | 120.6366 | 120.6802 | 120.4545 | 120.6669 | -0.31061
2566.3125 | 121.0968 | -120.5841 | 0.24719 | 1.4211e-13 | -0.089488 | 0.0016923 | 0.058449 | 0.020926 | 0.16381 | -0.22823 | -0.0050332 | 0.01449 | 0.017053 | 0.041021 | 0.0015811 | -14.4804 | -59.2915 | -76.8915 | -2.8094 | -2.7195 | -2.6968 | -120.6124 | 0.11552 | 0.087354 | 0.016908 | 0.057037 | 0.1007 | -0.12503 | -0.072572 | -0.028298 | -3.0566 | 106.1037 | 43.6926 | 43.7209 | -2.9667 | -2.944 | 120.5115 | -0.19015 | 120.6996 | 120.601 | 0.08948 | -0.14649 | -0.37222 | 117.7747 | 117.8646 | 117.8873 | 61.2926 | -120.8596 | 120.6411 | 120.6848 | 120.4591 | 120.6715 | -0.31976
2568 | 121.1105 | -120.5978 | 0.25177 | 1.4211e-13 | -0.089061 | 0.0014787 | 0.058449 | 0.020926 | 0.16402 | -0.23586 | -0.005247 | 0.01449 | 0.01684 | 0.041021 | 0.0020083 | -14.43 | -59.0992 | -76.8045 | -2.8323 | -2.747 | -2.7288 | -120.6399 | 0.11094 | 0.091933 | 0.016908 | 0.057037 | 0.096121 | -0.12961 | -0.067994 | -0.042038 | -3.084 | 106.1678 | 43.7934 | 43.8354 | -2.9988 | -2.9806 | 120.5298 | -0.19473 | 120.7088 | 120.6147 | 0.084902 | -0.15565 | -0.38138 | 117.7656 | 117.8508 | 117.869 | 61.4986 | -120.8916 | 120.6549 | 120.694 | 120.4682 | 120.6898 | -0.31976
2569.75 | 121.0785 | -120.6299 | 0.27466 | 1.4211e-13 | -0.089488 | 0.0014787 | 0.058449 | 0.021353 | 0.16424 | -0.24349 | -0.0050332 | 0.01449 | 0.017053 | 0.041021 | 0.0017947 | -14.3385 | -59.0809 | -76.7404 | -2.8323 | -2.7424 | -2.7288 | -120.6674 | 0.11552 | 0.087354 | 0.016908 | 0.061616 | 0.1007 | -0.12961 | -0.063415 | -0.037468 | -3.1069 | 106.2914 | 43.8895 | 43.927 | -3.0171 | -3.0035 | 120.5665 | -0.21304 | 120.7454 | 120.6468 | 0.080323 | -0.17396 | -0.40426 | 117.7976 | 117.8875 | 117.9011 | 61.549 | -120.942 | 120.6915 | 120.7306 | 120.5003 | 120.7172 | -0.33807
2571.5 | 120.2316 | -120.2408 | 0.27924 | 1.4211e-13 | -0.089916 | 0.0014787 | 0.058662 | 0.020926 | 0.16424 | -0.23586 | -0.005247 | 0.014704 | 0.016412 | 0.041235 | 0.0017947 | -14.3201 | -59.0076 | -76.6214 | -2.8368 | -2.7424 | -2.7288 | -120.6902 | 0.11094 | 0.087354 | 0.016908 | 0.061616 | 0.091543 | -0.12961 | -0.072572 | -0.44946 | -3.1161 | 105.9206 | 43.6194 | 44.0689 | -3.0217 | -3.0081 | 120.1682 | -0.21762 | 120.3517 | 120.2577 | 0.08948 | -0.18769 | -0.40884 | 117.4039 | 117.4984 | 117.512 | 61.2332 | -120.9695 | 120.3024 | 120.3323 | 120.1112 | 120.3281 | -0.35181
2573.2344 | 120.2362 | -120.1767 | 0.28381 | 1.4211e-13 | -0.089702 | 0.0010513 | 0.058876 | 0.021353 | 0.16488 | -0.25112 | -0.0050332 | 0.014704 | 0.01684 | 0.041235 | 0.0015811 | -14.2652 | -59.0671 | -76.5298 | -2.9147 | -2.8248 | -2.8067 | -120.7131 | 0.11094 | 0.082776 | 0.021487 | 0.061616 | 0.096121 | -0.13419 | -0.072572 | -0.53644 | -3.1985 | 105.9115 | 43.6469 | 44.1833 | -3.1086 | -3.0905 | 120.1041 | -0.2222 | 120.2876 | 120.1982 | 0.094059 | -0.18769 | -0.418 | 117.262 | 117.3519 | 117.37 | 61.1096 | -120.997 | 120.2383 | 120.2728 | 120.0425 | 120.2595 | -0.35638
2574.9844 | 121.1563 | -120.6757 | 0.25177 | 1.4211e-13 | -0.089275 | 0.0012649 | 0.058021 | 0.021567 | 0.16445 | -0.23586 | -0.0050332 | 0.01449 | 0.01684 | 0.041448 | 0.0017947 | -14.192 | -59.0259 | -76.4153 | -3.052 | -2.9576 | -2.944 | -120.7223 | 0.11552 | 0.087354 | 0.021487 | 0.052459 | 0.1007 | -0.12961 | -0.067994 | -0.046639 | -3.3038 | 106.4837 | 44.2603 | 44.307 | -3.2094 | -3.1958 | 120.6077 | -0.19931 | 120.7912 | 120.6971 | 0.089481 | -0.15107 | -0.38138 | 117.6236 | 117.718 | 117.7316 | 61.6497 | -120.9741 | 120.7281 | 120.7764 | 120.5461 | 120.763 | -0.31976
2576.75 | 121.0876 | -120.6528 | 0.25635 | 1.4211e-13 | -0.089061 | 0.00083771 | 0.058235 | 0.021353 | 0.16466 | -0.24349 | -0.005247 | 0.014704 | 0.01684 | 0.041235 | 0.0015811 | -14.1691 | -59.0763 | -76.3329 | -3.2672 | -3.1728 | -3.1592 | -120.7406 | 0.11094 | 0.091933 | 0.016908 | 0.066194 | 0.091543 | -0.13419 | -0.067994 | -0.087843 | -3.5236 | 106.4837 | 44.3198 | 44.4077 | -3.4292 | -3.4156 | 120.5848 | -0.19015 | 120.7637 | 120.6697 | 0.084902 | -0.16481 | -0.39053 | 117.3856 | 117.4799 | 117.4936 | 61.5765 | -120.997 | 120.719 | 120.7443 | 120.5186 | 120.7447 | -0.32434
2578.4375 | 121.2479 | -120.7214 | 0.25177 | 1.4211e-13 | -0.089061 | 0.0014787 | 0.058235 | 0.021781 | 0.16488 | -0.24349 | -0.0050332 | 0.014704 | 0.016626 | 0.041662 | 0.0015811 | -14.1095 | -59.0488 | -76.2047 | -3.2489 | -3.1637 | -3.1455 | -120.7589 | 0.10636 | 0.091933 | 0.01233 | 0.066194 | 0.1007 | -0.12961 | -0.072572 | -0.037493 | -3.5007 | 106.6119 | 44.5167 | 44.5542 | -3.4154 | -3.3972 | 120.6489 | -0.18558 | 120.8278 | 120.7338 | 0.084902 | -0.15107 | -0.38138 | 117.4725 | 117.5578 | 117.576 | 61.6726 | -121.0107 | 120.7876 | 120.8221 | 120.5918 | 120.8134 | -0.32434
2580.1875 | 121.2341 | -120.7443 | 0.2655 | 1.4211e-13 | -0.089061 | 0.0012649 | 0.057594 | 0.021567 | 0.16509 | -0.23586 | -0.005247 | 0.014277 | 0.01684 | 0.041235 | 0.0017947 | -14.0363 | -58.9847 | -76.0994 | -3.2535 | -3.1545 | -3.1409 | -120.7681 | 0.11552 | 0.082776 | 0.016908 | 0.057037 | 0.1007 | -0.12961 | -0.067994 | -0.023763 | -3.519 | 106.708 | 44.6449 | 44.6687 | -3.42 | -3.4064 | 120.6763 | -0.20847 | 120.8598 | 120.7612 | 0.084902 | -0.1648 | -0.39511 | 117.4909 | 117.5898 | 117.6034 | 61.7596 | -121.0336 | 120.8014 | 120.845 | 120.6147 | 120.8271 | -0.3335
2581.8906 | 121.2524 | -120.7077 | 0.25177 | 1.4211e-13 | -0.089061 | 0.00062391 | 0.057808 | 0.021781 | 0.16552 | -0.24349 | -0.0048196 | 0.014277 | 0.01684 | 0.041021 | 0.0017947 | -13.9997 | -58.852 | -75.93 | -3.226 | -3.1362 | -3.1134 | -120.791 | 0.11094 | 0.087354 | 0.026066 | 0.066194 | 0.10528 | -0.13876 | -0.067994 | -0.083279 | -3.4778 | 106.708 | 44.7777 | 44.8609 | -3.388 | -3.3652 | 120.6397 | -0.18558 | 120.8186 | 120.7338 | 0.09406 | -0.14649 | -0.39053 | 117.4817 | 117.5715 | 117.5943 | 61.8558 | -121.0428 | 120.7739 | 120.813 | 120.5689 | 120.7951 | -0.31976
2583.6406 | 120.9915 | -120.6802 | 0.33417 | 1.4211e-13 | -0.087993 | -1.7092e-05 | 0.056739 | 0.051907 | 0.16894 | -0.24349 | -0.005247 | 0.014704 | 0.016626 | 0.041662 | 0.0017947 | -13.6334 | -45.4824 | -32.3448 | -3.0886 | -3.0034 | -2.9806 | -120.7818 | 0.11552 | 0.082776 | 0.016908 | 0.057037 | 0.096121 | -0.13419 | -0.072572 | -0.10159 | -3.4228 | 107.0468 | 88.3354 | 88.437 | -3.3376 | -3.3148 | 120.6077 | -0.27713 | 120.7958 | 120.6971 | 0.08948 | -0.23805 | -0.46835 | 117.5916 | 117.6768 | 117.6996 | 75.1978 | -121.116 | 120.7373 | 120.7764 | 120.5461 | 120.763 | -0.40674
2585.3906 | 121.1929 | -120.7535 | 0.31128 | 1.4211e-13 | -0.087138 | -0.00044449 | 0.056739 | 0.072419 | 0.17086 | -0.24349 | -0.0048196 | 0.014277 | 0.016626 | 0.041448 | 0.0015811 | -13.6425 | -38.6786 | -9.4259 | -3.1115 | -3.0263 | -3.0035 | -120.7818 | 0.11552 | 0.082776 | 0.016908 | 0.061616 | 0.1007 | -0.13419 | -0.067994 | -0.028345 | -3.4228 | 107.1109 | 111.3275 | 111.3559 | -3.3376 | -3.3148 | 120.6855 | -0.24966 | 120.869 | 120.7704 | 0.084902 | -0.21058 | -0.44546 | 117.6419 | 117.7272 | 117.7499 | 82.0749 | -121.0931 | 120.8151 | 120.8542 | 120.6193 | 120.8363 | -0.37927
2587.1406 | 121.2753 | -120.7214 | 0.28839 | 1.4211e-13 | -0.087565 | -0.00044449 | 0.056312 | 0.072846 | 0.17107 | -0.23586 | -0.004606 | 0.01449 | 0.016412 | 0.041235 | 0.0017947 | -13.6013 | -38.4222 | -8.73 | -3.107 | -3.0172 | -3.0035 | -120.7864 | 0.11552 | 0.082776 | 0.021487 | 0.052459 | 0.1007 | -0.13419 | -0.063415 | -0.064967 | -3.3954 | 107.1201 | 111.9914 | 112.0564 | -3.3055 | -3.2919 | 120.658 | -0.23593 | 120.837 | 120.7429 | 0.084902 | -0.18769 | -0.42258 | 117.6145 | 117.7043 | 117.7179 | 82.2992 | -121.0748 | 120.7739 | 120.8221 | 120.5872 | 120.8042 | -0.35181
2588.8281 | 121.2616 | -120.7764 | 0.3067 | 1.4211e-13 | -0.087352 | -0.00023069 | 0.056526 | 0.072846 | 0.17086 | -0.24349 | -0.0050332 | 0.014063 | 0.01684 | 0.041448 | 0.0017947 | -13.5327 | -38.2849 | -8.3317 | -3.1207 | -3.0446 | -3.031 | -120.8001 | 0.11094 | 0.073618 | 0.007751 | 0.057037 | 0.10528 | -0.12961 | -0.067994 | -0.023773 | -3.4274 | 107.2437 | 112.4446 | 112.4684 | -3.3513 | -3.3377 | 120.7084 | -0.24966 | 120.8873 | 120.7841 | 0.075745 | -0.20142 | -0.43631 | 117.6557 | 117.7317 | 117.7454 | 82.4915 | -121.1068 | 120.8334 | 120.8816 | 120.6468 | 120.85 | -0.3747
2590.5781 | 121.1014 | -120.5841 | 0.32044 | 1.4211e-13 | -0.087138 | -0.00065809 | 0.056526 | 0.072633 | 0.17129 | -0.24349 | -0.0050332 | 0.01449 | 0.016626 | 0.041448 | 0.0017947 | -13.5098 | -38.1887 | -8.0845 | -3.1573 | -3.0767 | -3.0585 | -120.8093 | 0.11094 | 0.087354 | 0.021487 | 0.061616 | 0.10528 | -0.13876 | -0.072572 | -0.22519 | -3.4778 | 107.0743 | 112.4996 | 112.7248 | -3.3971 | -3.3789 | 120.5115 | -0.25882 | 120.695 | 120.6056 | 0.094059 | -0.21516 | -0.4592 | 117.4268 | 117.5074 | 117.5256 | 82.3954 | -121.1297 | 120.6457 | 120.6894 | 120.4453 | 120.6715 | -0.39301
2592.3281 | 121.3074 | -120.7718 | 0.3067 | 1.4211e-13 | -0.087352 | -0.00044449 | 0.056739 | 0.072419 | 0.17107 | -0.23586 | -0.005247 | 0.014063 | 0.016412 | 0.041662 | 0.0020083 | -13.5281 | -38.088 | -8.0112 | -3.1665 | -3.0767 | -3.0493 | -120.823 | 0.11552 | 0.082776 | 0.021487 | 0.057037 | 0.096121 | -0.12961 | -0.072572 | -0.051244 | -3.4732 | 107.2437 | 112.7605 | 112.8118 | -3.3834 | -3.356 | 120.6992 | -0.24966 | 120.8873 | 120.7933 | 0.094059 | -0.21058 | -0.43631 | 117.6053 | 117.6951 | 117.7225 | 82.6838 | -121.1297 | 120.8288 | 120.8679 | 120.6422 | 120.8546 | -0.37927
2594.0156 | 121.0098 | -120.5429 | 0.30212 | 1.4211e-13 | -0.087138 | -0.00023069 | 0.056526 | 0.072205 | 0.17065 | -0.22823 | -0.0048196 | 0.014704 | 0.01684 | 0.041448 | 0.0022219 | -13.4869 | -37.9644 | -7.9426 | -3.1619 | -3.0813 | -3.0585 | -120.6811 | 0.11094 | 0.082776 | 0.016908 | 0.066194 | 0.096121 | -0.13419 | -0.072572 | -0.13818 | -3.464 | 107.056 | 112.6003 | 112.7385 | -3.3834 | -3.3606 | 120.4703 | -0.23593 | 120.6538 | 120.5598 | 0.08948 | -0.206 | -0.43631 | 117.381 | 117.4617 | 117.4844 | 82.5785 | -120.9832 | 120.6091 | 120.639 | 120.4087 | 120.6257 | -0.3747
2595.7656 | 121.17 | -120.694 | 0.31586 | 1.4211e-13 | -0.087565 | -0.00023069 | 0.056526 | 0.072633 | 0.17107 | -0.23586 | -0.005247 | 0.014277 | 0.016626 | 0.041448 | 0.0015811 | -13.4228 | -37.9094 | -7.8922 | -3.1436 | -3.0492 | -3.0356 | -120.7269 | 0.11094 | 0.082776 | 0.016908 | 0.061616 | 0.10528 | -0.13419 | -0.067994 | -0.032907 | -3.4594 | 107.2712 | 112.8018 | 112.8347 | -3.3651 | -3.3514 | 120.626 | -0.25424 | 120.8049 | 120.7109 | 0.084902 | -0.21058 | -0.45004 | 117.5504 | 117.6448 | 117.6584 | 82.7845 | -121.0427 | 120.7556 | 120.7992 | 120.5598 | 120.7767 | -0.38385
2597.4688 | 121.2296 | -120.7214 | 0.28839 | 1.4211e-13 | -0.087138 | -0.00023069 | 0.056953 | 0.072846 | 0.17129 | -0.23586 | -0.0048196 | 0.01449 | 0.016626 | 0.041448 | 0.0017947 | -13.3404 | -37.882 | -7.7503 | -3.1253 | -3.0355 | -3.0218 | -120.7589 | 0.11552 | 0.078197 | 0.016908 | 0.061616 | 0.096121 | -0.13419 | -0.072572 | -0.037493 | -3.4137 | 107.3811 | 112.9712 | 113.0086 | -3.3239 | -3.3102 | 120.6489 | -0.22678 | 120.837 | 120.7383 | 0.08948 | -0.19227 | -0.42258 | 117.5962 | 117.686 | 117.6996 | 82.8395 | -121.0473 | 120.7831 | 120.8176 | 120.5872 | 120.7996 | -0.36096
2599.2031 | 121.1563 | -120.7352 | 0.3067 | 1.4211e-13 | -0.087565 | -0.00023069 | 0.056312 | 0.072633 | 0.17129 | -0.22823 | -0.004606 | 0.014277 | 0.016412 | 0.041448 | 0.0017947 | -13.3129 | -37.9094 | -7.8647 | -3.1482 | -3.0629 | -3.0447 | -120.7818 | 0.10636 | 0.087354 | 0.016908 | 0.061616 | 0.091543 | -0.12503 | -0.072572 | -0.046656 | -3.4549 | 107.4223 | 112.8704 | 112.9171 | -3.3696 | -3.3514 | 120.6626 | -0.24509 | 120.8415 | 120.7521 | 0.08948 | -0.21516 | -0.43173 | 117.587 | 117.6722 | 117.6904 | 82.8257 | -121.0885 | 120.7968 | 120.8267 | 120.6101 | 120.8225 | -0.37927
2600.8906 | 121.3028 | -120.7855 | 0.29755 | 1.4211e-13 | -0.087138 | -0.00044449 | 0.056739 | 0.072846 | 0.17171 | -0.2206 | -0.0050332 | 0.014277 | 0.01684 | 0.041448 | 0.0015811 | -13.2671 | -37.7446 | -7.8052 | -3.1527 | -3.0675 | -3.0493 | -120.8001 | 0.10636 | 0.078197 | 0.016908 | 0.061616 | 0.10528 | -0.13876 | -0.067994 | -0.014618 | -3.4503 | 107.5184 | 112.9803 | 112.9949 | -3.3651 | -3.3469 | 120.7175 | -0.23593 | 120.8919 | 120.8024 | 0.084902 | -0.19227 | -0.43631 | 117.6328 | 117.718 | 117.7362 | 83.0409 | -121.0977 | 120.8471 | 120.8908 | 120.6468 | 120.8637 | -0.36554
2602.6406 | 121.1792 | -120.8221 | 0.32501 | 1.4211e-13 | -0.087779 | -0.00023069 | 0.056526 | 0.072846 | 0.17171 | -0.22823 | -0.0050332 | 0.014704 | 0.016626 | 0.041235 | 0.0015811 | -13.2305 | -37.7721 | -7.7823 | -3.1711 | -3.0858 | -3.0631 | -120.8139 | 0.11094 | 0.087354 | 0.016908 | 0.057037 | 0.1007 | -0.13419 | -0.067994 | 0.008268 | -3.4961 | 107.5917 | 113.0398 | 113.0315 | -3.4108 | -3.3881 | 120.7541 | -0.26798 | 120.9331 | 120.8391 | 0.084902 | -0.22431 | -0.4592 | 117.6511 | 117.7363 | 117.7591 | 83.0501 | -121.1389 | 120.8792 | 120.9228 | 120.688 | 120.9095 | -0.39301
2604.3906 | 120.9869 | -119.5221 | 1.3916 | 1.4211e-13 | -0.087565 | -0.00023069 | 0.056953 | 0.072419 | 0.17171 | -0.23586 | -0.0048196 | 0.014063 | 0.016626 | 0.041448 | 0.0015811 | -13.2488 | -37.7446 | -7.7411 | -3.2306 | -3.1454 | -3.1272 | -120.8459 | 0.11094 | 0.082776 | 0.026066 | 0.066194 | 0.10528 | -0.12961 | -0.08173 | -1.3238 | -4.6222 | 106.2733 | 111.781 | 113.1048 | -4.537 | -4.5188 | 119.4404 | -1.3254 | 119.633 | 119.5482 | 0.1078 | -1.2863 | -1.5212 | 116.2915 | 116.3767 | 116.3949 | 81.7775 | -122.2375 | 119.5883 | 119.6274 | 119.3925 | 119.6049 | -1.4733
2606.1406 | 118.2587 | -86.2015 | 31.6498 | 1.4211e-13 | -0.071113 | -0.0010855 | 0.039858 | 0.051266 | 0.1245 | -0.22823 | -0.0050332 | 0.014277 | 0.016626 | 0.041876 | 0.0015811 | -10.1447 | -28.7293 | -6.0746 | -2.5347 | -2.4494 | -2.4358 | -91.2065 | 0.092622 | 0.059882 | -0.001407 | 0.038723 | 0.073228 | -0.13419 | -0.086309 | -5.0051 | -34.1844 | 76.0568 | 80.1268 | 85.1319 | -34.0991 | -34.0856 | 86.1152 | -31.6111 | 86.2941 | 86.2001 | 0.084902 | -31.5766 | -31.784 | 83.6668 | 83.7521 | 83.7657 | 57.4722 | -122.8563 | 86.2402 | 86.2747 | 86.0673 | 86.2614 | -31.7361
2607.8906 | 121.0556 | -120.5338 | 0.27924 | 1.4211e-13 | -0.087138 | -0.00044449 | 0.056312 | 0.071992 | 0.17193 | -0.23586 | -0.005247 | 0.014277 | 0.016412 | 0.041235 | 0.0011537 | -13.2076 | -37.7354 | -7.7732 | -3.2077 | -3.1225 | -3.1088 | -120.6719 | 0.10636 | 0.082776 | 0.016908 | 0.057037 | 0.091543 | -0.12961 | -0.072572 | -0.13818 | -3.4869 | 107.3262 | 112.7606 | 112.8988 | -3.4017 | -3.3881 | 120.4612 | -0.2222 | 120.6401 | 120.5507 | 0.08948 | -0.18769 | -0.40884 | 117.3261 | 117.4113 | 117.4249 | 82.7983 | -120.9512 | 120.5908 | 120.6253 | 120.4041 | 120.6165 | -0.35181
2609.6406 | 121.0785 | -120.6528 | 0.31128 | 1.4211e-13 | -0.087352 | -0.00023069 | 0.056526 | 0.071778 | 0.17236 | -0.22823 | -0.0050332 | 0.01449 | 0.016199 | 0.041662 | 0.0015811 | -13.1481 | -37.7766 | -7.7503 | -3.2168 | -3.1362 | -3.118 | -120.7498 | 0.10178 | 0.087354 | 0.01233 | 0.066194 | 0.096121 | -0.12961 | -0.067994 | -0.097 | -3.5281 | 107.5047 | 112.9025 | 112.9995 | -3.4475 | -3.4293 | 120.5848 | -0.24508 | 120.7545 | 120.6651 | 0.080324 | -0.21516 | -0.44089 | 117.4359 | 117.5166 | 117.5348 | 82.8761 | -121.061 | 120.719 | 120.7489 | 120.5232 | 120.7401 | -0.37927
2611.3906 | 120.845 | -120.3323 | 0.39825 | 1.4211e-13 | -0.087352 | -0.00023069 | 0.056312 | 0.071992 | 0.17193 | -0.24349 | -0.0050332 | 0.014704 | 0.016626 | 0.041448 | 0.0015811 | -13.1115 | -37.6301 | -7.7228 | -3.2397 | -3.1545 | -3.1363 | -120.4292 | 0.10636 | 0.087354 | 0.016908 | 0.061616 | 0.086964 | -0.12503 | -0.049678 | -0.096911 | -3.638 | 107.2209 | 112.6095 | 112.7064 | -3.5528 | -3.5346 | 120.2827 | -0.33664 | 120.4387 | 120.3492 | 0.066586 | -0.31129 | -0.52328 | 117.0926 | 117.1778 | 117.196 | 82.7022 | -120.8275 | 120.394 | 120.4193 | 120.2073 | 120.4197 | -0.44793
2613.0781 | 121.0785 | -120.5154 | 0.31128 | 1.4211e-13 | -0.087779 | -1.7092e-05 | 0.056098 | 0.071778 | 0.17236 | -0.22823 | -0.005247 | 0.01449 | 0.016626 | 0.041662 | 0.0017947 | -13.029 | -37.653 | -7.6816 | -3.2352 | -3.1408 | -3.1363 | -120.617 | 0.11094 | 0.082776 | 0.030644 | 0.066194 | 0.1007 | -0.12961 | -0.067994 | -0.10154 | -3.5464 | 107.4864 | 112.8338 | 112.9354 | -3.4521 | -3.4476 | 120.4474 | -0.24508 | 120.6264 | 120.5461 | 0.098638 | -0.21058 | -0.44089 | 117.2803 | 117.3747 | 117.3791 | 82.8624 | -120.9283 | 120.5816 | 120.6161 | 120.3858 | 120.5982 | -0.37927
2614.8281 | 120.9869 | -120.6253 | 0.33875 | 1.4211e-13 | -0.087565 | -0.00065809 | 0.056312 | 0.071992 | 0.17278 | -0.24349 | -0.005247 | 0.014704 | 0.01684 | 0.041662 | 0.0015811 | -12.9833 | -37.5843 | -7.6312 | -3.2535 | -3.1728 | -3.15 | -120.6124 | 0.11094 | 0.082776 | 0.021487 | 0.061616 | 0.1007 | -0.13419 | -0.077151 | 0.012901 | -3.5922 | 107.642 | 112.9941 | 112.9812 | -3.5116 | -3.4888 | 120.5482 | -0.27713 | 120.7362 | 120.6468 | 0.098638 | -0.23805 | -0.47293 | 117.3718 | 117.4525 | 117.4753 | 83.041 | -120.9511 | 120.6869 | 120.726 | 120.4911 | 120.7081 | -0.4159
2616.5 | 121.1517 | -120.5933 | 0.28381 | 1.4211e-13 | -0.087993 | -0.00023069 | 0.056312 | 0.071778 | 0.173 | -0.23586 | -0.0048196 | 0.01449 | 0.016412 | 0.041448 | 0.0015811 | -12.9375 | -37.4287 | -7.5992 | -3.2352 | -3.1545 | -3.1272 | -120.6445 | 0.097201 | 0.082776 | 0.01233 | 0.066194 | 0.1007 | -0.13419 | -0.067994 | -0.051194 | -3.519 | 107.6558 | 112.9941 | 113.0453 | -3.4383 | -3.411 | 120.5253 | -0.21762 | 120.6905 | 120.6056 | 0.080324 | -0.18311 | -0.418 | 117.3581 | 117.4387 | 117.4661 | 83.1646 | -120.9283 | 120.6595 | 120.694 | 120.4591 | 120.676 | -0.35181
2618.25 | 121.1105 | -120.6802 | 0.33417 | 1.4211e-13 | -0.087565 | -0.00065809 | 0.056098 | 0.071778 | 0.17342 | -0.23586 | -0.0050332 | 0.01449 | 0.016199 | 0.041876 | 0.0017947 | -12.9192 | -37.447 | -7.5397 | -3.3267 | -3.2369 | -3.2187 | -120.6765 | 0.11552 | 0.087354 | 0.021487 | 0.066194 | 0.096121 | -0.12503 | -0.072572 | 0.003728 | -3.6609 | 107.7611 | 113.1406 | 113.1368 | -3.5711 | -3.5529 | 120.6077 | -0.26797 | 120.7958 | 120.7017 | 0.094059 | -0.23805 | -0.4592 | 117.3535 | 117.4433 | 117.4615 | 83.2333 | -121.0107 | 120.7464 | 120.7764 | 120.5552 | 120.7676 | -0.40674
2619.9531 | 121.1975 | -120.6482 | 0.33417 | 1.4211e-13 | -0.087779 | -0.00023069 | 0.056526 | 0.072205 | 0.17385 | -0.22823 | -0.0050332 | 0.01449 | 0.016412 | 0.041448 | 0.0013673 | -12.9146 | -37.4195 | -7.4893 | -3.2626 | -3.1774 | -3.1638 | -120.6857 | 0.11094 | 0.078197 | 0.021487 | 0.061616 | 0.1007 | -0.13419 | -0.072572 | -0.037473 | -3.5968 | 107.7336 | 113.1589 | 113.1963 | -3.5116 | -3.498 | 120.5756 | -0.27255 | 120.7591 | 120.6697 | 0.094059 | -0.23347 | -0.46835 | 117.3856 | 117.4708 | 117.4844 | 83.2287 | -121.0198 | 120.7098 | 120.7489 | 120.514 | 120.7264 | -0.40674
2621.7031 | 121.0327 | -118.7393 | 2.4261 | 1.4211e-13 | -0.087565 | -0.00044449 | 0.056526 | 0.071778 | 0.17278 | -0.24349 | -0.0048196 | 0.014063 | 0.016199 | 0.041876 | 0.0017947 | -12.8688 | -37.1906 | -7.4023 | -3.3771 | -3.2919 | -3.2737 | -120.1408 | 0.11094 | 0.082776 | 0.016908 | 0.057037 | 0.096121 | -0.13419 | -0.072572 | -1.4015 | -5.8032 | 105.8705 | 111.337 | 112.7384 | -5.718 | -5.6998 | 118.6667 | -2.3691 | 118.8503 | 118.7562 | 0.08948 | -2.33 | -2.5603 | 115.3622 | 115.4474 | 115.4656 | 81.5487 | -122.5669 | 118.7964 | 118.8354 | 118.6051 | 118.8221 | -2.4987
2623.4531 | 121.0373 | -120.3415 | 0.48065 | 1.4211e-13 | -0.087352 | -1.7092e-05 | 0.055885 | 0.071778 | 0.17364 | -0.23586 | -0.0050332 | 0.014277 | 0.016412 | 0.041662 | 0.0013673 | -12.8871 | -37.2501 | -7.3749 | -3.487 | -3.3972 | -3.3744 | -120.475 | 0.10178 | 0.082776 | 0.016908 | 0.066194 | 0.10528 | -0.13419 | -0.077151 | -0.13354 | -3.9676 | 107.4544 | 112.9666 | 113.1002 | -3.8779 | -3.8551 | 120.2643 | -0.41446 | 120.4433 | 120.3584 | 0.094059 | -0.37537 | -0.61484 | 116.8545 | 116.9443 | 116.9671 | 83.0914 | -120.9557 | 120.4077 | 120.4468 | 120.2073 | 120.4243 | -0.5578
2625.125 | 121.0556 | -120.2866 | 0.60425 | 1.4211e-13 | -0.087779 | -0.00044449 | 0.056312 | 0.071564 | 0.17385 | -0.24349 | -0.0048196 | 0.014704 | 0.016412 | 0.041876 | 0.0011537 | -12.8505 | -37.1997 | -7.3199 | -3.5236 | -3.4384 | -3.4293 | -120.3239 | 0.11552 | 0.087354 | 0.021487 | 0.066194 | 0.096121 | -0.12961 | -0.067994 | -0.037371 | -4.1278 | 107.4361 | 112.9666 | 113.004 | -4.0427 | -4.0336 | 120.2186 | -0.53805 | 120.4021 | 120.308 | 0.089481 | -0.50813 | -0.73386 | 116.763 | 116.8481 | 116.8572 | 83.0868 | -120.9282 | 120.3528 | 120.3827 | 120.157 | 120.3739 | -0.67224
2626.875 | 120.9915 | -119.9753 | 0.88348 | 1.4211e-13 | -0.087352 | -0.00065809 | 0.055671 | 0.071351 | 0.17342 | -0.23586 | -0.0050332 | 0.014277 | 0.016199 | 0.041662 | 0.0013673 | -12.8047 | -37.0166 | -7.2375 | -3.519 | -3.4338 | -3.4156 | -120.0538 | 0.11094 | 0.087354 | 0.01233 | 0.066194 | 0.10986 | -0.12961 | -0.077151 | -0.078494 | -4.4025 | 107.1706 | 112.7378 | 112.8163 | -4.3173 | -4.2991 | 119.8981 | -0.81729 | 120.0862 | 119.9876 | 0.089481 | -0.77363 | -1.0131 | 116.4563 | 116.5414 | 116.5597 | 82.9587 | -120.9373 | 120.0415 | 120.0851 | 119.8457 | 120.0626 | -0.96064
2628.6406 | 120.7031 | -119.5358 | 1.0345 | 1.4211e-13 | -0.087352 | -0.00044449 | 0.055244 | 0.071137 | 0.173 | -0.24349 | -0.004606 | 0.014277 | 0.016626 | 0.041448 | 0.0013673 | -12.8276 | -36.8609 | -7.2329 | -3.5556 | -3.4796 | -3.4522 | -119.6737 | 0.11094 | 0.082776 | 0.026066 | 0.057037 | 0.10528 | -0.13419 | -0.063415 | -0.1379 | -4.5902 | 106.7082 | 112.3029 | 112.4408 | -4.5142 | -4.4868 | 119.4724 | -0.97751 | 119.6468 | 119.5619 | 0.089481 | -0.92927 | -1.1687 | 115.9802 | 116.0562 | 116.0836 | 82.6749 | -120.7083 | 119.5929 | 119.6411 | 119.4016 | 119.6186 | -1.098
2630.3281 | 120.7901 | -119.0781 | 1.4465 | 1.4211e-13 | -0.086711 | -0.00087189 | 0.054816 | 0.070496 | 0.17278 | -0.23586 | -0.0054606 | 0.013849 | 0.015985 | 0.041876 | 0.0015811 | -12.7269 | -36.7007 | -7.1963 | -3.6747 | -3.5712 | -3.5575 | -119.2204 | 0.12009 | 0.087354 | 0.035223 | 0.075351 | 0.10986 | -0.12503 | -0.058836 | -0.14235 | -5.1212 | 106.3512 | 111.8818 | 112.0241 | -5.0177 | -5.0041 | 119.0192 | -1.3712 | 119.1982 | 119.1133 | 0.094059 | -1.3367 | -1.5716 | 115.4034 | 115.5069 | 115.5205 | 82.3774 | -120.6669 | 119.1534 | 119.1879 | 118.953 | 119.1654 | -1.5054
2632.0781 | 120.6619 | -118.5562 | 1.9409 | 1.4211e-13 | -0.086283 | -0.00044449 | 0.054602 | 0.070282 | 0.17214 | -0.22823 | -0.0048196 | 0.01449 | 0.016412 | 0.042089 | 0.0013673 | -12.6628 | -36.4809 | -7.1322 | -3.6701 | -3.5895 | -3.5667 | -118.5336 | 0.12467 | 0.091933 | 0.030644 | 0.075351 | 0.11444 | -0.12961 | -0.054257 | 0.022641 | -5.611 | 105.8934 | 111.424 | 111.4014 | -5.5304 | -5.5076 | 118.502 | -1.8656 | 118.6809 | 118.5869 | 0.084901 | -1.8265 | -2.0705 | 114.8861 | 114.9667 | 114.9895 | 82.0753 | -120.4745 | 118.6316 | 118.6706 | 118.4266 | 118.6481 | -1.9952
2633.8281 | 120.7031 | -116.8671 | 3.3096 | 1.4211e-13 | -0.085642 | -0.00044449 | 0.054175 | 0.069 | 0.17043 | -0.22823 | -0.0050332 | 0.01449 | 0.016199 | 0.041662 | 0.0015811 | -12.5666 | -36.078 | -7.0361 | -3.5236 | -3.4293 | -3.411 | -117.3247 | 0.13383 | 0.10567 | 0.044381 | 0.07993 | 0.11444 | -0.12045 | -0.049678 | -0.45767 | -6.8332 | 104.3004 | 109.831 | 110.2887 | -6.7389 | -6.7207 | 116.8174 | -3.2297 | 117.0009 | 116.9114 | 0.094059 | -3.1952 | -3.4301 | 113.3435 | 113.4378 | 113.456 | 80.7891 | -120.6344 | 116.947 | 116.9815 | 116.7466 | 116.9727 | -3.3593
2635.5625 | 120.3827 | -116.7252 | 3.4195 | 1.4211e-13 | -0.085215 | -0.00065809 | 0.05332 | 0.068359 | 0.16915 | -0.2206 | -0.0050332 | 0.01449 | 0.015771 | 0.041876 | 0.0013673 | -12.4613 | -35.73 | -7.0498 | -3.5007 | -3.4201 | -3.3973 | -116.2029 | 0.14299 | 0.11483 | 0.044381 | 0.098244 | 0.12817 | -0.11587 | -0.035942 | 0.52226 | -6.9202 | 104.2638 | 109.6754 | 109.1531 | -6.8396 | -6.8168 | 116.6892 | -3.3213 | 116.8681 | 116.7695 | 0.080323 | -3.2913 | -3.5354 | 113.2245 | 113.3051 | 113.3279 | 80.9952 | -119.6224 | 116.8234 | 116.8533 | 116.6093 | 116.84 | -3.4554
2637.2344 | 119.7739 | -110.4584 | 9.0271 | 1.4211e-13 | -0.082437 | -0.00065809 | 0.05097 | 0.064941 | 0.16231 | -0.23586 | -0.0048196 | 0.01449 | 0.016412 | 0.041876 | 0.0015811 | -12.1775 | -34.329 | -6.7522 | -3.4503 | -3.3652 | -3.3424 | -111.7476 | 0.1842 | 0.15146 | 0.085589 | 0.13945 | 0.16938 | 0.067272 | 0.000689 | -1.2892 | -12.4774 | 98.2809 | 103.7062 | 104.9954 | -12.3923 | -12.3695 | 110.4591 | -8.8877 | 110.6426 | 110.544 | 0.0849 | -8.8577 | -8.9598 | 107.008 | 107.0932 | 107.116 | 76.1294 | -120.7747 | 110.5978 | 110.6278 | 110.5256 | 110.6098 | -9.0264
2638.9219 | 120.8267 | -120.314 | 0.23804 | 1.4211e-13 | -0.087993 | -0.00044449 | 0.055885 | 0.071564 | 0.17663 | -0.23586 | -0.0050332 | 0.014277 | 0.016626 | 0.041662 | 0.0013673 | -12.8459 | -36.8106 | -7.091 | -3.5328 | -3.443 | -3.4293 | -120.3972 | 0.097201 | 0.078197 | 0.01233 | 0.061616 | 0.091543 | -0.13419 | -0.08173 | -0.083168 | -3.7708 | 107.4681 | 113.223 | 113.3062 | -3.681 | -3.6674 | 120.2323 | -0.17642 | 120.4112 | 120.3264 | 0.09406 | -0.14649 | -0.37222 | 116.7813 | 116.871 | 116.8847 | 83.5035 | -120.6352 | 120.3756 | 120.4056 | 120.1798 | 120.3922 | -0.31977
2640.6562 | 120.9686 | -120.4468 | 0.23804 | 1.4211e-13 | -0.087565 | -0.00065809 | 0.055885 | 0.071137 | 0.17706 | -0.24349 | -0.0050332 | 0.014277 | 0.016199 | 0.042303 | 0.0011537 | -12.7955 | -36.8472 | -7.0819 | -3.6518 | -3.5666 | -3.5438 | -120.4934 | 0.10178 | 0.078197 | 0.01233 | 0.057037 | 0.096121 | -0.13419 | -0.077151 | -0.046575 | -3.8898 | 107.6512 | 113.3649 | 113.4115 | -3.8047 | -3.7818 | 120.3696 | -0.181 | 120.5486 | 120.4591 | 0.089481 | -0.14192 | -0.37222 | 116.795 | 116.8802 | 116.903 | 83.5996 | -120.7314 | 120.5038 | 120.5429 | 120.3126 | 120.525 | -0.31519
2642.4062 | 117.4393 | -90.8981 | 26.6327 | 1.4211e-13 | -0.074959 | -0.0010855 | 0.043064 | 0.055967 | 0.13902 | -0.23586 | -0.0050332 | 0.014277 | 0.016199 | 0.041876 | 0.0013673 | -10.5247 | -29.993 | -6.0151 | -3.0245 | -2.9347 | -2.9165 | -97.3744 | 0.088043 | 0.059882 | 0.003172 | 0.04788 | 0.077807 | -0.13876 | -0.095467 | -6.4762 | -29.6572 | 80.3735 | 84.883 | 91.3592 | -29.5674 | -29.5492 | 90.8027 | -26.5848 | 90.9862 | 90.9013 | 0.098639 | -26.5549 | -26.7715 | 87.8736 | 87.9634 | 87.9816 | 60.9051 | -124.0071 | 90.946 | 90.9759 | 90.7594 | 90.958 | -26.7282
2644.0938 | 120.7581 | -120.2087 | 0.22888 | 1.4211e-13 | -0.087565 | -0.00023069 | 0.055457 | 0.07071 | 0.1777 | -0.23586 | -0.005247 | 0.014277 | 0.016412 | 0.042089 | 0.0011537 | -12.7772 | -36.8518 | -7.1551 | -3.6747 | -3.5941 | -3.5713 | -120.3514 | 0.11094 | 0.073618 | 0.007751 | 0.057037 | 0.091543 | -0.12961 | -0.072572 | -0.14266 | -3.9036 | 107.4315 | 113.0536 | 113.1963 | -3.823 | -3.8002 | 120.1362 | -0.17184 | 120.3197 | 120.2165 | 0.080323 | -0.13734 | -0.35849 | 116.5341 | 116.6146 | 116.6375 | 83.357 | -120.5803 | 120.2658 | 120.3003 | 120.0791 | 120.2824 | -0.30145
2645.8281 | 120.7764 | -120.3461 | 0.27008 | 1.4211e-13 | -0.087779 | -0.00023069 | 0.055885 | 0.071137 | 0.17877 | -0.23586 | -0.005247 | 0.014277 | 0.016412 | 0.041876 | 0.0015811 | -12.7589 | -36.8106 | -7.0819 | -3.7067 | -3.617 | -3.5988 | -120.443 | 0.10636 | 0.082776 | 0.016908 | 0.04788 | 0.096121 | -0.13419 | -0.077151 | -0.096914 | -3.9768 | 107.5871 | 113.2642 | 113.3611 | -3.8871 | -3.8688 | 120.2689 | -0.2222 | 120.4524 | 120.363 | 0.094059 | -0.17396 | -0.40427 | 116.6393 | 116.7291 | 116.7473 | 83.5355 | -120.7131 | 120.3939 | 120.4422 | 120.2119 | 120.4288 | -0.34723
2647.5938 | 119.4031 | -116.8076 | 3.3508 | 1.4211e-13 | -0.087779 | -0.00044449 | 0.055885 | 0.071137 | 0.17877 | -0.23586 | -0.0054606 | 0.01449 | 0.015985 | 0.041662 | 0.0011537 | -12.8001 | -36.7739 | -7.1734 | -3.6609 | -3.5666 | -3.5484 | -120.1499 | 0.10636 | 0.078197 | 0.021487 | 0.057037 | 0.096121 | -0.13419 | -0.08173 | -3.3424 | -7.0118 | 104.0074 | 109.6341 | 112.9765 | -6.9175 | -6.8992 | 116.7258 | -3.2938 | 116.9139 | 116.829 | 0.10322 | -3.2547 | -3.485 | 113.1466 | 113.2409 | 113.2592 | 80.0336 | -123.5008 | 116.8646 | 116.9037 | 116.6734 | 116.8858 | -3.4326
2649.2812 | 116.6382 | -86.6592 | 29.7867 | 1.4211e-13 | -0.073463 | -0.0010855 | 0.040927 | 0.053189 | 0.13475 | -0.22823 | -0.0048196 | 0.014277 | 0.016199 | 0.041876 | 0.0013673 | -10.0531 | -28.9354 | -5.8503 | -2.846 | -2.7562 | -2.7334 | -93.7982 | 0.088043 | 0.059882 | -0.015143 | 0.034145 | 0.073228 | -0.13419 | -0.10004 | -7.139 | -32.6327 | 76.6061 | 80.8089 | 87.9479 | -32.5428 | -32.5201 | 86.5592 | -29.7525 | 86.7473 | 86.6441 | 0.084902 | -29.7135 | -29.9209 | 83.8132 | 83.9031 | 83.9258 | 57.7239 | -123.5849 | 86.6934 | 86.7325 | 86.5251 | 86.7191 | -29.8867
2651.0312 | 119.5953 | -119.1238 | 0.22888 | 1.4211e-13 | -0.074104 | -0.0010855 | 0.041568 | 0.051907 | 0.13667 | -0.23586 | -0.005247 | 0.01449 | 0.015771 | 0.041662 | 0.0009401 | -10.1996 | -29.1734 | -5.8457 | -2.9192 | -2.834 | -2.825 | -94.7186 | 0.088043 | 0.06904 | -0.001407 | 0.043302 | 0.073228 | -0.12961 | -0.090888 | 24.4053 | -3.1481 | 108.9242 | 113.2781 | 88.8729 | -3.0629 | -3.0539 | 119.033 | -0.18558 | 119.2119 | 119.1224 | 0.089481 | -0.15565 | -0.35849 | 116.2046 | 116.2898 | 116.2989 | 89.9504 | -94.9475 | 119.1671 | 119.1971 | 118.9942 | 119.1929 | -0.31977
2652.7969 | 120.5658 | -120.1721 | 0.24261 | 1.4211e-13 | -0.08842 | -0.00023069 | 0.055671 | 0.070923 | 0.18026 | -0.2206 | -0.0050332 | 0.01449 | 0.016412 | 0.042089 | 0.0009401 | -12.7498 | -36.719 | -7.21 | -3.487 | -3.4064 | -3.3927 | -120.2644 | 0.10178 | 0.082776 | 0.007751 | 0.057037 | 0.096121 | -0.13419 | -0.086309 | -0.092286 | -3.7296 | 107.4224 | 112.9621 | 113.0544 | -3.649 | -3.6353 | 120.0858 | -0.18558 | 120.2739 | 120.1799 | 0.09406 | -0.14649 | -0.3768 | 116.6852 | 116.7658 | 116.7794 | 83.4531 | -120.507 | 120.2292 | 120.2682 | 120.0379 | 120.2549 | -0.32892
2654.4844 | 120.7626 | -120.1447 | 0.32959 | 1.4211e-13 | -0.08842 | -0.00023069 | 0.055671 | 0.07071 | 0.18069 | -0.24349 | -0.0050332 | 0.014704 | 0.016199 | 0.042089 | 0.0013673 | -12.7086 | -36.7281 | -7.265 | -3.4687 | -3.388 | -3.3607 | -120.3056 | 0.097201 | 0.078197 | 0.016908 | 0.057037 | 0.096121 | -0.13419 | -0.08173 | -0.16096 | -3.7982 | 107.4361 | 112.8797 | 113.0406 | -3.7176 | -3.6903 | 120.0629 | -0.27255 | 120.2419 | 120.1616 | 0.098638 | -0.23347 | -0.46378 | 116.676 | 116.7566 | 116.784 | 83.4165 | -120.6352 | 120.2017 | 120.2408 | 120.0105 | 120.2229 | -0.41132
2656.2344 | 120.6528 | -120.2682 | 0.24719 | 1.4211e-13 | -0.088206 | -0.00023069 | 0.056098 | 0.07071 | 0.18154 | -0.22823 | -0.005247 | 0.01449 | 0.016199 | 0.042089 | 0.0013673 | -12.7131 | -36.6915 | -7.3108 | -3.4595 | -3.3743 | -3.3469 | -120.356 | 0.10636 | 0.073618 | 0.007751 | 0.057037 | 0.091543 | -0.12961 | -0.08173 | -0.087734 | -3.7067 | 107.5551 | 112.9575 | 113.0452 | -3.6215 | -3.5941 | 120.1865 | -0.19015 | 120.3746 | 120.276 | 0.089481 | -0.15565 | -0.3768 | 116.8088 | 116.8939 | 116.9213 | 83.5767 | -120.6032 | 120.3253 | 120.3598 | 120.1386 | 120.3419 | -0.32892
2657.9688 | 120.726 | -120.3552 | 0.25635 | 1.4211e-13 | -0.088634 | -1.7092e-05 | 0.056526 | 0.070496 | 0.18261 | -0.24349 | -0.0050332 | 0.01449 | 0.015985 | 0.042089 | 0.0013673 | -12.7131 | -36.6732 | -7.3245 | -3.4595 | -3.3743 | -3.3515 | -120.3606 | 0.097201 | 0.082776 | 0.016908 | 0.061616 | 0.1007 | -0.13419 | -0.077151 | -0.005338 | -3.7158 | 107.6421 | 113.0307 | 113.0361 | -3.6307 | -3.6079 | 120.2781 | -0.19473 | 120.4524 | 120.3721 | 0.094059 | -0.15565 | -0.39053 | 116.8957 | 116.9809 | 117.0037 | 83.682 | -120.6169 | 120.4168 | 120.4559 | 120.221 | 120.438 | -0.3335
2659.7031 | 120.639 | -120.1355 | 0.21515 | 1.4211e-13 | -0.088634 | -0.00023069 | 0.055885 | 0.070496 | 0.18261 | -0.25875 | -0.005247 | 0.014277 | 0.015985 | 0.042303 | 0.0009401 | -12.6811 | -36.6045 | -7.3016 | -3.4595 | -3.3697 | -3.3561 | -120.2324 | 0.10178 | 0.073618 | 0.016908 | 0.057037 | 0.10528 | -0.13419 | -0.077151 | -0.096855 | -3.6746 | 107.4544 | 112.8339 | 112.9307 | -3.5849 | -3.5712 | 120.0583 | -0.15811 | 120.2373 | 120.1524 | 0.094059 | -0.10987 | -0.34934 | 116.676 | 116.7658 | 116.7794 | 83.531 | -120.4475 | 120.1925 | 120.2408 | 120.0013 | 120.2091 | -0.2923
2661.3906 | 120.7077 | -120.314 | 0.24261 | 1.4211e-13 | -0.089061 | 0.00019651 | 0.056098 | 0.070496 | 0.18347 | -0.22823 | -0.0050332 | 0.014918 | 0.016199 | 0.041876 | 0.0013673 | -12.6811 | -36.5999 | -7.265 | -3.3725 | -3.2827 | -3.2599 | -120.388 | 0.11094 | 0.073618 | 0.016908 | 0.057037 | 0.1007 | -0.13419 | -0.077151 | -0.07401 | -3.6151 | 107.6329 | 113.049 | 113.1231 | -3.5253 | -3.5026 | 120.2369 | -0.18558 | 120.425 | 120.3309 | 0.094059 | -0.14192 | -0.3768 | 116.9415 | 117.0313 | 117.0541 | 83.7141 | -120.6307 | 120.3711 | 120.4147 | 120.1798 | 120.3876 | -0.31977
2663.1406 | 120.694 | -120.3873 | 0.24719 | 1.4211e-13 | -0.089275 | -1.7092e-05 | 0.055885 | 0.070282 | 0.18453 | -0.23586 | -0.0048196 | 0.014704 | 0.015985 | 0.041662 | 0.0013673 | -12.6674 | -36.6045 | -7.2879 | -3.3908 | -3.3056 | -3.2828 | -120.3789 | 0.11094 | 0.078197 | 0.021487 | 0.057037 | 0.10528 | -0.12961 | -0.077151 | 0.008389 | -3.638 | 107.7199 | 113.0994 | 113.091 | -3.5528 | -3.53 | 120.3101 | -0.19015 | 120.4982 | 120.4088 | 0.098638 | -0.14191 | -0.3768 | 116.9964 | 117.0816 | 117.1044 | 83.7827 | -120.6261 | 120.4443 | 120.4925 | 120.2577 | 120.4655 | -0.32434
2664.8281 | 120.8679 | -120.3598 | 0.21515 | 1.4211e-13 | -0.089061 | -0.00044449 | 0.055671 | 0.070496 | 0.18496 | -0.24349 | -0.0048196 | 0.014277 | 0.016199 | 0.041876 | 0.0011537 | -12.649 | -36.6183 | -7.3749 | -3.4183 | -3.3194 | -3.3011 | -120.4109 | 0.10636 | 0.078197 | 0.016908 | 0.052459 | 0.096121 | -0.13419 | -0.08173 | -0.051129 | -3.6334 | 107.7108 | 112.9849 | 113.0361 | -3.5345 | -3.5163 | 120.2781 | -0.16269 | 120.4662 | 120.3767 | 0.098638 | -0.11903 | -0.34934 | 116.9415 | 117.0404 | 117.0587 | 83.7415 | -120.6261 | 120.4123 | 120.4559 | 120.2256 | 120.438 | -0.29688
2666.5625 | 120.5338 | -120.1813 | 0.24261 | 1.4211e-13 | -0.088634 | 0.00019651 | 0.056098 | 0.070069 | 0.18539 | -0.23586 | -0.0050332 | 0.014277 | 0.016626 | 0.042089 | 0.0007265 | -12.6582 | -36.5313 | -7.4069 | -3.4366 | -3.3468 | -3.3378 | -120.2415 | 0.097201 | 0.078197 | 0.01233 | 0.052459 | 0.1007 | -0.13876 | -0.08173 | -0.060237 | -3.6792 | 107.5231 | 112.7744 | 112.8346 | -3.5894 | -3.5804 | 120.0995 | -0.19016 | 120.2785 | 120.1936 | 0.09406 | -0.14192 | -0.38138 | 116.7447 | 116.8344 | 116.8435 | 83.65 | -120.4841 | 120.2337 | 120.282 | 120.0425 | 120.2595 | -0.32434
2668.25 | 120.6985 | -120.3186 | 0.2655 | 1.4211e-13 | -0.089061 | -1.7092e-05 | 0.056526 | 0.070282 | 0.18646 | -0.23586 | -0.0050332 | 0.014704 | 0.016199 | 0.042303 | 0.0013673 | -12.6124 | -36.5587 | -7.3108 | -3.3634 | -3.2782 | -3.2508 | -120.388 | 0.10178 | 0.078197 | 0.01233 | 0.057037 | 0.096121 | -0.12961 | -0.067994 | -0.069432 | -3.6289 | 107.7062 | 113.0078 | 113.0773 | -3.5437 | -3.5163 | 120.2506 | -0.20847 | 120.4204 | 120.3309 | 0.080324 | -0.16938 | -0.39511 | 116.9553 | 117.0405 | 117.0678 | 83.7599 | -120.6535 | 120.3756 | 120.4147 | 120.189 | 120.3968 | -0.3335
2669.9844 | 120.7397 | -120.4102 | 0.2655 | 1.4211e-13 | -0.089275 | 0.00019651 | 0.056098 | 0.070282 | 0.18731 | -0.23586 | -0.0050332 | 0.014277 | 0.016199 | 0.042089 | 0.0015811 | -12.6033 | -36.5496 | -7.2284 | -3.2214 | -3.1408 | -3.118 | -120.3926 | 0.10636 | 0.082776 | 0.003172 | 0.057037 | 0.096121 | -0.13876 | -0.077151 | 0.017541 | -3.4869 | 107.8069 | 113.1818 | 113.1643 | -3.4063 | -3.3835 | 120.333 | -0.20847 | 120.5165 | 120.4133 | 0.080323 | -0.16938 | -0.40427 | 117.1887 | 117.2694 | 117.2922 | 83.8606 | -120.6581 | 120.4672 | 120.5063 | 120.2714 | 120.4929 | -0.34265
2671.7344 | 120.6253 | -120.4193 | 0.25635 | 1.4211e-13 | -0.089916 | 0.00019651 | 0.056312 | 0.070496 | 0.18817 | -0.2206 | -0.005247 | 0.01449 | 0.015985 | 0.042517 | 0.0011537 | -12.5987 | -36.6137 | -7.2192 | -3.1985 | -3.1133 | -3.0905 | -120.4384 | 0.10636 | 0.06904 | 0.01233 | 0.04788 | 0.1007 | -0.13419 | -0.072572 | -0.019093 | -3.4549 | 107.8206 | 113.2001 | 113.2192 | -3.3697 | -3.3469 | 120.3467 | -0.20847 | 120.5257 | 120.4316 | 0.084902 | -0.15565 | -0.39053 | 117.2208 | 117.306 | 117.3288 | 83.8056 | -120.6948 | 120.4672 | 120.52 | 120.2851 | 120.4884 | -0.32892
2673.4844 | 120.9045 | -120.4651 | 0.21973 | 1.4211e-13 | -0.089702 | 0.00019651 | 0.056526 | 0.070282 | 0.18945 | -0.23586 | -0.0050332 | 0.014277 | 0.016199 | 0.042517 | 0.0011537 | -12.6261 | -36.6549 | -7.2238 | -3.1115 | -3.0309 | -3.0081 | -120.4613 | 0.10178 | 0.082776 | 0.01233 | 0.061616 | 0.1007 | -0.13419 | -0.08173 | 0.003789 | -3.3313 | 107.8389 | 113.2413 | 113.2375 | -3.2506 | -3.2278 | 120.3834 | -0.15811 | 120.5669 | 120.4774 | 0.09406 | -0.11903 | -0.35391 | 117.3535 | 117.4342 | 117.457 | 83.8102 | -120.681 | 120.5267 | 120.5658 | 120.3309 | 120.5479 | -0.30146
2675.1562 | 120.369 | -120.4056 | 0.25177 | 1.4211e-13 | -0.089702 | 0.00019651 | 0.056312 | 0.070069 | 0.18988 | -0.23586 | -0.0048196 | 0.01449 | 0.016412 | 0.042089 | 0.0011537 | -12.649 | -36.806 | -7.4069 | -3.1711 | -3.0904 | -3.0631 | -120.4888 | 0.097201 | 0.073618 | 0.016908 | 0.052459 | 0.1007 | -0.13419 | -0.072572 | -0.083194 | -3.4228 | 107.7565 | 112.9987 | 113.0819 | -3.3422 | -3.3148 | 120.333 | -0.19931 | 120.5028 | 120.4225 | 0.08948 | -0.15107 | -0.38596 | 117.2345 | 117.3152 | 117.3425 | 83.5996 | -120.7405 | 120.458 | 120.5063 | 120.2714 | 120.4792 | -0.32434
2676.9062 | 119.783 | -119.2978 | 0.20142 | 1.4211e-13 | -0.081583 | -0.00023069 | 0.048406 | 0.058531 | 0.16552 | -0.22823 | -0.005247 | 0.01449 | 0.016412 | 0.041876 | 0.0013673 | -11.4999 | -32.4563 | -6.7751 | -2.8277 | -2.747 | -2.7242 | -105.5065 | 0.088043 | 0.078197 | 0.003172 | 0.04788 | 0.091543 | -0.13419 | -0.08173 | 13.7913 | -3.0291 | 107.7979 | 112.5227 | 98.7314 | -2.9484 | -2.9257 | 119.2161 | -0.15354 | 119.3858 | 119.301 | 0.084902 | -0.10987 | -0.3356 | 116.4701 | 116.5508 | 116.5736 | 86.8415 | -105.7079 | 119.3457 | 119.3893 | 119.1636 | 119.376 | -0.28315
2678.6562 | 120.1813 | -119.7693 | 0.091553 | 1.4211e-13 | -0.089488 | 0.00019651 | 0.055457 | 0.069 | 0.18945 | -0.22823 | -0.0050332 | 0.014277 | 0.015985 | 0.04273 | 0.0013673 | -12.8047 | -36.6366 | -7.5031 | -3.1756 | -3.0996 | -3.0722 | -119.4814 | 0.11094 | 0.078197 | 0.01233 | 0.052459 | 0.1007 | -0.13419 | -0.08173 | 0.28788 | -3.2672 | 106.9646 | 112.2662 | 111.9784 | -3.1911 | -3.1638 | 119.6876 | -0.039094 | 119.8802 | 119.7816 | 0.09406 | 0.009147 | -0.22574 | 116.5937 | 116.6697 | 116.6971 | 83.1327 | -119.573 | 119.8217 | 119.87 | 119.6351 | 119.8475 | -0.17328
2680.3438 | 120.5658 | -120.0714 | 0.21515 | 1.4211e-13 | -0.089916 | -1.7092e-05 | 0.056312 | 0.069855 | 0.19159 | -0.22823 | -0.0050332 | 0.014277 | 0.015771 | 0.042517 | 0.0011537 | -12.7543 | -36.8747 | -7.5809 | -3.1711 | -3.0858 | -3.0585 | -120.1637 | 0.097201 | 0.078197 | 0.01233 | 0.052459 | 0.1007 | -0.13419 | -0.072572 | -0.092258 | -3.3862 | 107.3171 | 112.4905 | 112.5828 | -3.301 | -3.2736 | 119.9988 | -0.16269 | 120.1686 | 120.0837 | 0.084902 | -0.11445 | -0.34934 | 116.9004 | 116.9856 | 117.0129 | 83.1968 | -120.3788 | 120.1239 | 120.1721 | 119.9372 | 120.1496 | -0.28772
2682.0312 | 120.5841 | -120.1767 | 0.22888 | 1.4211e-13 | -0.089916 | 0.00041031 | 0.055885 | 0.069428 | 0.19244 | -0.22823 | -0.0048196 | 0.014063 | 0.016412 | 0.042517 | 0.0011537 | -12.7864 | -36.9342 | -7.6633 | -3.2306 | -3.1499 | -3.1317 | -120.2644 | 0.10636 | 0.082776 | 0.021487 | 0.057037 | 0.091543 | -0.13419 | -0.08173 | -0.087708 | -3.4595 | 107.3903 | 112.5134 | 112.6011 | -3.3788 | -3.3606 | 120.095 | -0.17184 | 120.2831 | 120.1982 | 0.10322 | -0.13734 | -0.36307 | 116.9461 | 117.0268 | 117.045 | 83.2425 | -120.4933 | 120.2337 | 120.2682 | 120.0425 | 120.2595 | -0.31061
2683.7812 | 120.6665 | -120.195 | 0.23804 | 1.4211e-13 | -0.090343 | 0.00062391 | 0.056098 | 0.069641 | 0.19372 | -0.22823 | -0.005247 | 0.014277 | 0.015985 | 0.042303 | 0.0013673 | -12.7772 | -36.9708 | -7.6725 | -3.2397 | -3.1637 | -3.1409 | -120.2507 | 0.097201 | 0.078197 | 0.007751 | 0.052459 | 0.1007 | -0.13876 | -0.08173 | -0.055662 | -3.4778 | 107.4178 | 112.5226 | 112.5782 | -3.4017 | -3.3789 | 120.1133 | -0.18558 | 120.2922 | 120.2028 | 0.089481 | -0.13734 | -0.3768 | 116.9553 | 117.0313 | 117.0541 | 83.2242 | -120.4887 | 120.2475 | 120.2957 | 120.0562 | 120.2732 | -0.31977
2685.5312 | 120.4376 | -119.9524 | 0.25635 | 1.4211e-13 | -0.090557 | 0.00019651 | 0.056526 | 0.069641 | 0.195 | -0.22823 | -0.0050332 | 0.01449 | 0.015771 | 0.042303 | 0.0009401 | -12.7727 | -36.9525 | -7.5351 | -3.226 | -3.1454 | -3.1134 | -120.301 | 0.10178 | 0.073618 | 0.021487 | 0.057037 | 0.10528 | -0.13876 | -0.077151 | -0.34864 | -3.4823 | 107.1797 | 112.4173 | 112.7659 | -3.4017 | -3.3698 | 119.8752 | -0.19931 | 120.0542 | 119.9739 | 0.098638 | -0.15107 | -0.39511 | 116.7264 | 116.807 | 116.839 | 82.9999 | -120.5574 | 120.0094 | 120.0577 | 119.8136 | 120.026 | -0.3335
2687.2031 | 120.1813 | -119.9615 | 0.2655 | 1.4211e-13 | -0.090984 | 0.0010513 | 0.056953 | 0.069855 | 0.19607 | -0.23586 | -0.005247 | 0.01449 | 0.016199 | 0.042089 | 0.0011537 | -12.7955 | -36.9296 | -7.4756 | -2.9513 | -2.8615 | -2.8387 | -120.3377 | 0.097201 | 0.073618 | 0.01233 | 0.057037 | 0.10528 | -0.13876 | -0.072572 | -0.37612 | -3.2168 | 107.166 | 112.486 | 112.8621 | -3.127 | -3.1042 | 119.889 | -0.20847 | 120.0587 | 119.9739 | 0.084902 | -0.16022 | -0.40427 | 117.0103 | 117.1001 | 117.1228 | 83.0319 | -120.6032 | 120.0186 | 120.0668 | 119.8228 | 120.0352 | -0.33808
2688.9531 | 120.3827 | -120.3094 | 0.26093 | 1.4211e-13 | -0.091198 | 0.00083771 | 0.056312 | 0.069641 | 0.19757 | -0.23586 | -0.0050332 | 0.014277 | 0.016199 | 0.042303 | 0.0009401 | -12.8093 | -37.0578 | -7.5122 | -2.9147 | -2.8157 | -2.8067 | -120.3697 | 0.10178 | 0.06904 | 0.01233 | 0.057037 | 0.10528 | -0.12503 | -0.077151 | -0.060273 | -3.1756 | 107.5002 | 112.7972 | 112.8575 | -3.0766 | -3.0676 | 120.2323 | -0.20389 | 120.4112 | 120.3218 | 0.089481 | -0.15565 | -0.38595 | 117.3948 | 117.4938 | 117.5028 | 83.2516 | -120.6306 | 120.3665 | 120.4147 | 120.1844 | 120.3785 | -0.33808
2690.6875 | 120.8267 | -120.401 | 0.22888 | 1.4211e-13 | -0.090984 | 0.00083771 | 0.056739 | 0.069214 | 0.19906 | -0.22823 | -0.0050332 | 0.014277 | 0.015985 | 0.04273 | 0.0009401 | -12.8139 | -37.1219 | -7.5809 | -2.8872 | -2.8019 | -2.7929 | -120.4064 | 0.10178 | 0.06904 | 0.01233 | 0.052459 | 0.096121 | -0.13419 | -0.086309 | -0.005351 | -3.1161 | 107.5871 | 112.8201 | 112.8255 | -3.0308 | -3.0218 | 120.3147 | -0.17642 | 120.5028 | 120.4133 | 0.098639 | -0.13276 | -0.36307 | 117.5138 | 117.5991 | 117.6081 | 83.2791 | -120.6352 | 120.4535 | 120.4971 | 120.2668 | 120.47 | -0.31519
2692.4375 | 120.5338 | -120.0302 | 0.12817 | 1.4211e-13 | -0.091625 | 0.00083771 | 0.057167 | 0.069 | 0.20035 | -0.22823 | -0.0050332 | 0.013849 | 0.015771 | 0.042089 | 0.0011537 | -12.8322 | -37.0761 | -7.645 | -2.8002 | -2.7195 | -2.6968 | -120.1133 | 0.10636 | 0.073618 | 0.01233 | 0.061616 | 0.096121 | -0.13876 | -0.086309 | -0.083089 | -2.9284 | 107.198 | 112.3852 | 112.4683 | -2.8477 | -2.8249 | 119.9439 | -0.066558 | 120.1366 | 120.0425 | 0.098639 | -0.032053 | -0.26694 | 117.23 | 117.3107 | 117.3334 | 82.9541 | -120.2415 | 120.0918 | 120.1263 | 119.8914 | 120.1038 | -0.21448
2694.125 | 120.4102 | -119.9066 | 0.2243 | 1.4211e-13 | -0.091625 | 0.0010513 | 0.056739 | 0.068787 | 0.63643 | -0.23586 | -0.005247 | 0.014277 | 0.015985 | 0.042089 | 0.0009401 | -13.2168 | -37.3417 | -7.6129 | -2.933 | -2.8523 | -2.8295 | -119.8203 | 0.11094 | 0.06904 | 0.01233 | 0.052459 | 0.1007 | -0.13419 | -0.077151 | 0.086366 | -3.1573 | 106.6899 | 112.2937 | 112.2073 | -3.0766 | -3.0539 | 119.8295 | -0.17184 | 120.0176 | 119.9189 | 0.089481 | -0.1236 | -0.35849 | 116.9736 | 117.0543 | 117.0771 | 82.5649 | -120.0446 | 119.9591 | 120.0073 | 119.7724 | 119.9757 | -0.30146
2695.8594 | 120.4285 | -119.1925 | 1.0025 | 1.4211e-13 | -0.091625 | 0.0025471 | 0.055671 | 0.068359 | 1.8317 | -0.23586 | -0.0048196 | 0.014063 | 0.016199 | 0.04273 | 0.0009401 | -16.0462 | -39.4066 | -8.0753 | -4.247 | -4.1665 | -4.1436 | -119.3211 | 0.11094 | 0.091933 | 0.016908 | 0.061616 | 0.10528 | -0.12961 | -0.067994 | -0.12864 | -5.2495 | 103.1463 | 111.1172 | 111.2458 | -5.169 | -5.1461 | 119.1245 | -0.94089 | 119.3034 | 119.2094 | 0.084902 | -0.89722 | -1.1321 | 114.9455 | 115.026 | 115.0489 | 79.7859 | -120.3236 | 119.2541 | 119.2978 | 119.0629 | 119.2844 | -1.0705
2697.5469 | 120.4468 | -120.1263 | 0.13275 | 1.4211e-13 | -0.043549 | -0.00087189 | 0.009088 | 0.016653 | 4.5802 | -0.23586 | -0.005247 | 0.014277 | 0.016199 | 0.042089 | 0.0013673 | -6.7429 | -13.4414 | -3.4742 | -2.0219 | -1.9411 | -1.9276 | -37.743 | 0.11552 | 0.087354 | 0.030644 | 0.07993 | 0.12359 | -0.10214 | -0.058836 | 82.3833 | -2.1546 | 113.3834 | 116.6522 | 34.2689 | -2.0739 | -2.0603 | 120.0675 | -0.052821 | 120.2419 | 120.157 | 0.08948 | -0.009158 | -0.23489 | 118.1045 | 118.1852 | 118.1988 | 106.685 | -37.8758 | 120.2063 | 120.2499 | 120.0242 | 120.2137 | -0.19159
2699.2812 | 120.7443 | -120.3323 | 0.10986 | 1.4211e-13 | -0.023463 | -0.0030087 | -0.0092888 | -0.01326 | 0.012536 | -0.2206 | -0.0050332 | 0.014277 | 0.015985 | 0.042303 | 0.0009401 | 0.028518 | -0.003172 | -0.022144 | 0.065863 | 0.055306 | 0.1786 | -0.13632 | 0.097201 | 0.078197 | 0.01233 | 0.052459 | 0.096121 | -0.14334 | -0.08173 | 120.196 | -0.044 | 120.3609 | 120.3102 | 0.11418 | -0.054557 | 0.068732 | 120.2506 | -0.057404 | 120.4295 | 120.3447 | 0.09406 | -0.013742 | -0.25321 | 120.3982 | 120.3876 | 120.5109 | 120.3292 | -0.24618 | 120.3848 | 120.4285 | 120.189 | 120.4105 | -0.19159
2701.0312 | 120.7535 | -120.4605 | 0.11444 | 1.4211e-13 | -0.022822 | -0.0030087 | -0.0088614 | -0.012833 | 0.011681 | -0.23586 | -0.005247 | 0.014918 | 0.016199 | 0.04273 | 0.0011537 | 0.046831 | 0.0243 | -0.012988 | 0.07502 | -0.059167 | 0.18775 | -0.021847 | 0.10178 | 0.073618 | 0.003172 | 0.052459 | 0.091543 | -0.12961 | -0.08173 | 120.4387 | -0.039421 | 120.5073 | 120.4475 | 0.008859 | -0.17361 | 0.073311 | 120.3788 | -0.061982 | 120.5623 | 120.4637 | 0.084902 | -0.022898 | -0.24405 | 120.5355 | 120.4013 | 120.6483 | 120.4848 | -0.13629 | 120.513 | 120.5521 | 120.3309 | 120.5341 | -0.19617
2702.7812 | 120.7077 | -120.2591 | 0.12817 | 1.4211e-13 | -0.023463 | -0.0030087 | -0.0092888 | -0.013474 | 0.011895 | -0.23586 | -0.0048196 | 0.01449 | 0.016199 | 0.042517 | 0.0009401 | 0.055988 | 0.028878 | 0.000747 | 0.088755 | -0.063746 | 0.19233 | 0.005627 | 0.092622 | 0.06904 | 0.003172 | 0.057037 | 0.086964 | -0.13876 | -0.08173 | 120.2647 | -0.039419 | 120.3151 | 120.2598 | -0.00488 | -0.19192 | 0.064157 | 120.1774 | -0.071137 | 120.3517 | 120.2623 | 0.084902 | -0.04121 | -0.26694 | 120.3478 | 120.1953 | 120.4514 | 120.288 | -0.12255 | 120.3161 | 120.3461 | 120.1203 | 120.3281 | -0.2099
2704.4844 | 120.7031 | -120.4559 | 0.13733 | 1.4211e-13 | -0.02325 | -0.0030087 | -0.0090752 | -0.013046 | 0.011681 | -0.24349 | -0.0054606 | 0.01449 | 0.015771 | 0.042517 | 0.0007265 | 0.069723 | 0.033457 | -0.003831 | 0.084176 | -0.063746 | 0.19233 | 0.010206 | 0.10178 | 0.064461 | 0.01233 | 0.061616 | 0.086964 | -0.13876 | -0.090888 | 120.4661 | -0.053153 | 120.5257 | 120.4521 | -0.014037 | -0.20108 | 0.055002 | 120.365 | -0.075713 | 120.5577 | 120.4683 | 0.10322 | -0.050365 | -0.27609 | 120.5401 | 120.3922 | 120.6483 | 120.4894 | -0.12712 | 120.5175 | 120.5429 | 120.3172 | 120.5204 | -0.22822
2706.2188 | 120.3232 | -120.0851 | 0.10986 | 1.4211e-13 | -0.02325 | -0.0032223 | -0.0088614 | -0.012833 | 0.011467 | -0.23586 | -0.0054606 | 0.01449 | 0.016199 | 0.042089 | 0.0007265 | 0.069723 | 0.038035 | 0.005325 | 0.088755 | -0.059167 | 0.20149 | 0.010206 | 0.10178 | 0.073618 | 0.007751 | 0.057037 | 0.096121 | -0.12961 | -0.08173 | 120.0953 | -0.021108 | 120.1549 | 120.0905 | -0.004881 | -0.16903 | 0.091625 | 120.0034 | -0.052826 | 120.1869 | 120.0929 | 0.089481 | -0.013742 | -0.23947 | 120.1739 | 120.026 | 120.2866 | 120.1232 | -0.099657 | 120.1422 | 120.1813 | 119.9555 | 120.1588 | -0.19159
2707.8906 | 120.4468 | -120.0394 | 0.12817 | 1.4211e-13 | -0.023463 | -0.0027949 | -0.0090752 | -0.012833 | 0.011467 | -0.22823 | -0.005247 | 0.014063 | 0.015558 | 0.04273 | 0.0009401 | 0.07888 | 0.042614 | 0.000747 | 0.084176 | -0.054588 | 0.18775 | 0.014784 | 0.10178 | 0.078197 | -0.001407 | 0.057037 | 0.096121 | -0.13876 | -0.08173 | 120.0542 | -0.043998 | 120.1182 | 120.0401 | -0.014037 | -0.18276 | 0.059578 | 119.9576 | -0.071137 | 120.1411 | 120.038 | 0.080323 | -0.032053 | -0.26694 | 120.1235 | 119.9848 | 120.2271 | 120.082 | -0.11339 | 120.0964 | 120.1355 | 119.9006 | 120.1176 | -0.2099
2709.6406 | 120.6528 | -120.2637 | 0.12817 | 1.4211e-13 | -0.023463 | -0.0027949 | -0.0092888 | -0.01326 | 0.011895 | -0.23586 | -0.0050332 | 0.01449 | 0.016199 | 0.04273 | 0.0009401 | 0.069723 | 0.038035 | -0.003831 | 0.079598 | -0.059167 | 0.19691 | 0.019363 | 0.097201 | 0.073618 | 0.007751 | 0.057037 | 0.091543 | -0.13419 | -0.077151 | 120.283 | -0.048576 | 120.3334 | 120.2598 | -0.023194 | -0.18734 | 0.068735 | 120.1865 | -0.071137 | 120.3609 | 120.2714 | 0.084902 | -0.036631 | -0.26236 | 120.3433 | 120.2045 | 120.4606 | 120.3017 | -0.10881 | 120.3207 | 120.3552 | 120.1295 | 120.3373 | -0.20533
2711.375 | 120.7535 | -120.3278 | 0.1236 | 1.4211e-13 | -0.023463 | -0.0027949 | -0.0095024 | -0.01326 | 0.011895 | -0.22823 | -0.005247 | 0.014277 | 0.015771 | 0.042303 | 0.0007265 | 0.07888 | 0.042614 | 0.009904 | 0.088755 | -0.054588 | 0.19233 | 0.014784 | 0.10178 | 0.073618 | 0.007751 | 0.057037 | 0.091543 | -0.13419 | -0.086309 | 120.3425 | -0.034841 | 120.4066 | 120.3377 | -0.00488 | -0.17818 | 0.068735 | 120.2415 | -0.066559 | 120.4295 | 120.3355 | 0.09406 | -0.032053 | -0.25778 | 120.4165 | 120.2732 | 120.5201 | 120.3704 | -0.10881 | 120.3848 | 120.4193 | 120.1936 | 120.4014 | -0.20991
2713.0469 | 120.3461 | -119.3115 | -3.1677 | 1.4211e-13 | -0.023463 | -0.0027949 | -0.0090752 | -0.013046 | 0.012108 | -0.25112 | -0.005247 | 0.014063 | 0.015985 | 0.042303 | 0.0007265 | 0.07888 | 0.047193 | 0.009904 | 0.079598 | -0.054588 | 0.17402 | -0.021847 | 0.097201 | 0.064461 | 0.007751 | 0.052459 | 0.096121 | -0.13876 | -0.077151 | 119.2897 | 3.2473 | 119.3904 | 119.3214 | 0.031751 | 3.1131 | 3.3417 | 119.2344 | 3.2202 | 119.4087 | 119.3193 | 0.084902 | 3.2638 | 3.029 | 119.3911 | 119.2569 | 119.4855 | 119.3587 | 3.1459 | 119.364 | 119.4076 | 119.1728 | 119.376 | 3.0906
2714.8125 | 120.3781 | -120.0348 | 0.11902 | 1.4211e-13 | -0.02325 | -0.0034359 | -0.0095024 | -0.01326 | 0.011681 | -0.2206 | -0.0050332 | 0.014277 | 0.016199 | 0.042517 | 0.0007265 | 0.074302 | 0.047193 | 0.01906 | 0.093333 | -0.054588 | 0.16944 | 0.028521 | 0.097201 | 0.073618 | 0.01233 | 0.057037 | 0.091543 | -0.13419 | -0.086309 | 120.0633 | -0.025686 | 120.1091 | 120.0538 | -0.009461 | -0.17361 | 0.050419 | 119.9485 | -0.061982 | 120.132 | 120.0471 | 0.098639 | -0.027476 | -0.25321 | 120.1281 | 119.9802 | 120.2042 | 120.082 | -0.090498 | 120.0918 | 120.1263 | 119.9006 | 120.1084 | -0.20533
2716.5625 | 120.4742 | -120.3049 | 0.14648 | 1.4211e-13 | -0.023677 | -0.0030087 | -0.0095024 | -0.013046 | 0.012322 | -0.22823 | -0.0054606 | 0.014704 | 0.015771 | 0.04273 | 0.0011537 | 0.088037 | 0.047193 | 0.009904 | 0.084176 | -0.063746 | 0.17402 | 0.019363 | 0.10178 | 0.06904 | 0.007751 | 0.057037 | 0.096121 | -0.14334 | -0.077151 | 120.3242 | -0.062308 | 120.3929 | 120.3148 | -0.009459 | -0.21023 | 0.027532 | 120.2277 | -0.089447 | 120.4066 | 120.3126 | 0.084902 | -0.050363 | -0.28983 | 120.389 | 120.2411 | 120.4789 | 120.3521 | -0.12712 | 120.3619 | 120.401 | 120.1615 | 120.3739 | -0.22364
2718.2344 | 120.4147 | -120.3552 | 0.13733 | 1.4211e-13 | -0.023891 | -0.0032223 | -0.0097162 | -0.01326 | 0.011895 | -0.22823 | -0.005247 | 0.01449 | 0.015985 | 0.042517 | 0.0011537 | 0.088037 | 0.05635 | 0.01906 | 0.093333 | -0.050009 | 0.16944 | 0.0331 | 0.10636 | 0.06904 | 0.01233 | 0.057037 | 0.091543 | -0.13876 | -0.08173 | 120.3883 | -0.043996 | 120.4433 | 120.3743 | -0.01404 | -0.18734 | 0.032109 | 120.2735 | -0.080292 | 120.4616 | 120.3676 | 0.09406 | -0.045786 | -0.27609 | 120.4486 | 120.3052 | 120.5247 | 120.4116 | -0.10423 | 120.4123 | 120.4468 | 120.2165 | 120.4243 | -0.21906
2719.9219 | 120.3415 | -120.4193 | 0.15564 | 1.4211e-13 | -0.023463 | -0.0034359 | -0.0092888 | -0.01326 | 0.011681 | -0.23586 | -0.0050332 | 0.014277 | 0.015985 | 0.042517 | 0.0007265 | 0.083459 | 0.051771 | 0.01906 | 0.088755 | -0.059167 | 0.17402 | 0.0331 | 0.10178 | 0.06904 | 0.003172 | 0.052459 | 0.096121 | -0.13419 | -0.08173 | 120.4524 | -0.066885 | 120.5028 | 120.4384 | -0.01404 | -0.21481 | 0.018376 | 120.3376 | -0.10318 | 120.5211 | 120.4225 | 0.084902 | -0.059519 | -0.28983 | 120.5081 | 120.3601 | 120.5933 | 120.4711 | -0.12254 | 120.4718 | 120.5154 | 120.2851 | 120.4884 | -0.23737
2721.6719 | 120.369 | -120.4697 | 0.14191 | 1.4211e-13 | -0.023677 | -0.0030087 | -0.0095024 | -0.013474 | 0.011895 | -0.23586 | -0.0050332 | 0.01449 | 0.015985 | 0.042517 | 0.0007265 | 0.088037 | 0.05635 | 0.01906 | 0.093333 | -0.059167 | 0.17402 | 0.0331 | 0.097201 | 0.064461 | 0.003172 | 0.052459 | 0.10528 | -0.13876 | -0.08173 | 120.5028 | -0.048574 | 120.5577 | 120.4887 | -0.01404 | -0.20107 | 0.032109 | 120.3879 | -0.089448 | 120.5669 | 120.4728 | 0.084902 | -0.036628 | -0.28067 | 120.563 | 120.4105 | 120.6437 | 120.526 | -0.10881 | 120.5221 | 120.5749 | 120.3309 | 120.5341 | -0.22364
2723.4219 | 120.0668 | -120.0302 | 0.14648 | 1.4211e-13 | -0.023677 | -0.0032223 | -0.0088614 | -0.01326 | 0.012108 | -0.24349 | -0.005247 | 0.014277 | 0.015985 | 0.04273 | 0.0011537 | 0.088037 | 0.060928 | 0.01906 | 0.088755 | -0.063746 | 0.16944 | 0.055995 | 0.10178 | 0.078197 | 0.01233 | 0.052459 | 0.096121 | -0.13876 | -0.086309 | 120.0862 | -0.057729 | 120.1182 | 120.0493 | -0.036935 | -0.21023 | 0.022954 | 119.9439 | -0.094025 | 120.132 | 120.0425 | 0.098639 | -0.050363 | -0.28525 | 120.119 | 119.9665 | 120.1997 | 120.0911 | -0.090489 | 120.0827 | 120.1263 | 119.8914 | 120.1084 | -0.23279
2725.1562 | 120.5658 | -120.4926 | 0.1236 | 1.4211e-13 | -0.023677 | -0.0034359 | -0.0090752 | -0.01326 | 0.012108 | -0.22823 | -0.0048196 | 0.014277 | 0.015985 | 0.04273 | 0.0005127 | 0.088037 | 0.05635 | 0.01906 | 0.079598 | -0.054588 | 0.1786 | 0.055995 | 0.10178 | 0.06904 | 0.007751 | 0.04788 | 0.091543 | -0.13876 | -0.08173 | 120.5485 | -0.043998 | 120.5806 | 120.5116 | -0.036935 | -0.17818 | 0.054999 | 120.4108 | -0.075716 | 120.5943 | 120.5003 | 0.089481 | -0.032053 | -0.26236 | 120.5722 | 120.438 | 120.6711 | 120.5489 | -0.067601 | 120.5404 | 120.5841 | 120.3538 | 120.5616 | -0.20533
2726.8906 | 117.9657 | -89.4333 | 28.1754 | 1.4211e-13 | -0.023891 | -0.0034359 | -0.0095024 | -0.013046 | 0.011467 | -0.23586 | -0.0050332 | 0.014277 | 0.016412 | 0.04273 | 0.0007265 | 0.088037 | 0.05635 | 0.014482 | 0.065863 | -0.059167 | 0.16486 | 0.037679 | 0.088043 | 0.06904 | -0.001407 | 0.052459 | 0.077807 | -0.13419 | -0.095467 | 89.471 | -28.1095 | 89.5213 | 89.4478 | -0.023197 | -28.2345 | -28.0105 | 89.3378 | -28.1229 | 89.5213 | 89.4319 | 0.09406 | -28.0975 | -28.3095 | 89.4992 | 89.3741 | 89.5981 | 89.4896 | -28.1377 | 89.4857 | 89.5111 | 89.2991 | 89.5023 | -28.2708
2728.5781 | 120.7397 | -120.3094 | 0.10529 | 1.4211e-13 | -0.023677 | -0.0032223 | -0.0092888 | -0.01326 | 0.012108 | -0.25112 | -0.0054606 | 0.014277 | 0.015771 | 0.042517 | 0.0009401 | 0.097194 | 0.051771 | 0.01906 | 0.079598 | -0.059167 | 0.17402 | 0.083468 | 0.097201 | 0.073618 | 0.007751 | 0.04788 | 0.091543 | -0.13876 | -0.08173 | 120.3929 | -0.025688 | 120.4066 | 120.3285 | -0.064408 | -0.16445 | 0.06873 | 120.2277 | -0.057406 | 120.4066 | 120.3172 | 0.089481 | -0.013743 | -0.24405 | 120.389 | 120.2503 | 120.4835 | 120.3612 | -0.021818 | 120.3573 | 120.401 | 120.1707 | 120.3831 | -0.18702
2730.3281 | 118.0435 | -94.7159 | 22.5815 | 1.4211e-13 | -0.023891 | -0.0032223 | -0.0095024 | -0.01326 | 0.011681 | -0.22823 | -0.005247 | 0.01449 | 0.015771 | 0.042944 | 0.0007265 | 0.07888 | 0.047193 | 0.000747 | 0.056706 | -0.063746 | 0.16028 | 0.019363 | 0.083464 | 0.059882 | -0.015143 | 0.038723 | 0.077807 | -0.13876 | -0.10004 | 94.7352 | -22.5248 | 94.7948 | 94.7166 | -0.018616 | -22.6452 | -22.4212 | 94.6158 | -22.5428 | 94.7993 | 94.7007 | 0.084902 | -22.5037 | -22.7202 | 94.7726 | 94.6521 | 94.8762 | 94.7631 | -22.5621 | 94.7546 | 94.7937 | 94.5771 | 94.7758 | -22.6815
2732.0781 | 120.7306 | -120.2545 | 0.10529 | 1.4211e-13 | -0.023891 | -0.0034359 | -0.0090752 | -0.01326 | 0.011895 | -0.24349 | -0.0054606 | 0.014704 | 0.015771 | 0.042944 | 0.0007265 | 0.10177 | 0.060928 | 0.023639 | 0.070441 | -0.059167 | 0.16028 | 0.078889 | 0.097201 | 0.078197 | 0.01233 | 0.057037 | 0.091543 | -0.13419 | -0.086309 | 120.3334 | -0.034845 | 120.3563 | 120.2782 | -0.05525 | -0.16445 | 0.054994 | 120.1682 | -0.048249 | 120.3517 | 120.2668 | 0.098639 | -0.013743 | -0.23947 | 120.325 | 120.1954 | 120.4148 | 120.3154 | -0.026397 | 120.3116 | 120.3461 | 120.1203 | 120.3327 | -0.1916
2733.8281 | 120.8313 | -120.3918 | 0.11444 | 1.4211e-13 | -0.023677 | -0.0034359 | -0.0095024 | -0.012833 | 0.011895 | -0.23586 | -0.005247 | 0.01449 | 0.015771 | 0.04273 | 0.0007265 | 0.097194 | 0.060928 | 0.01906 | 0.079598 | -0.059167 | 0.16944 | 0.069732 | 0.097201 | 0.073618 | 0.01233 | 0.061616 | 0.091543 | -0.13876 | -0.086309 | 120.4616 | -0.034843 | 120.489 | 120.4109 | -0.050672 | -0.17361 | 0.054997 | 120.3055 | -0.052825 | 120.489 | 120.4042 | 0.098639 | -0.022898 | -0.25321 | 120.4714 | 120.3327 | 120.5613 | 120.4528 | -0.044709 | 120.4535 | 120.4834 | 120.2531 | 120.4655 | -0.20075
2735.5625 | 120.8176 | -120.5017 | 0.09613 | 1.4211e-13 | -0.023891 | -0.0032223 | -0.0090752 | -0.013046 | 0.012108 | -0.22823 | -0.005247 | 0.014063 | 0.015771 | 0.042944 | 0.0009401 | 0.097194 | 0.060928 | 0.014482 | 0.084176 | -0.054588 | 0.16486 | 0.088047 | 0.097201 | 0.06904 | 0.003172 | 0.052459 | 0.091543 | -0.13876 | -0.090888 | 120.5898 | -0.011954 | 120.5989 | 120.5162 | -0.073565 | -0.15072 | 0.068729 | 120.4108 | -0.043671 | 120.5989 | 120.5049 | 0.09406 | -0.004587 | -0.23489 | 120.5859 | 120.4471 | 120.6666 | 120.5626 | -0.008083 | 120.5542 | 120.5933 | 120.3629 | 120.5707 | -0.18702
2737.3125 | 120.8817 | -120.5521 | 0.1236 | 1.4211e-13 | -0.024104 | -0.0034359 | -0.0090752 | -0.013687 | 0.011895 | -0.23586 | -0.005247 | 0.014277 | 0.015985 | 0.04273 | 0.0009401 | 0.10177 | 0.065507 | 0.014482 | 0.079598 | -0.059167 | 0.16944 | 0.069732 | 0.092622 | 0.06904 | 0.007751 | 0.057037 | 0.091543 | -0.13419 | -0.08173 | 120.6218 | -0.043998 | 120.6538 | 120.5665 | -0.05525 | -0.18276 | 0.045842 | 120.4703 | -0.066559 | 120.6447 | 120.5598 | 0.089481 | -0.032053 | -0.25778 | 120.6317 | 120.4929 | 120.7215 | 120.6176 | -0.053864 | 120.6091 | 120.6436 | 120.4179 | 120.6211 | -0.20533
2739 | 120.9412 | -120.5704 | 0.11444 | 1.4211e-13 | -0.024104 | -0.0034359 | -0.0090752 | -0.01326 | 0.012108 | -0.22823 | -0.0050332 | 0.014277 | 0.015558 | 0.04273 | 0.0009401 | 0.10177 | 0.060928 | 0.014482 | 0.079598 | -0.054588 | 0.16944 | 0.092626 | 0.097201 | 0.06904 | 0.003172 | 0.057037 | 0.096121 | -0.12961 | -0.08173 | 120.663 | -0.034843 | 120.6721 | 120.5849 | -0.078144 | -0.16903 | 0.054997 | 120.4886 | -0.057404 | 120.6676 | 120.5735 | 0.084902 | -0.01832 | -0.24405 | 120.65 | 120.5158 | 120.7398 | 120.6313 | -0.021815 | 120.6274 | 120.6665 | 120.4408 | 120.6394 | -0.19617
2740.75 | 120.9274 | -120.6024 | 0.10071 | 1.4211e-13 | -0.023891 | -0.0032223 | -0.0095024 | -0.01326 | 0.011895 | -0.22823 | -0.0054606 | 0.01449 | 0.015985 | 0.042944 | 0.0005127 | 0.097194 | 0.070086 | 0.023639 | 0.079598 | -0.063746 | 0.16944 | 0.088047 | 0.097201 | 0.06904 | 0.003172 | 0.057037 | 0.091543 | -0.12961 | -0.086309 | 120.6905 | -0.02111 | 120.6996 | 120.6261 | -0.064408 | -0.16445 | 0.06873 | 120.5161 | -0.043671 | 120.6996 | 120.6056 | 0.089481 | -0.009165 | -0.23031 | 120.682 | 120.5387 | 120.7719 | 120.6725 | -0.012661 | 120.6595 | 120.694 | 120.4728 | 120.6715 | -0.18702
2742.4219 | 120.8588 | -120.6848 | 0.16022 | 1.4211e-13 | -0.023677 | -0.0032223 | -0.0095024 | -0.013474 | 0.011895 | -0.22823 | -0.005247 | 0.01449 | 0.015771 | 0.042944 | 0.0009401 | 0.097194 | 0.065507 | 0.01906 | 0.07502 | -0.063746 | 0.16944 | 0.083468 | 0.097201 | 0.078197 | 0.003172 | 0.04788 | 0.096121 | -0.13419 | -0.090888 | 120.7683 | -0.085197 | 120.782 | 120.7039 | -0.064408 | -0.22396 | 0.009221 | 120.5939 | -0.11234 | 120.782 | 120.688 | 0.09406 | -0.064096 | -0.2944 | 120.7598 | 120.6211 | 120.8543 | 120.7503 | -0.076749 | 120.7327 | 120.7809 | 120.5506 | 120.763 | -0.25111
2744.1719 | 121.0281 | -120.6482 | 0.11444 | 1.4211e-13 | -0.024104 | -0.0030087 | -0.0092888 | -0.013901 | 0.012108 | -0.23586 | -0.005247 | 0.01449 | 0.016199 | 0.04273 | 0.0002991 | 0.10177 | 0.070086 | 0.014482 | 0.07502 | -0.063746 | 0.16944 | 0.097205 | 0.10636 | 0.073618 | 0.003172 | 0.052459 | 0.091543 | -0.13876 | -0.086309 | 120.7454 | -0.039421 | 120.75 | 120.6627 | -0.082723 | -0.17819 | 0.054997 | 120.5619 | -0.061982 | 120.7546 | 120.6514 | 0.089481 | -0.022898 | -0.25321 | 120.7232 | 120.5844 | 120.8176 | 120.7183 | -0.017236 | 120.7007 | 120.7397 | 120.5094 | 120.7218 | -0.20075
2745.9062 | 120.9778 | -120.6802 | 0.11902 | 1.4211e-13 | -0.024318 | -0.0030087 | -0.0095024 | -0.013901 | 0.012108 | -0.23586 | -0.0050332 | 0.014704 | 0.015344 | 0.043158 | 0.0005127 | 0.11093 | 0.070086 | 0.028217 | 0.079598 | -0.059167 | 0.1786 | 0.092626 | 0.092622 | 0.073618 | 0.007751 | 0.066194 | 0.091543 | -0.13876 | -0.086309 | 120.7729 | -0.039421 | 120.7912 | 120.7085 | -0.064409 | -0.17819 | 0.059576 | 120.5939 | -0.052825 | 120.7729 | 120.688 | 0.09406 | -0.027476 | -0.25778 | 120.7598 | 120.6211 | 120.8588 | 120.7503 | -0.026393 | 120.7464 | 120.7718 | 120.5415 | 120.7539 | -0.20533
2747.6094 | 121.0419 | -120.7031 | 0.091553 | 1.4211e-13 | -0.024104 | -0.0034359 | -0.0092888 | -0.013687 | 0.012322 | -0.23586 | -0.0054606 | 0.014277 | 0.015771 | 0.042944 | 0.0005127 | 0.097194 | 0.070086 | 0.023639 | 0.07502 | -0.054588 | 0.16944 | 0.097205 | 0.10178 | 0.073618 | 0.007751 | 0.057037 | 0.086964 | -0.12961 | -0.08173 | 120.8003 | -0.016533 | 120.8003 | 120.7268 | -0.073566 | -0.14614 | 0.077885 | 120.6214 | -0.034516 | 120.8049 | 120.7109 | 0.089481 | -0.004589 | -0.22116 | 120.7781 | 120.6485 | 120.8726 | 120.7732 | 0.005652 | 120.7602 | 120.7901 | 120.5735 | 120.7767 | -0.17328
2749.375 | 121.0785 | -120.7214 | 0.11444 | 1.4211e-13 | -0.024104 | -0.0034359 | -0.0095024 | -0.01326 | 0.012322 | -0.22823 | -0.0056742 | 0.014277 | 0.015771 | 0.043158 | 0.0002991 | 0.11551 | 0.070086 | 0.014482 | 0.079598 | -0.054588 | 0.16486 | 0.10178 | 0.10178 | 0.078197 | 0.007751 | 0.061616 | 0.096121 | -0.12961 | -0.090888 | 120.8232 | -0.034843 | 120.8369 | 120.7359 | -0.087302 | -0.16903 | 0.050418 | 120.6305 | -0.052825 | 120.8232 | 120.7292 | 0.098639 | -0.01832 | -0.24405 | 120.801 | 120.6668 | 120.8863 | 120.7915 | -0.012657 | 120.7831 | 120.8176 | 120.5918 | 120.7996 | -0.20533
2751.0625 | 120.8679 | -120.813 | 0.15564 | 1.4211e-13 | -0.024318 | -0.0030087 | -0.0095024 | -0.01326 | 0.011895 | -0.22823 | -0.005247 | 0.014277 | 0.015771 | 0.042944 | 0.0005127 | 0.10177 | 0.070086 | 0.01906 | 0.079598 | -0.059167 | 0.16486 | 0.10178 | 0.10178 | 0.073618 | 0.007751 | 0.052459 | 0.091543 | -0.13419 | -0.08173 | 120.9148 | -0.076042 | 120.9148 | 120.832 | -0.082724 | -0.21481 | 0.009219 | 120.7313 | -0.10318 | 120.9148 | 120.8207 | 0.089481 | -0.064097 | -0.28983 | 120.8926 | 120.7538 | 120.9778 | 120.8831 | -0.053856 | 120.8654 | 120.9045 | 120.6788 | 120.8866 | -0.23737
2752.8125 | 121.0373 | -120.7993 | 0.11902 | 1.4211e-13 | -0.024104 | -0.0036497 | -0.0095024 | -0.01326 | 0.012108 | -0.22823 | -0.0050332 | 0.014277 | 0.015558 | 0.043158 | 0.0005127 | 0.10635 | 0.060928 | 0.01906 | 0.07502 | -0.059167 | 0.16028 | 0.097205 | 0.10178 | 0.06904 | 0.007751 | 0.057037 | 0.091543 | -0.13876 | -0.08173 | 120.8965 | -0.043999 | 120.9056 | 120.8183 | -0.078145 | -0.17819 | 0.041261 | 120.7175 | -0.061982 | 120.901 | 120.807 | 0.089481 | -0.027476 | -0.25778 | 120.8743 | 120.7401 | 120.9595 | 120.8602 | -0.021814 | 120.8563 | 120.8908 | 120.6605 | 120.8683 | -0.20075
2754.5156 | 120.9274 | -120.8084 | 0.16022 | 1.4211e-13 | -0.024746 | -0.0034359 | -0.0092888 | -0.013046 | 0.012322 | -0.23586 | -0.005247 | 0.014277 | 0.015771 | 0.043371 | 0.0005127 | 0.11551 | 0.060928 | 0.023639 | 0.079598 | -0.063746 | 0.16486 | 0.10178 | 0.10178 | 0.073618 | 0.007751 | 0.052459 | 0.096121 | -0.12961 | -0.08173 | 120.9102 | -0.080619 | 120.9239 | 120.8321 | -0.078145 | -0.22396 | 0.004642 | 120.7267 | -0.10776 | 120.9102 | 120.8162 | 0.089481 | -0.064096 | -0.28982 | 120.888 | 120.7447 | 120.9733 | 120.8693 | -0.058433 | 120.8609 | 120.9045 | 120.6788 | 120.882 | -0.24195
2756.2656 | 121.1655 | -120.7993 | 0.11444 | 1.4211e-13 | -0.024532 | -0.0032223 | -0.0097162 | -0.013474 | 0.012108 | -0.23586 | -0.0054606 | 0.014277 | 0.015558 | 0.042944 | 0.0005127 | 0.10177 | 0.065507 | 0.01906 | 0.079598 | -0.068325 | 0.16486 | 0.10178 | 0.097201 | 0.073618 | 0.01233 | 0.057037 | 0.096121 | -0.12961 | -0.086309 | 120.901 | -0.034843 | 120.901 | 120.8183 | -0.082724 | -0.18277 | 0.050418 | 120.7129 | -0.057404 | 120.8965 | 120.8116 | 0.098639 | -0.01832 | -0.24405 | 120.8789 | 120.7309 | 120.9641 | 120.8648 | -0.012657 | 120.8563 | 120.8954 | 120.6696 | 120.8729 | -0.20075
2758.0156 | 121.138 | -120.8267 | 0.11902 | 1.4211e-13 | -0.024532 | -0.0030087 | -0.0092888 | -0.01326 | 0.012108 | -0.2206 | -0.0050332 | 0.014277 | 0.015558 | 0.043158 | 0.0009401 | 0.10635 | 0.070086 | 0.014482 | 0.088755 | -0.054588 | 0.16028 | 0.10178 | 0.097201 | 0.073618 | 0.003172 | 0.057037 | 0.096121 | -0.12503 | -0.08173 | 120.9285 | -0.030264 | 120.9331 | 120.8412 | -0.087302 | -0.17361 | 0.041261 | 120.745 | -0.061982 | 120.9239 | 120.8299 | 0.084902 | -0.022898 | -0.24405 | 120.9155 | 120.7721 | 120.987 | 120.8968 | -0.017235 | 120.8838 | 120.9228 | 120.7017 | 120.9003 | -0.20075
2759.7812 | 120.9915 | -120.726 | 0.14648 | 1.4211e-13 | -0.024532 | -0.0032223 | -0.0092888 | -0.013901 | 0.011895 | -0.24349 | -0.0050332 | 0.014277 | 0.015558 | 0.043158 | 0.0005127 | 0.11093 | 0.074664 | 0.01906 | 0.079598 | -0.063746 | 0.16944 | 0.092626 | 0.10178 | 0.073618 | 0.003172 | 0.057037 | 0.1007 | -0.13419 | -0.090888 | 120.8186 | -0.066886 | 120.8369 | 120.7451 | -0.073566 | -0.21023 | 0.022954 | 120.6351 | -0.089447 | 120.8278 | 120.7292 | 0.09406 | -0.045784 | -0.28067 | 120.8056 | 120.6623 | 120.8955 | 120.8007 | -0.053858 | 120.783 | 120.8267 | 120.5918 | 120.7996 | -0.23737
2761.4531 | 121.2112 | -120.8725 | 0.12817 | 1.4211e-13 | -0.024318 | -0.0034359 | -0.0092888 | -0.013687 | 0.012108 | -0.22823 | -0.005247 | 0.01449 | 0.015344 | 0.043158 | 0.0005127 | 0.10635 | 0.070086 | 0.01906 | 0.084176 | -0.063746 | 0.16486 | 0.11094 | 0.092622 | 0.06904 | -0.001407 | 0.057037 | 0.091543 | -0.12961 | -0.090888 | 120.9834 | -0.043998 | 120.9788 | 120.8916 | -0.091882 | -0.19192 | 0.036685 | 120.7816 | -0.071137 | 120.9651 | 120.8711 | 0.089481 | -0.036631 | -0.25778 | 120.9567 | 120.8088 | 121.0374 | 120.9426 | -0.017232 | 120.9295 | 120.964 | 120.7429 | 120.9415 | -0.21906
2763.125 | 121.0236 | -120.607 | 0.12817 | 1.4211e-13 | -0.024746 | -0.0034359 | -0.0090752 | -0.01326 | 0.012108 | -0.23586 | -0.005247 | 0.014063 | 0.015771 | 0.042944 | 0.0007265 | 0.11093 | 0.070086 | 0.023639 | 0.07502 | -0.059167 | 0.16944 | 0.10636 | 0.10178 | 0.06904 | 0.003172 | 0.057037 | 0.091543 | -0.13876 | -0.086309 | 120.7134 | -0.053154 | 120.7179 | 120.6306 | -0.082724 | -0.18734 | 0.041264 | 120.5207 | -0.071137 | 120.7088 | 120.6102 | 0.089481 | -0.036631 | -0.26694 | 120.682 | 120.5478 | 120.7764 | 120.6771 | -0.021811 | 120.664 | 120.6985 | 120.4682 | 120.676 | -0.21448
2764.875 | 91.4658 | -108.9569 | 0.36621 | 1.4211e-13 | -0.024318 | -0.0027949 | -0.0095024 | -0.013046 | 0.011895 | -0.23586 | -0.0054606 | 0.014277 | 0.015771 | 0.042517 | 8.5502e-05 | 0.11093 | 0.070086 | 0.01906 | 0.079598 | -0.054588 | 0.16944 | -0.049321 | 0.097201 | 0.073618 | 0.003172 | 0.04788 | 0.086964 | -0.13876 | -0.086309 | 108.9076 | -0.28661 | 109.0678 | 108.976 | 0.068381 | -0.4208 | -0.19677 | 108.8706 | -0.31833 | 109.0541 | 108.9601 | 0.089481 | -0.27925 | -0.50498 | 109.0365 | 108.9023 | 109.1263 | 109.027 | -0.41553 | 109.0048 | 109.0439 | 108.8181 | 109.0305 | -0.45252
2766.625 | 120.8496 | -120.3964 | 0.10529 | 1.4211e-13 | -0.024318 | -0.0032223 | -0.0092888 | -0.013687 | 0.011895 | -0.23586 | -0.0050332 | 0.01449 | 0.015558 | 0.043371 | 0.0005127 | 0.11093 | 0.074664 | 0.023639 | 0.084176 | -0.059167 | 0.16944 | 0.097205 | 0.097201 | 0.06904 | 0.007751 | 0.057037 | 0.096121 | -0.12961 | -0.090888 | 120.4936 | -0.02111 | 120.5074 | 120.4201 | -0.073566 | -0.16445 | 0.064152 | 120.3055 | -0.048249 | 120.4936 | 120.4042 | 0.098639 | -0.009165 | -0.23489 | 120.4806 | 120.3373 | 120.5659 | 120.4711 | -0.008081 | 120.4535 | 120.4925 | 120.2668 | 120.4655 | -0.19617
2768.3125 | 120.9549 | -120.6299 | 0.1236 | 1.4211e-13 | -0.024318 | -0.0034359 | -0.0095024 | -0.01326 | 0.011895 | -0.24349 | -0.005247 | 0.014277 | 0.015558 | 0.043371 | 0.0002991 | 0.10177 | 0.065507 | 0.009904 | 0.084176 | -0.059167 | 0.17402 | 0.10178 | 0.092622 | 0.073618 | 0.003172 | 0.052459 | 0.1007 | -0.12961 | -0.08173 | 120.7317 | -0.03942 | 120.7317 | 120.6398 | -0.09188 | -0.18276 | 0.05042 | 120.5482 | -0.071137 | 120.7225 | 120.6331 | 0.084902 | -0.022896 | -0.2532 | 120.7141 | 120.5707 | 120.8039 | 120.6954 | -0.021812 | 120.6823 | 120.7306 | 120.5003 | 120.7035 | -0.20533
2770 | 121.0556 | -120.6894 | 0.1236 | 1.4211e-13 | -0.024959 | -0.0034359 | -0.0092888 | -0.013046 | 0.011895 | -0.24349 | -0.0050332 | 0.01449 | 0.015558 | 0.043158 | 0.0005127 | 0.10635 | 0.070086 | 0.01906 | 0.084176 | -0.054588 | 0.16944 | 0.10636 | 0.10178 | 0.073618 | 0.007751 | 0.061616 | 0.10528 | -0.13419 | -0.095467 | 120.7958 | -0.03942 | 120.7957 | 120.7085 | -0.087303 | -0.17818 | 0.045842 | 120.5939 | -0.06198 | 120.7912 | 120.6971 | 0.10322 | -0.018317 | -0.25778 | 120.7736 | 120.6348 | 120.8588 | 120.7595 | -0.017233 | 120.751 | 120.7947 | 120.5552 | 120.763 | -0.21906
2771.75 | 121.0693 | -120.7809 | 0.10986 | 1.4211e-13 | -0.024746 | -0.0032223 | -0.0092888 | -0.013687 | 0.011895 | -0.23586 | -0.0054606 | 0.014277 | 0.015558 | 0.043371 | 0.0007265 | 0.10635 | 0.070086 | 0.01906 | 0.070441 | -0.059167 | 0.17402 | 0.097205 | 0.10178 | 0.078197 | 0.003172 | 0.057037 | 0.1007 | -0.13419 | -0.090888 | 120.8782 | -0.039422 | 120.8873 | 120.8 | -0.078145 | -0.16903 | 0.064153 | 120.6901 | -0.052826 | 120.8827 | 120.7841 | 0.09406 | -0.009163 | -0.24405 | 120.8514 | 120.7218 | 120.955 | 120.851 | -0.012658 | 120.838 | 120.8816 | 120.6468 | 120.8591 | -0.20075
2773.4375 | 120.726 | -120.4514 | 0.12817 | 1.4211e-13 | -0.024532 | -0.0032223 | -0.0095024 | -0.013474 | 0.011681 | -0.22823 | -0.005247 | 0.014277 | 0.015344 | 0.043371 | 8.5502e-05 | 0.10635 | 0.074664 | 0.023639 | 0.079598 | -0.063746 | 0.16486 | 0.10178 | 0.092622 | 0.073618 | 0.003172 | 0.057037 | 0.1007 | -0.13876 | -0.095467 | 120.5531 | -0.048576 | 120.5577 | 120.475 | -0.078145 | -0.19192 | 0.036685 | 120.3559 | -0.071137 | 120.544 | 120.4545 | 0.098639 | -0.027474 | -0.26694 | 120.531 | 120.3876 | 120.6162 | 120.526 | -0.02639 | 120.5084 | 120.5521 | 120.3126 | 120.525 | -0.22364
2775.1875 | 120.8908 | -120.6528 | 0.14648 | 1.4211e-13 | -0.024746 | -0.0032223 | -0.0092888 | -0.013687 | 0.012108 | -0.23586 | -0.005247 | 0.01449 | 0.015558 | 0.043371 | 0.0002991 | 0.11093 | 0.070086 | 0.023639 | 0.07502 | -0.059167 | 0.16944 | 0.10178 | 0.097201 | 0.078197 | 0.007751 | 0.052459 | 0.091543 | -0.13419 | -0.077151 | 120.7546 | -0.071464 | 120.7637 | 120.6764 | -0.078145 | -0.20565 | 0.022954 | 120.5756 | -0.094025 | 120.75 | 120.6605 | 0.084902 | -0.054941 | -0.28067 | 120.7278 | 120.5936 | 120.8222 | 120.7229 | -0.0447 | 120.7052 | 120.7443 | 120.5186 | 120.731 | -0.22364
2776.875 | 121.0052 | -120.7169 | 0.12817 | 1.4211e-13 | -0.024746 | -0.0036497 | -0.0092888 | -0.013474 | 0.012108 | -0.23586 | -0.005247 | 0.014063 | 0.015771 | 0.04273 | 0.0005127 | 0.11093 | 0.074664 | 0.01906 | 0.07502 | -0.059167 | 0.17402 | 0.11094 | 0.097201 | 0.073618 | 0.003172 | 0.052459 | 0.091543 | -0.13876 | -0.090888 | 120.8278 | -0.053154 | 120.8278 | 120.7359 | -0.091882 | -0.18734 | 0.045842 | 120.626 | -0.075715 | 120.8141 | 120.72 | 0.09406 | -0.036631 | -0.26694 | 120.7919 | 120.6577 | 120.8909 | 120.7915 | -0.017232 | 120.7693 | 120.8084 | 120.5781 | 120.7905 | -0.21906
2778.625 | 121.0876 | -120.7123 | 0.11902 | 1.4211e-13 | -0.024746 | -0.0032223 | -0.0095024 | -0.01326 | 0.011681 | -0.23586 | -0.0056742 | 0.014277 | 0.015344 | 0.043158 | 8.5502e-05 | 0.11551 | 0.074664 | 0.028217 | 0.084176 | -0.063746 | 0.17402 | 0.10636 | 0.097201 | 0.078197 | 0.003172 | 0.052459 | 0.091543 | -0.13419 | -0.08173 | 120.8186 | -0.034843 | 120.8278 | 120.7405 | -0.078146 | -0.18277 | 0.054997 | 120.6306 | -0.06656 | 120.8095 | 120.7155 | 0.084902 | -0.027476 | -0.25321 | 120.7965 | 120.6485 | 120.8863 | 120.7869 | -0.012656 | 120.7647 | 120.8038 | 120.5781 | 120.7905 | -0.20075
2780.375 | 121.1655 | -120.7764 | 0.11902 | 1.4211e-13 | -0.024746 | -0.0032223 | -0.0092888 | -0.01326 | 0.011895 | -0.23586 | -0.0054606 | 0.01449 | 0.015558 | 0.043158 | 0.0002991 | 0.11551 | 0.070086 | 0.023639 | 0.084176 | -0.054588 | 0.17402 | 0.10636 | 0.092622 | 0.078197 | 0.003172 | 0.052459 | 0.096121 | -0.13419 | -0.090888 | 120.8827 | -0.034843 | 120.8919 | 120.8 | -0.082724 | -0.17361 | 0.054997 | 120.6855 | -0.06656 | 120.869 | 120.7795 | 0.09406 | -0.022898 | -0.25321 | 120.8605 | 120.7218 | 120.9504 | 120.8465 | -0.012656 | 120.8288 | 120.8725 | 120.6422 | 120.8546 | -0.20991
2782.1094 | 121.019 | -120.6894 | 0.13733 | 1.4211e-13 | -0.025173 | -0.0032223 | -0.0090752 | -0.01326 | 0.012108 | -0.24349 | -0.0054606 | 0.014277 | 0.015558 | 0.043585 | 0.0005127 | 0.10177 | 0.060928 | 0.01906 | 0.07502 | -0.059167 | 0.16944 | 0.10178 | 0.097201 | 0.06904 | 0.007751 | 0.057037 | 0.091543 | -0.14334 | -0.090888 | 120.7912 | -0.062309 | 120.7912 | 120.7085 | -0.082724 | -0.1965 | 0.032109 | 120.5985 | -0.080292 | 120.7866 | 120.6971 | 0.098639 | -0.045786 | -0.28067 | 120.7644 | 120.6302 | 120.8588 | 120.7503 | -0.035545 | 120.7464 | 120.7809 | 120.546 | 120.7584 | -0.22822
2783.7969 | 120.9915 | -120.8588 | 0.14191 | 1.4211e-13 | -0.025173 | -0.0038633 | -0.0092888 | -0.013474 | 0.011681 | -0.23586 | -0.0054606 | 0.014063 | 0.015558 | 0.043371 | 0.0005127 | 0.11551 | 0.065507 | 0.01906 | 0.07502 | -0.050009 | 0.16944 | 0.097205 | 0.092622 | 0.06904 | 0.01233 | 0.04788 | 0.096121 | -0.14334 | -0.086309 | 120.956 | -0.066887 | 120.9743 | 120.8778 | -0.078145 | -0.19192 | 0.027531 | 120.7725 | -0.094027 | 120.9514 | 120.8711 | 0.098639 | -0.045786 | -0.28525 | 120.9338 | 120.8088 | 121.0282 | 120.9243 | -0.044702 | 120.9066 | 120.9549 | 120.7154 | 120.9278 | -0.22822
2785.5469 | 121.1929 | -120.8313 | 0.10529 | 1.4211e-13 | -0.025173 | -0.0032223 | -0.0092888 | -0.013046 | 0.011895 | -0.23586 | -0.0054606 | 0.014063 | 0.015558 | 0.043158 | 8.5502e-05 | 0.11093 | 0.070086 | 0.023639 | 0.07502 | -0.063746 | 0.16944 | 0.10178 | 0.092622 | 0.073618 | 0.007751 | 0.04788 | 0.091543 | -0.14334 | -0.090888 | 120.9331 | -0.030266 | 120.9422 | 120.8549 | -0.078145 | -0.16903 | 0.064152 | 120.7404 | -0.057406 | 120.9239 | 120.8391 | 0.098639 | -0.013743 | -0.24863 | 120.9063 | 120.7676 | 121.0007 | 120.9014 | -0.003502 | 120.8792 | 120.9228 | 120.688 | 120.9049 | -0.19617
2787.2969 | 121.2341 | -120.8771 | 0.10071 | 1.4211e-13 | -0.025387 | -0.0030087 | -0.0095024 | -0.013474 | 0.011681 | -0.2206 | -0.0054606 | 0.014277 | 0.015771 | 0.043371 | 0.0002991 | 0.11093 | 0.065507 | 0.01906 | 0.079598 | -0.059167 | 0.17402 | 0.10178 | 0.092622 | 0.06904 | 0.007751 | 0.052459 | 0.096121 | -0.13419 | -0.090888 | 120.9789 | -0.02111 | 120.988 | 120.8961 | -0.082724 | -0.15987 | 0.073308 | 120.7862 | -0.048249 | 120.9697 | 120.8848 | 0.098639 | -0.004587 | -0.23489 | 120.9567 | 120.8179 | 121.0511 | 120.9426 | 0.001076 | 120.9295 | 120.9732 | 120.7429 | 120.9461 | -0.1916
2788.9688 | 120.9778 | -120.8633 | 0.10986 | 1.4211e-13 | -0.025387 | -0.0032223 | -0.0090752 | -0.013474 | 0.011895 | -0.23586 | -0.0050332 | 0.01449 | 0.015558 | 0.043158 | 0.0005127 | 0.11093 | 0.070086 | 0.023639 | 0.079598 | -0.063746 | 0.16944 | 0.10178 | 0.092622 | 0.06904 | 0.007751 | 0.04788 | 0.096121 | -0.12961 | -0.10004 | 120.9651 | -0.030265 | 120.9743 | 120.887 | -0.078145 | -0.17361 | 0.059575 | 120.7633 | -0.061983 | 120.956 | 120.8711 | 0.1078 | -0.013742 | -0.23947 | 120.9429 | 120.7996 | 121.0328 | 120.9334 | -0.008079 | 120.9112 | 120.9595 | 120.7337 | 120.9324 | -0.20991
2790.7188 | 121.2799 | -120.9091 | 0.09613 | 1.4211e-13 | -0.024959 | -0.0032223 | -0.0095024 | -0.01326 | 0.012108 | -0.22823 | -0.005247 | 0.014063 | 0.015344 | 0.043158 | 0.0005127 | 0.11551 | 0.070086 | 0.023639 | 0.07502 | -0.054588 | 0.16944 | 0.11094 | 0.097201 | 0.06904 | 0.003172 | 0.052459 | 0.086964 | -0.13419 | -0.090888 | 121.0201 | -0.02111 | 121.0246 | 120.9328 | -0.087303 | -0.15072 | 0.073308 | 120.8182 | -0.043671 | 121.0063 | 120.9123 | 0.09406 | -0.009166 | -0.23032 | 120.9841 | 120.8545 | 121.0786 | 120.9792 | 0.014812 | 120.9616 | 120.9961 | 120.7749 | 120.9782 | -0.18702
2792.4062 | 121.1746 | -120.9 | 0.10529 | 1.4211e-13 | -0.025387 | -0.0034359 | -0.0097162 | -0.013474 | 0.011681 | -0.24349 | -0.0056742 | 0.014063 | 0.015558 | 0.043585 | 8.5502e-05 | 0.11551 | 0.074664 | 0.01906 | 0.084176 | -0.063746 | 0.17402 | 0.11094 | 0.092622 | 0.064461 | 0.003172 | 0.052459 | 0.096121 | -0.13419 | -0.086309 | 121.0109 | -0.02111 | 121.0155 | 120.919 | -0.091882 | -0.16903 | 0.06873 | 120.8137 | -0.052827 | 120.9926 | 120.9031 | 0.089481 | -0.009165 | -0.23947 | 120.9841 | 120.8362 | 121.074 | 120.9746 | 0.005656 | 120.9524 | 120.9961 | 120.7658 | 120.9644 | -0.1916
2794.0781 | 121.2891 | -120.9549 | 0.11444 | 1.4211e-13 | -0.025173 | -0.0032223 | -0.0092888 | -0.013474 | 0.011681 | -0.23586 | -0.0054606 | 0.014277 | 0.015558 | 0.043371 | 0.0002991 | 0.11093 | 0.060928 | 0.023639 | 0.079598 | -0.059167 | 0.16944 | 0.11094 | 0.092622 | 0.06904 | 0.003172 | 0.04788 | 0.096121 | -0.13419 | -0.10004 | 121.0658 | -0.034843 | 121.0658 | 120.9785 | -0.087303 | -0.17361 | 0.054997 | 120.8548 | -0.066561 | 121.0475 | 120.9581 | 0.10322 | -0.01832 | -0.24863 | 121.0345 | 120.8957 | 121.1243 | 121.0158 | -0.003499 | 121.0028 | 121.051 | 120.8207 | 121.0239 | -0.21449
2795.8281 | 120.9457 | -120.8862 | 0.15564 | 1.4211e-13 | -0.025173 | -0.0034359 | -0.0092888 | -0.013046 | 0.011895 | -0.23586 | -0.005247 | 0.014063 | 0.015558 | 0.043585 | 0.0002991 | 0.11551 | 0.074664 | 0.023639 | 0.084176 | -0.059167 | 0.16944 | 0.1201 | 0.092622 | 0.078197 | 0.007751 | 0.04788 | 0.091543 | -0.13419 | -0.086309 | 121.0063 | -0.071464 | 121.0017 | 120.9099 | -0.096461 | -0.21481 | 0.013798 | 120.7999 | -0.10776 | 120.9789 | 120.894 | 0.09406 | -0.064097 | -0.28983 | 120.9704 | 120.8271 | 121.0557 | 120.9609 | -0.03554 | 120.9341 | 120.9778 | 120.752 | 120.9644 | -0.24195
2797.5781 | 121.3531 | -120.9824 | 0.10986 | 1.4211e-13 | -0.025173 | -0.0032223 | -0.0097162 | -0.013687 | 0.011895 | -0.23586 | -0.005247 | 0.014277 | 0.015558 | 0.043585 | 8.5502e-05 | 0.12009 | 0.070086 | 0.023639 | 0.084176 | -0.054588 | 0.16944 | 0.10636 | 0.092622 | 0.06904 | -0.001407 | 0.057037 | 0.1007 | -0.13419 | -0.090888 | 121.0887 | -0.025687 | 121.1024 | 121.006 | -0.082724 | -0.16445 | 0.059575 | 120.8915 | -0.052826 | 121.075 | 120.981 | 0.089481 | -0.009163 | -0.24405 | 121.0665 | 120.9278 | 121.1518 | 121.0524 | -0.0035 | 121.0394 | 121.0831 | 120.8482 | 121.0514 | -0.20075
2799.2656 | 120.8862 | -120.6619 | 0.15564 | 1.4211e-13 | -0.025387 | -0.0034359 | -0.0095024 | -0.01326 | 0.011895 | -0.24349 | -0.0050332 | 0.014277 | 0.015558 | 0.043585 | 0.0002991 | 0.11551 | 0.060928 | 0.01906 | 0.079598 | -0.059167 | 0.16944 | 0.10636 | 0.10636 | 0.073618 | 0.007751 | 0.061616 | 0.1007 | -0.14334 | -0.095467 | 120.7683 | -0.076042 | 120.7774 | 120.681 | -0.087303 | -0.21481 | 0.013798 | 120.5665 | -0.094024 | 120.7683 | 120.6697 | 0.10322 | -0.05494 | -0.29898 | 120.7415 | 120.6028 | 120.8314 | 120.7229 | -0.049277 | 120.7235 | 120.7626 | 120.5186 | 120.7355 | -0.25111
2800.9531 | 121.1975 | -121.0373 | 0.14191 | 1.4211e-13 | -0.025814 | -0.0036497 | -0.0095024 | -0.01326 | 0.011895 | -0.24349 | -0.005247 | 0.014063 | 0.015344 | 0.043585 | 0.0002991 | 0.11093 | 0.065507 | 0.023639 | 0.079598 | -0.054588 | 0.16944 | 0.11552 | 0.097201 | 0.06904 | 0.007751 | 0.057037 | 0.096121 | -0.13876 | -0.095467 | 121.1528 | -0.062309 | 121.1482 | 121.0609 | -0.091882 | -0.1965 | 0.027531 | 120.9418 | -0.08487 | 121.1345 | 121.045 | 0.10322 | -0.045786 | -0.28067 | 121.1169 | 120.9827 | 121.2067 | 121.1028 | -0.026386 | 121.0943 | 121.1334 | 120.8985 | 121.1063 | -0.23737
2802.7188 | 120.7993 | -120.3415 | 0.1236 | 1.4211e-13 | -0.025814 | -0.0032223 | -0.0097162 | -0.013474 | 0.011895 | -0.23586 | -0.0054606 | 0.014063 | 0.015558 | 0.043585 | 0.0005127 | 0.11551 | 0.065507 | 0.028217 | 0.088755 | -0.054588 | 0.16944 | 0.10178 | 0.092622 | 0.073618 | 0.007751 | 0.057037 | 0.091543 | -0.13876 | -0.095467 | 120.4433 | -0.034841 | 120.457 | 120.3697 | -0.073567 | -0.17818 | 0.045842 | 120.246 | -0.066559 | 120.4341 | 120.3492 | 0.10322 | -0.032053 | -0.26236 | 120.4302 | 120.2869 | 120.5109 | 120.407 | -0.021812 | 120.3985 | 120.433 | 120.2027 | 120.4151 | -0.21906
2804.4062 | 121.225 | -121.0281 | 0.16022 | 1.4211e-13 | -0.0256 | -0.0034359 | -0.0097162 | -0.013046 | 0.011895 | -0.23586 | -0.0050332 | 0.014277 | 0.015558 | 0.043799 | 8.5502e-05 | 0.11551 | 0.065507 | 0.023639 | 0.084176 | -0.063746 | 0.16028 | 0.10178 | 0.092622 | 0.073618 | -0.001407 | 0.04788 | 0.096121 | -0.13419 | -0.090888 | 121.1299 | -0.076041 | 121.1436 | 121.0518 | -0.078145 | -0.22396 | 6.3e-05 | 120.9372 | -0.11234 | 121.1208 | 121.0267 | 0.089481 | -0.064096 | -0.2944 | 121.1123 | 120.9644 | 121.1884 | 121.0936 | -0.058433 | 121.076 | 121.1243 | 120.894 | 121.1018 | -0.25111
2806.0938 | 121.3852 | -121.0602 | 0.10986 | 1.4211e-13 | -0.025814 | -0.0034359 | -0.0095024 | -0.013474 | 0.011895 | -0.23586 | -0.0048196 | 0.013849 | 0.015558 | 0.043799 | 8.5502e-05 | 0.12009 | 0.074664 | 0.032795 | 0.07502 | -0.059167 | 0.16486 | 0.11094 | 0.097201 | 0.06904 | 0.003172 | 0.057037 | 0.10528 | -0.12961 | -0.095467 | 121.1711 | -0.034843 | 121.1803 | 121.093 | -0.078147 | -0.16903 | 0.054996 | 120.9647 | -0.052826 | 121.1574 | 121.0634 | 0.098639 | -0.004584 | -0.23947 | 121.1352 | 121.001 | 121.225 | 121.1348 | 0.001079 | 121.1172 | 121.1655 | 120.9306 | 121.1292 | -0.20533
2807.8438 | 121.376 | -121.1197 | 0.11444 | 1.4211e-13 | -0.0256 | -0.0036497 | -0.0095024 | -0.01326 | 0.011467 | -0.23586 | -0.0054606 | 0.014063 | 0.015558 | 0.043799 | 0.0002991 | 0.12009 | 0.074664 | 0.032795 | 0.084176 | -0.059167 | 0.16944 | 0.10636 | 0.10178 | 0.073618 | 0.003172 | 0.04788 | 0.096121 | -0.13419 | -0.090888 | 121.2261 | -0.030265 | 121.2398 | 121.1525 | -0.073568 | -0.17361 | 0.054997 | 121.0288 | -0.066561 | 121.2215 | 121.1229 | 0.09406 | -0.01832 | -0.24863 | 121.2039 | 121.0605 | 121.2891 | 121.1944 | -0.008078 | 121.1676 | 121.2158 | 120.9855 | 121.1933 | -0.20533
2809.6094 | 121.3989 | -121.0922 | 0.11444 | 1.4211e-13 | -0.0256 | -0.0030087 | -0.0095024 | -0.01326 | 0.011681 | -0.23586 | -0.0050332 | 0.014063 | 0.015344 | 0.043799 | -0.0001281 | 0.12009 | 0.074664 | 0.037373 | 0.07502 | -0.059167 | 0.16944 | 0.10636 | 0.092622 | 0.06904 | -0.001407 | 0.04788 | 0.096121 | -0.13419 | -0.090888 | 121.1986 | -0.039421 | 121.2123 | 121.1296 | -0.06899 | -0.17361 | 0.054997 | 121.0013 | -0.066561 | 121.1848 | 121.0908 | 0.089481 | -0.01832 | -0.24863 | 121.1672 | 121.0331 | 121.2617 | 121.1669 | -0.008078 | 121.1401 | 121.1883 | 120.958 | 121.1613 | -0.20533
2811.2969 | 121.2936 | -120.9732 | 0.14648 | 1.4211e-13 | -0.025173 | -0.0032223 | -0.0088614 | -0.013046 | 0.011895 | -0.22823 | -0.0054606 | 0.014277 | 0.015344 | 0.044012 | 8.5502e-05 | 0.12009 | 0.074664 | 0.037373 | 0.079598 | -0.059167 | 0.17402 | 0.10178 | 0.10178 | 0.078197 | 0.003172 | 0.04788 | 0.091543 | -0.13419 | -0.095467 | 121.075 | -0.066886 | 121.0933 | 121.0106 | -0.064411 | -0.20565 | 0.027532 | 120.8777 | -0.098604 | 121.075 | 120.9764 | 0.098639 | -0.054941 | -0.28067 | 121.0528 | 120.914 | 121.1472 | 121.0479 | -0.0447 | 121.0211 | 121.0647 | 120.839 | 121.0514 | -0.24195
2813.0469 | 121.4264 | -121.1472 | 0.12817 | 1.4211e-13 | -0.025814 | -0.0036497 | -0.0095024 | -0.013474 | 0.011895 | -0.22823 | -0.0050332 | 0.014063 | 0.015344 | 0.043799 | 0.0002991 | 0.12009 | 0.074664 | 0.028217 | 0.084176 | -0.059167 | 0.17402 | 0.10636 | 0.097201 | 0.06904 | 0.007751 | 0.057037 | 0.1007 | -0.14334 | -0.095467 | 121.2535 | -0.043998 | 121.2672 | 121.1754 | -0.078146 | -0.18734 | 0.045842 | 121.0517 | -0.071137 | 121.2444 | 121.1549 | 0.10322 | -0.027474 | -0.27152 | 121.2313 | 121.088 | 121.3212 | 121.2218 | -0.021811 | 121.2042 | 121.2479 | 121.0038 | 121.2162 | -0.22364
2814.8125 | 121.3486 | -121.0098 | 0.13275 | 1.4211e-13 | -0.025814 | -0.0034359 | -0.0095024 | -0.013474 | 0.011681 | -0.23586 | -0.0058878 | 0.014063 | 0.015558 | 0.044012 | -0.0001281 | 0.12466 | 0.074664 | 0.037373 | 0.084176 | -0.063746 | 0.17402 | 0.10636 | 0.092622 | 0.06904 | 0.007751 | 0.057037 | 0.1007 | -0.12961 | -0.090888 | 121.1162 | -0.048575 | 121.1345 | 121.0472 | -0.06899 | -0.1965 | 0.041265 | 120.9189 | -0.075714 | 121.1024 | 121.0176 | 0.098639 | -0.032051 | -0.26236 | 121.094 | 120.9461 | 121.1838 | 121.0845 | -0.026388 | 121.0669 | 121.1105 | 120.8802 | 121.0789 | -0.22364
2816.4844 | 121.4813 | -121.138 | 0.10529 | 1.4211e-13 | -0.0256 | -0.0030087 | -0.0095024 | -0.01326 | 0.011681 | -0.25112 | -0.005247 | 0.014063 | 0.015558 | 0.044012 | -0.0001281 | 0.12009 | 0.074664 | 0.032795 | 0.088755 | -0.059167 | 0.1786 | 0.10636 | 0.097201 | 0.06904 | -0.005985 | 0.057037 | 0.10528 | -0.13419 | -0.095467 | 121.2444 | -0.016531 | 121.2581 | 121.1708 | -0.073568 | -0.16445 | 0.073309 | 121.0425 | -0.048249 | 121.2352 | 121.132 | 0.089482 | -7e-06 | -0.23947 | 121.2268 | 121.0788 | 121.3166 | 121.2127 | 0.001077 | 121.195 | 121.2433 | 121.0038 | 121.207 | -0.20075
2818.2344 | 121.4218 | -121.1563 | 0.14191 | 1.4211e-13 | -0.025814 | -0.0034359 | -0.0095024 | -0.01326 | 0.011467 | -0.23586 | -0.0054606 | 0.014063 | 0.01513 | 0.043799 | 8.5502e-05 | 0.11551 | 0.074664 | 0.037373 | 0.084176 | -0.059167 | 0.17402 | 0.10636 | 0.097201 | 0.073618 | -0.001407 | 0.057037 | 0.096121 | -0.13419 | -0.090888 | 121.2627 | -0.057731 | 121.2718 | 121.1937 | -0.06899 | -0.20107 | 0.032109 | 121.0654 | -0.08487 | 121.2535 | 121.1549 | 0.089481 | -0.045786 | -0.27609 | 121.2405 | 121.0971 | 121.3303 | 121.231 | -0.035544 | 121.2133 | 121.2524 | 121.0221 | 121.2299 | -0.2328
2819.9375 | 121.3806 | -121.2021 | 0.15564 | 1.4211e-13 | -0.026028 | -0.0036497 | -0.0097162 | -0.013474 | 0.012108 | -0.23586 | -0.005247 | 0.01449 | 0.015558 | 0.043585 | 0.0002991 | 0.12009 | 0.065507 | 0.032795 | 0.084176 | -0.063746 | 0.1786 | 0.11094 | 0.097201 | 0.06904 | -0.001407 | 0.052459 | 0.096121 | -0.13876 | -0.10004 | 121.313 | -0.071464 | 121.3222 | 121.2349 | -0.078147 | -0.21939 | 0.022955 | 121.102 | -0.10318 | 121.2993 | 121.2007 | 0.098638 | -0.059519 | -0.29441 | 121.2863 | 121.1383 | 121.3807 | 121.2676 | -0.044698 | 121.2545 | 121.2982 | 121.0633 | 121.2711 | -0.25568
2821.6719 | 121.3898 | -121.2433 | 0.14648 | 1.4211e-13 | -0.0256 | -0.0032223 | -0.0095024 | -0.013474 | 0.011681 | -0.23586 | -0.0054606 | 0.014277 | 0.01513 | 0.043585 | 8.5502e-05 | 0.12009 | 0.070086 | 0.037373 | 0.079598 | -0.063746 | 0.16944 | 0.10636 | 0.097201 | 0.06904 | 0.003172 | 0.052459 | 0.091543 | -0.13419 | -0.095467 | 121.3496 | -0.066886 | 121.3634 | 121.2807 | -0.06899 | -0.21023 | 0.022954 | 121.1478 | -0.094025 | 121.3405 | 121.2465 | 0.098639 | -0.054941 | -0.28067 | 121.3229 | 121.1795 | 121.4127 | 121.3134 | -0.040121 | 121.2957 | 121.3348 | 121.1091 | 121.3123 | -0.24195
2823.3438 | 121.4172 | -121.1929 | 0.14648 | 1.4211e-13 | -0.0256 | -0.0034359 | -0.0095024 | -0.013474 | 0.011681 | -0.23586 | -0.005247 | 0.01449 | 0.01513 | 0.043585 | 8.5502e-05 | 0.12466 | 0.070086 | 0.028217 | 0.084176 | -0.054588 | 0.17402 | 0.10636 | 0.092622 | 0.06904 | 0.003172 | 0.043302 | 0.10528 | -0.13876 | -0.095467 | 121.2993 | -0.062308 | 121.3176 | 121.2211 | -0.078146 | -0.20107 | 0.027532 | 121.0975 | -0.10318 | 121.2856 | 121.1961 | 0.098639 | -0.041205 | -0.28525 | 121.2771 | 121.1383 | 121.3669 | 121.263 | -0.040121 | 121.2362 | 121.2982 | 121.0542 | 121.262 | -0.24195
2825.0312 | 121.5683 | -121.1975 | 0.11902 | 1.4211e-13 | -0.025814 | -0.0032223 | -0.0095024 | -0.013687 | 0.011681 | -0.22823 | -0.005247 | 0.014704 | 0.015344 | 0.044012 | 8.5502e-05 | 0.12466 | 0.070086 | 0.037373 | 0.084176 | -0.059167 | 0.16944 | 0.10636 | 0.092622 | 0.064461 | 0.003172 | 0.052459 | 0.1007 | -0.13876 | -0.095467 | 121.3039 | -0.034843 | 121.3222 | 121.2349 | -0.06899 | -0.17819 | 0.050419 | 121.102 | -0.06656 | 121.2901 | 121.2007 | 0.098639 | -0.018319 | -0.25778 | 121.2817 | 121.1383 | 121.3669 | 121.2676 | -0.012656 | 121.25 | 121.2982 | 121.0587 | 121.262 | -0.21449
2826.7812 | 121.4676 | -121.2204 | 0.14648 | 1.4211e-13 | -0.025814 | -0.0034359 | -0.0095024 | -0.013687 | 0.011681 | -0.2206 | -0.005247 | 0.014063 | 0.01513 | 0.043585 | 8.5502e-05 | 0.12466 | 0.070086 | 0.037373 | 0.079598 | -0.063746 | 0.16944 | 0.10636 | 0.092622 | 0.064461 | 0.003172 | 0.04788 | 0.1007 | -0.13419 | -0.086309 | 121.3268 | -0.066886 | 121.3451 | 121.2578 | -0.06899 | -0.21023 | 0.022954 | 121.1341 | -0.098604 | 121.313 | 121.2236 | 0.089481 | -0.045784 | -0.28067 | 121.3 | 121.1567 | 121.3898 | 121.2905 | -0.040121 | 121.2683 | 121.3211 | 121.0862 | 121.2849 | -0.23279
2828.5156 | 121.55 | -121.2204 | 0.1236 | 1.4211e-13 | -0.026028 | -0.0038633 | -0.0095024 | -0.01326 | 0.011467 | -0.23586 | -0.0050332 | 0.013849 | 0.015344 | 0.043799 | -0.0001281 | 0.12009 | 0.065507 | 0.04653 | 0.084176 | -0.054588 | 0.16944 | 0.10636 | 0.097201 | 0.073618 | 0.007751 | 0.052459 | 0.091543 | -0.13876 | -0.086309 | 121.3268 | -0.03942 | 121.3405 | 121.2669 | -0.059833 | -0.17818 | 0.045842 | 121.1341 | -0.071137 | 121.3176 | 121.2281 | 0.09406 | -0.032053 | -0.26236 | 121.3046 | 121.1658 | 121.3898 | 121.2859 | -0.017233 | 121.2729 | 121.3119 | 121.0816 | 121.294 | -0.20991
2830.2656 | 121.2387 | -121.0373 | 0.15106 | 1.4211e-13 | -0.025814 | -0.0032223 | -0.0099298 | -0.013474 | 0.011254 | -0.22823 | -0.0056742 | 0.014063 | 0.01513 | 0.044012 | 0.0002991 | 0.12466 | 0.074664 | 0.037373 | 0.084176 | -0.059167 | 0.18317 | 0.11094 | 0.097201 | 0.078197 | 0.007751 | 0.052459 | 0.086964 | -0.14334 | -0.095467 | 121.1482 | -0.066886 | 121.162 | 121.0747 | -0.073569 | -0.21023 | 0.032111 | 120.9418 | -0.098603 | 121.1345 | 121.045 | 0.10322 | -0.064098 | -0.29441 | 121.1215 | 120.9781 | 121.2205 | 121.112 | -0.04012 | 121.0898 | 121.1243 | 120.8939 | 121.1155 | -0.24653
2831.9375 | 121.5042 | -121.1197 | 0.10071 | 1.4211e-13 | -0.026028 | -0.0036497 | -0.0097162 | -0.01326 | 0.011895 | -0.24349 | -0.0054606 | 0.014063 | 0.015344 | 0.044012 | 8.5502e-05 | 0.12466 | 0.074664 | 0.041952 | 0.079598 | -0.063746 | 0.16944 | 0.10178 | 0.088043 | 0.073618 | -0.001407 | 0.052459 | 0.096121 | -0.13419 | -0.10004 | 121.2215 | -0.02111 | 121.2444 | 121.1616 | -0.059832 | -0.16445 | 0.06873 | 121.0196 | -0.048249 | 121.2077 | 121.1183 | 0.098638 | -0.004587 | -0.23489 | 121.1993 | 121.0559 | 121.2891 | 121.1944 | 0.001076 | 121.1721 | 121.2158 | 120.9855 | 121.1933 | -0.20075
2833.625 | 121.2936 | -120.8908 | 0.11444 | 1.4211e-13 | -0.026028 | -0.0034359 | -0.0095024 | -0.013687 | 0.011681 | -0.23586 | -0.005247 | 0.014277 | 0.014917 | 0.044012 | 0.0005127 | 0.12009 | 0.065507 | 0.041952 | 0.079598 | -0.059167 | 0.17402 | 0.083468 | 0.092622 | 0.064461 | -0.005985 | 0.057037 | 0.1007 | -0.13419 | -0.090888 | 120.9743 | -0.034843 | 121.0109 | 120.9328 | -0.041516 | -0.17361 | 0.059575 | 120.7999 | -0.057404 | 120.9834 | 120.8848 | 0.084903 | -0.013741 | -0.24863 | 120.9704 | 120.8316 | 121.0648 | 120.9563 | -0.030973 | 120.9478 | 120.9915 | 120.7566 | 120.9553 | -0.20533
2835.375 | 121.1563 | -120.8633 | 0.12817 | 1.4211e-13 | -0.026241 | -0.0036497 | -0.0090752 | -0.013474 | 0.011681 | -0.24349 | -0.0054606 | 0.014277 | 0.015344 | 0.043799 | 8.5502e-05 | 0.12466 | 0.074664 | 0.04653 | 0.088755 | -0.059167 | 0.17402 | 0.11094 | 0.092622 | 0.06904 | 0.003172 | 0.052459 | 0.10528 | -0.13419 | -0.090888 | 120.9743 | -0.039419 | 120.988 | 120.9099 | -0.064412 | -0.18734 | 0.045842 | 120.7725 | -0.075715 | 120.956 | 120.8665 | 0.09406 | -0.022895 | -0.26236 | 120.9521 | 120.8042 | 121.0374 | 120.938 | -0.017232 | 120.9158 | 120.9686 | 120.7292 | 120.9324 | -0.21906
2837.0469 | 121.2982 | -120.9869 | 0.11902 | 1.4211e-13 | -0.026028 | -0.0032223 | -0.0095024 | -0.013687 | 0.011467 | -0.25112 | -0.0054606 | 0.013849 | 0.014917 | 0.044226 | 0.0002991 | 0.12924 | 0.070086 | 0.051108 | 0.088755 | -0.059167 | 0.16944 | 0.10636 | 0.097201 | 0.06904 | 0.01233 | 0.057037 | 0.091543 | -0.13419 | -0.095467 | 121.0933 | -0.030264 | 121.1162 | 121.038 | -0.055255 | -0.17819 | 0.050419 | 120.8915 | -0.061982 | 121.0841 | 120.9993 | 0.1078 | -0.027476 | -0.25321 | 121.0757 | 120.9278 | 121.1564 | 121.057 | -0.012656 | 121.044 | 121.0785 | 120.8528 | 121.056 | -0.21449
2838.7969 | 120.9778 | -120.7214 | 0.13733 | 1.4211e-13 | -0.026241 | -0.0036497 | -0.0095024 | -0.013687 | 0.011681 | -0.23586 | -0.005247 | 0.013849 | 0.01513 | 0.044226 | 8.5502e-05 | 0.12924 | 0.074664 | 0.04653 | 0.088755 | -0.063746 | 0.1786 | 0.10178 | 0.092622 | 0.06904 | 0.007751 | 0.052459 | 0.096121 | -0.13876 | -0.10004 | 120.8232 | -0.048574 | 120.8507 | 120.768 | -0.055254 | -0.20108 | 0.041266 | 120.6214 | -0.08487 | 120.8141 | 120.7292 | 0.1078 | -0.041208 | -0.27609 | 120.8102 | 120.6577 | 120.9 | 120.7961 | -0.035545 | 120.7739 | 120.8176 | 120.5827 | 120.7905 | -0.23737
2840.5469 | 120.9137 | -120.6802 | 0.12817 | 1.4211e-13 | -0.026241 | -0.0036497 | -0.0097162 | -0.013687 | 0.011681 | -0.23586 | -0.0054606 | 0.014063 | 0.015558 | 0.044012 | 0.0005127 | 0.12924 | 0.074664 | 0.04653 | 0.079598 | -0.059167 | 0.16944 | 0.10636 | 0.088043 | 0.06904 | -0.001407 | 0.052459 | 0.091543 | -0.13419 | -0.095467 | 120.7866 | -0.048576 | 120.8095 | 120.7268 | -0.059833 | -0.18734 | 0.041264 | 120.5848 | -0.075715 | 120.7683 | 120.6788 | 0.09406 | -0.036631 | -0.26236 | 120.7598 | 120.6211 | 120.8497 | 120.7549 | -0.021811 | 120.7327 | 120.7718 | 120.5461 | 120.7493 | -0.22364
2842.25 | 121.2433 | -120.8862 | 0.10529 | 1.4211e-13 | -0.026241 | -0.0036497 | -0.0095024 | -0.013687 | 0.011681 | -0.22823 | -0.0050332 | 0.014277 | 0.015344 | 0.044226 | 0.0002991 | 0.12009 | 0.060928 | 0.04653 | 0.079598 | -0.054588 | 0.16944 | 0.10178 | 0.097201 | 0.06904 | 0.003172 | 0.052459 | 0.096121 | -0.13419 | -0.090888 | 120.988 | -0.025688 | 121.0063 | 120.9328 | -0.055254 | -0.15987 | 0.064152 | 120.7953 | -0.052827 | 120.9834 | 120.8894 | 0.09406 | -0.009165 | -0.23947 | 120.9658 | 120.8316 | 121.0557 | 120.9472 | -0.003502 | 120.9387 | 120.9824 | 120.752 | 120.9553 | -0.19617
2844 | 121.1838 | -120.9961 | 0.11902 | 1.4211e-13 | -0.026241 | -0.0038633 | -0.0092888 | -0.014115 | 0.011467 | -0.22823 | -0.0056742 | 0.014063 | 0.01513 | 0.044226 | 8.5502e-05 | 0.12466 | 0.079243 | 0.041952 | 0.093333 | -0.063746 | 0.16486 | 0.10178 | 0.092622 | 0.073618 | 0.01233 | 0.057037 | 0.091543 | -0.12961 | -0.090888 | 121.0979 | -0.025686 | 121.1208 | 121.038 | -0.059832 | -0.18277 | 0.04584 | 120.9052 | -0.061982 | 121.0887 | 121.0084 | 0.10322 | -0.027476 | -0.24863 | 121.0894 | 120.9323 | 121.161 | 121.0753 | -0.017235 | 121.0531 | 121.0876 | 120.8665 | 121.0697 | -0.20991
2845.6875 | 121.312 | -121.0144 | 0.082397 | 1.4211e-13 | -0.026669 | -0.0036497 | -0.0097162 | -0.013901 | 0.011254 | -0.22823 | -0.0054606 | 0.014063 | 0.014917 | 0.04444 | 8.5502e-05 | 0.12466 | 0.065507 | 0.051108 | 0.088755 | -0.059167 | 0.17402 | 0.10178 | 0.097201 | 0.06904 | 0.007751 | 0.052459 | 0.091543 | -0.13876 | -0.10004 | 121.1162 | 0.006358 | 121.1391 | 121.0655 | -0.050676 | -0.14156 | 0.091619 | 120.9144 | -0.029938 | 121.1116 | 121.0222 | 0.1078 | 0.009146 | -0.22116 | 121.1032 | 120.9552 | 121.1884 | 121.0799 | 0.019387 | 121.0669 | 121.1059 | 120.8756 | 121.0834 | -0.18244
2847.4219 | 121.2662 | -121.0648 | 0.13275 | 1.4211e-13 | -0.026241 | -0.0036497 | -0.0095024 | -0.013687 | 0.011681 | -0.23586 | -0.0054606 | 0.014277 | 0.015344 | 0.044012 | -0.0001281 | 0.12924 | 0.060928 | 0.04653 | 0.079598 | -0.054588 | 0.17402 | 0.10636 | 0.097201 | 0.064461 | -0.001407 | 0.052459 | 0.1007 | -0.13876 | -0.095467 | 121.1711 | -0.053153 | 121.194 | 121.1113 | -0.059833 | -0.18734 | 0.041265 | 120.9693 | -0.080292 | 121.162 | 121.0634 | 0.09406 | -0.032051 | -0.27152 | 121.1444 | 121.0102 | 121.2388 | 121.1257 | -0.026388 | 121.1172 | 121.1655 | 120.926 | 121.1292 | -0.22822
2849.1562 | 121.2662 | -121.0739 | 0.11902 | 1.4211e-13 | -0.026669 | -0.0032223 | -0.0095024 | -0.01326 | 0.011681 | -0.22823 | -0.0054606 | 0.014063 | 0.01513 | 0.04444 | 0.0002991 | 0.13382 | 0.079243 | 0.04653 | 0.079598 | -0.063746 | 0.17402 | 0.10636 | 0.10178 | 0.06904 | 0.007751 | 0.061616 | 0.1007 | -0.13876 | -0.10004 | 121.1803 | -0.039421 | 121.2077 | 121.1204 | -0.059833 | -0.18277 | 0.054997 | 120.9739 | -0.057403 | 121.1757 | 121.0817 | 0.1078 | -0.018319 | -0.25778 | 121.1535 | 121.0102 | 121.2479 | 121.1532 | -0.012656 | 121.1355 | 121.1746 | 120.9351 | 121.143 | -0.21906
2850.9062 | 121.4127 | -121.0602 | 0.091553 | 1.4211e-13 | -0.026669 | -0.0034359 | -0.0095024 | -0.013474 | 0.011895 | -0.22823 | -0.0050332 | 0.013849 | 0.01513 | 0.04444 | 0.0002991 | 0.12924 | 0.060928 | 0.041952 | 0.084176 | -0.059167 | 0.17402 | 0.10178 | 0.088043 | 0.064461 | 0.003172 | 0.057037 | 0.096121 | -0.13876 | -0.095467 | 121.162 | -0.007377 | 121.1894 | 121.1021 | -0.059832 | -0.15072 | 0.082463 | 120.9647 | -0.034516 | 121.1482 | 121.0634 | 0.098639 | 0.004568 | -0.23032 | 121.1444 | 121.001 | 121.2342 | 121.1211 | 0.010231 | 121.1172 | 121.1563 | 120.9214 | 121.1246 | -0.18702
2852.6562 | 121.3303 | -121.1014 | 0.13275 | 1.4211e-13 | -0.026669 | -0.0032223 | -0.0095024 | -0.013474 | 0.011467 | -0.24349 | -0.0054606 | 0.013849 | 0.015344 | 0.04444 | 8.5502e-05 | 0.12924 | 0.065507 | 0.04653 | 0.084176 | -0.054588 | 0.17402 | 0.10178 | 0.092622 | 0.064461 | 0.003172 | 0.052459 | 0.096121 | -0.13876 | -0.090888 | 121.2032 | -0.048575 | 121.2306 | 121.1479 | -0.055254 | -0.18734 | 0.041265 | 121.0105 | -0.080292 | 121.194 | 121.1046 | 0.09406 | -0.03663 | -0.27152 | 121.1856 | 121.0468 | 121.2754 | 121.1669 | -0.030967 | 121.1538 | 121.1975 | 120.9626 | 121.1658 | -0.22364
2854.3438 | 121.3715 | -121.0327 | 0.11444 | 1.4211e-13 | -0.026241 | -0.0030087 | -0.0097162 | -0.013474 | 0.011254 | -0.22823 | -0.005247 | 0.013636 | 0.015344 | 0.044012 | -0.0001281 | 0.12009 | 0.070086 | 0.051108 | 0.079598 | -0.059167 | 0.1786 | 0.10178 | 0.097201 | 0.06904 | 0.003172 | 0.052459 | 0.091543 | -0.13876 | -0.095467 | 121.1345 | -0.034843 | 121.1528 | 121.0838 | -0.050676 | -0.17361 | 0.064154 | 120.9372 | -0.061982 | 121.1299 | 121.0359 | 0.098639 | -0.022898 | -0.25321 | 121.1123 | 120.9735 | 121.2113 | 121.1028 | -0.012657 | 121.0852 | 121.1243 | 120.8939 | 121.1018 | -0.20991
2856.0938 | 121.2936 | -121.0922 | 0.15106 | 1.4211e-13 | -0.026455 | -0.0034359 | -0.0092888 | -0.013901 | 0.011681 | -0.22823 | -0.0056742 | 0.013849 | 0.01513 | 0.04444 | 8.5502e-05 | 0.13382 | 0.083821 | 0.060265 | 0.093333 | -0.054588 | 0.1786 | 0.10178 | 0.097201 | 0.082776 | 0.007751 | 0.057037 | 0.1007 | -0.13876 | -0.095467 | 121.194 | -0.057729 | 121.226 | 121.1525 | -0.041519 | -0.20565 | 0.027533 | 120.9968 | -0.094025 | 121.1894 | 121.1 | 0.10322 | -0.050362 | -0.28983 | 121.1856 | 121.0376 | 121.2708 | 121.176 | -0.049278 | 121.1493 | 121.1929 | 120.9535 | 121.175 | -0.24653
2857.8438 | 121.3165 | -121.1655 | 0.14648 | 1.4211e-13 | -0.026669 | -0.0034359 | -0.0095024 | -0.013474 | 0.011895 | -0.23586 | -0.005247 | 0.014277 | 0.015344 | 0.04444 | 8.5502e-05 | 0.12466 | 0.070086 | 0.055687 | 0.088755 | -0.063746 | 0.1786 | 0.10636 | 0.097201 | 0.073618 | 0.003172 | 0.052459 | 0.096121 | -0.13419 | -0.095467 | 121.2718 | -0.057729 | 121.2901 | 121.2212 | -0.050676 | -0.21023 | 0.032111 | 121.07 | -0.094025 | 121.2627 | 121.1686 | 0.098639 | -0.050363 | -0.28067 | 121.2542 | 121.1017 | 121.3441 | 121.2356 | -0.040121 | 121.2179 | 121.2616 | 121.0313 | 121.2391 | -0.24195
2859.5156 | 121.4218 | -121.1197 | 0.11444 | 1.4211e-13 | -0.027096 | -0.0032223 | -0.0097162 | -0.013687 | 0.011681 | -0.23586 | -0.0054606 | 0.014277 | 0.01513 | 0.044226 | -0.0001281 | 0.12466 | 0.070086 | 0.055687 | 0.084176 | -0.059167 | 0.1786 | 0.10636 | 0.092622 | 0.073618 | -0.001407 | 0.057037 | 0.096121 | -0.14792 | -0.090888 | 121.2261 | -0.030265 | 121.2444 | 121.1754 | -0.050676 | -0.17361 | 0.064154 | 121.0288 | -0.057404 | 121.2123 | 121.1183 | 0.089481 | -0.01832 | -0.26236 | 121.2039 | 121.0605 | 121.2983 | 121.1898 | -0.008078 | 121.1767 | 121.2158 | 120.9718 | 121.1933 | -0.20533
2861.2656 | 121.3577 | -121.17 | 0.15564 | 1.4211e-13 | -0.026882 | -0.0034359 | -0.0097162 | -0.013687 | 0.011681 | -0.23586 | -0.0050332 | 0.013849 | 0.01513 | 0.044012 | -0.0003419 | 0.12009 | 0.070086 | 0.060265 | 0.088755 | -0.059167 | 0.1786 | 0.10636 | 0.10636 | 0.073618 | 0.003172 | 0.052459 | 0.1007 | -0.13876 | -0.10004 | 121.2764 | -0.066885 | 121.2901 | 121.2303 | -0.046098 | -0.21481 | 0.022955 | 121.07 | -0.10318 | 121.2764 | 121.1732 | 0.10322 | -0.05494 | -0.29441 | 121.2588 | 121.1109 | 121.3486 | 121.2401 | -0.049277 | 121.2225 | 121.2707 | 121.0313 | 121.2437 | -0.25568
2863 | 121.4859 | -121.1563 | 0.10529 | 1.4211e-13 | -0.026882 | -0.0034359 | -0.0095024 | -0.013901 | 0.011467 | -0.23586 | -0.005247 | 0.014063 | 0.01513 | 0.044653 | -0.0001281 | 0.12009 | 0.070086 | 0.060265 | 0.084176 | -0.063746 | 0.16944 | 0.097205 | 0.10178 | 0.073618 | 0.003172 | 0.052459 | 0.10528 | -0.13419 | -0.10004 | 121.2535 | -0.02111 | 121.2764 | 121.2166 | -0.03694 | -0.16903 | 0.064152 | 121.0563 | -0.052827 | 121.2581 | 121.1595 | 0.10322 | -7e-06 | -0.23947 | 121.2405 | 121.0926 | 121.3257 | 121.2264 | -0.008081 | 121.2088 | 121.2616 | 121.0221 | 121.2299 | -0.20533
2864.75 | 121.4539 | -121.1792 | 0.11902 | 1.4211e-13 | -0.026882 | -0.0034359 | -0.0095024 | -0.013901 | 0.011895 | -0.23586 | -0.005247 | 0.013636 | 0.01513 | 0.044653 | 0.0002991 | 0.12466 | 0.079243 | 0.051108 | 0.093333 | -0.059167 | 0.1786 | 0.097205 | 0.097201 | 0.078197 | 0.007751 | 0.057037 | 0.1007 | -0.13419 | -0.10462 | 121.2764 | -0.025686 | 121.3039 | 121.2303 | -0.046097 | -0.17819 | 0.059576 | 121.0746 | -0.061982 | 121.2764 | 121.1869 | 0.11237 | -0.018319 | -0.25321 | 121.2725 | 121.12 | 121.3578 | 121.2584 | -0.021814 | 121.2362 | 121.2799 | 121.045 | 121.2574 | -0.22364
2866.4375 | 121.4081 | -121.2204 | 0.1236 | 1.4211e-13 | -0.026455 | -0.0034359 | -0.0097162 | -0.013687 | 0.011254 | -0.23586 | -0.0056742 | 0.014063 | 0.01513 | 0.044653 | 8.5502e-05 | 0.12466 | 0.074664 | 0.055687 | 0.084176 | -0.059167 | 0.17402 | 0.10178 | 0.097201 | 0.073618 | 0.003172 | 0.04788 | 0.1007 | -0.13876 | -0.095467 | 121.3222 | -0.03942 | 121.3451 | 121.2761 | -0.046097 | -0.18276 | 0.05042 | 121.1249 | -0.075716 | 121.3176 | 121.2236 | 0.098639 | -0.022896 | -0.26236 | 121.3046 | 121.1612 | 121.3944 | 121.2951 | -0.021812 | 121.2683 | 121.3211 | 121.0816 | 121.294 | -0.21906
2868.1875 | 121.3943 | -121.2387 | 0.15564 | 1.4211e-13 | -0.026882 | -0.0038633 | -0.0095024 | -0.013901 | 0.011467 | -0.23586 | -0.0054606 | 0.014063 | 0.01513 | 0.04444 | -0.0001281 | 0.12924 | 0.079243 | 0.055687 | 0.088755 | -0.054588 | 0.16944 | 0.10178 | 0.10178 | 0.06904 | 0.007751 | 0.057037 | 0.096121 | -0.13876 | -0.090888 | 121.3405 | -0.066885 | 121.368 | 121.2944 | -0.046097 | -0.21023 | 0.013798 | 121.1478 | -0.098603 | 121.3405 | 121.2465 | 0.098639 | -0.059519 | -0.29441 | 121.3275 | 121.1841 | 121.4081 | 121.318 | -0.053856 | 121.2957 | 121.3348 | 121.0999 | 121.3077 | -0.24653
2869.9219 | 121.4584 | -121.225 | 0.1236 | 1.4211e-13 | -0.026882 | -0.0034359 | -0.0097162 | -0.013687 | 0.011467 | -0.22823 | -0.005247 | 0.013849 | 0.01513 | 0.044867 | 8.5502e-05 | 0.12466 | 0.070086 | 0.060265 | 0.088755 | -0.054588 | 0.1786 | 0.10636 | 0.092622 | 0.073618 | 0.007751 | 0.04788 | 0.1007 | -0.13876 | -0.10004 | 121.3313 | -0.034841 | 121.3496 | 121.2852 | -0.046098 | -0.17818 | 0.054999 | 121.1249 | -0.075716 | 121.3176 | 121.2327 | 0.1078 | -0.022896 | -0.26236 | 121.3137 | 121.1704 | 121.4036 | 121.2951 | -0.017233 | 121.2729 | 121.3257 | 121.0862 | 121.2986 | -0.22364
2871.6719 | 121.5591 | -121.2158 | 0.11444 | 1.4211e-13 | -0.026882 | -0.0036497 | -0.0095024 | -0.013474 | 0.011681 | -0.22823 | -0.005247 | 0.013849 | 0.014917 | 0.04444 | -0.0001281 | 0.12009 | 0.074664 | 0.055687 | 0.084176 | -0.059167 | 0.1786 | 0.10178 | 0.092622 | 0.06904 | -0.001407 | 0.052459 | 0.1007 | -0.12961 | -0.095467 | 121.3176 | -0.030265 | 121.3359 | 121.2715 | -0.046097 | -0.17361 | 0.064154 | 121.1204 | -0.061982 | 121.3084 | 121.2144 | 0.09406 | -0.013741 | -0.24405 | 121.3 | 121.1567 | 121.3944 | 121.2905 | -0.012657 | 121.2683 | 121.3165 | 121.0862 | 121.2849 | -0.20991
2873.3438 | 121.4401 | -121.2524 | 0.12817 | 1.4211e-13 | -0.026882 | -0.0032223 | -0.0095024 | -0.01326 | 0.011467 | -0.23586 | -0.005247 | 0.014063 | 0.014703 | 0.044653 | -0.0003419 | 0.12009 | 0.074664 | 0.064843 | 0.084176 | -0.054588 | 0.16944 | 0.10178 | 0.097201 | 0.073618 | 0.003172 | 0.04788 | 0.096121 | -0.13876 | -0.095467 | 121.3542 | -0.043998 | 121.3725 | 121.3173 | -0.036941 | -0.18276 | 0.041264 | 121.157 | -0.080294 | 121.3496 | 121.2556 | 0.098639 | -0.032053 | -0.26694 | 121.3366 | 121.1979 | 121.4219 | 121.3271 | -0.02639 | 121.3003 | 121.3486 | 121.1137 | 121.3261 | -0.22364
2875.0781 | 121.5271 | -121.2662 | 0.13733 | 1.4211e-13 | -0.026882 | -0.0036497 | -0.0099298 | -0.013901 | 0.011681 | -0.23586 | -0.005247 | 0.013849 | 0.014703 | 0.04444 | -0.0001281 | 0.12466 | 0.070086 | 0.060265 | 0.088755 | -0.054588 | 0.17402 | 0.10636 | 0.097201 | 0.064461 | 0.007751 | 0.052459 | 0.086964 | -0.13419 | -0.090888 | 121.3725 | -0.048574 | 121.3908 | 121.3264 | -0.046098 | -0.19192 | 0.036687 | 121.1753 | -0.08487 | 121.3634 | 121.2739 | 0.098639 | -0.050365 | -0.27152 | 121.3549 | 121.2116 | 121.4402 | 121.3363 | -0.030966 | 121.3186 | 121.3531 | 121.132 | 121.3306 | -0.22822
2876.8281 | 121.6324 | -121.225 | 0.10071 | 1.4211e-13 | -0.02731 | -0.0034359 | -0.0097162 | -0.013901 | 0.011467 | -0.2206 | -0.0050332 | 0.014277 | 0.014276 | 0.044867 | 8.5502e-05 | 0.12466 | 0.070086 | 0.051108 | 0.088755 | -0.050009 | 0.16944 | 0.10178 | 0.092622 | 0.078197 | -0.001407 | 0.061616 | 0.091543 | -0.13876 | -0.095467 | 121.3268 | -0.011953 | 121.3496 | 121.2761 | -0.050676 | -0.15072 | 0.06873 | 121.1295 | -0.039092 | 121.3176 | 121.2236 | 0.09406 | -0.009165 | -0.23947 | 121.3137 | 121.175 | 121.3944 | 121.2951 | 0.001076 | 121.2866 | 121.3165 | 121.0862 | 121.3032 | -0.19617
2878.5156 | 121.6095 | -121.2616 | 0.086975 | 1.4211e-13 | -0.026882 | -0.0032223 | -0.0097162 | -0.013687 | 0.011681 | -0.23586 | -0.0054606 | 0.014063 | 0.014917 | 0.044867 | -0.0001281 | 0.12466 | 0.079243 | 0.060265 | 0.088755 | -0.059167 | 0.1786 | 0.10178 | 0.097201 | 0.06904 | -0.001407 | 0.052459 | 0.086964 | -0.13419 | -0.095467 | 121.3634 | 0.00178 | 121.3863 | 121.3219 | -0.041519 | -0.14614 | 0.09162 | 121.1661 | -0.034516 | 121.3588 | 121.2602 | 0.09406 | -1.1e-05 | -0.22116 | 121.3504 | 121.2024 | 121.4402 | 121.3408 | 0.014809 | 121.3141 | 121.3486 | 121.1274 | 121.3306 | -0.18244
2880.25 | 121.5775 | -121.2708 | 0.1236 | 1.4211e-13 | -0.027096 | -0.0036497 | -0.0097162 | -0.01326 | 0.011467 | -0.23586 | -0.0050332 | 0.013849 | 0.015558 | 0.044653 | 8.5502e-05 | 0.11551 | 0.070086 | 0.055687 | 0.088755 | -0.059167 | 0.16486 | 0.097205 | 0.097201 | 0.073618 | 0.003172 | 0.057037 | 0.096121 | -0.13876 | -0.090888 | 121.368 | -0.034841 | 121.3863 | 121.3264 | -0.041518 | -0.18276 | 0.041263 | 121.1799 | -0.066559 | 121.368 | 121.2739 | 0.09406 | -0.027475 | -0.26236 | 121.3595 | 121.2116 | 121.4356 | 121.3408 | -0.026391 | 121.3278 | 121.3669 | 121.132 | 121.3444 | -0.21448
2881.9531 | 121.4996 | -121.3165 | 0.16022 | 1.4211e-13 | -0.027096 | -0.0036497 | -0.0097162 | -0.013474 | 0.011467 | -0.23586 | -0.0050332 | 0.013849 | 0.015558 | 0.044653 | 8.5502e-05 | 0.12466 | 0.074664 | 0.060265 | 0.079598 | -0.054588 | 0.17402 | 0.097205 | 0.097201 | 0.064461 | -0.001407 | 0.061616 | 0.10528 | -0.14334 | -0.090888 | 121.4137 | -0.080619 | 121.4412 | 121.3768 | -0.03694 | -0.2148 | 0.013799 | 121.2256 | -0.098601 | 121.4137 | 121.3151 | 0.089481 | -0.054938 | -0.30356 | 121.3961 | 121.2619 | 121.4905 | 121.3912 | -0.063012 | 121.3781 | 121.4218 | 121.1732 | 121.381 | -0.25111
2883.7031 | 121.6095 | -121.312 | 0.11444 | 1.4211e-13 | -0.027096 | -0.0034359 | -0.0095024 | -0.013474 | 0.011681 | -0.22823 | -0.0054606 | 0.014063 | 0.01513 | 0.044653 | -0.0001281 | 0.12009 | 0.079243 | 0.060265 | 0.084176 | -0.063746 | 0.1786 | 0.10178 | 0.092622 | 0.073618 | 0.007751 | 0.057037 | 0.1007 | -0.13419 | -0.095467 | 121.4137 | -0.030265 | 121.432 | 121.3722 | -0.041519 | -0.17819 | 0.064154 | 121.2165 | -0.057404 | 121.4046 | 121.3197 | 0.10322 | -0.013741 | -0.24863 | 121.3961 | 121.2482 | 121.4905 | 121.3912 | -0.012657 | 121.369 | 121.4127 | 121.1778 | 121.3856 | -0.20991
2885.4375 | 121.6095 | -121.344 | 0.10986 | 1.4211e-13 | -0.02731 | -0.0032223 | -0.0099298 | -0.013474 | 0.011467 | -0.24349 | -0.005247 | 0.014063 | 0.014917 | 0.044867 | 0.0002991 | 0.12009 | 0.074664 | 0.064843 | 0.084176 | -0.059167 | 0.1786 | 0.097205 | 0.10178 | 0.06904 | -0.001407 | 0.057037 | 0.096121 | -0.14334 | -0.095467 | 121.4412 | -0.025687 | 121.4641 | 121.4088 | -0.032362 | -0.16903 | 0.068732 | 121.2485 | -0.052826 | 121.4458 | 121.3426 | 0.09406 | -0.013742 | -0.25321 | 121.4282 | 121.2848 | 121.5226 | 121.4187 | -0.012658 | 121.401 | 121.4401 | 121.2007 | 121.413 | -0.20533
2887.1875 | 121.5546 | -121.3531 | 0.14648 | 1.4211e-13 | -0.027096 | -0.0034359 | -0.0097162 | -0.013687 | 0.01104 | -0.23586 | -0.0054606 | 0.013636 | 0.015344 | 0.044653 | 8.5502e-05 | 0.12009 | 0.079243 | 0.051108 | 0.088755 | -0.059167 | 0.17402 | 0.10636 | 0.10178 | 0.06904 | 0.003172 | 0.057037 | 0.096121 | -0.13419 | -0.090888 | 121.4595 | -0.057729 | 121.4732 | 121.4043 | -0.055255 | -0.20565 | 0.027532 | 121.2623 | -0.089447 | 121.4549 | 121.3563 | 0.09406 | -0.050363 | -0.28067 | 121.4419 | 121.294 | 121.5272 | 121.4324 | -0.040121 | 121.4102 | 121.4493 | 121.219 | 121.4222 | -0.23737
2888.9375 | 121.5775 | -121.3806 | 0.14191 | 1.4211e-13 | -0.02731 | -0.0036497 | -0.0097162 | -0.01326 | 0.011467 | -0.22823 | -0.005247 | 0.013636 | 0.01513 | 0.044867 | -0.0001281 | 0.12466 | 0.070086 | 0.051108 | 0.088755 | -0.059167 | 0.1786 | 0.10178 | 0.088043 | 0.073618 | 0.007751 | 0.061616 | 0.091543 | -0.13419 | -0.095467 | 121.4824 | -0.053152 | 121.5053 | 121.4317 | -0.050676 | -0.20107 | 0.036688 | 121.2851 | -0.080291 | 121.4687 | 121.3884 | 0.10322 | -0.050364 | -0.27609 | 121.4694 | 121.3214 | 121.5592 | 121.4507 | -0.040123 | 121.4422 | 121.4722 | 121.2464 | 121.4542 | -0.23737
2890.7031 | 121.6782 | -121.3394 | 0.09613 | 1.4211e-13 | -0.027523 | -0.0034359 | -0.0097162 | -0.013474 | 0.011467 | -0.24349 | -0.005247 | 0.014063 | 0.01513 | 0.044867 | -0.0001281 | 0.13382 | 0.079243 | 0.051108 | 0.093333 | -0.054588 | 0.18317 | 0.097205 | 0.10178 | 0.073618 | 0.003172 | 0.061616 | 0.096121 | -0.13419 | -0.10004 | 121.4366 | -0.002797 | 121.4732 | 121.3905 | -0.046097 | -0.15072 | 0.087043 | 121.2394 | -0.034514 | 121.4412 | 121.3426 | 0.10322 | -9e-06 | -0.23032 | 121.4327 | 121.2848 | 121.5226 | 121.4187 | 0.001075 | 121.401 | 121.4355 | 121.2052 | 121.413 | -0.19617
2892.3906 | 121.5729 | -121.3806 | 0.14191 | 1.4211e-13 | -0.027523 | -0.0036497 | -0.0097162 | -0.013687 | 0.011467 | -0.23586 | -0.0050332 | 0.014277 | 0.01513 | 0.045081 | -0.0001281 | 0.12924 | 0.083821 | 0.055687 | 0.084176 | -0.063746 | 0.17402 | 0.11094 | 0.10178 | 0.078197 | 0.007751 | 0.057037 | 0.1007 | -0.13876 | -0.095467 | 121.4916 | -0.057731 | 121.5099 | 121.4363 | -0.055255 | -0.20565 | 0.032109 | 121.2851 | -0.08487 | 121.4824 | 121.3884 | 0.10322 | -0.041207 | -0.28067 | 121.4648 | 121.3169 | 121.5546 | 121.4644 | -0.030965 | 121.4377 | 121.4813 | 121.2418 | 121.4588 | -0.23737
2894.1406 | 121.701 | -121.344 | 0.11444 | 1.4211e-13 | -0.027523 | -0.0034359 | -0.0097162 | -0.013901 | 0.011467 | -0.22823 | -0.0056742 | 0.014063 | 0.014703 | 0.044867 | 8.5502e-05 | 0.12924 | 0.070086 | 0.055687 | 0.084176 | -0.063746 | 0.16944 | 0.097205 | 0.092622 | 0.06904 | 0.003172 | 0.04788 | 0.10528 | -0.13876 | -0.090888 | 121.4412 | -0.030265 | 121.4732 | 121.3997 | -0.041518 | -0.17819 | 0.054997 | 121.2531 | -0.066561 | 121.4366 | 121.3472 | 0.09406 | -0.009162 | -0.25321 | 121.4282 | 121.2802 | 121.5134 | 121.4141 | -0.017236 | 121.3919 | 121.4493 | 121.2052 | 121.413 | -0.20533
2895.8906 | 121.6278 | -121.3943 | 0.14648 | 1.4211e-13 | -0.02731 | -0.0038633 | -0.0092888 | -0.013901 | 0.011254 | -0.24349 | -0.0054606 | 0.01449 | 0.014703 | 0.044653 | -0.0001281 | 0.12924 | 0.083821 | 0.064843 | 0.093333 | -0.054588 | 0.1786 | 0.10636 | 0.092622 | 0.06904 | 0.007751 | 0.066194 | 0.1007 | -0.14334 | -0.10004 | 121.5007 | -0.053151 | 121.5236 | 121.4592 | -0.04152 | -0.20107 | 0.032111 | 121.2943 | -0.08029 | 121.487 | 121.4021 | 0.1078 | -0.045784 | -0.28983 | 121.4877 | 121.3398 | 121.5729 | 121.4782 | -0.040121 | 121.4605 | 121.495 | 121.251 | 121.4634 | -0.24653
2897.5781 | 121.6049 | -121.4355 | 0.13733 | 1.4211e-13 | -0.027523 | -0.0034359 | -0.0099298 | -0.013474 | 0.011467 | -0.24349 | -0.0050332 | 0.013636 | 0.014917 | 0.044867 | 0.0002991 | 0.12924 | 0.079243 | 0.060265 | 0.084176 | -0.059167 | 0.17402 | 0.10178 | 0.092622 | 0.073618 | 0.003172 | 0.061616 | 0.1007 | -0.13419 | -0.10004 | 121.5373 | -0.053153 | 121.5648 | 121.4958 | -0.041519 | -0.1965 | 0.036687 | 121.3355 | -0.075713 | 121.5282 | 121.4387 | 0.10322 | -0.036629 | -0.27152 | 121.5197 | 121.3764 | 121.6096 | 121.5148 | -0.035545 | 121.4972 | 121.5362 | 121.3014 | 121.5092 | -0.23737
2899.3281 | 121.6507 | -121.4264 | 0.12817 | 1.4211e-13 | -0.02731 | -0.0034359 | -0.0099298 | -0.013474 | 0.011254 | -0.22823 | -0.0054606 | 0.014063 | 0.014703 | 0.044867 | -0.0005555 | 0.13382 | 0.083821 | 0.060265 | 0.084176 | -0.059167 | 0.18775 | 0.097205 | 0.092622 | 0.06904 | 0.007751 | 0.061616 | 0.10528 | -0.13876 | -0.090888 | 121.5236 | -0.043998 | 121.5602 | 121.4867 | -0.03694 | -0.18734 | 0.059578 | 121.3355 | -0.066558 | 121.519 | 121.4341 | 0.098639 | -0.022895 | -0.26694 | 121.5106 | 121.3672 | 121.6141 | 121.5102 | -0.030969 | 121.488 | 121.5317 | 121.2876 | 121.4954 | -0.21906
2901.0156 | 121.6599 | -121.4172 | 0.12817 | 1.4211e-13 | -0.027523 | -0.0036497 | -0.0099298 | -0.014115 | 0.01104 | -0.24349 | -0.0054606 | 0.014063 | 0.014917 | 0.045294 | -0.0003419 | 0.12466 | 0.074664 | 0.060265 | 0.088755 | -0.059167 | 0.1786 | 0.10636 | 0.097201 | 0.06904 | 0.007751 | 0.057037 | 0.10528 | -0.13876 | -0.086309 | 121.5236 | -0.039419 | 121.5419 | 121.4775 | -0.046098 | -0.18734 | 0.050421 | 121.3309 | -0.071137 | 121.5144 | 121.425 | 0.09406 | -0.022895 | -0.26694 | 121.506 | 121.3581 | 121.5958 | 121.4919 | -0.021811 | 121.4743 | 121.5225 | 121.2785 | 121.4863 | -0.21448
2902.7656 | 121.6324 | -121.4355 | 0.13733 | 1.4211e-13 | -0.027737 | -0.0032223 | -0.0097162 | -0.013687 | 0.011254 | -0.22823 | -0.005247 | 0.014063 | 0.014917 | 0.044653 | -0.0001281 | 0.1384 | 0.074664 | 0.064843 | 0.088755 | -0.059167 | 0.1786 | 0.10636 | 0.097201 | 0.073618 | 0.01233 | 0.061616 | 0.11444 | -0.13876 | -0.095467 | 121.5419 | -0.048574 | 121.5739 | 121.5004 | -0.04152 | -0.1965 | 0.041266 | 121.3401 | -0.075713 | 121.5327 | 121.4479 | 0.1078 | -0.022893 | -0.27609 | 121.5243 | 121.3764 | 121.6141 | 121.5102 | -0.030966 | 121.4972 | 121.55 | 121.2968 | 121.5092 | -0.2328
2904.5156 | 121.6965 | -121.4218 | 0.10529 | 1.4211e-13 | -0.027523 | -0.0036497 | -0.0095024 | -0.013474 | 0.011254 | -0.23586 | -0.0054606 | 0.014063 | 0.014703 | 0.044867 | -0.0005555 | 0.12924 | 0.074664 | 0.060265 | 0.084176 | -0.068325 | 0.17402 | 0.097205 | 0.097201 | 0.06904 | -0.001407 | 0.061616 | 0.10986 | -0.13876 | -0.10004 | 121.519 | -0.02111 | 121.5511 | 121.4821 | -0.03694 | -0.17361 | 0.06873 | 121.3218 | -0.04367 | 121.519 | 121.4204 | 0.098638 | 0.004571 | -0.24405 | 121.506 | 121.3535 | 121.5958 | 121.4965 | -0.008081 | 121.4834 | 121.5317 | 121.283 | 121.4909 | -0.20533
2906.2812 | 121.7194 | -121.4218 | 0.11444 | 1.4211e-13 | -0.027951 | -0.0034359 | -0.0097162 | -0.013687 | 0.011254 | -0.22823 | -0.0056742 | 0.014063 | 0.014703 | 0.045081 | -0.0003419 | 0.12466 | 0.079243 | 0.055687 | 0.097912 | -0.059167 | 0.17402 | 0.092626 | 0.10178 | 0.073618 | 0.003172 | 0.057037 | 0.10528 | -0.13876 | -0.095467 | 121.5144 | -0.016529 | 121.5465 | 121.4775 | -0.036939 | -0.17361 | 0.059575 | 121.3263 | -0.057404 | 121.5236 | 121.425 | 0.098639 | -0.009162 | -0.25321 | 121.5197 | 121.3626 | 121.5958 | 121.5011 | -0.021815 | 121.4789 | 121.5271 | 121.283 | 121.4954 | -0.20991
2907.9688 | 121.7468 | -121.4264 | 0.11902 | 1.4211e-13 | -0.027523 | -0.0038633 | -0.0099298 | -0.013687 | 0.01104 | -0.25112 | -0.0050332 | 0.013422 | 0.014703 | 0.044867 | -0.0003419 | 0.12924 | 0.083821 | 0.051108 | 0.079598 | -0.054588 | 0.17402 | 0.11094 | 0.097201 | 0.06904 | 0.003172 | 0.057037 | 0.10986 | -0.13419 | -0.090888 | 121.5373 | -0.039421 | 121.5556 | 121.4775 | -0.059834 | -0.17361 | 0.054997 | 121.3355 | -0.061982 | 121.5236 | 121.4296 | 0.09406 | -0.009162 | -0.25321 | 121.506 | 121.3718 | 121.6004 | 121.5102 | -0.008077 | 121.4834 | 121.5362 | 121.2922 | 121.4954 | -0.20991
2909.6719 | 121.8018 | -121.4447 | 0.11902 | 1.4211e-13 | -0.027737 | -0.0036497 | -0.0097162 | -0.013474 | 0.01104 | -0.23586 | -0.0054606 | 0.013422 | 0.01449 | 0.045081 | -0.0001281 | 0.1384 | 0.079243 | 0.051108 | 0.084176 | -0.050009 | 0.17402 | 0.097205 | 0.092622 | 0.06904 | 0.003172 | 0.066194 | 0.1007 | -0.13419 | -0.095467 | 121.5419 | -0.034843 | 121.5831 | 121.4958 | -0.046097 | -0.16903 | 0.054997 | 121.3492 | -0.052825 | 121.5373 | 121.4479 | 0.098639 | -0.018319 | -0.25321 | 121.5289 | 121.3947 | 121.6187 | 121.5239 | -0.021814 | 121.5109 | 121.5454 | 121.3105 | 121.5137 | -0.21449
2911.4219 | 121.7743 | -121.4493 | 0.09613 | 1.4211e-13 | -0.027951 | -0.0032223 | -0.0099298 | -0.013687 | 0.011254 | -0.23586 | -0.0056742 | 0.013849 | 0.01513 | 0.045081 | -0.0005555 | 0.1384 | 0.074664 | 0.055687 | 0.088755 | -0.054588 | 0.17402 | 0.10178 | 0.10178 | 0.073618 | 0.003172 | 0.061616 | 0.10528 | -0.13876 | -0.095467 | 121.5511 | -0.007375 | 121.5877 | 121.505 | -0.046097 | -0.15072 | 0.077886 | 121.3538 | -0.034514 | 121.5511 | 121.4525 | 0.098639 | 0.009149 | -0.23489 | 121.538 | 121.3947 | 121.6233 | 121.5239 | 0.005654 | 121.5109 | 121.5546 | 121.3105 | 121.5229 | -0.1916
2913.1719 | 121.7651 | -121.4172 | 0.1236 | 1.4211e-13 | -0.027951 | -0.0036497 | -0.0097162 | -0.013687 | 0.011254 | -0.25112 | -0.0054606 | 0.013849 | 0.014917 | 0.045294 | -0.0003419 | 0.12924 | 0.079243 | 0.055687 | 0.084176 | -0.063746 | 0.1786 | 0.10178 | 0.092622 | 0.06904 | 0.007751 | 0.061616 | 0.10528 | -0.14334 | -0.090888 | 121.519 | -0.03942 | 121.5465 | 121.4729 | -0.046097 | -0.18734 | 0.054999 | 121.3263 | -0.06198 | 121.5099 | 121.425 | 0.098639 | -0.018317 | -0.26694 | 121.5014 | 121.3535 | 121.5958 | 121.4965 | -0.021812 | 121.4789 | 121.5225 | 121.2739 | 121.4863 | -0.21448
2914.9219 | 121.6782 | -121.5042 | 0.13733 | 1.4211e-13 | -0.027737 | -0.0034359 | -0.0097162 | -0.013901 | 0.011254 | -0.22823 | -0.0050332 | 0.013636 | 0.014703 | 0.045081 | -0.0001281 | 0.13382 | 0.070086 | 0.055687 | 0.088755 | -0.059167 | 0.1786 | 0.097205 | 0.092622 | 0.06904 | 0.007751 | 0.057037 | 0.1007 | -0.13876 | -0.095467 | 121.6014 | -0.048574 | 121.638 | 121.5599 | -0.041518 | -0.1965 | 0.041266 | 121.4087 | -0.080292 | 121.5968 | 121.512 | 0.10322 | -0.036629 | -0.27609 | 121.593 | 121.445 | 121.6828 | 121.5743 | -0.040124 | 121.5612 | 121.6049 | 121.3654 | 121.5733 | -0.2328
2916.6094 | 121.6736 | -121.4905 | 0.14191 | 1.4211e-13 | -0.027737 | -0.0038633 | -0.0097162 | -0.013687 | 0.011254 | -0.24349 | -0.0054606 | 0.013849 | 0.014917 | 0.045081 | -0.0001281 | 0.13382 | 0.079243 | 0.055687 | 0.088755 | -0.054588 | 0.18317 | 0.10636 | 0.097201 | 0.06904 | 0.003172 | 0.052459 | 0.1007 | -0.13419 | -0.10004 | 121.5968 | -0.053152 | 121.6243 | 121.5462 | -0.050676 | -0.1965 | 0.041266 | 121.3904 | -0.089448 | 121.5877 | 121.4937 | 0.10322 | -0.041207 | -0.27609 | 121.5792 | 121.4359 | 121.6737 | 121.5697 | -0.035544 | 121.5429 | 121.5912 | 121.3563 | 121.5595 | -0.24195
2918.3594 | 121.7468 | -121.4951 | 0.13275 | 1.4211e-13 | -0.027951 | -0.0036497 | -0.0095024 | -0.013687 | 0.011254 | -0.23586 | -0.0056742 | 0.014063 | 0.014917 | 0.045081 | -0.0005555 | 0.13382 | 0.079243 | 0.060265 | 0.079598 | -0.063746 | 0.18317 | 0.10636 | 0.088043 | 0.073618 | 0.01233 | 0.052459 | 0.091543 | -0.12961 | -0.095467 | 121.6014 | -0.053153 | 121.6289 | 121.5553 | -0.046098 | -0.1965 | 0.050422 | 121.3996 | -0.080292 | 121.5831 | 121.5074 | 0.1078 | -0.041208 | -0.26236 | 121.5747 | 121.4313 | 121.6782 | 121.5743 | -0.026388 | 121.5475 | 121.5866 | 121.3654 | 121.5687 | -0.22822
2920.0469 | 121.6873 | -121.5271 | 0.16937 | 1.4211e-13 | -0.027951 | -0.0038633 | -0.0095024 | -0.013687 | 0.011254 | -0.25112 | -0.0056742 | 0.013636 | 0.01513 | 0.045081 | -0.0005555 | 0.13382 | 0.074664 | 0.055687 | 0.088755 | -0.059167 | 0.18317 | 0.097205 | 0.10636 | 0.064461 | 0.007751 | 0.057037 | 0.096121 | -0.13419 | -0.090888 | 121.6243 | -0.080618 | 121.6609 | 121.5828 | -0.041518 | -0.22854 | 0.0138 | 121.4362 | -0.11234 | 121.6335 | 121.5349 | 0.098639 | -0.073252 | -0.30356 | 121.6159 | 121.4679 | 121.7103 | 121.6018 | -0.072168 | 121.5841 | 121.6232 | 121.3929 | 121.5916 | -0.26026
2921.8125 | 121.7926 | -121.4951 | 0.13275 | 1.4211e-13 | -0.027737 | -0.0036497 | -0.0095024 | -0.013901 | 0.011254 | -0.24349 | -0.0056742 | 0.013849 | 0.01513 | 0.045081 | -0.0003419 | 0.13382 | 0.074664 | 0.055687 | 0.07502 | -0.063746 | 0.17402 | 0.10178 | 0.10178 | 0.06904 | -0.001407 | 0.061616 | 0.096121 | -0.13419 | -0.10004 | 121.5968 | -0.057731 | 121.6289 | 121.5507 | -0.046097 | -0.1965 | 0.041265 | 121.395 | -0.071135 | 121.5968 | 121.4936 | 0.098638 | -0.03663 | -0.26694 | 121.5701 | 121.4313 | 121.6691 | 121.5697 | -0.030967 | 121.5567 | 121.5912 | 121.3609 | 121.5641 | -0.2328
2923.4844 | 121.7468 | -121.5317 | 0.12817 | 1.4211e-13 | -0.027737 | -0.0040769 | -0.0097162 | -0.014115 | 0.011254 | -0.23586 | -0.0056742 | 0.014063 | 0.014917 | 0.045081 | -0.0001281 | 0.13382 | 0.074664 | 0.055687 | 0.084176 | -0.059167 | 0.16944 | 0.097205 | 0.097201 | 0.06904 | 0.007751 | 0.066194 | 0.1007 | -0.13419 | -0.095467 | 121.6289 | -0.043998 | 121.6655 | 121.5874 | -0.041518 | -0.18734 | 0.041264 | 121.4362 | -0.06198 | 121.6289 | 121.5394 | 0.10322 | -0.027474 | -0.26236 | 121.6159 | 121.4725 | 121.7011 | 121.6063 | -0.030969 | 121.5979 | 121.6324 | 121.3975 | 121.6007 | -0.22364
2925.2188 | 121.7651 | -121.5408 | 0.13275 | 1.4211e-13 | -0.027951 | -0.0038633 | -0.0097162 | -0.013687 | 0.010826 | -0.23586 | -0.005247 | 0.013849 | 0.01513 | 0.045081 | -0.0003419 | 0.1384 | 0.074664 | 0.051108 | 0.084176 | -0.059167 | 0.1786 | 0.10636 | 0.10178 | 0.064461 | 0.007751 | 0.061616 | 0.1007 | -0.12961 | -0.095467 | 121.6472 | -0.048575 | 121.6792 | 121.5919 | -0.055255 | -0.19192 | 0.045844 | 121.4454 | -0.071135 | 121.6426 | 121.5486 | 0.10322 | -0.032051 | -0.26236 | 121.625 | 121.4817 | 121.7194 | 121.6155 | -0.026388 | 121.6024 | 121.6415 | 121.4112 | 121.6053 | -0.22822
2926.9062 | 121.7331 | -121.5317 | 0.12817 | 1.4211e-13 | -0.027951 | -0.0032223 | -0.0095024 | -0.013901 | 0.01104 | -0.23586 | -0.0056742 | 0.013849 | 0.01449 | 0.045294 | -0.0003419 | 0.13382 | 0.074664 | 0.060265 | 0.084176 | -0.054588 | 0.18775 | 0.092626 | 0.11094 | 0.073618 | 0.01233 | 0.061616 | 0.096121 | -0.13876 | -0.090888 | 121.6243 | -0.043998 | 121.6655 | 121.5919 | -0.032361 | -0.18276 | 0.059578 | 121.4408 | -0.066558 | 121.6426 | 121.544 | 0.10322 | -0.032053 | -0.26694 | 121.6159 | 121.4771 | 121.7194 | 121.6063 | -0.035548 | 121.5933 | 121.6278 | 121.3929 | 121.6053 | -0.21906
2928.6562 | 121.8658 | -121.5317 | 0.11444 | 1.4211e-13 | -0.027951 | -0.0032223 | -0.010144 | -0.013687 | 0.011254 | -0.23586 | -0.005247 | 0.013636 | 0.01449 | 0.045081 | -0.0007691 | 0.12924 | 0.070086 | 0.055687 | 0.084176 | -0.059167 | 0.16944 | 0.10178 | 0.097201 | 0.06904 | 0.01233 | 0.061616 | 0.1007 | -0.14334 | -0.090888 | 121.6335 | -0.030265 | 121.6609 | 121.5874 | -0.046097 | -0.17361 | 0.054997 | 121.4408 | -0.052825 | 121.6289 | 121.544 | 0.10322 | -0.013741 | -0.25778 | 121.6159 | 121.4725 | 121.7011 | 121.6018 | -0.012657 | 121.5933 | 121.6324 | 121.3883 | 121.6007 | -0.20533
2930.4062 | 121.8521 | -121.5408 | 0.11444 | 1.4211e-13 | -0.027951 | -0.0040769 | -0.0099298 | -0.013901 | 0.01104 | -0.23586 | -0.0054606 | 0.013636 | 0.014703 | 0.045508 | -0.0003419 | 0.13382 | 0.070086 | 0.051108 | 0.084176 | -0.059167 | 0.17402 | 0.10178 | 0.10178 | 0.06904 | 0.01233 | 0.061616 | 0.10528 | -0.13876 | -0.090888 | 121.6426 | -0.030265 | 121.6747 | 121.5919 | -0.050676 | -0.17361 | 0.059575 | 121.4499 | -0.052825 | 121.6426 | 121.5532 | 0.10322 | -0.009162 | -0.25321 | 121.625 | 121.4817 | 121.7148 | 121.6109 | -0.012657 | 121.6024 | 121.6461 | 121.4021 | 121.6099 | -0.20533
2932.1562 | 121.3028 | -121.1609 | 0.11902 | 1.4211e-13 | -0.028164 | -0.0036497 | -0.0097162 | -0.013687 | 0.01104 | -0.23586 | -0.0054606 | 0.013849 | 0.014703 | 0.045294 | -0.0007691 | 0.13382 | 0.074664 | 0.055687 | 0.084176 | -0.059167 | 0.17402 | 0.097205 | 0.097201 | 0.078197 | 0.007751 | 0.061616 | 0.1007 | -0.12961 | -0.090888 | 121.2581 | -0.034843 | 121.2947 | 121.2166 | -0.041518 | -0.17819 | 0.054997 | 121.07 | -0.057403 | 121.2581 | 121.1686 | 0.098639 | -0.018319 | -0.24863 | 121.2451 | 121.1017 | 121.3349 | 121.2356 | -0.021814 | 121.2225 | 121.2616 | 121.0313 | 121.2391 | -0.20991
2933.9062 | 121.5454 | -121.3531 | 0.13275 | 1.4211e-13 | -0.027951 | -0.0038633 | -0.0097162 | -0.013687 | 0.01104 | -0.23586 | -0.005247 | 0.014063 | 0.01449 | 0.045508 | -0.0005555 | 0.1384 | 0.074664 | 0.055687 | 0.088755 | -0.054588 | 0.1786 | 0.10178 | 0.097201 | 0.073618 | 0.007751 | 0.052459 | 0.10528 | -0.14334 | -0.090888 | 121.4549 | -0.043996 | 121.4915 | 121.4088 | -0.046097 | -0.18734 | 0.045844 | 121.2623 | -0.080292 | 121.4504 | 121.3609 | 0.098639 | -0.027472 | -0.27609 | 121.4419 | 121.2986 | 121.5317 | 121.4278 | -0.030967 | 121.4056 | 121.4584 | 121.2098 | 121.4268 | -0.22364
2935.5781 | 121.6919 | -121.3623 | 0.10529 | 1.4211e-13 | -0.028378 | -0.0038633 | -0.0097162 | -0.013901 | 0.011467 | -0.22823 | -0.0054606 | 0.013636 | 0.014917 | 0.045081 | -0.0003419 | 0.1384 | 0.079243 | 0.055687 | 0.07502 | -0.054588 | 0.18317 | 0.097205 | 0.097201 | 0.073618 | 0.003172 | 0.057037 | 0.10528 | -0.14334 | -0.095467 | 121.4595 | -0.030266 | 121.5007 | 121.418 | -0.041518 | -0.15987 | 0.077887 | 121.2668 | -0.048249 | 121.4595 | 121.3655 | 0.098639 | -7e-06 | -0.24863 | 121.4373 | 121.3077 | 121.5455 | 121.4415 | -0.008081 | 121.4193 | 121.4676 | 121.219 | 121.4359 | -0.20075
2937.3281 | 121.6141 | -121.4401 | 0.14648 | 1.4211e-13 | -0.028378 | -0.0038633 | -0.0097162 | -0.013901 | 0.011254 | -0.24349 | -0.005247 | 0.013636 | 0.014703 | 0.045081 | -0.0003419 | 0.13382 | 0.070086 | 0.055687 | 0.084176 | -0.068325 | 0.1786 | 0.10178 | 0.092622 | 0.06904 | 0.003172 | 0.057037 | 0.10986 | -0.13876 | -0.090888 | 121.5419 | -0.062308 | 121.5739 | 121.4958 | -0.046097 | -0.21481 | 0.032111 | 121.3492 | -0.089447 | 121.5327 | 121.4433 | 0.09406 | -0.036627 | -0.28525 | 121.5243 | 121.3718 | 121.6187 | 121.5102 | -0.0447 | 121.4972 | 121.55 | 121.3014 | 121.5092 | -0.23737
2939.0625 | 120.8817 | -120.5933 | 0.10986 | 1.4211e-13 | -0.028378 | -0.0036497 | -0.0097162 | -0.013901 | 0.010826 | -0.23586 | -0.0054606 | 0.013422 | 0.014703 | 0.045294 | -0.0005555 | 0.14298 | 0.083821 | 0.064843 | 0.093333 | -0.059167 | 0.18317 | 0.0331 | 0.12009 | 0.091933 | 0.026066 | 0.07993 | 0.12359 | -0.12045 | -0.072572 | 120.6264 | -0.01653 | 120.7362 | 120.6581 | 0.031743 | -0.16903 | 0.07331 | 120.5207 | -0.029933 | 120.7134 | 120.6193 | 0.098638 | 0.01373 | -0.23031 | 120.6866 | 120.5341 | 120.7764 | 120.6771 | -0.076763 | 120.6732 | 120.7169 | 120.4728 | 120.6852 | -0.18244
2940.7969 | 120.9091 | -120.5933 | 0.11902 | 1.4211e-13 | -0.028592 | -0.0040769 | -0.010144 | -0.013901 | 0.01104 | -0.22823 | -0.0054606 | 0.014063 | 0.01513 | 0.044867 | -0.0003419 | 0.14298 | 0.079243 | 0.055687 | 0.084176 | -0.063746 | 0.17402 | 0.083468 | 0.088043 | 0.06904 | -0.001407 | 0.052459 | 0.086964 | -0.13876 | -0.1092 | 120.6767 | -0.034843 | 120.7362 | 120.6489 | -0.027781 | -0.18277 | 0.054997 | 120.4841 | -0.06656 | 120.6813 | 120.5919 | 0.1078 | -0.032055 | -0.25778 | 120.6774 | 120.5295 | 120.7673 | 120.6725 | -0.035551 | 120.6457 | 120.6802 | 120.4545 | 120.6623 | -0.22822
2942.5625 | 121.4035 | -121.138 | 0.10986 | 1.4211e-13 | -0.027951 | -0.0034359 | -0.0099298 | -0.014115 | 0.010826 | -0.23586 | -0.0056742 | 0.013422 | 0.014703 | 0.045508 | -0.0005555 | 0.13382 | 0.065507 | 0.04653 | 0.084176 | -0.059167 | 0.1786 | 0.097205 | 0.092622 | 0.06904 | 0.003172 | 0.057037 | 0.1007 | -0.13419 | -0.10004 | 121.2352 | -0.025687 | 121.2718 | 121.1845 | -0.050675 | -0.16903 | 0.068732 | 121.038 | -0.052826 | 121.2306 | 121.1412 | 0.10322 | -0.009163 | -0.24405 | 121.2222 | 121.0788 | 121.3166 | 121.2035 | -0.012658 | 121.195 | 121.2387 | 121.0038 | 121.207 | -0.20991
2944.25 | 121.3989 | -121.2662 | 0.1236 | 1.4211e-13 | -0.028378 | -0.0040769 | -0.0097162 | -0.014115 | 0.01104 | -0.23586 | -0.0054606 | 0.013849 | 0.014703 | 0.045294 | -0.0005555 | 0.1384 | 0.065507 | 0.051108 | 0.079598 | -0.063746 | 0.1786 | 0.097205 | 0.097201 | 0.06904 | -0.001407 | 0.052459 | 0.096121 | -0.13876 | -0.10004 | 121.3634 | -0.043998 | 121.4046 | 121.3173 | -0.046097 | -0.18734 | 0.054999 | 121.1661 | -0.071137 | 121.3634 | 121.2648 | 0.098638 | -0.027475 | -0.26236 | 121.3458 | 121.2024 | 121.4448 | 121.3317 | -0.026391 | 121.3186 | 121.3623 | 121.1274 | 121.3352 | -0.22364
2946 | 121.4767 | -121.2982 | 0.13733 | 1.4211e-13 | -0.028805 | -0.0036497 | -0.0092888 | -0.013687 | 0.010613 | -0.24349 | -0.0050332 | 0.014063 | 0.01449 | 0.045294 | -0.0003419 | 0.13382 | 0.070086 | 0.055687 | 0.079598 | -0.059167 | 0.17402 | 0.097205 | 0.092622 | 0.06904 | -0.001407 | 0.04788 | 0.1007 | -0.13876 | -0.10004 | 121.3954 | -0.057731 | 121.432 | 121.3539 | -0.041518 | -0.1965 | 0.036687 | 121.1982 | -0.089449 | 121.3908 | 121.2968 | 0.098638 | -0.036629 | -0.27609 | 121.3778 | 121.2391 | 121.4722 | 121.3683 | -0.040124 | 121.3461 | 121.3989 | 121.1595 | 121.3673 | -0.23737
2947.7812 | 121.1655 | -120.8084 | 0.11902 | 1.4211e-13 | -0.028164 | -0.0036497 | -0.0097162 | -0.014115 | 0.011467 | -0.23586 | -0.0056742 | 0.014063 | 0.014703 | 0.045508 | -0.0007691 | 0.1384 | 0.065507 | 0.051108 | 0.088755 | -0.059167 | 0.1786 | 0.083468 | 0.088043 | 0.059882 | 0.003172 | 0.052459 | 0.10528 | -0.14334 | -0.10004 | 120.8919 | -0.030264 | 120.9468 | 120.8595 | -0.03236 | -0.17819 | 0.059576 | 120.7084 | -0.06656 | 120.8965 | 120.8116 | 0.10322 | -0.01374 | -0.26236 | 120.8972 | 120.7492 | 120.987 | 120.8739 | -0.035551 | 120.8609 | 120.9137 | 120.6651 | 120.8683 | -0.21906
2949.4688 | 121.3074 | -121.0876 | 0.11902 | 1.4211e-13 | -0.028378 | -0.0034359 | -0.0097162 | -0.013687 | 0.01104 | -0.22823 | -0.0056742 | 0.013849 | 0.014917 | 0.045081 | -0.0005555 | 0.1384 | 0.060928 | 0.04653 | 0.084176 | -0.063746 | 0.1786 | 0.092626 | 0.092622 | 0.06904 | 0.003172 | 0.057037 | 0.1007 | -0.13876 | -0.095467 | 121.1803 | -0.034843 | 121.226 | 121.1342 | -0.046096 | -0.18277 | 0.059576 | 120.9922 | -0.061982 | 121.1803 | 121.0908 | 0.098639 | -0.018319 | -0.25778 | 121.1718 | 121.0239 | 121.2662 | 121.1486 | -0.026393 | 121.1447 | 121.1883 | 120.9489 | 121.1567 | -0.21449
2951.2188 | 121.4676 | -121.1426 | 0.07782 | 1.4211e-13 | -0.028164 | -0.0036497 | -0.0092888 | -0.014115 | 0.011254 | -0.23586 | -0.005247 | 0.013849 | 0.014917 | 0.045508 | -0.0007691 | 0.13382 | 0.060928 | 0.051108 | 0.084176 | -0.063746 | 0.18317 | 0.10178 | 0.092622 | 0.073618 | -0.001407 | 0.052459 | 0.10528 | -0.12961 | -0.10462 | 121.2444 | 0.006356 | 121.2764 | 121.1937 | -0.050676 | -0.14157 | 0.10535 | 121.038 | -0.025361 | 121.2352 | 121.1412 | 0.10322 | 0.027459 | -0.20743 | 121.2268 | 121.0788 | 121.3258 | 121.2035 | 0.023964 | 121.195 | 121.2479 | 121.013 | 121.2162 | -0.18244
2952.9688 | 118.3456 | -85.4507 | 32.0663 | 1.4211e-13 | -0.028164 | -0.0040769 | -0.010144 | -0.013474 | 0.010613 | -0.23586 | -0.005247 | 0.013849 | 0.014703 | 0.045508 | -0.0003419 | 0.2025 | 0.14334 | 0.087735 | 0.097912 | -0.031693 | 0.19691 | 0.088047 | 0.042256 | 0.018674 | -0.051772 | 0.011252 | 0.059493 | -0.12961 | -0.14583 | 85.5388 | -31.9684 | 85.6532 | 85.5385 | -0.000312 | -32.098 | -31.8694 | 85.3049 | -32.0551 | 85.493 | 85.399 | 0.094061 | -32.0069 | -32.196 | 85.5487 | 85.4191 | 85.6477 | 85.5941 | -31.9783 | 85.462 | 85.5102 | 85.3211 | 85.4694 | -32.2122
2954.7188 | 121.3028 | -121.0007 | 0.09613 | 1.4211e-13 | -0.028378 | -0.0038633 | -0.0097162 | -0.013901 | 0.011254 | -0.23586 | -0.0054606 | 0.013849 | 0.014703 | 0.045294 | -0.0005555 | 0.1384 | 0.065507 | 0.055687 | 0.084176 | -0.054588 | 0.1786 | 0.097205 | 0.092622 | 0.064461 | 0.003172 | 0.061616 | 0.1007 | -0.13419 | -0.095467 | 121.0979 | -0.011954 | 121.1391 | 121.0564 | -0.041518 | -0.15072 | 0.082465 | 120.9052 | -0.034514 | 121.0933 | 121.0038 | 0.098639 | 0.00457 | -0.23032 | 121.0848 | 120.9461 | 121.1793 | 121.0662 | 0.001075 | 121.0623 | 121.1014 | 120.8665 | 121.0651 | -0.1916
2956.3906 | 121.3348 | -121.1334 | 0.10986 | 1.4211e-13 | -0.028378 | -0.0038633 | -0.0097162 | -0.014115 | 0.01104 | -0.24349 | -0.005247 | 0.013422 | 0.014276 | 0.045081 | -0.0001281 | 0.14756 | 0.074664 | 0.055687 | 0.084176 | -0.059167 | 0.17402 | 0.10178 | 0.097201 | 0.064461 | -0.005985 | 0.052459 | 0.10528 | -0.13876 | -0.10004 | 121.2352 | -0.025687 | 121.281 | 121.1891 | -0.046097 | -0.16903 | 0.064153 | 121.0334 | -0.057404 | 121.2306 | 121.1274 | 0.09406 | -0.004584 | -0.24863 | 121.2176 | 121.0743 | 121.3074 | 121.2081 | -0.008079 | 121.1859 | 121.2387 | 120.9947 | 121.1979 | -0.20991
2958.1406 | 121.4722 | -121.138 | 0.091553 | 1.4211e-13 | -0.028592 | -0.0036497 | -0.0095024 | -0.014115 | 0.01104 | -0.23586 | -0.005247 | 0.013849 | 0.01449 | 0.045722 | -0.0005555 | 0.1384 | 0.070086 | 0.055687 | 0.084176 | -0.059167 | 0.17402 | 0.10636 | 0.088043 | 0.06904 | 0.003172 | 0.057037 | 0.10528 | -0.13876 | -0.095467 | 121.2444 | -0.007377 | 121.2764 | 121.1937 | -0.050676 | -0.15072 | 0.082463 | 121.0425 | -0.034516 | 121.226 | 121.1412 | 0.098639 | 0.013726 | -0.23032 | 121.2222 | 121.0788 | 121.312 | 121.2081 | 0.01481 | 121.195 | 121.2433 | 120.9992 | 121.207 | -0.18702
2959.875 | 121.4127 | -121.225 | 0.12817 | 1.4211e-13 | -0.028378 | -0.0038633 | -0.0097162 | -0.013901 | 0.01104 | -0.23586 | -0.005247 | 0.013636 | 0.01449 | 0.045508 | -0.0007691 | 0.1384 | 0.074664 | 0.051108 | 0.088755 | -0.063746 | 0.17402 | 0.10636 | 0.088043 | 0.064461 | -0.005985 | 0.057037 | 0.1007 | -0.13419 | -0.095467 | 121.3313 | -0.039419 | 121.3634 | 121.2761 | -0.055255 | -0.19192 | 0.045842 | 121.1295 | -0.071137 | 121.313 | 121.219 | 0.089482 | -0.027474 | -0.26236 | 121.3137 | 121.1612 | 121.399 | 121.2996 | -0.021811 | 121.282 | 121.3257 | 121.0908 | 121.2894 | -0.22364
2961.5625 | 121.3898 | -121.2433 | 0.10529 | 1.4211e-13 | -0.028378 | -0.0040769 | -0.0095024 | -0.013687 | 0.01104 | -0.23586 | -0.0054606 | 0.013636 | 0.014703 | 0.045722 | -0.0005555 | 0.1384 | 0.074664 | 0.055687 | 0.084176 | -0.063746 | 0.1786 | 0.10178 | 0.097201 | 0.064461 | 0.003172 | 0.04788 | 0.096121 | -0.13419 | -0.10462 | 121.3451 | -0.02111 | 121.3817 | 121.299 | -0.046097 | -0.16903 | 0.073309 | 121.1387 | -0.057406 | 121.3405 | 121.2465 | 0.1078 | -0.009165 | -0.23947 | 121.3275 | 121.1795 | 121.4219 | 121.3179 | -0.003502 | 121.2912 | 121.3394 | 121.1091 | 121.3077 | -0.20991
2963.2969 | 121.4905 | -121.2067 | 0.11902 | 1.4211e-13 | -0.028592 | -0.0036497 | -0.0097162 | -0.014115 | 0.011254 | -0.22823 | -0.005247 | 0.013636 | 0.01449 | 0.045508 | -0.0003419 | 0.1384 | 0.070086 | 0.04653 | 0.084176 | -0.054588 | 0.1786 | 0.097205 | 0.088043 | 0.064461 | 0.003172 | 0.057037 | 0.096121 | -0.14334 | -0.10462 | 121.3039 | -0.034843 | 121.3451 | 121.2532 | -0.050675 | -0.17361 | 0.059576 | 121.102 | -0.061982 | 121.2947 | 121.2098 | 0.1078 | -0.022898 | -0.26236 | 121.2908 | 121.1521 | 121.3853 | 121.2768 | -0.021814 | 121.2637 | 121.3028 | 121.0633 | 121.2711 | -0.22364
2965.0469 | 121.5271 | -121.2524 | 0.11444 | 1.4211e-13 | -0.028592 | -0.0038633 | -0.0095024 | -0.014115 | 0.01104 | -0.22823 | -0.0054606 | 0.013849 | 0.01449 | 0.045722 | -0.0007691 | 0.1384 | 0.065507 | 0.055687 | 0.084176 | -0.054588 | 0.17402 | 0.097205 | 0.092622 | 0.064461 | 0.003172 | 0.052459 | 0.11444 | -0.13876 | -0.10004 | 121.3496 | -0.030265 | 121.3908 | 121.3081 | -0.041518 | -0.16903 | 0.059575 | 121.1524 | -0.061982 | 121.3451 | 121.2556 | 0.10322 | -5e-06 | -0.25321 | 121.3366 | 121.1979 | 121.4265 | 121.3179 | -0.017236 | 121.3049 | 121.3669 | 121.1137 | 121.3169 | -0.21449
2966.8125 | 121.1243 | -120.813 | 0.10071 | 1.4211e-13 | -0.028592 | -0.0034359 | -0.0097162 | -0.014542 | 0.01104 | -0.23586 | -0.0056742 | 0.013849 | 0.01449 | 0.045508 | -0.0005555 | 0.1384 | 0.079243 | 0.051108 | 0.079598 | -0.054588 | 0.17402 | 0.10178 | 0.092622 | 0.06904 | 0.003172 | 0.061616 | 0.10528 | -0.13876 | -0.10462 | 120.9148 | -0.02111 | 120.9514 | 120.8641 | -0.050676 | -0.1553 | 0.073308 | 120.7084 | -0.039092 | 120.9056 | 120.8162 | 0.1078 | 0.004571 | -0.23947 | 120.8926 | 120.7584 | 120.987 | 120.8922 | 0.001076 | 120.8746 | 120.9183 | 120.6742 | 120.882 | -0.20533
2968.5 | 121.2296 | -121.0419 | 0.13275 | 1.4211e-13 | -0.028378 | -0.0038633 | -0.0099298 | -0.014115 | 0.010826 | -0.23586 | -0.0054606 | 0.013636 | 0.014276 | 0.045935 | -0.0007691 | 0.14298 | 0.070086 | 0.051108 | 0.084176 | -0.059167 | 0.1786 | 0.10178 | 0.097201 | 0.06904 | -0.001407 | 0.052459 | 0.10986 | -0.13876 | -0.10462 | 121.1437 | -0.048575 | 121.1848 | 121.093 | -0.050676 | -0.19192 | 0.045844 | 120.9372 | -0.080292 | 121.1391 | 121.0405 | 0.10322 | -0.022894 | -0.27152 | 121.126 | 120.9827 | 121.2205 | 121.112 | -0.030967 | 121.0943 | 121.1517 | 120.9031 | 121.1109 | -0.23738
2970.2344 | 121.2845 | -121.138 | 0.11444 | 1.4211e-13 | -0.028378 | -0.0042907 | -0.0099298 | -0.014115 | 0.010826 | -0.24349 | -0.0054606 | 0.013849 | 0.01449 | 0.045722 | -0.0007691 | 0.14756 | 0.070086 | 0.060265 | 0.079598 | -0.063746 | 0.18317 | 0.097205 | 0.088043 | 0.06904 | 0.003172 | 0.061616 | 0.10986 | -0.13876 | -0.095467 | 121.2352 | -0.034843 | 121.2856 | 121.1983 | -0.03694 | -0.17819 | 0.068732 | 121.0425 | -0.052825 | 121.226 | 121.1412 | 0.098639 | -0.004584 | -0.25321 | 121.2176 | 121.0743 | 121.3212 | 121.2081 | -0.017236 | 121.1996 | 121.2479 | 120.9992 | 121.207 | -0.20991
2971.9844 | 121.4355 | -121.1288 | 0.09613 | 1.4211e-13 | -0.029019 | -0.0038633 | -0.0099298 | -0.014542 | 0.011254 | -0.23586 | -0.005247 | 0.014063 | 0.01449 | 0.045294 | -0.0007691 | 0.1384 | 0.060928 | 0.055687 | 0.079598 | -0.063746 | 0.1786 | 0.0331 | 0.092622 | 0.06904 | -0.001407 | 0.061616 | 0.1007 | -0.14334 | -0.10462 | 121.1619 | -0.016532 | 121.2672 | 121.1845 | 0.022587 | -0.15988 | 0.082465 | 121.0242 | -0.034514 | 121.2215 | 121.1274 | 0.10322 | 0.00457 | -0.23947 | 121.2084 | 121.0651 | 121.3074 | 121.1898 | -0.06303 | 121.1905 | 121.2295 | 120.9855 | 121.1979 | -0.20075
2973.7344 | 121.0693 | -120.8313 | 0.10071 | 1.4211e-13 | -0.028592 | -0.0034359 | -0.010144 | -0.014115 | 0.011254 | -0.23586 | -0.0056742 | 0.013636 | 0.01449 | 0.045722 | -0.0007691 | 0.1384 | 0.074664 | 0.04653 | 0.084176 | -0.063746 | 0.1786 | 0.10178 | 0.097201 | 0.064461 | -0.005985 | 0.057037 | 0.1007 | -0.13419 | -0.095467 | 120.9331 | -0.016532 | 120.9697 | 120.8778 | -0.055254 | -0.16445 | 0.077887 | 120.7358 | -0.043671 | 120.9285 | 120.8253 | 0.089482 | -8e-06 | -0.23489 | 120.9155 | 120.7676 | 121.0099 | 120.906 | 0.001076 | 120.8883 | 120.932 | 120.6971 | 120.8958 | -0.19617
2975.4219 | 121.1929 | -121.0144 | 0.13733 | 1.4211e-13 | -0.028592 | -0.0036497 | -0.0095024 | -0.014115 | 0.010613 | -0.23586 | -0.0056742 | 0.013422 | 0.014703 | 0.045508 | -0.0007691 | 0.15213 | 0.065507 | 0.051108 | 0.084176 | -0.059167 | 0.18317 | 0.10178 | 0.088043 | 0.06904 | 0.007751 | 0.052459 | 0.1007 | -0.14334 | -0.1092 | 121.1162 | -0.053153 | 121.1665 | 121.0655 | -0.050676 | -0.1965 | 0.045844 | 120.9052 | -0.08487 | 121.1024 | 121.0222 | 0.11695 | -0.036629 | -0.28067 | 121.0986 | 120.9552 | 121.1976 | 121.0799 | -0.035545 | 121.0669 | 121.1151 | 120.8711 | 121.0834 | -0.24653
2977.1562 | 121.257 | -121.0693 | 0.12817 | 1.4211e-13 | -0.028592 | -0.0038633 | -0.0095024 | -0.013901 | 0.01104 | -0.22823 | -0.0054606 | 0.013422 | 0.014917 | 0.045722 | -0.0005555 | 0.1384 | 0.065507 | 0.051108 | 0.079598 | -0.063746 | 0.1786 | 0.097205 | 0.092622 | 0.073618 | 0.01233 | 0.052459 | 0.11444 | -0.14334 | -0.10462 | 121.1665 | -0.048576 | 121.2077 | 121.1204 | -0.046097 | -0.19192 | 0.050421 | 120.9647 | -0.075715 | 121.162 | 121.0817 | 0.11695 | -0.013738 | -0.27152 | 121.1489 | 121.0056 | 121.2479 | 121.1348 | -0.030969 | 121.1218 | 121.1838 | 120.926 | 121.143 | -0.2328
2978.8438 | 121.4127 | -121.0831 | 0.091553 | 1.4211e-13 | -0.029019 | -0.0040769 | -0.0097162 | -0.014756 | 0.010826 | -0.23586 | -0.0050332 | 0.013636 | 0.01449 | 0.045722 | -0.0007691 | 0.14298 | 0.065507 | 0.055687 | 0.088755 | -0.063746 | 0.1786 | 0.10178 | 0.088043 | 0.064461 | -0.001407 | 0.061616 | 0.10986 | -0.13876 | -0.095467 | 121.1849 | -0.002798 | 121.226 | 121.1388 | -0.046097 | -0.1553 | 0.087042 | 120.9876 | -0.029937 | 121.1711 | 121.0817 | 0.09406 | 0.018304 | -0.23032 | 121.1718 | 121.0193 | 121.2617 | 121.1486 | 0.010231 | 121.1447 | 121.1929 | 120.9443 | 121.1475 | -0.18702
2980.5938 | 120.9366 | -120.6299 | 0.10071 | 1.4211e-13 | -0.028592 | -0.0036497 | -0.0099298 | -0.014115 | 0.010185 | -0.22823 | -0.0056742 | 0.013636 | 0.01449 | 0.045722 | -0.0007691 | 0.14756 | 0.065507 | 0.04653 | 0.084176 | -0.068325 | 0.1786 | 0.097205 | 0.092622 | 0.064461 | -0.001407 | 0.057037 | 0.10528 | -0.14334 | -0.10004 | 120.7271 | -0.016532 | 120.7774 | 120.6764 | -0.050675 | -0.16903 | 0.077887 | 120.5298 | -0.043671 | 120.7225 | 120.6285 | 0.098638 | 0.004571 | -0.24405 | 120.7141 | 120.5616 | 120.8085 | 120.6954 | -0.003503 | 120.6869 | 120.7352 | 120.4865 | 120.6943 | -0.20075
2982.3438 | 121.1334 | -120.9183 | 0.11902 | 1.4211e-13 | -0.028805 | -0.0038633 | -0.0097162 | -0.014115 | 0.01104 | -0.2206 | -0.0054606 | 0.013849 | 0.014703 | 0.045508 | -0.0005555 | 0.1384 | 0.070086 | 0.055687 | 0.088755 | -0.050009 | 0.16944 | 0.10178 | 0.092622 | 0.06904 | -0.001407 | 0.061616 | 0.11444 | -0.13419 | -0.10462 | 121.0201 | -0.030264 | 121.0567 | 120.974 | -0.046097 | -0.16903 | 0.050419 | 120.8136 | -0.057403 | 121.0109 | 120.9169 | 0.10322 | -0.004583 | -0.25321 | 121.007 | 120.8683 | 121.0877 | 120.9884 | -0.017235 | 120.9799 | 121.0327 | 120.7841 | 120.9873 | -0.22364
2984.0938 | 121.2891 | -120.9641 | 0.064087 | 1.4211e-13 | -0.028592 | -0.0036497 | -0.0095024 | -0.013901 | 0.010613 | -0.23586 | -0.005247 | 0.013849 | 0.014703 | 0.045722 | -0.0009829 | 0.14298 | 0.060928 | 0.051108 | 0.084176 | -0.063746 | 0.18317 | 0.097205 | 0.092622 | 0.06904 | 0.003172 | 0.061616 | 0.10986 | -0.13876 | -0.095467 | 121.0613 | 0.020089 | 121.107 | 121.0152 | -0.046097 | -0.12783 | 0.11909 | 120.8686 | -0.002471 | 121.0567 | 120.9672 | 0.098639 | 0.04577 | -0.20285 | 121.0482 | 120.9003 | 121.1472 | 121.025 | 0.033118 | 121.0257 | 121.0739 | 120.8253 | 121.0331 | -0.15955
2985.8281 | 121.2158 | -121.0693 | 0.11444 | 1.4211e-13 | -0.029019 | -0.0036497 | -0.0092888 | -0.014328 | 0.010826 | -0.23586 | -0.005247 | 0.013849 | 0.01449 | 0.045935 | -0.0009829 | 0.14298 | 0.060928 | 0.041952 | 0.088755 | -0.059167 | 0.1786 | 0.097205 | 0.10178 | 0.06904 | 0.003172 | 0.061616 | 0.10986 | -0.13419 | -0.10004 | 121.1665 | -0.025686 | 121.2123 | 121.1113 | -0.055253 | -0.17361 | 0.064154 | 120.9693 | -0.052825 | 121.1711 | 121.0725 | 0.10322 | -0.004584 | -0.24863 | 121.1581 | 121.0102 | 121.2479 | 121.1303 | -0.017236 | 121.131 | 121.1792 | 120.9352 | 121.1384 | -0.21449
2987.5156 | 121.3531 | -121.0556 | 0.1236 | 1.4211e-13 | -0.028805 | -0.0038633 | -0.0097162 | -0.014542 | 0.010826 | -0.23586 | -0.005247 | 0.013849 | 0.01449 | 0.045935 | -0.0007691 | 0.14298 | 0.05635 | 0.04653 | 0.093333 | -0.059167 | 0.18317 | 0.097205 | 0.092622 | 0.073618 | -0.001407 | 0.057037 | 0.10986 | -0.13876 | -0.10004 | 121.1528 | -0.030263 | 121.1986 | 121.1021 | -0.050675 | -0.18276 | 0.059577 | 120.9556 | -0.066559 | 121.1482 | 121.0542 | 0.098638 | -0.013739 | -0.26236 | 121.1489 | 120.9964 | 121.2388 | 121.112 | -0.026391 | 121.1126 | 121.1655 | 120.9168 | 121.1292 | -0.22364
2989.2656 | 121.1563 | -120.8771 | 0.073242 | 1.4211e-13 | -0.029019 | -0.0038633 | -0.0095024 | -0.014328 | 0.010826 | -0.22823 | -0.005247 | 0.013636 | 0.014062 | 0.046149 | -0.0007691 | 0.14298 | 0.060928 | 0.055687 | 0.084176 | -0.059167 | 0.18317 | 0.10636 | 0.088043 | 0.064461 | -0.005985 | 0.057037 | 0.11444 | -0.13876 | -0.1092 | 120.9834 | 0.010934 | 121.0201 | 120.9328 | -0.050676 | -0.13241 | 0.10993 | 120.7679 | -0.016205 | 120.9651 | 120.8711 | 0.10322 | 0.041194 | -0.21201 | 120.9613 | 120.8179 | 121.0602 | 120.938 | 0.033121 | 120.9341 | 120.9915 | 120.7383 | 120.9415 | -0.18244
2990.9531 | 121.2112 | -120.9732 | 0.11444 | 1.4211e-13 | -0.029233 | -0.0036497 | -0.0095024 | -0.014542 | 0.010826 | -0.24349 | -0.0054606 | 0.013636 | 0.01449 | 0.045722 | -0.0007691 | 0.14298 | 0.070086 | 0.051108 | 0.088755 | -0.059167 | 0.17402 | 0.097205 | 0.092622 | 0.064461 | 0.003172 | 0.057037 | 0.10528 | -0.14792 | -0.1092 | 121.0704 | -0.025686 | 121.1162 | 121.0243 | -0.046097 | -0.17361 | 0.059575 | 120.864 | -0.057404 | 121.0658 | 120.9764 | 0.11237 | -0.009162 | -0.26236 | 121.062 | 120.914 | 121.1472 | 121.0433 | -0.017236 | 121.0302 | 121.0785 | 120.8253 | 121.0377 | -0.22364
2992.7031 | 121.0373 | -120.8176 | 0.1236 | 1.4211e-13 | -0.029019 | -0.0038633 | -0.0099298 | -0.014756 | 0.010613 | -0.23586 | -0.0058878 | 0.013636 | 0.01449 | 0.045722 | -0.0007691 | 0.1384 | 0.065507 | 0.04653 | 0.084176 | -0.054588 | 0.18317 | 0.10178 | 0.097201 | 0.06904 | 0.003172 | 0.057037 | 0.10986 | -0.13419 | -0.10462 | 120.9193 | -0.03942 | 120.956 | 120.8641 | -0.055254 | -0.17818 | 0.059577 | 120.7129 | -0.066559 | 120.9148 | 120.8207 | 0.1078 | -0.013739 | -0.25778 | 120.9017 | 120.763 | 121.0007 | 120.8831 | -0.021812 | 120.8746 | 120.9274 | 120.6834 | 120.8866 | -0.22822
2994.4375 | 121.1197 | -120.9366 | 0.12817 | 1.4211e-13 | -0.028805 | -0.0038633 | -0.0097162 | -0.014542 | 0.010613 | -0.23586 | -0.0056742 | 0.013636 | 0.014062 | 0.045935 | -0.0007691 | 0.1384 | 0.065507 | 0.051108 | 0.079598 | -0.063746 | 0.18317 | 0.10636 | 0.097201 | 0.064461 | 0.007751 | 0.057037 | 0.10986 | -0.13876 | -0.10462 | 121.0429 | -0.048576 | 121.075 | 120.9877 | -0.055255 | -0.19192 | 0.054999 | 120.832 | -0.071137 | 121.0338 | 120.9443 | 0.11237 | -0.018317 | -0.26694 | 121.0162 | 120.8728 | 121.1198 | 121.0021 | -0.021811 | 120.9936 | 121.0464 | 120.7978 | 121.001 | -0.2328
2996.125 | 121.1563 | -121.0052 | 0.11444 | 1.4211e-13 | -0.029019 | -0.0038633 | -0.0095024 | -0.014756 | 0.010826 | -0.23586 | -0.0054606 | 0.013849 | 0.01449 | 0.045722 | -0.0009829 | 0.14298 | 0.060928 | 0.051108 | 0.093333 | -0.063746 | 0.1786 | 0.097205 | 0.092622 | 0.064461 | 0.007751 | 0.057037 | 0.10528 | -0.13419 | -0.10462 | 121.1025 | -0.021108 | 121.1482 | 121.0564 | -0.046097 | -0.17819 | 0.064154 | 120.9006 | -0.057404 | 121.0979 | 121.013 | 0.11237 | -0.009162 | -0.24863 | 121.0986 | 120.9415 | 121.1838 | 121.0662 | -0.017236 | 121.0623 | 121.1105 | 120.8711 | 121.0697 | -0.21907
2997.8906 | 121.2662 | -121.0144 | 0.10071 | 1.4211e-13 | -0.028805 | -0.0038633 | -0.010144 | -0.014756 | 0.010826 | -0.22823 | -0.0056742 | 0.013636 | 0.014276 | 0.045508 | -0.0007691 | 0.1384 | 0.060928 | 0.051108 | 0.088755 | -0.059167 | 0.17402 | 0.092626 | 0.097201 | 0.073618 | -0.005985 | 0.061616 | 0.10528 | -0.13876 | -0.10462 | 121.107 | -0.011953 | 121.1528 | 121.0655 | -0.041518 | -0.15987 | 0.073308 | 120.9098 | -0.039092 | 121.1116 | 121.0084 | 0.098639 | 0.004571 | -0.23947 | 121.1032 | 120.9552 | 121.1884 | 121.0753 | -0.008082 | 121.076 | 121.1197 | 120.8756 | 121.088 | -0.20533
2999.6406 | 121.312 | -121.0419 | 0.10529 | 1.4211e-13 | -0.028805 | -0.0038633 | -0.0097162 | -0.014756 | 0.010826 | -0.22823 | -0.0056742 | 0.013636 | 0.014276 | 0.046149 | -0.0007691 | 0.1384 | 0.060928 | 0.04653 | 0.084176 | -0.059167 | 0.18317 | 0.11094 | 0.097201 | 0.06904 | 0.003172 | 0.057037 | 0.1007 | -0.14334 | -0.10462 | 121.1528 | -0.02111 | 121.1803 | 121.0884 | -0.064412 | -0.16445 | 0.077887 | 120.9372 | -0.048249 | 121.1391 | 121.045 | 0.1078 | -0.004586 | -0.24863 | 121.126 | 120.9827 | 121.225 | 121.1028 | 0.005656 | 121.0989 | 121.1426 | 120.8985 | 121.1109 | -0.20991
3001.3906 | 121.3165 | -121.1014 | 0.12817 | 1.4211e-13 | -0.028805 | -0.0036497 | -0.0099298 | -0.014542 | 0.01104 | -0.22823 | -0.0056742 | 0.013422 | 0.014062 | 0.045722 | -0.0005555 | 0.1384 | 0.05635 | 0.051108 | 0.079598 | -0.059167 | 0.18317 | 0.10636 | 0.097201 | 0.082776 | -0.001407 | 0.057037 | 0.1007 | -0.14334 | -0.1092 | 121.2077 | -0.048576 | 121.2398 | 121.1525 | -0.055255 | -0.18734 | 0.054999 | 120.9922 | -0.071137 | 121.1986 | 121.1 | 0.1078 | -0.027474 | -0.27152 | 121.181 | 121.0422 | 121.2846 | 121.1577 | -0.021811 | 121.1584 | 121.2021 | 120.958 | 121.1842 | -0.23738
3003.125 | 120.7809 | -120.4056 | 0.10071 | 1.4211e-13 | -0.029019 | -0.0038633 | -0.0097162 | -0.014542 | 0.010826 | -0.24349 | -0.005247 | 0.013636 | 0.014062 | 0.046149 | -0.0005555 | 0.15213 | 0.070086 | 0.04653 | 0.088755 | -0.050009 | 0.1786 | 0.10178 | 0.092622 | 0.06904 | -0.005985 | 0.066194 | 0.1007 | -0.13419 | -0.1092 | 120.5074 | -0.011953 | 120.5577 | 120.4521 | -0.055254 | -0.15072 | 0.077887 | 120.2964 | -0.034514 | 120.4982 | 120.3996 | 0.10322 | -8e-06 | -0.23489 | 120.4943 | 120.3556 | 120.5842 | 120.4757 | 0.001076 | 120.4718 | 120.5063 | 120.2714 | 120.4746 | -0.20991
3004.8125 | 121.1838 | -120.8908 | 0.10071 | 1.4211e-13 | -0.029233 | -0.0034359 | -0.0095024 | -0.014542 | 0.01104 | -0.23586 | -0.005247 | 0.013636 | 0.01449 | 0.045935 | -0.0007691 | 0.13382 | 0.060928 | 0.04653 | 0.093333 | -0.059167 | 0.17402 | 0.10178 | 0.088043 | 0.06904 | -0.001407 | 0.052459 | 0.1007 | -0.14334 | -0.10462 | 120.9926 | -0.007375 | 121.0246 | 120.9373 | -0.055254 | -0.15987 | 0.073308 | 120.7862 | -0.048249 | 120.9789 | 120.8894 | 0.10322 | -8e-06 | -0.24405 | 120.9841 | 120.8316 | 121.0648 | 120.9517 | 0.001076 | 120.9433 | 120.9915 | 120.7475 | 120.9598 | -0.20533
3006.5469 | 121.2616 | -120.9778 | 0.10071 | 1.4211e-13 | -0.029446 | -0.0040769 | -0.0099298 | -0.014328 | 0.010613 | -0.2206 | -0.005247 | 0.013636 | 0.014276 | 0.045935 | -0.0007691 | 0.13382 | 0.060928 | 0.051108 | 0.088755 | -0.059167 | 0.1786 | 0.10178 | 0.097201 | 0.073618 | 0.003172 | 0.057037 | 0.10528 | -0.12961 | -0.10462 | 121.0796 | -0.011953 | 121.1116 | 121.0289 | -0.050676 | -0.15987 | 0.077887 | 120.8732 | -0.043671 | 121.075 | 120.981 | 0.1078 | 0.004571 | -0.23031 | 121.0665 | 120.9186 | 121.1564 | 121.0387 | 0.001076 | 121.0348 | 121.0831 | 120.8482 | 121.0514 | -0.20533
3008.2969 | 117.6178 | -92.6102 | 24.7971 | 1.4211e-13 | -0.029019 | -0.0040769 | -0.010785 | -0.014328 | 0.0099716 | -0.22823 | -0.005247 | 0.013849 | 0.014276 | 0.045935 | -0.0009829 | 0.21623 | 0.13876 | 0.10147 | 0.11622 | 0.032411 | 0.21064 | 0.023942 | 0.02852 | 0.018674 | -0.047194 | -0.016219 | 0.045757 | -0.12503 | -0.16415 | 92.6341 | -24.6808 | 92.8264 | 92.7116 | 0.077527 | -24.7646 | -24.5864 | 92.446 | -24.8133 | 92.6387 | 92.563 | 0.11695 | -24.7513 | -24.9221 | 92.7264 | 92.6426 | 92.8208 | 92.7489 | -24.7731 | 92.5939 | 92.6559 | 92.4851 | 92.6288 | -24.9612
3010.0469 | 121.1472 | -120.8038 | 0.10071 | 1.4211e-13 | -0.028805 | -0.0034359 | -0.0099298 | -0.014328 | 0.010826 | -0.23586 | -0.0056742 | 0.013422 | 0.014276 | 0.046149 | -0.0009829 | 0.14298 | 0.051771 | 0.041952 | 0.088755 | -0.063746 | 0.18775 | 0.10636 | 0.092622 | 0.064461 | -0.001407 | 0.043302 | 0.10986 | -0.13876 | -0.1092 | 120.9102 | -0.011953 | 120.9468 | 120.8458 | -0.064411 | -0.16445 | 0.087044 | 120.6946 | -0.057406 | 120.8965 | 120.8024 | 0.1078 | 0.009149 | -0.23947 | 120.8926 | 120.7401 | 120.9916 | 120.8556 | 0.005655 | 120.8471 | 120.9137 | 120.6651 | 120.8683 | -0.20991
3011.7969 | 121.2296 | -120.8862 | 0.086975 | 1.4211e-13 | -0.029233 | -0.0040769 | -0.0097162 | -0.014756 | 0.011254 | -0.24349 | -0.0054606 | 0.013422 | 0.014062 | 0.046149 | -0.0011965 | 0.12924 | 0.060928 | 0.041952 | 0.088755 | -0.059167 | 0.18317 | 0.092626 | 0.088043 | 0.073618 | -0.001407 | 0.04788 | 0.10986 | -0.13876 | -0.1092 | 120.9789 | 0.00178 | 121.0155 | 120.9282 | -0.050674 | -0.14614 | 0.096198 | 120.777 | -0.039095 | 120.9743 | 120.8848 | 0.1078 | 0.022882 | -0.22574 | 120.975 | 120.8271 | 121.0694 | 120.9472 | 0.005651 | 120.9341 | 120.9961 | 120.7475 | 120.9598 | -0.19618
3013.5 | 121.2112 | -120.9778 | 0.10986 | 1.4211e-13 | -0.029446 | -0.0038633 | -0.0097162 | -0.014756 | 0.010826 | -0.24349 | -0.0054606 | 0.013422 | 0.014062 | 0.045722 | -0.0009829 | 0.14756 | 0.060928 | 0.04653 | 0.088755 | -0.063746 | 0.18317 | 0.10178 | 0.092622 | 0.078197 | -0.001407 | 0.04788 | 0.10528 | -0.14334 | -0.10004 | 121.0796 | -0.021108 | 121.1253 | 121.0243 | -0.055254 | -0.17361 | 0.07331 | 120.8777 | -0.061983 | 121.0704 | 120.9764 | 0.098638 | -0.004584 | -0.25321 | 121.0665 | 120.914 | 121.161 | 121.0387 | -0.008079 | 121.0257 | 121.0831 | 120.8344 | 121.056 | -0.20991
3015.25 | 121.3211 | -121.0281 | 0.07782 | 1.4211e-13 | -0.029233 | -0.0038633 | -0.0099298 | -0.014542 | 0.010826 | -0.25112 | -0.0054606 | 0.013422 | 0.014062 | 0.046149 | -0.0009829 | 0.14298 | 0.051771 | 0.041952 | 0.088755 | -0.054588 | 0.1786 | 0.10178 | 0.092622 | 0.06904 | -0.001407 | 0.052459 | 0.10986 | -0.14334 | -0.1092 | 121.1299 | 0.010935 | 121.1711 | 121.0701 | -0.059832 | -0.13241 | 0.10078 | 120.9189 | -0.025361 | 121.1208 | 121.0267 | 0.1078 | 0.032037 | -0.22116 | 121.1169 | 120.9735 | 121.2067 | 121.0799 | 0.023964 | 121.0806 | 121.138 | 120.8848 | 121.0972 | -0.18702
3016.9219 | 121.2204 | -121.0739 | 0.11444 | 1.4211e-13 | -0.029446 | -0.0038633 | -0.0097162 | -0.014328 | 0.010399 | -0.23586 | -0.0056742 | 0.013422 | 0.014062 | 0.046363 | -0.0007691 | 0.14298 | 0.05635 | 0.04653 | 0.093333 | -0.059167 | 0.18317 | 0.097205 | 0.097201 | 0.073618 | 0.003172 | 0.052459 | 0.10528 | -0.14334 | -0.10462 | 121.1711 | -0.021108 | 121.2169 | 121.1204 | -0.050675 | -0.17361 | 0.068732 | 120.9693 | -0.061982 | 121.1711 | 121.0771 | 0.1078 | -0.009162 | -0.25778 | 121.1672 | 121.0147 | 121.2571 | 121.1303 | -0.017236 | 121.1264 | 121.1792 | 120.9306 | 121.1475 | -0.21907
3018.6719 | 121.2845 | -121.106 | 0.1236 | 1.4211e-13 | -0.029233 | -0.0038633 | -0.0097162 | -0.014542 | 0.010613 | -0.23586 | -0.005247 | 0.013636 | 0.01449 | 0.045935 | -0.0005555 | 0.1384 | 0.05635 | 0.04653 | 0.088755 | -0.054588 | 0.18317 | 0.10178 | 0.092622 | 0.06904 | 0.003172 | 0.043302 | 0.10986 | -0.13876 | -0.10462 | 121.2077 | -0.034841 | 121.2444 | 121.1525 | -0.055254 | -0.17818 | 0.059577 | 121.0013 | -0.080294 | 121.1986 | 121.1091 | 0.1078 | -0.013739 | -0.26236 | 121.1947 | 121.0514 | 121.2891 | 121.1623 | -0.021812 | 121.1493 | 121.2158 | 120.9672 | 121.175 | -0.22822
3020.4219 | 121.3257 | -121.1014 | 0.10071 | 1.4211e-13 | -0.029446 | -0.0036497 | -0.0097162 | -0.014756 | 0.010185 | -0.24349 | -0.0054606 | 0.013849 | 0.014276 | 0.045935 | -0.0009829 | 0.1384 | 0.05635 | 0.041952 | 0.088755 | -0.068325 | 0.18317 | 0.097205 | 0.092622 | 0.078197 | 0.003172 | 0.052459 | 0.10986 | -0.13876 | -0.10004 | 121.1986 | -0.011953 | 121.2398 | 121.1433 | -0.055253 | -0.16903 | 0.082465 | 121.0013 | -0.048249 | 121.194 | 121.1046 | 0.10322 | 0.009149 | -0.23947 | 121.1901 | 121.0331 | 121.2846 | 121.1577 | -0.003503 | 121.1538 | 121.2112 | 120.9626 | 121.1796 | -0.20075
3022.1094 | 121.3028 | -121.1472 | 0.10986 | 1.4211e-13 | -0.029019 | -0.0038633 | -0.0099298 | -0.014756 | 0.010185 | -0.23586 | -0.0054606 | 0.013849 | 0.014276 | 0.046149 | -0.0007691 | 0.13382 | 0.060928 | 0.04653 | 0.097912 | -0.059167 | 0.18317 | 0.10636 | 0.092622 | 0.06904 | 0.01233 | 0.04788 | 0.10986 | -0.13876 | -0.10462 | 121.2535 | -0.011951 | 121.281 | 121.1937 | -0.059833 | -0.16903 | 0.07331 | 121.0425 | -0.061983 | 121.2398 | 121.1595 | 0.11695 | -6e-06 | -0.24863 | 121.2451 | 121.088 | 121.3303 | 121.2081 | -0.0035 | 121.195 | 121.257 | 121.0084 | 121.2162 | -0.21449
3023.8594 | 121.4355 | -121.1288 | 0.07782 | 1.4211e-13 | -0.029019 | -0.0040769 | -0.0097162 | -0.014756 | 0.010399 | -0.22823 | -0.005247 | 0.013422 | 0.014276 | 0.046149 | -0.0009829 | 0.13382 | 0.051771 | 0.041952 | 0.088755 | -0.063746 | 0.1786 | 0.10178 | 0.083464 | 0.073618 | -0.005985 | 0.038723 | 0.10528 | -0.14792 | -0.10004 | 121.2306 | 0.010935 | 121.2627 | 121.1708 | -0.059832 | -0.14157 | 0.10078 | 121.0288 | -0.039097 | 121.2123 | 121.1229 | 0.09406 | 0.027459 | -0.22574 | 121.2176 | 121.0651 | 121.3074 | 121.1806 | 0.023964 | 121.1676 | 121.2341 | 120.9809 | 121.2025 | -0.17786
3025.5469 | 121.4172 | -121.1426 | 0.10986 | 1.4211e-13 | -0.02966 | -0.0036497 | -0.0099298 | -0.014969 | 0.010826 | -0.22823 | -0.0054606 | 0.013422 | 0.014276 | 0.045935 | -0.0007691 | 0.13382 | 0.047193 | 0.04653 | 0.088755 | -0.063746 | 0.18317 | 0.097205 | 0.092622 | 0.06904 | -0.001407 | 0.04788 | 0.10528 | -0.13876 | -0.10004 | 121.2398 | -0.021108 | 121.2764 | 121.1891 | -0.050675 | -0.17361 | 0.07331 | 121.0425 | -0.061983 | 121.2352 | 121.1412 | 0.098638 | -0.004584 | -0.24863 | 121.2313 | 121.0788 | 121.3258 | 121.1898 | -0.012658 | 121.1905 | 121.2479 | 121.0038 | 121.2116 | -0.20991
3027.2812 | 121.4813 | -121.1472 | 0.10986 | 1.4211e-13 | -0.029019 | -0.0040769 | -0.010144 | -0.014969 | 0.010613 | -0.23586 | -0.0058878 | 0.013422 | 0.014062 | 0.046149 | -0.0009829 | 0.13382 | 0.047193 | 0.028217 | 0.088755 | -0.059167 | 0.18317 | 0.10636 | 0.092622 | 0.064461 | 0.007751 | 0.052459 | 0.11901 | -0.13876 | -0.10004 | 121.2535 | -0.021108 | 121.281 | 121.1754 | -0.078146 | -0.16903 | 0.07331 | 121.0471 | -0.057404 | 121.2398 | 121.1549 | 0.1078 | 0.009151 | -0.24863 | 121.2359 | 121.088 | 121.3303 | 121.1943 | -0.0035 | 121.1996 | 121.2662 | 121.0084 | 121.2116 | -0.20991
3029.0312 | 121.4676 | -121.1838 | 0.09613 | 1.4211e-13 | -0.029233 | -0.0038633 | -0.0097162 | -0.014756 | 0.010613 | -0.23586 | -0.0054606 | 0.013636 | 0.014276 | 0.046363 | -0.0005555 | 0.13382 | 0.051771 | 0.041952 | 0.088755 | -0.063746 | 0.18775 | 0.097205 | 0.092622 | 0.059882 | 0.007751 | 0.038723 | 0.10528 | -0.13876 | -0.10462 | 121.281 | -0.007375 | 121.3176 | 121.2257 | -0.055253 | -0.15988 | 0.091622 | 121.0792 | -0.057407 | 121.2764 | 121.1915 | 0.11237 | 0.009149 | -0.23489 | 121.2725 | 121.12 | 121.3715 | 121.2355 | 0.001075 | 121.2225 | 121.2891 | 121.045 | 121.2437 | -0.20075
3030.7812 | 121.4172 | -121.2433 | 0.13733 | 1.4211e-13 | -0.029446 | -0.0040769 | -0.0097162 | -0.014756 | 0.010185 | -0.23586 | -0.0058878 | 0.013208 | 0.014276 | 0.045935 | -0.0009829 | 0.1384 | 0.051771 | 0.037373 | 0.088755 | -0.063746 | 0.18775 | 0.10636 | 0.097201 | 0.06904 | -0.005985 | 0.04788 | 0.1007 | -0.13419 | -0.10004 | 121.3496 | -0.048574 | 121.3817 | 121.2807 | -0.06899 | -0.20108 | 0.050423 | 121.1432 | -0.089449 | 121.3405 | 121.2373 | 0.09406 | -0.036629 | -0.27152 | 121.332 | 121.1795 | 121.431 | 121.2951 | -0.030966 | 121.2912 | 121.344 | 121.1091 | 121.3123 | -0.23737
3032.4688 | 121.5134 | -121.1975 | 0.10986 | 1.4211e-13 | -0.029446 | -0.0038633 | -0.010144 | -0.014542 | 0.010613 | -0.23586 | -0.0054606 | 0.013422 | 0.014276 | 0.046149 | -0.0009829 | 0.1384 | 0.051771 | 0.037373 | 0.097912 | -0.059167 | 0.18775 | 0.10636 | 0.092622 | 0.073618 | 0.003172 | 0.04788 | 0.10528 | -0.13876 | -0.10004 | 121.3039 | -0.011951 | 121.3359 | 121.2349 | -0.06899 | -0.16903 | 0.077889 | 121.0975 | -0.061983 | 121.2901 | 121.2007 | 0.10322 | -0.004584 | -0.24863 | 121.2954 | 121.1383 | 121.3853 | 121.2493 | -0.0035 | 121.2454 | 121.3028 | 121.0587 | 121.2711 | -0.20991
3034.2188 | 121.4172 | -121.2662 | 0.10529 | 1.4211e-13 | -0.029446 | -0.0038633 | -0.010144 | -0.014756 | 0.010613 | -0.24349 | -0.0056742 | 0.013422 | 0.014062 | 0.046149 | -0.0011965 | 0.13382 | 0.047193 | 0.037373 | 0.093333 | -0.059167 | 0.19233 | 0.097205 | 0.092622 | 0.073618 | 0.007751 | 0.038723 | 0.096121 | -0.13876 | -0.10004 | 121.3634 | -0.011953 | 121.4 | 121.3035 | -0.059832 | -0.16445 | 0.087045 | 121.1661 | -0.066563 | 121.3588 | 121.2739 | 0.1078 | -0.009165 | -0.24405 | 121.3595 | 121.207 | 121.4585 | 121.3134 | -0.008081 | 121.3049 | 121.3623 | 121.1274 | 121.3398 | -0.20533
3035.9688 | 121.4218 | -121.2662 | 0.10986 | 1.4211e-13 | -0.02966 | -0.0038633 | -0.0099298 | -0.014542 | 0.010613 | -0.23586 | -0.0054606 | 0.013422 | 0.014276 | 0.046149 | -0.0009829 | 0.13382 | 0.047193 | 0.037373 | 0.093333 | -0.054588 | 0.18775 | 0.10636 | 0.10178 | 0.06904 | -0.005985 | 0.043302 | 0.10528 | -0.13876 | -0.10004 | 121.3725 | -0.01653 | 121.4 | 121.3035 | -0.06899 | -0.16445 | 0.077889 | 121.1661 | -0.066561 | 121.368 | 121.2602 | 0.09406 | -0.004584 | -0.24863 | 121.3595 | 121.2116 | 121.4539 | 121.3134 | -0.0035 | 121.3095 | 121.3715 | 121.1274 | 121.3352 | -0.20991
3037.7344 | 121.5683 | -121.2204 | 0.09613 | 1.4211e-13 | -0.02966 | -0.0038633 | -0.0099298 | -0.014969 | 0.010399 | -0.23586 | -0.0054606 | 0.013636 | 0.014276 | 0.046149 | -0.0009829 | 0.13382 | 0.047193 | 0.041952 | 0.093333 | -0.063746 | 0.18775 | 0.097205 | 0.088043 | 0.073618 | -0.001407 | 0.04788 | 0.10986 | -0.13876 | -0.1092 | 121.3176 | -0.002797 | 121.3542 | 121.2623 | -0.055253 | -0.15988 | 0.091622 | 121.1112 | -0.04825 | 121.3084 | 121.219 | 0.1078 | 0.013727 | -0.23489 | 121.3137 | 121.1567 | 121.4082 | 121.2676 | 0.001075 | 121.2683 | 121.3303 | 121.0816 | 121.294 | -0.20533
3039.4219 | 121.5042 | -121.2799 | 0.11444 | 1.4211e-13 | -0.029446 | -0.0042907 | -0.0097162 | -0.014756 | 0.010613 | -0.23586 | -0.0054606 | 0.013636 | 0.014276 | 0.046149 | -0.0014101 | 0.13382 | 0.047193 | 0.037373 | 0.097912 | -0.059167 | 0.18317 | 0.10178 | 0.097201 | 0.073618 | 0.007751 | 0.04788 | 0.10528 | -0.13419 | -0.10004 | 121.3817 | -0.016529 | 121.4137 | 121.3173 | -0.064411 | -0.17361 | 0.068732 | 121.1799 | -0.066561 | 121.3771 | 121.2877 | 0.1078 | -0.009162 | -0.24863 | 121.3778 | 121.2207 | 121.4631 | 121.3271 | -0.012657 | 121.3278 | 121.3852 | 121.1457 | 121.3535 | -0.21449
3041.1562 | 121.2708 | -121.0876 | 0.11902 | 1.4211e-13 | -0.02966 | -0.0038633 | -0.010144 | -0.014969 | 0.010399 | -0.23586 | -0.0054606 | 0.013422 | 0.014062 | 0.046363 | -0.0009829 | 0.13382 | 0.047193 | 0.04653 | 0.097912 | -0.059167 | 0.18775 | 0.10636 | 0.092622 | 0.078197 | -0.001407 | 0.052459 | 0.1007 | -0.13419 | -0.10462 | 121.194 | -0.021107 | 121.2215 | 121.1342 | -0.059833 | -0.17819 | 0.068733 | 120.983 | -0.06656 | 121.1803 | 121.0862 | 0.10322 | -0.018319 | -0.25321 | 121.1856 | 121.0285 | 121.2754 | 121.1348 | -0.012656 | 121.1401 | 121.1883 | 120.9535 | 121.1658 | -0.22364
3042.9062 | 121.4127 | -121.1563 | 0.12817 | 1.4211e-13 | -0.02966 | -0.0038633 | -0.0095024 | -0.014542 | 0.010399 | -0.23586 | -0.005247 | 0.013422 | 0.014062 | 0.046363 | -0.0009829 | 0.13382 | 0.051771 | 0.041952 | 0.084176 | -0.063746 | 0.18775 | 0.10178 | 0.097201 | 0.06904 | 0.003172 | 0.052459 | 0.10528 | -0.14334 | -0.10462 | 121.2581 | -0.043998 | 121.2901 | 121.1983 | -0.059832 | -0.19192 | 0.059578 | 121.0517 | -0.075715 | 121.2535 | 121.1595 | 0.1078 | -0.022895 | -0.27152 | 121.2405 | 121.0926 | 121.3441 | 121.2081 | -0.02639 | 121.2088 | 121.2616 | 121.013 | 121.2254 | -0.2328
3044.5938 | 121.4859 | -121.1884 | 0.10986 | 1.4211e-13 | -0.02966 | -0.0040769 | -0.0099298 | -0.014756 | 0.010399 | -0.23586 | -0.005247 | 0.013849 | 0.014276 | 0.046149 | -0.0011965 | 0.12466 | 0.051771 | 0.037373 | 0.097912 | -0.054588 | 0.18775 | 0.10178 | 0.092622 | 0.06904 | 0.003172 | 0.052459 | 0.10986 | -0.13876 | -0.10462 | 121.2901 | -0.011951 | 121.313 | 121.2257 | -0.064411 | -0.16445 | 0.077889 | 121.0837 | -0.057404 | 121.281 | 121.1915 | 0.1078 | -6e-06 | -0.24863 | 121.2863 | 121.1338 | 121.3761 | 121.2401 | -0.008079 | 121.2408 | 121.2982 | 121.0496 | 121.2574 | -0.21449
3046.3438 | 121.4172 | -121.257 | 0.13733 | 1.4211e-13 | -0.02966 | -0.0045043 | -0.010144 | -0.014328 | 0.010399 | -0.23586 | -0.0054606 | 0.013636 | 0.013849 | 0.046149 | -0.0007691 | 0.11093 | 0.05635 | 0.037373 | 0.093333 | -0.059167 | 0.18775 | 0.10178 | 0.097201 | 0.073618 | 0.007751 | 0.052459 | 0.10528 | -0.14334 | -0.10004 | 121.3588 | -0.043996 | 121.3679 | 121.2944 | -0.064411 | -0.1965 | 0.050423 | 121.157 | -0.08487 | 121.3542 | 121.2648 | 0.1078 | -0.03205 | -0.28067 | 121.3504 | 121.1979 | 121.4448 | 121.3134 | -0.035545 | 121.3095 | 121.3623 | 121.1137 | 121.3306 | -0.23737
3048.0938 | 121.4493 | -121.2524 | 0.10529 | 1.4211e-13 | -0.029874 | -0.0038633 | -0.010144 | -0.014756 | 0.010185 | -0.23586 | -0.0054606 | 0.013636 | 0.014276 | 0.04679 | -0.0011965 | 0.11093 | 0.051771 | 0.041952 | 0.093333 | -0.054588 | 0.19233 | 0.097205 | 0.088043 | 0.073618 | 0.003172 | 0.038723 | 0.10528 | -0.13876 | -0.10462 | 121.3496 | -0.011953 | 121.3634 | 121.2944 | -0.055253 | -0.15987 | 0.087045 | 121.1478 | -0.066563 | 121.3405 | 121.2556 | 0.1078 | -7e-06 | -0.24405 | 121.3458 | 121.1979 | 121.4448 | 121.3042 | -0.008081 | 121.2912 | 121.3577 | 121.1137 | 121.3261 | -0.20991
3049.8438 | 121.5591 | -121.2524 | 0.10529 | 1.4211e-13 | -0.02966 | -0.0040769 | -0.0097162 | -0.014328 | 0.010185 | -0.23586 | -0.005247 | 0.013636 | 0.014276 | 0.047004 | -0.0007691 | 0.11093 | 0.042614 | 0.037373 | 0.088755 | -0.063746 | 0.18775 | 0.097205 | 0.092622 | 0.06904 | -0.001407 | 0.04788 | 0.10528 | -0.14792 | -0.10462 | 121.3496 | -0.016531 | 121.3634 | 121.2898 | -0.059832 | -0.16903 | 0.082466 | 121.1478 | -0.057406 | 121.3451 | 121.251 | 0.10322 | -7e-06 | -0.25321 | 121.3412 | 121.1887 | 121.4402 | 121.2951 | -0.008081 | 121.3003 | 121.3577 | 121.1045 | 121.3215 | -0.20991
3051.5156 | 121.5088 | -121.2799 | 0.12817 | 1.4211e-13 | -0.029874 | -0.0038633 | -0.0099298 | -0.015183 | 0.010826 | -0.23586 | -0.0056742 | 0.013636 | 0.014062 | 0.046363 | -0.0009829 | 0.11551 | 0.042614 | 0.041952 | 0.088755 | -0.063746 | 0.1786 | 0.097205 | 0.092622 | 0.064461 | -0.001407 | 0.04788 | 0.10528 | -0.13419 | -0.1092 | 121.3771 | -0.039419 | 121.3954 | 121.3219 | -0.055253 | -0.19192 | 0.050421 | 121.1707 | -0.080294 | 121.3725 | 121.2785 | 0.1078 | -0.022895 | -0.26236 | 121.3687 | 121.2162 | 121.4585 | 121.3225 | -0.030969 | 121.3278 | 121.3852 | 121.1457 | 121.3444 | -0.23738
3053.2656 | 121.4813 | -121.3348 | 0.10986 | 1.4211e-13 | -0.02966 | -0.0042907 | -0.0099298 | -0.015183 | 0.010185 | -0.24349 | -0.0054606 | 0.013422 | 0.014062 | 0.046149 | -0.0009829 | 0.11551 | 0.051771 | 0.037373 | 0.093333 | -0.059167 | 0.19233 | 0.11094 | 0.088043 | 0.064461 | -0.001407 | 0.043302 | 0.10528 | -0.14792 | -0.10462 | 121.4458 | -0.01653 | 121.4503 | 121.3722 | -0.073569 | -0.16903 | 0.082468 | 121.2302 | -0.066561 | 121.4229 | 121.3334 | 0.10322 | -0.004584 | -0.25778 | 121.4282 | 121.2757 | 121.5272 | 121.3866 | 0.001079 | 121.3781 | 121.4401 | 121.1869 | 121.3993 | -0.21449
3054.9688 | 121.6232 | -121.2753 | 0.082397 | 1.4211e-13 | -0.030087 | -0.0040769 | -0.0099298 | -0.014969 | 0.010613 | -0.22823 | -0.0056742 | 0.013422 | 0.013849 | 0.046576 | -0.0014101 | 0.11093 | 0.051771 | 0.041952 | 0.093333 | -0.059167 | 0.19233 | 0.10636 | 0.092622 | 0.06904 | 0.003172 | 0.043302 | 0.10528 | -0.13876 | -0.10462 | 121.3817 | 0.010936 | 121.3863 | 121.3173 | -0.064411 | -0.14156 | 0.10993 | 121.1707 | -0.039095 | 121.368 | 121.2785 | 0.1078 | 0.022882 | -0.22116 | 121.3687 | 121.2162 | 121.4677 | 121.3271 | 0.023966 | 121.3186 | 121.3806 | 121.1366 | 121.3444 | -0.18702
3056.7188 | 121.6232 | -121.3348 | 0.10529 | 1.4211e-13 | -0.030301 | -0.0040769 | -0.010144 | -0.014969 | 0.010613 | -0.23586 | -0.0054606 | 0.013849 | 0.013849 | 0.046149 | -0.0011965 | 0.11551 | 0.047193 | 0.037373 | 0.097912 | -0.059167 | 0.18775 | 0.10178 | 0.092622 | 0.06904 | 0.01233 | 0.043302 | 0.10986 | -0.13876 | -0.10004 | 121.4366 | -0.007374 | 121.4503 | 121.3722 | -0.064411 | -0.16445 | 0.082466 | 121.2348 | -0.061984 | 121.4275 | 121.3472 | 0.11238 | 0.004571 | -0.24405 | 121.4328 | 121.2757 | 121.5226 | 121.382 | -0.003502 | 121.3781 | 121.4447 | 121.1961 | 121.4039 | -0.20533
3058.4688 | 121.6599 | -121.3165 | 0.10986 | 1.4211e-13 | -0.030087 | -0.0042907 | -0.0097162 | -0.014542 | 0.010399 | -0.2206 | -0.0054606 | 0.013208 | 0.014276 | 0.046363 | -0.0014101 | 0.11551 | 0.047193 | 0.032795 | 0.093333 | -0.054588 | 0.18317 | 0.10636 | 0.097201 | 0.06904 | -0.001407 | 0.052459 | 0.10528 | -0.14334 | -0.10004 | 121.4229 | -0.01653 | 121.432 | 121.3493 | -0.073568 | -0.16445 | 0.07331 | 121.2165 | -0.057404 | 121.4137 | 121.3151 | 0.098638 | -0.004584 | -0.25321 | 121.4099 | 121.2619 | 121.4997 | 121.3637 | -0.0035 | 121.369 | 121.4218 | 121.1732 | 121.3856 | -0.20991
3060.1406 | 121.5317 | -121.376 | 0.12817 | 1.4211e-13 | -0.02966 | -0.0038633 | -0.0099298 | -0.014969 | 0.010613 | -0.2206 | -0.0056742 | 0.013422 | 0.014062 | 0.046149 | -0.0009829 | 0.12009 | 0.051771 | 0.032795 | 0.093333 | -0.059167 | 0.18775 | 0.10178 | 0.088043 | 0.06904 | 0.003172 | 0.052459 | 0.10986 | -0.14334 | -0.11378 | 121.4778 | -0.034841 | 121.4961 | 121.4088 | -0.068989 | -0.18734 | 0.059578 | 121.2623 | -0.075715 | 121.4641 | 121.3792 | 0.11695 | -0.018317 | -0.27152 | 121.4694 | 121.3169 | 121.5638 | 121.4278 | -0.02639 | 121.4285 | 121.4859 | 121.2327 | 121.4451 | -0.24196
3061.8906 | 121.6187 | -121.3623 | 0.11902 | 1.4211e-13 | -0.02966 | -0.0040769 | -0.0099298 | -0.014969 | 0.010613 | -0.22823 | -0.0056742 | 0.013208 | 0.014703 | 0.046363 | -0.0009829 | 0.12009 | 0.047193 | 0.032795 | 0.093333 | -0.063746 | 0.19233 | 0.097205 | 0.092622 | 0.073618 | 0.007751 | 0.043302 | 0.10528 | -0.13876 | -0.1092 | 121.4595 | -0.025686 | 121.4824 | 121.3951 | -0.06441 | -0.18277 | 0.073312 | 121.2531 | -0.075717 | 121.4549 | 121.3701 | 0.11695 | -0.01374 | -0.25778 | 121.4556 | 121.2986 | 121.5546 | 121.4095 | -0.021814 | 121.4056 | 121.4676 | 121.2235 | 121.4359 | -0.22822
3063.625 | 121.5317 | -121.3852 | 0.11902 | 1.4211e-13 | -0.02966 | -0.0038633 | -0.010144 | -0.014969 | 0.010399 | -0.23586 | -0.005247 | 0.013208 | 0.013849 | 0.046149 | -0.0009829 | 0.11551 | 0.051771 | 0.032795 | 0.093333 | -0.054588 | 0.18775 | 0.10636 | 0.092622 | 0.06904 | 0.003172 | 0.04788 | 0.1007 | -0.13876 | -0.10462 | 121.4916 | -0.025686 | 121.5007 | 121.418 | -0.073568 | -0.17361 | 0.068733 | 121.2806 | -0.071139 | 121.4778 | 121.3884 | 0.1078 | -0.018319 | -0.25778 | 121.4785 | 121.3306 | 121.5729 | 121.437 | -0.012656 | 121.4331 | 121.4859 | 121.2464 | 121.4542 | -0.22364
3065.375 | 121.669 | -121.376 | 0.086975 | 1.4211e-13 | -0.029874 | -0.0038633 | -0.010144 | -0.014756 | 0.010613 | -0.22823 | -0.005247 | 0.013636 | 0.013849 | 0.046363 | -0.0011965 | 0.11551 | 0.047193 | 0.032795 | 0.097912 | -0.063746 | 0.18317 | 0.10178 | 0.097201 | 0.06904 | -0.005985 | 0.04788 | 0.11444 | -0.13876 | -0.10462 | 121.4778 | 0.010937 | 121.4915 | 121.4088 | -0.068989 | -0.15072 | 0.096198 | 121.2714 | -0.039095 | 121.4732 | 121.3701 | 0.098639 | 0.027461 | -0.22574 | 121.4739 | 121.3123 | 121.5592 | 121.4232 | 0.014809 | 121.4239 | 121.4905 | 121.2373 | 121.4451 | -0.1916
3067.0625 | 121.5729 | -121.431 | 0.12817 | 1.4211e-13 | -0.029874 | -0.0038633 | -0.0097162 | -0.014969 | 0.010613 | -0.23586 | -0.0058878 | 0.013208 | 0.013849 | 0.04679 | -0.0009829 | 0.11093 | 0.047193 | 0.037373 | 0.10249 | -0.050009 | 0.19233 | 0.10636 | 0.097201 | 0.06904 | 0.003172 | 0.043302 | 0.10986 | -0.13876 | -0.11378 | 121.5373 | -0.025684 | 121.5419 | 121.4683 | -0.06899 | -0.17818 | 0.064157 | 121.3172 | -0.084872 | 121.5282 | 121.4341 | 0.11695 | -0.018317 | -0.26694 | 121.5335 | 121.381 | 121.6233 | 121.4782 | -0.021811 | 121.4743 | 121.5408 | 121.2922 | 121.5 | -0.24196
3068.8281 | 121.7148 | -121.3852 | 0.082397 | 1.4211e-13 | -0.029874 | -0.0040769 | -0.0099298 | -0.015183 | 0.010613 | -0.23586 | -0.0054606 | 0.013636 | 0.013849 | 0.046363 | -0.0009829 | 0.11551 | 0.05635 | 0.041952 | 0.093333 | -0.059167 | 0.19233 | 0.097205 | 0.088043 | 0.078197 | -0.001407 | 0.04788 | 0.11444 | -0.13876 | -0.10462 | 121.4824 | 0.010936 | 121.5007 | 121.4271 | -0.055253 | -0.14156 | 0.10993 | 121.2806 | -0.034517 | 121.4732 | 121.3838 | 0.10322 | 0.032039 | -0.22116 | 121.4785 | 121.326 | 121.5775 | 121.4415 | 0.014808 | 121.4331 | 121.4996 | 121.2464 | 121.4634 | -0.18702
3070.5156 | 121.6324 | -121.4447 | 0.13275 | 1.4211e-13 | -0.030087 | -0.0042907 | -0.0099298 | -0.014969 | 0.010185 | -0.22823 | -0.0056742 | 0.013208 | 0.014062 | 0.04679 | -0.0009829 | 0.11551 | 0.047193 | 0.032795 | 0.093333 | -0.054588 | 0.19691 | 0.11094 | 0.092622 | 0.073618 | -0.001407 | 0.04788 | 0.10528 | -0.14792 | -0.10462 | 121.5556 | -0.039418 | 121.5602 | 121.4775 | -0.078147 | -0.18734 | 0.064158 | 121.3401 | -0.084871 | 121.5373 | 121.4433 | 0.10322 | -0.027472 | -0.28067 | 121.538 | 121.3901 | 121.6416 | 121.4919 | -0.021809 | 121.4926 | 121.55 | 121.2968 | 121.5183 | -0.23738
3072.2656 | 121.6599 | -121.431 | 0.12817 | 1.4211e-13 | -0.029874 | -0.0040769 | -0.0099298 | -0.014969 | 0.010399 | -0.22823 | -0.0056742 | 0.013422 | 0.014276 | 0.046363 | -0.0009829 | 0.12466 | 0.042614 | 0.037373 | 0.093333 | -0.063746 | 0.18775 | 0.11094 | 0.097201 | 0.06904 | 0.003172 | 0.052459 | 0.10986 | -0.14334 | -0.10462 | 121.5419 | -0.034841 | 121.5556 | 121.4683 | -0.073569 | -0.19192 | 0.059578 | 121.3263 | -0.075715 | 121.5282 | 121.4341 | 0.1078 | -0.018317 | -0.27152 | 121.5243 | 121.3672 | 121.6187 | 121.4736 | -0.017232 | 121.4834 | 121.5408 | 121.2876 | 121.5 | -0.2328
3073.9688 | 121.6049 | -121.463 | 0.13275 | 1.4211e-13 | -0.030301 | -0.0040769 | -0.0099298 | -0.014756 | 0.010185 | -0.2206 | -0.0056742 | 0.013422 | 0.013849 | 0.046363 | -0.0011965 | 0.11093 | 0.047193 | 0.032795 | 0.097912 | -0.059167 | 0.18775 | 0.10178 | 0.092622 | 0.06904 | 0.003172 | 0.052459 | 0.10986 | -0.13876 | -0.10462 | 121.5648 | -0.034839 | 121.5739 | 121.4958 | -0.068989 | -0.19192 | 0.055001 | 121.3584 | -0.080292 | 121.5556 | 121.4662 | 0.1078 | -0.022894 | -0.27152 | 121.5609 | 121.4038 | 121.6508 | 121.5102 | -0.030967 | 121.5155 | 121.5729 | 121.3242 | 121.5321 | -0.23738
3075.7188 | 121.637 | -121.4722 | 0.11902 | 1.4211e-13 | -0.030301 | -0.0038633 | -0.0097162 | -0.014756 | 0.010399 | -0.22823 | -0.0054606 | 0.013636 | 0.013849 | 0.046363 | -0.0011965 | 0.11551 | 0.042614 | 0.023639 | 0.088755 | -0.054588 | 0.19233 | 0.10636 | 0.097201 | 0.073618 | 0.003172 | 0.061616 | 0.10986 | -0.13876 | -0.095467 | 121.5785 | -0.030264 | 121.5877 | 121.4958 | -0.082724 | -0.17361 | 0.073312 | 121.3767 | -0.057403 | 121.5694 | 121.4753 | 0.098639 | -0.009162 | -0.25778 | 121.5609 | 121.4176 | 121.6645 | 121.5148 | -0.012656 | 121.5338 | 121.582 | 121.3334 | 121.5458 | -0.21449
3077.4688 | 121.7651 | -121.4172 | 0.10071 | 1.4211e-13 | -0.030515 | -0.0040769 | -0.0097162 | -0.014542 | 0.010185 | -0.23586 | -0.0054606 | 0.013208 | 0.013635 | 0.04679 | -0.0009829 | 0.11093 | 0.047193 | 0.032795 | 0.093333 | -0.036272 | 0.18775 | 0.10636 | 0.092622 | 0.06904 | 0.007751 | 0.04788 | 0.10986 | -0.13419 | -0.1092 | 121.5236 | -0.007375 | 121.5282 | 121.45 | -0.073568 | -0.13698 | 0.087044 | 121.308 | -0.052828 | 121.5099 | 121.425 | 0.11695 | 0.009149 | -0.23489 | 121.5106 | 121.381 | 121.605 | 121.4644 | 0.005655 | 121.4651 | 121.5271 | 121.2831 | 121.4863 | -0.20991
3079.1562 | 121.7102 | -121.4767 | 0.11444 | 1.4211e-13 | -0.030301 | -0.0040769 | -0.010144 | -0.014328 | 0.010399 | -0.22823 | -0.0056742 | 0.012995 | 0.014062 | 0.046576 | -0.0007691 | 0.11093 | 0.047193 | 0.028217 | 0.093333 | -0.054588 | 0.18775 | 0.10636 | 0.097201 | 0.06904 | -0.005985 | 0.038723 | 0.11444 | -0.14334 | -0.10004 | 121.5831 | -0.021108 | 121.5877 | 121.505 | -0.078146 | -0.16903 | 0.073311 | 121.3767 | -0.075718 | 121.5739 | 121.4708 | 0.09406 | -5e-06 | -0.25778 | 121.5701 | 121.4222 | 121.6645 | 121.5239 | -0.008078 | 121.5155 | 121.5912 | 121.3334 | 121.5458 | -0.21449
3080.9062 | 121.6553 | -121.5042 | 0.11902 | 1.4211e-13 | -0.030087 | -0.0042907 | -0.0099298 | -0.014756 | 0.010185 | -0.24349 | -0.0056742 | 0.013636 | 0.013849 | 0.046576 | -0.0011965 | 0.12009 | 0.047193 | 0.028217 | 0.084176 | -0.068325 | 0.19233 | 0.10636 | 0.092622 | 0.06904 | -0.001407 | 0.04788 | 0.11444 | -0.13876 | -0.11378 | 121.6106 | -0.034843 | 121.6243 | 121.5324 | -0.078146 | -0.18734 | 0.073312 | 121.3904 | -0.071139 | 121.5968 | 121.5028 | 0.11237 | -0.004583 | -0.25778 | 121.5884 | 121.4359 | 121.6965 | 121.5514 | -0.012656 | 121.5521 | 121.6186 | 121.3654 | 121.5733 | -0.2328
3082.5938 | 121.6873 | -121.4996 | 0.13733 | 1.4211e-13 | -0.030301 | -0.0038633 | -0.0097162 | -0.014756 | 0.010185 | -0.24349 | -0.0056742 | 0.013208 | 0.013849 | 0.046576 | -0.0011965 | 0.12009 | 0.042614 | 0.032795 | 0.093333 | -0.054588 | 0.18775 | 0.10178 | 0.10178 | 0.064461 | -0.001407 | 0.043302 | 0.10986 | -0.13876 | -0.10004 | 121.6014 | -0.043996 | 121.6197 | 121.5324 | -0.068989 | -0.19192 | 0.050423 | 121.3996 | -0.094027 | 121.6014 | 121.4982 | 0.098638 | -0.027472 | -0.27609 | 121.593 | 121.445 | 121.6874 | 121.5422 | -0.035545 | 121.5429 | 121.6095 | 121.3609 | 121.5641 | -0.23737
3084.3438 | 121.7972 | -121.4767 | 0.082397 | 1.4211e-13 | -0.030301 | -0.0040769 | -0.0099298 | -0.014756 | 0.010399 | -0.2206 | -0.0054606 | 0.012995 | 0.014062 | 0.04679 | -0.0014101 | 0.10635 | 0.042614 | 0.032795 | 0.097912 | -0.059167 | 0.18775 | 0.10636 | 0.097201 | 0.06904 | -0.005985 | 0.04788 | 0.10986 | -0.13419 | -0.10462 | 121.5831 | 0.015515 | 121.5831 | 121.5095 | -0.073568 | -0.14156 | 0.10536 | 121.3721 | -0.034517 | 121.5739 | 121.4708 | 0.098639 | 0.02746 | -0.21658 | 121.5747 | 121.4176 | 121.6645 | 121.5194 | 0.023966 | 121.5246 | 121.5866 | 121.3426 | 121.5458 | -0.18702
3086.0156 | 121.669 | -121.5042 | 0.12817 | 1.4211e-13 | -0.030087 | -0.0042907 | -0.010144 | -0.015183 | 0.010185 | -0.25112 | -0.0056742 | 0.013208 | 0.013849 | 0.046149 | -0.0011965 | 0.12009 | 0.047193 | 0.028217 | 0.093333 | -0.072904 | 0.18317 | 0.10636 | 0.097201 | 0.078197 | -0.005985 | 0.052459 | 0.11444 | -0.14334 | -0.10462 | 121.6106 | -0.034841 | 121.6243 | 121.5324 | -0.078146 | -0.20108 | 0.054999 | 121.3996 | -0.075715 | 121.6014 | 121.4982 | 0.098639 | -0.013738 | -0.27152 | 121.5975 | 121.4313 | 121.6874 | 121.5514 | -0.021811 | 121.5567 | 121.6186 | 121.3609 | 121.5824 | -0.2328
3087.7812 | 121.7789 | -121.4905 | 0.09613 | 1.4211e-13 | -0.030301 | -0.0040769 | -0.0099298 | -0.014756 | 0.010185 | -0.22823 | -0.0054606 | 0.012995 | 0.013849 | 0.046576 | -0.0011965 | 0.12009 | 0.042614 | 0.037373 | 0.097912 | -0.059167 | 0.18317 | 0.10636 | 0.088043 | 0.073618 | 0.003172 | 0.052459 | 0.11444 | -0.13876 | -0.1092 | 121.5968 | 0.001782 | 121.6106 | 121.5279 | -0.06899 | -0.1553 | 0.087043 | 121.3813 | -0.043671 | 121.5785 | 121.4937 | 0.11237 | 0.018306 | -0.23489 | 121.5884 | 121.4313 | 121.6737 | 121.5331 | 0.010233 | 121.5429 | 121.6049 | 121.3517 | 121.5641 | -0.20533
3089.5312 | 121.701 | -121.5363 | 0.1236 | 1.4211e-13 | -0.030301 | -0.0042907 | -0.010144 | -0.015183 | 0.010613 | -0.24349 | -0.0058878 | 0.013208 | 0.013421 | 0.046576 | -0.0009829 | 0.11093 | 0.038035 | 0.032795 | 0.097912 | -0.059167 | 0.18775 | 0.10178 | 0.092622 | 0.073618 | 0.003172 | 0.052459 | 0.10986 | -0.13876 | -0.10462 | 121.638 | -0.025684 | 121.6472 | 121.569 | -0.068989 | -0.18276 | 0.064156 | 121.4316 | -0.071137 | 121.6289 | 121.5394 | 0.1078 | -0.013739 | -0.26236 | 121.6342 | 121.4771 | 121.724 | 121.5743 | -0.021812 | 121.5887 | 121.6461 | 121.3975 | 121.6099 | -0.22822
3091.2031 | 121.7926 | -121.5317 | 0.10529 | 1.4211e-13 | -0.030515 | -0.0040769 | -0.010144 | -0.014756 | 0.010613 | -0.23586 | -0.0054606 | 0.013422 | 0.013635 | 0.046576 | -0.0009829 | 0.11093 | 0.038035 | 0.028217 | 0.088755 | -0.059167 | 0.18775 | 0.10178 | 0.10178 | 0.06904 | 0.003172 | 0.04788 | 0.11444 | -0.13876 | -0.1092 | 121.6335 | -0.016531 | 121.6426 | 121.5599 | -0.073567 | -0.16445 | 0.082466 | 121.4225 | -0.057406 | 121.6335 | 121.5348 | 0.11237 | 0.00915 | -0.24405 | 121.6204 | 121.4725 | 121.7194 | 121.5697 | -0.003502 | 121.5796 | 121.6461 | 121.3929 | 121.6007 | -0.21449
3092.9531 | 121.7789 | -121.5591 | 0.11444 | 1.4211e-13 | -0.030515 | -0.0040769 | -0.0099298 | -0.015183 | 0.010185 | -0.23586 | -0.0056742 | 0.013208 | 0.013635 | 0.04679 | -0.0009829 | 0.12009 | 0.038035 | 0.032795 | 0.093333 | -0.031693 | 0.18775 | 0.11094 | 0.092622 | 0.073618 | 0.003172 | 0.052459 | 0.11444 | -0.1525 | -0.10004 | 121.6701 | -0.021108 | 121.6792 | 121.5919 | -0.078147 | -0.14613 | 0.073311 | 121.4591 | -0.061982 | 121.6518 | 121.5623 | 0.10322 | -5e-06 | -0.26694 | 121.6525 | 121.5275 | 121.7469 | 121.5972 | -0.003499 | 121.6116 | 121.6736 | 121.4066 | 121.6328 | -0.21449
3094.6406 | 121.8613 | -121.5134 | 0.10986 | 1.4211e-13 | -0.030301 | -0.0040769 | -0.0099298 | -0.014969 | 0.010399 | -0.22823 | -0.0056742 | 0.013636 | 0.013849 | 0.047004 | -0.0014101 | 0.11551 | 0.028878 | 0.032795 | 0.10249 | -0.059167 | 0.18317 | 0.10178 | 0.097201 | 0.073618 | 0.003172 | 0.043302 | 0.11444 | -0.14334 | -0.10462 | 121.6152 | -0.007373 | 121.6289 | 121.5462 | -0.068989 | -0.16903 | 0.07331 | 121.4087 | -0.066561 | 121.6106 | 121.5165 | 0.1078 | 0.004573 | -0.25321 | 121.6159 | 121.4542 | 121.6965 | 121.5422 | -0.008079 | 121.5567 | 121.6278 | 121.37 | 121.587 | -0.21449
3096.375 | 121.7422 | -121.5546 | 0.12817 | 1.4211e-13 | -0.030301 | -0.0040769 | -0.0099298 | -0.014969 | 0.0099716 | -0.23586 | -0.0056742 | 0.013422 | 0.014062 | 0.047004 | -0.0014101 | 0.11551 | 0.038035 | 0.032795 | 0.093333 | -0.063746 | 0.19233 | 0.10178 | 0.092622 | 0.06904 | -0.001407 | 0.04788 | 0.11444 | -0.13876 | -0.1092 | 121.6563 | -0.034841 | 121.6701 | 121.5874 | -0.068989 | -0.19192 | 0.064157 | 121.4454 | -0.080294 | 121.6472 | 121.5532 | 0.1078 | -0.013738 | -0.26694 | 121.6479 | 121.4908 | 121.7469 | 121.5926 | -0.02639 | 121.6024 | 121.669 | 121.4158 | 121.6236 | -0.23738
3098.0625 | 121.7285 | -121.5683 | 0.12817 | 1.4211e-13 | -0.030301 | -0.0040769 | -0.0099298 | -0.014756 | 0.010185 | -0.22823 | -0.0054606 | 0.012995 | 0.013849 | 0.04679 | -0.0014101 | 0.11551 | 0.038035 | 0.037373 | 0.088755 | -0.063746 | 0.18775 | 0.10178 | 0.088043 | 0.073618 | 0.003172 | 0.04788 | 0.10986 | -0.13876 | -0.10462 | 121.6701 | -0.039419 | 121.6838 | 121.6057 | -0.064411 | -0.19192 | 0.059578 | 121.4637 | -0.080294 | 121.6563 | 121.5715 | 0.1078 | -0.018317 | -0.26694 | 121.6571 | 121.5046 | 121.7561 | 121.6063 | -0.02639 | 121.6162 | 121.6782 | 121.4295 | 121.6419 | -0.2328
3099.8281 | 121.7834 | -121.5866 | 0.11444 | 1.4211e-13 | -0.030301 | -0.0040769 | -0.0099298 | -0.015397 | 0.010399 | -0.2206 | -0.0056742 | 0.012995 | 0.013849 | 0.047004 | -0.0016237 | 0.11551 | 0.038035 | 0.032795 | 0.084176 | -0.054588 | 0.18775 | 0.10178 | 0.097201 | 0.06904 | -0.001407 | 0.04788 | 0.11901 | -0.14334 | -0.11378 | 121.6884 | -0.030265 | 121.7021 | 121.6194 | -0.068989 | -0.16903 | 0.073311 | 121.4728 | -0.066561 | 121.6838 | 121.5852 | 0.11237 | 0.004573 | -0.25778 | 121.6708 | 121.532 | 121.7744 | 121.6246 | -0.012657 | 121.6345 | 121.7056 | 121.4433 | 121.6556 | -0.22822
3101.5156 | 121.8018 | -121.5683 | 0.10529 | 1.4211e-13 | -0.030515 | -0.0042907 | -0.0097162 | -0.014756 | 0.010185 | -0.22823 | -0.0056742 | 0.013422 | 0.013421 | 0.046363 | -0.0011965 | 0.11093 | 0.033457 | 0.032795 | 0.088755 | -0.059167 | 0.18775 | 0.10636 | 0.097201 | 0.078197 | -0.005985 | 0.052459 | 0.10986 | -0.14334 | -0.1092 | 121.6747 | -0.016531 | 121.6792 | 121.6011 | -0.073568 | -0.16445 | 0.082466 | 121.4591 | -0.052827 | 121.6655 | 121.5623 | 0.10322 | 0.004571 | -0.24863 | 121.6571 | 121.5091 | 121.7561 | 121.6018 | 0.001077 | 121.6208 | 121.6782 | 121.425 | 121.6465 | -0.21449
3103.2656 | 121.8979 | -121.5775 | 0.073242 | 1.4211e-13 | -0.030728 | -0.0042907 | -0.0099298 | -0.014756 | 0.010613 | -0.23586 | -0.0056742 | 0.013636 | 0.013849 | 0.04679 | -0.0007691 | 0.10635 | 0.033457 | 0.023639 | 0.088755 | -0.054588 | 0.18775 | 0.11094 | 0.097201 | 0.078197 | 0.003172 | 0.043302 | 0.11444 | -0.13876 | -0.10462 | 121.6884 | 0.015513 | 121.6838 | 121.6011 | -0.087303 | -0.12783 | 0.11451 | 121.4728 | -0.02994 | 121.6747 | 121.5806 | 0.1078 | 0.041194 | -0.21201 | 121.6662 | 121.5229 | 121.7652 | 121.6109 | 0.0377 | 121.6208 | 121.6919 | 121.4387 | 121.6557 | -0.17787
3104.9688 | 121.8201 | -121.6049 | 0.10529 | 1.4211e-13 | -0.030301 | -0.0045043 | -0.010357 | -0.015183 | 0.010399 | -0.23586 | -0.0056742 | 0.012995 | 0.013849 | 0.046576 | -0.0014101 | 0.11551 | 0.038035 | 0.037373 | 0.093333 | -0.059167 | 0.19233 | 0.10636 | 0.097201 | 0.073618 | -0.005985 | 0.04788 | 0.1007 | -0.13876 | -0.1092 | 121.7113 | -0.011953 | 121.7204 | 121.6423 | -0.06899 | -0.16445 | 0.087045 | 121.4957 | -0.057406 | 121.7021 | 121.5989 | 0.10322 | -0.004586 | -0.24405 | 121.6983 | 121.5458 | 121.7972 | 121.643 | 0.001077 | 121.6528 | 121.7056 | 121.4662 | 121.6785 | -0.21449
3106.7031 | 121.8201 | -121.6278 | 0.11444 | 1.4211e-13 | -0.030301 | -0.0040769 | -0.0097162 | -0.014969 | 0.010399 | -0.22823 | -0.0054606 | 0.013208 | 0.014062 | 0.047217 | -0.0011965 | 0.11551 | 0.028878 | 0.037373 | 0.093333 | -0.063746 | 0.18775 | 0.10178 | 0.092622 | 0.073618 | 0.007751 | 0.04788 | 0.10986 | -0.13419 | -0.1092 | 121.7296 | -0.021108 | 121.7433 | 121.6652 | -0.064411 | -0.17819 | 0.073311 | 121.5186 | -0.066561 | 121.7204 | 121.6356 | 0.11695 | -0.004584 | -0.24863 | 121.7211 | 121.5641 | 121.8156 | 121.6567 | -0.012657 | 121.6757 | 121.7377 | 121.4936 | 121.7014 | -0.22364
3108.4375 | 121.8796 | -121.6095 | 0.09613 | 1.4211e-13 | -0.030728 | -0.0040769 | -0.010357 | -0.014756 | 0.010399 | -0.22823 | -0.0056742 | 0.013422 | 0.013635 | 0.04679 | -0.0011965 | 0.11551 | 0.038035 | 0.037373 | 0.088755 | -0.054588 | 0.18317 | 0.097205 | 0.097201 | 0.06904 | -0.001407 | 0.04788 | 0.11444 | -0.14334 | -0.10462 | 121.7067 | -0.007375 | 121.725 | 121.6469 | -0.059832 | -0.15072 | 0.087043 | 121.5049 | -0.04825 | 121.7067 | 121.6081 | 0.10322 | 0.018306 | -0.23947 | 121.6983 | 121.5549 | 121.7927 | 121.6475 | 0.001075 | 121.6574 | 121.7239 | 121.4662 | 121.6785 | -0.20075
3110.125 | 121.9208 | -121.5866 | 0.086975 | 1.4211e-13 | -0.030515 | -0.0042907 | -0.010144 | -0.014969 | 0.010613 | -0.22823 | -0.0054606 | 0.013422 | 0.013849 | 0.047004 | -0.0014101 | 0.10635 | 0.033457 | 0.032795 | 0.093333 | -0.063746 | 0.18775 | 0.10636 | 0.088043 | 0.064461 | -0.001407 | 0.04788 | 0.10528 | -0.13876 | -0.11378 | 121.693 | 0.006358 | 121.693 | 121.6194 | -0.073568 | -0.15072 | 0.10078 | 121.4728 | -0.039095 | 121.6747 | 121.5852 | 0.11237 | 0.018304 | -0.22574 | 121.6799 | 121.5229 | 121.7744 | 121.6201 | 0.019388 | 121.6345 | 121.6919 | 121.4478 | 121.6511 | -0.20076
3111.8594 | 121.8018 | -121.6461 | 0.10529 | 1.4211e-13 | -0.030515 | -0.0040769 | -0.0097162 | -0.014969 | 0.009758 | -0.24349 | -0.0054606 | 0.013208 | 0.013849 | 0.047217 | -0.0009829 | 0.10635 | 0.033457 | 0.032795 | 0.088755 | -0.054588 | 0.18775 | 0.10178 | 0.092622 | 0.073618 | -0.001407 | 0.057037 | 0.11444 | -0.13876 | -0.1092 | 121.7479 | -0.016531 | 121.7525 | 121.6789 | -0.068989 | -0.15987 | 0.082466 | 121.5369 | -0.048249 | 121.7387 | 121.6447 | 0.1078 | 0.00915 | -0.24405 | 121.7349 | 121.5915 | 121.8339 | 121.6796 | -0.003502 | 121.7032 | 121.7606 | 121.5074 | 121.7197 | -0.21449
3113.5469 | 121.9208 | -121.582 | 0.07782 | 1.4211e-13 | -0.030942 | -0.0038633 | -0.010144 | -0.014969 | 0.010185 | -0.23586 | -0.0056742 | 0.013636 | 0.013849 | 0.047004 | -0.0016237 | 0.11093 | 0.033457 | 0.032795 | 0.093333 | -0.068325 | 0.18775 | 0.10636 | 0.097201 | 0.06904 | 0.007751 | 0.052459 | 0.10986 | -0.14792 | -0.1092 | 121.6884 | 0.015513 | 121.693 | 121.6148 | -0.073568 | -0.14614 | 0.10993 | 121.4728 | -0.025361 | 121.6792 | 121.5898 | 0.11695 | 0.032037 | -0.22574 | 121.6754 | 121.5137 | 121.7698 | 121.6155 | 0.028543 | 121.6345 | 121.6919 | 121.4341 | 121.6511 | -0.18702
3115.2969 | 121.7972 | -121.6736 | 0.1236 | 1.4211e-13 | -0.030515 | -0.0045043 | -0.0097162 | -0.014756 | 0.010185 | -0.23586 | -0.0056742 | 0.013208 | 0.013635 | 0.046576 | -0.0016237 | 0.11551 | 0.028878 | 0.028217 | 0.093333 | -0.063746 | 0.19233 | 0.10178 | 0.092622 | 0.073618 | 0.007751 | 0.04788 | 0.10986 | -0.13876 | -0.1092 | 121.7754 | -0.030263 | 121.7891 | 121.7018 | -0.073567 | -0.18734 | 0.068735 | 121.5644 | -0.075716 | 121.7662 | 121.6813 | 0.11695 | -0.013739 | -0.26236 | 121.7669 | 121.6098 | 121.8659 | 121.7025 | -0.021812 | 121.7215 | 121.7834 | 121.5348 | 121.7472 | -0.2328
3116.9844 | 121.9345 | -121.6003 | 0.10071 | 1.4211e-13 | -0.030728 | -0.0038633 | -0.0099298 | -0.014969 | 0.0099716 | -0.24349 | -0.0056742 | 0.013208 | 0.013849 | 0.047004 | -0.0011965 | 0.097194 | 0.033457 | 0.032795 | 0.084176 | -0.054588 | 0.18775 | 0.097205 | 0.092622 | 0.06904 | -0.001407 | 0.052459 | 0.11901 | -0.13876 | -0.10462 | 121.6975 | -0.016532 | 121.6975 | 121.6331 | -0.06441 | -0.1553 | 0.087044 | 121.4957 | -0.048249 | 121.693 | 121.5989 | 0.10322 | 0.018306 | -0.23947 | 121.6845 | 121.5458 | 121.7881 | 121.6338 | -0.003503 | 121.6528 | 121.7194 | 121.4616 | 121.6694 | -0.20533
3118.75 | 121.9528 | -121.6049 | 0.09613 | 1.4211e-13 | -0.030942 | -0.0038633 | -0.010144 | -0.014756 | 0.010185 | -0.23586 | -0.005247 | 0.012995 | 0.013849 | 0.047004 | -0.0011965 | 0.10635 | 0.038035 | 0.032795 | 0.084176 | -0.054588 | 0.18317 | 0.11094 | 0.097201 | 0.073618 | -0.001407 | 0.04788 | 0.11444 | -0.14334 | -0.10004 | 121.7159 | -0.011954 | 121.7113 | 121.6377 | -0.078147 | -0.15072 | 0.087043 | 121.5049 | -0.04825 | 121.7021 | 121.6035 | 0.098638 | 0.018306 | -0.23947 | 121.6891 | 121.5503 | 121.7881 | 121.643 | 0.014812 | 121.6528 | 121.7194 | 121.4616 | 121.6785 | -0.19617
3120.5 | 121.9162 | -121.6461 | 0.091553 | 1.4211e-13 | -0.030728 | -0.0038633 | -0.0099298 | -0.014756 | 0.0099716 | -0.23586 | -0.0054606 | 0.013208 | 0.013849 | 0.04679 | -0.0014101 | 0.11093 | 0.028878 | 0.032795 | 0.084176 | -0.059167 | 0.18775 | 0.097205 | 0.083464 | 0.078197 | -0.001407 | 0.04788 | 0.12359 | -0.13876 | -0.10462 | 121.7433 | -0.007377 | 121.757 | 121.6789 | -0.06441 | -0.15072 | 0.096199 | 121.5415 | -0.043673 | 121.7296 | 121.6447 | 0.10322 | 0.03204 | -0.23032 | 121.7303 | 121.587 | 121.8339 | 121.675 | 0.005652 | 121.694 | 121.7697 | 121.5074 | 121.7243 | -0.19618
3122.25 | 121.8979 | -121.6782 | 0.10986 | 1.4211e-13 | -0.030942 | -0.0040769 | -0.0097162 | -0.014756 | 0.0099716 | -0.23586 | -0.0054606 | 0.013636 | 0.013635 | 0.047004 | -0.0011965 | 0.11093 | 0.033457 | 0.032795 | 0.088755 | -0.059167 | 0.19233 | 0.10636 | 0.092622 | 0.073618 | 0.003172 | 0.052459 | 0.10986 | -0.13876 | -0.1092 | 121.7845 | -0.021108 | 121.7891 | 121.711 | -0.073568 | -0.16903 | 0.082468 | 121.569 | -0.057404 | 121.7708 | 121.6813 | 0.11237 | -6e-06 | -0.24863 | 121.7669 | 121.619 | 121.8705 | 121.7116 | -0.0035 | 121.7306 | 121.788 | 121.5394 | 121.7518 | -0.21907
3123.9375 | 121.8201 | -121.7056 | 0.12817 | 1.4211e-13 | -0.030728 | -0.0040769 | -0.0097162 | -0.014969 | 0.010185 | -0.22823 | -0.0061014 | 0.013208 | 0.013635 | 0.047004 | -0.0009829 | 0.11093 | 0.033457 | 0.032795 | 0.088755 | -0.054588 | 0.19233 | 0.10636 | 0.088043 | 0.06904 | 0.003172 | 0.043302 | 0.10986 | -0.13876 | -0.10004 | 121.812 | -0.039419 | 121.8166 | 121.7384 | -0.073568 | -0.18276 | 0.064157 | 121.6056 | -0.084872 | 121.7937 | 121.7088 | 0.10322 | -0.018317 | -0.26694 | 121.7944 | 121.651 | 121.898 | 121.7391 | -0.021811 | 121.7489 | 121.8155 | 121.5669 | 121.7747 | -0.22822
3125.6719 | 121.9437 | -121.6644 | 0.10529 | 1.4211e-13 | -0.030942 | -0.0042907 | -0.010144 | -0.015183 | 0.010399 | -0.23586 | -0.0056742 | 0.013208 | 0.013635 | 0.047004 | -0.0009829 | 0.097194 | 0.038035 | 0.028217 | 0.084176 | -0.068325 | 0.19233 | 0.10636 | 0.097201 | 0.073618 | 0.007751 | 0.052459 | 0.11444 | -0.13876 | -0.1092 | 121.7708 | -0.02111 | 121.7616 | 121.6926 | -0.078146 | -0.17361 | 0.087045 | 121.5552 | -0.052827 | 121.7616 | 121.6722 | 0.11695 | 0.00915 | -0.24405 | 121.7486 | 121.5961 | 121.8568 | 121.7025 | 0.001077 | 121.7169 | 121.7789 | 121.5257 | 121.738 | -0.21449
3127.3594 | 121.9254 | -121.6873 | 0.10071 | 1.4211e-13 | -0.030728 | -0.0045043 | -0.0097162 | -0.015397 | 0.010399 | -0.24349 | -0.0056742 | 0.013208 | 0.013849 | 0.04679 | -0.0014101 | 0.10635 | 0.038035 | 0.028217 | 0.093333 | -0.063746 | 0.18317 | 0.10636 | 0.088043 | 0.082776 | 0.003172 | 0.04788 | 0.11444 | -0.14334 | -0.10004 | 121.7937 | -0.007375 | 121.7937 | 121.7155 | -0.078146 | -0.16445 | 0.082465 | 121.5873 | -0.052828 | 121.7754 | 121.6905 | 0.10322 | 0.013728 | -0.24405 | 121.7806 | 121.6236 | 121.8705 | 121.7254 | 0.005655 | 121.7352 | 121.8018 | 121.544 | 121.7701 | -0.20075
3129.1094 | 121.994 | -121.6461 | 0.068665 | 1.4211e-13 | -0.031156 | -0.0042907 | -0.0099298 | -0.015183 | 0.010185 | -0.23586 | -0.0056742 | 0.013208 | 0.013635 | 0.047217 | -0.0014101 | 0.10635 | 0.0243 | 0.032795 | 0.093333 | -0.059167 | 0.18775 | 0.10636 | 0.092622 | 0.073618 | 0.007751 | 0.057037 | 0.10986 | -0.13876 | -0.1092 | 121.7525 | 0.024668 | 121.7525 | 121.6789 | -0.073568 | -0.12783 | 0.11909 | 121.5369 | -0.011628 | 121.7387 | 121.6539 | 0.11695 | 0.041192 | -0.20743 | 121.7395 | 121.587 | 121.8339 | 121.6704 | 0.037698 | 121.7032 | 121.756 | 121.5074 | 121.7197 | -0.17787
3130.8438 | 121.9025 | -121.7148 | 0.11444 | 1.4211e-13 | -0.031369 | -0.0038633 | -0.0099298 | -0.014969 | 0.010185 | -0.24349 | -0.0056742 | 0.012995 | 0.013208 | 0.047004 | -0.0011965 | 0.10177 | 0.033457 | 0.028217 | 0.084176 | -0.059167 | 0.18775 | 0.10636 | 0.092622 | 0.073618 | 0.007751 | 0.04788 | 0.11901 | -0.13876 | -0.1092 | 121.8211 | -0.030265 | 121.8166 | 121.743 | -0.078146 | -0.17361 | 0.073311 | 121.6056 | -0.066561 | 121.8074 | 121.7225 | 0.11695 | 0.004573 | -0.25321 | 121.799 | 121.6556 | 121.9025 | 121.7482 | -0.008078 | 121.7627 | 121.8338 | 121.576 | 121.7884 | -0.22364
3132.5312 | 122.0078 | -121.6736 | 0.09613 | 1.4211e-13 | -0.031369 | -0.0042907 | -0.010144 | -0.014756 | 0.0099716 | -0.24349 | -0.0056742 | 0.013208 | 0.013421 | 0.047431 | -0.0014101 | 0.10635 | 0.038035 | 0.028217 | 0.088755 | -0.059167 | 0.18317 | 0.10636 | 0.088043 | 0.073618 | 0.003172 | 0.052459 | 0.11444 | -0.13876 | -0.10462 | 121.7799 | -0.007375 | 121.7799 | 121.7018 | -0.078146 | -0.1553 | 0.087043 | 121.569 | -0.043671 | 121.7616 | 121.6768 | 0.1078 | 0.018306 | -0.23489 | 121.7623 | 121.6144 | 121.8568 | 121.7116 | 0.010233 | 121.726 | 121.788 | 121.5348 | 121.7472 | -0.20075
3134.2812 | 121.9482 | -121.7056 | 0.11444 | 1.4211e-13 | -0.031156 | -0.0040769 | -0.0097162 | -0.014969 | 0.010185 | -0.23586 | -0.0056742 | 0.013208 | 0.013421 | 0.047004 | -0.0011965 | 0.10635 | 0.033457 | 0.01906 | 0.093333 | -0.059167 | 0.18775 | 0.10636 | 0.092622 | 0.078197 | 0.003172 | 0.04788 | 0.10528 | -0.14792 | -0.1092 | 121.812 | -0.021108 | 121.812 | 121.7247 | -0.087303 | -0.17361 | 0.073311 | 121.5964 | -0.066561 | 121.7982 | 121.7088 | 0.11237 | -0.009162 | -0.26236 | 121.799 | 121.6465 | 121.8934 | 121.7391 | -0.008078 | 121.7535 | 121.8109 | 121.5577 | 121.7838 | -0.22364
3136.0156 | 121.9299 | -121.7056 | 0.12817 | 1.4211e-13 | -0.030942 | -0.0042907 | -0.010144 | -0.014756 | 0.010399 | -0.23586 | -0.0056742 | 0.013208 | 0.013421 | 0.047431 | -0.0011965 | 0.10635 | 0.033457 | 0.023639 | 0.088755 | -0.059167 | 0.19233 | 0.10178 | 0.088043 | 0.078197 | 0.003172 | 0.057037 | 0.10986 | -0.14792 | -0.10462 | 121.8074 | -0.039419 | 121.812 | 121.7293 | -0.078145 | -0.18734 | 0.064157 | 121.601 | -0.071137 | 121.7937 | 121.7088 | 0.1078 | -0.018317 | -0.2761 | 121.7944 | 121.6465 | 121.898 | 121.7391 | -0.02639 | 121.7627 | 121.8155 | 121.5577 | 121.7838 | -0.2328
3137.7812 | 121.9482 | -121.7056 | 0.10986 | 1.4211e-13 | -0.031156 | -0.0040769 | -0.010357 | -0.015183 | 0.010185 | -0.23586 | -0.0054606 | 0.012995 | 0.013208 | 0.047217 | -0.0011965 | 0.11093 | 0.028878 | 0.028217 | 0.097912 | -0.059167 | 0.18775 | 0.11094 | 0.092622 | 0.06904 | -0.001407 | 0.04788 | 0.10986 | -0.13876 | -0.10004 | 121.8166 | -0.011951 | 121.8166 | 121.7338 | -0.082725 | -0.16903 | 0.077889 | 121.6056 | -0.061983 | 121.7982 | 121.7042 | 0.098638 | -6e-06 | -0.24863 | 121.8035 | 121.6465 | 121.8934 | 121.7345 | 0.001079 | 121.7535 | 121.8155 | 121.5669 | 121.7747 | -0.20991
3139.4844 | 121.994 | -121.7056 | 0.10529 | 1.4211e-13 | -0.030942 | -0.0038633 | -0.0099298 | -0.014969 | 0.010185 | -0.23586 | -0.0058878 | 0.013208 | 0.013635 | 0.047004 | -0.0011965 | 0.10635 | 0.028878 | 0.028217 | 0.088755 | -0.063746 | 0.19233 | 0.10636 | 0.097201 | 0.073618 | 0.01233 | 0.04788 | 0.11901 | -0.14334 | -0.1092 | 121.812 | -0.016531 | 121.812 | 121.7338 | -0.078146 | -0.16903 | 0.087045 | 121.5964 | -0.057406 | 121.8028 | 121.718 | 0.12153 | 0.013728 | -0.24863 | 121.7944 | 121.6419 | 121.898 | 121.7345 | 0.001077 | 121.7535 | 121.8246 | 121.5623 | 121.7792 | -0.21449
3141.1719 | 121.9116 | -121.7743 | 0.086975 | 1.4211e-13 | -0.031369 | -0.0042907 | -0.0099298 | -0.015183 | 0.0099716 | -0.23586 | -0.0058878 | 0.013208 | 0.013635 | 0.047217 | -0.0014101 | 0.10635 | 0.038035 | 0.01906 | 0.093333 | -0.059167 | 0.18775 | 0.10178 | 0.092622 | 0.073618 | 0.007751 | 0.057037 | 0.11444 | -0.13876 | -0.11378 | 121.8761 | 0.006358 | 121.8806 | 121.7934 | -0.082724 | -0.14614 | 0.10078 | 121.6605 | -0.029938 | 121.8669 | 121.782 | 0.12153 | 0.027461 | -0.22574 | 121.8676 | 121.7151 | 121.962 | 121.8123 | 0.014809 | 121.8313 | 121.8887 | 121.6355 | 121.8479 | -0.20076
3142.9062 | 122.0078 | -121.7239 | 0.091553 | 1.4211e-13 | -0.031156 | -0.0045043 | -0.0097162 | -0.015183 | 0.0099716 | -0.23586 | -0.0054606 | 0.013208 | 0.013635 | 0.047431 | -0.0014101 | 0.10177 | 0.038035 | 0.028217 | 0.093333 | -0.059167 | 0.18775 | 0.10178 | 0.092622 | 0.073618 | 0.003172 | 0.052459 | 0.10528 | -0.13876 | -0.10004 | 121.8257 | 0.00178 | 121.8257 | 121.7522 | -0.073567 | -0.15072 | 0.096199 | 121.6239 | -0.039094 | 121.8166 | 121.7271 | 0.10322 | 0.013726 | -0.23032 | 121.8173 | 121.6648 | 121.9117 | 121.762 | 0.010231 | 121.7764 | 121.8292 | 121.5852 | 121.7976 | -0.1916
3144.5938 | 121.9986 | -121.7606 | 0.10529 | 1.4211e-13 | -0.031369 | -0.0045043 | -0.0099298 | -0.015183 | 0.009758 | -0.23586 | -0.0061014 | 0.013422 | 0.013421 | 0.047431 | -0.0011965 | 0.10635 | 0.028878 | 0.037373 | 0.088755 | -0.063746 | 0.19233 | 0.11094 | 0.088043 | 0.073618 | 0.007751 | 0.052459 | 0.11444 | -0.13876 | -0.11378 | 121.8715 | -0.016531 | 121.8669 | 121.7979 | -0.073569 | -0.16903 | 0.087045 | 121.6468 | -0.052827 | 121.8486 | 121.7683 | 0.12153 | 0.00915 | -0.24405 | 121.8493 | 121.6968 | 121.9529 | 121.7894 | 0.005656 | 121.813 | 121.875 | 121.6218 | 121.8342 | -0.21907
3146.3438 | 121.9208 | -121.7697 | 0.11902 | 1.4211e-13 | -0.031369 | -0.0040769 | -0.0095024 | -0.014969 | 0.0099716 | -0.23586 | -0.005247 | 0.013422 | 0.013421 | 0.047217 | -0.0009829 | 0.10635 | 0.042614 | 0.028217 | 0.084176 | -0.054588 | 0.19233 | 0.10178 | 0.097201 | 0.06904 | 0.007751 | 0.052459 | 0.11444 | -0.13876 | -0.10462 | 121.8715 | -0.034843 | 121.8761 | 121.7979 | -0.073567 | -0.17361 | 0.073312 | 121.6651 | -0.06656 | 121.8669 | 121.7775 | 0.11237 | -0.004583 | -0.25778 | 121.8539 | 121.7151 | 121.962 | 121.8123 | -0.017235 | 121.8222 | 121.8841 | 121.6309 | 121.8388 | -0.22364
3148.0312 | 122.0352 | -121.7331 | 0.07782 | 1.4211e-13 | -0.031583 | -0.0040769 | -0.010357 | -0.015183 | 0.0099716 | -0.23586 | -0.0054606 | 0.012995 | 0.013421 | 0.047004 | -0.0014101 | 0.10635 | 0.033457 | 0.028217 | 0.088755 | -0.054588 | 0.18317 | 0.10178 | 0.097201 | 0.078197 | 0.007751 | 0.04788 | 0.11444 | -0.14334 | -0.1092 | 121.8349 | 0.010935 | 121.8394 | 121.7613 | -0.073567 | -0.13241 | 0.10535 | 121.6239 | -0.02994 | 121.8303 | 121.7408 | 0.11695 | 0.036616 | -0.22116 | 121.8218 | 121.6785 | 121.9163 | 121.7665 | 0.023964 | 121.781 | 121.8475 | 121.5897 | 121.8113 | -0.18702
3149.7969 | 121.9208 | -121.7789 | 0.11902 | 1.4211e-13 | -0.031583 | -0.0042907 | -0.0099298 | -0.015183 | 0.010185 | -0.23586 | -0.0054606 | 0.012995 | 0.013208 | 0.047431 | -0.0014101 | 0.10635 | 0.038035 | 0.028217 | 0.088755 | -0.050009 | 0.18317 | 0.10636 | 0.088043 | 0.06904 | 0.003172 | 0.043302 | 0.10986 | -0.13876 | -0.10004 | 121.8852 | -0.030264 | 121.8852 | 121.8071 | -0.078146 | -0.16903 | 0.064154 | 121.6788 | -0.075717 | 121.8669 | 121.782 | 0.10322 | -0.009162 | -0.25778 | 121.8676 | 121.7289 | 121.962 | 121.8169 | -0.012656 | 121.8222 | 121.8887 | 121.6401 | 121.8479 | -0.21906
3151.4844 | 122.0123 | -121.7651 | 0.09613 | 1.4211e-13 | -0.031583 | -0.0040769 | -0.010357 | -0.015183 | 0.0099716 | -0.22823 | -0.0054606 | 0.012995 | 0.013208 | 0.047217 | -0.0014101 | 0.11093 | 0.028878 | 0.028217 | 0.079598 | -0.059167 | 0.19233 | 0.10178 | 0.092622 | 0.073618 | -0.001407 | 0.052459 | 0.11901 | -0.14792 | -0.11378 | 121.8669 | -0.016532 | 121.8761 | 121.7934 | -0.073567 | -0.1553 | 0.096201 | 121.6514 | -0.043671 | 121.8578 | 121.7637 | 0.11237 | 0.022884 | -0.24405 | 121.8447 | 121.706 | 121.9575 | 121.794 | 0.005654 | 121.8176 | 121.8842 | 121.6172 | 121.8388 | -0.20991
3153.2344 | 121.9437 | -121.7789 | 0.11444 | 1.4211e-13 | -0.031583 | -0.0038633 | -0.010144 | -0.015183 | 0.0099716 | -0.23586 | -0.0056742 | 0.013208 | 0.013421 | 0.047217 | -0.0018375 | 0.10635 | 0.038035 | 0.028217 | 0.088755 | -0.059167 | 0.1786 | 0.10178 | 0.092622 | 0.078197 | 0.003172 | 0.052459 | 0.10986 | -0.13876 | -0.1092 | 121.8807 | -0.025686 | 121.8852 | 121.8071 | -0.073567 | -0.17361 | 0.064154 | 121.6697 | -0.061982 | 121.8715 | 121.782 | 0.11237 | -0.004584 | -0.25321 | 121.8676 | 121.7197 | 121.9575 | 121.8169 | -0.012657 | 121.8313 | 121.8887 | 121.6401 | 121.8571 | -0.22364
3154.9219 | 121.9528 | -121.7926 | 0.12817 | 1.4211e-13 | -0.031369 | -0.0040769 | -0.010144 | -0.015397 | 0.010185 | -0.23586 | -0.0056742 | 0.013422 | 0.013208 | 0.047431 | -0.0016237 | 0.10177 | 0.038035 | 0.028217 | 0.084176 | -0.063746 | 0.18317 | 0.11094 | 0.092622 | 0.073618 | 0.003172 | 0.057037 | 0.11444 | -0.13876 | -0.10462 | 121.9035 | -0.043998 | 121.8944 | 121.8208 | -0.082725 | -0.19192 | 0.054999 | 121.688 | -0.071137 | 121.8852 | 121.7958 | 0.1078 | -0.013738 | -0.26694 | 121.8768 | 121.7289 | 121.9758 | 121.8306 | -0.017232 | 121.8496 | 121.907 | 121.6538 | 121.8662 | -0.2328
3156.6719 | 122.0947 | -121.7422 | 0.082397 | 1.4211e-13 | -0.031583 | -0.0042907 | -0.0099298 | -0.015397 | 0.010185 | -0.23586 | -0.0054606 | 0.013422 | 0.013635 | 0.047217 | -0.0014101 | 0.10635 | 0.033457 | 0.01906 | 0.088755 | -0.059167 | 0.1786 | 0.10178 | 0.088043 | 0.064461 | -0.001407 | 0.052459 | 0.11901 | -0.14334 | -0.10004 | 121.844 | 0.006358 | 121.8486 | 121.7613 | -0.082724 | -0.14156 | 0.096198 | 121.6422 | -0.029938 | 121.8303 | 121.7408 | 0.098638 | 0.036617 | -0.22574 | 121.831 | 121.6831 | 121.9208 | 121.7757 | 0.019387 | 121.7947 | 121.8613 | 121.5989 | 121.8067 | -0.18244
3158.3594 | 122.0673 | -121.7697 | 0.10529 | 1.4211e-13 | -0.031369 | -0.0040769 | -0.0099298 | -0.015397 | 0.009758 | -0.23586 | -0.0056742 | 0.013208 | 0.013635 | 0.047645 | -0.0014101 | 0.097194 | 0.033457 | 0.01906 | 0.084176 | -0.063746 | 0.18775 | 0.10636 | 0.097201 | 0.06904 | -0.001407 | 0.057037 | 0.10986 | -0.13876 | -0.1092 | 121.8761 | -0.02111 | 121.8669 | 121.7888 | -0.087303 | -0.16903 | 0.082466 | 121.6605 | -0.048249 | 121.8669 | 121.7683 | 0.1078 | 0.004571 | -0.24405 | 121.8539 | 121.706 | 121.9575 | 121.8032 | 0.001077 | 121.8268 | 121.8796 | 121.6309 | 121.8388 | -0.21449
3160.1094 | 121.9803 | -121.788 | 0.11902 | 1.4211e-13 | -0.031797 | -0.0038633 | -0.010144 | -0.01561 | 0.0099716 | -0.24349 | -0.0054606 | 0.012781 | 0.012994 | 0.047004 | -0.0016237 | 0.10635 | 0.033457 | 0.028217 | 0.084176 | -0.063746 | 0.18775 | 0.10178 | 0.097201 | 0.073618 | 0.007751 | 0.057037 | 0.11444 | -0.13876 | -0.1092 | 121.8898 | -0.034843 | 121.8944 | 121.8162 | -0.073567 | -0.18277 | 0.068733 | 121.6788 | -0.061982 | 121.8852 | 121.7958 | 0.11695 | -0.004583 | -0.25778 | 121.8722 | 121.7243 | 121.9758 | 121.8215 | -0.017235 | 121.8451 | 121.9025 | 121.6493 | 121.8616 | -0.22822
3161.8594 | 122.1039 | -121.7697 | 0.086975 | 1.4211e-13 | -0.031156 | -0.0038633 | -0.0097162 | -0.015183 | 0.009758 | -0.23586 | -0.0056742 | 0.013208 | 0.013208 | 0.047431 | -0.0014101 | 0.10177 | 0.038035 | 0.028217 | 0.088755 | -0.059167 | 0.18317 | 0.10636 | 0.097201 | 0.078197 | 0.003172 | 0.057037 | 0.11444 | -0.13876 | -0.1092 | 121.8761 | 0.00178 | 121.8715 | 121.7979 | -0.078146 | -0.14614 | 0.096198 | 121.6605 | -0.029938 | 121.8669 | 121.7729 | 0.11237 | 0.027461 | -0.22574 | 121.8585 | 121.7105 | 121.9529 | 121.8077 | 0.019388 | 121.8268 | 121.8841 | 121.6309 | 121.8479 | -0.19618
3163.5312 | 121.9574 | -121.8155 | 0.11444 | 1.4211e-13 | -0.031369 | -0.0038633 | -0.0099298 | -0.015397 | 0.0099716 | -0.23586 | -0.0056742 | 0.012995 | 0.013421 | 0.047431 | -0.0014101 | 0.11093 | 0.038035 | 0.028217 | 0.084176 | -0.063746 | 0.19233 | 0.10636 | 0.097201 | 0.073618 | 0.003172 | 0.052459 | 0.11901 | -0.13876 | -0.1092 | 121.9219 | -0.030265 | 121.9264 | 121.8437 | -0.078146 | -0.17819 | 0.07789 | 121.7063 | -0.061982 | 121.9127 | 121.8187 | 0.11237 | 0.004573 | -0.25321 | 121.8997 | 121.7517 | 122.0078 | 121.8535 | -0.008078 | 121.8679 | 121.9345 | 121.6767 | 121.8891 | -0.22364
3165.2656 | 122.0032 | -121.8521 | 0.11902 | 1.4211e-13 | -0.03201 | -0.0040769 | -0.010144 | -0.014969 | 0.010185 | -0.24349 | -0.0054606 | 0.012995 | 0.013208 | 0.047645 | -0.0011965 | 0.10635 | 0.038035 | 0.028217 | 0.088755 | -0.063746 | 0.18317 | 0.10636 | 0.088043 | 0.073618 | 0.003172 | 0.057037 | 0.10528 | -0.13419 | -0.10462 | 121.9585 | -0.030264 | 121.9585 | 121.8803 | -0.078146 | -0.18277 | 0.064154 | 121.7475 | -0.061982 | 121.9402 | 121.8553 | 0.1078 | -0.01374 | -0.25321 | 121.9409 | 121.7884 | 122.0353 | 121.8901 | -0.012656 | 121.9091 | 121.9574 | 121.7179 | 121.9257 | -0.22364
3166.9531 | 122.0673 | -121.8109 | 0.10071 | 1.4211e-13 | -0.031369 | -0.0042907 | -0.0099298 | -0.015183 | 0.010185 | -0.22823 | -0.0056742 | 0.012995 | 0.013635 | 0.047858 | -0.0011965 | 0.10177 | 0.033457 | 0.028217 | 0.084176 | -0.068325 | 0.18317 | 0.11094 | 0.097201 | 0.078197 | 0.003172 | 0.052459 | 0.10986 | -0.13419 | -0.10004 | 121.9219 | -0.016532 | 121.9127 | 121.8391 | -0.082725 | -0.16903 | 0.082465 | 121.7109 | -0.048249 | 121.9081 | 121.8141 | 0.10322 | 0.009149 | -0.23489 | 121.8951 | 121.7426 | 121.9941 | 121.8444 | 0.010234 | 121.8634 | 121.9208 | 121.6767 | 121.8891 | -0.20075
3168.7031 | 122.1085 | -121.8018 | 0.091553 | 1.4211e-13 | -0.031369 | -0.0040769 | -0.010357 | -0.015183 | 0.0099716 | -0.23586 | -0.0054606 | 0.013208 | 0.013421 | 0.047645 | -0.0014101 | 0.10177 | 0.033457 | 0.023639 | 0.088755 | -0.063746 | 0.18317 | 0.10636 | 0.10178 | 0.06904 | -0.001407 | 0.057037 | 0.11444 | -0.13876 | -0.10462 | 121.9081 | -0.002798 | 121.9035 | 121.8254 | -0.082724 | -0.1553 | 0.09162 | 121.6971 | -0.034516 | 121.9035 | 121.8004 | 0.10322 | 0.022883 | -0.23032 | 121.8905 | 121.738 | 121.9849 | 121.8352 | 0.01481 | 121.8588 | 121.9162 | 121.663 | 121.8708 | -0.19618
3170.4531 | 122.1085 | -121.7651 | 0.091553 | 1.4211e-13 | -0.031583 | -0.0038633 | -0.010144 | -0.015397 | 0.0099716 | -0.23586 | -0.0054606 | 0.012995 | 0.012994 | 0.047217 | -0.0011965 | 0.097194 | 0.038035 | 0.028217 | 0.084176 | -0.054588 | 0.19233 | 0.10178 | 0.092622 | 0.06904 | 0.01233 | 0.061616 | 0.11444 | -0.13419 | -0.10462 | 121.8669 | -0.007377 | 121.8623 | 121.7934 | -0.073567 | -0.14614 | 0.10078 | 121.6605 | -0.029937 | 121.8578 | 121.7775 | 0.11695 | 0.022883 | -0.22574 | 121.8493 | 121.7105 | 121.9575 | 121.8032 | 0.010231 | 121.8268 | 121.8796 | 121.631 | 121.8342 | -0.19618
3172.1875 | 122.1176 | -121.8109 | 0.086975 | 1.4211e-13 | -0.031797 | -0.0038633 | -0.010144 | -0.014969 | 0.009758 | -0.24349 | -0.0054606 | 0.013208 | 0.013421 | 0.047645 | -0.0011965 | 0.10635 | 0.028878 | 0.023639 | 0.084176 | -0.054588 | 0.18775 | 0.10636 | 0.097201 | 0.078197 | 0.003172 | 0.061616 | 0.11901 | -0.13876 | -0.10462 | 121.9173 | -0.002799 | 121.9173 | 121.8346 | -0.082724 | -0.14156 | 0.10078 | 121.7063 | -0.025359 | 121.9081 | 121.8141 | 0.1078 | 0.032039 | -0.22574 | 121.8951 | 121.7563 | 121.9987 | 121.8398 | 0.019388 | 121.8725 | 121.9299 | 121.6721 | 121.8891 | -0.1916
3173.875 | 122.0078 | -121.8658 | 0.12817 | 1.4211e-13 | -0.031583 | -0.0040769 | -0.010144 | -0.015183 | 0.009758 | -0.22823 | -0.0061014 | 0.013208 | 0.013208 | 0.047004 | -0.0018375 | 0.097194 | 0.0243 | 0.028217 | 0.084176 | -0.068325 | 0.18775 | 0.10636 | 0.097201 | 0.073618 | 0.003172 | 0.057037 | 0.11444 | -0.14334 | -0.1092 | 121.9722 | -0.043998 | 121.963 | 121.8941 | -0.078146 | -0.1965 | 0.059578 | 121.7566 | -0.071137 | 121.963 | 121.869 | 0.11237 | -0.013738 | -0.27152 | 121.95 | 121.7975 | 122.0536 | 121.8901 | -0.021811 | 121.9229 | 121.9803 | 121.7225 | 121.9395 | -0.23738
3175.6406 | 122.049 | -121.8567 | 0.11902 | 1.4211e-13 | -0.03201 | -0.0040769 | -0.0099298 | -0.014969 | 0.010185 | -0.22823 | -0.0056742 | 0.012995 | 0.013208 | 0.047645 | -0.0014101 | 0.097194 | 0.038035 | 0.028217 | 0.079598 | -0.063746 | 0.18317 | 0.097205 | 0.10636 | 0.073618 | 0.003172 | 0.061616 | 0.11444 | -0.13876 | -0.1092 | 121.9539 | -0.039421 | 121.9539 | 121.8849 | -0.068988 | -0.18277 | 0.064154 | 121.7475 | -0.057403 | 121.963 | 121.8599 | 0.11237 | -0.004583 | -0.25778 | 121.9363 | 121.7929 | 122.0399 | 121.8947 | -0.021814 | 121.9183 | 121.9711 | 121.7179 | 121.9303 | -0.22822
3177.3906 | 122.0123 | -121.8384 | 0.14191 | 1.4211e-13 | -0.031583 | -0.0038633 | -0.0099298 | -0.015397 | 0.010399 | -0.22823 | -0.005247 | 0.012781 | 0.013421 | 0.047431 | -0.0011965 | 0.10177 | 0.038035 | 0.023639 | 0.079598 | -0.059167 | 0.18317 | 0.10636 | 0.092622 | 0.073618 | 0.01233 | 0.052459 | 0.11444 | -0.14334 | -0.1092 | 121.9447 | -0.062309 | 121.9402 | 121.862 | -0.082724 | -0.20107 | 0.041266 | 121.7292 | -0.089448 | 121.931 | 121.8507 | 0.12153 | -0.027471 | -0.28525 | 121.918 | 121.7792 | 122.0216 | 121.8764 | -0.035544 | 121.8908 | 121.9528 | 121.695 | 121.912 | -0.25111
3179.125 | 122.1451 | -121.8155 | 0.07782 | 1.4211e-13 | -0.031797 | -0.0036497 | -0.0097162 | -0.015397 | 0.0099716 | -0.23586 | -0.0056742 | 0.013208 | 0.013421 | 0.047645 | -0.0016237 | 0.097194 | 0.038035 | 0.023639 | 0.093333 | -0.068325 | 0.19233 | 0.11094 | 0.097201 | 0.073618 | 0.007751 | 0.052459 | 0.11901 | -0.13419 | -0.11378 | 121.9264 | 0.015513 | 121.9127 | 121.8391 | -0.087303 | -0.14614 | 0.11451 | 121.7017 | -0.025361 | 121.9127 | 121.8232 | 0.12153 | 0.041194 | -0.21201 | 121.9088 | 121.7472 | 122.0078 | 121.8535 | 0.033122 | 121.8679 | 121.9345 | 121.6813 | 121.8891 | -0.1916
3180.875 | 122.1313 | -121.7926 | 0.082397 | 1.4211e-13 | -0.031797 | -0.0040769 | -0.0097162 | -0.01561 | 0.009758 | -0.22823 | -0.0058878 | 0.012995 | 0.013635 | 0.047431 | -0.0016237 | 0.092615 | 0.028878 | 0.023639 | 0.088755 | -0.063746 | 0.18317 | 0.10636 | 0.097201 | 0.073618 | 0.007751 | 0.057037 | 0.11901 | -0.13876 | -0.1092 | 121.899 | 0.006358 | 121.8852 | 121.8162 | -0.082724 | -0.14614 | 0.10078 | 121.6834 | -0.02536 | 121.8898 | 121.8004 | 0.11695 | 0.036617 | -0.22116 | 121.8814 | 121.7289 | 121.9758 | 121.8215 | 0.023966 | 121.8496 | 121.9116 | 121.6538 | 121.8662 | -0.1916
3182.5625 | 122.168 | -121.8109 | 0.07782 | 1.4211e-13 | -0.03201 | -0.0040769 | -0.0099298 | -0.015397 | 0.0095442 | -0.22823 | -0.0056742 | 0.012995 | 0.013208 | 0.047431 | -0.0016237 | 0.092615 | 0.028878 | 0.023639 | 0.084176 | -0.054588 | 0.18317 | 0.10636 | 0.092622 | 0.06904 | -0.005985 | 0.057037 | 0.11901 | -0.13876 | -0.10004 | 121.9173 | 0.006356 | 121.9035 | 121.8346 | -0.082724 | -0.13241 | 0.10535 | 121.7109 | -0.020783 | 121.9035 | 121.8049 | 0.09406 | 0.041194 | -0.21658 | 121.8951 | 121.7563 | 121.9941 | 121.8398 | 0.028543 | 121.8679 | 121.9299 | 121.6721 | 121.88 | -0.17786
3184.2969 | 122.0215 | -121.8796 | 0.13275 | 1.4211e-13 | -0.03201 | -0.0038633 | -0.0099298 | -0.014969 | 0.0099716 | -0.24349 | -0.0056742 | 0.012995 | 0.013421 | 0.047645 | -0.0014101 | 0.097194 | 0.028878 | 0.023639 | 0.088755 | -0.063746 | 0.18775 | 0.10178 | 0.10178 | 0.078197 | 0.007751 | 0.052459 | 0.11901 | -0.13419 | -0.10004 | 121.9814 | -0.043996 | 121.9768 | 121.9032 | -0.078145 | -0.1965 | 0.055001 | 121.7795 | -0.080292 | 121.9814 | 121.8873 | 0.1078 | -0.013737 | -0.26694 | 121.9683 | 121.8158 | 122.0673 | 121.9085 | -0.030967 | 121.932 | 121.9986 | 121.7454 | 121.9578 | -0.2328
3185.9844 | 122.1542 | -121.8201 | 0.07782 | 1.4211e-13 | -0.03201 | -0.0040769 | -0.010144 | -0.015183 | 0.009758 | -0.23586 | -0.0056742 | 0.013208 | 0.013208 | 0.047431 | -0.0016237 | 0.10177 | 0.038035 | 0.01906 | 0.088755 | -0.059167 | 0.18775 | 0.11552 | 0.097201 | 0.073618 | 0.007751 | 0.066194 | 0.11444 | -0.13876 | -0.1092 | 121.9356 | 0.010935 | 121.9218 | 121.8391 | -0.096461 | -0.13699 | 0.10993 | 121.7109 | -0.011626 | 121.9173 | 121.8278 | 0.11695 | 0.036616 | -0.21658 | 121.9088 | 121.7609 | 122.0078 | 121.8581 | 0.037701 | 121.8863 | 121.9345 | 121.6813 | 121.8937 | -0.18702
3187.7344 | 122.0718 | -121.8704 | 0.10529 | 1.4211e-13 | -0.03201 | -0.0045043 | -0.0097162 | -0.01561 | 0.0095442 | -0.23586 | -0.0056742 | 0.012995 | 0.013208 | 0.047217 | -0.0014101 | 0.097194 | 0.028878 | 0.023639 | 0.093333 | -0.054588 | 0.18775 | 0.10636 | 0.097201 | 0.06904 | 0.007751 | 0.070773 | 0.11901 | -0.13876 | -0.1092 | 121.9768 | -0.011953 | 121.9676 | 121.8941 | -0.082724 | -0.15987 | 0.082466 | 121.7612 | -0.034513 | 121.9676 | 121.8782 | 0.11695 | 0.013728 | -0.24405 | 121.9638 | 121.8158 | 122.0582 | 121.8993 | 0.001077 | 121.9412 | 121.9894 | 121.7317 | 121.9395 | -0.21449
3189.4844 | 122.1268 | -121.8567 | 0.09613 | 1.4211e-13 | -0.03201 | -0.0042907 | -0.0092888 | -0.014969 | 0.0095442 | -0.23586 | -0.0056742 | 0.013208 | 0.013208 | 0.047431 | -0.0014101 | 0.097194 | 0.028878 | 0.023639 | 0.084176 | -0.059167 | 0.18317 | 0.10636 | 0.10178 | 0.06904 | 0.007751 | 0.066194 | 0.11444 | -0.14334 | -0.11378 | 121.9631 | -0.011954 | 121.9539 | 121.8803 | -0.082724 | -0.1553 | 0.087043 | 121.7429 | -0.029936 | 121.9585 | 121.8644 | 0.12153 | 0.018306 | -0.23947 | 121.9409 | 121.7975 | 122.0399 | 121.8856 | 0.010233 | 121.9229 | 121.9711 | 121.7133 | 121.9257 | -0.20991
3191.1719 | 122.1359 | -121.8704 | 0.10071 | 1.4211e-13 | -0.031797 | -0.0040769 | -0.0095024 | -0.015397 | 0.009758 | -0.23586 | -0.0058878 | 0.013208 | 0.013421 | 0.047431 | -0.0016237 | 0.092615 | 0.042614 | 0.01906 | 0.093333 | -0.063746 | 0.19233 | 0.10178 | 0.097201 | 0.078197 | 0.007751 | 0.061616 | 0.11901 | -0.14334 | -0.10004 | 121.9722 | -0.007375 | 121.963 | 121.8895 | -0.082724 | -0.16445 | 0.091623 | 121.7704 | -0.039092 | 121.9676 | 121.8782 | 0.1078 | 0.018306 | -0.24405 | 121.9638 | 121.8067 | 122.0628 | 121.913 | 0.001076 | 121.932 | 121.9894 | 121.7271 | 121.9486 | -0.20075
3192.9062 | 122.1497 | -121.8338 | 0.091553 | 1.4211e-13 | -0.03201 | -0.0042907 | -0.0095024 | -0.015397 | 0.0099716 | -0.23586 | -0.0056742 | 0.013208 | 0.012994 | 0.047645 | -0.0016237 | 0.10177 | 0.028878 | 0.01906 | 0.084176 | -0.059167 | 0.1786 | 0.11094 | 0.10178 | 0.073618 | 0.007751 | 0.075351 | 0.11444 | -0.13876 | -0.1092 | 121.9447 | -0.007377 | 121.9356 | 121.8529 | -0.091882 | -0.15072 | 0.087042 | 121.7246 | -0.016202 | 121.9356 | 121.8416 | 0.11695 | 0.022883 | -0.23032 | 121.918 | 121.7746 | 122.0124 | 121.8627 | 0.019389 | 121.9092 | 121.9482 | 121.695 | 121.9074 | -0.20076
3194.6562 | 122.0718 | -121.907 | 0.11444 | 1.4211e-13 | -0.032438 | -0.0038633 | -0.0097162 | -0.015397 | 0.009758 | -0.23586 | -0.0054606 | 0.013208 | 0.013208 | 0.047645 | -0.0014101 | 0.092615 | 0.038035 | 0.01906 | 0.084176 | -0.068325 | 0.19233 | 0.10178 | 0.097201 | 0.073618 | 0.01233 | 0.070773 | 0.11901 | -0.14792 | -0.1092 | 122.0088 | -0.030265 | 121.9997 | 121.9261 | -0.082724 | -0.18277 | 0.07789 | 121.7978 | -0.043668 | 122.0042 | 121.9194 | 0.12153 | 0.004573 | -0.26236 | 121.9912 | 121.8387 | 122.0994 | 121.9451 | -0.012657 | 121.9778 | 122.0261 | 121.7591 | 121.9807 | -0.22364
3196.3438 | 122.0673 | -121.9162 | 0.11444 | 1.4211e-13 | -0.032224 | -0.0045043 | -0.0092888 | -0.014969 | 0.009758 | -0.24349 | -0.0058878 | 0.013422 | 0.012994 | 0.047645 | -0.0018375 | 0.097194 | 0.033457 | 0.028217 | 0.084176 | -0.059167 | 0.18317 | 0.11094 | 0.097201 | 0.06904 | 0.016908 | 0.070773 | 0.11901 | -0.13419 | -0.10004 | 122.0271 | -0.030265 | 122.0134 | 121.9444 | -0.082725 | -0.17361 | 0.068732 | 121.8162 | -0.043668 | 122.0134 | 121.9331 | 0.11695 | 0.004573 | -0.24863 | 122.0004 | 121.857 | 122.0994 | 121.9497 | -0.003499 | 121.987 | 122.0352 | 121.782 | 121.9852 | -0.21449
3198.0312 | 122.1085 | -121.9208 | 0.10529 | 1.4211e-13 | -0.032224 | -0.0040769 | -0.0095024 | -0.015183 | 0.0095442 | -0.2206 | -0.0056742 | 0.013208 | 0.013208 | 0.047645 | -0.0016237 | 0.092615 | 0.033457 | 0.023639 | 0.079598 | -0.063746 | 0.1786 | 0.10636 | 0.10178 | 0.073618 | 0.016908 | 0.075351 | 0.12359 | -0.13876 | -0.10462 | 122.0271 | -0.025688 | 122.0134 | 121.9444 | -0.082724 | -0.16903 | 0.073309 | 121.8162 | -0.029935 | 122.0226 | 121.9377 | 0.12153 | 0.018307 | -0.24405 | 122.0004 | 121.857 | 122.0994 | 121.9542 | 0.001077 | 121.9961 | 122.0444 | 121.782 | 121.9944 | -0.20991
3199.7812 | 122.1909 | -121.8658 | 0.10071 | 1.4211e-13 | -0.032224 | -0.0042907 | -0.010144 | -0.01561 | 0.0093306 | -0.23586 | -0.0056742 | 0.012995 | 0.013208 | 0.047645 | -0.0016237 | 0.097194 | 0.042614 | 0.028217 | 0.088755 | -0.059167 | 0.18317 | 0.10178 | 0.097201 | 0.082776 | 0.007751 | 0.066194 | 0.12359 | -0.14334 | -0.10004 | 121.9676 | -0.011953 | 121.963 | 121.8941 | -0.073567 | -0.15987 | 0.082465 | 121.7658 | -0.034514 | 121.963 | 121.8736 | 0.1078 | 0.022885 | -0.24405 | 121.9546 | 121.8067 | 122.049 | 121.9085 | 0.001076 | 121.932 | 121.9894 | 121.7225 | 121.9486 | -0.20075
3201.5312 | 122.2046 | -121.8613 | 0.091553 | 1.4211e-13 | -0.03201 | -0.0040769 | -0.0097162 | -0.015183 | 0.0095442 | -0.24349 | -0.0058878 | 0.013208 | 0.013208 | 0.047645 | -0.0016237 | 0.097194 | 0.038035 | 0.023639 | 0.084176 | -0.063746 | 0.19233 | 0.10636 | 0.092622 | 0.073618 | 0.007751 | 0.066194 | 0.11901 | -0.13876 | -0.1092 | 121.9676 | -0.007377 | 121.9585 | 121.8849 | -0.082724 | -0.1553 | 0.10078 | 121.7521 | -0.025359 | 121.9539 | 121.869 | 0.11695 | 0.027461 | -0.23032 | 121.9454 | 121.7975 | 122.0536 | 121.8993 | 0.01481 | 121.9275 | 121.9803 | 121.7225 | 121.9349 | -0.20076
3203.2656 | 122.113 | -121.9116 | 0.12817 | 1.4211e-13 | -0.032438 | -0.0042907 | -0.0097162 | -0.015183 | 0.0099716 | -0.25112 | -0.0058878 | 0.012567 | 0.013421 | 0.047645 | -0.0018375 | 0.092615 | 0.033457 | 0.014482 | 0.084176 | -0.054588 | 0.18775 | 0.10636 | 0.088043 | 0.073618 | 0.007751 | 0.066194 | 0.12359 | -0.14334 | -0.1092 | 122.018 | -0.043998 | 122.0042 | 121.9261 | -0.091881 | -0.18276 | 0.059578 | 121.8024 | -0.06198 | 121.9997 | 121.9194 | 0.11695 | -0.004581 | -0.27152 | 121.9958 | 121.857 | 122.0994 | 121.9451 | -0.021811 | 121.9778 | 122.0352 | 121.7683 | 121.9852 | -0.23738
3204.9688 | 122.2092 | -121.8567 | 0.10071 | 1.4211e-13 | -0.032651 | -0.0042907 | -0.0092888 | -0.015397 | 0.009758 | -0.23586 | -0.0056742 | 0.012995 | 0.01278 | 0.047858 | -0.0016237 | 0.092615 | 0.033457 | 0.014482 | 0.088755 | -0.059167 | 0.19233 | 0.11094 | 0.092622 | 0.073618 | 0.007751 | 0.066194 | 0.11901 | -0.14334 | -0.10462 | 121.9676 | -0.011953 | 121.9493 | 121.8712 | -0.09646 | -0.15987 | 0.091623 | 121.7521 | -0.034514 | 121.9493 | 121.8644 | 0.11237 | 0.018306 | -0.24405 | 121.9454 | 121.7975 | 122.049 | 121.8901 | 0.010234 | 121.9229 | 121.9757 | 121.7133 | 121.9303 | -0.20533
3206.7188 | 122.1725 | -121.8567 | 0.10071 | 1.4211e-13 | -0.032224 | -0.0040769 | -0.0099298 | -0.015397 | 0.0095442 | -0.22823 | -0.0056742 | 0.012781 | 0.012994 | 0.047217 | -0.0016237 | 0.088037 | 0.028878 | 0.014482 | 0.088755 | -0.063746 | 0.18317 | 0.10178 | 0.10178 | 0.073618 | 0.007751 | 0.075351 | 0.11901 | -0.14334 | -0.1092 | 121.9585 | -0.011953 | 121.9447 | 121.8712 | -0.087302 | -0.16445 | 0.082465 | 121.7475 | -0.025357 | 121.9585 | 121.8644 | 0.11695 | 0.018306 | -0.24405 | 121.9454 | 121.7929 | 122.0399 | 121.8856 | 0.001076 | 121.932 | 121.9757 | 121.7133 | 121.9303 | -0.20991
3208.4062 | 122.1039 | -121.9299 | 0.1236 | 1.4211e-13 | -0.032438 | -0.0040769 | -0.0099298 | -0.015183 | 0.009758 | -0.23586 | -0.005247 | 0.013422 | 0.012994 | 0.047858 | -0.0016237 | 0.088037 | 0.033457 | 0.01906 | 0.088755 | -0.059167 | 0.18317 | 0.11552 | 0.10178 | 0.073618 | 0.01233 | 0.07993 | 0.12817 | -0.13876 | -0.10462 | 122.0455 | -0.034841 | 122.018 | 121.949 | -0.096461 | -0.18276 | 0.059577 | 121.8253 | -0.043666 | 122.0317 | 121.9423 | 0.11695 | 0.004576 | -0.26236 | 122.0187 | 121.8708 | 122.1131 | 121.9634 | -0.008075 | 122.0099 | 122.0581 | 121.7912 | 122.0035 | -0.22822
3210.1094 | 122.1497 | -121.9208 | 0.10986 | 1.4211e-13 | -0.032651 | -0.0040769 | -0.0097162 | -0.01561 | 0.009758 | -0.23586 | -0.0056742 | 0.012995 | 0.012994 | 0.047858 | -0.0016237 | 0.092615 | 0.028878 | 0.023639 | 0.084176 | -0.059167 | 0.19233 | 0.11094 | 0.097201 | 0.073618 | 0.007751 | 0.066194 | 0.11444 | -0.13419 | -0.10462 | 122.0317 | -0.025687 | 122.0134 | 121.9444 | -0.087303 | -0.16903 | 0.082468 | 121.8162 | -0.043669 | 122.018 | 121.9285 | 0.11237 | 0.004573 | -0.24405 | 122.005 | 121.8616 | 122.1131 | 121.9497 | 0.001079 | 121.987 | 122.0352 | 121.7866 | 121.9944 | -0.21449
3211.8594 | 122.1817 | -121.8979 | 0.086975 | 1.4211e-13 | -0.031797 | -0.0042907 | -0.0095024 | -0.015397 | 0.0095442 | -0.23586 | -0.0056742 | 0.012995 | 0.012994 | 0.047858 | -0.0020511 | 0.092615 | 0.033457 | 0.023639 | 0.088755 | -0.068325 | 0.19233 | 0.10178 | 0.10636 | 0.073618 | 0.01233 | 0.075351 | 0.12817 | -0.14334 | -0.10004 | 121.9997 | 0.00178 | 121.9905 | 121.9215 | -0.078145 | -0.1553 | 0.10536 | 121.7978 | -0.011624 | 122.0042 | 121.9102 | 0.11238 | 0.041197 | -0.23032 | 121.9866 | 121.8296 | 122.0902 | 121.9313 | 0.014809 | 121.9732 | 122.0261 | 121.7545 | 121.9715 | -0.18702
3213.6094 | 122.1405 | -121.9299 | 0.13733 | 1.4211e-13 | -0.032651 | -0.0038633 | -0.0095024 | -0.01561 | 0.0095442 | -0.22823 | -0.0058878 | 0.013422 | 0.013421 | 0.047858 | -0.0016237 | 0.088037 | 0.0243 | 0.01906 | 0.088755 | -0.059167 | 0.19691 | 0.10636 | 0.097201 | 0.078197 | 0.007751 | 0.075351 | 0.12359 | -0.13419 | -0.10462 | 122.0363 | -0.048574 | 122.018 | 121.949 | -0.087303 | -0.1965 | 0.05958 | 121.8253 | -0.061978 | 122.0271 | 121.9377 | 0.11237 | -0.013736 | -0.27152 | 122.0187 | 121.8708 | 122.1268 | 121.9542 | -0.030966 | 122.0053 | 122.0535 | 121.7957 | 122.0081 | -0.24195
3215.2969 | 122.2183 | -121.9162 | 0.091553 | 1.4211e-13 | -0.032438 | -0.0040769 | -0.0095024 | -0.014969 | 0.0095442 | -0.23586 | -0.0058878 | 0.012567 | 0.01278 | 0.048286 | -0.0016237 | 0.088037 | 0.028878 | 0.023639 | 0.084176 | -0.054588 | 0.18775 | 0.10636 | 0.10178 | 0.073618 | 0.007751 | 0.070773 | 0.11444 | -0.13876 | -0.10004 | 122.0226 | -0.007377 | 122.0042 | 121.9398 | -0.082724 | -0.14614 | 0.096199 | 121.8162 | -0.02078 | 122.018 | 121.924 | 0.1078 | 0.022883 | -0.23032 | 122.0004 | 121.8616 | 122.104 | 121.9451 | 0.01481 | 121.987 | 122.0306 | 121.7774 | 121.9898 | -0.1916
3216.9688 | 122.2549 | -121.9025 | 0.07782 | 1.4211e-13 | -0.032438 | -0.0040769 | -0.0095024 | -0.014969 | 0.0099716 | -0.22823 | -0.0056742 | 0.013208 | 0.012994 | 0.047645 | -0.0014101 | 0.088037 | 0.028878 | 0.023639 | 0.084176 | -0.059167 | 0.18317 | 0.10178 | 0.097201 | 0.073618 | 0.01233 | 0.070773 | 0.12359 | -0.14792 | -0.10462 | 122.0042 | 0.006356 | 121.9905 | 121.9261 | -0.078145 | -0.13699 | 0.10535 | 121.7978 | -0.007047 | 121.9997 | 121.9148 | 0.11695 | 0.045773 | -0.22574 | 121.9866 | 121.8433 | 122.0856 | 121.9313 | 0.023964 | 121.9732 | 122.0261 | 121.7545 | 121.9761 | -0.18244
3218.7188 | 122.1085 | -121.962 | 0.11902 | 1.4211e-13 | -0.032651 | -0.0042907 | -0.0095024 | -0.015397 | 0.009758 | -0.22823 | -0.0056742 | 0.012995 | 0.013208 | 0.047645 | -0.0018375 | 0.088037 | 0.033457 | 0.023639 | 0.084176 | -0.063746 | 0.18775 | 0.10178 | 0.097201 | 0.078197 | 0.007751 | 0.070773 | 0.11901 | -0.13876 | -0.1092 | 122.0638 | -0.034843 | 122.05 | 121.9856 | -0.078145 | -0.18277 | 0.068733 | 121.8528 | -0.048246 | 122.0592 | 121.9697 | 0.11695 | -5e-06 | -0.25778 | 122.0462 | 121.8982 | 122.1497 | 121.9954 | -0.017235 | 122.0327 | 122.081 | 121.8232 | 122.0402 | -0.22822
3220.4062 | 122.2458 | -121.9391 | 0.09613 | 1.4211e-13 | -0.032224 | -0.0042907 | -0.0095024 | -0.015397 | 0.0099716 | -0.22823 | -0.0054606 | 0.012781 | 0.01278 | 0.048072 | -0.0018375 | 0.083459 | 0.028878 | 0.023639 | 0.088755 | -0.059167 | 0.19233 | 0.10636 | 0.097201 | 0.078197 | 0.021487 | 0.084508 | 0.12817 | -0.14334 | -0.10004 | 122.0455 | -0.007375 | 122.0225 | 121.9627 | -0.082724 | -0.1553 | 0.096201 | 121.839 | -0.011622 | 122.0363 | 121.9606 | 0.12153 | 0.032042 | -0.23947 | 122.0278 | 121.8799 | 122.1314 | 121.968 | 0.010233 | 122.0236 | 122.0673 | 121.7957 | 122.0173 | -0.19617
3222.1562 | 122.2458 | -121.907 | 0.091553 | 1.4211e-13 | -0.032651 | -0.0047181 | -0.0097162 | -0.015397 | 0.009758 | -0.22823 | -0.0058878 | 0.013208 | 0.013421 | 0.047858 | -0.0018375 | 0.088037 | 0.038035 | 0.023639 | 0.084176 | -0.063746 | 0.18775 | 0.10636 | 0.10178 | 0.073618 | 0.01233 | 0.075351 | 0.12817 | -0.13419 | -0.10462 | 122.0134 | -0.007377 | 121.9951 | 121.9307 | -0.082724 | -0.1553 | 0.096199 | 121.8024 | -0.016202 | 122.0088 | 121.9194 | 0.11695 | 0.036619 | -0.22574 | 121.9912 | 121.8433 | 122.0948 | 121.9451 | 0.01481 | 121.9824 | 122.0352 | 121.7729 | 121.9807 | -0.19618
3223.8438 | 122.2046 | -121.9574 | 0.10529 | 1.4211e-13 | -0.033079 | -0.0038633 | -0.0097162 | -0.015397 | 0.009758 | -0.23586 | -0.0056742 | 0.013422 | 0.013208 | 0.048072 | -0.0018375 | 0.088037 | 0.0243 | 0.023639 | 0.084176 | -0.063746 | 0.18317 | 0.10636 | 0.097201 | 0.06904 | 0.016908 | 0.07993 | 0.12817 | -0.14334 | -0.10462 | 122.0638 | -0.02111 | 122.0454 | 121.981 | -0.082724 | -0.16903 | 0.077887 | 121.8528 | -0.025356 | 122.0546 | 121.9743 | 0.12153 | 0.022886 | -0.24863 | 122.0416 | 121.8937 | 122.1406 | 121.9817 | 0.001077 | 122.0373 | 122.0856 | 121.8141 | 122.0264 | -0.20991
3225.5938 | 122.2 | -121.9391 | 0.10529 | 1.4211e-13 | -0.032865 | -0.0045043 | -0.0095024 | -0.015397 | 0.0095442 | -0.2206 | -0.0056742 | 0.012781 | 0.013421 | 0.047858 | -0.0018375 | 0.083459 | 0.033457 | 0.01906 | 0.084176 | -0.063746 | 0.19691 | 0.11094 | 0.11094 | 0.078197 | 0.003172 | 0.075351 | 0.12817 | -0.14334 | -0.1092 | 122.05 | -0.02111 | 122.0225 | 121.9581 | -0.091882 | -0.16903 | 0.091623 | 121.8299 | -0.029935 | 122.05 | 121.9423 | 0.11237 | 0.022886 | -0.24863 | 122.0233 | 121.8753 | 122.136 | 121.9725 | 0.005656 | 122.0144 | 122.0673 | 121.7957 | 122.0173 | -0.21449
3227.2656 | 122.1771 | -121.9666 | 0.11902 | 1.4211e-13 | -0.032651 | -0.0042907 | -0.0092888 | -0.015183 | 0.009758 | -0.23586 | -0.0056742 | 0.012995 | 0.012994 | 0.048286 | -0.0016237 | 0.083459 | 0.038035 | 0.028217 | 0.079598 | -0.059167 | 0.1786 | 0.097205 | 0.097201 | 0.06904 | -0.001407 | 0.075351 | 0.12817 | -0.13876 | -0.10462 | 122.0638 | -0.039421 | 122.05 | 121.9948 | -0.068988 | -0.17819 | 0.059576 | 121.8619 | -0.043668 | 122.0638 | 121.9651 | 0.10322 | 0.009153 | -0.25778 | 122.0462 | 121.9074 | 122.1451 | 122.0046 | -0.021814 | 122.0419 | 122.0947 | 121.8278 | 122.0356 | -0.22364
3229 | 122.2641 | -121.9299 | 0.091553 | 1.4211e-13 | -0.032865 | -0.0042907 | -0.0097162 | -0.01561 | 0.0093306 | -0.22823 | -0.0058878 | 0.012995 | 0.01278 | 0.048072 | -0.0018375 | 0.088037 | 0.038035 | 0.028217 | 0.084176 | -0.068325 | 0.18317 | 0.10636 | 0.097201 | 0.078197 | 0.003172 | 0.070773 | 0.12359 | -0.13419 | -0.10462 | 122.0363 | -0.007377 | 122.018 | 121.9581 | -0.078146 | -0.15988 | 0.09162 | 121.8253 | -0.02078 | 122.0271 | 121.9331 | 0.1078 | 0.03204 | -0.22574 | 122.0141 | 121.8616 | 122.1131 | 121.968 | 0.01481 | 122.0007 | 122.0535 | 121.7957 | 122.0081 | -0.19618
3230.7656 | 122.2321 | -121.9437 | 0.091553 | 1.4211e-13 | -0.032651 | -0.0045043 | -0.0092888 | -0.01561 | 0.0095442 | -0.22823 | -0.0058878 | 0.012995 | 0.013208 | 0.047645 | -0.0018375 | 0.07888 | 0.0243 | 0.023639 | 0.084176 | -0.059167 | 0.19233 | 0.10178 | 0.10178 | 0.06904 | 0.016908 | 0.070773 | 0.12359 | -0.14334 | -0.10462 | 122.0454 | -0.007377 | 122.0225 | 121.9673 | -0.078145 | -0.15072 | 0.10078 | 121.839 | -0.02078 | 122.0454 | 121.9606 | 0.12153 | 0.03204 | -0.2349 | 122.0278 | 121.8845 | 122.136 | 121.968 | 0.010231 | 122.0144 | 122.0673 | 121.8003 | 122.0127 | -0.19618
3232.4531 | 122.1909 | -121.9574 | 0.1236 | 1.4211e-13 | -0.032865 | -0.0040769 | -0.0097162 | -0.015824 | 0.0095442 | -0.23586 | -0.0056742 | 0.012781 | 0.013208 | 0.048072 | -0.0014101 | 0.092615 | 0.033457 | 0.023639 | 0.088755 | -0.063746 | 0.18775 | 0.10178 | 0.10178 | 0.078197 | 0.016908 | 0.070773 | 0.12359 | -0.13876 | -0.10462 | 122.0592 | -0.034841 | 122.05 | 121.981 | -0.078145 | -0.18734 | 0.064156 | 121.8528 | -0.052823 | 122.0592 | 121.9743 | 0.12153 | -3e-06 | -0.26236 | 122.0462 | 121.8937 | 122.1451 | 121.9909 | -0.021812 | 122.0282 | 122.081 | 121.8186 | 122.0356 | -0.22822
3234.2031 | 122.1497 | -121.9803 | 0.10986 | 1.4211e-13 | -0.033079 | -0.0045043 | -0.0097162 | -0.015397 | 0.0095442 | -0.24349 | -0.0061014 | 0.012781 | 0.013208 | 0.047858 | -0.0016237 | 0.083459 | 0.033457 | 0.023639 | 0.088755 | -0.059167 | 0.18775 | 0.10636 | 0.10178 | 0.078197 | 0.01233 | 0.066194 | 0.12817 | -0.14792 | -0.1092 | 122.0866 | -0.021108 | 122.0637 | 122.0039 | -0.082724 | -0.16903 | 0.077889 | 121.8711 | -0.043669 | 122.0821 | 121.9926 | 0.12153 | 0.018309 | -0.25778 | 122.069 | 121.9211 | 122.168 | 122.0137 | -0.0035 | 122.0465 | 122.1085 | 121.8324 | 122.0585 | -0.21907
3235.9531 | 122.2275 | -121.9574 | 0.11444 | 1.4211e-13 | -0.033079 | -0.0042907 | -0.0097162 | -0.014969 | 0.0095442 | -0.24349 | -0.0056742 | 0.013208 | 0.013208 | 0.048072 | -0.0016237 | 0.083459 | 0.028878 | 0.014482 | 0.084176 | -0.063746 | 0.18317 | 0.11552 | 0.10178 | 0.073618 | 0.007751 | 0.066194 | 0.12359 | -0.13876 | -0.10004 | 122.0729 | -0.030265 | 122.0409 | 121.9719 | -0.10104 | -0.17819 | 0.068732 | 121.8574 | -0.048247 | 122.0592 | 121.9651 | 0.1078 | 0.009152 | -0.25321 | 122.0416 | 121.8937 | 122.1406 | 121.9863 | 0.00108 | 122.0236 | 122.081 | 121.8186 | 122.031 | -0.21449
3237.7031 | 122.1725 | -122.0078 | 0.13275 | 1.4211e-13 | -0.032865 | -0.0042907 | -0.0099298 | -0.014969 | 0.0095442 | -0.23586 | -0.0058878 | 0.013208 | 0.013208 | 0.048286 | -0.0016237 | 0.088037 | 0.038035 | 0.023639 | 0.084176 | -0.059167 | 0.18775 | 0.10178 | 0.10178 | 0.078197 | 0.016908 | 0.075351 | 0.12359 | -0.13876 | -0.10004 | 122.1095 | -0.048575 | 122.0958 | 122.0314 | -0.078145 | -0.19192 | 0.055001 | 121.9077 | -0.0574 | 122.1095 | 122.0247 | 0.11695 | -0.009158 | -0.27152 | 122.0919 | 121.9486 | 122.1955 | 122.0458 | -0.030967 | 122.0831 | 122.1313 | 121.869 | 122.0859 | -0.2328
3239.3906 | 122.2321 | -121.962 | 0.091553 | 1.4211e-13 | -0.032865 | -0.0042907 | -0.0095024 | -0.015183 | 0.0093306 | -0.23586 | -0.0056742 | 0.012995 | 0.01278 | 0.047858 | -0.0018375 | 0.088037 | 0.033457 | 0.01906 | 0.088755 | -0.063746 | 0.18775 | 0.10636 | 0.10178 | 0.078197 | 0.01233 | 0.070773 | 0.12817 | -0.13419 | -0.10462 | 122.0683 | -0.002798 | 122.05 | 121.981 | -0.087303 | -0.1553 | 0.096199 | 121.8574 | -0.02078 | 122.0638 | 121.9743 | 0.11695 | 0.036619 | -0.22574 | 122.0507 | 121.8982 | 122.1497 | 121.9954 | 0.01481 | 122.0327 | 122.0901 | 121.8278 | 122.0402 | -0.19618
3241.125 | 122.1542 | -122.0261 | 0.12817 | 1.4211e-13 | -0.033079 | -0.0045043 | -0.0092888 | -0.015397 | 0.009758 | -0.23586 | -0.0058878 | 0.013208 | 0.01278 | 0.048072 | -0.0014101 | 0.088037 | 0.033457 | 0.01906 | 0.084176 | -0.063746 | 0.18775 | 0.11552 | 0.10636 | 0.082776 | 0.007751 | 0.075351 | 0.12359 | -0.13419 | -0.10004 | 122.1416 | -0.043998 | 122.1141 | 122.0451 | -0.096461 | -0.19192 | 0.059578 | 121.926 | -0.052823 | 122.1324 | 122.0338 | 0.1078 | -0.004581 | -0.26236 | 122.1102 | 121.9623 | 122.2138 | 122.0595 | -0.012653 | 122.1014 | 122.1497 | 121.8919 | 122.1088 | -0.22822
3242.875 | 122.2275 | -121.994 | 0.11444 | 1.4211e-13 | -0.033079 | -0.0040769 | -0.0097162 | -0.015397 | 0.0095442 | -0.23586 | -0.0061014 | 0.012781 | 0.01278 | 0.048072 | -0.0018375 | 0.083459 | 0.038035 | 0.023639 | 0.084176 | -0.059167 | 0.18317 | 0.10178 | 0.097201 | 0.082776 | 0.01233 | 0.07993 | 0.12817 | -0.13876 | -0.10462 | 122.0958 | -0.030265 | 122.0775 | 122.0177 | -0.078145 | -0.17361 | 0.068732 | 121.8894 | -0.034511 | 122.0912 | 122.0063 | 0.11695 | 0.013731 | -0.25321 | 122.0782 | 121.9349 | 122.1772 | 122.0321 | -0.012657 | 122.0739 | 122.1222 | 121.8553 | 122.0768 | -0.21907
3244.5625 | 122.2183 | -122.0032 | 0.11444 | 1.4211e-13 | -0.032865 | -0.0040769 | -0.0095024 | -0.01561 | 0.009758 | -0.24349 | -0.0061014 | 0.012781 | 0.013208 | 0.048072 | -0.0016237 | 0.088037 | 0.042614 | 0.01906 | 0.084176 | -0.059167 | 0.18317 | 0.10636 | 0.097201 | 0.078197 | 0.01233 | 0.070773 | 0.12817 | -0.13876 | -0.10004 | 122.1095 | -0.030265 | 122.0912 | 122.0222 | -0.087303 | -0.17361 | 0.068732 | 121.9031 | -0.043668 | 122.1004 | 122.0155 | 0.11238 | 0.013731 | -0.25321 | 122.0874 | 121.944 | 122.1863 | 122.0458 | -0.008078 | 122.0739 | 122.1313 | 121.8644 | 122.0814 | -0.21449
3246.2969 | 122.2275 | -122.0078 | 0.11902 | 1.4211e-13 | -0.033292 | -0.0040769 | -0.0097162 | -0.015397 | 0.0093306 | -0.23586 | -0.0061014 | 0.013208 | 0.012994 | 0.047858 | -0.0018375 | 0.083459 | 0.033457 | 0.023639 | 0.088755 | -0.063746 | 0.18317 | 0.10178 | 0.10636 | 0.082776 | 0.01233 | 0.070773 | 0.12817 | -0.13876 | -0.10462 | 122.1095 | -0.030264 | 122.0912 | 122.0314 | -0.078145 | -0.18277 | 0.064154 | 121.9031 | -0.048246 | 122.1141 | 122.0201 | 0.11695 | 0.009153 | -0.25778 | 122.0965 | 121.944 | 122.1909 | 122.0412 | -0.017235 | 122.0785 | 122.1359 | 121.869 | 122.0905 | -0.22364
3248.0312 | 122.2549 | -122.0032 | 0.09613 | 1.4211e-13 | -0.033079 | -0.0045043 | -0.0097162 | -0.016038 | 0.0093306 | -0.23586 | -0.0058878 | 0.012781 | 0.01278 | 0.047858 | -0.0018375 | 0.083459 | 0.033457 | 0.01906 | 0.093333 | -0.063746 | 0.19233 | 0.10636 | 0.097201 | 0.078197 | 0.01233 | 0.075351 | 0.12817 | -0.13876 | -0.095467 | 122.1095 | -0.002797 | 122.0866 | 122.0222 | -0.087303 | -0.15988 | 0.096201 | 121.9077 | -0.020779 | 122.1004 | 122.0155 | 0.1078 | 0.032042 | -0.23489 | 122.0965 | 121.9394 | 122.1955 | 122.0366 | 0.010233 | 122.0785 | 122.1313 | 121.8644 | 122.0814 | -0.1916
3249.7188 | 122.2275 | -122.0261 | 0.11444 | 1.4211e-13 | -0.033506 | -0.0047181 | -0.0097162 | -0.01561 | 0.0093306 | -0.22823 | -0.0058878 | 0.012781 | 0.012994 | 0.048286 | -0.0020511 | 0.083459 | 0.033457 | 0.01906 | 0.088755 | -0.068325 | 0.18775 | 0.10636 | 0.10178 | 0.073618 | 0.007751 | 0.07993 | 0.11901 | -0.13876 | -0.10462 | 122.1324 | -0.025686 | 122.1095 | 122.0451 | -0.087303 | -0.18277 | 0.073311 | 121.9214 | -0.034511 | 122.1278 | 122.0338 | 0.11237 | 0.004573 | -0.25321 | 122.1148 | 121.9577 | 122.2138 | 122.0595 | -0.008078 | 122.106 | 122.1451 | 121.8873 | 122.0997 | -0.21907
3251.4531 | 122.2961 | -121.9803 | 0.091553 | 1.4211e-13 | -0.033292 | -0.0040769 | -0.0097162 | -0.015183 | 0.009758 | -0.23586 | -0.0054606 | 0.013208 | 0.012994 | 0.048286 | -0.0018375 | 0.088037 | 0.0243 | 0.023639 | 0.079598 | -0.068325 | 0.1786 | 0.11094 | 0.097201 | 0.078197 | 0.003172 | 0.075351 | 0.12359 | -0.14334 | -0.1092 | 122.0912 | -0.011955 | 122.0683 | 122.0039 | -0.087303 | -0.15988 | 0.087042 | 121.8711 | -0.016202 | 122.0775 | 121.9835 | 0.11237 | 0.03204 | -0.2349 | 122.0599 | 121.912 | 122.1589 | 122.0046 | 0.019389 | 122.0556 | 122.1039 | 121.8369 | 122.0585 | -0.20076
3253.1875 | 122.3099 | -121.9803 | 0.086975 | 1.4211e-13 | -0.033292 | -0.0040769 | -0.0095024 | -0.01561 | 0.009758 | -0.22823 | -0.0058878 | 0.012995 | 0.012994 | 0.048286 | -0.0016237 | 0.083459 | 0.033457 | 0.023639 | 0.079598 | -0.063746 | 0.18775 | 0.11094 | 0.10178 | 0.078197 | 0.016908 | 0.066194 | 0.12817 | -0.14334 | -0.10462 | 122.0912 | -0.007377 | 122.0637 | 122.0039 | -0.087303 | -0.15072 | 0.10078 | 121.8757 | -0.020781 | 122.0821 | 121.9972 | 0.12153 | 0.041197 | -0.23032 | 122.0599 | 121.9165 | 122.168 | 122.0137 | 0.023967 | 122.0465 | 122.1085 | 121.8369 | 122.0585 | -0.1916
3254.875 | 122.2641 | -121.9757 | 0.10071 | 1.4211e-13 | -0.033292 | -0.0042907 | -0.0097162 | -0.015397 | 0.0093306 | -0.23586 | -0.0056742 | 0.012781 | 0.012994 | 0.048072 | -0.0016237 | 0.07888 | 0.033457 | 0.01906 | 0.093333 | -0.059167 | 0.18775 | 0.10636 | 0.10178 | 0.073618 | 0.007751 | 0.061616 | 0.13275 | -0.14334 | -0.11378 | 122.0821 | -0.007375 | 122.0546 | 121.9948 | -0.087303 | -0.15987 | 0.087044 | 121.8619 | -0.039092 | 122.0775 | 121.9835 | 0.12153 | 0.032042 | -0.24405 | 122.069 | 121.9165 | 122.1635 | 122.0092 | 0.005655 | 122.0373 | 122.1085 | 121.8324 | 122.0493 | -0.21449
3256.625 | 122.2092 | -122.0306 | 0.12817 | 1.4211e-13 | -0.033506 | -0.0045043 | -0.0097162 | -0.015824 | 0.0095442 | -0.22823 | -0.0058878 | 0.012567 | 0.012994 | 0.048072 | -0.0018375 | 0.083459 | 0.033457 | 0.014482 | 0.079598 | -0.063746 | 0.18775 | 0.10636 | 0.10178 | 0.073618 | 0.01233 | 0.061616 | 0.12817 | -0.14334 | -0.10462 | 122.137 | -0.048576 | 122.1141 | 122.0451 | -0.091881 | -0.19192 | 0.059578 | 121.926 | -0.066558 | 122.1324 | 122.043 | 0.11695 | -2e-06 | -0.27152 | 122.1102 | 121.9669 | 122.2184 | 122.0641 | -0.021811 | 122.0923 | 122.1588 | 121.8873 | 122.1043 | -0.2328
3258.375 | 122.2458 | -122.0032 | 0.10071 | 1.4211e-13 | -0.03372 | -0.0042907 | -0.0099298 | -0.01561 | 0.0095442 | -0.22823 | -0.0056742 | 0.012781 | 0.01278 | 0.048286 | -0.0018375 | 0.083459 | 0.0243 | 0.028217 | 0.084176 | -0.059167 | 0.18317 | 0.10178 | 0.097201 | 0.082776 | 0.01233 | 0.061616 | 0.12359 | -0.13876 | -0.10004 | 122.105 | -0.016532 | 122.0866 | 122.0314 | -0.073567 | -0.15987 | 0.082465 | 121.9031 | -0.039092 | 122.1004 | 122.0155 | 0.11238 | 0.022885 | -0.23947 | 122.0874 | 121.944 | 122.1863 | 122.0275 | 0.001076 | 122.0648 | 122.1268 | 121.8644 | 122.0859 | -0.20075
3260.1406 | 122.2046 | -122.0306 | 0.10986 | 1.4211e-13 | -0.033292 | -0.0042907 | -0.0095024 | -0.015397 | 0.0095442 | -0.22823 | -0.0056742 | 0.012781 | 0.01278 | 0.047858 | -0.0016237 | 0.07888 | 0.033457 | 0.009904 | 0.079598 | -0.068325 | 0.18775 | 0.11094 | 0.097201 | 0.073618 | 0.01233 | 0.066194 | 0.12359 | -0.13876 | -0.1092 | 122.1416 | -0.030265 | 122.1095 | 122.0405 | -0.10104 | -0.17819 | 0.077889 | 121.9214 | -0.043669 | 122.1278 | 122.043 | 0.12153 | 0.01373 | -0.24863 | 122.1102 | 121.9623 | 122.2184 | 122.0641 | 0.001079 | 122.0968 | 122.1542 | 121.8919 | 122.1043 | -0.21907
3261.8906 | 122.2916 | -122.0261 | 0.10071 | 1.4211e-13 | -0.033933 | -0.0042907 | -0.0097162 | -0.01561 | 0.009758 | -0.25112 | -0.0061014 | 0.013208 | 0.013208 | 0.048499 | -0.0018375 | 0.07888 | 0.033457 | 0.01906 | 0.088755 | -0.063746 | 0.19233 | 0.11094 | 0.092622 | 0.073618 | 0.01233 | 0.061616 | 0.12817 | -0.14792 | -0.1092 | 122.137 | -0.011953 | 122.1049 | 122.0451 | -0.091882 | -0.16445 | 0.091623 | 121.9169 | -0.039092 | 122.1187 | 122.0384 | 0.12153 | 0.027464 | -0.24863 | 122.1148 | 121.9623 | 122.2184 | 122.0595 | 0.010234 | 122.0877 | 122.1542 | 121.8781 | 122.0997 | -0.20991
3263.5781 | 122.2321 | -122.0261 | 0.13733 | 1.4211e-13 | -0.03372 | -0.0040769 | -0.0097162 | -0.015397 | 0.009758 | -0.23586 | -0.0061014 | 0.012781 | 0.012567 | 0.047858 | -0.0016237 | 0.092615 | 0.028878 | 0.009904 | 0.093333 | -0.059167 | 0.18317 | 0.11094 | 0.10636 | 0.078197 | 0.01233 | 0.061616 | 0.13275 | -0.14792 | -0.1092 | 122.137 | -0.043996 | 122.1187 | 122.036 | -0.10104 | -0.1965 | 0.045844 | 121.9169 | -0.075713 | 122.1324 | 122.0384 | 0.12153 | -0.004579 | -0.28525 | 122.1194 | 121.9669 | 122.2092 | 122.0549 | -0.026387 | 122.0877 | 122.1588 | 121.8781 | 122.1043 | -0.24653
3265.3281 | 122.2412 | -122.049 | 0.11902 | 1.4211e-13 | -0.03372 | -0.0045043 | -0.0097162 | -0.016038 | 0.009758 | -0.23586 | -0.0058878 | 0.012781 | 0.012994 | 0.048286 | -0.0014101 | 0.083459 | 0.0243 | 0.01906 | 0.084176 | -0.059167 | 0.18317 | 0.11094 | 0.10636 | 0.082776 | 0.007751 | 0.066194 | 0.12359 | -0.13876 | -0.1092 | 122.1599 | -0.034843 | 122.1324 | 122.068 | -0.091882 | -0.17819 | 0.064154 | 121.9397 | -0.052825 | 122.1553 | 122.0567 | 0.11695 | 0.004574 | -0.25778 | 122.1331 | 121.9898 | 122.2321 | 122.0733 | -0.008077 | 122.1151 | 122.1725 | 121.9102 | 122.1317 | -0.22822
3267.0156 | 122.3328 | -121.9986 | 0.09613 | 1.4211e-13 | -0.033506 | -0.0038633 | -0.0097162 | -0.01561 | 0.0093306 | -0.23586 | -0.0061014 | 0.012995 | 0.012994 | 0.048286 | -0.0018375 | 0.083459 | 0.038035 | 0.01906 | 0.079598 | -0.063746 | 0.19233 | 0.10636 | 0.097201 | 0.078197 | 0.003172 | 0.061616 | 0.12359 | -0.13876 | -0.1092 | 122.105 | -0.016532 | 122.0821 | 122.0177 | -0.087303 | -0.15988 | 0.096201 | 121.8894 | -0.034514 | 122.0958 | 122.0018 | 0.11237 | 0.027463 | -0.23489 | 122.0782 | 121.9349 | 122.1909 | 122.0366 | 0.010233 | 122.0602 | 122.1222 | 121.8598 | 122.0768 | -0.20533
3268.75 | 122.2778 | -122.0398 | 0.10071 | 1.4211e-13 | -0.03372 | -0.0040769 | -0.0097162 | -0.01561 | 0.0095442 | -0.2206 | -0.0061014 | 0.012995 | 0.01278 | 0.048072 | -0.0016237 | 0.088037 | 0.038035 | 0.014482 | 0.084176 | -0.059167 | 0.1786 | 0.10636 | 0.097201 | 0.073618 | 0.007751 | 0.061616 | 0.12817 | -0.14334 | -0.1092 | 122.1462 | -0.016532 | 122.1278 | 122.0543 | -0.091881 | -0.15987 | 0.077887 | 121.9306 | -0.039092 | 122.137 | 122.0475 | 0.11695 | 0.027464 | -0.24405 | 122.124 | 121.9806 | 122.2184 | 122.0778 | 0.005655 | 122.1014 | 122.168 | 121.8965 | 122.1134 | -0.20991
3270.5156 | 122.2046 | -122.0764 | 0.12817 | 1.4211e-13 | -0.033506 | -0.0038633 | -0.0095024 | -0.015397 | 0.0093306 | -0.23586 | -0.0061014 | 0.012567 | 0.012994 | 0.048499 | -0.0022647 | 0.07888 | 0.038035 | 0.014482 | 0.084176 | -0.059167 | 0.18775 | 0.11552 | 0.10178 | 0.078197 | 0.016908 | 0.061616 | 0.11901 | -0.13419 | -0.1092 | 122.1919 | -0.043998 | 122.1553 | 122.0909 | -0.10104 | -0.18734 | 0.059578 | 121.9672 | -0.066558 | 122.1782 | 122.0933 | 0.12611 | -0.00916 | -0.26236 | 122.1606 | 122.0172 | 122.2642 | 122.1145 | -0.012653 | 122.138 | 122.1954 | 121.9422 | 122.1546 | -0.23738
3272.2656 | 122.3007 | -122.0398 | 0.09613 | 1.4211e-13 | -0.03372 | -0.0042907 | -0.0099298 | -0.01561 | 0.0095442 | -0.23586 | -0.0061014 | 0.012781 | 0.012994 | 0.048499 | -0.0018375 | 0.088037 | 0.028878 | 0.009904 | 0.084176 | -0.068325 | 0.18775 | 0.10636 | 0.097201 | 0.073618 | 0.01233 | 0.066194 | 0.11901 | -0.13419 | -0.1092 | 122.1462 | -0.011954 | 122.1278 | 122.0497 | -0.096459 | -0.16445 | 0.091622 | 121.9306 | -0.029936 | 122.137 | 122.0521 | 0.12153 | 0.022884 | -0.23032 | 122.124 | 121.9715 | 122.2275 | 122.0687 | 0.010233 | 122.106 | 122.1588 | 121.9056 | 122.1134 | -0.20533
3273.9375 | 122.2321 | -122.0627 | 0.11444 | 1.4211e-13 | -0.033292 | -0.0040769 | -0.0095024 | -0.01561 | 0.0095442 | -0.23586 | -0.0058878 | 0.012781 | 0.012994 | 0.048499 | -0.0020511 | 0.088037 | 0.038035 | 0.009904 | 0.084176 | -0.059167 | 0.18775 | 0.10636 | 0.10178 | 0.078197 | 0.01233 | 0.061616 | 0.11901 | -0.14334 | -0.1092 | 122.169 | -0.030265 | 122.1507 | 122.0726 | -0.096459 | -0.17361 | 0.073311 | 121.9535 | -0.052825 | 122.1645 | 122.075 | 0.12153 | 0.004573 | -0.25778 | 122.1469 | 122.0035 | 122.2504 | 122.1007 | -0.008078 | 122.1243 | 122.1817 | 121.9193 | 122.1409 | -0.22364
3275.6719 | 122.3053 | -122.0398 | 0.07782 | 1.4211e-13 | -0.03372 | -0.0045043 | -0.0097162 | -0.01561 | 0.0095442 | -0.23586 | -0.0056742 | 0.012995 | 0.01278 | 0.048286 | -0.0016237 | 0.092615 | 0.033457 | 0.009904 | 0.084176 | -0.059167 | 0.18317 | 0.10636 | 0.10178 | 0.073618 | 0.01233 | 0.061616 | 0.12817 | -0.14792 | -0.10462 | 122.1462 | 0.006356 | 122.1324 | 122.0497 | -0.096459 | -0.13699 | 0.10535 | 121.9352 | -0.016204 | 122.1416 | 122.0521 | 0.11695 | 0.050352 | -0.22574 | 122.124 | 121.9806 | 122.223 | 122.0733 | 0.028543 | 122.1014 | 122.168 | 121.8919 | 122.1134 | -0.18244
3277.375 | 122.3511 | -122.0215 | 0.091553 | 1.4211e-13 | -0.033933 | -0.0042907 | -0.0097162 | -0.01561 | 0.009117 | -0.23586 | -0.0058878 | 0.012781 | 0.01278 | 0.048286 | -0.0018375 | 0.088037 | 0.028878 | 0.014482 | 0.093333 | -0.059167 | 0.18775 | 0.11094 | 0.10636 | 0.078197 | 0.003172 | 0.061616 | 0.12817 | -0.14792 | -0.11378 | 122.1324 | 0.00178 | 122.1095 | 122.036 | -0.09646 | -0.15072 | 0.096199 | 121.9077 | -0.029937 | 122.1278 | 122.0247 | 0.11695 | 0.036619 | -0.23947 | 122.1148 | 121.9623 | 122.2092 | 122.0504 | 0.019389 | 122.0831 | 122.1497 | 121.8736 | 122.0997 | -0.20533
3279.0625 | 122.2366 | -122.081 | 0.11902 | 1.4211e-13 | -0.03372 | -0.0042907 | -0.0095024 | -0.015397 | 0.0095442 | -0.23586 | -0.0058878 | 0.012781 | 0.01278 | 0.048499 | -0.0018375 | 0.088037 | 0.033457 | 0.014482 | 0.07502 | -0.059167 | 0.17402 | 0.10178 | 0.097201 | 0.078197 | 0.007751 | 0.057037 | 0.12817 | -0.13876 | -0.1092 | 122.1828 | -0.043999 | 122.169 | 122.0955 | -0.087302 | -0.17819 | 0.054997 | 121.9718 | -0.061982 | 122.1782 | 122.0887 | 0.11695 | 0.009153 | -0.25778 | 122.156 | 122.0218 | 122.255 | 122.1145 | -0.017235 | 122.138 | 122.2092 | 121.9422 | 122.1592 | -0.22822
3280.8281 | 122.3831 | -122.0398 | 0.082397 | 1.4211e-13 | -0.033506 | -0.0042907 | -0.0097162 | -0.01561 | 0.0089032 | -0.2206 | -0.0058878 | 0.012781 | 0.012994 | 0.048072 | -0.0024783 | 0.083459 | 0.0243 | 0.005325 | 0.093333 | -0.063746 | 0.18317 | 0.11094 | 0.097201 | 0.078197 | 0.01233 | 0.066194 | 0.12817 | -0.13876 | -0.10462 | 122.1507 | 0.010936 | 122.1233 | 122.0451 | -0.10562 | -0.14614 | 0.10078 | 121.9352 | -0.016203 | 122.137 | 122.0521 | 0.11695 | 0.045775 | -0.22116 | 122.1331 | 121.976 | 122.223 | 122.0641 | 0.028545 | 122.106 | 122.168 | 121.901 | 122.118 | -0.18702
3282.5938 | 122.319 | -122.0581 | 0.091553 | 1.4211e-13 | -0.03372 | -0.0040769 | -0.0097162 | -0.015397 | 0.0093306 | -0.23586 | -0.0061014 | 0.012567 | 0.012567 | 0.048286 | -0.0020511 | 0.083459 | 0.028878 | 0.009904 | 0.084176 | -0.068325 | 0.18317 | 0.11094 | 0.10178 | 0.06904 | 0.007751 | 0.061616 | 0.13275 | -0.13419 | -0.1092 | 122.169 | -0.007377 | 122.1416 | 122.068 | -0.10104 | -0.15988 | 0.09162 | 121.9489 | -0.029937 | 122.1599 | 122.0659 | 0.11695 | 0.041197 | -0.22574 | 122.1423 | 121.9898 | 122.2413 | 122.087 | 0.019389 | 122.1197 | 122.1909 | 121.9239 | 122.1271 | -0.20076
3284.3438 | 122.287 | -122.081 | 0.11444 | 1.4211e-13 | -0.033933 | -0.0042907 | -0.0095024 | -0.015824 | 0.0093306 | -0.23586 | -0.0061014 | 0.012995 | 0.01278 | 0.048286 | -0.0020511 | 0.083459 | 0.033457 | 0.009904 | 0.084176 | -0.054588 | 0.18317 | 0.10636 | 0.097201 | 0.06904 | 0.007751 | 0.061616 | 0.12817 | -0.14334 | -0.11378 | 122.1874 | -0.030265 | 122.1645 | 122.0909 | -0.096459 | -0.16903 | 0.068732 | 121.9672 | -0.052825 | 122.1782 | 122.0887 | 0.12153 | 0.013731 | -0.25778 | 122.1652 | 122.0264 | 122.2642 | 122.1145 | -0.008078 | 122.1426 | 122.2092 | 121.9377 | 122.15 | -0.22822
3286.0312 | 122.2549 | -122.0901 | 0.11902 | 1.4211e-13 | -0.03372 | -0.0049317 | -0.0099298 | -0.016038 | 0.0095442 | -0.24349 | -0.0058878 | 0.012567 | 0.01278 | 0.048713 | -0.0018375 | 0.07888 | 0.033457 | 0.005325 | 0.084176 | -0.068325 | 0.18775 | 0.11094 | 0.092622 | 0.06904 | 0.007751 | 0.061616 | 0.13275 | -0.13876 | -0.1092 | 122.2011 | -0.034843 | 122.169 | 122.0955 | -0.10562 | -0.18734 | 0.068733 | 121.9809 | -0.057403 | 122.1828 | 122.0979 | 0.11695 | 0.013731 | -0.25778 | 122.1743 | 122.0218 | 122.2779 | 122.1236 | -0.008077 | 122.1518 | 122.2229 | 121.9514 | 122.1592 | -0.22822
3287.7969 | 122.2549 | -122.0947 | 0.13275 | 1.4211e-13 | -0.033292 | -0.0042907 | -0.0099298 | -0.015397 | 0.0093306 | -0.23586 | -0.0061014 | 0.012781 | 0.01278 | 0.047858 | -0.0020511 | 0.083459 | 0.028878 | 0.014482 | 0.079598 | -0.063746 | 0.18775 | 0.10178 | 0.097201 | 0.078197 | -0.001407 | 0.061616 | 0.12817 | -0.14334 | -0.10462 | 122.1965 | -0.053153 | 122.1782 | 122.1092 | -0.087302 | -0.1965 | 0.055001 | 121.9901 | -0.071135 | 122.1919 | 122.0933 | 0.10322 | -0.004579 | -0.27609 | 122.1743 | 122.031 | 122.2825 | 122.1236 | -0.030967 | 122.1563 | 122.2229 | 121.9514 | 122.1729 | -0.23738
3289.4688 | 122.2549 | -122.0993 | 0.13733 | 1.4211e-13 | -0.034147 | -0.0045043 | -0.0092888 | -0.015183 | 0.009117 | -0.23586 | -0.0061014 | 0.012781 | 0.012567 | 0.048499 | -0.0020511 | 0.07888 | 0.033457 | 0.000747 | 0.079598 | -0.063746 | 0.18775 | 0.11094 | 0.092622 | 0.06904 | 0.007751 | 0.061616 | 0.12817 | -0.14334 | -0.1092 | 122.2102 | -0.057731 | 122.1782 | 122.1001 | -0.1102 | -0.20108 | 0.050423 | 121.9901 | -0.075713 | 122.1919 | 122.1071 | 0.11695 | -0.009157 | -0.28067 | 122.1789 | 122.0356 | 122.2871 | 122.1328 | -0.026387 | 122.1609 | 122.2275 | 121.956 | 122.1683 | -0.24653
3291.2188 | 122.2778 | -122.1039 | 0.09613 | 1.4211e-13 | -0.033506 | -0.0042907 | -0.0097162 | -0.01561 | 0.0095442 | -0.23586 | -0.0058878 | 0.012995 | 0.01278 | 0.048499 | -0.0020511 | 0.092615 | 0.038035 | 0.009904 | 0.084176 | -0.059167 | 0.1786 | 0.10178 | 0.097201 | 0.073618 | 0.007751 | 0.061616 | 0.12359 | -0.14334 | -0.11378 | 122.2057 | -0.011954 | 122.1965 | 122.1138 | -0.09188 | -0.1553 | 0.082465 | 121.9901 | -0.034514 | 122.2011 | 122.1116 | 0.12153 | 0.027463 | -0.23947 | 122.1881 | 122.0447 | 122.2825 | 122.1419 | 0.005654 | 122.1655 | 122.2275 | 121.9605 | 122.1775 | -0.20991
3292.9062 | 122.2641 | -122.1268 | 0.11444 | 1.4211e-13 | -0.03372 | -0.0045043 | -0.0099298 | -0.01561 | 0.0093306 | -0.24349 | -0.0061014 | 0.012781 | 0.012994 | 0.048713 | -0.0018375 | 0.07888 | 0.0243 | 0.009904 | 0.088755 | -0.054588 | 0.1786 | 0.11094 | 0.10178 | 0.078197 | 0.007751 | 0.057037 | 0.12359 | -0.13419 | -0.11378 | 122.2377 | -0.025686 | 122.2056 | 122.1367 | -0.10104 | -0.16903 | 0.064154 | 122.013 | -0.057404 | 122.2285 | 122.1345 | 0.12153 | 0.009152 | -0.24863 | 122.2155 | 122.0722 | 122.3054 | 122.1511 | -0.003499 | 122.1838 | 122.2504 | 121.9926 | 122.205 | -0.22822
3294.6562 | 122.4106 | -122.0673 | 0.068665 | 1.4211e-13 | -0.033933 | -0.0045043 | -0.0097162 | -0.015397 | 0.009117 | -0.22823 | -0.0061014 | 0.012781 | 0.012353 | 0.048499 | -0.0020511 | 0.092615 | 0.028878 | 0.005325 | 0.079598 | -0.063746 | 0.18317 | 0.10636 | 0.097201 | 0.073618 | 0.016908 | 0.066194 | 0.11444 | -0.14334 | -0.11378 | 122.1736 | 0.010933 | 122.1599 | 122.0726 | -0.10104 | -0.13241 | 0.11451 | 121.9535 | -0.002471 | 122.1645 | 122.0842 | 0.13069 | 0.045771 | -0.21201 | 122.1469 | 122.0035 | 122.2504 | 122.0961 | 0.037698 | 122.1335 | 122.1817 | 121.9239 | 122.1409 | -0.18245
3296.3438 | 122.3923 | -122.0581 | 0.064087 | 1.4211e-13 | -0.033933 | -0.0040769 | -0.0099298 | -0.01561 | 0.0095442 | -0.23586 | -0.0058878 | 0.012567 | 0.012567 | 0.048499 | -0.0016237 | 0.088037 | 0.038035 | 0.005325 | 0.079598 | -0.059167 | 0.18317 | 0.10636 | 0.10178 | 0.06904 | 0.01233 | 0.061616 | 0.12359 | -0.14792 | -0.11378 | 122.1645 | 0.015511 | 122.1461 | 122.0634 | -0.10104 | -0.12325 | 0.11909 | 121.9443 | -0.002471 | 122.1599 | 122.0704 | 0.12611 | 0.059506 | -0.21201 | 122.1377 | 121.9989 | 122.2413 | 122.0961 | 0.042276 | 122.1197 | 122.1817 | 121.9102 | 122.1271 | -0.17787
3298.0938 | 122.2687 | -122.0993 | 0.1236 | 1.4211e-13 | -0.033933 | -0.0045043 | -0.0099298 | -0.015824 | 0.0095442 | -0.25112 | -0.0061014 | 0.012567 | 0.012567 | 0.048286 | -0.0020511 | 0.083459 | 0.028878 | 0.000747 | 0.084176 | -0.059167 | 0.1786 | 0.10636 | 0.097201 | 0.073618 | 0.007751 | 0.061616 | 0.12359 | -0.14334 | -0.1092 | 122.2057 | -0.03942 | 122.1828 | 122.1001 | -0.10562 | -0.18276 | 0.054999 | 121.9901 | -0.06198 | 122.1965 | 122.1071 | 0.11695 | -3e-06 | -0.26694 | 122.1835 | 122.0401 | 122.2779 | 122.1282 | -0.017233 | 122.1609 | 122.2229 | 121.956 | 122.1729 | -0.2328
3299.8438 | 122.3602 | -122.0947 | 0.082397 | 1.4211e-13 | -0.034361 | -0.0045043 | -0.0097162 | -0.01561 | 0.009117 | -0.25112 | -0.0056742 | 0.012781 | 0.012994 | 0.048499 | -0.0018375 | 0.07888 | 0.038035 | -0.003831 | 0.084176 | -0.063746 | 0.18775 | 0.11094 | 0.097201 | 0.073618 | 0.003172 | 0.066194 | 0.12359 | -0.13876 | -0.10004 | 122.2057 | 0.001779 | 122.1736 | 122.0909 | -0.11477 | -0.14614 | 0.10536 | 121.9947 | -0.016203 | 122.1919 | 122.0979 | 0.10322 | 0.041196 | -0.22116 | 122.1789 | 122.031 | 122.2825 | 122.1328 | 0.028545 | 122.1609 | 122.2183 | 121.956 | 122.1683 | -0.18244
3301.5312 | 122.4106 | -122.0627 | 0.091553 | 1.4211e-13 | -0.034361 | -0.0040769 | -0.0095024 | -0.015397 | 0.0095442 | -0.23586 | -0.0063152 | 0.012567 | 0.01278 | 0.048499 | -0.0018375 | 0.069723 | 0.028878 | 0.005325 | 0.084176 | -0.059167 | 0.19233 | 0.11552 | 0.10178 | 0.06904 | 0.003172 | 0.061616 | 0.12817 | -0.14334 | -0.1092 | 122.1782 | -0.007377 | 122.1324 | 122.068 | -0.1102 | -0.15072 | 0.10078 | 121.9535 | -0.029937 | 122.1645 | 122.0659 | 0.11237 | 0.036619 | -0.2349 | 122.1469 | 122.0035 | 122.255 | 122.0916 | 0.023968 | 122.1243 | 122.1909 | 121.9193 | 122.1317 | -0.20076

## Thermal Data
Fire Time | B Position - Middle | B Position - Kerite 10c w | D Position - 3' | D Position - Middle | D Position - 7' | D Position - Armored 3' | D Position - Armored 5' | D Position - Armored 7'
-0.6833 | 9.5457 | 9.114 | 10.3604 | 14.6612 | 9.9468 | 9.4625 | 9.0433 | 9.0386
0.3167 | 9.5449 | 9.1125 | 10.3598 | 14.6642 | 9.936 | 9.4706 | 9.0437 | 9.0371
1.3167 | 9.558 | 9.1131 | 10.3629 | 14.6601 | 9.9393 | 9.4679 | 9.042 | 9.0313
2.3167 | 9.5731 | 9.1184 | 10.3612 | 14.6761 | 9.9359 | 9.4703 | 9.0408 | 9.0392
3.3167 | 9.5847 | 9.1152 | 10.3559 | 14.6579 | 9.9399 | 9.473 | 9.0373 | 9.0274
4.3167 | 9.5792 | 9.1188 | 10.3511 | 14.6744 | 9.9395 | 9.4599 | 9.041 | 9.0298
5.3167 | 9.5795 | 9.117 | 10.372 | 14.713 | 9.9474 | 9.4619 | 9.0403 | 9.0409
6.3167 | 9.6007 | 9.1217 | 10.8384 | 15.0893 | 9.9512 | 9.4523 | 9.0386 | 9.0169
7.3167 | 9.6274 | 9.1257 | 11.3981 | 15.7038 | 10.1291 | 9.4274 | 9.0354 | 9.0346
8.3167 | 9.7009 | 9.1217 | 13.6391 | 16.6607 | 11.3313 | 9.3433 | 9.0233 | 9.0636
9.3167 | 9.8371 | 9.1032 | 16.2096 | 23.7718 | 13.6734 | 9.2572 | 9.0146 | 9.0761
10.3167 | 10.1031 | 9.1035 | 19.7706 | 23.8915 | 15.6148 | 9.2711 | 9.0268 | 9.0965
11.3167 | 10.8565 | 9.0973 | 24.4203 | 23.8991 | 16.906 | 9.2752 | 9.0261 | 9.0776
12.3167 | 11.677 | 9.1063 | 32.072 | 23.9037 | 19.8416 | 9.1465 | 9.0124 | 9.105
13.3167 | 12.901 | 9.1193 | 39.1357 | 23.9164 | 24.4956 | 9.0799 | 9.0108 | 9.1556
14.3167 | 13.5505 | 9.1502 | 44.4399 | 23.9188 | 27.1696 | 9.1218 | 9.0252 | 9.1714
15.3167 | 14.5821 | 9.1708 | 49.2618 | 23.9167 | 28.8317 | 9.211 | 9.0221 | 9.1643
16.3167 | 16.1696 | 9.2338 | 50.9169 | 23.9282 | 30.5283 | 9.2505 | 9.0352 | 9.1261
17.3167 | 17.9136 | 9.2874 | 54.7357 | 23.9249 | 32.1452 | 9.2513 | 9.0354 | 9.1539
18.3167 | 19.079 | 9.3492 | 56.8385 | 23.9303 | 34.3156 | 9.2457 | 9.0356 | 9.1916
19.3167 | 20.0216 | 9.4464 | 59.3208 | 23.9385 | 35.4197 | 9.2318 | 9.0475 | 9.2157
20.3167 | 20.7805 | 9.5775 | 61.8536 | 23.9307 | 37.976 | 9.2056 | 9.0488 | 9.237
21.3167 | 22.0379 | 9.7104 | 65.7431 | 23.9358 | 41.5309 | 9.1449 | 9.0448 | 9.2794
22.3167 | 23.2429 | 9.828 | 70.2154 | 23.9498 | 46.4228 | 9.1352 | 9.0675 | 9.2984
23.3167 | 24.6636 | 10.0025 | 73.744 | 23.9521 | 50.4616 | 9.1328 | 9.056 | 9.3263
24.3167 | 25.6395 | 10.1891 | 76.7188 | 23.9453 | 53.2801 | 9.2528 | 9.0506 | 9.2774
25.3167 | 27.5491 | 10.4048 | 80.0903 | 23.9568 | 56.0681 | 9.3134 | 9.0517 | 9.2959
26.3167 | 29.5115 | 10.5988 | 83.6435 | 23.9602 | 58.6156 | 9.3596 | 9.0775 | 9.2892
27.3167 | 30.0407 | 10.8095 | 87.0025 | 23.9769 | 62.2601 | 9.3992 | 9.0892 | 9.3193
28.3167 | 30.2874 | 11.0286 | 88.6989 | 23.9742 | 64.5767 | 9.4032 | 9.0781 | 9.335
29.3167 | 31.796 | 11.2451 | 91.2468 | 23.9758 | 67.939 | 9.5532 | 9.1108 | 9.3098
30.3167 | 32.3244 | 11.4663 | 92.906 | 23.9796 | 70.0996 | 9.6517 | 9.1276 | 9.3158
31.3167 | 33.7142 | 11.7285 | 94.2814 | 23.9827 | 72.065 | 9.6278 | 9.1181 | 9.346
32.3167 | 34.5068 | 11.9462 | 94.999 | 23.9841 | 73.4983 | 9.6392 | 9.15 | 9.3727
33.3167 | 35.4438 | 12.1664 | 96.3639 | 23.9906 | 74.9267 | 9.7524 | 9.1607 | 9.3494
34.3167 | 36.6241 | 12.4023 | 97.7332 | 23.9838 | 77.3002 | 9.8851 | 9.1947 | 9.3311
35.3167 | 37.7731 | 12.6445 | 99.8871 | 23.9987 | 79.498 | 9.9009 | 9.2055 | 9.3636
36.3167 | 39.0229 | 12.9077 | 101.6225 | 24.0045 | 81.8595 | 9.9117 | 9.208 | 9.3732
37.3167 | 39.8403 | 13.1447 | 104.3262 | 24.0084 | 83.7373 | 9.9433 | 9.2341 | 9.3697
38.3167 | 40.5508 | 13.3742 | 105.7444 | 24.0129 | 85.2177 | 10.0461 | 9.271 | 9.3898
39.3167 | 42.1702 | 13.6062 | 106.7416 | 24.0136 | 86.8987 | 10.1158 | 9.2666 | 9.4132
40.3167 | 43.06 | 13.8397 | 107.2293 | 24.0201 | 88.8537 | 10.2174 | 9.2943 | 9.3862
41.3167 | 44.3791 | 14.0762 | 108.3987 | 24.0308 | 89.9017 | 10.2917 | 9.3192 | 9.3977
42.3167 | 45.2886 | 14.3023 | 109.5592 | 24.0186 | 91.0565 | 10.3747 | 9.3404 | 9.4124
43.3167 | 46.0827 | 14.5451 | 109.7306 | 24.0242 | 92.4942 | 10.4171 | 9.3791 | 9.4293
44.3167 | 47.1983 | 14.7845 | 111.228 | 24.03 | 93.7177 | 10.5441 | 9.3687 | 9.4272
45.3167 | 48.384 | 14.9962 | 112.7311 | 24.0422 | 96.0917 | 10.5275 | 9.4107 | 9.4874
46.3167 | 48.7227 | 15.2285 | 114.0054 | 24.0494 | 97.8841 | 10.6394 | 9.4318 | 9.4659
47.3167 | 49.4085 | 15.4569 | 116.2567 | 24.0384 | 99.8806 | 10.7071 | 9.4719 | 9.4867
48.3167 | 49.5093 | 15.6827 | 116.6098 | 24.0529 | 101.9395 | 10.7071 | 9.4955 | 9.4991
49.3167 | 50.8997 | 15.8835 | 118.3171 | 24.0505 | 105.4964 | 10.6991 | 9.4996 | 9.5591
50.3167 | 51.9384 | 16.0975 | 119.5038 | 24.0498 | 106.8769 | 10.9873 | 9.5642 | 9.5287
51.3167 | 52.4962 | 16.3146 | 121.3088 | 24.064 | 108.1422 | 11.1323 | 9.597 | 9.5113
52.3167 | 53.8271 | 16.5472 | 122.251 | 24.0686 | 108.8896 | 11.1925 | 9.624 | 9.535
53.3167 | 54.0083 | 16.7673 | 122.8688 | 24.0728 | 111.177 | 11.2332 | 9.6697 | 9.5776
54.3167 | 54.9344 | 16.9663 | 123.4652 | 24.0661 | 113.3448 | 11.3145 | 9.6828 | 9.6169
55.3167 | 55.9298 | 17.2379 | 122.7712 | 24.0676 | 114.9923 | 11.3673 | 9.735 | 9.6414
56.3167 | 56.479 | 17.4515 | 122.2807 | 24.0691 | 116.5485 | 11.4813 | 9.7857 | 9.6307
57.3167 | 57.1225 | 17.6709 | 122.5654 | 24.0863 | 117.8386 | 11.5676 | 9.8112 | 9.689
58.3167 | 57.9187 | 17.8892 | 123.1375 | 24.082 | 118.7676 | 11.6487 | 9.8325 | 9.7035
59.3167 | 58.5971 | 18.1055 | 123.2165 | 24.0884 | 119.0811 | 11.7262 | 9.8753 | 9.6794
60.3167 | 59.3734 | 18.3014 | 123.834 | 24.088 | 120.1472 | 11.8704 | 9.9139 | 9.679
61.3167 | 60.1787 | 18.5062 | 123.6488 | 24.0952 | 121.142 | 11.945 | 9.9716 | 9.7023
62.3167 | 60.7607 | 18.7111 | 123.2558 | 24.0908 | 121.5507 | 11.9986 | 10.0167 | 9.754
63.3167 | 61.652 | 18.8777 | 123.6987 | 24.0961 | 122.2534 | 12.1 | 10.0552 | 9.7457
64.3167 | 62.3323 | 19.0868 | 123.6651 | 24.1023 | 122.5236 | 12.2221 | 10.0873 | 9.7601
65.3167 | 63.1386 | 19.289 | 124.3362 | 24.1069 | 122.7165 | 12.2394 | 10.1527 | 9.814
66.3167 | 63.7126 | 19.4885 | 124.6379 | 24.1173 | 123.857 | 12.3088 | 10.2002 | 9.8917
67.3167 | 64.1701 | 19.6767 | 124.7982 | 24.1142 | 124.8052 | 12.3916 | 10.2383 | 9.8757
68.3167 | 65.5313 | 19.8595 | 125.1903 | 24.118 | 125.0526 | 12.5276 | 10.3042 | 9.8804
69.3167 | 66.18 | 20.0215 | 125.4524 | 24.1224 | 126.1897 | 12.6158 | 10.3543 | 9.9078
70.3167 | 66.7141 | 20.2068 | 125.7732 | 24.1297 | 127.3386 | 12.6637 | 10.3858 | 9.9637
71.3167 | 66.8634 | 20.3545 | 126.0909 | 24.1281 | 128.6299 | 12.7432 | 10.4399 | 10.006
72.3167 | 67.1586 | 20.5241 | 126.5367 | 24.135 | 130.148 | 12.7989 | 10.4992 | 10.0319
73.3167 | 67.6307 | 20.7074 | 126.858 | 24.1397 | 130.7665 | 12.8589 | 10.5591 | 10.0524
74.3167 | 69.1264 | 20.8738 | 127.4187 | 24.1433 | 131.2657 | 12.9661 | 10.6436 | 10.1268
75.3167 | 69.9039 | 21.0357 | 129.0225 | 24.1421 | 133.0479 | 12.9954 | 10.6725 | 10.1425
76.3167 | 70.3769 | 21.2024 | 129.0375 | 24.1442 | 135.6374 | 13.0632 | 10.7425 | 10.2128
77.3167 | 71.2971 | 21.3539 | 128.813 | 24.1551 | 135.9598 | 13.2047 | 10.813 | 10.2317
78.3167 | 71.3881 | 21.5289 | 128.46 | 24.161 | 136.4288 | 13.359 | 10.8797 | 10.2386
79.3167 | 71.9881 | 21.6894 | 128.2703 | 24.1597 | 136.6855 | 13.4292 | 10.908 | 10.2466
80.3167 | 73.0633 | 21.8329 | 128.5345 | 24.1696 | 136.7798 | 13.5095 | 10.9887 | 10.2847
81.3167 | 73.5313 | 22.007 | 129.0466 | 24.1772 | 136.9122 | 13.5935 | 11.0442 | 10.3549
82.3167 | 74.312 | 22.1599 | 129.7698 | 24.1762 | 137.4993 | 13.5483 | 11.117 | 10.4245
83.3323 | 74.5614 | 22.3199 | 130.4433 | 24.1817 | 137.8357 | 13.7335 | 11.1752 | 10.4342
84.3167 | 74.7218 | 22.4419 | 131.898 | 24.182 | 138.5081 | 13.822 | 11.2247 | 10.4502
85.3167 | 74.909 | 22.5904 | 131.9851 | 24.1837 | 138.4727 | 13.9233 | 11.2761 | 10.5045
86.3167 | 75.3774 | 22.7647 | 131.9439 | 24.1835 | 138.5932 | 13.983 | 11.3526 | 10.5604
87.3167 | 75.805 | 22.9184 | 132.0343 | 24.1798 | 139.6988 | 14.0879 | 11.4052 | 10.5794
88.3167 | 76.2508 | 23.0884 | 131.8111 | 24.1897 | 140.0376 | 14.1993 | 11.5156 | 10.6202
89.3167 | 76.1505 | 23.2503 | 131.7827 | 24.2108 | 140.7166 | 14.2777 | 11.5794 | 10.6996
90.3167 | 76.48 | 23.4295 | 131.8192 | 24.2108 | 141.3168 | 14.3376 | 11.6265 | 10.7391
91.3167 | 77.0571 | 23.5837 | 132.3149 | 24.212 | 141.1724 | 14.4922 | 11.7186 | 10.7521
92.3167 | 78.0233 | 23.7349 | 133.4588 | 24.2164 | 141.5829 | 14.5434 | 11.7623 | 10.8054
93.3167 | 78.3281 | 23.8773 | 133.6066 | 24.2098 | 142.4054 | 14.6218 | 11.8591 | 10.8417
94.3167 | 79.1057 | 24.0233 | 133.9699 | 24.2165 | 142.7552 | 14.7048 | 11.9143 | 10.8681
95.3167 | 79.443 | 24.1891 | 134.1203 | 24.2165 | 143.5624 | 14.8288 | 11.9924 | 10.9407
96.3167 | 80.3175 | 24.3453 | 134.3523 | 24.23 | 143.3117 | 14.9269 | 12.0671 | 10.9581
97.3167 | 80.3762 | 24.4836 | 135.493 | 24.2151 | 143.6138 | 14.9681 | 12.1271 | 11.0288
98.3167 | 80.5497 | 24.603 | 135.8214 | 24.2397 | 144.2935 | 15.0801 | 12.2198 | 11.0845
99.3167 | 81.6164 | 24.7982 | 135.6633 | 24.2324 | 144.7124 | 15.1596 | 12.2916 | 11.1267
100.3167 | 82.2528 | 24.9304 | 136.365 | 24.2425 | 145.391 | 15.2073 | 12.3492 | 11.2079
101.3167 | 82.4767 | 25.1033 | 137.0594 | 24.2434 | 146.9557 | 15.2675 | 12.4301 | 11.2745
102.3167 | 83.3324 | 25.2444 | 138.5938 | 24.239 | 147.4167 | 15.4024 | 12.502 | 11.3162
103.3167 | 84.1909 | 25.3797 | 139.4801 | 24.2557 | 147.5262 | 15.4997 | 12.5707 | 11.3624
104.3167 | 84.7018 | 25.5695 | 140.9229 | 24.2479 | 147.4665 | 15.6133 | 12.6788 | 11.3973
105.3167 | 85.4888 | 25.6951 | 142.223 | 24.2488 | 148.1812 | 15.6652 | 12.7299 | 11.4803
106.3167 | 85.9335 | 25.8903 | 144.7071 | 24.2541 | 147.5537 | 15.8012 | 12.8152 | 11.4769
107.3167 | 86.9472 | 26.0744 | 145.1341 | 24.2572 | 148.3581 | 15.8008 | 12.9157 | 11.592
108.3167 | 87.709 | 26.2885 | 146.1795 | 24.2617 | 148.8595 | 15.9193 | 12.9995 | 11.6376
109.3167 | 87.7463 | 26.4868 | 146.7074 | 24.2708 | 149.9374 | 15.9975 | 13.0762 | 11.7038
110.3167 | 88.3451 | 26.6941 | 146.3559 | 24.2627 | 152.6238 | 16.065 | 13.136 | 11.7837
111.3167 | 88.5991 | 26.8712 | 146.9917 | 24.2715 | 154.2774 | 16.1578 | 13.2235 | 11.8445
112.3167 | 88.6762 | 27.0775 | 147.3327 | 24.2772 | 155.0583 | 16.302 | 13.3426 | 11.9108
113.3167 | 89.8799 | 27.2614 | 147.1789 | 24.2771 | 155.5892 | 16.4376 | 13.4475 | 11.9649
114.3167 | 89.8362 | 27.46 | 148.0821 | 24.2751 | 155.5118 | 16.5493 | 13.5245 | 11.9782
115.3167 | 89.8972 | 27.6587 | 148.1272 | 24.2866 | 156.2348 | 16.6623 | 13.6162 | 12.0462
116.3167 | 90.7025 | 27.8755 | 148.1049 | 24.2876 | 156.1952 | 16.791 | 13.7222 | 12.0796
117.3167 | 91.1527 | 28.0643 | 147.1289 | 24.2955 | 156.072 | 16.9069 | 13.8265 | 12.1616
118.3167 | 90.979 | 28.2525 | 147.245 | 24.2917 | 155.8441 | 16.9809 | 13.8873 | 12.2338
119.3167 | 90.8645 | 28.45 | 148.0294 | 24.3055 | 155.6436 | 17.0995 | 13.9831 | 12.3077
120.3167 | 91.2106 | 28.6194 | 147.9968 | 24.3068 | 156.5153 | 17.1302 | 14.1055 | 12.3715
121.3167 | 91.1813 | 28.7966 | 148.5459 | 24.3147 | 156.8283 | 17.2331 | 14.1562 | 12.4482
122.3167 | 91.5592 | 28.9724 | 148.7285 | 24.3091 | 156.828 | 17.359 | 14.2744 | 12.5176
123.3167 | 91.379 | 29.1618 | 149.777 | 24.3105 | 157.1284 | 17.472 | 14.3616 | 12.5892
124.3167 | 92.0045 | 29.3056 | 149.4822 | 24.319 | 156.6897 | 17.5984 | 14.4522 | 12.602
125.3167 | 92.7451 | 29.4714 | 149.1697 | 24.3185 | 155.8544 | 17.712 | 14.5275 | 12.6762
126.3167 | 93.118 | 29.6455 | 148.7916 | 24.3274 | 154.5765 | 17.7802 | 14.6393 | 12.7479
127.3167 | 93.0496 | 29.7945 | 150.1768 | 24.3282 | 154.6504 | 17.8296 | 14.7162 | 12.8332
128.3167 | 93.1773 | 29.9797 | 150.2967 | 24.3309 | 155.5353 | 17.9236 | 14.8357 | 12.9266
129.3167 | 93.585 | 30.154 | 150.8908 | 24.3312 | 155.7586 | 18.0165 | 14.9058 | 12.9856
130.3167 | 93.2278 | 30.3234 | 151.9688 | 24.3285 | 156.3528 | 18.159 | 15.0411 | 13.0599
131.3167 | 92.8996 | 30.4952 | 151.703 | 24.3397 | 156.0179 | 18.3148 | 15.1208 | 13.0913
132.3167 | 92.899 | 30.6915 | 152.6986 | 24.3431 | 155.5681 | 18.4213 | 15.2332 | 13.167
133.3167 | 93.5374 | 30.8791 | 152.3123 | 24.351 | 155.2034 | 18.5229 | 15.3386 | 13.2463
134.3167 | 94.024 | 31.0771 | 152.2769 | 24.358 | 155.304 | 18.6157 | 15.4455 | 13.3266
135.3167 | 94.5104 | 31.2591 | 152.8156 | 24.3638 | 155.0236 | 18.6472 | 15.5462 | 13.4195
136.3167 | 94.7747 | 31.4401 | 152.7717 | 24.3623 | 155.3603 | 18.8101 | 15.6381 | 13.4688
137.3167 | 96.0748 | 31.6505 | 152.6322 | 24.3509 | 155.0868 | 18.9307 | 15.7262 | 13.5169
138.3167 | 96.1775 | 31.8299 | 152.4457 | 24.3609 | 155.1049 | 19.0526 | 15.8487 | 13.6124
139.3167 | 96.8873 | 32.0226 | 152.1228 | 24.3755 | 154.2598 | 19.1597 | 15.9468 | 13.6937
140.3167 | 97.306 | 32.2208 | 151.6007 | 24.3757 | 153.897 | 19.2425 | 16.0553 | 13.7572
141.3167 | 97.4192 | 32.3885 | 150.9355 | 24.3774 | 152.9758 | 19.3539 | 16.1536 | 13.8475
142.3167 | 97.5792 | 32.5803 | 150.9681 | 24.3818 | 152.4083 | 19.4967 | 16.2528 | 13.9003
143.3167 | 97.6982 | 32.7658 | 150.3746 | 24.3891 | 152.2852 | 19.556 | 16.3544 | 13.9949
144.3167 | 97.0527 | 32.9426 | 151.1191 | 24.3878 | 151.801 | 19.6789 | 16.4391 | 14.0597
145.3167 | 97.0737 | 33.1128 | 151.7954 | 24.3909 | 151.4432 | 19.7858 | 16.5418 | 14.1308
146.3167 | 97.5164 | 33.2807 | 151.2021 | 24.3966 | 151.1766 | 19.923 | 16.6773 | 14.2395
147.3167 | 98.0403 | 33.4596 | 151.1014 | 24.4013 | 150.8976 | 20.039 | 16.7853 | 14.3005
148.3167 | 98.1381 | 33.6364 | 150.572 | 24.3979 | 150.9304 | 20.1236 | 16.8745 | 14.3726
149.3167 | 97.8606 | 33.7957 | 150.2488 | 24.4065 | 151.6892 | 20.2298 | 16.9803 | 14.4645
150.3167 | 98.2194 | 33.9761 | 149.6625 | 24.4125 | 151.8494 | 20.3292 | 17.1053 | 14.5563
151.3167 | 98.3124 | 34.1414 | 149.8753 | 24.4081 | 151.837 | 20.4039 | 17.213 | 14.6213
152.3167 | 98.7618 | 34.282 | 151.3736 | 24.4174 | 152.7975 | 20.5009 | 17.288 | 14.7119
153.3167 | 98.8059 | 34.4744 | 151.8941 | 24.422 | 153.2599 | 20.6654 | 17.4161 | 14.789
154.3167 | 99.5408 | 34.6454 | 152.0149 | 24.4232 | 153.1247 | 20.7717 | 17.5263 | 14.8659
155.3167 | 99.8504 | 34.8126 | 152.1634 | 24.4266 | 153.9599 | 20.8365 | 17.6506 | 14.9685
156.3167 | 99.5653 | 34.9649 | 151.9002 | 24.4262 | 155.1017 | 20.9642 | 17.7532 | 15.0363
157.3167 | 99.8698 | 35.1149 | 151.2992 | 24.4404 | 155.6179 | 21.1086 | 17.8645 | 15.1249
158.3167 | 99.7594 | 35.2472 | 150.7174 | 24.4281 | 156.2727 | 21.1871 | 17.9997 | 15.1776
159.3167 | 100.4036 | 35.4365 | 150.6014 | 24.4355 | 156.0688 | 21.2987 | 18.0881 | 15.2581
160.3167 | 100.7307 | 35.5765 | 150.0543 | 24.4492 | 156.6539 | 21.4028 | 18.2275 | 15.3563
161.3167 | 101.7029 | 35.7316 | 149.908 | 24.4523 | 156.8175 | 21.4861 | 18.312 | 15.4445
162.3167 | 102.4509 | 35.8805 | 149.6856 | 24.4416 | 157.6449 | 21.5992 | 18.4358 | 15.5341
163.3167 | 103.1458 | 36.0294 | 149.7076 | 24.4543 | 158.5869 | 21.6919 | 18.5537 | 15.6089
164.3167 | 103.593 | 36.1798 | 149.231 | 24.4548 | 158.7347 | 21.7853 | 18.664 | 15.7311
165.3167 | 103.8468 | 36.3136 | 149.4683 | 24.4601 | 159.0387 | 21.9308 | 18.7708 | 15.8036
166.3167 | 104.0072 | 36.4397 | 149.0498 | 24.4573 | 158.4903 | 22.037 | 18.874 | 15.8496
167.3167 | 104.3604 | 36.571 | 149.1591 | 24.465 | 158.0018 | 22.1222 | 19.0322 | 15.9543
168.3167 | 104.6952 | 36.7174 | 148.9525 | 24.4739 | 157.8817 | 22.2512 | 19.1193 | 16.0287
169.3167 | 104.8672 | 36.8576 | 149.6732 | 24.4628 | 158.8836 | 22.3222 | 19.2255 | 16.1315
170.3167 | 105.2411 | 36.9791 | 151.6703 | 24.4796 | 160.3424 | 22.4483 | 19.3334 | 16.228
171.3167 | 105.7399 | 37.1221 | 152.1106 | 24.4907 | 161.103 | 22.5818 | 19.5163 | 16.3384
172.3167 | 106.205 | 37.251 | 151.8589 | 24.4923 | 161.7002 | 22.659 | 19.6163 | 16.3822
173.3167 | 106.1888 | 37.397 | 151.4224 | 24.4949 | 160.9819 | 22.8216 | 19.7264 | 16.4864
174.3167 | 106.765 | 37.5255 | 150.7944 | 24.5092 | 160.409 | 22.8794 | 19.8415 | 16.5965
175.3167 | 107.3577 | 37.6596 | 150.4195 | 24.4981 | 159.5741 | 22.9815 | 19.9507 | 16.6707
176.3167 | 107.5781 | 37.788 | 151.3239 | 24.5136 | 159.7595 | 23.123 | 20.0901 | 16.7695
177.3167 | 107.0678 | 37.9132 | 151.6757 | 24.5088 | 160.3328 | 23.2177 | 20.1837 | 16.8321
178.3167 | 107.6716 | 38.0179 | 151.5061 | 24.5247 | 161.3175 | 23.2848 | 20.3353 | 16.9905
179.3167 | 108.0933 | 38.1506 | 151.3681 | 24.5308 | 162.6038 | 23.4314 | 20.4263 | 17.0394
180.3167 | 108.4628 | 38.2646 | 151.4933 | 24.5689 | 162.592 | 23.5207 | 20.561 | 17.1394
181.3167 | 108.6474 | 38.3859 | 151.8829 | 24.5923 | 163.6584 | 23.6489 | 20.7179 | 17.2257
182.3167 | 108.5775 | 38.4933 | 152.2983 | 24.6351 | 164.2286 | 23.7809 | 20.8327 | 17.2859
183.3167 | 108.9362 | 38.6126 | 151.8152 | 24.7085 | 165.0102 | 23.8666 | 20.9424 | 17.4052
184.3167 | 109.2106 | 38.7164 | 151.8776 | 24.822 | 165.2773 | 24.0052 | 21.0744 | 17.5089
185.3167 | 110.1006 | 38.838 | 151.8411 | 24.8705 | 165.8031 | 24.1077 | 21.1691 | 17.5867
186.3167 | 109.9436 | 38.9756 | 151.9192 | 24.933 | 166.2106 | 24.201 | 21.303 | 17.6932
187.3167 | 109.4688 | 39.103 | 152.2509 | 24.9596 | 166.8092 | 24.3139 | 21.4352 | 17.7969
188.3167 | 109.0635 | 39.2438 | 152.1544 | 25.0352 | 167.024 | 24.381 | 21.5585 | 17.8823
189.3167 | 108.592 | 39.359 | 151.8719 | 25.1625 | 166.957 | 24.5403 | 21.65 | 17.9631
190.3167 | 109.0738 | 39.5076 | 152.0028 | 25.3717 | 166.7647 | 24.6262 | 21.8254 | 18.0819
191.3167 | 108.9093 | 39.6219 | 152.2902 | 25.5409 | 166.9989 | 24.6988 | 21.9193 | 18.1711
192.3167 | 109.5704 | 39.7554 | 151.8424 | 25.8498 | 167.2196 | 24.8356 | 22.0312 | 18.2773
193.3167 | 109.2715 | 39.8913 | 152.0598 | 26.0399 | 167.2923 | 24.9413 | 22.1983 | 18.3781
194.3167 | 109.8703 | 40.0062 | 152.147 | 26.6176 | 166.8874 | 25.0109 | 22.2779 | 18.4546
195.3167 | 109.9615 | 40.1324 | 151.8215 | 26.9315 | 167.3389 | 25.111 | 22.4482 | 18.5486
196.3167 | 110.0535 | 40.2737 | 152.7273 | 27.1881 | 167.1895 | 25.26 | 22.5384 | 18.6626
197.3167 | 110.8075 | 40.4085 | 153.0367 | 28.0791 | 167.9814 | 25.3783 | 22.6867 | 18.7578
198.3167 | 111.2742 | 40.5338 | 153.3601 | 27.9452 | 168.0705 | 25.4779 | 22.8011 | 18.844
199.3167 | 111.6681 | 40.6791 | 154.3173 | 28.267 | 168.3285 | 25.5806 | 22.9218 | 18.9668
200.3167 | 112.375 | 40.7968 | 155.427 | 28.8768 | 168.4431 | 25.6836 | 23.0976 | 19.0833
201.3167 | 112.5528 | 40.946 | 158.11 | 29.646 | 169.0192 | 25.8234 | 23.1904 | 19.1521
202.3167 | 113.1026 | 41.0789 | 158.0556 | 30.9035 | 169.5808 | 25.9088 | 23.3123 | 19.2454
203.3167 | 113.6655 | 41.2098 | 157.9143 | 32.2288 | 169.6807 | 25.9873 | 23.4485 | 19.3842
204.3167 | 113.8839 | 41.352 | 157.8894 | 44.5193 | 170.5227 | 26.1036 | 23.591 | 19.4526
205.3167 | 113.9434 | 41.4853 | 158.3838 | 148.9101 | 170.2406 | 26.2123 | 23.7462 | 19.599
206.3167 | 114.2882 | 41.6223 | 159.6914 | 180.9841 | 170.9918 | 26.3019 | 23.842 | 19.7164
207.3167 | 114.4139 | 41.7629 | 161.6897 | 182.3466 | 172.0729 | 26.4272 | 23.993 | 19.7848
208.3167 | 114.8654 | 41.8942 | 163.5571 | 184.3577 | 173.3676 | 26.547 | 24.1171 | 19.8799
209.3167 | 115.2882 | 42.0248 | 163.7523 | 184.5883 | 173.5022 | 26.6641 | 24.2286 | 19.9698
210.3167 | 115.877 | 42.1348 | 164.5159 | 184.9801 | 174.7242 | 26.7844 | 24.3632 | 20.1141
211.3167 | 116.2623 | 42.2729 | 165.0495 | 185.2751 | 175.8486 | 26.8933 | 24.4939 | 20.238
212.3167 | 116.1196 | 42.4371 | 165.2512 | 185.248 | 176.2232 | 26.9811 | 24.639 | 20.3407
213.3167 | 116.249 | 42.5832 | 166.261 | 184.8791 | 176.5722 | 27.1212 | 24.7813 | 20.4299
214.3167 | 117.0699 | 42.712 | 166.8055 | 185.5121 | 178.2157 | 27.2483 | 24.8896 | 20.5253
215.3167 | 116.8316 | 42.8698 | 166.5909 | 185.9547 | 179.0304 | 27.3223 | 25.056 | 20.6661
216.3167 | 117.4678 | 43.0019 | 167.1153 | 186.0653 | 179.8978 | 27.4631 | 25.1511 | 20.7355
217.3167 | 118.5417 | 43.128 | 167.251 | 186.9248 | 180.6931 | 27.5361 | 25.2971 | 20.8642
218.3167 | 119.7608 | 43.28 | 167.1255 | 187.8061 | 181.0284 | 27.6612 | 25.4391 | 20.9536
219.3167 | 120.7109 | 43.4249 | 167.3961 | 188.406 | 181.6077 | 27.774 | 25.5697 | 21.0536
220.3167 | 121.4551 | 43.5784 | 167.0982 | 189.1754 | 182.3833 | 27.9055 | 25.7046 | 21.1553
221.3167 | 122.5446 | 43.7121 | 166.7512 | 190.0198 | 182.0758 | 28.0237 | 25.8824 | 21.2681
222.3167 | 123.0704 | 43.8704 | 166.4751 | 190.5227 | 181.9928 | 28.1236 | 25.9864 | 21.4004
223.3167 | 124.0431 | 44.0333 | 166.036 | 190.7013 | 182.26 | 28.2365 | 26.1095 | 21.5105
224.3167 | 125.267 | 44.1829 | 166.0746 | 191.1399 | 182.492 | 28.3643 | 26.2444 | 21.621
225.3167 | 126.4618 | 44.348 | 166.1808 | 191.2189 | 182.4354 | 28.4512 | 26.361 | 21.7177
226.3167 | 127.6 | 44.4828 | 166.1424 | 191.9869 | 183.2399 | 28.5781 | 26.5239 | 21.8165
227.3167 | 128.6136 | 44.6502 | 165.6004 | 191.9251 | 183.8271 | 28.7036 | 26.6519 | 21.9346
228.3167 | 130.0295 | 44.81 | 165.3382 | 192.1412 | 183.8947 | 28.8195 | 26.7997 | 22.0626
229.3167 | 130.9397 | 44.9741 | 165.2702 | 191.8789 | 184.0744 | 28.9286 | 26.9189 | 22.1666
230.3167 | 131.7762 | 45.1251 | 165.4003 | 190.9065 | 184.6009 | 29.0433 | 27.0453 | 22.2535
231.3167 | 132.21 | 45.2655 | 165.1849 | 190.4106 | 184.4058 | 29.1488 | 27.1864 | 22.3677
232.3167 | 133.2238 | 45.4087 | 164.7571 | 191.5581 | 184.7105 | 29.2631 | 27.3359 | 22.4959
233.3167 | 134.0992 | 45.5946 | 164.8919 | 191.3037 | 184.7257 | 29.3697 | 27.4796 | 22.6339
234.3167 | 135.04 | 45.747 | 165.2594 | 191.965 | 184.3897 | 29.4898 | 27.628 | 22.6993
235.3167 | 135.9993 | 45.9312 | 165.5287 | 192.5024 | 185.0871 | 29.6289 | 27.7419 | 22.803
236.3167 | 136.9439 | 46.1075 | 166.5295 | 193.4171 | 186.6879 | 29.7009 | 27.8875 | 22.961
237.3167 | 137.7841 | 46.2754 | 167.8085 | 194.2956 | 189.9977 | 29.7939 | 28.0132 | 23.1182
238.3167 | 138.9304 | 46.4158 | 167.8734 | 195.3351 | 191.8513 | 29.9301 | 28.192 | 23.1962
239.3167 | 139.9332 | 46.5784 | 168.3384 | 196.6 | 192.6463 | 30.0665 | 28.3385 | 23.297
240.3167 | 140.9218 | 46.7487 | 168.194 | 197.2561 | 192.7834 | 30.1908 | 28.4951 | 23.4415
241.3167 | 141.6965 | 46.8925 | 167.7686 | 197.5829 | 192.8599 | 30.2356 | 28.6087 | 23.5751
242.3167 | 141.9734 | 47.0759 | 168.5254 | 198.3023 | 193.7064 | 30.3855 | 28.7708 | 23.6604
243.3167 | 141.934 | 47.2392 | 170.5839 | 199.8501 | 194.3373 | 30.4942 | 28.8779 | 23.7961
244.3167 | 141.7283 | 47.4065 | 172.7324 | 201.5413 | 195.8308 | 30.601 | 29.0323 | 23.8773
245.3167 | 141.6703 | 47.5773 | 173.6529 | 202.5497 | 196.6958 | 30.7445 | 29.2109 | 24.0499
246.3167 | 141.3396 | 47.7542 | 173.856 | 203.2342 | 196.4327 | 30.8782 | 29.3423 | 24.1386
247.3167 | 141.6949 | 47.895 | 174.0914 | 203.6575 | 195.6992 | 30.9943 | 29.5012 | 24.2672
248.3167 | 142.002 | 48.0632 | 174.4179 | 204.1177 | 195.6641 | 31.1135 | 29.6334 | 24.3778
249.3167 | 142.8519 | 48.2233 | 173.9593 | 203.961 | 194.5795 | 31.2302 | 29.7835 | 24.4983
250.3167 | 143.4025 | 48.3509 | 174.2135 | 204.1159 | 194.2374 | 31.3305 | 29.9397 | 24.6174
251.3167 | 144.6278 | 48.5331 | 175.0985 | 205.435 | 195.2992 | 31.4289 | 30.087 | 24.7254
252.3167 | 146.3041 | 48.6596 | 175.7787 | 206.2171 | 196.3983 | 31.5558 | 30.2415 | 24.8407
253.3167 | 146.5484 | 48.8685 | 177.0596 | 207.87 | 197.1861 | 31.6619 | 30.3664 | 24.9808
254.3167 | 147.3634 | 49.0209 | 177.6215 | 209.0891 | 197.3783 | 31.8077 | 30.5277 | 25.0987
255.3167 | 147.5188 | 49.2037 | 178.7189 | 211.3846 | 198.7159 | 31.903 | 30.6782 | 25.2203
256.3167 | 147.8638 | 49.3707 | 180.2884 | 212.633 | 198.7515 | 32.0584 | 30.8299 | 25.338
257.3167 | 147.8988 | 49.5566 | 181.4342 | 212.8967 | 199.3785 | 32.1503 | 30.9704 | 25.443
258.3167 | 148.6597 | 49.7361 | 180.955 | 212.7955 | 199.2918 | 32.2696 | 31.147 | 25.5875
259.3167 | 148.881 | 49.9079 | 181.1854 | 212.8247 | 199.3163 | 32.4 | 31.2708 | 25.6982
260.3167 | 149.6115 | 50.1158 | 180.829 | 213.1199 | 199.5138 | 32.5256 | 31.4443 | 25.8314
261.3167 | 149.6385 | 50.2993 | 181.1437 | 213.8914 | 201.4405 | 32.6417 | 31.5763 | 25.9636
262.3167 | 150.6533 | 50.4862 | 182.1525 | 214.4313 | 202.0079 | 32.7722 | 31.7035 | 26.0834
263.3167 | 151.7214 | 50.6779 | 181.7907 | 214.4742 | 201.5029 | 32.9145 | 31.8582 | 26.206
264.3167 | 152.1423 | 50.8686 | 181.6459 | 214.8346 | 201.7399 | 33.0165 | 32.0299 | 26.3333
265.3167 | 152.8029 | 51.0579 | 182.1673 | 214.9634 | 201.4733 | 33.1369 | 32.1554 | 26.4431
266.3167 | 153.4297 | 51.2507 | 183.0382 | 215.3409 | 201.7 | 33.2678 | 32.3349 | 26.5904
267.3167 | 153.731 | 51.4383 | 182.8682 | 215.3407 | 201.4248 | 33.3651 | 32.4774 | 26.7094
268.3167 | 153.3014 | 51.6498 | 182.6434 | 216.2127 | 201.5584 | 33.4839 | 32.6217 | 26.8221
269.3167 | 152.9507 | 51.8345 | 182.9764 | 216.4798 | 203.6069 | 33.6113 | 32.786 | 26.9648
270.3167 | 153.6557 | 52.0215 | 183.2498 | 217.3722 | 205.331 | 33.7433 | 32.9401 | 27.1086
271.3167 | 153.8288 | 52.2149 | 183.0352 | 217.9369 | 204.6813 | 33.9093 | 33.081 | 27.208
272.3167 | 154.1839 | 52.4207 | 184.874 | 219.0254 | 204.7602 | 33.9843 | 33.2531 | 27.3555
273.3167 | 154.4949 | 52.6256 | 187.4075 | 220.1649 | 204.8262 | 34.1403 | 33.4031 | 27.4568
274.3167 | 154.2113 | 52.8053 | 189.3997 | 221.1098 | 205.7931 | 34.2428 | 33.5555 | 27.6024
275.3167 | 154.5009 | 53.0092 | 190.4477 | 221.7045 | 206.3531 | 34.3779 | 33.712 | 27.7251
276.3167 | 153.9088 | 53.1855 | 191.1994 | 222.6775 | 206.9749 | 34.4952 | 33.8808 | 27.8618
277.3167 | 153.7497 | 53.3999 | 190.8443 | 222.9914 | 207.8321 | 34.6224 | 34.0621 | 27.9986
278.3167 | 153.759 | 53.593 | 190.7455 | 223.0654 | 208.1963 | 34.7516 | 34.1969 | 28.1313
279.3167 | 154.3661 | 53.7821 | 192.6294 | 224.5297 | 207.9403 | 34.8651 | 34.3498 | 28.2614
280.3167 | 154.909 | 54.0079 | 194.5844 | 225.9029 | 210.2134 | 34.9873 | 34.5007 | 28.3969
281.3167 | 155.6823 | 54.2048 | 195.3839 | 227.4449 | 211.2395 | 35.1242 | 34.7013 | 28.5267
282.3167 | 156.6591 | 54.3635 | 196.2929 | 228.2882 | 211.9922 | 35.2367 | 34.8355 | 28.6901
283.3167 | 157.6543 | 54.5711 | 196.2316 | 229.6324 | 212.1096 | 35.3752 | 34.9982 | 28.7913
284.3167 | 158.4328 | 54.7982 | 196.2244 | 230.0831 | 214.5037 | 35.505 | 35.1378 | 28.9126
285.3167 | 158.7669 | 55.006 | 196.4916 | 231.1155 | 215.0473 | 35.6251 | 35.3172 | 29.0509
286.3167 | 159.5205 | 55.2176 | 196.2537 | 231.4946 | 216.2327 | 35.7801 | 35.4844 | 29.219
287.3167 | 159.6571 | 55.4123 | 196.2813 | 232.3538 | 215.6136 | 35.8995 | 35.6408 | 29.3397
288.3167 | 160.1234 | 55.6374 | 196.5137 | 232.9069 | 216.4326 | 36.0257 | 35.8167 | 29.4843
289.3167 | 160.0607 | 55.8411 | 197.5401 | 234.0982 | 218.542 | 36.1537 | 35.9599 | 29.6218
290.3167 | 161.5857 | 56.0395 | 197.4205 | 233.9933 | 218.4808 | 36.3008 | 36.1093 | 29.7569
291.3167 | 162.2876 | 56.2275 | 197.8983 | 233.6737 | 218.7448 | 36.4322 | 36.2778 | 29.8532
292.3167 | 161.8783 | 56.41 | 198.3092 | 233.7604 | 218.0491 | 36.5648 | 36.4597 | 29.9979
293.3167 | 162.1286 | 56.6433 | 198.5691 | 234.0713 | 218.7285 | 36.7198 | 36.6179 | 30.1421
294.3167 | 162.6399 | 56.839 | 199.2935 | 234.0004 | 218.4018 | 36.8443 | 36.8028 | 30.2862
295.3167 | 163.1098 | 57.0016 | 200.7548 | 234.919 | 219.7201 | 36.9777 | 36.9412 | 30.4308
296.3167 | 163.4828 | 57.2012 | 201.4679 | 235.5555 | 221.0527 | 37.1179 | 37.1301 | 30.5676
297.3167 | 164.2538 | 57.3997 | 201.7083 | 235.5142 | 222.784 | 37.2433 | 37.3056 | 30.7019
298.3167 | 164.4619 | 57.5676 | 203.3598 | 236.7929 | 223.9085 | 37.3875 | 37.4506 | 30.8392
299.3167 | 164.2649 | 57.81 | 206.1512 | 238.7487 | 225.9424 | 37.5254 | 37.6499 | 30.9544
300.3167 | 164.2024 | 57.9988 | 207.4309 | 239.8249 | 227.216 | 37.68 | 37.8103 | 31.114
301.3167 | 164.8188 | 58.1718 | 206.8036 | 240.2188 | 228.4902 | 37.7983 | 37.999 | 31.2432
302.3167 | 165.3232 | 58.3868 | 206.2114 | 240.4931 | 228.8934 | 37.9144 | 38.1557 | 31.3826
303.3167 | 165.7139 | 58.5954 | 208.7521 | 241.6326 | 229.5449 | 38.0805 | 38.3256 | 31.5428
304.3167 | 165.8899 | 58.7923 | 209.3424 | 243.1659 | 230.806 | 38.2144 | 38.4799 | 31.6661
305.3167 | 166.2 | 58.9868 | 209.0796 | 243.937 | 230.5854 | 38.3646 | 38.6593 | 31.7667
306.3167 | 166.2603 | 59.1649 | 208.416 | 243.5056 | 230.1289 | 38.5105 | 38.8279 | 31.934
307.3167 | 166.4646 | 59.3698 | 207.465 | 242.573 | 229.1004 | 38.636 | 38.9958 | 32.0814
308.3167 | 166.0121 | 59.5625 | 208.3716 | 243.0855 | 230.2366 | 38.808 | 39.1395 | 32.2214
309.3167 | 166.0819 | 59.7594 | 208.5002 | 242.0614 | 230.8827 | 38.9687 | 39.3187 | 32.3505
310.3167 | 166.7923 | 59.9389 | 209.9493 | 244.098 | 233.524 | 39.0787 | 39.5327 | 32.5374
311.3167 | 167.5464 | 60.1227 | 211.309 | 244.1723 | 235.892 | 39.244 | 39.6765 | 32.6981
312.3167 | 169.8077 | 60.3102 | 212.0011 | 244.4268 | 237.8664 | 39.4108 | 39.8758 | 32.8352
313.3167 | 171.229 | 60.4955 | 212.6584 | 245.1269 | 238.4379 | 39.5544 | 40.0378 | 32.9775
314.3167 | 171.9605 | 60.6673 | 215.0549 | 247.5278 | 240.0567 | 39.7071 | 40.233 | 33.1321
315.3167 | 175.0875 | 60.8674 | 215.8565 | 248.6762 | 239.6574 | 39.8659 | 40.4522 | 33.2649
316.3167 | 175.1344 | 61.0428 | 215.4466 | 248.2084 | 239.2902 | 40.0118 | 40.6149 | 33.3919
317.3167 | 176.3315 | 61.2146 | 214.5891 | 248.1289 | 239.6232 | 40.145 | 40.7795 | 33.5613
318.3167 | 177.1987 | 61.3853 | 214.6979 | 247.8907 | 238.8506 | 40.3024 | 40.9824 | 33.7124
319.3167 | 178.0844 | 61.5538 | 213.7869 | 247.9695 | 239.6543 | 40.4592 | 41.1129 | 33.8566
320.3167 | 179.0672 | 61.6787 | 213.8918 | 248.4303 | 238.6505 | 40.6086 | 41.33 | 33.9935
321.3167 | 179.5501 | 61.8556 | 213.3095 | 248.6026 | 240.1034 | 40.7686 | 41.48 | 34.1453
322.3167 | 179.4921 | 62.0441 | 212.6131 | 247.5027 | 240.1729 | 40.9414 | 41.6828 | 34.2815
323.3167 | 179.4886 | 62.2509 | 212.4239 | 247.0107 | 238.8816 | 41.11 | 41.8381 | 34.4371
324.3167 | 178.7667 | 62.4331 | 212.0371 | 246.7135 | 237.4353 | 41.2532 | 42.0229 | 34.58
325.3167 | 178.3269 | 62.6069 | 211.5588 | 246.1073 | 235.7909 | 41.4169 | 42.1999 | 34.7349
326.3167 | 177.7379 | 62.7729 | 211.9554 | 246.9224 | 235.9088 | 41.5599 | 42.3602 | 34.8655
327.3167 | 177.5958 | 62.9528 | 212.5304 | 247.1729 | 235.0937 | 41.725 | 42.541 | 35.0299
328.3167 | 177.4282 | 63.1151 | 213.3427 | 248.1768 | 234.1541 | 41.8819 | 42.7307 | 35.1653
329.3167 | 176.996 | 63.2637 | 213.8749 | 248.5152 | 234.6593 | 42.0268 | 42.9003 | 35.353
330.3167 | 178.2107 | 63.4151 | 213.0794 | 248.1524 | 234.0807 | 42.1743 | 43.0745 | 35.4794
331.3167 | 179.2631 | 63.577 | 212.43 | 247.9794 | 234.2845 | 42.3374 | 43.2933 | 35.6196
332.3167 | 179.9509 | 63.7267 | 213.3385 | 248.1382 | 233.2851 | 42.482 | 43.4581 | 35.7828
333.3167 | 180.6931 | 63.9007 | 213.737 | 248.7232 | 232.6412 | 42.6407 | 43.6582 | 35.9573
334.3167 | 180.9528 | 64.0535 | 213.6994 | 249.1224 | 233.5813 | 42.7924 | 43.8024 | 36.1019
335.3167 | 181.0685 | 64.2238 | 214.9072 | 249.331 | 233.6159 | 42.9374 | 43.9866 | 36.2363
336.3167 | 180.9236 | 64.3998 | 214.5262 | 249.3757 | 233.894 | 43.0933 | 44.1687 | 36.4041
337.3167 | 181.6341 | 64.5586 | 214.2963 | 249.7975 | 234.6767 | 43.2342 | 44.37 | 36.5758
338.3167 | 182.4866 | 64.7129 | 214.0561 | 250.2159 | 235.3542 | 43.3957 | 44.5242 | 36.7327
339.3167 | 181.7831 | 64.881 | 214.3656 | 250.536 | 236.078 | 43.5378 | 44.7016 | 36.8742
340.3167 | 181.4356 | 65.0473 | 215.283 | 250.5028 | 235.8554 | 43.7042 | 44.9074 | 37.0185
341.3167 | 180.9814 | 65.2093 | 216.4719 | 251.4408 | 236.2872 | 43.836 | 45.0984 | 37.1873
342.3167 | 181.3717 | 65.3907 | 216.9273 | 251.889 | 235.5141 | 43.9962 | 45.265 | 37.3489
343.3167 | 182.059 | 65.5483 | 219.1194 | 252.7386 | 234.8216 | 44.1526 | 45.4408 | 37.487
344.3167 | 181.847 | 65.7102 | 220.5567 | 254.6743 | 234.6416 | 44.3131 | 45.6352 | 37.6623
345.3167 | 182.5453 | 65.8758 | 221.2301 | 256.1751 | 235.5123 | 44.4788 | 45.8142 | 37.811
346.3167 | 182.9682 | 66.0442 | 221.9506 | 257.2552 | 235.2586 | 44.6252 | 46.0028 | 37.9849
347.3167 | 183.0069 | 66.1972 | 221.758 | 256.1256 | 234.8621 | 44.7885 | 46.185 | 38.1267
348.3167 | 183.5968 | 66.3814 | 220.3359 | 255.6103 | 234.3728 | 44.9317 | 46.365 | 38.2735
349.3167 | 183.5048 | 66.552 | 219.5181 | 255.8744 | 233.3364 | 45.0837 | 46.5383 | 38.4174
350.3167 | 183.3649 | 66.7221 | 219.7628 | 255.8642 | 232.3775 | 45.2395 | 46.7399 | 38.5848
351.3167 | 183.9991 | 66.8932 | 220.6553 | 256.2841 | 233.2599 | 45.4076 | 46.9049 | 38.7433
352.3167 | 183.9702 | 67.0364 | 221.8501 | 256.9292 | 233.7478 | 45.538 | 47.1027 | 38.9078
353.3167 | 185.2113 | 67.1797 | 222.2055 | 256.9839 | 234.1146 | 45.6991 | 47.2728 | 39.0559
354.3167 | 186.2417 | 67.3777 | 222.6191 | 257.9322 | 233.8193 | 45.8515 | 47.4704 | 39.2208
355.3167 | 187.3117 | 67.5008 | 222.7261 | 259.2924 | 235.0379 | 45.9926 | 47.646 | 39.3958
356.3167 | 187.98 | 67.7106 | 224.3718 | 260.363 | 236.4425 | 46.1571 | 47.8195 | 39.5503
357.3167 | 186.77 | 67.9031 | 225.4828 | 261.2857 | 236.4582 | 46.3266 | 48.0201 | 39.7119
358.3167 | 186.9404 | 68.0756 | 225.57 | 260.9114 | 235.8291 | 46.4669 | 48.2256 | 39.8594
359.3167 | 187.2186 | 68.268 | 226.2738 | 260.6569 | 235.1044 | 46.6323 | 48.4002 | 40.0344
360.3167 | 188.1653 | 68.4446 | 227.2195 | 261.2393 | 233.8928 | 46.8101 | 48.575 | 40.1831
361.3167 | 187.7246 | 68.6254 | 227.9633 | 261.7849 | 233.0106 | 46.9677 | 48.7855 | 40.3283
362.3167 | 187.8974 | 68.8128 | 227.9666 | 261.6106 | 234.3894 | 47.1185 | 48.9724 | 40.5114
363.3167 | 188.0402 | 68.992 | 228.8412 | 262.4769 | 234.871 | 47.2664 | 49.1502 | 40.6678
364.3167 | 187.7261 | 69.1665 | 231.1006 | 264.0396 | 237.2476 | 47.4331 | 49.3321 | 40.8301
365.3167 | 187.1133 | 69.3581 | 232.1449 | 264.8539 | 237.6237 | 47.6134 | 49.5328 | 40.9938
366.3167 | 187.6317 | 69.5324 | 233.6254 | 265.2206 | 237.7098 | 47.7676 | 49.7091 | 41.1552
367.3167 | 188.4773 | 69.7329 | 232.0302 | 265.224 | 240.0335 | 47.9162 | 49.9126 | 41.2841
368.3167 | 189.3153 | 69.9269 | 232.5073 | 266.7903 | 242.1837 | 48.0784 | 50.0877 | 41.4884
369.3167 | 189.6807 | 70.1298 | 235.1444 | 269.4037 | 242.8133 | 48.2585 | 50.3032 | 41.6646
370.3167 | 189.1025 | 70.3108 | 235.1407 | 269.016 | 243.0778 | 48.4296 | 50.4848 | 41.791
371.3167 | 189.5678 | 70.5054 | 233.3714 | 268.6511 | 242.3257 | 48.5978 | 50.6777 | 41.9548
372.3167 | 190.4898 | 70.712 | 232.3604 | 268.0814 | 243.0008 | 48.7466 | 50.8563 | 42.1131
373.3167 | 190.4241 | 70.8935 | 231.6446 | 267.8788 | 244.7135 | 48.9332 | 51.0486 | 42.2526
374.3167 | 191.4843 | 71.0962 | 231.7109 | 268.9564 | 246.8782 | 49.0904 | 51.2331 | 42.4527
375.3167 | 191.6044 | 71.301 | 231.1037 | 269.2722 | 248.7098 | 49.2569 | 51.4324 | 42.5978
376.3167 | 190.856 | 71.4967 | 231.5014 | 270.0141 | 248.9309 | 49.4238 | 51.6486 | 42.7677
377.3167 | 191.6727 | 71.6472 | 231.9845 | 270.5634 | 248.7805 | 49.6078 | 51.8264 | 42.9152
378.3167 | 192.2962 | 71.8586 | 233.2761 | 269.76 | 249.5201 | 49.7716 | 52.0154 | 43.0929
379.3167 | 192.9098 | 72.0762 | 232.1319 | 268.9361 | 250.2588 | 49.9489 | 52.2049 | 43.2232
380.3167 | 194.5064 | 72.2651 | 232.3575 | 269.6651 | 249.5182 | 50.1045 | 52.3963 | 43.3866
381.3167 | 194.7089 | 72.431 | 232.0041 | 270.1115 | 249.7369 | 50.2644 | 52.5842 | 43.5675
382.3167 | 195.751 | 72.6554 | 232.7199 | 271.7257 | 250.9896 | 50.4335 | 52.8036 | 43.7238
383.3167 | 196.8297 | 72.8623 | 231.3702 | 272.3823 | 250.2749 | 50.6135 | 52.97 | 43.8822
384.3167 | 197.8937 | 73.0441 | 231.8467 | 272.4937 | 250.4109 | 50.7852 | 53.1674 | 44.04
385.3167 | 199 | 73.2198 | 231.2295 | 272.9955 | 249.9486 | 50.9538 | 53.3882 | 44.1966
386.3167 | 198.8628 | 73.4343 | 232.7124 | 272.9006 | 249.8207 | 51.1185 | 53.5689 | 44.3749
387.3167 | 199.4389 | 73.6141 | 231.8811 | 272.8554 | 249.7523 | 51.3103 | 53.737 | 44.5212
388.3167 | 199.9383 | 73.8075 | 232.0864 | 272.5869 | 249.4504 | 51.4687 | 53.9559 | 44.6918
389.3167 | 200.4683 | 74.0137 | 231.7146 | 272.5317 | 249.0176 | 51.6394 | 54.1337 | 44.8335
390.3167 | 200.8592 | 74.2127 | 232.017 | 271.8347 | 248.6082 | 51.8089 | 54.3699 | 45.0117
391.3167 | 200.6358 | 74.401 | 233.4095 | 271.7358 | 248.241 | 51.9903 | 54.5311 | 45.1597
392.3167 | 200.6333 | 74.5985 | 234.7224 | 271.7892 | 247.7005 | 52.1562 | 54.7328 | 45.3171
393.3167 | 200.351 | 74.7788 | 235.6139 | 272.8615 | 248.5518 | 52.3471 | 54.9325 | 45.4714
394.3167 | 200.7654 | 74.9558 | 236.1232 | 273.6688 | 249.2389 | 52.511 | 55.1339 | 45.6533
395.3167 | 201.4974 | 75.1476 | 236.1455 | 274.283 | 249.6467 | 52.6948 | 55.3256 | 45.7932
396.3167 | 201.315 | 75.335 | 237.6145 | 274.808 | 251.3195 | 52.8536 | 55.5173 | 45.9516
397.3167 | 201.1557 | 75.5219 | 237.9471 | 274.7475 | 252.4454 | 53.0304 | 55.692 | 46.1228
398.3167 | 201.8226 | 75.7037 | 238.0782 | 275.2197 | 251.7868 | 53.2067 | 55.9195 | 46.2866
399.3167 | 201.7149 | 75.8459 | 238.9436 | 276.8027 | 251.2196 | 53.3634 | 56.121 | 46.4586
400.3167 | 202.262 | 76.0271 | 240.1863 | 278.2989 | 251.3067 | 53.5361 | 56.3087 | 46.633
401.3167 | 202.3585 | 76.2273 | 241.5882 | 280.5451 | 250.9181 | 53.7181 | 56.4862 | 46.7909
402.3167 | 202.7212 | 76.4102 | 242.2687 | 281.4845 | 250.8108 | 53.878 | 56.7084 | 46.9453
403.3167 | 202.7643 | 76.5724 | 245.3198 | 282.5499 | 251.5209 | 54.07 | 56.9108 | 47.1204
404.3167 | 203.2926 | 76.774 | 245.4733 | 282.0972 | 253.3983 | 54.2566 | 57.1085 | 47.288
405.3167 | 203.1304 | 76.9439 | 246.2514 | 282.1389 | 254.555 | 54.4423 | 57.2885 | 47.4419
406.3167 | 202.9855 | 77.1474 | 247.6449 | 283.0469 | 254.223 | 54.5955 | 57.4962 | 47.6132
407.3167 | 202.5186 | 77.3258 | 247.7213 | 283.998 | 253.5164 | 54.7846 | 57.6987 | 47.7833
408.3167 | 203.1364 | 77.5286 | 247.2169 | 283.9179 | 254.6266 | 54.9605 | 57.9032 | 47.9372
409.3167 | 203.8824 | 77.7213 | 247.7146 | 283.9354 | 254.2372 | 55.1286 | 58.0925 | 48.098
410.3167 | 203.9067 | 77.9205 | 247.6486 | 283.1806 | 253.8642 | 55.315 | 58.3069 | 48.2855
411.3167 | 204.4798 | 78.1018 | 247.9915 | 284.0485 | 255.2026 | 55.4862 | 58.4795 | 48.4364
412.3167 | 205.4211 | 78.2909 | 246.4752 | 284.2294 | 256.4175 | 55.6809 | 58.691 | 48.6014
413.3167 | 205.544 | 78.5254 | 245.7171 | 284.2829 | 257.0866 | 55.8548 | 58.8879 | 48.7744
414.3167 | 206.3038 | 78.7157 | 245.2479 | 284.8645 | 258.7004 | 56.037 | 59.0968 | 48.9798
415.3167 | 207.3992 | 78.9293 | 244.0787 | 284.3815 | 259.0819 | 56.2223 | 59.2815 | 49.1121
416.3167 | 208.094 | 79.1175 | 243.9957 | 284.4574 | 259.2949 | 56.3978 | 59.4582 | 49.2754
417.3167 | 209.3182 | 79.3254 | 243.2961 | 284.5367 | 259.1319 | 56.5795 | 59.6663 | 49.4265
418.3167 | 208.6577 | 79.5341 | 243.8654 | 285.1663 | 259.1677 | 56.7733 | 59.8757 | 49.5878
419.3167 | 209.475 | 79.7289 | 246.8257 | 285.7931 | 259.1849 | 56.9523 | 60.0709 | 49.7422
420.3167 | 210.1054 | 79.9335 | 247.4904 | 285.362 | 258.4372 | 57.155 | 60.2673 | 49.9229
421.3167 | 210.788 | 80.1228 | 247.4929 | 284.9364 | 258.1547 | 57.3404 | 60.4674 | 50.0732
422.3167 | 211.021 | 80.3281 | 246.7188 | 285.1913 | 260.1171 | 57.518 | 60.6651 | 50.2653
423.3167 | 211.7622 | 80.5429 | 248.4077 | 285.8967 | 261.127 | 57.7138 | 60.8357 | 50.4321
424.3167 | 211.6569 | 80.7162 | 248.6236 | 286.8054 | 260.532 | 57.9078 | 61.0319 | 50.5994
425.3167 | 212.0003 | 80.9582 | 250.1033 | 288.0767 | 260.5932 | 58.0922 | 61.2152 | 50.7508
426.3167 | 212.7284 | 81.1692 | 250.3594 | 288.6935 | 262.169 | 58.2865 | 61.4151 | 50.9145
427.3167 | 212.8702 | 81.3821 | 250.3046 | 288.7952 | 261.6826 | 58.4469 | 61.6315 | 51.0882
428.3167 | 212.8657 | 81.5969 | 252.0257 | 289.6227 | 262.1497 | 58.6514 | 61.8363 | 51.2445
429.3167 | 213.2552 | 81.8144 | 256.1368 | 291.2111 | 262.6754 | 58.8418 | 62.0327 | 51.4017
430.3167 | 212.9798 | 82.0514 | 257.3993 | 292.7449 | 262.7329 | 59.0456 | 62.2367 | 51.5661
431.3167 | 212.1414 | 82.2617 | 256.7116 | 292.3375 | 262.3384 | 59.2216 | 62.4166 | 51.7455
432.3167 | 212.9714 | 82.4551 | 256.4731 | 291.7121 | 261.974 | 59.4299 | 62.6198 | 51.9032
433.3167 | 212.8379 | 82.6826 | 257.5393 | 291.8402 | 261.2607 | 59.6241 | 62.8147 | 52.0644
434.3167 | 212.6751 | 82.9291 | 257.4518 | 291.7628 | 260.4708 | 59.8047 | 63.0272 | 52.2269
435.3167 | 212.5763 | 83.1538 | 256.3759 | 290.8969 | 259.95 | 59.9919 | 63.2074 | 52.4006
436.3167 | 212.2727 | 83.3783 | 255.46 | 290.1832 | 260.0271 | 60.18 | 63.445 | 52.5516
437.3167 | 212.4375 | 83.5928 | 256.1872 | 291.3189 | 259.7228 | 60.3609 | 63.6047 | 52.7247
438.3167 | 212.5724 | 83.8248 | 256.8698 | 291.4243 | 261.636 | 60.5522 | 63.8363 | 52.881
439.3167 | 212.4542 | 84.0474 | 256.5081 | 292.2336 | 263.1801 | 60.7486 | 64.0098 | 53.0587
440.3167 | 211.9588 | 84.3297 | 255.6521 | 291.7467 | 263.4806 | 60.9362 | 64.2005 | 53.2305
441.3167 | 212.264 | 84.5471 | 257.5773 | 292.715 | 262.4475 | 61.1454 | 64.4087 | 53.3968
442.3167 | 213.1352 | 84.789 | 258.6751 | 292.9374 | 262.0134 | 61.3259 | 64.6484 | 53.5311
443.3167 | 214.0455 | 85.0108 | 259.8936 | 295.1364 | 263.9313 | 61.5149 | 64.8093 | 53.7043
444.3167 | 215.1504 | 85.2288 | 259.696 | 295.3811 | 265.5314 | 61.7187 | 65.0144 | 53.8712
445.3167 | 216.2195 | 85.4871 | 259.1602 | 295.4217 | 266.6328 | 61.9162 | 65.2244 | 54.0464
446.3167 | 216.4424 | 85.7385 | 261.2347 | 298.2394 | 269.536 | 62.1143 | 65.4164 | 54.2278
447.3167 | 216.6158 | 85.9843 | 261.925 | 299.2304 | 269.9632 | 62.3018 | 65.6316 | 54.3846
448.3167 | 216.2309 | 86.2243 | 260.4336 | 300.0859 | 270.4687 | 62.4992 | 65.8421 | 54.566
449.3167 | 215.7122 | 86.4761 | 261.093 | 299.8579 | 270.1262 | 62.6984 | 66.0177 | 54.7272
450.3167 | 215.408 | 86.7251 | 262.1833 | 300.5074 | 269.4254 | 62.8931 | 66.2337 | 54.8944
451.3167 | 215.547 | 86.9692 | 261.9993 | 301.729 | 271.4065 | 63.0926 | 66.4102 | 55.0574
452.3167 | 216.4386 | 87.2487 | 261.5419 | 301.5948 | 271.689 | 63.3066 | 66.6032 | 55.2246
453.3167 | 216.7259 | 87.4686 | 263.9262 | 302.6691 | 271.4042 | 63.4837 | 66.834 | 55.3916
454.3167 | 217.1394 | 87.7421 | 266.1757 | 303.9435 | 272.1437 | 63.6914 | 67.0124 | 55.565
455.3167 | 217.1435 | 88.0116 | 266.143 | 304.2619 | 270.8972 | 63.888 | 67.1982 | 55.7326
456.3167 | 217.7738 | 88.2711 | 266.9231 | 305.3952 | 271.63 | 64.0856 | 67.4031 | 55.9019
457.3167 | 218.353 | 88.5471 | 266.4786 | 305.8844 | 272.1973 | 64.2963 | 67.6087 | 56.0509
458.3167 | 218.6692 | 88.8108 | 265.472 | 305.2249 | 271.8505 | 64.4867 | 67.8272 | 56.2184
459.3167 | 219.5785 | 89.0917 | 265.9261 | 304.5955 | 272.6134 | 64.6866 | 67.9984 | 56.3992
460.3167 | 220.1762 | 89.3346 | 265.2283 | 304.1454 | 273.5199 | 64.8863 | 68.1882 | 56.5363
461.3167 | 220.9028 | 89.5694 | 265.0774 | 305.4232 | 273.7446 | 65.0763 | 68.3849 | 56.7258
462.3167 | 221.2933 | 89.8643 | 264.9622 | 306.1813 | 275.9005 | 65.2717 | 68.5623 | 56.8947
463.3167 | 221.2299 | 90.151 | 268.1894 | 307.0691 | 276.7454 | 65.4794 | 68.8003 | 57.031
464.3167 | 222.0101 | 90.4029 | 266.9416 | 306.1855 | 276.9887 | 65.6649 | 68.9577 | 57.2339
465.3167 | 223.1742 | 90.6851 | 265.3064 | 306.1631 | 277.6561 | 65.8603 | 69.132 | 57.401
466.3167 | 224.1227 | 90.9604 | 265.864 | 306.7621 | 277.131 | 66.0812 | 69.3644 | 57.538
467.3167 | 225.0741 | 91.2313 | 263.7004 | 305.756 | 276.2193 | 66.278 | 69.5446 | 57.7188
468.3167 | 225.7842 | 91.4928 | 263.0426 | 305.8027 | 277.37 | 66.4756 | 69.7221 | 57.8791
469.3167 | 225.9646 | 91.7571 | 262.5085 | 305.9861 | 277.0312 | 66.6621 | 69.9324 | 58.044
470.3167 | 227.1374 | 92.0068 | 262.3175 | 305.474 | 276.3278 | 66.8515 | 70.1227 | 58.2209
471.3167 | 227.1196 | 92.2833 | 262.319 | 305.8941 | 276.3805 | 67.0746 | 70.3142 | 58.384
472.3167 | 227.4501 | 92.5465 | 262.2694 | 305.5993 | 276.1478 | 67.2713 | 70.5088 | 58.5861
473.3167 | 227.9081 | 92.8029 | 262.0049 | 306.6539 | 276.0617 | 67.4784 | 70.6822 | 58.7443
474.3167 | 228.6854 | 93.0683 | 262.6611 | 307.1214 | 274.7702 | 67.6627 | 70.8741 | 58.9247
475.3167 | 229.4482 | 93.3221 | 264.4174 | 308.8669 | 274.5115 | 67.8919 | 71.0769 | 59.0593
476.3167 | 230.2361 | 93.569 | 266.5556 | 309.9554 | 274.5948 | 68.0857 | 71.2813 | 59.2452
477.3167 | 230.673 | 93.8365 | 267.9727 | 310.7109 | 275.9709 | 68.2902 | 71.4517 | 59.4116
478.3167 | 231.3088 | 94.1287 | 270.4384 | 310.5943 | 279.2621 | 68.5072 | 71.6586 | 59.5869
479.3167 | 231.4946 | 94.3755 | 274.7579 | 313.8436 | 281.597 | 68.7049 | 71.8371 | 59.773
480.3167 | 231.1247 | 94.6641 | 276.5761 | 315.5373 | 282.2837 | 68.9292 | 72.0175 | 59.9199
481.3167 | 232.4205 | 94.9239 | 274.264 | 315.9441 | 282.9487 | 69.1361 | 72.2227 | 60.0716
482.3167 | 233.3086 | 95.18 | 274.3762 | 315.4245 | 282.969 | 69.3433 | 72.4143 | 60.2501
483.3167 | 234.1778 | 95.4581 | 274.5996 | 314.9132 | 282.8202 | 69.5432 | 72.5954 | 60.4276
484.3167 | 233.9819 | 95.7198 | 275.4897 | 314.8018 | 283.6987 | 69.7527 | 72.7807 | 60.5631
485.3167 | 235.148 | 95.9862 | 274.6051 | 314.4424 | 284.5397 | 69.9528 | 72.9784 | 60.7535
486.3167 | 237.1203 | 96.2818 | 273.7609 | 314.5923 | 284.9006 | 70.1544 | 73.1681 | 60.9181
487.3167 | 238.3223 | 96.5706 | 272.6292 | 313.6303 | 285.1595 | 70.3589 | 73.3678 | 61.0891
488.3167 | 238.8427 | 96.8103 | 271.9853 | 314.1195 | 284.3807 | 70.5433 | 73.5786 | 61.2501
489.3167 | 239.6154 | 97.0676 | 271.6115 | 313.1712 | 286.6806 | 70.7542 | 73.7717 | 61.4171
490.3167 | 240.5597 | 97.3307 | 270.5816 | 313.0884 | 286.2021 | 70.9697 | 73.9515 | 61.5876
491.3167 | 240.4883 | 97.567 | 269.1388 | 312.4079 | 284.6168 | 71.1508 | 74.1329 | 61.7694
492.3167 | 241.0824 | 97.8602 | 269.8504 | 311.2688 | 282.4859 | 71.3682 | 74.3346 | 61.9253
493.3167 | 242.1565 | 98.105 | 270.2366 | 311.3654 | 282.0222 | 71.5702 | 74.5248 | 62.0837
494.3167 | 242.2431 | 98.3667 | 269.5487 | 311.7083 | 283.1782 | 71.7921 | 74.7114 | 62.2601
495.3167 | 242.7741 | 98.6163 | 268.8895 | 310.5372 | 282.9356 | 71.9967 | 74.8945 | 62.4339
496.3167 | 241.8994 | 98.8535 | 269.1706 | 309.1204 | 281.7314 | 72.2023 | 75.0839 | 62.5788
497.3167 | 240.7889 | 99.0896 | 268.9664 | 308.6595 | 279.6882 | 72.4188 | 75.2965 | 62.7458
498.3167 | 241.1123 | 99.3333 | 270.4243 | 308.6438 | 278.2808 | 72.639 | 75.4578 | 62.9322
499.3167 | 241.2282 | 99.5669 | 274.2453 | 310.7258 | 278.8953 | 72.8482 | 75.6486 | 63.0854
500.3167 | 240.2784 | 99.7791 | 273.6739 | 311.1889 | 278.5278 | 73.0609 | 75.847 | 63.2684
501.3167 | 240.5492 | 100.0288 | 272.8528 | 311.517 | 278.9116 | 73.2576 | 76.074 | 63.4405
502.3167 | 240.9419 | 100.2476 | 273.095 | 311.9459 | 280.8461 | 73.4695 | 76.2644 | 63.619
503.3167 | 241.4593 | 100.4832 | 272.1015 | 311.8961 | 280.443 | 73.7007 | 76.4518 | 63.749
504.3167 | 242.1784 | 100.707 | 272.0602 | 312.4082 | 280.191 | 73.8983 | 76.6529 | 63.9388
505.3167 | 242.8877 | 100.9395 | 272.307 | 312.2822 | 280.7909 | 74.1072 | 76.8312 | 64.1201
506.3167 | 242.8198 | 101.1699 | 274.1021 | 311.8868 | 281.0914 | 74.3185 | 77.033 | 64.2847
507.3167 | 243.0934 | 101.3609 | 272.7112 | 313.3746 | 279.8272 | 74.5515 | 77.242 | 64.4277
508.3167 | 243.6205 | 101.5452 | 272.0291 | 312.2945 | 279.817 | 74.7527 | 77.4476 | 64.6173
509.3167 | 243.1301 | 101.7811 | 271.8353 | 312.7631 | 279.8016 | 74.9658 | 77.6392 | 64.7825
510.3167 | 242.9457 | 101.9749 | 272.7151 | 313.1662 | 279.1723 | 75.1719 | 77.8355 | 64.9534
511.3167 | 242.4921 | 102.202 | 271.6884 | 312.8704 | 279.1553 | 75.3833 | 78.0258 | 65.1286
512.3167 | 241.9756 | 102.413 | 272.9636 | 313.1594 | 279.4438 | 75.595 | 78.2317 | 65.2766
513.3167 | 242.4915 | 102.6241 | 274.3482 | 313.2061 | 278.9165 | 75.8003 | 78.4339 | 65.4661
514.3167 | 242.1849 | 102.8477 | 274.7714 | 314.0077 | 279.3189 | 76.0377 | 78.6121 | 65.6208
515.3167 | 241.583 | 103.0428 | 275.232 | 314.5375 | 280.072 | 76.2349 | 78.8257 | 65.8054
516.3167 | 242.2982 | 103.248 | 275.8168 | 314.7346 | 279.697 | 76.4375 | 79.036 | 65.9936
517.3167 | 241.961 | 103.4521 | 275.0258 | 314.1731 | 280.3539 | 76.6498 | 79.2216 | 66.1478
518.3167 | 241.1092 | 103.6641 | 274.4389 | 314.2364 | 281.9615 | 76.8541 | 79.4426 | 66.3301
519.3167 | 241.2664 | 103.8673 | 275.3876 | 314.9697 | 284.1454 | 77.0606 | 79.6179 | 66.5048
520.3167 | 241.1969 | 104.0681 | 276.8408 | 315.2594 | 285.1926 | 77.2847 | 79.8513 | 66.6738
521.3167 | 241.7019 | 104.2707 | 277.8437 | 316.2464 | 285.9635 | 77.4931 | 80.02 | 66.851
522.3167 | 241.3198 | 104.4547 | 277.5696 | 315.951 | 286.3086 | 77.6833 | 80.2043 | 67.0207
523.3167 | 241.8036 | 104.6623 | 276.7747 | 316.4785 | 287.2061 | 77.903 | 80.4162 | 67.1792
524.3167 | 242.2696 | 104.8397 | 276.0908 | 315.8025 | 286.4584 | 78.1106 | 80.6028 | 67.3557
525.3167 | 243.1208 | 105.0425 | 275.5798 | 315.6187 | 286.508 | 78.3154 | 80.8262 | 67.5247
526.3167 | 243.6255 | 105.2729 | 274.8516 | 315.0786 | 287.4228 | 78.522 | 81.0292 | 67.7236
527.3167 | 244.8009 | 105.4892 | 272.8065 | 313.7491 | 287.4965 | 78.7315 | 81.2185 | 67.8785
528.3167 | 245.5669 | 105.694 | 274.0478 | 313.8405 | 288.1687 | 78.9332 | 81.4243 | 68.0565
529.3167 | 245.9039 | 105.9014 | 275.4252 | 314.1198 | 289.2195 | 79.1765 | 81.5976 | 68.208
530.3167 | 246.2855 | 106.1153 | 275.7044 | 313.6454 | 290.185 | 79.3852 | 81.8265 | 68.3973
531.3167 | 246.3356 | 106.3022 | 274.6471 | 313.8244 | 290.0674 | 79.5866 | 81.9868 | 68.577
532.3167 | 245.5546 | 106.5182 | 273.0358 | 313.3601 | 290.4299 | 79.7989 | 82.2073 | 68.708
533.3167 | 245.6522 | 106.7239 | 273.8211 | 314.3473 | 289.4338 | 80.009 | 82.391 | 68.9072
534.3167 | 245.9404 | 106.9118 | 273.7414 | 314.1093 | 288.0405 | 80.2109 | 82.6002 | 69.0599
535.3167 | 246.1519 | 107.1388 | 272.7139 | 313.1398 | 287.3062 | 80.4261 | 82.8238 | 69.2469
536.3167 | 246.0487 | 107.3522 | 272.3685 | 312.4209 | 286.6242 | 80.6303 | 83.0014 | 69.4159
537.3167 | 246.5119 | 107.5625 | 272.4723 | 311.8757 | 285.2222 | 80.8316 | 83.2251 | 69.5821
538.3167 | 246.0954 | 107.7956 | 271.9984 | 311.7098 | 284.3509 | 81.0388 | 83.4201 | 69.7602
539.3167 | 245.4192 | 107.9904 | 272.065 | 311.9437 | 284.4898 | 81.248 | 83.6392 | 69.9163
540.3167 | 246.641 | 108.212 | 271.5295 | 312.0051 | 283.2974 | 81.4594 | 83.8317 | 70.0948
541.3167 | 246.681 | 108.4359 | 273.0835 | 311.9017 | 283.5046 | 81.6777 | 84.0564 | 70.2189
542.3167 | 246.9505 | 108.6453 | 273.47 | 312.5703 | 283.1699 | 81.8838 | 84.2322 | 70.4305
543.3167 | 248.0272 | 108.8656 | 273.4167 | 312.5842 | 282.5782 | 82.1084 | 84.4582 | 70.5799
544.3167 | 248.6394 | 109.0779 | 272.9196 | 312.9813 | 283.1274 | 82.3179 | 84.6772 | 70.7415
545.3167 | 249.229 | 109.2837 | 273.2676 | 313.3366 | 282.8044 | 82.5117 | 84.8867 | 70.929
546.3167 | 249.3467 | 109.5025 | 272.1704 | 313.0296 | 281.9049 | 82.7307 | 85.1145 | 71.078
547.3167 | 249.6013 | 109.7151 | 272.1694 | 314.2298 | 282.0046 | 82.9182 | 85.3311 | 71.2566
548.3167 | 249.4355 | 109.9342 | 273.2729 | 315.1099 | 282.4695 | 83.1169 | 85.538 | 71.4288
549.3167 | 249.6382 | 110.1377 | 273.3331 | 314.3383 | 283.333 | 83.3234 | 85.7461 | 71.6104
550.3167 | 250.2064 | 110.3547 | 273.753 | 314.2427 | 282.4612 | 83.5506 | 85.9626 | 71.7649
551.3167 | 250.7005 | 110.5778 | 275.3602 | 313.9572 | 281.5243 | 83.746 | 86.1752 | 71.9195
552.3167 | 250.5811 | 110.7786 | 275.2481 | 313.9079 | 280.132 | 83.9514 | 86.3857 | 72.0742
553.3167 | 249.554 | 110.9999 | 275.7816 | 314.1698 | 280.983 | 84.1636 | 86.6084 | 72.247
554.3167 | 249.7184 | 111.222 | 276.093 | 313.8076 | 279.4278 | 84.3726 | 86.8234 | 72.4242
555.3167 | 249.9815 | 111.4422 | 275.7451 | 314.1665 | 278.5925 | 84.5746 | 87.0402 | 72.5858
556.3167 | 249.7935 | 111.6594 | 275.8522 | 314.1105 | 278.6138 | 84.781 | 87.273 | 72.7524
557.3167 | 250.3561 | 111.8827 | 275.2695 | 313.5572 | 278.0323 | 84.9894 | 87.4609 | 72.9214
558.3167 | 250.6351 | 112.1051 | 276.5921 | 313.1188 | 278.1918 | 85.1741 | 87.6822 | 73.0944
559.3167 | 250.839 | 112.308 | 278.0454 | 314.634 | 279.1005 | 85.3826 | 87.8953 | 73.2234
560.3167 | 250.9085 | 112.52 | 278.7733 | 315.4231 | 281.1595 | 85.5872 | 88.1234 | 73.4216
561.3167 | 250.2359 | 112.7373 | 277.5772 | 315.1474 | 282.3059 | 85.8066 | 88.3393 | 73.5848
562.3167 | 250.1292 | 112.9473 | 278.9254 | 315.105 | 281.4755 | 86.0099 | 88.5447 | 73.7519
563.3167 | 250.5217 | 113.141 | 281.4794 | 316.6142 | 281.9118 | 86.2158 | 88.7589 | 73.908
564.3167 | 250.6427 | 113.3556 | 281.4066 | 316.5227 | 283.4553 | 86.4261 | 89.0042 | 74.1073
565.3167 | 251.7419 | 113.53 | 281.8784 | 317.5678 | 285.9408 | 86.6705 | 89.186 | 74.2452
566.3167 | 251.7402 | 113.7709 | 279.5868 | 316.8817 | 285.9666 | 86.8673 | 89.4212 | 74.4384
567.3167 | 252.3353 | 113.9849 | 278.7884 | 316.4549 | 286.3421 | 87.0666 | 89.6143 | 74.5814
568.3167 | 252.0803 | 114.2013 | 277.2754 | 315.4518 | 286.7925 | 87.2699 | 89.8365 | 74.7564
569.3167 | 252.3975 | 114.4008 | 277.4609 | 315.0141 | 286.1667 | 87.4748 | 90.06 | 74.936
570.3167 | 252.2589 | 114.5994 | 276.3182 | 314.2516 | 286.187 | 87.6754 | 90.2971 | 75.093
571.3167 | 252.7421 | 114.8121 | 276.5943 | 315.9975 | 287.4465 | 87.8912 | 90.5147 | 75.2568
572.3167 | 253.2407 | 115.0203 | 277.7722 | 314.8301 | 286.3633 | 88.1181 | 90.7448 | 75.4511
573.3167 | 253.4846 | 115.2197 | 278.5186 | 315.5143 | 287.0503 | 88.3217 | 90.9647 | 75.5841
574.3167 | 253.9401 | 115.4124 | 278.8799 | 315.7941 | 288.2827 | 88.528 | 91.1817 | 75.7357
575.3167 | 253.8126 | 115.612 | 278.0754 | 315.1424 | 288.5938 | 88.7351 | 91.4226 | 75.9037
576.3167 | 253.3407 | 115.8201 | 278.901 | 315.952 | 289.845 | 88.9426 | 91.6477 | 76.0659
577.3167 | 253.4901 | 115.9916 | 278.8607 | 317.5972 | 291.0542 | 89.1611 | 91.9058 | 76.2332
578.3167 | 253.9737 | 116.1979 | 278.2721 | 318.9428 | 292.5904 | 89.3624 | 92.1088 | 76.4105
579.3167 | 254.0685 | 116.3759 | 278.8144 | 320.0753 | 294.6087 | 89.5974 | 92.3768 | 76.5704
580.3167 | 254.0618 | 116.5671 | 279.4348 | 320.4153 | 295.1002 | 89.7783 | 92.5868 | 76.7789
581.3167 | 253.7408 | 116.761 | 280.9819 | 320.5533 | 294.2721 | 89.9961 | 92.8208 | 76.9357
582.3167 | 253.635 | 116.9554 | 280.8111 | 321.6008 | 294.7177 | 90.1951 | 93.0643 | 77.0845
583.3167 | 253.5208 | 117.1618 | 282.0418 | 321.1766 | 293.7797 | 90.4054 | 93.3164 | 77.2544
584.3167 | 253.6879 | 117.3448 | 282.0834 | 320.6646 | 293.399 | 90.6101 | 93.5511 | 77.4394
585.3167 | 254.7244 | 117.5366 | 282.8782 | 320.8053 | 293.273 | 90.8155 | 93.799 | 77.6149
586.3167 | 254.5642 | 117.732 | 283.9163 | 320.0556 | 292.4373 | 91.0242 | 94.0195 | 77.7788
587.3167 | 254.7138 | 117.9115 | 283.8433 | 320.5153 | 291.8492 | 91.2352 | 94.2869 | 77.9508
588.3167 | 255.6143 | 118.097 | 284.511 | 321.0333 | 291.2904 | 91.4169 | 94.5228 | 78.1324
589.3167 | 255.6824 | 118.2849 | 286.0464 | 321.87 | 291.3431 | 91.6411 | 94.7329 | 78.2845
590.3167 | 255.7306 | 118.4759 | 285.9027 | 321.4476 | 291.1472 | 91.8356 | 94.9919 | 78.4516
591.3167 | 255.7304 | 118.6496 | 285.9492 | 321.8041 | 291.1392 | 92.0198 | 95.2233 | 78.6204
592.3167 | 255.4008 | 118.8377 | 286.6149 | 321.784 | 292.4223 | 92.2106 | 95.4545 | 78.8047
593.3167 | 255.0047 | 119.0177 | 286.7071 | 322.5594 | 293.3235 | 92.3967 | 95.6996 | 78.9656
594.3167 | 254.8011 | 119.1974 | 287.5625 | 323.5263 | 294.4779 | 92.577 | 95.9098 | 79.1199
595.3167 | 255.095 | 119.38 | 288.1362 | 323.4339 | 295.6479 | 92.7538 | 96.154 | 79.3015
596.3167 | 255.6666 | 119.5559 | 286.7042 | 322.7763 | 295.4508 | 92.9439 | 96.4041 | 79.4412
597.3167 | 255.8734 | 119.7419 | 288.0342 | 324.371 | 296.3321 | 93.1218 | 96.6564 | 79.6312
598.3167 | 256.1365 | 119.9064 | 289.5489 | 324.9667 | 297.1384 | 93.3144 | 96.8565 | 79.7858
599.3167 | 256.2667 | 120.0822 | 288.6447 | 323.8088 | 296.6597 | 93.4997 | 97.1065 | 79.9517
600.3167 | 256.669 | 120.2575 | 288.3133 | 324.5812 | 297.0438 | 93.6698 | 97.3448 | 80.154
601.3167 | 256.5629 | 120.4329 | 287.6955 | 325.2155 | 295.799 | 93.8624 | 97.5894 | 80.2886
602.3167 | 256.4189 | 120.5875 | 287.2911 | 325.9904 | 294.6948 | 94.0257 | 97.8224 | 80.4687
603.3167 | 257.1226 | 120.7563 | 287.089 | 325.5002 | 292.798 | 94.2145 | 98.0633 | 80.6436
604.3167 | 257.541 | 120.9228 | 286.8438 | 325.9283 | 292.9093 | 94.3748 | 98.3028 | 80.8114
605.3167 | 258.0411 | 121.0939 | 286.9889 | 325.7738 | 292.614 | 94.5775 | 98.5111 | 80.9891
606.3167 | 258.5194 | 121.2431 | 285.8325 | 325.1251 | 292.2059 | 94.7693 | 98.7663 | 81.1551
607.3167 | 258.9028 | 121.4126 | 285.1075 | 324.4073 | 291.4303 | 94.953 | 98.9705 | 81.3099
608.3167 | 259.0732 | 121.5537 | 285.3421 | 324.2677 | 291.4625 | 95.1435 | 99.2237 | 81.4915
609.3167 | 259.0135 | 121.724 | 284.7987 | 323.9737 | 290.4711 | 95.3231 | 99.4469 | 81.6707
610.3167 | 259.304 | 121.8817 | 285.2961 | 324.1051 | 289.9742 | 95.5205 | 99.6896 | 81.8318
611.3167 | 259.8594 | 122.0354 | 286.432 | 324.4615 | 290.0841 | 95.7 | 99.9096 | 82.0357
612.3167 | 259.949 | 122.2049 | 285.8281 | 324.2165 | 290.6475 | 95.8731 | 100.1376 | 82.2293
613.3167 | 260.2182 | 122.349 | 287.2176 | 324.7383 | 289.7776 | 96.0487 | 100.3699 | 82.432
614.3167 | 260.4063 | 122.5148 | 287.5865 | 324.1946 | 289.267 | 96.2363 | 100.5715 | 82.6617
615.3167 | 260.2057 | 122.6719 | 287.6008 | 323.7811 | 288.0385 | 96.3848 | 100.8225 | 82.8959
616.3167 | 260.7524 | 122.846 | 288.1877 | 324.0114 | 287.3628 | 96.538 | 101.0495 | 83.1622
617.3167 | 260.1868 | 123.0005 | 289.2667 | 324.4156 | 287.3464 | 96.6942 | 101.2856 | 83.427
618.3167 | 260.5129 | 123.1596 | 289.4128 | 324.1836 | 288.6269 | 96.7882 | 101.529 | 83.7339
619.3167 | 260.2869 | 123.3185 | 290.0823 | 324.4073 | 288.3542 | 96.7751 | 101.7464 | 84.0462
620.3167 | 260.3651 | 123.4594 | 290.139 | 324.9828 | 290.0733 | 96.2642 | 101.9887 | 84.3433
621.3167 | 260.2047 | 123.6131 | 290.3622 | 324.4751 | 288.7586 | 95.8597 | 102.237 | 84.6782
622.3167 | 260.633 | 123.7657 | 291.5956 | 324.9752 | 287.3525 | 95.6156 | 102.4505 | 85.019
623.3167 | 261.5198 | 123.9125 | 292.3052 | 324.9294 | 289.0875 | 95.4981 | 102.692 | 85.3774
624.3167 | 261.738 | 124.0523 | 293.0718 | 325.4162 | 290.3371 | 95.4781 | 102.9056 | 85.7141
625.3167 | 262.226 | 124.2218 | 292.5845 | 324.7197 | 289.8456 | 95.4926 | 103.1476 | 86.0565
626.3167 | 263.0588 | 124.3719 | 290.691 | 325.4804 | 290.2471 | 95.5653 | 103.3727 | 86.3981
627.3167 | 263.4216 | 124.5163 | 291.3519 | 326.3866 | 290.5188 | 95.6136 | 103.5953 | 86.7479
628.3167 | 263.598 | 124.655 | 290.6118 | 325.6264 | 290.5259 | 95.7653 | 103.8418 | 87.067
629.3167 | 263.0157 | 124.8086 | 290.0365 | 325.03 | 290.431 | 95.8879 | 104.0763 | 87.3608
630.3167 | 262.9886 | 124.9667 | 289.6788 | 324.6774 | 289.7844 | 96.0585 | 104.2948 | 87.659
631.3167 | 263.0138 | 125.1051 | 289.2909 | 324.6382 | 288.633 | 96.2121 | 104.5418 | 87.9125
632.3167 | 263.7786 | 125.2526 | 291.0223 | 325.6023 | 289.6972 | 96.3803 | 104.7388 | 88.1708
633.3167 | 265.0964 | 125.3791 | 290.4906 | 325.4296 | 289.2882 | 96.5269 | 104.9645 | 88.382
634.3167 | 265.2471 | 125.5475 | 292.1411 | 326.2805 | 290.7724 | 96.6662 | 105.1864 | 88.6302
635.3167 | 265.179 | 125.6946 | 293.4764 | 327.3117 | 292.404 | 96.8278 | 105.4256 | 88.8557
636.3167 | 264.7337 | 125.8308 | 296.5548 | 328.0476 | 293.4369 | 97.0958 | 105.6552 | 89.1302
637.3167 | 264.6567 | 125.9731 | 296.3447 | 328.5745 | 295.3258 | 97.3743 | 105.9186 | 89.3803
638.3167 | 265.7899 | 126.1362 | 297.5812 | 329.6827 | 297.8031 | 98.7118 | 106.3229 | 89.9571
639.3167 | 265.1165 | 126.2587 | 299.0806 | 330.8057 | 300.2597 | 97.9484 | 106.3897 | 89.8579
640.3167 | 264.4127 | 126.3899 | 297.8872 | 331.8505 | 301.3684 | 98.318 | 106.6763 | 90.1384
641.3167 | 264.6836 | 126.5165 | 296.8395 | 331.4203 | 301.8881 | 97.6628 | 106.7848 | 90.0463
642.3167 | 265.7815 | 126.6629 | 296.4609 | 331.9299 | 302.8721 | 97.7779 | 106.9896 | 90.1893
643.3167 | 266.5627 | 126.8094 | 297.0869 | 332.7134 | 304.3085 | 97.8741 | 107.2149 | 90.3462
644.3167 | 267.0735 | 126.9253 | 298.356 | 333.042 | 306.5856 | 97.9781 | 107.4591 | 90.4828
645.3167 | 267.95 | 127.0623 | 299.2483 | 333.4228 | 309.2112 | 98.0919 | 107.6827 | 90.6404
646.3167 | 268.5787 | 127.1839 | 300.0436 | 334.9454 | 309.7317 | 98.1971 | 107.8821 | 90.8057
647.3167 | 268.6754 | 127.3026 | 300.2796 | 335.682 | 310.9925 | 98.2954 | 108.1351 | 90.9176
648.3167 | 269.9805 | 127.4358 | 298.0821 | 335.2502 | 312.3591 | 98.4032 | 108.3485 | 91.0524
649.3167 | 270.249 | 127.5763 | 297.0955 | 335.4884 | 312.5539 | 98.4993 | 108.5835 | 91.166
650.3167 | 270.2398 | 127.7016 | 296.0494 | 334.9232 | 311.4915 | 98.6104 | 108.8009 | 91.2491
651.3167 | 270.5401 | 127.8205 | 295.9098 | 334.3023 | 310.978 | 98.6736 | 109.0236 | 91.3694
652.3167 | 270.6512 | 127.9522 | 298.227 | 335.1002 | 310.6276 | 98.7762 | 109.2477 | 91.4973
653.3167 | 270.9777 | 128.0893 | 298.1421 | 336.5512 | 310.1733 | 98.865 | 109.4875 | 91.5941
654.3167 | 271.3604 | 128.2119 | 298.1089 | 336.6227 | 310.8972 | 98.9629 | 109.7148 | 91.699
655.3167 | 271.1421 | 128.3471 | 299.6256 | 337.4228 | 310.5724 | 99.0822 | 109.9351 | 91.8123
656.3167 | 270.949 | 128.4758 | 300.6144 | 339.2447 | 310.7547 | 99.1625 | 110.1801 | 91.9045
657.3167 | 271.0792 | 128.5779 | 298.7142 | 339.2665 | 310.4771 | 99.286 | 110.3856 | 91.9881
658.3167 | 271.9395 | 128.7328 | 297.6269 | 338.1673 | 309.3181 | 99.3654 | 110.6214 | 92.076
659.3167 | 272.2264 | 128.8592 | 298.6883 | 338.0765 | 308.6652 | 99.4597 | 110.8469 | 92.1604
660.3167 | 272.3652 | 128.9937 | 299.2584 | 338.9407 | 310.5555 | 99.5525 | 111.0552 | 92.2433
661.3167 | 271.4645 | 129.1194 | 299.4659 | 339.8033 | 311.362 | 99.6693 | 111.2935 | 92.3356
662.3167 | 272.7757 | 129.237 | 301.2028 | 340.1407 | 311.5846 | 99.7563 | 111.5299 | 92.3931
663.3167 | 273.3527 | 129.3767 | 300.3593 | 339.6948 | 312.2043 | 99.8728 | 111.758 | 92.4709
664.3167 | 274.6198 | 129.511 | 299.8078 | 339.5348 | 312.6997 | 99.9786 | 111.9753 | 92.5706
665.3167 | 274.938 | 129.641 | 301.1943 | 340.0442 | 313.8537 | 100.0746 | 112.1993 | 92.6411
666.3167 | 274.7164 | 129.7733 | 301.8886 | 341.6553 | 315.554 | 100.175 | 112.4318 | 92.7162
667.3167 | 274.4666 | 129.8934 | 302.7771 | 342.31 | 316.3232 | 100.288 | 112.6558 | 92.8034
668.3167 | 274.2529 | 130.0191 | 304.674 | 342.7179 | 314.6379 | 100.4073 | 112.907 | 92.8492
669.3167 | 274.4979 | 130.1525 | 305.6952 | 342.9924 | 313.934 | 100.4898 | 113.135 | 92.8953
670.3167 | 274.5831 | 130.2818 | 307.5133 | 343.7539 | 314.1704 | 100.5897 | 113.3525 | 92.9678
671.3167 | 276.1707 | 130.4184 | 309.816 | 345.107 | 314.4193 | 100.695 | 113.5946 | 92.9938
672.3167 | 276.547 | 130.5573 | 310.1493 | 344.4106 | 312.3632 | 100.8059 | 113.8301 | 93.0557
673.3167 | 276.5501 | 130.6789 | 309.5533 | 345.5948 | 313.055 | 100.8944 | 114.0594 | 93.0969
674.3167 | 276.7221 | 130.8134 | 308.8236 | 346.3476 | 312.2812 | 100.9881 | 114.3157 | 93.1199
675.3167 | 277.8062 | 130.9374 | 308.2424 | 346.245 | 311.4872 | 101.1057 | 114.534 | 93.1683
676.3167 | 277.0166 | 131.0561 | 309.6875 | 346.4235 | 311.8409 | 101.1917 | 114.795 | 93.2211
677.3167 | 277.3269 | 131.183 | 310.8836 | 347.6927 | 313.6486 | 101.2963 | 115.0347 | 93.2663
678.3167 | 278.7498 | 131.311 | 311.4887 | 348.6542 | 313.8092 | 101.3863 | 115.2887 | 93.2158
679.3167 | 279.3072 | 131.4116 | 310.5766 | 348.2202 | 313.2668 | 101.466 | 115.5465 | 93.2635
680.3167 | 278.9482 | 131.5361 | 309.9686 | 347.9642 | 313.796 | 101.5323 | 115.8047 | 93.3032
681.3167 | 279.1213 | 131.662 | 308.5244 | 347.6451 | 312.7905 | 101.6057 | 116.0587 | 93.3349
682.3167 | 279.5076 | 131.7852 | 307.854 | 347.4569 | 313.7792 | 101.7073 | 116.3302 | 93.3871
683.3167 | 277.9951 | 131.8995 | 307.2647 | 346.5388 | 313.3974 | 101.7857 | 116.594 | 93.4119
684.3167 | 277.3406 | 132.0191 | 306.5706 | 346.3094 | 313.3395 | 101.8506 | 116.8838 | 93.4899
685.3167 | 277.0255 | 132.1681 | 306.5293 | 346.9209 | 314.0045 | 101.9137 | 117.1615 | 93.547
686.3167 | 276.8888 | 132.2978 | 306.4687 | 346.1286 | 312.707 | 101.9782 | 117.4425 | 93.583
687.3167 | 277.1654 | 132.4201 | 306.0762 | 345.1582 | 310.9372 | 102.0749 | 117.7611 | 93.6492
688.3167 | 276.8693 | 132.5359 | 306.8859 | 345.4332 | 308.7084 | 102.1608 | 118.0598 | 93.7299
689.3167 | 277.1874 | 132.6565 | 307.408 | 345.3389 | 306.9264 | 102.2386 | 118.3469 | 93.7753
690.3167 | 278.1311 | 132.7621 | 308.1233 | 345.9407 | 305.6048 | 102.2951 | 118.6802 | 93.8403
691.3167 | 277.4537 | 132.8841 | 308.7932 | 345.5742 | 304.7215 | 102.3739 | 118.9985 | 93.9326
692.3167 | 277.1472 | 132.9924 | 309.4486 | 345.7983 | 305.0959 | 102.4471 | 119.3314 | 94.003
693.3167 | 276.4415 | 133.1128 | 310.2334 | 344.7268 | 305.9162 | 102.5488 | 119.694 | 94.0802
694.3167 | 277.1213 | 133.2289 | 310.5579 | 344.1865 | 305.1045 | 102.6163 | 120.0532 | 94.1812
695.3167 | 277.6862 | 133.3419 | 310.382 | 343.7024 | 306.1934 | 102.6973 | 120.4011 | 94.2622
696.3167 | 278.3736 | 133.4472 | 310.8309 | 343.7111 | 307.2852 | 102.7849 | 120.7593 | 94.3573
697.3167 | 278.4024 | 133.5749 | 312.288 | 344.5297 | 308.1552 | 102.8674 | 121.1579 | 94.4644
698.3167 | 279.2083 | 133.6958 | 312.8182 | 344.8548 | 309.4493 | 102.9518 | 121.5492 | 94.5538
699.3167 | 279.655 | 133.7945 | 313.7694 | 346.1874 | 310.9058 | 103.0289 | 121.9381 | 94.6453
700.3167 | 280.0089 | 133.8881 | 314.1556 | 346.5679 | 311.6237 | 103.0922 | 122.3633 | 94.7257
701.3167 | 280.1213 | 134.0021 | 314.1297 | 346.6256 | 311.5974 | 103.1812 | 122.7158 | 94.8143
702.3167 | 280.2098 | 134.1107 | 313.4873 | 345.5829 | 310.5751 | 103.2971 | 123.1141 | 94.9171
703.3167 | 280.7295 | 134.2086 | 311.0686 | 344.708 | 310.9405 | 103.3652 | 123.492 | 95.0177
704.3167 | 280.9929 | 134.3313 | 310.7061 | 344.1412 | 311.3984 | 103.4825 | 123.8629 | 95.1129
705.3167 | 281.4009 | 134.4307 | 309.5239 | 343.5879 | 312.1238 | 103.5956 | 124.238 | 95.235
706.3167 | 281.3609 | 134.5382 | 308.3721 | 342.5351 | 311.7257 | 103.711 | 124.56 | 95.3357
707.3167 | 281.4462 | 134.6486 | 307.1367 | 342.1465 | 310.2209 | 103.8812 | 124.9225 | 95.4187
708.3167 | 282.1004 | 134.7519 | 306.1838 | 342.5995 | 310.4608 | 104.071 | 125.3177 | 95.5463
709.3167 | 283.0793 | 134.8679 | 305.8687 | 341.8553 | 309.6833 | 104.2973 | 125.6513 | 95.6617
710.3167 | 283.088 | 134.9609 | 306.1537 | 342.9361 | 309.9656 | 104.5446 | 126.0135 | 95.7668
711.3167 | 283.0892 | 135.0655 | 306.1549 | 343.0153 | 311.4636 | 104.7981 | 126.3736 | 95.8931
712.3167 | 282.6967 | 135.1571 | 305.0073 | 342.7674 | 313.7318 | 105.0965 | 126.7095 | 96.0327
713.3167 | 281.7778 | 135.2807 | 304.0443 | 343.421 | 314.5288 | 105.3769 | 127.0627 | 96.1427
714.3167 | 281.7439 | 135.3829 | 303.7084 | 343.2037 | 313.6361 | 105.7053 | 127.4172 | 96.2479
715.3167 | 282.2439 | 135.4788 | 302.8756 | 343.4003 | 313.2127 | 106.0706 | 127.7324 | 96.3715
716.3167 | 282.9784 | 135.5784 | 302.0312 | 342.6828 | 312.5804 | 106.4458 | 128.0836 | 96.5088
717.3167 | 283.6547 | 135.6819 | 301.663 | 342.1755 | 312.5884 | 106.8501 | 128.4149 | 96.6237
718.3167 | 284.0941 | 135.7755 | 300.456 | 342.3008 | 312.1165 | 107.2542 | 128.7473 | 96.7446
719.3167 | 283.9177 | 135.8741 | 300.6268 | 342.524 | 310.9883 | 107.6826 | 129.0978 | 96.8877
720.3167 | 284.1363 | 135.9499 | 299.2128 | 342.2899 | 310.1527 | 108.1054 | 129.4347 | 97.0112
721.3167 | 284.6933 | 136.0494 | 299.4681 | 342.1694 | 309.3266 | 108.4977 | 129.7604 | 97.1593
722.3167 | 284.2067 | 136.1523 | 299.4361 | 342.3432 | 308.5171 | 108.8878 | 130.1104 | 97.2759
723.3167 | 284.3408 | 136.2481 | 298.8494 | 342.3142 | 308.3537 | 109.2593 | 130.4397 | 97.4148
724.3167 | 284.8638 | 136.3391 | 300.563 | 342.0734 | 307.9554 | 109.612 | 130.757 | 97.5553
725.3167 | 285.1202 | 136.4374 | 301.4949 | 341.82 | 306.4141 | 109.9498 | 131.0909 | 97.6565
726.3167 | 285.4727 | 136.5378 | 303.1308 | 342.2321 | 306.4489 | 110.3047 | 131.3961 | 97.784
727.3167 | 285.0983 | 136.6523 | 304.9942 | 342.8656 | 306.5003 | 110.636 | 131.7101 | 97.9173
728.3167 | 285.097 | 136.7399 | 306.587 | 343.9116 | 306.2995 | 110.9699 | 132.0294 | 98.0294
729.3167 | 285.2163 | 136.8276 | 309.158 | 345.073 | 307.616 | 111.2923 | 132.3728 | 98.1288
730.3167 | 285.2842 | 136.9151 | 310.8193 | 345.6752 | 308.3363 | 111.6125 | 132.6934 | 98.2581
731.3167 | 284.8696 | 137.008 | 311.8834 | 347.208 | 309.5397 | 111.9164 | 133.003 | 98.3305
732.3167 | 285.8377 | 137.0967 | 313.231 | 348.1444 | 310.8081 | 112.2237 | 133.3383 | 98.455
733.3167 | 285.5999 | 137.1897 | 312.1524 | 348.9873 | 312.8017 | 112.5286 | 133.6449 | 98.5476
734.3167 | 287.0563 | 137.2773 | 312.3742 | 349.0979 | 313.3806 | 112.8484 | 133.9733 | 98.6645
735.3167 | 285.6803 | 137.359 | 312.1127 | 349.2575 | 314.6126 | 113.1517 | 134.2805 | 98.7775
736.3167 | 285.5209 | 137.4538 | 312.9751 | 348.6651 | 314.9776 | 113.4585 | 134.5994 | 98.8797
737.3167 | 285.2141 | 137.531 | 311.531 | 348.5953 | 315.2029 | 113.7718 | 134.934 | 98.9853
738.3167 | 285.061 | 137.6349 | 312.2496 | 348.5774 | 314.9123 | 114.0917 | 135.2586 | 99.1177
739.3167 | 285.4895 | 137.7393 | 312.8177 | 349.0039 | 314.8566 | 114.4283 | 135.5326 | 99.2648
740.3167 | 287.4461 | 137.8273 | 313.6689 | 349.273 | 315.3321 | 114.7507 | 135.8692 | 99.3815
741.3167 | 287.5354 | 137.9168 | 313.0726 | 349.3832 | 315.7047 | 115.0879 | 136.1714 | 99.5321
742.3167 | 287.7106 | 138.0079 | 312.452 | 349.4612 | 315.6744 | 115.4459 | 136.4918 | 99.6766
743.3167 | 288.0845 | 138.1048 | 312.1014 | 349.4285 | 315.9809 | 115.7975 | 136.8153 | 99.8195
744.3167 | 287.9404 | 138.1894 | 313.043 | 349.9566 | 315.2679 | 116.1403 | 137.1233 | 99.9402
745.3167 | 288.6118 | 138.2775 | 314.8108 | 350.9101 | 316.2365 | 116.5084 | 137.4395 | 100.0809
746.3167 | 289.8855 | 138.3517 | 316.1668 | 351.2113 | 317.1478 | 116.8536 | 137.7489 | 100.1718
747.3167 | 291.1493 | 138.4362 | 316.4806 | 351.8575 | 319.522 | 117.1809 | 138.0644 | 100.2651
748.3167 | 292.0171 | 138.5664 | 317.8566 | 352.9413 | 319.8649 | 119.5003 | 138.7351 | 101.0947
749.3167 | 292.0748 | 138.606 | 316.7973 | 351.5812 | 320.423 | 117.8293 | 138.7276 | 100.4748
750.3167 | 292.4157 | 138.7337 | 317.7244 | 352.2725 | 320.2108 | 119.4997 | 139.2846 | 101.0759
751.3167 | 292.226 | 138.7721 | 317.9799 | 352.9221 | 322.4111 | 118.4434 | 139.3797 | 100.6644
752.3167 | 292.0896 | 138.8925 | 319.4159 | 353.9209 | 324.5092 | 119.0912 | 139.708 | 100.8884
753.3167 | 292.2205 | 138.9775 | 320.1213 | 354.2599 | 325.4742 | 119.9126 | 140.1657 | 101.1261
754.3167 | 293.0707 | 139.0388 | 318.82 | 355.9815 | 326.8067 | 119.377 | 140.3267 | 100.9526
755.3167 | 293.1819 | 139.1469 | 318.8137 | 356.4803 | 325.9711 | 119.6638 | 140.6628 | 101.0773
756.3167 | 293.8478 | 139.2191 | 318.3729 | 356.1054 | 324.1272 | 119.9678 | 140.9604 | 101.1413
757.3167 | 294.1188 | 139.3133 | 317.1044 | 355.6385 | 324.5655 | 120.2541 | 141.2913 | 101.2156
758.3167 | 293.6906 | 139.3917 | 316.1899 | 355.1656 | 323.4376 | 121.3325 | 141.7543 | 101.5867
759.3167 | 293.5786 | 139.4608 | 314.8464 | 354.3589 | 322.1431 | 121.1229 | 142.0205 | 101.5047
760.3167 | 293.4346 | 139.573 | 313.8102 | 353.9916 | 321.6612 | 121.4109 | 142.3221 | 101.6112
761.3167 | 294.2091 | 139.6915 | 313.3551 | 353.1489 | 321.7269 | 121.3825 | 142.5954 | 101.608
762.3167 | 295.0729 | 139.7954 | 313.6043 | 353.325 | 321.1397 | 121.6533 | 142.9148 | 101.7751
763.3167 | 295.1081 | 139.8784 | 312.9244 | 352.9968 | 319.5312 | 121.9149 | 143.2352 | 101.9346
764.3167 | 295.7563 | 139.9867 | 315.0345 | 352.8721 | 318.4366 | 122.148 | 143.551 | 102.0906
765.3167 | 295.2638 | 140.0864 | 315.0354 | 352.6529 | 316.6252 | 122.4121 | 143.8956 | 102.2546
766.3167 | 295.4319 | 140.1708 | 315.7323 | 352.8537 | 315.9441 | 124.3839 | 144.5567 | 103.0647
767.3167 | 295.6417 | 140.352 | 314.4364 | 353.0916 | 316.4399 | 123.2778 | 144.6289 | 102.7031
768.3167 | 295.7685 | 140.5108 | 313.6943 | 353.1573 | 317.3783 | 124.135 | 145.0353 | 103.0646
769.3167 | 295.022 | 140.5745 | 313.147 | 352.7942 | 317.0727 | 123.4523 | 145.248 | 102.9366
770.3167 | 295.2606 | 140.6462 | 314.5196 | 353.9392 | 316.2625 | 123.7668 | 145.6276 | 103.1366
771.3167 | 295.4345 | 140.7306 | 313.2282 | 354.1636 | 316.9151 | 123.9538 | 145.9409 | 103.2653
772.3167 | 295.8562 | 140.8217 | 311.7729 | 354.223 | 317.3309 | 124.1937 | 146.2699 | 103.4491
773.3167 | 295.8484 | 140.9089 | 312.4007 | 354.2818 | 316.8186 | 124.4573 | 146.6213 | 103.6091
774.3167 | 296.1489 | 140.9962 | 312.3702 | 354.4895 | 315.5949 | 124.6873 | 146.932 | 103.7692
775.3167 | 296.3559 | 141.0743 | 311.4814 | 353.5972 | 314.149 | 124.9577 | 147.2765 | 103.9264
776.3167 | 296.5381 | 141.1466 | 311.9755 | 354.585 | 314.5313 | 125.1932 | 147.6288 | 104.1201
777.3167 | 296.4017 | 141.2267 | 313.0771 | 355.753 | 314.9322 | 125.8339 | 148.0351 | 104.3874
778.3167 | 297.1668 | 141.272 | 313.3412 | 356.1302 | 315.5388 | 125.6864 | 148.3247 | 104.444
779.3167 | 296.8655 | 141.372 | 314.3526 | 356.4268 | 315.6049 | 125.9216 | 148.6727 | 104.5793
780.3167 | 297.3195 | 141.4429 | 314.1483 | 356.3097 | 315.9845 | 126.203 | 149.0242 | 104.7412
781.3167 | 298.4979 | 141.5184 | 312.8342 | 356.5051 | 315.6963 | 126.4838 | 149.3659 | 104.9227
782.3167 | 299.1206 | 141.5823 | 313.6264 | 356.5994 | 315.7638 | 126.753 | 149.7455 | 105.0934
783.3167 | 299.5429 | 141.6797 | 314.5792 | 356.734 | 316.2653 | 127.0019 | 150.0794 | 105.261
784.3167 | 300.1172 | 141.7758 | 314.5813 | 356.5525 | 317.3949 | 127.2595 | 150.4339 | 105.4181
785.3167 | 300.139 | 141.8671 | 314.2052 | 356.3034 | 318.3792 | 127.5087 | 150.7744 | 105.5608
786.3167 | 300.0775 | 141.973 | 313.4555 | 356.1308 | 318.5331 | 127.766 | 151.1307 | 105.7167
787.3167 | 300.3107 | 142.0871 | 311.8268 | 355.6419 | 318.9101 | 127.9721 | 151.4806 | 105.8815
788.3167 | 299.6414 | 142.1973 | 312.4563 | 355.3791 | 318.8929 | 128.2183 | 151.8065 | 106.0251
789.3167 | 299.5303 | 142.3075 | 312.8181 | 356.7334 | 318.8888 | 128.4707 | 152.1491 | 106.1767
790.3167 | 299.3613 | 142.4143 | 311.8946 | 356.4928 | 318.2848 | 128.71 | 152.523 | 106.3057
791.3167 | 300.4432 | 142.4946 | 313.4432 | 357.3795 | 316.8001 | 128.9508 | 152.8617 | 106.4723
792.3167 | 299.8236 | 142.6126 | 313.9831 | 357.3992 | 316.9871 | 129.1643 | 153.2253 | 106.6179
793.3167 | 299.752 | 142.7238 | 315.7437 | 358.6265 | 317.1645 | 129.3849 | 153.5692 | 106.7695
794.3167 | 298.9832 | 142.8657 | 319.2827 | 358.6703 | 318.0139 | 129.6403 | 153.9098 | 106.9267
795.3167 | 299.1552 | 142.987 | 322.3803 | 360.3816 | 318.8169 | 129.8524 | 154.2519 | 107.0567
796.3167 | 299.6515 | 143.1128 | 324.1511 | 360.7253 | 320.4667 | 130.0888 | 154.6272 | 107.2298
797.3167 | 300.1041 | 143.2383 | 325.1315 | 361.5609 | 321.6732 | 130.319 | 154.9698 | 107.373
798.3167 | 300.3851 | 143.3607 | 325.0584 | 362.0548 | 323.3966 | 130.5559 | 155.3215 | 107.5154
799.3167 | 300.5017 | 143.493 | 325.2375 | 362.7099 | 324.2013 | 130.7789 | 155.6772 | 107.6757
800.3167 | 300.8454 | 143.6146 | 325.7397 | 363.0499 | 323.9576 | 131.0271 | 156.0351 | 107.8125
801.3167 | 300.4444 | 143.7313 | 326.85 | 362.919 | 324.8838 | 131.2398 | 156.3583 | 107.9663
802.3167 | 300.4027 | 143.8589 | 326.7839 | 363.7262 | 325.8202 | 131.4388 | 156.6998 | 108.1011
803.3167 | 300.9655 | 143.9937 | 327.0899 | 364.2974 | 325.8178 | 131.6545 | 157.0419 | 108.2396
804.3167 | 301.0323 | 144.1235 | 324.9483 | 364.2912 | 326.1575 | 131.8584 | 157.3997 | 108.3896
805.3167 | 301.789 | 144.2438 | 323.2182 | 364.6759 | 325.2648 | 132.0968 | 157.7369 | 108.5284
806.3167 | 300.7948 | 144.4197 | 322.4325 | 364.4346 | 324.7245 | 132.295 | 158.0681 | 108.6823
807.3167 | 300.8162 | 144.5804 | 323.2786 | 364.2262 | 324.4719 | 132.5388 | 158.4236 | 108.8357
808.3167 | 301.2515 | 144.7332 | 325.3328 | 364.9659 | 325.2919 | 132.7517 | 158.7775 | 108.9862
809.3167 | 301.2358 | 144.8724 | 326.6426 | 365.8825 | 326.5757 | 132.9892 | 159.1076 | 109.1262
810.3167 | 301.3239 | 144.9671 | 327.6618 | 366.7108 | 327.4737 | 133.2133 | 159.4347 | 109.2665
811.3167 | 301.4662 | 145.0957 | 325.8723 | 366.8842 | 327.9445 | 133.4118 | 159.7799 | 109.424
812.3167 | 302.1537 | 145.2271 | 325.8663 | 368.1502 | 329.7041 | 133.6569 | 160.1082 | 109.566
813.3167 | 303.0719 | 145.3865 | 323.9902 | 367.243 | 330.3165 | 133.8704 | 160.4574 | 109.7281
814.3167 | 303.8389 | 145.5365 | 323.7318 | 367.9973 | 330.6577 | 134.0858 | 160.7945 | 109.8871
815.3167 | 303.9855 | 145.6825 | 322.67 | 367.9117 | 331.1306 | 134.2937 | 161.1237 | 110.0328
816.3167 | 302.9952 | 145.827 | 322.9362 | 367.614 | 331.3873 | 134.5052 | 161.446 | 110.1899
817.3167 | 302.4795 | 145.9486 | 322.3815 | 368.189 | 330.8665 | 134.7112 | 161.7849 | 110.365
818.3167 | 302.9771 | 146.0702 | 323.5756 | 368.718 | 330.8997 | 134.922 | 162.0983 | 110.5228
819.3167 | 303.1911 | 146.2177 | 324.7528 | 369.617 | 330.247 | 135.1176 | 162.4196 | 110.7048
820.3167 | 303.2328 | 146.3586 | 325.0764 | 370.0497 | 330.4873 | 135.3363 | 162.7471 | 110.8773
821.3167 | 303.5478 | 146.518 | 323.8421 | 369.1752 | 330.77 | 135.5174 | 163.1007 | 111.0643
822.3167 | 303.7067 | 146.6465 | 322.9449 | 367.5224 | 329.1142 | 135.7569 | 163.4333 | 111.2484
823.3167 | 303.1289 | 146.5999 | 323.1358 | 367.7571 | 328.7887 | 136.009 | 163.7384 | 111.4334
824.3167 | 303.2039 | 146.6771 | 323.0549 | 367.1813 | 327.5822 | 136.2357 | 164.0664 | 111.6184
825.3167 | 302.9385 | 146.8115 | 324.5712 | 367.6606 | 327.8541 | 136.4643 | 164.399 | 111.7858
826.3167 | 303.0074 | 146.9602 | 324.2743 | 367.3975 | 326.9201 | 136.6521 | 164.7329 | 111.9796
827.3167 | 302.9921 | 147.1187 | 325.6147 | 367.8556 | 325.7308 | 136.8891 | 165.0899 | 112.1418
828.3167 | 303.4839 | 147.2779 | 326.6102 | 368.3088 | 326.1875 | 137.1553 | 165.41 | 112.3136
829.3167 | 303.4799 | 147.4214 | 327.2652 | 368.7806 | 327.0038 | 137.3737 | 165.7559 | 112.5051
830.3167 | 302.8132 | 147.5952 | 327.1335 | 368.4972 | 325.541 | 137.6162 | 166.0924 | 112.6916
831.3167 | 302.6807 | 147.5333 | 327.1016 | 368.2339 | 324.8113 | 137.7736 | 166.4245 | 112.8592
832.3167 | 302.5453 | 147.5543 | 326.2941 | 367.1256 | 323.0573 | 138.0207 | 166.7567 | 113.0481
833.3167 | 301.9161 | 147.691 | 326.2539 | 366.7602 | 322.3686 | 138.243 | 167.1036 | 113.2435
834.3167 | 302.7579 | 147.8501 | 325.9146 | 365.9487 | 320.1676 | 138.4392 | 167.4342 | 113.4324
835.3167 | 302.5986 | 148.0022 | 326.9572 | 365.7073 | 318.8528 | 138.6758 | 167.7638 | 113.6013
836.3167 | 302.8803 | 148.1653 | 327.0527 | 365.9968 | 318.5294 | 138.9148 | 168.0985 | 113.777
837.3167 | 303.3321 | 148.3531 | 326.568 | 365.6244 | 318.7121 | 139.1587 | 168.4457 | 113.9936
838.3167 | 304.671 | 148.511 | 325.8963 | 365.5212 | 318.4188 | 139.3879 | 168.7721 | 114.1882
839.3167 | 303.6646 | 148.6641 | 324.4637 | 364.8074 | 317.4033 | 139.5851 | 169.1122 | 114.3883
840.3167 | 303.5446 | 148.8078 | 324.749 | 364.2795 | 315.7279 | 139.8522 | 169.4465 | 114.5584
841.3167 | 302.9538 | 148.8983 | 324.8855 | 364.0275 | 315.6964 | 140.0619 | 169.801 | 114.7547
842.3167 | 303.2371 | 149.0295 | 326.4918 | 365.2408 | 316.1897 | 140.2846 | 170.1132 | 114.9527
843.3167 | 302.6535 | 149.1457 | 327.181 | 365.5846 | 316.9949 | 140.5215 | 170.4835 | 115.1498
844.3167 | 302.3648 | 149.2661 | 325.6967 | 365.8444 | 317.1819 | 140.7599 | 170.8018 | 115.3686
845.3167 | 302.0044 | 149.385 | 325.289 | 365.3466 | 317.009 | 140.9465 | 171.1259 | 115.5688
846.3167 | 302.117 | 149.4959 | 324.8761 | 364.8626 | 317.7805 | 141.2209 | 171.4847 | 115.7692
847.3167 | 301.8447 | 149.6208 | 323.968 | 364.4118 | 318.4854 | 141.4603 | 171.7935 | 115.981
848.3167 | 302.2072 | 149.759 | 323.5457 | 364.3228 | 318.6409 | 141.7235 | 172.1402 | 116.2103
849.3167 | 302.5431 | 149.9081 | 323.1176 | 365.3743 | 319.2953 | 141.9651 | 172.4827 | 116.4104
850.3167 | 303.1961 | 150.046 | 323.926 | 366.124 | 320.5718 | 142.2436 | 172.8155 | 116.5604
851.3167 | 303.5911 | 150.1728 | 324.1192 | 366.4303 | 319.7854 | 142.4916 | 173.1728 | 116.7719
852.3167 | 304.2497 | 150.3929 | 323.8221 | 366.3878 | 319.8028 | 142.7034 | 173.4857 | 116.985
853.3167 | 305.3575 | 150.5733 | 322.5996 | 365.7778 | 319.0591 | 143.0114 | 173.8565 | 117.235
854.3167 | 306.0173 | 150.7524 | 322.7154 | 365.4572 | 320.0666 | 143.2917 | 174.188 | 117.4909
855.3167 | 306.6562 | 150.9363 | 322.2234 | 365.0116 | 320.7985 | 143.566 | 174.5181 | 117.7202
856.3167 | 307.1235 | 151.1184 | 321.5393 | 364.0107 | 321.0836 | 143.8167 | 174.8599 | 117.9241
857.3167 | 307.1926 | 151.2953 | 319.9822 | 363.8164 | 322.5998 | 144.0097 | 175.2048 | 118.1576
858.3167 | 307.1952 | 151.4829 | 320.5706 | 364.2114 | 323.8608 | 144.3995 | 175.5269 | 118.3797
859.3167 | 307.712 | 151.6648 | 320.8899 | 363.7992 | 323.9034 | 144.59 | 175.864 | 118.5634
860.3167 | 308.8733 | 151.8628 | 321.3639 | 363.5397 | 324.8451 | 144.8279 | 176.2102 | 118.7791
861.3167 | 308.6623 | 152.0595 | 321.8821 | 364.3429 | 325.4209 | 145.0275 | 176.5536 | 118.9966
862.3167 | 308.7713 | 152.2611 | 322.0287 | 364.9161 | 326.8963 | 145.3417 | 176.876 | 119.2051
863.3167 | 309.2998 | 152.457 | 322.6199 | 366.7413 | 328.7502 | 145.7695 | 177.2197 | 119.4308
864.3167 | 309.3649 | 152.6754 | 322.2578 | 366.7943 | 329.284 | 146.0928 | 177.5504 | 119.6647
865.3167 | 309.9162 | 152.8666 | 320.5246 | 366.2731 | 330.1869 | 146.2214 | 177.8968 | 119.8899
866.3167 | 310.4501 | 153.0606 | 320.4946 | 366.5611 | 331.7695 | 146.694 | 178.2182 | 120.0954
867.3167 | 310.4893 | 153.2471 | 320.6643 | 366.5959 | 331.5785 | 146.8826 | 178.5785 | 120.3253
868.3167 | 310.3033 | 153.4419 | 320.6915 | 365.9721 | 331.8848 | 147.2113 | 178.888 | 120.5677
869.3167 | 310.5015 | 153.6192 | 322.1389 | 365.2928 | 332.4918 | 147.4712 | 179.2001 | 120.7808
870.3167 | 310.2785 | 153.8255 | 321.2422 | 365.2724 | 332.8852 | 147.8107 | 179.521 | 120.9919
871.3167 | 310.6248 | 153.9677 | 321.0224 | 364.6524 | 332.5746 | 148.0013 | 179.8513 | 121.223
872.3167 | 310.1556 | 154.1228 | 320.9807 | 364.2751 | 332.4706 | 148.1466 | 180.1953 | 121.4531
873.3167 | 311.1378 | 154.2903 | 323.3765 | 365.6941 | 333.1914 | 148.5204 | 180.5256 | 121.691
874.3167 | 310.8274 | 154.4634 | 324.7076 | 365.4773 | 334.184 | 148.7444 | 180.8427 | 121.9243
875.3167 | 310.3534 | 154.6803 | 327.2452 | 366.2945 | 335.4222 | 149.1493 | 181.1964 | 122.1653
876.3167 | 310.5456 | 154.8681 | 327.486 | 365.8531 | 337.0666 | 149.1361 | 181.5294 | 122.4466
877.3167 | 310.5718 | 155.0472 | 326.1027 | 365.9091 | 336.3617 | 149.4386 | 181.8373 | 122.6539
878.3167 | 311.5404 | 155.2349 | 326.5001 | 365.631 | 336.2604 | 149.6736 | 182.1635 | 122.879
879.3167 | 311.6447 | 155.4277 | 325.8351 | 364.8541 | 335.7537 | 149.9794 | 182.5043 | 123.1132
880.3167 | 311.6546 | 155.6082 | 325.1875 | 364.6648 | 336.3664 | 150.2419 | 182.8351 | 123.3693
881.3167 | 311.6482 | 155.7761 | 325.2687 | 364.5412 | 336.8839 | 150.5298 | 183.1567 | 123.5839
882.3167 | 311.7515 | 155.9396 | 326.962 | 365.6543 | 338 | 150.8386 | 183.4781 | 123.8158
883.3167 | 312.2084 | 156.1186 | 326.6477 | 366.2253 | 338.7058 | 151.094 | 183.8095 | 124.0756
884.3167 | 312.6557 | 156.3066 | 325.0959 | 365.8172 | 338.3744 | 151.5414 | 184.1369 | 124.3236
885.3167 | 313.1323 | 156.4205 | 324.2635 | 365.5679 | 338.1545 | 151.6876 | 184.4641 | 124.5509
886.3167 | 312.9913 | 156.5952 | 324.7812 | 366.0247 | 337.0949 | 152.0384 | 184.7952 | 124.786
887.3167 | 312.4396 | 156.7528 | 323.2635 | 365.584 | 336.7374 | 152.3636 | 185.1135 | 125.0208
888.3167 | 311.5269 | 156.8864 | 322.8459 | 365.0685 | 335.4215 | 152.5835 | 185.4355 | 125.2396
889.3167 | 311.1142 | 157.0256 | 323.0217 | 364.3296 | 333.5752 | 152.8302 | 185.7491 | 125.4472
890.3167 | 311.6684 | 157.1211 | 322.9961 | 364.4119 | 331.8124 | 153.2814 | 186.0743 | 125.6665
891.3167 | 311.7324 | 157.2298 | 324.7457 | 365.3429 | 329.653 | 153.5 | 186.3861 | 125.9353
892.3167 | 312.7397 | 157.2569 | 326.8682 | 366.3344 | 328.6501 | 153.8566 | 186.7037 | 126.1778
893.3167 | 313.3274 | 157.3842 | 329.2019 | 366.7669 | 327.7494 | 154.1949 | 187.0135 | 126.4069
894.3167 | 313.614 | 157.5487 | 329.3254 | 366.2063 | 325.8835 | 154.5928 | 187.3454 | 126.6527
895.3167 | 313.8266 | 157.7227 | 329.8384 | 365.3457 | 324.3094 | 155.0018 | 187.6604 | 126.9234
896.3167 | 314.2611 | 157.8822 | 331.8718 | 365.6589 | 324.6281 | 155.4273 | 187.9692 | 127.1692
897.3167 | 316.1999 | 158.0356 | 333.2091 | 366.3226 | 325.1174 | 155.7781 | 188.2996 | 127.4251
898.3167 | 314.8216 | 158.1582 | 333.4896 | 367.4775 | 325.9561 | 156.1287 | 188.6217 | 127.6528
899.3167 | 314.8702 | 158.3093 | 334.8613 | 368.0178 | 327.5847 | 156.4144 | 188.9148 | 127.8875
900.3167 | 314.9975 | 158.4535 | 336.368 | 368.5778 | 327.8794 | 156.7395 | 189.2324 | 128.1218
901.3167 | 314.5421 | 158.6232 | 336.641 | 367.7284 | 328.8979 | 157.1008 | 189.542 | 128.371
902.3167 | 313.8061 | 158.7764 | 336.4707 | 367.2206 | 328.8726 | 157.4516 | 189.8418 | 128.6085
903.3167 | 313.3364 | 158.9247 | 337.2478 | 367.3503 | 329.6498 | 157.7923 | 190.1527 | 128.8385
904.3167 | 314.5379 | 159.0584 | 339.4573 | 368.2087 | 329.6042 | 158.0333 | 190.4712 | 129.0759
905.3167 | 316.1559 | 159.1943 | 340.1954 | 369.2252 | 331.9658 | 158.1948 | 190.7455 | 129.2991
906.3167 | 317.3375 | 159.3315 | 342.1516 | 370.1305 | 334.5529 | 158.6276 | 191.078 | 129.5735
907.3167 | 317.5889 | 159.4507 | 343.8876 | 371.3459 | 335.7415 | 159.0117 | 191.3869 | 129.7943
908.3167 | 317.3862 | 159.5784 | 343.3581 | 371.1315 | 335.0016 | 159.4086 | 191.6876 | 129.9894
909.3167 | 317.7014 | 159.688 | 343.1706 | 370.3599 | 333.5978 | 159.5695 | 191.9932 | 130.2509
910.3167 | 316.9113 | 159.7923 | 344.3285 | 370.4982 | 334.5379 | 159.9092 | 192.3096 | 130.4609
911.3167 | 317.0735 | 159.8569 | 342.9046 | 369.7801 | 335.3634 | 160.2279 | 192.6116 | 130.7063
912.3167 | 317.2826 | 159.9619 | 343.5617 | 369.3694 | 335.4263 | 160.4668 | 192.925 | 130.9594
913.3167 | 318.9995 | 160.0678 | 345.4784 | 371.0323 | 336.2188 | 160.7958 | 193.2336 | 131.2285
914.3167 | 319.7881 | 160.1599 | 346.4073 | 372.1672 | 335.8072 | 161.1229 | 193.5188 | 131.5017
915.3167 | 319.7038 | 160.2621 | 347.6397 | 373.3227 | 334.9815 | 161.4621 | 193.8578 | 131.7374
916.3167 | 320.8541 | 160.3513 | 348.3487 | 374.2626 | 334.6511 | 161.8144 | 194.1455 | 131.9849
917.3167 | 321.5109 | 160.4565 | 349.5949 | 375.1489 | 335.2378 | 162.1464 | 194.4761 | 132.2326
918.3167 | 321.968 | 160.5224 | 349.6868 | 376.2211 | 336.4975 | 162.4978 | 194.7798 | 132.4636
919.3167 | 324.8034 | 160.6405 | 350.796 | 376.6531 | 337.1619 | 162.8563 | 195.0915 | 132.6854
920.3167 | 326.0508 | 160.7507 | 352.0975 | 378.422 | 338.541 | 163.2122 | 195.398 | 132.9246
921.3167 | 326.4593 | 160.8632 | 352.8924 | 378.6948 | 339.882 | 163.5718 | 195.7049 | 133.1518
922.3167 | 326.6009 | 160.987 | 354.7863 | 379.8349 | 341.4715 | 163.958 | 196.0259 | 133.3869
923.3167 | 327.3235 | 161.0974 | 356.4389 | 380.7633 | 342.7287 | 164.351 | 196.3312 | 133.6425
924.3167 | 328.9136 | 161.1942 | 356.9845 | 383.3596 | 343.4058 | 164.7914 | 196.6387 | 133.9389
925.3167 | 329.1175 | 161.3136 | 357.5606 | 384.5776 | 343.2168 | 165.0525 | 196.9417 | 134.1878
926.3167 | 328.3418 | 161.4276 | 356.5442 | 384.7723 | 341.8922 | 165.4649 | 197.2525 | 134.4244
927.3167 | 329.1705 | 161.532 | 355.647 | 384.1238 | 340.0114 | 165.8302 | 197.5465 | 134.6626
928.3167 | 329.8607 | 161.6444 | 356.9058 | 385.6342 | 339.5918 | 166.1661 | 197.8488 | 134.9069
929.3167 | 330.6622 | 161.7681 | 357.9727 | 386.0179 | 340.1516 | 166.5643 | 198.1587 | 135.1552
930.3167 | 331.3448 | 161.8816 | 358.916 | 386.4037 | 340.2013 | 166.9802 | 198.4612 | 135.3986
931.3167 | 330.2623 | 162.0001 | 360.7825 | 387.2645 | 341.8916 | 167.441 | 198.743 | 135.6511
932.3167 | 330.87 | 162.1136 | 362.3428 | 389.6553 | 342.0882 | 167.8707 | 199.0487 | 135.8968
933.3167 | 332.1757 | 162.2248 | 362.4174 | 391.8679 | 343.4527 | 168.2714 | 199.3459 | 136.1462
934.3167 | 332.6693 | 162.3292 | 361.5655 | 391.7332 | 343.7546 | 168.7 | 199.6396 | 136.387
935.3167 | 332.4989 | 162.4521 | 359.6899 | 391.1701 | 343.6614 | 169.1019 | 199.9606 | 136.6651
936.3167 | 331.8376 | 162.5681 | 358.9678 | 390.845 | 343.3082 | 169.5139 | 200.2643 | 136.9203
937.3167 | 330.7656 | 162.6784 | 358.1234 | 389.8012 | 342.5899 | 169.8966 | 200.5934 | 137.1658
938.3167 | 332.0567 | 162.7973 | 359.2898 | 391.1971 | 342.2093 | 170.3047 | 200.8962 | 137.3993
939.3167 | 331.7169 | 162.9142 | 360.6669 | 391.7463 | 342.2264 | 170.7126 | 201.2358 | 137.6585
940.3167 | 332.647 | 163.0387 | 361.8213 | 391.3079 | 341.7383 | 171.1931 | 201.5109 | 137.91
941.3167 | 332.6298 | 163.1623 | 362.8741 | 391.665 | 341.7049 | 171.6147 | 201.8335 | 138.1752
942.3167 | 333.0467 | 163.2776 | 363.1556 | 391.5659 | 340.4772 | 171.9751 | 202.1281 | 138.4227
943.3167 | 332.8739 | 163.3884 | 362.9088 | 391.1733 | 341.8083 | 172.4512 | 202.4262 | 138.6517
944.3167 | 332.9089 | 163.5042 | 362.4962 | 391.4199 | 342.8877 | 172.9242 | 202.7421 | 138.9255
945.3167 | 333.426 | 163.6178 | 361.7264 | 392.4246 | 343.0759 | 173.4859 | 203.0371 | 139.1841
946.3167 | 334.6054 | 163.7347 | 362.2107 | 392.6084 | 345.1659 | 173.5861 | 203.3467 | 139.4641
947.3167 | 335.829 | 163.8521 | 361.576 | 393.2443 | 344.911 | 173.9655 | 203.6796 | 139.7138
948.3167 | 337.2327 | 163.9694 | 362.2355 | 394.2321 | 344.649 | 174.1902 | 204.006 | 139.9605
949.3167 | 337.7425 | 164.0844 | 362.0901 | 394.8802 | 344.5592 | 174.5916 | 204.3245 | 140.2133
950.3167 | 337.7295 | 164.1951 | 361.9309 | 395.425 | 343.8827 | 174.8562 | 204.6465 | 140.4835
951.3167 | 338.97 | 164.3094 | 362.9476 | 395.8441 | 343.0292 | 175.2021 | 204.9497 | 140.7312
952.3167 | 339.4878 | 164.4288 | 363.0329 | 397.231 | 342.3421 | 175.5687 | 205.2299 | 140.9853
953.3167 | 340.3877 | 164.5402 | 363.5887 | 398.2956 | 343.847 | 175.9399 | 205.5462 | 141.2437
954.3167 | 340.4347 | 164.6448 | 364.5783 | 398.9429 | 345.5951 | 176.3248 | 205.8412 | 141.5279
955.3167 | 340.5064 | 164.7699 | 364.7509 | 399.6481 | 347.5036 | 176.8529 | 206.134 | 141.8177
956.3167 | 340.68 | 164.8902 | 364.6742 | 400.2916 | 349.3668 | 177.2254 | 206.4243 | 142.0496
957.3167 | 340.8956 | 165.0001 | 365.7718 | 400.3682 | 350.2651 | 177.3194 | 206.7135 | 142.3258
958.3167 | 342.199 | 165.1152 | 365.9374 | 400.3273 | 350.9243 | 177.6671 | 207.0269 | 142.626
959.3167 | 342.1756 | 165.2172 | 364.7121 | 400.1085 | 352.7843 | 178.1303 | 207.3287 | 142.8766
960.3167 | 342.7807 | 165.3507 | 365.0761 | 400.53 | 354.0514 | 178.3579 | 207.6519 | 143.1458
961.3167 | 343.0981 | 165.457 | 366.5604 | 400.7758 | 354.6998 | 178.678 | 207.9808 | 143.4245
962.3167 | 344.44 | 165.5863 | 366.0026 | 402.0731 | 353.9528 | 179.0106 | 208.3043 | 143.6919
963.3167 | 344.1481 | 165.6987 | 364.7185 | 402.9398 | 353.8174 | 179.3307 | 208.6459 | 143.9524
964.3167 | 344.5273 | 165.8159 | 365.1895 | 402.9486 | 354.3934 | 179.6677 | 208.9551 | 144.2192
965.3167 | 345.1306 | 165.9383 | 365.7417 | 403.4899 | 354.4036 | 180.0161 | 209.2621 | 144.504
966.3167 | 345.478 | 166.0515 | 364.7275 | 403.4599 | 353.5522 | 180.3403 | 209.589 | 144.7653
967.3167 | 345.9667 | 166.1747 | 363.3885 | 402.0169 | 354.2411 | 180.6814 | 209.9176 | 145.0306
968.3167 | 346.1309 | 166.2909 | 363.3128 | 401.3839 | 355.6383 | 180.9535 | 210.2119 | 145.3282
969.3167 | 346.9242 | 166.4198 | 363.0153 | 401.3137 | 355.9752 | 181.2691 | 210.5165 | 145.6152
970.3167 | 347.1739 | 166.5322 | 362.0496 | 401.1699 | 356.0333 | 181.5619 | 210.8367 | 145.8816
971.3167 | 347.3543 | 166.6465 | 362.4399 | 401.038 | 355.7904 | 181.8987 | 211.1545 | 146.1364
972.3167 | 347.3552 | 166.7669 | 363.7319 | 401.4732 | 354.4815 | 182.2267 | 211.485 | 146.4294
973.3167 | 347.8578 | 166.8888 | 364.6527 | 401.8578 | 354.9557 | 182.6059 | 211.7746 | 146.6971
974.3167 | 348.0491 | 167.0151 | 364.5971 | 402.3075 | 354.653 | 182.9796 | 212.0903 | 146.9726
975.3167 | 347.293 | 167.1407 | 364.038 | 401.8397 | 353.5891 | 183.313 | 212.4225 | 147.2557
976.3167 | 346.434 | 167.2475 | 364.0288 | 402.198 | 354.619 | 183.6581 | 212.7491 | 147.5256
977.3167 | 346.6724 | 167.3747 | 363.8196 | 403.2982 | 355.4334 | 184.0187 | 213.0675 | 147.8078
978.3167 | 347.7134 | 167.4932 | 363.9298 | 404.0697 | 356.5915 | 184.3819 | 213.3567 | 148.0832
979.3167 | 348.5668 | 167.6075 | 363.9479 | 404.1977 | 357.9571 | 184.7413 | 213.7016 | 148.3717
980.3167 | 349.1739 | 167.7305 | 364.1129 | 404.3866 | 358.194 | 185.0828 | 214.0123 | 148.6486
981.3167 | 349.5935 | 167.8512 | 364.7584 | 404.202 | 358.5295 | 185.4178 | 214.3307 | 148.9469
982.3167 | 349.5648 | 167.9712 | 364.6938 | 404.5281 | 359.4517 | 185.7369 | 214.6456 | 149.2243
983.3167 | 349.1109 | 168.0839 | 364.5167 | 405.2767 | 361.4412 | 186.0866 | 214.9585 | 149.5016
984.3167 | 348.87 | 168.2053 | 363.7401 | 405.7019 | 361.6311 | 186.4047 | 215.2631 | 149.7946
985.3167 | 350.0856 | 168.333 | 364.3728 | 406.3696 | 361.3282 | 186.7022 | 215.572 | 150.0502
986.3167 | 349.763 | 168.4495 | 364.1851 | 406.8208 | 361.808 | 187.0255 | 215.9233 | 150.3153
987.3167 | 349.3148 | 168.5574 | 364.6159 | 407.6413 | 362.5158 | 187.3427 | 216.2235 | 150.5916
988.3167 | 350.4826 | 168.6801 | 364.3702 | 408.3243 | 362.3712 | 187.6464 | 216.5328 | 150.8907
989.3167 | 352.0496 | 168.7988 | 364.0265 | 408.2516 | 362.3071 | 187.9526 | 216.8801 | 151.156
990.3167 | 352.4366 | 168.9165 | 364.2445 | 408.1171 | 362.328 | 188.2536 | 217.208 | 151.4222
991.3167 | 351.5116 | 169.0386 | 363.5431 | 407.3981 | 361.0483 | 188.612 | 217.5465 | 151.6905
992.3167 | 350.7336 | 169.1495 | 364.1175 | 407.7743 | 361.6819 | 188.962 | 217.88 | 151.9644
993.3167 | 349.7219 | 169.2608 | 363.7146 | 407.0246 | 361.9499 | 189.3072 | 218.1989 | 152.2746
994.3167 | 350.363 | 169.3831 | 363.5287 | 406.4001 | 360.8825 | 189.6484 | 218.5092 | 152.5491
995.3167 | 351.3722 | 169.5037 | 362.6163 | 405.9803 | 359.424 | 189.989 | 218.8162 | 152.8084
996.3167 | 351.719 | 169.6244 | 362.4291 | 405.9178 | 358.4891 | 190.2244 | 219.1222 | 153.0713
997.3167 | 352.8376 | 169.7318 | 362.3123 | 405.9206 | 358.3878 | 190.4899 | 219.4289 | 153.3419
998.3167 | 352.6996 | 169.8482 | 362.3578 | 406.088 | 358.7975 | 190.7912 | 219.7382 | 153.6136
999.3167 | 351.039 | 169.9642 | 362.2184 | 405.7957 | 358.4856 | 191.1413 | 220.0338 | 153.918
1000.3167 | 350.2308 | 170.0763 | 361.5654 | 404.701 | 358.2381 | 191.4252 | 220.3623 | 154.2146
1001.3167 | 350.9819 | 170.194 | 362.407 | 404.8529 | 358.12 | 191.7545 | 220.6609 | 154.449
1002.3167 | 352.1647 | 170.2964 | 363.8024 | 405.4181 | 359.3736 | 192.0451 | 220.9986 | 154.742
1003.3167 | 352.1368 | 170.4196 | 364.5421 | 405.8507 | 360.8414 | 192.2887 | 221.3252 | 155.0013
1004.3167 | 353.6512 | 170.5331 | 366.1011 | 407.5561 | 362.3283 | 192.5899 | 221.6649 | 155.2803
1005.3167 | 356.7137 | 170.6566 | 367.204 | 409.7792 | 363.9343 | 192.9069 | 221.9974 | 155.5859
1006.3167 | 356.8723 | 170.7676 | 368.2585 | 409.9086 | 364.1025 | 193.1963 | 222.3255 | 155.8512
1007.3167 | 357.4378 | 170.8838 | 367.3106 | 410.4136 | 364.8712 | 193.502 | 222.6311 | 156.1239
1008.3167 | 358.9423 | 170.9978 | 366.7915 | 409.7729 | 364.2037 | 193.7768 | 222.9451 | 156.3632
1009.3167 | 358.1474 | 171.1085 | 365.7592 | 409.0999 | 363.2235 | 194.0579 | 223.2696 | 156.657
1010.3167 | 356.6247 | 171.2218 | 366.1244 | 409.0934 | 362.359 | 194.377 | 223.579 | 156.9408
1011.3167 | 357.3743 | 171.3272 | 366.2637 | 408.9719 | 361.7389 | 194.7137 | 223.898 | 157.2392
1012.3167 | 357.2172 | 171.4462 | 367.5069 | 409.311 | 360.7886 | 195.0256 | 224.1992 | 157.4987
1013.3167 | 358.6362 | 171.5518 | 369.3882 | 409.7944 | 360.5877 | 195.3792 | 224.5511 | 157.7812
1014.3167 | 358.7537 | 171.6687 | 370.0543 | 410.1354 | 361.5058 | 195.6696 | 224.8479 | 158.0507
1015.3167 | 358.6931 | 171.7865 | 369.376 | 409.7888 | 361.9544 | 195.996 | 225.1822 | 158.3155
1016.3167 | 356.9026 | 171.899 | 369.4606 | 411.1428 | 361.3249 | 196.2682 | 225.5005 | 158.591
1017.3167 | 355.2742 | 172.0098 | 370.1645 | 410.2145 | 360.4453 | 196.5663 | 225.8507 | 158.87
1018.3167 | 355.4501 | 172.1342 | 371.126 | 410.8264 | 359.8864 | 196.8518 | 226.1744 | 159.1492
1019.3167 | 354.9631 | 172.2478 | 371.6554 | 410.9876 | 360.0133 | 197.1947 | 226.5003 | 159.4111
1020.3167 | 356.2921 | 172.3691 | 371.6802 | 413.166 | 359.8191 | 197.4315 | 226.8262 | 159.7047
1021.3167 | 355.8717 | 172.4843 | 373.7616 | 412.4164 | 360.7305 | 197.7404 | 227.1477 | 160.0009
1022.3167 | 354.8647 | 172.6037 | 371.5322 | 410.7414 | 359.6803 | 198.0571 | 227.4674 | 160.2753
1023.3167 | 354.202 | 172.7266 | 369.4752 | 408.9059 | 358.3349 | 198.3453 | 227.7792 | 160.5513
1024.3167 | 354.185 | 172.83 | 369.6165 | 407.7105 | 356.4394 | 198.6431 | 228.0938 | 160.8199
1025.3167 | 354.1024 | 172.9494 | 369.5689 | 406.9566 | 356.8141 | 198.939 | 228.4219 | 161.0986
1026.3167 | 355.2362 | 173.0759 | 368.5639 | 406.2261 | 356.68 | 199.2358 | 228.7284 | 161.3926
1027.3167 | 354.6663 | 173.1908 | 368.5968 | 406.0483 | 358.0105 | 199.576 | 229.0853 | 161.6671
1028.3167 | 354.9733 | 173.31 | 366.4705 | 404.9058 | 357.2359 | 199.9161 | 229.4406 | 161.9243
1029.3167 | 355.7723 | 173.4221 | 364.3401 | 403.3487 | 356.89 | 200.2429 | 229.7842 | 162.2035
1030.3167 | 354.5265 | 173.5501 | 363.3594 | 402.4758 | 355.7602 | 200.531 | 230.1098 | 162.5051
1031.3167 | 354.0633 | 173.6607 | 363.4645 | 400.8733 | 353.7171 | 200.8334 | 230.463 | 162.7955
1032.3167 | 354.3424 | 173.7719 | 367.5809 | 401.6276 | 352.2307 | 201.187 | 230.7774 | 163.0635
1033.3167 | 354.5404 | 173.8987 | 368.9002 | 402.3791 | 351.6217 | 201.4914 | 231.0659 | 163.3353
1034.3167 | 356.6395 | 174.0153 | 371.496 | 402.6802 | 351.149 | 201.7271 | 231.393 | 163.6052
1035.3167 | 354.4824 | 174.1212 | 373.6963 | 404.3996 | 351.8222 | 202.053 | 231.727 | 163.8868
1036.3167 | 357.5563 | 174.2422 | 377.5597 | 407.0483 | 352.9474 | 202.4495 | 232.0229 | 164.1433
1037.3167 | 356.4585 | 174.3616 | 379.5488 | 408.169 | 352.8319 | 202.7726 | 232.3273 | 164.4255
1038.3167 | 356.289 | 174.4793 | 379.7877 | 407.8213 | 351.4975 | 203.1031 | 232.6494 | 164.6881
1039.3167 | 355.4838 | 174.5853 | 379.5224 | 407.5872 | 351.0235 | 203.4034 | 232.9688 | 164.9677
1040.3167 | 358.6234 | 174.7024 | 379.5174 | 408.4227 | 351.4395 | 203.7339 | 233.2959 | 165.2539
1041.3167 | 356.8936 | 174.8245 | 380.0402 | 409.9941 | 353.1087 | 204.063 | 233.584 | 165.5345
1042.3167 | 359.2888 | 174.9354 | 379.5627 | 409.6572 | 352.5631 | 204.3699 | 233.8909 | 165.7971
1043.3167 | 357.6947 | 175.0506 | 379.2339 | 409.8831 | 351.2128 | 204.6873 | 234.2158 | 166.0846
1044.3167 | 356.708 | 175.1673 | 380.7717 | 410.2769 | 351.6001 | 205.0089 | 234.525 | 166.3672
1045.3167 | 356.5466 | 175.2864 | 380.7824 | 409.3045 | 351.155 | 205.3194 | 234.8317 | 166.6183
1046.3167 | 356.1422 | 175.3969 | 379.6863 | 407.8701 | 350.2174 | 205.6454 | 235.1581 | 166.9097
1047.3167 | 355.7668 | 175.4989 | 378.5294 | 406.7772 | 349.0247 | 205.9537 | 235.4737 | 167.1857
1048.3167 | 355.3355 | 175.6133 | 377.9756 | 404.5688 | 347.4405 | 206.2558 | 235.7987 | 167.4524
1049.3167 | 356.322 | 175.7257 | 375.2561 | 402.7878 | 345.8915 | 206.5634 | 236.1203 | 167.7081
1050.3167 | 357.1254 | 175.8471 | 373.5933 | 402.1737 | 344.8961 | 206.7984 | 236.4014 | 167.9783
1051.3167 | 355.6711 | 175.9749 | 372.8818 | 401.0557 | 344.2606 | 207.0846 | 236.746 | 168.2768
1052.3167 | 354.5347 | 176.0801 | 372.5917 | 400.1815 | 343.8961 | 207.3732 | 237.0538 | 168.5416
1053.3167 | 356.6626 | 176.1997 | 373.2157 | 400.2668 | 343.2094 | 207.6914 | 237.3823 | 168.8329
1054.3167 | 356.9297 | 176.315 | 372.0986 | 399.7226 | 342.7545 | 207.9587 | 237.6747 | 169.1014
1055.3167 | 355.3575 | 176.4361 | 369.7452 | 398.4232 | 342.4241 | 208.2033 | 238.0103 | 169.3972
1056.3167 | 355.5022 | 176.5321 | 367.5522 | 397.2842 | 342.6396 | 208.5005 | 238.3119 | 169.682
1057.3167 | 355.6431 | 176.6545 | 365.9283 | 396.0708 | 342.0653 | 208.788 | 238.629 | 169.942
1058.3167 | 354.7258 | 176.7734 | 364.8096 | 395.4278 | 342.1082 | 209.0581 | 238.9428 | 170.2074
1059.3167 | 353.299 | 176.8957 | 363.7476 | 394.324 | 341.4147 | 209.3096 | 239.2655 | 170.4751
1060.3167 | 352.437 | 177.0062 | 362.8795 | 393.9679 | 341.0783 | 209.5324 | 239.5956 | 170.7917
1061.3167 | 353.2894 | 177.1217 | 363.3047 | 394.6426 | 340.0414 | 209.7414 | 239.8954 | 171.0724
1062.3167 | 353.6197 | 177.2253 | 363.9179 | 394.7364 | 339.1625 | 210.0272 | 240.2235 | 171.3826
1063.3167 | 352.6208 | 177.3345 | 364.1845 | 393.9898 | 338.2708 | 210.3008 | 240.5421 | 171.6632
1064.3167 | 350.79 | 177.4391 | 364.2982 | 393.0885 | 337.7419 | 210.553 | 240.8594 | 171.9502
1065.3167 | 351.0457 | 177.555 | 364.3029 | 393.6839 | 337.812 | 210.8815 | 241.1651 | 172.2201
1066.3167 | 351.2354 | 177.6798 | 363.7182 | 393.9735 | 337.5946 | 210.9569 | 241.5135 | 172.4965
1067.3167 | 350.4193 | 177.7912 | 363.4694 | 393.2614 | 336.7113 | 211.2547 | 241.8295 | 172.7566
1068.3167 | 350.4053 | 177.9003 | 363.8675 | 392.8066 | 335.9 | 211.4237 | 242.1257 | 173.036
1069.3167 | 347.7307 | 178.0212 | 364.3141 | 391.0674 | 335.7375 | 211.637 | 242.4439 | 173.2775
1070.3167 | 349.3936 | 178.1418 | 363.2733 | 390.0812 | 334.5932 | 211.8625 | 242.7732 | 173.5617
1071.3167 | 349.0225 | 178.245 | 362.5175 | 390.3238 | 334.6046 | 212.1472 | 243.1427 | 173.8168
1072.3167 | 348.4538 | 178.3492 | 363.7895 | 390.2603 | 334.0853 | 212.407 | 243.4542 | 174.0903
1073.3167 | 348.5774 | 178.4573 | 364.9588 | 391.165 | 333.872 | 212.691 | 243.7762 | 174.3623
1074.3167 | 347.5854 | 178.5667 | 365.3985 | 391.406 | 333.8641 | 212.8735 | 244.1017 | 174.6334
1075.3167 | 347.1371 | 178.6856 | 366.7753 | 391.0701 | 333.9234 | 213.0947 | 244.4545 | 174.9264
1076.3167 | 348.6798 | 178.8019 | 366.9832 | 391.024 | 333.77 | 213.3982 | 244.7762 | 175.2061
1077.3167 | 349.0216 | 178.9142 | 365.5146 | 390.5938 | 333.4458 | 213.6233 | 245.096 | 175.4773
1078.3167 | 348.4862 | 179.0204 | 364.0701 | 389.9436 | 333.7915 | 213.7907 | 245.4167 | 175.7433
1079.3167 | 348.2215 | 179.1367 | 364.3113 | 389.2219 | 333.9837 | 214.022 | 245.7173 | 176.0168
1080.3167 | 349.2043 | 179.2471 | 364.8689 | 390.3012 | 333.6737 | 214.2885 | 246.0419 | 176.2728
1081.3167 | 349.5601 | 179.3684 | 365.3574 | 391.1885 | 333.6042 | 214.542 | 246.3406 | 176.5423
1082.3167 | 350.001 | 179.4869 | 365.9628 | 391.0373 | 333.9851 | 214.7664 | 246.6394 | 176.8201
1083.3167 | 350.4503 | 179.5913 | 364.8263 | 390.4588 | 333.7894 | 215.0016 | 246.9329 | 177.0865
1084.3167 | 351.301 | 179.71 | 364.7755 | 390.6737 | 334.8213 | 215.2275 | 247.2559 | 177.3253
1085.3167 | 349.6743 | 179.8224 | 364.044 | 389.6921 | 334.7161 | 215.4603 | 247.5625 | 177.5851
1086.3167 | 350.6334 | 179.9275 | 363.3767 | 388.5711 | 334.3079 | 215.6446 | 247.8896 | 177.847
1087.3167 | 350.6891 | 180.0181 | 363.1251 | 387.6829 | 334.0289 | 215.8503 | 248.2278 | 178.1042
1088.3167 | 350.2923 | 180.1235 | 363.3402 | 388.4056 | 333.5071 | 216.0526 | 248.5321 | 178.3628
1089.3167 | 348.7381 | 180.2424 | 363.0722 | 387.7618 | 332.6878 | 216.2672 | 248.8527 | 178.6247
1090.3167 | 349.2791 | 180.3524 | 362.64 | 386.457 | 332.0135 | 216.5034 | 249.149 | 178.8593
1091.3167 | 348.7688 | 180.4588 | 361.4848 | 385.3331 | 331.7724 | 216.6777 | 249.4624 | 179.0886
1092.3167 | 348.83 | 180.5765 | 362.3619 | 385.319 | 332.1232 | 216.9597 | 249.7469 | 179.3335
1093.3167 | 348.991 | 180.691 | 362.936 | 386.0434 | 332.8512 | 217.2629 | 250.0653 | 179.589
1094.3167 | 348.7449 | 180.8029 | 361.595 | 385.1165 | 332.1313 | 217.5015 | 250.3671 | 179.8212
1095.3167 | 348.7141 | 180.9312 | 362.8478 | 385.8793 | 331.5437 | 217.7352 | 250.6573 | 180.0468
1096.3167 | 348.8319 | 181.0401 | 365.1991 | 386.8581 | 332.2799 | 217.9699 | 250.9472 | 180.2738
1097.3167 | 349.3962 | 181.1603 | 366.795 | 388.2273 | 333.5421 | 218.2373 | 251.2579 | 180.5384
1098.3167 | 349.7956 | 181.275 | 367.3582 | 388.5846 | 334.1246 | 218.4935 | 251.574 | 180.7742
1099.3167 | 349.4199 | 181.3952 | 367.7081 | 388.7244 | 333.8563 | 218.7547 | 251.8771 | 181.0247
1100.3167 | 348.8472 | 181.5126 | 368.8518 | 388.764 | 334.0478 | 218.9969 | 252.1677 | 181.2546
1101.3167 | 348.276 | 181.6295 | 369.5673 | 388.7632 | 334.1814 | 219.3085 | 252.483 | 181.5069
1102.3167 | 347.8966 | 181.744 | 369.4543 | 388.9266 | 333.9138 | 219.5585 | 252.7965 | 181.7449
1103.3167 | 348.7047 | 181.8628 | 370.8104 | 389.0026 | 334.328 | 219.8144 | 253.1102 | 181.9636
1104.3167 | 348.7872 | 181.9734 | 373.7097 | 390.4612 | 334.5902 | 220.141 | 253.43 | 182.1809
1105.3167 | 349.3635 | 182.094 | 374.6956 | 391.0452 | 335.6702 | 220.4078 | 253.7438 | 182.4402
1106.3167 | 348.9827 | 182.2083 | 374.6887 | 391.0243 | 335.2983 | 220.7057 | 254.0376 | 182.6593
1107.3167 | 348.1999 | 182.3193 | 372.9436 | 389.8074 | 334.6121 | 220.9644 | 254.3279 | 182.894
1108.3167 | 348.3015 | 182.4417 | 371.498 | 390.138 | 334.1062 | 221.1958 | 254.6291 | 183.136
1109.3167 | 348.5837 | 182.5614 | 370.4948 | 389.7535 | 334.4871 | 221.436 | 254.9534 | 183.3601
1110.3167 | 348.1882 | 182.6819 | 368.6718 | 389.023 | 334.2052 | 221.6696 | 255.2613 | 183.5763
1111.3167 | 347.5791 | 182.7915 | 366.9318 | 388.5274 | 334.725 | 221.9083 | 255.5648 | 183.8364
1112.3167 | 346.6783 | 182.9208 | 366.2977 | 387.9675 | 335.3526 | 222.1421 | 255.8527 | 184.0734
1113.3167 | 345.9233 | 183.0419 | 366.5937 | 387.2442 | 334.6427 | 222.4004 | 256.1349 | 184.294
1114.3167 | 346.4559 | 183.1567 | 365.3772 | 386.6358 | 333.8527 | 222.6422 | 256.4443 | 184.5652
1115.3167 | 345.6524 | 183.2645 | 363.4906 | 385.7756 | 332.7184 | 222.8766 | 256.7464 | 184.8282
1116.3167 | 344.3738 | 183.3951 | 363.0755 | 385.6032 | 332.1564 | 223.0812 | 257.0415 | 185.0854
1117.3167 | 345.1987 | 183.5163 | 362.9264 | 386.2274 | 332.231 | 223.3341 | 257.332 | 185.3343
1118.3167 | 344.8737 | 183.625 | 362.5159 | 385.6178 | 331.7272 | 223.5759 | 257.6418 | 185.5657
1119.3167 | 343.7802 | 183.7463 | 362.0544 | 384.4742 | 331.3047 | 223.8071 | 257.9296 | 185.7983
1120.3167 | 343.0149 | 183.8599 | 362.8131 | 384.2518 | 330.8191 | 224.0294 | 258.2383 | 186.0267
1121.3167 | 343.1758 | 183.9632 | 360.4106 | 383.3714 | 330.7533 | 224.273 | 258.5374 | 186.2581
1122.3167 | 343.8306 | 184.0864 | 358.4021 | 383.6034 | 331.124 | 224.4955 | 258.8395 | 186.4915
1123.3167 | 343.0019 | 184.2155 | 357.2281 | 382.9084 | 330.1744 | 224.7166 | 259.1399 | 186.7556
1124.3167 | 342.6513 | 184.3345 | 357.9946 | 382.5673 | 329.0491 | 224.9202 | 259.4156 | 187.0068
1125.3167 | 342.0811 | 184.4539 | 357.6637 | 381.8856 | 328.2644 | 225.1456 | 259.7081 | 187.228
1126.3167 | 341.9758 | 184.5742 | 358.5635 | 381.6713 | 328.1967 | 225.3492 | 260.0161 | 187.4736
1127.3167 | 340.6166 | 184.6789 | 358.9268 | 381.8303 | 328.4561 | 225.5715 | 260.3116 | 187.7165
1128.3167 | 340.4839 | 184.8073 | 359.9246 | 381.4399 | 328.3222 | 225.7795 | 260.602 | 187.9416
1129.3167 | 340.2584 | 184.9203 | 359.1285 | 380.4503 | 328.0992 | 225.9968 | 260.9082 | 188.197
1130.3167 | 339.2503 | 185.041 | 357.8349 | 378.9282 | 327.9788 | 226.1792 | 261.2173 | 188.4707
1131.3167 | 338.4148 | 185.1627 | 356.6048 | 377.6352 | 327.2962 | 226.4031 | 261.4971 | 188.6421
1132.3167 | 339.557 | 185.2841 | 356.62 | 376.894 | 326.633 | 226.5497 | 261.8188 | 188.8829
1133.3167 | 339.9683 | 185.3964 | 356.7215 | 377.2072 | 326.5498 | 226.8023 | 262.1146 | 189.1363
1134.3167 | 339.9636 | 185.4934 | 356.5792 | 377.4009 | 326.8759 | 227.0187 | 262.3936 | 189.5465
1135.3167 | 340.7481 | 185.6195 | 357.965 | 378.6568 | 327.0562 | 227.1537 | 262.6827 | 189.7872
1136.3167 | 341.2882 | 185.7348 | 360.0247 | 379.9507 | 329.086 | 227.395 | 262.9586 | 190.031
1137.3167 | 340.5286 | 185.8521 | 360.3685 | 379.8133 | 330.1472 | 227.6537 | 263.2373 | 190.2522
1138.3167 | 340.7519 | 185.9656 | 362.1542 | 379.9139 | 330.2154 | 227.8442 | 263.5257 | 190.4873
1139.3167 | 341.1438 | 186.0868 | 362.1995 | 379.546 | 330.348 | 228.1168 | 263.8053 | 190.7119
1140.3167 | 341.2073 | 186.2022 | 362.5194 | 380.5957 | 329.919 | 228.3542 | 264.0901 | 190.9641
1141.3167 | 341.5182 | 186.3181 | 364.0379 | 380.8209 | 329.6568 | 228.5915 | 264.3715 | 191.1993
1142.3167 | 341.7103 | 186.4404 | 363.1415 | 380.0601 | 329.3476 | 228.8283 | 264.6407 | 191.4431
1143.3167 | 341.3868 | 186.5679 | 362.1666 | 378.8295 | 329.0386 | 229.0647 | 264.9325 | 191.679
1144.3167 | 341.0622 | 186.6884 | 360.6673 | 377.5339 | 328.1747 | 229.2792 | 265.2123 | 191.9298
1145.3167 | 340.3198 | 186.8094 | 358.5948 | 376.2671 | 327.9997 | 229.4537 | 265.4988 | 192.1651
1146.3167 | 339.5726 | 186.9186 | 356.5977 | 375.2713 | 328.5434 | 229.6774 | 265.7659 | 192.3872
1147.3167 | 338.2963 | 187.0364 | 356.0941 | 374.9465 | 328.4063 | 229.9017 | 266.0458 | 192.6224
1148.3167 | 338.1276 | 187.1541 | 355.5927 | 373.9773 | 328.1546 | 230.0713 | 266.3082 | 192.8399
1149.3167 | 337.2346 | 187.2717 | 354.6883 | 372.4493 | 327.5126 | 230.2696 | 266.5958 | 193.0675
1150.3167 | 336.71 | 187.3864 | 353.9022 | 371.1786 | 326.5092 | 230.4809 | 266.8589 | 193.3407
1151.3167 | 337.0966 | 187.5087 | 353.111 | 370.6515 | 325.5316 | 230.6425 | 267.1405 | 193.567
1152.3167 | 336.9892 | 187.6172 | 352.2208 | 369.236 | 325.1166 | 230.8565 | 267.419 | 193.8103
1153.3167 | 337.0548 | 187.7373 | 350.7114 | 370.3078 | 325.1916 | 231.0502 | 267.6711 | 194.0373
1154.3167 | 337.5789 | 187.8425 | 351.9228 | 371.7358 | 326.382 | 231.2645 | 267.9757 | 194.2845
1155.3167 | 338.3682 | 187.9757 | 352.3602 | 372.6231 | 327.3571 | 231.4654 | 268.2882 | 194.5083
1156.3167 | 338.7065 | 188.0919 | 353.0279 | 373.6314 | 328.4657 | 231.6414 | 268.5308 | 194.744
1157.3167 | 338.7702 | 188.2081 | 351.9353 | 374.046 | 329.3408 | 231.8044 | 268.7894 | 194.9559
1158.3167 | 340.4179 | 188.3116 | 352.8633 | 376.3534 | 330.4258 | 231.9882 | 269.0729 | 195.1114
1159.3167 | 340.8096 | 188.4316 | 353.5495 | 377.7158 | 333.1728 | 232.1235 | 269.3652 | 195.3185
1160.3167 | 340.7616 | 188.5491 | 353.2031 | 377.9095 | 334.1495 | 232.3058 | 269.6215 | 195.5087
1161.3167 | 340.7304 | 188.6706 | 351.8902 | 376.9686 | 334.7166 | 232.4757 | 269.8785 | 195.7679
1162.3167 | 339.6696 | 188.7979 | 350.8962 | 376.357 | 334.1681 | 232.6673 | 270.1478 | 195.9215
1163.3167 | 338.8442 | 188.9179 | 350.6018 | 376.3366 | 333.5259 | 232.8046 | 270.4198 | 196.1318
1164.3167 | 338.6983 | 189.0356 | 350.1116 | 376.4239 | 333.1293 | 232.9484 | 270.6829 | 196.388
1165.3167 | 338.6237 | 189.164 | 350.0092 | 375.6507 | 332.5979 | 233.1126 | 270.9637 | 196.6657
1166.3167 | 338.5138 | 189.2719 | 349.1555 | 374.9993 | 332.5967 | 233.2996 | 271.2135 | 196.9281
1167.3167 | 337.5171 | 189.3888 | 348.7497 | 373.7874 | 331.3204 | 233.4724 | 271.4678 | 197.2041
1168.3167 | 337.2457 | 189.5164 | 349.535 | 373.6621 | 329.9591 | 233.6537 | 271.7352 | 197.4488
1169.3167 | 336.7388 | 189.6346 | 349.3997 | 373.4173 | 329.4638 | 233.8439 | 271.9848 | 197.6636
1170.3167 | 336.0127 | 189.7428 | 348.9425 | 372.8347 | 329.1407 | 234.0484 | 272.2699 | 197.8784
1171.3167 | 335.3298 | 189.8564 | 348.5508 | 372.1902 | 329.3099 | 234.2378 | 272.5182 | 198.1047
1172.3167 | 335.0908 | 189.9704 | 347.9276 | 371.3892 | 329.1734 | 234.439 | 272.7556 | 198.3028
1173.3167 | 334.4279 | 190.0848 | 349.0857 | 371.9504 | 328.9053 | 234.614 | 273.0227 | 198.5326
1174.3167 | 334.1529 | 190.2028 | 349.2126 | 372.2615 | 328.4062 | 234.8132 | 273.2634 | 198.7512
1175.3167 | 333.7252 | 190.3374 | 348.5338 | 371.6222 | 327.6913 | 235.0092 | 273.5382 | 198.9169
1176.3167 | 333.993 | 190.4385 | 349.1469 | 371.2909 | 327.2371 | 235.2266 | 273.7861 | 199.1618
1177.3167 | 333.9014 | 190.5641 | 348.7749 | 370.1614 | 326.9109 | 235.4242 | 274.0401 | 199.3675
1178.3167 | 333.6302 | 190.6953 | 348.6942 | 369.2203 | 326.4743 | 235.5895 | 274.2961 | 199.5706
1179.3167 | 333.7584 | 190.8056 | 349.5699 | 368.3716 | 325.7609 | 235.7736 | 274.5409 | 199.755
1180.3167 | 333.6443 | 190.9228 | 349.2308 | 367.7265 | 325.456 | 235.9625 | 274.808 | 199.9491
1181.3167 | 333.5713 | 191.0472 | 349.1758 | 367.4445 | 325.2234 | 236.1487 | 275.0556 | 200.1767
1182.3167 | 333.9844 | 191.1703 | 348.0463 | 367.2633 | 325.2541 | 236.3303 | 275.3017 | 200.3798
1183.3167 | 334.0074 | 191.2865 | 346.6194 | 365.8303 | 324.3912 | 236.5112 | 275.5255 | 200.6208
1184.3167 | 334.4271 | 191.3989 | 346.7777 | 364.7419 | 323.3085 | 236.6679 | 275.7621 | 200.8386
1185.3167 | 334.2982 | 191.5145 | 346.5036 | 364.4475 | 322.8073 | 236.8385 | 276.0059 | 200.9963
1186.3167 | 334.5925 | 191.6441 | 346.6632 | 363.6853 | 322.1761 | 237.0295 | 276.2536 | 201.2008
1187.3167 | 334.2805 | 191.7671 | 347.7044 | 362.8533 | 321.5767 | 237.1469 | 276.4845 | 201.4229
1188.3167 | 335.121 | 191.8785 | 348.7749 | 362.5258 | 321.4115 | 237.3675 | 276.7287 | 201.6508
1189.3167 | 335.783 | 191.9988 | 348.8211 | 361.9808 | 321.1956 | 237.5991 | 276.965 | 201.8787
1190.3167 | 334.9607 | 192.1139 | 349.4245 | 361.1158 | 321.4589 | 237.7658 | 277.2194 | 202.059
1191.3167 | 334.5525 | 192.2279 | 348.8108 | 360.9329 | 321.0701 | 237.9678 | 277.4362 | 202.2761
1192.3167 | 333.6581 | 192.3429 | 347.606 | 360.5823 | 320.7061 | 238.1186 | 277.6905 | 202.4844
1193.3167 | 333.0283 | 192.4613 | 346.9388 | 360.2246 | 319.9927 | 238.2791 | 277.8967 | 202.7443
1194.3167 | 332.9787 | 192.5858 | 347.7489 | 359.9257 | 319.2249 | 238.4301 | 278.1174 | 202.9499
1195.3167 | 333.0314 | 192.692 | 347.9966 | 359.8359 | 319.5854 | 238.6541 | 278.3631 | 203.1766
1196.3167 | 333.2518 | 192.816 | 348.3859 | 359.7693 | 319.524 | 238.8299 | 278.6107 | 203.3739
1197.3167 | 334.8305 | 192.9395 | 349.8312 | 361.0758 | 320.9143 | 239.0216 | 278.8249 | 203.5902
1198.3167 | 334.8212 | 193.0528 | 351.3478 | 361.4499 | 321.5418 | 239.2123 | 279.0534 | 203.7939
1199.3167 | 335.1401 | 193.1759 | 349.5903 | 361.2323 | 321.3469 | 239.4034 | 279.2894 | 203.9967
1200.3167 | 335.6524 | 193.2889 | 348.1036 | 360.2075 | 320.9625 | 239.5751 | 279.5177 | 204.193
1201.3167 | 335.4547 | 193.406 | 348.0873 | 360.1256 | 320.439 | 239.7354 | 279.7496 | 204.3893
1202.3167 | 335.5282 | 193.5151 | 347.6111 | 359.8061 | 320.422 | 239.9192 | 280 | 204.5668
1203.3167 | 335.119 | 193.6383 | 346.7325 | 359.0669 | 320.1485 | 240.094 | 280.2105 | 204.7387
1204.3167 | 334.1956 | 193.7658 | 346.4545 | 358.3316 | 319.5776 | 240.2571 | 280.4203 | 204.9077
1205.3167 | 334.7502 | 193.8734 | 348.1746 | 360.0779 | 319.9748 | 240.4415 | 280.6647 | 205.1188
1206.3167 | 334.3053 | 193.9985 | 348.1192 | 359.978 | 319.7998 | 240.6426 | 280.8723 | 205.3013
1207.3167 | 334.2419 | 194.1303 | 346.8097 | 359.8487 | 320.0563 | 240.5626 | 281.077 | 205.4865
1208.3167 | 334.2031 | 194.2338 | 345.4781 | 359.4211 | 320.7257 | 240.6704 | 281.2817 | 205.6885
1209.3167 | 333.7831 | 194.346 | 343.5575 | 358.5045 | 321.3517 | 240.8297 | 281.5163 | 205.9259
1210.3167 | 333.6176 | 194.4631 | 341.7154 | 357.8055 | 320.6791 | 241.2304 | 281.7432 | 206.0921
1211.3167 | 333.1683 | 194.5917 | 340.7527 | 356.9771 | 319.781 | 241.3893 | 281.935 | 206.296
1212.3167 | 332.3095 | 194.7062 | 340.8045 | 356.674 | 319.4793 | 241.2321 | 282.1473 | 206.5101
1213.3167 | 332.6283 | 194.8254 | 340.82 | 357.3761 | 319.8296 | 241.1299 | 282.3772 | 206.7182
1214.3167 | 332.3326 | 194.9397 | 339.6741 | 357.8931 | 321.172 | 241.2522 | 282.6066 | 206.9561
1215.3167 | 331.9027 | 195.0684 | 338.2151 | 357.6894 | 322.1449 | 241.4195 | 282.7982 | 207.2358
1216.3167 | 332.323 | 195.1909 | 337.2682 | 357.7861 | 323.5698 | 241.5453 | 283.0069 | 207.4072
1217.3167 | 332.9525 | 195.3136 | 339.3411 | 359.111 | 323.6639 | 241.7156 | 283.1991 | 207.5725
1218.3167 | 333.5125 | 195.4177 | 340.7685 | 359.9244 | 323.3255 | 241.9226 | 283.4286 | 207.79
1219.3167 | 333.8526 | 195.542 | 341.5306 | 359.8023 | 323.1373 | 242.0931 | 283.5975 | 207.9936
1220.3167 | 333.4702 | 195.6681 | 341.9213 | 359.6881 | 322.6033 | 242.2663 | 283.8146 | 208.2316
1221.3167 | 332.6591 | 195.7853 | 341.7752 | 358.9678 | 321.9986 | 242.4635 | 284.0194 | 208.4164
1222.3167 | 331.8821 | 195.9106 | 341.6776 | 358.5927 | 321.5334 | 242.6274 | 284.2261 | 208.6729
1223.3167 | 331.6895 | 196.0139 | 341.4203 | 358.7534 | 321.008 | 242.7422 | 284.4057 | 208.9267
1224.3167 | 331.3152 | 196.1474 | 340.5935 | 358.8127 | 320.6672 | 242.9206 | 284.6228 | 209.1006
1225.3167 | 330.8362 | 196.26 | 340.4335 | 358.6134 | 320.2583 | 243.062 | 284.822 | 209.342
1226.3167 | 330.8005 | 196.3882 | 340.8278 | 358.3199 | 319.9454 | 243.1997 | 285.016 | 209.508
1227.3167 | 330.8313 | 196.5094 | 341.2692 | 358.5055 | 320.6689 | 243.3823 | 285.2253 | 209.7123
1228.3167 | 330.2953 | 196.6302 | 341.1109 | 358.1091 | 320.479 | 243.527 | 285.3954 | 209.8828
1229.3167 | 329.6597 | 196.7476 | 340.1173 | 357.0396 | 319.8178 | 243.6869 | 285.5941 | 210.0708
1230.3167 | 329.9764 | 196.8614 | 338.547 | 355.6382 | 319.3668 | 243.8573 | 285.8032 | 210.2227
1231.3167 | 329.7381 | 196.9896 | 337.1839 | 355.066 | 320.494 | 243.9747 | 286.0008 | 210.4272
1232.3167 | 329.8865 | 197.1132 | 337.7227 | 356.3269 | 322.6546 | 244.0986 | 286.187 | 210.6209
1233.3167 | 329.5947 | 197.2225 | 338.7597 | 357.4225 | 324.1045 | 244.2087 | 286.3778 | 210.8554
1234.3167 | 329.6714 | 197.342 | 339.8496 | 358.2877 | 324.6382 | 244.3361 | 286.587 | 211.0379
1235.3167 | 330.0938 | 197.4679 | 339.7044 | 358.5369 | 324.6009 | 244.4755 | 286.7761 | 211.2206
1236.3167 | 330.2486 | 197.5417 | 338.6336 | 358.0682 | 324.4213 | 244.6192 | 286.9468 | 211.3922
1237.3167 | 330.8754 | 197.6584 | 338.7963 | 359.6905 | 325.2047 | 244.7578 | 287.1572 | 211.5657
1238.3167 | 331.2414 | 197.7844 | 340.1602 | 360.9734 | 325.9866 | 244.9029 | 287.3233 | 211.7614
1239.3167 | 331.0036 | 197.8926 | 340.2302 | 362.4175 | 326.561 | 245.0429 | 287.5388 | 211.9487
1240.3167 | 330.7267 | 198.0102 | 339.2673 | 362.3434 | 326.7847 | 245.1835 | 287.718 | 212.1269
1241.3167 | 330.5717 | 198.1395 | 340.0866 | 362.4838 | 326.1818 | 245.3318 | 287.9151 | 212.3565
1242.3167 | 331.5551 | 198.2547 | 341.6984 | 364.1882 | 326.8781 | 245.4813 | 288.0988 | 212.4831
1243.3167 | 331.9538 | 198.382 | 342.351 | 365.031 | 328.4621 | 245.63 | 288.2862 | 212.6854
1244.3167 | 331.5442 | 198.4995 | 341.9796 | 365.1165 | 328.9321 | 245.7864 | 288.4615 | 212.8889
1245.3167 | 332.1765 | 198.631 | 342.5681 | 365.3526 | 328.7128 | 245.9347 | 288.6579 | 213.0552
1246.3167 | 332.0421 | 198.751 | 344.7383 | 365.6408 | 328.5259 | 246.0962 | 288.8409 | 213.2729
1247.3167 | 331.6367 | 198.8774 | 345.7821 | 365.2014 | 328.2433 | 246.2872 | 289.02 | 213.4001
1248.3167 | 332.1689 | 198.999 | 347.7518 | 365.2351 | 327.4448 | 246.5023 | 289.1876 | 213.6533
1249.3167 | 332.5545 | 199.1284 | 349.4186 | 365.2959 | 327.4739 | 246.6798 | 289.3617 | 213.7826
1250.3167 | 332.932 | 199.2539 | 350.8909 | 365.5311 | 327.2601 | 246.8713 | 289.5358 | 214.0584
1251.3167 | 332.5747 | 199.4004 | 350.9941 | 364.7368 | 326.8467 | 247.0532 | 289.7235 | 214.2233
1252.3167 | 334.9457 | 199.521 | 351.9841 | 364.9401 | 327.3122 | 247.2884 | 289.8754 | 214.4227
1253.3167 | 336.0508 | 199.6521 | 352.012 | 366.9378 | 327.4812 | 247.4868 | 290.0727 | 214.5952
1254.3167 | 337.0485 | 199.7721 | 353.0725 | 368.7773 | 328.1976 | 247.651 | 290.2464 | 214.7926
1255.3167 | 337.6453 | 199.8997 | 355.1327 | 370.7804 | 328.6931 | 247.8316 | 290.4083 | 215.0096
1256.3167 | 339.0849 | 200.0188 | 356.0894 | 373.1293 | 328.7336 | 248.0108 | 290.5943 | 215.1783
1257.3167 | 339.4503 | 200.1513 | 357.692 | 375.9705 | 329.7889 | 248.1596 | 290.7681 | 215.3798
1258.3167 | 339.7279 | 200.2763 | 359.2014 | 378.1452 | 331.849 | 248.3155 | 290.96 | 215.6004
1259.3167 | 340.7755 | 200.4093 | 360.6394 | 380.5086 | 332.7981 | 248.5027 | 291.1304 | 215.7818
1260.3167 | 341.4062 | 200.5334 | 361.0892 | 382.3236 | 334.7598 | 248.6685 | 291.3053 | 215.9509
1261.3167 | 341.7792 | 200.6631 | 361.3027 | 383.8719 | 335.8895 | 248.856 | 291.4724 | 216.1436
1262.3167 | 342.5251 | 200.7863 | 361.862 | 384.7712 | 336.7304 | 249.0261 | 291.6505 | 216.3305
1263.3167 | 343.7836 | 200.9029 | 363.112 | 387.5788 | 338.407 | 249.2201 | 291.8543 | 216.5508
1264.3167 | 344.0231 | 201.0237 | 363.585 | 389.5904 | 338.8169 | 249.4129 | 292.0052 | 216.7689
1265.3167 | 344.5485 | 201.144 | 364.2463 | 391.184 | 340.0699 | 249.6024 | 292.1585 | 216.9519
1266.3167 | 344.6322 | 201.2691 | 365.3987 | 391.1199 | 340.384 | 249.7807 | 292.3537 | 217.1184
1267.3167 | 344.8826 | 201.3962 | 365.759 | 390.7347 | 340.4481 | 249.9498 | 292.5062 | 217.3363
1268.3167 | 344.8896 | 201.5216 | 365.7302 | 390.4019 | 340.8805 | 250.125 | 292.6654 | 217.514
1269.3167 | 344.2977 | 201.6299 | 364.9863 | 388.9697 | 340.301 | 250.292 | 292.8436 | 217.6845
1270.3167 | 344.9316 | 201.7648 | 364.7054 | 387.7559 | 339.5848 | 250.4694 | 293.0168 | 217.8527
1271.3167 | 344.5134 | 201.8998 | 364.6944 | 387.8905 | 338.3615 | 250.6306 | 293.1996 | 218.0333
1272.3167 | 345.0834 | 202.0167 | 364.8479 | 388.3679 | 339.4265 | 250.8382 | 293.3754 | 218.2134
1273.3167 | 345.995 | 202.1305 | 365.3251 | 390.2001 | 341.1366 | 250.9576 | 293.5303 | 218.377
1274.3167 | 346.1583 | 202.2583 | 366.1774 | 389.9663 | 341.5819 | 251.1241 | 293.7125 | 218.5754
1275.3167 | 346.3101 | 202.3767 | 366.5311 | 389.7419 | 342.3938 | 251.306 | 293.8836 | 218.761
1276.3167 | 346.0715 | 202.4911 | 366.0114 | 388.3138 | 341.4816 | 251.4944 | 294.0543 | 218.9464
1277.3167 | 345.5241 | 202.62 | 363.6087 | 387.1672 | 340.2566 | 251.6713 | 294.2278 | 219.1341
1278.3167 | 345.2456 | 202.7537 | 361.8872 | 385.7435 | 339.5474 | 251.7929 | 294.4055 | 219.3983
1279.3167 | 344.9757 | 202.8726 | 360.1293 | 384.2525 | 338.9302 | 252.246 | 294.6428 | 219.649
1280.3167 | 344.2816 | 203.0119 | 358.71 | 382.2936 | 337.3446 | 253.7333 | 295.0434 | 220.3446
1281.3167 | 342.9528 | 203.0979 | 356.1181 | 380.8201 | 336.9583 | 252.2383 | 294.9226 | 219.8608
1282.3167 | 342.6023 | 203.2333 | 356.6389 | 379.4771 | 335.9124 | 252.4048 | 295.1012 | 220.0233
1283.3167 | 342.3452 | 203.364 | 357.6556 | 378.6867 | 334.2444 | 252.573 | 295.2777 | 220.2079
1284.3167 | 342.2785 | 203.517 | 358.0989 | 379.4736 | 333.8104 | 252.6747 | 295.458 | 220.3487
1285.3167 | 341.2908 | 203.643 | 357.5696 | 378.7408 | 333.0588 | 252.8224 | 295.6245 | 220.5061
1286.3167 | 340.8674 | 203.7753 | 356.6324 | 378.4437 | 332.7502 | 252.9553 | 295.8066 | 220.7883
1287.3167 | 340.6321 | 203.881 | 357.0496 | 380.1815 | 333.045 | 253.1304 | 295.9651 | 220.9308
1288.3167 | 340.5012 | 204.0227 | 357.4146 | 382.0202 | 333.7069 | 253.316 | 296.1622 | 221.0806
1289.3167 | 340.9352 | 204.1498 | 357.8743 | 382.7141 | 334.5654 | 253.5321 | 296.3573 | 221.2502
1290.3167 | 342.1148 | 204.2784 | 359.3301 | 383.4741 | 335.3656 | 253.7381 | 296.5049 | 221.4823
1291.3167 | 342.49 | 204.3948 | 359.7043 | 383.3406 | 335.7732 | 253.8858 | 296.6878 | 221.6407
1292.3167 | 342.6186 | 204.5185 | 360.3351 | 383.0595 | 335.6612 | 254.0237 | 296.861 | 221.7733
1293.3167 | 342.3655 | 204.6366 | 362.2307 | 383.7237 | 336.0028 | 254.2007 | 297.043 | 221.9478
1294.3167 | 342.7296 | 204.7642 | 362.634 | 384.038 | 336.6249 | 254.4384 | 297.2237 | 222.1118
1295.3167 | 343.335 | 204.8946 | 363.703 | 384.0227 | 335.5091 | 254.677 | 297.4074 | 222.2788
1296.3167 | 343.4038 | 205.013 | 364.4542 | 383.9415 | 335.5497 | 254.8823 | 297.6006 | 222.4667
1297.3167 | 343.5986 | 205.1444 | 365.5933 | 383.9697 | 336.4264 | 255.0952 | 297.7525 | 222.6532
1298.3167 | 343.3787 | 205.2641 | 366.0001 | 383.2966 | 336.4811 | 255.3071 | 297.9423 | 222.8082
1299.3167 | 343.8014 | 205.3927 | 366.1292 | 383.0409 | 336.7344 | 255.5137 | 298.1053 | 222.9829
1300.3167 | 343.3295 | 205.5096 | 364.8446 | 382.0294 | 336.2393 | 255.7052 | 298.2691 | 223.1537
1301.3167 | 343.5899 | 205.6473 | 363.8776 | 380.8327 | 335.0975 | 255.8793 | 298.4589 | 223.3256
1302.3167 | 342.5094 | 205.77 | 361.9154 | 379.0186 | 333.9191 | 256.0223 | 298.6395 | 223.4879
1303.3167 | 342.0646 | 205.8946 | 360.706 | 378.0384 | 332.8757 | 256.1765 | 298.8257 | 223.6507
1304.3167 | 341.5226 | 206.0145 | 359.4936 | 377.2959 | 332.1744 | 256.3218 | 298.9987 | 223.8274
1305.3167 | 340.8127 | 206.1343 | 360.662 | 377.5256 | 331.6208 | 256.4945 | 299.1578 | 224.0177
1306.3167 | 340.0891 | 206.2612 | 360.7192 | 377.1499 | 331.4621 | 256.6734 | 299.321 | 224.2365
1307.3167 | 340.9269 | 206.3787 | 360.5227 | 376.488 | 330.9537 | 256.8556 | 299.4855 | 224.4489
1308.3167 | 340.6384 | 206.5066 | 359.8828 | 375.1388 | 330.2144 | 257.0315 | 299.6567 | 224.6077
1309.3167 | 340.5928 | 206.6302 | 359.5227 | 374.3428 | 328.9047 | 257.5688 | 299.8393 | 224.748
1310.3167 | 340.3475 | 206.7569 | 360.0753 | 373.9241 | 328.5523 | 257.3107 | 300.0434 | 224.8979
1311.3167 | 340.622 | 206.8765 | 359.0488 | 373.8304 | 328.1843 | 257.4531 | 300.1959 | 225.0634
1312.3167 | 340.953 | 206.9971 | 360.7707 | 374.1026 | 328.9117 | 257.6365 | 300.3957 | 225.2113
1313.3167 | 341.019 | 207.1157 | 360.859 | 373.0774 | 328.3294 | 257.8698 | 300.5573 | 225.3831
1314.3167 | 340.4949 | 207.2391 | 361.4305 | 371.6269 | 327.4449 | 258.0776 | 300.7479 | 225.5606
1315.3167 | 340.7666 | 207.3551 | 359.9641 | 370.3033 | 326.1547 | 258.5187 | 300.8853 | 225.7487
1316.3167 | 340.1904 | 207.4877 | 359.6502 | 369.5948 | 325.2133 | 258.4909 | 301.0725 | 225.9419
1317.3167 | 340.7489 | 207.6067 | 360.8426 | 371.0166 | 325.1657 | 258.6483 | 301.2372 | 226.111
1318.3167 | 342.0609 | 207.7317 | 362.2434 | 372.7608 | 325.9813 | 258.7808 | 301.427 | 226.3192
1319.3167 | 342.1766 | 207.8533 | 363.3232 | 372.8641 | 326.68 | 258.9511 | 301.6053 | 226.461
1320.3167 | 342.0742 | 207.972 | 362.0796 | 371.5415 | 326.3602 | 259.1059 | 301.7701 | 226.6657
1321.3167 | 342.4728 | 208.0851 | 360.9085 | 369.7553 | 325.2731 | 259.2323 | 301.9427 | 226.8242
1322.3167 | 342.8905 | 208.2103 | 359.4101 | 368.5928 | 324.262 | 259.3813 | 302.1085 | 226.9686
1323.3167 | 342.1867 | 208.3283 | 358.776 | 368.3447 | 324.1842 | 259.4906 | 302.286 | 227.1288
1324.3167 | 342.4031 | 208.4486 | 358.2244 | 369.2229 | 324.3278 | 259.6403 | 302.4473 | 227.3003
1325.3167 | 342.7661 | 208.5698 | 358.4192 | 369.9462 | 325.8101 | 259.8048 | 302.606 | 227.4719
1326.3167 | 342.0878 | 208.6934 | 358.8992 | 370.0922 | 326.5658 | 259.9617 | 302.7944 | 227.6059
1327.3167 | 341.4857 | 208.8226 | 358.3561 | 369.9899 | 326.6754 | 260.1184 | 302.9769 | 227.776
1328.3167 | 341.7981 | 208.9347 | 358.6 | 369.9279 | 326.5008 | 260.2611 | 303.1572 | 227.9413
1329.3167 | 342.301 | 209.0478 | 358.9361 | 370.751 | 326.3934 | 260.4096 | 303.309 | 228.0951
1330.3167 | 342.671 | 209.1494 | 359.4402 | 371.1876 | 326.2108 | 261.1292 | 303.4897 | 228.2658
1331.3167 | 342.6853 | 209.2506 | 359.1156 | 370.6081 | 325.8927 | 261.2487 | 303.6598 | 228.4222
1332.3167 | 342.1413 | 209.3689 | 358.8943 | 370.2996 | 325.6345 | 261.439 | 303.8367 | 228.559
1333.3167 | 340.9842 | 209.4873 | 358.7223 | 369.7717 | 324.7777 | 261.612 | 304.0154 | 228.7304
1334.3167 | 342.0292 | 209.6191 | 358.7023 | 368.9676 | 323.8774 | 261.7467 | 304.2085 | 228.9079
1335.3167 | 342.517 | 209.7467 | 358.4784 | 368.3864 | 324.1304 | 261.9338 | 304.3901 | 229.0113
1336.3167 | 342.3606 | 209.8696 | 359.8439 | 367.354 | 324.0275 | 262.1073 | 304.5514 | 229.1621
1337.3167 | 341.8737 | 209.9918 | 359.0947 | 367.0726 | 323.5481 | 262.2668 | 304.7415 | 229.3197
1338.3167 | 341.887 | 210.1268 | 358.8709 | 366.5292 | 323.1519 | 262.4288 | 304.9158 | 229.4894
1339.3167 | 340.7455 | 210.2611 | 360.179 | 366.2857 | 322.9479 | 262.5972 | 305.063 | 229.639
1340.3167 | 339.7086 | 210.3934 | 361.5164 | 366.9114 | 323.2606 | 262.7874 | 305.2412 | 229.8089
1341.3167 | 339.219 | 210.5188 | 361.6019 | 367.5512 | 324.1503 | 262.9765 | 305.3927 | 229.9845
1342.3167 | 339.4348 | 210.6448 | 363.1683 | 368.2648 | 324.8248 | 263.1899 | 305.5744 | 230.1491
1343.3167 | 339.2962 | 210.7752 | 364.1733 | 369.0819 | 325.2184 | 263.4306 | 305.7404 | 230.2948
1344.3167 | 339.8548 | 210.9034 | 364.3649 | 369.5859 | 325.0258 | 263.6572 | 305.88 | 230.4692
1345.3167 | 339.9989 | 211.0271 | 364.9301 | 369.7203 | 325.3239 | 264.0293 | 306.0417 | 230.5976
1346.3167 | 339.4606 | 211.1562 | 366.1618 | 370.9702 | 325.6648 | 264.5993 | 306.211 | 230.7524
1347.3167 | 339.7496 | 211.284 | 366.7602 | 372.3164 | 326.3117 | 264.5687 | 306.3902 | 230.9182
1348.3167 | 339.4644 | 211.4069 | 366.8215 | 372.2553 | 326.3818 | 264.7554 | 306.5356 | 231.077
1349.3167 | 339.2045 | 211.5239 | 366.9923 | 373.0519 | 326.895 | 264.9287 | 306.6909 | 231.2422
1350.3167 | 340.0954 | 211.6492 | 367.0884 | 374.7084 | 326.8962 | 265.1155 | 306.8913 | 231.3849
1351.3167 | 341.5394 | 211.7753 | 368.59 | 376.1454 | 328.3551 | 265.2964 | 307.048 | 231.5445
1352.3167 | 342.7248 | 211.8996 | 370.4954 | 378.3455 | 330.8946 | 265.4985 | 307.2316 | 231.746
1353.3167 | 343.7034 | 212.0213 | 370.8078 | 380.5119 | 332.7961 | 265.6586 | 307.3882 | 231.8712
1354.3167 | 343.8199 | 212.1447 | 370.9212 | 381.4744 | 333.7771 | 265.8458 | 307.5669 | 232.0347
1355.3167 | 344.5177 | 212.2566 | 371.2003 | 383.2087 | 334.5445 | 266.286 | 307.7335 | 232.1839
1356.3167 | 344.6935 | 212.3786 | 373.4263 | 385.1796 | 336.0523 | 266.4043 | 307.8733 | 232.2978
1357.3167 | 345.5454 | 212.5022 | 373.9574 | 385.7991 | 335.329 | 266.4277 | 308.0083 | 232.5556
1358.3167 | 346.1012 | 212.6172 | 375.8922 | 387.918 | 335.2317 | 266.6177 | 308.1595 | 232.6592
1359.3167 | 345.8483 | 212.7565 | 375.6203 | 388.5922 | 335.9231 | 266.7888 | 308.3176 | 232.8859
1360.3167 | 346.0991 | 212.8639 | 375.2208 | 388.3208 | 336.0632 | 266.9868 | 308.4783 | 233.003
1361.3167 | 345.2423 | 212.9948 | 373.9456 | 387.0955 | 335.6671 | 267.1542 | 308.6341 | 233.1222
1362.3167 | 344.7983 | 213.1074 | 371.0794 | 385.0647 | 334.7013 | 267.3286 | 308.7483 | 233.2872
1363.3167 | 344.8211 | 213.2242 | 368.7662 | 383.557 | 333.9502 | 267.4495 | 308.9008 | 233.4372
1364.3167 | 344.0969 | 213.3373 | 368.23 | 382.6631 | 333.5753 | 267.5912 | 309.0729 | 233.594
1365.3167 | 343.526 | 213.4583 | 367.4189 | 382.452 | 333.2871 | 267.705 | 309.2395 | 233.7685
1366.3167 | 342.6087 | 213.5659 | 366.8434 | 381.7062 | 332.6502 | 267.8513 | 309.4052 | 233.9304
1367.3167 | 342.5715 | 213.6787 | 366.7349 | 380.6571 | 332.373 | 267.9126 | 309.5455 | 234.0739
1368.3167 | 341.938 | 213.8 | 365.0377 | 378.2881 | 331.5117 | 268.0851 | 309.7239 | 234.2269
1369.3167 | 342.4916 | 213.9239 | 363.7254 | 376.2089 | 330.3406 | 268.1739 | 309.8817 | 234.3951
1370.3167 | 342.2403 | 214.025 | 363.0027 | 375.5593 | 329.2484 | 268.2486 | 310.0697 | 234.5198
1371.3167 | 341.5304 | 214.15 | 364.5757 | 376.0502 | 328.9861 | 268.3817 | 310.2278 | 234.6328
1372.3167 | 341.7641 | 214.2706 | 366.0328 | 377.6096 | 330.0246 | 268.5549 | 310.3699 | 234.7609
1373.3167 | 341.6804 | 214.3999 | 366.1477 | 378.1394 | 331.3148 | 269.081 | 310.5322 | 234.8987
1374.3167 | 343.0241 | 214.5289 | 366.2272 | 377.9159 | 331.6749 | 269.2035 | 310.7166 | 235.0249
1375.3167 | 343.6193 | 214.6527 | 364.6309 | 377.3409 | 331.3397 | 269.1995 | 310.8955 | 235.2073
1376.3167 | 343.4104 | 214.7691 | 362.3254 | 375.84 | 330.4433 | 269.3793 | 311.0715 | 235.3065
1377.3167 | 343.1699 | 214.9021 | 360.5877 | 374.8671 | 329.5369 | 269.5362 | 311.2297 | 235.4534
1378.3167 | 342.9655 | 215.0261 | 359.4715 | 374.3039 | 328.7608 | 269.8894 | 311.3932 | 235.6433
1379.3167 | 342.4376 | 215.145 | 359.6497 | 375.2662 | 329.3174 | 269.7004 | 311.5314 | 235.8817
1380.3167 | 341.8941 | 215.2782 | 360.1979 | 376.1174 | 330.8264 | 269.837 | 311.6841 | 235.9795
1381.3167 | 341.6079 | 215.3978 | 359.7993 | 375.8844 | 331.4497 | 270.0057 | 311.8165 | 236.0791
1382.3167 | 341.4094 | 215.5173 | 359.3793 | 374.9573 | 331.0698 | 270.1291 | 311.9507 | 236.198
1383.3167 | 342.2683 | 215.6429 | 358.938 | 373.9385 | 330.1008 | 270.2708 | 312.1088 | 236.3843
1384.3167 | 342.2086 | 215.7548 | 357.6084 | 372.9038 | 329.2523 | 270.3436 | 312.2396 | 236.499
1385.3167 | 342.2694 | 215.876 | 357.4077 | 371.7397 | 328.1154 | 270.4659 | 312.3949 | 236.6398
1386.3167 | 342.3557 | 215.9803 | 356.8532 | 371.0194 | 327.2055 | 270.5926 | 312.5268 | 236.7431
1387.3167 | 341.8124 | 216.1076 | 356.5139 | 370.3765 | 326.7797 | 270.7241 | 312.6622 | 236.8871
1388.3167 | 342.3616 | 216.2222 | 356.9957 | 369.5934 | 326.185 | 270.8081 | 312.808 | 237.0106
1389.3167 | 341.4424 | 216.3507 | 357.7979 | 368.891 | 325.7933 | 270.9355 | 312.9852 | 237.1589
1390.3167 | 340.5638 | 216.4834 | 358.0929 | 368.9911 | 325.5816 | 271.0508 | 313.134 | 237.3143
1391.3167 | 340.5354 | 216.6147 | 358.4107 | 370.0952 | 326.2508 | 271.1699 | 313.2944 | 237.4455
1392.3167 | 340.3602 | 216.7452 | 358.1324 | 370.0281 | 326.2863 | 271.1388 | 313.4762 | 237.5659
1393.3167 | 340.4064 | 216.8687 | 358.5025 | 370.0485 | 326.1203 | 271.2652 | 313.6376 | 237.7153
1394.3167 | 340.4191 | 217.0014 | 358.2444 | 370.4666 | 325.5149 | 271.4013 | 313.7854 | 237.8931
1395.3167 | 340.8258 | 217.1272 | 356.8653 | 370.3596 | 325.5159 | 271.5114 | 313.9424 | 238.0774
1396.3167 | 340.9924 | 217.2548 | 356.2199 | 369.8517 | 325.8151 | 271.8647 | 314.0951 | 238.2457
1397.3167 | 340.891 | 217.3679 | 357.7591 | 369.6328 | 325.4369 | 272.0367 | 314.2444 | 238.3752
1398.3167 | 340.9044 | 217.4892 | 357.7998 | 369.056 | 325.1571 | 272.1252 | 314.4143 | 238.5383
1399.3167 | 341.0968 | 217.6167 | 357.2544 | 368.9637 | 324.5196 | 272.1605 | 314.6057 | 238.6901
1400.3167 | 340.5332 | 217.7391 | 355.2554 | 367.7501 | 323.6555 | 272.3681 | 314.7596 | 238.8384
1401.3167 | 340.5642 | 217.87 | 355.614 | 367.1608 | 322.8522 | 272.5577 | 314.9217 | 238.9634
1402.3167 | 340.351 | 218.0055 | 357.5487 | 368.2017 | 323.7034 | 272.6245 | 315.0814 | 239.0948
1403.3167 | 340.274 | 218.1299 | 358.6438 | 369.4217 | 324.8393 | 272.6923 | 315.2437 | 239.2534
1404.3167 | 340.9269 | 218.2644 | 358.9659 | 368.9544 | 325.0686 | 272.8387 | 315.4269 | 239.4118
1405.3167 | 341.442 | 218.3758 | 358.9248 | 367.9052 | 324.8378 | 272.9821 | 315.5787 | 239.5535
1406.3167 | 341.3402 | 218.5083 | 359.0064 | 366.8269 | 324.457 | 273.0987 | 315.7346 | 239.6807
1407.3167 | 341.7757 | 218.6385 | 359.3222 | 366.5064 | 323.9667 | 273.2537 | 315.8775 | 239.8491
1408.3167 | 341.0458 | 218.7715 | 360.6036 | 366.7073 | 323.8588 | 274.0717 | 316.0207 | 239.9834
1409.3167 | 340.5924 | 218.887 | 361.6395 | 367.0143 | 323.4409 | 274.1869 | 316.159 | 240.11
1410.3167 | 341.2302 | 219.0052 | 361.6369 | 367.1998 | 323.985 | 274.1743 | 316.3162 | 240.2708
1411.3167 | 340.8288 | 219.111 | 362.4169 | 366.6395 | 324.1224 | 274.3092 | 316.4699 | 240.4093
1412.3167 | 340.9561 | 219.2481 | 361.8339 | 366.3684 | 324.0095 | 274.4544 | 316.6215 | 240.5564
1413.3167 | 340.6071 | 219.3703 | 361.4308 | 366.5426 | 323.8181 | 274.5876 | 316.7683 | 240.708
1414.3167 | 340.9916 | 219.5094 | 360.7705 | 366.0564 | 323.605 | 275.0295 | 316.9473 | 240.8257
1415.3167 | 341.6689 | 219.6305 | 360.4757 | 365.313 | 323.2292 | 275.1405 | 317.0924 | 240.9641
1416.3167 | 341.665 | 219.7592 | 360.2689 | 363.7592 | 322.8475 | 275.0094 | 317.2438 | 241.0971
1417.3167 | 341.1339 | 219.8791 | 359.8457 | 363.2354 | 322.0893 | 275.0805 | 317.3901 | 241.2166
1418.3167 | 340.8403 | 220.0195 | 359.6928 | 363.5382 | 321.6697 | 275.2131 | 317.541 | 241.358
1419.3167 | 340.8819 | 220.1447 | 359.1573 | 363.1352 | 321.5127 | 275.2871 | 317.672 | 241.4771
1420.3167 | 340.5898 | 220.2481 | 357.9224 | 362.7202 | 321.2349 | 275.5977 | 317.8345 | 241.6154
1421.3167 | 340.4152 | 220.4014 | 355.9571 | 362.5125 | 322.5937 | 275.6383 | 317.9807 | 241.7644
1422.3167 | 339.3333 | 220.5141 | 354.7905 | 362.7182 | 323.177 | 275.8479 | 318.0973 | 241.8958
1423.3167 | 338.455 | 220.63 | 354.5379 | 362.4969 | 323.1851 | 275.853 | 318.2568 | 242.036
1424.3167 | 337.2766 | 220.7591 | 356.1023 | 362.3041 | 323.1092 | 275.9542 | 318.3906 | 242.1927
1425.3167 | 336.9168 | 220.8806 | 356.1651 | 361.6511 | 322.285 | 276.0795 | 318.5359 | 242.3349
1426.3167 | 336.7948 | 221.0127 | 356.298 | 361.4932 | 321.8104 | 276.1423 | 318.6829 | 242.4648
1427.3167 | 335.9332 | 221.1492 | 356.6475 | 361.2043 | 321.2864 | 276.2697 | 318.8297 | 242.5924
1428.3167 | 335.846 | 221.2638 | 355.7944 | 360.334 | 320.7447 | 276.376 | 318.977 | 242.7306
1429.3167 | 336.4062 | 221.3867 | 355.0541 | 359.8483 | 320.6701 | 276.5263 | 319.1202 | 242.8927
1430.3167 | 336.7574 | 221.5253 | 354.9825 | 359.8591 | 320.8001 | 276.8536 | 319.2799 | 243.0389
1431.3167 | 336.6964 | 221.6517 | 354.5728 | 360.4989 | 321.7973 | 276.8212 | 319.4242 | 243.2095
1432.3167 | 336.3304 | 221.7742 | 354.2319 | 360.6752 | 322.3954 | 276.8778 | 319.5829 | 243.3512
1433.3167 | 335.6263 | 221.8969 | 353.3322 | 360.6177 | 322.5939 | 276.9985 | 319.7355 | 243.4795
1434.3167 | 335.1565 | 222.0266 | 352.5166 | 360.1652 | 322.2006 | 277.0947 | 319.8603 | 243.6355
1435.3167 | 335.5874 | 222.1631 | 352.3045 | 359.3099 | 321.3425 | 277.1878 | 320.0072 | 243.7478
1436.3167 | 335.2606 | 222.2896 | 351.9276 | 360.1927 | 321.1962 | 277.2658 | 320.1597 | 243.8725
1437.3167 | 335.0154 | 222.4138 | 351.9353 | 360.4975 | 321.4146 | 277.7822 | 320.2898 | 243.9816
1438.3167 | 334.546 | 222.5325 | 351.2342 | 359.9979 | 321.2946 | 277.7804 | 320.4252 | 244.0904
1439.3167 | 334.145 | 222.6541 | 350.8749 | 359.0973 | 320.5037 | 277.7091 | 320.5795 | 244.2075
1440.3167 | 333.6437 | 222.7712 | 350.7699 | 358.6394 | 319.8085 | 277.8021 | 320.7335 | 244.364
1441.3167 | 333.0042 | 222.8969 | 351.9301 | 358.3161 | 319.3949 | 277.9072 | 320.8698 | 244.4737
1442.3167 | 332.6919 | 222.9848 | 353.293 | 358.0472 | 318.9048 | 278.0849 | 321.0414 | 244.6051
1443.3167 | 332.5663 | 223.1103 | 354.1393 | 357.6677 | 318.516 | 278.3089 | 321.1764 | 244.7575
1444.3167 | 332.764 | 223.2321 | 355.4372 | 358.006 | 318.135 | 278.4289 | 321.3328 | 244.8715
1445.3167 | 331.6152 | 223.3474 | 355.5278 | 357.5396 | 318.0956 | 278.5593 | 321.449 | 245.0084
1446.3167 | 331.0429 | 223.4588 | 355.5389 | 358.2915 | 318.2598 | 278.736 | 321.6097 | 245.124
1447.3167 | 330.6938 | 223.582 | 355.3779 | 357.9298 | 318.4978 | 278.8723 | 321.7332 | 245.2425
1448.3167 | 331.0693 | 223.6858 | 357.1989 | 359.8808 | 319.4057 | 279.0293 | 321.8414 | 245.4048
1449.3167 | 331.5121 | 223.8047 | 358.2333 | 360.9464 | 321.0898 | 279.1699 | 321.9865 | 245.5075
1450.3167 | 332.4267 | 223.9266 | 358.9675 | 361.2593 | 321.6365 | 279.3403 | 322.1143 | 245.5943
1451.3167 | 333.2667 | 224.0312 | 361.45 | 363.5747 | 322.7099 | 279.5262 | 322.2707 | 245.7163
1452.3167 | 333.7964 | 224.1508 | 363.8744 | 364.0482 | 323.666 | 279.7198 | 322.4019 | 245.8535
1453.3167 | 334.161 | 224.2837 | 364.4942 | 364.3718 | 323.5185 | 279.9361 | 322.5324 | 246.0107
1454.3167 | 333.7221 | 224.3985 | 365.3687 | 365.2158 | 323.4996 | 280.0933 | 322.6583 | 246.3633
1455.3167 | 333.8139 | 224.5252 | 365.3602 | 365.7818 | 323.7462 | 280.2439 | 322.7877 | 246.4181
1456.3167 | 333.9536 | 224.6465 | 365.5185 | 366.6352 | 324.0521 | 280.3292 | 322.9191 | 246.5011
1457.3167 | 334.5821 | 224.7596 | 366.774 | 368.6815 | 325.3962 | 280.4522 | 323.0493 | 246.6094
1458.3167 | 334.5538 | 224.883 | 367.8193 | 369.486 | 327.2491 | 280.6166 | 323.1756 | 246.7379
1459.3167 | 334.573 | 225.0086 | 368.387 | 369.7411 | 328.1266 | 280.7669 | 323.3068 | 246.866
1460.3167 | 335.7864 | 225.1203 | 370.5031 | 371.1246 | 328.8186 | 280.9076 | 323.4137 | 246.9688
1461.3167 | 335.9415 | 225.2326 | 372.0676 | 372.5171 | 331.0048 | 281.0477 | 323.5593 | 247.1019
1462.3167 | 336.6967 | 225.3434 | 372.1651 | 372.4421 | 331.4511 | 281.1944 | 323.6727 | 247.2188
1463.3167 | 337.7134 | 225.4615 | 371.6908 | 372.2447 | 330.8347 | 281.37 | 323.7956 | 247.3427
1464.3167 | 337.8989 | 225.586 | 370.6679 | 371.2685 | 330.1803 | 281.4887 | 323.9111 | 247.4345
1465.3167 | 338.4322 | 225.6972 | 370.9405 | 370.7325 | 329.5135 | 281.6461 | 324.0392 | 247.5576
1466.3167 | 338.5182 | 225.8143 | 369.7765 | 370.0452 | 328.8487 | 281.787 | 324.1445 | 247.6971
1467.3167 | 338.8018 | 225.9393 | 368.4599 | 369.183 | 328.0865 | 281.9186 | 324.2765 | 247.7971
1468.3167 | 339.8337 | 226.0605 | 368.1959 | 370.1223 | 327.9722 | 282.0447 | 324.3945 | 247.9171
1469.3167 | 339.9857 | 226.1704 | 369.0917 | 371.8003 | 329.1302 | 282.2009 | 324.5196 | 248.018
1470.3167 | 340.6088 | 226.2847 | 368.7052 | 373.6318 | 329.9404 | 282.3807 | 324.6349 | 248.1415
1471.3167 | 340.931 | 226.3939 | 369.8769 | 374.8561 | 331.3261 | 282.5708 | 324.761 | 248.2673
1472.3167 | 342.3278 | 226.496 | 370.6002 | 377.1207 | 333.7514 | 282.7242 | 324.9121 | 248.3657
1473.3167 | 343.4328 | 226.6238 | 370.8559 | 378.5747 | 335.2739 | 282.8859 | 325.0379 | 248.4739
1474.3167 | 344.1354 | 226.7372 | 372.3781 | 379.5532 | 335.7501 | 283.0339 | 325.1767 | 248.6083
1475.3167 | 344.4215 | 226.8662 | 372.9052 | 379.5568 | 336.216 | 283.1489 | 325.303 | 248.7391
1476.3167 | 344.5619 | 226.9566 | 373.0698 | 382.6326 | 336.5561 | 283.3084 | 325.4369 | 248.865
1477.3167 | 345.7722 | 227.0691 | 373.4264 | 383.221 | 337.0972 | 283.4896 | 325.5506 | 248.993
1478.3167 | 346.9867 | 227.1834 | 375.1576 | 384.4267 | 338.6936 | 283.6247 | 325.6892 | 249.0769
1479.3167 | 348.2532 | 227.2909 | 375.3381 | 385.4497 | 339.7412 | 283.7769 | 325.8084 | 249.1878
1480.3167 | 348.7551 | 227.4071 | 374.6966 | 386.3468 | 340.6671 | 283.9078 | 325.9138 | 249.299
1481.3167 | 348.0543 | 227.5109 | 373.6462 | 386.0759 | 340.7766 | 284.0462 | 326.0385 | 249.4106
1482.3167 | 347.9364 | 227.651 | 372.6137 | 384.6726 | 340.0957 | 284.1771 | 326.1517 | 249.5553
1483.3167 | 348.7174 | 227.7462 | 372.2821 | 383.7782 | 339.3359 | 284.3004 | 326.2569 | 249.6663
1484.3167 | 349.355 | 227.8552 | 371.612 | 383.6177 | 338.9557 | 284.4039 | 326.3999 | 249.8236
1485.3167 | 348.8317 | 227.9628 | 371.5942 | 383.2439 | 338.7244 | 284.4919 | 326.4933 | 249.9326
1486.3167 | 349.1666 | 228.0758 | 370.0524 | 382.5727 | 338.3016 | 284.5757 | 326.6405 | 250.0371
1487.3167 | 349.2719 | 228.2022 | 368.19 | 381.0471 | 337.4309 | 284.6866 | 326.742 | 250.1652
1488.3167 | 349.4427 | 228.3068 | 367.6934 | 380.2518 | 336.8095 | 284.7949 | 326.858 | 250.2755
1489.3167 | 349.2141 | 228.4286 | 366.8367 | 380.0794 | 336.2611 | 284.8554 | 326.9848 | 250.423
1490.3167 | 349.8049 | 228.5495 | 366.4416 | 379.1098 | 335.9467 | 284.9883 | 327.1343 | 250.5268
1491.3167 | 349.2026 | 228.6628 | 367.0708 | 378.1974 | 335.0622 | 285.1006 | 327.2387 | 250.6297
1492.3167 | 349.3853 | 228.7799 | 368.3063 | 378.562 | 334.0434 | 285.2127 | 327.3613 | 250.7409
1493.3167 | 349.2514 | 228.887 | 369.5562 | 379.8586 | 334.47 | 285.3632 | 327.4904 | 250.8775
1494.3167 | 348.9712 | 229.0032 | 369.6559 | 380.9024 | 334.4007 | 285.5009 | 327.6074 | 250.9819
1495.3167 | 348.5669 | 229.1157 | 369.2594 | 381.8046 | 334.3417 | 285.6504 | 327.7361 | 251.0967
1496.3167 | 349.0967 | 229.2302 | 369.7313 | 382.1463 | 333.8734 | 285.7789 | 327.8531 | 251.2137
1497.3167 | 349.3148 | 229.3494 | 370.1166 | 382.3721 | 333.3632 | 285.9167 | 327.9914 | 251.3222
1498.3167 | 349.8483 | 229.4554 | 371.5225 | 382.6194 | 333.695 | 286.0697 | 328.1215 | 251.4229
1499.3167 | 349.3355 | 229.5876 | 371.5803 | 382.3548 | 333.8179 | 286.224 | 328.2598 | 251.5625
1500.3167 | 350.2388 | 229.6981 | 371.5158 | 382.6171 | 333.6347 | 286.374 | 328.3855 | 251.6432
1501.3167 | 350.5479 | 229.8172 | 373.1925 | 383.5045 | 334.488 | 286.5348 | 328.5132 | 251.7894
1502.3167 | 350.5333 | 229.9307 | 373.6876 | 383.6495 | 335.3239 | 286.7402 | 328.6542 | 251.8815
1503.3167 | 351.1613 | 230.035 | 374.1559 | 384.0324 | 335.466 | 286.9402 | 328.8283 | 251.9916
1504.3167 | 352.5444 | 230.1444 | 373.8554 | 385.3379 | 335.8765 | 287.1421 | 328.964 | 252.0956
1505.3167 | 354.5492 | 230.2553 | 372.1465 | 387.0382 | 336.6014 | 287.2948 | 329.1012 | 252.2053
1506.3167 | 355.7354 | 230.3856 | 371.7696 | 388.6563 | 336.72 | 287.4646 | 329.2481 | 252.3269
1507.3167 | 357.3031 | 230.5035 | 371.625 | 389.1718 | 336.8333 | 287.9546 | 329.3806 | 252.4208
1508.3167 | 356.4754 | 230.6231 | 372.487 | 390.0549 | 336.6017 | 288.1666 | 329.4849 | 252.5367
1509.3167 | 355.7331 | 230.7285 | 372.7219 | 390.4732 | 337.1266 | 287.9344 | 329.6104 | 252.6206
1510.3167 | 354.8011 | 230.8447 | 372.3718 | 390.7447 | 338.2986 | 288.1338 | 329.7403 | 252.7667
1511.3167 | 354.9663 | 230.9587 | 371.7083 | 391.7931 | 339.368 | 288.2683 | 329.8677 | 252.8678
1512.3167 | 355.009 | 231.0751 | 371.7006 | 393.3326 | 340.9999 | 288.4085 | 330.0317 | 252.9868
1513.3167 | 355.1057 | 231.1905 | 371.4919 | 393.6259 | 342.4234 | 288.5383 | 330.1682 | 253.0836
1514.3167 | 355.9295 | 231.3166 | 370.6378 | 394.9303 | 343.7026 | 288.7553 | 330.2972 | 253.1997
1515.3167 | 356.6976 | 231.4299 | 370.8437 | 395.4205 | 344.5759 | 288.8479 | 330.4305 | 253.2977
1516.3167 | 356.9074 | 231.5551 | 372.3949 | 396.4208 | 345.6493 | 288.916 | 330.586 | 253.4037
1517.3167 | 357.1769 | 231.6864 | 372.4873 | 397.2446 | 345.7954 | 289.0373 | 330.7258 | 253.5111
1518.3167 | 356.8234 | 231.8081 | 372.0604 | 397.6 | 346.6892 | 289.1335 | 330.8798 | 253.6126
1519.3167 | 357.3651 | 231.9303 | 373.4161 | 398.6351 | 347.5192 | 289.4348 | 331.0205 | 253.7446
1520.3167 | 357.8771 | 232.044 | 374.2215 | 399.1546 | 348.5285 | 289.6654 | 331.1663 | 253.8841
1521.3167 | 357.9 | 232.1557 | 374.7836 | 398.6992 | 348.7939 | 289.1761 | 331.311 | 253.957
1522.3167 | 357.8747 | 232.2757 | 374.937 | 398.2485 | 348.7603 | 289.4942 | 331.4439 | 254.0654
1523.3167 | 357.1557 | 232.401 | 373.5437 | 396.2761 | 347.765 | 289.5224 | 331.5793 | 254.2081
1524.3167 | 356.341 | 232.5248 | 372.4849 | 395.5746 | 347.3888 | 289.6486 | 331.7352 | 254.3026
1525.3167 | 355.6699 | 232.6438 | 370.9851 | 393.4618 | 346.7983 | 289.8 | 331.8842 | 254.3934
1526.3167 | 355.0807 | 232.7712 | 370.5606 | 393.2125 | 346.2313 | 289.9577 | 332.0215 | 254.4893
1527.3167 | 354.5802 | 232.8905 | 370.1767 | 392.0246 | 346.0801 | 289.8755 | 332.1487 | 254.5963
1528.3167 | 354.4388 | 233.0154 | 370.0028 | 392.063 | 345.9334 | 290.1907 | 332.3189 | 254.7233
1529.3167 | 354.4325 | 233.1397 | 369.7048 | 391.1217 | 344.8135 | 290.3246 | 332.4507 | 254.7948
1530.3167 | 354.5527 | 233.2535 | 368.4105 | 389.4199 | 343.9097 | 290.2398 | 332.6123 | 254.9307
1531.3167 | 353.9751 | 233.3818 | 367.3353 | 388.035 | 343.1878 | 290.8415 | 332.7647 | 255.042
1532.3167 | 354.6375 | 233.493 | 366.3547 | 387.1778 | 342.6381 | 290.7212 | 332.9074 | 255.1409
1533.3167 | 354.5569 | 233.6107 | 365.8996 | 387.6086 | 342.8292 | 290.8249 | 333.0702 | 255.2511
1534.3167 | 354.2777 | 233.741 | 367.2753 | 388.6 | 343.0444 | 290.8929 | 333.2493 | 255.3869
1535.3167 | 354.8653 | 233.8764 | 370.0613 | 390.5164 | 344.7606 | 290.809 | 333.4002 | 255.4704
1536.3167 | 357.1375 | 233.9924 | 370.8954 | 392.2094 | 344.6663 | 291.0072 | 333.5338 | 255.5991
1537.3167 | 357.8343 | 234.131 | 370.5641 | 393.0017 | 344.6155 | 291.476 | 333.7064 | 255.7023
1538.3167 | 358.2493 | 234.2549 | 371.0337 | 393.5904 | 343.8126 | 291.5635 | 333.8429 | 255.8166
1539.3167 | 359.6537 | 234.3886 | 372.417 | 395.2233 | 343.4523 | 291.8015 | 334.0031 | 255.9008
1540.3167 | 361.365 | 234.5208 | 372.9772 | 397.5048 | 344.1726 | 291.9779 | 334.1556 | 256.0804
1541.3167 | 363.2664 | 234.6521 | 372.9327 | 399.6541 | 344.9271 | 292.1407 | 334.2999 | 256.1693
1542.3167 | 363.7237 | 234.7735 | 373.2537 | 401.6555 | 345.5856 | 292.3276 | 334.4607 | 256.2845
1543.3167 | 363.6812 | 234.8923 | 372.2278 | 403.0534 | 346.4326 | 292.3663 | 334.6058 | 256.3833
1544.3167 | 363.0338 | 235.0079 | 372.7944 | 404.0474 | 347.3291 | 292.6193 | 334.7934 | 256.4633
1545.3167 | 361.9847 | 235.1558 | 373.927 | 404.3774 | 347.6404 | 292.6595 | 334.9631 | 256.6217
1546.3167 | 361.5308 | 235.2712 | 374.6476 | 403.7644 | 347.4751 | 292.6701 | 335.1008 | 256.6945
1547.3167 | 360.7981 | 235.4078 | 375.402 | 403.3021 | 348.1075 | 292.7334 | 335.261 | 256.8158
1548.3167 | 360.5958 | 235.5274 | 375.3357 | 403.6976 | 347.8479 | 292.9651 | 335.4144 | 256.9444
1549.3167 | 360.4687 | 235.6458 | 375.3104 | 403.0973 | 348.4899 | 292.8799 | 335.581 | 257.0461
1550.3167 | 361.4767 | 235.7721 | 375.878 | 403.7699 | 349.3208 | 293.1527 | 335.7264 | 257.1457
1551.3167 | 362.2479 | 235.8991 | 376.9398 | 404.9169 | 349.5433 | 293.524 | 335.8923 | 257.2501
1552.3167 | 362.9901 | 236.0175 | 376.4133 | 405.7942 | 349.0641 | 293.5696 | 336.0598 | 257.3755
1553.3167 | 364.0988 | 236.131 | 376.2111 | 406.0781 | 348.4975 | 293.9018 | 336.2146 | 257.4837
1554.3167 | 364.8288 | 236.2399 | 375.9756 | 406.446 | 348.0934 | 293.9131 | 336.3781 | 257.5881
1555.3167 | 365.7519 | 236.3679 | 376.1336 | 406.2036 | 347.9319 | 294.0654 | 336.5556 | 257.6905
1556.3167 | 366.2136 | 236.4713 | 375.7146 | 406.1804 | 347.7366 | 294.2293 | 336.7469 | 257.8289
1557.3167 | 367.1609 | 236.5924 | 376.6068 | 407.1347 | 347.8068 | 294.255 | 336.9004 | 257.9113
1558.3167 | 367.1393 | 236.7007 | 376.364 | 407.4916 | 348.1884 | 294.357 | 337.0855 | 258.0319
1559.3167 | 367.5299 | 236.8175 | 376.0117 | 407.5851 | 348.1124 | 294.3688 | 337.2517 | 258.1299
1560.3167 | 367.0548 | 236.9415 | 375.6702 | 408.4419 | 348.5054 | 294.4662 | 337.41 | 258.2154
1561.3167 | 367.7357 | 237.0847 | 375.1498 | 408.7245 | 348.8208 | 294.3932 | 337.5922 | 258.308
1562.3167 | 367.688 | 237.216 | 374.819 | 408.3128 | 349.2867 | 294.1548 | 337.7603 | 258.4242
1563.3167 | 368.4974 | 237.3343 | 374.2403 | 408.0835 | 349.3583 | 294.1024 | 337.948 | 258.5273
1564.3167 | 370.4053 | 237.4405 | 375.342 | 408.4001 | 349.8887 | 294.1972 | 338.1275 | 258.648
1565.3167 | 369.3756 | 237.5699 | 376.3185 | 408.0095 | 349.8257 | 294.5618 | 338.3036 | 258.7544
1566.3167 | 369.3345 | 237.6972 | 377.1924 | 407.4591 | 349.035 | 294.7431 | 338.485 | 258.8803
1567.3167 | 370.5446 | 237.8107 | 378.6757 | 407.7422 | 348.6811 | 295.0298 | 338.6621 | 258.9913
1568.3167 | 371.2152 | 237.927 | 378.9533 | 407.8974 | 348.7729 | 295.1692 | 338.852 | 259.1003
1569.3167 | 372.586 | 238.0651 | 379.2631 | 408.7207 | 349.3233 | 295.4693 | 339.0254 | 259.2215
1570.3167 | 372.057 | 238.1857 | 378.1906 | 408.801 | 350.4726 | 295.5815 | 339.2137 | 259.3376
1571.3167 | 371.3323 | 238.3102 | 377.973 | 409.2077 | 350.3741 | 295.774 | 339.4022 | 259.4429
1572.3167 | 371.4208 | 238.4439 | 377.1502 | 408.8003 | 349.9503 | 295.8413 | 339.5961 | 259.55
1573.3167 | 372.2725 | 238.5581 | 376.8694 | 408.2219 | 349.6939 | 295.9258 | 339.7754 | 259.6503
1574.3167 | 373.0101 | 238.682 | 376.7385 | 408.4771 | 350.1005 | 296.0855 | 339.9527 | 259.7602
1575.3167 | 372.3458 | 238.7979 | 376.709 | 408.7707 | 351.375 | 296.1122 | 340.1508 | 259.8862
1576.3167 | 373.0059 | 238.9042 | 376.0132 | 408.324 | 352.4266 | 296.3284 | 340.3683 | 259.9959
1577.3167 | 372.1064 | 239.0234 | 375.5556 | 408.0693 | 352.9042 | 296.4223 | 340.549 | 260.1241
1578.3167 | 370.3772 | 239.1342 | 376.2737 | 408.4084 | 354.3101 | 296.6287 | 340.7468 | 260.2222
1579.3167 | 370.5228 | 239.2787 | 377.6544 | 409.7287 | 354.6697 | 297.3186 | 341.0513 | 260.5709
1580.3167 | 369.6825 | 239.3841 | 377.8995 | 409.4047 | 355.6228 | 296.7317 | 341.1472 | 260.4561
1581.3167 | 370.4052 | 239.5194 | 378.7905 | 408.8468 | 357.41 | 297.5918 | 341.4695 | 260.841
1582.3167 | 370.0954 | 239.6134 | 379.2974 | 409.9434 | 357.9643 | 296.9675 | 341.5418 | 260.7065
1583.3167 | 370.437 | 239.7308 | 380.0675 | 410.2059 | 358.7587 | 297.1426 | 341.7432 | 260.8341
1584.3167 | 370.6256 | 239.8477 | 379.5776 | 409.5676 | 358.8067 | 297.3388 | 341.9422 | 260.9441
1585.3167 | 370.4552 | 239.9599 | 379.9792 | 409.0034 | 358.4121 | 297.4407 | 342.1689 | 261.0672
1586.3167 | 369.7978 | 240.0772 | 380.3564 | 408.6865 | 358.1179 | 297.5857 | 342.3719 | 261.1818
1587.3167 | 370.8022 | 240.1823 | 381.3533 | 409.0467 | 359.0067 | 297.7602 | 342.6038 | 261.2913
1588.3167 | 371.1631 | 240.3054 | 382.1131 | 409.9731 | 359.5238 | 297.8515 | 342.8053 | 261.4232
1589.3167 | 372.4104 | 240.4136 | 382.6475 | 410.5946 | 360.0926 | 297.9715 | 343.0093 | 261.5234
1590.3167 | 371.7543 | 240.5352 | 382.9125 | 410.3489 | 360.5529 | 298.0524 | 343.2284 | 261.6222
1591.3167 | 371.6688 | 240.6412 | 381.7976 | 409.3873 | 360.524 | 298.1033 | 343.4492 | 261.6909
1592.3167 | 369.9823 | 240.7492 | 380.7883 | 408.6244 | 361.3044 | 298.2261 | 343.6764 | 261.8084
1593.3167 | 371.8668 | 240.8444 | 379.9973 | 407.7815 | 362.1338 | 298.2726 | 343.8946 | 261.9268
1594.3167 | 372.5889 | 240.9491 | 378.7536 | 406.882 | 362.6208 | 298.4251 | 344.1219 | 262.0394
1595.3167 | 372.2712 | 241.0527 | 377.191 | 405.5849 | 362.5829 | 298.5026 | 344.3434 | 262.1421
1596.3167 | 372.6678 | 241.1764 | 375.4111 | 404.4497 | 361.9487 | 298.6334 | 344.5776 | 262.2868
1597.3167 | 373.0371 | 241.2933 | 375.1958 | 403.9082 | 361.0138 | 298.7088 | 344.8032 | 262.3757
1598.3167 | 374.3141 | 241.4092 | 374.8605 | 404.5919 | 360.2443 | 298.8119 | 345.0538 | 262.49
1599.3167 | 376.4676 | 241.5161 | 373.8816 | 404.1131 | 359.1533 | 298.8815 | 345.2994 | 262.5671
1600.3167 | 378.1988 | 241.6096 | 374.5229 | 404.3582 | 358.7209 | 299.0139 | 345.5255 | 262.6591
1601.3167 | 376.7335 | 241.732 | 376.7832 | 405.6679 | 358.4279 | 299.2398 | 345.7621 | 262.7398
1602.3167 | 377.4949 | 241.8662 | 378.5193 | 407.6614 | 356.7418 | 301.0105 | 346.558 | 263.568
1603.3167 | 376.8674 | 241.9769 | 379.2196 | 409.8939 | 356.2754 | 301.1778 | 346.5273 | 263.5051
1604.3167 | 376.0584 | 242.076 | 380.2567 | 411.4402 | 355.9161 | 300.0558 | 346.538 | 263.1521
1605.3167 | 376.2823 | 242.1799 | 379.9899 | 413.4245 | 356.2482 | 300.037 | 346.722 | 263.1855
1606.3167 | 378.4819 | 242.3015 | 380.554 | 415.6632 | 356.7086 | 300.2756 | 346.9448 | 263.3091
1607.3167 | 378.7257 | 242.4144 | 381.2973 | 415.7037 | 356.5168 | 300.3377 | 347.179 | 263.4272
1608.3167 | 380.0093 | 242.5324 | 380.6021 | 416.2097 | 356.7375 | 300.4839 | 347.4077 | 263.5797
1609.3167 | 379.3982 | 242.6571 | 380.0616 | 415.6525 | 356.6514 | 300.5707 | 347.6414 | 263.6806
1610.3167 | 379.9626 | 242.7676 | 380.2684 | 415.401 | 356.1792 | 300.7284 | 347.8842 | 263.8057
1611.3167 | 378.0574 | 242.8834 | 379.7864 | 415.5959 | 355.595 | 300.8434 | 348.1064 | 263.9515
1612.3167 | 379.0993 | 242.9905 | 380.0723 | 414.651 | 354.8807 | 301.0406 | 348.3535 | 264.0552
1613.3167 | 378.6215 | 243.1089 | 379.5819 | 413.7942 | 354.3426 | 301.1628 | 348.5955 | 264.1636
1614.3167 | 378.433 | 243.2344 | 379.5748 | 412.656 | 353.5924 | 301.3731 | 348.8239 | 264.257
1615.3167 | 377.896 | 243.3527 | 379.4274 | 412.1586 | 353.1551 | 301.5878 | 349.071 | 264.2786
1616.3167 | 378.5583 | 243.4663 | 379.412 | 412.1156 | 352.9053 | 301.7473 | 349.3136 | 264.4183
1617.3167 | 377.9273 | 243.5858 | 378.6372 | 411.4953 | 352.3511 | 301.8998 | 349.5651 | 264.5214
1618.3167 | 380.3914 | 243.7002 | 378.1635 | 411.3126 | 351.7875 | 302.0615 | 349.8235 | 264.5778
1619.3167 | 379.1704 | 243.8205 | 378.5101 | 411.0699 | 351.3215 | 302.174 | 350.1001 | 264.7033
1620.3167 | 380.0676 | 243.9411 | 377.8071 | 411.105 | 351.4908 | 302.2779 | 350.3937 | 264.7644
1621.3167 | 379.3534 | 244.0572 | 378.0227 | 411.0957 | 350.9343 | 302.4589 | 350.6633 | 264.8771
1622.3167 | 380.7857 | 244.1756 | 378.8159 | 412.4923 | 350.4344 | 302.5211 | 350.9297 | 264.9917
1623.3167 | 383.7487 | 244.2699 | 379.139 | 414.6788 | 351.0197 | 302.6986 | 351.185 | 265.1157
1624.3167 | 383.6593 | 244.3909 | 378.0284 | 414.7504 | 351.5476 | 302.7883 | 351.44 | 265.2037
1625.3167 | 385.1223 | 244.5033 | 377.6022 | 414.4367 | 351.1657 | 302.9202 | 351.6834 | 265.3512
1626.3167 | 381.8038 | 244.6277 | 377.2369 | 414.7964 | 352.27 | 303.0494 | 351.9339 | 265.5493
1627.3167 | 382.2228 | 244.7487 | 377.6504 | 414.9357 | 353.7692 | 303.1206 | 352.1834 | 265.6855
1628.3167 | 380.726 | 244.8793 | 378.4171 | 415.414 | 354.4484 | 303.1993 | 352.4343 | 265.8055
1629.3167 | 379.6325 | 245.0021 | 379.6412 | 416.3511 | 354.6116 | 303.3594 | 352.7169 | 265.8803
1630.3167 | 381.3779 | 245.1212 | 379.0807 | 416.3646 | 355.3753 | 303.4089 | 352.9874 | 266.0585
1631.3167 | 381.1359 | 245.2493 | 379.1221 | 416.3873 | 355.8339 | 303.4523 | 353.2756 | 266.1214
1632.3167 | 380.3725 | 245.3664 | 379.4451 | 416.7956 | 356.1412 | 303.6257 | 353.5825 | 266.2924
1633.3167 | 380.2087 | 245.4774 | 379.2271 | 416.1737 | 355.4795 | 303.6914 | 353.8961 | 266.3775
1634.3167 | 379.0552 | 245.6067 | 379.965 | 415.9058 | 354.3374 | 303.8424 | 354.2207 | 266.4653
1635.3167 | 381.7259 | 245.7164 | 381.2257 | 415.3243 | 354.616 | 303.9361 | 354.5715 | 266.6698
1636.3167 | 379.9245 | 245.8494 | 382.2531 | 415.3642 | 355.3207 | 304.0901 | 354.8984 | 266.6705
1637.3167 | 381.1297 | 245.9621 | 383.0169 | 415.801 | 355.8745 | 304.1742 | 355.2433 | 266.741
1638.3167 | 380.1794 | 246.0835 | 382.3147 | 414.5066 | 355.9065 | 304.3352 | 355.6145 | 266.9614
1639.3167 | 379.1113 | 246.2134 | 380.9108 | 412.47 | 354.9567 | 304.5034 | 355.9921 | 267.0518
1640.3167 | 379.5633 | 246.3236 | 378.5979 | 410.6555 | 354.1658 | 304.576 | 356.3885 | 267.1662
1641.3167 | 378.3787 | 246.4613 | 377.5578 | 409.2125 | 353.0019 | 304.7462 | 356.8193 | 267.2637
1642.3167 | 377.2699 | 246.5535 | 377.2893 | 408.4274 | 352.3111 | 304.9381 | 357.2484 | 267.3856
1643.3167 | 375.8772 | 246.6773 | 376.7828 | 407.5912 | 351.8355 | 305.0343 | 357.698 | 267.4804
1644.3167 | 376.2806 | 246.809 | 376.3609 | 406.7242 | 351.8113 | 305.1921 | 358.1517 | 267.6196
1645.3167 | 376.9917 | 246.921 | 375.6915 | 406.2384 | 351.3593 | 305.3921 | 358.6538 | 267.7357
1646.3167 | 375.5291 | 247.0387 | 375.2456 | 405.2602 | 350.5102 | 305.4452 | 359.1404 | 267.8724
1647.3167 | 374.3706 | 247.1462 | 374.5933 | 403.9856 | 349.3302 | 305.6603 | 359.6586 | 267.9766
1648.3167 | 373.1924 | 247.2817 | 373.5002 | 402.082 | 347.7632 | 305.7993 | 360.1326 | 268.0606
1649.3167 | 372.8727 | 247.3755 | 372.0899 | 400.3341 | 346.4121 | 305.9484 | 360.6261 | 268.1483
1650.3167 | 371.8692 | 247.488 | 370.7051 | 400.1498 | 346.5405 | 305.979 | 361.1126 | 268.2481
1651.3167 | 371.9885 | 247.6148 | 369.9607 | 399.103 | 346.0636 | 306.195 | 361.6418 | 268.3635
1652.3167 | 370.634 | 247.7567 | 369.8008 | 397.9222 | 345.2667 | 306.2803 | 362.2065 | 268.4483
1653.3167 | 370.9737 | 247.881 | 369.2962 | 397.3547 | 344.3641 | 306.4966 | 362.7723 | 268.5059
1654.3167 | 370.1335 | 248.0252 | 370.1722 | 397.239 | 344.1744 | 306.5784 | 363.3434 | 268.671
1655.3167 | 368.9975 | 248.1447 | 369.6612 | 396.0569 | 343.1193 | 306.7263 | 363.9472 | 268.7815
1656.3167 | 368.4523 | 248.282 | 368.7406 | 395.5165 | 342.1737 | 306.7529 | 364.5535 | 268.8983
1657.3167 | 366.8138 | 248.4069 | 369.0472 | 394.6695 | 341.1556 | 306.8394 | 365.1854 | 268.9658
1658.3167 | 365.871 | 248.5136 | 368.7905 | 394.1859 | 340.5483 | 306.9395 | 365.8079 | 269.1076
1659.3167 | 365.7198 | 248.647 | 369.6642 | 394.2238 | 340.8488 | 307.105 | 366.4603 | 269.2045
1660.3167 | 364.5229 | 248.7643 | 368.8764 | 394.0479 | 341.7132 | 307.2877 | 367.1092 | 269.3254
1661.3167 | 365.0865 | 248.9022 | 369.1244 | 394.8222 | 342.7905 | 307.2846 | 367.772 | 269.4193
1662.3167 | 368.456 | 249.0147 | 370.4812 | 396.0365 | 344.5455 | 307.3623 | 368.4505 | 269.5332
1663.3167 | 368.3618 | 249.1298 | 370.4021 | 395.8819 | 344.8488 | 307.5104 | 369.1338 | 269.6086
1664.3167 | 368.3328 | 249.2655 | 370.0486 | 395.5571 | 344.4759 | 307.5437 | 369.7987 | 269.7396
1665.3167 | 367.6179 | 249.3858 | 368.9008 | 394.6603 | 343.9505 | 307.7032 | 370.4836 | 269.9883
1666.3167 | 367.7055 | 249.455 | 369.0819 | 394.4104 | 343.4659 | 307.8132 | 371.1305 | 270.0236
1667.3167 | 366.7531 | 249.6064 | 368.0531 | 393.9819 | 343.4819 | 307.9431 | 371.8293 | 270.1465
1668.3167 | 367.9384 | 249.7216 | 368.8948 | 394.7599 | 343.4857 | 308.0592 | 372.5355 | 270.2776
1669.3167 | 367.6573 | 249.8543 | 369.3257 | 395.943 | 343.8898 | 308.0302 | 373.2638 | 270.362
1670.3167 | 368.0847 | 249.9771 | 371.6285 | 397.4222 | 343.5762 | 308.25 | 373.9789 | 270.4247
1671.3167 | 369.2026 | 250.079 | 372.8932 | 397.5645 | 344.4358 | 308.1032 | 374.6975 | 270.5289
1672.3167 | 369.8652 | 250.2222 | 373.8991 | 398.4862 | 345.3397 | 308.3325 | 375.4067 | 270.6443
1673.3167 | 370.0871 | 250.3492 | 375.0866 | 399.3343 | 346.4765 | 308.6221 | 376.1356 | 270.7189
1674.3167 | 370.4206 | 250.4756 | 375.4462 | 400.3053 | 346.9959 | 308.7606 | 376.8675 | 270.8172
1675.3167 | 371.1766 | 250.5847 | 375.6014 | 400.9889 | 346.5215 | 309.0623 | 377.5259 | 270.9885
1676.3167 | 371.6867 | 250.725 | 376.273 | 400.9882 | 346.2728 | 309.1307 | 378.2232 | 271.0894
1677.3167 | 374.1634 | 250.8446 | 375.2873 | 401.1398 | 346.0594 | 309.1017 | 378.9485 | 271.2893
1678.3167 | 376.5217 | 250.9725 | 374.8256 | 401.8364 | 345.7664 | 309.2046 | 379.6566 | 271.3922
1679.3167 | 377.9289 | 251.0949 | 375.3384 | 403.3908 | 345.4962 | 309.6465 | 380.387 | 271.4861
1680.3167 | 379.3579 | 251.2019 | 376.0106 | 405.2878 | 347.4088 | 309.7982 | 381.102 | 271.5359
1681.3167 | 379.5372 | 251.3312 | 377.1473 | 406.9152 | 348.7763 | 309.757 | 381.8706 | 271.6643
1682.3167 | 380.1751 | 251.4561 | 377.2255 | 407.9307 | 349.8632 | 310.033 | 382.6286 | 271.7052
1683.3167 | 381.7449 | 251.5841 | 377.3033 | 409.9043 | 350.4493 | 310.1729 | 383.37 | 271.7696
1684.3167 | 380.8304 | 251.7196 | 378.8635 | 411.9473 | 351.4281 | 310.2243 | 384.0125 | 271.9162
1685.3167 | 381.7431 | 251.8603 | 379.0857 | 413.9954 | 352.833 | 309.9447 | 384.6982 | 272.0771
1686.3167 | 384.4508 | 251.9959 | 380.5329 | 414.7679 | 352.8938 | 310.2653 | 385.3639 | 272.1247
1687.3167 | 385.7627 | 252.147 | 380.5225 | 415.4612 | 353.1981 | 310.3526 | 386.0099 | 272.3072
1688.3167 | 384.9035 | 252.213 | 382.0129 | 417.3292 | 353.8844 | 310.5155 | 386.6674 | 272.4268
1689.3167 | 384.8806 | 252.3679 | 382.4057 | 418.7557 | 353.2982 | 310.6479 | 387.2774 | 272.5063
1690.3167 | 386.3543 | 252.5039 | 384.9164 | 420.0463 | 353.6299 | 310.8379 | 387.85 | 272.679
1691.3167 | 387.4001 | 251.6321 | 385.248 | 419.9863 | 353.2281 | 311.0729 | 388.4028 | 272.8723
1692.3167 | 387.4677 | 251.7563 | 385.355 | 419.6554 | 353.2792 | 311.1861 | 388.947 | 272.9612
1693.3167 | 387.6293 | 251.8946 | 387.0895 | 420.259 | 353.569 | 311.3593 | 389.4639 | 273.1407
1694.3167 | 387.7589 | 251.9976 | 387.4 | 419.5569 | 354.5109 | 311.4539 | 389.9845 | 273.1755
1695.3167 | 388.3748 | 252.1179 | 386.4366 | 419.2116 | 354.5484 | 311.9294 | 390.4701 | 273.3084
1696.3167 | 387.9227 | 252.2645 | 385.149 | 417.1234 | 353.9737 | 311.5125 | 390.9087 | 273.4214
1697.3167 | 388.768 | 252.3771 | 383.1056 | 415.8449 | 353.8383 | 311.8203 | 391.339 | 273.4968
1698.3167 | 391.6834 | 252.5 | 382.7463 | 414.7575 | 354.0824 | 311.8282 | 391.7679 | 273.6759
1699.3167 | 390.1845 | 252.5718 | 381.5497 | 412.7594 | 353.7657 | 312.1002 | 392.1421 | 273.7555
1700.3167 | 387.8865 | 252.7115 | 379.9188 | 410.7362 | 353.0568 | 312.5842 | 392.5247 | 273.8493
1701.3167 | 386.4146 | 252.7395 | 379.5034 | 410.1194 | 352.0754 | 312.6428 | 392.8889 | 273.961
1702.3167 | 383.9801 | 252.8972 | 381.8656 | 410.0826 | 351.9188 | 312.4934 | 393.2515 | 274.0471
1703.3167 | 383.2943 | 252.9535 | 381.4323 | 409.3034 | 352.3068 | 312.6502 | 393.5707 | 274.1031
1704.3167 | 384.4253 | 253.0879 | 380.4013 | 408.4232 | 353.1044 | 312.8113 | 393.8885 | 274.0633
1705.3167 | 384.6318 | 253.1914 | 378.6863 | 406.9876 | 352.7501 | 312.8156 | 394.2012 | 274.2012
1706.3167 | 385.6441 | 253.3053 | 376.6303 | 405.9263 | 352.1848 | 313.0149 | 394.486 | 274.3019
1707.3167 | 382.9804 | 253.4347 | 375.5848 | 404.914 | 351.6128 | 313.0888 | 394.7597 | 274.4979
1708.3167 | 382.274 | 253.5487 | 375.082 | 404.1485 | 350.6504 | 313.168 | 395.0181 | 274.6277
1709.3167 | 382.6137 | 253.6846 | 374.3113 | 403.3095 | 349.9726 | 313.1908 | 395.273 | 274.7426
1710.3167 | 380.5864 | 253.7164 | 372.8211 | 401.8281 | 349.52 | 313.3399 | 395.5052 | 274.8686
1711.3167 | 378.348 | 253.8335 | 371.7715 | 399.8306 | 347.9638 | 313.4286 | 395.7065 | 274.9638
1712.3167 | 377.2085 | 253.9331 | 371.5617 | 398.3958 | 346.9032 | 313.747 | 395.9034 | 275.0774
1713.3167 | 375.3225 | 254.0416 | 371.0953 | 397.291 | 346.1593 | 313.7943 | 396.1134 | 275.1819
1714.3167 | 374.8642 | 254.1616 | 372.1936 | 396.9497 | 345.8091 | 313.8686 | 396.2909 | 275.2744
1715.3167 | 374.622 | 254.2775 | 373.5974 | 396.2214 | 345.4043 | 313.9479 | 396.4698 | 275.4208
1716.3167 | 372.8716 | 254.3696 | 373.5167 | 396.0604 | 344.8659 | 314.1212 | 396.6674 | 275.6624
1717.3167 | 373.6366 | 254.4696 | 372.6438 | 395.2797 | 344.5546 | 314.2205 | 396.8329 | 275.7268
1718.3167 | 374.6488 | 254.5719 | 371.615 | 395.4545 | 344.6008 | 314.2917 | 397.0083 | 275.8186
1719.3167 | 376.8727 | 254.6607 | 371.5737 | 395.0983 | 345.1229 | 314.5182 | 397.1801 | 275.918
1720.3167 | 377.506 | 254.812 | 372.5164 | 395.4521 | 345.248 | 314.4733 | 397.3485 | 276.0355
1721.3167 | 379.058 | 254.9361 | 373.6682 | 396.4152 | 345.8366 | 314.6613 | 397.5335 | 276.1323
1722.3167 | 378.6428 | 255.055 | 373.399 | 397.2305 | 346.9989 | 314.7878 | 397.707 | 276.2386
1723.3167 | 378.7399 | 255.1265 | 374.2282 | 397.714 | 347.5013 | 314.684 | 397.8908 | 276.3883
1724.3167 | 380.6936 | 255.1889 | 376.8175 | 398.8894 | 348.2201 | 314.9887 | 398.0584 | 276.4799
1725.3167 | 379.9485 | 255.3088 | 379.5484 | 400.0837 | 348.9138 | 315.3003 | 398.202 | 276.5757
1726.3167 | 378.9327 | 255.3455 | 382.74 | 402.1837 | 349.6733 | 315.3931 | 398.3718 | 276.6912
1727.3167 | 378.8333 | 255.5162 | 383.8522 | 402.0521 | 350.0281 | 315.6118 | 398.5371 | 276.7974
1728.3167 | 379.0479 | 255.6477 | 385.7031 | 402.3747 | 350.482 | 315.851 | 398.6652 | 276.9079
1729.3167 | 378.9918 | 255.7515 | 386.9692 | 402.9033 | 351.3256 | 316.0757 | 398.8262 | 277.0468
1730.3167 | 380.2512 | 255.8646 | 387.4321 | 403.5034 | 351.4442 | 316.3701 | 398.9831 | 277.1333
1731.3167 | 381.8396 | 255.932 | 391.2538 | 406.2299 | 353.8417 | 316.4808 | 399.1316 | 277.2104
1732.3167 | 383.2478 | 256.0172 | 393.0245 | 409.0097 | 354.4452 | 316.6155 | 399.2911 | 277.3262
1733.3167 | 385.6993 | 256.0909 | 394.6498 | 411.2701 | 354.697 | 317.0533 | 399.4314 | 277.4521
1734.3167 | 386.9176 | 256.1988 | 396.0759 | 413.6199 | 354.8016 | 317.2285 | 399.5678 | 277.5455
1735.3167 | 391.5624 | 256.283 | 397.3736 | 415.5222 | 355.1776 | 317.2892 | 399.725 | 277.6645
1736.3167 | 392.9536 | 256.3744 | 398.9961 | 418.3978 | 357.8822 | 317.6843 | 399.9171 | 277.7943
1737.3167 | 395.2824 | 256.5058 | 401.4097 | 421.0027 | 358.6799 | 317.7296 | 400.0678 | 277.9073
1738.3167 | 396.8074 | 256.6563 | 402.2749 | 422.0708 | 358.7138 | 318.1095 | 400.2113 | 278.0085
1739.3167 | 398.0473 | 256.8015 | 403.9923 | 423.2877 | 358.7052 | 318.33 | 400.3512 | 278.1184
1740.3167 | 397.1876 | 256.9363 | 405.1959 | 424.6645 | 358.8614 | 318.77 | 400.4856 | 278.2098
1741.3167 | 397.6296 | 257.0702 | 405.8172 | 426.3959 | 360.3408 | 318.9954 | 400.6299 | 278.3729
1742.3167 | 399.6775 | 257.1893 | 407.2569 | 428.7586 | 363.6325 | 319.3839 | 400.7822 | 278.4745
1743.3167 | 402.897 | 257.3277 | 407.5317 | 430.0801 | 366.1629 | 319.6041 | 400.9042 | 278.5704
1744.3167 | 405.3465 | 257.4491 | 407.0092 | 430.1016 | 367.5788 | 319.819 | 401.0449 | 278.688
1745.3167 | 405.2415 | 257.4713 | 404.6468 | 429.7588 | 368.0678 | 320.2707 | 401.1687 | 278.7976
1746.3167 | 407.6911 | 257.659 | 403.7192 | 429.7018 | 368.5408 | 320.3223 | 401.2995 | 278.8865
1747.3167 | 408.8501 | 257.7857 | 403.3043 | 430.6005 | 369.9464 | 320.2949 | 401.4383 | 278.9996
1748.3167 | 407.781 | 257.8239 | 403.4064 | 432.4743 | 372.2218 | 320.3334 | 401.5668 | 279.168
1749.3167 | 408.7044 | 257.9457 | 404.2421 | 434.6074 | 374.2808 | 320.6954 | 401.7113 | 279.2658
1750.3167 | 407.4569 | 258.1147 | 405.7712 | 435.7261 | 375.3842 | 320.7128 | 401.8062 | 279.377
1751.3167 | 408.9446 | 258.2674 | 405.887 | 437.5282 | 375.8233 | 321.0716 | 401.9287 | 279.4653
1752.3167 | 408.9099 | 258.3974 | 405.4063 | 436.8463 | 375.3832 | 321.3581 | 402.0693 | 279.5833
1753.3167 | 410.446 | 258.5381 | 404.8645 | 437.3163 | 375.7445 | 321.4039 | 402.1917 | 279.7024
1754.3167 | 409.7111 | 258.6736 | 404.2274 | 436.677 | 375.7038 | 321.3928 | 402.3326 | 279.7987
1755.3167 | 408.6146 | 258.8071 | 403.4037 | 435.1611 | 375.0081 | 321.7784 | 402.4618 | 279.92
1756.3167 | 410.0562 | 258.9648 | 402.5466 | 434.5239 | 374.387 | 321.8097 | 402.5729 | 280.0302
1757.3167 | 408.967 | 259.1044 | 401.9291 | 434.0524 | 372.8305 | 322.0549 | 402.6982 | 280.1415
1758.3167 | 407.0163 | 259.2546 | 405.2332 | 434.5775 | 371.5097 | 322.3006 | 402.8037 | 280.2445
1759.3167 | 406.4126 | 259.4034 | 407.8452 | 436.3256 | 371.5049 | 322.5661 | 402.9237 | 280.3552
1760.3167 | 406.7414 | 259.5427 | 410.1526 | 438.3877 | 372.3613 | 322.9447 | 403.0374 | 280.4783
1761.3167 | 407.6606 | 259.6802 | 410.7411 | 438.2929 | 373.2372 | 323.1065 | 403.1528 | 280.5942
1762.3167 | 409.4797 | 259.6565 | 410.6 | 438.2951 | 374.2556 | 323.2678 | 403.2591 | 280.706
1763.3167 | 407.2332 | 259.806 | 411.5124 | 440.3881 | 374.9255 | 323.5675 | 403.3801 | 280.8193
1764.3167 | 408.2126 | 259.9382 | 414.7776 | 442.1497 | 374.7311 | 323.8103 | 403.5041 | 280.939
1765.3167 | 409.9953 | 260.0437 | 414.764 | 443.3388 | 375.1259 | 324.2843 | 403.6245 | 281.0529
1766.3167 | 411.4567 | 260.1959 | 415.5306 | 444.1788 | 375.6056 | 324.0493 | 403.7482 | 281.1574
1767.3167 | 414.208 | 260.3519 | 415.6394 | 444.9873 | 376.5268 | 324.8362 | 403.8474 | 281.2664
1768.3167 | 415.9072 | 260.4842 | 417.682 | 446.1735 | 377.9096 | 324.6578 | 403.9748 | 281.3861
1769.3167 | 418.9392 | 260.6126 | 418.0317 | 445.9326 | 379.1534 | 324.8829 | 404.0976 | 281.5018
1770.3167 | 419.5277 | 260.7141 | 419.986 | 446.3597 | 378.8583 | 325.1897 | 404.1952 | 281.6083
1771.3167 | 416.8487 | 260.8506 | 419.9565 | 446.4085 | 378.1515 | 325.3811 | 404.306 | 281.7394
1772.3167 | 415.8985 | 260.9955 | 420.3857 | 446.5093 | 377.3842 | 325.8934 | 404.4026 | 281.8547
1773.3167 | 420.5253 | 261.145 | 424.1402 | 449.242 | 379.4862 | 326.3645 | 404.515 | 281.9765
1774.3167 | 423.5993 | 261.2731 | 425.7409 | 451.3621 | 379.6017 | 326.3854 | 404.659 | 282.0924
1775.3167 | 424.2148 | 261.3818 | 426.1617 | 453.1645 | 379.697 | 327.1701 | 404.7905 | 282.1923
1776.3167 | 423.1698 | 261.5118 | 426.6528 | 452.8613 | 379.3321 | 327.3545 | 404.893 | 282.3115
1777.3167 | 424.7663 | 261.6657 | 425.4779 | 453.2711 | 379.2157 | 327.9704 | 405.0145 | 282.4171
1778.3167 | 425.4594 | 261.8527 | 427.1752 | 454.0933 | 380.4217 | 328.2168 | 405.1216 | 282.5415
1779.3167 | 423.8065 | 262.0043 | 426.5385 | 453.1665 | 380.2271 | 328.4526 | 405.2552 | 282.6575
1780.3167 | 419.6922 | 262.0998 | 425.8846 | 453.9837 | 380.387 | 328.7355 | 405.3786 | 282.7719
1781.3167 | 423.6074 | 262.1313 | 426.8254 | 455.0867 | 382.3306 | 329.0145 | 405.4839 | 282.8715
1782.3167 | 421.398 | 262.3587 | 427.1892 | 455.6713 | 383.0683 | 329.2763 | 405.6208 | 282.993
1783.3167 | 421.4707 | 262.5202 | 429.6782 | 456.2865 | 383.8919 | 329.5557 | 405.7458 | 283.1136
1784.3167 | 423.9776 | 262.6791 | 429.3742 | 456.671 | 385.313 | 329.8351 | 405.8613 | 283.2479
1785.3167 | 427.2864 | 262.8424 | 430.011 | 457.912 | 388.0626 | 330.1174 | 405.981 | 283.3388
1786.3167 | 429.6756 | 262.9901 | 429.658 | 459.7486 | 388.6815 | 330.3517 | 406.1118 | 283.4642
1787.3167 | 428.3398 | 263.1147 | 427.8318 | 459.712 | 389.1712 | 330.4499 | 406.2279 | 283.5896
1788.3167 | 433.4885 | 263.2469 | 429.3654 | 461.7737 | 390.4258 | 330.583 | 406.3516 | 283.6918
1789.3167 | 439.0693 | 263.4088 | 429.1077 | 460.8885 | 390.2985 | 330.715 | 406.4834 | 283.7999
1790.3167 | 436.4127 | 263.5637 | 429.2811 | 459.5314 | 389.8036 | 331.032 | 406.6011 | 283.9198
1791.3167 | 442.9224 | 263.714 | 427.0746 | 457.8623 | 388.8677 | 331.2441 | 406.7487 | 284.0388
1792.3167 | 440.2004 | 263.8517 | 424.367 | 455.3288 | 387.833 | 331.6354 | 406.8675 | 284.1439
1793.3167 | 437.417 | 263.9835 | 420.9787 | 452.2052 | 386.522 | 331.7983 | 407.0075 | 284.2698
1794.3167 | 433.589 | 264.1164 | 419.3956 | 450.0605 | 384.8671 | 331.9218 | 407.1432 | 284.3598
1795.3167 | 437.3192 | 264.295 | 418.0576 | 448.7266 | 383.7599 | 331.8947 | 407.2757 | 284.4766
1796.3167 | 430.5668 | 264.4444 | 417.6994 | 446.8141 | 382.2216 | 332.1168 | 407.4162 | 284.6135
1797.3167 | 433.1507 | 264.5413 | 416.653 | 444.7355 | 380.6974 | 332.5326 | 407.5583 | 284.7183
1798.3167 | 427.4845 | 264.6633 | 415.3066 | 443.5516 | 378.9375 | 332.5642 | 407.6957 | 284.834
1799.3167 | 425.5425 | 264.7377 | 419.5199 | 445.3138 | 378.8392 | 333.1121 | 407.8342 | 285.0295
1800.3167 | 427.0459 | 264.9249 | 420.5507 | 444.9105 | 379.3914 | 333.4358 | 407.974 | 285.1444
1801.3167 | 425.4011 | 265.0717 | 421.5902 | 445.7114 | 379.7744 | 333.5868 | 408.1207 | 285.2674
1802.3167 | 423.4628 | 265.2112 | 421.7086 | 445.3923 | 380.1163 | 333.8324 | 408.2596 | 285.3929
1803.3167 | 421.8779 | 265.3498 | 419.7479 | 443.795 | 379.0776 | 334.0746 | 408.4093 | 285.5111
1804.3167 | 423.7617 | 265.5216 | 419.1742 | 444.1872 | 378.0655 | 334.0952 | 408.5677 | 285.6041
1805.3167 | 430.1881 | 265.684 | 421.5592 | 445.462 | 379.157 | 334.3818 | 408.7129 | 285.7562
1806.3167 | 427.1778 | 265.8416 | 421.2257 | 446.6388 | 379.9262 | 334.5143 | 408.8724 | 286.0164
1807.3167 | 429.0504 | 265.9995 | 421.1338 | 447.1419 | 380.4986 | 335.1578 | 409.0257 | 286.107
1808.3167 | 428.6953 | 266.162 | 421.9218 | 450.012 | 380.8184 | 335.4059 | 409.1844 | 286.1789
1809.3167 | 432.14 | 266.2881 | 424.6311 | 456.2241 | 382.9366 | 335.2138 | 409.3358 | 286.3045
1810.3167 | 431.746 | 266.4568 | 424.9163 | 457.4532 | 384.3375 | 335.5523 | 409.4923 | 286.5232
1811.3167 | 431.4567 | 266.5802 | 425.3421 | 457.7329 | 385.1262 | 335.9886 | 409.6572 | 286.6137
1812.3167 | 429.8031 | 266.7419 | 427.568 | 458.4597 | 386.5559 | 336.111 | 409.8147 | 286.7326
1813.3167 | 430.4689 | 266.909 | 429.9637 | 459.1627 | 387.2624 | 336.6432 | 409.9692 | 286.8284
1814.3167 | 429.3931 | 267.0575 | 432.1786 | 460.2744 | 387.9668 | 337.0317 | 410.1447 | 286.938
1815.3167 | 429.0772 | 267.2207 | 432.4388 | 459.5712 | 387.8809 | 337.4496 | 410.2842 | 287.0408
1816.3167 | 426.7423 | 267.3399 | 431.784 | 459.5158 | 387.3233 | 337.5652 | 410.4465 | 287.1638
1817.3167 | 427.3727 | 267.5097 | 432.2963 | 459.3799 | 386.1573 | 337.6017 | 410.6 | 287.3202
1818.3167 | 428.1009 | 267.4913 | 433.9101 | 459.5989 | 385.8063 | 338.5456 | 410.7587 | 287.4249
1819.3167 | 429.595 | 267.4145 | 436.9629 | 459.4038 | 385.1967 | 338.7324 | 410.9208 | 287.5356
1820.3167 | 426.3131 | 267.6306 | 437.22 | 471.8568 | 383.7331 | 339.0993 | 411.0956 | 287.6673
1821.3167 | 426.9327 | 267.818 | 437.1847 | 493.5206 | 382.1022 | 339.4211 | 411.2522 | 287.7761
1822.3167 | 426.6155 | 267.999 | 437.4072 | 491.0053 | 383.2607 | 339.6482 | 411.4067 | 287.9106
1823.3167 | 426.598 | 268.1794 | 438.0552 | 492.2079 | 386.1117 | 340.1585 | 411.5737 | 288.0007
1824.3167 | 430.0262 | 268.3332 | 438.7356 | 492.2591 | 386.6825 | 340.5381 | 411.7262 | 288.1132
1825.3167 | 430.4791 | 268.5276 | 440.5522 | 492.3024 | 386.723 | 340.7102 | 411.9018 | 288.2158
1826.3167 | 434.381 | 268.7015 | 441.9317 | 492.4804 | 385.8092 | 340.9631 | 412.0654 | 288.3403
1827.3167 | 436.5979 | 268.8781 | 443.5303 | 490.4635 | 385.075 | 341.3144 | 412.2291 | 288.4532
1828.3167 | 435.6445 | 269.0386 | 443.8581 | 490.2892 | 384.9751 | 341.6556 | 412.3996 | 288.5747
1829.3167 | 435.1498 | 269.1838 | 445.25 | 490.0575 | 384.932 | 342.2042 | 412.5533 | 288.6931
1830.3167 | 434.5695 | 269.3476 | 446.1075 | 490.5212 | 384.7189 | 342.6208 | 412.7403 | 288.8139
1831.3167 | 433.6388 | 269.4981 | 449.0766 | 491.8536 | 385.3455 | 342.9663 | 412.896 | 288.9448
1832.3167 | 436.7288 | 269.6104 | 448.4361 | 490.2878 | 385.011 | 342.9471 | 413.0688 | 289.075
1833.3167 | 437.1889 | 269.7825 | 449.76 | 493.3199 | 387.0567 | 343.4322 | 413.2298 | 289.1899
1834.3167 | 438.1921 | 269.9403 | 450.3438 | 493.2694 | 390.3423 | 344.03 | 413.4044 | 289.332
1835.3167 | 439.329 | 270.1041 | 449.7481 | 492.2376 | 391.242 | 344.3304 | 413.5712 | 289.4919
1836.3167 | 447.1168 | 270.2626 | 447.9652 | 492.1606 | 391.6887 | 344.8156 | 413.7412 | 289.6231
1837.3167 | 441.7167 | 270.4081 | 444.7756 | 489.5472 | 390.4736 | 345.1144 | 413.9245 | 289.741
1838.3167 | 447.1254 | 270.5598 | 444.5121 | 489.245 | 391.8955 | 345.5965 | 414.0807 | 289.8586
1839.3167 | 443.9554 | 270.6219 | 447.5418 | 490.1202 | 394.1009 | 345.9974 | 414.2657 | 290.0116
1840.3167 | 447.611 | 270.7324 | 448.1596 | 490.4173 | 395.3263 | 346.0687 | 414.4162 | 290.1633
1841.3167 | 445.7012 | 270.9164 | 447.3253 | 490.5192 | 394.9902 | 346.6208 | 414.5878 | 290.283
1842.3167 | 450.9343 | 271.0584 | 444.9443 | 490.439 | 395.8484 | 346.6968 | 414.772 | 290.3867
1843.3167 | 456.2236 | 271.0741 | 443.0442 | 490.7017 | 396.7639 | 347.2098 | 414.9329 | 290.5276
1844.3167 | 453.5837 | 271.1142 | 443.5063 | 490.2971 | 396.8915 | 347.6727 | 415.1191 | 290.6335
1845.3167 | 459.0508 | 271.3072 | 442.769 | 490.361 | 397.99 | 347.8166 | 415.2921 | 290.7615
1848.4729 | 453.7509 | 271.868 | 443.0048 | 488.6717 | 401.5932 | 349.3151 | 415.8397 | 291.1824
1849.3167 | 457.6097 | 272.0265 | 444.9591 | 490.612 | 403.595 | 349.5464 | 415.9899 | 291.2996
1850.3167 | 465.585 | 272.2208 | 446.7946 | 490.893 | 403.1333 | 350.0813 | 416.1494 | 291.4231
1851.3167 | 465.4421 | 272.3861 | 446.7864 | 489.9225 | 401.9441 | 350.4966 | 416.3405 | 291.5653
1854.4729 | 468.3191 | 272.9108 | 452.1613 | 495.053 | 405.854 | 351.8316 | 416.9127 | 292.1624
1855.3167 | 469.4947 | 273.0751 | 455.0242 | 495.7212 | 406.989 | 352.3152 | 417.064 | 292.2652
1856.3167 | 466.7517 | 273.2736 | 455.4535 | 496.3432 | 406.3715 | 352.6916 | 417.2455 | 292.3819
1860.4885 | 471.4377 | 273.7778 | 455.4923 | 508.7249 | 405.3649 | 355.16 | 418.0475 | 292.8279
1861.3167 | 472.0334 | 273.9702 | 455.0313 | 508.3777 | 404.9229 | 355.4281 | 418.1975 | 292.9739
1862.3167 | 472.9418 | 274.1734 | 455.7648 | 508.2287 | 404.6496 | 355.6606 | 418.3914 | 293.1201
1863.3167 | 470.6066 | 274.347 | 455.163 | 507.3485 | 404.2366 | 355.9576 | 418.6087 | 293.2153
1864.3167 | 475.1744 | 274.5499 | 455.831 | 507.8919 | 405.7665 | 356.4296 | 418.7915 | 293.346
1865.3167 | 477.1024 | 274.7409 | 454.7973 | 507.6023 | 407.4819 | 356.7001 | 419.0012 | 293.5423
1869.4729 | 480.7523 | 275.5017 | 450.746 | 508.2267 | 410.554 | 359.0214 | 419.8693 | 294.0924
1870.3167 | 478.7257 | 275.6223 | 451.2694 | 508.4007 | 412.0625 | 359.3386 | 420.032 | 294.2196
1871.3167 | 478.3718 | 275.5905 | 450.9448 | 508.4583 | 412.3116 | 359.7882 | 420.249 | 294.389
1872.3167 | 480.7374 | 275.7696 | 449.7658 | 509.9834 | 412.3483 | 360.1701 | 420.4728 | 294.5305
1873.3167 | 479.6378 | 275.9886 | 448.9616 | 509.5836 | 411.9494 | 360.8836 | 420.6747 | 294.6466
1874.3167 | 481.6459 | 276.1237 | 447.3394 | 537.4103 | 411.3087 | 361.2592 | 420.8886 | 294.8015
1875.3167 | 482.7783 | 276.2523 | 447.0083 | 554.1903 | 410.58 | 361.9279 | 421.1019 | 294.923
1876.3167 | 483.0957 | 276.5297 | 446.497 | 559.4689 | 409.4266 | 362.2278 | 421.3222 | 295.0379
1877.3167 | 484.1337 | 276.7378 | 447.7415 | 564.3653 | 409.5162 | 362.4074 | 421.5566 | 295.1815
1878.3167 | 484.1771 | 276.9077 | 449.679 | 578.8165 | 411.0979 | 362.6334 | 421.7827 | 295.3339
1879.3167 | 488.3013 | 277.011 | 447.5798 | 592.5585 | 412.6366 | 362.9752 | 422.0122 | 295.4847
1880.3167 | 493.9016 | 277.2438 | 446.6557 | 600.7326 | 415.262 | 363.4801 | 422.2474 | 295.595
1881.3167 | 497.1278 | 277.357 | 448.408 | 591.5923 | 415.8665 | 364.1591 | 422.4924 | 295.7499
1882.3167 | 497.8393 | 277.593 | 463.8292 | 586.6684 | 417.8833 | 364.51 | 422.7297 | 296.0271
1883.3167 | 499.6133 | 277.7969 | 465.411 | 577.6611 | 419.4963 | 365.0258 | 423.0061 | 296.1975
1884.3167 | 499.7773 | 277.9952 | 465.3373 | 570.8962 | 419.2038 | 365.2946 | 423.2382 | 296.3781
1885.3167 | 500.9532 | 278.0038 | 464.276 | 568.059 | 419.6079 | 365.6613 | 423.4858 | 296.4973
1889.4729 | 502.6166 | 278.7635 | 468.9343 | 621.6555 | 417.7221 | 367.4899 | 424.4874 | 297.2743
1890.3167 | 502.0104 | 278.7383 | 468.2149 | 629.4704 | 417.9216 | 367.8992 | 424.6935 | 297.3405
1891.3167 | 501.9289 | 279.0257 | 467.2243 | 616.9024 | 418.4618 | 368.4258 | 424.9373 | 297.4607
1895.4885 | 501.9805 | 279.8149 | 464.8056 | 582.9547 | 437.8781 | 369.4346 | 426.0796 | 298.1143
1896.3167 | 501.8303 | 280.0028 | 466.9913 | 578.4123 | 435.9314 | 369.6294 | 426.2971 | 298.2165
1897.3167 | 501.7633 | 280.0777 | 470.0136 | 573.2522 | 435.3745 | 370.0769 | 426.5555 | 298.3784
1898.3167 | 504.0003 | 280.2361 | 468.9469 | 568.0319 | 434.217 | 370.3652 | 426.8618 | 298.5729
1899.3167 | 505.7543 | 280.4742 | 467.1291 | 563.5046 | 433.3037 | 370.6669 | 427.1517 | 298.7432
1900.3167 | 507.4627 | 280.6278 | 467.1675 | 558.9776 | 432.2067 | 370.9329 | 427.474 | 298.8945
1901.3167 | 506.8256 | 280.8289 | 466.4433 | 555.5938 | 431.5474 | 371.2255 | 427.733 | 299.0397
1902.3167 | 507.5717 | 281.2607 | 468.4886 | 552.583 | 431.7313 | 371.5614 | 427.9961 | 299.2066
1903.3167 | 506.896 | 281.3934 | 467.8656 | 551.6114 | 432.6112 | 371.7834 | 428.2132 | 299.3485
1904.3167 | 507.7779 | 281.5537 | 467.4691 | 551.6527 | 431.9817 | 372.1382 | 428.4859 | 299.4609
1905.3167 | 508.2307 | 281.8304 | 468.7255 | 562.5735 | 430.5809 | 372.4605 | 428.741 | 299.6271
1906.3167 | 510.6083 | 282.059 | 469.0727 | 584.0012 | 429.7747 | 373.0595 | 429.0301 | 299.7947
1907.3167 | 510.0338 | 282.2151 | 469.4294 | 595.716 | 428.7486 | 373.4948 | 429.3645 | 299.9558
1908.3167 | 507.5071 | 282.5444 | 471.7803 | 598.7251 | 427.1912 | 374.1783 | 429.6501 | 300.1019
1909.3167 | 508.1035 | 282.7512 | 469.7355 | 604.4585 | 426.2173 | 374.6258 | 430.8173 | 300.2628
1910.3167 | 507.8341 | 283.0189 | 470.5509 | 611.8222 | 425.3326 | 375.0771 | 431.1642 | 300.4595
1911.3167 | 507.491 | 283.3769 | 472.9551 | 622.1542 | 424.3354 | 375.4194 | 431.5481 | 300.641
1912.3167 | 506.4209 | 283.6121 | 473.4888 | 624.3062 | 423.7691 | 376.0415 | 431.8233 | 300.8712
1913.3167 | 505.2998 | 284.0563 | 471.1843 | 625.5414 | 427.5537 | 376.5335 | 432.1743 | 301.0412
1914.3167 | 502.3302 | 284.3962 | 469.826 | 621.3264 | 428.3288 | 376.943 | 432.507 | 301.2142
1915.3167 | 499.0767 | 284.6859 | 468.8838 | 616.9878 | 426.9645 | 377.516 | 432.8061 | 301.4585
1916.3167 | 496.8536 | 284.9751 | 469.6155 | 616.4748 | 427.3313 | 379.1501 | 433.2409 | 301.7596
1917.3167 | 495.5051 | 284.9019 | 471.2586 | 616.9194 | 431.4405 | 382.3968 | 433.6761 | 301.8839
1918.3167 | 495.6316 | 285.2944 | 474.96 | 607.6114 | 437.2285 | 382.6825 | 434.0766 | 302.1636
1919.3167 | 496.6597 | 285.5224 | 474.1672 | 603.7041 | 440.7352 | 384.3882 | 434.6219 | 302.5394
1920.3167 | 497.1409 | 286.0062 | 473.1792 | 601.2229 | 445.2731 | 384.3154 | 434.8194 | 302.5259
1921.3167 | 498.3591 | 286.3919 | 471.6755 | 601.6036 | 446.9511 | 384.306 | 435.0458 | 302.5921
1922.3167 | 498.721 | 286.7185 | 471.503 | 598.916 | 453.8504 | 384.7009 | 435.3372 | 302.7652
1923.3167 | 497.8047 | 287.0117 | 470.0504 | 609.8582 | 460.7362 | 384.9261 | 435.6256 | 302.9211
1924.3167 | 496.2773 | 287.2524 | 470.8151 | 605.7566 | 466.2127 | 385.1999 | 435.9351 | 303.0847
1925.3167 | 496.0231 | 287.622 | 472.8656 | 600.6854 | 467.9126 | 385.6007 | 436.2322 | 303.3148
1926.3167 | 496.8564 | 287.8668 | 471.3033 | 597.5568 | 473.0552 | 385.6727 | 436.5666 | 303.3951
1927.3167 | 496.2279 | 288.1425 | 470.0925 | 593.8595 | 470.3056 | 385.9025 | 436.8726 | 303.6536
1928.3167 | 494.7172 | 288.4207 | 467.1327 | 589.5583 | 468.26 | 386.919 | 437.1912 | 303.7988
1929.3167 | 492.3051 | 288.5581 | 469.8049 | 587.0623 | 468.5772 | 387.8271 | 437.5181 | 304.0089
1930.3167 | 490.6636 | 288.8665 | 470.067 | 588.1746 | 468.9339 | 388.5652 | 437.8656 | 304.2267
1931.3167 | 489.8194 | 289.1622 | 471.5895 | 587.6098 | 468.3281 | 389.3152 | 438.2854 | 304.4675
1932.3167 | 489.4385 | 289.3794 | 473.3176 | 594.4564 | 469.2375 | 389.8366 | 438.7657 | 304.64
1933.3167 | 491.357 | 289.6248 | 473.5764 | 598.6405 | 482.2955 | 390.7785 | 439.4523 | 304.9389
1934.3167 | 493.1105 | 289.9546 | 473.5101 | 595.7993 | 502.2669 | 390.904 | 439.7592 | 305.0671
1935.3167 | 493.143 | 290.3329 | 472.6219 | 599.5541 | 513.1785 | 391.238 | 440.1475 | 305.2658
1936.3167 | 492.9608 | 290.6742 | 473.2944 | 602.6688 | 527.1966 | 391.5912 | 440.5384 | 305.6802
1937.3167 | 493.979 | 290.9424 | 471.1285 | 598.8948 | 536.2669 | 391.9026 | 440.7557 | 305.8371
1938.3167 | 496.4983 | 291.2657 | 469.5281 | 595.2515 | 536.0463 | 391.8882 | 440.7124 | 305.8966
1939.3167 | 497.2503 | 291.6208 | 468.3797 | 593.5413 | 532.4466 | 392.0726 | 440.7494 | 306.0528
1940.3167 | 497.3232 | 292.0223 | 467.1053 | 588.9447 | 528.4559 | 392.35 | 440.8735 | 306.2597
1941.3167 | 497.9187 | 292.2557 | 465.1412 | 582.1249 | 521.4634 | 392.481 | 441.0615 | 306.4675
1942.3167 | 498.0353 | 292.5094 | 466.1077 | 585.5201 | 514.2471 | 392.7597 | 441.2005 | 306.7593
1943.3167 | 499.2962 | 292.7783 | 470.1091 | 584.3514 | 508.6362 | 393.0606 | 441.3415 | 306.828
1944.3167 | 498.414 | 293.0555 | 470.0958 | 586.7087 | 502.3732 | 393.5819 | 441.4932 | 307.0242
1945.3167 | 500.3213 | 293.2449 | 472.7018 | 606.603 | 497.454 | 394.3214 | 441.6985 | 307.2162
1946.3167 | 513.2046 | 293.4556 | 474.4145 | 611.6208 | 494.4494 | 395.0203 | 441.9955 | 307.3925
1947.3167 | 523.3102 | 293.6235 | 475.0516 | 615.6236 | 490.6393 | 395.5733 | 442.2871 | 307.7181
1948.3167 | 522.0617 | 293.9932 | 475.9512 | 619.3254 | 489.1806 | 396.1162 | 442.5756 | 307.887
1949.3167 | 521.4975 | 294.2165 | 478.7543 | 628.958 | 498.142 | 396.5535 | 442.9158 | 308.1532
1950.3167 | 521.7301 | 294.4795 | 482.9583 | 627.9743 | 497.424 | 397.0229 | 443.2746 | 308.3595
1951.3167 | 521.4457 | 294.8018 | 486.3023 | 637.4132 | 502.8887 | 397.2597 | 443.6287 | 308.5117
1952.3167 | 521.4452 | 295.0298 | 489.4185 | 634.7324 | 502.596 | 397.5402 | 443.915 | 308.7134
1953.3167 | 521.118 | 295.2501 | 489.6202 | 631.4109 | 499.5107 | 397.8651 | 444.2246 | 308.9144
1954.3167 | 521.4413 | 295.4274 | 488.9588 | 628.2409 | 498.0541 | 398.1249 | 444.5592 | 309.0917
1955.3167 | 521.1239 | 295.4578 | 490.466 | 622.6095 | 497.5778 | 398.4074 | 444.8889 | 309.2998
1956.3167 | 519.8767 | 295.6312 | 488.3095 | 613.7688 | 494.268 | 398.6852 | 445.239 | 309.4902
1957.3167 | 520.6874 | 295.8064 | 490.2856 | 606.2312 | 489.5705 | 398.9992 | 445.6136 | 309.7512
1958.3167 | 519.9242 | 296.0083 | 493.7237 | 622.2188 | 499.9049 | 399.4902 | 445.9306 | 309.9916
1959.3167 | 519.2262 | 296.249 | 495.9753 | 624.4375 | 498.7789 | 399.9284 | 446.309 | 310.1477
1960.3167 | 520.9598 | 296.493 | 498.9666 | 621.2719 | 503.8013 | 400.4451 | 446.7341 | 310.3509
1961.3167 | 521.4042 | 296.7374 | 497.7132 | 615.9749 | 507.1986 | 400.873 | 447.1702 | 310.581
1962.3167 | 520.194 | 297.0053 | 497.5106 | 617.2836 | 521.5885 | 401.2903 | 447.6285 | 310.7568
1963.3167 | 521.798 | 297.226 | 496.32 | 624.4391 | 531.654 | 401.7946 | 448.0626 | 310.9819
1964.3167 | 521.0214 | 297.4215 | 499.1957 | 623.4755 | 534.1317 | 401.8438 | 448.4747 | 311.1714
1965.3167 | 521.8856 | 297.5926 | 495.5895 | 624.5291 | 536.9292 | 402.1545 | 448.9159 | 311.4283
1966.3167 | 521.951 | 297.6854 | 493.1689 | 617.8894 | 538.112 | 402.3659 | 449.317 | 311.6461
1967.3167 | 523.0431 | 297.7589 | 493.0434 | 619.0575 | 538.5662 | 402.4765 | 449.7506 | 311.8878
1968.3167 | 520.8252 | 297.8394 | 491.0206 | 611.1822 | 542.2644 | 402.865 | 450.2164 | 312.2092
1969.3167 | 518.2186 | 297.9598 | 492.0224 | 614.2603 | 551.2415 | 403.2297 | 450.6438 | 312.6102
1970.3167 | 517.2231 | 297.9937 | 490.644 | 613.5569 | 550.3779 | 403.1516 | 451.0579 | 312.7506
1971.3167 | 515.7368 | 297.8793 | 490.0566 | 625.2715 | 548.9442 | 403.0457 | 451.4443 | 312.9574
1972.3167 | 515.8275 | 297.9854 | 497.426 | 630.8379 | 549.3195 | 403.2725 | 451.8716 | 313.1938
1973.3167 | 516.5359 | 298.1315 | 498.0098 | 629.0079 | 548.8389 | 403.4129 | 452.4351 | 313.3707
1974.3167 | 518.6924 | 298.2413 | 495.3463 | 630.8455 | 542.1169 | 403.4436 | 452.8629 | 313.6086
1975.3167 | 519.3505 | 298.463 | 494.6465 | 621.9608 | 535.6412 | 403.4305 | 453.3242 | 313.7682
1976.3167 | 520.0895 | 298.5547 | 492.5928 | 619.4564 | 528.1299 | 403.6417 | 453.7238 | 314.0433
1977.3167 | 519.3841 | 298.7876 | 493.5704 | 617.5739 | 529.6676 | 403.9663 | 454.1594 | 314.2473
1978.3167 | 516.867 | 298.9944 | 490.8104 | 620.2672 | 534.9206 | 404.2588 | 454.7138 | 314.5
1979.3167 | 515.4054 | 299.1281 | 492.5067 | 619.5012 | 528.8294 | 404.8292 | 455.2427 | 314.6998
1980.3167 | 515.6507 | 299.3308 | 490.7019 | 619.2143 | 530.9076 | 404.9193 | 455.7253 | 314.9284
1981.3167 | 516.3938 | 298.99 | 491.2331 | 614.4644 | 527.3785 | 405.1696 | 456.3873 | 315.163
1982.3167 | 514.4465 | 299.1766 | 491.787 | 617.3004 | 522.1524 | 405.1727 | 457.0861 | 315.3991
1983.3167 | 513.9671 | 299.3843 | 494.6145 | 634.1072 | 516.3319 | 405.4311 | 457.7192 | 315.6777
1984.3167 | 514.2203 | 299.4918 | 497.1078 | 647.0117 | 510.6718 | 405.7036 | 458.2595 | 315.9253
1985.3167 | 516.2988 | 299.7259 | 503.7034 | 638.0828 | 516.4421 | 406.0707 | 459.0725 | 316.1931
1986.3167 | 516.6734 | 299.6826 | 503.0592 | 648.2381 | 519.6564 | 406.3961 | 459.7031 | 316.473
1987.3167 | 517.2417 | 299.7369 | 504.8651 | 645.7145 | 523.6956 | 406.9654 | 460.3098 | 316.7079
1988.3167 | 515.9584 | 299.7555 | 504.8765 | 647.4437 | 528.7664 | 407.1406 | 460.7816 | 316.9077
1989.3167 | 516.2325 | 299.6505 | 509.868 | 641.7757 | 524.1575 | 407.3292 | 461.2385 | 317.2999
1990.3167 | 516.1841 | 299.8217 | 511.0061 | 642.7902 | 518.6369 | 407.7932 | 461.5644 | 317.457
1991.3167 | 517.1198 | 299.8986 | 510.9427 | 637.0264 | 520.1243 | 407.9823 | 461.8357 | 317.6884
1992.3167 | 519.0489 | 299.7308 | 520.3589 | 633.6846 | 525.2625 | 408.0205 | 462.1108 | 317.8924
1993.3167 | 521.2275 | 299.9001 | 519.3942 | 631.772 | 526.2452 | 408.2996 | 462.3309 | 318.1987
1994.3167 | 521.8417 | 298.7187 | 514.2877 | 629.9211 | 520.6733 | 408.3672 | 462.6366 | 318.4798
1995.3167 | 522.2274 | 298.1721 | 510.7803 | 631.7891 | 516.978 | 408.4614 | 462.9626 | 318.7826
1996.3167 | 523.8051 | 297.1545 | 508.4101 | 631.5755 | 513.2054 | 408.7695 | 463.3435 | 319.0377
1997.3167 | 523.5001 | 296.1268 | 506.5245 | 631.5645 | 509.2883 | 408.9939 | 463.7239 | 319.3118
1998.3167 | 522.8782 | 296.3502 | 507.6145 | 633.8524 | 504.4941 | 409.2271 | 464.0851 | 319.5894
1999.3167 | 524.0822 | 296.5579 | 510.2524 | 635.4158 | 497.1428 | 409.5496 | 464.4867 | 319.7746
2000.3167 | 526.3665 | 296.7336 | 515.1327 | 633.2631 | 491.1632 | 409.8239 | 464.9178 | 320.0574
2001.3167 | 529.5342 | 296.9139 | 513.6829 | 639.4522 | 486.1066 | 410.1789 | 465.2628 | 320.1386
2002.3167 | 533.5401 | 297.1305 | 511.3662 | 638.4945 | 486.6016 | 410.3792 | 465.7372 | 320.4123
2003.3167 | 535.3765 | 297.3278 | 510.4422 | 631.7835 | 490.4744 | 410.6386 | 466.3161 | 320.869
2004.3167 | 535.4752 | 297.535 | 513.1142 | 630.7847 | 489.2268 | 410.9819 | 466.8101 | 321.2706
2005.3167 | 537.9248 | 297.7564 | 511.0099 | 626.2781 | 483.9668 | 412.0966 | 467.4343 | 321.8263
2006.3167 | 538.5375 | 297.9561 | 512.0197 | 625.8946 | 480.9026 | 411.3582 | 467.4513 | 321.7706
2007.3167 | 539.0939 | 298.1789 | 512.7011 | 621.7145 | 478.3623 | 411.5751 | 467.9192 | 322.0764
2008.3167 | 538.5877 | 298.4035 | 508.6582 | 609.9707 | 475.2028 | 412.0187 | 468.3113 | 322.3191
2009.3167 | 536.0941 | 298.6446 | 503.3809 | 601.499 | 470.9424 | 412.4629 | 468.9908 | 322.8467
2010.3167 | 537.061 | 298.8868 | 507.4653 | 607.547 | 467.3672 | 412.029 | 469.3463 | 323.0234
2011.3167 | 536.97 | 299.1586 | 517.4852 | 615.073 | 466.3906 | 412.7896 | 469.9702 | 323.3
2012.3167 | 536.9258 | 299.4209 | 522.5545 | 620.7754 | 464.0611 | 413.1893 | 470.4862 | 323.479
2013.3167 | 536.2643 | 299.6702 | 520.5411 | 621.7727 | 461.8214 | 413.4873 | 470.7759 | 323.7065
2014.3167 | 535.8534 | 299.947 | 518.5516 | 616.7127 | 460.3645 | 413.7712 | 471.2986 | 324.0465
2015.3167 | 536.2772 | 300.2439 | 519.1785 | 624.114 | 459.0543 | 414.0011 | 471.9339 | 324.3543
2016.3167 | 536.2882 | 300.5412 | 513.3381 | 623.8404 | 457.241 | 414.451 | 472.3758 | 324.688
2017.3167 | 535.7225 | 300.8308 | 508.9779 | 622.8292 | 456.0029 | 414.5166 | 472.8782 | 324.9107
2018.3167 | 536.8484 | 301.1307 | 505.972 | 616.8252 | 456.5087 | 414.8266 | 473.4007 | 325.2127
2019.3167 | 537.7179 | 301.4343 | 501.1772 | 624.685 | 455.9607 | 415.2035 | 473.921 | 325.5063
2020.3167 | 536.0116 | 301.7149 | 497.9173 | 633.9677 | 457.3279 | 415.613 | 474.2364 | 325.8769
2021.3167 | 536.0908 | 302.0037 | 495.5878 | 631.8895 | 458.754 | 416.1102 | 474.7089 | 326.2157
2022.3167 | 534.4981 | 302.2931 | 507.4562 | 632.8464 | 458.445 | 415.9455 | 475.2678 | 326.4201
2023.3167 | 533.5322 | 302.5742 | 514.7839 | 632.3437 | 458.6719 | 416.311 | 475.58 | 326.7138
2024.3167 | 535.1639 | 302.8493 | 514.8131 | 635.4304 | 458.509 | 416.7004 | 475.8697 | 326.9174
2025.3167 | 538.022 | 303.1298 | 534.2361 | 636.1335 | 460.7797 | 416.9637 | 476.3503 | 327.1924
2026.3167 | 539.2426 | 303.4137 | 533.1109 | 634.5993 | 463.1274 | 417.5554 | 476.5887 | 327.4738
2027.3167 | 539.943 | 303.6896 | 528.2966 | 630.5611 | 464.5056 | 417.8131 | 477.028 | 327.9122
2028.3167 | 539.1591 | 303.9952 | 526.5314 | 626.5548 | 464.4202 | 418.331 | 477.4181 | 328.2398
2029.3167 | 538.6929 | 304.2712 | 522.9127 | 625.8205 | 464.8891 | 418.206 | 477.5394 | 328.5429
2030.3167 | 539.5864 | 304.5503 | 520.4298 | 627.4429 | 464.4576 | 418.6994 | 477.916 | 328.9116
2031.3167 | 540.9612 | 304.8245 | 517.5389 | 632.2594 | 462.6233 | 418.7072 | 478.1682 | 329.1543
2032.3167 | 539.1388 | 305.1312 | 516.3176 | 633.9252 | 462.109 | 420.1105 | 478.7021 | 329.7707
2033.3167 | 539.3346 | 305.4013 | 516.4152 | 635.8739 | 462.078 | 420.4112 | 478.7993 | 330.1112
2034.3167 | 538.1399 | 305.6757 | 523.9421 | 637.0942 | 464.3545 | 420.4205 | 478.8426 | 330.3363
2035.3167 | 535.8049 | 305.9487 | 525.9669 | 651.1841 | 464.2161 | 421.3041 | 479.081 | 330.9774
2036.3167 | 537.2106 | 306.2156 | 519.3218 | 643.1722 | 461.7961 | 421.2403 | 479.1547 | 331.0957
2037.3167 | 541.0248 | 306.4959 | 516.049 | 633.3152 | 459.4598 | 421.6598 | 479.4104 | 331.4057
2038.3167 | 540.8232 | 306.7602 | 520.6105 | 624.9453 | 456.9386 | 420.6033 | 479.1914 | 331.2989
2039.3167 | 539.1133 | 307.0436 | 520.2025 | 644.6829 | 455.0031 | 420.7652 | 479.2568 | 331.5695
2040.3167 | 538.9808 | 307.3382 | 523.6681 | 636.6536 | 454.5792 | 421.4995 | 479.435 | 331.9068
2041.3167 | 538.937 | 307.6215 | 521.3545 | 639.499 | 455.7473 | 421.7092 | 479.7391 | 332.2637
2042.3167 | 536.8294 | 307.9033 | 522.6707 | 632.6016 | 455.2068 | 421.8976 | 480.0058 | 332.6011
2043.3167 | 536.4115 | 308.2047 | 523.7957 | 647.1349 | 454.8555 | 422.3408 | 480.08 | 332.8897
2044.3167 | 537.9052 | 308.5189 | 525.4563 | 642.454 | 455.614 | 423.1073 | 480.3191 | 333.3047
2045.3167 | 539.8878 | 308.8071 | 526.7557 | 647.049 | 456.9961 | 422.9705 | 480.4362 | 333.6898
2046.3167 | 541.1953 | 309.1313 | 529.9766 | 650.3894 | 458.4326 | 423.6235 | 480.8328 | 334.1002
2047.3167 | 543.5814 | 309.3866 | 528.5887 | 651.5355 | 458.6267 | 423.5471 | 480.9233 | 334.3827
2048.3167 | 543.6229 | 309.7271 | 527.8281 | 640.9112 | 457.4027 | 423.8035 | 481.1074 | 334.78
2049.3167 | 542.8483 | 309.9571 | 527.5921 | 645.238 | 457.5117 | 424.0364 | 481.2926 | 335.1323
2050.3167 | 541.9038 | 310.3357 | 529.1257 | 653.3679 | 456.0703 | 424.049 | 481.4875 | 335.5294
2051.3167 | 542.958 | 310.5514 | 531.7887 | 656.2668 | 455.1699 | 424.3557 | 481.7252 | 335.906
2052.3167 | 541.745 | 310.8706 | 529.9997 | 654.6165 | 453.4436 | 424.6672 | 482 | 336.2836
2053.3167 | 540.9699 | 311.1887 | 531.3674 | 659.3095 | 453.2026 | 424.9483 | 482.3119 | 336.6862
2054.3167 | 544.5349 | 311.5069 | 533.0813 | 660.1385 | 457.6684 | 425.5595 | 482.6506 | 337.0767
2055.3167 | 550.6949 | 311.8241 | 535.6845 | 667.676 | 460.7014 | 426.3089 | 483.0661 | 337.5421
2056.3167 | 551.109 | 312.1481 | 532.119 | 672.7067 | 465.8039 | 426.787 | 483.299 | 337.9749
2057.3167 | 552.8153 | 312.4825 | 537.4549 | 669.9904 | 466.6311 | 427.4794 | 483.7393 | 338.3924
2058.3167 | 553.078 | 312.8349 | 535.5732 | 670.3345 | 464.5906 | 427.6114 | 484.095 | 338.7818
2059.3167 | 565.4018 | 313.1976 | 543.0486 | 676.8 | 464.449 | 428.0369 | 484.4947 | 339.1957
2060.3167 | 567.941 | 313.5712 | 543.1761 | 664.9086 | 464.7246 | 428.2387 | 485.049 | 339.5825
2061.3167 | 571.758 | 313.9434 | 542.9256 | 662.4323 | 465.5195 | 428.3706 | 485.3779 | 340.0153
2062.3167 | 571.9608 | 314.3217 | 540.2603 | 657.4498 | 466.9185 | 428.5362 | 485.7338 | 340.4505
2063.3167 | 570.4101 | 314.7076 | 537.5631 | 660.838 | 465.3903 | 428.6629 | 486.066 | 340.8566
2064.3167 | 571.6438 | 315.0908 | 535.648 | 660.7763 | 463.9732 | 428.8877 | 486.3929 | 341.2896
2065.3167 | 571.3286 | 315.4818 | 533.4471 | 673.2274 | 462.6841 | 429.2274 | 486.6469 | 341.6942
2066.3167 | 570.1492 | 315.8686 | 532.6211 | 662.5259 | 460.611 | 429.8365 | 487.0203 | 342.1783
2067.3167 | 570.6839 | 316.2619 | 527.5835 | 656.6983 | 460.0923 | 429.5392 | 487.2617 | 342.5031
2068.3167 | 571.7297 | 316.6614 | 529.6883 | 652.4653 | 466.8229 | 429.8785 | 487.5719 | 343.0018
2069.3167 | 572.1843 | 317.0514 | 531.3463 | 673.6994 | 472.9718 | 430.3922 | 487.9371 | 343.4959
2070.3167 | 575.5302 | 317.4688 | 531.2109 | 682.6565 | 475.4492 | 431.3293 | 488.2584 | 344.0469
2071.3167 | 578.1448 | 317.8446 | 533.169 | 691.933 | 478.4495 | 431.7505 | 488.522 | 344.5575
2072.3167 | 583.4315 | 318.2616 | 538.2211 | 695.4132 | 483.6879 | 432.6615 | 488.832 | 344.996
2073.3167 | 588.5175 | 318.6596 | 541.4606 | 700.7586 | 485.1302 | 433.2203 | 489.1535 | 345.5057
2074.3167 | 589.7661 | 319.0467 | 544.3193 | 702.7004 | 484.2243 | 434.2048 | 489.5836 | 346.035
2075.3167 | 594.1419 | 319.4373 | 544.4965 | 703.0057 | 487.1354 | 435.0213 | 489.9332 | 346.4153
2076.3167 | 593.9985 | 319.8354 | 547.5287 | 703.6601 | 489.8374 | 435.8644 | 490.4702 | 346.9589
2077.3167 | 598.5126 | 320.2237 | 546.744 | 698.5797 | 497.3505 | 436.2964 | 490.8335 | 347.2937
2078.3167 | 599.4305 | 320.6337 | 546.7903 | 688.6539 | 500.3616 | 435.7495 | 491.3267 | 347.7247
2079.3167 | 597.8586 | 321.0441 | 542.7295 | 678.766 | 501.8798 | 435.5904 | 491.7551 | 348.2475
2080.3167 | 593.0807 | 321.4479 | 539.3763 | 671.1988 | 501.3 | 435.0729 | 492.0066 | 348.831
2081.3167 | 589.0479 | 321.8467 | 547.1384 | 671.553 | 503.3725 | 435.5841 | 492.308 | 349.0134
2082.3167 | 586.6724 | 322.2586 | 555.8784 | 672.6677 | 505.2807 | 435.538 | 492.777 | 349.3547
2083.3167 | 583.7588 | 322.665 | 555.866 | 672.3413 | 507.6957 | 435.7993 | 493.0778 | 349.776
2084.3167 | 580.7347 | 323.0617 | 552.2796 | 664.3257 | 506.7543 | 436.2219 | 493.5605 | 350.1929
2085.3167 | 578.7018 | 323.4716 | 551.2379 | 662.6775 | 519.6166 | 436.233 | 494.0109 | 350.5498
2086.3167 | 577.8075 | 323.8778 | 547.7173 | 658.5355 | 524.6687 | 436.2991 | 494.4623 | 350.9646
2087.3167 | 576.5801 | 324.2855 | 550.6348 | 655.2277 | 521.4047 | 436.3616 | 494.8868 | 351.4558
2088.801 | 575.6669 | 324.9017 | 553.8759 | 664.3708 | 530.3361 | 436.8051 | 495.4568 | 352.342
2089.3792 | 575.333 | 325.1218 | 558.4569 | 663.1707 | 530.7129 | 437.0733 | 495.6948 | 352.6138
2090.3948 | 574.3869 | 325.5412 | 554.616 | 659.1456 | 531.2633 | 437.2773 | 496.1481 | 353.3015
2091.426 | 573.3813 | 325.978 | 550.4478 | 657.7082 | 533.6447 | 437.387 | 496.545 | 353.5093
2092.4104 | 572.1787 | 326.379 | 549.0267 | 665.4268 | 542.9739 | 437.7995 | 496.9415 | 353.8821
2093.3167 | 571.8684 | 326.7499 | 548.8646 | 659.518 | 550.8712 | 438.2767 | 497.443 | 354.3103
2095.1604 | 570.7773 | 327.4815 | 547.1677 | 648.3994 | 572.886 | 438.5531 | 498.2474 | 355.3452
2095.6448 | 569.5301 | 327.6816 | 544.9506 | 645.2307 | 574.2593 | 438.4272 | 498.4999 | 355.5569
2096.3167 | 568.0758 | 327.9669 | 544.1152 | 642.9162 | 573.5543 | 438.3261 | 498.8721 | 355.992
2097.3167 | 568.4074 | 328.3802 | 542.6572 | 638.6156 | 581.9064 | 438.14 | 499.2518 | 357.8034
2098.3167 | 568.5282 | 328.8004 | 541.8078 | 640.7349 | 586.634 | 438.2438 | 499.6325 | 360.3323
2099.3167 | 569.434 | 329.2199 | 543.0471 | 638.415 | 583.8665 | 438.7166 | 499.9931 | 361.4359
2100.3167 | 570.6472 | 329.6468 | 546.3758 | 644.3622 | 581.0688 | 438.6268 | 500.3411 | 362.881
2101.3167 | 568.3756 | 330.0779 | 548.8126 | 639.4877 | 589.232 | 439.107 | 500.8105 | 364.0947
2102.3167 | 572.4837 | 330.4966 | 550.6787 | 646.5886 | 596.6182 | 438.9706 | 501.1873 | 365.0162
2103.3167 | 573.8935 | 330.9224 | 553.6123 | 646.7679 | 599.1262 | 439.6213 | 501.6107 | 365.8517
2104.3167 | 573.7221 | 331.3326 | 553.7101 | 645.322 | 595.8083 | 440.0737 | 502.181 | 366.7245
2105.3167 | 575.2568 | 331.7567 | 557.5346 | 651.9616 | 591.4374 | 440.4492 | 502.6496 | 367.5335
2106.3167 | 575.6622 | 332.1748 | 558.5799 | 648.0175 | 582.6595 | 440.5796 | 503.1584 | 368.3305
2107.3167 | 580.8192 | 332.5737 | 553.5253 | 644.1036 | 585.677 | 441.0709 | 503.5962 | 369.1522
2108.3167 | 580.5973 | 332.995 | 550.3588 | 639.0344 | 590.9786 | 441.2403 | 504.1012 | 369.9413
2109.3167 | 579.3788 | 333.4066 | 552.3231 | 637.5876 | 601.9749 | 442.1401 | 504.5722 | 370.6338
2110.3167 | 579.0162 | 333.8137 | 547.8617 | 636.7826 | 612.1733 | 442.541 | 505.1184 | 371.1726
2111.3167 | 577.7561 | 334.212 | 552.3464 | 648.4197 | 616.6818 | 442.96 | 505.5914 | 371.6342
2112.3167 | 578.4856 | 334.5858 | 553.0138 | 647.1602 | 622.7738 | 443.8678 | 506.1605 | 372.1423
2113.3167 | 580.1237 | 334.9692 | 552.2095 | 650.9521 | 627.3534 | 443.9469 | 506.7261 | 372.6662
2114.3167 | 583.3417 | 335.3336 | 549.5402 | 649.8965 | 629.7493 | 444.8363 | 507.2704 | 373.385
2115.3167 | 582.1005 | 335.6995 | 549.8235 | 645.1892 | 631.2589 | 445.0206 | 507.8423 | 374.1152
2116.3167 | 583.547 | 336.0604 | 550.8366 | 650.0354 | 623.8408 | 444.7788 | 508.3426 | 374.6308
2117.3167 | 585.4088 | 336.4376 | 553.4976 | 654.9431 | 633.4735 | 445.4449 | 508.9351 | 375.3933
2118.3167 | 589.6563 | 336.831 | 558.3432 | 663.7116 | 643.4525 | 445.9158 | 509.5444 | 375.6746
2119.3167 | 591.3797 | 337.2461 | 556.4271 | 678.444 | 639.6112 | 446.954 | 510.1202 | 376.2753
2120.3167 | 595.5218 | 337.6345 | 558.6337 | 680.7338 | 638.6995 | 447.6014 | 510.7571 | 376.7729
2121.3167 | 595.3947 | 337.9839 | 555.1979 | 676.5467 | 637.6654 | 448.5414 | 511.4002 | 377.4175
2122.3167 | 596.0927 | 338.3583 | 549.552 | 669.6033 | 629.7402 | 449.0418 | 512.0156 | 378.078
2123.3167 | 594.4689 | 338.7456 | 550.3178 | 666.7462 | 618.5775 | 448.5625 | 512.6497 | 378.576
2124.3167 | 593.45 | 339.1983 | 556.891 | 669.662 | 607.8351 | 447.9085 | 513.1453 | 379.0781
2125.3167 | 590.7301 | 339.6227 | 558.6799 | 668.9298 | 615.4019 | 447.9134 | 513.7103 | 379.7463
2126.3323 | 590.7431 | 340.0186 | 570.7819 | 671.7399 | 614.5 | 448.0799 | 514.2732 | 380.2906
2127.3167 | 590.0826 | 340.4155 | 567.3057 | 668.9712 | 618.0839 | 448.3433 | 514.8911 | 380.9935
2128.3323 | 591.2696 | 340.8492 | 560.8612 | 666.5419 | 621.7771 | 448.8309 | 515.4857 | 382.7867
2129.3167 | 589.8256 | 341.2976 | 555.5864 | 653.0895 | 614.0532 | 448.935 | 516.1481 | 383.4316
2130.3167 | 590.2951 | 341.65 | 553.3627 | 647.8398 | 613.776 | 449.4641 | 516.6179 | 384.1576
2131.3167 | 592.0464 | 341.9837 | 549.9715 | 648.5313 | 605.5551 | 449.6242 | 517.1897 | 385.0231
2132.3323 | 592.4577 | 342.3751 | 542.3664 | 638.3662 | 595.4701 | 449.4563 | 517.6826 | 385.7991
2133.3167 | 591.312 | 342.7364 | 540.7137 | 640.7041 | 586.2101 | 449.3855 | 518.1483 | 386.1066
2134.3167 | 589.6882 | 343.1411 | 542.1151 | 640.6689 | 580.9861 | 449.264 | 518.7023 | 386.6899
2135.3167 | 586.082 | 343.4698 | 543.6664 | 642.7779 | 575.6765 | 449.5138 | 519.1039 | 387.1871
2136.3167 | 585.0006 | 343.874 | 543.1199 | 637.8259 | 570.7016 | 449.4135 | 519.641 | 387.6698
2137.3167 | 583.5007 | 344.2512 | 539.6245 | 638.9091 | 564.6073 | 449.2705 | 520.0953 | 388.3237
2138.3167 | 584.3728 | 344.632 | 542.1579 | 646.6604 | 566.534 | 449.2867 | 520.4803 | 389.2598
2139.3167 | 584.5245 | 344.9999 | 541.5536 | 641.4424 | 576.4715 | 449.606 | 521.0693 | 390.8056
2140.3167 | 585.4981 | 345.3487 | 539.8481 | 636.6825 | 572.0014 | 449.3753 | 521.5001 | 391.5292
2141.3167 | 586.5064 | 345.7209 | 540.9379 | 647.2086 | 568.6424 | 450.9071 | 520.8127 | 392.8117
2142.3167 | 586.4151 | 346.2388 | 541.5388 | 647.6035 | 563.4251 | 452.1394 | 518.4547 | 394.6919
2143.3167 | 586.55 | 346.5605 | 537.9068 | 644.3093 | 556.7894 | 452.2814 | 516.4501 | 395.8311
2144.3167 | 584.2894 | 346.8682 | 536.8864 | 639.8208 | 557.7995 | 452.5699 | 514.5867 | 396.8565
2145.3167 | 581.7516 | 347.2016 | 533.9951 | 629.4616 | 552.7229 | 453.5482 | 513.102 | 396.9672
2146.3167 | 581.2174 | 347.5538 | 535.0539 | 627.4835 | 547.4407 | 453.8986 | 511.8069 | 397.4419
2147.3167 | 581.1623 | 347.9013 | 539.8798 | 622.1993 | 541.0787 | 454.2978 | 510.8735 | 397.8633
2148.3167 | 582.2087 | 348.2981 | 540.8561 | 619.845 | 536.2659 | 454.6727 | 510.204 | 398.5125
2149.3167 | 583.9541 | 348.7317 | 538.8434 | 614.4891 | 531.2858 | 455.2659 | 509.8125 | 399.1172
2150.3167 | 584.2782 | 349.0173 | 536.2076 | 608.7563 | 526.9279 | 455.9638 | 509.4181 | 400.2922
2151.3167 | 582.7509 | 349.3603 | 537.0337 | 603.8283 | 523.1789 | 456.4669 | 509.1762 | 401.0758
2152.3167 | 582.5537 | 349.9021 | 534.711 | 598.8955 | 519.6855 | 457.0562 | 509.0388 | 401.9563
2153.3167 | 584.0228 | 350.2866 | 535.7609 | 598.43 | 517.1401 | 457.8243 | 508.9666 | 402.7269
2154.3167 | 584.2711 | 350.6568 | 535.4985 | 595.2604 | 515.7007 | 458.4999 | 508.9366 | 403.5827
2155.3167 | 581.8815 | 351.2722 | 535.0453 | 589.0983 | 512.2616 | 459.115 | 508.9748 | 404.0442
2156.3167 | 582.8193 | 351.7457 | 535.7364 | 590.7576 | 508.1115 | 459.8773 | 509.2152 | 405.2144
2157.3167 | 590.1705 | 353.0918 | 538.3232 | 592.2231 | 507.3019 | 460.151 | 509.4374 | 405.8343
2158.3167 | 590.6514 | 353.6164 | 549.777 | 593.0744 | 506.7805 | 460.0698 | 509.6687 | 406.244
2159.3167 | 593.4922 | 354.0391 | 552.4345 | 597.9712 | 506.3986 | 459.7518 | 509.6851 | 406.6449
2160.3167 | 591.2499 | 354.5102 | 558.253 | 598.9315 | 505.3265 | 459.8836 | 510.0819 | 407.0184
2161.3167 | 591.4838 | 355.121 | 556.1586 | 604.8564 | 504.3915 | 460.0721 | 510.2192 | 407.7043
2162.3479 | 589.9999 | 355.9063 | 552.5379 | 604.3153 | 504.2306 | 460.6471 | 510.5291 | 408.2912
2163.3167 | 588.7787 | 356.5873 | 549.7644 | 609.0981 | 505.0234 | 461.8101 | 510.7419 | 409.0073
2164.3167 | 588.9896 | 357.3379 | 548.0308 | 612.1907 | 503.7301 | 462.2201 | 510.9764 | 409.614
2165.3167 | 589.8458 | 358.0278 | 543.5956 | 611.2724 | 503.1458 | 462.7211 | 511.3099 | 410.1005
2166.3323 | 588.1808 | 358.6184 | 542.9718 | 612.5985 | 501.8778 | 463.1605 | 511.6124 | 410.2531
2167.3167 | 588.1935 | 359.0987 | 543.3492 | 614.2708 | 501.3954 | 463.8635 | 511.9359 | 410.4278
2168.3167 | 591.9265 | 359.6407 | 542.3727 | 615.0373 | 501.1047 | 464.7833 | 512.2744 | 410.8066
2169.3167 | 591.7949 | 360.2982 | 543.0714 | 614.4066 | 500.4817 | 465.4205 | 512.6187 | 411.572
2170.3167 | 591.336 | 360.8317 | 541.2821 | 612.3293 | 499.0175 | 465.2204 | 513.0773 | 412.1297
2171.3167 | 590.7212 | 361.2888 | 539.1269 | 609.9978 | 497.0022 | 464.1761 | 513.3769 | 412.3554
2172.3167 | 589.1647 | 361.8703 | 539.1939 | 612.8079 | 494.9967 | 462.9482 | 513.8525 | 412.7793
2173.3167 | 589.2227 | 362.4227 | 539.0116 | 616.3235 | 495.8496 | 462.4379 | 514.2153 | 413.257
2174.3167 | 588.6895 | 362.851 | 540.3842 | 617.9788 | 497.8812 | 461.435 | 514.7403 | 413.8287
2175.3167 | 588.5836 | 363.3981 | 542.9129 | 621.7066 | 497.2993 | 461.0559 | 515.2334 | 414.2121
2176.3167 | 589.0111 | 363.868 | 540.7228 | 622.066 | 499.4959 | 461.1117 | 515.6847 | 414.5189
2177.3167 | 589.6999 | 364.3337 | 538.6284 | 623.0943 | 499.144 | 461.6316 | 516.1096 | 414.7926
2178.3167 | 589.1263 | 364.8625 | 535.6473 | 629.8616 | 498.5385 | 461.7999 | 516.6571 | 415.0704
2179.3167 | 590.4586 | 365.3329 | 539.259 | 631.1093 | 497.0043 | 462.1502 | 517.1584 | 415.6899
2180.3167 | 591.5138 | 365.846 | 539.0392 | 631.2598 | 495.027 | 462.563 | 517.5431 | 416.0606
2181.3167 | 592.1234 | 366.3644 | 540.9196 | 629.3895 | 494.5222 | 462.7426 | 518.0059 | 416.5345
2182.3167 | 590.4625 | 366.8288 | 538.0912 | 621.1165 | 493.2114 | 463.0733 | 518.5884 | 416.4258
2183.3167 | 592.405 | 367.298 | 538.412 | 621.6907 | 495.6396 | 463.0629 | 519.0296 | 415.2389
2184.3167 | 591.3766 | 367.7826 | 533.254 | 617.8247 | 497.6099 | 463.3315 | 519.4433 | 415.3497
2185.3167 | 591.0593 | 368.2286 | 529.9071 | 615.9279 | 500.5506 | 463.5676 | 519.7831 | 415.6238
2186.3167 | 591.7534 | 368.6566 | 526.6389 | 619.2691 | 503.4278 | 463.6635 | 520.18 | 416.0357
2187.3167 | 593.055 | 369.0243 | 527.0562 | 618.6031 | 504.6043 | 463.6231 | 520.4241 | 416.1527
2188.3167 | 597.2083 | 369.4066 | 526.8407 | 623.9048 | 504.2564 | 464.3552 | 521.0994 | 416.6213
2189.3167 | 596.676 | 369.8528 | 529.8442 | 627.1152 | 505.1432 | 463.4421 | 521.1607 | 416.5625
2190.3167 | 595.2852 | 370.1963 | 531.5808 | 626.4393 | 503.9809 | 463.5339 | 521.505 | 416.8253
2191.3167 | 594.5397 | 370.6446 | 531.8407 | 622.522 | 503.0398 | 463.552 | 521.9321 | 417.132
2192.3167 | 596.441 | 371.1206 | 531.8933 | 622.8109 | 502.4182 | 463.3533 | 522.3141 | 417.354
2193.3167 | 595.3908 | 371.4669 | 531.1473 | 627.1782 | 503.0494 | 463.079 | 522.7497 | 417.5926
2194.3167 | 598.7111 | 371.9478 | 533.9683 | 627.2042 | 506.1066 | 463.5946 | 523.1658 | 417.9173
2195.3167 | 599.6721 | 372.3033 | 530.6977 | 630.3982 | 506.6639 | 463.9126 | 523.7564 | 418.1709
2196.3167 | 600.6053 | 372.8026 | 531.807 | 629.2369 | 508.7755 | 463.9133 | 524.1374 | 418.4929
2197.3167 | 609.1218 | 373.2142 | 530.8122 | 626.7976 | 507.4592 | 463.9431 | 524.5428 | 418.7119
2198.3167 | 605.028 | 373.6591 | 534.2288 | 629.4237 | 506.3294 | 464.0363 | 524.9483 | 418.9368
2199.3167 | 602.1385 | 374.0696 | 535.7888 | 627.0342 | 506.8494 | 464.278 | 525.2885 | 419.2242
2200.3167 | 599.484 | 374.4714 | 538.2745 | 620.3845 | 505.1689 | 464.6527 | 525.6813 | 419.4939
2201.3167 | 599.1518 | 374.9305 | 541.9109 | 634.859 | 502.6243 | 465.0494 | 526.0236 | 419.7069
2202.3167 | 599.0059 | 375.3314 | 543.8814 | 629.5778 | 500.6583 | 465.5033 | 526.3514 | 420.0271
2203.3167 | 598.4746 | 375.6691 | 541.1057 | 630.1512 | 499.526 | 465.5325 | 526.6825 | 420.3113
2204.3167 | 598.5596 | 376.1195 | 536.5416 | 627.9793 | 498.3868 | 465.7939 | 527.0491 | 420.6441
2205.3167 | 596.8728 | 376.4668 | 534.978 | 627.5903 | 497.4332 | 466.0289 | 527.4705 | 421.2682
2206.3167 | 596.0128 | 376.8261 | 537.54 | 626.716 | 495.4505 | 466.2947 | 527.8514 | 422.1746
2207.3167 | 597.9648 | 377.2539 | 539.9512 | 624.7443 | 494.3189 | 466.8037 | 528.1095 | 423.4383
2208.3167 | 602.2188 | 377.2958 | 542.0089 | 622.7953 | 491.4802 | 467.3376 | 528.4722 | 423.6616
2209.3167 | 602.2161 | 377.6179 | 543.6463 | 633.9389 | 489.1809 | 467.9575 | 528.8386 | 423.8447
2210.3167 | 601.9641 | 378.0146 | 548.0473 | 632.3315 | 487.308 | 468.2575 | 529.1686 | 423.7051
2211.3167 | 604.6695 | 378.4396 | 549.3847 | 642.3735 | 485.5349 | 468.4628 | 529.5564 | 424.0141
2212.3167 | 606.9087 | 378.8798 | 548.8535 | 643.4649 | 484.3189 | 468.8517 | 529.9322 | 424.3463
2213.3167 | 606.7073 | 378.9894 | 549.7686 | 638.7539 | 483.1809 | 469.3349 | 530.3503 | 424.6956
2214.3167 | 610.6876 | 379.39 | 548.8571 | 636.0554 | 482.4083 | 469.7695 | 530.7853 | 425.1526
2215.3167 | 613.7185 | 379.8011 | 550.5737 | 636.0372 | 480.7 | 470.1575 | 531.187 | 425.6281
2216.3167 | 616.1149 | 380.2314 | 550.5702 | 637.5608 | 483.0634 | 470.4984 | 531.6425 | 426.0356
2217.3167 | 611.0892 | 380.6041 | 549.6749 | 631.2308 | 484.4669 | 470.7261 | 532.069 | 426.4505
2218.3167 | 609.7946 | 380.3994 | 551.5226 | 645.1896 | 483.5839 | 471.1397 | 532.4579 | 427.0141
2219.3167 | 611.5605 | 380.8704 | 556.425 | 654.9094 | 484.2515 | 471.4733 | 532.8823 | 427.2898
2220.3167 | 611.1223 | 381.104 | 556.9933 | 649.5118 | 483.2133 | 471.8126 | 533.2516 | 429.9485
2221.3167 | 611.7574 | 381.5772 | 556.5755 | 646.9413 | 483.5948 | 472.1598 | 533.4761 | 429.6754
2222.3323 | 612.0913 | 382.0029 | 555.5094 | 644.5088 | 485.72 | 472.4228 | 533.6596 | 429.4161
2223.3167 | 617.5489 | 382.2967 | 556.9465 | 639.72 | 488.9036 | 472.7442 | 533.8642 | 429.7172
2224.3167 | 621.0587 | 382.5819 | 554.5655 | 638.0459 | 493.0215 | 472.9903 | 534.1273 | 430.2328
2225.3167 | 626.6904 | 382.9463 | 550.2177 | 640.0017 | 495.1568 | 473.0999 | 534.4509 | 430.6519
2226.3167 | 623 | 383.3657 | 548.9592 | 639.2151 | 493.4546 | 473.2561 | 534.7738 | 430.9
2227.3167 | 618.7696 | 383.8107 | 549.6228 | 638.1175 | 492.7638 | 473.483 | 535.1501 | 431.1396
2228.3167 | 621.3765 | 384.1956 | 547.8936 | 633.2668 | 494.5437 | 473.7816 | 535.5447 | 431.4173
2229.3167 | 624.9502 | 384.5474 | 547.673 | 634.4787 | 496.1266 | 473.9796 | 535.946 | 431.8884
2230.3167 | 630.0408 | 384.8292 | 549.3057 | 630.7259 | 501.0602 | 474.2395 | 536.3629 | 432.1398
2231.3167 | 627.2306 | 385.1272 | 548.6214 | 630.2951 | 503.6247 | 474.2623 | 536.7832 | 432.5025
2232.3167 | 624.0678 | 385.356 | 545.5799 | 627.4486 | 503.1286 | 474.6184 | 537.2231 | 432.8284
2233.3167 | 620.1377 | 385.6988 | 545.4167 | 623.138 | 501.021 | 474.7953 | 537.6502 | 433.1076
2234.3167 | 622.0476 | 385.749 | 542.7224 | 618.39 | 499.7023 | 474.9677 | 538.0799 | 433.3351
2235.3167 | 623.5089 | 386.162 | 541.0736 | 621.0536 | 499.2953 | 475.1563 | 538.4961 | 433.5673
2236.3167 | 619.6436 | 386.4112 | 540.0054 | 621.9389 | 499.2797 | 475.377 | 538.9095 | 433.8304
2237.3167 | 617.4254 | 386.739 | 540.7247 | 622.5127 | 497.494 | 475.484 | 539.375 | 434.0813
2238.3167 | 615.5897 | 387.1394 | 540.4167 | 621.4232 | 496.8437 | 475.6809 | 539.8358 | 434.2664
2239.3167 | 625.5404 | 387.5501 | 539.9289 | 621.0277 | 495.6863 | 475.7459 | 540.3394 | 434.5229
2240.3167 | 631.6821 | 386.2371 | 536.1695 | 616.5629 | 495.1934 | 475.9916 | 540.8268 | 434.8243
2241.3167 | 636.343 | 386.8511 | 536.7536 | 618.8193 | 494.2014 | 476.0392 | 541.3291 | 435.1396
2242.3167 | 635.9762 | 387.3209 | 535.8433 | 618.1097 | 493.947 | 476.2119 | 541.7799 | 435.5116
2243.3167 | 631.5855 | 387.4143 | 534.6402 | 611.9869 | 492.7294 | 476.5562 | 542.2543 | 435.86
2244.3167 | 630.0742 | 387.8474 | 537.1712 | 608.5145 | 490.7313 | 476.8271 | 542.7021 | 436.1475
2245.3167 | 628.0666 | 388.0808 | 536.6109 | 602.6763 | 489.2523 | 477.1492 | 543.1744 | 436.3523
2246.3167 | 627.0505 | 388.0857 | 530.8755 | 597.1013 | 487.2764 | 477.3799 | 543.6137 | 436.5945
2247.3167 | 625.6617 | 388.3355 | 525.8747 | 595.8641 | 485.83 | 477.5485 | 544.0815 | 436.7634
2248.3167 | 621.9096 | 388.0202 | 530.275 | 598.571 | 486.3115 | 477.6366 | 544.52 | 436.9315
2249.3167 | 617.7151 | 387.772 | 533.8662 | 594.9625 | 487.3497 | 477.8966 | 544.9928 | 437.0536
2250.3167 | 614.6345 | 387.5635 | 537.1766 | 591.8136 | 486.9826 | 478.1387 | 545.4675 | 437.3407
2251.3167 | 611.199 | 387.4672 | 540.3157 | 590.5907 | 486.8552 | 478.4906 | 545.9739 | 437.4884
2252.3167 | 611.4223 | 387.7817 | 541.4912 | 588.3576 | 486.68 | 479.1888 | 546.6394 | 437.8409
2253.3167 | 608.6708 | 388.0382 | 541.5665 | 595.2685 | 485.3525 | 479.0196 | 546.963 | 437.8657
2254.3167 | 607.8366 | 388.0499 | 541.9449 | 600.5853 | 484.5763 | 479.3231 | 547.4215 | 437.9956
2255.3167 | 611.9656 | 388.0945 | 542.1129 | 599.1246 | 484.7483 | 479.5895 | 547.8879 | 438.1835
2256.3167 | 609.8744 | 388.1979 | 544.6085 | 601.7225 | 484.1277 | 479.8507 | 548.3878 | 438.3756
2257.3167 | 609.0946 | 388.3123 | 548.5917 | 608.1654 | 485.1723 | 480.0645 | 548.8977 | 438.6408
2258.3167 | 609.0315 | 388.9074 | 548.9292 | 604.2722 | 485.1487 | 480.157 | 549.3527 | 438.7426
2259.3167 | 614.1549 | 389.3297 | 544.935 | 598.8807 | 484.4565 | 480.2498 | 549.8783 | 438.9146
2260.3167 | 621.1598 | 389.6172 | 541.0484 | 599.4072 | 483.9199 | 480.2224 | 550.4546 | 439.1311
2261.3167 | 626.9948 | 389.8272 | 542.7435 | 605.3677 | 483.5285 | 480.1253 | 550.9601 | 439.2574
2262.3167 | 630.0938 | 390.1054 | 539.5187 | 609.7816 | 485.8201 | 480.2632 | 551.4811 | 439.4165
2263.3167 | 629.7257 | 390.4012 | 541.6205 | 614.3461 | 488.6984 | 480.3852 | 552.0153 | 439.5929
2264.3167 | 628.8361 | 390.4254 | 541.3572 | 612.033 | 491.2298 | 480.3066 | 552.4675 | 439.7398
2265.3167 | 629.9239 | 390.7888 | 540.0104 | 617.4042 | 493.1486 | 480.2337 | 553.0121 | 439.9035
2266.3167 | 623.8144 | 391.0482 | 541.5586 | 618.635 | 492.2289 | 480.3904 | 553.5701 | 440.1189
2267.3167 | 624.4441 | 391.1753 | 545.2594 | 621.993 | 492.3928 | 480.9026 | 554.1851 | 440.3908
2268.3167 | 633.9046 | 391.5113 | 542.8786 | 623.604 | 493.5372 | 480.5173 | 554.5291 | 440.3304
2269.3167 | 632.1815 | 391.6046 | 544.5447 | 624.1014 | 493.3169 | 480.4657 | 555.0211 | 440.4469
2270.3167 | 630.7834 | 391.979 | 541.5141 | 625.9959 | 493.8663 | 480.4387 | 555.5897 | 440.5322
2271.3167 | 632.3735 | 392.3315 | 540.621 | 629.3719 | 494.0429 | 480.4723 | 556.1823 | 440.6546
2272.3167 | 626.1633 | 392.3999 | 542.5028 | 626.6556 | 493.0865 | 480.4467 | 556.7795 | 440.7792
2273.3167 | 623.1466 | 392.6642 | 541.3289 | 622.1516 | 491.8732 | 480.4089 | 557.3635 | 440.9031
2274.3167 | 620.1518 | 392.8406 | 541.142 | 618.2243 | 491.6701 | 480.4025 | 557.9538 | 441.0295
2275.3167 | 620.0997 | 393.0586 | 547.2139 | 617.9416 | 489.761 | 480.4059 | 558.491 | 441.1916
2276.3167 | 624.4891 | 393.2729 | 548.311 | 621.4529 | 489.8312 | 480.5136 | 559.1052 | 441.2939
2277.3167 | 623.846 | 393.425 | 543.7085 | 613.4936 | 489.0162 | 480.5842 | 559.7647 | 441.3897
2278.3167 | 622.6514 | 393.6729 | 543.7009 | 609.3485 | 487.4054 | 480.2964 | 560.4141 | 441.5247
2279.3167 | 624.8213 | 393.8553 | 542.7472 | 604.3162 | 485.1089 | 480.1483 | 561.072 | 441.6268
2280.3167 | 627.2757 | 394.022 | 539.5728 | 603.3743 | 483.7675 | 479.99 | 561.728 | 441.7254
2281.3167 | 627.6073 | 394.346 | 540.6366 | 606.35 | 485.9128 | 479.8881 | 562.358 | 441.8289
2282.3167 | 632.3207 | 394.5988 | 540.8828 | 608.5733 | 488.5843 | 479.7897 | 563.0131 | 442.0058
2283.3167 | 632.1272 | 394.867 | 540.2007 | 607.8417 | 490.4476 | 479.7158 | 563.6998 | 442.1349
2284.3167 | 637.8774 | 395.0896 | 539.7897 | 609.9371 | 493.5787 | 479.6134 | 564.424 | 442.261
2285.3167 | 636.4808 | 395.3056 | 538.5895 | 616.2591 | 495.6748 | 479.4511 | 565.1308 | 442.4257
2286.3167 | 640.5933 | 395.6116 | 549.6489 | 622.1339 | 499.0412 | 479.494 | 565.795 | 442.5563
2287.3167 | 643.2117 | 395.831 | 554.4731 | 627.854 | 503.3056 | 479.5939 | 566.5708 | 442.7019
2288.3167 | 635.8568 | 395.9856 | 556.1038 | 632.8396 | 502.1815 | 479.7487 | 567.4105 | 442.854
2289.3167 | 630.2147 | 396.1898 | 559.602 | 635.8191 | 504.5329 | 479.8367 | 568.2302 | 442.9897
2290.3167 | 628.09 | 396.3984 | 559.8446 | 641.4066 | 508.1837 | 479.8974 | 569.1123 | 443.113
2291.3167 | 625.5335 | 396.6431 | 560.9102 | 644.4888 | 510.2427 | 479.9857 | 569.9171 | 443.2635
2292.3167 | 628.3126 | 396.8727 | 561.1749 | 646.0465 | 510.9865 | 480.131 | 570.5925 | 443.4164
2293.3167 | 632.8902 | 397.1017 | 569.575 | 643.0868 | 512.7964 | 480.1989 | 571.3129 | 443.5138
2294.3167 | 634.0893 | 397.2663 | 570.9725 | 640.0399 | 511.9316 | 480.4849 | 572.0272 | 443.6556
2295.3167 | 634.9558 | 397.4822 | 574.0529 | 644.208 | 511.6256 | 480.8222 | 572.6887 | 443.7653
2296.3167 | 635.5671 | 397.6924 | 577.1262 | 645.9073 | 512.0954 | 481.1869 | 573.3494 | 443.9059
2297.3167 | 641.0068 | 397.8936 | 578.5678 | 650.4319 | 511.9685 | 481.5498 | 574.1711 | 443.9998
2298.3167 | 643.6062 | 398.0811 | 580.1751 | 650.2017 | 512.078 | 481.7723 | 574.9595 | 444.1317
2299.3167 | 642.8517 | 398.2551 | 579.8003 | 650.5044 | 512.7056 | 481.9691 | 575.7303 | 444.2456
2300.3167 | 649.0283 | 398.5352 | 579.5536 | 652.2685 | 517.2174 | 482.1965 | 576.3919 | 444.3674
2301.3167 | 652.4619 | 398.7622 | 578.259 | 648.1353 | 521.8002 | 482.4039 | 577.1228 | 444.5056
2302.3167 | 652.5108 | 398.9434 | 575.9999 | 645.5688 | 522.8863 | 482.5577 | 577.921 | 444.6592
2303.3167 | 646.9078 | 399.0777 | 576.2282 | 643.9003 | 519.8694 | 482.785 | 578.5206 | 444.7753
2304.3167 | 642.1272 | 399.2635 | 580.5407 | 652.1067 | 518.6151 | 483.04 | 579.0082 | 444.8614
2305.3167 | 641.5881 | 399.4855 | 582.5992 | 653.25 | 517.602 | 483.4121 | 579.5298 | 444.9614
2306.3167 | 642.2825 | 399.7876 | 582.6238 | 654.0501 | 516.8061 | 483.8528 | 580.1133 | 445.0768
2307.3167 | 646.6916 | 399.9762 | 582.0024 | 652.6648 | 518.9264 | 484.5295 | 580.8417 | 445.4234
2308.3167 | 649.19 | 400.1336 | 584.8773 | 659.3929 | 526.772 | 484.2692 | 581.1925 | 445.3214
2309.3167 | 648.349 | 400.2384 | 585.0625 | 662.6921 | 530.736 | 484.5686 | 581.6183 | 445.4459
2310.3167 | 649.1325 | 400.4083 | 584.9325 | 660.3606 | 531.0625 | 485.1801 | 582.475 | 445.6869
2311.3167 | 648.8114 | 400.5548 | 582.0447 | 661.0396 | 531.5635 | 485.0146 | 582.934 | 445.6869
2312.3167 | 648.2714 | 400.6646 | 583.9138 | 659.4892 | 531.6265 | 485.1456 | 583.3798 | 445.7952
2313.3167 | 651.4439 | 400.8016 | 584.0425 | 661.5184 | 533.614 | 485.602 | 583.8379 | 445.9505
2314.3167 | 650.2996 | 400.7797 | 585.7177 | 658.4944 | 532.356 | 486.2405 | 584.3899 | 446.059
2315.3167 | 646.3044 | 400.8938 | 587.9762 | 655.5084 | 530.1632 | 486.6609 | 585.0087 | 446.2216
2316.3167 | 643.929 | 401.061 | 587.8993 | 651.3484 | 528.141 | 487.0779 | 585.6036 | 446.358
2317.3167 | 642.8813 | 401.163 | 585.8333 | 651.3781 | 525.3294 | 487.3723 | 586.0458 | 446.5093
2318.3167 | 641.1029 | 401.2395 | 581.2238 | 650.5132 | 525.4771 | 487.6694 | 586.4678 | 446.5908
2319.3167 | 639.206 | 401.3573 | 582.2476 | 650.1055 | 527.5858 | 487.9283 | 586.9005 | 446.7526
2320.3167 | 638.8128 | 401.4579 | 582.5853 | 650.3953 | 529.3344 | 488.1811 | 587.514 | 446.9081
2321.3167 | 638.638 | 401.5958 | 584.9358 | 648.9105 | 530.4942 | 488.4267 | 587.8687 | 447.0532
2322.3167 | 645.2178 | 401.7388 | 585.7478 | 654.9509 | 532.72 | 488.7554 | 588.4725 | 447.1671
2323.3167 | 648.3936 | 401.8389 | 586.5352 | 660.0038 | 533.9165 | 488.9041 | 589.0686 | 447.3345
2324.3167 | 650.8231 | 401.9439 | 586.5879 | 659.2925 | 534.5447 | 489.2323 | 589.4257 | 447.4867
2325.3167 | 658.1983 | 402.0451 | 588.2062 | 658.8157 | 535.7937 | 489.5036 | 589.8576 | 447.6496
2326.3167 | 653.3545 | 405.5404 | 590.3903 | 663.3531 | 535.9402 | 489.7594 | 590.4002 | 447.7729
2327.3167 | 652.2966 | 407.4095 | 591.1796 | 665.3651 | 537.7423 | 489.8822 | 590.8655 | 447.8878
2328.3167 | 653.3894 | 408.6181 | 593.5723 | 668.6854 | 538.7058 | 490.1433 | 591.3651 | 448.0194
2329.3167 | 654.6836 | 409.119 | 590.8241 | 672.0875 | 540.0882 | 490.3626 | 591.9152 | 448.1436
2330.3167 | 657.9122 | 409.4055 | 589.5056 | 674.2827 | 542.0411 | 490.5037 | 592.4673 | 448.2622
2331.3167 | 663.8149 | 409.7151 | 590.9549 | 678.2973 | 542.7369 | 490.7182 | 592.9179 | 448.4493
2332.3167 | 661.5271 | 409.8823 | 592.5096 | 678.1272 | 538.9937 | 491.1641 | 593.4437 | 448.6329
2333.3167 | 665.0584 | 409.9161 | 593.3412 | 678.7301 | 536.7389 | 491.5943 | 593.8872 | 448.7615
2334.3167 | 665.4743 | 409.9934 | 595.7748 | 679.6198 | 536.9088 | 492.1069 | 594.4865 | 448.9143
2335.3167 | 663.8717 | 410.0581 | 594.8208 | 677.0168 | 537.7683 | 492.4385 | 595.0495 | 449.0794
2336.3167 | 661.4879 | 410.1086 | 594.1084 | 675.4471 | 539.6938 | 492.7976 | 595.6702 | 449.2204
2337.3167 | 660.7128 | 410.1634 | 593.0823 | 672.9846 | 541.2241 | 493.4255 | 596.0823 | 449.3617
2338.3167 | 661.5639 | 410.2491 | 595.026 | 677.0129 | 542.7972 | 493.9945 | 596.5265 | 449.5221
2339.3167 | 658.4548 | 410.4549 | 595.0838 | 683.0171 | 544.1734 | 494.7925 | 596.8749 | 449.6067
2340.3167 | 657.9838 | 410.5858 | 594.2462 | 680.4904 | 543.9808 | 495.5709 | 597.1937 | 449.7402
2341.3167 | 661.919 | 410.6992 | 597.565 | 683.2936 | 544.2788 | 496.484 | 597.41 | 449.8979
2342.3167 | 661.8787 | 410.8122 | 598.4537 | 679.8041 | 544.5394 | 497.7716 | 597.5805 | 449.9989
2343.3167 | 659.9954 | 410.9547 | 599.4184 | 677.1025 | 543.3654 | 498.9477 | 597.6109 | 450.1657
2344.3167 | 658.5839 | 411.0634 | 598.9521 | 672.3608 | 545.1104 | 499.9901 | 597.9077 | 450.2714
2345.3167 | 652.7091 | 411.1645 | 599.8675 | 671.0884 | 544.1655 | 501.0556 | 597.9502 | 450.4029
2346.3167 | 653.5706 | 411.3179 | 602.876 | 681.821 | 540.7811 | 502.179 | 597.9189 | 450.5428
2347.3167 | 660.7743 | 411.4163 | 602.8933 | 687.9482 | 538.1499 | 503.1598 | 597.9654 | 450.694
2348.3167 | 671.6074 | 411.5442 | 607.4641 | 690.0049 | 544.8591 | 503.8952 | 598.0803 | 450.8355
2349.3167 | 670.1965 | 411.7087 | 615.8618 | 690.2559 | 544.8582 | 504.8923 | 598.1719 | 450.92
2350.3167 | 673.3637 | 411.8342 | 620.0058 | 689.8138 | 548.688 | 505.9196 | 598.2911 | 451.0388
2351.3167 | 669.1804 | 411.9678 | 620.5988 | 692.1632 | 548.5283 | 506.8852 | 598.4599 | 451.1885
2352.3167 | 674.8714 | 412.1248 | 620.8368 | 694.5906 | 546.7303 | 507.676 | 598.6237 | 451.3204
2353.3167 | 674.4347 | 412.3288 | 620.3258 | 690.9422 | 543.9013 | 508.5672 | 598.7982 | 451.4319
2354.3167 | 672.3166 | 412.4062 | 623.1074 | 692.4193 | 541.6386 | 509.1291 | 599.0738 | 451.5429
2355.3167 | 667.6934 | 412.5008 | 622.2798 | 694.2227 | 539.1797 | 509.8148 | 599.2647 | 451.7085
2356.3167 | 664.1796 | 412.6636 | 619.0601 | 693.8286 | 536.2096 | 510.453 | 599.4966 | 451.874
2357.3167 | 663.2101 | 412.8501 | 616.4672 | 688.7018 | 537.0175 | 511.2032 | 599.7599 | 452.0424
2358.3167 | 667.7383 | 412.9017 | 620.04 | 689.5555 | 539.2071 | 511.7191 | 599.9943 | 452.1792
2359.3167 | 669.7023 | 412.9908 | 622.1764 | 686.7649 | 542.447 | 512.5361 | 600.223 | 452.3247
2360.3167 | 670.0743 | 413.0993 | 622.1967 | 686.8144 | 544.8272 | 513.468 | 600.5164 | 452.5064
2361.3167 | 672.2088 | 413.2344 | 625.0855 | 689.0791 | 544.2097 | 514.2914 | 600.8555 | 452.7194
2362.3167 | 681.7437 | 413.2929 | 624.2941 | 687.5394 | 549.2476 | 515.3065 | 601.1036 | 452.8409
2363.3167 | 687.9744 | 413.4733 | 621.9354 | 683.8177 | 552.607 | 516.2528 | 601.5271 | 452.9734
2364.3167 | 690.969 | 413.6328 | 621.2429 | 681.7467 | 555.7004 | 517.3842 | 601.8028 | 453.1599
2365.3167 | 689.6144 | 413.8317 | 623.4966 | 684.0596 | 555.9425 | 518.6904 | 602.0933 | 453.358
2366.3167 | 685.7355 | 413.9992 | 622.2687 | 680.5689 | 554.0894 | 520.0223 | 602.3819 | 453.4918
2367.3167 | 687.4077 | 414.2175 | 622.2299 | 680.0829 | 555.7076 | 520.8746 | 602.6917 | 453.6149
2368.3167 | 684.8375 | 414.4408 | 616.9495 | 678.8679 | 556.0811 | 521.765 | 602.9715 | 453.7929
2369.3167 | 688.6925 | 414.9542 | 614.5985 | 677.342 | 553.7722 | 522.3949 | 603.2732 | 454.0097
2370.3167 | 683.595 | 415.1637 | 614.9465 | 681.696 | 555.2665 | 522.882 | 603.4309 | 454.1873
2371.3167 | 683.7213 | 416.3683 | 614.2689 | 682.4552 | 558.3417 | 523.5124 | 603.7219 | 454.3991
2372.3167 | 683.6101 | 416.4247 | 612.4312 | 686.1984 | 560.7205 | 524.0305 | 604.065 | 454.5638
2373.3167 | 684.4021 | 416.473 | 612.5677 | 690.0815 | 564.4179 | 524.4485 | 604.2835 | 454.7954
2374.3167 | 681.3378 | 416.0998 | 614.7561 | 688.5192 | 565.6444 | 525.0303 | 604.5974 | 454.9787
2375.3167 | 679.1885 | 416.0962 | 613.7494 | 688.9341 | 565.3052 | 525.9526 | 604.9291 | 455.3096
2376.3167 | 674.7132 | 415.3648 | 615.5835 | 688.9434 | 564.5088 | 526.2645 | 604.9719 | 455.3964
2377.3167 | 674.597 | 415.4616 | 615.2375 | 691.428 | 564.6628 | 526.9776 | 605.062 | 455.5797
2378.3167 | 673.2432 | 415.2843 | 613.9812 | 689.7926 | 564.8191 | 527.4624 | 605.211 | 455.722
2379.3167 | 672.4965 | 415.4336 | 613.8766 | 686.9565 | 563.2737 | 528.0135 | 605.3575 | 455.8708
2380.3167 | 671.7249 | 415.4975 | 607.2817 | 684.0196 | 563.8775 | 528.3705 | 605.433 | 455.9881
2381.3167 | 677.0118 | 415.6659 | 607.2721 | 680.3904 | 563.1096 | 528.7026 | 605.4095 | 456.1327
2382.3167 | 673.9846 | 415.8447 | 607.451 | 677.9143 | 562.4703 | 529.2673 | 605.618 | 456.4098
2383.3167 | 672 | 415.9807 | 608.3466 | 676.9218 | 559.7583 | 529.6057 | 605.6228 | 456.5545
2384.3167 | 671.6165 | 416.1272 | 607.0964 | 680.79 | 559.479 | 530.0266 | 605.5849 | 456.6657
2385.3167 | 671.8047 | 416.2987 | 609.4503 | 678.2054 | 558.9087 | 530.2843 | 605.6794 | 456.7941
2386.3167 | 672.458 | 416.4641 | 608.0749 | 676.1293 | 557.7405 | 530.6436 | 605.7601 | 456.9121
2387.3167 | 668.7053 | 416.672 | 608.226 | 675.8507 | 557.5761 | 531.1064 | 605.9122 | 457.0523
2388.3167 | 669.0754 | 416.9185 | 606.9772 | 674.8557 | 556.7557 | 531.2271 | 606.1091 | 457.1724
2389.3167 | 667.6813 | 416.988 | 606.191 | 674.0037 | 555.5709 | 531.3006 | 606.2634 | 457.3353
2390.3167 | 666.2713 | 417.0741 | 605.4828 | 676.9989 | 555.0214 | 531.4853 | 606.4155 | 457.5588
2391.3167 | 666.7029 | 417.2509 | 604.2045 | 677.9632 | 555.5545 | 531.838 | 606.6226 | 457.7695
2392.3167 | 665.3518 | 417.255 | 604.0352 | 680.0106 | 555.6227 | 531.8727 | 606.8201 | 457.9782
2393.3167 | 665.3199 | 417.3472 | 605.5878 | 677.0313 | 555.706 | 532.3485 | 607.1619 | 458.2376
2394.3167 | 673.5431 | 417.6311 | 607.24 | 676.441 | 554.6143 | 533.6987 | 607.6549 | 458.8049
2395.3167 | 679.7322 | 417.6222 | 607.1406 | 674.4019 | 555.3684 | 533.0864 | 607.5718 | 458.7162
2396.3167 | 689.9012 | 417.8124 | 608.3867 | 677.57 | 553.8527 | 533.3116 | 607.7452 | 458.9275
2397.3167 | 694.5151 | 417.8978 | 608.0299 | 673.2871 | 549.9747 | 533.5818 | 608.0151 | 459.106
2398.3167 | 695.5757 | 417.9979 | 612.6494 | 674.7052 | 549.0063 | 533.8903 | 608.3008 | 459.2758
2399.3167 | 694.5758 | 418.1466 | 611.9302 | 678.1627 | 548.4834 | 534.0958 | 608.5389 | 459.4278
2400.3167 | 694.7267 | 418.2646 | 609.366 | 674.6387 | 551.3574 | 534.3366 | 608.7868 | 459.6278
2401.3167 | 700.8233 | 418.3854 | 618.7919 | 673.2172 | 554.071 | 534.4351 | 609.0638 | 459.8454
2402.3167 | 692.9538 | 418.5058 | 621.4548 | 670.2594 | 554.9646 | 534.8519 | 609.3469 | 460.0851
2403.3167 | 691.0788 | 418.5891 | 618.6777 | 669.1417 | 557.2462 | 534.8816 | 609.5712 | 460.2727
2404.3167 | 687.5042 | 418.7325 | 614.533 | 668.7027 | 558.1195 | 535.0704 | 609.8611 | 460.4606
2405.3167 | 685.0138 | 418.8443 | 610.4738 | 669.1217 | 557.7238 | 535.4987 | 610.0577 | 460.645
2406.3167 | 680.5593 | 418.9504 | 605.4354 | 666.464 | 558.1423 | 535.7238 | 610.2978 | 460.8607
2407.3167 | 680.2079 | 419.0328 | 599.6122 | 667.259 | 561.1908 | 535.7228 | 610.5464 | 461.0982
2408.3167 | 684.0494 | 419.2317 | 599.0244 | 665.1878 | 563.0287 | 535.6884 | 610.6868 | 461.3187
2409.3167 | 677.4435 | 419.3306 | 601.906 | 665.1171 | 561.4786 | 535.9809 | 610.9591 | 461.6134
2410.3167 | 678.8984 | 419.449 | 604.3054 | 667.3426 | 560.2402 | 536.0528 | 611.1917 | 461.7567
2411.3167 | 677.2736 | 419.5951 | 606.5497 | 665.5623 | 559.9072 | 536.315 | 611.4592 | 461.9326
2412.3167 | 686.7613 | 419.7177 | 605.6406 | 664.297 | 559.6885 | 536.4915 | 611.5804 | 462.091
2413.3167 | 690.4385 | 419.8482 | 607.9567 | 668.9173 | 560.6345 | 537.3999 | 611.9417 | 462.46
2414.3167 | 686.456 | 419.9103 | 608.9595 | 670.5016 | 562.4041 | 537.2455 | 612.0993 | 462.4736
2415.3167 | 689.6501 | 419.9013 | 612.8762 | 675.6648 | 563.481 | 537.8172 | 612.3886 | 462.7945
2416.3167 | 689.8862 | 419.9464 | 616.0272 | 678.9411 | 564.8227 | 537.9862 | 612.4888 | 463.1595
2417.3167 | 687.8928 | 420.0143 | 616.6785 | 683.3992 | 565.2922 | 538.3041 | 612.7754 | 463.7447
2418.3167 | 688.2934 | 420.2715 | 619.0766 | 685.3701 | 567.0722 | 538.49 | 612.9371 | 464.2742
2419.3167 | 690.8145 | 420.5738 | 619.6351 | 688.7319 | 568.9439 | 538.898 | 613.1529 | 464.6669
2420.3167 | 689.8744 | 420.657 | 625.8537 | 696.4679 | 569.5553 | 539.2676 | 613.4275 | 464.9923
2421.3167 | 691.4689 | 420.7967 | 627.0838 | 699.871 | 567.7938 | 539.8144 | 613.838 | 465.4121
2422.3167 | 693.057 | 420.8458 | 629.1536 | 702.7619 | 565.1104 | 540.1958 | 613.9877 | 465.6574
2423.3167 | 695.8017 | 421.0052 | 626.2286 | 703.1466 | 564.639 | 540.3844 | 614.2512 | 465.6378
2424.3167 | 696.5659 | 421.194 | 627.7233 | 705.817 | 564.2258 | 540.4612 | 614.5322 | 465.7525
2425.3167 | 697.3395 | 421.2539 | 633.5757 | 709.6759 | 562.57 | 540.5639 | 614.9075 | 465.9449
2426.3167 | 700.2049 | 421.3936 | 635.0649 | 711.3596 | 560.3555 | 541.0268 | 615.1883 | 466.1408
2427.3167 | 699.5994 | 421.5797 | 633.064 | 708.5001 | 558.5563 | 541.5865 | 615.5384 | 466.2981
2428.3167 | 698.7402 | 421.7361 | 632.2503 | 708.7314 | 561.2575 | 542.1041 | 615.8793 | 466.6168
2429.3167 | 703.0167 | 421.8235 | 634.7664 | 712.8086 | 560.9335 | 542.4612 | 616.2082 | 466.8832
2430.3167 | 699.5116 | 421.9726 | 634.8783 | 712.8358 | 559.6614 | 543.0731 | 616.5508 | 467.096
2431.3167 | 704.5376 | 422.1265 | 632.9375 | 706.4007 | 560.1223 | 543.5637 | 616.9834 | 467.3018
2432.3167 | 703.3572 | 422.255 | 635.9034 | 709.3424 | 560.9257 | 543.8174 | 617.3619 | 467.5024
2433.3167 | 700.2198 | 422.3924 | 638.0487 | 707.5317 | 560.9834 | 544.7668 | 617.8014 | 467.8839
2434.3167 | 703.9868 | 422.3132 | 638.0299 | 708.0109 | 557.2317 | 550.5424 | 619.7101 | 470.1207
2435.3167 | 707.2354 | 422.725 | 638.4635 | 703.9037 | 556.5304 | 545.9157 | 618.3285 | 468.1136
2436.3167 | 703.3877 | 422.7649 | 638.0525 | 699.5854 | 554.7532 | 546.2758 | 618.5581 | 468.3375
2437.3167 | 701.3394 | 422.9914 | 636.3721 | 699.1839 | 554.012 | 546.7218 | 618.9044 | 468.5654
2438.3167 | 697.8358 | 423.1753 | 635.7101 | 701.2567 | 553.469 | 547.4682 | 619.2639 | 468.88
2439.3167 | 696.7785 | 423.36 | 637.3636 | 704.0534 | 552.5549 | 547.8386 | 619.6175 | 468.9663
2440.3167 | 695.0329 | 423.5048 | 638.8633 | 701.3743 | 554.6963 | 548.4226 | 619.8347 | 469.1181
2441.3167 | 696.9973 | 423.6043 | 638.4144 | 702.8686 | 553.4283 | 548.7603 | 620.1267 | 469.2892
2442.3167 | 697.6403 | 423.7847 | 637.4957 | 701.2068 | 553.0687 | 549.3938 | 620.4705 | 469.4032
2443.3167 | 696.2762 | 423.9309 | 634.2709 | 699.7977 | 554.2002 | 549.7658 | 620.647 | 469.5904
2444.3167 | 696.9807 | 424.1459 | 636.3172 | 699.5802 | 556.2315 | 550.4306 | 620.9524 | 469.7031
2445.3167 | 694.0593 | 424.2841 | 634.2249 | 703.4049 | 556.1093 | 550.4623 | 621.1953 | 469.7886
2446.3167 | 693.7987 | 424.457 | 635.1568 | 702.1083 | 558.9202 | 550.8375 | 621.4825 | 469.9091
2447.3167 | 696.3598 | 424.6544 | 636.2588 | 702.6844 | 562.1331 | 551.2848 | 621.7122 | 470.0232
2448.3167 | 695.6635 | 424.8139 | 638.9241 | 705.6862 | 563.8327 | 551.5353 | 621.9881 | 470.1095
2449.3167 | 693.3886 | 424.9445 | 639.168 | 715.5193 | 561.7382 | 551.8671 | 622.2054 | 470.156
2450.3167 | 693.89 | 425.2089 | 640.4501 | 713.0091 | 560.0216 | 552.2837 | 622.4624 | 470.2787
2451.3167 | 701.3618 | 425.3634 | 639.4579 | 706.7765 | 561.8742 | 552.8678 | 622.7178 | 470.3929
2452.3167 | 700.2729 | 425.647 | 640.5693 | 708.7081 | 561.028 | 553.1268 | 622.9178 | 470.4184
2453.3167 | 701.9334 | 425.7874 | 643.4499 | 712.1023 | 560.9246 | 553.5931 | 623.1126 | 470.4615
2454.3167 | 700.2345 | 426.0295 | 641.4533 | 708.979 | 563.0838 | 554.0582 | 623.4272 | 470.575
2455.3167 | 700.9602 | 426.1974 | 639.8433 | 709.7752 | 566.2242 | 554.3811 | 623.7252 | 470.7209
2456.3167 | 699.7666 | 426.4103 | 639.8764 | 707.2674 | 566.8479 | 554.8336 | 623.9731 | 470.8911
2457.3167 | 697.5355 | 426.6175 | 637.3638 | 706.098 | 566.5143 | 555.3004 | 624.0872 | 470.9067
2458.3167 | 697.2444 | 426.8299 | 635.6314 | 708.5806 | 565.1399 | 555.6327 | 624.3161 | 471.041
2459.3167 | 694.3424 | 427.1344 | 636.7963 | 714.2314 | 562.5944 | 555.9874 | 624.5125 | 471.2682
2460.3167 | 694.3581 | 427.3939 | 639.9271 | 716.7329 | 561.051 | 556.0549 | 624.67 | 471.3755
2461.3167 | 698.2466 | 427.5398 | 639.5449 | 715.4674 | 561.7814 | 556.6276 | 624.8762 | 471.535
2462.3167 | 695.1541 | 427.8679 | 638.3175 | 712.0852 | 561.3603 | 557.0937 | 625.1431 | 471.6093
2463.3167 | 696.2689 | 428.0897 | 635.2992 | 707.9547 | 562.2428 | 557.6817 | 625.3534 | 471.6346
2464.3167 | 694.9958 | 428.2543 | 632.9696 | 704.7291 | 564.4518 | 558.0704 | 625.5482 | 471.7155
2465.3167 | 695.9039 | 428.4393 | 632.7671 | 702.8672 | 565.2265 | 558.4196 | 625.7857 | 471.7465
2466.3167 | 694.0932 | 428.6623 | 632.3249 | 702.6172 | 566.4606 | 558.5563 | 625.9678 | 471.6745
2467.3167 | 691.3116 | 428.9043 | 628.1755 | 702.4945 | 566.9664 | 558.9156 | 626.1099 | 471.7134
2468.3167 | 689.3264 | 429.122 | 625.8313 | 701.622 | 565.7469 | 559.2115 | 626.265 | 471.7649
2469.3167 | 688.3013 | 429.4 | 628.2931 | 704.3683 | 566.9491 | 559.2799 | 626.4099 | 471.8241
2470.3167 | 686.8448 | 429.5134 | 632.3225 | 702.3907 | 567.3038 | 559.8297 | 626.601 | 472.0094
2471.3167 | 690.5353 | 429.6393 | 633.9665 | 701.0674 | 565.4822 | 560.2418 | 626.7349 | 472.2125
2472.3167 | 694.7092 | 429.8219 | 633.5129 | 703.2717 | 564.1222 | 560.3344 | 626.8145 | 472.5454
2473.3167 | 695.8906 | 430.0588 | 631.1581 | 707.5454 | 561.087 | 560.7488 | 627.0861 | 472.7257
2474.3167 | 694.1021 | 430.5291 | 632.7066 | 709.6952 | 558.4193 | 561.3113 | 627.2839 | 472.9706
2475.3167 | 698.1932 | 430.7308 | 632.4051 | 707.0082 | 558.2483 | 561.6715 | 627.4202 | 472.9938
2476.3167 | 698.3404 | 430.9485 | 630.3218 | 705.9658 | 561.8405 | 561.8489 | 627.5725 | 473.2479
2477.3167 | 695.9145 | 431.3605 | 630.8427 | 709.769 | 564.3916 | 561.905 | 627.7069 | 473.3503
2478.3167 | 695.2917 | 431.6802 | 632.0638 | 707.2646 | 567.3542 | 562.236 | 627.8336 | 473.4163
2479.3167 | 696.0187 | 431.8691 | 633.4622 | 706.0537 | 565.7021 | 562.5692 | 627.911 | 473.5874
2480.3167 | 697.3369 | 432.1987 | 633.1873 | 703.7398 | 566.2682 | 562.9894 | 628.0744 | 473.7743
2481.3167 | 694.5272 | 432.2829 | 631.1385 | 702.1635 | 567.8207 | 562.9498 | 628.1874 | 473.9405
2482.3167 | 693.099 | 432.284 | 628.4515 | 702.7805 | 570.4389 | 563.3135 | 628.359 | 474.0802
2483.3167 | 690.5191 | 432.6035 | 626.7316 | 705.2257 | 570.1478 | 563.604 | 628.4775 | 474.2586
2484.3167 | 690.9248 | 432.6655 | 628.0469 | 704.9965 | 569.8982 | 563.984 | 628.4881 | 474.391
2485.3167 | 689.0778 | 432.8942 | 627.4688 | 707.0823 | 571.0435 | 564.4239 | 628.5877 | 474.5623
2486.3167 | 687.4599 | 433.0649 | 630.1168 | 704.1111 | 571.9318 | 564.4702 | 628.7345 | 474.6882
2487.3167 | 692.9502 | 433.2823 | 632.3312 | 703.6729 | 573.787 | 564.8847 | 628.8076 | 474.8065
2488.3167 | 693.7791 | 433.7196 | 632.6131 | 708.8637 | 574.3678 | 564.9376 | 628.9149 | 474.9472
2489.3167 | 695.821 | 433.6771 | 631.9724 | 709.3198 | 571.884 | 565.3219 | 629.0122 | 475.1046
2490.3167 | 696.1154 | 433.8215 | 632.9534 | 709.2571 | 568.8128 | 565.7653 | 629.0944 | 475.2533
2491.3167 | 696.4193 | 434.0078 | 634.7878 | 714.2441 | 565.556 | 565.8871 | 629.2318 | 475.3791
2492.3167 | 699.1071 | 434.2284 | 634.2788 | 716.606 | 563.6149 | 566.4226 | 629.3279 | 475.5358
2493.3167 | 701.2421 | 434.2784 | 635.4556 | 718.5418 | 563.0411 | 566.602 | 629.4104 | 475.6295
2494.3167 | 701.2675 | 434.4692 | 636.8582 | 722.8533 | 561.0311 | 566.9211 | 629.4955 | 475.7727
2495.3167 | 700.3373 | 434.6427 | 638.6471 | 724.1635 | 558.5485 | 567.3561 | 629.6643 | 475.8656
2496.3167 | 700.4217 | 434.8271 | 640.5179 | 723.5088 | 558.3426 | 567.9544 | 629.8624 | 475.9313
2497.3167 | 705.0166 | 434.9651 | 644.9224 | 722.1877 | 556.5805 | 568.5296 | 630.093 | 475.9912
2498.3167 | 705.0237 | 435.2199 | 642.8284 | 721.529 | 554.2046 | 568.9341 | 630.257 | 476.0701
2499.3167 | 702.7537 | 435.426 | 643.6465 | 718.6339 | 555.6807 | 569.5606 | 630.461 | 476.1527
2500.3167 | 701.9071 | 435.5999 | 641.4856 | 717.1008 | 558.4419 | 569.2649 | 630.7155 | 476.1936
2501.3167 | 700.3518 | 435.7317 | 641.8288 | 718.4369 | 561.1234 | 569.6918 | 630.9811 | 476.2145
2502.3167 | 699.531 | 435.9023 | 645.0254 | 716.0092 | 563.3816 | 570.2138 | 631.1999 | 476.3038
2503.3167 | 700.2894 | 436.1058 | 644.1267 | 717.5545 | 563.7772 | 570.7607 | 631.4986 | 476.4107
2504.3167 | 699.1089 | 436.2657 | 643.6823 | 721.4287 | 563.7614 | 571.1874 | 631.8236 | 476.4625
2505.3167 | 704.8869 | 436.3744 | 646.029 | 721.634 | 566.9978 | 571.719 | 632.0061 | 476.5551
2506.3167 | 706.4323 | 436.693 | 647.7045 | 718.3914 | 569.1361 | 572.1291 | 632.2807 | 476.5825
2507.3167 | 704.8932 | 436.7776 | 647.8228 | 713.8921 | 570.8554 | 572.6587 | 632.5807 | 476.6816
2508.3167 | 705.3488 | 437.0189 | 644.7228 | 713.6525 | 569.1962 | 573.1353 | 632.7652 | 476.7441
2509.3167 | 706.3879 | 437.1799 | 646.1732 | 708.9557 | 571.1974 | 573.7532 | 633.079 | 476.8006
2510.3167 | 708.5499 | 437.3532 | 645.0274 | 706.8084 | 570.2937 | 574.0452 | 633.3123 | 476.8366
2511.3167 | 705.3892 | 437.3607 | 645.8182 | 705.9596 | 571.0413 | 574.6435 | 633.6075 | 476.8998
2512.3167 | 706.2187 | 437.5302 | 644.7958 | 704.7871 | 572.0363 | 575.0212 | 633.7789 | 476.9335
2513.3167 | 703.5996 | 437.7492 | 642.9893 | 700.255 | 572.5551 | 575.5106 | 634.0612 | 477.0102
2514.3167 | 699.4816 | 437.7878 | 643.9388 | 695.8808 | 571.9698 | 575.7483 | 634.3066 | 477.0605
2515.3167 | 695.4072 | 437.9545 | 642.17 | 690.6827 | 571.1477 | 576.287 | 634.5388 | 477.1139
2516.3167 | 694.6679 | 438.1549 | 645.2789 | 688.8839 | 568.4936 | 576.7968 | 634.7474 | 477.156
2517.3167 | 693.9876 | 438.1779 | 646.5242 | 694.4216 | 568.104 | 577.2169 | 634.9478 | 477.1702
2518.3167 | 695.8267 | 438.324 | 645.7707 | 696.5101 | 568.5961 | 577.6634 | 635.0848 | 477.2367
2519.3167 | 698.8764 | 438.5077 | 645.2622 | 692.6225 | 566.4819 | 578.1885 | 635.2707 | 477.3105
2520.3167 | 702.0979 | 438.9953 | 645.9491 | 691.394 | 562.6719 | 578.6027 | 635.4584 | 477.3075
2521.3167 | 701.784 | 439.1256 | 646.8386 | 693.9633 | 559.9081 | 579.3057 | 635.6816 | 477.3556
2522.3167 | 701.2087 | 439.1454 | 646.4311 | 694.448 | 558.9033 | 579.5678 | 635.8928 | 477.4055
2523.3167 | 707.1035 | 439.2894 | 646.9987 | 697.4048 | 558.4022 | 580.006 | 636.0794 | 477.4219
2524.3167 | 706.4599 | 439.4494 | 646.6735 | 694.8693 | 560.5696 | 580.5132 | 636.3077 | 477.4708
2525.3167 | 703.3874 | 439.7669 | 645.6999 | 691.912 | 560.3183 | 580.8809 | 636.5539 | 477.5001
2526.3167 | 701.5964 | 439.9081 | 645.0353 | 691.6571 | 559.5583 | 581.2227 | 636.7305 | 477.49
2527.3167 | 700.5772 | 439.9819 | 646.0549 | 691.4755 | 559.1697 | 581.8383 | 636.9521 | 477.5233
2528.3167 | 695.8865 | 440.0874 | 647.8303 | 689.5721 | 560.1332 | 582.2373 | 637.0748 | 477.5484
2529.3167 | 692.5947 | 440.2144 | 652.252 | 688.6421 | 558.6629 | 583.2961 | 637.2745 | 477.756
2530.3167 | 691.9991 | 440.3937 | 656.0116 | 693.6799 | 556.8654 | 583.1885 | 637.4289 | 477.6523
2531.3167 | 698.7578 | 440.5489 | 653.8586 | 697.6279 | 557.2448 | 583.7935 | 637.5801 | 477.7
2532.3167 | 700.9824 | 440.6677 | 652.4181 | 696.986 | 559.6455 | 583.8686 | 637.7207 | 477.7363
2533.3167 | 702.2121 | 440.7999 | 654.7599 | 699.7521 | 561.2171 | 584.5117 | 637.9877 | 477.8053
2534.3167 | 702.7513 | 441.0504 | 654.7688 | 704.7053 | 559.7531 | 584.7268 | 638.147 | 477.8739
2535.3167 | 705.8764 | 441.178 | 653.8602 | 704.4561 | 563.6887 | 585.2395 | 638.2405 | 477.8781
2536.3167 | 704.2184 | 441.4022 | 653.3272 | 700.857 | 564.3682 | 585.1065 | 638.427 | 477.9327
2537.3167 | 703.3545 | 441.6256 | 647.7397 | 700.6895 | 565.6317 | 585.05 | 638.5131 | 477.8934
2538.3167 | 701.7843 | 441.6435 | 647.11 | 704.0602 | 567.8332 | 585.1292 | 638.7563 | 477.9158
2539.3167 | 700.0062 | 441.913 | 646.9614 | 705.1786 | 570.055 | 585.4687 | 638.8698 | 477.938
2540.3167 | 699.6887 | 441.9761 | 645.927 | 703.7738 | 573.6807 | 585.896 | 638.9968 | 477.9929
2541.3167 | 703.8038 | 442.0796 | 643.5008 | 701.5155 | 577.3115 | 585.9532 | 639.2232 | 478.0131
2542.3167 | 703.8451 | 442.1365 | 642.971 | 699.2389 | 579.4768 | 586.3789 | 639.3969 | 478.0603
2543.3167 | 701.8579 | 442.2301 | 639.4417 | 696.8331 | 578.7236 | 586.5503 | 639.67 | 478.123
2544.3167 | 697.0922 | 442.2508 | 638.1633 | 695.461 | 576.0555 | 586.4294 | 639.7841 | 478.0916
2545.3167 | 697.5786 | 442.7385 | 640.9085 | 694.4057 | 575.608 | 586.6704 | 639.8702 | 478.1003
2546.3167 | 698.9678 | 442.9548 | 641.9593 | 695.2005 | 579.341 | 586.9849 | 639.9834 | 478.0915
2547.3167 | 701.8946 | 442.8916 | 643.4489 | 699.8061 | 581.0836 | 587.0123 | 640.1781 | 478.13
2548.3167 | 703.5763 | 442.8089 | 644.8917 | 703.2649 | 579.6846 | 587.4369 | 640.4275 | 478.1778
2549.3167 | 700.571 | 442.8805 | 643.4039 | 700.9416 | 578.9909 | 587.567 | 640.6613 | 478.2393
2550.3167 | 700.5326 | 443.0087 | 638.1585 | 698.5382 | 578.8987 | 587.7246 | 640.7656 | 478.247
2551.3167 | 700.3173 | 443.016 | 635.1117 | 694.3283 | 578.0682 | 588.2452 | 640.9964 | 478.3874
2552.3167 | 697.107 | 443.0325 | 633.5798 | 694.4552 | 577.5419 | 587.9755 | 641.0125 | 478.3255
2553.3167 | 696.497 | 443.1817 | 631.9237 | 696.0066 | 576.5109 | 588.0162 | 641.1748 | 478.3763
2554.3167 | 695.5271 | 443.1438 | 631.8858 | 695.6885 | 575.4964 | 588.4285 | 641.3186 | 478.4718
2555.3167 | 695.1576 | 443.1048 | 634.0232 | 698.106 | 572.9231 | 589.6226 | 641.832 | 478.9313
2556.3167 | 695.2862 | 443.1713 | 633.7186 | 696.4121 | 572.6569 | 588.8648 | 641.5277 | 478.5361
2557.3167 | 702.1173 | 443.1601 | 635.9794 | 698.1786 | 572.0215 | 588.8492 | 641.6926 | 478.5763
2558.3167 | 710.2175 | 443.2234 | 637.5428 | 694.1416 | 572.1005 | 589.3209 | 641.7508 | 478.6495
2559.3167 | 712.6867 | 443.3313 | 640.7244 | 697.1497 | 570.4132 | 589.578 | 642.0662 | 478.6329
2560.3167 | 708.1247 | 443.5049 | 640.6441 | 697.5296 | 570.5548 | 589.9263 | 642.2763 | 478.6811
2561.3167 | 710.6148 | 443.4557 | 640.034 | 699.2561 | 569.8145 | 590.3248 | 642.4184 | 478.7031
2562.3167 | 709.2575 | 443.5384 | 640.0608 | 697.4984 | 568.9448 | 590.4286 | 642.5161 | 478.7394
2563.3167 | 705.4634 | 443.6536 | 641.1565 | 698.4468 | 568.3437 | 590.797 | 642.7014 | 478.7837
2564.3167 | 704.481 | 443.7848 | 646.7053 | 699.9048 | 566.999 | 591.0588 | 642.8997 | 478.8587
2565.3167 | 711.0347 | 443.8052 | 649.1188 | 705.8862 | 566.0105 | 591.6643 | 643.064 | 478.9331
2566.3167 | 708.9922 | 443.8235 | 650.0483 | 699.5224 | 565.2556 | 591.9024 | 643.2169 | 478.9956
2567.3167 | 708.0792 | 443.8552 | 652.5855 | 700.639 | 564.5813 | 592.1624 | 643.4055 | 479.0587
2568.3167 | 707.7523 | 443.9359 | 656.0917 | 702.1985 | 563.2314 | 592.4898 | 643.5475 | 479.0936
2569.3167 | 708.984 | 443.9942 | 659.3507 | 701.7116 | 560.6202 | 593.0464 | 643.7209 | 479.172
2570.3167 | 716.3495 | 444.0977 | 662.7118 | 706.5815 | 559.7449 | 593.3951 | 643.8618 | 479.2278
2571.3167 | 718.1682 | 444.1114 | 663.7257 | 703.9989 | 557.8259 | 594.0454 | 643.9956 | 479.3161
2572.3167 | 717.9835 | 444.3559 | 663.8549 | 704.5888 | 561.3832 | 594.239 | 644.1092 | 479.3732
2573.3167 | 718.931 | 444.4133 | 664.9145 | 701.2633 | 562.6344 | 594.6469 | 644.247 | 479.4252
2574.3167 | 720.3141 | 444.4998 | 667.3321 | 705.7119 | 564.1195 | 594.961 | 644.4232 | 479.4827
2575.3167 | 722.5534 | 444.6145 | 666.7062 | 703.3552 | 564.5024 | 595.3949 | 644.5533 | 479.5483
2576.3167 | 721.1984 | 444.7733 | 660.133 | 700.0375 | 566.3381 | 595.6045 | 644.632 | 479.6352
2577.3167 | 721.2304 | 444.8577 | 660.7981 | 701.5456 | 568.9189 | 595.8004 | 644.7475 | 479.6677
2578.3167 | 717.6302 | 445.0569 | 664.2411 | 705.2112 | 570.2937 | 595.7509 | 644.939 | 479.7232
2579.3167 | 715.8535 | 445.2445 | 666.8304 | 705.9359 | 572.8183 | 595.9484 | 645.0902 | 479.8173
2580.3167 | 714.6475 | 445.5383 | 664.747 | 707.901 | 575.3858 | 596.2247 | 645.1511 | 479.9033
2581.3167 | 714.6193 | 445.5523 | 662.918 | 709.7911 | 574.9827 | 596.577 | 645.3142 | 479.9828
2582.3167 | 716.3682 | 445.8606 | 665.0586 | 708.829 | 572.9001 | 596.7947 | 645.4717 | 480.028
2583.3167 | 717.4979 | 445.9488 | 666.8408 | 711.664 | 570.4101 | 597.2395 | 645.6247 | 480.0903
2584.3167 | 720.8779 | 446.0393 | 669.0355 | 710.6392 | 574.7419 | 597.7052 | 645.7338 | 480.1558
2585.3167 | 718.1865 | 446.183 | 667.025 | 706.1317 | 577.2895 | 597.8933 | 645.8667 | 480.2287
2586.3167 | 717.5649 | 446.3008 | 663.2921 | 704.9716 | 576.4979 | 598.272 | 645.9073 | 480.2488
2587.3167 | 711.4739 | 446.3582 | 656.911 | 701.5107 | 574.4909 | 598.4369 | 646.0184 | 480.2783
2588.3167 | 708.0565 | 446.5318 | 655.7817 | 698.2275 | 572.9874 | 598.4689 | 646.0829 | 480.3575
2589.3167 | 706.5162 | 446.7059 | 654.5772 | 698.6027 | 571.676 | 598.5631 | 646.1113 | 480.4178
2590.3167 | 706.5297 | 446.9358 | 656.5422 | 700.3912 | 571.9366 | 598.8303 | 646.1577 | 480.4831
2591.3167 | 708.6938 | 447.1025 | 663.0363 | 700.2115 | 571.4284 | 599.4419 | 646.3378 | 480.5605
2592.3167 | 716.5298 | 447.3672 | 669.0693 | 710.1989 | 568.6576 | 599.8242 | 646.5953 | 480.6356
2593.3167 | 727.8676 | 447.3555 | 675.9486 | 720.3601 | 565.858 | 602.7231 | 647.6371 | 481.7987
2594.3167 | 728.9209 | 447.5685 | 678.0046 | 719.471 | 564.9142 | 600.4639 | 647.0073 | 480.8182
2595.3167 | 730.9741 | 447.7245 | 677.318 | 724.6748 | 564.0622 | 601.084 | 647.1704 | 480.9256
2596.3167 | 727.0043 | 448.0922 | 675.0298 | 724.409 | 563.6388 | 601.5627 | 647.2787 | 481.0077
2597.3167 | 726.3144 | 448.101 | 670.9943 | 717.9878 | 564.2718 | 601.7424 | 647.4318 | 481.074
2598.3167 | 722.2988 | 448.2239 | 669.9428 | 714.6669 | 568.4229 | 602.0117 | 647.5175 | 481.1623
2599.3167 | 717.7685 | 448.3675 | 668.7816 | 710.1291 | 569.3919 | 602.245 | 647.5507 | 481.2463
2600.3167 | 715.3126 | 448.5958 | 667.8009 | 704.7179 | 570.4794 | 602.615 | 647.6731 | 481.3245
2601.3167 | 711.8288 | 448.7565 | 666.8167 | 705.8205 | 569.5572 | 603.0622 | 647.7452 | 481.4177
2602.3167 | 712.2618 | 448.9392 | 665.1334 | 704.6811 | 571.1216 | 603.271 | 647.7742 | 481.4999
2603.3167 | 711.5754 | 449.2263 | 665.5026 | 702.6274 | 572.1213 | 603.6119 | 647.747 | 481.5901
2604.3167 | 714.1405 | 449.4179 | 667.2151 | 706.8538 | 575.2724 | 603.9684 | 647.8906 | 481.6904
2605.3167 | 713.7513 | 449.5655 | 668.7422 | 708.6904 | 573.1625 | 605.1611 | 648.3156 | 482.0873
2606.3167 | 720.4511 | 449.7154 | 671.9873 | 711.8511 | 572.0728 | 604.9354 | 648.1705 | 481.8914
2607.3167 | 721.8397 | 449.8185 | 669.9675 | 709.0852 | 573.3918 | 605.4255 | 648.3364 | 482.0872
2608.3167 | 718.5293 | 449.9613 | 665.3118 | 707.4912 | 574.2994 | 605.7089 | 648.321 | 482.1379
2609.3167 | 716.9489 | 450.1632 | 662.4066 | 704.9996 | 577.0646 | 605.7785 | 648.384 | 482.2227
2610.3167 | 714.5927 | 450.3009 | 661.0782 | 703.1966 | 578.431 | 605.965 | 648.4301 | 482.3273
2611.3167 | 714.4505 | 450.2404 | 658.4936 | 701.7807 | 577.785 | 606.2665 | 648.437 | 482.4138
2612.3167 | 713.8873 | 450.4776 | 655.7406 | 702.1773 | 577.3894 | 606.3141 | 648.5526 | 482.5726
2613.3167 | 716.6478 | 450.7952 | 656.1912 | 700.7304 | 579.1458 | 606.4272 | 648.5908 | 482.6289
2614.3167 | 713.1446 | 451.1369 | 655.1965 | 707.8597 | 577.6805 | 606.6648 | 648.6733 | 482.743
2615.3167 | 708.903 | 451.0304 | 656.9718 | 706.1284 | 576.1903 | 606.8461 | 648.7722 | 482.8465
2616.3167 | 706.6772 | 451.014 | 658.5361 | 704.3823 | 574.1104 | 607.1636 | 648.7755 | 482.9304
2617.3167 | 704.3155 | 451.1338 | 659.4933 | 701.1381 | 572.7159 | 607.5491 | 648.8759 | 483.0286
2618.3167 | 704.549 | 451.2818 | 660.6994 | 699.9747 | 571.9556 | 607.6156 | 648.9809 | 483.1227
2619.3167 | 714.4074 | 451.5471 | 660.6893 | 701.0261 | 572.7179 | 607.7782 | 649.0928 | 483.2581
2620.3167 | 711.1483 | 451.6651 | 663.0806 | 702.784 | 570.8207 | 608.0658 | 649.2369 | 483.3717
2621.3167 | 714.47 | 452.0022 | 666.0512 | 702.3063 | 570.1912 | 608.4011 | 649.3462 | 483.4947
2622.3167 | 717.6357 | 451.9622 | 666.5401 | 704.5753 | 570.2422 | 608.7877 | 649.4673 | 483.6206
2623.3167 | 725.8801 | 452.3166 | 668.8836 | 713.1787 | 567.9757 | 609.1 | 649.5987 | 483.7221
2624.3167 | 727.7787 | 452.3897 | 670.763 | 716.2204 | 568.2984 | 609.4633 | 649.7512 | 483.84
2625.3167 | 726.9007 | 452.2953 | 668.0173 | 714.3073 | 566.473 | 609.732 | 649.8623 | 483.9508
2626.3167 | 727.9369 | 452.5415 | 667.9409 | 713.9647 | 564.5496 | 609.9539 | 650.0103 | 484.0752
2627.3167 | 731.2839 | 452.7216 | 670.7958 | 715.8411 | 563.1216 | 610.3194 | 650.2093 | 484.213
2628.3167 | 733.125 | 452.629 | 674.2759 | 714.5914 | 562.8732 | 610.6561 | 650.3589 | 484.3227
2629.3167 | 736.649 | 452.7255 | 676.3733 | 713.0255 | 562.8966 | 610.9786 | 650.4774 | 484.4195
2630.3167 | 736.9875 | 452.6782 | 671.5895 | 711.8941 | 562.0818 | 611.32 | 650.6015 | 484.5192
2631.3167 | 735.5567 | 452.8453 | 670.5736 | 712.4744 | 561.8838 | 611.4717 | 650.7446 | 484.6154
2632.3167 | 736.0817 | 453.1557 | 668.7714 | 717.9514 | 561.3422 | 611.9749 | 650.8446 | 484.752
2633.3167 | 735.2722 | 452.9833 | 665.9375 | 717.0098 | 562.1282 | 612.3085 | 650.8874 | 484.8796
2634.3167 | 734.0406 | 453.3144 | 667.5419 | 714.522 | 571.6596 | 612.4968 | 651.016 | 485.0181
2635.3167 | 731.7744 | 453.2131 | 665.7464 | 714.0984 | 573.1231 | 612.5473 | 651.0675 | 485.1031
2636.3167 | 732.2139 | 453.4307 | 664.5617 | 714.2323 | 572.5013 | 612.9378 | 651.1671 | 485.2364
2637.3167 | 734.0008 | 453.282 | 666.5856 | 714.2041 | 572.8857 | 613.3474 | 651.3701 | 485.421
2638.3167 | 732.9677 | 453.4882 | 664.7349 | 713.8094 | 572.5903 | 613.3279 | 651.3959 | 485.4752
2639.3167 | 730.211 | 453.8907 | 663.886 | 711.9647 | 571.9868 | 613.3215 | 651.4308 | 485.5612
2640.3167 | 727.4937 | 453.6979 | 661.6874 | 714.0798 | 575.3175 | 613.7402 | 651.4964 | 485.697
2641.3167 | 726.4362 | 453.7054 | 659.323 | 711.7986 | 576.3811 | 613.9959 | 651.5554 | 485.8419
2642.3167 | 725.2181 | 453.7491 | 659.0479 | 713.5972 | 574.8346 | 614.2566 | 651.6254 | 485.9685
2643.3167 | 725.3059 | 453.9408 | 658.8265 | 714.1015 | 573.8036 | 614.6137 | 651.7995 | 486.1637
2644.3167 | 733.1196 | 454.0611 | 659.2064 | 710.509 | 576.9465 | 614.5851 | 651.8855 | 486.2179
2645.3167 | 731.039 | 454.2533 | 658.3692 | 708.1823 | 579.7502 | 614.6852 | 651.8823 | 486.3399
2646.3167 | 727.5365 | 454.5596 | 658.9223 | 708.2029 | 580.5898 | 615.4225 | 652.1272 | 486.7132
2647.3167 | 726.8589 | 454.7298 | 659.7826 | 712.3386 | 582.2657 | 615.4791 | 652.214 | 486.6646
2648.3167 | 729.3546 | 454.6956 | 660.2431 | 707.6154 | 578.7498 | 615.9527 | 652.2675 | 486.7816
2649.3167 | 728.8478 | 454.8293 | 658.7339 | 708.3975 | 578.1603 | 616.2117 | 652.3147 | 486.9019
2650.3167 | 728.2254 | 455.0383 | 660.9873 | 709.6653 | 579.1616 | 616.2904 | 652.4128 | 487.0262
2651.3167 | 728.0436 | 455.0359 | 665.9277 | 715.3832 | 578.4239 | 616.8148 | 652.6252 | 487.1355
2652.3167 | 729.7649 | 455.009 | 663.4362 | 716.4271 | 576.375 | 617.4225 | 652.8727 | 487.3332
2653.3167 | 734.875 | 455.0071 | 668.0375 | 718.6752 | 575.6942 | 617.5048 | 652.9944 | 487.4706
2654.3167 | 735.1807 | 455.3207 | 667.8314 | 721.0153 | 593.6638 | 617.9325 | 653.1831 | 487.6286
2655.3167 | 738.2274 | 455.1579 | 670.8492 | 721.9807 | 606.1951 | 618.5406 | 653.4041 | 487.887
2656.3167 | 736.0211 | 455.4611 | 667.2524 | 720.047 | 610.4697 | 618.8963 | 653.4695 | 487.9454
2657.3167 | 732.6148 | 455.336 | 664.9638 | 718.976 | 608.0146 | 619.2332 | 653.5879 | 488.0836
2658.3167 | 733.6294 | 455.5059 | 662.3873 | 718.7756 | 603.6687 | 619.3965 | 653.6023 | 488.2394
2659.3167 | 728.833 | 455.6335 | 660.3319 | 712.9059 | 600.3622 | 619.7111 | 653.6787 | 488.3899
2660.3167 | 729.0071 | 455.9545 | 659.6495 | 713.7636 | 596.101 | 619.8391 | 653.7644 | 488.5405
2661.3167 | 728.5677 | 455.9381 | 662.0892 | 713.1682 | 594.3105 | 620.3631 | 653.917 | 488.6751
2662.3167 | 728.8657 | 456.059 | 662.4677 | 716.9191 | 592.0222 | 620.4673 | 654.0759 | 488.8432
2663.3167 | 727.6236 | 456.2572 | 666.3151 | 721.3648 | 589.258 | 621.0366 | 654.2761 | 488.9882
2664.3167 | 733.7146 | 456.4021 | 666.2306 | 719.7305 | 585.3359 | 621.6634 | 654.4224 | 489.182
2665.3167 | 734.0733 | 456.4451 | 670.6335 | 727.0035 | 582.5542 | 622.0156 | 654.545 | 489.346
2666.3167 | 733.401 | 456.8503 | 668.3325 | 722.9074 | 580.0526 | 623.8987 | 655.3102 | 490.061
2667.3167 | 732.4589 | 456.7925 | 667.6049 | 718.6721 | 581.2675 | 622.4948 | 654.7785 | 489.6383
2668.3167 | 734.2323 | 456.7154 | 668.7456 | 714.3565 | 579.1249 | 623.071 | 654.9285 | 489.8391
2669.3167 | 733.3837 | 457.1269 | 667.5076 | 714.5441 | 576.8369 | 623.4095 | 655.0057 | 490.0067
2670.3167 | 729.8194 | 457.0894 | 667.6386 | 713.9995 | 573.8073 | 623.7038 | 655.1022 | 490.1587
2671.3167 | 724.4954 | 457.1321 | 665.7711 | 713.9004 | 571.7498 | 623.954 | 655.1649 | 490.3289
2672.3167 | 718.7172 | 457.2831 | 663.1229 | 710.7986 | 570.3267 | 624.1324 | 655.1627 | 490.4826
2673.3167 | 714.8052 | 457.3461 | 663.4841 | 714.175 | 568.5698 | 624.4029 | 655.3238 | 490.639
2674.3167 | 713.8103 | 457.4177 | 662.1467 | 715.7319 | 568.0217 | 624.4572 | 655.4198 | 490.7914
2675.3167 | 711.7965 | 457.5253 | 661.6567 | 710.3102 | 567.6491 | 624.8396 | 655.461 | 490.9593
2676.3167 | 713.8082 | 457.6832 | 659.1021 | 709.4832 | 568.0359 | 625.3339 | 655.5859 | 491.239
2677.3167 | 709.4228 | 458.1773 | 657.668 | 708.0569 | 568.4079 | 625.4245 | 655.5726 | 491.3175
2678.3167 | 708.0826 | 458.534 | 656.8863 | 710.2578 | 567.542 | 625.6015 | 655.6267 | 491.4817
2679.3167 | 709.1476 | 458.3775 | 657.5818 | 707.6283 | 569.9224 | 625.7738 | 655.6948 | 491.6475
2680.3167 | 712.1449 | 458.321 | 657.104 | 707.8917 | 571.8857 | 626.0652 | 655.7023 | 491.8328
2681.3167 | 716.1675 | 458.4371 | 653.6863 | 705.6256 | 573.6449 | 626.2318 | 655.8034 | 492.0168
2682.3167 | 719.6675 | 458.5043 | 652.5044 | 703.4907 | 574.8622 | 626.1828 | 655.913 | 492.1994
2683.3167 | 719.6211 | 458.8584 | 651.1383 | 699.5606 | 577.7191 | 626.1934 | 655.9593 | 492.378
2684.3167 | 717.1727 | 459.0424 | 648.6334 | 700.355 | 577.5072 | 626.2452 | 656.0899 | 492.5697
2685.3167 | 716.5466 | 459.0853 | 649.2466 | 698.3656 | 575.9115 | 626.2986 | 656.132 | 492.7387
2686.3167 | 722.5438 | 459.4137 | 649.1289 | 702.0685 | 576.03 | 626.3779 | 656.2567 | 492.9212
2687.3167 | 726.7662 | 459.4354 | 647.5438 | 703.1343 | 573.9492 | 626.454 | 656.3727 | 493.0877
2688.3167 | 726.5474 | 459.4371 | 647.1549 | 703.2503 | 575.2269 | 626.5999 | 656.4453 | 493.2808
2689.3167 | 724.0168 | 459.5921 | 646.2438 | 699.5701 | 575.1824 | 626.4565 | 656.4983 | 493.4407
2690.3167 | 722.6997 | 459.6897 | 645.9095 | 697.2061 | 575.3941 | 626.5439 | 656.5266 | 493.6081
2691.3167 | 719.6153 | 459.8041 | 644.3373 | 696.4752 | 576.0867 | 626.6677 | 656.5586 | 493.7988
2692.3167 | 722.8043 | 459.9832 | 644.5157 | 693.1244 | 577.384 | 627.0699 | 656.7582 | 494.1983
2693.3167 | 721.6561 | 460.5178 | 644.7102 | 698.87 | 578.3161 | 626.7132 | 656.7217 | 494.1868
2694.3167 | 726.0082 | 460.1535 | 646.2633 | 705.2798 | 577.8027 | 626.7415 | 656.9418 | 494.389
2695.3167 | 729.9391 | 460.417 | 646.5311 | 708.9536 | 576.5276 | 627.041 | 657.1812 | 494.6513
2696.3167 | 728.4253 | 462.5482 | 645.2597 | 711.4927 | 578.3912 | 626.9326 | 657.2335 | 494.7748
2697.3167 | 728.2837 | 465.9532 | 643.799 | 711.3641 | 579.4179 | 626.8556 | 657.2965 | 494.9543
2698.3167 | 728.7708 | 461.5076 | 644.5501 | 711.5465 | 578.2156 | 626.9431 | 657.4656 | 495.1414
2699.3167 | 731.0756 | 460.2915 | 644.1658 | 713.6248 | 580.086 | 626.9879 | 657.6068 | 495.3206
2700.3167 | 730.9075 | 460.7877 | 640.9181 | 708.7788 | 581.359 | 627.026 | 657.74 | 495.5346
2701.3167 | 728.3256 | 460.809 | 638.7841 | 706.6762 | 581.2787 | 626.8092 | 657.8014 | 495.7497
2702.3167 | 723.3547 | 460.7487 | 638.9937 | 699.7874 | 579.8862 | 626.93 | 657.8742 | 495.9399
2703.3167 | 721.6608 | 460.8589 | 639.1729 | 699.1329 | 577.7638 | 626.9846 | 657.927 | 496.1367
2704.3167 | 722.4194 | 461.521 | 640.2498 | 701.7352 | 578.7022 | 626.8557 | 658.046 | 496.291
2705.3167 | 727.2061 | 461.5851 | 644.6289 | 709.1903 | 580.4049 | 626.8973 | 658.1647 | 496.5074
2706.3167 | 732.9324 | 461.5176 | 645.558 | 710.2379 | 580.2153 | 627.2728 | 658.4583 | 496.7878
2707.3167 | 736.7518 | 461.4846 | 646.6101 | 714.7243 | 579.4948 | 627.5955 | 658.6829 | 497.0945
2708.3167 | 734.3033 | 461.7598 | 644.3394 | 715.7515 | 579.8724 | 627.3243 | 658.8063 | 497.1745
2709.3167 | 735.7652 | 462.1489 | 646.3347 | 717.0412 | 580.0965 | 627.4037 | 659.0171 | 497.4061
2710.3167 | 731.5534 | 462.2467 | 644.1267 | 709.9329 | 579.3376 | 627.6405 | 659.1124 | 497.6546
2711.3167 | 730.6693 | 462.2324 | 642.9395 | 706.5982 | 577.8689 | 627.5915 | 659.1654 | 497.8515
2712.3167 | 731.6223 | 462.3384 | 647.0163 | 708.5727 | 579.0897 | 627.6433 | 659.2582 | 498.0544
2713.3167 | 736.536 | 462.4985 | 648.3832 | 710.6963 | 578.325 | 629.032 | 659.7146 | 498.5749
2714.3167 | 740.4233 | 463.0273 | 646.069 | 712.8553 | 578.2558 | 628.9056 | 659.9124 | 498.796
2715.3167 | 739.9767 | 462.8261 | 645.0132 | 715.3862 | 577.6935 | 628.1937 | 659.8945 | 498.7634
2716.3167 | 738.6348 | 462.9339 | 644.7435 | 716.6048 | 576.3498 | 628.3034 | 660.0861 | 498.9744
2717.3167 | 745.5583 | 463.1571 | 646.2748 | 714.7327 | 574.9585 | 628.3563 | 660.3537 | 499.1807
2718.3167 | 744.0384 | 463.1573 | 646.5772 | 718.3018 | 573.5821 | 628.5252 | 660.5971 | 499.4158
2719.3167 | 745.4722 | 463.4287 | 646.3183 | 715.5905 | 572.4648 | 628.8679 | 660.8401 | 499.6524
2720.3167 | 742.9747 | 463.4994 | 646.6382 | 714.2325 | 570.5603 | 629.0286 | 661.0034 | 499.8731
2721.3167 | 743.2693 | 463.4578 | 646.4683 | 712.4201 | 568.0267 | 629.1221 | 661.209 | 499.9554
2722.3167 | 743.1061 | 463.4484 | 646.3593 | 707.2548 | 567.5255 | 629.2662 | 661.3553 | 500.1698
2723.3167 | 740.6209 | 463.9849 | 649.3281 | 707.6646 | 565.9428 | 629.3344 | 661.5436 | 500.3897
2724.3167 | 738.5764 | 463.9747 | 650.6054 | 707.3015 | 567.2961 | 629.6179 | 661.717 | 500.6155
2725.3167 | 735.8633 | 464.0967 | 652.103 | 703.8657 | 565.5234 | 629.8225 | 661.9185 | 500.8156
2726.3167 | 732.8328 | 464.2343 | 651.8502 | 715.8926 | 563.1742 | 630.2053 | 662.1529 | 501.0378
2727.3167 | 728.5163 | 464.2906 | 651.464 | 710.143 | 562.0632 | 630.4332 | 662.3337 | 501.2496
2728.3167 | 729.0761 | 464.4342 | 651.0927 | 712.8016 | 562.2591 | 630.6193 | 662.5198 | 501.4737
2729.3167 | 730.1831 | 464.4977 | 652.186 | 711.789 | 565.8248 | 630.7734 | 662.6587 | 501.6631
2730.3167 | 728.1213 | 464.7048 | 651.0314 | 710.8549 | 567.187 | 631.2314 | 662.8424 | 501.9024
2731.3167 | 728.7632 | 464.7629 | 648.3472 | 703.1216 | 567.6409 | 631.53 | 663.0392 | 502.1203
2732.3167 | 727.1409 | 465.0399 | 649.2456 | 702.9395 | 567.2222 | 631.411 | 663.1681 | 502.3162
2733.3167 | 725.5851 | 465.058 | 650.2418 | 703.7178 | 566.3453 | 631.6599 | 663.3702 | 502.538
2734.3167 | 724.8647 | 465.2778 | 653.2555 | 703.9712 | 564.9853 | 632.1027 | 663.6424 | 502.7912
2735.3167 | 728.9702 | 465.3139 | 648.8107 | 696.1544 | 562.5038 | 632.4464 | 663.8167 | 503.0078
2736.3167 | 725.7056 | 465.4118 | 649.8929 | 695.1536 | 561.0946 | 632.3748 | 663.9844 | 503.2334
2737.3167 | 726.0987 | 465.4941 | 651.4344 | 699.223 | 560.7234 | 632.5024 | 664.2196 | 503.4293
2738.3167 | 728.5219 | 465.4772 | 651.4747 | 702.8236 | 561.6914 | 632.5005 | 664.5025 | 503.649
2739.3167 | 726.5908 | 465.7176 | 648.5803 | 698.3396 | 563.2909 | 632.826 | 664.645 | 503.8666
2740.3167 | 725.6844 | 465.9326 | 647.0986 | 693.9299 | 564.3057 | 632.9695 | 664.7825 | 504.0981
2741.3167 | 723.624 | 466.4456 | 645.7677 | 694.1117 | 565.5167 | 633.0026 | 664.8955 | 504.3017
2742.3167 | 723.3434 | 466.3742 | 642.2943 | 691.4609 | 567.7617 | 633.1637 | 665.0376 | 504.5162
2743.3167 | 719.7599 | 466.4141 | 637.3895 | 688.2745 | 567.7527 | 633.2876 | 665.1669 | 504.7304
2744.3167 | 718.1093 | 466.6414 | 635.5842 | 685.8669 | 567.1557 | 633.1248 | 665.3426 | 504.9499
2745.3167 | 718.985 | 466.7141 | 637.2888 | 691.4698 | 568.5903 | 633.1243 | 665.4947 | 505.1691
2746.3167 | 721.7515 | 466.947 | 636.6059 | 693.8646 | 571.0116 | 633.0919 | 665.627 | 505.4136
2747.3167 | 723.7484 | 467.0144 | 637.3028 | 695.4274 | 571.0269 | 633.1197 | 665.8404 | 505.6614
2748.3167 | 728.3195 | 467.0706 | 638.7875 | 698.6151 | 568.7925 | 633.1897 | 666.082 | 505.8894
2749.3167 | 731.5512 | 467.256 | 643.3748 | 698.1678 | 567.35 | 633.3745 | 666.3762 | 506.1471
2750.3167 | 737.9502 | 467.4811 | 643.0931 | 699.2341 | 565.8056 | 633.6182 | 666.6625 | 506.387
2751.3167 | 740.0491 | 467.4412 | 642.7675 | 695.6638 | 564.0185 | 633.7284 | 666.9536 | 506.6288
2752.3167 | 740.0414 | 467.4646 | 643.6721 | 694.7249 | 562.2536 | 633.8211 | 667.1836 | 506.8681
2753.3167 | 738.1517 | 467.8768 | 644.444 | 697.8537 | 561.6508 | 633.9038 | 667.4458 | 507.0827
2754.3167 | 737.4458 | 468.1331 | 642.938 | 695.7727 | 560.0935 | 634.1462 | 667.6792 | 507.3148
2755.3167 | 733.3147 | 468.2527 | 641.6836 | 694.2893 | 559.2859 | 634.3871 | 667.8454 | 507.5609
2756.3167 | 733.1601 | 468.3734 | 641.4848 | 701.7651 | 559.3203 | 634.3816 | 668.0496 | 507.7731
2757.3167 | 734.301 | 468.1295 | 641.4149 | 698.7271 | 558.8267 | 634.6277 | 668.2603 | 508.0328
2758.3167 | 732.7574 | 468.0929 | 639.1179 | 694.8019 | 559.5245 | 634.7631 | 668.4465 | 508.2711
2759.3167 | 733.4406 | 468.2454 | 638.4189 | 695.1375 | 561.1148 | 634.7511 | 668.577 | 508.4815
2760.3167 | 735.1526 | 468.3885 | 638.0008 | 693.8986 | 565.2144 | 634.7996 | 668.8185 | 508.7445
2761.3167 | 736.3312 | 468.6198 | 637.1914 | 697.5827 | 566.0996 | 634.7534 | 669.0596 | 509.0059
2762.3167 | 735.0798 | 468.6493 | 637.6155 | 698.5412 | 568.0367 | 634.7632 | 669.2373 | 509.2774
2763.3167 | 731.9595 | 468.674 | 637.1911 | 698.3989 | 569.3257 | 634.8205 | 669.4284 | 509.5229
2764.3167 | 729.0025 | 468.9244 | 635.5759 | 694.8824 | 571.212 | 634.9935 | 669.6476 | 509.8044
2765.3167 | 729.8557 | 469.0693 | 632.2966 | 697.5981 | 571.466 | 635.5752 | 670.0468 | 510.3013
2766.3167 | 730.0481 | 469.2685 | 630.5259 | 693.0894 | 573.5865 | 635.8188 | 670.3739 | 510.6492
2767.3167 | 724.8617 | 469.4218 | 627.0276 | 687.6471 | 575.7913 | 634.8486 | 670.346 | 510.5735
2768.3167 | 721.5918 | 469.616 | 625.1463 | 687.1244 | 576.3037 | 634.7128 | 670.4583 | 510.8642
2769.3167 | 722.6797 | 469.7826 | 626.3757 | 692.2527 | 578.5758 | 634.4525 | 670.6732 | 511.1457
2770.3167 | 722.6359 | 469.8869 | 627.6243 | 691.6463 | 580.9072 | 634.5794 | 670.8916 | 511.4423
2771.3167 | 719.8091 | 470.0256 | 623.7438 | 687.0299 | 584.226 | 634.6527 | 671.025 | 511.7241
2772.3167 | 718.7634 | 470.2622 | 618.4435 | 681.8636 | 586.1862 | 634.6274 | 671.2844 | 512.0333
2773.3167 | 720.0016 | 470.369 | 613.9749 | 678.5256 | 585.6802 | 634.7123 | 671.5128 | 512.4156
2774.3167 | 712.5781 | 470.5476 | 612.3652 | 676.4897 | 585.836 | 634.2174 | 671.5755 | 512.6196
2775.3167 | 712.3639 | 470.6649 | 612.2086 | 675.2973 | 583.9135 | 634.14 | 671.7152 | 512.9141
2776.3167 | 714.3894 | 470.8322 | 614.8366 | 676.3614 | 583.7824 | 633.8389 | 671.8095 | 513.2089
2777.3167 | 716.3787 | 470.9494 | 617.9259 | 680.4982 | 583.4154 | 633.7966 | 671.9251 | 513.5206
2778.3167 | 714.9821 | 471.0102 | 618.2576 | 687.3074 | 582.9442 | 633.9251 | 672.1139 | 513.8518
2779.3167 | 715.5153 | 471.0766 | 619.0179 | 689.3906 | 581.8741 | 633.9023 | 672.2413 | 514.1705
2780.3167 | 715.4995 | 471.21 | 619.6687 | 685.792 | 582.2683 | 633.957 | 672.3841 | 514.4972
2781.3167 | 717.595 | 471.3193 | 618.5984 | 682.8949 | 582.4475 | 633.9808 | 672.5298 | 514.8379
2782.3167 | 715.1757 | 471.5307 | 615.5959 | 679.4153 | 581.6059 | 634.0482 | 672.7945 | 515.1671
2783.3167 | 713.8053 | 471.6308 | 613.3109 | 680.9698 | 579.9236 | 633.8309 | 672.9208 | 515.4606
2784.3167 | 716.0017 | 471.7175 | 613.1187 | 678.7187 | 579.5763 | 633.7361 | 673.0164 | 515.7636
2785.3167 | 716.8271 | 471.8701 | 614.9228 | 679.9711 | 579.9971 | 633.5466 | 673.1378 | 516.0915
2786.3167 | 715.4192 | 471.9513 | 616.1657 | 681.5114 | 579.3677 | 633.5635 | 673.2852 | 516.4105
2787.3167 | 713.2203 | 472.2688 | 615.3584 | 681.3784 | 577.8936 | 633.5423 | 673.4187 | 516.7676
2788.3167 | 712.6339 | 472.398 | 618.1514 | 682.8583 | 575.6333 | 633.485 | 673.4941 | 517.1003
2789.3167 | 713.1283 | 472.398 | 618.867 | 682.9929 | 574.9141 | 633.4957 | 673.6626 | 517.4071
2790.3167 | 713.0726 | 472.5026 | 618.5249 | 684.2948 | 574.3661 | 633.4104 | 673.7848 | 517.7305
2791.3167 | 712.5905 | 472.6487 | 618.796 | 682.5023 | 574.8375 | 633.3061 | 673.9167 | 518.1265
2792.3167 | 709.256 | 472.7489 | 617.4182 | 679.3067 | 574.6479 | 633.2465 | 674.0483 | 518.5293
2793.3167 | 705.5342 | 472.9563 | 615.6832 | 678.7128 | 574.2981 | 633.129 | 674.1985 | 518.8714
2794.3167 | 702.8423 | 473.036 | 616.8802 | 676.7668 | 573.0227 | 633.1135 | 674.4015 | 519.2381
2795.3167 | 703.1293 | 473.1253 | 617.5961 | 678.2651 | 571.2789 | 632.9828 | 674.5157 | 519.5598
2796.3167 | 703.9248 | 473.2973 | 618.624 | 678.5181 | 571.7899 | 632.9585 | 674.6543 | 519.8964
2797.3167 | 702.5683 | 473.3917 | 615.994 | 676.3537 | 571.9487 | 632.9706 | 674.8499 | 520.2385
2798.3167 | 701.2076 | 473.6974 | 614.1673 | 671.9243 | 570.1619 | 632.9805 | 675.1011 | 520.568
2799.3167 | 699.8502 | 473.9088 | 612.6269 | 669.3441 | 568.0687 | 632.7103 | 675.2346 | 520.867
2800.3167 | 698.4502 | 473.7976 | 611.1247 | 669.6315 | 567.3171 | 632.7298 | 675.3876 | 521.1183
2801.3167 | 699.049 | 473.98 | 609.8458 | 670.6786 | 568.7564 | 632.4381 | 675.5377 | 521.4617
2802.3167 | 698.6083 | 474.1675 | 606.7421 | 668.3262 | 569.5112 | 632.3377 | 675.7398 | 521.9713
2803.3167 | 700.9358 | 474.3522 | 604.9174 | 670.206 | 572.187 | 632.1352 | 675.9112 | 522.2353
2804.3167 | 706.0114 | 474.4872 | 602.1159 | 671.1078 | 575.6656 | 631.9853 | 676.0697 | 522.6588
2805.3167 | 712.6152 | 474.6531 | 600.7672 | 668.9631 | 577.3008 | 631.7414 | 676.2047 | 522.9784
2806.3167 | 711.7535 | 474.8862 | 600.7754 | 666.5202 | 579.3056 | 631.5049 | 676.3001 | 523.3908
2807.3167 | 708.8919 | 475.107 | 602.4329 | 667.1452 | 578.0951 | 631.2731 | 676.5134 | 523.7264
2808.3167 | 707.8255 | 475.2817 | 605.3957 | 670.3626 | 576.455 | 631.1506 | 676.6204 | 524.0438
2809.3167 | 706.4607 | 475.3774 | 605.0555 | 671.0006 | 576.1804 | 631.1348 | 676.7031 | 524.3757
2810.3167 | 703.9628 | 475.6542 | 602.6826 | 667.4078 | 574.5914 | 631.1214 | 676.8056 | 524.6845
2811.3167 | 704.2967 | 475.9332 | 603.5767 | 670.2087 | 573.0317 | 630.7814 | 677.2062 | 525.0149
2812.3167 | 703.6961 | 475.8609 | 604.7788 | 669.3953 | 573.9422 | 630.7227 | 677.4538 | 525.3484
2813.3167 | 703.9922 | 476.0045 | 607.4533 | 670.5677 | 572.2957 | 630.4869 | 677.7348 | 525.672
2814.3167 | 707.4836 | 475.8851 | 608.7843 | 671.447 | 571.7554 | 630.5608 | 677.9382 | 526.0757
2815.3167 | 713.3174 | 475.933 | 610.2271 | 671.402 | 571.5209 | 630.5201 | 678.3048 | 526.4319
2816.3167 | 716.8277 | 475.9912 | 610.9179 | 667.3186 | 570.9932 | 630.5098 | 678.6936 | 526.7323
2817.3167 | 715.7715 | 476.1571 | 610.2358 | 668.734 | 570.5252 | 630.4488 | 678.8815 | 527.0505
2818.3167 | 714.8076 | 476.3111 | 609.1351 | 667.9145 | 572.4914 | 630.2834 | 678.9371 | 527.3819
2819.3167 | 714.4123 | 476.4168 | 606.4865 | 667.8377 | 573.6815 | 630.1472 | 679.0181 | 527.7198
2820.3167 | 713.7803 | 476.5695 | 607.9476 | 670.8411 | 574.3453 | 629.7955 | 679.0875 | 528.0272
2821.3167 | 713.2576 | 476.6816 | 609.4899 | 671.9005 | 576.4391 | 629.7491 | 679.2102 | 528.3658
2822.3167 | 712.193 | 476.9425 | 608.5432 | 672.372 | 576.1682 | 629.6901 | 679.3493 | 528.7068
2823.3167 | 709.0669 | 477.1281 | 607.2245 | 668.9582 | 575.0352 | 629.6563 | 679.5274 | 529.0044
2824.3167 | 706.4901 | 477.237 | 603.2818 | 669.9018 | 574.9632 | 629.526 | 679.5345 | 529.3222
2825.3167 | 704.634 | 477.2376 | 600.3227 | 669.3469 | 573.6484 | 629.3084 | 679.6915 | 529.6698
2826.3167 | 703.3139 | 477.5292 | 602.7079 | 671.4684 | 571.6431 | 628.798 | 679.7384 | 529.9826
2827.3167 | 705.4498 | 477.7287 | 604.8055 | 671.8207 | 569.8907 | 628.9415 | 679.9463 | 530.2871
2828.3167 | 709.568 | 477.7709 | 605.6159 | 668.0442 | 567.8773 | 628.9384 | 679.8448 | 530.5885
2829.3167 | 712.11 | 477.6636 | 606.0062 | 667.0468 | 567.1756 | 628.8138 | 679.9205 | 530.8837
2830.3167 | 715.2649 | 477.7988 | 607.7325 | 671.2173 | 566.6539 | 628.8551 | 680.0069 | 531.2108
2831.3167 | 713.7742 | 478.1857 | 608.4039 | 672.642 | 566.5918 | 628.6016 | 679.9516 | 531.457
2832.3167 | 716.027 | 478.3695 | 609.8672 | 672.5456 | 568.6303 | 628.4755 | 679.9831 | 531.705
2833.3167 | 717.471 | 478.4569 | 609.362 | 672.8033 | 568.6915 | 628.3043 | 679.9773 | 531.9828
2834.3167 | 720.1128 | 478.5259 | 609.7655 | 674.6575 | 567.6764 | 628.2614 | 680.1292 | 532.239
2835.3167 | 721.3733 | 478.6222 | 609.9271 | 676.3447 | 566.2446 | 628.1602 | 680.1635 | 532.5048
2836.3167 | 721.1971 | 478.954 | 608.9832 | 675.1213 | 565.4378 | 628.098 | 680.3884 | 532.6883
2837.3167 | 721.8663 | 479.1268 | 610.0894 | 680.6668 | 565.1187 | 627.9209 | 680.5223 | 533.0604
2838.3167 | 720.4532 | 479.1608 | 611.435 | 678.4922 | 563.8746 | 627.9074 | 680.5215 | 533.3526
2839.3167 | 721.8841 | 479.698 | 611.9385 | 677.2657 | 563.0247 | 628.6424 | 680.7513 | 533.9214
2840.3167 | 722.2694 | 480.2903 | 612.8492 | 680.6077 | 564.1913 | 627.8227 | 680.6103 | 533.9252
2841.3167 | 719.9834 | 479.9126 | 612.9371 | 681.7543 | 564.0442 | 627.7092 | 680.8066 | 534.1116
2842.3167 | 718.4499 | 479.7348 | 614.3158 | 683.0788 | 564.0593 | 627.6022 | 680.9995 | 534.2953
2843.3167 | 717.3381 | 479.9023 | 614.422 | 683.3878 | 564.5941 | 627.4805 | 681.0267 | 534.6488
2844.3167 | 719.0692 | 480.0438 | 619.2504 | 684.3057 | 564.8178 | 627.402 | 681.1192 | 534.9242
2845.3167 | 722.6908 | 480.1642 | 621.9733 | 687.1372 | 565.082 | 627.3294 | 681.2782 | 535.1321
2846.3167 | 728.3729 | 480.3324 | 622.7334 | 687.5095 | 563.771 | 627.3654 | 681.6043 | 535.3968
2847.3167 | 735.2626 | 480.4901 | 622.7094 | 689.2 | 562.6396 | 627.282 | 681.9884 | 535.6247
2848.3167 | 736.4577 | 480.5906 | 621.7509 | 688.382 | 562.133 | 627.3275 | 682.054 | 535.8679
2849.3167 | 737.0171 | 480.7993 | 622.4299 | 688.9287 | 561.9414 | 627.2812 | 682.1164 | 536.0273
2850.3167 | 737.9576 | 481.0054 | 622.3235 | 688.3351 | 561.9316 | 627.3083 | 682.3383 | 536.3171
2851.3167 | 740.2339 | 481.2497 | 622.2339 | 688.2567 | 563.6673 | 626.9781 | 682.3268 | 536.4678
2852.3167 | 739.8345 | 481.482 | 620.3643 | 685.0273 | 564.4347 | 627.1346 | 682.5187 | 536.7956
2853.3167 | 738.0973 | 481.6905 | 618.3098 | 681.9745 | 565.4586 | 627.8219 | 682.7674 | 537.3026
2854.3167 | 734.1392 | 481.8076 | 615.951 | 678.4928 | 567.7113 | 626.894 | 682.5808 | 537.1015
2855.3167 | 731.5438 | 481.8856 | 615.0816 | 682.8885 | 570.6311 | 626.7335 | 682.5073 | 537.4324
2856.3167 | 730.1045 | 482.1581 | 615.4786 | 680.3162 | 572.9272 | 626.6288 | 682.5171 | 537.656
2857.3167 | 727.0147 | 482.3529 | 614.3299 | 679.3493 | 571.8347 | 626.4493 | 682.6077 | 537.817
2858.3167 | 725.5265 | 482.6177 | 612.6658 | 679.4189 | 571.2055 | 626.3521 | 682.574 | 537.9598
2859.3167 | 723.5367 | 482.8418 | 613.4811 | 682.7498 | 570.9125 | 626.0946 | 682.591 | 538.2838
2860.3167 | 722.3051 | 483.4871 | 615.5622 | 687.1955 | 571.553 | 625.8951 | 682.5976 | 538.4806
2861.3167 | 722.0675 | 483.3826 | 616.1576 | 686.9786 | 572.95 | 625.9074 | 682.7389 | 538.7265
2862.3167 | 720.0771 | 483.5353 | 616.6725 | 685.9568 | 572.6255 | 625.7968 | 682.8338 | 538.9189
2863.3167 | 720.1861 | 484.0885 | 618.3857 | 684.0413 | 570.8721 | 625.7457 | 682.848 | 539.0377
2864.3167 | 725.6382 | 484.7039 | 619.6871 | 682.9242 | 569.8809 | 625.5332 | 683.0288 | 539.2304
2865.3167 | 724.7642 | 484.4787 | 619.2159 | 679.9724 | 567.798 | 625.6316 | 683.2157 | 539.4426
2866.3167 | 724.5396 | 484.2966 | 615.6913 | 674.7689 | 566.2866 | 625.671 | 683.4025 | 539.6448
2867.3167 | 722.3112 | 484.297 | 615.2449 | 674.0187 | 565.0196 | 625.4614 | 683.3558 | 539.9331
2868.3167 | 722.1989 | 484.4025 | 615.6563 | 675.3779 | 565.7341 | 625.295 | 683.2751 | 540.0245
2869.3167 | 721.4518 | 484.9722 | 614.9273 | 675.0765 | 565.6721 | 625.0894 | 683.2489 | 540.2988
2870.3167 | 720.4559 | 484.8879 | 616.9051 | 677.1961 | 565.6996 | 624.8784 | 683.2726 | 540.4614
2871.3167 | 723.7479 | 484.8265 | 618.5251 | 679.2916 | 566.6485 | 624.6089 | 683.2993 | 540.6827
2872.3167 | 726.4813 | 484.811 | 616.3305 | 681.0935 | 566.6107 | 624.7586 | 683.5155 | 540.8886
2873.3167 | 728.7279 | 484.9968 | 615.8908 | 679.8014 | 565.8243 | 624.5153 | 683.5712 | 541.1059
2874.3167 | 729.2515 | 485.2159 | 614.3002 | 678.0856 | 564.6353 | 624.3631 | 683.6199 | 541.2812
2875.3167 | 731.2251 | 485.3385 | 615.7034 | 677.4733 | 565.204 | 624.0411 | 683.6345 | 541.4947
2876.3167 | 731.9254 | 485.5315 | 615.0967 | 674.0145 | 564.0385 | 623.996 | 683.642 | 541.6735
2877.3167 | 730.6306 | 485.6892 | 613.3019 | 675.8257 | 565.0559 | 623.7061 | 683.5652 | 541.8481
2878.3167 | 729.4755 | 485.8726 | 612.1881 | 678.6532 | 567.4275 | 623.6488 | 683.5428 | 542.0404
2879.3167 | 726.2143 | 485.9657 | 611.8509 | 678.9884 | 569.2803 | 623.5729 | 683.441 | 542.247
2880.3167 | 724.5525 | 486.2233 | 612.072 | 679.4597 | 572.6018 | 623.2237 | 683.4901 | 542.4471
2881.3167 | 726.0893 | 486.7008 | 613.6666 | 682.7275 | 573.9711 | 622.8609 | 683.4704 | 542.6393
2882.3167 | 724.094 | 486.7081 | 613.3975 | 678.7076 | 575.8824 | 622.7468 | 683.3994 | 542.8724
2883.3167 | 721.1244 | 486.9382 | 612.735 | 678.3681 | 575.9833 | 622.7317 | 683.458 | 543.0668
2884.3167 | 719.3574 | 487.2014 | 614.4792 | 678.8761 | 574.4039 | 622.6287 | 683.4446 | 543.258
2885.3167 | 717.0697 | 487.6347 | 611.0533 | 674.8742 | 572.5236 | 622.6154 | 683.4293 | 543.4649
2886.3167 | 715.4235 | 487.819 | 611.6859 | 673.4111 | 570.2883 | 622.4577 | 683.3686 | 543.6634
2887.3167 | 715.5102 | 487.8178 | 612.6345 | 675.769 | 568.0761 | 622.2762 | 683.3297 | 543.8553
2888.3167 | 720.2388 | 487.8935 | 613.6086 | 674.8329 | 569.9325 | 622.3131 | 683.2959 | 544.0435
2889.3167 | 720.1169 | 488.0809 | 613.8425 | 679.3803 | 572.4953 | 622.2674 | 683.374 | 544.2296
2890.3167 | 722.2006 | 488.4073 | 615.7082 | 680.3473 | 575.5133 | 621.8938 | 683.3659 | 544.4399
2891.3167 | 722.4799 | 488.4965 | 613.516 | 679.6228 | 575.5609 | 622.1401 | 683.5252 | 544.6917
2892.3167 | 723.303 | 488.814 | 612.3574 | 677.9207 | 573.7797 | 621.9651 | 683.7233 | 544.8907
2893.3167 | 722.3223 | 488.8423 | 612.7476 | 679.0585 | 572.565 | 621.7356 | 683.876 | 545.0823
2894.3167 | 724.2748 | 488.9048 | 610.1776 | 676.3454 | 570.5321 | 621.8147 | 683.8612 | 545.2716
2895.3167 | 723.8992 | 489.062 | 610.6477 | 677.351 | 568.9709 | 621.4579 | 683.9021 | 545.4435
2896.3167 | 725.6255 | 489.1465 | 611.8323 | 679.393 | 567.2649 | 621.4479 | 684.0301 | 545.6292
2897.3167 | 728.2331 | 489.1795 | 612.0159 | 676.8388 | 565.5464 | 621.3491 | 683.9884 | 545.7993
2898.3167 | 728.2921 | 489.5292 | 611.7371 | 677.3901 | 567.3325 | 621.36 | 684.0122 | 545.9911
2899.3167 | 726.9593 | 489.7052 | 611.2805 | 677.4719 | 568.1643 | 621.2667 | 683.8747 | 546.1614
2900.3167 | 726.2237 | 490.083 | 609.9772 | 679.0649 | 568.1674 | 620.9288 | 683.9337 | 546.3482
2901.3167 | 726.7712 | 489.9344 | 610.4665 | 678.0779 | 570.0287 | 620.859 | 683.8218 | 546.5278
2902.3167 | 728.3658 | 490.2745 | 609.2603 | 674.7476 | 572.1793 | 620.747 | 683.8407 | 546.7259
2903.3167 | 726.3391 | 490.4414 | 611.0889 | 677.5807 | 573.4913 | 620.6868 | 683.9604 | 546.9186
2904.3167 | 726.3252 | 490.7728 | 612.4741 | 680.6569 | 574.3807 | 620.4346 | 683.9909 | 547.1181
2905.3167 | 729.6136 | 490.8907 | 612.2455 | 684.2752 | 573.7486 | 620.3571 | 684.0413 | 547.2989
2906.3167 | 730.4437 | 490.9512 | 612.3196 | 686.8678 | 571.7867 | 620.1891 | 684.1885 | 547.4625
2907.3167 | 733.3377 | 490.9411 | 611.9731 | 685.4736 | 570.913 | 620.2186 | 684.2218 | 547.6264
2908.3167 | 734.5437 | 491.1347 | 610.7208 | 683.8137 | 572.2945 | 620.1675 | 684.253 | 547.8012
2909.3167 | 733.3191 | 491.3253 | 610.9949 | 682.8235 | 572.5482 | 620.0118 | 684.264 | 547.9705
2910.3167 | 730.506 | 491.4789 | 610.1378 | 680.7835 | 571.9974 | 620.1357 | 684.3317 | 548.1745
2911.3167 | 727.4172 | 491.6903 | 607.7322 | 679.9432 | 571.9739 | 620.0465 | 684.3497 | 548.3202
2912.3167 | 725.1501 | 491.9462 | 606.5008 | 675.0206 | 572.8471 | 619.9285 | 684.3477 | 548.5042
2913.3167 | 727.9374 | 492.0357 | 604.5532 | 675.2655 | 574.058 | 619.5107 | 684.3684 | 548.6645
2914.3167 | 731.7114 | 492.3428 | 601.9848 | 671.5017 | 575.7739 | 619.3582 | 684.4051 | 548.8788
2915.3167 | 729.7204 | 492.5963 | 599.7837 | 669.5466 | 577.0133 | 619.2697 | 684.4318 | 549.0612
2916.3167 | 727.495 | 492.836 | 598.917 | 666.7253 | 579.1419 | 619.1171 | 684.3924 | 549.2398
2917.3167 | 726.047 | 492.9125 | 597.25 | 663.4223 | 582.2609 | 618.9418 | 684.4754 | 549.4733
2918.3167 | 725.3566 | 493.0718 | 593.1651 | 658.607 | 583.4859 | 618.7974 | 684.5173 | 549.6668
2919.3167 | 722.8982 | 493.2653 | 590.2555 | 657.6197 | 583.1922 | 618.4883 | 684.4747 | 549.8822
2920.3167 | 722.9123 | 493.4543 | 590.0859 | 656.8346 | 584.6069 | 618.2551 | 684.2674 | 550.1171
2921.3167 | 719.718 | 493.7062 | 588.4279 | 657.2418 | 584.8903 | 618.0726 | 684.1381 | 550.3433
2922.3167 | 718.923 | 493.8649 | 587.5962 | 658.7708 | 583.2916 | 617.6152 | 684.1021 | 550.548
2923.3167 | 719.1289 | 494.1238 | 589.5653 | 660.8848 | 584.2815 | 617.4302 | 684.0539 | 550.7793
2924.3167 | 717.49 | 494.3591 | 588.9529 | 662.0824 | 586.5069 | 617.0987 | 683.9268 | 551.0322
2925.3167 | 713.7385 | 494.462 | 588.8406 | 663.2843 | 587.2045 | 616.8166 | 683.792 | 551.2661
2926.3167 | 712.1015 | 494.8079 | 587.7541 | 664.8597 | 586.2816 | 616.4704 | 683.8072 | 551.4861
2927.3167 | 711.1798 | 495.1006 | 588.3413 | 667.7589 | 585.7631 | 616.1158 | 683.6157 | 551.7057
2928.3167 | 709.6279 | 495.3861 | 588.6657 | 665.9374 | 585.92 | 615.9463 | 683.4171 | 551.9381
2929.3167 | 709.8883 | 495.6378 | 591.5443 | 667.4627 | 585.6921 | 615.6074 | 683.396 | 552.1658
2930.3167 | 709.5072 | 495.8559 | 592.5265 | 667.9176 | 584.7056 | 615.5068 | 683.3421 | 552.434
2931.3167 | 709.2778 | 496.1024 | 590.3114 | 665.4238 | 584.1204 | 615.3894 | 683.3233 | 552.6995
2932.3167 | 708.0861 | 496.3279 | 587.4888 | 660.6975 | 581.03 | 615.6396 | 683.4357 | 553.0979
2933.3167 | 704.6182 | 496.6757 | 585.5865 | 661.2806 | 577.75 | 614.8532 | 683.3322 | 553.1751
2934.3167 | 701.7379 | 496.862 | 583.7021 | 662.2993 | 576.078 | 614.5676 | 683.1842 | 553.3857
2935.3167 | 700.0142 | 497.0869 | 582.814 | 663.307 | 574.4458 | 614.1858 | 683.0639 | 553.6017
2936.3167 | 697.9055 | 497.449 | 583.0723 | 663.3559 | 573.3924 | 613.8495 | 683.0393 | 553.8217
2937.3167 | 696.9867 | 497.5911 | 582.2494 | 660.7726 | 572.2606 | 613.6038 | 683.0033 | 554.0507
2938.3167 | 697.8835 | 497.8765 | 583.6772 | 661.7547 | 571.6514 | 613.2535 | 682.9213 | 554.27
2939.3167 | 697.208 | 498.1879 | 580.126 | 659.4892 | 572.019 | 612.9742 | 682.9591 | 554.506
2940.3167 | 698.743 | 498.6853 | 580.3905 | 660.4075 | 571.6445 | 612.9699 | 683.1045 | 554.8518
2941.3167 | 700.6055 | 498.7493 | 584.6076 | 664.0535 | 570.5235 | 612.9599 | 683.0198 | 555.1258
2942.3167 | 699.5662 | 499.0719 | 585.1086 | 664.087 | 570.5703 | 612.0405 | 682.7087 | 555.1766
2943.3167 | 698.1885 | 499.4736 | 583.6248 | 664.6051 | 569.569 | 611.8546 | 682.6359 | 555.3902
2944.3167 | 698.9294 | 499.8445 | 582.8321 | 663.631 | 568.1598 | 611.4314 | 682.5044 | 555.6163
2945.3167 | 701.3694 | 500.1017 | 585.6137 | 664.1659 | 566.8176 | 611.1237 | 682.3036 | 555.8139
2946.3167 | 703.6468 | 500.0143 | 590.3885 | 666.3635 | 566.3301 | 610.9002 | 682.3079 | 556.0218
2947.3167 | 704.3673 | 500.138 | 591.2331 | 666.6019 | 567.0979 | 611.3435 | 682.4714 | 556.434
2948.3167 | 706.2485 | 500.2982 | 594.9307 | 669.5953 | 569.2993 | 610.5365 | 682.3356 | 556.432
2949.3167 | 710.5615 | 500.5583 | 594.4621 | 662.837 | 567.8675 | 610.6493 | 682.3577 | 556.6357
2950.3167 | 713.0729 | 500.6373 | 594.0193 | 656.5963 | 566.227 | 610.5738 | 682.327 | 556.7899
2951.3167 | 710.8533 | 501.0085 | 590.9286 | 651.1425 | 566.6481 | 610.5457 | 682.2423 | 556.9325
2952.3167 | 709.2431 | 501.2711 | 591.6131 | 652.9073 | 565.6811 | 610.32 | 682.1561 | 557.1414
2953.3167 | 708.8201 | 501.4074 | 591.6358 | 654.7462 | 565.3466 | 610.0183 | 681.9306 | 557.2623
2954.3167 | 709.4194 | 501.6701 | 591.5507 | 657.3714 | 566.1378 | 609.6343 | 681.7676 | 557.3981
2955.3167 | 709.1114 | 501.9937 | 591.8281 | 657.3412 | 567.3373 | 609.4588 | 681.7713 | 557.5663
2956.3167 | 709.415 | 502.2538 | 592.425 | 658.1345 | 567.5699 | 609.2122 | 681.7185 | 557.7434
2957.3167 | 712.9618 | 502.3773 | 592.0793 | 662.5004 | 570.7936 | 608.91 | 681.5826 | 557.8855
2958.3167 | 710.4917 | 502.8083 | 592.4111 | 663.1599 | 572.7361 | 608.633 | 681.4459 | 558.0545
2959.3167 | 709.6799 | 503.0416 | 591.0419 | 668.0384 | 572.179 | 608.2411 | 681.3072 | 558.2074
2960.3167 | 709.3033 | 503.3839 | 592.1656 | 668.768 | 573.2916 | 608.147 | 681.2954 | 558.3667
2961.3167 | 709.4347 | 504.0554 | 592.0576 | 667.8546 | 573.2355 | 608.005 | 681.2923 | 558.5147
2962.3167 | 709.5837 | 504.6583 | 589.4607 | 665.9936 | 573.2434 | 607.6569 | 681.3041 | 558.6625
2963.3167 | 707.9984 | 504.5635 | 588.8723 | 662.285 | 573.3479 | 607.5053 | 681.3479 | 558.8274
2964.3167 | 706.6177 | 504.7759 | 584.5096 | 658.7616 | 573.621 | 607.3577 | 681.4561 | 558.9797
2965.3167 | 705.2739 | 504.9856 | 581.7144 | 655.6135 | 572.5819 | 606.9908 | 681.3973 | 559.1051
2966.3167 | 702.9709 | 505.7019 | 582.3922 | 656.323 | 571.8385 | 606.5597 | 681.2987 | 559.2464
2967.3167 | 703.5758 | 506.0024 | 585.5052 | 662.2156 | 569.7807 | 606.1278 | 681.3167 | 559.3985
2968.3167 | 707.0074 | 505.9497 | 589.0906 | 661.2473 | 569.1662 | 605.935 | 681.1912 | 559.5433
2969.3167 | 707.5817 | 506.0226 | 590.5991 | 658.5952 | 570.155 | 605.8208 | 681.1378 | 559.6878
2970.3167 | 707.6854 | 506.1622 | 588.9053 | 653.3863 | 569.0063 | 605.7283 | 681.0653 | 559.8197
2971.3167 | 705.9596 | 506.448 | 587.5871 | 653.1506 | 567.1979 | 605.5552 | 680.9551 | 559.9396
2972.3167 | 703.0549 | 507.0517 | 585.8058 | 651.256 | 564.8243 | 606.028 | 681.0623 | 560.3261
2973.3167 | 704.229 | 507.0369 | 587.9595 | 654.4555 | 565.6745 | 604.8123 | 680.6451 | 560.1333
2974.3167 | 703.4699 | 507.2763 | 589.2491 | 654.3909 | 566.0809 | 604.6377 | 680.4757 | 560.2631
2975.3167 | 699.4779 | 507.6924 | 589.131 | 654.1855 | 564.6624 | 604.4348 | 680.3897 | 560.3911
2976.3167 | 696.9098 | 508.1657 | 587.6192 | 656.0114 | 563.2451 | 604.065 | 680.2822 | 560.487
2977.3167 | 699.656 | 508.259 | 588.6719 | 656.9817 | 563.7757 | 603.7436 | 680.085 | 560.5933
2978.3167 | 700.2172 | 508.3904 | 589.5824 | 659.9494 | 565.7996 | 603.3372 | 679.9972 | 560.7228
2979.3167 | 701.7734 | 508.8423 | 592.7575 | 658.4854 | 565.424 | 603.1392 | 680.0045 | 560.8565
2980.3167 | 705.8984 | 509.1141 | 594.4112 | 661.9933 | 565.5168 | 602.9089 | 680.0489 | 560.969
2981.3167 | 710.3608 | 509.1054 | 593.6869 | 665.033 | 566.2464 | 602.7854 | 680.0093 | 561.0866
2982.3167 | 712.3934 | 509.4807 | 593.2661 | 664.2755 | 565.407 | 602.5107 | 679.9929 | 561.1889
2983.3167 | 713.3567 | 509.568 | 593.5075 | 662.9655 | 564.3775 | 602.2889 | 679.9882 | 561.2883
2984.3167 | 713.8603 | 509.7246 | 594.51 | 664.4224 | 564.6973 | 602.0085 | 679.9365 | 561.3691
2985.3167 | 716.9704 | 509.9631 | 596.0153 | 665.5712 | 564.6126 | 601.7996 | 679.9534 | 561.4669
2986.3167 | 718.8117 | 510.4653 | 597.23 | 663.6201 | 565.2764 | 601.6732 | 679.9181 | 561.5561
2987.3167 | 721.4665 | 510.981 | 599.1 | 668.8451 | 568.0791 | 601.2101 | 679.8792 | 561.658
2988.3167 | 724.6595 | 511.1211 | 598.0011 | 667.0718 | 568.7172 | 601.3819 | 679.8696 | 561.8608
2989.3167 | 726.7105 | 511.4194 | 598.3436 | 666.9529 | 568.0367 | 600.9175 | 679.9103 | 561.9114
2990.3167 | 725.3482 | 511.6276 | 597.3938 | 660.1388 | 566.0983 | 600.902 | 679.8459 | 562.0474
2991.3167 | 721.825 | 511.6589 | 595.1931 | 654.0185 | 564.4034 | 600.669 | 679.7112 | 562.1406
2992.3167 | 721.495 | 511.8575 | 594.1623 | 655.6382 | 563.2982 | 600.4216 | 679.4978 | 562.2137
2993.3167 | 721.6833 | 512.0548 | 593.2691 | 653.5891 | 564.8951 | 600.1117 | 679.302 | 562.279
2994.3167 | 718.9937 | 512.4779 | 592.4956 | 653.3602 | 567.0902 | 599.8452 | 679.188 | 562.3602
2995.3167 | 715.8326 | 512.8708 | 592.0781 | 655.8855 | 566.95 | 599.6156 | 679.1275 | 562.4762
2996.3167 | 713.4396 | 513.038 | 592.4194 | 657.9076 | 566.151 | 599.3513 | 678.9947 | 562.5688
2997.3167 | 713.7911 | 513.4058 | 594.4794 | 662.7114 | 564.8418 | 599.0474 | 678.9286 | 562.6595
2998.3167 | 711.7379 | 513.4769 | 594.3303 | 662.8398 | 563.2559 | 598.8498 | 678.7878 | 562.7292
2999.3167 | 711.9963 | 513.7763 | 594.5437 | 663.3319 | 562.299 | 598.517 | 678.6401 | 562.7968
3000.3167 | 713.3163 | 513.8389 | 596.6147 | 662.7345 | 562.4378 | 598.291 | 678.4831 | 562.8867
3001.3167 | 712.8484 | 514.1303 | 594.7686 | 661.639 | 563.7605 | 598.1494 | 678.3926 | 562.9608
3002.3167 | 709.4688 | 514.3888 | 591.9141 | 661.5705 | 563.5978 | 597.8525 | 678.4201 | 563.0459
3003.3167 | 710.7969 | 514.6074 | 593.661 | 665.2026 | 563.1501 | 597.654 | 678.4226 | 563.2102
3004.3167 | 709.1055 | 515.0367 | 594.2904 | 665.4614 | 563.2197 | 597.1793 | 678.2458 | 563.208
3005.3167 | 709.6703 | 515.3462 | 596.2213 | 666.8559 | 562.9867 | 596.8498 | 678.1699 | 563.2632
3006.3167 | 711.3051 | 515.5261 | 595.2581 | 666.9958 | 565.2615 | 596.6782 | 678.0421 | 563.3475
3007.3167 | 713.8882 | 515.6892 | 597.8506 | 668.2919 | 569.0398 | 596.2249 | 677.9473 | 563.4078
3008.3167 | 714.7388 | 516.1172 | 597.8932 | 669.8121 | 569.4812 | 595.8824 | 677.9313 | 563.4894
3009.3167 | 716.4122 | 516.6069 | 596.7868 | 667.0704 | 568.5173 | 595.7718 | 677.9199 | 563.6126
3010.3167 | 717.6363 | 516.7257 | 596.6511 | 668.9874 | 566.5204 | 595.4284 | 677.9392 | 563.6747
3011.3167 | 717.4871 | 516.8634 | 596.5749 | 667.4823 | 566.1529 | 595.1726 | 677.9844 | 563.7398
3012.3167 | 717.7832 | 517.2419 | 596.9982 | 665.2038 | 569.1191 | 594.9952 | 678.0157 | 563.8135
3013.3167 | 719.3186 | 517.5665 | 596.1881 | 664.5409 | 569.9772 | 594.6348 | 678.0019 | 563.9073
3014.3167 | 719.6539 | 517.9768 | 596.203 | 664.4728 | 570.5306 | 594.4361 | 678.0515 | 563.9775
3015.3167 | 717.6939 | 518.1144 | 594.3231 | 665.4111 | 569.2451 | 594.1565 | 678.0155 | 564.0559
3016.3167 | 717.4782 | 518.3478 | 594.5714 | 668.6215 | 568.3589 | 593.7903 | 677.9756 | 564.0957
3017.3167 | 719.8934 | 519.0321 | 594.0004 | 667.0561 | 568.7319 | 593.5989 | 677.9843 | 564.1693
3018.3167 | 716.1631 | 519.2278 | 592.2473 | 665.6667 | 569.5045 | 593.2886 | 677.9459 | 564.2272
3019.3167 | 712.4407 | 519.677 | 590.5797 | 661.7269 | 568.6746 | 593.0717 | 677.8915 | 564.308
3020.3167 | 710.5484 | 519.9887 | 590.493 | 661.8516 | 566.9338 | 592.5873 | 677.8584 | 564.3752
3021.3167 | 711.2944 | 520.0516 | 593.2845 | 660.5128 | 566.1882 | 592.4068 | 677.7721 | 564.4573
3022.3167 | 709.8701 | 520.8327 | 593.1874 | 656.4805 | 564.0915 | 592.1757 | 677.7115 | 564.5095
3023.3167 | 708.7693 | 520.9046 | 593.4309 | 656.7189 | 561.8573 | 591.9096 | 677.595 | 564.5911
3024.3167 | 708.395 | 521.0632 | 591.5041 | 657.0786 | 562.3155 | 591.6092 | 677.4763 | 564.6441
3025.3167 | 708.0771 | 521.231 | 590.0133 | 655.3378 | 566.0254 | 591.4445 | 677.386 | 564.7366
3026.3167 | 707.734 | 521.3108 | 585.4072 | 651.9459 | 567.8183 | 591.1438 | 677.3586 | 564.8192
3027.3167 | 704.5154 | 521.5386 | 582.4155 | 646.6117 | 567.5879 | 590.9621 | 677.3281 | 564.9084
3028.3167 | 702.9163 | 521.9278 | 581.5816 | 649.2529 | 566.6426 | 590.4169 | 677.2758 | 564.9544
3029.3167 | 703.909 | 522.2409 | 585.5886 | 650.7407 | 566.2837 | 589.9782 | 677.1731 | 565.0214
3030.3167 | 707.782 | 522.6305 | 584.5362 | 653.2015 | 568.1386 | 589.6013 | 677.1386 | 565.0705
3031.3167 | 706.3824 | 523.071 | 583.5593 | 656.0044 | 568.0115 | 589.3732 | 677.0883 | 565.1444
3032.3167 | 703.9538 | 523.4461 | 583.2731 | 653.2258 | 567.1973 | 589.125 | 676.9817 | 565.183
3033.3167 | 702.2078 | 523.7603 | 582.3362 | 652.7262 | 567.8123 | 588.8759 | 676.8157 | 565.2482
3034.3167 | 706.0221 | 524.1363 | 581.6492 | 649.0621 | 570.376 | 588.697 | 676.729 | 565.3363
3035.3167 | 708.8199 | 524.2694 | 579.7641 | 645.1405 | 573.5909 | 588.4631 | 676.6807 | 565.4203
3036.3167 | 706.1595 | 524.4933 | 579.6479 | 640.6558 | 573.4981 | 588.1787 | 676.5885 | 565.5209
3037.3167 | 702.454 | 524.5842 | 579.9597 | 643.7028 | 573.0104 | 587.7867 | 676.4739 | 565.5701
3038.3167 | 700.7385 | 524.9525 | 581.9064 | 642.9967 | 571.0784 | 587.4009 | 676.3886 | 565.663
3039.3167 | 701.885 | 525.7487 | 585.0895 | 643.404 | 568.5213 | 587.6643 | 676.4169 | 565.9553
3040.3167 | 705.8339 | 525.9115 | 586.7884 | 644.6452 | 566.5012 | 587.2408 | 676.2424 | 565.96
3041.3167 | 707.4155 | 525.8911 | 588.0071 | 644.7724 | 565.3436 | 586.4116 | 675.9819 | 565.9029
3042.3167 | 707.1821 | 526.1443 | 590.2982 | 650.2944 | 564.2133 | 586.0925 | 675.8963 | 565.9789
3043.3167 | 708.005 | 526.3235 | 590.7988 | 651.3286 | 562.7786 | 585.9957 | 675.8582 | 566.081
3044.3167 | 711.0518 | 526.5806 | 591.595 | 652.044 | 563.2293 | 585.7894 | 675.7709 | 566.154
3045.3167 | 712.2938 | 526.8688 | 588.7837 | 649.3412 | 566.1459 | 585.5706 | 675.6329 | 566.2531
3046.3167 | 709.7907 | 526.9872 | 586.6856 | 645.3048 | 565.8196 | 585.4225 | 675.5188 | 566.3587
3047.3167 | 708.2182 | 527.2914 | 584.718 | 647.4726 | 565.3813 | 584.9604 | 675.348 | 566.3981
3048.3167 | 707.4938 | 527.2298 | 585.1457 | 644.7795 | 567.709 | 584.8132 | 675.1741 | 566.4756
3049.3167 | 704.9257 | 527.4788 | 582.4893 | 644.3129 | 570.9682 | 584.5239 | 675.0663 | 566.5487
3050.3167 | 701.9899 | 527.7047 | 583.0446 | 647.0274 | 571.2085 | 584.1148 | 674.9686 | 566.6252
3051.3167 | 699.7479 | 528.319 | 583.2455 | 647.277 | 571.0738 | 584.0306 | 674.877 | 566.7309
3052.3167 | 697.6054 | 528.6459 | 583.1272 | 644.9218 | 568.5273 | 583.9243 | 674.7998 | 566.8107
3053.3167 | 697.3903 | 529.0615 | 585.5303 | 646.7807 | 565.7041 | 583.6319 | 674.6641 | 566.8765
3054.3167 | 699.1594 | 529.311 | 585.3759 | 644.9336 | 563.3465 | 583.5543 | 674.4726 | 566.9547
3055.3167 | 700.0785 | 529.5402 | 586.8826 | 645.3788 | 561.6524 | 583.4005 | 674.3176 | 567.0197
3056.3167 | 701.1142 | 529.6749 | 588.8516 | 648.2309 | 560.3521 | 583.3011 | 674.1775 | 567.0849
3057.3167 | 701.858 | 529.6684 | 588.1172 | 653.7064 | 561.3075 | 583.2441 | 674.0234 | 567.1512
3058.3167 | 704.6656 | 530.0879 | 587.8306 | 655.1384 | 563.4231 | 583.092 | 673.8919 | 567.2131
3059.3167 | 704.8375 | 530.4581 | 586.203 | 655.1402 | 565.2416 | 582.9975 | 673.7815 | 567.285
3060.3167 | 700.7622 | 530.625 | 585.871 | 651.5942 | 565.9945 | 582.9361 | 673.6896 | 567.3523
3061.3167 | 697.2363 | 530.6096 | 586.4416 | 651.4406 | 564.6647 | 582.7253 | 673.6104 | 567.3977
3062.3167 | 694.7096 | 530.8962 | 586.7117 | 651.9544 | 563.1597 | 582.6498 | 673.493 | 567.4432
3063.3167 | 695.9677 | 531.4427 | 586.1386 | 652.9551 | 561.8275 | 582.5219 | 673.3839 | 567.4682
3064.3167 | 696.3606 | 531.6888 | 587.2581 | 655.4151 | 561.9371 | 582.3911 | 673.3172 | 567.4884
3065.3167 | 698.9021 | 531.9137 | 588.1247 | 657.2894 | 562.0838 | 582.2915 | 673.2305 | 567.5171
3066.3167 | 696.9339 | 532.2272 | 587.5398 | 654.3475 | 562.5727 | 582.3216 | 673.156 | 567.566
3067.3167 | 698.2446 | 532.307 | 586.8456 | 655.9358 | 561.4619 | 582.1393 | 673.1154 | 567.5853
3068.3167 | 701.0839 | 532.4288 | 586.9981 | 655.8501 | 561.0423 | 582.161 | 673.0911 | 567.6112
3069.3167 | 701.0325 | 532.9102 | 587.7314 | 653.5398 | 561.046 | 582.0843 | 673.0658 | 567.6359
3070.3167 | 700.0401 | 533.254 | 588.9046 | 653.2898 | 560.2608 | 582.0447 | 673.075 | 567.6615
3071.3167 | 701.7046 | 533.2786 | 588.9579 | 652.1568 | 560.1377 | 582.0969 | 673.0215 | 567.6819
3072.3167 | 702.9495 | 533.3027 | 587.331 | 650.1019 | 561.1534 | 582.0028 | 672.9173 | 567.7076
3073.3167 | 706.5337 | 533.5377 | 587.6536 | 651.3577 | 561.8292 | 581.9399 | 672.8367 | 567.7343
3074.3167 | 705.8795 | 533.7517 | 586.8935 | 648.5679 | 564.7275 | 582.0501 | 672.7021 | 567.7769
3075.3167 | 707.2407 | 534.1664 | 586.7813 | 648.9738 | 565.0128 | 581.824 | 672.6597 | 567.783
3076.3167 | 704.7284 | 534.7749 | 586.9302 | 647.4695 | 565.8855 | 581.8504 | 672.5867 | 567.8172
3077.3167 | 700.3304 | 534.9438 | 586.4319 | 646.8542 | 564.7771 | 581.84 | 672.5141 | 567.8335
3078.3167 | 697.6657 | 535.0071 | 583.0748 | 644.7654 | 564.0268 | 581.915 | 672.4383 | 567.8553
3079.3167 | 696.9429 | 535.1157 | 580.318 | 643.8623 | 564.3374 | 581.7966 | 672.3647 | 567.8832
3080.3167 | 696.1236 | 535.359 | 580.9608 | 642.1446 | 565.7683 | 581.6726 | 672.2907 | 567.9473
3081.3167 | 698.394 | 535.5059 | 583.2074 | 642.2824 | 565.4891 | 581.4821 | 672.2864 | 567.9884
3082.3167 | 702.2638 | 535.986 | 585.3219 | 641.154 | 563.3642 | 581.5942 | 672.3101 | 568.0411
3083.3167 | 704.7521 | 536.1232 | 585.4041 | 638.5828 | 560.8996 | 581.5926 | 672.3097 | 568.0773
3084.3167 | 707.4483 | 536.3304 | 587.2164 | 637.081 | 558.7902 | 581.7549 | 672.2641 | 568.0813
3085.3167 | 707.8877 | 536.4081 | 586.2053 | 636.1241 | 558.6629 | 581.7986 | 672.1849 | 568.0847
3086.3167 | 706.7828 | 536.4998 | 585.4622 | 637.2238 | 558.7798 | 581.7181 | 672.0697 | 568.0933
3087.3167 | 706.0412 | 536.7928 | 589.6629 | 639.8408 | 559.6557 | 581.6188 | 671.9441 | 568.1161
3088.3167 | 704.0141 | 537.4487 | 589.6798 | 640.3499 | 560.8109 | 581.7752 | 671.8038 | 568.1477
3089.3167 | 704.0228 | 537.6012 | 589.8586 | 641.0355 | 561.4806 | 581.829 | 671.7111 | 568.1787
3090.3167 | 700.7483 | 537.7919 | 590.0637 | 642.2589 | 561.5519 | 581.8364 | 671.5565 | 568.1784
3091.3167 | 699.5872 | 538.1258 | 591.7518 | 643.4178 | 560.6482 | 581.8444 | 671.4542 | 568.1732
3092.3167 | 699.0419 | 538.2417 | 591.5313 | 645.1054 | 561.0998 | 581.9832 | 671.3397 | 568.1807
3093.3323 | 697.1685 | 538.3698 | 590.8942 | 642.6321 | 561.6923 | 582.1387 | 671.2452 | 568.2233
3094.3167 | 697.4245 | 538.8855 | 591.1369 | 642.7708 | 561.8933 | 582.2086 | 671.1233 | 568.2321
3095.3167 | 700.9178 | 539.2986 | 593.7469 | 642.5526 | 564.3034 | 582.318 | 671.0985 | 568.2486
3096.3167 | 701.8878 | 539.4979 | 591.8266 | 641.7184 | 564.939 | 582.3387 | 671.0009 | 568.2578
3097.3167 | 700.7235 | 539.9844 | 591.5193 | 642.3609 | 565.7893 | 582.3645 | 670.9237 | 568.2693
3098.3167 | 699.5635 | 540.8642 | 592.2079 | 644.0958 | 565.4015 | 582.345 | 670.8044 | 568.2549
3099.3167 | 701.8521 | 541.2539 | 590.9951 | 645.8221 | 565.9301 | 582.4082 | 670.654 | 568.2449
3100.3167 | 704.3323 | 541.1759 | 590.6404 | 647.518 | 566.1533 | 582.5272 | 670.573 | 568.262
3101.3167 | 706.7037 | 541.094 | 589.4288 | 647.1684 | 564.712 | 582.5758 | 670.5122 | 568.2656
3102.3167 | 709.4138 | 541.2369 | 589.9053 | 646.6748 | 563.1573 | 582.6281 | 670.4713 | 568.2628
3103.3167 | 714.2572 | 541.4106 | 590.4479 | 648.5563 | 561.7359 | 582.6351 | 670.3807 | 568.2369
3104.3167 | 715.0767 | 541.6497 | 591.1712 | 648.5024 | 560.493 | 582.6952 | 670.3213 | 568.2483
3105.3167 | 714.1946 | 541.9352 | 591.0058 | 648.4147 | 559.2999 | 582.7309 | 670.2551 | 568.252
3106.3167 | 712.7237 | 542.1869 | 591.0358 | 647.4995 | 557.8761 | 582.9645 | 670.1712 | 568.2352
3107.3167 | 711.908 | 542.338 | 589.1235 | 646.1758 | 556.2337 | 583.089 | 670.0345 | 568.2094
3108.3167 | 714.0735 | 542.4268 | 588.2095 | 645.4184 | 556.4149 | 583.2243 | 669.9731 | 568.2094
3109.3167 | 713.0807 | 542.8333 | 587.7609 | 650.728 | 557.8419 | 583.3558 | 669.8884 | 568.2045
3110.3167 | 713.659 | 543.5404 | 589.8813 | 649.4576 | 559.3398 | 583.4587 | 669.7994 | 568.2028
3111.3167 | 714.8876 | 543.8893 | 588.9643 | 649.4987 | 558.5006 | 583.4083 | 669.6761 | 568.1777
3112.3167 | 712.2835 | 544.2167 | 586.9242 | 647.0733 | 558.3467 | 583.738 | 669.5447 | 568.1956
3113.3167 | 710.0864 | 544.1874 | 585.9722 | 646.3121 | 558.0224 | 583.7767 | 669.4533 | 568.1913
3114.3167 | 706.0444 | 544.3911 | 585.4868 | 643.9098 | 557.5927 | 583.9656 | 669.3544 | 568.1954
3115.3167 | 707.4276 | 544.6363 | 585.2722 | 643.6154 | 556.5794 | 583.9425 | 669.2705 | 568.1705
3116.3167 | 707.6169 | 544.9955 | 586.362 | 643.0869 | 556.8096 | 584.018 | 669.2115 | 568.1568
3117.3167 | 706.7606 | 545.1553 | 586.2273 | 646.9126 | 557.6383 | 584.0557 | 669.1128 | 568.1455
3118.3167 | 702.8315 | 544.984 | 584.187 | 643.8025 | 557.4552 | 584.1998 | 669.0268 | 568.137
3119.3167 | 700.6362 | 545.1734 | 581.1367 | 640.5324 | 557.1273 | 584.1833 | 668.9657 | 568.098
3120.3167 | 700.8514 | 545.572 | 580.2457 | 641.455 | 558.458 | 584.0688 | 668.8889 | 568.0753
3121.3167 | 700.7122 | 545.715 | 581.2557 | 642.5838 | 558.6321 | 583.9823 | 668.8141 | 568.0489
3122.3167 | 702.6833 | 546.479 | 583.9873 | 641.6044 | 558.3774 | 584.0533 | 668.747 | 568.0209
3123.3323 | 702.347 | 546.7935 | 583.0907 | 642.8793 | 558.5997 | 584.1777 | 668.6717 | 568.0084
3124.3167 | 703.9529 | 546.947 | 581.6905 | 643.3564 | 559.8281 | 584.2005 | 668.6297 | 567.9788
3125.3167 | 706.3824 | 547.3244 | 585.0389 | 644.5727 | 560.5927 | 584.1782 | 668.5677 | 567.9608
3126.3167 | 712.9407 | 547.427 | 584.2192 | 644.8189 | 560.2283 | 584.1713 | 668.5057 | 567.9326
3127.3167 | 715.2884 | 547.4789 | 582.5088 | 644.8139 | 559.4678 | 584.2714 | 668.4619 | 567.9257
3128.3167 | 715.792 | 547.9249 | 581.4356 | 645.6882 | 558.3239 | 584.3857 | 668.4301 | 567.9092
3129.3167 | 713.4336 | 548.0465 | 580.4386 | 644.3439 | 557.9208 | 584.4906 | 668.3535 | 567.8779
3130.3167 | 715.3563 | 548.359 | 579.282 | 641.9042 | 559.3353 | 584.4391 | 668.2741 | 567.8441
3131.3167 | 717.605 | 548.2906 | 577.4801 | 639.8664 | 560.4938 | 584.5799 | 668.2098 | 567.8366
3132.3167 | 722.1471 | 548.3855 | 576.535 | 638.8095 | 562.1578 | 584.491 | 668.0862 | 567.833
3133.3167 | 718.3994 | 548.6385 | 574.9649 | 635.9087 | 563.3754 | 584.5552 | 667.9076 | 567.8188
3134.3167 | 717.8538 | 548.9852 | 577.4133 | 635.2432 | 563.2848 | 584.4914 | 667.7979 | 567.7947
3135.3167 | 717.3372 | 549.4294 | 577.4498 | 635.8361 | 564.2986 | 584.4712 | 667.6498 | 567.7803
3136.3167 | 717.6109 | 549.7669 | 577.2769 | 637.8596 | 564.2246 | 584.3976 | 667.5239 | 567.7851
3137.3167 | 716.9506 | 549.8352 | 577.0543 | 637.7928 | 563.8164 | 584.4408 | 667.3961 | 567.7539
3138.3167 | 715.3539 | 550.0876 | 576.5682 | 637.1835 | 564.1328 | 584.564 | 667.2616 | 567.7631
3139.3167 | 719.1414 | 550.515 | 577.8433 | 638.1376 | 565.9607 | 584.341 | 667.1646 | 567.7398
3140.3167 | 719.2763 | 550.6128 | 578.2977 | 634.6915 | 565.2453 | 584.5534 | 667.1134 | 567.7824
3141.3167 | 723.3987 | 550.7772 | 579.1329 | 634.2049 | 563.4444 | 584.5811 | 667.0282 | 567.7617
3142.3167 | 724.6328 | 550.8684 | 579.8287 | 635.4891 | 562.198 | 584.6735 | 666.9247 | 567.7423
3143.3167 | 723.096 | 550.9528 | 580.8224 | 636.3904 | 562.2421 | 584.6599 | 666.8401 | 567.7249
3144.3167 | 719.7217 | 551.2202 | 580.5038 | 635.2425 | 560.8059 | 584.7996 | 666.7309 | 567.7183
3145.3167 | 718.1856 | 551.2205 | 580.4464 | 634.5087 | 558.7304 | 584.8291 | 666.6103 | 567.6848
3146.3167 | 718.0174 | 551.4218 | 581.198 | 634.7933 | 557.6019 | 584.9419 | 666.4227 | 567.6584
3147.3167 | 715.4409 | 551.8325 | 582.3141 | 640.3928 | 557.9174 | 584.9307 | 666.2911 | 567.621
3148.3167 | 715.6151 | 552.199 | 581.0332 | 640.3435 | 557.7978 | 584.8999 | 666.1386 | 567.614
3149.3167 | 716.4566 | 552.7642 | 582.5438 | 640.1216 | 558.8159 | 585.0083 | 665.9897 | 567.5989
3150.3167 | 712.1167 | 552.96 | 581.8027 | 637.7426 | 558.1075 | 585.0757 | 665.8588 | 567.5957
3151.3167 | 710.9592 | 553.2673 | 582.6713 | 640.488 | 558.002 | 584.9481 | 665.724 | 567.562
3152.3167 | 714.3594 | 553.67 | 584.9204 | 643.228 | 559.8783 | 584.9475 | 665.6178 | 567.554
3153.3167 | 717.9834 | 553.8465 | 585.3084 | 643.3801 | 559.5412 | 585.0518 | 665.5376 | 567.5476
3154.3167 | 719.5274 | 553.6673 | 585.7773 | 643.3623 | 558.1101 | 585.1316 | 665.4609 | 567.5519
3155.3167 | 719.7101 | 553.9074 | 585.4027 | 640.9462 | 557.2544 | 585.2248 | 665.3837 | 567.5144
3156.3167 | 719.3984 | 554.0319 | 586.1698 | 640.8944 | 557.018 | 585.275 | 665.2916 | 567.505
3157.3167 | 720.6297 | 554.1129 | 585.4106 | 642.2219 | 556.327 | 585.3133 | 665.1772 | 567.4841
3158.3167 | 724.2382 | 554.4607 | 585.238 | 644.18 | 555.521 | 585.3982 | 665.1378 | 567.4808
3159.3167 | 724.5613 | 554.685 | 583.9082 | 642.8002 | 554.8313 | 585.608 | 665.0899 | 567.465
3160.3167 | 719.5211 | 554.8687 | 580.9269 | 640.668 | 555.0279 | 585.7908 | 665.0097 | 567.4591
3161.3167 | 716.03 | 555.0644 | 577.6796 | 639.4353 | 554.4584 | 585.7931 | 664.9335 | 567.4451
3162.3167 | 714.9135 | 555.302 | 575.7121 | 637.4042 | 554.1305 | 585.7286 | 664.8072 | 567.4371
3163.3167 | 714.8513 | 555.6065 | 575.1181 | 634.4024 | 555.324 | 585.7856 | 664.6851 | 567.4312
3164.3167 | 711.2091 | 555.8385 | 575.0206 | 632.8852 | 556.0221 | 585.7538 | 664.531 | 567.4166
3165.3167 | 710.3665 | 556.0233 | 576.439 | 635.0384 | 556.5306 | 585.682 | 664.3811 | 567.408
3166.3167 | 709.2702 | 556.1325 | 576.082 | 634.9872 | 557.7468 | 585.6215 | 664.2272 | 567.3986
3167.3167 | 708.172 | 556.4722 | 575.715 | 635.5956 | 558.4356 | 585.5863 | 664.0933 | 567.3775
3168.3167 | 709.5149 | 556.542 | 578.3125 | 635.4113 | 560.6095 | 585.638 | 663.9647 | 567.3735
3169.3167 | 707.1686 | 556.7212 | 577.2685 | 632.2788 | 561.0292 | 585.741 | 663.8745 | 567.3783
3170.3167 | 704.9527 | 557.0083 | 575.054 | 631.1168 | 560.3244 | 585.7094 | 663.7415 | 567.3754
3171.3167 | 705.6506 | 557.1109 | 573.8987 | 629.3954 | 561.9332 | 585.6992 | 663.6064 | 567.3544
3172.3167 | 708.4531 | 557.2202 | 573.615 | 628.1115 | 563.1679 | 585.6717 | 663.4449 | 567.3503
3173.3167 | 706.9176 | 557.4733 | 571.8931 | 626.0531 | 563.7393 | 585.6286 | 663.3486 | 567.3614
3174.3167 | 706.4446 | 557.6582 | 574.3951 | 628.5701 | 563.7499 | 585.5113 | 663.2237 | 567.3485
3175.3167 | 705.8715 | 558.0802 | 573.4375 | 627.8326 | 562.8018 | 585.5426 | 663.0997 | 567.3469
3176.3167 | 705.7538 | 558.2081 | 571.8509 | 628.0685 | 563.1917 | 585.5251 | 662.976 | 567.3566
3177.3167 | 707.8058 | 558.4429 | 570.5711 | 627.6972 | 563.2566 | 585.4662 | 662.861 | 567.3392
3178.3167 | 711.4603 | 558.6212 | 569.9002 | 629.1175 | 565.5514 | 585.4094 | 662.7588 | 567.3257
3179.3167 | 715.3016 | 558.8027 | 567.9162 | 630.465 | 566.0549 | 585.3783 | 662.6471 | 567.3291
3180.3167 | 714.6328 | 558.9433 | 566.3618 | 629.1603 | 565.1502 | 585.3116 | 662.5172 | 567.3425
3181.3167 | 715.1331 | 559.1615 | 568.2755 | 629.224 | 563.658 | 585.1518 | 662.3653 | 567.3311
3182.3167 | 717.4205 | 559.6303 | 572.3999 | 629.6847 | 561.3889 | 585.1258 | 662.2645 | 567.3207
3183.3167 | 719.0955 | 559.5366 | 575.7988 | 628.9778 | 558.7266 | 585.1859 | 662.2323 | 567.3177
3184.3167 | 722.4974 | 559.8893 | 576.9292 | 629.5132 | 556.5488 | 585.1852 | 662.1141 | 567.306
3185.3167 | 725.8261 | 559.9671 | 579.5219 | 630.4683 | 554.7551 | 585.2942 | 661.957 | 567.3055
3186.3167 | 728.6873 | 560.1256 | 582.3623 | 631.6553 | 553.5943 | 585.3171 | 661.8235 | 567.2776
3187.3167 | 726.1037 | 560.4548 | 584.4559 | 632.4568 | 552.2893 | 585.4974 | 661.6999 | 567.2529
3188.3167 | 725.9684 | 560.8876 | 585.5932 | 634.5912 | 551.9347 | 585.6063 | 661.5472 | 567.2083
3189.3167 | 725.1168 | 561.1025 | 585.7483 | 634.7346 | 550.7607 | 585.7851 | 661.3753 | 567.1954
3190.3167 | 724.4013 | 561.1368 | 587.2588 | 635.8679 | 552.799 | 585.9053 | 661.2233 | 567.1605
3191.3167 | 726.1226 | 561.1315 | 587.7146 | 638.2756 | 554.692 | 585.9613 | 661.1231 | 567.1485
3192.3167 | 729.4016 | 561.5212 | 586.5425 | 637.7197 | 555.2375 | 586.1066 | 661.0401 | 567.1484
3193.3167 | 729.6963 | 561.7486 | 584.5967 | 635.7871 | 554.3694 | 586.3148 | 660.9507 | 567.1476
3194.3167 | 729.1397 | 561.8575 | 583.794 | 634.4652 | 552.7785 | 586.3428 | 660.7932 | 567.1256
3195.3167 | 728.2892 | 561.7103 | 583.1017 | 631.3454 | 551.5765 | 586.5432 | 660.6206 | 567.1364
3196.3167 | 724.8836 | 561.8277 | 580.8989 | 628.7241 | 551.0728 | 586.6591 | 660.4232 | 567.0985
3197.3167 | 725.1159 | 562.0654 | 580.1777 | 629.1354 | 552.5393 | 586.5653 | 660.2701 | 567.064
3198.3167 | 725.5194 | 562.1919 | 581.1081 | 631.4546 | 554.2186 | 586.5118 | 660.1298 | 567.0489
3199.3167 | 726.1256 | 562.5321 | 582.0443 | 634.6696 | 554.4436 | 586.4648 | 659.9867 | 567.02
3200.3167 | 726.9524 | 562.7271 | 581.9937 | 635.8727 | 554.8497 | 586.6467 | 659.8512 | 566.9916
3201.3167 | 727.9246 | 563.0119 | 579.8443 | 636.2856 | 555.9232 | 586.6351 | 659.7352 | 566.9749
3202.3167 | 729.2061 | 563.46 | 578.8671 | 636.9983 | 556.8333 | 586.6779 | 659.6192 | 566.9474
3203.3167 | 726.6601 | 563.9158 | 578.0206 | 635.6276 | 557.0565 | 586.7997 | 659.4978 | 566.9686
3204.3167 | 723.0619 | 563.8988 | 578.1663 | 634.1341 | 557.1104 | 586.7932 | 659.3754 | 566.9567
3205.3167 | 718.2217 | 564.1526 | 578.0052 | 633.0734 | 555.9491 | 586.9041 | 659.2305 | 566.9392
3206.3167 | 716.9228 | 564.1134 | 577.1121 | 634.1125 | 555.5759 | 586.9467 | 659.1257 | 566.9195
3207.3167 | 714.0199 | 564.2718 | 576.4901 | 632.4443 | 556.438 | 586.9784 | 658.9596 | 566.9223
3208.3167 | 711.0143 | 564.5657 | 575.0141 | 630.488 | 558.0963 | 587.0367 | 658.799 | 566.9035
3209.3167 | 710.0754 | 564.7253 | 572.8629 | 628.6694 | 558.9453 | 587.0779 | 658.6615 | 566.8878
3210.3167 | 712.0415 | 565.0491 | 571.5129 | 628.7279 | 561.256 | 586.9891 | 658.5273 | 566.8929
3211.3167 | 717.3872 | 565.2421 | 572.3722 | 633.18 | 563.3561 | 586.8251 | 658.4075 | 566.8744
3212.3167 | 721.0501 | 565.3271 | 571.8036 | 632.4909 | 563.9153 | 586.8128 | 658.3623 | 566.9077
3213.3167 | 724.1125 | 565.5684 | 570.6126 | 632.672 | 564.0124 | 586.7953 | 658.2673 | 566.9344
3214.3167 | 726.1268 | 566.0424 | 569.6092 | 633.9974 | 563.8075 | 586.6738 | 658.1319 | 566.9392
3215.3167 | 728.8698 | 566.2771 | 569.2905 | 632.2846 | 563.1876 | 586.6264 | 658.0033 | 566.9606
3216.3167 | 729.7627 | 566.6766 | 570.5116 | 632.5109 | 561.8225 | 586.5853 | 657.899 | 566.9639
3217.3167 | 730.4197 | 566.9181 | 571.3937 | 631.3761 | 560.5329 | 586.6281 | 657.7916 | 566.9758
3218.3167 | 730.1201 | 566.9492 | 571.9376 | 628.7584 | 558.6725 | 586.6825 | 657.6484 | 566.9625
3219.3167 | 728.6254 | 567.0432 | 571.6886 | 627.3929 | 561.8037 | 586.7213 | 657.4759 | 566.9605
3220.3167 | 724.8078 | 567.1785 | 569.3635 | 626.2478 | 562.9652 | 586.7776 | 657.3349 | 566.978
3221.3167 | 720.4981 | 567.2433 | 568.383 | 625.259 | 563.3542 | 586.7087 | 657.1781 | 566.9869
3222.3167 | 719.0042 | 567.2525 | 567.2028 | 625.4558 | 563.7565 | 586.5777 | 657.0162 | 566.9941
3223.3167 | 720.935 | 567.6854 | 568.4397 | 626.9722 | 564.0999 | 586.5111 | 656.8669 | 567.0157
3224.3167 | 722.3271 | 567.7617 | 569.4184 | 628.0574 | 562.7091 | 586.3346 | 656.6992 | 567.0413
3225.3167 | 724.2935 | 567.8579 | 570.1374 | 629.4869 | 561.1113 | 586.3638 | 656.5519 | 567.0548
3226.3167 | 724.81 | 568.1452 | 569.4063 | 627.6946 | 559.8368 | 586.3998 | 656.4336 | 567.0753
3227.3167 | 726.5142 | 568.523 | 570.0289 | 628.9495 | 560.699 | 586.2613 | 656.2994 | 567.0806
3228.3167 | 727.8319 | 568.7016 | 571.8768 | 630.7401 | 563.6119 | 586.2769 | 656.2015 | 567.1023
3229.3167 | 728.7606 | 568.8117 | 572.6383 | 631.4676 | 565.6535 | 586.1635 | 656.1206 | 567.1213
3230.3167 | 727.4852 | 568.9086 | 573.0043 | 630.6437 | 564.1674 | 586.1935 | 656.0092 | 567.1499
3231.3167 | 728.0472 | 569.0279 | 572.9407 | 631.2828 | 563.2643 | 586.1623 | 655.855 | 567.1591
3232.3167 | 727.4521 | 569.3672 | 575.1006 | 632.2424 | 564.1611 | 586.0072 | 655.7689 | 567.1642
3233.3167 | 726.5658 | 569.8009 | 576.8571 | 633.7286 | 564.5263 | 585.9925 | 655.6437 | 567.1864
3234.3167 | 725.3032 | 570.0286 | 576.3315 | 633.5405 | 564.9109 | 586.1346 | 655.5035 | 567.2216
3235.3167 | 723.6745 | 569.9419 | 575.6364 | 631.533 | 563.2218 | 586.1668 | 655.3706 | 567.2466
3236.3167 | 720.6041 | 570.1695 | 574.802 | 630.2401 | 561.6819 | 586.1855 | 655.2464 | 567.2463
3237.3167 | 717.7356 | 570.2348 | 572.4071 | 628.1887 | 561.0759 | 586.2287 | 655.1232 | 567.2521
3238.3167 | 713.7535 | 570.4822 | 570.0457 | 626.1845 | 560.2343 | 586.1443 | 655.0242 | 567.2689
3239.3167 | 712.81 | 570.709 | 570.701 | 626.4589 | 559.5547 | 586.0945 | 654.8955 | 567.2892
3240.3167 | 712.1643 | 570.8052 | 571.5588 | 626.3722 | 559.4733 | 586.0683 | 654.7544 | 567.314
3241.3167 | 716.7311 | 570.9402 | 572.6855 | 628.8344 | 559.4178 | 586.0788 | 654.6835 | 567.3217
3242.3167 | 720.6936 | 571.2353 | 569.8979 | 627.768 | 560.1865 | 586.1222 | 654.6455 | 567.3489
3243.3167 | 720.8459 | 571.424 | 568.5081 | 627.5831 | 559.7391 | 586.0407 | 654.57 | 567.3707
3244.3167 | 723.5349 | 571.6383 | 569.1587 | 628.3744 | 561.0538 | 585.9173 | 654.4961 | 567.3608
3245.3167 | 728.1396 | 571.9159 | 570.162 | 631.0605 | 561.3594 | 585.732 | 654.4331 | 567.3555
3246.3167 | 726.884 | 572.116 | 573.8848 | 631.891 | 559.4059 | 585.7541 | 654.3826 | 567.378
3247.3167 | 724.2683 | 572.1985 | 574.0669 | 630.6487 | 557.6336 | 585.8042 | 654.3371 | 567.3625
3248.3167 | 723.9277 | 572.4996 | 572.758 | 627.8516 | 555.5942 | 585.9584 | 654.2428 | 567.3672
3249.3167 | 721.0137 | 572.6251 | 571.1772 | 625.2866 | 554.434 | 585.9815 | 654.1643 | 567.348
3250.3167 | 719.0618 | 572.6916 | 570.3818 | 623.2829 | 555.9876 | 585.9896 | 654.0567 | 567.3232
3251.3167 | 721.042 | 572.7722 | 568.8212 | 621.0107 | 558.0369 | 586.0794 | 653.9699 | 567.3377
3252.3167 | 720.1365 | 572.605 | 565.778 | 617.6342 | 559.1902 | 586.1112 | 653.8298 | 567.3556
3253.3167 | 718.725 | 572.4056 | 562.6407 | 614.6634 | 559.6696 | 586.0798 | 653.6742 | 567.3484
3254.3167 | 714.7378 | 572.7826 | 560.01 | 612.3983 | 558.8829 | 585.9373 | 653.535 | 567.3374
3255.3167 | 712.3681 | 572.8146 | 559.4199 | 612.0325 | 557.202 | 585.7744 | 653.3799 | 567.3481
3256.3167 | 710.4123 | 573.2202 | 559.6399 | 612.8038 | 555.894 | 585.6418 | 653.2031 | 567.3415
3257.3167 | 709.344 | 573.4264 | 561.1348 | 614.6556 | 556.6885 | 585.5164 | 653.0321 | 567.3422
3258.3167 | 707.1196 | 573.7346 | 561.2755 | 615.054 | 555.944 | 585.3729 | 652.9135 | 567.3454
3259.3167 | 708.0379 | 573.9819 | 563.4201 | 617.9036 | 555.638 | 585.2065 | 652.7864 | 567.3479
3260.3167 | 708.0257 | 574.4884 | 564.8445 | 617.3378 | 555.8842 | 585.3269 | 652.6699 | 567.3516
3261.3167 | 705.3857 | 574.2684 | 562.8096 | 615.6222 | 554.77 | 585.3562 | 652.5638 | 567.3477
3262.3167 | 705.2756 | 574.1854 | 562.5553 | 615.1935 | 554.2438 | 585.315 | 652.4753 | 567.3265
3263.3167 | 708.2455 | 574.2083 | 563.7242 | 618.7176 | 555.5253 | 585.123 | 652.3863 | 567.2909
3264.3167 | 708.8728 | 574.3207 | 562.8406 | 618.95 | 555.3369 | 585.1452 | 652.2672 | 567.2855
3265.3167 | 707.0317 | 574.2322 | 562.5265 | 618.497 | 556.0504 | 585.0571 | 652.1818 | 567.2671
3266.3167 | 709.5069 | 574.4512 | 564.247 | 619.8857 | 555.8905 | 584.8925 | 652.0876 | 567.2509
3267.3167 | 710.6728 | 574.4233 | 565.9317 | 620.276 | 555.7234 | 584.8809 | 651.9751 | 567.2348
3268.3167 | 711.8274 | 574.5444 | 565.2098 | 619.3744 | 554.8401 | 584.8627 | 651.8264 | 567.2087
3269.3167 | 711.5251 | 574.78 | 565.8221 | 618.4066 | 553.877 | 584.8585 | 651.7059 | 567.203
3270.3167 | 710.4485 | 575.2297 | 566.8439 | 619.9 | 554.2512 | 584.7594 | 651.678 | 567.1834
3271.3167 | 710.6915 | 575.5582 | 567.9368 | 620.4733 | 552.7216 | 584.7217 | 651.5646 | 567.1545
3272.3167 | 710.4074 | 575.7712 | 569.5179 | 620.9518 | 552.6174 | 584.6592 | 651.473 | 567.1404
3273.3167 | 711.781 | 575.7522 | 569.7871 | 620.4841 | 550.8518 | 584.6942 | 651.3703 | 567.1167
3274.3167 | 712.7885 | 575.6783 | 570.7043 | 619.2199 | 548.8241 | 584.6835 | 651.269 | 567.0615
3275.3167 | 716.6756 | 575.6146 | 571.5512 | 618.1452 | 546.8254 | 584.7658 | 651.1558 | 567.013
3276.3167 | 716.0148 | 575.5551 | 571.1944 | 615.0535 | 545.162 | 584.9209 | 651.0377 | 566.9604
3277.3167 | 715.0481 | 575.5513 | 569.5768 | 612.4954 | 543.8767 | 584.959 | 650.8532 | 566.8902
3278.3167 | 712.6748 | 575.5948 | 570.3702 | 612.4364 | 542.7878 | 584.9214 | 650.708 | 566.8135
3279.3167 | 711.8413 | 575.5401 | 572.3259 | 611.8873 | 542.8163 | 584.9305 | 650.5731 | 566.7541
3280.3167 | 714.012 | 575.7188 | 573.5949 | 610.836 | 542.6318 | 584.8709 | 650.4193 | 566.6701
3281.3167 | 717.7949 | 575.9996 | 574.4288 | 614.2629 | 543.0341 | 584.819 | 650.2872 | 566.5927
3282.3167 | 721.1002 | 576.1421 | 573.5331 | 617.0511 | 542.5948 | 585.0104 | 650.1963 | 566.5422
3283.3167 | 722.8792 | 576.2108 | 571.9886 | 616.8343 | 541.7932 | 585.0417 | 650.0954 | 566.4823
3284.3167 | 722.5169 | 576.4159 | 572.0767 | 615.533 | 542.049 | 585.1112 | 649.9556 | 566.4199
3285.3167 | 722.2405 | 576.4758 | 571.429 | 613.906 | 543.7331 | 585.1881 | 649.8272 | 566.3401
3286.3167 | 721.4608 | 576.5253 | 573.984 | 614.2911 | 544.1355 | 585.1756 | 649.71 | 566.2761
3287.3167 | 720.2111 | 576.5383 | 574.0693 | 614.571 | 543.3237 | 585.2905 | 649.5716 | 566.1984
3288.3167 | 718.7107 | 576.5657 | 573.2416 | 613.4406 | 542.6636 | 585.3773 | 649.428 | 566.1181
3289.3167 | 718.5358 | 576.7242 | 573.6025 | 613.8269 | 543.3175 | 585.2654 | 649.2762 | 566.0216
3290.3167 | 715.9461 | 576.8612 | 576.2338 | 615.3599 | 544.5022 | 585.3477 | 649.1434 | 565.9547
3291.3167 | 714.0138 | 576.8073 | 576.1007 | 613.6252 | 543.1754 | 585.5332 | 648.9831 | 565.8806
3292.3167 | 713.8484 | 577.0249 | 575.6832 | 610.7479 | 541.7063 | 585.6185 | 648.8184 | 565.7793
3293.3167 | 714.1424 | 576.7117 | 575.6335 | 610.7761 | 542.1881 | 585.6547 | 648.6603 | 565.6817
3294.3167 | 714.0969 | 576.6446 | 574.9547 | 610.655 | 542.8475 | 585.74 | 648.5013 | 565.6098
3295.3167 | 714.1532 | 577.1464 | 575.4437 | 612.9903 | 543.7647 | 585.7497 | 648.3634 | 565.5279
3296.3167 | 713.5088 | 577.5075 | 577.7642 | 614.9995 | 545.0279 | 585.7168 | 648.2302 | 565.4353
3297.3167 | 715.6617 | 577.5212 | 578.1978 | 617.8976 | 543.3775 | 585.8132 | 648.112 | 565.3711
3298.3167 | 718.8976 | 577.7197 | 577.0447 | 616.8676 | 542.0973 | 585.9329 | 647.9898 | 565.2682
3299.3167 | 718.5042 | 577.9925 | 575.636 | 616.1355 | 543.2816 | 586.0755 | 647.859 | 565.1942
3300.3167 | 719.9213 | 578.5247 | 576.7942 | 620.6291 | 546.4614 | 585.8963 | 647.7484 | 565.111
3301.3167 | 861.0705 | 578.8955 | 578.3597 | 621.3512 | 549.4722 | 586.0109 | 647.6121 | 565.0432