## Test Conditions
DESIREE-FIRE Test Number 47 - Circuit Simulator Data Only
Test Date: | 2009-10-08
DCSim DAQ Start Time | 8:08
DCSim Time for Synchronization | 8:32
Heat Source Synchronization | 16:03 | minutes:seconds
Heat Source DAQ Start Time | 8:16
Fire Time | 8:34
Offset | 0:26 | minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 1560 | seconds
Heat Source Offset | 0:18 | minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 1053 | seconds
Heat Source Stop Time | 10:58
Test Duration | 2:24 | minutes:seconds
| 8640 | seconds
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit number | Cable Type |  | Cable TC channel | Air TC Channel
PE/PVC, 7c, 12AWG
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds.
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | Int-Cab_VT7-T1 | Int-Cab_VT7-T2 | Int-Cab_VT7-T3 | Int-Cab_VT7-T4 | Int-Cab_VT7-T5 | Int-Cab_VT7-T6 | Int-Cab_VT7-T7 | Int-Cab_VTU-S1+a | Int-Cab_VTU-S1+b | Int-Cab_VTU-S2+a | Int-Cab_VTU-S2+b | Int-Cab_VTU-S1-a | Int-Cab_VTU-S1-b | Int-Cab_VTU-S2-a | Int-Cab_VTU-S2-b | T1-V(Batt -) | T2 -V(Batt -) | T3 - V(Batt -) | T4 - V(Batt -) | T5 - V(Batt -) | T6 - V(Batt -) | T7 - V(Batt -) | {S1+a} - V(Batt - ) | {S1+b} - V(Batt - ) | {S2+a} - V(Batt - ) | {S2+b} - V(Batt - ) | {S1-a} - V(Batt -) | {S1-b} - V(Batt - ) | {S2-a} - V(Batt - ) | {S2-b} - V(Batt - ) | {S1+a} - {S1-a} | {S1+a} - {S2-a} | {S2+a} - {S1-a} | {S2+a} - {S2-a}
-0.9375 | 123.2941 | -61.4685 | 61.6104 | 0.025705 | -0.0451 | -0.012 | -0.01586 | 0.008797 | -0.005985 | 0.005955 | 61.5005 | 0.12958 | 61.4363 | -0.092628 | 0.002454 | 61.5524 | -0.038063 | 61.5183 | 61.4942 | 61.4234 | 61.4565 | 61.4526 | 61.4773 | 61.4625 | 61.4745 | 122.969 | 61.5981 | 122.9048 | 61.3759 | 61.471 | 123.0209 | 61.4304 | 122.9868 | 61.498 | 61.5385 | 61.4339 | 61.4744
0.125 | 123.3536 | -61.441 | 61.5738 | 0.025705 | -0.035942 | -0.016578 | -0.01586 | 0.017953 | -0.010563 | 0.015112 | 61.5005 | 0.12958 | 61.4455 | -0.088049 | 0.007032 | 61.5524 | -0.028906 | 61.2894 | 61.4667 | 61.4051 | 61.4245 | 61.4252 | 61.459 | 61.4305 | 61.4562 | 122.9415 | 61.5706 | 122.8865 | 61.353 | 61.4481 | 122.9935 | 61.4121 | 122.7305 | 61.4934 | 61.5294 | 61.4384 | 61.4744
1.0625 | 123.3627 | -61.4456 | 61.5646 | 0.025705 | -0.035942 | -0.012 | -0.011281 | 0.013375 | -0.005985 | 0.010533 | 61.505 | 0.12958 | 61.4409 | -0.11552 | -0.006702 | 61.5616 | -0.028906 | 61.2894 | 61.4713 | 61.4097 | 61.4336 | 61.4343 | 61.459 | 61.4396 | 61.4562 | 122.9507 | 61.5752 | 122.8865 | 61.3301 | 61.4389 | 123.0072 | 61.4167 | 122.735 | 61.5118 | 61.534 | 61.4476 | 61.4698
2.125 | 123.3307 | -61.4639 | 61.5692 | 0.021127 | -0.035942 | -0.012 | -0.01586 | 0.008797 | -0.010563 | 0.015112 | 61.5005 | 0.12501 | 61.4363 | -0.10637 | 0.002454 | 61.5524 | -0.04722 | 61.2894 | 61.4851 | 61.428 | 61.4519 | 61.4481 | 61.4727 | 61.4534 | 61.479 | 122.9644 | 61.5889 | 122.9002 | 61.3576 | 61.4664 | 123.0164 | 61.4167 | 122.7533 | 61.498 | 61.5477 | 61.4339 | 61.4835
3.0625 | 123.3444 | -61.4685 | 61.5463 | 0.021127 | -0.049678 | -0.021157 | -0.01586 | 0.013375 | -0.005985 | 0.010533 | 61.4959 | 0.12043 | 61.4455 | -0.097207 | 0.002454 | 61.557 | -0.042641 | 61.2848 | 61.4896 | 61.4188 | 61.4473 | 61.4526 | 61.4819 | 61.4625 | 61.479 | 122.9644 | 61.5889 | 122.914 | 61.3713 | 61.471 | 123.0255 | 61.4259 | 122.7533 | 61.4934 | 61.5385 | 61.443 | 61.4881
4.0625 | 123.3032 | -61.4777 | 61.5509 | 0.025705 | -0.035942 | -0.021157 | -0.01586 | 0.017953 | -0.005985 | 0.005955 | 61.4959 | 0.12501 | 61.45 | -0.10637 | 0.002454 | 61.5616 | -0.04722 | 61.2848 | 61.5034 | 61.4417 | 61.4565 | 61.4618 | 61.4956 | 61.4717 | 61.4836 | 122.9736 | 61.6027 | 122.9277 | 61.3713 | 61.4801 | 123.0392 | 61.4304 | 122.7625 | 61.4934 | 61.5431 | 61.4476 | 61.4973
5.125 | 123.2941 | -61.4639 | 61.5646 | 0.025705 | -0.035942 | -0.021157 | -0.006703 | 0.022531 | -0.010563 | 0.001377 | 61.5005 | 0.12958 | 61.4409 | -0.10637 | -0.002124 | 61.5478 | -0.042641 | 61.2894 | 61.4896 | 61.428 | 61.4428 | 61.4572 | 61.4865 | 61.4534 | 61.4653 | 122.9644 | 61.5935 | 122.9048 | 61.3576 | 61.4618 | 123.0118 | 61.4213 | 122.7533 | 61.5026 | 61.5431 | 61.443 | 61.4835
6.0625 | 123.3719 | -61.4548 | 61.5555 | 0.021127 | -0.035942 | -0.016578 | -0.01586 | 0.022531 | -0.005985 | 0.010533 | 61.5096 | 0.12501 | 61.4455 | -0.10637 | 0.002454 | 61.557 | -0.04722 | 61.2894 | 61.4759 | 61.4188 | 61.4382 | 61.4389 | 61.4773 | 61.4488 | 61.4653 | 122.9644 | 61.5798 | 122.9002 | 61.3484 | 61.4572 | 123.0118 | 61.4076 | 122.7442 | 61.5072 | 61.5568 | 61.443 | 61.4927
7.0625 | 123.3444 | -61.4685 | 61.5463 | 0.025705 | -0.0451 | -0.012 | -0.011281 | 0.022531 | -0.005985 | 0.005955 | 61.5005 | 0.12501 | 61.45 | -0.10179 | -0.006702 | 61.5524 | -0.042641 | 61.2894 | 61.4942 | 61.4234 | 61.4565 | 61.4572 | 61.491 | 61.4625 | 61.4745 | 122.969 | 61.5935 | 122.9185 | 61.3667 | 61.4618 | 123.0209 | 61.4259 | 122.7579 | 61.5072 | 61.5431 | 61.4567 | 61.4927
8.125 | 123.3307 | -61.4365 | 61.5646 | 0.021127 | -0.040521 | -0.016578 | -0.011281 | 0.013375 | -0.005985 | 0.010533 | 61.505 | 0.12958 | 61.4409 | -0.11094 | 0.007032 | 61.5524 | -0.042641 | 61.2894 | 61.4576 | 61.3959 | 61.4199 | 61.4252 | 61.4498 | 61.4305 | 61.447 | 122.9415 | 61.566 | 122.8773 | 61.3255 | 61.4435 | 122.9889 | 61.3938 | 122.7259 | 61.498 | 61.5477 | 61.4339 | 61.4835
9.0625 | 123.2437 | -61.4822 | 61.6058 | 0.016548 | -0.035942 | -0.007421 | -0.011281 | 0.013375 | -0.005985 | 0.010533 | 61.4959 | 0.12958 | 61.3905 | -0.10637 | 0.002454 | 61.5524 | -0.042641 | 61.294 | 61.4988 | 61.4463 | 61.4748 | 61.471 | 61.4956 | 61.4763 | 61.4928 | 122.9781 | 61.6118 | 122.8728 | 61.3759 | 61.4847 | 123.0347 | 61.4396 | 122.7762 | 61.4934 | 61.5385 | 61.3881 | 61.4332
10.125 | 123.3261 | -61.4868 | 61.5555 | 0.021127 | -0.035942 | -0.016578 | -0.011281 | 0.013375 | -0.005985 | 0.005955 | 61.5005 | 0.13416 | 61.3722 | -0.10637 | -0.006702 | 61.5616 | -0.04722 | 61.294 | 61.5079 | 61.4509 | 61.4702 | 61.4755 | 61.5002 | 61.4808 | 61.4928 | 122.9873 | 61.621 | 122.859 | 61.3805 | 61.4801 | 123.0484 | 61.4396 | 122.7808 | 61.5072 | 61.5477 | 61.3789 | 61.4194
11.0625 | 123.381 | -61.4136 | 61.5967 | 0.016548 | -0.035942 | -0.016578 | -0.01586 | 0.013375 | -0.005985 | 0.010533 | 61.505 | 0.12958 | 61.3722 | -0.11094 | 0.002454 | 61.557 | -0.042641 | 61.2986 | 61.4301 | 61.3776 | 61.397 | 61.3977 | 61.4269 | 61.4076 | 61.4241 | 122.9186 | 61.5432 | 122.7858 | 61.3026 | 61.416 | 122.9706 | 61.3709 | 122.7121 | 61.5026 | 61.5477 | 61.3698 | 61.4149
12.125 | 123.2437 | -61.4914 | 61.6013 | 0.025705 | -0.040521 | -0.016578 | -0.006703 | 0.013375 | -0.005985 | 0.010533 | 61.5005 | 0.12501 | 61.4088 | -0.10179 | 0.002454 | 61.557 | -0.051798 | 61.2803 | 61.5171 | 61.4509 | 61.4748 | 61.4847 | 61.5048 | 61.4854 | 61.5019 | 122.9919 | 61.6164 | 122.9002 | 61.3896 | 61.4938 | 123.0484 | 61.4396 | 122.7716 | 61.498 | 61.5523 | 61.4064 | 61.4606
13.0625 | 123.2346 | -61.4639 | 61.6013 | 0.021127 | -0.031363 | -0.016578 | -0.006703 | 0.013375 | -0.001406 | 0.005955 | 61.505 | 0.13874 | 61.4409 | -0.11094 | -0.011281 | 61.5433 | -0.04722 | 61.294 | 61.4851 | 61.4326 | 61.4474 | 61.4572 | 61.4773 | 61.4625 | 61.4699 | 122.969 | 61.6027 | 122.9048 | 61.353 | 61.4526 | 123.0072 | 61.4167 | 122.7579 | 61.5163 | 61.5523 | 61.4522 | 61.4881
14.1406 | 123.3398 | -61.4227 | 61.5784 | 0.021127 | -0.0451 | -0.012 | -0.011281 | 0.008797 | -0.005985 | 0.005955 | 61.505 | 0.12501 | 61.4363 | -0.11094 | 0.01161 | 61.5524 | -0.042641 | 61.294 | 61.4439 | 61.3776 | 61.4107 | 61.4114 | 61.4315 | 61.4167 | 61.4287 | 122.9278 | 61.5477 | 122.859 | 61.3118 | 61.4343 | 122.9752 | 61.3801 | 122.7167 | 61.4934 | 61.5477 | 61.4247 | 61.4789
15.0625 | 123.2758 | -61.4868 | 61.6013 | 0.025705 | -0.035942 | -0.007421 | -0.011281 | 0.017953 | -0.010563 | 0.005955 | 61.5005 | 0.12958 | 61.4409 | -0.10637 | 0.007032 | 61.5616 | -0.042641 | 61.2986 | 61.5125 | 61.4509 | 61.4794 | 61.4755 | 61.5048 | 61.4763 | 61.4928 | 122.9873 | 61.6164 | 122.9277 | 61.3805 | 61.4938 | 123.0484 | 61.4442 | 122.7854 | 61.4934 | 61.5431 | 61.4339 | 61.4835
16.125 | 123.3582 | -61.4502 | 61.5875 | 0.016548 | -0.040521 | -0.012 | -0.01586 | 0.008797 | -0.010563 | 0.005955 | 61.5005 | 0.13416 | 61.4409 | -0.11094 | 0.002454 | 61.5616 | -0.042641 | 61.294 | 61.4667 | 61.4097 | 61.4382 | 61.4343 | 61.459 | 61.4396 | 61.4562 | 122.9507 | 61.5844 | 122.8911 | 61.3393 | 61.4526 | 123.0118 | 61.4076 | 122.7442 | 61.498 | 61.5431 | 61.4384 | 61.4835
17.0625 | 123.3124 | -61.4502 | 61.5738 | 0.021127 | -0.040521 | -0.012 | -0.01586 | 0.013375 | -0.01972 | 0.005955 | 61.505 | 0.12501 | 61.4043 | -0.10637 | 0.002454 | 61.5524 | -0.04722 | 61.2894 | 61.4713 | 61.4097 | 61.4382 | 61.4343 | 61.4636 | 61.4305 | 61.4562 | 122.9552 | 61.5752 | 122.8545 | 61.3438 | 61.4526 | 123.0026 | 61.403 | 122.7396 | 61.5026 | 61.5523 | 61.4018 | 61.4515
18.125 | 123.2849 | -61.4548 | 61.5738 | 0.025705 | -0.040521 | -0.016578 | -0.01586 | 0.017953 | -0.010563 | 0.005955 | 61.5005 | 0.12958 | 61.3722 | -0.11094 | 0.002454 | 61.5524 | -0.051798 | 61.294 | 61.4805 | 61.4143 | 61.4382 | 61.4389 | 61.4727 | 61.4442 | 61.4607 | 122.9552 | 61.5844 | 122.827 | 61.3438 | 61.4572 | 123.0072 | 61.403 | 122.7488 | 61.498 | 61.5523 | 61.3698 | 61.424
19.0625 | 123.3078 | -61.4731 | 61.5967 | 0.021127 | -0.040521 | -0.016578 | -0.011281 | 0.013375 | -0.001406 | 0.005955 | 61.505 | 0.12501 | 61.3768 | -0.11094 | -0.002124 | 61.557 | -0.033484 | 61.2986 | 61.4942 | 61.4326 | 61.4565 | 61.4618 | 61.4865 | 61.4717 | 61.479 | 122.9781 | 61.5981 | 122.8499 | 61.3621 | 61.471 | 123.0301 | 61.4396 | 122.7717 | 61.5072 | 61.5385 | 61.3789 | 61.4103
20.125 | 123.2254 | -61.5097 | 61.5829 | 0.025705 | -0.031363 | -0.021157 | -0.011281 | 0.022531 | -0.010563 | 0.015112 | 61.5005 | 0.13416 | 61.4226 | -0.10637 | 0.007032 | 61.5616 | -0.038063 | 61.2894 | 61.5354 | 61.4783 | 61.4885 | 61.4984 | 61.5322 | 61.4991 | 61.5248 | 123.0102 | 61.6439 | 122.9323 | 61.4033 | 61.5167 | 123.0713 | 61.4716 | 122.7991 | 61.4934 | 61.5385 | 61.4155 | 61.4606
21.0625 | 123.3765 | -61.4594 | 61.5555 | 0.025705 | -0.040521 | -0.012 | -0.011281 | 0.013375 | -0.005985 | 0.005955 | 61.505 | 0.12501 | 61.4363 | -0.10637 | 0.002454 | 61.557 | -0.042641 | 61.294 | 61.4851 | 61.4188 | 61.4474 | 61.4481 | 61.4727 | 61.4534 | 61.4653 | 122.9644 | 61.5844 | 122.8957 | 61.353 | 61.4618 | 123.0164 | 61.4167 | 122.7533 | 61.5026 | 61.5477 | 61.4339 | 61.4789
22.125 | 123.2986 | -61.4639 | 61.5555 | 0.016548 | -0.040521 | -0.012 | -0.006703 | 0.022531 | -0.001406 | 0.010533 | 61.5096 | 0.13416 | 61.4546 | -0.11094 | -0.002124 | 61.5662 | -0.038063 | 61.294 | 61.4805 | 61.4234 | 61.4519 | 61.4572 | 61.4865 | 61.4625 | 61.4745 | 122.9736 | 61.5981 | 122.9185 | 61.353 | 61.4618 | 123.0301 | 61.4259 | 122.7579 | 61.5118 | 61.5477 | 61.4567 | 61.4927
23.0625 | 123.2849 | -61.4777 | 61.5738 | 0.021127 | -0.035942 | -0.012 | -0.011281 | 0.008797 | -0.001406 | 0.005955 | 61.5005 | 0.12958 | 61.4409 | -0.11094 | 0.007032 | 61.5524 | -0.042641 | 61.2848 | 61.4988 | 61.4417 | 61.4657 | 61.4664 | 61.4865 | 61.4763 | 61.4836 | 122.9781 | 61.6072 | 122.9185 | 61.3667 | 61.4847 | 123.0301 | 61.435 | 122.7625 | 61.4934 | 61.5431 | 61.4339 | 61.4835
24.1406 | 123.3536 | -61.4319 | 61.5692 | 0.016548 | -0.040521 | -0.012 | -0.006703 | 0.013375 | -0.005985 | 0.005955 | 61.5142 | 0.12958 | 61.45 | -0.10637 | 0.002454 | 61.557 | -0.038063 | 61.2986 | 61.4484 | 61.3914 | 61.4199 | 61.4252 | 61.4453 | 61.4259 | 61.4378 | 122.9461 | 61.5615 | 122.8819 | 61.3255 | 61.4343 | 122.9889 | 61.3938 | 122.7305 | 61.5118 | 61.5523 | 61.4476 | 61.4881
25.0625 | 123.2391 | -61.4914 | 61.6013 | 0.034862 | -0.035942 | -0.007421 | -0.011281 | 0.013375 | -0.005985 | 0.015112 | 61.5096 | 0.13416 | 61.4455 | -0.11094 | 0.002454 | 61.5524 | -0.04722 | 61.2894 | 61.5263 | 61.4555 | 61.484 | 61.4801 | 61.5048 | 61.4854 | 61.5065 | 123.001 | 61.6256 | 122.9369 | 61.3804 | 61.4938 | 123.0438 | 61.4442 | 122.7808 | 61.5072 | 61.5568 | 61.443 | 61.4927
26.125 | 123.3444 | -61.4594 | 61.5829 | 0.025705 | -0.035942 | -0.016578 | -0.01586 | 0.013375 | -0.015142 | 0.005955 | 61.505 | 0.12958 | 61.3905 | -0.10179 | 0.002454 | 61.5524 | -0.042641 | 61.2894 | 61.4851 | 61.4234 | 61.4428 | 61.4435 | 61.4727 | 61.4442 | 61.4653 | 122.9644 | 61.5889 | 122.8499 | 61.3576 | 61.4618 | 123.0118 | 61.4167 | 122.7488 | 61.5026 | 61.5477 | 61.3881 | 61.4332
27.0625 | 123.3627 | -61.4639 | 61.5555 | 0.025705 | -0.035942 | -0.016578 | -0.011281 | 0.017953 | -0.010563 | 0.010533 | 61.4959 | 0.12958 | 61.3722 | -0.11094 | 0.002454 | 61.557 | -0.042641 | 61.2894 | 61.4896 | 61.428 | 61.4474 | 61.4526 | 61.4819 | 61.4534 | 61.4745 | 122.9598 | 61.5935 | 122.8361 | 61.353 | 61.4664 | 123.0209 | 61.4213 | 122.7533 | 61.4934 | 61.5385 | 61.3698 | 61.4149
28.125 | 123.349 | -61.4502 | 61.5601 | 0.025705 | -0.040521 | -0.016578 | -0.011281 | 0.017953 | -0.010563 | 0.010533 | 61.505 | 0.13416 | 61.418 | -0.10637 | 0.002454 | 61.5616 | -0.04722 | 61.294 | 61.4759 | 61.4097 | 61.4336 | 61.4389 | 61.4681 | 61.4396 | 61.4607 | 122.9552 | 61.5844 | 122.8682 | 61.3438 | 61.4526 | 123.0118 | 61.403 | 122.7442 | 61.5026 | 61.5523 | 61.4155 | 61.4652
29.0625 | 123.3032 | -61.4868 | 61.5829 | 0.025705 | -0.035942 | -0.012 | -0.011281 | 0.017953 | -0.005985 | 0.010533 | 61.505 | 0.12043 | 61.45 | -0.10637 | -0.002124 | 61.557 | -0.042641 | 61.2986 | 61.5125 | 61.4509 | 61.4748 | 61.4755 | 61.5048 | 61.4808 | 61.4973 | 122.9919 | 61.6072 | 122.9369 | 61.3805 | 61.4847 | 123.0438 | 61.4442 | 122.7854 | 61.5072 | 61.5477 | 61.4522 | 61.4927
30.125 | 123.2986 | -61.4914 | 61.5784 | 0.016548 | -0.035942 | -0.016578 | -0.011281 | 0.017953 | -0.010563 | 0.010533 | 61.5096 | 0.12501 | 61.45 | -0.11552 | -0.002124 | 61.557 | -0.042641 | 61.294 | 61.5079 | 61.4555 | 61.4748 | 61.4801 | 61.5093 | 61.4808 | 61.5019 | 123.001 | 61.6164 | 122.9414 | 61.3759 | 61.4893 | 123.0484 | 61.4488 | 122.7854 | 61.5118 | 61.5523 | 61.4522 | 61.4927
31.0625 | 123.3353 | -61.441 | 61.5646 | 0.025705 | -0.031363 | -0.016578 | -0.011281 | 0.017953 | -0.001406 | 0.010533 | 61.505 | 0.12501 | 61.4409 | -0.10637 | -0.006702 | 61.557 | -0.042641 | 61.294 | 61.4667 | 61.4097 | 61.4245 | 61.4298 | 61.459 | 61.4396 | 61.4516 | 122.9461 | 61.566 | 122.8819 | 61.3347 | 61.4343 | 122.998 | 61.3984 | 122.735 | 61.5118 | 61.5477 | 61.4476 | 61.4835
32.0625 | 123.2208 | -61.496 | 61.5784 | 0.025705 | -0.040521 | -0.012 | -0.011281 | 0.017953 | -0.001406 | 0.015112 | 61.5142 | 0.12501 | 61.4363 | -0.10637 | 0.002454 | 61.557 | -0.038063 | 61.2894 | 61.5217 | 61.4555 | 61.484 | 61.4847 | 61.5139 | 61.4946 | 61.5111 | 123.0102 | 61.621 | 122.9323 | 61.3896 | 61.4984 | 123.053 | 61.4579 | 122.7854 | 61.5118 | 61.5523 | 61.4339 | 61.4744
33.125 | 123.3627 | -61.4456 | 61.5646 | 0.025705 | -0.031363 | -0.016578 | -0.01586 | 0.017953 | -0.010563 | 0.005955 | 61.505 | 0.12958 | 61.4409 | -0.10637 | 0.007032 | 61.557 | -0.051798 | 61.2986 | 61.4713 | 61.4143 | 61.429 | 61.4298 | 61.4636 | 61.4351 | 61.4516 | 122.9507 | 61.5752 | 122.8865 | 61.3393 | 61.4527 | 123.0026 | 61.3938 | 122.7442 | 61.498 | 61.5568 | 61.4339 | 61.4927
34.0625 | 123.3124 | -61.4822 | 61.5509 | 0.030283 | -0.035942 | -0.016578 | -0.011281 | 0.008797 | -0.005985 | 0.010533 | 61.4959 | 0.13416 | 61.3814 | -0.11094 | -0.002124 | 61.557 | -0.038063 | 61.294 | 61.5125 | 61.4463 | 61.4657 | 61.471 | 61.491 | 61.4763 | 61.4928 | 122.9781 | 61.6164 | 122.8636 | 61.3713 | 61.4801 | 123.0392 | 61.4442 | 122.7762 | 61.498 | 61.534 | 61.3835 | 61.4194
35.0625 | 123.3215 | -61.4594 | 61.5692 | 0.030283 | -0.040521 | -0.021157 | -0.011281 | 0.017953 | -0.005985 | 0.005955 | 61.4959 | 0.12043 | 61.3859 | -0.10179 | -0.006702 | 61.557 | -0.04722 | 61.294 | 61.4896 | 61.4188 | 61.4382 | 61.4481 | 61.4773 | 61.4534 | 61.4653 | 122.9552 | 61.5798 | 122.8453 | 61.3576 | 61.4526 | 123.0164 | 61.4121 | 122.7533 | 61.5026 | 61.5431 | 61.3926 | 61.4332
36.125 | 123.3719 | -61.4594 | 61.5875 | 0.025705 | -0.040521 | -0.012 | -0.011281 | 0.022531 | 0.003172 | 0.010533 | 61.505 | 0.12958 | 61.418 | -0.11094 | -0.002124 | 61.5524 | -0.033484 | 61.2986 | 61.4851 | 61.4188 | 61.4474 | 61.4481 | 61.4819 | 61.4625 | 61.4699 | 122.9644 | 61.5889 | 122.8773 | 61.3484 | 61.4572 | 123.0118 | 61.4259 | 122.7579 | 61.5072 | 61.5385 | 61.4201 | 61.4515
37.0625 | 123.23 | -61.5005 | 61.6196 | 0.016548 | -0.040521 | -0.012 | -0.006703 | 0.013375 | -0.005985 | 0.010533 | 61.5005 | 0.13416 | 61.4409 | -0.10179 | -0.002124 | 61.557 | -0.038063 | 61.2894 | 61.5171 | 61.46 | 61.4885 | 61.4938 | 61.5139 | 61.4946 | 61.5111 | 123.001 | 61.6347 | 122.9414 | 61.3988 | 61.4984 | 123.0576 | 61.4625 | 122.79 | 61.5026 | 61.5385 | 61.443 | 61.4789
38.0625 | 123.2895 | -61.4822 | 61.5829 | 0.025705 | -0.035942 | -0.012 | -0.020438 | 0.017953 | -0.005985 | 0.015112 | 61.5096 | 0.13416 | 61.45 | -0.10179 | 0.002454 | 61.5616 | -0.042641 | 61.2894 | 61.5079 | 61.4463 | 61.4702 | 61.4618 | 61.5002 | 61.4763 | 61.4974 | 122.9919 | 61.6164 | 122.9323 | 61.3805 | 61.4847 | 123.0438 | 61.4396 | 122.7716 | 61.5072 | 61.5523 | 61.4476 | 61.4927
39.1406 | 123.3398 | -61.4456 | 61.6104 | 0.021127 | -0.031363 | -0.025735 | -0.01586 | 0.022531 | -0.001406 | 0.005955 | 61.5142 | 0.12958 | 61.4592 | -0.10179 | 0.002454 | 61.557 | -0.04722 | 61.2986 | 61.4667 | 61.4143 | 61.4199 | 61.4298 | 61.4681 | 61.4442 | 61.4516 | 122.9598 | 61.5752 | 122.9048 | 61.3438 | 61.4481 | 123.0026 | 61.3984 | 122.7442 | 61.5118 | 61.5614 | 61.4567 | 61.5064
40.0625 | 123.2208 | -61.5051 | 61.5967 | 0.016548 | -0.040521 | -0.016578 | -0.01586 | 0.022531 | -0.005985 | 0.010533 | 61.505 | 0.12958 | 61.4592 | -0.11094 | 0.002454 | 61.5616 | -0.04722 | 61.2894 | 61.5217 | 61.4646 | 61.4885 | 61.4893 | 61.5277 | 61.4991 | 61.5157 | 123.0102 | 61.6347 | 122.9643 | 61.3942 | 61.5076 | 123.0667 | 61.4579 | 122.7945 | 61.5026 | 61.5523 | 61.4567 | 61.5064
41.0625 | 123.3353 | -61.4639 | 61.5463 | 0.021127 | -0.035942 | -0.012 | -0.006703 | 0.013375 | -0.001406 | 0.015112 | 61.5096 | 0.13416 | 61.45 | -0.10637 | 0.007032 | 61.5616 | -0.042641 | 61.294 | 61.4851 | 61.428 | 61.4519 | 61.4572 | 61.4773 | 61.4625 | 61.479 | 122.9736 | 61.5981 | 122.914 | 61.3576 | 61.471 | 123.0255 | 61.4213 | 122.7579 | 61.5026 | 61.5523 | 61.443 | 61.4927
42.0625 | 123.23 | -61.5097 | 61.615 | 0.021127 | -0.035942 | -0.007421 | -0.011281 | 0.022531 | -0.005985 | 0.015112 | 61.5096 | 0.12501 | 61.4088 | -0.10637 | -0.002124 | 61.5616 | -0.042641 | 61.294 | 61.5308 | 61.4738 | 61.5023 | 61.4984 | 61.5322 | 61.5037 | 61.5248 | 123.0193 | 61.6347 | 122.9185 | 61.4033 | 61.5076 | 123.0713 | 61.4671 | 122.8037 | 61.5118 | 61.5523 | 61.411 | 61.4515
43.125 | 123.3627 | -61.4594 | 61.5601 | 0.025705 | -0.035942 | -0.016578 | -0.011281 | 0.017953 | -0.010563 | 0.015112 | 61.4959 | 0.12501 | 61.3997 | -0.10637 | -0.002124 | 61.5616 | -0.038063 | 61.294 | 61.4851 | 61.4234 | 61.4428 | 61.4481 | 61.4773 | 61.4488 | 61.4745 | 122.9552 | 61.5844 | 122.859 | 61.353 | 61.4572 | 123.0209 | 61.4213 | 122.7533 | 61.498 | 61.534 | 61.4018 | 61.4377
44.0625 | 123.3215 | -61.4822 | 61.5784 | 0.025705 | -0.040521 | -0.016578 | -0.020438 | 0.017953 | -0.005985 | 0.010533 | 61.505 | 0.12958 | 61.3859 | -0.10179 | -0.002124 | 61.5478 | -0.042641 | 61.2848 | 61.5079 | 61.4417 | 61.4657 | 61.4618 | 61.5002 | 61.4763 | 61.4928 | 122.9873 | 61.6118 | 122.8682 | 61.3805 | 61.4801 | 123.0301 | 61.4396 | 122.7671 | 61.5072 | 61.5477 | 61.3881 | 61.4286
45.0625 | 123.2208 | -61.5051 | 61.5875 | 0.021127 | -0.031363 | -0.012 | -0.011281 | 0.022531 | -0.001406 | 0.010533 | 61.5005 | 0.12958 | 61.4409 | -0.11094 | 0.002454 | 61.557 | -0.038063 | 61.294 | 61.5263 | 61.4738 | 61.4931 | 61.4938 | 61.5277 | 61.5037 | 61.5157 | 123.0056 | 61.6347 | 122.946 | 61.3942 | 61.5076 | 123.0621 | 61.4671 | 122.7991 | 61.498 | 61.5385 | 61.4384 | 61.4789
46.0625 | 123.2941 | -61.4639 | 61.5784 | 0.021127 | -0.040521 | -0.016578 | -0.006703 | 0.027109 | -0.005985 | 0.015112 | 61.5096 | 0.12501 | 61.45 | -0.11094 | -0.002124 | 61.557 | -0.042641 | 61.2894 | 61.4851 | 61.4234 | 61.4474 | 61.4572 | 61.491 | 61.4579 | 61.479 | 122.9736 | 61.5889 | 122.914 | 61.353 | 61.4618 | 123.0209 | 61.4213 | 122.7533 | 61.5118 | 61.5523 | 61.4522 | 61.4927
47.0625 | 123.2529 | -61.4777 | 61.5738 | 0.030283 | -0.040521 | -0.007421 | -0.006703 | 0.013375 | -0.005985 | 0.010533 | 61.505 | 0.12958 | 61.4546 | -0.10637 | 0.007032 | 61.557 | -0.04722 | 61.294 | 61.5079 | 61.4371 | 61.4702 | 61.471 | 61.491 | 61.4717 | 61.4882 | 122.9827 | 61.6072 | 122.9323 | 61.3713 | 61.4847 | 123.0347 | 61.4304 | 122.7717 | 61.498 | 61.5523 | 61.4476 | 61.5018
48.125 | 123.3124 | -61.4731 | 61.5601 | 0.025705 | -0.040521 | -0.016578 | -0.011281 | 0.022531 | -0.001406 | 0.010533 | 61.5142 | 0.13416 | 61.45 | -0.097207 | 0.002454 | 61.5524 | -0.042641 | 61.294 | 61.4988 | 61.4326 | 61.4565 | 61.4618 | 61.4956 | 61.4717 | 61.4836 | 122.9873 | 61.6072 | 122.9231 | 61.3759 | 61.4755 | 123.0255 | 61.4304 | 122.7671 | 61.5118 | 61.5568 | 61.4476 | 61.4927
49.0625 | 123.317 | -61.4685 | 61.5326 | 0.021127 | -0.035942 | -0.012 | -0.011281 | 0.013375 | -0.005985 | 0.010533 | 61.5096 | 0.12501 | 61.4546 | -0.10637 | 0.002454 | 61.5524 | -0.051798 | 61.2894 | 61.4896 | 61.4326 | 61.4565 | 61.4572 | 61.4819 | 61.4625 | 61.479 | 122.9781 | 61.5935 | 122.9231 | 61.3621 | 61.471 | 123.0209 | 61.4167 | 122.7579 | 61.5072 | 61.5614 | 61.4522 | 61.5064
50.0625 | 123.3627 | -61.4731 | 61.5601 | 0.030283 | -0.031363 | -0.016578 | -0.01586 | 0.022531 | -0.010563 | 0.005955 | 61.5096 | 0.13874 | 61.4455 | -0.10179 | 0.007032 | 61.5616 | -0.042641 | 61.2986 | 61.5034 | 61.4417 | 61.4565 | 61.4572 | 61.4956 | 61.4625 | 61.479 | 122.9827 | 61.6118 | 122.9185 | 61.3713 | 61.4801 | 123.0347 | 61.4304 | 122.7717 | 61.5026 | 61.5523 | 61.4384 | 61.4881
51.125 | 123.3398 | -61.4548 | 61.5784 | 0.016548 | -0.040521 | -0.025735 | -0.01586 | 0.013375 | -0.005985 | 0.005955 | 61.505 | 0.13874 | 61.4363 | -0.10179 | 0.007032 | 61.5524 | -0.028906 | 61.2986 | 61.4713 | 61.4143 | 61.429 | 61.4389 | 61.4681 | 61.4488 | 61.4607 | 122.9598 | 61.5935 | 122.8911 | 61.353 | 61.4618 | 123.0072 | 61.4259 | 122.7533 | 61.498 | 61.534 | 61.4293 | 61.4652
52.0625 | 123.2071 | -61.4914 | 61.615 | 0.030283 | -0.031363 | -0.012 | -0.006703 | 0.017953 | 0.00775 | 0.01969 | 61.5279 | 0.13416 | 61.4775 | -0.046838 | 0.002454 | 61.5524 | -0.038063 | 61.3306 | 61.5217 | 61.46 | 61.4794 | 61.4847 | 61.5093 | 61.4991 | 61.5111 | 123.0193 | 61.6256 | 122.9689 | 61.4446 | 61.4938 | 123.0438 | 61.4533 | 122.822 | 61.5255 | 61.566 | 61.4751 | 61.5156
53.125 | 123.3078 | -61.4594 | 61.5601 | 0.030283 | -0.031363 | -0.016578 | -0.011281 | 0.017953 | -0.001406 | 0.010533 | 61.5188 | 0.12958 | 61.4684 | -0.051417 | 0.002454 | 61.5616 | -0.038063 | 61.326 | 61.4896 | 61.428 | 61.4428 | 61.4481 | 61.4773 | 61.4579 | 61.4699 | 122.9781 | 61.5889 | 122.9277 | 61.4079 | 61.4618 | 123.0209 | 61.4213 | 122.7854 | 61.5163 | 61.5568 | 61.4659 | 61.5064
54.0625 | 123.3582 | -61.4548 | 61.5555 | 0.025705 | -0.026784 | -0.007421 | -0.006703 | 0.022531 | -0.010563 | 0.024268 | 61.5279 | 0.13874 | 61.4729 | -0.046838 | -0.006702 | 61.5616 | -0.051798 | 61.326 | 61.4805 | 61.428 | 61.4474 | 61.4481 | 61.4773 | 61.4442 | 61.479 | 122.9827 | 61.5935 | 122.9277 | 61.4079 | 61.4481 | 123.0164 | 61.403 | 122.7808 | 61.5346 | 61.5797 | 61.4796 | 61.5247
55.125 | 123.2712 | -61.4731 | 61.5784 | 0.030283 | -0.040521 | -0.012 | -0.002124 | 0.027109 | 0.003172 | 0.01969 | 61.5371 | 0.13416 | 61.4775 | -0.046838 | -0.002124 | 61.5524 | -0.038063 | 61.326 | 61.5034 | 61.4326 | 61.4611 | 61.471 | 61.5002 | 61.4763 | 61.4928 | 123.0102 | 61.6072 | 122.9506 | 61.4262 | 61.471 | 123.0255 | 61.435 | 122.7991 | 61.5392 | 61.5752 | 61.4796 | 61.5156
56.0625 | 123.3444 | -61.4685 | 61.5646 | 0.021127 | -0.040521 | -0.012 | -0.011281 | 0.017953 | -0.005985 | 0.024268 | 61.5279 | 0.13874 | 61.4729 | -0.042259 | 0.007032 | 61.5662 | -0.042641 | 61.326 | 61.4896 | 61.428 | 61.4565 | 61.4572 | 61.4865 | 61.4625 | 61.4928 | 122.9964 | 61.6072 | 122.9414 | 61.4262 | 61.4755 | 123.0347 | 61.4259 | 122.7945 | 61.5209 | 61.5706 | 61.4659 | 61.5156
57.125 | 123.2941 | -61.4685 | 61.5646 | 0.021127 | -0.040521 | -0.021157 | -0.011281 | 0.022531 | 0.003172 | 0.015112 | 61.5279 | 0.12958 | 61.4729 | -0.03768 | 0.007032 | 61.5616 | -0.024328 | 61.3352 | 61.4896 | 61.428 | 61.4473 | 61.4572 | 61.491 | 61.4717 | 61.4836 | 122.9964 | 61.5981 | 122.9414 | 61.4308 | 61.4755 | 123.0301 | 61.4442 | 122.8037 | 61.5209 | 61.5523 | 61.4659 | 61.4973
58.0625 | 123.2986 | -61.4594 | 61.6013 | 0.025705 | -0.031363 | -0.012 | -0.006703 | 0.022531 | 0.003172 | 0.015112 | 61.5325 | 0.13874 | 61.4867 | -0.03768 | 0.01161 | 61.557 | -0.024328 | 61.3398 | 61.4851 | 61.428 | 61.4474 | 61.4526 | 61.4819 | 61.4625 | 61.4745 | 122.9919 | 61.5981 | 122.946 | 61.4217 | 61.471 | 123.0164 | 61.435 | 122.7991 | 61.5209 | 61.5568 | 61.4751 | 61.511
59.1406 | 123.349 | -61.4594 | 61.5875 | 0.021127 | -0.035942 | -0.012 | -0.011281 | 0.017953 | -0.001406 | 0.010533 | 61.5188 | 0.13416 | 61.4592 | -0.046838 | 0.01161 | 61.5616 | -0.07469 | 61.3215 | 61.4805 | 61.4234 | 61.4474 | 61.4481 | 61.4773 | 61.4579 | 61.4699 | 122.9781 | 61.5935 | 122.9185 | 61.4125 | 61.471 | 123.0209 | 61.3847 | 122.7808 | 61.5072 | 61.5935 | 61.4476 | 61.5339
60.0469 | 123.2254 | -61.4822 | 61.6013 | 0.021127 | -0.035942 | -0.016578 | -0.006703 | 0.022531 | 0.003172 | 0.01969 | 61.505 | 0.12501 | 61.45 | -0.060575 | -0.043328 | 61.5616 | -0.024328 | 61.3123 | 61.5034 | 61.4463 | 61.4657 | 61.4755 | 61.5048 | 61.4854 | 61.5019 | 122.9873 | 61.6072 | 122.9323 | 61.4217 | 61.4389 | 123.0438 | 61.4579 | 122.7945 | 61.5484 | 61.5294 | 61.4934 | 61.4744
61.125 | 123.2895 | -61.4456 | 61.5738 | 0.021127 | -0.035942 | -0.016578 | -0.011281 | 0.013375 | -0.010563 | 0.015112 | 61.5005 | 0.13416 | 61.3814 | -0.042259 | 0.016188 | 61.557 | -0.015171 | 61.3077 | 61.4667 | 61.4097 | 61.429 | 61.4343 | 61.459 | 61.4351 | 61.4607 | 122.9461 | 61.5798 | 122.827 | 61.4034 | 61.4618 | 123.0026 | 61.4304 | 122.7533 | 61.4843 | 61.5156 | 61.3652 | 61.3965
62.0625 | 123.2483 | -61.4731 | 61.6058 | 0.025705 | -0.040521 | -0.016578 | -0.01586 | 0.017953 | -0.005985 | 0.005955 | 61.505 | 0.12501 | 61.3722 | -0.097207 | 0.01161 | 61.5524 | -0.015171 | 61.5137 | 61.4988 | 61.4326 | 61.4565 | 61.4572 | 61.491 | 61.4671 | 61.479 | 122.9781 | 61.5981 | 122.8453 | 61.3759 | 61.4847 | 123.0255 | 61.4579 | 122.9868 | 61.4934 | 61.5202 | 61.3606 | 61.3874
63.0625 | 123.23 | -61.5097 | 61.6013 | 0.025705 | -0.035942 | -0.016578 | -0.011281 | 0.013375 | -0.005985 | 0.015112 | 61.5142 | 0.13416 | 61.4546 | -0.065154 | -0.002124 | 61.557 | -0.015171 | 61.3947 | 61.5354 | 61.4738 | 61.4931 | 61.4984 | 61.5231 | 61.5037 | 61.5248 | 123.0239 | 61.6439 | 122.9643 | 61.4446 | 61.5076 | 123.0667 | 61.4945 | 122.9044 | 61.5163 | 61.5294 | 61.4567 | 61.4698
64.0625 | 123.2849 | -61.4822 | 61.5738 | 0.025705 | -0.0451 | -0.016578 | -0.006703 | 0.013375 | -0.015142 | 0.010533 | 61.5096 | 0.13874 | 61.4455 | -0.051417 | 0.007032 | 61.5616 | -0.010593 | 61.4542 | 61.5079 | 61.4371 | 61.4657 | 61.4755 | 61.4956 | 61.4671 | 61.4928 | 122.9919 | 61.621 | 122.9277 | 61.4308 | 61.4893 | 123.0438 | 61.4716 | 122.9365 | 61.5026 | 61.5202 | 61.4384 | 61.4561
65.0625 | 123.2529 | -61.4868 | 61.615 | 0.021127 | -0.040521 | -0.016578 | -0.011281 | 0.013375 | -0.001406 | 0.01969 | 61.5234 | 0.12501 | 61.4592 | -0.055996 | 0.007032 | 61.5616 | -0.010593 | 61.4496 | 61.5079 | 61.4463 | 61.4702 | 61.4755 | 61.5002 | 61.4854 | 61.5065 | 123.0102 | 61.6118 | 122.946 | 61.4308 | 61.4938 | 123.0484 | 61.4762 | 122.9365 | 61.5163 | 61.534 | 61.4522 | 61.4698
66.125 | 123.3536 | -61.4548 | 61.5555 | 0.030283 | -0.035942 | -0.016578 | -0.011281 | 0.013375 | -0.005985 | 0.001377 | 61.5142 | 0.12958 | 61.45 | -0.069733 | 0.007032 | 61.557 | -0.015171 | 61.4405 | 61.4851 | 61.4188 | 61.4382 | 61.4435 | 61.4681 | 61.4488 | 61.4562 | 122.969 | 61.5844 | 122.9048 | 61.385 | 61.4618 | 123.0118 | 61.4396 | 122.8953 | 61.5072 | 61.5294 | 61.443 | 61.4652
67.0625 | 123.349 | -61.441 | 61.5921 | 0.030283 | -0.0451 | -0.016578 | -0.01586 | 0.013375 | -0.001406 | 0.001377 | 61.5096 | 0.12958 | 61.4546 | -0.078891 | 0.007032 | 61.557 | -0.006014 | 61.4313 | 61.4713 | 61.3959 | 61.4245 | 61.4252 | 61.4544 | 61.4396 | 61.4424 | 122.9507 | 61.5706 | 122.8957 | 61.3621 | 61.4481 | 122.998 | 61.435 | 122.8724 | 61.5026 | 61.5156 | 61.4476 | 61.4606
68.0625 | 123.2346 | -61.4822 | 61.6196 | 0.025705 | -0.031363 | -0.016578 | -0.006703 | 0.017953 | -0.005985 | 0.005955 | 61.5096 | 0.12501 | 61.4363 | -0.078891 | -0.002124 | 61.5616 | -0.015171 | 61.4084 | 61.5079 | 61.4509 | 61.4657 | 61.4755 | 61.5002 | 61.4763 | 61.4882 | 122.9919 | 61.6072 | 122.9185 | 61.4033 | 61.4801 | 123.0438 | 61.4671 | 122.8907 | 61.5118 | 61.5248 | 61.4384 | 61.4515
69.1562 | 123.1842 | -61.5005 | 61.6104 | 0.025705 | -0.035942 | -0.012 | -0.01586 | 0.017953 | -0.010563 | 0.005955 | 61.5096 | 0.13416 | 61.4134 | -0.088049 | -0.002124 | 61.557 | -0.010593 | 61.326 | 61.5263 | 61.4646 | 61.4885 | 61.4847 | 61.5185 | 61.49 | 61.5065 | 123.0102 | 61.6347 | 122.914 | 61.4125 | 61.4984 | 123.0576 | 61.49 | 122.8266 | 61.5118 | 61.5202 | 61.4155 | 61.424
70.0625 | 123.2986 | -61.4822 | 61.6333 | 0.034862 | -0.035942 | -0.016578 | -0.006703 | 0.017953 | -0.001406 | 0.015112 | 61.5142 | 0.12958 | 61.418 | -0.088049 | 0.01161 | 61.557 | -0.024328 | 61.3352 | 61.5171 | 61.4463 | 61.4657 | 61.4755 | 61.5002 | 61.4808 | 61.4974 | 122.9964 | 61.6118 | 122.9002 | 61.3942 | 61.4938 | 123.0392 | 61.4579 | 122.8174 | 61.5026 | 61.5385 | 61.4064 | 61.4423
71.0625 | 123.2346 | -61.4639 | 61.5875 | 0.034862 | -0.040521 | -0.012 | -0.002124 | 0.027109 | -0.001406 | 0.015112 | 61.5096 | 0.12958 | 61.4592 | -0.088049 | 0.007032 | 61.557 | -0.042641 | 61.3306 | 61.4988 | 61.4234 | 61.4519 | 61.4618 | 61.491 | 61.4625 | 61.479 | 122.9736 | 61.5935 | 122.9231 | 61.3759 | 61.471 | 123.0209 | 61.4213 | 122.7945 | 61.5026 | 61.5523 | 61.4522 | 61.5018
72.0625 | 123.2895 | -61.4548 | 61.5784 | 0.030283 | -0.031363 | -0.021157 | -0.002124 | 0.031687 | -0.001406 | 0.01969 | 61.5325 | 0.12958 | 61.4912 | -0.088049 | 0.01161 | 61.557 | -0.033484 | 61.3215 | 61.4851 | 61.4234 | 61.4336 | 61.4526 | 61.4865 | 61.4534 | 61.4745 | 122.9873 | 61.5844 | 122.946 | 61.3667 | 61.4664 | 123.0118 | 61.4213 | 122.7762 | 61.5209 | 61.566 | 61.4796 | 61.5247
73.0625 | 123.2483 | -61.5051 | 61.6058 | 0.034862 | -0.035942 | -0.016578 | -0.002124 | 0.027109 | 0.003172 | 0.024268 | 61.5508 | 0.12958 | 61.4912 | -0.092628 | 0.01161 | 61.557 | -0.04722 | 61.3123 | 61.54 | 61.4692 | 61.4885 | 61.503 | 61.5322 | 61.5083 | 61.5294 | 123.056 | 61.6347 | 122.9964 | 61.4125 | 61.5167 | 123.0621 | 61.4579 | 122.8174 | 61.5392 | 61.5981 | 61.4796 | 61.5385
74.1406 | 123.3398 | -61.4685 | 61.5784 | 0.030283 | -0.035942 | -0.012 | -0.006703 | 0.027109 | -0.001406 | 0.01969 | 61.5508 | 0.13416 | 61.4867 | -0.088049 | 0.007032 | 61.557 | -0.038063 | 61.3123 | 61.4988 | 61.4326 | 61.4565 | 61.4618 | 61.4956 | 61.4671 | 61.4882 | 123.0193 | 61.6027 | 122.9552 | 61.3805 | 61.4755 | 123.0255 | 61.4304 | 122.7808 | 61.5438 | 61.5889 | 61.4796 | 61.5247
75.0625 | 123.2666 | -61.4639 | 61.5967 | 0.025705 | -0.031363 | -0.016578 | -0.006703 | 0.017953 | 0.00775 | 0.028846 | 61.5463 | 0.13416 | 61.4958 | -0.088049 | 0.01161 | 61.5524 | -0.042641 | 61.3169 | 61.4896 | 61.4326 | 61.4474 | 61.4572 | 61.4819 | 61.4717 | 61.4928 | 123.0102 | 61.5981 | 122.9598 | 61.3759 | 61.4755 | 123.0164 | 61.4213 | 122.7808 | 61.5346 | 61.5889 | 61.4842 | 61.5385
76.125 | 123.2208 | -61.4731 | 61.5738 | 0.025705 | -0.031363 | -0.012 | -0.006703 | 0.027109 | 0.003172 | 0.01969 | 61.5463 | 0.14332 | 61.4912 | -0.092628 | 0.01161 | 61.5662 | -0.042641 | 61.3123 | 61.4988 | 61.4417 | 61.4611 | 61.4664 | 61.5002 | 61.4763 | 61.4928 | 123.0193 | 61.6164 | 122.9643 | 61.3805 | 61.4847 | 123.0392 | 61.4304 | 122.7854 | 61.5346 | 61.5889 | 61.4796 | 61.5339
77.0625 | 123.2895 | -61.4594 | 61.5738 | 0.030283 | -0.035942 | -0.012 | -0.002124 | 0.027109 | -0.005985 | 0.01969 | 61.56 | 0.13416 | 61.4912 | -0.092628 | 0.01161 | 61.557 | -0.038063 | 61.3169 | 61.4896 | 61.4234 | 61.4474 | 61.4572 | 61.4865 | 61.4534 | 61.479 | 123.0193 | 61.5935 | 122.9506 | 61.3667 | 61.471 | 123.0164 | 61.4213 | 122.7762 | 61.5484 | 61.5981 | 61.4796 | 61.5293
78.125 | 123.2849 | -61.4685 | 61.6287 | 0.030283 | -0.035942 | -0.012 | -0.002124 | 0.027109 | -0.001406 | 0.01969 | 61.5463 | 0.12958 | 61.4958 | -0.097207 | 0.007032 | 61.5662 | -0.042641 | 61.3215 | 61.4988 | 61.4326 | 61.4565 | 61.4664 | 61.4956 | 61.4671 | 61.4882 | 123.0148 | 61.5981 | 122.9643 | 61.3713 | 61.4755 | 123.0347 | 61.4259 | 122.79 | 61.5392 | 61.5889 | 61.4888 | 61.5385
79.0625 | 123.2208 | -61.4868 | 61.5875 | 0.034862 | -0.031363 | -0.016578 | -0.006703 | 0.031687 | 0.003172 | 0.01969 | 61.5508 | 0.13416 | 61.4958 | -0.08347 | 0.01161 | 61.557 | -0.042641 | 61.3169 | 61.5217 | 61.4555 | 61.4702 | 61.4801 | 61.5185 | 61.49 | 61.5065 | 123.0377 | 61.621 | 122.9826 | 61.4033 | 61.4984 | 123.0438 | 61.4442 | 122.8037 | 61.5392 | 61.5935 | 61.4842 | 61.5385
80.0625 | 123.2208 | -61.4777 | 61.6013 | 0.03944 | -0.035942 | -0.012 | -0.002124 | 0.017953 | -0.001406 | 0.01969 | 61.5554 | 0.13416 | 61.4958 | -0.08347 | 0.016188 | 61.557 | -0.042641 | 61.326 | 61.5171 | 61.4417 | 61.4657 | 61.4755 | 61.4956 | 61.4763 | 61.4974 | 123.0331 | 61.6118 | 122.9735 | 61.3942 | 61.4938 | 123.0347 | 61.435 | 122.8037 | 61.5392 | 61.5981 | 61.4796 | 61.5385
81.0625 | 123.2666 | -61.4731 | 61.6379 | 0.034862 | -0.035942 | -0.016578 | -0.002124 | 0.027109 | -0.001406 | 0.024268 | 61.5325 | 0.12958 | 61.4958 | -0.078891 | 0.007032 | 61.557 | -0.038063 | 61.3352 | 61.5079 | 61.4371 | 61.4565 | 61.471 | 61.5002 | 61.4717 | 61.4974 | 123.0056 | 61.6027 | 122.9689 | 61.3942 | 61.4801 | 123.0301 | 61.435 | 122.8083 | 61.5255 | 61.5706 | 61.4888 | 61.5339
82.0625 | 123.317 | -61.4822 | 61.5463 | 0.034862 | -0.035942 | -0.012 | -0.006703 | 0.031687 | -0.005985 | 0.015112 | 61.5371 | 0.13416 | 61.4867 | -0.088049 | 0.007032 | 61.5524 | -0.042641 | 61.3215 | 61.5171 | 61.4463 | 61.4702 | 61.4755 | 61.5139 | 61.4763 | 61.4974 | 123.0193 | 61.6164 | 122.9689 | 61.3942 | 61.4893 | 123.0347 | 61.4396 | 122.8037 | 61.5301 | 61.5797 | 61.4796 | 61.5293
83.125 | 123.2346 | -61.4822 | 61.6196 | 0.034862 | -0.031363 | -0.012 | -0.006703 | 0.027109 | 0.003172 | 0.015112 | 61.5142 | 0.12501 | 61.4363 | -0.088049 | 0.002454 | 61.557 | -0.033484 | 61.3352 | 61.5171 | 61.4509 | 61.4702 | 61.4755 | 61.5093 | 61.4854 | 61.4974 | 122.9964 | 61.6072 | 122.9185 | 61.3942 | 61.4847 | 123.0392 | 61.4488 | 122.8174 | 61.5118 | 61.5477 | 61.4339 | 61.4698
84.0625 | 123.2574 | -61.4548 | 61.6425 | 0.03944 | -0.040521 | -0.012 | -0.002124 | 0.013375 | -0.001406 | 0.015112 | 61.5188 | 0.13416 | 61.4409 | -0.08347 | 0.01161 | 61.557 | -0.038063 | 61.3352 | 61.4942 | 61.4143 | 61.4428 | 61.4526 | 61.4681 | 61.4534 | 61.4699 | 122.9736 | 61.5889 | 122.8957 | 61.3713 | 61.4664 | 123.0118 | 61.4167 | 122.79 | 61.5072 | 61.5568 | 61.4293 | 61.4789
85.0625 | 123.262 | -61.5005 | 61.6058 | 0.025705 | -0.040521 | -0.016578 | -0.006703 | 0.013375 | -0.005985 | 0.024268 | 61.5188 | 0.12958 | 61.4638 | -0.088049 | 0.01161 | 61.5616 | -0.010593 | 61.3352 | 61.5263 | 61.46 | 61.484 | 61.4938 | 61.5139 | 61.4946 | 61.5248 | 123.0193 | 61.6301 | 122.9643 | 61.4125 | 61.5122 | 123.0621 | 61.49 | 122.8357 | 61.5072 | 61.5294 | 61.4522 | 61.4744
86.0625 | 123.2574 | -61.4548 | 61.6241 | 0.016548 | -0.035942 | -0.021157 | -0.011281 | 0.017953 | -0.005985 | 0.010533 | 61.5142 | 0.12958 | 61.4455 | -0.08347 | 0.01161 | 61.5662 | -0.006014 | 61.3398 | 61.4713 | 61.4188 | 61.4336 | 61.4435 | 61.4727 | 61.4488 | 61.4653 | 122.969 | 61.5844 | 122.9002 | 61.3713 | 61.4664 | 123.0209 | 61.4488 | 122.7945 | 61.5026 | 61.5202 | 61.4339 | 61.4515
87.125 | 123.2941 | -61.4868 | 61.5967 | 0.021127 | -0.040521 | -0.021157 | -0.011281 | 0.008797 | 0.003172 | 0.010533 | 61.5188 | 0.13416 | 61.4409 | -0.078891 | 0.007032 | 61.557 | -0.015171 | 61.3398 | 61.5079 | 61.4463 | 61.4657 | 61.4755 | 61.4956 | 61.49 | 61.4973 | 123.0056 | 61.621 | 122.9277 | 61.4079 | 61.4938 | 123.0438 | 61.4716 | 122.8266 | 61.5118 | 61.534 | 61.4339 | 61.4561
88.0625 | 123.2483 | -61.4731 | 61.6333 | 0.030283 | -0.035942 | -0.016578 | -0.01586 | 0.017953 | -0.005985 | 0.015112 | 61.5188 | 0.12958 | 61.4546 | -0.078891 | 0.002454 | 61.5616 | -0.010593 | 61.3489 | 61.5034 | 61.4371 | 61.4565 | 61.4572 | 61.491 | 61.4671 | 61.4882 | 122.9919 | 61.6027 | 122.9277 | 61.3942 | 61.4755 | 123.0347 | 61.4625 | 122.822 | 61.5163 | 61.5294 | 61.4522 | 61.4652
89.1406 | 123.3307 | -61.4456 | 61.5692 | 0.01197 | -0.0451 | -0.021157 | -0.020438 | 0.017953 | -0.005985 | 0.015112 | 61.5096 | 0.13416 | 61.418 | -0.08347 | 0.007032 | 61.5616 | -0.015171 | 61.3627 | 61.4576 | 61.4005 | 61.4245 | 61.4252 | 61.4636 | 61.4396 | 61.4607 | 122.9552 | 61.5798 | 122.8636 | 61.3621 | 61.4527 | 123.0072 | 61.4304 | 122.8083 | 61.5026 | 61.5248 | 61.411 | 61.4332
90.0625 | 123.2391 | -61.4685 | 61.615 | 0.021127 | -0.040521 | -0.012 | -0.01586 | 0.022531 | 0.003172 | 0.015112 | 61.5142 | 0.12958 | 61.418 | -0.078891 | 0.007032 | 61.5662 | -0.006014 | 61.413 | 61.4896 | 61.428 | 61.4565 | 61.4526 | 61.491 | 61.4717 | 61.4836 | 122.9827 | 61.5981 | 122.8865 | 61.3896 | 61.4755 | 123.0347 | 61.4625 | 122.8815 | 61.5072 | 61.5202 | 61.411 | 61.424
91.125 | 123.262 | -61.4777 | 61.615 | 0.030283 | -0.040521 | -0.012 | -0.011281 | 0.017953 | -0.005985 | 0.015112 | 61.5142 | 0.12958 | 61.4546 | -0.078891 | 0.002454 | 61.5524 | -0.006014 | 61.4222 | 61.5079 | 61.4371 | 61.4657 | 61.4664 | 61.4956 | 61.4717 | 61.4928 | 122.9919 | 61.6072 | 122.9323 | 61.3988 | 61.4801 | 123.0301 | 61.4716 | 122.8998 | 61.5118 | 61.5202 | 61.4522 | 61.4606
92.0625 | 123.2849 | -61.4822 | 61.6013 | 0.025705 | -0.031363 | -0.016578 | -0.006703 | 0.022531 | -0.001406 | 0.015112 | 61.5142 | 0.12958 | 61.4638 | -0.08347 | 0.01161 | 61.5616 | -0.015171 | 61.4268 | 61.5079 | 61.4509 | 61.4657 | 61.4755 | 61.5048 | 61.4808 | 61.4974 | 122.9964 | 61.6118 | 122.946 | 61.3988 | 61.4938 | 123.0438 | 61.4671 | 122.909 | 61.5026 | 61.5294 | 61.4522 | 61.4789
93.125 | 123.1888 | -61.4914 | 61.5829 | 0.021127 | -0.040521 | -0.021157 | -0.006703 | 0.008797 | -0.005985 | 0.010533 | 61.5142 | 0.13874 | 61.4226 | -0.08347 | 0.002454 | 61.5524 | -0.006014 | 61.4268 | 61.5125 | 61.4509 | 61.4702 | 61.4847 | 61.5002 | 61.4854 | 61.5019 | 123.0056 | 61.6301 | 122.914 | 61.4079 | 61.4938 | 123.0438 | 61.4854 | 122.9182 | 61.5118 | 61.5202 | 61.4201 | 61.4286
94.0625 | 123.2529 | -61.4868 | 61.6058 | 0.030283 | -0.035942 | -0.012 | -0.006703 | 0.022531 | -0.010563 | 0.010533 | 61.5142 | 0.12958 | 61.3997 | -0.078891 | 0.007032 | 61.5524 | -0.006014 | 61.4222 | 61.5171 | 61.4509 | 61.4748 | 61.4801 | 61.5093 | 61.4763 | 61.4973 | 123.001 | 61.6164 | 122.8865 | 61.4079 | 61.4938 | 123.0392 | 61.4808 | 122.909 | 61.5072 | 61.5202 | 61.3926 | 61.4057
95.0625 | 123.3536 | -61.4456 | 61.5829 | 0.016548 | -0.0451 | -0.016578 | -0.011281 | 0.008797 | -0.010563 | 0.010533 | 61.5096 | 0.13416 | 61.4134 | -0.065154 | 0.007032 | 61.5616 | -0.006014 | 61.4359 | 61.4622 | 61.4005 | 61.429 | 61.4343 | 61.4544 | 61.4351 | 61.4562 | 122.9552 | 61.5798 | 122.859 | 61.3805 | 61.4527 | 123.0072 | 61.4396 | 122.8815 | 61.5026 | 61.5156 | 61.4064 | 61.4194
96.125 | 123.317 | -61.528 | 61.6196 | 0.025705 | -0.031363 | -0.016578 | -0.01586 | 0.017953 | 0.003172 | 0.01969 | 61.5188 | 0.12501 | 61.4546 | -0.069733 | 0.002454 | 61.557 | -0.006014 | 61.4359 | 61.5537 | 61.4967 | 61.5114 | 61.5122 | 61.546 | 61.5312 | 61.5477 | 123.0468 | 61.653 | 122.9826 | 61.4583 | 61.5305 | 123.085 | 61.522 | 122.9639 | 61.5163 | 61.5248 | 61.4522 | 61.4606
97.0625 | 123.2346 | -61.4639 | 61.6241 | 0.025705 | -0.035942 | -0.016578 | -0.002124 | 0.013375 | -0.005985 | 0.005955 | 61.5096 | 0.13416 | 61.3951 | -0.060575 | 0.002454 | 61.5616 | -0.010593 | 61.4451 | 61.4896 | 61.428 | 61.4474 | 61.4618 | 61.4773 | 61.4579 | 61.4699 | 122.9736 | 61.5981 | 122.859 | 61.4034 | 61.4664 | 123.0255 | 61.4533 | 122.909 | 61.5072 | 61.5202 | 61.3926 | 61.4057
98.0625 | 123.3215 | -61.4548 | 61.5967 | 0.025705 | -0.0451 | -0.016578 | -0.011281 | 0.013375 | -0.005985 | 0.015112 | 61.5142 | 0.12958 | 61.4317 | -0.055996 | 0.007032 | 61.5616 | -0.006014 | 61.4451 | 61.4805 | 61.4097 | 61.4382 | 61.4435 | 61.4681 | 61.4488 | 61.4699 | 122.969 | 61.5844 | 122.8865 | 61.3988 | 61.4618 | 123.0164 | 61.4488 | 122.8998 | 61.5072 | 61.5202 | 61.4247 | 61.4377
99.1406 | 123.2254 | -61.5143 | 61.6196 | 0.025705 | -0.031363 | -0.016578 | -0.011281 | 0.027109 | -0.001406 | 0.01969 | 61.5188 | 0.13416 | 61.4546 | -0.055996 | 0.002454 | 61.5616 | -0.010593 | 61.4359 | 61.54 | 61.4829 | 61.4977 | 61.503 | 61.5414 | 61.5129 | 61.534 | 123.0331 | 61.6484 | 122.9689 | 61.4583 | 61.5167 | 123.0759 | 61.5037 | 122.9502 | 61.5163 | 61.5294 | 61.4522 | 61.4652
100.0625 | 123.3582 | -61.4319 | 61.5692 | 0.025705 | -0.035942 | -0.016578 | -0.011281 | 0.017953 | -0.005985 | 0.005955 | 61.5142 | 0.13416 | 61.3905 | -0.055996 | 0.002454 | 61.5524 | -0.010593 | 61.4405 | 61.4576 | 61.3959 | 61.4153 | 61.4206 | 61.4498 | 61.4259 | 61.4378 | 122.9461 | 61.566 | 122.8224 | 61.3759 | 61.4343 | 122.9843 | 61.4213 | 122.8724 | 61.5118 | 61.5248 | 61.3881 | 61.4011
101.0625 | 123.2574 | -61.4777 | 61.6196 | 0.025705 | -0.035942 | -0.021157 | -0.01586 | 0.013375 | -0.005985 | 0.015112 | 61.5142 | 0.12958 | 61.3951 | -0.055996 | 0.002454 | 61.557 | -0.010593 | 61.4496 | 61.5034 | 61.4417 | 61.4565 | 61.4618 | 61.491 | 61.4717 | 61.4928 | 122.9919 | 61.6072 | 122.8728 | 61.4217 | 61.4801 | 123.0347 | 61.4671 | 122.9273 | 61.5118 | 61.5248 | 61.3926 | 61.4057
102.0625 | 123.3673 | -61.4731 | 61.6013 | 0.030283 | -0.031363 | -0.012 | -0.011281 | 0.017953 | -0.001406 | 0.015112 | 61.5188 | 0.13416 | 61.4546 | -0.065154 | -0.002124 | 61.5524 | -0.010593 | 61.4496 | 61.5034 | 61.4417 | 61.4611 | 61.4618 | 61.491 | 61.4717 | 61.4882 | 122.9919 | 61.6072 | 122.9277 | 61.4079 | 61.471 | 123.0255 | 61.4625 | 122.9227 | 61.5209 | 61.5294 | 61.4567 | 61.4652
103.125 | 123.3398 | -61.4273 | 61.5967 | 0.025705 | -0.040521 | -0.016578 | -0.01586 | 0.017953 | -0.001406 | 0.015112 | 61.5096 | 0.13416 | 61.4134 | -0.055996 | 0.01161 | 61.5662 | -0.006014 | 61.4542 | 61.453 | 61.3868 | 61.4107 | 61.4114 | 61.4453 | 61.4259 | 61.4424 | 122.9369 | 61.5615 | 122.8407 | 61.3713 | 61.4389 | 122.9935 | 61.4213 | 122.8815 | 61.498 | 61.5156 | 61.4018 | 61.4194
104.0625 | 123.2803 | -61.4822 | 61.6379 | 0.025705 | -0.035942 | -0.021157 | -0.011281 | 0.017953 | -0.005985 | 0.005955 | 61.505 | 0.13874 | 61.4088 | -0.055996 | 0.002454 | 61.557 | -0.010593 | 61.4542 | 61.5079 | 61.4463 | 61.4611 | 61.471 | 61.5002 | 61.4763 | 61.4882 | 122.9873 | 61.621 | 122.8911 | 61.4262 | 61.4847 | 123.0392 | 61.4716 | 122.9365 | 61.5026 | 61.5156 | 61.4064 | 61.4194
105.0625 | 123.3627 | -61.4227 | 61.5967 | 0.025705 | -0.040521 | -0.021157 | -0.011281 | 0.017953 | -0.010563 | 0.015112 | 61.5188 | 0.13874 | 61.4638 | -0.060575 | 0.007032 | 61.5616 | -0.010593 | 61.4496 | 61.4484 | 61.3822 | 61.4016 | 61.4114 | 61.4407 | 61.4122 | 61.4378 | 122.9415 | 61.5615 | 122.8865 | 61.3622 | 61.4298 | 122.9843 | 61.4121 | 122.8724 | 61.5118 | 61.5294 | 61.4567 | 61.4744
106.125 | 123.2941 | -61.4639 | 61.6196 | 0.016548 | -0.0451 | -0.012 | -0.011281 | 0.022531 | -0.005985 | 0.010533 | 61.505 | 0.12501 | 61.4134 | -0.060575 | 0.01161 | 61.5478 | -0.006014 | 61.4588 | 61.4805 | 61.4188 | 61.4519 | 61.4526 | 61.4865 | 61.4579 | 61.4745 | 122.969 | 61.5889 | 122.8773 | 61.4034 | 61.4755 | 123.0118 | 61.4579 | 122.9227 | 61.4934 | 61.5111 | 61.4018 | 61.4194
107.0625 | 123.3398 | -61.4456 | 61.5875 | 0.025705 | -0.0451 | -0.021157 | -0.011281 | 0.013375 | -0.001406 | 0.015112 | 61.5096 | 0.13416 | 61.4088 | -0.055996 | 0.007032 | 61.557 | -0.015171 | 61.4496 | 61.4713 | 61.4005 | 61.4245 | 61.4343 | 61.459 | 61.4442 | 61.4607 | 122.9552 | 61.5798 | 122.8545 | 61.3896 | 61.4527 | 123.0026 | 61.4304 | 122.8953 | 61.5026 | 61.5248 | 61.4018 | 61.424
108.0625 | 123.3398 | -61.4822 | 61.5784 | 0.021127 | -0.035942 | -0.012 | -0.006703 | 0.017953 | -0.005985 | 0.015112 | 61.5188 | 0.13416 | 61.45 | -0.060575 | 0.002454 | 61.557 | -0.010593 | 61.4496 | 61.5034 | 61.4463 | 61.4702 | 61.4755 | 61.5002 | 61.4763 | 61.4974 | 123.001 | 61.6164 | 122.9323 | 61.4217 | 61.4847 | 123.0392 | 61.4716 | 122.9319 | 61.5163 | 61.5294 | 61.4476 | 61.4606
109.0625 | 123.2529 | -61.496 | 61.6196 | 0.016548 | -0.040521 | -0.016578 | -0.011281 | 0.027109 | -0.001406 | 0.010533 | 61.5234 | 0.12958 | 61.45 | -0.046838 | 0.007032 | 61.5524 | -0.010593 | 61.4451 | 61.5125 | 61.4555 | 61.4794 | 61.4847 | 61.5231 | 61.4946 | 61.5065 | 123.0193 | 61.6256 | 122.946 | 61.4491 | 61.503 | 123.0484 | 61.4854 | 122.941 | 61.5163 | 61.534 | 61.443 | 61.4606
110.125 | 123.3902 | -61.441 | 61.6058 | 0.016548 | -0.035942 | -0.012 | -0.01586 | 0.008797 | -0.005985 | 0.010533 | 61.5142 | 0.13874 | 61.3951 | -0.060575 | 0.002454 | 61.557 | -0.001436 | 61.4588 | 61.4576 | 61.4051 | 61.429 | 61.4252 | 61.4498 | 61.4351 | 61.4516 | 122.9552 | 61.5798 | 122.8361 | 61.3805 | 61.4435 | 122.998 | 61.4396 | 122.8998 | 61.5118 | 61.5156 | 61.3926 | 61.3965
111.0625 | 123.3353 | -61.4594 | 61.5967 | 0.030283 | -0.0451 | -0.021157 | -0.006703 | 0.008797 | -0.010563 | 0.015112 | 61.5142 | 0.12501 | 61.4317 | -0.055996 | 0.007032 | 61.5524 | -0.006014 | 61.4542 | 61.4896 | 61.4143 | 61.4382 | 61.4526 | 61.4681 | 61.4488 | 61.4745 | 122.9736 | 61.5844 | 122.8911 | 61.4034 | 61.4664 | 123.0118 | 61.4533 | 122.9136 | 61.5072 | 61.5202 | 61.4247 | 61.4377
112.125 | 123.2666 | -61.4914 | 61.6425 | 0.016548 | -0.040521 | -0.016578 | -0.011281 | 0.022531 | -0.001406 | 0.01969 | 61.5234 | 0.12501 | 61.4638 | -0.051417 | 0.007032 | 61.5524 | -0.006014 | 61.4542 | 61.5079 | 61.4509 | 61.4748 | 61.4801 | 61.5139 | 61.49 | 61.5111 | 123.0148 | 61.6164 | 122.9552 | 61.44 | 61.4984 | 123.0438 | 61.4854 | 122.9456 | 61.5163 | 61.5294 | 61.4567 | 61.4698
113.0625 | 123.3215 | -61.4685 | 61.615 | 0.021127 | -0.049678 | -0.016578 | -0.011281 | 0.017953 | -0.005985 | 0.005955 | 61.5142 | 0.13416 | 61.4043 | -0.055996 | 0.007032 | 61.5524 | -0.006014 | 61.4496 | 61.4896 | 61.4188 | 61.4519 | 61.4572 | 61.4865 | 61.4625 | 61.4745 | 122.9827 | 61.6027 | 122.8728 | 61.4125 | 61.4755 | 123.0209 | 61.4625 | 122.9182 | 61.5072 | 61.5202 | 61.3972 | 61.4103
114.1406 | 123.2986 | -61.4685 | 61.6425 | 0.021127 | -0.040521 | -0.016578 | -0.006703 | 0.013375 | -0.005985 | 0.015112 | 61.5096 | 0.13416 | 61.45 | -0.055996 | 0.002454 | 61.5616 | -0.010593 | 61.4542 | 61.4896 | 61.428 | 61.4519 | 61.4618 | 61.4819 | 61.4625 | 61.4836 | 122.9781 | 61.6027 | 122.9185 | 61.4125 | 61.471 | 123.0301 | 61.4579 | 122.9227 | 61.5072 | 61.5202 | 61.4476 | 61.4606
115.0625 | 123.349 | -61.4365 | 61.6013 | 0.021127 | -0.049678 | -0.021157 | -0.011281 | 0.008797 | -0.010563 | 0.010533 | 61.5142 | 0.13416 | 61.4592 | -0.065154 | 0.002454 | 61.5524 | -0.010593 | 61.4496 | 61.4576 | 61.3868 | 61.4153 | 61.4252 | 61.4453 | 61.4259 | 61.447 | 122.9507 | 61.5706 | 122.8957 | 61.3713 | 61.4389 | 122.9889 | 61.4259 | 122.8861 | 61.5118 | 61.5248 | 61.4567 | 61.4698
116.125 | 123.2986 | -61.4685 | 61.5967 | 0.025705 | -0.040521 | -0.012 | -0.006703 | 0.013375 | -0.005985 | 0.010533 | 61.5188 | 0.13416 | 61.418 | -0.055996 | 0.01161 | 61.557 | -0.010593 | 61.4542 | 61.4942 | 61.428 | 61.4565 | 61.4618 | 61.4819 | 61.4625 | 61.479 | 122.9873 | 61.6027 | 122.8865 | 61.4125 | 61.4801 | 123.0255 | 61.4579 | 122.9227 | 61.5072 | 61.5294 | 61.4064 | 61.4286
117.0625 | 123.3765 | -61.4365 | 61.6562 | 0.021127 | -0.0451 | -0.021157 | -0.006703 | 0.017953 | -0.005985 | 0.015112 | 61.5096 | 0.13874 | 61.4592 | -0.060575 | 0.002454 | 61.5616 | -0.006014 | 61.4542 | 61.4576 | 61.3914 | 61.4153 | 61.4298 | 61.4544 | 61.4305 | 61.4516 | 122.9461 | 61.5752 | 122.8957 | 61.3759 | 61.4389 | 122.998 | 61.4304 | 122.8907 | 61.5072 | 61.5156 | 61.4567 | 61.4652
118.125 | 123.2895 | -61.4685 | 61.5829 | 0.021127 | -0.035942 | -0.016578 | -0.006703 | 0.017953 | -0.001406 | 0.015112 | 61.5142 | 0.13416 | 61.4592 | -0.046838 | 0.01161 | 61.557 | -0.015171 | 61.4542 | 61.4896 | 61.4326 | 61.4519 | 61.4618 | 61.4865 | 61.4671 | 61.4836 | 122.9827 | 61.6027 | 122.9277 | 61.4217 | 61.4801 | 123.0255 | 61.4533 | 122.9227 | 61.5026 | 61.5294 | 61.4476 | 61.4744
119.0625 | 123.2162 | -61.4822 | 61.6379 | 0.025705 | -0.040521 | -0.007421 | -0.01586 | 0.017953 | -0.005985 | 0.010533 | 61.5096 | 0.13874 | 61.4043 | -0.051417 | 0.01161 | 61.557 | -0.019749 | 61.4542 | 61.5079 | 61.4417 | 61.4748 | 61.4664 | 61.5002 | 61.4763 | 61.4928 | 122.9919 | 61.621 | 122.8865 | 61.4308 | 61.4938 | 123.0392 | 61.4625 | 122.9365 | 61.498 | 61.5294 | 61.3926 | 61.424
120.0625 | 123.2895 | -61.4456 | 61.6241 | 0.025705 | -0.040521 | -0.016578 | -0.011281 | 0.022531 | -0.010563 | 0.01969 | 61.5188 | 0.13416 | 61.4592 | -0.055996 | 0.002454 | 61.557 | -0.010593 | 61.4588 | 61.4713 | 61.4051 | 61.429 | 61.4343 | 61.4681 | 61.4351 | 61.4653 | 122.9644 | 61.5798 | 122.9048 | 61.3896 | 61.4481 | 123.0026 | 61.435 | 122.9044 | 61.5163 | 61.5294 | 61.4567 | 61.4698
121.125 | 123.2895 | -61.4822 | 61.6058 | 0.030283 | -0.0451 | -0.007421 | -0.020438 | 0.031687 | -0.001406 | 0.015112 | 61.5142 | 0.13416 | 61.4546 | -0.055996 | 0.002454 | 61.5616 | -0.010593 | 61.4588 | 61.5125 | 61.4371 | 61.4748 | 61.4618 | 61.5139 | 61.4808 | 61.4974 | 122.9964 | 61.6164 | 122.9369 | 61.4262 | 61.4847 | 123.0438 | 61.4716 | 122.941 | 61.5118 | 61.5248 | 61.4522 | 61.4652
122.0625 | 123.3856 | -61.4548 | 61.5967 | 0.030283 | -0.0451 | -0.007421 | -0.01586 | 0.017953 | -0.010563 | 0.010533 | 61.5142 | 0.13874 | 61.4088 | -0.055996 | 0.002454 | 61.5616 | -0.001436 | 61.4588 | 61.4851 | 61.4097 | 61.4474 | 61.4389 | 61.4727 | 61.4442 | 61.4653 | 122.969 | 61.5935 | 122.8636 | 61.3988 | 61.4572 | 123.0164 | 61.4533 | 122.9136 | 61.5118 | 61.5156 | 61.4064 | 61.4103
123.125 | 123.2712 | -61.4914 | 61.6333 | 0.025705 | -0.040521 | -0.016578 | -0.011281 | 0.022531 | -0.001406 | 0.01969 | 61.5234 | 0.13874 | 61.4638 | -0.055996 | 0.002454 | 61.5524 | -0.010593 | 61.4588 | 61.5171 | 61.4509 | 61.4748 | 61.4801 | 61.5139 | 61.49 | 61.5111 | 123.0148 | 61.6301 | 122.9552 | 61.4354 | 61.4938 | 123.0438 | 61.4808 | 122.9502 | 61.5209 | 61.534 | 61.4613 | 61.4744
124.0625 | 123.2391 | -61.4639 | 61.6425 | 0.030283 | -0.035942 | -0.016578 | -0.011281 | 0.017953 | -0.005985 | 0.015112 | 61.5188 | 0.13416 | 61.4088 | -0.055996 | 0.016188 | 61.5524 | -0.006014 | 61.4588 | 61.4942 | 61.428 | 61.4474 | 61.4526 | 61.4819 | 61.4579 | 61.479 | 122.9827 | 61.5981 | 122.8728 | 61.4079 | 61.4801 | 123.0164 | 61.4579 | 122.9227 | 61.5026 | 61.5248 | 61.3926 | 61.4149
125.0625 | 123.3627 | -61.4639 | 61.6013 | 0.021127 | -0.035942 | -0.016578 | -0.01586 | 0.013375 | -0.001406 | 0.01969 | 61.5096 | 0.13416 | 61.4592 | -0.060575 | 0.007032 | 61.5616 | -0.001436 | 61.4451 | 61.4851 | 61.428 | 61.4474 | 61.4481 | 61.4773 | 61.4625 | 61.4836 | 122.9736 | 61.5981 | 122.9231 | 61.4034 | 61.471 | 123.0255 | 61.4625 | 122.909 | 61.5026 | 61.5111 | 61.4522 | 61.4606
126.0625 | 123.3353 | -61.4548 | 61.5875 | 0.016548 | -0.031363 | -0.016578 | -0.01586 | 0.017953 | -0.015142 | 0.010533 | 61.505 | 0.13416 | 61.4043 | -0.060575 | 0.01161 | 61.557 | -0.015171 | 61.4405 | 61.4713 | 61.4234 | 61.4382 | 61.4389 | 61.4727 | 61.4396 | 61.4653 | 122.9598 | 61.5889 | 122.859 | 61.3942 | 61.4664 | 123.0118 | 61.4396 | 122.8953 | 61.4934 | 61.5202 | 61.3926 | 61.4194
127.125 | 123.2941 | -61.4685 | 61.6104 | 0.021127 | -0.040521 | -0.016578 | -0.01586 | 0.017953 | -0.001406 | 0.01969 | 61.5188 | 0.13874 | 61.4546 | -0.051417 | 0.007032 | 61.5616 | -0.006014 | 61.4359 | 61.4896 | 61.428 | 61.4519 | 61.4526 | 61.4865 | 61.4671 | 61.4882 | 122.9873 | 61.6072 | 122.9231 | 61.4171 | 61.4755 | 123.0301 | 61.4625 | 122.9044 | 61.5118 | 61.5248 | 61.4476 | 61.4606
128.0625 | 123.381 | -61.4594 | 61.5875 | 0.030283 | -0.040521 | -0.021157 | -0.011281 | 0.017953 | -0.015142 | 0.015112 | 61.5142 | 0.13874 | 61.4043 | -0.055996 | 0.002454 | 61.5616 | -0.010593 | 61.4542 | 61.4896 | 61.4188 | 61.4382 | 61.4481 | 61.4773 | 61.4442 | 61.4745 | 122.9736 | 61.5981 | 122.8636 | 61.4034 | 61.4618 | 123.0209 | 61.4488 | 122.9136 | 61.5118 | 61.5248 | 61.4018 | 61.4149
129.1406 | 123.2803 | -61.4777 | 61.5829 | 0.025705 | -0.040521 | -0.016578 | -0.002124 | 0.022531 | -0.010563 | 0.024268 | 61.5142 | 0.12958 | 61.4638 | -0.055996 | 0.002454 | 61.5662 | -0.015171 | 61.4405 | 61.5034 | 61.4371 | 61.4611 | 61.4755 | 61.5002 | 61.4671 | 61.5019 | 122.9919 | 61.6072 | 122.9414 | 61.4217 | 61.4801 | 123.0438 | 61.4625 | 122.9182 | 61.5118 | 61.5294 | 61.4613 | 61.4789
130.0469 | 123.3719 | -61.4502 | 61.5967 | 0.021127 | -0.040521 | -0.012 | -0.01586 | 0.017953 | -0.005985 | 0.010533 | 61.5142 | 0.12958 | 61.4363 | -0.051417 | 0.007032 | 61.557 | -0.001436 | 61.4451 | 61.4713 | 61.4097 | 61.4382 | 61.4343 | 61.4681 | 61.4442 | 61.4607 | 122.9644 | 61.5798 | 122.8865 | 61.3988 | 61.4572 | 123.0072 | 61.4488 | 122.8953 | 61.5072 | 61.5156 | 61.4293 | 61.4377
131.0625 | 123.3398 | -61.4548 | 61.5967 | 0.025705 | -0.040521 | -0.012 | -0.020438 | 0.013375 | -0.005985 | 0.010533 | 61.5096 | 0.13416 | 61.4317 | -0.055996 | -0.002124 | 61.5662 | -0.015171 | 61.4451 | 61.4805 | 61.4143 | 61.4428 | 61.4343 | 61.4681 | 61.4488 | 61.4653 | 122.9644 | 61.5889 | 122.8865 | 61.3988 | 61.4526 | 123.0209 | 61.4396 | 122.8998 | 61.5118 | 61.5248 | 61.4339 | 61.4469
132.125 | 123.2162 | -61.4685 | 61.6287 | 0.021127 | -0.0451 | -0.021157 | -0.01586 | 0.017953 | 0.003172 | 0.01969 | 61.5188 | 0.13416 | 61.4409 | -0.055996 | 0.007032 | 61.5524 | -0.006014 | 61.4542 | 61.4896 | 61.4234 | 61.4473 | 61.4526 | 61.4865 | 61.4717 | 61.4882 | 122.9873 | 61.6027 | 122.9094 | 61.4125 | 61.4755 | 123.0209 | 61.4625 | 122.9227 | 61.5118 | 61.5248 | 61.4339 | 61.4469
133.0625 | 123.3124 | -61.4639 | 61.5738 | 0.021127 | -0.040521 | -0.016578 | -0.011281 | 0.013375 | -0.001406 | 0.01969 | 61.5142 | 0.13874 | 61.3997 | -0.055996 | 0.002454 | 61.557 | -0.001436 | 61.4405 | 61.4851 | 61.4234 | 61.4474 | 61.4526 | 61.4773 | 61.4625 | 61.4836 | 122.9781 | 61.6027 | 122.8636 | 61.4079 | 61.4664 | 123.0209 | 61.4625 | 122.9044 | 61.5118 | 61.5156 | 61.3972 | 61.4011
134.0625 | 123.3627 | -61.3998 | 61.6058 | 0.021127 | -0.035942 | -0.016578 | -0.006703 | 0.017953 | -0.005985 | 0.010533 | 61.5142 | 0.12043 | 61.4592 | -0.055996 | 0.007032 | 61.5616 | -0.010593 | 61.4542 | 61.421 | 61.3639 | 61.3833 | 61.3931 | 61.4178 | 61.3939 | 61.4104 | 122.914 | 61.5203 | 122.859 | 61.3438 | 61.4069 | 122.9614 | 61.3892 | 122.8541 | 61.5072 | 61.5248 | 61.4522 | 61.4698
135.0625 | 123.3215 | -61.4777 | 61.5921 | 0.021127 | -0.040521 | -0.021157 | -0.006703 | 0.013375 | -0.015142 | 0.015112 | 61.5096 | 0.12958 | 61.3951 | -0.060575 | 0.007032 | 61.5616 | -0.010593 | 61.4451 | 61.4988 | 61.4371 | 61.4565 | 61.471 | 61.491 | 61.4625 | 61.4928 | 122.9873 | 61.6072 | 122.8728 | 61.4171 | 61.4847 | 123.0392 | 61.4671 | 122.9227 | 61.5026 | 61.5202 | 61.3881 | 61.4057
136.125 | 123.3444 | -61.4685 | 61.5875 | 0.021127 | -0.035942 | -0.012 | -0.011281 | 0.017953 | -0.005985 | 0.010533 | 61.5188 | 0.13416 | 61.4638 | -0.060575 | -0.002124 | 61.557 | -0.015171 | 61.4451 | 61.4896 | 61.4326 | 61.4565 | 61.4572 | 61.4865 | 61.4625 | 61.479 | 122.9873 | 61.6027 | 122.9323 | 61.4079 | 61.4664 | 123.0255 | 61.4533 | 122.9136 | 61.5209 | 61.534 | 61.4659 | 61.4789
137.0625 | 123.3261 | -61.4594 | 61.5784 | 0.021127 | -0.040521 | -0.012 | -0.01586 | 0.017953 | -0.005985 | 0.010533 | 61.5096 | 0.13416 | 61.3951 | -0.051417 | 0.002454 | 61.5616 | -0.010593 | 61.4405 | 61.4805 | 61.4188 | 61.4474 | 61.4435 | 61.4773 | 61.4534 | 61.4699 | 122.969 | 61.5935 | 122.8545 | 61.4079 | 61.4618 | 123.0209 | 61.4488 | 122.8998 | 61.5072 | 61.5202 | 61.3926 | 61.4057
138.125 | 123.2529 | -61.4731 | 61.615 | 0.025705 | -0.040521 | -0.012 | -0.011281 | 0.008797 | -0.005985 | 0.010533 | 61.5188 | 0.14332 | 61.4638 | -0.055996 | 0.002454 | 61.5616 | -0.010593 | 61.4405 | 61.4988 | 61.4326 | 61.4611 | 61.4618 | 61.4819 | 61.4671 | 61.4836 | 122.9919 | 61.6164 | 122.9369 | 61.4171 | 61.4755 | 123.0347 | 61.4625 | 122.9136 | 61.5163 | 61.5294 | 61.4613 | 61.4744
139.0625 | 123.3444 | -61.441 | 61.5829 | 0.030283 | -0.0451 | -0.016578 | -0.006703 | 0.017953 | -0.005985 | 0.010533 | 61.5142 | 0.12958 | 61.3951 | -0.055996 | 0.01161 | 61.5616 | -0.010593 | 61.4588 | 61.4713 | 61.3959 | 61.4245 | 61.4343 | 61.459 | 61.4351 | 61.4516 | 122.9552 | 61.5706 | 122.8361 | 61.385 | 61.4526 | 123.0026 | 61.4304 | 122.8998 | 61.5026 | 61.5248 | 61.3835 | 61.4057
140.125 | 123.2849 | -61.4548 | 61.6196 | 0.030283 | -0.040521 | -0.021157 | -0.011281 | 0.022531 | -0.001406 | 0.010533 | 61.5188 | 0.13416 | 61.4638 | -0.060575 | 0.007032 | 61.5662 | -0.006014 | 61.4451 | 61.4851 | 61.4143 | 61.4336 | 61.4435 | 61.4773 | 61.4534 | 61.4653 | 122.9736 | 61.5889 | 122.9185 | 61.3942 | 61.4618 | 123.0209 | 61.4488 | 122.8998 | 61.5118 | 61.5248 | 61.4567 | 61.4698
141.0625 | 123.3307 | -61.4685 | 61.5967 | 0.030283 | -0.031363 | -0.007421 | -0.01586 | 0.017953 | 0.003172 | 0.01969 | 61.5142 | 0.12958 | 61.3951 | -0.060575 | 0.002454 | 61.5662 | -0.006014 | 61.4496 | 61.4988 | 61.4371 | 61.4611 | 61.4526 | 61.4865 | 61.4717 | 61.4882 | 122.9827 | 61.5981 | 122.8636 | 61.4079 | 61.471 | 123.0347 | 61.4625 | 122.9182 | 61.5118 | 61.5202 | 61.3926 | 61.4011
142.0625 | 123.3582 | -61.4639 | 61.5738 | 0.025705 | -0.040521 | -0.012 | -0.011281 | 0.013375 | -0.010563 | 0.015112 | 61.5279 | 0.13416 | 61.4592 | -0.055996 | 0.007032 | 61.5616 | -0.015171 | 61.4542 | 61.4896 | 61.4234 | 61.4519 | 61.4526 | 61.4773 | 61.4534 | 61.479 | 122.9919 | 61.5981 | 122.9231 | 61.4079 | 61.471 | 123.0255 | 61.4488 | 122.9182 | 61.5209 | 61.5431 | 61.4522 | 61.4744
143.125 | 123.3536 | -61.496 | 61.5784 | 0.034862 | -0.040521 | -0.016578 | -0.01586 | 0.013375 | -0.005985 | 0.015112 | 61.5188 | 0.13874 | 61.4043 | -0.055996 | 0.007032 | 61.5662 | -0.015171 | 61.4542 | 61.5308 | 61.4555 | 61.4794 | 61.4801 | 61.5093 | 61.49 | 61.5111 | 123.0148 | 61.6347 | 122.9002 | 61.44 | 61.503 | 123.0621 | 61.4808 | 122.9502 | 61.5118 | 61.534 | 61.3972 | 61.4194
144.0625 | 123.3398 | -61.4502 | 61.5646 | 0.025705 | -0.040521 | -0.016578 | -0.011281 | 0.008797 | -0.005985 | 0.015112 | 61.5142 | 0.14332 | 61.4409 | -0.051417 | 0.002454 | 61.5616 | -0.015171 | 61.4542 | 61.4759 | 61.4097 | 61.4336 | 61.4389 | 61.459 | 61.4442 | 61.4653 | 122.9644 | 61.5935 | 122.8911 | 61.3988 | 61.4526 | 123.0118 | 61.435 | 122.9044 | 61.5118 | 61.5294 | 61.4384 | 61.4561
145.0625 | 123.2986 | -61.4594 | 61.5967 | 0.021127 | -0.0451 | -0.021157 | -0.01586 | 0.013375 | -0.010563 | 0.005955 | 61.5234 | 0.12958 | 61.4455 | -0.055996 | -0.002124 | 61.5616 | -0.010593 | 61.4451 | 61.4805 | 61.4143 | 61.4382 | 61.4435 | 61.4727 | 61.4488 | 61.4653 | 122.9827 | 61.5889 | 122.9048 | 61.4034 | 61.4572 | 123.0209 | 61.4488 | 122.9044 | 61.5255 | 61.534 | 61.4476 | 61.4561
146.0625 | 123.3582 | -61.4594 | 61.5829 | 0.021127 | -0.0451 | -0.016578 | -0.011281 | 0.017953 | -0.005985 | 0.010533 | 61.5188 | 0.13416 | 61.4134 | -0.060575 | 0.01161 | 61.5524 | -0.006014 | 61.4451 | 61.4805 | 61.4143 | 61.4428 | 61.4481 | 61.4773 | 61.4534 | 61.4699 | 122.9781 | 61.5935 | 122.8728 | 61.3988 | 61.471 | 123.0118 | 61.4533 | 122.9044 | 61.5072 | 61.5248 | 61.4018 | 61.4194
147.0625 | 123.349 | -61.4868 | 61.5784 | 0.030283 | -0.040521 | -0.016578 | -0.006703 | 0.022531 | -0.001406 | 0.015112 | 61.5234 | 0.13416 | 61.4546 | -0.055996 | 0.002454 | 61.557 | -0.001436 | 61.4496 | 61.5171 | 61.4463 | 61.4702 | 61.4801 | 61.5093 | 61.4854 | 61.5019 | 123.0102 | 61.621 | 122.9414 | 61.4308 | 61.4893 | 123.0438 | 61.4854 | 122.9365 | 61.5209 | 61.5248 | 61.4522 | 61.4561
148.0625 | 123.4039 | -61.441 | 61.5921 | 0.025705 | -0.049678 | -0.021157 | -0.01586 | 0.013375 | -0.001406 | 0.015112 | 61.5096 | 0.13416 | 61.3951 | -0.051417 | 0.01161 | 61.557 | -0.010593 | 61.4496 | 61.4667 | 61.3914 | 61.4199 | 61.4252 | 61.4544 | 61.4396 | 61.4562 | 122.9507 | 61.5752 | 122.8361 | 61.3896 | 61.4526 | 122.998 | 61.4304 | 122.8907 | 61.498 | 61.5202 | 61.3835 | 61.4057
149.0625 | 123.3719 | -61.4227 | 61.5829 | 0.025705 | -0.040521 | -0.016578 | -0.01586 | 0.013375 | -0.001406 | 0.015112 | 61.5142 | 0.13416 | 61.4592 | -0.051417 | 0.01161 | 61.5524 | -0.010593 | 61.4451 | 61.4484 | 61.3822 | 61.4062 | 61.4069 | 61.4361 | 61.4213 | 61.4378 | 122.9369 | 61.5569 | 122.8819 | 61.3713 | 61.4343 | 122.9752 | 61.4121 | 122.8678 | 61.5026 | 61.5248 | 61.4476 | 61.4698
150.125 | 123.3124 | -61.4822 | 61.5921 | 0.021127 | -0.035942 | -0.012 | -0.006703 | 0.017953 | -0.001406 | 0.010533 | 61.5188 | 0.12958 | 61.4546 | -0.051417 | 0.002454 | 61.5616 | -0.010593 | 61.4451 | 61.5034 | 61.4463 | 61.4702 | 61.4755 | 61.5002 | 61.4808 | 61.4928 | 123.001 | 61.6118 | 122.9369 | 61.4308 | 61.4847 | 123.0438 | 61.4716 | 122.9273 | 61.5163 | 61.5294 | 61.4522 | 61.4652
151.0469 | 123.3078 | -61.4594 | 61.5829 | 0.025705 | -0.049678 | -0.012 | -0.025017 | 0.022531 | -0.015142 | 0.010533 | 61.5142 | 0.13416 | 61.3997 | -0.055996 | 0.002454 | 61.557 | -0.010593 | 61.4496 | 61.4851 | 61.4097 | 61.4474 | 61.4343 | 61.4819 | 61.4442 | 61.4699 | 122.9736 | 61.5935 | 122.859 | 61.4034 | 61.4618 | 123.0164 | 61.4488 | 122.909 | 61.5118 | 61.5248 | 61.3972 | 61.4103
152.0625 | 123.349 | -61.4639 | 61.5601 | 0.030283 | -0.035942 | -0.021157 | -0.01586 | 0.013375 | -0.010563 | 0.010533 | 61.5188 | 0.13416 | 61.4592 | -0.065154 | 0.016188 | 61.5524 | -0.010593 | 61.4451 | 61.4942 | 61.428 | 61.4428 | 61.4481 | 61.4773 | 61.4534 | 61.4745 | 122.9827 | 61.5981 | 122.9231 | 61.3988 | 61.4801 | 123.0164 | 61.4533 | 122.909 | 61.5026 | 61.5294 | 61.443 | 61.4698
153.0625 | 123.3078 | -61.4639 | 61.5784 | 0.025705 | -0.035942 | -0.016578 | -0.011281 | 0.008797 | 0.003172 | 0.015112 | 61.5142 | 0.13416 | 61.3951 | -0.060575 | 0.01161 | 61.5616 | -0.015171 | 61.4405 | 61.4896 | 61.428 | 61.4474 | 61.4526 | 61.4727 | 61.4671 | 61.479 | 122.9781 | 61.5981 | 122.859 | 61.4034 | 61.4755 | 123.0255 | 61.4488 | 122.9044 | 61.5026 | 61.5294 | 61.3835 | 61.4103
154.0625 | 123.3856 | -61.441 | 61.5875 | 0.030283 | -0.035942 | -0.016578 | -0.01586 | 0.013375 | -0.001406 | 0.015112 | 61.5234 | 0.12958 | 61.45 | -0.055996 | 0.007032 | 61.5616 | -0.001436 | 61.4451 | 61.4713 | 61.4051 | 61.4245 | 61.4252 | 61.4544 | 61.4396 | 61.4562 | 122.9644 | 61.5706 | 122.8911 | 61.385 | 61.4481 | 123.0026 | 61.4396 | 122.8861 | 61.5163 | 61.5248 | 61.443 | 61.4515
155.125 | 123.2986 | -61.441 | 61.6104 | 0.025705 | -0.040521 | -0.021157 | -0.01586 | 0.017953 | -0.015142 | 0.015112 | 61.5234 | 0.13874 | 61.45 | -0.060575 | 0.01161 | 61.5616 | -0.006014 | 61.4496 | 61.4667 | 61.4005 | 61.4199 | 61.4252 | 61.459 | 61.4259 | 61.4562 | 122.9644 | 61.5798 | 122.8911 | 61.3805 | 61.4526 | 123.0026 | 61.435 | 122.8907 | 61.5118 | 61.5294 | 61.4384 | 61.4561
156.0625 | 123.3444 | -61.4777 | 61.6013 | 0.016548 | -0.040521 | -0.012 | -0.011281 | 0.013375 | -0.005985 | 0.010533 | 61.5142 | 0.12958 | 61.3951 | -0.060575 | 0.002454 | 61.557 | -0.015171 | 61.4496 | 61.4942 | 61.4371 | 61.4657 | 61.4664 | 61.491 | 61.4717 | 61.4882 | 122.9919 | 61.6072 | 122.8728 | 61.4171 | 61.4801 | 123.0347 | 61.4625 | 122.9273 | 61.5118 | 61.5294 | 61.3926 | 61.4103
157.125 | 123.3719 | -61.4456 | 61.6013 | 0.021127 | -0.035942 | -0.016578 | -0.011281 | 0.017953 | -0.005985 | 0.015112 | 61.5188 | 0.13416 | 61.4592 | -0.051417 | 0.01161 | 61.5616 | -0.006014 | 61.4496 | 61.4667 | 61.4097 | 61.429 | 61.4343 | 61.4636 | 61.4396 | 61.4607 | 122.9644 | 61.5798 | 122.9048 | 61.3942 | 61.4572 | 123.0072 | 61.4396 | 122.8953 | 61.5072 | 61.5248 | 61.4476 | 61.4652
158.0625 | 123.317 | -61.4639 | 61.5692 | 0.025705 | -0.040521 | -0.016578 | -0.01586 | 0.013375 | -0.024298 | 0.015112 | 61.5096 | 0.13874 | 61.3997 | -0.060575 | 0.007032 | 61.557 | -0.010593 | 61.4451 | 61.4896 | 61.4234 | 61.4474 | 61.4481 | 61.4773 | 61.4396 | 61.479 | 122.9736 | 61.6027 | 122.8636 | 61.4034 | 61.471 | 123.0209 | 61.4533 | 122.909 | 61.5026 | 61.5202 | 61.3926 | 61.4103
159.0625 | 123.3124 | -61.4502 | 61.6196 | 0.030283 | -0.040521 | -0.021157 | -0.01586 | 0.013375 | 0.003172 | 0.015112 | 61.5142 | 0.13416 | 61.45 | -0.055996 | 0.01161 | 61.5616 | -0.010593 | 61.4451 | 61.4805 | 61.4097 | 61.429 | 61.4343 | 61.4636 | 61.4534 | 61.4653 | 122.9644 | 61.5844 | 122.9002 | 61.3942 | 61.4618 | 123.0118 | 61.4396 | 122.8953 | 61.5026 | 61.5248 | 61.4384 | 61.4606
160.125 | 123.3627 | -61.4731 | 61.5738 | 0.025705 | -0.040521 | -0.012 | -0.006703 | 0.017953 | -0.015142 | 0.005955 | 61.5142 | 0.13416 | 61.4546 | -0.060575 | 0.002454 | 61.557 | -0.010593 | 61.4451 | 61.4988 | 61.4326 | 61.4611 | 61.4664 | 61.491 | 61.4579 | 61.479 | 122.9873 | 61.6072 | 122.9277 | 61.4125 | 61.4755 | 123.0301 | 61.4625 | 122.9182 | 61.5118 | 61.5248 | 61.4522 | 61.4652
161.0625 | 123.3353 | -61.4456 | 61.5692 | 0.021127 | -0.0451 | -0.016578 | -0.011281 | 0.017953 | -0.015142 | 0.015112 | 61.5142 | 0.13416 | 61.4088 | -0.055996 | 0.002454 | 61.5616 | -0.010593 | 61.4405 | 61.4667 | 61.4005 | 61.429 | 61.4343 | 61.4636 | 61.4305 | 61.4607 | 122.9598 | 61.5798 | 122.8545 | 61.3896 | 61.4481 | 123.0072 | 61.435 | 122.8861 | 61.5118 | 61.5248 | 61.4064 | 61.4194
162.125 | 123.2803 | -61.4731 | 61.615 | 0.021127 | -0.035942 | -0.021157 | -0.011281 | 0.022531 | -0.005985 | 0.015112 | 61.5188 | 0.13416 | 61.4592 | -0.055996 | 0.01161 | 61.557 | -0.006014 | 61.4405 | 61.4942 | 61.4371 | 61.4519 | 61.4618 | 61.4956 | 61.4671 | 61.4882 | 122.9919 | 61.6072 | 122.9323 | 61.4171 | 61.4847 | 123.0301 | 61.4671 | 122.9136 | 61.5072 | 61.5248 | 61.4476 | 61.4652
163.0625 | 123.3261 | -61.4777 | 61.5784 | 0.021127 | -0.035942 | -0.016578 | -0.006703 | 0.013375 | -0.005985 | 0.010533 | 61.5142 | 0.13416 | 61.4043 | -0.060575 | 0.01161 | 61.5616 | -0.015171 | 61.4405 | 61.4988 | 61.4417 | 61.4611 | 61.471 | 61.491 | 61.4717 | 61.4882 | 122.9919 | 61.6118 | 122.8819 | 61.4171 | 61.4893 | 123.0392 | 61.4625 | 122.9182 | 61.5026 | 61.5294 | 61.3926 | 61.4194
164.0625 | 123.3398 | -61.4685 | 61.6287 | 0.030283 | -0.040521 | -0.016578 | -0.011281 | 0.022531 | -0.005985 | 0.015112 | 61.5234 | 0.13416 | 61.4592 | -0.055996 | 0.01161 | 61.557 | -0.001436 | 61.4542 | 61.4988 | 61.428 | 61.4519 | 61.4572 | 61.491 | 61.4625 | 61.4836 | 122.9919 | 61.6027 | 122.9277 | 61.4125 | 61.4801 | 123.0255 | 61.4671 | 122.9227 | 61.5118 | 61.5248 | 61.4476 | 61.4606
165.125 | 123.3582 | -61.4594 | 61.5555 | 0.025705 | -0.035942 | -0.016578 | -0.006703 | 0.027109 | -0.010563 | 0.015112 | 61.5188 | 0.14332 | 61.4546 | -0.060575 | 0.002454 | 61.557 | -0.006014 | 61.4451 | 61.4851 | 61.4234 | 61.4428 | 61.4526 | 61.4865 | 61.4488 | 61.4745 | 122.9781 | 61.6027 | 122.914 | 61.3988 | 61.4618 | 123.0164 | 61.4533 | 122.9044 | 61.5163 | 61.5248 | 61.4522 | 61.4606
166.0625 | 123.3719 | -61.4548 | 61.5555 | 0.030283 | -0.0451 | -0.016578 | -0.01586 | 0.013375 | -0.001406 | 0.015112 | 61.5188 | 0.13416 | 61.4043 | -0.051417 | 0.007032 | 61.557 | -0.001436 | 61.4451 | 61.4851 | 61.4097 | 61.4382 | 61.4389 | 61.4681 | 61.4534 | 61.4699 | 122.9736 | 61.5889 | 122.859 | 61.4034 | 61.4618 | 123.0118 | 61.4533 | 122.8998 | 61.5118 | 61.5202 | 61.3972 | 61.4057
167.125 | 123.3627 | -61.4639 | 61.5921 | 0.025705 | -0.035942 | -0.021157 | -0.002124 | 0.017953 | -0.005985 | 0.015112 | 61.5279 | 0.13874 | 61.4638 | -0.055996 | 0.007032 | 61.5616 | -0.010593 | 61.4496 | 61.4896 | 61.428 | 61.4428 | 61.4618 | 61.4819 | 61.4579 | 61.479 | 122.9919 | 61.6027 | 122.9277 | 61.4079 | 61.471 | 123.0255 | 61.4533 | 122.9136 | 61.5209 | 61.5385 | 61.4567 | 61.4744
168.0625 | 123.3078 | -61.4731 | 61.6379 | 0.021127 | -0.035942 | -0.025735 | -0.002124 | 0.017953 | -0.005985 | 0.010533 | 61.5142 | 0.13416 | 61.3951 | -0.055996 | 0.007032 | 61.5616 | -0.015171 | 61.4451 | 61.4942 | 61.4371 | 61.4473 | 61.471 | 61.491 | 61.4671 | 61.4836 | 122.9873 | 61.6072 | 122.8682 | 61.4171 | 61.4801 | 123.0347 | 61.4579 | 122.9182 | 61.5072 | 61.5294 | 61.3881 | 61.4103
169.0625 | 123.3124 | -61.4868 | 61.5829 | 0.021127 | -0.040521 | -0.021157 | -0.002124 | 0.022531 | -0.005985 | 0.015112 | 61.5188 | 0.14332 | 61.4592 | -0.051417 | 0.007032 | 61.5616 | -0.001436 | 61.4496 | 61.5079 | 61.4463 | 61.4657 | 61.4847 | 61.5093 | 61.4808 | 61.5019 | 123.0056 | 61.6301 | 122.946 | 61.4354 | 61.4938 | 123.0484 | 61.4854 | 122.9365 | 61.5118 | 61.5202 | 61.4522 | 61.4606
170.125 | 123.3673 | -61.4548 | 61.5646 | 0.021127 | -0.040521 | -0.016578 | -0.006703 | 0.017953 | -0.005985 | 0.010533 | 61.5188 | 0.13874 | 61.4226 | -0.065154 | 0.007032 | 61.5662 | -0.006014 | 61.4496 | 61.4759 | 61.4143 | 61.4382 | 61.4481 | 61.4727 | 61.4488 | 61.4653 | 122.9736 | 61.5935 | 122.8773 | 61.3896 | 61.4618 | 123.0209 | 61.4488 | 122.9044 | 61.5118 | 61.5248 | 61.4155 | 61.4286
171.0469 | 123.3398 | -61.4822 | 61.5601 | 0.025705 | -0.040521 | -0.021157 | -0.011281 | 0.017953 | 0.003172 | 0.015112 | 61.5142 | 0.12958 | 61.3997 | -0.055996 | 0.002454 | 61.5524 | -0.010593 | 61.4451 | 61.5079 | 61.4417 | 61.4611 | 61.471 | 61.5002 | 61.4854 | 61.4974 | 122.9964 | 61.6118 | 122.8819 | 61.4262 | 61.4847 | 123.0347 | 61.4716 | 122.9273 | 61.5118 | 61.5248 | 61.3972 | 61.4103
172.125 | 123.3078 | -61.4685 | 61.5829 | 0.025705 | -0.035942 | -0.012 | -0.011281 | 0.022531 | -0.005985 | 0.015112 | 61.5234 | 0.13416 | 61.4546 | -0.055996 | 0.007032 | 61.5616 | -0.006014 | 61.4496 | 61.4942 | 61.4326 | 61.4565 | 61.4572 | 61.491 | 61.4625 | 61.4836 | 122.9919 | 61.6027 | 122.9231 | 61.4125 | 61.4755 | 123.0301 | 61.4625 | 122.9182 | 61.5163 | 61.5294 | 61.4476 | 61.4606
173.0625 | 123.3856 | -61.4456 | 61.615 | 0.025705 | -0.035942 | -0.012 | -0.011281 | 0.017953 | -0.005985 | 0.015112 | 61.505 | 0.13416 | 61.3905 | -0.051417 | 0.002454 | 61.5662 | -0.010593 | 61.4496 | 61.4713 | 61.4097 | 61.4336 | 61.4343 | 61.4636 | 61.4396 | 61.4607 | 122.9507 | 61.5798 | 122.8361 | 61.3942 | 61.4481 | 123.0118 | 61.435 | 122.8953 | 61.5026 | 61.5156 | 61.3881 | 61.4011
174.0625 | 123.3536 | -61.4822 | 61.5784 | 0.025705 | -0.0451 | -0.012 | 0.002454 | 0.013375 | -0.010563 | 0.010533 | 61.5188 | 0.13874 | 61.45 | -0.065154 | 0.002454 | 61.5662 | -0.010593 | 61.4451 | 61.5079 | 61.4371 | 61.4702 | 61.4847 | 61.4956 | 61.4717 | 61.4928 | 123.001 | 61.621 | 122.9323 | 61.4171 | 61.4847 | 123.0484 | 61.4716 | 122.9273 | 61.5163 | 61.5294 | 61.4476 | 61.4606
175.125 | 123.381 | -61.4639 | 61.5738 | 0.025705 | -0.0451 | -0.016578 | -0.011281 | 0.017953 | -0.010563 | 0.010533 | 61.5234 | 0.13874 | 61.418 | -0.055996 | 0.007032 | 61.5524 | -0.010593 | 61.4451 | 61.4896 | 61.4188 | 61.4474 | 61.4526 | 61.4819 | 61.4534 | 61.4745 | 122.9873 | 61.6027 | 122.8819 | 61.4079 | 61.471 | 123.0164 | 61.4533 | 122.909 | 61.5163 | 61.534 | 61.411 | 61.4286
176.0625 | 123.3078 | -61.4639 | 61.5646 | 0.021127 | -0.035942 | -0.016578 | -0.011281 | 0.017953 | -0.010563 | 0.010533 | 61.5188 | 0.13874 | 61.418 | -0.055996 | 0.007032 | 61.5616 | -0.001436 | 61.4496 | 61.4851 | 61.428 | 61.4474 | 61.4526 | 61.4819 | 61.4534 | 61.4745 | 122.9827 | 61.6027 | 122.8819 | 61.4079 | 61.471 | 123.0255 | 61.4625 | 122.9136 | 61.5118 | 61.5202 | 61.411 | 61.4194
177.0625 | 123.3261 | -61.4594 | 61.5738 | 0.030283 | -0.035942 | -0.021157 | -0.002124 | 0.017953 | -0.005985 | 0.015112 | 61.5188 | 0.13874 | 61.4592 | -0.055996 | -0.002124 | 61.5616 | -0.006014 | 61.4451 | 61.4896 | 61.4234 | 61.4382 | 61.4572 | 61.4773 | 61.4534 | 61.4745 | 122.9781 | 61.5981 | 122.9185 | 61.4034 | 61.4572 | 123.0209 | 61.4533 | 122.9044 | 61.5209 | 61.5248 | 61.4613 | 61.4652
178.125 | 123.349 | -61.4594 | 61.5692 | 0.025705 | -0.040521 | -0.021157 | -0.011281 | 0.022531 | -0.010563 | 0.010533 | 61.5234 | 0.13874 | 61.3997 | -0.055996 | 0.002454 | 61.557 | -0.010593 | 61.4405 | 61.4851 | 61.4188 | 61.4382 | 61.4481 | 61.4819 | 61.4488 | 61.4699 | 122.9827 | 61.5981 | 122.859 | 61.4034 | 61.4618 | 123.0164 | 61.4488 | 122.8998 | 61.5209 | 61.534 | 61.3972 | 61.4103
179.0625 | 123.3582 | -61.4639 | 61.5875 | 0.025705 | -0.040521 | -0.021157 | -0.011281 | 0.013375 | -0.005985 | 0.015112 | 61.5279 | 0.14332 | 61.4546 | -0.065154 | 0.007032 | 61.5616 | -0.015171 | 61.4405 | 61.4896 | 61.4234 | 61.4428 | 61.4526 | 61.4773 | 61.4579 | 61.479 | 122.9919 | 61.6072 | 122.9185 | 61.3988 | 61.471 | 123.0255 | 61.4488 | 122.9044 | 61.5209 | 61.5431 | 61.4476 | 61.4698
180.125 | 123.3398 | -61.4548 | 61.5738 | 0.030283 | -0.040521 | -0.016578 | -0.011281 | 0.022531 | 0.003172 | 0.024268 | 61.5279 | 0.13416 | 61.4043 | -0.055996 | 0.002454 | 61.5616 | -0.006014 | 61.4359 | 61.4851 | 61.4143 | 61.4382 | 61.4435 | 61.4773 | 61.4579 | 61.479 | 122.9827 | 61.5889 | 122.859 | 61.3988 | 61.4572 | 123.0164 | 61.4488 | 122.8907 | 61.5255 | 61.534 | 61.4018 | 61.4103
181.0625 | 123.3353 | -61.4822 | 61.5738 | 0.030283 | -0.040521 | -0.016578 | -0.011281 | 0.013375 | -0.010563 | 0.010533 | 61.5188 | 0.14332 | 61.4088 | -0.065154 | 0.007032 | 61.5616 | -0.015171 | 61.4496 | 61.5125 | 61.4417 | 61.4657 | 61.471 | 61.4956 | 61.4717 | 61.4928 | 123.001 | 61.6256 | 122.8911 | 61.4171 | 61.4893 | 123.0438 | 61.4671 | 122.9319 | 61.5118 | 61.534 | 61.4018 | 61.424
182.0625 | 123.3215 | -61.496 | 61.6013 | 0.030283 | -0.040521 | -0.016578 | -0.006703 | 0.027109 | -0.005985 | 0.010533 | 61.5234 | 0.12958 | 61.4546 | -0.055996 | -0.002124 | 61.5662 | -0.010593 | 61.4451 | 61.5263 | 61.4555 | 61.4794 | 61.4893 | 61.5231 | 61.49 | 61.5065 | 123.0193 | 61.6256 | 122.9506 | 61.44 | 61.4938 | 123.0621 | 61.4854 | 122.941 | 61.5255 | 61.534 | 61.4567 | 61.4652
183.0625 | 123.317 | -61.4639 | 61.5875 | 0.025705 | -0.035942 | -0.012 | -0.011281 | 0.017953 | -0.005985 | 0.01969 | 61.5188 | 0.13416 | 61.3951 | -0.055996 | 0.007032 | 61.5616 | -0.006014 | 61.4496 | 61.4896 | 61.428 | 61.4519 | 61.4526 | 61.4819 | 61.4579 | 61.4836 | 122.9827 | 61.5981 | 122.859 | 61.4079 | 61.471 | 123.0255 | 61.4579 | 122.9136 | 61.5118 | 61.5248 | 61.3881 | 61.4011
184.1406 | 123.2803 | -61.4822 | 61.6516 | 0.030283 | -0.040521 | -0.016578 | -0.006703 | 0.017953 | -0.005985 | 0.015112 | 61.5142 | 0.13874 | 61.4592 | -0.051417 | -0.002124 | 61.557 | 0.003143 | 61.4405 | 61.5125 | 61.4417 | 61.4657 | 61.4755 | 61.5002 | 61.4763 | 61.4974 | 122.9964 | 61.621 | 122.9414 | 61.4308 | 61.4801 | 123.0392 | 61.4854 | 122.9227 | 61.5163 | 61.5111 | 61.4613 | 61.4561
185.0469 | 123.3856 | -61.4685 | 61.5601 | 0.021127 | -0.040521 | -0.016578 | -0.01586 | 0.017953 | -0.001406 | 0.01969 | 61.5234 | 0.13874 | 61.4271 | -0.065154 | 0.002454 | 61.5662 | -0.006014 | 61.4451 | 61.4896 | 61.428 | 61.4519 | 61.4526 | 61.4865 | 61.4671 | 61.4882 | 122.9919 | 61.6072 | 122.8957 | 61.4034 | 61.471 | 123.0347 | 61.4625 | 122.9136 | 61.5209 | 61.5294 | 61.4247 | 61.4332
186.0625 | 123.349 | -61.4777 | 61.5646 | 0.025705 | -0.026784 | -0.016578 | -0.006703 | 0.013375 | -0.010563 | 0.010533 | 61.5142 | 0.13874 | 61.3997 | -0.055996 | 0.007032 | 61.5616 | -0.010593 | 61.4451 | 61.5034 | 61.4509 | 61.4611 | 61.471 | 61.491 | 61.4671 | 61.4882 | 122.9919 | 61.6164 | 122.8773 | 61.4217 | 61.4847 | 123.0392 | 61.4671 | 122.9227 | 61.5072 | 61.5248 | 61.3926 | 61.4103
187.0625 | 123.3124 | -61.4822 | 61.5143 | 0.025705 | -0.040521 | -0.021157 | -0.006703 | 0.008797 | -0.005985 | 0.010533 | 61.5234 | 0.14332 | 61.4592 | -0.055996 | 0.002454 | 61.5524 | -0.010593 | 61.4496 | 61.5079 | 61.4417 | 61.4611 | 61.4755 | 61.491 | 61.4763 | 61.4928 | 123.0056 | 61.6256 | 122.9414 | 61.4262 | 61.4847 | 123.0347 | 61.4716 | 122.9319 | 61.5209 | 61.534 | 61.4567 | 61.4698
188.0625 | 123.349 | -61.4639 | 61.5601 | 0.030283 | -0.035942 | -0.021157 | -0.011281 | 0.013375 | -0.010563 | 0.015112 | 61.5142 | 0.14332 | 61.3997 | -0.060575 | 0.002454 | 61.5616 | -0.006014 | 61.4405 | 61.4942 | 61.428 | 61.4428 | 61.4526 | 61.4773 | 61.4534 | 61.479 | 122.9781 | 61.6072 | 122.8636 | 61.4034 | 61.4664 | 123.0255 | 61.4579 | 122.9044 | 61.5118 | 61.5202 | 61.3972 | 61.4057
189.1406 | 123.3582 | -61.4273 | 61.6058 | 0.030283 | -0.040521 | -0.016578 | -0.011281 | 0.017953 | -0.001406 | 0.01969 | 61.5234 | 0.13874 | 61.4043 | -0.055996 | 0.002454 | 61.5662 | -0.010593 | 61.4588 | 61.4576 | 61.3868 | 61.4107 | 61.416 | 61.4453 | 61.4259 | 61.447 | 122.9507 | 61.566 | 122.8316 | 61.3713 | 61.4298 | 122.9935 | 61.4167 | 122.8861 | 61.5209 | 61.534 | 61.4018 | 61.4149
190.0625 | 123.2437 | -61.4685 | 61.6379 | 0.030283 | -0.035942 | -0.007421 | -0.006703 | 0.022531 | 0.00775 | 0.015112 | 61.5279 | 0.14332 | 61.4684 | -0.055996 | 0.007032 | 61.5662 | -0.010593 | 61.4451 | 61.4988 | 61.4326 | 61.4611 | 61.4618 | 61.491 | 61.4763 | 61.4836 | 122.9964 | 61.6118 | 122.9369 | 61.4125 | 61.4755 | 123.0347 | 61.4579 | 122.9136 | 61.5209 | 61.5385 | 61.4613 | 61.4789
191.0625 | 123.2437 | -61.4731 | 61.6013 | 0.030283 | -0.035942 | -0.012 | -0.011281 | 0.017953 | -0.001406 | 0.015112 | 61.5279 | 0.13416 | 61.4134 | -0.060575 | 0.002454 | 61.5616 | -0.015171 | 61.4496 | 61.5034 | 61.4371 | 61.4611 | 61.4618 | 61.491 | 61.4717 | 61.4882 | 123.001 | 61.6072 | 122.8865 | 61.4125 | 61.4755 | 123.0347 | 61.4579 | 122.9227 | 61.5255 | 61.5431 | 61.411 | 61.4286
192.125 | 123.3398 | -61.4594 | 61.5601 | 0.016548 | -0.040521 | -0.012 | -0.006703 | 0.022531 | -0.001406 | 0.005955 | 61.5096 | 0.14332 | 61.3951 | -0.051417 | -0.002124 | 61.5616 | -0.010593 | 61.4496 | 61.4759 | 61.4188 | 61.4474 | 61.4526 | 61.4819 | 61.4579 | 61.4653 | 122.969 | 61.6027 | 122.8545 | 61.4079 | 61.4572 | 123.0209 | 61.4488 | 122.909 | 61.5118 | 61.5202 | 61.3972 | 61.4057
193.0625 | 123.3398 | -61.4639 | 61.5417 | 0.030283 | -0.040521 | -0.016578 | -0.01586 | 0.022531 | -0.005985 | 0.015112 | 61.5234 | 0.13416 | 61.4592 | -0.055996 | 0.01161 | 61.5616 | -0.006014 | 61.4451 | 61.4942 | 61.4234 | 61.4474 | 61.4481 | 61.4865 | 61.4579 | 61.479 | 122.9873 | 61.5981 | 122.9231 | 61.4079 | 61.4755 | 123.0255 | 61.4579 | 122.909 | 61.5118 | 61.5294 | 61.4476 | 61.4652
194.1406 | 123.3124 | -61.4777 | 61.6196 | 0.021127 | -0.040521 | -0.016578 | -0.011281 | 0.022531 | -0.005985 | 0.010533 | 61.5234 | 0.13416 | 61.4684 | -0.051417 | 0.007032 | 61.5616 | -0.006014 | 61.4588 | 61.4988 | 61.4371 | 61.4611 | 61.4664 | 61.5002 | 61.4717 | 61.4882 | 123.001 | 61.6118 | 122.946 | 61.4262 | 61.4847 | 123.0392 | 61.4716 | 122.9365 | 61.5163 | 61.5294 | 61.4613 | 61.4744
195.0625 | 123.349 | -61.4685 | 61.5601 | 0.025705 | -0.0451 | -0.012 | -0.020438 | 0.022531 | -0.010563 | 0.01969 | 61.5234 | 0.13416 | 61.3951 | -0.051417 | 0.016188 | 61.557 | -0.010593 | 61.4496 | 61.4942 | 61.4234 | 61.4565 | 61.4481 | 61.491 | 61.4579 | 61.4882 | 122.9919 | 61.6027 | 122.8636 | 61.4171 | 61.4847 | 123.0255 | 61.4579 | 122.9182 | 61.5072 | 61.534 | 61.3789 | 61.4057
196.125 | 123.3536 | -61.4548 | 61.5417 | 0.030283 | -0.040521 | -0.016578 | -0.006703 | 0.017953 | -0.001406 | 0.01969 | 61.5142 | 0.14332 | 61.4043 | -0.065154 | 0.007032 | 61.557 | -0.015171 | 61.4405 | 61.4851 | 61.4143 | 61.4382 | 61.4481 | 61.4727 | 61.4534 | 61.4745 | 122.969 | 61.5981 | 122.859 | 61.3896 | 61.4618 | 123.0118 | 61.4396 | 122.8953 | 61.5072 | 61.5294 | 61.3972 | 61.4194
197.0625 | 123.2346 | -61.4822 | 61.6196 | 0.030283 | -0.040521 | -0.012 | -0.006703 | 0.022531 | -0.001406 | 0.015112 | 61.5279 | 0.14332 | 61.4638 | -0.055996 | 0.007032 | 61.557 | -0.006014 | 61.4451 | 61.5125 | 61.4417 | 61.4702 | 61.4755 | 61.5048 | 61.4808 | 61.4974 | 123.0102 | 61.6256 | 122.946 | 61.4262 | 61.4893 | 123.0392 | 61.4762 | 122.9273 | 61.5209 | 61.534 | 61.4567 | 61.4698
198.125 | 123.3261 | -61.4731 | 61.5738 | 0.021127 | -0.040521 | -0.016578 | -0.011281 | 0.017953 | -0.001406 | 0.015112 | 61.5279 | 0.13874 | 61.4455 | -0.055996 | -0.002124 | 61.557 | -0.006014 | 61.4451 | 61.4942 | 61.4326 | 61.4565 | 61.4618 | 61.491 | 61.4717 | 61.4882 | 123.001 | 61.6118 | 122.9185 | 61.4171 | 61.471 | 123.0301 | 61.4671 | 122.9182 | 61.5301 | 61.534 | 61.4476 | 61.4515
199.0625 | 123.3536 | -61.441 | 61.5784 | 0.030283 | -0.035942 | -0.016578 | -0.011281 | 0.013375 | -0.005985 | 0.015112 | 61.5188 | 0.1479 | 61.3997 | -0.051417 | 0.01161 | 61.5616 | -0.006014 | 61.4588 | 61.4713 | 61.4051 | 61.4245 | 61.4298 | 61.4544 | 61.4351 | 61.4562 | 122.9598 | 61.5889 | 122.8407 | 61.3896 | 61.4526 | 123.0026 | 61.435 | 122.8998 | 61.5072 | 61.5248 | 61.3881 | 61.4057
200.0625 | 123.3627 | -61.4777 | 61.5921 | 0.025705 | -0.040521 | -0.016578 | -0.011281 | 0.022531 | -0.001406 | 0.015112 | 61.5142 | 0.1479 | 61.4546 | -0.055996 | 0.01161 | 61.5616 | -0.010593 | 61.4496 | 61.5034 | 61.4371 | 61.4611 | 61.4664 | 61.5002 | 61.4763 | 61.4928 | 122.9919 | 61.6256 | 122.9323 | 61.4217 | 61.4893 | 123.0392 | 61.4671 | 122.9273 | 61.5026 | 61.5248 | 61.443 | 61.4652
201.125 | 123.2254 | -61.4822 | 61.615 | 0.025705 | -0.035942 | -0.016578 | -0.011281 | 0.022531 | -0.005985 | 0.010533 | 61.5234 | 0.13874 | 61.4226 | -0.055996 | 0.002454 | 61.5616 | -0.015171 | 61.4451 | 61.5079 | 61.4463 | 61.4657 | 61.471 | 61.5048 | 61.4763 | 61.4928 | 123.0056 | 61.621 | 122.9048 | 61.4262 | 61.4847 | 123.0438 | 61.4671 | 122.9273 | 61.5209 | 61.5385 | 61.4201 | 61.4377
202.0625 | 123.2483 | -61.4914 | 61.6013 | 0.021127 | -0.035942 | -0.012 | -0.002124 | 0.017953 | -0.001406 | 0.01969 | 61.5234 | 0.13416 | 61.418 | -0.055996 | 0.007032 | 61.5616 | -0.010593 | 61.4451 | 61.5125 | 61.4555 | 61.4794 | 61.4893 | 61.5093 | 61.49 | 61.5111 | 123.0148 | 61.6256 | 122.9094 | 61.4354 | 61.4984 | 123.053 | 61.4808 | 122.9365 | 61.5163 | 61.534 | 61.411 | 61.4286
203.125 | 123.317 | -61.4639 | 61.5875 | 0.021127 | -0.035942 | -0.016578 | -0.011281 | 0.027109 | -0.005985 | 0.001377 | 61.5188 | 0.13874 | 61.4455 | -0.060575 | 0.01161 | 61.557 | -0.006014 | 61.4451 | 61.4851 | 61.428 | 61.4474 | 61.4526 | 61.491 | 61.4579 | 61.4653 | 122.9827 | 61.6027 | 122.9094 | 61.4034 | 61.4755 | 123.0209 | 61.4579 | 122.909 | 61.5072 | 61.5248 | 61.4339 | 61.4515
204.0625 | 123.349 | -61.4731 | 61.5692 | 0.030283 | -0.0451 | -0.012 | -0.011281 | 0.013375 | -0.005985 | 0.010533 | 61.5142 | 0.13874 | 61.4043 | -0.065154 | 0.002454 | 61.557 | -0.006014 | 61.4359 | 61.5034 | 61.428 | 61.4611 | 61.4618 | 61.4865 | 61.4671 | 61.4836 | 122.9873 | 61.6118 | 122.8773 | 61.4079 | 61.4755 | 123.0301 | 61.4671 | 122.909 | 61.5118 | 61.5202 | 61.4018 | 61.4103
205.125 | 123.2986 | -61.4822 | 61.5921 | 0.030283 | -0.035942 | -0.012 | -0.011281 | 0.022531 | -0.005985 | 0.010533 | 61.5142 | 0.14332 | 61.418 | -0.060575 | 0.002454 | 61.5616 | -0.006014 | 61.4405 | 61.5125 | 61.4463 | 61.4702 | 61.471 | 61.5048 | 61.4763 | 61.4928 | 122.9964 | 61.6256 | 122.9002 | 61.4217 | 61.4847 | 123.0438 | 61.4762 | 122.9227 | 61.5118 | 61.5202 | 61.4155 | 61.424
206.0625 | 123.3307 | -61.4685 | 61.5784 | 0.025705 | -0.031363 | -0.016578 | -0.006703 | 0.017953 | -0.010563 | 0.01969 | 61.5279 | 0.13874 | 61.4546 | -0.055996 | 0.007032 | 61.5662 | -0.010593 | 61.4405 | 61.4942 | 61.4371 | 61.4519 | 61.4618 | 61.4865 | 61.4579 | 61.4882 | 122.9964 | 61.6072 | 122.9231 | 61.4125 | 61.4755 | 123.0347 | 61.4579 | 122.909 | 61.5209 | 61.5385 | 61.4476 | 61.4652
207.125 | 123.2162 | -61.5189 | 61.6058 | 0.030283 | -0.031363 | -0.021157 | -0.006703 | 0.017953 | -0.001406 | 0.01969 | 61.5234 | 0.13874 | 61.418 | -0.060575 | 0.01161 | 61.5662 | -0.010593 | 61.4451 | 61.5491 | 61.4875 | 61.4977 | 61.5122 | 61.5368 | 61.5175 | 61.5385 | 123.0422 | 61.6576 | 122.9369 | 61.4583 | 61.5305 | 123.085 | 61.5083 | 122.9639 | 61.5118 | 61.534 | 61.4064 | 61.4286
208.0625 | 123.1979 | -61.4822 | 61.6196 | 0.025705 | -0.040521 | -0.021157 | -0.011281 | 0.017953 | -0.001406 | 0.015112 | 61.5188 | 0.13416 | 61.4043 | -0.051417 | 0.01161 | 61.5707 | 0.003143 | 61.4405 | 61.5079 | 61.4417 | 61.4611 | 61.471 | 61.5002 | 61.4808 | 61.4974 | 123.001 | 61.6164 | 122.8865 | 61.4308 | 61.4938 | 123.053 | 61.4854 | 122.9227 | 61.5072 | 61.5156 | 61.3926 | 61.4011
209.1406 | 123.317 | -61.4594 | 61.5829 | 0.025705 | -0.035942 | -0.016578 | -0.006703 | 0.017953 | -0.001406 | 0.015112 | 61.5279 | 0.13874 | 61.4546 | -0.055996 | 0.007032 | 61.5662 | -0.006014 | 61.4496 | 61.4851 | 61.4234 | 61.4428 | 61.4526 | 61.4773 | 61.4579 | 61.4745 | 122.9873 | 61.5981 | 122.914 | 61.4034 | 61.4664 | 123.0255 | 61.4533 | 122.909 | 61.5209 | 61.534 | 61.4476 | 61.4606
210.0625 | 123.2712 | -61.4731 | 61.6287 | 0.021127 | -0.035942 | -0.012 | 0.002454 | 0.022531 | -0.005985 | 0.01969 | 61.5279 | 0.13416 | 61.4684 | -0.055996 | 0.007032 | 61.5662 | -0.010593 | 61.4451 | 61.4942 | 61.4371 | 61.4611 | 61.4755 | 61.4956 | 61.4671 | 61.4928 | 123.001 | 61.6072 | 122.9414 | 61.4171 | 61.4801 | 123.0392 | 61.4625 | 122.9182 | 61.5209 | 61.5385 | 61.4613 | 61.4789
211.0625 | 123.2025 | -61.5005 | 61.615 | 0.030283 | -0.040521 | -0.012 | -0.002124 | 0.013375 | -0.005985 | 0.01969 | 61.5234 | 0.13874 | 61.4043 | -0.046838 | 0.007032 | 61.5662 | -0.006014 | 61.4451 | 61.5308 | 61.46 | 61.4885 | 61.4984 | 61.5139 | 61.4946 | 61.5202 | 123.0239 | 61.6393 | 122.9048 | 61.4537 | 61.5076 | 123.0667 | 61.4945 | 122.9456 | 61.5163 | 61.5294 | 61.3972 | 61.4103
212.125 | 123.2071 | -61.496 | 61.6196 | 0.016548 | -0.049678 | -0.012 | -0.002124 | 0.017953 | -0.001406 | 0.01969 | 61.5188 | 0.13874 | 61.4271 | -0.055996 | 0.007032 | 61.557 | -0.006014 | 61.4451 | 61.5125 | 61.4463 | 61.484 | 61.4938 | 61.5139 | 61.4946 | 61.5157 | 123.0148 | 61.6347 | 122.9231 | 61.44 | 61.503 | 123.053 | 61.49 | 122.941 | 61.5118 | 61.5248 | 61.4201 | 61.4332
213.0469 | 123.2025 | -61.5005 | 61.6058 | 0.030283 | -0.035942 | -0.012 | -0.006703 | 0.022531 | -0.010563 | 0.01969 | 61.5371 | 0.14332 | 61.4684 | -0.046838 | -0.002124 | 61.5616 | -0.001436 | 61.4496 | 61.5308 | 61.4646 | 61.4885 | 61.4938 | 61.5231 | 61.49 | 61.5202 | 123.0376 | 61.6439 | 122.9689 | 61.4537 | 61.4984 | 123.0621 | 61.4991 | 122.9502 | 61.5392 | 61.5385 | 61.4705 | 61.4698
214.0625 | 123.3536 | -61.4731 | 61.5509 | 0.025705 | -0.035942 | -0.016578 | -0.002124 | 0.022531 | -0.015142 | 0.005955 | 61.5234 | 0.13874 | 61.418 | -0.065154 | 0.007032 | 61.5616 | -0.010593 | 61.4496 | 61.4988 | 61.4371 | 61.4565 | 61.471 | 61.4956 | 61.4579 | 61.479 | 122.9964 | 61.6118 | 122.8911 | 61.4079 | 61.4801 | 123.0347 | 61.4625 | 122.9227 | 61.5163 | 61.534 | 61.411 | 61.4286
215.0625 | 123.2117 | -61.496 | 61.5829 | 0.030283 | -0.031363 | -0.012 | -0.011281 | 0.017953 | -0.005985 | 0.015112 | 61.5234 | 0.13874 | 61.4134 | -0.065154 | 0.007032 | 61.5616 | -0.010593 | 61.4496 | 61.5263 | 61.4646 | 61.484 | 61.4847 | 61.5139 | 61.49 | 61.5111 | 123.0193 | 61.6347 | 122.9094 | 61.4308 | 61.503 | 123.0576 | 61.4854 | 122.9456 | 61.5163 | 61.534 | 61.4064 | 61.424
216.125 | 123.2712 | -61.5005 | 61.6333 | 0.030283 | -0.040521 | -0.016578 | -0.002124 | 0.022531 | -0.005985 | 0.005955 | 61.5325 | 0.14332 | 61.4684 | -0.060575 | 0.007032 | 61.5616 | -0.001436 | 61.4451 | 61.5308 | 61.46 | 61.484 | 61.4984 | 61.5231 | 61.4946 | 61.5065 | 123.0331 | 61.6439 | 122.9689 | 61.44 | 61.5076 | 123.0621 | 61.4991 | 122.9456 | 61.5255 | 61.534 | 61.4613 | 61.4698
217.0625 | 123.3032 | -61.4548 | 61.6058 | 0.030283 | -0.040521 | -0.012 | -0.006703 | 0.017953 | -0.001406 | 0.024268 | 61.5279 | 0.13416 | 61.45 | -0.060575 | 0.016188 | 61.5616 | -0.010593 | 61.4451 | 61.4851 | 61.4143 | 61.4428 | 61.4481 | 61.4727 | 61.4534 | 61.479 | 122.9827 | 61.5889 | 122.9048 | 61.3942 | 61.471 | 123.0164 | 61.4442 | 122.8998 | 61.5118 | 61.5385 | 61.4339 | 61.4606
218.125 | 123.2254 | -61.4914 | 61.6013 | 0.016548 | -0.031363 | -0.016578 | -0.01586 | 0.017953 | -0.001406 | 0.01969 | 61.5234 | 0.14332 | 61.4043 | -0.060575 | 0.007032 | 61.5662 | -0.010593 | 61.4451 | 61.5079 | 61.46 | 61.4748 | 61.4755 | 61.5093 | 61.49 | 61.5111 | 123.0148 | 61.6347 | 122.8957 | 61.4308 | 61.4984 | 123.0576 | 61.4808 | 122.9365 | 61.5163 | 61.534 | 61.3972 | 61.4149
219.0625 | 123.317 | -61.4639 | 61.5601 | 0.025705 | -0.031363 | -0.012 | -0.002124 | 0.022531 | -0.005985 | 0.01969 | 61.5234 | 0.13874 | 61.4271 | -0.051417 | 0.007032 | 61.557 | -0.006014 | 61.4451 | 61.4896 | 61.4326 | 61.4519 | 61.4618 | 61.4865 | 61.4579 | 61.4836 | 122.9873 | 61.6027 | 122.8911 | 61.4125 | 61.471 | 123.0209 | 61.4579 | 122.909 | 61.5163 | 61.5294 | 61.4201 | 61.4332
220.125 | 123.2712 | -61.4685 | 61.6379 | 0.030283 | -0.026784 | -0.012 | -0.002124 | 0.017953 | -0.001406 | 0.01969 | 61.5371 | 0.1479 | 61.4729 | -0.065154 | 0.01161 | 61.5616 | -0.015171 | 61.4451 | 61.4988 | 61.4417 | 61.4565 | 61.4664 | 61.4865 | 61.4671 | 61.4882 | 123.0056 | 61.6164 | 122.9414 | 61.4034 | 61.4801 | 123.0301 | 61.4533 | 122.9136 | 61.5255 | 61.5523 | 61.4613 | 61.4881
221.0625 | 123.2758 | -61.4731 | 61.6104 | 0.021127 | -0.040521 | -0.012 | -0.01586 | 0.022531 | -0.010563 | 0.01969 | 61.5234 | 0.14332 | 61.4043 | -0.055996 | 0.016188 | 61.5662 | -0.010593 | 61.4451 | 61.4942 | 61.4326 | 61.4611 | 61.4572 | 61.4956 | 61.4625 | 61.4928 | 122.9964 | 61.6164 | 122.8773 | 61.4171 | 61.4893 | 123.0392 | 61.4625 | 122.9182 | 61.5072 | 61.534 | 61.3881 | 61.4149
222.0625 | 123.262 | -61.4502 | 61.6058 | 0.030283 | -0.031363 | -0.012 | -0.006703 | 0.022531 | -0.005985 | 0.024268 | 61.5279 | 0.13874 | 61.4729 | -0.046838 | 0.007032 | 61.5616 | -0.001436 | 61.4496 | 61.4805 | 61.4188 | 61.4382 | 61.4435 | 61.4727 | 61.4442 | 61.4745 | 122.9781 | 61.5889 | 122.9231 | 61.4034 | 61.4572 | 123.0118 | 61.4488 | 122.8998 | 61.5209 | 61.5294 | 61.4659 | 61.4744
223.125 | 123.2574 | -61.4685 | 61.6196 | 0.030283 | -0.031363 | -0.021157 | -0.002124 | 0.022531 | 0.003172 | 0.01969 | 61.5234 | 0.14332 | 61.418 | -0.055996 | 0.007032 | 61.557 | -0.006014 | 61.4451 | 61.4988 | 61.4371 | 61.4473 | 61.4664 | 61.491 | 61.4717 | 61.4882 | 122.9919 | 61.6118 | 122.8865 | 61.4125 | 61.4755 | 123.0255 | 61.4625 | 122.9136 | 61.5163 | 61.5294 | 61.411 | 61.424
224.0625 | 123.2529 | -61.4868 | 61.6241 | 0.034862 | -0.040521 | -0.021157 | -0.006703 | 0.017953 | -0.010563 | 0.01969 | 61.5234 | 0.14332 | 61.4271 | -0.055996 | 0.01161 | 61.5616 | -0.010593 | 61.4405 | 61.5217 | 61.4463 | 61.4657 | 61.4801 | 61.5048 | 61.4763 | 61.5065 | 123.0102 | 61.6301 | 122.914 | 61.4308 | 61.4984 | 123.0484 | 61.4762 | 122.9273 | 61.5118 | 61.534 | 61.4155 | 61.4377
225.125 | 123.262 | -61.4868 | 61.6287 | 0.034862 | -0.035942 | -0.016578 | -0.011281 | 0.017953 | -0.001406 | 0.015112 | 61.5325 | 0.13874 | 61.4684 | -0.060575 | 0.01161 | 61.5662 | -0.001436 | 61.4496 | 61.5217 | 61.4509 | 61.4702 | 61.4755 | 61.5048 | 61.4854 | 61.5019 | 123.0193 | 61.6256 | 122.9552 | 61.4262 | 61.4984 | 123.053 | 61.4854 | 122.9365 | 61.5209 | 61.534 | 61.4567 | 61.4698
226.0625 | 123.2529 | -61.4594 | 61.6058 | 0.030283 | -0.035942 | -0.016578 | -0.006703 | 0.027109 | -0.001406 | 0.024268 | 61.5234 | 0.13874 | 61.4226 | -0.055996 | 0.007032 | 61.5616 | -0.010593 | 61.4451 | 61.4896 | 61.4234 | 61.4428 | 61.4526 | 61.4865 | 61.4579 | 61.4836 | 122.9827 | 61.5981 | 122.8819 | 61.4034 | 61.4664 | 123.0209 | 61.4488 | 122.9044 | 61.5163 | 61.534 | 61.4155 | 61.4332
227.125 | 123.2574 | -61.4731 | 61.6104 | 0.030283 | -0.040521 | -0.016578 | -0.006703 | 0.017953 | 0.003172 | 0.01969 | 61.5234 | 0.12958 | 61.3951 | -0.055996 | 0.007032 | 61.557 | -0.006014 | 61.4451 | 61.5034 | 61.4326 | 61.4565 | 61.4664 | 61.491 | 61.4763 | 61.4928 | 122.9964 | 61.6027 | 122.8682 | 61.4171 | 61.4801 | 123.0301 | 61.4671 | 122.9182 | 61.5163 | 61.5294 | 61.3881 | 61.4011
228.0625 | 123.262 | -61.4731 | 61.6104 | 0.025705 | -0.031363 | -0.021157 | -0.006703 | 0.027109 | -0.010563 | 0.01969 | 61.5371 | 0.13874 | 61.4638 | -0.055996 | 0.016188 | 61.5616 | -0.001436 | 61.4496 | 61.4988 | 61.4417 | 61.4519 | 61.4664 | 61.5002 | 61.4625 | 61.4928 | 123.0102 | 61.6118 | 122.9369 | 61.4171 | 61.4893 | 123.0347 | 61.4716 | 122.9227 | 61.5209 | 61.5385 | 61.4476 | 61.4652
229.0625 | 123.2895 | -61.5189 | 61.5829 | 0.030283 | -0.026784 | -0.012 | -0.002124 | 0.017953 | -0.001406 | 0.015112 | 61.5234 | 0.14332 | 61.4684 | -0.051417 | 0.007032 | 61.5662 | -0.006014 | 61.4451 | 61.5491 | 61.4921 | 61.5069 | 61.5167 | 61.5368 | 61.5175 | 61.534 | 123.0422 | 61.6622 | 122.9872 | 61.4674 | 61.5259 | 123.085 | 61.5128 | 122.9639 | 61.5163 | 61.5294 | 61.4613 | 61.4744
230.125 | 123.2712 | -61.4685 | 61.5967 | 0.025705 | -0.031363 | -0.016578 | -0.006703 | 0.017953 | 0.003172 | 0.015112 | 61.5234 | 0.13874 | 61.4088 | -0.055996 | 0.01161 | 61.557 | -0.006014 | 61.4451 | 61.4942 | 61.4371 | 61.4519 | 61.4618 | 61.4865 | 61.4717 | 61.4836 | 122.9919 | 61.6072 | 122.8773 | 61.4125 | 61.4801 | 123.0255 | 61.4625 | 122.9136 | 61.5118 | 61.5294 | 61.3972 | 61.4149
231.0625 | 123.1979 | -61.4822 | 61.6287 | 0.030283 | -0.035942 | -0.012 | -0.011281 | 0.022531 | -0.010563 | 0.01969 | 61.5279 | 0.14332 | 61.418 | -0.055996 | 0.01161 | 61.5616 | -0.015171 | 61.4496 | 61.5125 | 61.4463 | 61.4702 | 61.471 | 61.5048 | 61.4717 | 61.5019 | 123.0102 | 61.6256 | 122.9002 | 61.4262 | 61.4938 | 123.0438 | 61.4671 | 122.9319 | 61.5163 | 61.5431 | 61.4064 | 61.4332
232.125 | 123.262 | -61.4822 | 61.6287 | 0.021127 | -0.035942 | -0.021157 | -0.006703 | 0.022531 | -0.001406 | 0.010533 | 61.5325 | 0.13874 | 61.4684 | -0.055996 | 0.007032 | 61.557 | -0.015171 | 61.4359 | 61.5034 | 61.4463 | 61.4611 | 61.4755 | 61.5048 | 61.4808 | 61.4928 | 123.0148 | 61.621 | 122.9506 | 61.4262 | 61.4893 | 123.0392 | 61.4671 | 122.9182 | 61.5255 | 61.5477 | 61.4613 | 61.4835
233.0469 | 123.2574 | -61.5005 | 61.6013 | 0.034862 | -0.035942 | -0.012 | -0.006703 | 0.022531 | -0.001406 | 0.01969 | 61.5371 | 0.13416 | 61.4226 | -0.055996 | 0.01161 | 61.5662 | -0.015171 | 61.4496 | 61.5354 | 61.4646 | 61.4885 | 61.4938 | 61.5231 | 61.4991 | 61.5202 | 123.0376 | 61.6347 | 122.9231 | 61.4446 | 61.5122 | 123.0667 | 61.4854 | 122.9502 | 61.5255 | 61.5523 | 61.411 | 61.4377
234.1406 | 123.3353 | -61.4685 | 61.5555 | 0.025705 | -0.031363 | -0.012 | -0.01586 | 0.008797 | -0.005985 | 0.015112 | 61.5142 | 0.13416 | 61.3997 | -0.055996 | 0.007032 | 61.5616 | -0.001436 | 61.4451 | 61.4942 | 61.4371 | 61.4565 | 61.4526 | 61.4773 | 61.4625 | 61.4836 | 122.9827 | 61.6027 | 122.8682 | 61.4125 | 61.4755 | 123.0301 | 61.4671 | 122.9136 | 61.5072 | 61.5156 | 61.3926 | 61.4011
235.0625 | 123.2758 | -61.4639 | 61.6516 | 0.025705 | -0.031363 | -0.002842 | -0.006703 | 0.017953 | -0.005985 | 0.015112 | 61.5279 | 0.13874 | 61.4638 | -0.060575 | 0.007032 | 61.557 | -0.006014 | 61.4405 | 61.4896 | 61.4326 | 61.4611 | 61.4572 | 61.4819 | 61.4579 | 61.479 | 122.9919 | 61.6027 | 122.9277 | 61.4034 | 61.471 | 123.0209 | 61.4579 | 122.9044 | 61.5209 | 61.534 | 61.4567 | 61.4698
236.125 | 123.23 | -61.4822 | 61.615 | 0.030283 | -0.026784 | -0.012 | -0.011281 | 0.013375 | -0.010563 | 0.01969 | 61.5325 | 0.14332 | 61.4684 | -0.055996 | 0.01161 | 61.557 | -0.001436 | 61.4405 | 61.5125 | 61.4555 | 61.4702 | 61.471 | 61.4956 | 61.4717 | 61.5019 | 123.0148 | 61.6256 | 122.9506 | 61.4262 | 61.4938 | 123.0392 | 61.4808 | 122.9227 | 61.5209 | 61.534 | 61.4567 | 61.4698
237.0625 | 123.262 | -61.4777 | 61.6425 | 0.030283 | -0.040521 | -0.016578 | -0.01586 | 0.013375 | -0.005985 | 0.015112 | 61.5279 | 0.14332 | 61.3997 | -0.055996 | 0.007032 | 61.5616 | -0.010593 | 61.4451 | 61.5079 | 61.4371 | 61.4611 | 61.4618 | 61.491 | 61.4717 | 61.4928 | 123.0056 | 61.621 | 122.8773 | 61.4217 | 61.4847 | 123.0392 | 61.4671 | 122.9227 | 61.5209 | 61.5385 | 61.3926 | 61.4103
238.0625 | 123.2208 | -61.4731 | 61.647 | 0.025705 | -0.035942 | -0.007421 | -0.006703 | 0.027109 | -0.005985 | 0.024268 | 61.5279 | 0.13874 | 61.4317 | -0.060575 | 0.01161 | 61.557 | -0.010593 | 61.4496 | 61.4988 | 61.4371 | 61.4657 | 61.4664 | 61.5002 | 61.4671 | 61.4974 | 123.001 | 61.6118 | 122.9048 | 61.4125 | 61.4847 | 123.0301 | 61.4625 | 122.9227 | 61.5163 | 61.5385 | 61.4201 | 61.4423
239.1406 | 123.3444 | -61.4502 | 61.5738 | 0.030283 | -0.035942 | -0.007421 | -0.011281 | 0.027109 | -0.005985 | 0.005955 | 61.5234 | 0.14332 | 61.4638 | -0.055996 | 0.002454 | 61.5616 | -0.010593 | 61.4542 | 61.4805 | 61.4143 | 61.4428 | 61.4389 | 61.4773 | 61.4442 | 61.4562 | 122.9736 | 61.5935 | 122.914 | 61.3942 | 61.4526 | 123.0118 | 61.4396 | 122.9044 | 61.5209 | 61.534 | 61.4613 | 61.4744
240.0469 | 123.262 | -61.4685 | 61.6196 | 0.021127 | -0.040521 | -0.021157 | -0.011281 | 0.017953 | -0.010563 | 0.015112 | 61.5234 | 0.13874 | 61.4134 | -0.055996 | 0.007032 | 61.5616 | -0.010593 | 61.4451 | 61.4896 | 61.428 | 61.4473 | 61.4572 | 61.4865 | 61.4579 | 61.4836 | 122.9919 | 61.6072 | 122.8819 | 61.4125 | 61.4755 | 123.0301 | 61.4579 | 122.9136 | 61.5163 | 61.534 | 61.4064 | 61.424
241.0469 | 123.2666 | -61.4914 | 61.647 | 0.030283 | -0.031363 | -0.012 | -0.002124 | 0.017953 | -0.005985 | 0.01969 | 61.5325 | 0.13874 | 61.4317 | -0.051417 | 0.002454 | 61.5616 | -0.006014 | 61.4451 | 61.5217 | 61.46 | 61.4794 | 61.4893 | 61.5093 | 61.4854 | 61.5111 | 123.0239 | 61.6301 | 122.9231 | 61.44 | 61.4938 | 123.053 | 61.4854 | 122.9365 | 61.5301 | 61.5385 | 61.4293 | 61.4377
242.125 | 123.262 | -61.4639 | 61.6196 | 0.025705 | -0.035942 | -0.012 | -0.006703 | 0.022531 | -0.005985 | 0.015112 | 61.5325 | 0.13874 | 61.4775 | -0.051417 | 0.01161 | 61.5616 | -0.006014 | 61.4496 | 61.4896 | 61.428 | 61.4519 | 61.4572 | 61.4865 | 61.4579 | 61.479 | 122.9964 | 61.6027 | 122.9414 | 61.4125 | 61.4755 | 123.0255 | 61.4579 | 122.9136 | 61.5209 | 61.5385 | 61.4659 | 61.4835
243.0625 | 123.3124 | -61.4731 | 61.6196 | 0.025705 | -0.031363 | -0.016578 | -0.006703 | 0.022531 | -0.010563 | 0.01969 | 61.5325 | 0.1479 | 61.4134 | -0.051417 | 0.007032 | 61.5707 | -0.001436 | 61.4451 | 61.4988 | 61.4417 | 61.4565 | 61.4664 | 61.4956 | 61.4625 | 61.4928 | 123.0056 | 61.621 | 122.8865 | 61.4217 | 61.4801 | 123.0438 | 61.4716 | 122.9182 | 61.5255 | 61.534 | 61.4064 | 61.4149
244.1406 | 123.3627 | -61.4639 | 61.5829 | 0.025705 | -0.040521 | -0.012 | -0.006703 | 0.017953 | -0.005985 | 0.01969 | 61.5234 | 0.14332 | 61.45 | -0.060575 | 0.01161 | 61.5616 | -0.006014 | 61.4542 | 61.4896 | 61.4234 | 61.4519 | 61.4572 | 61.4819 | 61.4579 | 61.4836 | 122.9873 | 61.6072 | 122.914 | 61.4034 | 61.4755 | 123.0255 | 61.4579 | 122.9182 | 61.5118 | 61.5294 | 61.4384 | 61.4561
245.0625 | 123.3124 | -61.4731 | 61.6241 | 0.021127 | -0.031363 | -0.012 | -0.01586 | 0.008797 | -0.010563 | 0.015112 | 61.5279 | 0.14332 | 61.45 | -0.051417 | 0.002454 | 61.5616 | -0.001436 | 61.4451 | 61.4942 | 61.4417 | 61.4611 | 61.4572 | 61.4819 | 61.4625 | 61.4882 | 123.001 | 61.6164 | 122.9231 | 61.4217 | 61.4755 | 123.0347 | 61.4716 | 122.9182 | 61.5255 | 61.5294 | 61.4476 | 61.4515
246.0625 | 123.2986 | -61.4777 | 61.6333 | 0.030283 | -0.035942 | -0.021157 | 0.002454 | 0.022531 | -0.010563 | 0.01969 | 61.5188 | 0.13874 | 61.418 | -0.055996 | 0.01161 | 61.5616 | -0.006014 | 61.4451 | 61.5079 | 61.4417 | 61.4565 | 61.4801 | 61.5002 | 61.4671 | 61.4974 | 122.9964 | 61.6164 | 122.8957 | 61.4217 | 61.4893 | 123.0392 | 61.4716 | 122.9227 | 61.5072 | 61.5248 | 61.4064 | 61.424
247.0625 | 123.2437 | -61.4868 | 61.6516 | 0.025705 | -0.031363 | -0.012 | -0.002124 | 0.017953 | -0.010563 | 0.010533 | 61.5279 | 0.13874 | 61.4271 | -0.055996 | 0.007032 | 61.557 | -0.010593 | 61.4405 | 61.5125 | 61.4555 | 61.4748 | 61.4847 | 61.5048 | 61.4763 | 61.4973 | 123.0148 | 61.6256 | 122.914 | 61.4308 | 61.4938 | 123.0438 | 61.4762 | 122.9273 | 61.5209 | 61.5385 | 61.4201 | 61.4377
248.125 | 123.2666 | -61.4822 | 61.615 | 0.025705 | -0.040521 | -0.016578 | -0.006703 | 0.017953 | -0.005985 | 0.01969 | 61.5325 | 0.1479 | 61.4684 | -0.055996 | 0.002454 | 61.5662 | -0.001436 | 61.4451 | 61.5079 | 61.4417 | 61.4657 | 61.4755 | 61.5002 | 61.4763 | 61.5019 | 123.0148 | 61.6301 | 122.9506 | 61.4262 | 61.4847 | 123.0484 | 61.4808 | 122.9273 | 61.5301 | 61.534 | 61.4659 | 61.4698
249.0625 | 123.23 | -61.528 | 61.5829 | 0.021127 | -0.031363 | -0.016578 | -0.006703 | 0.027109 | -0.005985 | 0.01969 | 61.5279 | 0.15248 | 61.4271 | -0.055996 | 0.01161 | 61.5662 | -0.006014 | 61.4451 | 61.5491 | 61.4967 | 61.5114 | 61.5213 | 61.5551 | 61.522 | 61.5477 | 123.056 | 61.6805 | 122.9552 | 61.472 | 61.5396 | 123.0942 | 61.522 | 122.9731 | 61.5163 | 61.534 | 61.4155 | 61.4332
250.125 | 123.2391 | -61.4822 | 61.6379 | 0.021127 | -0.035942 | -0.007421 | -0.006703 | 0.008797 | -0.001406 | 0.010533 | 61.5234 | 0.13874 | 61.4043 | -0.065154 | 0.01161 | 61.5616 | -0.001436 | 61.4542 | 61.5034 | 61.4463 | 61.4748 | 61.4755 | 61.491 | 61.4808 | 61.4928 | 123.0056 | 61.621 | 122.8865 | 61.4171 | 61.4938 | 123.0438 | 61.4808 | 122.9365 | 61.5118 | 61.5248 | 61.3926 | 61.4057
251.0625 | 123.262 | -61.4731 | 61.6241 | 0.030283 | -0.031363 | -0.016578 | -0.002124 | 0.017953 | -0.005985 | 0.015112 | 61.5325 | 0.14332 | 61.4684 | -0.055996 | 0.01161 | 61.557 | -0.006014 | 61.4451 | 61.5034 | 61.4417 | 61.4565 | 61.471 | 61.491 | 61.4671 | 61.4882 | 123.0056 | 61.6164 | 122.9414 | 61.4171 | 61.4847 | 123.0301 | 61.4671 | 122.9182 | 61.5209 | 61.5385 | 61.4567 | 61.4744
252.0625 | 123.2071 | -61.4868 | 61.6333 | 0.030283 | -0.035942 | -0.007421 | -0.011281 | 0.017953 | -0.010563 | 0.01969 | 61.5279 | 0.14332 | 61.4638 | -0.055996 | 0.01161 | 61.5524 | -0.006014 | 61.4496 | 61.5171 | 61.4509 | 61.4794 | 61.4755 | 61.5048 | 61.4763 | 61.5065 | 123.0148 | 61.6301 | 122.9506 | 61.4308 | 61.4984 | 123.0392 | 61.4808 | 122.9365 | 61.5163 | 61.534 | 61.4522 | 61.4698
253.125 | 123.262 | -61.4639 | 61.615 | 0.030283 | -0.031363 | -0.021157 | -0.011281 | 0.017953 | -0.005985 | 0.015112 | 61.5325 | 0.1479 | 61.418 | -0.060575 | 0.007032 | 61.5662 | -0.006014 | 61.4451 | 61.4942 | 61.4326 | 61.4428 | 61.4526 | 61.4819 | 61.4579 | 61.479 | 122.9964 | 61.6118 | 122.8819 | 61.4034 | 61.471 | 123.0301 | 61.4579 | 122.909 | 61.5255 | 61.5385 | 61.411 | 61.424
254.0625 | 123.349 | -61.4548 | 61.6058 | 0.021127 | -0.031363 | -0.016578 | -0.011281 | 0.017953 | -0.005985 | 0.01969 | 61.5279 | 0.14332 | 61.418 | -0.055996 | 0.007032 | 61.5662 | 0.003143 | 61.4542 | 61.4759 | 61.4234 | 61.4382 | 61.4435 | 61.4727 | 61.4488 | 61.4745 | 122.9827 | 61.5981 | 122.8728 | 61.3988 | 61.4618 | 123.0209 | 61.4579 | 122.909 | 61.5209 | 61.5248 | 61.411 | 61.4148
255.125 | 123.2162 | -61.4639 | 61.6241 | 0.025705 | -0.035942 | -0.016578 | -0.006703 | 0.022531 | -0.010563 | 0.01969 | 61.5371 | 0.13874 | 61.4729 | -0.051417 | 0.007032 | 61.5662 | -0.010593 | 61.4542 | 61.4896 | 61.428 | 61.4474 | 61.4572 | 61.4865 | 61.4534 | 61.4836 | 123.001 | 61.6027 | 122.9369 | 61.4125 | 61.471 | 123.0301 | 61.4533 | 122.9182 | 61.5301 | 61.5477 | 61.4659 | 61.4835
256.0625 | 123.2986 | -61.4822 | 61.6013 | 0.034862 | -0.035942 | -0.007421 | -0.011281 | 0.022531 | -0.005985 | 0.010533 | 61.5279 | 0.1479 | 61.4226 | -0.055996 | 0.01161 | 61.5616 | -0.010593 | 61.4405 | 61.5171 | 61.4463 | 61.4748 | 61.471 | 61.5048 | 61.4763 | 61.4928 | 123.0102 | 61.6301 | 122.9048 | 61.4262 | 61.4938 | 123.0438 | 61.4716 | 122.9227 | 61.5163 | 61.5385 | 61.411 | 61.4332
257.0625 | 123.2803 | -61.4594 | 61.6287 | 0.025705 | -0.035942 | -0.012 | -0.011281 | 0.017953 | -0.005985 | 0.015112 | 61.5234 | 0.14332 | 61.4134 | -0.055996 | 0.007032 | 61.5616 | -0.015171 | 61.4451 | 61.4851 | 61.4234 | 61.4474 | 61.4481 | 61.4773 | 61.4534 | 61.4745 | 122.9827 | 61.6027 | 122.8728 | 61.4034 | 61.4664 | 123.0209 | 61.4442 | 122.9044 | 61.5163 | 61.5385 | 61.4064 | 61.4286
258.0625 | 123.2483 | -61.4868 | 61.6745 | 0.025705 | -0.031363 | -0.016578 | -0.011281 | 0.017953 | -0.001406 | 0.01969 | 61.5279 | 0.13874 | 61.4638 | -0.055996 | 0.007032 | 61.5616 | -0.010593 | 61.4496 | 61.5125 | 61.4555 | 61.4702 | 61.4755 | 61.5048 | 61.4854 | 61.5065 | 123.0148 | 61.6256 | 122.9506 | 61.4308 | 61.4938 | 123.0484 | 61.4762 | 122.9365 | 61.5209 | 61.5385 | 61.4567 | 61.4744
259.1562 | 123.3261 | -61.4502 | 61.5829 | 0.030283 | -0.035942 | -0.016578 | -0.011281 | 0.013375 | -0.005985 | 0.015112 | 61.5234 | 0.13874 | 61.4134 | -0.051417 | 0.007032 | 61.5616 | -0.006014 | 61.4542 | 61.4805 | 61.4143 | 61.4336 | 61.4389 | 61.4636 | 61.4442 | 61.4653 | 122.9736 | 61.5889 | 122.8636 | 61.3988 | 61.4572 | 123.0118 | 61.4442 | 122.9044 | 61.5163 | 61.5294 | 61.4064 | 61.4194
260.0625 | 123.2895 | -61.4822 | 61.6196 | 0.025705 | -0.031363 | -0.021157 | -0.002124 | 0.013375 | -0.005985 | 0.015112 | 61.5371 | 0.13874 | 61.4638 | -0.055996 | 0.016188 | 61.5616 | -0.006014 | 61.4451 | 61.5079 | 61.4509 | 61.4611 | 61.4801 | 61.4956 | 61.4763 | 61.4974 | 123.0193 | 61.621 | 122.946 | 61.4262 | 61.4984 | 123.0438 | 61.4762 | 122.9273 | 61.5209 | 61.5431 | 61.4476 | 61.4698
261.125 | 123.3215 | -61.4639 | 61.6287 | 0.025705 | -0.031363 | -0.016578 | -0.002124 | 0.022531 | -0.001406 | 0.01969 | 61.5371 | 0.13874 | 61.4409 | -0.055996 | 0.016188 | 61.5524 | -0.001436 | 61.4359 | 61.4896 | 61.4326 | 61.4474 | 61.4618 | 61.4865 | 61.4625 | 61.4836 | 123.001 | 61.6027 | 122.9048 | 61.4079 | 61.4801 | 123.0164 | 61.4625 | 122.8998 | 61.5209 | 61.5385 | 61.4247 | 61.4423
262.0469 | 123.2483 | -61.4731 | 61.6241 | 0.025705 | -0.035942 | -0.016578 | -0.011281 | 0.022531 | -0.010563 | 0.015112 | 61.5234 | 0.13416 | 61.4226 | -0.051417 | 0.002454 | 61.5616 | -0.006014 | 61.4496 | 61.4988 | 61.4371 | 61.4565 | 61.4618 | 61.4956 | 61.4625 | 61.4882 | 122.9964 | 61.6072 | 122.8957 | 61.4217 | 61.4755 | 123.0347 | 61.4671 | 122.9227 | 61.5209 | 61.5294 | 61.4201 | 61.4286
263.125 | 123.2483 | -61.4914 | 61.6562 | 0.021127 | -0.035942 | -0.025735 | -0.002124 | 0.013375 | -0.001406 | 0.024268 | 61.5325 | 0.15248 | 61.4684 | -0.055996 | 0.007032 | 61.5616 | -0.010593 | 61.4451 | 61.5125 | 61.4555 | 61.4657 | 61.4893 | 61.5048 | 61.49 | 61.5157 | 123.0239 | 61.6439 | 122.9597 | 61.4354 | 61.4984 | 123.053 | 61.4808 | 122.9365 | 61.5255 | 61.5431 | 61.4613 | 61.4789
264.0625 | 123.3124 | -61.4868 | 61.5875 | 0.034862 | -0.0451 | -0.021157 | -0.006703 | 0.022531 | -0.005985 | 0.015112 | 61.5188 | 0.14332 | 61.4088 | -0.055996 | 0.007032 | 61.5616 | -0.006014 | 61.4405 | 61.5217 | 61.4417 | 61.4657 | 61.4801 | 61.5093 | 61.4808 | 61.5019 | 123.0056 | 61.6301 | 122.8957 | 61.4308 | 61.4938 | 123.0484 | 61.4808 | 122.9273 | 61.5118 | 61.5248 | 61.4018 | 61.4149
265.125 | 123.2712 | -61.4685 | 61.647 | 0.025705 | -0.035942 | -0.012 | -0.006703 | 0.017953 | -0.001406 | 0.010533 | 61.5325 | 0.1479 | 61.45 | -0.060575 | 0.007032 | 61.5616 | -0.006014 | 61.4405 | 61.4942 | 61.4326 | 61.4565 | 61.4618 | 61.4865 | 61.4671 | 61.479 | 123.001 | 61.6164 | 122.9185 | 61.4079 | 61.4755 | 123.0301 | 61.4625 | 122.909 | 61.5255 | 61.5385 | 61.443 | 61.4561
266.0625 | 123.2758 | -61.441 | 61.6608 | 0.021127 | -0.026784 | -0.016578 | -0.011281 | 0.013375 | -0.005985 | 0.01969 | 61.5279 | 0.1479 | 61.4409 | -0.055996 | 0.007032 | 61.5707 | -0.006014 | 61.4451 | 61.4622 | 61.4143 | 61.4245 | 61.4298 | 61.4544 | 61.4351 | 61.4607 | 122.969 | 61.5889 | 122.8819 | 61.385 | 61.4481 | 123.0118 | 61.435 | 122.8861 | 61.5209 | 61.534 | 61.4339 | 61.4469
267.0625 | 123.2895 | -61.4914 | 61.6608 | 0.030283 | -0.035942 | -0.025735 | -0.011281 | 0.022531 | -0.005985 | 0.010533 | 61.5279 | 0.14332 | 61.4134 | -0.055996 | 0.01161 | 61.5662 | -0.010593 | 61.4496 | 61.5217 | 61.4555 | 61.4657 | 61.4801 | 61.5139 | 61.4854 | 61.5019 | 123.0193 | 61.6347 | 122.9048 | 61.4354 | 61.503 | 123.0576 | 61.4808 | 122.941 | 61.5163 | 61.5385 | 61.4018 | 61.424
268.0625 | 123.2391 | -61.4731 | 61.6425 | 0.030283 | -0.026784 | -0.016578 | -0.006703 | 0.017953 | -0.001406 | 0.024268 | 61.5325 | 0.1479 | 61.4729 | -0.055996 | 0.01161 | 61.5662 | -0.006014 | 61.4451 | 61.5034 | 61.4463 | 61.4565 | 61.4664 | 61.491 | 61.4717 | 61.4974 | 123.0056 | 61.621 | 122.946 | 61.4171 | 61.4847 | 123.0392 | 61.4671 | 122.9182 | 61.5209 | 61.5385 | 61.4613 | 61.4789
269.1562 | 123.3398 | -61.4548 | 61.615 | 0.025705 | -0.031363 | -0.021157 | -0.002124 | 0.017953 | -0.001406 | 0.024268 | 61.5279 | 0.14332 | 61.4592 | -0.055996 | 0.01161 | 61.5616 | -0.001436 | 61.4542 | 61.4805 | 61.4234 | 61.4336 | 61.4526 | 61.4727 | 61.4534 | 61.479 | 122.9827 | 61.5981 | 122.914 | 61.3988 | 61.4664 | 123.0164 | 61.4533 | 122.909 | 61.5163 | 61.5294 | 61.4476 | 61.4606
270.0625 | 123.2254 | -61.5051 | 61.615 | 0.025705 | -0.035942 | -0.016578 | -0.011281 | 0.022531 | -0.001406 | 0.015112 | 61.5279 | 0.14332 | 61.418 | -0.055996 | 0.007032 | 61.5616 | -0.010593 | 61.4451 | 61.5308 | 61.4692 | 61.4885 | 61.4938 | 61.5277 | 61.5037 | 61.5202 | 123.0331 | 61.6484 | 122.9231 | 61.4491 | 61.5122 | 123.0667 | 61.4945 | 122.9502 | 61.5209 | 61.5385 | 61.411 | 61.4286
271.125 | 123.3078 | -61.4914 | 61.6241 | 0.030283 | -0.040521 | -0.016578 | -0.006703 | 0.017953 | -0.001406 | 0.015112 | 61.5279 | 0.14332 | 61.4363 | -0.046838 | 0.01161 | 61.557 | -0.006014 | 61.4542 | 61.5217 | 61.4509 | 61.4748 | 61.4847 | 61.5093 | 61.49 | 61.5065 | 123.0193 | 61.6347 | 122.9277 | 61.4446 | 61.503 | 123.0484 | 61.4854 | 122.9456 | 61.5163 | 61.534 | 61.4247 | 61.4423
272.0625 | 123.2391 | -61.4822 | 61.6333 | 0.030283 | -0.035942 | -0.016578 | -0.002124 | 0.017953 | 0.003172 | 0.015112 | 61.5279 | 0.1479 | 61.4775 | -0.055996 | 0.01161 | 61.5616 | -0.010593 | 61.4405 | 61.5125 | 61.4463 | 61.4657 | 61.4801 | 61.5002 | 61.4854 | 61.4974 | 123.0102 | 61.6301 | 122.9597 | 61.4262 | 61.4938 | 123.0438 | 61.4716 | 122.9227 | 61.5163 | 61.5385 | 61.4659 | 61.4881
273.0625 | 123.2162 | -61.4822 | 61.6562 | 0.030283 | -0.035942 | -0.007421 | -0.006703 | 0.017953 | 0.003172 | 0.01969 | 61.5279 | 0.13874 | 61.4226 | -0.051417 | 0.016188 | 61.5662 | -0.006014 | 61.4451 | 61.5125 | 61.4463 | 61.4748 | 61.4755 | 61.5002 | 61.4854 | 61.5019 | 123.0102 | 61.621 | 122.9048 | 61.4308 | 61.4984 | 123.0484 | 61.4762 | 122.9273 | 61.5118 | 61.534 | 61.4064 | 61.4286
274.1406 | 123.3353 | -61.4182 | 61.6013 | 0.025705 | -0.040521 | -0.016578 | -0.011281 | 0.017953 | -0.005985 | 0.015112 | 61.5234 | 0.13874 | 61.3997 | -0.055996 | 0.007032 | 61.5524 | -0.006014 | 61.4496 | 61.4439 | 61.3776 | 61.4016 | 61.4069 | 61.4361 | 61.4122 | 61.4333 | 122.9415 | 61.5569 | 122.8178 | 61.3622 | 61.4252 | 122.9706 | 61.4121 | 122.8678 | 61.5163 | 61.5294 | 61.3926 | 61.4057
275.0625 | 123.2849 | -61.4685 | 61.647 | 0.034862 | -0.035942 | -0.016578 | -0.002124 | 0.027109 | -0.001406 | 0.024268 | 61.5371 | 0.1479 | 61.4638 | -0.051417 | 0.007032 | 61.5707 | -0.010593 | 61.4451 | 61.5034 | 61.4326 | 61.4519 | 61.4664 | 61.4956 | 61.4671 | 61.4928 | 123.0056 | 61.6164 | 122.9323 | 61.4171 | 61.4755 | 123.0392 | 61.4579 | 122.9136 | 61.5301 | 61.5477 | 61.4567 | 61.4744
276.0625 | 123.2803 | -61.4594 | 61.6379 | 0.025705 | -0.035942 | -0.016578 | -0.006703 | 0.017953 | -0.010563 | 0.015112 | 61.5234 | 0.14332 | 61.4455 | -0.060575 | 0.007032 | 61.5662 | -0.006014 | 61.4496 | 61.4851 | 61.4234 | 61.4428 | 61.4526 | 61.4773 | 61.4488 | 61.4745 | 122.9827 | 61.6027 | 122.9048 | 61.3988 | 61.4664 | 123.0255 | 61.4533 | 122.909 | 61.5163 | 61.5294 | 61.4384 | 61.4515
277.0625 | 123.3124 | -61.4685 | 61.6653 | 0.030283 | -0.035942 | -0.021157 | -0.002124 | 0.022531 | -0.001406 | 0.01969 | 61.5371 | 0.13416 | 61.4226 | -0.051417 | 0.016188 | 61.557 | -0.010593 | 61.4451 | 61.4988 | 61.4326 | 61.4473 | 61.4664 | 61.491 | 61.4671 | 61.4882 | 123.0056 | 61.6027 | 122.8911 | 61.4171 | 61.4847 | 123.0255 | 61.4579 | 122.9136 | 61.5209 | 61.5477 | 61.4064 | 61.4332
278.125 | 123.2803 | -61.4731 | 61.615 | 0.034862 | -0.031363 | -0.012 | -0.01586 | 0.027109 | -0.001406 | 0.01969 | 61.5371 | 0.13416 | 61.4821 | -0.055996 | 0.01161 | 61.5616 | -0.001436 | 61.4542 | 61.5079 | 61.4417 | 61.4611 | 61.4572 | 61.5002 | 61.4717 | 61.4928 | 123.0102 | 61.6072 | 122.9552 | 61.4171 | 61.4847 | 123.0347 | 61.4716 | 122.9273 | 61.5255 | 61.5385 | 61.4705 | 61.4835
279.0625 | 123.0972 | -61.5143 | 61.5601 | 0.034862 | -0.031363 | -0.007421 | -0.006703 | 0.022531 | -0.001406 | 0.024268 | 61.5234 | 0.13874 | 61.418 | -0.051417 | 0.01161 | 61.5616 | -0.001436 | 61.4542 | 61.5491 | 61.4829 | 61.5069 | 61.5076 | 61.5368 | 61.5129 | 61.5386 | 123.0376 | 61.653 | 122.9323 | 61.4629 | 61.5259 | 123.0759 | 61.5128 | 122.9685 | 61.5118 | 61.5248 | 61.4064 | 61.4194
280.125 | 123.2666 | -61.4594 | 61.6196 | 0.034862 | -0.031363 | -0.016578 | -0.006703 | 0.013375 | -0.005985 | 0.01969 | 61.5325 | 0.15248 | 61.4638 | -0.046838 | 0.01161 | 61.5616 | -0.006014 | 61.4588 | 61.4942 | 61.428 | 61.4428 | 61.4526 | 61.4727 | 61.4534 | 61.479 | 122.9919 | 61.6118 | 122.9231 | 61.4125 | 61.471 | 123.0209 | 61.4533 | 122.9182 | 61.5209 | 61.5385 | 61.4522 | 61.4698
281.0625 | 123.23 | -61.4868 | 61.6333 | 0.021127 | -0.026784 | -0.016578 | -0.01586 | 0.022531 | -0.001406 | 0.015112 | 61.5279 | 0.14332 | 61.4455 | -0.051417 | 0.007032 | 61.5707 | -0.015171 | 61.4496 | 61.5079 | 61.46 | 61.4702 | 61.471 | 61.5093 | 61.4854 | 61.5019 | 123.0148 | 61.6301 | 122.9323 | 61.4354 | 61.4938 | 123.0576 | 61.4716 | 122.9365 | 61.5209 | 61.5431 | 61.4384 | 61.4606
282.125 | 123.2803 | -61.5005 | 61.5921 | 0.030283 | -0.031363 | -0.021157 | -0.011281 | 0.017953 | -0.001406 | 0.01969 | 61.5279 | 0.14332 | 61.4134 | -0.055996 | 0.01161 | 61.5616 | -0.006014 | 61.4588 | 61.5308 | 61.4692 | 61.4794 | 61.4893 | 61.5185 | 61.4991 | 61.5202 | 123.0285 | 61.6439 | 122.914 | 61.4446 | 61.5122 | 123.0621 | 61.4945 | 122.9594 | 61.5163 | 61.534 | 61.4018 | 61.4194
283.0625 | 123.2666 | -61.4548 | 61.6196 | 0.025705 | -0.035942 | -0.016578 | -0.006703 | 0.027109 | 0.003172 | 0.024268 | 61.5371 | 0.13874 | 61.4729 | -0.051417 | 0.007032 | 61.5662 | -0.010593 | 61.4496 | 61.4805 | 61.4188 | 61.4382 | 61.4481 | 61.4819 | 61.4579 | 61.479 | 122.9919 | 61.5935 | 122.9277 | 61.4034 | 61.4618 | 123.0209 | 61.4442 | 122.9044 | 61.5301 | 61.5477 | 61.4659 | 61.4835
284.0625 | 123.317 | -61.4685 | 61.5921 | 0.030283 | -0.026784 | -0.012 | -0.002124 | 0.022531 | 0.003172 | 0.010533 | 61.5279 | 0.14332 | 61.4088 | -0.055996 | 0.007032 | 61.5662 | -0.001436 | 61.4405 | 61.4988 | 61.4417 | 61.4565 | 61.4664 | 61.491 | 61.4717 | 61.479 | 122.9964 | 61.6118 | 122.8773 | 61.4125 | 61.4755 | 123.0347 | 61.4671 | 122.909 | 61.5209 | 61.5294 | 61.4018 | 61.4103
285.0625 | 123.2666 | -61.4822 | 61.615 | 0.025705 | -0.031363 | -0.021157 | -0.006703 | 0.027109 | -0.001406 | 0.024268 | 61.5325 | 0.1479 | 61.4592 | -0.046838 | 0.016188 | 61.5616 | -0.010593 | 61.4451 | 61.5079 | 61.4509 | 61.4611 | 61.4755 | 61.5093 | 61.4808 | 61.5065 | 123.0148 | 61.6301 | 122.9414 | 61.4354 | 61.4984 | 123.0438 | 61.4716 | 122.9273 | 61.5163 | 61.5431 | 61.443 | 61.4698
286.125 | 123.3032 | -61.4548 | 61.6241 | 0.025705 | -0.040521 | -0.012 | -0.002124 | 0.013375 | -0.001406 | 0.01969 | 61.5279 | 0.14332 | 61.4638 | -0.051417 | 0.007032 | 61.5616 | -0.001436 | 61.4405 | 61.4805 | 61.4143 | 61.4428 | 61.4526 | 61.4681 | 61.4534 | 61.4745 | 122.9827 | 61.5981 | 122.9185 | 61.4034 | 61.4618 | 123.0164 | 61.4533 | 122.8953 | 61.5209 | 61.5294 | 61.4567 | 61.4652
287.0625 | 123.2437 | -61.4731 | 61.6653 | 0.025705 | -0.035942 | -0.012 | -0.002124 | 0.017953 | -0.010563 | 0.024268 | 61.5279 | 0.1479 | 61.418 | -0.051417 | 0.002454 | 61.5662 | -0.006014 | 61.4405 | 61.4988 | 61.4371 | 61.4611 | 61.471 | 61.491 | 61.4625 | 61.4974 | 123.001 | 61.621 | 122.8911 | 61.4217 | 61.4755 | 123.0392 | 61.4671 | 122.9136 | 61.5255 | 61.534 | 61.4155 | 61.424
288.0625 | 123.2391 | -61.5189 | 61.6104 | 0.03944 | -0.040521 | -0.016578 | -0.011281 | 0.022531 | -0.005985 | 0.01969 | 61.5325 | 0.14332 | 61.4684 | -0.055996 | 0.01161 | 61.557 | -0.010593 | 61.4496 | 61.5583 | 61.4783 | 61.5023 | 61.5076 | 61.5414 | 61.5129 | 61.5385 | 123.0514 | 61.6622 | 122.9872 | 61.4629 | 61.5305 | 123.0759 | 61.5083 | 122.9685 | 61.5209 | 61.5431 | 61.4567 | 61.4789
289.1406 | 123.3353 | -61.4731 | 61.5875 | 0.021127 | -0.031363 | -0.016578 | -0.006703 | 0.008797 | -0.001406 | 0.01969 | 61.5279 | 0.15248 | 61.4546 | -0.055996 | 0.002454 | 61.5662 | -0.001436 | 61.4405 | 61.4942 | 61.4417 | 61.4565 | 61.4664 | 61.4819 | 61.4717 | 61.4928 | 123.001 | 61.6256 | 122.9277 | 61.4171 | 61.4755 | 123.0392 | 61.4716 | 122.9136 | 61.5255 | 61.5294 | 61.4522 | 61.4561
290.0625 | 123.2849 | -61.4822 | 61.647 | 0.030283 | -0.035942 | -0.012 | -0.006703 | 0.022531 | -0.005985 | 0.015112 | 61.5325 | 0.14332 | 61.4088 | -0.055996 | 0.01161 | 61.557 | -0.001436 | 61.4496 | 61.5125 | 61.4463 | 61.4702 | 61.4755 | 61.5048 | 61.4763 | 61.4974 | 123.0148 | 61.6256 | 122.8911 | 61.4262 | 61.4938 | 123.0392 | 61.4808 | 122.9319 | 61.5209 | 61.534 | 61.3972 | 61.4103
291.0625 | 123.2895 | -61.4868 | 61.6333 | 0.030283 | -0.035942 | -0.012 | -0.011281 | 0.022531 | -0.001406 | 0.01969 | 61.5325 | 0.1479 | 61.4363 | -0.060575 | 0.007032 | 61.557 | -0.006014 | 61.4405 | 61.5171 | 61.4509 | 61.4748 | 61.4755 | 61.5093 | 61.4854 | 61.5065 | 123.0193 | 61.6347 | 122.9231 | 61.4262 | 61.4938 | 123.0438 | 61.4808 | 122.9273 | 61.5255 | 61.5385 | 61.4293 | 61.4423
292.0625 | 123.2666 | -61.4502 | 61.6425 | 0.021127 | -0.035942 | -0.012 | -0.006703 | 0.022531 | -0.001406 | 0.033424 | 61.5371 | 0.13874 | 61.4729 | -0.055996 | 0.007032 | 61.5616 | -0.006014 | 61.4542 | 61.4713 | 61.4143 | 61.4382 | 61.4435 | 61.4727 | 61.4488 | 61.4836 | 122.9873 | 61.5889 | 122.9231 | 61.3942 | 61.4572 | 123.0118 | 61.4442 | 122.9044 | 61.5301 | 61.5431 | 61.4659 | 61.4789
293.125 | 123.2986 | -61.4777 | 61.6379 | 0.025705 | -0.035942 | -0.016578 | -0.006703 | 0.022531 | -0.005985 | 0.01969 | 61.5325 | 0.14332 | 61.4088 | -0.060575 | 0.016188 | 61.5662 | -0.006014 | 61.4451 | 61.5034 | 61.4417 | 61.4611 | 61.471 | 61.5002 | 61.4717 | 61.4974 | 123.0102 | 61.621 | 122.8865 | 61.4171 | 61.4938 | 123.0438 | 61.4716 | 122.9227 | 61.5163 | 61.5385 | 61.3926 | 61.4149
294.0625 | 123.2117 | -61.4777 | 61.6104 | 0.030283 | -0.031363 | -0.012 | 0.002454 | 0.022531 | -0.001406 | 0.024268 | 61.5325 | 0.1479 | 61.4684 | -0.065154 | 0.01161 | 61.5662 | -0.006014 | 61.4405 | 61.5079 | 61.4463 | 61.4657 | 61.4801 | 61.5002 | 61.4763 | 61.5019 | 123.0102 | 61.6256 | 122.946 | 61.4125 | 61.4893 | 123.0438 | 61.4716 | 122.9182 | 61.5209 | 61.5385 | 61.4567 | 61.4744
295.125 | 123.262 | -61.4731 | 61.6196 | 0.030283 | -0.031363 | -0.012 | -0.006703 | 0.027109 | -0.005985 | 0.010533 | 61.5325 | 0.14332 | 61.418 | -0.055996 | 0.002454 | 61.5524 | -0.006014 | 61.4496 | 61.5034 | 61.4417 | 61.4611 | 61.4664 | 61.5002 | 61.4671 | 61.4836 | 123.0056 | 61.6164 | 122.8911 | 61.4171 | 61.4755 | 123.0255 | 61.4671 | 122.9227 | 61.5301 | 61.5385 | 61.4155 | 61.424
296.0469 | 123.2986 | -61.4868 | 61.6196 | 0.034862 | -0.031363 | -0.012 | -0.006703 | 0.017953 | -0.010563 | 0.01969 | 61.5279 | 0.14332 | 61.4409 | -0.051417 | 0.002454 | 61.5662 | -0.006014 | 61.4451 | 61.5217 | 61.4555 | 61.4748 | 61.4801 | 61.5048 | 61.4763 | 61.5065 | 123.0148 | 61.6301 | 122.9277 | 61.4354 | 61.4893 | 123.053 | 61.4808 | 122.9319 | 61.5255 | 61.534 | 61.4384 | 61.4469
297.125 | 123.2437 | -61.4914 | 61.5921 | 0.021127 | -0.040521 | -0.007421 | -0.006703 | 0.017953 | -0.010563 | 0.015112 | 61.5371 | 0.14332 | 61.4684 | -0.060575 | 0.002454 | 61.5662 | -0.006014 | 61.4496 | 61.5125 | 61.4509 | 61.484 | 61.4847 | 61.5093 | 61.4808 | 61.5065 | 123.0285 | 61.6347 | 122.9597 | 61.4308 | 61.4938 | 123.0576 | 61.4854 | 122.941 | 61.5346 | 61.5431 | 61.4659 | 61.4744
298.0625 | 123.3032 | -61.4731 | 61.6013 | 0.034862 | -0.026784 | -0.012 | -0.011281 | 0.017953 | -0.001406 | 0.015112 | 61.5279 | 0.13874 | 61.4134 | -0.051417 | 0.01161 | 61.5662 | -0.006014 | 61.4451 | 61.5079 | 61.4463 | 61.4611 | 61.4618 | 61.491 | 61.4717 | 61.4882 | 123.001 | 61.6118 | 122.8865 | 61.4217 | 61.4847 | 123.0392 | 61.4671 | 122.9182 | 61.5163 | 61.534 | 61.4018 | 61.4194
299.0625 | 123.3032 | -61.4822 | 61.5829 | 0.025705 | -0.026784 | -0.012 | -0.006703 | 0.022531 | -0.001406 | 0.01969 | 61.5417 | 0.13874 | 61.4729 | -0.055996 | 0.007032 | 61.5662 | -0.006014 | 61.4496 | 61.5079 | 61.4555 | 61.4702 | 61.4755 | 61.5048 | 61.4808 | 61.5019 | 123.0239 | 61.621 | 122.9552 | 61.4262 | 61.4893 | 123.0484 | 61.4762 | 122.9319 | 61.5346 | 61.5477 | 61.4659 | 61.4789
300.125 | 123.2986 | -61.441 | 61.6104 | 0.025705 | -0.031363 | -0.012 | -0.006703 | 0.027109 | -0.005985 | 0.01969 | 61.5371 | 0.13874 | 61.4409 | -0.051417 | 0.007032 | 61.5616 | -0.006014 | 61.4496 | 61.4667 | 61.4097 | 61.429 | 61.4343 | 61.4681 | 61.4351 | 61.4607 | 122.9781 | 61.5798 | 122.8819 | 61.3896 | 61.4481 | 123.0026 | 61.435 | 122.8907 | 61.5301 | 61.5431 | 61.4339 | 61.4469
301.0625 | 123.2437 | -61.4822 | 61.6379 | 0.025705 | -0.040521 | -0.012 | -0.006703 | 0.017953 | -0.005985 | 0.015112 | 61.5279 | 0.1479 | 61.4409 | -0.060575 | 0.01161 | 61.557 | -0.001436 | 61.4451 | 61.5079 | 61.4417 | 61.4702 | 61.4755 | 61.5002 | 61.4763 | 61.4974 | 123.0102 | 61.6301 | 122.9231 | 61.4217 | 61.4938 | 123.0392 | 61.4808 | 122.9273 | 61.5163 | 61.5294 | 61.4293 | 61.4423
302.0625 | 123.2437 | -61.4777 | 61.6699 | 0.025705 | -0.040521 | -0.021157 | -0.011281 | 0.008797 | -0.005985 | 0.024268 | 61.5325 | 0.14332 | 61.4684 | -0.055996 | 0.007032 | 61.5707 | -0.010593 | 61.4451 | 61.5034 | 61.4371 | 61.4565 | 61.4664 | 61.4865 | 61.4717 | 61.5019 | 123.0102 | 61.621 | 122.946 | 61.4217 | 61.4847 | 123.0484 | 61.4671 | 122.9227 | 61.5255 | 61.5431 | 61.4613 | 61.4789
303.125 | 123.2483 | -61.5005 | 61.6379 | 0.021127 | -0.026784 | -0.016578 | -0.011281 | 0.017953 | -0.010563 | 0.01969 | 61.5279 | 0.13416 | 61.4134 | -0.051417 | 0.007032 | 61.557 | -0.006014 | 61.4496 | 61.5217 | 61.4738 | 61.484 | 61.4893 | 61.5185 | 61.49 | 61.5202 | 123.0285 | 61.6347 | 122.914 | 61.4491 | 61.5076 | 123.0576 | 61.4945 | 122.9502 | 61.5209 | 61.534 | 61.4064 | 61.4194
304.0625 | 123.3078 | -61.4822 | 61.5692 | 0.025705 | -0.035942 | -0.021157 | -0.006703 | 0.017953 | -0.001406 | 0.015112 | 61.5279 | 0.13416 | 61.4729 | -0.055996 | 0.01161 | 61.5662 | -0.006014 | 61.4588 | 61.5079 | 61.4463 | 61.4611 | 61.4755 | 61.5002 | 61.4808 | 61.4974 | 123.0102 | 61.6164 | 122.9552 | 61.4262 | 61.4938 | 123.0484 | 61.4762 | 122.941 | 61.5163 | 61.534 | 61.4613 | 61.4789
305.125 | 123.2162 | -61.4868 | 61.6379 | 0.021127 | -0.040521 | -0.012 | -0.011281 | 0.017953 | 0.003172 | 0.01969 | 61.5371 | 0.13874 | 61.45 | -0.051417 | 0.007032 | 61.5662 | -0.006014 | 61.4451 | 61.5079 | 61.4463 | 61.4748 | 61.4755 | 61.5048 | 61.49 | 61.5065 | 123.0239 | 61.6256 | 122.9369 | 61.4354 | 61.4938 | 123.053 | 61.4808 | 122.9319 | 61.5301 | 61.5431 | 61.443 | 61.4561
306.0625 | 123.317 | -61.4685 | 61.6379 | 0.034862 | -0.035942 | -0.016578 | -0.006703 | 0.022531 | -0.001406 | 0.028846 | 61.5371 | 0.1479 | 61.4317 | -0.055996 | 0.016188 | 61.5662 | -0.001436 | 61.4588 | 61.5034 | 61.4326 | 61.4519 | 61.4618 | 61.491 | 61.4671 | 61.4974 | 123.0056 | 61.6164 | 122.9002 | 61.4125 | 61.4847 | 123.0347 | 61.4671 | 122.9273 | 61.5209 | 61.5385 | 61.4155 | 61.4332
307.125 | 123.23 | -61.4731 | 61.615 | 0.025705 | -0.035942 | -0.012 | -0.002124 | 0.022531 | -0.005985 | 0.01969 | 61.5279 | 0.1479 | 61.4729 | -0.051417 | 0.007032 | 61.5616 | -0.001436 | 61.4496 | 61.4988 | 61.4371 | 61.4611 | 61.471 | 61.4956 | 61.4671 | 61.4928 | 123.001 | 61.621 | 122.946 | 61.4217 | 61.4801 | 123.0347 | 61.4716 | 122.9227 | 61.5209 | 61.5294 | 61.4659 | 61.4744
308.0625 | 123.2071 | -61.4868 | 61.6333 | 0.030283 | -0.035942 | -0.012 | -0.006703 | 0.013375 | 0.003172 | 0.01969 | 61.5371 | 0.14332 | 61.418 | -0.055996 | 0.002454 | 61.5662 | 0.003143 | 61.4405 | 61.5171 | 61.4509 | 61.4748 | 61.4801 | 61.5002 | 61.49 | 61.5065 | 123.0239 | 61.6301 | 122.9048 | 61.4308 | 61.4893 | 123.053 | 61.49 | 122.9273 | 61.5346 | 61.534 | 61.4155 | 61.4148
309.0625 | 123.317 | -61.5005 | 61.615 | 0.030283 | -0.0451 | -0.012 | -0.006703 | 0.008797 | -0.005985 | 0.01969 | 61.5417 | 0.15248 | 61.4729 | -0.060575 | 0.01161 | 61.5616 | -0.001436 | 61.4542 | 61.5308 | 61.4554 | 61.4885 | 61.4938 | 61.5093 | 61.4946 | 61.5202 | 123.0422 | 61.653 | 122.9735 | 61.44 | 61.5122 | 123.0621 | 61.4991 | 122.9548 | 61.5301 | 61.5431 | 61.4613 | 61.4744
310.125 | 123.3032 | -61.4548 | 61.647 | 0.030283 | -0.031363 | -0.016578 | 0.002454 | 0.017953 | -0.010563 | 0.01969 | 61.5417 | 0.1479 | 61.4317 | -0.051417 | 0.016188 | 61.5616 | 0.003143 | 61.4451 | 61.4851 | 61.4234 | 61.4382 | 61.4572 | 61.4727 | 61.4442 | 61.4745 | 122.9965 | 61.6027 | 122.8865 | 61.4034 | 61.471 | 123.0164 | 61.4579 | 122.8998 | 61.5255 | 61.5385 | 61.4155 | 61.4286
311.0625 | 123.2712 | -61.4868 | 61.6333 | 0.030283 | -0.035942 | -0.012 | -0.006703 | 0.022531 | -0.010563 | 0.01969 | 61.5279 | 0.1479 | 61.4271 | -0.051417 | 0.01161 | 61.5707 | -0.006014 | 61.4542 | 61.5171 | 61.4509 | 61.4748 | 61.4801 | 61.5093 | 61.4763 | 61.5065 | 123.0148 | 61.6347 | 122.914 | 61.4354 | 61.4984 | 123.0576 | 61.4808 | 122.941 | 61.5163 | 61.534 | 61.4155 | 61.4332
312.0625 | 123.2758 | -61.4639 | 61.6379 | 0.025705 | -0.040521 | -0.016578 | -0.011281 | 0.022531 | -0.001406 | 0.015112 | 61.5371 | 0.15248 | 61.4729 | -0.051417 | -0.002124 | 61.557 | -0.006014 | 61.4451 | 61.4896 | 61.4234 | 61.4474 | 61.4526 | 61.4865 | 61.4625 | 61.479 | 123.001 | 61.6164 | 122.9369 | 61.4125 | 61.4618 | 123.0209 | 61.4579 | 122.909 | 61.5392 | 61.5431 | 61.4751 | 61.4789
313.0625 | 123.2254 | -61.4639 | 61.6333 | 0.021127 | -0.026784 | -0.012 | -0.002124 | 0.017953 | -0.005985 | 0.01969 | 61.5325 | 0.14332 | 61.418 | -0.055996 | 0.01161 | 61.5616 | -0.010593 | 61.4451 | 61.4851 | 61.4371 | 61.4519 | 61.4618 | 61.4819 | 61.4579 | 61.4836 | 122.9964 | 61.6072 | 122.8819 | 61.4079 | 61.4755 | 123.0255 | 61.4533 | 122.909 | 61.5209 | 61.5431 | 61.4064 | 61.4286
314.1406 | 123.3536 | -61.4685 | 61.5921 | 0.025705 | -0.026784 | -0.012 | -0.006703 | 0.022531 | -0.005985 | 0.01969 | 61.5325 | 0.1479 | 61.4638 | -0.051417 | 0.002454 | 61.5616 | -0.010593 | 61.4405 | 61.4942 | 61.4417 | 61.4565 | 61.4618 | 61.491 | 61.4625 | 61.4882 | 123.001 | 61.6164 | 122.9323 | 61.4171 | 61.471 | 123.0301 | 61.4579 | 122.909 | 61.5301 | 61.5431 | 61.4613 | 61.4744
315.0625 | 123.2666 | -61.4685 | 61.6379 | 0.021127 | -0.035942 | -0.016578 | -0.006703 | 0.022531 | -0.001406 | 0.01969 | 61.5417 | 0.14332 | 61.4271 | -0.051417 | 0.01161 | 61.5616 | -0.006014 | 61.4451 | 61.4896 | 61.4326 | 61.4519 | 61.4618 | 61.491 | 61.4671 | 61.4882 | 123.0102 | 61.6118 | 122.8957 | 61.4171 | 61.4801 | 123.0301 | 61.4625 | 122.9136 | 61.5301 | 61.5477 | 61.4155 | 61.4332
316.0625 | 123.2941 | -61.4822 | 61.6516 | 0.021127 | -0.031363 | -0.021157 | -0.006703 | 0.022531 | -0.005985 | 0.015112 | 61.5371 | 0.14332 | 61.4271 | -0.055996 | 0.01161 | 61.557 | -0.001436 | 61.4451 | 61.5034 | 61.4509 | 61.4611 | 61.4755 | 61.5048 | 61.4763 | 61.4974 | 123.0193 | 61.6256 | 122.9094 | 61.4262 | 61.4938 | 123.0392 | 61.4808 | 122.9273 | 61.5255 | 61.5385 | 61.4155 | 61.4286
317.125 | 123.2117 | -61.5005 | 61.647 | 0.030283 | -0.035942 | -0.012 | -0.006703 | 0.027109 | -0.001406 | 0.028846 | 61.5371 | 0.13874 | 61.4775 | -0.055996 | 0.01161 | 61.5707 | -0.006014 | 61.4451 | 61.5308 | 61.4646 | 61.4885 | 61.4938 | 61.5277 | 61.4991 | 61.5294 | 123.0376 | 61.6393 | 122.9781 | 61.4446 | 61.5122 | 123.0713 | 61.4945 | 122.9456 | 61.5255 | 61.5431 | 61.4659 | 61.4835
318.0625 | 123.2941 | -61.5005 | 61.615 | 0.025705 | -0.040521 | -0.016578 | -0.011281 | 0.017953 | -0.001406 | 0.015112 | 61.5325 | 0.13874 | 61.4134 | -0.051417 | 0.01161 | 61.5662 | -0.010593 | 61.4451 | 61.5263 | 61.46 | 61.484 | 61.4893 | 61.5185 | 61.4991 | 61.5157 | 123.0331 | 61.6393 | 122.914 | 61.4491 | 61.5122 | 123.0667 | 61.49 | 122.9456 | 61.5209 | 61.5431 | 61.4018 | 61.424
319.1406 | 123.1934 | -61.4914 | 61.6287 | 0.030283 | -0.035942 | -0.012 | -0.006703 | 0.022531 | -0.005985 | 0.01969 | 61.5371 | 0.14332 | 61.4775 | -0.051417 | 0.01161 | 61.5616 | -0.006014 | 61.4451 | 61.5217 | 61.4555 | 61.4794 | 61.4847 | 61.5139 | 61.4854 | 61.5111 | 123.0285 | 61.6347 | 122.9689 | 61.44 | 61.503 | 123.053 | 61.4854 | 122.9365 | 61.5255 | 61.5431 | 61.4659 | 61.4835
320.0625 | 123.23 | -61.5005 | 61.6013 | 0.021127 | -0.040521 | -0.016578 | -0.011281 | 0.022531 | -0.005985 | 0.024268 | 61.5325 | 0.15248 | 61.4226 | -0.055996 | 0.007032 | 61.5616 | -0.006014 | 61.4542 | 61.5217 | 61.46 | 61.484 | 61.4893 | 61.5231 | 61.4946 | 61.5248 | 123.0331 | 61.653 | 122.9231 | 61.4446 | 61.5076 | 123.0621 | 61.4945 | 122.9548 | 61.5255 | 61.5385 | 61.4155 | 61.4286
321.0625 | 123.2986 | -61.4914 | 61.6333 | 0.034862 | -0.026784 | -0.016578 | -0.002124 | 0.027109 | -0.001406 | 0.024268 | 61.5325 | 0.14332 | 61.4409 | -0.051417 | 0.016188 | 61.5616 | -0.010593 | 61.4496 | 61.5263 | 61.4646 | 61.4748 | 61.4893 | 61.5185 | 61.49 | 61.5157 | 123.0239 | 61.6347 | 122.9323 | 61.44 | 61.5076 | 123.053 | 61.4808 | 122.941 | 61.5163 | 61.5431 | 61.4247 | 61.4515
322.0625 | 123.23 | -61.4685 | 61.6425 | 0.025705 | -0.031363 | -0.021157 | -0.011281 | 0.013375 | -0.015142 | 0.01969 | 61.5371 | 0.1479 | 61.4729 | -0.046838 | 0.016188 | 61.5616 | -0.006014 | 61.4496 | 61.4942 | 61.4371 | 61.4473 | 61.4572 | 61.4819 | 61.4534 | 61.4882 | 123.0056 | 61.6164 | 122.9414 | 61.4217 | 61.4847 | 123.0301 | 61.4625 | 122.9182 | 61.5209 | 61.5431 | 61.4567 | 61.4789
323.125 | 123.2666 | -61.4594 | 61.6287 | 0.025705 | -0.035942 | -0.021157 | -0.006703 | 0.017953 | -0.001406 | 0.024268 | 61.5371 | 0.1479 | 61.4226 | -0.060575 | 0.002454 | 61.5662 | -0.006014 | 61.4496 | 61.4851 | 61.4234 | 61.4382 | 61.4526 | 61.4773 | 61.4579 | 61.4836 | 122.9965 | 61.6073 | 122.8819 | 61.3988 | 61.4618 | 123.0255 | 61.4533 | 122.909 | 61.5346 | 61.5431 | 61.4201 | 61.4286
324.0625 | 123.262 | -61.4822 | 61.6241 | 0.025705 | -0.035942 | -0.007421 | 0.002454 | 0.017953 | -0.001406 | 0.01969 | 61.5417 | 0.14332 | 61.4867 | -0.055996 | 0.016188 | 61.5616 | -0.015171 | 61.4359 | 61.5079 | 61.4463 | 61.4748 | 61.4847 | 61.5002 | 61.4808 | 61.5019 | 123.0239 | 61.6256 | 122.9689 | 61.4262 | 61.4984 | 123.0438 | 61.4671 | 122.9182 | 61.5255 | 61.5568 | 61.4705 | 61.5018
325.0625 | 123.2529 | -61.4548 | 61.6516 | 0.025705 | -0.031363 | -0.016578 | -0.011281 | 0.017953 | -0.010563 | 0.01969 | 61.5279 | 0.14332 | 61.4226 | -0.051417 | 0.01161 | 61.5616 | -0.006014 | 61.4405 | 61.4805 | 61.4234 | 61.4382 | 61.4435 | 61.4727 | 61.4442 | 61.4745 | 122.9827 | 61.5981 | 122.8773 | 61.4034 | 61.4664 | 123.0164 | 61.4488 | 122.8953 | 61.5163 | 61.534 | 61.411 | 61.4286
326.125 | 123.2758 | -61.5005 | 61.6379 | 0.025705 | -0.040521 | -0.012 | -0.006703 | 0.017953 | -0.015142 | 0.024268 | 61.5325 | 0.1479 | 61.4317 | -0.060575 | 0.01161 | 61.5753 | -0.006014 | 61.4451 | 61.5263 | 61.46 | 61.4885 | 61.4938 | 61.5185 | 61.4854 | 61.5248 | 123.0331 | 61.6484 | 122.9323 | 61.44 | 61.5122 | 123.0759 | 61.4945 | 122.9456 | 61.5209 | 61.5385 | 61.4201 | 61.4377
327.0625 | 123.2941 | -61.4914 | 61.6287 | 0.030283 | -0.031363 | -0.016578 | -0.006703 | 0.022531 | -0.001406 | 0.01969 | 61.5417 | 0.1479 | 61.4729 | -0.051417 | 0.007032 | 61.557 | -0.010593 | 61.4451 | 61.5217 | 61.46 | 61.4748 | 61.4847 | 61.5139 | 61.49 | 61.5111 | 123.0331 | 61.6393 | 122.9643 | 61.44 | 61.4984 | 123.0484 | 61.4808 | 122.9365 | 61.5346 | 61.5523 | 61.4659 | 61.4835
328.0625 | 123.2391 | -61.4868 | 61.6516 | 0.025705 | -0.031363 | -0.016578 | -0.011281 | 0.017953 | -0.005985 | 0.024268 | 61.5279 | 0.1479 | 61.4043 | -0.051417 | 0.01161 | 61.5662 | -0.006014 | 61.4496 | 61.5125 | 61.4555 | 61.4702 | 61.4755 | 61.5048 | 61.4808 | 61.5111 | 123.0148 | 61.6347 | 122.8911 | 61.4354 | 61.4984 | 123.053 | 61.4808 | 122.9365 | 61.5163 | 61.534 | 61.3926 | 61.4103
329.0625 | 123.2849 | -61.4456 | 61.6196 | 0.030283 | -0.031363 | -0.016578 | 0.007033 | 0.031687 | -0.005985 | 0.010533 | 61.5325 | 0.1479 | 61.4729 | -0.055996 | 0.016188 | 61.557 | -0.001436 | 61.4451 | 61.4759 | 61.4143 | 61.429 | 61.4527 | 61.4773 | 61.4396 | 61.4562 | 122.9781 | 61.5935 | 122.9186 | 61.3896 | 61.4618 | 123.0026 | 61.4442 | 122.8907 | 61.5163 | 61.534 | 61.4567 | 61.4744
330.0625 | 123.2574 | -61.4777 | 61.647 | 0.025705 | -0.031363 | -0.021157 | -0.002124 | 0.022531 | -0.005985 | 0.024268 | 61.5279 | 0.15248 | 61.418 | -0.055996 | 0.01161 | 61.5616 | -0.001436 | 61.4496 | 61.5034 | 61.4463 | 61.4565 | 61.4755 | 61.5002 | 61.4717 | 61.5019 | 123.0056 | 61.6301 | 122.8957 | 61.4217 | 61.4893 | 123.0392 | 61.4762 | 122.9273 | 61.5163 | 61.5294 | 61.4064 | 61.4194
331.125 | 123.2529 | -61.4594 | 61.6562 | 0.025705 | -0.031363 | -0.007421 | -0.011281 | 0.022531 | -0.005985 | 0.015112 | 61.5371 | 0.14332 | 61.4317 | -0.055996 | 0.01161 | 61.5616 | 0.003143 | 61.4496 | 61.4851 | 61.428 | 61.4519 | 61.4481 | 61.4819 | 61.4534 | 61.4745 | 122.9965 | 61.6027 | 122.8911 | 61.4034 | 61.471 | 123.0209 | 61.4625 | 122.909 | 61.5255 | 61.534 | 61.4201 | 61.4286
332.0625 | 123.2162 | -61.496 | 61.6379 | 0.034862 | -0.040521 | -0.021157 | 0.002454 | 0.022531 | -0.001406 | 0.028846 | 61.5417 | 0.1479 | 61.4592 | -0.055996 | 0.002454 | 61.5662 | -0.010593 | 61.4451 | 61.5308 | 61.4555 | 61.4748 | 61.4984 | 61.5185 | 61.4946 | 61.5248 | 123.0376 | 61.6439 | 122.9552 | 61.44 | 61.4984 | 123.0621 | 61.4854 | 122.941 | 61.5392 | 61.5523 | 61.4567 | 61.4698
333.0625 | 123.2712 | -61.4594 | 61.6653 | 0.025705 | -0.040521 | -0.025735 | -0.006703 | 0.017953 | -0.001406 | 0.01969 | 61.5325 | 0.1479 | 61.4271 | -0.055996 | 0.01161 | 61.5662 | -0.006014 | 61.4359 | 61.4851 | 61.4188 | 61.4336 | 61.4526 | 61.4773 | 61.4579 | 61.479 | 122.9919 | 61.6073 | 122.8865 | 61.4034 | 61.471 | 123.0255 | 61.4533 | 122.8953 | 61.5209 | 61.5385 | 61.4155 | 61.4332
334.1406 | 123.2483 | -61.5005 | 61.6013 | 0.025705 | -0.035942 | -0.016578 | -0.006703 | 0.013375 | -0.001406 | 0.024268 | 61.5371 | 0.14332 | 61.4638 | -0.060575 | 0.007032 | 61.5707 | -0.015171 | 61.4405 | 61.5263 | 61.4646 | 61.484 | 61.4938 | 61.5139 | 61.4991 | 61.5248 | 123.0376 | 61.6439 | 122.9643 | 61.44 | 61.5076 | 123.0713 | 61.4854 | 122.941 | 61.5301 | 61.5523 | 61.4567 | 61.4789
335.0625 | 123.3627 | -61.4731 | 61.5921 | 0.021127 | -0.040521 | -0.021157 | -0.006703 | 0.022531 | -0.010563 | 0.01969 | 61.5325 | 0.14332 | 61.4271 | -0.055996 | 0.01161 | 61.5616 | -0.006014 | 61.4496 | 61.4942 | 61.4326 | 61.4519 | 61.4664 | 61.4956 | 61.4625 | 61.4928 | 123.0056 | 61.6164 | 122.9002 | 61.4171 | 61.4847 | 123.0347 | 61.4671 | 122.9227 | 61.5209 | 61.5385 | 61.4155 | 61.4332
336.0625 | 123.3032 | -61.4822 | 61.6287 | 0.025705 | -0.035942 | -0.016578 | -0.006703 | 0.017953 | -0.005985 | 0.01969 | 61.5325 | 0.14332 | 61.4409 | -0.055996 | 0.01161 | 61.5616 | -0.006014 | 61.4359 | 61.5079 | 61.4463 | 61.4657 | 61.4755 | 61.5002 | 61.4763 | 61.5019 | 123.0148 | 61.6256 | 122.9231 | 61.4262 | 61.4938 | 123.0438 | 61.4762 | 122.9182 | 61.5209 | 61.5385 | 61.4293 | 61.4469
337.125 | 123.2208 | -61.5097 | 61.6333 | 0.030283 | -0.026784 | -0.012 | -0.002124 | 0.017953 | -0.001406 | 0.024268 | 61.5463 | 0.14332 | 61.4638 | -0.060575 | 0.002454 | 61.5662 | -0.010593 | 61.4405 | 61.54 | 61.4829 | 61.4977 | 61.5076 | 61.5277 | 61.5083 | 61.534 | 123.056 | 61.653 | 122.9735 | 61.4491 | 61.5122 | 123.0759 | 61.4991 | 122.9502 | 61.5438 | 61.5568 | 61.4613 | 61.4744
338.0625 | 123.2574 | -61.4914 | 61.6516 | 0.025705 | -0.031363 | -0.012 | -0.006703 | 0.013375 | -0.005985 | 0.010533 | 61.5371 | 0.13874 | 61.418 | -0.055996 | 0.002454 | 61.5707 | -0.001436 | 61.4405 | 61.5171 | 61.46 | 61.4794 | 61.4847 | 61.5048 | 61.4854 | 61.5019 | 123.0285 | 61.6301 | 122.9094 | 61.4354 | 61.4938 | 123.0621 | 61.49 | 122.9319 | 61.5346 | 61.5385 | 61.4155 | 61.4194
339.0625 | 123.3032 | -61.4639 | 61.6287 | 0.025705 | -0.026784 | -0.012 | 0.002454 | 0.022531 | -0.001406 | 0.01969 | 61.5417 | 0.14332 | 61.4684 | -0.055996 | 0.01161 | 61.5707 | -0.001436 | 61.4405 | 61.4896 | 61.4371 | 61.4519 | 61.4664 | 61.4865 | 61.4625 | 61.4836 | 123.0056 | 61.6072 | 122.9323 | 61.4079 | 61.4755 | 123.0347 | 61.4625 | 122.9044 | 61.5301 | 61.5431 | 61.4567 | 61.4698
340.125 | 123.262 | -61.4777 | 61.6516 | 0.025705 | -0.035942 | -0.016578 | 0.002454 | 0.027109 | -0.005985 | 0.01969 | 61.5279 | 0.1479 | 61.4226 | -0.055996 | 0.016188 | 61.5662 | 0.003143 | 61.4451 | 61.5034 | 61.4417 | 61.4611 | 61.4801 | 61.5048 | 61.4717 | 61.4974 | 123.0056 | 61.6256 | 122.9002 | 61.4217 | 61.4938 | 123.0438 | 61.4808 | 122.9227 | 61.5118 | 61.5248 | 61.4064 | 61.4194
341.0625 | 123.2208 | -61.4456 | 61.6653 | 0.025705 | -0.040521 | -0.016578 | -0.006703 | 0.022531 | -0.001406 | 0.024268 | 61.5417 | 0.15706 | 61.4409 | -0.055996 | 0.002454 | 61.5707 | -0.010593 | 61.4359 | 61.4713 | 61.4051 | 61.429 | 61.4389 | 61.4681 | 61.4442 | 61.4699 | 122.9873 | 61.6027 | 122.8865 | 61.3896 | 61.4481 | 123.0164 | 61.435 | 122.8815 | 61.5392 | 61.5523 | 61.4384 | 61.4515
342.125 | 123.2483 | -61.4914 | 61.6241 | 0.034862 | -0.026784 | -0.007421 | -0.006703 | 0.022531 | -0.001406 | 0.015112 | 61.5463 | 0.14332 | 61.4729 | -0.051417 | 0.002454 | 61.5616 | -0.006014 | 61.4359 | 61.5263 | 61.4646 | 61.484 | 61.4847 | 61.5139 | 61.49 | 61.5065 | 123.0377 | 61.6347 | 122.9643 | 61.44 | 61.4938 | 123.053 | 61.4854 | 122.9273 | 61.5438 | 61.5523 | 61.4705 | 61.4789
343.0625 | 123.3444 | -61.4594 | 61.6287 | 0.025705 | -0.035942 | -0.016578 | -0.006703 | 0.022531 | -0.005985 | 0.015112 | 61.5325 | 0.14332 | 61.4271 | -0.051417 | 0.01161 | 61.5616 | 0.003143 | 61.4451 | 61.4851 | 61.4234 | 61.4428 | 61.4526 | 61.4819 | 61.4534 | 61.4745 | 122.9919 | 61.6027 | 122.8865 | 61.4079 | 61.471 | 123.0209 | 61.4625 | 122.9044 | 61.5209 | 61.5294 | 61.4155 | 61.424
344.0625 | 123.3948 | -61.4548 | 61.5646 | 0.030283 | -0.022205 | -0.021157 | -0.006703 | 0.017953 | -0.005985 | 0.015112 | 61.5371 | 0.13874 | 61.4729 | -0.060575 | 0.01161 | 61.5616 | -0.006014 | 61.4405 | 61.4851 | 61.4326 | 61.4336 | 61.4481 | 61.4727 | 61.4488 | 61.4699 | 122.9919 | 61.5935 | 122.9277 | 61.3942 | 61.4664 | 123.0164 | 61.4488 | 122.8953 | 61.5255 | 61.5431 | 61.4613 | 61.4789
345.125 | 123.2391 | -61.496 | 61.6058 | 0.030283 | -0.040521 | -0.007421 | 0.002454 | 0.017953 | -0.001406 | 0.024268 | 61.5279 | 0.1479 | 61.418 | -0.060575 | 0.002454 | 61.5707 | 0.003143 | 61.4313 | 61.5263 | 61.4555 | 61.4886 | 61.4984 | 61.5139 | 61.4946 | 61.5202 | 123.0239 | 61.6439 | 122.914 | 61.4354 | 61.4984 | 123.0667 | 61.4991 | 122.9273 | 61.5255 | 61.5248 | 61.4155 | 61.4148
346.0625 | 123.2941 | -61.4777 | 61.6379 | 0.021127 | -0.040521 | -0.016578 | -0.006703 | 0.022531 | -0.005985 | 0.01969 | 61.5417 | 0.15248 | 61.4455 | -0.055996 | 0.01161 | 61.5707 | -0.006014 | 61.4405 | 61.4988 | 61.4371 | 61.4611 | 61.471 | 61.5002 | 61.4717 | 61.4974 | 123.0193 | 61.6301 | 122.9231 | 61.4217 | 61.4893 | 123.0484 | 61.4716 | 122.9182 | 61.5301 | 61.5477 | 61.4339 | 61.4515
347.2344 | 123.3856 | -61.4639 | 61.615 | 0.025705 | -0.031363 | -0.016578 | -0.006703 | 0.027109 | -0.005985 | 0.024268 | 61.5371 | 0.14332 | 61.4775 | -0.051417 | 0.002454 | 61.5707 | -0.006014 | 61.4451 | 61.4896 | 61.4326 | 61.4474 | 61.4572 | 61.491 | 61.4579 | 61.4882 | 123.001 | 61.6072 | 122.9414 | 61.4125 | 61.4664 | 123.0347 | 61.4579 | 122.909 | 61.5346 | 61.5431 | 61.4751 | 61.4835
348.0625 | 123.262 | -61.4868 | 61.6104 | 0.034862 | -0.026784 | -0.012 | -0.002124 | 0.022531 | -0.001406 | 0.010533 | 61.5325 | 0.15248 | 61.418 | -0.051417 | 0.007032 | 61.5616 | -0.010593 | 61.4405 | 61.5217 | 61.46 | 61.4748 | 61.4847 | 61.5093 | 61.4854 | 61.4973 | 123.0193 | 61.6393 | 122.9048 | 61.4354 | 61.4938 | 123.0484 | 61.4762 | 122.9273 | 61.5255 | 61.5431 | 61.411 | 61.4286
349.0781 | 123.3124 | -61.4822 | 61.647 | 0.030283 | -0.031363 | -0.007421 | -0.002124 | 0.017953 | -0.010563 | 0.024268 | 61.5417 | 0.1479 | 61.4821 | -0.051417 | 0.016188 | 61.5616 | -0.006014 | 61.4451 | 61.5125 | 61.4509 | 61.4748 | 61.4801 | 61.5002 | 61.4717 | 61.5065 | 123.0239 | 61.6301 | 122.9643 | 61.4308 | 61.4984 | 123.0438 | 61.4762 | 122.9273 | 61.5255 | 61.5477 | 61.4659 | 61.4881
350.375 | 123.2391 | -61.4868 | 61.6379 | 0.030283 | -0.031363 | -0.016578 | -0.006703 | 0.027109 | -0.001406 | 0.015112 | 61.5417 | 0.14332 | 61.4592 | -0.051417 | 0.01161 | 61.5662 | -0.006014 | 61.4405 | 61.5171 | 61.4555 | 61.4702 | 61.4801 | 61.5139 | 61.4854 | 61.5019 | 123.0285 | 61.6301 | 122.946 | 61.4354 | 61.4984 | 123.053 | 61.4808 | 122.9273 | 61.5301 | 61.5477 | 61.4476 | 61.4652
351.1406 | 123.2666 | -61.5005 | 61.615 | 0.03944 | -0.022205 | -0.016578 | -0.006703 | 0.017953 | -0.001406 | 0.01969 | 61.5417 | 0.1479 | 61.4363 | -0.065154 | 0.01161 | 61.5662 | -0.006014 | 61.4405 | 61.54 | 61.4783 | 61.484 | 61.4938 | 61.5185 | 61.4991 | 61.5202 | 123.0422 | 61.6484 | 122.9369 | 61.4354 | 61.5122 | 123.0667 | 61.4945 | 122.941 | 61.5301 | 61.5477 | 61.4247 | 61.4423
352.7031 | 123.3261 | -61.4731 | 61.6196 | 0.025705 | -0.031363 | -0.012 | -0.011281 | 0.017953 | -0.005985 | 0.01969 | 61.5325 | 0.1479 | 61.4684 | -0.060575 | 0.01161 | 61.5707 | -0.006014 | 61.4496 | 61.4988 | 61.4417 | 61.4611 | 61.4618 | 61.491 | 61.4671 | 61.4928 | 123.0056 | 61.621 | 122.9414 | 61.4125 | 61.4847 | 123.0438 | 61.4671 | 122.9227 | 61.5209 | 61.5385 | 61.4567 | 61.4744
353.2969 | 123.3536 | -61.4548 | 61.5646 | 0.030283 | -0.035942 | -0.016578 | -0.011281 | 0.017953 | 0.003172 | 0.01969 | 61.5325 | 0.1479 | 61.418 | -0.060575 | 0.007032 | 61.5616 | -0.001436 | 61.4496 | 61.4851 | 61.4188 | 61.4382 | 61.4435 | 61.4727 | 61.4579 | 61.4745 | 122.9873 | 61.6027 | 122.8728 | 61.3942 | 61.4618 | 123.0164 | 61.4533 | 122.9044 | 61.5255 | 61.534 | 61.411 | 61.4194
355.1719 | 123.3032 | -61.4914 | 61.6196 | 0.034862 | -0.040521 | -0.016578 | -0.006703 | 0.027109 | -0.005985 | 0.024268 | 61.5417 | 0.1479 | 61.4271 | -0.055996 | 0.01161 | 61.5616 | -0.006014 | 61.4451 | 61.5263 | 61.4509 | 61.4748 | 61.4847 | 61.5185 | 61.4854 | 61.5157 | 123.0331 | 61.6393 | 122.9185 | 61.4354 | 61.503 | 123.053 | 61.4854 | 122.9365 | 61.5301 | 61.5477 | 61.4155 | 61.4332
355.75 | 123.2346 | -61.4639 | 61.6013 | 0.025705 | -0.031363 | -0.021157 | -0.011281 | 0.022531 | -0.001406 | 0.024268 | 61.5417 | 0.1479 | 61.4684 | -0.060575 | 0.01161 | 61.5616 | -0.006014 | 61.4405 | 61.4896 | 61.4326 | 61.4428 | 61.4526 | 61.4865 | 61.4625 | 61.4882 | 123.0056 | 61.6118 | 122.9323 | 61.4034 | 61.4755 | 123.0255 | 61.4579 | 122.9044 | 61.5301 | 61.5477 | 61.4567 | 61.4744
356.5 | 123.3673 | -61.4456 | 61.5829 | 0.030283 | -0.031363 | -0.016578 | -0.006703 | 0.022531 | -0.010563 | 0.015112 | 61.5325 | 0.1479 | 61.4088 | -0.051417 | 0.01161 | 61.5662 | -0.006014 | 61.4451 | 61.4759 | 61.4143 | 61.429 | 61.4389 | 61.4681 | 61.4351 | 61.4607 | 122.9781 | 61.5935 | 122.8545 | 61.3942 | 61.4572 | 123.0118 | 61.4396 | 122.8907 | 61.5209 | 61.5385 | 61.3972 | 61.4149
357.0625 | 123.381 | -61.4502 | 61.6058 | 0.016548 | -0.031363 | -0.012 | -0.006703 | 0.017953 | -0.001406 | 0.01969 | 61.5371 | 0.15248 | 61.4638 | -0.055996 | 0.01161 | 61.5662 | 0.003143 | 61.4359 | 61.4667 | 61.4188 | 61.4382 | 61.4435 | 61.4681 | 61.4488 | 61.4699 | 122.9873 | 61.6027 | 122.914 | 61.3942 | 61.4618 | 123.0164 | 61.4533 | 122.8861 | 61.5255 | 61.534 | 61.4522 | 61.4606
358.0781 | 123.2986 | -61.4777 | 61.6653 | 0.030283 | -0.035942 | -0.007421 | -0.011281 | 0.027109 | -0.010563 | 0.01969 | 61.5325 | 0.15248 | 61.418 | -0.055996 | 0.007032 | 61.5616 | -0.006014 | 61.4313 | 61.5079 | 61.4417 | 61.4702 | 61.4664 | 61.5048 | 61.4671 | 61.4974 | 123.0102 | 61.6301 | 122.8957 | 61.4217 | 61.4847 | 123.0392 | 61.4716 | 122.909 | 61.5255 | 61.5385 | 61.411 | 61.424
359.0938 | 123.2803 | -61.4822 | 61.647 | 0.030283 | -0.040521 | -0.016578 | -0.006703 | 0.013375 | -0.001406 | 0.015112 | 61.5417 | 0.1479 | 61.4775 | -0.065154 | 0.016188 | 61.5707 | -0.001436 | 61.4268 | 61.5125 | 61.4417 | 61.4657 | 61.4755 | 61.4956 | 61.4808 | 61.4974 | 123.0239 | 61.6301 | 122.9597 | 61.4171 | 61.4984 | 123.053 | 61.4808 | 122.909 | 61.5255 | 61.5431 | 61.4613 | 61.4789
360.0938 | 123.3902 | -61.4456 | 61.5601 | 0.025705 | -0.040521 | -0.021157 | -0.002124 | 0.017953 | -0.010563 | 0.024268 | 61.5279 | 0.14332 | 61.418 | -0.060575 | 0.01161 | 61.5707 | -0.006014 | 61.4405 | 61.4713 | 61.4051 | 61.4245 | 61.4435 | 61.4636 | 61.4351 | 61.4699 | 122.9736 | 61.5889 | 122.8636 | 61.385 | 61.4572 | 123.0164 | 61.4396 | 122.8861 | 61.5163 | 61.534 | 61.4064 | 61.424
361.0625 | 123.3307 | -61.4639 | 61.6058 | 0.021127 | -0.040521 | -0.016578 | -0.01586 | 0.022531 | -0.010563 | 0.024268 | 61.5371 | 0.1479 | 61.4409 | -0.051417 | 0.01161 | 61.5662 | -0.001436 | 61.4359 | 61.4851 | 61.4234 | 61.4474 | 61.4481 | 61.4865 | 61.4534 | 61.4882 | 123.001 | 61.6118 | 122.9048 | 61.4125 | 61.4755 | 123.0301 | 61.4625 | 122.8998 | 61.5255 | 61.5385 | 61.4293 | 61.4423
365.0781 | 123.3353 | -61.4639 | 61.5646 | 0.025705 | -0.0451 | -0.016578 | -0.011281 | 0.013375 | -0.001406 | 0.015112 | 61.5371 | 0.15248 | 61.4271 | -0.051417 | 0.01161 | 61.5662 | -0.001436 | 61.4451 | 61.4896 | 61.4188 | 61.4474 | 61.4526 | 61.4773 | 61.4625 | 61.479 | 123.001 | 61.6164 | 122.8911 | 61.4125 | 61.4755 | 123.0301 | 61.4625 | 122.909 | 61.5255 | 61.5385 | 61.4155 | 61.4286
365.4844 | 123.2758 | -61.441 | 61.6013 | 0.034862 | -0.035942 | -0.012 | -0.011281 | 0.022531 | -0.005985 | 0.01969 | 61.5417 | 0.14332 | 61.4729 | -0.051417 | 0.01161 | 61.557 | -0.006014 | 61.4451 | 61.4759 | 61.4051 | 61.429 | 61.4298 | 61.4636 | 61.4351 | 61.4607 | 122.9827 | 61.5844 | 122.914 | 61.3896 | 61.4526 | 122.998 | 61.435 | 122.8861 | 61.5301 | 61.5477 | 61.4613 | 61.4789
366.0781 | 123.3398 | -61.5005 | 61.5921 | 0.030283 | -0.040521 | -0.016578 | -0.002124 | 0.022531 | -0.005985 | 0.024268 | 61.5417 | 0.15248 | 61.4271 | -0.060575 | 0.01161 | 61.5707 | -0.010593 | 61.4451 | 61.5308 | 61.46 | 61.484 | 61.4984 | 61.5231 | 61.4946 | 61.5248 | 123.0422 | 61.653 | 122.9277 | 61.44 | 61.5122 | 123.0713 | 61.49 | 122.9456 | 61.5301 | 61.5523 | 61.4155 | 61.4377
367.0625 | 123.3765 | -61.4594 | 61.5921 | 0.025705 | -0.035942 | -0.016578 | -0.002124 | 0.022531 | -0.001406 | 0.015112 | 61.5463 | 0.1479 | 61.4638 | -0.055996 | 0.007032 | 61.5616 | -0.010593 | 61.4405 | 61.4851 | 61.4234 | 61.4428 | 61.4572 | 61.4819 | 61.4579 | 61.4745 | 123.0056 | 61.6073 | 122.9231 | 61.4034 | 61.4664 | 123.0209 | 61.4488 | 122.8998 | 61.5392 | 61.5568 | 61.4567 | 61.4744
368.0625 | 123.2895 | -61.4731 | 61.6196 | 0.025705 | -0.0451 | -0.021157 | -0.002124 | 0.017953 | -0.001406 | 0.015112 | 61.5279 | 0.14332 | 61.418 | -0.055996 | 0.007032 | 61.5662 | -0.006014 | 61.4451 | 61.4988 | 61.428 | 61.4519 | 61.471 | 61.491 | 61.4717 | 61.4882 | 123.001 | 61.6164 | 122.8911 | 61.4171 | 61.4801 | 123.0392 | 61.4671 | 122.9182 | 61.5209 | 61.534 | 61.411 | 61.424
369.0625 | 123.3078 | -61.4548 | 61.6058 | 0.030283 | -0.040521 | -0.012 | -0.006703 | 0.017953 | -0.005985 | 0.024268 | 61.5417 | 0.1479 | 61.4684 | -0.051417 | 0.01161 | 61.5662 | -0.006014 | 61.4268 | 61.4851 | 61.4143 | 61.4428 | 61.4481 | 61.4727 | 61.4488 | 61.479 | 122.9965 | 61.6027 | 122.9231 | 61.4034 | 61.4664 | 123.0209 | 61.4488 | 122.8815 | 61.5301 | 61.5477 | 61.4567 | 61.4744
370.0625 | 123.3261 | -61.4319 | 61.615 | 0.025705 | -0.035942 | -0.021157 | -0.006703 | 0.022531 | -0.005985 | 0.015112 | 61.5371 | 0.14332 | 61.4226 | -0.055996 | 0.01161 | 61.5662 | -0.010593 | 61.413 | 61.4576 | 61.3959 | 61.4107 | 61.4252 | 61.4544 | 61.4259 | 61.447 | 122.969 | 61.5752 | 122.8545 | 61.3759 | 61.4435 | 122.998 | 61.4213 | 122.8449 | 61.5255 | 61.5477 | 61.411 | 61.4332
371.0625 | 123.23 | -61.4594 | 61.647 | 0.034862 | -0.035942 | -0.012 | -0.006703 | 0.017953 | -0.005985 | 0.024268 | 61.5371 | 0.15248 | 61.4363 | -0.051417 | 0.016188 | 61.5707 | -0.001436 | 61.4496 | 61.4942 | 61.4234 | 61.4474 | 61.4526 | 61.4773 | 61.4534 | 61.4836 | 122.9965 | 61.6118 | 122.8957 | 61.4079 | 61.4755 | 123.0301 | 61.4579 | 122.909 | 61.5209 | 61.5385 | 61.4201 | 61.4377
372.0625 | 123.3078 | -61.4594 | 61.6196 | 0.034862 | -0.026784 | -0.016578 | -0.002124 | 0.017953 | 0.003172 | 0.01969 | 61.5417 | 0.15248 | 61.4684 | -0.046838 | 0.016188 | 61.5707 | -0.010593 | 61.4222 | 61.4942 | 61.4326 | 61.4428 | 61.4572 | 61.4773 | 61.4625 | 61.479 | 123.001 | 61.6118 | 122.9277 | 61.4125 | 61.4755 | 123.0301 | 61.4488 | 122.8815 | 61.5255 | 61.5523 | 61.4522 | 61.4789
373.0625 | 123.2666 | -61.4502 | 61.6562 | 0.025705 | -0.0451 | -0.016578 | -0.011281 | 0.022531 | -0.001406 | 0.01969 | 61.5325 | 0.13416 | 61.418 | -0.051417 | 0.01161 | 61.5753 | -0.006014 | 61.4268 | 61.4759 | 61.4051 | 61.4336 | 61.4389 | 61.4727 | 61.4488 | 61.4699 | 122.9827 | 61.5844 | 122.8682 | 61.3988 | 61.4618 | 123.0255 | 61.4442 | 122.877 | 61.5209 | 61.5385 | 61.4064 | 61.424
374.0625 | 123.175 | -61.4685 | 61.6425 | 0.025705 | -0.0451 | -0.016578 | -0.011281 | 0.017953 | -0.001406 | 0.024268 | 61.5463 | 0.1479 | 61.4867 | -0.060575 | 0.01161 | 61.5707 | -0.010593 | 61.381 | 61.4942 | 61.4234 | 61.4519 | 61.4572 | 61.4865 | 61.4671 | 61.4928 | 123.0148 | 61.6164 | 122.9552 | 61.4079 | 61.4801 | 123.0392 | 61.4579 | 122.8495 | 61.5346 | 61.5568 | 61.4751 | 61.4973
375.0625 | 123.2391 | -61.4777 | 61.6333 | 0.030283 | -0.0451 | -0.016578 | -0.011281 | 0.027109 | -0.005985 | 0.024268 | 61.5371 | 0.1479 | 61.4363 | -0.069733 | 0.016188 | 61.5707 | -0.001436 | 61.381 | 61.5079 | 61.4326 | 61.4611 | 61.4664 | 61.5048 | 61.4717 | 61.5019 | 123.0148 | 61.6256 | 122.914 | 61.4079 | 61.4938 | 123.0484 | 61.4762 | 122.8586 | 61.5209 | 61.5385 | 61.4201 | 61.4377
376.0625 | 123.3078 | -61.4685 | 61.6333 | 0.021127 | -0.035942 | -0.016578 | -0.006703 | 0.022531 | -0.001406 | 0.015112 | 61.5371 | 0.14332 | 61.4271 | -0.055996 | 0.016188 | 61.5753 | 0.003143 | 61.4039 | 61.4896 | 61.4326 | 61.4519 | 61.4618 | 61.491 | 61.4671 | 61.4836 | 123.0056 | 61.6118 | 122.8957 | 61.4125 | 61.4847 | 123.0438 | 61.4716 | 122.8724 | 61.5209 | 61.534 | 61.411 | 61.424
377.0625 | 123.2437 | -61.4777 | 61.6379 | 0.034862 | -0.035942 | -0.016578 | -0.002124 | 0.027109 | 0.003172 | 0.028846 | 61.5371 | 0.1479 | 61.4684 | -0.055996 | 0.007032 | 61.5616 | -0.001436 | 61.413 | 61.5125 | 61.4417 | 61.4611 | 61.4755 | 61.5048 | 61.4808 | 61.5065 | 123.0148 | 61.6256 | 122.946 | 61.4217 | 61.4847 | 123.0392 | 61.4762 | 122.8907 | 61.5301 | 61.5385 | 61.4613 | 61.4698
378.0625 | 123.2803 | -61.4639 | 61.6425 | 0.030283 | -0.040521 | -0.021157 | -0.006703 | 0.022531 | -0.001406 | 0.01969 | 61.5417 | 0.1479 | 61.4271 | -0.051417 | 0.01161 | 61.5707 | -0.006014 | 61.4405 | 61.4942 | 61.4234 | 61.4428 | 61.4572 | 61.4865 | 61.4625 | 61.4836 | 123.0056 | 61.6118 | 122.8911 | 61.4125 | 61.4755 | 123.0347 | 61.4579 | 122.9044 | 61.5301 | 61.5477 | 61.4155 | 61.4332
379.0625 | 123.262 | -61.496 | 61.6425 | 0.025705 | -0.035942 | -0.016578 | -0.011281 | 0.013375 | -0.005985 | 0.015112 | 61.5417 | 0.1479 | 61.45 | -0.055996 | 0.020767 | 61.5662 | -0.006014 | 61.4496 | 61.5217 | 61.46 | 61.4794 | 61.4847 | 61.5093 | 61.49 | 61.5111 | 123.0376 | 61.6439 | 122.946 | 61.44 | 61.5167 | 123.0621 | 61.49 | 122.9456 | 61.5209 | 61.5477 | 61.4293 | 61.4561
380.0625 | 123.3032 | -61.4822 | 61.7065 | 0.021127 | -0.035942 | -0.016578 | -0.011281 | 0.017953 | -0.005985 | 0.015112 | 61.5234 | 0.14332 | 61.4317 | -0.051417 | 0.016188 | 61.5707 | -0.001436 | 61.4496 | 61.5034 | 61.4463 | 61.4657 | 61.471 | 61.5002 | 61.4763 | 61.4974 | 123.0056 | 61.6256 | 122.914 | 61.4308 | 61.4984 | 123.053 | 61.4808 | 122.9319 | 61.5072 | 61.5248 | 61.4155 | 61.4332
381.0625 | 123.2254 | -61.4731 | 61.6425 | 0.030283 | -0.035942 | -0.007421 | -0.006703 | 0.017953 | -0.001406 | 0.01969 | 61.5508 | 0.1479 | 61.4775 | -0.060575 | 0.01161 | 61.5616 | -0.001436 | 61.4451 | 61.5034 | 61.4371 | 61.4657 | 61.4664 | 61.491 | 61.4717 | 61.4928 | 123.0239 | 61.621 | 122.9506 | 61.4125 | 61.4847 | 123.0347 | 61.4716 | 122.9182 | 61.5392 | 61.5523 | 61.4659 | 61.4789
382.0625 | 123.2666 | -61.4685 | 61.6196 | 0.021127 | -0.031363 | -0.016578 | -0.002124 | 0.013375 | -0.001406 | 0.024268 | 61.5417 | 0.1479 | 61.4226 | -0.051417 | 0.002454 | 61.5707 | -0.001436 | 61.4405 | 61.4896 | 61.4371 | 61.4519 | 61.4664 | 61.4819 | 61.4671 | 61.4928 | 123.0102 | 61.6164 | 122.8911 | 61.4171 | 61.471 | 123.0392 | 61.4671 | 122.909 | 61.5392 | 61.5431 | 61.4201 | 61.424
383.0625 | 123.3398 | -61.441 | 61.6058 | 0.030283 | -0.040521 | -0.021157 | -0.006703 | 0.017953 | -0.001406 | 0.015112 | 61.5417 | 0.14332 | 61.4546 | -0.055996 | 0.01161 | 61.5616 | -0.001436 | 61.4268 | 61.4713 | 61.4005 | 61.4199 | 61.4343 | 61.459 | 61.4396 | 61.4562 | 122.9827 | 61.5844 | 122.8957 | 61.385 | 61.4526 | 123.0026 | 61.4396 | 122.8678 | 61.5301 | 61.5431 | 61.443 | 61.4561
384.0625 | 123.3353 | -61.4502 | 61.615 | 0.030283 | -0.035942 | -0.016578 | -0.002124 | 0.022531 | -0.015142 | 0.01969 | 61.5463 | 0.14332 | 61.4271 | -0.055996 | 0.01161 | 61.5662 | 0.003143 | 61.4405 | 61.4805 | 61.4143 | 61.4336 | 61.4481 | 61.4727 | 61.4351 | 61.4699 | 122.9965 | 61.5935 | 122.8773 | 61.3942 | 61.4618 | 123.0164 | 61.4533 | 122.8907 | 61.5346 | 61.5431 | 61.4155 | 61.424
385.0625 | 123.2849 | -61.4594 | 61.647 | 0.025705 | -0.035942 | -0.016578 | -0.011281 | 0.022531 | -0.001406 | 0.01969 | 61.5417 | 0.1479 | 61.4729 | -0.055996 | 0.01161 | 61.5707 | -0.006014 | 61.4268 | 61.4851 | 61.4234 | 61.4428 | 61.4481 | 61.4819 | 61.4579 | 61.479 | 123.001 | 61.6073 | 122.9323 | 61.4034 | 61.471 | 123.0301 | 61.4533 | 122.8861 | 61.5301 | 61.5477 | 61.4613 | 61.4789
386.0625 | 123.3215 | -61.4685 | 61.6425 | 0.025705 | -0.0451 | -0.021157 | -0.006703 | 0.022531 | -0.001406 | 0.010533 | 61.5325 | 0.1479 | 61.4271 | -0.055996 | 0.020767 | 61.5707 | -0.006014 | 61.4451 | 61.4942 | 61.4234 | 61.4473 | 61.4618 | 61.491 | 61.4671 | 61.479 | 123.001 | 61.6164 | 122.8957 | 61.4125 | 61.4893 | 123.0392 | 61.4625 | 122.9136 | 61.5118 | 61.5385 | 61.4064 | 61.4332
387.0625 | 123.2437 | -61.4822 | 61.6333 | 0.025705 | -0.035942 | -0.021157 | -0.006703 | 0.022531 | -0.001406 | 0.024268 | 61.5463 | 0.1479 | 61.4775 | -0.055996 | 0.016188 | 61.5616 | -0.006014 | 61.4451 | 61.5079 | 61.4463 | 61.4611 | 61.4755 | 61.5048 | 61.4808 | 61.5065 | 123.0285 | 61.6301 | 122.9597 | 61.4262 | 61.4984 | 123.0438 | 61.4762 | 122.9273 | 61.5301 | 61.5523 | 61.4613 | 61.4835
388.0625 | 123.2712 | -61.4639 | 61.6333 | 0.025705 | -0.040521 | -0.016578 | -0.002124 | 0.017953 | -0.010563 | 0.01969 | 61.5371 | 0.1479 | 61.4317 | -0.051417 | 0.007032 | 61.5662 | -0.001436 | 61.4496 | 61.4896 | 61.4234 | 61.4474 | 61.4618 | 61.4819 | 61.4534 | 61.4836 | 123.001 | 61.6118 | 122.8957 | 61.4125 | 61.471 | 123.0301 | 61.4625 | 122.9136 | 61.5301 | 61.5385 | 61.4247 | 61.4332
389.0625 | 123.3398 | -61.4548 | 61.6241 | 0.025705 | -0.035942 | -0.016578 | 0.002454 | 0.027109 | -0.005985 | 0.024268 | 61.5417 | 0.15248 | 61.4317 | -0.051417 | 0.01161 | 61.5662 | 0.003143 | 61.4542 | 61.4805 | 61.4188 | 61.4382 | 61.4572 | 61.4819 | 61.4488 | 61.479 | 122.9965 | 61.6073 | 122.8865 | 61.4034 | 61.4664 | 123.0209 | 61.4579 | 122.909 | 61.5301 | 61.5385 | 61.4201 | 61.4286
390.0625 | 123.381 | -61.409 | 61.6791 | 0.021127 | -0.035942 | -0.016578 | -0.011281 | 0.013375 | 0.003172 | 0.024268 | 61.5371 | 0.1479 | 61.4821 | -0.060575 | 0.01161 | 61.5662 | -0.001436 | 61.4405 | 61.4301 | 61.3731 | 61.3924 | 61.3977 | 61.4224 | 61.4122 | 61.4333 | 122.9461 | 61.5569 | 122.8911 | 61.3484 | 61.4206 | 122.9752 | 61.4076 | 122.8495 | 61.5255 | 61.5385 | 61.4705 | 61.4835
391.0625 | 123.4085 | -61.4456 | 61.6241 | 0.025705 | -0.035942 | -0.016578 | -0.011281 | 0.017953 | -0.005985 | 0.01969 | 61.5371 | 0.15248 | 61.418 | -0.051417 | 0.007032 | 61.5616 | -0.001436 | 61.4496 | 61.4713 | 61.4097 | 61.429 | 61.4343 | 61.4636 | 61.4396 | 61.4653 | 122.9827 | 61.5981 | 122.8636 | 61.3942 | 61.4527 | 123.0072 | 61.4442 | 122.8953 | 61.5301 | 61.5385 | 61.411 | 61.4194
392.0625 | 123.2529 | -61.496 | 61.6516 | 0.021127 | -0.040521 | -0.016578 | -0.006703 | 0.017953 | -0.005985 | 0.01969 | 61.5463 | 0.14332 | 61.4821 | -0.060575 | 0.01161 | 61.5616 | -0.001436 | 61.4359 | 61.5171 | 61.4555 | 61.4794 | 61.4893 | 61.5139 | 61.49 | 61.5157 | 123.0422 | 61.6393 | 122.9781 | 61.4354 | 61.5076 | 123.0576 | 61.4945 | 122.9319 | 61.5346 | 61.5477 | 61.4705 | 61.4835
393.0625 | 123.4451 | -61.409 | 61.647 | 0.021127 | -0.0451 | -0.016578 | -0.011281 | 0.017953 | -0.005985 | 0.024268 | 61.5417 | 0.14332 | 61.4317 | -0.046838 | 0.016188 | 61.5662 | -0.006014 | 61.4313 | 61.4301 | 61.3639 | 61.3924 | 61.3977 | 61.4269 | 61.403 | 61.4333 | 122.9507 | 61.5523 | 122.8407 | 61.3622 | 61.4252 | 122.9752 | 61.403 | 122.8403 | 61.5255 | 61.5477 | 61.4155 | 61.4377
394.0625 | 123.3261 | -61.4685 | 61.6104 | 0.025705 | -0.031363 | -0.021157 | -0.006703 | 0.017953 | -0.001406 | 0.028846 | 61.5371 | 0.15248 | 61.4363 | -0.046838 | 0.007032 | 61.5662 | -0.006014 | 61.4405 | 61.4942 | 61.4371 | 61.4473 | 61.4618 | 61.4865 | 61.4671 | 61.4974 | 123.0056 | 61.621 | 122.9048 | 61.4217 | 61.4755 | 123.0347 | 61.4625 | 122.909 | 61.5301 | 61.5431 | 61.4293 | 61.4423
395.0625 | 123.3627 | -61.4502 | 61.615 | 0.025705 | -0.035942 | -0.025735 | -0.002124 | 0.022531 | -0.005985 | 0.01969 | 61.5463 | 0.14332 | 61.4684 | -0.051417 | 0.016188 | 61.5707 | -0.006014 | 61.4084 | 61.4759 | 61.4143 | 61.4245 | 61.4481 | 61.4727 | 61.4442 | 61.4699 | 122.9965 | 61.5935 | 122.9185 | 61.3988 | 61.4664 | 123.0209 | 61.4442 | 122.8586 | 61.5301 | 61.5523 | 61.4522 | 61.4744
396.0625 | 123.3215 | -61.4319 | 61.6013 | 0.025705 | -0.035942 | -0.016578 | -0.011281 | 0.022531 | -0.005985 | 0.028846 | 61.5371 | 0.15248 | 61.4271 | -0.051417 | 0.01161 | 61.5707 | -0.001436 | 61.4451 | 61.4576 | 61.3959 | 61.4153 | 61.4206 | 61.4544 | 61.4259 | 61.4607 | 122.969 | 61.5844 | 122.859 | 61.3805 | 61.4435 | 123.0026 | 61.4304 | 122.877 | 61.5255 | 61.5385 | 61.4155 | 61.4286
397.0625 | 123.262 | -61.4685 | 61.6562 | 0.030283 | -0.035942 | -0.012 | -0.006703 | 0.022531 | 0.003172 | 0.028846 | 61.5417 | 0.1479 | 61.4867 | -0.055996 | 0.007032 | 61.5662 | 0.003143 | 61.413 | 61.4988 | 61.4326 | 61.4565 | 61.4618 | 61.491 | 61.4717 | 61.4974 | 123.0102 | 61.6164 | 122.9552 | 61.4125 | 61.4755 | 123.0347 | 61.4716 | 122.8815 | 61.5346 | 61.5385 | 61.4796 | 61.4835
398.0625 | 123.381 | -61.4639 | 61.5784 | 0.025705 | -0.035942 | -0.021157 | -0.011281 | 0.017953 | -0.005985 | 0.024268 | 61.5417 | 0.1479 | 61.4226 | -0.051417 | 0.016188 | 61.5662 | -0.006014 | 61.4313 | 61.4896 | 61.428 | 61.4428 | 61.4526 | 61.4819 | 61.4579 | 61.4882 | 123.0056 | 61.6118 | 122.8865 | 61.4125 | 61.4801 | 123.0301 | 61.4579 | 122.8953 | 61.5255 | 61.5477 | 61.4064 | 61.4286
399.0625 | 123.3765 | -61.4502 | 61.5875 | 0.016548 | -0.040521 | -0.012 | -0.011281 | 0.013375 | -0.001406 | 0.015112 | 61.5417 | 0.1479 | 61.4363 | -0.051417 | 0.016188 | 61.5616 | -0.010593 | 61.4268 | 61.4667 | 61.4097 | 61.4382 | 61.4389 | 61.4636 | 61.4488 | 61.4653 | 122.9919 | 61.5981 | 122.8865 | 61.3988 | 61.4664 | 123.0118 | 61.4396 | 122.877 | 61.5255 | 61.5523 | 61.4201 | 61.4469
400.0625 | 123.3856 | -61.4731 | 61.5921 | 0.025705 | -0.040521 | -0.021157 | -0.011281 | 0.022531 | -0.005985 | 0.015112 | 61.5371 | 0.14332 | 61.4592 | -0.060575 | 0.016188 | 61.5662 | -0.001436 | 61.3947 | 61.4988 | 61.4326 | 61.4519 | 61.4618 | 61.4956 | 61.4671 | 61.4882 | 123.0102 | 61.6164 | 122.9323 | 61.4125 | 61.4893 | 123.0392 | 61.4716 | 122.8678 | 61.5209 | 61.5385 | 61.443 | 61.4606
401.0625 | 123.381 | -61.4456 | 61.5967 | 0.025705 | -0.040521 | -0.021157 | -0.006703 | 0.017953 | -0.005985 | 0.01969 | 61.5371 | 0.14332 | 61.4226 | -0.055996 | 0.016188 | 61.5662 | -0.010593 | 61.3901 | 61.4713 | 61.4051 | 61.4245 | 61.4389 | 61.4636 | 61.4396 | 61.4653 | 122.9827 | 61.5889 | 122.8682 | 61.3896 | 61.4618 | 123.0118 | 61.435 | 122.8357 | 61.5209 | 61.5477 | 61.4064 | 61.4332
402.0625 | 123.2208 | -61.4822 | 61.6287 | 0.021127 | -0.040521 | -0.016578 | -0.006703 | 0.022531 | -0.001406 | 0.024268 | 61.5554 | 0.15248 | 61.4867 | -0.060575 | 0.007032 | 61.5753 | 0.003143 | 61.3856 | 61.5034 | 61.4417 | 61.4657 | 61.4755 | 61.5048 | 61.4808 | 61.5065 | 123.0377 | 61.6347 | 122.9689 | 61.4217 | 61.4893 | 123.0576 | 61.4854 | 122.8678 | 61.5484 | 61.5523 | 61.4796 | 61.4835
403.0625 | 123.3444 | -61.4502 | 61.5829 | 0.025705 | -0.035942 | -0.012 | -0.011281 | 0.022531 | -0.010563 | 0.01969 | 61.5371 | 0.1479 | 61.4317 | -0.055996 | 0.016188 | 61.5616 | 0.003143 | 61.3993 | 61.4759 | 61.4143 | 61.4382 | 61.4389 | 61.4727 | 61.4396 | 61.4699 | 122.9873 | 61.5981 | 122.8819 | 61.3942 | 61.4664 | 123.0118 | 61.4533 | 122.8495 | 61.5209 | 61.534 | 61.4155 | 61.4286
404.0625 | 123.4039 | -61.4914 | 61.6013 | 0.030283 | -0.031363 | -0.025735 | -0.006703 | 0.027109 | -0.010563 | 0.01969 | 61.5371 | 0.15248 | 61.4546 | -0.055996 | 0.007032 | 61.5616 | -0.010593 | 61.381 | 61.5217 | 61.46 | 61.4657 | 61.4847 | 61.5185 | 61.4808 | 61.5111 | 123.0285 | 61.6439 | 122.946 | 61.4354 | 61.4984 | 123.053 | 61.4808 | 122.8724 | 61.5301 | 61.5477 | 61.4476 | 61.4652
405.0625 | 123.3536 | -61.4639 | 61.6104 | 0.021127 | -0.031363 | -0.016578 | -0.006703 | 0.022531 | -0.010563 | 0.024268 | 61.5417 | 0.1479 | 61.4363 | -0.065154 | 0.016188 | 61.5662 | -0.006014 | 61.3901 | 61.4851 | 61.4326 | 61.4474 | 61.4572 | 61.4865 | 61.4534 | 61.4882 | 123.0056 | 61.6118 | 122.9002 | 61.3988 | 61.4801 | 123.0301 | 61.4579 | 122.8541 | 61.5255 | 61.5477 | 61.4201 | 61.4423
406.0625 | 123.3078 | -61.4822 | 61.5738 | 0.034862 | -0.040521 | -0.021157 | -0.011281 | 0.017953 | -0.010563 | 0.024268 | 61.5371 | 0.15248 | 61.418 | -0.055996 | 0.007032 | 61.5707 | -0.006014 | 61.4222 | 61.5171 | 61.4417 | 61.4611 | 61.471 | 61.5002 | 61.4717 | 61.5065 | 123.0193 | 61.6347 | 122.9002 | 61.4262 | 61.4893 | 123.053 | 61.4762 | 122.9044 | 61.5301 | 61.5431 | 61.411 | 61.424
407.0625 | 123.2483 | -61.4914 | 61.615 | 0.030283 | -0.040521 | -0.012 | -0.011281 | 0.027109 | 0.003172 | 0.033424 | 61.5463 | 0.15248 | 61.4775 | -0.051417 | 0.007032 | 61.5662 | -0.006014 | 61.4084 | 61.5217 | 61.4509 | 61.4794 | 61.4801 | 61.5185 | 61.4946 | 61.5248 | 123.0377 | 61.6439 | 122.9689 | 61.44 | 61.4984 | 123.0576 | 61.4854 | 122.8998 | 61.5392 | 61.5523 | 61.4705 | 61.4835
408.0625 | 123.3215 | -61.4868 | 61.6058 | 0.025705 | -0.031363 | -0.021157 | -0.006703 | 0.013375 | -0.010563 | 0.01969 | 61.5417 | 0.15706 | 61.418 | -0.051417 | 0.007032 | 61.5662 | -0.006014 | 61.4222 | 61.5125 | 61.4555 | 61.4657 | 61.4801 | 61.5002 | 61.4763 | 61.5065 | 123.0285 | 61.6439 | 122.9048 | 61.4354 | 61.4938 | 123.053 | 61.4808 | 122.909 | 61.5346 | 61.5477 | 61.411 | 61.424
409.0625 | 123.3536 | -61.4639 | 61.5692 | 0.025705 | -0.035942 | -0.016578 | -0.006703 | 0.013375 | -0.005985 | 0.015112 | 61.5417 | 0.15248 | 61.4729 | -0.055996 | 0.007032 | 61.5662 | 0.003143 | 61.3947 | 61.4896 | 61.428 | 61.4474 | 61.4572 | 61.4773 | 61.4579 | 61.479 | 123.0056 | 61.6164 | 122.9369 | 61.4079 | 61.471 | 123.0301 | 61.4671 | 122.8586 | 61.5346 | 61.5385 | 61.4659 | 61.4698
410.0625 | 123.3215 | -61.4456 | 61.6058 | 0.034862 | -0.035942 | -0.012 | -0.006703 | 0.022531 | -0.005985 | 0.024268 | 61.5371 | 0.14332 | 61.4317 | -0.055996 | 0.016188 | 61.5662 | -0.006014 | 61.3856 | 61.4805 | 61.4097 | 61.4336 | 61.4389 | 61.4681 | 61.4396 | 61.4699 | 122.9827 | 61.5889 | 122.8773 | 61.3896 | 61.4618 | 123.0118 | 61.4396 | 122.8312 | 61.5209 | 61.5431 | 61.4155 | 61.4377
411.0625 | 123.3078 | -61.4639 | 61.5875 | 0.03944 | -0.031363 | -0.021157 | -0.002124 | 0.022531 | -0.005985 | 0.01969 | 61.5417 | 0.15248 | 61.4317 | -0.051417 | 0.01161 | 61.5707 | -0.001436 | 61.3856 | 61.5034 | 61.4326 | 61.4428 | 61.4618 | 61.4865 | 61.4579 | 61.4836 | 123.0056 | 61.6164 | 122.8957 | 61.4125 | 61.4755 | 123.0347 | 61.4625 | 122.8495 | 61.5301 | 61.5431 | 61.4201 | 61.4332
412.0625 | 123.3398 | -61.4731 | 61.5829 | 0.025705 | -0.0451 | -0.012 | -0.011281 | 0.022531 | -0.001406 | 0.024268 | 61.5463 | 0.15248 | 61.4821 | -0.046838 | 0.01161 | 61.5707 | -0.001436 | 61.3947 | 61.4988 | 61.428 | 61.4611 | 61.4618 | 61.4956 | 61.4717 | 61.4974 | 123.0193 | 61.6256 | 122.9552 | 61.4262 | 61.4847 | 123.0438 | 61.4716 | 122.8678 | 61.5346 | 61.5477 | 61.4705 | 61.4835
413.0625 | 123.3398 | -61.4685 | 61.5875 | 0.030283 | -0.035942 | -0.021157 | -0.011281 | 0.022531 | -0.001406 | 0.015112 | 61.5417 | 0.14332 | 61.4271 | -0.060575 | 0.016188 | 61.5662 | -0.006014 | 61.3993 | 61.4988 | 61.4326 | 61.4473 | 61.4572 | 61.491 | 61.4671 | 61.4836 | 123.0102 | 61.6118 | 122.8957 | 61.4079 | 61.4847 | 123.0347 | 61.4625 | 122.8678 | 61.5255 | 61.5477 | 61.411 | 61.4332
414.0625 | 123.3261 | -61.4685 | 61.5829 | 0.021127 | -0.035942 | -0.016578 | -0.006703 | 0.027109 | -0.015142 | 0.024268 | 61.5371 | 0.1479 | 61.4592 | -0.060575 | 0.016188 | 61.5662 | -0.001436 | 61.381 | 61.4896 | 61.4326 | 61.4519 | 61.4618 | 61.4956 | 61.4534 | 61.4928 | 123.0056 | 61.6164 | 122.9277 | 61.4079 | 61.4847 | 123.0347 | 61.4671 | 122.8495 | 61.5209 | 61.5385 | 61.443 | 61.4606
415.0625 | 123.3398 | -61.4731 | 61.5921 | 0.030283 | -0.040521 | -0.016578 | -0.002124 | 0.013375 | -0.001406 | 0.024268 | 61.5417 | 0.1479 | 61.4409 | -0.065154 | 0.007032 | 61.5616 | -0.001436 | 61.3856 | 61.5034 | 61.4326 | 61.4565 | 61.471 | 61.4865 | 61.4717 | 61.4974 | 123.0148 | 61.621 | 122.914 | 61.4079 | 61.4801 | 123.0347 | 61.4716 | 122.8586 | 61.5346 | 61.5431 | 61.4339 | 61.4423
416.0625 | 123.349 | -61.4639 | 61.5875 | 0.025705 | -0.031363 | -0.012 | -0.006703 | 0.027109 | -0.010563 | 0.024268 | 61.5417 | 0.1479 | 61.4409 | -0.060575 | 0.002454 | 61.5753 | -0.006014 | 61.3901 | 61.4896 | 61.4326 | 61.4519 | 61.4572 | 61.491 | 61.4534 | 61.4882 | 123.0056 | 61.6118 | 122.9048 | 61.4034 | 61.4664 | 123.0392 | 61.4579 | 122.8541 | 61.5392 | 61.5477 | 61.4384 | 61.4469
417.0625 | 123.2895 | -61.4685 | 61.6104 | 0.025705 | -0.040521 | -0.021157 | -0.002124 | 0.017953 | 0.003172 | 0.033424 | 61.5417 | 0.15248 | 61.4455 | -0.051417 | 0.01161 | 61.5662 | -0.006014 | 61.3901 | 61.4942 | 61.428 | 61.4473 | 61.4664 | 61.4865 | 61.4717 | 61.5019 | 123.0102 | 61.621 | 122.914 | 61.4171 | 61.4801 | 123.0347 | 61.4625 | 122.8586 | 61.5301 | 61.5477 | 61.4339 | 61.4515
418.0625 | 123.3582 | -61.4594 | 61.5921 | 0.030283 | -0.035942 | -0.016578 | -0.01586 | 0.017953 | -0.001406 | 0.01969 | 61.5463 | 0.15248 | 61.4317 | -0.060575 | 0.007032 | 61.5707 | -0.006014 | 61.381 | 61.4896 | 61.4234 | 61.4428 | 61.4435 | 61.4773 | 61.4579 | 61.479 | 123.0056 | 61.6118 | 122.8911 | 61.3988 | 61.4664 | 123.0301 | 61.4533 | 122.8403 | 61.5392 | 61.5523 | 61.4247 | 61.4377
419.0625 | 123.3582 | -61.4639 | 61.5784 | 0.025705 | -0.031363 | -0.016578 | -0.006703 | 0.022531 | -0.001406 | 0.01969 | 61.5417 | 0.1479 | 61.4729 | -0.046838 | 0.01161 | 61.5662 | -0.010593 | 61.381 | 61.4896 | 61.4326 | 61.4474 | 61.4572 | 61.4865 | 61.4625 | 61.4836 | 123.0056 | 61.6118 | 122.9369 | 61.4171 | 61.4755 | 123.0301 | 61.4533 | 122.8449 | 61.5301 | 61.5523 | 61.4613 | 61.4835
420.0625 | 123.3078 | -61.4731 | 61.5646 | 0.030283 | -0.0451 | -0.016578 | -0.011281 | 0.022531 | -0.010563 | 0.015112 | 61.5417 | 0.1479 | 61.4226 | -0.060575 | 0.01161 | 61.5707 | -0.001436 | 61.381 | 61.5034 | 61.428 | 61.4565 | 61.4618 | 61.4956 | 61.4625 | 61.4882 | 123.0148 | 61.621 | 122.8957 | 61.4125 | 61.4847 | 123.0438 | 61.4716 | 122.8541 | 61.5301 | 61.5431 | 61.411 | 61.424
421.0625 | 123.3307 | -61.4594 | 61.5601 | 0.025705 | -0.031363 | -0.016578 | -0.006703 | 0.022531 | -0.001406 | 0.024268 | 61.5463 | 0.15248 | 61.4775 | -0.055996 | 0.01161 | 61.5707 | -0.006014 | 61.3856 | 61.4851 | 61.428 | 61.4428 | 61.4526 | 61.4819 | 61.4579 | 61.4836 | 123.0056 | 61.6118 | 122.9369 | 61.4034 | 61.471 | 123.0301 | 61.4533 | 122.8449 | 61.5346 | 61.5523 | 61.4659 | 61.4835
422.0625 | 123.2254 | -61.5051 | 61.5921 | 0.030283 | -0.035942 | -0.021157 | -0.006703 | 0.022531 | -0.001406 | 0.024268 | 61.5463 | 0.15706 | 61.4271 | -0.060575 | 0.007032 | 61.5753 | -0.006014 | 61.3947 | 61.5354 | 61.4692 | 61.484 | 61.4984 | 61.5277 | 61.5037 | 61.5294 | 123.0514 | 61.6622 | 122.9323 | 61.4446 | 61.5122 | 123.0804 | 61.4991 | 122.8998 | 61.5392 | 61.5523 | 61.4201 | 61.4332
423.0625 | 123.3627 | -61.4731 | 61.5646 | 0.030283 | -0.035942 | -0.021157 | -0.006703 | 0.027109 | 0.003172 | 0.015112 | 61.5463 | 0.15248 | 61.4867 | -0.060575 | 0.01161 | 61.5707 | -0.006014 | 61.3856 | 61.5034 | 61.4371 | 61.4519 | 61.4664 | 61.5002 | 61.4763 | 61.4882 | 123.0193 | 61.6256 | 122.9597 | 61.4125 | 61.4847 | 123.0438 | 61.4671 | 122.8586 | 61.5346 | 61.5523 | 61.4751 | 61.4927
424.0625 | 123.2849 | -61.4822 | 61.5829 | 0.025705 | -0.035942 | -0.012 | -0.002124 | 0.017953 | -0.005985 | 0.015112 | 61.5325 | 0.14332 | 61.4317 | -0.060575 | 0.007032 | 61.5616 | -0.001436 | 61.3856 | 61.5079 | 61.4463 | 61.4702 | 61.4801 | 61.5002 | 61.4763 | 61.4974 | 123.0148 | 61.6256 | 122.914 | 61.4217 | 61.4893 | 123.0438 | 61.4808 | 122.8678 | 61.5255 | 61.534 | 61.4247 | 61.4332
425.0625 | 123.3627 | -61.4594 | 61.5692 | 0.030283 | -0.0451 | -0.016578 | -0.006703 | 0.022531 | -0.010563 | 0.015112 | 61.5371 | 0.15706 | 61.4455 | -0.055996 | 0.01161 | 61.5753 | -0.006014 | 61.381 | 61.4896 | 61.4143 | 61.4428 | 61.4526 | 61.4819 | 61.4488 | 61.4745 | 122.9965 | 61.6164 | 122.9048 | 61.4034 | 61.471 | 123.0347 | 61.4533 | 122.8403 | 61.5255 | 61.5431 | 61.4339 | 61.4515
426.0625 | 123.3582 | -61.4456 | 61.5738 | 0.025705 | -0.040521 | -0.025735 | -0.002124 | 0.022531 | 0.003172 | 0.01969 | 61.5371 | 0.1479 | 61.4867 | -0.055996 | 0.002454 | 61.5616 | -0.006014 | 61.3901 | 61.4713 | 61.4051 | 61.4199 | 61.4435 | 61.4681 | 61.4488 | 61.4653 | 122.9827 | 61.5935 | 122.9323 | 61.3896 | 61.4481 | 123.0072 | 61.4396 | 122.8357 | 61.5346 | 61.5431 | 61.4842 | 61.4927
427.0625 | 123.349 | -61.4639 | 61.6379 | 0.025705 | -0.040521 | -0.025735 | -0.006703 | 0.022531 | -0.005985 | 0.024268 | 61.5371 | 0.1479 | 61.4271 | -0.055996 | 0.01161 | 61.5707 | -0.006014 | 61.3993 | 61.4896 | 61.4234 | 61.4382 | 61.4572 | 61.4865 | 61.4579 | 61.4882 | 123.001 | 61.6118 | 122.8911 | 61.4079 | 61.4755 | 123.0347 | 61.4579 | 122.8632 | 61.5255 | 61.5431 | 61.4155 | 61.4332
428.0625 | 123.3398 | -61.4731 | 61.5784 | 0.025705 | -0.040521 | -0.016578 | -0.006703 | 0.017953 | -0.001406 | 0.028846 | 61.5508 | 0.15248 | 61.4775 | -0.060575 | 0.01161 | 61.5753 | -0.001436 | 61.3947 | 61.4988 | 61.4326 | 61.4565 | 61.4664 | 61.491 | 61.4717 | 61.5019 | 123.0239 | 61.6256 | 122.9506 | 61.4125 | 61.4847 | 123.0484 | 61.4716 | 122.8678 | 61.5392 | 61.5523 | 61.4659 | 61.4789
429.0625 | 123.2895 | -61.4594 | 61.5829 | 0.030283 | -0.031363 | -0.016578 | -0.011281 | 0.013375 | -0.010563 | 0.01969 | 61.5325 | 0.15248 | 61.4226 | -0.055996 | 0.01161 | 61.5616 | -0.006014 | 61.4405 | 61.4896 | 61.428 | 61.4428 | 61.4481 | 61.4727 | 61.4488 | 61.479 | 122.9919 | 61.6118 | 122.8819 | 61.4034 | 61.471 | 123.0209 | 61.4533 | 122.8998 | 61.5209 | 61.5385 | 61.411 | 61.4286
430.0625 | 123.3124 | -61.4639 | 61.5921 | 0.025705 | -0.035942 | -0.021157 | -0.006703 | 0.017953 | 0.00775 | 0.024268 | 61.5463 | 0.15706 | 61.4867 | -0.060575 | 0.01161 | 61.5662 | -0.015171 | 61.4405 | 61.4896 | 61.428 | 61.4428 | 61.4572 | 61.4819 | 61.4717 | 61.4882 | 123.0102 | 61.621 | 122.9506 | 61.4034 | 61.4755 | 123.0301 | 61.4488 | 122.9044 | 61.5346 | 61.5614 | 61.4751 | 61.5018
431.0625 | 123.2941 | -61.4777 | 61.5921 | 0.021127 | -0.035942 | -0.016578 | -0.011281 | 0.017953 | -0.001406 | 0.01969 | 61.5417 | 0.1479 | 61.4271 | -0.051417 | 0.016188 | 61.5753 | -0.006014 | 61.4496 | 61.4988 | 61.4417 | 61.4611 | 61.4664 | 61.4956 | 61.4763 | 61.4974 | 123.0193 | 61.6256 | 122.9048 | 61.4262 | 61.4938 | 123.053 | 61.4716 | 122.9273 | 61.5255 | 61.5477 | 61.411 | 61.4332
432.0625 | 123.3444 | -61.4456 | 61.5601 | 0.025705 | -0.040521 | -0.016578 | -0.01586 | 0.027109 | -0.005985 | 0.01969 | 61.5508 | 0.1479 | 61.4821 | -0.046838 | 0.007032 | 61.5753 | 0.003143 | 61.4451 | 61.4713 | 61.4051 | 61.429 | 61.4298 | 61.4727 | 61.4396 | 61.4653 | 122.9965 | 61.5935 | 122.9277 | 61.3988 | 61.4527 | 123.0209 | 61.4488 | 122.8907 | 61.5438 | 61.5477 | 61.4751 | 61.4789
433.0625 | 123.4177 | -61.4502 | 61.6058 | 0.030283 | -0.031363 | -0.012 | -0.002124 | 0.022531 | -0.005985 | 0.01969 | 61.5371 | 0.15248 | 61.4226 | -0.051417 | 0.01161 | 61.5707 | -0.006014 | 61.4405 | 61.4805 | 61.4188 | 61.4382 | 61.4481 | 61.4727 | 61.4442 | 61.4699 | 122.9873 | 61.6027 | 122.8728 | 61.3988 | 61.4618 | 123.0209 | 61.4442 | 122.8907 | 61.5255 | 61.5431 | 61.411 | 61.4286
434.0625 | 123.3444 | -61.4731 | 61.5829 | 0.030283 | -0.035942 | -0.016578 | -0.006703 | 0.022531 | -0.005985 | 0.024268 | 61.5417 | 0.14332 | 61.4821 | -0.055996 | 0.01161 | 61.5707 | -0.006014 | 61.4176 | 61.5034 | 61.4371 | 61.4565 | 61.4664 | 61.4956 | 61.4671 | 61.4974 | 123.0148 | 61.6164 | 122.9552 | 61.4171 | 61.4847 | 123.0438 | 61.4671 | 122.8907 | 61.5301 | 61.5477 | 61.4705 | 61.4881
435.0625 | 123.3307 | -61.4731 | 61.5829 | 0.030283 | -0.035942 | -0.016578 | -0.002124 | 0.022531 | -0.005985 | 0.024268 | 61.5417 | 0.15706 | 61.4226 | -0.046838 | 0.01161 | 61.5662 | -0.006014 | 61.413 | 61.5034 | 61.4371 | 61.4565 | 61.471 | 61.4956 | 61.4671 | 61.4974 | 123.0148 | 61.6301 | 122.8957 | 61.4262 | 61.4847 | 123.0392 | 61.4671 | 122.8861 | 61.5301 | 61.5477 | 61.411 | 61.4286
436.0625 | 123.3353 | -61.4548 | 61.5967 | 0.025705 | -0.0451 | -0.025735 | -0.002124 | 0.017953 | -0.005985 | 0.015112 | 61.5417 | 0.14332 | 61.4867 | -0.051417 | 0.002454 | 61.5707 | -0.006014 | 61.4222 | 61.4805 | 61.4097 | 61.429 | 61.4526 | 61.4727 | 61.4488 | 61.4699 | 122.9965 | 61.5981 | 122.9414 | 61.4034 | 61.4572 | 123.0255 | 61.4488 | 122.877 | 61.5392 | 61.5477 | 61.4842 | 61.4927
437.0625 | 123.2758 | -61.4868 | 61.6241 | 0.030283 | -0.035942 | -0.016578 | -0.002124 | 0.022531 | -0.001406 | 0.024268 | 61.5508 | 0.15706 | 61.4271 | -0.055996 | 0.007032 | 61.5662 | -0.001436 | 61.4405 | 61.5171 | 61.4509 | 61.4702 | 61.4847 | 61.5093 | 61.4854 | 61.5111 | 123.0377 | 61.6439 | 122.914 | 61.4308 | 61.4938 | 123.053 | 61.4854 | 122.9273 | 61.5438 | 61.5523 | 61.4201 | 61.4286
438.0625 | 123.3078 | -61.4731 | 61.5921 | 0.025705 | -0.035942 | -0.016578 | -0.011281 | 0.017953 | -0.001406 | 0.01969 | 61.5371 | 0.15248 | 61.4729 | -0.051417 | 0.007032 | 61.5707 | -0.006014 | 61.4222 | 61.4988 | 61.4371 | 61.4565 | 61.4618 | 61.491 | 61.4717 | 61.4928 | 123.0102 | 61.6256 | 122.946 | 61.4217 | 61.4801 | 123.0438 | 61.4671 | 122.8953 | 61.5301 | 61.5431 | 61.4659 | 61.4789
439.0625 | 123.3353 | -61.4639 | 61.5829 | 0.025705 | -0.035942 | -0.025735 | -0.006703 | 0.017953 | -0.005985 | 0.01969 | 61.5463 | 0.15706 | 61.4317 | -0.051417 | 0.01161 | 61.5707 | -0.010593 | 61.4359 | 61.4896 | 61.428 | 61.4382 | 61.4572 | 61.4819 | 61.4579 | 61.4836 | 123.0102 | 61.621 | 122.8957 | 61.4125 | 61.4755 | 123.0347 | 61.4533 | 122.8998 | 61.5346 | 61.5568 | 61.4201 | 61.4423
440.0625 | 123.3673 | -61.4456 | 61.5601 | 0.021127 | -0.0451 | -0.025735 | -0.011281 | 0.017953 | -0.001406 | 0.01969 | 61.5463 | 0.1479 | 61.4775 | -0.051417 | 0.016188 | 61.5707 | -0.001436 | 61.4268 | 61.4667 | 61.4005 | 61.4199 | 61.4343 | 61.4636 | 61.4442 | 61.4653 | 122.9919 | 61.5935 | 122.9231 | 61.3942 | 61.4618 | 123.0164 | 61.4442 | 122.8724 | 61.5301 | 61.5477 | 61.4613 | 61.4789
441.0625 | 123.3398 | -61.4502 | 61.5875 | 0.025705 | -0.0451 | -0.016578 | -0.006703 | 0.022531 | -0.005985 | 0.015112 | 61.5417 | 0.14332 | 61.4363 | -0.055996 | 0.016188 | 61.5662 | -0.010593 | 61.4313 | 61.4759 | 61.4051 | 61.4336 | 61.4435 | 61.4727 | 61.4442 | 61.4653 | 122.9919 | 61.5935 | 122.8865 | 61.3942 | 61.4664 | 123.0164 | 61.4396 | 122.8815 | 61.5255 | 61.5523 | 61.4201 | 61.4469
442.0625 | 123.2758 | -61.4914 | 61.6287 | 0.030283 | -0.035942 | -0.016578 | 0.002454 | 0.022531 | -0.001406 | 0.024268 | 61.5508 | 0.15248 | 61.4455 | -0.051417 | 0.01161 | 61.5662 | -0.001436 | 61.413 | 61.5217 | 61.4555 | 61.4748 | 61.4938 | 61.5139 | 61.49 | 61.5157 | 123.0422 | 61.6439 | 122.9369 | 61.44 | 61.503 | 123.0576 | 61.49 | 122.9044 | 61.5392 | 61.5523 | 61.4339 | 61.4469
443.0625 | 123.3032 | -61.4685 | 61.5829 | 0.025705 | -0.040521 | -0.021157 | -0.002124 | 0.027109 | -0.005985 | 0.01969 | 61.5417 | 0.1479 | 61.4317 | -0.051417 | 0.007032 | 61.5753 | -0.006014 | 61.4496 | 61.4942 | 61.428 | 61.4473 | 61.4664 | 61.4956 | 61.4625 | 61.4882 | 123.0102 | 61.6164 | 122.9002 | 61.4171 | 61.4755 | 123.0438 | 61.4625 | 122.9182 | 61.5346 | 61.5477 | 61.4247 | 61.4377
444.0625 | 123.3307 | -61.496 | 61.5967 | 0.021127 | -0.035942 | -0.016578 | -0.006703 | 0.017953 | -0.005985 | 0.01969 | 61.5417 | 0.1479 | 61.4317 | -0.055996 | 0.01161 | 61.5662 | -0.001436 | 61.4359 | 61.5171 | 61.46 | 61.4794 | 61.4893 | 61.5139 | 61.49 | 61.5157 | 123.0376 | 61.6439 | 122.9277 | 61.44 | 61.5076 | 123.0621 | 61.4945 | 122.9319 | 61.5301 | 61.5431 | 61.4201 | 61.4332
445.0625 | 123.3078 | -61.4822 | 61.5738 | 0.030283 | -0.040521 | -0.016578 | -0.006703 | 0.013375 | -0.005985 | 0.01969 | 61.5463 | 0.15248 | 61.4729 | -0.055996 | 0.007032 | 61.5662 | -0.001436 | 61.4313 | 61.5125 | 61.4417 | 61.4657 | 61.4755 | 61.4956 | 61.4763 | 61.5019 | 123.0285 | 61.6347 | 122.9552 | 61.4262 | 61.4893 | 123.0484 | 61.4808 | 122.9136 | 61.5392 | 61.5477 | 61.4659 | 61.4744
446.0625 | 123.3353 | -61.4777 | 61.5875 | 0.030283 | -0.040521 | -0.016578 | -0.011281 | 0.027109 | -0.005985 | 0.01969 | 61.5417 | 0.1479 | 61.4317 | -0.051417 | 0.01161 | 61.5662 | 0.003143 | 61.4451 | 61.5079 | 61.4371 | 61.4611 | 61.4664 | 61.5048 | 61.4717 | 61.4974 | 123.0193 | 61.6256 | 122.9094 | 61.4262 | 61.4893 | 123.0438 | 61.4808 | 122.9227 | 61.5301 | 61.5385 | 61.4201 | 61.4286
447.0625 | 123.3582 | -61.4502 | 61.5967 | 0.021127 | -0.040521 | -0.012 | -0.006703 | 0.017953 | 0.003172 | 0.024268 | 61.5417 | 0.15248 | 61.4729 | -0.051417 | 0.01161 | 61.5662 | -0.001436 | 61.4359 | 61.4713 | 61.4097 | 61.4382 | 61.4435 | 61.4681 | 61.4534 | 61.4745 | 122.9919 | 61.6027 | 122.9231 | 61.3988 | 61.4618 | 123.0164 | 61.4488 | 122.8861 | 61.5301 | 61.5431 | 61.4613 | 61.4744
448.0625 | 123.3215 | -61.4731 | 61.5784 | 0.025705 | -0.0451 | -0.016578 | -0.011281 | 0.017953 | -0.005985 | 0.01969 | 61.5417 | 0.1479 | 61.4363 | -0.051417 | 0.007032 | 61.5662 | 0.003143 | 61.4405 | 61.4988 | 61.428 | 61.4565 | 61.4618 | 61.491 | 61.4671 | 61.4928 | 123.0148 | 61.621 | 122.9094 | 61.4217 | 61.4801 | 123.0392 | 61.4762 | 122.9136 | 61.5346 | 61.5385 | 61.4293 | 61.4332
449.0625 | 123.3078 | -61.496 | 61.5875 | 0.034862 | -0.035942 | -0.025735 | -0.006703 | 0.022531 | -0.001406 | 0.028846 | 61.5463 | 0.15706 | 61.4821 | -0.055996 | 0.01161 | 61.5616 | -0.001436 | 61.4222 | 61.5308 | 61.46 | 61.4702 | 61.4893 | 61.5185 | 61.4946 | 61.5248 | 123.0422 | 61.653 | 122.9781 | 61.44 | 61.5076 | 123.0576 | 61.4945 | 122.9181 | 61.5346 | 61.5477 | 61.4705 | 61.4835
450.0625 | 123.3032 | -61.4777 | 61.6196 | 0.025705 | -0.040521 | -0.016578 | -0.011281 | 0.017953 | -0.005985 | 0.015112 | 61.5325 | 0.1479 | 61.418 | -0.051417 | 0.01161 | 61.5753 | 0.003143 | 61.4451 | 61.5034 | 61.4371 | 61.4611 | 61.4664 | 61.4956 | 61.4717 | 61.4928 | 123.0102 | 61.6256 | 122.8957 | 61.4262 | 61.4893 | 123.053 | 61.4808 | 122.9227 | 61.5209 | 61.5294 | 61.4064 | 61.4148
451.0625 | 123.3353 | -61.4594 | 61.5829 | 0.025705 | -0.040521 | -0.016578 | -0.011281 | 0.017953 | 0.003172 | 0.01969 | 61.5508 | 0.1479 | 61.4867 | -0.055996 | 0.01161 | 61.5707 | -0.006014 | 61.4268 | 61.4851 | 61.4188 | 61.4428 | 61.4481 | 61.4773 | 61.4625 | 61.479 | 123.0102 | 61.6073 | 122.946 | 61.4034 | 61.471 | 123.0301 | 61.4533 | 122.8861 | 61.5392 | 61.5568 | 61.4751 | 61.4927
452.0625 | 123.262 | -61.4914 | 61.647 | 0.025705 | -0.035942 | -0.016578 | -0.006703 | 0.017953 | -0.001406 | 0.024268 | 61.5371 | 0.15248 | 61.4409 | -0.051417 | 0.01161 | 61.5753 | -0.001436 | 61.4222 | 61.5171 | 61.4555 | 61.4748 | 61.4847 | 61.5093 | 61.49 | 61.5157 | 123.0285 | 61.6439 | 122.9323 | 61.44 | 61.503 | 123.0667 | 61.49 | 122.9136 | 61.5255 | 61.5385 | 61.4293 | 61.4423
453.0625 | 123.3398 | -61.4685 | 61.6013 | 0.030283 | -0.035942 | -0.012 | -0.011281 | 0.027109 | -0.005985 | 0.024268 | 61.5463 | 0.15706 | 61.4821 | -0.051417 | 0.01161 | 61.5707 | -0.006014 | 61.381 | 61.4988 | 61.4326 | 61.4565 | 61.4572 | 61.4956 | 61.4625 | 61.4928 | 123.0148 | 61.6256 | 122.9506 | 61.4171 | 61.4801 | 123.0392 | 61.4625 | 122.8495 | 61.5346 | 61.5523 | 61.4705 | 61.4881
454.0625 | 123.3719 | -61.441 | 61.5646 | 0.030283 | -0.040521 | -0.021157 | 0.002454 | 0.017953 | -0.005985 | 0.01969 | 61.5417 | 0.15248 | 61.4317 | -0.055996 | 0.01161 | 61.5707 | -0.006014 | 61.3901 | 61.4713 | 61.4005 | 61.4199 | 61.4435 | 61.459 | 61.4351 | 61.4607 | 122.9827 | 61.5935 | 122.8728 | 61.385 | 61.4526 | 123.0118 | 61.435 | 122.8312 | 61.5301 | 61.5477 | 61.4201 | 61.4377
455.0625 | 123.317 | -61.4685 | 61.5784 | 0.021127 | -0.040521 | -0.016578 | -0.011281 | 0.017953 | -0.005985 | 0.01969 | 61.5417 | 0.1479 | 61.4958 | -0.055996 | 0.016188 | 61.5662 | -0.010593 | 61.3764 | 61.4896 | 61.428 | 61.4519 | 61.4572 | 61.4865 | 61.4625 | 61.4882 | 123.0102 | 61.6164 | 122.9643 | 61.4125 | 61.4847 | 123.0347 | 61.4579 | 122.8449 | 61.5255 | 61.5523 | 61.4796 | 61.5064
456.0625 | 123.3582 | -61.4639 | 61.5692 | 0.021127 | -0.035942 | -0.021157 | -0.011281 | 0.027109 | -0.005985 | 0.015112 | 61.5371 | 0.15706 | 61.4226 | -0.065154 | 0.007032 | 61.5707 | -0.006014 | 61.381 | 61.4851 | 61.428 | 61.4428 | 61.4526 | 61.491 | 61.4579 | 61.479 | 123.001 | 61.621 | 122.8865 | 61.3988 | 61.471 | 123.0347 | 61.4579 | 122.8449 | 61.5301 | 61.5431 | 61.4155 | 61.4286
457.0625 | 123.2895 | -61.4365 | 61.5829 | 0.030283 | -0.035942 | -0.016578 | -0.01586 | 0.031687 | -0.005985 | 0.01969 | 61.5417 | 0.14332 | 61.4912 | -0.055996 | 0.002454 | 61.5662 | -0.001436 | 61.3901 | 61.4667 | 61.4005 | 61.4199 | 61.4206 | 61.4681 | 61.4305 | 61.4562 | 122.9781 | 61.5798 | 122.9277 | 61.3805 | 61.4389 | 123.0026 | 61.435 | 122.8266 | 61.5392 | 61.5431 | 61.4888 | 61.4927
458.0625 | 123.3398 | -61.4777 | 61.5601 | 0.030283 | -0.031363 | -0.016578 | -0.002124 | 0.022531 | -0.001406 | 0.024268 | 61.5508 | 0.15248 | 61.4317 | -0.055996 | 0.01161 | 61.5662 | -0.006014 | 61.381 | 61.5079 | 61.4463 | 61.4611 | 61.4755 | 61.5002 | 61.4763 | 61.5019 | 123.0285 | 61.6301 | 122.9094 | 61.4217 | 61.4893 | 123.0438 | 61.4716 | 122.8586 | 61.5392 | 61.5568 | 61.4201 | 61.4377
459.0625 | 123.2986 | -61.4777 | 61.5875 | 0.030283 | -0.040521 | -0.021157 | -0.006703 | 0.017953 | -0.005985 | 0.024268 | 61.5417 | 0.15248 | 61.4821 | -0.055996 | 0.01161 | 61.5662 | -0.001436 | 61.3764 | 61.5079 | 61.4371 | 61.4565 | 61.471 | 61.4956 | 61.4717 | 61.5019 | 123.0193 | 61.6301 | 122.9597 | 61.4217 | 61.4893 | 123.0438 | 61.4762 | 122.8541 | 61.5301 | 61.5431 | 61.4705 | 61.4835
460.0625 | 123.3032 | -61.4914 | 61.5372 | 0.025705 | -0.035942 | -0.021157 | -0.006703 | 0.022531 | -0.005985 | 0.01969 | 61.5371 | 0.15248 | 61.4317 | -0.051417 | 0.007032 | 61.5616 | 0.003143 | 61.3901 | 61.5171 | 61.4555 | 61.4702 | 61.4847 | 61.5139 | 61.4854 | 61.5111 | 123.0285 | 61.6439 | 122.9231 | 61.44 | 61.4984 | 123.053 | 61.4945 | 122.8815 | 61.5301 | 61.534 | 61.4247 | 61.4286
461.0625 | 123.3948 | -61.4594 | 61.5646 | 0.025705 | -0.035942 | -0.016578 | -0.006703 | 0.022531 | -0.001406 | 0.024268 | 61.5463 | 0.15248 | 61.4821 | -0.055996 | 0.01161 | 61.5707 | -0.001436 | 61.381 | 61.4851 | 61.4234 | 61.4428 | 61.4526 | 61.4819 | 61.4579 | 61.4836 | 123.0056 | 61.6118 | 122.9414 | 61.4034 | 61.471 | 123.0301 | 61.4579 | 122.8403 | 61.5346 | 61.5477 | 61.4705 | 61.4835
462.0625 | 123.3582 | -61.4731 | 61.5875 | 0.021127 | -0.040521 | -0.021157 | -0.006703 | 0.017953 | -0.010563 | 0.024268 | 61.5417 | 0.15706 | 61.4317 | -0.060575 | 0.016188 | 61.5662 | -0.001436 | 61.3901 | 61.4942 | 61.4326 | 61.4519 | 61.4664 | 61.491 | 61.4625 | 61.4974 | 123.0148 | 61.6301 | 122.9048 | 61.4125 | 61.4893 | 123.0392 | 61.4716 | 122.8632 | 61.5255 | 61.5431 | 61.4155 | 61.4332
463.0625 | 123.3948 | -61.4685 | 61.5601 | 0.025705 | -0.040521 | -0.012 | -0.006703 | 0.022531 | -0.005985 | 0.028846 | 61.5508 | 0.15248 | 61.4729 | -0.055996 | 0.01161 | 61.5707 | -0.001436 | 61.381 | 61.4942 | 61.428 | 61.4565 | 61.4618 | 61.491 | 61.4625 | 61.4974 | 123.0193 | 61.621 | 122.9414 | 61.4125 | 61.4801 | 123.0392 | 61.4671 | 122.8495 | 61.5392 | 61.5523 | 61.4613 | 61.4744
464.0625 | 123.3124 | -61.4914 | 61.5738 | 0.034862 | -0.040521 | -0.016578 | -0.006703 | 0.013375 | -0.005985 | 0.01969 | 61.5417 | 0.15706 | 61.4409 | -0.051417 | 0.016188 | 61.5616 | -0.001436 | 61.3856 | 61.5263 | 61.4509 | 61.4748 | 61.4847 | 61.5048 | 61.4854 | 61.5111 | 123.0331 | 61.6485 | 122.9323 | 61.44 | 61.5076 | 123.053 | 61.49 | 122.8769 | 61.5255 | 61.5431 | 61.4247 | 61.4423
465.0625 | 123.349 | -61.4731 | 61.5875 | 0.030283 | -0.040521 | -0.021157 | -0.006703 | 0.017953 | -0.005985 | 0.028846 | 61.5417 | 0.1479 | 61.4592 | -0.055996 | 0.01161 | 61.5662 | -0.006014 | 61.381 | 61.5034 | 61.4326 | 61.4519 | 61.4664 | 61.491 | 61.4671 | 61.5019 | 123.0148 | 61.621 | 122.9323 | 61.4171 | 61.4847 | 123.0392 | 61.4671 | 122.8541 | 61.5301 | 61.5477 | 61.4476 | 61.4652
466.0625 | 123.3398 | -61.4594 | 61.5646 | 0.025705 | -0.035942 | -0.012 | -0.011281 | 0.022531 | -0.005985 | 0.028846 | 61.5463 | 0.15248 | 61.4317 | -0.051417 | 0.01161 | 61.5707 | -0.001436 | 61.3764 | 61.4851 | 61.4234 | 61.4474 | 61.4481 | 61.4819 | 61.4534 | 61.4882 | 123.0056 | 61.6118 | 122.8911 | 61.4079 | 61.471 | 123.0301 | 61.4579 | 122.8357 | 61.5346 | 61.5477 | 61.4201 | 61.4332
467.0625 | 123.2666 | -61.4914 | 61.647 | 0.025705 | -0.035942 | -0.016578 | -0.006703 | 0.027109 | -0.001406 | 0.024268 | 61.5508 | 0.15248 | 61.4363 | -0.051417 | 0.01161 | 61.5707 | -0.006014 | 61.381 | 61.5171 | 61.4555 | 61.4748 | 61.4847 | 61.5185 | 61.49 | 61.5157 | 123.0422 | 61.6439 | 122.9277 | 61.44 | 61.503 | 123.0621 | 61.4854 | 122.8724 | 61.5392 | 61.5568 | 61.4247 | 61.4423
468.0625 | 123.4039 | -61.4548 | 61.5829 | 0.030283 | -0.0451 | -0.021157 | -0.006703 | 0.027109 | -0.001406 | 0.01969 | 61.5417 | 0.1479 | 61.4455 | -0.055996 | 0.007032 | 61.5662 | 0.003143 | 61.381 | 61.4851 | 61.4097 | 61.4336 | 61.4481 | 61.4819 | 61.4534 | 61.4745 | 122.9965 | 61.6027 | 122.9002 | 61.3988 | 61.4618 | 123.0209 | 61.4579 | 122.8357 | 61.5346 | 61.5385 | 61.4384 | 61.4423
469.0625 | 123.3215 | -61.4456 | 61.5692 | 0.025705 | -0.031363 | -0.012 | -0.006703 | 0.022531 | -0.005985 | 0.01969 | 61.5463 | 0.1479 | 61.4317 | -0.051417 | 0.016188 | 61.5707 | 0.003143 | 61.3764 | 61.4713 | 61.4143 | 61.4336 | 61.4389 | 61.4681 | 61.4396 | 61.4653 | 122.9919 | 61.5935 | 122.8773 | 61.3942 | 61.4618 | 123.0164 | 61.4488 | 122.822 | 61.5301 | 61.5431 | 61.4155 | 61.4286
470.0625 | 123.3398 | -61.4639 | 61.5692 | 0.034862 | -0.040521 | -0.012 | -0.002124 | 0.022531 | -0.010563 | 0.024268 | 61.5371 | 0.15706 | 61.4546 | -0.055996 | 0.007032 | 61.5707 | -0.006014 | 61.3764 | 61.4988 | 61.4234 | 61.4519 | 61.4618 | 61.4865 | 61.4534 | 61.4882 | 123.001 | 61.621 | 122.9185 | 61.4079 | 61.471 | 123.0347 | 61.4579 | 122.8403 | 61.5301 | 61.5431 | 61.4476 | 61.4606
471.0625 | 123.2986 | -61.4777 | 61.5967 | 0.021127 | -0.040521 | -0.021157 | -0.006703 | 0.013375 | -0.001406 | 0.01969 | 61.5463 | 0.15248 | 61.4409 | -0.055996 | 0.01161 | 61.5753 | -0.001436 | 61.381 | 61.4988 | 61.4371 | 61.4565 | 61.471 | 61.491 | 61.4763 | 61.4974 | 123.0239 | 61.6301 | 122.9185 | 61.4217 | 61.4893 | 123.053 | 61.4762 | 122.8586 | 61.5346 | 61.5477 | 61.4293 | 61.4423
472.0625 | 123.3765 | -61.4685 | 61.5875 | 0.030283 | -0.035942 | -0.016578 | -0.006703 | 0.022531 | -0.001406 | 0.028846 | 61.5508 | 0.15248 | 61.4821 | -0.051417 | 0.007032 | 61.5753 | -0.001436 | 61.3856 | 61.4988 | 61.4326 | 61.4519 | 61.4618 | 61.491 | 61.4671 | 61.4974 | 123.0193 | 61.621 | 122.9506 | 61.4171 | 61.4755 | 123.0438 | 61.4671 | 122.8541 | 61.5438 | 61.5523 | 61.4751 | 61.4835
473.0625 | 123.3353 | -61.4777 | 61.5829 | 0.025705 | -0.035942 | -0.021157 | -0.011281 | 0.017953 | -0.005985 | 0.024268 | 61.5417 | 0.1479 | 61.4226 | -0.051417 | 0.016188 | 61.5707 | -0.010593 | 61.3764 | 61.5034 | 61.4417 | 61.4565 | 61.4664 | 61.4956 | 61.4717 | 61.5019 | 123.0193 | 61.6256 | 122.9002 | 61.4262 | 61.4938 | 123.0484 | 61.4671 | 122.8541 | 61.5255 | 61.5523 | 61.4064 | 61.4332
474.0625 | 123.3673 | -61.4822 | 61.5372 | 0.034862 | -0.035942 | -0.012 | -0.011281 | 0.022531 | -0.005985 | 0.01969 | 61.5463 | 0.15248 | 61.4867 | -0.055996 | 0.016188 | 61.5662 | -0.010593 | 61.381 | 61.5171 | 61.4463 | 61.4702 | 61.471 | 61.5048 | 61.4763 | 61.5019 | 123.0285 | 61.6347 | 122.9689 | 61.4262 | 61.4984 | 123.0484 | 61.4716 | 122.8632 | 61.5301 | 61.5568 | 61.4705 | 61.4973
475.0625 | 123.3765 | -61.4731 | 61.5738 | 0.025705 | -0.031363 | -0.016578 | -0.006703 | 0.022531 | -0.005985 | 0.01969 | 61.5417 | 0.16164 | 61.4271 | -0.046838 | 0.01161 | 61.5753 | -0.001436 | 61.3764 | 61.4988 | 61.4417 | 61.4565 | 61.4664 | 61.4956 | 61.4671 | 61.4928 | 123.0148 | 61.6347 | 122.9002 | 61.4262 | 61.4847 | 123.0484 | 61.4716 | 122.8495 | 61.5301 | 61.5431 | 61.4155 | 61.4286
476.0625 | 123.349 | -61.4685 | 61.5555 | 0.025705 | -0.035942 | -0.021157 | -0.002124 | 0.022531 | 0.003172 | 0.024268 | 61.5508 | 0.15706 | 61.4821 | -0.046838 | 0.007032 | 61.5662 | -0.006014 | 61.381 | 61.4942 | 61.4326 | 61.4473 | 61.4664 | 61.491 | 61.4717 | 61.4928 | 123.0193 | 61.6256 | 122.9506 | 61.4217 | 61.4755 | 123.0347 | 61.4625 | 122.8495 | 61.5438 | 61.5568 | 61.4751 | 61.4881
477.0625 | 123.3582 | -61.4594 | 61.6104 | 0.030283 | -0.035942 | -0.016578 | -0.002124 | 0.027109 | -0.005985 | 0.01969 | 61.5417 | 0.15706 | 61.4409 | -0.055996 | 0.01161 | 61.5707 | 0.003143 | 61.3856 | 61.4896 | 61.4234 | 61.4428 | 61.4572 | 61.4865 | 61.4534 | 61.479 | 123.001 | 61.6164 | 122.9002 | 61.4034 | 61.471 | 123.0301 | 61.4625 | 122.8449 | 61.5301 | 61.5385 | 61.4293 | 61.4377
478.0625 | 123.2986 | -61.4456 | 61.5921 | 0.025705 | -0.035942 | -0.016578 | -0.006703 | 0.017953 | 0.003172 | 0.01969 | 61.5463 | 0.15248 | 61.4821 | -0.051417 | 0.007032 | 61.5707 | -0.010593 | 61.381 | 61.4713 | 61.4097 | 61.429 | 61.4389 | 61.4636 | 61.4488 | 61.4653 | 122.9919 | 61.5981 | 122.9277 | 61.3942 | 61.4527 | 123.0164 | 61.435 | 122.8266 | 61.5392 | 61.5568 | 61.4751 | 61.4927
479.0625 | 123.3536 | -61.4594 | 61.5555 | 0.021127 | -0.040521 | -0.025735 | -0.006703 | 0.017953 | -0.010563 | 0.015112 | 61.5417 | 0.15248 | 61.4317 | -0.051417 | 0.01161 | 61.5662 | -0.006014 | 61.381 | 61.4805 | 61.4188 | 61.4336 | 61.4526 | 61.4773 | 61.4488 | 61.4745 | 123.001 | 61.6118 | 122.8911 | 61.4079 | 61.471 | 123.0255 | 61.4533 | 122.8403 | 61.5301 | 61.5477 | 61.4201 | 61.4377
480.0625 | 123.3078 | -61.4594 | 61.5692 | 0.030283 | -0.026784 | -0.016578 | -0.002124 | 0.022531 | -0.005985 | 0.015112 | 61.5463 | 0.1479 | 61.4867 | -0.051417 | 0.01161 | 61.5662 | -0.001436 | 61.381 | 61.4896 | 61.4326 | 61.4428 | 61.4572 | 61.4819 | 61.4534 | 61.4745 | 123.0056 | 61.6073 | 122.946 | 61.4079 | 61.471 | 123.0255 | 61.4579 | 122.8403 | 61.5346 | 61.5477 | 61.4751 | 61.4881
481.0625 | 123.3765 | -61.4639 | 61.5784 | 0.030283 | -0.040521 | -0.016578 | 0.002454 | 0.017953 | -0.005985 | 0.015112 | 61.5463 | 0.1479 | 61.4226 | -0.055996 | 0.007032 | 61.5616 | -0.001436 | 61.381 | 61.4942 | 61.4234 | 61.4474 | 61.4664 | 61.4819 | 61.4579 | 61.479 | 123.0102 | 61.6118 | 122.8865 | 61.4079 | 61.471 | 123.0255 | 61.4625 | 122.8449 | 61.5392 | 61.5477 | 61.4155 | 61.424
482.0625 | 123.3078 | -61.4731 | 61.6196 | 0.021127 | -0.035942 | -0.016578 | -0.002124 | 0.031687 | -0.005985 | 0.01969 | 61.5417 | 0.15706 | 61.4729 | -0.060575 | 0.01161 | 61.5707 | 0.003143 | 61.381 | 61.4942 | 61.4371 | 61.4565 | 61.471 | 61.5048 | 61.4671 | 61.4928 | 123.0148 | 61.6301 | 122.946 | 61.4125 | 61.4847 | 123.0438 | 61.4762 | 122.8541 | 61.5301 | 61.5385 | 61.4613 | 61.4698
483.0625 | 123.349 | -61.4685 | 61.5829 | 0.030283 | -0.031363 | -0.021157 | -0.006703 | 0.027109 | -0.005985 | 0.028846 | 61.5371 | 0.15706 | 61.4363 | -0.055996 | 0.016188 | 61.5753 | 0.003143 | 61.3856 | 61.4988 | 61.4371 | 61.4473 | 61.4618 | 61.4956 | 61.4625 | 61.4974 | 123.0056 | 61.6256 | 122.9048 | 61.4125 | 61.4847 | 123.0438 | 61.4716 | 122.8541 | 61.5209 | 61.534 | 61.4201 | 61.4332
484.0625 | 123.3673 | -61.4731 | 61.5692 | 0.025705 | -0.035942 | -0.016578 | -0.011281 | 0.027109 | -0.001406 | 0.01969 | 61.56 | 0.16164 | 61.4821 | -0.051417 | 0.007032 | 61.5662 | -0.006014 | 61.381 | 61.4988 | 61.4371 | 61.4565 | 61.4618 | 61.5002 | 61.4717 | 61.4928 | 123.0331 | 61.6347 | 122.9552 | 61.4217 | 61.4801 | 123.0392 | 61.4671 | 122.8541 | 61.553 | 61.566 | 61.4751 | 61.4881
485.0625 | 123.3261 | -61.4639 | 61.5829 | 0.025705 | -0.031363 | -0.016578 | -0.006703 | 0.022531 | -0.005985 | 0.01969 | 61.5463 | 0.15248 | 61.45 | -0.051417 | 0.01161 | 61.5707 | -0.001436 | 61.3764 | 61.4896 | 61.4326 | 61.4474 | 61.4572 | 61.4865 | 61.4579 | 61.4836 | 123.0102 | 61.6164 | 122.914 | 61.4125 | 61.4755 | 123.0347 | 61.4625 | 122.8403 | 61.5346 | 61.5477 | 61.4384 | 61.4515
486.0625 | 123.317 | -61.4777 | 61.5784 | 0.034862 | -0.040521 | -0.021157 | -0.006703 | 0.027109 | -0.001406 | 0.01969 | 61.5463 | 0.15706 | 61.4271 | -0.055996 | 0.01161 | 61.5707 | -0.006014 | 61.381 | 61.5125 | 61.4371 | 61.4565 | 61.471 | 61.5048 | 61.4763 | 61.4974 | 123.0239 | 61.6347 | 122.9048 | 61.4217 | 61.4893 | 123.0484 | 61.4716 | 122.8586 | 61.5346 | 61.5523 | 61.4155 | 61.4332
487.0625 | 123.2758 | -61.4777 | 61.6104 | 0.034862 | -0.031363 | -0.012 | 0.002454 | 0.017953 | -0.001406 | 0.028846 | 61.5554 | 0.16164 | 61.4867 | -0.051417 | 0.01161 | 61.5662 | -0.006014 | 61.381 | 61.5125 | 61.4463 | 61.4657 | 61.4801 | 61.4956 | 61.4763 | 61.5065 | 123.0331 | 61.6393 | 122.9643 | 61.4262 | 61.4893 | 123.0438 | 61.4716 | 122.8586 | 61.5438 | 61.5614 | 61.4751 | 61.4927
488.0625 | 123.3398 | -61.4731 | 61.5875 | 0.025705 | -0.035942 | -0.025735 | -0.006703 | 0.017953 | -0.005985 | 0.024268 | 61.5463 | 0.16164 | 61.4409 | -0.055996 | 0.020767 | 61.5616 | -0.001436 | 61.3764 | 61.4988 | 61.4371 | 61.4473 | 61.4664 | 61.491 | 61.4671 | 61.4974 | 123.0193 | 61.6347 | 122.914 | 61.4171 | 61.4939 | 123.0347 | 61.4716 | 122.8495 | 61.5255 | 61.5477 | 61.4201 | 61.4423
489.0625 | 123.3398 | -61.4639 | 61.5692 | 0.025705 | -0.031363 | -0.016578 | -0.002124 | 0.017953 | -0.005985 | 0.01969 | 61.5417 | 0.1479 | 61.4363 | -0.060575 | 0.01161 | 61.5616 | -0.001436 | 61.3856 | 61.4896 | 61.4326 | 61.4474 | 61.4618 | 61.4819 | 61.4579 | 61.4836 | 123.0056 | 61.6118 | 122.9002 | 61.4034 | 61.4755 | 123.0255 | 61.4625 | 122.8495 | 61.5301 | 61.5431 | 61.4247 | 61.4377
490.0625 | 123.3627 | -61.4685 | 61.5646 | 0.030283 | -0.031363 | -0.021157 | -0.006703 | 0.027109 | -0.005985 | 0.024268 | 61.5463 | 0.15248 | 61.4821 | -0.055996 | 0.01161 | 61.5662 | -0.001436 | 61.3764 | 61.4988 | 61.4371 | 61.4473 | 61.4618 | 61.4956 | 61.4625 | 61.4928 | 123.0148 | 61.621 | 122.9506 | 61.4125 | 61.4801 | 123.0347 | 61.4671 | 122.8449 | 61.5346 | 61.5477 | 61.4705 | 61.4835
491.0625 | 123.3032 | -61.4914 | 61.5829 | 0.030283 | -0.035942 | -0.016578 | -0.002124 | 0.022531 | -0.010563 | 0.024268 | 61.5417 | 0.15248 | 61.4363 | -0.046838 | 0.016188 | 61.5707 | -0.006014 | 61.3856 | 61.5217 | 61.4555 | 61.4748 | 61.4893 | 61.5139 | 61.4808 | 61.5157 | 123.0331 | 61.6439 | 122.9277 | 61.4446 | 61.5076 | 123.0621 | 61.4854 | 122.8769 | 61.5255 | 61.5477 | 61.4201 | 61.4423
492.0625 | 123.3627 | -61.4227 | 61.5921 | 0.030283 | -0.0451 | -0.016578 | -0.006703 | 0.027109 | -0.005985 | 0.024268 | 61.5554 | 0.15248 | 61.4638 | -0.046838 | 0.01161 | 61.5707 | -0.001436 | 61.3901 | 61.453 | 61.3776 | 61.4062 | 61.416 | 61.4498 | 61.4167 | 61.447 | 122.9781 | 61.5752 | 122.8865 | 61.3759 | 61.4343 | 122.9935 | 61.4213 | 122.8129 | 61.5438 | 61.5568 | 61.4522 | 61.4652
493.0625 | 123.3444 | -61.4594 | 61.5875 | 0.030283 | -0.040521 | -0.021157 | -0.002124 | 0.022531 | -0.010563 | 0.01969 | 61.5508 | 0.15248 | 61.4775 | -0.051417 | 0.016188 | 61.5662 | -0.001436 | 61.3856 | 61.4896 | 61.4188 | 61.4382 | 61.4572 | 61.4819 | 61.4488 | 61.479 | 123.0102 | 61.6118 | 122.9369 | 61.4079 | 61.4755 | 123.0255 | 61.4579 | 122.8449 | 61.5346 | 61.5523 | 61.4613 | 61.4789
494.0625 | 123.3353 | -61.4685 | 61.5829 | 0.025705 | -0.040521 | -0.021157 | -0.006703 | 0.027109 | -0.005985 | 0.015112 | 61.5417 | 0.1479 | 61.418 | -0.051417 | 0.007032 | 61.5662 | -0.006014 | 61.3856 | 61.4942 | 61.428 | 61.4473 | 61.4618 | 61.4956 | 61.4625 | 61.4836 | 123.0102 | 61.6164 | 122.8865 | 61.4171 | 61.4755 | 123.0347 | 61.4625 | 122.8541 | 61.5346 | 61.5477 | 61.411 | 61.424
495.0625 | 123.381 | -61.4639 | 61.5692 | 0.030283 | -0.035942 | -0.012 | -0.006703 | 0.017953 | -0.001406 | 0.01969 | 61.5371 | 0.1479 | 61.4775 | -0.055996 | 0.016188 | 61.5707 | -0.006014 | 61.3764 | 61.4942 | 61.428 | 61.4519 | 61.4572 | 61.4819 | 61.4625 | 61.4836 | 123.001 | 61.6118 | 122.9414 | 61.4079 | 61.4801 | 123.0347 | 61.4579 | 122.8403 | 61.5209 | 61.5431 | 61.4613 | 61.4835
496.0625 | 123.3124 | -61.4822 | 61.5601 | 0.025705 | -0.035942 | -0.021157 | -0.011281 | 0.017953 | -0.005985 | 0.024268 | 61.5554 | 0.15706 | 61.4821 | -0.055996 | 0.007032 | 61.5616 | 0.003143 | 61.3856 | 61.5079 | 61.4463 | 61.4611 | 61.471 | 61.5002 | 61.4763 | 61.5065 | 123.0377 | 61.6393 | 122.9643 | 61.4262 | 61.4893 | 123.0438 | 61.4854 | 122.8678 | 61.5484 | 61.5523 | 61.4751 | 61.4789
497.0625 | 123.3719 | -61.4365 | 61.6013 | 0.025705 | -0.035942 | -0.016578 | -0.002124 | 0.022531 | -0.005985 | 0.024268 | 61.5463 | 0.16164 | 61.4317 | -0.051417 | 0.016188 | 61.5707 | -0.001436 | 61.381 | 61.4622 | 61.4005 | 61.4199 | 61.4343 | 61.459 | 61.4305 | 61.4607 | 122.9827 | 61.5981 | 122.8682 | 61.385 | 61.4526 | 123.0072 | 61.435 | 122.8174 | 61.5301 | 61.5477 | 61.4155 | 61.4332
498.0625 | 123.2941 | -61.4685 | 61.5921 | 0.030283 | -0.0451 | -0.021157 | -0.011281 | 0.022531 | -0.010563 | 0.024268 | 61.5417 | 0.15706 | 61.4271 | -0.046838 | 0.01161 | 61.5662 | -0.001436 | 61.3856 | 61.4988 | 61.4234 | 61.4473 | 61.4572 | 61.491 | 61.4579 | 61.4928 | 123.0102 | 61.6256 | 122.8957 | 61.4217 | 61.4801 | 123.0347 | 61.4671 | 122.8541 | 61.5301 | 61.5431 | 61.4155 | 61.4286
499.0625 | 123.3444 | -61.4777 | 61.5738 | 0.025705 | -0.031363 | -0.016578 | -0.002124 | 0.022531 | -0.001406 | 0.015112 | 61.5463 | 0.1479 | 61.4363 | -0.051417 | 0.01161 | 61.5662 | -0.001436 | 61.3856 | 61.5034 | 61.4463 | 61.4611 | 61.4755 | 61.5002 | 61.4763 | 61.4928 | 123.0239 | 61.6256 | 122.914 | 61.4262 | 61.4893 | 123.0438 | 61.4762 | 122.8632 | 61.5346 | 61.5477 | 61.4247 | 61.4377
500.0625 | 123.3078 | -61.4822 | 61.5463 | 0.025705 | -0.031363 | -0.007421 | -0.006703 | 0.017953 | -0.010563 | 0.01969 | 61.5508 | 0.16164 | 61.4912 | -0.051417 | 0.016188 | 61.5707 | 0.003143 | 61.381 | 61.5079 | 61.4509 | 61.4748 | 61.4755 | 61.5002 | 61.4717 | 61.5019 | 123.0331 | 61.6439 | 122.9735 | 61.4308 | 61.4984 | 123.053 | 61.4854 | 122.8632 | 61.5346 | 61.5477 | 61.4751 | 61.4881
501.0625 | 123.3902 | -61.4639 | 61.5738 | 0.021127 | -0.035942 | -0.016578 | -0.002124 | 0.022531 | -0.001406 | 0.024268 | 61.5417 | 0.15706 | 61.4271 | -0.046838 | 0.01161 | 61.5707 | -0.006014 | 61.381 | 61.4851 | 61.428 | 61.4474 | 61.4618 | 61.4865 | 61.4625 | 61.4882 | 123.0056 | 61.621 | 122.8911 | 61.4171 | 61.4755 | 123.0347 | 61.4579 | 122.8449 | 61.5301 | 61.5477 | 61.4155 | 61.4332
502.0625 | 123.3444 | -61.4502 | 61.6013 | 0.025705 | -0.031363 | -0.012 | -0.006703 | 0.027109 | -0.005985 | 0.033424 | 61.5463 | 0.1479 | 61.4546 | -0.055996 | 0.016188 | 61.5753 | -0.006014 | 61.3901 | 61.4759 | 61.4188 | 61.4382 | 61.4435 | 61.4773 | 61.4442 | 61.4836 | 122.9965 | 61.5981 | 122.9048 | 61.3942 | 61.4664 | 123.0255 | 61.4442 | 122.8403 | 61.5301 | 61.5523 | 61.4384 | 61.4606
503.0625 | 123.349 | -61.4456 | 61.5738 | 0.025705 | -0.035942 | -0.012 | -0.002124 | 0.022531 | -0.005985 | 0.01969 | 61.5463 | 0.15706 | 61.4775 | -0.046838 | 0.01161 | 61.5707 | -0.001436 | 61.381 | 61.4713 | 61.4097 | 61.4336 | 61.4435 | 61.4681 | 61.4396 | 61.4653 | 122.9919 | 61.6027 | 122.9231 | 61.3988 | 61.4572 | 123.0164 | 61.4442 | 122.8266 | 61.5346 | 61.5477 | 61.4659 | 61.4789
504.0625 | 123.3902 | -61.4319 | 61.5784 | 0.030283 | -0.031363 | -0.016578 | -0.006703 | 0.017953 | -0.001406 | 0.01969 | 61.5417 | 0.16622 | 61.4226 | -0.055996 | 0.002454 | 61.5753 | -0.001436 | 61.381 | 61.4622 | 61.4005 | 61.4153 | 61.4252 | 61.4498 | 61.4305 | 61.4516 | 122.9736 | 61.5981 | 122.8545 | 61.3759 | 61.4343 | 123.0072 | 61.4304 | 122.8129 | 61.5392 | 61.5431 | 61.4201 | 61.424
505.0625 | 123.3582 | -61.4868 | 61.5784 | 0.030283 | -0.0451 | -0.016578 | -0.006703 | 0.027109 | -0.005985 | 0.024268 | 61.5463 | 0.15706 | 61.4821 | -0.051417 | 0.01161 | 61.5662 | -0.001436 | 61.3718 | 61.5171 | 61.4417 | 61.4702 | 61.4801 | 61.5139 | 61.4808 | 61.5111 | 123.0331 | 61.6439 | 122.9689 | 61.4354 | 61.4984 | 123.053 | 61.4854 | 122.8586 | 61.5346 | 61.5477 | 61.4705 | 61.4835
506.0625 | 123.3536 | -61.4731 | 61.5921 | 0.034862 | -0.035942 | -0.030314 | -0.002124 | 0.027109 | -0.005985 | 0.024268 | 61.5417 | 0.15706 | 61.45 | -0.046838 | 0.01161 | 61.5707 | -0.001436 | 61.381 | 61.5079 | 61.4371 | 61.4428 | 61.471 | 61.5002 | 61.4671 | 61.4974 | 123.0148 | 61.6301 | 122.9231 | 61.4262 | 61.4847 | 123.0438 | 61.4716 | 122.8541 | 61.5301 | 61.5431 | 61.4384 | 61.4515
507.0625 | 123.3719 | -61.4502 | 61.6058 | 0.021127 | -0.035942 | -0.016578 | -0.011281 | 0.017953 | -0.005985 | 0.01969 | 61.5463 | 0.16164 | 61.4271 | -0.051417 | 0.025345 | 61.5662 | -0.006014 | 61.381 | 61.4713 | 61.4143 | 61.4336 | 61.4389 | 61.4681 | 61.4442 | 61.4699 | 122.9965 | 61.6118 | 122.8773 | 61.3988 | 61.4755 | 123.0164 | 61.4442 | 122.8312 | 61.5209 | 61.5523 | 61.4018 | 61.4332
508.0625 | 123.3719 | -61.4685 | 61.5829 | 0.025705 | -0.031363 | -0.012 | -0.002124 | 0.022531 | -0.001406 | 0.01969 | 61.56 | 0.16622 | 61.4775 | -0.055996 | 0.01161 | 61.5707 | -0.001436 | 61.381 | 61.4942 | 61.4371 | 61.4565 | 61.4664 | 61.491 | 61.4671 | 61.4882 | 123.0285 | 61.6347 | 122.946 | 61.4125 | 61.4801 | 123.0392 | 61.4671 | 122.8495 | 61.5484 | 61.5614 | 61.4659 | 61.4789
509.0625 | 123.2849 | -61.5005 | 61.5967 | 0.034862 | -0.035942 | -0.016578 | -0.006703 | 0.022531 | -0.010563 | 0.01969 | 61.5508 | 0.15706 | 61.4363 | -0.055996 | 0.007032 | 61.5707 | 0.007721 | 61.3856 | 61.5354 | 61.4646 | 61.484 | 61.4938 | 61.5231 | 61.49 | 61.5202 | 123.0514 | 61.6576 | 122.9369 | 61.4446 | 61.5076 | 123.0713 | 61.5083 | 122.8861 | 61.5438 | 61.5431 | 61.4293 | 61.4286
510.0625 | 123.3994 | -61.4548 | 61.5829 | 0.025705 | -0.040521 | -0.016578 | 0.002454 | 0.022531 | -0.001406 | 0.024268 | 61.5463 | 0.15248 | 61.4317 | -0.046838 | 0.01161 | 61.5662 | -0.006014 | 61.381 | 61.4805 | 61.4143 | 61.4382 | 61.4572 | 61.4773 | 61.4534 | 61.479 | 123.001 | 61.6073 | 122.8865 | 61.4079 | 61.4664 | 123.0209 | 61.4488 | 122.8357 | 61.5346 | 61.5523 | 61.4201 | 61.4377
511.0625 | 123.3398 | -61.4639 | 61.5509 | 0.030283 | -0.035942 | -0.016578 | -0.01586 | 0.027109 | -0.010563 | 0.024268 | 61.5554 | 0.15248 | 61.4821 | -0.055996 | 0.01161 | 61.5616 | -0.010593 | 61.3764 | 61.4942 | 61.428 | 61.4474 | 61.4481 | 61.491 | 61.4534 | 61.4882 | 123.0193 | 61.6164 | 122.946 | 61.4079 | 61.4755 | 123.0255 | 61.4533 | 122.8403 | 61.5438 | 61.566 | 61.4705 | 61.4927
512.0625 | 123.3444 | -61.4731 | 61.5646 | 0.021127 | -0.035942 | -0.025735 | -0.020438 | 0.017953 | -0.015142 | 0.024268 | 61.5463 | 0.15706 | 61.4363 | -0.051417 | 0.01161 | 61.5753 | 0.007721 | 61.3856 | 61.4942 | 61.4371 | 61.4473 | 61.4526 | 61.491 | 61.4579 | 61.4974 | 123.0193 | 61.6301 | 122.9094 | 61.4217 | 61.4847 | 123.0484 | 61.4808 | 122.8586 | 61.5346 | 61.5385 | 61.4247 | 61.4286
513.0625 | 123.3582 | -61.4639 | 61.5875 | 0.025705 | -0.035942 | -0.016578 | 0.002454 | 0.017953 | -0.005985 | 0.015112 | 61.5417 | 0.15248 | 61.4317 | -0.051417 | 0.01161 | 61.5616 | 0.003143 | 61.3856 | 61.4896 | 61.428 | 61.4474 | 61.4664 | 61.4819 | 61.4579 | 61.479 | 123.0056 | 61.6164 | 122.8957 | 61.4125 | 61.4755 | 123.0255 | 61.4671 | 122.8495 | 61.5301 | 61.5385 | 61.4201 | 61.4286
514.0625 | 123.3353 | -61.4685 | 61.5738 | 0.030283 | -0.031363 | -0.021157 | -0.006703 | 0.027109 | -0.001406 | 0.024268 | 61.56 | 0.15706 | 61.4867 | -0.046838 | 0.016188 | 61.5707 | -0.010593 | 61.381 | 61.4988 | 61.4371 | 61.4473 | 61.4618 | 61.4956 | 61.4671 | 61.4928 | 123.0285 | 61.6256 | 122.9552 | 61.4217 | 61.4847 | 123.0392 | 61.4579 | 122.8495 | 61.5438 | 61.5706 | 61.4705 | 61.4973
515.0625 | 123.2849 | -61.4822 | 61.6104 | 0.030283 | -0.035942 | -0.012 | -0.011281 | 0.022531 | -0.005985 | 0.024268 | 61.5508 | 0.15706 | 61.4317 | -0.051417 | 0.01161 | 61.5707 | -0.001436 | 61.3856 | 61.5125 | 61.4463 | 61.4702 | 61.471 | 61.5048 | 61.4763 | 61.5065 | 123.0331 | 61.6393 | 122.914 | 61.4308 | 61.4938 | 123.053 | 61.4808 | 122.8678 | 61.5392 | 61.5523 | 61.4201 | 61.4332
516.0625 | 123.1476 | -61.528 | 61.5601 | 0.025705 | -0.035942 | -0.016578 | -0.006703 | 0.031687 | -0.001406 | 0.01969 | 61.5417 | 0.1479 | 61.4409 | -0.055996 | 0.016188 | 61.5662 | -0.006014 | 61.3901 | 61.5537 | 61.4921 | 61.5114 | 61.5213 | 61.5597 | 61.5266 | 61.5477 | 123.0697 | 61.6759 | 122.9689 | 61.472 | 61.5442 | 123.0942 | 61.522 | 122.9181 | 61.5255 | 61.5477 | 61.4247 | 61.4469
517.0625 | 123.3627 | -61.4822 | 61.5646 | 0.034862 | -0.031363 | -0.012 | -0.002124 | 0.017953 | -0.005985 | 0.01969 | 61.5554 | 0.15706 | 61.4821 | -0.055996 | 0.016188 | 61.5616 | -0.001436 | 61.3764 | 61.5171 | 61.4509 | 61.4702 | 61.4801 | 61.5002 | 61.4763 | 61.5019 | 123.0377 | 61.6393 | 122.9643 | 61.4262 | 61.4984 | 123.0438 | 61.4808 | 122.8586 | 61.5392 | 61.5568 | 61.4659 | 61.4835
518.0625 | 123.3444 | -61.5005 | 61.5921 | 0.03944 | -0.035942 | -0.021157 | 0.002454 | 0.017953 | -0.005985 | 0.015112 | 61.5508 | 0.15248 | 61.4867 | -0.051417 | 0.01161 | 61.5616 | -0.006014 | 61.381 | 61.54 | 61.4646 | 61.4794 | 61.503 | 61.5185 | 61.4946 | 61.5157 | 123.0514 | 61.653 | 122.9872 | 61.4491 | 61.5122 | 123.0621 | 61.4945 | 122.8815 | 61.5392 | 61.5568 | 61.4751 | 61.4927
519.0625 | 123.317 | -61.4777 | 61.6013 | 0.030283 | -0.035942 | -0.021157 | -0.006703 | 0.027109 | -0.005985 | 0.024268 | 61.5463 | 0.15706 | 61.418 | -0.051417 | 0.016188 | 61.5662 | -0.010593 | 61.3901 | 61.5079 | 61.4417 | 61.4565 | 61.471 | 61.5048 | 61.4717 | 61.5019 | 123.0239 | 61.6347 | 122.8957 | 61.4262 | 61.4938 | 123.0438 | 61.4671 | 122.8678 | 61.5301 | 61.5568 | 61.4018 | 61.4286
520.0625 | 123.262 | -61.4914 | 61.6058 | 0.034862 | -0.035942 | -0.016578 | -0.002124 | 0.017953 | -0.010563 | 0.015112 | 61.5463 | 0.15706 | 61.4363 | -0.051417 | 0.01161 | 61.5707 | -0.010593 | 61.3856 | 61.5263 | 61.4555 | 61.4748 | 61.4893 | 61.5093 | 61.4808 | 61.5065 | 123.0377 | 61.6485 | 122.9277 | 61.44 | 61.503 | 123.0621 | 61.4808 | 122.8769 | 61.5346 | 61.5568 | 61.4247 | 61.4469
521.0625 | 123.2895 | -61.4822 | 61.6287 | 0.021127 | -0.040521 | -0.007421 | -0.002124 | 0.022531 | -0.005985 | 0.01969 | 61.5554 | 0.15706 | 61.4638 | -0.051417 | 0.01161 | 61.5707 | 0.003143 | 61.381 | 61.5034 | 61.4417 | 61.4748 | 61.4801 | 61.5048 | 61.4763 | 61.5019 | 123.0377 | 61.6393 | 122.946 | 61.4308 | 61.4938 | 123.053 | 61.4854 | 122.8632 | 61.5438 | 61.5523 | 61.4522 | 61.4606
522.0625 | 123.3124 | -61.4868 | 61.6058 | 0.030283 | -0.040521 | -0.012 | -0.006703 | 0.017953 | -0.010563 | 0.01969 | 61.5463 | 0.16164 | 61.4867 | -0.051417 | 0.01161 | 61.5799 | -0.006014 | 61.3718 | 61.5171 | 61.4463 | 61.4748 | 61.4801 | 61.5048 | 61.4763 | 61.5065 | 123.0331 | 61.6485 | 122.9735 | 61.4354 | 61.4984 | 123.0667 | 61.4808 | 122.8586 | 61.5346 | 61.5523 | 61.4751 | 61.4927
523.0625 | 123.3536 | -61.4594 | 61.6287 | 0.021127 | -0.031363 | -0.016578 | -0.002124 | 0.027109 | -0.001406 | 0.024268 | 61.5508 | 0.15706 | 61.4363 | -0.051417 | 0.016188 | 61.5753 | 0.003143 | 61.381 | 61.4805 | 61.428 | 61.4428 | 61.4572 | 61.4865 | 61.4579 | 61.4836 | 123.0102 | 61.6164 | 122.8957 | 61.4079 | 61.4755 | 123.0347 | 61.4625 | 122.8403 | 61.5346 | 61.5477 | 61.4201 | 61.4332
524.0625 | 123.2483 | -61.4914 | 61.6379 | 0.030283 | -0.035942 | -0.012 | -0.011281 | 0.027109 | -0.001406 | 0.024268 | 61.5463 | 0.15706 | 61.4226 | -0.051417 | 0.016188 | 61.5662 | -0.015171 | 61.381 | 61.5217 | 61.4555 | 61.4794 | 61.4801 | 61.5185 | 61.49 | 61.5157 | 123.0377 | 61.6485 | 122.914 | 61.44 | 61.5076 | 123.0576 | 61.4762 | 122.8724 | 61.5301 | 61.5614 | 61.4064 | 61.4377
525.0469 | 123.2437 | -61.5051 | 61.6379 | 0.030283 | -0.035942 | -0.021157 | -0.006703 | 0.013375 | -0.001406 | 0.024268 | 61.5508 | 0.15706 | 61.4546 | -0.055996 | 0.020767 | 61.5662 | 0.003143 | 61.381 | 61.5354 | 61.4692 | 61.484 | 61.4984 | 61.5185 | 61.5037 | 61.5294 | 123.056 | 61.6622 | 122.9597 | 61.4491 | 61.5259 | 123.0713 | 61.5083 | 122.8861 | 61.5301 | 61.5477 | 61.4339 | 61.4515
526.0625 | 123.2346 | -61.4868 | 61.6379 | 0.030283 | -0.040521 | -0.012 | -0.002124 | 0.022531 | -0.005985 | 0.024268 | 61.5508 | 0.16164 | 61.4821 | -0.055996 | 0.016188 | 61.5707 | -0.006014 | 61.381 | 61.5171 | 61.4463 | 61.4748 | 61.4847 | 61.5093 | 61.4808 | 61.5111 | 123.0377 | 61.6485 | 122.9689 | 61.4308 | 61.503 | 123.0576 | 61.4808 | 122.8678 | 61.5346 | 61.5568 | 61.4659 | 61.4881
527.0625 | 123.317 | -61.4777 | 61.6379 | 0.025705 | -0.031363 | -0.012 | -0.002124 | 0.022531 | -0.001406 | 0.015112 | 61.5554 | 0.15706 | 61.4409 | -0.046838 | 0.016188 | 61.5707 | -0.001436 | 61.381 | 61.5034 | 61.4463 | 61.4657 | 61.4755 | 61.5002 | 61.4763 | 61.4928 | 123.0331 | 61.6347 | 122.9185 | 61.4308 | 61.4938 | 123.0484 | 61.4762 | 122.8586 | 61.5392 | 61.5568 | 61.4247 | 61.4423
528.0625 | 123.3398 | -61.4868 | 61.5967 | 0.021127 | -0.035942 | -0.012 | -0.011281 | 0.017953 | -0.001406 | 0.028846 | 61.5463 | 0.16164 | 61.4226 | -0.051417 | 0.01161 | 61.5753 | 0.003143 | 61.381 | 61.5079 | 61.4509 | 61.4748 | 61.4755 | 61.5048 | 61.4854 | 61.5157 | 123.0331 | 61.6485 | 122.9094 | 61.4354 | 61.4984 | 123.0621 | 61.49 | 122.8678 | 61.5346 | 61.5431 | 61.411 | 61.4194
529.0625 | 123.2803 | -61.4914 | 61.615 | 0.025705 | -0.035942 | -0.012 | -0.002124 | 0.027109 | -0.005985 | 0.01969 | 61.5554 | 0.15706 | 61.4409 | -0.051417 | 0.007032 | 61.5753 | -0.010593 | 61.3764 | 61.5171 | 61.4555 | 61.4794 | 61.4893 | 61.5185 | 61.4854 | 61.5111 | 123.0468 | 61.6485 | 122.9323 | 61.44 | 61.4984 | 123.0667 | 61.4808 | 122.8678 | 61.5484 | 61.566 | 61.4339 | 61.4515
530.0625 | 123.2391 | -61.4822 | 61.6287 | 0.034862 | -0.040521 | -0.016578 | -0.002124 | 0.022531 | -0.001406 | 0.024268 | 61.5508 | 0.15706 | 61.4821 | -0.055996 | 0.01161 | 61.5707 | -0.006014 | 61.3764 | 61.5171 | 61.4417 | 61.4657 | 61.4801 | 61.5048 | 61.4808 | 61.5065 | 123.0331 | 61.6393 | 122.9643 | 61.4262 | 61.4938 | 123.053 | 61.4762 | 122.8586 | 61.5392 | 61.5568 | 61.4705 | 61.4881
531.0625 | 123.2162 | -61.5143 | 61.6562 | 0.025705 | -0.040521 | -0.021157 | -0.002124 | 0.027109 | -0.005985 | 0.028846 | 61.5463 | 0.15706 | 61.4684 | -0.051417 | 0.016188 | 61.5662 | -0.006014 | 61.3672 | 61.54 | 61.4738 | 61.4931 | 61.5122 | 61.5414 | 61.5083 | 61.5431 | 123.0605 | 61.6713 | 122.9826 | 61.4629 | 61.5305 | 123.0804 | 61.5083 | 122.8815 | 61.5301 | 61.5523 | 61.4522 | 61.4744
532.0625 | 123.3215 | -61.4822 | 61.6013 | 0.021127 | -0.035942 | -0.012 | -0.006703 | 0.022531 | -0.005985 | 0.01969 | 61.5417 | 0.15706 | 61.4271 | -0.046838 | 0.007032 | 61.5707 | -0.006014 | 61.3764 | 61.5034 | 61.4463 | 61.4702 | 61.4755 | 61.5048 | 61.4763 | 61.5019 | 123.0239 | 61.6393 | 122.9094 | 61.4354 | 61.4893 | 123.053 | 61.4762 | 122.8586 | 61.5346 | 61.5477 | 61.4201 | 61.4332
533.0781 | 123.3353 | -61.4456 | 61.6241 | 0.025705 | -0.040521 | -0.007421 | -0.002124 | 0.027109 | -0.001406 | 0.01969 | 61.5508 | 0.16164 | 61.4317 | -0.055996 | 0.016188 | 61.5707 | -0.001436 | 61.3856 | 61.4713 | 61.4051 | 61.4382 | 61.4435 | 61.4727 | 61.4442 | 61.4653 | 122.9965 | 61.6073 | 122.8773 | 61.3896 | 61.4618 | 123.0164 | 61.4442 | 122.8312 | 61.5346 | 61.5523 | 61.4155 | 61.4332
534.0625 | 123.1979 | -61.5051 | 61.615 | 0.030283 | -0.035942 | -0.007421 | -0.006703 | 0.031687 | -0.001406 | 0.033424 | 61.5554 | 0.1479 | 61.4821 | -0.055996 | 0.01161 | 61.5707 | -0.006014 | 61.3718 | 61.5354 | 61.4692 | 61.4977 | 61.4984 | 61.5368 | 61.5037 | 61.5386 | 123.0605 | 61.653 | 122.9872 | 61.4491 | 61.5167 | 123.0759 | 61.4991 | 122.8769 | 61.5438 | 61.5614 | 61.4705 | 61.4881
535.0625 | 123.2483 | -61.4868 | 61.6333 | 0.030283 | -0.040521 | -0.016578 | -0.006703 | 0.017953 | -0.001406 | 0.01969 | 61.5554 | 0.16164 | 61.4775 | -0.055996 | 0.01161 | 61.5753 | -0.006014 | 61.3672 | 61.5171 | 61.4463 | 61.4702 | 61.4801 | 61.5048 | 61.4854 | 61.5065 | 123.0422 | 61.6485 | 122.9643 | 61.4308 | 61.4984 | 123.0621 | 61.4808 | 122.8541 | 61.5438 | 61.5614 | 61.4659 | 61.4835
536.0625 | 123.2574 | -61.4548 | 61.615 | 0.034862 | -0.031363 | -0.016578 | 0.002454 | 0.022531 | 0.003172 | 0.024268 | 61.5508 | 0.16164 | 61.4363 | -0.055996 | 0.01161 | 61.5707 | 0.003143 | 61.3764 | 61.4896 | 61.4234 | 61.4382 | 61.4572 | 61.4773 | 61.4579 | 61.479 | 123.0056 | 61.6164 | 122.8911 | 61.3988 | 61.4664 | 123.0255 | 61.4579 | 122.8312 | 61.5392 | 61.5477 | 61.4247 | 61.4332
537.0625 | 123.317 | -61.4731 | 61.5829 | 0.025705 | -0.031363 | -0.016578 | -0.011281 | 0.022531 | -0.001406 | 0.024268 | 61.5417 | 0.15248 | 61.4317 | -0.051417 | 0.01161 | 61.5662 | 0.007721 | 61.381 | 61.4988 | 61.4417 | 61.4565 | 61.4618 | 61.4956 | 61.4717 | 61.4974 | 123.0148 | 61.6256 | 122.9048 | 61.4217 | 61.4847 | 123.0392 | 61.4808 | 122.8541 | 61.5301 | 61.534 | 61.4201 | 61.424
538.0625 | 123.2483 | -61.496 | 61.6287 | 0.030283 | -0.040521 | -0.012 | 0.002454 | 0.031687 | -0.001406 | 0.024268 | 61.5554 | 0.15248 | 61.4821 | -0.051417 | 0.007032 | 61.5707 | -0.006014 | 61.3718 | 61.5263 | 61.4555 | 61.484 | 61.4984 | 61.5277 | 61.4946 | 61.5202 | 123.0514 | 61.6485 | 122.9781 | 61.4446 | 61.503 | 123.0667 | 61.49 | 122.8678 | 61.5484 | 61.5614 | 61.4751 | 61.4881
539.0625 | 123.2437 | -61.4731 | 61.6196 | 0.030283 | -0.040521 | -0.016578 | -0.006703 | 0.027109 | -0.005985 | 0.01969 | 61.5554 | 0.15248 | 61.4867 | -0.055996 | 0.020767 | 61.5753 | -0.006014 | 61.3764 | 61.5034 | 61.4326 | 61.4565 | 61.4664 | 61.5002 | 61.4671 | 61.4928 | 123.0285 | 61.6256 | 122.9597 | 61.4171 | 61.4939 | 123.0484 | 61.4671 | 122.8495 | 61.5346 | 61.5614 | 61.4659 | 61.4927
540.0625 | 123.2117 | -61.4914 | 61.6287 | 0.030283 | -0.040521 | -0.012 | 0.002454 | 0.022531 | -0.001406 | 0.028846 | 61.5463 | 0.16164 | 61.4363 | -0.046838 | 0.007032 | 61.5707 | -0.006014 | 61.3718 | 61.5217 | 61.4509 | 61.4794 | 61.4938 | 61.5139 | 61.49 | 61.5202 | 123.0377 | 61.653 | 122.9277 | 61.4446 | 61.4984 | 123.0621 | 61.4854 | 122.8632 | 61.5392 | 61.5523 | 61.4293 | 61.4423
541.0625 | 123.2254 | -61.4594 | 61.6241 | 0.025705 | -0.026784 | -0.016578 | -0.002124 | 0.022531 | -0.001406 | 0.01969 | 61.5463 | 0.15248 | 61.4317 | -0.055996 | 0.016188 | 61.5707 | -0.006014 | 61.3718 | 61.4851 | 61.4326 | 61.4428 | 61.4572 | 61.4819 | 61.4579 | 61.479 | 123.0056 | 61.6118 | 122.8911 | 61.4034 | 61.4755 | 123.0301 | 61.4533 | 122.8312 | 61.5301 | 61.5523 | 61.4155 | 61.4377
542.0625 | 123.3902 | -61.4502 | 61.5967 | 0.034862 | -0.035942 | -0.021157 | -0.011281 | 0.022531 | -0.005985 | 0.028846 | 61.5463 | 0.15248 | 61.4455 | -0.055996 | 0.01161 | 61.5707 | -0.001436 | 61.3672 | 61.4851 | 61.4143 | 61.429 | 61.4389 | 61.4727 | 61.4442 | 61.479 | 122.9965 | 61.6027 | 122.8957 | 61.3942 | 61.4618 | 123.0209 | 61.4488 | 122.8174 | 61.5346 | 61.5477 | 61.4339 | 61.4469
543.0625 | 123.2574 | -61.4731 | 61.6196 | 0.025705 | -0.035942 | -0.007421 | -0.011281 | 0.022531 | -0.001406 | 0.024268 | 61.56 | 0.15248 | 61.4684 | -0.051417 | 0.01161 | 61.5662 | -0.001436 | 61.3764 | 61.4988 | 61.4371 | 61.4657 | 61.4618 | 61.4956 | 61.4717 | 61.4974 | 123.0331 | 61.6256 | 122.9414 | 61.4217 | 61.4847 | 123.0392 | 61.4716 | 122.8495 | 61.5484 | 61.5614 | 61.4567 | 61.4698
544.0625 | 123.2941 | -61.4777 | 61.6196 | 0.030283 | -0.031363 | -0.016578 | -0.002124 | 0.027109 | -0.001406 | 0.024268 | 61.5554 | 0.15248 | 61.4546 | -0.055996 | 0.016188 | 61.5799 | -0.001436 | 61.3718 | 61.5079 | 61.4463 | 61.4611 | 61.4755 | 61.5048 | 61.4763 | 61.5019 | 123.0331 | 61.6301 | 122.9323 | 61.4217 | 61.4938 | 123.0576 | 61.4762 | 122.8495 | 61.5392 | 61.5568 | 61.4384 | 61.4561
545.0625 | 123.2712 | -61.4731 | 61.6379 | 0.025705 | -0.031363 | -0.016578 | -0.006703 | 0.027109 | -0.001406 | 0.01969 | 61.5463 | 0.16164 | 61.4363 | -0.065154 | 0.01161 | 61.557 | -0.006014 | 61.3718 | 61.4988 | 61.4417 | 61.4565 | 61.4664 | 61.5002 | 61.4717 | 61.4928 | 123.0193 | 61.6347 | 122.9094 | 61.4079 | 61.4847 | 123.0301 | 61.4671 | 122.8449 | 61.5346 | 61.5523 | 61.4247 | 61.4423
546.0625 | 123.3124 | -61.4914 | 61.647 | 0.025705 | -0.031363 | -0.012 | -0.006703 | 0.022531 | -0.001406 | 0.024268 | 61.5508 | 0.15706 | 61.45 | -0.051417 | 0.020767 | 61.5707 | -0.001436 | 61.3718 | 61.5171 | 61.46 | 61.4794 | 61.4847 | 61.5139 | 61.49 | 61.5157 | 123.0422 | 61.6485 | 122.9414 | 61.44 | 61.5122 | 123.0621 | 61.49 | 122.8632 | 61.5301 | 61.5523 | 61.4293 | 61.4515
547.0625 | 123.3398 | -61.5005 | 61.6013 | 0.021127 | -0.040521 | -0.012 | -0.002124 | 0.022531 | 0.003172 | 0.01969 | 61.5554 | 0.15706 | 61.4775 | -0.055996 | 0.016188 | 61.5707 | -0.001436 | 61.3718 | 61.5217 | 61.46 | 61.4885 | 61.4984 | 61.5231 | 61.5037 | 61.5202 | 123.056 | 61.6576 | 122.9781 | 61.4446 | 61.5167 | 123.0713 | 61.4991 | 122.8724 | 61.5392 | 61.5568 | 61.4613 | 61.4789
548.0625 | 123.317 | -61.4502 | 61.6379 | 0.030283 | -0.035942 | -0.012 | 0.002454 | 0.031687 | -0.001406 | 0.024268 | 61.5554 | 0.15706 | 61.4638 | -0.055996 | 0.01161 | 61.5707 | -0.001436 | 61.3764 | 61.4805 | 61.4143 | 61.4382 | 61.4526 | 61.4819 | 61.4488 | 61.4745 | 123.0056 | 61.6073 | 122.914 | 61.3942 | 61.4618 | 123.0209 | 61.4488 | 122.8266 | 61.5438 | 61.5568 | 61.4522 | 61.4652
549.0625 | 123.2391 | -61.4822 | 61.6196 | 0.025705 | -0.040521 | -0.016578 | -0.002124 | 0.027109 | 0.003172 | 0.024268 | 61.5554 | 0.16164 | 61.4363 | -0.060575 | 0.016188 | 61.5707 | -0.006014 | 61.381 | 61.5079 | 61.4417 | 61.4657 | 61.4801 | 61.5093 | 61.4854 | 61.5065 | 123.0377 | 61.6439 | 122.9185 | 61.4217 | 61.4984 | 123.053 | 61.4762 | 122.8632 | 61.5392 | 61.5614 | 61.4201 | 61.4423
550.0625 | 123.2849 | -61.4685 | 61.6333 | 0.034862 | -0.031363 | -0.016578 | -0.002124 | 0.027109 | -0.005985 | 0.024268 | 61.5508 | 0.16164 | 61.4455 | -0.051417 | 0.01161 | 61.5707 | -0.010593 | 61.3856 | 61.5034 | 61.4371 | 61.4519 | 61.4664 | 61.4956 | 61.4625 | 61.4928 | 123.0193 | 61.6301 | 122.914 | 61.4171 | 61.4801 | 123.0392 | 61.4579 | 122.8541 | 61.5392 | 61.5614 | 61.4339 | 61.4561
551.0625 | 123.3536 | -61.4639 | 61.6058 | 0.034862 | -0.026784 | -0.016578 | 0.002454 | 0.027109 | -0.001406 | 0.024268 | 61.5554 | 0.16164 | 61.4912 | -0.042259 | 0.01161 | 61.5753 | 0.003143 | 61.3764 | 61.4988 | 61.4371 | 61.4474 | 61.4664 | 61.491 | 61.4625 | 61.4882 | 123.0193 | 61.6256 | 122.9552 | 61.4217 | 61.4755 | 123.0392 | 61.4671 | 122.8403 | 61.5438 | 61.5523 | 61.4796 | 61.4881
552.0625 | 123.2803 | -61.5005 | 61.6241 | 0.030283 | -0.035942 | -0.016578 | -0.006703 | 0.022531 | -0.001406 | 0.024268 | 61.5463 | 0.15706 | 61.4912 | -0.055996 | 0.016188 | 61.5662 | -0.001436 | 61.3764 | 61.5308 | 61.4646 | 61.484 | 61.4938 | 61.5231 | 61.4991 | 61.5248 | 123.0468 | 61.6576 | 122.9918 | 61.4446 | 61.5167 | 123.0667 | 61.4991 | 122.8769 | 61.5301 | 61.5477 | 61.4751 | 61.4927
553.0625 | 123.3078 | -61.4685 | 61.615 | 0.025705 | -0.0451 | -0.012 | -0.002124 | 0.022531 | -0.001406 | 0.028846 | 61.5463 | 0.15706 | 61.4409 | -0.051417 | 0.01161 | 61.5707 | -0.001436 | 61.3764 | 61.4942 | 61.4234 | 61.4565 | 61.4664 | 61.491 | 61.4671 | 61.4974 | 123.0148 | 61.6256 | 122.9094 | 61.4171 | 61.4801 | 123.0392 | 61.4671 | 122.8449 | 61.5346 | 61.5477 | 61.4293 | 61.4423
554.0625 | 123.2666 | -61.4822 | 61.6379 | 0.025705 | -0.035942 | -0.012 | -0.002124 | 0.017953 | -0.001406 | 0.033424 | 61.5554 | 0.16164 | 61.4317 | -0.055996 | 0.020767 | 61.5707 | 0.003143 | 61.3901 | 61.5079 | 61.4463 | 61.4702 | 61.4801 | 61.5002 | 61.4808 | 61.5157 | 123.0377 | 61.6439 | 122.914 | 61.4262 | 61.503 | 123.053 | 61.4854 | 122.8724 | 61.5346 | 61.5523 | 61.411 | 61.4286
555.0625 | 123.2986 | -61.4914 | 61.6287 | 0.030283 | -0.040521 | -0.016578 | -0.002124 | 0.022531 | 0.003172 | 0.028846 | 61.5554 | 0.16622 | 61.4821 | -0.051417 | 0.016188 | 61.5707 | 0.003143 | 61.381 | 61.5217 | 61.4509 | 61.4748 | 61.4893 | 61.5139 | 61.4946 | 61.5202 | 123.0468 | 61.6576 | 122.9735 | 61.44 | 61.5076 | 123.0621 | 61.4945 | 122.8724 | 61.5392 | 61.5523 | 61.4659 | 61.4789
556.0625 | 123.2574 | -61.4685 | 61.6333 | 0.025705 | -0.031363 | -0.016578 | -0.011281 | 0.031687 | -0.001406 | 0.01969 | 61.5554 | 0.15248 | 61.4958 | -0.051417 | 0.016188 | 61.5707 | -0.001436 | 61.3856 | 61.4942 | 61.4371 | 61.4519 | 61.4572 | 61.5002 | 61.4671 | 61.4882 | 123.0239 | 61.621 | 122.9643 | 61.4171 | 61.4847 | 123.0392 | 61.4671 | 122.8541 | 61.5392 | 61.5568 | 61.4796 | 61.4973
557.0625 | 123.2529 | -61.4822 | 61.6058 | 0.025705 | -0.040521 | -0.012 | -0.002124 | 0.022531 | -0.005985 | 0.01969 | 61.5463 | 0.15706 | 61.4409 | -0.051417 | 0.016188 | 61.5753 | 0.003143 | 61.3764 | 61.5079 | 61.4417 | 61.4702 | 61.4801 | 61.5048 | 61.4763 | 61.5019 | 123.0285 | 61.6393 | 122.9231 | 61.4308 | 61.4984 | 123.0576 | 61.4854 | 122.8586 | 61.5301 | 61.5431 | 61.4247 | 61.4377
558.0625 | 123.3124 | -61.4731 | 61.6562 | 0.030283 | -0.0451 | -0.016578 | -0.002124 | 0.027109 | -0.005985 | 0.024268 | 61.5554 | 0.15706 | 61.4409 | -0.055996 | 0.016188 | 61.5707 | -0.006014 | 61.3901 | 61.5034 | 61.428 | 61.4565 | 61.471 | 61.5002 | 61.4671 | 61.4974 | 123.0285 | 61.6301 | 122.914 | 61.4171 | 61.4893 | 123.0438 | 61.4671 | 122.8632 | 61.5392 | 61.5614 | 61.4247 | 61.4469
559.0625 | 123.2803 | -61.4685 | 61.6287 | 0.025705 | -0.040521 | -0.012 | -0.006703 | 0.027109 | -0.001406 | 0.028846 | 61.56 | 0.16164 | 61.45 | -0.055996 | 0.01161 | 61.5753 | -0.006014 | 61.3856 | 61.4942 | 61.428 | 61.4565 | 61.4618 | 61.4956 | 61.4671 | 61.4974 | 123.0285 | 61.6301 | 122.9185 | 61.4125 | 61.4801 | 123.0438 | 61.4625 | 122.8541 | 61.5484 | 61.566 | 61.4384 | 61.4561
560.0625 | 123.2941 | -61.4868 | 61.6379 | 0.021127 | -0.0451 | -0.012 | 0.002454 | 0.027109 | 0.00775 | 0.028846 | 61.5554 | 0.15706 | 61.4912 | -0.046838 | 0.016188 | 61.5662 | -0.001436 | 61.381 | 61.5079 | 61.4417 | 61.4748 | 61.4893 | 61.5139 | 61.4946 | 61.5157 | 123.0422 | 61.6439 | 122.9781 | 61.44 | 61.503 | 123.053 | 61.4854 | 122.8678 | 61.5392 | 61.5568 | 61.4751 | 61.4927
561.0625 | 123.2803 | -61.4868 | 61.6287 | 0.025705 | -0.035942 | -0.012 | -0.011281 | 0.027109 | 0.00775 | 0.028846 | 61.5417 | 0.15248 | 61.4546 | -0.051417 | 0.020767 | 61.5707 | -0.010593 | 61.3856 | 61.5125 | 61.4509 | 61.4748 | 61.4755 | 61.5139 | 61.4946 | 61.5157 | 123.0285 | 61.6393 | 122.9414 | 61.4354 | 61.5076 | 123.0576 | 61.4762 | 122.8724 | 61.5209 | 61.5523 | 61.4339 | 61.4652
562.0625 | 123.2529 | -61.4822 | 61.6287 | 0.025705 | -0.040521 | -0.016578 | 0.002454 | 0.022531 | -0.001406 | 0.024268 | 61.5463 | 0.15248 | 61.4226 | -0.046838 | 0.007032 | 61.5707 | 0.007721 | 61.3856 | 61.5079 | 61.4417 | 61.4657 | 61.4847 | 61.5048 | 61.4808 | 61.5065 | 123.0285 | 61.6347 | 122.9048 | 61.4354 | 61.4893 | 123.053 | 61.49 | 122.8678 | 61.5392 | 61.5385 | 61.4155 | 61.4149
563.0625 | 123.2574 | -61.4639 | 61.6333 | 0.030283 | -0.0451 | -0.012 | 0.002454 | 0.022531 | -0.005985 | 0.024268 | 61.5554 | 0.15248 | 61.4363 | -0.055996 | 0.016188 | 61.5616 | -0.001436 | 61.3856 | 61.4942 | 61.4188 | 61.4519 | 61.4664 | 61.4865 | 61.4579 | 61.4882 | 123.0193 | 61.6164 | 122.9002 | 61.4079 | 61.4801 | 123.0255 | 61.4625 | 122.8495 | 61.5392 | 61.5568 | 61.4201 | 61.4377
564.0625 | 123.23 | -61.4777 | 61.6608 | 0.030283 | -0.040521 | -0.016578 | -0.002124 | 0.022531 | 0.003172 | 0.028846 | 61.5463 | 0.1479 | 61.4821 | -0.051417 | 0.007032 | 61.5753 | -0.001436 | 61.381 | 61.5079 | 61.4371 | 61.4611 | 61.4755 | 61.5002 | 61.4808 | 61.5065 | 123.0239 | 61.6256 | 122.9597 | 61.4262 | 61.4847 | 123.053 | 61.4762 | 122.8586 | 61.5392 | 61.5477 | 61.4751 | 61.4835
565.0625 | 123.2758 | -61.496 | 61.6516 | 0.030283 | -0.035942 | -0.021157 | -0.006703 | 0.022531 | -0.005985 | 0.024268 | 61.56 | 0.15706 | 61.4638 | -0.051417 | 0.016188 | 61.5707 | -0.001436 | 61.3718 | 61.5263 | 61.46 | 61.4748 | 61.4893 | 61.5185 | 61.49 | 61.5202 | 123.056 | 61.653 | 122.9597 | 61.4446 | 61.5122 | 123.0667 | 61.4945 | 122.8678 | 61.5438 | 61.5614 | 61.4476 | 61.4652
566.0625 | 123.2437 | -61.4685 | 61.6562 | 0.030283 | -0.035942 | -0.021157 | -0.002124 | 0.022531 | -0.001406 | 0.024268 | 61.5508 | 0.15706 | 61.4363 | -0.051417 | 0.016188 | 61.5753 | -0.001436 | 61.3947 | 61.4988 | 61.4326 | 61.4473 | 61.4664 | 61.491 | 61.4671 | 61.4928 | 123.0193 | 61.6256 | 122.9048 | 61.4171 | 61.4847 | 123.0438 | 61.4671 | 122.8632 | 61.5346 | 61.5523 | 61.4201 | 61.4377
567.0625 | 123.3444 | -61.528 | 61.6699 | 0.030283 | -0.040521 | -0.021157 | 0.002454 | 0.027109 | -0.001406 | 0.024268 | 61.5463 | 0.15706 | 61.4317 | -0.046838 | 0.01161 | 61.5662 | -0.006014 | 61.381 | 61.5583 | 61.4875 | 61.5069 | 61.5305 | 61.5551 | 61.5266 | 61.5523 | 123.0743 | 61.6851 | 122.9597 | 61.4812 | 61.5396 | 123.0942 | 61.522 | 122.909 | 61.5346 | 61.5523 | 61.4201 | 61.4377
568.0625 | 123.2758 | -61.4639 | 61.6562 | 0.030283 | -0.0451 | -0.007421 | -0.002124 | 0.022531 | -0.005985 | 0.01969 | 61.5554 | 0.1479 | 61.4958 | -0.051417 | 0.016188 | 61.5707 | 0.003143 | 61.3856 | 61.4942 | 61.4188 | 61.4565 | 61.4618 | 61.4865 | 61.4579 | 61.4836 | 123.0193 | 61.6118 | 122.9598 | 61.4125 | 61.4801 | 123.0347 | 61.4671 | 122.8495 | 61.5392 | 61.5523 | 61.4796 | 61.4927
569.0625 | 123.2941 | -61.4731 | 61.6745 | 0.030283 | -0.040521 | -0.021157 | -0.006703 | 0.017953 | 0.003172 | 0.024268 | 61.5463 | 0.16164 | 61.4638 | -0.051417 | 0.01161 | 61.5662 | 0.003143 | 61.381 | 61.5034 | 61.4326 | 61.4519 | 61.4664 | 61.491 | 61.4763 | 61.4974 | 123.0193 | 61.6347 | 122.9369 | 61.4217 | 61.4847 | 123.0392 | 61.4762 | 122.8541 | 61.5346 | 61.5431 | 61.4522 | 61.4606
570.0625 | 123.2574 | -61.4731 | 61.6882 | 0.030283 | -0.035942 | -0.016578 | -0.006703 | 0.027109 | -0.001406 | 0.010533 | 61.5463 | 0.15706 | 61.4363 | -0.051417 | 0.020767 | 61.5662 | -0.001436 | 61.3901 | 61.5034 | 61.4371 | 61.4565 | 61.4664 | 61.5002 | 61.4717 | 61.4836 | 123.0193 | 61.6301 | 122.9094 | 61.4217 | 61.4939 | 123.0392 | 61.4716 | 122.8632 | 61.5255 | 61.5477 | 61.4155 | 61.4377
571.0625 | 123.262 | -61.4868 | 61.6562 | 0.030283 | -0.040521 | -0.012 | -0.006703 | 0.022531 | -0.001406 | 0.028846 | 61.56 | 0.15248 | 61.4867 | -0.051417 | 0.016188 | 61.5662 | -0.001436 | 61.3718 | 61.5171 | 61.4463 | 61.4748 | 61.4801 | 61.5093 | 61.4854 | 61.5157 | 123.0468 | 61.6393 | 122.9735 | 61.4354 | 61.503 | 123.053 | 61.4854 | 122.8586 | 61.5438 | 61.5614 | 61.4705 | 61.4881
572.0625 | 123.2758 | -61.4639 | 61.6425 | 0.030283 | -0.040521 | -0.016578 | 0.007033 | 0.022531 | -0.005985 | 0.024268 | 61.5463 | 0.15706 | 61.45 | -0.046838 | 0.016188 | 61.5707 | -0.001436 | 61.3856 | 61.4942 | 61.4234 | 61.4474 | 61.471 | 61.4865 | 61.4579 | 61.4882 | 123.0102 | 61.621 | 122.914 | 61.4171 | 61.4801 | 123.0347 | 61.4625 | 122.8495 | 61.5301 | 61.5477 | 61.4339 | 61.4515
573.0625 | 123.1842 | -61.4868 | 61.6791 | 0.025705 | -0.0451 | -0.012 | -0.006703 | 0.022531 | -0.005985 | 0.01969 | 61.5554 | 0.16164 | 61.4363 | -0.055996 | 0.016188 | 61.5707 | -0.001436 | 61.3901 | 61.5125 | 61.4417 | 61.4748 | 61.4801 | 61.5093 | 61.4808 | 61.5065 | 123.0422 | 61.6485 | 122.9231 | 61.4308 | 61.503 | 123.0576 | 61.4854 | 122.8769 | 61.5392 | 61.5568 | 61.4201 | 61.4377
574.0625 | 123.2574 | -61.5005 | 61.6791 | 0.030283 | -0.031363 | -0.016578 | -0.002124 | 0.031687 | 0.003172 | 0.024268 | 61.5646 | 0.15706 | 61.4821 | -0.051417 | 0.01161 | 61.5662 | -0.006014 | 61.3764 | 61.5308 | 61.4692 | 61.484 | 61.4984 | 61.5322 | 61.5037 | 61.5248 | 123.0651 | 61.6576 | 122.9826 | 61.4491 | 61.5122 | 123.0667 | 61.4945 | 122.8769 | 61.553 | 61.5706 | 61.4705 | 61.4881
575.0625 | 123.2208 | -61.4914 | 61.6745 | 0.034862 | -0.0451 | -0.016578 | -0.002124 | 0.027109 | 0.003172 | 0.024268 | 61.5508 | 0.15706 | 61.4455 | -0.055996 | 0.020767 | 61.5707 | 0.003143 | 61.3764 | 61.5263 | 61.4463 | 61.4748 | 61.4893 | 61.5185 | 61.4946 | 61.5157 | 123.0422 | 61.6485 | 122.9369 | 61.4354 | 61.5122 | 123.0621 | 61.4945 | 122.8678 | 61.5301 | 61.5477 | 61.4247 | 61.4423
576.0625 | 123.317 | -61.4273 | 61.702 | 0.025705 | -0.040521 | -0.012 | 0.002454 | 0.022531 | 0.003172 | 0.024268 | 61.5554 | 0.15706 | 61.4317 | -0.051417 | 0.020767 | 61.5662 | -0.001436 | 61.3764 | 61.453 | 61.3868 | 61.4153 | 61.4298 | 61.4498 | 61.4305 | 61.4516 | 122.9827 | 61.5844 | 122.859 | 61.3759 | 61.4481 | 122.9935 | 61.4259 | 122.8037 | 61.5346 | 61.5568 | 61.411 | 61.4332
577.0625 | 123.349 | -61.4777 | 61.6013 | 0.025705 | -0.035942 | -0.012 | -0.006703 | 0.027109 | -0.001406 | 0.01969 | 61.5646 | 0.16164 | 61.4684 | -0.055996 | 0.01161 | 61.5753 | -0.010593 | 61.3718 | 61.5034 | 61.4417 | 61.4657 | 61.471 | 61.5048 | 61.4763 | 61.4974 | 123.0422 | 61.6393 | 122.946 | 61.4217 | 61.4893 | 123.053 | 61.4671 | 122.8495 | 61.553 | 61.5752 | 61.4567 | 61.4789
578.0625 | 123.3536 | -61.4548 | 61.5967 | 0.021127 | -0.035942 | -0.016578 | 0.002454 | 0.017953 | -0.001406 | 0.015112 | 61.5463 | 0.15706 | 61.4409 | -0.051417 | 0.016188 | 61.5707 | 0.003143 | 61.381 | 61.4759 | 61.4188 | 61.4382 | 61.4572 | 61.4727 | 61.4534 | 61.4699 | 123.001 | 61.6118 | 122.8957 | 61.4034 | 61.471 | 123.0255 | 61.4579 | 122.8357 | 61.5301 | 61.5431 | 61.4247 | 61.4377
579.0625 | 123.3627 | -61.4456 | 61.6104 | 0.030283 | -0.040521 | -0.007421 | -0.006703 | 0.013375 | -0.005985 | 0.01969 | 61.5463 | 0.16622 | 61.45 | -0.051417 | 0.016188 | 61.5707 | -0.001436 | 61.381 | 61.4759 | 61.4051 | 61.4382 | 61.4389 | 61.459 | 61.4396 | 61.4653 | 122.9919 | 61.6118 | 122.8957 | 61.3942 | 61.4618 | 123.0164 | 61.4442 | 122.8266 | 61.5301 | 61.5477 | 61.4339 | 61.4515
580.0625 | 123.2666 | -61.4777 | 61.6653 | 0.030283 | -0.040521 | -0.021157 | 0.002454 | 0.022531 | 0.003172 | 0.024268 | 61.56 | 0.15248 | 61.4729 | -0.046838 | 0.01161 | 61.5753 | 0.003143 | 61.3718 | 61.5079 | 61.4371 | 61.4565 | 61.4801 | 61.5002 | 61.4808 | 61.5019 | 123.0377 | 61.6301 | 122.9506 | 61.4308 | 61.4893 | 123.053 | 61.4808 | 122.8495 | 61.5484 | 61.5568 | 61.4613 | 61.4698
581.0625 | 123.262 | -61.4914 | 61.6562 | 0.030283 | -0.040521 | -0.016578 | -0.002124 | 0.022531 | -0.005985 | 0.024268 | 61.5554 | 0.15706 | 61.4455 | -0.055996 | 0.016188 | 61.5662 | -0.006014 | 61.381 | 61.5217 | 61.4509 | 61.4748 | 61.4893 | 61.5139 | 61.4854 | 61.5157 | 123.0468 | 61.6485 | 122.9369 | 61.4354 | 61.5076 | 123.0576 | 61.4854 | 122.8724 | 61.5392 | 61.5614 | 61.4293 | 61.4515
582.0625 | 123.2483 | -61.4548 | 61.6241 | 0.030283 | -0.031363 | -0.007421 | 0.002454 | 0.017953 | -0.001406 | 0.01969 | 61.5554 | 0.15706 | 61.4317 | -0.060575 | 0.01161 | 61.5753 | 0.003143 | 61.381 | 61.4851 | 61.4234 | 61.4474 | 61.4572 | 61.4727 | 61.4534 | 61.4745 | 123.0102 | 61.6118 | 122.8865 | 61.3942 | 61.4664 | 123.0301 | 61.4579 | 122.8357 | 61.5438 | 61.5523 | 61.4201 | 61.4286
583.0625 | 123.2712 | -61.4731 | 61.6516 | 0.034862 | -0.035942 | -0.012 | -0.011281 | 0.022531 | -0.001406 | 0.024268 | 61.5554 | 0.15706 | 61.4409 | -0.042259 | 0.01161 | 61.5662 | -0.001436 | 61.3718 | 61.5079 | 61.4371 | 61.4611 | 61.4618 | 61.4956 | 61.4717 | 61.4974 | 123.0285 | 61.6301 | 122.914 | 61.4308 | 61.4847 | 123.0392 | 61.4716 | 122.8449 | 61.5438 | 61.5568 | 61.4293 | 61.4423
584.0625 | 123.2574 | -61.4685 | 61.6608 | 0.021127 | -0.040521 | -0.012 | -0.002124 | 0.027109 | 0.003172 | 0.024268 | 61.56 | 0.16164 | 61.4912 | -0.046838 | 0.01161 | 61.5662 | 0.003143 | 61.3764 | 61.4896 | 61.428 | 61.4565 | 61.4664 | 61.4956 | 61.4717 | 61.4928 | 123.0285 | 61.6301 | 122.9598 | 61.4217 | 61.4801 | 123.0347 | 61.4716 | 122.8449 | 61.5484 | 61.5568 | 61.4796 | 61.4881
585.0625 | 123.3719 | -61.4456 | 61.6058 | 0.030283 | -0.040521 | -0.012 | -0.002124 | 0.022531 | -0.001406 | 0.024268 | 61.5554 | 0.15706 | 61.4546 | -0.051417 | 0.020767 | 61.5753 | 0.003143 | 61.3856 | 61.4759 | 61.4051 | 61.4336 | 61.4435 | 61.4681 | 61.4442 | 61.4699 | 123.001 | 61.6027 | 122.9002 | 61.3942 | 61.4664 | 123.0209 | 61.4488 | 122.8312 | 61.5346 | 61.5523 | 61.4339 | 61.4515
586.0625 | 123.3032 | -61.441 | 61.6516 | 0.025705 | -0.031363 | -0.007421 | -0.006703 | 0.022531 | -0.010563 | 0.01969 | 61.5463 | 0.15706 | 61.4271 | -0.051417 | 0.016188 | 61.5707 | 0.003143 | 61.381 | 61.4667 | 61.4097 | 61.4336 | 61.4343 | 61.4636 | 61.4305 | 61.4607 | 122.9873 | 61.5981 | 122.8682 | 61.3896 | 61.4572 | 123.0118 | 61.4442 | 122.822 | 61.5301 | 61.5431 | 61.411 | 61.424
587.0625 | 123.2437 | -61.4777 | 61.6333 | 0.030283 | -0.035942 | -0.012 | -0.002124 | 0.027109 | -0.001406 | 0.01969 | 61.56 | 0.15248 | 61.4409 | -0.051417 | 0.01161 | 61.5707 | -0.001436 | 61.3764 | 61.5079 | 61.4417 | 61.4657 | 61.4755 | 61.5048 | 61.4763 | 61.4974 | 123.0377 | 61.6301 | 122.9185 | 61.4262 | 61.4893 | 123.0484 | 61.4762 | 122.8541 | 61.5484 | 61.5614 | 61.4293 | 61.4423
588.0625 | 123.2483 | -61.4822 | 61.6653 | 0.034862 | -0.035942 | -0.016578 | -0.002124 | 0.027109 | 0.003172 | 0.01969 | 61.56 | 0.15706 | 61.4958 | -0.046838 | 0.016188 | 61.5616 | 0.003143 | 61.3718 | 61.5171 | 61.4463 | 61.4657 | 61.4801 | 61.5093 | 61.4854 | 61.5019 | 123.0422 | 61.6393 | 122.9781 | 61.4354 | 61.4984 | 123.0438 | 61.4854 | 122.8541 | 61.5438 | 61.5568 | 61.4796 | 61.4927
589.0625 | 123.2849 | -61.4639 | 61.6516 | 0.030283 | -0.035942 | -0.016578 | -0.006703 | 0.022531 | -0.005985 | 0.015112 | 61.5508 | 0.16164 | 61.45 | -0.055996 | 0.020767 | 61.5753 | 0.003143 | 61.381 | 61.4942 | 61.428 | 61.4474 | 61.4572 | 61.4865 | 61.4579 | 61.479 | 123.0148 | 61.6256 | 122.914 | 61.4079 | 61.4847 | 123.0392 | 61.4671 | 122.8449 | 61.5301 | 61.5477 | 61.4293 | 61.4469
590.0625 | 123.2712 | -61.4868 | 61.6425 | 0.034862 | -0.040521 | -0.016578 | 0.002454 | 0.022531 | -0.001406 | 0.015112 | 61.5508 | 0.16164 | 61.4317 | -0.055996 | 0.01161 | 61.5662 | -0.001436 | 61.3856 | 61.5217 | 61.4463 | 61.4702 | 61.4893 | 61.5093 | 61.4854 | 61.5019 | 123.0377 | 61.6485 | 122.9185 | 61.4308 | 61.4984 | 123.053 | 61.4854 | 122.8724 | 61.5392 | 61.5523 | 61.4201 | 61.4332
591.0625 | 123.2437 | -61.4822 | 61.6516 | 0.034862 | -0.035942 | -0.021157 | -0.006703 | 0.027109 | -0.005985 | 0.01969 | 61.5463 | 0.16164 | 61.4363 | -0.046838 | 0.016188 | 61.5753 | 0.003143 | 61.3718 | 61.5171 | 61.4463 | 61.4611 | 61.4755 | 61.5093 | 61.4763 | 61.5019 | 123.0285 | 61.6439 | 122.9185 | 61.4354 | 61.4984 | 123.0576 | 61.4854 | 122.8541 | 61.5301 | 61.5431 | 61.4201 | 61.4332
592.0625 | 123.2895 | -61.4639 | 61.6379 | 0.030283 | -0.035942 | -0.007421 | -0.002124 | 0.031687 | -0.001406 | 0.024268 | 61.5554 | 0.15706 | 61.4775 | -0.055996 | 0.01161 | 61.5616 | -0.001436 | 61.3718 | 61.4942 | 61.428 | 61.4565 | 61.4618 | 61.4956 | 61.4625 | 61.4882 | 123.0193 | 61.621 | 122.9414 | 61.4079 | 61.4755 | 123.0255 | 61.4625 | 122.8357 | 61.5438 | 61.5568 | 61.4659 | 61.4789
593.0625 | 123.2483 | -61.4731 | 61.6516 | 0.025705 | -0.035942 | -0.012 | -0.011281 | 0.027109 | -0.005985 | 0.024268 | 61.5646 | 0.16622 | 61.4729 | -0.055996 | 0.020767 | 61.5616 | -0.006014 | 61.3718 | 61.4988 | 61.4371 | 61.4611 | 61.4618 | 61.5002 | 61.4671 | 61.4974 | 123.0377 | 61.6393 | 122.946 | 61.4171 | 61.4939 | 123.0347 | 61.4671 | 122.8449 | 61.5438 | 61.5706 | 61.4522 | 61.4789
594.0625 | 123.3032 | -61.4914 | 61.647 | 0.025705 | -0.040521 | -0.012 | -0.006703 | 0.017953 | -0.005985 | 0.024268 | 61.5508 | 0.16164 | 61.4271 | -0.055996 | 0.01161 | 61.5662 | -0.001436 | 61.3764 | 61.5171 | 61.4509 | 61.4794 | 61.4847 | 61.5093 | 61.4854 | 61.5157 | 123.0422 | 61.653 | 122.9185 | 61.4354 | 61.503 | 123.0576 | 61.49 | 122.8678 | 61.5392 | 61.5523 | 61.4155 | 61.4286
595.0625 | 123.2483 | -61.4914 | 61.6699 | 0.030283 | -0.035942 | -0.007421 | -0.011281 | 0.022531 | -0.005985 | 0.01969 | 61.56 | 0.16164 | 61.4363 | -0.051417 | 0.01161 | 61.5753 | 0.003143 | 61.3764 | 61.5217 | 61.4555 | 61.484 | 61.4801 | 61.5139 | 61.4854 | 61.5111 | 123.0514 | 61.653 | 122.9277 | 61.44 | 61.503 | 123.0667 | 61.4945 | 122.8678 | 61.5484 | 61.5568 | 61.4247 | 61.4332
596.0625 | 123.262 | -61.4731 | 61.6516 | 0.034862 | -0.031363 | -0.007421 | -0.006703 | 0.022531 | -0.001406 | 0.028846 | 61.5554 | 0.15706 | 61.4867 | -0.051417 | 0.020767 | 61.5662 | -0.001436 | 61.3672 | 61.5079 | 61.4417 | 61.4657 | 61.4664 | 61.4956 | 61.4717 | 61.5019 | 123.0285 | 61.6301 | 122.9597 | 61.4217 | 61.4939 | 123.0392 | 61.4716 | 122.8403 | 61.5346 | 61.5568 | 61.4659 | 61.4881
597.0625 | 123.2437 | -61.4777 | 61.6333 | 0.030283 | -0.040521 | -0.016578 | -0.002124 | 0.027109 | -0.005985 | 0.028846 | 61.5463 | 0.15706 | 61.4271 | -0.055996 | 0.016188 | 61.5662 | -0.001436 | 61.3764 | 61.5079 | 61.4371 | 61.4611 | 61.4755 | 61.5048 | 61.4717 | 61.5065 | 123.0239 | 61.6347 | 122.9048 | 61.4217 | 61.4938 | 123.0438 | 61.4762 | 122.8541 | 61.5301 | 61.5477 | 61.411 | 61.4286
598.0625 | 123.2346 | -61.5005 | 61.6562 | 0.025705 | -0.035942 | -0.012 | 0.002454 | 0.022531 | -0.001406 | 0.01969 | 61.5463 | 0.16164 | 61.4363 | -0.051417 | 0.020767 | 61.5707 | 0.003143 | 61.3718 | 61.5263 | 61.4646 | 61.4885 | 61.503 | 61.5231 | 61.4991 | 61.5202 | 123.0468 | 61.6622 | 122.9369 | 61.4491 | 61.5213 | 123.0713 | 61.5037 | 122.8724 | 61.5255 | 61.5431 | 61.4155 | 61.4332
599.0625 | 123.3353 | -61.4822 | 61.6333 | 0.025705 | -0.031363 | -0.016578 | -0.006703 | 0.027109 | -0.005985 | 0.024268 | 61.5554 | 0.15706 | 61.5004 | -0.051417 | 0.016188 | 61.5707 | -0.001436 | 61.3764 | 61.5079 | 61.4509 | 61.4657 | 61.4755 | 61.5093 | 61.4763 | 61.5065 | 123.0377 | 61.6393 | 122.9826 | 61.4308 | 61.4984 | 123.053 | 61.4808 | 122.8586 | 61.5392 | 61.5568 | 61.4842 | 61.5018
600.0625 | 123.23 | -61.4731 | 61.6425 | 0.030283 | -0.040521 | -0.012 | -0.006703 | 0.022531 | -0.001406 | 0.015112 | 61.5417 | 0.15248 | 61.4409 | -0.055996 | 0.020767 | 61.5799 | -0.006014 | 61.381 | 61.5034 | 61.4326 | 61.4611 | 61.4664 | 61.4956 | 61.4717 | 61.4882 | 123.0148 | 61.6256 | 122.914 | 61.4171 | 61.4939 | 123.053 | 61.4671 | 122.8541 | 61.5209 | 61.5477 | 61.4201 | 61.4469
601.0625 | 123.2895 | -61.4777 | 61.6516 | 0.034862 | -0.035942 | -0.007421 | -0.002124 | 0.022531 | -0.005985 | 0.01969 | 61.56 | 0.15706 | 61.4684 | -0.055996 | 0.016188 | 61.5662 | -0.006014 | 61.3764 | 61.5125 | 61.4417 | 61.4702 | 61.4755 | 61.5002 | 61.4717 | 61.4974 | 123.0377 | 61.6347 | 122.946 | 61.4217 | 61.4938 | 123.0438 | 61.4716 | 122.8541 | 61.5438 | 61.566 | 61.4522 | 61.4744
602.0625 | 123.2529 | -61.5005 | 61.647 | 0.030283 | -0.040521 | -0.016578 | 0.002454 | 0.027109 | -0.005985 | 0.033424 | 61.5554 | 0.15706 | 61.4684 | -0.051417 | 0.016188 | 61.5616 | -0.006014 | 61.3764 | 61.5308 | 61.46 | 61.484 | 61.503 | 61.5277 | 61.4946 | 61.534 | 123.056 | 61.6576 | 122.9689 | 61.4491 | 61.5167 | 123.0621 | 61.4945 | 122.8769 | 61.5392 | 61.5614 | 61.4522 | 61.4744
603.0625 | 123.2758 | -61.4868 | 61.6608 | 0.030283 | -0.035942 | -0.012 | 0.007033 | 0.031687 | -0.010563 | 0.015112 | 61.5508 | 0.15706 | 61.4317 | -0.055996 | 0.01161 | 61.5662 | -0.006014 | 61.381 | 61.5171 | 61.4509 | 61.4748 | 61.4938 | 61.5185 | 61.4763 | 61.5019 | 123.0377 | 61.6439 | 122.9185 | 61.4308 | 61.4984 | 123.053 | 61.4808 | 122.8678 | 61.5392 | 61.5568 | 61.4201 | 61.4377
604.0625 | 123.3673 | -61.4273 | 61.5875 | 0.021127 | -0.040521 | -0.021157 | -0.002124 | 0.017953 | -0.001406 | 0.01969 | 61.56 | 0.16622 | 61.4775 | -0.046838 | 0.002454 | 61.5616 | -0.006014 | 61.381 | 61.4484 | 61.3868 | 61.4061 | 61.4252 | 61.4453 | 61.4259 | 61.447 | 122.9873 | 61.5935 | 122.9048 | 61.3805 | 61.4298 | 122.9889 | 61.4213 | 122.8083 | 61.5575 | 61.566 | 61.4751 | 61.4835
605.0625 | 123.3032 | -61.4273 | 61.6196 | 0.034862 | -0.031363 | -0.021157 | 0.002454 | 0.017953 | -0.005985 | 0.024268 | 61.5554 | 0.15248 | 61.4363 | -0.046838 | 0.01161 | 61.5707 | 0.003143 | 61.381 | 61.4622 | 61.3959 | 61.4061 | 61.4298 | 61.4453 | 61.4213 | 61.4516 | 122.9827 | 61.5798 | 122.8636 | 61.3805 | 61.4389 | 122.998 | 61.4305 | 122.8083 | 61.5438 | 61.5523 | 61.4247 | 61.4332
606.0625 | 123.3582 | -61.4365 | 61.6287 | 0.034862 | -0.040521 | -0.016578 | -0.006703 | 0.017953 | -0.001406 | 0.024268 | 61.5554 | 0.16164 | 61.4317 | -0.051417 | 0.020767 | 61.5753 | -0.001436 | 61.3856 | 61.4713 | 61.3959 | 61.4199 | 61.4298 | 61.4544 | 61.4351 | 61.4607 | 122.9919 | 61.5981 | 122.8682 | 61.385 | 61.4572 | 123.0118 | 61.435 | 122.822 | 61.5346 | 61.5568 | 61.411 | 61.4332
607.0625 | 123.3078 | -61.4639 | 61.6425 | 0.03944 | -0.035942 | -0.007421 | 0.007033 | 0.022531 | 0.003172 | 0.024268 | 61.5554 | 0.16622 | 61.4912 | -0.055996 | 0.01161 | 61.5707 | -0.001436 | 61.3764 | 61.5034 | 61.428 | 61.4565 | 61.471 | 61.4865 | 61.4671 | 61.4882 | 123.0193 | 61.6301 | 122.9552 | 61.4079 | 61.4755 | 123.0347 | 61.4625 | 122.8403 | 61.5438 | 61.5568 | 61.4796 | 61.4927
608.0625 | 123.2803 | -61.4868 | 61.6562 | 0.030283 | -0.035942 | -0.021157 | -0.006703 | 0.022531 | 0.003172 | 0.024268 | 61.56 | 0.16164 | 61.4271 | -0.042259 | 0.016188 | 61.5707 | -0.001436 | 61.3764 | 61.5171 | 61.4509 | 61.4657 | 61.4801 | 61.5093 | 61.49 | 61.5111 | 123.0468 | 61.6485 | 122.914 | 61.4446 | 61.503 | 123.0576 | 61.4854 | 122.8632 | 61.5438 | 61.5614 | 61.411 | 61.4286
609.0625 | 123.2483 | -61.5097 | 61.6196 | 0.025705 | -0.035942 | -0.012 | -0.002124 | 0.027109 | 0.003172 | 0.024268 | 61.5554 | 0.15706 | 61.4409 | -0.055996 | 0.007032 | 61.5662 | -0.006014 | 61.3764 | 61.5354 | 61.4738 | 61.4977 | 61.5076 | 61.5368 | 61.5129 | 61.534 | 123.0651 | 61.6668 | 122.9506 | 61.4537 | 61.5167 | 123.0759 | 61.5037 | 122.8861 | 61.5484 | 61.5614 | 61.4339 | 61.4469
610.0625 | 123.2986 | -61.4822 | 61.6333 | 0.025705 | -0.026784 | -0.012 | 0.002454 | 0.027109 | 0.003172 | 0.01969 | 61.5508 | 0.17079 | 61.4775 | -0.051417 | 0.025345 | 61.5845 | -0.001436 | 61.3672 | 61.5079 | 61.4555 | 61.4702 | 61.4847 | 61.5093 | 61.4854 | 61.5019 | 123.0331 | 61.653 | 122.9597 | 61.4308 | 61.5076 | 123.0667 | 61.4808 | 122.8495 | 61.5255 | 61.5523 | 61.4522 | 61.4789
611.0625 | 123.2803 | -61.4502 | 61.6562 | 0.030283 | -0.035942 | -0.016578 | -0.002124 | 0.027109 | -0.001406 | 0.024268 | 61.5554 | 0.16164 | 61.4226 | -0.060575 | 0.01161 | 61.5707 | -0.001436 | 61.381 | 61.4805 | 61.4143 | 61.4336 | 61.4481 | 61.4773 | 61.4488 | 61.4745 | 123.0056 | 61.6118 | 122.8728 | 61.3896 | 61.4618 | 123.0209 | 61.4488 | 122.8312 | 61.5438 | 61.5568 | 61.411 | 61.424
612.0625 | 123.2574 | -61.496 | 61.6379 | 0.030283 | -0.035942 | -0.021157 | -0.002124 | 0.031687 | -0.001406 | 0.028846 | 61.56 | 0.15248 | 61.4775 | -0.051417 | 0.020767 | 61.5707 | 0.003143 | 61.3764 | 61.5263 | 61.46 | 61.4748 | 61.4938 | 61.5277 | 61.4946 | 61.5248 | 123.056 | 61.6485 | 122.9735 | 61.4446 | 61.5167 | 123.0667 | 61.4991 | 122.8724 | 61.5392 | 61.5568 | 61.4567 | 61.4744
613.0625 | 123.2391 | -61.4777 | 61.6516 | 0.034862 | -0.035942 | -0.012 | -0.002124 | 0.022531 | -0.001406 | 0.01969 | 61.5554 | 0.15706 | 61.4455 | -0.051417 | 0.020767 | 61.5707 | 0.007721 | 61.3764 | 61.5125 | 61.4417 | 61.4657 | 61.4755 | 61.5002 | 61.4763 | 61.4974 | 123.0331 | 61.6347 | 122.9231 | 61.4262 | 61.4984 | 123.0484 | 61.4854 | 122.8541 | 61.5346 | 61.5477 | 61.4247 | 61.4377
614.0625 | 123.3215 | -61.5234 | 61.615 | 0.025705 | -0.040521 | -0.012 | 0.007033 | 0.022531 | -0.005985 | 0.01969 | 61.5508 | 0.16164 | 61.4271 | -0.051417 | 0.020767 | 61.5707 | -0.001436 | 61.3718 | 61.5491 | 61.4829 | 61.5114 | 61.5305 | 61.546 | 61.5175 | 61.5431 | 123.0743 | 61.6851 | 122.9506 | 61.472 | 61.5442 | 123.0942 | 61.522 | 122.8953 | 61.5301 | 61.5523 | 61.4064 | 61.4286
615.0625 | 123.2849 | -61.4594 | 61.615 | 0.030283 | -0.035942 | -0.016578 | -0.006703 | 0.022531 | 0.003172 | 0.024268 | 61.5554 | 0.15248 | 61.4867 | -0.055996 | 0.01161 | 61.5707 | -0.006014 | 61.381 | 61.4896 | 61.4234 | 61.4428 | 61.4526 | 61.4819 | 61.4625 | 61.4836 | 123.0148 | 61.6118 | 122.946 | 61.4034 | 61.471 | 123.0301 | 61.4533 | 122.8403 | 61.5438 | 61.5614 | 61.4751 | 61.4927
616.0625 | 123.2941 | -61.4685 | 61.6379 | 0.025705 | -0.031363 | -0.007421 | -0.006703 | 0.027109 | -0.005985 | 0.024268 | 61.5508 | 0.16164 | 61.4409 | -0.055996 | 0.007032 | 61.5707 | -0.006014 | 61.3764 | 61.4942 | 61.4371 | 61.4611 | 61.4618 | 61.4956 | 61.4625 | 61.4928 | 123.0193 | 61.6301 | 122.9094 | 61.4125 | 61.4755 | 123.0392 | 61.4625 | 122.8449 | 61.5438 | 61.5568 | 61.4339 | 61.4469
617.0625 | 123.2712 | -61.496 | 61.6516 | 0.030283 | -0.040521 | -0.012 | -0.006703 | 0.027109 | -0.001406 | 0.024268 | 61.5554 | 0.15706 | 61.4409 | -0.046838 | 0.01161 | 61.5662 | 0.003143 | 61.381 | 61.5263 | 61.4555 | 61.484 | 61.4893 | 61.5231 | 61.4946 | 61.5202 | 123.0514 | 61.653 | 122.9369 | 61.4491 | 61.5076 | 123.0621 | 61.4991 | 122.8769 | 61.5438 | 61.5523 | 61.4293 | 61.4377
618.0625 | 123.317 | -61.4914 | 61.615 | 0.030283 | -0.040521 | -0.016578 | -0.002124 | 0.022531 | -0.001406 | 0.024268 | 61.56 | 0.16164 | 61.4867 | -0.051417 | 0.01161 | 61.5662 | 0.003143 | 61.3764 | 61.5217 | 61.4509 | 61.4748 | 61.4893 | 61.5139 | 61.49 | 61.5157 | 123.0514 | 61.653 | 122.9781 | 61.44 | 61.503 | 123.0576 | 61.4945 | 122.8678 | 61.5484 | 61.5568 | 61.4751 | 61.4835
619.0625 | 123.2986 | -61.4731 | 61.6699 | 0.034862 | -0.040521 | -0.007421 | -0.006703 | 0.022531 | 0.003172 | 0.028846 | 61.5554 | 0.16164 | 61.4409 | -0.046838 | 0.01161 | 61.5662 | -0.006014 | 61.381 | 61.5079 | 61.4326 | 61.4657 | 61.4664 | 61.4956 | 61.4763 | 61.5019 | 123.0285 | 61.6347 | 122.914 | 61.4262 | 61.4847 | 123.0392 | 61.4671 | 122.8541 | 61.5438 | 61.5614 | 61.4293 | 61.4469
620.0625 | 123.2758 | -61.4868 | 61.6425 | 0.030283 | -0.035942 | -0.012 | -0.002124 | 0.031687 | -0.001406 | 0.024268 | 61.56 | 0.16622 | 61.4684 | -0.060575 | 0.020767 | 61.5753 | -0.001436 | 61.3764 | 61.5171 | 61.4509 | 61.4748 | 61.4847 | 61.5185 | 61.4854 | 61.5111 | 123.0468 | 61.653 | 122.9552 | 61.4262 | 61.5076 | 123.0621 | 61.4854 | 122.8632 | 61.5392 | 61.5614 | 61.4476 | 61.4698
621.0625 | 123.2941 | -61.4822 | 61.6379 | 0.034862 | -0.040521 | -0.016578 | 0.002454 | 0.031687 | -0.005985 | 0.024268 | 61.56 | 0.16164 | 61.4409 | -0.046838 | 0.016188 | 61.5753 | -0.006014 | 61.3856 | 61.5171 | 61.4417 | 61.4657 | 61.4847 | 61.5139 | 61.4763 | 61.5065 | 123.0422 | 61.6439 | 122.9231 | 61.4354 | 61.4984 | 123.0576 | 61.4762 | 122.8678 | 61.5438 | 61.566 | 61.4247 | 61.4469
622.0625 | 123.3261 | -61.4639 | 61.5829 | 0.030283 | -0.035942 | -0.021157 | -0.006703 | 0.022531 | -0.010563 | 0.024268 | 61.5463 | 0.16164 | 61.4363 | -0.065154 | 0.016188 | 61.5707 | -0.006014 | 61.3718 | 61.4942 | 61.428 | 61.4428 | 61.4572 | 61.4865 | 61.4534 | 61.4882 | 123.0102 | 61.6256 | 122.9002 | 61.3988 | 61.4801 | 123.0347 | 61.4579 | 122.8357 | 61.5301 | 61.5523 | 61.4201 | 61.4423
623.0625 | 123.2941 | -61.4914 | 61.6287 | 0.030283 | -0.040521 | -0.012 | -0.002124 | 0.031687 | -0.001406 | 0.024268 | 61.5691 | 0.16622 | 61.4867 | -0.055996 | 0.016188 | 61.5707 | -0.006014 | 61.3718 | 61.5217 | 61.4509 | 61.4794 | 61.4893 | 61.5231 | 61.49 | 61.5157 | 123.0605 | 61.6576 | 122.9781 | 61.4354 | 61.5076 | 123.0621 | 61.4854 | 122.8632 | 61.553 | 61.5752 | 61.4705 | 61.4927
624.0625 | 123.2803 | -61.4777 | 61.6241 | 0.025705 | -0.035942 | -0.016578 | -0.011281 | 0.022531 | -0.001406 | 0.028846 | 61.56 | 0.16164 | 61.4409 | -0.051417 | 0.01161 | 61.5753 | -0.010593 | 61.3764 | 61.5034 | 61.4417 | 61.4611 | 61.4664 | 61.5002 | 61.4763 | 61.5065 | 123.0377 | 61.6393 | 122.9185 | 61.4262 | 61.4893 | 123.053 | 61.4671 | 122.8541 | 61.5484 | 61.5706 | 61.4293 | 61.4515
625.0625 | 123.2437 | -61.4822 | 61.6013 | 0.030283 | -0.040521 | -0.012 | -0.002124 | 0.017953 | -0.001406 | 0.024268 | 61.5554 | 0.16622 | 61.4455 | -0.051417 | 0.020767 | 61.5662 | -0.001436 | 61.3764 | 61.5125 | 61.4417 | 61.4702 | 61.4801 | 61.5002 | 61.4808 | 61.5065 | 123.0377 | 61.6485 | 122.9277 | 61.4308 | 61.503 | 123.0484 | 61.4808 | 122.8586 | 61.5346 | 61.5568 | 61.4247 | 61.4469
626.0625 | 123.2986 | -61.4548 | 61.6196 | 0.030283 | -0.031363 | -0.012 | -0.002124 | 0.022531 | 0.003172 | 0.024268 | 61.5646 | 0.16164 | 61.4958 | -0.046838 | 0.016188 | 61.5707 | -0.006014 | 61.3764 | 61.4851 | 61.4234 | 61.4428 | 61.4526 | 61.4773 | 61.4579 | 61.479 | 123.0193 | 61.6164 | 122.9506 | 61.4079 | 61.471 | 123.0255 | 61.4488 | 122.8312 | 61.5484 | 61.5706 | 61.4796 | 61.5018
627.0625 | 123.381 | -61.4502 | 61.5829 | 0.025705 | -0.040521 | -0.012 | -0.006703 | 0.017953 | 0.003172 | 0.01969 | 61.5554 | 0.15706 | 61.4317 | -0.051417 | 0.007032 | 61.5707 | -0.001436 | 61.3718 | 61.4759 | 61.4097 | 61.4382 | 61.4435 | 61.4681 | 61.4534 | 61.4699 | 123.0056 | 61.6073 | 122.8819 | 61.3988 | 61.4572 | 123.0209 | 61.4488 | 122.822 | 61.5484 | 61.5568 | 61.4247 | 61.4332
628.0625 | 123.2895 | -61.4868 | 61.615 | 0.025705 | -0.035942 | -0.016578 | -0.002124 | 0.022531 | 0.003172 | 0.015112 | 61.56 | 0.15706 | 61.4592 | -0.055996 | 0.016188 | 61.5662 | 0.003143 | 61.3764 | 61.5125 | 61.4509 | 61.4702 | 61.4847 | 61.5093 | 61.49 | 61.5019 | 123.0468 | 61.6439 | 122.946 | 61.4308 | 61.503 | 123.053 | 61.49 | 122.8632 | 61.5438 | 61.5568 | 61.443 | 61.4561
629.0625 | 123.2758 | -61.4594 | 61.6241 | 0.030283 | -0.040521 | -0.007421 | 0.002454 | 0.027109 | -0.001406 | 0.024268 | 61.5646 | 0.16164 | 61.4775 | -0.055996 | 0.01161 | 61.5707 | -0.006014 | 61.3718 | 61.4896 | 61.4188 | 61.4519 | 61.4618 | 61.4865 | 61.4579 | 61.4836 | 123.0239 | 61.621 | 122.9369 | 61.4034 | 61.471 | 123.0301 | 61.4533 | 122.8312 | 61.553 | 61.5706 | 61.4659 | 61.4835
630.0625 | 123.2483 | -61.4594 | 61.6196 | 0.030283 | -0.040521 | -0.007421 | 0.002454 | 0.022531 | -0.015142 | 0.024268 | 61.56 | 0.16164 | 61.4363 | -0.055996 | 0.007032 | 61.5662 | -0.001436 | 61.3764 | 61.4896 | 61.4188 | 61.4519 | 61.4618 | 61.4819 | 61.4442 | 61.4836 | 123.0193 | 61.621 | 122.8957 | 61.4034 | 61.4664 | 123.0255 | 61.4579 | 122.8357 | 61.553 | 61.5614 | 61.4293 | 61.4377
631.0625 | 123.3032 | -61.4639 | 61.6196 | 0.030283 | -0.031363 | -0.016578 | -0.006703 | 0.027109 | -0.005985 | 0.024268 | 61.56 | 0.15706 | 61.4684 | -0.051417 | 0.020767 | 61.5707 | -0.006014 | 61.3764 | 61.4942 | 61.4326 | 61.4474 | 61.4572 | 61.491 | 61.4579 | 61.4882 | 123.0239 | 61.621 | 122.9323 | 61.4125 | 61.4847 | 123.0347 | 61.4579 | 122.8403 | 61.5392 | 61.566 | 61.4476 | 61.4744
632.0625 | 123.2437 | -61.5005 | 61.6241 | 0.034862 | -0.040521 | -0.012 | 0.002454 | 0.027109 | 0.003172 | 0.015112 | 61.5646 | 0.16164 | 61.4592 | -0.055996 | 0.01161 | 61.5662 | -0.006014 | 61.381 | 61.5354 | 61.46 | 61.4885 | 61.503 | 61.5277 | 61.5037 | 61.5157 | 123.0651 | 61.6622 | 122.9597 | 61.4446 | 61.5122 | 123.0667 | 61.4945 | 122.8815 | 61.553 | 61.5706 | 61.4476 | 61.4652
633.0625 | 123.3215 | -61.4822 | 61.6287 | 0.030283 | -0.035942 | -0.016578 | -0.006703 | 0.027109 | -0.001406 | 0.01969 | 61.56 | 0.16164 | 61.4363 | -0.060575 | 0.01161 | 61.5707 | -0.001436 | 61.381 | 61.5125 | 61.4463 | 61.4657 | 61.4755 | 61.5093 | 61.4808 | 61.5019 | 123.0422 | 61.6439 | 122.9185 | 61.4217 | 61.4938 | 123.053 | 61.4808 | 122.8632 | 61.5484 | 61.5614 | 61.4247 | 61.4377
634.0625 | 123.3124 | -61.4456 | 61.6287 | 0.021127 | -0.031363 | -0.012 | -0.006703 | 0.017953 | 0.003172 | 0.024268 | 61.5646 | 0.16164 | 61.5004 | -0.051417 | 0.020767 | 61.5799 | -0.001436 | 61.3718 | 61.4667 | 61.4143 | 61.4336 | 61.4389 | 61.4636 | 61.4488 | 61.4699 | 123.0102 | 61.6073 | 122.946 | 61.3942 | 61.4664 | 123.0255 | 61.4442 | 122.8174 | 61.5438 | 61.566 | 61.4796 | 61.5018
635.0625 | 123.262 | -61.4639 | 61.6241 | 0.034862 | -0.035942 | -0.007421 | -0.002124 | 0.027109 | -0.001406 | 0.024268 | 61.56 | 0.15706 | 61.4455 | -0.051417 | 0.025345 | 61.5662 | -0.006014 | 61.3764 | 61.4988 | 61.428 | 61.4565 | 61.4618 | 61.491 | 61.4625 | 61.4882 | 123.0239 | 61.621 | 122.9094 | 61.4125 | 61.4893 | 123.0301 | 61.4579 | 122.8403 | 61.5346 | 61.566 | 61.4201 | 61.4515
636.0625 | 123.317 | -61.4822 | 61.6333 | 0.030283 | -0.035942 | -0.012 | -0.006703 | 0.022531 | -0.005985 | 0.024268 | 61.5691 | 0.16622 | 61.4455 | -0.055996 | 0.020767 | 61.5662 | -0.001436 | 61.381 | 61.5125 | 61.4463 | 61.4702 | 61.4755 | 61.5048 | 61.4763 | 61.5065 | 123.0514 | 61.6485 | 122.9277 | 61.4262 | 61.503 | 123.0484 | 61.4808 | 122.8632 | 61.5484 | 61.5706 | 61.4247 | 61.4469
637.0625 | 123.2803 | -61.5005 | 61.6013 | 0.030283 | -0.035942 | -0.012 | -0.006703 | 0.027109 | -0.001406 | 0.024268 | 61.56 | 0.16164 | 61.4867 | -0.055996 | 0.016188 | 61.5707 | -0.006014 | 61.3718 | 61.5308 | 61.4646 | 61.4885 | 61.4938 | 61.5277 | 61.4991 | 61.5248 | 123.0605 | 61.6622 | 122.9872 | 61.4446 | 61.5167 | 123.0713 | 61.4945 | 122.8724 | 61.5438 | 61.566 | 61.4705 | 61.4927
638.0625 | 123.2986 | -61.4456 | 61.6333 | 0.021127 | -0.031363 | -0.016578 | 0.002454 | 0.017953 | -0.001406 | 0.024268 | 61.56 | 0.16164 | 61.4455 | -0.046838 | 0.016188 | 61.5707 | 0.003143 | 61.3764 | 61.4667 | 61.4143 | 61.429 | 61.4481 | 61.4636 | 61.4442 | 61.4699 | 123.0056 | 61.6073 | 122.8911 | 61.3988 | 61.4618 | 123.0164 | 61.4488 | 122.822 | 61.5438 | 61.5568 | 61.4293 | 61.4423
639.0625 | 123.2986 | -61.4548 | 61.6425 | 0.030283 | -0.031363 | -0.012 | -0.002124 | 0.027109 | -0.005985 | 0.024268 | 61.5646 | 0.16164 | 61.4455 | -0.046838 | 0.016188 | 61.5799 | 0.007721 | 61.3718 | 61.4851 | 61.4234 | 61.4428 | 61.4526 | 61.4819 | 61.4488 | 61.479 | 123.0193 | 61.6164 | 122.9002 | 61.4079 | 61.471 | 123.0347 | 61.4625 | 122.8266 | 61.5484 | 61.5569 | 61.4293 | 61.4377
640.0625 | 123.2941 | -61.4639 | 61.6745 | 0.034862 | -0.035942 | -0.012 | -0.006703 | 0.027109 | -0.005985 | 0.024268 | 61.5691 | 0.15706 | 61.4867 | -0.051417 | 0.01161 | 61.5707 | -0.001436 | 61.3764 | 61.4988 | 61.428 | 61.4519 | 61.4572 | 61.491 | 61.4579 | 61.4882 | 123.0331 | 61.621 | 122.9506 | 61.4125 | 61.4755 | 123.0347 | 61.4625 | 122.8403 | 61.5575 | 61.5706 | 61.4751 | 61.4881
641.0625 | 123.2758 | -61.4868 | 61.6516 | 0.025705 | -0.031363 | -0.016578 | -0.002124 | 0.017953 | -0.001406 | 0.024268 | 61.56 | 0.16164 | 61.4455 | -0.055996 | 0.020767 | 61.5799 | -0.001436 | 61.381 | 61.5125 | 61.4555 | 61.4702 | 61.4847 | 61.5048 | 61.4854 | 61.5111 | 123.0468 | 61.6485 | 122.9323 | 61.4308 | 61.5076 | 123.0667 | 61.4854 | 122.8678 | 61.5392 | 61.5614 | 61.4247 | 61.4469
642.0625 | 123.2254 | -61.4822 | 61.6333 | 0.025705 | -0.035942 | -0.012 | -0.002124 | 0.027109 | -0.005985 | 0.01969 | 61.56 | 0.16164 | 61.4455 | -0.046838 | 0.016188 | 61.5662 | 0.003143 | 61.3718 | 61.5079 | 61.4463 | 61.4702 | 61.4801 | 61.5093 | 61.4763 | 61.5019 | 123.0422 | 61.6439 | 122.9277 | 61.4354 | 61.4984 | 123.0484 | 61.4854 | 122.8541 | 61.5438 | 61.5568 | 61.4293 | 61.4423
643.0625 | 123.2483 | -61.4777 | 61.6837 | 0.030283 | -0.035942 | -0.012 | -0.002124 | 0.017953 | -0.001406 | 0.028846 | 61.5646 | 0.15706 | 61.5004 | -0.046838 | 0.016188 | 61.5707 | 0.003143 | 61.381 | 61.5079 | 61.4417 | 61.4657 | 61.4755 | 61.4956 | 61.4763 | 61.5065 | 123.0422 | 61.6347 | 122.9781 | 61.4308 | 61.4938 | 123.0484 | 61.4808 | 122.8586 | 61.5484 | 61.5614 | 61.4842 | 61.4973
644.0625 | 123.3124 | -61.4777 | 61.6333 | 0.030283 | -0.040521 | -0.016578 | -0.002124 | 0.027109 | -0.005985 | 0.015112 | 61.5554 | 0.15706 | 61.4317 | -0.046838 | 0.016188 | 61.5662 | 0.003143 | 61.381 | 61.5079 | 61.4371 | 61.4611 | 61.4755 | 61.5048 | 61.4717 | 61.4928 | 123.0331 | 61.6347 | 122.9094 | 61.4308 | 61.4938 | 123.0438 | 61.4808 | 122.8586 | 61.5392 | 61.5523 | 61.4155 | 61.4286
645.0625 | 123.262 | -61.4685 | 61.6516 | 0.034862 | -0.040521 | -0.016578 | 0.002454 | 0.017953 | -0.010563 | 0.01969 | 61.5646 | 0.16622 | 61.4638 | -0.055996 | 0.01161 | 61.5707 | 0.007721 | 61.381 | 61.5034 | 61.428 | 61.4519 | 61.471 | 61.4865 | 61.4579 | 61.4882 | 123.0331 | 61.6347 | 122.9323 | 61.4125 | 61.4801 | 123.0392 | 61.4762 | 122.8495 | 61.553 | 61.5569 | 61.4522 | 61.4561
646.0625 | 123.2941 | -61.4822 | 61.6745 | 0.030283 | -0.031363 | -0.016578 | -0.006703 | 0.022531 | 0.003172 | 0.01969 | 61.5646 | 0.15706 | 61.4775 | -0.051417 | 0.01161 | 61.5662 | 0.007721 | 61.3718 | 61.5125 | 61.4509 | 61.4657 | 61.4755 | 61.5048 | 61.4854 | 61.5019 | 123.0468 | 61.6393 | 122.9597 | 61.4308 | 61.4938 | 123.0484 | 61.49 | 122.8541 | 61.553 | 61.5569 | 61.4659 | 61.4698
647.0625 | 123.2941 | -61.5189 | 61.6699 | 0.025705 | -0.035942 | -0.016578 | -0.002124 | 0.027109 | -0.001406 | 0.024268 | 61.5508 | 0.16164 | 61.4409 | -0.055996 | 0.020767 | 61.5662 | -0.001436 | 61.3764 | 61.5446 | 61.4829 | 61.5023 | 61.5167 | 61.546 | 61.5175 | 61.5431 | 123.0697 | 61.6805 | 122.9597 | 61.4629 | 61.5396 | 123.085 | 61.5174 | 122.8953 | 61.5301 | 61.5523 | 61.4201 | 61.4423
648.0625 | 123.2346 | -61.4731 | 61.6608 | 0.021127 | -0.0451 | -0.012 | -0.006703 | 0.027109 | 0.00775 | 0.033424 | 61.56 | 0.15248 | 61.4729 | -0.055996 | 0.020767 | 61.5799 | -0.006014 | 61.3672 | 61.4942 | 61.428 | 61.4611 | 61.4664 | 61.5002 | 61.4808 | 61.5065 | 123.0331 | 61.6256 | 122.946 | 61.4171 | 61.4939 | 123.053 | 61.4671 | 122.8403 | 61.5392 | 61.566 | 61.4522 | 61.4789
649.0625 | 123.2849 | -61.4868 | 61.6745 | 0.034862 | -0.0451 | -0.016578 | -0.002124 | 0.031687 | 0.003172 | 0.024268 | 61.56 | 0.16164 | 61.4455 | -0.055996 | 0.01161 | 61.5707 | -0.006014 | 61.3764 | 61.5217 | 61.4417 | 61.4702 | 61.4847 | 61.5185 | 61.49 | 61.5111 | 123.0468 | 61.6485 | 122.9323 | 61.4308 | 61.4984 | 123.0576 | 61.4808 | 122.8632 | 61.5484 | 61.566 | 61.4339 | 61.4515
650.0625 | 123.2666 | -61.4914 | 61.6425 | 0.034862 | -0.031363 | -0.012 | -0.006703 | 0.022531 | -0.001406 | 0.024268 | 61.56 | 0.16622 | 61.4409 | -0.051417 | 0.020767 | 61.5616 | 0.003143 | 61.3764 | 61.5263 | 61.46 | 61.4794 | 61.4847 | 61.5139 | 61.49 | 61.5157 | 123.0514 | 61.6576 | 122.9323 | 61.44 | 61.5122 | 123.053 | 61.4945 | 122.8678 | 61.5392 | 61.5568 | 61.4201 | 61.4377
651.0625 | 123.2391 | -61.4456 | 61.6516 | 0.030283 | -0.0451 | -0.016578 | 0.002454 | 0.027109 | 0.003172 | 0.028846 | 61.56 | 0.1479 | 61.4821 | -0.046838 | 0.016188 | 61.5707 | 0.003143 | 61.3856 | 61.4759 | 61.4005 | 61.429 | 61.4481 | 61.4727 | 61.4488 | 61.4745 | 123.0056 | 61.5935 | 122.9277 | 61.3988 | 61.4618 | 123.0164 | 61.4488 | 122.8312 | 61.5438 | 61.5568 | 61.4659 | 61.4789
652.0625 | 123.2346 | -61.4365 | 61.6562 | 0.030283 | -0.031363 | -0.021157 | 0.002454 | 0.027109 | -0.001406 | 0.024268 | 61.5554 | 0.16164 | 61.4363 | -0.055996 | 0.020767 | 61.5662 | 0.003143 | 61.3856 | 61.4667 | 61.4051 | 61.4153 | 61.4389 | 61.4636 | 61.4351 | 61.4607 | 122.9919 | 61.5981 | 122.8728 | 61.3805 | 61.4572 | 123.0026 | 61.4396 | 122.822 | 61.5346 | 61.5523 | 61.4155 | 61.4332
653.0625 | 123.2529 | -61.4685 | 61.6699 | 0.021127 | -0.040521 | -0.016578 | 0.002454 | 0.022531 | 0.003172 | 0.01969 | 61.56 | 0.15248 | 61.45 | -0.060575 | 0.016188 | 61.5707 | 0.003143 | 61.3718 | 61.4896 | 61.428 | 61.4519 | 61.471 | 61.491 | 61.4717 | 61.4882 | 123.0285 | 61.621 | 122.9185 | 61.4079 | 61.4847 | 123.0392 | 61.4716 | 122.8403 | 61.5438 | 61.5568 | 61.4339 | 61.4469
654.0625 | 123.2483 | -61.4777 | 61.6653 | 0.030283 | -0.031363 | -0.012 | -0.006703 | 0.027109 | 0.00775 | 0.033424 | 61.5646 | 0.16622 | 61.4912 | -0.046838 | 0.016188 | 61.5707 | 0.003143 | 61.3718 | 61.5079 | 61.4463 | 61.4657 | 61.471 | 61.5048 | 61.4854 | 61.5111 | 123.0422 | 61.6439 | 122.9689 | 61.4308 | 61.4938 | 123.0484 | 61.4808 | 122.8495 | 61.5484 | 61.5614 | 61.4751 | 61.4881
655.0625 | 123.3582 | -61.4639 | 61.6379 | 0.030283 | -0.035942 | -0.012 | 0.002454 | 0.022531 | -0.010563 | 0.024268 | 61.5463 | 0.16164 | 61.4363 | -0.055996 | 0.01161 | 61.5707 | 0.007721 | 61.3764 | 61.4942 | 61.428 | 61.4519 | 61.4664 | 61.4865 | 61.4534 | 61.4882 | 123.0102 | 61.6256 | 122.9002 | 61.4079 | 61.4755 | 123.0347 | 61.4716 | 122.8403 | 61.5346 | 61.5385 | 61.4247 | 61.4286
656.0625 | 123.262 | -61.4548 | 61.6379 | 0.025705 | -0.035942 | -0.016578 | -0.006703 | 0.022531 | -0.001406 | 0.024268 | 61.5554 | 0.15706 | 61.4775 | -0.046838 | 0.016188 | 61.5662 | -0.001436 | 61.3764 | 61.4805 | 61.4188 | 61.4382 | 61.4481 | 61.4773 | 61.4534 | 61.479 | 123.0102 | 61.6118 | 122.9323 | 61.4079 | 61.471 | 123.0209 | 61.4533 | 122.8312 | 61.5392 | 61.5568 | 61.4613 | 61.4789
657.0625 | 123.2254 | -61.4914 | 61.615 | 0.034862 | -0.035942 | -0.007421 | 0.002454 | 0.022531 | -0.005985 | 0.024268 | 61.5646 | 0.16164 | 61.4729 | -0.055996 | 0.016188 | 61.5707 | 0.003143 | 61.3672 | 61.5263 | 61.4555 | 61.484 | 61.4938 | 61.5139 | 61.4854 | 61.5157 | 123.056 | 61.653 | 122.9643 | 61.4354 | 61.5076 | 123.0621 | 61.4945 | 122.8586 | 61.5484 | 61.5614 | 61.4567 | 61.4698
658.0625 | 123.262 | -61.4731 | 61.6562 | 0.025705 | -0.040521 | -0.016578 | -0.002124 | 0.017953 | -0.001406 | 0.024268 | 61.56 | 0.15706 | 61.4317 | -0.046838 | 0.016188 | 61.5753 | 0.003143 | 61.3764 | 61.4988 | 61.4326 | 61.4565 | 61.471 | 61.491 | 61.4717 | 61.4974 | 123.0331 | 61.6301 | 122.9048 | 61.4262 | 61.4893 | 123.0484 | 61.4762 | 122.8495 | 61.5438 | 61.5568 | 61.4155 | 61.4286
659.0625 | 123.2666 | -61.4868 | 61.6516 | 0.025705 | -0.035942 | -0.012 | -0.002124 | 0.022531 | 0.003172 | 0.028846 | 61.5646 | 0.16164 | 61.4912 | -0.051417 | 0.01161 | 61.5707 | -0.001436 | 61.3718 | 61.5125 | 61.4509 | 61.4748 | 61.4847 | 61.5093 | 61.49 | 61.5157 | 123.0514 | 61.6485 | 122.9781 | 61.4354 | 61.4984 | 123.0576 | 61.4854 | 122.8586 | 61.553 | 61.566 | 61.4796 | 61.4927
660.0625 | 123.2529 | -61.4822 | 61.647 | 0.025705 | -0.035942 | -0.012 | -0.011281 | 0.027109 | -0.005985 | 0.028846 | 61.5508 | 0.16164 | 61.4546 | -0.051417 | 0.025345 | 61.5707 | 0.003143 | 61.3718 | 61.5079 | 61.4463 | 61.4702 | 61.471 | 61.5093 | 61.4763 | 61.5111 | 123.0331 | 61.6439 | 122.9369 | 61.4308 | 61.5076 | 123.053 | 61.4854 | 122.8541 | 61.5255 | 61.5477 | 61.4293 | 61.4515
661.0625 | 123.3856 | -61.4319 | 61.615 | 0.025705 | -0.031363 | -0.016578 | -0.002124 | 0.022531 | -0.005985 | 0.028846 | 61.5508 | 0.16164 | 61.4592 | -0.055996 | 0.016188 | 61.5707 | -0.001436 | 61.3672 | 61.4576 | 61.4005 | 61.4153 | 61.4298 | 61.4544 | 61.4259 | 61.4607 | 122.9827 | 61.5935 | 122.8911 | 61.3759 | 61.4481 | 123.0026 | 61.4304 | 122.7991 | 61.5346 | 61.5523 | 61.443 | 61.4606
662.0625 | 123.349 | -61.4502 | 61.5967 | 0.025705 | -0.040521 | -0.021157 | -0.002124 | 0.017953 | -0.005985 | 0.015112 | 61.5508 | 0.16164 | 61.4592 | -0.055996 | 0.01161 | 61.5707 | -0.006014 | 61.3764 | 61.4759 | 61.4097 | 61.429 | 61.4481 | 61.4681 | 61.4442 | 61.4653 | 123.001 | 61.6118 | 122.9094 | 61.3942 | 61.4618 | 123.0209 | 61.4442 | 122.8266 | 61.5392 | 61.5568 | 61.4476 | 61.4652
663.0625 | 123.3582 | -61.4639 | 61.6333 | 0.030283 | -0.035942 | -0.012 | -0.002124 | 0.027109 | -0.005985 | 0.028846 | 61.5554 | 0.16164 | 61.45 | -0.051417 | 0.025345 | 61.5753 | 0.003143 | 61.3718 | 61.4942 | 61.428 | 61.4519 | 61.4618 | 61.491 | 61.4579 | 61.4928 | 123.0193 | 61.6256 | 122.914 | 61.4125 | 61.4893 | 123.0392 | 61.4671 | 122.8357 | 61.5301 | 61.5523 | 61.4247 | 61.4469
664.0625 | 123.3398 | -61.4639 | 61.6241 | 0.030283 | -0.040521 | -0.025735 | -0.006703 | 0.022531 | -0.005985 | 0.024268 | 61.56 | 0.16164 | 61.4775 | -0.051417 | 0.020767 | 61.5753 | -0.001436 | 61.3672 | 61.4942 | 61.4234 | 61.4382 | 61.4572 | 61.4865 | 61.4579 | 61.4882 | 123.0239 | 61.6256 | 122.9414 | 61.4125 | 61.4847 | 123.0392 | 61.4625 | 122.8312 | 61.5392 | 61.5614 | 61.4567 | 61.4789
665.0625 | 123.317 | -61.4639 | 61.6425 | 0.030283 | -0.040521 | -0.012 | -0.002124 | 0.022531 | -0.005985 | 0.01969 | 61.5554 | 0.15706 | 61.4455 | -0.051417 | 0.020767 | 61.5662 | 0.003143 | 61.3856 | 61.4942 | 61.4234 | 61.4519 | 61.4618 | 61.4865 | 61.4579 | 61.4836 | 123.0193 | 61.621 | 122.9094 | 61.4125 | 61.4847 | 123.0301 | 61.4671 | 122.8495 | 61.5346 | 61.5523 | 61.4247 | 61.4423
666.0625 | 123.317 | -61.4731 | 61.647 | 0.034862 | -0.040521 | -0.016578 | 0.002454 | 0.031687 | -0.001406 | 0.024268 | 61.5554 | 0.16622 | 61.4775 | -0.051417 | 0.01161 | 61.5707 | -0.001436 | 61.381 | 61.5079 | 61.4326 | 61.4565 | 61.4755 | 61.5048 | 61.4717 | 61.4974 | 123.0285 | 61.6393 | 122.9506 | 61.4217 | 61.4847 | 123.0438 | 61.4716 | 122.8541 | 61.5438 | 61.5568 | 61.4659 | 61.4789
667.0625 | 123.3124 | -61.4731 | 61.6196 | 0.025705 | -0.040521 | -0.021157 | -0.002124 | 0.027109 | -0.001406 | 0.01969 | 61.5646 | 0.16622 | 61.4409 | -0.051417 | 0.016188 | 61.5707 | -0.001436 | 61.3901 | 61.4988 | 61.4326 | 61.4519 | 61.471 | 61.5002 | 61.4717 | 61.4928 | 123.0377 | 61.6393 | 122.914 | 61.4217 | 61.4893 | 123.0438 | 61.4716 | 122.8632 | 61.5484 | 61.566 | 61.4247 | 61.4423
668.0625 | 123.3765 | -61.4182 | 61.6653 | 0.030283 | -0.035942 | -0.016578 | -0.002124 | 0.022531 | -0.001406 | 0.028846 | 61.56 | 0.15706 | 61.4958 | -0.051417 | 0.016188 | 61.5707 | -0.001436 | 61.3764 | 61.4484 | 61.3822 | 61.4016 | 61.416 | 61.4407 | 61.4167 | 61.447 | 122.9781 | 61.5752 | 122.914 | 61.3667 | 61.4343 | 122.9889 | 61.4167 | 122.7945 | 61.5438 | 61.5614 | 61.4796 | 61.4973
669.0625 | 123.3582 | -61.4594 | 61.6241 | 0.025705 | -0.035942 | -0.012 | -0.006703 | 0.027109 | -0.001406 | 0.024268 | 61.56 | 0.16622 | 61.4363 | -0.055996 | 0.020767 | 61.5753 | 0.007721 | 61.3764 | 61.4851 | 61.4234 | 61.4474 | 61.4526 | 61.4865 | 61.4579 | 61.4836 | 123.0193 | 61.6256 | 122.8957 | 61.4034 | 61.4801 | 123.0347 | 61.4671 | 122.8357 | 61.5392 | 61.5523 | 61.4155 | 61.4286
670.0625 | 123.3536 | -61.4273 | 61.6104 | 0.030283 | -0.040521 | -0.012 | -0.006703 | 0.022531 | -0.005985 | 0.028846 | 61.56 | 0.15706 | 61.4912 | -0.055996 | 0.01161 | 61.557 | -0.001436 | 61.3627 | 61.4576 | 61.3868 | 61.4153 | 61.4206 | 61.4498 | 61.4213 | 61.4562 | 122.9873 | 61.5844 | 122.9186 | 61.3713 | 61.4389 | 122.9843 | 61.4259 | 122.79 | 61.5484 | 61.5614 | 61.4796 | 61.4927
671.0625 | 123.349 | -61.4456 | 61.5967 | 0.030283 | -0.035942 | -0.021157 | -0.002124 | 0.022531 | -0.001406 | 0.024268 | 61.5646 | 0.17079 | 61.4409 | -0.051417 | 0.020767 | 61.5753 | 0.003143 | 61.3718 | 61.4759 | 61.4097 | 61.4245 | 61.4435 | 61.4681 | 61.4442 | 61.4699 | 123.0102 | 61.6164 | 122.8865 | 61.3942 | 61.4664 | 123.0209 | 61.4488 | 122.8174 | 61.5438 | 61.5614 | 61.4201 | 61.4377
672.0625 | 123.317 | -61.4502 | 61.6379 | 0.025705 | -0.035942 | -0.016578 | 0.007033 | 0.031687 | 0.003172 | 0.028846 | 61.56 | 0.16622 | 61.4821 | -0.051417 | 0.016188 | 61.5707 | 0.003143 | 61.3764 | 61.4759 | 61.4143 | 61.4336 | 61.4572 | 61.4819 | 61.4534 | 61.479 | 123.0102 | 61.6164 | 122.9323 | 61.3988 | 61.4664 | 123.0209 | 61.4533 | 122.8266 | 61.5438 | 61.5568 | 61.4659 | 61.4789
673.0625 | 123.349 | -61.4685 | 61.6425 | 0.030283 | -0.035942 | -0.016578 | -0.006703 | 0.022531 | 0.003172 | 0.028846 | 61.5554 | 0.16164 | 61.45 | -0.051417 | 0.020767 | 61.5707 | 0.003143 | 61.3718 | 61.4988 | 61.4326 | 61.4519 | 61.4618 | 61.491 | 61.4717 | 61.4974 | 123.0239 | 61.6301 | 122.9185 | 61.4171 | 61.4893 | 123.0392 | 61.4716 | 122.8403 | 61.5346 | 61.5523 | 61.4293 | 61.4469
674.0625 | 123.3582 | -61.4502 | 61.6287 | 0.025705 | -0.035942 | -0.016578 | 0.007033 | 0.027109 | -0.001406 | 0.024268 | 61.5554 | 0.16164 | 61.4409 | -0.055996 | 0.020767 | 61.5662 | 0.003143 | 61.3672 | 61.4759 | 61.4143 | 61.4336 | 61.4572 | 61.4773 | 61.4488 | 61.4745 | 123.0056 | 61.6118 | 122.8911 | 61.3942 | 61.471 | 123.0164 | 61.4533 | 122.8174 | 61.5346 | 61.5523 | 61.4201 | 61.4377
675.0625 | 123.3673 | -61.4639 | 61.6241 | 0.025705 | -0.0451 | -0.012 | -0.002124 | 0.027109 | -0.005985 | 0.024268 | 61.5646 | 0.16622 | 61.4775 | -0.051417 | 0.020767 | 61.5707 | 0.003143 | 61.3718 | 61.4896 | 61.4188 | 61.4519 | 61.4618 | 61.491 | 61.4579 | 61.4882 | 123.0285 | 61.6301 | 122.9414 | 61.4125 | 61.4847 | 123.0347 | 61.4671 | 122.8357 | 61.5438 | 61.5614 | 61.4567 | 61.4744
676.0625 | 123.4314 | -61.4502 | 61.6287 | 0.030283 | -0.040521 | -0.012 | -0.002124 | 0.027109 | -0.001406 | 0.024268 | 61.5554 | 0.17079 | 61.4455 | -0.046838 | 0.025345 | 61.5753 | -0.001436 | 61.3764 | 61.4805 | 61.4097 | 61.4382 | 61.4481 | 61.4773 | 61.4488 | 61.4745 | 123.0056 | 61.621 | 122.8957 | 61.4034 | 61.4755 | 123.0255 | 61.4488 | 122.8266 | 61.5301 | 61.5568 | 61.4201 | 61.4469
677.0625 | 123.2758 | -61.4639 | 61.6379 | 0.030283 | -0.040521 | -0.016578 | -0.002124 | 0.027109 | -0.001406 | 0.024268 | 61.56 | 0.16622 | 61.4592 | -0.051417 | 0.01161 | 61.5707 | 0.003143 | 61.3672 | 61.4942 | 61.4234 | 61.4474 | 61.4618 | 61.491 | 61.4625 | 61.4882 | 123.0239 | 61.6301 | 122.9231 | 61.4125 | 61.4755 | 123.0347 | 61.4671 | 122.8312 | 61.5484 | 61.5568 | 61.4476 | 61.4561
678.0625 | 123.3536 | -61.4548 | 61.6241 | 0.025705 | -0.035942 | -0.021157 | -0.006703 | 0.027109 | -0.001406 | 0.024268 | 61.5646 | 0.17079 | 61.4912 | -0.051417 | 0.016188 | 61.5707 | -0.001436 | 61.3672 | 61.4805 | 61.4188 | 61.4336 | 61.4481 | 61.4819 | 61.4534 | 61.479 | 123.0193 | 61.6256 | 122.946 | 61.4034 | 61.471 | 123.0255 | 61.4533 | 122.822 | 61.5484 | 61.566 | 61.4751 | 61.4927
679.0625 | 123.3261 | -61.4639 | 61.6516 | 0.034862 | -0.0451 | -0.007421 | -0.006703 | 0.017953 | -0.010563 | 0.024268 | 61.5554 | 0.16164 | 61.4363 | -0.051417 | 0.020767 | 61.5662 | -0.001436 | 61.3718 | 61.4988 | 61.4188 | 61.4565 | 61.4572 | 61.4819 | 61.4534 | 61.4882 | 123.0193 | 61.6256 | 122.9002 | 61.4125 | 61.4847 | 123.0301 | 61.4625 | 122.8357 | 61.5346 | 61.5568 | 61.4155 | 61.4377
680.0625 | 123.3948 | -61.4273 | 61.6425 | 0.025705 | -0.040521 | -0.016578 | -0.006703 | 0.027109 | -0.005985 | 0.028846 | 61.5554 | 0.16164 | 61.4775 | -0.055996 | 0.020767 | 61.5707 | 0.003143 | 61.3718 | 61.453 | 61.3868 | 61.4107 | 61.4206 | 61.4544 | 61.4213 | 61.4562 | 122.9827 | 61.5889 | 122.9048 | 61.3713 | 61.4481 | 122.998 | 61.4305 | 122.7991 | 61.5346 | 61.5523 | 61.4567 | 61.4744
681.0625 | 123.3627 | -61.4456 | 61.6241 | 0.025705 | -0.035942 | -0.016578 | -0.006703 | 0.022531 | -0.005985 | 0.024268 | 61.56 | 0.17537 | 61.4684 | -0.055996 | 0.01161 | 61.5753 | -0.001436 | 61.3718 | 61.4713 | 61.4097 | 61.429 | 61.4389 | 61.4681 | 61.4396 | 61.4699 | 123.0056 | 61.621 | 122.914 | 61.3896 | 61.4572 | 123.0209 | 61.4442 | 122.8174 | 61.5484 | 61.5614 | 61.4567 | 61.4698
682.0625 | 123.3261 | -61.4502 | 61.647 | 0.021127 | -0.040521 | -0.012 | 0.002454 | 0.027109 | -0.005985 | 0.028846 | 61.56 | 0.15706 | 61.4455 | -0.055996 | 0.016188 | 61.5753 | -0.001436 | 61.3718 | 61.4713 | 61.4097 | 61.4382 | 61.4526 | 61.4773 | 61.4442 | 61.479 | 123.0102 | 61.6073 | 122.8957 | 61.3942 | 61.4664 | 123.0255 | 61.4488 | 122.822 | 61.5438 | 61.5614 | 61.4293 | 61.4469
683.0625 | 123.4039 | -61.4594 | 61.6104 | 0.030283 | -0.035942 | -0.012 | -0.006703 | 0.027109 | -0.010563 | 0.015112 | 61.5737 | 0.16164 | 61.4867 | -0.060575 | 0.016188 | 61.5707 | 0.003143 | 61.3627 | 61.4896 | 61.4234 | 61.4474 | 61.4526 | 61.4865 | 61.4488 | 61.4745 | 123.0331 | 61.621 | 122.946 | 61.3988 | 61.4755 | 123.0301 | 61.4625 | 122.822 | 61.5575 | 61.5706 | 61.4705 | 61.4835
684.0625 | 123.3994 | -61.441 | 61.6196 | 0.025705 | -0.026784 | -0.012 | -0.006703 | 0.027109 | -0.005985 | 0.01969 | 61.5554 | 0.16164 | 61.45 | -0.055996 | 0.016188 | 61.5662 | -0.001436 | 61.3672 | 61.4667 | 61.4143 | 61.429 | 61.4343 | 61.4681 | 61.4351 | 61.4607 | 122.9965 | 61.6027 | 122.8911 | 61.385 | 61.4572 | 123.0072 | 61.4396 | 122.8083 | 61.5392 | 61.5568 | 61.4339 | 61.4515
685.0625 | 123.2849 | -61.4777 | 61.6425 | 0.030283 | -0.040521 | -0.007421 | -0.002124 | 0.040843 | 0.003172 | 0.028846 | 61.5691 | 0.16164 | 61.4729 | -0.055996 | 0.01161 | 61.5707 | 0.003143 | 61.3718 | 61.5079 | 61.4371 | 61.4702 | 61.4755 | 61.5185 | 61.4808 | 61.5065 | 123.0468 | 61.6393 | 122.9506 | 61.4217 | 61.4893 | 123.0484 | 61.4808 | 122.8495 | 61.5575 | 61.566 | 61.4613 | 61.4698
686.0625 | 123.3902 | -61.4639 | 61.6333 | 0.025705 | -0.035942 | -0.007421 | -0.002124 | 0.022531 | -0.001406 | 0.01969 | 61.5554 | 0.16164 | 61.45 | -0.055996 | 0.016188 | 61.5753 | -0.006014 | 61.3718 | 61.4896 | 61.428 | 61.4565 | 61.4618 | 61.4865 | 61.4625 | 61.4836 | 123.0193 | 61.6256 | 122.914 | 61.4079 | 61.4801 | 123.0392 | 61.4579 | 122.8357 | 61.5392 | 61.5614 | 61.4339 | 61.4561
687.0625 | 123.2941 | -61.4548 | 61.6608 | 0.030283 | -0.040521 | -0.012 | 0.002454 | 0.027109 | -0.001406 | 0.01969 | 61.5646 | 0.16164 | 61.4592 | -0.051417 | 0.01161 | 61.5707 | 0.003143 | 61.3627 | 61.4851 | 61.4143 | 61.4428 | 61.4572 | 61.4819 | 61.4534 | 61.4745 | 123.0193 | 61.6164 | 122.914 | 61.4034 | 61.4664 | 123.0255 | 61.4579 | 122.8174 | 61.553 | 61.5614 | 61.4476 | 61.4561
688.0625 | 123.2986 | -61.441 | 61.6058 | 0.016548 | -0.035942 | -0.021157 | 0.002454 | 0.027109 | 0.003172 | 0.024268 | 61.5646 | 0.16622 | 61.4684 | -0.051417 | 0.007032 | 61.5707 | -0.001436 | 61.3672 | 61.4576 | 61.4051 | 61.4199 | 61.4435 | 61.4681 | 61.4442 | 61.4653 | 123.0056 | 61.6073 | 122.9094 | 61.3896 | 61.4481 | 123.0118 | 61.4396 | 122.8083 | 61.5575 | 61.566 | 61.4613 | 61.4698
689.0625 | 123.3948 | -61.441 | 61.6058 | 0.034862 | -0.035942 | -0.016578 | -0.002124 | 0.027109 | -0.005985 | 0.01969 | 61.5508 | 0.15706 | 61.4409 | -0.051417 | 0.01161 | 61.5707 | -0.001436 | 61.3718 | 61.4759 | 61.4051 | 61.4245 | 61.4389 | 61.4681 | 61.4351 | 61.4607 | 122.9919 | 61.5981 | 122.8819 | 61.3896 | 61.4526 | 123.0118 | 61.4396 | 122.8129 | 61.5392 | 61.5523 | 61.4293 | 61.4423
690.0625 | 123.2666 | -61.4777 | 61.647 | 0.025705 | -0.031363 | -0.007421 | 0.002454 | 0.031687 | -0.001406 | 0.024268 | 61.5646 | 0.16622 | 61.4912 | -0.042259 | 0.016188 | 61.5662 | 0.003143 | 61.3672 | 61.5034 | 61.4463 | 61.4702 | 61.4801 | 61.5093 | 61.4763 | 61.5019 | 123.0422 | 61.6439 | 122.9689 | 61.4354 | 61.4938 | 123.0438 | 61.4808 | 122.8449 | 61.5484 | 61.5614 | 61.4751 | 61.4881
691.0625 | 123.381 | -61.4456 | 61.5921 | 0.030283 | -0.035942 | -0.021157 | 0.002454 | 0.022531 | -0.010563 | 0.024268 | 61.56 | 0.16164 | 61.4546 | -0.051417 | 0.016188 | 61.5707 | -0.001436 | 61.3672 | 61.4759 | 61.4097 | 61.4245 | 61.4481 | 61.4681 | 61.4351 | 61.4699 | 123.0056 | 61.6073 | 122.9002 | 61.3942 | 61.4618 | 123.0164 | 61.4442 | 122.8129 | 61.5438 | 61.5614 | 61.4384 | 61.4561
692.0625 | 123.262 | -61.5143 | 61.6425 | 0.030283 | -0.040521 | -0.016578 | 0.002454 | 0.031687 | -0.005985 | 0.024268 | 61.5554 | 0.16622 | 61.4409 | -0.051417 | 0.020767 | 61.5662 | -0.001436 | 61.3718 | 61.5446 | 61.4738 | 61.4977 | 61.5167 | 61.546 | 61.5083 | 61.5386 | 123.0697 | 61.6805 | 122.9552 | 61.4629 | 61.535 | 123.0804 | 61.5128 | 122.8861 | 61.5346 | 61.5568 | 61.4201 | 61.4423
693.0625 | 123.4131 | -61.4365 | 61.5921 | 0.021127 | -0.031363 | -0.016578 | -0.006703 | 0.022531 | -0.001406 | 0.024268 | 61.5691 | 0.17079 | 61.4821 | -0.051417 | 0.020767 | 61.5707 | 0.003143 | 61.3672 | 61.4576 | 61.4051 | 61.4199 | 61.4298 | 61.459 | 61.4351 | 61.4607 | 123.0056 | 61.6073 | 122.9185 | 61.385 | 61.4572 | 123.0072 | 61.4396 | 122.8037 | 61.5484 | 61.566 | 61.4613 | 61.4789
694.0625 | 123.3673 | -61.441 | 61.6104 | 0.025705 | -0.040521 | -0.025735 | 0.002454 | 0.027109 | -0.005985 | 0.024268 | 61.5554 | 0.16622 | 61.45 | -0.055996 | 0.016188 | 61.5753 | 0.007721 | 61.3718 | 61.4667 | 61.4005 | 61.4153 | 61.4435 | 61.4681 | 61.4351 | 61.4653 | 122.9965 | 61.6073 | 122.8911 | 61.385 | 61.4572 | 123.0164 | 61.4488 | 122.8129 | 61.5392 | 61.5477 | 61.4339 | 61.4423
695.0625 | 123.2254 | -61.496 | 61.6516 | 0.025705 | -0.035942 | -0.016578 | 0.007033 | 0.027109 | -0.001406 | 0.024268 | 61.56 | 0.17079 | 61.4409 | -0.051417 | 0.016188 | 61.5707 | 0.003143 | 61.3718 | 61.5217 | 61.46 | 61.4794 | 61.503 | 61.5231 | 61.4946 | 61.5202 | 123.056 | 61.6668 | 122.9369 | 61.4446 | 61.5122 | 123.0667 | 61.4991 | 122.8678 | 61.5438 | 61.5568 | 61.4247 | 61.4377
696.0625 | 123.3307 | -61.496 | 61.5875 | 0.030283 | -0.040521 | -0.012 | -0.002124 | 0.017953 | 0.003172 | 0.028846 | 61.56 | 0.16622 | 61.4958 | -0.055996 | 0.016188 | 61.5753 | 0.003143 | 61.3627 | 61.5263 | 61.4555 | 61.484 | 61.4938 | 61.5139 | 61.4991 | 61.5248 | 123.056 | 61.6622 | 122.9918 | 61.44 | 61.5122 | 123.0713 | 61.4991 | 122.8586 | 61.5438 | 61.5568 | 61.4796 | 61.4927
697.0625 | 123.3719 | -61.4777 | 61.5875 | 0.034862 | -0.040521 | -0.007421 | -0.002124 | 0.022531 | -0.001406 | 0.028846 | 61.5646 | 0.16622 | 61.4455 | -0.042259 | 0.029923 | 61.5707 | 0.007721 | 61.3718 | 61.5125 | 61.4371 | 61.4702 | 61.4755 | 61.5002 | 61.4763 | 61.5065 | 123.0422 | 61.6439 | 122.9231 | 61.4354 | 61.5076 | 123.0484 | 61.4854 | 122.8495 | 61.5346 | 61.5569 | 61.4155 | 61.4377
698.0625 | 123.349 | -61.4639 | 61.6196 | 0.025705 | -0.040521 | -0.016578 | -0.002124 | 0.027109 | -0.010563 | 0.01969 | 61.56 | 0.16622 | 61.4409 | -0.046838 | 0.016188 | 61.5753 | 0.003143 | 61.3672 | 61.4896 | 61.4234 | 61.4474 | 61.4618 | 61.491 | 61.4534 | 61.4836 | 123.0239 | 61.6301 | 122.9048 | 61.4171 | 61.4801 | 123.0392 | 61.4671 | 122.8312 | 61.5438 | 61.5568 | 61.4247 | 61.4377
699.0625 | 123.3856 | -61.4731 | 61.6196 | 0.034862 | -0.049678 | -0.021157 | 0.002454 | 0.022531 | -0.005985 | 0.01969 | 61.5737 | 0.16622 | 61.5004 | -0.051417 | 0.020767 | 61.5799 | 0.007721 | 61.3718 | 61.5079 | 61.4234 | 61.4519 | 61.4755 | 61.4956 | 61.4671 | 61.4928 | 123.0468 | 61.6393 | 122.9735 | 61.4217 | 61.4939 | 123.053 | 61.4808 | 122.8449 | 61.553 | 61.566 | 61.4796 | 61.4927
700.0625 | 123.2712 | -61.4456 | 61.6562 | 0.025705 | -0.040521 | -0.016578 | -0.006703 | 0.031687 | -0.001406 | 0.024268 | 61.5554 | 0.16622 | 61.4546 | -0.046838 | 0.016188 | 61.5707 | 0.007721 | 61.3718 | 61.4713 | 61.4051 | 61.429 | 61.4389 | 61.4773 | 61.4442 | 61.4699 | 123.001 | 61.6118 | 122.9002 | 61.3988 | 61.4618 | 123.0164 | 61.4533 | 122.8174 | 61.5392 | 61.5477 | 61.4384 | 61.4469
701.0625 | 123.3627 | -61.4822 | 61.5967 | 0.030283 | -0.040521 | -0.012 | -0.01586 | 0.022531 | -0.001406 | 0.024268 | 61.5554 | 0.16164 | 61.4592 | -0.046838 | 0.016188 | 61.5707 | 0.012299 | 61.3856 | 61.5125 | 61.4417 | 61.4702 | 61.4664 | 61.5048 | 61.4808 | 61.5065 | 123.0377 | 61.6439 | 122.9414 | 61.4354 | 61.4984 | 123.053 | 61.4945 | 122.8678 | 61.5392 | 61.5431 | 61.443 | 61.4469
702.0625 | 123.2483 | -61.496 | 61.647 | 0.030283 | -0.031363 | -0.021157 | -0.006703 | 0.027109 | 0.003172 | 0.01969 | 61.56 | 0.16164 | 61.4912 | -0.042259 | 0.020767 | 61.5662 | 0.003143 | 61.3856 | 61.5263 | 61.4646 | 61.4748 | 61.4893 | 61.5231 | 61.4991 | 61.5157 | 123.056 | 61.6576 | 122.9872 | 61.4537 | 61.5167 | 123.0621 | 61.4991 | 122.8815 | 61.5392 | 61.5568 | 61.4705 | 61.4881
703.0625 | 123.317 | -61.4639 | 61.6058 | 0.025705 | -0.040521 | -0.016578 | -0.002124 | 0.027109 | 0.003172 | 0.024268 | 61.5554 | 0.16164 | 61.4455 | -0.046838 | 0.016188 | 61.5707 | 0.003143 | 61.3672 | 61.4896 | 61.4234 | 61.4474 | 61.4618 | 61.491 | 61.4671 | 61.4882 | 123.0193 | 61.6256 | 122.9094 | 61.4171 | 61.4801 | 123.0347 | 61.4671 | 122.8312 | 61.5392 | 61.5523 | 61.4293 | 61.4423
704.0625 | 123.3398 | -61.4868 | 61.5921 | 0.030283 | -0.040521 | -0.016578 | -0.006703 | 0.022531 | -0.001406 | 0.024268 | 61.56 | 0.15706 | 61.4546 | -0.055996 | 0.01161 | 61.5753 | 0.003143 | 61.3718 | 61.5171 | 61.4463 | 61.4702 | 61.4801 | 61.5093 | 61.4854 | 61.5111 | 123.0468 | 61.6439 | 122.9414 | 61.4308 | 61.4984 | 123.0621 | 61.49 | 122.8586 | 61.5484 | 61.5568 | 61.443 | 61.4515
705.0625 | 123.3032 | -61.4731 | 61.6013 | 0.030283 | -0.035942 | -0.012 | 0.002454 | 0.022531 | -0.001406 | 0.024268 | 61.5646 | 0.16622 | 61.505 | -0.051417 | 0.01161 | 61.5662 | 0.003143 | 61.381 | 61.5034 | 61.4371 | 61.4611 | 61.4755 | 61.4956 | 61.4717 | 61.4974 | 123.0377 | 61.6393 | 122.9781 | 61.4217 | 61.4847 | 123.0392 | 61.4762 | 122.8541 | 61.553 | 61.5614 | 61.4934 | 61.5018
706.0625 | 123.3627 | -61.4822 | 61.6196 | 0.025705 | -0.035942 | -0.016578 | -0.006703 | 0.027109 | -0.001406 | 0.01969 | 61.56 | 0.17537 | 61.4592 | -0.051417 | 0.016188 | 61.5707 | 0.003143 | 61.3764 | 61.5079 | 61.4463 | 61.4657 | 61.4755 | 61.5093 | 61.4808 | 61.5019 | 123.0422 | 61.6576 | 122.9414 | 61.4308 | 61.4984 | 123.053 | 61.4854 | 122.8586 | 61.5438 | 61.5568 | 61.443 | 61.4561
707.0625 | 123.4909 | -61.4365 | 61.6699 | 0.025705 | -0.031363 | -0.016578 | -0.002124 | 0.017953 | -0.005985 | 0.024268 | 61.56 | 0.17079 | 61.4409 | -0.055996 | 0.016188 | 61.5707 | 0.003143 | 61.3764 | 61.4622 | 61.4051 | 61.4199 | 61.4343 | 61.4544 | 61.4305 | 61.4607 | 122.9965 | 61.6073 | 122.8773 | 61.3805 | 61.4526 | 123.0072 | 61.4396 | 122.8129 | 61.5438 | 61.5568 | 61.4247 | 61.4377
708.0625 | 123.349 | -61.4822 | 61.6058 | 0.025705 | -0.040521 | -0.012 | -0.002124 | 0.017953 | -0.001406 | 0.024268 | 61.56 | 0.16622 | 61.4409 | -0.055996 | 0.01161 | 61.5753 | 0.003143 | 61.3718 | 61.5079 | 61.4417 | 61.4702 | 61.4801 | 61.5002 | 61.4808 | 61.5065 | 123.0422 | 61.6485 | 122.9231 | 61.4262 | 61.4938 | 123.0576 | 61.4854 | 122.8541 | 61.5484 | 61.5568 | 61.4293 | 61.4377
709.0625 | 123.3032 | -61.4594 | 61.6058 | 0.025705 | -0.040521 | -0.007421 | -0.002124 | 0.022531 | -0.005985 | 0.01969 | 61.5646 | 0.16164 | 61.4912 | -0.051417 | 0.016188 | 61.5707 | -0.001436 | 61.3718 | 61.4851 | 61.4188 | 61.4519 | 61.4572 | 61.4819 | 61.4534 | 61.479 | 123.0239 | 61.621 | 122.9506 | 61.4079 | 61.4755 | 123.0301 | 61.4579 | 122.8312 | 61.5484 | 61.566 | 61.4751 | 61.4927
710.0625 | 123.3582 | -61.4914 | 61.5692 | 0.025705 | -0.0451 | -0.021157 | -0.002124 | 0.022531 | -0.001406 | 0.028846 | 61.5646 | 0.16164 | 61.5004 | -0.055996 | 0.016188 | 61.5753 | -0.006014 | 61.3627 | 61.5171 | 61.4463 | 61.4702 | 61.4893 | 61.5139 | 61.49 | 61.5202 | 123.056 | 61.653 | 122.9918 | 61.4354 | 61.5076 | 123.0667 | 61.4854 | 122.8541 | 61.5484 | 61.5706 | 61.4842 | 61.5064
711.0625 | 123.3261 | -61.4868 | 61.5738 | 0.030283 | -0.0451 | -0.007421 | -0.006703 | 0.027109 | -0.005985 | 0.015112 | 61.5508 | 0.16622 | 61.45 | -0.055996 | 0.016188 | 61.5662 | -0.001436 | 61.3718 | 61.5171 | 61.4417 | 61.4794 | 61.4801 | 61.5139 | 61.4808 | 61.5019 | 123.0377 | 61.653 | 122.9369 | 61.4308 | 61.503 | 123.053 | 61.4854 | 122.8586 | 61.5346 | 61.5523 | 61.4339 | 61.4515
712.0625 | 123.3673 | -61.4868 | 61.5692 | 0.034862 | -0.035942 | -0.012 | -0.006703 | 0.027109 | -0.001406 | 0.024268 | 61.56 | 0.16622 | 61.4409 | -0.046838 | 0.025345 | 61.5662 | -0.006014 | 61.3718 | 61.5217 | 61.4509 | 61.4748 | 61.4801 | 61.5139 | 61.4854 | 61.5111 | 123.0468 | 61.653 | 122.9277 | 61.44 | 61.5122 | 123.053 | 61.4808 | 122.8586 | 61.5346 | 61.566 | 61.4155 | 61.4469
713.0625 | 123.3307 | -61.4639 | 61.5967 | 0.034862 | -0.0451 | -0.016578 | -0.002124 | 0.022531 | -0.001406 | 0.01969 | 61.56 | 0.16622 | 61.4729 | -0.051417 | 0.01161 | 61.5616 | 0.007721 | 61.3718 | 61.4988 | 61.4188 | 61.4474 | 61.4618 | 61.4865 | 61.4625 | 61.4836 | 123.0239 | 61.6301 | 122.9369 | 61.4125 | 61.4755 | 123.0255 | 61.4716 | 122.8357 | 61.5484 | 61.5523 | 61.4613 | 61.4652
714.0625 | 123.349 | -61.4594 | 61.5829 | 0.034862 | -0.040521 | -0.016578 | 0.002454 | 0.022531 | 0.003172 | 0.024268 | 61.56 | 0.16164 | 61.4821 | -0.046838 | 0.020767 | 61.5662 | 0.007721 | 61.3718 | 61.4942 | 61.4188 | 61.4428 | 61.4618 | 61.4819 | 61.4625 | 61.4836 | 123.0193 | 61.621 | 122.9414 | 61.4125 | 61.4801 | 123.0255 | 61.4671 | 122.8312 | 61.5392 | 61.5523 | 61.4613 | 61.4744
715.0625 | 123.4039 | -61.4456 | 61.5967 | 0.030283 | -0.040521 | -0.016578 | 0.002454 | 0.022531 | -0.005985 | 0.01969 | 61.5646 | 0.17995 | 61.45 | -0.051417 | 0.016188 | 61.5753 | -0.001436 | 61.3718 | 61.4759 | 61.4051 | 61.429 | 61.4481 | 61.4681 | 61.4396 | 61.4653 | 123.0102 | 61.6256 | 122.8957 | 61.3942 | 61.4618 | 123.0209 | 61.4442 | 122.8174 | 61.5484 | 61.566 | 61.4339 | 61.4515
716.0625 | 123.349 | -61.4594 | 61.5921 | 0.030283 | -0.035942 | -0.007421 | 0.002454 | 0.022531 | -0.010563 | 0.024268 | 61.56 | 0.17079 | 61.4317 | -0.046838 | 0.016188 | 61.5707 | 0.003143 | 61.3672 | 61.4896 | 61.4234 | 61.4519 | 61.4618 | 61.4819 | 61.4488 | 61.4836 | 123.0193 | 61.6301 | 122.8911 | 61.4125 | 61.4755 | 123.0301 | 61.4625 | 122.8266 | 61.5438 | 61.5568 | 61.4155 | 61.4286
717.0625 | 123.3856 | -61.4731 | 61.5784 | 0.030283 | -0.040521 | -0.021157 | -0.002124 | 0.022531 | -0.001406 | 0.01969 | 61.5691 | 0.17079 | 61.4775 | -0.051417 | 0.01161 | 61.5707 | -0.001436 | 61.3718 | 61.5034 | 61.4326 | 61.4519 | 61.471 | 61.4956 | 61.4717 | 61.4928 | 123.0422 | 61.6439 | 122.9506 | 61.4217 | 61.4847 | 123.0438 | 61.4716 | 122.8449 | 61.5575 | 61.5706 | 61.4659 | 61.4789
718.0625 | 123.3261 | -61.4685 | 61.5967 | 0.025705 | -0.0451 | -0.012 | -0.006703 | 0.027109 | 0.003172 | 0.033424 | 61.56 | 0.16164 | 61.4592 | -0.055996 | 0.01161 | 61.5753 | 0.007721 | 61.3764 | 61.4942 | 61.4234 | 61.4565 | 61.4618 | 61.4956 | 61.4717 | 61.5019 | 123.0285 | 61.6301 | 122.9277 | 61.4125 | 61.4801 | 123.0438 | 61.4762 | 122.8449 | 61.5484 | 61.5523 | 61.4476 | 61.4515
719.0625 | 123.317 | -61.4822 | 61.5967 | 0.030283 | -0.0451 | -0.016578 | -0.006703 | 0.022531 | -0.005985 | 0.024268 | 61.56 | 0.16622 | 61.4363 | -0.051417 | 0.01161 | 61.5753 | -0.006014 | 61.3764 | 61.5125 | 61.4371 | 61.4657 | 61.4755 | 61.5048 | 61.4763 | 61.5065 | 123.0422 | 61.6485 | 122.9185 | 61.4308 | 61.4938 | 123.0576 | 61.4762 | 122.8586 | 61.5484 | 61.566 | 61.4247 | 61.4423
720.0625 | 123.3353 | -61.4639 | 61.5692 | 0.025705 | -0.040521 | -0.012 | -0.002124 | 0.027109 | -0.001406 | 0.033424 | 61.5646 | 0.16622 | 61.4867 | -0.055996 | 0.01161 | 61.5707 | 0.003143 | 61.3672 | 61.4896 | 61.4234 | 61.4519 | 61.4618 | 61.491 | 61.4625 | 61.4974 | 123.0285 | 61.6301 | 122.9506 | 61.4079 | 61.4755 | 123.0347 | 61.4671 | 122.8312 | 61.553 | 61.5614 | 61.4751 | 61.4835
721.0625 | 123.3948 | -61.4456 | 61.5692 | 0.030283 | -0.035942 | -0.007421 | 0.002454 | 0.022531 | 0.003172 | 0.024268 | 61.56 | 0.17079 | 61.4592 | -0.051417 | 0.020767 | 61.5753 | -0.001436 | 61.3764 | 61.4759 | 61.4097 | 61.4382 | 61.4481 | 61.4681 | 61.4488 | 61.4699 | 123.0056 | 61.6164 | 122.9048 | 61.3942 | 61.4664 | 123.0209 | 61.4442 | 122.822 | 61.5392 | 61.5614 | 61.4384 | 61.4606
722.0625 | 123.3444 | -61.4685 | 61.5509 | 0.030283 | -0.035942 | -0.016578 | 0.002454 | 0.022531 | -0.001406 | 0.01969 | 61.56 | 0.16164 | 61.4409 | -0.046838 | 0.016188 | 61.5707 | 0.003143 | 61.3672 | 61.4988 | 61.4326 | 61.4519 | 61.471 | 61.491 | 61.4671 | 61.4882 | 123.0285 | 61.6301 | 122.9094 | 61.4217 | 61.4847 | 123.0392 | 61.4716 | 122.8357 | 61.5438 | 61.5568 | 61.4247 | 61.4377
723.0625 | 123.381 | -61.4548 | 61.5738 | 0.030283 | -0.040521 | -0.021157 | -0.006703 | 0.022531 | -0.001406 | 0.028846 | 61.5691 | 0.16622 | 61.505 | -0.046838 | 0.01161 | 61.5662 | -0.006014 | 61.3718 | 61.4851 | 61.4143 | 61.4336 | 61.4481 | 61.4773 | 61.4534 | 61.4836 | 123.0239 | 61.621 | 122.9598 | 61.4079 | 61.4664 | 123.0209 | 61.4488 | 122.8266 | 61.5575 | 61.5752 | 61.4934 | 61.511
724.0625 | 123.2666 | -61.4822 | 61.6058 | 0.030283 | -0.035942 | -0.012 | -0.006703 | 0.022531 | 0.003172 | 0.033424 | 61.56 | 0.16622 | 61.45 | -0.051417 | 0.016188 | 61.5707 | 0.003143 | 61.3718 | 61.5125 | 61.4463 | 61.4702 | 61.4755 | 61.5048 | 61.4854 | 61.5157 | 123.0422 | 61.6485 | 122.9323 | 61.4308 | 61.4984 | 123.053 | 61.4854 | 122.8541 | 61.5438 | 61.5568 | 61.4339 | 61.4469
725.0625 | 123.2071 | -61.5097 | 61.647 | 0.034862 | -0.035942 | -0.007421 | -0.002124 | 0.027109 | -0.001406 | 0.024268 | 61.5646 | 0.16622 | 61.4409 | -0.051417 | 0.016188 | 61.5753 | -0.001436 | 61.3764 | 61.5446 | 61.4738 | 61.5023 | 61.5076 | 61.5368 | 61.5083 | 61.534 | 123.0743 | 61.6759 | 122.9506 | 61.4583 | 61.5259 | 123.085 | 61.5083 | 122.8861 | 61.5484 | 61.566 | 61.4247 | 61.4423
726.0625 | 123.2849 | -61.4685 | 61.6333 | 0.030283 | -0.040521 | -0.007421 | 0.007033 | 0.031687 | -0.001406 | 0.01969 | 61.5646 | 0.16164 | 61.4409 | -0.046838 | 0.020767 | 61.5662 | 0.003143 | 61.3718 | 61.4988 | 61.428 | 61.4611 | 61.4755 | 61.5002 | 61.4671 | 61.4882 | 123.0331 | 61.6301 | 122.9094 | 61.4217 | 61.4893 | 123.0347 | 61.4716 | 122.8403 | 61.5438 | 61.5614 | 61.4201 | 61.4377
727.0625 | 123.3444 | -61.4731 | 61.5967 | 0.030283 | -0.0451 | -0.012 | -0.002124 | 0.031687 | -0.001406 | 0.028846 | 61.56 | 0.17537 | 61.4821 | -0.051417 | 0.016188 | 61.5707 | 0.007721 | 61.3672 | 61.5034 | 61.428 | 61.4611 | 61.471 | 61.5048 | 61.4717 | 61.5019 | 123.0331 | 61.6485 | 122.9552 | 61.4217 | 61.4893 | 123.0438 | 61.4808 | 122.8403 | 61.5438 | 61.5523 | 61.4659 | 61.4744
728.0625 | 123.2574 | -61.4777 | 61.6425 | 0.034862 | -0.031363 | -0.021157 | 0.002454 | 0.022531 | -0.001406 | 0.028846 | 61.5646 | 0.16622 | 61.5004 | -0.055996 | 0.01161 | 61.5753 | -0.001436 | 61.3718 | 61.5125 | 61.4463 | 61.4565 | 61.4801 | 61.5002 | 61.4763 | 61.5065 | 123.0422 | 61.6439 | 122.9781 | 61.4217 | 61.4893 | 123.053 | 61.4762 | 122.8495 | 61.553 | 61.566 | 61.4888 | 61.5018
729.0625 | 123.2483 | -61.4777 | 61.6333 | 0.034862 | -0.035942 | -0.007421 | 0.002454 | 0.031687 | 0.003172 | 0.028846 | 61.56 | 0.16164 | 61.4455 | -0.051417 | 0.01161 | 61.5799 | 0.003143 | 61.3718 | 61.5125 | 61.4417 | 61.4702 | 61.4801 | 61.5093 | 61.4808 | 61.5065 | 123.0377 | 61.6393 | 122.9231 | 61.4262 | 61.4893 | 123.0576 | 61.4808 | 122.8495 | 61.5484 | 61.5568 | 61.4339 | 61.4423
730.0625 | 123.3032 | -61.4914 | 61.6379 | 0.030283 | -0.0451 | -0.016578 | 0.007033 | 0.036265 | -0.001406 | 0.01969 | 61.5554 | 0.16622 | 61.4409 | -0.046838 | 0.020767 | 61.5753 | -0.001436 | 61.3718 | 61.5217 | 61.4463 | 61.4748 | 61.4984 | 61.5277 | 61.49 | 61.5111 | 123.0468 | 61.6576 | 122.9323 | 61.4446 | 61.5122 | 123.0667 | 61.49 | 122.8632 | 61.5346 | 61.5568 | 61.4201 | 61.4423
731.0625 | 123.3124 | -61.4777 | 61.6425 | 0.034862 | -0.031363 | -0.016578 | -0.002124 | 0.027109 | -0.010563 | 0.033424 | 61.5691 | 0.16622 | 61.4638 | -0.046838 | 0.016188 | 61.5799 | -0.001436 | 61.3718 | 61.5125 | 61.4463 | 61.4611 | 61.4755 | 61.5048 | 61.4671 | 61.5111 | 123.0468 | 61.6439 | 122.9414 | 61.4308 | 61.4938 | 123.0576 | 61.4762 | 122.8495 | 61.553 | 61.5706 | 61.4476 | 61.4652
732.0625 | 123.2986 | -61.4822 | 61.6287 | 0.030283 | -0.040521 | -0.016578 | -0.006703 | 0.031687 | -0.001406 | 0.01969 | 61.5691 | 0.16622 | 61.5004 | -0.051417 | 0.020767 | 61.5753 | 0.003143 | 61.3718 | 61.5125 | 61.4417 | 61.4657 | 61.4755 | 61.5139 | 61.4808 | 61.5019 | 123.0514 | 61.6485 | 122.9826 | 61.4308 | 61.503 | 123.0576 | 61.4854 | 122.8541 | 61.5484 | 61.566 | 61.4796 | 61.4973
733.0625 | 123.2986 | -61.4777 | 61.6516 | 0.034862 | -0.040521 | -0.016578 | -0.002124 | 0.017953 | 0.003172 | 0.028846 | 61.5646 | 0.16164 | 61.4684 | -0.055996 | 0.016188 | 61.5753 | -0.001436 | 61.3764 | 61.5125 | 61.4371 | 61.4611 | 61.4755 | 61.4956 | 61.4808 | 61.5065 | 123.0422 | 61.6393 | 122.946 | 61.4217 | 61.4938 | 123.053 | 61.4762 | 122.8541 | 61.5484 | 61.566 | 61.4522 | 61.4698
734.0625 | 123.3261 | -61.4685 | 61.647 | 0.030283 | -0.040521 | -0.016578 | 0.002454 | 0.027109 | -0.010563 | 0.01969 | 61.5646 | 0.16622 | 61.4409 | -0.046838 | 0.025345 | 61.5707 | 0.003143 | 61.3764 | 61.4988 | 61.428 | 61.4519 | 61.471 | 61.4956 | 61.4579 | 61.4882 | 123.0331 | 61.6347 | 122.9094 | 61.4217 | 61.4939 | 123.0392 | 61.4716 | 122.8449 | 61.5392 | 61.5614 | 61.4155 | 61.4377
735.0625 | 123.2986 | -61.4685 | 61.6379 | 0.034862 | -0.040521 | -0.016578 | -0.002124 | 0.027109 | -0.001406 | 0.01969 | 61.5691 | 0.17079 | 61.45 | -0.055996 | 0.020767 | 61.5753 | 0.003143 | 61.3718 | 61.5034 | 61.428 | 61.4519 | 61.4664 | 61.4956 | 61.4671 | 61.4882 | 123.0377 | 61.6393 | 122.9185 | 61.4125 | 61.4893 | 123.0438 | 61.4716 | 122.8403 | 61.5484 | 61.566 | 61.4293 | 61.4469
736.0625 | 123.2986 | -61.5005 | 61.6791 | 0.030283 | -0.040521 | -0.002842 | 0.007033 | 0.027109 | -0.001406 | 0.028846 | 61.5737 | 0.17079 | 61.4958 | -0.055996 | 0.016188 | 61.5753 | -0.001436 | 61.3764 | 61.5308 | 61.46 | 61.4977 | 61.5076 | 61.5277 | 61.4991 | 61.5294 | 123.0743 | 61.6713 | 122.9964 | 61.4446 | 61.5167 | 123.0759 | 61.4991 | 122.8769 | 61.5575 | 61.5752 | 61.4796 | 61.4973
737.0625 | 123.3124 | -61.5097 | 61.6196 | 0.030283 | -0.035942 | -0.012 | 0.002454 | 0.027109 | -0.001406 | 0.028846 | 61.5646 | 0.16164 | 61.4912 | -0.051417 | 0.01161 | 61.5707 | -0.010593 | 61.3672 | 61.54 | 61.4738 | 61.4977 | 61.5122 | 61.5368 | 61.5083 | 61.5386 | 123.0743 | 61.6713 | 123.0009 | 61.4583 | 61.5213 | 123.0804 | 61.4991 | 122.8769 | 61.553 | 61.5752 | 61.4796 | 61.5018
738.0625 | 123.2437 | -61.528 | 61.6379 | 0.025705 | -0.040521 | -0.007421 | -0.006703 | 0.022531 | -0.005985 | 0.024268 | 61.56 | 0.16164 | 61.45 | -0.051417 | 0.016188 | 61.5662 | 0.003143 | 61.3764 | 61.5537 | 61.4875 | 61.5206 | 61.5213 | 61.5505 | 61.522 | 61.5523 | 123.088 | 61.6897 | 122.9781 | 61.4766 | 61.5442 | 123.0942 | 61.5312 | 122.9044 | 61.5438 | 61.5568 | 61.4339 | 61.4469
739.0625 | 123.3078 | -61.4639 | 61.6379 | 0.030283 | -0.035942 | -0.012 | -0.002124 | 0.031687 | -0.005985 | 0.024268 | 61.5691 | 0.16622 | 61.4455 | -0.046838 | 0.016188 | 61.5707 | 0.003143 | 61.3672 | 61.4942 | 61.428 | 61.4519 | 61.4618 | 61.4956 | 61.4579 | 61.4882 | 123.0331 | 61.6301 | 122.9094 | 61.4171 | 61.4801 | 123.0347 | 61.4671 | 122.8312 | 61.553 | 61.566 | 61.4293 | 61.4423
740.0625 | 123.2529 | -61.4731 | 61.6516 | 0.025705 | -0.040521 | -0.016578 | -0.011281 | 0.031687 | -0.001406 | 0.028846 | 61.5691 | 0.16622 | 61.4912 | -0.051417 | 0.016188 | 61.5753 | 0.007721 | 61.3718 | 61.4988 | 61.4326 | 61.4565 | 61.4618 | 61.5048 | 61.4717 | 61.5019 | 123.0422 | 61.6393 | 122.9643 | 61.4217 | 61.4893 | 123.0484 | 61.4808 | 122.8449 | 61.553 | 61.5614 | 61.4751 | 61.4835
741.0625 | 123.3124 | -61.4639 | 61.6379 | 0.030283 | -0.040521 | -0.016578 | 0.002454 | 0.031687 | -0.005985 | 0.024268 | 61.5646 | 0.16164 | 61.4958 | -0.055996 | 0.016188 | 61.5753 | 0.003143 | 61.3718 | 61.4942 | 61.4234 | 61.4474 | 61.4664 | 61.4956 | 61.4579 | 61.4882 | 123.0285 | 61.6256 | 122.9598 | 61.4079 | 61.4801 | 123.0392 | 61.4671 | 122.8357 | 61.5484 | 61.5614 | 61.4796 | 61.4927
742.0625 | 123.3032 | -61.4731 | 61.6333 | 0.030283 | -0.040521 | -0.007421 | -0.002124 | 0.031687 | -0.001406 | 0.024268 | 61.5646 | 0.16622 | 61.4592 | -0.060575 | 0.020767 | 61.5753 | 0.003143 | 61.3672 | 61.5034 | 61.4326 | 61.4657 | 61.471 | 61.5048 | 61.4717 | 61.4974 | 123.0377 | 61.6393 | 122.9323 | 61.4125 | 61.4939 | 123.0484 | 61.4762 | 122.8403 | 61.5438 | 61.5614 | 61.4384 | 61.4561
743.0625 | 123.2941 | -61.5005 | 61.6562 | 0.021127 | -0.031363 | -0.012 | 0.002454 | 0.027109 | 0.003172 | 0.028846 | 61.5646 | 0.16164 | 61.4455 | -0.055996 | 0.020767 | 61.5662 | 0.003143 | 61.3718 | 61.5217 | 61.4692 | 61.4885 | 61.503 | 61.5277 | 61.5037 | 61.5294 | 123.0651 | 61.6622 | 122.946 | 61.4446 | 61.5213 | 123.0667 | 61.5037 | 122.8724 | 61.5438 | 61.5614 | 61.4247 | 61.4423
744.0625 | 123.2391 | -61.4685 | 61.6699 | 0.025705 | -0.040521 | -0.021157 | -0.006703 | 0.027109 | -0.005985 | 0.01969 | 61.5691 | 0.16622 | 61.4592 | -0.055996 | 0.016188 | 61.5707 | 0.003143 | 61.3718 | 61.4942 | 61.428 | 61.4473 | 61.4618 | 61.4956 | 61.4625 | 61.4882 | 123.0377 | 61.6347 | 122.9277 | 61.4125 | 61.4847 | 123.0392 | 61.4716 | 122.8403 | 61.553 | 61.566 | 61.443 | 61.4561
745.0625 | 123.2483 | -61.4777 | 61.6425 | 0.030283 | -0.035942 | -0.012 | -0.002124 | 0.031687 | -0.001406 | 0.028846 | 61.5691 | 0.15706 | 61.4821 | -0.046838 | 0.025345 | 61.5707 | 0.007721 | 61.3764 | 61.5079 | 61.4417 | 61.4657 | 61.4755 | 61.5093 | 61.4763 | 61.5065 | 123.0468 | 61.6347 | 122.9597 | 61.4308 | 61.503 | 123.0484 | 61.4854 | 122.8541 | 61.5438 | 61.5614 | 61.4567 | 61.4744
746.0625 | 123.2437 | -61.4777 | 61.6562 | 0.030283 | -0.040521 | -0.016578 | -0.002124 | 0.027109 | -0.001406 | 0.024268 | 61.5646 | 0.16164 | 61.4592 | -0.051417 | 0.020767 | 61.5662 | 0.003143 | 61.3672 | 61.5079 | 61.4371 | 61.4611 | 61.4755 | 61.5048 | 61.4763 | 61.5019 | 123.0422 | 61.6393 | 122.9369 | 61.4262 | 61.4984 | 123.0438 | 61.4808 | 122.8449 | 61.5438 | 61.5614 | 61.4384 | 61.4561
747.0625 | 123.2666 | -61.4548 | 61.6425 | 0.030283 | -0.035942 | -0.007421 | 0.002454 | 0.031687 | -0.005985 | 0.01969 | 61.56 | 0.17079 | 61.4455 | -0.051417 | 0.01161 | 61.5707 | 0.003143 | 61.3627 | 61.4851 | 61.4188 | 61.4474 | 61.4572 | 61.4865 | 61.4488 | 61.4745 | 123.0148 | 61.6256 | 122.9002 | 61.4034 | 61.4664 | 123.0255 | 61.4579 | 122.8174 | 61.5484 | 61.5568 | 61.4339 | 61.4423
748.0625 | 123.2437 | -61.4822 | 61.6562 | 0.025705 | -0.040521 | -0.012 | 0.002454 | 0.022531 | -0.001406 | 0.028846 | 61.5646 | 0.16622 | 61.4638 | -0.055996 | 0.020767 | 61.5662 | -0.001436 | 61.3764 | 61.5079 | 61.4417 | 61.4702 | 61.4847 | 61.5048 | 61.4808 | 61.5111 | 123.0468 | 61.6485 | 122.946 | 61.4262 | 61.503 | 123.0484 | 61.4808 | 122.8586 | 61.5438 | 61.566 | 61.443 | 61.4652
749.0625 | 123.2437 | -61.4731 | 61.6974 | 0.025705 | -0.0451 | -0.016578 | -0.002124 | 0.027109 | -0.010563 | 0.028846 | 61.5783 | 0.16622 | 61.5004 | -0.051417 | 0.01161 | 61.5707 | 0.003143 | 61.3672 | 61.4988 | 61.428 | 61.4565 | 61.471 | 61.5002 | 61.4625 | 61.5019 | 123.0514 | 61.6393 | 122.9735 | 61.4217 | 61.4847 | 123.0438 | 61.4762 | 122.8403 | 61.5667 | 61.5752 | 61.4888 | 61.4973
750.0625 | 123.2849 | -61.4731 | 61.6699 | 0.021127 | -0.040521 | -0.012 | -0.002124 | 0.031687 | 0.003172 | 0.024268 | 61.5646 | 0.16622 | 61.4867 | -0.055996 | 0.025345 | 61.5662 | 0.003143 | 61.3764 | 61.4942 | 61.4326 | 61.4611 | 61.471 | 61.5048 | 61.4763 | 61.4974 | 123.0377 | 61.6393 | 122.9597 | 61.4171 | 61.4984 | 123.0392 | 61.4762 | 122.8495 | 61.5392 | 61.5614 | 61.4613 | 61.4835
751.0625 | 123.3124 | -61.4594 | 61.6333 | 0.025705 | -0.040521 | -0.016578 | -0.002124 | 0.027109 | -0.005985 | 0.01969 | 61.56 | 0.17079 | 61.45 | -0.051417 | 0.016188 | 61.5753 | 0.003143 | 61.3718 | 61.4851 | 61.4188 | 61.4428 | 61.4572 | 61.4865 | 61.4534 | 61.479 | 123.0193 | 61.6301 | 122.9094 | 61.4079 | 61.4755 | 123.0347 | 61.4625 | 122.8312 | 61.5438 | 61.5568 | 61.4339 | 61.4469
752.0625 | 123.3582 | -61.4456 | 61.6425 | 0.030283 | -0.040521 | -0.025735 | -0.002124 | 0.027109 | 0.00775 | 0.024268 | 61.5691 | 0.16164 | 61.45 | -0.051417 | 0.016188 | 61.5753 | 0.007721 | 61.3672 | 61.4759 | 61.4051 | 61.4199 | 61.4435 | 61.4727 | 61.4534 | 61.4699 | 123.0148 | 61.6073 | 122.8957 | 61.3942 | 61.4618 | 123.0209 | 61.4533 | 122.8129 | 61.553 | 61.5614 | 61.4339 | 61.4423
753.0625 | 123.2666 | -61.4639 | 61.6379 | 0.034862 | -0.040521 | -0.021157 | -0.002124 | 0.027109 | -0.001406 | 0.01969 | 61.5691 | 0.17079 | 61.4912 | -0.060575 | 0.020767 | 61.5707 | 0.003143 | 61.3764 | 61.4988 | 61.4234 | 61.4428 | 61.4618 | 61.491 | 61.4625 | 61.4836 | 123.0331 | 61.6347 | 122.9552 | 61.4034 | 61.4847 | 123.0347 | 61.4671 | 122.8403 | 61.5484 | 61.566 | 61.4705 | 61.4881
754.0625 | 123.3627 | -61.4594 | 61.6241 | 0.025705 | -0.035942 | -0.007421 | 0.002454 | 0.027109 | -0.001406 | 0.01969 | 61.5691 | 0.16622 | 61.4958 | -0.055996 | 0.020767 | 61.5662 | -0.001436 | 61.3764 | 61.4851 | 61.4234 | 61.4519 | 61.4618 | 61.4865 | 61.4579 | 61.479 | 123.0285 | 61.6256 | 122.9552 | 61.4034 | 61.4801 | 123.0255 | 61.4579 | 122.8357 | 61.5484 | 61.5706 | 61.4751 | 61.4973
755.0625 | 123.262 | -61.4914 | 61.6287 | 0.021127 | -0.0451 | -0.012 | 0.002454 | 0.027109 | -0.005985 | 0.024268 | 61.5691 | 0.16164 | 61.4546 | -0.051417 | 0.016188 | 61.5707 | -0.001436 | 61.381 | 61.5125 | 61.4463 | 61.4794 | 61.4938 | 61.5185 | 61.4854 | 61.5157 | 123.0605 | 61.653 | 122.946 | 61.44 | 61.5076 | 123.0621 | 61.49 | 122.8724 | 61.553 | 61.5706 | 61.4384 | 61.4561
756.0625 | 123.3215 | -61.4639 | 61.6699 | 0.025705 | -0.040521 | -0.016578 | 0.007033 | 0.022531 | -0.001406 | 0.01969 | 61.5646 | 0.17079 | 61.45 | -0.055996 | 0.025345 | 61.5707 | 0.012299 | 61.3764 | 61.4896 | 61.4234 | 61.4474 | 61.471 | 61.4865 | 61.4625 | 61.4836 | 123.0285 | 61.6347 | 122.914 | 61.4079 | 61.4893 | 123.0347 | 61.4762 | 122.8403 | 61.5392 | 61.5523 | 61.4247 | 61.4377
757.0625 | 123.2849 | -61.4548 | 61.6653 | 0.025705 | -0.035942 | -0.007421 | -0.006703 | 0.022531 | -0.005985 | 0.01969 | 61.5737 | 0.16622 | 61.4729 | -0.051417 | 0.020767 | 61.5662 | -0.001436 | 61.3718 | 61.4805 | 61.4188 | 61.4474 | 61.4481 | 61.4773 | 61.4488 | 61.4745 | 123.0285 | 61.621 | 122.9277 | 61.4034 | 61.4755 | 123.0209 | 61.4533 | 122.8266 | 61.553 | 61.5752 | 61.4522 | 61.4744
758.0625 | 123.3444 | -61.4456 | 61.6241 | 0.025705 | -0.035942 | -0.021157 | -0.011281 | 0.027109 | -0.001406 | 0.024268 | 61.5646 | 0.16622 | 61.4958 | -0.046838 | 0.016188 | 61.5799 | 0.007721 | 61.3718 | 61.4713 | 61.4097 | 61.4245 | 61.4343 | 61.4727 | 61.4442 | 61.4699 | 123.0102 | 61.6118 | 122.9414 | 61.3988 | 61.4618 | 123.0255 | 61.4533 | 122.8174 | 61.5484 | 61.5569 | 61.4796 | 61.4881
759.0625 | 123.4085 | -61.4685 | 61.6333 | 0.025705 | -0.0451 | -0.012 | 0.002454 | 0.022531 | -0.001406 | 0.01969 | 61.5646 | 0.17537 | 61.4638 | -0.055996 | 0.016188 | 61.5753 | 0.007721 | 61.381 | 61.4942 | 61.4234 | 61.4565 | 61.471 | 61.491 | 61.4671 | 61.4882 | 123.0331 | 61.6439 | 122.9323 | 61.4125 | 61.4847 | 123.0438 | 61.4762 | 122.8495 | 61.5484 | 61.5569 | 61.4476 | 61.4561
760.0625 | 123.3994 | -61.4822 | 61.6013 | 0.025705 | -0.040521 | -0.012 | -0.006703 | 0.031687 | -0.005985 | 0.01969 | 61.5646 | 0.16622 | 61.45 | -0.055996 | 0.020767 | 61.5662 | 0.007721 | 61.3764 | 61.5079 | 61.4417 | 61.4702 | 61.4755 | 61.5139 | 61.4763 | 61.5019 | 123.0468 | 61.6485 | 122.9323 | 61.4262 | 61.503 | 123.0484 | 61.49 | 122.8586 | 61.5438 | 61.5569 | 61.4293 | 61.4423
761.0625 | 123.4039 | -61.4456 | 61.6196 | 0.025705 | -0.035942 | -0.016578 | 0.007033 | 0.022531 | -0.001406 | 0.028846 | 61.56 | 0.17537 | 61.4546 | -0.046838 | 0.016188 | 61.5707 | 0.007721 | 61.381 | 61.4713 | 61.4097 | 61.429 | 61.4527 | 61.4681 | 61.4442 | 61.4745 | 123.0056 | 61.621 | 122.9002 | 61.3988 | 61.4618 | 123.0164 | 61.4533 | 122.8266 | 61.5438 | 61.5523 | 61.4384 | 61.4469
762.0625 | 123.2391 | -61.4685 | 61.6287 | 0.034862 | -0.035942 | -0.012 | 0.002454 | 0.031687 | -0.005985 | 0.033424 | 61.5691 | 0.17079 | 61.5096 | -0.051417 | 0.01161 | 61.5753 | -0.001436 | 61.3764 | 61.5034 | 61.4326 | 61.4565 | 61.471 | 61.5002 | 61.4625 | 61.5019 | 123.0377 | 61.6393 | 122.9781 | 61.4171 | 61.4801 | 123.0438 | 61.4671 | 122.8449 | 61.5575 | 61.5706 | 61.4979 | 61.511
763.0625 | 123.3627 | -61.4731 | 61.6104 | 0.034862 | -0.035942 | -0.012 | -0.002124 | 0.017953 | -0.001406 | 0.01969 | 61.5691 | 0.17079 | 61.4867 | -0.046838 | 0.025345 | 61.5662 | 0.007721 | 61.3764 | 61.5079 | 61.4371 | 61.4611 | 61.471 | 61.491 | 61.4717 | 61.4928 | 123.0422 | 61.6439 | 122.9597 | 61.4262 | 61.4984 | 123.0392 | 61.4808 | 122.8495 | 61.5438 | 61.5614 | 61.4613 | 61.4789
764.0625 | 123.3673 | -61.4456 | 61.6196 | 0.025705 | -0.040521 | -0.016578 | -0.011281 | 0.027109 | 0.003172 | 0.028846 | 61.5646 | 0.16622 | 61.45 | -0.051417 | 0.025345 | 61.5662 | 0.003143 | 61.381 | 61.4713 | 61.4051 | 61.429 | 61.4343 | 61.4727 | 61.4488 | 61.4745 | 123.0102 | 61.6118 | 122.8957 | 61.3942 | 61.471 | 123.0118 | 61.4488 | 122.8266 | 61.5392 | 61.5614 | 61.4247 | 61.4469
765.0625 | 123.3902 | -61.4685 | 61.5921 | 0.021127 | -0.040521 | -0.016578 | -0.002124 | 0.027109 | -0.001406 | 0.024268 | 61.5691 | 0.17079 | 61.45 | -0.046838 | 0.016188 | 61.5662 | 0.007721 | 61.3764 | 61.4896 | 61.428 | 61.4519 | 61.4664 | 61.4956 | 61.4671 | 61.4928 | 123.0377 | 61.6393 | 122.9185 | 61.4217 | 61.4847 | 123.0347 | 61.4762 | 122.8449 | 61.553 | 61.5614 | 61.4339 | 61.4423
766.0625 | 123.3582 | -61.4548 | 61.6058 | 0.034862 | -0.035942 | -0.016578 | -0.002124 | 0.027109 | -0.001406 | 0.01969 | 61.5646 | 0.17079 | 61.4775 | -0.046838 | 0.01161 | 61.5707 | 0.003143 | 61.3718 | 61.4896 | 61.4188 | 61.4382 | 61.4526 | 61.4819 | 61.4534 | 61.4745 | 123.0193 | 61.6256 | 122.9323 | 61.4079 | 61.4664 | 123.0255 | 61.4579 | 122.8266 | 61.553 | 61.5614 | 61.4659 | 61.4744
767.0625 | 123.3032 | -61.4639 | 61.702 | 0.034862 | -0.035942 | -0.012 | 0.007033 | 0.031687 | -0.001406 | 0.028846 | 61.5646 | 0.16164 | 61.505 | -0.042259 | 0.020767 | 61.5662 | 0.007721 | 61.3764 | 61.4988 | 61.428 | 61.4519 | 61.471 | 61.4956 | 61.4625 | 61.4928 | 123.0285 | 61.6256 | 122.9689 | 61.4217 | 61.4847 | 123.0301 | 61.4716 | 122.8403 | 61.5438 | 61.5569 | 61.4842 | 61.4973
768.0625 | 123.3307 | -61.4685 | 61.615 | 0.030283 | -0.040521 | -0.021157 | 0.002454 | 0.022531 | -0.005985 | 0.015112 | 61.56 | 0.16164 | 61.45 | -0.055996 | 0.016188 | 61.5753 | -0.001436 | 61.3718 | 61.4988 | 61.428 | 61.4473 | 61.471 | 61.491 | 61.4625 | 61.4836 | 123.0285 | 61.6301 | 122.9185 | 61.4125 | 61.4847 | 123.0438 | 61.4671 | 122.8403 | 61.5438 | 61.5614 | 61.4339 | 61.4515
769.0625 | 123.4177 | -61.4456 | 61.5875 | 0.025705 | -0.049678 | -0.007421 | -0.006703 | 0.022531 | -0.001406 | 0.024268 | 61.56 | 0.16622 | 61.4409 | -0.046838 | 0.025345 | 61.5707 | 0.003143 | 61.3672 | 61.4713 | 61.3959 | 61.4382 | 61.4389 | 61.4681 | 61.4442 | 61.4699 | 123.0056 | 61.6118 | 122.8865 | 61.3988 | 61.471 | 123.0164 | 61.4488 | 122.8129 | 61.5346 | 61.5568 | 61.4155 | 61.4377
770.0625 | 123.3582 | -61.4685 | 61.5921 | 0.030283 | -0.040521 | -0.016578 | -0.002124 | 0.027109 | 0.003172 | 0.024268 | 61.5646 | 0.17079 | 61.4684 | -0.055996 | 0.016188 | 61.5753 | -0.006014 | 61.3764 | 61.4988 | 61.428 | 61.4519 | 61.4664 | 61.4956 | 61.4717 | 61.4928 | 123.0331 | 61.6393 | 122.9369 | 61.4125 | 61.4847 | 123.0438 | 61.4625 | 122.8449 | 61.5484 | 61.5706 | 61.4522 | 61.4744
771.0625 | 123.3902 | -61.4777 | 61.5967 | 0.030283 | -0.040521 | -0.012 | -0.002124 | 0.022531 | -0.001406 | 0.01969 | 61.5646 | 0.16622 | 61.505 | -0.051417 | 0.020767 | 61.5753 | 0.003143 | 61.3718 | 61.5079 | 61.4371 | 61.4657 | 61.4755 | 61.5002 | 61.4763 | 61.4974 | 123.0422 | 61.6439 | 122.9826 | 61.4262 | 61.4984 | 123.053 | 61.4808 | 122.8495 | 61.5438 | 61.5614 | 61.4842 | 61.5018
772.0625 | 123.3353 | -61.4594 | 61.647 | 0.030283 | -0.040521 | -0.016578 | -0.002124 | 0.022531 | -0.001406 | 0.024268 | 61.5646 | 0.16622 | 61.4684 | -0.051417 | 0.025345 | 61.5707 | 0.003143 | 61.381 | 61.4896 | 61.4188 | 61.4428 | 61.4572 | 61.4819 | 61.4579 | 61.4836 | 123.0239 | 61.6256 | 122.9277 | 61.4079 | 61.4847 | 123.0301 | 61.4625 | 122.8403 | 61.5392 | 61.5614 | 61.443 | 61.4652
773.0625 | 123.2986 | -61.4731 | 61.6058 | 0.034862 | -0.035942 | -0.012 | -0.006703 | 0.022531 | -0.001406 | 0.01969 | 61.5646 | 0.16622 | 61.4455 | -0.046838 | 0.020767 | 61.5707 | 0.007721 | 61.3718 | 61.5079 | 61.4371 | 61.4611 | 61.4664 | 61.4956 | 61.4717 | 61.4928 | 123.0377 | 61.6393 | 122.9185 | 61.4262 | 61.4939 | 123.0438 | 61.4808 | 122.8449 | 61.5438 | 61.5569 | 61.4247 | 61.4377
774.0625 | 123.349 | -61.4685 | 61.5967 | 0.030283 | -0.040521 | -0.016578 | 0.002454 | 0.027109 | -0.005985 | 0.01969 | 61.56 | 0.16622 | 61.4546 | -0.055996 | 0.016188 | 61.5707 | 0.007721 | 61.3764 | 61.4988 | 61.428 | 61.4519 | 61.471 | 61.4956 | 61.4625 | 61.4882 | 123.0285 | 61.6347 | 122.9231 | 61.4125 | 61.4847 | 123.0392 | 61.4762 | 122.8449 | 61.5438 | 61.5523 | 61.4384 | 61.4469
775.0625 | 123.3353 | -61.4731 | 61.6241 | 0.034862 | -0.040521 | -0.012 | -0.006703 | 0.031687 | 0.003172 | 0.024268 | 61.5691 | 0.16622 | 61.5004 | -0.051417 | 0.01161 | 61.5753 | -0.006014 | 61.3718 | 61.5079 | 61.4326 | 61.4611 | 61.4664 | 61.5048 | 61.4763 | 61.4974 | 123.0422 | 61.6393 | 122.9735 | 61.4217 | 61.4847 | 123.0484 | 61.4671 | 122.8449 | 61.5575 | 61.5752 | 61.4888 | 61.5064
776.0625 | 123.2849 | -61.4822 | 61.6333 | 0.030283 | -0.035942 | -0.016578 | 0.007033 | 0.031687 | -0.001406 | 0.028846 | 61.5737 | 0.17079 | 61.4912 | -0.046838 | 0.016188 | 61.5753 | 0.003143 | 61.3718 | 61.5125 | 61.4463 | 61.4657 | 61.4893 | 61.5139 | 61.4808 | 61.5111 | 123.056 | 61.653 | 122.9735 | 61.4354 | 61.4984 | 123.0576 | 61.4854 | 122.8541 | 61.5575 | 61.5706 | 61.4751 | 61.4881
777.0625 | 123.3307 | -61.4365 | 61.615 | 0.030283 | -0.035942 | -0.012 | 0.002454 | 0.027109 | -0.001406 | 0.024268 | 61.56 | 0.17537 | 61.4409 | -0.046838 | 0.020767 | 61.5662 | 0.003143 | 61.3718 | 61.4667 | 61.4005 | 61.4245 | 61.4389 | 61.4636 | 61.4351 | 61.4607 | 122.9965 | 61.6118 | 122.8773 | 61.3896 | 61.4572 | 123.0026 | 61.4396 | 122.8083 | 61.5392 | 61.5568 | 61.4201 | 61.4377
778.0625 | 123.3627 | -61.4914 | 61.6058 | 0.021127 | -0.040521 | -0.012 | -0.002124 | 0.027109 | -0.005985 | 0.01969 | 61.56 | 0.17079 | 61.4455 | -0.051417 | 0.016188 | 61.5662 | 0.003143 | 61.381 | 61.5125 | 61.4509 | 61.4794 | 61.4893 | 61.5185 | 61.4854 | 61.5111 | 123.0514 | 61.6622 | 122.9369 | 61.44 | 61.5076 | 123.0576 | 61.4945 | 122.8724 | 61.5438 | 61.5568 | 61.4293 | 61.4423
779.0625 | 123.3124 | -61.4822 | 61.5875 | 0.025705 | -0.040521 | -0.007421 | 0.002454 | 0.022531 | -0.001406 | 0.028846 | 61.5691 | 0.17079 | 61.4958 | -0.055996 | 0.025345 | 61.5753 | -0.001436 | 61.3672 | 61.5079 | 61.4417 | 61.4748 | 61.4847 | 61.5048 | 61.4808 | 61.5111 | 123.0514 | 61.653 | 122.9781 | 61.4262 | 61.5076 | 123.0576 | 61.4808 | 122.8495 | 61.5438 | 61.5706 | 61.4705 | 61.4973
780.0625 | 123.3307 | -61.4639 | 61.5967 | 0.025705 | -0.035942 | -0.012 | 0.002454 | 0.031687 | -0.005985 | 0.024268 | 61.5691 | 0.16622 | 61.5096 | -0.046838 | 0.01161 | 61.5662 | 0.007721 | 61.3718 | 61.4896 | 61.428 | 61.4519 | 61.4664 | 61.4956 | 61.4579 | 61.4882 | 123.0331 | 61.6301 | 122.9735 | 61.4171 | 61.4755 | 123.0301 | 61.4716 | 122.8357 | 61.5575 | 61.5614 | 61.4979 | 61.5018
781.0625 | 123.3627 | -61.4456 | 61.6104 | 0.030283 | -0.031363 | -0.016578 | -0.002124 | 0.013375 | -0.005985 | 0.01969 | 61.5646 | 0.17995 | 61.4592 | -0.051417 | 0.016188 | 61.5707 | 0.003143 | 61.381 | 61.4759 | 61.4143 | 61.429 | 61.4435 | 61.459 | 61.4396 | 61.4653 | 123.0102 | 61.6256 | 122.9048 | 61.3942 | 61.4618 | 123.0164 | 61.4488 | 122.8266 | 61.5484 | 61.5614 | 61.443 | 61.4561
782.0625 | 123.3582 | -61.4639 | 61.6013 | 0.025705 | -0.0451 | -0.021157 | -0.002124 | 0.022531 | -0.005985 | 0.024268 | 61.56 | 0.17079 | 61.45 | -0.055996 | 0.025345 | 61.5799 | 0.003143 | 61.3764 | 61.4896 | 61.4188 | 61.4428 | 61.4618 | 61.4865 | 61.4579 | 61.4882 | 123.0239 | 61.6347 | 122.914 | 61.4079 | 61.4893 | 123.0438 | 61.4671 | 122.8403 | 61.5346 | 61.5568 | 61.4247 | 61.4469
783.0625 | 123.3124 | -61.4594 | 61.5921 | 0.025705 | -0.0451 | -0.016578 | 0.002454 | 0.027109 | -0.001406 | 0.01969 | 61.5691 | 0.17079 | 61.4775 | -0.046838 | 0.020767 | 61.5753 | 0.007721 | 61.3764 | 61.4851 | 61.4143 | 61.4428 | 61.4618 | 61.4865 | 61.4579 | 61.479 | 123.0285 | 61.6301 | 122.9369 | 61.4125 | 61.4801 | 123.0347 | 61.4671 | 122.8357 | 61.5484 | 61.5614 | 61.4567 | 61.4698
784.0625 | 123.3582 | -61.4594 | 61.615 | 0.034862 | -0.035942 | -0.012 | 0.007033 | 0.031687 | 0.003172 | 0.024268 | 61.5691 | 0.16622 | 61.4912 | -0.051417 | 0.020767 | 61.5753 | 0.003143 | 61.3672 | 61.4942 | 61.4234 | 61.4474 | 61.4664 | 61.491 | 61.4625 | 61.4836 | 123.0285 | 61.6256 | 122.9506 | 61.4079 | 61.4801 | 123.0347 | 61.4625 | 122.8266 | 61.5484 | 61.566 | 61.4705 | 61.4881
785.0625 | 123.2803 | -61.4731 | 61.5829 | 0.021127 | -0.040521 | -0.021157 | -0.002124 | 0.027109 | -0.010563 | 0.028846 | 61.5691 | 0.16622 | 61.4638 | -0.055996 | 0.016188 | 61.5707 | 0.003143 | 61.3764 | 61.4942 | 61.4326 | 61.4519 | 61.471 | 61.5002 | 61.4625 | 61.5019 | 123.0422 | 61.6393 | 122.9369 | 61.4171 | 61.4893 | 123.0438 | 61.4762 | 122.8495 | 61.553 | 61.566 | 61.4476 | 61.4606
786.0625 | 123.3124 | -61.4777 | 61.6425 | 0.030283 | -0.0451 | -0.007421 | 0.007033 | 0.031687 | -0.001406 | 0.024268 | 61.5691 | 0.17079 | 61.4455 | -0.055996 | 0.020767 | 61.5753 | -0.001436 | 61.3764 | 61.5079 | 61.4326 | 61.4702 | 61.4847 | 61.5093 | 61.4763 | 61.5019 | 123.0468 | 61.6485 | 122.9231 | 61.4217 | 61.4984 | 123.053 | 61.4762 | 122.8541 | 61.5484 | 61.5706 | 61.4247 | 61.4469
787.0625 | 123.3215 | -61.4731 | 61.6196 | 0.030283 | -0.040521 | -0.007421 | -0.002124 | 0.027109 | -0.005985 | 0.024268 | 61.5691 | 0.17537 | 61.4638 | -0.051417 | 0.020767 | 61.5753 | -0.006014 | 61.3672 | 61.5034 | 61.4326 | 61.4657 | 61.471 | 61.5002 | 61.4671 | 61.4974 | 123.0422 | 61.6485 | 122.9369 | 61.4217 | 61.4939 | 123.0484 | 61.4671 | 122.8403 | 61.5484 | 61.5752 | 61.443 | 61.4698
788.0625 | 123.349 | -61.4777 | 61.5875 | 0.030283 | -0.035942 | -0.016578 | -0.006703 | 0.017953 | -0.001406 | 0.01969 | 61.5783 | 0.16622 | 61.4958 | -0.051417 | 0.007032 | 61.5662 | -0.001436 | 61.3718 | 61.5079 | 61.4417 | 61.4611 | 61.471 | 61.4956 | 61.4763 | 61.4974 | 123.056 | 61.6439 | 122.9735 | 61.4262 | 61.4847 | 123.0438 | 61.4762 | 122.8495 | 61.5713 | 61.5797 | 61.4888 | 61.4973
789.0625 | 123.3673 | -61.4685 | 61.5601 | 0.044018 | -0.040521 | -0.007421 | -0.002124 | 0.027109 | 0.003172 | 0.015112 | 61.56 | 0.16622 | 61.4638 | -0.060575 | 0.020767 | 61.5753 | 0.007721 | 61.3718 | 61.5125 | 61.428 | 61.4611 | 61.4664 | 61.4956 | 61.4717 | 61.4836 | 123.0285 | 61.6347 | 122.9323 | 61.4079 | 61.4893 | 123.0438 | 61.4762 | 122.8403 | 61.5392 | 61.5523 | 61.443 | 61.4561
790.0625 | 123.3582 | -61.4822 | 61.5967 | 0.030283 | -0.035942 | -0.007421 | -0.002124 | 0.031687 | -0.005985 | 0.01969 | 61.5646 | 0.17537 | 61.4455 | -0.046838 | 0.020767 | 61.5799 | 0.003143 | 61.3718 | 61.5125 | 61.4463 | 61.4748 | 61.4801 | 61.5139 | 61.4763 | 61.5019 | 123.0468 | 61.6576 | 122.9277 | 61.4354 | 61.503 | 123.0621 | 61.4854 | 122.8541 | 61.5438 | 61.5614 | 61.4247 | 61.4423
791.0625 | 123.2391 | -61.4822 | 61.647 | 0.034862 | -0.0451 | -0.007421 | 0.002454 | 0.036265 | -0.005985 | 0.01969 | 61.5691 | 0.16622 | 61.4592 | -0.055996 | 0.016188 | 61.5799 | 0.003143 | 61.3718 | 61.5171 | 61.4371 | 61.4748 | 61.4847 | 61.5185 | 61.4763 | 61.5019 | 123.0514 | 61.6485 | 122.9414 | 61.4262 | 61.4984 | 123.0621 | 61.4854 | 122.8541 | 61.553 | 61.566 | 61.443 | 61.4561
792.0625 | 123.3627 | -61.4914 | 61.5921 | 0.025705 | -0.040521 | -0.021157 | -0.006703 | 0.027109 | -0.001406 | 0.010533 | 61.5646 | 0.16164 | 61.505 | -0.051417 | 0.016188 | 61.5707 | 0.003143 | 61.3718 | 61.5171 | 61.4509 | 61.4702 | 61.4847 | 61.5185 | 61.49 | 61.5019 | 123.056 | 61.653 | 122.9964 | 61.44 | 61.5076 | 123.0621 | 61.4945 | 122.8632 | 61.5484 | 61.5614 | 61.4888 | 61.5018
793.0625 | 123.3765 | -61.4502 | 61.5829 | 0.030283 | -0.040521 | -0.016578 | 0.007033 | 0.027109 | -0.001406 | 0.024268 | 61.5691 | 0.17079 | 61.4821 | -0.051417 | 0.016188 | 61.5753 | 0.003143 | 61.3672 | 61.4805 | 61.4097 | 61.4336 | 61.4572 | 61.4773 | 61.4488 | 61.4745 | 123.0193 | 61.621 | 122.9323 | 61.3988 | 61.4664 | 123.0255 | 61.4533 | 122.8174 | 61.553 | 61.566 | 61.4659 | 61.4789
794.0625 | 123.3627 | -61.4639 | 61.5784 | 0.034862 | -0.031363 | -0.016578 | 0.007033 | 0.031687 | -0.005985 | 0.024268 | 61.5554 | 0.17079 | 61.4455 | -0.051417 | 0.01161 | 61.5707 | 0.003143 | 61.3718 | 61.4988 | 61.4326 | 61.4474 | 61.471 | 61.4956 | 61.4579 | 61.4882 | 123.0193 | 61.6347 | 122.9094 | 61.4125 | 61.4755 | 123.0347 | 61.4671 | 122.8357 | 61.5438 | 61.5523 | 61.4339 | 61.4423
795.0625 | 123.3994 | -61.4456 | 61.5692 | 0.025705 | -0.0451 | -0.012 | -0.002124 | 0.022531 | -0.001406 | 0.024268 | 61.56 | 0.16622 | 61.4546 | -0.046838 | 0.016188 | 61.5753 | 0.003143 | 61.3718 | 61.4713 | 61.4005 | 61.4336 | 61.4435 | 61.4681 | 61.4442 | 61.4699 | 123.0056 | 61.6118 | 122.9002 | 61.3988 | 61.4618 | 123.0209 | 61.4488 | 122.8174 | 61.5438 | 61.5568 | 61.4384 | 61.4515
796.0625 | 123.3444 | -61.4777 | 61.5601 | 0.030283 | -0.035942 | -0.016578 | -0.002124 | 0.027109 | -0.001406 | 0.028846 | 61.5737 | 0.17079 | 61.4867 | -0.055996 | 0.020767 | 61.5707 | 0.003143 | 61.3718 | 61.5079 | 61.4417 | 61.4611 | 61.4755 | 61.5048 | 61.4763 | 61.5065 | 123.0514 | 61.6485 | 122.9643 | 61.4217 | 61.4984 | 123.0484 | 61.4808 | 122.8495 | 61.553 | 61.5706 | 61.4659 | 61.4835
797.0625 | 123.3444 | -61.4456 | 61.6058 | 0.030283 | -0.040521 | -0.012 | 0.002454 | 0.031687 | -0.001406 | 0.024268 | 61.5691 | 0.16622 | 61.4912 | -0.046838 | 0.016188 | 61.5707 | -0.001436 | 61.3764 | 61.4759 | 61.4051 | 61.4336 | 61.4481 | 61.4773 | 61.4442 | 61.4699 | 123.0148 | 61.6118 | 122.9369 | 61.3988 | 61.4618 | 123.0164 | 61.4442 | 122.822 | 61.553 | 61.5706 | 61.4751 | 61.4927
798.0625 | 123.381 | -61.4502 | 61.5784 | 0.025705 | -0.040521 | -0.012 | 0.007033 | 0.027109 | 0.003172 | 0.024268 | 61.5646 | 0.17079 | 61.45 | -0.055996 | 0.020767 | 61.5662 | 0.003143 | 61.3672 | 61.4759 | 61.4097 | 61.4382 | 61.4572 | 61.4773 | 61.4534 | 61.4745 | 123.0148 | 61.621 | 122.9002 | 61.3942 | 61.471 | 123.0164 | 61.4533 | 122.8174 | 61.5438 | 61.5614 | 61.4293 | 61.4469
799.0625 | 123.3902 | -61.4548 | 61.5875 | 0.025705 | -0.035942 | -0.007421 | 0.002454 | 0.027109 | 0.003172 | 0.024268 | 61.5691 | 0.17079 | 61.4546 | -0.046838 | 0.016188 | 61.5707 | 0.003143 | 61.3672 | 61.4805 | 61.4188 | 61.4474 | 61.4572 | 61.4819 | 61.4579 | 61.479 | 123.0239 | 61.6256 | 122.9094 | 61.4079 | 61.471 | 123.0255 | 61.4579 | 122.822 | 61.553 | 61.566 | 61.4384 | 61.4515
800.0625 | 123.3353 | -61.4731 | 61.5692 | 0.025705 | -0.040521 | -0.021157 | 0.002454 | 0.027109 | -0.001406 | 0.024268 | 61.5691 | 0.16622 | 61.4638 | -0.046838 | 0.016188 | 61.5707 | 0.003143 | 61.3718 | 61.4988 | 61.4326 | 61.4519 | 61.4755 | 61.5002 | 61.4717 | 61.4974 | 123.0422 | 61.6393 | 122.9369 | 61.4262 | 61.4893 | 123.0438 | 61.4762 | 122.8449 | 61.553 | 61.566 | 61.4476 | 61.4606
801.0625 | 123.2803 | -61.4822 | 61.6058 | 0.025705 | -0.040521 | -0.007421 | -0.002124 | 0.031687 | -0.005985 | 0.028846 | 61.5691 | 0.17537 | 61.4867 | -0.051417 | 0.016188 | 61.5845 | -0.001436 | 61.3672 | 61.5079 | 61.4417 | 61.4748 | 61.4801 | 61.5139 | 61.4763 | 61.5111 | 123.0514 | 61.6576 | 122.9689 | 61.4308 | 61.4984 | 123.0667 | 61.4808 | 122.8495 | 61.553 | 61.5706 | 61.4705 | 61.4881
802.0625 | 123.3536 | -61.4731 | 61.5967 | 0.030283 | -0.040521 | -0.016578 | -0.002124 | 0.036265 | -0.005985 | 0.024268 | 61.56 | 0.17079 | 61.4592 | -0.051417 | 0.016188 | 61.5753 | -0.006014 | 61.3764 | 61.5034 | 61.4326 | 61.4565 | 61.471 | 61.5093 | 61.4671 | 61.4974 | 123.0331 | 61.6439 | 122.9323 | 61.4217 | 61.4893 | 123.0484 | 61.4671 | 122.8495 | 61.5438 | 61.566 | 61.443 | 61.4652
803.0625 | 123.3719 | -61.4868 | 61.5555 | 0.034862 | -0.049678 | -0.021157 | 0.007033 | 0.027109 | -0.001406 | 0.024268 | 61.5646 | 0.16622 | 61.45 | -0.055996 | 0.020767 | 61.5662 | 0.007721 | 61.3718 | 61.5217 | 61.4371 | 61.4657 | 61.4938 | 61.5139 | 61.4854 | 61.5111 | 123.0514 | 61.653 | 122.9369 | 61.4308 | 61.5076 | 123.053 | 61.4945 | 122.8586 | 61.5438 | 61.5569 | 61.4293 | 61.4423
804.0625 | 123.3994 | -61.4594 | 61.5875 | 0.030283 | -0.040521 | -0.012 | 0.002454 | 0.027109 | -0.010563 | 0.024268 | 61.5646 | 0.17079 | 61.45 | -0.051417 | 0.016188 | 61.5662 | 0.003143 | 61.3718 | 61.4896 | 61.4188 | 61.4474 | 61.4618 | 61.4865 | 61.4488 | 61.4836 | 123.0239 | 61.6301 | 122.9094 | 61.4079 | 61.4755 | 123.0255 | 61.4625 | 122.8312 | 61.5484 | 61.5614 | 61.4339 | 61.4469
805.0625 | 123.3444 | -61.4731 | 61.5784 | 0.030283 | -0.035942 | -0.007421 | -0.002124 | 0.022531 | 0.003172 | 0.024268 | 61.5691 | 0.16622 | 61.4912 | -0.055996 | 0.016188 | 61.5662 | -0.001436 | 61.3672 | 61.5034 | 61.4371 | 61.4657 | 61.471 | 61.4956 | 61.4763 | 61.4974 | 123.0422 | 61.6393 | 122.9643 | 61.4171 | 61.4893 | 123.0392 | 61.4716 | 122.8403 | 61.553 | 61.5706 | 61.4751 | 61.4927
806.0625 | 123.3673 | -61.4777 | 61.5829 | 0.025705 | -0.031363 | -0.016578 | 0.007033 | 0.017953 | -0.001406 | 0.024268 | 61.5691 | 0.17079 | 61.4821 | -0.051417 | 0.01161 | 61.5707 | -0.001436 | 61.3672 | 61.5034 | 61.4463 | 61.4611 | 61.4847 | 61.4956 | 61.4763 | 61.5019 | 123.0468 | 61.6485 | 122.9597 | 61.4262 | 61.4893 | 123.0484 | 61.4762 | 122.8449 | 61.5575 | 61.5706 | 61.4705 | 61.4835
807.0625 | 123.349 | -61.4868 | 61.5784 | 0.025705 | -0.035942 | -0.012 | 0.002454 | 0.027109 | -0.005985 | 0.024268 | 61.5646 | 0.16622 | 61.45 | -0.051417 | 0.016188 | 61.5753 | -0.001436 | 61.3718 | 61.5125 | 61.4509 | 61.4748 | 61.4893 | 61.5139 | 61.4808 | 61.5111 | 123.0514 | 61.653 | 122.9369 | 61.4354 | 61.503 | 123.0621 | 61.4854 | 122.8586 | 61.5484 | 61.566 | 61.4339 | 61.4515
808.0625 | 123.2346 | -61.5143 | 61.6058 | 0.025705 | -0.0451 | -0.016578 | -0.006703 | 0.027109 | 0.003172 | 0.01969 | 61.56 | 0.17079 | 61.45 | -0.051417 | 0.01161 | 61.5707 | -0.001436 | 61.3764 | 61.54 | 61.4692 | 61.4977 | 61.5076 | 61.5414 | 61.5175 | 61.534 | 123.0743 | 61.6851 | 122.9643 | 61.4629 | 61.5259 | 123.085 | 61.5128 | 122.8907 | 61.5484 | 61.5614 | 61.4384 | 61.4515
809.0625 | 123.2529 | -61.5051 | 61.6333 | 0.034862 | -0.0451 | -0.007421 | -0.002124 | 0.027109 | -0.001406 | 0.024268 | 61.5691 | 0.17537 | 61.4867 | -0.051417 | 0.01161 | 61.5753 | -0.001436 | 61.3718 | 61.54 | 61.46 | 61.4977 | 61.503 | 61.5322 | 61.5037 | 61.5294 | 123.0743 | 61.6805 | 122.9918 | 61.4537 | 61.5167 | 123.0804 | 61.5037 | 122.8769 | 61.5575 | 61.5706 | 61.4751 | 61.4881
810.0625 | 123.3215 | -61.4868 | 61.6104 | 0.030283 | -0.040521 | -0.012 | 0.002454 | 0.027109 | -0.001406 | 0.024268 | 61.5646 | 0.17537 | 61.505 | -0.051417 | 0.016188 | 61.5753 | 0.003143 | 61.3718 | 61.5171 | 61.4463 | 61.4748 | 61.4893 | 61.5139 | 61.4854 | 61.5111 | 123.0514 | 61.6622 | 122.9918 | 61.4354 | 61.503 | 123.0621 | 61.49 | 122.8586 | 61.5484 | 61.5614 | 61.4888 | 61.5018
811.0625 | 123.2712 | -61.4731 | 61.6196 | 0.034862 | -0.026784 | -0.012 | 0.002454 | 0.027109 | -0.001406 | 0.028846 | 61.5737 | 0.17079 | 61.4592 | -0.055996 | 0.020767 | 61.5662 | -0.001436 | 61.3672 | 61.5079 | 61.4463 | 61.4611 | 61.4755 | 61.5002 | 61.4717 | 61.5019 | 123.0468 | 61.6439 | 122.9323 | 61.4171 | 61.4939 | 123.0392 | 61.4716 | 122.8403 | 61.553 | 61.5752 | 61.4384 | 61.4606
812.0625 | 123.3307 | -61.4731 | 61.6013 | 0.021127 | -0.0451 | -0.016578 | 0.002454 | 0.022531 | -0.010563 | 0.028846 | 61.56 | 0.16164 | 61.4546 | -0.051417 | 0.020767 | 61.5662 | -0.001436 | 61.3764 | 61.4942 | 61.428 | 61.4565 | 61.4755 | 61.4956 | 61.4625 | 61.5019 | 123.0331 | 61.6347 | 122.9277 | 61.4217 | 61.4939 | 123.0392 | 61.4716 | 122.8495 | 61.5392 | 61.5614 | 61.4339 | 61.4561
813.0625 | 123.2986 | -61.496 | 61.6196 | 0.030283 | -0.035942 | -0.012 | -0.002124 | 0.027109 | 0.003172 | 0.01969 | 61.5691 | 0.16164 | 61.4729 | -0.060575 | 0.01161 | 61.5753 | -0.001436 | 61.3764 | 61.5263 | 61.46 | 61.484 | 61.4938 | 61.5231 | 61.4991 | 61.5157 | 123.0651 | 61.6576 | 122.9689 | 61.4354 | 61.5076 | 123.0713 | 61.4945 | 122.8724 | 61.5575 | 61.5706 | 61.4613 | 61.4744
814.0625 | 123.2391 | -61.5051 | 61.6379 | 0.034862 | -0.031363 | -0.007421 | 0.011611 | 0.036265 | -0.001406 | 0.028846 | 61.5691 | 0.16622 | 61.4958 | -0.055996 | 0.016188 | 61.5662 | 0.003143 | 61.3718 | 61.54 | 61.4738 | 61.4977 | 61.5167 | 61.5414 | 61.5037 | 61.534 | 123.0743 | 61.6713 | 123.001 | 61.4491 | 61.5213 | 123.0713 | 61.5083 | 122.8769 | 61.553 | 61.566 | 61.4796 | 61.4927
815.0625 | 123.2803 | -61.4868 | 61.6425 | 0.030283 | -0.040521 | -0.016578 | 0.002454 | 0.027109 | 0.003172 | 0.033424 | 61.5691 | 0.16164 | 61.4592 | -0.046838 | 0.016188 | 61.5707 | 0.003143 | 61.3672 | 61.5171 | 61.4463 | 61.4702 | 61.4893 | 61.5139 | 61.49 | 61.5202 | 123.056 | 61.6485 | 122.946 | 61.44 | 61.503 | 123.0576 | 61.49 | 122.8541 | 61.553 | 61.566 | 61.443 | 61.4561
816.0625 | 123.2071 | -61.4868 | 61.6425 | 0.030283 | -0.035942 | -0.007421 | 0.002454 | 0.036265 | -0.001406 | 0.024268 | 61.5646 | 0.17079 | 61.45 | -0.055996 | 0.01161 | 61.5753 | -0.001436 | 61.3718 | 61.5171 | 61.4509 | 61.4794 | 61.4893 | 61.5231 | 61.4854 | 61.5111 | 123.0514 | 61.6576 | 122.9369 | 61.4308 | 61.4984 | 123.0621 | 61.4854 | 122.8586 | 61.553 | 61.566 | 61.4384 | 61.4515
817.0625 | 123.3444 | -61.4731 | 61.6058 | 0.030283 | -0.040521 | -0.021157 | -0.002124 | 0.031687 | 0.003172 | 0.01969 | 61.5737 | 0.17079 | 61.4592 | -0.055996 | 0.016188 | 61.5707 | 0.003143 | 61.3764 | 61.5034 | 61.4326 | 61.4519 | 61.471 | 61.5048 | 61.4763 | 61.4928 | 123.0468 | 61.6439 | 122.9323 | 61.4171 | 61.4893 | 123.0438 | 61.4762 | 122.8495 | 61.5575 | 61.5706 | 61.443 | 61.4561
818.0625 | 123.23 | -61.496 | 61.6379 | 0.030283 | -0.0451 | -0.012 | 0.002454 | 0.027109 | -0.005985 | 0.028846 | 61.5737 | 0.17079 | 61.5004 | -0.042259 | 0.020767 | 61.5707 | 0.007721 | 61.3672 | 61.5263 | 61.4509 | 61.484 | 61.4984 | 61.5231 | 61.49 | 61.5248 | 123.0697 | 61.6668 | 122.9964 | 61.4537 | 61.5167 | 123.0667 | 61.5037 | 122.8632 | 61.553 | 61.566 | 61.4796 | 61.4927
819.0625 | 123.2391 | -61.5005 | 61.6425 | 0.03944 | -0.040521 | -0.021157 | 0.002454 | 0.027109 | -0.001406 | 0.028846 | 61.5646 | 0.17079 | 61.4958 | -0.051417 | 0.016188 | 61.5662 | 0.003143 | 61.3718 | 61.54 | 61.46 | 61.4794 | 61.503 | 61.5277 | 61.4991 | 61.5294 | 123.0651 | 61.6713 | 122.9964 | 61.4491 | 61.5167 | 123.0667 | 61.5037 | 122.8724 | 61.5484 | 61.5614 | 61.4796 | 61.4927
820.0625 | 123.2117 | -61.4822 | 61.6241 | 0.034862 | -0.0451 | -0.016578 | 0.002454 | 0.036265 | -0.001406 | 0.028846 | 61.5691 | 0.17079 | 61.5004 | -0.051417 | 0.020767 | 61.5707 | 0.003143 | 61.3718 | 61.5171 | 61.4371 | 61.4657 | 61.4847 | 61.5185 | 61.4808 | 61.5111 | 123.0514 | 61.653 | 122.9826 | 61.4308 | 61.503 | 123.053 | 61.4854 | 122.8541 | 61.5484 | 61.566 | 61.4796 | 61.4973
821.0625 | 123.2574 | -61.4639 | 61.6516 | 0.030283 | -0.040521 | -0.012 | -0.002124 | 0.017953 | 0.003172 | 0.028846 | 61.5691 | 0.17537 | 61.4729 | -0.051417 | 0.020767 | 61.5753 | -0.001436 | 61.3672 | 61.4942 | 61.4234 | 61.4519 | 61.4618 | 61.4819 | 61.4671 | 61.4928 | 123.0331 | 61.6393 | 122.9369 | 61.4125 | 61.4847 | 123.0392 | 61.4625 | 122.8312 | 61.5484 | 61.5706 | 61.4522 | 61.4744
822.0625 | 123.2529 | -61.5005 | 61.6104 | 0.030283 | -0.035942 | -0.016578 | -0.002124 | 0.027109 | -0.005985 | 0.028846 | 61.5691 | 0.16622 | 61.4546 | -0.042259 | 0.016188 | 61.5707 | 0.003143 | 61.3627 | 61.5308 | 61.4646 | 61.484 | 61.4984 | 61.5277 | 61.4946 | 61.5294 | 123.0697 | 61.6668 | 122.9552 | 61.4583 | 61.5167 | 123.0713 | 61.5037 | 122.8632 | 61.553 | 61.566 | 61.4384 | 61.4515
823.0625 | 123.2666 | -61.4594 | 61.6104 | 0.030283 | -0.031363 | -0.012 | 0.002454 | 0.022531 | 0.003172 | 0.028846 | 61.5691 | 0.17995 | 61.4592 | -0.051417 | 0.020767 | 61.5707 | -0.001436 | 61.3764 | 61.4896 | 61.428 | 61.4474 | 61.4618 | 61.4819 | 61.4625 | 61.4882 | 123.0285 | 61.6393 | 122.9185 | 61.4079 | 61.4801 | 123.0301 | 61.4579 | 122.8357 | 61.5484 | 61.5706 | 61.4384 | 61.4606
824.0625 | 123.2712 | -61.4868 | 61.615 | 0.030283 | -0.0451 | -0.025735 | 0.002454 | 0.027109 | -0.005985 | 0.028846 | 61.5691 | 0.17079 | 61.4546 | -0.051417 | 0.020767 | 61.5707 | -0.001436 | 61.3672 | 61.5171 | 61.4417 | 61.4611 | 61.4893 | 61.5139 | 61.4808 | 61.5157 | 123.056 | 61.6576 | 122.9414 | 61.4354 | 61.5076 | 123.0576 | 61.4854 | 122.8541 | 61.5484 | 61.5706 | 61.4339 | 61.4561
825.0625 | 123.2666 | -61.4868 | 61.6241 | 0.025705 | -0.035942 | -0.012 | 0.011611 | 0.031687 | -0.001406 | 0.024268 | 61.5737 | 0.17079 | 61.4592 | -0.055996 | 0.016188 | 61.5753 | -0.001436 | 61.3764 | 61.5125 | 61.4509 | 61.4748 | 61.4984 | 61.5185 | 61.4854 | 61.5111 | 123.0605 | 61.6576 | 122.946 | 61.4308 | 61.503 | 123.0621 | 61.4854 | 122.8632 | 61.5575 | 61.5752 | 61.443 | 61.4606
826.0625 | 123.2803 | -61.4685 | 61.6516 | 0.034862 | -0.0451 | -0.012 | 0.002454 | 0.027109 | 0.003172 | 0.033424 | 61.5783 | 0.16622 | 61.4821 | -0.046838 | 0.020767 | 61.5662 | 0.003143 | 61.3718 | 61.5034 | 61.4234 | 61.4565 | 61.471 | 61.4956 | 61.4717 | 61.5019 | 123.0468 | 61.6347 | 122.9506 | 61.4217 | 61.4893 | 123.0347 | 61.4716 | 122.8403 | 61.5575 | 61.5752 | 61.4613 | 61.4789
827.0625 | 123.2941 | -61.496 | 61.6333 | 0.025705 | -0.040521 | -0.016578 | -0.002124 | 0.027109 | 0.003172 | 0.028846 | 61.5737 | 0.17079 | 61.5004 | -0.051417 | 0.016188 | 61.5707 | -0.001436 | 61.3718 | 61.5217 | 61.4555 | 61.4794 | 61.4938 | 61.5231 | 61.4991 | 61.5248 | 123.0697 | 61.6668 | 122.9964 | 61.4446 | 61.5122 | 123.0667 | 61.4945 | 122.8678 | 61.5575 | 61.5752 | 61.4842 | 61.5018
828.0625 | 123.3078 | -61.4639 | 61.6516 | 0.025705 | -0.035942 | -0.016578 | -0.002124 | 0.027109 | -0.005985 | 0.024268 | 61.5783 | 0.17079 | 61.505 | -0.051417 | 0.01161 | 61.5753 | -0.001436 | 61.3718 | 61.4896 | 61.428 | 61.4474 | 61.4618 | 61.491 | 61.4579 | 61.4882 | 123.0422 | 61.6347 | 122.9689 | 61.4125 | 61.4755 | 123.0392 | 61.4625 | 122.8357 | 61.5667 | 61.5797 | 61.4934 | 61.5064
829.0625 | 123.2803 | -61.4822 | 61.6379 | 0.025705 | -0.035942 | -0.002842 | -0.002124 | 0.036265 | 0.003172 | 0.028846 | 61.5783 | 0.16622 | 61.505 | -0.051417 | 0.025345 | 61.5753 | 0.003143 | 61.3718 | 61.5079 | 61.4463 | 61.4794 | 61.4801 | 61.5185 | 61.4854 | 61.5111 | 123.0605 | 61.6485 | 122.9872 | 61.4308 | 61.5076 | 123.0576 | 61.4854 | 122.8541 | 61.553 | 61.5752 | 61.4796 | 61.5018
830.0625 | 123.3261 | -61.5005 | 61.6608 | 0.030283 | -0.0451 | -0.025735 | 0.007033 | 0.031687 | -0.005985 | 0.024268 | 61.5691 | 0.16164 | 61.4867 | -0.051417 | 0.020767 | 61.5707 | -0.001436 | 61.3764 | 61.5308 | 61.4554 | 61.4748 | 61.5076 | 61.5322 | 61.4946 | 61.5248 | 123.0697 | 61.6622 | 122.9872 | 61.4491 | 61.5213 | 123.0713 | 61.4991 | 122.8769 | 61.5484 | 61.5706 | 61.4659 | 61.4881
831.0625 | 123.2895 | -61.4914 | 61.6425 | 0.025705 | -0.035942 | -0.012 | -0.002124 | 0.027109 | -0.005985 | 0.028846 | 61.5737 | 0.17537 | 61.4684 | -0.051417 | 0.020767 | 61.5753 | 0.003143 | 61.3672 | 61.5171 | 61.4555 | 61.4794 | 61.4893 | 61.5185 | 61.4854 | 61.5202 | 123.0651 | 61.6668 | 122.9597 | 61.44 | 61.5122 | 123.0667 | 61.4945 | 122.8586 | 61.553 | 61.5706 | 61.4476 | 61.4652
832.0625 | 123.317 | -61.5143 | 61.6104 | 0.025705 | -0.040521 | -0.016578 | 0.007033 | 0.027109 | -0.001406 | 0.024268 | 61.5691 | 0.17079 | 61.4592 | -0.055996 | 0.016188 | 61.5662 | -0.001436 | 61.3718 | 61.54 | 61.4738 | 61.4977 | 61.5213 | 61.5414 | 61.5129 | 61.5386 | 123.0834 | 61.6851 | 122.9735 | 61.4583 | 61.5305 | 123.0804 | 61.5128 | 122.8861 | 61.553 | 61.5706 | 61.443 | 61.4606
833.0625 | 123.2758 | -61.4731 | 61.6333 | 0.034862 | -0.0451 | -0.007421 | -0.006703 | 0.031687 | -0.001406 | 0.024268 | 61.5691 | 0.17537 | 61.4592 | -0.055996 | 0.025345 | 61.5662 | 0.003143 | 61.3672 | 61.5079 | 61.428 | 61.4657 | 61.4664 | 61.5048 | 61.4717 | 61.4974 | 123.0422 | 61.6485 | 122.9323 | 61.4171 | 61.4984 | 123.0392 | 61.4762 | 122.8403 | 61.5438 | 61.566 | 61.4339 | 61.4561
834.0625 | 123.3215 | -61.4731 | 61.6516 | 0.025705 | -0.035942 | -0.016578 | 0.007033 | 0.031687 | -0.001406 | 0.028846 | 61.5737 | 0.16622 | 61.4592 | -0.051417 | 0.025345 | 61.5753 | -0.001436 | 61.3764 | 61.4988 | 61.4371 | 61.4565 | 61.4801 | 61.5048 | 61.4717 | 61.5019 | 123.0468 | 61.6393 | 122.9323 | 61.4217 | 61.4984 | 123.0484 | 61.4716 | 122.8495 | 61.5484 | 61.5752 | 61.4339 | 61.4606
835.0625 | 123.2895 | -61.4731 | 61.647 | 0.034862 | -0.035942 | -0.021157 | 0.002454 | 0.027109 | 0.00775 | 0.024268 | 61.5691 | 0.16622 | 61.4729 | -0.051417 | 0.020767 | 61.5662 | 0.007721 | 61.3764 | 61.5079 | 61.4371 | 61.4519 | 61.4755 | 61.5002 | 61.4808 | 61.4974 | 123.0422 | 61.6393 | 122.946 | 61.4217 | 61.4939 | 123.0392 | 61.4808 | 122.8495 | 61.5484 | 61.5614 | 61.4522 | 61.4652
836.0625 | 123.2391 | -61.4822 | 61.6608 | 0.025705 | -0.040521 | -0.016578 | 0.002454 | 0.022531 | -0.001406 | 0.024268 | 61.5737 | 0.17995 | 61.5004 | -0.046838 | 0.020767 | 61.5707 | -0.006014 | 61.3718 | 61.5079 | 61.4417 | 61.4657 | 61.4847 | 61.5048 | 61.4808 | 61.5065 | 123.056 | 61.6622 | 122.9826 | 61.4354 | 61.503 | 123.053 | 61.4762 | 122.8541 | 61.553 | 61.5797 | 61.4796 | 61.5064
837.0625 | 123.2941 | -61.4731 | 61.6379 | 0.034862 | -0.040521 | -0.012 | 0.002454 | 0.031687 | 0.00775 | 0.033424 | 61.5783 | 0.17079 | 61.5187 | -0.051417 | 0.025345 | 61.5753 | 0.007721 | 61.3718 | 61.5079 | 61.4326 | 61.4611 | 61.4755 | 61.5048 | 61.4808 | 61.5065 | 123.0514 | 61.6439 | 122.9918 | 61.4217 | 61.4984 | 123.0484 | 61.4808 | 122.8449 | 61.553 | 61.5706 | 61.4934 | 61.511
838.0625 | 123.2941 | -61.4914 | 61.6562 | 0.030283 | -0.035942 | -0.012 | -0.006703 | 0.027109 | -0.005985 | 0.024268 | 61.5646 | 0.17079 | 61.5004 | -0.055996 | 0.007032 | 61.5707 | -0.001436 | 61.3764 | 61.5217 | 61.4555 | 61.4794 | 61.4847 | 61.5185 | 61.4854 | 61.5157 | 123.056 | 61.6622 | 122.9918 | 61.4354 | 61.4984 | 123.0621 | 61.49 | 122.8678 | 61.5575 | 61.566 | 61.4934 | 61.5018
839.0625 | 123.2941 | -61.4777 | 61.6608 | 0.030283 | -0.040521 | -0.016578 | -0.002124 | 0.027109 | -0.005985 | 0.024268 | 61.5783 | 0.16622 | 61.4867 | -0.055996 | 0.016188 | 61.5753 | 0.003143 | 61.381 | 61.5079 | 61.4371 | 61.4611 | 61.4755 | 61.5048 | 61.4717 | 61.5019 | 123.056 | 61.6439 | 122.9643 | 61.4217 | 61.4938 | 123.053 | 61.4808 | 122.8586 | 61.5621 | 61.5752 | 61.4705 | 61.4835
840.0625 | 123.2483 | -61.496 | 61.6287 | 0.025705 | -0.0451 | -0.016578 | -0.006703 | 0.036265 | -0.001406 | 0.024268 | 61.5646 | 0.17537 | 61.4684 | -0.042259 | 0.025345 | 61.5662 | -0.001436 | 61.3764 | 61.5217 | 61.4509 | 61.4794 | 61.4893 | 61.5322 | 61.4946 | 61.5202 | 123.0605 | 61.6713 | 122.9643 | 61.4537 | 61.5213 | 123.0621 | 61.4945 | 122.8724 | 61.5392 | 61.566 | 61.443 | 61.4698
841.0625 | 123.2895 | -61.4548 | 61.6516 | 0.034862 | -0.0451 | -0.016578 | -0.002124 | 0.027109 | -0.001406 | 0.028846 | 61.5691 | 0.17537 | 61.4592 | -0.055996 | 0.020767 | 61.5753 | -0.001436 | 61.3764 | 61.4896 | 61.4097 | 61.4382 | 61.4526 | 61.4819 | 61.4534 | 61.4836 | 123.0239 | 61.6301 | 122.914 | 61.3988 | 61.4755 | 123.0301 | 61.4533 | 122.8312 | 61.5484 | 61.5706 | 61.4384 | 61.4606
842.0625 | 123.2941 | -61.496 | 61.6425 | 0.025705 | -0.0451 | -0.016578 | 0.002454 | 0.027109 | -0.001406 | 0.024268 | 61.5691 | 0.17079 | 61.4546 | -0.03768 | 0.020767 | 61.5707 | 0.003143 | 61.3764 | 61.5217 | 61.4509 | 61.4794 | 61.4984 | 61.5231 | 61.4946 | 61.5202 | 123.0651 | 61.6668 | 122.9506 | 61.4583 | 61.5167 | 123.0667 | 61.4991 | 122.8724 | 61.5484 | 61.566 | 61.4339 | 61.4515
843.0625 | 123.1934 | -61.4777 | 61.6608 | 0.025705 | -0.0451 | -0.021157 | 0.007033 | 0.022531 | -0.005985 | 0.01969 | 61.5737 | 0.17537 | 61.4684 | -0.051417 | 0.016188 | 61.5707 | 0.003143 | 61.381 | 61.5034 | 61.4326 | 61.4565 | 61.4847 | 61.5002 | 61.4717 | 61.4974 | 123.0514 | 61.653 | 122.946 | 61.4262 | 61.4938 | 123.0484 | 61.4808 | 122.8586 | 61.5575 | 61.5706 | 61.4522 | 61.4652
844.0625 | 123.23 | -61.5005 | 61.6562 | 0.030283 | -0.049678 | -0.012 | 0.002454 | 0.027109 | 0.003172 | 0.033424 | 61.5737 | 0.17079 | 61.4912 | -0.042259 | 0.025345 | 61.5753 | 0.003143 | 61.3764 | 61.5308 | 61.4509 | 61.4885 | 61.503 | 61.5277 | 61.5037 | 61.534 | 123.0743 | 61.6713 | 122.9918 | 61.4583 | 61.5259 | 123.0759 | 61.5037 | 122.8769 | 61.5484 | 61.5706 | 61.4659 | 61.4881
845.0625 | 123.2666 | -61.5005 | 61.6608 | 0.034862 | -0.040521 | -0.012 | 0.002454 | 0.031687 | 0.003172 | 0.024268 | 61.5737 | 0.17079 | 61.505 | -0.051417 | 0.020767 | 61.5707 | 0.007721 | 61.3764 | 61.5354 | 61.46 | 61.4885 | 61.503 | 61.5322 | 61.5037 | 61.5248 | 123.0743 | 61.6713 | 123.0055 | 61.4491 | 61.5213 | 123.0713 | 61.5083 | 122.8769 | 61.553 | 61.566 | 61.4842 | 61.4973
846.0625 | 123.2483 | -61.4731 | 61.6516 | 0.030283 | -0.040521 | -0.012 | 0.002454 | 0.031687 | -0.001406 | 0.024268 | 61.5737 | 0.17537 | 61.5141 | -0.051417 | 0.020767 | 61.5753 | -0.001436 | 61.3764 | 61.5034 | 61.4326 | 61.4611 | 61.4755 | 61.5048 | 61.4717 | 61.4974 | 123.0468 | 61.6485 | 122.9872 | 61.4217 | 61.4939 | 123.0484 | 61.4716 | 122.8495 | 61.553 | 61.5752 | 61.4934 | 61.5156
847.0625 | 123.2895 | -61.5372 | 61.6241 | 0.034862 | -0.0451 | -0.016578 | 0.007033 | 0.027109 | -0.010563 | 0.024268 | 61.5691 | 0.17537 | 61.4775 | -0.046838 | 0.01161 | 61.5753 | 0.003143 | 61.3718 | 61.572 | 61.4921 | 61.5206 | 61.5442 | 61.5643 | 61.5266 | 61.5614 | 123.1063 | 61.7125 | 123.0147 | 61.4903 | 61.5488 | 123.1125 | 61.5403 | 122.909 | 61.5575 | 61.566 | 61.4659 | 61.4744
848.0625 | 123.2254 | -61.5005 | 61.6745 | 0.030283 | -0.049678 | -0.016578 | 0.007033 | 0.031687 | -0.005985 | 0.024268 | 61.5691 | 0.16622 | 61.4638 | -0.046838 | 0.025345 | 61.5753 | -0.001436 | 61.3764 | 61.5308 | 61.4509 | 61.484 | 61.5076 | 61.5322 | 61.4946 | 61.5248 | 123.0697 | 61.6668 | 122.9643 | 61.4537 | 61.5259 | 123.0759 | 61.4991 | 122.8769 | 61.5438 | 61.5706 | 61.4384 | 61.4652
849.0625 | 123.2803 | -61.4868 | 61.6745 | 0.030283 | -0.0451 | -0.021157 | 0.002454 | 0.027109 | -0.005985 | 0.01969 | 61.5737 | 0.17079 | 61.45 | -0.055996 | 0.020767 | 61.5707 | 0.003143 | 61.3718 | 61.5171 | 61.4417 | 61.4657 | 61.4893 | 61.5139 | 61.4808 | 61.5065 | 123.0605 | 61.6576 | 122.9369 | 61.4308 | 61.5076 | 123.0576 | 61.49 | 122.8586 | 61.553 | 61.5706 | 61.4293 | 61.4469
850.0625 | 123.3902 | -61.4914 | 61.5784 | 0.030283 | -0.040521 | -0.012 | 0.002454 | 0.027109 | 0.00775 | 0.024268 | 61.5691 | 0.17995 | 61.45 | -0.051417 | 0.020767 | 61.5799 | 0.007721 | 61.3764 | 61.5217 | 61.4509 | 61.4794 | 61.4938 | 61.5185 | 61.4991 | 61.5157 | 123.0605 | 61.6713 | 122.9414 | 61.44 | 61.5122 | 123.0713 | 61.4991 | 122.8678 | 61.5484 | 61.5614 | 61.4293 | 61.4423
851.0469 | 123.2895 | -61.4685 | 61.6653 | 0.030283 | -0.0451 | -0.021157 | 0.002454 | 0.036265 | 0.003172 | 0.024268 | 61.5737 | 0.17079 | 61.4684 | -0.042259 | 0.025345 | 61.5707 | 0.007721 | 61.3718 | 61.4988 | 61.4234 | 61.4473 | 61.471 | 61.5048 | 61.4717 | 61.4928 | 123.0422 | 61.6393 | 122.9369 | 61.4262 | 61.4939 | 123.0392 | 61.4762 | 122.8403 | 61.5484 | 61.566 | 61.443 | 61.4606
852.0625 | 123.3994 | -61.4594 | 61.6013 | 0.034862 | -0.040521 | -0.021157 | -0.002124 | 0.027109 | -0.001406 | 0.024268 | 61.5737 | 0.17995 | 61.4912 | -0.051417 | 0.020767 | 61.5753 | 0.003143 | 61.3672 | 61.4942 | 61.4188 | 61.4382 | 61.4572 | 61.4865 | 61.4579 | 61.4836 | 123.0331 | 61.6393 | 122.9506 | 61.4079 | 61.4801 | 123.0347 | 61.4625 | 122.8266 | 61.553 | 61.5706 | 61.4705 | 61.4881
853.0625 | 123.2712 | -61.4822 | 61.6608 | 0.034862 | -0.040521 | -0.021157 | 0.002454 | 0.031687 | -0.005985 | 0.033424 | 61.5691 | 0.17537 | 61.4958 | -0.042259 | 0.016188 | 61.5753 | -0.001436 | 61.381 | 61.5171 | 61.4417 | 61.4611 | 61.4847 | 61.5139 | 61.4763 | 61.5157 | 123.0514 | 61.6576 | 122.9781 | 61.44 | 61.4984 | 123.0576 | 61.4808 | 122.8632 | 61.553 | 61.5706 | 61.4796 | 61.4973
854.0625 | 123.2574 | -61.496 | 61.6196 | 0.025705 | -0.040521 | -0.012 | 0.002454 | 0.027109 | -0.005985 | 0.024268 | 61.5829 | 0.17537 | 61.5187 | -0.046838 | 0.025345 | 61.5707 | 0.003143 | 61.3718 | 61.5217 | 61.4555 | 61.484 | 61.4984 | 61.5231 | 61.49 | 61.5202 | 123.0789 | 61.6713 | 123.0147 | 61.4491 | 61.5213 | 123.0667 | 61.4991 | 122.8678 | 61.5575 | 61.5797 | 61.4934 | 61.5156
855.0625 | 123.317 | -61.4594 | 61.5829 | 0.030283 | -0.049678 | -0.012 | -0.002124 | 0.031687 | -0.005985 | 0.01969 | 61.5737 | 0.16622 | 61.4729 | -0.055996 | 0.020767 | 61.5707 | 0.003143 | 61.3764 | 61.4896 | 61.4097 | 61.4474 | 61.4572 | 61.491 | 61.4534 | 61.479 | 123.0331 | 61.6256 | 122.9323 | 61.4034 | 61.4801 | 123.0301 | 61.4625 | 122.8357 | 61.553 | 61.5706 | 61.4522 | 61.4698
856.0781 | 123.2712 | -61.4868 | 61.647 | 0.030283 | -0.040521 | -0.016578 | -0.006703 | 0.022531 | 0.003172 | 0.024268 | 61.5737 | 0.16622 | 61.4592 | -0.055996 | 0.01161 | 61.5707 | 0.007721 | 61.3764 | 61.5171 | 61.4463 | 61.4702 | 61.4801 | 61.5093 | 61.49 | 61.5111 | 123.0605 | 61.653 | 122.946 | 61.4308 | 61.4984 | 123.0576 | 61.4945 | 122.8632 | 61.5621 | 61.566 | 61.4476 | 61.4515
857.375 | 123.3765 | -61.4319 | 61.615 | 0.030283 | -0.049678 | -0.016578 | -0.002124 | 0.031687 | -0.005985 | 0.024268 | 61.5783 | 0.17079 | 61.4546 | -0.051417 | 0.025345 | 61.5799 | 0.003143 | 61.381 | 61.4622 | 61.3822 | 61.4153 | 61.4298 | 61.4636 | 61.4259 | 61.4562 | 123.0102 | 61.6027 | 122.8865 | 61.3805 | 61.4572 | 123.0118 | 61.435 | 122.8129 | 61.553 | 61.5752 | 61.4293 | 61.4515
858.2656 | 123.381 | -61.4502 | 61.6058 | 0.030283 | -0.040521 | -0.007421 | -0.011281 | 0.027109 | -0.005985 | 0.01969 | 61.5691 | 0.17537 | 61.45 | -0.051417 | 0.029923 | 61.5753 | -0.001436 | 61.381 | 61.4805 | 61.4097 | 61.4428 | 61.4389 | 61.4773 | 61.4442 | 61.4699 | 123.0193 | 61.6256 | 122.9002 | 61.3988 | 61.4801 | 123.0255 | 61.4488 | 122.8312 | 61.5392 | 61.5706 | 61.4201 | 61.4515
859.1094 | 123.3536 | -61.4685 | 61.5784 | 0.030283 | -0.0451 | -0.012 | 0.007033 | 0.022531 | 0.003172 | 0.01969 | 61.5737 | 0.17079 | 61.45 | -0.051417 | 0.016188 | 61.5707 | -0.006014 | 61.3764 | 61.4988 | 61.4234 | 61.4565 | 61.4755 | 61.491 | 61.4717 | 61.4882 | 123.0422 | 61.6393 | 122.9185 | 61.4171 | 61.4847 | 123.0392 | 61.4625 | 122.8449 | 61.5575 | 61.5797 | 61.4339 | 61.4561
860.0781 | 123.349 | -61.4273 | 61.6379 | 0.025705 | -0.040521 | -0.012 | 0.007033 | 0.031687 | -0.001406 | 0.024268 | 61.5691 | 0.17079 | 61.4684 | -0.046838 | 0.016188 | 61.5753 | -0.001436 | 61.3764 | 61.453 | 61.3868 | 61.4153 | 61.4343 | 61.459 | 61.4259 | 61.4516 | 122.9965 | 61.5981 | 122.8957 | 61.3805 | 61.4435 | 123.0026 | 61.4259 | 122.8037 | 61.553 | 61.5706 | 61.4522 | 61.4698
861.0625 | 123.2758 | -61.5005 | 61.6516 | 0.025705 | -0.0451 | -0.016578 | 0.002454 | 0.027109 | 0.00775 | 0.028846 | 61.5737 | 0.17537 | 61.4958 | -0.055996 | 0.016188 | 61.5707 | -0.001436 | 61.381 | 61.5263 | 61.4554 | 61.484 | 61.503 | 61.5277 | 61.5083 | 61.5294 | 123.0743 | 61.6759 | 122.9964 | 61.4446 | 61.5167 | 123.0713 | 61.4991 | 122.8815 | 61.5575 | 61.5752 | 61.4796 | 61.4973
862.0625 | 123.3353 | -61.4639 | 61.6104 | 0.030283 | -0.040521 | -0.021157 | 0.002454 | 0.022531 | -0.001406 | 0.01969 | 61.5737 | 0.17537 | 61.5096 | -0.051417 | 0.020767 | 61.5753 | 0.003143 | 61.3764 | 61.4942 | 61.4234 | 61.4428 | 61.4664 | 61.4865 | 61.4625 | 61.4836 | 123.0377 | 61.6393 | 122.9735 | 61.4125 | 61.4847 | 123.0392 | 61.4671 | 122.8403 | 61.553 | 61.5706 | 61.4888 | 61.5064
863.0625 | 123.3673 | -61.4685 | 61.615 | 0.025705 | -0.049678 | -0.016578 | -0.002124 | 0.031687 | 0.003172 | 0.024268 | 61.5783 | 0.17079 | 61.5141 | -0.051417 | 0.020767 | 61.5707 | 0.007721 | 61.3718 | 61.4942 | 61.4188 | 61.4519 | 61.4664 | 61.5002 | 61.4717 | 61.4928 | 123.0468 | 61.6393 | 122.9826 | 61.4171 | 61.4893 | 123.0392 | 61.4762 | 122.8403 | 61.5575 | 61.5706 | 61.4934 | 61.5064
864.0625 | 123.3078 | -61.4548 | 61.6333 | 0.034862 | -0.0451 | -0.007421 | 0.002454 | 0.031687 | -0.005985 | 0.024268 | 61.5737 | 0.16622 | 61.4775 | -0.051417 | 0.020767 | 61.5753 | 0.012299 | 61.3718 | 61.4896 | 61.4097 | 61.4474 | 61.4572 | 61.4865 | 61.4488 | 61.479 | 123.0285 | 61.621 | 122.9323 | 61.4034 | 61.4755 | 123.0301 | 61.4671 | 122.8266 | 61.553 | 61.5614 | 61.4567 | 61.4652
865.0781 | 123.3582 | -61.4594 | 61.615 | 0.034862 | -0.040521 | -0.016578 | 0.002454 | 0.027109 | -0.001406 | 0.024268 | 61.5691 | 0.17079 | 61.4684 | -0.051417 | 0.020767 | 61.5707 | 0.003143 | 61.3764 | 61.4942 | 61.4188 | 61.4428 | 61.4618 | 61.4865 | 61.4579 | 61.4836 | 123.0285 | 61.6301 | 122.9277 | 61.4079 | 61.4801 | 123.0301 | 61.4625 | 122.8357 | 61.5484 | 61.566 | 61.4476 | 61.4652
866.0625 | 123.3673 | -61.4868 | 61.6287 | 0.025705 | -0.040521 | -0.021157 | -0.006703 | 0.027109 | -0.001406 | 0.028846 | 61.5737 | 0.16622 | 61.4592 | -0.051417 | 0.016188 | 61.5707 | 0.007721 | 61.381 | 61.5125 | 61.4463 | 61.4657 | 61.4801 | 61.5139 | 61.4854 | 61.5157 | 123.0605 | 61.653 | 122.946 | 61.4354 | 61.503 | 123.0576 | 61.4945 | 122.8678 | 61.5575 | 61.566 | 61.443 | 61.4515
867.0781 | 123.3719 | -61.4548 | 61.5829 | 0.034862 | -0.040521 | -0.012 | -0.002124 | 0.027109 | -0.005985 | 0.024268 | 61.5646 | 0.17079 | 61.4546 | -0.055996 | 0.020767 | 61.5707 | 0.003143 | 61.3764 | 61.4896 | 61.4143 | 61.4428 | 61.4526 | 61.4819 | 61.4488 | 61.479 | 123.0193 | 61.6256 | 122.9094 | 61.3988 | 61.4755 | 123.0255 | 61.4579 | 122.8312 | 61.5438 | 61.5614 | 61.4339 | 61.4515
868.0625 | 123.3353 | -61.4456 | 61.6379 | 0.030283 | -0.040521 | -0.016578 | 0.007033 | 0.031687 | -0.001406 | 0.01969 | 61.5691 | 0.16622 | 61.4638 | -0.055996 | 0.020767 | 61.5753 | -0.006014 | 61.3856 | 61.4759 | 61.4051 | 61.429 | 61.4527 | 61.4773 | 61.4442 | 61.4653 | 123.0148 | 61.6118 | 122.9094 | 61.3896 | 61.4664 | 123.0209 | 61.4396 | 122.8312 | 61.5484 | 61.5752 | 61.443 | 61.4698
869.0625 | 123.2712 | -61.496 | 61.6425 | 0.025705 | -0.0451 | -0.016578 | 0.007033 | 0.027109 | -0.005985 | 0.015112 | 61.5646 | 0.17079 | 61.4684 | -0.051417 | 0.025345 | 61.5799 | -0.001436 | 61.3856 | 61.5217 | 61.4509 | 61.4794 | 61.503 | 61.5231 | 61.49 | 61.5111 | 123.0605 | 61.6668 | 122.9643 | 61.4446 | 61.5213 | 123.0759 | 61.4945 | 122.8815 | 61.5392 | 61.566 | 61.443 | 61.4698
870.0625 | 123.3032 | -61.4731 | 61.6241 | 0.021127 | -0.049678 | -0.021157 | 0.002454 | 0.031687 | -0.005985 | 0.024268 | 61.5829 | 0.17537 | 61.505 | -0.051417 | 0.016188 | 61.5707 | 0.007721 | 61.3718 | 61.4942 | 61.4234 | 61.4519 | 61.4755 | 61.5048 | 61.4671 | 61.4974 | 123.056 | 61.6485 | 122.9781 | 61.4217 | 61.4893 | 123.0438 | 61.4808 | 122.8449 | 61.5667 | 61.5752 | 61.4888 | 61.4973
871.0625 | 123.3719 | -61.4502 | 61.5967 | 0.021127 | -0.035942 | -0.016578 | 0.007033 | 0.027109 | -0.001406 | 0.01969 | 61.5829 | 0.17537 | 61.4912 | -0.046838 | 0.01161 | 61.5799 | 0.007721 | 61.3718 | 61.4713 | 61.4143 | 61.4336 | 61.4572 | 61.4773 | 61.4488 | 61.4699 | 123.0331 | 61.6256 | 122.9414 | 61.4034 | 61.4618 | 123.0301 | 61.4579 | 122.822 | 61.5713 | 61.5752 | 61.4796 | 61.4835
872.0625 | 123.2391 | -61.4731 | 61.6699 | 0.034862 | -0.049678 | -0.016578 | -0.002124 | 0.027109 | 0.003172 | 0.033424 | 61.5783 | 0.16164 | 61.4867 | -0.051417 | 0.016188 | 61.5799 | 0.003143 | 61.3764 | 61.5079 | 61.4234 | 61.4565 | 61.471 | 61.5002 | 61.4763 | 61.5065 | 123.0514 | 61.6347 | 122.9597 | 61.4217 | 61.4893 | 123.053 | 61.4762 | 122.8495 | 61.5621 | 61.5752 | 61.4705 | 61.4835
873.0625 | 123.3444 | -61.4639 | 61.6196 | 0.025705 | -0.040521 | -0.016578 | 0.002454 | 0.027109 | -0.005985 | 0.024268 | 61.5691 | 0.16622 | 61.4592 | -0.051417 | 0.020767 | 61.5753 | 0.003143 | 61.3764 | 61.4896 | 61.4234 | 61.4474 | 61.4664 | 61.491 | 61.4579 | 61.4882 | 123.0331 | 61.6301 | 122.9231 | 61.4125 | 61.4847 | 123.0392 | 61.4671 | 122.8403 | 61.5484 | 61.566 | 61.4384 | 61.4561
874.0625 | 123.3994 | -61.4182 | 61.6196 | 0.025705 | -0.049678 | -0.012 | -0.002124 | 0.031687 | -0.005985 | 0.024268 | 61.5737 | 0.17079 | 61.4638 | -0.046838 | 0.020767 | 61.557 | 0.007721 | 61.381 | 61.4439 | 61.3685 | 61.4062 | 61.416 | 61.4498 | 61.4122 | 61.4424 | 122.9919 | 61.5889 | 122.8819 | 61.3713 | 61.4389 | 122.9752 | 61.4259 | 122.7991 | 61.553 | 61.566 | 61.443 | 61.4561
875.0625 | 123.3582 | -61.496 | 61.6287 | 0.030283 | -0.035942 | -0.016578 | -0.006703 | 0.022531 | -0.001406 | 0.024268 | 61.5691 | 0.17537 | 61.505 | -0.046838 | 0.020767 | 61.5753 | 0.003143 | 61.3672 | 61.5263 | 61.46 | 61.4794 | 61.4893 | 61.5185 | 61.4946 | 61.5202 | 123.0651 | 61.6713 | 123.001 | 61.4491 | 61.5167 | 123.0713 | 61.4991 | 122.8632 | 61.5484 | 61.566 | 61.4842 | 61.5018
876.0625 | 123.3215 | -61.4685 | 61.6562 | 0.025705 | -0.040521 | -0.016578 | -0.002124 | 0.022531 | -0.005985 | 0.01969 | 61.5737 | 0.17537 | 61.5096 | -0.051417 | 0.020767 | 61.5753 | -0.001436 | 61.3718 | 61.4942 | 61.428 | 61.4519 | 61.4664 | 61.491 | 61.4625 | 61.4882 | 123.0422 | 61.6439 | 122.9781 | 61.4171 | 61.4893 | 123.0438 | 61.4671 | 122.8403 | 61.553 | 61.5752 | 61.4888 | 61.511
877.0625 | 123.349 | -61.4639 | 61.647 | 0.030283 | -0.040521 | -0.025735 | 0.002454 | 0.022531 | 0.003172 | 0.024268 | 61.5691 | 0.17537 | 61.4684 | -0.046838 | 0.020767 | 61.5707 | 0.003143 | 61.3764 | 61.4942 | 61.4234 | 61.4382 | 61.4664 | 61.4865 | 61.4671 | 61.4882 | 123.0331 | 61.6393 | 122.9323 | 61.4171 | 61.4847 | 123.0347 | 61.4671 | 122.8403 | 61.5484 | 61.566 | 61.4476 | 61.4652
878.0625 | 123.4039 | -61.4548 | 61.5967 | 0.025705 | -0.040521 | -0.021157 | 0.007033 | 0.027109 | -0.010563 | 0.028846 | 61.5737 | 0.17537 | 61.4546 | -0.046838 | 0.01161 | 61.5753 | 0.007721 | 61.3718 | 61.4805 | 61.4143 | 61.4336 | 61.4618 | 61.4819 | 61.4442 | 61.4836 | 123.0285 | 61.6301 | 122.9094 | 61.4079 | 61.4664 | 123.0301 | 61.4625 | 122.8266 | 61.5621 | 61.566 | 61.443 | 61.4469
879.0625 | 123.4039 | -61.4456 | 61.6104 | 0.025705 | -0.040521 | -0.021157 | 0.002454 | 0.027109 | -0.001406 | 0.028846 | 61.5783 | 0.16622 | 61.4867 | -0.051417 | 0.020767 | 61.5707 | 0.007721 | 61.3718 | 61.4713 | 61.4051 | 61.4245 | 61.4481 | 61.4727 | 61.4442 | 61.4745 | 123.0239 | 61.6118 | 122.9323 | 61.3942 | 61.4664 | 123.0164 | 61.4533 | 122.8174 | 61.5575 | 61.5706 | 61.4659 | 61.4789
880.0625 | 123.2483 | -61.5189 | 61.6241 | 0.034862 | -0.040521 | -0.012 | 0.002454 | 0.027109 | 0.003172 | 0.028846 | 61.5829 | 0.17537 | 61.5141 | -0.051417 | 0.016188 | 61.5753 | 0.003143 | 61.3627 | 61.5537 | 61.4783 | 61.5069 | 61.5213 | 61.546 | 61.522 | 61.5477 | 123.1017 | 61.6942 | 123.033 | 61.4674 | 61.535 | 123.0942 | 61.522 | 122.8815 | 61.5667 | 61.5797 | 61.4979 | 61.511
881.0625 | 123.3582 | -61.4594 | 61.6058 | 0.034862 | -0.040521 | -0.016578 | -0.002124 | 0.027109 | 0.003172 | 0.024268 | 61.5829 | 0.17079 | 61.505 | -0.042259 | 0.020767 | 61.5753 | 0.007721 | 61.3764 | 61.4942 | 61.4188 | 61.4428 | 61.4572 | 61.4865 | 61.4625 | 61.4836 | 123.0422 | 61.6301 | 122.9643 | 61.4171 | 61.4801 | 123.0347 | 61.4671 | 122.8357 | 61.5621 | 61.5752 | 61.4842 | 61.4973
882.0625 | 123.4131 | -61.4639 | 61.6196 | 0.025705 | -0.040521 | -0.016578 | 0.002454 | 0.031687 | -0.001406 | 0.024268 | 61.56 | 0.17537 | 61.4684 | -0.051417 | 0.020767 | 61.5753 | 0.007721 | 61.3718 | 61.4896 | 61.4234 | 61.4474 | 61.4664 | 61.4956 | 61.4625 | 61.4882 | 123.0239 | 61.6393 | 122.9323 | 61.4125 | 61.4847 | 123.0392 | 61.4716 | 122.8357 | 61.5392 | 61.5523 | 61.4476 | 61.4606
883.0625 | 123.2849 | -61.4731 | 61.6379 | 0.034862 | -0.035942 | -0.021157 | 0.007033 | 0.036265 | -0.005985 | 0.024268 | 61.5783 | 0.17079 | 61.4684 | -0.051417 | 0.020767 | 61.5799 | 0.007721 | 61.3764 | 61.5079 | 61.4371 | 61.4519 | 61.4801 | 61.5093 | 61.4671 | 61.4974 | 123.0514 | 61.6439 | 122.9414 | 61.4217 | 61.4939 | 123.053 | 61.4808 | 122.8495 | 61.5575 | 61.5706 | 61.4476 | 61.4606
884.0625 | 123.349 | -61.4868 | 61.6013 | 0.030283 | -0.040521 | -0.007421 | 0.007033 | 0.027109 | -0.001406 | 0.028846 | 61.5646 | 0.17537 | 61.4592 | -0.051417 | 0.020767 | 61.5707 | 0.003143 | 61.3672 | 61.5171 | 61.4463 | 61.4794 | 61.4938 | 61.5139 | 61.4854 | 61.5157 | 123.0514 | 61.6622 | 122.946 | 61.4354 | 61.5076 | 123.0576 | 61.49 | 122.8541 | 61.5438 | 61.5614 | 61.4384 | 61.4561
885.0625 | 123.3536 | -61.4502 | 61.6287 | 0.030283 | -0.0451 | -0.012 | -0.002124 | 0.027109 | 0.003172 | 0.024268 | 61.5737 | 0.16622 | 61.4638 | -0.055996 | 0.020767 | 61.5799 | 0.012299 | 61.3718 | 61.4805 | 61.4051 | 61.4382 | 61.4481 | 61.4773 | 61.4534 | 61.4745 | 123.0239 | 61.6164 | 122.914 | 61.3942 | 61.471 | 123.0301 | 61.4625 | 122.822 | 61.553 | 61.5614 | 61.443 | 61.4515
886.0625 | 123.2849 | -61.4594 | 61.647 | 0.030283 | -0.0451 | -0.012 | 0.002454 | 0.027109 | -0.001406 | 0.028846 | 61.5737 | 0.17079 | 61.4775 | -0.055996 | 0.01161 | 61.5753 | 0.007721 | 61.3672 | 61.4896 | 61.4143 | 61.4474 | 61.4618 | 61.4865 | 61.4579 | 61.4882 | 123.0331 | 61.6301 | 122.9369 | 61.4034 | 61.471 | 123.0347 | 61.4671 | 122.8266 | 61.5621 | 61.566 | 61.4659 | 61.4698
887.0625 | 123.3673 | -61.4273 | 61.6241 | 0.030283 | -0.049678 | -0.007421 | 0.002454 | 0.027109 | -0.001406 | 0.024268 | 61.5829 | 0.17537 | 61.5096 | -0.055996 | 0.029923 | 61.5707 | 0.003143 | 61.3718 | 61.4576 | 61.3776 | 61.4199 | 61.4298 | 61.4544 | 61.4259 | 61.4516 | 123.0102 | 61.6027 | 122.9369 | 61.3713 | 61.4572 | 122.998 | 61.4305 | 122.7991 | 61.553 | 61.5797 | 61.4796 | 61.5064
888.0625 | 123.4085 | -61.4273 | 61.6241 | 0.030283 | -0.040521 | -0.016578 | -0.002124 | 0.022531 | -0.001406 | 0.01969 | 61.5783 | 0.17079 | 61.4912 | -0.046838 | 0.020767 | 61.5616 | 0.003143 | 61.3764 | 61.4576 | 61.3868 | 61.4107 | 61.4252 | 61.4498 | 61.4259 | 61.447 | 123.0056 | 61.5981 | 122.9186 | 61.3805 | 61.4481 | 122.9889 | 61.4305 | 122.8037 | 61.5575 | 61.5752 | 61.4705 | 61.4881
889.0625 | 123.2574 | -61.4777 | 61.6287 | 0.034862 | -0.040521 | -0.007421 | 0.002454 | 0.027109 | -0.001406 | 0.028846 | 61.5691 | 0.17537 | 61.4912 | -0.055996 | 0.020767 | 61.5753 | 0.003143 | 61.3672 | 61.5125 | 61.4371 | 61.4702 | 61.4801 | 61.5048 | 61.4763 | 61.5065 | 123.0468 | 61.653 | 122.9689 | 61.4217 | 61.4984 | 123.053 | 61.4808 | 122.8449 | 61.5484 | 61.566 | 61.4705 | 61.4881
890.0625 | 123.3582 | -61.4914 | 61.6058 | 0.025705 | -0.049678 | -0.016578 | -0.002124 | 0.027109 | -0.005985 | 0.024268 | 61.5737 | 0.16622 | 61.4684 | -0.046838 | 0.016188 | 61.5799 | 0.003143 | 61.3718 | 61.5171 | 61.4417 | 61.4748 | 61.4893 | 61.5185 | 61.4854 | 61.5157 | 123.0651 | 61.6576 | 122.9597 | 61.4446 | 61.5076 | 123.0713 | 61.4945 | 122.8632 | 61.5575 | 61.5706 | 61.4522 | 61.4652
891.0625 | 123.349 | -61.4914 | 61.6333 | 0.030283 | -0.0451 | -0.012 | 0.007033 | 0.036265 | -0.001406 | 0.01969 | 61.5691 | 0.17537 | 61.4546 | -0.051417 | 0.016188 | 61.5707 | -0.001436 | 61.3672 | 61.5217 | 61.4463 | 61.4794 | 61.4984 | 61.5277 | 61.49 | 61.5111 | 123.0605 | 61.6668 | 122.946 | 61.44 | 61.5076 | 123.0621 | 61.49 | 122.8586 | 61.553 | 61.5706 | 61.4384 | 61.4561
892.0625 | 123.2849 | -61.5005 | 61.6333 | 0.030283 | -0.040521 | -0.016578 | 0.002454 | 0.031687 | 0.003172 | 0.033424 | 61.5691 | 0.17079 | 61.4546 | -0.051417 | 0.020767 | 61.5707 | -0.001436 | 61.3764 | 61.5308 | 61.46 | 61.484 | 61.503 | 61.5322 | 61.5037 | 61.534 | 123.0697 | 61.6713 | 122.9552 | 61.4491 | 61.5213 | 123.0713 | 61.4991 | 122.8769 | 61.5484 | 61.5706 | 61.4339 | 61.4561
893.0625 | 123.2574 | -61.4914 | 61.6745 | 0.030283 | -0.040521 | -0.021157 | 0.002454 | 0.027109 | 0.003172 | 0.024268 | 61.5737 | 0.17079 | 61.4638 | -0.042259 | 0.020767 | 61.5707 | 0.007721 | 61.3718 | 61.5217 | 61.4509 | 61.4702 | 61.4938 | 61.5185 | 61.4946 | 61.5157 | 123.0651 | 61.6622 | 122.9552 | 61.4491 | 61.5122 | 123.0621 | 61.4991 | 122.8632 | 61.553 | 61.566 | 61.443 | 61.4561
894.0625 | 123.2346 | -61.4914 | 61.647 | 0.030283 | -0.035942 | -0.016578 | 0.007033 | 0.027109 | -0.005985 | 0.01969 | 61.5783 | 0.17079 | 61.4867 | -0.046838 | 0.020767 | 61.5753 | 0.012299 | 61.3764 | 61.5217 | 61.4555 | 61.4748 | 61.4984 | 61.5185 | 61.4854 | 61.5111 | 123.0697 | 61.6622 | 122.9781 | 61.4446 | 61.5122 | 123.0667 | 61.5037 | 122.8678 | 61.5575 | 61.566 | 61.4659 | 61.4744
895.0625 | 123.3307 | -61.4822 | 61.6058 | 0.034862 | -0.040521 | -0.016578 | -0.011281 | 0.027109 | 0.003172 | 0.024268 | 61.5737 | 0.17537 | 61.505 | -0.051417 | 0.020767 | 61.5707 | 0.003143 | 61.3718 | 61.5171 | 61.4417 | 61.4657 | 61.471 | 61.5093 | 61.4854 | 61.5065 | 123.056 | 61.6576 | 122.9872 | 61.4308 | 61.503 | 123.053 | 61.4854 | 122.8541 | 61.553 | 61.5706 | 61.4842 | 61.5018
896.0625 | 123.3398 | -61.4548 | 61.6287 | 0.034862 | -0.040521 | -0.012 | -0.002124 | 0.027109 | -0.010563 | 0.024268 | 61.5691 | 0.16164 | 61.5187 | -0.046838 | 0.020767 | 61.5707 | 0.003143 | 61.3718 | 61.4896 | 61.4143 | 61.4428 | 61.4526 | 61.4819 | 61.4442 | 61.479 | 123.0239 | 61.6164 | 122.9735 | 61.4079 | 61.4755 | 123.0255 | 61.4579 | 122.8266 | 61.5484 | 61.566 | 61.4979 | 61.5156
897.0625 | 123.3124 | -61.4548 | 61.647 | 0.034862 | -0.035942 | -0.016578 | -0.002124 | 0.031687 | -0.001406 | 0.028846 | 61.5737 | 0.17079 | 61.4729 | -0.055996 | 0.029923 | 61.5707 | 0.003143 | 61.3764 | 61.4896 | 61.4188 | 61.4382 | 61.4526 | 61.4865 | 61.4534 | 61.4836 | 123.0285 | 61.6256 | 122.9277 | 61.3988 | 61.4847 | 123.0255 | 61.4579 | 122.8312 | 61.5438 | 61.5706 | 61.443 | 61.4698
898.0625 | 123.2849 | -61.4639 | 61.6333 | 0.034862 | -0.031363 | -0.012 | 0.002454 | 0.031687 | -0.001406 | 0.028846 | 61.5783 | 0.17079 | 61.4684 | -0.046838 | 0.016188 | 61.5707 | 0.003143 | 61.381 | 61.4988 | 61.4326 | 61.4519 | 61.4664 | 61.4956 | 61.4625 | 61.4928 | 123.0422 | 61.6347 | 122.9323 | 61.4171 | 61.4801 | 123.0347 | 61.4671 | 122.8449 | 61.5621 | 61.5752 | 61.4522 | 61.4652
899.0625 | 123.3078 | -61.4822 | 61.647 | 0.021127 | -0.0451 | -0.021157 | 0.007033 | 0.036265 | -0.005985 | 0.033424 | 61.5737 | 0.17537 | 61.4592 | -0.046838 | 0.029923 | 61.5662 | 0.003143 | 61.381 | 61.5034 | 61.4371 | 61.4611 | 61.4893 | 61.5185 | 61.4763 | 61.5157 | 123.056 | 61.6576 | 122.9414 | 61.4354 | 61.5122 | 123.0484 | 61.4854 | 122.8632 | 61.5438 | 61.5706 | 61.4293 | 61.4561
900.0625 | 123.2666 | -61.496 | 61.6653 | 0.030283 | -0.040521 | -0.016578 | 0.002454 | 0.031687 | 0.003172 | 0.01969 | 61.56 | 0.17079 | 61.4684 | -0.051417 | 0.025345 | 61.5707 | 0.007721 | 61.3764 | 61.5263 | 61.4555 | 61.4794 | 61.4984 | 61.5277 | 61.4991 | 61.5157 | 123.056 | 61.6668 | 122.9643 | 61.4446 | 61.5213 | 123.0667 | 61.5037 | 122.8724 | 61.5346 | 61.5523 | 61.443 | 61.4606
901.0625 | 123.2666 | -61.4914 | 61.6058 | 0.030283 | -0.035942 | -0.021157 | 0.002454 | 0.031687 | 0.003172 | 0.01969 | 61.5783 | 0.17537 | 61.4729 | -0.046838 | 0.020767 | 61.5753 | 0.007721 | 61.3764 | 61.5217 | 61.4555 | 61.4702 | 61.4938 | 61.5231 | 61.4946 | 61.5111 | 123.0697 | 61.6668 | 122.9643 | 61.4446 | 61.5122 | 123.0667 | 61.4991 | 122.8678 | 61.5575 | 61.5706 | 61.4522 | 61.4652
902.0625 | 123.2758 | -61.4685 | 61.6425 | 0.025705 | -0.035942 | -0.007421 | 0.007033 | 0.031687 | -0.005985 | 0.033424 | 61.5783 | 0.17537 | 61.5096 | -0.046838 | 0.016188 | 61.5707 | -0.001436 | 61.3718 | 61.4942 | 61.4326 | 61.4611 | 61.4755 | 61.5002 | 61.4625 | 61.5019 | 123.0468 | 61.6439 | 122.9781 | 61.4217 | 61.4847 | 123.0392 | 61.4671 | 122.8403 | 61.5621 | 61.5797 | 61.4934 | 61.511
903.0625 | 123.2574 | -61.5051 | 61.6791 | 0.030283 | -0.035942 | -0.012 | 0.002454 | 0.027109 | 0.012329 | 0.028846 | 61.5783 | 0.17537 | 61.505 | -0.055996 | 0.025345 | 61.5799 | -0.001436 | 61.3672 | 61.5354 | 61.4692 | 61.4931 | 61.5076 | 61.5322 | 61.5175 | 61.534 | 123.0834 | 61.6805 | 123.0101 | 61.4491 | 61.5305 | 123.085 | 61.5037 | 122.8724 | 61.553 | 61.5797 | 61.4796 | 61.5064
904.0625 | 123.2895 | -61.4914 | 61.6379 | 0.030283 | -0.035942 | -0.012 | 0.01619 | 0.027109 | -0.001406 | 0.028846 | 61.5829 | 0.17079 | 61.5141 | -0.046838 | 0.016188 | 61.5753 | -0.001436 | 61.3718 | 61.5217 | 61.4555 | 61.4794 | 61.5076 | 61.5185 | 61.49 | 61.5202 | 123.0743 | 61.6622 | 123.0055 | 61.4446 | 61.5076 | 123.0667 | 61.49 | 122.8632 | 61.5667 | 61.5843 | 61.4979 | 61.5156
905.0625 | 123.2437 | -61.4868 | 61.6653 | 0.025705 | -0.031363 | -0.021157 | -0.002124 | 0.022531 | -0.001406 | 0.033424 | 61.5646 | 0.17079 | 61.4775 | -0.046838 | 0.025345 | 61.5707 | 0.003143 | 61.3718 | 61.5125 | 61.4555 | 61.4657 | 61.4847 | 61.5093 | 61.4854 | 61.5202 | 123.0514 | 61.6576 | 122.9643 | 61.44 | 61.5122 | 123.0576 | 61.49 | 122.8586 | 61.5392 | 61.5614 | 61.4522 | 61.4744
906.0625 | 123.317 | -61.4731 | 61.6379 | 0.03944 | -0.035942 | -0.016578 | 0.002454 | 0.031687 | 0.003172 | 0.028846 | 61.5737 | 0.17079 | 61.4592 | -0.051417 | 0.029923 | 61.5662 | 0.003143 | 61.3718 | 61.5125 | 61.4371 | 61.4565 | 61.4755 | 61.5048 | 61.4763 | 61.5019 | 123.0468 | 61.6439 | 122.9323 | 61.4217 | 61.503 | 123.0392 | 61.4762 | 122.8449 | 61.5438 | 61.5706 | 61.4293 | 61.4561
907.0625 | 123.23 | -61.5097 | 61.6241 | 0.030283 | -0.040521 | -0.007421 | 0.007033 | 0.027109 | -0.001406 | 0.028846 | 61.5554 | 0.17079 | 61.4592 | -0.055996 | 0.01161 | 61.5662 | -0.001436 | 61.3718 | 61.54 | 61.4692 | 61.5023 | 61.5167 | 61.5368 | 61.5083 | 61.5386 | 123.0651 | 61.6805 | 122.9689 | 61.4537 | 61.5213 | 123.0759 | 61.5083 | 122.8815 | 61.5438 | 61.5568 | 61.4476 | 61.4606
908.0625 | 123.3124 | -61.5097 | 61.647 | 0.025705 | -0.040521 | -0.012 | 0.002454 | 0.031687 | -0.001406 | 0.028846 | 61.5737 | 0.17995 | 61.4684 | -0.051417 | 0.016188 | 61.5707 | 0.003143 | 61.381 | 61.5354 | 61.4692 | 61.4977 | 61.5122 | 61.5414 | 61.5083 | 61.5386 | 123.0834 | 61.6897 | 122.9781 | 61.4583 | 61.5259 | 123.0804 | 61.5128 | 122.8907 | 61.5575 | 61.5706 | 61.4522 | 61.4652
909.0625 | 123.2986 | -61.4594 | 61.6653 | 0.03944 | -0.035942 | -0.012 | 0.002454 | 0.031687 | 0.003172 | 0.028846 | 61.5691 | 0.17537 | 61.4775 | -0.046838 | 0.020767 | 61.5662 | 0.007721 | 61.3672 | 61.4988 | 61.4234 | 61.4474 | 61.4618 | 61.491 | 61.4625 | 61.4882 | 123.0285 | 61.6347 | 122.9369 | 61.4125 | 61.4801 | 123.0255 | 61.4671 | 122.8266 | 61.5484 | 61.5614 | 61.4567 | 61.4698
910.0625 | 123.349 | -61.4731 | 61.5738 | 0.03944 | -0.040521 | -0.016578 | 0.007033 | 0.031687 | 0.003172 | 0.028846 | 61.5737 | 0.17079 | 61.5141 | -0.051417 | 0.020767 | 61.5707 | 0.007721 | 61.3672 | 61.5125 | 61.4326 | 61.4565 | 61.4801 | 61.5048 | 61.4763 | 61.5019 | 123.0468 | 61.6439 | 122.9872 | 61.4217 | 61.4939 | 123.0438 | 61.4808 | 122.8403 | 61.553 | 61.566 | 61.4934 | 61.5064
911.0625 | 123.4131 | -61.4685 | 61.6104 | 0.034862 | -0.040521 | -0.012 | -0.002124 | 0.027109 | -0.005985 | 0.024268 | 61.5737 | 0.16622 | 61.5233 | -0.051417 | 0.020767 | 61.5707 | 0.003143 | 61.3764 | 61.5034 | 61.428 | 61.4565 | 61.4664 | 61.4956 | 61.4625 | 61.4928 | 123.0422 | 61.6347 | 122.9918 | 61.4171 | 61.4893 | 123.0392 | 61.4716 | 122.8449 | 61.553 | 61.5706 | 61.5025 | 61.5202
912.0625 | 123.2895 | -61.4685 | 61.6516 | 0.021127 | -0.0451 | -0.016578 | 0.002454 | 0.022531 | -0.001406 | 0.024268 | 61.5783 | 0.17537 | 61.5096 | -0.042259 | 0.016188 | 61.5707 | -0.001436 | 61.381 | 61.4896 | 61.4234 | 61.4519 | 61.471 | 61.491 | 61.4671 | 61.4928 | 123.0468 | 61.6439 | 122.9781 | 61.4262 | 61.4847 | 123.0392 | 61.4671 | 122.8495 | 61.5621 | 61.5797 | 61.4934 | 61.511
913.0625 | 123.262 | -61.4914 | 61.6608 | 0.034862 | -0.0451 | -0.012 | 0.002454 | 0.031687 | -0.005985 | 0.028846 | 61.5783 | 0.17079 | 61.4775 | -0.046838 | 0.020767 | 61.5753 | -0.001436 | 61.3672 | 61.5263 | 61.4463 | 61.4794 | 61.4938 | 61.5231 | 61.4854 | 61.5202 | 123.0697 | 61.6622 | 122.9689 | 61.4446 | 61.5122 | 123.0667 | 61.49 | 122.8586 | 61.5575 | 61.5797 | 61.4567 | 61.4789
914.0625 | 123.3078 | -61.4639 | 61.6562 | 0.034862 | -0.0451 | -0.016578 | 0.002454 | 0.036265 | 0.003172 | 0.024268 | 61.5691 | 0.17537 | 61.4684 | -0.042259 | 0.020767 | 61.5707 | 0.003143 | 61.3764 | 61.4988 | 61.4188 | 61.4474 | 61.4664 | 61.5002 | 61.4671 | 61.4882 | 123.0331 | 61.6393 | 122.9323 | 61.4217 | 61.4847 | 123.0347 | 61.4671 | 122.8403 | 61.5484 | 61.566 | 61.4476 | 61.4652
915.0625 | 123.1888 | -61.4822 | 61.6653 | 0.025705 | -0.040521 | -0.007421 | -0.002124 | 0.031687 | -0.010563 | 0.028846 | 61.5783 | 0.17079 | 61.4684 | -0.051417 | 0.020767 | 61.5707 | -0.001436 | 61.3764 | 61.5079 | 61.4417 | 61.4748 | 61.4801 | 61.5139 | 61.4717 | 61.5111 | 123.0605 | 61.653 | 122.9506 | 61.4308 | 61.503 | 123.053 | 61.4808 | 122.8586 | 61.5575 | 61.5797 | 61.4476 | 61.4698
916.0625 | 123.3353 | -61.4639 | 61.5967 | 0.030283 | -0.040521 | -0.016578 | -0.002124 | 0.022531 | -0.001406 | 0.028846 | 61.5691 | 0.17537 | 61.4638 | -0.046838 | 0.016188 | 61.5707 | 0.003143 | 61.3718 | 61.4942 | 61.4234 | 61.4474 | 61.4618 | 61.4865 | 61.4625 | 61.4928 | 123.0331 | 61.6393 | 122.9277 | 61.4171 | 61.4801 | 123.0347 | 61.4671 | 122.8357 | 61.553 | 61.566 | 61.4476 | 61.4606
917.0625 | 123.2666 | -61.4685 | 61.6608 | 0.034862 | -0.0451 | -0.016578 | 0.002454 | 0.031687 | 0.003172 | 0.028846 | 61.5783 | 0.17079 | 61.4775 | -0.051417 | 0.020767 | 61.5753 | 0.003143 | 61.3672 | 61.5034 | 61.4234 | 61.4519 | 61.471 | 61.5002 | 61.4717 | 61.4974 | 123.0468 | 61.6393 | 122.946 | 61.4171 | 61.4893 | 123.0438 | 61.4716 | 122.8357 | 61.5575 | 61.5752 | 61.4567 | 61.4744
918.0625 | 123.2941 | -61.4639 | 61.6699 | 0.034862 | -0.0451 | -0.016578 | 0.002454 | 0.027109 | -0.005985 | 0.028846 | 61.5829 | 0.17537 | 61.505 | -0.051417 | 0.025345 | 61.5707 | -0.001436 | 61.3718 | 61.4988 | 61.4188 | 61.4474 | 61.4664 | 61.491 | 61.4579 | 61.4928 | 123.0468 | 61.6393 | 122.9689 | 61.4125 | 61.4893 | 123.0347 | 61.4625 | 122.8357 | 61.5575 | 61.5843 | 61.4796 | 61.5064
919.0625 | 123.3856 | -61.4731 | 61.5875 | 0.030283 | -0.040521 | -0.016578 | -0.002124 | 0.031687 | -0.005985 | 0.033424 | 61.5737 | 0.17537 | 61.505 | -0.060575 | 0.020767 | 61.5707 | 0.003143 | 61.3672 | 61.5034 | 61.4326 | 61.4565 | 61.471 | 61.5048 | 61.4671 | 61.5065 | 123.0468 | 61.6485 | 122.9781 | 61.4125 | 61.4939 | 123.0438 | 61.4762 | 122.8403 | 61.553 | 61.5706 | 61.4842 | 61.5018
920.0625 | 123.2712 | -61.4822 | 61.6516 | 0.025705 | -0.0451 | -0.021157 | 0.002454 | 0.031687 | 0.003172 | 0.033424 | 61.5829 | 0.17995 | 61.5004 | -0.042259 | 0.029923 | 61.5753 | -0.001436 | 61.3718 | 61.5079 | 61.4371 | 61.4611 | 61.4847 | 61.5139 | 61.4854 | 61.5157 | 123.0651 | 61.6622 | 122.9826 | 61.44 | 61.5122 | 123.0576 | 61.4808 | 122.8541 | 61.553 | 61.5843 | 61.4705 | 61.5018
921.0625 | 123.2758 | -61.4639 | 61.6699 | 0.030283 | -0.040521 | -0.012 | 0.011611 | 0.031687 | 0.003172 | 0.028846 | 61.5691 | 0.17079 | 61.4867 | -0.046838 | 0.025345 | 61.5707 | 0.003143 | 61.3718 | 61.4942 | 61.4234 | 61.4519 | 61.4755 | 61.4956 | 61.4671 | 61.4928 | 123.0331 | 61.6347 | 122.9506 | 61.4171 | 61.4893 | 123.0347 | 61.4671 | 122.8357 | 61.5438 | 61.566 | 61.4613 | 61.4835
922.0625 | 123.2803 | -61.4731 | 61.6562 | 0.030283 | -0.049678 | -0.007421 | 0.007033 | 0.031687 | -0.001406 | 0.033424 | 61.5737 | 0.17537 | 61.4684 | -0.051417 | 0.020767 | 61.5799 | 0.003143 | 61.3718 | 61.5034 | 61.4234 | 61.4657 | 61.4801 | 61.5048 | 61.4717 | 61.5065 | 123.0468 | 61.6485 | 122.9414 | 61.4217 | 61.4939 | 123.053 | 61.4762 | 122.8449 | 61.553 | 61.5706 | 61.4476 | 61.4652
923.0625 | 123.2208 | -61.4868 | 61.6562 | 0.025705 | -0.0451 | -0.016578 | 0.002454 | 0.027109 | 0.003172 | 0.024268 | 61.5737 | 0.17079 | 61.4592 | -0.051417 | 0.029923 | 61.5753 | 0.007721 | 61.3672 | 61.5125 | 61.4417 | 61.4702 | 61.4893 | 61.5139 | 61.49 | 61.5111 | 123.0605 | 61.6576 | 122.946 | 61.4354 | 61.5167 | 123.0621 | 61.4945 | 122.8541 | 61.5438 | 61.566 | 61.4293 | 61.4515
924.0625 | 123.262 | -61.5005 | 61.6425 | 0.030283 | -0.0451 | -0.002842 | -0.002124 | 0.031687 | 0.00775 | 0.038003 | 61.5691 | 0.17537 | 61.4638 | -0.03768 | 0.025345 | 61.5707 | 0.007721 | 61.3672 | 61.5308 | 61.4554 | 61.4977 | 61.4984 | 61.5322 | 61.5083 | 61.5386 | 123.0697 | 61.6759 | 122.9643 | 61.4629 | 61.5259 | 123.0713 | 61.5083 | 122.8678 | 61.5438 | 61.5614 | 61.4384 | 61.4561
925.0625 | 123.2666 | -61.4639 | 61.6516 | 0.025705 | -0.0451 | -0.007421 | 0.002454 | 0.022531 | -0.005985 | 0.024268 | 61.5783 | 0.17079 | 61.4638 | -0.051417 | 0.029923 | 61.5753 | 0.003143 | 61.3764 | 61.4896 | 61.4188 | 61.4565 | 61.4664 | 61.4865 | 61.4579 | 61.4882 | 123.0422 | 61.6347 | 122.9277 | 61.4125 | 61.4939 | 123.0392 | 61.4671 | 122.8403 | 61.5484 | 61.5752 | 61.4339 | 61.4606
926.0625 | 123.3444 | -61.4594 | 61.5875 | 0.030283 | -0.049678 | -0.016578 | -0.002124 | 0.027109 | 0.003172 | 0.028846 | 61.5829 | 0.17537 | 61.4729 | -0.055996 | 0.025345 | 61.5662 | 0.007721 | 61.3764 | 61.4896 | 61.4097 | 61.4428 | 61.4572 | 61.4865 | 61.4625 | 61.4882 | 123.0422 | 61.6347 | 122.9323 | 61.4034 | 61.4847 | 123.0255 | 61.4671 | 122.8357 | 61.5575 | 61.5752 | 61.4476 | 61.4652
927.0625 | 123.3261 | -61.4731 | 61.5967 | 0.025705 | -0.049678 | -0.016578 | -0.002124 | 0.027109 | 0.003172 | 0.033424 | 61.5737 | 0.17079 | 61.505 | -0.055996 | 0.029923 | 61.5799 | 0.007721 | 61.3764 | 61.4988 | 61.4234 | 61.4565 | 61.471 | 61.5002 | 61.4763 | 61.5065 | 123.0468 | 61.6439 | 122.9781 | 61.4171 | 61.503 | 123.053 | 61.4808 | 122.8495 | 61.5438 | 61.566 | 61.4751 | 61.4973
928.0625 | 123.2986 | -61.4777 | 61.6608 | 0.025705 | -0.0451 | -0.012 | -0.002124 | 0.027109 | -0.001406 | 0.033424 | 61.5783 | 0.17537 | 61.505 | -0.042259 | 0.020767 | 61.5753 | -0.001436 | 61.3718 | 61.5034 | 61.4326 | 61.4657 | 61.4755 | 61.5048 | 61.4763 | 61.5111 | 123.056 | 61.653 | 122.9826 | 61.4354 | 61.4984 | 123.053 | 61.4762 | 122.8495 | 61.5575 | 61.5797 | 61.4842 | 61.5064
929.0625 | 123.3444 | -61.4822 | 61.647 | 0.034862 | -0.040521 | -0.007421 | 0.002454 | 0.031687 | 0.00775 | 0.024268 | 61.5829 | 0.18453 | 61.5233 | -0.051417 | 0.020767 | 61.5753 | 0.003143 | 61.3672 | 61.5171 | 61.4417 | 61.4748 | 61.4847 | 61.5139 | 61.49 | 61.5065 | 123.0651 | 61.6668 | 123.0055 | 61.4308 | 61.503 | 123.0576 | 61.4854 | 122.8495 | 61.5621 | 61.5797 | 61.5025 | 61.5202
930.0625 | 123.2849 | -61.4822 | 61.6699 | 0.034862 | -0.0451 | -0.012 | 0.002454 | 0.031687 | 0.003172 | 0.024268 | 61.5737 | 0.17537 | 61.4684 | -0.055996 | 0.016188 | 61.5753 | 0.007721 | 61.381 | 61.5171 | 61.4371 | 61.4702 | 61.4847 | 61.5139 | 61.4854 | 61.5065 | 123.056 | 61.6576 | 122.9506 | 61.4262 | 61.4984 | 123.0576 | 61.49 | 122.8632 | 61.5575 | 61.566 | 61.4522 | 61.4606
931.0625 | 123.2849 | -61.5051 | 61.6379 | 0.025705 | -0.040521 | -0.016578 | 0.002454 | 0.031687 | -0.001406 | 0.028846 | 61.5737 | 0.17079 | 61.4684 | -0.051417 | 0.016188 | 61.5753 | 0.003143 | 61.3672 | 61.5308 | 61.4646 | 61.4885 | 61.5076 | 61.5368 | 61.5037 | 61.534 | 123.0789 | 61.6759 | 122.9735 | 61.4537 | 61.5213 | 123.0804 | 61.5083 | 122.8724 | 61.5575 | 61.5706 | 61.4522 | 61.4652
932.0625 | 123.3765 | -61.4502 | 61.6379 | 0.030283 | -0.0451 | -0.012 | 0.007033 | 0.036265 | -0.001406 | 0.024268 | 61.5737 | 0.17995 | 61.4638 | -0.051417 | 0.016188 | 61.5753 | 0.007721 | 61.3718 | 61.4805 | 61.4051 | 61.4382 | 61.4572 | 61.4865 | 61.4488 | 61.4745 | 123.0239 | 61.6301 | 122.914 | 61.3988 | 61.4664 | 123.0255 | 61.4579 | 122.822 | 61.5575 | 61.566 | 61.4476 | 61.4561
933.0625 | 123.3856 | -61.4456 | 61.6241 | 0.025705 | -0.0451 | -0.016578 | -0.002124 | 0.027109 | -0.005985 | 0.024268 | 61.5691 | 0.17079 | 61.4546 | -0.055996 | 0.016188 | 61.5753 | 0.003143 | 61.3718 | 61.4713 | 61.4005 | 61.429 | 61.4435 | 61.4727 | 61.4396 | 61.4699 | 123.0148 | 61.6164 | 122.9002 | 61.3896 | 61.4618 | 123.0209 | 61.4488 | 122.8174 | 61.553 | 61.566 | 61.4384 | 61.4515
934.0625 | 123.3032 | -61.4777 | 61.6287 | 0.030283 | -0.0451 | -0.007421 | 0.01619 | 0.040843 | -0.005985 | 0.033424 | 61.5737 | 0.17079 | 61.4729 | -0.046838 | 0.025345 | 61.5753 | -0.001436 | 61.3764 | 61.5079 | 61.4326 | 61.4702 | 61.4939 | 61.5185 | 61.4717 | 61.5111 | 123.0514 | 61.6485 | 122.9506 | 61.4308 | 61.503 | 123.053 | 61.4762 | 122.8541 | 61.5484 | 61.5752 | 61.4476 | 61.4744
935.0625 | 123.1979 | -61.5097 | 61.6425 | 0.030283 | -0.0451 | -0.021157 | 0.007033 | 0.031687 | 0.003172 | 0.033424 | 61.5737 | 0.17079 | 61.4729 | -0.055996 | 0.025345 | 61.5799 | 0.003143 | 61.3718 | 61.54 | 61.4646 | 61.4885 | 61.5167 | 61.5414 | 61.5129 | 61.5431 | 123.0834 | 61.6805 | 122.9826 | 61.4537 | 61.535 | 123.0896 | 61.5128 | 122.8815 | 61.5484 | 61.5706 | 61.4476 | 61.4698
936.0625 | 123.2849 | -61.4868 | 61.6608 | 0.025705 | -0.040521 | -0.016578 | 0.002454 | 0.022531 | 0.003172 | 0.028846 | 61.5737 | 0.17079 | 61.5096 | -0.051417 | 0.025345 | 61.5753 | 0.007721 | 61.3718 | 61.5125 | 61.4463 | 61.4702 | 61.4893 | 61.5093 | 61.49 | 61.5157 | 123.0605 | 61.6576 | 122.9964 | 61.4354 | 61.5122 | 123.0621 | 61.4945 | 122.8586 | 61.5484 | 61.566 | 61.4842 | 61.5018
937.0625 | 123.3627 | -61.4639 | 61.6058 | 0.030283 | -0.040521 | -0.021157 | 0.002454 | 0.027109 | -0.005985 | 0.033424 | 61.5783 | 0.17995 | 61.4958 | -0.046838 | 0.020767 | 61.5753 | 0.003143 | 61.3718 | 61.4942 | 61.4234 | 61.4428 | 61.4664 | 61.491 | 61.4579 | 61.4974 | 123.0422 | 61.6439 | 122.9598 | 61.4171 | 61.4847 | 123.0392 | 61.4671 | 122.8357 | 61.5575 | 61.5752 | 61.4751 | 61.4927
938.0625 | 123.262 | -61.496 | 61.647 | 0.034862 | -0.040521 | -0.012 | -0.002124 | 0.017953 | -0.005985 | 0.033424 | 61.5829 | 0.17537 | 61.5004 | -0.051417 | 0.020767 | 61.5707 | -0.001436 | 61.3718 | 61.5308 | 61.4555 | 61.484 | 61.4938 | 61.5139 | 61.49 | 61.5294 | 123.0789 | 61.6713 | 122.9964 | 61.4446 | 61.5167 | 123.0667 | 61.4945 | 122.8678 | 61.5621 | 61.5843 | 61.4796 | 61.5018
939.0625 | 123.3215 | -61.4639 | 61.6196 | 0.034862 | -0.040521 | -0.016578 | 0.002454 | 0.027109 | -0.005985 | 0.024268 | 61.5737 | 0.17537 | 61.4684 | -0.051417 | 0.025345 | 61.5753 | 0.007721 | 61.3764 | 61.4988 | 61.4234 | 61.4474 | 61.4664 | 61.491 | 61.4579 | 61.4882 | 123.0377 | 61.6393 | 122.9323 | 61.4125 | 61.4893 | 123.0392 | 61.4716 | 122.8403 | 61.5484 | 61.566 | 61.443 | 61.4606
940.0625 | 123.3719 | -61.4594 | 61.6013 | 0.030283 | -0.040521 | -0.016578 | 0.002454 | 0.027109 | -0.005985 | 0.024268 | 61.5737 | 0.17537 | 61.4638 | -0.046838 | 0.016188 | 61.5707 | 0.003143 | 61.381 | 61.4896 | 61.4188 | 61.4428 | 61.4618 | 61.4865 | 61.4534 | 61.4836 | 123.0331 | 61.6347 | 122.9231 | 61.4125 | 61.4755 | 123.0301 | 61.4625 | 122.8403 | 61.5575 | 61.5706 | 61.4476 | 61.4606
941.0625 | 123.2391 | -61.4822 | 61.6425 | 0.034862 | -0.040521 | -0.016578 | 0.002454 | 0.031687 | -0.001406 | 0.028846 | 61.5691 | 0.17995 | 61.4684 | -0.055996 | 0.020767 | 61.5753 | -0.001436 | 61.3764 | 61.5171 | 61.4417 | 61.4657 | 61.4847 | 61.5139 | 61.4808 | 61.5111 | 123.0514 | 61.6622 | 122.9506 | 61.4262 | 61.503 | 123.0576 | 61.4808 | 122.8586 | 61.5484 | 61.5706 | 61.4476 | 61.4698
942.0625 | 123.349 | -61.4594 | 61.6379 | 0.034862 | -0.040521 | -0.016578 | -0.002124 | 0.027109 | -0.001406 | 0.028846 | 61.5691 | 0.17079 | 61.4638 | -0.051417 | 0.020767 | 61.5753 | 0.003143 | 61.3764 | 61.4942 | 61.4188 | 61.4428 | 61.4572 | 61.4865 | 61.4579 | 61.4882 | 123.0285 | 61.6301 | 122.9231 | 61.4079 | 61.4801 | 123.0347 | 61.4625 | 122.8357 | 61.5484 | 61.566 | 61.443 | 61.4606
943.0625 | 123.4131 | -61.4594 | 61.6013 | 0.030283 | -0.040521 | -0.016578 | 0.002454 | 0.027109 | 0.003172 | 0.028846 | 61.5737 | 0.17537 | 61.4684 | -0.055996 | 0.01161 | 61.5753 | -0.001436 | 61.3718 | 61.4896 | 61.4188 | 61.4428 | 61.4618 | 61.4865 | 61.4625 | 61.4882 | 123.0331 | 61.6347 | 122.9277 | 61.4034 | 61.471 | 123.0347 | 61.4579 | 122.8312 | 61.5621 | 61.5752 | 61.4567 | 61.4698
944.0625 | 123.262 | -61.4822 | 61.6379 | 0.030283 | -0.0451 | -0.012 | -0.002124 | 0.027109 | -0.005985 | 0.028846 | 61.5737 | 0.17995 | 61.505 | -0.046838 | 0.016188 | 61.5707 | -0.001436 | 61.3718 | 61.5125 | 61.4371 | 61.4702 | 61.4801 | 61.5093 | 61.4763 | 61.5111 | 123.056 | 61.6622 | 122.9872 | 61.4354 | 61.4984 | 123.053 | 61.4808 | 122.8541 | 61.5575 | 61.5752 | 61.4888 | 61.5064
945.0625 | 123.3948 | -61.4548 | 61.6196 | 0.034862 | -0.0451 | -0.016578 | -0.002124 | 0.027109 | -0.001406 | 0.033424 | 61.5829 | 0.17537 | 61.5096 | -0.055996 | 0.020767 | 61.5753 | 0.003143 | 61.3718 | 61.4896 | 61.4097 | 61.4382 | 61.4526 | 61.4819 | 61.4534 | 61.4882 | 123.0377 | 61.6301 | 122.9643 | 61.3988 | 61.4755 | 123.0301 | 61.4579 | 122.8266 | 61.5621 | 61.5797 | 61.4888 | 61.5064
946.0625 | 123.2666 | -61.4639 | 61.6196 | 0.034862 | -0.0451 | -0.016578 | 0.002454 | 0.036265 | -0.001406 | 0.033424 | 61.5737 | 0.17995 | 61.505 | -0.051417 | 0.020767 | 61.5753 | 0.007721 | 61.3672 | 61.4988 | 61.4188 | 61.4474 | 61.4664 | 61.5002 | 61.4625 | 61.4974 | 123.0377 | 61.6439 | 122.9689 | 61.4125 | 61.4847 | 123.0392 | 61.4716 | 122.8312 | 61.553 | 61.566 | 61.4842 | 61.4973
947.0625 | 123.3261 | -61.4777 | 61.6013 | 0.034862 | -0.049678 | -0.012 | -0.002124 | 0.027109 | 0.003172 | 0.033424 | 61.5691 | 0.17537 | 61.505 | -0.055996 | 0.016188 | 61.5799 | 0.003143 | 61.3672 | 61.5125 | 61.428 | 61.4657 | 61.4755 | 61.5048 | 61.4808 | 61.5111 | 123.0468 | 61.653 | 122.9826 | 61.4217 | 61.4938 | 123.0576 | 61.4808 | 122.8449 | 61.553 | 61.566 | 61.4888 | 61.5018
948.0625 | 123.2941 | -61.4868 | 61.6974 | 0.034862 | -0.0451 | -0.021157 | 0.007033 | 0.031687 | -0.001406 | 0.028846 | 61.5783 | 0.17079 | 61.4867 | -0.055996 | 0.020767 | 61.5662 | 0.003143 | 61.3764 | 61.5217 | 61.4417 | 61.4657 | 61.4938 | 61.5185 | 61.4854 | 61.5157 | 123.0651 | 61.6576 | 122.9735 | 61.4308 | 61.5076 | 123.053 | 61.49 | 122.8632 | 61.5575 | 61.5752 | 61.4659 | 61.4835
949.0625 | 123.2529 | -61.4731 | 61.6608 | 0.034862 | -0.040521 | -0.016578 | -0.002124 | 0.031687 | -0.005985 | 0.024268 | 61.5737 | 0.17537 | 61.4684 | -0.055996 | 0.020767 | 61.5753 | 0.007721 | 61.3764 | 61.5079 | 61.4326 | 61.4565 | 61.471 | 61.5048 | 61.4671 | 61.4974 | 123.0468 | 61.6485 | 122.9414 | 61.4171 | 61.4939 | 123.0484 | 61.4808 | 122.8495 | 61.553 | 61.566 | 61.4476 | 61.4606
950.0625 | 123.3627 | -61.441 | 61.6333 | 0.03944 | -0.0451 | -0.012 | -0.006703 | 0.027109 | -0.005985 | 0.01969 | 61.5737 | 0.17079 | 61.4638 | -0.055996 | 0.020767 | 61.5707 | -0.001436 | 61.3627 | 61.4805 | 61.3959 | 61.429 | 61.4343 | 61.4681 | 61.4351 | 61.4607 | 123.0148 | 61.6118 | 122.9048 | 61.385 | 61.4618 | 123.0118 | 61.4396 | 122.8037 | 61.553 | 61.5752 | 61.443 | 61.4652
951.0625 | 123.2529 | -61.4822 | 61.6699 | 0.030283 | -0.0451 | -0.012 | 0.002454 | 0.036265 | 0.003172 | 0.033424 | 61.5691 | 0.17079 | 61.4638 | -0.055996 | 0.020767 | 61.5707 | 0.003143 | 61.3718 | 61.5125 | 61.4371 | 61.4702 | 61.4847 | 61.5185 | 61.4854 | 61.5157 | 123.0514 | 61.653 | 122.946 | 61.4262 | 61.503 | 123.053 | 61.4854 | 122.8541 | 61.5484 | 61.566 | 61.443 | 61.4606
952.0625 | 123.3582 | -61.4639 | 61.6013 | 0.025705 | -0.040521 | -0.021157 | -0.006703 | 0.036265 | -0.005985 | 0.024268 | 61.5783 | 0.17079 | 61.4729 | -0.055996 | 0.025345 | 61.5753 | -0.001436 | 61.3764 | 61.4896 | 61.4234 | 61.4428 | 61.4572 | 61.5002 | 61.4579 | 61.4882 | 123.0422 | 61.6347 | 122.9369 | 61.4079 | 61.4893 | 123.0392 | 61.4625 | 122.8403 | 61.553 | 61.5797 | 61.4476 | 61.4744
953.0625 | 123.3215 | -61.5005 | 61.6058 | 0.034862 | -0.040521 | -0.016578 | 0.002454 | 0.031687 | -0.001406 | 0.024268 | 61.5737 | 0.17995 | 61.5004 | -0.051417 | 0.020767 | 61.5707 | 0.007721 | 61.3718 | 61.5354 | 61.46 | 61.484 | 61.503 | 61.5322 | 61.4991 | 61.5248 | 123.0743 | 61.6805 | 123.0009 | 61.4491 | 61.5213 | 123.0713 | 61.5083 | 122.8724 | 61.553 | 61.566 | 61.4796 | 61.4927
954.0625 | 123.3627 | -61.4594 | 61.6241 | 0.030283 | -0.049678 | -0.012 | 0.002454 | 0.022531 | -0.001406 | 0.028846 | 61.5829 | 0.17079 | 61.4958 | -0.051417 | 0.020767 | 61.5799 | 0.003143 | 61.3718 | 61.4896 | 61.4097 | 61.4474 | 61.4618 | 61.4819 | 61.4579 | 61.4882 | 123.0422 | 61.6301 | 122.9552 | 61.4079 | 61.4801 | 123.0392 | 61.4625 | 122.8312 | 61.5621 | 61.5797 | 61.4751 | 61.4927
955.0625 | 123.4222 | -61.4456 | 61.6058 | 0.03944 | -0.0451 | -0.016578 | 0.011611 | 0.027109 | -0.005985 | 0.024268 | 61.5691 | 0.17995 | 61.4775 | -0.046838 | 0.025345 | 61.5845 | 0.003143 | 61.3672 | 61.4851 | 61.4005 | 61.429 | 61.4572 | 61.4727 | 61.4396 | 61.4699 | 123.0148 | 61.6256 | 122.9231 | 61.3988 | 61.471 | 123.0301 | 61.4488 | 122.8129 | 61.5438 | 61.566 | 61.4522 | 61.4744
956.0625 | 123.3673 | -61.4548 | 61.6333 | 0.034862 | -0.040521 | -0.016578 | 0.007033 | 0.031687 | -0.005985 | 0.028846 | 61.5737 | 0.16164 | 61.4684 | -0.051417 | 0.020767 | 61.5753 | 0.007721 | 61.3672 | 61.4896 | 61.4143 | 61.4382 | 61.4618 | 61.4865 | 61.4488 | 61.4836 | 123.0285 | 61.6164 | 122.9231 | 61.4034 | 61.4755 | 123.0301 | 61.4625 | 122.822 | 61.553 | 61.566 | 61.4476 | 61.4606
957.0781 | 123.3307 | -61.4548 | 61.6333 | 0.021127 | -0.040521 | -0.016578 | 0.002454 | 0.022531 | 0.003172 | 0.024268 | 61.5646 | 0.17995 | 61.4592 | -0.055996 | 0.016188 | 61.5753 | -0.001436 | 61.381 | 61.4759 | 61.4143 | 61.4382 | 61.4572 | 61.4773 | 61.4579 | 61.479 | 123.0193 | 61.6347 | 122.914 | 61.3988 | 61.471 | 123.0301 | 61.4533 | 122.8357 | 61.5484 | 61.566 | 61.443 | 61.4606
958.0625 | 123.3627 | -61.441 | 61.6104 | 0.03944 | -0.0451 | -0.007421 | 0.007033 | 0.027109 | 0.003172 | 0.028846 | 61.5783 | 0.17995 | 61.4638 | -0.046838 | 0.020767 | 61.5799 | 0.007721 | 61.3764 | 61.4805 | 61.3959 | 61.4336 | 61.4481 | 61.4681 | 61.4442 | 61.4699 | 123.0193 | 61.621 | 122.9048 | 61.3942 | 61.4618 | 123.0209 | 61.4488 | 122.8174 | 61.5575 | 61.5706 | 61.443 | 61.4561
959.0625 | 123.3994 | -61.409 | 61.6425 | 0.034862 | -0.0451 | -0.012 | 0.002454 | 0.027109 | -0.005985 | 0.024268 | 61.5691 | 0.17995 | 61.4775 | -0.051417 | 0.025345 | 61.5753 | -0.001436 | 61.3764 | 61.4439 | 61.3639 | 61.397 | 61.4115 | 61.4361 | 61.403 | 61.4333 | 122.9781 | 61.5889 | 122.8865 | 61.3576 | 61.4343 | 122.9843 | 61.4076 | 122.7854 | 61.5438 | 61.5706 | 61.4522 | 61.4789
960.0625 | 123.3261 | -61.4731 | 61.6013 | 0.025705 | -0.035942 | -0.012 | 0.002454 | 0.036265 | -0.001406 | 0.028846 | 61.5737 | 0.17537 | 61.505 | -0.051417 | 0.020767 | 61.5799 | 0.007721 | 61.3718 | 61.4988 | 61.4371 | 61.4611 | 61.4755 | 61.5093 | 61.4717 | 61.5019 | 123.0468 | 61.6485 | 122.9781 | 61.4217 | 61.4939 | 123.053 | 61.4808 | 122.8449 | 61.553 | 61.566 | 61.4842 | 61.4973
961.0625 | 123.317 | -61.4731 | 61.6013 | 0.034862 | -0.0451 | -0.012 | 0.002454 | 0.031687 | -0.005985 | 0.024268 | 61.5829 | 0.18911 | 61.5096 | -0.051417 | 0.025345 | 61.5799 | -0.001436 | 61.3672 | 61.5079 | 61.428 | 61.4611 | 61.4755 | 61.5048 | 61.4671 | 61.4974 | 123.056 | 61.6622 | 122.9826 | 61.4217 | 61.4984 | 123.053 | 61.4716 | 122.8403 | 61.5575 | 61.5843 | 61.4842 | 61.511
962.0625 | 123.3398 | -61.4777 | 61.6104 | 0.03944 | -0.0451 | -0.016578 | -0.002124 | 0.031687 | 0.003172 | 0.028846 | 61.5691 | 0.17079 | 61.5141 | -0.051417 | 0.020767 | 61.5707 | 0.003143 | 61.3764 | 61.5171 | 61.4326 | 61.4611 | 61.4755 | 61.5093 | 61.4808 | 61.5065 | 123.0468 | 61.6485 | 122.9918 | 61.4262 | 61.4984 | 123.0484 | 61.4808 | 122.8541 | 61.5484 | 61.566 | 61.4934 | 61.511
963.0625 | 123.3627 | -61.4639 | 61.6104 | 0.030283 | -0.0451 | -0.016578 | 0.002454 | 0.036265 | 0.003172 | 0.033424 | 61.5737 | 0.17537 | 61.4775 | -0.055996 | 0.020767 | 61.5662 | 0.003143 | 61.3718 | 61.4942 | 61.4188 | 61.4474 | 61.4664 | 61.5002 | 61.4671 | 61.4974 | 123.0377 | 61.6393 | 122.9414 | 61.4079 | 61.4847 | 123.0301 | 61.4671 | 122.8357 | 61.553 | 61.5706 | 61.4567 | 61.4744
964.0625 | 123.3353 | -61.4822 | 61.6058 | 0.030283 | -0.035942 | -0.016578 | 0.007033 | 0.031687 | -0.005985 | 0.028846 | 61.5829 | 0.17995 | 61.4638 | -0.051417 | 0.025345 | 61.5799 | 0.007721 | 61.3764 | 61.5125 | 61.4463 | 61.4657 | 61.4893 | 61.5139 | 61.4763 | 61.5111 | 123.0651 | 61.6622 | 122.946 | 61.4308 | 61.5076 | 123.0621 | 61.49 | 122.8586 | 61.5575 | 61.5752 | 61.4384 | 61.4561
965.0625 | 123.317 | -61.4868 | 61.5875 | 0.034862 | -0.0451 | -0.016578 | 0.002454 | 0.031687 | -0.005985 | 0.01969 | 61.5737 | 0.17995 | 61.45 | -0.046838 | 0.029923 | 61.5753 | 0.003143 | 61.3718 | 61.5217 | 61.4417 | 61.4702 | 61.4893 | 61.5185 | 61.4808 | 61.5065 | 123.0605 | 61.6668 | 122.9369 | 61.44 | 61.5167 | 123.0621 | 61.49 | 122.8586 | 61.5438 | 61.5706 | 61.4201 | 61.4469
966.0625 | 123.3398 | -61.4914 | 61.6013 | 0.030283 | -0.040521 | -0.025735 | 0.007033 | 0.027109 | -0.001406 | 0.028846 | 61.5737 | 0.17537 | 61.4638 | -0.046838 | 0.01161 | 61.5753 | -0.001436 | 61.3764 | 61.5217 | 61.4509 | 61.4657 | 61.4984 | 61.5185 | 61.49 | 61.5202 | 123.0651 | 61.6668 | 122.9552 | 61.4446 | 61.503 | 123.0667 | 61.49 | 122.8678 | 61.5621 | 61.5752 | 61.4522 | 61.4652
967.0625 | 123.3261 | -61.4914 | 61.615 | 0.030283 | -0.0451 | -0.016578 | -0.002124 | 0.022531 | -0.005985 | 0.024268 | 61.5691 | 0.17995 | 61.4638 | -0.055996 | 0.029923 | 61.5707 | 0.003143 | 61.3764 | 61.5217 | 61.4463 | 61.4748 | 61.4893 | 61.5139 | 61.4854 | 61.5157 | 123.0605 | 61.6713 | 122.9552 | 61.4354 | 61.5213 | 123.0621 | 61.4945 | 122.8678 | 61.5392 | 61.566 | 61.4339 | 61.4606
968.0625 | 123.4177 | -61.4639 | 61.5829 | 0.030283 | -0.0451 | -0.016578 | 0.002454 | 0.031687 | -0.001406 | 0.028846 | 61.5829 | 0.18453 | 61.4729 | -0.046838 | 0.016188 | 61.5753 | 0.007721 | 61.3718 | 61.4942 | 61.4188 | 61.4474 | 61.4664 | 61.4956 | 61.4625 | 61.4928 | 123.0468 | 61.6485 | 122.9369 | 61.4171 | 61.4801 | 123.0392 | 61.4716 | 122.8357 | 61.5667 | 61.5752 | 61.4567 | 61.4652
969.0625 | 123.3948 | -61.4273 | 61.6196 | 0.030283 | -0.0451 | -0.007421 | -0.002124 | 0.022531 | -0.005985 | 0.033424 | 61.5691 | 0.18453 | 61.5004 | -0.046838 | 0.01161 | 61.5753 | 0.007721 | 61.3718 | 61.4576 | 61.3822 | 61.4199 | 61.4252 | 61.4498 | 61.4213 | 61.4607 | 122.9965 | 61.6118 | 122.9277 | 61.3805 | 61.4389 | 123.0026 | 61.435 | 122.7991 | 61.5575 | 61.5614 | 61.4888 | 61.4927
970.0625 | 123.349 | -61.4822 | 61.6013 | 0.03944 | -0.049678 | -0.021157 | 0.002454 | 0.022531 | -0.005985 | 0.024268 | 61.5829 | 0.17995 | 61.5141 | -0.055996 | 0.020767 | 61.5753 | -0.001436 | 61.3718 | 61.5217 | 61.4326 | 61.4611 | 61.4847 | 61.5048 | 61.4763 | 61.5065 | 123.0651 | 61.6622 | 122.9964 | 61.4262 | 61.503 | 123.0576 | 61.4808 | 122.8541 | 61.5621 | 61.5843 | 61.4934 | 61.5156
971.0625 | 123.3948 | -61.409 | 61.6013 | 0.034862 | -0.040521 | -0.012 | 0.002454 | 0.027109 | -0.001406 | 0.024268 | 61.5829 | 0.17537 | 61.5096 | -0.046838 | 0.020767 | 61.5799 | 0.003143 | 61.3764 | 61.4439 | 61.3685 | 61.397 | 61.4115 | 61.4361 | 61.4076 | 61.4333 | 122.9919 | 61.5844 | 122.9186 | 61.3622 | 61.4298 | 122.9889 | 61.4121 | 122.7854 | 61.5621 | 61.5797 | 61.4888 | 61.5064
972.0625 | 123.3078 | -61.4868 | 61.6058 | 0.034862 | -0.0451 | -0.016578 | 0.002454 | 0.036265 | -0.001406 | 0.028846 | 61.5783 | 0.18453 | 61.4775 | -0.051417 | 0.016188 | 61.5753 | 0.007721 | 61.3764 | 61.5217 | 61.4417 | 61.4702 | 61.4893 | 61.5231 | 61.4854 | 61.5157 | 123.0651 | 61.6713 | 122.9643 | 61.4354 | 61.503 | 123.0621 | 61.4945 | 122.8632 | 61.5621 | 61.5706 | 61.4613 | 61.4698
973.0625 | 123.3582 | -61.4822 | 61.615 | 0.030283 | -0.0451 | -0.016578 | 0.002454 | 0.027109 | -0.001406 | 0.024268 | 61.5691 | 0.17079 | 61.4684 | -0.046838 | 0.016188 | 61.5753 | 0.003143 | 61.3672 | 61.5125 | 61.4371 | 61.4657 | 61.4847 | 61.5093 | 61.4808 | 61.5065 | 123.0514 | 61.653 | 122.9506 | 61.4354 | 61.4984 | 123.0576 | 61.4854 | 122.8495 | 61.553 | 61.566 | 61.4522 | 61.4652
974.0625 | 123.3582 | -61.4639 | 61.6104 | 0.025705 | -0.0451 | -0.012 | 0.002454 | 0.027109 | -0.001406 | 0.033424 | 61.5691 | 0.17995 | 61.4546 | -0.051417 | 0.020767 | 61.5753 | 0.012299 | 61.3672 | 61.4896 | 61.4188 | 61.4519 | 61.4664 | 61.491 | 61.4625 | 61.4974 | 123.0331 | 61.6439 | 122.9185 | 61.4125 | 61.4847 | 123.0392 | 61.4762 | 122.8312 | 61.5484 | 61.5569 | 61.4339 | 61.4423
975.0625 | 123.3536 | -61.4685 | 61.5875 | 0.021127 | -0.0451 | -0.021157 | -0.006703 | 0.022531 | -0.001406 | 0.028846 | 61.5737 | 0.17537 | 61.4592 | -0.046838 | 0.01161 | 61.5799 | -0.001436 | 61.3627 | 61.4896 | 61.4234 | 61.4473 | 61.4618 | 61.491 | 61.4671 | 61.4974 | 123.0422 | 61.6439 | 122.9277 | 61.4217 | 61.4801 | 123.0484 | 61.4671 | 122.8312 | 61.5621 | 61.5752 | 61.4476 | 61.4606
976.0625 | 123.3261 | -61.4731 | 61.6058 | 0.030283 | -0.049678 | -0.007421 | 0.011611 | 0.031687 | 0.003172 | 0.028846 | 61.5783 | 0.17995 | 61.4592 | -0.046838 | 0.020767 | 61.5662 | 0.007721 | 61.3718 | 61.5034 | 61.4234 | 61.4657 | 61.4847 | 61.5048 | 61.4763 | 61.5019 | 123.0514 | 61.653 | 122.9323 | 61.4262 | 61.4939 | 123.0392 | 61.4808 | 122.8449 | 61.5575 | 61.5706 | 61.4384 | 61.4515
977.0625 | 123.3719 | -61.4548 | 61.5738 | 0.030283 | -0.040521 | -0.016578 | 0.002454 | 0.031687 | 0.003172 | 0.024268 | 61.5783 | 0.17537 | 61.4684 | -0.051417 | 0.016188 | 61.5753 | 0.007721 | 61.3627 | 61.4851 | 61.4143 | 61.4382 | 61.4572 | 61.4865 | 61.4579 | 61.479 | 123.0331 | 61.6301 | 122.9231 | 61.4034 | 61.471 | 123.0301 | 61.4625 | 122.8174 | 61.5621 | 61.5706 | 61.4522 | 61.4606
978.0625 | 123.4085 | -61.4685 | 61.5829 | 0.034862 | -0.0451 | -0.012 | 0.007033 | 0.036265 | 0.003172 | 0.028846 | 61.5829 | 0.17995 | 61.4958 | -0.046838 | 0.020767 | 61.5707 | 0.012299 | 61.3718 | 61.5034 | 61.4234 | 61.4565 | 61.4755 | 61.5048 | 61.4717 | 61.4974 | 123.0514 | 61.6485 | 122.9643 | 61.4217 | 61.4893 | 123.0392 | 61.4808 | 122.8403 | 61.5621 | 61.5706 | 61.4751 | 61.4835
979.0625 | 123.3078 | -61.4639 | 61.6241 | 0.030283 | -0.035942 | -0.016578 | -0.002124 | 0.031687 | 0.003172 | 0.028846 | 61.5737 | 0.17537 | 61.5004 | -0.051417 | 0.025345 | 61.5753 | 0.003143 | 61.3764 | 61.4942 | 61.428 | 61.4474 | 61.4618 | 61.4956 | 61.4671 | 61.4928 | 123.0377 | 61.6393 | 122.9643 | 61.4125 | 61.4893 | 123.0392 | 61.4671 | 122.8403 | 61.5484 | 61.5706 | 61.4751 | 61.4973
980.0625 | 123.2254 | -61.5143 | 61.6104 | 0.025705 | -0.040521 | -0.012 | 0.002454 | 0.031687 | 0.003172 | 0.033424 | 61.5875 | 0.17995 | 61.5187 | -0.042259 | 0.016188 | 61.5799 | -0.001436 | 61.3718 | 61.54 | 61.4738 | 61.5023 | 61.5167 | 61.546 | 61.5175 | 61.5477 | 123.1017 | 61.6942 | 123.033 | 61.472 | 61.5305 | 123.0942 | 61.5128 | 122.8861 | 61.5713 | 61.5889 | 61.5025 | 61.5202
981.0625 | 123.3078 | -61.4822 | 61.5967 | 0.03944 | -0.040521 | -0.016578 | 0.002454 | 0.022531 | -0.001406 | 0.024268 | 61.5829 | 0.17079 | 61.4821 | -0.051417 | 0.020767 | 61.5753 | 0.003143 | 61.3672 | 61.5217 | 61.4417 | 61.4657 | 61.4847 | 61.5048 | 61.4808 | 61.5065 | 123.0651 | 61.653 | 122.9643 | 61.4308 | 61.503 | 123.0576 | 61.4854 | 122.8495 | 61.5621 | 61.5797 | 61.4613 | 61.4789
982.0625 | 123.2712 | -61.5097 | 61.6104 | 0.034862 | -0.0451 | -0.007421 | 0.002454 | 0.027109 | -0.001406 | 0.024268 | 61.5737 | 0.17537 | 61.4638 | -0.046838 | 0.020767 | 61.5753 | -0.006014 | 61.3718 | 61.5446 | 61.4646 | 61.5023 | 61.5122 | 61.5368 | 61.5083 | 61.534 | 123.0834 | 61.6851 | 122.9735 | 61.4629 | 61.5305 | 123.085 | 61.5037 | 122.8815 | 61.553 | 61.5797 | 61.443 | 61.4698
983.0625 | 123.3307 | -61.4731 | 61.5417 | 0.030283 | -0.040521 | -0.021157 | 0.007033 | 0.031687 | -0.005985 | 0.028846 | 61.5737 | 0.17995 | 61.4592 | -0.046838 | 0.01161 | 61.5753 | 0.003143 | 61.3764 | 61.5034 | 61.4326 | 61.4519 | 61.4801 | 61.5048 | 61.4671 | 61.5019 | 123.0468 | 61.653 | 122.9323 | 61.4262 | 61.4847 | 123.0484 | 61.4762 | 122.8495 | 61.5621 | 61.5706 | 61.4476 | 61.4561
984.0625 | 123.3215 | -61.4822 | 61.6013 | 0.030283 | -0.0451 | -0.012 | 0.002454 | 0.027109 | -0.005985 | 0.028846 | 61.5646 | 0.17537 | 61.4684 | -0.042259 | 0.025345 | 61.5753 | 0.003143 | 61.3718 | 61.5125 | 61.4371 | 61.4702 | 61.4847 | 61.5093 | 61.4763 | 61.5111 | 123.0468 | 61.6576 | 122.9506 | 61.44 | 61.5076 | 123.0576 | 61.4854 | 122.8541 | 61.5392 | 61.5614 | 61.443 | 61.4652
985.0625 | 123.2986 | -61.5005 | 61.6104 | 0.034862 | -0.049678 | -0.016578 | 0.002454 | 0.022531 | -0.005985 | 0.024268 | 61.5783 | 0.17995 | 61.4638 | -0.046838 | 0.020767 | 61.5707 | -0.001436 | 61.3718 | 61.5354 | 61.4509 | 61.484 | 61.503 | 61.5231 | 61.4946 | 61.5248 | 123.0789 | 61.6805 | 122.9643 | 61.4537 | 61.5213 | 123.0713 | 61.4991 | 122.8724 | 61.5575 | 61.5797 | 61.443 | 61.4652
986.0625 | 123.3765 | -61.496 | 61.5555 | 0.030283 | -0.040521 | -0.021157 | -0.002124 | 0.036265 | -0.005985 | 0.024268 | 61.5737 | 0.17995 | 61.4729 | -0.051417 | 0.020767 | 61.5662 | 0.003143 | 61.3718 | 61.5263 | 61.4555 | 61.4748 | 61.4938 | 61.5322 | 61.49 | 61.5202 | 123.0697 | 61.6759 | 122.9689 | 61.4446 | 61.5167 | 123.0621 | 61.4991 | 122.8678 | 61.553 | 61.5706 | 61.4522 | 61.4698
987.0625 | 123.2941 | -61.5097 | 61.6104 | 0.030283 | -0.0451 | -0.012 | 0.002454 | 0.027109 | 0.003172 | 0.024268 | 61.5783 | 0.17537 | 61.5187 | -0.046838 | 0.020767 | 61.5753 | -0.006014 | 61.3718 | 61.54 | 61.4646 | 61.4977 | 61.5122 | 61.5368 | 61.5129 | 61.534 | 123.088 | 61.6851 | 123.0284 | 61.4629 | 61.5305 | 123.085 | 61.5037 | 122.8815 | 61.5575 | 61.5843 | 61.4979 | 61.5247
988.0625 | 123.2849 | -61.5143 | 61.6196 | 0.030283 | -0.040521 | -0.012 | 0.002454 | 0.027109 | -0.001406 | 0.038003 | 61.5829 | 0.18453 | 61.5096 | -0.051417 | 0.020767 | 61.5753 | 0.003143 | 61.3718 | 61.5446 | 61.4738 | 61.5023 | 61.5167 | 61.5414 | 61.5129 | 61.5523 | 123.0972 | 61.6988 | 123.0238 | 61.4629 | 61.535 | 123.0896 | 61.5174 | 122.8861 | 61.5621 | 61.5797 | 61.4888 | 61.5064
989.0625 | 123.3719 | -61.4594 | 61.5829 | 0.025705 | -0.0451 | -0.007421 | 0.007033 | 0.036265 | -0.005985 | 0.028846 | 61.5783 | 0.17537 | 61.5096 | -0.046838 | 0.016188 | 61.5753 | 0.003143 | 61.3627 | 61.4851 | 61.4143 | 61.4519 | 61.4664 | 61.4956 | 61.4534 | 61.4882 | 123.0377 | 61.6347 | 122.9689 | 61.4125 | 61.4755 | 123.0347 | 61.4625 | 122.822 | 61.5621 | 61.5752 | 61.4934 | 61.5064
990.0625 | 123.2712 | -61.5005 | 61.6287 | 0.030283 | -0.035942 | -0.016578 | -0.002124 | 0.031687 | 0.003172 | 0.028846 | 61.5737 | 0.17537 | 61.4912 | -0.055996 | 0.020767 | 61.5799 | -0.001436 | 61.381 | 61.5308 | 61.4646 | 61.484 | 61.4984 | 61.5322 | 61.5037 | 61.5294 | 123.0743 | 61.6759 | 122.9918 | 61.4446 | 61.5213 | 123.0804 | 61.4991 | 122.8815 | 61.553 | 61.5752 | 61.4705 | 61.4927
991.0625 | 123.3444 | -61.4914 | 61.5784 | 0.025705 | -0.040521 | -0.021157 | 0.002454 | 0.031687 | -0.001406 | 0.028846 | 61.5783 | 0.17537 | 61.4684 | -0.046838 | 0.025345 | 61.5753 | 0.003143 | 61.3718 | 61.5171 | 61.4509 | 61.4702 | 61.4938 | 61.5231 | 61.49 | 61.5202 | 123.0697 | 61.6668 | 122.9597 | 61.4446 | 61.5167 | 123.0667 | 61.4945 | 122.8632 | 61.553 | 61.5752 | 61.443 | 61.4652
992.0625 | 123.3398 | -61.4685 | 61.5967 | 0.030283 | -0.040521 | -0.012 | 0.002454 | 0.031687 | 0.00775 | 0.028846 | 61.5783 | 0.17995 | 61.4684 | -0.051417 | 0.020767 | 61.5707 | 0.003143 | 61.3718 | 61.4988 | 61.428 | 61.4565 | 61.471 | 61.5002 | 61.4763 | 61.4974 | 123.0468 | 61.6485 | 122.9369 | 61.4171 | 61.4893 | 123.0392 | 61.4716 | 122.8403 | 61.5575 | 61.5752 | 61.4476 | 61.4652
993.0625 | 123.2574 | -61.4868 | 61.6241 | 0.030283 | -0.0451 | -0.012 | 0.002454 | 0.027109 | -0.001406 | 0.024268 | 61.5737 | 0.17995 | 61.4592 | -0.051417 | 0.016188 | 61.5891 | 0.003143 | 61.3718 | 61.5171 | 61.4417 | 61.4748 | 61.4893 | 61.5139 | 61.4854 | 61.5111 | 123.0605 | 61.6668 | 122.946 | 61.4354 | 61.503 | 123.0759 | 61.49 | 122.8586 | 61.5575 | 61.5706 | 61.443 | 61.4561
994.0625 | 123.3902 | -61.4456 | 61.6013 | 0.030283 | -0.040521 | -0.016578 | -0.002124 | 0.022531 | 0.003172 | 0.028846 | 61.5691 | 0.17995 | 61.4684 | -0.042259 | 0.016188 | 61.5799 | 0.007721 | 61.3718 | 61.4759 | 61.4051 | 61.429 | 61.4435 | 61.4681 | 61.4488 | 61.4745 | 123.0148 | 61.6256 | 122.914 | 61.4034 | 61.4618 | 123.0255 | 61.4533 | 122.8174 | 61.553 | 61.5614 | 61.4522 | 61.4606
995.0625 | 123.2574 | -61.4868 | 61.647 | 0.03944 | -0.040521 | -0.007421 | -0.002124 | 0.031687 | 0.003172 | 0.033424 | 61.5829 | 0.17995 | 61.4729 | -0.042259 | 0.025345 | 61.5799 | 0.007721 | 61.3764 | 61.5263 | 61.4463 | 61.4794 | 61.4847 | 61.5185 | 61.49 | 61.5202 | 123.0697 | 61.6668 | 122.9597 | 61.4446 | 61.5122 | 123.0667 | 61.4945 | 122.8632 | 61.5575 | 61.5752 | 61.4476 | 61.4652
996.0625 | 123.2986 | -61.4731 | 61.6058 | 0.034862 | -0.0451 | -0.016578 | 0.007033 | 0.027109 | -0.001406 | 0.028846 | 61.5783 | 0.17079 | 61.505 | -0.051417 | 0.020767 | 61.5707 | 0.007721 | 61.3764 | 61.5079 | 61.428 | 61.4565 | 61.4801 | 61.5002 | 61.4717 | 61.5019 | 123.0514 | 61.6439 | 122.9781 | 61.4217 | 61.4939 | 123.0438 | 61.4808 | 122.8495 | 61.5575 | 61.5706 | 61.4842 | 61.4973
997.0625 | 123.3124 | -61.5051 | 61.6196 | 0.034862 | -0.040521 | -0.012 | -0.002124 | 0.031687 | 0.003172 | 0.028846 | 61.5783 | 0.17995 | 61.5141 | -0.060575 | 0.020767 | 61.5753 | -0.001436 | 61.3764 | 61.54 | 61.4646 | 61.4931 | 61.503 | 61.5368 | 61.5083 | 61.534 | 123.0834 | 61.6851 | 123.0193 | 61.4446 | 61.5259 | 123.0804 | 61.5037 | 122.8815 | 61.5575 | 61.5797 | 61.4934 | 61.5156
998.0625 | 123.2666 | -61.4731 | 61.6653 | 0.03944 | -0.040521 | -0.007421 | -0.002124 | 0.036265 | 0.00775 | 0.033424 | 61.592 | 0.17995 | 61.5187 | -0.046838 | 0.020767 | 61.5753 | 0.012299 | 61.3764 | 61.5125 | 61.4326 | 61.4657 | 61.471 | 61.5093 | 61.4808 | 61.5065 | 123.0651 | 61.653 | 122.9918 | 61.4262 | 61.4939 | 123.0484 | 61.4854 | 122.8495 | 61.5713 | 61.5797 | 61.4979 | 61.5064
999.0625 | 123.2803 | -61.5005 | 61.615 | 0.025705 | -0.0451 | -0.012 | 0.007033 | 0.031687 | 0.003172 | 0.028846 | 61.5783 | 0.17995 | 61.4912 | -0.046838 | 0.020767 | 61.5799 | -0.001436 | 61.3764 | 61.5263 | 61.4554 | 61.4885 | 61.5076 | 61.5322 | 61.5037 | 61.5294 | 123.0789 | 61.6805 | 122.9918 | 61.4537 | 61.5213 | 123.0804 | 61.4991 | 122.8769 | 61.5575 | 61.5797 | 61.4705 | 61.4927
1000.0625 | 123.2346 | -61.5005 | 61.6196 | 0.034862 | -0.0451 | -0.016578 | 0.002454 | 0.027109 | -0.001406 | 0.038003 | 61.5783 | 0.17995 | 61.4684 | -0.055996 | 0.016188 | 61.5799 | -0.001436 | 61.3627 | 61.5354 | 61.4554 | 61.484 | 61.503 | 61.5277 | 61.4991 | 61.5386 | 123.0789 | 61.6805 | 122.9689 | 61.4446 | 61.5167 | 123.0804 | 61.4991 | 122.8632 | 61.5621 | 61.5797 | 61.4522 | 61.4698
1001.0625 | 123.3353 | -61.4868 | 61.6013 | 0.034862 | -0.0451 | -0.016578 | -0.002124 | 0.036265 | 0.003172 | 0.024268 | 61.5737 | 0.17537 | 61.4684 | -0.051417 | 0.020767 | 61.5753 | 0.007721 | 61.3718 | 61.5217 | 61.4417 | 61.4702 | 61.4847 | 61.5231 | 61.49 | 61.5111 | 123.0605 | 61.6622 | 122.9552 | 61.4354 | 61.5076 | 123.0621 | 61.4945 | 122.8586 | 61.553 | 61.566 | 61.4476 | 61.4606
1002.0625 | 123.3032 | -61.496 | 61.6516 | 0.025705 | -0.040521 | -0.012 | -0.002124 | 0.022531 | -0.005985 | 0.028846 | 61.5829 | 0.17537 | 61.4729 | -0.046838 | 0.016188 | 61.5845 | 0.007721 | 61.381 | 61.5217 | 61.4555 | 61.484 | 61.4938 | 61.5185 | 61.49 | 61.5248 | 123.0789 | 61.6713 | 122.9689 | 61.4491 | 61.5122 | 123.0804 | 61.5037 | 122.8769 | 61.5667 | 61.5752 | 61.4567 | 61.4652
1003.0625 | 123.2346 | -61.5326 | 61.6241 | 0.030283 | -0.0451 | -0.016578 | -0.002124 | 0.027109 | 0.003172 | 0.033424 | 61.5829 | 0.17995 | 61.4684 | -0.046838 | 0.020767 | 61.5753 | 0.007721 | 61.3718 | 61.5629 | 61.4875 | 61.516 | 61.5305 | 61.5597 | 61.5358 | 61.566 | 123.1155 | 61.7125 | 123.0009 | 61.4858 | 61.5534 | 123.1079 | 61.5403 | 122.9044 | 61.5621 | 61.5752 | 61.4476 | 61.4606
1004.0625 | 123.3536 | -61.5005 | 61.6196 | 0.030283 | -0.040521 | -0.016578 | -0.002124 | 0.031687 | -0.001406 | 0.028846 | 61.5875 | 0.17995 | 61.5004 | -0.051417 | 0.025345 | 61.5799 | 0.003143 | 61.3718 | 61.5308 | 61.46 | 61.484 | 61.4984 | 61.5322 | 61.4991 | 61.5294 | 123.088 | 61.6805 | 123.0009 | 61.4491 | 61.5259 | 123.0804 | 61.5037 | 122.8724 | 61.5621 | 61.5843 | 61.4751 | 61.4973
1005.0625 | 123.3215 | -61.4731 | 61.6196 | 0.030283 | -0.040521 | -0.012 | 0.002454 | 0.031687 | 0.003172 | 0.028846 | 61.5829 | 0.17537 | 61.505 | -0.046838 | 0.016188 | 61.5753 | -0.001436 | 61.3718 | 61.5034 | 61.4326 | 61.4611 | 61.4755 | 61.5048 | 61.4763 | 61.5019 | 123.056 | 61.6485 | 122.9781 | 61.4262 | 61.4893 | 123.0484 | 61.4716 | 122.8449 | 61.5667 | 61.5843 | 61.4888 | 61.5064
1006.0625 | 123.2574 | -61.5143 | 61.6379 | 0.034862 | -0.040521 | -0.016578 | 0.002454 | 0.036265 | 0.00775 | 0.033424 | 61.5829 | 0.18453 | 61.5141 | -0.051417 | 0.025345 | 61.5799 | 0.007721 | 61.3718 | 61.5491 | 61.4738 | 61.4977 | 61.5167 | 61.5505 | 61.522 | 61.5477 | 123.0972 | 61.6988 | 123.0284 | 61.4629 | 61.5396 | 123.0942 | 61.522 | 122.8861 | 61.5575 | 61.5752 | 61.4888 | 61.5064
1007.0625 | 123.2254 | -61.5097 | 61.6516 | 0.030283 | -0.0451 | -0.012 | 0.007033 | 0.031687 | -0.001406 | 0.028846 | 61.5829 | 0.17995 | 61.4958 | -0.055996 | 0.016188 | 61.5707 | -0.006014 | 61.3764 | 61.54 | 61.4646 | 61.4977 | 61.5167 | 61.5414 | 61.5083 | 61.5386 | 123.0926 | 61.6897 | 123.0055 | 61.4537 | 61.5259 | 123.0804 | 61.5037 | 122.8861 | 61.5667 | 61.5889 | 61.4796 | 61.5018
1008.0625 | 123.2529 | -61.5143 | 61.6333 | 0.030283 | -0.040521 | -0.016578 | -0.002124 | 0.027109 | -0.001406 | 0.024268 | 61.5875 | 0.17995 | 61.4775 | -0.055996 | 0.01161 | 61.5799 | 0.003143 | 61.3764 | 61.5446 | 61.4738 | 61.4977 | 61.5122 | 61.5414 | 61.5129 | 61.5386 | 123.1017 | 61.6942 | 122.9918 | 61.4583 | 61.5259 | 123.0942 | 61.5174 | 122.8907 | 61.5759 | 61.5843 | 61.4659 | 61.4744
1009.0625 | 123.3124 | -61.4731 | 61.6013 | 0.030283 | -0.049678 | -0.012 | -0.002124 | 0.027109 | -0.001406 | 0.033424 | 61.5737 | 0.17537 | 61.4684 | -0.046838 | 0.016188 | 61.5799 | -0.001436 | 61.381 | 61.5034 | 61.4234 | 61.4611 | 61.471 | 61.5002 | 61.4717 | 61.5065 | 123.0468 | 61.6485 | 122.9414 | 61.4262 | 61.4893 | 123.053 | 61.4716 | 122.8541 | 61.5575 | 61.5752 | 61.4522 | 61.4698
1010.0625 | 123.2574 | -61.496 | 61.6241 | 0.034862 | -0.040521 | -0.007421 | 0.002454 | 0.031687 | -0.001406 | 0.033424 | 61.5875 | 0.17537 | 61.5233 | -0.046838 | 0.020767 | 61.5753 | 0.003143 | 61.3764 | 61.5308 | 61.4555 | 61.4886 | 61.4984 | 61.5277 | 61.4946 | 61.5294 | 123.0834 | 61.6713 | 123.0193 | 61.4491 | 61.5167 | 123.0713 | 61.4991 | 122.8724 | 61.5667 | 61.5843 | 61.5025 | 61.5202
1011.0625 | 123.262 | -61.5051 | 61.6333 | 0.03944 | -0.031363 | -0.016578 | 0.002454 | 0.031687 | -0.001406 | 0.028846 | 61.5875 | 0.17995 | 61.5141 | -0.051417 | 0.020767 | 61.5707 | -0.001436 | 61.3718 | 61.5446 | 61.4738 | 61.4885 | 61.5076 | 61.5368 | 61.5037 | 61.534 | 123.0926 | 61.6851 | 123.0193 | 61.4537 | 61.5259 | 123.0759 | 61.5037 | 122.8769 | 61.5667 | 61.5889 | 61.4934 | 61.5156
1012.0625 | 123.2895 | -61.4914 | 61.6241 | 0.034862 | -0.040521 | -0.012 | -0.006703 | 0.036265 | 0.003172 | 0.028846 | 61.5783 | 0.17537 | 61.4684 | -0.046838 | 0.020767 | 61.5753 | 0.007721 | 61.3672 | 61.5263 | 61.4509 | 61.4794 | 61.4847 | 61.5277 | 61.4946 | 61.5202 | 123.0697 | 61.6668 | 122.9597 | 61.4446 | 61.5122 | 123.0667 | 61.4991 | 122.8586 | 61.5575 | 61.5706 | 61.4476 | 61.4606
1013.0625 | 123.349 | -61.4685 | 61.6058 | 0.034862 | -0.0451 | -0.016578 | 0.007033 | 0.027109 | -0.005985 | 0.024268 | 61.5783 | 0.17995 | 61.4592 | -0.046838 | 0.020767 | 61.5845 | 0.007721 | 61.3718 | 61.5034 | 61.4234 | 61.4519 | 61.4755 | 61.4956 | 61.4625 | 61.4928 | 123.0468 | 61.6485 | 122.9277 | 61.4217 | 61.4893 | 123.053 | 61.4762 | 122.8403 | 61.5575 | 61.5706 | 61.4384 | 61.4515
1014.0625 | 123.3765 | -61.5005 | 61.5646 | 0.034862 | -0.0451 | -0.012 | 0.002454 | 0.031687 | -0.001406 | 0.028846 | 61.5783 | 0.17995 | 61.4592 | -0.051417 | 0.020767 | 61.5753 | 0.007721 | 61.3764 | 61.5354 | 61.4554 | 61.4885 | 61.503 | 61.5322 | 61.4991 | 61.5294 | 123.0789 | 61.6805 | 122.9597 | 61.4491 | 61.5213 | 123.0759 | 61.5083 | 122.8769 | 61.5575 | 61.5706 | 61.4384 | 61.4515
1015.0625 | 123.2574 | -61.496 | 61.6516 | 0.030283 | -0.0451 | -0.016578 | -0.002124 | 0.036265 | 0.003172 | 0.028846 | 61.5829 | 0.18453 | 61.4775 | -0.046838 | 0.020767 | 61.5662 | 0.007721 | 61.3718 | 61.5263 | 61.4509 | 61.4794 | 61.4938 | 61.5322 | 61.4991 | 61.5248 | 123.0789 | 61.6805 | 122.9735 | 61.4491 | 61.5167 | 123.0621 | 61.5037 | 122.8678 | 61.5621 | 61.5752 | 61.4567 | 61.4698
1016.0625 | 123.3078 | -61.4868 | 61.5692 | 0.034862 | -0.0451 | -0.016578 | -0.002124 | 0.036265 | 0.003172 | 0.028846 | 61.5783 | 0.17537 | 61.5096 | -0.042259 | 0.016188 | 61.5799 | 0.003143 | 61.3718 | 61.5217 | 61.4417 | 61.4702 | 61.4847 | 61.5231 | 61.49 | 61.5157 | 123.0651 | 61.6622 | 122.9964 | 61.4446 | 61.503 | 123.0667 | 61.49 | 122.8586 | 61.5621 | 61.5752 | 61.4934 | 61.5064
1017.0625 | 123.2071 | -61.496 | 61.6333 | 0.025705 | -0.040521 | -0.016578 | 0.002454 | 0.027109 | -0.001406 | 0.033424 | 61.5875 | 0.17995 | 61.5096 | -0.046838 | 0.025345 | 61.5845 | -0.001436 | 61.3718 | 61.5217 | 61.4555 | 61.4794 | 61.4984 | 61.5231 | 61.4946 | 61.5294 | 123.0834 | 61.6759 | 123.0055 | 61.4491 | 61.5213 | 123.0804 | 61.4945 | 122.8678 | 61.5621 | 61.5889 | 61.4842 | 61.511
1018.0625 | 123.3765 | -61.4822 | 61.5784 | 0.030283 | -0.040521 | -0.021157 | 0.002454 | 0.036265 | -0.001406 | 0.028846 | 61.5829 | 0.18911 | 61.505 | -0.055996 | 0.016188 | 61.5799 | 0.003143 | 61.3764 | 61.5125 | 61.4417 | 61.4611 | 61.4847 | 61.5185 | 61.4808 | 61.5111 | 123.0651 | 61.6713 | 122.9872 | 61.4262 | 61.4984 | 123.0621 | 61.4854 | 122.8586 | 61.5667 | 61.5797 | 61.4888 | 61.5018
1019.0625 | 123.2529 | -61.5143 | 61.615 | 0.034862 | -0.040521 | -0.012 | -0.002124 | 0.040843 | 0.003172 | 0.033424 | 61.5829 | 0.17995 | 61.4912 | -0.046838 | 0.016188 | 61.5707 | -0.001436 | 61.3672 | 61.5491 | 61.4738 | 61.5023 | 61.5122 | 61.5551 | 61.5175 | 61.5477 | 123.0972 | 61.6942 | 123.0055 | 61.4674 | 61.5305 | 123.085 | 61.5128 | 122.8815 | 61.5667 | 61.5843 | 61.4751 | 61.4927
1020.0625 | 123.317 | -61.4777 | 61.6287 | 0.048597 | -0.040521 | -0.016578 | 0.002454 | 0.036265 | 0.003172 | 0.033424 | 61.5737 | 0.17995 | 61.4729 | -0.051417 | 0.020767 | 61.5707 | 0.003143 | 61.3764 | 61.5263 | 61.4371 | 61.4611 | 61.4801 | 61.5139 | 61.4808 | 61.5111 | 123.0514 | 61.6576 | 122.9506 | 61.4262 | 61.4984 | 123.0484 | 61.4808 | 122.8541 | 61.553 | 61.5706 | 61.4522 | 61.4698
1021.0625 | 123.3444 | -61.4822 | 61.5829 | 0.034862 | -0.049678 | -0.012 | 0.007033 | 0.027109 | 0.003172 | 0.028846 | 61.5829 | 0.17537 | 61.4592 | -0.055996 | 0.020767 | 61.5753 | 0.003143 | 61.3764 | 61.5171 | 61.4326 | 61.4702 | 61.4893 | 61.5093 | 61.4854 | 61.5111 | 123.0651 | 61.6576 | 122.9414 | 61.4262 | 61.503 | 123.0576 | 61.4854 | 122.8586 | 61.5621 | 61.5797 | 61.4384 | 61.4561
1022.0625 | 123.3444 | -61.4914 | 61.6013 | 0.030283 | -0.0451 | -0.016578 | -0.002124 | 0.027109 | 0.003172 | 0.024268 | 61.5783 | 0.17537 | 61.4638 | -0.046838 | 0.025345 | 61.5753 | 0.007721 | 61.3764 | 61.5217 | 61.4463 | 61.4748 | 61.4893 | 61.5185 | 61.4946 | 61.5157 | 123.0697 | 61.6668 | 122.9552 | 61.4446 | 61.5167 | 123.0667 | 61.4991 | 122.8678 | 61.553 | 61.5706 | 61.4384 | 61.4561
1023.0625 | 123.2529 | -61.4777 | 61.6287 | 0.034862 | -0.035942 | -0.007421 | -0.002124 | 0.036265 | -0.010563 | 0.024268 | 61.5783 | 0.17537 | 61.4684 | -0.046838 | 0.020767 | 61.5753 | 0.003143 | 61.381 | 61.5125 | 61.4417 | 61.4702 | 61.4755 | 61.5139 | 61.4671 | 61.5019 | 123.056 | 61.653 | 122.946 | 61.4308 | 61.4984 | 123.053 | 61.4808 | 122.8586 | 61.5575 | 61.5752 | 61.4476 | 61.4652
1024.0625 | 123.3307 | -61.496 | 61.6196 | 0.034862 | -0.0451 | -0.012 | 0.007033 | 0.040843 | -0.001406 | 0.028846 | 61.5829 | 0.17995 | 61.5096 | -0.046838 | 0.020767 | 61.5753 | 0.007721 | 61.3764 | 61.5308 | 61.4509 | 61.484 | 61.503 | 61.5368 | 61.4946 | 61.5248 | 123.0789 | 61.6759 | 123.0055 | 61.4491 | 61.5167 | 123.0713 | 61.5037 | 122.8724 | 61.5621 | 61.5752 | 61.4888 | 61.5018
1025.0625 | 123.3994 | -61.4456 | 61.5692 | 0.034862 | -0.049678 | -0.012 | 0.002454 | 0.031687 | -0.001406 | 0.024268 | 61.5783 | 0.18453 | 61.505 | -0.051417 | 0.025345 | 61.5753 | -0.001436 | 61.3764 | 61.4805 | 61.3959 | 61.4336 | 61.4481 | 61.4773 | 61.4442 | 61.4699 | 123.0239 | 61.6301 | 122.9506 | 61.3942 | 61.471 | 123.0209 | 61.4442 | 122.822 | 61.553 | 61.5797 | 61.4796 | 61.5064
1026.0625 | 123.3627 | -61.441 | 61.6104 | 0.025705 | -0.0451 | -0.012 | 0.002454 | 0.036265 | -0.001406 | 0.028846 | 61.5783 | 0.17995 | 61.4729 | -0.042259 | 0.029923 | 61.5799 | 0.003143 | 61.381 | 61.4667 | 61.3959 | 61.429 | 61.4435 | 61.4773 | 61.4396 | 61.4699 | 123.0193 | 61.621 | 122.914 | 61.3988 | 61.471 | 123.0209 | 61.4442 | 122.822 | 61.5484 | 61.5752 | 61.443 | 61.4698
1027.0625 | 123.2346 | -61.5097 | 61.6287 | 0.030283 | -0.049678 | -0.021157 | -0.002124 | 0.027109 | -0.001406 | 0.024268 | 61.5783 | 0.17537 | 61.4638 | -0.051417 | 0.016188 | 61.5753 | -0.001436 | 61.3718 | 61.54 | 61.46 | 61.4885 | 61.5076 | 61.5368 | 61.5083 | 61.534 | 123.088 | 61.6851 | 122.9735 | 61.4583 | 61.5259 | 123.085 | 61.5083 | 122.8815 | 61.5621 | 61.5797 | 61.4476 | 61.4652
1028.0625 | 123.3124 | -61.4914 | 61.5967 | 0.030283 | -0.035942 | -0.021157 | -0.006703 | 0.036265 | -0.005985 | 0.024268 | 61.5829 | 0.17537 | 61.4958 | -0.046838 | 0.029923 | 61.5753 | 0.007721 | 61.3718 | 61.5217 | 61.4555 | 61.4702 | 61.4847 | 61.5277 | 61.4854 | 61.5157 | 123.0743 | 61.6668 | 122.9872 | 61.4446 | 61.5213 | 123.0667 | 61.4991 | 122.8632 | 61.553 | 61.5752 | 61.4659 | 61.4881
1029.0625 | 123.2803 | -61.4685 | 61.6333 | 0.030283 | -0.040521 | -0.007421 | -0.006703 | 0.036265 | -0.001406 | 0.038003 | 61.5829 | 0.17537 | 61.505 | -0.046838 | 0.020767 | 61.5707 | 0.003143 | 61.3764 | 61.4988 | 61.428 | 61.4611 | 61.4618 | 61.5048 | 61.4671 | 61.5065 | 123.0514 | 61.6439 | 122.9735 | 61.4217 | 61.4893 | 123.0392 | 61.4716 | 122.8449 | 61.5621 | 61.5797 | 61.4842 | 61.5018
1030.0625 | 123.2758 | -61.4822 | 61.6425 | 0.030283 | -0.040521 | -0.021157 | 0.002454 | 0.027109 | 0.003172 | 0.028846 | 61.5875 | 0.18453 | 61.5233 | -0.055996 | 0.020767 | 61.5753 | 0.007721 | 61.3718 | 61.5125 | 61.4417 | 61.4611 | 61.4847 | 61.5093 | 61.4854 | 61.5111 | 123.0697 | 61.6668 | 123.0055 | 61.4262 | 61.503 | 123.0576 | 61.49 | 122.8541 | 61.5667 | 61.5797 | 61.5025 | 61.5156
1031.0625 | 123.3627 | -61.4639 | 61.5967 | 0.034862 | -0.049678 | -0.012 | 0.002454 | 0.027109 | -0.001406 | 0.01969 | 61.5783 | 0.17995 | 61.4958 | -0.051417 | 0.016188 | 61.5753 | 0.003143 | 61.3718 | 61.4988 | 61.4143 | 61.4519 | 61.4664 | 61.491 | 61.4625 | 61.4836 | 123.0422 | 61.6439 | 122.9598 | 61.4125 | 61.4801 | 123.0392 | 61.4671 | 122.8357 | 61.5621 | 61.5752 | 61.4796 | 61.4927
1032.0625 | 123.262 | -61.5005 | 61.6196 | 0.030283 | -0.0451 | -0.016578 | 0.002454 | 0.027109 | -0.005985 | 0.033424 | 61.5783 | 0.17995 | 61.4729 | -0.046838 | 0.020767 | 61.5753 | 0.003143 | 61.3764 | 61.5308 | 61.4554 | 61.484 | 61.503 | 61.5277 | 61.4946 | 61.534 | 123.0789 | 61.6805 | 122.9735 | 61.4537 | 61.5213 | 123.0759 | 61.5037 | 122.8769 | 61.5575 | 61.5752 | 61.4522 | 61.4698
1033.0625 | 123.3582 | -61.4777 | 61.5921 | 0.030283 | -0.0451 | -0.012 | -0.002124 | 0.031687 | -0.005985 | 0.024268 | 61.5691 | 0.17995 | 61.4592 | -0.051417 | 0.020767 | 61.5753 | 0.007721 | 61.3718 | 61.5079 | 61.4326 | 61.4657 | 61.4755 | 61.5093 | 61.4717 | 61.5019 | 123.0468 | 61.6576 | 122.9369 | 61.4262 | 61.4984 | 123.053 | 61.4854 | 122.8495 | 61.5484 | 61.5614 | 61.4384 | 61.4515
1034.0625 | 123.317 | -61.4731 | 61.6608 | 0.034862 | -0.0451 | -0.007421 | 0.002454 | 0.031687 | -0.001406 | 0.028846 | 61.5783 | 0.17995 | 61.505 | -0.051417 | 0.020767 | 61.5753 | 0.003143 | 61.381 | 61.5079 | 61.428 | 61.4657 | 61.4755 | 61.5048 | 61.4717 | 61.5019 | 123.0514 | 61.653 | 122.9781 | 61.4217 | 61.4939 | 123.0484 | 61.4762 | 122.8541 | 61.5575 | 61.5752 | 61.4842 | 61.5018
1035.0625 | 123.262 | -61.5143 | 61.6287 | 0.034862 | -0.0451 | -0.007421 | 0.002454 | 0.027109 | -0.001406 | 0.028846 | 61.5829 | 0.17995 | 61.505 | -0.051417 | 0.016188 | 61.5707 | -0.001436 | 61.3672 | 61.5491 | 61.4692 | 61.5069 | 61.5167 | 61.5414 | 61.5129 | 61.5431 | 123.0972 | 61.6942 | 123.0193 | 61.4629 | 61.5305 | 123.085 | 61.5128 | 122.8815 | 61.5667 | 61.5843 | 61.4888 | 61.5064
1036.0625 | 123.317 | -61.441 | 61.615 | 0.03944 | -0.049678 | -0.016578 | 0.002454 | 0.027109 | -0.005985 | 0.028846 | 61.5783 | 0.17537 | 61.4821 | -0.051417 | 0.020767 | 61.5753 | -0.001436 | 61.3718 | 61.4805 | 61.3914 | 61.4245 | 61.4435 | 61.4681 | 61.4351 | 61.4699 | 123.0193 | 61.6164 | 122.9231 | 61.3896 | 61.4618 | 123.0164 | 61.4396 | 122.8129 | 61.5575 | 61.5797 | 61.4613 | 61.4835
1037.0625 | 123.2483 | -61.5005 | 61.647 | 0.034862 | -0.035942 | -0.016578 | 0.002454 | 0.036265 | -0.005985 | 0.024268 | 61.5737 | 0.17537 | 61.4592 | -0.055996 | 0.020767 | 61.5753 | -0.006014 | 61.3672 | 61.5354 | 61.4646 | 61.484 | 61.503 | 61.5368 | 61.4946 | 61.5248 | 123.0743 | 61.6759 | 122.9597 | 61.4446 | 61.5213 | 123.0759 | 61.4945 | 122.8678 | 61.553 | 61.5797 | 61.4384 | 61.4652
1038.0625 | 123.2849 | -61.4822 | 61.615 | 0.034862 | -0.0451 | -0.016578 | 0.002454 | 0.036265 | 0.00775 | 0.038003 | 61.5783 | 0.18911 | 61.5004 | -0.051417 | 0.025345 | 61.5753 | -0.001436 | 61.3718 | 61.5171 | 61.4371 | 61.4657 | 61.4847 | 61.5185 | 61.49 | 61.5202 | 123.0605 | 61.6713 | 122.9826 | 61.4308 | 61.5076 | 123.0576 | 61.4808 | 122.8541 | 61.553 | 61.5797 | 61.4751 | 61.5018
1039.0625 | 123.2803 | -61.4822 | 61.6653 | 0.034862 | -0.0451 | -0.007421 | 0.002454 | 0.031687 | -0.001406 | 0.024268 | 61.5875 | 0.17079 | 61.5096 | -0.055996 | 0.020767 | 61.5753 | -0.006014 | 61.3764 | 61.5171 | 61.4371 | 61.4748 | 61.4847 | 61.5139 | 61.4808 | 61.5065 | 123.0697 | 61.653 | 122.9918 | 61.4262 | 61.503 | 123.0576 | 61.4762 | 122.8586 | 61.5667 | 61.5935 | 61.4888 | 61.5156
1040.0625 | 123.2758 | -61.4822 | 61.615 | 0.025705 | -0.0451 | -0.007421 | 0.002454 | 0.036265 | -0.001406 | 0.028846 | 61.5783 | 0.18453 | 61.4821 | -0.055996 | 0.020767 | 61.5753 | -0.010593 | 61.3718 | 61.5079 | 61.4371 | 61.4748 | 61.4847 | 61.5185 | 61.4808 | 61.5111 | 123.0605 | 61.6668 | 122.9643 | 61.4262 | 61.503 | 123.0576 | 61.4716 | 122.8541 | 61.5575 | 61.5889 | 61.4613 | 61.4927
1041.0625 | 123.3215 | -61.4594 | 61.6013 | 0.030283 | -0.0451 | -0.012 | -0.006703 | 0.036265 | -0.005985 | 0.028846 | 61.5783 | 0.17995 | 61.4729 | -0.051417 | 0.025345 | 61.5799 | -0.010593 | 61.3672 | 61.4896 | 61.4143 | 61.4474 | 61.4526 | 61.4956 | 61.4534 | 61.4882 | 123.0377 | 61.6393 | 122.9323 | 61.4079 | 61.4847 | 123.0392 | 61.4488 | 122.8266 | 61.553 | 61.5889 | 61.4476 | 61.4835
1042.0625 | 123.2574 | -61.5005 | 61.6241 | 0.034862 | -0.040521 | -0.012 | 0.002454 | 0.031687 | -0.001406 | 0.024268 | 61.5783 | 0.18453 | 61.4958 | -0.051417 | 0.020767 | 61.5707 | -0.006014 | 61.3672 | 61.5354 | 61.46 | 61.4885 | 61.503 | 61.5322 | 61.4991 | 61.5248 | 123.0789 | 61.6851 | 122.9964 | 61.4491 | 61.5213 | 123.0713 | 61.4945 | 122.8678 | 61.5575 | 61.5843 | 61.4751 | 61.5018
1043.0625 | 123.2391 | -61.4822 | 61.6379 | 0.030283 | -0.040521 | -0.012 | 0.011611 | 0.040843 | -0.001406 | 0.028846 | 61.5875 | 0.17995 | 61.5187 | -0.055996 | 0.020767 | 61.5753 | -0.006014 | 61.3718 | 61.5125 | 61.4417 | 61.4702 | 61.4939 | 61.5231 | 61.4808 | 61.5111 | 123.0697 | 61.6622 | 123.001 | 61.4262 | 61.503 | 123.0576 | 61.4762 | 122.8541 | 61.5667 | 61.5935 | 61.4979 | 61.5247
1044.0625 | 123.3536 | -61.4594 | 61.5921 | 0.025705 | -0.0451 | -0.012 | 0.002454 | 0.027109 | -0.005985 | 0.024268 | 61.5783 | 0.17995 | 61.4958 | -0.055996 | 0.016188 | 61.5753 | -0.006014 | 61.3764 | 61.4851 | 61.4143 | 61.4474 | 61.4618 | 61.4865 | 61.4534 | 61.4836 | 123.0377 | 61.6393 | 122.9552 | 61.4034 | 61.4755 | 123.0347 | 61.4533 | 122.8357 | 61.5621 | 61.5843 | 61.4796 | 61.5018
1045.0625 | 123.2941 | -61.496 | 61.6241 | 0.034862 | -0.040521 | -0.025735 | 0.007033 | 0.031687 | 0.003172 | 0.028846 | 61.5783 | 0.17995 | 61.4775 | -0.042259 | 0.016188 | 61.5707 | -0.006014 | 61.3718 | 61.5308 | 61.4555 | 61.4702 | 61.503 | 61.5277 | 61.4991 | 61.5248 | 123.0743 | 61.6759 | 122.9735 | 61.4537 | 61.5122 | 123.0667 | 61.49 | 122.8678 | 61.5621 | 61.5843 | 61.4613 | 61.4835
1046.0625 | 123.3078 | -61.4227 | 61.6241 | 0.030283 | -0.040521 | -0.012 | 0.002454 | 0.036265 | -0.005985 | 0.028846 | 61.5875 | 0.18453 | 61.4958 | -0.046838 | 0.029923 | 61.5753 | -0.006014 | 61.3764 | 61.453 | 61.3822 | 61.4107 | 61.4252 | 61.459 | 61.4167 | 61.4516 | 123.0102 | 61.6073 | 122.9186 | 61.3759 | 61.4527 | 122.998 | 61.4167 | 122.7991 | 61.5575 | 61.5935 | 61.4659 | 61.5018
1047.0625 | 123.2803 | -61.4731 | 61.6241 | 0.034862 | -0.035942 | -0.021157 | 0.011611 | 0.031687 | -0.001406 | 0.028846 | 61.592 | 0.17995 | 61.5141 | -0.051417 | 0.016188 | 61.5845 | -0.001436 | 61.3718 | 61.5079 | 61.4371 | 61.4519 | 61.4847 | 61.5048 | 61.4717 | 61.5019 | 123.0651 | 61.653 | 122.9872 | 61.4217 | 61.4893 | 123.0576 | 61.4716 | 122.8449 | 61.5759 | 61.5935 | 61.4979 | 61.5156
1048.0625 | 123.2758 | -61.5143 | 61.6241 | 0.034862 | -0.040521 | -0.016578 | 0.007033 | 0.031687 | -0.005985 | 0.033424 | 61.5875 | 0.18453 | 61.5004 | -0.055996 | 0.016188 | 61.5799 | -0.001436 | 61.3718 | 61.5491 | 61.4738 | 61.4977 | 61.5213 | 61.546 | 61.5083 | 61.5477 | 123.1017 | 61.6988 | 123.0147 | 61.4583 | 61.5305 | 123.0942 | 61.5128 | 122.8861 | 61.5713 | 61.5889 | 61.4842 | 61.5018
1049.0625 | 123.349 | -61.4731 | 61.6058 | 0.034862 | -0.035942 | -0.016578 | -0.002124 | 0.027109 | -0.005985 | 0.028846 | 61.5829 | 0.18453 | 61.4775 | -0.055996 | 0.020767 | 61.5845 | -0.001436 | 61.3718 | 61.5079 | 61.4371 | 61.4565 | 61.471 | 61.5002 | 61.4671 | 61.5019 | 123.056 | 61.6576 | 122.9506 | 61.4171 | 61.4939 | 123.0576 | 61.4716 | 122.8449 | 61.5621 | 61.5843 | 61.4567 | 61.4789
1050.0625 | 123.2986 | -61.4594 | 61.6562 | 0.030283 | -0.0451 | -0.016578 | 0.007033 | 0.031687 | -0.001406 | 0.024268 | 61.5783 | 0.17995 | 61.4775 | -0.046838 | 0.025345 | 61.5799 | -0.006014 | 61.3718 | 61.4896 | 61.4143 | 61.4428 | 61.4664 | 61.491 | 61.4579 | 61.4836 | 123.0377 | 61.6393 | 122.9369 | 61.4125 | 61.4847 | 123.0392 | 61.4533 | 122.8312 | 61.553 | 61.5843 | 61.4522 | 61.4835
1051.0625 | 123.2758 | -61.4914 | 61.6287 | 0.034862 | -0.040521 | -0.016578 | 0.002454 | 0.031687 | -0.001406 | 0.024268 | 61.5875 | 0.17537 | 61.5141 | -0.051417 | 0.020767 | 61.5799 | -0.010593 | 61.3764 | 61.5263 | 61.4509 | 61.4748 | 61.4938 | 61.5231 | 61.49 | 61.5157 | 123.0789 | 61.6668 | 123.0055 | 61.44 | 61.5122 | 123.0713 | 61.4808 | 122.8678 | 61.5667 | 61.5981 | 61.4934 | 61.5247
1052.0625 | 123.2483 | -61.5005 | 61.6379 | 0.03944 | -0.040521 | -0.007421 | -0.002124 | 0.031687 | -0.001406 | 0.028846 | 61.5875 | 0.17079 | 61.5141 | -0.046838 | 0.025345 | 61.5753 | -0.001436 | 61.3718 | 61.54 | 61.46 | 61.4931 | 61.4984 | 61.5322 | 61.4991 | 61.5294 | 123.088 | 61.6713 | 123.0147 | 61.4537 | 61.5259 | 123.0759 | 61.4991 | 122.8724 | 61.5621 | 61.5889 | 61.4888 | 61.5156
1053.0625 | 123.2529 | -61.4914 | 61.6516 | 0.030283 | -0.0451 | -0.016578 | 0.002454 | 0.036265 | -0.001406 | 0.028846 | 61.5829 | 0.17995 | 61.4775 | -0.046838 | 0.025345 | 61.5707 | -0.006014 | 61.3672 | 61.5217 | 61.4463 | 61.4748 | 61.4938 | 61.5277 | 61.49 | 61.5202 | 123.0743 | 61.6713 | 122.9689 | 61.4446 | 61.5167 | 123.0621 | 61.4854 | 122.8586 | 61.5575 | 61.5889 | 61.4522 | 61.4835
1054.0625 | 123.3536 | -61.4777 | 61.615 | 0.034862 | -0.040521 | -0.016578 | -0.002124 | 0.031687 | -0.005985 | 0.024268 | 61.5875 | 0.17995 | 61.4638 | -0.042259 | 0.016188 | 61.5707 | -0.006014 | 61.3764 | 61.5125 | 61.4371 | 61.4611 | 61.4755 | 61.5093 | 61.4717 | 61.5019 | 123.0651 | 61.6576 | 122.9414 | 61.4354 | 61.4938 | 123.0484 | 61.4716 | 122.8541 | 61.5713 | 61.5935 | 61.4476 | 61.4698
1055.0625 | 123.2803 | -61.5005 | 61.6333 | 0.034862 | -0.035942 | -0.007421 | 0.002454 | 0.031687 | 0.003172 | 0.033424 | 61.5829 | 0.17995 | 61.4867 | -0.046838 | 0.020767 | 61.5707 | -0.006014 | 61.3718 | 61.5354 | 61.4646 | 61.4931 | 61.503 | 61.5322 | 61.5037 | 61.534 | 123.0834 | 61.6805 | 122.9872 | 61.4537 | 61.5213 | 123.0713 | 61.4945 | 122.8724 | 61.5621 | 61.5889 | 61.4659 | 61.4927
1056.0625 | 123.3124 | -61.4822 | 61.6379 | 0.034862 | -0.0451 | -0.012 | 0.002454 | 0.040843 | -0.001406 | 0.028846 | 61.592 | 0.17537 | 61.5187 | -0.051417 | 0.020767 | 61.5753 | -0.010593 | 61.3718 | 61.5171 | 61.4371 | 61.4702 | 61.4847 | 61.5231 | 61.4808 | 61.5111 | 123.0743 | 61.6576 | 123.001 | 61.4308 | 61.503 | 123.0576 | 61.4716 | 122.8541 | 61.5713 | 61.6026 | 61.4979 | 61.5293
1057.0625 | 123.317 | -61.4822 | 61.647 | 0.034862 | -0.040521 | -0.012 | -0.006703 | 0.031687 | -0.001406 | 0.033424 | 61.5875 | 0.18453 | 61.4958 | -0.051417 | 0.016188 | 61.5707 | -0.006014 | 61.3764 | 61.5171 | 61.4417 | 61.4702 | 61.4755 | 61.5139 | 61.4808 | 61.5157 | 123.0697 | 61.6668 | 122.9781 | 61.4308 | 61.4984 | 123.053 | 61.4762 | 122.8586 | 61.5713 | 61.5935 | 61.4796 | 61.5018
1058.0625 | 123.2986 | -61.4914 | 61.647 | 0.025705 | -0.0451 | -0.012 | 0.002454 | 0.036265 | -0.005985 | 0.028846 | 61.5829 | 0.18453 | 61.4684 | -0.042259 | 0.020767 | 61.5799 | 0.003143 | 61.3764 | 61.5171 | 61.4463 | 61.4794 | 61.4938 | 61.5277 | 61.4854 | 61.5202 | 123.0743 | 61.6759 | 122.9597 | 61.4491 | 61.5122 | 123.0713 | 61.4945 | 122.8678 | 61.5621 | 61.5797 | 61.4476 | 61.4652
1059.0625 | 123.2712 | -61.4914 | 61.6013 | 0.030283 | -0.040521 | -0.007421 | 0.002454 | 0.031687 | 0.003172 | 0.024268 | 61.5829 | 0.17537 | 61.4775 | -0.046838 | 0.01161 | 61.5707 | -0.006014 | 61.3672 | 61.5217 | 61.4509 | 61.484 | 61.4938 | 61.5231 | 61.4946 | 61.5157 | 123.0743 | 61.6668 | 122.9689 | 61.4446 | 61.503 | 123.0621 | 61.4854 | 122.8586 | 61.5713 | 61.5889 | 61.4659 | 61.4835
1060.0625 | 123.2849 | -61.4868 | 61.6425 | 0.034862 | -0.040521 | -0.016578 | 0.007033 | 0.031687 | 0.003172 | 0.033424 | 61.592 | 0.17537 | 61.5187 | -0.055996 | 0.029923 | 61.5707 | -0.006014 | 61.3764 | 61.5217 | 61.4463 | 61.4702 | 61.4938 | 61.5185 | 61.49 | 61.5202 | 123.0789 | 61.6622 | 123.0055 | 61.4308 | 61.5167 | 123.0576 | 61.4808 | 122.8632 | 61.5621 | 61.5981 | 61.4888 | 61.5247
1061.0625 | 123.2346 | -61.5005 | 61.6333 | 0.034862 | -0.0451 | -0.007421 | 0.007033 | 0.036265 | 0.003172 | 0.033424 | 61.5875 | 0.18453 | 61.5187 | -0.051417 | 0.020767 | 61.5799 | -0.010593 | 61.3672 | 61.5354 | 61.4554 | 61.4931 | 61.5076 | 61.5368 | 61.5037 | 61.534 | 123.088 | 61.6851 | 123.0193 | 61.4491 | 61.5213 | 123.0804 | 61.49 | 122.8678 | 61.5667 | 61.5981 | 61.4979 | 61.5293
1062.0625 | 123.3261 | -61.4777 | 61.647 | 0.025705 | -0.031363 | -0.012 | 0.002454 | 0.027109 | -0.001406 | 0.033424 | 61.5875 | 0.18911 | 61.4729 | -0.046838 | 0.025345 | 61.5753 | 0.007721 | 61.381 | 61.5034 | 61.4463 | 61.4657 | 61.4801 | 61.5048 | 61.4763 | 61.5111 | 123.0651 | 61.6668 | 122.9506 | 61.4308 | 61.503 | 123.053 | 61.4854 | 122.8586 | 61.5621 | 61.5797 | 61.4476 | 61.4652
1063.0625 | 123.2803 | -61.4822 | 61.647 | 0.03944 | -0.035942 | -0.016578 | 0.007033 | 0.027109 | -0.005985 | 0.024268 | 61.5829 | 0.17995 | 61.4729 | -0.051417 | 0.025345 | 61.5662 | 0.007721 | 61.3764 | 61.5217 | 61.4463 | 61.4657 | 61.4893 | 61.5093 | 61.4763 | 61.5065 | 123.0651 | 61.6622 | 122.9552 | 61.4308 | 61.5076 | 123.0484 | 61.49 | 122.8586 | 61.5575 | 61.5752 | 61.4476 | 61.4652
1064.0625 | 123.1659 | -61.4685 | 61.702 | 0.030283 | -0.040521 | -0.012 | 0.007033 | 0.036265 | -0.005985 | 0.028846 | 61.5829 | 0.18453 | 61.5187 | -0.051417 | 0.029923 | 61.5753 | 0.003143 | 61.3764 | 61.4988 | 61.428 | 61.4565 | 61.4755 | 61.5048 | 61.4625 | 61.4974 | 123.0514 | 61.653 | 122.9872 | 61.4171 | 61.4984 | 123.0438 | 61.4716 | 122.8449 | 61.553 | 61.5797 | 61.4888 | 61.5156
1065.0625 | 123.2849 | -61.4822 | 61.647 | 0.030283 | -0.040521 | -0.012 | 0.007033 | 0.031687 | 0.00775 | 0.033424 | 61.5829 | 0.18453 | 61.5279 | -0.046838 | 0.020767 | 61.5799 | 0.007721 | 61.3718 | 61.5125 | 61.4417 | 61.4702 | 61.4893 | 61.5139 | 61.49 | 61.5157 | 123.0651 | 61.6668 | 123.0101 | 61.4354 | 61.503 | 123.0621 | 61.49 | 122.8541 | 61.5621 | 61.5752 | 61.5071 | 61.5202
1066.0625 | 123.2483 | -61.4594 | 61.6745 | 0.034862 | -0.035942 | -0.007421 | 0.007033 | 0.040843 | 0.003172 | 0.024268 | 61.5829 | 0.17537 | 61.4775 | -0.051417 | 0.016188 | 61.5799 | 0.003143 | 61.3764 | 61.4942 | 61.4234 | 61.4519 | 61.4664 | 61.5002 | 61.4625 | 61.4836 | 123.0422 | 61.6347 | 122.9369 | 61.4079 | 61.4755 | 123.0392 | 61.4625 | 122.8357 | 61.5667 | 61.5797 | 61.4613 | 61.4744
1067.0625 | 123.2941 | -61.4777 | 61.6837 | 0.030283 | -0.035942 | -0.012 | -0.002124 | 0.022531 | 0.003172 | 0.028846 | 61.5829 | 0.17995 | 61.4729 | -0.03768 | 0.025345 | 61.5799 | -0.010593 | 61.3764 | 61.5079 | 61.4417 | 61.4657 | 61.4755 | 61.5002 | 61.4808 | 61.5065 | 123.0605 | 61.6576 | 122.9506 | 61.44 | 61.503 | 123.0576 | 61.4671 | 122.8541 | 61.5575 | 61.5935 | 61.4476 | 61.4835
1068.0625 | 123.2803 | -61.4868 | 61.6791 | 0.030283 | -0.0451 | -0.012 | 0.002454 | 0.027109 | -0.010563 | 0.033424 | 61.5875 | 0.18453 | 61.5004 | -0.046838 | 0.029923 | 61.5799 | -0.006014 | 61.3718 | 61.5171 | 61.4417 | 61.4748 | 61.4893 | 61.5139 | 61.4763 | 61.5202 | 123.0743 | 61.6713 | 122.9872 | 61.44 | 61.5167 | 123.0667 | 61.4808 | 122.8586 | 61.5575 | 61.5935 | 61.4705 | 61.5064
1069.0625 | 123.2895 | -61.4868 | 61.647 | 0.030283 | -0.035942 | -0.012 | -0.006703 | 0.036265 | 0.003172 | 0.033424 | 61.5829 | 0.17995 | 61.5096 | -0.046838 | 0.025345 | 61.5707 | -0.006014 | 61.3718 | 61.5171 | 61.4509 | 61.4748 | 61.4801 | 61.5231 | 61.49 | 61.5202 | 123.0697 | 61.6668 | 122.9964 | 61.44 | 61.5122 | 123.0576 | 61.4808 | 122.8586 | 61.5575 | 61.5889 | 61.4842 | 61.5156
1070.0625 | 123.2712 | -61.5097 | 61.6562 | 0.034862 | -0.040521 | -0.012 | -0.002124 | 0.036265 | 0.003172 | 0.028846 | 61.5783 | 0.17537 | 61.4821 | -0.046838 | 0.016188 | 61.5799 | -0.010593 | 61.3764 | 61.5446 | 61.4692 | 61.4977 | 61.5076 | 61.546 | 61.5129 | 61.5386 | 123.088 | 61.6851 | 122.9918 | 61.4629 | 61.5259 | 123.0896 | 61.4991 | 122.8861 | 61.5621 | 61.5889 | 61.4659 | 61.4927
1071.0625 | 123.2803 | -61.4914 | 61.6699 | 0.025705 | -0.040521 | -0.016578 | 0.002454 | 0.036265 | -0.001406 | 0.033424 | 61.5829 | 0.17995 | 61.4775 | -0.042259 | 0.020767 | 61.5753 | -0.001436 | 61.3718 | 61.5171 | 61.4509 | 61.4748 | 61.4938 | 61.5277 | 61.49 | 61.5248 | 123.0743 | 61.6713 | 122.9689 | 61.4491 | 61.5122 | 123.0667 | 61.49 | 122.8632 | 61.5621 | 61.5843 | 61.4567 | 61.4789
1072.0625 | 123.3124 | -61.496 | 61.6608 | 0.03944 | -0.040521 | -0.016578 | 0.002454 | 0.031687 | -0.005985 | 0.024268 | 61.5783 | 0.17537 | 61.5004 | -0.055996 | 0.020767 | 61.5799 | -0.006014 | 61.381 | 61.5354 | 61.4555 | 61.4794 | 61.4984 | 61.5277 | 61.49 | 61.5202 | 123.0743 | 61.6713 | 122.9964 | 61.44 | 61.5167 | 123.0759 | 61.49 | 122.8769 | 61.5575 | 61.5843 | 61.4796 | 61.5064
1073.0625 | 123.2666 | -61.5097 | 61.6608 | 0.034862 | -0.040521 | -0.012 | 0.002454 | 0.031687 | 0.012329 | 0.033424 | 61.5829 | 0.18453 | 61.5141 | -0.046838 | 0.029923 | 61.5753 | -0.010593 | 61.3718 | 61.5446 | 61.4692 | 61.4977 | 61.5122 | 61.5414 | 61.522 | 61.5431 | 123.0926 | 61.6942 | 123.0238 | 61.4629 | 61.5396 | 123.085 | 61.4991 | 122.8815 | 61.553 | 61.5935 | 61.4842 | 61.5247
1074.0625 | 123.2254 | -61.5005 | 61.6379 | 0.025705 | -0.0451 | -0.021157 | 0.007033 | 0.036265 | -0.010563 | 0.024268 | 61.5875 | 0.18453 | 61.4958 | -0.046838 | 0.020767 | 61.5799 | -0.001436 | 61.3672 | 61.5263 | 61.4554 | 61.4794 | 61.5076 | 61.5368 | 61.49 | 61.5248 | 123.088 | 61.6851 | 122.9964 | 61.4537 | 61.5213 | 123.0804 | 61.4991 | 122.8678 | 61.5667 | 61.5889 | 61.4751 | 61.4973
1075.0625 | 123.2803 | -61.4685 | 61.6333 | 0.03944 | -0.035942 | -0.007421 | 0.002454 | 0.031687 | -0.001406 | 0.028846 | 61.5875 | 0.17995 | 61.4821 | -0.051417 | 0.025345 | 61.5799 | -0.006014 | 61.3672 | 61.5079 | 61.4326 | 61.4611 | 61.471 | 61.5002 | 61.4671 | 61.4974 | 123.056 | 61.6485 | 122.9506 | 61.4171 | 61.4939 | 123.0484 | 61.4625 | 122.8357 | 61.5621 | 61.5935 | 61.4567 | 61.4881
1076.0625 | 123.2941 | -61.4822 | 61.6196 | 0.030283 | -0.035942 | -0.012 | 0.007033 | 0.040843 | 0.003172 | 0.033424 | 61.592 | 0.17995 | 61.5004 | -0.046838 | 0.025345 | 61.5707 | -0.006014 | 61.3672 | 61.5125 | 61.4463 | 61.4702 | 61.4893 | 61.5231 | 61.4854 | 61.5157 | 123.0743 | 61.6622 | 122.9826 | 61.4354 | 61.5076 | 123.053 | 61.4762 | 122.8495 | 61.5667 | 61.5981 | 61.4751 | 61.5064
1077.0625 | 123.2849 | -61.4822 | 61.6562 | 0.034862 | -0.0451 | -0.012 | 0.002454 | 0.031687 | 0.003172 | 0.033424 | 61.5829 | 0.18911 | 61.5187 | -0.046838 | 0.025345 | 61.5707 | -0.006014 | 61.3764 | 61.5171 | 61.4371 | 61.4702 | 61.4847 | 61.5139 | 61.4854 | 61.5157 | 123.0651 | 61.6713 | 123.001 | 61.4354 | 61.5076 | 123.053 | 61.4762 | 122.8586 | 61.5575 | 61.5889 | 61.4934 | 61.5247
1078.0625 | 123.1705 | -61.4822 | 61.6425 | 0.025705 | -0.035942 | -0.016578 | 0.002454 | 0.027109 | 0.00775 | 0.033424 | 61.5875 | 0.18453 | 61.5004 | -0.046838 | 0.025345 | 61.5707 | -0.001436 | 61.3718 | 61.5079 | 61.4463 | 61.4657 | 61.4847 | 61.5093 | 61.49 | 61.5157 | 123.0697 | 61.6668 | 122.9826 | 61.4354 | 61.5076 | 123.053 | 61.4808 | 122.8541 | 61.5621 | 61.5889 | 61.4751 | 61.5018
1079.0625 | 123.3032 | -61.5189 | 61.6287 | 0.030283 | -0.040521 | -0.016578 | 0.011611 | 0.031687 | -0.001406 | 0.033424 | 61.5783 | 0.18453 | 61.4684 | -0.046838 | 0.016188 | 61.5707 | -0.019749 | 61.3718 | 61.5491 | 61.4783 | 61.5023 | 61.5305 | 61.5505 | 61.5175 | 61.5523 | 123.0972 | 61.7034 | 122.9872 | 61.472 | 61.535 | 123.0896 | 61.4991 | 122.8907 | 61.5621 | 61.5981 | 61.4522 | 61.4881
1080.0625 | 123.2574 | -61.4822 | 61.6608 | 0.030283 | -0.040521 | -0.007421 | 0.002454 | 0.031687 | 0.003172 | 0.024268 | 61.592 | 0.17995 | 61.5004 | -0.046838 | 0.025345 | 61.5799 | -0.010593 | 61.3764 | 61.5125 | 61.4417 | 61.4748 | 61.4847 | 61.5139 | 61.4854 | 61.5065 | 123.0743 | 61.6622 | 122.9826 | 61.4354 | 61.5076 | 123.0621 | 61.4716 | 122.8586 | 61.5667 | 61.6026 | 61.4751 | 61.511
1081.0625 | 123.2986 | -61.496 | 61.6379 | 0.030283 | -0.040521 | -0.012 | 0.002454 | 0.036265 | 0.003172 | 0.033424 | 61.5875 | 0.18453 | 61.5233 | -0.046838 | 0.016188 | 61.5662 | -0.006014 | 61.3718 | 61.5263 | 61.4555 | 61.484 | 61.4984 | 61.5322 | 61.4991 | 61.5294 | 123.0834 | 61.6805 | 123.0193 | 61.4491 | 61.5122 | 123.0621 | 61.49 | 122.8678 | 61.5713 | 61.5935 | 61.5071 | 61.5293
1082.0625 | 123.3078 | -61.4777 | 61.6653 | 0.034862 | -0.031363 | -0.012 | 0.002454 | 0.031687 | -0.001406 | 0.028846 | 61.5829 | 0.17995 | 61.4958 | -0.046838 | 0.025345 | 61.5845 | -0.001436 | 61.3672 | 61.5125 | 61.4463 | 61.4657 | 61.4801 | 61.5093 | 61.4763 | 61.5065 | 123.0605 | 61.6576 | 122.9735 | 61.4308 | 61.503 | 123.0621 | 61.4762 | 122.8449 | 61.5575 | 61.5843 | 61.4705 | 61.4973
1083.0625 | 123.2849 | -61.4639 | 61.6516 | 0.030283 | -0.031363 | -0.016578 | 0.007033 | 0.036265 | -0.005985 | 0.028846 | 61.5829 | 0.17537 | 61.4821 | -0.046838 | 0.020767 | 61.5707 | -0.006014 | 61.381 | 61.4942 | 61.4326 | 61.4474 | 61.471 | 61.5002 | 61.4579 | 61.4928 | 123.0468 | 61.6393 | 122.946 | 61.4171 | 61.4847 | 123.0347 | 61.4579 | 122.8449 | 61.5621 | 61.5889 | 61.4613 | 61.4881
1084.0625 | 123.2254 | -61.496 | 61.6425 | 0.034862 | -0.040521 | -0.016578 | 0.002454 | 0.031687 | 0.003172 | 0.028846 | 61.5875 | 0.17995 | 61.505 | -0.046838 | 0.020767 | 61.5753 | -0.006014 | 61.3672 | 61.5308 | 61.4555 | 61.4794 | 61.4984 | 61.5277 | 61.4991 | 61.5248 | 123.0834 | 61.6759 | 123.001 | 61.4491 | 61.5167 | 123.0713 | 61.49 | 122.8632 | 61.5667 | 61.5935 | 61.4842 | 61.511
1085.0625 | 123.3124 | -61.4914 | 61.647 | 0.030283 | -0.035942 | -0.016578 | 0.002454 | 0.036265 | -0.001406 | 0.028846 | 61.5875 | 0.17995 | 61.505 | -0.055996 | 0.029923 | 61.5753 | -0.010593 | 61.3672 | 61.5217 | 61.4555 | 61.4748 | 61.4938 | 61.5277 | 61.49 | 61.5202 | 123.0789 | 61.6713 | 122.9964 | 61.4354 | 61.5213 | 123.0667 | 61.4808 | 122.8586 | 61.5575 | 61.5981 | 61.4751 | 61.5156
1086.0625 | 123.3948 | -61.4731 | 61.6196 | 0.025705 | -0.040521 | -0.007421 | -0.002124 | 0.027109 | -0.005985 | 0.028846 | 61.5783 | 0.18453 | 61.4958 | -0.051417 | 0.016188 | 61.5799 | -0.001436 | 61.3764 | 61.4988 | 61.4326 | 61.4657 | 61.471 | 61.5002 | 61.4671 | 61.5019 | 123.0514 | 61.6576 | 122.9689 | 61.4217 | 61.4893 | 123.053 | 61.4716 | 122.8495 | 61.5621 | 61.5797 | 61.4796 | 61.4973
1087.0625 | 123.2529 | -61.4868 | 61.6287 | 0.025705 | -0.040521 | -0.016578 | -0.002124 | 0.036265 | -0.001406 | 0.028846 | 61.5829 | 0.17995 | 61.4821 | -0.046838 | 0.020767 | 61.5707 | -0.006014 | 61.3718 | 61.5125 | 61.4463 | 61.4702 | 61.4847 | 61.5231 | 61.4854 | 61.5157 | 123.0697 | 61.6668 | 122.9689 | 61.44 | 61.5076 | 123.0576 | 61.4808 | 122.8586 | 61.5621 | 61.5889 | 61.4613 | 61.4881
1088.0625 | 123.262 | -61.496 | 61.6562 | 0.030283 | -0.031363 | -0.012 | 0.002454 | 0.031687 | 0.003172 | 0.033424 | 61.5829 | 0.17995 | 61.505 | -0.046838 | 0.025345 | 61.5753 | -0.006014 | 61.3672 | 61.5263 | 61.4646 | 61.484 | 61.4984 | 61.5277 | 61.4991 | 61.5294 | 123.0789 | 61.6759 | 123.001 | 61.4491 | 61.5213 | 123.0713 | 61.49 | 122.8632 | 61.5575 | 61.5889 | 61.4796 | 61.511
1089.0625 | 123.3353 | -61.4731 | 61.6058 | 0.034862 | -0.040521 | -0.012 | 0.002454 | 0.022531 | -0.005985 | 0.033424 | 61.5875 | 0.17995 | 61.5233 | -0.055996 | 0.016188 | 61.5753 | -0.015171 | 61.3672 | 61.5079 | 61.4326 | 61.4611 | 61.4755 | 61.4956 | 61.4671 | 61.5065 | 123.0605 | 61.653 | 122.9964 | 61.4171 | 61.4893 | 123.0484 | 61.4579 | 122.8403 | 61.5713 | 61.6026 | 61.5071 | 61.5385
1090.0625 | 123.2437 | -61.4822 | 61.6425 | 0.030283 | -0.040521 | -0.012 | 0.007033 | 0.027109 | -0.001406 | 0.033424 | 61.592 | 0.18453 | 61.4821 | -0.051417 | 0.020767 | 61.5707 | -0.006014 | 61.3764 | 61.5125 | 61.4417 | 61.4702 | 61.4893 | 61.5093 | 61.4808 | 61.5157 | 123.0743 | 61.6668 | 122.9643 | 61.4308 | 61.503 | 123.053 | 61.4762 | 122.8586 | 61.5713 | 61.5981 | 61.4613 | 61.4881
1091.0625 | 123.2986 | -61.4273 | 61.647 | 0.034862 | -0.035942 | -0.016578 | 0.007033 | 0.036265 | -0.005985 | 0.028846 | 61.5829 | 0.19369 | 61.4821 | -0.051417 | 0.025345 | 61.5753 | -0.006014 | 61.3718 | 61.4622 | 61.3914 | 61.4107 | 61.4343 | 61.4636 | 61.4213 | 61.4562 | 123.0102 | 61.621 | 122.9094 | 61.3759 | 61.4527 | 123.0026 | 61.4213 | 122.7991 | 61.5575 | 61.5889 | 61.4567 | 61.4881
1092.0625 | 123.3124 | -61.4822 | 61.6333 | 0.034862 | -0.035942 | -0.016578 | 0.002454 | 0.036265 | -0.001406 | 0.033424 | 61.592 | 0.17995 | 61.5096 | -0.042259 | 0.025345 | 61.5753 | -0.001436 | 61.381 | 61.5171 | 61.4463 | 61.4657 | 61.4847 | 61.5185 | 61.4808 | 61.5157 | 123.0743 | 61.6622 | 122.9918 | 61.44 | 61.5076 | 123.0576 | 61.4808 | 122.8632 | 61.5667 | 61.5935 | 61.4842 | 61.511
1093.0625 | 123.2437 | -61.4868 | 61.6241 | 0.025705 | -0.035942 | -0.016578 | 0.007033 | 0.027109 | 0.003172 | 0.033424 | 61.5829 | 0.18911 | 61.5279 | -0.051417 | 0.020767 | 61.5845 | 0.003143 | 61.3764 | 61.5125 | 61.4509 | 61.4702 | 61.4938 | 61.5139 | 61.49 | 61.5202 | 123.0697 | 61.6759 | 123.0147 | 61.4354 | 61.5076 | 123.0713 | 61.49 | 122.8632 | 61.5621 | 61.5797 | 61.5071 | 61.5247
1094.0625 | 123.349 | -61.4777 | 61.6058 | 0.025705 | -0.040521 | -0.012 | 0.007033 | 0.027109 | -0.001406 | 0.033424 | 61.5875 | 0.17995 | 61.4729 | -0.046838 | 0.01161 | 61.5799 | -0.006014 | 61.3764 | 61.5034 | 61.4371 | 61.4657 | 61.4847 | 61.5048 | 61.4763 | 61.5111 | 123.0651 | 61.6576 | 122.9506 | 61.4308 | 61.4893 | 123.0576 | 61.4716 | 122.8541 | 61.5759 | 61.5935 | 61.4613 | 61.4789
1095.0625 | 123.2437 | -61.5143 | 61.6241 | 0.034862 | -0.040521 | -0.012 | 0.007033 | 0.031687 | -0.001406 | 0.033424 | 61.5737 | 0.18453 | 61.4638 | -0.046838 | 0.016188 | 61.5799 | -0.001436 | 61.3718 | 61.5491 | 61.4738 | 61.5023 | 61.5213 | 61.546 | 61.5129 | 61.5477 | 123.088 | 61.6988 | 122.9781 | 61.4674 | 61.5305 | 123.0942 | 61.5128 | 122.8861 | 61.5575 | 61.5752 | 61.4476 | 61.4652
1096.0625 | 123.2712 | -61.5005 | 61.647 | 0.034862 | -0.040521 | -0.016578 | 0.002454 | 0.031687 | -0.005985 | 0.028846 | 61.592 | 0.17995 | 61.505 | -0.055996 | 0.020767 | 61.5799 | -0.006014 | 61.3672 | 61.5354 | 61.46 | 61.484 | 61.503 | 61.5322 | 61.4946 | 61.5294 | 123.0926 | 61.6805 | 123.0055 | 61.4446 | 61.5213 | 123.0804 | 61.4945 | 122.8678 | 61.5713 | 61.5981 | 61.4842 | 61.511
1097.0625 | 123.2346 | -61.4914 | 61.6379 | 0.034862 | -0.040521 | -0.016578 | 0.002454 | 0.031687 | -0.001406 | 0.028846 | 61.5875 | 0.17995 | 61.5187 | -0.046838 | 0.020767 | 61.5799 | -0.010593 | 61.3718 | 61.5263 | 61.4509 | 61.4748 | 61.4938 | 61.5231 | 61.49 | 61.5202 | 123.0789 | 61.6713 | 123.0101 | 61.4446 | 61.5122 | 123.0713 | 61.4808 | 122.8632 | 61.5667 | 61.5981 | 61.4979 | 61.5293
1098.0625 | 123.2391 | -61.496 | 61.6333 | 0.034862 | -0.035942 | -0.007421 | 0.002454 | 0.027109 | -0.001406 | 0.033424 | 61.5875 | 0.17995 | 61.4867 | -0.046838 | 0.025345 | 61.5753 | -0.010593 | 61.3672 | 61.5308 | 61.46 | 61.4886 | 61.4984 | 61.5231 | 61.4946 | 61.5294 | 123.0834 | 61.6759 | 122.9826 | 61.4491 | 61.5213 | 123.0713 | 61.4854 | 122.8632 | 61.5621 | 61.5981 | 61.4613 | 61.4973
1099.0625 | 123.3078 | -61.4731 | 61.6013 | 0.034862 | -0.040521 | -0.016578 | 0.002454 | 0.036265 | -0.001406 | 0.028846 | 61.5829 | 0.18453 | 61.4729 | -0.046838 | 0.025345 | 61.5799 | -0.006014 | 61.3718 | 61.5079 | 61.4326 | 61.4565 | 61.4755 | 61.5093 | 61.4717 | 61.5019 | 123.056 | 61.6576 | 122.946 | 61.4262 | 61.4984 | 123.053 | 61.4671 | 122.8449 | 61.5575 | 61.5889 | 61.4476 | 61.4789
1100.0625 | 123.23 | -61.5097 | 61.6425 | 0.034862 | -0.035942 | -0.016578 | 0.002454 | 0.036265 | 0.003172 | 0.033424 | 61.5875 | 0.18911 | 61.5004 | -0.051417 | 0.025345 | 61.5753 | -0.006014 | 61.3672 | 61.5446 | 61.4738 | 61.4931 | 61.5122 | 61.546 | 61.5129 | 61.5431 | 123.0972 | 61.6988 | 123.0101 | 61.4583 | 61.535 | 123.085 | 61.5037 | 122.8769 | 61.5621 | 61.5935 | 61.4751 | 61.5064
1101.0625 | 123.3215 | -61.4731 | 61.6516 | 0.034862 | -0.035942 | -0.016578 | 0.002454 | 0.022531 | 0.003172 | 0.033424 | 61.5829 | 0.17995 | 61.5279 | -0.055996 | 0.020767 | 61.5753 | -0.006014 | 61.3718 | 61.5079 | 61.4371 | 61.4565 | 61.4755 | 61.4956 | 61.4763 | 61.5065 | 123.056 | 61.653 | 123.001 | 61.4171 | 61.4939 | 123.0484 | 61.4671 | 122.8449 | 61.5621 | 61.5889 | 61.5071 | 61.5339
1102.0625 | 123.2391 | -61.5051 | 61.5601 | 0.034862 | -0.040521 | -0.007421 | 0.007033 | 0.027109 | 0.003172 | 0.028846 | 61.5829 | 0.18453 | 61.4821 | -0.051417 | 0.025345 | 61.5799 | 0.003143 | 61.3672 | 61.54 | 61.4646 | 61.4977 | 61.5122 | 61.5322 | 61.5083 | 61.534 | 123.088 | 61.6897 | 122.9872 | 61.4537 | 61.5305 | 123.085 | 61.5083 | 122.8724 | 61.5575 | 61.5797 | 61.4567 | 61.4789
1103.0625 | 123.2483 | -61.4914 | 61.6379 | 0.025705 | -0.031363 | -0.007421 | -0.002124 | 0.036265 | -0.001406 | 0.028846 | 61.5737 | 0.18453 | 61.4684 | -0.046838 | 0.020767 | 61.5753 | -0.006014 | 61.3627 | 61.5171 | 61.46 | 61.484 | 61.4893 | 61.5277 | 61.49 | 61.5202 | 123.0651 | 61.6759 | 122.9597 | 61.4446 | 61.5122 | 123.0667 | 61.4854 | 122.8541 | 61.553 | 61.5797 | 61.4476 | 61.4744
1104.0625 | 123.2574 | -61.4914 | 61.6196 | 0.034862 | -0.035942 | -0.016578 | -0.006703 | 0.031687 | -0.001406 | 0.033424 | 61.5783 | 0.18911 | 61.4867 | -0.051417 | 0.016188 | 61.5707 | -0.001436 | 61.3672 | 61.5263 | 61.4555 | 61.4748 | 61.4847 | 61.5231 | 61.49 | 61.5248 | 123.0697 | 61.6805 | 122.9781 | 61.44 | 61.5076 | 123.0621 | 61.49 | 122.8586 | 61.5621 | 61.5797 | 61.4705 | 61.4881
1105.0625 | 123.2391 | -61.4914 | 61.6425 | 0.025705 | -0.035942 | -0.012 | 0.002454 | 0.036265 | 0.00775 | 0.033424 | 61.5875 | 0.18911 | 61.5279 | -0.046838 | 0.025345 | 61.5753 | -0.006014 | 61.3764 | 61.5171 | 61.4555 | 61.4794 | 61.4938 | 61.5277 | 61.4991 | 61.5248 | 123.0789 | 61.6805 | 123.0193 | 61.4446 | 61.5167 | 123.0667 | 61.4854 | 122.8678 | 61.5621 | 61.5935 | 61.5025 | 61.5339
1106.0625 | 123.2712 | -61.4731 | 61.6333 | 0.030283 | -0.035942 | -0.007421 | 0.002454 | 0.031687 | -0.001406 | 0.033424 | 61.5829 | 0.17995 | 61.4821 | -0.051417 | 0.025345 | 61.5845 | 0.003143 | 61.3764 | 61.5034 | 61.4371 | 61.4657 | 61.4755 | 61.5048 | 61.4717 | 61.5065 | 123.056 | 61.653 | 122.9552 | 61.4217 | 61.4984 | 123.0576 | 61.4762 | 122.8495 | 61.5575 | 61.5797 | 61.4567 | 61.4789
1107.0625 | 123.2254 | -61.5005 | 61.6379 | 0.030283 | -0.040521 | -0.016578 | 0.002454 | 0.031687 | 0.00775 | 0.028846 | 61.5875 | 0.17995 | 61.4684 | -0.042259 | 0.020767 | 61.5707 | -0.001436 | 61.3672 | 61.5308 | 61.46 | 61.484 | 61.503 | 61.5322 | 61.5083 | 61.5294 | 123.088 | 61.6805 | 122.9689 | 61.4583 | 61.5213 | 123.0713 | 61.4991 | 122.8678 | 61.5667 | 61.5889 | 61.4476 | 61.4698
1108.0625 | 123.2574 | -61.5326 | 61.6196 | 0.030283 | -0.035942 | -0.012 | 0.002454 | 0.031687 | -0.001406 | 0.028846 | 61.5875 | 0.19369 | 61.4821 | -0.055996 | 0.025345 | 61.5753 | 0.003143 | 61.3764 | 61.5629 | 61.4967 | 61.5206 | 61.535 | 61.5643 | 61.5312 | 61.5614 | 123.1201 | 61.7263 | 123.0147 | 61.4766 | 61.5579 | 123.1079 | 61.5357 | 122.909 | 61.5621 | 61.5843 | 61.4567 | 61.4789
1109.0625 | 123.349 | -61.4777 | 61.5967 | 0.025705 | -0.035942 | -0.016578 | 0.002454 | 0.027109 | -0.001406 | 0.033424 | 61.5875 | 0.17995 | 61.5279 | -0.051417 | 0.020767 | 61.5753 | -0.001436 | 61.3764 | 61.5034 | 61.4417 | 61.4611 | 61.4801 | 61.5048 | 61.4763 | 61.5111 | 123.0651 | 61.6576 | 123.0055 | 61.4262 | 61.4984 | 123.053 | 61.4762 | 122.8541 | 61.5667 | 61.5889 | 61.5071 | 61.5293
1110.0625 | 123.4131 | -61.441 | 61.6058 | 0.034862 | -0.040521 | -0.012 | -0.002124 | 0.031687 | -0.005985 | 0.028846 | 61.5875 | 0.17537 | 61.505 | -0.051417 | 0.020767 | 61.5799 | -0.001436 | 61.3764 | 61.4759 | 61.4005 | 61.429 | 61.4389 | 61.4727 | 61.4351 | 61.4699 | 123.0285 | 61.6164 | 122.946 | 61.3896 | 61.4618 | 123.0209 | 61.4396 | 122.8174 | 61.5667 | 61.5889 | 61.4842 | 61.5064
1111.0625 | 123.2986 | -61.4731 | 61.6516 | 0.030283 | -0.040521 | -0.012 | -0.002124 | 0.031687 | 0.003172 | 0.033424 | 61.5783 | 0.18453 | 61.4775 | -0.060575 | 0.020767 | 61.5799 | -0.006014 | 61.3764 | 61.5034 | 61.4326 | 61.4611 | 61.471 | 61.5048 | 61.4763 | 61.5065 | 123.0514 | 61.6576 | 122.9506 | 61.4125 | 61.4939 | 123.053 | 61.4671 | 122.8495 | 61.5575 | 61.5843 | 61.4567 | 61.4835
1112.0625 | 123.262 | -61.4914 | 61.6241 | 0.034862 | -0.031363 | -0.012 | 0.007033 | 0.031687 | -0.001406 | 0.033424 | 61.5829 | 0.18911 | 61.4729 | -0.046838 | 0.020767 | 61.5799 | -0.001436 | 61.381 | 61.5263 | 61.46 | 61.4794 | 61.4984 | 61.5231 | 61.49 | 61.5248 | 123.0743 | 61.6805 | 122.9643 | 61.4446 | 61.5122 | 123.0713 | 61.49 | 122.8724 | 61.5621 | 61.5843 | 61.4522 | 61.4744
1113.0625 | 123.2758 | -61.4868 | 61.647 | 0.030283 | -0.026784 | -0.016578 | 0.011611 | 0.036265 | 0.00775 | 0.038003 | 61.5875 | 0.18911 | 61.5279 | -0.046838 | 0.016188 | 61.5845 | -0.001436 | 61.381 | 61.5171 | 61.46 | 61.4702 | 61.4984 | 61.5231 | 61.4946 | 61.5248 | 123.0743 | 61.6759 | 123.0147 | 61.44 | 61.503 | 123.0713 | 61.4854 | 122.8678 | 61.5713 | 61.5889 | 61.5117 | 61.5293
1114.0625 | 123.3627 | -61.4868 | 61.5921 | 0.030283 | -0.026784 | -0.016578 | 0.002454 | 0.036265 | -0.001406 | 0.033424 | 61.5829 | 0.18911 | 61.5141 | -0.046838 | 0.020767 | 61.5707 | 0.003143 | 61.3718 | 61.5171 | 61.46 | 61.4702 | 61.4893 | 61.5231 | 61.4854 | 61.5202 | 123.0697 | 61.6759 | 123.001 | 61.44 | 61.5076 | 123.0576 | 61.49 | 122.8586 | 61.5621 | 61.5797 | 61.4934 | 61.511
1115.0625 | 123.3307 | -61.4594 | 61.6196 | 0.025705 | -0.031363 | -0.021157 | 0.007033 | 0.027109 | -0.001406 | 0.028846 | 61.592 | 0.18911 | 61.4729 | -0.042259 | 0.025345 | 61.5753 | -0.001436 | 61.3718 | 61.4851 | 61.428 | 61.4382 | 61.4664 | 61.4865 | 61.4579 | 61.4882 | 123.0514 | 61.6485 | 122.9323 | 61.4171 | 61.4847 | 123.0347 | 61.4579 | 122.8312 | 61.5667 | 61.5935 | 61.4476 | 61.4744
1116.0625 | 123.2483 | -61.496 | 61.6425 | 0.034862 | -0.031363 | -0.012 | 0.007033 | 0.027109 | -0.001406 | 0.028846 | 61.5829 | 0.18453 | 61.4729 | -0.042259 | 0.016188 | 61.5753 | -0.010593 | 61.3718 | 61.5308 | 61.4646 | 61.484 | 61.503 | 61.5231 | 61.4946 | 61.5248 | 123.0789 | 61.6805 | 122.9689 | 61.4537 | 61.5122 | 123.0713 | 61.4854 | 122.8678 | 61.5667 | 61.5935 | 61.4567 | 61.4835
1117.0625 | 123.2391 | -61.4868 | 61.6333 | 0.03944 | -0.031363 | -0.016578 | 0.002454 | 0.027109 | 0.00775 | 0.028846 | 61.5875 | 0.17995 | 61.5141 | -0.046838 | 0.016188 | 61.5753 | -0.006014 | 61.3672 | 61.5263 | 61.4555 | 61.4702 | 61.4893 | 61.5139 | 61.4946 | 61.5157 | 123.0743 | 61.6668 | 123.001 | 61.44 | 61.503 | 123.0621 | 61.4808 | 122.8541 | 61.5713 | 61.5935 | 61.4979 | 61.5202
1118.0625 | 123.3032 | -61.4639 | 61.6425 | 0.021127 | -0.035942 | -0.016578 | 0.007033 | 0.036265 | 0.003172 | 0.033424 | 61.5875 | 0.18453 | 61.5187 | -0.051417 | 0.025345 | 61.5845 | 0.007721 | 61.3718 | 61.4851 | 61.428 | 61.4474 | 61.471 | 61.5002 | 61.4671 | 61.4974 | 123.0514 | 61.6485 | 122.9826 | 61.4125 | 61.4893 | 123.0484 | 61.4716 | 122.8357 | 61.5621 | 61.5797 | 61.4934 | 61.511
1119.0625 | 123.3719 | -61.4548 | 61.6013 | 0.025705 | -0.026784 | -0.012 | -0.002124 | 0.031687 | -0.001406 | 0.024268 | 61.5829 | 0.19369 | 61.4775 | -0.051417 | 0.020767 | 61.5753 | 0.003143 | 61.3764 | 61.4805 | 61.428 | 61.4428 | 61.4526 | 61.4865 | 61.4534 | 61.479 | 123.0377 | 61.6485 | 122.9323 | 61.4034 | 61.4755 | 123.0301 | 61.4579 | 122.8312 | 61.5621 | 61.5797 | 61.4567 | 61.4744
1120.0625 | 123.3856 | -61.4685 | 61.5829 | 0.025705 | -0.035942 | -0.012 | 0.002454 | 0.031687 | -0.010563 | 0.01969 | 61.5829 | 0.17995 | 61.4729 | -0.051417 | 0.016188 | 61.5753 | 0.003143 | 61.3718 | 61.4942 | 61.4326 | 61.4565 | 61.471 | 61.5002 | 61.4579 | 61.4882 | 123.0514 | 61.6485 | 122.9414 | 61.4171 | 61.4847 | 123.0438 | 61.4716 | 122.8403 | 61.5667 | 61.5797 | 61.4567 | 61.4698
1121.0625 | 123.3124 | -61.4639 | 61.6287 | 0.034862 | -0.035942 | -0.021157 | 0.002454 | 0.027109 | -0.001406 | 0.033424 | 61.5875 | 0.18453 | 61.4912 | -0.046838 | 0.020767 | 61.5799 | 0.003143 | 61.3764 | 61.4988 | 61.428 | 61.4428 | 61.4664 | 61.491 | 61.4625 | 61.4974 | 123.0514 | 61.6485 | 122.9552 | 61.4171 | 61.4847 | 123.0438 | 61.4671 | 122.8403 | 61.5667 | 61.5843 | 61.4705 | 61.4881
1122.0625 | 123.3078 | -61.4639 | 61.6425 | 0.030283 | -0.031363 | -0.016578 | 0.002454 | 0.027109 | -0.001406 | 0.038003 | 61.5875 | 0.17537 | 61.5187 | -0.051417 | 0.025345 | 61.5845 | 0.007721 | 61.381 | 61.4942 | 61.4326 | 61.4474 | 61.4664 | 61.491 | 61.4625 | 61.5019 | 123.0514 | 61.6393 | 122.9826 | 61.4125 | 61.4893 | 123.0484 | 61.4716 | 122.8449 | 61.5621 | 61.5797 | 61.4934 | 61.511
1123.0625 | 123.3398 | -61.4822 | 61.647 | 0.03944 | -0.026784 | -0.016578 | 0.002454 | 0.036265 | -0.005985 | 0.024268 | 61.5875 | 0.18453 | 61.5004 | -0.046838 | 0.025345 | 61.5845 | 0.003143 | 61.3764 | 61.5217 | 61.4555 | 61.4657 | 61.4847 | 61.5185 | 61.4763 | 61.5065 | 123.0697 | 61.6668 | 122.9826 | 61.4354 | 61.5076 | 123.0667 | 61.4854 | 122.8586 | 61.5621 | 61.5843 | 61.4751 | 61.4973
1124.0625 | 123.3078 | -61.4777 | 61.6287 | 0.034862 | -0.040521 | -0.012 | 0.007033 | 0.040843 | 0.003172 | 0.033424 | 61.5829 | 0.18453 | 61.4729 | -0.051417 | 0.020767 | 61.5799 | -0.001436 | 61.3718 | 61.5125 | 61.4371 | 61.4657 | 61.4847 | 61.5185 | 61.4808 | 61.5111 | 123.0605 | 61.6622 | 122.9506 | 61.4262 | 61.4984 | 123.0576 | 61.4762 | 122.8495 | 61.5621 | 61.5843 | 61.4522 | 61.4744
1125.0625 | 123.3307 | -61.4777 | 61.6745 | 0.030283 | -0.031363 | -0.016578 | -0.002124 | 0.027109 | -0.001406 | 0.033424 | 61.5783 | 0.18453 | 61.4729 | -0.042259 | 0.020767 | 61.5662 | 0.003143 | 61.3764 | 61.5079 | 61.4463 | 61.4611 | 61.4755 | 61.5048 | 61.4763 | 61.5111 | 123.056 | 61.6622 | 122.9506 | 61.4354 | 61.4984 | 123.0438 | 61.4808 | 122.8541 | 61.5575 | 61.5752 | 61.4522 | 61.4698
1126.0625 | 123.2666 | -61.4914 | 61.6653 | 0.025705 | -0.035942 | -0.021157 | 0.007033 | 0.027109 | -0.001406 | 0.028846 | 61.5875 | 0.17995 | 61.4684 | -0.042259 | 0.020767 | 61.5753 | 0.003143 | 61.3764 | 61.5171 | 61.4555 | 61.4702 | 61.4984 | 61.5185 | 61.49 | 61.5202 | 123.0789 | 61.6713 | 122.9597 | 61.4491 | 61.5122 | 123.0667 | 61.4945 | 122.8678 | 61.5667 | 61.5843 | 61.4476 | 61.4652
1127.0625 | 123.2483 | -61.5005 | 61.6608 | 0.034862 | -0.031363 | -0.016578 | 0.002454 | 0.036265 | 0.003172 | 0.033424 | 61.5875 | 0.17995 | 61.4867 | -0.042259 | 0.025345 | 61.5845 | 0.003143 | 61.381 | 61.5354 | 61.4692 | 61.484 | 61.503 | 61.5368 | 61.5037 | 61.534 | 123.088 | 61.6805 | 122.9872 | 61.4583 | 61.5259 | 123.085 | 61.5037 | 122.8815 | 61.5621 | 61.5843 | 61.4613 | 61.4835
1128.0625 | 123.2712 | -61.4731 | 61.6516 | 0.034862 | -0.031363 | -0.021157 | -0.002124 | 0.031687 | -0.001406 | 0.042581 | 61.5875 | 0.17995 | 61.5233 | -0.051417 | 0.020767 | 61.5707 | 0.003143 | 61.381 | 61.5079 | 61.4417 | 61.4519 | 61.471 | 61.5048 | 61.4717 | 61.5157 | 123.0605 | 61.653 | 122.9964 | 61.4217 | 61.4939 | 123.0438 | 61.4762 | 122.8541 | 61.5667 | 61.5843 | 61.5025 | 61.5202
1129.0625 | 123.3078 | -61.4777 | 61.6516 | 0.025705 | -0.031363 | -0.007421 | 0.002454 | 0.022531 | 0.00775 | 0.033424 | 61.592 | 0.18453 | 61.5233 | -0.042259 | 0.020767 | 61.5799 | 0.003143 | 61.3764 | 61.5034 | 61.4463 | 61.4702 | 61.4801 | 61.5002 | 61.4854 | 61.5111 | 123.0697 | 61.6622 | 123.001 | 61.4354 | 61.4984 | 123.0576 | 61.4808 | 122.8541 | 61.5713 | 61.5889 | 61.5025 | 61.5202
1130.0625 | 123.2803 | -61.4914 | 61.6608 | 0.030283 | -0.031363 | -0.016578 | 0.007033 | 0.031687 | -0.001406 | 0.028846 | 61.5783 | 0.17995 | 61.4867 | -0.051417 | 0.034501 | 61.5799 | 0.003143 | 61.381 | 61.5217 | 61.46 | 61.4748 | 61.4984 | 61.5231 | 61.49 | 61.5202 | 123.0697 | 61.6713 | 122.9781 | 61.44 | 61.5259 | 123.0713 | 61.4945 | 122.8724 | 61.5438 | 61.5752 | 61.4522 | 61.4835
1131.0625 | 123.2437 | -61.4868 | 61.6882 | 0.034862 | -0.035942 | -0.012 | 0.007033 | 0.027109 | 0.003172 | 0.028846 | 61.5783 | 0.18453 | 61.4775 | -0.046838 | 0.029923 | 61.5753 | 0.007721 | 61.3718 | 61.5217 | 61.4509 | 61.4748 | 61.4938 | 61.5139 | 61.49 | 61.5157 | 123.0651 | 61.6713 | 122.9643 | 61.44 | 61.5167 | 123.0621 | 61.4945 | 122.8586 | 61.5484 | 61.5706 | 61.4476 | 61.4698
1132.0625 | 123.2391 | -61.5005 | 61.6425 | 0.030283 | -0.035942 | -0.012 | 0.002454 | 0.031687 | 0.003172 | 0.042581 | 61.5829 | 0.18911 | 61.4912 | -0.051417 | 0.025345 | 61.5753 | 0.007721 | 61.3718 | 61.5308 | 61.4646 | 61.4885 | 61.503 | 61.5322 | 61.5037 | 61.5431 | 123.0834 | 61.6897 | 122.9918 | 61.4491 | 61.5259 | 123.0759 | 61.5083 | 122.8724 | 61.5575 | 61.5752 | 61.4659 | 61.4835
1133.0625 | 123.317 | -61.4502 | 61.6516 | 0.030283 | -0.031363 | -0.016578 | 0.007033 | 0.031687 | 0.00775 | 0.033424 | 61.592 | 0.17995 | 61.5233 | -0.042259 | 0.025345 | 61.5799 | 0.012299 | 61.381 | 61.4805 | 61.4188 | 61.4336 | 61.4572 | 61.4819 | 61.4579 | 61.4836 | 123.0422 | 61.6301 | 122.9735 | 61.4079 | 61.4755 | 123.0301 | 61.4625 | 122.8312 | 61.5667 | 61.5797 | 61.4979 | 61.511
1134.0625 | 123.3215 | -61.4685 | 61.6287 | 0.030283 | -0.026784 | -0.016578 | 0.002454 | 0.027109 | 0.003172 | 0.028846 | 61.592 | 0.17995 | 61.4867 | -0.051417 | 0.025345 | 61.5753 | -0.001436 | 61.3856 | 61.4988 | 61.4417 | 61.4519 | 61.471 | 61.4956 | 61.4717 | 61.4974 | 123.0605 | 61.6485 | 122.9552 | 61.4171 | 61.4939 | 123.0438 | 61.4671 | 122.8541 | 61.5667 | 61.5935 | 61.4613 | 61.4881
1135.0625 | 123.2941 | -61.4822 | 61.647 | 0.030283 | -0.035942 | -0.012 | -0.002124 | 0.036265 | 0.00775 | 0.024268 | 61.5783 | 0.18911 | 61.4684 | -0.046838 | 0.029923 | 61.5707 | 0.007721 | 61.3764 | 61.5125 | 61.4463 | 61.4702 | 61.4801 | 61.5185 | 61.49 | 61.5065 | 123.0605 | 61.6713 | 122.9506 | 61.4354 | 61.5122 | 123.053 | 61.49 | 122.8586 | 61.5484 | 61.5706 | 61.4384 | 61.4606
1136.0625 | 123.262 | -61.4731 | 61.6516 | 0.025705 | -0.035942 | -0.012 | 0.011611 | 0.027109 | 0.003172 | 0.024268 | 61.5829 | 0.18453 | 61.4775 | -0.051417 | 0.025345 | 61.5753 | 0.003143 | 61.381 | 61.4988 | 61.4371 | 61.4611 | 61.4847 | 61.5002 | 61.4763 | 61.4974 | 123.056 | 61.6576 | 122.9506 | 61.4217 | 61.4984 | 123.0484 | 61.4762 | 122.8541 | 61.5575 | 61.5797 | 61.4522 | 61.4744
1137.0625 | 123.2712 | -61.4777 | 61.6882 | 0.025705 | -0.035942 | -0.012 | 0.011611 | 0.031687 | -0.001406 | 0.028846 | 61.5875 | 0.18453 | 61.5279 | -0.042259 | 0.025345 | 61.5845 | -0.006014 | 61.3718 | 61.5034 | 61.4417 | 61.4657 | 61.4893 | 61.5093 | 61.4763 | 61.5065 | 123.0651 | 61.6622 | 123.0055 | 61.4354 | 61.503 | 123.0621 | 61.4716 | 122.8495 | 61.5621 | 61.5935 | 61.5025 | 61.5339
1138.0625 | 123.2437 | -61.496 | 61.6653 | 0.030283 | -0.035942 | -0.016578 | 0.002454 | 0.036265 | 0.012329 | 0.038003 | 61.5829 | 0.18911 | 61.5096 | -0.046838 | 0.025345 | 61.5753 | -0.006014 | 61.381 | 61.5263 | 61.46 | 61.4794 | 61.4984 | 61.5322 | 61.5083 | 61.534 | 123.0789 | 61.6851 | 123.0055 | 61.4491 | 61.5213 | 123.0713 | 61.49 | 122.8769 | 61.5575 | 61.5889 | 61.4842 | 61.5156
1139.0625 | 123.2803 | -61.4731 | 61.6425 | 0.030283 | -0.0451 | -0.016578 | 0.002454 | 0.027109 | -0.005985 | 0.028846 | 61.5829 | 0.18911 | 61.4775 | -0.051417 | 0.016188 | 61.5753 | -0.006014 | 61.381 | 61.5034 | 61.428 | 61.4565 | 61.4755 | 61.5002 | 61.4671 | 61.5019 | 123.056 | 61.6622 | 122.9506 | 61.4217 | 61.4893 | 123.0484 | 61.4671 | 122.8541 | 61.5667 | 61.5889 | 61.4613 | 61.4835
1140.0625 | 123.3765 | -61.4685 | 61.6333 | 0.025705 | -0.031363 | -0.016578 | -0.002124 | 0.027109 | 0.003172 | 0.028846 | 61.5829 | 0.18453 | 61.4775 | -0.046838 | 0.025345 | 61.5799 | -0.001436 | 61.381 | 61.4942 | 61.4371 | 61.4519 | 61.4664 | 61.4956 | 61.4717 | 61.4974 | 123.0514 | 61.653 | 122.946 | 61.4217 | 61.4939 | 123.0484 | 61.4671 | 122.8495 | 61.5575 | 61.5843 | 61.4522 | 61.4789
1141.0625 | 123.3627 | -61.4594 | 61.615 | 0.030283 | -0.035942 | -0.016578 | 0.002454 | 0.031687 | -0.001406 | 0.038003 | 61.592 | 0.17995 | 61.5324 | -0.042259 | 0.025345 | 61.5707 | -0.001436 | 61.3764 | 61.4896 | 61.4234 | 61.4428 | 61.4618 | 61.491 | 61.4579 | 61.4974 | 123.0514 | 61.6393 | 122.9918 | 61.4171 | 61.4847 | 123.0301 | 61.4579 | 122.8357 | 61.5667 | 61.5935 | 61.5071 | 61.5339
1142.0625 | 123.3536 | -61.4777 | 61.647 | 0.030283 | -0.031363 | -0.016578 | 0.002454 | 0.031687 | -0.001406 | 0.028846 | 61.5875 | 0.18453 | 61.5187 | -0.055996 | 0.029923 | 61.5799 | -0.010593 | 61.3764 | 61.5079 | 61.4463 | 61.4611 | 61.4801 | 61.5093 | 61.4763 | 61.5065 | 123.0651 | 61.6622 | 122.9964 | 61.4217 | 61.5076 | 123.0576 | 61.4671 | 122.8541 | 61.5575 | 61.5981 | 61.4888 | 61.5293
1143.0625 | 123.2895 | -61.4731 | 61.6745 | 0.030283 | -0.040521 | -0.012 | 0.007033 | 0.031687 | -0.001406 | 0.028846 | 61.5875 | 0.18453 | 61.4867 | -0.051417 | 0.029923 | 61.5753 | -0.010593 | 61.3718 | 61.5034 | 61.4326 | 61.4611 | 61.4801 | 61.5048 | 61.4717 | 61.5019 | 123.0605 | 61.6576 | 122.9597 | 61.4217 | 61.503 | 123.0484 | 61.4625 | 122.8449 | 61.5575 | 61.5981 | 61.4567 | 61.4973
1144.0625 | 123.3353 | -61.4822 | 61.6653 | 0.034862 | -0.035942 | -0.021157 | 0.007033 | 0.031687 | -0.001406 | 0.033424 | 61.5829 | 0.18453 | 61.4775 | -0.046838 | 0.020767 | 61.5753 | -0.006014 | 61.3672 | 61.5171 | 61.4463 | 61.4611 | 61.4893 | 61.5139 | 61.4808 | 61.5157 | 123.0651 | 61.6668 | 122.9597 | 61.4354 | 61.503 | 123.0576 | 61.4762 | 122.8495 | 61.5621 | 61.5889 | 61.4567 | 61.4835
1145.0625 | 123.2803 | -61.4777 | 61.6516 | 0.025705 | -0.031363 | -0.016578 | 0.011611 | 0.031687 | -0.001406 | 0.033424 | 61.592 | 0.17995 | 61.5187 | -0.046838 | 0.020767 | 61.5799 | -0.001436 | 61.3718 | 61.5034 | 61.4463 | 61.4611 | 61.4893 | 61.5093 | 61.4763 | 61.5111 | 123.0697 | 61.6576 | 122.9964 | 61.4308 | 61.4984 | 123.0576 | 61.4762 | 122.8495 | 61.5713 | 61.5935 | 61.4979 | 61.5202
1146.0625 | 123.3353 | -61.4548 | 61.6562 | 0.030283 | -0.031363 | -0.012 | 0.002454 | 0.036265 | 0.003172 | 0.038003 | 61.592 | 0.19369 | 61.5233 | -0.060575 | 0.020767 | 61.5753 | -0.006014 | 61.3718 | 61.4851 | 61.4234 | 61.4428 | 61.4572 | 61.491 | 61.4579 | 61.4928 | 123.0468 | 61.6485 | 122.9781 | 61.3942 | 61.4755 | 123.0301 | 61.4488 | 122.8266 | 61.5713 | 61.5981 | 61.5025 | 61.5293
1147.0625 | 123.3261 | -61.4456 | 61.6104 | 0.030283 | -0.031363 | -0.016578 | -0.002124 | 0.031687 | 0.003172 | 0.028846 | 61.5875 | 0.17995 | 61.4821 | -0.046838 | 0.016188 | 61.5753 | -0.006014 | 61.3764 | 61.4759 | 61.4143 | 61.429 | 61.4435 | 61.4773 | 61.4488 | 61.4745 | 123.0331 | 61.6256 | 122.9277 | 61.3988 | 61.4618 | 123.0209 | 61.4396 | 122.822 | 61.5713 | 61.5935 | 61.4659 | 61.4881
1148.0625 | 123.3994 | -61.4456 | 61.6608 | 0.021127 | -0.031363 | -0.016578 | 0.007033 | 0.027109 | -0.010563 | 0.033424 | 61.5829 | 0.18453 | 61.4867 | -0.046838 | 0.025345 | 61.5753 | -0.010593 | 61.3764 | 61.4667 | 61.4143 | 61.429 | 61.4527 | 61.4727 | 61.4351 | 61.479 | 123.0285 | 61.6301 | 122.9323 | 61.3988 | 61.471 | 123.0209 | 61.435 | 122.822 | 61.5575 | 61.5935 | 61.4613 | 61.4973
1149.0625 | 123.3444 | -61.4685 | 61.6425 | 0.025705 | -0.031363 | -0.021157 | 0.002454 | 0.022531 | -0.001406 | 0.024268 | 61.592 | 0.17995 | 61.505 | -0.046838 | 0.020767 | 61.5753 | -0.006014 | 61.3764 | 61.4942 | 61.4371 | 61.4473 | 61.471 | 61.491 | 61.4671 | 61.4928 | 123.0605 | 61.6485 | 122.9735 | 61.4217 | 61.4893 | 123.0438 | 61.4625 | 122.8449 | 61.5713 | 61.5981 | 61.4842 | 61.511
1150.0625 | 123.2986 | -61.4822 | 61.6516 | 0.030283 | -0.031363 | -0.016578 | 0.002454 | 0.031687 | 0.003172 | 0.028846 | 61.5875 | 0.18911 | 61.5187 | -0.046838 | 0.034501 | 61.5753 | -0.001436 | 61.3718 | 61.5125 | 61.4509 | 61.4657 | 61.4847 | 61.5139 | 61.4854 | 61.5111 | 123.0697 | 61.6713 | 123.001 | 61.4354 | 61.5167 | 123.0576 | 61.4808 | 122.8541 | 61.553 | 61.5889 | 61.4842 | 61.5202
1151.0625 | 123.2803 | -61.4594 | 61.6562 | 0.021127 | -0.035942 | -0.012 | 0.002454 | 0.031687 | -0.001406 | 0.038003 | 61.5875 | 0.17995 | 61.4958 | -0.046838 | 0.020767 | 61.5799 | -0.010593 | 61.3718 | 61.4805 | 61.4234 | 61.4474 | 61.4618 | 61.491 | 61.4579 | 61.4974 | 123.0468 | 61.6393 | 122.9552 | 61.4125 | 61.4801 | 123.0392 | 61.4488 | 122.8312 | 61.5667 | 61.5981 | 61.4751 | 61.5064
1152.0625 | 123.3261 | -61.4639 | 61.6745 | 0.030283 | -0.035942 | -0.016578 | 0.007033 | 0.031687 | -0.001406 | 0.028846 | 61.5829 | 0.17995 | 61.4821 | -0.046838 | 0.025345 | 61.5753 | -0.001436 | 61.3718 | 61.4942 | 61.428 | 61.4474 | 61.471 | 61.4956 | 61.4625 | 61.4928 | 123.0468 | 61.6439 | 122.946 | 61.4171 | 61.4893 | 123.0392 | 61.4625 | 122.8357 | 61.5575 | 61.5843 | 61.4567 | 61.4835
1153.0625 | 123.3307 | -61.4548 | 61.6699 | 0.030283 | -0.035942 | -0.016578 | 0.007033 | 0.036265 | 0.003172 | 0.028846 | 61.5829 | 0.18911 | 61.4867 | -0.046838 | 0.029923 | 61.5799 | -0.001436 | 61.3764 | 61.4851 | 61.4188 | 61.4382 | 61.4618 | 61.491 | 61.4579 | 61.4836 | 123.0377 | 61.6439 | 122.9414 | 61.4079 | 61.4847 | 123.0347 | 61.4533 | 122.8312 | 61.553 | 61.5843 | 61.4567 | 61.4881
1154.0625 | 123.2666 | -61.4685 | 61.6516 | 0.025705 | -0.026784 | -0.016578 | 0.002454 | 0.027109 | 0.003172 | 0.028846 | 61.5829 | 0.17995 | 61.5187 | -0.051417 | 0.020767 | 61.5707 | -0.006014 | 61.3718 | 61.4942 | 61.4417 | 61.4519 | 61.471 | 61.4956 | 61.4717 | 61.4974 | 123.0514 | 61.6485 | 122.9872 | 61.4171 | 61.4893 | 123.0392 | 61.4625 | 122.8403 | 61.5621 | 61.5889 | 61.4979 | 61.5247
1155.0625 | 123.3948 | -61.4456 | 61.615 | 0.030283 | -0.035942 | -0.021157 | 0.002454 | 0.027109 | -0.001406 | 0.033424 | 61.592 | 0.18911 | 61.4958 | -0.042259 | 0.020767 | 61.5845 | -0.006014 | 61.3672 | 61.4759 | 61.4097 | 61.4245 | 61.4481 | 61.4727 | 61.4442 | 61.479 | 123.0377 | 61.6347 | 122.9414 | 61.4034 | 61.4664 | 123.0301 | 61.4396 | 122.8129 | 61.5713 | 61.5981 | 61.4751 | 61.5018
1156.0625 | 123.3078 | -61.4685 | 61.6608 | 0.034862 | -0.031363 | -0.012 | -0.002124 | 0.031687 | -0.001406 | 0.038003 | 61.5875 | 0.17995 | 61.4775 | -0.046838 | 0.025345 | 61.5753 | 0.007721 | 61.3764 | 61.5034 | 61.4371 | 61.4565 | 61.4664 | 61.5002 | 61.4671 | 61.5065 | 123.056 | 61.6485 | 122.946 | 61.4217 | 61.4939 | 123.0438 | 61.4762 | 122.8449 | 61.5621 | 61.5797 | 61.4522 | 61.4698
1157.0625 | 123.2803 | -61.4868 | 61.6699 | 0.030283 | -0.035942 | -0.012 | 0.007033 | 0.031687 | 0.003172 | 0.024268 | 61.5875 | 0.18453 | 61.4867 | -0.051417 | 0.025345 | 61.5753 | -0.006014 | 61.3764 | 61.5171 | 61.4509 | 61.4748 | 61.4938 | 61.5185 | 61.49 | 61.5111 | 123.0743 | 61.6713 | 122.9735 | 61.4354 | 61.5122 | 123.0621 | 61.4808 | 122.8632 | 61.5621 | 61.5935 | 61.4613 | 61.4927
1158.0625 | 123.2529 | -61.4822 | 61.6653 | 0.030283 | -0.040521 | -0.021157 | 0.007033 | 0.040843 | 0.00775 | 0.033424 | 61.5875 | 0.18911 | 61.5324 | -0.051417 | 0.025345 | 61.5753 | -0.006014 | 61.381 | 61.5125 | 61.4417 | 61.4611 | 61.4893 | 61.5231 | 61.49 | 61.5157 | 123.0697 | 61.6713 | 123.0147 | 61.4308 | 61.5076 | 123.0576 | 61.4762 | 122.8632 | 61.5621 | 61.5935 | 61.5071 | 61.5385
1159.0625 | 123.2803 | -61.4594 | 61.6653 | 0.034862 | -0.035942 | -0.021157 | 0.002454 | 0.027109 | 0.003172 | 0.042581 | 61.5875 | 0.18911 | 61.4958 | -0.051417 | 0.029923 | 61.5799 | -0.006014 | 61.381 | 61.4942 | 61.4234 | 61.4382 | 61.4618 | 61.4865 | 61.4625 | 61.5019 | 123.0468 | 61.6485 | 122.9552 | 61.4079 | 61.4893 | 123.0392 | 61.4533 | 122.8403 | 61.5575 | 61.5935 | 61.4659 | 61.5018
1160.0625 | 123.262 | -61.4914 | 61.6562 | 0.030283 | -0.031363 | -0.016578 | 0.011611 | 0.027109 | -0.001406 | 0.024268 | 61.5875 | 0.18911 | 61.4821 | -0.042259 | 0.025345 | 61.5753 | -0.006014 | 61.381 | 61.5217 | 61.46 | 61.4748 | 61.503 | 61.5185 | 61.49 | 61.5157 | 123.0789 | 61.6805 | 122.9735 | 61.4491 | 61.5167 | 123.0667 | 61.4854 | 122.8724 | 61.5621 | 61.5935 | 61.4567 | 61.4881
1161.0625 | 123.3582 | -61.4822 | 61.6653 | 0.030283 | -0.040521 | -0.016578 | -0.006703 | 0.036265 | 0.003172 | 0.038003 | 61.592 | 0.18453 | 61.4958 | -0.042259 | 0.025345 | 61.5707 | -0.010593 | 61.3718 | 61.5125 | 61.4417 | 61.4657 | 61.4755 | 61.5185 | 61.4854 | 61.5202 | 123.0743 | 61.6668 | 122.9781 | 61.44 | 61.5076 | 123.053 | 61.4716 | 122.8541 | 61.5667 | 61.6026 | 61.4705 | 61.5064
1162.0625 | 123.381 | -61.4731 | 61.615 | 0.030283 | -0.031363 | -0.016578 | 0.002454 | 0.045421 | 0.003172 | 0.033424 | 61.5829 | 0.18453 | 61.5141 | -0.051417 | 0.025345 | 61.5707 | -0.010593 | 61.3718 | 61.5034 | 61.4417 | 61.4565 | 61.4755 | 61.5185 | 61.4763 | 61.5065 | 123.056 | 61.6576 | 122.9872 | 61.4217 | 61.4984 | 123.0438 | 61.4625 | 122.8449 | 61.5575 | 61.5935 | 61.4888 | 61.5247
1163.0625 | 123.2712 | -61.4685 | 61.6837 | 0.025705 | -0.031363 | -0.012 | 0.007033 | 0.036265 | 0.003172 | 0.028846 | 61.592 | 0.18911 | 61.505 | -0.042259 | 0.025345 | 61.5845 | -0.006014 | 61.3718 | 61.4942 | 61.4371 | 61.4565 | 61.4755 | 61.5048 | 61.4717 | 61.4974 | 123.0605 | 61.6576 | 122.9735 | 61.4262 | 61.4939 | 123.053 | 61.4625 | 122.8403 | 61.5667 | 61.5981 | 61.4796 | 61.511
1164.0625 | 123.2483 | -61.496 | 61.647 | 0.03944 | -0.031363 | -0.016578 | 0.011611 | 0.031687 | -0.001406 | 0.028846 | 61.5829 | 0.18453 | 61.4821 | -0.051417 | 0.025345 | 61.5753 | -0.006014 | 61.3764 | 61.5354 | 61.4646 | 61.4794 | 61.5076 | 61.5277 | 61.4946 | 61.5248 | 123.0789 | 61.6805 | 122.9781 | 61.4446 | 61.5213 | 123.0713 | 61.49 | 122.8724 | 61.5575 | 61.5889 | 61.4567 | 61.4881
1165.0625 | 123.23 | -61.4822 | 61.6562 | 0.025705 | -0.026784 | -0.016578 | 0.011611 | 0.027109 | 0.00775 | 0.028846 | 61.5829 | 0.18453 | 61.5004 | -0.046838 | 0.020767 | 61.5662 | -0.010593 | 61.381 | 61.5079 | 61.4555 | 61.4657 | 61.4939 | 61.5093 | 61.49 | 61.5111 | 123.0651 | 61.6668 | 122.9826 | 61.4354 | 61.503 | 123.0484 | 61.4716 | 122.8632 | 61.5621 | 61.5935 | 61.4796 | 61.511
1166.0625 | 123.2895 | -61.4822 | 61.6333 | 0.030283 | -0.031363 | -0.016578 | -0.002124 | 0.031687 | 0.00775 | 0.028846 | 61.592 | 0.18453 | 61.5279 | -0.046838 | 0.025345 | 61.5753 | -0.006014 | 61.3764 | 61.5125 | 61.4509 | 61.4657 | 61.4801 | 61.5139 | 61.49 | 61.5111 | 123.0743 | 61.6668 | 123.0101 | 61.4354 | 61.5076 | 123.0576 | 61.4762 | 122.8586 | 61.5667 | 61.5981 | 61.5025 | 61.5339
1167.0625 | 123.2574 | -61.4868 | 61.6791 | 0.034862 | -0.035942 | -0.016578 | -0.002124 | 0.027109 | -0.001406 | 0.042581 | 61.5875 | 0.18453 | 61.5141 | -0.051417 | 0.025345 | 61.5707 | -0.006014 | 61.381 | 61.5217 | 61.4509 | 61.4702 | 61.4847 | 61.5139 | 61.4854 | 61.5294 | 123.0743 | 61.6713 | 123.001 | 61.4354 | 61.5122 | 123.0576 | 61.4808 | 122.8678 | 61.5621 | 61.5935 | 61.4888 | 61.5202
1168.0625 | 123.3627 | -61.4639 | 61.647 | 0.025705 | -0.026784 | -0.016578 | 0.007033 | 0.036265 | -0.010563 | 0.028846 | 61.5829 | 0.18453 | 61.4729 | -0.046838 | 0.020767 | 61.5707 | -0.006014 | 61.3764 | 61.4896 | 61.4371 | 61.4474 | 61.471 | 61.5002 | 61.4534 | 61.4928 | 123.0468 | 61.6485 | 122.9369 | 61.4171 | 61.4847 | 123.0347 | 61.4579 | 122.8403 | 61.5621 | 61.5889 | 61.4522 | 61.4789
1169.0625 | 123.3078 | -61.4731 | 61.6699 | 0.030283 | -0.035942 | -0.012 | 0.002454 | 0.040843 | 0.003172 | 0.028846 | 61.5966 | 0.17995 | 61.4821 | -0.046838 | 0.025345 | 61.5753 | -0.006014 | 61.3764 | 61.5034 | 61.4371 | 61.4611 | 61.4755 | 61.5139 | 61.4763 | 61.5019 | 123.0697 | 61.653 | 122.9552 | 61.4262 | 61.4984 | 123.0484 | 61.4671 | 122.8495 | 61.5713 | 61.6026 | 61.4567 | 61.4881
1170.0625 | 123.2758 | -61.4548 | 61.6608 | 0.025705 | -0.031363 | -0.016578 | 0.007033 | 0.027109 | 0.003172 | 0.028846 | 61.5966 | 0.17995 | 61.5141 | -0.051417 | 0.020767 | 61.5753 | -0.001436 | 61.3764 | 61.4805 | 61.4234 | 61.4382 | 61.4618 | 61.4819 | 61.4579 | 61.4836 | 123.0514 | 61.6347 | 122.9689 | 61.4034 | 61.4755 | 123.0301 | 61.4533 | 122.8312 | 61.5759 | 61.5981 | 61.4934 | 61.5156
1171.0625 | 123.2803 | -61.4868 | 61.6562 | 0.030283 | -0.035942 | -0.016578 | 0.002454 | 0.027109 | -0.001406 | 0.033424 | 61.592 | 0.18911 | 61.5233 | -0.046838 | 0.029923 | 61.5845 | 0.003143 | 61.3764 | 61.5171 | 61.4509 | 61.4702 | 61.4893 | 61.5139 | 61.4854 | 61.5202 | 123.0789 | 61.6759 | 123.0101 | 61.44 | 61.5167 | 123.0713 | 61.49 | 122.8632 | 61.5621 | 61.5889 | 61.4934 | 61.5202
1172.0625 | 123.262 | -61.4594 | 61.6837 | 0.025705 | -0.035942 | -0.016578 | 0.002454 | 0.031687 | -0.001406 | 0.033424 | 61.5829 | 0.19369 | 61.4821 | -0.046838 | 0.025345 | 61.5799 | -0.006014 | 61.3718 | 61.4851 | 61.4234 | 61.4428 | 61.4618 | 61.491 | 61.4579 | 61.4928 | 123.0422 | 61.653 | 122.9414 | 61.4125 | 61.4847 | 123.0392 | 61.4533 | 122.8312 | 61.5575 | 61.5889 | 61.4567 | 61.4881
1173.0625 | 123.2803 | -61.4822 | 61.6379 | 0.025705 | -0.026784 | -0.012 | 0.007033 | 0.040843 | 0.003172 | 0.028846 | 61.5829 | 0.18911 | 61.505 | -0.051417 | 0.020767 | 61.5753 | -0.006014 | 61.3856 | 61.5079 | 61.4555 | 61.4702 | 61.4893 | 61.5231 | 61.4854 | 61.5111 | 123.0651 | 61.6713 | 122.9872 | 61.4308 | 61.503 | 123.0576 | 61.4762 | 122.8678 | 61.5621 | 61.5889 | 61.4842 | 61.511
1174.0625 | 123.2849 | -61.4731 | 61.6516 | 0.044018 | -0.031363 | -0.016578 | 0.011611 | 0.031687 | -0.005985 | 0.033424 | 61.592 | 0.18911 | 61.5141 | -0.046838 | 0.025345 | 61.5845 | -0.010593 | 61.3856 | 61.5171 | 61.4417 | 61.4565 | 61.4847 | 61.5048 | 61.4671 | 61.5065 | 123.0651 | 61.6622 | 122.9872 | 61.4262 | 61.4984 | 123.0576 | 61.4625 | 122.8586 | 61.5667 | 61.6026 | 61.4888 | 61.5247
1175.0625 | 123.3948 | -61.4639 | 61.6333 | 0.030283 | -0.040521 | -0.016578 | 0.007033 | 0.031687 | -0.001406 | 0.028846 | 61.5875 | 0.18911 | 61.4729 | -0.046838 | 0.020767 | 61.5799 | -0.001436 | 61.381 | 61.4942 | 61.4234 | 61.4474 | 61.471 | 61.4956 | 61.4625 | 61.4928 | 123.0514 | 61.653 | 122.9369 | 61.4171 | 61.4847 | 123.0438 | 61.4625 | 122.8449 | 61.5667 | 61.5889 | 61.4522 | 61.4744
1176.0625 | 123.3398 | -61.4548 | 61.6425 | 0.030283 | -0.035942 | -0.021157 | -0.002124 | 0.027109 | -0.001406 | 0.033424 | 61.5783 | 0.18453 | 61.4958 | -0.042259 | 0.029923 | 61.5799 | -0.006014 | 61.3718 | 61.4851 | 61.4188 | 61.4336 | 61.4526 | 61.4819 | 61.4534 | 61.4882 | 123.0331 | 61.6393 | 122.9506 | 61.4125 | 61.4847 | 123.0347 | 61.4488 | 122.8266 | 61.5484 | 61.5843 | 61.4659 | 61.5018
1177.0625 | 123.3124 | -61.4822 | 61.6653 | 0.030283 | -0.026784 | -0.016578 | -0.002124 | 0.027109 | -0.005985 | 0.033424 | 61.5966 | 0.17995 | 61.5187 | -0.042259 | 0.025345 | 61.5799 | -0.006014 | 61.3856 | 61.5125 | 61.4555 | 61.4657 | 61.4801 | 61.5093 | 61.4763 | 61.5157 | 123.0789 | 61.6622 | 123.001 | 61.44 | 61.5076 | 123.0621 | 61.4762 | 122.8678 | 61.5713 | 61.6026 | 61.4934 | 61.5247
1178.0625 | 123.349 | -61.4594 | 61.6516 | 0.025705 | -0.040521 | -0.016578 | 0.007033 | 0.036265 | -0.005985 | 0.028846 | 61.5875 | 0.18911 | 61.4821 | -0.042259 | 0.025345 | 61.5799 | 0.003143 | 61.3764 | 61.4851 | 61.4188 | 61.4428 | 61.4664 | 61.4956 | 61.4534 | 61.4882 | 123.0468 | 61.6485 | 122.9414 | 61.4171 | 61.4847 | 123.0392 | 61.4625 | 122.8357 | 61.5621 | 61.5843 | 61.4567 | 61.4789
1179.0625 | 123.2803 | -61.4777 | 61.6562 | 0.030283 | -0.031363 | -0.007421 | 0.007033 | 0.031687 | -0.001406 | 0.024268 | 61.592 | 0.18911 | 61.4775 | -0.046838 | 0.020767 | 61.5799 | -0.010593 | 61.3718 | 61.5079 | 61.4463 | 61.4702 | 61.4847 | 61.5093 | 61.4763 | 61.5019 | 123.0697 | 61.6668 | 122.9552 | 61.4308 | 61.4984 | 123.0576 | 61.4671 | 122.8495 | 61.5713 | 61.6026 | 61.4567 | 61.4881
1180.0625 | 123.4131 | -61.4594 | 61.6058 | 0.034862 | -0.031363 | -0.007421 | 0.002454 | 0.036265 | -0.005985 | 0.024268 | 61.6012 | 0.18911 | 61.4821 | -0.046838 | 0.029923 | 61.5799 | -0.001436 | 61.3764 | 61.4942 | 61.428 | 61.4519 | 61.4618 | 61.4956 | 61.4534 | 61.4836 | 123.0606 | 61.6485 | 122.9414 | 61.4125 | 61.4893 | 123.0392 | 61.4579 | 122.8357 | 61.5713 | 61.6026 | 61.4522 | 61.4835
1181.0625 | 123.3765 | -61.4502 | 61.6196 | 0.030283 | -0.035942 | -0.012 | 0.007033 | 0.036265 | 0.003172 | 0.038003 | 61.592 | 0.18911 | 61.5233 | -0.046838 | 0.025345 | 61.5799 | -0.010593 | 61.381 | 61.4805 | 61.4143 | 61.4382 | 61.4572 | 61.4865 | 61.4534 | 61.4882 | 123.0422 | 61.6393 | 122.9735 | 61.4034 | 61.4755 | 123.0301 | 61.4396 | 122.8312 | 61.5667 | 61.6026 | 61.4979 | 61.5339
1182.0625 | 123.4177 | -61.441 | 61.6196 | 0.030283 | -0.040521 | -0.012 | -0.002124 | 0.031687 | -0.005985 | 0.024268 | 61.6012 | 0.17995 | 61.5279 | -0.046838 | 0.034501 | 61.5845 | -0.001436 | 61.3764 | 61.4713 | 61.4005 | 61.429 | 61.4389 | 61.4727 | 61.4351 | 61.4653 | 123.0422 | 61.621 | 122.9689 | 61.3942 | 61.4755 | 123.0255 | 61.4396 | 122.8174 | 61.5667 | 61.6026 | 61.4934 | 61.5293
1183.0625 | 123.3673 | -61.4639 | 61.6104 | 0.030283 | -0.035942 | -0.016578 | 0.007033 | 0.031687 | -0.001406 | 0.01969 | 61.5875 | 0.18453 | 61.4775 | -0.051417 | 0.020767 | 61.5707 | -0.010593 | 61.3718 | 61.4942 | 61.428 | 61.4474 | 61.471 | 61.4956 | 61.4625 | 61.4836 | 123.0514 | 61.6485 | 122.9414 | 61.4125 | 61.4847 | 123.0347 | 61.4533 | 122.8357 | 61.5667 | 61.5981 | 61.4567 | 61.4881
1184.0625 | 123.2803 | -61.5005 | 61.6562 | 0.030283 | -0.040521 | -0.012 | 0.007033 | 0.027109 | -0.001406 | 0.01969 | 61.5875 | 0.17995 | 61.4821 | -0.046838 | 0.020767 | 61.5799 | 0.003143 | 61.3764 | 61.5308 | 61.46 | 61.4885 | 61.5076 | 61.5277 | 61.4991 | 61.5202 | 123.088 | 61.6805 | 122.9826 | 61.4537 | 61.5213 | 123.0804 | 61.5037 | 122.8769 | 61.5667 | 61.5843 | 61.4613 | 61.4789
1185.0625 | 123.3719 | -61.4548 | 61.615 | 0.030283 | -0.040521 | -0.016578 | 0.002454 | 0.027109 | 0.003172 | 0.024268 | 61.592 | 0.18453 | 61.5187 | -0.042259 | 0.029923 | 61.5662 | 0.003143 | 61.3718 | 61.4851 | 61.4143 | 61.4382 | 61.4572 | 61.4819 | 61.4579 | 61.479 | 123.0468 | 61.6393 | 122.9735 | 61.4125 | 61.4847 | 123.0209 | 61.4579 | 122.8266 | 61.5621 | 61.5889 | 61.4888 | 61.5156
1186.0625 | 123.3719 | -61.4548 | 61.615 | 0.025705 | -0.031363 | -0.007421 | 0.007033 | 0.022531 | -0.005985 | 0.024268 | 61.592 | 0.18911 | 61.5233 | -0.055996 | 0.029923 | 61.5799 | 0.003143 | 61.3764 | 61.4805 | 61.4234 | 61.4474 | 61.4618 | 61.4773 | 61.4488 | 61.479 | 123.0468 | 61.6439 | 122.9781 | 61.3988 | 61.4847 | 123.0347 | 61.4579 | 122.8312 | 61.5621 | 61.5889 | 61.4934 | 61.5202
1187.0625 | 123.3444 | -61.4594 | 61.6287 | 0.030283 | -0.035942 | -0.016578 | 0.002454 | 0.027109 | 0.003172 | 0.024268 | 61.5875 | 0.18911 | 61.4775 | -0.046838 | 0.034501 | 61.5753 | 0.007721 | 61.3764 | 61.4896 | 61.4234 | 61.4428 | 61.4618 | 61.4865 | 61.4625 | 61.4836 | 123.0468 | 61.6485 | 122.9369 | 61.4125 | 61.4939 | 123.0347 | 61.4671 | 122.8357 | 61.553 | 61.5797 | 61.443 | 61.4698
1188.0625 | 123.3398 | -61.4639 | 61.615 | 0.030283 | -0.040521 | -0.007421 | 0.007033 | 0.036265 | -0.010563 | 0.028846 | 61.592 | 0.17995 | 61.4958 | -0.042259 | 0.029923 | 61.5799 | -0.006014 | 61.3764 | 61.4942 | 61.4234 | 61.4565 | 61.471 | 61.5002 | 61.4534 | 61.4928 | 123.056 | 61.6439 | 122.9598 | 61.4217 | 61.4939 | 123.0438 | 61.4579 | 122.8403 | 61.5621 | 61.5981 | 61.4659 | 61.5018
1189.0625 | 123.3582 | -61.4731 | 61.5829 | 0.034862 | -0.031363 | -0.016578 | 0.011611 | 0.027109 | -0.001406 | 0.028846 | 61.592 | 0.18911 | 61.5233 | -0.055996 | 0.029923 | 61.5799 | -0.006014 | 61.3718 | 61.5079 | 61.4417 | 61.4565 | 61.4847 | 61.5002 | 61.4717 | 61.5019 | 123.0651 | 61.6622 | 122.9964 | 61.4171 | 61.503 | 123.053 | 61.4671 | 122.8449 | 61.5621 | 61.5981 | 61.4934 | 61.5293
1190.0625 | 123.3444 | -61.4868 | 61.5967 | 0.030283 | -0.031363 | -0.016578 | 0.002454 | 0.027109 | 0.003172 | 0.033424 | 61.5829 | 0.18453 | 61.4775 | -0.046838 | 0.020767 | 61.5753 | -0.006014 | 61.3718 | 61.5171 | 61.4555 | 61.4702 | 61.4893 | 61.5139 | 61.49 | 61.5202 | 123.0697 | 61.6713 | 122.9643 | 61.44 | 61.5076 | 123.0621 | 61.4808 | 122.8586 | 61.5621 | 61.5889 | 61.4567 | 61.4835
1191.0625 | 123.3719 | -61.4777 | 61.5921 | 0.030283 | -0.031363 | -0.016578 | 0.011611 | 0.027109 | -0.001406 | 0.033424 | 61.5875 | 0.17995 | 61.4867 | -0.042259 | 0.025345 | 61.5799 | -0.010593 | 61.3718 | 61.5079 | 61.4463 | 61.4611 | 61.4893 | 61.5048 | 61.4763 | 61.5111 | 123.0651 | 61.6576 | 122.9643 | 61.4354 | 61.503 | 123.0576 | 61.4671 | 122.8495 | 61.5621 | 61.5981 | 61.4613 | 61.4973
1192.0625 | 123.3353 | -61.5005 | 61.6013 | 0.030283 | -0.040521 | -0.012 | 0.002454 | 0.017953 | -0.005985 | 0.028846 | 61.5966 | 0.18453 | 61.5279 | -0.046838 | 0.020767 | 61.5753 | -0.019749 | 61.3718 | 61.5308 | 61.46 | 61.4885 | 61.503 | 61.5185 | 61.4946 | 61.5294 | 123.0972 | 61.6851 | 123.0284 | 61.4537 | 61.5213 | 123.0759 | 61.4808 | 122.8724 | 61.5759 | 61.6164 | 61.5071 | 61.5476
1193.0625 | 123.3582 | -61.4731 | 61.5921 | 0.025705 | -0.031363 | -0.007421 | 0.002454 | 0.036265 | -0.001406 | 0.01969 | 61.5875 | 0.18911 | 61.4912 | -0.051417 | 0.020767 | 61.5753 | -0.006014 | 61.3718 | 61.4988 | 61.4417 | 61.4657 | 61.4755 | 61.5093 | 61.4717 | 61.4928 | 123.0605 | 61.6622 | 122.9643 | 61.4217 | 61.4939 | 123.0484 | 61.4671 | 122.8449 | 61.5667 | 61.5935 | 61.4705 | 61.4973
1194.0625 | 123.4039 | -61.4639 | 61.6241 | 0.034862 | -0.040521 | -0.021157 | 0.002454 | 0.027109 | 0.003172 | 0.033424 | 61.5829 | 0.18911 | 61.4729 | -0.046838 | 0.020767 | 61.5799 | -0.006014 | 61.3672 | 61.4988 | 61.4234 | 61.4428 | 61.4664 | 61.491 | 61.4671 | 61.4974 | 123.0468 | 61.653 | 122.9369 | 61.4171 | 61.4847 | 123.0438 | 61.4579 | 122.8312 | 61.5621 | 61.5889 | 61.4522 | 61.4789
1195.0625 | 123.3627 | -61.4731 | 61.6058 | 0.034862 | -0.040521 | -0.016578 | 0.011611 | 0.027109 | -0.001406 | 0.033424 | 61.5875 | 0.18911 | 61.4958 | -0.046838 | 0.020767 | 61.5845 | -0.010593 | 61.3672 | 61.5079 | 61.4326 | 61.4565 | 61.4847 | 61.5002 | 61.4717 | 61.5065 | 123.0605 | 61.6622 | 122.9689 | 61.4262 | 61.4939 | 123.0576 | 61.4625 | 122.8403 | 61.5667 | 61.5981 | 61.4751 | 61.5064
1196.0625 | 123.2849 | -61.4639 | 61.6837 | 0.034862 | -0.035942 | -0.021157 | 0.002454 | 0.031687 | 0.00775 | 0.033424 | 61.592 | 0.18453 | 61.5233 | -0.051417 | 0.025345 | 61.5753 | -0.006014 | 61.3718 | 61.4988 | 61.428 | 61.4428 | 61.4664 | 61.4956 | 61.4717 | 61.4974 | 123.056 | 61.6485 | 122.9872 | 61.4125 | 61.4893 | 123.0392 | 61.4579 | 122.8357 | 61.5667 | 61.5981 | 61.4979 | 61.5293
1197.0625 | 123.3261 | -61.4822 | 61.615 | 0.030283 | -0.031363 | -0.016578 | 0.002454 | 0.027109 | -0.001406 | 0.033424 | 61.592 | 0.19369 | 61.5096 | -0.042259 | 0.020767 | 61.5753 | -0.006014 | 61.3718 | 61.5125 | 61.4509 | 61.4657 | 61.4847 | 61.5093 | 61.4808 | 61.5157 | 123.0743 | 61.6759 | 122.9918 | 61.44 | 61.503 | 123.0576 | 61.4762 | 122.8541 | 61.5713 | 61.5981 | 61.4888 | 61.5156
1198.0625 | 123.3902 | -61.4777 | 61.5875 | 0.03944 | -0.031363 | -0.012 | 0.002454 | 0.036265 | -0.005985 | 0.033424 | 61.5875 | 0.18911 | 61.4729 | -0.046838 | 0.025345 | 61.5799 | -0.010593 | 61.3718 | 61.5171 | 61.4463 | 61.4657 | 61.4801 | 61.5139 | 61.4717 | 61.5111 | 123.0651 | 61.6668 | 122.9506 | 61.4308 | 61.503 | 123.0576 | 61.4671 | 122.8495 | 61.5621 | 61.5981 | 61.4476 | 61.4835
1199.0625 | 123.4222 | -61.4822 | 61.5967 | 0.034862 | -0.035942 | -0.016578 | 0.002454 | 0.036265 | -0.001406 | 0.028846 | 61.5783 | 0.18453 | 61.4821 | -0.046838 | 0.020767 | 61.5753 | -0.006014 | 61.3672 | 61.5171 | 61.4463 | 61.4657 | 61.4847 | 61.5185 | 61.4808 | 61.5111 | 123.0605 | 61.6668 | 122.9643 | 61.4354 | 61.503 | 123.0576 | 61.4762 | 122.8495 | 61.5575 | 61.5843 | 61.4613 | 61.4881
1200.0625 | 123.3902 | -61.4777 | 61.5829 | 0.034862 | -0.026784 | -0.012 | 0.002454 | 0.027109 | 0.003172 | 0.038003 | 61.592 | 0.18453 | 61.537 | -0.046838 | 0.025345 | 61.5753 | -0.010593 | 61.3718 | 61.5125 | 61.4509 | 61.4657 | 61.4801 | 61.5048 | 61.4808 | 61.5157 | 123.0697 | 61.6622 | 123.0147 | 61.4308 | 61.503 | 123.053 | 61.4671 | 122.8495 | 61.5667 | 61.6026 | 61.5117 | 61.5476
1201.0625 | 123.2895 | -61.4868 | 61.6333 | 0.034862 | -0.031363 | -0.021157 | 0.007033 | 0.031687 | 0.003172 | 0.033424 | 61.5966 | 0.18911 | 61.5187 | -0.055996 | 0.020767 | 61.5799 | -0.010593 | 61.381 | 61.5217 | 61.4555 | 61.4657 | 61.4938 | 61.5185 | 61.49 | 61.5202 | 123.0834 | 61.6759 | 123.0055 | 61.4308 | 61.5076 | 123.0667 | 61.4762 | 122.8678 | 61.5759 | 61.6072 | 61.4979 | 61.5293
1202.0625 | 123.3215 | -61.496 | 61.6608 | 0.030283 | -0.031363 | -0.007421 | 0.002454 | 0.036265 | 0.003172 | 0.024268 | 61.592 | 0.18453 | 61.4867 | -0.046838 | 0.025345 | 61.5753 | -0.006014 | 61.3718 | 61.5263 | 61.4646 | 61.4886 | 61.4984 | 61.5322 | 61.4991 | 61.5202 | 123.088 | 61.6805 | 122.9826 | 61.4491 | 61.5213 | 123.0713 | 61.49 | 122.8678 | 61.5667 | 61.5981 | 61.4613 | 61.4927
1203.0625 | 123.2437 | -61.5005 | 61.6287 | 0.025705 | -0.031363 | -0.016578 | -0.002124 | 0.031687 | 0.00775 | 0.033424 | 61.5783 | 0.18911 | 61.4775 | -0.055996 | 0.020767 | 61.5799 | -0.010593 | 61.381 | 61.5263 | 61.4692 | 61.484 | 61.4984 | 61.5322 | 61.5083 | 61.534 | 123.0789 | 61.6897 | 122.9781 | 61.4446 | 61.5213 | 123.0804 | 61.49 | 122.8815 | 61.5575 | 61.5889 | 61.4567 | 61.4881
1204.0625 | 123.3536 | -61.4685 | 61.6058 | 0.03944 | -0.031363 | -0.016578 | 0.002454 | 0.040843 | -0.005985 | 0.028846 | 61.5829 | 0.18453 | 61.505 | -0.03768 | 0.025345 | 61.5799 | -0.006014 | 61.3718 | 61.5079 | 61.4371 | 61.4519 | 61.471 | 61.5093 | 61.4625 | 61.4974 | 123.0514 | 61.653 | 122.9735 | 61.4308 | 61.4939 | 123.0484 | 61.4625 | 122.8403 | 61.5575 | 61.5889 | 61.4796 | 61.511
1205.0625 | 123.381 | -61.4685 | 61.5738 | 0.034862 | -0.031363 | -0.012 | 0.002454 | 0.040843 | -0.001406 | 0.024268 | 61.592 | 0.18453 | 61.5233 | -0.046838 | 0.020767 | 61.5845 | -0.001436 | 61.3718 | 61.5034 | 61.4371 | 61.4565 | 61.471 | 61.5093 | 61.4671 | 61.4928 | 123.0605 | 61.653 | 122.9918 | 61.4217 | 61.4893 | 123.053 | 61.4671 | 122.8403 | 61.5713 | 61.5935 | 61.5025 | 61.5247
1206.0625 | 123.2712 | -61.4731 | 61.6699 | 0.025705 | -0.035942 | -0.016578 | 0.002454 | 0.031687 | -0.001406 | 0.033424 | 61.592 | 0.18453 | 61.4867 | -0.051417 | 0.039079 | 61.5799 | -0.006014 | 61.3718 | 61.4988 | 61.4371 | 61.4565 | 61.4755 | 61.5048 | 61.4717 | 61.5065 | 123.0651 | 61.6576 | 122.9597 | 61.4217 | 61.5122 | 123.053 | 61.4671 | 122.8449 | 61.553 | 61.5981 | 61.4476 | 61.4927
1207.0625 | 123.3124 | -61.4914 | 61.6196 | 0.034862 | -0.031363 | -0.012 | 0.011611 | 0.036265 | -0.005985 | 0.028846 | 61.5829 | 0.19369 | 61.4684 | -0.046838 | 0.025345 | 61.5753 | -0.001436 | 61.3718 | 61.5263 | 61.46 | 61.4794 | 61.503 | 61.5277 | 61.4854 | 61.5202 | 123.0743 | 61.6851 | 122.9597 | 61.4446 | 61.5167 | 123.0667 | 61.49 | 122.8632 | 61.5575 | 61.5843 | 61.443 | 61.4698
1208.0625 | 123.3719 | -61.4731 | 61.615 | 0.034862 | -0.031363 | -0.007421 | 0.002454 | 0.027109 | 0.003172 | 0.033424 | 61.5783 | 0.18453 | 61.5187 | -0.046838 | 0.020767 | 61.5799 | -0.006014 | 61.3764 | 61.5079 | 61.4417 | 61.4657 | 61.4755 | 61.5002 | 61.4763 | 61.5065 | 123.0514 | 61.6576 | 122.9918 | 61.4262 | 61.4939 | 123.053 | 61.4671 | 122.8495 | 61.5575 | 61.5843 | 61.4979 | 61.5247
1209.0625 | 123.3673 | -61.4731 | 61.6013 | 0.034862 | -0.031363 | -0.016578 | 0.007033 | 0.036265 | 0.003172 | 0.038003 | 61.5829 | 0.19369 | 61.5279 | -0.055996 | 0.025345 | 61.5753 | -0.006014 | 61.3764 | 61.5079 | 61.4417 | 61.4565 | 61.4801 | 61.5093 | 61.4763 | 61.5111 | 123.056 | 61.6668 | 123.001 | 61.4171 | 61.4984 | 123.0484 | 61.4671 | 122.8495 | 61.5575 | 61.5889 | 61.5025 | 61.5339
1210.0625 | 123.3078 | -61.4868 | 61.6104 | 0.034862 | -0.031363 | -0.021157 | 0.011611 | 0.040843 | 0.00775 | 0.033424 | 61.5875 | 0.18453 | 61.4912 | -0.046838 | 0.016188 | 61.5753 | -0.010593 | 61.3718 | 61.5217 | 61.4555 | 61.4657 | 61.4984 | 61.5277 | 61.4946 | 61.5202 | 123.0743 | 61.6713 | 122.9781 | 61.44 | 61.503 | 123.0621 | 61.4762 | 122.8586 | 61.5713 | 61.5981 | 61.4751 | 61.5018
1211.0625 | 123.262 | -61.4868 | 61.6608 | 0.025705 | -0.031363 | -0.016578 | 0.011611 | 0.040843 | 0.003172 | 0.024268 | 61.5966 | 0.18453 | 61.4821 | -0.051417 | 0.020767 | 61.5753 | -0.006014 | 61.3764 | 61.5125 | 61.4555 | 61.4702 | 61.4984 | 61.5277 | 61.49 | 61.5111 | 123.0834 | 61.6713 | 122.9689 | 61.4354 | 61.5076 | 123.0621 | 61.4808 | 122.8632 | 61.5759 | 61.6026 | 61.4613 | 61.4881
1212.0625 | 123.3444 | -61.496 | 61.6013 | 0.025705 | -0.031363 | -0.016578 | 0.002454 | 0.031687 | 0.003172 | 0.01969 | 61.5875 | 0.19369 | 61.4958 | -0.046838 | 0.025345 | 61.5799 | -0.015171 | 61.3718 | 61.5217 | 61.4646 | 61.4794 | 61.4984 | 61.5277 | 61.4991 | 61.5157 | 123.0834 | 61.6897 | 122.9918 | 61.4491 | 61.5213 | 123.0759 | 61.4808 | 122.8678 | 61.5621 | 61.6026 | 61.4705 | 61.511
1213.0625 | 123.3673 | -61.4639 | 61.5738 | 0.030283 | -0.035942 | -0.016578 | 0.011611 | 0.027109 | 0.003172 | 0.028846 | 61.5875 | 0.18911 | 61.5187 | -0.051417 | 0.025345 | 61.5799 | -0.006014 | 61.3672 | 61.4942 | 61.428 | 61.4474 | 61.4755 | 61.491 | 61.4671 | 61.4928 | 123.0514 | 61.653 | 122.9826 | 61.4125 | 61.4893 | 123.0438 | 61.4579 | 122.8312 | 61.5621 | 61.5935 | 61.4934 | 61.5247
1214.0625 | 123.349 | -61.4868 | 61.5738 | 0.025705 | -0.031363 | -0.012 | 0.002454 | 0.031687 | -0.005985 | 0.024268 | 61.5829 | 0.19369 | 61.4912 | -0.055996 | 0.020767 | 61.5753 | -0.015171 | 61.3718 | 61.5125 | 61.4555 | 61.4748 | 61.4893 | 61.5185 | 61.4808 | 61.5111 | 123.0697 | 61.6805 | 122.9781 | 61.4308 | 61.5076 | 123.0621 | 61.4716 | 122.8586 | 61.5621 | 61.5981 | 61.4705 | 61.5064
1215.0625 | 123.3627 | -61.4639 | 61.5875 | 0.025705 | -0.035942 | -0.016578 | 0.002454 | 0.036265 | -0.001406 | 0.038003 | 61.5875 | 0.18453 | 61.4912 | -0.051417 | 0.020767 | 61.5799 | -0.006014 | 61.3718 | 61.4896 | 61.428 | 61.4474 | 61.4664 | 61.5002 | 61.4625 | 61.5019 | 123.0514 | 61.6485 | 122.9552 | 61.4125 | 61.4847 | 123.0438 | 61.4579 | 122.8357 | 61.5667 | 61.5935 | 61.4705 | 61.4973
1216.0781 | 123.4085 | -61.4548 | 61.6241 | 0.025705 | -0.040521 | -0.007421 | 0.007033 | 0.031687 | -0.005985 | 0.028846 | 61.5966 | 0.17995 | 61.5004 | -0.055996 | 0.025345 | 61.5799 | -0.006014 | 61.3764 | 61.4805 | 61.4143 | 61.4474 | 61.4618 | 61.4865 | 61.4488 | 61.4836 | 123.0514 | 61.6347 | 122.9552 | 61.3988 | 61.4801 | 123.0347 | 61.4488 | 122.8312 | 61.5713 | 61.6026 | 61.4751 | 61.5064
1217.0625 | 123.3124 | -61.5051 | 61.6287 | 0.025705 | -0.026784 | -0.016578 | 0.002454 | 0.031687 | -0.001406 | 0.033424 | 61.592 | 0.18911 | 61.5279 | -0.046838 | 0.016188 | 61.5753 | -0.010593 | 61.3627 | 61.5308 | 61.4783 | 61.4885 | 61.5076 | 61.5368 | 61.5037 | 61.5386 | 123.0972 | 61.6942 | 123.033 | 61.4583 | 61.5213 | 123.0804 | 61.4945 | 122.8678 | 61.5759 | 61.6026 | 61.5117 | 61.5385
1218.0625 | 123.349 | -61.4365 | 61.5967 | 0.030283 | -0.035942 | -0.016578 | 0.007033 | 0.040843 | 0.003172 | 0.033424 | 61.5875 | 0.18453 | 61.505 | -0.055996 | 0.016188 | 61.5753 | -0.015171 | 61.3672 | 61.4667 | 61.4005 | 61.4199 | 61.4435 | 61.4773 | 61.4396 | 61.4699 | 123.0239 | 61.621 | 122.9414 | 61.3805 | 61.4526 | 123.0118 | 61.4213 | 122.8037 | 61.5713 | 61.6026 | 61.4888 | 61.5202
1219.0625 | 123.3627 | -61.4502 | 61.6333 | 0.034862 | -0.026784 | -0.016578 | 0.011611 | 0.027109 | -0.001406 | 0.028846 | 61.592 | 0.19369 | 61.4867 | -0.046838 | 0.020767 | 61.5753 | -0.006014 | 61.3627 | 61.4851 | 61.4234 | 61.4336 | 61.4618 | 61.4773 | 61.4488 | 61.479 | 123.0422 | 61.6439 | 122.9369 | 61.4034 | 61.471 | 123.0255 | 61.4442 | 122.8129 | 61.5713 | 61.5981 | 61.4659 | 61.4927
1220.0625 | 123.3673 | -61.4777 | 61.6013 | 0.034862 | -0.035942 | -0.012 | 0.002454 | 0.027109 | 0.003172 | 0.033424 | 61.5875 | 0.18911 | 61.4775 | -0.046838 | 0.016188 | 61.5707 | -0.006014 | 61.3718 | 61.5125 | 61.4417 | 61.4657 | 61.4801 | 61.5048 | 61.4808 | 61.5111 | 123.0651 | 61.6668 | 122.9552 | 61.4308 | 61.4938 | 123.0484 | 61.4716 | 122.8495 | 61.5713 | 61.5935 | 61.4613 | 61.4835
1221.0625 | 123.3902 | -61.4731 | 61.5875 | 0.030283 | -0.035942 | -0.012 | 0.007033 | 0.027109 | 0.003172 | 0.028846 | 61.592 | 0.18453 | 61.5187 | -0.046838 | 0.025345 | 61.5707 | -0.006014 | 61.381 | 61.5034 | 61.4371 | 61.4611 | 61.4801 | 61.5002 | 61.4763 | 61.5019 | 123.0651 | 61.6576 | 122.9918 | 61.4262 | 61.4984 | 123.0438 | 61.4671 | 122.8541 | 61.5667 | 61.5981 | 61.4934 | 61.5247
1222.0625 | 123.3994 | -61.4639 | 61.6104 | 0.021127 | -0.035942 | -0.016578 | -0.002124 | 0.036265 | 0.003172 | 0.033424 | 61.5966 | 0.18911 | 61.5324 | -0.046838 | 0.020767 | 61.5799 | -0.015171 | 61.3672 | 61.4851 | 61.428 | 61.4474 | 61.4618 | 61.5002 | 61.4671 | 61.4974 | 123.0605 | 61.653 | 122.9964 | 61.4171 | 61.4847 | 123.0438 | 61.4488 | 122.8312 | 61.5759 | 61.6118 | 61.5117 | 61.5476
1223.0625 | 123.2803 | -61.4868 | 61.6196 | 0.034862 | -0.031363 | -0.012 | 0.002454 | 0.031687 | 0.00775 | 0.033424 | 61.592 | 0.18911 | 61.4821 | -0.046838 | 0.016188 | 61.5707 | -0.006014 | 61.3764 | 61.5217 | 61.4555 | 61.4748 | 61.4893 | 61.5185 | 61.4946 | 61.5202 | 123.0789 | 61.6759 | 122.9689 | 61.44 | 61.503 | 123.0576 | 61.4808 | 122.8632 | 61.5759 | 61.5981 | 61.4659 | 61.4881
1224.0625 | 123.317 | -61.4639 | 61.5875 | 0.03944 | -0.040521 | -0.016578 | 0.002454 | 0.036265 | -0.005985 | 0.028846 | 61.592 | 0.19369 | 61.4684 | -0.042259 | 0.025345 | 61.5799 | -0.001436 | 61.3718 | 61.5034 | 61.4234 | 61.4474 | 61.4664 | 61.5002 | 61.4579 | 61.4928 | 123.056 | 61.6576 | 122.9323 | 61.4217 | 61.4893 | 123.0438 | 61.4625 | 122.8357 | 61.5667 | 61.5935 | 61.443 | 61.4698
1225.0625 | 123.3719 | -61.4639 | 61.5921 | 0.030283 | -0.035942 | -0.016578 | 0.002454 | 0.031687 | 0.00775 | 0.028846 | 61.5875 | 0.18911 | 61.4867 | -0.051417 | 0.020767 | 61.5707 | -0.006014 | 61.3672 | 61.4942 | 61.428 | 61.4474 | 61.4664 | 61.4956 | 61.4717 | 61.4928 | 123.0514 | 61.653 | 122.9506 | 61.4125 | 61.4847 | 123.0347 | 61.4579 | 122.8312 | 61.5667 | 61.5935 | 61.4659 | 61.4927
1226.0625 | 123.4085 | -61.4639 | 61.5738 | 0.034862 | -0.031363 | -0.016578 | 0.007033 | 0.031687 | -0.001406 | 0.033424 | 61.5875 | 0.18911 | 61.5004 | -0.046838 | 0.025345 | 61.5799 | -0.010593 | 61.3627 | 61.4988 | 61.4326 | 61.4474 | 61.471 | 61.4956 | 61.4625 | 61.4974 | 123.0514 | 61.653 | 122.9643 | 61.4171 | 61.4893 | 123.0438 | 61.4533 | 122.8266 | 61.5621 | 61.5981 | 61.4751 | 61.511
1227.0625 | 123.3673 | -61.4731 | 61.5875 | 0.034862 | -0.035942 | -0.012 | 0.002454 | 0.036265 | 0.003172 | 0.038003 | 61.5966 | 0.17995 | 61.5279 | -0.046838 | 0.016188 | 61.5799 | -0.006014 | 61.3672 | 61.5079 | 61.4371 | 61.4611 | 61.4755 | 61.5093 | 61.4763 | 61.5111 | 123.0697 | 61.653 | 123.001 | 61.4262 | 61.4893 | 123.053 | 61.4671 | 122.8403 | 61.5804 | 61.6026 | 61.5117 | 61.5339
1228.0625 | 123.4131 | -61.4685 | 61.5784 | 0.030283 | -0.035942 | -0.016578 | 0.007033 | 0.027109 | -0.001406 | 0.033424 | 61.592 | 0.18911 | 61.5187 | -0.051417 | 0.029923 | 61.5753 | -0.010593 | 61.3764 | 61.4988 | 61.4326 | 61.4519 | 61.4755 | 61.4956 | 61.4671 | 61.5019 | 123.0605 | 61.6576 | 122.9872 | 61.4171 | 61.4984 | 123.0438 | 61.4579 | 122.8449 | 61.5621 | 61.6026 | 61.4888 | 61.5293
1229.0625 | 123.3719 | -61.4685 | 61.6287 | 0.034862 | -0.035942 | -0.016578 | -0.002124 | 0.031687 | 0.003172 | 0.033424 | 61.5875 | 0.19369 | 61.4958 | -0.046838 | 0.020767 | 61.5753 | -0.010593 | 61.3718 | 61.5034 | 61.4326 | 61.4519 | 61.4664 | 61.5002 | 61.4717 | 61.5019 | 123.056 | 61.6622 | 122.9643 | 61.4217 | 61.4893 | 123.0438 | 61.4579 | 122.8403 | 61.5667 | 61.5981 | 61.4751 | 61.5064
1230.0625 | 123.2712 | -61.4639 | 61.6013 | 0.030283 | -0.026784 | -0.012 | 0.002454 | 0.027109 | -0.005985 | 0.024268 | 61.592 | 0.18911 | 61.4775 | -0.051417 | 0.020767 | 61.5799 | -0.010593 | 61.3627 | 61.4942 | 61.4371 | 61.4519 | 61.4664 | 61.491 | 61.4579 | 61.4882 | 123.056 | 61.653 | 122.9414 | 61.4125 | 61.4847 | 123.0438 | 61.4533 | 122.8266 | 61.5713 | 61.6026 | 61.4567 | 61.4881
1231.0625 | 123.317 | -61.4914 | 61.6379 | 0.034862 | -0.040521 | -0.021157 | 0.01619 | 0.040843 | -0.001406 | 0.028846 | 61.5966 | 0.19369 | 61.4912 | -0.046838 | 0.025345 | 61.5799 | -0.010593 | 61.3672 | 61.5263 | 61.4509 | 61.4702 | 61.5076 | 61.5322 | 61.49 | 61.5202 | 123.088 | 61.6851 | 122.9826 | 61.4446 | 61.5167 | 123.0713 | 61.4808 | 122.8586 | 61.5713 | 61.6072 | 61.4659 | 61.5018
1232.0625 | 123.3444 | -61.4822 | 61.5967 | 0.03944 | -0.035942 | -0.021157 | 0.002454 | 0.036265 | 0.003172 | 0.033424 | 61.592 | 0.19369 | 61.5141 | -0.051417 | 0.01161 | 61.5753 | -0.006014 | 61.3764 | 61.5217 | 61.4463 | 61.4611 | 61.4847 | 61.5185 | 61.4854 | 61.5157 | 123.0743 | 61.6759 | 122.9964 | 61.4308 | 61.4938 | 123.0576 | 61.4762 | 122.8586 | 61.5804 | 61.5981 | 61.5025 | 61.5202
1233.0625 | 123.3719 | -61.4731 | 61.5921 | 0.030283 | -0.031363 | -0.021157 | 0.007033 | 0.031687 | -0.005985 | 0.038003 | 61.5829 | 0.19827 | 61.4958 | -0.046838 | 0.020767 | 61.5799 | -0.010593 | 61.3718 | 61.5034 | 61.4417 | 61.4519 | 61.4801 | 61.5048 | 61.4671 | 61.5111 | 123.056 | 61.6713 | 122.9689 | 61.4262 | 61.4939 | 123.053 | 61.4625 | 122.8449 | 61.5621 | 61.5935 | 61.4751 | 61.5064
1234.0625 | 123.3444 | -61.4777 | 61.6196 | 0.025705 | -0.031363 | -0.021157 | 0.007033 | 0.027109 | -0.001406 | 0.024268 | 61.5829 | 0.18911 | 61.4729 | -0.051417 | 0.016188 | 61.5845 | -0.001436 | 61.3764 | 61.5034 | 61.4463 | 61.4565 | 61.4847 | 61.5048 | 61.4763 | 61.5019 | 123.0605 | 61.6668 | 122.9506 | 61.4262 | 61.4938 | 123.0621 | 61.4762 | 122.8541 | 61.5667 | 61.5843 | 61.4567 | 61.4744
1235.0625 | 123.3902 | -61.4731 | 61.5921 | 0.034862 | -0.035942 | -0.016578 | 0.007033 | 0.031687 | 0.003172 | 0.033424 | 61.592 | 0.18911 | 61.4912 | -0.042259 | 0.020767 | 61.5753 | -0.006014 | 61.3718 | 61.5079 | 61.4371 | 61.4565 | 61.4801 | 61.5048 | 61.4763 | 61.5065 | 123.0651 | 61.6622 | 122.9643 | 61.4308 | 61.4939 | 123.0484 | 61.4671 | 122.8449 | 61.5713 | 61.5981 | 61.4705 | 61.4973
1236.0625 | 123.3582 | -61.4731 | 61.5875 | 0.025705 | -0.035942 | -0.016578 | 0.007033 | 0.031687 | -0.001406 | 0.033424 | 61.5875 | 0.18453 | 61.5187 | -0.051417 | 0.01161 | 61.5799 | -0.015171 | 61.3718 | 61.4988 | 61.4371 | 61.4565 | 61.4801 | 61.5048 | 61.4717 | 61.5065 | 123.0605 | 61.6576 | 122.9918 | 61.4217 | 61.4847 | 123.053 | 61.4579 | 122.8449 | 61.5759 | 61.6026 | 61.5071 | 61.5339
1237.0625 | 123.262 | -61.5005 | 61.6287 | 0.034862 | -0.026784 | -0.012 | 0.007033 | 0.036265 | -0.001406 | 0.038003 | 61.592 | 0.18911 | 61.5004 | -0.055996 | 0.020767 | 61.5799 | -0.010593 | 61.3672 | 61.5354 | 61.4738 | 61.4885 | 61.5076 | 61.5368 | 61.4991 | 61.5386 | 123.0926 | 61.6897 | 123.0009 | 61.4446 | 61.5213 | 123.0804 | 61.49 | 122.8678 | 61.5713 | 61.6026 | 61.4796 | 61.511
1238.0625 | 123.3215 | -61.5005 | 61.6058 | 0.030283 | -0.026784 | -0.007421 | -0.002124 | 0.027109 | -0.001406 | 0.033424 | 61.592 | 0.18911 | 61.4867 | -0.046838 | 0.025345 | 61.5799 | -0.015171 | 61.3718 | 61.5308 | 61.4738 | 61.4931 | 61.4984 | 61.5277 | 61.4991 | 61.534 | 123.0926 | 61.6897 | 122.9872 | 61.4537 | 61.5259 | 123.0804 | 61.4854 | 122.8724 | 61.5667 | 61.6072 | 61.4613 | 61.5018
1239.0625 | 123.317 | -61.4731 | 61.615 | 0.034862 | -0.031363 | -0.016578 | 0.002454 | 0.040843 | -0.005985 | 0.024268 | 61.5875 | 0.19369 | 61.4821 | -0.051417 | 0.029923 | 61.5753 | -0.001436 | 61.3718 | 61.5079 | 61.4417 | 61.4565 | 61.4755 | 61.5139 | 61.4671 | 61.4974 | 123.0605 | 61.6668 | 122.9552 | 61.4217 | 61.503 | 123.0484 | 61.4716 | 122.8449 | 61.5575 | 61.5889 | 61.4522 | 61.4835
1240.0625 | 123.3444 | -61.4731 | 61.5005 | 0.034862 | -0.026784 | -0.016578 | 0.007033 | 0.031687 | -0.001406 | 0.028846 | 61.5829 | 0.18911 | 61.5279 | -0.042259 | 0.020767 | 61.5799 | -0.010593 | 61.381 | 61.5079 | 61.4463 | 61.4565 | 61.4801 | 61.5048 | 61.4717 | 61.5019 | 123.056 | 61.6622 | 123.001 | 61.4308 | 61.4939 | 123.053 | 61.4625 | 122.8541 | 61.5621 | 61.5935 | 61.5071 | 61.5385
1241.0625 | 123.3994 | -61.4594 | 61.5601 | 0.034862 | -0.031363 | -0.012 | 0.007033 | 0.031687 | 0.003172 | 0.033424 | 61.5829 | 0.19369 | 61.5004 | -0.03768 | 0.016188 | 61.5799 | -0.001436 | 61.3672 | 61.4942 | 61.428 | 61.4474 | 61.4664 | 61.491 | 61.4625 | 61.4928 | 123.0422 | 61.653 | 122.9598 | 61.4217 | 61.4755 | 123.0392 | 61.4579 | 122.8266 | 61.5667 | 61.5843 | 61.4842 | 61.5018
1242.0625 | 123.3948 | -61.4456 | 61.5784 | 0.034862 | -0.031363 | -0.012 | 0.011611 | 0.027109 | 0.003172 | 0.028846 | 61.5829 | 0.19369 | 61.4775 | -0.046838 | 0.020767 | 61.5799 | -0.006014 | 61.3718 | 61.4805 | 61.4143 | 61.4336 | 61.4572 | 61.4727 | 61.4488 | 61.4745 | 123.0285 | 61.6393 | 122.9231 | 61.3988 | 61.4664 | 123.0255 | 61.4396 | 122.8174 | 61.5621 | 61.5889 | 61.4567 | 61.4835
1243.0625 | 123.3627 | -61.4639 | 61.5829 | 0.030283 | -0.035942 | -0.016578 | 0.007033 | 0.027109 | 0.003172 | 0.028846 | 61.5829 | 0.18911 | 61.4912 | -0.046838 | 0.016188 | 61.5799 | -0.001436 | 61.3764 | 61.4942 | 61.428 | 61.4474 | 61.471 | 61.491 | 61.4671 | 61.4928 | 123.0468 | 61.653 | 122.9552 | 61.4171 | 61.4801 | 123.0438 | 61.4625 | 122.8403 | 61.5667 | 61.5843 | 61.4751 | 61.4927
1244.0625 | 123.3994 | -61.4777 | 61.6058 | 0.030283 | -0.035942 | -0.016578 | 0.011611 | 0.031687 | -0.001406 | 0.024268 | 61.592 | 0.18911 | 61.5233 | -0.051417 | 0.016188 | 61.5845 | -0.006014 | 61.3764 | 61.5079 | 61.4417 | 61.4611 | 61.4893 | 61.5093 | 61.4763 | 61.5019 | 123.0697 | 61.6668 | 123.001 | 61.4262 | 61.4938 | 123.0621 | 61.4716 | 122.8541 | 61.5759 | 61.5981 | 61.5071 | 61.5293
1245.0625 | 123.3444 | -61.4777 | 61.6013 | 0.025705 | -0.040521 | -0.016578 | 0.002454 | 0.031687 | 0.003172 | 0.028846 | 61.592 | 0.17995 | 61.5141 | -0.042259 | 0.025345 | 61.5753 | -0.006014 | 61.3672 | 61.5034 | 61.4371 | 61.4611 | 61.4801 | 61.5093 | 61.4808 | 61.5065 | 123.0697 | 61.6576 | 122.9918 | 61.4354 | 61.503 | 123.053 | 61.4716 | 122.8449 | 61.5667 | 61.5981 | 61.4888 | 61.5202
1246.0625 | 123.3994 | -61.4639 | 61.5784 | 0.030283 | -0.031363 | -0.016578 | 0.011611 | 0.031687 | 0.003172 | 0.028846 | 61.5875 | 0.18453 | 61.4729 | -0.051417 | 0.029923 | 61.5799 | -0.001436 | 61.3764 | 61.4942 | 61.4326 | 61.4474 | 61.4755 | 61.4956 | 61.4671 | 61.4928 | 123.0514 | 61.6485 | 122.9369 | 61.4125 | 61.4939 | 123.0438 | 61.4625 | 122.8403 | 61.5575 | 61.5889 | 61.443 | 61.4744
1247.0625 | 123.3902 | -61.4731 | 61.5967 | 0.034862 | -0.026784 | -0.012 | 0.01619 | 0.031687 | -0.005985 | 0.024268 | 61.5829 | 0.18911 | 61.4729 | -0.051417 | 0.020767 | 61.5753 | -0.001436 | 61.3718 | 61.5079 | 61.4463 | 61.4611 | 61.4893 | 61.5048 | 61.4671 | 61.4974 | 123.056 | 61.6622 | 122.946 | 61.4217 | 61.4939 | 123.0484 | 61.4716 | 122.8449 | 61.5621 | 61.5843 | 61.4522 | 61.4744
1248.0625 | 123.3994 | -61.4868 | 61.5784 | 0.030283 | -0.031363 | -0.021157 | 0.007033 | 0.031687 | -0.001406 | 0.033424 | 61.5966 | 0.19369 | 61.5324 | -0.051417 | 0.020767 | 61.5753 | -0.010593 | 61.3718 | 61.5171 | 61.4555 | 61.4657 | 61.4938 | 61.5185 | 61.4854 | 61.5202 | 123.0834 | 61.6805 | 123.0193 | 61.4354 | 61.5076 | 123.0621 | 61.4762 | 122.8586 | 61.5759 | 61.6072 | 61.5117 | 61.543
1249.0625 | 123.4177 | -61.4639 | 61.6287 | 0.034862 | -0.031363 | -0.016578 | 0.007033 | 0.036265 | -0.001406 | 0.024268 | 61.592 | 0.18453 | 61.5096 | -0.046838 | 0.025345 | 61.5845 | 0.012299 | 61.381 | 61.4988 | 61.4326 | 61.4474 | 61.471 | 61.5002 | 61.4625 | 61.4882 | 123.056 | 61.6485 | 122.9735 | 61.4171 | 61.4893 | 123.0484 | 61.4762 | 122.8449 | 61.5667 | 61.5797 | 61.4842 | 61.4973
1250.0625 | 123.3627 | -61.4914 | 61.5601 | 0.030283 | -0.035942 | -0.021157 | 0.01619 | 0.027109 | -0.005985 | 0.033424 | 61.5875 | 0.18911 | 61.4775 | -0.051417 | 0.025345 | 61.5845 | -0.001436 | 61.381 | 61.5217 | 61.4555 | 61.4702 | 61.5076 | 61.5185 | 61.4854 | 61.5248 | 123.0789 | 61.6805 | 122.9689 | 61.44 | 61.5167 | 123.0759 | 61.49 | 122.8724 | 61.5621 | 61.5889 | 61.4522 | 61.4789
1251.0625 | 123.3536 | -61.4731 | 61.6058 | 0.034862 | -0.031363 | -0.025735 | 0.002454 | 0.031687 | 0.003172 | 0.028846 | 61.5875 | 0.19369 | 61.4775 | -0.046838 | 0.025345 | 61.5753 | -0.001436 | 61.3718 | 61.5079 | 61.4417 | 61.4473 | 61.4755 | 61.5048 | 61.4763 | 61.5019 | 123.0605 | 61.6668 | 122.9506 | 61.4262 | 61.4984 | 123.0484 | 61.4716 | 122.8449 | 61.5621 | 61.5889 | 61.4522 | 61.4789
1252.0625 | 123.2758 | -61.4914 | 61.6196 | 0.030283 | -0.031363 | -0.012 | 0.011611 | 0.036265 | 0.003172 | 0.038003 | 61.5875 | 0.18911 | 61.5141 | -0.051417 | 0.029923 | 61.5753 | -0.006014 | 61.381 | 61.5217 | 61.46 | 61.4794 | 61.503 | 61.5277 | 61.4946 | 61.5294 | 123.0789 | 61.6805 | 123.0055 | 61.44 | 61.5213 | 123.0667 | 61.4854 | 122.8724 | 61.5575 | 61.5935 | 61.4842 | 61.5202
1253.0625 | 123.3627 | -61.4502 | 61.5967 | 0.034862 | -0.035942 | -0.030314 | 0.002454 | 0.036265 | 0.003172 | 0.038003 | 61.5875 | 0.19827 | 61.5279 | -0.051417 | 0.025345 | 61.5753 | -0.001436 | 61.381 | 61.4851 | 61.4143 | 61.4199 | 61.4526 | 61.4865 | 61.4534 | 61.4882 | 123.0377 | 61.6485 | 122.9781 | 61.3988 | 61.4755 | 123.0255 | 61.4488 | 122.8312 | 61.5621 | 61.5889 | 61.5025 | 61.5293
1254.0625 | 123.3856 | -61.4731 | 61.5829 | 0.021127 | -0.026784 | -0.012 | 0.01619 | 0.031687 | -0.001406 | 0.024268 | 61.592 | 0.17995 | 61.4775 | -0.055996 | 0.020767 | 61.5753 | 0.003143 | 61.3718 | 61.4942 | 61.4463 | 61.4611 | 61.4893 | 61.5048 | 61.4717 | 61.4974 | 123.0651 | 61.653 | 122.9506 | 61.4171 | 61.4939 | 123.0484 | 61.4762 | 122.8449 | 61.5713 | 61.5889 | 61.4567 | 61.4744
1255.0625 | 123.381 | -61.4685 | 61.5692 | 0.034862 | -0.035942 | -0.021157 | 0.002454 | 0.031687 | 0.003172 | 0.033424 | 61.5875 | 0.17995 | 61.4775 | -0.046838 | 0.020767 | 61.5753 | -0.006014 | 61.3672 | 61.5034 | 61.4326 | 61.4473 | 61.471 | 61.5002 | 61.4717 | 61.5019 | 123.056 | 61.6485 | 122.946 | 61.4217 | 61.4893 | 123.0438 | 61.4625 | 122.8357 | 61.5667 | 61.5935 | 61.4567 | 61.4835
1256.0625 | 123.3719 | -61.4731 | 61.6013 | 0.030283 | -0.035942 | -0.012 | 0.01619 | 0.031687 | -0.005985 | 0.028846 | 61.592 | 0.19827 | 61.4958 | -0.051417 | 0.020767 | 61.5799 | -0.006014 | 61.3764 | 61.5034 | 61.4371 | 61.4611 | 61.4893 | 61.5048 | 61.4671 | 61.5019 | 123.0651 | 61.6713 | 122.9689 | 61.4217 | 61.4939 | 123.053 | 61.4671 | 122.8495 | 61.5713 | 61.5981 | 61.4751 | 61.5018
1257.0625 | 123.3536 | -61.4868 | 61.6104 | 0.034862 | -0.026784 | -0.016578 | 0.007033 | 0.040843 | 0.003172 | 0.028846 | 61.5875 | 0.18911 | 61.5233 | -0.046838 | 0.020767 | 61.5799 | -0.001436 | 61.381 | 61.5217 | 61.46 | 61.4702 | 61.4938 | 61.5277 | 61.49 | 61.5157 | 123.0743 | 61.6759 | 123.0101 | 61.44 | 61.5076 | 123.0667 | 61.4854 | 122.8678 | 61.5667 | 61.5889 | 61.5025 | 61.5247
1258.0625 | 123.2529 | -61.496 | 61.6562 | 0.030283 | -0.031363 | -0.012 | 0.007033 | 0.040843 | -0.005985 | 0.024268 | 61.5875 | 0.18453 | 61.4867 | -0.046838 | 0.016188 | 61.5753 | -0.006014 | 61.3764 | 61.5263 | 61.4646 | 61.484 | 61.503 | 61.5368 | 61.49 | 61.5202 | 123.0834 | 61.6805 | 122.9826 | 61.4491 | 61.5122 | 123.0713 | 61.49 | 122.8724 | 61.5713 | 61.5935 | 61.4705 | 61.4927
1259.0625 | 123.317 | -61.496 | 61.5967 | 0.030283 | -0.026784 | -0.016578 | 0.002454 | 0.031687 | -0.001406 | 0.028846 | 61.5829 | 0.19369 | 61.4775 | -0.046838 | 0.025345 | 61.5753 | -0.006014 | 61.3764 | 61.5263 | 61.4692 | 61.4794 | 61.4984 | 61.5277 | 61.4946 | 61.5248 | 123.0789 | 61.6897 | 122.9735 | 61.4491 | 61.5213 | 123.0713 | 61.49 | 122.8724 | 61.5575 | 61.5889 | 61.4522 | 61.4835
1260.0625 | 123.2666 | -61.4868 | 61.6104 | 0.025705 | -0.035942 | -0.021157 | 0.002454 | 0.031687 | 0.003172 | 0.028846 | 61.5875 | 0.19369 | 61.4958 | -0.042259 | 0.025345 | 61.5799 | -0.015171 | 61.3718 | 61.5125 | 61.4509 | 61.4657 | 61.4893 | 61.5185 | 61.49 | 61.5157 | 123.0743 | 61.6805 | 122.9826 | 61.4446 | 61.5122 | 123.0667 | 61.4716 | 122.8586 | 61.5621 | 61.6026 | 61.4705 | 61.511
1261.0625 | 123.3353 | -61.4685 | 61.6013 | 0.034862 | -0.035942 | -0.007421 | 0.007033 | 0.036265 | 0.00775 | 0.033424 | 61.6012 | 0.18911 | 61.5279 | -0.042259 | 0.020767 | 61.5753 | -0.010593 | 61.3764 | 61.5034 | 61.4326 | 61.4611 | 61.4755 | 61.5048 | 61.4763 | 61.5019 | 123.0697 | 61.6576 | 122.9964 | 61.4262 | 61.4893 | 123.0438 | 61.4579 | 122.8449 | 61.5804 | 61.6118 | 61.5071 | 61.5385
1262.0625 | 123.2941 | -61.4777 | 61.5967 | 0.034862 | -0.031363 | -0.016578 | 0.011611 | 0.036265 | 0.003172 | 0.033424 | 61.592 | 0.17995 | 61.5004 | -0.042259 | 0.020767 | 61.5845 | -0.006014 | 61.381 | 61.5125 | 61.4463 | 61.4611 | 61.4893 | 61.5139 | 61.4808 | 61.5111 | 123.0697 | 61.6576 | 122.9781 | 61.4354 | 61.4984 | 123.0621 | 61.4716 | 122.8586 | 61.5713 | 61.5981 | 61.4796 | 61.5064
1263.0625 | 123.3215 | -61.4822 | 61.6333 | 0.03944 | -0.031363 | -0.016578 | 0.002454 | 0.031687 | -0.001406 | 0.028846 | 61.5875 | 0.19369 | 61.4821 | -0.051417 | 0.025345 | 61.5799 | -0.006014 | 61.3672 | 61.5217 | 61.4509 | 61.4657 | 61.4847 | 61.5139 | 61.4808 | 61.5111 | 123.0697 | 61.6759 | 122.9643 | 61.4308 | 61.5076 | 123.0621 | 61.4762 | 122.8495 | 61.5621 | 61.5935 | 61.4567 | 61.4881
1264.0625 | 123.3307 | -61.4594 | 61.6241 | 0.030283 | -0.035942 | -0.016578 | 0.002454 | 0.031687 | 0.003172 | 0.033424 | 61.5829 | 0.19369 | 61.4821 | -0.042259 | 0.025345 | 61.5753 | -0.006014 | 61.3764 | 61.4896 | 61.4234 | 61.4428 | 61.4618 | 61.491 | 61.4625 | 61.4928 | 123.0422 | 61.653 | 122.9414 | 61.4171 | 61.4847 | 123.0347 | 61.4533 | 122.8357 | 61.5575 | 61.5889 | 61.4567 | 61.4881
1265.0625 | 123.2162 | -61.5051 | 61.647 | 0.034862 | -0.035942 | -0.012 | 0.011611 | 0.027109 | -0.001406 | 0.038003 | 61.592 | 0.18911 | 61.5187 | -0.051417 | 0.025345 | 61.5753 | -0.006014 | 61.3718 | 61.54 | 61.4692 | 61.4931 | 61.5167 | 61.5322 | 61.5037 | 61.5431 | 123.0972 | 61.6942 | 123.0238 | 61.4537 | 61.5305 | 123.0804 | 61.4991 | 122.8769 | 61.5667 | 61.5981 | 61.4934 | 61.5247
1266.0625 | 123.2758 | -61.4868 | 61.6516 | 0.030283 | -0.035942 | -0.012 | 0.020768 | 0.036265 | 0.003172 | 0.028846 | 61.592 | 0.18453 | 61.4867 | -0.046838 | 0.025345 | 61.5753 | -0.010593 | 61.3672 | 61.5171 | 61.4509 | 61.4748 | 61.5076 | 61.5231 | 61.49 | 61.5157 | 123.0789 | 61.6713 | 122.9735 | 61.44 | 61.5122 | 123.0621 | 61.4762 | 122.8541 | 61.5667 | 61.6026 | 61.4613 | 61.4973
1267.0625 | 123.2346 | -61.5234 | 61.6333 | 0.025705 | -0.035942 | -0.016578 | 0.002454 | 0.036265 | 0.003172 | 0.028846 | 61.592 | 0.19369 | 61.5096 | -0.055996 | 0.020767 | 61.5799 | -0.015171 | 61.3764 | 61.5491 | 61.4875 | 61.5069 | 61.5259 | 61.5597 | 61.5266 | 61.5523 | 123.1155 | 61.7171 | 123.033 | 61.4674 | 61.5442 | 123.1033 | 61.5083 | 122.8998 | 61.5713 | 61.6072 | 61.4888 | 61.5247
1268.0625 | 123.2895 | -61.496 | 61.6241 | 0.03944 | -0.026784 | -0.007421 | 0.007033 | 0.036265 | 0.003172 | 0.024268 | 61.6012 | 0.19369 | 61.5233 | -0.055996 | 0.025345 | 61.5799 | -0.010593 | 61.3718 | 61.5354 | 61.4692 | 61.4886 | 61.503 | 61.5322 | 61.4991 | 61.5202 | 123.0972 | 61.6897 | 123.0193 | 61.44 | 61.5213 | 123.0759 | 61.4854 | 122.8678 | 61.5759 | 61.6118 | 61.4979 | 61.5339
1269.0625 | 123.3261 | -61.4822 | 61.6058 | 0.030283 | -0.026784 | -0.016578 | 0.002454 | 0.031687 | 0.003172 | 0.028846 | 61.592 | 0.18911 | 61.4821 | -0.051417 | 0.020767 | 61.5799 | -0.010593 | 61.3672 | 61.5125 | 61.4555 | 61.4657 | 61.4847 | 61.5139 | 61.4854 | 61.5111 | 123.0743 | 61.6713 | 122.9643 | 61.4308 | 61.503 | 123.0621 | 61.4716 | 122.8495 | 61.5713 | 61.6026 | 61.4613 | 61.4927
1270.0625 | 123.262 | -61.4914 | 61.6608 | 0.034862 | -0.031363 | -0.012 | 0.002454 | 0.040843 | -0.001406 | 0.038003 | 61.592 | 0.18453 | 61.5279 | -0.046838 | 0.025345 | 61.5753 | -0.006014 | 61.3672 | 61.5263 | 61.46 | 61.4794 | 61.4938 | 61.5322 | 61.49 | 61.5294 | 123.0834 | 61.6759 | 123.0193 | 61.4446 | 61.5167 | 123.0667 | 61.4854 | 122.8586 | 61.5667 | 61.5981 | 61.5025 | 61.5339
1271.0625 | 123.2162 | -61.4868 | 61.6333 | 0.03944 | -0.035942 | -0.007421 | 0.007033 | 0.036265 | -0.001406 | 0.033424 | 61.592 | 0.18911 | 61.5233 | -0.051417 | 0.020767 | 61.5799 | -0.006014 | 61.3672 | 61.5263 | 61.4509 | 61.4794 | 61.4938 | 61.5231 | 61.4854 | 61.5202 | 123.0789 | 61.6759 | 123.0101 | 61.4354 | 61.5076 | 123.0667 | 61.4808 | 122.8541 | 61.5713 | 61.5981 | 61.5025 | 61.5293
1272.0625 | 123.2712 | -61.4868 | 61.6287 | 0.044018 | -0.031363 | -0.007421 | 0.007033 | 0.036265 | -0.001406 | 0.033424 | 61.592 | 0.19369 | 61.4912 | -0.042259 | 0.025345 | 61.5707 | -0.010593 | 61.3718 | 61.5308 | 61.4555 | 61.4794 | 61.4938 | 61.5231 | 61.4854 | 61.5202 | 123.0789 | 61.6805 | 122.9781 | 61.4446 | 61.5122 | 123.0576 | 61.4762 | 122.8586 | 61.5667 | 61.6026 | 61.4659 | 61.5018
1273.0625 | 123.2941 | -61.4731 | 61.647 | 0.03944 | -0.035942 | -0.012 | 0.01619 | 0.040843 | -0.001406 | 0.038003 | 61.592 | 0.19827 | 61.4867 | -0.046838 | 0.020767 | 61.5753 | -0.006014 | 61.3718 | 61.5125 | 61.4371 | 61.4611 | 61.4893 | 61.5139 | 61.4717 | 61.5111 | 123.0651 | 61.6713 | 122.9597 | 61.4262 | 61.4939 | 123.0484 | 61.4671 | 122.8449 | 61.5713 | 61.5981 | 61.4659 | 61.4927
1274.0625 | 123.3627 | -61.4685 | 61.6058 | 0.03944 | -0.035942 | -0.021157 | 0.011611 | 0.036265 | -0.001406 | 0.033424 | 61.592 | 0.18911 | 61.5233 | -0.046838 | 0.016188 | 61.5799 | -0.015171 | 61.3718 | 61.5079 | 61.4326 | 61.4473 | 61.4801 | 61.5048 | 61.4671 | 61.5019 | 123.0605 | 61.6576 | 122.9918 | 61.4217 | 61.4847 | 123.0484 | 61.4533 | 122.8403 | 61.5759 | 61.6072 | 61.5071 | 61.5385
1275.0625 | 123.2391 | -61.5005 | 61.6425 | 0.034862 | -0.035942 | -0.016578 | -0.002124 | 0.040843 | 0.00775 | 0.033424 | 61.5966 | 0.19369 | 61.5187 | -0.046838 | 0.020767 | 61.5753 | -0.010593 | 61.3764 | 61.5354 | 61.4646 | 61.484 | 61.4984 | 61.5414 | 61.5083 | 61.534 | 123.0972 | 61.6942 | 123.0193 | 61.4537 | 61.5213 | 123.0759 | 61.49 | 122.8769 | 61.5759 | 61.6072 | 61.4979 | 61.5293
1276.0625 | 123.2666 | -61.4822 | 61.6241 | 0.034862 | -0.026784 | -0.012 | 0.011611 | 0.040843 | 0.003172 | 0.038003 | 61.592 | 0.19827 | 61.4867 | -0.046838 | 0.016188 | 61.5662 | -0.006014 | 61.3764 | 61.5171 | 61.4555 | 61.4702 | 61.4939 | 61.5231 | 61.4854 | 61.5202 | 123.0743 | 61.6805 | 122.9689 | 61.4354 | 61.4984 | 123.0484 | 61.4762 | 122.8586 | 61.5759 | 61.5981 | 61.4705 | 61.4927
1277.0625 | 123.2666 | -61.5051 | 61.6425 | 0.03944 | -0.026784 | -0.021157 | 0.011611 | 0.036265 | 0.003172 | 0.033424 | 61.592 | 0.18911 | 61.4775 | -0.042259 | 0.025345 | 61.5753 | -0.001436 | 61.3764 | 61.5446 | 61.4783 | 61.484 | 61.5167 | 61.5414 | 61.5083 | 61.5386 | 123.0972 | 61.6942 | 122.9826 | 61.4629 | 61.5305 | 123.0804 | 61.5037 | 122.8815 | 61.5667 | 61.5935 | 61.4522 | 61.4789
1278.0625 | 123.2941 | -61.4822 | 61.6333 | 0.034862 | -0.031363 | -0.016578 | 0.002454 | 0.027109 | -0.010563 | 0.028846 | 61.5966 | 0.18911 | 61.537 | -0.046838 | 0.016188 | 61.5799 | -0.001436 | 61.3856 | 61.5171 | 61.4509 | 61.4657 | 61.4847 | 61.5093 | 61.4717 | 61.5111 | 123.0789 | 61.6713 | 123.0193 | 61.4354 | 61.4984 | 123.0621 | 61.4808 | 122.8678 | 61.5804 | 61.5981 | 61.5208 | 61.5385
1279.0625 | 123.436 | -61.4502 | 61.6058 | 0.03944 | -0.026784 | -0.012 | 0.011611 | 0.031687 | -0.001406 | 0.033424 | 61.5966 | 0.19369 | 61.537 | -0.051417 | 0.025345 | 61.5799 | -0.006014 | 61.3672 | 61.4896 | 61.4234 | 61.4382 | 61.4618 | 61.4819 | 61.4488 | 61.4836 | 123.0468 | 61.6439 | 122.9872 | 61.3988 | 61.4755 | 123.0301 | 61.4442 | 122.8174 | 61.5713 | 61.6026 | 61.5117 | 61.543
1280.0625 | 123.2803 | -61.4594 | 61.6333 | 0.034862 | -0.031363 | -0.021157 | 0.011611 | 0.040843 | -0.005985 | 0.028846 | 61.5966 | 0.18911 | 61.4912 | -0.042259 | 0.029923 | 61.5753 | -0.001436 | 61.3856 | 61.4942 | 61.428 | 61.4382 | 61.471 | 61.5002 | 61.4534 | 61.4882 | 123.056 | 61.6485 | 122.9506 | 61.4171 | 61.4893 | 123.0347 | 61.4579 | 122.8449 | 61.5667 | 61.5981 | 61.4613 | 61.4927
1281.0625 | 123.3215 | -61.4731 | 61.6241 | 0.030283 | -0.040521 | -0.016578 | -0.002124 | 0.031687 | 0.003172 | 0.038003 | 61.592 | 0.18911 | 61.4867 | -0.042259 | 0.020767 | 61.5753 | 0.003143 | 61.3764 | 61.5034 | 61.4326 | 61.4565 | 61.471 | 61.5048 | 61.4763 | 61.5111 | 123.0651 | 61.6622 | 122.9597 | 61.4308 | 61.4939 | 123.0484 | 61.4762 | 122.8495 | 61.5713 | 61.5889 | 61.4659 | 61.4835
1282.0625 | 123.2803 | -61.4914 | 61.6608 | 0.034862 | -0.031363 | -0.007421 | 0.011611 | 0.031687 | -0.005985 | 0.033424 | 61.592 | 0.18911 | 61.4867 | -0.046838 | 0.020767 | 61.5799 | -0.006014 | 61.3718 | 61.5263 | 61.46 | 61.484 | 61.503 | 61.5231 | 61.4854 | 61.5248 | 123.0834 | 61.6805 | 122.9781 | 61.4446 | 61.5122 | 123.0713 | 61.4854 | 122.8632 | 61.5713 | 61.5981 | 61.4659 | 61.4927
1283.0625 | 123.3032 | -61.4639 | 61.6379 | 0.034862 | -0.040521 | -0.016578 | 0.01619 | 0.040843 | -0.005985 | 0.033424 | 61.592 | 0.19827 | 61.4958 | -0.051417 | 0.025345 | 61.5707 | -0.006014 | 61.3718 | 61.4988 | 61.4234 | 61.4474 | 61.4801 | 61.5048 | 61.4579 | 61.4974 | 123.056 | 61.6622 | 122.9598 | 61.4125 | 61.4893 | 123.0347 | 61.4579 | 122.8357 | 61.5667 | 61.5981 | 61.4705 | 61.5018
1284.0625 | 123.3536 | -61.4914 | 61.5875 | 0.030283 | -0.035942 | -0.016578 | 0.007033 | 0.036265 | -0.001406 | 0.033424 | 61.592 | 0.18911 | 61.505 | -0.046838 | 0.016188 | 61.5707 | -0.006014 | 61.3718 | 61.5217 | 61.4555 | 61.4748 | 61.4984 | 61.5277 | 61.49 | 61.5248 | 123.0834 | 61.6805 | 122.9964 | 61.4446 | 61.5076 | 123.0621 | 61.4854 | 122.8632 | 61.5759 | 61.5981 | 61.4888 | 61.511
1285.0625 | 123.3124 | -61.4548 | 61.6379 | 0.034862 | -0.026784 | -0.016578 | 0.007033 | 0.031687 | 0.00775 | 0.038003 | 61.5966 | 0.18911 | 61.5416 | -0.042259 | 0.025345 | 61.5799 | -0.010593 | 61.3718 | 61.4896 | 61.428 | 61.4382 | 61.4618 | 61.4865 | 61.4625 | 61.4928 | 123.0514 | 61.6439 | 122.9964 | 61.4125 | 61.4801 | 123.0347 | 61.4442 | 122.8266 | 61.5713 | 61.6072 | 61.5163 | 61.5522
1286.0625 | 123.3124 | -61.4731 | 61.6562 | 0.044018 | -0.026784 | -0.016578 | 0.002454 | 0.027109 | -0.001406 | 0.033424 | 61.5875 | 0.19369 | 61.5096 | -0.046838 | 0.025345 | 61.5799 | -0.006014 | 61.3764 | 61.5171 | 61.4463 | 61.4565 | 61.4755 | 61.5002 | 61.4717 | 61.5065 | 123.0605 | 61.6668 | 122.9826 | 61.4262 | 61.4984 | 123.053 | 61.4671 | 122.8495 | 61.5621 | 61.5935 | 61.4842 | 61.5156
1287.0625 | 123.3078 | -61.4822 | 61.6837 | 0.034862 | -0.031363 | -0.012 | 0.007033 | 0.036265 | -0.005985 | 0.024268 | 61.5966 | 0.19369 | 61.4867 | -0.042259 | 0.029923 | 61.5799 | -0.001436 | 61.3764 | 61.5171 | 61.4509 | 61.4702 | 61.4893 | 61.5185 | 61.4763 | 61.5065 | 123.0789 | 61.6759 | 122.9689 | 61.44 | 61.5122 | 123.0621 | 61.4808 | 122.8586 | 61.5667 | 61.5981 | 61.4567 | 61.4881
1288.0625 | 123.2849 | -61.496 | 61.6653 | 0.030283 | -0.035942 | -0.012 | 0.011611 | 0.040843 | -0.005985 | 0.024268 | 61.5966 | 0.18911 | 61.5096 | -0.051417 | 0.029923 | 61.5799 | -0.001436 | 61.3672 | 61.5263 | 61.46 | 61.484 | 61.5076 | 61.5368 | 61.49 | 61.5202 | 123.0926 | 61.6851 | 123.0055 | 61.4446 | 61.5259 | 123.0759 | 61.4945 | 122.8632 | 61.5667 | 61.5981 | 61.4796 | 61.511
1289.0625 | 123.3124 | -61.4822 | 61.6058 | 0.034862 | -0.026784 | -0.016578 | 0.011611 | 0.027109 | 0.003172 | 0.038003 | 61.5966 | 0.19369 | 61.5279 | -0.046838 | 0.016188 | 61.5753 | -0.015171 | 61.3764 | 61.5171 | 61.4555 | 61.4657 | 61.4939 | 61.5093 | 61.4854 | 61.5202 | 123.0789 | 61.6759 | 123.0101 | 61.4354 | 61.4984 | 123.0576 | 61.4671 | 122.8586 | 61.5804 | 61.6118 | 61.5117 | 61.543
1290.0625 | 123.2758 | -61.4777 | 61.615 | 0.034862 | -0.031363 | -0.012 | 0.011611 | 0.036265 | 0.00775 | 0.033424 | 61.6012 | 0.19369 | 61.5233 | -0.042259 | 0.025345 | 61.5707 | -0.001436 | 61.3718 | 61.5125 | 61.4463 | 61.4657 | 61.4893 | 61.5139 | 61.4854 | 61.5111 | 123.0789 | 61.6713 | 123.001 | 61.4354 | 61.503 | 123.0484 | 61.4762 | 122.8495 | 61.5759 | 61.6026 | 61.4979 | 61.5247
1291.0625 | 123.3444 | -61.4548 | 61.647 | 0.030283 | -0.026784 | -0.012 | 0.011611 | 0.040843 | 0.003172 | 0.033424 | 61.5966 | 0.19369 | 61.4912 | -0.042259 | 0.020767 | 61.5845 | -0.001436 | 61.3672 | 61.4851 | 61.428 | 61.4428 | 61.4664 | 61.4956 | 61.4579 | 61.4882 | 123.0514 | 61.6485 | 122.946 | 61.4125 | 61.4755 | 123.0392 | 61.4533 | 122.822 | 61.5759 | 61.5981 | 61.4705 | 61.4927
1292.0625 | 123.3261 | -61.4731 | 61.6013 | 0.025705 | -0.031363 | -0.012 | 0.002454 | 0.031687 | -0.001406 | 0.033424 | 61.5966 | 0.19369 | 61.505 | -0.055996 | 0.025345 | 61.5799 | -0.010593 | 61.3672 | 61.4988 | 61.4417 | 61.4611 | 61.4755 | 61.5048 | 61.4717 | 61.5065 | 123.0697 | 61.6668 | 122.9781 | 61.4171 | 61.4984 | 123.053 | 61.4625 | 122.8403 | 61.5713 | 61.6072 | 61.4796 | 61.5156
1293.0625 | 123.2758 | -61.4868 | 61.6745 | 0.030283 | -0.031363 | -0.007421 | 0.007033 | 0.036265 | -0.005985 | 0.028846 | 61.5966 | 0.18911 | 61.5324 | -0.03768 | 0.020767 | 61.5753 | -0.006014 | 61.3672 | 61.5171 | 61.4555 | 61.4794 | 61.4938 | 61.5231 | 61.4808 | 61.5157 | 123.0834 | 61.6759 | 123.0193 | 61.4491 | 61.5076 | 123.0621 | 61.4808 | 122.8541 | 61.5759 | 61.6026 | 61.5117 | 61.5385
1294.0625 | 123.2574 | -61.4868 | 61.647 | 0.034862 | -0.035942 | -0.007421 | 0.007033 | 0.036265 | 0.00775 | 0.028846 | 61.592 | 0.19369 | 61.5141 | -0.051417 | 0.025345 | 61.5799 | -0.006014 | 61.3764 | 61.5217 | 61.4509 | 61.4794 | 61.4938 | 61.5231 | 61.4946 | 61.5157 | 123.0789 | 61.6805 | 123.001 | 61.4354 | 61.5122 | 123.0667 | 61.4808 | 122.8632 | 61.5667 | 61.5981 | 61.4888 | 61.5202
1295.0625 | 123.3353 | -61.4594 | 61.6699 | 0.030283 | -0.031363 | -0.007421 | 0.011611 | 0.036265 | 0.00775 | 0.028846 | 61.5829 | 0.19827 | 61.4958 | -0.03768 | 0.020767 | 61.5753 | -0.010593 | 61.3672 | 61.4896 | 61.428 | 61.4519 | 61.471 | 61.4956 | 61.4671 | 61.4882 | 123.0422 | 61.6576 | 122.9552 | 61.4217 | 61.4801 | 123.0347 | 61.4488 | 122.8266 | 61.5621 | 61.5935 | 61.4751 | 61.5064
1296.0625 | 123.2941 | -61.4594 | 61.6608 | 0.030283 | -0.031363 | -0.021157 | 0.01619 | 0.036265 | -0.001406 | 0.024268 | 61.592 | 0.19369 | 61.5004 | -0.051417 | 0.025345 | 61.5799 | -0.006014 | 61.3672 | 61.4896 | 61.428 | 61.4382 | 61.4755 | 61.4956 | 61.4579 | 61.4836 | 123.0514 | 61.653 | 122.9598 | 61.4079 | 61.4847 | 123.0392 | 61.4533 | 122.8266 | 61.5667 | 61.5981 | 61.4751 | 61.5064
1297.0625 | 123.3444 | -61.4685 | 61.5875 | 0.030283 | -0.035942 | -0.016578 | 0.002454 | 0.040843 | -0.001406 | 0.038003 | 61.5875 | 0.19827 | 61.5187 | -0.046838 | 0.025345 | 61.5799 | -0.006014 | 61.3764 | 61.4988 | 61.4326 | 61.4519 | 61.471 | 61.5093 | 61.4671 | 61.5065 | 123.056 | 61.6668 | 122.9872 | 61.4217 | 61.4939 | 123.0484 | 61.4625 | 122.8449 | 61.5621 | 61.5935 | 61.4934 | 61.5247
1298.0625 | 123.3353 | -61.5005 | 61.6379 | 0.034862 | -0.031363 | -0.012 | 0.011611 | 0.040843 | 0.003172 | 0.028846 | 61.5966 | 0.19369 | 61.5233 | -0.046838 | 0.025345 | 61.5799 | -0.010593 | 61.381 | 61.5354 | 61.4692 | 61.4885 | 61.5122 | 61.5414 | 61.5037 | 61.5294 | 123.0972 | 61.6942 | 123.0238 | 61.4537 | 61.5259 | 123.0804 | 61.49 | 122.8815 | 61.5713 | 61.6072 | 61.4979 | 61.5339
1299.0625 | 123.3582 | -61.4731 | 61.5784 | 0.030283 | -0.035942 | -0.016578 | 0.007033 | 0.040843 | -0.001406 | 0.024268 | 61.592 | 0.18911 | 61.4867 | -0.042259 | 0.020767 | 61.5753 | -0.006014 | 61.3764 | 61.5034 | 61.4371 | 61.4565 | 61.4801 | 61.5139 | 61.4717 | 61.4974 | 123.0651 | 61.6622 | 122.9597 | 61.4308 | 61.4939 | 123.0484 | 61.4671 | 122.8495 | 61.5713 | 61.5981 | 61.4659 | 61.4927
1300.0625 | 123.3353 | -61.4731 | 61.647 | 0.034862 | -0.022205 | -0.016578 | 0.011611 | 0.031687 | -0.001406 | 0.033424 | 61.6012 | 0.18911 | 61.4958 | -0.046838 | 0.029923 | 61.5799 | -0.006014 | 61.3718 | 61.5079 | 61.4509 | 61.4565 | 61.4847 | 61.5048 | 61.4717 | 61.5065 | 123.0743 | 61.6622 | 122.9689 | 61.4262 | 61.503 | 123.053 | 61.4671 | 122.8449 | 61.5713 | 61.6072 | 61.4659 | 61.5018
1301.0625 | 123.2391 | -61.4639 | 61.647 | 0.034862 | -0.035942 | -0.012 | 0.011611 | 0.040843 | 0.003172 | 0.042581 | 61.6012 | 0.18911 | 61.5324 | -0.051417 | 0.025345 | 61.5753 | -0.001436 | 61.3718 | 61.4988 | 61.428 | 61.4519 | 61.4755 | 61.5048 | 61.4671 | 61.5065 | 123.0651 | 61.653 | 122.9964 | 61.4125 | 61.4893 | 123.0392 | 61.4625 | 122.8357 | 61.5759 | 61.6026 | 61.5071 | 61.5339
1302.0625 | 123.3215 | -61.4639 | 61.6058 | 0.034862 | -0.031363 | -0.012 | 0.002454 | 0.036265 | -0.001406 | 0.033424 | 61.5966 | 0.19369 | 61.5233 | -0.051417 | 0.025345 | 61.5845 | -0.006014 | 61.3764 | 61.4988 | 61.4326 | 61.4519 | 61.4664 | 61.5002 | 61.4625 | 61.4974 | 123.0605 | 61.6576 | 122.9872 | 61.4125 | 61.4893 | 123.0484 | 61.4579 | 122.8403 | 61.5713 | 61.6026 | 61.4979 | 61.5293
1303.0625 | 123.2941 | -61.4685 | 61.6425 | 0.034862 | -0.035942 | -0.012 | 0.002454 | 0.040843 | -0.001406 | 0.033424 | 61.592 | 0.19827 | 61.4912 | -0.042259 | 0.020767 | 61.5753 | -0.001436 | 61.381 | 61.5034 | 61.4326 | 61.4565 | 61.471 | 61.5093 | 61.4671 | 61.5019 | 123.0605 | 61.6668 | 122.9598 | 61.4262 | 61.4893 | 123.0438 | 61.4671 | 122.8495 | 61.5713 | 61.5935 | 61.4705 | 61.4927
1304.0625 | 123.2574 | -61.496 | 61.6379 | 0.030283 | -0.026784 | -0.016578 | 0.011611 | 0.036265 | 0.003172 | 0.033424 | 61.6058 | 0.19827 | 61.4867 | -0.042259 | 0.016188 | 61.5799 | -0.010593 | 61.3764 | 61.5263 | 61.4692 | 61.4794 | 61.5076 | 61.5322 | 61.4991 | 61.5294 | 123.1017 | 61.6942 | 122.9826 | 61.4537 | 61.5122 | 123.0759 | 61.4854 | 122.8724 | 61.5896 | 61.6164 | 61.4705 | 61.4973
1305.0625 | 123.2758 | -61.4594 | 61.6562 | 0.030283 | -0.031363 | -0.016578 | 0.011611 | 0.036265 | 0.003172 | 0.033424 | 61.5966 | 0.19369 | 61.5324 | -0.051417 | 0.029923 | 61.5845 | -0.001436 | 61.3718 | 61.4896 | 61.428 | 61.4428 | 61.471 | 61.4956 | 61.4625 | 61.4928 | 123.056 | 61.653 | 122.9918 | 61.4079 | 61.4893 | 123.0438 | 61.4579 | 122.8312 | 61.5667 | 61.5981 | 61.5025 | 61.5339
1306.0625 | 123.317 | -61.4685 | 61.6516 | 0.034862 | -0.031363 | -0.016578 | 0.007033 | 0.040843 | -0.001406 | 0.028846 | 61.5966 | 0.19369 | 61.5416 | -0.046838 | 0.029923 | 61.5753 | -0.001436 | 61.3764 | 61.5034 | 61.4371 | 61.4519 | 61.4755 | 61.5093 | 61.4671 | 61.4974 | 123.0651 | 61.6622 | 123.0101 | 61.4217 | 61.4984 | 123.0438 | 61.4671 | 122.8449 | 61.5667 | 61.5981 | 61.5117 | 61.543
1307.0625 | 123.2758 | -61.5189 | 61.6425 | 0.034862 | -0.031363 | -0.012 | 0.007033 | 0.045421 | 0.003172 | 0.038003 | 61.5829 | 0.19369 | 61.4958 | -0.046838 | 0.020767 | 61.5753 | -0.010593 | 61.3718 | 61.5537 | 61.4875 | 61.5069 | 61.5259 | 61.5643 | 61.522 | 61.5569 | 123.1017 | 61.7125 | 123.0147 | 61.472 | 61.5396 | 123.0942 | 61.5083 | 122.8907 | 61.5621 | 61.5935 | 61.4751 | 61.5064
1308.0625 | 123.2208 | -61.496 | 61.6287 | 0.03944 | -0.022205 | -0.021157 | 0.002454 | 0.022531 | 0.003172 | 0.033424 | 61.5966 | 0.19827 | 61.4958 | -0.03768 | 0.020767 | 61.5753 | -0.010593 | 61.3718 | 61.5354 | 61.4738 | 61.4748 | 61.4984 | 61.5185 | 61.4991 | 61.5294 | 123.0926 | 61.6942 | 122.9918 | 61.4583 | 61.5167 | 123.0713 | 61.4854 | 122.8678 | 61.5759 | 61.6072 | 61.4751 | 61.5064
1309.0625 | 123.3902 | -61.4594 | 61.5967 | 0.034862 | -0.031363 | -0.012 | 0.002454 | 0.031687 | -0.001406 | 0.028846 | 61.5966 | 0.18911 | 61.5187 | -0.042259 | 0.020767 | 61.5799 | -0.010593 | 61.3764 | 61.4942 | 61.428 | 61.4474 | 61.4618 | 61.491 | 61.4579 | 61.4882 | 123.056 | 61.6485 | 122.9781 | 61.4171 | 61.4801 | 123.0392 | 61.4488 | 122.8357 | 61.5759 | 61.6072 | 61.4979 | 61.5293
1310.0625 | 123.3032 | -61.496 | 61.6608 | 0.034862 | -0.026784 | -0.016578 | 0.007033 | 0.036265 | 0.003172 | 0.042581 | 61.6058 | 0.18911 | 61.5324 | -0.046838 | 0.020767 | 61.5799 | -0.006014 | 61.3764 | 61.5308 | 61.4692 | 61.4794 | 61.503 | 61.5322 | 61.4991 | 61.5386 | 123.1017 | 61.6851 | 123.0284 | 61.4491 | 61.5167 | 123.0759 | 61.49 | 122.8724 | 61.585 | 61.6118 | 61.5117 | 61.5385
1311.0625 | 123.317 | -61.4594 | 61.647 | 0.034862 | -0.026784 | -0.016578 | 0.007033 | 0.036265 | 0.003172 | 0.038003 | 61.6012 | 0.19827 | 61.4867 | -0.046838 | 0.020767 | 61.5753 | -0.001436 | 61.381 | 61.4942 | 61.4326 | 61.4428 | 61.4664 | 61.4956 | 61.4625 | 61.4974 | 123.0606 | 61.6576 | 122.946 | 61.4125 | 61.4801 | 123.0347 | 61.4579 | 122.8403 | 61.5804 | 61.6026 | 61.4659 | 61.4881
1312.0625 | 123.2849 | -61.4868 | 61.6287 | 0.03944 | -0.031363 | -0.012 | 0.011611 | 0.040843 | -0.001406 | 0.028846 | 61.5966 | 0.18911 | 61.4867 | -0.046838 | 0.025345 | 61.5799 | -0.006014 | 61.3764 | 61.5263 | 61.4555 | 61.4748 | 61.4984 | 61.5277 | 61.4854 | 61.5157 | 123.0834 | 61.6759 | 122.9735 | 61.44 | 61.5122 | 123.0667 | 61.4808 | 122.8632 | 61.5713 | 61.6026 | 61.4613 | 61.4927
1313.0625 | 123.2529 | -61.4777 | 61.6425 | 0.034862 | -0.031363 | -0.016578 | 0.002454 | 0.036265 | 0.003172 | 0.033424 | 61.6012 | 0.19369 | 61.5096 | -0.046838 | 0.025345 | 61.5799 | -0.010593 | 61.3764 | 61.5125 | 61.4463 | 61.4611 | 61.4801 | 61.5139 | 61.4808 | 61.5111 | 123.0789 | 61.6713 | 122.9872 | 61.4308 | 61.503 | 123.0576 | 61.4671 | 122.8541 | 61.5759 | 61.6118 | 61.4842 | 61.5202
1314.0625 | 123.3398 | -61.4639 | 61.6196 | 0.025705 | -0.035942 | -0.021157 | 0.007033 | 0.040843 | 0.003172 | 0.038003 | 61.5966 | 0.18911 | 61.5324 | -0.042259 | 0.025345 | 61.5799 | -0.006014 | 61.3718 | 61.4896 | 61.428 | 61.4428 | 61.471 | 61.5048 | 61.4671 | 61.5019 | 123.0605 | 61.653 | 122.9964 | 61.4217 | 61.4893 | 123.0438 | 61.4579 | 122.8357 | 61.5713 | 61.6026 | 61.5071 | 61.5385
1315.0625 | 123.3032 | -61.4639 | 61.6608 | 0.030283 | -0.040521 | -0.012 | 0.007033 | 0.036265 | 0.00775 | 0.033424 | 61.592 | 0.18911 | 61.4958 | -0.051417 | 0.029923 | 61.5753 | -0.001436 | 61.3764 | 61.4942 | 61.4234 | 61.4519 | 61.471 | 61.5002 | 61.4717 | 61.4974 | 123.056 | 61.653 | 122.9598 | 61.4125 | 61.4939 | 123.0392 | 61.4625 | 122.8403 | 61.5621 | 61.5935 | 61.4659 | 61.4973
1316.0625 | 123.2986 | -61.4777 | 61.6516 | 0.030283 | -0.026784 | -0.016578 | 0.002454 | 0.040843 | 0.003172 | 0.033424 | 61.592 | 0.19369 | 61.4821 | -0.046838 | 0.025345 | 61.5799 | -0.006014 | 61.3764 | 61.5079 | 61.4509 | 61.4611 | 61.4801 | 61.5185 | 61.4808 | 61.5111 | 123.0697 | 61.6713 | 122.9597 | 61.4308 | 61.503 | 123.0576 | 61.4716 | 122.8541 | 61.5667 | 61.5981 | 61.4567 | 61.4881
1317.0625 | 123.3078 | -61.4456 | 61.6379 | 0.030283 | -0.035942 | -0.012 | 0.002454 | 0.040843 | 0.003172 | 0.033424 | 61.5966 | 0.18911 | 61.5096 | -0.046838 | 0.029923 | 61.5753 | -0.006014 | 61.381 | 61.4759 | 61.4097 | 61.4336 | 61.4481 | 61.4865 | 61.4488 | 61.479 | 123.0422 | 61.6347 | 122.9552 | 61.3988 | 61.4755 | 123.0209 | 61.4396 | 122.8266 | 61.5667 | 61.6026 | 61.4796 | 61.5156
1318.0625 | 123.2895 | -61.4639 | 61.647 | 0.030283 | -0.026784 | -0.007421 | 0.007033 | 0.036265 | 0.003172 | 0.038003 | 61.5966 | 0.18911 | 61.5233 | -0.042259 | 0.034501 | 61.5753 | -0.001436 | 61.381 | 61.4942 | 61.4371 | 61.4565 | 61.471 | 61.5002 | 61.4671 | 61.5019 | 123.0605 | 61.653 | 122.9872 | 61.4217 | 61.4984 | 123.0392 | 61.4625 | 122.8449 | 61.5621 | 61.5981 | 61.4888 | 61.5247
1319.0625 | 123.3765 | -61.4594 | 61.5738 | 0.034862 | -0.031363 | -0.021157 | 0.007033 | 0.027109 | 0.003172 | 0.038003 | 61.5966 | 0.19369 | 61.4958 | -0.042259 | 0.020767 | 61.5707 | -0.006014 | 61.381 | 61.4942 | 61.428 | 61.4382 | 61.4664 | 61.4865 | 61.4625 | 61.4974 | 123.056 | 61.653 | 122.9552 | 61.4171 | 61.4801 | 123.0301 | 61.4533 | 122.8403 | 61.5759 | 61.6026 | 61.4751 | 61.5018
1320.0625 | 123.3261 | -61.4822 | 61.647 | 0.030283 | -0.026784 | -0.016578 | 0.011611 | 0.036265 | 0.00775 | 0.038003 | 61.592 | 0.18911 | 61.4867 | -0.055996 | 0.034501 | 61.5891 | -0.006014 | 61.3764 | 61.5125 | 61.4555 | 61.4657 | 61.4939 | 61.5185 | 61.49 | 61.5202 | 123.0743 | 61.6713 | 122.9689 | 61.4262 | 61.5167 | 123.0713 | 61.4762 | 122.8586 | 61.5575 | 61.5981 | 61.4522 | 61.4927
1321.0625 | 123.3032 | -61.4777 | 61.6425 | 0.025705 | -0.026784 | -0.012 | -0.002124 | 0.040843 | -0.005985 | 0.024268 | 61.5966 | 0.19369 | 61.4912 | -0.046838 | 0.020767 | 61.5753 | -0.010593 | 61.3764 | 61.5034 | 61.4509 | 61.4657 | 61.4755 | 61.5185 | 61.4717 | 61.5019 | 123.0743 | 61.6713 | 122.9689 | 61.4308 | 61.4984 | 123.053 | 61.4671 | 122.8541 | 61.5759 | 61.6072 | 61.4705 | 61.5018
1322.0625 | 123.3307 | -61.4731 | 61.6562 | 0.03944 | -0.026784 | -0.012 | 0.007033 | 0.036265 | 0.003172 | 0.033424 | 61.5966 | 0.19827 | 61.5187 | -0.051417 | 0.025345 | 61.5753 | -0.010593 | 61.3764 | 61.5125 | 61.4463 | 61.4611 | 61.4801 | 61.5093 | 61.4763 | 61.5065 | 123.0697 | 61.6713 | 122.9918 | 61.4217 | 61.4984 | 123.0484 | 61.4625 | 122.8495 | 61.5713 | 61.6072 | 61.4934 | 61.5293
1323.0625 | 123.2803 | -61.4868 | 61.6425 | 0.034862 | -0.022205 | -0.012 | 0.011611 | 0.036265 | 0.003172 | 0.033424 | 61.5966 | 0.18911 | 61.5141 | -0.042259 | 0.020767 | 61.5845 | -0.001436 | 61.3764 | 61.5217 | 61.4646 | 61.4748 | 61.4984 | 61.5231 | 61.49 | 61.5202 | 123.0834 | 61.6759 | 123.001 | 61.4446 | 61.5076 | 123.0713 | 61.4854 | 122.8632 | 61.5759 | 61.5981 | 61.4934 | 61.5156
1324.0625 | 123.2803 | -61.4639 | 61.6196 | 0.030283 | -0.031363 | -0.012 | 0.007033 | 0.036265 | -0.001406 | 0.033424 | 61.592 | 0.19369 | 61.4775 | -0.042259 | 0.016188 | 61.5845 | 0.007721 | 61.3718 | 61.4942 | 61.4326 | 61.4519 | 61.471 | 61.5002 | 61.4625 | 61.4974 | 123.056 | 61.6576 | 122.9414 | 61.4217 | 61.4801 | 123.0484 | 61.4716 | 122.8357 | 61.5759 | 61.5843 | 61.4613 | 61.4698
1325.0625 | 123.3124 | -61.4548 | 61.6379 | 0.025705 | -0.031363 | -0.021157 | 0.011611 | 0.040843 | -0.001406 | 0.028846 | 61.6012 | 0.18911 | 61.4912 | -0.042259 | 0.029923 | 61.5707 | 0.003143 | 61.381 | 61.4805 | 61.4234 | 61.4336 | 61.4664 | 61.4956 | 61.4534 | 61.4836 | 123.056 | 61.6439 | 122.946 | 61.4125 | 61.4847 | 123.0255 | 61.4579 | 122.8357 | 61.5713 | 61.5981 | 61.4613 | 61.4881
1326.0625 | 123.2895 | -61.4914 | 61.6379 | 0.034862 | -0.031363 | -0.016578 | 0.011611 | 0.045421 | -0.001406 | 0.033424 | 61.6012 | 0.19369 | 61.5279 | -0.051417 | 0.029923 | 61.5799 | -0.010593 | 61.3764 | 61.5263 | 61.46 | 61.4748 | 61.503 | 61.5368 | 61.49 | 61.5248 | 123.0926 | 61.6851 | 123.0193 | 61.44 | 61.5213 | 123.0713 | 61.4808 | 122.8678 | 61.5713 | 61.6118 | 61.4979 | 61.5385
1327.0625 | 123.2986 | -61.496 | 61.6837 | 0.030283 | -0.035942 | -0.021157 | 0.007033 | 0.040843 | 0.003172 | 0.038003 | 61.6058 | 0.19827 | 61.537 | -0.042259 | 0.029923 | 61.5799 | -0.006014 | 61.381 | 61.5263 | 61.46 | 61.4748 | 61.503 | 61.5368 | 61.4991 | 61.534 | 123.1017 | 61.6942 | 123.033 | 61.4537 | 61.5259 | 123.0759 | 61.49 | 122.8769 | 61.5759 | 61.6118 | 61.5071 | 61.543
1328.0625 | 123.262 | -61.4731 | 61.6791 | 0.025705 | -0.026784 | -0.012 | 0.011611 | 0.031687 | 0.003172 | 0.028846 | 61.592 | 0.18911 | 61.4912 | -0.046838 | 0.025345 | 61.5799 | -0.001436 | 61.3718 | 61.4988 | 61.4463 | 61.4611 | 61.4847 | 61.5048 | 61.4763 | 61.5019 | 123.0651 | 61.6622 | 122.9643 | 61.4262 | 61.4984 | 123.053 | 61.4716 | 122.8449 | 61.5667 | 61.5935 | 61.4659 | 61.4927
1329.0625 | 123.2895 | -61.5005 | 61.6699 | 0.030283 | -0.026784 | -0.016578 | 0.002454 | 0.040843 | -0.001406 | 0.038003 | 61.5966 | 0.19827 | 61.4821 | -0.046838 | 0.029923 | 61.5753 | -0.006014 | 61.381 | 61.5308 | 61.4738 | 61.484 | 61.503 | 61.5414 | 61.4991 | 61.5386 | 123.0972 | 61.6988 | 122.9826 | 61.4537 | 61.5305 | 123.0759 | 61.4945 | 122.8815 | 61.5667 | 61.6026 | 61.4522 | 61.4881
1330.0625 | 123.3032 | -61.4594 | 61.6653 | 0.030283 | -0.031363 | -0.016578 | 0.011611 | 0.036265 | 0.00775 | 0.033424 | 61.6012 | 0.18911 | 61.5233 | -0.046838 | 0.025345 | 61.5799 | -0.006014 | 61.3764 | 61.4896 | 61.428 | 61.4428 | 61.471 | 61.4956 | 61.4671 | 61.4928 | 123.0606 | 61.6485 | 122.9826 | 61.4125 | 61.4847 | 123.0392 | 61.4533 | 122.8357 | 61.5759 | 61.6072 | 61.4979 | 61.5293
1331.0625 | 123.3124 | -61.5051 | 61.6745 | 0.025705 | -0.031363 | -0.016578 | 0.002454 | 0.031687 | 0.003172 | 0.042581 | 61.6058 | 0.18911 | 61.5462 | -0.042259 | 0.020767 | 61.5753 | -0.006014 | 61.3764 | 61.5308 | 61.4738 | 61.4885 | 61.5076 | 61.5368 | 61.5083 | 61.5477 | 123.1109 | 61.6942 | 123.0513 | 61.4629 | 61.5259 | 123.0804 | 61.4991 | 122.8815 | 61.585 | 61.6118 | 61.5254 | 61.5522
1332.0625 | 123.2712 | -61.4685 | 61.6974 | 0.021127 | -0.026784 | -0.021157 | 0.002454 | 0.036265 | -0.001406 | 0.042581 | 61.6058 | 0.19369 | 61.5004 | -0.046838 | 0.025345 | 61.5753 | -0.001436 | 61.3856 | 61.4896 | 61.4417 | 61.4473 | 61.471 | 61.5048 | 61.4671 | 61.5111 | 123.0743 | 61.6622 | 122.9689 | 61.4217 | 61.4939 | 123.0438 | 61.4671 | 122.8541 | 61.5804 | 61.6072 | 61.4751 | 61.5018
1333.0625 | 123.2849 | -61.4822 | 61.6608 | 0.025705 | -0.026784 | -0.021157 | 0.007033 | 0.036265 | 0.003172 | 0.033424 | 61.5875 | 0.19369 | 61.4775 | -0.051417 | 0.025345 | 61.5753 | 0.003143 | 61.3718 | 61.5079 | 61.4555 | 61.4611 | 61.4893 | 61.5185 | 61.4854 | 61.5157 | 123.0697 | 61.6759 | 122.9597 | 61.4308 | 61.5076 | 123.0576 | 61.4854 | 122.8541 | 61.5621 | 61.5843 | 61.4522 | 61.4744
1334.0625 | 123.2574 | -61.4822 | 61.6608 | 0.03944 | -0.031363 | -0.012 | 0.007033 | 0.027109 | 0.003172 | 0.033424 | 61.6012 | 0.19827 | 61.4867 | -0.051417 | 0.029923 | 61.5799 | -0.001436 | 61.3718 | 61.5217 | 61.4509 | 61.4702 | 61.4893 | 61.5093 | 61.4854 | 61.5157 | 123.0834 | 61.6805 | 122.9689 | 61.4308 | 61.5122 | 123.0621 | 61.4808 | 122.8541 | 61.5713 | 61.6026 | 61.4567 | 61.4881
1335.0625 | 123.2849 | -61.4502 | 61.6608 | 0.021127 | -0.026784 | -0.016578 | 0.007033 | 0.036265 | 0.003172 | 0.038003 | 61.5966 | 0.19369 | 61.4821 | -0.055996 | 0.025345 | 61.5845 | -0.010593 | 61.3764 | 61.4713 | 61.4234 | 61.4336 | 61.4572 | 61.4865 | 61.4534 | 61.4882 | 123.0468 | 61.6439 | 122.9323 | 61.3942 | 61.4755 | 123.0347 | 61.4396 | 122.8266 | 61.5713 | 61.6072 | 61.4567 | 61.4927
1336.0625 | 123.2895 | -61.4639 | 61.6653 | 0.034862 | -0.031363 | -0.012 | 0.007033 | 0.036265 | -0.001406 | 0.038003 | 61.6012 | 0.19369 | 61.5187 | -0.046838 | 0.029923 | 61.5707 | -0.001436 | 61.3764 | 61.4988 | 61.4326 | 61.4519 | 61.471 | 61.5002 | 61.4625 | 61.5019 | 123.0651 | 61.6576 | 122.9826 | 61.4171 | 61.4939 | 123.0347 | 61.4625 | 122.8403 | 61.5713 | 61.6026 | 61.4888 | 61.5202
1337.0625 | 123.2712 | -61.4868 | 61.6882 | 0.034862 | -0.031363 | -0.012 | 0.011611 | 0.036265 | -0.001406 | 0.033424 | 61.6012 | 0.19369 | 61.5279 | -0.03768 | 0.034501 | 61.5753 | -0.006014 | 61.3764 | 61.5217 | 61.4555 | 61.4748 | 61.4984 | 61.5231 | 61.4854 | 61.5202 | 123.088 | 61.6805 | 123.0147 | 61.4491 | 61.5213 | 123.0621 | 61.4808 | 122.8632 | 61.5667 | 61.6072 | 61.4934 | 61.5339
1338.0625 | 123.2666 | -61.4777 | 61.6699 | 0.025705 | -0.035942 | -0.016578 | 0.011611 | 0.031687 | -0.001406 | 0.033424 | 61.592 | 0.18911 | 61.5004 | -0.03768 | 0.020767 | 61.5845 | -0.001436 | 61.381 | 61.5034 | 61.4417 | 61.4611 | 61.4893 | 61.5093 | 61.4763 | 61.5111 | 123.0697 | 61.6668 | 122.9781 | 61.44 | 61.4984 | 123.0621 | 61.4762 | 122.8586 | 61.5713 | 61.5935 | 61.4796 | 61.5018
1339.0625 | 123.2895 | -61.4822 | 61.6425 | 0.030283 | -0.026784 | -0.016578 | 0.011611 | 0.040843 | 0.003172 | 0.033424 | 61.5966 | 0.19369 | 61.4912 | -0.046838 | 0.025345 | 61.5799 | -0.006014 | 61.3764 | 61.5125 | 61.4555 | 61.4657 | 61.4939 | 61.5231 | 61.4854 | 61.5157 | 123.0789 | 61.6759 | 122.9735 | 61.4354 | 61.5076 | 123.0621 | 61.4762 | 122.8586 | 61.5713 | 61.6026 | 61.4659 | 61.4973
1340.0625 | 123.2895 | -61.4594 | 61.6837 | 0.034862 | -0.031363 | -0.016578 | 0.011611 | 0.036265 | 0.003172 | 0.033424 | 61.5875 | 0.19369 | 61.5004 | -0.042259 | 0.025345 | 61.5845 | -0.001436 | 61.3718 | 61.4942 | 61.428 | 61.4428 | 61.471 | 61.4956 | 61.4625 | 61.4928 | 123.0468 | 61.653 | 122.9598 | 61.4171 | 61.4847 | 123.0438 | 61.4579 | 122.8312 | 61.5621 | 61.5889 | 61.4751 | 61.5018
1341.0625 | 123.3627 | -61.4594 | 61.6516 | 0.030283 | -0.035942 | -0.016578 | 0.002454 | 0.031687 | 0.003172 | 0.033424 | 61.6012 | 0.19369 | 61.5233 | -0.042259 | 0.020767 | 61.5753 | -0.001436 | 61.3764 | 61.4896 | 61.4234 | 61.4428 | 61.4618 | 61.491 | 61.4625 | 61.4928 | 123.0606 | 61.653 | 122.9826 | 61.4171 | 61.4801 | 123.0347 | 61.4579 | 122.8357 | 61.5804 | 61.6026 | 61.5025 | 61.5247
1342.0625 | 123.4406 | -61.4365 | 61.6699 | 0.030283 | -0.035942 | -0.021157 | 0.01619 | 0.031687 | 0.003172 | 0.033424 | 61.5966 | 0.19369 | 61.5096 | -0.046838 | 0.034501 | 61.5845 | -0.006014 | 61.3764 | 61.4667 | 61.4005 | 61.4153 | 61.4527 | 61.4681 | 61.4396 | 61.4699 | 123.0331 | 61.6302 | 122.946 | 61.3896 | 61.471 | 123.0209 | 61.4304 | 122.8129 | 61.5621 | 61.6026 | 61.4751 | 61.5156
1343.0625 | 123.3536 | -61.4685 | 61.6516 | 0.030283 | -0.031363 | -0.016578 | 0.011611 | 0.036265 | -0.010563 | 0.033424 | 61.592 | 0.19369 | 61.4912 | -0.042259 | 0.025345 | 61.5753 | -0.006014 | 61.3718 | 61.4988 | 61.4371 | 61.4519 | 61.4801 | 61.5048 | 61.4579 | 61.5019 | 123.0605 | 61.6622 | 122.9598 | 61.4262 | 61.4939 | 123.0438 | 61.4625 | 122.8403 | 61.5667 | 61.5981 | 61.4659 | 61.4973
1344.0625 | 123.3398 | -61.4822 | 61.6241 | 0.034862 | -0.031363 | -0.016578 | 0.01619 | 0.031687 | 0.003172 | 0.033424 | 61.6012 | 0.19369 | 61.5004 | -0.046838 | 0.025345 | 61.5845 | -0.006014 | 61.3718 | 61.5171 | 61.4509 | 61.4657 | 61.4984 | 61.5139 | 61.4854 | 61.5157 | 123.0834 | 61.6759 | 122.9826 | 61.4354 | 61.5076 | 123.0667 | 61.4762 | 122.8541 | 61.5759 | 61.6072 | 61.4751 | 61.5064
1345.0625 | 123.3536 | -61.4502 | 61.6699 | 0.034862 | -0.031363 | -0.021157 | 0.002454 | 0.031687 | 0.00775 | 0.038003 | 61.6012 | 0.19369 | 61.5416 | -0.046838 | 0.029923 | 61.5753 | -0.006014 | 61.3764 | 61.4851 | 61.4188 | 61.429 | 61.4526 | 61.4819 | 61.4579 | 61.4882 | 123.0514 | 61.6439 | 122.9918 | 61.4034 | 61.4801 | 123.0255 | 61.4442 | 122.8266 | 61.5713 | 61.6072 | 61.5117 | 61.5476
1346.0625 | 123.3719 | -61.4639 | 61.6425 | 0.025705 | -0.031363 | -0.021157 | 0.002454 | 0.036265 | -0.005985 | 0.033424 | 61.5966 | 0.18453 | 61.4867 | -0.046838 | 0.025345 | 61.5753 | -0.001436 | 61.3764 | 61.4896 | 61.4326 | 61.4428 | 61.4664 | 61.5002 | 61.4579 | 61.4974 | 123.0605 | 61.6485 | 122.9506 | 61.4171 | 61.4893 | 123.0392 | 61.4625 | 122.8403 | 61.5713 | 61.5981 | 61.4613 | 61.4881
1347.0625 | 123.3627 | -61.4777 | 61.615 | 0.025705 | -0.026784 | -0.016578 | 0.007033 | 0.031687 | 0.003172 | 0.028846 | 61.5966 | 0.19369 | 61.5004 | -0.051417 | 0.029923 | 61.5799 | -0.006014 | 61.3718 | 61.5034 | 61.4509 | 61.4611 | 61.4847 | 61.5093 | 61.4808 | 61.5065 | 123.0743 | 61.6713 | 122.9781 | 61.4262 | 61.5076 | 123.0576 | 61.4716 | 122.8495 | 61.5667 | 61.6026 | 61.4705 | 61.5064
1348.0625 | 123.3307 | -61.441 | 61.6058 | 0.030283 | -0.035942 | -0.016578 | 0.007033 | 0.031687 | -0.001406 | 0.038003 | 61.6012 | 0.18911 | 61.537 | -0.046838 | 0.029923 | 61.5753 | -0.010593 | 61.3764 | 61.4713 | 61.4051 | 61.4245 | 61.4481 | 61.4727 | 61.4396 | 61.479 | 123.0422 | 61.6301 | 122.9781 | 61.3942 | 61.471 | 123.0164 | 61.4304 | 122.8174 | 61.5713 | 61.6118 | 61.5071 | 61.5476
1349.0625 | 123.2986 | -61.4731 | 61.6699 | 0.025705 | -0.031363 | -0.012 | 0.007033 | 0.036265 | 0.003172 | 0.028846 | 61.592 | 0.19827 | 61.4867 | -0.042259 | 0.020767 | 61.5845 | -0.001436 | 61.3718 | 61.4988 | 61.4417 | 61.4611 | 61.4801 | 61.5093 | 61.4763 | 61.5019 | 123.0651 | 61.6713 | 122.9597 | 61.4308 | 61.4939 | 123.0576 | 61.4716 | 122.8449 | 61.5713 | 61.5935 | 61.4659 | 61.4881
1350.0625 | 123.4543 | -61.4548 | 61.6287 | 0.034862 | -0.031363 | -0.021157 | 0.002454 | 0.027109 | 0.00775 | 0.024268 | 61.6012 | 0.19369 | 61.5187 | -0.055996 | 0.029923 | 61.5799 | -0.010593 | 61.3718 | 61.4896 | 61.4234 | 61.4336 | 61.4572 | 61.4819 | 61.4625 | 61.479 | 123.056 | 61.6485 | 122.9735 | 61.3988 | 61.4847 | 123.0347 | 61.4442 | 122.8266 | 61.5713 | 61.6118 | 61.4888 | 61.5293
1351.0625 | 123.3856 | -61.4777 | 61.6058 | 0.030283 | -0.031363 | -0.025735 | 0.011611 | 0.031687 | -0.001406 | 0.033424 | 61.592 | 0.18911 | 61.5279 | -0.046838 | 0.034501 | 61.5799 | -0.001436 | 61.3764 | 61.5079 | 61.4463 | 61.4519 | 61.4893 | 61.5093 | 61.4763 | 61.5111 | 123.0697 | 61.6668 | 123.0055 | 61.4308 | 61.5122 | 123.0576 | 61.4762 | 122.8541 | 61.5575 | 61.5935 | 61.4934 | 61.5293
1352.0625 | 123.4268 | -61.4548 | 61.615 | 0.025705 | -0.031363 | -0.021157 | 0.002454 | 0.031687 | -0.001406 | 0.033424 | 61.6012 | 0.19369 | 61.4821 | -0.051417 | 0.025345 | 61.5845 | -0.006014 | 61.3672 | 61.4805 | 61.4234 | 61.4336 | 61.4572 | 61.4865 | 61.4534 | 61.4882 | 123.056 | 61.6485 | 122.9369 | 61.4034 | 61.4801 | 123.0392 | 61.4488 | 122.822 | 61.5759 | 61.6072 | 61.4567 | 61.4881
1353.0625 | 123.3536 | -61.4777 | 61.6196 | 0.030283 | -0.031363 | -0.016578 | 0.007033 | 0.036265 | 0.003172 | 0.033424 | 61.592 | 0.19369 | 61.4912 | -0.046838 | 0.025345 | 61.5753 | -0.006014 | 61.3764 | 61.5079 | 61.4463 | 61.4611 | 61.4847 | 61.5139 | 61.4808 | 61.5111 | 123.0697 | 61.6713 | 122.9689 | 61.4308 | 61.503 | 123.053 | 61.4716 | 122.8541 | 61.5667 | 61.5981 | 61.4659 | 61.4973
1354.0625 | 123.2437 | -61.4822 | 61.6241 | 0.034862 | -0.035942 | -0.012 | 0.007033 | 0.036265 | -0.001406 | 0.033424 | 61.6058 | 0.18911 | 61.5324 | -0.046838 | 0.025345 | 61.5753 | -0.006014 | 61.3718 | 61.5171 | 61.4463 | 61.4702 | 61.4893 | 61.5185 | 61.4808 | 61.5157 | 123.088 | 61.6713 | 123.0147 | 61.4354 | 61.5076 | 123.0576 | 61.4762 | 122.8541 | 61.5804 | 61.6118 | 61.5071 | 61.5385
1355.0625 | 123.3582 | -61.4731 | 61.6058 | 0.034862 | -0.026784 | -0.016578 | 0.007033 | 0.031687 | -0.001406 | 0.028846 | 61.5966 | 0.19369 | 61.5279 | -0.042259 | 0.020767 | 61.5799 | -0.006014 | 61.3764 | 61.5079 | 61.4463 | 61.4565 | 61.4801 | 61.5048 | 61.4717 | 61.5019 | 123.0697 | 61.6668 | 123.001 | 61.4308 | 61.4939 | 123.053 | 61.4671 | 122.8495 | 61.5759 | 61.6026 | 61.5071 | 61.5339
1356.0625 | 123.3353 | -61.5097 | 61.6013 | 0.030283 | -0.031363 | -0.012 | 0.007033 | 0.031687 | 0.003172 | 0.028846 | 61.592 | 0.19369 | 61.4912 | -0.051417 | 0.025345 | 61.5707 | -0.010593 | 61.3718 | 61.54 | 61.4783 | 61.4977 | 61.5167 | 61.5414 | 61.5129 | 61.5386 | 123.1017 | 61.7034 | 123.0009 | 61.4583 | 61.535 | 123.0804 | 61.4991 | 122.8815 | 61.5667 | 61.6026 | 61.4659 | 61.5018
1357.0625 | 123.3627 | -61.4685 | 61.615 | 0.034862 | -0.022205 | -0.016578 | -0.002124 | 0.031687 | -0.001406 | 0.028846 | 61.5875 | 0.19369 | 61.4867 | -0.046838 | 0.025345 | 61.5799 | -0.006014 | 61.3718 | 61.5034 | 61.4463 | 61.4519 | 61.4664 | 61.5002 | 61.4671 | 61.4974 | 123.056 | 61.6622 | 122.9552 | 61.4217 | 61.4939 | 123.0484 | 61.4625 | 122.8403 | 61.5621 | 61.5935 | 61.4613 | 61.4927
1358.0625 | 123.4085 | -61.4456 | 61.5967 | 0.025705 | -0.031363 | -0.012 | 0.007033 | 0.031687 | -0.005985 | 0.028846 | 61.5966 | 0.19827 | 61.537 | -0.046838 | 0.029923 | 61.5799 | -0.006014 | 61.3672 | 61.4713 | 61.4143 | 61.4336 | 61.4527 | 61.4773 | 61.4396 | 61.4745 | 123.0422 | 61.6439 | 122.9826 | 61.3988 | 61.4755 | 123.0255 | 61.4396 | 122.8129 | 61.5667 | 61.6026 | 61.5071 | 61.543
1359.0625 | 123.2895 | -61.4868 | 61.6791 | 0.025705 | -0.026784 | -0.012 | 0.01619 | 0.031687 | 0.00775 | 0.028846 | 61.6012 | 0.19369 | 61.5279 | -0.055996 | 0.020767 | 61.5753 | -0.006014 | 61.381 | 61.5125 | 61.46 | 61.4748 | 61.503 | 61.5185 | 61.4946 | 61.5157 | 123.088 | 61.6805 | 123.0147 | 61.4308 | 61.5076 | 123.0621 | 61.4808 | 122.8678 | 61.5804 | 61.6072 | 61.5071 | 61.5339
1360.0625 | 123.381 | -61.4777 | 61.6196 | 0.03944 | -0.026784 | -0.016578 | 0.007033 | 0.031687 | -0.005985 | 0.024268 | 61.592 | 0.19369 | 61.505 | -0.046838 | 0.020767 | 61.5707 | -0.015171 | 61.3764 | 61.5171 | 61.4509 | 61.4611 | 61.4847 | 61.5093 | 61.4717 | 61.5019 | 123.0697 | 61.6713 | 122.9826 | 61.4308 | 61.4984 | 123.0484 | 61.4625 | 122.8541 | 61.5713 | 61.6072 | 61.4842 | 61.5202
1361.0625 | 123.3994 | -61.4594 | 61.6333 | 0.030283 | -0.035942 | -0.016578 | 0.002454 | 0.027109 | -0.001406 | 0.038003 | 61.5966 | 0.18911 | 61.4912 | -0.042259 | 0.020767 | 61.5707 | -0.006014 | 61.381 | 61.4896 | 61.4234 | 61.4428 | 61.4618 | 61.4865 | 61.4579 | 61.4974 | 123.056 | 61.6485 | 122.9506 | 61.4171 | 61.4801 | 123.0301 | 61.4533 | 122.8403 | 61.5759 | 61.6026 | 61.4705 | 61.4973
1362.0625 | 123.3353 | -61.4731 | 61.6058 | 0.034862 | -0.031363 | -0.016578 | 0.007033 | 0.036265 | 0.003172 | 0.033424 | 61.5875 | 0.18911 | 61.5187 | -0.051417 | 0.020767 | 61.5753 | -0.010593 | 61.3718 | 61.5079 | 61.4417 | 61.4565 | 61.4801 | 61.5093 | 61.4763 | 61.5065 | 123.0605 | 61.6622 | 122.9918 | 61.4217 | 61.4939 | 123.0484 | 61.4625 | 122.8449 | 61.5667 | 61.5981 | 61.4979 | 61.5293
1363.0625 | 123.3627 | -61.4914 | 61.5921 | 0.025705 | -0.022205 | -0.016578 | 0.007033 | 0.031687 | 0.003172 | 0.038003 | 61.5966 | 0.19369 | 61.5279 | -0.042259 | 0.025345 | 61.5845 | -0.006014 | 61.3672 | 61.5171 | 61.4692 | 61.4748 | 61.4984 | 61.5231 | 61.4946 | 61.5294 | 123.088 | 61.6851 | 123.0193 | 61.4491 | 61.5167 | 123.0759 | 61.4854 | 122.8586 | 61.5713 | 61.6026 | 61.5025 | 61.5339
1364.0625 | 123.4085 | -61.4685 | 61.6104 | 0.034862 | -0.031363 | -0.025735 | 0.002454 | 0.031687 | 0.003172 | 0.028846 | 61.5875 | 0.19369 | 61.5096 | -0.042259 | 0.025345 | 61.5799 | 0.003143 | 61.3764 | 61.5034 | 61.4371 | 61.4428 | 61.471 | 61.5002 | 61.4717 | 61.4974 | 123.056 | 61.6622 | 122.9781 | 61.4262 | 61.4939 | 123.0484 | 61.4716 | 122.8449 | 61.5621 | 61.5843 | 61.4842 | 61.5064
1365.0625 | 123.349 | -61.4868 | 61.6196 | 0.030283 | -0.031363 | -0.021157 | 0.007033 | 0.040843 | -0.001406 | 0.024268 | 61.6012 | 0.19369 | 61.4912 | -0.046838 | 0.020767 | 61.5799 | -0.015171 | 61.3672 | 61.5171 | 61.4555 | 61.4657 | 61.4938 | 61.5277 | 61.4854 | 61.5111 | 123.088 | 61.6805 | 122.9781 | 61.44 | 61.5076 | 123.0667 | 61.4716 | 122.8541 | 61.5804 | 61.6164 | 61.4705 | 61.5064
1366.0625 | 123.3444 | -61.4822 | 61.5875 | 0.030283 | -0.035942 | -0.012 | 0.011611 | 0.036265 | -0.001406 | 0.033424 | 61.6012 | 0.19827 | 61.5096 | -0.051417 | 0.020767 | 61.5753 | -0.006014 | 61.3718 | 61.5125 | 61.4463 | 61.4702 | 61.4939 | 61.5185 | 61.4808 | 61.5157 | 123.0834 | 61.6805 | 122.9918 | 61.4308 | 61.503 | 123.0576 | 61.4762 | 122.8541 | 61.5804 | 61.6072 | 61.4888 | 61.5156
1367.0625 | 123.3444 | -61.4777 | 61.6333 | 0.030283 | -0.031363 | -0.016578 | 0.007033 | 0.040843 | 0.003172 | 0.038003 | 61.5966 | 0.19369 | 61.5233 | -0.046838 | 0.025345 | 61.5753 | -0.006014 | 61.3764 | 61.5079 | 61.4463 | 61.4611 | 61.4847 | 61.5185 | 61.4808 | 61.5157 | 123.0743 | 61.6713 | 123.001 | 61.4308 | 61.503 | 123.053 | 61.4716 | 122.8541 | 61.5713 | 61.6026 | 61.4979 | 61.5293
1368.0625 | 123.3444 | -61.4777 | 61.6333 | 0.034862 | -0.031363 | -0.016578 | 0.007033 | 0.036265 | -0.005985 | 0.028846 | 61.592 | 0.18453 | 61.5141 | -0.046838 | 0.025345 | 61.5753 | -0.010593 | 61.3672 | 61.5125 | 61.4463 | 61.4611 | 61.4847 | 61.5139 | 61.4717 | 61.5065 | 123.0697 | 61.6622 | 122.9918 | 61.4308 | 61.503 | 123.053 | 61.4671 | 122.8449 | 61.5667 | 61.6026 | 61.4888 | 61.5247
1369.0625 | 123.468 | -61.441 | 61.6928 | 0.030283 | -0.031363 | -0.007421 | 0.007033 | 0.031687 | 0.003172 | 0.028846 | 61.592 | 0.19369 | 61.5004 | -0.046838 | 0.034501 | 61.5799 | -0.006014 | 61.3718 | 61.4713 | 61.4097 | 61.4336 | 61.4481 | 61.4727 | 61.4442 | 61.4699 | 123.0331 | 61.6347 | 122.9414 | 61.3942 | 61.4755 | 123.0209 | 61.435 | 122.8129 | 61.5575 | 61.5981 | 61.4659 | 61.5064
1370.0625 | 123.3078 | -61.4777 | 61.6104 | 0.025705 | -0.026784 | -0.016578 | -0.002124 | 0.036265 | -0.005985 | 0.033424 | 61.5875 | 0.18911 | 61.4912 | -0.046838 | 0.029923 | 61.5799 | -0.010593 | 61.3672 | 61.5034 | 61.4509 | 61.4611 | 61.4755 | 61.5139 | 61.4717 | 61.5111 | 123.0651 | 61.6668 | 122.9689 | 61.4308 | 61.5076 | 123.0576 | 61.4671 | 122.8449 | 61.5575 | 61.5981 | 61.4613 | 61.5018
1371.0625 | 123.3719 | -61.4777 | 61.5921 | 0.030283 | -0.026784 | -0.016578 | 0.007033 | 0.027109 | -0.001406 | 0.033424 | 61.592 | 0.19369 | 61.5324 | -0.055996 | 0.025345 | 61.5753 | -0.006014 | 61.3672 | 61.5079 | 61.4509 | 61.4611 | 61.4847 | 61.5048 | 61.4763 | 61.5111 | 123.0697 | 61.6713 | 123.0101 | 61.4217 | 61.503 | 123.053 | 61.4716 | 122.8449 | 61.5667 | 61.5981 | 61.5071 | 61.5385
1372.0625 | 123.3215 | -61.4914 | 61.615 | 0.021127 | -0.026784 | -0.016578 | 0.002454 | 0.031687 | -0.001406 | 0.038003 | 61.5966 | 0.18911 | 61.5279 | -0.051417 | 0.029923 | 61.5753 | -0.006014 | 61.3718 | 61.5125 | 61.4646 | 61.4748 | 61.4938 | 61.5231 | 61.49 | 61.5294 | 123.088 | 61.6805 | 123.0193 | 61.44 | 61.5213 | 123.0667 | 61.4854 | 122.8632 | 61.5667 | 61.6026 | 61.4979 | 61.5339
1373.0625 | 123.381 | -61.4639 | 61.6333 | 0.030283 | -0.040521 | -0.016578 | 0.011611 | 0.031687 | 0.003172 | 0.028846 | 61.592 | 0.19827 | 61.5004 | -0.051417 | 0.025345 | 61.5799 | -0.006014 | 61.3672 | 61.4942 | 61.4234 | 61.4474 | 61.4755 | 61.4956 | 61.4671 | 61.4928 | 123.056 | 61.6622 | 122.9643 | 61.4125 | 61.4893 | 123.0438 | 61.4579 | 122.8312 | 61.5667 | 61.5981 | 61.4751 | 61.5064
1374.0625 | 123.2758 | -61.4731 | 61.6653 | 0.030283 | -0.026784 | -0.016578 | 0.011611 | 0.031687 | -0.005985 | 0.028846 | 61.5966 | 0.19369 | 61.5096 | -0.051417 | 0.029923 | 61.5799 | -0.006014 | 61.3764 | 61.5034 | 61.4463 | 61.4565 | 61.4847 | 61.5048 | 61.4671 | 61.5019 | 123.0697 | 61.6668 | 122.9826 | 61.4217 | 61.503 | 123.053 | 61.4671 | 122.8495 | 61.5667 | 61.6026 | 61.4796 | 61.5156
1375.0625 | 123.3124 | -61.4868 | 61.6196 | 0.034862 | -0.031363 | -0.012 | 0.007033 | 0.031687 | -0.005985 | 0.033424 | 61.6012 | 0.19369 | 61.537 | -0.051417 | 0.020767 | 61.5753 | -0.006014 | 61.3856 | 61.5217 | 61.4555 | 61.4748 | 61.4938 | 61.5185 | 61.4808 | 61.5202 | 123.088 | 61.6805 | 123.0238 | 61.4354 | 61.5076 | 123.0621 | 61.4808 | 122.8724 | 61.5804 | 61.6072 | 61.5163 | 61.543
1376.0625 | 123.3673 | -61.4822 | 61.5967 | 0.025705 | -0.031363 | -0.016578 | 0.007033 | 0.040843 | -0.005985 | 0.024268 | 61.5966 | 0.19827 | 61.4958 | -0.051417 | 0.025345 | 61.5799 | -0.006014 | 61.3764 | 61.5079 | 61.4509 | 61.4657 | 61.4893 | 61.5231 | 61.4763 | 61.5065 | 123.0789 | 61.6805 | 122.9781 | 61.4308 | 61.5076 | 123.0621 | 61.4762 | 122.8586 | 61.5713 | 61.6026 | 61.4705 | 61.5018
1377.0625 | 123.3215 | -61.4731 | 61.5921 | 0.034862 | -0.031363 | -0.012 | 0.007033 | 0.036265 | 0.003172 | 0.033424 | 61.5966 | 0.19827 | 61.5279 | -0.042259 | 0.016188 | 61.5799 | -0.006014 | 61.3718 | 61.5079 | 61.4417 | 61.4611 | 61.4801 | 61.5093 | 61.4763 | 61.5065 | 123.0697 | 61.6713 | 123.001 | 61.4308 | 61.4893 | 123.053 | 61.4671 | 122.8449 | 61.5804 | 61.6026 | 61.5117 | 61.5339
1378.0625 | 123.3582 | -61.4639 | 61.6287 | 0.030283 | -0.035942 | -0.016578 | 0.007033 | 0.040843 | -0.005985 | 0.033424 | 61.5966 | 0.19369 | 61.5279 | -0.042259 | 0.034501 | 61.5753 | -0.006014 | 61.3856 | 61.4942 | 61.428 | 61.4474 | 61.471 | 61.5048 | 61.4579 | 61.4974 | 123.0605 | 61.6576 | 122.9918 | 61.4217 | 61.4984 | 123.0392 | 61.4579 | 122.8495 | 61.5621 | 61.6026 | 61.4934 | 61.5339
1379.0625 | 123.262 | -61.4731 | 61.6745 | 0.034862 | -0.031363 | -0.007421 | 0.007033 | 0.036265 | -0.001406 | 0.033424 | 61.5966 | 0.19369 | 61.4912 | -0.046838 | 0.029923 | 61.5753 | -0.010593 | 61.381 | 61.5079 | 61.4417 | 61.4657 | 61.4801 | 61.5093 | 61.4717 | 61.5065 | 123.0697 | 61.6668 | 122.9643 | 61.4262 | 61.503 | 123.0484 | 61.4625 | 122.8541 | 61.5667 | 61.6072 | 61.4613 | 61.5018
1380.0625 | 123.3948 | -61.4365 | 61.615 | 0.030283 | -0.040521 | -0.021157 | 0.007033 | 0.040843 | -0.005985 | 0.033424 | 61.5966 | 0.18911 | 61.537 | -0.051417 | 0.029923 | 61.5845 | -0.006014 | 61.3764 | 61.4667 | 61.3959 | 61.4153 | 61.4435 | 61.4773 | 61.4305 | 61.4699 | 123.0331 | 61.6256 | 122.9735 | 61.385 | 61.4664 | 123.0209 | 61.4304 | 122.8129 | 61.5667 | 61.6026 | 61.5071 | 61.543
1381.0625 | 123.3948 | -61.4777 | 61.6058 | 0.030283 | -0.031363 | -0.016578 | 0.011611 | 0.031687 | -0.005985 | 0.028846 | 61.6058 | 0.19369 | 61.5187 | -0.046838 | 0.025345 | 61.5753 | -0.006014 | 61.3764 | 61.5079 | 61.4463 | 61.4611 | 61.4893 | 61.5093 | 61.4717 | 61.5065 | 123.0834 | 61.6713 | 122.9964 | 61.4308 | 61.503 | 123.053 | 61.4716 | 122.8541 | 61.5804 | 61.6118 | 61.4934 | 61.5247
1382.0625 | 123.3856 | -61.5005 | 61.6241 | 0.034862 | -0.026784 | -0.016578 | 0.007033 | 0.031687 | 0.003172 | 0.033424 | 61.5966 | 0.18911 | 61.4958 | -0.042259 | 0.029923 | 61.5753 | -0.006014 | 61.3718 | 61.5354 | 61.4738 | 61.484 | 61.5076 | 61.5322 | 61.5037 | 61.534 | 123.0972 | 61.6897 | 122.9964 | 61.4583 | 61.5305 | 123.0759 | 61.4945 | 122.8724 | 61.5667 | 61.6026 | 61.4659 | 61.5018
1383.0625 | 123.2712 | -61.4868 | 61.6333 | 0.03944 | -0.026784 | -0.016578 | -0.002124 | 0.036265 | 0.003172 | 0.033424 | 61.5966 | 0.19827 | 61.4912 | -0.051417 | 0.016188 | 61.5753 | -0.006014 | 61.3764 | 61.5263 | 61.46 | 61.4702 | 61.4847 | 61.5231 | 61.49 | 61.5202 | 123.0834 | 61.6851 | 122.9781 | 61.4354 | 61.503 | 123.0621 | 61.4808 | 122.8632 | 61.5804 | 61.6026 | 61.4751 | 61.4973
1384.0625 | 123.381 | -61.4502 | 61.6058 | 0.034862 | -0.026784 | -0.016578 | 0.011611 | 0.031687 | -0.005985 | 0.033424 | 61.6058 | 0.19369 | 61.5416 | -0.042259 | 0.025345 | 61.5799 | -0.001436 | 61.381 | 61.4851 | 61.4234 | 61.4336 | 61.4618 | 61.4819 | 61.4442 | 61.4836 | 123.056 | 61.6439 | 122.9918 | 61.4079 | 61.4755 | 123.0301 | 61.4488 | 122.8312 | 61.5804 | 61.6072 | 61.5163 | 61.543
1385.0625 | 123.4085 | -61.4365 | 61.615 | 0.03944 | -0.031363 | -0.012 | -0.002124 | 0.036265 | -0.001406 | 0.038003 | 61.6058 | 0.19827 | 61.5324 | -0.051417 | 0.020767 | 61.5799 | -0.006014 | 61.3718 | 61.4759 | 61.4051 | 61.4245 | 61.4343 | 61.4727 | 61.4351 | 61.4745 | 123.0422 | 61.6347 | 122.9689 | 61.385 | 61.4572 | 123.0164 | 61.4304 | 122.8083 | 61.585 | 61.6118 | 61.5117 | 61.5385
1386.0625 | 123.4039 | -61.4777 | 61.6287 | 0.025705 | -0.035942 | -0.012 | 0.002454 | 0.040843 | -0.001406 | 0.028846 | 61.6058 | 0.19369 | 61.4867 | -0.042259 | 0.025345 | 61.5753 | 0.003143 | 61.3764 | 61.5034 | 61.4417 | 61.4657 | 61.4801 | 61.5185 | 61.4763 | 61.5065 | 123.0834 | 61.6713 | 122.9643 | 61.4354 | 61.503 | 123.053 | 61.4808 | 122.8541 | 61.5804 | 61.6026 | 61.4613 | 61.4835
1387.0625 | 123.4222 | -61.441 | 61.6104 | 0.025705 | -0.026784 | -0.016578 | 0.007033 | 0.031687 | 0.00775 | 0.033424 | 61.6012 | 0.19369 | 61.4912 | -0.046838 | 0.029923 | 61.5753 | -0.006014 | 61.3672 | 61.4667 | 61.4143 | 61.4245 | 61.4481 | 61.4727 | 61.4488 | 61.4745 | 123.0422 | 61.6347 | 122.9323 | 61.3942 | 61.471 | 123.0164 | 61.435 | 122.8083 | 61.5713 | 61.6072 | 61.4613 | 61.4973
1388.0625 | 123.3124 | -61.4685 | 61.6379 | 0.025705 | -0.035942 | -0.021157 | 0.002454 | 0.036265 | 0.00775 | 0.038003 | 61.5966 | 0.19827 | 61.5279 | -0.042259 | 0.020767 | 61.5753 | -0.006014 | 61.381 | 61.4942 | 61.4326 | 61.4473 | 61.471 | 61.5048 | 61.4763 | 61.5065 | 123.0651 | 61.6668 | 122.9964 | 61.4262 | 61.4893 | 123.0438 | 61.4625 | 122.8495 | 61.5759 | 61.6026 | 61.5071 | 61.5339
1389.0625 | 123.2483 | -61.4731 | 61.6791 | 0.034862 | -0.031363 | -0.012 | 0.007033 | 0.036265 | 0.003172 | 0.038003 | 61.6058 | 0.19827 | 61.537 | -0.046838 | 0.029923 | 61.5707 | -0.001436 | 61.3856 | 61.5079 | 61.4417 | 61.4611 | 61.4801 | 61.5093 | 61.4763 | 61.5111 | 123.0789 | 61.6713 | 123.0101 | 61.4262 | 61.503 | 123.0438 | 61.4716 | 122.8586 | 61.5759 | 61.6072 | 61.5071 | 61.5385
1390.0625 | 123.381 | -61.4822 | 61.6241 | 0.030283 | -0.026784 | -0.012 | 0.007033 | 0.027109 | -0.001406 | 0.024268 | 61.6104 | 0.19827 | 61.4867 | -0.042259 | 0.025345 | 61.5799 | -0.006014 | 61.3718 | 61.5125 | 61.4555 | 61.4702 | 61.4893 | 61.5093 | 61.4808 | 61.5065 | 123.0926 | 61.6805 | 122.9689 | 61.44 | 61.5076 | 123.0621 | 61.4762 | 122.8541 | 61.585 | 61.6164 | 61.4613 | 61.4927
1391.0625 | 123.3627 | -61.4731 | 61.6013 | 0.03944 | -0.031363 | -0.021157 | 0.002454 | 0.022531 | 0.003172 | 0.028846 | 61.5966 | 0.19827 | 61.4912 | -0.042259 | 0.029923 | 61.5799 | -0.006014 | 61.3764 | 61.5125 | 61.4417 | 61.4519 | 61.4755 | 61.4956 | 61.4763 | 61.5019 | 123.0697 | 61.6713 | 122.9643 | 61.4308 | 61.503 | 123.053 | 61.4671 | 122.8495 | 61.5667 | 61.6026 | 61.4613 | 61.4973
1392.0625 | 123.381 | -61.441 | 61.647 | 0.034862 | -0.035942 | -0.016578 | 0.002454 | 0.036265 | 0.003172 | 0.038003 | 61.6104 | 0.20284 | 61.5233 | -0.046838 | 0.025345 | 61.5753 | -0.001436 | 61.381 | 61.4759 | 61.4051 | 61.4245 | 61.4435 | 61.4773 | 61.4442 | 61.479 | 123.0514 | 61.6439 | 122.9643 | 61.3942 | 61.4664 | 123.0164 | 61.4396 | 122.822 | 61.585 | 61.6118 | 61.4979 | 61.5247
1393.0625 | 123.262 | -61.4914 | 61.6974 | 0.025705 | -0.035942 | -0.012 | 0.011611 | 0.036265 | 0.003172 | 0.033424 | 61.6012 | 0.19369 | 61.537 | -0.051417 | 0.020767 | 61.5753 | -0.006014 | 61.3764 | 61.5171 | 61.4555 | 61.4794 | 61.503 | 61.5277 | 61.4946 | 61.5248 | 123.0926 | 61.6851 | 123.0284 | 61.44 | 61.5122 | 123.0667 | 61.4854 | 122.8678 | 61.5804 | 61.6072 | 61.5163 | 61.543
1394.0625 | 123.2895 | -61.5005 | 61.6653 | 0.034862 | -0.026784 | -0.012 | 0.007033 | 0.036265 | 0.003172 | 0.033424 | 61.6058 | 0.19369 | 61.4912 | -0.03768 | 0.025345 | 61.5845 | -0.006014 | 61.3764 | 61.5354 | 61.4738 | 61.4885 | 61.5076 | 61.5368 | 61.5037 | 61.534 | 123.1063 | 61.6942 | 122.9918 | 61.4629 | 61.5259 | 123.085 | 61.4945 | 122.8769 | 61.5804 | 61.6118 | 61.4659 | 61.4973
1395.0625 | 123.3902 | -61.4685 | 61.6287 | 0.030283 | -0.026784 | -0.021157 | 0.007033 | 0.036265 | -0.005985 | 0.028846 | 61.592 | 0.19369 | 61.4867 | -0.042259 | 0.029923 | 61.5753 | -0.006014 | 61.3764 | 61.4988 | 61.4417 | 61.4473 | 61.4755 | 61.5048 | 61.4625 | 61.4974 | 123.0605 | 61.6622 | 122.9552 | 61.4262 | 61.4984 | 123.0438 | 61.4625 | 122.8449 | 61.5621 | 61.5981 | 61.4567 | 61.4927
1396.0625 | 123.317 | -61.4685 | 61.6608 | 0.030283 | -0.035942 | -0.016578 | -0.002124 | 0.031687 | -0.001406 | 0.033424 | 61.6012 | 0.19827 | 61.5324 | -0.046838 | 0.029923 | 61.5753 | -0.006014 | 61.381 | 61.4988 | 61.4326 | 61.4519 | 61.4664 | 61.5002 | 61.4671 | 61.5019 | 123.0697 | 61.6668 | 123.001 | 61.4217 | 61.4984 | 123.0438 | 61.4625 | 122.8495 | 61.5713 | 61.6072 | 61.5025 | 61.5385
1397.0625 | 123.3902 | -61.4639 | 61.6425 | 0.030283 | -0.031363 | -0.016578 | 0.011611 | 0.031687 | -0.001406 | 0.038003 | 61.6104 | 0.19827 | 61.537 | -0.042259 | 0.029923 | 61.5753 | -0.006014 | 61.381 | 61.4942 | 61.4326 | 61.4474 | 61.4755 | 61.4956 | 61.4625 | 61.5019 | 123.0743 | 61.6622 | 123.001 | 61.4217 | 61.4939 | 123.0392 | 61.4579 | 122.8449 | 61.5804 | 61.6164 | 61.5071 | 61.543
1398.0625 | 123.4222 | -61.4548 | 61.6196 | 0.030283 | -0.035942 | -0.012 | 0.002454 | 0.031687 | -0.001406 | 0.038003 | 61.592 | 0.19827 | 61.4867 | -0.046838 | 0.029923 | 61.5799 | -0.001436 | 61.381 | 61.4851 | 61.4188 | 61.4428 | 61.4572 | 61.4865 | 61.4534 | 61.4928 | 123.0468 | 61.653 | 122.9414 | 61.4079 | 61.4847 | 123.0347 | 61.4533 | 122.8357 | 61.5621 | 61.5935 | 61.4567 | 61.4881
1399.0625 | 123.2986 | -61.5005 | 61.6287 | 0.030283 | -0.031363 | -0.016578 | 0.011611 | 0.040843 | 0.003172 | 0.033424 | 61.5966 | 0.18453 | 61.4912 | -0.042259 | 0.020767 | 61.5799 | -0.001436 | 61.3718 | 61.5308 | 61.4692 | 61.484 | 61.5122 | 61.5414 | 61.5037 | 61.534 | 123.0972 | 61.6851 | 122.9918 | 61.4583 | 61.5213 | 123.0804 | 61.4991 | 122.8724 | 61.5759 | 61.5981 | 61.4705 | 61.4927
1400.0625 | 123.3948 | -61.4502 | 61.6196 | 0.025705 | -0.035942 | -0.021157 | 0.002454 | 0.045421 | 0.003172 | 0.042581 | 61.5966 | 0.18911 | 61.5324 | -0.042259 | 0.029923 | 61.5753 | -0.006014 | 61.381 | 61.4759 | 61.4143 | 61.429 | 61.4526 | 61.4956 | 61.4534 | 61.4928 | 123.0468 | 61.6393 | 122.9826 | 61.4079 | 61.4801 | 123.0255 | 61.4442 | 122.8312 | 61.5667 | 61.6026 | 61.5025 | 61.5385
1401.0625 | 123.3627 | -61.4594 | 61.6516 | 0.025705 | -0.031363 | -0.012 | 0.002454 | 0.036265 | -0.001406 | 0.033424 | 61.6012 | 0.19827 | 61.5324 | -0.03768 | 0.025345 | 61.5753 | -0.006014 | 61.381 | 61.4851 | 61.428 | 61.4474 | 61.4618 | 61.4956 | 61.4579 | 61.4928 | 123.0606 | 61.6576 | 122.9918 | 61.4217 | 61.4847 | 123.0347 | 61.4533 | 122.8403 | 61.5759 | 61.6072 | 61.5071 | 61.5385
1402.0625 | 123.3307 | -61.4548 | 61.6425 | 0.030283 | -0.035942 | -0.012 | 0.011611 | 0.036265 | -0.001406 | 0.028846 | 61.5966 | 0.20284 | 61.4912 | -0.042259 | 0.025345 | 61.5753 | -0.006014 | 61.381 | 61.4851 | 61.4188 | 61.4428 | 61.4664 | 61.491 | 61.4534 | 61.4836 | 123.0514 | 61.6576 | 122.946 | 61.4125 | 61.4801 | 123.0301 | 61.4488 | 122.8357 | 61.5713 | 61.6026 | 61.4659 | 61.4973
1403.0625 | 123.3078 | -61.4685 | 61.6379 | 0.030283 | -0.031363 | -0.012 | 0.007033 | 0.036265 | 0.003172 | 0.024268 | 61.592 | 0.19827 | 61.4958 | -0.042259 | 0.025345 | 61.5753 | -0.006014 | 61.3856 | 61.4988 | 61.4371 | 61.4565 | 61.4755 | 61.5048 | 61.4717 | 61.4928 | 123.0605 | 61.6668 | 122.9643 | 61.4262 | 61.4939 | 123.0438 | 61.4625 | 122.8541 | 61.5667 | 61.5981 | 61.4705 | 61.5018
1404.0625 | 123.2941 | -61.4822 | 61.6379 | 0.034862 | -0.031363 | -0.012 | 0.007033 | 0.036265 | -0.001406 | 0.042581 | 61.6058 | 0.18911 | 61.5416 | -0.042259 | 0.020767 | 61.5845 | -0.010593 | 61.381 | 61.5171 | 61.4509 | 61.4702 | 61.4893 | 61.5185 | 61.4808 | 61.5248 | 123.088 | 61.6713 | 123.0238 | 61.44 | 61.503 | 123.0667 | 61.4716 | 122.8632 | 61.585 | 61.6164 | 61.5208 | 61.5522
1405.0625 | 123.3444 | -61.4594 | 61.6562 | 0.016548 | -0.035942 | -0.012 | 0.002454 | 0.036265 | -0.001406 | 0.038003 | 61.592 | 0.19369 | 61.4912 | -0.046838 | 0.020767 | 61.5753 | -0.010593 | 61.3764 | 61.4759 | 61.4234 | 61.4474 | 61.4618 | 61.4956 | 61.4579 | 61.4974 | 123.0514 | 61.653 | 122.9506 | 61.4125 | 61.4801 | 123.0347 | 61.4488 | 122.8357 | 61.5713 | 61.6026 | 61.4705 | 61.5018
1406.0625 | 123.2346 | -61.4731 | 61.6882 | 0.030283 | -0.035942 | -0.007421 | 0.011611 | 0.040843 | 0.003172 | 0.038003 | 61.6058 | 0.19827 | 61.5004 | -0.046838 | 0.029923 | 61.5799 | -0.006014 | 61.381 | 61.5034 | 61.4371 | 61.4657 | 61.4847 | 61.5139 | 61.4763 | 61.5111 | 123.0789 | 61.6713 | 122.9735 | 61.4262 | 61.503 | 123.053 | 61.4671 | 122.8541 | 61.5759 | 61.6118 | 61.4705 | 61.5064
1407.0625 | 123.2849 | -61.4822 | 61.6745 | 0.034862 | -0.035942 | -0.007421 | -0.002124 | 0.031687 | 0.003172 | 0.024268 | 61.6104 | 0.18911 | 61.5416 | -0.046838 | 0.029923 | 61.5753 | -0.006014 | 61.3764 | 61.5171 | 61.4463 | 61.4748 | 61.4801 | 61.5139 | 61.4854 | 61.5065 | 123.0926 | 61.6713 | 123.0238 | 61.4354 | 61.5122 | 123.0576 | 61.4762 | 122.8586 | 61.5804 | 61.6164 | 61.5117 | 61.5476
1408.0625 | 123.2758 | -61.4822 | 61.6653 | 0.030283 | -0.031363 | -0.021157 | 0.007033 | 0.036265 | 0.003172 | 0.038003 | 61.6012 | 0.18911 | 61.4912 | -0.051417 | 0.029923 | 61.5845 | -0.001436 | 61.3764 | 61.5125 | 61.4509 | 61.4611 | 61.4893 | 61.5185 | 61.4854 | 61.5202 | 123.0834 | 61.6713 | 122.9735 | 61.4308 | 61.5122 | 123.0667 | 61.4808 | 122.8586 | 61.5713 | 61.6026 | 61.4613 | 61.4927
1409.0625 | 123.2437 | -61.5189 | 61.6516 | 0.034862 | -0.026784 | -0.007421 | 0.007033 | 0.036265 | 0.003172 | 0.042581 | 61.6012 | 0.19369 | 61.537 | -0.046838 | 0.029923 | 61.5845 | -0.010593 | 61.3718 | 61.5537 | 61.4921 | 61.5114 | 61.5259 | 61.5551 | 61.522 | 61.5614 | 123.1201 | 61.7125 | 123.0559 | 61.472 | 61.5488 | 123.1033 | 61.5083 | 122.8907 | 61.5713 | 61.6118 | 61.5071 | 61.5476
1410.0625 | 123.2483 | -61.4639 | 61.6791 | 0.034862 | -0.026784 | -0.021157 | 0.011611 | 0.045421 | -0.001406 | 0.042581 | 61.6104 | 0.19369 | 61.5279 | -0.051417 | 0.034501 | 61.5753 | -0.001436 | 61.3718 | 61.4988 | 61.4371 | 61.4428 | 61.4755 | 61.5093 | 61.4625 | 61.5065 | 123.0743 | 61.6576 | 122.9918 | 61.4125 | 61.4984 | 123.0392 | 61.4625 | 122.8357 | 61.5759 | 61.6118 | 61.4934 | 61.5293
1411.0625 | 123.2712 | -61.4639 | 61.6516 | 0.030283 | -0.035942 | -0.025735 | 0.002454 | 0.031687 | -0.001406 | 0.042581 | 61.592 | 0.20284 | 61.4958 | -0.046838 | 0.029923 | 61.5799 | -0.001436 | 61.3718 | 61.4942 | 61.428 | 61.4382 | 61.4664 | 61.4956 | 61.4625 | 61.5065 | 123.056 | 61.6668 | 122.9598 | 61.4171 | 61.4939 | 123.0438 | 61.4625 | 122.8357 | 61.5621 | 61.5935 | 61.4659 | 61.4973
1412.0625 | 123.2712 | -61.5005 | 61.6791 | 0.030283 | -0.026784 | -0.016578 | 0.002454 | 0.031687 | -0.001406 | 0.038003 | 61.6149 | 0.19827 | 61.537 | -0.046838 | 0.029923 | 61.5799 | -0.006014 | 61.3856 | 61.5308 | 61.4738 | 61.484 | 61.503 | 61.5322 | 61.4991 | 61.5386 | 123.1155 | 61.6988 | 123.0376 | 61.4537 | 61.5305 | 123.0804 | 61.4945 | 122.8861 | 61.585 | 61.6209 | 61.5071 | 61.543
1413.0625 | 123.2941 | -61.4868 | 61.6791 | 0.030283 | -0.031363 | -0.012 | 0.007033 | 0.027109 | 0.003172 | 0.038003 | 61.6104 | 0.19827 | 61.537 | -0.042259 | 0.025345 | 61.5753 | -0.001436 | 61.381 | 61.5171 | 61.4555 | 61.4748 | 61.4938 | 61.5139 | 61.49 | 61.5248 | 123.0972 | 61.6851 | 123.0238 | 61.4446 | 61.5122 | 123.0621 | 61.4854 | 122.8678 | 61.585 | 61.6118 | 61.5117 | 61.5385
1414.0625 | 123.2895 | -61.5051 | 61.6699 | 0.030283 | -0.026784 | -0.012 | 0.007033 | 0.031687 | -0.001406 | 0.033424 | 61.5966 | 0.19369 | 61.5096 | -0.046838 | 0.034501 | 61.5753 | -0.006014 | 61.3672 | 61.5354 | 61.4783 | 61.4931 | 61.5122 | 61.5368 | 61.5037 | 61.5386 | 123.1017 | 61.6988 | 123.0147 | 61.4583 | 61.5396 | 123.0804 | 61.4991 | 122.8724 | 61.5621 | 61.6026 | 61.4751 | 61.5156
1415.0625 | 123.3215 | -61.4639 | 61.6653 | 0.034862 | -0.017627 | -0.012 | 0.007033 | 0.031687 | -0.001406 | 0.038003 | 61.5966 | 0.19369 | 61.505 | -0.051417 | 0.020767 | 61.5799 | -0.006014 | 61.3718 | 61.4988 | 61.4463 | 61.4519 | 61.471 | 61.4956 | 61.4625 | 61.5019 | 123.0605 | 61.6576 | 122.9689 | 61.4125 | 61.4847 | 123.0438 | 61.4579 | 122.8357 | 61.5759 | 61.6026 | 61.4842 | 61.511
1416.0625 | 123.2712 | -61.4868 | 61.6699 | 0.025705 | -0.031363 | -0.002842 | 0.011611 | 0.040843 | 0.003172 | 0.042581 | 61.6058 | 0.18911 | 61.537 | -0.051417 | 0.034501 | 61.5753 | -0.010593 | 61.3718 | 61.5125 | 61.4555 | 61.484 | 61.4984 | 61.5277 | 61.49 | 61.5294 | 123.0926 | 61.6759 | 123.0238 | 61.4354 | 61.5213 | 123.0621 | 61.4762 | 122.8586 | 61.5713 | 61.6164 | 61.5025 | 61.5476
1417.0625 | 123.2803 | -61.4822 | 61.6745 | 0.030283 | -0.031363 | -0.007421 | 0.011611 | 0.036265 | -0.005985 | 0.033424 | 61.6058 | 0.19827 | 61.537 | -0.051417 | 0.029923 | 61.5707 | -0.001436 | 61.3764 | 61.5125 | 61.4509 | 61.4748 | 61.4939 | 61.5185 | 61.4763 | 61.5157 | 123.088 | 61.6805 | 123.0193 | 61.4308 | 61.5122 | 123.053 | 61.4808 | 122.8586 | 61.5759 | 61.6072 | 61.5071 | 61.5385
1418.0625 | 123.2895 | -61.4868 | 61.6928 | 0.025705 | -0.035942 | -0.012 | 0.011611 | 0.031687 | -0.001406 | 0.038003 | 61.6058 | 0.19369 | 61.5096 | -0.051417 | 0.029923 | 61.5707 | -0.006014 | 61.3764 | 61.5125 | 61.4509 | 61.4748 | 61.4984 | 61.5185 | 61.4854 | 61.5248 | 123.0926 | 61.6805 | 122.9964 | 61.4354 | 61.5167 | 123.0576 | 61.4808 | 122.8632 | 61.5759 | 61.6118 | 61.4796 | 61.5156
1419.0625 | 123.2529 | -61.5051 | 61.6653 | 0.030283 | -0.022205 | -0.016578 | 0.007033 | 0.031687 | -0.001406 | 0.042581 | 61.6058 | 0.19827 | 61.5096 | -0.051417 | 0.020767 | 61.5799 | -0.006014 | 61.3764 | 61.5354 | 61.4829 | 61.4885 | 61.5122 | 61.5368 | 61.5037 | 61.5477 | 123.1109 | 61.7034 | 123.0147 | 61.4537 | 61.5259 | 123.085 | 61.4991 | 122.8815 | 61.585 | 61.6118 | 61.4888 | 61.5156
1420.0625 | 123.2758 | -61.4868 | 61.6608 | 0.030283 | -0.026784 | -0.007421 | 0.007033 | 0.036265 | -0.001406 | 0.042581 | 61.6058 | 0.19369 | 61.537 | -0.046838 | 0.029923 | 61.5845 | -0.006014 | 61.3718 | 61.5171 | 61.46 | 61.4794 | 61.4938 | 61.5231 | 61.4854 | 61.5294 | 123.0926 | 61.6805 | 123.0238 | 61.44 | 61.5167 | 123.0713 | 61.4808 | 122.8586 | 61.5759 | 61.6118 | 61.5071 | 61.543
1421.0625 | 123.2803 | -61.4822 | 61.6562 | 0.030283 | -0.026784 | -0.012 | 0.007033 | 0.031687 | 0.003172 | 0.038003 | 61.6104 | 0.19827 | 61.5416 | -0.042259 | 0.034501 | 61.5845 | -0.006014 | 61.3764 | 61.5125 | 61.4555 | 61.4702 | 61.4893 | 61.5139 | 61.4854 | 61.5202 | 123.0926 | 61.6805 | 123.0238 | 61.44 | 61.5167 | 123.0667 | 61.4762 | 122.8586 | 61.5759 | 61.6164 | 61.5071 | 61.5476
1422.0625 | 123.3032 | -61.4548 | 61.6699 | 0.03944 | -0.031363 | -0.016578 | 0.011611 | 0.040843 | 0.003172 | 0.038003 | 61.5966 | 0.19369 | 61.5141 | -0.042259 | 0.034501 | 61.5845 | -0.006014 | 61.3764 | 61.4942 | 61.4234 | 61.4382 | 61.4664 | 61.4956 | 61.4579 | 61.4928 | 123.0514 | 61.6485 | 122.9689 | 61.4125 | 61.4893 | 123.0392 | 61.4488 | 122.8312 | 61.5621 | 61.6026 | 61.4796 | 61.5202
1423.0625 | 123.3215 | -61.4868 | 61.6379 | 0.034862 | -0.035942 | -0.016578 | 0.007033 | 0.036265 | -0.005985 | 0.033424 | 61.6012 | 0.18911 | 61.5004 | -0.046838 | 0.020767 | 61.5799 | -0.001436 | 61.3764 | 61.5217 | 61.4509 | 61.4702 | 61.4938 | 61.5231 | 61.4808 | 61.5202 | 123.088 | 61.6759 | 122.9872 | 61.44 | 61.5076 | 123.0667 | 61.4854 | 122.8632 | 61.5804 | 61.6026 | 61.4796 | 61.5018
1424.0625 | 123.3215 | -61.4914 | 61.6425 | 0.034862 | -0.035942 | -0.021157 | 0.002454 | 0.036265 | 0.003172 | 0.033424 | 61.5966 | 0.19827 | 61.537 | -0.046838 | 0.020767 | 61.5799 | -0.015171 | 61.3718 | 61.5263 | 61.4555 | 61.4702 | 61.4938 | 61.5277 | 61.4946 | 61.5248 | 123.088 | 61.6897 | 123.0284 | 61.4446 | 61.5122 | 123.0713 | 61.4762 | 122.8632 | 61.5759 | 61.6118 | 61.5163 | 61.5522
1425.0625 | 123.2483 | -61.496 | 61.6699 | 0.021127 | -0.035942 | -0.016578 | -0.002124 | 0.036265 | 0.003172 | 0.033424 | 61.6058 | 0.19827 | 61.5096 | -0.046838 | 0.025345 | 61.5845 | -0.006014 | 61.3764 | 61.5171 | 61.46 | 61.4794 | 61.4938 | 61.5322 | 61.4991 | 61.5294 | 123.1017 | 61.6942 | 123.0055 | 61.4491 | 61.5213 | 123.0804 | 61.49 | 122.8724 | 61.5804 | 61.6118 | 61.4842 | 61.5156
1426.0625 | 123.3261 | -61.496 | 61.6608 | 0.034862 | -0.035942 | -0.016578 | 0.002454 | 0.040843 | 0.00775 | 0.033424 | 61.6149 | 0.19827 | 61.505 | -0.046838 | 0.025345 | 61.5845 | -0.010593 | 61.3672 | 61.5308 | 61.46 | 61.4794 | 61.4984 | 61.5368 | 61.5037 | 61.5294 | 123.1109 | 61.6942 | 123.001 | 61.4491 | 61.5213 | 123.0804 | 61.4854 | 122.8632 | 61.5896 | 61.6255 | 61.4796 | 61.5156
1427.0625 | 123.2941 | -61.4731 | 61.6608 | 0.025705 | -0.031363 | -0.007421 | 0.007033 | 0.040843 | 0.003172 | 0.038003 | 61.6058 | 0.19827 | 61.5324 | -0.042259 | 0.025345 | 61.5845 | -0.010593 | 61.3764 | 61.4988 | 61.4417 | 61.4657 | 61.4801 | 61.5139 | 61.4763 | 61.5111 | 123.0789 | 61.6713 | 123.0055 | 61.4308 | 61.4984 | 123.0576 | 61.4625 | 122.8495 | 61.5804 | 61.6164 | 61.5071 | 61.543
1428.0625 | 123.3215 | -61.4731 | 61.6333 | 0.034862 | -0.031363 | -0.007421 | 0.002454 | 0.036265 | 0.003172 | 0.038003 | 61.592 | 0.20284 | 61.5096 | -0.03768 | 0.029923 | 61.5799 | -0.010593 | 61.3764 | 61.5079 | 61.4417 | 61.4657 | 61.4755 | 61.5093 | 61.4763 | 61.5111 | 123.0651 | 61.6759 | 122.9826 | 61.4354 | 61.503 | 123.053 | 61.4625 | 122.8495 | 61.5621 | 61.6026 | 61.4796 | 61.5202
1429.0625 | 123.3078 | -61.5143 | 61.6287 | 0.030283 | -0.031363 | -0.007421 | 0.007033 | 0.031687 | 0.003172 | 0.033424 | 61.6012 | 0.19827 | 61.505 | -0.046838 | 0.025345 | 61.5753 | -0.006014 | 61.3718 | 61.5446 | 61.4829 | 61.5069 | 61.5213 | 61.546 | 61.5175 | 61.5477 | 123.1155 | 61.7125 | 123.0193 | 61.4674 | 61.5396 | 123.0896 | 61.5083 | 122.8861 | 61.5759 | 61.6072 | 61.4796 | 61.511
1430.0625 | 123.3124 | -61.5189 | 61.6379 | 0.034862 | -0.031363 | -0.012 | 0.002454 | 0.036265 | -0.005985 | 0.033424 | 61.6058 | 0.19369 | 61.537 | -0.051417 | 0.029923 | 61.5753 | -0.010593 | 61.3764 | 61.5537 | 61.4875 | 61.5069 | 61.5213 | 61.5551 | 61.5129 | 61.5523 | 123.1246 | 61.7125 | 123.0559 | 61.4674 | 61.5488 | 123.0942 | 61.5083 | 122.8953 | 61.5759 | 61.6164 | 61.5071 | 61.5476
1431.0625 | 123.2941 | -61.4868 | 61.6562 | 0.034862 | -0.031363 | -0.002842 | 0.007033 | 0.036265 | 0.003172 | 0.038003 | 61.6012 | 0.20284 | 61.505 | -0.042259 | 0.029923 | 61.5753 | -0.001436 | 61.3672 | 61.5217 | 61.4555 | 61.484 | 61.4938 | 61.5231 | 61.49 | 61.5248 | 123.088 | 61.6897 | 122.9918 | 61.4446 | 61.5167 | 123.0621 | 61.4854 | 122.8541 | 61.5713 | 61.6026 | 61.4751 | 61.5064
1432.0625 | 123.2574 | -61.4594 | 61.6699 | 0.025705 | -0.031363 | -0.012 | 0.002454 | 0.040843 | -0.001406 | 0.038003 | 61.6058 | 0.20284 | 61.5233 | -0.042259 | 0.025345 | 61.5799 | -0.001436 | 61.381 | 61.4851 | 61.428 | 61.4474 | 61.4618 | 61.5002 | 61.4579 | 61.4974 | 123.0651 | 61.6622 | 122.9826 | 61.4171 | 61.4847 | 123.0392 | 61.4579 | 122.8403 | 61.5804 | 61.6072 | 61.4979 | 61.5247
1433.0625 | 123.2803 | -61.4777 | 61.6653 | 0.025705 | -0.031363 | -0.016578 | -0.002124 | 0.036265 | 0.003172 | 0.038003 | 61.6058 | 0.19827 | 61.5416 | -0.046838 | 0.025345 | 61.5799 | -0.006014 | 61.381 | 61.5034 | 61.4463 | 61.4611 | 61.4755 | 61.5139 | 61.4808 | 61.5157 | 123.0834 | 61.6759 | 123.0193 | 61.4308 | 61.503 | 123.0576 | 61.4716 | 122.8586 | 61.5804 | 61.6118 | 61.5163 | 61.5476
1434.0625 | 123.317 | -61.4777 | 61.6104 | 0.030283 | -0.031363 | -0.021157 | 0.002454 | 0.036265 | -0.001406 | 0.033424 | 61.6058 | 0.19369 | 61.5004 | -0.046838 | 0.025345 | 61.5799 | -0.006014 | 61.3672 | 61.5079 | 61.4463 | 61.4565 | 61.4801 | 61.5139 | 61.4763 | 61.5111 | 123.0834 | 61.6713 | 122.9781 | 61.4308 | 61.503 | 123.0576 | 61.4716 | 122.8449 | 61.5804 | 61.6118 | 61.4751 | 61.5064
1435.0625 | 123.2986 | -61.4868 | 61.6608 | 0.030283 | -0.022205 | -0.016578 | 0.011611 | 0.036265 | -0.001406 | 0.038003 | 61.6058 | 0.19827 | 61.5324 | -0.046838 | 0.034501 | 61.5799 | -0.006014 | 61.381 | 61.5171 | 61.4646 | 61.4702 | 61.4984 | 61.5231 | 61.4854 | 61.5248 | 123.0926 | 61.6851 | 123.0193 | 61.44 | 61.5213 | 123.0667 | 61.4808 | 122.8678 | 61.5713 | 61.6118 | 61.4979 | 61.5385
1436.0625 | 123.3261 | -61.4777 | 61.647 | 0.034862 | -0.035942 | -0.012 | 0.007033 | 0.036265 | 0.003172 | 0.042581 | 61.6058 | 0.19369 | 61.5279 | -0.042259 | 0.034501 | 61.5799 | -0.006014 | 61.3718 | 61.5125 | 61.4417 | 61.4657 | 61.4847 | 61.5139 | 61.4808 | 61.5202 | 123.0834 | 61.6713 | 123.0055 | 61.4354 | 61.5122 | 123.0576 | 61.4716 | 122.8495 | 61.5713 | 61.6118 | 61.4934 | 61.5339
1437.0625 | 123.2849 | -61.4594 | 61.6745 | 0.030283 | -0.031363 | -0.012 | 0.007033 | 0.031687 | -0.001406 | 0.038003 | 61.6012 | 0.19827 | 61.4958 | -0.042259 | 0.025345 | 61.5753 | -0.010593 | 61.381 | 61.4896 | 61.428 | 61.4474 | 61.4664 | 61.491 | 61.4579 | 61.4974 | 123.0606 | 61.6576 | 122.9552 | 61.4171 | 61.4847 | 123.0347 | 61.4488 | 122.8403 | 61.5759 | 61.6118 | 61.4705 | 61.5064
1438.0625 | 123.3215 | -61.4822 | 61.6425 | 0.034862 | -0.031363 | -0.012 | 0.007033 | 0.036265 | 0.003172 | 0.033424 | 61.5966 | 0.19827 | 61.4958 | -0.051417 | 0.025345 | 61.5799 | -0.001436 | 61.381 | 61.5171 | 61.4509 | 61.4702 | 61.4893 | 61.5185 | 61.4854 | 61.5157 | 123.0789 | 61.6805 | 122.9781 | 61.4308 | 61.5076 | 123.0621 | 61.4808 | 122.8632 | 61.5713 | 61.5981 | 61.4705 | 61.4973
1439.0625 | 123.23 | -61.496 | 61.647 | 0.044018 | -0.035942 | -0.012 | 0.007033 | 0.031687 | 0.00775 | 0.033424 | 61.5966 | 0.19827 | 61.537 | -0.042259 | 0.020767 | 61.5845 | -0.006014 | 61.381 | 61.54 | 61.46 | 61.484 | 61.503 | 61.5277 | 61.5037 | 61.5294 | 123.0926 | 61.6942 | 123.033 | 61.4537 | 61.5167 | 123.0804 | 61.49 | 122.8769 | 61.5759 | 61.6026 | 61.5163 | 61.543
1440.0625 | 123.3032 | -61.496 | 61.6745 | 0.025705 | -0.022205 | -0.025735 | 0.007033 | 0.031687 | -0.001406 | 0.038003 | 61.6104 | 0.19827 | 61.537 | -0.046838 | 0.029923 | 61.5662 | -0.006014 | 61.381 | 61.5217 | 61.4738 | 61.4702 | 61.503 | 61.5277 | 61.4946 | 61.534 | 123.1063 | 61.6942 | 123.033 | 61.4491 | 61.5259 | 123.0621 | 61.49 | 122.8769 | 61.5804 | 61.6164 | 61.5071 | 61.543
1441.0625 | 123.2895 | -61.4731 | 61.6653 | 0.030283 | -0.031363 | -0.012 | 0.011611 | 0.045421 | 0.003172 | 0.038003 | 61.6012 | 0.19369 | 61.4958 | -0.046838 | 0.020767 | 61.5753 | -0.010593 | 61.3764 | 61.5034 | 61.4417 | 61.4611 | 61.4847 | 61.5185 | 61.4763 | 61.5111 | 123.0743 | 61.6668 | 122.9689 | 61.4262 | 61.4939 | 123.0484 | 61.4625 | 122.8495 | 61.5804 | 61.6118 | 61.4751 | 61.5064
1442.0625 | 123.3032 | -61.4822 | 61.6974 | 0.03944 | -0.031363 | -0.007421 | 0.011611 | 0.036265 | 0.003172 | 0.028846 | 61.6012 | 0.18911 | 61.537 | -0.051417 | 0.029923 | 61.5799 | -0.010593 | 61.381 | 61.5217 | 61.4509 | 61.4748 | 61.4939 | 61.5185 | 61.4854 | 61.5111 | 123.0834 | 61.6713 | 123.0193 | 61.4308 | 61.5122 | 123.0621 | 61.4716 | 122.8632 | 61.5713 | 61.6118 | 61.5071 | 61.5476
1443.0625 | 123.2391 | -61.5005 | 61.6837 | 0.03944 | -0.022205 | -0.012 | 0.011611 | 0.031687 | 0.003172 | 0.042581 | 61.6058 | 0.19827 | 61.5141 | -0.046838 | 0.029923 | 61.5845 | -0.001436 | 61.3764 | 61.54 | 61.4783 | 61.4885 | 61.5122 | 61.5322 | 61.5037 | 61.5431 | 123.1063 | 61.6988 | 123.0147 | 61.4537 | 61.5305 | 123.085 | 61.4991 | 122.8769 | 61.5759 | 61.6072 | 61.4842 | 61.5156
1444.0625 | 123.2529 | -61.4731 | 61.6608 | 0.034862 | -0.022205 | -0.012 | 0.007033 | 0.036265 | -0.001406 | 0.033424 | 61.6058 | 0.19827 | 61.4912 | -0.051417 | 0.029923 | 61.5891 | -0.006014 | 61.3718 | 61.5079 | 61.4509 | 61.4611 | 61.4801 | 61.5093 | 61.4717 | 61.5065 | 123.0789 | 61.6713 | 122.9643 | 61.4217 | 61.503 | 123.0621 | 61.4671 | 122.8449 | 61.5759 | 61.6118 | 61.4613 | 61.4973
1445.0625 | 123.2849 | -61.4731 | 61.6653 | 0.025705 | -0.026784 | -0.012 | 0.011611 | 0.036265 | -0.001406 | 0.038003 | 61.6149 | 0.19827 | 61.5416 | -0.046838 | 0.029923 | 61.5753 | -0.006014 | 61.381 | 61.4988 | 61.4463 | 61.4611 | 61.4847 | 61.5093 | 61.4717 | 61.5111 | 123.088 | 61.6713 | 123.0147 | 61.4262 | 61.503 | 123.0484 | 61.4671 | 122.8541 | 61.585 | 61.6209 | 61.5117 | 61.5476
1446.0625 | 123.3353 | -61.441 | 61.6791 | 0.030283 | -0.031363 | -0.016578 | 0.011611 | 0.031687 | -0.001406 | 0.033424 | 61.6012 | 0.19827 | 61.5004 | -0.042259 | 0.025345 | 61.5753 | -0.006014 | 61.381 | 61.4713 | 61.4097 | 61.4245 | 61.4527 | 61.4727 | 61.4396 | 61.4745 | 123.0422 | 61.6393 | 122.9414 | 61.3988 | 61.4664 | 123.0164 | 61.435 | 122.822 | 61.5759 | 61.6072 | 61.4751 | 61.5064
1447.0625 | 123.2803 | -61.4914 | 61.6562 | 0.034862 | -0.026784 | -0.012 | 0.007033 | 0.031687 | 0.003172 | 0.033424 | 61.6058 | 0.19827 | 61.5004 | -0.046838 | 0.020767 | 61.5799 | -0.006014 | 61.381 | 61.5263 | 61.4646 | 61.4794 | 61.4984 | 61.5231 | 61.4946 | 61.5248 | 123.0972 | 61.6897 | 122.9918 | 61.4446 | 61.5122 | 123.0713 | 61.4854 | 122.8724 | 61.585 | 61.6118 | 61.4796 | 61.5064
1448.0625 | 123.2712 | -61.5005 | 61.6562 | 0.025705 | -0.022205 | -0.021157 | -0.002124 | 0.031687 | -0.001406 | 0.038003 | 61.6104 | 0.19827 | 61.537 | -0.03768 | 0.029923 | 61.5753 | -0.001436 | 61.381 | 61.5263 | 61.4783 | 61.4794 | 61.4984 | 61.5322 | 61.4991 | 61.5386 | 123.1109 | 61.6988 | 123.0376 | 61.4629 | 61.5305 | 123.0759 | 61.4991 | 122.8815 | 61.5804 | 61.6118 | 61.5071 | 61.5385
1449.0625 | 123.3032 | -61.4731 | 61.6516 | 0.044018 | -0.022205 | -0.007421 | 0.011611 | 0.040843 | 0.003172 | 0.033424 | 61.6104 | 0.19827 | 61.4958 | -0.046838 | 0.029923 | 61.5707 | -0.006014 | 61.3672 | 61.5171 | 61.4509 | 61.4657 | 61.4847 | 61.5139 | 61.4763 | 61.5065 | 123.0834 | 61.6713 | 122.9689 | 61.4262 | 61.503 | 123.0438 | 61.4671 | 122.8403 | 61.5804 | 61.6164 | 61.4659 | 61.5018
1450.0625 | 123.2758 | -61.4777 | 61.6791 | 0.034862 | -0.026784 | -0.016578 | 0.002454 | 0.036265 | -0.001406 | 0.038003 | 61.6058 | 0.19827 | 61.505 | -0.042259 | 0.029923 | 61.5799 | -0.015171 | 61.3764 | 61.5125 | 61.4509 | 61.4611 | 61.4801 | 61.5139 | 61.4763 | 61.5157 | 123.0834 | 61.6759 | 122.9826 | 61.4354 | 61.5076 | 123.0576 | 61.4625 | 122.8541 | 61.5759 | 61.6209 | 61.4751 | 61.5202
1451.0625 | 123.2941 | -61.4731 | 61.6562 | 0.030283 | -0.035942 | -0.007421 | 0.01619 | 0.036265 | -0.001406 | 0.028846 | 61.6058 | 0.19369 | 61.537 | -0.042259 | 0.025345 | 61.5707 | -0.006014 | 61.381 | 61.5034 | 61.4371 | 61.4657 | 61.4893 | 61.5093 | 61.4717 | 61.5019 | 123.0789 | 61.6668 | 123.0101 | 61.4308 | 61.4984 | 123.0438 | 61.4671 | 122.8541 | 61.5804 | 61.6118 | 61.5117 | 61.543
1452.0625 | 123.3719 | -61.4731 | 61.6241 | 0.030283 | -0.031363 | -0.016578 | 0.011611 | 0.036265 | -0.001406 | 0.028846 | 61.6012 | 0.19369 | 61.4867 | -0.03768 | 0.029923 | 61.5799 | -0.010593 | 61.3718 | 61.5034 | 61.4417 | 61.4565 | 61.4847 | 61.5093 | 61.4717 | 61.5019 | 123.0743 | 61.6668 | 122.9597 | 61.4354 | 61.503 | 123.053 | 61.4625 | 122.8449 | 61.5713 | 61.6118 | 61.4567 | 61.4973
1453.0625 | 123.4131 | -61.4456 | 61.6379 | 0.025705 | -0.031363 | -0.012 | 0.011611 | 0.027109 | -0.001406 | 0.033424 | 61.5966 | 0.19827 | 61.5096 | -0.051417 | 0.029923 | 61.5799 | -0.006014 | 61.3764 | 61.4713 | 61.4143 | 61.4336 | 61.4572 | 61.4727 | 61.4442 | 61.479 | 123.0422 | 61.6439 | 122.9552 | 61.3942 | 61.4755 | 123.0255 | 61.4396 | 122.822 | 61.5667 | 61.6026 | 61.4796 | 61.5156
1454.0625 | 123.3353 | -61.4777 | 61.6791 | 0.030283 | -0.026784 | -0.012 | 0.007033 | 0.040843 | 0.003172 | 0.038003 | 61.5966 | 0.19827 | 61.5416 | -0.046838 | 0.025345 | 61.5845 | -0.006014 | 61.381 | 61.5079 | 61.4509 | 61.4657 | 61.4847 | 61.5185 | 61.4808 | 61.5157 | 123.0743 | 61.6759 | 123.0193 | 61.4308 | 61.503 | 123.0621 | 61.4716 | 122.8586 | 61.5713 | 61.6026 | 61.5163 | 61.5476
1455.0625 | 123.3673 | -61.441 | 61.6653 | 0.034862 | -0.035942 | -0.016578 | 0.002454 | 0.036265 | -0.001406 | 0.033424 | 61.5966 | 0.19827 | 61.505 | -0.051417 | 0.025345 | 61.5799 | -0.001436 | 61.3764 | 61.4759 | 61.4051 | 61.4245 | 61.4435 | 61.4773 | 61.4396 | 61.4745 | 123.0377 | 61.6393 | 122.946 | 61.3896 | 61.4664 | 123.0209 | 61.4396 | 122.8174 | 61.5713 | 61.5981 | 61.4796 | 61.5064
1456.0625 | 123.3673 | -61.4639 | 61.6241 | 0.034862 | -0.031363 | -0.016578 | 0.007033 | 0.045421 | -0.001406 | 0.033424 | 61.5966 | 0.19827 | 61.5141 | -0.046838 | 0.029923 | 61.5662 | -0.006014 | 61.3764 | 61.4988 | 61.4326 | 61.4474 | 61.471 | 61.5093 | 61.4625 | 61.4974 | 123.0605 | 61.6622 | 122.9781 | 61.4171 | 61.4939 | 123.0301 | 61.4579 | 122.8403 | 61.5667 | 61.6026 | 61.4842 | 61.5202
1457.0625 | 123.4177 | -61.4639 | 61.5875 | 0.03944 | -0.031363 | -0.012 | 0.002454 | 0.031687 | 0.003172 | 0.028846 | 61.6058 | 0.19827 | 61.537 | -0.03768 | 0.020767 | 61.5753 | -0.010593 | 61.381 | 61.5034 | 61.4326 | 61.4519 | 61.4664 | 61.4956 | 61.4671 | 61.4928 | 123.0697 | 61.6622 | 123.001 | 61.4262 | 61.4847 | 123.0392 | 61.4533 | 122.8449 | 61.585 | 61.6164 | 61.5163 | 61.5476
1458.0625 | 123.3765 | -61.4548 | 61.647 | 0.030283 | -0.031363 | -0.016578 | 0.002454 | 0.031687 | -0.001406 | 0.038003 | 61.592 | 0.19369 | 61.4867 | -0.046838 | 0.029923 | 61.5799 | -0.006014 | 61.3718 | 61.4851 | 61.4234 | 61.4382 | 61.4572 | 61.4865 | 61.4534 | 61.4928 | 123.0468 | 61.6485 | 122.9414 | 61.4079 | 61.4847 | 123.0347 | 61.4488 | 122.8266 | 61.5621 | 61.5981 | 61.4567 | 61.4927
1459.0625 | 123.3536 | -61.4594 | 61.615 | 0.030283 | -0.031363 | -0.021157 | 0.007033 | 0.036265 | -0.001406 | 0.038003 | 61.6058 | 0.20742 | 61.5187 | -0.046838 | 0.029923 | 61.5799 | -0.006014 | 61.3764 | 61.4896 | 61.428 | 61.4382 | 61.4664 | 61.4956 | 61.4579 | 61.4974 | 123.0651 | 61.6668 | 122.9781 | 61.4125 | 61.4893 | 123.0392 | 61.4533 | 122.8357 | 61.5759 | 61.6118 | 61.4888 | 61.5247
1460.0625 | 123.3719 | -61.4822 | 61.5875 | 0.034862 | -0.031363 | -0.016578 | 0.01619 | 0.040843 | 0.003172 | 0.028846 | 61.6012 | 0.19369 | 61.5324 | -0.051417 | 0.029923 | 61.5845 | -0.010593 | 61.381 | 61.5171 | 61.4509 | 61.4657 | 61.4984 | 61.5231 | 61.4854 | 61.5111 | 123.0834 | 61.6759 | 123.0147 | 61.4308 | 61.5122 | 123.0667 | 61.4716 | 122.8632 | 61.5713 | 61.6118 | 61.5025 | 61.543
1461.0625 | 123.4039 | -61.4639 | 61.6241 | 0.030283 | -0.031363 | -0.012 | 0.007033 | 0.040843 | 0.003172 | 0.028846 | 61.6012 | 0.19369 | 61.4912 | -0.051417 | 0.020767 | 61.5799 | -0.015171 | 61.3764 | 61.4942 | 61.4326 | 61.4519 | 61.471 | 61.5048 | 61.4671 | 61.4928 | 123.0651 | 61.6576 | 122.9552 | 61.4125 | 61.4847 | 123.0438 | 61.4488 | 122.8403 | 61.5804 | 61.6164 | 61.4705 | 61.5064
1462.0625 | 123.4085 | -61.4456 | 61.6287 | 0.030283 | -0.031363 | -0.016578 | 0.007033 | 0.040843 | -0.001406 | 0.038003 | 61.6012 | 0.19369 | 61.5324 | -0.051417 | 0.025345 | 61.5707 | -0.006014 | 61.3856 | 61.4759 | 61.4143 | 61.429 | 61.4527 | 61.4865 | 61.4442 | 61.4836 | 123.0468 | 61.6393 | 122.9781 | 61.3942 | 61.471 | 123.0164 | 61.4396 | 122.8312 | 61.5759 | 61.6072 | 61.5071 | 61.5385
1463.0625 | 123.4039 | -61.4639 | 61.6425 | 0.030283 | -0.031363 | -0.012 | 0.002454 | 0.027109 | 0.003172 | 0.038003 | 61.6058 | 0.20742 | 61.5187 | -0.03768 | 0.020767 | 61.5799 | -0.001436 | 61.3764 | 61.4942 | 61.4326 | 61.4519 | 61.4664 | 61.491 | 61.4671 | 61.5019 | 123.0697 | 61.6714 | 122.9826 | 61.4262 | 61.4847 | 123.0438 | 61.4625 | 122.8403 | 61.585 | 61.6072 | 61.4979 | 61.5202
1464.0625 | 123.381 | -61.4731 | 61.615 | 0.030283 | -0.031363 | -0.016578 | 0.011611 | 0.036265 | -0.005985 | 0.033424 | 61.6012 | 0.19827 | 61.4867 | -0.03768 | 0.020767 | 61.5799 | -0.006014 | 61.3718 | 61.5034 | 61.4417 | 61.4565 | 61.4847 | 61.5093 | 61.4671 | 61.5065 | 123.0743 | 61.6713 | 122.9597 | 61.4354 | 61.4939 | 123.053 | 61.4671 | 122.8449 | 61.5804 | 61.6072 | 61.4659 | 61.4927
1465.0625 | 123.3261 | -61.4639 | 61.615 | 0.030283 | -0.035942 | -0.016578 | 0.002454 | 0.036265 | 0.003172 | 0.038003 | 61.6012 | 0.20284 | 61.537 | -0.042259 | 0.025345 | 61.5707 | -0.015171 | 61.3718 | 61.4942 | 61.428 | 61.4474 | 61.4664 | 61.5002 | 61.4671 | 61.5019 | 123.0651 | 61.6668 | 123.001 | 61.4217 | 61.4893 | 123.0347 | 61.4488 | 122.8357 | 61.5759 | 61.6164 | 61.5117 | 61.5522
1466.0625 | 123.3765 | -61.4777 | 61.6058 | 0.025705 | -0.031363 | -0.012 | -0.002124 | 0.031687 | -0.001406 | 0.033424 | 61.6012 | 0.20284 | 61.5096 | -0.051417 | 0.020767 | 61.5753 | -0.010593 | 61.3764 | 61.5034 | 61.4463 | 61.4657 | 61.4755 | 61.5093 | 61.4763 | 61.5111 | 123.0789 | 61.6805 | 122.9872 | 61.4262 | 61.4984 | 123.053 | 61.4671 | 122.8541 | 61.5804 | 61.6118 | 61.4888 | 61.5202
1467.0625 | 123.3307 | -61.4731 | 61.6379 | 0.025705 | -0.040521 | -0.016578 | 0.002454 | 0.031687 | -0.001406 | 0.038003 | 61.6058 | 0.19827 | 61.505 | -0.051417 | 0.029923 | 61.5799 | -0.001436 | 61.3718 | 61.4988 | 61.4326 | 61.4565 | 61.4755 | 61.5048 | 61.4717 | 61.5111 | 123.0789 | 61.6713 | 122.9781 | 61.4217 | 61.503 | 123.053 | 61.4716 | 122.8449 | 61.5759 | 61.6072 | 61.4751 | 61.5064
1468.0625 | 123.3627 | -61.4822 | 61.6013 | 0.030283 | -0.026784 | -0.016578 | 0.002454 | 0.036265 | -0.001406 | 0.028846 | 61.6104 | 0.19827 | 61.537 | -0.046838 | 0.025345 | 61.5753 | -0.015171 | 61.381 | 61.5125 | 61.4555 | 61.4657 | 61.4847 | 61.5185 | 61.4808 | 61.5111 | 123.0926 | 61.6805 | 123.0193 | 61.4354 | 61.5076 | 123.0576 | 61.4671 | 122.8632 | 61.585 | 61.6255 | 61.5117 | 61.5522
1469.0625 | 123.3398 | -61.4914 | 61.6104 | 0.025705 | -0.035942 | -0.012 | 0.007033 | 0.040843 | -0.001406 | 0.028846 | 61.6058 | 0.19369 | 61.4958 | -0.046838 | 0.025345 | 61.5707 | -0.010593 | 61.3718 | 61.5171 | 61.4555 | 61.4794 | 61.4984 | 61.5322 | 61.49 | 61.5202 | 123.0972 | 61.6851 | 122.9872 | 61.4446 | 61.5167 | 123.0621 | 61.4808 | 122.8632 | 61.5804 | 61.6164 | 61.4705 | 61.5064
1470.0625 | 123.349 | -61.4639 | 61.6104 | 0.034862 | -0.035942 | -0.016578 | 0.011611 | 0.036265 | -0.005985 | 0.038003 | 61.6012 | 0.19369 | 61.5096 | -0.051417 | 0.025345 | 61.5799 | -0.006014 | 61.3672 | 61.4988 | 61.428 | 61.4474 | 61.4755 | 61.5002 | 61.4579 | 61.5019 | 123.0651 | 61.6576 | 122.9735 | 61.4125 | 61.4893 | 123.0438 | 61.4579 | 122.8312 | 61.5759 | 61.6072 | 61.4842 | 61.5156
1471.0625 | 123.317 | -61.4914 | 61.6287 | 0.034862 | -0.031363 | -0.016578 | 0.011611 | 0.036265 | -0.010563 | 0.033424 | 61.6012 | 0.20742 | 61.5416 | -0.042259 | 0.025345 | 61.5891 | -0.006014 | 61.3764 | 61.5263 | 61.46 | 61.4748 | 61.503 | 61.5277 | 61.4808 | 61.5248 | 123.0926 | 61.6988 | 123.033 | 61.4491 | 61.5167 | 123.0804 | 61.4854 | 122.8678 | 61.5759 | 61.6072 | 61.5163 | 61.5476
1472.0625 | 123.381 | -61.4685 | 61.615 | 0.034862 | -0.035942 | -0.007421 | 0.002454 | 0.036265 | 0.003172 | 0.033424 | 61.5966 | 0.19369 | 61.4958 | -0.042259 | 0.025345 | 61.5753 | -0.010593 | 61.3718 | 61.5034 | 61.4326 | 61.4611 | 61.471 | 61.5048 | 61.4717 | 61.5019 | 123.0651 | 61.6622 | 122.9643 | 61.4262 | 61.4939 | 123.0438 | 61.4579 | 122.8403 | 61.5713 | 61.6072 | 61.4705 | 61.5064
1473.0625 | 123.3627 | -61.4594 | 61.6241 | 0.03944 | -0.035942 | -0.012 | 0.007033 | 0.031687 | -0.005985 | 0.033424 | 61.5966 | 0.20284 | 61.5004 | -0.055996 | 0.025345 | 61.5845 | -0.006014 | 61.3718 | 61.4988 | 61.4234 | 61.4474 | 61.4664 | 61.491 | 61.4534 | 61.4928 | 123.056 | 61.6622 | 122.9598 | 61.4034 | 61.4847 | 123.0438 | 61.4533 | 122.8312 | 61.5713 | 61.6026 | 61.4751 | 61.5064
1474.0781 | 123.2712 | -61.5372 | 61.6379 | 0.03944 | -0.026784 | -0.016578 | 0.007033 | 0.036265 | -0.005985 | 0.038003 | 61.6104 | 0.19827 | 61.537 | -0.046838 | 0.029923 | 61.5707 | -0.006014 | 61.3764 | 61.5766 | 61.5104 | 61.5206 | 61.5442 | 61.5734 | 61.5312 | 61.5752 | 123.1475 | 61.7354 | 123.0742 | 61.4903 | 61.5671 | 123.1079 | 61.5312 | 122.9136 | 61.5804 | 61.6164 | 61.5071 | 61.543
1475.0625 | 123.3261 | -61.496 | 61.6013 | 0.030283 | -0.031363 | -0.012 | 0.011611 | 0.036265 | -0.001406 | 0.038003 | 61.6012 | 0.18453 | 61.4867 | -0.046838 | 0.020767 | 61.5753 | -0.001436 | 61.3672 | 61.5263 | 61.4646 | 61.484 | 61.5076 | 61.5322 | 61.4946 | 61.534 | 123.0972 | 61.6805 | 122.9826 | 61.4491 | 61.5167 | 123.0713 | 61.4945 | 122.8632 | 61.5804 | 61.6026 | 61.4659 | 61.4881
1476.0625 | 123.3307 | -61.4868 | 61.6241 | 0.025705 | -0.031363 | -0.016578 | 0.002454 | 0.031687 | 0.003172 | 0.038003 | 61.6104 | 0.19827 | 61.5324 | -0.03768 | 0.025345 | 61.5753 | -0.001436 | 61.381 | 61.5125 | 61.4555 | 61.4702 | 61.4893 | 61.5185 | 61.49 | 61.5248 | 123.0972 | 61.6851 | 123.0193 | 61.4491 | 61.5122 | 123.0621 | 61.4854 | 122.8678 | 61.585 | 61.6118 | 61.5071 | 61.5339
1477.0625 | 123.3444 | -61.4685 | 61.6058 | 0.034862 | -0.026784 | -0.016578 | -0.002124 | 0.040843 | 0.003172 | 0.038003 | 61.6058 | 0.18911 | 61.5279 | -0.042259 | 0.025345 | 61.5753 | -0.001436 | 61.3764 | 61.5034 | 61.4417 | 61.4519 | 61.4664 | 61.5093 | 61.4717 | 61.5065 | 123.0743 | 61.6576 | 122.9964 | 61.4262 | 61.4939 | 123.0438 | 61.4671 | 122.8449 | 61.5804 | 61.6072 | 61.5025 | 61.5293
1478.0625 | 123.3444 | -61.496 | 61.6241 | 0.03944 | -0.026784 | -0.016578 | 0.011611 | 0.040843 | -0.001406 | 0.028846 | 61.5966 | 0.19827 | 61.4912 | -0.046838 | 0.029923 | 61.5753 | -0.001436 | 61.3718 | 61.5354 | 61.4692 | 61.4794 | 61.5076 | 61.5368 | 61.4946 | 61.5248 | 123.0926 | 61.6942 | 122.9872 | 61.4491 | 61.5259 | 123.0713 | 61.4945 | 122.8678 | 61.5667 | 61.5981 | 61.4613 | 61.4927
1479.0625 | 123.4039 | -61.4639 | 61.6241 | 0.030283 | -0.031363 | -0.012 | 0.011611 | 0.040843 | -0.001406 | 0.047159 | 61.5966 | 0.19827 | 61.5324 | -0.051417 | 0.025345 | 61.5799 | -0.006014 | 61.3764 | 61.4942 | 61.4326 | 61.4519 | 61.4755 | 61.5048 | 61.4625 | 61.5111 | 123.0605 | 61.6622 | 122.9964 | 61.4125 | 61.4893 | 123.0438 | 61.4579 | 122.8403 | 61.5713 | 61.6026 | 61.5071 | 61.5385
1480.0625 | 123.349 | -61.4685 | 61.5921 | 0.030283 | -0.035942 | -0.021157 | 0.007033 | 0.036265 | -0.005985 | 0.028846 | 61.5966 | 0.20742 | 61.5279 | -0.046838 | 0.029923 | 61.5707 | -0.010593 | 61.3764 | 61.4988 | 61.4326 | 61.4473 | 61.4755 | 61.5048 | 61.4625 | 61.4974 | 123.0651 | 61.6759 | 122.9964 | 61.4217 | 61.4984 | 123.0392 | 61.4579 | 122.8449 | 61.5667 | 61.6072 | 61.4979 | 61.5385
1481.0625 | 123.3902 | -61.4731 | 61.5829 | 0.030283 | -0.026784 | -0.016578 | 0.002454 | 0.036265 | -0.001406 | 0.028846 | 61.5966 | 0.20742 | 61.505 | -0.046838 | 0.029923 | 61.5845 | -0.001436 | 61.3672 | 61.5034 | 61.4463 | 61.4565 | 61.4755 | 61.5093 | 61.4717 | 61.5019 | 123.0697 | 61.6805 | 122.9781 | 61.4262 | 61.503 | 123.0576 | 61.4716 | 122.8403 | 61.5667 | 61.5981 | 61.4751 | 61.5064
1482.0625 | 123.3398 | -61.4548 | 61.6058 | 0.030283 | -0.031363 | -0.016578 | 0.011611 | 0.040843 | -0.001406 | 0.038003 | 61.5966 | 0.20742 | 61.5324 | -0.046838 | 0.016188 | 61.5799 | -0.010593 | 61.381 | 61.4851 | 61.4234 | 61.4382 | 61.4664 | 61.4956 | 61.4534 | 61.4928 | 123.0514 | 61.6622 | 122.9872 | 61.4079 | 61.471 | 123.0347 | 61.4442 | 122.8357 | 61.5804 | 61.6072 | 61.5163 | 61.543
1483.0625 | 123.3765 | -61.4868 | 61.5967 | 0.030283 | -0.031363 | -0.016578 | 0.007033 | 0.036265 | -0.001406 | 0.038003 | 61.6012 | 0.19827 | 61.5096 | -0.046838 | 0.025345 | 61.5799 | -0.001436 | 61.381 | 61.5171 | 61.4555 | 61.4702 | 61.4938 | 61.5231 | 61.4854 | 61.5248 | 123.088 | 61.6851 | 122.9964 | 61.44 | 61.5122 | 123.0667 | 61.4854 | 122.8678 | 61.5759 | 61.6026 | 61.4842 | 61.511
1484.0625 | 123.3353 | -61.4685 | 61.6196 | 0.034862 | -0.026784 | -0.016578 | 0.007033 | 0.031687 | -0.005985 | 0.038003 | 61.6058 | 0.20284 | 61.4912 | -0.03768 | 0.025345 | 61.5845 | -0.010593 | 61.3672 | 61.5034 | 61.4417 | 61.4519 | 61.4755 | 61.5002 | 61.4625 | 61.5065 | 123.0743 | 61.6714 | 122.9598 | 61.4308 | 61.4939 | 123.053 | 61.4579 | 122.8357 | 61.5804 | 61.6164 | 61.4659 | 61.5018
1485.0625 | 123.4406 | -61.4502 | 61.6104 | 0.030283 | -0.031363 | -0.016578 | 0.007033 | 0.036265 | -0.005985 | 0.024268 | 61.6058 | 0.20284 | 61.5324 | -0.055996 | 0.029923 | 61.5799 | -0.006014 | 61.3718 | 61.4805 | 61.4188 | 61.4336 | 61.4572 | 61.4865 | 61.4442 | 61.4745 | 123.056 | 61.653 | 122.9826 | 61.3942 | 61.4801 | 123.0301 | 61.4442 | 122.822 | 61.5759 | 61.6118 | 61.5025 | 61.5385
1486.0625 | 123.349 | -61.4777 | 61.6013 | 0.025705 | -0.040521 | -0.016578 | 0.007033 | 0.036265 | -0.010563 | 0.033424 | 61.6012 | 0.19827 | 61.5096 | -0.051417 | 0.029923 | 61.5799 | -0.010593 | 61.381 | 61.5034 | 61.4371 | 61.4611 | 61.4847 | 61.5139 | 61.4671 | 61.5111 | 123.0789 | 61.6759 | 122.9872 | 61.4262 | 61.5076 | 123.0576 | 61.4671 | 122.8586 | 61.5713 | 61.6118 | 61.4796 | 61.5202
1487.0625 | 123.3765 | -61.4594 | 61.6058 | 0.030283 | -0.031363 | -0.012 | 0.011611 | 0.031687 | -0.005985 | 0.033424 | 61.5966 | 0.19827 | 61.4912 | -0.046838 | 0.020767 | 61.5799 | -0.006014 | 61.3764 | 61.4896 | 61.428 | 61.4474 | 61.471 | 61.491 | 61.4534 | 61.4928 | 123.056 | 61.6576 | 122.9506 | 61.4125 | 61.4801 | 123.0392 | 61.4533 | 122.8357 | 61.5759 | 61.6026 | 61.4705 | 61.4973
1488.0625 | 123.2941 | -61.5143 | 61.6241 | 0.034862 | -0.031363 | -0.016578 | 0.002454 | 0.036265 | 0.003172 | 0.042581 | 61.6149 | 0.19827 | 61.5416 | -0.042259 | 0.029923 | 61.5753 | -0.006014 | 61.3764 | 61.5491 | 61.4829 | 61.4977 | 61.5167 | 61.5505 | 61.5175 | 61.5569 | 123.1292 | 61.7125 | 123.0559 | 61.472 | 61.5442 | 123.0896 | 61.5083 | 122.8907 | 61.585 | 61.6209 | 61.5117 | 61.5476
1489.0625 | 123.2986 | -61.4868 | 61.6287 | 0.030283 | -0.035942 | -0.012 | 0.01619 | 0.031687 | 0.003172 | 0.028846 | 61.6012 | 0.20284 | 61.505 | -0.051417 | 0.020767 | 61.5753 | -0.006014 | 61.381 | 61.5171 | 61.4509 | 61.4748 | 61.503 | 61.5185 | 61.49 | 61.5157 | 123.088 | 61.6897 | 122.9918 | 61.4354 | 61.5076 | 123.0621 | 61.4808 | 122.8678 | 61.5804 | 61.6072 | 61.4842 | 61.511
1490.0625 | 123.2895 | -61.496 | 61.6196 | 0.03944 | -0.026784 | -0.016578 | 0.011611 | 0.031687 | -0.001406 | 0.033424 | 61.6012 | 0.19827 | 61.4958 | -0.046838 | 0.020767 | 61.5707 | -0.006014 | 61.3764 | 61.5354 | 61.4692 | 61.4794 | 61.5076 | 61.5277 | 61.4946 | 61.5294 | 123.0972 | 61.6942 | 122.9918 | 61.4491 | 61.5167 | 123.0667 | 61.49 | 122.8724 | 61.5804 | 61.6072 | 61.4751 | 61.5018
1491.0625 | 123.2986 | -61.5005 | 61.6287 | 0.030283 | -0.026784 | -0.016578 | 0.007033 | 0.036265 | 0.003172 | 0.038003 | 61.6104 | 0.19369 | 61.5416 | -0.042259 | 0.025345 | 61.5799 | -0.010593 | 61.3718 | 61.5308 | 61.4738 | 61.484 | 61.5076 | 61.5368 | 61.5037 | 61.5386 | 123.1109 | 61.6942 | 123.0422 | 61.4583 | 61.5259 | 123.0804 | 61.49 | 122.8724 | 61.585 | 61.6209 | 61.5163 | 61.5522
1492.0625 | 123.2895 | -61.4914 | 61.6516 | 0.030283 | -0.022205 | -0.016578 | 0.002454 | 0.040843 | -0.005985 | 0.038003 | 61.6012 | 0.19827 | 61.4958 | -0.046838 | 0.020767 | 61.5799 | -0.010593 | 61.3764 | 61.5217 | 61.4692 | 61.4748 | 61.4938 | 61.5322 | 61.4854 | 61.5294 | 123.0926 | 61.6897 | 122.9872 | 61.4446 | 61.5122 | 123.0713 | 61.4808 | 122.8678 | 61.5804 | 61.6118 | 61.4751 | 61.5064
1493.0625 | 123.2529 | -61.5143 | 61.6379 | 0.030283 | -0.031363 | -0.016578 | 0.011611 | 0.040843 | 0.003172 | 0.042581 | 61.6104 | 0.20284 | 61.5279 | -0.042259 | 0.025345 | 61.5799 | -0.010593 | 61.3764 | 61.5446 | 61.4829 | 61.4977 | 61.5259 | 61.5551 | 61.5175 | 61.5569 | 123.1246 | 61.7171 | 123.0422 | 61.472 | 61.5396 | 123.0942 | 61.5037 | 122.8907 | 61.585 | 61.6209 | 61.5025 | 61.5385
1494.0625 | 123.3719 | -61.4456 | 61.615 | 0.034862 | -0.031363 | -0.021157 | 0.007033 | 0.036265 | 0.003172 | 0.042581 | 61.6058 | 0.20742 | 61.505 | -0.046838 | 0.025345 | 61.5799 | -0.010593 | 61.3718 | 61.4805 | 61.4143 | 61.4245 | 61.4527 | 61.4819 | 61.4488 | 61.4882 | 123.0514 | 61.653 | 122.9506 | 61.3988 | 61.471 | 123.0255 | 61.435 | 122.8174 | 61.5804 | 61.6164 | 61.4796 | 61.5156
1495.0625 | 123.2941 | -61.4868 | 61.6608 | 0.030283 | -0.031363 | -0.016578 | 0.011611 | 0.040843 | 0.003172 | 0.033424 | 61.6058 | 0.19827 | 61.5141 | -0.051417 | 0.020767 | 61.5799 | -0.006014 | 61.3764 | 61.5171 | 61.4555 | 61.4702 | 61.4984 | 61.5277 | 61.49 | 61.5202 | 123.0926 | 61.6851 | 123.001 | 61.4354 | 61.5076 | 123.0667 | 61.4808 | 122.8632 | 61.585 | 61.6118 | 61.4934 | 61.5202
1496.0625 | 123.2574 | -61.5051 | 61.6196 | 0.034862 | -0.026784 | -0.016578 | 0.011611 | 0.036265 | -0.001406 | 0.038003 | 61.6058 | 0.19827 | 61.5324 | -0.046838 | 0.025345 | 61.5753 | -0.006014 | 61.381 | 61.54 | 61.4783 | 61.4885 | 61.5167 | 61.5414 | 61.5037 | 61.5431 | 123.1109 | 61.7034 | 123.0376 | 61.4583 | 61.5305 | 123.0804 | 61.4991 | 122.8861 | 61.5804 | 61.6118 | 61.5071 | 61.5385
1497.0625 | 123.2346 | -61.496 | 61.6516 | 0.025705 | -0.026784 | -0.016578 | 0.011611 | 0.040843 | 0.003172 | 0.038003 | 61.6058 | 0.19369 | 61.5004 | -0.055996 | 0.025345 | 61.5799 | -0.006014 | 61.3672 | 61.5217 | 61.4692 | 61.4794 | 61.5076 | 61.5368 | 61.4991 | 61.534 | 123.1017 | 61.6897 | 122.9964 | 61.44 | 61.5213 | 123.0759 | 61.49 | 122.8632 | 61.5804 | 61.6118 | 61.4751 | 61.5064
1498.0625 | 123.3078 | -61.5051 | 61.6287 | 0.030283 | -0.022205 | -0.016578 | 0.002454 | 0.036265 | 0.003172 | 0.038003 | 61.6012 | 0.19369 | 61.5324 | -0.051417 | 0.025345 | 61.5799 | -0.001436 | 61.381 | 61.5354 | 61.4829 | 61.4885 | 61.5076 | 61.5414 | 61.5083 | 61.5431 | 123.1063 | 61.6988 | 123.0376 | 61.4537 | 61.5305 | 123.085 | 61.5037 | 122.8861 | 61.5759 | 61.6026 | 61.5071 | 61.5339
1499.0625 | 123.3673 | -61.4822 | 61.5967 | 0.030283 | -0.026784 | -0.016578 | 0.020768 | 0.036265 | -0.001406 | 0.038003 | 61.6012 | 0.19369 | 61.5324 | -0.046838 | 0.029923 | 61.5753 | -0.015171 | 61.3764 | 61.5125 | 61.4555 | 61.4657 | 61.503 | 61.5185 | 61.4808 | 61.5202 | 123.0834 | 61.6759 | 123.0147 | 61.4354 | 61.5122 | 123.0576 | 61.4671 | 122.8586 | 61.5713 | 61.6164 | 61.5025 | 61.5476
1500.0625 | 123.3536 | -61.4868 | 61.6562 | 0.025705 | -0.022205 | -0.012 | 0.007033 | 0.040843 | -0.001406 | 0.042581 | 61.6058 | 0.19827 | 61.4912 | -0.042259 | 0.020767 | 61.5799 | -0.006014 | 61.3718 | 61.5125 | 61.4646 | 61.4748 | 61.4938 | 61.5277 | 61.4854 | 61.5294 | 123.0926 | 61.6851 | 122.9781 | 61.4446 | 61.5076 | 123.0667 | 61.4808 | 122.8586 | 61.585 | 61.6118 | 61.4705 | 61.4973
1501.0625 | 123.2941 | -61.4822 | 61.6287 | 0.034862 | -0.031363 | -0.016578 | 0.002454 | 0.031687 | 0.003172 | 0.038003 | 61.6104 | 0.19827 | 61.5416 | -0.046838 | 0.029923 | 61.5799 | -0.015171 | 61.381 | 61.5171 | 61.4509 | 61.4657 | 61.4847 | 61.5139 | 61.4854 | 61.5202 | 123.0926 | 61.6805 | 123.0238 | 61.4354 | 61.5122 | 123.0621 | 61.4671 | 122.8632 | 61.5804 | 61.6255 | 61.5117 | 61.5568
1502.0625 | 123.2849 | -61.4639 | 61.6562 | 0.034862 | -0.031363 | -0.021157 | 0.011611 | 0.036265 | 0.003172 | 0.042581 | 61.6058 | 0.19827 | 61.5324 | -0.03768 | 0.029923 | 61.5845 | -0.001436 | 61.3856 | 61.4988 | 61.4326 | 61.4428 | 61.4755 | 61.5002 | 61.4671 | 61.5065 | 123.0697 | 61.6622 | 122.9964 | 61.4262 | 61.4939 | 123.0484 | 61.4625 | 122.8495 | 61.5759 | 61.6072 | 61.5025 | 61.5339
1503.0625 | 123.2895 | -61.4548 | 61.6379 | 0.030283 | -0.026784 | -0.012 | 0.011611 | 0.040843 | 0.003172 | 0.042581 | 61.6012 | 0.20284 | 61.5004 | -0.046838 | 0.034501 | 61.5845 | -0.001436 | 61.3718 | 61.4851 | 61.428 | 61.4428 | 61.4664 | 61.4956 | 61.4579 | 61.4974 | 123.056 | 61.6576 | 122.9552 | 61.4079 | 61.4893 | 123.0392 | 61.4533 | 122.8266 | 61.5667 | 61.6026 | 61.4659 | 61.5018
1504.0625 | 123.3444 | -61.4731 | 61.6058 | 0.030283 | -0.026784 | -0.021157 | 0.011611 | 0.040843 | 0.003172 | 0.033424 | 61.6058 | 0.19827 | 61.5416 | -0.042259 | 0.025345 | 61.5799 | -0.006014 | 61.3856 | 61.5034 | 61.4463 | 61.4519 | 61.4847 | 61.5139 | 61.4763 | 61.5065 | 123.0789 | 61.6713 | 123.0147 | 61.4308 | 61.4984 | 123.053 | 61.4671 | 122.8586 | 61.5804 | 61.6118 | 61.5163 | 61.5476
1505.0625 | 123.2941 | -61.4777 | 61.6653 | 0.030283 | -0.026784 | -0.021157 | 0.011611 | 0.036265 | -0.001406 | 0.038003 | 61.6058 | 0.20742 | 61.5187 | -0.042259 | 0.034501 | 61.5753 | -0.010593 | 61.3856 | 61.5079 | 61.4509 | 61.4565 | 61.4893 | 61.5139 | 61.4763 | 61.5157 | 123.0834 | 61.6851 | 122.9964 | 61.4354 | 61.5122 | 123.053 | 61.4671 | 122.8632 | 61.5713 | 61.6164 | 61.4842 | 61.5293
1506.0625 | 123.3398 | -61.4548 | 61.6425 | 0.034862 | -0.031363 | -0.012 | 0.007033 | 0.036265 | 0.00775 | 0.033424 | 61.6058 | 0.19827 | 61.5004 | -0.051417 | 0.025345 | 61.5799 | -0.001436 | 61.381 | 61.4896 | 61.4234 | 61.4428 | 61.4618 | 61.491 | 61.4625 | 61.4882 | 123.0606 | 61.653 | 122.9552 | 61.4034 | 61.4801 | 123.0347 | 61.4533 | 122.8357 | 61.5804 | 61.6072 | 61.4751 | 61.5018
1507.0625 | 123.2986 | -61.4822 | 61.6837 | 0.030283 | -0.031363 | -0.016578 | 0.007033 | 0.045421 | -0.005985 | 0.038003 | 61.6104 | 0.19827 | 61.5553 | -0.042259 | 0.025345 | 61.5799 | -0.006014 | 61.3764 | 61.5125 | 61.4509 | 61.4657 | 61.4893 | 61.5277 | 61.4763 | 61.5202 | 123.0926 | 61.6805 | 123.0376 | 61.44 | 61.5076 | 123.0621 | 61.4762 | 122.8586 | 61.585 | 61.6164 | 61.53 | 61.5614
1508.0625 | 123.2483 | -61.496 | 61.6608 | 0.030283 | -0.026784 | -0.007421 | 0.011611 | 0.036265 | -0.001406 | 0.038003 | 61.5966 | 0.19369 | 61.5096 | -0.046838 | 0.034501 | 61.5845 | -0.010593 | 61.381 | 61.5263 | 61.4692 | 61.4886 | 61.5076 | 61.5322 | 61.4946 | 61.534 | 123.0926 | 61.6897 | 123.0055 | 61.4491 | 61.5305 | 123.0804 | 61.4854 | 122.8769 | 61.5621 | 61.6072 | 61.4751 | 61.5202
1509.0625 | 123.2849 | -61.5051 | 61.6333 | 0.034862 | -0.026784 | -0.016578 | 0.011611 | 0.040843 | -0.001406 | 0.033424 | 61.6104 | 0.19369 | 61.5004 | -0.042259 | 0.029923 | 61.5845 | -0.006014 | 61.3764 | 61.54 | 61.4783 | 61.4885 | 61.5167 | 61.546 | 61.5037 | 61.5386 | 123.1155 | 61.6988 | 123.0055 | 61.4629 | 61.535 | 123.0896 | 61.4991 | 122.8815 | 61.5804 | 61.6164 | 61.4705 | 61.5064
1510.0625 | 123.262 | -61.4731 | 61.6699 | 0.025705 | -0.031363 | -0.016578 | 0.011611 | 0.036265 | -0.010563 | 0.033424 | 61.6058 | 0.19827 | 61.5508 | -0.046838 | 0.029923 | 61.5753 | 0.003143 | 61.381 | 61.4988 | 61.4417 | 61.4565 | 61.4847 | 61.5093 | 61.4625 | 61.5065 | 123.0789 | 61.6713 | 123.0238 | 61.4262 | 61.503 | 123.0484 | 61.4762 | 122.8541 | 61.5759 | 61.6026 | 61.5208 | 61.5476
1511.0625 | 123.2941 | -61.5005 | 61.702 | 0.030283 | -0.026784 | -0.012 | 0.011611 | 0.036265 | 0.00775 | 0.033424 | 61.5966 | 0.19827 | 61.5141 | -0.046838 | 0.029923 | 61.5753 | -0.006014 | 61.3856 | 61.5308 | 61.4738 | 61.4885 | 61.5122 | 61.5368 | 61.5083 | 61.534 | 123.0972 | 61.6988 | 123.0147 | 61.4537 | 61.5305 | 123.0759 | 61.4945 | 122.8861 | 61.5667 | 61.6026 | 61.4842 | 61.5202
1512.0625 | 123.2574 | -61.4822 | 61.6974 | 0.030283 | -0.035942 | -0.007421 | 0.011611 | 0.036265 | -0.005985 | 0.038003 | 61.5966 | 0.19369 | 61.505 | -0.046838 | 0.025345 | 61.5799 | -0.006014 | 61.381 | 61.5125 | 61.4463 | 61.4748 | 61.4939 | 61.5185 | 61.4763 | 61.5202 | 123.0789 | 61.6759 | 122.9872 | 61.4354 | 61.5076 | 123.0621 | 61.4762 | 122.8632 | 61.5713 | 61.6026 | 61.4796 | 61.511
1513.0625 | 123.2941 | -61.4685 | 61.6837 | 0.030283 | -0.026784 | -0.016578 | 0.011611 | 0.040843 | -0.005985 | 0.042581 | 61.6012 | 0.20742 | 61.5096 | -0.046838 | 0.025345 | 61.5799 | -0.010593 | 61.3718 | 61.4988 | 61.4417 | 61.4519 | 61.4801 | 61.5093 | 61.4625 | 61.5111 | 123.0697 | 61.6759 | 122.9781 | 61.4217 | 61.4939 | 123.0484 | 61.4579 | 122.8403 | 61.5759 | 61.6118 | 61.4842 | 61.5202
1514.0625 | 123.2574 | -61.496 | 61.6608 | 0.030283 | -0.026784 | -0.007421 | 0.002454 | 0.040843 | -0.001406 | 0.038003 | 61.6104 | 0.20284 | 61.5462 | -0.046838 | 0.025345 | 61.5799 | -0.006014 | 61.3764 | 61.5263 | 61.4692 | 61.4886 | 61.4984 | 61.5368 | 61.4946 | 61.534 | 123.1063 | 61.6988 | 123.0422 | 61.4491 | 61.5213 | 123.0759 | 61.49 | 122.8724 | 61.585 | 61.6164 | 61.5208 | 61.5522
1515.0625 | 123.2895 | -61.496 | 61.6882 | 0.030283 | -0.026784 | -0.012 | 0.007033 | 0.040843 | -0.001406 | 0.038003 | 61.6058 | 0.19827 | 61.5462 | -0.042259 | 0.029923 | 61.5753 | -0.001436 | 61.3764 | 61.5263 | 61.4692 | 61.484 | 61.503 | 61.5368 | 61.4946 | 61.534 | 123.1017 | 61.6942 | 123.0422 | 61.4537 | 61.5259 | 123.0713 | 61.4945 | 122.8724 | 61.5759 | 61.6072 | 61.5163 | 61.5476
1516.0625 | 123.4314 | -61.4639 | 61.6241 | 0.034862 | -0.022205 | -0.012 | 0.007033 | 0.036265 | -0.001406 | 0.038003 | 61.6012 | 0.20742 | 61.4958 | -0.046838 | 0.034501 | 61.5845 | -0.006014 | 61.3764 | 61.4988 | 61.4417 | 61.4519 | 61.471 | 61.5002 | 61.4625 | 61.5019 | 123.0651 | 61.6714 | 122.9598 | 61.4171 | 61.4984 | 123.0484 | 61.4579 | 122.8403 | 61.5667 | 61.6072 | 61.4613 | 61.5018
1517.0625 | 123.3353 | -61.4685 | 61.6562 | 0.030283 | -0.031363 | -0.016578 | 0.007033 | 0.036265 | 0.003172 | 0.033424 | 61.6012 | 0.19827 | 61.4958 | -0.042259 | 0.029923 | 61.5753 | -0.001436 | 61.3718 | 61.4988 | 61.4371 | 61.4519 | 61.4755 | 61.5048 | 61.4717 | 61.5019 | 123.0697 | 61.6668 | 122.9643 | 61.4262 | 61.4984 | 123.0438 | 61.4671 | 122.8403 | 61.5713 | 61.6026 | 61.4659 | 61.4973
1518.0625 | 123.3398 | -61.4822 | 61.6516 | 0.03944 | -0.031363 | -0.016578 | 0.011611 | 0.036265 | 0.003172 | 0.033424 | 61.6012 | 0.19827 | 61.5462 | -0.042259 | 0.034501 | 61.5753 | -0.006014 | 61.381 | 61.5217 | 61.4509 | 61.4657 | 61.4939 | 61.5185 | 61.4854 | 61.5157 | 123.0834 | 61.6805 | 123.0284 | 61.44 | 61.5167 | 123.0576 | 61.4762 | 122.8632 | 61.5667 | 61.6072 | 61.5117 | 61.5522
1519.0625 | 123.3765 | -61.441 | 61.6379 | 0.030283 | -0.035942 | -0.016578 | 0.002454 | 0.040843 | -0.001406 | 0.038003 | 61.6195 | 0.19369 | 61.5416 | -0.046838 | 0.029923 | 61.5799 | -0.006014 | 61.3764 | 61.4713 | 61.4051 | 61.4245 | 61.4435 | 61.4819 | 61.4396 | 61.479 | 123.0606 | 61.6347 | 122.9826 | 61.3942 | 61.471 | 123.0209 | 61.435 | 122.8174 | 61.5896 | 61.6255 | 61.5117 | 61.5476
1520.0625 | 123.3948 | -61.4822 | 61.6562 | 0.025705 | -0.031363 | -0.012 | 0.007033 | 0.031687 | -0.010563 | 0.033424 | 61.6012 | 0.212 | 61.5096 | -0.042259 | 0.034501 | 61.5799 | -0.006014 | 61.381 | 61.5079 | 61.4509 | 61.4702 | 61.4893 | 61.5139 | 61.4717 | 61.5157 | 123.0834 | 61.6942 | 122.9918 | 61.44 | 61.5167 | 123.0621 | 61.4762 | 122.8632 | 61.5667 | 61.6072 | 61.4751 | 61.5156
1521.0625 | 123.381 | -61.4731 | 61.615 | 0.030283 | -0.026784 | -0.012 | 0.007033 | 0.031687 | -0.005985 | 0.024268 | 61.6058 | 0.20742 | 61.5141 | -0.051417 | 0.029923 | 61.5707 | -0.006014 | 61.3764 | 61.5034 | 61.4463 | 61.4611 | 61.4801 | 61.5048 | 61.4671 | 61.4974 | 123.0789 | 61.6805 | 122.9872 | 61.4217 | 61.503 | 123.0438 | 61.4671 | 122.8495 | 61.5759 | 61.6118 | 61.4842 | 61.5202
1522.0625 | 123.436 | -61.4502 | 61.6287 | 0.025705 | -0.031363 | -0.021157 | 0.007033 | 0.036265 | -0.001406 | 0.033424 | 61.6012 | 0.19369 | 61.5233 | -0.055996 | 0.034501 | 61.5799 | -0.006014 | 61.3764 | 61.4759 | 61.4188 | 61.429 | 61.4572 | 61.4865 | 61.4488 | 61.4836 | 123.0514 | 61.6439 | 122.9735 | 61.3942 | 61.4847 | 123.0301 | 61.4442 | 122.8266 | 61.5667 | 61.6072 | 61.4888 | 61.5293
1523.0625 | 123.3948 | -61.4548 | 61.6241 | 0.034862 | -0.031363 | -0.016578 | 0.002454 | 0.040843 | 0.003172 | 0.033424 | 61.6058 | 0.19827 | 61.5324 | -0.046838 | 0.025345 | 61.5845 | -0.010593 | 61.3764 | 61.4896 | 61.4234 | 61.4382 | 61.4572 | 61.4956 | 61.4579 | 61.4882 | 123.0606 | 61.653 | 122.9872 | 61.4079 | 61.4801 | 123.0392 | 61.4442 | 122.8312 | 61.5804 | 61.6164 | 61.5071 | 61.543
1524.0625 | 123.2849 | -61.4914 | 61.6608 | 0.030283 | -0.031363 | -0.016578 | 0.007033 | 0.036265 | -0.001406 | 0.038003 | 61.6104 | 0.20742 | 61.5324 | -0.046838 | 0.020767 | 61.5799 | -0.010593 | 61.3764 | 61.5217 | 61.46 | 61.4748 | 61.4984 | 61.5277 | 61.49 | 61.5294 | 123.1018 | 61.6988 | 123.0238 | 61.4446 | 61.5122 | 123.0713 | 61.4808 | 122.8678 | 61.5896 | 61.6209 | 61.5117 | 61.543
1525.0625 | 123.3765 | -61.4502 | 61.6425 | 0.025705 | -0.035942 | -0.025735 | 0.002454 | 0.031687 | -0.005985 | 0.038003 | 61.5966 | 0.19827 | 61.505 | -0.042259 | 0.029923 | 61.5845 | -0.001436 | 61.3718 | 61.4759 | 61.4143 | 61.4245 | 61.4526 | 61.4819 | 61.4442 | 61.4882 | 123.0468 | 61.6485 | 122.9552 | 61.4079 | 61.4801 | 123.0347 | 61.4488 | 122.822 | 61.5667 | 61.5981 | 61.4751 | 61.5064
1526.0625 | 123.4314 | -61.4822 | 61.6196 | 0.025705 | -0.026784 | -0.012 | 0.007033 | 0.040843 | -0.001406 | 0.038003 | 61.5966 | 0.19827 | 61.5141 | -0.046838 | 0.039079 | 61.5753 | -0.006014 | 61.3764 | 61.5079 | 61.4555 | 61.4702 | 61.4893 | 61.5231 | 61.4808 | 61.5202 | 123.0789 | 61.6805 | 122.9964 | 61.4354 | 61.5213 | 123.0576 | 61.4762 | 122.8586 | 61.5575 | 61.6026 | 61.4751 | 61.5202
1527.0625 | 123.3902 | -61.441 | 61.647 | 0.03944 | -0.026784 | -0.016578 | 0.002454 | 0.036265 | -0.001406 | 0.033424 | 61.6058 | 0.20284 | 61.5462 | -0.03768 | 0.029923 | 61.5845 | -0.006014 | 61.381 | 61.4805 | 61.4143 | 61.4245 | 61.4435 | 61.4773 | 61.4396 | 61.4745 | 123.0468 | 61.6439 | 122.9872 | 61.4034 | 61.471 | 123.0255 | 61.435 | 122.822 | 61.5759 | 61.6118 | 61.5163 | 61.5522
1528.0625 | 123.4314 | -61.441 | 61.6058 | 0.034862 | -0.026784 | -0.016578 | 0.011611 | 0.040843 | 0.003172 | 0.038003 | 61.6058 | 0.20284 | 61.537 | -0.046838 | 0.025345 | 61.5799 | -0.006014 | 61.3764 | 61.4759 | 61.4143 | 61.4245 | 61.4527 | 61.4819 | 61.4442 | 61.479 | 123.0468 | 61.6439 | 122.9781 | 61.3942 | 61.4664 | 123.0209 | 61.435 | 122.8174 | 61.5804 | 61.6118 | 61.5117 | 61.543
1529.0625 | 123.262 | -61.5005 | 61.6653 | 0.034862 | -0.040521 | -0.007421 | 0.007033 | 0.036265 | -0.001406 | 0.042581 | 61.6104 | 0.19827 | 61.505 | -0.042259 | 0.034501 | 61.5845 | -0.001436 | 61.3718 | 61.5354 | 61.46 | 61.4931 | 61.5076 | 61.5368 | 61.4991 | 61.5431 | 123.1109 | 61.6988 | 123.0055 | 61.4583 | 61.535 | 123.085 | 61.4991 | 122.8724 | 61.5759 | 61.6118 | 61.4705 | 61.5064
1530.0625 | 123.3994 | -61.4594 | 61.615 | 0.030283 | -0.026784 | -0.012 | 0.007033 | 0.031687 | 0.003172 | 0.038003 | 61.6012 | 0.19827 | 61.5004 | -0.042259 | 0.020767 | 61.5845 | -0.006014 | 61.3764 | 61.4896 | 61.4326 | 61.4474 | 61.4664 | 61.491 | 61.4625 | 61.4974 | 123.0606 | 61.6576 | 122.9598 | 61.4171 | 61.4801 | 123.0438 | 61.4533 | 122.8357 | 61.5804 | 61.6072 | 61.4796 | 61.5064
1531.0625 | 123.3856 | -61.4868 | 61.6333 | 0.030283 | -0.031363 | -0.016578 | 0.007033 | 0.036265 | 0.003172 | 0.047159 | 61.6104 | 0.19369 | 61.5508 | -0.042259 | 0.025345 | 61.5845 | -0.010593 | 61.3718 | 61.5171 | 61.4555 | 61.4702 | 61.4938 | 61.5231 | 61.49 | 61.534 | 123.0972 | 61.6805 | 123.0376 | 61.4446 | 61.5122 | 123.0713 | 61.4762 | 122.8586 | 61.585 | 61.6209 | 61.5254 | 61.5614
1532.0625 | 123.4131 | -61.4456 | 61.6333 | 0.030283 | -0.031363 | -0.016578 | 0.007033 | 0.040843 | -0.001406 | 0.038003 | 61.6104 | 0.19827 | 61.5416 | -0.046838 | 0.029923 | 61.5753 | -0.006014 | 61.381 | 61.4759 | 61.4143 | 61.429 | 61.4527 | 61.4865 | 61.4442 | 61.4836 | 123.056 | 61.6439 | 122.9872 | 61.3988 | 61.4755 | 123.0209 | 61.4396 | 122.8266 | 61.5804 | 61.6164 | 61.5117 | 61.5476
1533.0625 | 123.3994 | -61.4639 | 61.6379 | 0.034862 | -0.031363 | -0.021157 | 0.007033 | 0.036265 | -0.001406 | 0.038003 | 61.6012 | 0.20742 | 61.505 | -0.042259 | 0.025345 | 61.5845 | -0.010593 | 61.381 | 61.4988 | 61.4326 | 61.4428 | 61.471 | 61.5002 | 61.4625 | 61.5019 | 123.0651 | 61.6714 | 122.9689 | 61.4217 | 61.4893 | 123.0484 | 61.4533 | 122.8449 | 61.5759 | 61.6118 | 61.4796 | 61.5156
1534.0625 | 123.3215 | -61.4868 | 61.6699 | 0.030283 | -0.026784 | -0.016578 | 0.002454 | 0.040843 | -0.005985 | 0.038003 | 61.6012 | 0.20284 | 61.5096 | -0.042259 | 0.029923 | 61.5753 | -0.006014 | 61.381 | 61.5171 | 61.46 | 61.4702 | 61.4893 | 61.5277 | 61.4808 | 61.5248 | 123.088 | 61.6897 | 122.9964 | 61.4446 | 61.5167 | 123.0621 | 61.4808 | 122.8678 | 61.5713 | 61.6072 | 61.4796 | 61.5156
1535.0625 | 123.381 | -61.4639 | 61.6333 | 0.025705 | -0.031363 | -0.012 | 0.007033 | 0.036265 | -0.005985 | 0.038003 | 61.6058 | 0.20742 | 61.5279 | -0.03768 | 0.029923 | 61.5799 | -0.006014 | 61.381 | 61.4896 | 61.4326 | 61.4519 | 61.471 | 61.5002 | 61.4579 | 61.5019 | 123.0697 | 61.6714 | 122.9918 | 61.4262 | 61.4939 | 123.0438 | 61.4579 | 122.8449 | 61.5759 | 61.6118 | 61.4979 | 61.5339
1536.0625 | 123.3948 | -61.4502 | 61.6287 | 0.021127 | -0.031363 | -0.021157 | 0.007033 | 0.040843 | -0.001406 | 0.038003 | 61.6104 | 0.20742 | 61.5462 | -0.051417 | 0.025345 | 61.5799 | -0.010593 | 61.3718 | 61.4713 | 61.4188 | 61.429 | 61.4572 | 61.491 | 61.4488 | 61.4882 | 123.0606 | 61.6576 | 122.9964 | 61.3988 | 61.4755 | 123.0301 | 61.4396 | 122.822 | 61.585 | 61.6209 | 61.5208 | 61.5568
1537.0625 | 123.3582 | -61.4777 | 61.6287 | 0.030283 | -0.031363 | -0.012 | 0.011611 | 0.040843 | -0.001406 | 0.033424 | 61.6104 | 0.20284 | 61.5416 | -0.042259 | 0.029923 | 61.5799 | -0.010593 | 61.3764 | 61.5079 | 61.4463 | 61.4657 | 61.4893 | 61.5185 | 61.4763 | 61.5111 | 123.088 | 61.6805 | 123.0193 | 61.4354 | 61.5076 | 123.0576 | 61.4671 | 122.8541 | 61.5804 | 61.6209 | 61.5117 | 61.5522
1538.0625 | 123.4222 | -61.4548 | 61.6058 | 0.025705 | -0.031363 | -0.016578 | 0.011611 | 0.036265 | -0.005985 | 0.033424 | 61.6012 | 0.20284 | 61.537 | -0.046838 | 0.034501 | 61.5845 | -0.001436 | 61.381 | 61.4805 | 61.4234 | 61.4382 | 61.4664 | 61.491 | 61.4488 | 61.4882 | 123.056 | 61.6576 | 122.9918 | 61.4079 | 61.4893 | 123.0392 | 61.4533 | 122.8357 | 61.5667 | 61.6026 | 61.5025 | 61.5385
1539.0625 | 123.2803 | -61.4548 | 61.6562 | 0.03944 | -0.031363 | -0.012 | 0.011611 | 0.045421 | -0.005985 | 0.028846 | 61.6104 | 0.20284 | 61.5096 | -0.042259 | 0.034501 | 61.5845 | -0.010593 | 61.3718 | 61.4942 | 61.4234 | 61.4428 | 61.4664 | 61.5002 | 61.4488 | 61.4836 | 123.0651 | 61.6576 | 122.9643 | 61.4125 | 61.4893 | 123.0392 | 61.4442 | 122.8266 | 61.5759 | 61.6209 | 61.4751 | 61.5202
1540.0625 | 123.3673 | -61.4639 | 61.6058 | 0.025705 | -0.035942 | -0.016578 | 0.007033 | 0.031687 | -0.005985 | 0.038003 | 61.6012 | 0.20284 | 61.4958 | -0.03768 | 0.029923 | 61.5845 | -0.006014 | 61.3764 | 61.4896 | 61.428 | 61.4474 | 61.471 | 61.4956 | 61.4579 | 61.5019 | 123.0651 | 61.6668 | 122.9598 | 61.4262 | 61.4939 | 123.0484 | 61.4579 | 122.8403 | 61.5713 | 61.6072 | 61.4659 | 61.5018
1541.0625 | 123.381 | -61.4685 | 61.6104 | 0.034862 | -0.035942 | -0.025735 | 0.007033 | 0.049999 | -0.005985 | 0.028846 | 61.6058 | 0.19827 | 61.4958 | -0.051417 | 0.025345 | 61.5845 | -0.001436 | 61.3764 | 61.5034 | 61.4326 | 61.4428 | 61.4755 | 61.5185 | 61.4625 | 61.4974 | 123.0743 | 61.6668 | 122.9643 | 61.4171 | 61.4939 | 123.053 | 61.4671 | 122.8449 | 61.5804 | 61.6072 | 61.4705 | 61.4973
1542.0625 | 123.4039 | -61.4639 | 61.6241 | 0.030283 | -0.031363 | -0.016578 | 0.002454 | 0.040843 | 0.00775 | 0.038003 | 61.6149 | 0.20284 | 61.5416 | -0.046838 | 0.029923 | 61.5753 | -0.001436 | 61.3764 | 61.4942 | 61.4326 | 61.4474 | 61.4664 | 61.5048 | 61.4717 | 61.5019 | 123.0789 | 61.6668 | 123.0055 | 61.4171 | 61.4939 | 123.0392 | 61.4625 | 122.8403 | 61.585 | 61.6164 | 61.5117 | 61.543
1543.0625 | 123.349 | -61.4548 | 61.5967 | 0.025705 | -0.031363 | -0.012 | 0.007033 | 0.036265 | 0.003172 | 0.033424 | 61.6058 | 0.19827 | 61.537 | -0.042259 | 0.020767 | 61.5753 | -0.001436 | 61.3764 | 61.4805 | 61.4234 | 61.4428 | 61.4618 | 61.491 | 61.4579 | 61.4882 | 123.0606 | 61.653 | 122.9918 | 61.4125 | 61.4755 | 123.0301 | 61.4533 | 122.8312 | 61.585 | 61.6072 | 61.5163 | 61.5385
1544.0625 | 123.3307 | -61.4502 | 61.6333 | 0.030283 | -0.026784 | -0.012 | 0.002454 | 0.031687 | 0.00775 | 0.042581 | 61.6012 | 0.212 | 61.5004 | -0.046838 | 0.029923 | 61.5753 | -0.015171 | 61.3718 | 61.4805 | 61.4234 | 61.4382 | 61.4526 | 61.4819 | 61.4579 | 61.4928 | 123.0514 | 61.6622 | 122.9506 | 61.4034 | 61.4801 | 123.0255 | 61.435 | 122.822 | 61.5713 | 61.6164 | 61.4705 | 61.5156
1545.0625 | 123.2391 | -61.5189 | 61.6425 | 0.034862 | -0.031363 | -0.016578 | 0.01619 | 0.045421 | -0.001406 | 0.042581 | 61.6104 | 0.19827 | 61.5004 | -0.03768 | 0.025345 | 61.5845 | -0.006014 | 61.381 | 61.5537 | 61.4875 | 61.5023 | 61.535 | 61.5643 | 61.5175 | 61.5614 | 123.1292 | 61.7171 | 123.0193 | 61.4812 | 61.5442 | 123.1033 | 61.5128 | 122.8998 | 61.585 | 61.6164 | 61.4751 | 61.5064
1546.0625 | 123.4085 | -61.4731 | 61.615 | 0.03944 | -0.031363 | -0.012 | 0.002454 | 0.040843 | -0.001406 | 0.038003 | 61.6058 | 0.20284 | 61.5141 | -0.042259 | 0.025345 | 61.5753 | -0.006014 | 61.381 | 61.5125 | 61.4417 | 61.4611 | 61.4755 | 61.5139 | 61.4717 | 61.5111 | 123.0789 | 61.6759 | 122.9872 | 61.4308 | 61.4984 | 123.0484 | 61.4671 | 122.8541 | 61.5804 | 61.6118 | 61.4888 | 61.5202
1547.0625 | 123.3719 | -61.4502 | 61.6104 | 0.03944 | -0.040521 | -0.012 | -0.002124 | 0.045421 | 0.003172 | 0.042581 | 61.6012 | 0.20742 | 61.5462 | -0.042259 | 0.029923 | 61.5845 | -0.015171 | 61.3764 | 61.4896 | 61.4097 | 61.4382 | 61.4481 | 61.4956 | 61.4534 | 61.4928 | 123.0514 | 61.6576 | 122.9964 | 61.4079 | 61.4801 | 123.0347 | 61.435 | 122.8266 | 61.5713 | 61.6164 | 61.5163 | 61.5614
1548.0625 | 123.3398 | -61.4868 | 61.6104 | 0.034862 | -0.026784 | -0.012 | 0.011611 | 0.040843 | 0.003172 | 0.033424 | 61.6104 | 0.20284 | 61.5141 | -0.042259 | 0.025345 | 61.5799 | 0.003143 | 61.3764 | 61.5217 | 61.46 | 61.4748 | 61.4984 | 61.5277 | 61.49 | 61.5202 | 123.0972 | 61.6897 | 123.001 | 61.4446 | 61.5122 | 123.0667 | 61.49 | 122.8632 | 61.585 | 61.6072 | 61.4888 | 61.511
1549.0625 | 123.3124 | -61.4731 | 61.6287 | 0.034862 | -0.035942 | -0.016578 | 0.007033 | 0.040843 | -0.001406 | 0.038003 | 61.6012 | 0.19827 | 61.5004 | -0.046838 | 0.025345 | 61.5845 | -0.001436 | 61.3718 | 61.5079 | 61.4371 | 61.4565 | 61.4801 | 61.5139 | 61.4717 | 61.5111 | 123.0743 | 61.6713 | 122.9735 | 61.4262 | 61.4984 | 123.0576 | 61.4716 | 122.8449 | 61.5759 | 61.6026 | 61.4751 | 61.5018
1550.0625 | 123.3353 | -61.4639 | 61.6608 | 0.025705 | -0.031363 | -0.012 | 0.01619 | 0.045421 | 0.003172 | 0.038003 | 61.6104 | 0.20742 | 61.5096 | -0.046838 | 0.025345 | 61.5891 | -0.006014 | 61.381 | 61.4896 | 61.4326 | 61.4519 | 61.4801 | 61.5093 | 61.4671 | 61.5019 | 123.0743 | 61.6714 | 122.9735 | 61.4171 | 61.4893 | 123.053 | 61.4579 | 122.8449 | 61.585 | 61.6164 | 61.4842 | 61.5156
1551.0625 | 123.3856 | -61.4639 | 61.5967 | 0.034862 | -0.031363 | -0.012 | 0.007033 | 0.040843 | -0.001406 | 0.051737 | 61.6058 | 0.19827 | 61.5462 | -0.051417 | 0.025345 | 61.5845 | -0.006014 | 61.381 | 61.4988 | 61.4326 | 61.4519 | 61.471 | 61.5048 | 61.4625 | 61.5157 | 123.0697 | 61.6622 | 123.0101 | 61.4125 | 61.4893 | 123.0484 | 61.4579 | 122.8449 | 61.5804 | 61.6118 | 61.5208 | 61.5522
1552.0625 | 123.349 | -61.4731 | 61.6013 | 0.034862 | -0.026784 | -0.012 | 0.007033 | 0.036265 | 0.003172 | 0.042581 | 61.6104 | 0.19827 | 61.5416 | -0.03768 | 0.029923 | 61.5845 | -0.006014 | 61.3764 | 61.5079 | 61.4463 | 61.4611 | 61.4801 | 61.5093 | 61.4763 | 61.5157 | 123.0834 | 61.6713 | 123.0147 | 61.4354 | 61.503 | 123.0576 | 61.4671 | 122.8495 | 61.5804 | 61.6164 | 61.5117 | 61.5476
1553.0625 | 123.3948 | -61.4731 | 61.6333 | 0.034862 | -0.031363 | -0.016578 | 0.007033 | 0.036265 | -0.005985 | 0.033424 | 61.6058 | 0.20284 | 61.4958 | -0.042259 | 0.025345 | 61.5799 | -0.001436 | 61.3764 | 61.5079 | 61.4417 | 61.4565 | 61.4801 | 61.5093 | 61.4671 | 61.5065 | 123.0789 | 61.6759 | 122.9689 | 61.4308 | 61.4984 | 123.053 | 61.4716 | 122.8495 | 61.5804 | 61.6072 | 61.4705 | 61.4973
1554.0625 | 123.3765 | -61.4685 | 61.6196 | 0.034862 | -0.031363 | -0.012 | 0.01619 | 0.045421 | -0.005985 | 0.038003 | 61.6012 | 0.19827 | 61.4912 | -0.046838 | 0.029923 | 61.5799 | -0.006014 | 61.3627 | 61.5034 | 61.4371 | 61.4565 | 61.4847 | 61.5139 | 61.4625 | 61.5065 | 123.0697 | 61.6668 | 122.9598 | 61.4217 | 61.4984 | 123.0484 | 61.4625 | 122.8312 | 61.5713 | 61.6072 | 61.4613 | 61.4973
1555.0625 | 123.2895 | -61.4502 | 61.6699 | 0.034862 | -0.031363 | -0.007421 | 0.007033 | 0.049999 | 0.00775 | 0.038003 | 61.6149 | 0.19827 | 61.537 | -0.042259 | 0.029923 | 61.5799 | -0.006014 | 61.381 | 61.4851 | 61.4188 | 61.4428 | 61.4572 | 61.5002 | 61.4579 | 61.4882 | 123.0651 | 61.6485 | 122.9872 | 61.4079 | 61.4801 | 123.0301 | 61.4442 | 122.8312 | 61.585 | 61.6209 | 61.5071 | 61.543
1556.0625 | 123.3032 | -61.4639 | 61.6287 | 0.034862 | -0.031363 | -0.012 | 0.007033 | 0.045421 | 0.003172 | 0.042581 | 61.6104 | 0.20742 | 61.5416 | -0.051417 | 0.025345 | 61.5753 | -0.010593 | 61.381 | 61.4988 | 61.4326 | 61.4519 | 61.471 | 61.5093 | 61.4671 | 61.5065 | 123.0743 | 61.6714 | 123.0055 | 61.4125 | 61.4893 | 123.0392 | 61.4533 | 122.8449 | 61.585 | 61.6209 | 61.5163 | 61.5522
1557.0625 | 123.2712 | -61.4868 | 61.6516 | 0.03944 | -0.031363 | -0.012 | 0.011611 | 0.036265 | -0.001406 | 0.038003 | 61.6104 | 0.20284 | 61.5233 | -0.051417 | 0.020767 | 61.5799 | -0.001436 | 61.3764 | 61.5263 | 61.4555 | 61.4748 | 61.4984 | 61.5231 | 61.4854 | 61.5248 | 123.0972 | 61.6897 | 123.0101 | 61.4354 | 61.5076 | 123.0667 | 61.4854 | 122.8632 | 61.5896 | 61.6118 | 61.5025 | 61.5247
1558.0625 | 123.3078 | -61.496 | 61.6196 | 0.034862 | -0.031363 | -0.016578 | 0.007033 | 0.040843 | 0.003172 | 0.033424 | 61.6058 | 0.20742 | 61.5004 | -0.046838 | 0.029923 | 61.5845 | -0.010593 | 61.3718 | 61.5308 | 61.4646 | 61.4794 | 61.503 | 61.5368 | 61.4991 | 61.5294 | 123.1017 | 61.7034 | 122.9964 | 61.4491 | 61.5259 | 123.0804 | 61.4854 | 122.8678 | 61.5759 | 61.6164 | 61.4705 | 61.511
1559.0625 | 123.3398 | -61.4914 | 61.6287 | 0.030283 | -0.031363 | -0.016578 | 0.002454 | 0.040843 | -0.001406 | 0.038003 | 61.6104 | 0.19827 | 61.505 | -0.042259 | 0.029923 | 61.5799 | -0.010593 | 61.381 | 61.5217 | 61.46 | 61.4748 | 61.4938 | 61.5322 | 61.49 | 61.5294 | 123.1018 | 61.6897 | 122.9964 | 61.4491 | 61.5213 | 123.0713 | 61.4808 | 122.8724 | 61.5804 | 61.6209 | 61.4751 | 61.5156
1560.0625 | 123.349 | -61.4822 | 61.615 | 0.030283 | -0.031363 | -0.016578 | 0.011611 | 0.036265 | -0.001406 | 0.042581 | 61.6058 | 0.20284 | 61.5416 | -0.051417 | 0.025345 | 61.5799 | -0.006014 | 61.3856 | 61.5125 | 61.4509 | 61.4657 | 61.4939 | 61.5185 | 61.4808 | 61.5248 | 123.088 | 61.6851 | 123.0238 | 61.4308 | 61.5076 | 123.0621 | 61.4762 | 122.8678 | 61.5804 | 61.6118 | 61.5163 | 61.5476
1561.0625 | 123.2803 | -61.5097 | 61.6333 | 0.034862 | -0.031363 | -0.016578 | 0.007033 | 0.040843 | 0.003172 | 0.038003 | 61.6058 | 0.20284 | 61.5416 | -0.042259 | 0.029923 | 61.5845 | -0.010593 | 61.3764 | 61.5446 | 61.4783 | 61.4931 | 61.5167 | 61.5505 | 61.5129 | 61.5477 | 123.1155 | 61.7126 | 123.0513 | 61.4674 | 61.5396 | 123.0942 | 61.4991 | 122.8861 | 61.5759 | 61.6164 | 61.5117 | 61.5522
1562.0625 | 123.3032 | -61.4914 | 61.6516 | 0.030283 | -0.035942 | -0.002842 | 0.007033 | 0.040843 | 0.003172 | 0.042581 | 61.6058 | 0.20284 | 61.5004 | -0.042259 | 0.020767 | 61.5845 | -0.006014 | 61.3718 | 61.5217 | 61.4555 | 61.4886 | 61.4984 | 61.5322 | 61.4946 | 61.534 | 123.0972 | 61.6942 | 122.9918 | 61.4491 | 61.5122 | 123.0759 | 61.4854 | 122.8632 | 61.585 | 61.6118 | 61.4796 | 61.5064
1563.0625 | 123.2437 | -61.4685 | 61.6379 | 0.034862 | -0.031363 | -0.021157 | 0.01619 | 0.040843 | -0.001406 | 0.028846 | 61.6012 | 0.20742 | 61.4958 | -0.042259 | 0.020767 | 61.5845 | -0.010593 | 61.3764 | 61.5034 | 61.4371 | 61.4473 | 61.4847 | 61.5093 | 61.4671 | 61.4974 | 123.0697 | 61.6759 | 122.9643 | 61.4262 | 61.4893 | 123.053 | 61.4579 | 122.8449 | 61.5804 | 61.6118 | 61.4751 | 61.5064
1564.0625 | 123.3719 | -61.4685 | 61.6333 | 0.03944 | -0.031363 | -0.016578 | 0.007033 | 0.036265 | 0.003172 | 0.038003 | 61.6104 | 0.19827 | 61.5324 | -0.046838 | 0.029923 | 61.5799 | -0.006014 | 61.3718 | 61.5079 | 61.4371 | 61.4519 | 61.4755 | 61.5048 | 61.4717 | 61.5065 | 123.0789 | 61.6668 | 123.001 | 61.4217 | 61.4984 | 123.0484 | 61.4625 | 122.8403 | 61.5804 | 61.6164 | 61.5025 | 61.5385
1565.0625 | 123.2437 | -61.5005 | 61.6379 | 0.034862 | -0.026784 | -0.012 | 0.007033 | 0.045421 | 0.003172 | 0.042581 | 61.6104 | 0.20742 | 61.537 | -0.03768 | 0.029923 | 61.5707 | -0.006014 | 61.3764 | 61.5354 | 61.4738 | 61.4885 | 61.5076 | 61.546 | 61.5037 | 61.5431 | 123.1109 | 61.708 | 123.0376 | 61.4629 | 61.5305 | 123.0713 | 61.4945 | 122.8769 | 61.5804 | 61.6164 | 61.5071 | 61.543
1566.0625 | 123.2437 | -61.5234 | 61.6241 | 0.025705 | -0.026784 | -0.012 | 0.011611 | 0.040843 | 0.003172 | 0.033424 | 61.6149 | 0.19827 | 61.5141 | -0.046838 | 0.020767 | 61.5753 | -0.006014 | 61.381 | 61.5491 | 61.4967 | 61.5114 | 61.535 | 61.5643 | 61.5266 | 61.5569 | 123.1384 | 61.7217 | 123.0376 | 61.4766 | 61.5442 | 123.0988 | 61.5174 | 122.9044 | 61.5942 | 61.6209 | 61.4934 | 61.5202
1567.0625 | 123.2346 | -61.5051 | 61.6425 | 0.03944 | -0.035942 | -0.012 | 0.007033 | 0.036265 | 0.003172 | 0.038003 | 61.6012 | 0.19369 | 61.5004 | -0.046838 | 0.029923 | 61.5799 | -0.010593 | 61.3672 | 61.5446 | 61.4692 | 61.4931 | 61.5122 | 61.5414 | 61.5083 | 61.5431 | 123.1063 | 61.6988 | 123.0055 | 61.4583 | 61.535 | 123.085 | 61.4945 | 122.8724 | 61.5713 | 61.6118 | 61.4705 | 61.511
1568.0625 | 123.2986 | -61.4822 | 61.647 | 0.030283 | -0.031363 | -0.012 | 0.002454 | 0.040843 | -0.001406 | 0.042581 | 61.6058 | 0.20284 | 61.5141 | -0.042259 | 0.029923 | 61.5753 | -0.010593 | 61.3764 | 61.5125 | 61.4509 | 61.4702 | 61.4847 | 61.5231 | 61.4808 | 61.5248 | 123.088 | 61.6851 | 122.9964 | 61.44 | 61.5122 | 123.0576 | 61.4716 | 122.8586 | 61.5759 | 61.6164 | 61.4842 | 61.5247
1569.0625 | 123.4039 | -61.4731 | 61.5875 | 0.03944 | -0.031363 | -0.016578 | 0.002454 | 0.036265 | -0.001406 | 0.042581 | 61.6058 | 0.20742 | 61.537 | -0.042259 | 0.029923 | 61.5799 | -0.015171 | 61.3672 | 61.5125 | 61.4417 | 61.4565 | 61.4755 | 61.5093 | 61.4717 | 61.5157 | 123.0789 | 61.6805 | 123.0101 | 61.4308 | 61.503 | 123.053 | 61.4579 | 122.8403 | 61.5759 | 61.6209 | 61.5071 | 61.5522
1570.0625 | 123.2986 | -61.4914 | 61.647 | 0.034862 | -0.035942 | -0.002842 | 0.007033 | 0.040843 | -0.005985 | 0.038003 | 61.6104 | 0.20742 | 61.5279 | -0.042259 | 0.034501 | 61.5753 | -0.001436 | 61.3764 | 61.5263 | 61.4555 | 61.4886 | 61.4984 | 61.5322 | 61.4854 | 61.5294 | 123.1018 | 61.6988 | 123.0193 | 61.4491 | 61.5259 | 123.0667 | 61.49 | 122.8678 | 61.5759 | 61.6118 | 61.4934 | 61.5293
1571.0625 | 123.3307 | -61.4822 | 61.647 | 0.030283 | -0.026784 | -0.016578 | 0.007033 | 0.040843 | -0.001406 | 0.038003 | 61.6058 | 0.20742 | 61.4958 | -0.046838 | 0.025345 | 61.5799 | 0.003143 | 61.3718 | 61.5125 | 61.4555 | 61.4657 | 61.4893 | 61.5231 | 61.4808 | 61.5202 | 123.088 | 61.6897 | 122.9781 | 61.4354 | 61.5076 | 123.0621 | 61.4854 | 122.8541 | 61.5804 | 61.6026 | 61.4705 | 61.4927
1572.0625 | 123.2666 | -61.4914 | 61.6608 | 0.03944 | -0.035942 | -0.007421 | 0.011611 | 0.040843 | 0.003172 | 0.047159 | 61.6104 | 0.20284 | 61.505 | -0.051417 | 0.025345 | 61.5799 | -0.006014 | 61.381 | 61.5308 | 61.4555 | 61.484 | 61.503 | 61.5322 | 61.4946 | 61.5386 | 123.1018 | 61.6942 | 122.9964 | 61.44 | 61.5167 | 123.0713 | 61.4854 | 122.8724 | 61.585 | 61.6164 | 61.4796 | 61.511
1573.0625 | 123.2437 | -61.5097 | 61.6699 | 0.03944 | -0.035942 | -0.007421 | 0.01619 | 0.045421 | 0.003172 | 0.038003 | 61.6104 | 0.19827 | 61.5462 | -0.03768 | 0.034501 | 61.5799 | -0.010593 | 61.381 | 61.5491 | 61.4738 | 61.5023 | 61.5259 | 61.5551 | 61.5129 | 61.5477 | 123.1201 | 61.708 | 123.0559 | 61.472 | 61.5442 | 123.0896 | 61.4991 | 122.8907 | 61.5759 | 61.6209 | 61.5117 | 61.5568
1574.0625 | 123.381 | -61.4594 | 61.6058 | 0.030283 | -0.031363 | -0.012 | 0.011611 | 0.045421 | -0.001406 | 0.038003 | 61.6012 | 0.19827 | 61.5416 | -0.042259 | 0.020767 | 61.5845 | -0.006014 | 61.3764 | 61.4896 | 61.428 | 61.4474 | 61.471 | 61.5048 | 61.4579 | 61.4974 | 123.0606 | 61.6576 | 123.001 | 61.4171 | 61.4801 | 123.0438 | 61.4533 | 122.8357 | 61.5804 | 61.6072 | 61.5208 | 61.5476
1575.0625 | 123.2483 | -61.4685 | 61.647 | 0.03944 | -0.026784 | -0.012 | 0.011611 | 0.040843 | 0.00775 | 0.038003 | 61.6058 | 0.20284 | 61.505 | -0.046838 | 0.025345 | 61.5845 | -0.006014 | 61.3718 | 61.5079 | 61.4417 | 61.4565 | 61.4801 | 61.5093 | 61.4763 | 61.5065 | 123.0743 | 61.6714 | 122.9735 | 61.4217 | 61.4939 | 123.053 | 61.4625 | 122.8403 | 61.5804 | 61.6118 | 61.4796 | 61.511
1576.0625 | 123.2529 | -61.5234 | 61.647 | 0.034862 | -0.040521 | -0.012 | 0.011611 | 0.040843 | -0.001406 | 0.042581 | 61.6104 | 0.20284 | 61.4958 | -0.03768 | 0.029923 | 61.5845 | -0.006014 | 61.3718 | 61.5583 | 61.4829 | 61.5114 | 61.535 | 61.5643 | 61.522 | 61.566 | 123.1338 | 61.7263 | 123.0193 | 61.4858 | 61.5534 | 123.1079 | 61.5174 | 122.8953 | 61.5804 | 61.6164 | 61.4659 | 61.5018
1577.0625 | 123.3261 | -61.4731 | 61.6379 | 0.044018 | -0.031363 | -0.016578 | 0.007033 | 0.045421 | -0.001406 | 0.042581 | 61.6104 | 0.20284 | 61.5141 | -0.046838 | 0.029923 | 61.5799 | -0.006014 | 61.3718 | 61.5171 | 61.4417 | 61.4565 | 61.4801 | 61.5185 | 61.4717 | 61.5157 | 123.0834 | 61.6759 | 122.9872 | 61.4262 | 61.503 | 123.053 | 61.4671 | 122.8449 | 61.5804 | 61.6164 | 61.4842 | 61.5202
1578.0625 | 123.262 | -61.4777 | 61.6516 | 0.030283 | -0.031363 | -0.016578 | 0.01619 | 0.045421 | 0.003172 | 0.038003 | 61.6149 | 0.20284 | 61.5416 | -0.046838 | 0.029923 | 61.5799 | -0.001436 | 61.381 | 61.5079 | 61.4463 | 61.4611 | 61.4939 | 61.5231 | 61.4808 | 61.5157 | 123.0926 | 61.6805 | 123.0193 | 61.4308 | 61.5076 | 123.0576 | 61.4762 | 122.8586 | 61.585 | 61.6164 | 61.5117 | 61.543
1579.0625 | 123.3078 | -61.4914 | 61.6241 | 0.034862 | -0.035942 | -0.012 | 0.007033 | 0.036265 | -0.001406 | 0.038003 | 61.6195 | 0.20284 | 61.5462 | -0.055996 | 0.020767 | 61.5753 | -0.006014 | 61.3764 | 61.5263 | 61.4555 | 61.4794 | 61.4984 | 61.5277 | 61.49 | 61.5294 | 123.1109 | 61.6942 | 123.0376 | 61.4354 | 61.5122 | 123.0667 | 61.4854 | 122.8678 | 61.5987 | 61.6255 | 61.5254 | 61.5522
1580.0625 | 123.2483 | -61.5005 | 61.6241 | 0.034862 | -0.031363 | -0.021157 | 0.007033 | 0.045421 | 0.003172 | 0.047159 | 61.6104 | 0.20742 | 61.5416 | -0.042259 | 0.029923 | 61.5753 | -0.006014 | 61.381 | 61.5354 | 61.4692 | 61.4794 | 61.5076 | 61.546 | 61.5037 | 61.5477 | 123.1109 | 61.708 | 123.0422 | 61.4583 | 61.5305 | 123.0759 | 61.4945 | 122.8815 | 61.5804 | 61.6164 | 61.5117 | 61.5476
1581.0625 | 123.2803 | -61.4868 | 61.6745 | 0.034862 | -0.040521 | -0.012 | 0.011611 | 0.045421 | -0.001406 | 0.042581 | 61.6104 | 0.20742 | 61.5004 | -0.042259 | 0.025345 | 61.5799 | -0.015171 | 61.3672 | 61.5217 | 61.4463 | 61.4748 | 61.4984 | 61.5322 | 61.4854 | 61.5294 | 123.0972 | 61.6942 | 122.9872 | 61.4446 | 61.5122 | 123.0667 | 61.4716 | 122.8541 | 61.585 | 61.6255 | 61.4751 | 61.5156
1582.0625 | 123.2803 | -61.5189 | 61.6425 | 0.034862 | -0.022205 | -0.025735 | 0.011611 | 0.040843 | 0.003172 | 0.038003 | 61.6104 | 0.19827 | 61.5096 | -0.046838 | 0.029923 | 61.5845 | -0.006014 | 61.3764 | 61.5537 | 61.4967 | 61.4931 | 61.5305 | 61.5597 | 61.522 | 61.5569 | 123.1292 | 61.7171 | 123.0284 | 61.472 | 61.5488 | 123.1033 | 61.5128 | 122.8953 | 61.5804 | 61.6164 | 61.4796 | 61.5156
1583.0625 | 123.262 | -61.5143 | 61.6653 | 0.03944 | -0.031363 | -0.007421 | 0.011611 | 0.040843 | -0.001406 | 0.042581 | 61.6104 | 0.20742 | 61.5416 | -0.051417 | 0.016188 | 61.5753 | -0.006014 | 61.3764 | 61.5537 | 61.4829 | 61.5069 | 61.5259 | 61.5551 | 61.5129 | 61.5569 | 123.1246 | 61.7217 | 123.0559 | 61.4629 | 61.5305 | 123.0896 | 61.5083 | 122.8907 | 61.5942 | 61.6164 | 61.5254 | 61.5476
1584.0625 | 123.3719 | -61.4639 | 61.5829 | 0.034862 | -0.035942 | -0.016578 | 0.007033 | 0.031687 | -0.005985 | 0.042581 | 61.6149 | 0.20284 | 61.537 | -0.051417 | 0.025345 | 61.5799 | -0.001436 | 61.381 | 61.4988 | 61.428 | 61.4474 | 61.471 | 61.4956 | 61.4579 | 61.5065 | 123.0789 | 61.6668 | 123.001 | 61.4125 | 61.4893 | 123.0438 | 61.4625 | 122.8449 | 61.5896 | 61.6164 | 61.5117 | 61.5385
1585.0625 | 123.2803 | -61.5005 | 61.6287 | 0.025705 | -0.031363 | -0.007421 | 0.007033 | 0.040843 | 0.003172 | 0.042581 | 61.6149 | 0.20742 | 61.505 | -0.046838 | 0.034501 | 61.5845 | -0.006014 | 61.3764 | 61.5263 | 61.4692 | 61.4931 | 61.5076 | 61.5414 | 61.5037 | 61.5431 | 123.1155 | 61.708 | 123.0055 | 61.4537 | 61.535 | 123.085 | 61.4945 | 122.8769 | 61.5804 | 61.6209 | 61.4705 | 61.511
1586.0625 | 123.3078 | -61.4822 | 61.647 | 0.034862 | -0.031363 | -0.016578 | 0.007033 | 0.031687 | -0.001406 | 0.033424 | 61.6058 | 0.20742 | 61.505 | -0.046838 | 0.020767 | 61.5799 | -0.006014 | 61.3764 | 61.5171 | 61.4509 | 61.4657 | 61.4893 | 61.5139 | 61.4808 | 61.5157 | 123.088 | 61.6897 | 122.9872 | 61.4354 | 61.503 | 123.0621 | 61.4762 | 122.8586 | 61.585 | 61.6118 | 61.4842 | 61.511
1587.0625 | 123.3078 | -61.5189 | 61.6333 | 0.030283 | -0.026784 | -0.007421 | 0.007033 | 0.045421 | 0.00775 | 0.038003 | 61.6058 | 0.20284 | 61.5324 | -0.046838 | 0.025345 | 61.5845 | -0.010593 | 61.3764 | 61.5491 | 61.4921 | 61.5114 | 61.5259 | 61.5643 | 61.5266 | 61.5569 | 123.1246 | 61.7217 | 123.0513 | 61.472 | 61.5442 | 123.1033 | 61.5083 | 122.8953 | 61.5804 | 61.6164 | 61.5071 | 61.543
1588.0625 | 123.2986 | -61.5143 | 61.6287 | 0.034862 | -0.026784 | -0.007421 | 0.002454 | 0.045421 | -0.001406 | 0.033424 | 61.6195 | 0.20742 | 61.5416 | -0.046838 | 0.025345 | 61.5753 | -0.010593 | 61.3718 | 61.5491 | 61.4875 | 61.5069 | 61.5167 | 61.5597 | 61.5129 | 61.5477 | 123.1338 | 61.7217 | 123.0559 | 61.4674 | 61.5396 | 123.0896 | 61.5037 | 122.8861 | 61.5942 | 61.6301 | 61.5163 | 61.5522
1589.0625 | 123.3902 | -61.4639 | 61.5784 | 0.034862 | -0.031363 | -0.016578 | 0.007033 | 0.045421 | -0.005985 | 0.038003 | 61.5966 | 0.20284 | 61.5004 | -0.046838 | 0.029923 | 61.5799 | -0.006014 | 61.3672 | 61.4988 | 61.4326 | 61.4474 | 61.471 | 61.5093 | 61.4579 | 61.5019 | 123.0605 | 61.6668 | 122.9643 | 61.4171 | 61.4939 | 123.0438 | 61.4579 | 122.8312 | 61.5667 | 61.6026 | 61.4705 | 61.5064
1590.0625 | 123.2895 | -61.5005 | 61.6287 | 0.034862 | -0.031363 | -0.016578 | 0.007033 | 0.040843 | -0.001406 | 0.047159 | 61.6058 | 0.20284 | 61.5096 | -0.046838 | 0.020767 | 61.5799 | -0.010593 | 61.381 | 61.5354 | 61.4692 | 61.484 | 61.5076 | 61.5414 | 61.4991 | 61.5477 | 123.1063 | 61.7034 | 123.0101 | 61.4537 | 61.5213 | 123.0804 | 61.49 | 122.8815 | 61.585 | 61.6164 | 61.4888 | 61.5202
1591.0625 | 123.23 | -61.4914 | 61.6425 | 0.034862 | -0.031363 | -0.016578 | 0.007033 | 0.040843 | -0.001406 | 0.042581 | 61.6058 | 0.19827 | 61.5416 | -0.051417 | 0.025345 | 61.5845 | -0.006014 | 61.3764 | 61.5263 | 61.46 | 61.4748 | 61.4984 | 61.5322 | 61.49 | 61.534 | 123.0972 | 61.6897 | 123.033 | 61.44 | 61.5167 | 123.0759 | 61.4854 | 122.8678 | 61.5804 | 61.6118 | 61.5163 | 61.5476
1592.0625 | 123.262 | -61.5005 | 61.6425 | 0.025705 | -0.031363 | -0.012 | 0.011611 | 0.045421 | -0.001406 | 0.042581 | 61.6149 | 0.20284 | 61.5416 | -0.046838 | 0.025345 | 61.5753 | -0.015171 | 61.3764 | 61.5263 | 61.4692 | 61.4885 | 61.5122 | 61.546 | 61.4991 | 61.5431 | 123.1155 | 61.7034 | 123.0422 | 61.4537 | 61.5259 | 123.0759 | 61.4854 | 122.8769 | 61.5896 | 61.6301 | 61.5163 | 61.5568
1593.0625 | 123.2529 | -61.496 | 61.6241 | 0.025705 | -0.031363 | -0.016578 | 0.011611 | 0.045421 | -0.001406 | 0.038003 | 61.6104 | 0.19827 | 61.5096 | -0.051417 | 0.025345 | 61.5753 | -0.010593 | 61.381 | 61.5217 | 61.4646 | 61.4794 | 61.5076 | 61.5414 | 61.4946 | 61.534 | 123.1063 | 61.6942 | 123.0055 | 61.4446 | 61.5213 | 123.0713 | 61.4854 | 122.8769 | 61.585 | 61.6209 | 61.4842 | 61.5202
1594.0625 | 123.3307 | -61.4868 | 61.6196 | 0.030283 | -0.040521 | -0.016578 | 0.011611 | 0.040843 | 0.003172 | 0.038003 | 61.6012 | 0.20742 | 61.5004 | -0.051417 | 0.025345 | 61.5845 | -0.010593 | 61.3764 | 61.5171 | 61.4463 | 61.4702 | 61.4984 | 61.5277 | 61.49 | 61.5248 | 123.088 | 61.6942 | 122.9872 | 61.4354 | 61.5122 | 123.0713 | 61.4762 | 122.8632 | 61.5759 | 61.6118 | 61.4751 | 61.511
1595.0625 | 123.2666 | -61.4914 | 61.6333 | 0.03944 | -0.031363 | -0.016578 | 0.011611 | 0.040843 | -0.001406 | 0.042581 | 61.6149 | 0.19827 | 61.5462 | -0.03768 | 0.020767 | 61.5845 | -0.001436 | 61.3718 | 61.5308 | 61.46 | 61.4748 | 61.503 | 61.5322 | 61.49 | 61.534 | 123.1063 | 61.6897 | 123.0376 | 61.4537 | 61.5122 | 123.0759 | 61.49 | 122.8632 | 61.5942 | 61.6164 | 61.5254 | 61.5476
1596.0625 | 123.3353 | -61.4822 | 61.6699 | 0.034862 | -0.026784 | -0.021157 | 0.011611 | 0.040843 | 0.00775 | 0.042581 | 61.6104 | 0.19827 | 61.5416 | -0.046838 | 0.016188 | 61.5845 | -0.010593 | 61.381 | 61.5171 | 61.4555 | 61.4611 | 61.4939 | 61.5231 | 61.49 | 61.5248 | 123.0926 | 61.6805 | 123.0238 | 61.4354 | 61.4984 | 123.0667 | 61.4716 | 122.8632 | 61.5942 | 61.6209 | 61.5254 | 61.5522
1597.0625 | 123.2529 | -61.496 | 61.6241 | 0.034862 | -0.031363 | -0.016578 | 0.007033 | 0.036265 | 0.003172 | 0.042581 | 61.6058 | 0.19827 | 61.505 | -0.046838 | 0.029923 | 61.5799 | -0.010593 | 61.3718 | 61.5308 | 61.4646 | 61.4794 | 61.503 | 61.5322 | 61.4991 | 61.5386 | 123.1017 | 61.6942 | 123.001 | 61.4491 | 61.5259 | 123.0759 | 61.4854 | 122.8678 | 61.5759 | 61.6164 | 61.4751 | 61.5156
1598.0625 | 123.262 | -61.4914 | 61.6562 | 0.03944 | -0.026784 | -0.016578 | 0.011611 | 0.040843 | -0.005985 | 0.028846 | 61.6058 | 0.20284 | 61.5004 | -0.046838 | 0.025345 | 61.5845 | -0.015171 | 61.3672 | 61.5308 | 61.4646 | 61.4748 | 61.503 | 61.5322 | 61.4854 | 61.5202 | 123.0972 | 61.6942 | 122.9918 | 61.4446 | 61.5167 | 123.0759 | 61.4762 | 122.8586 | 61.5804 | 61.6209 | 61.4751 | 61.5156
1599.0625 | 123.2758 | -61.496 | 61.6425 | 0.03944 | -0.035942 | -0.016578 | 0.011611 | 0.040843 | 0.003172 | 0.038003 | 61.6058 | 0.20284 | 61.5233 | -0.042259 | 0.025345 | 61.5799 | -0.006014 | 61.3856 | 61.5354 | 61.46 | 61.4794 | 61.5076 | 61.5368 | 61.4991 | 61.534 | 123.1017 | 61.6988 | 123.0193 | 61.4537 | 61.5213 | 123.0759 | 61.49 | 122.8815 | 61.5804 | 61.6118 | 61.4979 | 61.5293
1600.0625 | 123.2529 | -61.5463 | 61.615 | 0.030283 | -0.031363 | -0.016578 | 0.01619 | 0.045421 | 0.012329 | 0.042581 | 61.6149 | 0.20284 | 61.5416 | -0.046838 | 0.025345 | 61.5799 | -0.006014 | 61.3672 | 61.5766 | 61.515 | 61.5297 | 61.5625 | 61.5917 | 61.5587 | 61.5889 | 123.1613 | 61.7492 | 123.0879 | 61.4995 | 61.5717 | 123.1262 | 61.5403 | 122.9136 | 61.5896 | 61.6209 | 61.5163 | 61.5476
1601.0625 | 123.2529 | -61.5189 | 61.6516 | 0.030283 | -0.026784 | -0.012 | 0.007033 | 0.040843 | -0.001406 | 0.038003 | 61.6195 | 0.20284 | 61.5324 | -0.051417 | 0.034501 | 61.5753 | -0.010593 | 61.381 | 61.5491 | 61.4921 | 61.5069 | 61.5259 | 61.5597 | 61.5175 | 61.5569 | 123.1384 | 61.7217 | 123.0513 | 61.4674 | 61.5534 | 123.0942 | 61.5083 | 122.8998 | 61.585 | 61.6301 | 61.4979 | 61.543
1602.0625 | 123.262 | -61.5005 | 61.6425 | 0.034862 | -0.031363 | -0.012 | 0.011611 | 0.045421 | -0.005985 | 0.033424 | 61.6012 | 0.20284 | 61.5187 | -0.042259 | 0.025345 | 61.5799 | -0.006014 | 61.3764 | 61.5354 | 61.4692 | 61.4885 | 61.5122 | 61.546 | 61.4946 | 61.534 | 123.1017 | 61.7034 | 123.0193 | 61.4583 | 61.5259 | 123.0804 | 61.4945 | 122.8769 | 61.5759 | 61.6072 | 61.4934 | 61.5247
1603.0625 | 123.262 | -61.5005 | 61.6653 | 0.034862 | -0.035942 | -0.007421 | 0.002454 | 0.036265 | 0.003172 | 0.042581 | 61.6104 | 0.19369 | 61.5187 | -0.046838 | 0.025345 | 61.5845 | 0.003143 | 61.3718 | 61.5354 | 61.4646 | 61.4931 | 61.503 | 61.5368 | 61.5037 | 61.5431 | 123.1109 | 61.6942 | 123.0193 | 61.4537 | 61.5259 | 123.085 | 61.5037 | 122.8724 | 61.585 | 61.6072 | 61.4934 | 61.5156
1604.0625 | 123.3444 | -61.5005 | 61.5875 | 0.034862 | -0.026784 | -0.012 | 0.002454 | 0.036265 | -0.005985 | 0.038003 | 61.6058 | 0.20742 | 61.5462 | -0.046838 | 0.025345 | 61.5753 | -0.006014 | 61.3718 | 61.5354 | 61.4738 | 61.4885 | 61.503 | 61.5368 | 61.4946 | 61.5386 | 123.1063 | 61.708 | 123.0467 | 61.4537 | 61.5259 | 123.0759 | 61.4945 | 122.8724 | 61.5804 | 61.6118 | 61.5208 | 61.5522
1605.0625 | 123.3444 | -61.4639 | 61.6425 | 0.03944 | -0.031363 | -0.021157 | 0.007033 | 0.045421 | 0.003172 | 0.042581 | 61.6104 | 0.20742 | 61.537 | -0.03768 | 0.029923 | 61.5799 | -0.006014 | 61.3764 | 61.5034 | 61.4326 | 61.4428 | 61.471 | 61.5093 | 61.4671 | 61.5065 | 123.0743 | 61.6714 | 123.001 | 61.4262 | 61.4939 | 123.0438 | 61.4579 | 122.8403 | 61.5804 | 61.6164 | 61.5071 | 61.543
1606.0625 | 123.3215 | -61.4777 | 61.6516 | 0.03944 | -0.026784 | -0.016578 | 0.007033 | 0.040843 | -0.001406 | 0.047159 | 61.6104 | 0.19827 | 61.505 | -0.046838 | 0.029923 | 61.5799 | -0.006014 | 61.3718 | 61.5171 | 61.4509 | 61.4611 | 61.4847 | 61.5185 | 61.4763 | 61.5248 | 123.088 | 61.6759 | 122.9826 | 61.4308 | 61.5076 | 123.0576 | 61.4716 | 122.8495 | 61.5804 | 61.6164 | 61.4751 | 61.511
1607.0625 | 123.2758 | -61.496 | 61.6653 | 0.030283 | -0.031363 | -0.016578 | 0.011611 | 0.045421 | 0.003172 | 0.042581 | 61.6104 | 0.20284 | 61.5141 | -0.03768 | 0.034501 | 61.5845 | -0.006014 | 61.3718 | 61.5263 | 61.4646 | 61.4794 | 61.5076 | 61.5414 | 61.4991 | 61.5386 | 123.1063 | 61.6988 | 123.0101 | 61.4583 | 61.5305 | 123.0804 | 61.49 | 122.8678 | 61.5759 | 61.6164 | 61.4796 | 61.5202
1608.0625 | 123.2803 | -61.4731 | 61.6653 | 0.034862 | -0.031363 | -0.012 | 0.011611 | 0.045421 | 0.003172 | 0.042581 | 61.6149 | 0.20742 | 61.5508 | -0.046838 | 0.020767 | 61.5753 | -0.001436 | 61.3764 | 61.5079 | 61.4417 | 61.4611 | 61.4847 | 61.5185 | 61.4763 | 61.5157 | 123.088 | 61.6805 | 123.0238 | 61.4262 | 61.4939 | 123.0484 | 61.4716 | 122.8495 | 61.5942 | 61.6164 | 61.53 | 61.5522
1609.0625 | 123.262 | -61.496 | 61.6379 | 0.034862 | -0.026784 | -0.021157 | 0.007033 | 0.040843 | -0.001406 | 0.042581 | 61.6104 | 0.20284 | 61.5508 | -0.051417 | 0.034501 | 61.5799 | -0.010593 | 61.3764 | 61.5308 | 61.4692 | 61.4748 | 61.503 | 61.5368 | 61.4946 | 61.5386 | 123.1063 | 61.6988 | 123.0467 | 61.4446 | 61.5305 | 123.0759 | 61.4854 | 122.8724 | 61.5759 | 61.6209 | 61.5163 | 61.5614
1610.0625 | 123.2941 | -61.4777 | 61.6425 | 0.034862 | -0.026784 | -0.007421 | 0.011611 | 0.040843 | -0.001406 | 0.038003 | 61.6149 | 0.20284 | 61.5462 | -0.051417 | 0.025345 | 61.5845 | -0.006014 | 61.3764 | 61.5125 | 61.4509 | 61.4702 | 61.4893 | 61.5185 | 61.4763 | 61.5157 | 123.0926 | 61.6805 | 123.0238 | 61.4262 | 61.503 | 123.0621 | 61.4716 | 122.8541 | 61.5896 | 61.6209 | 61.5208 | 61.5522
1611.0625 | 123.3398 | -61.4822 | 61.6608 | 0.025705 | -0.035942 | -0.012 | 0.01619 | 0.045421 | 0.003172 | 0.042581 | 61.6104 | 0.20742 | 61.5324 | -0.03768 | 0.029923 | 61.5891 | -0.001436 | 61.381 | 61.5079 | 61.4463 | 61.4702 | 61.4984 | 61.5277 | 61.4854 | 61.5248 | 123.0926 | 61.6897 | 123.0147 | 61.4446 | 61.5122 | 123.0713 | 61.4808 | 122.8632 | 61.5804 | 61.6118 | 61.5025 | 61.5339
1612.0625 | 123.2758 | -61.496 | 61.6653 | 0.034862 | -0.031363 | -0.012 | 0.007033 | 0.031687 | 0.003172 | 0.047159 | 61.6104 | 0.19827 | 61.5233 | -0.051417 | 0.029923 | 61.5753 | 0.003143 | 61.381 | 61.5308 | 61.4646 | 61.484 | 61.503 | 61.5277 | 61.4991 | 61.5431 | 123.1063 | 61.6942 | 123.0193 | 61.4446 | 61.5259 | 123.0713 | 61.4991 | 122.8769 | 61.5804 | 61.6072 | 61.4934 | 61.5202
1613.0625 | 123.2803 | -61.4868 | 61.6974 | 0.034862 | -0.031363 | -0.012 | 0.011611 | 0.040843 | -0.001406 | 0.042581 | 61.6149 | 0.20284 | 61.5141 | -0.042259 | 0.029923 | 61.5845 | -0.010593 | 61.3627 | 61.5217 | 61.4555 | 61.4748 | 61.4984 | 61.5277 | 61.4854 | 61.5294 | 123.1017 | 61.6897 | 123.001 | 61.4446 | 61.5167 | 123.0713 | 61.4762 | 122.8495 | 61.585 | 61.6255 | 61.4842 | 61.5247
1614.0625 | 123.2712 | -61.5189 | 61.6333 | 0.030283 | -0.031363 | -0.016578 | 0.002454 | 0.045421 | 0.00775 | 0.038003 | 61.6104 | 0.20284 | 61.5416 | -0.046838 | 0.029923 | 61.5799 | -0.010593 | 61.381 | 61.5491 | 61.4875 | 61.5023 | 61.5213 | 61.5643 | 61.5266 | 61.5569 | 123.1292 | 61.7217 | 123.0605 | 61.472 | 61.5488 | 123.0988 | 61.5083 | 122.8998 | 61.5804 | 61.6209 | 61.5117 | 61.5522
1615.0625 | 123.3215 | -61.4822 | 61.6653 | 0.034862 | -0.031363 | -0.016578 | 0.011611 | 0.045421 | 0.00775 | 0.038003 | 61.6149 | 0.20742 | 61.5553 | -0.042259 | 0.029923 | 61.5891 | -0.010593 | 61.3764 | 61.5171 | 61.4509 | 61.4657 | 61.4939 | 61.5277 | 61.49 | 61.5202 | 123.0972 | 61.6897 | 123.0376 | 61.44 | 61.5122 | 123.0713 | 61.4716 | 122.8586 | 61.585 | 61.6255 | 61.5254 | 61.5659
1616.0625 | 123.2666 | -61.5097 | 61.6653 | 0.030283 | -0.031363 | -0.016578 | 0.007033 | 0.040843 | -0.001406 | 0.042581 | 61.6149 | 0.20284 | 61.5279 | -0.042259 | 0.025345 | 61.5799 | -0.010593 | 61.3764 | 61.54 | 61.4783 | 61.4931 | 61.5167 | 61.5505 | 61.5083 | 61.5523 | 123.1246 | 61.7126 | 123.0376 | 61.4674 | 61.535 | 123.0896 | 61.4991 | 122.8861 | 61.5896 | 61.6255 | 61.5025 | 61.5385
1617.0625 | 123.2895 | -61.5005 | 61.6791 | 0.025705 | -0.026784 | -0.012 | 0.011611 | 0.040843 | -0.005985 | 0.033424 | 61.6104 | 0.20284 | 61.5096 | -0.051417 | 0.025345 | 61.5845 | -0.006014 | 61.3764 | 61.5263 | 61.4738 | 61.4885 | 61.5122 | 61.5414 | 61.4946 | 61.534 | 123.1109 | 61.7034 | 123.0101 | 61.4491 | 61.5259 | 123.085 | 61.4945 | 122.8769 | 61.585 | 61.6164 | 61.4842 | 61.5156
1618.0625 | 123.2346 | -61.4822 | 61.6928 | 0.034862 | -0.031363 | -0.012 | 0.011611 | 0.040843 | -0.010563 | 0.047159 | 61.6104 | 0.19827 | 61.5279 | -0.051417 | 0.034501 | 61.5845 | -0.006014 | 61.3764 | 61.5171 | 61.4509 | 61.4702 | 61.4939 | 61.5231 | 61.4717 | 61.5294 | 123.0926 | 61.6805 | 123.0101 | 61.4308 | 61.5167 | 123.0667 | 61.4762 | 122.8586 | 61.5759 | 61.6164 | 61.4934 | 61.5339
1619.0625 | 123.2574 | -61.4868 | 61.6699 | 0.03944 | -0.031363 | -0.016578 | 0.011611 | 0.045421 | -0.001406 | 0.038003 | 61.6241 | 0.20742 | 61.5508 | -0.046838 | 0.025345 | 61.5799 | -0.001436 | 61.3764 | 61.5263 | 61.4555 | 61.4702 | 61.4984 | 61.5322 | 61.4854 | 61.5248 | 123.1109 | 61.6942 | 123.0376 | 61.44 | 61.5122 | 123.0667 | 61.4854 | 122.8632 | 61.5987 | 61.6255 | 61.5254 | 61.5522
1620.0625 | 123.2712 | -61.4548 | 61.6882 | 0.030283 | -0.026784 | -0.016578 | 0.011611 | 0.045421 | 0.003172 | 0.038003 | 61.6104 | 0.20742 | 61.5462 | -0.046838 | 0.034501 | 61.5799 | -0.001436 | 61.381 | 61.4851 | 61.428 | 61.4382 | 61.4664 | 61.5002 | 61.4579 | 61.4928 | 123.0651 | 61.6622 | 123.001 | 61.4079 | 61.4893 | 123.0347 | 61.4533 | 122.8357 | 61.5759 | 61.6118 | 61.5117 | 61.5476
1621.0625 | 123.3261 | -61.4914 | 61.702 | 0.030283 | -0.031363 | -0.016578 | 0.011611 | 0.036265 | -0.001406 | 0.042581 | 61.6104 | 0.19827 | 61.5096 | -0.051417 | 0.034501 | 61.5799 | -0.001436 | 61.3718 | 61.5217 | 61.46 | 61.4748 | 61.503 | 61.5277 | 61.49 | 61.534 | 123.1018 | 61.6897 | 123.001 | 61.44 | 61.5259 | 123.0713 | 61.49 | 122.8632 | 61.5759 | 61.6118 | 61.4751 | 61.511
1622.0625 | 123.2529 | -61.4731 | 61.6745 | 0.030283 | -0.040521 | -0.016578 | 0.011611 | 0.036265 | -0.001406 | 0.038003 | 61.6012 | 0.20284 | 61.5141 | -0.03768 | 0.029923 | 61.5891 | -0.001436 | 61.3718 | 61.5034 | 61.4326 | 61.4565 | 61.4847 | 61.5093 | 61.4717 | 61.5111 | 123.0743 | 61.6759 | 122.9872 | 61.4354 | 61.503 | 123.0621 | 61.4716 | 122.8449 | 61.5713 | 61.6026 | 61.4842 | 61.5156
1623.0625 | 123.2849 | -61.4914 | 61.6745 | 0.030283 | -0.035942 | -0.007421 | 0.011611 | 0.040843 | 0.003172 | 0.042581 | 61.6149 | 0.20742 | 61.537 | -0.042259 | 0.039079 | 61.5845 | -0.006014 | 61.3718 | 61.5217 | 61.4555 | 61.484 | 61.503 | 61.5322 | 61.4946 | 61.534 | 123.1063 | 61.6988 | 123.0284 | 61.4491 | 61.5305 | 123.0759 | 61.4854 | 122.8632 | 61.5759 | 61.6209 | 61.4979 | 61.543
1624.0625 | 123.3582 | -61.4914 | 61.6425 | 0.034862 | -0.035942 | -0.016578 | 0.011611 | 0.040843 | 0.003172 | 0.047159 | 61.6195 | 0.20284 | 61.5462 | -0.03768 | 0.029923 | 61.5845 | -0.006014 | 61.381 | 61.5263 | 61.4555 | 61.4748 | 61.503 | 61.5322 | 61.4946 | 61.5386 | 123.1109 | 61.6942 | 123.0376 | 61.4537 | 61.5213 | 123.0759 | 61.4854 | 122.8724 | 61.5896 | 61.6255 | 61.5163 | 61.5522
1625.0625 | 123.3444 | -61.441 | 61.6516 | 0.025705 | -0.031363 | -0.016578 | 0.007033 | 0.036265 | -0.010563 | 0.047159 | 61.6058 | 0.20742 | 61.5096 | -0.033101 | 0.025345 | 61.5845 | -0.001436 | 61.3856 | 61.4667 | 61.4097 | 61.4245 | 61.4481 | 61.4773 | 61.4305 | 61.4882 | 123.0468 | 61.6485 | 122.9506 | 61.4079 | 61.4664 | 123.0255 | 61.4396 | 122.8266 | 61.5804 | 61.6072 | 61.4842 | 61.511
1626.0625 | 123.2529 | -61.5005 | 61.6699 | 0.034862 | -0.031363 | -0.012 | 0.011611 | 0.040843 | -0.001406 | 0.038003 | 61.6012 | 0.20284 | 61.5096 | -0.046838 | 0.025345 | 61.5799 | -0.006014 | 61.3764 | 61.5354 | 61.4692 | 61.4885 | 61.5122 | 61.5414 | 61.4991 | 61.5386 | 123.1017 | 61.7034 | 123.0101 | 61.4537 | 61.5259 | 123.0804 | 61.4945 | 122.8769 | 61.5759 | 61.6072 | 61.4842 | 61.5156
1627.0625 | 123.381 | -61.441 | 61.6104 | 0.021127 | -0.035942 | -0.012 | 0.007033 | 0.045421 | -0.001406 | 0.042581 | 61.6104 | 0.20742 | 61.5416 | -0.042259 | 0.034501 | 61.5845 | -0.006014 | 61.3718 | 61.4622 | 61.4051 | 61.429 | 61.4481 | 61.4865 | 61.4396 | 61.4836 | 123.0514 | 61.6485 | 122.9826 | 61.3988 | 61.4755 | 123.0255 | 61.435 | 122.8129 | 61.5759 | 61.6164 | 61.5071 | 61.5476
1628.0625 | 123.3124 | -61.4868 | 61.6608 | 0.044018 | -0.035942 | -0.021157 | 0.011611 | 0.036265 | 0.003172 | 0.042581 | 61.6149 | 0.20742 | 61.5416 | -0.042259 | 0.029923 | 61.5799 | -0.006014 | 61.3764 | 61.5308 | 61.4509 | 61.4657 | 61.4984 | 61.5231 | 61.49 | 61.5294 | 123.1017 | 61.6942 | 123.0284 | 61.4446 | 61.5167 | 123.0667 | 61.4808 | 122.8632 | 61.585 | 61.6209 | 61.5117 | 61.5476
1629.0625 | 123.2666 | -61.4914 | 61.6699 | 0.034862 | -0.026784 | -0.012 | 0.01619 | 0.036265 | -0.001406 | 0.047159 | 61.6195 | 0.20284 | 61.5279 | -0.042259 | 0.029923 | 61.5799 | -0.001436 | 61.3856 | 61.5263 | 61.4646 | 61.4794 | 61.5076 | 61.5277 | 61.49 | 61.5386 | 123.1109 | 61.6942 | 123.0193 | 61.4491 | 61.5213 | 123.0713 | 61.49 | 122.8769 | 61.5896 | 61.6209 | 61.4979 | 61.5293
1630.0625 | 123.381 | -61.4548 | 61.647 | 0.030283 | -0.026784 | -0.007421 | 0.011611 | 0.040843 | -0.001406 | 0.038003 | 61.6058 | 0.20284 | 61.5096 | -0.046838 | 0.020767 | 61.5845 | -0.006014 | 61.3718 | 61.4851 | 61.428 | 61.4474 | 61.4664 | 61.4956 | 61.4534 | 61.4928 | 123.0606 | 61.6576 | 122.9643 | 61.4079 | 61.4755 | 123.0392 | 61.4488 | 122.8266 | 61.585 | 61.6118 | 61.4888 | 61.5156
1631.0625 | 123.3673 | -61.4548 | 61.5967 | 0.025705 | -0.031363 | -0.007421 | 0.007033 | 0.040843 | -0.001406 | 0.033424 | 61.6104 | 0.20742 | 61.5096 | -0.051417 | 0.025345 | 61.5753 | -0.006014 | 61.3764 | 61.4805 | 61.4234 | 61.4474 | 61.4618 | 61.4956 | 61.4534 | 61.4882 | 123.0651 | 61.6622 | 122.9643 | 61.4034 | 61.4801 | 123.0301 | 61.4488 | 122.8312 | 61.585 | 61.6164 | 61.4842 | 61.5156
1632.0625 | 123.4314 | -61.441 | 61.6608 | 0.034862 | -0.031363 | -0.016578 | 0.011611 | 0.036265 | -0.001406 | 0.038003 | 61.6104 | 0.20284 | 61.5508 | -0.046838 | 0.029923 | 61.5891 | 0.003143 | 61.3764 | 61.4759 | 61.4097 | 61.4245 | 61.4527 | 61.4773 | 61.4396 | 61.479 | 123.0514 | 61.6439 | 122.9918 | 61.3942 | 61.471 | 123.0301 | 61.4442 | 122.8174 | 61.5804 | 61.6072 | 61.5208 | 61.5476
1633.0625 | 123.3765 | -61.4731 | 61.6333 | 0.034862 | -0.031363 | -0.016578 | 0.011611 | 0.040843 | -0.005985 | 0.042581 | 61.6104 | 0.20284 | 61.5462 | -0.046838 | 0.029923 | 61.5799 | -0.001436 | 61.3718 | 61.5079 | 61.4417 | 61.4565 | 61.4847 | 61.5139 | 61.4671 | 61.5157 | 123.0834 | 61.6759 | 123.0193 | 61.4262 | 61.503 | 123.053 | 61.4716 | 122.8449 | 61.5804 | 61.6118 | 61.5163 | 61.5476
1634.0625 | 123.2254 | -61.4914 | 61.6882 | 0.030283 | -0.026784 | -0.016578 | 0.01619 | 0.040843 | -0.001406 | 0.042581 | 61.6104 | 0.19827 | 61.505 | -0.042259 | 0.020767 | 61.5799 | -0.006014 | 61.3764 | 61.5217 | 61.4646 | 61.4748 | 61.5076 | 61.5322 | 61.49 | 61.534 | 123.1018 | 61.6897 | 122.9964 | 61.4491 | 61.5122 | 123.0713 | 61.4854 | 122.8678 | 61.5896 | 61.6164 | 61.4842 | 61.511
1635.0625 | 123.381 | -61.4548 | 61.6425 | 0.025705 | -0.035942 | -0.012 | 0.007033 | 0.036265 | 0.003172 | 0.033424 | 61.6058 | 0.212 | 61.5141 | -0.03768 | 0.025345 | 61.5891 | -0.001436 | 61.3764 | 61.4805 | 61.4188 | 61.4428 | 61.4618 | 61.491 | 61.4579 | 61.4882 | 123.0606 | 61.6668 | 122.9689 | 61.4171 | 61.4801 | 123.0438 | 61.4533 | 122.8312 | 61.5804 | 61.6072 | 61.4888 | 61.5156
1636.0625 | 123.2437 | -61.5189 | 61.6425 | 0.030283 | -0.031363 | -0.012 | 0.007033 | 0.049999 | -0.010563 | 0.038003 | 61.6149 | 0.20284 | 61.537 | -0.03768 | 0.029923 | 61.5799 | -0.006014 | 61.3764 | 61.5491 | 61.4875 | 61.5069 | 61.5259 | 61.5689 | 61.5083 | 61.5569 | 123.1338 | 61.7217 | 123.0559 | 61.4812 | 61.5488 | 123.0988 | 61.5128 | 122.8953 | 61.585 | 61.6209 | 61.5071 | 61.543
1637.0625 | 123.3948 | -61.4502 | 61.6333 | 0.03944 | -0.040521 | -0.016578 | 0.007033 | 0.031687 | 0.003172 | 0.038003 | 61.6058 | 0.20284 | 61.5508 | -0.042259 | 0.025345 | 61.5799 | -0.001436 | 61.381 | 61.4896 | 61.4097 | 61.4336 | 61.4572 | 61.4819 | 61.4534 | 61.4882 | 123.056 | 61.653 | 123.001 | 61.4079 | 61.4755 | 123.0301 | 61.4488 | 122.8312 | 61.5804 | 61.6072 | 61.5254 | 61.5522
1638.0625 | 123.4268 | -61.4182 | 61.6425 | 0.030283 | -0.031363 | -0.012 | 0.01619 | 0.036265 | -0.005985 | 0.038003 | 61.6149 | 0.19827 | 61.5508 | -0.046838 | 0.029923 | 61.5845 | -0.010593 | 61.3764 | 61.4484 | 61.3868 | 61.4062 | 61.4343 | 61.4544 | 61.4122 | 61.4562 | 123.0331 | 61.6164 | 122.9689 | 61.3713 | 61.4481 | 123.0026 | 61.4076 | 122.7945 | 61.585 | 61.6255 | 61.5208 | 61.5614
1639.0625 | 123.2712 | -61.4639 | 61.6928 | 0.030283 | -0.031363 | -0.012 | 0.011611 | 0.031687 | 0.003172 | 0.042581 | 61.6149 | 0.20742 | 61.5416 | -0.051417 | 0.025345 | 61.5799 | -0.006014 | 61.3856 | 61.4942 | 61.4326 | 61.4519 | 61.4755 | 61.4956 | 61.4671 | 61.5065 | 123.0789 | 61.6714 | 123.0055 | 61.4125 | 61.4893 | 123.0438 | 61.4579 | 122.8495 | 61.5896 | 61.6209 | 61.5163 | 61.5476
1640.0625 | 123.4085 | -61.4594 | 61.6241 | 0.030283 | -0.031363 | -0.016578 | 0.007033 | 0.036265 | -0.001406 | 0.038003 | 61.6058 | 0.20284 | 61.5141 | -0.051417 | 0.029923 | 61.5799 | -0.001436 | 61.3764 | 61.4896 | 61.428 | 61.4428 | 61.4664 | 61.4956 | 61.4579 | 61.4974 | 123.0651 | 61.6622 | 122.9735 | 61.4079 | 61.4893 | 123.0392 | 61.4579 | 122.8357 | 61.5759 | 61.6072 | 61.4842 | 61.5156
1641.0625 | 123.2849 | -61.4594 | 61.6653 | 0.030283 | -0.035942 | -0.007421 | 0.011611 | 0.040843 | 0.003172 | 0.028846 | 61.6104 | 0.20742 | 61.505 | -0.042259 | 0.029923 | 61.5707 | -0.001436 | 61.3764 | 61.4896 | 61.4234 | 61.4519 | 61.471 | 61.5002 | 61.4625 | 61.4882 | 123.0697 | 61.6668 | 122.9643 | 61.4171 | 61.4893 | 123.0301 | 61.4579 | 122.8357 | 61.5804 | 61.6118 | 61.4751 | 61.5064
1642.0625 | 123.3948 | -61.4731 | 61.6104 | 0.025705 | -0.031363 | -0.016578 | 0.002454 | 0.036265 | 0.003172 | 0.038003 | 61.6149 | 0.20742 | 61.5462 | -0.046838 | 0.029923 | 61.5799 | -0.006014 | 61.3764 | 61.4988 | 61.4417 | 61.4565 | 61.4755 | 61.5093 | 61.4763 | 61.5111 | 123.088 | 61.6805 | 123.0193 | 61.4262 | 61.503 | 123.053 | 61.4671 | 122.8495 | 61.585 | 61.6209 | 61.5163 | 61.5522
1643.0625 | 123.3032 | -61.4182 | 61.647 | 0.03944 | -0.035942 | -0.012 | 0.011611 | 0.040843 | -0.001406 | 0.042581 | 61.6104 | 0.20742 | 61.5462 | -0.042259 | 0.025345 | 61.5799 | -0.010593 | 61.381 | 61.4576 | 61.3822 | 61.4062 | 61.4298 | 61.459 | 61.4167 | 61.4607 | 123.0285 | 61.6256 | 122.9643 | 61.3759 | 61.4435 | 122.998 | 61.4076 | 122.7991 | 61.585 | 61.6209 | 61.5208 | 61.5568
1644.0625 | 123.3307 | -61.4685 | 61.6516 | 0.025705 | -0.026784 | -0.012 | 0.011611 | 0.045421 | 0.00775 | 0.042581 | 61.6149 | 0.20284 | 61.5508 | -0.042259 | 0.025345 | 61.5753 | -0.006014 | 61.3856 | 61.4942 | 61.4417 | 61.4565 | 61.4801 | 61.5139 | 61.4763 | 61.5111 | 123.0834 | 61.6714 | 123.0193 | 61.4262 | 61.4939 | 123.0438 | 61.4625 | 122.8541 | 61.5896 | 61.6209 | 61.5254 | 61.5568
1645.0625 | 123.3948 | -61.4594 | 61.6241 | 0.025705 | -0.031363 | -0.016578 | 0.007033 | 0.036265 | -0.005985 | 0.038003 | 61.6149 | 0.212 | 61.5233 | -0.042259 | 0.029923 | 61.5799 | -0.006014 | 61.3764 | 61.4851 | 61.428 | 61.4428 | 61.4664 | 61.4956 | 61.4534 | 61.4974 | 123.0743 | 61.6714 | 122.9826 | 61.4171 | 61.4893 | 123.0392 | 61.4533 | 122.8357 | 61.585 | 61.6209 | 61.4934 | 61.5293
1646.0625 | 123.4314 | -61.441 | 61.6379 | 0.030283 | -0.026784 | -0.016578 | 0.011611 | 0.036265 | 0.003172 | 0.038003 | 61.6058 | 0.20284 | 61.5096 | -0.042259 | 0.029923 | 61.5799 | 0.003143 | 61.3718 | 61.4713 | 61.4143 | 61.4245 | 61.4527 | 61.4773 | 61.4442 | 61.479 | 123.0468 | 61.6439 | 122.9506 | 61.3988 | 61.471 | 123.0209 | 61.4442 | 122.8129 | 61.5759 | 61.6026 | 61.4796 | 61.5064
1647.0625 | 123.3902 | -61.4502 | 61.6425 | 0.025705 | -0.031363 | -0.012 | 0.007033 | 0.036265 | -0.001406 | 0.042581 | 61.6058 | 0.20284 | 61.5004 | -0.042259 | 0.029923 | 61.5753 | -0.001436 | 61.3627 | 61.4759 | 61.4188 | 61.4382 | 61.4572 | 61.4865 | 61.4488 | 61.4928 | 123.056 | 61.653 | 122.9506 | 61.4079 | 61.4801 | 123.0255 | 61.4488 | 122.8129 | 61.5759 | 61.6072 | 61.4705 | 61.5018
1648.0625 | 123.4131 | -61.4594 | 61.6379 | 0.034862 | -0.035942 | -0.016578 | 0.011611 | 0.027109 | -0.001406 | 0.038003 | 61.6104 | 0.20284 | 61.5096 | -0.03768 | 0.025345 | 61.5845 | -0.006014 | 61.3764 | 61.4942 | 61.4234 | 61.4428 | 61.471 | 61.4865 | 61.4579 | 61.4974 | 123.0697 | 61.6622 | 122.9689 | 61.4217 | 61.4847 | 123.0438 | 61.4533 | 122.8357 | 61.585 | 61.6164 | 61.4842 | 61.5156
1649.0625 | 123.2712 | -61.5234 | 61.6516 | 0.030283 | -0.031363 | -0.012 | 0.011611 | 0.040843 | -0.001406 | 0.042581 | 61.6058 | 0.20284 | 61.5141 | -0.03768 | 0.025345 | 61.5845 | -0.010593 | 61.381 | 61.5537 | 61.4921 | 61.5114 | 61.535 | 61.5643 | 61.522 | 61.566 | 123.1292 | 61.7263 | 123.0376 | 61.4858 | 61.5488 | 123.1079 | 61.5128 | 122.9044 | 61.5804 | 61.6164 | 61.4888 | 61.5247
1650.0625 | 123.4314 | -61.4319 | 61.6241 | 0.034862 | -0.035942 | -0.016578 | 0.011611 | 0.036265 | -0.001406 | 0.042581 | 61.6241 | 0.20284 | 61.5553 | -0.042259 | 0.034501 | 61.5936 | -0.001436 | 61.3856 | 61.4667 | 61.3959 | 61.4153 | 61.4435 | 61.4682 | 61.4305 | 61.4745 | 123.056 | 61.6347 | 122.9872 | 61.3896 | 61.4664 | 123.0255 | 61.4304 | 122.8174 | 61.5896 | 61.6255 | 61.5208 | 61.5568
1651.0625 | 123.3856 | -61.4594 | 61.6196 | 0.030283 | -0.035942 | -0.012 | 0.002454 | 0.031687 | 0.003172 | 0.038003 | 61.6104 | 0.20284 | 61.5553 | -0.051417 | 0.034501 | 61.5753 | -0.001436 | 61.3856 | 61.4896 | 61.4234 | 61.4474 | 61.4618 | 61.491 | 61.4625 | 61.4974 | 123.0697 | 61.6622 | 123.0147 | 61.4079 | 61.4939 | 123.0347 | 61.4579 | 122.8449 | 61.5759 | 61.6118 | 61.5208 | 61.5568
1652.0625 | 123.4314 | -61.4639 | 61.6104 | 0.030283 | -0.040521 | -0.016578 | 0.01619 | 0.040843 | -0.001406 | 0.042581 | 61.6195 | 0.20284 | 61.5508 | -0.042259 | 0.029923 | 61.5845 | -0.006014 | 61.381 | 61.4942 | 61.4234 | 61.4474 | 61.4801 | 61.5048 | 61.4625 | 61.5065 | 123.0834 | 61.6668 | 123.0147 | 61.4217 | 61.4939 | 123.0484 | 61.4579 | 122.8449 | 61.5896 | 61.6255 | 61.5208 | 61.5568
1653.0625 | 123.3856 | -61.441 | 61.6241 | 0.034862 | -0.035942 | -0.012 | 0.011611 | 0.036265 | -0.001406 | 0.042581 | 61.6058 | 0.20284 | 61.5324 | -0.03768 | 0.029923 | 61.5845 | -0.001436 | 61.381 | 61.4759 | 61.4051 | 61.429 | 61.4527 | 61.4773 | 61.4396 | 61.4836 | 123.0468 | 61.6439 | 122.9735 | 61.4034 | 61.471 | 123.0255 | 61.4396 | 122.822 | 61.5759 | 61.6072 | 61.5025 | 61.5339
1654.0625 | 123.2437 | -61.4868 | 61.6608 | 0.030283 | -0.031363 | -0.012 | 0.002454 | 0.045421 | 0.003172 | 0.042581 | 61.6104 | 0.19827 | 61.5141 | -0.042259 | 0.029923 | 61.5845 | 0.003143 | 61.3764 | 61.5171 | 61.4555 | 61.4748 | 61.4893 | 61.5322 | 61.49 | 61.5294 | 123.0972 | 61.6851 | 123.001 | 61.4446 | 61.5167 | 123.0713 | 61.49 | 122.8632 | 61.5804 | 61.6072 | 61.4842 | 61.511
1655.0625 | 123.4131 | -61.4685 | 61.6058 | 0.034862 | -0.026784 | -0.016578 | 0.011611 | 0.040843 | -0.001406 | 0.051737 | 61.6058 | 0.20742 | 61.505 | -0.042259 | 0.034501 | 61.5799 | -0.006014 | 61.3718 | 61.5034 | 61.4417 | 61.4519 | 61.4801 | 61.5093 | 61.4671 | 61.5202 | 123.0743 | 61.6759 | 122.9735 | 61.4262 | 61.503 | 123.0484 | 61.4625 | 122.8403 | 61.5713 | 61.6118 | 61.4705 | 61.511
1656.0625 | 123.4955 | -61.4365 | 61.7065 | 0.030283 | -0.035942 | -0.012 | 0.007033 | 0.040843 | -0.001406 | 0.042581 | 61.6104 | 0.20742 | 61.505 | -0.051417 | 0.029923 | 61.5891 | -0.006014 | 61.381 | 61.4667 | 61.4005 | 61.4245 | 61.4435 | 61.4773 | 61.4351 | 61.479 | 123.0468 | 61.6439 | 122.9414 | 61.385 | 61.4664 | 123.0255 | 61.4304 | 122.8174 | 61.5804 | 61.6164 | 61.4751 | 61.511
1657.0625 | 123.3856 | -61.4365 | 61.6379 | 0.034862 | -0.022205 | -0.012 | 0.011611 | 0.036265 | 0.003172 | 0.038003 | 61.6104 | 0.212 | 61.5141 | -0.03768 | 0.029923 | 61.5799 | -0.001436 | 61.3764 | 61.4713 | 61.4143 | 61.4245 | 61.4481 | 61.4727 | 61.4396 | 61.4745 | 123.0468 | 61.6485 | 122.9506 | 61.3988 | 61.4664 | 123.0164 | 61.435 | 122.8129 | 61.5804 | 61.6118 | 61.4842 | 61.5156
1658.0625 | 123.4268 | -61.4365 | 61.6196 | 0.025705 | -0.035942 | -0.012 | 0.007033 | 0.036265 | -0.001406 | 0.042581 | 61.6241 | 0.19827 | 61.5416 | -0.042259 | 0.034501 | 61.5799 | -0.006014 | 61.381 | 61.4622 | 61.4005 | 61.4245 | 61.4435 | 61.4727 | 61.4351 | 61.479 | 123.0606 | 61.6347 | 122.9781 | 61.3942 | 61.471 | 123.0164 | 61.4304 | 122.8174 | 61.5896 | 61.6301 | 61.5071 | 61.5476
1659.0625 | 123.3444 | -61.4731 | 61.6516 | 0.030283 | -0.026784 | -0.007421 | 0.011611 | 0.036265 | -0.001406 | 0.038003 | 61.6241 | 0.212 | 61.5553 | -0.042259 | 0.029923 | 61.5891 | -0.001436 | 61.3764 | 61.5034 | 61.4463 | 61.4657 | 61.4847 | 61.5093 | 61.4717 | 61.5111 | 123.0972 | 61.6851 | 123.0284 | 61.4308 | 61.503 | 123.0621 | 61.4716 | 122.8495 | 61.5942 | 61.6255 | 61.5254 | 61.5568
1660.0625 | 123.3673 | -61.4456 | 61.6379 | 0.025705 | -0.031363 | -0.012 | 0.002454 | 0.036265 | -0.001406 | 0.042581 | 61.6149 | 0.19827 | 61.5416 | -0.042259 | 0.020767 | 61.5753 | -0.006014 | 61.381 | 61.4713 | 61.4143 | 61.4336 | 61.4481 | 61.4819 | 61.4442 | 61.4882 | 123.0606 | 61.6439 | 122.9872 | 61.4034 | 61.4664 | 123.0209 | 61.4396 | 122.8266 | 61.5942 | 61.6209 | 61.5208 | 61.5476
1661.0625 | 123.3902 | -61.5051 | 61.6196 | 0.030283 | -0.026784 | -0.012 | 0.011611 | 0.036265 | 0.003172 | 0.042581 | 61.6104 | 0.20742 | 61.5324 | -0.042259 | 0.025345 | 61.5799 | -0.006014 | 61.3718 | 61.5354 | 61.4783 | 61.4931 | 61.5167 | 61.5414 | 61.5083 | 61.5477 | 123.1155 | 61.7126 | 123.0376 | 61.4629 | 61.5305 | 123.085 | 61.4991 | 122.8769 | 61.585 | 61.6164 | 61.5071 | 61.5385
1662.0625 | 123.3902 | -61.4777 | 61.6241 | 0.034862 | -0.031363 | -0.016578 | 0.007033 | 0.036265 | -0.001406 | 0.038003 | 61.6104 | 0.20284 | 61.5096 | -0.03768 | 0.020767 | 61.5845 | -0.006014 | 61.381 | 61.5125 | 61.4463 | 61.4611 | 61.4847 | 61.5139 | 61.4763 | 61.5157 | 123.088 | 61.6805 | 122.9872 | 61.44 | 61.4984 | 123.0621 | 61.4716 | 122.8586 | 61.5896 | 61.6164 | 61.4888 | 61.5156
1663.0625 | 123.436 | -61.4365 | 61.6379 | 0.030283 | -0.026784 | -0.016578 | 0.007033 | 0.040843 | 0.003172 | 0.033424 | 61.6104 | 0.212 | 61.505 | -0.051417 | 0.025345 | 61.5799 | -0.006014 | 61.3764 | 61.4667 | 61.4097 | 61.4199 | 61.4435 | 61.4773 | 61.4396 | 61.4699 | 123.0468 | 61.6485 | 122.9414 | 61.385 | 61.4618 | 123.0164 | 61.4304 | 122.8129 | 61.585 | 61.6164 | 61.4796 | 61.511
1664.0625 | 123.2803 | -61.4868 | 61.6882 | 0.034862 | -0.022205 | -0.016578 | 0.007033 | 0.040843 | 0.003172 | 0.042581 | 61.6149 | 0.20284 | 61.505 | -0.051417 | 0.025345 | 61.5799 | -0.006014 | 61.3718 | 61.5217 | 61.4646 | 61.4702 | 61.4938 | 61.5277 | 61.49 | 61.5294 | 123.1017 | 61.6897 | 122.9918 | 61.4354 | 61.5122 | 123.0667 | 61.4808 | 122.8586 | 61.5896 | 61.6209 | 61.4796 | 61.511
1665.0625 | 123.4131 | -61.4502 | 61.6379 | 0.034862 | -0.031363 | -0.012 | 0.007033 | 0.036265 | -0.005985 | 0.033424 | 61.6104 | 0.20284 | 61.5141 | -0.051417 | 0.029923 | 61.5799 | -0.010593 | 61.3764 | 61.4851 | 61.4188 | 61.4382 | 61.4572 | 61.4865 | 61.4442 | 61.4836 | 123.0606 | 61.653 | 122.9643 | 61.3988 | 61.4801 | 123.0301 | 61.4396 | 122.8266 | 61.5804 | 61.6209 | 61.4842 | 61.5247
1666.0625 | 123.3719 | -61.4822 | 61.6104 | 0.025705 | -0.031363 | -0.012 | 0.01619 | 0.040843 | -0.001406 | 0.047159 | 61.6149 | 0.20284 | 61.5324 | -0.046838 | 0.025345 | 61.5799 | -0.006014 | 61.3764 | 61.5079 | 61.4509 | 61.4702 | 61.4984 | 61.5231 | 61.4808 | 61.5294 | 123.0972 | 61.6851 | 123.0147 | 61.4354 | 61.5076 | 123.0621 | 61.4762 | 122.8586 | 61.5896 | 61.6209 | 61.5071 | 61.5385
1667.0625 | 123.3902 | -61.4914 | 61.6241 | 0.03944 | -0.022205 | -0.016578 | 0.01619 | 0.040843 | -0.001406 | 0.038003 | 61.6149 | 0.20284 | 61.5553 | -0.042259 | 0.020767 | 61.5799 | -0.001436 | 61.3764 | 61.5308 | 61.4692 | 61.4748 | 61.5076 | 61.5322 | 61.49 | 61.5294 | 123.1063 | 61.6942 | 123.0467 | 61.4491 | 61.5122 | 123.0713 | 61.49 | 122.8678 | 61.5942 | 61.6164 | 61.5346 | 61.5568
1668.0625 | 123.3765 | -61.4868 | 61.6287 | 0.03944 | -0.026784 | -0.021157 | 0.011611 | 0.045421 | 0.003172 | 0.038003 | 61.6149 | 0.20284 | 61.5508 | -0.046838 | 0.029923 | 61.5845 | -0.006014 | 61.381 | 61.5263 | 61.46 | 61.4657 | 61.4984 | 61.5322 | 61.49 | 61.5248 | 123.1017 | 61.6897 | 123.0376 | 61.44 | 61.5167 | 123.0713 | 61.4808 | 122.8678 | 61.585 | 61.6209 | 61.5208 | 61.5568
1669.0625 | 123.3444 | -61.4548 | 61.647 | 0.034862 | -0.017627 | -0.016578 | 0.01619 | 0.040843 | 0.00775 | 0.047159 | 61.6195 | 0.20742 | 61.5508 | -0.042259 | 0.029923 | 61.5753 | -0.006014 | 61.381 | 61.4896 | 61.4371 | 61.4382 | 61.471 | 61.4956 | 61.4625 | 61.5019 | 123.0743 | 61.6622 | 123.0055 | 61.4125 | 61.4847 | 123.0301 | 61.4488 | 122.8357 | 61.5896 | 61.6255 | 61.5208 | 61.5568
1670.0625 | 123.3719 | -61.4502 | 61.6241 | 0.025705 | -0.031363 | -0.016578 | 0.007033 | 0.040843 | -0.005985 | 0.038003 | 61.6149 | 0.21658 | 61.5233 | -0.042259 | 0.020767 | 61.5753 | -0.006014 | 61.3856 | 61.4759 | 61.4188 | 61.4336 | 61.4572 | 61.491 | 61.4442 | 61.4882 | 123.0651 | 61.6668 | 122.9735 | 61.4079 | 61.471 | 123.0255 | 61.4442 | 122.8357 | 61.5942 | 61.6209 | 61.5025 | 61.5293
1671.0625 | 123.3994 | -61.4639 | 61.6104 | 0.025705 | -0.031363 | -0.007421 | 0.007033 | 0.036265 | -0.005985 | 0.033424 | 61.6104 | 0.20742 | 61.5096 | -0.046838 | 0.020767 | 61.5753 | -0.006014 | 61.3718 | 61.4896 | 61.4326 | 61.4565 | 61.471 | 61.5002 | 61.4579 | 61.4974 | 123.0743 | 61.6714 | 122.9735 | 61.4171 | 61.4847 | 123.0392 | 61.4579 | 122.8357 | 61.5896 | 61.6164 | 61.4888 | 61.5156
1672.0625 | 123.3673 | -61.4502 | 61.6196 | 0.030283 | -0.031363 | -0.016578 | 0.007033 | 0.031687 | -0.001406 | 0.042581 | 61.6058 | 0.20742 | 61.5141 | -0.046838 | 0.029923 | 61.5891 | -0.010593 | 61.3856 | 61.4805 | 61.4188 | 61.4336 | 61.4572 | 61.4819 | 61.4488 | 61.4928 | 123.056 | 61.6576 | 122.9643 | 61.4034 | 61.4801 | 123.0392 | 61.4396 | 122.8357 | 61.5759 | 61.6164 | 61.4842 | 61.5247
1673.0625 | 123.349 | -61.4777 | 61.6196 | 0.030283 | -0.031363 | -0.016578 | 0.007033 | 0.036265 | -0.001406 | 0.033424 | 61.6058 | 0.20284 | 61.505 | -0.046838 | 0.025345 | 61.5845 | -0.006014 | 61.3718 | 61.5079 | 61.4463 | 61.4611 | 61.4847 | 61.5139 | 61.4763 | 61.5111 | 123.0834 | 61.6805 | 122.9826 | 61.4308 | 61.503 | 123.0621 | 61.4716 | 122.8495 | 61.5804 | 61.6118 | 61.4796 | 61.511
1674.0625 | 123.2071 | -61.496 | 61.6241 | 0.030283 | -0.026784 | -0.016578 | 0.011611 | 0.040843 | 0.003172 | 0.042581 | 61.6149 | 0.20742 | 61.5096 | -0.042259 | 0.025345 | 61.5845 | -0.010593 | 61.3764 | 61.5263 | 61.4692 | 61.4794 | 61.5076 | 61.5368 | 61.4991 | 61.5386 | 123.1109 | 61.7034 | 123.0055 | 61.4537 | 61.5213 | 123.0804 | 61.4854 | 122.8724 | 61.5896 | 61.6255 | 61.4842 | 61.5202
1675.0625 | 123.3444 | -61.4685 | 61.5921 | 0.030283 | -0.031363 | -0.012 | 0.002454 | 0.031687 | -0.001406 | 0.038003 | 61.6149 | 0.20742 | 61.537 | -0.042259 | 0.025345 | 61.5753 | -0.006014 | 61.3856 | 61.4988 | 61.4371 | 61.4565 | 61.471 | 61.5002 | 61.4671 | 61.5065 | 123.0834 | 61.6759 | 123.0055 | 61.4262 | 61.4939 | 123.0438 | 61.4625 | 122.8541 | 61.5896 | 61.6209 | 61.5117 | 61.543
1676.0625 | 123.3719 | -61.4777 | 61.6104 | 0.03944 | -0.035942 | -0.012 | 0.007033 | 0.036265 | -0.001406 | 0.051737 | 61.6104 | 0.20284 | 61.5508 | -0.042259 | 0.020767 | 61.5891 | -0.006014 | 61.381 | 61.5171 | 61.4417 | 61.4657 | 61.4847 | 61.5139 | 61.4763 | 61.5294 | 123.088 | 61.6805 | 123.0284 | 61.4354 | 61.4984 | 123.0667 | 61.4716 | 122.8586 | 61.5896 | 61.6164 | 61.53 | 61.5568
1677.0625 | 123.349 | -61.4914 | 61.6104 | 0.030283 | -0.031363 | -0.012 | 0.01619 | 0.040843 | -0.005985 | 0.042581 | 61.6149 | 0.20742 | 61.5462 | -0.03768 | 0.034501 | 61.5845 | -0.010593 | 61.381 | 61.5217 | 61.46 | 61.4794 | 61.5076 | 61.5322 | 61.4854 | 61.534 | 123.1063 | 61.6988 | 123.0376 | 61.4537 | 61.5259 | 123.0759 | 61.4808 | 122.8724 | 61.5804 | 61.6255 | 61.5117 | 61.5568
1678.0625 | 123.3536 | -61.4639 | 61.6287 | 0.030283 | -0.031363 | -0.012 | 0.007033 | 0.036265 | -0.001406 | 0.047159 | 61.6104 | 0.19827 | 61.5462 | -0.046838 | 0.029923 | 61.5799 | -0.001436 | 61.3764 | 61.4942 | 61.4326 | 61.4519 | 61.471 | 61.5002 | 61.4625 | 61.5111 | 123.0743 | 61.6622 | 123.0101 | 61.4171 | 61.4939 | 123.0438 | 61.4625 | 122.8403 | 61.5804 | 61.6118 | 61.5163 | 61.5476
1679.0625 | 123.3078 | -61.4548 | 61.6425 | 0.034862 | -0.026784 | -0.016578 | 0.01619 | 0.040843 | -0.001406 | 0.042581 | 61.6104 | 0.20284 | 61.5324 | -0.051417 | 0.029923 | 61.5753 | -0.001436 | 61.381 | 61.4896 | 61.428 | 61.4382 | 61.471 | 61.4956 | 61.4534 | 61.4974 | 123.0651 | 61.6576 | 122.9872 | 61.4034 | 61.4847 | 123.0301 | 61.4533 | 122.8357 | 61.5804 | 61.6118 | 61.5025 | 61.5339
1680.0625 | 123.3673 | -61.4868 | 61.6196 | 0.030283 | -0.031363 | -0.012 | 0.007033 | 0.036265 | -0.005985 | 0.047159 | 61.6149 | 0.20284 | 61.5141 | -0.042259 | 0.029923 | 61.5845 | -0.006014 | 61.381 | 61.5171 | 61.4555 | 61.4748 | 61.4938 | 61.5231 | 61.4808 | 61.534 | 123.1017 | 61.6897 | 123.001 | 61.4446 | 61.5167 | 123.0713 | 61.4808 | 122.8678 | 61.585 | 61.6209 | 61.4842 | 61.5202
1681.0625 | 123.3536 | -61.496 | 61.6104 | 0.030283 | -0.035942 | -0.007421 | 0.002454 | 0.031687 | -0.001406 | 0.042581 | 61.6104 | 0.20742 | 61.5141 | -0.046838 | 0.029923 | 61.5845 | -0.006014 | 61.3672 | 61.5263 | 61.46 | 61.4886 | 61.4984 | 61.5277 | 61.4946 | 61.5386 | 123.1063 | 61.7034 | 123.0101 | 61.4491 | 61.5259 | 123.0804 | 61.49 | 122.8632 | 61.5804 | 61.6164 | 61.4842 | 61.5202
1682.0625 | 123.3353 | -61.4548 | 61.5784 | 0.034862 | -0.031363 | -0.021157 | 0.007033 | 0.040843 | -0.001406 | 0.038003 | 61.6012 | 0.20284 | 61.505 | -0.046838 | 0.029923 | 61.5845 | -0.006014 | 61.3764 | 61.4896 | 61.4234 | 61.4336 | 61.4618 | 61.4956 | 61.4534 | 61.4928 | 123.056 | 61.6576 | 122.9598 | 61.4079 | 61.4847 | 123.0392 | 61.4488 | 122.8312 | 61.5713 | 61.6072 | 61.4751 | 61.511
1683.0625 | 123.2712 | -61.496 | 61.615 | 0.030283 | -0.026784 | -0.012 | 0.01619 | 0.036265 | -0.005985 | 0.042581 | 61.6149 | 0.20284 | 61.5233 | -0.046838 | 0.029923 | 61.5707 | -0.010593 | 61.3718 | 61.5263 | 61.4692 | 61.484 | 61.5122 | 61.5322 | 61.49 | 61.5386 | 123.1109 | 61.6988 | 123.0193 | 61.4491 | 61.5259 | 123.0667 | 61.4854 | 122.8678 | 61.585 | 61.6255 | 61.4934 | 61.5339
1684.0625 | 123.2666 | -61.4731 | 61.6653 | 0.034862 | -0.026784 | -0.016578 | 0.011611 | 0.040843 | -0.001406 | 0.047159 | 61.6195 | 0.19827 | 61.5508 | -0.042259 | 0.029923 | 61.5845 | -0.001436 | 61.3718 | 61.5079 | 61.4463 | 61.4565 | 61.4847 | 61.5139 | 61.4717 | 61.5202 | 123.0926 | 61.6713 | 123.0238 | 61.4308 | 61.503 | 123.0576 | 61.4716 | 122.8449 | 61.5896 | 61.6209 | 61.5208 | 61.5522
1685.0625 | 123.3398 | -61.5051 | 61.647 | 0.030283 | -0.031363 | -0.007421 | 0.007033 | 0.040843 | -0.001406 | 0.047159 | 61.6104 | 0.20284 | 61.5508 | -0.042259 | 0.029923 | 61.5845 | -0.001436 | 61.3672 | 61.5354 | 61.4738 | 61.4977 | 61.5122 | 61.546 | 61.5037 | 61.5523 | 123.1155 | 61.708 | 123.0559 | 61.4629 | 61.535 | 123.0896 | 61.5037 | 122.8724 | 61.5804 | 61.6118 | 61.5208 | 61.5522
1686.0625 | 123.3444 | -61.4639 | 61.6196 | 0.025705 | -0.035942 | -0.012 | 0.011611 | 0.040843 | -0.005985 | 0.047159 | 61.6149 | 0.20284 | 61.5462 | -0.046838 | 0.034501 | 61.5845 | -0.006014 | 61.3718 | 61.4896 | 61.428 | 61.4519 | 61.4755 | 61.5048 | 61.4579 | 61.5111 | 123.0789 | 61.6668 | 123.0101 | 61.4171 | 61.4984 | 123.0484 | 61.4579 | 122.8357 | 61.5804 | 61.6209 | 61.5117 | 61.5522
1687.0625 | 123.3444 | -61.4731 | 61.5875 | 0.034862 | -0.026784 | -0.016578 | 0.007033 | 0.040843 | 0.003172 | 0.051737 | 61.6104 | 0.20284 | 61.5462 | -0.046838 | 0.025345 | 61.5799 | -0.010593 | 61.3718 | 61.5079 | 61.4463 | 61.4565 | 61.4801 | 61.5139 | 61.4763 | 61.5248 | 123.0834 | 61.6759 | 123.0193 | 61.4262 | 61.4984 | 123.053 | 61.4625 | 122.8449 | 61.585 | 61.6209 | 61.5208 | 61.5568
1688.0625 | 123.4085 | -61.4685 | 61.5829 | 0.034862 | -0.026784 | -0.012 | 0.007033 | 0.040843 | -0.010563 | 0.042581 | 61.6104 | 0.20742 | 61.5324 | -0.046838 | 0.020767 | 61.5799 | -0.006014 | 61.3718 | 61.5034 | 61.4417 | 61.4565 | 61.4755 | 61.5093 | 61.4579 | 61.5111 | 123.0789 | 61.6759 | 123.001 | 61.4217 | 61.4893 | 123.0484 | 61.4625 | 122.8403 | 61.5896 | 61.6164 | 61.5117 | 61.5385
1689.0625 | 123.4085 | -61.4548 | 61.615 | 0.034862 | -0.017627 | -0.016578 | 0.007033 | 0.036265 | -0.005985 | 0.038003 | 61.6149 | 0.212 | 61.5096 | -0.051417 | 0.025345 | 61.5845 | -0.006014 | 61.381 | 61.4896 | 61.4371 | 61.4382 | 61.4618 | 61.491 | 61.4488 | 61.4928 | 123.0697 | 61.6668 | 122.9643 | 61.4034 | 61.4801 | 123.0392 | 61.4488 | 122.8357 | 61.5896 | 61.6209 | 61.4842 | 61.5156
1690.0625 | 123.3444 | -61.4685 | 61.5784 | 0.030283 | -0.026784 | -0.012 | 0.011611 | 0.040843 | -0.001406 | 0.042581 | 61.6195 | 0.20284 | 61.5096 | -0.051417 | 0.025345 | 61.5845 | -0.010593 | 61.381 | 61.4988 | 61.4417 | 61.4565 | 61.4801 | 61.5093 | 61.4671 | 61.5111 | 123.088 | 61.6714 | 122.9781 | 61.4171 | 61.4939 | 123.053 | 61.4579 | 122.8495 | 61.5942 | 61.6301 | 61.4842 | 61.5202
1691.0625 | 123.3856 | -61.4777 | 61.6013 | 0.030283 | -0.031363 | -0.016578 | 0.011611 | 0.036265 | -0.001406 | 0.042581 | 61.6058 | 0.20284 | 61.5096 | -0.051417 | 0.034501 | 61.5845 | -0.001436 | 61.3764 | 61.5079 | 61.4463 | 61.4611 | 61.4893 | 61.5139 | 61.4763 | 61.5202 | 123.0834 | 61.6805 | 122.9872 | 61.4262 | 61.5122 | 123.0621 | 61.4762 | 122.8541 | 61.5713 | 61.6072 | 61.4751 | 61.511
1692.0625 | 123.3582 | -61.4594 | 61.5921 | 0.030283 | -0.031363 | -0.016578 | 0.011611 | 0.045421 | -0.010563 | 0.042581 | 61.6149 | 0.212 | 61.5141 | -0.042259 | 0.029923 | 61.5799 | -0.006014 | 61.3764 | 61.4896 | 61.428 | 61.4428 | 61.471 | 61.5048 | 61.4488 | 61.5019 | 123.0743 | 61.6714 | 122.9735 | 61.4171 | 61.4893 | 123.0392 | 61.4533 | 122.8357 | 61.585 | 61.6209 | 61.4842 | 61.5202
1693.0625 | 123.3765 | -61.5005 | 61.5646 | 0.034862 | -0.031363 | -0.012 | 0.011611 | 0.045421 | -0.001406 | 0.047159 | 61.6104 | 0.20742 | 61.537 | -0.046838 | 0.029923 | 61.5891 | -0.015171 | 61.3764 | 61.5354 | 61.4692 | 61.4885 | 61.5122 | 61.546 | 61.4991 | 61.5477 | 123.1109 | 61.708 | 123.0376 | 61.4537 | 61.5305 | 123.0896 | 61.4854 | 122.8769 | 61.5804 | 61.6255 | 61.5071 | 61.5522
1694.0625 | 123.3994 | -61.4914 | 61.6287 | 0.030283 | -0.031363 | -0.016578 | 0.007033 | 0.045421 | -0.005985 | 0.038003 | 61.6104 | 0.20742 | 61.5508 | -0.042259 | 0.029923 | 61.5845 | -0.010593 | 61.3764 | 61.5217 | 61.46 | 61.4748 | 61.4984 | 61.5368 | 61.4854 | 61.5294 | 123.1018 | 61.6988 | 123.0422 | 61.4491 | 61.5213 | 123.0759 | 61.4808 | 122.8678 | 61.5804 | 61.6209 | 61.5208 | 61.5614
1695.0625 | 123.2666 | -61.5097 | 61.6379 | 0.03944 | -0.026784 | -0.007421 | 0.011611 | 0.040843 | -0.001406 | 0.042581 | 61.6104 | 0.20742 | 61.5462 | -0.03768 | 0.025345 | 61.5845 | -0.001436 | 61.3764 | 61.5491 | 61.4829 | 61.5023 | 61.5213 | 61.5505 | 61.5083 | 61.5523 | 123.1201 | 61.7171 | 123.0559 | 61.472 | 61.535 | 123.0942 | 61.5083 | 122.8861 | 61.585 | 61.6118 | 61.5208 | 61.5476
1696.0625 | 123.3582 | -61.4777 | 61.6104 | 0.034862 | -0.031363 | -0.012 | 0.01619 | 0.040843 | 0.003172 | 0.042581 | 61.6104 | 0.20284 | 61.5462 | -0.042259 | 0.025345 | 61.5753 | -0.010593 | 61.3718 | 61.5125 | 61.4463 | 61.4657 | 61.4939 | 61.5185 | 61.4808 | 61.5202 | 123.088 | 61.6805 | 123.0238 | 61.4354 | 61.503 | 123.053 | 61.4671 | 122.8495 | 61.585 | 61.6209 | 61.5208 | 61.5568
1697.0625 | 123.3902 | -61.4731 | 61.5921 | 0.030283 | -0.035942 | -0.016578 | 0.007033 | 0.036265 | -0.005985 | 0.051737 | 61.6104 | 0.20742 | 61.537 | -0.042259 | 0.029923 | 61.5799 | -0.010593 | 61.3764 | 61.5034 | 61.4371 | 61.4565 | 61.4801 | 61.5093 | 61.4671 | 61.5248 | 123.0834 | 61.6805 | 123.0101 | 61.4308 | 61.503 | 123.053 | 61.4625 | 122.8495 | 61.5804 | 61.6209 | 61.5071 | 61.5476
1698.0625 | 123.3536 | -61.4868 | 61.5967 | 0.034862 | -0.026784 | -0.012 | 0.01619 | 0.045421 | -0.001406 | 0.051737 | 61.6104 | 0.212 | 61.5141 | -0.042259 | 0.025345 | 61.5845 | -0.001436 | 61.3718 | 61.5217 | 61.46 | 61.4748 | 61.503 | 61.5322 | 61.4854 | 61.5386 | 123.0972 | 61.6988 | 123.001 | 61.4446 | 61.5122 | 123.0713 | 61.4854 | 122.8586 | 61.585 | 61.6118 | 61.4888 | 61.5156
1699.0625 | 123.3353 | -61.4914 | 61.6241 | 0.030283 | -0.031363 | -0.012 | 0.002454 | 0.040843 | -0.005985 | 0.047159 | 61.6104 | 0.20284 | 61.5004 | -0.046838 | 0.025345 | 61.5799 | -0.001436 | 61.381 | 61.5217 | 61.46 | 61.4794 | 61.4938 | 61.5322 | 61.4854 | 61.5386 | 123.1018 | 61.6942 | 122.9918 | 61.4446 | 61.5167 | 123.0713 | 61.49 | 122.8724 | 61.585 | 61.6118 | 61.4751 | 61.5018
1700.0625 | 123.3078 | -61.4914 | 61.6287 | 0.025705 | -0.031363 | -0.016578 | 0.011611 | 0.040843 | -0.005985 | 0.042581 | 61.6104 | 0.20284 | 61.5096 | -0.042259 | 0.025345 | 61.5799 | -0.001436 | 61.381 | 61.5171 | 61.46 | 61.4748 | 61.503 | 61.5322 | 61.4854 | 61.534 | 123.1018 | 61.6942 | 123.001 | 61.4491 | 61.5167 | 123.0713 | 61.49 | 122.8724 | 61.585 | 61.6118 | 61.4842 | 61.511
1701.0625 | 123.2666 | -61.4822 | 61.6837 | 0.044018 | -0.031363 | -0.012 | 0.01619 | 0.045421 | -0.005985 | 0.047159 | 61.6149 | 0.20742 | 61.5096 | -0.051417 | 0.025345 | 61.5799 | -0.010593 | 61.3718 | 61.5263 | 61.4509 | 61.4702 | 61.4984 | 61.5277 | 61.4763 | 61.5294 | 123.0972 | 61.6897 | 122.9918 | 61.4308 | 61.5076 | 123.0621 | 61.4716 | 122.8541 | 61.5896 | 61.6255 | 61.4842 | 61.5202
1702.0625 | 123.2712 | -61.4685 | 61.6516 | 0.03944 | -0.026784 | -0.012 | 0.011611 | 0.045421 | 0.00775 | 0.047159 | 61.6195 | 0.20742 | 61.5187 | -0.042259 | 0.025345 | 61.5891 | -0.015171 | 61.3764 | 61.5079 | 61.4417 | 61.4565 | 61.4801 | 61.5139 | 61.4763 | 61.5157 | 123.088 | 61.6759 | 122.9872 | 61.4262 | 61.4939 | 123.0576 | 61.4533 | 122.8449 | 61.5942 | 61.6347 | 61.4934 | 61.5339
1703.0625 | 123.2895 | -61.5005 | 61.6516 | 0.034862 | -0.035942 | -0.007421 | 0.01619 | 0.036265 | -0.001406 | 0.047159 | 61.6149 | 0.19827 | 61.5462 | -0.046838 | 0.034501 | 61.5845 | -0.015171 | 61.3764 | 61.5354 | 61.4646 | 61.4931 | 61.5167 | 61.5368 | 61.4991 | 61.5477 | 123.1155 | 61.6988 | 123.0467 | 61.4537 | 61.535 | 123.085 | 61.4854 | 122.8769 | 61.5804 | 61.6301 | 61.5117 | 61.5614
1704.0625 | 123.2712 | -61.5143 | 61.6379 | 0.034862 | -0.026784 | -0.012 | 0.01619 | 0.040843 | -0.001406 | 0.047159 | 61.6195 | 0.20742 | 61.5508 | -0.046838 | 0.025345 | 61.5753 | -0.001436 | 61.3718 | 61.5491 | 61.4875 | 61.5023 | 61.5305 | 61.5551 | 61.5129 | 61.5614 | 123.1338 | 61.7217 | 123.065 | 61.4674 | 61.5396 | 123.0896 | 61.5128 | 122.8861 | 61.5942 | 61.6209 | 61.5254 | 61.5522
1705.0625 | 123.2529 | -61.4914 | 61.647 | 0.030283 | -0.026784 | -0.007421 | 0.011611 | 0.045421 | 0.003172 | 0.042581 | 61.6104 | 0.20742 | 61.5508 | -0.051417 | 0.025345 | 61.5845 | -0.006014 | 61.3764 | 61.5217 | 61.4646 | 61.484 | 61.503 | 61.5368 | 61.4946 | 61.534 | 123.1018 | 61.6988 | 123.0422 | 61.44 | 61.5167 | 123.0759 | 61.4854 | 122.8678 | 61.585 | 61.6164 | 61.5254 | 61.5568
1706.0625 | 123.2758 | -61.4685 | 61.6516 | 0.034862 | -0.022205 | -0.021157 | 0.002454 | 0.040843 | -0.001406 | 0.047159 | 61.6195 | 0.20742 | 61.5508 | -0.046838 | 0.025345 | 61.5891 | -0.006014 | 61.381 | 61.5034 | 61.4463 | 61.4473 | 61.471 | 61.5093 | 61.4671 | 61.5157 | 123.088 | 61.6759 | 123.0193 | 61.4217 | 61.4939 | 123.0576 | 61.4625 | 122.8495 | 61.5942 | 61.6255 | 61.5254 | 61.5568
1707.0625 | 123.381 | -61.4685 | 61.6196 | 0.030283 | -0.031363 | -0.012 | 0.007033 | 0.040843 | -0.010563 | 0.047159 | 61.6195 | 0.20742 | 61.5279 | -0.042259 | 0.025345 | 61.5845 | -0.006014 | 61.3718 | 61.4988 | 61.4371 | 61.4565 | 61.4755 | 61.5093 | 61.4579 | 61.5157 | 123.088 | 61.6759 | 122.9964 | 61.4262 | 61.4939 | 123.053 | 61.4625 | 122.8403 | 61.5942 | 61.6255 | 61.5025 | 61.5339
1708.0625 | 123.3124 | -61.5005 | 61.647 | 0.030283 | -0.026784 | -0.016578 | 0.01619 | 0.040843 | -0.005985 | 0.047159 | 61.6104 | 0.20284 | 61.5187 | -0.042259 | 0.029923 | 61.5891 | -0.010593 | 61.3764 | 61.5308 | 61.4738 | 61.484 | 61.5167 | 61.5414 | 61.4946 | 61.5477 | 123.1109 | 61.7034 | 123.0193 | 61.4583 | 61.5305 | 123.0896 | 61.49 | 122.8769 | 61.5804 | 61.6209 | 61.4888 | 61.5293
1709.0625 | 123.3765 | -61.4731 | 61.6379 | 0.034862 | -0.022205 | -0.007421 | 0.007033 | 0.045421 | -0.001406 | 0.047159 | 61.6058 | 0.20742 | 61.505 | -0.042259 | 0.029923 | 61.5799 | -0.015171 | 61.3718 | 61.5079 | 61.4509 | 61.4657 | 61.4801 | 61.5185 | 61.4717 | 61.5202 | 123.0789 | 61.6805 | 122.9781 | 61.4308 | 61.503 | 123.053 | 61.4579 | 122.8449 | 61.5759 | 61.6209 | 61.4751 | 61.5202
1710.0625 | 123.3398 | -61.4685 | 61.6608 | 0.034862 | -0.026784 | -0.007421 | 0.007033 | 0.049999 | 0.00775 | 0.047159 | 61.6149 | 0.212 | 61.505 | -0.03768 | 0.034501 | 61.5799 | -0.010593 | 61.3718 | 61.5034 | 61.4417 | 61.4611 | 61.4755 | 61.5185 | 61.4763 | 61.5157 | 123.0834 | 61.6805 | 122.9735 | 61.4308 | 61.503 | 123.0484 | 61.4579 | 122.8403 | 61.5804 | 61.6255 | 61.4705 | 61.5156
1711.0625 | 123.3032 | -61.4685 | 61.6379 | 0.034862 | -0.022205 | -0.016578 | 0.011611 | 0.036265 | -0.001406 | 0.047159 | 61.6149 | 0.212 | 61.5233 | -0.046838 | 0.034501 | 61.5753 | -0.006014 | 61.3764 | 61.5034 | 61.4463 | 61.4519 | 61.4801 | 61.5048 | 61.4671 | 61.5157 | 123.0834 | 61.6805 | 122.9918 | 61.4217 | 61.503 | 123.0438 | 61.4625 | 122.8449 | 61.5804 | 61.6209 | 61.4888 | 61.5293
1712.0625 | 123.381 | -61.4685 | 61.647 | 0.030283 | -0.022205 | -0.016578 | 0.002454 | 0.040843 | 0.003172 | 0.042581 | 61.6149 | 0.212 | 61.5416 | -0.042259 | 0.020767 | 61.5799 | -0.006014 | 61.3764 | 61.4988 | 61.4463 | 61.4519 | 61.471 | 61.5093 | 61.4717 | 61.5111 | 123.0834 | 61.6805 | 123.0101 | 61.4262 | 61.4893 | 123.0484 | 61.4625 | 122.8449 | 61.5942 | 61.6209 | 61.5208 | 61.5476
1713.0625 | 123.2941 | -61.4822 | 61.6653 | 0.034862 | -0.026784 | -0.012 | 0.011611 | 0.040843 | 0.00775 | 0.051737 | 61.6149 | 0.20742 | 61.5553 | -0.042259 | 0.029923 | 61.5799 | -0.001436 | 61.3764 | 61.5171 | 61.4555 | 61.4702 | 61.4939 | 61.5231 | 61.49 | 61.534 | 123.0972 | 61.6897 | 123.0376 | 61.44 | 61.5122 | 123.0621 | 61.4808 | 122.8586 | 61.585 | 61.6164 | 61.5254 | 61.5568
1714.0625 | 123.262 | -61.4914 | 61.6653 | 0.025705 | -0.031363 | -0.012 | -0.002124 | 0.036265 | -0.001406 | 0.051737 | 61.6149 | 0.20284 | 61.5553 | -0.046838 | 0.025345 | 61.5845 | -0.006014 | 61.3764 | 61.5171 | 61.46 | 61.4794 | 61.4893 | 61.5277 | 61.49 | 61.5431 | 123.1063 | 61.6942 | 123.0467 | 61.4446 | 61.5167 | 123.0759 | 61.4854 | 122.8678 | 61.5896 | 61.6209 | 61.53 | 61.5614
1715.0625 | 123.2803 | -61.4639 | 61.6699 | 0.025705 | -0.017627 | -0.016578 | 0.011611 | 0.040843 | 0.003172 | 0.047159 | 61.6195 | 0.20742 | 61.5553 | -0.042259 | 0.029923 | 61.5753 | -0.015171 | 61.381 | 61.4896 | 61.4463 | 61.4474 | 61.4755 | 61.5048 | 61.4671 | 61.5111 | 123.0834 | 61.6714 | 123.0193 | 61.4217 | 61.4939 | 123.0392 | 61.4488 | 122.8449 | 61.5896 | 61.6347 | 61.5254 | 61.5705
1716.0625 | 123.3078 | -61.4639 | 61.6699 | 0.030283 | -0.031363 | -0.021157 | 0.007033 | 0.045421 | 0.003172 | 0.047159 | 61.6149 | 0.212 | 61.5279 | -0.042259 | 0.029923 | 61.5799 | -0.006014 | 61.3764 | 61.4942 | 61.4326 | 61.4428 | 61.471 | 61.5093 | 61.4671 | 61.5111 | 123.0789 | 61.6759 | 122.9918 | 61.4217 | 61.4939 | 123.0438 | 61.4579 | 122.8403 | 61.585 | 61.6209 | 61.4979 | 61.5339
1717.0625 | 123.3948 | -61.4914 | 61.5738 | 0.034862 | -0.026784 | -0.016578 | 0.002454 | 0.040843 | 0.003172 | 0.051737 | 61.6104 | 0.20284 | 61.505 | -0.042259 | 0.020767 | 61.5845 | -0.006014 | 61.3672 | 61.5263 | 61.4646 | 61.4748 | 61.4938 | 61.5322 | 61.4946 | 61.5431 | 123.1018 | 61.6942 | 122.9964 | 61.4491 | 61.5122 | 123.0759 | 61.4854 | 122.8586 | 61.5896 | 61.6164 | 61.4842 | 61.511
1718.0625 | 123.3032 | -61.4594 | 61.647 | 0.030283 | -0.031363 | -0.012 | 0.011611 | 0.049999 | 0.003172 | 0.042581 | 61.6195 | 0.19827 | 61.505 | -0.051417 | 0.034501 | 61.5845 | -0.006014 | 61.3764 | 61.4896 | 61.428 | 61.4474 | 61.471 | 61.5093 | 61.4625 | 61.5019 | 123.0789 | 61.6576 | 122.9643 | 61.4079 | 61.4939 | 123.0438 | 61.4533 | 122.8357 | 61.585 | 61.6255 | 61.4705 | 61.511
1719.0625 | 123.2895 | -61.5005 | 61.6562 | 0.03944 | -0.035942 | -0.016578 | 0.01619 | 0.045421 | -0.001406 | 0.047159 | 61.6058 | 0.20284 | 61.5096 | -0.051417 | 0.029923 | 61.5845 | -0.010593 | 61.3764 | 61.54 | 61.4646 | 61.484 | 61.5167 | 61.546 | 61.4991 | 61.5477 | 123.1063 | 61.7034 | 123.0101 | 61.4491 | 61.5305 | 123.085 | 61.49 | 122.8769 | 61.5759 | 61.6164 | 61.4796 | 61.5202
1720.0625 | 123.349 | -61.4685 | 61.6379 | 0.034862 | -0.022205 | -0.012 | 0.011611 | 0.045421 | 0.003172 | 0.051737 | 61.6149 | 0.20742 | 61.5324 | -0.03768 | 0.034501 | 61.5799 | -0.001436 | 61.3901 | 61.5034 | 61.4463 | 61.4565 | 61.4801 | 61.5139 | 61.4717 | 61.5202 | 123.0834 | 61.6759 | 123.001 | 61.4308 | 61.503 | 123.0484 | 61.4671 | 122.8586 | 61.5804 | 61.6164 | 61.4979 | 61.5339
1721.0625 | 123.349 | -61.4822 | 61.6287 | 0.034862 | -0.022205 | -0.012 | 0.011611 | 0.045421 | 0.003172 | 0.047159 | 61.6241 | 0.212 | 61.5553 | -0.046838 | 0.029923 | 61.5799 | -0.006014 | 61.381 | 61.5171 | 61.46 | 61.4702 | 61.4939 | 61.5277 | 61.4854 | 61.5294 | 123.1063 | 61.6942 | 123.0376 | 61.4354 | 61.5122 | 123.0621 | 61.4762 | 122.8632 | 61.5942 | 61.6301 | 61.5254 | 61.5614
1722.0625 | 123.3353 | -61.5051 | 61.6241 | 0.030283 | -0.022205 | -0.012 | 0.011611 | 0.040843 | 0.003172 | 0.051737 | 61.6195 | 0.20284 | 61.5462 | -0.042259 | 0.025345 | 61.5845 | -0.006014 | 61.3672 | 61.5354 | 61.4829 | 61.4931 | 61.5167 | 61.546 | 61.5083 | 61.5569 | 123.1246 | 61.708 | 123.0513 | 61.4629 | 61.5305 | 123.0896 | 61.4991 | 122.8724 | 61.5942 | 61.6255 | 61.5208 | 61.5522
1723.0625 | 123.3032 | -61.4777 | 61.6608 | 0.030283 | -0.022205 | -0.007421 | 0.007033 | 0.040843 | -0.001406 | 0.051737 | 61.6195 | 0.20284 | 61.5553 | -0.046838 | 0.029923 | 61.5799 | -0.015171 | 61.3718 | 61.5079 | 61.4555 | 61.4702 | 61.4847 | 61.5185 | 61.4763 | 61.5294 | 123.0972 | 61.6805 | 123.033 | 61.4308 | 61.5076 | 123.0576 | 61.4625 | 122.8495 | 61.5896 | 61.6347 | 61.5254 | 61.5705
1724.0625 | 123.2712 | -61.4685 | 61.6516 | 0.03944 | -0.035942 | -0.007421 | 0.01619 | 0.045421 | -0.001406 | 0.051737 | 61.6195 | 0.20284 | 61.5462 | -0.046838 | 0.029923 | 61.5891 | -0.001436 | 61.3856 | 61.5079 | 61.4326 | 61.4611 | 61.4847 | 61.5139 | 61.4671 | 61.5202 | 123.088 | 61.6714 | 123.0147 | 61.4217 | 61.4984 | 123.0576 | 61.4671 | 122.8541 | 61.5896 | 61.6209 | 61.5163 | 61.5476
1725.0625 | 123.3307 | -61.4777 | 61.6608 | 0.030283 | -0.022205 | -0.002842 | 0.020768 | 0.049999 | 0.003172 | 0.042581 | 61.6149 | 0.212 | 61.5141 | -0.046838 | 0.029923 | 61.5799 | -0.006014 | 61.381 | 61.5079 | 61.4555 | 61.4748 | 61.4984 | 61.5277 | 61.4808 | 61.5202 | 123.0926 | 61.6897 | 122.9918 | 61.4308 | 61.5076 | 123.0576 | 61.4716 | 122.8586 | 61.585 | 61.6209 | 61.4842 | 61.5202
1726.0625 | 123.3124 | -61.496 | 61.6608 | 0.030283 | -0.022205 | -0.016578 | 0.011611 | 0.049999 | 0.003172 | 0.047159 | 61.6104 | 0.20742 | 61.505 | -0.051417 | 0.034501 | 61.5799 | -0.006014 | 61.3718 | 61.5263 | 61.4738 | 61.4794 | 61.5076 | 61.546 | 61.4991 | 61.5431 | 123.1063 | 61.7034 | 123.001 | 61.4446 | 61.5305 | 123.0759 | 61.49 | 122.8678 | 61.5759 | 61.6164 | 61.4705 | 61.511
1727.0625 | 123.3032 | -61.4777 | 61.647 | 0.030283 | -0.022205 | -0.007421 | 0.011611 | 0.040843 | 0.00775 | 0.042581 | 61.6195 | 0.20284 | 61.5141 | -0.046838 | 0.029923 | 61.5845 | -0.010593 | 61.3718 | 61.5079 | 61.4555 | 61.4702 | 61.4893 | 61.5185 | 61.4854 | 61.5202 | 123.0972 | 61.6805 | 122.9918 | 61.4308 | 61.5076 | 123.0621 | 61.4671 | 122.8495 | 61.5896 | 61.6301 | 61.4842 | 61.5247
1728.0625 | 123.317 | -61.4731 | 61.647 | 0.030283 | -0.026784 | -0.012 | 0.020768 | 0.045421 | 0.003172 | 0.056315 | 61.6149 | 0.20742 | 61.5096 | -0.042259 | 0.025345 | 61.5799 | -0.006014 | 61.3718 | 61.5034 | 61.4463 | 61.4611 | 61.4939 | 61.5185 | 61.4763 | 61.5294 | 123.088 | 61.6805 | 122.9826 | 61.4308 | 61.4984 | 123.053 | 61.4671 | 122.8449 | 61.5896 | 61.6209 | 61.4842 | 61.5156
1729.0625 | 123.2941 | -61.4731 | 61.5967 | 0.030283 | -0.017627 | -0.007421 | 0.01619 | 0.040843 | -0.005985 | 0.051737 | 61.6241 | 0.20742 | 61.537 | -0.042259 | 0.025345 | 61.5845 | -0.010593 | 61.3718 | 61.5034 | 61.4555 | 61.4657 | 61.4893 | 61.5139 | 61.4671 | 61.5248 | 123.0972 | 61.6805 | 123.0101 | 61.4308 | 61.4984 | 123.0576 | 61.4625 | 122.8449 | 61.5987 | 61.6347 | 61.5117 | 61.5476
1730.0625 | 123.2758 | -61.4777 | 61.6882 | 0.034862 | -0.026784 | -0.002842 | 0.01619 | 0.036265 | 0.003172 | 0.056315 | 61.6195 | 0.20284 | 61.5553 | -0.042259 | 0.034501 | 61.5845 | -0.006014 | 61.3764 | 61.5125 | 61.4509 | 61.4748 | 61.4939 | 61.5139 | 61.4808 | 61.534 | 123.0972 | 61.6805 | 123.033 | 61.4354 | 61.5122 | 123.0621 | 61.4716 | 122.8541 | 61.585 | 61.6255 | 61.5208 | 61.5614
1731.0625 | 123.2895 | -61.5051 | 61.6791 | 0.034862 | -0.022205 | -0.016578 | 0.01619 | 0.045421 | 0.00775 | 0.051737 | 61.6195 | 0.20742 | 61.5553 | -0.046838 | 0.034501 | 61.5799 | -0.001436 | 61.3764 | 61.54 | 61.4829 | 61.4885 | 61.5213 | 61.5505 | 61.5129 | 61.5569 | 123.1246 | 61.7126 | 123.0605 | 61.4583 | 61.5396 | 123.085 | 61.5037 | 122.8815 | 61.585 | 61.6209 | 61.5208 | 61.5568
1732.0625 | 123.3536 | -61.5051 | 61.6608 | 0.034862 | -0.017627 | -0.016578 | 0.007033 | 0.049999 | 0.003172 | 0.051737 | 61.6195 | 0.20284 | 61.5508 | -0.042259 | 0.034501 | 61.5891 | -0.001436 | 61.3764 | 61.54 | 61.4875 | 61.4885 | 61.5122 | 61.5551 | 61.5083 | 61.5569 | 123.1246 | 61.708 | 123.0559 | 61.4629 | 61.5396 | 123.0942 | 61.5037 | 122.8815 | 61.585 | 61.6209 | 61.5163 | 61.5522
1733.0625 | 123.2849 | -61.4822 | 61.647 | 0.034862 | -0.022205 | -0.012 | 0.011611 | 0.040843 | -0.001406 | 0.056315 | 61.6195 | 0.20742 | 61.537 | -0.051417 | 0.034501 | 61.5799 | -0.001436 | 61.3764 | 61.5171 | 61.46 | 61.4702 | 61.4939 | 61.5231 | 61.4808 | 61.5386 | 123.1018 | 61.6897 | 123.0193 | 61.4308 | 61.5167 | 123.0621 | 61.4808 | 122.8586 | 61.585 | 61.6209 | 61.5025 | 61.5385
1734.0625 | 123.143 | -61.5189 | 61.5875 | 0.03944 | -0.017627 | -0.007421 | 0.011611 | 0.049999 | 0.00775 | 0.051737 | 61.6104 | 0.20284 | 61.505 | -0.046838 | 0.034501 | 61.5707 | -0.006014 | 61.3764 | 61.5583 | 61.5012 | 61.5114 | 61.5305 | 61.5689 | 61.5266 | 61.5706 | 123.1292 | 61.7217 | 123.0238 | 61.472 | 61.5534 | 123.0896 | 61.5128 | 122.8953 | 61.5759 | 61.6164 | 61.4705 | 61.511
1735.0625 | 123.3124 | -61.4639 | 61.6699 | 0.03944 | -0.022205 | -0.012 | 0.011611 | 0.045421 | -0.001406 | 0.042581 | 61.6104 | 0.20742 | 61.5141 | -0.03768 | 0.029923 | 61.5891 | -0.010593 | 61.3764 | 61.5034 | 61.4417 | 61.4519 | 61.4755 | 61.5093 | 61.4625 | 61.5065 | 123.0743 | 61.6714 | 122.9781 | 61.4262 | 61.4939 | 123.053 | 61.4533 | 122.8403 | 61.5804 | 61.6209 | 61.4842 | 61.5247
1736.0625 | 123.2666 | -61.5005 | 61.6653 | 0.025705 | -0.017627 | -0.012 | 0.01619 | 0.040843 | -0.005985 | 0.056315 | 61.6195 | 0.19827 | 61.505 | -0.042259 | 0.025345 | 61.5845 | 0.003143 | 61.3764 | 61.5263 | 61.4829 | 61.4885 | 61.5167 | 61.5414 | 61.4946 | 61.5569 | 123.1201 | 61.6988 | 123.0055 | 61.4583 | 61.5259 | 123.085 | 61.5037 | 122.8769 | 61.5942 | 61.6164 | 61.4796 | 61.5018
1737.0625 | 123.2986 | -61.4822 | 61.702 | 0.034862 | -0.022205 | -0.016578 | 0.011611 | 0.040843 | -0.001406 | 0.047159 | 61.6149 | 0.20742 | 61.5279 | -0.03768 | 0.029923 | 61.5799 | -0.001436 | 61.3672 | 61.5171 | 61.46 | 61.4657 | 61.4939 | 61.5231 | 61.4808 | 61.5294 | 123.0972 | 61.6897 | 123.0101 | 61.4446 | 61.5122 | 123.0621 | 61.4808 | 122.8495 | 61.585 | 61.6164 | 61.4979 | 61.5293
1738.0625 | 123.2574 | -61.4822 | 61.6745 | 0.034862 | -0.022205 | -0.007421 | 0.011611 | 0.040843 | 0.003172 | 0.051737 | 61.6104 | 0.212 | 61.5508 | -0.051417 | 0.029923 | 61.5845 | -0.006014 | 61.381 | 61.5171 | 61.46 | 61.4748 | 61.4939 | 61.5231 | 61.4854 | 61.534 | 123.0926 | 61.6942 | 123.033 | 61.4308 | 61.5122 | 123.0667 | 61.4762 | 122.8632 | 61.5804 | 61.6164 | 61.5208 | 61.5568
1739.0625 | 123.2758 | -61.4868 | 61.6791 | 0.03944 | -0.026784 | -0.012 | 0.011611 | 0.045421 | -0.001406 | 0.056315 | 61.6195 | 0.212 | 61.5553 | -0.046838 | 0.029923 | 61.5891 | -0.001436 | 61.3672 | 61.5263 | 61.46 | 61.4748 | 61.4984 | 61.5322 | 61.4854 | 61.5431 | 123.1063 | 61.6988 | 123.0422 | 61.44 | 61.5167 | 123.0759 | 61.4854 | 122.8541 | 61.5896 | 61.6209 | 61.5254 | 61.5568
1740.0625 | 123.3078 | -61.4594 | 61.6608 | 0.034862 | -0.026784 | -0.016578 | 0.011611 | 0.036265 | 0.003172 | 0.060893 | 61.6195 | 0.20742 | 61.5553 | -0.046838 | 0.034501 | 61.5753 | -0.010593 | 61.381 | 61.4942 | 61.4326 | 61.4428 | 61.471 | 61.4956 | 61.4625 | 61.5202 | 123.0789 | 61.6668 | 123.0147 | 61.4125 | 61.4939 | 123.0347 | 61.4488 | 122.8403 | 61.585 | 61.6301 | 61.5208 | 61.5659
1741.0625 | 123.2986 | -61.4868 | 61.6745 | 0.030283 | -0.017627 | -0.007421 | 0.01619 | 0.045421 | -0.001406 | 0.051737 | 61.6241 | 0.19827 | 61.5462 | -0.042259 | 0.034501 | 61.5799 | -0.010593 | 61.3764 | 61.5171 | 61.4692 | 61.4794 | 61.503 | 61.5322 | 61.4854 | 61.5386 | 123.1109 | 61.6851 | 123.033 | 61.4446 | 61.5213 | 123.0667 | 61.4762 | 122.8632 | 61.5896 | 61.6347 | 61.5117 | 61.5568
1742.0625 | 123.2849 | -61.4914 | 61.6791 | 0.030283 | -0.017627 | -0.012 | 0.011611 | 0.036265 | -0.001406 | 0.051737 | 61.6104 | 0.20284 | 61.5416 | -0.042259 | 0.029923 | 61.5799 | -0.006014 | 61.381 | 61.5217 | 61.4738 | 61.4794 | 61.503 | 61.5277 | 61.49 | 61.5431 | 123.1018 | 61.6942 | 123.033 | 61.4491 | 61.5213 | 123.0713 | 61.4854 | 122.8724 | 61.5804 | 61.6164 | 61.5117 | 61.5476
1743.0625 | 123.2666 | -61.4914 | 61.6699 | 0.025705 | -0.022205 | -0.012 | 0.011611 | 0.036265 | -0.001406 | 0.051737 | 61.6195 | 0.19827 | 61.5141 | -0.051417 | 0.034501 | 61.5845 | 0.003143 | 61.381 | 61.5171 | 61.4692 | 61.4794 | 61.503 | 61.5277 | 61.49 | 61.5431 | 123.1109 | 61.6897 | 123.0055 | 61.44 | 61.5259 | 123.0759 | 61.4945 | 122.8724 | 61.585 | 61.6164 | 61.4796 | 61.511
1744.0625 | 123.3307 | -61.4594 | 61.6562 | 0.034862 | -0.022205 | -0.012 | 0.01619 | 0.045421 | -0.005985 | 0.051737 | 61.6149 | 0.212 | 61.5096 | -0.03768 | 0.034501 | 61.5799 | -0.001436 | 61.381 | 61.4942 | 61.4371 | 61.4474 | 61.4755 | 61.5048 | 61.4534 | 61.5111 | 123.0743 | 61.6714 | 122.9689 | 61.4217 | 61.4939 | 123.0392 | 61.4579 | 122.8403 | 61.5804 | 61.6164 | 61.4751 | 61.511
1745.0625 | 123.3536 | -61.4456 | 61.6241 | 0.030283 | -0.026784 | -0.012 | 0.01619 | 0.045421 | -0.005985 | 0.042581 | 61.6104 | 0.212 | 61.505 | -0.046838 | 0.034501 | 61.5845 | -0.001436 | 61.3764 | 61.4759 | 61.4188 | 61.4336 | 61.4618 | 61.491 | 61.4396 | 61.4882 | 123.056 | 61.6576 | 122.9506 | 61.3988 | 61.4801 | 123.0301 | 61.4442 | 122.822 | 61.5759 | 61.6118 | 61.4705 | 61.5064
1746.0625 | 123.3078 | -61.4731 | 61.6653 | 0.034862 | -0.026784 | -0.012 | 0.011611 | 0.040843 | 0.003172 | 0.056315 | 61.6149 | 0.20742 | 61.5141 | -0.03768 | 0.029923 | 61.5799 | -0.006014 | 61.3856 | 61.5079 | 61.4463 | 61.4611 | 61.4847 | 61.5139 | 61.4763 | 61.5294 | 123.088 | 61.6805 | 122.9872 | 61.4354 | 61.503 | 123.053 | 61.4671 | 122.8586 | 61.585 | 61.6209 | 61.4842 | 61.5202
1747.0625 | 123.2941 | -61.4639 | 61.6562 | 0.03944 | -0.022205 | -0.012 | 0.011611 | 0.036265 | -0.001406 | 0.047159 | 61.6195 | 0.20742 | 61.5187 | -0.03768 | 0.029923 | 61.5891 | -0.006014 | 61.381 | 61.5034 | 61.4417 | 61.4519 | 61.4755 | 61.5002 | 61.4625 | 61.5111 | 123.0834 | 61.6714 | 122.9826 | 61.4262 | 61.4939 | 123.053 | 61.4579 | 122.8449 | 61.5896 | 61.6255 | 61.4888 | 61.5247
1748.0625 | 123.381 | -61.4685 | 61.6562 | 0.034862 | -0.017627 | -0.016578 | 0.007033 | 0.040843 | 0.003172 | 0.051737 | 61.6104 | 0.20742 | 61.5096 | -0.03768 | 0.034501 | 61.5799 | 0.003143 | 61.381 | 61.5034 | 61.4509 | 61.4519 | 61.4755 | 61.5093 | 61.4717 | 61.5202 | 123.0789 | 61.6759 | 122.9781 | 61.4308 | 61.503 | 123.0484 | 61.4716 | 122.8495 | 61.5759 | 61.6072 | 61.4751 | 61.5064
1749.0625 | 123.2758 | -61.4914 | 61.6379 | 0.034862 | -0.022205 | -0.007421 | 0.011611 | 0.040843 | -0.001406 | 0.056315 | 61.6149 | 0.20742 | 61.5233 | -0.051417 | 0.029923 | 61.5799 | -0.006014 | 61.3718 | 61.5263 | 61.4692 | 61.484 | 61.503 | 61.5322 | 61.49 | 61.5477 | 123.1063 | 61.6988 | 123.0147 | 61.44 | 61.5213 | 123.0713 | 61.4854 | 122.8632 | 61.585 | 61.6209 | 61.4934 | 61.5293
1750.0625 | 123.4039 | -61.4731 | 61.6196 | 0.034862 | -0.022205 | -0.016578 | 0.007033 | 0.040843 | -0.005985 | 0.051737 | 61.6104 | 0.20742 | 61.5141 | -0.046838 | 0.029923 | 61.5799 | -0.006014 | 61.3764 | 61.5079 | 61.4509 | 61.4565 | 61.4801 | 61.5139 | 61.4671 | 61.5248 | 123.0834 | 61.6805 | 122.9872 | 61.4262 | 61.503 | 123.053 | 61.4671 | 122.8495 | 61.5804 | 61.6164 | 61.4842 | 61.5202
1751.0625 | 123.4131 | -61.4868 | 61.6196 | 0.030283 | -0.031363 | -0.012 | 0.01619 | 0.040843 | -0.001406 | 0.042581 | 61.6149 | 0.20742 | 61.505 | -0.042259 | 0.029923 | 61.5845 | -0.006014 | 61.3672 | 61.5171 | 61.4555 | 61.4748 | 61.503 | 61.5277 | 61.4854 | 61.5294 | 123.1017 | 61.6942 | 122.9918 | 61.4446 | 61.5167 | 123.0713 | 61.4808 | 122.8541 | 61.585 | 61.6209 | 61.4751 | 61.511
1752.0625 | 123.349 | -61.4914 | 61.6058 | 0.03944 | -0.026784 | -0.007421 | 0.007033 | 0.045421 | 0.003172 | 0.051737 | 61.6104 | 0.20742 | 61.5187 | -0.046838 | 0.025345 | 61.5845 | -0.001436 | 61.3718 | 61.5308 | 61.4646 | 61.484 | 61.4984 | 61.5368 | 61.4946 | 61.5431 | 123.1018 | 61.6988 | 123.0101 | 61.4446 | 61.5167 | 123.0759 | 61.49 | 122.8632 | 61.585 | 61.6118 | 61.4934 | 61.5202
1753.0625 | 123.4131 | -61.4502 | 61.6013 | 0.030283 | -0.013048 | -0.021157 | 0.011611 | 0.040843 | 0.00775 | 0.051737 | 61.6195 | 0.20742 | 61.537 | -0.042259 | 0.029923 | 61.5845 | -0.010593 | 61.381 | 61.4805 | 61.4371 | 61.429 | 61.4618 | 61.491 | 61.4579 | 61.5019 | 123.0697 | 61.6576 | 122.9872 | 61.4079 | 61.4801 | 123.0347 | 61.4396 | 122.8312 | 61.5896 | 61.6301 | 61.5071 | 61.5476
1754.0625 | 123.2391 | -61.496 | 61.6562 | 0.034862 | -0.022205 | -0.002842 | 0.01619 | 0.040843 | 0.012329 | 0.056315 | 61.6241 | 0.20742 | 61.5508 | -0.03768 | 0.034501 | 61.5799 | 0.003143 | 61.3764 | 61.5308 | 61.4738 | 61.4931 | 61.5122 | 61.5368 | 61.5083 | 61.5523 | 123.1201 | 61.7034 | 123.0467 | 61.4583 | 61.5305 | 123.0759 | 61.4991 | 122.8724 | 61.5896 | 61.6209 | 61.5163 | 61.5476
1755.0625 | 123.3856 | -61.4731 | 61.6196 | 0.030283 | -0.022205 | -0.012 | 0.007033 | 0.045421 | 0.003172 | 0.051737 | 61.6149 | 0.20742 | 61.5462 | -0.033101 | 0.029923 | 61.5845 | -0.006014 | 61.3718 | 61.5034 | 61.4509 | 61.4611 | 61.4801 | 61.5185 | 61.4763 | 61.5248 | 123.088 | 61.6805 | 123.0193 | 61.44 | 61.503 | 123.0576 | 61.4671 | 122.8449 | 61.585 | 61.6209 | 61.5163 | 61.5522
1756.0625 | 123.3673 | -61.4685 | 61.6196 | 0.030283 | -0.022205 | -0.007421 | 0.011611 | 0.045421 | 0.003172 | 0.060893 | 61.6241 | 0.20742 | 61.5508 | -0.046838 | 0.039079 | 61.5799 | 0.003143 | 61.3718 | 61.4988 | 61.4463 | 61.4611 | 61.4801 | 61.5139 | 61.4717 | 61.5294 | 123.0926 | 61.6759 | 123.0193 | 61.4217 | 61.5076 | 123.0484 | 61.4716 | 122.8403 | 61.585 | 61.6209 | 61.5117 | 61.5476
1757.0625 | 123.3536 | -61.496 | 61.5967 | 0.034862 | -0.022205 | -0.012 | 0.011611 | 0.040843 | -0.001406 | 0.051737 | 61.6058 | 0.20742 | 61.5553 | -0.046838 | 0.029923 | 61.5845 | -0.006014 | 61.3764 | 61.5308 | 61.4738 | 61.484 | 61.5076 | 61.5368 | 61.4946 | 61.5477 | 123.1017 | 61.7034 | 123.0513 | 61.4491 | 61.5259 | 123.0804 | 61.49 | 122.8724 | 61.5759 | 61.6118 | 61.5254 | 61.5614
1758.0625 | 123.3307 | -61.5051 | 61.6241 | 0.03944 | -0.013048 | -0.016578 | 0.011611 | 0.045421 | -0.001406 | 0.051737 | 61.6149 | 0.20742 | 61.5233 | -0.03768 | 0.025345 | 61.5753 | -0.010593 | 61.3764 | 61.5446 | 61.4921 | 61.4885 | 61.5167 | 61.5505 | 61.5037 | 61.5569 | 123.1201 | 61.7126 | 123.0284 | 61.4674 | 61.5305 | 123.0804 | 61.4945 | 122.8815 | 61.5896 | 61.6255 | 61.4979 | 61.5339
1759.0625 | 123.3673 | -61.4685 | 61.6104 | 0.030283 | -0.022205 | -0.016578 | 0.011611 | 0.040843 | -0.001406 | 0.051737 | 61.6149 | 0.212 | 61.5141 | -0.046838 | 0.029923 | 61.5845 | -0.006014 | 61.3718 | 61.4988 | 61.4463 | 61.4519 | 61.4801 | 61.5093 | 61.4671 | 61.5202 | 123.0834 | 61.6805 | 122.9826 | 61.4217 | 61.4984 | 123.053 | 61.4625 | 122.8403 | 61.585 | 61.6209 | 61.4842 | 61.5202
1760.0625 | 123.3353 | -61.4594 | 61.6013 | 0.025705 | -0.022205 | -0.012 | 0.007033 | 0.045421 | 0.003172 | 0.047159 | 61.6149 | 0.20284 | 61.505 | -0.055996 | 0.025345 | 61.5891 | -0.006014 | 61.3764 | 61.4851 | 61.4371 | 61.4474 | 61.4664 | 61.5048 | 61.4625 | 61.5065 | 123.0743 | 61.6622 | 122.9643 | 61.4034 | 61.4847 | 123.0484 | 61.4533 | 122.8357 | 61.5896 | 61.6209 | 61.4796 | 61.511
1761.0625 | 123.3856 | -61.4914 | 61.6379 | 0.030283 | -0.026784 | -0.016578 | 0.01619 | 0.045421 | 0.003172 | 0.051737 | 61.6149 | 0.212 | 61.5187 | -0.042259 | 0.029923 | 61.5799 | -0.001436 | 61.3718 | 61.5217 | 61.4646 | 61.4748 | 61.5076 | 61.5368 | 61.4946 | 61.5431 | 123.1063 | 61.7034 | 123.0101 | 61.4491 | 61.5213 | 123.0713 | 61.49 | 122.8632 | 61.585 | 61.6164 | 61.4888 | 61.5202
1762.0625 | 123.3215 | -61.4868 | 61.6058 | 0.030283 | -0.017627 | -0.016578 | 0.011611 | 0.040843 | 0.003172 | 0.047159 | 61.6149 | 0.20742 | 61.5141 | -0.046838 | 0.034501 | 61.5845 | -0.006014 | 61.3764 | 61.5171 | 61.4692 | 61.4702 | 61.4984 | 61.5277 | 61.49 | 61.534 | 123.1017 | 61.6942 | 123.001 | 61.44 | 61.5213 | 123.0713 | 61.4808 | 122.8632 | 61.5804 | 61.6209 | 61.4796 | 61.5202
1763.0625 | 123.3719 | -61.496 | 61.5738 | 0.034862 | -0.022205 | -0.012 | 0.011611 | 0.036265 | 0.003172 | 0.056315 | 61.6241 | 0.20742 | 61.5462 | -0.042259 | 0.029923 | 61.5845 | -0.006014 | 61.3764 | 61.5308 | 61.4738 | 61.484 | 61.5076 | 61.5322 | 61.4991 | 61.5523 | 123.1201 | 61.7034 | 123.0422 | 61.4537 | 61.5259 | 123.0804 | 61.49 | 122.8724 | 61.5942 | 61.6301 | 61.5163 | 61.5522
1764.0625 | 123.4085 | -61.4548 | 61.6379 | 0.025705 | -0.013048 | -0.021157 | 0.011611 | 0.040843 | 0.003172 | 0.056315 | 61.6287 | 0.19827 | 61.5508 | -0.046838 | 0.029923 | 61.5845 | -0.006014 | 61.381 | 61.4805 | 61.4417 | 61.4336 | 61.4664 | 61.4956 | 61.4579 | 61.5111 | 123.0834 | 61.653 | 123.0055 | 61.4079 | 61.4847 | 123.0392 | 61.4488 | 122.8357 | 61.5987 | 61.6347 | 61.5208 | 61.5568
1765.0625 | 123.3994 | -61.4502 | 61.6196 | 0.034862 | -0.017627 | -0.002842 | 0.011611 | 0.049999 | 0.003172 | 0.051737 | 61.6241 | 0.20742 | 61.5599 | -0.046838 | 0.029923 | 61.5845 | -0.010593 | 61.3672 | 61.4851 | 61.4326 | 61.4474 | 61.4618 | 61.5002 | 61.4534 | 61.5019 | 123.0743 | 61.6576 | 123.0101 | 61.4034 | 61.4801 | 123.0347 | 61.4396 | 122.8174 | 61.5942 | 61.6347 | 61.53 | 61.5705
1766.0625 | 123.4085 | -61.4914 | 61.6104 | 0.030283 | -0.022205 | -0.012 | 0.01619 | 0.045421 | 0.00775 | 0.056315 | 61.6195 | 0.20284 | 61.5553 | -0.042259 | 0.029923 | 61.5891 | -0.006014 | 61.3718 | 61.5217 | 61.4692 | 61.4794 | 61.5076 | 61.5368 | 61.4991 | 61.5477 | 123.1109 | 61.6942 | 123.0467 | 61.4491 | 61.5213 | 123.0804 | 61.4854 | 122.8632 | 61.5896 | 61.6255 | 61.5254 | 61.5614
1767.0625 | 123.3948 | -61.4777 | 61.6013 | 0.03944 | -0.017627 | -0.007421 | 0.011611 | 0.049999 | -0.001406 | 0.056315 | 61.6195 | 0.20742 | 61.537 | -0.042259 | 0.034501 | 61.5799 | -0.006014 | 61.3672 | 61.5171 | 61.46 | 61.4702 | 61.4893 | 61.5277 | 61.4763 | 61.534 | 123.0972 | 61.6851 | 123.0147 | 61.4354 | 61.5122 | 123.0576 | 61.4716 | 122.8449 | 61.585 | 61.6255 | 61.5025 | 61.543
1768.0625 | 123.3765 | -61.4594 | 61.5967 | 0.030283 | -0.022205 | -0.012 | 0.011611 | 0.045421 | -0.005985 | 0.051737 | 61.6241 | 0.20742 | 61.5279 | -0.051417 | 0.034501 | 61.5845 | -0.006014 | 61.3672 | 61.4896 | 61.4371 | 61.4474 | 61.471 | 61.5048 | 61.4534 | 61.5111 | 123.0834 | 61.6668 | 122.9872 | 61.4079 | 61.4939 | 123.0438 | 61.4533 | 122.8266 | 61.5896 | 61.6301 | 61.4934 | 61.5339
1769.0625 | 123.3948 | -61.4502 | 61.6425 | 0.034862 | -0.022205 | -0.007421 | 0.011611 | 0.036265 | 0.003172 | 0.051737 | 61.6195 | 0.20284 | 61.5141 | -0.051417 | 0.029923 | 61.5799 | -0.006014 | 61.3718 | 61.4851 | 61.428 | 61.4428 | 61.4618 | 61.4865 | 61.4534 | 61.5019 | 123.0697 | 61.653 | 122.9643 | 61.3988 | 61.4801 | 123.0301 | 61.4442 | 122.822 | 61.5896 | 61.6255 | 61.4842 | 61.5202
1770.0625 | 123.4039 | -61.4731 | 61.5921 | 0.034862 | -0.013048 | -0.016578 | 0.011611 | 0.045421 | 0.00775 | 0.051737 | 61.6104 | 0.212 | 61.505 | -0.03768 | 0.034501 | 61.5799 | -0.010593 | 61.3718 | 61.5079 | 61.46 | 61.4565 | 61.4847 | 61.5185 | 61.4808 | 61.5248 | 123.0834 | 61.6851 | 122.9781 | 61.4354 | 61.5076 | 123.053 | 61.4625 | 122.8449 | 61.5759 | 61.6209 | 61.4705 | 61.5156
1771.0625 | 123.3124 | -61.496 | 61.615 | 0.025705 | -0.017627 | -0.007421 | 0.01619 | 0.045421 | 0.003172 | 0.056315 | 61.6195 | 0.21658 | 61.5096 | -0.051417 | 0.020767 | 61.5891 | -0.006014 | 61.3718 | 61.5217 | 61.4783 | 61.4886 | 61.5122 | 61.5414 | 61.4991 | 61.5523 | 123.1155 | 61.7126 | 123.0055 | 61.4446 | 61.5167 | 123.085 | 61.49 | 122.8678 | 61.5987 | 61.6255 | 61.4888 | 61.5156
1772.0625 | 123.2025 | -61.5189 | 61.5829 | 0.03944 | -0.017627 | -0.007421 | 0.011611 | 0.036265 | 0.003172 | 0.056315 | 61.6195 | 0.20742 | 61.5324 | -0.046838 | 0.025345 | 61.5753 | -0.010593 | 61.3764 | 61.5583 | 61.5012 | 61.5114 | 61.5305 | 61.5551 | 61.522 | 61.5752 | 123.1384 | 61.7263 | 123.0513 | 61.472 | 61.5442 | 123.0942 | 61.5083 | 122.8953 | 61.5942 | 61.6301 | 61.5071 | 61.543
1773.0625 | 123.2437 | -61.5097 | 61.6379 | 0.034862 | -0.013048 | -0.007421 | 0.011611 | 0.045421 | 0.00775 | 0.047159 | 61.6241 | 0.20742 | 61.5508 | -0.046838 | 0.029923 | 61.5845 | -0.006014 | 61.3764 | 61.5446 | 61.4967 | 61.5023 | 61.5213 | 61.5551 | 61.5175 | 61.5569 | 123.1338 | 61.7171 | 123.0605 | 61.4629 | 61.5396 | 123.0942 | 61.5037 | 122.8861 | 61.5942 | 61.6301 | 61.5208 | 61.5568
1774.0625 | 123.3673 | -61.4914 | 61.6241 | 0.03944 | -0.013048 | -0.007421 | 0.01619 | 0.040843 | 0.012329 | 0.060893 | 61.6104 | 0.20742 | 61.5508 | -0.051417 | 0.029923 | 61.5799 | -0.010593 | 61.3718 | 61.5308 | 61.4783 | 61.484 | 61.5076 | 61.5322 | 61.5037 | 61.5523 | 123.1018 | 61.6988 | 123.0422 | 61.44 | 61.5213 | 123.0713 | 61.4808 | 122.8632 | 61.5804 | 61.6209 | 61.5208 | 61.5614
1775.0625 | 123.262 | -61.5097 | 61.6425 | 0.03944 | -0.013048 | -0.012 | 0.01619 | 0.045421 | 0.003172 | 0.060893 | 61.6195 | 0.212 | 61.5508 | -0.051417 | 0.025345 | 61.5845 | -0.010593 | 61.3764 | 61.5491 | 61.4967 | 61.4977 | 61.5259 | 61.5551 | 61.5129 | 61.5706 | 123.1292 | 61.7217 | 123.0605 | 61.4583 | 61.535 | 123.0942 | 61.4991 | 122.8861 | 61.5942 | 61.6301 | 61.5254 | 61.5614
1776.0625 | 123.2895 | -61.5005 | 61.6379 | 0.03944 | -0.017627 | -0.007421 | 0.01619 | 0.045421 | 0.003172 | 0.056315 | 61.6149 | 0.20742 | 61.5553 | -0.046838 | 0.029923 | 61.5799 | -0.010593 | 61.3718 | 61.54 | 61.4829 | 61.4931 | 61.5167 | 61.546 | 61.5037 | 61.5569 | 123.1155 | 61.708 | 123.0559 | 61.4537 | 61.5305 | 123.0804 | 61.49 | 122.8724 | 61.585 | 61.6255 | 61.5254 | 61.5659
1777.0625 | 123.2208 | -61.5463 | 61.5875 | 0.030283 | -0.022205 | -0.007421 | 0.011611 | 0.045421 | 0.00775 | 0.051737 | 61.6195 | 0.20284 | 61.5599 | -0.046838 | 0.029923 | 61.5845 | -0.001436 | 61.381 | 61.5766 | 61.5241 | 61.5389 | 61.5579 | 61.5917 | 61.5541 | 61.5981 | 123.1658 | 61.7492 | 123.1062 | 61.4995 | 61.5762 | 123.1308 | 61.5449 | 122.9273 | 61.5896 | 61.6209 | 61.53 | 61.5614
1778.0625 | 123.2712 | -61.5143 | 61.615 | 0.034862 | -0.017627 | -0.016578 | 0.020768 | 0.036265 | 0.003172 | 0.060893 | 61.6195 | 0.212 | 61.5553 | -0.046838 | 0.029923 | 61.5799 | -0.015171 | 61.3764 | 61.5491 | 61.4967 | 61.4977 | 61.535 | 61.5505 | 61.5175 | 61.5752 | 123.1338 | 61.7263 | 123.0696 | 61.4674 | 61.5442 | 123.0942 | 61.4991 | 122.8907 | 61.5896 | 61.6347 | 61.5254 | 61.5705
1779.0625 | 123.4085 | -61.4914 | 61.5921 | 0.034862 | -0.013048 | -0.007421 | 0.011611 | 0.045421 | 0.003172 | 0.056315 | 61.6195 | 0.20742 | 61.5553 | -0.042259 | 0.025345 | 61.5845 | -0.006014 | 61.3718 | 61.5263 | 61.4783 | 61.484 | 61.503 | 61.5368 | 61.4946 | 61.5477 | 123.1109 | 61.6988 | 123.0467 | 61.4491 | 61.5167 | 123.0759 | 61.4854 | 122.8632 | 61.5942 | 61.6255 | 61.53 | 61.5614
1780.0625 | 123.2895 | -61.4685 | 61.6516 | 0.030283 | -0.022205 | -0.007421 | 0.007033 | 0.049999 | 0.003172 | 0.060893 | 61.6149 | 0.20742 | 61.5599 | -0.042259 | 0.034501 | 61.5845 | -0.006014 | 61.3764 | 61.4988 | 61.4463 | 61.4611 | 61.4755 | 61.5185 | 61.4717 | 61.5294 | 123.0834 | 61.6759 | 123.0284 | 61.4262 | 61.503 | 123.053 | 61.4625 | 122.8449 | 61.5804 | 61.6209 | 61.5254 | 61.5659
1781.0625 | 123.2254 | -61.496 | 61.6333 | 0.03944 | -0.013048 | -0.021157 | 0.007033 | 0.059155 | 0.003172 | 0.056315 | 61.6195 | 0.20284 | 61.5599 | -0.042259 | 0.025345 | 61.5845 | -0.010593 | 61.3718 | 61.5354 | 61.4829 | 61.4748 | 61.503 | 61.5551 | 61.4991 | 61.5523 | 123.1155 | 61.6988 | 123.0559 | 61.4537 | 61.5213 | 123.0804 | 61.4854 | 122.8678 | 61.5942 | 61.6301 | 61.5346 | 61.5705
1782.0625 | 123.2758 | -61.5051 | 61.6608 | 0.030283 | -0.013048 | -0.007421 | 0.020768 | 0.045421 | 0.00775 | 0.060893 | 61.6195 | 0.212 | 61.5553 | -0.046838 | 0.029923 | 61.5845 | -0.006014 | 61.3718 | 61.5354 | 61.4921 | 61.4977 | 61.5259 | 61.5505 | 61.5129 | 61.566 | 123.1246 | 61.7171 | 123.0605 | 61.4583 | 61.535 | 123.0896 | 61.4991 | 122.8769 | 61.5896 | 61.6255 | 61.5254 | 61.5614
1783.0625 | 123.2895 | -61.4914 | 61.6516 | 0.03944 | -0.017627 | -0.007421 | 0.01619 | 0.045421 | 0.003172 | 0.060893 | 61.6241 | 0.20284 | 61.5599 | -0.042259 | 0.034501 | 61.5845 | -0.010593 | 61.3672 | 61.5308 | 61.4738 | 61.484 | 61.5076 | 61.5368 | 61.4946 | 61.5523 | 123.1155 | 61.6942 | 123.0513 | 61.4491 | 61.5259 | 123.0759 | 61.4808 | 122.8586 | 61.5896 | 61.6347 | 61.5254 | 61.5705
1784.0625 | 123.3582 | -61.4685 | 61.6013 | 0.034862 | -0.022205 | -0.016578 | 0.01619 | 0.045421 | 0.012329 | 0.056315 | 61.6149 | 0.212 | 61.5462 | -0.042259 | 0.029923 | 61.5799 | -0.006014 | 61.3764 | 61.5034 | 61.4463 | 61.4519 | 61.4847 | 61.5139 | 61.4808 | 61.5248 | 123.0834 | 61.6805 | 123.0147 | 61.4262 | 61.4984 | 123.0484 | 61.4625 | 122.8449 | 61.585 | 61.6209 | 61.5163 | 61.5522
1785.0625 | 123.3215 | -61.4594 | 61.6699 | 0.03944 | -0.013048 | -0.012 | 0.01619 | 0.045421 | 0.003172 | 0.060893 | 61.6241 | 0.21658 | 61.5553 | -0.042259 | 0.034501 | 61.5845 | -0.006014 | 61.3764 | 61.4988 | 61.4463 | 61.4474 | 61.4755 | 61.5048 | 61.4625 | 61.5202 | 123.0834 | 61.6759 | 123.0147 | 61.4171 | 61.4939 | 123.0438 | 61.4533 | 122.8357 | 61.5896 | 61.6301 | 61.5208 | 61.5614
1786.0625 | 123.3032 | -61.4731 | 61.647 | 0.034862 | -0.013048 | -0.007421 | 0.011611 | 0.045421 | 0.003172 | 0.060893 | 61.6149 | 0.20742 | 61.5553 | -0.046838 | 0.029923 | 61.5845 | -0.006014 | 61.381 | 61.5079 | 61.46 | 61.4657 | 61.4847 | 61.5185 | 61.4763 | 61.534 | 123.088 | 61.6805 | 123.0284 | 61.4262 | 61.503 | 123.0576 | 61.4671 | 122.8541 | 61.585 | 61.6209 | 61.5254 | 61.5614
1787.0625 | 123.3215 | -61.4731 | 61.6516 | 0.034862 | -0.013048 | -0.012 | 0.011611 | 0.045421 | 0.00775 | 0.051737 | 61.6195 | 0.20284 | 61.5599 | -0.03768 | 0.029923 | 61.5753 | -0.006014 | 61.3764 | 61.5079 | 61.46 | 61.4611 | 61.4847 | 61.5185 | 61.4808 | 61.5248 | 123.0926 | 61.6759 | 123.033 | 61.4354 | 61.503 | 123.0484 | 61.4671 | 122.8495 | 61.5896 | 61.6255 | 61.53 | 61.5659
1788.0625 | 123.2803 | -61.4914 | 61.6562 | 0.030283 | -0.017627 | -0.012 | 0.01619 | 0.049999 | 0.003172 | 0.060893 | 61.6287 | 0.20284 | 61.5599 | -0.042259 | 0.029923 | 61.5799 | -0.006014 | 61.3856 | 61.5217 | 61.4738 | 61.4794 | 61.5076 | 61.5414 | 61.4946 | 61.5523 | 123.1201 | 61.6942 | 123.0513 | 61.4491 | 61.5213 | 123.0713 | 61.4854 | 122.8769 | 61.5987 | 61.6347 | 61.53 | 61.5659
1789.0625 | 123.381 | -61.4548 | 61.6196 | 0.034862 | -0.013048 | -0.007421 | 0.011611 | 0.045421 | 0.00775 | 0.060893 | 61.6195 | 0.20742 | 61.5553 | -0.042259 | 0.025345 | 61.5799 | -0.006014 | 61.3764 | 61.4896 | 61.4417 | 61.4474 | 61.4664 | 61.5002 | 61.4625 | 61.5157 | 123.0743 | 61.6622 | 123.0101 | 61.4125 | 61.4801 | 123.0347 | 61.4488 | 122.8312 | 61.5942 | 61.6255 | 61.53 | 61.5614
1790.0625 | 123.2941 | -61.4777 | 61.6745 | 0.030283 | -0.017627 | -0.007421 | 0.020768 | 0.049999 | -0.001406 | 0.060893 | 61.6149 | 0.20284 | 61.5553 | -0.042259 | 0.025345 | 61.5845 | -0.001436 | 61.381 | 61.5079 | 61.46 | 61.4702 | 61.4984 | 61.5277 | 61.4763 | 61.5386 | 123.0926 | 61.6805 | 123.033 | 61.4354 | 61.503 | 123.0621 | 61.4762 | 122.8586 | 61.5896 | 61.6164 | 61.53 | 61.5568
1791.0625 | 123.2895 | -61.4777 | 61.6562 | 0.030283 | -0.013048 | -0.007421 | 0.011611 | 0.045421 | 0.003172 | 0.056315 | 61.6195 | 0.20742 | 61.5508 | -0.046838 | 0.034501 | 61.5845 | 0.003143 | 61.3856 | 61.5079 | 61.4646 | 61.4702 | 61.4893 | 61.5231 | 61.4808 | 61.534 | 123.0972 | 61.6851 | 123.0284 | 61.4308 | 61.5122 | 123.0621 | 61.4808 | 122.8632 | 61.585 | 61.6164 | 61.5163 | 61.5476
1792.0625 | 123.2849 | -61.4731 | 61.6699 | 0.034862 | -0.013048 | -0.012 | 0.01619 | 0.049999 | 0.003172 | 0.051737 | 61.6195 | 0.212 | 61.5141 | -0.042259 | 0.029923 | 61.5799 | -0.006014 | 61.3764 | 61.5079 | 61.46 | 61.4611 | 61.4893 | 61.5231 | 61.4763 | 61.5248 | 123.0926 | 61.6851 | 122.9872 | 61.4308 | 61.503 | 123.053 | 61.4671 | 122.8495 | 61.5896 | 61.6255 | 61.4842 | 61.5202
1793.0625 | 123.3078 | -61.4685 | 61.6837 | 0.03944 | -0.013048 | -0.016578 | 0.011611 | 0.045421 | 0.00775 | 0.056315 | 61.6104 | 0.21658 | 61.5187 | -0.046838 | 0.029923 | 61.5799 | -0.006014 | 61.3718 | 61.5079 | 61.4555 | 61.4519 | 61.4801 | 61.5139 | 61.4763 | 61.5248 | 123.0789 | 61.6851 | 122.9872 | 61.4217 | 61.4984 | 123.0484 | 61.4625 | 122.8403 | 61.5804 | 61.6164 | 61.4888 | 61.5247
1794.0625 | 123.2941 | -61.4777 | 61.6653 | 0.034862 | -0.013048 | -0.002842 | 0.01619 | 0.045421 | 0.00775 | 0.060893 | 61.6149 | 0.212 | 61.5141 | -0.042259 | 0.034501 | 61.5845 | -0.001436 | 61.3764 | 61.5125 | 61.4646 | 61.4748 | 61.4939 | 61.5231 | 61.4854 | 61.5386 | 123.0926 | 61.6897 | 122.9918 | 61.4354 | 61.5122 | 123.0621 | 61.4762 | 122.8541 | 61.5804 | 61.6164 | 61.4796 | 61.5156
1795.0625 | 123.2666 | -61.4822 | 61.6974 | 0.034862 | -0.017627 | -0.002842 | 0.01619 | 0.045421 | 0.003172 | 0.051737 | 61.6149 | 0.212 | 61.5141 | -0.03768 | 0.034501 | 61.5753 | -0.001436 | 61.381 | 61.5171 | 61.4646 | 61.4794 | 61.4984 | 61.5277 | 61.4854 | 61.534 | 123.0972 | 61.6942 | 122.9964 | 61.4446 | 61.5167 | 123.0576 | 61.4808 | 122.8632 | 61.5804 | 61.6164 | 61.4796 | 61.5156
1796.0625 | 123.2941 | -61.5097 | 61.6699 | 0.03944 | -0.013048 | -0.012 | 0.020768 | 0.045421 | 0.016907 | 0.07005 | 61.647 | 0.20742 | 61.5782 | -0.069733 | 0.029923 | 61.5936 | 0.012299 | 61.5458 | 61.5491 | 61.4967 | 61.4977 | 61.5305 | 61.5551 | 61.5266 | 61.5798 | 123.1567 | 61.7171 | 123.0879 | 61.44 | 61.5396 | 123.1033 | 61.522 | 123.0555 | 61.6171 | 61.6347 | 61.5483 | 61.5659
1797.0625 | 123.2895 | -61.5005 | 61.6699 | 0.025705 | -0.013048 | -0.002842 | 0.01619 | 0.049999 | 0.003172 | 0.056315 | 61.6149 | 0.20742 | 61.5508 | -0.092628 | 0.029923 | 61.5753 | -0.010593 | 61.3306 | 61.5263 | 61.4875 | 61.4977 | 61.5167 | 61.5505 | 61.5037 | 61.5569 | 123.1155 | 61.708 | 123.0513 | 61.4079 | 61.5305 | 123.0759 | 61.49 | 122.8312 | 61.585 | 61.6255 | 61.5208 | 61.5614
1798.0625 | 123.2803 | -61.4731 | 61.615 | 0.034862 | -0.013048 | -0.016578 | 0.011611 | 0.045421 | -0.001406 | 0.051737 | 61.6104 | 0.20284 | 61.537 | -0.088049 | 0.016188 | 61.5845 | -0.006014 | 61.3123 | 61.5079 | 61.46 | 61.4565 | 61.4847 | 61.5185 | 61.4717 | 61.5248 | 123.0834 | 61.6759 | 123.0101 | 61.385 | 61.4893 | 123.0576 | 61.4671 | 122.7854 | 61.5942 | 61.6164 | 61.5208 | 61.543
1799.0625 | 123.3398 | -61.496 | 61.6699 | 0.025705 | -0.008469 | -0.007421 | 0.011611 | 0.059155 | 0.012329 | 0.056315 | 61.6241 | 0.212 | 61.5599 | -0.12926 | 0.029923 | 61.5799 | -0.006014 | 61.3215 | 61.5217 | 61.4875 | 61.4886 | 61.5076 | 61.5551 | 61.5083 | 61.5523 | 123.1201 | 61.708 | 123.0559 | 61.3667 | 61.5259 | 123.0759 | 61.49 | 122.8174 | 61.5942 | 61.6301 | 61.53 | 61.5659
1800.0625 | 123.381 | -61.4685 | 61.6058 | 0.025705 | -0.013048 | -0.012 | 0.01619 | 0.040843 | 0.003172 | 0.060893 | 61.6195 | 0.212 | 61.5553 | -0.12468 | 0.029923 | 61.5799 | -0.010593 | 61.3169 | 61.4942 | 61.4555 | 61.4565 | 61.4847 | 61.5093 | 61.4717 | 61.5294 | 123.088 | 61.6805 | 123.0238 | 61.3438 | 61.4984 | 123.0484 | 61.4579 | 122.7854 | 61.5896 | 61.6301 | 61.5254 | 61.5659
1801.0625 | 123.3765 | -61.441 | 61.6425 | 0.025705 | -0.008469 | -0.016578 | 0.007033 | 0.049999 | -0.001406 | 0.051737 | 61.6104 | 0.212 | 61.5279 | -0.092628 | 0.034501 | 61.5799 | -0.010593 | 61.3215 | 61.4667 | 61.4326 | 61.4245 | 61.4481 | 61.491 | 61.4396 | 61.4928 | 123.0514 | 61.653 | 122.9689 | 61.3484 | 61.4755 | 123.0209 | 61.4304 | 122.7625 | 61.5759 | 61.6209 | 61.4934 | 61.5385
1802.0625 | 123.3582 | -61.4365 | 61.6562 | 0.030283 | -0.013048 | -0.012 | 0.01619 | 0.045421 | -0.001406 | 0.060893 | 61.6195 | 0.20742 | 61.5004 | -0.10637 | 0.029923 | 61.5799 | -0.006014 | 61.3169 | 61.4667 | 61.4234 | 61.4245 | 61.4527 | 61.4819 | 61.4351 | 61.4974 | 123.056 | 61.6439 | 122.9369 | 61.3301 | 61.4664 | 123.0164 | 61.4304 | 122.7533 | 61.5896 | 61.6255 | 61.4705 | 61.5064
1803.0625 | 123.2529 | -61.4685 | 61.6653 | 0.048597 | 0.005267 | -0.002842 | 0.020768 | 0.054577 | 0.012329 | 0.079206 | 61.647 | 0.20284 | 61.5965 | -0.08347 | 0.029923 | 61.5707 | -0.010593 | 61.3581 | 61.5171 | 61.4738 | 61.4657 | 61.4893 | 61.5231 | 61.4808 | 61.5477 | 123.1155 | 61.6714 | 123.0651 | 61.385 | 61.4984 | 123.0392 | 61.4579 | 122.8266 | 61.6171 | 61.6576 | 61.5666 | 61.6071
1804.0625 | 123.3536 | -61.4822 | 61.6196 | 0.030283 | -0.013048 | -0.021157 | 0.007033 | 0.036265 | -0.001406 | 0.060893 | 61.6378 | 0.20742 | 61.5599 | -0.023943 | 0.048236 | 61.5845 | -0.070112 | 61.3489 | 61.5125 | 61.4692 | 61.4611 | 61.4893 | 61.5185 | 61.4808 | 61.5431 | 123.1201 | 61.6897 | 123.0422 | 61.4583 | 61.5305 | 123.0667 | 61.4121 | 122.8312 | 61.5896 | 61.7079 | 61.5117 | 61.63
1805.0625 | 123.381 | -61.4548 | 61.6379 | 0.025705 | -0.013048 | -0.016578 | 0.01619 | 0.040843 | 0.003172 | 0.056315 | 61.6149 | 0.212 | 61.537 | -0.019364 | 0.048236 | 61.5891 | 0.012299 | 61.326 | 61.4805 | 61.4417 | 61.4382 | 61.471 | 61.4956 | 61.4579 | 61.5111 | 123.0697 | 61.6668 | 122.9918 | 61.4354 | 61.503 | 123.0438 | 61.4671 | 122.7808 | 61.5667 | 61.6026 | 61.4888 | 61.5247
1806.0625 | 123.3627 | -61.4731 | 61.6058 | 0.034862 | -0.017627 | -0.012 | 0.01619 | 0.045421 | 0.003172 | 0.056315 | 61.6149 | 0.212 | 61.5324 | -0.092628 | 0.034501 | 61.5845 | 0.012299 | 61.5412 | 61.5079 | 61.4555 | 61.4611 | 61.4893 | 61.5185 | 61.4763 | 61.5294 | 123.088 | 61.6851 | 123.0055 | 61.3805 | 61.5076 | 123.0576 | 61.4854 | 123.0143 | 61.5804 | 61.6026 | 61.4979 | 61.5202
1807.0625 | 123.3353 | -61.4822 | 61.6104 | 0.025705 | -0.017627 | -0.007421 | 0.01619 | 0.040843 | 0.003172 | 0.060893 | 61.6195 | 0.20742 | 61.5462 | -0.03768 | 0.029923 | 61.5845 | 0.016878 | 61.3443 | 61.5079 | 61.4646 | 61.4748 | 61.4984 | 61.5231 | 61.4854 | 61.5431 | 123.1018 | 61.6897 | 123.0284 | 61.4446 | 61.5122 | 123.0667 | 61.4991 | 122.8266 | 61.5896 | 61.6026 | 61.5163 | 61.5293
1808.0625 | 123.3078 | -61.4868 | 61.6562 | 0.030283 | -0.00389 | -0.002842 | 0.020768 | 0.049999 | 0.003172 | 0.056315 | 61.6287 | 0.212 | 61.5599 | -0.051417 | 0.034501 | 61.5845 | -0.001436 | 61.3718 | 61.5171 | 61.4829 | 61.484 | 61.5076 | 61.5368 | 61.49 | 61.5431 | 123.1155 | 61.6988 | 123.0467 | 61.4354 | 61.5213 | 123.0713 | 61.4854 | 122.8586 | 61.5942 | 61.6301 | 61.5254 | 61.5614
1809.0625 | 123.3353 | -61.4868 | 61.615 | 0.034862 | -0.00389 | -0.012 | 0.01619 | 0.049999 | 0.00775 | 0.056315 | 61.6195 | 0.212 | 61.5508 | -0.051417 | 0.029923 | 61.5891 | -0.006014 | 61.3672 | 61.5217 | 61.4829 | 61.4748 | 61.503 | 61.5368 | 61.4946 | 61.5431 | 123.1063 | 61.6988 | 123.0376 | 61.4354 | 61.5167 | 123.0759 | 61.4808 | 122.8541 | 61.5896 | 61.6255 | 61.5208 | 61.5568
1810.0625 | 123.349 | -61.4548 | 61.6013 | 0.030283 | -0.013048 | -0.012 | 0.011611 | 0.049999 | 0.012329 | 0.060893 | 61.6149 | 0.20284 | 61.5599 | -0.060575 | 0.025345 | 61.5799 | -0.001436 | 61.3627 | 61.4851 | 61.4417 | 61.4428 | 61.4664 | 61.5048 | 61.4671 | 61.5157 | 123.0697 | 61.6576 | 123.0147 | 61.3942 | 61.4801 | 123.0347 | 61.4533 | 122.8174 | 61.5896 | 61.6164 | 61.5346 | 61.5614
1811.0625 | 123.3398 | -61.4685 | 61.615 | 0.030283 | -0.017627 | -0.012 | 0.011611 | 0.040843 | 0.00775 | 0.056315 | 61.6149 | 0.20742 | 61.5508 | -0.074312 | 0.025345 | 61.5845 | -0.006014 | 61.3581 | 61.4988 | 61.4509 | 61.4565 | 61.4801 | 61.5093 | 61.4763 | 61.5248 | 123.0834 | 61.6759 | 123.0193 | 61.3942 | 61.4939 | 123.053 | 61.4625 | 122.8266 | 61.5896 | 61.6209 | 61.5254 | 61.5568
1812.0625 | 123.381 | -61.4777 | 61.5829 | 0.034862 | -0.00389 | -0.016578 | 0.025347 | 0.049999 | 0.016907 | 0.07005 | 61.6241 | 0.212 | 61.5691 | -0.092628 | 0.029923 | 61.5845 | -0.010593 | 61.3352 | 61.5125 | 61.4738 | 61.4611 | 61.503 | 61.5277 | 61.4946 | 61.5477 | 123.1018 | 61.6897 | 123.0467 | 61.385 | 61.5076 | 123.0621 | 61.4671 | 122.8129 | 61.5942 | 61.6347 | 61.5392 | 61.5797
1813.0625 | 123.349 | -61.4639 | 61.6425 | 0.03944 | -0.013048 | -0.012 | 0.020768 | 0.054577 | 0.012329 | 0.07005 | 61.6561 | 0.20742 | 61.592 | -0.092628 | 0.029923 | 61.5845 | -0.015171 | 61.3398 | 61.5034 | 61.4509 | 61.4519 | 61.4847 | 61.5185 | 61.4763 | 61.534 | 123.1201 | 61.6714 | 123.0559 | 61.3713 | 61.4939 | 123.0484 | 61.4488 | 122.8037 | 61.6262 | 61.6713 | 61.562 | 61.6071
1814.0625 | 123.381 | -61.4777 | 61.6425 | 0.034862 | -0.008469 | -0.002842 | 0.025347 | 0.049999 | 0.00775 | 0.060893 | 61.6424 | 0.212 | 61.592 | -0.10179 | 0.034501 | 61.5891 | -0.010593 | 61.326 | 61.5125 | 61.4692 | 61.4748 | 61.503 | 61.5277 | 61.4854 | 61.5386 | 123.1201 | 61.6897 | 123.0696 | 61.3759 | 61.5122 | 123.0667 | 61.4671 | 122.8037 | 61.6079 | 61.653 | 61.5575 | 61.6026
1815.0625 | 123.3582 | -61.4639 | 61.5692 | 0.044018 | -0.00389 | -0.007421 | 0.020768 | 0.054577 | 0.003172 | 0.065472 | 61.647 | 0.21658 | 61.5782 | -0.11094 | 0.034501 | 61.5891 | -0.015171 | 61.3215 | 61.5079 | 61.46 | 61.4565 | 61.4847 | 61.5185 | 61.4671 | 61.5294 | 123.1109 | 61.6805 | 123.0422 | 61.353 | 61.4984 | 123.053 | 61.4488 | 122.7854 | 61.6125 | 61.6622 | 61.5437 | 61.5934
1816.0625 | 123.3994 | -61.4731 | 61.5921 | 0.03944 | -0.008469 | -0.007421 | 0.020768 | 0.059155 | 0.00775 | 0.065472 | 61.6424 | 0.212 | 61.5782 | -0.10637 | 0.034501 | 61.5845 | -0.006014 | 61.326 | 61.5125 | 61.4646 | 61.4657 | 61.4939 | 61.5322 | 61.4808 | 61.5386 | 123.1155 | 61.6851 | 123.0513 | 61.3667 | 61.5076 | 123.0576 | 61.4671 | 122.7991 | 61.6079 | 61.6484 | 61.5437 | 61.5842
1817.0625 | 123.3902 | -61.4777 | 61.5829 | 0.034862 | -0.008469 | -0.002842 | 0.011611 | 0.049999 | 0.00775 | 0.07005 | 61.6378 | 0.20742 | 61.5737 | -0.055996 | 0.025345 | 61.5799 | -0.006014 | 61.3443 | 61.5125 | 61.4692 | 61.4748 | 61.4893 | 61.5277 | 61.4854 | 61.5477 | 123.1155 | 61.6851 | 123.0513 | 61.4217 | 61.503 | 123.0576 | 61.4716 | 122.822 | 61.6125 | 61.6438 | 61.5483 | 61.5797
1818.0625 | 123.3627 | -61.4594 | 61.6013 | 0.034862 | -0.008469 | -0.016578 | 0.020768 | 0.059155 | 0.016907 | 0.07005 | 61.6378 | 0.20742 | 61.5828 | -0.028522 | 0.025345 | 61.5891 | -0.001436 | 61.3489 | 61.4942 | 61.4509 | 61.4428 | 61.4801 | 61.5185 | 61.4763 | 61.5294 | 123.0972 | 61.6668 | 123.0422 | 61.4308 | 61.4847 | 123.0484 | 61.4579 | 122.8083 | 61.6125 | 61.6393 | 61.5575 | 61.5842
1819.0625 | 123.3627 | -61.4914 | 61.6287 | 0.030283 | -0.008469 | -0.007421 | 0.01619 | 0.059155 | 0.012329 | 0.065472 | 61.6378 | 0.212 | 61.5782 | -0.014785 | 0.025345 | 61.5799 | -0.006014 | 61.3535 | 61.5217 | 61.4829 | 61.484 | 61.5076 | 61.5505 | 61.5037 | 61.5569 | 123.1292 | 61.7034 | 123.0696 | 61.4766 | 61.5167 | 123.0713 | 61.4854 | 122.8449 | 61.6125 | 61.6438 | 61.5529 | 61.5842
1820.0625 | 123.2483 | -61.5189 | 61.6379 | 0.03944 | -0.00389 | -0.012 | 0.01619 | 0.049999 | 0.016907 | 0.07005 | 61.6378 | 0.212 | 61.5782 | -0.046838 | 0.034501 | 61.5753 | -0.006014 | 61.3489 | 61.5583 | 61.515 | 61.5069 | 61.535 | 61.5689 | 61.5358 | 61.5889 | 123.1567 | 61.7309 | 123.0971 | 61.472 | 61.5534 | 123.0942 | 61.5128 | 122.8678 | 61.6033 | 61.6438 | 61.5437 | 61.5842
1821.0625 | 123.2803 | -61.5051 | 61.6608 | 0.03944 | 0.000689 | -0.002842 | 0.020768 | 0.059155 | 0.012329 | 0.07005 | 61.6378 | 0.212 | 61.5782 | -0.11552 | 0.029923 | 61.5799 | -0.010593 | 61.3443 | 61.5446 | 61.5058 | 61.5023 | 61.5259 | 61.5643 | 61.5175 | 61.5752 | 123.143 | 61.7171 | 123.0834 | 61.3896 | 61.535 | 123.085 | 61.4945 | 122.8495 | 61.6079 | 61.6484 | 61.5483 | 61.5888
1822.0625 | 123.2895 | -61.4822 | 61.6241 | 0.03944 | -0.008469 | -0.007421 | 0.025347 | 0.049999 | 0.016907 | 0.060893 | 61.6332 | 0.212 | 61.5737 | -0.097207 | 0.029923 | 61.5753 | -0.001436 | 61.3306 | 61.5217 | 61.4738 | 61.4748 | 61.5076 | 61.5322 | 61.4991 | 61.5431 | 123.1155 | 61.6942 | 123.0559 | 61.385 | 61.5122 | 123.0576 | 61.4808 | 122.8129 | 61.6033 | 61.6347 | 61.5437 | 61.5751
1823.0625 | 123.3124 | -61.4822 | 61.6333 | 0.034862 | 0.000689 | -0.002842 | 0.01619 | 0.054577 | 0.00775 | 0.07005 | 61.6378 | 0.212 | 61.5782 | -0.12468 | 0.029923 | 61.5753 | -0.019749 | 61.3306 | 61.5171 | 61.4829 | 61.4794 | 61.4984 | 61.5368 | 61.49 | 61.5523 | 123.1201 | 61.6942 | 123.0605 | 61.3576 | 61.5122 | 123.0576 | 61.4625 | 122.8129 | 61.6079 | 61.6576 | 61.5483 | 61.598
1824.0625 | 123.3536 | -61.4639 | 61.6287 | 0.034862 | -0.00389 | -0.007421 | 0.025347 | 0.049999 | 0.00775 | 0.07005 | 61.6378 | 0.20742 | 61.5737 | -0.10179 | 0.029923 | 61.5891 | -0.015171 | 61.3306 | 61.4988 | 61.46 | 61.4565 | 61.4893 | 61.5139 | 61.4717 | 61.534 | 123.1018 | 61.6714 | 123.0376 | 61.3621 | 61.4939 | 123.053 | 61.4488 | 122.7945 | 61.6079 | 61.653 | 61.5437 | 61.5888
1825.0625 | 123.2712 | -61.5143 | 61.6425 | 0.03944 | -0.00389 | -0.007421 | 0.025347 | 0.049999 | 0.012329 | 0.065472 | 61.647 | 0.20742 | 61.5874 | -0.10179 | 0.034501 | 61.5845 | -0.006014 | 61.3306 | 61.5537 | 61.5104 | 61.5069 | 61.5396 | 61.5643 | 61.5266 | 61.5798 | 123.1613 | 61.7217 | 123.1017 | 61.4125 | 61.5488 | 123.0988 | 61.5083 | 122.8449 | 61.6125 | 61.653 | 61.5529 | 61.5934
1826.0625 | 123.262 | -61.5005 | 61.6425 | 0.034862 | -0.00389 | -0.007421 | 0.029925 | 0.054577 | 0.012329 | 0.07005 | 61.6424 | 0.212 | 61.5782 | -0.092628 | 0.034501 | 61.5799 | -0.010593 | 61.3352 | 61.5354 | 61.4967 | 61.4931 | 61.5305 | 61.5551 | 61.5129 | 61.5706 | 123.143 | 61.7126 | 123.0788 | 61.4079 | 61.535 | 123.0804 | 61.49 | 122.8357 | 61.6079 | 61.653 | 61.5437 | 61.5888
1827.0625 | 123.2986 | -61.4594 | 61.647 | 0.03944 | -0.008469 | -0.007421 | 0.025347 | 0.059155 | 0.016907 | 0.07005 | 61.6561 | 0.212 | 61.5874 | -0.046838 | 0.034501 | 61.5845 | -0.006014 | 61.3581 | 61.4988 | 61.4509 | 61.4519 | 61.4847 | 61.5185 | 61.4763 | 61.5294 | 123.1155 | 61.6714 | 123.0467 | 61.4125 | 61.4939 | 123.0438 | 61.4533 | 122.8174 | 61.6216 | 61.6622 | 61.5529 | 61.5934
1828.0625 | 123.3124 | -61.4822 | 61.6653 | 0.034862 | 0.000689 | -0.007421 | 0.01619 | 0.059155 | 0.016907 | 0.074628 | 61.647 | 0.212 | 61.5874 | -0.019364 | 0.039079 | 61.5799 | -0.006014 | 61.3489 | 61.5171 | 61.4829 | 61.4748 | 61.4984 | 61.5414 | 61.4991 | 61.5569 | 123.1292 | 61.6942 | 123.0696 | 61.4629 | 61.5213 | 123.0621 | 61.4762 | 122.8312 | 61.6079 | 61.653 | 61.5483 | 61.5934
1829.0625 | 123.2712 | -61.5143 | 61.6333 | 0.03944 | -0.00389 | -0.007421 | 0.025347 | 0.059155 | 0.012329 | 0.079206 | 61.6516 | 0.212 | 61.5965 | -0.078891 | 0.034501 | 61.5799 | -0.010593 | 61.3306 | 61.5537 | 61.5104 | 61.5069 | 61.5396 | 61.5734 | 61.5266 | 61.5935 | 123.1658 | 61.7263 | 123.1108 | 61.4354 | 61.5488 | 123.0942 | 61.5037 | 122.8449 | 61.6171 | 61.6622 | 61.562 | 61.6071
1830.0625 | 123.3032 | -61.5051 | 61.6516 | 0.048597 | -0.00389 | -0.007421 | 0.020768 | 0.059155 | 0.021485 | 0.07005 | 61.6561 | 0.20742 | 61.592 | -0.097207 | 0.034501 | 61.5845 | -0.006014 | 61.326 | 61.5537 | 61.5012 | 61.4977 | 61.5259 | 61.5643 | 61.5266 | 61.5752 | 123.1613 | 61.7126 | 123.0971 | 61.4079 | 61.5396 | 123.0896 | 61.4991 | 122.8312 | 61.6216 | 61.6622 | 61.5575 | 61.598
1831.0625 | 123.2758 | -61.496 | 61.6425 | 0.044018 | -0.008469 | -0.007421 | 0.025347 | 0.059155 | 0.012329 | 0.074628 | 61.6607 | 0.20284 | 61.592 | -0.088049 | 0.034501 | 61.5753 | -0.010593 | 61.3306 | 61.54 | 61.4875 | 61.4886 | 61.5213 | 61.5551 | 61.5083 | 61.5706 | 123.1567 | 61.6988 | 123.0879 | 61.4079 | 61.5305 | 123.0713 | 61.4854 | 122.8266 | 61.6262 | 61.6713 | 61.5575 | 61.6026
1832.0625 | 123.3261 | -61.496 | 61.6608 | 0.03944 | 0.000689 | -0.007421 | 0.025347 | 0.06831 | 0.016907 | 0.074628 | 61.6561 | 0.20742 | 61.5874 | -0.088049 | 0.043657 | 61.5799 | -0.010593 | 61.3352 | 61.5354 | 61.4967 | 61.4886 | 61.5213 | 61.5643 | 61.5129 | 61.5706 | 123.1521 | 61.7034 | 123.0834 | 61.4079 | 61.5396 | 123.0759 | 61.4854 | 122.8312 | 61.6125 | 61.6667 | 61.5437 | 61.598
1833.0625 | 123.2941 | -61.4685 | 61.647 | 0.034862 | 0.000689 | -0.002842 | 0.020768 | 0.06831 | 0.012329 | 0.074628 | 61.6607 | 0.21658 | 61.6011 | -0.088049 | 0.034501 | 61.5845 | -0.010593 | 61.3352 | 61.5034 | 61.4692 | 61.4657 | 61.4893 | 61.5368 | 61.4808 | 61.5431 | 123.1292 | 61.6851 | 123.0696 | 61.3805 | 61.503 | 123.053 | 61.4579 | 122.8037 | 61.6262 | 61.6713 | 61.5666 | 61.6117
1834.0625 | 123.2803 | -61.4822 | 61.6699 | 0.044018 | 0.000689 | -0.007421 | 0.025347 | 0.063733 | 0.016907 | 0.07005 | 61.6378 | 0.212 | 61.5874 | -0.092628 | 0.034501 | 61.5891 | -0.010593 | 61.3398 | 61.5263 | 61.4829 | 61.4748 | 61.5076 | 61.546 | 61.4991 | 61.5523 | 123.1201 | 61.6942 | 123.0696 | 61.3896 | 61.5167 | 123.0713 | 61.4716 | 122.822 | 61.6033 | 61.6484 | 61.5529 | 61.598
1835.0625 | 123.317 | -61.4914 | 61.6653 | 0.044018 | -0.00389 | -0.002842 | 0.029925 | 0.054577 | 0.016907 | 0.074628 | 61.6241 | 0.212 | 61.5508 | -0.08347 | 0.039079 | 61.5753 | -0.001436 | 61.3443 | 61.5354 | 61.4875 | 61.4886 | 61.5213 | 61.546 | 61.5083 | 61.566 | 123.1155 | 61.7034 | 123.0422 | 61.4079 | 61.5305 | 123.0667 | 61.49 | 122.8357 | 61.585 | 61.6255 | 61.5117 | 61.5522
1836.0625 | 123.2758 | -61.4731 | 61.6653 | 0.03944 | -0.008469 | -0.002842 | 0.020768 | 0.049999 | 0.012329 | 0.060893 | 61.6241 | 0.212 | 61.5599 | -0.08347 | 0.034501 | 61.5845 | -0.001436 | 61.3535 | 61.5125 | 61.4646 | 61.4702 | 61.4939 | 61.5231 | 61.4854 | 61.534 | 123.0972 | 61.6851 | 123.033 | 61.3896 | 61.5076 | 123.0576 | 61.4716 | 122.8266 | 61.5896 | 61.6255 | 61.5254 | 61.5614
1837.0625 | 123.3032 | -61.4868 | 61.647 | 0.030283 | -0.00389 | -0.007421 | 0.025347 | 0.049999 | 0.00775 | 0.060893 | 61.6332 | 0.212 | 61.5645 | -0.069733 | 0.025345 | 61.5799 | -0.010593 | 61.3535 | 61.5171 | 61.4829 | 61.4794 | 61.5122 | 61.5368 | 61.4946 | 61.5477 | 123.1201 | 61.6988 | 123.0513 | 61.4171 | 61.5122 | 123.0667 | 61.4762 | 122.8403 | 61.6079 | 61.6438 | 61.5392 | 61.5751
1838.0625 | 123.2895 | -61.4777 | 61.6791 | 0.03944 | -0.008469 | -0.012 | 0.025347 | 0.054577 | 0.012329 | 0.07005 | 61.6241 | 0.20742 | 61.5645 | -0.078891 | 0.029923 | 61.5845 | -0.001436 | 61.3672 | 61.5171 | 61.4692 | 61.4657 | 61.503 | 61.5322 | 61.49 | 61.5477 | 123.1018 | 61.6851 | 123.0422 | 61.3988 | 61.5076 | 123.0621 | 61.4762 | 122.8449 | 61.5942 | 61.6255 | 61.5346 | 61.5659
1839.0625 | 123.2574 | -61.496 | 61.6516 | 0.030283 | -0.008469 | -0.002842 | 0.025347 | 0.054577 | 0.012329 | 0.065472 | 61.6241 | 0.212 | 61.5645 | -0.060575 | 0.020767 | 61.5753 | -0.006014 | 61.3627 | 61.5263 | 61.4875 | 61.4931 | 61.5213 | 61.5505 | 61.5083 | 61.5614 | 123.1201 | 61.708 | 123.0605 | 61.4354 | 61.5167 | 123.0713 | 61.49 | 122.8586 | 61.6033 | 61.6301 | 61.5437 | 61.5705
1840.0625 | 123.2712 | -61.4868 | 61.6699 | 0.030283 | -0.008469 | -0.002842 | 0.011611 | 0.045421 | 0.003172 | 0.065472 | 61.6195 | 0.212 | 61.5508 | -0.051417 | 0.034501 | 61.5845 | -0.001436 | 61.3672 | 61.5171 | 61.4783 | 61.484 | 61.4984 | 61.5322 | 61.49 | 61.5523 | 123.1063 | 61.6988 | 123.0376 | 61.4354 | 61.5213 | 123.0713 | 61.4854 | 122.8541 | 61.585 | 61.6209 | 61.5163 | 61.5522
1841.0625 | 123.3124 | -61.4685 | 61.647 | 0.030283 | -0.008469 | -0.016578 | 0.01619 | 0.049999 | 0.00775 | 0.060893 | 61.6195 | 0.212 | 61.5324 | -0.051417 | 0.029923 | 61.5891 | -0.010593 | 61.3672 | 61.4988 | 61.46 | 61.4519 | 61.4847 | 61.5185 | 61.4763 | 61.5294 | 123.088 | 61.6805 | 123.001 | 61.4171 | 61.4984 | 123.0576 | 61.4579 | 122.8357 | 61.5896 | 61.6301 | 61.5025 | 61.543
1842.0625 | 123.2574 | -61.5097 | 61.6882 | 0.025705 | -0.013048 | -0.002842 | 0.020768 | 0.054577 | 0.00775 | 0.065472 | 61.6195 | 0.20742 | 61.5324 | -0.042259 | 0.029923 | 61.5799 | -0.010593 | 61.3672 | 61.5354 | 61.4967 | 61.5069 | 61.5305 | 61.5643 | 61.5175 | 61.5752 | 123.1292 | 61.7171 | 123.0422 | 61.4674 | 61.5396 | 123.0896 | 61.4991 | 122.8769 | 61.5896 | 61.6301 | 61.5025 | 61.543
1843.0625 | 123.2574 | -61.5005 | 61.6928 | 0.034862 | -0.008469 | -0.002842 | 0.01619 | 0.054577 | 0.00775 | 0.07005 | 61.6195 | 0.20284 | 61.5553 | -0.042259 | 0.034501 | 61.5936 | -0.010593 | 61.381 | 61.5354 | 61.4921 | 61.4977 | 61.5167 | 61.5551 | 61.5083 | 61.5706 | 123.1201 | 61.7034 | 123.0559 | 61.4583 | 61.535 | 123.0942 | 61.49 | 122.8815 | 61.585 | 61.6301 | 61.5208 | 61.5659
1844.0625 | 123.3124 | -61.4731 | 61.6516 | 0.030283 | -0.00389 | -0.007421 | 0.025347 | 0.049999 | 0.003172 | 0.074628 | 61.6287 | 0.20742 | 61.5645 | -0.042259 | 0.025345 | 61.5845 | -0.006014 | 61.3718 | 61.5034 | 61.4692 | 61.4657 | 61.4984 | 61.5231 | 61.4763 | 61.5477 | 123.1018 | 61.6805 | 123.0376 | 61.4308 | 61.4984 | 123.0576 | 61.4671 | 122.8449 | 61.6033 | 61.6347 | 61.5392 | 61.5705
1845.0625 | 123.3215 | -61.4822 | 61.6699 | 0.030283 | -0.008469 | -0.007421 | 0.020768 | 0.054577 | 0.012329 | 0.065472 | 61.6241 | 0.20742 | 61.5233 | -0.042259 | 0.029923 | 61.5845 | -0.006014 | 61.381 | 61.5125 | 61.4738 | 61.4748 | 61.503 | 61.5368 | 61.4946 | 61.5477 | 123.1063 | 61.6897 | 123.0055 | 61.44 | 61.5122 | 123.0667 | 61.4762 | 122.8632 | 61.5942 | 61.6301 | 61.4934 | 61.5293
1846.0625 | 123.3719 | -61.4639 | 61.6699 | 0.030283 | -0.00389 | -0.007421 | 0.025347 | 0.045421 | 0.012329 | 0.060893 | 61.6149 | 0.20742 | 61.5096 | -0.03768 | 0.034501 | 61.5845 | -0.006014 | 61.3856 | 61.4942 | 61.46 | 61.4565 | 61.4893 | 61.5093 | 61.4763 | 61.5248 | 123.0789 | 61.6714 | 122.9735 | 61.4262 | 61.4984 | 123.0484 | 61.4579 | 122.8495 | 61.5804 | 61.6209 | 61.4751 | 61.5156
1847.0625 | 123.2071 | -61.496 | 61.6516 | 0.034862 | -0.00389 | -0.007421 | 0.025347 | 0.049999 | 0.012329 | 0.07005 | 61.6241 | 0.212 | 61.5462 | -0.03768 | 0.029923 | 61.5799 | -0.001436 | 61.3764 | 61.5308 | 61.4921 | 61.4886 | 61.5213 | 61.546 | 61.5083 | 61.566 | 123.1201 | 61.708 | 123.0422 | 61.4583 | 61.5259 | 123.0759 | 61.4945 | 122.8724 | 61.5942 | 61.6255 | 61.5163 | 61.5476
1848.0625 | 123.436 | -61.4685 | 61.6013 | 0.025705 | -0.00389 | -0.012 | 0.025347 | 0.049999 | 0.00775 | 0.065472 | 61.6195 | 0.21658 | 61.5599 | -0.042259 | 0.029923 | 61.5845 | -0.001436 | 61.381 | 61.4942 | 61.4646 | 61.4565 | 61.4939 | 61.5185 | 61.4763 | 61.534 | 123.088 | 61.6851 | 123.0284 | 61.4262 | 61.4984 | 123.053 | 61.4671 | 122.8495 | 61.5896 | 61.6209 | 61.53 | 61.5614
1849.0625 | 123.3307 | -61.4777 | 61.6882 | 0.034862 | 0.005267 | -0.002842 | 0.029925 | 0.054577 | 0.012329 | 0.07005 | 61.6241 | 0.20742 | 61.5599 | -0.046838 | 0.029923 | 61.5799 | -0.001436 | 61.381 | 61.5125 | 61.4829 | 61.4748 | 61.5076 | 61.5322 | 61.49 | 61.5477 | 123.1018 | 61.6851 | 123.0376 | 61.4308 | 61.5076 | 123.0576 | 61.4762 | 122.8586 | 61.5942 | 61.6255 | 61.53 | 61.5614
1850.0625 | 123.4085 | -61.4639 | 61.6104 | 0.034862 | 0.000689 | -0.007421 | 0.020768 | 0.049999 | 0.00775 | 0.065472 | 61.6195 | 0.20742 | 61.5553 | -0.033101 | 0.029923 | 61.5799 | -0.010593 | 61.381 | 61.4988 | 61.4646 | 61.4565 | 61.4847 | 61.5139 | 61.4717 | 61.5294 | 123.0834 | 61.6714 | 123.0193 | 61.4308 | 61.4939 | 123.0438 | 61.4533 | 122.8449 | 61.5896 | 61.6301 | 61.5254 | 61.5659
1851.0625 | 123.381 | -61.4548 | 61.6425 | 0.030283 | 0.000689 | -0.007421 | 0.020768 | 0.049999 | 0.012329 | 0.074628 | 61.6241 | 0.22116 | 61.5324 | -0.03768 | 0.034501 | 61.5799 | -0.006014 | 61.381 | 61.4851 | 61.4555 | 61.4474 | 61.4755 | 61.5048 | 61.4671 | 61.5294 | 123.0789 | 61.6759 | 122.9872 | 61.4171 | 61.4893 | 123.0347 | 61.4488 | 122.8357 | 61.5896 | 61.6301 | 61.4979 | 61.5385
1852.0625 | 123.3078 | -61.4777 | 61.6699 | 0.03944 | -0.008469 | -0.002842 | 0.020768 | 0.063733 | 0.012329 | 0.065472 | 61.6287 | 0.21658 | 61.5187 | -0.042259 | 0.034501 | 61.5845 | -0.001436 | 61.3764 | 61.5171 | 61.4692 | 61.4748 | 61.4984 | 61.5414 | 61.49 | 61.5431 | 123.1063 | 61.6942 | 122.9964 | 61.4354 | 61.5122 | 123.0621 | 61.4762 | 122.8541 | 61.5942 | 61.6301 | 61.4842 | 61.5202
1853.0625 | 123.4222 | -61.4731 | 61.6333 | 0.025705 | -0.008469 | -0.012 | 0.020768 | 0.049999 | 0.00775 | 0.07005 | 61.6149 | 0.20742 | 61.5141 | -0.046838 | 0.029923 | 61.5936 | -0.006014 | 61.3764 | 61.4988 | 61.4646 | 61.4611 | 61.4939 | 61.5231 | 61.4808 | 61.5431 | 123.088 | 61.6805 | 122.9872 | 61.4262 | 61.503 | 123.0667 | 61.4671 | 122.8495 | 61.585 | 61.6209 | 61.4842 | 61.5202
1854.0625 | 123.2758 | -61.4731 | 61.6837 | 0.030283 | 0.000689 | -0.002842 | 0.025347 | 0.059155 | -0.001406 | 0.07005 | 61.6195 | 0.20742 | 61.5187 | -0.046838 | 0.034501 | 61.5753 | 0.003143 | 61.3718 | 61.5034 | 61.4738 | 61.4702 | 61.4984 | 61.5322 | 61.4717 | 61.5431 | 123.0926 | 61.6805 | 122.9918 | 61.4262 | 61.5076 | 123.0484 | 61.4762 | 122.8449 | 61.585 | 61.6164 | 61.4842 | 61.5156
1855.0625 | 123.3353 | -61.4777 | 61.6379 | 0.034862 | -0.00389 | -0.012 | 0.029925 | 0.049999 | 0.012329 | 0.060893 | 61.6195 | 0.212 | 61.537 | -0.042259 | 0.029923 | 61.5845 | -0.001436 | 61.381 | 61.5125 | 61.4738 | 61.4657 | 61.5076 | 61.5277 | 61.49 | 61.5386 | 123.0972 | 61.6897 | 123.0147 | 61.4354 | 61.5076 | 123.0621 | 61.4762 | 122.8586 | 61.5896 | 61.6209 | 61.5071 | 61.5385
1856.0625 | 123.381 | -61.4777 | 61.6104 | 0.030283 | -0.013048 | -0.012 | 0.020768 | 0.049999 | 0.012329 | 0.060893 | 61.6241 | 0.20742 | 61.5553 | -0.042259 | 0.029923 | 61.5799 | 0.003143 | 61.3581 | 61.5079 | 61.4646 | 61.4657 | 61.4984 | 61.5277 | 61.49 | 61.5386 | 123.1018 | 61.6851 | 123.033 | 61.4354 | 61.5076 | 123.0576 | 61.4808 | 122.8357 | 61.5942 | 61.6209 | 61.5254 | 61.5522
1857.0625 | 123.2529 | -61.4685 | 61.6425 | 0.034862 | 0.005267 | -0.012 | 0.029925 | 0.049999 | 0.00775 | 0.07005 | 61.6241 | 0.212 | 61.5553 | -0.042259 | 0.029923 | 61.5799 | -0.001436 | 61.3627 | 61.5034 | 61.4738 | 61.4565 | 61.4984 | 61.5185 | 61.4763 | 61.5386 | 123.0926 | 61.6805 | 123.0238 | 61.4262 | 61.4984 | 123.0484 | 61.4671 | 122.8312 | 61.5942 | 61.6255 | 61.5254 | 61.5568
1858.0625 | 123.3627 | -61.4777 | 61.6196 | 0.034862 | -0.008469 | -0.007421 | 0.020768 | 0.054577 | 0.012329 | 0.074628 | 61.6195 | 0.21658 | 61.5553 | -0.046838 | 0.029923 | 61.5799 | -0.001436 | 61.3718 | 61.5125 | 61.4692 | 61.4702 | 61.4984 | 61.5322 | 61.49 | 61.5523 | 123.0972 | 61.6942 | 123.033 | 61.4308 | 61.5076 | 123.0576 | 61.4762 | 122.8495 | 61.5896 | 61.6209 | 61.5254 | 61.5568
1859.0625 | 123.2895 | -61.4777 | 61.6333 | 0.03944 | -0.00389 | -0.002842 | 0.029925 | 0.040843 | 0.016907 | 0.056315 | 61.6195 | 0.20742 | 61.5553 | -0.042259 | 0.029923 | 61.5845 | -0.006014 | 61.3535 | 61.5171 | 61.4738 | 61.4748 | 61.5076 | 61.5185 | 61.4946 | 61.534 | 123.0972 | 61.6851 | 123.033 | 61.4354 | 61.5076 | 123.0621 | 61.4716 | 122.8312 | 61.5896 | 61.6255 | 61.5254 | 61.5614
1860.0625 | 123.3994 | -61.4548 | 61.6562 | 0.030283 | -0.00389 | -0.007421 | 0.025347 | 0.054577 | 0.003172 | 0.060893 | 61.6149 | 0.20742 | 61.5324 | -0.03768 | 0.025345 | 61.5845 | 0.003143 | 61.3718 | 61.4851 | 61.4509 | 61.4474 | 61.4801 | 61.5094 | 61.4579 | 61.5157 | 123.0697 | 61.6622 | 122.9872 | 61.4171 | 61.4801 | 123.0392 | 61.4579 | 122.8266 | 61.5896 | 61.6118 | 61.5071 | 61.5293
1861.0625 | 123.3994 | -61.441 | 61.6104 | 0.034862 | 0.000689 | -0.007421 | 0.020768 | 0.054577 | 0.00775 | 0.065472 | 61.6149 | 0.212 | 61.5187 | -0.03768 | 0.025345 | 61.5845 | -0.001436 | 61.3718 | 61.4759 | 61.4417 | 61.4336 | 61.4618 | 61.4956 | 61.4488 | 61.5065 | 123.056 | 61.653 | 122.9598 | 61.4034 | 61.4664 | 123.0255 | 61.4396 | 122.8129 | 61.5896 | 61.6164 | 61.4934 | 61.5202
1862.0781 | 123.381 | -61.4914 | 61.6058 | 0.034862 | -0.00389 | -0.002842 | 0.025347 | 0.054577 | 0.00775 | 0.060893 | 61.6149 | 0.20742 | 61.5096 | -0.042259 | 0.029923 | 61.5845 | -0.010593 | 61.3672 | 61.5263 | 61.4875 | 61.4886 | 61.5167 | 61.546 | 61.4991 | 61.5523 | 123.1063 | 61.6988 | 123.001 | 61.4491 | 61.5213 | 123.0759 | 61.4808 | 122.8586 | 61.585 | 61.6255 | 61.4796 | 61.5202
1863.0625 | 123.3582 | -61.4868 | 61.6196 | 0.034862 | -0.008469 | -0.007421 | 0.025347 | 0.045421 | 0.00775 | 0.065472 | 61.6195 | 0.212 | 61.5324 | -0.046838 | 0.034501 | 61.5891 | -0.006014 | 61.3535 | 61.5217 | 61.4783 | 61.4794 | 61.5122 | 61.5322 | 61.4946 | 61.5523 | 123.1063 | 61.6988 | 123.0193 | 61.44 | 61.5213 | 123.0759 | 61.4808 | 122.8403 | 61.585 | 61.6255 | 61.4979 | 61.5385
1864.0625 | 123.3627 | -61.4456 | 61.6608 | 0.034862 | -0.008469 | -0.012 | 0.020768 | 0.049999 | 0.00775 | 0.07005 | 61.6241 | 0.212 | 61.5553 | -0.042259 | 0.029923 | 61.5845 | -0.001436 | 61.3672 | 61.4805 | 61.4371 | 61.4336 | 61.4664 | 61.4956 | 61.4534 | 61.5157 | 123.0697 | 61.6576 | 123.001 | 61.4034 | 61.4755 | 123.0301 | 61.4442 | 122.8129 | 61.5942 | 61.6255 | 61.5254 | 61.5568
1865.0625 | 123.3582 | -61.5189 | 61.6333 | 0.025705 | 0.000689 | -0.007421 | 0.020768 | 0.054577 | 0.003172 | 0.07005 | 61.6287 | 0.21658 | 61.5553 | -0.046838 | 0.029923 | 61.5799 | 0.003143 | 61.3627 | 61.5446 | 61.5195 | 61.5114 | 61.5396 | 61.5734 | 61.522 | 61.5889 | 123.1475 | 61.7354 | 123.0742 | 61.472 | 61.5488 | 123.0988 | 61.522 | 122.8815 | 61.5987 | 61.6255 | 61.5254 | 61.5522
1866.0625 | 123.349 | -61.4639 | 61.6699 | 0.034862 | 0.005267 | -0.007421 | 0.029925 | 0.054577 | 0.00775 | 0.07005 | 61.6287 | 0.212 | 61.5508 | -0.042259 | 0.029923 | 61.5845 | -0.001436 | 61.3856 | 61.4988 | 61.4692 | 61.4565 | 61.4939 | 61.5185 | 61.4717 | 61.534 | 123.0926 | 61.6759 | 123.0147 | 61.4217 | 61.4939 | 123.0484 | 61.4625 | 122.8495 | 61.5987 | 61.6301 | 61.5208 | 61.5522
1867.0781 | 123.349 | -61.4822 | 61.6058 | 0.034862 | -0.008469 | -0.007421 | 0.020768 | 0.054577 | 0.012329 | 0.060893 | 61.6195 | 0.21658 | 61.5553 | -0.046838 | 0.039079 | 61.5891 | -0.001436 | 61.3718 | 61.5171 | 61.4738 | 61.4748 | 61.503 | 61.5368 | 61.4946 | 61.5431 | 123.1018 | 61.6988 | 123.0376 | 61.4354 | 61.5213 | 123.0713 | 61.4808 | 122.8541 | 61.5804 | 61.6209 | 61.5163 | 61.5568
1868.0625 | 123.2162 | -61.4822 | 61.7294 | 0.03944 | 0.005267 | -0.007421 | 0.029925 | 0.045421 | 0.00775 | 0.07005 | 61.6241 | 0.22116 | 61.5416 | -0.042259 | 0.029923 | 61.5845 | -0.006014 | 61.3764 | 61.5217 | 61.4875 | 61.4748 | 61.5122 | 61.5277 | 61.49 | 61.5523 | 123.1063 | 61.7034 | 123.0238 | 61.44 | 61.5122 | 123.0667 | 61.4762 | 122.8586 | 61.5942 | 61.6301 | 61.5117 | 61.5476
1869.0625 | 123.3215 | -61.4639 | 61.6608 | 0.034862 | -0.00389 | -0.012 | 0.020768 | 0.045421 | 0.003172 | 0.065472 | 61.6149 | 0.212 | 61.5233 | -0.042259 | 0.029923 | 61.5891 | -0.001436 | 61.3672 | 61.4988 | 61.46 | 61.4519 | 61.4847 | 61.5093 | 61.4671 | 61.5294 | 123.0789 | 61.6759 | 122.9872 | 61.4217 | 61.4939 | 123.053 | 61.4625 | 122.8312 | 61.585 | 61.6164 | 61.4934 | 61.5247
1870.0625 | 123.4268 | -61.4639 | 61.6241 | 0.025705 | -0.00389 | -0.012 | 0.020768 | 0.049999 | 0.00775 | 0.060893 | 61.6149 | 0.212 | 61.5141 | -0.03768 | 0.034501 | 61.5799 | -0.001436 | 61.3627 | 61.4896 | 61.46 | 61.4519 | 61.4847 | 61.5139 | 61.4717 | 61.5248 | 123.0789 | 61.6759 | 122.9781 | 61.4262 | 61.4984 | 123.0438 | 61.4625 | 122.8266 | 61.5804 | 61.6164 | 61.4796 | 61.5156
1871.0625 | 123.381 | -61.4456 | 61.6379 | 0.030283 | -0.00389 | -0.007421 | 0.020768 | 0.059155 | 0.00775 | 0.065472 | 61.6241 | 0.20742 | 61.5279 | -0.046838 | 0.029923 | 61.5753 | -0.006014 | 61.3718 | 61.4759 | 61.4417 | 61.4382 | 61.4664 | 61.5048 | 61.4534 | 61.5111 | 123.0697 | 61.653 | 122.9735 | 61.3988 | 61.4755 | 123.0209 | 61.4396 | 122.8174 | 61.5942 | 61.6301 | 61.4979 | 61.5339
1872.0781 | 123.3719 | -61.4685 | 61.6058 | 0.034862 | -0.00389 | -0.002842 | 0.020768 | 0.049999 | 0.003172 | 0.060893 | 61.6149 | 0.212 | 61.5187 | -0.046838 | 0.029923 | 61.5845 | 0.003143 | 61.3764 | 61.5034 | 61.4646 | 61.4657 | 61.4893 | 61.5185 | 61.4717 | 61.5294 | 123.0834 | 61.6805 | 122.9872 | 61.4217 | 61.4984 | 123.053 | 61.4716 | 122.8449 | 61.585 | 61.6118 | 61.4888 | 61.5156
1873.0625 | 123.4039 | -61.4777 | 61.6241 | 0.034862 | 0.000689 | -0.007421 | 0.025347 | 0.054577 | 0.003172 | 0.065472 | 61.6195 | 0.20742 | 61.5553 | -0.042259 | 0.025345 | 61.5799 | -0.006014 | 61.3764 | 61.5125 | 61.4783 | 61.4702 | 61.503 | 61.5322 | 61.4808 | 61.5431 | 123.0972 | 61.6851 | 123.033 | 61.4354 | 61.503 | 123.0576 | 61.4716 | 122.8541 | 61.5942 | 61.6255 | 61.53 | 61.5614
1874.0625 | 123.3124 | -61.5051 | 61.6837 | 0.034862 | 0.009846 | -0.012 | 0.020768 | 0.054577 | 0.016907 | 0.07005 | 61.6287 | 0.212 | 61.5645 | -0.042259 | 0.029923 | 61.5845 | -0.006014 | 61.3764 | 61.54 | 61.515 | 61.4931 | 61.5259 | 61.5597 | 61.522 | 61.5752 | 123.1338 | 61.7171 | 123.0696 | 61.4629 | 61.535 | 123.0896 | 61.4991 | 122.8815 | 61.5987 | 61.6347 | 61.5346 | 61.5705
1875.0625 | 123.3582 | -61.4639 | 61.6196 | 0.030283 | -0.00389 | -0.012 | 0.020768 | 0.059155 | 0.00775 | 0.07005 | 61.6287 | 0.212 | 61.5599 | -0.042259 | 0.020767 | 61.5891 | -0.006014 | 61.3718 | 61.4942 | 61.46 | 61.4519 | 61.4847 | 61.5231 | 61.4717 | 61.534 | 123.0926 | 61.6759 | 123.0238 | 61.4217 | 61.4847 | 123.053 | 61.4579 | 122.8357 | 61.6079 | 61.6347 | 61.5392 | 61.5659
1876.0625 | 123.3536 | -61.4777 | 61.5875 | 0.034862 | 0.000689 | -0.002842 | 0.029925 | 0.054577 | 0.012329 | 0.07005 | 61.6195 | 0.212 | 61.5553 | -0.046838 | 0.029923 | 61.5753 | -0.006014 | 61.381 | 61.5125 | 61.4783 | 61.4748 | 61.5076 | 61.5322 | 61.49 | 61.5477 | 123.0972 | 61.6897 | 123.033 | 61.4308 | 61.5076 | 123.053 | 61.4716 | 122.8586 | 61.5896 | 61.6255 | 61.5254 | 61.5614
1877.0781 | 123.349 | -61.4639 | 61.5875 | 0.034862 | -0.00389 | -0.012 | 0.029925 | 0.059155 | 0.00775 | 0.07005 | 61.6241 | 0.21658 | 61.5508 | -0.042259 | 0.025345 | 61.5753 | -0.001436 | 61.3672 | 61.4988 | 61.46 | 61.4519 | 61.4939 | 61.5231 | 61.4717 | 61.534 | 123.088 | 61.6805 | 123.0147 | 61.4217 | 61.4893 | 123.0392 | 61.4625 | 122.8312 | 61.5987 | 61.6255 | 61.5254 | 61.5522
1878.0625 | 123.3536 | -61.4731 | 61.6241 | 0.030283 | -0.00389 | -0.012 | 0.025347 | 0.049999 | 0.012329 | 0.060893 | 61.6195 | 0.21658 | 61.5233 | -0.046838 | 0.029923 | 61.5845 | -0.001436 | 61.381 | 61.5034 | 61.4692 | 61.4611 | 61.4984 | 61.5231 | 61.4854 | 61.534 | 123.0926 | 61.6897 | 122.9964 | 61.4262 | 61.503 | 123.0576 | 61.4716 | 122.8541 | 61.5896 | 61.6209 | 61.4934 | 61.5247
1879.0625 | 123.3124 | -61.496 | 61.6333 | 0.034862 | 0.000689 | -0.012 | 0.025347 | 0.049999 | 0.00775 | 0.074628 | 61.6149 | 0.21658 | 61.5141 | -0.033101 | 0.039079 | 61.5753 | -0.006014 | 61.3718 | 61.5308 | 61.4967 | 61.484 | 61.5213 | 61.546 | 61.5037 | 61.5706 | 123.1109 | 61.7126 | 123.0101 | 61.4629 | 61.5351 | 123.0713 | 61.49 | 122.8678 | 61.5759 | 61.6209 | 61.4751 | 61.5202
1880.0625 | 123.3719 | -61.4731 | 61.6058 | 0.025705 | -0.013048 | -0.007421 | 0.025347 | 0.049999 | 0.003172 | 0.07005 | 61.6149 | 0.212 | 61.5141 | -0.046838 | 0.029923 | 61.5891 | 0.003143 | 61.381 | 61.4988 | 61.46 | 61.4657 | 61.4984 | 61.5231 | 61.4763 | 61.5431 | 123.088 | 61.6851 | 122.9872 | 61.4262 | 61.503 | 123.0621 | 61.4762 | 122.8541 | 61.585 | 61.6118 | 61.4842 | 61.511
1881.0625 | 123.349 | -61.4731 | 61.5921 | 0.030283 | 0.000689 | -0.002842 | 0.025347 | 0.049999 | 0.00775 | 0.060893 | 61.6195 | 0.21658 | 61.5187 | -0.051417 | 0.029923 | 61.5891 | -0.001436 | 61.3764 | 61.5034 | 61.4738 | 61.4702 | 61.4984 | 61.5231 | 61.4808 | 61.534 | 123.0926 | 61.6897 | 122.9918 | 61.4217 | 61.503 | 123.0621 | 61.4716 | 122.8495 | 61.5896 | 61.6209 | 61.4888 | 61.5202
1882.0781 | 123.3856 | -61.4639 | 61.5967 | 0.030283 | -0.00389 | -0.002842 | 0.025347 | 0.063733 | 0.00775 | 0.07005 | 61.6195 | 0.20742 | 61.5508 | -0.03768 | 0.029923 | 61.5799 | -0.006014 | 61.3764 | 61.4942 | 61.46 | 61.4611 | 61.4893 | 61.5277 | 61.4717 | 61.534 | 123.0834 | 61.6714 | 123.0147 | 61.4262 | 61.4939 | 123.0438 | 61.4579 | 122.8403 | 61.5896 | 61.6255 | 61.5208 | 61.5568
1883.0625 | 123.349 | -61.4868 | 61.6241 | 0.030283 | 0.005267 | -0.007421 | 0.025347 | 0.063733 | 0.00775 | 0.065472 | 61.6195 | 0.212 | 61.5645 | -0.046838 | 0.039079 | 61.5799 | -0.006014 | 61.3764 | 61.5171 | 61.4921 | 61.4794 | 61.5122 | 61.5505 | 61.4946 | 61.5523 | 123.1063 | 61.6988 | 123.0513 | 61.44 | 61.5259 | 123.0667 | 61.4808 | 122.8632 | 61.5804 | 61.6255 | 61.5254 | 61.5705
1884.0625 | 123.3032 | -61.4822 | 61.6379 | 0.044018 | 0.009846 | 0.001736 | 0.029925 | 0.054577 | 0.012329 | 0.074628 | 61.6195 | 0.212 | 61.5553 | -0.042259 | 0.025345 | 61.5799 | -0.006014 | 61.381 | 61.5263 | 61.4921 | 61.484 | 61.5122 | 61.5368 | 61.4946 | 61.5569 | 123.1018 | 61.6942 | 123.0376 | 61.44 | 61.5076 | 123.0621 | 61.4762 | 122.8632 | 61.5942 | 61.6255 | 61.53 | 61.5614
1885.0625 | 123.4314 | -61.4502 | 61.647 | 0.030283 | -0.00389 | -0.007421 | 0.020768 | 0.049999 | 0.012329 | 0.07005 | 61.6241 | 0.212 | 61.5599 | -0.042259 | 0.034501 | 61.5891 | -0.006014 | 61.3764 | 61.4805 | 61.4463 | 61.4428 | 61.471 | 61.5002 | 61.4625 | 61.5202 | 123.0743 | 61.6622 | 123.0101 | 61.4079 | 61.4847 | 123.0392 | 61.4442 | 122.8266 | 61.5896 | 61.6301 | 61.5254 | 61.5659
1886.0625 | 123.3536 | -61.4639 | 61.6241 | 0.030283 | 0.000689 | -0.012 | 0.029925 | 0.054577 | 0.012329 | 0.065472 | 61.6195 | 0.21658 | 61.5508 | -0.03768 | 0.029923 | 61.5845 | -0.001436 | 61.3856 | 61.4942 | 61.4646 | 61.4519 | 61.4939 | 61.5185 | 61.4763 | 61.5294 | 123.0834 | 61.6805 | 123.0147 | 61.4262 | 61.4939 | 123.0484 | 61.4625 | 122.8495 | 61.5896 | 61.6209 | 61.5208 | 61.5522
1887.0625 | 123.3536 | -61.4731 | 61.5967 | 0.030283 | 0.000689 | -0.002842 | 0.029925 | 0.054577 | 0.012329 | 0.07005 | 61.6241 | 0.212 | 61.5141 | -0.042259 | 0.025345 | 61.5845 | -0.006014 | 61.3627 | 61.5034 | 61.4738 | 61.4702 | 61.503 | 61.5277 | 61.4854 | 61.5431 | 123.0972 | 61.6851 | 122.9872 | 61.4308 | 61.4984 | 123.0576 | 61.4671 | 122.8357 | 61.5987 | 61.6301 | 61.4888 | 61.5202
1888.0625 | 123.2666 | -61.4685 | 61.6837 | 0.030283 | 0.005267 | -0.002842 | 0.020768 | 0.063733 | 0.016907 | 0.065472 | 61.6195 | 0.212 | 61.5141 | -0.042259 | 0.029923 | 61.5845 | -0.001436 | 61.3718 | 61.4988 | 61.4738 | 61.4657 | 61.4893 | 61.5322 | 61.4854 | 61.534 | 123.088 | 61.6805 | 122.9826 | 61.4262 | 61.4984 | 123.053 | 61.4671 | 122.8403 | 61.5896 | 61.6209 | 61.4842 | 61.5156
1889.0625 | 123.3398 | -61.4685 | 61.6516 | 0.034862 | 0.000689 | -0.007421 | 0.029925 | 0.054577 | 0.012329 | 0.07005 | 61.6195 | 0.20742 | 61.5141 | -0.03768 | 0.029923 | 61.5891 | -0.001436 | 61.381 | 61.5034 | 61.4692 | 61.4611 | 61.4984 | 61.5231 | 61.4808 | 61.5386 | 123.088 | 61.6759 | 122.9826 | 61.4308 | 61.4984 | 123.0576 | 61.4671 | 122.8495 | 61.5896 | 61.6209 | 61.4842 | 61.5156
1890.0625 | 123.4131 | -61.4731 | 61.6013 | 0.030283 | 0.009846 | -0.002842 | 0.025347 | 0.049999 | 0.00775 | 0.065472 | 61.6195 | 0.21658 | 61.5233 | -0.03768 | 0.025345 | 61.5845 | -0.006014 | 61.3718 | 61.5034 | 61.4829 | 61.4702 | 61.4984 | 61.5231 | 61.4808 | 61.5386 | 123.0926 | 61.6897 | 122.9964 | 61.4354 | 61.4984 | 123.0576 | 61.4671 | 122.8449 | 61.5942 | 61.6255 | 61.4979 | 61.5293
1891.0625 | 123.3902 | -61.4685 | 61.6379 | 0.03944 | -0.00389 | -0.002842 | 0.025347 | 0.054577 | 0.012329 | 0.07005 | 61.6241 | 0.20742 | 61.5462 | -0.042259 | 0.029923 | 61.5845 | -0.006014 | 61.3856 | 61.5079 | 61.4646 | 61.4657 | 61.4939 | 61.5231 | 61.4808 | 61.5386 | 123.0926 | 61.6759 | 123.0147 | 61.4262 | 61.4984 | 123.053 | 61.4625 | 122.8541 | 61.5942 | 61.6301 | 61.5163 | 61.5522
1892.0625 | 123.3307 | -61.4685 | 61.6104 | 0.034862 | -0.008469 | -0.012 | 0.029925 | 0.054577 | 0.00775 | 0.074628 | 61.6287 | 0.212 | 61.5599 | -0.033101 | 0.034501 | 61.5936 | -0.010593 | 61.3718 | 61.5034 | 61.46 | 61.4565 | 61.4984 | 61.5231 | 61.4763 | 61.5431 | 123.0972 | 61.6805 | 123.0284 | 61.4354 | 61.503 | 123.0621 | 61.4579 | 122.8403 | 61.5942 | 61.6393 | 61.5254 | 61.5705
1893.0625 | 123.3582 | -61.4868 | 61.615 | 0.03944 | 0.005267 | -0.002842 | 0.025347 | 0.059155 | 0.012329 | 0.079206 | 61.6241 | 0.20742 | 61.5599 | -0.042259 | 0.020767 | 61.5891 | -0.001436 | 61.381 | 61.5263 | 61.4921 | 61.484 | 61.5122 | 61.546 | 61.4991 | 61.566 | 123.1109 | 61.6942 | 123.0467 | 61.4446 | 61.5076 | 123.0759 | 61.4854 | 122.8678 | 61.6033 | 61.6255 | 61.5392 | 61.5614
1894.0781 | 123.262 | -61.528 | 61.6104 | 0.030283 | 0.000689 | -0.012 | 0.025347 | 0.059155 | 0.016907 | 0.079206 | 61.6241 | 0.20742 | 61.5553 | -0.046838 | 0.029923 | 61.5799 | -0.010593 | 61.381 | 61.5583 | 61.5287 | 61.516 | 61.5534 | 61.5872 | 61.5449 | 61.6072 | 123.1521 | 61.7354 | 123.0834 | 61.4812 | 61.5579 | 123.1079 | 61.5174 | 122.909 | 61.5942 | 61.6347 | 61.5254 | 61.5659
1895.0625 | 123.381 | -61.4868 | 61.5784 | 0.034862 | 0.005267 | -0.007421 | 0.020768 | 0.054577 | 0.00775 | 0.07005 | 61.6195 | 0.212 | 61.537 | -0.03768 | 0.025345 | 61.5799 | -0.001436 | 61.381 | 61.5217 | 61.4921 | 61.4794 | 61.5076 | 61.5414 | 61.4946 | 61.5569 | 123.1063 | 61.6988 | 123.0238 | 61.4491 | 61.5122 | 123.0667 | 61.4854 | 122.8678 | 61.5942 | 61.6209 | 61.5117 | 61.5385
1896.0625 | 123.3582 | -61.4822 | 61.615 | 0.030283 | 0.000689 | -0.007421 | 0.025347 | 0.063733 | 0.003172 | 0.079206 | 61.6149 | 0.21658 | 61.5141 | -0.046838 | 0.029923 | 61.5799 | -0.006014 | 61.3672 | 61.5125 | 61.4829 | 61.4748 | 61.5076 | 61.546 | 61.4854 | 61.5614 | 123.0972 | 61.6988 | 122.9964 | 61.4354 | 61.5122 | 123.0621 | 61.4762 | 122.8495 | 61.585 | 61.6209 | 61.4842 | 61.5202
1897.0625 | 123.4039 | -61.4456 | 61.6333 | 0.030283 | 0.000689 | -0.007421 | 0.025347 | 0.049999 | 0.00775 | 0.074628 | 61.6195 | 0.212 | 61.5141 | -0.03768 | 0.034501 | 61.5845 | -0.006014 | 61.3718 | 61.4759 | 61.4463 | 61.4382 | 61.471 | 61.4956 | 61.4534 | 61.5202 | 123.0651 | 61.6576 | 122.9598 | 61.4079 | 61.4801 | 123.0301 | 61.4396 | 122.8174 | 61.585 | 61.6255 | 61.4796 | 61.5202
1898.0625 | 123.2803 | -61.5234 | 61.6287 | 0.025705 | 0.005267 | 0.001736 | 0.025347 | 0.049999 | 0.012329 | 0.065472 | 61.6195 | 0.20742 | 61.5279 | -0.03768 | 0.029923 | 61.5845 | 0.003143 | 61.3764 | 61.5491 | 61.5287 | 61.5252 | 61.5488 | 61.5734 | 61.5358 | 61.5889 | 123.1429 | 61.7309 | 123.0513 | 61.4858 | 61.5534 | 123.1079 | 61.5266 | 122.8998 | 61.5896 | 61.6164 | 61.4979 | 61.5247
1899.0625 | 123.317 | -61.4868 | 61.6333 | 0.030283 | 0.000689 | -0.012 | 0.034504 | 0.054577 | 0.012329 | 0.065472 | 61.6241 | 0.20742 | 61.5416 | -0.03768 | 0.029923 | 61.5845 | -0.006014 | 61.3718 | 61.5171 | 61.4875 | 61.4748 | 61.5213 | 61.5414 | 61.4991 | 61.5523 | 123.1109 | 61.6942 | 123.0284 | 61.4491 | 61.5167 | 123.0713 | 61.4808 | 122.8586 | 61.5942 | 61.6301 | 61.5117 | 61.5476
1900.0625 | 123.262 | -61.4868 | 61.6608 | 0.025705 | -0.00389 | -0.007421 | 0.029925 | 0.059155 | 0.012329 | 0.074628 | 61.6195 | 0.21658 | 61.5599 | -0.03768 | 0.029923 | 61.5753 | -0.001436 | 61.381 | 61.5125 | 61.4829 | 61.4794 | 61.5167 | 61.546 | 61.4991 | 61.5614 | 123.1063 | 61.7034 | 123.0467 | 61.4491 | 61.5167 | 123.0621 | 61.4854 | 122.8678 | 61.5896 | 61.6209 | 61.53 | 61.5614
1901.0625 | 123.175 | -61.528 | 61.5921 | 0.03944 | 0.000689 | -0.002842 | 0.029925 | 0.059155 | 0.012329 | 0.065472 | 61.6332 | 0.21658 | 61.5553 | -0.033101 | 0.029923 | 61.5799 | -0.010593 | 61.381 | 61.5675 | 61.5287 | 61.5252 | 61.5579 | 61.5872 | 61.5403 | 61.5935 | 123.1613 | 61.7446 | 123.0834 | 61.4949 | 61.5579 | 123.1079 | 61.5174 | 122.909 | 61.6033 | 61.6438 | 61.5254 | 61.5659
1902.0625 | 123.3582 | -61.4685 | 61.5875 | 0.034862 | -0.008469 | -0.007421 | 0.020768 | 0.063733 | 0.016907 | 0.07005 | 61.6195 | 0.22116 | 61.5599 | -0.046838 | 0.025345 | 61.5799 | 0.003143 | 61.3764 | 61.5034 | 61.46 | 61.4611 | 61.4893 | 61.5322 | 61.4854 | 61.5386 | 123.088 | 61.6897 | 123.0284 | 61.4217 | 61.4939 | 123.0484 | 61.4716 | 122.8449 | 61.5942 | 61.6164 | 61.5346 | 61.5568
1903.0625 | 123.4131 | -61.4639 | 61.615 | 0.044018 | -0.00389 | -0.012 | 0.025347 | 0.054577 | 0.00775 | 0.07005 | 61.6195 | 0.212 | 61.5462 | -0.042259 | 0.029923 | 61.5891 | -0.006014 | 61.3764 | 61.5079 | 61.46 | 61.4519 | 61.4893 | 61.5185 | 61.4717 | 61.534 | 123.0834 | 61.6759 | 123.0101 | 61.4217 | 61.4939 | 123.053 | 61.4579 | 122.8403 | 61.5896 | 61.6255 | 61.5163 | 61.5522
1904.0625 | 123.3902 | -61.4822 | 61.6058 | 0.034862 | 0.000689 | -0.007421 | 0.029925 | 0.054577 | 0.016907 | 0.060893 | 61.6195 | 0.20284 | 61.5324 | -0.03768 | 0.029923 | 61.5845 | -0.006014 | 61.3718 | 61.5171 | 61.4829 | 61.4748 | 61.5122 | 61.5368 | 61.4991 | 61.5431 | 123.1018 | 61.6851 | 123.0147 | 61.4446 | 61.5122 | 123.0667 | 61.4762 | 122.8541 | 61.5896 | 61.6255 | 61.5025 | 61.5385
1905.0625 | 123.2437 | -61.4822 | 61.6791 | 0.030283 | 0.000689 | -0.002842 | 0.025347 | 0.054577 | 0.016907 | 0.065472 | 61.6149 | 0.212 | 61.5141 | -0.033101 | 0.025345 | 61.5753 | 0.003143 | 61.3764 | 61.5125 | 61.4829 | 61.4794 | 61.5076 | 61.5368 | 61.4991 | 61.5477 | 123.0972 | 61.6942 | 122.9964 | 61.4491 | 61.5076 | 123.0576 | 61.4854 | 122.8586 | 61.5896 | 61.6118 | 61.4888 | 61.511
1906.0625 | 123.381 | -61.4594 | 61.6608 | 0.030283 | 0.000689 | -0.007421 | 0.025347 | 0.054577 | 0.012329 | 0.074628 | 61.6149 | 0.212 | 61.5141 | -0.03768 | 0.029923 | 61.5891 | -0.006014 | 61.3856 | 61.4896 | 61.46 | 61.4519 | 61.4847 | 61.5139 | 61.4717 | 61.534 | 123.0743 | 61.6714 | 122.9735 | 61.4217 | 61.4893 | 123.0484 | 61.4533 | 122.8449 | 61.585 | 61.6209 | 61.4842 | 61.5202
1907.0625 | 123.2391 | -61.4914 | 61.647 | 0.03944 | 0.005267 | -0.007421 | 0.029925 | 0.054577 | 0.00775 | 0.07005 | 61.6241 | 0.212 | 61.5279 | -0.042259 | 0.029923 | 61.5845 | -0.010593 | 61.381 | 61.5308 | 61.4967 | 61.484 | 61.5213 | 61.546 | 61.4991 | 61.5614 | 123.1155 | 61.7034 | 123.0193 | 61.4491 | 61.5213 | 123.0759 | 61.4808 | 122.8724 | 61.5942 | 61.6347 | 61.4979 | 61.5385
1908.0625 | 123.2849 | -61.496 | 61.6837 | 0.03944 | 0.009846 | -0.007421 | 0.025347 | 0.059155 | 0.012329 | 0.07005 | 61.6195 | 0.212 | 61.5599 | -0.033101 | 0.029923 | 61.5799 | -0.006014 | 61.3856 | 61.5354 | 61.5058 | 61.4886 | 61.5213 | 61.5551 | 61.5083 | 61.566 | 123.1155 | 61.708 | 123.0559 | 61.4629 | 61.5259 | 123.0759 | 61.49 | 122.8815 | 61.5896 | 61.6255 | 61.53 | 61.5659
1909.0625 | 123.3994 | -61.4639 | 61.6287 | 0.034862 | 0.005267 | -0.012 | 0.025347 | 0.059155 | 0.012329 | 0.060893 | 61.6195 | 0.20742 | 61.5553 | -0.042259 | 0.025345 | 61.5845 | 0.003143 | 61.3764 | 61.4988 | 61.4692 | 61.4519 | 61.4893 | 61.5231 | 61.4763 | 61.5248 | 123.0834 | 61.6714 | 123.0193 | 61.4217 | 61.4893 | 123.0484 | 61.4671 | 122.8403 | 61.5942 | 61.6164 | 61.53 | 61.5522
1910.0625 | 123.2849 | -61.4868 | 61.6837 | 0.030283 | 0.000689 | -0.002842 | 0.029925 | 0.054577 | 0.00775 | 0.074628 | 61.6241 | 0.212 | 61.5233 | -0.051417 | 0.025345 | 61.5845 | -0.010593 | 61.3764 | 61.5171 | 61.4875 | 61.484 | 61.5167 | 61.5414 | 61.4946 | 61.5614 | 123.1109 | 61.6988 | 123.0101 | 61.4354 | 61.5122 | 123.0713 | 61.4762 | 122.8632 | 61.5987 | 61.6347 | 61.4979 | 61.5339
1911.0625 | 123.2483 | -61.4685 | 61.6608 | 0.034862 | 0.005267 | -0.007421 | 0.025347 | 0.054577 | 0.00775 | 0.074628 | 61.6241 | 0.21658 | 61.5187 | -0.03768 | 0.029923 | 61.5753 | -0.006014 | 61.3764 | 61.5034 | 61.4738 | 61.4611 | 61.4939 | 61.5231 | 61.4763 | 61.5431 | 123.0926 | 61.6851 | 122.9872 | 61.4308 | 61.4984 | 123.0438 | 61.4625 | 122.8449 | 61.5942 | 61.6301 | 61.4888 | 61.5247
1912.0625 | 123.317 | -61.4594 | 61.615 | 0.034862 | 0.005267 | -0.016578 | 0.029925 | 0.049999 | 0.00775 | 0.060893 | 61.6195 | 0.212 | 61.5462 | -0.046838 | 0.029923 | 61.5753 | -0.001436 | 61.381 | 61.4942 | 61.4646 | 61.4428 | 61.4893 | 61.5093 | 61.4671 | 61.5202 | 123.0789 | 61.6714 | 123.0055 | 61.4125 | 61.4893 | 123.0347 | 61.4579 | 122.8403 | 61.5896 | 61.6209 | 61.5163 | 61.5476
1913.0625 | 123.2803 | -61.4822 | 61.6287 | 0.030283 | 0.005267 | -0.012 | 0.025347 | 0.059155 | 0.016907 | 0.079206 | 61.6287 | 0.212 | 61.5645 | -0.03768 | 0.029923 | 61.5891 | -0.006014 | 61.3856 | 61.5125 | 61.4875 | 61.4702 | 61.5076 | 61.5414 | 61.4991 | 61.5614 | 123.1109 | 61.6942 | 123.0467 | 61.4446 | 61.5122 | 123.0713 | 61.4762 | 122.8678 | 61.5987 | 61.6347 | 61.5346 | 61.5705
1914.0625 | 123.2895 | -61.5143 | 61.6333 | 0.034862 | -0.00389 | -0.007421 | 0.029925 | 0.054577 | 0.012329 | 0.07005 | 61.6287 | 0.21658 | 61.5645 | -0.03768 | 0.034501 | 61.5891 | -0.010593 | 61.381 | 61.5491 | 61.5104 | 61.5069 | 61.5442 | 61.5689 | 61.5266 | 61.5843 | 123.143 | 61.7309 | 123.0788 | 61.4766 | 61.5488 | 123.1033 | 61.5037 | 122.8953 | 61.5942 | 61.6393 | 61.53 | 61.5751
1915.0625 | 123.4131 | -61.4731 | 61.615 | 0.034862 | 0.005267 | -0.012 | 0.020768 | 0.063733 | 0.00775 | 0.07005 | 61.6287 | 0.212 | 61.5508 | -0.046838 | 0.025345 | 61.5891 | -0.010593 | 61.3764 | 61.5079 | 61.4784 | 61.4611 | 61.4939 | 61.5368 | 61.4808 | 61.5431 | 123.1018 | 61.6851 | 123.0238 | 61.4262 | 61.4984 | 123.0621 | 61.4625 | 122.8495 | 61.6033 | 61.6393 | 61.5254 | 61.5614
1916.0625 | 123.3673 | -61.4456 | 61.615 | 0.034862 | 0.000689 | -0.007421 | 0.020768 | 0.054577 | 0.012329 | 0.07005 | 61.6149 | 0.21658 | 61.5462 | -0.042259 | 0.034501 | 61.5799 | -0.006014 | 61.3718 | 61.4805 | 61.4463 | 61.4382 | 61.4664 | 61.5002 | 61.4579 | 61.5157 | 123.0606 | 61.6622 | 122.9918 | 61.4034 | 61.4801 | 123.0255 | 61.4396 | 122.8174 | 61.5804 | 61.6209 | 61.5117 | 61.5522
1917.0625 | 123.3078 | -61.4868 | 61.6379 | 0.030283 | 0.005267 | -0.012 | 0.025347 | 0.059155 | 0.012329 | 0.07005 | 61.6241 | 0.20742 | 61.5279 | -0.042259 | 0.029923 | 61.5799 | -0.001436 | 61.3764 | 61.5171 | 61.4921 | 61.4748 | 61.5122 | 61.546 | 61.4991 | 61.5569 | 123.1109 | 61.6942 | 123.0147 | 61.4446 | 61.5167 | 123.0667 | 61.4854 | 122.8632 | 61.5942 | 61.6255 | 61.4979 | 61.5293
1918.0625 | 123.381 | -61.496 | 61.5875 | 0.030283 | 0.005267 | -0.002842 | 0.034504 | 0.059155 | 0.012329 | 0.07005 | 61.6149 | 0.21658 | 61.505 | -0.042259 | 0.025345 | 61.5799 | -0.006014 | 61.3672 | 61.5263 | 61.5012 | 61.4931 | 61.5305 | 61.5551 | 61.5083 | 61.566 | 123.1109 | 61.7126 | 123.001 | 61.4537 | 61.5213 | 123.0759 | 61.49 | 122.8632 | 61.5896 | 61.6209 | 61.4796 | 61.511
1919.0625 | 123.2895 | -61.5097 | 61.6241 | 0.03944 | 0.000689 | 0.006315 | 0.029925 | 0.059155 | 0.012329 | 0.074628 | 61.6149 | 0.212 | 61.5141 | -0.03768 | 0.025345 | 61.5799 | -0.006014 | 61.3764 | 61.5491 | 61.5104 | 61.516 | 61.5396 | 61.5689 | 61.522 | 61.5843 | 123.1246 | 61.7217 | 123.0238 | 61.472 | 61.535 | 123.0896 | 61.5037 | 122.8861 | 61.5896 | 61.6209 | 61.4888 | 61.5202
1920.0625 | 123.4131 | -61.4777 | 61.5875 | 0.034862 | 0.005267 | -0.002842 | 0.029925 | 0.054577 | 0.012329 | 0.074628 | 61.6241 | 0.212 | 61.5233 | -0.046838 | 0.029923 | 61.5891 | -0.006014 | 61.3764 | 61.5125 | 61.4829 | 61.4748 | 61.5076 | 61.5322 | 61.49 | 61.5523 | 123.1018 | 61.6897 | 123.001 | 61.4308 | 61.5076 | 123.0667 | 61.4716 | 122.8541 | 61.5942 | 61.6301 | 61.4934 | 61.5293
1921.0625 | 123.3765 | -61.4502 | 61.5921 | 0.034862 | 0.005267 | -0.007421 | 0.025347 | 0.063733 | 0.003172 | 0.079206 | 61.6195 | 0.21658 | 61.5553 | -0.042259 | 0.029923 | 61.5799 | -0.001436 | 61.3764 | 61.4851 | 61.4555 | 61.4428 | 61.4755 | 61.5139 | 61.4534 | 61.5294 | 123.0697 | 61.6668 | 123.0055 | 61.4079 | 61.4801 | 123.0301 | 61.4488 | 122.8266 | 61.5896 | 61.6209 | 61.5254 | 61.5568
1922.0625 | 123.2437 | -61.5051 | 61.647 | 0.034862 | 0.005267 | -0.002842 | 0.029925 | 0.059155 | 0.016907 | 0.079206 | 61.6241 | 0.21658 | 61.5508 | -0.033101 | 0.025345 | 61.5891 | -0.010593 | 61.381 | 61.54 | 61.5104 | 61.5023 | 61.5351 | 61.5643 | 61.522 | 61.5843 | 123.1292 | 61.7217 | 123.0559 | 61.472 | 61.5305 | 123.0942 | 61.4945 | 122.8861 | 61.5987 | 61.6347 | 61.5254 | 61.5614
1923.0625 | 123.3124 | -61.4868 | 61.6699 | 0.034862 | 0.000689 | -0.007421 | 0.039082 | 0.06831 | 0.012329 | 0.074628 | 61.6287 | 0.20284 | 61.5599 | -0.03768 | 0.034501 | 61.5845 | -0.001436 | 61.3901 | 61.5217 | 61.4875 | 61.4794 | 61.5259 | 61.5551 | 61.4991 | 61.5614 | 123.1155 | 61.6897 | 123.0467 | 61.4491 | 61.5213 | 123.0713 | 61.4854 | 122.8769 | 61.5942 | 61.6301 | 61.5254 | 61.5614
1924.0625 | 123.2712 | -61.4777 | 61.6608 | 0.03944 | 0.000689 | -0.007421 | 0.029925 | 0.059155 | 0.016907 | 0.074628 | 61.6195 | 0.22116 | 61.5645 | -0.046838 | 0.034501 | 61.5845 | -0.006014 | 61.381 | 61.5171 | 61.4783 | 61.4702 | 61.5076 | 61.5368 | 61.4946 | 61.5523 | 123.0972 | 61.6988 | 123.0422 | 61.4308 | 61.5122 | 123.0621 | 61.4716 | 122.8586 | 61.585 | 61.6255 | 61.53 | 61.5705
1925.0625 | 123.2758 | -61.496 | 61.6562 | 0.030283 | 0.005267 | -0.002842 | 0.029925 | 0.059155 | 0.012329 | 0.074628 | 61.6287 | 0.20742 | 61.5416 | -0.042259 | 0.034501 | 61.5799 | -0.006014 | 61.381 | 61.5263 | 61.5012 | 61.4931 | 61.5259 | 61.5551 | 61.5083 | 61.5706 | 123.1246 | 61.7034 | 123.0376 | 61.4537 | 61.5305 | 123.0759 | 61.49 | 122.8769 | 61.5942 | 61.6347 | 61.5071 | 61.5476
1926.0625 | 123.2712 | -61.4777 | 61.6653 | 0.030283 | 0.005267 | -0.002842 | 0.025347 | 0.059155 | 0.012329 | 0.079206 | 61.6149 | 0.20742 | 61.5324 | -0.042259 | 0.029923 | 61.5799 | -0.006014 | 61.381 | 61.5079 | 61.4829 | 61.4748 | 61.503 | 61.5368 | 61.49 | 61.5569 | 123.0926 | 61.6851 | 123.0101 | 61.4354 | 61.5076 | 123.0576 | 61.4716 | 122.8586 | 61.585 | 61.6209 | 61.5025 | 61.5385
1927.0625 | 123.349 | -61.4822 | 61.5921 | 0.03944 | 0.009846 | -0.002842 | 0.025347 | 0.063733 | 0.012329 | 0.074628 | 61.6241 | 0.20284 | 61.5187 | -0.042259 | 0.029923 | 61.5891 | -0.006014 | 61.3718 | 61.5217 | 61.4921 | 61.4794 | 61.5076 | 61.546 | 61.4946 | 61.5569 | 123.1063 | 61.6851 | 123.001 | 61.44 | 61.5122 | 123.0713 | 61.4762 | 122.8541 | 61.5942 | 61.6301 | 61.4888 | 61.5247
1928.0625 | 123.2529 | -61.5097 | 61.647 | 0.034862 | 0.005267 | -0.007421 | 0.025347 | 0.059155 | 0.021485 | 0.079206 | 61.6241 | 0.212 | 61.5141 | -0.046838 | 0.029923 | 61.5845 | -0.001436 | 61.3672 | 61.5446 | 61.515 | 61.5023 | 61.5351 | 61.5689 | 61.5312 | 61.5889 | 123.1338 | 61.7217 | 123.0238 | 61.4629 | 61.5396 | 123.0942 | 61.5083 | 122.8769 | 61.5942 | 61.6255 | 61.4842 | 61.5156
1929.0625 | 123.3902 | -61.441 | 61.615 | 0.03944 | 0.000689 | -0.016578 | 0.025347 | 0.059155 | 0.012329 | 0.074628 | 61.6287 | 0.212 | 61.5187 | -0.051417 | 0.029923 | 61.5799 | -0.001436 | 61.381 | 61.4805 | 61.4417 | 61.4245 | 61.4664 | 61.5002 | 61.4534 | 61.5157 | 123.0697 | 61.653 | 122.9598 | 61.3896 | 61.471 | 123.0209 | 61.4396 | 122.822 | 61.5987 | 61.6301 | 61.4888 | 61.5202
1930.0625 | 123.3261 | -61.4777 | 61.6837 | 0.034862 | -0.00389 | -0.007421 | 0.025347 | 0.059155 | 0.016907 | 0.079206 | 61.6241 | 0.20742 | 61.5279 | -0.042259 | 0.029923 | 61.5845 | -0.010593 | 61.3764 | 61.5125 | 61.4738 | 61.4702 | 61.503 | 61.5368 | 61.4946 | 61.5569 | 123.1018 | 61.6851 | 123.0055 | 61.4354 | 61.5076 | 123.0621 | 61.4671 | 122.8541 | 61.5942 | 61.6347 | 61.4979 | 61.5385
1931.0625 | 123.2986 | -61.4639 | 61.6791 | 0.03944 | 0.000689 | -0.007421 | 0.020768 | 0.059155 | 0.016907 | 0.083784 | 61.6241 | 0.212 | 61.5691 | -0.03768 | 0.034501 | 61.5845 | -0.006014 | 61.3764 | 61.5034 | 61.4646 | 61.4565 | 61.4847 | 61.5231 | 61.4808 | 61.5477 | 123.088 | 61.6759 | 123.033 | 61.4262 | 61.4984 | 123.0484 | 61.4579 | 122.8403 | 61.5896 | 61.6301 | 61.5346 | 61.5751
1932.0625 | 123.3994 | -61.4685 | 61.615 | 0.025705 | 0.000689 | -0.012 | 0.025347 | 0.059155 | 0.012329 | 0.079206 | 61.6241 | 0.212 | 61.5599 | -0.042259 | 0.034501 | 61.5799 | -0.001436 | 61.381 | 61.4942 | 61.4692 | 61.4565 | 61.4939 | 61.5277 | 61.4808 | 61.5477 | 123.0926 | 61.6805 | 123.0284 | 61.4262 | 61.503 | 123.0484 | 61.4671 | 122.8495 | 61.5896 | 61.6255 | 61.5254 | 61.5614
1933.0625 | 123.2941 | -61.5005 | 61.6745 | 0.034862 | -0.00389 | -0.002842 | 0.029925 | 0.054577 | 0.012329 | 0.074628 | 61.6241 | 0.20742 | 61.5599 | -0.042259 | 0.039079 | 61.5891 | -0.006014 | 61.3856 | 61.5354 | 61.4967 | 61.4977 | 61.5305 | 61.5551 | 61.5129 | 61.5752 | 123.1246 | 61.708 | 123.0605 | 61.4583 | 61.5396 | 123.0896 | 61.4945 | 122.8861 | 61.585 | 61.6301 | 61.5208 | 61.5659
1934.0625 | 123.2849 | -61.4594 | 61.647 | 0.030283 | 0.009846 | -0.012 | 0.029925 | 0.059155 | 0.012329 | 0.079206 | 61.6195 | 0.20742 | 61.5645 | -0.042259 | 0.029923 | 61.5799 | -0.001436 | 61.3901 | 61.4896 | 61.4692 | 61.4474 | 61.4893 | 61.5185 | 61.4717 | 61.5386 | 123.0789 | 61.6668 | 123.0238 | 61.4171 | 61.4893 | 123.0392 | 61.4579 | 122.8495 | 61.5896 | 61.6209 | 61.5346 | 61.5659
1935.0625 | 123.2895 | -61.4777 | 61.6791 | 0.025705 | 0.005267 | -0.012 | 0.025347 | 0.059155 | 0.00775 | 0.083784 | 61.6287 | 0.20742 | 61.5462 | -0.042259 | 0.029923 | 61.5845 | -0.006014 | 61.381 | 61.5034 | 61.4829 | 61.4657 | 61.503 | 61.5368 | 61.4854 | 61.5614 | 123.1063 | 61.6851 | 123.0238 | 61.4354 | 61.5076 | 123.0621 | 61.4716 | 122.8586 | 61.5987 | 61.6347 | 61.5163 | 61.5522
1936.0625 | 123.3353 | -61.4594 | 61.6608 | 0.034862 | 0.000689 | -0.007421 | 0.029925 | 0.063733 | 0.012329 | 0.074628 | 61.6287 | 0.21658 | 61.5279 | -0.03768 | 0.039079 | 61.5799 | -0.006014 | 61.3856 | 61.4942 | 61.46 | 61.4519 | 61.4893 | 61.5231 | 61.4717 | 61.534 | 123.088 | 61.6759 | 122.9872 | 61.4217 | 61.4984 | 123.0392 | 61.4533 | 122.8449 | 61.5896 | 61.6347 | 61.4888 | 61.5339
1937.0625 | 123.2712 | -61.5005 | 61.6516 | 0.034862 | 0.005267 | -0.012 | 0.025347 | 0.063733 | 0.012329 | 0.079206 | 61.6241 | 0.22116 | 61.5187 | -0.046838 | 0.029923 | 61.5845 | -0.006014 | 61.3718 | 61.5354 | 61.5058 | 61.4885 | 61.5259 | 61.5643 | 61.5129 | 61.5798 | 123.1246 | 61.7217 | 123.0193 | 61.4537 | 61.5305 | 123.085 | 61.4945 | 122.8724 | 61.5942 | 61.6301 | 61.4888 | 61.5247
1938.0625 | 123.2666 | -61.4731 | 61.6837 | 0.034862 | 0.000689 | -0.002842 | 0.029925 | 0.059155 | 0.012329 | 0.079206 | 61.6241 | 0.212 | 61.5233 | -0.042259 | 0.029923 | 61.5799 | -0.010593 | 61.3718 | 61.5079 | 61.4738 | 61.4702 | 61.503 | 61.5322 | 61.4854 | 61.5523 | 123.0972 | 61.6851 | 122.9964 | 61.4308 | 61.503 | 123.053 | 61.4625 | 122.8449 | 61.5942 | 61.6347 | 61.4934 | 61.5339
1939.0625 | 123.2986 | -61.4502 | 61.6425 | 0.03944 | 0.005267 | -0.002842 | 0.029925 | 0.063733 | 0.003172 | 0.079206 | 61.6241 | 0.212 | 61.5187 | -0.051417 | 0.034501 | 61.5891 | -0.001436 | 61.3718 | 61.4896 | 61.4555 | 61.4474 | 61.4801 | 61.5139 | 61.4534 | 61.5294 | 123.0743 | 61.6622 | 122.9689 | 61.3988 | 61.4847 | 123.0392 | 61.4488 | 122.822 | 61.5896 | 61.6255 | 61.4842 | 61.5202
1940.0625 | 123.2941 | -61.4777 | 61.6699 | 0.034862 | 0.000689 | -0.016578 | 0.029925 | 0.059155 | 0.021485 | 0.074628 | 61.6241 | 0.20742 | 61.537 | -0.042259 | 0.034501 | 61.5799 | -0.001436 | 61.381 | 61.5125 | 61.4783 | 61.4611 | 61.5076 | 61.5368 | 61.4991 | 61.5523 | 123.1018 | 61.6851 | 123.0147 | 61.4354 | 61.5122 | 123.0576 | 61.4762 | 122.8586 | 61.5896 | 61.6255 | 61.5025 | 61.5385
1941.0625 | 123.3719 | -61.4685 | 61.6425 | 0.025705 | 0.000689 | -0.002842 | 0.029925 | 0.059155 | 0.012329 | 0.079206 | 61.6332 | 0.212 | 61.5599 | -0.042259 | 0.034501 | 61.5799 | -0.001436 | 61.381 | 61.4942 | 61.4692 | 61.4657 | 61.4984 | 61.5277 | 61.4808 | 61.5477 | 123.1018 | 61.6805 | 123.0284 | 61.4262 | 61.503 | 123.0484 | 61.4671 | 122.8495 | 61.5987 | 61.6347 | 61.5254 | 61.5614
1942.0625 | 123.4268 | -61.4502 | 61.6516 | 0.030283 | -0.00389 | -0.007421 | 0.029925 | 0.06831 | 0.016907 | 0.083784 | 61.6287 | 0.20742 | 61.5645 | -0.042259 | 0.034501 | 61.5891 | -0.006014 | 61.381 | 61.4805 | 61.4463 | 61.4428 | 61.4801 | 61.5185 | 61.4671 | 61.534 | 123.0789 | 61.6576 | 123.0147 | 61.4079 | 61.4847 | 123.0392 | 61.4442 | 122.8312 | 61.5942 | 61.6347 | 61.53 | 61.5705
1943.0625 | 123.4268 | -61.4502 | 61.6241 | 0.03944 | 0.005267 | -0.007421 | 0.029925 | 0.054577 | 0.012329 | 0.074628 | 61.6241 | 0.21658 | 61.5553 | -0.03768 | 0.029923 | 61.5845 | 0.003143 | 61.3764 | 61.4896 | 61.4555 | 61.4428 | 61.4801 | 61.5048 | 61.4625 | 61.5248 | 123.0743 | 61.6668 | 123.0055 | 61.4125 | 61.4801 | 123.0347 | 61.4533 | 122.8266 | 61.5942 | 61.6209 | 61.5254 | 61.5522
1944.0625 | 123.2986 | -61.4822 | 61.647 | 0.03944 | 0.000689 | -0.012 | 0.029925 | 0.063733 | 0.012329 | 0.074628 | 61.6195 | 0.212 | 61.5599 | -0.03768 | 0.029923 | 61.5845 | -0.010593 | 61.3764 | 61.5217 | 61.4829 | 61.4702 | 61.5122 | 61.546 | 61.4946 | 61.5569 | 123.1018 | 61.6942 | 123.0422 | 61.4446 | 61.5122 | 123.0667 | 61.4716 | 122.8586 | 61.5896 | 61.6301 | 61.53 | 61.5705
1945.0625 | 123.3307 | -61.4685 | 61.615 | 0.034862 | -0.00389 | -0.002842 | 0.029925 | 0.059155 | 0.00775 | 0.07005 | 61.6195 | 0.21658 | 61.5416 | -0.046838 | 0.034501 | 61.5891 | -0.006014 | 61.3718 | 61.5034 | 61.4646 | 61.4657 | 61.4984 | 61.5277 | 61.4763 | 61.5386 | 123.088 | 61.6851 | 123.0101 | 61.4217 | 61.503 | 123.0576 | 61.4625 | 122.8403 | 61.585 | 61.6255 | 61.5071 | 61.5476
1946.0625 | 123.3856 | -61.4639 | 61.6196 | 0.030283 | -0.00389 | -0.007421 | 0.029925 | 0.06831 | 0.012329 | 0.07005 | 61.6241 | 0.21658 | 61.5233 | -0.042259 | 0.029923 | 61.5891 | -0.001436 | 61.381 | 61.4942 | 61.46 | 61.4565 | 61.4939 | 61.5322 | 61.4763 | 61.534 | 123.088 | 61.6805 | 122.9872 | 61.4217 | 61.4939 | 123.053 | 61.4625 | 122.8449 | 61.5942 | 61.6255 | 61.4934 | 61.5247
1947.0625 | 123.2483 | -61.4822 | 61.6837 | 0.044018 | 0.000689 | -0.002842 | 0.029925 | 0.06831 | 0.016907 | 0.074628 | 61.6241 | 0.21658 | 61.5141 | -0.042259 | 0.039079 | 61.5891 | 0.007721 | 61.3718 | 61.5263 | 61.4829 | 61.4794 | 61.5122 | 61.5505 | 61.4991 | 61.5569 | 123.1063 | 61.6988 | 122.9964 | 61.44 | 61.5213 | 123.0713 | 61.49 | 122.8541 | 61.585 | 61.6164 | 61.4751 | 61.5064
1948.0625 | 123.3444 | -61.4639 | 61.6516 | 0.025705 | 0.000689 | -0.016578 | 0.029925 | 0.063733 | 0.012329 | 0.07005 | 61.6195 | 0.21658 | 61.5187 | -0.042259 | 0.029923 | 61.5845 | -0.001436 | 61.3764 | 61.4896 | 61.4646 | 61.4474 | 61.4939 | 61.5277 | 61.4763 | 61.534 | 123.0834 | 61.6805 | 122.9826 | 61.4217 | 61.4939 | 123.0484 | 61.4625 | 122.8403 | 61.5896 | 61.6209 | 61.4888 | 61.5202
1949.0625 | 123.3444 | -61.4685 | 61.6562 | 0.034862 | 0.000689 | -0.007421 | 0.029925 | 0.063733 | 0.016907 | 0.083784 | 61.6241 | 0.22116 | 61.5279 | -0.042259 | 0.039079 | 61.5845 | -0.006014 | 61.3764 | 61.5034 | 61.4692 | 61.4611 | 61.4984 | 61.5322 | 61.4854 | 61.5523 | 123.0926 | 61.6897 | 122.9964 | 61.4262 | 61.5076 | 123.053 | 61.4625 | 122.8449 | 61.585 | 61.6301 | 61.4888 | 61.5339
1950.0625 | 123.3719 | -61.4822 | 61.6241 | 0.03944 | 0.000689 | -0.002842 | 0.029925 | 0.054577 | 0.016907 | 0.07005 | 61.6195 | 0.21658 | 61.5462 | -0.042259 | 0.034501 | 61.5799 | -0.006014 | 61.3764 | 61.5217 | 61.4829 | 61.4794 | 61.5122 | 61.5368 | 61.4991 | 61.5523 | 123.1018 | 61.6988 | 123.0284 | 61.44 | 61.5167 | 123.0621 | 61.4762 | 122.8586 | 61.585 | 61.6255 | 61.5117 | 61.5522
1951.0625 | 123.3398 | -61.4914 | 61.6196 | 0.034862 | 0.000689 | -0.007421 | 0.029925 | 0.063733 | 0.016907 | 0.079206 | 61.6195 | 0.20742 | 61.5553 | -0.042259 | 0.029923 | 61.5891 | -0.010593 | 61.381 | 61.5263 | 61.4921 | 61.484 | 61.5213 | 61.5551 | 61.5083 | 61.5706 | 123.1109 | 61.6988 | 123.0467 | 61.4491 | 61.5213 | 123.0804 | 61.4808 | 122.8724 | 61.5896 | 61.6301 | 61.5254 | 61.5659
1952.0625 | 123.3856 | -61.4639 | 61.6104 | 0.034862 | 0.005267 | -0.016578 | 0.029925 | 0.063733 | 0.016907 | 0.074628 | 61.6332 | 0.21658 | 61.5508 | -0.03768 | 0.029923 | 61.5845 | -0.006014 | 61.381 | 61.4988 | 61.4692 | 61.4474 | 61.4939 | 61.5277 | 61.4808 | 61.5386 | 123.0972 | 61.6805 | 123.0147 | 61.4262 | 61.4939 | 123.0484 | 61.4579 | 122.8449 | 61.6033 | 61.6393 | 61.5208 | 61.5568
1953.0625 | 123.3215 | -61.496 | 61.6013 | 0.030283 | -0.00389 | -0.007421 | 0.034504 | 0.059155 | 0.016907 | 0.079206 | 61.6287 | 0.21658 | 61.5553 | -0.033101 | 0.029923 | 61.5845 | -0.006014 | 61.3718 | 61.5263 | 61.4921 | 61.4886 | 61.5305 | 61.5551 | 61.5129 | 61.5752 | 123.1246 | 61.7126 | 123.0513 | 61.4629 | 61.5259 | 123.0804 | 61.49 | 122.8678 | 61.5987 | 61.6347 | 61.5254 | 61.5614
1954.0625 | 123.3307 | -61.4639 | 61.6562 | 0.034862 | 0.005267 | -0.007421 | 0.029925 | 0.063733 | 0.012329 | 0.079206 | 61.6241 | 0.21658 | 61.5553 | -0.03768 | 0.029923 | 61.5799 | 0.003143 | 61.381 | 61.4988 | 61.4692 | 61.4565 | 61.4939 | 61.5277 | 61.4763 | 61.5431 | 123.088 | 61.6805 | 123.0193 | 61.4262 | 61.4939 | 123.0438 | 61.4671 | 122.8449 | 61.5942 | 61.6209 | 61.5254 | 61.5522
1955.0625 | 123.3948 | -61.4822 | 61.5829 | 0.025705 | 0.009846 | -0.007421 | 0.029925 | 0.049999 | 0.016907 | 0.079206 | 61.6241 | 0.212 | 61.5279 | -0.051417 | 0.034501 | 61.5845 | -0.006014 | 61.3718 | 61.5079 | 61.4921 | 61.4748 | 61.5122 | 61.5322 | 61.4991 | 61.5614 | 123.1063 | 61.6942 | 123.0101 | 61.4308 | 61.5167 | 123.0667 | 61.4762 | 122.8541 | 61.5896 | 61.6301 | 61.4934 | 61.5339
1956.0625 | 123.3627 | -61.4777 | 61.6104 | 0.030283 | 0.005267 | -0.007421 | 0.020768 | 0.054577 | 0.016907 | 0.074628 | 61.6195 | 0.212 | 61.5187 | -0.033101 | 0.039079 | 61.5799 | -0.010593 | 61.3764 | 61.5079 | 61.4829 | 61.4702 | 61.4984 | 61.5322 | 61.4946 | 61.5523 | 123.0972 | 61.6897 | 122.9964 | 61.4446 | 61.5167 | 123.0576 | 61.4671 | 122.8541 | 61.5804 | 61.6301 | 61.4796 | 61.5293
1957.0625 | 123.3994 | -61.4548 | 61.6104 | 0.030283 | 0.000689 | -0.007421 | 0.020768 | 0.063733 | 0.012329 | 0.07005 | 61.6195 | 0.21658 | 61.5096 | -0.042259 | 0.029923 | 61.5845 | -0.006014 | 61.381 | 61.4851 | 61.4555 | 61.4474 | 61.4755 | 61.5185 | 61.4671 | 61.5248 | 123.0743 | 61.6714 | 122.9643 | 61.4125 | 61.4847 | 123.0392 | 61.4488 | 122.8357 | 61.5896 | 61.6255 | 61.4796 | 61.5156
1958.0625 | 123.3582 | -61.496 | 61.6425 | 0.025705 | 0.000689 | -0.012 | 0.034504 | 0.059155 | 0.016907 | 0.083784 | 61.6241 | 0.212 | 61.5187 | -0.03768 | 0.039079 | 61.5845 | -0.001436 | 61.3718 | 61.5217 | 61.4967 | 61.484 | 61.5305 | 61.5551 | 61.5129 | 61.5798 | 123.1201 | 61.708 | 123.0147 | 61.4583 | 61.5351 | 123.0804 | 61.4945 | 122.8678 | 61.585 | 61.6255 | 61.4796 | 61.5202
1959.0625 | 123.3536 | -61.4731 | 61.5555 | 0.025705 | 0.000689 | -0.007421 | 0.025347 | 0.06831 | 0.016907 | 0.074628 | 61.6195 | 0.20742 | 61.5141 | -0.042259 | 0.029923 | 61.5799 | -0.006014 | 61.3764 | 61.4988 | 61.4738 | 61.4657 | 61.4984 | 61.5414 | 61.49 | 61.5477 | 123.0926 | 61.6805 | 122.9872 | 61.4308 | 61.503 | 123.053 | 61.4671 | 122.8495 | 61.5896 | 61.6255 | 61.4842 | 61.5202
1960.0625 | 123.3902 | -61.4456 | 61.5921 | 0.034862 | 0.000689 | -0.012 | 0.039082 | 0.059155 | 0.016907 | 0.083784 | 61.6149 | 0.21658 | 61.5416 | -0.046838 | 0.029923 | 61.5891 | -0.006014 | 61.381 | 61.4805 | 61.4463 | 61.4336 | 61.4847 | 61.5048 | 61.4625 | 61.5294 | 123.0606 | 61.6622 | 122.9872 | 61.3988 | 61.4755 | 123.0347 | 61.4396 | 122.8266 | 61.585 | 61.6209 | 61.5117 | 61.5476
1961.0625 | 123.349 | -61.4868 | 61.6058 | 0.025705 | 0.009846 | -0.002842 | 0.029925 | 0.054577 | 0.021485 | 0.079206 | 61.6195 | 0.212 | 61.5279 | -0.03768 | 0.025345 | 61.5799 | -0.006014 | 61.3764 | 61.5125 | 61.4967 | 61.484 | 61.5167 | 61.5414 | 61.5083 | 61.566 | 123.1063 | 61.6988 | 123.0147 | 61.4491 | 61.5122 | 123.0667 | 61.4808 | 122.8632 | 61.5942 | 61.6255 | 61.5025 | 61.5339
1962.0625 | 123.3582 | -61.4456 | 61.6196 | 0.034862 | 0.009846 | -0.012 | 0.029925 | 0.059155 | 0.00775 | 0.074628 | 61.6241 | 0.212 | 61.5187 | -0.03768 | 0.029923 | 61.5845 | -0.006014 | 61.3718 | 61.4805 | 61.4555 | 61.4336 | 61.4755 | 61.5048 | 61.4534 | 61.5202 | 123.0697 | 61.6576 | 122.9643 | 61.4079 | 61.4755 | 123.0301 | 61.4396 | 122.8174 | 61.5942 | 61.6301 | 61.4888 | 61.5247
1963.0625 | 123.3124 | -61.5051 | 61.6241 | 0.034862 | 0.005267 | -0.002842 | 0.034504 | 0.06831 | 0.016907 | 0.079206 | 61.6195 | 0.22116 | 61.537 | -0.046838 | 0.029923 | 61.5799 | -0.006014 | 61.3764 | 61.54 | 61.5104 | 61.5023 | 61.5396 | 61.5734 | 61.522 | 61.5843 | 123.1246 | 61.7263 | 123.0422 | 61.4583 | 61.535 | 123.085 | 61.4991 | 122.8815 | 61.5896 | 61.6255 | 61.5071 | 61.543
1964.0625 | 123.4085 | -61.4822 | 61.5967 | 0.034862 | 0.005267 | -0.012 | 0.034504 | 0.063733 | 0.016907 | 0.079206 | 61.6241 | 0.21658 | 61.5233 | -0.042259 | 0.034501 | 61.5753 | -0.006014 | 61.381 | 61.5171 | 61.4875 | 61.4702 | 61.5167 | 61.546 | 61.4991 | 61.5614 | 123.1063 | 61.6988 | 123.0055 | 61.44 | 61.5167 | 123.0576 | 61.4762 | 122.8632 | 61.5896 | 61.6301 | 61.4888 | 61.5293
1965.0625 | 123.3307 | -61.4822 | 61.6425 | 0.030283 | 0.005267 | -0.012 | 0.029925 | 0.063733 | 0.00775 | 0.079206 | 61.6287 | 0.21658 | 61.5599 | -0.046838 | 0.034501 | 61.5799 | -0.010593 | 61.3856 | 61.5125 | 61.4875 | 61.4702 | 61.5122 | 61.546 | 61.49 | 61.5614 | 123.1109 | 61.6988 | 123.0422 | 61.4354 | 61.5167 | 123.0621 | 61.4716 | 122.8678 | 61.5942 | 61.6393 | 61.5254 | 61.5705
1966.0625 | 123.23 | -61.5097 | 61.6425 | 0.034862 | 0.005267 | -0.007421 | 0.034504 | 0.063733 | 0.026064 | 0.088362 | 61.6287 | 0.21658 | 61.5508 | -0.042259 | 0.034501 | 61.5845 | -0.006014 | 61.381 | 61.5446 | 61.515 | 61.5023 | 61.5442 | 61.5734 | 61.5358 | 61.5981 | 123.1384 | 61.7263 | 123.0605 | 61.4674 | 61.5442 | 123.0942 | 61.5037 | 122.8907 | 61.5942 | 61.6347 | 61.5163 | 61.5568
1967.0625 | 123.436 | -61.496 | 61.615 | 0.034862 | 0.009846 | -0.007421 | 0.025347 | 0.06831 | 0.016907 | 0.079206 | 61.6332 | 0.21658 | 61.5599 | -0.042259 | 0.034501 | 61.5799 | -0.010593 | 61.3764 | 61.5308 | 61.5058 | 61.4886 | 61.5213 | 61.5643 | 61.5129 | 61.5752 | 123.1292 | 61.7126 | 123.0559 | 61.4537 | 61.5305 | 123.0759 | 61.4854 | 122.8724 | 61.5987 | 61.6438 | 61.5254 | 61.5705
1968.0625 | 123.3902 | -61.4594 | 61.6287 | 0.030283 | 0.000689 | -0.007421 | 0.039082 | 0.06831 | 0.016907 | 0.083784 | 61.6287 | 0.212 | 61.5645 | -0.042259 | 0.039079 | 61.5891 | 0.003143 | 61.3856 | 61.4896 | 61.46 | 61.4519 | 61.4984 | 61.5277 | 61.4763 | 61.5431 | 123.088 | 61.6714 | 123.0238 | 61.4171 | 61.4984 | 123.0484 | 61.4625 | 122.8449 | 61.5896 | 61.6255 | 61.5254 | 61.5614
1969.0625 | 123.2986 | -61.5097 | 61.6196 | 0.034862 | 0.005267 | -0.002842 | 0.029925 | 0.06831 | 0.021485 | 0.079206 | 61.6241 | 0.22116 | 61.5508 | -0.046838 | 0.029923 | 61.5845 | -0.001436 | 61.381 | 61.5446 | 61.515 | 61.5069 | 61.5396 | 61.578 | 61.5312 | 61.5889 | 123.1338 | 61.7309 | 123.0605 | 61.4629 | 61.5396 | 123.0942 | 61.5083 | 122.8907 | 61.5942 | 61.6255 | 61.5208 | 61.5522
1970.0625 | 123.4497 | -61.4548 | 61.6333 | 0.034862 | 0.005267 | -0.007421 | 0.029925 | 0.063733 | 0.021485 | 0.079206 | 61.6195 | 0.212 | 61.5324 | -0.03768 | 0.039079 | 61.5891 | 0.003143 | 61.3856 | 61.4896 | 61.46 | 61.4474 | 61.4847 | 61.5185 | 61.4763 | 61.534 | 123.0743 | 61.6668 | 122.9872 | 61.4171 | 61.4939 | 123.0438 | 61.4579 | 122.8403 | 61.5804 | 61.6164 | 61.4934 | 61.5293
1971.0625 | 123.2895 | -61.5005 | 61.6516 | 0.034862 | 0.009846 | -0.016578 | 0.034504 | 0.06831 | 0.016907 | 0.079206 | 61.6195 | 0.21658 | 61.5187 | -0.03768 | 0.039079 | 61.5891 | -0.010593 | 61.3718 | 61.5354 | 61.5104 | 61.484 | 61.5351 | 61.5689 | 61.5175 | 61.5798 | 123.1201 | 61.7171 | 123.0193 | 61.4629 | 61.5396 | 123.0896 | 61.49 | 122.8724 | 61.5804 | 61.6301 | 61.4796 | 61.5293
1972.0625 | 123.317 | -61.4639 | 61.6516 | 0.034862 | 0.000689 | -0.007421 | 0.025347 | 0.063733 | 0.00775 | 0.074628 | 61.6195 | 0.22116 | 61.5187 | -0.042259 | 0.029923 | 61.5845 | -0.006014 | 61.3718 | 61.4988 | 61.4646 | 61.4565 | 61.4893 | 61.5277 | 61.4717 | 61.5386 | 123.0834 | 61.6851 | 122.9826 | 61.4217 | 61.4939 | 123.0484 | 61.4579 | 122.8357 | 61.5896 | 61.6255 | 61.4888 | 61.5247
1973.0625 | 123.2712 | -61.5005 | 61.6699 | 0.034862 | 0.009846 | -0.007421 | 0.029925 | 0.06831 | 0.021485 | 0.079206 | 61.6241 | 0.212 | 61.5187 | -0.046838 | 0.029923 | 61.5845 | -0.006014 | 61.3764 | 61.5354 | 61.5104 | 61.4931 | 61.5305 | 61.5689 | 61.522 | 61.5798 | 123.1246 | 61.7126 | 123.0193 | 61.4537 | 61.5305 | 123.085 | 61.4945 | 122.8769 | 61.5942 | 61.6301 | 61.4888 | 61.5247
1974.0625 | 123.23 | -61.5143 | 61.6608 | 0.03944 | 0.005267 | -0.002842 | 0.034504 | 0.072888 | 0.016907 | 0.083784 | 61.6195 | 0.212 | 61.5233 | -0.046838 | 0.034501 | 61.5845 | -0.010593 | 61.3764 | 61.5537 | 61.5195 | 61.5114 | 61.5488 | 61.5872 | 61.5312 | 61.5981 | 123.1338 | 61.7263 | 123.0376 | 61.4674 | 61.5488 | 123.0988 | 61.5037 | 122.8907 | 61.585 | 61.6301 | 61.4888 | 61.5339
1975.0625 | 123.3627 | -61.4639 | 61.6379 | 0.034862 | -0.00389 | -0.012 | 0.025347 | 0.063733 | 0.016907 | 0.079206 | 61.6332 | 0.21658 | 61.5462 | -0.042259 | 0.034501 | 61.5936 | -0.006014 | 61.3856 | 61.4988 | 61.46 | 61.4519 | 61.4893 | 61.5277 | 61.4808 | 61.5431 | 123.0972 | 61.6805 | 123.0101 | 61.4217 | 61.4984 | 123.0576 | 61.4579 | 122.8495 | 61.5987 | 61.6393 | 61.5117 | 61.5522
1976.0625 | 123.262 | -61.5189 | 61.6745 | 0.03944 | 0.009846 | -0.007421 | 0.034504 | 0.06831 | 0.021485 | 0.079206 | 61.6287 | 0.21658 | 61.5553 | -0.042259 | 0.025345 | 61.5845 | -0.006014 | 61.381 | 61.5583 | 61.5287 | 61.5114 | 61.5534 | 61.5872 | 61.5403 | 61.5981 | 123.1475 | 61.7354 | 123.0742 | 61.4766 | 61.5442 | 123.1033 | 61.5128 | 122.8998 | 61.6033 | 61.6347 | 61.53 | 61.5614
1977.0625 | 123.2941 | -61.4822 | 61.6287 | 0.034862 | 0.005267 | -0.007421 | 0.034504 | 0.06831 | 0.021485 | 0.079206 | 61.6287 | 0.22116 | 61.5599 | -0.046838 | 0.029923 | 61.5845 | -0.006014 | 61.381 | 61.5171 | 61.4875 | 61.4748 | 61.5167 | 61.5505 | 61.5037 | 61.5614 | 123.1109 | 61.7034 | 123.0422 | 61.4354 | 61.5122 | 123.0667 | 61.4762 | 122.8632 | 61.5987 | 61.6347 | 61.53 | 61.5659
1978.0625 | 123.2666 | -61.5143 | 61.6425 | 0.034862 | 0.005267 | -0.016578 | 0.025347 | 0.072888 | 0.026064 | 0.079206 | 61.6241 | 0.21658 | 61.5599 | -0.03768 | 0.029923 | 61.5891 | 0.003143 | 61.381 | 61.5491 | 61.5195 | 61.4977 | 61.5396 | 61.5872 | 61.5403 | 61.5935 | 123.1384 | 61.7309 | 123.0742 | 61.4766 | 61.5442 | 123.1033 | 61.5174 | 122.8953 | 61.5942 | 61.6209 | 61.53 | 61.5568
1979.0625 | 123.2849 | -61.5005 | 61.6196 | 0.034862 | 0.000689 | -0.007421 | 0.029925 | 0.059155 | 0.021485 | 0.088362 | 61.6241 | 0.22116 | 61.537 | -0.046838 | 0.029923 | 61.5845 | -0.006014 | 61.3856 | 61.5354 | 61.5012 | 61.4931 | 61.5305 | 61.5597 | 61.522 | 61.5889 | 123.1246 | 61.7217 | 123.0376 | 61.4537 | 61.5305 | 123.085 | 61.4945 | 122.8861 | 61.5942 | 61.6301 | 61.5071 | 61.543
1980.0625 | 123.4177 | -61.4639 | 61.6104 | 0.030283 | 0.005267 | -0.012 | 0.029925 | 0.06831 | 0.016907 | 0.083784 | 61.6241 | 0.21658 | 61.5279 | -0.03768 | 0.025345 | 61.5799 | -0.001436 | 61.3856 | 61.4942 | 61.4692 | 61.4519 | 61.4939 | 61.5322 | 61.4808 | 61.5477 | 123.088 | 61.6805 | 122.9918 | 61.4262 | 61.4893 | 123.0438 | 61.4625 | 122.8495 | 61.5987 | 61.6255 | 61.5025 | 61.5293
1981.0625 | 123.2574 | -61.4914 | 61.6425 | 0.030283 | 0.000689 | -0.002842 | 0.029925 | 0.06831 | 0.026064 | 0.088362 | 61.6241 | 0.21658 | 61.5233 | -0.042259 | 0.034501 | 61.5845 | -0.010593 | 61.3764 | 61.5217 | 61.4921 | 61.4886 | 61.5213 | 61.5597 | 61.5175 | 61.5798 | 123.1155 | 61.708 | 123.0147 | 61.4491 | 61.5259 | 123.0759 | 61.4808 | 122.8678 | 61.5896 | 61.6347 | 61.4888 | 61.5339
1982.0625 | 123.2574 | -61.4731 | 61.6791 | 0.044018 | 0.000689 | -0.007421 | 0.034504 | 0.06831 | 0.026064 | 0.083784 | 61.6195 | 0.21658 | 61.5187 | -0.03768 | 0.029923 | 61.5891 | -0.006014 | 61.3764 | 61.5171 | 61.4738 | 61.4657 | 61.5076 | 61.5414 | 61.4991 | 61.5569 | 123.0926 | 61.6897 | 122.9918 | 61.4354 | 61.503 | 123.0621 | 61.4671 | 122.8495 | 61.5896 | 61.6255 | 61.4888 | 61.5247
1983.0625 | 123.2849 | -61.5005 | 61.6699 | 0.030283 | 0.005267 | -0.007421 | 0.029925 | 0.063733 | 0.021485 | 0.083784 | 61.6241 | 0.21658 | 61.5233 | -0.03768 | 0.034501 | 61.5891 | 0.003143 | 61.381 | 61.5308 | 61.5058 | 61.4931 | 61.5305 | 61.5643 | 61.522 | 61.5843 | 123.1246 | 61.7171 | 123.0238 | 61.4629 | 61.535 | 123.0896 | 61.5037 | 122.8815 | 61.5896 | 61.6209 | 61.4888 | 61.5202
1984.0625 | 123.2208 | -61.5051 | 61.6608 | 0.044018 | 0.005267 | -0.002842 | 0.034504 | 0.072888 | 0.016907 | 0.083784 | 61.6195 | 0.20742 | 61.5462 | -0.042259 | 0.029923 | 61.5845 | -0.006014 | 61.3764 | 61.5491 | 61.5104 | 61.5023 | 61.5396 | 61.578 | 61.522 | 61.5889 | 123.1246 | 61.7126 | 123.0513 | 61.4629 | 61.535 | 123.0896 | 61.4991 | 122.8815 | 61.5896 | 61.6255 | 61.5163 | 61.5522
1985.0625 | 123.2849 | -61.4777 | 61.6608 | 0.034862 | 0.009846 | -0.002842 | 0.029925 | 0.063733 | 0.026064 | 0.088362 | 61.6287 | 0.212 | 61.5599 | -0.03768 | 0.034501 | 61.5799 | -0.001436 | 61.3901 | 61.5125 | 61.4875 | 61.4748 | 61.5076 | 61.5414 | 61.5037 | 61.566 | 123.1063 | 61.6897 | 123.0376 | 61.44 | 61.5122 | 123.0576 | 61.4762 | 122.8678 | 61.5942 | 61.6301 | 61.5254 | 61.5614
1986.0625 | 123.2803 | -61.5005 | 61.6379 | 0.034862 | 0.005267 | -0.007421 | 0.034504 | 0.063733 | 0.026064 | 0.079206 | 61.6287 | 0.20742 | 61.5645 | -0.03768 | 0.034501 | 61.5799 | 0.003143 | 61.381 | 61.5354 | 61.5058 | 61.4931 | 61.5351 | 61.5643 | 61.5266 | 61.5798 | 123.1292 | 61.708 | 123.065 | 61.4629 | 61.535 | 123.0804 | 61.5037 | 122.8815 | 61.5942 | 61.6255 | 61.53 | 61.5614
1987.0625 | 123.3032 | -61.496 | 61.647 | 0.034862 | 0.005267 | -0.007421 | 0.029925 | 0.077466 | 0.021485 | 0.088362 | 61.6287 | 0.22116 | 61.5599 | -0.051417 | 0.039079 | 61.5799 | -0.006014 | 61.381 | 61.5308 | 61.5012 | 61.4886 | 61.5259 | 61.5734 | 61.5175 | 61.5843 | 123.1246 | 61.7171 | 123.0559 | 61.4446 | 61.5351 | 123.0759 | 61.49 | 122.8769 | 61.5896 | 61.6347 | 61.5208 | 61.5659
1988.0625 | 123.2712 | -61.4868 | 61.6882 | 0.034862 | 0.005267 | -0.016578 | 0.034504 | 0.06831 | 0.021485 | 0.083784 | 61.6241 | 0.21658 | 61.5508 | -0.03768 | 0.029923 | 61.5799 | 0.003143 | 61.381 | 61.5217 | 61.4921 | 61.4702 | 61.5213 | 61.5551 | 61.5083 | 61.5706 | 123.1109 | 61.7034 | 123.0376 | 61.4491 | 61.5167 | 123.0667 | 61.49 | 122.8678 | 61.5942 | 61.6209 | 61.5208 | 61.5476
1989.0625 | 123.3307 | -61.4822 | 61.6791 | 0.034862 | 0.005267 | -0.007421 | 0.039082 | 0.063733 | 0.026064 | 0.083784 | 61.6195 | 0.20742 | 61.5324 | -0.03768 | 0.025345 | 61.5845 | -0.006014 | 61.381 | 61.5171 | 61.4875 | 61.4748 | 61.5213 | 61.546 | 61.5083 | 61.566 | 123.1018 | 61.6897 | 123.0147 | 61.4446 | 61.5076 | 123.0667 | 61.4762 | 122.8632 | 61.5942 | 61.6255 | 61.5071 | 61.5385
1990.0625 | 123.3353 | -61.4639 | 61.6791 | 0.034862 | 0.000689 | -0.002842 | 0.043661 | 0.06831 | 0.021485 | 0.088362 | 61.6287 | 0.22116 | 61.5233 | -0.042259 | 0.034501 | 61.5799 | 0.003143 | 61.381 | 61.4988 | 61.4646 | 61.4611 | 61.5076 | 61.5322 | 61.4854 | 61.5523 | 123.0926 | 61.6851 | 122.9872 | 61.4217 | 61.4984 | 123.0438 | 61.4671 | 122.8449 | 61.5942 | 61.6255 | 61.4888 | 61.5202
1991.0625 | 123.3444 | -61.4594 | 61.647 | 0.030283 | 0.000689 | -0.016578 | 0.029925 | 0.06831 | 0.016907 | 0.079206 | 61.6195 | 0.21658 | 61.5187 | -0.03768 | 0.039079 | 61.5845 | 0.007721 | 61.3718 | 61.4896 | 61.46 | 61.4428 | 61.4893 | 61.5277 | 61.4763 | 61.5386 | 123.0789 | 61.6759 | 122.9781 | 61.4217 | 61.4984 | 123.0438 | 61.4671 | 122.8312 | 61.5804 | 61.6118 | 61.4796 | 61.511
1992.0625 | 123.3673 | -61.5143 | 61.6608 | 0.030283 | 0.005267 | -0.007421 | 0.029925 | 0.06831 | 0.016907 | 0.083784 | 61.6195 | 0.21658 | 61.5233 | -0.046838 | 0.029923 | 61.5891 | -0.010593 | 61.381 | 61.5446 | 61.5195 | 61.5069 | 61.5442 | 61.5826 | 61.5312 | 61.5981 | 123.1338 | 61.7309 | 123.0376 | 61.4674 | 61.5442 | 123.1033 | 61.5037 | 122.8953 | 61.5896 | 61.6301 | 61.4934 | 61.5339
1993.0625 | 123.3261 | -61.4594 | 61.6425 | 0.030283 | 0.005267 | -0.007421 | 0.029925 | 0.063733 | 0.016907 | 0.079206 | 61.6241 | 0.21658 | 61.537 | -0.03768 | 0.034501 | 61.5891 | -0.010593 | 61.381 | 61.4896 | 61.4646 | 61.4519 | 61.4893 | 61.5231 | 61.4763 | 61.5386 | 123.0834 | 61.6759 | 122.9964 | 61.4217 | 61.4939 | 123.0484 | 61.4488 | 122.8403 | 61.5896 | 61.6347 | 61.5025 | 61.5476
1994.0625 | 123.2574 | -61.496 | 61.6608 | 0.044018 | 0.009846 | -0.012 | 0.043661 | 0.072888 | 0.016907 | 0.083784 | 61.6287 | 0.21658 | 61.5599 | -0.042259 | 0.039079 | 61.5799 | -0.001436 | 61.3764 | 61.54 | 61.5058 | 61.484 | 61.5396 | 61.5689 | 61.5129 | 61.5798 | 123.1246 | 61.7126 | 123.0559 | 61.4537 | 61.5351 | 123.0759 | 61.4945 | 122.8724 | 61.5896 | 61.6301 | 61.5208 | 61.5614
1995.0625 | 123.4131 | -61.4731 | 61.6333 | 0.030283 | 0.005267 | -0.007421 | 0.025347 | 0.06831 | 0.016907 | 0.083784 | 61.6287 | 0.21658 | 61.5645 | -0.042259 | 0.029923 | 61.5891 | -0.001436 | 61.381 | 61.5034 | 61.4784 | 61.4657 | 61.4984 | 61.5414 | 61.49 | 61.5569 | 123.1018 | 61.6897 | 123.0376 | 61.4308 | 61.503 | 123.0621 | 61.4716 | 122.8541 | 61.5987 | 61.6301 | 61.5346 | 61.5659
1996.0625 | 123.3444 | -61.4731 | 61.6608 | 0.030283 | 0.005267 | -0.021157 | 0.029925 | 0.063733 | 0.021485 | 0.074628 | 61.6287 | 0.212 | 61.5553 | -0.03768 | 0.029923 | 61.5845 | -0.001436 | 61.381 | 61.5034 | 61.4784 | 61.4519 | 61.503 | 61.5368 | 61.4946 | 61.5477 | 123.1018 | 61.6851 | 123.0284 | 61.4354 | 61.503 | 123.0576 | 61.4716 | 122.8541 | 61.5987 | 61.6301 | 61.5254 | 61.5568
1997.0625 | 123.317 | -61.4548 | 61.6745 | 0.03944 | 0.005267 | -0.012 | 0.029925 | 0.072888 | 0.021485 | 0.092941 | 61.6241 | 0.21658 | 61.5599 | -0.042259 | 0.034501 | 61.5753 | -0.001436 | 61.381 | 61.4942 | 61.46 | 61.4428 | 61.4847 | 61.5277 | 61.4763 | 61.5477 | 123.0789 | 61.6714 | 123.0147 | 61.4125 | 61.4893 | 123.0301 | 61.4533 | 122.8357 | 61.5896 | 61.6255 | 61.5254 | 61.5614
1998.0625 | 123.2986 | -61.4731 | 61.6745 | 0.034862 | 0.009846 | -0.012 | 0.034504 | 0.063733 | 0.021485 | 0.083784 | 61.6287 | 0.212 | 61.5462 | -0.042259 | 0.029923 | 61.5845 | -0.006014 | 61.3901 | 61.5079 | 61.4829 | 61.4611 | 61.5076 | 61.5368 | 61.4946 | 61.5569 | 123.1018 | 61.6851 | 123.0193 | 61.4308 | 61.503 | 123.0576 | 61.4671 | 122.8632 | 61.5987 | 61.6347 | 61.5163 | 61.5522
1999.0625 | 123.3444 | -61.4594 | 61.6379 | 0.030283 | -0.00389 | -0.012 | 0.034504 | 0.059155 | 0.016907 | 0.083784 | 61.6149 | 0.21658 | 61.5096 | -0.033101 | 0.039079 | 61.5799 | -0.006014 | 61.381 | 61.4896 | 61.4555 | 61.4474 | 61.4939 | 61.5185 | 61.4763 | 61.5431 | 123.0743 | 61.6759 | 122.9689 | 61.4262 | 61.4984 | 123.0392 | 61.4533 | 122.8403 | 61.5759 | 61.6209 | 61.4705 | 61.5156
2000.0625 | 123.4131 | -61.4594 | 61.6425 | 0.030283 | 0.005267 | -0.021157 | 0.034504 | 0.06831 | 0.016907 | 0.079206 | 61.6195 | 0.21658 | 61.5233 | -0.042259 | 0.029923 | 61.5891 | -0.006014 | 61.3764 | 61.4896 | 61.4646 | 61.4382 | 61.4939 | 61.5277 | 61.4763 | 61.5386 | 123.0789 | 61.6759 | 122.9826 | 61.4171 | 61.4893 | 123.0484 | 61.4533 | 122.8357 | 61.5896 | 61.6255 | 61.4934 | 61.5293
2001.0625 | 123.3948 | -61.5005 | 61.6104 | 0.034862 | 0.000689 | -0.012 | 0.025347 | 0.059155 | 0.021485 | 0.083784 | 61.6149 | 0.21658 | 61.5141 | -0.03768 | 0.029923 | 61.5845 | -0.006014 | 61.3718 | 61.5354 | 61.5012 | 61.4885 | 61.5259 | 61.5597 | 61.522 | 61.5843 | 123.1155 | 61.7171 | 123.0147 | 61.4629 | 61.5305 | 123.085 | 61.4945 | 122.8724 | 61.585 | 61.6209 | 61.4842 | 61.5202
2002.0625 | 123.2941 | -61.4914 | 61.6516 | 0.034862 | 0.005267 | -0.007421 | 0.043661 | 0.072888 | 0.021485 | 0.088362 | 61.6241 | 0.22116 | 61.5462 | -0.046838 | 0.039079 | 61.5845 | -0.010593 | 61.3718 | 61.5263 | 61.4967 | 61.484 | 61.5351 | 61.5643 | 61.5129 | 61.5798 | 123.1155 | 61.7126 | 123.0376 | 61.4446 | 61.5305 | 123.0759 | 61.4808 | 122.8632 | 61.585 | 61.6347 | 61.5071 | 61.5568
2003.0625 | 123.349 | -61.4822 | 61.5967 | 0.034862 | 0.005267 | -0.012 | 0.029925 | 0.06831 | 0.026064 | 0.079206 | 61.6241 | 0.21658 | 61.5462 | -0.046838 | 0.039079 | 61.5845 | -0.006014 | 61.381 | 61.5171 | 61.4875 | 61.4702 | 61.5122 | 61.5505 | 61.5083 | 61.5614 | 123.1063 | 61.6988 | 123.0284 | 61.4354 | 61.5213 | 123.0667 | 61.4762 | 122.8632 | 61.585 | 61.6301 | 61.5071 | 61.5522
2004.0625 | 123.3398 | -61.4822 | 61.6196 | 0.044018 | 0.009846 | -0.002842 | 0.034504 | 0.06831 | 0.030642 | 0.088362 | 61.6241 | 0.22116 | 61.5553 | -0.03768 | 0.039079 | 61.5845 | -0.006014 | 61.3856 | 61.5263 | 61.4921 | 61.4794 | 61.5167 | 61.5505 | 61.5129 | 61.5706 | 123.1063 | 61.7034 | 123.0376 | 61.4446 | 61.5213 | 123.0667 | 61.4762 | 122.8678 | 61.585 | 61.6301 | 61.5163 | 61.5614
2005.0625 | 123.3398 | -61.4731 | 61.6608 | 0.034862 | 0.019004 | -0.012 | 0.034504 | 0.06831 | 0.026064 | 0.097519 | 61.6287 | 0.212 | 61.5508 | -0.033101 | 0.025345 | 61.5845 | -0.001436 | 61.381 | 61.5079 | 61.4921 | 61.4611 | 61.5076 | 61.5414 | 61.4991 | 61.5706 | 123.1018 | 61.6851 | 123.0238 | 61.44 | 61.4984 | 123.0576 | 61.4716 | 122.8541 | 61.6033 | 61.6301 | 61.5254 | 61.5522
2006.0625 | 123.468 | -61.4594 | 61.7111 | 0.034862 | 0.005267 | -0.012 | 0.034504 | 0.06831 | 0.021485 | 0.088362 | 61.6287 | 0.212 | 61.5599 | -0.046838 | 0.034501 | 61.5891 | -0.001436 | 61.381 | 61.4942 | 61.4646 | 61.4474 | 61.4939 | 61.5277 | 61.4808 | 61.5477 | 123.088 | 61.6714 | 123.0193 | 61.4125 | 61.4939 | 123.0484 | 61.4579 | 122.8403 | 61.5942 | 61.6301 | 61.5254 | 61.5614
2007.0625 | 123.3902 | -61.4594 | 61.6379 | 0.03944 | 0.005267 | -0.012 | 0.034504 | 0.06831 | 0.016907 | 0.092941 | 61.6241 | 0.20742 | 61.5416 | -0.042259 | 0.034501 | 61.5845 | -0.001436 | 61.3764 | 61.4988 | 61.4646 | 61.4474 | 61.4939 | 61.5277 | 61.4763 | 61.5523 | 123.0834 | 61.6668 | 123.001 | 61.4171 | 61.4939 | 123.0438 | 61.4579 | 122.8357 | 61.5896 | 61.6255 | 61.5071 | 61.543
2008.0625 | 123.3765 | -61.496 | 61.615 | 0.034862 | 0.005267 | -0.012 | 0.034504 | 0.072888 | 0.021485 | 0.083784 | 61.6195 | 0.21658 | 61.5233 | -0.042259 | 0.029923 | 61.5799 | -0.001436 | 61.3718 | 61.5308 | 61.5012 | 61.484 | 61.5305 | 61.5689 | 61.5175 | 61.5798 | 123.1155 | 61.7126 | 123.0193 | 61.4537 | 61.5259 | 123.0759 | 61.4945 | 122.8678 | 61.5896 | 61.6209 | 61.4934 | 61.5247
2009.0625 | 123.3261 | -61.5097 | 61.6196 | 0.034862 | 0.000689 | -0.016578 | 0.034504 | 0.063733 | 0.016907 | 0.079206 | 61.6195 | 0.22116 | 61.5141 | -0.042259 | 0.034501 | 61.5891 | -0.001436 | 61.3672 | 61.5446 | 61.5104 | 61.4931 | 61.5442 | 61.5734 | 61.5266 | 61.5889 | 123.1292 | 61.7309 | 123.0238 | 61.4674 | 61.5442 | 123.0988 | 61.5083 | 122.8769 | 61.585 | 61.6209 | 61.4796 | 61.5156
2010.0625 | 123.3994 | -61.4548 | 61.6287 | 0.030283 | 0.005267 | -0.007421 | 0.034504 | 0.072888 | 0.021485 | 0.079206 | 61.6149 | 0.22116 | 61.5187 | -0.042259 | 0.029923 | 61.5845 | -0.001436 | 61.3764 | 61.4851 | 61.46 | 61.4474 | 61.4893 | 61.5277 | 61.4763 | 61.534 | 123.0697 | 61.6759 | 122.9735 | 61.4125 | 61.4847 | 123.0392 | 61.4533 | 122.8312 | 61.585 | 61.6164 | 61.4888 | 61.5202
2011.0625 | 123.3398 | -61.4548 | 61.6287 | 0.030283 | 0.014425 | 0.001736 | 0.034504 | 0.077466 | 0.016907 | 0.074628 | 61.6149 | 0.21658 | 61.5141 | -0.042259 | 0.029923 | 61.5936 | -0.006014 | 61.3718 | 61.4851 | 61.4692 | 61.4565 | 61.4893 | 61.5322 | 61.4717 | 61.5294 | 123.0697 | 61.6714 | 122.9689 | 61.4125 | 61.4847 | 123.0484 | 61.4488 | 122.8266 | 61.585 | 61.6209 | 61.4842 | 61.5202
2012.0625 | 123.3765 | -61.4456 | 61.6241 | 0.030283 | 0.005267 | -0.012 | 0.029925 | 0.06831 | 0.021485 | 0.088362 | 61.6241 | 0.212 | 61.5462 | -0.046838 | 0.029923 | 61.5845 | -0.006014 | 61.381 | 61.4759 | 61.4509 | 61.4336 | 61.4755 | 61.5139 | 61.4671 | 61.534 | 123.0697 | 61.6576 | 122.9918 | 61.3988 | 61.4755 | 123.0301 | 61.4396 | 122.8266 | 61.5942 | 61.6301 | 61.5163 | 61.5522
2013.0625 | 123.4039 | -61.4731 | 61.5967 | 0.034862 | 0.014425 | -0.012 | 0.029925 | 0.06831 | 0.021485 | 0.088362 | 61.6241 | 0.21658 | 61.5553 | -0.042259 | 0.029923 | 61.5799 | -0.006014 | 61.381 | 61.5079 | 61.4875 | 61.4611 | 61.503 | 61.5414 | 61.4946 | 61.5614 | 123.0972 | 61.6897 | 123.0284 | 61.4308 | 61.503 | 123.053 | 61.4671 | 122.8541 | 61.5942 | 61.6301 | 61.5254 | 61.5614
2014.0625 | 123.3994 | -61.441 | 61.6241 | 0.034862 | 0.014425 | -0.007421 | 0.043661 | 0.06831 | 0.026064 | 0.088362 | 61.6332 | 0.212 | 61.5599 | -0.03768 | 0.034501 | 61.5845 | -0.001436 | 61.381 | 61.4759 | 61.4555 | 61.4336 | 61.4847 | 61.5093 | 61.4671 | 61.5294 | 123.0743 | 61.653 | 123.001 | 61.4034 | 61.4755 | 123.0255 | 61.4396 | 122.822 | 61.5987 | 61.6347 | 61.5254 | 61.5614
2015.0625 | 123.4039 | -61.4685 | 61.615 | 0.034862 | 0.009846 | -0.002842 | 0.029925 | 0.077466 | 0.026064 | 0.083784 | 61.6241 | 0.21658 | 61.5599 | -0.042259 | 0.025345 | 61.5799 | -0.006014 | 61.3856 | 61.5034 | 61.4784 | 61.4657 | 61.4984 | 61.546 | 61.4946 | 61.5523 | 123.0926 | 61.6851 | 123.0284 | 61.4262 | 61.4939 | 123.0484 | 61.4625 | 122.8541 | 61.5987 | 61.6301 | 61.5346 | 61.5659
2016.0625 | 123.3948 | -61.4822 | 61.615 | 0.034862 | 0.005267 | -0.007421 | 0.029925 | 0.072888 | 0.026064 | 0.079206 | 61.6241 | 0.212 | 61.5553 | -0.033101 | 0.034501 | 61.5845 | -0.001436 | 61.3718 | 61.5171 | 61.4875 | 61.4748 | 61.5122 | 61.5551 | 61.5083 | 61.5614 | 123.1063 | 61.6942 | 123.0376 | 61.4491 | 61.5167 | 123.0667 | 61.4808 | 122.8541 | 61.5896 | 61.6255 | 61.5208 | 61.5568
2017.0625 | 123.381 | -61.4685 | 61.615 | 0.034862 | 0.005267 | -0.007421 | 0.039082 | 0.072888 | 0.021485 | 0.088362 | 61.6149 | 0.22116 | 61.5324 | -0.03768 | 0.034501 | 61.5799 | 0.003143 | 61.3856 | 61.5034 | 61.4738 | 61.4611 | 61.5076 | 61.5414 | 61.49 | 61.5569 | 123.0834 | 61.6897 | 123.001 | 61.4308 | 61.503 | 123.0484 | 61.4716 | 122.8541 | 61.5804 | 61.6118 | 61.4979 | 61.5293
2018.0625 | 123.3536 | -61.496 | 61.6196 | 0.034862 | 0.005267 | -0.002842 | 0.039082 | 0.06831 | 0.026064 | 0.088362 | 61.6287 | 0.212 | 61.5187 | -0.042259 | 0.029923 | 61.5845 | -0.001436 | 61.381 | 61.5308 | 61.5012 | 61.4931 | 61.5351 | 61.5643 | 61.522 | 61.5843 | 123.1246 | 61.708 | 123.0147 | 61.4537 | 61.5259 | 123.0804 | 61.4945 | 122.8769 | 61.5987 | 61.6301 | 61.4888 | 61.5202
2019.0625 | 123.3627 | -61.4822 | 61.6608 | 0.030283 | 0.014425 | -0.007421 | 0.039082 | 0.06831 | 0.016907 | 0.088362 | 61.6287 | 0.212 | 61.5141 | -0.042259 | 0.034501 | 61.5845 | -0.001436 | 61.3764 | 61.5125 | 61.4967 | 61.4748 | 61.5213 | 61.5505 | 61.4991 | 61.5706 | 123.1109 | 61.6942 | 122.9964 | 61.44 | 61.5167 | 123.0667 | 61.4808 | 122.8586 | 61.5942 | 61.6301 | 61.4796 | 61.5156
2020.0625 | 123.381 | -61.4822 | 61.5875 | 0.034862 | 0.005267 | -0.002842 | 0.029925 | 0.072888 | 0.016907 | 0.088362 | 61.6149 | 0.21658 | 61.5096 | -0.042259 | 0.034501 | 61.5845 | -0.010593 | 61.3764 | 61.5171 | 61.4875 | 61.4794 | 61.5122 | 61.5551 | 61.4991 | 61.5706 | 123.0972 | 61.6988 | 122.9918 | 61.44 | 61.5167 | 123.0667 | 61.4716 | 122.8586 | 61.5804 | 61.6255 | 61.4751 | 61.5202
2021.0625 | 123.2803 | -61.5097 | 61.6058 | 0.030283 | 0.000689 | -0.007421 | 0.039082 | 0.077466 | 0.021485 | 0.092941 | 61.6241 | 0.22116 | 61.5187 | -0.042259 | 0.025345 | 61.5891 | -0.006014 | 61.3718 | 61.54 | 61.5104 | 61.5023 | 61.5488 | 61.5872 | 61.5312 | 61.6026 | 123.1338 | 61.7309 | 123.0284 | 61.4674 | 61.535 | 123.0988 | 61.5037 | 122.8815 | 61.5987 | 61.6301 | 61.4934 | 61.5247
2022.0625 | 123.4177 | -61.4594 | 61.6287 | 0.030283 | 0.014425 | -0.007421 | 0.034504 | 0.077466 | 0.021485 | 0.092941 | 61.6149 | 0.22574 | 61.5416 | -0.03768 | 0.043657 | 61.5891 | -0.006014 | 61.3856 | 61.4896 | 61.4738 | 61.4519 | 61.4939 | 61.5368 | 61.4808 | 61.5523 | 123.0743 | 61.6851 | 123.001 | 61.4217 | 61.503 | 123.0484 | 61.4533 | 122.8449 | 61.5713 | 61.6209 | 61.4979 | 61.5476
2023.0625 | 123.2941 | -61.5189 | 61.6379 | 0.034862 | 0.009846 | -0.007421 | 0.039082 | 0.06831 | 0.016907 | 0.092941 | 61.6287 | 0.22116 | 61.5599 | -0.042259 | 0.025345 | 61.5799 | -0.006014 | 61.3856 | 61.5537 | 61.5287 | 61.5114 | 61.5579 | 61.5872 | 61.5358 | 61.6118 | 123.1475 | 61.74 | 123.0788 | 61.4766 | 61.5442 | 123.0988 | 61.5128 | 122.9044 | 61.6033 | 61.6347 | 61.5346 | 61.5659
2024.0625 | 123.4314 | -61.4548 | 61.5875 | 0.034862 | 0.014425 | -0.016578 | 0.029925 | 0.072888 | 0.030642 | 0.092941 | 61.6287 | 0.21658 | 61.5645 | -0.042259 | 0.029923 | 61.5845 | -0.006014 | 61.3764 | 61.4896 | 61.4692 | 61.4382 | 61.4847 | 61.5277 | 61.4854 | 61.5477 | 123.0834 | 61.6714 | 123.0193 | 61.4125 | 61.4847 | 123.0392 | 61.4488 | 122.8312 | 61.5987 | 61.6347 | 61.5346 | 61.5705
2025.0625 | 123.2666 | -61.528 | 61.6333 | 0.030283 | 0.019004 | -0.007421 | 0.034504 | 0.077466 | 0.030642 | 0.088362 | 61.6332 | 0.22116 | 61.5645 | -0.03768 | 0.034501 | 61.5753 | -0.006014 | 61.3764 | 61.5583 | 61.547 | 61.5206 | 61.5625 | 61.6055 | 61.5587 | 61.6164 | 123.1613 | 61.7492 | 123.0925 | 61.4903 | 61.5625 | 123.1033 | 61.522 | 122.9044 | 61.5987 | 61.6393 | 61.53 | 61.5705
2026.0625 | 123.3261 | -61.4914 | 61.6104 | 0.03944 | 0.014425 | -0.002842 | 0.034504 | 0.082044 | 0.026064 | 0.092941 | 61.6241 | 0.21658 | 61.5508 | -0.042259 | 0.034501 | 61.5845 | 0.003143 | 61.3718 | 61.5308 | 61.5058 | 61.4886 | 61.5259 | 61.5734 | 61.5175 | 61.5843 | 123.1155 | 61.708 | 123.0422 | 61.4491 | 61.5259 | 123.0759 | 61.4945 | 122.8632 | 61.5896 | 61.6209 | 61.5163 | 61.5476
2027.0625 | 123.3902 | -61.4456 | 61.615 | 0.030283 | 0.005267 | -0.002842 | 0.034504 | 0.072888 | 0.026064 | 0.092941 | 61.6241 | 0.22116 | 61.537 | -0.046838 | 0.034501 | 61.5891 | -0.001436 | 61.3856 | 61.4759 | 61.4509 | 61.4428 | 61.4801 | 61.5185 | 61.4717 | 61.5386 | 123.0697 | 61.6668 | 122.9826 | 61.3988 | 61.4801 | 123.0347 | 61.4442 | 122.8312 | 61.5896 | 61.6255 | 61.5025 | 61.5385
2028.0625 | 123.4222 | -61.4731 | 61.6425 | 0.034862 | 0.009846 | -0.016578 | 0.029925 | 0.077466 | 0.026064 | 0.088362 | 61.6241 | 0.22574 | 61.5187 | -0.03768 | 0.034501 | 61.5845 | -0.001436 | 61.3764 | 61.5079 | 61.4829 | 61.4565 | 61.503 | 61.5505 | 61.4991 | 61.5614 | 123.0972 | 61.6988 | 122.9918 | 61.4354 | 61.5076 | 123.0576 | 61.4716 | 122.8495 | 61.5896 | 61.6255 | 61.4842 | 61.5202
2029.0625 | 123.2666 | -61.5097 | 61.6241 | 0.030283 | 0.014425 | -0.007421 | 0.043661 | 0.077466 | 0.021485 | 0.088362 | 61.6149 | 0.21658 | 61.5187 | -0.046838 | 0.039079 | 61.5845 | -0.006014 | 61.3718 | 61.54 | 61.5241 | 61.5023 | 61.5534 | 61.5872 | 61.5312 | 61.5981 | 123.1246 | 61.7263 | 123.0284 | 61.4629 | 61.5488 | 123.0942 | 61.5037 | 122.8815 | 61.5759 | 61.6209 | 61.4796 | 61.5247
2030.0625 | 123.2712 | -61.5051 | 61.6608 | 0.034862 | 0.005267 | -0.012 | 0.039082 | 0.077466 | 0.030642 | 0.083784 | 61.6287 | 0.21658 | 61.5141 | -0.042259 | 0.029923 | 61.5891 | -0.006014 | 61.3672 | 61.54 | 61.5104 | 61.4931 | 61.5442 | 61.5826 | 61.5358 | 61.5889 | 123.1338 | 61.7217 | 123.0193 | 61.4629 | 61.535 | 123.0942 | 61.4991 | 122.8724 | 61.5987 | 61.6347 | 61.4842 | 61.5202
2031.0625 | 123.262 | -61.5051 | 61.6562 | 0.034862 | 0.009846 | -0.007421 | 0.043661 | 0.077466 | 0.030642 | 0.088362 | 61.6241 | 0.21658 | 61.5279 | -0.046838 | 0.034501 | 61.5845 | -0.006014 | 61.3718 | 61.54 | 61.515 | 61.4977 | 61.5488 | 61.5826 | 61.5358 | 61.5935 | 123.1292 | 61.7217 | 123.033 | 61.4583 | 61.5396 | 123.0896 | 61.4991 | 122.8769 | 61.5896 | 61.6301 | 61.4934 | 61.5339
2032.0625 | 123.317 | -61.4777 | 61.6379 | 0.034862 | 0.023583 | -0.002842 | 0.043661 | 0.082044 | 0.035221 | 0.092941 | 61.6241 | 0.22116 | 61.5645 | -0.03768 | 0.025345 | 61.5845 | -0.006014 | 61.3718 | 61.5125 | 61.5012 | 61.4748 | 61.5213 | 61.5597 | 61.5129 | 61.5706 | 123.1018 | 61.6988 | 123.0422 | 61.44 | 61.503 | 123.0621 | 61.4716 | 122.8495 | 61.5987 | 61.6301 | 61.5392 | 61.5705
2033.0625 | 123.3307 | -61.4777 | 61.6516 | 0.034862 | 0.014425 | -0.007421 | 0.043661 | 0.077466 | 0.035221 | 0.1021 | 61.6332 | 0.21658 | 61.5599 | -0.042259 | 0.034501 | 61.5845 | -0.006014 | 61.3856 | 61.5125 | 61.4921 | 61.4702 | 61.5213 | 61.5551 | 61.5129 | 61.5798 | 123.1109 | 61.6942 | 123.0376 | 61.4354 | 61.5122 | 123.0621 | 61.4716 | 122.8632 | 61.5987 | 61.6393 | 61.5254 | 61.5659
2034.0625 | 123.349 | -61.4731 | 61.5967 | 0.03944 | 0.014425 | -0.012 | 0.039082 | 0.072888 | 0.026064 | 0.097519 | 61.6287 | 0.21658 | 61.5599 | -0.042259 | 0.029923 | 61.5845 | -0.010593 | 61.381 | 61.5125 | 61.4875 | 61.4611 | 61.5122 | 61.546 | 61.4991 | 61.5706 | 123.1018 | 61.6897 | 123.033 | 61.4308 | 61.503 | 123.0576 | 61.4625 | 122.8541 | 61.5987 | 61.6393 | 61.53 | 61.5705
2035.0625 | 123.2437 | -61.4914 | 61.6699 | 0.034862 | 0.009846 | -0.002842 | 0.039082 | 0.082044 | 0.026064 | 0.1021 | 61.6287 | 0.21658 | 61.5553 | -0.042259 | 0.029923 | 61.5845 | -0.006014 | 61.381 | 61.5263 | 61.5012 | 61.4886 | 61.5305 | 61.5734 | 61.5175 | 61.5935 | 123.1201 | 61.708 | 123.0467 | 61.4491 | 61.5213 | 123.0759 | 61.4854 | 122.8724 | 61.5987 | 61.6347 | 61.5254 | 61.5614
2036.0625 | 123.3215 | -61.4639 | 61.6562 | 0.034862 | 0.019004 | -0.007421 | 0.034504 | 0.086622 | 0.030642 | 0.1021 | 61.6241 | 0.212 | 61.5553 | -0.033101 | 0.029923 | 61.5799 | -0.006014 | 61.3856 | 61.4988 | 61.4829 | 61.4565 | 61.4984 | 61.5506 | 61.4946 | 61.566 | 123.088 | 61.6759 | 123.0193 | 61.4308 | 61.4939 | 123.0438 | 61.4579 | 122.8495 | 61.5942 | 61.6301 | 61.5254 | 61.5614
2037.0625 | 123.2574 | -61.5189 | 61.6562 | 0.030283 | 0.014425 | -0.002842 | 0.034504 | 0.086622 | 0.026064 | 0.097519 | 61.6287 | 0.22574 | 61.5279 | -0.03768 | 0.034501 | 61.5845 | -0.001436 | 61.3764 | 61.5491 | 61.5333 | 61.516 | 61.5534 | 61.6055 | 61.5449 | 61.6164 | 123.1475 | 61.7446 | 123.0467 | 61.4812 | 61.5534 | 123.1033 | 61.5174 | 122.8953 | 61.5942 | 61.6301 | 61.4934 | 61.5293
2038.0625 | 123.2849 | -61.4914 | 61.6699 | 0.030283 | 0.019004 | -0.007421 | 0.039082 | 0.0912 | 0.035221 | 0.1021 | 61.6287 | 0.20742 | 61.5279 | -0.03768 | 0.029923 | 61.5845 | -0.006014 | 61.3764 | 61.5217 | 61.5104 | 61.484 | 61.5305 | 61.5826 | 61.5266 | 61.5935 | 123.1201 | 61.6988 | 123.0193 | 61.4537 | 61.5213 | 123.0759 | 61.4854 | 122.8678 | 61.5987 | 61.6347 | 61.4979 | 61.5339
2039.0625 | 123.2162 | -61.5326 | 61.6104 | 0.034862 | 0.009846 | -0.007421 | 0.048239 | 0.082044 | 0.030642 | 0.097519 | 61.6149 | 0.212 | 61.5187 | -0.042259 | 0.029923 | 61.5845 | -0.010593 | 61.3764 | 61.5675 | 61.5424 | 61.5252 | 61.5808 | 61.6146 | 61.5632 | 61.6301 | 123.1475 | 61.7446 | 123.0513 | 61.4903 | 61.5625 | 123.1171 | 61.522 | 122.909 | 61.585 | 61.6255 | 61.4888 | 61.5293
2040.0625 | 123.3032 | -61.4639 | 61.6791 | 0.034862 | 0.009846 | -0.007421 | 0.039082 | 0.086622 | 0.039799 | 0.097519 | 61.6195 | 0.22574 | 61.5233 | -0.03768 | 0.039079 | 61.5845 | -0.006014 | 61.3764 | 61.4988 | 61.4738 | 61.4565 | 61.503 | 61.5506 | 61.5037 | 61.5614 | 123.0834 | 61.6897 | 122.9872 | 61.4262 | 61.503 | 123.0484 | 61.4579 | 122.8403 | 61.5804 | 61.6255 | 61.4842 | 61.5293
2041.0625 | 123.2849 | -61.4731 | 61.6653 | 0.034862 | 0.019004 | -0.002842 | 0.043661 | 0.082044 | 0.030642 | 0.1021 | 61.6241 | 0.21658 | 61.5233 | -0.042259 | 0.034501 | 61.5845 | -0.006014 | 61.3856 | 61.5079 | 61.4921 | 61.4702 | 61.5167 | 61.5551 | 61.5037 | 61.5752 | 123.0972 | 61.6897 | 122.9964 | 61.4308 | 61.5076 | 123.0576 | 61.4671 | 122.8586 | 61.5896 | 61.6301 | 61.4888 | 61.5293
2042.0625 | 123.3994 | -61.4548 | 61.6013 | 0.034862 | 0.019004 | -0.002842 | 0.043661 | 0.086622 | 0.035221 | 0.092941 | 61.6287 | 0.22116 | 61.5508 | -0.033101 | 0.029923 | 61.5845 | -0.006014 | 61.3856 | 61.4896 | 61.4738 | 61.4519 | 61.4984 | 61.5414 | 61.49 | 61.5477 | 123.0834 | 61.6759 | 123.0055 | 61.4217 | 61.4847 | 123.0392 | 61.4488 | 122.8403 | 61.5987 | 61.6347 | 61.5208 | 61.5568
2043.0625 | 123.2895 | -61.496 | 61.6562 | 0.030283 | 0.019004 | -0.002842 | 0.039082 | 0.086622 | 0.035221 | 0.088362 | 61.6332 | 0.21658 | 61.5645 | -0.033101 | 0.043657 | 61.5891 | -0.006014 | 61.3856 | 61.5263 | 61.515 | 61.4931 | 61.5351 | 61.5826 | 61.5312 | 61.5843 | 123.1292 | 61.7126 | 123.0605 | 61.4629 | 61.5396 | 123.085 | 61.49 | 122.8815 | 61.5896 | 61.6393 | 61.5208 | 61.5705
2044.0625 | 123.4177 | -61.4777 | 61.5875 | 0.034862 | 0.019004 | -0.007421 | 0.048239 | 0.082044 | 0.030642 | 0.097519 | 61.6287 | 0.212 | 61.5553 | -0.055996 | 0.029923 | 61.5845 | -0.001436 | 61.3764 | 61.5125 | 61.4967 | 61.4702 | 61.5259 | 61.5597 | 61.5083 | 61.5752 | 123.1063 | 61.6897 | 123.033 | 61.4217 | 61.5076 | 123.0621 | 61.4762 | 122.8541 | 61.5987 | 61.6301 | 61.5254 | 61.5568
2045.0625 | 123.4085 | -61.4502 | 61.6196 | 0.034862 | 0.014425 | 0.001736 | 0.039082 | 0.077466 | 0.030642 | 0.097519 | 61.6287 | 0.22116 | 61.5599 | -0.046838 | 0.034501 | 61.5845 | -0.006014 | 61.3901 | 61.4851 | 61.4646 | 61.4519 | 61.4893 | 61.5277 | 61.4808 | 61.5477 | 123.0789 | 61.6714 | 123.0101 | 61.4034 | 61.4847 | 123.0347 | 61.4442 | 122.8403 | 61.5942 | 61.6347 | 61.5254 | 61.5659
2046.0625 | 123.2895 | -61.4914 | 61.7065 | 0.030283 | 0.023583 | -0.002842 | 0.043661 | 0.082044 | 0.030642 | 0.097519 | 61.6287 | 0.22574 | 61.5508 | -0.03768 | 0.039079 | 61.5845 | 0.003143 | 61.3901 | 61.5217 | 61.515 | 61.4886 | 61.5351 | 61.5734 | 61.522 | 61.5889 | 123.1201 | 61.7171 | 123.0422 | 61.4537 | 61.5305 | 123.0759 | 61.4945 | 122.8815 | 61.5896 | 61.6255 | 61.5117 | 61.5476
2047.0625 | 123.2895 | -61.4822 | 61.6562 | 0.034862 | 0.019004 | 0.001736 | 0.034504 | 0.086622 | 0.039799 | 0.10668 | 61.6287 | 0.21658 | 61.5645 | -0.042259 | 0.029923 | 61.5891 | -0.006014 | 61.3901 | 61.5171 | 61.5012 | 61.484 | 61.5167 | 61.5689 | 61.522 | 61.5889 | 123.1109 | 61.6988 | 123.0467 | 61.44 | 61.5122 | 123.0713 | 61.4762 | 122.8724 | 61.5987 | 61.6347 | 61.5346 | 61.5705
2048.0625 | 123.2758 | -61.4685 | 61.6608 | 0.030283 | 0.014425 | -0.002842 | 0.043661 | 0.077466 | 0.030642 | 0.092941 | 61.6332 | 0.212 | 61.5645 | -0.042259 | 0.034501 | 61.5891 | -0.001436 | 61.3856 | 61.4988 | 61.4829 | 61.4657 | 61.5122 | 61.546 | 61.4991 | 61.5614 | 123.1018 | 61.6805 | 123.033 | 61.4262 | 61.503 | 123.0576 | 61.4671 | 122.8541 | 61.5987 | 61.6347 | 61.53 | 61.5659
2049.0625 | 123.2803 | -61.5005 | 61.6928 | 0.034862 | 0.019004 | -0.012 | 0.048239 | 0.0912 | 0.039799 | 0.097519 | 61.6287 | 0.22116 | 61.5599 | -0.042259 | 0.039079 | 61.5799 | -0.001436 | 61.3901 | 61.5354 | 61.5196 | 61.4885 | 61.5488 | 61.5917 | 61.5403 | 61.5981 | 123.1292 | 61.7217 | 123.0605 | 61.4583 | 61.5396 | 123.0804 | 61.4991 | 122.8907 | 61.5896 | 61.6301 | 61.5208 | 61.5614
2050.0625 | 123.4222 | -61.4685 | 61.6379 | 0.030283 | 0.014425 | -0.002842 | 0.043661 | 0.077466 | 0.039799 | 0.092941 | 61.6287 | 0.21658 | 61.5553 | -0.042259 | 0.034501 | 61.5845 | -0.001436 | 61.381 | 61.4988 | 61.4829 | 61.4657 | 61.5122 | 61.546 | 61.5083 | 61.5614 | 123.0972 | 61.6851 | 123.0238 | 61.4262 | 61.503 | 123.053 | 61.4671 | 122.8495 | 61.5942 | 61.6301 | 61.5208 | 61.5568
2051.0625 | 123.3719 | -61.4456 | 61.6196 | 0.034862 | 0.009846 | -0.002842 | 0.043661 | 0.086622 | 0.035221 | 0.097519 | 61.6241 | 0.22116 | 61.5599 | -0.033101 | 0.029923 | 61.5936 | 0.003143 | 61.3856 | 61.4805 | 61.4555 | 61.4428 | 61.4893 | 61.5322 | 61.4808 | 61.5431 | 123.0697 | 61.6668 | 123.0055 | 61.4125 | 61.4755 | 123.0392 | 61.4488 | 122.8312 | 61.5942 | 61.6209 | 61.53 | 61.5568
2052.0625 | 123.2849 | -61.4777 | 61.6882 | 0.034862 | 0.014425 | -0.007421 | 0.043661 | 0.086622 | 0.030642 | 0.097519 | 61.6287 | 0.22574 | 61.5599 | -0.03768 | 0.029923 | 61.5799 | -0.001436 | 61.3856 | 61.5125 | 61.4921 | 61.4702 | 61.5213 | 61.5643 | 61.5083 | 61.5752 | 123.1063 | 61.7034 | 123.0376 | 61.44 | 61.5076 | 123.0576 | 61.4762 | 122.8632 | 61.5987 | 61.6301 | 61.53 | 61.5614
2053.0625 | 123.3444 | -61.4777 | 61.6425 | 0.03944 | 0.005267 | -0.007421 | 0.043661 | 0.077466 | 0.039799 | 0.097519 | 61.6195 | 0.212 | 61.5508 | -0.042259 | 0.034501 | 61.5845 | 0.003143 | 61.3764 | 61.5171 | 61.4829 | 61.4702 | 61.5213 | 61.5551 | 61.5175 | 61.5752 | 123.0972 | 61.6897 | 123.0284 | 61.4354 | 61.5122 | 123.0621 | 61.4808 | 122.8541 | 61.585 | 61.6164 | 61.5163 | 61.5476
2054.0625 | 123.2849 | -61.5051 | 61.6425 | 0.034862 | 0.019004 | -0.012 | 0.043661 | 0.086622 | 0.030642 | 0.097519 | 61.6241 | 0.22116 | 61.5553 | -0.03768 | 0.034501 | 61.5845 | -0.001436 | 61.3764 | 61.54 | 61.5241 | 61.4931 | 61.5488 | 61.5917 | 61.5358 | 61.6026 | 123.1292 | 61.7263 | 123.0605 | 61.4674 | 61.5396 | 123.0896 | 61.5037 | 122.8815 | 61.5896 | 61.6255 | 61.5208 | 61.5568
2055.0625 | 123.3673 | -61.4777 | 61.6013 | 0.034862 | 0.005267 | -0.012 | 0.043661 | 0.082044 | 0.035221 | 0.088362 | 61.6195 | 0.21658 | 61.5508 | -0.042259 | 0.034501 | 61.5891 | -0.006014 | 61.381 | 61.5125 | 61.4829 | 61.4657 | 61.5213 | 61.5597 | 61.5129 | 61.566 | 123.0972 | 61.6942 | 123.0284 | 61.4354 | 61.5122 | 123.0667 | 61.4716 | 122.8586 | 61.585 | 61.6255 | 61.5163 | 61.5568
2056.0625 | 123.3444 | -61.4639 | 61.6974 | 0.034862 | 0.014425 | -0.002842 | 0.043661 | 0.086622 | 0.039799 | 0.10668 | 61.6195 | 0.21658 | 61.5324 | -0.046838 | 0.034501 | 61.5799 | -0.001436 | 61.381 | 61.4988 | 61.4784 | 61.4611 | 61.5076 | 61.5506 | 61.5037 | 61.5706 | 123.0834 | 61.6805 | 122.9964 | 61.4171 | 61.4984 | 123.0438 | 61.4625 | 122.8449 | 61.585 | 61.6209 | 61.4979 | 61.5339
2057.0625 | 123.3856 | -61.4502 | 61.615 | 0.034862 | 0.005267 | -0.007421 | 0.043661 | 0.077466 | 0.035221 | 0.088362 | 61.6195 | 0.21658 | 61.5187 | -0.042259 | 0.039079 | 61.5845 | -0.001436 | 61.3856 | 61.4851 | 61.4555 | 61.4428 | 61.4939 | 61.5277 | 61.4854 | 61.5386 | 123.0697 | 61.6668 | 122.9689 | 61.4079 | 61.4893 | 123.0347 | 61.4488 | 122.8357 | 61.5804 | 61.6209 | 61.4796 | 61.5202
2058.0625 | 123.3627 | -61.4777 | 61.6333 | 0.034862 | 0.014425 | -0.007421 | 0.048239 | 0.072888 | 0.030642 | 0.092941 | 61.6149 | 0.22574 | 61.5233 | -0.042259 | 0.029923 | 61.5891 | -0.006014 | 61.381 | 61.5125 | 61.4921 | 61.4702 | 61.5259 | 61.5505 | 61.5083 | 61.5706 | 123.0926 | 61.7034 | 123.001 | 61.4354 | 61.5076 | 123.0667 | 61.4716 | 122.8586 | 61.585 | 61.6209 | 61.4934 | 61.5293
2059.0625 | 123.3765 | -61.4731 | 61.647 | 0.034862 | 0.009846 | 0.001736 | 0.043661 | 0.086622 | 0.030642 | 0.097519 | 61.6241 | 0.21658 | 61.5187 | -0.046838 | 0.034501 | 61.5799 | -0.001436 | 61.381 | 61.5079 | 61.4829 | 61.4748 | 61.5167 | 61.5597 | 61.5037 | 61.5706 | 123.0972 | 61.6897 | 122.9918 | 61.4262 | 61.5076 | 123.053 | 61.4716 | 122.8541 | 61.5896 | 61.6255 | 61.4842 | 61.5202
2060.0625 | 123.3765 | -61.4777 | 61.6058 | 0.030283 | 0.005267 | -0.002842 | 0.039082 | 0.082044 | 0.030642 | 0.092941 | 61.6241 | 0.212 | 61.5141 | -0.046838 | 0.029923 | 61.5799 | -0.001436 | 61.3764 | 61.5079 | 61.4829 | 61.4748 | 61.5167 | 61.5597 | 61.5083 | 61.5706 | 123.1018 | 61.6897 | 122.9918 | 61.4308 | 61.5076 | 123.0576 | 61.4762 | 122.8541 | 61.5942 | 61.6255 | 61.4842 | 61.5156
2061.0625 | 123.262 | -61.5005 | 61.6287 | 0.034862 | 0.023583 | 0.001736 | 0.043661 | 0.086622 | 0.035221 | 0.1021 | 61.6195 | 0.22116 | 61.5141 | -0.046838 | 0.034501 | 61.5799 | 0.003143 | 61.3764 | 61.5354 | 61.5241 | 61.5023 | 61.5442 | 61.5872 | 61.5358 | 61.6026 | 123.1201 | 61.7217 | 123.0147 | 61.4537 | 61.535 | 123.0804 | 61.5037 | 122.8769 | 61.585 | 61.6164 | 61.4796 | 61.511
2062.0625 | 123.2849 | -61.4594 | 61.6699 | 0.030283 | 0.009846 | -0.007421 | 0.043661 | 0.0912 | 0.039799 | 0.088362 | 61.6195 | 0.20742 | 61.5233 | -0.042259 | 0.034501 | 61.5845 | -0.006014 | 61.381 | 61.4896 | 61.4692 | 61.4519 | 61.503 | 61.5506 | 61.4992 | 61.5477 | 123.0789 | 61.6668 | 122.9826 | 61.4171 | 61.4939 | 123.0438 | 61.4533 | 122.8403 | 61.585 | 61.6255 | 61.4888 | 61.5293
2063.0625 | 123.2758 | -61.5005 | 61.647 | 0.030283 | 0.019004 | -0.007421 | 0.048239 | 0.086622 | 0.026064 | 0.097519 | 61.6241 | 0.212 | 61.5187 | -0.03768 | 0.039079 | 61.5845 | -0.006014 | 61.381 | 61.5308 | 61.5196 | 61.4931 | 61.5488 | 61.5872 | 61.5266 | 61.5981 | 123.1246 | 61.7126 | 123.0193 | 61.4629 | 61.5396 | 123.085 | 61.4945 | 122.8815 | 61.585 | 61.6301 | 61.4796 | 61.5247
2064.0625 | 123.3902 | -61.4685 | 61.615 | 0.034862 | 0.014425 | -0.012 | 0.043661 | 0.086622 | 0.035221 | 0.097519 | 61.6149 | 0.21658 | 61.5096 | -0.042259 | 0.025345 | 61.5845 | -0.001436 | 61.3718 | 61.5034 | 61.4829 | 61.4565 | 61.5122 | 61.5551 | 61.5037 | 61.566 | 123.0834 | 61.6851 | 122.9781 | 61.4262 | 61.4939 | 123.053 | 61.4671 | 122.8403 | 61.5896 | 61.6164 | 61.4842 | 61.511
2065.0625 | 123.3353 | -61.4822 | 61.6104 | 0.03944 | 0.014425 | -0.007421 | 0.052818 | 0.0912 | 0.039799 | 0.097519 | 61.6195 | 0.22116 | 61.5187 | -0.051417 | 0.025345 | 61.5845 | -0.006014 | 61.3718 | 61.5217 | 61.4967 | 61.4748 | 61.5351 | 61.5734 | 61.522 | 61.5798 | 123.1018 | 61.7034 | 123.001 | 61.4308 | 61.5076 | 123.0667 | 61.4762 | 122.8541 | 61.5942 | 61.6255 | 61.4934 | 61.5247
2066.0625 | 123.3398 | -61.5097 | 61.6608 | 0.034862 | 0.023583 | -0.007421 | 0.043661 | 0.0912 | 0.035221 | 0.1021 | 61.6241 | 0.22574 | 61.5187 | -0.033101 | 0.039079 | 61.5891 | -0.006014 | 61.381 | 61.5446 | 61.5333 | 61.5023 | 61.5534 | 61.6009 | 61.5449 | 61.6118 | 123.1338 | 61.7354 | 123.0284 | 61.4766 | 61.5488 | 123.0988 | 61.5037 | 122.8907 | 61.585 | 61.6301 | 61.4796 | 61.5247
2067.0625 | 123.4406 | -61.4319 | 61.6287 | 0.03944 | 0.019004 | -0.002842 | 0.039082 | 0.086622 | 0.035221 | 0.10668 | 61.6195 | 0.21658 | 61.5141 | -0.042259 | 0.029923 | 61.5799 | -0.010593 | 61.381 | 61.4713 | 61.4509 | 61.429 | 61.471 | 61.5185 | 61.4671 | 61.5386 | 123.0514 | 61.6485 | 122.946 | 61.3896 | 61.4618 | 123.0118 | 61.4213 | 122.8129 | 61.5896 | 61.6301 | 61.4842 | 61.5247
2068.0625 | 123.3353 | -61.4639 | 61.5921 | 0.034862 | 0.014425 | -0.007421 | 0.039082 | 0.086622 | 0.030642 | 0.1021 | 61.6241 | 0.21658 | 61.5279 | -0.042259 | 0.029923 | 61.5799 | -0.006014 | 61.3718 | 61.4988 | 61.4784 | 61.4565 | 61.503 | 61.5506 | 61.4946 | 61.566 | 123.088 | 61.6805 | 122.9918 | 61.4217 | 61.4939 | 123.0438 | 61.4579 | 122.8357 | 61.5942 | 61.6301 | 61.4979 | 61.5339
2069.0625 | 123.2758 | -61.4868 | 61.6196 | 0.03944 | 0.019004 | -0.007421 | 0.043661 | 0.082044 | 0.035221 | 0.097519 | 61.6149 | 0.21658 | 61.5141 | -0.042259 | 0.039079 | 61.5845 | -0.010593 | 61.381 | 61.5263 | 61.5058 | 61.4794 | 61.5305 | 61.5689 | 61.522 | 61.5843 | 123.1017 | 61.7034 | 123.001 | 61.4446 | 61.5259 | 123.0713 | 61.4762 | 122.8678 | 61.5759 | 61.6255 | 61.4751 | 61.5247
2070.0625 | 123.2483 | -61.4868 | 61.647 | 0.034862 | 0.019004 | -0.002842 | 0.043661 | 0.086622 | 0.039799 | 0.097519 | 61.6241 | 0.22116 | 61.5187 | -0.042259 | 0.039079 | 61.5845 | -0.006014 | 61.381 | 61.5217 | 61.5058 | 61.484 | 61.5305 | 61.5734 | 61.5266 | 61.5843 | 123.1109 | 61.708 | 123.0055 | 61.4446 | 61.5259 | 123.0713 | 61.4808 | 122.8678 | 61.585 | 61.6301 | 61.4796 | 61.5247
2071.0625 | 123.3582 | -61.4777 | 61.6379 | 0.030283 | 0.014425 | -0.012 | 0.057396 | 0.0912 | 0.026064 | 0.088362 | 61.6149 | 0.22116 | 61.5279 | -0.042259 | 0.029923 | 61.5845 | -0.006014 | 61.3718 | 61.5079 | 61.4921 | 61.4657 | 61.5351 | 61.5689 | 61.5037 | 61.566 | 123.0926 | 61.6988 | 123.0055 | 61.4354 | 61.5076 | 123.0621 | 61.4716 | 122.8495 | 61.585 | 61.6209 | 61.4979 | 61.5339
2072.0625 | 123.3673 | -61.4731 | 61.6425 | 0.030283 | 0.019004 | -0.007421 | 0.043661 | 0.077466 | 0.026064 | 0.1021 | 61.6241 | 0.22574 | 61.5279 | -0.033101 | 0.029923 | 61.5753 | -0.006014 | 61.381 | 61.5034 | 61.4921 | 61.4657 | 61.5167 | 61.5505 | 61.4991 | 61.5752 | 123.0972 | 61.6988 | 123.001 | 61.44 | 61.503 | 123.0484 | 61.4671 | 122.8541 | 61.5942 | 61.6301 | 61.4979 | 61.5339
2073.0625 | 123.317 | -61.4822 | 61.6425 | 0.025705 | 0.014425 | -0.007421 | 0.043661 | 0.086622 | 0.035221 | 0.1021 | 61.6195 | 0.21658 | 61.5233 | -0.046838 | 0.034501 | 61.5891 | -0.006014 | 61.3856 | 61.5079 | 61.4967 | 61.4748 | 61.5259 | 61.5689 | 61.5175 | 61.5843 | 123.1018 | 61.6988 | 123.0055 | 61.4354 | 61.5167 | 123.0713 | 61.4762 | 122.8678 | 61.585 | 61.6255 | 61.4888 | 61.5293
2074.0625 | 123.2483 | -61.5143 | 61.6516 | 0.030283 | 0.014425 | -0.007421 | 0.043661 | 0.082044 | 0.035221 | 0.1021 | 61.6241 | 0.22116 | 61.5279 | -0.046838 | 0.034501 | 61.5936 | -0.006014 | 61.3901 | 61.5446 | 61.5287 | 61.5069 | 61.5579 | 61.5963 | 61.5495 | 61.6164 | 123.1384 | 61.7354 | 123.0422 | 61.4674 | 61.5488 | 123.1079 | 61.5083 | 122.9044 | 61.5896 | 61.6301 | 61.4934 | 61.5339
2075.0625 | 123.2803 | -61.4639 | 61.6745 | 0.03944 | 0.014425 | -0.002842 | 0.039082 | 0.086622 | 0.039799 | 0.097519 | 61.6241 | 0.22116 | 61.5324 | -0.03768 | 0.029923 | 61.5936 | -0.001436 | 61.3856 | 61.5034 | 61.4784 | 61.4611 | 61.503 | 61.5506 | 61.5037 | 61.5614 | 123.088 | 61.6851 | 122.9964 | 61.4262 | 61.4939 | 123.0576 | 61.4625 | 122.8495 | 61.5942 | 61.6255 | 61.5025 | 61.5339
2076.0625 | 123.2849 | -61.5005 | 61.647 | 0.03944 | 0.019004 | -0.012 | 0.048239 | 0.082044 | 0.035221 | 0.097519 | 61.6241 | 0.21658 | 61.537 | -0.046838 | 0.034501 | 61.5845 | -0.006014 | 61.3718 | 61.54 | 61.5196 | 61.4885 | 61.5488 | 61.5826 | 61.5358 | 61.5981 | 123.1246 | 61.7171 | 123.0376 | 61.4537 | 61.535 | 123.085 | 61.4945 | 122.8724 | 61.5896 | 61.6301 | 61.5025 | 61.543
2077.0625 | 123.3124 | -61.4685 | 61.6196 | 0.044018 | 0.019004 | -0.002842 | 0.048239 | 0.086622 | 0.035221 | 0.1021 | 61.6149 | 0.22574 | 61.537 | -0.046838 | 0.034501 | 61.5845 | -0.001436 | 61.3856 | 61.5125 | 61.4875 | 61.4657 | 61.5167 | 61.5551 | 61.5037 | 61.5706 | 123.0834 | 61.6942 | 123.0055 | 61.4217 | 61.503 | 123.053 | 61.4671 | 122.8541 | 61.5804 | 61.6164 | 61.5025 | 61.5385
2078.0625 | 123.3032 | -61.4777 | 61.647 | 0.034862 | 0.014425 | 0.001736 | 0.043661 | 0.0912 | 0.039799 | 0.10668 | 61.6195 | 0.21658 | 61.5324 | -0.042259 | 0.039079 | 61.5891 | -0.006014 | 61.381 | 61.5125 | 61.4921 | 61.4794 | 61.5213 | 61.5689 | 61.5175 | 61.5843 | 123.0972 | 61.6942 | 123.0101 | 61.4354 | 61.5167 | 123.0667 | 61.4716 | 122.8586 | 61.5804 | 61.6255 | 61.4934 | 61.5385
2079.0625 | 123.2986 | -61.4868 | 61.6653 | 0.034862 | 0.014425 | -0.007421 | 0.043661 | 0.082044 | 0.039799 | 0.092941 | 61.6287 | 0.21658 | 61.5462 | -0.051417 | 0.034501 | 61.5753 | -0.001436 | 61.381 | 61.5217 | 61.5012 | 61.4794 | 61.5305 | 61.5689 | 61.5266 | 61.5798 | 123.1155 | 61.7034 | 123.033 | 61.4354 | 61.5213 | 123.0621 | 61.4854 | 122.8678 | 61.5942 | 61.6301 | 61.5117 | 61.5476
2080.0625 | 123.3307 | -61.4731 | 61.6196 | 0.03944 | 0.019004 | -0.007421 | 0.048239 | 0.082044 | 0.035221 | 0.1021 | 61.6287 | 0.22116 | 61.5553 | -0.03768 | 0.039079 | 61.5891 | -0.001436 | 61.3856 | 61.5125 | 61.4921 | 61.4657 | 61.5213 | 61.5551 | 61.5083 | 61.5752 | 123.1018 | 61.6942 | 123.0284 | 61.4354 | 61.5122 | 123.0621 | 61.4716 | 122.8586 | 61.5896 | 61.6301 | 61.5163 | 61.5568
2081.0625 | 123.3032 | -61.4731 | 61.6562 | 0.03944 | 0.019004 | 0.001736 | 0.048239 | 0.082044 | 0.039799 | 0.1021 | 61.6241 | 0.21658 | 61.5645 | -0.042259 | 0.034501 | 61.5799 | -0.001436 | 61.3901 | 61.5125 | 61.4921 | 61.4748 | 61.5213 | 61.5551 | 61.5129 | 61.5752 | 123.0972 | 61.6897 | 123.0376 | 61.4308 | 61.5076 | 123.053 | 61.4716 | 122.8632 | 61.5896 | 61.6255 | 61.53 | 61.5659
2082.0625 | 123.2758 | -61.5097 | 61.6699 | 0.044018 | 0.019004 | 0.001736 | 0.039082 | 0.077466 | 0.035221 | 0.1021 | 61.6241 | 0.21658 | 61.5645 | -0.042259 | 0.039079 | 61.5845 | -0.010593 | 61.381 | 61.5537 | 61.5287 | 61.5114 | 61.5488 | 61.5872 | 61.5449 | 61.6118 | 123.1338 | 61.7263 | 123.0742 | 61.4674 | 61.5488 | 123.0942 | 61.4991 | 122.8907 | 61.585 | 61.6347 | 61.5254 | 61.5751
2083.0625 | 123.2758 | -61.5143 | 61.6287 | 0.03944 | 0.009846 | -0.002842 | 0.043661 | 0.086622 | 0.039799 | 0.10668 | 61.6287 | 0.22116 | 61.5599 | -0.03768 | 0.029923 | 61.5799 | -0.006014 | 61.381 | 61.5537 | 61.5241 | 61.5114 | 61.5579 | 61.6009 | 61.5541 | 61.621 | 123.143 | 61.7354 | 123.0742 | 61.4766 | 61.5442 | 123.0942 | 61.5083 | 122.8953 | 61.5987 | 61.6347 | 61.53 | 61.5659
2084.0625 | 123.2483 | -61.4868 | 61.7249 | 0.034862 | 0.014425 | -0.002842 | 0.039082 | 0.082044 | 0.044377 | 0.10668 | 61.6195 | 0.21658 | 61.5279 | -0.046838 | 0.029923 | 61.5845 | -0.001436 | 61.381 | 61.5217 | 61.5012 | 61.484 | 61.5259 | 61.5689 | 61.5312 | 61.5935 | 123.1063 | 61.7034 | 123.0147 | 61.44 | 61.5167 | 123.0713 | 61.4854 | 122.8678 | 61.5896 | 61.6209 | 61.4979 | 61.5293
2085.0625 | 123.2849 | -61.4868 | 61.6562 | 0.034862 | 0.019004 | -0.007421 | 0.048239 | 0.082044 | 0.030642 | 0.1021 | 61.6287 | 0.22116 | 61.5141 | -0.042259 | 0.029923 | 61.5891 | -0.001436 | 61.3764 | 61.5217 | 61.5058 | 61.4794 | 61.5351 | 61.5689 | 61.5175 | 61.5889 | 123.1155 | 61.708 | 123.001 | 61.4446 | 61.5167 | 123.0759 | 61.4854 | 122.8632 | 61.5987 | 61.6301 | 61.4842 | 61.5156
2086.0625 | 123.3032 | -61.4731 | 61.6791 | 0.034862 | 0.014425 | 0.001736 | 0.039082 | 0.086622 | 0.030642 | 0.10668 | 61.6195 | 0.212 | 61.5279 | -0.03768 | 0.029923 | 61.5845 | -0.001436 | 61.3718 | 61.5079 | 61.4875 | 61.4748 | 61.5122 | 61.5597 | 61.5037 | 61.5798 | 123.0926 | 61.6851 | 123.001 | 61.4354 | 61.503 | 123.0576 | 61.4716 | 122.8449 | 61.5896 | 61.6209 | 61.4979 | 61.5293
2087.0625 | 123.3582 | -61.4639 | 61.5509 | 0.044018 | 0.023583 | -0.007421 | 0.048239 | 0.082044 | 0.030642 | 0.10668 | 61.6241 | 0.212 | 61.537 | -0.042259 | 0.029923 | 61.5891 | -0.006014 | 61.3764 | 61.5079 | 61.4875 | 61.4565 | 61.5122 | 61.546 | 61.4946 | 61.5706 | 123.088 | 61.6759 | 123.001 | 61.4217 | 61.4939 | 123.053 | 61.4579 | 122.8403 | 61.5942 | 61.6301 | 61.5071 | 61.543
2088.0625 | 123.262 | -61.4822 | 61.6699 | 0.03944 | 0.019004 | -0.007421 | 0.043661 | 0.072888 | 0.035221 | 0.1021 | 61.6241 | 0.21658 | 61.5599 | -0.046838 | 0.039079 | 61.5891 | -0.006014 | 61.381 | 61.5217 | 61.5012 | 61.4748 | 61.5259 | 61.5551 | 61.5175 | 61.5843 | 123.1063 | 61.6988 | 123.0422 | 61.4354 | 61.5213 | 123.0713 | 61.4762 | 122.8632 | 61.585 | 61.6301 | 61.5208 | 61.5659
2089.0625 | 123.2941 | -61.5143 | 61.6653 | 0.034862 | 0.019004 | -0.007421 | 0.052818 | 0.086622 | 0.039799 | 0.10668 | 61.6332 | 0.21658 | 61.5508 | -0.03768 | 0.039079 | 61.5845 | -0.006014 | 61.381 | 61.5491 | 61.5333 | 61.5069 | 61.5671 | 61.6009 | 61.5541 | 61.621 | 123.1475 | 61.7309 | 123.065 | 61.4766 | 61.5534 | 123.0988 | 61.5083 | 122.8953 | 61.5942 | 61.6393 | 61.5117 | 61.5568
2090.0625 | 123.2758 | -61.4548 | 61.6653 | 0.034862 | 0.014425 | -0.007421 | 0.043661 | 0.082044 | 0.026064 | 0.11125 | 61.6241 | 0.21658 | 61.5553 | -0.042259 | 0.039079 | 61.5845 | -0.006014 | 61.381 | 61.4896 | 61.4692 | 61.4474 | 61.4984 | 61.5368 | 61.4808 | 61.566 | 123.0789 | 61.6714 | 123.0101 | 61.4125 | 61.4939 | 123.0392 | 61.4488 | 122.8357 | 61.585 | 61.6301 | 61.5163 | 61.5614
2091.0625 | 123.3536 | -61.4685 | 61.6333 | 0.034862 | 0.019004 | -0.012 | 0.043661 | 0.082044 | 0.030642 | 0.11125 | 61.6332 | 0.21658 | 61.5324 | -0.042259 | 0.034501 | 61.5845 | -0.010593 | 61.381 | 61.5034 | 61.4875 | 61.4565 | 61.5122 | 61.5506 | 61.4991 | 61.5798 | 123.1018 | 61.6851 | 123.001 | 61.4262 | 61.503 | 123.053 | 61.4579 | 122.8495 | 61.5987 | 61.6438 | 61.4979 | 61.543
2092.0625 | 123.2529 | -61.4822 | 61.6882 | 0.034862 | 0.009846 | -0.002842 | 0.048239 | 0.082044 | 0.030642 | 0.10668 | 61.6241 | 0.22116 | 61.5233 | -0.033101 | 0.029923 | 61.5891 | -0.006014 | 61.3764 | 61.5171 | 61.4921 | 61.4794 | 61.5305 | 61.5643 | 61.5129 | 61.5889 | 123.1063 | 61.7034 | 123.0055 | 61.4491 | 61.5122 | 123.0713 | 61.4762 | 122.8586 | 61.5942 | 61.6301 | 61.4934 | 61.5293
2093.0625 | 123.3582 | -61.4777 | 61.6425 | 0.034862 | 0.014425 | 0.001736 | 0.043661 | 0.0912 | 0.030642 | 0.1021 | 61.6241 | 0.22574 | 61.5279 | -0.042259 | 0.034501 | 61.5891 | 0.003143 | 61.3901 | 61.5125 | 61.4921 | 61.4794 | 61.5213 | 61.5689 | 61.5083 | 61.5798 | 123.1018 | 61.7034 | 123.0055 | 61.4354 | 61.5122 | 123.0667 | 61.4808 | 122.8678 | 61.5896 | 61.6209 | 61.4934 | 61.5247
2094.0625 | 123.3994 | -61.4639 | 61.615 | 0.03944 | 0.009846 | -0.007421 | 0.048239 | 0.0912 | 0.026064 | 0.097519 | 61.6287 | 0.21658 | 61.5462 | -0.03768 | 0.029923 | 61.5845 | -0.006014 | 61.3764 | 61.5034 | 61.4738 | 61.4565 | 61.5122 | 61.5551 | 61.49 | 61.5614 | 123.0926 | 61.6805 | 123.0101 | 61.4262 | 61.4939 | 123.0484 | 61.4579 | 122.8403 | 61.5987 | 61.6347 | 61.5163 | 61.5522
2095.0625 | 123.3765 | -61.4365 | 61.6379 | 0.03944 | 0.014425 | -0.002842 | 0.057396 | 0.086622 | 0.030642 | 0.1021 | 61.6287 | 0.22116 | 61.5599 | -0.03768 | 0.029923 | 61.5845 | 0.003143 | 61.3764 | 61.4759 | 61.4509 | 61.4336 | 61.4939 | 61.5231 | 61.4671 | 61.5386 | 123.0651 | 61.6576 | 122.9964 | 61.3988 | 61.4664 | 123.0209 | 61.4396 | 122.8129 | 61.5987 | 61.6255 | 61.53 | 61.5568
2096.0625 | 123.4268 | -61.4639 | 61.6058 | 0.025705 | 0.014425 | 0.006315 | 0.048239 | 0.082044 | 0.026064 | 0.10668 | 61.6241 | 0.22574 | 61.5645 | -0.042259 | 0.034501 | 61.5845 | -0.006014 | 61.3764 | 61.4896 | 61.4784 | 61.4702 | 61.5122 | 61.546 | 61.49 | 61.5706 | 123.088 | 61.6897 | 123.0284 | 61.4217 | 61.4984 | 123.0484 | 61.4579 | 122.8403 | 61.5896 | 61.6301 | 61.53 | 61.5705
2097.0625 | 123.3078 | -61.4822 | 61.6745 | 0.030283 | 0.019004 | 0.006315 | 0.048239 | 0.082044 | 0.035221 | 0.10668 | 61.6287 | 0.20742 | 61.5599 | -0.042259 | 0.034501 | 61.5936 | -0.006014 | 61.3764 | 61.5125 | 61.5012 | 61.4886 | 61.5305 | 61.5643 | 61.5175 | 61.5889 | 123.1109 | 61.6897 | 123.0422 | 61.44 | 61.5167 | 123.0759 | 61.4762 | 122.8586 | 61.5942 | 61.6347 | 61.5254 | 61.5659
2098.0625 | 123.3353 | -61.5051 | 61.6333 | 0.03944 | 0.023583 | -0.002842 | 0.043661 | 0.077466 | 0.030642 | 0.10668 | 61.6287 | 0.22116 | 61.5553 | -0.03768 | 0.034501 | 61.5799 | -0.010593 | 61.3718 | 61.5446 | 61.5287 | 61.5023 | 61.5488 | 61.5826 | 61.5358 | 61.6118 | 123.1338 | 61.7263 | 123.0605 | 61.4674 | 61.5396 | 123.085 | 61.4945 | 122.8769 | 61.5942 | 61.6393 | 61.5208 | 61.5659
2099.0625 | 123.3582 | -61.4868 | 61.6104 | 0.03944 | 0.019004 | -0.007421 | 0.048239 | 0.086622 | 0.035221 | 0.10668 | 61.6287 | 0.22116 | 61.5553 | -0.042259 | 0.039079 | 61.5845 | -0.001436 | 61.3901 | 61.5263 | 61.5058 | 61.4794 | 61.5351 | 61.5734 | 61.522 | 61.5935 | 123.1155 | 61.708 | 123.0422 | 61.4446 | 61.5259 | 123.0713 | 61.4854 | 122.8769 | 61.5896 | 61.6301 | 61.5163 | 61.5568
2100.0625 | 123.4177 | -61.4777 | 61.615 | 0.030283 | 0.019004 | -0.002842 | 0.048239 | 0.086622 | 0.035221 | 0.10668 | 61.6241 | 0.22116 | 61.5645 | -0.03768 | 0.039079 | 61.5845 | -0.006014 | 61.3764 | 61.5079 | 61.4967 | 61.4748 | 61.5259 | 61.5643 | 61.5129 | 61.5843 | 123.1018 | 61.6988 | 123.0422 | 61.44 | 61.5167 | 123.0621 | 61.4716 | 122.8541 | 61.585 | 61.6301 | 61.5254 | 61.5705
2101.0625 | 123.3765 | -61.4594 | 61.6562 | 0.034862 | 0.014425 | -0.002842 | 0.057396 | 0.086622 | 0.035221 | 0.10668 | 61.6241 | 0.212 | 61.5599 | -0.051417 | 0.034501 | 61.5845 | -0.001436 | 61.381 | 61.4942 | 61.4738 | 61.4565 | 61.5167 | 61.546 | 61.4946 | 61.566 | 123.0834 | 61.6714 | 123.0193 | 61.4079 | 61.4939 | 123.0438 | 61.4579 | 122.8403 | 61.5896 | 61.6255 | 61.5254 | 61.5614
2102.0625 | 123.3215 | -61.4914 | 61.6425 | 0.03944 | 0.019004 | 0.001736 | 0.048239 | 0.0912 | 0.035221 | 0.1021 | 61.6332 | 0.22116 | 61.5645 | -0.033101 | 0.034501 | 61.5845 | -0.006014 | 61.381 | 61.5308 | 61.5104 | 61.4931 | 61.5396 | 61.5826 | 61.5266 | 61.5935 | 123.1246 | 61.7126 | 123.0559 | 61.4583 | 61.5259 | 123.0759 | 61.4854 | 122.8724 | 61.5987 | 61.6393 | 61.53 | 61.5705
2103.0625 | 123.3902 | -61.4548 | 61.6013 | 0.03944 | 0.023583 | -0.002842 | 0.052818 | 0.086622 | 0.026064 | 0.11125 | 61.6241 | 0.23032 | 61.5508 | -0.033101 | 0.029923 | 61.5799 | -0.001436 | 61.3856 | 61.4942 | 61.4784 | 61.4519 | 61.5076 | 61.5414 | 61.4808 | 61.566 | 123.0789 | 61.6851 | 123.0055 | 61.4217 | 61.4847 | 123.0347 | 61.4533 | 122.8403 | 61.5942 | 61.6255 | 61.5208 | 61.5522
2104.0625 | 123.3353 | -61.4731 | 61.6196 | 0.025705 | 0.014425 | -0.002842 | 0.043661 | 0.0912 | 0.030642 | 0.10668 | 61.6241 | 0.21658 | 61.5508 | -0.042259 | 0.034501 | 61.5936 | -0.006014 | 61.381 | 61.4988 | 61.4875 | 61.4702 | 61.5167 | 61.5643 | 61.5037 | 61.5798 | 123.0972 | 61.6897 | 123.0238 | 61.4308 | 61.5076 | 123.0667 | 61.4671 | 122.8541 | 61.5896 | 61.6301 | 61.5163 | 61.5568
2105.0625 | 123.381 | -61.4777 | 61.5967 | 0.044018 | 0.014425 | -0.002842 | 0.057396 | 0.086622 | 0.026064 | 0.10668 | 61.6195 | 0.212 | 61.537 | -0.042259 | 0.034501 | 61.5799 | -0.006014 | 61.3856 | 61.5217 | 61.4921 | 61.4748 | 61.5351 | 61.5643 | 61.5037 | 61.5843 | 123.0972 | 61.6897 | 123.0147 | 61.4354 | 61.5122 | 123.0576 | 61.4716 | 122.8632 | 61.585 | 61.6255 | 61.5025 | 61.543
2106.0625 | 123.3902 | -61.4731 | 61.5784 | 0.034862 | 0.028162 | -0.002842 | 0.048239 | 0.086622 | 0.035221 | 0.1021 | 61.6287 | 0.22116 | 61.5187 | -0.042259 | 0.025345 | 61.5845 | -0.001436 | 61.3718 | 61.5079 | 61.5012 | 61.4702 | 61.5213 | 61.5597 | 61.5083 | 61.5752 | 123.1018 | 61.6942 | 122.9918 | 61.4308 | 61.4984 | 123.0576 | 61.4716 | 122.8449 | 61.6033 | 61.6301 | 61.4934 | 61.5202
2107.0625 | 123.3261 | -61.5051 | 61.615 | 0.034862 | 0.009846 | -0.002842 | 0.052818 | 0.0912 | 0.030642 | 0.10668 | 61.6195 | 0.21658 | 61.5187 | -0.046838 | 0.034501 | 61.5891 | -0.006014 | 61.381 | 61.54 | 61.515 | 61.5023 | 61.5579 | 61.5963 | 61.5358 | 61.6118 | 123.1246 | 61.7217 | 123.0238 | 61.4583 | 61.5396 | 123.0942 | 61.4991 | 122.8861 | 61.585 | 61.6255 | 61.4842 | 61.5247
2108.0625 | 123.381 | -61.4548 | 61.5921 | 0.034862 | 0.009846 | -0.002842 | 0.048239 | 0.082044 | 0.039799 | 0.10668 | 61.6241 | 0.21658 | 61.5141 | -0.046838 | 0.029923 | 61.5799 | -0.001436 | 61.3764 | 61.4896 | 61.4646 | 61.4519 | 61.503 | 61.5368 | 61.4946 | 61.5614 | 123.0789 | 61.6714 | 122.9689 | 61.4079 | 61.4847 | 123.0347 | 61.4533 | 122.8312 | 61.5942 | 61.6255 | 61.4842 | 61.5156
2109.0625 | 123.3719 | -61.4777 | 61.5875 | 0.030283 | 0.023583 | -0.007421 | 0.052818 | 0.0912 | 0.035221 | 0.10668 | 61.6195 | 0.23032 | 61.5187 | -0.042259 | 0.025345 | 61.5845 | 0.003143 | 61.3718 | 61.5079 | 61.5012 | 61.4702 | 61.5305 | 61.5689 | 61.5129 | 61.5843 | 123.0972 | 61.708 | 122.9964 | 61.4354 | 61.503 | 123.0621 | 61.4808 | 122.8495 | 61.5942 | 61.6164 | 61.4934 | 61.5156
2110.0625 | 123.4039 | -61.4685 | 61.6058 | 0.03944 | 0.019004 | -0.002842 | 0.048239 | 0.086622 | 0.035221 | 0.10668 | 61.6195 | 0.22116 | 61.5233 | -0.042259 | 0.034501 | 61.5799 | -0.006014 | 61.3856 | 61.5079 | 61.4875 | 61.4657 | 61.5167 | 61.5551 | 61.5037 | 61.5752 | 123.088 | 61.6897 | 122.9918 | 61.4262 | 61.503 | 123.0484 | 61.4625 | 122.8541 | 61.585 | 61.6255 | 61.4888 | 61.5293
2111.0625 | 123.317 | -61.5051 | 61.6196 | 0.034862 | 0.019004 | 0.001736 | 0.057396 | 0.095778 | 0.039799 | 0.1021 | 61.6149 | 0.22574 | 61.5141 | -0.03768 | 0.029923 | 61.5891 | 0.003143 | 61.3764 | 61.54 | 61.5241 | 61.5069 | 61.5625 | 61.6009 | 61.5449 | 61.6072 | 123.1201 | 61.7309 | 123.0193 | 61.4674 | 61.535 | 123.0942 | 61.5083 | 122.8815 | 61.585 | 61.6118 | 61.4842 | 61.511
2112.0625 | 123.349 | -61.4777 | 61.615 | 0.030283 | 0.014425 | 0.001736 | 0.052818 | 0.0912 | 0.044377 | 0.11125 | 61.6195 | 0.21658 | 61.5279 | -0.046838 | 0.029923 | 61.5845 | -0.001436 | 61.3764 | 61.5079 | 61.4921 | 61.4794 | 61.5305 | 61.5689 | 61.522 | 61.5889 | 123.0972 | 61.6942 | 123.0055 | 61.4308 | 61.5076 | 123.0621 | 61.4762 | 122.8541 | 61.5896 | 61.6209 | 61.4979 | 61.5293
2113.0625 | 123.2895 | -61.496 | 61.6379 | 0.034862 | 0.023583 | -0.002842 | 0.052818 | 0.095778 | 0.039799 | 0.1021 | 61.6241 | 0.22116 | 61.5599 | -0.046838 | 0.029923 | 61.5936 | -0.006014 | 61.381 | 61.5308 | 61.5196 | 61.4931 | 61.5488 | 61.5918 | 61.5358 | 61.5981 | 123.1201 | 61.7171 | 123.0559 | 61.4491 | 61.5259 | 123.0896 | 61.49 | 122.8769 | 61.5942 | 61.6301 | 61.53 | 61.5659
2114.0625 | 123.3124 | -61.4868 | 61.6058 | 0.03944 | 0.023583 | 0.001736 | 0.057396 | 0.0912 | 0.044377 | 0.10668 | 61.6332 | 0.212 | 61.5645 | -0.042259 | 0.029923 | 61.5845 | -0.006014 | 61.381 | 61.5263 | 61.5104 | 61.4886 | 61.5442 | 61.578 | 61.5312 | 61.5935 | 123.1201 | 61.6988 | 123.0513 | 61.4446 | 61.5167 | 123.0713 | 61.4808 | 122.8678 | 61.6033 | 61.6393 | 61.5346 | 61.5705
2115.0625 | 123.2803 | -61.5005 | 61.6425 | 0.03944 | 0.028162 | 0.006315 | 0.057396 | 0.095778 | 0.039799 | 0.11125 | 61.6287 | 0.21658 | 61.5599 | -0.03768 | 0.029923 | 61.5799 | -0.001436 | 61.3764 | 61.54 | 61.5287 | 61.5069 | 61.5579 | 61.5963 | 61.5403 | 61.6118 | 123.1292 | 61.7171 | 123.0605 | 61.4629 | 61.5305 | 123.0804 | 61.4991 | 122.8769 | 61.5987 | 61.6301 | 61.53 | 61.5614
2116.0625 | 123.262 | -61.5005 | 61.6379 | 0.03944 | 0.03274 | 0.001736 | 0.057396 | 0.10493 | 0.048956 | 0.10668 | 61.6241 | 0.22116 | 61.537 | -0.042259 | 0.029923 | 61.5845 | -0.006014 | 61.3764 | 61.54 | 61.5333 | 61.5023 | 61.5579 | 61.6055 | 61.5495 | 61.6072 | 123.1246 | 61.7217 | 123.0376 | 61.4583 | 61.5305 | 123.085 | 61.4945 | 122.8769 | 61.5942 | 61.6301 | 61.5071 | 61.543
2117.0625 | 123.3719 | -61.4914 | 61.6379 | 0.030283 | 0.023583 | 0.006315 | 0.057396 | 0.095778 | 0.044377 | 0.10668 | 61.6195 | 0.22574 | 61.5187 | -0.042259 | 0.029923 | 61.5936 | 0.003143 | 61.3718 | 61.5217 | 61.515 | 61.4977 | 61.5488 | 61.5872 | 61.5358 | 61.5981 | 123.1109 | 61.7171 | 123.0101 | 61.4491 | 61.5213 | 123.085 | 61.4945 | 122.8632 | 61.5896 | 61.6164 | 61.4888 | 61.5156
2118.0625 | 123.2437 | -61.5051 | 61.6791 | 0.03944 | 0.028162 | 0.001736 | 0.048239 | 0.10036 | 0.048956 | 0.11125 | 61.6195 | 0.21658 | 61.5187 | -0.042259 | 0.029923 | 61.5845 | -0.010593 | 61.3764 | 61.5446 | 61.5333 | 61.5069 | 61.5534 | 61.6055 | 61.5541 | 61.6164 | 123.1246 | 61.7217 | 123.0238 | 61.4629 | 61.535 | 123.0896 | 61.4945 | 122.8815 | 61.5896 | 61.6301 | 61.4888 | 61.5293
2119.0625 | 123.317 | -61.4914 | 61.6379 | 0.044018 | 0.023583 | 0.006315 | 0.066553 | 0.095778 | 0.048956 | 0.11125 | 61.6241 | 0.21658 | 61.5279 | -0.042259 | 0.034501 | 61.5845 | 0.003143 | 61.3856 | 61.5354 | 61.515 | 61.4977 | 61.5579 | 61.5872 | 61.5403 | 61.6026 | 123.1155 | 61.708 | 123.0193 | 61.4491 | 61.5259 | 123.0759 | 61.4945 | 122.8769 | 61.5896 | 61.6209 | 61.4934 | 61.5247
2120.0625 | 123.3353 | -61.5051 | 61.6333 | 0.034862 | 0.028162 | 0.010893 | 0.057396 | 0.10036 | 0.053534 | 0.11125 | 61.6332 | 0.22116 | 61.5599 | -0.03768 | 0.034501 | 61.5753 | -0.006014 | 61.3856 | 61.54 | 61.5333 | 61.516 | 61.5625 | 61.6055 | 61.5587 | 61.6164 | 123.1384 | 61.7263 | 123.065 | 61.4674 | 61.5396 | 123.0804 | 61.4991 | 122.8907 | 61.5987 | 61.6393 | 61.5254 | 61.5659
2121.0625 | 123.2849 | -61.4685 | 61.6608 | 0.034862 | 0.028162 | 0.001736 | 0.066553 | 0.10036 | 0.048956 | 0.10668 | 61.6287 | 0.21658 | 61.5645 | -0.03768 | 0.029923 | 61.5845 | -0.001436 | 61.3764 | 61.5034 | 61.4967 | 61.4702 | 61.5351 | 61.5689 | 61.5175 | 61.5752 | 123.0972 | 61.6851 | 123.033 | 61.4308 | 61.4984 | 123.053 | 61.4671 | 122.8449 | 61.5987 | 61.6301 | 61.5346 | 61.5659
2122.0625 | 123.4177 | -61.4639 | 61.5829 | 0.034862 | 0.023583 | -0.002842 | 0.066553 | 0.10036 | 0.044377 | 0.10668 | 61.6287 | 0.21658 | 61.5645 | -0.046838 | 0.034501 | 61.5936 | -0.001436 | 61.3764 | 61.4988 | 61.4875 | 61.4611 | 61.5305 | 61.5643 | 61.5083 | 61.5706 | 123.0926 | 61.6805 | 123.0284 | 61.4171 | 61.4984 | 123.0576 | 61.4625 | 122.8403 | 61.5942 | 61.6301 | 61.53 | 61.5659
2123.0625 | 123.2941 | -61.5097 | 61.6653 | 0.034862 | 0.028162 | -0.007421 | 0.061975 | 0.10951 | 0.048956 | 0.10668 | 61.6332 | 0.21658 | 61.5508 | -0.042259 | 0.039079 | 61.5799 | -0.006014 | 61.381 | 61.5446 | 61.5379 | 61.5023 | 61.5717 | 61.6192 | 61.5587 | 61.6164 | 123.143 | 61.7263 | 123.0605 | 61.4674 | 61.5488 | 123.0896 | 61.5037 | 122.8907 | 61.5942 | 61.6393 | 61.5117 | 61.5568
2124.0625 | 123.3536 | -61.4731 | 61.6653 | 0.034862 | 0.023583 | 0.001736 | 0.061975 | 0.10493 | 0.053534 | 0.11125 | 61.6195 | 0.22116 | 61.5187 | -0.042259 | 0.039079 | 61.5753 | -0.006014 | 61.3856 | 61.5079 | 61.4967 | 61.4748 | 61.5351 | 61.578 | 61.5266 | 61.5843 | 123.0926 | 61.6942 | 122.9918 | 61.4308 | 61.5122 | 123.0484 | 61.4671 | 122.8586 | 61.5804 | 61.6255 | 61.4796 | 61.5247
2125.0625 | 123.2574 | -61.4914 | 61.6425 | 0.034862 | 0.028162 | 0.001736 | 0.052818 | 0.10493 | 0.053534 | 0.11583 | 61.6241 | 0.22116 | 61.5141 | -0.03768 | 0.039079 | 61.5845 | -0.001436 | 61.381 | 61.5263 | 61.5196 | 61.4931 | 61.5442 | 61.5963 | 61.5449 | 61.6072 | 123.1155 | 61.7126 | 123.0055 | 61.4537 | 61.5305 | 123.0759 | 61.49 | 122.8724 | 61.585 | 61.6255 | 61.4751 | 61.5156
2126.0625 | 123.3261 | -61.4868 | 61.6379 | 0.03944 | 0.03274 | 0.001736 | 0.061975 | 0.10493 | 0.048956 | 0.11125 | 61.6287 | 0.212 | 61.5233 | -0.042259 | 0.034501 | 61.5799 | -0.006014 | 61.3901 | 61.5263 | 61.5196 | 61.4886 | 61.5488 | 61.5917 | 61.5358 | 61.5981 | 123.1155 | 61.6988 | 123.0101 | 61.4446 | 61.5213 | 123.0667 | 61.4808 | 122.8769 | 61.5942 | 61.6347 | 61.4888 | 61.5293
2127.0625 | 123.2895 | -61.5143 | 61.6516 | 0.044018 | 0.028162 | 0.001736 | 0.057396 | 0.10951 | 0.044377 | 0.11583 | 61.6241 | 0.22574 | 61.5416 | -0.03768 | 0.034501 | 61.5936 | -0.001436 | 61.381 | 61.5583 | 61.5424 | 61.516 | 61.5717 | 61.6238 | 61.5587 | 61.6301 | 123.1384 | 61.74 | 123.0559 | 61.4766 | 61.5488 | 123.1079 | 61.5128 | 122.8953 | 61.5896 | 61.6255 | 61.5071 | 61.543
2128.0625 | 123.3353 | -61.496 | 61.6608 | 0.034862 | 0.03274 | 0.001736 | 0.066553 | 0.10951 | 0.048956 | 0.097519 | 61.6287 | 0.21658 | 61.5599 | -0.042259 | 0.034501 | 61.5799 | -0.001436 | 61.3856 | 61.5308 | 61.5287 | 61.4977 | 61.5625 | 61.6055 | 61.5449 | 61.5935 | 123.1246 | 61.7126 | 123.0559 | 61.4537 | 61.5305 | 123.0759 | 61.4945 | 122.8815 | 61.5942 | 61.6301 | 61.5254 | 61.5614
2129.0625 | 123.3032 | -61.4731 | 61.6608 | 0.030283 | 0.03274 | 0.006315 | 0.057396 | 0.10951 | 0.053534 | 0.10668 | 61.6378 | 0.22116 | 61.5599 | -0.046838 | 0.034501 | 61.5891 | -0.006014 | 61.381 | 61.5034 | 61.5058 | 61.4794 | 61.5305 | 61.5826 | 61.5266 | 61.5798 | 123.1109 | 61.6942 | 123.033 | 61.4262 | 61.5076 | 123.0621 | 61.4671 | 122.8541 | 61.6033 | 61.6438 | 61.5254 | 61.5659
2130.0625 | 123.3215 | -61.4822 | 61.6562 | 0.030283 | 0.023583 | 0.001736 | 0.061975 | 0.10493 | 0.048956 | 0.10668 | 61.6287 | 0.22116 | 61.5599 | -0.042259 | 0.039079 | 61.5845 | -0.006014 | 61.3901 | 61.5125 | 61.5058 | 61.484 | 61.5442 | 61.5872 | 61.5312 | 61.5889 | 123.1109 | 61.7034 | 123.0422 | 61.44 | 61.5213 | 123.0667 | 61.4762 | 122.8724 | 61.5896 | 61.6347 | 61.5208 | 61.5659
2131.0625 | 123.3353 | -61.4639 | 61.6516 | 0.034862 | 0.023583 | 0.001736 | 0.057396 | 0.11409 | 0.053534 | 0.1021 | 61.6287 | 0.22116 | 61.5645 | -0.042259 | 0.039079 | 61.5845 | 0.003143 | 61.3856 | 61.4988 | 61.4875 | 61.4657 | 61.5213 | 61.578 | 61.5175 | 61.566 | 123.0926 | 61.6851 | 123.0284 | 61.4217 | 61.503 | 123.0484 | 61.4671 | 122.8495 | 61.5896 | 61.6255 | 61.5254 | 61.5614
2132.0625 | 123.3856 | -61.4685 | 61.5967 | 0.030283 | 0.028162 | -0.002842 | 0.061975 | 0.10493 | 0.053534 | 0.1021 | 61.6287 | 0.21658 | 61.5645 | -0.042259 | 0.029923 | 61.5799 | -0.001436 | 61.381 | 61.4988 | 61.4967 | 61.4657 | 61.5305 | 61.5734 | 61.522 | 61.5706 | 123.0972 | 61.6851 | 123.033 | 61.4262 | 61.4984 | 123.0484 | 61.4671 | 122.8495 | 61.5987 | 61.6301 | 61.5346 | 61.5659
2133.0625 | 123.2803 | -61.5189 | 61.6699 | 0.030283 | 0.028162 | 0.001736 | 0.066553 | 0.10036 | 0.053534 | 0.1021 | 61.6332 | 0.22116 | 61.5599 | -0.042259 | 0.034501 | 61.5799 | -0.001436 | 61.3856 | 61.5491 | 61.547 | 61.5206 | 61.5854 | 61.6192 | 61.5724 | 61.621 | 123.1521 | 61.74 | 123.0788 | 61.4766 | 61.5534 | 123.0988 | 61.5174 | 122.9044 | 61.5987 | 61.6347 | 61.5254 | 61.5614
2134.0625 | 123.2803 | -61.5051 | 61.6653 | 0.034862 | 0.019004 | 0.006315 | 0.061975 | 0.10493 | 0.058113 | 0.1021 | 61.6287 | 0.21658 | 61.5553 | -0.03768 | 0.039079 | 61.5936 | -0.006014 | 61.3856 | 61.54 | 61.5241 | 61.5114 | 61.5671 | 61.6101 | 61.5632 | 61.6072 | 123.1338 | 61.7217 | 123.0605 | 61.4674 | 61.5442 | 123.0988 | 61.4991 | 122.8907 | 61.5896 | 61.6347 | 61.5163 | 61.5614
2135.0625 | 123.3398 | -61.4731 | 61.6699 | 0.03944 | 0.023583 | 0.006315 | 0.066553 | 0.10951 | 0.058113 | 0.10668 | 61.6332 | 0.22116 | 61.5416 | -0.03768 | 0.034501 | 61.5799 | 0.003143 | 61.3856 | 61.5125 | 61.4967 | 61.4794 | 61.5396 | 61.5826 | 61.5312 | 61.5798 | 123.1063 | 61.6942 | 123.0147 | 61.4354 | 61.5076 | 123.053 | 61.4762 | 122.8586 | 61.5987 | 61.6301 | 61.5071 | 61.5385
2136.0625 | 123.2986 | -61.4731 | 61.6653 | 0.03944 | 0.019004 | 0.001736 | 0.061975 | 0.11409 | 0.058113 | 0.10668 | 61.6241 | 0.22574 | 61.5233 | -0.042259 | 0.034501 | 61.5845 | -0.006014 | 61.381 | 61.5125 | 61.4921 | 61.4748 | 61.5351 | 61.5872 | 61.5312 | 61.5798 | 123.0972 | 61.6988 | 122.9964 | 61.4308 | 61.5076 | 123.0576 | 61.4671 | 122.8541 | 61.5896 | 61.6301 | 61.4888 | 61.5293
2137.0625 | 123.349 | -61.496 | 61.6287 | 0.044018 | 0.028162 | 0.001736 | 0.057396 | 0.10493 | 0.058113 | 0.1021 | 61.6149 | 0.22574 | 61.5233 | -0.051417 | 0.029923 | 61.5845 | -0.010593 | 61.3764 | 61.54 | 61.5241 | 61.4977 | 61.5534 | 61.6009 | 61.5541 | 61.5981 | 123.1109 | 61.7217 | 123.0193 | 61.4446 | 61.5259 | 123.0804 | 61.4854 | 122.8724 | 61.585 | 61.6255 | 61.4934 | 61.5339
2138.0625 | 123.2986 | -61.4914 | 61.6745 | 0.034862 | 0.023583 | 0.006315 | 0.061975 | 0.11409 | 0.058113 | 0.1021 | 61.6195 | 0.21658 | 61.5324 | -0.03768 | 0.029923 | 61.5891 | 0.003143 | 61.381 | 61.5263 | 61.515 | 61.4977 | 61.5534 | 61.6055 | 61.5495 | 61.5935 | 123.1109 | 61.708 | 123.0238 | 61.4537 | 61.5213 | 123.0804 | 61.4945 | 122.8724 | 61.5896 | 61.6164 | 61.5025 | 61.5293
2139.0625 | 123.2803 | -61.4868 | 61.6882 | 0.03944 | 0.019004 | 0.001736 | 0.066553 | 0.10493 | 0.058113 | 0.097519 | 61.6332 | 0.212 | 61.5553 | -0.03768 | 0.034501 | 61.5845 | 0.003143 | 61.381 | 61.5263 | 61.5058 | 61.4886 | 61.5534 | 61.5917 | 61.5449 | 61.5843 | 123.1201 | 61.6988 | 123.0422 | 61.4491 | 61.5213 | 123.0713 | 61.49 | 122.8678 | 61.5987 | 61.6301 | 61.5208 | 61.5522
2140.0625 | 123.2758 | -61.4822 | 61.6699 | 0.03944 | 0.023583 | 0.006315 | 0.061975 | 0.11409 | 0.062691 | 0.1021 | 61.6241 | 0.21658 | 61.5691 | -0.03768 | 0.043657 | 61.5845 | 0.003143 | 61.3856 | 61.5217 | 61.5058 | 61.4886 | 61.5442 | 61.5963 | 61.5449 | 61.5843 | 123.1063 | 61.6988 | 123.0513 | 61.4446 | 61.5259 | 123.0667 | 61.4854 | 122.8678 | 61.5804 | 61.6209 | 61.5254 | 61.5659
2141.0625 | 123.3215 | -61.4731 | 61.6974 | 0.030283 | 0.023583 | 0.006315 | 0.066553 | 0.10951 | 0.062691 | 0.10668 | 61.6332 | 0.22116 | 61.5691 | -0.042259 | 0.025345 | 61.5845 | -0.006014 | 61.3856 | 61.5034 | 61.4967 | 61.4794 | 61.5396 | 61.5826 | 61.5358 | 61.5798 | 123.1063 | 61.6942 | 123.0422 | 61.4308 | 61.4984 | 123.0576 | 61.4671 | 122.8586 | 61.6079 | 61.6393 | 61.5437 | 61.5751
2142.0625 | 123.4406 | -61.4548 | 61.6196 | 0.03944 | 0.028162 | 0.006315 | 0.057396 | 0.10951 | 0.053534 | 0.088362 | 61.6241 | 0.21658 | 61.5599 | -0.03768 | 0.039079 | 61.5845 | -0.001436 | 61.3856 | 61.4942 | 61.4829 | 61.4611 | 61.5122 | 61.5643 | 61.5083 | 61.5431 | 123.0789 | 61.6714 | 123.0147 | 61.4171 | 61.4939 | 123.0392 | 61.4533 | 122.8403 | 61.585 | 61.6255 | 61.5208 | 61.5614
2143.0625 | 123.262 | -61.4777 | 61.6653 | 0.030283 | 0.019004 | 0.006315 | 0.066553 | 0.11409 | 0.058113 | 0.097519 | 61.6241 | 0.22116 | 61.537 | -0.042259 | 0.034501 | 61.5891 | -0.001436 | 61.3856 | 61.5079 | 61.4967 | 61.484 | 61.5442 | 61.5918 | 61.5358 | 61.5752 | 123.1018 | 61.6988 | 123.0147 | 61.4354 | 61.5122 | 123.0667 | 61.4762 | 122.8632 | 61.5896 | 61.6255 | 61.5025 | 61.5385
2144.0625 | 123.2941 | -61.4822 | 61.6837 | 0.034862 | 0.019004 | 0.006315 | 0.061975 | 0.10951 | 0.053534 | 0.1021 | 61.6332 | 0.21658 | 61.5233 | -0.03768 | 0.039079 | 61.5845 | -0.001436 | 61.3764 | 61.5171 | 61.5012 | 61.4886 | 61.5442 | 61.5918 | 61.5358 | 61.5843 | 123.1155 | 61.6988 | 123.0055 | 61.4446 | 61.5213 | 123.0667 | 61.4808 | 122.8586 | 61.5942 | 61.6347 | 61.4842 | 61.5247
2145.0625 | 123.2758 | -61.5005 | 61.6516 | 0.044018 | 0.019004 | 0.001736 | 0.066553 | 0.10951 | 0.058113 | 0.092941 | 61.6241 | 0.21658 | 61.5233 | -0.042259 | 0.039079 | 61.5845 | -0.001436 | 61.3764 | 61.5446 | 61.5196 | 61.5023 | 61.5671 | 61.6101 | 61.5587 | 61.5935 | 123.1246 | 61.7171 | 123.0238 | 61.4583 | 61.5396 | 123.085 | 61.4991 | 122.8769 | 61.585 | 61.6255 | 61.4842 | 61.5247
2146.0625 | 123.2574 | -61.5097 | 61.6653 | 0.034862 | 0.028162 | 0.006315 | 0.071132 | 0.11409 | 0.062691 | 0.1021 | 61.6287 | 0.22116 | 61.5279 | -0.03768 | 0.039079 | 61.5845 | -0.006014 | 61.381 | 61.5446 | 61.5379 | 61.516 | 61.5808 | 61.6238 | 61.5724 | 61.6118 | 123.1384 | 61.7309 | 123.0376 | 61.472 | 61.5488 | 123.0942 | 61.5037 | 122.8907 | 61.5896 | 61.6347 | 61.4888 | 61.5339
2147.0625 | 123.3765 | -61.4822 | 61.6196 | 0.034862 | 0.019004 | 0.006315 | 0.066553 | 0.11409 | 0.048956 | 0.092941 | 61.6241 | 0.22574 | 61.5508 | -0.051417 | 0.020767 | 61.5936 | -0.006014 | 61.3718 | 61.5171 | 61.5012 | 61.4886 | 61.5488 | 61.5963 | 61.5312 | 61.5752 | 123.1063 | 61.708 | 123.033 | 61.4308 | 61.503 | 123.0759 | 61.4762 | 122.8541 | 61.6033 | 61.6301 | 61.53 | 61.5568
2148.0625 | 123.2666 | -61.5005 | 61.6745 | 0.034862 | 0.019004 | 0.006315 | 0.066553 | 0.11867 | 0.062691 | 0.092941 | 61.6287 | 0.21658 | 61.5599 | -0.03768 | 0.034501 | 61.5891 | -0.001436 | 61.381 | 61.5354 | 61.5196 | 61.5069 | 61.5671 | 61.6192 | 61.5632 | 61.5935 | 123.1292 | 61.7171 | 123.0605 | 61.4629 | 61.535 | 123.0896 | 61.4991 | 122.8815 | 61.5942 | 61.6301 | 61.5254 | 61.5614
2149.0625 | 123.2758 | -61.4914 | 61.6608 | 0.025705 | 0.019004 | 0.006315 | 0.061975 | 0.11867 | 0.053534 | 0.1021 | 61.6332 | 0.21658 | 61.5645 | -0.042259 | 0.034501 | 61.5799 | 0.003143 | 61.3856 | 61.5171 | 61.5104 | 61.4977 | 61.5534 | 61.6101 | 61.5449 | 61.5935 | 123.1246 | 61.708 | 123.0559 | 61.4491 | 61.5259 | 123.0713 | 61.4945 | 122.8769 | 61.5987 | 61.6301 | 61.53 | 61.5614
2150.0625 | 123.2574 | -61.4868 | 61.6791 | 0.030283 | 0.014425 | 0.001736 | 0.066553 | 0.11409 | 0.053534 | 0.1021 | 61.6195 | 0.22116 | 61.5599 | -0.042259 | 0.029923 | 61.5845 | -0.006014 | 61.3856 | 61.5171 | 61.5012 | 61.4886 | 61.5534 | 61.6009 | 61.5403 | 61.5889 | 123.1063 | 61.708 | 123.0467 | 61.4446 | 61.5167 | 123.0713 | 61.4808 | 122.8724 | 61.5896 | 61.6255 | 61.53 | 61.5659
2151.0625 | 123.2986 | -61.4914 | 61.6974 | 0.034862 | 0.014425 | -0.002842 | 0.066553 | 0.11409 | 0.062691 | 0.092941 | 61.6287 | 0.22116 | 61.5508 | -0.042259 | 0.029923 | 61.5845 | -0.001436 | 61.3856 | 61.5263 | 61.5058 | 61.4886 | 61.5579 | 61.6055 | 61.5541 | 61.5843 | 123.1201 | 61.7126 | 123.0422 | 61.4491 | 61.5213 | 123.0759 | 61.49 | 122.8769 | 61.5987 | 61.6301 | 61.5208 | 61.5522
2152.0625 | 123.4085 | -61.4548 | 61.6333 | 0.034862 | 0.009846 | 0.001736 | 0.057396 | 0.11409 | 0.048956 | 0.088362 | 61.6241 | 0.21658 | 61.5187 | -0.042259 | 0.034501 | 61.5845 | -0.006014 | 61.3764 | 61.4896 | 61.4646 | 61.4565 | 61.5122 | 61.5689 | 61.5037 | 61.5431 | 123.0789 | 61.6714 | 122.9735 | 61.4125 | 61.4893 | 123.0392 | 61.4488 | 122.8312 | 61.5896 | 61.6301 | 61.4842 | 61.5247
2153.0625 | 123.2529 | -61.4868 | 61.734 | 0.034862 | 0.019004 | 0.006315 | 0.057396 | 0.10951 | 0.062691 | 0.088362 | 61.6241 | 0.21658 | 61.5141 | -0.046838 | 0.034501 | 61.5845 | -0.001436 | 61.3764 | 61.5217 | 61.5058 | 61.4931 | 61.5442 | 61.5963 | 61.5495 | 61.5752 | 123.1109 | 61.7034 | 123.001 | 61.44 | 61.5213 | 123.0713 | 61.4854 | 122.8632 | 61.5896 | 61.6255 | 61.4796 | 61.5156
2154.0625 | 123.2483 | -61.496 | 61.6928 | 0.03944 | 0.019004 | 0.001736 | 0.066553 | 0.10951 | 0.053534 | 0.088362 | 61.6195 | 0.21658 | 61.5279 | -0.033101 | 0.029923 | 61.5891 | -0.001436 | 61.3764 | 61.5354 | 61.515 | 61.4977 | 61.5625 | 61.6055 | 61.5495 | 61.5843 | 123.1155 | 61.7126 | 123.0238 | 61.4629 | 61.5259 | 123.085 | 61.4945 | 122.8724 | 61.5896 | 61.6209 | 61.4979 | 61.5293
2155.0625 | 123.2712 | -61.4731 | 61.7065 | 0.030283 | 0.019004 | -0.002842 | 0.066553 | 0.10951 | 0.058113 | 0.092941 | 61.6195 | 0.22116 | 61.537 | -0.03768 | 0.029923 | 61.5799 | -0.006014 | 61.3856 | 61.5034 | 61.4921 | 61.4702 | 61.5396 | 61.5826 | 61.5312 | 61.566 | 123.0926 | 61.6942 | 123.0101 | 61.4354 | 61.503 | 123.053 | 61.4671 | 122.8586 | 61.5896 | 61.6255 | 61.5071 | 61.543
2156.0625 | 123.2437 | -61.4822 | 61.6608 | 0.030283 | 0.014425 | 0.001736 | 0.066553 | 0.11867 | 0.044377 | 0.088362 | 61.6287 | 0.22116 | 61.5599 | -0.03768 | 0.034501 | 61.5845 | -0.006014 | 61.3856 | 61.5125 | 61.4967 | 61.484 | 61.5488 | 61.6009 | 61.5266 | 61.5706 | 123.1109 | 61.7034 | 123.0422 | 61.4446 | 61.5167 | 123.0667 | 61.4762 | 122.8678 | 61.5942 | 61.6347 | 61.5254 | 61.5659
2157.0625 | 123.2758 | -61.5005 | 61.6608 | 0.03944 | 0.014425 | -0.002842 | 0.066553 | 0.11867 | 0.053534 | 0.092941 | 61.6332 | 0.22116 | 61.5645 | -0.046838 | 0.029923 | 61.5753 | -0.006014 | 61.3901 | 61.54 | 61.515 | 61.4977 | 61.5671 | 61.6192 | 61.5541 | 61.5935 | 123.1338 | 61.7217 | 123.065 | 61.4537 | 61.5305 | 123.0759 | 61.4945 | 122.8907 | 61.6033 | 61.6393 | 61.5346 | 61.5705
2158.0625 | 123.2529 | -61.4685 | 61.6699 | 0.025705 | 0.014425 | 0.006315 | 0.057396 | 0.10951 | 0.048956 | 0.092941 | 61.6378 | 0.21658 | 61.5645 | -0.042259 | 0.034501 | 61.5845 | 0.007721 | 61.3901 | 61.4942 | 61.4829 | 61.4748 | 61.5259 | 61.578 | 61.5175 | 61.5614 | 123.1063 | 61.6851 | 123.033 | 61.4262 | 61.503 | 123.053 | 61.4762 | 122.8586 | 61.6033 | 61.6301 | 61.53 | 61.5568
2159.0625 | 123.317 | -61.4868 | 61.6425 | 0.034862 | 0.014425 | 0.006315 | 0.061975 | 0.11409 | 0.058113 | 0.092941 | 61.6287 | 0.22116 | 61.5462 | -0.033101 | 0.039079 | 61.5891 | -0.001436 | 61.3901 | 61.5217 | 61.5012 | 61.4931 | 61.5488 | 61.6009 | 61.5449 | 61.5798 | 123.1155 | 61.708 | 123.033 | 61.4537 | 61.5259 | 123.0759 | 61.4854 | 122.8769 | 61.5896 | 61.6301 | 61.5071 | 61.5476
2160.0625 | 123.2529 | -61.5005 | 61.7065 | 0.03944 | 0.009846 | 0.006315 | 0.057396 | 0.10951 | 0.048956 | 0.097519 | 61.6241 | 0.21658 | 61.5233 | -0.042259 | 0.039079 | 61.5845 | -0.001436 | 61.3764 | 61.54 | 61.5104 | 61.5069 | 61.5579 | 61.6101 | 61.5495 | 61.5981 | 123.1246 | 61.7171 | 123.0238 | 61.4583 | 61.5396 | 123.085 | 61.4991 | 122.8769 | 61.585 | 61.6255 | 61.4842 | 61.5247
2161.0625 | 123.3307 | -61.4639 | 61.6653 | 0.034862 | 0.019004 | -0.007421 | 0.061975 | 0.11409 | 0.048956 | 0.088362 | 61.6195 | 0.22574 | 61.5233 | -0.042259 | 0.029923 | 61.5799 | -0.001436 | 61.381 | 61.4988 | 61.4829 | 61.4565 | 61.5259 | 61.578 | 61.5129 | 61.5523 | 123.0834 | 61.6897 | 122.9872 | 61.4217 | 61.4939 | 123.0438 | 61.4625 | 122.8449 | 61.5896 | 61.6209 | 61.4934 | 61.5247
2162.0625 | 123.3307 | -61.4822 | 61.6562 | 0.030283 | 0.023583 | 0.001736 | 0.071132 | 0.11867 | 0.048956 | 0.092941 | 61.6287 | 0.23032 | 61.5233 | -0.042259 | 0.029923 | 61.5845 | -0.006014 | 61.3764 | 61.5125 | 61.5058 | 61.484 | 61.5534 | 61.6009 | 61.5312 | 61.5752 | 123.1109 | 61.7126 | 123.0055 | 61.44 | 61.5122 | 123.0667 | 61.4762 | 122.8586 | 61.5987 | 61.6347 | 61.4934 | 61.5293
2163.0625 | 123.2941 | -61.4914 | 61.647 | 0.030283 | 0.019004 | 0.001736 | 0.071132 | 0.11867 | 0.048956 | 0.088362 | 61.6287 | 0.21658 | 61.5553 | -0.033101 | 0.039079 | 61.5936 | -0.006014 | 61.3856 | 61.5217 | 61.5104 | 61.4931 | 61.5625 | 61.6101 | 61.5403 | 61.5798 | 123.1201 | 61.708 | 123.0467 | 61.4583 | 61.5305 | 123.085 | 61.4854 | 122.8769 | 61.5896 | 61.6347 | 61.5163 | 61.5614
2164.0625 | 123.3353 | -61.4731 | 61.6653 | 0.025705 | 0.019004 | 0.001736 | 0.071132 | 0.11867 | 0.048956 | 0.088362 | 61.6332 | 0.22574 | 61.5599 | -0.046838 | 0.029923 | 61.5845 | -0.001436 | 61.381 | 61.4988 | 61.4921 | 61.4748 | 61.5442 | 61.5918 | 61.522 | 61.5614 | 123.1063 | 61.6988 | 123.033 | 61.4262 | 61.503 | 123.0576 | 61.4716 | 122.8541 | 61.6033 | 61.6347 | 61.53 | 61.5614
2165.0625 | 123.349 | -61.4777 | 61.6379 | 0.030283 | 0.014425 | -0.002842 | 0.057396 | 0.11409 | 0.053534 | 0.088362 | 61.6378 | 0.22116 | 61.5645 | -0.03768 | 0.029923 | 61.5936 | -0.001436 | 61.381 | 61.5079 | 61.4921 | 61.4748 | 61.5351 | 61.5918 | 61.5312 | 61.566 | 123.1155 | 61.6988 | 123.0422 | 61.44 | 61.5076 | 123.0713 | 61.4762 | 122.8586 | 61.6079 | 61.6393 | 61.5346 | 61.5659
2166.0625 | 123.4085 | -61.4639 | 61.6516 | 0.034862 | 0.009846 | -0.002842 | 0.057396 | 0.11867 | 0.048956 | 0.079206 | 61.6378 | 0.22116 | 61.5599 | -0.046838 | 0.034501 | 61.5799 | -0.001436 | 61.3856 | 61.4988 | 61.4738 | 61.4611 | 61.5213 | 61.5826 | 61.5129 | 61.5431 | 123.1018 | 61.6851 | 123.0238 | 61.4171 | 61.4984 | 123.0438 | 61.4625 | 122.8495 | 61.6033 | 61.6393 | 61.5254 | 61.5614
2167.0625 | 123.3124 | -61.5005 | 61.647 | 0.044018 | 0.019004 | 0.001736 | 0.066553 | 0.12325 | 0.053534 | 0.083784 | 61.6287 | 0.21658 | 61.5645 | -0.042259 | 0.034501 | 61.5845 | -0.006014 | 61.381 | 61.5446 | 61.5196 | 61.5023 | 61.5671 | 61.6238 | 61.5541 | 61.5843 | 123.1292 | 61.7171 | 123.065 | 61.4583 | 61.535 | 123.085 | 61.4945 | 122.8815 | 61.5942 | 61.6347 | 61.53 | 61.5705
2168.0625 | 123.3856 | -61.4731 | 61.6379 | 0.034862 | 0.023583 | 0.006315 | 0.061975 | 0.11867 | 0.048956 | 0.088362 | 61.6287 | 0.22116 | 61.5599 | -0.042259 | 0.034501 | 61.5845 | -0.006014 | 61.3764 | 61.5079 | 61.4967 | 61.4794 | 61.5351 | 61.5918 | 61.522 | 61.5614 | 123.1018 | 61.6942 | 123.033 | 61.4308 | 61.5076 | 123.0576 | 61.4671 | 122.8495 | 61.5942 | 61.6347 | 61.5254 | 61.5659
2169.0625 | 123.3124 | -61.4639 | 61.6699 | 0.030283 | 0.014425 | 0.006315 | 0.061975 | 0.12325 | 0.048956 | 0.088362 | 61.6195 | 0.212 | 61.5508 | -0.042259 | 0.039079 | 61.5845 | -0.001436 | 61.3901 | 61.4942 | 61.4784 | 61.4702 | 61.5259 | 61.5872 | 61.5129 | 61.5523 | 123.0834 | 61.6759 | 123.0147 | 61.4217 | 61.503 | 123.0484 | 61.4625 | 122.8541 | 61.5804 | 61.6209 | 61.5117 | 61.5522
2170.0625 | 123.3673 | -61.4731 | 61.6425 | 0.034862 | 0.009846 | 0.006315 | 0.052818 | 0.11409 | 0.048956 | 0.083784 | 61.6287 | 0.22116 | 61.5599 | -0.03768 | 0.034501 | 61.5891 | -0.001436 | 61.381 | 61.5079 | 61.4829 | 61.4794 | 61.5259 | 61.5872 | 61.522 | 61.5569 | 123.1018 | 61.6942 | 123.033 | 61.4354 | 61.5076 | 123.0621 | 61.4716 | 122.8541 | 61.5942 | 61.6301 | 61.5254 | 61.5614
2171.0625 | 123.3673 | -61.441 | 61.6241 | 0.034862 | 0.019004 | 0.001736 | 0.066553 | 0.11867 | 0.044377 | 0.083784 | 61.6378 | 0.22574 | 61.5508 | -0.033101 | 0.034501 | 61.5799 | -0.001436 | 61.381 | 61.4759 | 61.46 | 61.4428 | 61.5076 | 61.5597 | 61.4854 | 61.5248 | 123.0789 | 61.6668 | 122.9918 | 61.4079 | 61.4755 | 123.0209 | 61.4396 | 122.822 | 61.6033 | 61.6393 | 61.5163 | 61.5522
2172.0625 | 123.3032 | -61.4685 | 61.6425 | 0.034862 | 0.019004 | 0.006315 | 0.061975 | 0.11867 | 0.058113 | 0.083784 | 61.6332 | 0.21658 | 61.5599 | -0.03768 | 0.039079 | 61.5799 | 0.003143 | 61.3764 | 61.5034 | 61.4875 | 61.4748 | 61.5305 | 61.5872 | 61.5266 | 61.5523 | 123.1018 | 61.6851 | 123.0284 | 61.4308 | 61.5076 | 123.0484 | 61.4716 | 122.8449 | 61.5942 | 61.6301 | 61.5208 | 61.5568
2173.0625 | 123.2986 | -61.4685 | 61.6699 | 0.044018 | 0.009846 | 0.001736 | 0.048239 | 0.12325 | 0.058113 | 0.088362 | 61.6287 | 0.22574 | 61.5599 | -0.042259 | 0.039079 | 61.5891 | -0.006014 | 61.3856 | 61.5125 | 61.4784 | 61.4702 | 61.5167 | 61.5918 | 61.5266 | 61.5569 | 123.0972 | 61.6942 | 123.0284 | 61.4262 | 61.5076 | 123.0576 | 61.4625 | 122.8541 | 61.5896 | 61.6347 | 61.5208 | 61.5659
2174.0625 | 123.4039 | -61.4594 | 61.6196 | 0.034862 | 0.023583 | 0.006315 | 0.057396 | 0.11867 | 0.053534 | 0.088362 | 61.6241 | 0.21658 | 61.5508 | -0.03768 | 0.029923 | 61.5845 | 0.003143 | 61.3901 | 61.4942 | 61.4829 | 61.4657 | 61.5167 | 61.578 | 61.5129 | 61.5477 | 123.0834 | 61.6759 | 123.0101 | 61.4217 | 61.4893 | 123.0438 | 61.4625 | 122.8495 | 61.5942 | 61.6209 | 61.5208 | 61.5476
2175.0625 | 123.4085 | -61.4548 | 61.6287 | 0.030283 | 0.023583 | -0.002842 | 0.052818 | 0.11409 | 0.053534 | 0.088362 | 61.6241 | 0.22574 | 61.5508 | -0.042259 | 0.034501 | 61.5891 | -0.006014 | 61.381 | 61.4851 | 61.4784 | 61.4519 | 61.5076 | 61.5689 | 61.5083 | 61.5431 | 123.0789 | 61.6805 | 123.0055 | 61.4125 | 61.4893 | 123.0438 | 61.4488 | 122.8357 | 61.5896 | 61.6301 | 61.5163 | 61.5568
2176.0625 | 123.3353 | -61.4639 | 61.6745 | 0.03944 | 0.019004 | 0.006315 | 0.057396 | 0.11867 | 0.053534 | 0.083784 | 61.6287 | 0.22116 | 61.5553 | -0.03768 | 0.039079 | 61.5845 | -0.006014 | 61.3856 | 61.5034 | 61.4829 | 61.4702 | 61.5213 | 61.5826 | 61.5175 | 61.5477 | 123.0926 | 61.6851 | 123.0193 | 61.4262 | 61.503 | 123.0484 | 61.4579 | 122.8495 | 61.5896 | 61.6347 | 61.5163 | 61.5614
2177.0625 | 123.3261 | -61.4868 | 61.6379 | 0.034862 | 0.014425 | -0.002842 | 0.057396 | 0.12325 | 0.058113 | 0.088362 | 61.6332 | 0.21658 | 61.5599 | -0.033101 | 0.034501 | 61.5845 | -0.006014 | 61.381 | 61.5217 | 61.5012 | 61.484 | 61.5442 | 61.6101 | 61.5449 | 61.5752 | 123.1201 | 61.7034 | 123.0467 | 61.4537 | 61.5213 | 123.0713 | 61.4808 | 122.8678 | 61.5987 | 61.6393 | 61.5254 | 61.5659
2178.0625 | 123.3765 | -61.4777 | 61.6562 | 0.030283 | 0.014425 | 0.001736 | 0.061975 | 0.11867 | 0.053534 | 0.079206 | 61.6332 | 0.21658 | 61.5553 | -0.033101 | 0.043657 | 61.5845 | 0.003143 | 61.3856 | 61.5079 | 61.4921 | 61.4794 | 61.5396 | 61.5963 | 61.5312 | 61.5569 | 123.1109 | 61.6942 | 123.033 | 61.4446 | 61.5213 | 123.0621 | 61.4808 | 122.8632 | 61.5896 | 61.6301 | 61.5117 | 61.5522
2179.0625 | 123.3902 | -61.4594 | 61.6379 | 0.034862 | 0.019004 | 0.001736 | 0.061975 | 0.12325 | 0.053534 | 0.079206 | 61.6287 | 0.22574 | 61.5599 | -0.033101 | 0.034501 | 61.5799 | -0.006014 | 61.3901 | 61.4942 | 61.4784 | 61.4611 | 61.5213 | 61.5826 | 61.5129 | 61.5386 | 123.088 | 61.6851 | 123.0193 | 61.4262 | 61.4939 | 123.0392 | 61.4533 | 122.8495 | 61.5942 | 61.6347 | 61.5254 | 61.5659
2180.0625 | 123.3627 | -61.4914 | 61.6333 | 0.034862 | 0.014425 | 0.001736 | 0.061975 | 0.11409 | 0.053534 | 0.088362 | 61.6287 | 0.22116 | 61.5599 | -0.042259 | 0.034501 | 61.5799 | 0.003143 | 61.3856 | 61.5263 | 61.5058 | 61.4931 | 61.5534 | 61.6055 | 61.5449 | 61.5798 | 123.1201 | 61.7126 | 123.0513 | 61.4491 | 61.5259 | 123.0713 | 61.4945 | 122.8769 | 61.5942 | 61.6255 | 61.5254 | 61.5568
2181.0625 | 123.4131 | -61.4731 | 61.6379 | 0.034862 | 0.019004 | 0.006315 | 0.066553 | 0.12325 | 0.053534 | 0.079206 | 61.6332 | 0.22116 | 61.5553 | -0.03768 | 0.034501 | 61.5891 | -0.001436 | 61.3764 | 61.5079 | 61.4921 | 61.4794 | 61.5396 | 61.5963 | 61.5266 | 61.5523 | 123.1063 | 61.6942 | 123.0284 | 61.4354 | 61.5076 | 123.0621 | 61.4716 | 122.8495 | 61.5987 | 61.6347 | 61.5208 | 61.5568
2182.0625 | 123.3215 | -61.4868 | 61.6928 | 0.030283 | 0.014425 | 0.006315 | 0.066553 | 0.12325 | 0.053534 | 0.079206 | 61.6287 | 0.22574 | 61.5645 | -0.046838 | 0.034501 | 61.5845 | -0.006014 | 61.381 | 61.5171 | 61.5012 | 61.4931 | 61.5534 | 61.6101 | 61.5403 | 61.566 | 123.1155 | 61.7126 | 123.0513 | 61.44 | 61.5213 | 123.0713 | 61.4808 | 122.8678 | 61.5942 | 61.6347 | 61.53 | 61.5705
2183.0625 | 123.3673 | -61.4548 | 61.6562 | 0.025705 | 0.019004 | 0.001736 | 0.071132 | 0.12325 | 0.053534 | 0.088362 | 61.6287 | 0.22116 | 61.5645 | -0.042259 | 0.029923 | 61.5845 | -0.006014 | 61.3856 | 61.4805 | 61.4738 | 61.4565 | 61.5259 | 61.578 | 61.5083 | 61.5431 | 123.0834 | 61.6759 | 123.0193 | 61.4125 | 61.4847 | 123.0392 | 61.4488 | 122.8403 | 61.5987 | 61.6347 | 61.5346 | 61.5705
2184.0625 | 123.3307 | -61.4685 | 61.6379 | 0.034862 | 0.009846 | 0.001736 | 0.066553 | 0.11867 | 0.053534 | 0.088362 | 61.6332 | 0.21658 | 61.5599 | -0.033101 | 0.039079 | 61.5799 | -0.010593 | 61.381 | 61.5034 | 61.4784 | 61.4702 | 61.5351 | 61.5872 | 61.522 | 61.5569 | 123.1018 | 61.6851 | 123.0284 | 61.4354 | 61.5076 | 123.0484 | 61.4579 | 122.8495 | 61.5942 | 61.6438 | 61.5208 | 61.5705
2185.0625 | 123.3902 | -61.4777 | 61.6699 | 0.044018 | 0.023583 | 0.006315 | 0.071132 | 0.12782 | 0.053534 | 0.088362 | 61.6241 | 0.21658 | 61.5599 | -0.033101 | 0.039079 | 61.5845 | -0.001436 | 61.381 | 61.5217 | 61.5012 | 61.484 | 61.5488 | 61.6055 | 61.5312 | 61.566 | 123.1018 | 61.6942 | 123.0376 | 61.4446 | 61.5167 | 123.0621 | 61.4762 | 122.8586 | 61.585 | 61.6255 | 61.5208 | 61.5614
2186.0625 | 123.381 | -61.4777 | 61.6516 | 0.034862 | 0.014425 | -0.002842 | 0.066553 | 0.1324 | 0.048956 | 0.088362 | 61.6195 | 0.21658 | 61.5553 | -0.03768 | 0.029923 | 61.5845 | -0.006014 | 61.3856 | 61.5125 | 61.4921 | 61.4748 | 61.5442 | 61.6101 | 61.5266 | 61.566 | 123.0972 | 61.6942 | 123.033 | 61.44 | 61.5076 | 123.0621 | 61.4716 | 122.8632 | 61.5896 | 61.6255 | 61.5254 | 61.5614
2187.0625 | 123.2941 | -61.4777 | 61.6745 | 0.034862 | 0.009846 | 0.010893 | 0.071132 | 0.1324 | 0.053534 | 0.088362 | 61.6332 | 0.212 | 61.5737 | -0.033101 | 0.034501 | 61.5891 | -0.006014 | 61.3856 | 61.5125 | 61.4875 | 61.4886 | 61.5488 | 61.6101 | 61.5312 | 61.566 | 123.1109 | 61.6897 | 123.0513 | 61.4446 | 61.5122 | 123.0667 | 61.4716 | 122.8632 | 61.5987 | 61.6393 | 61.5392 | 61.5797
2188.0625 | 123.4543 | -61.4365 | 61.615 | 0.030283 | 0.019004 | -0.002842 | 0.071132 | 0.12782 | 0.048956 | 0.088362 | 61.6332 | 0.22116 | 61.5645 | -0.046838 | 0.029923 | 61.5845 | -0.001436 | 61.3901 | 61.4667 | 61.4555 | 61.4336 | 61.5076 | 61.5643 | 61.4854 | 61.5248 | 123.0697 | 61.6576 | 123.001 | 61.3896 | 61.4664 | 123.0209 | 61.435 | 122.8266 | 61.6033 | 61.6347 | 61.5346 | 61.5659
2189.0625 | 123.381 | -61.4685 | 61.6333 | 0.025705 | 0.019004 | 0.010893 | 0.07571 | 0.1324 | 0.058113 | 0.083784 | 61.6378 | 0.22116 | 61.5599 | -0.033101 | 0.034501 | 61.5891 | -0.001436 | 61.3856 | 61.4942 | 61.4875 | 61.4794 | 61.5442 | 61.6009 | 61.5266 | 61.5523 | 123.1063 | 61.6897 | 123.0284 | 61.4354 | 61.503 | 123.0576 | 61.4671 | 122.8541 | 61.6033 | 61.6393 | 61.5254 | 61.5614
2190.0625 | 123.3582 | -61.4731 | 61.6516 | 0.03944 | 0.019004 | 0.006315 | 0.07571 | 0.12782 | 0.053534 | 0.088362 | 61.6287 | 0.22116 | 61.5645 | -0.03768 | 0.034501 | 61.5799 | 0.007721 | 61.3993 | 61.5125 | 61.4921 | 61.4794 | 61.5488 | 61.6009 | 61.5266 | 61.5614 | 123.1018 | 61.6942 | 123.0376 | 61.4354 | 61.5076 | 123.053 | 61.4808 | 122.8724 | 61.5942 | 61.6209 | 61.53 | 61.5568
2191.0625 | 123.3673 | -61.4639 | 61.647 | 0.025705 | 0.009846 | 0.001736 | 0.07571 | 0.1324 | 0.053534 | 0.083784 | 61.6332 | 0.21658 | 61.5553 | -0.042259 | 0.034501 | 61.5891 | -0.006014 | 61.3901 | 61.4896 | 61.4738 | 61.4657 | 61.5396 | 61.5963 | 61.5175 | 61.5477 | 123.0972 | 61.6805 | 123.0193 | 61.4217 | 61.4984 | 123.053 | 61.4579 | 122.8541 | 61.5987 | 61.6393 | 61.5208 | 61.5614
2192.0625 | 123.317 | -61.4594 | 61.6653 | 0.03944 | 0.019004 | 0.006315 | 0.080288 | 0.14156 | 0.067269 | 0.088362 | 61.6332 | 0.21658 | 61.5599 | -0.03768 | 0.034501 | 61.5845 | -0.006014 | 61.3901 | 61.4988 | 61.4784 | 61.4657 | 61.5396 | 61.6009 | 61.5266 | 61.5477 | 123.0926 | 61.6759 | 123.0193 | 61.4217 | 61.4939 | 123.0438 | 61.4533 | 122.8495 | 61.5987 | 61.6393 | 61.5254 | 61.5659
2193.0625 | 123.3582 | -61.4594 | 61.6425 | 0.030283 | 0.009846 | 0.006315 | 0.07571 | 0.13698 | 0.053534 | 0.092941 | 61.6287 | 0.22574 | 61.5508 | -0.033101 | 0.025345 | 61.5845 | -0.006014 | 61.3901 | 61.4896 | 61.4692 | 61.4657 | 61.5351 | 61.5963 | 61.5129 | 61.5523 | 123.088 | 61.6851 | 123.0101 | 61.4262 | 61.4847 | 123.0438 | 61.4533 | 122.8495 | 61.6033 | 61.6347 | 61.5254 | 61.5568
2194.0625 | 123.3856 | -61.4594 | 61.6241 | 0.030283 | 0.009846 | 0.010893 | 0.080288 | 0.13698 | 0.062691 | 0.088362 | 61.6287 | 0.22116 | 61.5553 | -0.03768 | 0.034501 | 61.5799 | 0.003143 | 61.381 | 61.4896 | 61.4692 | 61.4702 | 61.5396 | 61.5963 | 61.522 | 61.5477 | 123.088 | 61.6805 | 123.0147 | 61.4217 | 61.4939 | 123.0392 | 61.4625 | 122.8403 | 61.5942 | 61.6255 | 61.5208 | 61.5522
2195.0625 | 123.4268 | -61.4502 | 61.6287 | 0.025705 | 0.014425 | 0.010893 | 0.07571 | 0.13698 | 0.058113 | 0.097519 | 61.6287 | 0.22116 | 61.5645 | -0.03768 | 0.043657 | 61.5891 | -0.006014 | 61.3856 | 61.4759 | 61.4646 | 61.4611 | 61.5259 | 61.5872 | 61.5083 | 61.5477 | 123.0789 | 61.6714 | 123.0147 | 61.4125 | 61.4939 | 123.0392 | 61.4442 | 122.8357 | 61.585 | 61.6347 | 61.5208 | 61.5705
2196.0625 | 123.3398 | -61.4639 | 61.6241 | 0.025705 | 0.014425 | 0.001736 | 0.07571 | 0.12782 | 0.062691 | 0.092941 | 61.6378 | 0.22116 | 61.5599 | -0.03768 | 0.034501 | 61.5891 | -0.001436 | 61.3901 | 61.4896 | 61.4784 | 61.4657 | 61.5396 | 61.5918 | 61.5266 | 61.5569 | 123.1018 | 61.6851 | 123.0238 | 61.4262 | 61.4984 | 123.053 | 61.4625 | 122.8541 | 61.6033 | 61.6393 | 61.5254 | 61.5614
2197.0625 | 123.2666 | -61.4456 | 61.6837 | 0.025705 | 0.014425 | 0.001736 | 0.084867 | 0.14156 | 0.058113 | 0.088362 | 61.6332 | 0.22116 | 61.5599 | -0.03768 | 0.043657 | 61.5799 | -0.001436 | 61.3856 | 61.4713 | 61.46 | 61.4474 | 61.5305 | 61.5872 | 61.5037 | 61.534 | 123.0789 | 61.6668 | 123.0055 | 61.4079 | 61.4893 | 123.0255 | 61.4442 | 122.8312 | 61.5896 | 61.6347 | 61.5163 | 61.5614
2198.0625 | 123.3765 | -61.4594 | 61.6287 | 0.03944 | 0.009846 | 0.015472 | 0.084867 | 0.14614 | 0.053534 | 0.088362 | 61.6287 | 0.21658 | 61.5553 | -0.033101 | 0.034501 | 61.5845 | -0.006014 | 61.3901 | 61.4988 | 61.4692 | 61.4748 | 61.5442 | 61.6055 | 61.5129 | 61.5477 | 123.088 | 61.6759 | 123.0147 | 61.4262 | 61.4939 | 123.0438 | 61.4533 | 122.8495 | 61.5942 | 61.6347 | 61.5208 | 61.5614
2199.0625 | 123.3994 | -61.4731 | 61.6425 | 0.03944 | 0.009846 | 0.001736 | 0.084867 | 0.13698 | 0.048956 | 0.092941 | 61.6332 | 0.21658 | 61.5599 | -0.042259 | 0.029923 | 61.5845 | -0.006014 | 61.381 | 61.5125 | 61.4829 | 61.4748 | 61.558 | 61.6101 | 61.522 | 61.566 | 123.1063 | 61.6897 | 123.033 | 61.4308 | 61.503 | 123.0576 | 61.4671 | 122.8541 | 61.6033 | 61.6393 | 61.53 | 61.5659
2200.0625 | 123.3765 | -61.4777 | 61.6333 | 0.025705 | 0.019004 | 0.001736 | 0.080288 | 0.1324 | 0.058113 | 0.097519 | 61.6241 | 0.21658 | 61.5599 | -0.03768 | 0.034501 | 61.5891 | -0.001436 | 61.3901 | 61.5034 | 61.4967 | 61.4794 | 61.5579 | 61.6101 | 61.5358 | 61.5752 | 123.1018 | 61.6942 | 123.0376 | 61.44 | 61.5122 | 123.0667 | 61.4762 | 122.8678 | 61.5896 | 61.6255 | 61.5254 | 61.5614
2201.0625 | 123.3765 | -61.4685 | 61.6562 | 0.030283 | 0.014425 | 0.010893 | 0.080288 | 0.14614 | 0.058113 | 0.097519 | 61.6287 | 0.22116 | 61.5645 | -0.042259 | 0.034501 | 61.5799 | -0.006014 | 61.3856 | 61.4988 | 61.4829 | 61.4794 | 61.5488 | 61.6146 | 61.5266 | 61.566 | 123.0972 | 61.6897 | 123.033 | 61.4262 | 61.503 | 123.0484 | 61.4625 | 122.8541 | 61.5942 | 61.6347 | 61.53 | 61.5705
2202.0625 | 123.2529 | -61.4914 | 61.6699 | 0.030283 | 0.005267 | 0.010893 | 0.080288 | 0.14156 | 0.058113 | 0.092941 | 61.6332 | 0.21658 | 61.5691 | -0.03768 | 0.034501 | 61.5845 | 0.003143 | 61.3901 | 61.5217 | 61.4967 | 61.5023 | 61.5717 | 61.633 | 61.5495 | 61.5843 | 123.1246 | 61.708 | 123.0605 | 61.4537 | 61.5259 | 123.0759 | 61.4945 | 122.8815 | 61.5987 | 61.6301 | 61.5346 | 61.5659
2203.0625 | 123.4131 | -61.4777 | 61.6196 | 0.034862 | 0.014425 | 0.001736 | 0.07571 | 0.14156 | 0.058113 | 0.092941 | 61.6287 | 0.22116 | 61.5599 | -0.046838 | 0.029923 | 61.5845 | -0.001436 | 61.381 | 61.5125 | 61.4921 | 61.4794 | 61.5534 | 61.6192 | 61.5358 | 61.5706 | 123.1063 | 61.6988 | 123.0376 | 61.4308 | 61.5076 | 123.0621 | 61.4762 | 122.8586 | 61.5987 | 61.6301 | 61.53 | 61.5614
2204.0625 | 123.3444 | -61.4777 | 61.647 | 0.034862 | 0.014425 | 0.006315 | 0.080288 | 0.13698 | 0.044377 | 0.097519 | 61.6332 | 0.21658 | 61.5737 | -0.046838 | 0.039079 | 61.5845 | -0.001436 | 61.3901 | 61.5125 | 61.4921 | 61.484 | 61.5579 | 61.6146 | 61.522 | 61.5752 | 123.1109 | 61.6942 | 123.0513 | 61.4308 | 61.5167 | 123.0621 | 61.4762 | 122.8678 | 61.5942 | 61.6347 | 61.5346 | 61.5751
2205.0625 | 123.3765 | -61.441 | 61.647 | 0.03944 | 0.009846 | 0.006315 | 0.07571 | 0.14156 | 0.048956 | 0.088362 | 61.6332 | 0.21658 | 61.5691 | -0.03768 | 0.034501 | 61.5845 | 0.003143 | 61.3856 | 61.4805 | 61.4509 | 61.4474 | 61.5168 | 61.5826 | 61.49 | 61.5294 | 123.0743 | 61.6576 | 123.0101 | 61.4034 | 61.4755 | 123.0255 | 61.4442 | 122.8266 | 61.5987 | 61.6301 | 61.5346 | 61.5659
2206.0625 | 123.3765 | -61.4594 | 61.6425 | 0.030283 | 0.014425 | 0.010893 | 0.080288 | 0.14156 | 0.053534 | 0.097519 | 61.6332 | 0.22574 | 61.5645 | -0.042259 | 0.039079 | 61.5845 | -0.006014 | 61.3901 | 61.4896 | 61.4738 | 61.4702 | 61.5396 | 61.6009 | 61.5129 | 61.5569 | 123.0926 | 61.6851 | 123.0238 | 61.4171 | 61.4984 | 123.0438 | 61.4533 | 122.8495 | 61.5942 | 61.6393 | 61.5254 | 61.5705
2207.0625 | 123.2758 | -61.496 | 61.6791 | 0.034862 | 0.014425 | 0.015472 | 0.084867 | 0.15071 | 0.048956 | 0.1021 | 61.6287 | 0.22116 | 61.5691 | -0.03768 | 0.034501 | 61.5891 | -0.006014 | 61.381 | 61.5308 | 61.5104 | 61.5114 | 61.5808 | 61.6467 | 61.5449 | 61.5981 | 123.1246 | 61.7171 | 123.065 | 61.4583 | 61.5305 | 123.085 | 61.49 | 122.8769 | 61.5942 | 61.6347 | 61.5346 | 61.5751
2208.0625 | 123.3719 | -61.4914 | 61.6425 | 0.034862 | 0.019004 | 0.010893 | 0.084867 | 0.14614 | 0.048956 | 0.1021 | 61.6287 | 0.22116 | 61.5645 | -0.033101 | 0.034501 | 61.5845 | -0.001436 | 61.3856 | 61.5263 | 61.5104 | 61.5023 | 61.5763 | 61.6375 | 61.5403 | 61.5935 | 123.1201 | 61.7126 | 123.0559 | 61.4583 | 61.5259 | 123.0759 | 61.49 | 122.8769 | 61.5942 | 61.6301 | 61.53 | 61.5659
2209.0625 | 123.3719 | -61.4731 | 61.6287 | 0.034862 | 0.014425 | 0.015472 | 0.089445 | 0.14156 | 0.058113 | 0.1021 | 61.6241 | 0.22574 | 61.5645 | -0.03768 | 0.034501 | 61.5891 | -0.006014 | 61.381 | 61.5079 | 61.4875 | 61.4886 | 61.5625 | 61.6146 | 61.5312 | 61.5752 | 123.0972 | 61.6988 | 123.0376 | 61.4354 | 61.5076 | 123.0621 | 61.4671 | 122.8541 | 61.5896 | 61.6301 | 61.53 | 61.5705
2210.0625 | 123.4497 | -61.4594 | 61.6287 | 0.03944 | 0.028162 | 0.010893 | 0.084867 | 0.14614 | 0.048956 | 0.097519 | 61.6287 | 0.22116 | 61.5691 | -0.03768 | 0.029923 | 61.5891 | -0.006014 | 61.3856 | 61.4988 | 61.4875 | 61.4702 | 61.5442 | 61.6055 | 61.5083 | 61.5569 | 123.088 | 61.6805 | 123.0284 | 61.4217 | 61.4893 | 123.0484 | 61.4533 | 122.8449 | 61.5987 | 61.6347 | 61.5392 | 61.5751
2211.0625 | 123.3719 | -61.4502 | 61.6379 | 0.030283 | 0.023583 | 0.015472 | 0.089445 | 0.15071 | 0.053534 | 0.1021 | 61.6287 | 0.22574 | 61.5599 | -0.03768 | 0.039079 | 61.5845 | -0.006014 | 61.381 | 61.4805 | 61.4738 | 61.4657 | 61.5396 | 61.6009 | 61.5037 | 61.5523 | 123.0789 | 61.6759 | 123.0101 | 61.4125 | 61.4893 | 123.0347 | 61.4442 | 122.8312 | 61.5896 | 61.6347 | 61.5208 | 61.5659
2212.0625 | 123.2574 | -61.4822 | 61.6882 | 0.034862 | 0.023583 | 0.020051 | 0.089445 | 0.14614 | 0.048956 | 0.11125 | 61.6332 | 0.21658 | 61.5645 | -0.03768 | 0.034501 | 61.5845 | -0.006014 | 61.3856 | 61.5171 | 61.5058 | 61.5023 | 61.5717 | 61.6284 | 61.5312 | 61.5935 | 123.1155 | 61.6988 | 123.0467 | 61.4446 | 61.5167 | 123.0667 | 61.4762 | 122.8678 | 61.5987 | 61.6393 | 61.53 | 61.5705
2213.0625 | 123.3719 | -61.4548 | 61.647 | 0.03944 | 0.023583 | 0.015472 | 0.089445 | 0.14614 | 0.048956 | 0.10668 | 61.6287 | 0.22574 | 61.5599 | -0.046838 | 0.025345 | 61.5891 | -0.001436 | 61.3856 | 61.4942 | 61.4784 | 61.4702 | 61.5442 | 61.6009 | 61.5037 | 61.5614 | 123.0834 | 61.6805 | 123.0147 | 61.4079 | 61.4801 | 123.0438 | 61.4533 | 122.8403 | 61.6033 | 61.6301 | 61.5346 | 61.5614
2214.0625 | 123.3673 | -61.4319 | 61.6333 | 0.030283 | 0.019004 | 0.024629 | 0.089445 | 0.14614 | 0.044377 | 0.10668 | 61.6287 | 0.22116 | 61.5599 | -0.042259 | 0.034501 | 61.5845 | -0.006014 | 61.381 | 61.4622 | 61.4509 | 61.4565 | 61.5213 | 61.578 | 61.4763 | 61.5386 | 123.0606 | 61.653 | 122.9918 | 61.3896 | 61.4664 | 123.0164 | 61.4259 | 122.8129 | 61.5942 | 61.6347 | 61.5254 | 61.5659
2215.0625 | 123.3948 | -61.4594 | 61.647 | 0.03944 | 0.023583 | 0.020051 | 0.084867 | 0.14614 | 0.053534 | 0.10668 | 61.6241 | 0.22116 | 61.5599 | -0.046838 | 0.039079 | 61.5891 | -0.006014 | 61.3856 | 61.4988 | 61.4829 | 61.4794 | 61.5442 | 61.6055 | 61.5129 | 61.566 | 123.0834 | 61.6805 | 123.0193 | 61.4125 | 61.4984 | 123.0484 | 61.4533 | 122.8449 | 61.585 | 61.6301 | 61.5208 | 61.5659
2216.0625 | 123.3994 | -61.4639 | 61.6241 | 0.03944 | 0.019004 | 0.020051 | 0.089445 | 0.15529 | 0.058113 | 0.11125 | 61.6332 | 0.22574 | 61.5599 | -0.03768 | 0.029923 | 61.5891 | -0.001436 | 61.381 | 61.5034 | 61.4829 | 61.484 | 61.5534 | 61.6192 | 61.522 | 61.5752 | 123.0972 | 61.6897 | 123.0238 | 61.4262 | 61.4939 | 123.053 | 61.4625 | 122.8449 | 61.6033 | 61.6347 | 61.53 | 61.5614
2217.0625 | 123.3124 | -61.496 | 61.6928 | 0.03944 | 0.023583 | 0.029208 | 0.089445 | 0.15987 | 0.067269 | 0.10668 | 61.6287 | 0.22116 | 61.5645 | -0.03768 | 0.043657 | 61.5845 | -0.010593 | 61.3856 | 61.5354 | 61.5196 | 61.5252 | 61.5854 | 61.6558 | 61.5632 | 61.6026 | 123.1246 | 61.7171 | 123.0605 | 61.4583 | 61.5396 | 123.0804 | 61.4854 | 122.8815 | 61.585 | 61.6393 | 61.5208 | 61.5751
2218.0625 | 123.3673 | -61.4548 | 61.6379 | 0.030283 | 0.023583 | 0.029208 | 0.089445 | 0.15071 | 0.062691 | 0.11125 | 61.6287 | 0.22116 | 61.5645 | -0.046838 | 0.029923 | 61.5982 | -0.006014 | 61.3901 | 61.4851 | 61.4784 | 61.484 | 61.5442 | 61.6055 | 61.5175 | 61.566 | 123.0834 | 61.6759 | 123.0193 | 61.4079 | 61.4847 | 123.053 | 61.4488 | 122.8449 | 61.5987 | 61.6347 | 61.5346 | 61.5705
2219.0625 | 123.4039 | -61.4685 | 61.6333 | 0.030283 | 0.019004 | 0.020051 | 0.084867 | 0.15529 | 0.058113 | 0.11125 | 61.6241 | 0.21658 | 61.5691 | -0.042259 | 0.034501 | 61.5845 | -0.006014 | 61.3901 | 61.4988 | 61.4875 | 61.4886 | 61.5534 | 61.6238 | 61.5266 | 61.5798 | 123.0926 | 61.6851 | 123.0376 | 61.4262 | 61.503 | 123.053 | 61.4625 | 122.8586 | 61.5896 | 61.6301 | 61.5346 | 61.5751
2220.0625 | 123.3994 | -61.4685 | 61.615 | 0.030283 | 0.019004 | 0.029208 | 0.089445 | 0.15529 | 0.053534 | 0.11125 | 61.6287 | 0.212 | 61.5691 | -0.046838 | 0.029923 | 61.5891 | -0.010593 | 61.3856 | 61.4988 | 61.4875 | 61.4977 | 61.558 | 61.6238 | 61.522 | 61.5798 | 123.0972 | 61.6805 | 123.0376 | 61.4217 | 61.4984 | 123.0576 | 61.4579 | 122.8541 | 61.5987 | 61.6393 | 61.5392 | 61.5797
2221.0625 | 123.5001 | -61.4182 | 61.7065 | 0.044018 | 0.009846 | 0.024629 | 0.089445 | 0.15071 | 0.058113 | 0.1021 | 61.6287 | 0.22116 | 61.5645 | -0.03768 | 0.039079 | 61.5891 | -0.006014 | 61.3856 | 61.4622 | 61.428 | 61.4428 | 61.5076 | 61.5689 | 61.4763 | 61.5202 | 123.0468 | 61.6393 | 122.9826 | 61.3805 | 61.4572 | 123.0072 | 61.4121 | 122.8037 | 61.5896 | 61.6347 | 61.5254 | 61.5705
2222.0625 | 123.3032 | -61.4548 | 61.6928 | 0.030283 | 0.014425 | 0.029208 | 0.089445 | 0.15987 | 0.053534 | 0.1021 | 61.6332 | 0.22116 | 61.5691 | -0.042259 | 0.043657 | 61.5891 | -0.001436 | 61.3947 | 61.4851 | 61.4692 | 61.484 | 61.5442 | 61.6146 | 61.5083 | 61.5569 | 123.088 | 61.6759 | 123.0238 | 61.4125 | 61.4984 | 123.0438 | 61.4533 | 122.8495 | 61.5896 | 61.6347 | 61.5254 | 61.5705
2223.0625 | 123.4131 | -61.4685 | 61.5784 | 0.03944 | 0.014425 | 0.029208 | 0.089445 | 0.15529 | 0.053534 | 0.1021 | 61.6287 | 0.22116 | 61.5691 | -0.033101 | 0.034501 | 61.5891 | -0.006014 | 61.381 | 61.5079 | 61.4829 | 61.4977 | 61.558 | 61.6238 | 61.522 | 61.5706 | 123.0972 | 61.6897 | 123.0376 | 61.4354 | 61.503 | 123.0576 | 61.4625 | 122.8495 | 61.5942 | 61.6347 | 61.5346 | 61.5751
2224.0625 | 123.4085 | -61.4685 | 61.615 | 0.030283 | 0.014425 | 0.029208 | 0.084867 | 0.15071 | 0.062691 | 0.1021 | 61.6332 | 0.22116 | 61.5599 | -0.042259 | 0.029923 | 61.5891 | -0.006014 | 61.381 | 61.4988 | 61.4829 | 61.4977 | 61.5534 | 61.6192 | 61.5312 | 61.5706 | 123.1018 | 61.6897 | 123.0284 | 61.4262 | 61.4984 | 123.0576 | 61.4625 | 122.8495 | 61.6033 | 61.6393 | 61.53 | 61.5659
2225.0625 | 123.3627 | -61.4639 | 61.6241 | 0.030283 | 0.009846 | 0.024629 | 0.084867 | 0.15529 | 0.053534 | 0.1021 | 61.6332 | 0.22116 | 61.5645 | -0.03768 | 0.029923 | 61.5891 | -0.001436 | 61.3901 | 61.4942 | 61.4738 | 61.4886 | 61.5488 | 61.6192 | 61.5175 | 61.566 | 123.0972 | 61.6851 | 123.0284 | 61.4262 | 61.4939 | 123.053 | 61.4625 | 122.8541 | 61.6033 | 61.6347 | 61.5346 | 61.5659
2226.0625 | 123.3719 | -61.4685 | 61.6562 | 0.034862 | 0.009846 | 0.033786 | 0.089445 | 0.16445 | 0.058113 | 0.10668 | 61.6332 | 0.22116 | 61.5691 | -0.033101 | 0.039079 | 61.5891 | 0.003143 | 61.3901 | 61.5034 | 61.4784 | 61.5023 | 61.558 | 61.633 | 61.5266 | 61.5752 | 123.1018 | 61.6897 | 123.0376 | 61.4354 | 61.5076 | 123.0576 | 61.4716 | 122.8586 | 61.5942 | 61.6301 | 61.53 | 61.5659
2227.0625 | 123.2895 | -61.4868 | 61.6699 | 0.034862 | 0.009846 | 0.033786 | 0.094024 | 0.15987 | 0.062691 | 0.11125 | 61.6241 | 0.21658 | 61.5691 | -0.033101 | 0.029923 | 61.5891 | -0.006014 | 61.3856 | 61.5217 | 61.4967 | 61.5206 | 61.5808 | 61.6467 | 61.5495 | 61.5981 | 123.1109 | 61.7034 | 123.0559 | 61.4537 | 61.5167 | 123.0759 | 61.4808 | 122.8724 | 61.5942 | 61.6301 | 61.5392 | 61.5751
2228.0625 | 123.3307 | -61.4822 | 61.6608 | 0.034862 | 0.014425 | 0.029208 | 0.094024 | 0.16445 | 0.058113 | 0.12041 | 61.6332 | 0.22574 | 61.5737 | -0.03768 | 0.039079 | 61.5799 | -0.006014 | 61.3947 | 61.5171 | 61.4967 | 61.5114 | 61.5763 | 61.6467 | 61.5404 | 61.6026 | 123.1155 | 61.708 | 123.0559 | 61.4446 | 61.5213 | 123.0621 | 61.4762 | 122.8769 | 61.5942 | 61.6393 | 61.5346 | 61.5797
2229.0625 | 123.3536 | -61.4731 | 61.6241 | 0.030283 | 0.009846 | 0.047522 | 0.094024 | 0.15987 | 0.058113 | 0.11583 | 61.6332 | 0.21658 | 61.5599 | -0.03768 | 0.034501 | 61.5845 | 0.003143 | 61.3856 | 61.5034 | 61.4829 | 61.5206 | 61.5671 | 61.633 | 61.5312 | 61.5889 | 123.1063 | 61.6897 | 123.033 | 61.4354 | 61.5076 | 123.0576 | 61.4762 | 122.8586 | 61.5987 | 61.6301 | 61.5254 | 61.5568
2230.0625 | 123.3948 | -61.4594 | 61.6333 | 0.030283 | 0.019004 | 0.042944 | 0.094024 | 0.16445 | 0.058113 | 0.11125 | 61.6332 | 0.21658 | 61.5645 | -0.03768 | 0.029923 | 61.5845 | -0.006014 | 61.3856 | 61.4896 | 61.4784 | 61.5023 | 61.5534 | 61.6238 | 61.5175 | 61.5706 | 123.0926 | 61.6759 | 123.0238 | 61.4217 | 61.4893 | 123.0438 | 61.4533 | 122.8449 | 61.6033 | 61.6393 | 61.5346 | 61.5705
2231.0625 | 123.4131 | -61.4868 | 61.647 | 0.034862 | 0.019004 | 0.042944 | 0.098602 | 0.15529 | 0.058113 | 0.11125 | 61.6287 | 0.22574 | 61.5645 | -0.042259 | 0.039079 | 61.5845 | 0.003143 | 61.3856 | 61.5217 | 61.5058 | 61.5298 | 61.5854 | 61.6421 | 61.5449 | 61.5981 | 123.1155 | 61.7126 | 123.0513 | 61.4446 | 61.5259 | 123.0713 | 61.49 | 122.8724 | 61.5896 | 61.6255 | 61.5254 | 61.5614
2232.0625 | 123.2758 | -61.5097 | 61.6928 | 0.03944 | 0.014425 | 0.047522 | 0.094024 | 0.15987 | 0.053534 | 0.11583 | 61.6287 | 0.21658 | 61.5691 | -0.03768 | 0.034501 | 61.5891 | -0.006014 | 61.3901 | 61.5491 | 61.5241 | 61.5572 | 61.6037 | 61.6696 | 61.5632 | 61.6255 | 123.1384 | 61.7263 | 123.0788 | 61.472 | 61.5442 | 123.0988 | 61.5037 | 122.8998 | 61.5942 | 61.6347 | 61.5346 | 61.5751
2233.0625 | 123.3444 | -61.4914 | 61.615 | 0.034862 | 0.023583 | 0.042944 | 0.10318 | 0.15987 | 0.058113 | 0.11125 | 61.6287 | 0.22574 | 61.5599 | -0.042259 | 0.039079 | 61.5891 | -0.006014 | 61.3856 | 61.5263 | 61.515 | 61.5343 | 61.5946 | 61.6513 | 61.5495 | 61.6026 | 123.1201 | 61.7171 | 123.0513 | 61.4491 | 61.5305 | 123.0804 | 61.4854 | 122.8769 | 61.5896 | 61.6347 | 61.5208 | 61.5659
2234.0625 | 123.4726 | -61.4319 | 61.6928 | 0.030283 | 0.023583 | 0.038365 | 0.089445 | 0.15987 | 0.058113 | 0.11125 | 61.6332 | 0.22116 | 61.5599 | -0.03768 | 0.029923 | 61.5845 | -0.001436 | 61.3901 | 61.4622 | 61.4555 | 61.4703 | 61.5213 | 61.5918 | 61.49 | 61.5431 | 123.0651 | 61.653 | 122.9918 | 61.3942 | 61.4618 | 123.0164 | 61.4304 | 122.822 | 61.6033 | 61.6347 | 61.53 | 61.5614
2235.0625 | 123.3902 | -61.4777 | 61.6425 | 0.03944 | 0.019004 | 0.042944 | 0.098602 | 0.16903 | 0.058113 | 0.11125 | 61.6241 | 0.22116 | 61.5691 | -0.03768 | 0.034501 | 61.5799 | -0.006014 | 61.3947 | 61.5171 | 61.4967 | 61.5206 | 61.5763 | 61.6467 | 61.5358 | 61.5889 | 123.1018 | 61.6988 | 123.0467 | 61.44 | 61.5122 | 123.0576 | 61.4716 | 122.8724 | 61.5896 | 61.6301 | 61.5346 | 61.5751
2236.0625 | 123.3582 | -61.4639 | 61.6333 | 0.034862 | 0.028162 | 0.047522 | 0.098602 | 0.16445 | 0.053534 | 0.11125 | 61.6332 | 0.22116 | 61.5645 | -0.046838 | 0.034501 | 61.5936 | 0.003143 | 61.3856 | 61.4988 | 61.4921 | 61.5115 | 61.5625 | 61.6284 | 61.5175 | 61.5752 | 123.0972 | 61.6851 | 123.0284 | 61.4171 | 61.4984 | 123.0576 | 61.4671 | 122.8495 | 61.5987 | 61.6301 | 61.53 | 61.5614
2237.0625 | 123.2895 | -61.4914 | 61.6608 | 0.03944 | 0.023583 | 0.052101 | 0.10318 | 0.1736 | 0.062691 | 0.11583 | 61.6287 | 0.22574 | 61.5645 | -0.03768 | 0.034501 | 61.5891 | -0.001436 | 61.3856 | 61.5308 | 61.515 | 61.5435 | 61.5946 | 61.665 | 61.5541 | 61.6072 | 123.1201 | 61.7171 | 123.0559 | 61.4537 | 61.5259 | 123.0804 | 61.49 | 122.8769 | 61.5942 | 61.6301 | 61.53 | 61.5659
2238.0625 | 123.2941 | -61.496 | 61.647 | 0.03944 | 0.028162 | 0.047522 | 0.098602 | 0.17818 | 0.053534 | 0.11583 | 61.6332 | 0.22574 | 61.5737 | -0.046838 | 0.039079 | 61.5845 | -0.006014 | 61.3901 | 61.5354 | 61.5241 | 61.5435 | 61.5946 | 61.6742 | 61.5495 | 61.6118 | 123.1292 | 61.7217 | 123.0696 | 61.4491 | 61.5351 | 123.0804 | 61.49 | 122.8861 | 61.5942 | 61.6393 | 61.5346 | 61.5797
2239.0625 | 123.3536 | -61.4594 | 61.6562 | 0.034862 | 0.014425 | 0.047522 | 0.098602 | 0.1736 | 0.053534 | 0.11583 | 61.6332 | 0.22574 | 61.5737 | -0.042259 | 0.043657 | 61.5936 | -0.001436 | 61.3856 | 61.4942 | 61.4738 | 61.5069 | 61.558 | 61.633 | 61.5129 | 61.5752 | 123.0926 | 61.6851 | 123.033 | 61.4171 | 61.503 | 123.053 | 61.4579 | 122.8449 | 61.5896 | 61.6347 | 61.53 | 61.5751
2240.0625 | 123.3353 | -61.4822 | 61.6562 | 0.034862 | 0.028162 | 0.042944 | 0.10318 | 0.16445 | 0.053534 | 0.12041 | 61.6241 | 0.21658 | 61.5691 | -0.03768 | 0.029923 | 61.5891 | -0.006014 | 61.3856 | 61.5171 | 61.5104 | 61.5252 | 61.5854 | 61.6467 | 61.5358 | 61.6026 | 123.1063 | 61.6988 | 123.0513 | 61.4446 | 61.5122 | 123.0713 | 61.4762 | 122.8678 | 61.5942 | 61.6301 | 61.5392 | 61.5751
2241.0625 | 123.3444 | -61.4731 | 61.6608 | 0.034862 | 0.023583 | 0.052101 | 0.10776 | 0.16903 | 0.048956 | 0.11583 | 61.6241 | 0.22574 | 61.5691 | -0.042259 | 0.039079 | 61.5845 | 0.003143 | 61.3947 | 61.5079 | 61.4967 | 61.5252 | 61.5808 | 61.6421 | 61.522 | 61.5889 | 123.0972 | 61.6988 | 123.0422 | 61.4308 | 61.5122 | 123.0576 | 61.4762 | 122.8678 | 61.585 | 61.6209 | 61.53 | 61.5659
2242.0625 | 123.3353 | -61.4822 | 61.6287 | 0.034862 | 0.028162 | 0.052101 | 0.10318 | 0.16903 | 0.062691 | 0.13414 | 61.6332 | 0.22116 | 61.5782 | -0.03768 | 0.034501 | 61.5891 | 0.003143 | 61.3856 | 61.5171 | 61.5104 | 61.5343 | 61.5854 | 61.6513 | 61.5449 | 61.6164 | 123.1155 | 61.7034 | 123.0605 | 61.4446 | 61.5167 | 123.0713 | 61.4854 | 122.8678 | 61.5987 | 61.6301 | 61.5437 | 61.5751
2243.0625 | 123.3719 | -61.4502 | 61.6333 | 0.030283 | 0.023583 | 0.052101 | 0.10776 | 0.1736 | 0.062691 | 0.12957 | 61.6332 | 0.23032 | 61.5645 | -0.033101 | 0.034501 | 61.5891 | -0.006014 | 61.3856 | 61.4805 | 61.4738 | 61.5023 | 61.558 | 61.6238 | 61.5129 | 61.5798 | 123.0834 | 61.6805 | 123.0147 | 61.4171 | 61.4847 | 123.0392 | 61.4442 | 122.8357 | 61.5987 | 61.6393 | 61.53 | 61.5705
2244.0625 | 123.4085 | -61.4548 | 61.6287 | 0.030283 | 0.03274 | 0.056679 | 0.10318 | 0.17818 | 0.058113 | 0.12499 | 61.6287 | 0.22116 | 61.5599 | -0.042259 | 0.029923 | 61.5982 | -0.010593 | 61.3856 | 61.4851 | 61.4875 | 61.5115 | 61.558 | 61.633 | 61.5129 | 61.5798 | 123.0834 | 61.6759 | 123.0147 | 61.4125 | 61.4847 | 123.053 | 61.4442 | 122.8403 | 61.5987 | 61.6393 | 61.53 | 61.5705
2245.0625 | 123.4085 | -61.4822 | 61.6104 | 0.034862 | 0.03274 | 0.052101 | 0.10318 | 0.16903 | 0.058113 | 0.13414 | 61.6332 | 0.22574 | 61.5599 | -0.03768 | 0.034501 | 61.5891 | -0.006014 | 61.381 | 61.5171 | 61.515 | 61.5343 | 61.5854 | 61.6513 | 61.5404 | 61.6164 | 123.1155 | 61.708 | 123.0422 | 61.4446 | 61.5167 | 123.0713 | 61.4762 | 122.8632 | 61.5987 | 61.6393 | 61.5254 | 61.5659
2246.0625 | 123.3765 | -61.4777 | 61.6516 | 0.03944 | 0.028162 | 0.061258 | 0.098602 | 0.16445 | 0.058113 | 0.12957 | 61.6332 | 0.22116 | 61.5691 | -0.03768 | 0.034501 | 61.5891 | 0.003143 | 61.3856 | 61.5171 | 61.5058 | 61.5389 | 61.5763 | 61.6421 | 61.5358 | 61.6072 | 123.1109 | 61.6988 | 123.0467 | 61.44 | 61.5122 | 123.0667 | 61.4808 | 122.8632 | 61.5987 | 61.6301 | 61.5346 | 61.5659
2247.0625 | 123.2986 | -61.4685 | 61.6608 | 0.030283 | 0.03274 | 0.061258 | 0.10776 | 0.1736 | 0.058113 | 0.1433 | 61.6332 | 0.22116 | 61.5645 | -0.042259 | 0.034501 | 61.5845 | -0.001436 | 61.3856 | 61.4988 | 61.5012 | 61.5298 | 61.5763 | 61.6421 | 61.5266 | 61.6118 | 123.1018 | 61.6897 | 123.033 | 61.4262 | 61.503 | 123.053 | 61.4671 | 122.8541 | 61.5987 | 61.6347 | 61.53 | 61.5659
2248.0625 | 123.4131 | -61.4914 | 61.6104 | 0.034862 | 0.03274 | 0.061258 | 0.098602 | 0.16903 | 0.048956 | 0.1433 | 61.6287 | 0.22116 | 61.5645 | -0.03768 | 0.039079 | 61.5845 | -0.001436 | 61.3901 | 61.5263 | 61.5241 | 61.5527 | 61.59 | 61.6604 | 61.5403 | 61.6347 | 123.1201 | 61.7126 | 123.0559 | 61.4537 | 61.5305 | 123.0759 | 61.49 | 122.8815 | 61.5896 | 61.6301 | 61.5254 | 61.5659
2249.0625 | 123.3902 | -61.4548 | 61.6974 | 0.034862 | 0.037319 | 0.061258 | 0.10776 | 0.17818 | 0.058113 | 0.1433 | 61.6332 | 0.21658 | 61.5645 | -0.042259 | 0.034501 | 61.5845 | -0.001436 | 61.3901 | 61.4896 | 61.4921 | 61.516 | 61.5625 | 61.633 | 61.5129 | 61.5981 | 123.088 | 61.6714 | 123.0193 | 61.4125 | 61.4893 | 123.0392 | 61.4533 | 122.8449 | 61.5987 | 61.6347 | 61.53 | 61.5659
2250.0625 | 123.436 | -61.4456 | 61.6287 | 0.034862 | 0.03274 | 0.061258 | 0.10318 | 0.16445 | 0.048956 | 0.13872 | 61.6287 | 0.22574 | 61.5645 | -0.046838 | 0.034501 | 61.5891 | 0.003143 | 61.3856 | 61.4805 | 61.4784 | 61.5069 | 61.5488 | 61.6101 | 61.4946 | 61.5843 | 123.0743 | 61.6714 | 123.0101 | 61.3988 | 61.4801 | 123.0347 | 61.4488 | 122.8312 | 61.5942 | 61.6255 | 61.53 | 61.5614
2251.0625 | 123.4222 | -61.4685 | 61.6013 | 0.034862 | 0.041898 | 0.056679 | 0.10318 | 0.16903 | 0.044377 | 0.13872 | 61.6149 | 0.22574 | 61.5462 | -0.046838 | 0.029923 | 61.5845 | -0.006014 | 61.3856 | 61.5034 | 61.5104 | 61.5252 | 61.5717 | 61.6375 | 61.5129 | 61.6072 | 123.0834 | 61.6942 | 123.0147 | 61.4217 | 61.4984 | 123.053 | 61.4625 | 122.8541 | 61.585 | 61.6209 | 61.5163 | 61.5522
2252.0625 | 123.2346 | -61.5097 | 61.6837 | 0.034862 | 0.041898 | 0.061258 | 0.10318 | 0.1736 | 0.053534 | 0.15246 | 61.6332 | 0.22574 | 61.5324 | -0.03768 | 0.029923 | 61.5845 | -0.001436 | 61.381 | 61.5446 | 61.5516 | 61.571 | 61.6129 | 61.6833 | 61.5632 | 61.6622 | 123.143 | 61.7354 | 123.0422 | 61.472 | 61.5396 | 123.0942 | 61.5083 | 122.8907 | 61.6033 | 61.6347 | 61.5025 | 61.5339
2253.0625 | 123.3994 | -61.4822 | 61.6333 | 0.034862 | 0.041898 | 0.070415 | 0.10318 | 0.16903 | 0.044377 | 0.15246 | 61.6195 | 0.21658 | 61.5233 | -0.042259 | 0.034501 | 61.5799 | -0.001436 | 61.381 | 61.5171 | 61.5241 | 61.5527 | 61.5854 | 61.6513 | 61.5266 | 61.6347 | 123.1018 | 61.6988 | 123.0055 | 61.44 | 61.5167 | 123.0621 | 61.4808 | 122.8632 | 61.585 | 61.6209 | 61.4888 | 61.5247
2254.0625 | 123.4268 | -61.4594 | 61.6333 | 0.034862 | 0.046477 | 0.070415 | 0.10776 | 0.17818 | 0.048956 | 0.15246 | 61.6332 | 0.22116 | 61.5324 | -0.042259 | 0.039079 | 61.5845 | 0.003143 | 61.381 | 61.4942 | 61.5058 | 61.5298 | 61.5671 | 61.6375 | 61.5083 | 61.6118 | 123.0926 | 61.6805 | 122.9918 | 61.4171 | 61.4984 | 123.0438 | 61.4625 | 122.8403 | 61.5942 | 61.6301 | 61.4934 | 61.5293
2255.0625 | 123.4039 | -61.4594 | 61.6196 | 0.030283 | 0.041898 | 0.079572 | 0.11234 | 0.17818 | 0.058113 | 0.15704 | 61.6241 | 0.23032 | 61.5553 | -0.046838 | 0.039079 | 61.5936 | -0.001436 | 61.3856 | 61.4896 | 61.5012 | 61.5389 | 61.5717 | 61.6375 | 61.5175 | 61.6164 | 123.0834 | 61.6897 | 123.0147 | 61.4125 | 61.4984 | 123.053 | 61.4579 | 122.8449 | 61.585 | 61.6255 | 61.5163 | 61.5568
2256.1406 | 123.3307 | -61.5143 | 61.6196 | 0.03944 | 0.051056 | 0.079572 | 0.10318 | 0.18276 | 0.062691 | 0.15704 | 61.6241 | 0.22574 | 61.5599 | -0.046838 | 0.025345 | 61.5891 | -0.010593 | 61.3856 | 61.5537 | 61.5653 | 61.5939 | 61.6175 | 61.697 | 61.577 | 61.6713 | 123.1384 | 61.74 | 123.0742 | 61.4674 | 61.5396 | 123.1033 | 61.5037 | 122.8998 | 61.5987 | 61.6347 | 61.5346 | 61.5705
2257.2188 | 123.3078 | -61.528 | 61.6608 | 0.03944 | 0.051056 | 0.070415 | 0.11234 | 0.18734 | 0.058113 | 0.16619 | 61.6332 | 0.22116 | 61.5691 | -0.033101 | 0.025345 | 61.5845 | -0.010593 | 61.3856 | 61.5675 | 61.5791 | 61.5984 | 61.6404 | 61.7154 | 61.5861 | 61.6942 | 123.1613 | 61.7492 | 123.0971 | 61.4949 | 61.5534 | 123.1125 | 61.5174 | 122.9136 | 61.6079 | 61.6438 | 61.5437 | 61.5797
2258.0625 | 123.3078 | -61.496 | 61.6608 | 0.03944 | 0.051056 | 0.074994 | 0.10776 | 0.18276 | 0.058113 | 0.17535 | 61.6332 | 0.22116 | 61.5645 | -0.03768 | 0.039079 | 61.5891 | -0.001436 | 61.3856 | 61.5354 | 61.547 | 61.571 | 61.6037 | 61.6787 | 61.5541 | 61.6713 | 123.1292 | 61.7171 | 123.0605 | 61.4583 | 61.5351 | 123.085 | 61.4945 | 122.8815 | 61.5942 | 61.6347 | 61.5254 | 61.5659
2259.125 | 123.4085 | -61.4594 | 61.6196 | 0.03944 | 0.055634 | 0.079572 | 0.10318 | 0.19192 | 0.067269 | 0.17993 | 61.6241 | 0.22574 | 61.5553 | -0.042259 | 0.029923 | 61.5936 | -0.001436 | 61.3856 | 61.4988 | 61.515 | 61.5389 | 61.5625 | 61.6513 | 61.5266 | 61.6393 | 123.0834 | 61.6851 | 123.0147 | 61.4171 | 61.4893 | 123.053 | 61.4579 | 122.8449 | 61.5942 | 61.6255 | 61.5254 | 61.5568
2260.3281 | 123.3215 | -61.496 | 61.6425 | 0.034862 | 0.060213 | 0.079572 | 0.10776 | 0.18734 | 0.067269 | 0.17535 | 61.6332 | 0.22574 | 61.5324 | -0.03768 | 0.034501 | 61.5845 | -0.010593 | 61.381 | 61.5308 | 61.5562 | 61.5755 | 61.6037 | 61.6833 | 61.5632 | 61.6713 | 123.1292 | 61.7217 | 123.0284 | 61.4583 | 61.5305 | 123.0804 | 61.4854 | 122.8769 | 61.5987 | 61.6438 | 61.4979 | 61.543
2261.1562 | 123.2803 | -61.5051 | 61.6425 | 0.034862 | 0.055634 | 0.074994 | 0.11234 | 0.18734 | 0.062691 | 0.17993 | 61.6287 | 0.22116 | 61.5324 | -0.042259 | 0.034501 | 61.5845 | -0.010593 | 61.3764 | 61.54 | 61.5608 | 61.5801 | 61.6175 | 61.6925 | 61.5678 | 61.6851 | 123.1338 | 61.7263 | 123.0376 | 61.4629 | 61.5396 | 123.0896 | 61.4945 | 122.8815 | 61.5942 | 61.6393 | 61.4979 | 61.543
2262.8594 | 123.2254 | -61.5463 | 61.5921 | 0.044018 | 0.055634 | 0.074994 | 0.10776 | 0.19649 | 0.067269 | 0.1845 | 61.6287 | 0.22574 | 61.537 | -0.042259 | 0.029923 | 61.5891 | -0.015171 | 61.381 | 61.5903 | 61.602 | 61.6213 | 61.6541 | 61.7428 | 61.6136 | 61.7308 | 123.175 | 61.7721 | 123.0834 | 61.5041 | 61.5762 | 123.1354 | 61.5312 | 122.9273 | 61.5987 | 61.6438 | 61.5071 | 61.5522
2263.3906 | 123.4085 | -61.4777 | 61.6058 | 0.030283 | 0.060213 | 0.084151 | 0.11234 | 0.19192 | 0.058113 | 0.18908 | 61.6195 | 0.21658 | 61.5508 | -0.03768 | 0.034501 | 61.5936 | -0.001436 | 61.3856 | 61.5079 | 61.5379 | 61.5618 | 61.59 | 61.6696 | 61.5358 | 61.6667 | 123.0972 | 61.6942 | 123.0284 | 61.44 | 61.5122 | 123.0713 | 61.4762 | 122.8632 | 61.585 | 61.6209 | 61.5163 | 61.5522
2264.0625 | 123.2986 | -61.4914 | 61.6379 | 0.034862 | 0.060213 | 0.079572 | 0.10776 | 0.19649 | 0.067269 | 0.20282 | 61.6332 | 0.22574 | 61.5599 | -0.03768 | 0.039079 | 61.5891 | -0.001436 | 61.3856 | 61.5263 | 61.5516 | 61.571 | 61.5992 | 61.6879 | 61.5587 | 61.6942 | 123.1246 | 61.7171 | 123.0513 | 61.4537 | 61.5305 | 123.0804 | 61.49 | 122.8769 | 61.5942 | 61.6347 | 61.5208 | 61.5614
2265.125 | 123.3719 | -61.4914 | 61.6241 | 0.034862 | 0.060213 | 0.084151 | 0.10318 | 0.20107 | 0.062691 | 0.19824 | 61.6287 | 0.22574 | 61.5599 | -0.03768 | 0.029923 | 61.5891 | -0.006014 | 61.3856 | 61.5263 | 61.5516 | 61.5755 | 61.5946 | 61.6925 | 61.5541 | 61.6896 | 123.1201 | 61.7171 | 123.0513 | 61.4537 | 61.5213 | 123.0804 | 61.4854 | 122.8769 | 61.5987 | 61.6347 | 61.53 | 61.5659
2266.0625 | 123.3902 | -61.4685 | 61.6287 | 0.030283 | 0.055634 | 0.08873 | 0.10776 | 0.20107 | 0.058113 | 0.20282 | 61.6287 | 0.22574 | 61.5737 | -0.042259 | 0.034501 | 61.5891 | -0.001436 | 61.3901 | 61.4988 | 61.5241 | 61.5572 | 61.5763 | 61.6696 | 61.5266 | 61.6713 | 123.0972 | 61.6942 | 123.0422 | 61.4262 | 61.503 | 123.0576 | 61.4671 | 122.8586 | 61.5942 | 61.6301 | 61.5392 | 61.5751
2267.0625 | 123.3994 | -61.4548 | 61.615 | 0.034862 | 0.060213 | 0.084151 | 0.10776 | 0.20107 | 0.053534 | 0.20739 | 61.6287 | 0.22116 | 61.5599 | -0.042259 | 0.034501 | 61.5936 | -0.006014 | 61.381 | 61.4896 | 61.515 | 61.5389 | 61.5625 | 61.6558 | 61.5083 | 61.6622 | 123.0834 | 61.6759 | 123.0147 | 61.4125 | 61.4893 | 123.0484 | 61.4488 | 122.8357 | 61.5942 | 61.6347 | 61.5254 | 61.5659
2268.0625 | 123.4039 | -61.4822 | 61.5967 | 0.034862 | 0.060213 | 0.084151 | 0.10318 | 0.19192 | 0.058113 | 0.20739 | 61.6241 | 0.22116 | 61.537 | -0.03768 | 0.039079 | 61.5845 | -0.006014 | 61.3764 | 61.5171 | 61.5425 | 61.5664 | 61.5854 | 61.6742 | 61.5404 | 61.6896 | 123.1063 | 61.7034 | 123.0193 | 61.4446 | 61.5213 | 123.0667 | 61.4762 | 122.8586 | 61.585 | 61.6301 | 61.4979 | 61.543
2269.0938 | 123.349 | -61.4914 | 61.5967 | 0.034862 | 0.055634 | 0.084151 | 0.10318 | 0.20107 | 0.062691 | 0.21197 | 61.6241 | 0.23032 | 61.5187 | -0.042259 | 0.029923 | 61.5936 | -0.001436 | 61.3764 | 61.5263 | 61.547 | 61.5755 | 61.5946 | 61.6925 | 61.5541 | 61.7034 | 123.1155 | 61.7217 | 123.0101 | 61.4491 | 61.5213 | 123.085 | 61.49 | 122.8678 | 61.5942 | 61.6255 | 61.4888 | 61.5202
2270.0625 | 123.3307 | -61.5005 | 61.6745 | 0.03944 | 0.064792 | 0.08873 | 0.10776 | 0.20107 | 0.062691 | 0.22113 | 61.6287 | 0.22574 | 61.5279 | -0.046838 | 0.034501 | 61.5845 | -0.001436 | 61.381 | 61.54 | 61.5653 | 61.5893 | 61.6083 | 61.7016 | 61.5632 | 61.7217 | 123.1292 | 61.7263 | 123.0284 | 61.4537 | 61.535 | 123.085 | 61.4991 | 122.8815 | 61.5942 | 61.6301 | 61.4934 | 61.5293
2271.0781 | 123.3902 | -61.4868 | 61.5738 | 0.03944 | 0.069371 | 0.093308 | 0.11234 | 0.20107 | 0.058113 | 0.23486 | 61.6241 | 0.22574 | 61.537 | -0.03768 | 0.029923 | 61.5982 | -0.006014 | 61.381 | 61.5263 | 61.5562 | 61.5801 | 61.5992 | 61.6879 | 61.5449 | 61.7217 | 123.1109 | 61.7126 | 123.0238 | 61.4491 | 61.5167 | 123.085 | 61.4808 | 122.8678 | 61.5942 | 61.6301 | 61.5071 | 61.543
2272.0625 | 123.4085 | -61.4685 | 61.5967 | 0.034862 | 0.060213 | 0.093308 | 0.11692 | 0.20107 | 0.058113 | 0.23486 | 61.6287 | 0.23032 | 61.5645 | -0.042259 | 0.039079 | 61.5936 | -0.006014 | 61.3856 | 61.5034 | 61.5287 | 61.5618 | 61.5854 | 61.6696 | 61.5266 | 61.7034 | 123.0972 | 61.6988 | 123.033 | 61.4262 | 61.5076 | 123.0621 | 61.4625 | 122.8541 | 61.5896 | 61.6347 | 61.5254 | 61.5705
2273.0781 | 123.3215 | -61.496 | 61.6104 | 0.03944 | 0.064792 | 0.08873 | 0.11234 | 0.20107 | 0.062691 | 0.23944 | 61.6287 | 0.22574 | 61.5691 | -0.042259 | 0.025345 | 61.5891 | -0.006014 | 61.3856 | 61.5354 | 61.5608 | 61.5847 | 61.6083 | 61.697 | 61.5587 | 61.7354 | 123.1246 | 61.7217 | 123.065 | 61.4537 | 61.5213 | 123.085 | 61.49 | 122.8815 | 61.6033 | 61.6347 | 61.5437 | 61.5751
2274.0625 | 123.4497 | -61.4777 | 61.6058 | 0.034862 | 0.07395 | 0.093308 | 0.11692 | 0.20107 | 0.062691 | 0.24402 | 61.6287 | 0.22574 | 61.5599 | -0.042259 | 0.029923 | 61.5891 | -0.001436 | 61.3856 | 61.5125 | 61.5516 | 61.571 | 61.5946 | 61.6787 | 61.5404 | 61.7217 | 123.1063 | 61.7034 | 123.0376 | 61.4354 | 61.5076 | 123.0667 | 61.4762 | 122.8632 | 61.5987 | 61.6301 | 61.53 | 61.5614
2275.1094 | 123.4085 | -61.4731 | 61.6196 | 0.030283 | 0.07395 | 0.084151 | 0.11234 | 0.20107 | 0.062691 | 0.2486 | 61.6241 | 0.22574 | 61.5553 | -0.033101 | 0.039079 | 61.5936 | 0.007721 | 61.3856 | 61.5034 | 61.547 | 61.5572 | 61.5854 | 61.6742 | 61.5358 | 61.7217 | 123.0972 | 61.6988 | 123.0284 | 61.44 | 61.5122 | 123.0667 | 61.4808 | 122.8586 | 61.585 | 61.6164 | 61.5163 | 61.5476
2276.0625 | 123.436 | -61.4685 | 61.5967 | 0.034862 | 0.069371 | 0.08873 | 0.11692 | 0.21023 | 0.062691 | 0.25318 | 61.6241 | 0.21658 | 61.5279 | -0.03768 | 0.034501 | 61.5891 | 0.003143 | 61.3901 | 61.5034 | 61.5379 | 61.5572 | 61.5854 | 61.6787 | 61.5312 | 61.7217 | 123.0926 | 61.6851 | 122.9964 | 61.4308 | 61.503 | 123.0576 | 61.4716 | 122.8586 | 61.5896 | 61.6209 | 61.4934 | 61.5247
2277.0938 | 123.3673 | -61.5005 | 61.6241 | 0.030283 | 0.078529 | 0.08873 | 0.11234 | 0.21023 | 0.067269 | 0.26691 | 61.6287 | 0.22574 | 61.5141 | -0.033101 | 0.034501 | 61.5982 | -0.001436 | 61.381 | 61.5308 | 61.5791 | 61.5893 | 61.6129 | 61.7108 | 61.5678 | 61.7675 | 123.1292 | 61.7263 | 123.0147 | 61.4674 | 61.535 | 123.0988 | 61.4991 | 122.8815 | 61.5942 | 61.6301 | 61.4796 | 61.5156
2278.0625 | 123.3307 | -61.4731 | 61.6241 | 0.03944 | 0.078529 | 0.10247 | 0.11692 | 0.20107 | 0.062691 | 0.27149 | 61.6195 | 0.22574 | 61.5233 | -0.042259 | 0.034501 | 61.5936 | -0.006014 | 61.3947 | 61.5125 | 61.5516 | 61.5755 | 61.59 | 61.6742 | 61.5358 | 61.7446 | 123.0926 | 61.6988 | 122.9964 | 61.4308 | 61.5076 | 123.0667 | 61.4671 | 122.8678 | 61.585 | 61.6255 | 61.4888 | 61.5293
2279.0938 | 123.3032 | -61.496 | 61.6608 | 0.034862 | 0.083107 | 0.10704 | 0.11692 | 0.21938 | 0.067269 | 0.2898 | 61.6241 | 0.21658 | 61.537 | -0.03768 | 0.034501 | 61.5891 | -0.001436 | 61.3856 | 61.5308 | 61.5791 | 61.603 | 61.6129 | 61.7154 | 61.5632 | 61.7858 | 123.1201 | 61.7126 | 123.033 | 61.4583 | 61.5305 | 123.085 | 61.4945 | 122.8815 | 61.5896 | 61.6255 | 61.5025 | 61.5385
2280.0625 | 123.2758 | -61.496 | 61.6882 | 0.03944 | 0.087686 | 0.10704 | 0.11692 | 0.20565 | 0.071848 | 0.29438 | 61.6241 | 0.22116 | 61.5599 | -0.042259 | 0.034501 | 61.5936 | -0.001436 | 61.3947 | 61.5354 | 61.5837 | 61.603 | 61.6129 | 61.7016 | 61.5678 | 61.7904 | 123.1201 | 61.7171 | 123.0559 | 61.4537 | 61.5305 | 123.0896 | 61.4945 | 122.8907 | 61.5896 | 61.6255 | 61.5254 | 61.5614
2281.0938 | 123.3673 | -61.4822 | 61.6104 | 0.03944 | 0.087686 | 0.10704 | 0.11692 | 0.2148 | 0.071848 | 0.30812 | 61.6287 | 0.23032 | 61.5599 | -0.042259 | 0.039079 | 61.5891 | -0.001436 | 61.3901 | 61.5217 | 61.5699 | 61.5893 | 61.5992 | 61.697 | 61.5541 | 61.7904 | 123.1109 | 61.7126 | 123.0422 | 61.44 | 61.5213 | 123.0713 | 61.4808 | 122.8724 | 61.5896 | 61.6301 | 61.5208 | 61.5614
2282.0625 | 123.3582 | -61.496 | 61.615 | 0.034862 | 0.087686 | 0.11162 | 0.11234 | 0.20107 | 0.067269 | 0.30354 | 61.6195 | 0.22574 | 61.5599 | -0.042259 | 0.034501 | 61.5891 | -0.006014 | 61.3901 | 61.5308 | 61.5837 | 61.6076 | 61.6083 | 61.697 | 61.5632 | 61.7995 | 123.1155 | 61.7217 | 123.0559 | 61.4537 | 61.5305 | 123.085 | 61.49 | 122.8861 | 61.585 | 61.6255 | 61.5254 | 61.5659
2283.0938 | 123.3307 | -61.4731 | 61.5738 | 0.030283 | 0.087686 | 0.1162 | 0.11234 | 0.2148 | 0.067269 | 0.31727 | 61.6287 | 0.21658 | 61.5553 | -0.033101 | 0.034501 | 61.5936 | -0.006014 | 61.381 | 61.5034 | 61.5608 | 61.5893 | 61.5854 | 61.6879 | 61.5404 | 61.7904 | 123.1018 | 61.6897 | 123.0284 | 61.44 | 61.5076 | 123.0667 | 61.4671 | 122.8541 | 61.5942 | 61.6347 | 61.5208 | 61.5614
2284.0625 | 123.3078 | -61.496 | 61.6241 | 0.034862 | 0.096844 | 0.13452 | 0.1215 | 0.2148 | 0.071848 | 0.32643 | 61.6241 | 0.22574 | 61.5416 | -0.03768 | 0.029923 | 61.5891 | -0.006014 | 61.3901 | 61.5308 | 61.5928 | 61.6305 | 61.6175 | 61.7108 | 61.5678 | 61.8224 | 123.1201 | 61.7217 | 123.0376 | 61.4583 | 61.5259 | 123.085 | 61.49 | 122.8861 | 61.5942 | 61.6301 | 61.5117 | 61.5476
2285.1094 | 123.3627 | -61.4914 | 61.5875 | 0.03944 | 0.092265 | 0.12536 | 0.1215 | 0.22396 | 0.076426 | 0.32185 | 61.6241 | 0.22574 | 61.5187 | -0.046838 | 0.029923 | 61.5891 | -0.006014 | 61.381 | 61.5308 | 61.5837 | 61.6168 | 61.6129 | 61.7154 | 61.5678 | 61.8132 | 123.1155 | 61.7171 | 123.0101 | 61.4446 | 61.5213 | 123.0804 | 61.4854 | 122.8724 | 61.5942 | 61.6301 | 61.4888 | 61.5247
2286.0625 | 123.3994 | -61.4639 | 61.6241 | 0.034862 | 0.092265 | 0.12536 | 0.11692 | 0.2148 | 0.071848 | 0.31269 | 61.6287 | 0.22574 | 61.5599 | -0.033101 | 0.034501 | 61.5936 | 0.003143 | 61.3856 | 61.4988 | 61.5562 | 61.5893 | 61.5808 | 61.6787 | 61.5358 | 61.7766 | 123.0926 | 61.6897 | 123.0238 | 61.4308 | 61.4984 | 123.0576 | 61.4671 | 122.8495 | 61.5942 | 61.6255 | 61.5254 | 61.5568
2287.0781 | 123.3215 | -61.4685 | 61.6241 | 0.034862 | 0.096844 | 0.13452 | 0.10776 | 0.21023 | 0.071848 | 0.32643 | 61.6195 | 0.22116 | 61.5599 | -0.042259 | 0.039079 | 61.5982 | -0.006014 | 61.3947 | 61.5034 | 61.5653 | 61.603 | 61.5763 | 61.6787 | 61.5404 | 61.7949 | 123.088 | 61.6897 | 123.0284 | 61.4262 | 61.5076 | 123.0667 | 61.4625 | 122.8632 | 61.5804 | 61.6255 | 61.5208 | 61.5659
2288.0625 | 123.3627 | -61.4731 | 61.6058 | 0.044018 | 0.106 | 0.14367 | 0.1215 | 0.21023 | 0.071848 | 0.34932 | 61.6195 | 0.22574 | 61.537 | -0.03768 | 0.039079 | 61.5891 | 0.007721 | 61.3901 | 61.5171 | 61.5791 | 61.6168 | 61.5946 | 61.6833 | 61.5449 | 61.8224 | 123.0926 | 61.6988 | 123.0101 | 61.4354 | 61.5122 | 123.0621 | 61.4808 | 122.8632 | 61.5804 | 61.6118 | 61.4979 | 61.5293
2289.0938 | 123.3307 | -61.5143 | 61.6379 | 0.044018 | 0.11058 | 0.14367 | 0.11234 | 0.21023 | 0.071848 | 0.35847 | 61.6287 | 0.22116 | 61.5233 | -0.03768 | 0.029923 | 61.5936 | -0.006014 | 61.3764 | 61.5583 | 61.6249 | 61.658 | 61.6266 | 61.7245 | 61.5861 | 61.8728 | 123.143 | 61.7354 | 123.0376 | 61.4766 | 61.5442 | 123.1079 | 61.5083 | 122.8907 | 61.5987 | 61.6347 | 61.4934 | 61.5293
2290.0625 | 123.2529 | -61.4777 | 61.647 | 0.044018 | 0.11516 | 0.15283 | 0.1215 | 0.2148 | 0.071848 | 0.35847 | 61.6287 | 0.22116 | 61.5599 | -0.03768 | 0.039079 | 61.5891 | -0.010593 | 61.3947 | 61.5217 | 61.5928 | 61.6305 | 61.5992 | 61.6925 | 61.5495 | 61.8361 | 123.1063 | 61.6988 | 123.0376 | 61.44 | 61.5167 | 123.0667 | 61.4671 | 122.8724 | 61.5896 | 61.6393 | 61.5208 | 61.5705
2291.0625 | 123.349 | -61.4822 | 61.6241 | 0.03944 | 0.11058 | 0.14825 | 0.1215 | 0.2148 | 0.071848 | 0.36763 | 61.6241 | 0.22574 | 61.5599 | -0.042259 | 0.039079 | 61.5891 | -0.001436 | 61.3856 | 61.5217 | 61.5928 | 61.6305 | 61.6037 | 61.697 | 61.5541 | 61.8499 | 123.1063 | 61.708 | 123.0422 | 61.44 | 61.5213 | 123.0713 | 61.4808 | 122.8678 | 61.585 | 61.6255 | 61.5208 | 61.5614
2292.0938 | 123.349 | -61.5051 | 61.6333 | 0.034862 | 0.11058 | 0.15283 | 0.11692 | 0.22396 | 0.076426 | 0.37679 | 61.6241 | 0.22574 | 61.5462 | -0.042259 | 0.034501 | 61.5891 | -0.010593 | 61.3856 | 61.54 | 61.6157 | 61.658 | 61.622 | 61.7291 | 61.5816 | 61.8819 | 123.1292 | 61.7309 | 123.0513 | 61.4629 | 61.5396 | 123.0942 | 61.4945 | 122.8907 | 61.5896 | 61.6347 | 61.5117 | 61.5568
2293.0625 | 123.3353 | -61.4822 | 61.6058 | 0.034862 | 0.11058 | 0.15283 | 0.11234 | 0.22396 | 0.076426 | 0.38137 | 61.6241 | 0.23032 | 61.5233 | -0.03768 | 0.029923 | 61.5845 | -0.001436 | 61.381 | 61.5171 | 61.5928 | 61.6351 | 61.5946 | 61.7062 | 61.5587 | 61.8636 | 123.1063 | 61.7126 | 123.0055 | 61.4446 | 61.5122 | 123.0667 | 61.4808 | 122.8632 | 61.5942 | 61.6255 | 61.4934 | 61.5247
2294.0938 | 123.3261 | -61.5005 | 61.6058 | 0.044018 | 0.106 | 0.15283 | 0.11234 | 0.21938 | 0.085583 | 0.3951 | 61.6241 | 0.23032 | 61.5462 | -0.033101 | 0.039079 | 61.5936 | -0.001436 | 61.3901 | 61.5446 | 61.6065 | 61.6534 | 61.6129 | 61.7199 | 61.5861 | 61.8956 | 123.1246 | 61.7309 | 123.0467 | 61.4674 | 61.5396 | 123.0942 | 61.4991 | 122.8907 | 61.585 | 61.6255 | 61.5071 | 61.5476
2295.0625 | 123.2895 | -61.5051 | 61.6745 | 0.030283 | 0.11516 | 0.16657 | 0.11692 | 0.22396 | 0.090161 | 0.39968 | 61.6287 | 0.23032 | 61.5553 | -0.03768 | 0.034501 | 61.5936 | -0.001436 | 61.3901 | 61.5354 | 61.6203 | 61.6717 | 61.622 | 61.7291 | 61.5953 | 61.9048 | 123.1338 | 61.7354 | 123.0605 | 61.4674 | 61.5396 | 123.0988 | 61.5037 | 122.8953 | 61.5942 | 61.6301 | 61.5208 | 61.5568
2296.0781 | 123.3719 | -61.4868 | 61.6058 | 0.034862 | 0.11516 | 0.17572 | 0.13065 | 0.21938 | 0.090161 | 0.41341 | 61.6195 | 0.22116 | 61.5553 | -0.042259 | 0.034501 | 61.5936 | -0.001436 | 61.3901 | 61.5217 | 61.602 | 61.6625 | 61.6175 | 61.7062 | 61.577 | 61.9002 | 123.1063 | 61.708 | 123.0422 | 61.4446 | 61.5213 | 123.0804 | 61.4854 | 122.8769 | 61.585 | 61.6209 | 61.5208 | 61.5568
2297.0625 | 123.4177 | -61.4639 | 61.6196 | 0.034862 | 0.11058 | 0.16657 | 0.13523 | 0.22396 | 0.085583 | 0.41799 | 61.6149 | 0.22574 | 61.5233 | -0.042259 | 0.043657 | 61.5936 | 0.003143 | 61.3856 | 61.4988 | 61.5745 | 61.6305 | 61.5992 | 61.6879 | 61.5495 | 61.8819 | 123.0789 | 61.6897 | 122.9872 | 61.4217 | 61.5076 | 123.0576 | 61.4671 | 122.8495 | 61.5713 | 61.6118 | 61.4796 | 61.5202
2298.0781 | 123.4039 | -61.4548 | 61.5921 | 0.03944 | 0.11516 | 0.1803 | 0.12607 | 0.22396 | 0.085583 | 0.44088 | 61.6241 | 0.22574 | 61.5416 | -0.03768 | 0.034501 | 61.5982 | -0.006014 | 61.3856 | 61.4942 | 61.5699 | 61.6351 | 61.5808 | 61.6787 | 61.5404 | 61.8957 | 123.0789 | 61.6805 | 122.9964 | 61.4171 | 61.4893 | 123.053 | 61.4488 | 122.8403 | 61.5896 | 61.6301 | 61.5071 | 61.5476
2299.0625 | 123.4177 | -61.4914 | 61.6058 | 0.034862 | 0.12432 | 0.20319 | 0.13523 | 0.22854 | 0.090161 | 0.46377 | 61.6287 | 0.22574 | 61.5645 | -0.03768 | 0.025345 | 61.5891 | -0.001436 | 61.3901 | 61.5263 | 61.6157 | 61.6946 | 61.6266 | 61.7199 | 61.5816 | 61.9552 | 123.1201 | 61.7171 | 123.0559 | 61.4537 | 61.5167 | 123.0804 | 61.49 | 122.8815 | 61.6033 | 61.6301 | 61.5392 | 61.5659
2300.1094 | 123.3765 | -61.5051 | 61.5967 | 0.034862 | 0.12432 | 0.21693 | 0.14439 | 0.22854 | 0.09474 | 0.46835 | 61.6195 | 0.22116 | 61.5553 | -0.042259 | 0.034501 | 61.5936 | -0.001436 | 61.3856 | 61.54 | 61.6294 | 61.7221 | 61.6495 | 61.7337 | 61.5999 | 61.9735 | 123.1246 | 61.7263 | 123.0605 | 61.4629 | 61.5396 | 123.0988 | 61.5037 | 122.8907 | 61.585 | 61.6209 | 61.5208 | 61.5568
2301.0625 | 123.3627 | -61.4822 | 61.6104 | 0.025705 | 0.11974 | 0.21235 | 0.14439 | 0.22396 | 0.09474 | 0.46835 | 61.6149 | 0.22574 | 61.5141 | -0.03768 | 0.043657 | 61.5936 | -0.010593 | 61.3856 | 61.5079 | 61.602 | 61.6946 | 61.6266 | 61.7062 | 61.577 | 61.9506 | 123.0972 | 61.708 | 122.9964 | 61.4446 | 61.5259 | 123.0759 | 61.4716 | 122.8678 | 61.5713 | 61.6255 | 61.4705 | 61.5247
2302.0781 | 123.3582 | -61.5143 | 61.5829 | 0.03944 | 0.13347 | 0.2444 | 0.15354 | 0.24227 | 0.11305 | 0.52329 | 61.6195 | 0.22116 | 61.5416 | -0.042259 | 0.039079 | 61.5891 | -0.010593 | 61.3947 | 61.5537 | 61.6478 | 61.7587 | 61.6678 | 61.7566 | 61.6273 | 62.0376 | 123.1338 | 61.7354 | 123.0559 | 61.472 | 61.5534 | 123.1033 | 61.5037 | 122.909 | 61.5804 | 61.6301 | 61.5025 | 61.5522
2303.0625 | 123.3994 | -61.4822 | 61.6241 | 0.03944 | 0.13347 | 0.25356 | 0.15354 | 0.23769 | 0.1039 | 0.55534 | 61.6149 | 0.23032 | 61.5553 | -0.03768 | 0.034501 | 61.5936 | -0.006014 | 61.3901 | 61.5217 | 61.6157 | 61.7358 | 61.6358 | 61.7199 | 61.5861 | 62.0376 | 123.0972 | 61.7126 | 123.0376 | 61.4446 | 61.5167 | 123.0759 | 61.4762 | 122.8724 | 61.5804 | 61.6209 | 61.5208 | 61.5614
2304.0781 | 123.349 | -61.5051 | 61.6013 | 0.034862 | 0.13805 | 0.27187 | 0.14897 | 0.22854 | 0.10848 | 0.56907 | 61.6149 | 0.22574 | 61.5553 | -0.033101 | 0.034501 | 61.5982 | -0.001436 | 61.3993 | 61.54 | 61.6432 | 61.777 | 61.6541 | 61.7337 | 61.6136 | 62.0742 | 123.1201 | 61.7309 | 123.0605 | 61.472 | 61.5396 | 123.1033 | 61.5037 | 122.9044 | 61.5804 | 61.6164 | 61.5208 | 61.5568
2305.0625 | 123.2986 | -61.4914 | 61.6699 | 0.034862 | 0.13347 | 0.27187 | 0.15354 | 0.23312 | 0.1039 | 0.58281 | 61.6104 | 0.22574 | 61.5141 | -0.03768 | 0.025345 | 61.5936 | -0.006014 | 61.3947 | 61.5263 | 61.6249 | 61.7633 | 61.6449 | 61.7245 | 61.5953 | 62.0742 | 123.1018 | 61.7171 | 123.0055 | 61.4537 | 61.5167 | 123.085 | 61.4854 | 122.8861 | 61.585 | 61.6164 | 61.4888 | 61.5202
2306.0781 | 123.3719 | -61.5005 | 61.5967 | 0.034862 | 0.14263 | 0.27187 | 0.15354 | 0.2148 | 0.1039 | 0.60112 | 61.6104 | 0.23032 | 61.5233 | -0.042259 | 0.029923 | 61.5936 | -0.006014 | 61.3947 | 61.5354 | 61.6432 | 61.7724 | 61.6541 | 61.7154 | 61.6044 | 62.1017 | 123.1109 | 61.7309 | 123.0238 | 61.4583 | 61.5305 | 123.0942 | 61.4945 | 122.8953 | 61.5804 | 61.6164 | 61.4934 | 61.5293
2307.0625 | 123.381 | -61.4822 | 61.6196 | 0.03944 | 0.13347 | 0.27645 | 0.14897 | 0.2148 | 0.099318 | 0.61485 | 61.6195 | 0.22116 | 61.5599 | -0.042259 | 0.034501 | 61.5891 | -0.001436 | 61.3947 | 61.5217 | 61.6157 | 61.7587 | 61.6312 | 61.697 | 61.5816 | 62.0971 | 123.1018 | 61.7034 | 123.0422 | 61.44 | 61.5167 | 123.0713 | 61.4808 | 122.8769 | 61.585 | 61.6209 | 61.5254 | 61.5614
2308.0781 | 123.3627 | -61.5051 | 61.5463 | 0.048597 | 0.14263 | 0.28103 | 0.15812 | 0.21938 | 0.099318 | 0.66521 | 61.6241 | 0.22574 | 61.5599 | -0.03768 | 0.034501 | 61.5982 | -0.001436 | 61.3993 | 61.5537 | 61.6478 | 61.7862 | 61.6633 | 61.7245 | 61.6044 | 62.1703 | 123.1292 | 61.7309 | 123.065 | 61.4674 | 61.5396 | 123.1033 | 61.5037 | 122.9044 | 61.5896 | 61.6255 | 61.5254 | 61.5614
2309.0625 | 123.3994 | -61.441 | 61.6104 | 0.044018 | 0.14721 | 0.28561 | 0.14897 | 0.22854 | 0.090161 | 0.67437 | 61.6195 | 0.22574 | 61.5233 | -0.033101 | 0.034501 | 61.5982 | -0.001436 | 61.3901 | 61.4851 | 61.5883 | 61.7266 | 61.59 | 61.6696 | 61.5312 | 62.1154 | 123.0606 | 61.6668 | 122.9643 | 61.4079 | 61.4755 | 123.0392 | 61.4396 | 122.8312 | 61.585 | 61.6209 | 61.4888 | 61.5247
2310.0938 | 123.4131 | -61.4777 | 61.5738 | 0.034862 | 0.14263 | 0.28561 | 0.15812 | 0.21938 | 0.085583 | 0.67895 | 61.6104 | 0.22574 | 61.5233 | -0.03768 | 0.025345 | 61.6028 | -0.001436 | 61.3856 | 61.5125 | 61.6203 | 61.7633 | 61.6358 | 61.697 | 61.5632 | 62.1566 | 123.088 | 61.7034 | 123.001 | 61.44 | 61.503 | 123.0804 | 61.4762 | 122.8632 | 61.585 | 61.6118 | 61.4979 | 61.5247
2311.0625 | 123.3765 | -61.4639 | 61.6013 | 0.03944 | 0.14721 | 0.29935 | 0.15354 | 0.21938 | 0.085583 | 0.69268 | 61.6195 | 0.22116 | 61.5508 | -0.03768 | 0.043657 | 61.6028 | 0.003143 | 61.3947 | 61.5034 | 61.6111 | 61.7633 | 61.6175 | 61.6833 | 61.5495 | 62.1566 | 123.0834 | 61.6851 | 123.0147 | 61.4262 | 61.5076 | 123.0667 | 61.4671 | 122.8586 | 61.5759 | 61.6164 | 61.5071 | 61.5476
2312.0938 | 123.3444 | -61.5005 | 61.615 | 0.034862 | 0.14721 | 0.28103 | 0.1627 | 0.21938 | 0.071848 | 0.71557 | 61.6149 | 0.22574 | 61.5508 | -0.042259 | 0.029923 | 61.6028 | -0.001436 | 61.3993 | 61.5354 | 61.6478 | 61.7816 | 61.6632 | 61.7199 | 61.5724 | 62.2161 | 123.1155 | 61.7263 | 123.0513 | 61.4583 | 61.5305 | 123.1033 | 61.4991 | 122.8998 | 61.585 | 61.6164 | 61.5208 | 61.5522
2313.0625 | 123.3719 | -61.4456 | 61.6241 | 0.034862 | 0.14721 | 0.28103 | 0.15354 | 0.21938 | 0.071848 | 0.72015 | 61.6195 | 0.22574 | 61.5187 | -0.042259 | 0.039079 | 61.5982 | -0.006014 | 61.3856 | 61.4805 | 61.5928 | 61.7266 | 61.5992 | 61.665 | 61.5175 | 62.1658 | 123.0651 | 61.6714 | 122.9643 | 61.4034 | 61.4847 | 123.0438 | 61.4396 | 122.8312 | 61.5804 | 61.6255 | 61.4796 | 61.5247
2314.0781 | 123.3673 | -61.4822 | 61.5967 | 0.03944 | 0.14721 | 0.2673 | 0.15354 | 0.22396 | 0.076426 | 0.73389 | 61.6241 | 0.22574 | 61.5553 | -0.042259 | 0.034501 | 61.5982 | -0.006014 | 61.3901 | 61.5217 | 61.6294 | 61.7495 | 61.6358 | 61.7062 | 61.5587 | 62.2161 | 123.1063 | 61.708 | 123.0376 | 61.44 | 61.5167 | 123.0804 | 61.4762 | 122.8724 | 61.5896 | 61.6301 | 61.5208 | 61.5614
2315.0625 | 123.317 | -61.5143 | 61.6241 | 0.034862 | 0.16553 | 0.27645 | 0.1627 | 0.23312 | 0.090161 | 0.76135 | 61.6195 | 0.22116 | 61.5508 | -0.042259 | 0.034501 | 61.5982 | -0.010593 | 61.381 | 61.5491 | 61.6798 | 61.7907 | 61.677 | 61.7474 | 61.6044 | 62.2756 | 123.1338 | 61.7354 | 123.065 | 61.472 | 61.5488 | 123.1125 | 61.5037 | 122.8953 | 61.585 | 61.6301 | 61.5163 | 61.5614
2316.0781 | 123.3994 | -61.4731 | 61.5921 | 0.034862 | 0.14721 | 0.26272 | 0.15354 | 0.2148 | 0.076426 | 0.76135 | 61.6149 | 0.22116 | 61.5187 | -0.042259 | 0.029923 | 61.5936 | -0.010593 | 61.381 | 61.5079 | 61.6203 | 61.7358 | 61.6266 | 61.6879 | 61.5495 | 62.2344 | 123.088 | 61.6942 | 122.9918 | 61.4308 | 61.503 | 123.0667 | 61.4625 | 122.8541 | 61.585 | 61.6255 | 61.4888 | 61.5293
2317.0625 | 123.3627 | -61.4777 | 61.6241 | 0.030283 | 0.15179 | 0.25814 | 0.15354 | 0.21938 | 0.081005 | 0.78882 | 61.6287 | 0.22574 | 61.5462 | -0.042259 | 0.043657 | 61.5982 | -0.010593 | 61.3901 | 61.5079 | 61.6295 | 61.7358 | 61.6312 | 61.697 | 61.5587 | 62.2665 | 123.1063 | 61.7034 | 123.0238 | 61.4354 | 61.5213 | 123.0759 | 61.4671 | 122.8678 | 61.585 | 61.6393 | 61.5025 | 61.5568
2318.0938 | 123.381 | -61.4548 | 61.6058 | 0.034862 | 0.15637 | 0.24898 | 0.16728 | 0.21938 | 0.076426 | 0.79798 | 61.6195 | 0.22574 | 61.5233 | -0.03768 | 0.025345 | 61.5845 | -0.006014 | 61.3901 | 61.4896 | 61.6111 | 61.7038 | 61.6221 | 61.6742 | 61.5312 | 62.2528 | 123.0743 | 61.6805 | 122.9781 | 61.4171 | 61.4801 | 123.0392 | 61.4488 | 122.8449 | 61.5942 | 61.6255 | 61.4979 | 61.5293
2319.0625 | 123.3994 | -61.4639 | 61.6241 | 0.03944 | 0.17468 | 0.2673 | 0.17186 | 0.22396 | 0.1451 | 0.83461 | 61.6241 | 0.23032 | 61.537 | -0.046838 | 0.039079 | 61.6028 | -0.006014 | 61.3901 | 61.5034 | 61.6386 | 61.7312 | 61.6358 | 61.6879 | 61.609 | 62.2985 | 123.088 | 61.6942 | 123.001 | 61.4171 | 61.503 | 123.0667 | 61.4579 | 122.8541 | 61.585 | 61.6301 | 61.4979 | 61.543
2320.0938 | 123.2758 | -61.5005 | 61.647 | 0.03944 | 0.17926 | 0.28103 | 0.1627 | 0.23769 | 0.17715 | 0.87123 | 61.6241 | 0.23032 | 61.5553 | -0.033101 | 0.039079 | 61.5982 | -0.001436 | 61.3947 | 61.54 | 61.6798 | 61.7816 | 61.6632 | 61.7382 | 61.6777 | 62.3718 | 123.1246 | 61.7309 | 123.0559 | 61.4674 | 61.5396 | 123.0988 | 61.4991 | 122.8953 | 61.585 | 61.6255 | 61.5163 | 61.5568
2321.0625 | 123.4268 | -61.4731 | 61.6379 | 0.044018 | 0.17926 | 0.28561 | 0.16728 | 0.22396 | 0.18631 | 0.88039 | 61.6195 | 0.22574 | 61.5187 | -0.046838 | 0.039079 | 61.5982 | -0.006014 | 61.3856 | 61.5171 | 61.6523 | 61.7587 | 61.6404 | 61.697 | 61.6594 | 62.3535 | 123.0926 | 61.6988 | 122.9918 | 61.4262 | 61.5122 | 123.0713 | 61.4671 | 122.8586 | 61.5804 | 61.6255 | 61.4796 | 61.5247
2322.0781 | 123.4177 | -61.496 | 61.5921 | 0.044018 | 0.17468 | 0.27187 | 0.1627 | 0.22396 | 0.18631 | 0.88039 | 61.6149 | 0.23032 | 61.5508 | -0.03768 | 0.025345 | 61.6028 | -0.006014 | 61.3856 | 61.54 | 61.6707 | 61.7678 | 61.6587 | 61.7199 | 61.6823 | 62.3764 | 123.1109 | 61.7263 | 123.0467 | 61.4583 | 61.5213 | 123.0988 | 61.49 | 122.8815 | 61.5896 | 61.6209 | 61.5254 | 61.5568
2323.0625 | 123.4268 | -61.4914 | 61.6104 | 0.03944 | 0.17468 | 0.25356 | 0.17186 | 0.22854 | 0.18173 | 1.3748 | 61.6104 | 0.22574 | 61.5462 | -0.033101 | 0.029923 | 61.6028 | -0.001436 | 61.4084 | 61.5308 | 61.6661 | 61.745 | 61.6633 | 61.7199 | 61.6731 | 62.8662 | 123.1018 | 61.7171 | 123.0376 | 61.4583 | 61.5213 | 123.0942 | 61.49 | 122.8998 | 61.5804 | 61.6118 | 61.5163 | 61.5476
2324.0938 | 123.3719 | -61.4914 | 61.5784 | 0.044018 | 0.18384 | 0.25814 | 0.17644 | 0.23312 | 0.20462 | 1.2283 | 61.6149 | 0.22574 | 61.5096 | -0.042259 | 0.039079 | 61.6028 | -0.001436 | 61.3947 | 61.5354 | 61.6752 | 61.7495 | 61.6678 | 61.7245 | 61.696 | 62.7197 | 123.1063 | 61.7171 | 123.001 | 61.4491 | 61.5305 | 123.0942 | 61.49 | 122.8861 | 61.5759 | 61.6164 | 61.4705 | 61.511
2325.0625 | 123.3307 | -61.4731 | 61.6287 | 0.034862 | 0.18842 | 0.25356 | 0.17186 | 0.24685 | 0.22293 | 1.1322 | 61.6149 | 0.23032 | 61.5508 | -0.03768 | 0.029923 | 61.5936 | 0.003143 | 61.4084 | 61.5079 | 61.6615 | 61.7266 | 61.6449 | 61.7199 | 61.696 | 62.6053 | 123.088 | 61.7034 | 123.0238 | 61.4354 | 61.503 | 123.0667 | 61.4762 | 122.8815 | 61.585 | 61.6118 | 61.5208 | 61.5476
2326.0781 | 123.262 | -61.5234 | 61.615 | 0.044018 | 0.18384 | 0.25814 | 0.18102 | 0.22854 | 0.21836 | 1.329 | 61.6104 | 0.22574 | 61.5462 | -0.042259 | 0.029923 | 61.5982 | 0.003143 | 61.3901 | 61.5675 | 61.7073 | 61.7816 | 61.7045 | 61.752 | 61.7418 | 62.8525 | 123.1338 | 61.7492 | 123.0696 | 61.4812 | 61.5534 | 123.1216 | 61.5266 | 122.9136 | 61.5804 | 61.6072 | 61.5163 | 61.543
2327.0625 | 123.3536 | -61.4914 | 61.6058 | 0.034862 | 0.18842 | 0.27645 | 0.19017 | 0.24227 | 0.2092 | 1.7136 | 61.6058 | 0.22574 | 61.5004 | -0.03768 | 0.034501 | 61.6028 | -0.001436 | 61.3947 | 61.5263 | 61.6798 | 61.7678 | 61.6816 | 61.7337 | 61.7006 | 63.205 | 123.0972 | 61.7171 | 122.9918 | 61.4537 | 61.5259 | 123.0942 | 61.49 | 122.8861 | 61.5713 | 61.6072 | 61.4659 | 61.5018
2328.0781 | 123.381 | -61.4868 | 61.5829 | 0.044018 | 0.193 | 0.25356 | 0.17186 | 0.23769 | 0.23209 | 1.1642 | 61.6104 | 0.22574 | 61.5416 | -0.046838 | 0.029923 | 61.5936 | -0.001436 | 61.3993 | 61.5308 | 61.6798 | 61.7404 | 61.6587 | 61.7245 | 61.7189 | 62.651 | 123.0972 | 61.7126 | 123.0284 | 61.44 | 61.5167 | 123.0804 | 61.4854 | 122.8861 | 61.5804 | 61.6118 | 61.5117 | 61.543
2329.0625 | 123.3444 | -61.5143 | 61.6241 | 0.034862 | 0.22047 | 0.29019 | 0.19017 | 0.26059 | 0.23667 | 1.1734 | 61.6195 | 0.22574 | 61.5462 | -0.03768 | 0.034501 | 61.6074 | -0.001436 | 61.4039 | 61.5491 | 61.7348 | 61.8045 | 61.7045 | 61.7749 | 61.751 | 62.6877 | 123.1338 | 61.74 | 123.0605 | 61.4766 | 61.5488 | 123.1216 | 61.5128 | 122.9181 | 61.585 | 61.6209 | 61.5117 | 61.5476
2330.0625 | 123.3398 | -61.4822 | 61.6241 | 0.03944 | 0.22505 | 0.26272 | 0.19017 | 0.25601 | 0.24125 | 1.1825 | 61.6104 | 0.23032 | 61.5187 | -0.042259 | 0.034501 | 61.6028 | 0.003143 | 61.4039 | 61.5217 | 61.7073 | 61.745 | 61.6724 | 61.7382 | 61.7235 | 62.6648 | 123.0926 | 61.7126 | 123.001 | 61.44 | 61.5167 | 123.085 | 61.4854 | 122.8861 | 61.5759 | 61.6072 | 61.4842 | 61.5156
2331.0781 | 123.2666 | -61.5097 | 61.5967 | 0.044018 | 0.22047 | 0.27187 | 0.19933 | 0.26059 | 0.2504 | 1.5259 | 61.6058 | 0.22116 | 61.5416 | -0.051417 | 0.029923 | 61.6119 | -0.006014 | 61.4039 | 61.5537 | 61.7302 | 61.7816 | 61.709 | 61.7703 | 61.7601 | 63.0356 | 123.1155 | 61.7309 | 123.0513 | 61.4583 | 61.5396 | 123.1216 | 61.5037 | 122.9136 | 61.5759 | 61.6118 | 61.5117 | 61.5476
2332.0625 | 123.3719 | -61.5005 | 61.5829 | 0.034862 | 0.22047 | 0.27645 | 0.20391 | 0.25143 | 0.24125 | 1.8418 | 61.6104 | 0.22574 | 61.5462 | -0.042259 | 0.029923 | 61.6119 | -0.010593 | 61.4084 | 61.5354 | 61.721 | 61.777 | 61.7045 | 61.752 | 61.7418 | 63.3424 | 123.1109 | 61.7263 | 123.0467 | 61.4583 | 61.5305 | 123.1125 | 61.49 | 122.909 | 61.5804 | 61.6209 | 61.5163 | 61.5568
2333.0938 | 123.2895 | -61.528 | 61.647 | 0.03944 | 0.21131 | 0.27187 | 0.19933 | 0.24685 | 0.23209 | 1.8372 | 61.6104 | 0.23032 | 61.5187 | -0.03768 | 0.029923 | 61.6119 | -0.006014 | 61.3993 | 61.5675 | 61.7393 | 61.7999 | 61.7273 | 61.7749 | 61.7601 | 63.3652 | 123.1384 | 61.7583 | 123.0467 | 61.4903 | 61.5579 | 123.14 | 61.522 | 122.9273 | 61.5804 | 61.6164 | 61.4888 | 61.5247
2334.0625 | 123.3673 | -61.5097 | 61.5829 | 0.044018 | 0.19758 | 0.27645 | 0.19475 | 0.25143 | 0.21836 | 1.7182 | 61.6058 | 0.22574 | 61.5416 | -0.03768 | 0.034501 | 61.6119 | -0.001436 | 61.4039 | 61.5537 | 61.7073 | 61.7862 | 61.7045 | 61.7611 | 61.7281 | 63.2279 | 123.1155 | 61.7354 | 123.0513 | 61.472 | 61.5442 | 123.1216 | 61.5083 | 122.9136 | 61.5713 | 61.6072 | 61.5071 | 61.543
2335.1094 | 123.3353 | -61.5051 | 61.6562 | 0.044018 | 0.21131 | 0.27645 | 0.19017 | 0.25601 | 0.23667 | 1.6633 | 61.6149 | 0.22116 | 61.5508 | -0.03768 | 0.034501 | 61.6074 | -0.010593 | 61.3993 | 61.5491 | 61.7164 | 61.7816 | 61.6953 | 61.7611 | 61.7418 | 63.1684 | 123.1201 | 61.7263 | 123.0559 | 61.4674 | 61.5396 | 123.1125 | 61.4945 | 122.9044 | 61.5804 | 61.6255 | 61.5163 | 61.5614
2336.0625 | 123.3627 | -61.5005 | 61.5829 | 0.034862 | 0.21131 | 0.27645 | 0.19017 | 0.26059 | 0.24583 | 1.677 | 61.6104 | 0.23032 | 61.5096 | -0.042259 | 0.039079 | 61.6028 | -0.001436 | 61.3947 | 61.5354 | 61.7119 | 61.777 | 61.6907 | 61.7611 | 61.7464 | 63.1775 | 123.1109 | 61.7309 | 123.0101 | 61.4583 | 61.5396 | 123.1033 | 61.4991 | 122.8953 | 61.5713 | 61.6118 | 61.4705 | 61.511
2337.0781 | 123.3124 | -61.4914 | 61.6241 | 0.048597 | 0.20216 | 0.24898 | 0.18559 | 0.25601 | 0.22751 | 1.5442 | 61.6149 | 0.22574 | 61.5416 | -0.042259 | 0.029923 | 61.6119 | -0.006014 | 61.413 | 61.54 | 61.6936 | 61.7404 | 61.677 | 61.7474 | 61.7189 | 63.0356 | 123.1063 | 61.7171 | 123.033 | 61.4491 | 61.5213 | 123.1033 | 61.4854 | 122.9044 | 61.585 | 61.6209 | 61.5117 | 61.5476
2338.0625 | 123.3215 | -61.5372 | 61.6241 | 0.044018 | 0.18384 | 0.23982 | 0.18559 | 0.25143 | 0.21836 | 1.4801 | 61.6104 | 0.22574 | 61.5416 | -0.042259 | 0.029923 | 61.6028 | -0.001436 | 61.3993 | 61.5812 | 61.721 | 61.777 | 61.7228 | 61.7886 | 61.7555 | 63.0173 | 123.1475 | 61.7629 | 123.0788 | 61.4949 | 61.5671 | 123.14 | 61.5357 | 122.9365 | 61.5804 | 61.6118 | 61.5117 | 61.543
2339.0938 | 123.3032 | -61.5005 | 61.6425 | 0.03944 | 0.17468 | 0.23982 | 0.19017 | 0.25143 | 0.22751 | 1.4893 | 61.6195 | 0.23032 | 61.5096 | -0.033101 | 0.029923 | 61.5982 | 0.003143 | 61.3993 | 61.54 | 61.6752 | 61.7404 | 61.6907 | 61.752 | 61.7281 | 62.9898 | 123.1201 | 61.7309 | 123.0101 | 61.4674 | 61.5305 | 123.0988 | 61.5037 | 122.8998 | 61.5896 | 61.6164 | 61.4796 | 61.5064
2340.0625 | 123.3765 | -61.5097 | 61.615 | 0.030283 | 0.17011 | 0.28561 | 0.18559 | 0.25601 | 0.20462 | 1.4115 | 61.6104 | 0.22574 | 61.5508 | -0.042259 | 0.034501 | 61.6119 | -0.006014 | 61.3993 | 61.54 | 61.6798 | 61.7953 | 61.6953 | 61.7657 | 61.7143 | 62.9212 | 123.1201 | 61.7354 | 123.0605 | 61.4674 | 61.5442 | 123.1216 | 61.5037 | 122.909 | 61.5759 | 61.6164 | 61.5163 | 61.5568
2341.0781 | 123.2437 | -61.5097 | 61.6425 | 0.03944 | 0.193 | 0.25814 | 0.20849 | 0.26974 | 0.24125 | 1.7273 | 61.6058 | 0.23032 | 61.5141 | -0.042259 | 0.039079 | 61.6074 | -0.006014 | 61.3993 | 61.5491 | 61.7027 | 61.7678 | 61.7182 | 61.7794 | 61.751 | 63.2371 | 123.1155 | 61.74 | 123.0238 | 61.4674 | 61.5488 | 123.1171 | 61.5037 | 122.909 | 61.5667 | 61.6118 | 61.4751 | 61.5202
2342.0625 | 123.2758 | -61.5326 | 61.6379 | 0.03944 | 0.19758 | 0.25814 | 0.20849 | 0.26974 | 0.24583 | 1.6816 | 61.6104 | 0.22116 | 61.5462 | -0.03768 | 0.029923 | 61.6028 | 0.003143 | 61.4084 | 61.572 | 61.7302 | 61.7907 | 61.7411 | 61.8023 | 61.7784 | 63.2142 | 123.1429 | 61.7538 | 123.0788 | 61.4949 | 61.5625 | 123.1354 | 61.5357 | 122.941 | 61.5804 | 61.6072 | 61.5163 | 61.543
2343.0781 | 123.2529 | -61.528 | 61.6653 | 0.03944 | 0.18384 | 0.25356 | 0.21307 | 0.26059 | 0.23209 | 1.558 | 61.6149 | 0.22116 | 61.5233 | -0.042259 | 0.034501 | 61.6074 | -0.006014 | 61.4039 | 61.5675 | 61.7119 | 61.7816 | 61.7411 | 61.7886 | 61.7601 | 63.086 | 123.1429 | 61.7492 | 123.0513 | 61.4858 | 61.5625 | 123.1354 | 61.522 | 122.9319 | 61.5804 | 61.6209 | 61.4888 | 61.5293
2344.0625 | 123.3627 | -61.5372 | 61.6837 | 0.03944 | 0.20674 | 0.2444 | 0.20391 | 0.26974 | 0.22293 | 1.2558 | 61.6149 | 0.22574 | 61.5324 | -0.042259 | 0.039079 | 61.5982 | -0.001436 | 61.3993 | 61.5766 | 61.7439 | 61.7816 | 61.7411 | 61.8069 | 61.7601 | 62.793 | 123.1521 | 61.7629 | 123.0696 | 61.4949 | 61.5762 | 123.1354 | 61.5357 | 122.9365 | 61.5759 | 61.6164 | 61.4934 | 61.5339
2345.1094 | 123.3078 | -61.4914 | 61.6608 | 0.034862 | 0.19758 | 0.2444 | 0.19933 | 0.26059 | 0.21378 | 1.1642 | 61.6241 | 0.22574 | 61.5508 | -0.042259 | 0.034501 | 61.6028 | -0.001436 | 61.3993 | 61.5263 | 61.689 | 61.7358 | 61.6907 | 61.752 | 61.7052 | 62.6556 | 123.1155 | 61.7171 | 123.0422 | 61.4491 | 61.5259 | 123.0942 | 61.49 | 122.8907 | 61.5896 | 61.6255 | 61.5163 | 61.5522
2346.0625 | 123.2666 | -61.5234 | 61.6562 | 0.03944 | 0.193 | 0.24898 | 0.20391 | 0.26059 | 0.21836 | 1.2787 | 61.6149 | 0.22574 | 61.5096 | -0.03768 | 0.034501 | 61.6028 | -0.006014 | 61.3993 | 61.5629 | 61.7164 | 61.7724 | 61.7273 | 61.784 | 61.7418 | 62.8021 | 123.1384 | 61.7492 | 123.033 | 61.4858 | 61.5579 | 123.1262 | 61.5174 | 122.9227 | 61.5804 | 61.6209 | 61.4751 | 61.5156
2347.0781 | 123.262 | -61.5005 | 61.6516 | 0.044018 | 0.20674 | 0.24898 | 0.19933 | 0.26059 | 0.2504 | 1.3016 | 61.6241 | 0.22116 | 61.5508 | -0.03768 | 0.034501 | 61.6119 | -0.001436 | 61.3993 | 61.5446 | 61.7073 | 61.7495 | 61.6999 | 61.7611 | 61.751 | 62.8021 | 123.1246 | 61.7217 | 123.0513 | 61.4629 | 61.535 | 123.1125 | 61.4991 | 122.8998 | 61.5896 | 61.6255 | 61.5163 | 61.5522
2348.0625 | 123.2437 | -61.528 | 61.6562 | 0.048597 | 0.25252 | 0.28103 | 0.21764 | 0.26059 | 0.27787 | 1.3657 | 61.6149 | 0.22116 | 61.5416 | -0.042259 | 0.034501 | 61.6074 | -0.006014 | 61.4039 | 61.5766 | 61.7805 | 61.809 | 61.7457 | 61.7886 | 61.8059 | 62.8937 | 123.1429 | 61.7492 | 123.0696 | 61.4858 | 61.5625 | 123.1354 | 61.522 | 122.9319 | 61.5804 | 61.6209 | 61.5071 | 61.5476
2349.0938 | 123.3307 | -61.4868 | 61.647 | 0.03944 | 0.23879 | 0.25356 | 0.21307 | 0.24227 | 0.26414 | 1.3428 | 61.6149 | 0.22116 | 61.5141 | -0.03768 | 0.039079 | 61.6074 | -0.001436 | 61.3947 | 61.5263 | 61.7256 | 61.7404 | 61.6999 | 61.7291 | 61.751 | 62.8296 | 123.1017 | 61.708 | 123.001 | 61.4491 | 61.5259 | 123.0942 | 61.4854 | 122.8815 | 61.5759 | 61.6164 | 61.4751 | 61.5156
2350.0625 | 123.3673 | -61.5051 | 61.5692 | 0.030283 | 0.25252 | 0.25814 | 0.22222 | 0.24685 | 0.26414 | 1.4206 | 61.6241 | 0.21658 | 61.5462 | -0.03768 | 0.029923 | 61.6028 | 0.003143 | 61.4039 | 61.5354 | 61.7577 | 61.7633 | 61.7273 | 61.752 | 61.7693 | 62.9257 | 123.1292 | 61.7217 | 123.0513 | 61.4674 | 61.535 | 123.1079 | 61.5083 | 122.909 | 61.5942 | 61.6209 | 61.5163 | 61.543
2351.0781 | 123.3078 | -61.5143 | 61.6287 | 0.044018 | 0.23879 | 0.23525 | 0.21764 | 0.24685 | 0.26414 | 1.5076 | 61.6149 | 0.22574 | 61.5141 | -0.03768 | 0.034501 | 61.6119 | -0.001436 | 61.3993 | 61.5583 | 61.7531 | 61.7495 | 61.7319 | 61.7611 | 61.7784 | 63.0219 | 123.1292 | 61.74 | 123.0284 | 61.4766 | 61.5488 | 123.1262 | 61.5128 | 122.9136 | 61.5804 | 61.6164 | 61.4796 | 61.5156
2352.0625 | 123.2346 | -61.5097 | 61.6241 | 0.044018 | 0.25252 | 0.25814 | 0.2268 | 0.25601 | 0.28703 | 1.4847 | 61.6104 | 0.23032 | 61.5553 | -0.033101 | 0.034501 | 61.6119 | 0.003143 | 61.4039 | 61.5537 | 61.7622 | 61.7678 | 61.7365 | 61.7657 | 61.7967 | 62.9944 | 123.1201 | 61.74 | 123.065 | 61.4766 | 61.5442 | 123.1216 | 61.5128 | 122.9136 | 61.5759 | 61.6072 | 61.5208 | 61.5522
2353.0938 | 123.3032 | -61.5005 | 61.6608 | 0.034862 | 0.22505 | 0.2444 | 0.2268 | 0.24685 | 0.25956 | 1.4572 | 61.6149 | 0.22574 | 61.5279 | -0.042259 | 0.034501 | 61.6074 | -0.001436 | 61.4039 | 61.5354 | 61.7256 | 61.745 | 61.7273 | 61.7474 | 61.7601 | 62.9578 | 123.1155 | 61.7263 | 123.0284 | 61.4583 | 61.535 | 123.1079 | 61.4991 | 122.9044 | 61.5804 | 61.6164 | 61.4934 | 61.5293
2354.0625 | 123.2437 | -61.528 | 61.6379 | 0.044018 | 0.22963 | 0.24898 | 0.23138 | 0.24227 | 0.26872 | 1.471 | 61.6104 | 0.23032 | 61.5324 | -0.042259 | 0.029923 | 61.6028 | -0.001436 | 61.3947 | 61.572 | 61.7576 | 61.777 | 61.7594 | 61.7703 | 61.7967 | 62.999 | 123.1384 | 61.7583 | 123.0605 | 61.4858 | 61.5579 | 123.1308 | 61.5266 | 122.9227 | 61.5804 | 61.6118 | 61.5025 | 61.5339
2355.0938 | 123.3536 | -61.4914 | 61.6196 | 0.034862 | 0.25252 | 0.25356 | 0.24511 | 0.25143 | 0.29161 | 1.5305 | 61.6149 | 0.2349 | 61.5508 | -0.03768 | 0.029923 | 61.6119 | -0.006014 | 61.4084 | 61.5263 | 61.7439 | 61.745 | 61.7365 | 61.7428 | 61.783 | 63.0219 | 123.1063 | 61.7263 | 123.0422 | 61.4537 | 61.5213 | 123.1033 | 61.4854 | 122.8998 | 61.585 | 61.6209 | 61.5208 | 61.5568
2356.0625 | 123.2941 | -61.5234 | 61.6196 | 0.034862 | 0.23879 | 0.25356 | 0.26343 | 0.25601 | 0.29619 | 1.5992 | 61.6104 | 0.22116 | 61.5187 | -0.03768 | 0.029923 | 61.6074 | -0.006014 | 61.4084 | 61.5583 | 61.7622 | 61.777 | 61.7869 | 61.7794 | 61.8196 | 63.1226 | 123.1338 | 61.7446 | 123.0422 | 61.4858 | 61.5534 | 123.1308 | 61.5174 | 122.9319 | 61.5804 | 61.6164 | 61.4888 | 61.5247
2357.0781 | 123.2941 | -61.5143 | 61.6608 | 0.03944 | 0.26168 | 0.28103 | 0.28632 | 0.26059 | 0.34655 | 1.6953 | 61.6104 | 0.22574 | 61.5324 | -0.03768 | 0.043657 | 61.6119 | 0.003143 | 61.4084 | 61.5537 | 61.776 | 61.7953 | 61.8006 | 61.7749 | 61.8608 | 63.2096 | 123.1246 | 61.74 | 123.0467 | 61.4766 | 61.5579 | 123.1262 | 61.5174 | 122.9227 | 61.5667 | 61.6072 | 61.4888 | 61.5293
2358.0625 | 123.2574 | -61.5234 | 61.5967 | 0.034862 | 0.27542 | 0.28103 | 0.30463 | 0.26974 | 0.33739 | 1.5808 | 61.6149 | 0.22574 | 61.5462 | -0.042259 | 0.039079 | 61.5982 | -0.010593 | 61.413 | 61.5583 | 61.7989 | 61.8045 | 61.8281 | 61.7932 | 61.8608 | 63.1043 | 123.1384 | 61.7492 | 123.0696 | 61.4812 | 61.5625 | 123.1216 | 61.5128 | 122.9365 | 61.5759 | 61.6255 | 61.5071 | 61.5568
2359.0938 | 123.3215 | -61.5097 | 61.6516 | 0.03944 | 0.27084 | 0.27645 | 0.30006 | 0.26059 | 0.30992 | 2.4965 | 61.5966 | 0.23032 | 61.5141 | -0.051417 | 0.029923 | 61.6074 | 0.003143 | 61.4084 | 61.5491 | 61.7805 | 61.7862 | 61.8098 | 61.7703 | 61.8196 | 64.0062 | 123.1063 | 61.74 | 123.0238 | 61.4583 | 61.5396 | 123.1171 | 61.5128 | 122.9181 | 61.5667 | 61.5935 | 61.4842 | 61.511
2360.0625 | 123.381 | -61.5234 | 61.5692 | 0.034862 | 0.24794 | 0.26272 | 0.30006 | 0.25601 | 0.28703 | 3.3801 | 61.6012 | 0.22574 | 61.5279 | -0.046838 | 0.029923 | 61.6303 | -0.001436 | 61.4176 | 61.5583 | 61.7714 | 61.7862 | 61.8235 | 61.7794 | 61.8105 | 64.9035 | 123.1246 | 61.7492 | 123.0513 | 61.4766 | 61.5534 | 123.1537 | 61.522 | 122.941 | 61.5713 | 61.6026 | 61.4979 | 61.5293
2361.0781 | 123.3124 | -61.5326 | 61.6241 | 0.03944 | 0.23879 | 0.25814 | 0.30463 | 0.25601 | 0.28245 | 3.4075 | 61.5966 | 0.22574 | 61.5233 | -0.033101 | 0.034501 | 61.6211 | 0.003143 | 61.4222 | 61.572 | 61.7714 | 61.7907 | 61.8372 | 61.7886 | 61.815 | 64.9401 | 123.1292 | 61.7583 | 123.0559 | 61.4995 | 61.5671 | 123.1537 | 61.5357 | 122.9548 | 61.5621 | 61.5935 | 61.4888 | 61.5202
2362.0625 | 123.2849 | -61.5417 | 61.6104 | 0.03944 | 0.22505 | 0.27187 | 0.31379 | 0.25143 | 0.30992 | 3.4442 | 61.5875 | 0.22574 | 61.505 | -0.03768 | 0.034501 | 61.6211 | -0.001436 | 61.413 | 61.5812 | 61.7668 | 61.8136 | 61.8555 | 61.7932 | 61.8517 | 64.9859 | 123.1292 | 61.7675 | 123.0467 | 61.5041 | 61.5762 | 123.1628 | 61.5403 | 122.9548 | 61.553 | 61.5889 | 61.4705 | 61.5064
2363.0938 | 123.2941 | -61.4777 | 61.647 | 0.044018 | 0.23421 | 0.27645 | 0.32295 | 0.26516 | 0.30535 | 3.1374 | 61.6058 | 0.22574 | 61.537 | -0.042259 | 0.034501 | 61.6211 | -0.010593 | 61.4084 | 61.5217 | 61.7119 | 61.7541 | 61.8006 | 61.7428 | 61.783 | 64.6151 | 123.0834 | 61.7034 | 123.0147 | 61.4354 | 61.5122 | 123.0988 | 61.4671 | 122.8861 | 61.5713 | 61.6164 | 61.5025 | 61.5476
2364.0625 | 123.2758 | -61.5601 | 61.615 | 0.044018 | 0.23421 | 0.2673 | 0.34126 | 0.26974 | 0.3145 | 3.0825 | 61.6012 | 0.22574 | 61.5141 | -0.042259 | 0.034501 | 61.6165 | -0.001436 | 61.413 | 61.6041 | 61.7943 | 61.8274 | 61.9013 | 61.8298 | 61.8746 | 64.6425 | 123.1613 | 61.7858 | 123.0742 | 61.5178 | 61.5946 | 123.1766 | 61.5586 | 122.9731 | 61.5667 | 61.6026 | 61.4796 | 61.5156
2365.0938 | 123.2529 | -61.5005 | 61.6608 | 0.03944 | 0.24337 | 0.28103 | 0.34584 | 0.26974 | 0.32824 | 3.1969 | 61.5966 | 0.23032 | 61.5004 | -0.033101 | 0.029923 | 61.6165 | -0.001436 | 61.4222 | 61.54 | 61.7439 | 61.7816 | 61.8464 | 61.7703 | 61.8288 | 64.6975 | 123.0972 | 61.7309 | 123.0009 | 61.4674 | 61.5305 | 123.1171 | 61.4991 | 122.9227 | 61.5667 | 61.5981 | 61.4705 | 61.5018
2366.0625 | 123.2346 | -61.5326 | 61.5921 | 0.044018 | 0.26168 | 0.28561 | 0.355 | 0.26974 | 0.33282 | 3.6319 | 61.5966 | 0.22574 | 61.5324 | -0.03768 | 0.039079 | 61.6211 | -0.001436 | 61.4222 | 61.5766 | 61.7943 | 61.8182 | 61.8876 | 61.8023 | 61.8654 | 65.1645 | 123.1292 | 61.7583 | 123.065 | 61.4949 | 61.5717 | 123.1537 | 61.5312 | 122.9548 | 61.5575 | 61.5981 | 61.4934 | 61.5339
2367.0781 | 123.3032 | -61.528 | 61.6379 | 0.044018 | 0.24794 | 0.27187 | 0.355 | 0.26059 | 0.32366 | 3.5632 | 61.5829 | 0.23032 | 61.4958 | -0.03768 | 0.048236 | 61.6257 | -0.001436 | 61.413 | 61.572 | 61.776 | 61.7999 | 61.883 | 61.7886 | 61.8517 | 65.0912 | 123.1109 | 61.7583 | 123.0238 | 61.4903 | 61.5763 | 123.1537 | 61.5266 | 122.941 | 61.5346 | 61.5843 | 61.4476 | 61.4973
2368.0625 | 123.2529 | -61.5463 | 61.6333 | 0.03944 | 0.22963 | 0.27645 | 0.35042 | 0.25143 | 0.34197 | 3.7646 | 61.5966 | 0.2349 | 61.5096 | -0.03768 | 0.039079 | 61.6394 | 0.003143 | 61.4176 | 61.5858 | 61.776 | 61.8228 | 61.8967 | 61.7978 | 61.8883 | 65.311 | 123.1429 | 61.7812 | 123.0559 | 61.5086 | 61.5854 | 123.1857 | 61.5495 | 122.9639 | 61.5575 | 61.5935 | 61.4705 | 61.5064
2369.0781 | 123.2941 | -61.5509 | 61.6516 | 0.044018 | 0.23421 | 0.2673 | 0.36416 | 0.26516 | 0.38776 | 2.469 | 61.6104 | 0.23032 | 61.537 | -0.033101 | 0.039079 | 61.6257 | 0.003143 | 61.4176 | 61.5949 | 61.7851 | 61.8182 | 61.9151 | 61.8161 | 61.9387 | 64.0199 | 123.1613 | 61.7812 | 123.0879 | 61.5178 | 61.59 | 123.1766 | 61.554 | 122.9685 | 61.5713 | 61.6072 | 61.4979 | 61.5339
2370.0625 | 123.3215 | -61.5234 | 61.6287 | 0.03944 | 0.22505 | 0.25814 | 0.355 | 0.25601 | 0.36486 | 3.6136 | 61.592 | 0.22574 | 61.4958 | -0.042259 | 0.039079 | 61.6211 | -0.006014 | 61.4222 | 61.5629 | 61.7485 | 61.7816 | 61.8784 | 61.7794 | 61.8883 | 65.137 | 123.1155 | 61.7492 | 123.0193 | 61.4812 | 61.5625 | 123.1445 | 61.5174 | 122.9456 | 61.553 | 61.5981 | 61.4567 | 61.5018
2371.0781 | 123.2803 | -61.5097 | 61.6745 | 0.044018 | 0.21589 | 0.24898 | 0.35042 | 0.24685 | 0.35113 | 3.4671 | 61.592 | 0.22574 | 61.5279 | -0.042259 | 0.039079 | 61.6211 | -0.006014 | 61.4176 | 61.5537 | 61.7256 | 61.7587 | 61.8601 | 61.7566 | 61.8608 | 64.9768 | 123.1017 | 61.7354 | 123.0376 | 61.4674 | 61.5488 | 123.1308 | 61.5037 | 122.9273 | 61.553 | 61.5981 | 61.4888 | 61.5339
2372.0625 | 123.2803 | -61.5692 | 61.615 | 0.03944 | 0.22047 | 0.25814 | 0.35958 | 0.25601 | 0.36944 | 3.5678 | 61.5966 | 0.22574 | 61.5279 | -0.03768 | 0.039079 | 61.6211 | -0.006014 | 61.4222 | 61.6087 | 61.7897 | 61.8274 | 61.9288 | 61.8252 | 61.9387 | 65.137 | 123.1658 | 61.795 | 123.0971 | 61.5315 | 61.6083 | 123.1903 | 61.5632 | 122.9914 | 61.5575 | 61.6026 | 61.4888 | 61.5339
2373.0938 | 123.3215 | -61.528 | 61.6425 | 0.03944 | 0.193 | 0.23982 | 0.355 | 0.25601 | 0.37402 | 3.6593 | 61.592 | 0.23032 | 61.4958 | -0.03768 | 0.039079 | 61.6257 | -0.001436 | 61.413 | 61.5675 | 61.721 | 61.7678 | 61.883 | 61.784 | 61.902 | 65.1874 | 123.1201 | 61.7583 | 123.0238 | 61.4903 | 61.5671 | 123.1537 | 61.5266 | 122.941 | 61.553 | 61.5935 | 61.4567 | 61.4973
2374.0625 | 123.2803 | -61.5555 | 61.6104 | 0.03944 | 0.18384 | 0.23525 | 0.34126 | 0.26059 | 0.36029 | 3.554 | 61.592 | 0.23032 | 61.5324 | -0.033101 | 0.034501 | 61.6257 | -0.001436 | 61.4176 | 61.5949 | 61.7393 | 61.7907 | 61.8967 | 61.8161 | 61.9158 | 65.1095 | 123.1475 | 61.7858 | 123.0879 | 61.5224 | 61.59 | 123.1812 | 61.554 | 122.9731 | 61.5575 | 61.5935 | 61.4979 | 61.5339
2375.1094 | 123.4497 | -61.4868 | 61.6196 | 0.03944 | 0.21589 | 0.2673 | 0.37331 | 0.27432 | 0.44728 | 1.9608 | 61.6058 | 0.22574 | 61.5233 | -0.03768 | 0.039079 | 61.6119 | 0.007721 | 61.4084 | 61.5263 | 61.7027 | 61.7541 | 61.8601 | 61.7611 | 61.9341 | 63.4477 | 123.0926 | 61.7126 | 123.0101 | 61.4491 | 61.5259 | 123.0988 | 61.4945 | 122.8953 | 61.5667 | 61.5981 | 61.4842 | 61.5156
2376.0625 | 123.2529 | -61.5326 | 61.6333 | 0.03944 | 0.14721 | 0.2444 | 0.355 | 0.26059 | 0.36944 | 2.9039 | 61.592 | 0.23032 | 61.5141 | -0.042259 | 0.039079 | 61.6165 | -0.001436 | 61.4039 | 61.572 | 61.6798 | 61.777 | 61.8876 | 61.7932 | 61.902 | 64.4365 | 123.1246 | 61.7629 | 123.0467 | 61.4903 | 61.5717 | 123.1491 | 61.5312 | 122.9365 | 61.553 | 61.5935 | 61.4751 | 61.5156
2377.0781 | 123.3124 | -61.5234 | 61.6608 | 0.03944 | 0.19758 | 0.2673 | 0.37331 | 0.26516 | 0.41065 | 3.5449 | 61.6012 | 0.23032 | 61.5279 | -0.03768 | 0.029923 | 61.6257 | -0.001436 | 61.4268 | 61.5629 | 61.721 | 61.7907 | 61.8967 | 61.7886 | 61.9341 | 65.0683 | 123.1246 | 61.7538 | 123.0513 | 61.4858 | 61.5534 | 123.1491 | 61.522 | 122.9502 | 61.5713 | 61.6026 | 61.4979 | 61.5293
2378.0625 | 123.262 | -61.5601 | 61.6241 | 0.034862 | 0.16095 | 0.23982 | 0.37789 | 0.25143 | 0.40149 | 3.4213 | 61.5875 | 0.22574 | 61.4821 | -0.03768 | 0.034501 | 61.6211 | 0.007721 | 61.4176 | 61.5949 | 61.721 | 61.7999 | 61.938 | 61.8115 | 61.9616 | 64.9813 | 123.1475 | 61.7858 | 123.0421 | 61.5224 | 61.5946 | 123.1812 | 61.5678 | 122.9777 | 61.553 | 61.5797 | 61.4476 | 61.4744
2379.0625 | 123.2803 | -61.5234 | 61.6333 | 0.034862 | 0.11516 | 0.24898 | 0.3962 | 0.25601 | 0.40149 | 3.4259 | 61.6012 | 0.21658 | 61.5279 | -0.042259 | 0.034501 | 61.6257 | -0.001436 | 61.4176 | 61.5583 | 61.6386 | 61.7724 | 61.9196 | 61.7794 | 61.9249 | 64.9493 | 123.1246 | 61.74 | 123.0513 | 61.4812 | 61.5579 | 123.1491 | 61.522 | 122.941 | 61.5667 | 61.6026 | 61.4934 | 61.5293
2380.0625 | 123.3032 | -61.5372 | 61.6379 | 0.03944 | 0.14263 | 0.26272 | 0.42368 | 0.2789 | 0.42896 | 3.2885 | 61.5966 | 0.22574 | 61.5324 | -0.03768 | 0.034501 | 61.6119 | -0.001436 | 61.4176 | 61.5766 | 61.6798 | 61.7999 | 61.9608 | 61.8161 | 61.9661 | 64.8257 | 123.1338 | 61.7629 | 123.0696 | 61.4995 | 61.5717 | 123.1491 | 61.5357 | 122.9548 | 61.5621 | 61.5981 | 61.4979 | 61.5339
2381.0781 | 123.2941 | -61.5372 | 61.6241 | 0.044018 | 0.106 | 0.25356 | 0.42368 | 0.25601 | 0.43354 | 2.3958 | 61.6012 | 0.23032 | 61.5004 | -0.042259 | 0.029923 | 61.6165 | -0.001436 | 61.4039 | 61.5812 | 61.6432 | 61.7907 | 61.9608 | 61.7932 | 61.9707 | 63.9329 | 123.1384 | 61.7675 | 123.0376 | 61.4949 | 61.5671 | 123.1537 | 61.5357 | 122.941 | 61.5713 | 61.6026 | 61.4705 | 61.5018
2382.0625 | 123.2895 | -61.5417 | 61.6058 | 0.03944 | 0.13347 | 0.25356 | 0.47404 | 0.29263 | 0.48848 | 2.6567 | 61.5966 | 0.22574 | 61.537 | -0.042259 | 0.034501 | 61.6165 | -0.006014 | 61.4084 | 61.5812 | 61.6752 | 61.7953 | 62.0158 | 61.8344 | 62.0302 | 64.1985 | 123.1384 | 61.7675 | 123.0788 | 61.4995 | 61.5762 | 123.1583 | 61.5357 | 122.9502 | 61.5621 | 61.6026 | 61.5025 | 61.543
2383.0625 | 123.2666 | -61.5463 | 61.6287 | 0.03944 | 0.087686 | 0.2673 | 0.45572 | 0.26516 | 0.43354 | 2.4782 | 61.6012 | 0.22574 | 61.5279 | -0.042259 | 0.029923 | 61.6074 | 0.003143 | 61.4084 | 61.5858 | 61.634 | 61.8136 | 62.0021 | 61.8115 | 61.9799 | 64.0245 | 123.1475 | 61.7721 | 123.0742 | 61.5041 | 61.5762 | 123.1537 | 61.5495 | 122.9548 | 61.5713 | 61.5981 | 61.4979 | 61.5247
2384.0781 | 123.317 | -61.5097 | 61.6379 | 0.044018 | 0.106 | 0.25356 | 0.46488 | 0.28805 | 0.56631 | 1.7457 | 61.6058 | 0.22574 | 61.5279 | -0.042259 | 0.025345 | 61.6119 | -0.010593 | 61.3993 | 61.5537 | 61.6157 | 61.7633 | 61.9746 | 61.7978 | 62.076 | 63.2554 | 123.1155 | 61.7354 | 123.0376 | 61.4674 | 61.535 | 123.1216 | 61.4991 | 122.909 | 61.5804 | 61.6164 | 61.5025 | 61.5385
2385.0625 | 123.3627 | -61.5372 | 61.5784 | 0.03944 | 0.13347 | 0.2673 | 0.4832 | 0.28347 | 0.85475 | 2.4141 | 61.6012 | 0.22574 | 61.5324 | -0.042259 | 0.029923 | 61.6257 | -0.006014 | 61.4084 | 61.5766 | 61.6706 | 61.8045 | 62.0204 | 61.8206 | 62.3919 | 63.9512 | 123.1384 | 61.7629 | 123.0696 | 61.4949 | 61.5671 | 123.1628 | 61.5312 | 122.9456 | 61.5713 | 61.6072 | 61.5025 | 61.5385
2386.0781 | 123.2986 | -61.5143 | 61.6104 | 0.03944 | 0.1289 | 0.26272 | 0.49693 | 0.2789 | 0.85933 | 2.5972 | 61.5966 | 0.23032 | 61.505 | -0.046838 | 0.029923 | 61.6165 | -0.006014 | 61.4084 | 61.5537 | 61.6432 | 61.777 | 62.0112 | 61.7932 | 62.3736 | 64.1115 | 123.1109 | 61.7446 | 123.0193 | 61.4674 | 61.5442 | 123.1308 | 61.5083 | 122.9227 | 61.5667 | 61.6026 | 61.4751 | 61.511
2387.0625 | 123.3124 | -61.5372 | 61.5738 | 0.034862 | 0.12432 | 0.26272 | 0.4832 | 0.28347 | 0.79523 | 2.5194 | 61.6012 | 0.2349 | 61.5233 | -0.046838 | 0.029923 | 61.6211 | -0.001436 | 61.4039 | 61.572 | 61.6615 | 61.7999 | 62.0204 | 61.8206 | 62.3324 | 64.0565 | 123.1384 | 61.7721 | 123.0605 | 61.4903 | 61.5671 | 123.1583 | 61.5357 | 122.941 | 61.5713 | 61.6026 | 61.4934 | 61.5247
2388.0781 | 123.3078 | -61.5234 | 61.6196 | 0.03944 | 0.15179 | 0.29477 | 0.49693 | 0.30179 | 0.92801 | 1.7228 | 61.6058 | 0.23032 | 61.537 | -0.042259 | 0.034501 | 61.6165 | -0.006014 | 61.4084 | 61.5629 | 61.6752 | 61.8182 | 62.0204 | 61.8252 | 62.4514 | 63.2462 | 123.1292 | 61.7538 | 123.0605 | 61.4812 | 61.5579 | 123.14 | 61.5174 | 122.9319 | 61.5713 | 61.6118 | 61.5025 | 61.543
2389.0625 | 123.3994 | -61.4914 | 61.5509 | 0.03944 | 0.14721 | 0.29019 | 0.48778 | 0.30179 | 0.91427 | 1.6449 | 61.6012 | 0.22574 | 61.5141 | -0.042259 | 0.029923 | 61.6119 | -0.006014 | 61.3993 | 61.5308 | 61.6386 | 61.7816 | 61.9792 | 61.7932 | 62.4057 | 63.1363 | 123.0926 | 61.7171 | 123.0055 | 61.4491 | 61.5213 | 123.1033 | 61.4854 | 122.8907 | 61.5713 | 61.6072 | 61.4842 | 61.5202
2390.0938 | 123.4177 | -61.496 | 61.5692 | 0.034862 | 0.13347 | 0.29019 | 0.51525 | 0.3201 | 0.99668 | 1.7823 | 61.6058 | 0.23032 | 61.537 | -0.042259 | 0.029923 | 61.6165 | -0.006014 | 61.4039 | 61.5308 | 61.6294 | 61.7862 | 62.0112 | 61.8161 | 62.4927 | 63.2783 | 123.1017 | 61.7263 | 123.033 | 61.4537 | 61.5259 | 123.1125 | 61.49 | 122.8998 | 61.5759 | 61.6118 | 61.5071 | 61.543
2391.0625 | 123.3261 | -61.528 | 61.6104 | 0.044018 | 0.096844 | 0.28103 | 0.52898 | 0.32468 | 0.9921 | 1.7319 | 61.6058 | 0.22116 | 61.537 | -0.042259 | 0.029923 | 61.6165 | -0.001436 | 61.4039 | 61.572 | 61.6249 | 61.809 | 62.057 | 61.8527 | 62.5201 | 63.2599 | 123.1338 | 61.7492 | 123.065 | 61.4858 | 61.5579 | 123.1445 | 61.5266 | 122.9319 | 61.5759 | 61.6072 | 61.5071 | 61.5385
2392.0781 | 123.2849 | -61.5463 | 61.6058 | 0.03944 | 0.106 | 0.30392 | 0.56103 | 0.32925 | 1.0745 | 1.7273 | 61.5966 | 0.22116 | 61.505 | -0.042259 | 0.043657 | 61.6165 | -0.006014 | 61.4039 | 61.5858 | 61.6523 | 61.8503 | 62.1074 | 61.8756 | 62.6208 | 63.2737 | 123.1429 | 61.7675 | 123.0513 | 61.5041 | 61.59 | 123.1628 | 61.5403 | 122.9502 | 61.553 | 61.6026 | 61.4613 | 61.511
2393.0625 | 123.4039 | -61.5051 | 61.5555 | 0.044018 | 0.037319 | 0.28103 | 0.56103 | 0.3201 | 0.98295 | 1.677 | 61.6058 | 0.22574 | 61.537 | -0.046838 | 0.034501 | 61.6119 | -0.001436 | 61.4039 | 61.5491 | 61.5424 | 61.7862 | 62.0662 | 61.8252 | 62.4881 | 63.1821 | 123.1109 | 61.7309 | 123.0422 | 61.4583 | 61.5396 | 123.1171 | 61.5037 | 122.909 | 61.5713 | 61.6072 | 61.5025 | 61.5385
2394.0938 | 123.3444 | -61.5326 | 61.5829 | 0.034862 | 0.051056 | 0.27645 | 0.57934 | 0.32468 | 1.0516 | 1.7136 | 61.6058 | 0.22116 | 61.537 | -0.042259 | 0.029923 | 61.6119 | 0.003143 | 61.3993 | 61.5675 | 61.5836 | 61.809 | 62.1119 | 61.8573 | 62.5842 | 63.2462 | 123.1384 | 61.7538 | 123.0696 | 61.4903 | 61.5625 | 123.1445 | 61.5357 | 122.9319 | 61.5759 | 61.6026 | 61.5071 | 61.5339
2395.0625 | 123.3765 | -61.5234 | 61.6058 | 0.03944 | 0.028162 | 0.25814 | 0.59766 | 0.31094 | 1.0974 | 1.7136 | 61.592 | 0.22116 | 61.5141 | -0.03768 | 0.029923 | 61.6211 | 0.003143 | 61.413 | 61.5629 | 61.5516 | 61.7816 | 62.1211 | 61.8344 | 62.6208 | 63.2371 | 123.1155 | 61.7446 | 123.0376 | 61.4858 | 61.5534 | 123.1445 | 61.5266 | 122.9365 | 61.5621 | 61.5889 | 61.4842 | 61.511
2396.0625 | 123.3536 | -61.4777 | 61.5875 | 0.044018 | 0.037319 | 0.25814 | 0.58392 | 0.31552 | 1.0058 | 1.796 | 61.6012 | 0.23032 | 61.5416 | -0.03768 | 0.029923 | 61.6074 | -0.006014 | 61.4039 | 61.5217 | 61.515 | 61.7358 | 62.0616 | 61.7932 | 62.4835 | 63.2737 | 123.0789 | 61.708 | 123.0193 | 61.44 | 61.5076 | 123.085 | 61.4716 | 122.8815 | 61.5713 | 61.6072 | 61.5117 | 61.5476
2397.0625 | 123.3261 | -61.528 | 61.6058 | 0.03944 | 0.046477 | 0.27187 | 0.60224 | 0.31552 | 0.85475 | 1.7365 | 61.592 | 0.22116 | 61.5141 | -0.042259 | 0.029923 | 61.6165 | -0.001436 | 61.3993 | 61.5675 | 61.5745 | 61.7999 | 62.1303 | 61.8435 | 62.3828 | 63.2645 | 123.1201 | 61.7492 | 123.0422 | 61.4858 | 61.5579 | 123.1445 | 61.5266 | 122.9273 | 61.5621 | 61.5935 | 61.4842 | 61.5156
2398.0625 | 123.3444 | -61.5143 | 61.5784 | 0.034862 | 0.055634 | 0.2444 | 0.5885 | 0.29263 | 0.7815 | 1.6175 | 61.6058 | 0.22574 | 61.5416 | -0.03768 | 0.029923 | 61.6074 | -0.010593 | 61.3993 | 61.5491 | 61.5699 | 61.7587 | 62.1028 | 61.8069 | 62.2958 | 63.1318 | 123.1201 | 61.74 | 123.0559 | 61.4766 | 61.5442 | 123.1216 | 61.5037 | 122.9136 | 61.5759 | 61.6164 | 61.5117 | 61.5522
2399.0781 | 123.349 | -61.5005 | 61.615 | 0.03944 | 0.041898 | 0.26272 | 0.5885 | 0.30179 | 0.79981 | 1.6587 | 61.6104 | 0.22574 | 61.5462 | -0.03768 | 0.039079 | 61.6074 | -0.001436 | 61.4039 | 61.54 | 61.5424 | 61.7633 | 62.0891 | 61.8023 | 62.3004 | 63.1592 | 123.1109 | 61.7263 | 123.0467 | 61.4629 | 61.5396 | 123.1079 | 61.4991 | 122.9044 | 61.5713 | 61.6118 | 61.5071 | 61.5476
2400.0625 | 123.3719 | -61.5005 | 61.5875 | 0.03944 | 0.046477 | 0.3085 | 0.5885 | 0.30179 | 0.77692 | 1.6678 | 61.5966 | 0.23032 | 61.5004 | -0.03768 | 0.029923 | 61.6165 | -0.006014 | 61.3993 | 61.54 | 61.547 | 61.8091 | 62.0891 | 61.8023 | 62.2775 | 63.1684 | 123.0972 | 61.7309 | 123.0009 | 61.4629 | 61.5305 | 123.1171 | 61.4945 | 122.8998 | 61.5667 | 61.6026 | 61.4705 | 61.5064
2401.0781 | 123.3536 | -61.496 | 61.615 | 0.044018 | 0.046477 | 0.88083 | 0.63887 | 0.31552 | 0.68077 | 1.6495 | 61.6012 | 0.22574 | 61.5416 | -0.03768 | 0.034501 | 61.6165 | -0.001436 | 61.413 | 61.54 | 61.5424 | 62.3768 | 62.1348 | 61.8115 | 62.1767 | 63.1455 | 123.0972 | 61.7217 | 123.0376 | 61.4583 | 61.5305 | 123.1125 | 61.4945 | 122.909 | 61.5667 | 61.6026 | 61.5071 | 61.543
2402.0625 | 123.3719 | -61.5326 | 61.5692 | 0.034862 | 0.023583 | 1.4577 | 0.65718 | 0.31094 | 0.61668 | 1.5946 | 61.6012 | 0.23032 | 61.5187 | -0.046838 | 0.029923 | 61.6211 | -0.006014 | 61.413 | 61.5675 | 61.5562 | 62.9903 | 62.1898 | 61.8435 | 62.1493 | 63.1272 | 123.1338 | 61.7629 | 123.0513 | 61.4858 | 61.5625 | 123.1537 | 61.5266 | 122.9456 | 61.5713 | 61.6072 | 61.4888 | 61.5247
2403.0781 | 123.3032 | -61.5097 | 61.6241 | 0.044018 | 0.009846 | 1.6317 | 0.63887 | 0.31094 | 0.69451 | 1.59 | 61.6012 | 0.22116 | 61.5004 | -0.046838 | 0.039079 | 61.6257 | -0.001436 | 61.413 | 61.5537 | 61.5196 | 63.1414 | 62.1486 | 61.8206 | 62.2042 | 63.0997 | 123.1109 | 61.7309 | 123.0101 | 61.4629 | 61.5488 | 123.1354 | 61.5083 | 122.9227 | 61.5621 | 61.6026 | 61.4613 | 61.5018
2404.0625 | 123.4222 | -61.5189 | 61.5692 | 0.03944 | 0.028162 | 1.737 | 0.65718 | 0.31552 | 0.66246 | 1.5992 | 61.5966 | 0.22574 | 61.5324 | -0.03768 | 0.034501 | 61.6257 | -0.001436 | 61.413 | 61.5583 | 61.547 | 63.2559 | 62.176 | 61.8344 | 62.1813 | 63.118 | 123.1155 | 61.7446 | 123.0513 | 61.4812 | 61.5534 | 123.1445 | 61.5174 | 122.9319 | 61.5621 | 61.5981 | 61.4979 | 61.5339
2405.1094 | 123.3078 | -61.5372 | 61.615 | 0.044018 | -0.017627 | 1.7645 | 0.65718 | 0.32925 | 0.72656 | 1.622 | 61.5829 | 0.22116 | 61.4912 | -0.033101 | 0.039079 | 61.6303 | -0.006014 | 61.4084 | 61.5812 | 61.5195 | 63.3017 | 62.1943 | 61.8664 | 62.2637 | 63.1592 | 123.1201 | 61.7583 | 123.0284 | 61.5041 | 61.5762 | 123.1674 | 61.5312 | 122.9456 | 61.5438 | 61.5889 | 61.4522 | 61.4973
2406.0625 | 123.3856 | -61.5097 | 61.5417 | 0.03944 | -0.022205 | 1.7324 | 0.62971 | 0.32925 | 0.71282 | 1.4618 | 61.6012 | 0.2349 | 61.5187 | -0.03768 | 0.029923 | 61.6211 | -0.001436 | 61.4222 | 61.5491 | 61.4875 | 63.2422 | 62.1394 | 61.839 | 62.2225 | 62.9715 | 123.1109 | 61.7446 | 123.0284 | 61.472 | 61.5396 | 123.1308 | 61.5083 | 122.9319 | 61.5713 | 61.6026 | 61.4888 | 61.5202
2407.0625 | 123.3353 | -61.5417 | 61.5143 | 0.034862 | -0.063415 | 1.7553 | 0.61597 | 0.32925 | 0.63499 | 1.3977 | 61.5966 | 0.22116 | 61.5324 | -0.046838 | 0.029923 | 61.6257 | -0.006014 | 61.4176 | 61.5766 | 61.4783 | 63.2971 | 62.1577 | 61.871 | 62.1767 | 62.9395 | 123.1384 | 61.7629 | 123.0742 | 61.4949 | 61.5717 | 123.1674 | 61.5357 | 122.9593 | 61.5667 | 61.6026 | 61.5025 | 61.5385
2408.0938 | 123.3261 | -61.5189 | 61.5692 | 0.034862 | -0.086309 | 1.7462 | 0.61597 | 0.31552 | 0.60752 | 1.1459 | 61.6012 | 0.23032 | 61.4958 | -0.03768 | 0.029923 | 61.6211 | -0.010593 | 61.4084 | 61.5537 | 61.4326 | 63.265 | 62.1348 | 61.8344 | 62.1264 | 62.6648 | 123.1201 | 61.7492 | 123.0147 | 61.4812 | 61.5488 | 123.14 | 61.5083 | 122.9273 | 61.5713 | 61.6118 | 61.4659 | 61.5064
2409.0625 | 123.381 | -61.5326 | 61.5234 | 0.03944 | -0.090888 | 1.7599 | 0.64802 | 0.32468 | 0.6121 | 0.99942 | 61.6058 | 0.22116 | 61.5324 | -0.03768 | 0.029923 | 61.6165 | 0.003143 | 61.4084 | 61.572 | 61.4417 | 63.2925 | 62.1806 | 61.8573 | 62.1447 | 62.532 | 123.1384 | 61.7538 | 123.065 | 61.4949 | 61.5625 | 123.1491 | 61.5357 | 122.941 | 61.5759 | 61.6026 | 61.5025 | 61.5293
2410.0938 | 123.2895 | -61.5463 | 61.6104 | 0.03944 | -0.090888 | 1.824 | 0.68465 | 0.34299 | 0.62583 | 0.87581 | 61.6058 | 0.23032 | 61.5324 | -0.03768 | 0.034501 | 61.6211 | 0.003143 | 61.413 | 61.5858 | 61.4554 | 63.3703 | 62.231 | 61.8893 | 62.1722 | 62.4221 | 123.1521 | 61.7766 | 123.0788 | 61.5086 | 61.5808 | 123.1674 | 61.5495 | 122.9593 | 61.5713 | 61.6026 | 61.4979 | 61.5293
2411.0625 | 123.3902 | -61.5326 | 61.5555 | 0.034862 | -0.08173 | 1.8103 | 0.69839 | 0.32468 | 0.56631 | 0.95822 | 61.5966 | 0.23032 | 61.505 | -0.042259 | 0.034501 | 61.6165 | -0.006014 | 61.4084 | 61.5675 | 61.4509 | 63.3429 | 62.231 | 61.8573 | 62.0989 | 62.4908 | 123.1292 | 61.7629 | 123.0376 | 61.4903 | 61.5671 | 123.1491 | 61.5266 | 122.941 | 61.5621 | 61.6026 | 61.4705 | 61.511
2412.0781 | 123.2712 | -61.5234 | 61.6104 | 0.044018 | -0.049678 | 1.8286 | 0.69381 | 0.33841 | 0.6121 | 0.91243 | 61.5966 | 0.22574 | 61.5462 | -0.03768 | 0.034501 | 61.6257 | -0.006014 | 61.4084 | 61.5675 | 61.4738 | 63.352 | 62.2172 | 61.8618 | 62.1355 | 62.4359 | 123.1201 | 61.7492 | 123.0696 | 61.4858 | 61.5579 | 123.1491 | 61.5174 | 122.9319 | 61.5621 | 61.6026 | 61.5117 | 61.5522
2413.0625 | 123.3673 | -61.528 | 61.5875 | 0.03944 | -0.040521 | 1.8103 | 0.67091 | 0.33841 | 0.64415 | 0.89412 | 61.6012 | 0.23032 | 61.5096 | -0.042259 | 0.029923 | 61.6257 | 0.003143 | 61.4039 | 61.5675 | 61.4875 | 63.3383 | 62.1989 | 61.8664 | 62.1722 | 62.4221 | 123.1292 | 61.7583 | 123.0376 | 61.4858 | 61.5579 | 123.1537 | 61.5312 | 122.9319 | 61.5713 | 61.5981 | 61.4796 | 61.5064
2414.0781 | 123.2849 | -61.5372 | 61.6333 | 0.034862 | -0.0451 | 1.6821 | 0.62055 | 0.32925 | 0.64872 | 0.95364 | 61.6012 | 0.22574 | 61.5279 | -0.03768 | 0.034501 | 61.6211 | -0.001436 | 61.413 | 61.572 | 61.4921 | 63.2193 | 62.1577 | 61.8664 | 62.1859 | 62.4908 | 123.1384 | 61.7629 | 123.065 | 61.4995 | 61.5717 | 123.1583 | 61.5357 | 122.9502 | 61.5667 | 61.6026 | 61.4934 | 61.5293
2415.0625 | 123.3261 | -61.496 | 61.6425 | 0.034862 | -0.086309 | 1.5951 | 0.59308 | 0.30179 | 0.62125 | 0.87581 | 61.6012 | 0.2349 | 61.5462 | -0.03768 | 0.039079 | 61.6165 | -0.001436 | 61.413 | 61.5308 | 61.4097 | 63.0911 | 62.0891 | 61.7978 | 62.1172 | 62.3718 | 123.0972 | 61.7309 | 123.0422 | 61.4583 | 61.5351 | 123.1125 | 61.4945 | 122.909 | 61.5621 | 61.6026 | 61.5071 | 61.5476
2416.0938 | 123.3673 | -61.528 | 61.5875 | 0.03944 | -0.10462 | 1.5401 | 0.40994 | 0.28347 | 0.58005 | 0.75678 | 61.6058 | 0.23948 | 61.5004 | -0.046838 | 0.034501 | 61.6119 | -0.001436 | 61.3993 | 61.5675 | 61.4234 | 63.0682 | 61.938 | 61.8115 | 62.1081 | 62.2848 | 123.1338 | 61.7675 | 123.0284 | 61.4812 | 61.5625 | 123.14 | 61.5266 | 122.9273 | 61.5713 | 61.6072 | 61.4659 | 61.5018
2417.0625 | 123.3994 | -61.4868 | 61.5967 | 0.03944 | -0.08173 | 1.5676 | 0.31379 | 0.30179 | 0.60752 | 0.86207 | 61.6149 | 0.22116 | 61.5462 | -0.03768 | 0.029923 | 61.6119 | -0.001436 | 61.4084 | 61.5263 | 61.4051 | 63.0544 | 61.8006 | 61.7886 | 62.0943 | 62.3489 | 123.1017 | 61.708 | 123.033 | 61.4491 | 61.5167 | 123.0988 | 61.4854 | 122.8953 | 61.585 | 61.6164 | 61.5163 | 61.5476
2418.0938 | 123.3902 | -61.5051 | 61.5601 | 0.03944 | -0.086309 | 1.6226 | 0.26343 | 0.30636 | 0.52511 | 0.78424 | 61.6012 | 0.22574 | 61.5416 | -0.03768 | 0.029923 | 61.6074 | -0.006014 | 61.4039 | 61.5446 | 61.4188 | 63.1277 | 61.7686 | 61.8115 | 62.0302 | 62.2894 | 123.1063 | 61.7309 | 123.0467 | 61.4674 | 61.535 | 123.1125 | 61.4991 | 122.909 | 61.5713 | 61.6072 | 61.5117 | 61.5476
2419.0625 | 123.3673 | -61.5143 | 61.6196 | 0.03944 | -0.12752 | 1.4898 | 0.19475 | 0.27432 | 0.42438 | 0.81171 | 61.6012 | 0.22574 | 61.5004 | -0.03768 | 0.034501 | 61.6074 | -0.006014 | 61.3993 | 61.5537 | 61.3868 | 63.0041 | 61.709 | 61.7886 | 61.9387 | 62.326 | 123.1155 | 61.74 | 123.0147 | 61.4766 | 61.5488 | 123.1216 | 61.5083 | 122.9136 | 61.5667 | 61.6072 | 61.4659 | 61.5064
2420.1094 | 123.2986 | -61.5372 | 61.5921 | 0.03944 | -0.086309 | 1.6134 | 0.18559 | 0.31094 | 0.4427 | 0.74762 | 61.6104 | 0.22116 | 61.5416 | -0.033101 | 0.039079 | 61.6119 | -0.001436 | 61.4039 | 61.5766 | 61.4509 | 63.1506 | 61.7228 | 61.8481 | 61.9799 | 62.2848 | 123.1475 | 61.7583 | 123.0788 | 61.5041 | 61.5762 | 123.1491 | 61.5357 | 122.941 | 61.5713 | 61.6118 | 61.5025 | 61.543
2421.0625 | 123.3765 | -61.5189 | 61.6104 | 0.03944 | -0.067994 | 1.6592 | 0.18102 | 0.32925 | 0.4198 | 0.77967 | 61.6058 | 0.22574 | 61.5279 | -0.042259 | 0.034501 | 61.6119 | -0.001436 | 61.3993 | 61.5583 | 61.4509 | 63.178 | 61.6999 | 61.8481 | 61.9387 | 62.2985 | 123.1246 | 61.7446 | 123.0467 | 61.4766 | 61.5534 | 123.1308 | 61.5174 | 122.9181 | 61.5713 | 61.6072 | 61.4934 | 61.5293
2422.0781 | 123.4268 | -61.4914 | 61.528 | 0.030283 | -0.11836 | 1.5218 | 0.16728 | 0.30636 | 0.34197 | 0.74762 | 61.6149 | 0.23032 | 61.5233 | -0.03768 | 0.039079 | 61.6074 | -0.006014 | 61.3901 | 61.5217 | 61.373 | 63.0132 | 61.6587 | 61.7978 | 61.8334 | 62.239 | 123.1063 | 61.7217 | 123.0147 | 61.4537 | 61.5305 | 123.0988 | 61.4854 | 122.8815 | 61.5759 | 61.6209 | 61.4842 | 61.5293
2423.0625 | 123.3398 | -61.5097 | 61.6013 | 0.034862 | -0.090888 | 1.5127 | 0.13981 | 0.29721 | 0.3786 | 0.85292 | 61.6104 | 0.23032 | 61.5462 | -0.042259 | 0.034501 | 61.6074 | -0.001436 | 61.3993 | 61.5446 | 61.4188 | 63.0224 | 61.6495 | 61.8069 | 61.8883 | 62.3626 | 123.1201 | 61.74 | 123.0559 | 61.4674 | 61.5442 | 123.1171 | 61.5083 | 122.909 | 61.5759 | 61.6118 | 61.5117 | 61.5476
2424.0781 | 123.2529 | -61.5326 | 61.5921 | 0.044018 | -0.10462 | 1.618 | 0.1215 | 0.30636 | 0.39233 | 0.88954 | 61.6104 | 0.23032 | 61.5279 | -0.042259 | 0.034501 | 61.6074 | -0.006014 | 61.3856 | 61.5766 | 61.428 | 63.1506 | 61.6541 | 61.839 | 61.9249 | 62.4221 | 123.1429 | 61.7629 | 123.0605 | 61.4903 | 61.5671 | 123.14 | 61.5266 | 122.9181 | 61.5759 | 61.6164 | 61.4934 | 61.5339
2425.0625 | 123.3765 | -61.4868 | 61.6241 | 0.048597 | -0.095467 | 1.8332 | 0.094024 | 0.32925 | 0.38776 | 0.81171 | 61.6104 | 0.23032 | 61.5187 | -0.03768 | 0.029923 | 61.6119 | 0.003143 | 61.4039 | 61.5354 | 61.3913 | 63.32 | 61.5808 | 61.8161 | 61.8746 | 62.2985 | 123.0972 | 61.7171 | 123.0055 | 61.4491 | 61.5167 | 123.0988 | 61.49 | 122.8907 | 61.5804 | 61.6072 | 61.4888 | 61.5156
2426.0938 | 123.3765 | -61.528 | 61.5738 | 0.03944 | -0.12752 | 1.6042 | 0.089445 | 0.29721 | 0.22293 | 0.82545 | 61.6104 | 0.23032 | 61.5508 | -0.042259 | 0.039079 | 61.6165 | 0.003143 | 61.3993 | 61.5675 | 61.4005 | 63.1323 | 61.6175 | 61.8252 | 61.751 | 62.3535 | 123.1384 | 61.7583 | 123.0788 | 61.4858 | 61.5671 | 123.1445 | 61.5312 | 122.9273 | 61.5713 | 61.6072 | 61.5117 | 61.5476
2427.0625 | 123.3719 | -61.4914 | 61.6241 | 0.03944 | -0.14125 | 1.6683 | 0.071132 | 0.29721 | 0.24125 | 0.71099 | 61.6149 | 0.22574 | 61.5599 | -0.046838 | 0.029923 | 61.6074 | -0.006014 | 61.3993 | 61.5308 | 61.3501 | 63.1597 | 61.5625 | 61.7886 | 61.7326 | 62.2024 | 123.1063 | 61.7171 | 123.0513 | 61.4446 | 61.5213 | 123.0988 | 61.4854 | 122.8907 | 61.585 | 61.6209 | 61.53 | 61.5659
2428.0781 | 123.2803 | -61.5189 | 61.5921 | 0.034862 | -0.12294 | 1.7782 | 0.07571 | 0.31552 | 0.29161 | 0.72015 | 61.6104 | 0.23032 | 61.5279 | -0.046838 | 0.039079 | 61.6074 | -0.001436 | 61.3947 | 61.5537 | 61.3959 | 63.2971 | 61.5946 | 61.8344 | 61.8105 | 62.239 | 123.1292 | 61.7492 | 123.0467 | 61.472 | 61.5579 | 123.1262 | 61.5174 | 122.9136 | 61.5713 | 61.6118 | 61.4888 | 61.5293
2429.0625 | 123.4039 | -61.4822 | 61.6058 | 0.034862 | -0.13668 | 1.7782 | 0.071132 | 0.30636 | 0.2733 | 0.58281 | 61.6058 | 0.23032 | 61.5141 | -0.042259 | 0.039079 | 61.6074 | -0.001436 | 61.3993 | 61.5171 | 61.3456 | 63.2605 | 61.5534 | 61.7886 | 61.7555 | 62.065 | 123.088 | 61.7126 | 122.9964 | 61.44 | 61.5213 | 123.0896 | 61.4808 | 122.8815 | 61.5667 | 61.6072 | 61.4751 | 61.5156
2430.0938 | 123.317 | -61.5372 | 61.5967 | 0.03944 | -0.12752 | 1.8103 | 0.080288 | 0.31552 | 0.27787 | 0.61485 | 61.6149 | 0.2349 | 61.5462 | -0.042259 | 0.034501 | 61.6074 | -0.001436 | 61.3947 | 61.5766 | 61.4097 | 63.3475 | 61.6175 | 61.8527 | 61.815 | 62.152 | 123.1521 | 61.7721 | 123.0834 | 61.4949 | 61.5717 | 123.1445 | 61.5357 | 122.9319 | 61.5804 | 61.6164 | 61.5117 | 61.5476
2431.0625 | 123.3902 | -61.4639 | 61.5738 | 0.034862 | -0.17788 | 1.8378 | 0.066553 | 0.3201 | 0.22751 | 0.34932 | 61.6149 | 0.23032 | 61.5508 | -0.03768 | 0.039079 | 61.6074 | -0.001436 | 61.4039 | 61.4988 | 61.286 | 63.3017 | 61.5305 | 61.784 | 61.6914 | 61.8132 | 123.0789 | 61.6942 | 123.0147 | 61.4262 | 61.503 | 123.0713 | 61.4625 | 122.8678 | 61.5759 | 61.6164 | 61.5117 | 61.5522
2432.0781 | 123.2666 | -61.528 | 61.6379 | 0.03944 | -0.18246 | 1.8332 | 0.071132 | 0.32468 | 0.22751 | 0.40426 | 61.6149 | 0.22574 | 61.5187 | -0.042259 | 0.039079 | 61.6074 | -0.006014 | 61.3993 | 61.5675 | 61.3456 | 63.3612 | 61.5991 | 61.8527 | 61.7555 | 61.9323 | 123.1429 | 61.7538 | 123.0467 | 61.4858 | 61.5671 | 123.1354 | 61.522 | 122.9273 | 61.5759 | 61.6209 | 61.4796 | 61.5247
2433.0625 | 123.3856 | -61.4639 | 61.5967 | 0.034862 | -0.20994 | 1.7965 | 0.061975 | 0.32925 | 0.20004 | 0.36763 | 61.6195 | 0.22574 | 61.5416 | -0.03768 | 0.034501 | 61.6074 | -0.001436 | 61.3993 | 61.4988 | 61.254 | 63.2605 | 61.5259 | 61.7932 | 61.664 | 61.8316 | 123.0834 | 61.6897 | 123.0055 | 61.4262 | 61.4984 | 123.0713 | 61.4625 | 122.8632 | 61.585 | 61.6209 | 61.5071 | 61.543
2434.0781 | 123.3856 | -61.5097 | 61.6013 | 0.03944 | -0.19162 | 1.8515 | 0.07571 | 0.35672 | 0.24125 | 0.40426 | 61.6149 | 0.23032 | 61.5508 | -0.033101 | 0.029923 | 61.6028 | -0.001436 | 61.3993 | 61.5491 | 61.3181 | 63.3612 | 61.5854 | 61.8664 | 61.751 | 61.914 | 123.1246 | 61.74 | 123.0605 | 61.4766 | 61.5396 | 123.1125 | 61.5083 | 122.909 | 61.585 | 61.6164 | 61.5208 | 61.5522
2435.0625 | 123.2986 | -61.496 | 61.6699 | 0.044018 | -0.17788 | 1.8698 | 0.080288 | 0.36588 | 0.2092 | 0.44088 | 61.6104 | 0.22574 | 61.5187 | -0.03768 | 0.034501 | 61.6074 | -0.001436 | 61.3947 | 61.54 | 61.3181 | 63.3658 | 61.5763 | 61.8619 | 61.7052 | 61.9369 | 123.1063 | 61.7217 | 123.0147 | 61.4583 | 61.5305 | 123.1033 | 61.4945 | 122.8907 | 61.5759 | 61.6118 | 61.4842 | 61.5202
2436.0781 | 123.3994 | -61.5005 | 61.5829 | 0.044018 | -0.20078 | 1.7553 | 0.071132 | 0.34299 | 0.18631 | 0.42715 | 61.6195 | 0.22574 | 61.5508 | -0.042259 | 0.034501 | 61.6074 | -0.006014 | 61.3947 | 61.5446 | 61.2998 | 63.2559 | 61.5717 | 61.8435 | 61.6869 | 61.9277 | 123.1201 | 61.7263 | 123.0513 | 61.4583 | 61.535 | 123.1079 | 61.4945 | 122.8953 | 61.585 | 61.6255 | 61.5163 | 61.5568
2437.0625 | 123.4039 | -61.4868 | 61.5967 | 0.030283 | -0.19162 | 1.8515 | 0.066553 | 0.35214 | 0.2092 | 0.44088 | 61.6058 | 0.23032 | 61.5324 | -0.03768 | 0.029923 | 61.6119 | -0.001436 | 61.3947 | 61.5171 | 61.2952 | 63.3383 | 61.5534 | 61.839 | 61.696 | 61.9277 | 123.0926 | 61.7171 | 123.0193 | 61.4491 | 61.5167 | 123.0988 | 61.4854 | 122.8815 | 61.5759 | 61.6072 | 61.5025 | 61.5339
2438.0625 | 123.4131 | -61.4639 | 61.615 | 0.034862 | -0.18704 | 1.8881 | 0.066553 | 0.37961 | 0.22293 | 0.46377 | 61.6149 | 0.22574 | 61.5141 | -0.03768 | 0.039079 | 61.6028 | -0.001436 | 61.3993 | 61.4988 | 61.2769 | 63.352 | 61.5305 | 61.8435 | 61.6869 | 61.9277 | 123.0789 | 61.6897 | 122.9781 | 61.4262 | 61.503 | 123.0667 | 61.4625 | 122.8632 | 61.5759 | 61.6164 | 61.4751 | 61.5156
2439.0625 | 123.4222 | -61.5051 | 61.6196 | 0.034862 | -0.19162 | 1.8469 | 0.061975 | 0.36588 | 0.17715 | 0.37221 | 61.6149 | 0.22116 | 61.5553 | -0.03768 | 0.039079 | 61.6028 | -0.001436 | 61.3947 | 61.54 | 61.3135 | 63.352 | 61.5671 | 61.871 | 61.6823 | 61.8773 | 123.1201 | 61.7263 | 123.0605 | 61.4674 | 61.5442 | 123.1079 | 61.5037 | 122.8998 | 61.5759 | 61.6164 | 61.5163 | 61.5568
2440.1094 | 123.2346 | -61.5234 | 61.6241 | 0.034862 | -0.17331 | 1.8744 | 0.066553 | 0.36588 | 0.15884 | 0.42257 | 61.6149 | 0.23032 | 61.5233 | -0.042259 | 0.034501 | 61.6028 | -0.001436 | 61.4084 | 61.5583 | 61.3501 | 63.3978 | 61.59 | 61.8893 | 61.6823 | 61.946 | 123.1384 | 61.7538 | 123.0467 | 61.4812 | 61.5579 | 123.1262 | 61.522 | 122.9319 | 61.5804 | 61.6164 | 61.4888 | 61.5247
2441.0625 | 123.436 | -61.4777 | 61.615 | 0.034862 | -0.24199 | 1.6912 | 0.057396 | 0.32925 | 0.1039 | 0.35847 | 61.6149 | 0.22574 | 61.5141 | -0.03768 | 0.029923 | 61.6074 | -0.006014 | 61.3901 | 61.5125 | 61.2357 | 63.1689 | 61.5351 | 61.8069 | 61.5816 | 61.8361 | 123.0926 | 61.7034 | 122.9918 | 61.44 | 61.5076 | 123.085 | 61.4716 | 122.8678 | 61.585 | 61.6209 | 61.4842 | 61.5202
2442.0625 | 123.4085 | -61.4639 | 61.6241 | 0.03944 | -0.20536 | 1.6775 | 0.057396 | 0.33383 | 0.11763 | 0.38137 | 61.6241 | 0.23032 | 61.5508 | -0.033101 | 0.034501 | 61.6119 | -0.001436 | 61.3993 | 61.5034 | 61.2586 | 63.1414 | 61.5213 | 61.7978 | 61.5816 | 61.8453 | 123.088 | 61.6942 | 123.0147 | 61.4308 | 61.4984 | 123.0759 | 61.4625 | 122.8632 | 61.5896 | 61.6255 | 61.5163 | 61.5522
2443.1094 | 123.4131 | -61.4594 | 61.5875 | 0.03944 | -0.18246 | 1.8469 | 0.052818 | 0.37503 | 0.13595 | 0.41799 | 61.6241 | 0.22574 | 61.5508 | -0.042259 | 0.043657 | 61.6074 | -0.015171 | 61.4039 | 61.4988 | 61.2769 | 63.3063 | 61.5122 | 61.8344 | 61.5953 | 61.8773 | 123.0834 | 61.6851 | 123.0101 | 61.4171 | 61.503 | 123.0667 | 61.4442 | 122.8632 | 61.5804 | 61.6393 | 61.5071 | 61.5659
2444.0625 | 123.4039 | -61.4777 | 61.6058 | 0.044018 | -0.1962 | 1.7828 | 0.052818 | 0.35672 | 0.12679 | 0.42257 | 61.6104 | 0.22116 | 61.5462 | -0.033101 | 0.034501 | 61.6028 | -0.001436 | 61.3856 | 61.5217 | 61.2815 | 63.2605 | 61.5305 | 61.8344 | 61.6044 | 61.9002 | 123.088 | 61.6988 | 123.0238 | 61.4446 | 61.5122 | 123.0804 | 61.4762 | 122.8632 | 61.5759 | 61.6118 | 61.5117 | 61.5476
2445.0625 | 123.3398 | -61.4822 | 61.6379 | 0.044018 | -0.13668 | 1.8103 | 0.039082 | 0.37046 | 0.11763 | 0.42257 | 61.6149 | 0.23032 | 61.5141 | -0.03768 | 0.034501 | 61.6119 | -0.001436 | 61.3993 | 61.5263 | 61.3456 | 63.2925 | 61.5213 | 61.8527 | 61.5999 | 61.9048 | 123.0972 | 61.7126 | 122.9964 | 61.4446 | 61.5167 | 123.0942 | 61.4808 | 122.8815 | 61.5804 | 61.6164 | 61.4796 | 61.5156
2446.0625 | 123.4177 | -61.4731 | 61.6104 | 0.044018 | -0.1321 | 1.7279 | 0.025347 | 0.36588 | 0.090161 | 0.47751 | 61.6149 | 0.22574 | 61.5462 | -0.03768 | 0.034501 | 61.6119 | -0.001436 | 61.3901 | 61.5171 | 61.341 | 63.201 | 61.4984 | 61.839 | 61.5632 | 61.9506 | 123.088 | 61.6988 | 123.0193 | 61.4354 | 61.5076 | 123.085 | 61.4716 | 122.8632 | 61.5804 | 61.6164 | 61.5117 | 61.5476
2447.0625 | 123.4177 | -61.4822 | 61.5967 | 0.034862 | -0.13668 | 1.705 | 0.039082 | 0.35214 | 0.090161 | 0.41799 | 61.6149 | 0.22574 | 61.5508 | -0.033101 | 0.039079 | 61.6165 | -0.001436 | 61.4084 | 61.5171 | 61.3456 | 63.1872 | 61.5213 | 61.8344 | 61.5724 | 61.9002 | 123.0972 | 61.708 | 123.033 | 61.4491 | 61.5213 | 123.0988 | 61.4808 | 122.8907 | 61.5759 | 61.6164 | 61.5117 | 61.5522
2448.0625 | 123.349 | -61.4685 | 61.5875 | 0.03944 | -0.11378 | 1.6226 | 0.052818 | 0.3613 | 0.1039 | 0.42715 | 61.6195 | 0.23948 | 61.537 | -0.033101 | 0.039079 | 61.6028 | -0.006014 | 61.3947 | 61.5079 | 61.3547 | 63.0911 | 61.5213 | 61.8298 | 61.5724 | 61.8957 | 123.088 | 61.708 | 123.0055 | 61.4354 | 61.5076 | 123.0713 | 61.4625 | 122.8632 | 61.5804 | 61.6255 | 61.4979 | 61.543
2449.0781 | 123.349 | -61.5005 | 61.5784 | 0.03944 | -0.10004 | 1.4577 | 0.057396 | 0.37503 | 0.11763 | 0.47293 | 61.6058 | 0.23032 | 61.5096 | -0.033101 | 0.029923 | 61.6028 | -0.001436 | 61.3993 | 61.54 | 61.4005 | 62.9583 | 61.5579 | 61.8756 | 61.6182 | 61.9735 | 123.1063 | 61.7309 | 123.0101 | 61.4674 | 61.5305 | 123.1033 | 61.4991 | 122.8998 | 61.5759 | 61.6072 | 61.4796 | 61.511
2450.0625 | 123.317 | -61.5051 | 61.6241 | 0.03944 | -0.063415 | 1.3021 | 0.094024 | 0.38877 | 0.12221 | 0.4363 | 61.6195 | 0.22574 | 61.5462 | -0.03768 | 0.039079 | 61.5982 | 0.003143 | 61.3993 | 61.5446 | 61.4417 | 62.8072 | 61.5992 | 61.8939 | 61.6273 | 61.9414 | 123.1246 | 61.7309 | 123.0513 | 61.4674 | 61.5442 | 123.1033 | 61.5083 | 122.9044 | 61.5804 | 61.6164 | 61.5071 | 61.543
2451.0625 | 123.4222 | -61.4822 | 61.6287 | 0.03944 | -0.067994 | 1.6134 | 0.10776 | 0.38419 | 0.12679 | 0.41341 | 61.6104 | 0.23032 | 61.5508 | -0.042259 | 0.043657 | 61.6074 | -0.006014 | 61.3993 | 61.5217 | 61.4142 | 63.0956 | 61.59 | 61.8664 | 61.609 | 61.8957 | 123.0926 | 61.7126 | 123.033 | 61.44 | 61.5259 | 123.0896 | 61.4762 | 122.8815 | 61.5667 | 61.6164 | 61.5071 | 61.5568
2452.0938 | 123.3582 | -61.5143 | 61.5967 | 0.044018 | -0.08173 | 1.792 | 0.089445 | 0.38877 | 0.10848 | 0.35847 | 61.6195 | 0.23032 | 61.5416 | -0.033101 | 0.029923 | 61.6074 | -0.001436 | 61.4039 | 61.5583 | 61.4326 | 63.3063 | 61.6037 | 61.9031 | 61.6228 | 61.8728 | 123.1338 | 61.7446 | 123.0559 | 61.4812 | 61.5442 | 123.1216 | 61.5128 | 122.9181 | 61.5896 | 61.6209 | 61.5117 | 61.543
2453.0625 | 123.4131 | -61.4822 | 61.5967 | 0.044018 | -0.10004 | 1.824 | 0.094024 | 0.37961 | 0.099318 | 0.32643 | 61.6195 | 0.23032 | 61.5141 | -0.03768 | 0.025345 | 61.6074 | 0.003143 | 61.3901 | 61.5263 | 61.3822 | 63.3063 | 61.5763 | 61.8619 | 61.5816 | 61.8087 | 123.1018 | 61.7126 | 122.9964 | 61.4446 | 61.5076 | 123.0896 | 61.4854 | 122.8724 | 61.5942 | 61.6164 | 61.4888 | 61.511
2454.0625 | 123.4131 | -61.4685 | 61.6196 | 0.034862 | -0.12294 | 1.7782 | 0.057396 | 0.36588 | 0.076426 | 0.31269 | 61.6195 | 0.22574 | 61.5324 | -0.046838 | 0.029923 | 61.6119 | -0.006014 | 61.3993 | 61.5034 | 61.3456 | 63.2467 | 61.5259 | 61.8344 | 61.5449 | 61.7812 | 123.088 | 61.6942 | 123.001 | 61.4217 | 61.4984 | 123.0804 | 61.4625 | 122.8678 | 61.5896 | 61.6255 | 61.5025 | 61.5385
2455.1094 | 123.2574 | -61.5005 | 61.647 | 0.044018 | -0.10462 | 1.8332 | 0.066553 | 0.4025 | 0.09474 | 0.34016 | 61.6241 | 0.23032 | 61.5508 | -0.03768 | 0.039079 | 61.6165 | -0.006014 | 61.3993 | 61.5446 | 61.3959 | 63.3337 | 61.5671 | 61.9031 | 61.5953 | 61.8407 | 123.1246 | 61.7309 | 123.0513 | 61.4629 | 61.5396 | 123.1171 | 61.4945 | 122.8998 | 61.585 | 61.6301 | 61.5117 | 61.5568
2456.0625 | 123.3856 | -61.4685 | 61.6058 | 0.03944 | -0.086309 | 1.8652 | 0.066553 | 0.41166 | 0.1039 | 0.34932 | 61.6149 | 0.2349 | 61.5416 | -0.03768 | 0.034501 | 61.6165 | -0.006014 | 61.3993 | 61.5079 | 61.3822 | 63.3337 | 61.5351 | 61.8802 | 61.5724 | 61.8178 | 123.0834 | 61.7034 | 123.0101 | 61.4308 | 61.503 | 123.085 | 61.4625 | 122.8678 | 61.5804 | 61.6209 | 61.5071 | 61.5476
2457.0625 | 123.381 | -61.4914 | 61.5829 | 0.03944 | -0.095467 | 1.911 | 0.057396 | 0.4025 | 0.11763 | 0.35847 | 61.6104 | 0.22574 | 61.5141 | -0.03768 | 0.034501 | 61.6119 | -0.006014 | 61.3947 | 61.5308 | 61.3959 | 63.4024 | 61.5488 | 61.8939 | 61.609 | 61.8499 | 123.1018 | 61.7171 | 123.0055 | 61.4537 | 61.5259 | 123.1033 | 61.4854 | 122.8861 | 61.5759 | 61.6164 | 61.4796 | 61.5202
2458.0625 | 123.3902 | -61.4777 | 61.6058 | 0.034862 | -0.11836 | 1.9934 | 0.057396 | 0.4025 | 0.09474 | 0.31269 | 61.6149 | 0.23032 | 61.5508 | -0.03768 | 0.034501 | 61.6028 | -0.001436 | 61.3947 | 61.5125 | 61.3593 | 63.4711 | 61.5351 | 61.8802 | 61.5724 | 61.7904 | 123.0926 | 61.708 | 123.0284 | 61.44 | 61.5122 | 123.0804 | 61.4762 | 122.8724 | 61.5804 | 61.6164 | 61.5163 | 61.5522
2459.0625 | 123.3902 | -61.4914 | 61.6104 | 0.044018 | -0.10004 | 2.0575 | 0.057396 | 0.41166 | 0.10848 | 0.3539 | 61.6104 | 0.22574 | 61.5324 | -0.033101 | 0.034501 | 61.6119 | -0.001436 | 61.3993 | 61.5354 | 61.3913 | 63.5489 | 61.5488 | 61.9031 | 61.5999 | 61.8453 | 123.1018 | 61.7171 | 123.0238 | 61.4583 | 61.5259 | 123.1033 | 61.49 | 122.8907 | 61.5759 | 61.6118 | 61.4979 | 61.5339
2460.0625 | 123.381 | -61.4777 | 61.5967 | 0.044018 | -0.086309 | 2.0438 | 0.048239 | 0.41624 | 0.12679 | 0.3539 | 61.6104 | 0.22574 | 61.5187 | -0.042259 | 0.029923 | 61.6119 | 0.003143 | 61.3901 | 61.5217 | 61.3914 | 63.5215 | 61.5259 | 61.8939 | 61.6044 | 61.8316 | 123.088 | 61.7034 | 122.9964 | 61.4354 | 61.5076 | 123.0896 | 61.4808 | 122.8678 | 61.5804 | 61.6072 | 61.4888 | 61.5156
2461.0781 | 123.3261 | -61.5097 | 61.6013 | 0.034862 | -0.08173 | 2.0987 | 0.043661 | 0.41624 | 0.13137 | 0.33101 | 61.6195 | 0.22574 | 61.5508 | -0.03768 | 0.034501 | 61.6074 | -0.006014 | 61.3947 | 61.5446 | 61.428 | 63.6084 | 61.5534 | 61.9259 | 61.6411 | 61.8407 | 123.1292 | 61.7354 | 123.0605 | 61.472 | 61.5442 | 123.1171 | 61.5037 | 122.9044 | 61.585 | 61.6255 | 61.5163 | 61.5568
2462.0625 | 123.3994 | -61.5005 | 61.5784 | 0.044018 | -0.095467 | 2.0209 | 0.01619 | 0.39335 | 0.081005 | 0.28522 | 61.6149 | 0.2349 | 61.5324 | -0.03768 | 0.034501 | 61.6074 | -0.006014 | 61.3901 | 61.5446 | 61.4051 | 63.5214 | 61.5167 | 61.8939 | 61.5816 | 61.7858 | 123.1155 | 61.7354 | 123.033 | 61.4629 | 61.535 | 123.1079 | 61.4945 | 122.8907 | 61.5804 | 61.6209 | 61.4979 | 61.5385
2463.0625 | 123.3444 | -61.4914 | 61.6104 | 0.048597 | -0.077151 | 1.998 | 0.002454 | 0.39792 | 0.062691 | 0.26233 | 61.6149 | 0.22574 | 61.537 | -0.042259 | 0.034501 | 61.6119 | -0.006014 | 61.4039 | 61.54 | 61.4142 | 63.4894 | 61.4938 | 61.8893 | 61.5541 | 61.7537 | 123.1063 | 61.7171 | 123.0284 | 61.4491 | 61.5259 | 123.1033 | 61.4854 | 122.8953 | 61.5804 | 61.6209 | 61.5025 | 61.543
2464.0625 | 123.381 | -61.5005 | 61.5921 | 0.03944 | -0.067994 | 1.9889 | 0.020768 | 0.39335 | 0.048956 | 0.2486 | 61.6195 | 0.22574 | 61.5462 | -0.03768 | 0.029923 | 61.6119 | -0.001436 | 61.3947 | 61.54 | 61.4326 | 63.4894 | 61.5213 | 61.8939 | 61.5495 | 61.7491 | 123.1201 | 61.7263 | 123.0467 | 61.4629 | 61.5305 | 123.1125 | 61.4991 | 122.8953 | 61.5896 | 61.6209 | 61.5163 | 61.5476
2465.0625 | 123.4085 | -61.4822 | 61.6058 | 0.03944 | -0.049678 | 2.1583 | 0.025347 | 0.42081 | 0.076426 | 0.24402 | 61.6058 | 0.2349 | 61.5096 | -0.03768 | 0.034501 | 61.6074 | -0.006014 | 61.3993 | 61.5217 | 61.4326 | 63.6405 | 61.5076 | 61.9031 | 61.5587 | 61.7263 | 123.088 | 61.7171 | 122.9918 | 61.4446 | 61.5167 | 123.0896 | 61.4762 | 122.8815 | 61.5713 | 61.6118 | 61.4751 | 61.5156
2466.0625 | 123.3582 | -61.4822 | 61.6104 | 0.03944 | -0.1092 | 2.0896 | 0.002454 | 0.38419 | 0.053534 | 0.19366 | 61.6195 | 0.2349 | 61.5553 | -0.03768 | 0.034501 | 61.5982 | -0.006014 | 61.3947 | 61.5217 | 61.373 | 63.5718 | 61.4847 | 61.8664 | 61.5358 | 61.6759 | 123.1018 | 61.7171 | 123.0376 | 61.4446 | 61.5167 | 123.0804 | 61.4762 | 122.8769 | 61.585 | 61.6255 | 61.5208 | 61.5614
2467.0625 | 123.4268 | -61.4777 | 61.5967 | 0.030283 | -0.072572 | 2.1033 | 0.007033 | 0.37961 | 0.048956 | 0.1845 | 61.6149 | 0.2349 | 61.5187 | -0.033101 | 0.039079 | 61.6119 | 0.007721 | 61.3947 | 61.5079 | 61.4051 | 63.581 | 61.4847 | 61.8573 | 61.5266 | 61.6622 | 123.0926 | 61.7126 | 122.9964 | 61.4446 | 61.5167 | 123.0896 | 61.4854 | 122.8724 | 61.5759 | 61.6072 | 61.4796 | 61.511
2468.0625 | 123.4222 | -61.496 | 61.6013 | 0.03944 | -0.049678 | 2.1079 | 0.029925 | 0.38877 | 0.067269 | 0.17993 | 61.6241 | 0.23032 | 61.5462 | -0.046838 | 0.034501 | 61.6074 | 0.003143 | 61.4039 | 61.5354 | 61.4463 | 63.6039 | 61.5259 | 61.8847 | 61.5632 | 61.6759 | 123.1201 | 61.7263 | 123.0422 | 61.4491 | 61.5305 | 123.1033 | 61.4991 | 122.8998 | 61.5896 | 61.6209 | 61.5117 | 61.543
2469.0625 | 123.2803 | -61.5326 | 61.6287 | 0.034862 | -0.090888 | 2.2132 | 0.029925 | 0.4025 | 0.085583 | 0.19824 | 61.6104 | 0.22574 | 61.5187 | -0.042259 | 0.039079 | 61.6028 | -0.010593 | 61.3947 | 61.5675 | 61.4417 | 63.7458 | 61.5625 | 61.9351 | 61.6182 | 61.7308 | 123.1429 | 61.7583 | 123.0513 | 61.4903 | 61.5717 | 123.1354 | 61.522 | 122.9273 | 61.5713 | 61.6209 | 61.4796 | 61.5293
2470.0625 | 123.4268 | -61.4914 | 61.6013 | 0.044018 | -0.10004 | 2.1628 | 0.025347 | 0.39792 | 0.076426 | 0.1845 | 61.6149 | 0.22574 | 61.5416 | -0.03768 | 0.034501 | 61.6119 | -0.001436 | 61.3993 | 61.5354 | 61.3913 | 63.6542 | 61.5167 | 61.8893 | 61.5678 | 61.6759 | 123.1063 | 61.7171 | 123.033 | 61.4537 | 61.5259 | 123.1033 | 61.49 | 122.8907 | 61.5804 | 61.6164 | 61.5071 | 61.543
2471.0625 | 123.4039 | -61.4914 | 61.6013 | 0.03944 | -0.10004 | 2.1171 | 0.002454 | 0.37503 | 0.071848 | 0.18908 | 61.6149 | 0.23032 | 61.5462 | -0.042259 | 0.043657 | 61.6028 | -0.001436 | 61.3901 | 61.5308 | 61.3913 | 63.6084 | 61.4938 | 61.8664 | 61.5632 | 61.6805 | 123.1063 | 61.7217 | 123.0376 | 61.4491 | 61.5351 | 123.0942 | 61.49 | 122.8815 | 61.5713 | 61.6164 | 61.5025 | 61.5476
2472.0781 | 123.2986 | -61.528 | 61.6287 | 0.03944 | -0.1092 | 2.1171 | -0.020438 | 0.37046 | 0.058113 | 0.17993 | 61.6104 | 0.23032 | 61.5187 | -0.042259 | 0.029923 | 61.6028 | -0.001436 | 61.3901 | 61.5675 | 61.4188 | 63.6451 | 61.5076 | 61.8985 | 61.5861 | 61.7079 | 123.1384 | 61.7583 | 123.0467 | 61.4858 | 61.5579 | 123.1308 | 61.5266 | 122.9181 | 61.5804 | 61.6118 | 61.4888 | 61.5202
2473.0625 | 123.4039 | -61.4777 | 61.6104 | 0.044018 | -0.1092 | 2.1216 | -0.052488 | 0.35672 | 0.048956 | 0.15246 | 61.6241 | 0.2349 | 61.5645 | -0.042259 | 0.039079 | 61.6028 | -0.001436 | 61.3947 | 61.5217 | 61.3685 | 63.5993 | 61.4252 | 61.8344 | 61.5266 | 61.6301 | 123.1018 | 61.7126 | 123.0422 | 61.4354 | 61.5167 | 123.0804 | 61.4762 | 122.8724 | 61.585 | 61.6255 | 61.5254 | 61.5659
2474.0625 | 123.3719 | -61.5097 | 61.6013 | 0.034862 | -0.1321 | 1.9843 | -0.070802 | 0.32925 | 0.035221 | 0.12499 | 61.6195 | 0.23032 | 61.5279 | -0.03768 | 0.043657 | 61.6028 | 0.003143 | 61.3856 | 61.5446 | 61.3776 | 63.494 | 61.4389 | 61.839 | 61.5449 | 61.6347 | 123.1292 | 61.74 | 123.0376 | 61.472 | 61.5534 | 123.1125 | 61.5128 | 122.8953 | 61.5759 | 61.6164 | 61.4842 | 61.5247
2475.0625 | 123.4085 | -61.4685 | 61.6013 | 0.034862 | -0.16415 | 1.8423 | -0.057066 | 0.33841 | 0.035221 | 0.12041 | 61.6195 | 0.23032 | 61.5462 | -0.033101 | 0.029923 | 61.6074 | 0.003143 | 61.3993 | 61.5034 | 61.3044 | 63.3108 | 61.4114 | 61.8069 | 61.5037 | 61.5889 | 123.088 | 61.6988 | 123.0147 | 61.4354 | 61.4984 | 123.0759 | 61.4716 | 122.8678 | 61.5896 | 61.6164 | 61.5163 | 61.543
2476.0625 | 123.2666 | -61.5005 | 61.6699 | 0.03944 | -0.16873 | 1.7096 | -0.052488 | 0.33841 | 0.030642 | 0.11583 | 61.6241 | 0.23032 | 61.5599 | -0.03768 | 0.039079 | 61.5936 | -0.006014 | 61.3993 | 61.54 | 61.3318 | 63.2101 | 61.4481 | 61.839 | 61.5312 | 61.6164 | 123.1246 | 61.7309 | 123.0605 | 61.4629 | 61.5396 | 123.0942 | 61.4945 | 122.8998 | 61.585 | 61.6301 | 61.5208 | 61.5659
2477.0625 | 123.3856 | -61.4777 | 61.6333 | 0.034862 | -0.16415 | 1.6088 | -0.043331 | 0.32925 | 0.021485 | 0.1021 | 61.6149 | 0.23032 | 61.5233 | -0.033101 | 0.034501 | 61.6074 | 0.003143 | 61.3856 | 61.5125 | 61.3135 | 63.0865 | 61.4343 | 61.8069 | 61.4991 | 61.5798 | 123.0926 | 61.708 | 123.001 | 61.4446 | 61.5122 | 123.085 | 61.4808 | 122.8632 | 61.5804 | 61.6118 | 61.4888 | 61.5202
2478.0625 | 123.3627 | -61.4639 | 61.6425 | 0.03944 | -0.14583 | 1.6134 | -0.052488 | 0.33841 | 0.021485 | 0.1021 | 61.6241 | 0.23032 | 61.5508 | -0.03768 | 0.034501 | 61.6028 | 0.003143 | 61.3993 | 61.5034 | 61.3181 | 63.0773 | 61.4114 | 61.8023 | 61.4854 | 61.566 | 123.088 | 61.6942 | 123.0147 | 61.4262 | 61.4984 | 123.0667 | 61.4671 | 122.8632 | 61.5896 | 61.6209 | 61.5163 | 61.5476
2479.0938 | 123.3261 | -61.4822 | 61.6653 | 0.03944 | -0.15041 | 1.5493 | -0.061645 | 0.27432 | -0.001406 | 0.088362 | 61.6241 | 0.22574 | 61.5508 | -0.042259 | 0.043657 | 61.5982 | 0.003143 | 61.3947 | 61.5217 | 61.3318 | 63.0315 | 61.4206 | 61.7566 | 61.4808 | 61.5706 | 123.1063 | 61.708 | 123.033 | 61.44 | 61.5259 | 123.0804 | 61.4854 | 122.8769 | 61.5804 | 61.6209 | 61.5071 | 61.5476
2480.0625 | 123.3902 | -61.4639 | 61.6241 | 0.034862 | -0.14583 | 1.4577 | -0.07538 | 0.24685 | -0.033455 | 0.056315 | 61.6241 | 0.2349 | 61.5279 | -0.033101 | 0.039079 | 61.6028 | 0.003143 | 61.3901 | 61.4988 | 61.3181 | 62.9217 | 61.3885 | 61.7108 | 61.4305 | 61.5202 | 123.088 | 61.6988 | 122.9918 | 61.4308 | 61.503 | 123.0667 | 61.4671 | 122.8541 | 61.585 | 61.6209 | 61.4888 | 61.5247
2481.0625 | 123.4222 | -61.4731 | 61.6013 | 0.044018 | -0.10004 | 1.5127 | -0.047909 | 0.24227 | -0.005985 | 0.074628 | 61.6332 | 0.22574 | 61.5599 | -0.028522 | 0.039079 | 61.5936 | -0.006014 | 61.3901 | 61.5171 | 61.373 | 62.9858 | 61.4252 | 61.7154 | 61.4671 | 61.5477 | 123.1063 | 61.6988 | 123.033 | 61.4446 | 61.5122 | 123.0667 | 61.4671 | 122.8632 | 61.5942 | 61.6393 | 61.5208 | 61.5659
2482.0781 | 123.381 | -61.4777 | 61.5692 | 0.03944 | -0.077151 | 1.4394 | -0.043331 | 0.28347 | 0.003172 | 0.079206 | 61.6195 | 0.22574 | 61.5324 | -0.051417 | 0.029923 | 61.5982 | -0.006014 | 61.3947 | 61.5171 | 61.4005 | 62.9171 | 61.4343 | 61.7611 | 61.4808 | 61.5569 | 123.0972 | 61.7034 | 123.0101 | 61.4262 | 61.5076 | 123.0759 | 61.4716 | 122.8724 | 61.5896 | 61.6255 | 61.5025 | 61.5385
2483.0625 | 123.3398 | -61.4777 | 61.6425 | 0.044018 | -0.10004 | 1.3204 | -0.066223 | 0.25143 | 0.00775 | 0.060893 | 61.6287 | 0.2349 | 61.5416 | -0.046838 | 0.034501 | 61.5936 | -0.001436 | 61.3993 | 61.5217 | 61.3776 | 62.798 | 61.4114 | 61.7291 | 61.4854 | 61.5386 | 123.1063 | 61.7126 | 123.0193 | 61.4308 | 61.5122 | 123.0713 | 61.4762 | 122.8769 | 61.5942 | 61.6301 | 61.5071 | 61.543
2484.0781 | 123.2986 | -61.4777 | 61.6562 | 0.048597 | -0.10462 | 1.2654 | -0.066223 | 0.27432 | -0.005985 | 0.060893 | 61.6287 | 0.22574 | 61.5691 | -0.042259 | 0.034501 | 61.5936 | -0.006014 | 61.3947 | 61.5263 | 61.373 | 62.7431 | 61.4114 | 61.752 | 61.4717 | 61.5386 | 123.1063 | 61.7034 | 123.0467 | 61.4354 | 61.5122 | 123.0713 | 61.4716 | 122.8724 | 61.5942 | 61.6347 | 61.5346 | 61.5751
2485.0625 | 123.381 | -61.4456 | 61.6562 | 0.034862 | -0.11378 | 1.238 | -0.070802 | 0.25601 | -0.024298 | 0.065472 | 61.6241 | 0.2349 | 61.5599 | -0.042259 | 0.039079 | 61.5936 | -0.001436 | 61.3901 | 61.4805 | 61.3318 | 62.6836 | 61.3748 | 61.7016 | 61.4213 | 61.5111 | 123.0697 | 61.6805 | 123.0055 | 61.4034 | 61.4847 | 123.0392 | 61.4442 | 122.8357 | 61.585 | 61.6255 | 61.5208 | 61.5614
2486.0625 | 123.3032 | -61.5005 | 61.6608 | 0.03944 | -0.095467 | 1.3021 | -0.061645 | 0.26516 | -0.015142 | 0.065472 | 61.6287 | 0.2349 | 61.5187 | -0.033101 | 0.039079 | 61.5982 | 0.003143 | 61.3901 | 61.54 | 61.4051 | 62.8026 | 61.4389 | 61.7657 | 61.4854 | 61.566 | 123.1292 | 61.7354 | 123.0193 | 61.4674 | 61.5396 | 123.0988 | 61.5037 | 122.8907 | 61.5896 | 61.6255 | 61.4796 | 61.5156
2487.0625 | 123.4177 | -61.4868 | 61.6104 | 0.034862 | -0.031363 | 1.4623 | -0.043331 | 0.29721 | 0.016907 | 0.10668 | 61.6195 | 0.23032 | 61.5462 | -0.033101 | 0.029923 | 61.6028 | -0.001436 | 61.3947 | 61.5217 | 61.4555 | 62.9491 | 61.4435 | 61.784 | 61.5037 | 61.5935 | 123.1063 | 61.7171 | 123.033 | 61.4537 | 61.5167 | 123.0896 | 61.4854 | 122.8815 | 61.5896 | 61.6209 | 61.5163 | 61.5476
2488.0625 | 123.3582 | -61.4777 | 61.6425 | 0.03944 | -0.0451 | 1.444 | -0.038752 | 0.31094 | 0.012329 | 0.097519 | 61.6287 | 0.23032 | 61.5553 | -0.042259 | 0.034501 | 61.5982 | -0.010593 | 61.3993 | 61.5171 | 61.4326 | 62.9217 | 61.4389 | 61.7886 | 61.49 | 61.5752 | 123.1063 | 61.708 | 123.033 | 61.4354 | 61.5122 | 123.0759 | 61.4671 | 122.8769 | 61.5942 | 61.6393 | 61.5208 | 61.5659
2489.0781 | 123.2849 | -61.5005 | 61.6608 | 0.03944 | 0.005267 | 1.5997 | -0.01586 | 0.35214 | 0.030642 | 0.13414 | 61.6195 | 0.23948 | 61.5553 | -0.03768 | 0.043657 | 61.6074 | -0.001436 | 61.4039 | 61.54 | 61.5058 | 63.1002 | 61.4847 | 61.8527 | 61.5312 | 61.6347 | 123.1201 | 61.74 | 123.0559 | 61.4629 | 61.5442 | 123.1079 | 61.4991 | 122.9044 | 61.5759 | 61.6209 | 61.5117 | 61.5568
2490.0625 | 123.3032 | -61.4914 | 61.6699 | 0.044018 | -0.013048 | 1.4669 | -0.025017 | 0.30636 | 0.016907 | 0.11583 | 61.6241 | 0.23032 | 61.5187 | -0.03768 | 0.039079 | 61.5982 | -0.001436 | 61.3901 | 61.5354 | 61.4783 | 62.9583 | 61.4664 | 61.7978 | 61.5083 | 61.6072 | 123.1155 | 61.7217 | 123.0101 | 61.4537 | 61.5305 | 123.0896 | 61.49 | 122.8815 | 61.585 | 61.6255 | 61.4796 | 61.5202
2491.0625 | 123.3215 | -61.5005 | 61.6745 | 0.03944 | -0.031363 | 1.4028 | -0.043331 | 0.29263 | -0.005985 | 0.1021 | 61.6149 | 0.22574 | 61.5416 | -0.03768 | 0.034501 | 61.6028 | -0.001436 | 61.3947 | 61.54 | 61.4692 | 62.9033 | 61.4572 | 61.7932 | 61.4946 | 61.6026 | 123.1155 | 61.7263 | 123.0422 | 61.4629 | 61.535 | 123.1033 | 61.4991 | 122.8953 | 61.5804 | 61.6164 | 61.5071 | 61.543
2492.0625 | 123.2849 | -61.4777 | 61.6745 | 0.03944 | -0.022205 | 1.3753 | -0.029595 | 0.2789 | -0.04719 | 0.1021 | 61.6287 | 0.23032 | 61.5691 | -0.03768 | 0.043657 | 61.6028 | -0.001436 | 61.3947 | 61.5171 | 61.4555 | 62.853 | 61.4481 | 61.7566 | 61.4305 | 61.5798 | 123.1063 | 61.708 | 123.0467 | 61.44 | 61.5213 | 123.0804 | 61.4762 | 122.8724 | 61.585 | 61.6301 | 61.5254 | 61.5705
2493.0625 | 123.3307 | -61.4914 | 61.6699 | 0.034862 | 0.037319 | 1.444 | -0.038752 | 0.31552 | -0.038034 | 0.12041 | 61.6195 | 0.22574 | 61.5508 | -0.046838 | 0.034501 | 61.5982 | -0.001436 | 61.3947 | 61.5263 | 61.5287 | 62.9354 | 61.4526 | 61.8069 | 61.4534 | 61.6118 | 123.1109 | 61.7171 | 123.0422 | 61.4446 | 61.5259 | 123.0896 | 61.49 | 122.8861 | 61.585 | 61.6209 | 61.5163 | 61.5522
2494.0625 | 123.3627 | -61.4822 | 61.6562 | 0.048597 | -0.022205 | 1.4577 | -0.034174 | 0.29721 | -0.038034 | 0.12041 | 61.6195 | 0.2349 | 61.5187 | -0.03768 | 0.039079 | 61.6028 | -0.001436 | 61.3856 | 61.5308 | 61.46 | 62.94 | 61.4481 | 61.7794 | 61.4442 | 61.6026 | 123.1018 | 61.7171 | 123.001 | 61.4446 | 61.5213 | 123.085 | 61.4808 | 122.8678 | 61.5804 | 61.6209 | 61.4796 | 61.5202
2495.0625 | 123.317 | -61.5097 | 61.6699 | 0.044018 | 0.041898 | 1.4852 | -0.01586 | 0.32468 | -0.005985 | 0.15246 | 61.6195 | 0.23032 | 61.537 | -0.042259 | 0.043657 | 61.5936 | -0.001436 | 61.4039 | 61.5537 | 61.5516 | 62.9949 | 61.4938 | 61.8344 | 61.5037 | 61.6622 | 123.1292 | 61.74 | 123.0467 | 61.4674 | 61.5534 | 123.1033 | 61.5083 | 122.9136 | 61.5759 | 61.6209 | 61.4934 | 61.5385
2496.0625 | 123.2712 | -61.5234 | 61.6653 | 0.044018 | 0.019004 | 1.6729 | -0.002124 | 0.32925 | 0.021485 | 0.15246 | 61.6287 | 0.22574 | 61.5553 | -0.03768 | 0.039079 | 61.5936 | -0.001436 | 61.3993 | 61.5675 | 61.5424 | 63.1964 | 61.5213 | 61.8527 | 61.5449 | 61.6759 | 123.1521 | 61.7492 | 123.0788 | 61.4858 | 61.5625 | 123.1171 | 61.522 | 122.9227 | 61.5896 | 61.6301 | 61.5163 | 61.5568
2497.0625 | 123.2986 | -61.4914 | 61.6608 | 0.034862 | 0.019004 | 1.4532 | -0.025017 | 0.31552 | 0.021485 | 0.12957 | 61.6241 | 0.23032 | 61.5553 | -0.028522 | 0.034501 | 61.6074 | -0.001436 | 61.3901 | 61.5263 | 61.5104 | 62.9445 | 61.4664 | 61.8069 | 61.5129 | 61.621 | 123.1155 | 61.7217 | 123.0467 | 61.4629 | 61.5259 | 123.0988 | 61.49 | 122.8815 | 61.5896 | 61.6255 | 61.5208 | 61.5568
2498.0625 | 123.317 | -61.4868 | 61.6425 | 0.044018 | -0.008469 | 1.2883 | -0.011281 | 0.2789 | 0.003172 | 0.097519 | 61.6241 | 0.2349 | 61.5279 | -0.033101 | 0.043657 | 61.5982 | -0.001436 | 61.3856 | 61.5308 | 61.4783 | 62.7751 | 61.4755 | 61.7657 | 61.49 | 61.5843 | 123.1109 | 61.7217 | 123.0147 | 61.4537 | 61.5305 | 123.085 | 61.4854 | 122.8724 | 61.5804 | 61.6255 | 61.4842 | 61.5293
2499.1094 | 123.2758 | -61.5051 | 61.6928 | 0.044018 | -0.017627 | 1.2151 | -0.01586 | 0.25143 | -0.015142 | 0.097519 | 61.6287 | 0.2349 | 61.5462 | -0.033101 | 0.039079 | 61.6028 | -0.001436 | 61.3856 | 61.5491 | 61.4875 | 62.7202 | 61.4893 | 61.7566 | 61.49 | 61.6026 | 123.1338 | 61.74 | 123.0513 | 61.472 | 61.5442 | 123.1079 | 61.5037 | 122.8907 | 61.5896 | 61.6301 | 61.5071 | 61.5476
2500.0625 | 123.4085 | -61.4685 | 61.6516 | 0.044018 | -0.054257 | 1.0777 | -0.043331 | 0.22854 | -0.01972 | 0.060893 | 61.6241 | 0.2349 | 61.5645 | -0.042259 | 0.034501 | 61.5982 | -0.001436 | 61.3901 | 61.5125 | 61.4142 | 62.5462 | 61.4252 | 61.697 | 61.4488 | 61.5294 | 123.0926 | 61.7034 | 123.033 | 61.4262 | 61.503 | 123.0667 | 61.4671 | 122.8586 | 61.5896 | 61.6255 | 61.53 | 61.5659
2501.1562 | 123.2849 | -61.4868 | 61.6791 | 0.044018 | -0.090888 | 1.0731 | -0.052488 | 0.18276 | -0.028877 | 0.038003 | 61.6424 | 0.23032 | 61.5691 | -0.042259 | 0.039079 | 61.5982 | -0.006014 | 61.3947 | 61.5308 | 61.3959 | 62.5599 | 61.4343 | 61.6696 | 61.4579 | 61.5248 | 123.1292 | 61.7171 | 123.0559 | 61.4446 | 61.5259 | 123.085 | 61.4808 | 122.8815 | 61.6033 | 61.6484 | 61.53 | 61.5751
2502.0625 | 123.349 | -61.4822 | 61.6516 | 0.03944 | -0.040521 | 1.1922 | -0.034174 | 0.24685 | -0.015142 | 0.079206 | 61.6241 | 0.22574 | 61.5324 | -0.03768 | 0.043657 | 61.6028 | -0.006014 | 61.3993 | 61.5217 | 61.4417 | 62.6744 | 61.4481 | 61.7291 | 61.4671 | 61.5614 | 123.1063 | 61.708 | 123.0147 | 61.4446 | 61.5259 | 123.085 | 61.4762 | 122.8815 | 61.5804 | 61.6301 | 61.4888 | 61.5385
2503.0625 | 123.3124 | -61.5005 | 61.6974 | 0.03944 | 0.03274 | 1.1922 | 0.002454 | 0.25143 | 0.003172 | 0.11125 | 61.6241 | 0.22574 | 61.5233 | -0.042259 | 0.029923 | 61.5936 | -0.001436 | 61.3993 | 61.54 | 61.5333 | 62.6927 | 61.503 | 61.752 | 61.5037 | 61.6118 | 123.1246 | 61.7263 | 123.0238 | 61.4583 | 61.5305 | 123.0942 | 61.4991 | 122.8998 | 61.5942 | 61.6255 | 61.4934 | 61.5247
2504.125 | 123.3215 | -61.5051 | 61.6516 | 0.048597 | 0.069371 | 1.2471 | 0.029925 | 0.29263 | 0.021485 | 0.13414 | 61.6241 | 0.22574 | 61.5599 | -0.033101 | 0.039079 | 61.5982 | -0.001436 | 61.3947 | 61.5537 | 61.5745 | 62.7522 | 61.5351 | 61.7978 | 61.5266 | 61.6393 | 123.1292 | 61.7309 | 123.065 | 61.472 | 61.5442 | 123.1033 | 61.5037 | 122.8998 | 61.585 | 61.6255 | 61.5208 | 61.5614
2505.0625 | 123.2895 | -61.5005 | 61.6699 | 0.048597 | 0.037319 | 1.1876 | 0.011611 | 0.26974 | 0.00775 | 0.092941 | 61.6287 | 0.2349 | 61.5691 | -0.03768 | 0.039079 | 61.5982 | -0.006014 | 61.3901 | 61.5491 | 61.5379 | 62.6881 | 61.5122 | 61.7703 | 61.5083 | 61.5935 | 123.1292 | 61.7354 | 123.0696 | 61.4629 | 61.5396 | 123.0988 | 61.4945 | 122.8907 | 61.5896 | 61.6347 | 61.53 | 61.5751
2506.0781 | 123.3856 | -61.4777 | 61.615 | 0.03944 | 0.051056 | 1.2013 | 0.01619 | 0.26516 | 0.00775 | 0.1021 | 61.6195 | 0.2349 | 61.5233 | -0.03768 | 0.034501 | 61.5982 | -0.006014 | 61.381 | 61.5171 | 61.5287 | 62.679 | 61.4939 | 61.7428 | 61.4854 | 61.5798 | 123.0972 | 61.7126 | 123.001 | 61.44 | 61.5122 | 123.0759 | 61.4716 | 122.8586 | 61.585 | 61.6255 | 61.4888 | 61.5293
2507.0625 | 123.3719 | -61.5051 | 61.5829 | 0.044018 | 0.023583 | 1.1098 | 0.007033 | 0.25143 | 0.003172 | 0.065472 | 61.6241 | 0.2349 | 61.5233 | -0.03768 | 0.039079 | 61.5982 | 0.003143 | 61.3856 | 61.5491 | 61.5287 | 62.6149 | 61.5122 | 61.7566 | 61.5083 | 61.5706 | 123.1292 | 61.74 | 123.0284 | 61.4674 | 61.5442 | 123.1033 | 61.5083 | 122.8907 | 61.585 | 61.6209 | 61.4842 | 61.5202
2508.0625 | 123.3353 | -61.4868 | 61.6379 | 0.03944 | 0.092265 | 1.2151 | 0.007033 | 0.29721 | 0.016907 | 0.097519 | 61.6195 | 0.23032 | 61.5645 | -0.03768 | 0.034501 | 61.5936 | 0.003143 | 61.3947 | 61.5263 | 61.5791 | 62.7019 | 61.4938 | 61.784 | 61.5037 | 61.5843 | 123.1063 | 61.7171 | 123.0513 | 61.4491 | 61.5213 | 123.0804 | 61.49 | 122.8815 | 61.585 | 61.6164 | 61.53 | 61.5614
2509.0781 | 123.3078 | -61.4822 | 61.6608 | 0.044018 | 0.11974 | 1.2242 | 0.020768 | 0.32468 | 0.044377 | 0.12041 | 61.6241 | 0.2349 | 61.5645 | -0.03768 | 0.034501 | 61.5936 | -0.001436 | 61.3993 | 61.5263 | 61.602 | 62.7065 | 61.503 | 61.8069 | 61.5266 | 61.6026 | 123.1063 | 61.7171 | 123.0467 | 61.4446 | 61.5167 | 123.0759 | 61.4808 | 122.8815 | 61.5896 | 61.6255 | 61.53 | 61.5659
2510.0781 | 123.3948 | -61.5189 | 61.6058 | 0.034862 | 0.064792 | 1.1784 | 0.01619 | 0.31552 | 0.039799 | 0.12041 | 61.6195 | 0.23032 | 61.5324 | -0.042259 | 0.039079 | 61.6028 | -0.006014 | 61.3856 | 61.5537 | 61.5837 | 62.6973 | 61.535 | 61.8344 | 61.5587 | 61.6393 | 123.1384 | 61.7492 | 123.0513 | 61.4766 | 61.5579 | 123.1216 | 61.5128 | 122.9044 | 61.5804 | 61.6255 | 61.4934 | 61.5385
2511.0625 | 123.3536 | -61.4868 | 61.6425 | 0.044018 | 0.03274 | 1.2196 | 0.020768 | 0.30636 | 0.030642 | 0.097519 | 61.6241 | 0.2349 | 61.5233 | -0.033101 | 0.029923 | 61.5982 | 0.003143 | 61.3901 | 61.5308 | 61.5196 | 62.7065 | 61.5076 | 61.7932 | 61.5175 | 61.5843 | 123.1109 | 61.7217 | 123.0101 | 61.4537 | 61.5167 | 123.085 | 61.49 | 122.8769 | 61.5942 | 61.6209 | 61.4934 | 61.5202
2512.0625 | 123.2758 | -61.5143 | 61.6608 | 0.044018 | 0.019004 | 1.2837 | 0.007033 | 0.29721 | 0.030642 | 0.088362 | 61.6241 | 0.22574 | 61.5508 | -0.042259 | 0.043657 | 61.5982 | -0.001436 | 61.3993 | 61.5583 | 61.5333 | 62.798 | 61.5213 | 61.8115 | 61.5449 | 61.6026 | 123.1384 | 61.74 | 123.065 | 61.472 | 61.5579 | 123.1125 | 61.5128 | 122.9136 | 61.5804 | 61.6255 | 61.5071 | 61.5522
2513.0625 | 123.2895 | -61.5097 | 61.6608 | 0.03944 | 0.019004 | 1.1281 | -0.034174 | 0.26516 | 0.003172 | 0.051737 | 61.6332 | 0.2349 | 61.5553 | -0.03768 | 0.034501 | 61.5936 | -0.001436 | 61.3947 | 61.5491 | 61.5287 | 62.6378 | 61.4755 | 61.7749 | 61.5129 | 61.5614 | 123.143 | 61.7446 | 123.065 | 61.472 | 61.5442 | 123.1033 | 61.5083 | 122.9044 | 61.5987 | 61.6347 | 61.5208 | 61.5568
2514.0781 | 123.3719 | -61.496 | 61.6058 | 0.034862 | -0.072572 | 0.94493 | -0.043331 | 0.20565 | -0.033455 | -0.007779 | 61.6241 | 0.22574 | 61.537 | -0.042259 | 0.034501 | 61.5936 | -0.001436 | 61.3856 | 61.5308 | 61.4234 | 62.4409 | 61.4526 | 61.7016 | 61.4625 | 61.4882 | 123.1201 | 61.7217 | 123.033 | 61.4537 | 61.5305 | 123.0896 | 61.4945 | 122.8815 | 61.5896 | 61.6255 | 61.5025 | 61.5385
2515.0625 | 123.317 | -61.4639 | 61.6516 | 0.048597 | 0.13347 | 1.1601 | -0.006703 | 0.27432 | 0.044377 | 0.16161 | 61.6241 | 0.2349 | 61.5233 | -0.042259 | 0.029923 | 61.5982 | 0.003143 | 61.3993 | 61.5125 | 61.5974 | 62.6241 | 61.4572 | 61.7382 | 61.5083 | 61.6255 | 123.088 | 61.6988 | 122.9872 | 61.4217 | 61.4939 | 123.0621 | 61.4671 | 122.8632 | 61.5942 | 61.6209 | 61.4934 | 61.5202
2516.0625 | 123.3536 | -61.5051 | 61.6058 | 0.03944 | 0.051056 | 1.0182 | -0.020438 | 0.26516 | 0.035221 | 0.12499 | 61.6287 | 0.22574 | 61.5279 | -0.042259 | 0.039079 | 61.5936 | -0.006014 | 61.4039 | 61.5446 | 61.5562 | 62.5233 | 61.4847 | 61.7703 | 61.5403 | 61.6301 | 123.1338 | 61.7309 | 123.033 | 61.4629 | 61.5442 | 123.0988 | 61.4991 | 122.909 | 61.5896 | 61.6347 | 61.4888 | 61.5339
2517.0625 | 123.3444 | -61.4777 | 61.6287 | 0.03944 | 0.014425 | 0.94951 | -0.029595 | 0.22854 | 0.026064 | 0.092941 | 61.6287 | 0.2349 | 61.5645 | -0.03768 | 0.048236 | 61.5982 | 0.003143 | 61.3901 | 61.5171 | 61.4921 | 62.4272 | 61.4481 | 61.7062 | 61.5037 | 61.5706 | 123.1063 | 61.7126 | 123.0422 | 61.44 | 61.5259 | 123.0759 | 61.4808 | 122.8678 | 61.5804 | 61.6255 | 61.5163 | 61.5614
2518.0938 | 123.3673 | -61.4777 | 61.6196 | 0.030283 | -0.12752 | 0.77552 | -0.07538 | 0.14614 | -0.033455 | -0.044405 | 61.6332 | 0.23032 | 61.5782 | -0.042259 | 0.043657 | 61.5891 | -0.001436 | 61.3856 | 61.5079 | 61.3501 | 62.2532 | 61.4023 | 61.6238 | 61.4442 | 61.4333 | 123.1109 | 61.708 | 123.0559 | 61.4354 | 61.5213 | 123.0667 | 61.4762 | 122.8632 | 61.5896 | 61.6347 | 61.5346 | 61.5797
2519.0625 | 123.3627 | -61.4548 | 61.6287 | 0.03944 | -0.12752 | 0.77094 | -0.079959 | 0.14614 | -0.005985 | -0.03067 | 61.6332 | 0.23032 | 61.5737 | -0.033101 | 0.039079 | 61.5936 | -0.001436 | 61.3856 | 61.4942 | 61.3273 | 62.2257 | 61.3748 | 61.6009 | 61.4488 | 61.4241 | 123.088 | 61.6851 | 123.0284 | 61.4217 | 61.4939 | 123.0484 | 61.4533 | 122.8403 | 61.5942 | 61.6347 | 61.5346 | 61.5751
2520.0625 | 123.3353 | -61.4914 | 61.6562 | 0.03944 | -0.040521 | 0.7801 | -0.043331 | 0.20565 | 0.035221 | -0.016936 | 61.6332 | 0.23032 | 61.5599 | -0.03768 | 0.039079 | 61.5891 | 0.003143 | 61.3856 | 61.5308 | 61.4509 | 62.2715 | 61.4481 | 61.697 | 61.5266 | 61.4745 | 123.1246 | 61.7217 | 123.0513 | 61.4537 | 61.5305 | 123.0804 | 61.4945 | 122.8769 | 61.5942 | 61.6301 | 61.5208 | 61.5568
2521.0781 | 123.3536 | -61.4639 | 61.6058 | 0.044018 | -0.12294 | 0.66105 | -0.084537 | 0.15071 | 0.00775 | -0.076452 | 61.6287 | 0.2349 | 61.5279 | -0.042259 | 0.029923 | 61.5799 | -0.006014 | 61.381 | 61.5079 | 61.341 | 62.125 | 61.3794 | 61.6146 | 61.4717 | 61.3875 | 123.0926 | 61.6988 | 122.9918 | 61.4217 | 61.4939 | 123.0438 | 61.4579 | 122.8449 | 61.5987 | 61.6347 | 61.4979 | 61.5339
2522.0625 | 123.381 | -61.4731 | 61.6379 | 0.034862 | 0.005267 | 0.83962 | -0.057066 | 0.22396 | 0.044377 | -0.03067 | 61.6332 | 0.2349 | 61.5599 | -0.033101 | 0.039079 | 61.5891 | 0.003143 | 61.3856 | 61.5079 | 61.4784 | 62.3127 | 61.416 | 61.697 | 61.5175 | 61.4424 | 123.1063 | 61.708 | 123.033 | 61.44 | 61.5122 | 123.0621 | 61.4762 | 122.8586 | 61.5942 | 61.6301 | 61.5208 | 61.5568
2523.0625 | 123.2803 | -61.4731 | 61.6837 | 0.03944 | -0.013048 | 0.7801 | -0.066223 | 0.24685 | 0.067269 | -0.026092 | 61.6332 | 0.23032 | 61.5691 | -0.042259 | 0.034501 | 61.6028 | -0.001436 | 61.3856 | 61.5125 | 61.46 | 62.2532 | 61.4069 | 61.7199 | 61.5404 | 61.447 | 123.1063 | 61.7034 | 123.0422 | 61.4308 | 61.5076 | 123.0759 | 61.4716 | 122.8586 | 61.5987 | 61.6347 | 61.5346 | 61.5705
2524.0625 | 123.3032 | -61.5005 | 61.6699 | 0.03944 | 0.069371 | 0.78926 | -0.043331 | 0.27432 | 0.062691 | -0.048983 | 61.6332 | 0.23948 | 61.5553 | -0.033101 | 0.034501 | 61.5982 | -0.006014 | 61.3856 | 61.54 | 61.5699 | 62.2898 | 61.4572 | 61.7749 | 61.5632 | 61.4516 | 123.1338 | 61.74 | 123.0559 | 61.4674 | 61.535 | 123.0988 | 61.4945 | 122.8861 | 61.5987 | 61.6393 | 61.5208 | 61.5614
2525.0625 | 123.3032 | -61.4731 | 61.6791 | 0.03944 | 0.20216 | 0.98614 | -0.025017 | 0.32925 | 0.099318 | 0.051737 | 61.6332 | 0.23948 | 61.5416 | -0.042259 | 0.039079 | 61.5936 | -0.001436 | 61.3901 | 61.5125 | 61.6752 | 62.4592 | 61.4481 | 61.8023 | 61.5724 | 61.5248 | 123.1063 | 61.7126 | 123.0147 | 61.4308 | 61.5122 | 123.0667 | 61.4716 | 122.8632 | 61.5942 | 61.6347 | 61.5025 | 61.543
2526.0625 | 123.3719 | -61.4868 | 61.647 | 0.034862 | 0.20674 | 0.99987 | -0.006703 | 0.35214 | 0.1039 | 0.038003 | 61.6195 | 0.2349 | 61.5324 | -0.03768 | 0.039079 | 61.6028 | -0.001436 | 61.3856 | 61.5217 | 61.6936 | 62.4867 | 61.4801 | 61.839 | 61.5907 | 61.5248 | 123.1063 | 61.7217 | 123.0193 | 61.4491 | 61.5259 | 123.0896 | 61.4854 | 122.8724 | 61.5804 | 61.6209 | 61.4934 | 61.5339
2527.0625 | 123.3582 | -61.5097 | 61.6608 | 0.044018 | 0.15179 | 0.94035 | 0.002454 | 0.36588 | 0.1039 | 0.038003 | 61.6287 | 0.2349 | 61.5141 | -0.042259 | 0.039079 | 61.6028 | -0.001436 | 61.3856 | 61.5537 | 61.6615 | 62.4501 | 61.5122 | 61.8756 | 61.6136 | 61.5477 | 123.1384 | 61.7446 | 123.0238 | 61.4674 | 61.5488 | 123.1125 | 61.5083 | 122.8953 | 61.5896 | 61.6301 | 61.4751 | 61.5156
2528.0781 | 123.2712 | -61.5097 | 61.6287 | 0.044018 | 0.28915 | 0.83962 | 0.002454 | 0.35214 | 0.10848 | 0.015112 | 61.6195 | 0.23032 | 61.5324 | -0.03768 | 0.034501 | 61.5982 | -0.001436 | 61.3856 | 61.5537 | 61.7989 | 62.3493 | 61.5122 | 61.8618 | 61.6182 | 61.5248 | 123.1292 | 61.74 | 123.0422 | 61.472 | 61.5442 | 123.1079 | 61.5083 | 122.8953 | 61.585 | 61.6209 | 61.4979 | 61.5339
2529.0625 | 123.3719 | -61.4822 | 61.615 | 0.03944 | 0.26626 | 0.91288 | 0.025347 | 0.41624 | 0.15884 | 0.07005 | 61.6287 | 0.2349 | 61.5553 | -0.042259 | 0.043657 | 61.6028 | 0.003143 | 61.3993 | 61.5217 | 61.7485 | 62.3951 | 61.5076 | 61.8985 | 61.6411 | 61.5523 | 123.1109 | 61.7171 | 123.0376 | 61.44 | 61.5259 | 123.085 | 61.4854 | 122.8815 | 61.585 | 61.6255 | 61.5117 | 61.5522
2530.0781 | 123.3536 | -61.5051 | 61.5921 | 0.044018 | 0.18842 | 0.82588 | 0.029925 | 0.38419 | 0.16799 | 0.024268 | 61.6287 | 0.23032 | 61.5553 | -0.03768 | 0.029923 | 61.6028 | -0.001436 | 61.3856 | 61.5491 | 61.6935 | 62.331 | 61.5351 | 61.8893 | 61.6731 | 61.5294 | 123.1338 | 61.7354 | 123.0605 | 61.4674 | 61.535 | 123.1079 | 61.5037 | 122.8907 | 61.5987 | 61.6301 | 61.5254 | 61.5568
2531.0625 | 123.3719 | -61.4502 | 61.6287 | 0.044018 | 0.22047 | 0.79841 | 0.029925 | 0.37046 | 0.14968 | 0.051737 | 61.6149 | 0.23032 | 61.5324 | -0.03768 | 0.039079 | 61.6028 | -0.006014 | 61.3901 | 61.4942 | 61.6707 | 62.2486 | 61.4801 | 61.8207 | 61.5999 | 61.5019 | 123.0651 | 61.6805 | 122.9826 | 61.4125 | 61.4893 | 123.053 | 61.4442 | 122.8403 | 61.5759 | 61.6209 | 61.4934 | 61.5385
2532.0625 | 123.3902 | -61.4594 | 61.6425 | 0.048597 | 0.21131 | 0.69768 | 0.025347 | 0.35672 | 0.1451 | 0.042581 | 61.6287 | 0.22574 | 61.5462 | -0.042259 | 0.039079 | 61.5936 | -0.001436 | 61.381 | 61.5079 | 61.6707 | 62.157 | 61.4847 | 61.8161 | 61.6045 | 61.5019 | 123.088 | 61.6851 | 123.0055 | 61.4171 | 61.4984 | 123.053 | 61.4579 | 122.8403 | 61.5896 | 61.6301 | 61.5071 | 61.5476
2533.0625 | 123.3124 | -61.4777 | 61.6425 | 0.048597 | 0.24794 | 0.74805 | 0.029925 | 0.35672 | 0.16342 | 0.060893 | 61.6195 | 0.22574 | 61.5645 | -0.033101 | 0.039079 | 61.5936 | 0.003143 | 61.3901 | 61.5263 | 61.7256 | 62.2257 | 61.5076 | 61.8344 | 61.6411 | 61.5386 | 123.0972 | 61.7034 | 123.0422 | 61.4446 | 61.5167 | 123.0713 | 61.4808 | 122.8678 | 61.5804 | 61.6164 | 61.5254 | 61.5614
2534.0781 | 123.3215 | -61.4822 | 61.6608 | 0.048597 | 0.22047 | 0.67021 | 0.011611 | 0.35214 | 0.16342 | 0.028846 | 61.6332 | 0.23948 | 61.5645 | -0.03768 | 0.039079 | 61.5936 | 0.003143 | 61.3947 | 61.5308 | 61.7027 | 62.1525 | 61.4939 | 61.8344 | 61.6457 | 61.5111 | 123.1155 | 61.7217 | 123.0467 | 61.4446 | 61.5213 | 123.0759 | 61.4854 | 122.8769 | 61.5942 | 61.6301 | 61.5254 | 61.5614
2535.0625 | 123.2574 | -61.4914 | 61.702 | 0.044018 | 0.22505 | 0.5878 | 0.020768 | 0.34757 | 0.1451 | -0.035248 | 61.6241 | 0.23032 | 61.5233 | -0.033101 | 0.039079 | 61.6028 | -0.006014 | 61.3764 | 61.5354 | 61.7164 | 62.0792 | 61.5122 | 61.839 | 61.6365 | 61.4561 | 123.1155 | 61.7217 | 123.0147 | 61.4583 | 61.5305 | 123.0942 | 61.4854 | 122.8678 | 61.585 | 61.6301 | 61.4842 | 61.5293
2536.0625 | 123.3627 | -61.4868 | 61.6562 | 0.048597 | 0.24337 | 0.54659 | 0.039082 | 0.36588 | 0.14968 | -0.035248 | 61.6241 | 0.23032 | 61.537 | -0.03768 | 0.039079 | 61.6028 | -0.010593 | 61.381 | 61.5354 | 61.7302 | 62.0334 | 61.5259 | 61.8527 | 61.6365 | 61.4516 | 123.1109 | 61.7171 | 123.0238 | 61.4491 | 61.5259 | 123.0896 | 61.4762 | 122.8678 | 61.585 | 61.6347 | 61.4979 | 61.5476
2537.0781 | 123.3261 | -61.5234 | 61.6104 | 0.053175 | 0.22047 | 0.54659 | 0.034504 | 0.36588 | 0.15884 | -0.039826 | 61.6287 | 0.23032 | 61.5691 | -0.03768 | 0.029923 | 61.6028 | -0.001436 | 61.381 | 61.5766 | 61.7439 | 62.07 | 61.5579 | 61.8893 | 61.6823 | 61.4836 | 123.1521 | 61.7538 | 123.0925 | 61.4858 | 61.5534 | 123.1262 | 61.522 | 122.9044 | 61.5987 | 61.6301 | 61.5392 | 61.5705
2538.0625 | 123.2895 | -61.496 | 61.6882 | 0.053175 | 0.17011 | 0.52828 | -0.002124 | 0.33383 | 0.1451 | -0.044405 | 61.6287 | 0.24405 | 61.5553 | -0.03768 | 0.039079 | 61.5936 | 0.003143 | 61.3993 | 61.5491 | 61.6661 | 62.0242 | 61.4938 | 61.8298 | 61.6411 | 61.4516 | 123.1246 | 61.74 | 123.0513 | 61.4583 | 61.5351 | 123.0896 | 61.4991 | 122.8953 | 61.5896 | 61.6255 | 61.5163 | 61.5522
2539.0781 | 123.3582 | -61.4822 | 61.6379 | 0.057754 | 0.33494 | 0.82131 | 0.034504 | 0.48033 | 0.21378 | 0.083784 | 61.6195 | 0.23032 | 61.5233 | -0.046838 | 0.034501 | 61.5982 | -0.010593 | 61.3856 | 61.54 | 61.8172 | 62.3035 | 61.5167 | 61.9626 | 61.696 | 61.566 | 123.1018 | 61.7126 | 123.0055 | 61.4354 | 61.5167 | 123.0804 | 61.4716 | 122.8678 | 61.585 | 61.6301 | 61.4888 | 61.5339
2540.0625 | 123.3078 | -61.5051 | 61.6745 | 0.048597 | 0.30747 | 0.70684 | 0.01619 | 0.43912 | 0.18631 | 0.015112 | 61.6287 | 0.22574 | 61.5553 | -0.03768 | 0.043657 | 61.5982 | -0.001436 | 61.3993 | 61.5537 | 61.8126 | 62.212 | 61.5213 | 61.9443 | 61.6914 | 61.5202 | 123.1338 | 61.7309 | 123.0605 | 61.4674 | 61.5488 | 123.1033 | 61.5037 | 122.9044 | 61.585 | 61.6301 | 61.5117 | 61.5568
2541.0781 | 123.3948 | -61.4548 | 61.6379 | 0.044018 | 0.32578 | 0.74805 | 0.043661 | 0.46202 | 0.17715 | 0.010533 | 61.6287 | 0.22574 | 61.5645 | -0.03768 | 0.034501 | 61.6028 | -0.001436 | 61.3993 | 61.4988 | 61.7806 | 62.2028 | 61.4984 | 61.9168 | 61.6319 | 61.4653 | 123.0834 | 61.6805 | 123.0193 | 61.4171 | 61.4893 | 123.0576 | 61.4533 | 122.8541 | 61.5942 | 61.6301 | 61.53 | 61.5659
2542.0625 | 123.4222 | -61.4822 | 61.6241 | 0.057754 | 0.38073 | 0.83962 | 0.071132 | 0.51695 | 0.18631 | 0.033424 | 61.6241 | 0.22574 | 61.5553 | -0.046838 | 0.029923 | 61.5891 | -0.006014 | 61.3901 | 61.54 | 61.863 | 62.3219 | 61.5534 | 61.9992 | 61.6685 | 61.5157 | 123.1063 | 61.708 | 123.0376 | 61.4354 | 61.5122 | 123.0713 | 61.4762 | 122.8724 | 61.5942 | 61.6301 | 61.5254 | 61.5614
2543.0625 | 123.3124 | -61.5097 | 61.647 | 0.053175 | 0.34868 | 0.8442 | 0.071132 | 0.50779 | 0.18631 | 0.005955 | 61.6195 | 0.23032 | 61.5187 | -0.033101 | 0.034501 | 61.5982 | -0.006014 | 61.3901 | 61.5629 | 61.8584 | 62.3539 | 61.5808 | 62.0175 | 61.696 | 61.5157 | 123.1292 | 61.74 | 123.0284 | 61.4766 | 61.5442 | 123.1079 | 61.5037 | 122.8998 | 61.585 | 61.6255 | 61.4842 | 61.5247
2544.0781 | 123.3536 | -61.4914 | 61.6013 | 0.057754 | 0.36241 | 0.90372 | 0.084867 | 0.54442 | 0.20004 | 0.047159 | 61.6241 | 0.23032 | 61.5462 | -0.042259 | 0.034501 | 61.5982 | 0.003143 | 61.3947 | 61.5491 | 61.8538 | 62.3951 | 61.5763 | 62.0358 | 61.6914 | 61.5386 | 123.1155 | 61.7217 | 123.0376 | 61.4491 | 61.5259 | 123.0896 | 61.4945 | 122.8861 | 61.5896 | 61.6209 | 61.5117 | 61.543
2545.0625 | 123.3032 | -61.4868 | 61.6562 | 0.053175 | 0.29831 | 0.88083 | 0.07571 | 0.51695 | 0.18173 | 0.015112 | 61.6332 | 0.23032 | 61.5645 | -0.03768 | 0.043657 | 61.6028 | 0.003143 | 61.3947 | 61.54 | 61.7851 | 62.3676 | 61.5625 | 62.0038 | 61.6685 | 61.5019 | 123.1201 | 61.7171 | 123.0513 | 61.4491 | 61.5305 | 123.0896 | 61.49 | 122.8815 | 61.5896 | 61.6301 | 61.5208 | 61.5614
2546.0625 | 123.3032 | -61.5051 | 61.647 | 0.048597 | 0.23879 | 0.81215 | 0.057396 | 0.47575 | 0.16799 | -0.044405 | 61.6241 | 0.23948 | 61.5462 | -0.03768 | 0.043657 | 61.5982 | 0.003143 | 61.3947 | 61.5537 | 61.7439 | 62.3173 | 61.5625 | 61.9809 | 61.6731 | 61.4607 | 123.1292 | 61.7446 | 123.0513 | 61.4674 | 61.5488 | 123.1033 | 61.5083 | 122.8998 | 61.5804 | 61.6209 | 61.5025 | 61.543
2547.0625 | 123.3307 | -61.496 | 61.647 | 0.057754 | 0.31205 | 1.009 | 0.094024 | 0.57189 | 0.18631 | 0.01969 | 61.6332 | 0.23032 | 61.5233 | -0.042259 | 0.039079 | 61.6119 | 0.003143 | 61.3901 | 61.5537 | 61.808 | 62.505 | 61.59 | 62.0679 | 61.6823 | 61.5157 | 123.1292 | 61.7263 | 123.0193 | 61.4537 | 61.5351 | 123.1079 | 61.4991 | 122.8861 | 61.5942 | 61.6301 | 61.4842 | 61.5202
2548.0625 | 123.2895 | -61.4868 | 61.6699 | 0.062332 | 0.21589 | 0.81673 | 0.066553 | 0.48948 | 0.14968 | -0.099343 | 61.6195 | 0.2349 | 61.537 | -0.033101 | 0.039079 | 61.5982 | 0.003143 | 61.3947 | 61.5491 | 61.7027 | 62.3035 | 61.5534 | 61.9763 | 61.6365 | 61.3875 | 123.1063 | 61.7217 | 123.0238 | 61.4537 | 61.5259 | 123.085 | 61.49 | 122.8815 | 61.5804 | 61.6164 | 61.4979 | 61.5339
2549.0781 | 123.4177 | -61.4731 | 61.6287 | 0.053175 | 0.13805 | 0.60611 | 0.029925 | 0.39335 | 0.081005 | -0.22753 | 61.6378 | 0.23948 | 61.5645 | -0.028522 | 0.039079 | 61.5982 | 0.007721 | 61.3856 | 61.5263 | 61.6111 | 62.0792 | 61.503 | 61.8664 | 61.5541 | 61.2456 | 123.1109 | 61.7126 | 123.0376 | 61.4446 | 61.5122 | 123.0713 | 61.4808 | 122.8586 | 61.5987 | 61.6301 | 61.5254 | 61.5568
2550.0625 | 123.3078 | -61.4777 | 61.6608 | 0.053175 | 0.15637 | 0.59696 | 0.011611 | 0.42539 | 0.085583 | -0.2138 | 61.6378 | 0.23032 | 61.5645 | -0.03768 | 0.039079 | 61.5936 | -0.006014 | 61.3856 | 61.5308 | 61.634 | 62.0746 | 61.4893 | 61.9031 | 61.5632 | 61.2639 | 123.1155 | 61.708 | 123.0422 | 61.44 | 61.5167 | 123.0713 | 61.4716 | 122.8632 | 61.5987 | 61.6438 | 61.5254 | 61.5705
2551.0625 | 123.3124 | -61.5097 | 61.647 | 0.053175 | 0.22505 | 0.68395 | 0.043661 | 0.46659 | 0.11305 | -0.18633 | 61.6241 | 0.23948 | 61.5324 | -0.033101 | 0.029923 | 61.5891 | -0.001436 | 61.3764 | 61.5629 | 61.7348 | 62.1937 | 61.5534 | 61.9763 | 61.6228 | 61.3234 | 123.1338 | 61.7492 | 123.0422 | 61.4766 | 61.5396 | 123.0988 | 61.5083 | 122.8861 | 61.5942 | 61.6255 | 61.5025 | 61.5339
2552.0625 | 123.3307 | -61.4914 | 61.6562 | 0.062332 | 0.32121 | 0.67021 | 0.080288 | 0.53984 | 0.14052 | -0.090186 | 61.6332 | 0.23948 | 61.5553 | -0.028522 | 0.039079 | 61.5982 | -0.001436 | 61.3993 | 61.5537 | 61.8126 | 62.1616 | 61.5717 | 62.0312 | 61.6319 | 61.4012 | 123.1246 | 61.7309 | 123.0467 | 61.4629 | 61.5305 | 123.0896 | 61.49 | 122.8907 | 61.5942 | 61.6347 | 61.5163 | 61.5568
2553.0781 | 123.4268 | -61.4822 | 61.6425 | 0.048597 | 0.32578 | 0.6931 | 0.089445 | 0.549 | 0.14968 | -0.085608 | 61.6241 | 0.23032 | 61.5645 | -0.042259 | 0.034501 | 61.6028 | -0.001436 | 61.3947 | 61.5308 | 61.808 | 62.1753 | 61.5717 | 62.0312 | 61.6319 | 61.3966 | 123.1063 | 61.7126 | 123.0467 | 61.44 | 61.5167 | 123.085 | 61.4808 | 122.8769 | 61.5896 | 61.6255 | 61.53 | 61.5659
2554.0625 | 123.2025 | -61.5005 | 61.6196 | 0.06691 | 0.49062 | 0.89914 | 0.14439 | 0.66802 | 0.22293 | 0.051737 | 61.6241 | 0.24405 | 61.5508 | -0.03768 | 0.039079 | 61.6119 | -0.001436 | 61.3993 | 61.5675 | 61.9912 | 62.3997 | 61.6449 | 62.1686 | 61.7235 | 61.5523 | 123.1246 | 61.7446 | 123.0513 | 61.4629 | 61.5396 | 123.1125 | 61.4991 | 122.8998 | 61.585 | 61.6255 | 61.5117 | 61.5522
2555.0781 | 123.3948 | -61.4868 | 61.6562 | 0.057754 | 0.35784 | 0.72515 | 0.089445 | 0.54442 | 0.14052 | -0.099343 | 61.6195 | 0.2349 | 61.5187 | -0.033101 | 0.029923 | 61.5982 | -0.006014 | 61.381 | 61.5446 | 61.8447 | 62.212 | 61.5763 | 62.0312 | 61.6273 | 61.3875 | 123.1063 | 61.7217 | 123.0055 | 61.4537 | 61.5167 | 123.085 | 61.4808 | 122.8678 | 61.5896 | 61.6255 | 61.4888 | 61.5247
2556.0625 | 123.2895 | -61.5143 | 61.6516 | 0.06691 | 0.38073 | 0.75721 | 0.098602 | 0.55815 | 0.15426 | -0.08103 | 61.6195 | 0.22574 | 61.537 | -0.046838 | 0.034501 | 61.5982 | 0.003143 | 61.3947 | 61.5812 | 61.895 | 62.2715 | 61.6129 | 62.0724 | 61.6685 | 61.4333 | 123.1338 | 61.74 | 123.0513 | 61.4674 | 61.5488 | 123.1125 | 61.5174 | 122.909 | 61.585 | 61.6164 | 61.5025 | 61.5339
2557.0625 | 123.2941 | -61.5051 | 61.6379 | 0.062332 | 0.4952 | 0.90372 | 0.14439 | 0.65887 | 0.2092 | 0.051737 | 61.6195 | 0.23032 | 61.5508 | -0.03768 | 0.034501 | 61.6028 | -0.006014 | 61.3993 | 61.5675 | 62.0003 | 62.4088 | 61.6495 | 62.164 | 61.7143 | 61.5569 | 123.1246 | 61.7354 | 123.0559 | 61.4674 | 61.5396 | 123.1079 | 61.4991 | 122.9044 | 61.585 | 61.6255 | 61.5163 | 61.5568
2558.0781 | 123.3536 | -61.5005 | 61.5829 | 0.071489 | 0.58678 | 1.0182 | 0.19017 | 0.74127 | 0.23667 | 0.20282 | 61.6195 | 0.23032 | 61.5462 | -0.03768 | 0.029923 | 61.6211 | 0.012299 | 61.3901 | 61.572 | 62.0873 | 62.5187 | 61.6907 | 62.2418 | 61.7372 | 61.7034 | 123.1201 | 61.7309 | 123.0467 | 61.4629 | 61.5305 | 123.1216 | 61.5128 | 122.8907 | 61.5896 | 61.6072 | 61.5163 | 61.5339
2559.0625 | 123.2895 | -61.5143 | 61.6379 | 0.071489 | 0.59593 | 1.0319 | 0.19475 | 0.76874 | 0.2504 | 0.21197 | 61.6195 | 0.2349 | 61.5508 | -0.03768 | 0.034501 | 61.6165 | -0.001436 | 61.4039 | 61.5858 | 62.1102 | 62.5462 | 61.709 | 62.283 | 61.7647 | 61.7263 | 123.1338 | 61.7492 | 123.065 | 61.4766 | 61.5488 | 123.1308 | 61.5128 | 122.9181 | 61.585 | 61.6209 | 61.5163 | 61.5522
2560.0625 | 123.3078 | -61.5189 | 61.6241 | 0.076067 | 0.64172 | 1.1098 | 0.24511 | 0.82367 | 0.24125 | 0.26691 | 61.6104 | 0.22574 | 61.5416 | -0.03768 | 0.034501 | 61.6119 | -0.001436 | 61.4176 | 61.5949 | 62.1606 | 62.6286 | 61.764 | 62.3425 | 61.7601 | 61.7858 | 123.1292 | 61.7446 | 123.0605 | 61.4812 | 61.5534 | 123.1308 | 61.5174 | 122.9365 | 61.5759 | 61.6118 | 61.5071 | 61.543
2561.0625 | 123.262 | -61.528 | 61.6379 | 0.076067 | 0.63257 | 1.064 | 0.24969 | 0.76874 | 0.15884 | 0.20739 | 61.6149 | 0.23032 | 61.5324 | -0.046838 | 0.039079 | 61.6074 | -0.006014 | 61.3947 | 61.6041 | 62.1606 | 62.592 | 61.7777 | 62.2968 | 61.6869 | 61.7354 | 123.1429 | 61.7583 | 123.0605 | 61.4812 | 61.5671 | 123.1354 | 61.522 | 122.9227 | 61.5759 | 61.6209 | 61.4934 | 61.5385
2562.0625 | 123.2986 | -61.4822 | 61.6653 | 0.071489 | 0.51352 | 0.93119 | 0.22222 | 0.66802 | 0.09474 | -0.007779 | 61.6241 | 0.22574 | 61.537 | -0.03768 | 0.029923 | 61.6028 | -0.001436 | 61.3901 | 61.5537 | 61.9958 | 62.4134 | 61.7045 | 62.1503 | 61.577 | 61.4745 | 123.1063 | 61.708 | 123.0193 | 61.4446 | 61.5122 | 123.085 | 61.4808 | 122.8724 | 61.5942 | 61.6255 | 61.5071 | 61.5385
2563.0625 | 123.2803 | -61.496 | 61.6287 | 0.06691 | 0.50436 | 0.92661 | 0.23596 | 0.64971 | 0.1039 | 0.005955 | 61.6195 | 0.2349 | 61.5279 | -0.042259 | 0.029923 | 61.6074 | -0.001436 | 61.3947 | 61.5629 | 62.0003 | 62.4226 | 61.7319 | 62.1457 | 61.5999 | 61.5019 | 123.1155 | 61.7309 | 123.0238 | 61.4537 | 61.5259 | 123.1033 | 61.4945 | 122.8907 | 61.5896 | 61.6209 | 61.4979 | 61.5293
2564.0625 | 123.3261 | -61.496 | 61.6287 | 0.071489 | 0.48604 | 0.96324 | 0.23138 | 0.66344 | 0.1039 | -0.007779 | 61.6241 | 0.2349 | 61.5462 | -0.03768 | 0.043657 | 61.6074 | -0.010593 | 61.4039 | 61.5675 | 61.982 | 62.4592 | 61.7274 | 62.1594 | 61.5999 | 61.4882 | 123.1201 | 61.7309 | 123.0422 | 61.4583 | 61.5396 | 123.1033 | 61.4854 | 122.8998 | 61.5804 | 61.6347 | 61.5025 | 61.5568
2565.0625 | 123.2483 | -61.5234 | 61.6653 | 0.071489 | 0.53641 | 1.0686 | 0.27259 | 0.70922 | 0.12221 | 0.07005 | 61.6104 | 0.2349 | 61.5599 | -0.046838 | 0.039079 | 61.6074 | -0.006014 | 61.4039 | 61.5949 | 62.0598 | 62.592 | 61.796 | 62.2327 | 61.6456 | 61.5935 | 123.1338 | 61.7583 | 123.0834 | 61.4766 | 61.5625 | 123.1308 | 61.5174 | 122.9273 | 61.5713 | 61.6164 | 61.5208 | 61.5659
2566.0625 | 123.2803 | -61.5189 | 61.6425 | 0.06691 | 0.56388 | 1.1189 | 0.28174 | 0.74585 | 0.13137 | 0.088362 | 61.6149 | 0.2349 | 61.5416 | -0.03768 | 0.039079 | 61.5982 | -0.001436 | 61.3993 | 61.5858 | 62.0827 | 62.6378 | 61.8006 | 62.2647 | 61.6502 | 61.6072 | 123.1338 | 61.7538 | 123.0605 | 61.4812 | 61.5579 | 123.1171 | 61.5174 | 122.9181 | 61.5759 | 61.6164 | 61.5025 | 61.543
2567.0625 | 123.2758 | -61.5463 | 61.6333 | 0.080646 | 0.5593 | 1.1739 | 0.29548 | 0.74585 | 0.13595 | 0.11125 | 61.6149 | 0.23032 | 61.5187 | -0.042259 | 0.034501 | 61.6165 | -0.001436 | 61.3901 | 61.627 | 62.1056 | 62.7202 | 61.8418 | 62.2922 | 61.6823 | 61.6576 | 123.1613 | 61.7766 | 123.065 | 61.5041 | 61.5808 | 123.1628 | 61.5449 | 122.9365 | 61.5804 | 61.6164 | 61.4842 | 61.5202
2568.0781 | 123.349 | -61.4685 | 61.6013 | 0.080646 | 0.72872 | 1.3662 | 0.33668 | 0.87861 | 0.22293 | 0.36305 | 61.6058 | 0.22574 | 61.5233 | -0.042259 | 0.039079 | 61.6211 | 0.003143 | 61.413 | 61.5492 | 62.1972 | 62.8347 | 61.8052 | 62.3471 | 61.6914 | 61.8316 | 123.0743 | 61.6942 | 122.9918 | 61.4262 | 61.5076 | 123.0896 | 61.4716 | 122.8815 | 61.5667 | 61.6026 | 61.4842 | 61.5202
2569.0625 | 123.2986 | -61.5372 | 61.6333 | 0.089802 | 0.79282 | 1.4119 | 0.37331 | 0.93812 | 0.23209 | 0.41799 | 61.6104 | 0.2349 | 61.5508 | -0.033101 | 0.034501 | 61.6165 | -0.001436 | 61.413 | 61.627 | 62.33 | 62.9491 | 61.9105 | 62.4753 | 61.7693 | 61.9552 | 123.1475 | 61.7721 | 123.0879 | 61.5041 | 61.5717 | 123.1537 | 61.5357 | 122.9502 | 61.5759 | 61.6118 | 61.5163 | 61.5522
2570.0938 | 123.2895 | -61.5143 | 61.6516 | 0.089802 | 0.78367 | 1.3845 | 0.355 | 0.89692 | 0.18173 | 0.39968 | 61.6058 | 0.23032 | 61.5324 | -0.046838 | 0.034501 | 61.6165 | -0.006014 | 61.413 | 61.6041 | 62.2979 | 62.8988 | 61.8693 | 62.4112 | 61.696 | 61.914 | 123.1201 | 61.7446 | 123.0467 | 61.4674 | 61.5488 | 123.1308 | 61.5083 | 122.9273 | 61.5713 | 61.6118 | 61.4979 | 61.5385
2571.0625 | 123.317 | -61.5143 | 61.6653 | 0.080646 | 0.58678 | 1.1143 | 0.28174 | 0.74127 | 0.085583 | 0.12041 | 61.6149 | 0.2349 | 61.5141 | -0.042259 | 0.039079 | 61.6119 | -0.010593 | 61.3901 | 61.5949 | 62.1011 | 62.6286 | 61.796 | 62.2556 | 61.5999 | 61.6347 | 123.1292 | 61.7492 | 123.0284 | 61.472 | 61.5534 | 123.1262 | 61.5037 | 122.9044 | 61.5759 | 61.6255 | 61.4751 | 61.5247
2572.0625 | 123.2437 | -61.5417 | 61.6013 | 0.094381 | 0.7974 | 1.3616 | 0.36416 | 0.9015 | 0.18173 | 0.41341 | 61.5966 | 0.23032 | 61.537 | -0.042259 | 0.043657 | 61.6257 | -0.001436 | 61.413 | 61.6361 | 62.3392 | 62.9033 | 61.9059 | 62.4432 | 61.7235 | 61.9552 | 123.1384 | 61.7721 | 123.0788 | 61.4995 | 61.5854 | 123.1674 | 61.5403 | 122.9548 | 61.553 | 61.5981 | 61.4934 | 61.5385
2573.0625 | 123.3948 | -61.4822 | 61.6241 | 0.080646 | 0.75162 | 1.2929 | 0.35958 | 0.84656 | 0.15884 | 0.2486 | 61.6104 | 0.2349 | 61.5416 | -0.033101 | 0.034501 | 61.6211 | -0.006014 | 61.413 | 61.5629 | 62.2339 | 62.7751 | 61.8418 | 62.3288 | 61.6411 | 61.7308 | 123.0926 | 61.7171 | 123.0238 | 61.4491 | 61.5167 | 123.1033 | 61.4762 | 122.8953 | 61.5759 | 61.6164 | 61.5071 | 61.5476
2574.0625 | 123.2986 | -61.5234 | 61.6287 | 0.085224 | 0.59136 | 1.0777 | 0.30006 | 0.74127 | 0.11763 | 0.051737 | 61.6149 | 0.22574 | 61.5508 | -0.042259 | 0.029923 | 61.6119 | 0.003143 | 61.413 | 61.6087 | 62.1148 | 62.6011 | 61.8235 | 62.2647 | 61.6411 | 61.5752 | 123.1384 | 61.7492 | 123.0742 | 61.4812 | 61.5534 | 123.1354 | 61.5266 | 122.9365 | 61.585 | 61.6118 | 61.5208 | 61.5476
2575.0625 | 123.2483 | -61.5234 | 61.6333 | 0.080646 | 0.58678 | 1.0273 | 0.30006 | 0.65887 | 0.12221 | 0.010533 | 61.6195 | 0.2349 | 61.5187 | -0.046838 | 0.029923 | 61.6074 | 0.003143 | 61.4039 | 61.6041 | 62.1102 | 62.5508 | 61.8235 | 62.1823 | 61.6456 | 61.534 | 123.1429 | 61.7583 | 123.0422 | 61.4766 | 61.5534 | 123.1308 | 61.5266 | 122.9273 | 61.5896 | 61.6164 | 61.4888 | 61.5156
2576.0625 | 123.2849 | -61.5189 | 61.6196 | 0.089802 | 0.74704 | 1.2105 | 0.35958 | 0.8191 | 0.18173 | 0.2486 | 61.6149 | 0.23948 | 61.5233 | -0.03768 | 0.034501 | 61.6211 | -0.001436 | 61.4084 | 61.6087 | 62.2659 | 62.7293 | 61.8784 | 62.338 | 61.7006 | 61.7675 | 123.1338 | 61.7583 | 123.0422 | 61.4812 | 61.5534 | 123.14 | 61.5174 | 122.9273 | 61.5804 | 61.6164 | 61.4888 | 61.5247
2577.0625 | 123.2986 | -61.5189 | 61.6333 | 0.089802 | 0.70583 | 1.1555 | 0.34126 | 0.75043 | 0.15426 | 0.23944 | 61.6287 | 0.23032 | 61.5416 | -0.046838 | 0.034501 | 61.6211 | -0.001436 | 61.4084 | 61.6087 | 62.2247 | 62.6744 | 61.8601 | 62.2693 | 61.6731 | 61.7583 | 123.1475 | 61.7492 | 123.0605 | 61.472 | 61.5534 | 123.14 | 61.5174 | 122.9273 | 61.5942 | 61.6301 | 61.5071 | 61.543
2578.0625 | 123.2758 | -61.5189 | 61.6333 | 0.085224 | 0.69209 | 1.1647 | 0.35042 | 0.7138 | 0.16799 | 0.26233 | 61.6149 | 0.23032 | 61.5508 | -0.042259 | 0.039079 | 61.6211 | -0.001436 | 61.413 | 61.6041 | 62.2109 | 62.6836 | 61.8693 | 62.2327 | 61.6869 | 61.7812 | 123.1338 | 61.7492 | 123.0696 | 61.4766 | 61.5579 | 123.14 | 61.5174 | 122.9319 | 61.5759 | 61.6164 | 61.5117 | 61.5522
2579.0625 | 123.262 | -61.5143 | 61.6241 | 0.080646 | 0.63257 | 1.0914 | 0.31379 | 0.74585 | 0.15426 | 0.18908 | 61.6149 | 0.23948 | 61.5141 | -0.042259 | 0.029923 | 61.6211 | -0.001436 | 61.3947 | 61.5949 | 62.1468 | 62.6057 | 61.8281 | 62.2601 | 61.6685 | 61.7034 | 123.1292 | 61.7538 | 123.0284 | 61.472 | 61.5442 | 123.1354 | 61.5128 | 122.909 | 61.585 | 61.6164 | 61.4842 | 61.5156
2580.0781 | 123.2666 | -61.528 | 61.6241 | 0.080646 | 0.7104 | 1.2013 | 0.36873 | 0.82367 | 0.21378 | 0.29896 | 61.6012 | 0.2349 | 61.5096 | -0.051417 | 0.034501 | 61.6119 | 0.007721 | 61.4039 | 61.6087 | 62.2384 | 62.7293 | 61.8967 | 62.3517 | 61.7418 | 61.827 | 123.1292 | 61.7629 | 123.0376 | 61.4766 | 61.5625 | 123.14 | 61.5357 | 122.9319 | 61.5667 | 61.5935 | 61.4751 | 61.5018
2581.0625 | 123.2895 | -61.5234 | 61.6196 | 0.085224 | 0.61425 | 1.1143 | 0.35042 | 0.77332 | 0.19089 | 0.21655 | 61.6149 | 0.2349 | 61.537 | -0.051417 | 0.034501 | 61.6119 | -0.001436 | 61.413 | 61.6087 | 62.1377 | 62.6378 | 61.8739 | 62.2968 | 61.7143 | 61.74 | 123.1384 | 61.7583 | 123.0605 | 61.472 | 61.5579 | 123.1354 | 61.522 | 122.9365 | 61.5804 | 61.6164 | 61.5025 | 61.5385
2582.0781 | 123.3994 | -61.5005 | 61.5601 | 0.089802 | 0.72872 | 1.2746 | 0.40536 | 0.8603 | 0.24583 | 0.38594 | 61.6104 | 0.23032 | 61.537 | -0.051417 | 0.034501 | 61.6257 | -0.001436 | 61.4039 | 61.5904 | 62.2293 | 62.7751 | 61.9059 | 62.3608 | 61.7464 | 61.8865 | 123.1109 | 61.7309 | 123.0376 | 61.4491 | 61.535 | 123.1262 | 61.4991 | 122.9044 | 61.5759 | 61.6118 | 61.5025 | 61.5385
2583.0625 | 123.2849 | -61.5326 | 61.6333 | 0.089802 | 0.74246 | 1.2517 | 0.42368 | 0.82825 | 0.23209 | 0.32643 | 61.6149 | 0.23032 | 61.5462 | -0.03768 | 0.034501 | 61.6119 | -0.001436 | 61.413 | 61.6224 | 62.2751 | 62.7843 | 61.9563 | 62.3608 | 61.7647 | 61.859 | 123.1475 | 61.7629 | 123.0788 | 61.4949 | 61.5671 | 123.1445 | 61.5312 | 122.9456 | 61.5804 | 61.6164 | 61.5117 | 61.5476
2584.0625 | 123.2895 | -61.5234 | 61.6379 | 0.085224 | 0.72872 | 1.2196 | 0.40536 | 0.78705 | 0.21836 | 0.2486 | 61.6195 | 0.2349 | 61.5462 | -0.033101 | 0.034501 | 61.6165 | -0.001436 | 61.4084 | 61.6087 | 62.2522 | 62.7431 | 61.9288 | 62.3105 | 61.7418 | 61.772 | 123.1429 | 61.7583 | 123.0696 | 61.4903 | 61.5579 | 123.14 | 61.522 | 122.9319 | 61.585 | 61.6209 | 61.5117 | 61.5476
2585.0625 | 123.2895 | -61.5143 | 61.6379 | 0.098959 | 0.8203 | 1.3021 | 0.45115 | 0.8603 | 0.2504 | 0.29438 | 61.6058 | 0.2349 | 61.537 | -0.03768 | 0.034501 | 61.6211 | -0.010593 | 61.4222 | 61.6132 | 62.3346 | 62.8163 | 61.9654 | 62.3746 | 61.7647 | 61.8087 | 123.1201 | 61.7492 | 123.0513 | 61.4766 | 61.5488 | 123.1354 | 61.5037 | 122.9365 | 61.5713 | 61.6164 | 61.5025 | 61.5476
2586.0781 | 123.3307 | -61.4868 | 61.5738 | 0.094381 | 0.80656 | 1.2563 | 0.40994 | 0.84198 | 0.22751 | 0.28065 | 61.6012 | 0.23032 | 61.5141 | -0.042259 | 0.034501 | 61.6165 | -0.001436 | 61.3947 | 61.5812 | 62.2934 | 62.7431 | 61.8968 | 62.3288 | 61.7143 | 61.7675 | 123.088 | 61.7171 | 123.001 | 61.4446 | 61.5213 | 123.1033 | 61.4854 | 122.8815 | 61.5667 | 61.6026 | 61.4796 | 61.5156
2587.0625 | 123.262 | -61.528 | 61.6241 | 0.089802 | 0.78824 | 1.2425 | 0.4191 | 0.81452 | 0.20462 | 0.23029 | 61.6104 | 0.23032 | 61.505 | -0.03768 | 0.034501 | 61.6211 | -0.006014 | 61.4039 | 61.6178 | 62.3163 | 62.7706 | 61.9471 | 62.3425 | 61.7326 | 61.7583 | 123.1384 | 61.7583 | 123.033 | 61.4903 | 61.5625 | 123.1491 | 61.522 | 122.9319 | 61.5759 | 61.6164 | 61.4705 | 61.511
2588.0781 | 123.2803 | -61.5326 | 61.615 | 0.094381 | 0.81114 | 1.2425 | 0.4191 | 0.75958 | 0.23209 | 0.25318 | 61.6012 | 0.2349 | 61.505 | -0.042259 | 0.034501 | 61.6211 | 0.003143 | 61.3993 | 61.627 | 62.3437 | 62.7751 | 61.9517 | 62.2922 | 61.7647 | 61.7858 | 123.1338 | 61.7675 | 123.0376 | 61.4903 | 61.5671 | 123.1537 | 61.5357 | 122.9319 | 61.5667 | 61.5981 | 61.4705 | 61.5018
2589.0625 | 123.2712 | -61.528 | 61.6104 | 0.10354 | 0.82946 | 1.238 | 0.42825 | 0.77789 | 0.26414 | 0.27149 | 61.6104 | 0.2349 | 61.5141 | -0.033101 | 0.034501 | 61.6165 | 0.003143 | 61.413 | 61.6316 | 62.3575 | 62.766 | 61.9563 | 62.3059 | 61.7922 | 61.7995 | 123.1384 | 61.7629 | 123.0422 | 61.4949 | 61.5625 | 123.1445 | 61.5312 | 122.941 | 61.5759 | 61.6072 | 61.4796 | 61.511
2590.0781 | 123.3856 | -61.5005 | 61.6104 | 0.10812 | 0.85693 | 1.2883 | 0.45115 | 0.79621 | 0.27787 | 0.29896 | 61.6058 | 0.22574 | 61.5416 | -0.03768 | 0.039079 | 61.6165 | -0.001436 | 61.4176 | 61.6087 | 62.3575 | 62.7889 | 61.9517 | 62.2968 | 61.7784 | 61.7995 | 123.1063 | 61.7263 | 123.0422 | 61.4629 | 61.5396 | 123.1171 | 61.4991 | 122.9181 | 61.5667 | 61.6072 | 61.5025 | 61.543
2591.0625 | 123.2758 | -61.5372 | 61.6333 | 0.11269 | 0.96224 | 1.3891 | 0.46946 | 0.84198 | 0.24125 | 0.36763 | 61.6104 | 0.2349 | 61.5416 | -0.042259 | 0.039079 | 61.6211 | -0.006014 | 61.4176 | 61.6499 | 62.4994 | 62.9262 | 62.0066 | 62.3792 | 61.7784 | 61.9048 | 123.1475 | 61.7721 | 123.0788 | 61.4949 | 61.5762 | 123.1583 | 61.5312 | 122.9548 | 61.5713 | 61.6164 | 61.5025 | 61.5476
2592.0625 | 123.317 | -61.496 | 61.6425 | 0.10812 | 0.89356 | 1.3295 | 0.46488 | 0.82367 | 0.21378 | 0.29896 | 61.6058 | 0.23032 | 61.5508 | -0.03768 | 0.034501 | 61.6257 | -0.006014 | 61.4176 | 61.6041 | 62.3895 | 62.8255 | 61.9609 | 62.3196 | 61.7097 | 61.7949 | 123.1017 | 61.7263 | 123.0467 | 61.4583 | 61.5305 | 123.1216 | 61.49 | 122.9136 | 61.5713 | 61.6118 | 61.5163 | 61.5568
2593.0625 | 123.2849 | -61.5097 | 61.6241 | 0.11269 | 0.87066 | 1.2883 | 0.47404 | 0.82367 | 0.2092 | 0.26233 | 61.6149 | 0.2349 | 61.5416 | -0.03768 | 0.029923 | 61.6211 | 0.003143 | 61.4222 | 61.6224 | 62.3804 | 62.798 | 61.9837 | 62.3334 | 61.7189 | 61.772 | 123.1246 | 61.7446 | 123.0513 | 61.472 | 61.5396 | 123.1308 | 61.5128 | 122.9319 | 61.585 | 61.6118 | 61.5117 | 61.5385
2594.0625 | 123.2895 | -61.5097 | 61.6241 | 0.11269 | 0.88898 | 1.2837 | 0.46488 | 0.84198 | 0.2733 | 0.26691 | 61.6058 | 0.23948 | 61.5324 | -0.033101 | 0.034501 | 61.6257 | 0.003143 | 61.4084 | 61.6224 | 62.3987 | 62.7934 | 61.9746 | 62.3517 | 61.783 | 61.7766 | 123.1155 | 61.7492 | 123.0422 | 61.4766 | 61.5442 | 123.1354 | 61.5128 | 122.9181 | 61.5713 | 61.6026 | 61.4979 | 61.5293
2595.0625 | 123.2849 | -61.496 | 61.6241 | 0.11269 | 0.88898 | 1.3204 | 0.47404 | 0.84198 | 0.27787 | 0.21197 | 61.6058 | 0.2349 | 61.5233 | -0.042259 | 0.029923 | 61.6211 | -0.006014 | 61.413 | 61.6087 | 62.385 | 62.8163 | 61.97 | 62.338 | 61.7738 | 61.7079 | 123.1017 | 61.7309 | 123.0193 | 61.4537 | 61.5259 | 123.1171 | 61.49 | 122.909 | 61.5759 | 61.6118 | 61.4934 | 61.5293
2596.0625 | 123.2895 | -61.5189 | 61.6196 | 0.11727 | 0.86608 | 1.2975 | 0.4832 | 0.82825 | 0.2733 | 0.17535 | 61.6149 | 0.2349 | 61.5096 | -0.03768 | 0.048236 | 61.6165 | -0.001436 | 61.4084 | 61.6361 | 62.3849 | 62.8163 | 62.0021 | 62.3471 | 61.7922 | 61.6942 | 123.1338 | 61.7538 | 123.0284 | 61.4812 | 61.5671 | 123.1354 | 61.5174 | 122.9273 | 61.5667 | 61.6164 | 61.4613 | 61.511
2597.0781 | 123.3398 | -61.5143 | 61.6058 | 0.12185 | 0.9485 | 1.357 | 0.50151 | 0.87861 | 0.29619 | 0.2898 | 61.6012 | 0.2349 | 61.505 | -0.03768 | 0.034501 | 61.6257 | -0.001436 | 61.4084 | 61.6361 | 62.4628 | 62.8713 | 62.0158 | 62.3929 | 61.8105 | 61.8041 | 123.1155 | 61.7492 | 123.0193 | 61.4766 | 61.5488 | 123.14 | 61.5128 | 122.9227 | 61.5667 | 61.6026 | 61.4705 | 61.5064
2598.0625 | 123.2849 | -61.5234 | 61.6516 | 0.11269 | 0.87982 | 1.2929 | 0.46946 | 0.84198 | 0.25956 | 0.24402 | 61.6104 | 0.2349 | 61.5141 | -0.042259 | 0.043657 | 61.6211 | -0.001436 | 61.413 | 61.6361 | 62.4033 | 62.8163 | 61.9929 | 62.3654 | 61.783 | 61.7675 | 123.1338 | 61.7583 | 123.0376 | 61.4812 | 61.5671 | 123.1445 | 61.522 | 122.9365 | 61.5667 | 61.6118 | 61.4705 | 61.5156
2599.0625 | 123.3398 | -61.528 | 61.615 | 0.11727 | 0.91187 | 1.325 | 0.47404 | 0.82367 | 0.28703 | 0.21655 | 61.6149 | 0.2349 | 61.5416 | -0.03768 | 0.039079 | 61.6211 | -0.006014 | 61.4268 | 61.6453 | 62.4399 | 62.853 | 62.0021 | 62.3517 | 61.815 | 61.7446 | 123.1429 | 61.7629 | 123.0696 | 61.4903 | 61.5671 | 123.1491 | 61.522 | 122.9548 | 61.5759 | 61.6209 | 61.5025 | 61.5476
2600.0625 | 123.2941 | -61.5326 | 61.6287 | 0.12185 | 0.8844 | 1.3021 | 0.47404 | 0.80536 | 0.28245 | 0.18908 | 61.6149 | 0.2349 | 61.5462 | -0.03768 | 0.029923 | 61.6165 | -0.001436 | 61.4222 | 61.6544 | 62.417 | 62.8347 | 62.0066 | 62.338 | 61.815 | 61.7217 | 123.1475 | 61.7675 | 123.0788 | 61.4949 | 61.5625 | 123.1491 | 61.5312 | 122.9548 | 61.585 | 61.6164 | 61.5163 | 61.5476
2601.0625 | 123.2986 | -61.496 | 61.6241 | 0.13101 | 0.93935 | 1.3662 | 0.53356 | 0.86487 | 0.33282 | 0.24402 | 61.6149 | 0.23032 | 61.537 | -0.033101 | 0.039079 | 61.6165 | 0.003143 | 61.4176 | 61.627 | 62.4353 | 62.8621 | 62.0295 | 62.3608 | 61.8288 | 61.74 | 123.1109 | 61.7263 | 123.033 | 61.4629 | 61.5351 | 123.1125 | 61.4991 | 122.9136 | 61.5759 | 61.6118 | 61.4979 | 61.5339
2602.0625 | 123.349 | -61.5051 | 61.6425 | 0.11269 | 0.84319 | 1.2609 | 0.51067 | 0.80078 | 0.36944 | 0.17993 | 61.6104 | 0.23032 | 61.5096 | -0.042259 | 0.034501 | 61.6165 | -0.001436 | 61.4039 | 61.6178 | 62.3483 | 62.766 | 62.0158 | 62.3059 | 61.8746 | 61.6851 | 123.1155 | 61.7354 | 123.0147 | 61.4629 | 61.5396 | 123.1216 | 61.5037 | 122.909 | 61.5759 | 61.6118 | 61.4751 | 61.511
2603.0625 | 123.2986 | -61.496 | 61.6241 | 0.11727 | 0.88898 | 1.2563 | 0.5244 | 0.8191 | 0.40607 | 0.23029 | 61.6058 | 0.23032 | 61.505 | -0.03768 | 0.034501 | 61.6211 | -0.001436 | 61.4176 | 61.6132 | 62.385 | 62.7522 | 62.0204 | 62.3151 | 61.902 | 61.7263 | 123.1017 | 61.7263 | 123.001 | 61.4583 | 61.5305 | 123.1171 | 61.4945 | 122.9136 | 61.5713 | 61.6072 | 61.4705 | 61.5064
2604.0625 | 123.3215 | -61.528 | 61.6516 | 0.11269 | 0.83861 | 1.2105 | 0.50609 | 0.78247 | 0.41523 | 0.16619 | 61.6058 | 0.23948 | 61.5508 | -0.03768 | 0.039079 | 61.6211 | 0.003143 | 61.413 | 61.6407 | 62.3666 | 62.7385 | 62.0341 | 62.3105 | 61.9432 | 61.6942 | 123.1338 | 61.7675 | 123.0788 | 61.4903 | 61.5671 | 123.1491 | 61.5312 | 122.941 | 61.5667 | 61.6026 | 61.5117 | 61.5476
2605.0625 | 123.2895 | -61.5417 | 61.6425 | 0.12643 | 0.93935 | 1.2517 | 0.54272 | 0.81452 | 0.43354 | 0.27607 | 61.6058 | 0.23032 | 61.5416 | -0.042259 | 0.043657 | 61.6211 | -0.006014 | 61.4176 | 61.6682 | 62.4811 | 62.7934 | 62.0845 | 62.3563 | 61.9753 | 61.8178 | 123.1475 | 61.7721 | 123.0834 | 61.4995 | 61.5854 | 123.1628 | 61.5357 | 122.9593 | 61.5621 | 61.6118 | 61.4979 | 61.5476
2606.0625 | 123.3078 | -61.5189 | 61.6699 | 0.11727 | 0.96682 | 1.3021 | 0.57019 | 0.82825 | 0.4427 | 0.31727 | 61.6058 | 0.22574 | 61.5416 | -0.042259 | 0.039079 | 61.6211 | 0.003143 | 61.4176 | 61.6361 | 62.4857 | 62.8209 | 62.089 | 62.3471 | 61.9616 | 61.8361 | 123.1246 | 61.7446 | 123.0605 | 61.4766 | 61.5579 | 123.14 | 61.522 | 122.9365 | 61.5667 | 61.6026 | 61.5025 | 61.5385
2607.0625 | 123.3353 | -61.5417 | 61.6379 | 0.13101 | 0.99429 | 1.3204 | 0.59308 | 0.82825 | 0.42896 | 0.2898 | 61.6012 | 0.2349 | 61.5416 | -0.033101 | 0.034501 | 61.6211 | 0.003143 | 61.4176 | 61.6728 | 62.536 | 62.8621 | 62.1348 | 62.37 | 61.9707 | 61.8316 | 123.1429 | 61.7766 | 123.0834 | 61.5086 | 61.5762 | 123.1628 | 61.5449 | 122.9593 | 61.5667 | 61.5981 | 61.5071 | 61.5385
2608.0625 | 123.3353 | -61.5189 | 61.5875 | 0.12643 | 1.0034 | 1.3112 | 0.5885 | 0.82367 | 0.4427 | 0.34016 | 61.6104 | 0.2349 | 61.5141 | -0.03768 | 0.034501 | 61.6211 | -0.001436 | 61.413 | 61.6453 | 62.5223 | 62.8301 | 62.1074 | 62.3425 | 61.9616 | 61.859 | 123.1292 | 61.7538 | 123.033 | 61.4812 | 61.5534 | 123.14 | 61.5174 | 122.9319 | 61.5759 | 61.6118 | 61.4796 | 61.5156
2609.0781 | 123.2803 | -61.5143 | 61.6241 | 0.13559 | 0.99887 | 1.3341 | 0.57934 | 0.82367 | 0.42438 | 0.29438 | 61.6012 | 0.23032 | 61.505 | -0.042259 | 0.039079 | 61.6257 | -0.010593 | 61.4176 | 61.6499 | 62.5132 | 62.8484 | 62.0936 | 62.338 | 61.9387 | 61.8087 | 123.1155 | 61.7446 | 123.0193 | 61.472 | 61.5534 | 123.14 | 61.5037 | 122.9319 | 61.5621 | 61.6118 | 61.4659 | 61.5156
2610.0625 | 123.2849 | -61.5326 | 61.6379 | 0.13101 | 1.0263 | 1.3845 | 0.63887 | 0.83283 | 0.39233 | 0.2486 | 61.6012 | 0.23032 | 61.5004 | -0.033101 | 0.039079 | 61.6257 | 0.003143 | 61.4084 | 61.6636 | 62.5589 | 62.9171 | 62.1715 | 62.3654 | 61.9249 | 61.7812 | 123.1338 | 61.7629 | 123.033 | 61.4995 | 61.5717 | 123.1583 | 61.5357 | 122.941 | 61.5621 | 61.5981 | 61.4613 | 61.4973
2611.0625 | 123.3261 | -61.528 | 61.6333 | 0.13559 | 1.0904 | 1.476 | 0.66176 | 0.85114 | 0.35571 | 0.27149 | 61.6012 | 0.2349 | 61.4958 | -0.033101 | 0.039079 | 61.6165 | 0.003143 | 61.413 | 61.6636 | 62.6185 | 63.0041 | 62.1898 | 62.3792 | 61.8837 | 61.7995 | 123.1292 | 61.7629 | 123.0238 | 61.4949 | 61.5671 | 123.1445 | 61.5312 | 122.941 | 61.5621 | 61.5981 | 61.4567 | 61.4927
2612.0625 | 123.2803 | -61.5189 | 61.6425 | 0.14474 | 1.0492 | 1.4852 | 0.69381 | 0.86945 | 0.33282 | 0.22571 | 61.6012 | 0.23032 | 61.5324 | -0.042259 | 0.048236 | 61.6257 | 0.003143 | 61.4222 | 61.6636 | 62.5681 | 63.0041 | 62.2127 | 62.3883 | 61.8517 | 61.7446 | 123.1201 | 61.7492 | 123.0513 | 61.4766 | 61.5671 | 123.1445 | 61.522 | 122.941 | 61.553 | 61.5981 | 61.4842 | 61.5293
2613.0625 | 123.2803 | -61.5692 | 61.6608 | 0.15848 | 1.0676 | 1.4944 | 0.67091 | 0.89234 | 0.3786 | 0.25776 | 61.6012 | 0.2349 | 61.5416 | -0.033101 | 0.043657 | 61.6303 | -0.001436 | 61.4268 | 61.7277 | 62.6368 | 63.0636 | 62.2401 | 62.4616 | 61.9478 | 61.827 | 123.1704 | 61.8041 | 123.1108 | 61.5361 | 61.6129 | 123.1995 | 61.5678 | 122.996 | 61.5575 | 61.6026 | 61.4979 | 61.543
2614.0625 | 123.2986 | -61.5051 | 61.6516 | 0.14474 | 1.0218 | 1.4577 | 0.65718 | 0.84198 | 0.38318 | 0.26691 | 61.6104 | 0.23948 | 61.5462 | -0.03768 | 0.034501 | 61.6303 | -0.001436 | 61.4222 | 61.6499 | 62.5269 | 62.9629 | 62.1623 | 62.3471 | 61.8883 | 61.772 | 123.1155 | 61.7446 | 123.0513 | 61.4674 | 61.5396 | 123.1354 | 61.5037 | 122.9273 | 61.5759 | 61.6118 | 61.5117 | 61.5476
2615.0625 | 123.2803 | -61.5189 | 61.6333 | 0.15848 | 1.0676 | 1.5493 | 0.7167 | 0.87861 | 0.43354 | 0.41341 | 61.6012 | 0.23032 | 61.5324 | -0.033101 | 0.034501 | 61.6303 | -0.001436 | 61.4222 | 61.6773 | 62.5864 | 63.0682 | 62.2356 | 62.3975 | 61.9524 | 61.9323 | 123.1201 | 61.7492 | 123.0513 | 61.4858 | 61.5534 | 123.1491 | 61.5174 | 122.941 | 61.5667 | 61.6026 | 61.4979 | 61.5339
2616.0625 | 123.3353 | -61.5051 | 61.6608 | 0.14932 | 1.0492 | 1.5814 | 0.7808 | 0.89692 | 0.47932 | 0.49124 | 61.6012 | 0.23948 | 61.5187 | -0.042259 | 0.034501 | 61.6394 | -0.001436 | 61.4268 | 61.6544 | 62.5544 | 63.0865 | 62.2859 | 62.402 | 61.9845 | 61.9964 | 123.1063 | 61.7446 | 123.0238 | 61.4629 | 61.5396 | 123.1445 | 61.5037 | 122.9319 | 61.5667 | 61.6026 | 61.4842 | 61.5202
2617.0625 | 123.3032 | -61.5234 | 61.6745 | 0.15848 | 1.0218 | 1.4852 | 0.74875 | 0.8603 | 0.51595 | 0.45004 | 61.5966 | 0.23948 | 61.4912 | -0.042259 | 0.034501 | 61.6348 | 0.003143 | 61.4222 | 61.6819 | 62.5452 | 63.0086 | 62.2722 | 62.3837 | 62.0394 | 61.9735 | 123.1201 | 61.7629 | 123.0147 | 61.4812 | 61.5579 | 123.1583 | 61.5266 | 122.9456 | 61.5621 | 61.5935 | 61.4567 | 61.4881
2618.0781 | 123.3307 | -61.5189 | 61.6241 | 0.15848 | 1.0859 | 1.563 | 0.76248 | 0.91981 | 0.52053 | 0.57823 | 61.592 | 0.23032 | 61.5279 | -0.046838 | 0.039079 | 61.6303 | 0.003143 | 61.4268 | 61.6773 | 62.6047 | 63.0819 | 62.2813 | 62.4387 | 62.0394 | 62.0971 | 123.1109 | 61.7492 | 123.0467 | 61.472 | 61.5579 | 123.1491 | 61.522 | 122.9456 | 61.553 | 61.5889 | 61.4888 | 61.5247
2619.0625 | 123.3261 | -61.5097 | 61.6333 | 0.16306 | 1.1088 | 1.5676 | 0.77622 | 0.93354 | 0.4839 | 0.62401 | 61.592 | 0.2349 | 61.537 | -0.042259 | 0.039079 | 61.6348 | -0.001436 | 61.4359 | 61.6728 | 62.6185 | 63.0773 | 62.2859 | 62.4432 | 61.9936 | 62.1337 | 123.1017 | 61.7446 | 123.0467 | 61.4674 | 61.5488 | 123.1445 | 61.5083 | 122.9456 | 61.553 | 61.5935 | 61.4979 | 61.5385
2620.0625 | 123.2849 | -61.5417 | 61.647 | 0.16764 | 1.1317 | 1.5585 | 0.75333 | 0.89234 | 0.47932 | 0.64232 | 61.5966 | 0.2349 | 61.5233 | -0.042259 | 0.043657 | 61.6348 | -0.001436 | 61.4313 | 61.7094 | 62.6734 | 63.1002 | 62.2951 | 62.4341 | 62.0211 | 62.1841 | 123.1384 | 61.7766 | 123.065 | 61.4995 | 61.5854 | 123.1766 | 61.5403 | 122.9731 | 61.553 | 61.5981 | 61.4796 | 61.5247
2621.0781 | 123.2849 | -61.5509 | 61.6104 | 0.16764 | 1.095 | 1.5173 | 0.74417 | 0.86945 | 0.52053 | 0.62401 | 61.592 | 0.23032 | 61.4958 | -0.042259 | 0.034501 | 61.6303 | -0.010593 | 61.4222 | 61.7185 | 62.6459 | 63.0682 | 62.2951 | 62.4204 | 62.0714 | 62.1749 | 123.1429 | 61.7812 | 123.0467 | 61.5086 | 61.5854 | 123.1812 | 61.5403 | 122.9731 | 61.5575 | 61.6026 | 61.4613 | 61.5064
2622.0625 | 123.3124 | -61.5097 | 61.615 | 0.17221 | 1.0401 | 1.4806 | 0.74417 | 0.85114 | 0.56631 | 0.61027 | 61.6104 | 0.23948 | 61.4958 | -0.03768 | 0.043657 | 61.6211 | -0.001436 | 61.4176 | 61.6819 | 62.5498 | 62.9903 | 62.2539 | 62.3608 | 62.076 | 62.12 | 123.1201 | 61.7492 | 123.0055 | 61.472 | 61.5534 | 123.1308 | 61.5083 | 122.9273 | 61.5667 | 61.6118 | 61.4522 | 61.4973
2623.0625 | 123.3444 | -61.5143 | 61.615 | 0.17679 | 1.0676 | 1.5493 | 0.77622 | 0.86945 | 0.58005 | 0.66063 | 61.5966 | 0.2349 | 61.5004 | -0.033101 | 0.034501 | 61.6394 | -0.001436 | 61.4268 | 61.6911 | 62.5818 | 63.0636 | 62.2905 | 62.3837 | 62.0943 | 62.1749 | 123.1109 | 61.7492 | 123.0147 | 61.4812 | 61.5488 | 123.1537 | 61.5128 | 122.941 | 61.5621 | 61.5981 | 61.4659 | 61.5018
2624.0625 | 123.2712 | -61.5189 | 61.6196 | 0.16764 | 1.0859 | 1.5264 | 0.76706 | 0.8603 | 0.56173 | 0.64232 | 61.6012 | 0.23032 | 61.5324 | -0.03768 | 0.029923 | 61.6348 | -0.006014 | 61.4268 | 61.6865 | 62.6047 | 63.0453 | 62.2859 | 62.3792 | 62.0806 | 62.1612 | 123.1201 | 61.7492 | 123.0513 | 61.4812 | 61.5488 | 123.1537 | 61.5128 | 122.9456 | 61.5713 | 61.6072 | 61.5025 | 61.5385
2625.0625 | 123.3124 | -61.5189 | 61.615 | 0.16764 | 1.0721 | 1.4944 | 0.77164 | 0.88319 | 0.54342 | 0.65148 | 61.6012 | 0.2349 | 61.537 | -0.042259 | 0.039079 | 61.6303 | -0.001436 | 61.4313 | 61.6865 | 62.591 | 63.0132 | 62.2905 | 62.402 | 62.0623 | 62.1703 | 123.1201 | 61.7538 | 123.0559 | 61.4766 | 61.5579 | 123.1491 | 61.5174 | 122.9502 | 61.5621 | 61.6026 | 61.4979 | 61.5385
2626.0625 | 123.3307 | -61.5189 | 61.6104 | 0.17679 | 1.0492 | 1.4623 | 0.73501 | 0.87403 | 0.53426 | 0.64232 | 61.6012 | 0.24405 | 61.537 | -0.028522 | 0.029923 | 61.6348 | -0.001436 | 61.4268 | 61.6957 | 62.5681 | 62.9812 | 62.2539 | 62.3929 | 62.0531 | 62.1612 | 123.1201 | 61.7629 | 123.0559 | 61.4903 | 61.5488 | 123.1537 | 61.5174 | 122.9456 | 61.5713 | 61.6026 | 61.5071 | 61.5385
2627.0781 | 123.3856 | -61.5051 | 61.6104 | 0.16306 | 1.0218 | 1.4211 | 0.73043 | 0.86945 | 0.55258 | 0.61943 | 61.592 | 0.23032 | 61.5324 | -0.042259 | 0.034501 | 61.6303 | 0.003143 | 61.4222 | 61.6682 | 62.5269 | 62.9262 | 62.2356 | 62.3746 | 62.0577 | 62.1246 | 123.0972 | 61.7354 | 123.0376 | 61.4629 | 61.5396 | 123.1354 | 61.5083 | 122.9273 | 61.5575 | 61.5889 | 61.4979 | 61.5293
2628.0625 | 123.2849 | -61.5326 | 61.6058 | 0.18137 | 1.0309 | 1.4257 | 0.76248 | 0.87861 | 0.53884 | 0.65148 | 61.592 | 0.23032 | 61.5233 | -0.03768 | 0.034501 | 61.6394 | -0.006014 | 61.4313 | 61.714 | 62.5635 | 62.9583 | 62.2951 | 62.4112 | 62.0714 | 62.1841 | 123.1246 | 61.7629 | 123.0559 | 61.4949 | 61.5671 | 123.172 | 61.5266 | 122.9639 | 61.5575 | 61.5981 | 61.4888 | 61.5293
2629.0625 | 123.3124 | -61.5005 | 61.6241 | 0.17221 | 0.98971 | 1.3845 | 0.74417 | 0.85114 | 0.49764 | 0.61943 | 61.6012 | 0.2349 | 61.5004 | -0.042259 | 0.034501 | 61.6303 | -0.001436 | 61.4222 | 61.6728 | 62.4903 | 62.885 | 62.2447 | 62.3517 | 61.9982 | 62.12 | 123.1017 | 61.7354 | 123.0009 | 61.4583 | 61.535 | 123.1308 | 61.4991 | 122.9227 | 61.5667 | 61.6026 | 61.4659 | 61.5018
2630.0625 | 123.3398 | -61.5005 | 61.615 | 0.17221 | 0.97598 | 1.3799 | 0.73501 | 0.84656 | 0.49306 | 0.6057 | 61.6012 | 0.2349 | 61.4958 | -0.042259 | 0.034501 | 61.6257 | -0.006014 | 61.4268 | 61.6728 | 62.4765 | 62.8804 | 62.2356 | 62.3471 | 61.9936 | 62.1062 | 123.1017 | 61.7354 | 122.9964 | 61.4583 | 61.535 | 123.1262 | 61.4945 | 122.9273 | 61.5667 | 61.6072 | 61.4613 | 61.5018
2631.0625 | 123.2437 | -61.5326 | 61.647 | 0.16764 | 0.99429 | 1.3845 | 0.7167 | 0.85572 | 0.51137 | 0.60112 | 61.6012 | 0.24405 | 61.4958 | -0.033101 | 0.039079 | 61.6348 | -0.006014 | 61.413 | 61.7002 | 62.5269 | 62.9171 | 62.2493 | 62.3883 | 62.044 | 62.1337 | 123.1338 | 61.7766 | 123.0284 | 61.4995 | 61.5717 | 123.1674 | 61.5266 | 122.9456 | 61.5621 | 61.6072 | 61.4567 | 61.5018
2632.0625 | 123.3353 | -61.5601 | 61.6562 | 0.17679 | 1.0218 | 1.3936 | 0.72128 | 0.85572 | 0.50222 | 0.60112 | 61.5966 | 0.2349 | 61.5004 | -0.03768 | 0.039079 | 61.6257 | -0.001436 | 61.4176 | 61.7369 | 62.5818 | 62.9537 | 62.2813 | 62.4158 | 62.0623 | 62.1612 | 123.1567 | 61.795 | 123.0605 | 61.5224 | 61.5991 | 123.1857 | 61.5586 | 122.9777 | 61.5575 | 61.5981 | 61.4613 | 61.5018
2633.0781 | 123.2986 | -61.5509 | 61.5829 | 0.18137 | 1.0355 | 1.4119 | 0.73043 | 0.85572 | 0.4839 | 0.57365 | 61.6012 | 0.2349 | 61.5096 | -0.03768 | 0.034501 | 61.6394 | -0.001436 | 61.413 | 61.7323 | 62.5864 | 62.9628 | 62.2813 | 62.4066 | 62.0348 | 62.1246 | 123.1521 | 61.7858 | 123.0605 | 61.5132 | 61.5854 | 123.1903 | 61.5495 | 122.9639 | 61.5667 | 61.6026 | 61.4751 | 61.511
2634.0625 | 123.3765 | -61.496 | 61.5921 | 0.18137 | 1.0538 | 1.4348 | 0.76248 | 0.87403 | 0.46101 | 0.59196 | 61.6012 | 0.2349 | 61.5187 | -0.042259 | 0.043657 | 61.6348 | -0.001436 | 61.4359 | 61.6773 | 62.5498 | 62.9308 | 62.2585 | 62.37 | 61.957 | 62.0879 | 123.0972 | 61.7309 | 123.0147 | 61.4537 | 61.5396 | 123.1308 | 61.4945 | 122.9319 | 61.5575 | 61.6026 | 61.4751 | 61.5202
2635.0625 | 123.3948 | -61.5051 | 61.5829 | 0.18137 | 1.0767 | 1.4532 | 0.78538 | 0.88319 | 0.48848 | 0.62401 | 61.6012 | 0.2349 | 61.5233 | -0.03768 | 0.039079 | 61.6303 | -0.001436 | 61.4222 | 61.6865 | 62.5818 | 62.9583 | 62.2905 | 62.3883 | 61.9936 | 62.1291 | 123.1063 | 61.74 | 123.0284 | 61.4674 | 61.5442 | 123.1354 | 61.5037 | 122.9273 | 61.5621 | 61.6026 | 61.4842 | 61.5247
2636.0781 | 123.3536 | -61.5372 | 61.5234 | 0.19968 | 1.095 | 1.4303 | 0.7808 | 0.87861 | 0.47932 | 0.62401 | 61.5966 | 0.23032 | 61.5279 | -0.046838 | 0.034501 | 61.6257 | -0.001436 | 61.4313 | 61.7369 | 62.6322 | 62.9674 | 62.318 | 62.4158 | 62.0165 | 62.1612 | 123.1338 | 61.7675 | 123.065 | 61.4903 | 61.5717 | 123.1628 | 61.5357 | 122.9685 | 61.5621 | 61.5981 | 61.4934 | 61.5293
2637.0625 | 123.3856 | -61.5189 | 61.5692 | 0.19511 | 1.1179 | 1.4303 | 0.78995 | 0.85572 | 0.48848 | 0.61027 | 61.5966 | 0.2349 | 61.5324 | -0.046838 | 0.043657 | 61.6348 | -0.001436 | 61.4176 | 61.714 | 62.6368 | 62.9491 | 62.3088 | 62.3746 | 62.0073 | 62.1291 | 123.1155 | 61.7538 | 123.0513 | 61.472 | 61.5625 | 123.1537 | 61.5174 | 122.9365 | 61.553 | 61.5981 | 61.4888 | 61.5339
2638.0781 | 123.2849 | -61.5509 | 61.6058 | 0.19511 | 1.063 | 1.3982 | 0.80827 | 0.82367 | 0.47932 | 0.59196 | 61.5966 | 0.23032 | 61.537 | -0.03768 | 0.029923 | 61.6348 | -0.001436 | 61.4313 | 61.746 | 62.6139 | 62.9491 | 62.3592 | 62.3746 | 62.0302 | 62.1429 | 123.1475 | 61.7812 | 123.0879 | 61.5132 | 61.5808 | 123.1857 | 61.5495 | 122.9822 | 61.5667 | 61.5981 | 61.5071 | 61.5385
2639.0625 | 123.3307 | -61.528 | 61.5875 | 0.19511 | 1.0309 | 1.3433 | 0.79911 | 0.80078 | 0.47475 | 0.57365 | 61.5966 | 0.2349 | 61.537 | -0.033101 | 0.043657 | 61.6303 | -0.001436 | 61.4268 | 61.7231 | 62.5589 | 62.8713 | 62.3271 | 62.3288 | 62.0028 | 62.1017 | 123.1246 | 61.7629 | 123.065 | 61.4949 | 61.5717 | 123.1583 | 61.5266 | 122.9548 | 61.553 | 61.5981 | 61.4934 | 61.5385
2640.0625 | 123.3948 | -61.5234 | 61.5326 | 0.19511 | 0.98513 | 1.3021 | 0.79453 | 0.79163 | 0.4839 | 0.54618 | 61.6012 | 0.2349 | 61.5324 | -0.042259 | 0.034501 | 61.6257 | -0.001436 | 61.4176 | 61.7185 | 62.5086 | 62.8255 | 62.318 | 62.3151 | 62.0073 | 62.0696 | 123.1246 | 61.7583 | 123.0559 | 61.4812 | 61.5579 | 123.1491 | 61.522 | 122.941 | 61.5667 | 61.6026 | 61.4979 | 61.5339
2641.0781 | 123.2758 | -61.5189 | 61.6241 | 0.19511 | 0.95766 | 1.27 | 0.7808 | 0.79163 | 0.51137 | 0.59196 | 61.6012 | 0.23032 | 61.5324 | -0.033101 | 0.034501 | 61.6257 | -0.006014 | 61.4222 | 61.714 | 62.4765 | 62.7889 | 62.2997 | 62.3105 | 62.0302 | 62.1108 | 123.1201 | 61.7492 | 123.0513 | 61.4858 | 61.5534 | 123.1445 | 61.5128 | 122.941 | 61.5667 | 61.6072 | 61.4979 | 61.5385
2642.0625 | 123.3627 | -61.5189 | 61.5738 | 0.19053 | 0.98513 | 1.3524 | 0.79453 | 0.8191 | 0.52969 | 0.65606 | 61.5966 | 0.23032 | 61.5187 | -0.042259 | 0.029923 | 61.6348 | -0.006014 | 61.4176 | 61.7094 | 62.504 | 62.8713 | 62.3134 | 62.338 | 62.0485 | 62.1749 | 123.1155 | 61.7492 | 123.0376 | 61.4766 | 61.5488 | 123.1537 | 61.5128 | 122.9365 | 61.5667 | 61.6026 | 61.4888 | 61.5247
2643.0625 | 123.317 | -61.5189 | 61.5738 | 0.19968 | 0.97598 | 1.3341 | 0.73959 | 0.82367 | 0.52053 | 0.66521 | 61.592 | 0.23032 | 61.5096 | -0.03768 | 0.034501 | 61.6303 | -0.001436 | 61.4222 | 61.7185 | 62.4948 | 62.853 | 62.2585 | 62.3425 | 62.0394 | 62.1841 | 123.1109 | 61.7492 | 123.0284 | 61.4812 | 61.5534 | 123.1491 | 61.5174 | 122.941 | 61.5575 | 61.5935 | 61.4751 | 61.511
2644.0625 | 123.3353 | -61.5509 | 61.6058 | 0.20884 | 1.0538 | 1.3707 | 0.78995 | 0.85572 | 0.55258 | 0.73846 | 61.592 | 0.2349 | 61.4912 | -0.033101 | 0.043657 | 61.6257 | 0.003143 | 61.4268 | 61.7597 | 62.6047 | 62.9216 | 62.3409 | 62.4066 | 62.1035 | 62.2894 | 123.1429 | 61.7858 | 123.0421 | 61.5178 | 61.5946 | 123.1766 | 61.554 | 122.9777 | 61.5484 | 61.5889 | 61.4476 | 61.4881
2645.0625 | 123.262 | -61.528 | 61.6058 | 0.20884 | 1.063 | 1.3982 | 0.79911 | 0.84198 | 0.56173 | 0.71557 | 61.5966 | 0.2349 | 61.4912 | -0.03768 | 0.034501 | 61.6394 | -0.001436 | 61.4176 | 61.7369 | 62.591 | 62.9262 | 62.3271 | 62.37 | 62.0898 | 62.2436 | 123.1246 | 61.7629 | 123.0193 | 61.4903 | 61.5625 | 123.1674 | 61.5266 | 122.9456 | 61.5621 | 61.5981 | 61.4567 | 61.4927
2646.0625 | 123.2941 | -61.5601 | 61.6241 | 0.218 | 1.0538 | 1.4028 | 0.79453 | 0.82825 | 0.54342 | 0.70642 | 61.5966 | 0.2349 | 61.4867 | -0.03768 | 0.034501 | 61.6394 | -0.006014 | 61.4176 | 61.7781 | 62.6139 | 62.9628 | 62.3546 | 62.3883 | 62.1035 | 62.2665 | 123.1567 | 61.795 | 123.0467 | 61.5224 | 61.5946 | 123.1995 | 61.554 | 122.9777 | 61.5621 | 61.6026 | 61.4522 | 61.4927
2647.0781 | 123.317 | -61.5326 | 61.6196 | 0.23173 | 1.0767 | 1.4348 | 0.80369 | 0.84198 | 0.56173 | 0.72931 | 61.592 | 0.22574 | 61.5004 | -0.042259 | 0.039079 | 61.6257 | 0.003143 | 61.4268 | 61.7643 | 62.6093 | 62.9674 | 62.3363 | 62.3746 | 62.0943 | 62.2619 | 123.1246 | 61.7583 | 123.033 | 61.4903 | 61.5717 | 123.1583 | 61.5357 | 122.9594 | 61.553 | 61.5889 | 61.4613 | 61.4973
2648.0625 | 123.3124 | -61.5189 | 61.6013 | 0.23173 | 1.0538 | 1.4577 | 0.80369 | 0.83283 | 0.56173 | 0.73389 | 61.5829 | 0.2349 | 61.5233 | -0.03768 | 0.034501 | 61.6394 | -0.001436 | 61.4313 | 61.7506 | 62.5727 | 62.9766 | 62.3226 | 62.3517 | 62.0806 | 62.2527 | 123.1017 | 61.7538 | 123.0422 | 61.4812 | 61.5534 | 123.1583 | 61.5174 | 122.9502 | 61.5484 | 61.5843 | 61.4888 | 61.5247
2649.0625 | 123.2986 | -61.5189 | 61.6013 | 0.22715 | 1.0447 | 1.4119 | 0.79453 | 0.82367 | 0.548 | 0.72015 | 61.6012 | 0.2349 | 61.5279 | -0.046838 | 0.029923 | 61.6348 | -0.006014 | 61.4268 | 61.746 | 62.5635 | 62.9308 | 62.3134 | 62.3425 | 62.0669 | 62.239 | 123.1201 | 61.7538 | 123.0467 | 61.472 | 61.5488 | 123.1537 | 61.5128 | 122.9456 | 61.5713 | 61.6072 | 61.4979 | 61.5339
2650.0781 | 123.3444 | -61.528 | 61.6013 | 0.22258 | 1.0218 | 1.3891 | 0.80827 | 0.80994 | 0.52053 | 0.66063 | 61.6012 | 0.23032 | 61.5279 | -0.03768 | 0.048236 | 61.6303 | -0.001436 | 61.4268 | 61.7506 | 62.5498 | 62.9171 | 62.3363 | 62.338 | 62.0485 | 62.1886 | 123.1292 | 61.7583 | 123.0559 | 61.4903 | 61.5763 | 123.1583 | 61.5266 | 122.9548 | 61.553 | 61.6026 | 61.4796 | 61.5293
2651.0625 | 123.2758 | -61.5189 | 61.6425 | 0.22715 | 0.9714 | 1.3616 | 0.80827 | 0.79621 | 0.51595 | 0.65606 | 61.6149 | 0.23032 | 61.537 | -0.042259 | 0.039079 | 61.6303 | -0.006014 | 61.4268 | 61.746 | 62.4903 | 62.8804 | 62.3271 | 62.3151 | 62.0348 | 62.1749 | 123.1338 | 61.7492 | 123.0559 | 61.4766 | 61.5579 | 123.1491 | 61.5128 | 122.9456 | 61.5759 | 61.6209 | 61.4979 | 61.543
2652.0625 | 123.2849 | -61.5005 | 61.647 | 0.22258 | 0.9714 | 1.3524 | 0.79911 | 0.80078 | 0.52969 | 0.65148 | 61.6058 | 0.2349 | 61.5279 | -0.033101 | 0.039079 | 61.6348 | 0.003143 | 61.4405 | 61.7231 | 62.4719 | 62.853 | 62.2997 | 62.3013 | 62.0302 | 62.152 | 123.1063 | 61.7354 | 123.0284 | 61.4674 | 61.5396 | 123.1354 | 61.5037 | 122.941 | 61.5667 | 61.6026 | 61.4888 | 61.5247
2653.0625 | 123.2986 | -61.5555 | 61.6379 | 0.22715 | 0.98971 | 1.3524 | 0.79911 | 0.83283 | 0.55258 | 0.70642 | 61.5966 | 0.2349 | 61.5233 | -0.042259 | 0.034501 | 61.6348 | -0.001436 | 61.4313 | 61.7826 | 62.5452 | 62.9079 | 62.3546 | 62.3883 | 62.1081 | 62.2619 | 123.1521 | 61.7904 | 123.0788 | 61.5132 | 61.59 | 123.1903 | 61.554 | 122.9868 | 61.5621 | 61.5981 | 61.4888 | 61.5247
2654.0625 | 123.349 | -61.5097 | 61.6013 | 0.22258 | 0.96682 | 1.3433 | 0.78538 | 0.8191 | 0.52511 | 0.73389 | 61.5966 | 0.2349 | 61.4958 | -0.03768 | 0.034501 | 61.6303 | -0.001436 | 61.4313 | 61.7323 | 62.4765 | 62.853 | 62.2951 | 62.3288 | 62.0348 | 62.2436 | 123.1063 | 61.7446 | 123.0055 | 61.472 | 61.5442 | 123.14 | 61.5083 | 122.941 | 61.5621 | 61.5981 | 61.4613 | 61.4973
2655.0781 | 123.349 | -61.5189 | 61.5921 | 0.22258 | 0.9485 | 1.3021 | 0.77164 | 0.80078 | 0.52053 | 0.71099 | 61.592 | 0.2349 | 61.5187 | -0.042259 | 0.034501 | 61.6257 | -0.010593 | 61.4176 | 61.7414 | 62.4674 | 62.8209 | 62.2905 | 62.3196 | 62.0394 | 62.2299 | 123.1109 | 61.7538 | 123.0376 | 61.4766 | 61.5534 | 123.1445 | 61.5083 | 122.9365 | 61.5575 | 61.6026 | 61.4842 | 61.5293
2656.0625 | 123.4085 | -61.496 | 61.5921 | 0.22715 | 0.95308 | 1.3204 | 0.80369 | 0.80536 | 0.54342 | 0.71557 | 61.6012 | 0.23032 | 61.537 | -0.042259 | 0.043657 | 61.6394 | -0.001436 | 61.4268 | 61.7231 | 62.4491 | 62.8163 | 62.2997 | 62.3013 | 62.0394 | 62.2115 | 123.0972 | 61.7263 | 123.033 | 61.4537 | 61.5396 | 123.1354 | 61.4945 | 122.9227 | 61.5575 | 61.6026 | 61.4934 | 61.5385
2657.0625 | 123.4085 | -61.5051 | 61.5738 | 0.22258 | 0.93477 | 1.3066 | 0.7808 | 0.80536 | 0.53426 | 0.66979 | 61.6012 | 0.23032 | 61.5324 | -0.03768 | 0.039079 | 61.6348 | -0.001436 | 61.4313 | 61.7277 | 62.4399 | 62.8118 | 62.2859 | 62.3105 | 62.0394 | 62.1749 | 123.1063 | 61.7354 | 123.0376 | 61.4674 | 61.5442 | 123.14 | 61.5037 | 122.9365 | 61.5621 | 61.6026 | 61.4934 | 61.5339
2658.0625 | 123.3719 | -61.5417 | 61.5967 | 0.22715 | 0.92103 | 1.2837 | 0.79453 | 0.80536 | 0.548 | 0.66063 | 61.6012 | 0.24405 | 61.537 | -0.042259 | 0.039079 | 61.6257 | -0.006014 | 61.4268 | 61.7689 | 62.4628 | 62.8255 | 62.3363 | 62.3471 | 62.0897 | 62.2024 | 123.1429 | 61.7858 | 123.0788 | 61.4995 | 61.5808 | 123.1674 | 61.5357 | 122.9685 | 61.5621 | 61.6072 | 61.4979 | 61.543
2659.0625 | 123.381 | -61.5372 | 61.5738 | 0.22258 | 0.87524 | 1.2334 | 0.7808 | 0.79163 | 0.52969 | 0.64232 | 61.5966 | 0.2349 | 61.505 | -0.03768 | 0.039079 | 61.6348 | 0.003143 | 61.413 | 61.7597 | 62.4124 | 62.7706 | 62.318 | 62.3288 | 62.0669 | 62.1795 | 123.1338 | 61.7721 | 123.0422 | 61.4995 | 61.5762 | 123.172 | 61.5403 | 122.9502 | 61.5575 | 61.5935 | 61.4659 | 61.5018
2660.0625 | 123.3719 | -61.528 | 61.5692 | 0.20884 | 0.85693 | 1.2242 | 0.78995 | 0.79163 | 0.53426 | 0.65148 | 61.5966 | 0.23032 | 61.5233 | -0.042259 | 0.034501 | 61.6303 | -0.010593 | 61.4268 | 61.7369 | 62.3849 | 62.7522 | 62.318 | 62.3196 | 62.0623 | 62.1795 | 123.1246 | 61.7583 | 123.0513 | 61.4858 | 61.5625 | 123.1583 | 61.5174 | 122.9548 | 61.5621 | 61.6072 | 61.4888 | 61.5339
2661.0625 | 123.3078 | -61.5143 | 61.5692 | 0.20884 | 0.85693 | 1.1922 | 0.76706 | 0.78705 | 0.55258 | 0.64232 | 61.6012 | 0.23948 | 61.5324 | -0.03768 | 0.034501 | 61.6303 | -0.006014 | 61.4313 | 61.7231 | 62.3712 | 62.7065 | 62.2813 | 62.3013 | 62.0669 | 62.1566 | 123.1155 | 61.7538 | 123.0467 | 61.4766 | 61.5488 | 123.1445 | 61.5083 | 122.9456 | 61.5667 | 61.6072 | 61.4979 | 61.5385
2662.0625 | 123.3398 | -61.5189 | 61.5555 | 0.19968 | 0.85235 | 1.1739 | 0.74417 | 0.78705 | 0.55258 | 0.63774 | 61.6058 | 0.23032 | 61.537 | -0.03768 | 0.034501 | 61.6348 | -0.001436 | 61.4176 | 61.7185 | 62.3712 | 62.6927 | 62.263 | 62.3059 | 62.0714 | 62.1566 | 123.1246 | 61.7492 | 123.0559 | 61.4812 | 61.5534 | 123.1537 | 61.5174 | 122.9365 | 61.5713 | 61.6072 | 61.5025 | 61.5385
2663.0625 | 123.3627 | -61.5143 | 61.5692 | 0.19968 | 0.82488 | 1.1235 | 0.72586 | 0.76416 | 0.548 | 0.61485 | 61.5966 | 0.2349 | 61.5279 | -0.03768 | 0.034501 | 61.6211 | -0.006014 | 61.4176 | 61.714 | 62.3392 | 62.6378 | 62.2401 | 62.2784 | 62.0623 | 62.1291 | 123.1109 | 61.7492 | 123.0422 | 61.4766 | 61.5488 | 123.1354 | 61.5083 | 122.9319 | 61.5621 | 61.6026 | 61.4934 | 61.5339
2664.0625 | 123.381 | -61.528 | 61.5738 | 0.20426 | 0.82488 | 1.1098 | 0.73501 | 0.755 | 0.54342 | 0.59654 | 61.6012 | 0.2349 | 61.505 | -0.046838 | 0.034501 | 61.6348 | -0.010593 | 61.4222 | 61.7323 | 62.3529 | 62.6378 | 62.263 | 62.283 | 62.0714 | 62.1246 | 123.1292 | 61.7629 | 123.033 | 61.4812 | 61.5625 | 123.1628 | 61.5174 | 122.9502 | 61.5667 | 61.6118 | 61.4705 | 61.5156
2665.0625 | 123.3719 | -61.4822 | 61.5738 | 0.20426 | 0.83403 | 1.0869 | 0.76706 | 0.755 | 0.56173 | 0.61485 | 61.592 | 0.23948 | 61.5004 | -0.042259 | 0.039079 | 61.6303 | -0.001436 | 61.4176 | 61.6865 | 62.3163 | 62.5691 | 62.2493 | 62.2372 | 62.044 | 62.0971 | 123.0743 | 61.7217 | 122.9826 | 61.44 | 61.5213 | 123.1125 | 61.4808 | 122.8998 | 61.553 | 61.5935 | 61.4613 | 61.5018
2666.0625 | 123.3948 | -61.496 | 61.5646 | 0.19968 | 0.82488 | 1.0823 | 0.75333 | 0.74585 | 0.548 | 0.61943 | 61.6012 | 0.23032 | 61.5004 | -0.042259 | 0.029923 | 61.6257 | -0.001436 | 61.4176 | 61.6957 | 62.3208 | 62.5783 | 62.2493 | 62.2418 | 62.044 | 62.1154 | 123.0972 | 61.7263 | 122.9964 | 61.4537 | 61.5259 | 123.1216 | 61.4945 | 122.9136 | 61.5713 | 61.6026 | 61.4705 | 61.5018
2667.0781 | 123.381 | -61.5143 | 61.5967 | 0.20426 | 0.80656 | 1.0686 | 0.72586 | 0.73669 | 0.53426 | 0.61485 | 61.5966 | 0.2349 | 61.5324 | -0.033101 | 0.034501 | 61.6211 | 0.003143 | 61.4222 | 61.7185 | 62.3208 | 62.5828 | 62.2401 | 62.251 | 62.0485 | 62.1291 | 123.1109 | 61.7492 | 123.0467 | 61.4812 | 61.5488 | 123.1354 | 61.5174 | 122.9365 | 61.5621 | 61.5935 | 61.4979 | 61.5293
2668.0625 | 123.3124 | -61.5051 | 61.5829 | 0.19968 | 0.77909 | 1.0273 | 0.72128 | 0.74127 | 0.53884 | 0.61485 | 61.6058 | 0.2349 | 61.537 | -0.033101 | 0.034501 | 61.6211 | -0.006014 | 61.4176 | 61.7048 | 62.2842 | 62.5325 | 62.2264 | 62.2464 | 62.044 | 62.12 | 123.1109 | 61.74 | 123.0422 | 61.472 | 61.5396 | 123.1262 | 61.4991 | 122.9227 | 61.5713 | 61.6118 | 61.5025 | 61.543
2669.0625 | 123.2986 | -61.5326 | 61.5967 | 0.19968 | 0.77451 | 1.0319 | 0.73043 | 0.74127 | 0.52969 | 0.61485 | 61.6058 | 0.23948 | 61.537 | -0.03768 | 0.039079 | 61.6211 | -0.001436 | 61.4222 | 61.7323 | 62.3071 | 62.5645 | 62.263 | 62.2739 | 62.0623 | 62.1474 | 123.1384 | 61.7721 | 123.0696 | 61.4949 | 61.5717 | 123.1537 | 61.5312 | 122.9548 | 61.5667 | 61.6072 | 61.4979 | 61.5385
2670.0625 | 123.2849 | -61.5189 | 61.615 | 0.20884 | 0.74246 | 0.97698 | 0.72128 | 0.72296 | 0.51137 | 0.60112 | 61.6149 | 0.2349 | 61.537 | -0.03768 | 0.034501 | 61.6211 | 0.003143 | 61.4222 | 61.7277 | 62.2613 | 62.4958 | 62.2401 | 62.2418 | 62.0302 | 62.12 | 123.1338 | 61.7538 | 123.0559 | 61.4812 | 61.5534 | 123.14 | 61.522 | 122.941 | 61.5804 | 61.6118 | 61.5025 | 61.5339
2671.0625 | 123.2941 | -61.528 | 61.6104 | 0.21342 | 0.77909 | 1.0045 | 0.75791 | 0.74127 | 0.55716 | 0.63316 | 61.6149 | 0.2349 | 61.537 | -0.03768 | 0.043657 | 61.6211 | -0.001436 | 61.4222 | 61.7414 | 62.3071 | 62.5325 | 62.2859 | 62.2693 | 62.0852 | 62.1612 | 123.1429 | 61.7629 | 123.065 | 61.4903 | 61.5717 | 123.1491 | 61.5266 | 122.9502 | 61.5713 | 61.6164 | 61.4934 | 61.5385
2672.0625 | 123.2712 | -61.5372 | 61.6196 | 0.20884 | 0.79282 | 0.99529 | 0.74875 | 0.73669 | 0.55716 | 0.62401 | 61.6058 | 0.23948 | 61.5462 | -0.03768 | 0.039079 | 61.6348 | -0.001436 | 61.4176 | 61.746 | 62.33 | 62.5325 | 62.2859 | 62.2739 | 62.0943 | 62.1612 | 123.1429 | 61.7766 | 123.0834 | 61.4995 | 61.5762 | 123.172 | 61.5357 | 122.9548 | 61.5667 | 61.6072 | 61.5071 | 61.5476
2673.0625 | 123.2803 | -61.5463 | 61.6241 | 0.20884 | 0.81114 | 1.009 | 0.77164 | 0.74127 | 0.57547 | 0.61485 | 61.6149 | 0.23948 | 61.5324 | -0.03768 | 0.039079 | 61.6211 | -0.001436 | 61.4268 | 61.7552 | 62.3575 | 62.5554 | 62.318 | 62.2876 | 62.1218 | 62.1612 | 123.1613 | 61.7858 | 123.0788 | 61.5086 | 61.5854 | 123.1674 | 61.5449 | 122.9731 | 61.5759 | 61.6164 | 61.4934 | 61.5339
2674.0625 | 123.2346 | -61.5372 | 61.6287 | 0.22258 | 0.84319 | 1.0273 | 0.76706 | 0.75043 | 0.59378 | 0.61027 | 61.6104 | 0.2349 | 61.537 | -0.042259 | 0.029923 | 61.6348 | -0.006014 | 61.4176 | 61.7597 | 62.3804 | 62.5645 | 62.3042 | 62.2876 | 62.131 | 62.1474 | 123.1475 | 61.7721 | 123.0742 | 61.4949 | 61.5671 | 123.172 | 61.5312 | 122.9548 | 61.5804 | 61.6164 | 61.5071 | 61.543
2675.0625 | 123.2986 | -61.5189 | 61.6013 | 0.218 | 0.85693 | 1.0548 | 0.80369 | 0.76874 | 0.61668 | 0.65148 | 61.6058 | 0.23032 | 61.537 | -0.042259 | 0.034501 | 61.6257 | 0.003143 | 61.4268 | 61.7369 | 62.3758 | 62.5737 | 62.3226 | 62.2876 | 62.1355 | 62.1703 | 123.1246 | 61.7492 | 123.0559 | 61.4766 | 61.5534 | 123.1445 | 61.522 | 122.9456 | 61.5713 | 61.6026 | 61.5025 | 61.5339
2676.0625 | 123.317 | -61.5143 | 61.6196 | 0.21342 | 0.81572 | 0.99987 | 0.78995 | 0.74585 | 0.57089 | 0.62859 | 61.6058 | 0.2349 | 61.537 | -0.03768 | 0.034501 | 61.6257 | -0.006014 | 61.4268 | 61.7277 | 62.33 | 62.5142 | 62.3042 | 62.2601 | 62.0852 | 62.1429 | 123.1201 | 61.7492 | 123.0513 | 61.4766 | 61.5488 | 123.14 | 61.5083 | 122.941 | 61.5713 | 61.6118 | 61.5025 | 61.543
2677.0781 | 123.262 | -61.5372 | 61.615 | 0.20884 | 0.80656 | 0.99071 | 0.76706 | 0.71838 | 0.54342 | 0.60112 | 61.6104 | 0.23032 | 61.5416 | -0.03768 | 0.029923 | 61.6257 | -0.001436 | 61.4176 | 61.746 | 62.3437 | 62.5279 | 62.3042 | 62.2556 | 62.0806 | 62.1383 | 123.1475 | 61.7675 | 123.0788 | 61.4995 | 61.5671 | 123.1628 | 61.5357 | 122.9548 | 61.5804 | 61.6118 | 61.5117 | 61.543
2678.0625 | 123.3353 | -61.5372 | 61.6104 | 0.21342 | 0.81114 | 0.99071 | 0.80369 | 0.72754 | 0.58463 | 0.6057 | 61.6058 | 0.23948 | 61.5462 | -0.046838 | 0.039079 | 61.6257 | 0.003143 | 61.4268 | 61.7506 | 62.3483 | 62.5279 | 62.3409 | 62.2647 | 62.1218 | 62.1429 | 123.1429 | 61.7766 | 123.0834 | 61.4903 | 61.5762 | 123.1628 | 61.5403 | 122.9639 | 61.5667 | 61.6026 | 61.5071 | 61.543
2679.0625 | 123.2803 | -61.5189 | 61.6287 | 0.218 | 0.77451 | 0.96782 | 0.78538 | 0.7138 | 0.55716 | 0.57823 | 61.6104 | 0.2349 | 61.5416 | -0.03768 | 0.039079 | 61.6211 | -0.006014 | 61.4176 | 61.7369 | 62.2934 | 62.4867 | 62.3042 | 62.2327 | 62.076 | 62.0971 | 123.1292 | 61.7538 | 123.0605 | 61.4812 | 61.5579 | 123.14 | 61.5128 | 122.9365 | 61.5713 | 61.6164 | 61.5025 | 61.5476
2680.0625 | 123.317 | -61.5555 | 61.6699 | 0.20884 | 0.76993 | 0.94951 | 0.75333 | 0.69091 | 0.53884 | 0.58281 | 61.6058 | 0.2349 | 61.537 | -0.03768 | 0.043657 | 61.6211 | 0.003143 | 61.4222 | 61.7643 | 62.3254 | 62.505 | 62.3088 | 62.2464 | 62.0943 | 62.1383 | 123.1613 | 61.7904 | 123.0925 | 61.5178 | 61.5991 | 123.1766 | 61.5586 | 122.9777 | 61.5621 | 61.6026 | 61.4934 | 61.5339
2681.0625 | 123.2941 | -61.5051 | 61.6608 | 0.218 | 0.77451 | 0.93119 | 0.76706 | 0.72754 | 0.57089 | 0.59196 | 61.6012 | 0.2349 | 61.5279 | -0.033101 | 0.034501 | 61.6211 | -0.001436 | 61.4176 | 61.7231 | 62.2796 | 62.4363 | 62.2722 | 62.2327 | 62.076 | 62.0971 | 123.1063 | 61.74 | 123.033 | 61.472 | 61.5396 | 123.1262 | 61.5037 | 122.9227 | 61.5667 | 61.6026 | 61.4934 | 61.5293
2682.0625 | 123.2803 | -61.528 | 61.6608 | 0.218 | 0.7333 | 0.91288 | 0.73959 | 0.7138 | 0.53884 | 0.60112 | 61.6012 | 0.2349 | 61.5096 | -0.03768 | 0.034501 | 61.6211 | 0.003143 | 61.4176 | 61.746 | 62.2613 | 62.4409 | 62.2676 | 62.2418 | 62.0669 | 62.1291 | 123.1292 | 61.7629 | 123.0376 | 61.4903 | 61.5625 | 123.1491 | 61.5312 | 122.9456 | 61.5667 | 61.5981 | 61.4751 | 61.5064
2683.0625 | 123.2529 | -61.528 | 61.6379 | 0.218 | 0.72414 | 0.92661 | 0.73043 | 0.70007 | 0.52511 | 0.58281 | 61.6012 | 0.2349 | 61.5004 | -0.03768 | 0.039079 | 61.6165 | -0.001436 | 61.4222 | 61.746 | 62.2522 | 62.4546 | 62.2585 | 62.2281 | 62.0531 | 62.1108 | 123.1292 | 61.7629 | 123.0284 | 61.4903 | 61.5671 | 123.1445 | 61.5266 | 122.9502 | 61.5621 | 61.6026 | 61.4613 | 61.5018
2684.0625 | 123.2986 | -61.5372 | 61.6425 | 0.218 | 0.7104 | 0.93577 | 0.73043 | 0.68176 | 0.53884 | 0.56907 | 61.6104 | 0.22574 | 61.5141 | -0.03768 | 0.039079 | 61.6211 | -0.001436 | 61.4176 | 61.7552 | 62.2476 | 62.4729 | 62.2676 | 62.2189 | 62.076 | 62.1062 | 123.1475 | 61.7629 | 123.0513 | 61.4995 | 61.5762 | 123.1583 | 61.5357 | 122.9548 | 61.5713 | 61.6118 | 61.4751 | 61.5156
2685.0625 | 123.3353 | -61.4914 | 61.6013 | 0.22258 | 0.68293 | 0.89914 | 0.70296 | 0.67718 | 0.51595 | 0.5416 | 61.6058 | 0.2349 | 61.5233 | -0.03768 | 0.043657 | 61.6257 | -0.006014 | 61.4176 | 61.714 | 62.1743 | 62.3905 | 62.1944 | 62.1686 | 62.0073 | 62.033 | 123.0972 | 61.7263 | 123.0147 | 61.4537 | 61.5351 | 123.1171 | 61.4854 | 122.909 | 61.5621 | 61.6118 | 61.4796 | 61.5293
2686.0781 | 123.3215 | -61.5234 | 61.6333 | 0.22258 | 0.69209 | 0.89456 | 0.70754 | 0.68176 | 0.52053 | 0.5416 | 61.6149 | 0.2349 | 61.5416 | -0.042259 | 0.039079 | 61.6211 | -0.001436 | 61.4176 | 61.746 | 62.2155 | 62.418 | 62.231 | 62.2052 | 62.044 | 62.065 | 123.1384 | 61.7583 | 123.065 | 61.4812 | 61.5625 | 123.1445 | 61.522 | 122.941 | 61.5759 | 61.6164 | 61.5025 | 61.543
2687.0625 | 123.4268 | -61.5234 | 61.6333 | 0.21342 | 0.67378 | 0.85794 | 0.69839 | 0.68634 | 0.51595 | 0.51413 | 61.6104 | 0.23032 | 61.5416 | -0.03768 | 0.034501 | 61.6257 | -0.006014 | 61.4222 | 61.7369 | 62.1972 | 62.3814 | 62.2218 | 62.2098 | 62.0394 | 62.0376 | 123.1338 | 61.7538 | 123.065 | 61.4858 | 61.5579 | 123.1491 | 61.5174 | 122.9456 | 61.5759 | 61.6164 | 61.5071 | 61.5476
2688.0625 | 123.4039 | -61.4731 | 61.6013 | 0.21342 | 0.67378 | 0.82588 | 0.72128 | 0.71838 | 0.548 | 0.5416 | 61.6104 | 0.2349 | 61.5508 | -0.03768 | 0.039079 | 61.6257 | 0.003143 | 61.4222 | 61.6865 | 62.1469 | 62.299 | 62.1944 | 62.1915 | 62.0211 | 62.0147 | 123.0834 | 61.708 | 123.0238 | 61.4354 | 61.5122 | 123.0988 | 61.4762 | 122.8953 | 61.5713 | 61.6072 | 61.5117 | 61.5476
2689.0625 | 123.3902 | -61.5097 | 61.6104 | 0.218 | 0.67835 | 0.8442 | 0.73043 | 0.75043 | 0.54342 | 0.55991 | 61.6104 | 0.2349 | 61.5462 | -0.03768 | 0.034501 | 61.6211 | 0.007721 | 61.4176 | 61.7277 | 62.1881 | 62.3539 | 62.2401 | 62.2601 | 62.0531 | 62.0696 | 123.1201 | 61.7446 | 123.0559 | 61.472 | 61.5442 | 123.1308 | 61.5174 | 122.9273 | 61.5759 | 61.6026 | 61.5117 | 61.5385
2690.0781 | 123.3261 | -61.5372 | 61.5738 | 0.22715 | 0.7104 | 0.92661 | 0.72586 | 0.75043 | 0.55258 | 0.55076 | 61.6058 | 0.2349 | 61.537 | -0.03768 | 0.039079 | 61.6303 | 0.003143 | 61.4222 | 61.7643 | 62.2476 | 62.4638 | 62.263 | 62.2876 | 62.0897 | 62.0879 | 123.1429 | 61.7721 | 123.0742 | 61.4995 | 61.5762 | 123.1674 | 61.5403 | 122.9593 | 61.5667 | 61.6026 | 61.4979 | 61.5339
2691.0625 | 123.4131 | -61.5005 | 61.6058 | 0.218 | 0.70125 | 0.89914 | 0.70754 | 0.74127 | 0.52511 | 0.53702 | 61.6104 | 0.24405 | 61.537 | -0.03768 | 0.043657 | 61.6257 | -0.001436 | 61.4176 | 61.7185 | 62.2018 | 62.3997 | 62.2081 | 62.2418 | 62.0257 | 62.0376 | 123.1109 | 61.7446 | 123.0376 | 61.4629 | 61.5442 | 123.1262 | 61.4991 | 122.9181 | 61.5667 | 61.6118 | 61.4934 | 61.5385
2692.0938 | 123.3902 | -61.5097 | 61.615 | 0.22258 | 0.69667 | 0.92661 | 0.69839 | 0.73211 | 0.52511 | 0.55534 | 61.6012 | 0.23032 | 61.505 | -0.042259 | 0.034501 | 61.6257 | 0.003143 | 61.4176 | 61.7323 | 62.2064 | 62.4363 | 62.2081 | 62.2418 | 62.0348 | 62.065 | 123.1109 | 61.74 | 123.0147 | 61.4674 | 61.5442 | 123.1354 | 61.5128 | 122.9273 | 61.5667 | 61.5981 | 61.4705 | 61.5018
2693.0625 | 123.3398 | -61.5326 | 61.5875 | 0.22715 | 0.72414 | 0.93577 | 0.7167 | 0.75043 | 0.55716 | 0.61485 | 61.6012 | 0.2349 | 61.5096 | -0.042259 | 0.039079 | 61.6257 | 0.003143 | 61.413 | 61.7597 | 62.2567 | 62.4684 | 62.2493 | 62.283 | 62.0897 | 62.1474 | 123.1338 | 61.7675 | 123.0422 | 61.4903 | 61.5717 | 123.1583 | 61.5357 | 122.9456 | 61.5621 | 61.5981 | 61.4705 | 61.5064
2694.0625 | 123.349 | -61.5097 | 61.6241 | 0.23173 | 0.71498 | 0.95866 | 0.69839 | 0.74127 | 0.53884 | 0.63316 | 61.6104 | 0.23948 | 61.5187 | -0.03768 | 0.039079 | 61.6257 | 0.003143 | 61.4176 | 61.7414 | 62.2247 | 62.4684 | 62.2081 | 62.251 | 62.0485 | 62.1429 | 123.1201 | 61.7492 | 123.0284 | 61.472 | 61.5488 | 123.1354 | 61.5128 | 122.9273 | 61.5713 | 61.6072 | 61.4796 | 61.5156
2695.125 | 123.2208 | -61.5784 | 61.5784 | 0.24547 | 0.72872 | 0.96782 | 0.71212 | 0.76416 | 0.55716 | 0.65606 | 61.6012 | 0.2349 | 61.505 | -0.042259 | 0.029923 | 61.6211 | 0.003143 | 61.4176 | 61.8238 | 62.3071 | 62.5462 | 62.2905 | 62.3425 | 62.1355 | 62.2344 | 123.1796 | 61.8133 | 123.0833 | 61.5361 | 61.6083 | 123.1995 | 61.5815 | 122.996 | 61.5713 | 61.5981 | 61.4751 | 61.5018
2696.0625 | 123.349 | -61.5372 | 61.5601 | 0.24547 | 0.76535 | 0.99529 | 0.74417 | 0.79621 | 0.60294 | 0.68353 | 61.6012 | 0.23032 | 61.5279 | -0.033101 | 0.039079 | 61.6257 | -0.001436 | 61.413 | 61.7826 | 62.3025 | 62.5325 | 62.2813 | 62.3334 | 62.1401 | 62.2207 | 123.1384 | 61.7675 | 123.065 | 61.5041 | 61.5762 | 123.1628 | 61.5357 | 122.9502 | 61.5621 | 61.6026 | 61.4888 | 61.5293
2697.0781 | 123.3856 | -61.5372 | 61.5509 | 0.25462 | 0.76077 | 0.99529 | 0.75333 | 0.80994 | 0.63957 | 0.66979 | 61.6058 | 0.2349 | 61.5324 | -0.033101 | 0.034501 | 61.6257 | -0.001436 | 61.4176 | 61.7918 | 62.2979 | 62.5325 | 62.2905 | 62.3471 | 62.1767 | 62.207 | 123.1429 | 61.7721 | 123.0696 | 61.5041 | 61.5717 | 123.1628 | 61.5357 | 122.9548 | 61.5713 | 61.6072 | 61.4979 | 61.5339
2698.0625 | 123.3765 | -61.5097 | 61.5738 | 0.24547 | 0.73788 | 0.9724 | 0.73501 | 0.81452 | 0.62583 | 0.63316 | 61.5966 | 0.2349 | 61.537 | -0.033101 | 0.039079 | 61.6211 | 0.003143 | 61.4176 | 61.7552 | 62.2476 | 62.4821 | 62.2447 | 62.3242 | 62.1355 | 62.1429 | 123.1063 | 61.7446 | 123.0467 | 61.4766 | 61.5488 | 123.1308 | 61.5128 | 122.9273 | 61.5575 | 61.5935 | 61.4979 | 61.5339
2699.0938 | 123.2803 | -61.528 | 61.6653 | 0.33703 | 0.69667 | 0.89914 | 0.72128 | 0.81452 | 0.59378 | 0.51871 | 61.6104 | 0.23032 | 61.5416 | -0.03768 | 0.043657 | 61.6257 | -0.006014 | 61.4176 | 61.8651 | 62.2247 | 62.4272 | 62.2493 | 62.3425 | 62.1218 | 62.0467 | 123.1384 | 61.7583 | 123.0696 | 61.4903 | 61.5717 | 123.1537 | 61.522 | 122.9456 | 61.5667 | 61.6164 | 61.4979 | 61.5476
2700.0625 | 123.4085 | -61.5189 | 61.5967 | 0.44234 | 0.70125 | 0.88999 | 0.72128 | 0.82367 | 0.60294 | 0.45919 | 61.6104 | 0.23948 | 61.537 | -0.033101 | 0.039079 | 61.6257 | -0.001436 | 61.4222 | 61.9612 | 62.2201 | 62.4088 | 62.2401 | 62.3425 | 62.1218 | 61.9781 | 123.1292 | 61.7583 | 123.0559 | 61.4858 | 61.5579 | 123.1445 | 61.5174 | 122.941 | 61.5713 | 61.6118 | 61.4979 | 61.5385
2701.0625 | 123.3765 | -61.5234 | 61.5784 | 0.44234 | 0.70125 | 0.89914 | 0.73501 | 0.84198 | 0.63041 | 0.46377 | 61.6058 | 0.2349 | 61.537 | -0.042259 | 0.034501 | 61.6211 | -0.006014 | 61.4176 | 61.9658 | 62.2247 | 62.4226 | 62.2585 | 62.3654 | 62.1538 | 61.9872 | 123.1292 | 61.7583 | 123.0605 | 61.4812 | 61.5579 | 123.1445 | 61.5174 | 122.941 | 61.5713 | 61.6118 | 61.5025 | 61.543
2702.0625 | 123.3627 | -61.528 | 61.5829 | 0.4286 | 0.63257 | 0.86709 | 0.69839 | 0.80536 | 0.59836 | 0.44088 | 61.6104 | 0.23948 | 61.537 | -0.042259 | 0.039079 | 61.6303 | 0.007721 | 61.4176 | 61.9566 | 62.1606 | 62.3951 | 62.2264 | 62.3334 | 62.1264 | 61.9689 | 123.1384 | 61.7675 | 123.065 | 61.4858 | 61.5671 | 123.1583 | 61.5357 | 122.9456 | 61.5713 | 61.6026 | 61.4979 | 61.5293
2703.0625 | 123.2758 | -61.5417 | 61.6013 | 0.45149 | 0.63257 | 0.91746 | 0.71212 | 0.84198 | 0.61668 | 0.46835 | 61.6058 | 0.23032 | 61.5324 | -0.03768 | 0.039079 | 61.6257 | -0.001436 | 61.4176 | 61.9932 | 62.1743 | 62.4592 | 62.2539 | 62.3837 | 62.1584 | 62.0101 | 123.1475 | 61.7721 | 123.0742 | 61.5041 | 61.5808 | 123.1674 | 61.5403 | 122.9593 | 61.5667 | 61.6072 | 61.4934 | 61.5339
2704.0938 | 123.3444 | -61.5189 | 61.5555 | 0.48812 | 0.6463 | 0.94951 | 0.74417 | 0.88319 | 0.67619 | 0.5004 | 61.592 | 0.2349 | 61.5233 | -0.033101 | 0.025345 | 61.6257 | -0.001436 | 61.4222 | 62.007 | 62.1652 | 62.4684 | 62.263 | 62.402 | 62.1951 | 62.0193 | 123.1109 | 61.7538 | 123.0422 | 61.4858 | 61.5442 | 123.1445 | 61.5174 | 122.941 | 61.5667 | 61.5935 | 61.4979 | 61.5247
2705.0625 | 123.3627 | -61.5417 | 61.5234 | 0.50186 | 0.66462 | 0.98156 | 0.76248 | 0.88777 | 0.70824 | 0.51413 | 61.6012 | 0.22574 | 61.5096 | -0.042259 | 0.039079 | 61.6257 | -0.001436 | 61.4176 | 62.0436 | 62.2064 | 62.5233 | 62.3042 | 62.4295 | 62.25 | 62.0559 | 123.1429 | 61.7675 | 123.0513 | 61.4995 | 61.5808 | 123.1674 | 61.5403 | 122.9593 | 61.5621 | 61.6026 | 61.4705 | 61.511
2706.0781 | 123.3124 | -61.5143 | 61.6333 | 0.4927 | 0.66462 | 0.98156 | 0.79453 | 0.91981 | 0.73571 | 0.51413 | 61.5966 | 0.22574 | 61.5004 | -0.03768 | 0.034501 | 61.6257 | -0.001436 | 61.4222 | 62.007 | 62.1789 | 62.4958 | 62.3088 | 62.4341 | 62.25 | 62.0284 | 123.1109 | 61.74 | 123.0147 | 61.4766 | 61.5488 | 123.14 | 61.5128 | 122.9365 | 61.5621 | 61.5981 | 61.4659 | 61.5018
2707.0625 | 123.2895 | -61.5326 | 61.6013 | 0.46065 | 0.60509 | 0.92204 | 0.75791 | 0.86945 | 0.68993 | 0.46835 | 61.6058 | 0.2349 | 61.505 | -0.03768 | 0.034501 | 61.6211 | 0.003143 | 61.4084 | 61.9932 | 62.1377 | 62.4546 | 62.2905 | 62.402 | 62.2225 | 62.0009 | 123.1384 | 61.7675 | 123.0376 | 61.4949 | 61.5671 | 123.1537 | 61.5357 | 122.941 | 61.5713 | 61.6026 | 61.4705 | 61.5018
2708.0625 | 123.2803 | -61.5463 | 61.5967 | 0.48812 | 0.64172 | 0.97698 | 0.78538 | 0.9015 | 0.7174 | 0.50955 | 61.6012 | 0.2349 | 61.5233 | -0.042259 | 0.034501 | 61.6257 | -0.001436 | 61.4222 | 62.0344 | 62.188 | 62.5233 | 62.3317 | 62.4478 | 62.2637 | 62.0559 | 123.1475 | 61.7812 | 123.0696 | 61.5041 | 61.5808 | 123.172 | 61.5449 | 122.9685 | 61.5667 | 61.6026 | 61.4888 | 61.5247
2709.0938 | 123.2712 | -61.5372 | 61.5967 | 0.47896 | 0.6463 | 0.94493 | 0.76248 | 0.88319 | 0.65788 | 0.49124 | 61.6058 | 0.23032 | 61.537 | -0.042259 | 0.039079 | 61.6348 | -0.006014 | 61.4176 | 62.0161 | 62.1835 | 62.4821 | 62.2997 | 62.4204 | 62.1951 | 62.0284 | 123.1429 | 61.7675 | 123.0742 | 61.4949 | 61.5762 | 123.172 | 61.5312 | 122.9548 | 61.5667 | 61.6118 | 61.4979 | 61.543
2710.0625 | 123.3902 | -61.5509 | 61.5509 | 0.50644 | 0.65088 | 0.98614 | 0.7808 | 0.91065 | 0.68535 | 0.51413 | 61.6104 | 0.23032 | 61.5324 | -0.033101 | 0.034501 | 61.6348 | -0.006014 | 61.4222 | 62.0573 | 62.2018 | 62.537 | 62.3317 | 62.4616 | 62.2363 | 62.065 | 123.1613 | 61.7812 | 123.0834 | 61.5178 | 61.5854 | 123.1857 | 61.5449 | 122.9731 | 61.5759 | 61.6164 | 61.4979 | 61.5385
2711.0938 | 123.2986 | -61.5417 | 61.6287 | 0.52017 | 0.68751 | 1.0319 | 0.81285 | 0.92897 | 0.72656 | 0.53244 | 61.6058 | 0.22574 | 61.5416 | -0.03768 | 0.039079 | 61.6303 | -0.006014 | 61.4268 | 62.0619 | 62.2293 | 62.5737 | 62.3546 | 62.4707 | 62.2683 | 62.0742 | 123.1475 | 61.7675 | 123.0834 | 61.5041 | 61.5808 | 123.172 | 61.5357 | 122.9685 | 61.5667 | 61.6118 | 61.5025 | 61.5476
2712.0625 | 123.262 | -61.5463 | 61.6104 | 0.50186 | 0.65088 | 0.97698 | 0.79453 | 0.91065 | 0.69451 | 0.52329 | 61.6104 | 0.2349 | 61.537 | -0.028522 | 0.039079 | 61.6303 | 0.003143 | 61.4222 | 62.0482 | 62.1972 | 62.5233 | 62.3409 | 62.457 | 62.2408 | 62.0696 | 123.1567 | 61.7812 | 123.0834 | 61.5178 | 61.5854 | 123.1766 | 61.5495 | 122.9685 | 61.5713 | 61.6072 | 61.4979 | 61.5339
2713.0625 | 123.2895 | -61.5372 | 61.615 | 0.51101 | 0.65546 | 0.92661 | 0.81743 | 0.91981 | 0.72198 | 0.52329 | 61.6058 | 0.2349 | 61.5324 | -0.03768 | 0.039079 | 61.6211 | -0.010593 | 61.4176 | 62.0482 | 62.1926 | 62.4638 | 62.3546 | 62.457 | 62.2591 | 62.0605 | 123.1429 | 61.7721 | 123.0696 | 61.4995 | 61.5762 | 123.1583 | 61.5266 | 122.9548 | 61.5667 | 61.6164 | 61.4934 | 61.543
2714.0625 | 123.2849 | -61.5189 | 61.6196 | 0.52933 | 0.67378 | 0.95866 | 0.83574 | 0.96101 | 0.74487 | 0.54618 | 61.5966 | 0.23948 | 61.537 | -0.03768 | 0.039079 | 61.6348 | 0.003143 | 61.4176 | 62.0482 | 62.1926 | 62.4775 | 62.3546 | 62.4799 | 62.2637 | 62.065 | 123.1155 | 61.7583 | 123.0559 | 61.4812 | 61.5579 | 123.1537 | 61.522 | 122.9365 | 61.5575 | 61.5935 | 61.4979 | 61.5339
2715.0625 | 123.3627 | -61.528 | 61.5784 | 0.53848 | 0.7104 | 1.0182 | 0.84948 | 0.99764 | 0.79981 | 0.56449 | 61.6012 | 0.23032 | 61.5233 | -0.042259 | 0.034501 | 61.6165 | -0.010593 | 61.4268 | 62.0665 | 62.2384 | 62.5462 | 62.3775 | 62.5257 | 62.3278 | 62.0925 | 123.1292 | 61.7583 | 123.0513 | 61.4858 | 61.5625 | 123.1445 | 61.5174 | 122.9548 | 61.5667 | 61.6118 | 61.4888 | 61.5339
2716.0625 | 123.3627 | -61.528 | 61.6058 | 0.53391 | 0.7104 | 1.0182 | 0.84948 | 1.0343 | 0.81812 | 0.55534 | 61.6058 | 0.23032 | 61.5416 | -0.042259 | 0.039079 | 61.6257 | 0.003143 | 61.4313 | 62.0619 | 62.2384 | 62.5462 | 62.3775 | 62.5623 | 62.3461 | 62.0834 | 123.1338 | 61.7583 | 123.0696 | 61.4858 | 61.5671 | 123.1537 | 61.5312 | 122.9594 | 61.5667 | 61.6026 | 61.5025 | 61.5385
2717.0625 | 123.2986 | -61.5189 | 61.615 | 0.5568 | 0.73788 | 1.0502 | 0.89068 | 1.0938 | 0.86391 | 0.57823 | 61.6012 | 0.23948 | 61.5416 | -0.028522 | 0.039079 | 61.6394 | -0.001436 | 61.4268 | 62.0757 | 62.2567 | 62.5691 | 62.4095 | 62.6126 | 62.3828 | 62.0971 | 123.1201 | 61.7583 | 123.0605 | 61.4903 | 61.5579 | 123.1583 | 61.5174 | 122.9456 | 61.5621 | 61.6026 | 61.5025 | 61.543
2718.0781 | 123.2574 | -61.5417 | 61.6333 | 0.56595 | 0.71956 | 1.0411 | 0.89068 | 1.0892 | 0.88222 | 0.56907 | 61.592 | 0.2349 | 61.5233 | -0.042259 | 0.039079 | 61.6303 | -0.001436 | 61.4313 | 62.1077 | 62.2613 | 62.5828 | 62.4324 | 62.6309 | 62.424 | 62.1108 | 123.1338 | 61.7766 | 123.065 | 61.4995 | 61.5808 | 123.172 | 61.5403 | 122.9731 | 61.553 | 61.5935 | 61.4842 | 61.5247
2719.0625 | 123.3261 | -61.5234 | 61.6196 | 0.57053 | 0.73788 | 1.0914 | 0.89526 | 1.1212 | 0.8868 | 0.58281 | 61.5966 | 0.23032 | 61.505 | -0.03768 | 0.034501 | 61.6348 | -0.001436 | 61.4268 | 62.094 | 62.2613 | 62.6149 | 62.4187 | 62.6447 | 62.4102 | 62.1062 | 123.1201 | 61.7538 | 123.0284 | 61.4858 | 61.5579 | 123.1583 | 61.522 | 122.9502 | 61.5621 | 61.5981 | 61.4705 | 61.5064
2720.0938 | 123.3261 | -61.5417 | 61.5738 | 0.56595 | 0.73788 | 1.0731 | 0.89068 | 1.1396 | 0.89596 | 0.58281 | 61.5966 | 0.2349 | 61.4958 | -0.03768 | 0.034501 | 61.6303 | -0.001436 | 61.4268 | 62.1077 | 62.2796 | 62.6149 | 62.4324 | 62.6813 | 62.4377 | 62.1246 | 123.1384 | 61.7766 | 123.0376 | 61.5041 | 61.5762 | 123.172 | 61.5403 | 122.9685 | 61.5621 | 61.5981 | 61.4613 | 61.4973
2721.0625 | 123.2849 | -61.5234 | 61.6196 | 0.58427 | 0.71498 | 1.1006 | 0.909 | 1.1396 | 0.92343 | 0.60112 | 61.592 | 0.23948 | 61.505 | -0.033101 | 0.039079 | 61.6348 | 0.003143 | 61.4268 | 62.1077 | 62.2384 | 62.624 | 62.4324 | 62.663 | 62.4469 | 62.1246 | 123.1155 | 61.7629 | 123.0284 | 61.4903 | 61.5625 | 123.1583 | 61.5266 | 122.9502 | 61.553 | 61.5889 | 61.4659 | 61.5018
2722.0625 | 123.317 | -61.5326 | 61.6196 | 0.60258 | 0.72872 | 1.1098 | 0.91358 | 1.1212 | 0.95548 | 0.62401 | 61.592 | 0.2349 | 61.505 | -0.042259 | 0.039079 | 61.6348 | -0.001436 | 61.4313 | 62.1352 | 62.2613 | 62.6424 | 62.4462 | 62.6538 | 62.4881 | 62.1566 | 123.1246 | 61.7675 | 123.0376 | 61.4903 | 61.5717 | 123.1674 | 61.5312 | 122.9639 | 61.553 | 61.5935 | 61.4659 | 61.5064
2723.0625 | 123.3078 | -61.5417 | 61.6425 | 0.62089 | 0.76077 | 1.0731 | 0.93647 | 1.1212 | 1.0058 | 0.64232 | 61.6012 | 0.23948 | 61.5279 | -0.03768 | 0.034501 | 61.6394 | -0.001436 | 61.4405 | 62.1626 | 62.3025 | 62.6149 | 62.4782 | 62.663 | 62.5476 | 62.1841 | 123.1429 | 61.7812 | 123.0696 | 61.5041 | 61.5762 | 123.1812 | 61.5403 | 122.9822 | 61.5667 | 61.6026 | 61.4934 | 61.5293
2724.0625 | 123.2574 | -61.5784 | 61.6241 | 0.63921 | 0.78367 | 1.1189 | 0.91358 | 1.1212 | 1.0013 | 0.65606 | 61.6012 | 0.23032 | 61.5279 | -0.03768 | 0.039079 | 61.644 | -0.006014 | 61.4359 | 62.2176 | 62.362 | 62.6973 | 62.4919 | 62.6996 | 62.5796 | 62.2344 | 123.1796 | 61.8087 | 123.1062 | 61.5407 | 61.6174 | 123.2224 | 61.5724 | 123.0143 | 61.5621 | 61.6072 | 61.4888 | 61.5339
2725.1094 | 123.4039 | -61.5051 | 61.5967 | 0.63921 | 0.80198 | 1.1052 | 0.89984 | 1.1716 | 0.96005 | 0.65606 | 61.6012 | 0.23948 | 61.5324 | -0.03768 | 0.034501 | 61.644 | -0.001436 | 61.4313 | 62.1443 | 62.3071 | 62.6103 | 62.405 | 62.6767 | 62.4652 | 62.1612 | 123.1063 | 61.7446 | 123.0376 | 61.4674 | 61.5396 | 123.1491 | 61.5037 | 122.9365 | 61.5667 | 61.6026 | 61.4979 | 61.5339
2726.0625 | 123.2758 | -61.5463 | 61.6287 | 0.63921 | 0.8203 | 1.0686 | 0.90442 | 1.2036 | 0.99668 | 0.66063 | 61.5966 | 0.23948 | 61.5279 | -0.03768 | 0.039079 | 61.644 | -0.001436 | 61.4405 | 62.1855 | 62.3666 | 62.6149 | 62.4507 | 62.75 | 62.543 | 62.207 | 123.1429 | 61.7858 | 123.0742 | 61.5086 | 61.5854 | 123.1903 | 61.5449 | 122.9868 | 61.5575 | 61.5981 | 61.4888 | 61.5293
2727.0781 | 123.3582 | -61.5143 | 61.5967 | 0.64837 | 0.80656 | 1.0823 | 0.89984 | 1.222 | 0.97837 | 0.66063 | 61.5875 | 0.23948 | 61.5187 | -0.042259 | 0.039079 | 61.6348 | 0.003143 | 61.4405 | 62.1626 | 62.3208 | 62.5966 | 62.4141 | 62.7362 | 62.4927 | 62.1749 | 123.1017 | 61.7538 | 123.033 | 61.472 | 61.5534 | 123.1491 | 61.5174 | 122.9548 | 61.5484 | 61.5843 | 61.4796 | 61.5156
2728.0625 | 123.2803 | -61.5555 | 61.6333 | 0.66668 | 0.81114 | 1.1098 | 0.91358 | 1.2311 | 0.99668 | 0.68353 | 61.5875 | 0.2349 | 61.505 | -0.042259 | 0.034501 | 61.6394 | -0.001436 | 61.4451 | 62.2222 | 62.3666 | 62.6652 | 62.4691 | 62.7866 | 62.5522 | 62.239 | 123.1429 | 61.7904 | 123.0605 | 61.5132 | 61.59 | 123.1949 | 61.554 | 123.0006 | 61.553 | 61.5889 | 61.4705 | 61.5064
2729.0938 | 123.3765 | -61.5417 | 61.5738 | 0.64837 | 0.83861 | 1.1235 | 0.94105 | 1.2265 | 1.0104 | 0.66063 | 61.592 | 0.2349 | 61.4867 | -0.033101 | 0.029923 | 61.6394 | -0.001436 | 61.4405 | 62.1901 | 62.3804 | 62.6652 | 62.4828 | 62.7683 | 62.5522 | 62.2024 | 123.1338 | 61.7766 | 123.0284 | 61.5086 | 61.5717 | 123.1812 | 61.5403 | 122.9822 | 61.5621 | 61.5935 | 61.4567 | 61.4881
2730.0625 | 123.3124 | -61.5372 | 61.6379 | 0.67126 | 0.85235 | 1.1968 | 0.97767 | 1.2448 | 1.0379 | 0.67895 | 61.5829 | 0.23032 | 61.4912 | -0.033101 | 0.039079 | 61.644 | -0.001436 | 61.4359 | 62.2084 | 62.3895 | 62.7339 | 62.5148 | 62.782 | 62.5751 | 62.2161 | 123.1201 | 61.7675 | 123.0284 | 61.5041 | 61.5762 | 123.1812 | 61.5357 | 122.9731 | 61.5438 | 61.5843 | 61.4522 | 61.4927
2731.0781 | 123.3673 | -61.5372 | 61.5829 | 0.63921 | 0.83861 | 1.151 | 0.95478 | 1.2311 | 1.0013 | 0.65606 | 61.5875 | 0.24405 | 61.4912 | -0.03768 | 0.034501 | 61.6394 | -0.001436 | 61.4222 | 62.1764 | 62.3758 | 62.6881 | 62.492 | 62.7683 | 62.5384 | 62.1932 | 123.1246 | 61.7812 | 123.0284 | 61.4995 | 61.5717 | 123.1766 | 61.5357 | 122.9593 | 61.553 | 61.5889 | 61.4567 | 61.4927
2732.0625 | 123.3261 | -61.5372 | 61.615 | 0.68957 | 0.89814 | 1.1693 | 0.96852 | 1.2494 | 1.0333 | 0.70184 | 61.5875 | 0.2349 | 61.5141 | -0.03768 | 0.039079 | 61.6348 | 0.003143 | 61.4405 | 62.2267 | 62.4353 | 62.7065 | 62.5057 | 62.7866 | 62.5705 | 62.239 | 123.1246 | 61.7721 | 123.0513 | 61.4995 | 61.5762 | 123.172 | 61.5403 | 122.9777 | 61.5484 | 61.5843 | 61.4751 | 61.511
2733.0625 | 123.3536 | -61.5509 | 61.5921 | 0.70788 | 0.87524 | 1.1784 | 0.96394 | 1.222 | 1.0379 | 0.72473 | 61.5875 | 0.2349 | 61.5233 | -0.033101 | 0.034501 | 61.644 | 0.003143 | 61.4451 | 62.2588 | 62.4261 | 62.7293 | 62.5148 | 62.7729 | 62.5888 | 62.2756 | 123.1384 | 61.7858 | 123.0742 | 61.5178 | 61.5854 | 123.1949 | 61.554 | 122.996 | 61.553 | 61.5843 | 61.4888 | 61.5202
2734.0625 | 123.381 | -61.5234 | 61.5921 | 0.72162 | 0.86608 | 1.1281 | 0.96852 | 1.1899 | 1.0379 | 0.73389 | 61.592 | 0.23948 | 61.5233 | -0.03768 | 0.034501 | 61.6531 | 0.007721 | 61.4542 | 62.2451 | 62.3895 | 62.6515 | 62.492 | 62.7133 | 62.5613 | 62.2573 | 123.1155 | 61.7629 | 123.0467 | 61.4858 | 61.5579 | 123.1766 | 61.5312 | 122.9777 | 61.5575 | 61.5843 | 61.4888 | 61.5156
2735.0625 | 123.3353 | -61.5417 | 61.6104 | 0.73993 | 0.87066 | 1.1327 | 0.96394 | 1.1762 | 1.0013 | 0.7522 | 61.5966 | 0.2349 | 61.5279 | -0.028522 | 0.034501 | 61.6394 | -0.006014 | 61.4359 | 62.2817 | 62.4124 | 62.6744 | 62.5057 | 62.7179 | 62.543 | 62.2939 | 123.1384 | 61.7766 | 123.0696 | 61.5132 | 61.5762 | 123.1812 | 61.5357 | 122.9777 | 61.5621 | 61.6026 | 61.4934 | 61.5339
2736.0781 | 123.3902 | -61.5372 | 61.5601 | 0.73078 | 0.83861 | 1.1418 | 0.93189 | 1.1579 | 0.97379 | 0.74304 | 61.592 | 0.2349 | 61.5279 | -0.033101 | 0.039079 | 61.6394 | -0.010593 | 61.4313 | 62.2679 | 62.3758 | 62.679 | 62.4691 | 62.695 | 62.511 | 62.2802 | 123.1292 | 61.7721 | 123.065 | 61.5041 | 61.5762 | 123.1766 | 61.5266 | 122.9685 | 61.553 | 61.6026 | 61.4888 | 61.5385
2737.0625 | 123.4406 | -61.4914 | 61.6516 | 0.71704 | 0.82488 | 1.1052 | 0.92273 | 1.1624 | 0.9509 | 0.72015 | 61.5966 | 0.23032 | 61.5004 | -0.033101 | 0.039079 | 61.644 | -0.001436 | 61.4359 | 62.2084 | 62.3163 | 62.5966 | 62.4141 | 62.6538 | 62.4423 | 62.2115 | 123.088 | 61.7217 | 122.9918 | 61.4583 | 61.5305 | 123.1354 | 61.49 | 122.9273 | 61.5575 | 61.5981 | 61.4613 | 61.5018
2738.0938 | 123.3536 | -61.5189 | 61.6104 | 0.70788 | 0.83403 | 1.0869 | 0.94562 | 1.1762 | 0.96005 | 0.72931 | 61.5829 | 0.2349 | 61.4821 | -0.033101 | 0.034501 | 61.6394 | -0.001436 | 61.4268 | 62.2267 | 62.3529 | 62.6057 | 62.4645 | 62.695 | 62.4789 | 62.2482 | 123.1017 | 61.7538 | 123.0009 | 61.4858 | 61.5534 | 123.1583 | 61.5174 | 122.9456 | 61.5484 | 61.5843 | 61.4476 | 61.4835
2739.1719 | 123.3582 | -61.5417 | 61.5738 | 0.72162 | 0.8203 | 1.0686 | 0.93647 | 1.1716 | 0.96921 | 0.73389 | 61.5829 | 0.2349 | 61.4912 | -0.03768 | 0.043657 | 61.6348 | -0.001436 | 61.4268 | 62.2634 | 62.362 | 62.6103 | 62.4782 | 62.7133 | 62.511 | 62.2756 | 123.1246 | 61.7766 | 123.033 | 61.5041 | 61.5854 | 123.1766 | 61.5403 | 122.9685 | 61.5392 | 61.5843 | 61.4476 | 61.4927
2740.0625 | 123.2986 | -61.5555 | 61.6241 | 0.73078 | 0.85235 | 1.0823 | 0.94105 | 1.1762 | 0.9921 | 0.74304 | 61.5875 | 0.23032 | 61.505 | -0.033101 | 0.039079 | 61.6394 | -0.001436 | 61.4359 | 62.2863 | 62.4078 | 62.6378 | 62.4965 | 62.7317 | 62.5476 | 62.2985 | 123.1429 | 61.7858 | 123.0605 | 61.5224 | 61.5946 | 123.1949 | 61.554 | 122.9914 | 61.5484 | 61.5889 | 61.4659 | 61.5064
2741.0625 | 123.4406 | -61.5005 | 61.6058 | 0.75367 | 0.87524 | 1.096 | 0.98225 | 1.2036 | 1.0379 | 0.77967 | 61.592 | 0.2349 | 61.5004 | -0.042259 | 0.034501 | 61.644 | 0.003143 | 61.4313 | 62.2542 | 62.3758 | 62.5966 | 62.4828 | 62.7042 | 62.5384 | 62.2802 | 123.0926 | 61.7354 | 123.0009 | 61.4583 | 61.535 | 123.1445 | 61.5037 | 122.9319 | 61.5575 | 61.5889 | 61.4659 | 61.4973
2742.0625 | 123.3994 | -61.5189 | 61.5875 | 0.78572 | 0.91187 | 1.1189 | 1.0097 | 1.2357 | 1.0654 | 0.7934 | 61.5875 | 0.23032 | 61.5096 | -0.033101 | 0.043657 | 61.6486 | 0.007721 | 61.4405 | 62.3046 | 62.4307 | 62.6378 | 62.5286 | 62.7545 | 62.5842 | 62.3123 | 123.1063 | 61.7492 | 123.0284 | 61.4858 | 61.5625 | 123.1674 | 61.5266 | 122.9594 | 61.5438 | 61.5797 | 61.4659 | 61.5018
2743.0625 | 123.4497 | -61.496 | 61.6104 | 0.77656 | 0.92103 | 1.1464 | 1.0235 | 1.254 | 1.1111 | 0.78882 | 61.5829 | 0.23948 | 61.5187 | -0.042259 | 0.034501 | 61.6486 | 0.007721 | 61.4405 | 62.2725 | 62.417 | 62.6424 | 62.5194 | 62.75 | 62.6071 | 62.2848 | 123.0789 | 61.7354 | 123.0147 | 61.4537 | 61.5305 | 123.1445 | 61.5037 | 122.9365 | 61.5484 | 61.5752 | 61.4842 | 61.511
2744.0625 | 123.381 | -61.528 | 61.5738 | 0.75825 | 0.89814 | 1.0914 | 1.0097 | 1.2494 | 1.0928 | 0.77967 | 61.5875 | 0.23032 | 61.5187 | -0.042259 | 0.039079 | 61.6531 | -0.001436 | 61.4451 | 62.2863 | 62.4262 | 62.6195 | 62.5377 | 62.7774 | 62.6208 | 62.3077 | 123.1155 | 61.7583 | 123.0467 | 61.4858 | 61.5671 | 123.1812 | 61.5266 | 122.9731 | 61.5484 | 61.5889 | 61.4796 | 61.5202
2745.0625 | 123.2712 | -61.5234 | 61.6425 | 0.73078 | 0.87066 | 1.0731 | 0.96394 | 1.2036 | 1.0425 | 0.74304 | 61.592 | 0.2349 | 61.5233 | -0.033101 | 0.039079 | 61.6394 | 0.007721 | 61.4496 | 62.2542 | 62.3941 | 62.5966 | 62.4874 | 62.7271 | 62.5659 | 62.2665 | 123.1155 | 61.7583 | 123.0467 | 61.4903 | 61.5625 | 123.1628 | 61.5312 | 122.9731 | 61.553 | 61.5843 | 61.4842 | 61.5156
2746.0625 | 123.4131 | -61.5051 | 61.5692 | 0.74909 | 0.87524 | 1.096 | 0.95478 | 1.2174 | 1.0654 | 0.76135 | 61.5875 | 0.2349 | 61.5096 | -0.033101 | 0.029923 | 61.6394 | -0.001436 | 61.4359 | 62.2542 | 62.3804 | 62.6011 | 62.4599 | 62.7225 | 62.5705 | 62.2665 | 123.0926 | 61.74 | 123.0147 | 61.472 | 61.535 | 123.1445 | 61.5037 | 122.941 | 61.5575 | 61.5889 | 61.4796 | 61.511
2747.0625 | 123.3765 | -61.5509 | 61.5784 | 0.75367 | 0.87066 | 1.1098 | 0.95936 | 1.2128 | 1.0608 | 0.77509 | 61.5875 | 0.23948 | 61.4912 | -0.033101 | 0.034501 | 61.644 | -0.001436 | 61.4313 | 62.3046 | 62.4216 | 62.6607 | 62.5103 | 62.7637 | 62.6117 | 62.326 | 123.1384 | 61.7904 | 123.0421 | 61.5178 | 61.5854 | 123.1949 | 61.5495 | 122.9822 | 61.553 | 61.5889 | 61.4567 | 61.4927
2748.0938 | 123.3627 | -61.528 | 61.5692 | 0.7674 | 0.87524 | 1.1464 | 0.97767 | 1.2632 | 1.0745 | 0.78424 | 61.5829 | 0.23032 | 61.4821 | -0.03768 | 0.029923 | 61.644 | 0.003143 | 61.4313 | 62.2954 | 62.4033 | 62.6744 | 62.5057 | 62.7912 | 62.6025 | 62.3123 | 123.1109 | 61.7583 | 123.0101 | 61.4903 | 61.5579 | 123.172 | 61.5312 | 122.9594 | 61.553 | 61.5797 | 61.4522 | 61.4789
2749.0625 | 123.3582 | -61.5463 | 61.5784 | 0.77198 | 0.87066 | 1.1418 | 0.9731 | 1.2357 | 1.0791 | 0.7934 | 61.5829 | 0.2349 | 61.4867 | -0.046838 | 0.039079 | 61.6486 | -0.006014 | 61.4313 | 62.3183 | 62.417 | 62.6881 | 62.5194 | 62.782 | 62.6254 | 62.3397 | 123.1292 | 61.7812 | 123.033 | 61.4995 | 61.5854 | 123.1949 | 61.5403 | 122.9777 | 61.5438 | 61.5889 | 61.4476 | 61.4927
2750.0625 | 123.3078 | -61.5555 | 61.6516 | 0.77656 | 0.87066 | 1.1327 | 0.9731 | 1.2128 | 1.0928 | 0.78424 | 61.5875 | 0.2349 | 61.5096 | -0.03768 | 0.039079 | 61.6486 | -0.001436 | 61.4451 | 62.332 | 62.4261 | 62.6881 | 62.5286 | 62.7683 | 62.6483 | 62.3397 | 123.1429 | 61.7904 | 123.065 | 61.5178 | 61.5946 | 123.204 | 61.554 | 123.0006 | 61.5484 | 61.5889 | 61.4705 | 61.511
2751.0625 | 123.3215 | -61.5555 | 61.5646 | 0.80403 | 0.91187 | 1.183 | 1.0006 | 1.254 | 1.1203 | 0.82545 | 61.5829 | 0.24405 | 61.5141 | -0.028522 | 0.029923 | 61.6486 | -0.001436 | 61.4405 | 62.3595 | 62.4674 | 62.7385 | 62.556 | 62.8095 | 62.6758 | 62.3809 | 123.1384 | 61.7995 | 123.0696 | 61.527 | 61.5854 | 123.204 | 61.554 | 122.996 | 61.553 | 61.5843 | 61.4842 | 61.5156
2752.0938 | 123.2849 | -61.5784 | 61.6058 | 0.78114 | 0.89356 | 1.1235 | 0.95936 | 1.2128 | 1.0974 | 0.78882 | 61.5966 | 0.2349 | 61.5141 | -0.042259 | 0.025345 | 61.644 | -0.001436 | 61.4405 | 62.3595 | 62.4719 | 62.7019 | 62.5377 | 62.7912 | 62.6758 | 62.3672 | 123.175 | 61.8133 | 123.0925 | 61.5361 | 61.6037 | 123.2224 | 61.5769 | 123.0189 | 61.5713 | 61.5981 | 61.4888 | 61.5156
2753.0625 | 123.3627 | -61.5326 | 61.5875 | 0.75825 | 0.89814 | 1.1327 | 0.95936 | 1.1945 | 1.0928 | 0.77967 | 61.5875 | 0.23032 | 61.5233 | -0.03768 | 0.039079 | 61.644 | 0.007721 | 61.4359 | 62.2908 | 62.4307 | 62.6652 | 62.492 | 62.7271 | 62.6254 | 62.3123 | 123.1201 | 61.7629 | 123.0559 | 61.4949 | 61.5717 | 123.1766 | 61.5403 | 122.9685 | 61.5484 | 61.5797 | 61.4842 | 61.5156
2754.0625 | 123.3719 | -61.5234 | 61.5692 | 0.74451 | 0.86151 | 1.0869 | 0.92273 | 1.1487 | 1.047 | 0.75678 | 61.592 | 0.2349 | 61.5187 | -0.03768 | 0.029923 | 61.6394 | -0.006014 | 61.4313 | 62.2679 | 62.3849 | 62.6103 | 62.4462 | 62.6721 | 62.5705 | 62.2802 | 123.1155 | 61.7583 | 123.0422 | 61.4858 | 61.5534 | 123.1628 | 61.5174 | 122.9548 | 61.5621 | 61.5981 | 61.4888 | 61.5247
2755.0938 | 123.2346 | -61.5692 | 61.5875 | 0.7674 | 0.84777 | 1.1372 | 0.92731 | 1.1441 | 1.0654 | 0.7934 | 61.592 | 0.23032 | 61.5096 | -0.03768 | 0.029923 | 61.6394 | 0.003143 | 61.4359 | 62.3366 | 62.417 | 62.7064 | 62.4965 | 62.7133 | 62.6346 | 62.3626 | 123.1613 | 61.7995 | 123.0788 | 61.5315 | 61.5991 | 123.2086 | 61.5724 | 123.0051 | 61.5621 | 61.5889 | 61.4796 | 61.5064
2756.0625 | 123.3307 | -61.5372 | 61.5646 | 0.76282 | 0.83861 | 1.1281 | 0.89984 | 1.1853 | 1.0242 | 0.78424 | 61.5829 | 0.2349 | 61.4958 | -0.033101 | 0.039079 | 61.6486 | 0.003143 | 61.4359 | 62.3 | 62.3758 | 62.6652 | 62.437 | 62.7225 | 62.5613 | 62.3214 | 123.1201 | 61.7721 | 123.033 | 61.5041 | 61.5762 | 123.1857 | 61.5403 | 122.9731 | 61.5438 | 61.5797 | 61.4567 | 61.4927
2757.0625 | 123.4039 | -61.5372 | 61.5967 | 0.73535 | 0.80198 | 1.0686 | 0.84948 | 1.167 | 0.97379 | 0.7522 | 61.5875 | 0.2349 | 61.4912 | -0.028522 | 0.034501 | 61.6348 | -0.001436 | 61.4268 | 62.2725 | 62.3392 | 62.6057 | 62.3866 | 62.7042 | 62.511 | 62.2894 | 123.1246 | 61.7721 | 123.0284 | 61.5086 | 61.5717 | 123.172 | 61.5357 | 122.9639 | 61.553 | 61.5889 | 61.4567 | 61.4927
2758.0625 | 123.3536 | -61.5234 | 61.528 | 0.7262 | 0.77451 | 1.064 | 0.83574 | 1.1579 | 0.9509 | 0.74762 | 61.592 | 0.23948 | 61.4912 | -0.03768 | 0.034501 | 61.6394 | -0.001436 | 61.4313 | 62.2496 | 62.2979 | 62.5874 | 62.3592 | 62.6813 | 62.4743 | 62.2711 | 123.1155 | 61.7629 | 123.0147 | 61.4858 | 61.5579 | 123.1628 | 61.522 | 122.9548 | 61.5575 | 61.5935 | 61.4567 | 61.4927
2759.0625 | 123.3673 | -61.5097 | 61.5784 | 0.71246 | 0.72872 | 0.99529 | 0.79453 | 1.135 | 0.91885 | 0.72015 | 61.592 | 0.2349 | 61.505 | -0.042259 | 0.029923 | 61.644 | -0.006014 | 61.4268 | 62.2222 | 62.2384 | 62.505 | 62.3042 | 62.6447 | 62.4286 | 62.2299 | 123.1017 | 61.7446 | 123.0147 | 61.4674 | 61.5396 | 123.1537 | 61.5037 | 122.9365 | 61.5621 | 61.5981 | 61.4751 | 61.511
2760.0625 | 123.3032 | -61.5189 | 61.615 | 0.70788 | 0.71956 | 0.9724 | 0.79453 | 1.1212 | 0.91885 | 0.72473 | 61.6104 | 0.24405 | 61.5279 | -0.03768 | 0.039079 | 61.6348 | 0.003143 | 61.4359 | 62.2267 | 62.2384 | 62.4913 | 62.3134 | 62.6401 | 62.4377 | 62.2436 | 123.1292 | 61.7629 | 123.0467 | 61.4812 | 61.5579 | 123.1537 | 61.522 | 122.9548 | 61.5713 | 61.6072 | 61.4888 | 61.5247
2761.0781 | 123.3261 | -61.528 | 61.6058 | 0.73535 | 0.74246 | 0.96324 | 0.81285 | 1.1533 | 0.93716 | 0.74304 | 61.5966 | 0.2349 | 61.5187 | -0.033101 | 0.034501 | 61.6394 | -0.006014 | 61.4313 | 62.2634 | 62.2705 | 62.4913 | 62.3409 | 62.6813 | 62.4652 | 62.2711 | 123.1246 | 61.7629 | 123.0467 | 61.4949 | 61.5625 | 123.1674 | 61.522 | 122.9594 | 61.5621 | 61.6026 | 61.4842 | 61.5247
2762.0625 | 123.3582 | -61.5509 | 61.5601 | 0.73535 | 0.74246 | 0.93577 | 0.80827 | 1.1533 | 0.94632 | 0.74762 | 61.5875 | 0.2349 | 61.5187 | -0.03768 | 0.039079 | 61.6394 | -0.001436 | 61.4268 | 62.2863 | 62.2934 | 62.4867 | 62.3592 | 62.7042 | 62.4972 | 62.2985 | 123.1384 | 61.7858 | 123.0696 | 61.5132 | 61.59 | 123.1903 | 61.5495 | 122.9777 | 61.5484 | 61.5889 | 61.4796 | 61.5202
2763.0625 | 123.3582 | -61.5326 | 61.5555 | 0.7262 | 0.72872 | 0.92661 | 0.78538 | 1.1167 | 0.93258 | 0.74762 | 61.592 | 0.23948 | 61.5279 | -0.03768 | 0.039079 | 61.6394 | 0.003143 | 61.4268 | 62.2588 | 62.2613 | 62.4592 | 62.318 | 62.6493 | 62.4652 | 62.2802 | 123.1246 | 61.7721 | 123.0605 | 61.4949 | 61.5717 | 123.172 | 61.5357 | 122.9594 | 61.553 | 61.5889 | 61.4888 | 61.5247
2764.0625 | 123.3536 | -61.528 | 61.5646 | 0.73535 | 0.7333 | 0.95866 | 0.77622 | 1.1167 | 0.91885 | 0.74762 | 61.592 | 0.2349 | 61.5187 | -0.033101 | 0.039079 | 61.6348 | -0.001436 | 61.4313 | 62.2634 | 62.2613 | 62.4867 | 62.3042 | 62.6447 | 62.4469 | 62.2756 | 123.1201 | 61.7629 | 123.0467 | 61.4949 | 61.5671 | 123.1628 | 61.5266 | 122.9594 | 61.553 | 61.5935 | 61.4796 | 61.5202
2765.0625 | 123.3078 | -61.5784 | 61.6196 | 0.7674 | 0.74246 | 0.9724 | 0.7808 | 1.1304 | 0.9509 | 0.78424 | 61.592 | 0.2349 | 61.5004 | -0.042259 | 0.039079 | 61.6394 | 0.007721 | 61.4176 | 62.3458 | 62.3208 | 62.5508 | 62.3592 | 62.7088 | 62.5293 | 62.3626 | 123.1704 | 61.8133 | 123.0788 | 61.5361 | 61.6174 | 123.2178 | 61.5861 | 122.996 | 61.553 | 61.5843 | 61.4613 | 61.4927
2766.0781 | 123.2712 | -61.5555 | 61.615 | 0.75367 | 0.70583 | 0.87625 | 0.73043 | 1.0938 | 0.91427 | 0.76135 | 61.592 | 0.2349 | 61.4912 | -0.042259 | 0.034501 | 61.6348 | -0.001436 | 61.4176 | 62.3092 | 62.2613 | 62.4317 | 62.2859 | 62.6493 | 62.4698 | 62.3168 | 123.1475 | 61.7904 | 123.0467 | 61.5132 | 61.59 | 123.1903 | 61.554 | 122.9731 | 61.5575 | 61.5935 | 61.4567 | 61.4927
2767.0625 | 123.3398 | -61.5372 | 61.5784 | 0.73993 | 0.70125 | 0.86251 | 0.69839 | 1.0846 | 0.88222 | 0.75678 | 61.592 | 0.2349 | 61.5141 | -0.03768 | 0.034501 | 61.6303 | -0.001436 | 61.4268 | 62.2771 | 62.2384 | 62.3997 | 62.2356 | 62.6218 | 62.4194 | 62.2939 | 123.1292 | 61.7721 | 123.0513 | 61.4995 | 61.5717 | 123.1674 | 61.5357 | 122.9639 | 61.5575 | 61.5935 | 61.4796 | 61.5156
2768.0781 | 123.262 | -61.5692 | 61.5829 | 0.75825 | 0.71956 | 0.88541 | 0.73043 | 1.0938 | 0.90511 | 0.77967 | 61.6012 | 0.2349 | 61.5324 | -0.03768 | 0.034501 | 61.6303 | 0.003143 | 61.4268 | 62.3275 | 62.2888 | 62.4546 | 62.2996 | 62.663 | 62.4743 | 62.3489 | 123.1704 | 61.8041 | 123.1017 | 61.5315 | 61.6037 | 123.1995 | 61.5724 | 122.996 | 61.5667 | 61.5981 | 61.4979 | 61.5293
2769.0625 | 123.3673 | -61.5189 | 61.5784 | 0.78572 | 0.7333 | 0.89914 | 0.73043 | 1.1029 | 0.91885 | 0.80256 | 61.592 | 0.2349 | 61.5279 | -0.03768 | 0.034501 | 61.6394 | -0.006014 | 61.4313 | 62.3046 | 62.2522 | 62.418 | 62.2493 | 62.6218 | 62.4377 | 62.3214 | 123.1109 | 61.7538 | 123.0467 | 61.4812 | 61.5534 | 123.1583 | 61.5128 | 122.9502 | 61.5575 | 61.5981 | 61.4934 | 61.5339
2770.0625 | 123.3902 | -61.528 | 61.5829 | 0.78572 | 0.7333 | 0.90372 | 0.7167 | 1.0617 | 0.89596 | 0.7934 | 61.5875 | 0.2349 | 61.5187 | -0.042259 | 0.029923 | 61.6394 | -0.001436 | 61.4313 | 62.3137 | 62.2613 | 62.4317 | 62.2447 | 62.5897 | 62.424 | 62.3214 | 123.1155 | 61.7629 | 123.0467 | 61.4858 | 61.5579 | 123.1674 | 61.5266 | 122.9594 | 61.5575 | 61.5889 | 61.4888 | 61.5202
2771.0625 | 123.3444 | -61.5372 | 61.5463 | 0.76282 | 0.7104 | 0.93577 | 0.7167 | 1.0297 | 0.88222 | 0.78424 | 61.6012 | 0.23948 | 61.4958 | -0.042259 | 0.039079 | 61.6348 | -0.001436 | 61.413 | 62.3 | 62.2476 | 62.4729 | 62.2539 | 62.5669 | 62.4194 | 62.3214 | 123.1384 | 61.7766 | 123.033 | 61.4949 | 61.5762 | 123.172 | 61.5357 | 122.9502 | 61.5621 | 61.6026 | 61.4567 | 61.4973
2772.0625 | 123.3719 | -61.5372 | 61.5463 | 0.73993 | 0.67835 | 0.9083 | 0.7167 | 1.0297 | 0.89138 | 0.76135 | 61.5966 | 0.2349 | 61.5279 | -0.042259 | 0.039079 | 61.6348 | -0.001436 | 61.4268 | 62.2771 | 62.2155 | 62.4455 | 62.2539 | 62.5669 | 62.4285 | 62.2985 | 123.1338 | 61.7721 | 123.065 | 61.4949 | 61.5762 | 123.172 | 61.5357 | 122.9639 | 61.5575 | 61.5981 | 61.4888 | 61.5293
2773.0625 | 123.4039 | -61.5143 | 61.5372 | 0.73078 | 0.66004 | 0.87167 | 0.70296 | 0.99306 | 0.89596 | 0.74762 | 61.6012 | 0.23032 | 61.5324 | -0.03768 | 0.025345 | 61.6348 | -0.001436 | 61.4268 | 62.2451 | 62.1743 | 62.386 | 62.2172 | 62.5073 | 62.4102 | 62.2619 | 123.1155 | 61.7446 | 123.0467 | 61.4766 | 61.5396 | 123.1491 | 61.5128 | 122.941 | 61.5759 | 61.6026 | 61.5071 | 61.5339
2774.0625 | 123.3536 | -61.5326 | 61.5417 | 0.75367 | 0.67378 | 0.86709 | 0.69381 | 0.96101 | 0.90054 | 0.77051 | 61.6012 | 0.2349 | 61.5324 | -0.03768 | 0.029923 | 61.6348 | -0.001436 | 61.4268 | 62.2863 | 62.2064 | 62.3997 | 62.2264 | 62.4936 | 62.4331 | 62.3031 | 123.1338 | 61.7675 | 123.065 | 61.4949 | 61.5625 | 123.1674 | 61.5312 | 122.9594 | 61.5713 | 61.6026 | 61.5025 | 61.5339
2775.0625 | 123.2574 | -61.5372 | 61.5784 | 0.77656 | 0.67835 | 0.86251 | 0.71212 | 0.96559 | 0.91885 | 0.7934 | 61.5966 | 0.23948 | 61.537 | -0.042259 | 0.034501 | 61.6303 | -0.001436 | 61.4268 | 62.3137 | 62.2155 | 62.3997 | 62.2493 | 62.5028 | 62.456 | 62.3306 | 123.1338 | 61.7766 | 123.0742 | 61.4949 | 61.5717 | 123.1674 | 61.5357 | 122.9639 | 61.5621 | 61.5981 | 61.5025 | 61.5385
2776.0625 | 123.3582 | -61.5189 | 61.5509 | 0.80861 | 0.71956 | 0.95866 | 0.75333 | 0.99764 | 0.98295 | 0.81629 | 61.5875 | 0.23948 | 61.5141 | -0.046838 | 0.039079 | 61.6348 | -0.006014 | 61.4268 | 62.3275 | 62.2384 | 62.4775 | 62.2722 | 62.5165 | 62.5018 | 62.3352 | 123.1063 | 61.7583 | 123.033 | 61.472 | 61.5579 | 123.1537 | 61.5128 | 122.9456 | 61.5484 | 61.5935 | 61.4751 | 61.5202
2777.0625 | 123.3948 | -61.528 | 61.5646 | 0.82692 | 0.76993 | 0.98156 | 0.79453 | 1.0251 | 1.0333 | 0.83918 | 61.5783 | 0.23948 | 61.4821 | -0.03768 | 0.034501 | 61.6394 | -0.001436 | 61.4359 | 62.3549 | 62.2979 | 62.5096 | 62.3225 | 62.5531 | 62.5613 | 62.3672 | 123.1063 | 61.7675 | 123.0101 | 61.4903 | 61.5625 | 123.1674 | 61.5266 | 122.9639 | 61.5438 | 61.5797 | 61.4476 | 61.4835
2778.0625 | 123.3307 | -61.5143 | 61.5372 | 0.7903 | 0.71956 | 0.89914 | 0.75333 | 1.0114 | 0.97379 | 0.80714 | 61.6012 | 0.24405 | 61.5233 | -0.03768 | 0.029923 | 61.6394 | -0.006014 | 61.4268 | 62.3046 | 62.2338 | 62.4134 | 62.2676 | 62.5257 | 62.4881 | 62.3214 | 123.1155 | 61.7583 | 123.0376 | 61.4766 | 61.5442 | 123.1537 | 61.5083 | 122.941 | 61.5713 | 61.6072 | 61.4934 | 61.5293
2779.0625 | 123.3673 | -61.5189 | 61.5692 | 0.81777 | 0.75619 | 0.93119 | 0.77622 | 1.0388 | 1.0058 | 0.83003 | 61.5875 | 0.2349 | 61.5279 | -0.03768 | 0.034501 | 61.6348 | -0.001436 | 61.4268 | 62.3366 | 62.2751 | 62.4501 | 62.2951 | 62.5577 | 62.5247 | 62.3489 | 123.1063 | 61.7538 | 123.0467 | 61.4812 | 61.5534 | 123.1537 | 61.5174 | 122.9456 | 61.553 | 61.5889 | 61.4934 | 61.5293
2780.0625 | 123.3353 | -61.5326 | 61.5967 | 0.80861 | 0.74704 | 0.9083 | 0.77622 | 1.0434 | 1.0196 | 0.82087 | 61.6012 | 0.23948 | 61.5233 | -0.03768 | 0.034501 | 61.6394 | 0.003143 | 61.4359 | 62.3412 | 62.2796 | 62.4409 | 62.3088 | 62.576 | 62.5522 | 62.3535 | 123.1338 | 61.7721 | 123.0559 | 61.4949 | 61.5671 | 123.172 | 61.5357 | 122.9685 | 61.5667 | 61.5981 | 61.4888 | 61.5202
2781.0625 | 123.3765 | -61.528 | 61.5326 | 0.83608 | 0.77909 | 0.9083 | 0.79453 | 1.0663 | 1.047 | 0.84834 | 61.5966 | 0.23948 | 61.4912 | -0.042259 | 0.034501 | 61.6348 | -0.006014 | 61.4268 | 62.3641 | 62.3071 | 62.4363 | 62.3225 | 62.5943 | 62.5751 | 62.3764 | 123.1246 | 61.7675 | 123.0193 | 61.4858 | 61.5625 | 123.1628 | 61.522 | 122.9548 | 61.5621 | 61.6026 | 61.4567 | 61.4973
2782.0625 | 123.4177 | -61.496 | 61.5784 | 0.85897 | 0.82946 | 0.9724 | 0.83116 | 1.1075 | 1.0928 | 0.87581 | 61.5875 | 0.23948 | 61.5096 | -0.046838 | 0.034501 | 61.6394 | -0.001436 | 61.4359 | 62.3549 | 62.3254 | 62.4684 | 62.3271 | 62.6035 | 62.5888 | 62.3718 | 123.0834 | 61.7354 | 123.0055 | 61.4491 | 61.5305 | 123.1354 | 61.4945 | 122.9319 | 61.553 | 61.5889 | 61.4751 | 61.511
2783.0938 | 123.3582 | -61.5326 | 61.5646 | 0.84981 | 0.82488 | 0.96324 | 0.79911 | 1.0846 | 1.0745 | 0.86207 | 61.5875 | 0.23032 | 61.5279 | -0.03768 | 0.039079 | 61.6486 | 0.003143 | 61.4405 | 62.3824 | 62.3575 | 62.4958 | 62.3317 | 62.6172 | 62.6071 | 62.3947 | 123.1201 | 61.7629 | 123.0605 | 61.4949 | 61.5717 | 123.1812 | 61.5357 | 122.9731 | 61.5484 | 61.5843 | 61.4888 | 61.5247
2784.0625 | 123.4131 | -61.5417 | 61.5601 | 0.87728 | 0.86151 | 1.0731 | 0.83116 | 1.1029 | 1.0928 | 0.89412 | 61.5875 | 0.2349 | 61.5233 | -0.033101 | 0.043657 | 61.644 | -0.006014 | 61.4313 | 62.419 | 62.4033 | 62.6149 | 62.3729 | 62.6447 | 62.6346 | 62.4359 | 123.1292 | 61.7766 | 123.065 | 61.5086 | 61.5854 | 123.1857 | 61.5357 | 122.9731 | 61.5438 | 61.5935 | 61.4796 | 61.5293
2785.0625 | 123.2712 | -61.5372 | 61.5784 | 0.90475 | 0.90729 | 1.1235 | 0.85863 | 1.1304 | 1.1295 | 0.92159 | 61.5875 | 0.23032 | 61.4912 | -0.03768 | 0.034501 | 61.644 | -0.006014 | 61.4359 | 62.4419 | 62.4445 | 62.6607 | 62.3958 | 62.6676 | 62.6666 | 62.4588 | 123.1246 | 61.7675 | 123.0284 | 61.4995 | 61.5717 | 123.1812 | 61.5312 | 122.9731 | 61.553 | 61.5935 | 61.4567 | 61.4973
2786.0938 | 123.2849 | -61.5646 | 61.5967 | 0.9368 | 0.98513 | 1.1784 | 0.91358 | 1.1853 | 1.1432 | 0.94906 | 61.5783 | 0.2349 | 61.4775 | -0.042259 | 0.039079 | 61.6486 | -0.001436 | 61.4405 | 62.5014 | 62.5498 | 62.7431 | 62.4782 | 62.75 | 62.7078 | 62.5137 | 123.1429 | 61.7995 | 123.0421 | 61.5224 | 61.6037 | 123.2132 | 61.5632 | 123.0051 | 61.5392 | 61.5797 | 61.4384 | 61.4789
2787.0625 | 123.381 | -61.5417 | 61.5372 | 0.96427 | 0.99429 | 1.2242 | 0.96394 | 1.2265 | 1.1752 | 0.97653 | 61.5875 | 0.2349 | 61.5187 | -0.03768 | 0.034501 | 61.644 | -0.001436 | 61.4405 | 62.506 | 62.536 | 62.766 | 62.5057 | 62.7683 | 62.717 | 62.5183 | 123.1292 | 61.7766 | 123.0605 | 61.5041 | 61.5762 | 123.1857 | 61.5403 | 122.9822 | 61.553 | 61.5889 | 61.4842 | 61.5202
2788.0625 | 123.381 | -61.5234 | 61.5326 | 0.98259 | 1.008 | 1.2929 | 0.98225 | 1.2448 | 1.2027 | 0.99942 | 61.5829 | 0.23948 | 61.5141 | -0.042259 | 0.029923 | 61.6486 | -0.001436 | 61.4451 | 62.506 | 62.5315 | 62.8163 | 62.5057 | 62.7683 | 62.7261 | 62.5229 | 123.1063 | 61.7629 | 123.0376 | 61.4812 | 61.5534 | 123.172 | 61.522 | 122.9685 | 61.553 | 61.5843 | 61.4842 | 61.5156
2789.0938 | 123.436 | -61.528 | 61.5921 | 0.97801 | 1.008 | 1.3753 | 0.96852 | 1.2265 | 1.1752 | 0.99026 | 61.5829 | 0.23948 | 61.505 | -0.03768 | 0.034501 | 61.6531 | 0.003143 | 61.4405 | 62.506 | 62.536 | 62.9033 | 62.4965 | 62.7545 | 62.7033 | 62.5183 | 123.1109 | 61.7675 | 123.033 | 61.4903 | 61.5625 | 123.1812 | 61.5312 | 122.9685 | 61.5484 | 61.5797 | 61.4705 | 61.5018
2790.0625 | 123.3078 | -61.528 | 61.6013 | 1.0101 | 1.0263 | 1.3707 | 0.96852 | 1.2265 | 1.1386 | 1.0315 | 61.5829 | 0.2349 | 61.4867 | -0.042259 | 0.039079 | 61.6531 | 0.003143 | 61.4405 | 62.5381 | 62.5544 | 62.8988 | 62.4965 | 62.7545 | 62.6666 | 62.5595 | 123.1109 | 61.7629 | 123.0147 | 61.4858 | 61.5671 | 123.1812 | 61.5312 | 122.9685 | 61.5438 | 61.5797 | 61.4476 | 61.4835
2791.0625 | 123.3856 | -61.528 | 61.5509 | 1.0192 | 1.0447 | 1.3936 | 0.98225 | 1.2128 | 1.1386 | 1.036 | 61.5783 | 0.2349 | 61.5004 | -0.03768 | 0.034501 | 61.6486 | -0.006014 | 61.4405 | 62.5472 | 62.5727 | 62.9216 | 62.5103 | 62.7408 | 62.6666 | 62.5641 | 123.1063 | 61.7629 | 123.0284 | 61.4903 | 61.5625 | 123.1766 | 61.522 | 122.9685 | 61.5438 | 61.5843 | 61.4659 | 61.5064
2792.0625 | 123.3124 | -61.5601 | 61.5509 | 1.0375 | 1.0492 | 1.3936 | 0.99599 | 1.222 | 1.1523 | 1.0589 | 61.5829 | 0.2349 | 61.505 | -0.042259 | 0.029923 | 61.6577 | -0.001436 | 61.4496 | 62.5976 | 62.6093 | 62.9537 | 62.556 | 62.782 | 62.7124 | 62.619 | 123.1429 | 61.795 | 123.065 | 61.5178 | 61.59 | 123.2178 | 61.5586 | 123.0097 | 61.553 | 61.5843 | 61.4751 | 61.5064
2793.0625 | 123.2346 | -61.5555 | 61.5829 | 1.0421 | 1.0538 | 1.3753 | 1.0189 | 1.1899 | 1.1615 | 1.0681 | 61.5875 | 0.2349 | 61.5096 | -0.033101 | 0.039079 | 61.6577 | 0.003143 | 61.4496 | 62.5976 | 62.6093 | 62.9308 | 62.5744 | 62.7454 | 62.717 | 62.6236 | 123.1429 | 61.7904 | 123.065 | 61.5224 | 61.5946 | 123.2132 | 61.5586 | 123.0051 | 61.5484 | 61.5843 | 61.4705 | 61.5064
2794.0625 | 123.3124 | -61.5601 | 61.6013 | 1.0421 | 1.0355 | 1.2975 | 1.0006 | 1.167 | 1.1478 | 1.0498 | 61.5783 | 0.23948 | 61.4912 | -0.03768 | 0.039079 | 61.6486 | -0.006014 | 61.4451 | 62.6022 | 62.5956 | 62.8575 | 62.5606 | 62.7271 | 62.7078 | 62.6098 | 123.1384 | 61.7995 | 123.0513 | 61.5224 | 61.5991 | 123.2086 | 61.554 | 123.0051 | 61.5392 | 61.5843 | 61.4522 | 61.4973
2795.0625 | 123.4131 | -61.528 | 61.5601 | 1.0421 | 1.0172 | 1.2929 | 0.99599 | 1.1716 | 1.1707 | 1.0589 | 61.5737 | 0.23948 | 61.4821 | -0.03768 | 0.043657 | 61.6486 | 0.003143 | 61.4451 | 62.5701 | 62.5452 | 62.8209 | 62.524 | 62.6996 | 62.6987 | 62.587 | 123.1017 | 61.7675 | 123.0101 | 61.4903 | 61.5717 | 123.1766 | 61.5312 | 122.9731 | 61.5301 | 61.5706 | 61.4384 | 61.4789
2796.0625 | 123.2941 | -61.5692 | 61.5875 | 1.0558 | 1.0309 | 1.3616 | 1.028 | 1.1762 | 1.2119 | 1.0681 | 61.5829 | 0.2349 | 61.5141 | -0.046838 | 0.039079 | 61.6531 | -0.006014 | 61.4496 | 62.6251 | 62.6001 | 62.9308 | 62.5973 | 62.7454 | 62.7811 | 62.6373 | 123.1521 | 61.8041 | 123.0833 | 61.5224 | 61.6083 | 123.2224 | 61.5632 | 123.0189 | 61.5438 | 61.5889 | 61.4751 | 61.5202
2797.0625 | 123.2986 | -61.5601 | 61.5875 | 1.097 | 1.0904 | 1.4806 | 1.0647 | 1.1991 | 1.2714 | 1.1185 | 61.5783 | 0.2349 | 61.5096 | -0.051417 | 0.034501 | 61.6577 | -0.001436 | 61.4542 | 62.6571 | 62.6505 | 63.0407 | 62.6247 | 62.7591 | 62.8314 | 62.6785 | 123.1384 | 61.795 | 123.0696 | 61.5086 | 61.5946 | 123.2178 | 61.5586 | 123.0143 | 61.5438 | 61.5797 | 61.4751 | 61.511
2798.0625 | 123.2941 | -61.5738 | 61.6104 | 1.1199 | 1.1271 | 1.4806 | 1.0784 | 1.1624 | 1.2897 | 1.1459 | 61.5783 | 0.23948 | 61.5004 | -0.042259 | 0.029923 | 61.6623 | -0.006014 | 61.4588 | 62.6937 | 62.7009 | 63.0544 | 62.6522 | 62.7362 | 62.8635 | 62.7197 | 123.1521 | 61.8133 | 123.0742 | 61.5315 | 61.6037 | 123.2361 | 61.5678 | 123.0326 | 61.5484 | 61.5843 | 61.4705 | 61.5064
2799.0938 | 123.3353 | -61.5326 | 61.6104 | 1.152 | 1.1408 | 1.4852 | 1.115 | 1.1853 | 1.3309 | 1.1688 | 61.5691 | 0.2349 | 61.4729 | -0.033101 | 0.029923 | 61.6669 | -0.006014 | 61.4496 | 62.6846 | 62.6734 | 63.0178 | 62.6476 | 62.7179 | 62.8635 | 62.7014 | 123.1017 | 61.7675 | 123.0055 | 61.4995 | 61.5625 | 123.1995 | 61.5266 | 122.9822 | 61.5392 | 61.5752 | 61.443 | 61.4789
2800.0625 | 123.381 | -61.5646 | 61.5463 | 1.152 | 1.1317 | 1.476 | 1.0967 | 1.1624 | 1.3034 | 1.1688 | 61.5783 | 0.2349 | 61.4912 | -0.03768 | 0.029923 | 61.6623 | -0.001436 | 61.4542 | 62.7166 | 62.6963 | 63.0407 | 62.6613 | 62.7271 | 62.8681 | 62.7334 | 123.1429 | 61.7995 | 123.0559 | 61.527 | 61.5946 | 123.2269 | 61.5632 | 123.0189 | 61.5484 | 61.5797 | 61.4613 | 61.4927
2801.0625 | 123.3307 | -61.5555 | 61.5738 | 1.1474 | 1.1088 | 1.4211 | 1.0647 | 1.1716 | 1.2576 | 1.1597 | 61.592 | 0.2349 | 61.5141 | -0.028522 | 0.034501 | 61.6531 | 0.007721 | 61.4542 | 62.7029 | 62.6642 | 62.9766 | 62.6201 | 62.7271 | 62.8131 | 62.7151 | 123.1475 | 61.7904 | 123.0696 | 61.527 | 61.59 | 123.2086 | 61.5632 | 123.0097 | 61.5575 | 61.5843 | 61.4796 | 61.5064
2802.0781 | 123.3032 | -61.5417 | 61.6104 | 1.1657 | 1.1271 | 1.4623 | 1.0647 | 1.167 | 1.2485 | 1.178 | 61.5783 | 0.24405 | 61.505 | -0.033101 | 0.034501 | 61.6669 | -0.001436 | 61.4542 | 62.7075 | 62.6688 | 63.0041 | 62.6064 | 62.7088 | 62.7902 | 62.7197 | 123.1201 | 61.7858 | 123.0467 | 61.5086 | 61.5762 | 123.2086 | 61.5403 | 122.996 | 61.5438 | 61.5797 | 61.4705 | 61.5064
2803.0625 | 123.3307 | -61.5601 | 61.6058 | 1.1749 | 1.15 | 1.4852 | 1.1104 | 1.2174 | 1.2851 | 1.1963 | 61.5646 | 0.2349 | 61.4867 | -0.03768 | 0.034501 | 61.6577 | 0.003143 | 61.4496 | 62.7349 | 62.71 | 63.0453 | 62.6705 | 62.7774 | 62.8452 | 62.7563 | 123.1246 | 61.795 | 123.0467 | 61.5224 | 61.5946 | 123.2178 | 61.5632 | 123.0097 | 61.5301 | 61.5614 | 61.4522 | 61.4835
2804.0625 | 123.317 | -61.5463 | 61.6287 | 1.1611 | 1.1408 | 1.4898 | 1.0921 | 1.1808 | 1.2714 | 1.178 | 61.5691 | 0.2349 | 61.4821 | -0.042259 | 0.029923 | 61.6623 | 0.003143 | 61.4542 | 62.7075 | 62.6871 | 63.0361 | 62.6385 | 62.7271 | 62.8177 | 62.7243 | 123.1155 | 61.7812 | 123.0284 | 61.5041 | 61.5762 | 123.2086 | 61.5495 | 123.0006 | 61.5392 | 61.566 | 61.4522 | 61.4789
2805.0938 | 123.3994 | -61.5234 | 61.5875 | 1.2252 | 1.1683 | 1.5081 | 1.0876 | 1.1808 | 1.1798 | 1.2375 | 61.5829 | 0.23948 | 61.505 | -0.042259 | 0.034501 | 61.6577 | 0.007721 | 61.4542 | 62.7487 | 62.6917 | 63.0315 | 62.611 | 62.7042 | 62.7033 | 62.7609 | 123.1063 | 61.7629 | 123.0284 | 61.4812 | 61.5579 | 123.1812 | 61.5312 | 122.9777 | 61.5484 | 61.5752 | 61.4705 | 61.4973
2806.0625 | 123.3124 | -61.5738 | 61.615 | 1.2207 | 1.1729 | 1.4944 | 1.115 | 1.254 | 1.1707 | 1.2329 | 61.5829 | 0.23948 | 61.5141 | -0.03768 | 0.039079 | 61.6531 | -0.001436 | 61.4588 | 62.7945 | 62.7467 | 63.0682 | 62.6888 | 62.8278 | 62.7445 | 62.8067 | 123.1567 | 61.8133 | 123.0879 | 61.5361 | 61.6129 | 123.2269 | 61.5724 | 123.0326 | 61.5438 | 61.5843 | 61.4751 | 61.5156
2807.0625 | 123.2666 | -61.5646 | 61.615 | 1.2298 | 1.1912 | 1.4898 | 1.1196 | 1.2677 | 1.1981 | 1.2512 | 61.5737 | 0.23948 | 61.5004 | -0.03768 | 0.043657 | 61.6623 | 0.007721 | 61.4588 | 62.7945 | 62.7558 | 63.0544 | 62.6842 | 62.8324 | 62.7628 | 62.8159 | 123.1384 | 61.8041 | 123.065 | 61.527 | 61.6083 | 123.2269 | 61.5724 | 123.0234 | 61.5301 | 61.566 | 61.4567 | 61.4927
2808.1094 | 123.2986 | -61.5784 | 61.5692 | 1.1611 | 1.1729 | 1.444 | 1.1013 | 1.2723 | 1.2805 | 1.1688 | 61.5737 | 0.2349 | 61.4775 | -0.042259 | 0.034501 | 61.6623 | -0.001436 | 61.4451 | 62.7395 | 62.7512 | 63.0224 | 62.6797 | 62.8507 | 62.8589 | 62.7472 | 123.1521 | 61.8133 | 123.0559 | 61.5361 | 61.6129 | 123.2407 | 61.5769 | 123.0234 | 61.5392 | 61.5752 | 61.443 | 61.4789
2809.0625 | 123.4543 | -61.5601 | 61.5097 | 1.1245 | 1.1912 | 1.4486 | 1.0967 | 1.3181 | 1.2531 | 1.1551 | 61.5737 | 0.23032 | 61.4729 | -0.042259 | 0.029923 | 61.6577 | -0.001436 | 61.4496 | 62.6846 | 62.7512 | 63.0086 | 62.6568 | 62.8782 | 62.8131 | 62.7151 | 123.1338 | 61.7904 | 123.033 | 61.5178 | 61.59 | 123.2178 | 61.5586 | 123.0097 | 61.5438 | 61.5752 | 61.443 | 61.4744
2810.0625 | 123.2803 | -61.5463 | 61.615 | 1.1428 | 1.1912 | 1.476 | 1.0921 | 1.3181 | 1.2393 | 1.1688 | 61.5737 | 0.23032 | 61.4729 | -0.042259 | 0.039079 | 61.6623 | 0.003143 | 61.4542 | 62.6892 | 62.7375 | 63.0224 | 62.6385 | 62.8644 | 62.7857 | 62.7151 | 123.1201 | 61.7766 | 123.0193 | 61.5041 | 61.5854 | 123.2086 | 61.5495 | 123.0006 | 61.5346 | 61.5706 | 61.4339 | 61.4698
2811.0625 | 123.3582 | -61.528 | 61.5646 | 1.1611 | 1.2049 | 1.4486 | 1.1104 | 1.341 | 1.2668 | 1.178 | 61.5737 | 0.23948 | 61.4912 | -0.03768 | 0.043657 | 61.6577 | 0.007721 | 61.4588 | 62.6892 | 62.7329 | 62.9766 | 62.6385 | 62.869 | 62.7948 | 62.706 | 123.1017 | 61.7675 | 123.0193 | 61.4903 | 61.5717 | 123.1857 | 61.5357 | 122.9868 | 61.5301 | 61.566 | 61.4476 | 61.4835
2812.0625 | 123.3765 | -61.5189 | 61.5784 | 1.2115 | 1.1958 | 1.325 | 1.0967 | 1.3181 | 1.1707 | 1.2375 | 61.5783 | 0.23032 | 61.5096 | -0.03768 | 0.039079 | 61.6623 | 0.003143 | 61.4496 | 62.7304 | 62.7146 | 62.8438 | 62.6156 | 62.837 | 62.6895 | 62.7563 | 123.0972 | 61.7492 | 123.0284 | 61.4812 | 61.5579 | 123.1812 | 61.522 | 122.9685 | 61.5392 | 61.5752 | 61.4705 | 61.5064
2813.0625 | 123.2941 | -61.5555 | 61.5967 | 1.2115 | 1.1546 | 1.3295 | 1.083 | 1.2952 | 1.1661 | 1.2237 | 61.5829 | 0.2349 | 61.5096 | -0.03768 | 0.039079 | 61.6623 | -0.006014 | 61.4588 | 62.767 | 62.71 | 62.885 | 62.6385 | 62.8507 | 62.7216 | 62.7792 | 123.1384 | 61.7904 | 123.065 | 61.5178 | 61.5946 | 123.2178 | 61.5495 | 123.0143 | 61.5438 | 61.5889 | 61.4705 | 61.5156
2814.0625 | 123.4543 | -61.5189 | 61.5646 | 1.1886 | 1.15 | 1.2929 | 1.0647 | 1.286 | 1.1432 | 1.2054 | 61.5783 | 0.2349 | 61.5141 | -0.033101 | 0.034501 | 61.6531 | -0.001436 | 61.4496 | 62.7075 | 62.6688 | 62.8118 | 62.5835 | 62.8049 | 62.662 | 62.7243 | 123.0972 | 61.7538 | 123.033 | 61.4858 | 61.5534 | 123.172 | 61.5174 | 122.9685 | 61.5438 | 61.5797 | 61.4796 | 61.5156
2815.0625 | 123.349 | -61.5326 | 61.5509 | 1.1886 | 1.15 | 1.2425 | 1.0738 | 1.2815 | 1.1386 | 1.1963 | 61.5829 | 0.2349 | 61.5141 | -0.046838 | 0.029923 | 61.6577 | -0.001436 | 61.4542 | 62.7212 | 62.6826 | 62.7751 | 62.6064 | 62.8141 | 62.6712 | 62.7289 | 123.1155 | 61.7675 | 123.0467 | 61.4858 | 61.5625 | 123.1903 | 61.5312 | 122.9868 | 61.553 | 61.5843 | 61.4842 | 61.5156
2816.0625 | 123.4406 | -61.5463 | 61.5784 | 1.2161 | 1.1362 | 1.2471 | 1.083 | 1.3135 | 1.1752 | 1.2237 | 61.5783 | 0.23948 | 61.5004 | -0.042259 | 0.039079 | 61.6531 | 0.003143 | 61.4542 | 62.7624 | 62.6826 | 62.7934 | 62.6293 | 62.8598 | 62.7216 | 62.7701 | 123.1246 | 61.7858 | 123.0467 | 61.5041 | 61.5854 | 123.1995 | 61.5495 | 123.0006 | 61.5392 | 61.5752 | 61.4613 | 61.4973
2817.0625 | 123.4177 | -61.5555 | 61.5921 | 1.152 | 1.1408 | 1.2151 | 1.1059 | 1.2906 | 1.2943 | 1.1642 | 61.5737 | 0.23032 | 61.4729 | -0.042259 | 0.039079 | 61.6623 | -0.001436 | 61.4451 | 62.7075 | 62.6963 | 62.7705 | 62.6614 | 62.8461 | 62.8498 | 62.7197 | 123.1292 | 61.7858 | 123.0284 | 61.5132 | 61.5946 | 123.2178 | 61.554 | 123.0006 | 61.5346 | 61.5752 | 61.4339 | 61.4744
2818.1094 | 123.3856 | -61.5417 | 61.5829 | 1.1154 | 1.1088 | 1.2013 | 1.0647 | 1.2586 | 1.2714 | 1.1368 | 61.5737 | 0.24405 | 61.4821 | -0.03768 | 0.029923 | 61.6623 | -0.001436 | 61.4451 | 62.6571 | 62.6505 | 62.7431 | 62.6064 | 62.8003 | 62.8131 | 62.6785 | 123.1155 | 61.7858 | 123.0238 | 61.5041 | 61.5717 | 123.204 | 61.5403 | 122.9868 | 61.5438 | 61.5752 | 61.4522 | 61.4835
2819.0625 | 123.3994 | -61.5189 | 61.5692 | 1.0925 | 1.1088 | 1.1784 | 1.0509 | 1.2403 | 1.2393 | 1.1093 | 61.5829 | 0.2349 | 61.505 | -0.03768 | 0.039079 | 61.6577 | -0.001436 | 61.4542 | 62.6113 | 62.6276 | 62.6973 | 62.5698 | 62.7591 | 62.7582 | 62.6282 | 123.1017 | 61.7538 | 123.0238 | 61.4812 | 61.5579 | 123.1766 | 61.5174 | 122.9731 | 61.5438 | 61.5843 | 61.4659 | 61.5064
2820.0625 | 123.3719 | -61.5326 | 61.5601 | 1.0742 | 1.1362 | 1.2242 | 1.0555 | 1.2403 | 1.2622 | 1.091 | 61.5829 | 0.23948 | 61.5141 | -0.042259 | 0.039079 | 61.6577 | 0.003143 | 61.4496 | 62.6067 | 62.6688 | 62.7568 | 62.5881 | 62.7729 | 62.7948 | 62.6236 | 123.1155 | 61.7721 | 123.0467 | 61.4903 | 61.5717 | 123.1903 | 61.5357 | 122.9822 | 61.5438 | 61.5797 | 61.4751 | 61.511
2821.1094 | 123.2849 | -61.5692 | 61.5829 | 1.0787 | 1.1683 | 1.2746 | 1.0784 | 1.2494 | 1.2622 | 1.0956 | 61.5783 | 0.2349 | 61.4912 | -0.03768 | 0.043657 | 61.6577 | -0.006014 | 61.4451 | 62.6479 | 62.7375 | 62.8438 | 62.6476 | 62.8186 | 62.8314 | 62.6648 | 123.1475 | 61.8041 | 123.0605 | 61.5315 | 61.6129 | 123.2269 | 61.5632 | 123.0143 | 61.5346 | 61.5843 | 61.4476 | 61.4973
2822.0625 | 123.3765 | -61.5234 | 61.6013 | 1.097 | 1.1271 | 1.2654 | 1.0738 | 1.2448 | 1.2531 | 1.1047 | 61.5691 | 0.2349 | 61.4775 | -0.03768 | 0.039079 | 61.6531 | -0.001436 | 61.4451 | 62.6205 | 62.6505 | 62.7889 | 62.5973 | 62.7683 | 62.7765 | 62.6282 | 123.0926 | 61.7583 | 123.0009 | 61.4858 | 61.5625 | 123.1766 | 61.522 | 122.9685 | 61.5301 | 61.5706 | 61.4384 | 61.4789
2823.0625 | 123.3307 | -61.528 | 61.5555 | 1.1154 | 1.1362 | 1.2471 | 1.0738 | 1.254 | 1.2576 | 1.1276 | 61.5783 | 0.2349 | 61.5096 | -0.03768 | 0.039079 | 61.6577 | -0.001436 | 61.4496 | 62.6434 | 62.6643 | 62.7751 | 62.6018 | 62.782 | 62.7857 | 62.6556 | 123.1063 | 61.7629 | 123.0376 | 61.4903 | 61.5671 | 123.1857 | 61.5266 | 122.9777 | 61.5392 | 61.5797 | 61.4705 | 61.511
2824.0625 | 123.3307 | -61.5372 | 61.5738 | 1.1062 | 1.1408 | 1.238 | 1.083 | 1.2357 | 1.2393 | 1.1139 | 61.5737 | 0.2349 | 61.5141 | -0.033101 | 0.034501 | 61.6486 | -0.001436 | 61.4496 | 62.6434 | 62.678 | 62.7751 | 62.6201 | 62.7729 | 62.7765 | 62.651 | 123.1109 | 61.7721 | 123.0513 | 61.5041 | 61.5717 | 123.1857 | 61.5357 | 122.9868 | 61.5392 | 61.5752 | 61.4796 | 61.5156
2825.0938 | 123.4406 | -61.5463 | 61.5417 | 1.0604 | 1.1133 | 1.1693 | 1.0143 | 1.1808 | 1.1844 | 1.0772 | 61.5737 | 0.23948 | 61.5096 | -0.042259 | 0.029923 | 61.6623 | -0.006014 | 61.4496 | 62.6067 | 62.6597 | 62.7156 | 62.5606 | 62.7271 | 62.7307 | 62.6236 | 123.1201 | 61.7858 | 123.0559 | 61.5041 | 61.5762 | 123.2086 | 61.5403 | 122.996 | 61.5438 | 61.5797 | 61.4796 | 61.5156
2826.0625 | 123.3902 | -61.5326 | 61.6058 | 1.0742 | 1.1088 | 1.1739 | 1.028 | 1.1991 | 1.1981 | 1.0864 | 61.5783 | 0.2349 | 61.4867 | -0.042259 | 0.039079 | 61.6531 | 0.003143 | 61.4451 | 62.6067 | 62.6414 | 62.7065 | 62.5606 | 62.7317 | 62.7307 | 62.619 | 123.1109 | 61.7675 | 123.0193 | 61.4903 | 61.5717 | 123.1857 | 61.5357 | 122.9777 | 61.5392 | 61.5752 | 61.4476 | 61.4835
2827.0625 | 123.4085 | -61.5417 | 61.5417 | 1.0513 | 1.0996 | 1.1464 | 1.0097 | 1.1899 | 1.2027 | 1.0589 | 61.5737 | 0.23948 | 61.4912 | -0.042259 | 0.034501 | 61.6531 | 0.003143 | 61.4451 | 62.593 | 62.6414 | 62.6881 | 62.5515 | 62.7317 | 62.7445 | 62.6007 | 123.1155 | 61.7812 | 123.033 | 61.4995 | 61.5762 | 123.1949 | 61.5449 | 122.9868 | 61.5392 | 61.5706 | 61.4567 | 61.4881
2828.0938 | 123.2986 | -61.5646 | 61.5875 | 1.0375 | 1.1088 | 1.1784 | 1.0051 | 1.1808 | 1.221 | 1.0544 | 61.5829 | 0.2349 | 61.5141 | -0.03768 | 0.034501 | 61.6486 | -0.006014 | 61.4542 | 62.6022 | 62.6734 | 62.7431 | 62.5698 | 62.7454 | 62.7857 | 62.619 | 123.1475 | 61.7995 | 123.0788 | 61.527 | 61.5991 | 123.2132 | 61.5586 | 123.0189 | 61.5484 | 61.5889 | 61.4796 | 61.5202
2829.0625 | 123.3902 | -61.5417 | 61.5463 | 1.0284 | 1.1225 | 1.1601 | 1.0051 | 1.1808 | 1.2531 | 1.0544 | 61.5783 | 0.23948 | 61.5096 | -0.03768 | 0.029923 | 61.6577 | -0.001436 | 61.4451 | 62.5701 | 62.6642 | 62.7019 | 62.5469 | 62.7225 | 62.7948 | 62.5961 | 123.1201 | 61.7812 | 123.0513 | 61.5041 | 61.5717 | 123.1995 | 61.5403 | 122.9868 | 61.5484 | 61.5797 | 61.4796 | 61.511
2830.0938 | 123.3215 | -61.5601 | 61.5463 | 1.0238 | 1.1225 | 1.183 | 1.0051 | 1.1945 | 1.2256 | 1.0406 | 61.5829 | 0.2349 | 61.5187 | -0.042259 | 0.039079 | 61.6486 | -0.006014 | 61.4496 | 62.5839 | 62.6826 | 62.7431 | 62.5652 | 62.7545 | 62.7857 | 62.6007 | 123.1429 | 61.795 | 123.0788 | 61.5178 | 61.5991 | 123.2086 | 61.554 | 123.0097 | 61.5438 | 61.5889 | 61.4796 | 61.5247
2831.0625 | 123.3673 | -61.528 | 61.5601 | 1.0833 | 1.1454 | 1.1876 | 1.0097 | 1.2403 | 1.2668 | 1.1001 | 61.5783 | 0.24405 | 61.5141 | -0.03768 | 0.039079 | 61.6531 | 0.007721 | 61.4496 | 62.6113 | 62.6734 | 62.7156 | 62.5377 | 62.7683 | 62.7948 | 62.6282 | 123.1063 | 61.7721 | 123.0422 | 61.4903 | 61.5671 | 123.1812 | 61.5357 | 122.9777 | 61.5392 | 61.5706 | 61.4751 | 61.5064
2832.0625 | 123.2758 | -61.5646 | 61.5372 | 1.1108 | 1.1683 | 1.2288 | 1.0235 | 1.2632 | 1.3126 | 1.1276 | 61.5829 | 0.23948 | 61.5096 | -0.033101 | 0.034501 | 61.6577 | -0.001436 | 61.4542 | 62.6754 | 62.7329 | 62.7934 | 62.5881 | 62.8278 | 62.8772 | 62.6922 | 123.1475 | 61.8041 | 123.0742 | 61.5315 | 61.5991 | 123.2224 | 61.5632 | 123.0189 | 61.5484 | 61.5843 | 61.4751 | 61.511
2833.0625 | 123.3719 | -61.528 | 61.5189 | 1.1108 | 1.1683 | 1.2196 | 1.0189 | 1.254 | 1.2989 | 1.1368 | 61.5646 | 0.23948 | 61.5096 | -0.042259 | 0.034501 | 61.6623 | 0.003143 | 61.4451 | 62.6388 | 62.6963 | 62.7477 | 62.5469 | 62.782 | 62.8269 | 62.6648 | 123.0926 | 61.7675 | 123.0376 | 61.4858 | 61.5625 | 123.1903 | 61.5312 | 122.9731 | 61.5301 | 61.5614 | 61.4751 | 61.5064
2834.0625 | 123.2758 | -61.5829 | 61.5555 | 1.1108 | 1.182 | 1.2609 | 1.028 | 1.254 | 1.308 | 1.1276 | 61.5691 | 0.2349 | 61.4775 | -0.033101 | 0.039079 | 61.6531 | 0.003143 | 61.4451 | 62.6937 | 62.765 | 62.8438 | 62.611 | 62.8369 | 62.891 | 62.7106 | 123.1521 | 61.8178 | 123.0605 | 61.5498 | 61.622 | 123.2361 | 61.5861 | 123.028 | 61.5301 | 61.566 | 61.4384 | 61.4744
2835.0781 | 123.2895 | -61.5646 | 61.5829 | 1.1245 | 1.1637 | 1.2334 | 1.0235 | 1.254 | 1.3217 | 1.1413 | 61.5691 | 0.24863 | 61.4821 | -0.033101 | 0.039079 | 61.6577 | -0.001436 | 61.4451 | 62.6892 | 62.7283 | 62.798 | 62.5881 | 62.8186 | 62.8864 | 62.706 | 123.1338 | 61.8133 | 123.0467 | 61.5315 | 61.6037 | 123.2224 | 61.5632 | 123.0097 | 61.5301 | 61.5706 | 61.443 | 61.4835
2836.0625 | 123.3902 | -61.5417 | 61.5463 | 1.1154 | 1.1683 | 1.2425 | 1.0143 | 1.2494 | 1.3126 | 1.1459 | 61.5737 | 0.2349 | 61.4821 | -0.03768 | 0.039079 | 61.6486 | -0.006014 | 61.4405 | 62.6571 | 62.71 | 62.7843 | 62.556 | 62.7912 | 62.8543 | 62.6877 | 123.1155 | 61.7766 | 123.0238 | 61.5041 | 61.5808 | 123.1903 | 61.5357 | 122.9822 | 61.5346 | 61.5797 | 61.443 | 61.4881
2837.0625 | 123.2391 | -61.5646 | 61.5829 | 1.2298 | 1.182 | 1.2746 | 1.0372 | 1.2586 | 1.2119 | 1.2512 | 61.5783 | 0.22574 | 61.4775 | -0.03768 | 0.034501 | 61.6577 | -0.001436 | 61.4496 | 62.7945 | 62.7467 | 62.8392 | 62.6018 | 62.8232 | 62.7765 | 62.8159 | 123.1429 | 61.7904 | 123.0421 | 61.527 | 61.5991 | 123.2224 | 61.5632 | 123.0143 | 61.5438 | 61.5797 | 61.443 | 61.4789
2838.0625 | 123.2849 | -61.5875 | 61.5921 | 1.239 | 1.15 | 1.2425 | 1.028 | 1.2311 | 1.189 | 1.2512 | 61.5783 | 0.2349 | 61.5141 | -0.033101 | 0.034501 | 61.6623 | -0.006014 | 61.4496 | 62.8265 | 62.7375 | 62.8301 | 62.6156 | 62.8186 | 62.7765 | 62.8387 | 123.1658 | 61.8224 | 123.1017 | 61.5544 | 61.622 | 123.2498 | 61.5815 | 123.0372 | 61.5438 | 61.5843 | 61.4796 | 61.5202
2839.1094 | 123.3353 | -61.5372 | 61.5646 | 1.2436 | 1.1546 | 1.2517 | 1.0326 | 1.2265 | 1.1981 | 1.2558 | 61.5783 | 0.24405 | 61.5141 | -0.042259 | 0.043657 | 61.6531 | -0.001436 | 61.4496 | 62.7807 | 62.6917 | 62.7889 | 62.5698 | 62.7637 | 62.7353 | 62.793 | 123.1155 | 61.7812 | 123.0513 | 61.4949 | 61.5808 | 123.1903 | 61.5357 | 122.9868 | 61.5346 | 61.5797 | 61.4705 | 61.5156
2840.0625 | 123.3032 | -61.5326 | 61.6013 | 1.152 | 1.1729 | 1.238 | 1.0555 | 1.2769 | 1.3858 | 1.1642 | 61.5783 | 0.23948 | 61.5141 | -0.042259 | 0.043657 | 61.6623 | -0.006014 | 61.4588 | 62.6846 | 62.7055 | 62.7706 | 62.5881 | 62.8095 | 62.9184 | 62.6968 | 123.1109 | 61.7721 | 123.0467 | 61.4903 | 61.5763 | 123.1949 | 61.5266 | 122.9914 | 61.5346 | 61.5843 | 61.4705 | 61.5202
2841.0781 | 123.1888 | -61.5372 | 61.615 | 1.2298 | 1.1637 | 1.2013 | 1.0051 | 1.2036 | 1.1936 | 1.2558 | 61.5829 | 0.2349 | 61.5141 | -0.033101 | 0.039079 | 61.6623 | 0.003143 | 61.4542 | 62.767 | 62.7009 | 62.7385 | 62.5423 | 62.7408 | 62.7307 | 62.793 | 123.1201 | 61.7721 | 123.0513 | 61.5041 | 61.5762 | 123.1995 | 61.5403 | 122.9914 | 61.5438 | 61.5797 | 61.4751 | 61.511
2842.0625 | 123.3124 | -61.5784 | 61.5829 | 1.2161 | 1.1271 | 1.1693 | 0.99141 | 1.1808 | 1.1752 | 1.2375 | 61.5783 | 0.2349 | 61.5141 | -0.042259 | 0.039079 | 61.6577 | -0.006014 | 61.4451 | 62.7945 | 62.7054 | 62.7476 | 62.5698 | 62.7591 | 62.7536 | 62.8159 | 123.1567 | 61.8133 | 123.0925 | 61.5361 | 61.6174 | 123.2361 | 61.5724 | 123.0234 | 61.5392 | 61.5843 | 61.4751 | 61.5202
2843.0625 | 123.317 | -61.5463 | 61.5967 | 1.2436 | 1.1546 | 1.183 | 0.99599 | 1.1945 | 1.2027 | 1.2604 | 61.5829 | 0.23948 | 61.505 | -0.033101 | 0.034501 | 61.6623 | 0.007721 | 61.4542 | 62.7899 | 62.7009 | 62.7293 | 62.5423 | 62.7408 | 62.749 | 62.8067 | 123.1292 | 61.7858 | 123.0513 | 61.5132 | 61.5808 | 123.2086 | 61.554 | 123.0006 | 61.5484 | 61.5752 | 61.4705 | 61.4973
2844.0625 | 123.3261 | -61.5738 | 61.5738 | 1.2573 | 1.1591 | 1.2013 | 1.0097 | 1.222 | 1.2119 | 1.2695 | 61.5737 | 0.23948 | 61.4821 | -0.03768 | 0.034501 | 61.6623 | -0.001436 | 61.4405 | 62.8311 | 62.7329 | 62.7751 | 62.5835 | 62.7957 | 62.7857 | 62.8433 | 123.1475 | 61.8133 | 123.0559 | 61.5361 | 61.6083 | 123.2361 | 61.5724 | 123.0143 | 61.5392 | 61.5752 | 61.4476 | 61.4835
2845.0938 | 123.2712 | -61.5555 | 61.6333 | 1.2848 | 1.182 | 1.2471 | 1.0326 | 1.2403 | 1.2393 | 1.297 | 61.5737 | 0.22574 | 61.4867 | -0.028522 | 0.043657 | 61.6623 | -0.001436 | 61.4588 | 62.8402 | 62.7375 | 62.8026 | 62.5881 | 62.7957 | 62.7948 | 62.8525 | 123.1292 | 61.7812 | 123.0421 | 61.527 | 61.5991 | 123.2178 | 61.554 | 123.0143 | 61.5301 | 61.5752 | 61.443 | 61.4881
2846.0625 | 123.317 | -61.5692 | 61.6104 | 1.271 | 1.1591 | 1.1647 | 0.99599 | 1.2403 | 1.2348 | 1.3016 | 61.5829 | 0.23948 | 61.4958 | -0.028522 | 0.039079 | 61.6623 | 0.003143 | 61.4496 | 62.8402 | 62.7283 | 62.7339 | 62.5652 | 62.8095 | 62.804 | 62.8708 | 123.1521 | 61.8087 | 123.065 | 61.5407 | 61.6083 | 123.2315 | 61.5724 | 123.0189 | 61.5438 | 61.5797 | 61.4567 | 61.4927
2847.0625 | 123.3719 | -61.5509 | 61.5463 | 1.2939 | 1.1637 | 1.1098 | 1.0006 | 1.2632 | 1.2439 | 1.297 | 61.5783 | 0.24405 | 61.4958 | -0.03768 | 0.034501 | 61.6577 | -0.001436 | 61.4542 | 62.8448 | 62.7146 | 62.6607 | 62.5515 | 62.8141 | 62.7948 | 62.8479 | 123.1292 | 61.795 | 123.0467 | 61.5132 | 61.5854 | 123.2086 | 61.5495 | 123.0051 | 61.5438 | 61.5797 | 61.4613 | 61.4973
2848.0938 | 123.3673 | -61.5646 | 61.5921 | 1.2756 | 1.15 | 1.0869 | 1.0051 | 1.254 | 1.2393 | 1.297 | 61.5783 | 0.23948 | 61.505 | -0.042259 | 0.034501 | 61.6531 | -0.001436 | 61.4588 | 62.8402 | 62.7146 | 62.6515 | 62.5698 | 62.8186 | 62.804 | 62.8616 | 123.1429 | 61.8041 | 123.0696 | 61.5224 | 61.5991 | 123.2178 | 61.5632 | 123.0234 | 61.5438 | 61.5797 | 61.4705 | 61.5064
2849.0625 | 123.3536 | -61.5234 | 61.5097 | 1.2893 | 1.1408 | 1.0731 | 1.0189 | 1.2632 | 1.2439 | 1.3062 | 61.5737 | 0.23948 | 61.5004 | -0.033101 | 0.034501 | 61.6577 | -0.001436 | 61.4496 | 62.8128 | 62.6643 | 62.5966 | 62.5423 | 62.7866 | 62.7674 | 62.8296 | 123.0972 | 61.7629 | 123.0238 | 61.4903 | 61.5579 | 123.1812 | 61.522 | 122.9731 | 61.5392 | 61.5752 | 61.4659 | 61.5018
2850.0781 | 123.3902 | -61.528 | 61.5875 | 1.271 | 1.1133 | 1.0548 | 1.0189 | 1.2769 | 1.2393 | 1.297 | 61.5783 | 0.2349 | 61.5096 | -0.046838 | 0.034501 | 61.6531 | -0.006014 | 61.4542 | 62.799 | 62.6414 | 62.5828 | 62.5469 | 62.8049 | 62.7674 | 62.825 | 123.1063 | 61.7629 | 123.0376 | 61.4812 | 61.5625 | 123.1812 | 61.522 | 122.9822 | 61.5438 | 61.5843 | 61.4751 | 61.5156
2851.0625 | 123.2895 | -61.5509 | 61.6196 | 1.1474 | 1.1133 | 1.064 | 1.0051 | 1.2769 | 1.3813 | 1.1734 | 61.5737 | 0.2349 | 61.5096 | -0.03768 | 0.039079 | 61.6577 | -0.006014 | 61.4542 | 62.6983 | 62.6642 | 62.6149 | 62.556 | 62.8278 | 62.9322 | 62.7243 | 123.1246 | 61.7858 | 123.0605 | 61.5132 | 61.59 | 123.2086 | 61.5449 | 123.0051 | 61.5346 | 61.5797 | 61.4705 | 61.5156
2852.0625 | 123.3948 | -61.5463 | 61.5646 | 1.1199 | 1.0859 | 1.0319 | 0.96852 | 1.2632 | 1.363 | 1.1276 | 61.5737 | 0.24405 | 61.5004 | -0.03768 | 0.039079 | 61.6486 | 0.003143 | 61.4542 | 62.6663 | 62.6322 | 62.5782 | 62.5148 | 62.8095 | 62.9093 | 62.6739 | 123.1201 | 61.7904 | 123.0467 | 61.5086 | 61.5854 | 123.1949 | 61.5495 | 123.0006 | 61.5346 | 61.5706 | 61.4613 | 61.4973
2853.0938 | 123.3627 | -61.5234 | 61.5829 | 1.1337 | 1.0813 | 0.99529 | 0.96394 | 1.254 | 1.3355 | 1.1505 | 61.5737 | 0.23032 | 61.4821 | -0.03768 | 0.039079 | 61.6531 | -0.006014 | 61.4542 | 62.6571 | 62.6047 | 62.5187 | 62.4874 | 62.7774 | 62.8589 | 62.6739 | 123.0972 | 61.7538 | 123.0055 | 61.4858 | 61.5625 | 123.1766 | 61.5174 | 122.9777 | 61.5346 | 61.5797 | 61.443 | 61.4881
2854.0625 | 123.2758 | -61.5692 | 61.5875 | 1.2207 | 1.1271 | 1.0319 | 0.99599 | 1.2723 | 1.2164 | 1.2375 | 61.5783 | 0.23948 | 61.4775 | -0.042259 | 0.039079 | 61.6531 | -0.006014 | 61.4496 | 62.7899 | 62.6963 | 62.6011 | 62.5652 | 62.8415 | 62.7857 | 62.8067 | 123.1475 | 61.8087 | 123.0467 | 61.527 | 61.6083 | 123.2224 | 61.5632 | 123.0189 | 61.5392 | 61.5843 | 61.4384 | 61.4835
2855.0625 | 123.262 | -61.5601 | 61.6287 | 1.2527 | 1.1317 | 1.0457 | 1.0143 | 1.3044 | 1.2027 | 1.2695 | 61.5829 | 0.24405 | 61.4775 | -0.03768 | 0.039079 | 61.6531 | 0.003143 | 61.4451 | 62.8128 | 62.6917 | 62.6057 | 62.5744 | 62.8644 | 62.7628 | 62.8296 | 123.1429 | 61.8041 | 123.0376 | 61.5224 | 61.5991 | 123.2132 | 61.5632 | 123.0051 | 61.5438 | 61.5797 | 61.4384 | 61.4744
2856.0625 | 123.2803 | -61.5463 | 61.6379 | 1.1474 | 1.1317 | 1.0548 | 1.0418 | 1.3181 | 1.3126 | 1.1688 | 61.5783 | 0.23948 | 61.5096 | -0.03768 | 0.048236 | 61.6623 | 0.007721 | 61.4542 | 62.6937 | 62.678 | 62.6011 | 62.5881 | 62.8644 | 62.8589 | 62.7151 | 123.1246 | 61.7858 | 123.0559 | 61.5086 | 61.5946 | 123.2086 | 61.554 | 123.0006 | 61.5301 | 61.5706 | 61.4613 | 61.5018
2857.0781 | 123.2941 | -61.5784 | 61.6013 | 1.2115 | 1.1317 | 1.0273 | 1.0097 | 1.2357 | 1.1661 | 1.2237 | 61.5875 | 0.23948 | 61.5141 | -0.028522 | 0.039079 | 61.6623 | -0.001436 | 61.4496 | 62.7899 | 62.71 | 62.6057 | 62.5881 | 62.8141 | 62.7445 | 62.8021 | 123.1658 | 61.8178 | 123.0925 | 61.5498 | 61.6174 | 123.2407 | 61.5769 | 123.028 | 61.5484 | 61.5889 | 61.4751 | 61.5156
2858.0625 | 123.317 | -61.5372 | 61.6196 | 1.2115 | 1.1408 | 1.0136 | 1.0235 | 1.2586 | 1.1707 | 1.2375 | 61.5875 | 0.2349 | 61.5233 | -0.03768 | 0.034501 | 61.6577 | -0.001436 | 61.4496 | 62.7487 | 62.678 | 62.5508 | 62.5606 | 62.7958 | 62.7078 | 62.7747 | 123.1246 | 61.7721 | 123.0605 | 61.4995 | 61.5717 | 123.1949 | 61.5357 | 122.9868 | 61.553 | 61.5889 | 61.4888 | 61.5247
2859.0625 | 123.349 | -61.5646 | 61.5692 | 1.2252 | 1.15 | 1.0182 | 1.028 | 1.2586 | 1.1752 | 1.2329 | 61.5829 | 0.2349 | 61.5187 | -0.03768 | 0.029923 | 61.6577 | -0.006014 | 61.4496 | 62.7899 | 62.7146 | 62.5828 | 62.5927 | 62.8232 | 62.7399 | 62.7975 | 123.1475 | 61.7995 | 123.0834 | 61.527 | 61.5946 | 123.2224 | 61.5586 | 123.0143 | 61.553 | 61.5889 | 61.4888 | 61.5247
2860.0625 | 123.3078 | -61.5463 | 61.6104 | 1.2664 | 1.182 | 1.0594 | 1.0509 | 1.286 | 1.2119 | 1.2741 | 61.5783 | 0.23032 | 61.5187 | -0.03768 | 0.039079 | 61.6623 | -0.006014 | 61.4588 | 62.8128 | 62.7283 | 62.6057 | 62.5973 | 62.8324 | 62.7582 | 62.8204 | 123.1246 | 61.7766 | 123.065 | 61.5086 | 61.5854 | 123.2086 | 61.5403 | 123.0051 | 61.5392 | 61.5843 | 61.4796 | 61.5247
2861.0625 | 123.2941 | -61.5463 | 61.6196 | 1.1337 | 1.1225 | 1.0228 | 1.0189 | 1.2632 | 1.308 | 1.1413 | 61.5783 | 0.2349 | 61.4958 | -0.033101 | 0.039079 | 61.6577 | 0.003143 | 61.4496 | 62.68 | 62.6688 | 62.5691 | 62.5652 | 62.8095 | 62.8543 | 62.6877 | 123.1246 | 61.7812 | 123.0421 | 61.5132 | 61.5854 | 123.204 | 61.5495 | 122.996 | 61.5392 | 61.5752 | 61.4567 | 61.4927
2862.0781 | 123.2941 | -61.5509 | 61.6196 | 1.1199 | 1.1179 | 0.99987 | 0.99141 | 1.2632 | 1.3172 | 1.1322 | 61.5829 | 0.23948 | 61.4775 | -0.028522 | 0.039079 | 61.6531 | -0.001436 | 61.4542 | 62.6708 | 62.6688 | 62.5508 | 62.5423 | 62.8141 | 62.8681 | 62.6831 | 123.1338 | 61.7904 | 123.0284 | 61.5224 | 61.59 | 123.204 | 61.5495 | 123.0051 | 61.5438 | 61.5843 | 61.4384 | 61.4789
2863.0625 | 123.3902 | -61.5326 | 61.6013 | 1.1154 | 1.1088 | 0.95866 | 0.98683 | 1.2723 | 1.3401 | 1.123 | 61.5875 | 0.23948 | 61.4775 | -0.033101 | 0.043657 | 61.6577 | 0.003143 | 61.4496 | 62.648 | 62.6414 | 62.4913 | 62.5194 | 62.8049 | 62.8727 | 62.6556 | 123.1201 | 61.7721 | 123.0101 | 61.4995 | 61.5763 | 123.1903 | 61.5357 | 122.9822 | 61.5438 | 61.5843 | 61.4339 | 61.4744
2864.0625 | 123.3215 | -61.5417 | 61.5921 | 1.239 | 1.1133 | 0.94951 | 1.0097 | 1.2723 | 1.1936 | 1.2512 | 61.5783 | 0.23948 | 61.4912 | -0.028522 | 0.034501 | 61.6531 | 0.003143 | 61.4496 | 62.7807 | 62.6551 | 62.4913 | 62.5515 | 62.8141 | 62.7353 | 62.793 | 123.1201 | 61.7812 | 123.033 | 61.5132 | 61.5762 | 123.1949 | 61.5449 | 122.9914 | 61.5438 | 61.5752 | 61.4567 | 61.4881
2865.0625 | 123.2849 | -61.5372 | 61.6287 | 1.2664 | 1.1225 | 0.99987 | 1.028 | 1.2906 | 1.221 | 1.2878 | 61.5829 | 0.23948 | 61.5141 | -0.03768 | 0.034501 | 61.6531 | 0.003143 | 61.4496 | 62.8036 | 62.6597 | 62.537 | 62.5652 | 62.8278 | 62.7582 | 62.825 | 123.1201 | 61.7766 | 123.0513 | 61.4995 | 61.5717 | 123.1903 | 61.5403 | 122.9868 | 61.5484 | 61.5797 | 61.4796 | 61.511
2866.0625 | 123.4497 | -61.5555 | 61.5417 | 1.2939 | 1.1408 | 1.0365 | 1.0464 | 1.3272 | 1.2485 | 1.3107 | 61.5829 | 0.24405 | 61.5096 | -0.03768 | 0.043657 | 61.6531 | 0.007721 | 61.4496 | 62.8494 | 62.6963 | 62.592 | 62.6018 | 62.8827 | 62.804 | 62.8662 | 123.1384 | 61.7995 | 123.065 | 61.5178 | 61.5991 | 123.2086 | 61.5632 | 123.0051 | 61.5392 | 61.5752 | 61.4659 | 61.5018
2867.0625 | 123.3627 | -61.5463 | 61.5646 | 1.3077 | 1.1683 | 1.0411 | 1.0647 | 1.3364 | 1.2668 | 1.3199 | 61.5829 | 0.23948 | 61.505 | -0.03768 | 0.039079 | 61.6623 | -0.001436 | 61.4588 | 62.854 | 62.7146 | 62.5874 | 62.611 | 62.8827 | 62.8131 | 62.8662 | 123.1292 | 61.7858 | 123.0513 | 61.5086 | 61.5854 | 123.2086 | 61.5449 | 123.0051 | 61.5438 | 61.5843 | 61.4659 | 61.5064
2868.0625 | 123.2803 | -61.5372 | 61.6104 | 1.2985 | 1.1729 | 1.0731 | 1.0647 | 1.3181 | 1.2531 | 1.3199 | 61.5829 | 0.23948 | 61.5141 | -0.03768 | 0.034501 | 61.6623 | -0.001436 | 61.4588 | 62.8357 | 62.71 | 62.6103 | 62.6018 | 62.8553 | 62.7902 | 62.8571 | 123.1201 | 61.7766 | 123.0513 | 61.4995 | 61.5717 | 123.1995 | 61.5357 | 122.996 | 61.5484 | 61.5843 | 61.4796 | 61.5156
2869.0625 | 123.3948 | -61.5417 | 61.5829 | 1.2939 | 1.1683 | 1.064 | 1.0464 | 1.2815 | 1.2531 | 1.3199 | 61.5737 | 0.24405 | 61.505 | -0.033101 | 0.034501 | 61.6623 | -0.001436 | 61.4542 | 62.8357 | 62.71 | 62.6057 | 62.5881 | 62.8232 | 62.7948 | 62.8616 | 123.1155 | 61.7858 | 123.0467 | 61.5086 | 61.5762 | 123.204 | 61.5403 | 122.996 | 61.5392 | 61.5752 | 61.4705 | 61.5064
2870.0625 | 123.2849 | -61.5555 | 61.615 | 1.3489 | 1.2232 | 1.1052 | 1.1059 | 1.2998 | 1.3126 | 1.3657 | 61.5691 | 0.2349 | 61.4729 | -0.03768 | 0.034501 | 61.6669 | -0.006014 | 61.4588 | 62.9043 | 62.7787 | 62.6607 | 62.6614 | 62.8553 | 62.8681 | 62.9212 | 123.1246 | 61.7904 | 123.0284 | 61.5178 | 61.59 | 123.2224 | 61.5495 | 123.0143 | 61.5346 | 61.5752 | 61.4384 | 61.4789
2871.0625 | 123.3673 | -61.5326 | 61.5555 | 1.3077 | 1.1774 | 1.0731 | 1.0647 | 1.254 | 1.2805 | 1.329 | 61.5691 | 0.23032 | 61.4775 | -0.03768 | 0.039079 | 61.6577 | -0.001436 | 61.4405 | 62.8402 | 62.71 | 62.6057 | 62.5973 | 62.7866 | 62.8131 | 62.8616 | 123.1017 | 61.7629 | 123.0101 | 61.4949 | 61.5717 | 123.1903 | 61.5312 | 122.9731 | 61.5301 | 61.5706 | 61.4384 | 61.4789
2872.0625 | 123.3994 | -61.5143 | 61.5463 | 1.3122 | 1.2049 | 1.096 | 1.0601 | 1.2632 | 1.2622 | 1.3336 | 61.5737 | 0.23948 | 61.4684 | -0.03768 | 0.039079 | 61.6623 | -0.001436 | 61.4496 | 62.8265 | 62.7192 | 62.6103 | 62.5744 | 62.7774 | 62.7765 | 62.8479 | 123.088 | 61.7538 | 122.9826 | 61.4766 | 61.5534 | 123.1766 | 61.5128 | 122.9639 | 61.5346 | 61.5752 | 61.4293 | 61.4698
2873.0625 | 123.2346 | -61.5738 | 61.5875 | 1.3031 | 1.2095 | 1.0686 | 1.0647 | 1.2586 | 1.2531 | 1.3199 | 61.5783 | 0.2349 | 61.4958 | -0.033101 | 0.039079 | 61.6623 | -0.006014 | 61.4496 | 62.8769 | 62.7833 | 62.6423 | 62.6385 | 62.8324 | 62.8269 | 62.8937 | 123.1521 | 61.8087 | 123.0696 | 61.5407 | 61.6129 | 123.2361 | 61.5678 | 123.0234 | 61.5392 | 61.5843 | 61.4567 | 61.5018
2874.0625 | 123.3078 | -61.5784 | 61.5509 | 1.3214 | 1.2141 | 1.0869 | 1.0784 | 1.254 | 1.276 | 1.3382 | 61.5829 | 0.24405 | 61.505 | -0.042259 | 0.034501 | 61.6623 | -0.006014 | 61.4542 | 62.8998 | 62.7924 | 62.6652 | 62.6568 | 62.8324 | 62.8543 | 62.9166 | 123.1613 | 61.8224 | 123.0833 | 61.5361 | 61.6129 | 123.2407 | 61.5724 | 123.0326 | 61.5484 | 61.5889 | 61.4705 | 61.511
2875.0625 | 123.2895 | -61.5417 | 61.6104 | 1.3168 | 1.2095 | 1.064 | 1.0692 | 1.2494 | 1.2714 | 1.3336 | 61.5875 | 0.2349 | 61.5096 | -0.042259 | 0.029923 | 61.6623 | -0.001436 | 61.4496 | 62.8586 | 62.7512 | 62.6057 | 62.611 | 62.7912 | 62.8131 | 62.8754 | 123.1292 | 61.7766 | 123.0513 | 61.4995 | 61.5717 | 123.204 | 61.5403 | 122.9914 | 61.5575 | 61.5889 | 61.4796 | 61.511
2876.0938 | 123.349 | -61.528 | 61.5692 | 1.3305 | 1.2278 | 1.1281 | 1.0738 | 1.2677 | 1.2897 | 1.3519 | 61.5783 | 0.24405 | 61.5096 | -0.03768 | 0.039079 | 61.6577 | 0.003143 | 61.4542 | 62.8586 | 62.7558 | 62.6561 | 62.6018 | 62.7958 | 62.8177 | 62.88 | 123.1063 | 61.7721 | 123.0376 | 61.4903 | 61.5671 | 123.1857 | 61.5312 | 122.9822 | 61.5392 | 61.5752 | 61.4705 | 61.5064
2877.0625 | 123.317 | -61.5921 | 61.5967 | 1.326 | 1.2232 | 1.1235 | 1.0692 | 1.2448 | 1.2851 | 1.3428 | 61.5737 | 0.23948 | 61.4912 | -0.046838 | 0.034501 | 61.6623 | -0.006014 | 61.4542 | 62.9181 | 62.8153 | 62.7156 | 62.6613 | 62.8369 | 62.8772 | 62.9349 | 123.1658 | 61.8316 | 123.0833 | 61.5453 | 61.6266 | 123.2544 | 61.5861 | 123.0463 | 61.5392 | 61.5797 | 61.4567 | 61.4973
2878.0625 | 123.2529 | -61.5601 | 61.615 | 1.3397 | 1.2324 | 1.1189 | 1.0738 | 1.2586 | 1.2897 | 1.3474 | 61.5783 | 0.23948 | 61.4729 | -0.042259 | 0.039079 | 61.6577 | 0.003143 | 61.4588 | 62.8998 | 62.7924 | 62.679 | 62.6339 | 62.8186 | 62.8498 | 62.9074 | 123.1384 | 61.7995 | 123.033 | 61.5178 | 61.5991 | 123.2178 | 61.5632 | 123.0189 | 61.5392 | 61.5752 | 61.4339 | 61.4698
2879.0938 | 123.3582 | -61.5784 | 61.5463 | 1.3305 | 1.2599 | 1.1372 | 1.0967 | 1.2632 | 1.2805 | 1.3474 | 61.5737 | 0.23032 | 61.5187 | -0.03768 | 0.043657 | 61.6577 | -0.006014 | 61.4496 | 62.9089 | 62.8382 | 62.7156 | 62.6751 | 62.8415 | 62.8589 | 62.9257 | 123.1521 | 61.8087 | 123.0971 | 61.5407 | 61.622 | 123.2361 | 61.5724 | 123.028 | 61.5301 | 61.5797 | 61.4751 | 61.5247
2880.0625 | 123.2574 | -61.5784 | 61.5555 | 1.2985 | 1.2324 | 1.0869 | 1.0647 | 1.2311 | 1.2439 | 1.3062 | 61.5783 | 0.24863 | 61.5141 | -0.033101 | 0.034501 | 61.6577 | -0.001436 | 61.4588 | 62.8769 | 62.8108 | 62.6652 | 62.643 | 62.8095 | 62.8223 | 62.8845 | 123.1567 | 61.827 | 123.0925 | 61.5453 | 61.6129 | 123.2361 | 61.5769 | 123.0372 | 61.5438 | 61.5797 | 61.4796 | 61.5156
2881.0625 | 123.381 | -61.5463 | 61.5372 | 1.3077 | 1.2415 | 1.1006 | 1.0464 | 1.2311 | 1.2622 | 1.3199 | 61.5737 | 0.2349 | 61.505 | -0.03768 | 0.034501 | 61.6623 | -0.010593 | 61.4496 | 62.854 | 62.7879 | 62.6469 | 62.5927 | 62.7774 | 62.8086 | 62.8662 | 123.1201 | 61.7812 | 123.0513 | 61.5086 | 61.5808 | 123.2086 | 61.5357 | 122.996 | 61.5392 | 61.5843 | 61.4705 | 61.5156
2882.0625 | 123.2803 | -61.5738 | 61.5646 | 1.3351 | 1.2736 | 1.1464 | 1.0692 | 1.254 | 1.2805 | 1.3474 | 61.5691 | 0.23032 | 61.4821 | -0.042259 | 0.039079 | 61.6623 | 0.003143 | 61.4542 | 62.9089 | 62.8474 | 62.7202 | 62.643 | 62.8278 | 62.8543 | 62.9212 | 123.1429 | 61.8041 | 123.0559 | 61.5315 | 61.6129 | 123.2361 | 61.5769 | 123.028 | 61.5301 | 61.566 | 61.443 | 61.4789
2883.125 | 123.262 | -61.5692 | 61.6241 | 1.2893 | 1.2553 | 1.1464 | 1.0555 | 1.2448 | 1.2393 | 1.3016 | 61.5783 | 0.2349 | 61.5096 | -0.03768 | 0.034501 | 61.676 | -0.006014 | 61.4496 | 62.8586 | 62.8245 | 62.7156 | 62.6247 | 62.8141 | 62.8086 | 62.8708 | 123.1475 | 61.8041 | 123.0788 | 61.5315 | 61.6037 | 123.2452 | 61.5632 | 123.0189 | 61.5438 | 61.5843 | 61.4751 | 61.5156
2884.0625 | 123.4314 | -61.5189 | 61.5555 | 1.2985 | 1.269 | 1.1601 | 1.0418 | 1.2906 | 1.2485 | 1.3107 | 61.5829 | 0.23948 | 61.505 | -0.03768 | 0.039079 | 61.6715 | -0.010593 | 61.4542 | 62.8174 | 62.7879 | 62.679 | 62.5606 | 62.8095 | 62.7674 | 62.8296 | 123.1017 | 61.7583 | 123.0238 | 61.4812 | 61.5579 | 123.1903 | 61.5083 | 122.9731 | 61.5438 | 61.5935 | 61.4659 | 61.5156
2885.0625 | 123.3902 | -61.5234 | 61.5829 | 1.2893 | 1.2553 | 1.1464 | 1.0464 | 1.2998 | 1.2439 | 1.3107 | 61.5783 | 0.24405 | 61.5187 | -0.03768 | 0.039079 | 61.6623 | -0.001436 | 61.4405 | 62.8128 | 62.7787 | 62.6698 | 62.5698 | 62.8232 | 62.7674 | 62.8342 | 123.1017 | 61.7675 | 123.0422 | 61.4858 | 61.5625 | 123.1857 | 61.522 | 122.9639 | 61.5392 | 61.5797 | 61.4796 | 61.5202
2886.0625 | 123.2254 | -61.5555 | 61.5738 | 1.3031 | 1.2599 | 1.1464 | 1.0601 | 1.2952 | 1.2622 | 1.3199 | 61.5737 | 0.23948 | 61.505 | -0.03768 | 0.029923 | 61.6669 | -0.006014 | 61.4451 | 62.8586 | 62.8153 | 62.7019 | 62.6156 | 62.8507 | 62.8177 | 62.8754 | 123.1292 | 61.795 | 123.0605 | 61.5178 | 61.5854 | 123.2224 | 61.5495 | 123.0006 | 61.5438 | 61.5797 | 61.4751 | 61.511
2887.0625 | 123.4039 | -61.5234 | 61.5555 | 1.2024 | 1.2415 | 1.151 | 1.0692 | 1.2815 | 1.4316 | 1.2192 | 61.5737 | 0.23032 | 61.5004 | -0.03768 | 0.039079 | 61.6577 | 0.003143 | 61.4496 | 62.7258 | 62.765 | 62.6744 | 62.5927 | 62.8049 | 62.9551 | 62.7426 | 123.0972 | 61.7538 | 123.0238 | 61.4858 | 61.5625 | 123.1812 | 61.5266 | 122.9731 | 61.5346 | 61.5706 | 61.4613 | 61.4973
2888.0781 | 123.4268 | -61.5555 | 61.5555 | 1.3351 | 1.2873 | 1.1555 | 1.1059 | 1.2952 | 1.2851 | 1.3474 | 61.5646 | 0.2349 | 61.4775 | -0.03768 | 0.029923 | 61.6623 | -0.001436 | 61.4542 | 62.8906 | 62.8428 | 62.711 | 62.6614 | 62.8507 | 62.8406 | 62.9028 | 123.1201 | 61.7904 | 123.033 | 61.5178 | 61.5854 | 123.2178 | 61.554 | 123.0097 | 61.5346 | 61.566 | 61.4476 | 61.4789
2889.1094 | 123.3215 | -61.5509 | 61.5829 | 1.3489 | 1.2919 | 1.1693 | 1.0967 | 1.2723 | 1.3034 | 1.3611 | 61.5783 | 0.23948 | 61.4729 | -0.03768 | 0.034501 | 61.6623 | 0.003143 | 61.4634 | 62.8998 | 62.8428 | 62.7202 | 62.6476 | 62.8232 | 62.8543 | 62.912 | 123.1292 | 61.7904 | 123.0238 | 61.5132 | 61.5854 | 123.2132 | 61.554 | 123.0143 | 61.5438 | 61.5752 | 61.4384 | 61.4698
2890.0625 | 123.4222 | -61.4914 | 61.6013 | 1.3534 | 1.2873 | 1.1968 | 1.1104 | 1.2998 | 1.2989 | 1.3657 | 61.5691 | 0.24405 | 61.4775 | -0.042259 | 0.043657 | 61.6669 | 0.003143 | 61.4634 | 62.8448 | 62.7787 | 62.6881 | 62.6018 | 62.7912 | 62.7903 | 62.8571 | 123.0605 | 61.7354 | 122.9689 | 61.4491 | 61.5351 | 123.1583 | 61.4945 | 122.9548 | 61.5255 | 61.566 | 61.4339 | 61.4744
2891.0625 | 123.4222 | -61.5372 | 61.5692 | 1.3489 | 1.2828 | 1.1647 | 1.1059 | 1.3044 | 1.3034 | 1.3611 | 61.5783 | 0.23948 | 61.5004 | -0.042259 | 0.039079 | 61.6577 | 0.003143 | 61.4588 | 62.886 | 62.8199 | 62.7019 | 62.643 | 62.8415 | 62.8406 | 62.8983 | 123.1155 | 61.7766 | 123.0376 | 61.4949 | 61.5762 | 123.1949 | 61.5403 | 122.996 | 61.5392 | 61.5752 | 61.4613 | 61.4973
2892.0625 | 123.2941 | -61.5372 | 61.6058 | 1.3489 | 1.2873 | 1.1327 | 1.1059 | 1.3272 | 1.3034 | 1.3611 | 61.5829 | 0.23948 | 61.5096 | -0.046838 | 0.034501 | 61.6577 | -0.001436 | 61.4588 | 62.886 | 62.8245 | 62.6698 | 62.643 | 62.8644 | 62.8406 | 62.8983 | 123.1201 | 61.7766 | 123.0467 | 61.4903 | 61.5717 | 123.1949 | 61.5357 | 122.996 | 61.5484 | 61.5843 | 61.4751 | 61.511
2893.0625 | 123.3353 | -61.5143 | 61.5967 | 1.3763 | 1.3194 | 1.1784 | 1.1517 | 1.3593 | 1.3401 | 1.4023 | 61.5737 | 0.23948 | 61.5096 | -0.03768 | 0.034501 | 61.6577 | 0.007721 | 61.4588 | 62.8906 | 62.8337 | 62.6927 | 62.6659 | 62.8736 | 62.8543 | 62.9166 | 123.088 | 61.7538 | 123.0238 | 61.4766 | 61.5488 | 123.172 | 61.522 | 122.9731 | 61.5392 | 61.566 | 61.4751 | 61.5018
2894.0625 | 123.3536 | -61.5601 | 61.5738 | 1.3672 | 1.3057 | 1.1418 | 1.1517 | 1.3547 | 1.3217 | 1.384 | 61.5691 | 0.23948 | 61.4775 | -0.03768 | 0.039079 | 61.6669 | -0.006014 | 61.4634 | 62.9272 | 62.8657 | 62.7019 | 62.7117 | 62.9148 | 62.8818 | 62.944 | 123.1292 | 61.7995 | 123.0376 | 61.5224 | 61.5991 | 123.2269 | 61.554 | 123.0234 | 61.5301 | 61.5752 | 61.4384 | 61.4835
2895.0625 | 123.3078 | -61.5646 | 61.6058 | 1.4175 | 1.3698 | 1.2151 | 1.2112 | 1.4371 | 1.3767 | 1.4343 | 61.5691 | 0.24405 | 61.4775 | -0.03768 | 0.039079 | 61.6669 | -0.001436 | 61.4542 | 62.9822 | 62.9344 | 62.7797 | 62.7758 | 63.0018 | 62.9413 | 62.999 | 123.1338 | 61.8087 | 123.0421 | 61.527 | 61.6037 | 123.2315 | 61.5632 | 123.0189 | 61.5301 | 61.5706 | 61.4384 | 61.4789
2896.0625 | 123.3673 | -61.5509 | 61.6058 | 1.3901 | 1.324 | 1.1968 | 1.1791 | 1.428 | 1.3401 | 1.4069 | 61.5691 | 0.2349 | 61.5141 | -0.033101 | 0.034501 | 61.6669 | 0.003143 | 61.4588 | 62.941 | 62.8749 | 62.7477 | 62.73 | 62.9789 | 62.891 | 62.9578 | 123.1201 | 61.7858 | 123.065 | 61.5178 | 61.5854 | 123.2178 | 61.554 | 123.0097 | 61.5346 | 61.566 | 61.4796 | 61.511
2897.0938 | 123.349 | -61.5738 | 61.5601 | 1.3901 | 1.3331 | 1.2105 | 1.1745 | 1.3913 | 1.3355 | 1.3977 | 61.5783 | 0.2349 | 61.505 | -0.03768 | 0.043657 | 61.6623 | -0.001436 | 61.4542 | 62.9639 | 62.9069 | 62.7843 | 62.7483 | 62.9651 | 62.9093 | 62.9715 | 123.1521 | 61.8087 | 123.0788 | 61.5361 | 61.6174 | 123.2361 | 61.5724 | 123.028 | 61.5346 | 61.5797 | 61.4613 | 61.5064
2898.0625 | 123.2941 | -61.5372 | 61.615 | 1.3718 | 1.3377 | 1.1876 | 1.17 | 1.3959 | 1.3263 | 1.384 | 61.5737 | 0.2349 | 61.4775 | -0.042259 | 0.039079 | 61.6623 | -0.001436 | 61.4634 | 62.9089 | 62.8749 | 62.7248 | 62.7071 | 62.9331 | 62.8635 | 62.9212 | 123.1109 | 61.7721 | 123.0147 | 61.4949 | 61.5762 | 123.1995 | 61.5357 | 123.0006 | 61.5346 | 61.5752 | 61.4384 | 61.4789
2899.0625 | 123.4177 | -61.528 | 61.5372 | 1.3809 | 1.3469 | 1.1876 | 1.1471 | 1.4005 | 1.3401 | 1.3977 | 61.5646 | 0.23948 | 61.4867 | -0.03768 | 0.034501 | 61.6715 | 0.003143 | 61.4588 | 62.9089 | 62.8749 | 62.7156 | 62.6751 | 62.9285 | 62.8681 | 62.9257 | 123.0926 | 61.7675 | 123.0147 | 61.4903 | 61.5625 | 123.1995 | 61.5312 | 122.9868 | 61.5301 | 61.5614 | 61.4522 | 61.4835
2900.0625 | 123.4268 | -61.5509 | 61.5601 | 1.413 | 1.3926 | 1.2471 | 1.1654 | 1.3776 | 1.3584 | 1.4252 | 61.5691 | 0.24863 | 61.4958 | -0.033101 | 0.039079 | 61.6669 | -0.001436 | 61.4588 | 62.9639 | 62.9436 | 62.798 | 62.7163 | 62.9285 | 62.9093 | 62.9761 | 123.1201 | 61.7995 | 123.0467 | 61.5178 | 61.59 | 123.2178 | 61.5495 | 123.0097 | 61.5301 | 61.5706 | 61.4567 | 61.4973
2901.0625 | 123.3307 | -61.5692 | 61.5784 | 1.3901 | 1.3972 | 1.2746 | 1.1745 | 1.3959 | 1.3401 | 1.416 | 61.5783 | 0.23948 | 61.5096 | -0.03768 | 0.034501 | 61.6715 | -0.001436 | 61.4588 | 62.9593 | 62.9664 | 62.8438 | 62.7438 | 62.9651 | 62.9093 | 62.9852 | 123.1475 | 61.8087 | 123.0788 | 61.5315 | 61.6037 | 123.2407 | 61.5678 | 123.028 | 61.5438 | 61.5797 | 61.4751 | 61.511
2902.0781 | 123.3582 | -61.5646 | 61.5372 | 1.3901 | 1.4018 | 1.2288 | 1.1425 | 1.4142 | 1.3446 | 1.4023 | 61.5737 | 0.24405 | 61.5004 | -0.03768 | 0.039079 | 61.6715 | -0.001436 | 61.4588 | 62.9547 | 62.9664 | 62.7934 | 62.7071 | 62.9789 | 62.9093 | 62.9669 | 123.1384 | 61.8087 | 123.065 | 61.527 | 61.6037 | 123.2361 | 61.5632 | 123.0234 | 61.5346 | 61.5752 | 61.4613 | 61.5018
2903.0625 | 123.4177 | -61.5234 | 61.5784 | 1.3809 | 1.4018 | 1.2563 | 1.1425 | 1.4234 | 1.3355 | 1.3977 | 61.5783 | 0.2349 | 61.4958 | -0.03768 | 0.048236 | 61.6715 | -0.001436 | 61.4634 | 62.9043 | 62.9252 | 62.7797 | 62.6659 | 62.9468 | 62.8589 | 62.9212 | 123.1017 | 61.7583 | 123.0193 | 61.4858 | 61.5717 | 123.1949 | 61.522 | 122.9868 | 61.5301 | 61.5797 | 61.4476 | 61.4973
2904.1094 | 123.381 | -61.5463 | 61.5646 | 1.326 | 1.411 | 1.27 | 1.1654 | 1.4097 | 1.2851 | 1.503 | 61.5691 | 0.24405 | 61.4821 | -0.046838 | 0.029923 | 61.6669 | 0.003143 | 61.4588 | 62.8723 | 62.9573 | 62.8163 | 62.7117 | 62.956 | 62.8314 | 63.0493 | 123.1155 | 61.7904 | 123.0284 | 61.4995 | 61.5762 | 123.2132 | 61.5495 | 123.0051 | 61.5392 | 61.566 | 61.4522 | 61.4789
2905.0625 | 123.3765 | -61.5509 | 61.5509 | 1.3809 | 1.3972 | 1.2746 | 1.1745 | 1.3868 | 1.3401 | 1.4023 | 61.56 | 0.2349 | 61.4638 | -0.033101 | 0.039079 | 61.6669 | -0.006014 | 61.468 | 62.9318 | 62.9481 | 62.8255 | 62.7255 | 62.9377 | 62.891 | 62.9532 | 123.1109 | 61.7858 | 123.0147 | 61.5178 | 61.59 | 123.2178 | 61.5449 | 123.0189 | 61.5209 | 61.566 | 61.4247 | 61.4698
2906.0625 | 123.2574 | -61.5738 | 61.6241 | 1.3763 | 1.3881 | 1.2792 | 1.1654 | 1.3501 | 1.3309 | 1.3931 | 61.5691 | 0.24405 | 61.4775 | -0.03768 | 0.039079 | 61.6623 | 0.003143 | 61.4496 | 62.9501 | 62.9619 | 62.853 | 62.7392 | 62.9239 | 62.9047 | 62.9669 | 123.1429 | 61.8178 | 123.0513 | 61.5361 | 61.6129 | 123.2361 | 61.5769 | 123.0234 | 61.5301 | 61.566 | 61.4384 | 61.4744
2907.0625 | 123.381 | -61.5372 | 61.5646 | 1.3763 | 1.3789 | 1.2471 | 1.1379 | 1.3227 | 1.3217 | 1.3886 | 61.5646 | 0.2349 | 61.4958 | -0.03768 | 0.039079 | 61.6669 | -0.006014 | 61.4588 | 62.9135 | 62.9161 | 62.7843 | 62.6751 | 62.8598 | 62.8589 | 62.9257 | 123.1017 | 61.7721 | 123.033 | 61.4995 | 61.5762 | 123.204 | 61.5312 | 122.996 | 61.5255 | 61.5706 | 61.4567 | 61.5018
2908.0625 | 123.3536 | -61.5189 | 61.6058 | 1.3763 | 1.3698 | 1.2288 | 1.1288 | 1.3181 | 1.3263 | 1.3977 | 61.5691 | 0.24405 | 61.505 | -0.03768 | 0.034501 | 61.6669 | -0.001436 | 61.4634 | 62.8952 | 62.8886 | 62.7477 | 62.6476 | 62.837 | 62.8452 | 62.9166 | 123.088 | 61.7629 | 123.0238 | 61.4812 | 61.5534 | 123.1857 | 61.5174 | 122.9822 | 61.5346 | 61.5706 | 61.4705 | 61.5064
2909.1406 | 123.3536 | -61.5692 | 61.5417 | 1.3855 | 1.3881 | 1.2288 | 1.1425 | 1.3364 | 1.3446 | 1.4069 | 61.5783 | 0.24405 | 61.5141 | -0.042259 | 0.034501 | 61.6623 | 0.003143 | 61.4588 | 62.9547 | 62.9573 | 62.798 | 62.7117 | 62.9056 | 62.9139 | 62.9761 | 123.1475 | 61.8133 | 123.0833 | 61.527 | 61.6037 | 123.2315 | 61.5724 | 123.028 | 61.5438 | 61.5752 | 61.4796 | 61.511
2910.0625 | 123.3124 | -61.5509 | 61.5921 | 1.3809 | 1.3881 | 1.2196 | 1.1288 | 1.3364 | 1.3401 | 1.4115 | 61.5737 | 0.23948 | 61.5141 | -0.03768 | 0.039079 | 61.676 | -0.006014 | 61.4634 | 62.9318 | 62.939 | 62.7705 | 62.6797 | 62.8873 | 62.891 | 62.9624 | 123.1246 | 61.7904 | 123.065 | 61.5132 | 61.59 | 123.2269 | 61.5449 | 123.0143 | 61.5346 | 61.5797 | 61.4751 | 61.5202
2911.0625 | 123.3627 | -61.528 | 61.5829 | 1.4084 | 1.4018 | 1.2563 | 1.1562 | 1.3639 | 1.3584 | 1.416 | 61.5646 | 0.23948 | 61.4912 | -0.03768 | 0.043657 | 61.6623 | 0.003143 | 61.4634 | 62.9364 | 62.9298 | 62.7843 | 62.6843 | 62.8919 | 62.8864 | 62.944 | 123.0926 | 61.7675 | 123.0193 | 61.4903 | 61.5717 | 123.1903 | 61.5312 | 122.9914 | 61.5209 | 61.5614 | 61.4476 | 61.4881
2912.0625 | 123.3032 | -61.5875 | 61.6013 | 1.4221 | 1.4064 | 1.2517 | 1.1745 | 1.3685 | 1.3813 | 1.4389 | 61.5646 | 0.24405 | 61.4592 | -0.03768 | 0.039079 | 61.6715 | -0.006014 | 61.4588 | 63.0096 | 62.9939 | 62.8392 | 62.7621 | 62.956 | 62.9688 | 63.0264 | 123.1521 | 61.8316 | 123.0467 | 61.5498 | 61.6266 | 123.259 | 61.5815 | 123.0463 | 61.5255 | 61.5706 | 61.4201 | 61.4652
2913.0625 | 123.262 | -61.5784 | 61.6287 | 1.4313 | 1.3972 | 1.2334 | 1.17 | 1.3547 | 1.3767 | 1.4435 | 61.5646 | 0.24405 | 61.4638 | -0.033101 | 0.034501 | 61.6669 | -0.001436 | 61.4542 | 63.0096 | 62.9756 | 62.8117 | 62.7483 | 62.9331 | 62.9551 | 63.0219 | 123.1429 | 61.8224 | 123.0421 | 61.5453 | 61.6129 | 123.2452 | 61.5769 | 123.0326 | 61.5301 | 61.566 | 61.4293 | 61.4652
2914.0938 | 123.2986 | -61.5692 | 61.6287 | 1.4542 | 1.4293 | 1.27 | 1.1929 | 1.3776 | 1.3996 | 1.471 | 61.5646 | 0.24863 | 61.4821 | -0.033101 | 0.029923 | 61.6669 | -0.001436 | 61.4634 | 63.0234 | 62.9985 | 62.8392 | 62.7621 | 62.9468 | 62.9688 | 63.0402 | 123.1338 | 61.8178 | 123.0513 | 61.5361 | 61.5991 | 123.2361 | 61.5678 | 123.0326 | 61.5346 | 61.566 | 61.4522 | 61.4835
2915.0625 | 123.2803 | -61.5784 | 61.6058 | 1.4633 | 1.4522 | 1.2654 | 1.1974 | 1.3776 | 1.4133 | 1.471 | 61.5691 | 0.2349 | 61.5004 | -0.03768 | 0.043657 | 61.6577 | 0.003143 | 61.468 | 63.0417 | 63.0305 | 62.8438 | 62.7758 | 62.956 | 62.9917 | 63.0493 | 123.1475 | 61.8133 | 123.0788 | 61.5407 | 61.622 | 123.2361 | 61.5815 | 123.0463 | 61.5255 | 61.566 | 61.4567 | 61.4973
2916.0781 | 123.4131 | -61.5417 | 61.5646 | 1.4267 | 1.4247 | 1.2654 | 1.1791 | 1.3547 | 1.3813 | 1.4435 | 61.5646 | 0.23948 | 61.505 | -0.03768 | 0.039079 | 61.6669 | -0.010593 | 61.4634 | 62.9684 | 62.9664 | 62.8072 | 62.7209 | 62.8965 | 62.923 | 62.9853 | 123.1063 | 61.7812 | 123.0467 | 61.5041 | 61.5808 | 123.2086 | 61.5312 | 123.0051 | 61.5255 | 61.5752 | 61.4659 | 61.5156
2917.0625 | 123.3444 | -61.5738 | 61.528 | 1.4175 | 1.4201 | 1.2563 | 1.1791 | 1.3364 | 1.3721 | 1.4343 | 61.5646 | 0.23948 | 61.4775 | -0.046838 | 0.034501 | 61.6715 | -0.001436 | 61.4634 | 62.9913 | 62.9939 | 62.8301 | 62.7529 | 62.9102 | 62.9459 | 63.0081 | 123.1384 | 61.8133 | 123.0513 | 61.527 | 61.6083 | 123.2452 | 61.5724 | 123.0372 | 61.5301 | 61.566 | 61.443 | 61.4789
2918.0938 | 123.3124 | -61.5555 | 61.5646 | 1.4267 | 1.4293 | 1.2837 | 1.1791 | 1.3456 | 1.3767 | 1.4343 | 61.5783 | 0.23948 | 61.4729 | -0.033101 | 0.043657 | 61.6715 | 0.003143 | 61.4634 | 62.9822 | 62.9848 | 62.8392 | 62.7346 | 62.901 | 62.9322 | 62.9898 | 123.1338 | 61.795 | 123.0284 | 61.5224 | 61.5991 | 123.2269 | 61.5586 | 123.0189 | 61.5346 | 61.5752 | 61.4293 | 61.4698
2919.0625 | 123.3994 | -61.5417 | 61.5326 | 1.4221 | 1.4339 | 1.2837 | 1.1562 | 1.3364 | 1.3767 | 1.4389 | 61.5691 | 0.23948 | 61.4912 | -0.042259 | 0.034501 | 61.6715 | 0.003143 | 61.4542 | 62.9639 | 62.9756 | 62.8255 | 62.698 | 62.8782 | 62.9184 | 62.9807 | 123.1109 | 61.7812 | 123.033 | 61.4995 | 61.5762 | 123.2132 | 61.5449 | 122.996 | 61.5346 | 61.566 | 61.4567 | 61.4881
2920.0938 | 123.2483 | -61.5417 | 61.6104 | 1.413 | 1.443 | 1.3295 | 1.17 | 1.3547 | 1.3813 | 1.4435 | 61.5691 | 0.23948 | 61.5187 | -0.03768 | 0.043657 | 61.6715 | 0.003143 | 61.4634 | 62.9547 | 62.9848 | 62.8713 | 62.7117 | 62.8965 | 62.923 | 62.9853 | 123.1109 | 61.7812 | 123.0605 | 61.5041 | 61.5854 | 123.2132 | 61.5449 | 123.0051 | 61.5255 | 61.566 | 61.4751 | 61.5156
2921.0625 | 123.317 | -61.5646 | 61.5784 | 1.4175 | 1.4522 | 1.357 | 1.1929 | 1.3822 | 1.3767 | 1.4389 | 61.5646 | 0.24405 | 61.4912 | -0.03768 | 0.034501 | 61.676 | 0.003143 | 61.4634 | 62.9822 | 63.0168 | 62.9216 | 62.7575 | 62.9468 | 62.9413 | 63.0036 | 123.1292 | 61.8087 | 123.0559 | 61.527 | 61.5991 | 123.2407 | 61.5678 | 123.028 | 61.5301 | 61.5614 | 61.4567 | 61.4881
2922.1094 | 123.3948 | -61.5326 | 61.5692 | 1.413 | 1.443 | 1.2609 | 1.1608 | 1.3685 | 1.3675 | 1.4343 | 61.5646 | 0.24405 | 61.4775 | -0.03768 | 0.043657 | 61.6715 | 0.003143 | 61.4542 | 62.9455 | 62.9756 | 62.7934 | 62.6934 | 62.901 | 62.9001 | 62.9669 | 123.0972 | 61.7766 | 123.0101 | 61.4949 | 61.5763 | 123.204 | 61.5357 | 122.9868 | 61.5209 | 61.5614 | 61.4339 | 61.4744
2923.0625 | 123.3353 | -61.5646 | 61.5646 | 1.445 | 1.4705 | 1.3066 | 1.1791 | 1.4051 | 1.395 | 1.4664 | 61.5737 | 0.24405 | 61.505 | -0.03768 | 0.034501 | 61.6669 | -0.001436 | 61.4634 | 63.0096 | 63.0351 | 62.8713 | 62.7438 | 62.9697 | 62.9596 | 63.031 | 123.1384 | 61.8087 | 123.0696 | 61.527 | 61.5991 | 123.2315 | 61.5632 | 123.028 | 61.5392 | 61.5752 | 61.4705 | 61.5064
2924.0938 | 123.3994 | -61.5601 | 61.5372 | 1.4221 | 1.4613 | 1.2837 | 1.1791 | 1.3913 | 1.3767 | 1.4481 | 61.5829 | 0.2349 | 61.505 | -0.046838 | 0.029923 | 61.6715 | -0.001436 | 61.4588 | 62.9822 | 63.0214 | 62.8438 | 62.7392 | 62.9514 | 62.9367 | 63.0081 | 123.1429 | 61.795 | 123.065 | 61.5132 | 61.59 | 123.2315 | 61.5586 | 123.0189 | 61.553 | 61.5843 | 61.4751 | 61.5064
2925.0625 | 123.3719 | -61.5601 | 61.5738 | 1.3992 | 1.4659 | 1.325 | 1.1883 | 1.4325 | 1.3584 | 1.4206 | 61.5646 | 0.23948 | 61.4821 | -0.03768 | 0.034501 | 61.6715 | 0.003143 | 61.4588 | 62.9593 | 63.026 | 62.885 | 62.7483 | 62.9926 | 62.9184 | 62.9807 | 123.1246 | 61.7995 | 123.0421 | 61.5224 | 61.5946 | 123.2315 | 61.5632 | 123.0189 | 61.5301 | 61.5614 | 61.4476 | 61.4789
2926.0781 | 123.349 | -61.5463 | 61.5601 | 1.4038 | 1.4934 | 1.3295 | 1.2158 | 1.3959 | 1.3584 | 1.4252 | 61.5691 | 0.23948 | 61.4638 | -0.03768 | 0.039079 | 61.6669 | -0.001436 | 61.4588 | 62.9501 | 63.0397 | 62.8759 | 62.7621 | 62.9422 | 62.9047 | 62.9715 | 123.1155 | 61.7858 | 123.0101 | 61.5086 | 61.5854 | 123.2132 | 61.5449 | 123.0051 | 61.5301 | 61.5706 | 61.4247 | 61.4652
2927.0625 | 123.1384 | -61.6013 | 61.5189 | 1.4221 | 1.498 | 1.3478 | 1.2066 | 1.4188 | 1.3767 | 1.4343 | 61.5737 | 0.24405 | 61.5004 | -0.042259 | 0.039079 | 61.6715 | -0.001436 | 61.4588 | 63.0234 | 63.0992 | 62.9491 | 62.8079 | 63.0201 | 62.9779 | 63.0356 | 123.175 | 61.8453 | 123.1017 | 61.559 | 61.6403 | 123.2727 | 61.5998 | 123.0601 | 61.5346 | 61.5752 | 61.4613 | 61.5018
2928.0625 | 123.3398 | -61.5509 | 61.5784 | 1.3718 | 1.5254 | 1.2975 | 1.2203 | 1.4325 | 1.3217 | 1.5808 | 61.5691 | 0.2349 | 61.5004 | -0.042259 | 0.039079 | 61.676 | -0.006014 | 61.4634 | 62.9227 | 63.0763 | 62.8484 | 62.7712 | 62.9834 | 62.8727 | 63.1317 | 123.1201 | 61.7858 | 123.0513 | 61.5086 | 61.59 | 123.2269 | 61.5449 | 123.0143 | 61.5301 | 61.5752 | 61.4613 | 61.5064
2929.0781 | 123.3032 | -61.5921 | 61.6058 | 1.4679 | 1.5437 | 1.4119 | 1.2615 | 1.46 | 1.4316 | 1.4939 | 61.5737 | 0.2349 | 61.5004 | -0.042259 | 0.034501 | 61.6715 | 0.003143 | 61.4588 | 63.06 | 63.1359 | 63.004 | 62.8536 | 63.0521 | 63.0237 | 63.086 | 123.1658 | 61.827 | 123.0925 | 61.5498 | 61.6266 | 123.2636 | 61.5952 | 123.0509 | 61.5392 | 61.5706 | 61.4659 | 61.4973
2930.0938 | 123.3353 | -61.5875 | 61.6058 | 1.4999 | 1.5666 | 1.4303 | 1.2707 | 1.4783 | 1.4545 | 1.5168 | 61.5691 | 0.2349 | 61.4775 | -0.033101 | 0.039079 | 61.676 | 0.003143 | 61.4588 | 63.0875 | 63.1542 | 63.0178 | 62.8582 | 63.0658 | 63.042 | 63.1043 | 123.1567 | 61.8224 | 123.065 | 61.5544 | 61.6266 | 123.2636 | 61.5907 | 123.0463 | 61.5301 | 61.566 | 61.4384 | 61.4744
2931.0625 | 123.262 | -61.6058 | 61.5555 | 1.4816 | 1.5529 | 1.4074 | 1.2478 | 1.4646 | 1.4362 | 1.4984 | 61.5691 | 0.2349 | 61.4592 | -0.033101 | 0.034501 | 61.676 | -0.001436 | 61.4588 | 63.0875 | 63.1587 | 63.0132 | 62.8536 | 63.0704 | 63.042 | 63.1043 | 123.175 | 61.8407 | 123.065 | 61.5727 | 61.6403 | 123.2819 | 61.6044 | 123.0646 | 61.5346 | 61.5706 | 61.4247 | 61.4606
2932.0625 | 123.3261 | -61.5692 | 61.5372 | 1.5091 | 1.585 | 1.4394 | 1.257 | 1.4921 | 1.4637 | 1.5213 | 61.5508 | 0.24405 | 61.4592 | -0.03768 | 0.034501 | 61.6669 | -0.006014 | 61.4588 | 63.0783 | 63.1542 | 63.0086 | 62.8262 | 63.0613 | 63.0329 | 63.0905 | 123.12 | 61.8133 | 123.0284 | 61.5315 | 61.6037 | 123.2361 | 61.5632 | 123.028 | 61.5163 | 61.5568 | 61.4247 | 61.4652
2933.0625 | 123.3307 | -61.5738 | 61.5692 | 1.5366 | 1.6262 | 1.4852 | 1.2844 | 1.5424 | 1.4911 | 1.5625 | 61.56 | 0.2349 | 61.4684 | -0.033101 | 0.034501 | 61.6715 | 0.003143 | 61.4725 | 63.1104 | 63.2 | 63.059 | 62.8582 | 63.1162 | 63.0649 | 63.1363 | 123.1338 | 61.8087 | 123.0421 | 61.5407 | 61.6083 | 123.2452 | 61.5769 | 123.0463 | 61.5255 | 61.5568 | 61.4339 | 61.4652
2934.0938 | 123.3902 | -61.5738 | 61.5189 | 1.5595 | 1.6307 | 1.4898 | 1.2707 | 1.5607 | 1.5095 | 1.5717 | 61.5554 | 0.2349 | 61.4867 | -0.03768 | 0.043657 | 61.6806 | -0.001436 | 61.468 | 63.1333 | 63.2045 | 63.0636 | 62.8445 | 63.1345 | 63.0833 | 63.1455 | 123.1292 | 61.8087 | 123.0605 | 61.5361 | 61.6174 | 123.2544 | 61.5724 | 123.0418 | 61.5118 | 61.5568 | 61.443 | 61.4881
2935.0625 | 123.2437 | -61.5509 | 61.5601 | 1.5457 | 1.6033 | 1.4715 | 1.2661 | 1.5973 | 1.5049 | 1.5625 | 61.5737 | 0.2349 | 61.5004 | -0.03768 | 0.039079 | 61.676 | -0.006014 | 61.4725 | 63.0966 | 63.1542 | 63.0224 | 62.817 | 63.1483 | 63.0558 | 63.1134 | 123.1246 | 61.7858 | 123.0513 | 61.5132 | 61.59 | 123.2269 | 61.5449 | 123.0234 | 61.5346 | 61.5797 | 61.4613 | 61.5064
2936.0625 | 123.3261 | -61.5692 | 61.5601 | 1.5183 | 1.5575 | 1.4486 | 1.2615 | 1.6065 | 1.4728 | 1.5351 | 61.5691 | 0.24405 | 61.5096 | -0.03768 | 0.039079 | 61.6715 | -0.001436 | 61.468 | 63.0875 | 63.1267 | 63.0178 | 62.8308 | 63.1757 | 63.042 | 63.1043 | 123.1384 | 61.8133 | 123.0788 | 61.5315 | 61.6083 | 123.2407 | 61.5678 | 123.0372 | 61.5301 | 61.5706 | 61.4705 | 61.511
2937.0625 | 123.3582 | -61.5784 | 61.5234 | 1.4679 | 1.5575 | 1.3936 | 1.2432 | 1.5928 | 1.4179 | 1.6266 | 61.5646 | 0.2349 | 61.4958 | -0.03768 | 0.034501 | 61.6715 | -0.001436 | 61.4634 | 63.0463 | 63.1359 | 62.972 | 62.8216 | 63.1711 | 62.9963 | 63.205 | 123.1429 | 61.8133 | 123.0742 | 61.5407 | 61.6129 | 123.2498 | 61.5769 | 123.0418 | 61.5301 | 61.566 | 61.4613 | 61.4973
2938.0625 | 123.2895 | -61.5784 | 61.5829 | 1.5183 | 1.6216 | 1.4486 | 1.2799 | 1.6385 | 1.4683 | 1.6816 | 61.5646 | 0.23948 | 61.4775 | -0.033101 | 0.034501 | 61.6806 | -0.001436 | 61.468 | 63.0966 | 63.2 | 63.0269 | 62.8582 | 63.2169 | 63.0466 | 63.2599 | 123.1429 | 61.8178 | 123.0559 | 61.5453 | 61.6129 | 123.259 | 61.5769 | 123.0463 | 61.5301 | 61.566 | 61.443 | 61.4789
2939.0625 | 123.3765 | -61.5921 | 61.5326 | 1.4771 | 1.6079 | 1.4119 | 1.2753 | 1.6019 | 1.4316 | 1.677 | 61.5646 | 0.24405 | 61.4592 | -0.033101 | 0.034501 | 61.676 | 0.003143 | 61.4634 | 63.0692 | 63.2 | 63.004 | 62.8674 | 63.194 | 63.0237 | 63.2691 | 123.1567 | 61.8362 | 123.0513 | 61.559 | 61.6266 | 123.2681 | 61.5952 | 123.0555 | 61.5301 | 61.5614 | 61.4247 | 61.4561
2940.0781 | 123.3582 | -61.5326 | 61.5829 | 1.5045 | 1.6124 | 1.4303 | 1.2936 | 1.5836 | 1.4591 | 1.5168 | 61.5646 | 0.24405 | 61.4592 | -0.03768 | 0.039079 | 61.676 | 0.003143 | 61.4634 | 63.0371 | 63.145 | 62.9629 | 62.8262 | 63.1162 | 62.9917 | 63.0493 | 123.0972 | 61.7766 | 122.9918 | 61.4949 | 61.5717 | 123.2086 | 61.5357 | 122.996 | 61.5255 | 61.5614 | 61.4201 | 61.4561
2941.0625 | 123.3032 | -61.5829 | 61.5601 | 1.4908 | 1.5987 | 1.4211 | 1.2661 | 1.5561 | 1.4408 | 1.503 | 61.5646 | 0.24405 | 61.4592 | -0.03768 | 0.029923 | 61.676 | 0.003143 | 61.468 | 63.0737 | 63.1816 | 63.004 | 62.8491 | 63.1391 | 63.0237 | 63.086 | 123.1475 | 61.827 | 123.0421 | 61.5453 | 61.6129 | 123.259 | 61.5861 | 123.0509 | 61.5346 | 61.5614 | 61.4293 | 61.4561
2942.0625 | 123.349 | -61.5646 | 61.5509 | 1.5183 | 1.585 | 1.4577 | 1.2707 | 1.579 | 1.4774 | 1.5396 | 61.5508 | 0.23948 | 61.4867 | -0.03768 | 0.034501 | 61.6715 | 0.003143 | 61.468 | 63.0829 | 63.1496 | 63.0224 | 62.8353 | 63.1437 | 63.042 | 63.1043 | 123.1155 | 61.8041 | 123.0513 | 61.527 | 61.5991 | 123.2361 | 61.5678 | 123.0326 | 61.5163 | 61.5477 | 61.4522 | 61.4835
2943.0938 | 123.2895 | -61.5875 | 61.5509 | 1.5274 | 1.6033 | 1.4669 | 1.2982 | 1.6157 | 1.4866 | 1.5488 | 61.5691 | 0.23948 | 61.4912 | -0.042259 | 0.034501 | 61.6806 | 0.003143 | 61.4725 | 63.1149 | 63.1908 | 63.0544 | 62.8857 | 63.2032 | 63.0741 | 63.1363 | 123.1567 | 61.827 | 123.0788 | 61.5453 | 61.622 | 123.2681 | 61.5907 | 123.0601 | 61.5346 | 61.566 | 61.4567 | 61.4881
2944.0625 | 123.2346 | -61.6058 | 61.5189 | 1.5457 | 1.6079 | 1.476 | 1.2982 | 1.6248 | 1.4957 | 1.5671 | 61.5554 | 0.23948 | 61.4821 | -0.03768 | 0.034501 | 61.6669 | -0.001436 | 61.468 | 63.1516 | 63.2137 | 63.0819 | 62.904 | 63.2307 | 63.1016 | 63.1729 | 123.1612 | 61.8453 | 123.0879 | 61.5682 | 61.6403 | 123.2727 | 61.6044 | 123.0738 | 61.5209 | 61.5568 | 61.4476 | 61.4835
2945.0625 | 123.3536 | -61.5921 | 61.5738 | 1.564 | 1.6216 | 1.4944 | 1.3165 | 1.6385 | 1.5095 | 1.5808 | 61.5554 | 0.24405 | 61.4638 | -0.028522 | 0.039079 | 61.676 | 0.003143 | 61.4817 | 63.1561 | 63.2137 | 63.0865 | 62.9086 | 63.2307 | 63.1016 | 63.1729 | 123.1475 | 61.8362 | 123.0559 | 61.5636 | 61.6312 | 123.2681 | 61.5952 | 123.0738 | 61.5163 | 61.5523 | 61.4247 | 61.4606
2946.0938 | 123.3353 | -61.5784 | 61.5509 | 1.5778 | 1.6399 | 1.4989 | 1.3394 | 1.6523 | 1.5232 | 1.5854 | 61.5508 | 0.23948 | 61.4592 | -0.028522 | 0.034501 | 61.6806 | 0.003143 | 61.4725 | 63.1561 | 63.2183 | 63.0773 | 62.9177 | 63.2307 | 63.1016 | 63.1638 | 123.1292 | 61.8178 | 123.0376 | 61.5498 | 61.6129 | 123.259 | 61.5815 | 123.0509 | 61.5163 | 61.5477 | 61.4247 | 61.4561
2947.0625 | 123.2849 | -61.5967 | 61.5646 | 1.5503 | 1.6399 | 1.4852 | 1.3394 | 1.6477 | 1.4957 | 1.5625 | 61.5554 | 0.23948 | 61.45 | -0.03768 | 0.034501 | 61.6715 | -0.006014 | 61.468 | 63.147 | 63.2366 | 63.0819 | 62.9361 | 63.2444 | 63.0924 | 63.1592 | 123.1521 | 61.8362 | 123.0467 | 61.559 | 61.6312 | 123.2681 | 61.5907 | 123.0646 | 61.5209 | 61.5614 | 61.4155 | 61.4561
2948.0625 | 123.3078 | -61.5829 | 61.5601 | 1.5549 | 1.6536 | 1.4944 | 1.3485 | 1.6477 | 1.5186 | 1.5671 | 61.5646 | 0.23948 | 61.4958 | -0.033101 | 0.039079 | 61.676 | -0.001436 | 61.4725 | 63.1378 | 63.2366 | 63.0773 | 62.9315 | 63.2307 | 63.1016 | 63.1501 | 123.1475 | 61.8224 | 123.0788 | 61.5498 | 61.622 | 123.259 | 61.5815 | 123.0555 | 61.5255 | 61.566 | 61.4567 | 61.4973
2949.0938 | 123.3444 | -61.5646 | 61.5829 | 1.5869 | 1.6582 | 1.5081 | 1.3623 | 1.6752 | 1.5369 | 1.5946 | 61.5646 | 0.23948 | 61.4912 | -0.03768 | 0.034501 | 61.676 | -0.006014 | 61.468 | 63.1516 | 63.2229 | 63.0727 | 62.9269 | 63.2398 | 63.1016 | 63.1592 | 123.1292 | 61.8041 | 123.0559 | 61.527 | 61.5991 | 123.2407 | 61.5586 | 123.0326 | 61.5301 | 61.5706 | 61.4567 | 61.4973
2950.0625 | 123.2712 | -61.6013 | 61.5829 | 1.6327 | 1.6903 | 1.5585 | 1.3806 | 1.721 | 1.5827 | 1.6449 | 61.56 | 0.24863 | 61.4729 | -0.03768 | 0.039079 | 61.6806 | -0.006014 | 61.4771 | 63.234 | 63.2915 | 63.1597 | 62.9818 | 63.3222 | 63.184 | 63.2462 | 123.1612 | 61.8499 | 123.0742 | 61.5636 | 61.6403 | 123.2819 | 61.5952 | 123.0784 | 61.5209 | 61.566 | 61.4339 | 61.4789
2951.0938 | 123.3124 | -61.5601 | 61.5967 | 1.6556 | 1.6949 | 1.5814 | 1.3897 | 1.7347 | 1.6102 | 1.6724 | 61.5554 | 0.2349 | 61.45 | -0.03768 | 0.039079 | 61.676 | 0.003143 | 61.4725 | 63.2157 | 63.2549 | 63.1414 | 62.9498 | 63.2947 | 63.1702 | 63.2325 | 123.1155 | 61.795 | 123.0101 | 61.5224 | 61.5991 | 123.2361 | 61.5632 | 123.0326 | 61.5163 | 61.5523 | 61.411 | 61.4469
2952.0625 | 123.262 | -61.5784 | 61.5463 | 1.6922 | 1.7269 | 1.618 | 1.4126 | 1.7667 | 1.6468 | 1.7045 | 61.5508 | 0.2349 | 61.4546 | -0.03768 | 0.034501 | 61.6943 | -0.001436 | 61.4817 | 63.2706 | 63.3053 | 63.1964 | 62.991 | 63.3451 | 63.2252 | 63.2828 | 123.1292 | 61.8133 | 123.033 | 61.5407 | 61.6129 | 123.2727 | 61.5769 | 123.0601 | 61.5163 | 61.5523 | 61.4201 | 61.4561
2953.0938 | 123.3261 | -61.6058 | 61.5555 | 1.7518 | 1.7635 | 1.6867 | 1.4538 | 1.7759 | 1.7063 | 1.7731 | 61.5508 | 0.24405 | 61.4867 | -0.03768 | 0.043657 | 61.6852 | -0.006014 | 61.4817 | 63.3576 | 63.3694 | 63.2925 | 63.0597 | 63.3817 | 63.3122 | 63.379 | 123.1567 | 61.8499 | 123.0925 | 61.5682 | 61.6495 | 123.291 | 61.5998 | 123.0875 | 61.5072 | 61.5568 | 61.443 | 61.4927
2954.0625 | 123.3627 | -61.6013 | 61.5784 | 1.7472 | 1.7498 | 1.6729 | 1.4493 | 1.7805 | 1.6972 | 1.764 | 61.5554 | 0.23948 | 61.4821 | -0.042259 | 0.039079 | 61.6943 | -0.001436 | 61.4817 | 63.3484 | 63.3511 | 63.2742 | 63.0505 | 63.3817 | 63.2984 | 63.3652 | 123.1567 | 61.8407 | 123.0833 | 61.559 | 61.6403 | 123.2956 | 61.5998 | 123.083 | 61.5163 | 61.5568 | 61.443 | 61.4835
2955.0938 | 123.2986 | -61.5967 | 61.6058 | 1.7518 | 1.7544 | 1.6821 | 1.4584 | 1.8034 | 1.6972 | 1.7594 | 61.56 | 0.24405 | 61.4867 | -0.033101 | 0.039079 | 61.6943 | -0.001436 | 61.4725 | 63.3484 | 63.3511 | 63.2788 | 63.0551 | 63.4 | 63.2939 | 63.3561 | 123.1567 | 61.8407 | 123.0833 | 61.5636 | 61.6358 | 123.291 | 61.5952 | 123.0692 | 61.5209 | 61.5614 | 61.4476 | 61.4881
2956.0625 | 123.2986 | -61.5692 | 61.5555 | 1.7426 | 1.7544 | 1.6729 | 1.4493 | 1.8308 | 1.6972 | 1.7686 | 61.5463 | 0.24405 | 61.4775 | -0.042259 | 0.034501 | 61.6806 | 0.003143 | 61.4863 | 63.3118 | 63.3236 | 63.2421 | 63.0185 | 63.4 | 63.2664 | 63.3378 | 123.1155 | 61.8133 | 123.0467 | 61.527 | 61.6037 | 123.2498 | 61.5724 | 123.0555 | 61.5118 | 61.5431 | 61.443 | 61.4744
2957.1094 | 123.4039 | -61.5463 | 61.5509 | 1.738 | 1.759 | 1.6775 | 1.463 | 1.8446 | 1.6972 | 1.7548 | 61.5463 | 0.2349 | 61.4546 | -0.033101 | 0.043657 | 61.6943 | -0.001436 | 61.4725 | 63.2843 | 63.3053 | 63.2238 | 63.0093 | 63.3909 | 63.2435 | 63.3011 | 123.0926 | 61.7812 | 123.0009 | 61.5132 | 61.59 | 123.2407 | 61.5449 | 123.0189 | 61.5026 | 61.5477 | 61.411 | 61.4561
2958.0625 | 123.2849 | -61.5967 | 61.5555 | 1.7563 | 1.7452 | 1.6912 | 1.4905 | 1.8812 | 1.7109 | 1.7731 | 61.5463 | 0.2349 | 61.4546 | -0.042259 | 0.034501 | 61.6852 | -0.006014 | 61.4863 | 63.353 | 63.3419 | 63.2879 | 63.0871 | 63.4779 | 63.3076 | 63.3698 | 123.1429 | 61.8316 | 123.0513 | 61.5544 | 61.6312 | 123.2819 | 61.5907 | 123.083 | 61.5118 | 61.5523 | 61.4201 | 61.4606
2959.0625 | 123.3536 | -61.5509 | 61.5509 | 1.7838 | 1.7544 | 1.7187 | 1.4767 | 1.8812 | 1.7338 | 1.796 | 61.5463 | 0.24405 | 61.4455 | -0.042259 | 0.039079 | 61.6898 | -0.006014 | 61.4817 | 63.3347 | 63.3053 | 63.2696 | 63.0276 | 63.4321 | 63.2847 | 63.3469 | 123.0972 | 61.795 | 122.9964 | 61.5086 | 61.59 | 123.2407 | 61.5449 | 123.0326 | 61.5072 | 61.5523 | 61.4064 | 61.4515
2960.0781 | 123.2941 | -61.5875 | 61.5555 | 1.8296 | 1.7864 | 1.7691 | 1.5271 | 1.9407 | 1.7887 | 1.8601 | 61.5463 | 0.24405 | 61.4775 | -0.033101 | 0.043657 | 61.6943 | -0.001436 | 61.4863 | 63.4171 | 63.374 | 63.3566 | 63.1146 | 63.5282 | 63.3763 | 63.4476 | 123.1338 | 61.8316 | 123.065 | 61.5544 | 61.6312 | 123.2819 | 61.5861 | 123.0738 | 61.5026 | 61.5477 | 61.4339 | 61.4789
2961.0625 | 123.2895 | -61.6058 | 61.5417 | 1.8387 | 1.7773 | 1.7691 | 1.5408 | 1.9499 | 1.7933 | 1.851 | 61.5417 | 0.23948 | 61.4867 | -0.042259 | 0.043657 | 61.6898 | -0.006014 | 61.4863 | 63.4446 | 63.3831 | 63.3749 | 63.1467 | 63.5557 | 63.3992 | 63.4568 | 123.1475 | 61.8453 | 123.0925 | 61.5636 | 61.6495 | 123.2956 | 61.5998 | 123.0921 | 61.498 | 61.5477 | 61.443 | 61.4927
2962.0625 | 123.3444 | -61.5463 | 61.5646 | 1.8113 | 1.791 | 1.7416 | 1.5591 | 1.9499 | 1.7521 | 1.97 | 61.5463 | 0.24405 | 61.4912 | -0.033101 | 0.039079 | 61.6898 | -0.001436 | 61.4863 | 63.3576 | 63.3373 | 63.2879 | 63.1055 | 63.4962 | 63.2984 | 63.5163 | 123.0926 | 61.7904 | 123.0376 | 61.5132 | 61.5854 | 123.2361 | 61.5449 | 123.0326 | 61.5072 | 61.5477 | 61.4522 | 61.4927
2963.0625 | 123.3353 | -61.6196 | 61.5326 | 1.8479 | 1.7956 | 1.7691 | 1.5408 | 1.9361 | 1.7933 | 1.8555 | 61.5463 | 0.23948 | 61.4775 | -0.03768 | 0.029923 | 61.6943 | -0.006014 | 61.4817 | 63.4675 | 63.4152 | 63.3886 | 63.1604 | 63.5557 | 63.4129 | 63.4751 | 123.1658 | 61.859 | 123.0971 | 61.5819 | 61.6495 | 123.3139 | 61.6136 | 123.1013 | 61.5163 | 61.5523 | 61.4476 | 61.4835
2964.0938 | 123.2483 | -61.5921 | 61.5784 | 1.8296 | 1.7864 | 1.7599 | 1.55 | 1.927 | 1.7796 | 1.8784 | 61.5463 | 0.24405 | 61.4775 | -0.033101 | 0.039079 | 61.6989 | -0.001436 | 61.4909 | 63.4217 | 63.3785 | 63.352 | 63.1421 | 63.5191 | 63.3717 | 63.4705 | 123.1384 | 61.8362 | 123.0696 | 61.559 | 61.6312 | 123.291 | 61.5907 | 123.083 | 61.5072 | 61.5477 | 61.4384 | 61.4789
2965.0625 | 123.2803 | -61.6104 | 61.5601 | 1.8616 | 1.8185 | 1.8057 | 1.5729 | 1.959 | 1.8208 | 1.8876 | 61.5371 | 0.23948 | 61.4729 | -0.042259 | 0.034501 | 61.7035 | -0.001436 | 61.4863 | 63.4721 | 63.4289 | 63.4161 | 63.1833 | 63.5694 | 63.4312 | 63.498 | 123.1475 | 61.8499 | 123.0833 | 61.5682 | 61.6449 | 123.3139 | 61.609 | 123.0967 | 61.5026 | 61.5385 | 61.4384 | 61.4744
2966.0625 | 123.3124 | -61.5875 | 61.5372 | 1.9212 | 1.8505 | 1.8515 | 1.6141 | 2.0048 | 1.8849 | 1.9425 | 61.5463 | 0.23948 | 61.4729 | -0.03768 | 0.039079 | 61.6943 | 0.003143 | 61.4954 | 63.5087 | 63.4381 | 63.439 | 63.2016 | 63.5923 | 63.4724 | 63.53 | 123.1338 | 61.827 | 123.0605 | 61.5498 | 61.6266 | 123.2819 | 61.5907 | 123.083 | 61.5072 | 61.5431 | 61.4339 | 61.4698
2967.1094 | 123.3307 | -61.5692 | 61.5967 | 1.8845 | 1.8047 | 1.8149 | 1.5912 | 1.9773 | 1.8391 | 1.9059 | 61.5371 | 0.2349 | 61.4729 | -0.042259 | 0.039079 | 61.7035 | 0.003143 | 61.4954 | 63.4537 | 63.374 | 63.3841 | 63.1604 | 63.5465 | 63.4083 | 63.4751 | 123.1063 | 61.8041 | 123.0421 | 61.527 | 61.6083 | 123.2727 | 61.5724 | 123.0646 | 61.498 | 61.534 | 61.4339 | 61.4698
2968.0625 | 123.2574 | -61.6104 | 61.5692 | 1.8845 | 1.7956 | 1.8149 | 1.5866 | 1.9636 | 1.8345 | 1.9013 | 61.5417 | 0.23948 | 61.4684 | -0.03768 | 0.034501 | 61.7035 | -0.001436 | 61.4863 | 63.4949 | 63.406 | 63.4253 | 63.197 | 63.574 | 63.4449 | 63.5117 | 123.1521 | 61.8499 | 123.0788 | 61.5727 | 61.6449 | 123.3139 | 61.609 | 123.0967 | 61.5072 | 61.5431 | 61.4339 | 61.4698
2969.0625 | 123.4039 | -61.5875 | 61.5189 | 1.8662 | 1.7818 | 1.8011 | 1.5591 | 1.9453 | 1.8208 | 1.8876 | 61.5371 | 0.2349 | 61.4729 | -0.03768 | 0.039079 | 61.6898 | 0.003143 | 61.4771 | 63.4537 | 63.3694 | 63.3887 | 63.1467 | 63.5328 | 63.4083 | 63.4751 | 123.1246 | 61.8224 | 123.0605 | 61.5498 | 61.6266 | 123.2773 | 61.5907 | 123.0646 | 61.498 | 61.534 | 61.4339 | 61.4698
2970.0781 | 123.3124 | -61.5646 | 61.5646 | 1.8754 | 1.7818 | 1.8011 | 1.5637 | 1.9682 | 1.8208 | 1.883 | 61.5417 | 0.23948 | 61.4729 | -0.033101 | 0.043657 | 61.6989 | -0.001436 | 61.4909 | 63.44 | 63.3465 | 63.3658 | 63.1284 | 63.5328 | 63.3854 | 63.4476 | 123.1063 | 61.8041 | 123.0376 | 61.5315 | 61.6083 | 123.2636 | 61.5632 | 123.0555 | 61.498 | 61.5431 | 61.4293 | 61.4744
2971.0625 | 123.381 | -61.5921 | 61.496 | 1.9074 | 1.791 | 1.8561 | 1.5912 | 2.0094 | 1.8712 | 1.9334 | 61.5371 | 0.23948 | 61.4684 | -0.042259 | 0.029923 | 61.6989 | -0.001436 | 61.4909 | 63.4995 | 63.3831 | 63.4482 | 63.1833 | 63.6015 | 63.4633 | 63.5255 | 123.1292 | 61.8316 | 123.0605 | 61.5498 | 61.622 | 123.291 | 61.5907 | 123.083 | 61.5072 | 61.5385 | 61.4384 | 61.4698
2972.1094 | 123.349 | -61.5738 | 61.5509 | 1.999 | 1.8551 | 1.9339 | 1.6232 | 2.0002 | 1.9627 | 2.0204 | 61.5371 | 0.23948 | 61.4592 | -0.042259 | 0.043657 | 61.7035 | 0.007721 | 61.4909 | 63.5728 | 63.4289 | 63.5077 | 63.197 | 63.574 | 63.5365 | 63.5941 | 123.1109 | 61.8133 | 123.033 | 61.5315 | 61.6174 | 123.2773 | 61.5815 | 123.0646 | 61.4934 | 61.5294 | 61.4155 | 61.4515
2973.0625 | 123.3948 | -61.5967 | 61.4914 | 2.0127 | 1.8643 | 1.9431 | 1.6187 | 1.9544 | 1.9627 | 2.0295 | 61.5417 | 0.24405 | 61.4638 | -0.042259 | 0.029923 | 61.7035 | -0.001436 | 61.4954 | 63.6094 | 63.4609 | 63.5397 | 63.2153 | 63.5511 | 63.5594 | 63.6262 | 123.1384 | 61.8407 | 123.0605 | 61.5544 | 61.6266 | 123.3002 | 61.5952 | 123.0921 | 61.5118 | 61.5431 | 61.4339 | 61.4652
2974.0625 | 123.2941 | -61.6196 | 61.5143 | 1.9669 | 1.8688 | 1.9019 | 1.6095 | 2.0735 | 1.9215 | 1.9975 | 61.5371 | 0.2349 | 61.4546 | -0.033101 | 0.029923 | 61.6989 | 0.003143 | 61.4863 | 63.5865 | 63.4884 | 63.5214 | 63.2291 | 63.693 | 63.5411 | 63.617 | 123.1567 | 61.8545 | 123.0742 | 61.5865 | 61.6495 | 123.3185 | 61.6227 | 123.1058 | 61.5072 | 61.534 | 61.4247 | 61.4515
2975.0781 | 123.2941 | -61.5875 | 61.5555 | 1.9853 | 1.8505 | 1.9064 | 1.6095 | 2.0689 | 1.9261 | 2.002 | 61.5417 | 0.24863 | 61.45 | -0.033101 | 0.034501 | 61.6989 | 0.003143 | 61.4954 | 63.5728 | 63.4381 | 63.494 | 63.197 | 63.6564 | 63.5136 | 63.5896 | 123.1292 | 61.8362 | 123.0376 | 61.5544 | 61.622 | 123.2864 | 61.5907 | 123.083 | 61.5072 | 61.5385 | 61.4155 | 61.4469
2976.0625 | 123.2712 | -61.6104 | 61.5234 | 1.9578 | 1.8597 | 1.8881 | 1.6187 | 2.0918 | 1.9078 | 1.9791 | 61.5371 | 0.23948 | 61.4455 | -0.042259 | 0.034501 | 61.7035 | -0.006014 | 61.4817 | 63.5682 | 63.4701 | 63.4985 | 63.2291 | 63.7022 | 63.5182 | 63.5896 | 123.1475 | 61.8499 | 123.0559 | 61.5682 | 61.6449 | 123.3139 | 61.6044 | 123.0921 | 61.5026 | 61.5431 | 61.411 | 61.4515
2977.1094 | 123.2986 | -61.5829 | 61.5417 | 1.999 | 1.8826 | 1.9293 | 1.6782 | 2.1559 | 1.949 | 2.0204 | 61.5371 | 0.24405 | 61.4409 | -0.03768 | 0.034501 | 61.6989 | -0.001436 | 61.5 | 63.5819 | 63.4655 | 63.5123 | 63.2611 | 63.7388 | 63.5319 | 63.6033 | 123.12 | 61.827 | 123.0238 | 61.5453 | 61.6174 | 123.2819 | 61.5815 | 123.083 | 61.5026 | 61.5385 | 61.4064 | 61.4423
2978.0625 | 123.3536 | -61.5784 | 61.5189 | 2.0127 | 1.8734 | 1.9431 | 1.6736 | 2.1559 | 1.9627 | 2.0341 | 61.5325 | 0.24863 | 61.4317 | -0.042259 | 0.034501 | 61.7081 | -0.006014 | 61.4909 | 63.5911 | 63.4518 | 63.5214 | 63.252 | 63.7342 | 63.5411 | 63.6125 | 123.1109 | 61.827 | 123.0101 | 61.5361 | 61.6129 | 123.2864 | 61.5724 | 123.0692 | 61.498 | 61.5385 | 61.3972 | 61.4377
2979.0625 | 123.4177 | -61.5829 | 61.5234 | 2.0494 | 1.8963 | 1.9843 | 1.7057 | 2.2016 | 1.9993 | 2.0707 | 61.5417 | 0.24405 | 61.4271 | -0.042259 | 0.039079 | 61.7035 | -0.001436 | 61.5 | 63.6323 | 63.4793 | 63.5672 | 63.2886 | 63.7846 | 63.5823 | 63.6537 | 123.1246 | 61.827 | 123.0101 | 61.5407 | 61.622 | 123.2864 | 61.5815 | 123.083 | 61.5026 | 61.5431 | 61.3881 | 61.4286
2980.0781 | 123.3124 | -61.5967 | 61.5326 | 2.0585 | 1.9146 | 1.9797 | 1.7148 | 2.22 | 2.0131 | 2.0753 | 61.5417 | 0.24405 | 61.4409 | -0.03768 | 0.034501 | 61.7035 | -0.001436 | 61.4954 | 63.6552 | 63.5113 | 63.5764 | 63.3115 | 63.8166 | 63.6098 | 63.672 | 123.1384 | 61.8407 | 123.0376 | 61.559 | 61.6312 | 123.3002 | 61.5952 | 123.0921 | 61.5072 | 61.5431 | 61.4064 | 61.4423
2981.0625 | 123.3948 | -61.615 | 61.5005 | 2.0677 | 1.9329 | 1.9934 | 1.7148 | 2.2016 | 2.0131 | 2.0844 | 61.5234 | 0.24405 | 61.4317 | -0.033101 | 0.039079 | 61.7081 | 0.003143 | 61.4909 | 63.6827 | 63.5479 | 63.6084 | 63.3298 | 63.8166 | 63.6281 | 63.6994 | 123.1384 | 61.859 | 123.0467 | 61.5819 | 61.6541 | 123.3231 | 61.6181 | 123.1058 | 61.4843 | 61.5202 | 61.3926 | 61.4286
2982.0625 | 123.3719 | -61.5921 | 61.5189 | 2.0814 | 1.9467 | 2.0117 | 1.7514 | 2.2795 | 2.036 | 2.0982 | 61.5234 | 0.2349 | 61.4226 | -0.042259 | 0.039079 | 61.7035 | 0.003143 | 61.4954 | 63.6735 | 63.5388 | 63.6038 | 63.3435 | 63.8716 | 63.6281 | 63.6903 | 123.1155 | 61.827 | 123.0147 | 61.5498 | 61.6312 | 123.2956 | 61.5952 | 123.0875 | 61.4843 | 61.5202 | 61.3835 | 61.4194
2983.0625 | 123.3902 | -61.5829 | 61.5463 | 2.0814 | 1.9604 | 2.0117 | 1.7194 | 2.133 | 2.0314 | 2.0982 | 61.5279 | 0.24863 | 61.4271 | -0.042259 | 0.034501 | 61.7081 | -0.001436 | 61.4954 | 63.6643 | 63.5434 | 63.5947 | 63.3023 | 63.7159 | 63.6143 | 63.6811 | 123.1109 | 61.8316 | 123.0101 | 61.5407 | 61.6174 | 123.291 | 61.5815 | 123.0784 | 61.4934 | 61.5294 | 61.3926 | 61.4286
2984.0938 | 123.2529 | -61.6104 | 61.5509 | 2.1089 | 1.9787 | 2.0255 | 1.7469 | 2.1787 | 2.0589 | 2.1211 | 61.5234 | 0.2349 | 61.4271 | -0.03768 | 0.029923 | 61.7035 | 0.003143 | 61.4909 | 63.7193 | 63.5892 | 63.6359 | 63.3573 | 63.7892 | 63.6693 | 63.7315 | 123.1338 | 61.8453 | 123.0376 | 61.5727 | 61.6403 | 123.3139 | 61.6136 | 123.1013 | 61.4934 | 61.5202 | 61.3972 | 61.424
2985.0625 | 123.3765 | -61.5967 | 61.496 | 2.0951 | 1.9604 | 2.0255 | 1.7469 | 2.1925 | 2.0406 | 2.1256 | 61.5279 | 0.23948 | 61.4271 | -0.03768 | 0.034501 | 61.7081 | -0.001436 | 61.4817 | 63.6918 | 63.5571 | 63.6222 | 63.3435 | 63.7892 | 63.6372 | 63.7223 | 123.1246 | 61.8362 | 123.0238 | 61.559 | 61.6312 | 123.3048 | 61.5952 | 123.0784 | 61.4934 | 61.5294 | 61.3926 | 61.4286
2986.0625 | 123.3444 | -61.5738 | 61.4822 | 2.118 | 2.0108 | 2.0484 | 1.7743 | 2.22 | 2.0772 | 2.1302 | 61.5371 | 0.23948 | 61.4226 | -0.042259 | 0.039079 | 61.7127 | 0.003143 | 61.4909 | 63.6918 | 63.5846 | 63.6222 | 63.3481 | 63.7937 | 63.651 | 63.704 | 123.1109 | 61.8133 | 122.9964 | 61.5315 | 61.6129 | 123.2865 | 61.5769 | 123.0646 | 61.498 | 61.534 | 61.3835 | 61.4194
2987.0625 | 123.3124 | -61.6013 | 61.5051 | 2.1226 | 2.0337 | 2.0621 | 1.7926 | 2.2612 | 2.0818 | 2.1348 | 61.5279 | 0.23948 | 61.4271 | -0.03768 | 0.043657 | 61.7081 | -0.001436 | 61.4954 | 63.7239 | 63.6349 | 63.6634 | 63.3939 | 63.8624 | 63.683 | 63.7361 | 123.1292 | 61.8407 | 123.0284 | 61.5636 | 61.6449 | 123.3093 | 61.5998 | 123.0967 | 61.4843 | 61.5294 | 61.3835 | 61.4286
2988.0781 | 123.2391 | -61.6287 | 61.5601 | 2.1318 | 2.0154 | 2.0621 | 1.7789 | 2.22 | 2.0818 | 2.1485 | 61.5279 | 0.24863 | 61.4317 | -0.03768 | 0.043657 | 61.7035 | -0.006014 | 61.5 | 63.7605 | 63.6441 | 63.6908 | 63.4076 | 63.8487 | 63.7105 | 63.7773 | 123.1567 | 61.8774 | 123.0605 | 61.591 | 61.6724 | 123.3322 | 61.6227 | 123.1287 | 61.4843 | 61.534 | 61.3881 | 61.4377
2989.0625 | 123.2574 | -61.6287 | 61.5555 | 2.1226 | 2.0337 | 2.0575 | 1.7698 | 2.2703 | 2.0772 | 2.1485 | 61.5279 | 0.23948 | 61.4271 | -0.033101 | 0.039079 | 61.7081 | 0.003143 | 61.4954 | 63.7513 | 63.6624 | 63.6863 | 63.3985 | 63.899 | 63.7059 | 63.7773 | 123.1567 | 61.8682 | 123.0559 | 61.5956 | 61.6678 | 123.3368 | 61.6319 | 123.1242 | 61.4889 | 61.5248 | 61.3881 | 61.424
2990.0938 | 123.4131 | -61.5921 | 61.5005 | 2.1226 | 2.0337 | 2.0484 | 1.7469 | 2.2703 | 2.0726 | 2.1348 | 61.5188 | 0.23948 | 61.4226 | -0.03768 | 0.039079 | 61.7035 | -0.006014 | 61.5 | 63.7147 | 63.6258 | 63.6405 | 63.339 | 63.8624 | 63.6647 | 63.7269 | 123.1109 | 61.8316 | 123.0147 | 61.5544 | 61.6312 | 123.2956 | 61.5861 | 123.0921 | 61.4797 | 61.5248 | 61.3835 | 61.4286
2991.0625 | 123.3902 | -61.6196 | 61.5189 | 2.1592 | 2.0428 | 2.0896 | 1.7652 | 2.3436 | 2.1092 | 2.1943 | 61.5234 | 0.24405 | 61.4271 | -0.03768 | 0.039079 | 61.7081 | 0.003143 | 61.5046 | 63.7788 | 63.6624 | 63.7091 | 63.3847 | 63.9631 | 63.7288 | 63.8139 | 123.1429 | 61.8636 | 123.0467 | 61.5819 | 61.6586 | 123.3276 | 61.6227 | 123.1242 | 61.4843 | 61.5202 | 61.3881 | 61.424
2992.0625 | 123.3673 | -61.5921 | 61.5097 | 2.1409 | 2.0199 | 2.0667 | 1.7606 | 2.2612 | 2.0909 | 2.144 | 61.5279 | 0.24405 | 61.418 | -0.042259 | 0.039079 | 61.7081 | -0.001436 | 61.4954 | 63.733 | 63.612 | 63.6588 | 63.3527 | 63.8533 | 63.683 | 63.7361 | 123.12 | 61.8362 | 123.0101 | 61.5498 | 61.6312 | 123.3002 | 61.5907 | 123.0875 | 61.4889 | 61.5294 | 61.3789 | 61.4194
2993.0625 | 123.3765 | -61.6104 | 61.5097 | 2.1226 | 2.0062 | 2.053 | 1.7652 | 2.3024 | 2.0818 | 2.144 | 61.5188 | 0.24405 | 61.4271 | -0.03768 | 0.039079 | 61.7127 | -0.001436 | 61.4954 | 63.733 | 63.6166 | 63.6634 | 63.3756 | 63.9128 | 63.6922 | 63.7544 | 123.1292 | 61.8545 | 123.0376 | 61.5727 | 61.6495 | 123.3231 | 61.609 | 123.1058 | 61.4797 | 61.5202 | 61.3881 | 61.4286
2994.0938 | 123.3353 | -61.5967 | 61.4868 | 2.1501 | 1.9971 | 2.0896 | 1.7469 | 2.2428 | 2.0955 | 2.1623 | 61.5234 | 0.23948 | 61.4271 | -0.033101 | 0.034501 | 61.7127 | -0.001436 | 61.4909 | 63.7468 | 63.5937 | 63.6863 | 63.3435 | 63.8395 | 63.6922 | 63.759 | 123.12 | 61.8362 | 123.0238 | 61.5636 | 61.6312 | 123.3093 | 61.5952 | 123.0875 | 61.4889 | 61.5248 | 61.3926 | 61.4286
2995.0625 | 123.3719 | -61.6013 | 61.5005 | 2.1592 | 2.0383 | 2.0896 | 1.756 | 2.2291 | 2.1138 | 2.1531 | 61.5188 | 0.23948 | 61.4226 | -0.042259 | 0.039079 | 61.7127 | 0.007721 | 61.5046 | 63.7605 | 63.6395 | 63.6908 | 63.3573 | 63.8304 | 63.7151 | 63.7544 | 123.12 | 61.8407 | 123.0238 | 61.559 | 61.6403 | 123.3139 | 61.609 | 123.1058 | 61.4797 | 61.5111 | 61.3835 | 61.4149
2996.0625 | 123.3673 | -61.5829 | 61.496 | 2.1959 | 2.0566 | 2.1216 | 1.7652 | 2.2428 | 2.1413 | 2.1302 | 61.5234 | 0.24405 | 61.4271 | -0.033101 | 0.034501 | 61.7081 | 0.003143 | 61.5046 | 63.7788 | 63.6395 | 63.7046 | 63.3481 | 63.8258 | 63.7242 | 63.7132 | 123.1063 | 61.827 | 123.0101 | 61.5498 | 61.6174 | 123.291 | 61.5861 | 123.0875 | 61.4889 | 61.5202 | 61.3926 | 61.424
2997.0625 | 123.3536 | -61.5875 | 61.5189 | 2.2279 | 2.0703 | 2.1628 | 1.7926 | 2.252 | 2.1733 | 2.2035 | 61.5279 | 0.24405 | 61.4226 | -0.03768 | 0.039079 | 61.7172 | -0.006014 | 61.5 | 63.8154 | 63.6578 | 63.7504 | 63.3802 | 63.8395 | 63.7609 | 63.791 | 123.1155 | 61.8316 | 123.0101 | 61.5498 | 61.6266 | 123.3048 | 61.5815 | 123.0875 | 61.4889 | 61.534 | 61.3835 | 61.4286
2998.0625 | 123.381 | -61.5875 | 61.496 | 2.2188 | 2.084 | 2.1491 | 1.8201 | 2.2932 | 2.1687 | 2.2401 | 61.5234 | 0.23032 | 61.4226 | -0.03768 | 0.034501 | 61.7172 | -0.001436 | 61.5046 | 63.8063 | 63.6716 | 63.7366 | 63.4076 | 63.8807 | 63.7563 | 63.8276 | 123.1109 | 61.8178 | 123.0101 | 61.5498 | 61.622 | 123.3048 | 61.5861 | 123.0921 | 61.4889 | 61.5248 | 61.3881 | 61.424
2999.0625 | 123.4085 | -61.615 | 61.5097 | 2.2325 | 2.0932 | 2.1628 | 1.8155 | 2.2795 | 2.1825 | 2.2401 | 61.5234 | 0.24405 | 61.4226 | -0.03768 | 0.039079 | 61.7172 | -0.006014 | 61.5046 | 63.8475 | 63.7082 | 63.7778 | 63.4305 | 63.8945 | 63.7975 | 63.8551 | 123.1384 | 61.859 | 123.0376 | 61.5773 | 61.6541 | 123.3322 | 61.609 | 123.1196 | 61.4843 | 61.5294 | 61.3835 | 61.4286
3000.0625 | 123.3902 | -61.6196 | 61.4868 | 2.2371 | 2.1024 | 2.1812 | 1.8384 | 2.2932 | 2.1871 | 2.2584 | 61.5142 | 0.23948 | 61.4226 | -0.03768 | 0.039079 | 61.7081 | 0.003143 | 61.5 | 63.8566 | 63.7219 | 63.8007 | 63.458 | 63.9128 | 63.8066 | 63.878 | 123.1338 | 61.859 | 123.0421 | 61.5819 | 61.6586 | 123.3276 | 61.6227 | 123.1196 | 61.4751 | 61.5111 | 61.3835 | 61.4194
3001.0625 | 123.3627 | -61.6013 | 61.496 | 2.2828 | 2.1069 | 2.2132 | 1.8751 | 2.2978 | 2.2283 | 2.2493 | 61.5234 | 0.23948 | 61.418 | -0.03768 | 0.039079 | 61.7127 | -0.001436 | 61.5046 | 63.8841 | 63.7082 | 63.8145 | 63.4763 | 63.899 | 63.8295 | 63.8505 | 123.1246 | 61.8407 | 123.0192 | 61.5636 | 61.6403 | 123.3139 | 61.5998 | 123.1058 | 61.4843 | 61.5248 | 61.3789 | 61.4194
3002.0625 | 123.4085 | -61.5601 | 61.5005 | 2.292 | 2.0978 | 2.2178 | 1.8659 | 2.2978 | 2.2374 | 2.2264 | 61.5234 | 0.2349 | 61.4226 | -0.033101 | 0.039079 | 61.7218 | 0.003143 | 61.5092 | 63.8521 | 63.6578 | 63.7778 | 63.426 | 63.8578 | 63.7975 | 63.7864 | 123.0834 | 61.795 | 122.9826 | 61.527 | 61.5991 | 123.2819 | 61.5632 | 123.0692 | 61.4843 | 61.5202 | 61.3835 | 61.4194
3003.0625 | 123.349 | -61.6104 | 61.5097 | 2.2279 | 2.0703 | 2.1628 | 1.843 | 2.3069 | 2.1871 | 2.176 | 61.5188 | 0.23948 | 61.4226 | -0.042259 | 0.043657 | 61.7127 | -0.001436 | 61.5046 | 63.8383 | 63.6807 | 63.7733 | 63.4534 | 63.9173 | 63.7975 | 63.7864 | 123.1292 | 61.8499 | 123.033 | 61.5682 | 61.6541 | 123.3231 | 61.609 | 123.115 | 61.4751 | 61.5202 | 61.3789 | 61.424
3004.0625 | 123.4085 | -61.615 | 61.5005 | 2.2325 | 2.0795 | 2.1537 | 1.8476 | 2.3252 | 2.1687 | 2.1852 | 61.5188 | 0.2349 | 61.4271 | -0.03768 | 0.029923 | 61.7172 | -0.001436 | 61.5046 | 63.8475 | 63.6945 | 63.7687 | 63.4626 | 63.9402 | 63.7837 | 63.8002 | 123.1338 | 61.8499 | 123.0421 | 61.5773 | 61.6449 | 123.3322 | 61.6136 | 123.1196 | 61.4889 | 61.5202 | 61.3972 | 61.4286
3005.0625 | 123.3856 | -61.6058 | 61.4777 | 2.2462 | 2.0886 | 2.172 | 1.8613 | 2.3481 | 2.1962 | 2.1943 | 61.5142 | 0.24405 | 61.418 | -0.042259 | 0.034501 | 61.7081 | 0.007721 | 61.5046 | 63.8521 | 63.6945 | 63.7778 | 63.4672 | 63.954 | 63.8021 | 63.8002 | 123.12 | 61.8499 | 123.0238 | 61.5636 | 61.6403 | 123.3139 | 61.6136 | 123.1104 | 61.4797 | 61.5065 | 61.3835 | 61.4103
3006.0625 | 123.3948 | -61.5921 | 61.4685 | 2.2188 | 2.0978 | 2.1537 | 1.8659 | 2.339 | 2.1642 | 2.1989 | 61.5188 | 0.24405 | 61.418 | -0.03768 | 0.034501 | 61.7127 | 0.003143 | 61.5 | 63.8109 | 63.6899 | 63.7458 | 63.458 | 63.9311 | 63.7563 | 63.791 | 123.1109 | 61.8362 | 123.0101 | 61.5544 | 61.6266 | 123.3048 | 61.5952 | 123.0921 | 61.4843 | 61.5156 | 61.3835 | 61.4148
3007.0625 | 123.3078 | -61.5921 | 61.5555 | 2.2645 | 2.084 | 2.1903 | 1.8934 | 2.3344 | 2.2145 | 2.1577 | 61.5234 | 0.2349 | 61.4317 | -0.028522 | 0.034501 | 61.7218 | -0.001436 | 61.5 | 63.8566 | 63.6762 | 63.7824 | 63.4855 | 63.9265 | 63.8066 | 63.7498 | 123.1155 | 61.827 | 123.0238 | 61.5636 | 61.6266 | 123.3139 | 61.5907 | 123.0921 | 61.4889 | 61.5248 | 61.3972 | 61.4332
3008.0625 | 123.4268 | -61.5784 | 61.4868 | 2.2645 | 2.0978 | 2.1949 | 1.8842 | 2.3024 | 2.21 | 2.1577 | 61.5234 | 0.24405 | 61.4271 | -0.033101 | 0.034501 | 61.7172 | 0.003143 | 61.5046 | 63.8429 | 63.6762 | 63.7733 | 63.4626 | 63.8807 | 63.7883 | 63.7361 | 123.1017 | 61.8224 | 123.0055 | 61.5453 | 61.6129 | 123.2956 | 61.5815 | 123.083 | 61.4889 | 61.5202 | 61.3926 | 61.424
3009.0938 | 123.2941 | -61.615 | 61.5555 | 2.2691 | 2.0978 | 2.1949 | 1.843 | 2.3115 | 2.2237 | 2.2081 | 61.5188 | 0.24863 | 61.4226 | -0.03768 | 0.034501 | 61.7172 | -0.006014 | 61.5 | 63.8841 | 63.7128 | 63.8099 | 63.458 | 63.9265 | 63.8387 | 63.823 | 123.1338 | 61.8636 | 123.0376 | 61.5773 | 61.6495 | 123.3322 | 61.609 | 123.115 | 61.4843 | 61.5248 | 61.3881 | 61.4286
3010.0625 | 123.381 | -61.5738 | 61.4685 | 2.2554 | 2.0978 | 2.1903 | 1.8201 | 2.3252 | 2.2054 | 2.2081 | 61.5234 | 0.2349 | 61.4226 | -0.042259 | 0.034501 | 61.7218 | 0.003143 | 61.5 | 63.8292 | 63.6716 | 63.7641 | 63.3939 | 63.899 | 63.7792 | 63.7818 | 123.0972 | 61.8087 | 122.9964 | 61.5315 | 61.6083 | 123.2956 | 61.5769 | 123.0738 | 61.4889 | 61.5202 | 61.3881 | 61.4194
3011.0938 | 123.2895 | -61.6013 | 61.5555 | 2.292 | 2.1115 | 2.2086 | 1.8659 | 2.3436 | 2.2328 | 2.2584 | 61.5188 | 0.2349 | 61.4226 | -0.042259 | 0.039079 | 61.7218 | -0.006014 | 61.5092 | 63.8933 | 63.7128 | 63.8099 | 63.4672 | 63.9448 | 63.8341 | 63.8597 | 123.12 | 61.8362 | 123.0238 | 61.559 | 61.6403 | 123.3231 | 61.5952 | 123.1104 | 61.4797 | 61.5248 | 61.3835 | 61.4286
3012.0625 | 123.2941 | -61.5738 | 61.5463 | 2.2874 | 2.0978 | 2.2178 | 1.8842 | 2.3069 | 2.242 | 2.2401 | 61.5234 | 0.23948 | 61.4271 | -0.033101 | 0.034501 | 61.7127 | -0.001436 | 61.5092 | 63.8612 | 63.6716 | 63.7916 | 63.458 | 63.8807 | 63.8158 | 63.8139 | 123.0972 | 61.8133 | 123.0009 | 61.5407 | 61.6083 | 123.2865 | 61.5724 | 123.083 | 61.4889 | 61.5248 | 61.3926 | 61.4286
3013.0625 | 123.3261 | -61.615 | 61.5005 | 2.2783 | 2.0932 | 2.2086 | 1.8705 | 2.2154 | 2.2283 | 2.2355 | 61.5142 | 0.23948 | 61.4226 | -0.042259 | 0.034501 | 61.7218 | -0.001436 | 61.5 | 63.8933 | 63.7082 | 63.8236 | 63.4855 | 63.8304 | 63.8433 | 63.8505 | 123.1292 | 61.8545 | 123.0376 | 61.5727 | 61.6495 | 123.3368 | 61.6136 | 123.115 | 61.4797 | 61.5156 | 61.3881 | 61.424
3014.0625 | 123.3444 | -61.5921 | 61.5372 | 2.2691 | 2.0978 | 2.1949 | 1.8522 | 2.2062 | 2.2237 | 2.2081 | 61.5234 | 0.23948 | 61.4226 | -0.03768 | 0.034501 | 61.7127 | -0.001436 | 61.5046 | 63.8612 | 63.6899 | 63.787 | 63.4443 | 63.7983 | 63.8158 | 63.8002 | 123.1155 | 61.8316 | 123.0147 | 61.5544 | 61.6266 | 123.3048 | 61.5907 | 123.0967 | 61.4889 | 61.5248 | 61.3881 | 61.424
3015.0625 | 123.3719 | -61.6013 | 61.4868 | 2.2371 | 2.1436 | 2.172 | 1.8476 | 2.2108 | 2.1871 | 2.1256 | 61.5234 | 0.24405 | 61.4317 | -0.03768 | 0.034501 | 61.7127 | -0.006014 | 61.4909 | 63.8383 | 63.7448 | 63.7733 | 63.4488 | 63.8121 | 63.7883 | 63.7269 | 123.1246 | 61.8453 | 123.033 | 61.5636 | 61.6358 | 123.3139 | 61.5952 | 123.0921 | 61.4889 | 61.5294 | 61.3972 | 61.4377
3016.0781 | 123.2758 | -61.6196 | 61.5326 | 2.2325 | 2.0932 | 2.1674 | 1.843 | 2.22 | 2.1871 | 2.1348 | 61.5234 | 0.23948 | 61.4226 | -0.033101 | 0.039079 | 61.7127 | -0.001436 | 61.5046 | 63.8521 | 63.7128 | 63.787 | 63.4626 | 63.8395 | 63.8066 | 63.7544 | 123.1429 | 61.859 | 123.0421 | 61.5865 | 61.6586 | 123.3322 | 61.6181 | 123.1242 | 61.4843 | 61.5248 | 61.3835 | 61.424
3017.0625 | 123.4039 | -61.6196 | 61.5051 | 2.2188 | 2.1161 | 2.1445 | 1.843 | 2.2062 | 2.1596 | 2.1852 | 61.5188 | 0.23948 | 61.4226 | -0.042259 | 0.029923 | 61.7127 | 0.007721 | 61.5 | 63.8383 | 63.7357 | 63.7641 | 63.4626 | 63.8258 | 63.7792 | 63.8047 | 123.1384 | 61.859 | 123.0421 | 61.5773 | 61.6495 | 123.3322 | 61.6273 | 123.1196 | 61.4889 | 61.5111 | 61.3926 | 61.4149
3018.0625 | 123.4268 | -61.6058 | 61.4548 | 2.205 | 2.0474 | 2.1308 | 1.8522 | 2.2108 | 2.155 | 2.1852 | 61.5279 | 0.24405 | 61.4271 | -0.046838 | 0.039079 | 61.7172 | -0.006014 | 61.4909 | 63.8109 | 63.6533 | 63.7366 | 63.458 | 63.8166 | 63.7608 | 63.791 | 123.1338 | 61.8499 | 123.033 | 61.559 | 61.6449 | 123.3231 | 61.5998 | 123.0967 | 61.4889 | 61.534 | 61.3881 | 61.4332
3019.0625 | 123.2803 | -61.6241 | 61.5646 | 2.2142 | 2.0428 | 2.1537 | 1.8522 | 2.2062 | 2.1687 | 2.1531 | 61.5279 | 0.23948 | 61.4271 | -0.03768 | 0.034501 | 61.7127 | -0.001436 | 61.5 | 63.8383 | 63.667 | 63.7778 | 63.4763 | 63.8304 | 63.7929 | 63.7773 | 123.1521 | 61.8636 | 123.0513 | 61.5865 | 61.6586 | 123.3368 | 61.6227 | 123.1242 | 61.4934 | 61.5294 | 61.3926 | 61.4286
3020.0938 | 123.2895 | -61.6241 | 61.5372 | 2.2142 | 2.1298 | 2.1537 | 1.8705 | 2.1879 | 2.1642 | 2.144 | 61.5234 | 0.24405 | 61.4226 | -0.03768 | 0.043657 | 61.7127 | -0.006014 | 61.5 | 63.8383 | 63.754 | 63.7778 | 63.4946 | 63.8121 | 63.7883 | 63.7681 | 123.1475 | 61.8682 | 123.0467 | 61.5865 | 61.6678 | 123.3368 | 61.6181 | 123.1242 | 61.4797 | 61.5294 | 61.3789 | 61.4286
3021.0625 | 123.2666 | -61.615 | 61.5646 | 2.2371 | 2.1436 | 2.1674 | 1.8934 | 2.1787 | 2.1916 | 2.1623 | 61.5188 | 0.2349 | 61.4271 | -0.033101 | 0.043657 | 61.7172 | -0.006014 | 61.5046 | 63.8521 | 63.7586 | 63.7824 | 63.5084 | 63.7937 | 63.8066 | 63.7773 | 123.1338 | 61.8499 | 123.0421 | 61.5819 | 61.6586 | 123.3322 | 61.609 | 123.1196 | 61.4751 | 61.5248 | 61.3835 | 61.4332
3022.0625 | 123.4406 | -61.6196 | 61.4685 | 2.2325 | 2.139 | 2.1583 | 1.9163 | 2.1879 | 2.1825 | 2.1669 | 61.5234 | 0.23948 | 61.4271 | -0.033101 | 0.034501 | 61.7081 | -0.006014 | 61.5046 | 63.8521 | 63.7586 | 63.7778 | 63.5358 | 63.8075 | 63.8021 | 63.7864 | 123.1429 | 61.859 | 123.0467 | 61.5865 | 61.6541 | 123.3276 | 61.6136 | 123.1242 | 61.4889 | 61.5294 | 61.3926 | 61.4332
3023.0938 | 123.3078 | -61.647 | 61.5005 | 2.2233 | 2.1298 | 2.1537 | 1.9025 | 2.0002 | 2.1779 | 2.1623 | 61.5234 | 0.24863 | 61.4317 | -0.03768 | 0.034501 | 61.7172 | -0.010593 | 61.4954 | 63.8704 | 63.7769 | 63.8007 | 63.5496 | 63.6472 | 63.8249 | 63.8093 | 123.1704 | 61.8957 | 123.0788 | 61.6094 | 61.6815 | 123.3643 | 61.6364 | 123.1425 | 61.4889 | 61.534 | 61.3972 | 61.4423
3024.0625 | 123.3536 | -61.5738 | 61.5005 | 2.2508 | 2.1436 | 2.1674 | 1.9254 | 1.9819 | 2.1871 | 2.2035 | 61.5188 | 0.2349 | 61.4271 | -0.03768 | 0.039079 | 61.7127 | -0.006014 | 61.5092 | 63.8246 | 63.7174 | 63.7412 | 63.4992 | 63.5557 | 63.7609 | 63.7773 | 123.0926 | 61.8087 | 123.0009 | 61.5361 | 61.6129 | 123.2865 | 61.5678 | 123.083 | 61.4797 | 61.5248 | 61.3881 | 61.4332
3025.0781 | 123.2483 | -61.6013 | 61.5509 | 2.1913 | 2.0978 | 2.1125 | 1.898 | 2.0597 | 2.1367 | 2.1943 | 61.5279 | 0.24405 | 61.418 | -0.03768 | 0.039079 | 61.7172 | 0.003143 | 61.5 | 63.7925 | 63.699 | 63.7137 | 63.4992 | 63.661 | 63.738 | 63.7956 | 123.1292 | 61.8453 | 123.0192 | 61.5636 | 61.6403 | 123.3185 | 61.6044 | 123.1013 | 61.4889 | 61.5248 | 61.3789 | 61.4148
3026.0625 | 123.3765 | -61.5921 | 61.4868 | 2.1775 | 2.084 | 2.1171 | 1.8888 | 1.9911 | 2.1413 | 2.1989 | 61.5188 | 0.23948 | 61.4271 | -0.042259 | 0.039079 | 61.7127 | 0.003143 | 61.4909 | 63.7696 | 63.6762 | 63.7092 | 63.4809 | 63.5832 | 63.7334 | 63.791 | 123.1109 | 61.8316 | 123.0193 | 61.5498 | 61.6312 | 123.3048 | 61.5952 | 123.083 | 61.4797 | 61.5156 | 61.3881 | 61.424
3027.0625 | 123.2849 | -61.6241 | 61.5326 | 2.2142 | 2.0108 | 2.1445 | 1.8934 | 1.9361 | 2.1687 | 2.1852 | 61.5279 | 0.24863 | 61.4317 | -0.03768 | 0.034501 | 61.7172 | -0.001436 | 61.5 | 63.8383 | 63.6349 | 63.7687 | 63.5175 | 63.5603 | 63.7929 | 63.8093 | 123.1521 | 61.8728 | 123.0559 | 61.5865 | 61.6586 | 123.3414 | 61.6227 | 123.1242 | 61.4934 | 61.5294 | 61.3972 | 61.4332
3028.0938 | 123.3215 | -61.6241 | 61.528 | 2.1959 | 1.9971 | 2.1216 | 1.898 | 1.9361 | 2.155 | 2.176 | 61.5325 | 0.23948 | 61.45 | -0.03768 | 0.034501 | 61.7081 | -0.001436 | 61.5046 | 63.82 | 63.6212 | 63.7458 | 63.5221 | 63.5603 | 63.7792 | 63.8002 | 123.1567 | 61.8636 | 123.0742 | 61.5865 | 61.6586 | 123.3322 | 61.6227 | 123.1287 | 61.498 | 61.534 | 61.4155 | 61.4515
3029.0625 | 123.3124 | -61.6104 | 61.5326 | 2.2004 | 2.0062 | 2.1399 | 1.898 | 1.927 | 2.1642 | 2.1577 | 61.5417 | 0.24405 | 61.4638 | -0.03768 | 0.043657 | 61.7127 | 0.003143 | 61.5 | 63.8109 | 63.6166 | 63.7504 | 63.5084 | 63.5374 | 63.7746 | 63.7681 | 123.1521 | 61.8545 | 123.0742 | 61.5727 | 61.6541 | 123.3231 | 61.6136 | 123.1104 | 61.498 | 61.5385 | 61.4201 | 61.4606
3030.0625 | 123.3902 | -61.6058 | 61.4868 | 2.2371 | 2.0337 | 2.1674 | 1.9529 | 2.0185 | 2.1916 | 2.1806 | 61.5279 | 0.24405 | 61.4592 | -0.042259 | 0.039079 | 61.7172 | -0.006014 | 61.5 | 63.8429 | 63.6395 | 63.7732 | 63.5587 | 63.6244 | 63.7975 | 63.7864 | 123.1338 | 61.8499 | 123.065 | 61.5636 | 61.6449 | 123.3231 | 61.5998 | 123.1058 | 61.4889 | 61.534 | 61.4201 | 61.4652
3031.0625 | 123.4268 | -61.6013 | 61.5097 | 2.1867 | 2.0062 | 2.1171 | 1.9346 | 1.9865 | 2.1367 | 2.1577 | 61.5279 | 0.23948 | 61.4638 | -0.033101 | 0.034501 | 61.7127 | -0.006014 | 61.5 | 63.788 | 63.6075 | 63.7183 | 63.5358 | 63.5877 | 63.738 | 63.759 | 123.1292 | 61.8407 | 123.065 | 61.5682 | 61.6358 | 123.3139 | 61.5952 | 123.1013 | 61.4934 | 61.534 | 61.4293 | 61.4698
3032.1094 | 123.3444 | -61.5921 | 61.5005 | 2.1501 | 1.9925 | 2.085 | 1.9575 | 1.9773 | 2.1047 | 2.1394 | 61.5325 | 0.24405 | 61.4409 | -0.042259 | 0.034501 | 61.7081 | -0.010593 | 61.4909 | 63.7422 | 63.5846 | 63.6771 | 63.5496 | 63.5694 | 63.6968 | 63.7315 | 123.1246 | 61.8362 | 123.033 | 61.5498 | 61.6266 | 123.3002 | 61.5815 | 123.083 | 61.498 | 61.5431 | 61.4064 | 61.4515
3033.0625 | 123.4268 | -61.5967 | 61.5234 | 2.1592 | 2.0016 | 2.0942 | 1.9804 | 1.9865 | 2.1184 | 2.1485 | 61.5234 | 0.24405 | 61.4317 | -0.033101 | 0.034501 | 61.7081 | 0.007721 | 61.5046 | 63.7559 | 63.5983 | 63.6908 | 63.577 | 63.5832 | 63.7151 | 63.7452 | 123.12 | 61.8407 | 123.0284 | 61.5636 | 61.6312 | 123.3048 | 61.6044 | 123.1013 | 61.4889 | 61.5156 | 61.3972 | 61.424
3034.0938 | 123.3719 | -61.6196 | 61.5372 | 2.0814 | 1.9467 | 2.0209 | 1.9529 | 1.9544 | 2.036 | 2.0844 | 61.5279 | 0.24405 | 61.4226 | -0.033101 | 0.034501 | 61.7035 | 0.003143 | 61.4863 | 63.701 | 63.5663 | 63.6405 | 63.5725 | 63.574 | 63.6555 | 63.704 | 123.1475 | 61.8636 | 123.0421 | 61.5865 | 61.6541 | 123.3231 | 61.6227 | 123.1058 | 61.4934 | 61.5248 | 61.3881 | 61.4194
3035.0625 | 123.3856 | -61.5646 | 61.5189 | 2.173 | 1.9787 | 2.1033 | 2.0033 | 1.9911 | 2.1275 | 2.1485 | 61.5234 | 0.2349 | 61.4455 | -0.042259 | 0.039079 | 61.7127 | 0.003143 | 61.5046 | 63.7376 | 63.5434 | 63.668 | 63.5679 | 63.5557 | 63.6922 | 63.7132 | 123.088 | 61.7995 | 123.0101 | 61.5224 | 61.6037 | 123.2773 | 61.5678 | 123.0692 | 61.4843 | 61.5202 | 61.4064 | 61.4423
3036.0625 | 123.3856 | -61.6104 | 61.528 | 2.1089 | 1.9467 | 2.0438 | 1.9575 | 1.9499 | 2.0634 | 2.1073 | 61.5325 | 0.23948 | 61.4592 | -0.033101 | 0.039079 | 61.7081 | 0.007721 | 61.5 | 63.7193 | 63.5571 | 63.6542 | 63.5679 | 63.5603 | 63.6739 | 63.7178 | 123.1429 | 61.8499 | 123.0696 | 61.5773 | 61.6495 | 123.3185 | 61.6181 | 123.1104 | 61.4934 | 61.5248 | 61.4201 | 61.4515
3037.1094 | 123.3627 | -61.5829 | 61.5097 | 2.1455 | 1.965 | 2.085 | 1.9941 | 1.9224 | 2.0909 | 2.0936 | 61.5371 | 0.23948 | 61.4638 | -0.03768 | 0.034501 | 61.7127 | -0.001436 | 61.4909 | 63.7284 | 63.5479 | 63.6679 | 63.577 | 63.5053 | 63.6739 | 63.6765 | 123.12 | 61.8224 | 123.0467 | 61.5453 | 61.6174 | 123.2956 | 61.5815 | 123.0738 | 61.5026 | 61.5385 | 61.4293 | 61.4652
3038.0625 | 123.4039 | -61.5829 | 61.4914 | 2.1592 | 1.9742 | 2.085 | 1.9941 | 1.9453 | 2.1092 | 2.0982 | 61.5325 | 0.2349 | 61.4729 | -0.03768 | 0.034501 | 61.7081 | 0.007721 | 61.4954 | 63.7422 | 63.5571 | 63.6679 | 63.577 | 63.5282 | 63.6922 | 63.6811 | 123.1155 | 61.8178 | 123.0559 | 61.5453 | 61.6174 | 123.291 | 61.5907 | 123.0784 | 61.498 | 61.5248 | 61.4384 | 61.4652
3039.0625 | 123.3398 | -61.6058 | 61.5555 | 2.1272 | 1.9879 | 2.0621 | 2.0033 | 1.9453 | 2.0909 | 2.0753 | 61.5325 | 0.24863 | 61.4546 | -0.033101 | 0.039079 | 61.7035 | 0.003143 | 61.5 | 63.733 | 63.5937 | 63.6679 | 63.6091 | 63.5511 | 63.6968 | 63.6811 | 123.1384 | 61.8545 | 123.0605 | 61.5727 | 61.6449 | 123.3093 | 61.609 | 123.1058 | 61.4934 | 61.5294 | 61.4155 | 61.4515
3040.0938 | 123.3444 | -61.6241 | 61.5417 | 2.1226 | 1.9787 | 2.0484 | 2.0078 | 1.9453 | 2.0726 | 2.0616 | 61.5325 | 0.24405 | 61.4317 | -0.03768 | 0.029923 | 61.7172 | 0.003143 | 61.4954 | 63.7468 | 63.6029 | 63.6725 | 63.632 | 63.5694 | 63.6967 | 63.6857 | 123.1567 | 61.8682 | 123.0559 | 61.5865 | 61.6541 | 123.3414 | 61.6273 | 123.1196 | 61.5026 | 61.5294 | 61.4018 | 61.4286
3041.0625 | 123.3398 | -61.5967 | 61.5509 | 2.1409 | 1.9742 | 2.0575 | 2.0078 | 1.9315 | 2.0863 | 2.057 | 61.5279 | 0.24405 | 61.4271 | -0.03768 | 0.039079 | 61.7081 | 0.003143 | 61.5 | 63.7376 | 63.5708 | 63.6542 | 63.6045 | 63.5282 | 63.683 | 63.6537 | 123.1246 | 61.8407 | 123.0238 | 61.559 | 61.6358 | 123.3048 | 61.5998 | 123.0967 | 61.4889 | 61.5248 | 61.3881 | 61.424
3042.0625 | 123.2758 | -61.6241 | 61.528 | 2.1592 | 1.9742 | 2.0942 | 2.0124 | 1.9682 | 2.1092 | 2.0707 | 61.5279 | 0.24405 | 61.4317 | -0.033101 | 0.039079 | 61.7081 | 0.003143 | 61.5 | 63.7834 | 63.5983 | 63.7183 | 63.6366 | 63.5923 | 63.7334 | 63.6949 | 123.1521 | 61.8682 | 123.0559 | 61.591 | 61.6632 | 123.3322 | 61.6273 | 123.1242 | 61.4889 | 61.5248 | 61.3926 | 61.4286
3043.0625 | 123.3444 | -61.615 | 61.528 | 2.1547 | 1.965 | 2.085 | 2.0033 | 1.9911 | 2.1092 | 2.0616 | 61.5279 | 0.23948 | 61.4592 | -0.033101 | 0.034501 | 61.7081 | 0.003143 | 61.4954 | 63.7696 | 63.58 | 63.7 | 63.6182 | 63.606 | 63.7242 | 63.6765 | 123.1429 | 61.8545 | 123.0742 | 61.5819 | 61.6495 | 123.3231 | 61.6181 | 123.1104 | 61.4934 | 61.5248 | 61.4247 | 61.4561
3044.0625 | 123.3078 | -61.647 | 61.5189 | 2.1501 | 1.9558 | 2.085 | 2.0033 | 1.959 | 2.1001 | 2.0616 | 61.5463 | 0.2349 | 61.4684 | -0.046838 | 0.034501 | 61.7035 | 0.007721 | 61.4909 | 63.7971 | 63.6029 | 63.732 | 63.6503 | 63.606 | 63.7471 | 63.7086 | 123.1933 | 61.8819 | 123.1154 | 61.6002 | 61.6815 | 123.3505 | 61.6548 | 123.1379 | 61.5118 | 61.5385 | 61.4339 | 61.4606
3045.0781 | 123.3353 | -61.6104 | 61.4914 | 2.1318 | 1.9146 | 2.0621 | 1.9941 | 1.9499 | 2.0818 | 2.0432 | 61.5371 | 0.23948 | 61.4638 | -0.042259 | 0.043657 | 61.7127 | -0.001436 | 61.4954 | 63.7422 | 63.525 | 63.6725 | 63.6045 | 63.5603 | 63.6922 | 63.6537 | 123.1475 | 61.8499 | 123.0742 | 61.5682 | 61.6541 | 123.3231 | 61.609 | 123.1058 | 61.4934 | 61.5385 | 61.4201 | 61.4652
3046.0625 | 123.3215 | -61.5738 | 61.5326 | 2.1272 | 1.9467 | 2.0621 | 1.9987 | 1.9773 | 2.0818 | 2.002 | 61.5325 | 0.2349 | 61.4684 | -0.033101 | 0.034501 | 61.7127 | -0.006014 | 61.5 | 63.701 | 63.5205 | 63.6359 | 63.5725 | 63.5511 | 63.6556 | 63.5758 | 123.1063 | 61.8087 | 123.0421 | 61.5407 | 61.6083 | 123.2865 | 61.5678 | 123.0738 | 61.498 | 61.5385 | 61.4339 | 61.4744
3047.0625 | 123.4131 | -61.5967 | 61.496 | 2.031 | 1.9146 | 1.9568 | 1.9987 | 1.9727 | 1.9719 | 1.9471 | 61.5279 | 0.24405 | 61.4363 | -0.03768 | 0.039079 | 61.7035 | -0.001436 | 61.4909 | 63.6277 | 63.5113 | 63.5535 | 63.5954 | 63.5694 | 63.5686 | 63.5438 | 123.1246 | 61.8407 | 123.033 | 61.559 | 61.6358 | 123.3002 | 61.5952 | 123.0875 | 61.4889 | 61.5294 | 61.3972 | 61.4377
3048.0625 | 123.4131 | -61.5509 | 61.4868 | 2.0448 | 1.9192 | 1.966 | 2.017 | 2.0185 | 1.981 | 1.9883 | 61.5325 | 0.23948 | 61.4226 | -0.042259 | 0.039079 | 61.7081 | -0.001436 | 61.4817 | 63.5957 | 63.4701 | 63.5169 | 63.5679 | 63.5694 | 63.5319 | 63.5392 | 123.0834 | 61.7904 | 122.9735 | 61.5086 | 61.59 | 123.259 | 61.5495 | 123.0326 | 61.4934 | 61.534 | 61.3835 | 61.424
3049.0625 | 123.4039 | -61.5601 | 61.528 | 1.9898 | 1.8826 | 1.9202 | 1.9895 | 1.9911 | 1.9398 | 1.9608 | 61.5279 | 0.24405 | 61.4546 | -0.033101 | 0.039079 | 61.6989 | 0.003143 | 61.4909 | 63.5499 | 63.4426 | 63.4802 | 63.5496 | 63.5511 | 63.4999 | 63.5209 | 123.088 | 61.8041 | 123.0147 | 61.527 | 61.5991 | 123.259 | 61.5632 | 123.0509 | 61.4889 | 61.5248 | 61.4155 | 61.4515
3050.0938 | 123.3856 | -61.5738 | 61.5234 | 1.9761 | 1.8872 | 1.911 | 2.017 | 2.0277 | 1.9261 | 1.9608 | 61.5279 | 0.23948 | 61.4684 | -0.03768 | 0.029923 | 61.7035 | -0.001436 | 61.5046 | 63.5499 | 63.461 | 63.4848 | 63.5908 | 63.6015 | 63.4999 | 63.5346 | 123.1017 | 61.8133 | 123.0421 | 61.5361 | 61.6037 | 123.2773 | 61.5724 | 123.0784 | 61.498 | 61.5294 | 61.4384 | 61.4698
3051.0625 | 123.2529 | -61.6241 | 61.5784 | 1.9761 | 1.878 | 1.9019 | 2.0078 | 2.0506 | 1.9215 | 1.9379 | 61.5463 | 0.23948 | 61.4775 | -0.033101 | 0.039079 | 61.6989 | -0.001436 | 61.4954 | 63.6002 | 63.5022 | 63.526 | 63.632 | 63.6747 | 63.5457 | 63.5621 | 123.1704 | 61.8636 | 123.1017 | 61.591 | 61.6632 | 123.3231 | 61.6227 | 123.1196 | 61.5072 | 61.5477 | 61.4384 | 61.4789
3052.0625 | 123.2803 | -61.6013 | 61.5417 | 1.9257 | 1.8368 | 1.8515 | 2.0124 | 2.046 | 1.8803 | 1.8739 | 61.5417 | 0.24863 | 61.4775 | -0.033101 | 0.034501 | 61.7035 | -0.001436 | 61.4954 | 63.527 | 63.4381 | 63.4527 | 63.6137 | 63.6472 | 63.4816 | 63.4751 | 123.1429 | 61.8499 | 123.0788 | 61.5682 | 61.6358 | 123.3048 | 61.5998 | 123.0967 | 61.5072 | 61.5431 | 61.443 | 61.4789
3053.0938 | 123.3627 | -61.5875 | 61.4868 | 1.9486 | 1.8185 | 1.8744 | 2.0033 | 2.0643 | 1.894 | 1.851 | 61.5417 | 0.24405 | 61.4684 | -0.046838 | 0.039079 | 61.7035 | 0.003143 | 61.4954 | 63.5362 | 63.406 | 63.4619 | 63.5908 | 63.6518 | 63.4816 | 63.4385 | 123.1292 | 61.8316 | 123.0559 | 61.5407 | 61.6266 | 123.291 | 61.5907 | 123.083 | 61.5026 | 61.5385 | 61.4293 | 61.4652
3054.0625 | 123.3444 | -61.5646 | 61.528 | 1.9761 | 1.8414 | 1.911 | 1.9987 | 2.0872 | 1.9353 | 1.9013 | 61.5325 | 0.23948 | 61.4455 | -0.03768 | 0.039079 | 61.7081 | -0.001436 | 61.4954 | 63.5407 | 63.406 | 63.4756 | 63.5633 | 63.6518 | 63.4999 | 63.466 | 123.0972 | 61.8041 | 123.0101 | 61.527 | 61.6037 | 123.2727 | 61.5632 | 123.0601 | 61.4934 | 61.534 | 61.4064 | 61.4469
3055.0938 | 123.4039 | -61.5738 | 61.5189 | 1.9532 | 1.8368 | 1.879 | 1.9895 | 2.0872 | 1.9078 | 1.8418 | 61.5279 | 0.24405 | 61.4317 | -0.042259 | 0.043657 | 61.7035 | -0.001436 | 61.4909 | 63.527 | 63.4106 | 63.4528 | 63.5633 | 63.661 | 63.4816 | 63.4156 | 123.1017 | 61.8178 | 123.0055 | 61.5315 | 61.6174 | 123.2773 | 61.5724 | 123.0646 | 61.4843 | 61.5294 | 61.3881 | 61.4332
3056.0625 | 123.2986 | -61.6013 | 61.5509 | 1.9807 | 1.8597 | 1.9202 | 2.017 | 2.1147 | 1.9398 | 1.8555 | 61.5417 | 0.24405 | 61.45 | -0.042259 | 0.039079 | 61.7035 | 0.003143 | 61.4954 | 63.5819 | 63.4609 | 63.5214 | 63.6182 | 63.7159 | 63.5411 | 63.4568 | 123.1429 | 61.8453 | 123.0513 | 61.559 | 61.6403 | 123.3048 | 61.6044 | 123.0967 | 61.5026 | 61.5385 | 61.411 | 61.4469
3057.0625 | 123.262 | -61.6013 | 61.5509 | 1.9944 | 1.8505 | 1.9202 | 2.0033 | 2.1192 | 1.9444 | 1.8601 | 61.5371 | 0.23948 | 61.4455 | -0.033101 | 0.039079 | 61.7081 | -0.001436 | 61.5046 | 63.5957 | 63.4518 | 63.5214 | 63.6045 | 63.7205 | 63.5457 | 63.4614 | 123.1384 | 61.8407 | 123.0467 | 61.5682 | 61.6403 | 123.3093 | 61.5998 | 123.1058 | 61.498 | 61.5385 | 61.4064 | 61.4469
3058.0625 | 123.3582 | -61.5875 | 61.496 | 2.0036 | 1.8231 | 1.9385 | 2.0033 | 2.1101 | 1.9627 | 1.8555 | 61.5371 | 0.25321 | 61.4729 | -0.03768 | 0.034501 | 61.7035 | -0.001436 | 61.4909 | 63.5911 | 63.4106 | 63.526 | 63.5908 | 63.6976 | 63.5502 | 63.4431 | 123.1246 | 61.8407 | 123.0605 | 61.5498 | 61.622 | 123.291 | 61.5861 | 123.0784 | 61.5026 | 61.5385 | 61.4384 | 61.4744
3059.0938 | 123.3353 | -61.6058 | 61.5051 | 2.0127 | 1.8322 | 1.9431 | 2.0399 | 2.133 | 1.9627 | 1.8739 | 61.5279 | 0.24863 | 61.4729 | -0.03768 | 0.039079 | 61.7035 | -0.001436 | 61.5 | 63.6186 | 63.4381 | 63.5489 | 63.6457 | 63.7388 | 63.5686 | 63.4797 | 123.1338 | 61.8545 | 123.0788 | 61.5682 | 61.6449 | 123.3093 | 61.6044 | 123.1058 | 61.4889 | 61.5294 | 61.4339 | 61.4744
3060.0625 | 123.3261 | -61.6058 | 61.5555 | 1.9486 | 1.8047 | 1.879 | 2.0261 | 2.1513 | 1.9032 | 1.8464 | 61.5417 | 0.24405 | 61.4821 | -0.033101 | 0.039079 | 61.7035 | -0.001436 | 61.5 | 63.5545 | 63.4106 | 63.4848 | 63.632 | 63.7571 | 63.509 | 63.4522 | 123.1475 | 61.8499 | 123.0879 | 61.5727 | 61.6449 | 123.3093 | 61.6044 | 123.1058 | 61.5026 | 61.5431 | 61.443 | 61.4835
3061.0625 | 123.3353 | -61.5738 | 61.5463 | 1.88 | 1.7818 | 1.8149 | 2.0261 | 2.1375 | 1.8391 | 1.8235 | 61.5417 | 0.24405 | 61.4729 | -0.033101 | 0.034501 | 61.6989 | 0.003143 | 61.4909 | 63.4537 | 63.3556 | 63.3887 | 63.5999 | 63.7113 | 63.4129 | 63.3973 | 123.1155 | 61.8178 | 123.0467 | 61.5407 | 61.6083 | 123.2727 | 61.5769 | 123.0646 | 61.5072 | 61.5385 | 61.4384 | 61.4698
3062.0625 | 123.317 | -61.6196 | 61.5372 | 1.8296 | 1.7498 | 1.7462 | 1.9758 | 2.1009 | 1.775 | 1.7548 | 61.5371 | 0.25321 | 61.4363 | -0.03768 | 0.039079 | 61.6989 | -0.006014 | 61.4817 | 63.4492 | 63.3694 | 63.3658 | 63.5954 | 63.7205 | 63.3946 | 63.3744 | 123.1567 | 61.8728 | 123.0559 | 61.5819 | 61.6586 | 123.3185 | 61.6136 | 123.1013 | 61.498 | 61.5431 | 61.3972 | 61.4423
3063.0938 | 123.3444 | -61.6058 | 61.5417 | 1.8616 | 1.7635 | 1.7874 | 1.9804 | 2.0826 | 1.8071 | 1.7136 | 61.5417 | 0.24405 | 61.4455 | -0.03768 | 0.039079 | 61.7035 | -0.006014 | 61.4909 | 63.4675 | 63.3694 | 63.3932 | 63.5862 | 63.6884 | 63.4129 | 63.3194 | 123.1475 | 61.8499 | 123.0513 | 61.5682 | 61.6449 | 123.3093 | 61.5998 | 123.0967 | 61.5026 | 61.5477 | 61.4064 | 61.4515
3064.0625 | 123.2986 | -61.5601 | 61.5372 | 1.8662 | 1.7635 | 1.7965 | 1.9621 | 2.0002 | 1.8162 | 1.7502 | 61.5371 | 0.23948 | 61.4455 | -0.033101 | 0.034501 | 61.6943 | -0.006014 | 61.4909 | 63.4263 | 63.3236 | 63.3566 | 63.5221 | 63.5603 | 63.3763 | 63.3103 | 123.0972 | 61.7995 | 123.0055 | 61.527 | 61.5946 | 123.2544 | 61.554 | 123.0509 | 61.5026 | 61.5431 | 61.411 | 61.4515
3065.0781 | 123.349 | -61.5646 | 61.5692 | 1.8708 | 1.7864 | 1.7965 | 1.9575 | 1.9956 | 1.8345 | 1.7319 | 61.5417 | 0.24405 | 61.4592 | -0.033101 | 0.048236 | 61.6989 | -0.001436 | 61.5046 | 63.4354 | 63.3511 | 63.3612 | 63.5221 | 63.5603 | 63.3992 | 63.2966 | 123.1063 | 61.8087 | 123.0238 | 61.5315 | 61.6129 | 123.2636 | 61.5632 | 123.0692 | 61.4934 | 61.5431 | 61.411 | 61.4606
3066.0625 | 123.3261 | -61.5967 | 61.5417 | 1.9166 | 1.8047 | 1.8378 | 1.9483 | 1.9682 | 1.8574 | 1.7502 | 61.5463 | 0.24863 | 61.4821 | -0.033101 | 0.029923 | 61.7035 | 0.007721 | 61.4909 | 63.5133 | 63.4014 | 63.4344 | 63.545 | 63.5648 | 63.4541 | 63.3469 | 123.1429 | 61.8453 | 123.0788 | 61.5636 | 61.6266 | 123.3002 | 61.6044 | 123.0875 | 61.5163 | 61.5385 | 61.4522 | 61.4744
3067.0625 | 123.2986 | -61.5967 | 61.5463 | 2.0356 | 1.7956 | 1.966 | 1.9712 | 1.9911 | 1.9856 | 1.7319 | 61.5417 | 0.2349 | 61.4729 | -0.042259 | 0.029923 | 61.7081 | -0.006014 | 61.4954 | 63.6323 | 63.3923 | 63.5626 | 63.5679 | 63.5877 | 63.5823 | 63.3286 | 123.1384 | 61.8316 | 123.0696 | 61.5544 | 61.6266 | 123.3048 | 61.5907 | 123.0921 | 61.5118 | 61.5477 | 61.443 | 61.4789
3068.0625 | 123.2941 | -61.5784 | 61.5326 | 2.0173 | 1.8047 | 1.9431 | 1.9208 | 1.9361 | 1.9719 | 1.764 | 61.5417 | 0.24863 | 61.4729 | -0.03768 | 0.039079 | 61.7127 | 0.003143 | 61.4863 | 63.5957 | 63.3831 | 63.5214 | 63.4992 | 63.5145 | 63.5502 | 63.3423 | 123.12 | 61.827 | 123.0513 | 61.5407 | 61.6174 | 123.291 | 61.5815 | 123.0646 | 61.5026 | 61.5385 | 61.4339 | 61.4698
3069.0938 | 123.3673 | -61.6058 | 61.5005 | 2.0036 | 1.8139 | 1.9385 | 1.9208 | 1.8629 | 1.9581 | 1.709 | 61.5325 | 0.23948 | 61.4638 | -0.03768 | 0.039079 | 61.6989 | -0.006014 | 61.4863 | 63.6094 | 63.4197 | 63.5443 | 63.5267 | 63.4687 | 63.564 | 63.3149 | 123.1384 | 61.8453 | 123.0696 | 61.5682 | 61.6449 | 123.3048 | 61.5998 | 123.0921 | 61.4934 | 61.5385 | 61.4247 | 61.4698
3070.0625 | 123.3398 | -61.6196 | 61.5326 | 1.8845 | 1.791 | 1.8194 | 1.9025 | 1.8674 | 1.8483 | 1.6861 | 61.5417 | 0.24405 | 61.45 | -0.042259 | 0.034501 | 61.6943 | -0.006014 | 61.4863 | 63.5041 | 63.4106 | 63.439 | 63.5221 | 63.487 | 63.4678 | 63.3057 | 123.1612 | 61.8636 | 123.0696 | 61.5773 | 61.6541 | 123.3139 | 61.6136 | 123.1058 | 61.5072 | 61.5477 | 61.4155 | 61.4561
3071.0625 | 123.262 | -61.615 | 61.5646 | 1.8571 | 1.7544 | 1.7874 | 1.8888 | 1.8674 | 1.8116 | 1.6175 | 61.5463 | 0.24863 | 61.4546 | -0.03768 | 0.034501 | 61.7035 | -0.001436 | 61.4817 | 63.472 | 63.3694 | 63.4024 | 63.5038 | 63.4824 | 63.4266 | 63.2325 | 123.1612 | 61.8636 | 123.0696 | 61.5773 | 61.6495 | 123.3185 | 61.6136 | 123.0967 | 61.5118 | 61.5477 | 61.4201 | 61.4561
3072.0625 | 123.2666 | -61.6379 | 61.5555 | 1.88 | 1.7773 | 1.8103 | 1.898 | 1.8629 | 1.8299 | 1.5992 | 61.5417 | 0.24405 | 61.4409 | -0.03768 | 0.043657 | 61.6898 | -0.006014 | 61.4817 | 63.5178 | 63.4151 | 63.4482 | 63.5358 | 63.5007 | 63.4678 | 63.237 | 123.1796 | 61.8819 | 123.0788 | 61.6002 | 61.6815 | 123.3276 | 61.6319 | 123.1196 | 61.498 | 61.5477 | 61.3972 | 61.4469
3073.0625 | 123.3032 | -61.615 | 61.5601 | 1.8891 | 1.7956 | 1.8149 | 1.9025 | 1.8766 | 1.8437 | 1.6495 | 61.5463 | 0.24405 | 61.4775 | -0.033101 | 0.043657 | 61.6989 | -0.001436 | 61.4863 | 63.5041 | 63.4106 | 63.4299 | 63.5175 | 63.4916 | 63.4587 | 63.2645 | 123.1612 | 61.859 | 123.0925 | 61.5819 | 61.6586 | 123.3139 | 61.6136 | 123.1013 | 61.5026 | 61.5477 | 61.4339 | 61.4789
3074.0625 | 123.3353 | -61.5967 | 61.5234 | 1.8891 | 1.8002 | 1.8286 | 1.9483 | 1.9361 | 1.8483 | 1.6678 | 61.5463 | 0.24863 | 61.4821 | -0.033101 | 0.039079 | 61.6989 | -0.001436 | 61.4954 | 63.4858 | 63.3968 | 63.4253 | 63.545 | 63.5328 | 63.4449 | 63.2645 | 123.1429 | 61.8453 | 123.0788 | 61.5636 | 61.6358 | 123.2956 | 61.5952 | 123.0921 | 61.5072 | 61.5477 | 61.443 | 61.4835
3075.0781 | 123.3261 | -61.6013 | 61.5829 | 1.8662 | 1.759 | 1.792 | 1.9254 | 1.9315 | 1.8116 | 1.7182 | 61.5371 | 0.24863 | 61.4592 | -0.033101 | 0.039079 | 61.6989 | 0.003143 | 61.4909 | 63.4675 | 63.3602 | 63.3932 | 63.5267 | 63.5328 | 63.4129 | 63.3194 | 123.1384 | 61.8499 | 123.0605 | 61.5682 | 61.6403 | 123.3002 | 61.6044 | 123.0921 | 61.498 | 61.534 | 61.4201 | 61.4561
3076.0625 | 123.2941 | -61.5829 | 61.5234 | 1.9349 | 1.8414 | 1.8652 | 2.0261 | 2.0414 | 1.8803 | 1.8098 | 61.5325 | 0.24405 | 61.4455 | -0.042259 | 0.039079 | 61.6989 | 0.003143 | 61.4954 | 63.5178 | 63.4243 | 63.4482 | 63.6091 | 63.6244 | 63.4633 | 63.3927 | 123.1155 | 61.827 | 123.0284 | 61.5407 | 61.622 | 123.2819 | 61.5861 | 123.0784 | 61.4934 | 61.5294 | 61.4064 | 61.4423
3077.0625 | 123.3353 | -61.5875 | 61.5555 | 1.8113 | 1.7132 | 1.737 | 1.898 | 1.9636 | 1.7613 | 1.6358 | 61.5463 | 0.24405 | 61.4775 | -0.033101 | 0.039079 | 61.6989 | -0.006014 | 61.4909 | 63.3988 | 63.3007 | 63.3246 | 63.4855 | 63.5511 | 63.3488 | 63.2233 | 123.1338 | 61.8316 | 123.065 | 61.5544 | 61.6266 | 123.2864 | 61.5815 | 123.0784 | 61.5072 | 61.5523 | 61.4384 | 61.4835
3078.0625 | 123.349 | -61.5921 | 61.5646 | 1.8067 | 1.7177 | 1.7324 | 1.9346 | 1.9865 | 1.7567 | 1.6266 | 61.5554 | 0.23948 | 61.4867 | -0.03768 | 0.034501 | 61.6989 | 0.003143 | 61.4817 | 63.3988 | 63.3098 | 63.3245 | 63.5267 | 63.5786 | 63.3488 | 63.2187 | 123.1475 | 61.8316 | 123.0788 | 61.5544 | 61.6266 | 123.291 | 61.5952 | 123.0738 | 61.5209 | 61.5523 | 61.4522 | 61.4835
3079.0625 | 123.3215 | -61.5829 | 61.5784 | 1.8387 | 1.7361 | 1.7737 | 1.9712 | 2.0231 | 1.7933 | 1.6449 | 61.5371 | 0.24863 | 61.4546 | -0.028522 | 0.034501 | 61.6898 | -0.006014 | 61.4817 | 63.4217 | 63.319 | 63.3566 | 63.5542 | 63.606 | 63.3763 | 63.2279 | 123.12 | 61.8316 | 123.0376 | 61.5544 | 61.6174 | 123.2727 | 61.5769 | 123.0646 | 61.5026 | 61.5431 | 61.4201 | 61.4606
3080.0781 | 123.4085 | -61.5875 | 61.528 | 1.8067 | 1.7132 | 1.7324 | 1.93 | 2.0094 | 1.7613 | 1.5808 | 61.5463 | 0.24405 | 61.4455 | -0.033101 | 0.034501 | 61.6989 | 0.003143 | 61.4817 | 63.3942 | 63.3007 | 63.32 | 63.5175 | 63.5969 | 63.3488 | 63.1684 | 123.1338 | 61.8316 | 123.033 | 61.5544 | 61.622 | 123.2864 | 61.5907 | 123.0692 | 61.5118 | 61.5431 | 61.411 | 61.4423
3081.0625 | 123.2849 | -61.5784 | 61.5738 | 1.8204 | 1.7223 | 1.7508 | 1.9346 | 2.0048 | 1.7796 | 1.5671 | 61.5463 | 0.23948 | 61.4821 | -0.033101 | 0.039079 | 61.6989 | 0.003143 | 61.4863 | 63.3988 | 63.3007 | 63.3291 | 63.5129 | 63.5832 | 63.358 | 63.1455 | 123.1246 | 61.8178 | 123.0605 | 61.5453 | 61.6174 | 123.2773 | 61.5815 | 123.0646 | 61.5072 | 61.5431 | 61.443 | 61.4789
3082.0625 | 123.3856 | -61.5738 | 61.4914 | 1.8159 | 1.7132 | 1.7416 | 1.93 | 2.0002 | 1.7567 | 1.5442 | 61.5508 | 0.24405 | 61.4729 | -0.033101 | 0.039079 | 61.6943 | -0.001436 | 61.4817 | 63.3896 | 63.287 | 63.3154 | 63.5038 | 63.574 | 63.3305 | 63.118 | 123.1246 | 61.8178 | 123.0467 | 61.5407 | 61.6129 | 123.2681 | 61.5724 | 123.0555 | 61.5118 | 61.5523 | 61.4339 | 61.4744
3083.0938 | 123.3444 | -61.5967 | 61.5509 | 1.793 | 1.6994 | 1.7233 | 1.9529 | 2.0368 | 1.7475 | 1.5351 | 61.5508 | 0.24405 | 61.4592 | -0.042259 | 0.034501 | 61.6989 | 0.003143 | 61.4863 | 63.3896 | 63.2961 | 63.32 | 63.5496 | 63.6335 | 63.3442 | 63.1317 | 123.1475 | 61.8407 | 123.0559 | 61.5544 | 61.6312 | 123.2956 | 61.5998 | 123.083 | 61.5163 | 61.5477 | 61.4247 | 61.4561
3084.0625 | 123.3078 | -61.5784 | 61.5692 | 1.8113 | 1.7223 | 1.7462 | 1.9346 | 2.0414 | 1.7704 | 1.5259 | 61.5463 | 0.24405 | 61.4409 | -0.033101 | 0.039079 | 61.6943 | -0.001436 | 61.4817 | 63.3896 | 63.3007 | 63.3246 | 63.5129 | 63.6198 | 63.3488 | 63.1043 | 123.1246 | 61.8224 | 123.0193 | 61.5453 | 61.6174 | 123.2727 | 61.5769 | 123.0601 | 61.5072 | 61.5477 | 61.4018 | 61.4423
3085.0625 | 123.2986 | -61.5784 | 61.5417 | 1.8159 | 1.7315 | 1.7508 | 1.9529 | 2.0918 | 1.775 | 1.5396 | 61.5508 | 0.23948 | 61.4684 | -0.033101 | 0.039079 | 61.6943 | -0.001436 | 61.4909 | 63.3942 | 63.3099 | 63.3291 | 63.5313 | 63.6701 | 63.3534 | 63.118 | 123.1292 | 61.8178 | 123.0467 | 61.5453 | 61.6174 | 123.2727 | 61.5769 | 123.0692 | 61.5118 | 61.5523 | 61.4293 | 61.4698
3086.0625 | 123.2574 | -61.647 | 61.5646 | 1.8021 | 1.6949 | 1.737 | 1.9392 | 2.1009 | 1.7613 | 1.5122 | 61.5508 | 0.23948 | 61.4821 | -0.03768 | 0.034501 | 61.6989 | 0.007721 | 61.468 | 63.4492 | 63.3419 | 63.3841 | 63.5862 | 63.748 | 63.4083 | 63.1592 | 123.1979 | 61.8865 | 123.1291 | 61.6094 | 61.6815 | 123.346 | 61.6548 | 123.115 | 61.5163 | 61.5431 | 61.4476 | 61.4744
3087.0625 | 123.3353 | -61.5967 | 61.4868 | 1.8067 | 1.704 | 1.7416 | 1.9346 | 2.1147 | 1.7659 | 1.5122 | 61.5417 | 0.24405 | 61.4455 | -0.03768 | 0.034501 | 61.6989 | -0.006014 | 61.4863 | 63.4034 | 63.3007 | 63.3383 | 63.5313 | 63.7113 | 63.3625 | 63.1089 | 123.1384 | 61.8407 | 123.0421 | 61.559 | 61.6312 | 123.2956 | 61.5907 | 123.083 | 61.5072 | 61.5477 | 61.411 | 61.4515
3088.0625 | 123.2666 | -61.6333 | 61.5234 | 1.8204 | 1.7544 | 1.7553 | 1.9941 | 2.133 | 1.7796 | 1.5763 | 61.5417 | 0.23948 | 61.4409 | -0.033101 | 0.039079 | 61.6989 | -0.006014 | 61.4863 | 63.4537 | 63.3877 | 63.3886 | 63.6274 | 63.7663 | 63.4129 | 63.2096 | 123.175 | 61.8728 | 123.0742 | 61.6002 | 61.6724 | 123.3322 | 61.6273 | 123.1196 | 61.5026 | 61.5477 | 61.4018 | 61.4469
3089.0625 | 123.2346 | -61.615 | 61.5417 | 1.8159 | 1.7498 | 1.7416 | 1.9575 | 2.1421 | 1.7659 | 1.5442 | 61.5417 | 0.23948 | 61.4729 | -0.028522 | 0.039079 | 61.6989 | 0.003143 | 61.4909 | 63.4308 | 63.3648 | 63.3566 | 63.5725 | 63.7571 | 63.3808 | 63.1592 | 123.1567 | 61.8545 | 123.0879 | 61.5865 | 61.6541 | 123.3139 | 61.6181 | 123.1058 | 61.5026 | 61.5385 | 61.4339 | 61.4698
3090.0625 | 123.2986 | -61.6058 | 61.5692 | 1.8433 | 1.7406 | 1.7828 | 1.93 | 2.1421 | 1.7979 | 1.5992 | 61.5508 | 0.25321 | 61.4821 | -0.042259 | 0.034501 | 61.7035 | 0.007721 | 61.4909 | 63.4492 | 63.3465 | 63.3886 | 63.5358 | 63.748 | 63.4037 | 63.205 | 123.1567 | 61.859 | 123.0879 | 61.5636 | 61.6403 | 123.3093 | 61.6136 | 123.0967 | 61.5163 | 61.5431 | 61.4476 | 61.4744
3091.0625 | 123.317 | -61.6196 | 61.5555 | 1.8021 | 1.7223 | 1.737 | 1.9254 | 2.133 | 1.7659 | 1.5763 | 61.5417 | 0.23948 | 61.45 | -0.033101 | 0.039079 | 61.6943 | -0.006014 | 61.4863 | 63.4217 | 63.3419 | 63.3566 | 63.545 | 63.7525 | 63.3854 | 63.1958 | 123.1612 | 61.859 | 123.0696 | 61.5865 | 61.6586 | 123.3139 | 61.6136 | 123.1058 | 61.5026 | 61.5477 | 61.411 | 61.4561
3092.1094 | 123.2437 | -61.6287 | 61.5326 | 1.7655 | 1.6949 | 1.705 | 1.9437 | 2.1742 | 1.7201 | 1.4847 | 61.5371 | 0.2349 | 61.4455 | -0.03768 | 0.043657 | 61.6943 | -0.001436 | 61.4817 | 63.3942 | 63.3236 | 63.3337 | 63.5725 | 63.8029 | 63.3488 | 63.1134 | 123.1658 | 61.8636 | 123.0742 | 61.591 | 61.6724 | 123.3231 | 61.6273 | 123.1104 | 61.4934 | 61.5385 | 61.4018 | 61.4469
3093.0625 | 123.3261 | -61.5967 | 61.5555 | 1.8937 | 1.7956 | 1.824 | 2.0216 | 2.2795 | 1.8437 | 1.5992 | 61.5325 | 0.24405 | 61.4546 | -0.03768 | 0.039079 | 61.7035 | -0.006014 | 61.4863 | 63.4904 | 63.3923 | 63.4207 | 63.6182 | 63.8761 | 63.4404 | 63.1958 | 123.1292 | 61.8407 | 123.0513 | 61.559 | 61.6358 | 123.3002 | 61.5907 | 123.083 | 61.4934 | 61.5385 | 61.4155 | 61.4606
3094.0625 | 123.2849 | -61.6241 | 61.5555 | 1.8937 | 1.7452 | 1.8332 | 1.9483 | 2.2154 | 1.8528 | 1.5213 | 61.5417 | 0.24405 | 61.4684 | -0.033101 | 0.034501 | 61.6989 | -0.006014 | 61.4909 | 63.5178 | 63.3694 | 63.4573 | 63.5725 | 63.8395 | 63.477 | 63.1455 | 123.1658 | 61.8682 | 123.0925 | 61.591 | 61.6586 | 123.3231 | 61.6181 | 123.115 | 61.5072 | 61.5477 | 61.4339 | 61.4744
3095.0781 | 123.3078 | -61.6013 | 61.5601 | 1.8708 | 1.7177 | 1.8103 | 1.93 | 2.2154 | 1.8299 | 1.5076 | 61.5554 | 0.24863 | 61.4775 | -0.033101 | 0.034501 | 61.7035 | -0.006014 | 61.4863 | 63.4721 | 63.319 | 63.4115 | 63.5313 | 63.8166 | 63.4312 | 63.1089 | 123.1567 | 61.8499 | 123.0788 | 61.5682 | 61.6358 | 123.3048 | 61.5952 | 123.0875 | 61.5209 | 61.5614 | 61.443 | 61.4835
3096.0625 | 123.2574 | -61.6196 | 61.5692 | 1.8662 | 1.7223 | 1.7965 | 1.9575 | 2.2795 | 1.8345 | 1.5717 | 61.5463 | 0.24405 | 61.4867 | -0.042259 | 0.034501 | 61.7081 | -0.001436 | 61.4909 | 63.4858 | 63.3419 | 63.4161 | 63.577 | 63.899 | 63.4541 | 63.1913 | 123.1658 | 61.8636 | 123.1062 | 61.5773 | 61.6541 | 123.3276 | 61.6181 | 123.1104 | 61.5118 | 61.5477 | 61.4522 | 61.4881
3097.0938 | 123.3536 | -61.6013 | 61.5372 | 1.8067 | 1.7406 | 1.7324 | 1.9895 | 2.3207 | 1.7567 | 1.5763 | 61.5508 | 0.24405 | 61.4775 | -0.033101 | 0.034501 | 61.6989 | 0.003143 | 61.4909 | 63.408 | 63.3419 | 63.3337 | 63.5908 | 63.9219 | 63.358 | 63.1775 | 123.1521 | 61.8453 | 123.0788 | 61.5682 | 61.6358 | 123.3002 | 61.6044 | 123.0921 | 61.5163 | 61.5477 | 61.443 | 61.4744
3098.0625 | 123.2941 | -61.5967 | 61.6013 | 1.8891 | 1.7773 | 1.8194 | 2.0261 | 2.3802 | 1.8437 | 1.6083 | 61.5463 | 0.24405 | 61.4592 | -0.03768 | 0.039079 | 61.7035 | -0.001436 | 61.4909 | 63.4858 | 63.374 | 63.4161 | 63.6228 | 63.9769 | 63.4404 | 63.205 | 123.1429 | 61.8407 | 123.0559 | 61.559 | 61.6358 | 123.3002 | 61.5952 | 123.0875 | 61.5072 | 61.5477 | 61.4201 | 61.4606
3099.0781 | 123.3032 | -61.5921 | 61.5601 | 1.8387 | 1.6903 | 1.7782 | 1.9254 | 2.2566 | 1.8025 | 1.5534 | 61.5371 | 0.24405 | 61.4455 | -0.042259 | 0.043657 | 61.6943 | -0.006014 | 61.4863 | 63.4308 | 63.2824 | 63.3703 | 63.5175 | 63.8487 | 63.3946 | 63.1455 | 123.1292 | 61.8362 | 123.0376 | 61.5498 | 61.6358 | 123.2864 | 61.5861 | 123.0784 | 61.4934 | 61.5431 | 61.4018 | 61.4515
3100.0625 | 123.317 | -61.5829 | 61.5463 | 1.8708 | 1.6262 | 1.792 | 1.8751 | 2.1971 | 1.8162 | 1.4893 | 61.5463 | 0.24405 | 61.45 | -0.03768 | 0.034501 | 61.6989 | 0.007721 | 61.4725 | 63.4537 | 63.2091 | 63.3749 | 63.458 | 63.78 | 63.3992 | 63.0722 | 123.1292 | 61.827 | 123.033 | 61.5453 | 61.6174 | 123.2819 | 61.5907 | 123.0555 | 61.5118 | 61.5385 | 61.4155 | 61.4423
3101.0938 | 123.2712 | -61.5875 | 61.5555 | 1.825 | 1.6079 | 1.7508 | 1.8293 | 2.1742 | 1.7796 | 1.4572 | 61.5463 | 0.24863 | 61.4775 | -0.033101 | 0.039079 | 61.6898 | -0.001436 | 61.4817 | 63.4125 | 63.1954 | 63.3383 | 63.4168 | 63.7617 | 63.3671 | 63.0448 | 123.1338 | 61.8362 | 123.065 | 61.5544 | 61.6266 | 123.2773 | 61.5861 | 123.0692 | 61.5072 | 61.5477 | 61.4384 | 61.4789
3102.0625 | 123.3902 | -61.5784 | 61.5234 | 1.7746 | 1.672 | 1.7004 | 1.8201 | 2.1971 | 1.7246 | 1.4572 | 61.5554 | 0.24405 | 61.4821 | -0.046838 | 0.039079 | 61.6943 | 0.003143 | 61.4817 | 63.353 | 63.2503 | 63.2788 | 63.3985 | 63.7754 | 63.303 | 63.0356 | 123.1338 | 61.8224 | 123.0605 | 61.5315 | 61.6174 | 123.2727 | 61.5815 | 123.0601 | 61.5163 | 61.5523 | 61.443 | 61.4789
3103.0625 | 123.4131 | -61.5738 | 61.5051 | 1.7975 | 1.5758 | 1.7233 | 1.8201 | 2.1971 | 1.743 | 1.471 | 61.5463 | 0.24405 | 61.4546 | -0.042259 | 0.034501 | 61.6898 | -0.006014 | 61.4725 | 63.3713 | 63.1496 | 63.2971 | 63.3939 | 63.7709 | 63.3168 | 63.0448 | 123.12 | 61.8178 | 123.0284 | 61.5315 | 61.6083 | 123.2636 | 61.5678 | 123.0463 | 61.5118 | 61.5523 | 61.4201 | 61.4606
3104.0625 | 123.3948 | -61.5601 | 61.4914 | 1.7426 | 1.53 | 1.6775 | 1.8064 | 2.1742 | 1.6972 | 1.4343 | 61.5463 | 0.23948 | 61.45 | -0.042259 | 0.039079 | 61.6943 | -0.001436 | 61.4771 | 63.3027 | 63.0901 | 63.2376 | 63.3664 | 63.7342 | 63.2572 | 62.9944 | 123.1063 | 61.7995 | 123.0101 | 61.5178 | 61.5991 | 123.2544 | 61.5586 | 123.0372 | 61.5072 | 61.5477 | 61.411 | 61.4515
3105.0781 | 123.2941 | -61.5921 | 61.528 | 1.7426 | 1.5575 | 1.6683 | 1.7835 | 2.1879 | 1.6972 | 1.4343 | 61.5554 | 0.24405 | 61.4912 | -0.042259 | 0.039079 | 61.6943 | -0.001436 | 61.4817 | 63.3347 | 63.1496 | 63.2604 | 63.3756 | 63.78 | 63.2893 | 63.0264 | 123.1475 | 61.8362 | 123.0833 | 61.5498 | 61.6312 | 123.2864 | 61.5907 | 123.0738 | 61.5163 | 61.5568 | 61.4522 | 61.4927
3106.0625 | 123.3536 | -61.5738 | 61.4868 | 1.7243 | 1.5575 | 1.6455 | 1.7698 | 2.2108 | 1.6789 | 1.4618 | 61.5508 | 0.24405 | 61.4821 | -0.042259 | 0.039079 | 61.6898 | 0.003143 | 61.4817 | 63.2981 | 63.1313 | 63.2192 | 63.3435 | 63.7846 | 63.2527 | 63.0356 | 123.1246 | 61.8178 | 123.0559 | 61.5315 | 61.6129 | 123.2636 | 61.5769 | 123.0555 | 61.5118 | 61.5477 | 61.443 | 61.4789
3107.0938 | 123.3582 | -61.5417 | 61.5692 | 1.5915 | 1.5163 | 1.531 | 1.7423 | 2.2108 | 1.5507 | 1.3977 | 61.5508 | 0.23948 | 61.4546 | -0.033101 | 0.039079 | 61.6898 | 0.007721 | 61.4725 | 63.1333 | 63.058 | 63.0727 | 63.284 | 63.7525 | 63.0924 | 62.9395 | 123.0926 | 61.7812 | 122.9964 | 61.5086 | 61.5808 | 123.2315 | 61.5495 | 123.0143 | 61.5118 | 61.5431 | 61.4155 | 61.4469
3108.0625 | 123.3948 | -61.5738 | 61.5097 | 1.5595 | 1.5071 | 1.4898 | 1.7469 | 2.2337 | 1.514 | 1.3886 | 61.5554 | 0.24405 | 61.4546 | -0.042259 | 0.034501 | 61.6806 | -0.006014 | 61.4725 | 63.1333 | 63.0809 | 63.0636 | 63.3207 | 63.8075 | 63.0878 | 62.9624 | 123.1292 | 61.8178 | 123.0284 | 61.5315 | 61.6083 | 123.2544 | 61.5678 | 123.0463 | 61.5209 | 61.5614 | 61.4201 | 61.4606
3109.0625 | 123.3994 | -61.5646 | 61.5051 | 1.5869 | 1.5346 | 1.5173 | 1.7743 | 2.2474 | 1.5369 | 1.4023 | 61.5463 | 0.24405 | 61.4638 | -0.03768 | 0.039079 | 61.6898 | -0.006014 | 61.4725 | 63.1516 | 63.0992 | 63.0819 | 63.339 | 63.8121 | 63.1016 | 62.9669 | 123.1109 | 61.8087 | 123.0284 | 61.527 | 61.6037 | 123.2544 | 61.5586 | 123.0372 | 61.5072 | 61.5523 | 61.4247 | 61.4698
3110.0625 | 123.3856 | -61.5738 | 61.5051 | 1.706 | 1.6307 | 1.6409 | 1.8613 | 2.3207 | 1.6605 | 1.4984 | 61.5463 | 0.23948 | 61.4867 | -0.03768 | 0.034501 | 61.6989 | -0.001436 | 61.4725 | 63.2798 | 63.2045 | 63.2147 | 63.4351 | 63.8945 | 63.2343 | 63.0722 | 123.12 | 61.8133 | 123.0605 | 61.5361 | 61.6083 | 123.2727 | 61.5724 | 123.0463 | 61.5118 | 61.5477 | 61.4522 | 61.4881
3111.0938 | 123.2666 | -61.6241 | 61.5372 | 1.6602 | 1.5529 | 1.5905 | 1.7743 | 2.3298 | 1.6193 | 1.4343 | 61.5554 | 0.24405 | 61.4958 | -0.033101 | 0.039079 | 61.6943 | 0.003143 | 61.4771 | 63.2843 | 63.1771 | 63.2147 | 63.3985 | 63.954 | 63.2435 | 63.0585 | 123.1796 | 61.8682 | 123.12 | 61.591 | 61.6632 | 123.3185 | 61.6273 | 123.1013 | 61.5163 | 61.5523 | 61.4567 | 61.4927
3112.0625 | 123.381 | -61.5738 | 61.5051 | 1.6052 | 1.5163 | 1.5401 | 1.6965 | 2.2886 | 1.5644 | 1.3794 | 61.5554 | 0.24405 | 61.4912 | -0.03768 | 0.039079 | 61.6852 | 0.003143 | 61.4725 | 63.179 | 63.0901 | 63.1139 | 63.2703 | 63.8624 | 63.1382 | 62.9532 | 123.1292 | 61.8178 | 123.065 | 61.5361 | 61.6129 | 123.259 | 61.5769 | 123.0463 | 61.5163 | 61.5523 | 61.4522 | 61.4881
3113.0625 | 123.3902 | -61.5646 | 61.5005 | 1.6602 | 1.5666 | 1.5859 | 1.7926 | 2.3481 | 1.6102 | 1.4389 | 61.5508 | 0.24405 | 61.4729 | -0.042259 | 0.034501 | 61.6852 | -0.001436 | 61.4817 | 63.2248 | 63.1313 | 63.1506 | 63.3573 | 63.9128 | 63.1748 | 63.0036 | 123.1155 | 61.8087 | 123.0376 | 61.5224 | 61.5991 | 123.2498 | 61.5632 | 123.0463 | 61.5163 | 61.5523 | 61.4384 | 61.4744
3114.0625 | 123.3994 | -61.5646 | 61.5051 | 1.6373 | 1.5071 | 1.563 | 1.7652 | 2.3024 | 1.5873 | 1.3794 | 61.5463 | 0.24405 | 61.4592 | -0.03768 | 0.025345 | 61.6852 | -0.006014 | 61.4725 | 63.2019 | 63.0718 | 63.1277 | 63.3298 | 63.867 | 63.1519 | 62.944 | 123.1109 | 61.8087 | 123.0238 | 61.527 | 61.59 | 123.2498 | 61.5586 | 123.0372 | 61.5209 | 61.5523 | 61.4339 | 61.4652
3115.0938 | 123.2849 | -61.6104 | 61.5509 | 1.6052 | 1.4842 | 1.5264 | 1.756 | 2.2795 | 1.5552 | 1.3565 | 61.56 | 0.24863 | 61.4546 | -0.033101 | 0.034501 | 61.6898 | -0.001436 | 61.4725 | 63.2157 | 63.0946 | 63.1368 | 63.3664 | 63.8899 | 63.1657 | 62.9669 | 123.1704 | 61.859 | 123.065 | 61.5773 | 61.6449 | 123.3002 | 61.609 | 123.083 | 61.5255 | 61.5614 | 61.4201 | 61.4561
3116.0625 | 123.4268 | -61.5875 | 61.4822 | 1.5869 | 1.4751 | 1.5173 | 1.756 | 2.2886 | 1.5369 | 1.3886 | 61.5554 | 0.24863 | 61.4546 | -0.042259 | 0.034501 | 61.6943 | -0.001436 | 61.468 | 63.1745 | 63.0626 | 63.1048 | 63.3435 | 63.8761 | 63.1245 | 62.9761 | 123.1429 | 61.8362 | 123.0421 | 61.5453 | 61.622 | 123.2819 | 61.5861 | 123.0555 | 61.5209 | 61.5568 | 61.4201 | 61.4561
3117.0625 | 123.3536 | -61.5784 | 61.5417 | 1.5183 | 1.4247 | 1.4486 | 1.7102 | 2.2703 | 1.4774 | 1.3153 | 61.5554 | 0.24405 | 61.4729 | -0.03768 | 0.034501 | 61.6806 | -0.001436 | 61.4771 | 63.0966 | 63.0031 | 63.0269 | 63.2886 | 63.8487 | 63.0558 | 62.8937 | 123.1338 | 61.8224 | 123.0513 | 61.5407 | 61.6129 | 123.259 | 61.5769 | 123.0555 | 61.5209 | 61.5568 | 61.4384 | 61.4744
3118.0781 | 123.2849 | -61.6196 | 61.5372 | 1.4633 | 1.3698 | 1.3982 | 1.6919 | 2.2657 | 1.4133 | 1.3245 | 61.56 | 0.24863 | 61.5004 | -0.033101 | 0.034501 | 61.6806 | 0.003143 | 61.4725 | 63.0829 | 62.9893 | 63.0178 | 63.3115 | 63.8853 | 63.0329 | 62.944 | 123.1796 | 61.8682 | 123.12 | 61.5865 | 61.6541 | 123.3002 | 61.6227 | 123.0921 | 61.5255 | 61.5568 | 61.4659 | 61.4973
3119.0625 | 123.4314 | -61.5875 | 61.5372 | 1.4587 | 1.3698 | 1.3891 | 1.7148 | 2.2703 | 1.4133 | 1.3382 | 61.5646 | 0.24405 | 61.4867 | -0.042259 | 0.029923 | 61.676 | 0.003143 | 61.468 | 63.0463 | 62.9573 | 62.9766 | 63.3023 | 63.8578 | 63.0008 | 62.9257 | 123.1521 | 61.8316 | 123.0742 | 61.5453 | 61.6174 | 123.2636 | 61.5907 | 123.0555 | 61.5346 | 61.5614 | 61.4567 | 61.4835
3120.0781 | 123.3215 | -61.5921 | 61.5509 | 1.4267 | 1.3285 | 1.3616 | 1.6965 | 2.2154 | 1.3858 | 1.3107 | 61.5646 | 0.23948 | 61.4958 | -0.042259 | 0.039079 | 61.6852 | -0.001436 | 61.468 | 63.0188 | 62.9206 | 62.9537 | 63.2886 | 63.8075 | 62.9779 | 62.9028 | 123.1567 | 61.8316 | 123.0879 | 61.5498 | 61.6312 | 123.2773 | 61.5907 | 123.0601 | 61.5255 | 61.566 | 61.4567 | 61.4973
3121.0625 | 123.4085 | -61.5417 | 61.5326 | 1.413 | 1.3011 | 1.3433 | 1.6873 | 2.1467 | 1.363 | 1.2695 | 61.5646 | 0.25321 | 61.4912 | -0.042259 | 0.034501 | 61.676 | -0.001436 | 61.468 | 62.9547 | 62.8428 | 62.885 | 63.2291 | 63.6885 | 62.9047 | 62.8113 | 123.1063 | 61.795 | 123.033 | 61.4995 | 61.5762 | 123.2178 | 61.5403 | 123.0097 | 61.5301 | 61.566 | 61.4567 | 61.4927
3122.0625 | 123.3902 | -61.5509 | 61.528 | 1.3992 | 1.2644 | 1.3341 | 1.7102 | 2.1284 | 1.363 | 1.2604 | 61.5554 | 0.2349 | 61.4729 | -0.03768 | 0.034501 | 61.676 | -0.006014 | 61.468 | 62.9501 | 62.8153 | 62.885 | 63.2611 | 63.6793 | 62.9139 | 62.8113 | 123.1063 | 61.7858 | 123.0238 | 61.5132 | 61.5854 | 123.2269 | 61.5449 | 123.0189 | 61.5209 | 61.5614 | 61.4384 | 61.4789
3123.0938 | 123.2666 | -61.5784 | 61.5646 | 1.3718 | 1.2782 | 1.3021 | 1.7102 | 2.0735 | 1.3355 | 1.2833 | 61.5554 | 0.24405 | 61.4638 | -0.03768 | 0.034501 | 61.6806 | 0.003143 | 61.4634 | 62.9501 | 62.8565 | 62.8804 | 63.2886 | 63.6518 | 62.9139 | 62.8616 | 123.1338 | 61.8224 | 123.0421 | 61.5407 | 61.6129 | 123.259 | 61.5815 | 123.0418 | 61.5209 | 61.5523 | 61.4293 | 61.4606
3124.0625 | 123.4222 | -61.5646 | 61.528 | 1.3763 | 1.2873 | 1.3158 | 1.7057 | 2.0551 | 1.3263 | 1.2878 | 61.56 | 0.24405 | 61.4638 | -0.042259 | 0.039079 | 61.6715 | -0.001436 | 61.4634 | 62.941 | 62.852 | 62.8804 | 63.2703 | 63.6198 | 62.891 | 62.8525 | 123.1246 | 61.8087 | 123.0284 | 61.5224 | 61.6037 | 123.2361 | 61.5632 | 123.028 | 61.5209 | 61.5614 | 61.4247 | 61.4652
3125.0625 | 123.3719 | -61.5692 | 61.5326 | 1.3626 | 1.2644 | 1.2883 | 1.669 | 2.0414 | 1.3126 | 1.2604 | 61.56 | 0.24863 | 61.4821 | -0.03768 | 0.034501 | 61.6806 | -0.006014 | 61.4634 | 62.9318 | 62.8337 | 62.8575 | 63.2382 | 63.6106 | 62.8818 | 62.8296 | 123.1292 | 61.8178 | 123.0513 | 61.5315 | 61.6037 | 123.2498 | 61.5632 | 123.0326 | 61.5255 | 61.566 | 61.4476 | 61.4881
3126.0781 | 123.349 | -61.5646 | 61.5646 | 1.3901 | 1.3011 | 1.3295 | 1.7285 | 2.1147 | 1.3538 | 1.3016 | 61.5691 | 0.24405 | 61.4958 | -0.033101 | 0.029923 | 61.676 | -0.006014 | 61.4817 | 62.9547 | 62.8657 | 62.8942 | 63.2932 | 63.6793 | 62.9184 | 62.8662 | 123.1338 | 61.8087 | 123.0605 | 61.5315 | 61.5946 | 123.2407 | 61.5586 | 123.0463 | 61.5392 | 61.5752 | 61.4659 | 61.5018
3127.0625 | 123.3765 | -61.6013 | 61.5417 | 1.3809 | 1.2873 | 1.3112 | 1.6919 | 2.1147 | 1.3401 | 1.2924 | 61.5737 | 0.24405 | 61.5004 | -0.03768 | 0.039079 | 61.6806 | -0.010593 | 61.4771 | 62.9822 | 62.8886 | 62.9125 | 63.2932 | 63.7159 | 62.9413 | 62.8937 | 123.175 | 61.8453 | 123.1017 | 61.5636 | 61.6403 | 123.2819 | 61.5907 | 123.0784 | 61.5346 | 61.5843 | 61.4613 | 61.511
3128.0625 | 123.3994 | -61.5601 | 61.5143 | 1.4267 | 1.3285 | 1.3616 | 1.7148 | 2.1879 | 1.3813 | 1.329 | 61.5646 | 0.24863 | 61.5004 | -0.042259 | 0.034501 | 61.6852 | -0.001436 | 61.468 | 62.9868 | 62.8886 | 62.9216 | 63.2749 | 63.748 | 62.9413 | 62.8891 | 123.1246 | 61.8087 | 123.0605 | 61.5178 | 61.5946 | 123.2452 | 61.5586 | 123.028 | 61.5301 | 61.566 | 61.4659 | 61.5018
3129.0938 | 123.3765 | -61.5784 | 61.5234 | 1.3901 | 1.3102 | 1.3295 | 1.6965 | 2.1375 | 1.3492 | 1.2924 | 61.5646 | 0.24405 | 61.505 | -0.046838 | 0.039079 | 61.676 | -0.001436 | 61.4725 | 62.9684 | 62.8886 | 62.9079 | 63.2749 | 63.7159 | 62.9276 | 62.8708 | 123.1429 | 61.8224 | 123.0833 | 61.5315 | 61.6174 | 123.2544 | 61.5769 | 123.0509 | 61.5255 | 61.566 | 61.4659 | 61.5064
3130.0625 | 123.3627 | -61.5601 | 61.5143 | 1.3534 | 1.2553 | 1.2837 | 1.6461 | 2.078 | 1.3126 | 1.2604 | 61.5646 | 0.24863 | 61.5096 | -0.042259 | 0.034501 | 61.676 | -0.006014 | 61.4634 | 62.9135 | 62.8153 | 62.8438 | 63.2062 | 63.6381 | 62.8727 | 62.8204 | 123.1246 | 61.8087 | 123.0696 | 61.5178 | 61.5946 | 123.2361 | 61.554 | 123.0234 | 61.5301 | 61.5706 | 61.4751 | 61.5156
3131.0938 | 123.349 | -61.5692 | 61.5829 | 1.3809 | 1.2828 | 1.3066 | 1.6644 | 2.0735 | 1.3355 | 1.2695 | 61.5646 | 0.23948 | 61.4729 | -0.042259 | 0.034501 | 61.6806 | -0.001436 | 61.4725 | 62.9501 | 62.852 | 62.8759 | 63.2337 | 63.6427 | 62.9047 | 62.8387 | 123.1338 | 61.8087 | 123.0421 | 61.527 | 61.6037 | 123.2498 | 61.5678 | 123.0418 | 61.5301 | 61.566 | 61.4384 | 61.4744
3132.0625 | 123.2758 | -61.5921 | 61.6058 | 1.3489 | 1.2507 | 1.2746 | 1.6644 | 2.0231 | 1.3034 | 1.2604 | 61.56 | 0.23948 | 61.4684 | -0.033101 | 0.043657 | 61.6669 | -0.006014 | 61.4634 | 62.941 | 62.8428 | 62.8667 | 63.2565 | 63.6152 | 62.8955 | 62.8525 | 123.1521 | 61.8316 | 123.0605 | 61.559 | 61.6358 | 123.259 | 61.5861 | 123.0555 | 61.5163 | 61.566 | 61.4247 | 61.4744
3133.0625 | 123.3536 | -61.5692 | 61.528 | 1.326 | 1.2324 | 1.2609 | 1.669 | 2.0323 | 1.2851 | 1.2329 | 61.5691 | 0.24405 | 61.4729 | -0.03768 | 0.029923 | 61.676 | 0.003143 | 61.4634 | 62.8952 | 62.8016 | 62.8301 | 63.2382 | 63.6015 | 62.8543 | 62.8021 | 123.1384 | 61.8133 | 123.0421 | 61.5315 | 61.5991 | 123.2452 | 61.5724 | 123.0326 | 61.5392 | 61.566 | 61.443 | 61.4698
3134.0938 | 123.3307 | -61.5829 | 61.5326 | 1.3351 | 1.237 | 1.2654 | 1.6828 | 2.1009 | 1.2897 | 1.21 | 61.5646 | 0.2349 | 61.4958 | -0.042259 | 0.034501 | 61.6806 | -0.006014 | 61.4725 | 62.9181 | 62.8199 | 62.8484 | 63.2657 | 63.6839 | 62.8726 | 62.793 | 123.1475 | 61.8178 | 123.0788 | 61.5407 | 61.6174 | 123.2636 | 61.5769 | 123.0555 | 61.5301 | 61.5706 | 61.4613 | 61.5018
3135.0625 | 123.3765 | -61.5646 | 61.5051 | 1.3855 | 1.2965 | 1.3066 | 1.7469 | 2.1467 | 1.3492 | 1.2512 | 61.5691 | 0.24405 | 61.5004 | -0.042259 | 0.034501 | 61.6806 | -0.001436 | 61.468 | 62.9501 | 62.8611 | 62.8713 | 63.3115 | 63.7113 | 62.9139 | 62.8159 | 123.1338 | 61.8087 | 123.065 | 61.5224 | 61.5991 | 123.2452 | 61.5632 | 123.0326 | 61.5346 | 61.5706 | 61.4659 | 61.5018
3136.0625 | 123.4268 | -61.5509 | 61.4731 | 1.5732 | 1.4339 | 1.4989 | 1.8155 | 2.2795 | 1.5324 | 1.4115 | 61.5554 | 0.25321 | 61.4912 | -0.042259 | 0.039079 | 61.6898 | -0.001436 | 61.468 | 63.1241 | 62.9848 | 63.0498 | 63.3664 | 63.8304 | 63.0833 | 62.9624 | 123.1063 | 61.8041 | 123.0421 | 61.5086 | 61.59 | 123.2407 | 61.5495 | 123.0189 | 61.5163 | 61.5568 | 61.4522 | 61.4927
3137.0938 | 123.3261 | -61.5692 | 61.5692 | 1.5183 | 1.3881 | 1.4532 | 1.7698 | 2.2291 | 1.4774 | 1.3382 | 61.56 | 0.24405 | 61.4958 | -0.03768 | 0.039079 | 61.6852 | -0.006014 | 61.4771 | 63.0875 | 62.9573 | 63.0224 | 63.339 | 63.7983 | 63.0466 | 62.9074 | 123.1292 | 61.8133 | 123.065 | 61.5315 | 61.6083 | 123.2544 | 61.5632 | 123.0463 | 61.5209 | 61.566 | 61.4567 | 61.5018
3138.0625 | 123.3856 | -61.5326 | 61.5326 | 1.3397 | 1.2553 | 1.2746 | 1.6599 | 2.0918 | 1.2943 | 1.21 | 61.5646 | 0.24405 | 61.4867 | -0.03768 | 0.029923 | 61.676 | -0.001436 | 61.4588 | 62.8723 | 62.7879 | 62.8072 | 63.1925 | 63.6244 | 62.8269 | 62.7426 | 123.0972 | 61.7766 | 123.0193 | 61.4949 | 61.5625 | 123.2086 | 61.5312 | 122.9914 | 61.5346 | 61.566 | 61.4567 | 61.4881
3139.0625 | 123.2803 | -61.528 | 61.6333 | 1.3443 | 1.269 | 1.2792 | 1.6599 | 2.0872 | 1.3034 | 1.2146 | 61.56 | 0.24405 | 61.4684 | -0.033101 | 0.039079 | 61.676 | 0.003143 | 61.4588 | 62.8723 | 62.797 | 62.8072 | 63.1879 | 63.6152 | 62.8314 | 62.7426 | 123.088 | 61.7721 | 122.9964 | 61.4949 | 61.5671 | 123.204 | 61.5312 | 122.9868 | 61.5209 | 61.5568 | 61.4293 | 61.4652
3140.0625 | 123.3902 | -61.5646 | 61.5189 | 1.3214 | 1.269 | 1.2517 | 1.6599 | 2.078 | 1.276 | 1.2054 | 61.5737 | 0.25321 | 61.4958 | -0.03768 | 0.034501 | 61.6806 | 0.003143 | 61.4588 | 62.886 | 62.8337 | 62.8163 | 63.2245 | 63.6427 | 62.8406 | 62.7701 | 123.1384 | 61.8178 | 123.0605 | 61.527 | 61.5991 | 123.2452 | 61.5678 | 123.0234 | 61.5392 | 61.5706 | 61.4613 | 61.4927
3141.0781 | 123.3353 | -61.5463 | 61.5829 | 1.2344 | 1.1637 | 1.1647 | 1.5637 | 1.9499 | 1.1936 | 1.091 | 61.5783 | 0.24405 | 61.505 | -0.03768 | 0.039079 | 61.6715 | 0.003143 | 61.4542 | 62.7807 | 62.71 | 62.711 | 63.11 | 63.4962 | 62.7399 | 62.6373 | 123.1246 | 61.7904 | 123.0513 | 61.5086 | 61.5854 | 123.2178 | 61.5495 | 123.0006 | 61.5392 | 61.5752 | 61.4659 | 61.5018
3142.0625 | 123.4177 | -61.5555 | 61.5417 | 1.2481 | 1.1546 | 1.1876 | 1.5546 | 1.9315 | 1.2027 | 1.0864 | 61.5737 | 0.24863 | 61.505 | -0.03768 | 0.043657 | 61.6623 | -0.001436 | 61.468 | 62.8036 | 62.71 | 62.7431 | 63.11 | 63.487 | 62.7582 | 62.6419 | 123.1292 | 61.8041 | 123.0605 | 61.5178 | 61.5991 | 123.2178 | 61.554 | 123.0234 | 61.5301 | 61.5752 | 61.4613 | 61.5064
3143.0625 | 123.3582 | -61.5555 | 61.5417 | 1.2848 | 1.1729 | 1.2196 | 1.5912 | 1.9727 | 1.2393 | 1.123 | 61.5737 | 0.24863 | 61.505 | -0.042259 | 0.034501 | 61.6669 | 0.003143 | 61.4542 | 62.8402 | 62.7283 | 62.7751 | 63.1467 | 63.5282 | 62.7948 | 62.6785 | 123.1292 | 61.8041 | 123.0605 | 61.5132 | 61.59 | 123.2224 | 61.5586 | 123.0097 | 61.5392 | 61.5706 | 61.4705 | 61.5018
3144.0625 | 123.2346 | -61.5967 | 61.5875 | 1.326 | 1.2324 | 1.2609 | 1.6187 | 2.0551 | 1.2805 | 1.1642 | 61.56 | 0.24863 | 61.4684 | -0.03768 | 0.034501 | 61.6669 | -0.001436 | 61.4634 | 62.9226 | 62.8291 | 62.8575 | 63.2153 | 63.6518 | 62.8772 | 62.7609 | 123.1567 | 61.8453 | 123.065 | 61.559 | 61.6312 | 123.2636 | 61.5952 | 123.0601 | 61.5255 | 61.5614 | 61.4339 | 61.4698
3145.0938 | 123.2437 | -61.5784 | 61.5601 | 1.2848 | 1.1866 | 1.2059 | 1.5637 | 2.0277 | 1.2302 | 1.1368 | 61.5646 | 0.24863 | 61.4867 | -0.042259 | 0.039079 | 61.6715 | 0.007721 | 61.4588 | 62.8631 | 62.765 | 62.7843 | 63.1421 | 63.606 | 62.8085 | 62.7151 | 123.1429 | 61.827 | 123.065 | 61.5361 | 61.6174 | 123.2498 | 61.5861 | 123.0372 | 61.5255 | 61.5569 | 61.4476 | 61.4789
3146.0625 | 123.3719 | -61.5601 | 61.5463 | 1.2069 | 1.1408 | 1.1418 | 1.5134 | 1.9819 | 1.1752 | 1.1368 | 61.5783 | 0.24405 | 61.5141 | -0.03768 | 0.039079 | 61.6669 | -0.001436 | 61.4542 | 62.767 | 62.7009 | 62.7019 | 63.0734 | 63.542 | 62.7353 | 62.6968 | 123.1384 | 61.8041 | 123.0742 | 61.5224 | 61.5991 | 123.2269 | 61.5586 | 123.0143 | 61.5392 | 61.5797 | 61.4751 | 61.5156
3147.0625 | 123.3353 | -61.5509 | 61.5509 | 1.1749 | 1.0767 | 1.1052 | 1.4859 | 1.9636 | 1.1249 | 1.0772 | 61.5737 | 0.23948 | 61.5004 | -0.042259 | 0.039079 | 61.6623 | -0.010593 | 61.4542 | 62.7258 | 62.6276 | 62.6561 | 63.0368 | 63.5145 | 62.6758 | 62.6282 | 123.1246 | 61.7904 | 123.0513 | 61.5086 | 61.59 | 123.2132 | 61.5403 | 123.0051 | 61.5346 | 61.5843 | 61.4613 | 61.511
3148.0625 | 123.3627 | -61.5417 | 61.5692 | 1.1932 | 1.095 | 1.1235 | 1.4859 | 1.8949 | 1.1432 | 1.0727 | 61.5737 | 0.24863 | 61.4729 | -0.033101 | 0.039079 | 61.6669 | -0.001436 | 61.4451 | 62.7349 | 62.6368 | 62.6652 | 63.0276 | 63.4367 | 62.6849 | 62.6144 | 123.1155 | 61.7904 | 123.0147 | 61.5086 | 61.5808 | 123.2086 | 61.5403 | 122.9868 | 61.5346 | 61.5752 | 61.4339 | 61.4744
3149.0625 | 123.3673 | -61.5601 | 61.5509 | 1.2848 | 1.1866 | 1.2151 | 1.5225 | 1.785 | 1.2302 | 1.123 | 61.5737 | 0.23948 | 61.4592 | -0.033101 | 0.034501 | 61.6715 | -0.001436 | 61.4542 | 62.8448 | 62.7467 | 62.7751 | 63.0826 | 63.3451 | 62.7902 | 62.6831 | 123.1338 | 61.7995 | 123.0193 | 61.527 | 61.5946 | 123.2315 | 61.5586 | 123.0143 | 61.5392 | 61.5752 | 61.4247 | 61.4606
3150.0625 | 123.3673 | -61.5417 | 61.5509 | 1.271 | 1.1774 | 1.2013 | 1.495 | 1.7942 | 1.2256 | 1.1551 | 61.5646 | 0.24863 | 61.4958 | -0.03768 | 0.029923 | 61.6715 | -0.001436 | 61.4542 | 62.8128 | 62.7192 | 62.7431 | 63.0368 | 63.3359 | 62.7673 | 62.6968 | 123.1063 | 61.7904 | 123.0376 | 61.5041 | 61.5717 | 123.2132 | 61.5403 | 122.996 | 61.5346 | 61.566 | 61.4659 | 61.4973
3151.0625 | 123.3719 | -61.5326 | 61.5463 | 1.239 | 1.1454 | 1.1739 | 1.4996 | 1.872 | 1.1981 | 1.1001 | 61.5737 | 0.24863 | 61.5096 | -0.03768 | 0.043657 | 61.676 | -0.001436 | 61.4588 | 62.7716 | 62.678 | 62.7065 | 63.0322 | 63.4046 | 62.7307 | 62.6327 | 123.1063 | 61.7812 | 123.0422 | 61.4949 | 61.5763 | 123.2086 | 61.5312 | 122.9914 | 61.5301 | 61.5752 | 61.4659 | 61.511
3152.1094 | 123.3948 | -61.5463 | 61.5463 | 1.2527 | 1.1637 | 1.183 | 1.4905 | 1.8858 | 1.2027 | 1.1139 | 61.5691 | 0.24405 | 61.5141 | -0.046838 | 0.039079 | 61.6669 | 0.003143 | 61.4496 | 62.799 | 62.71 | 62.7293 | 63.0368 | 63.4321 | 62.749 | 62.6602 | 123.1155 | 61.7904 | 123.0605 | 61.4995 | 61.5854 | 123.2132 | 61.5495 | 122.996 | 61.5301 | 61.566 | 61.4751 | 61.511
3153.0625 | 123.4222 | -61.5326 | 61.5601 | 1.2024 | 1.0538 | 1.1281 | 1.4859 | 1.8949 | 1.1615 | 1.0818 | 61.5737 | 0.24405 | 61.505 | -0.03768 | 0.034501 | 61.6669 | -0.006014 | 61.4588 | 62.7349 | 62.5864 | 62.6607 | 63.0185 | 63.4275 | 62.6941 | 62.6144 | 123.1063 | 61.7766 | 123.0376 | 61.4949 | 61.5671 | 123.1995 | 61.5266 | 122.9914 | 61.5392 | 61.5797 | 61.4705 | 61.511
3154.0625 | 123.3948 | -61.5372 | 61.5692 | 1.0696 | 0.99429 | 0.99529 | 1.4584 | 1.8674 | 1.0287 | 1.036 | 61.5783 | 0.23948 | 61.4867 | -0.03768 | 0.039079 | 61.6623 | -0.001436 | 61.4496 | 62.6067 | 62.5315 | 62.5325 | 62.9956 | 63.4046 | 62.5659 | 62.5732 | 123.1155 | 61.7766 | 123.0238 | 61.4995 | 61.5762 | 123.1995 | 61.5357 | 122.9868 | 61.5392 | 61.5797 | 61.4476 | 61.4881
3155.0625 | 123.3765 | -61.5372 | 61.5829 | 1.0238 | 0.9714 | 0.95409 | 1.4401 | 1.8949 | 0.98295 | 1.036 | 61.5783 | 0.24405 | 61.4867 | -0.03768 | 0.043657 | 61.6623 | 0.003143 | 61.4496 | 62.561 | 62.5086 | 62.4913 | 62.9773 | 63.4321 | 62.5201 | 62.5732 | 123.1155 | 61.7812 | 123.0238 | 61.4995 | 61.5808 | 123.1995 | 61.5403 | 122.9868 | 61.5346 | 61.5752 | 61.443 | 61.4835
3156.0625 | 123.4314 | -61.5326 | 61.5646 | 1.0375 | 0.96224 | 0.9724 | 1.4172 | 1.8812 | 0.99668 | 1.0177 | 61.5783 | 0.24863 | 61.4821 | -0.042259 | 0.043657 | 61.6669 | -0.001436 | 61.4451 | 62.5701 | 62.4948 | 62.505 | 62.9498 | 63.4138 | 62.5293 | 62.5503 | 123.1109 | 61.7812 | 123.0147 | 61.4903 | 61.5763 | 123.1995 | 61.5312 | 122.9777 | 61.5346 | 61.5797 | 61.4384 | 61.4835
3157.0625 | 123.2849 | -61.5921 | 61.5692 | 1.2664 | 1.1271 | 1.2013 | 1.5866 | 1.9636 | 1.2119 | 1.178 | 61.5737 | 0.24405 | 61.4775 | -0.03768 | 0.039079 | 61.6715 | -0.001436 | 61.468 | 62.8585 | 62.7192 | 62.7934 | 63.1787 | 63.5557 | 62.804 | 62.7701 | 123.1658 | 61.8362 | 123.0696 | 61.5544 | 61.6312 | 123.2636 | 61.5907 | 123.0601 | 61.5346 | 61.5752 | 61.4384 | 61.4789
3158.0625 | 123.381 | -61.5372 | 61.5738 | 1.0787 | 0.95766 | 1.0136 | 1.4126 | 1.579 | 1.0379 | 0.98568 | 61.5875 | 0.24863 | 61.4821 | -0.033101 | 0.039079 | 61.6623 | 0.003143 | 61.4405 | 62.6159 | 62.4948 | 62.5508 | 62.9498 | 63.1162 | 62.5751 | 62.5229 | 123.1246 | 61.7858 | 123.0193 | 61.5041 | 61.5762 | 123.1995 | 61.5403 | 122.9777 | 61.5484 | 61.5843 | 61.443 | 61.4789
3159.0781 | 123.3627 | -61.5417 | 61.5234 | 1.1886 | 1.0309 | 1.1235 | 1.4813 | 1.6477 | 1.1478 | 1.0818 | 61.5783 | 0.23948 | 61.4775 | -0.03768 | 0.034501 | 61.6669 | -0.006014 | 61.4405 | 62.7304 | 62.5727 | 62.6652 | 63.0231 | 63.1895 | 62.6895 | 62.6236 | 123.1201 | 61.7812 | 123.0193 | 61.5041 | 61.5762 | 123.2086 | 61.5357 | 122.9822 | 61.5438 | 61.5843 | 61.443 | 61.4835
3160.0625 | 123.3078 | -61.5692 | 61.6241 | 1.097 | 0.94393 | 1.0319 | 1.4035 | 1.5424 | 1.0562 | 1.0132 | 61.5875 | 0.24405 | 61.505 | -0.042259 | 0.043657 | 61.6577 | 0.007721 | 61.4496 | 62.6663 | 62.5131 | 62.6011 | 62.9727 | 63.1116 | 62.6254 | 62.5824 | 123.1567 | 61.8133 | 123.0742 | 61.527 | 61.6129 | 123.2269 | 61.5769 | 123.0189 | 61.5438 | 61.5797 | 61.4613 | 61.4973
3161.0625 | 123.3902 | -61.5189 | 61.5784 | 1.184 | 0.97598 | 1.1189 | 1.4447 | 1.5516 | 1.1386 | 1.0315 | 61.5737 | 0.2349 | 61.5141 | -0.028522 | 0.043657 | 61.6623 | -0.001436 | 61.4542 | 62.7029 | 62.4948 | 62.6378 | 62.9635 | 63.0704 | 62.6575 | 62.5503 | 123.0926 | 61.7538 | 123.033 | 61.4903 | 61.5625 | 123.1812 | 61.5174 | 122.9731 | 61.5301 | 61.5752 | 61.4705 | 61.5156
3162.0625 | 123.2574 | -61.5829 | 61.6196 | 1.3122 | 1.1133 | 1.2471 | 1.5866 | 1.7484 | 1.2622 | 1.1642 | 61.5737 | 0.24863 | 61.5096 | -0.028522 | 0.043657 | 61.6669 | 0.007721 | 61.4634 | 62.8952 | 62.6963 | 62.8301 | 63.1696 | 63.3314 | 62.8452 | 62.7472 | 123.1567 | 61.8316 | 123.0925 | 61.5544 | 61.6266 | 123.2498 | 61.5907 | 123.0463 | 61.5301 | 61.566 | 61.4659 | 61.5018
3163.0938 | 123.3673 | -61.5646 | 61.5417 | 1.2664 | 1.1042 | 1.1968 | 1.5546 | 1.7301 | 1.2256 | 1.1413 | 61.5737 | 0.24405 | 61.505 | -0.033101 | 0.034501 | 61.676 | 0.003143 | 61.4542 | 62.8311 | 62.6688 | 62.7614 | 63.1192 | 63.2947 | 62.7902 | 62.706 | 123.1384 | 61.8087 | 123.0696 | 61.5315 | 61.5991 | 123.2407 | 61.5678 | 123.0189 | 61.5392 | 61.5706 | 61.4705 | 61.5018
3164.0625 | 123.2986 | -61.5646 | 61.6287 | 1.2664 | 1.0721 | 1.1922 | 1.5134 | 1.6843 | 1.2164 | 1.0818 | 61.5783 | 0.25321 | 61.5187 | -0.033101 | 0.043657 | 61.6715 | 0.003143 | 61.468 | 62.8311 | 62.6368 | 62.7568 | 63.078 | 63.249 | 62.7811 | 62.6465 | 123.1429 | 61.8178 | 123.0834 | 61.5315 | 61.6083 | 123.2361 | 61.5678 | 123.0326 | 61.5346 | 61.5752 | 61.4751 | 61.5156
3165.0625 | 123.2758 | -61.5601 | 61.6379 | 1.2481 | 1.0309 | 1.183 | 1.4813 | 1.6111 | 1.2027 | 1.0589 | 61.5783 | 0.24405 | 61.5233 | -0.03768 | 0.043657 | 61.6669 | 0.003143 | 61.4634 | 62.8082 | 62.591 | 62.7431 | 63.0414 | 63.1711 | 62.7628 | 62.619 | 123.1384 | 61.8041 | 123.0834 | 61.5224 | 61.6037 | 123.2269 | 61.5632 | 123.0234 | 61.5346 | 61.5752 | 61.4796 | 61.5202
3166.0625 | 123.2803 | -61.5463 | 61.6013 | 1.358 | 1.1454 | 1.2883 | 1.5958 | 1.7026 | 1.3172 | 1.1688 | 61.5783 | 0.24405 | 61.5096 | -0.03768 | 0.039079 | 61.6715 | 0.003143 | 61.4634 | 62.9043 | 62.6917 | 62.8347 | 63.1421 | 63.249 | 62.8635 | 62.7151 | 123.1246 | 61.7904 | 123.0559 | 61.5086 | 61.5854 | 123.2178 | 61.5495 | 123.0097 | 61.5392 | 61.5752 | 61.4705 | 61.5064
3167.0625 | 123.2391 | -61.5829 | 61.5921 | 1.3031 | 1.1637 | 1.2334 | 1.5775 | 1.6935 | 1.2668 | 1.2329 | 61.5737 | 0.24405 | 61.5096 | -0.03768 | 0.039079 | 61.6715 | -0.001436 | 61.4588 | 62.886 | 62.7467 | 62.8163 | 63.1604 | 63.2764 | 62.8498 | 62.8159 | 123.1567 | 61.827 | 123.0925 | 61.5453 | 61.622 | 123.2544 | 61.5815 | 123.0418 | 61.5346 | 61.5752 | 61.4705 | 61.511
3168.0625 | 123.2712 | -61.5875 | 61.5967 | 1.3534 | 1.2461 | 1.2883 | 1.6461 | 1.8262 | 1.3126 | 1.3611 | 61.5783 | 0.24863 | 61.5096 | -0.033101 | 0.039079 | 61.6806 | -0.006014 | 61.4634 | 62.941 | 62.8337 | 62.8758 | 63.2337 | 63.4138 | 62.9001 | 62.9486 | 123.1658 | 61.8362 | 123.0971 | 61.5544 | 61.6266 | 123.2681 | 61.5815 | 123.0509 | 61.5392 | 61.5843 | 61.4705 | 61.5156
3169.0625 | 123.2803 | -61.5692 | 61.6287 | 1.4908 | 1.4018 | 1.4348 | 1.7926 | 1.9865 | 1.4499 | 1.5122 | 61.5737 | 0.24863 | 61.5004 | -0.028522 | 0.039079 | 61.6852 | 0.003143 | 61.4817 | 63.06 | 62.971 | 63.0041 | 63.3619 | 63.5557 | 63.0192 | 63.0814 | 123.1429 | 61.8178 | 123.0696 | 61.5407 | 61.6083 | 123.2544 | 61.5724 | 123.0509 | 61.5346 | 61.5706 | 61.4613 | 61.4973
3170.0625 | 123.2803 | -61.5692 | 61.5829 | 1.3031 | 1.2141 | 1.238 | 1.6095 | 1.8034 | 1.2622 | 1.3199 | 61.5783 | 0.24405 | 61.505 | -0.03768 | 0.039079 | 61.6806 | 0.003143 | 61.468 | 62.8723 | 62.7833 | 62.8072 | 63.1787 | 63.3726 | 62.8314 | 62.8891 | 123.1475 | 61.8133 | 123.0742 | 61.5315 | 61.6083 | 123.2498 | 61.5724 | 123.0372 | 61.5392 | 61.5752 | 61.4659 | 61.5018
3171.0625 | 123.317 | -61.5738 | 61.6196 | 1.1795 | 1.0859 | 1.1143 | 1.4905 | 1.7164 | 1.1432 | 1.2009 | 61.5783 | 0.23948 | 61.4912 | -0.03768 | 0.043657 | 61.6669 | -0.001436 | 61.4542 | 62.7533 | 62.6597 | 62.6881 | 63.0643 | 63.2902 | 62.717 | 62.7746 | 123.1521 | 61.8133 | 123.065 | 61.5361 | 61.6174 | 123.2407 | 61.5724 | 123.028 | 61.5346 | 61.5797 | 61.4476 | 61.4927
3172.0938 | 123.3902 | -61.5372 | 61.5829 | 1.1383 | 1.0492 | 1.0777 | 1.4722 | 1.7118 | 1.0974 | 1.1551 | 61.5829 | 0.24863 | 61.4821 | -0.03768 | 0.029923 | 61.6669 | -0.001436 | 61.4496 | 62.6754 | 62.5864 | 62.6149 | 63.0093 | 63.249 | 62.6346 | 62.6922 | 123.1201 | 61.7858 | 123.0193 | 61.4995 | 61.5671 | 123.204 | 61.5357 | 122.9868 | 61.553 | 61.5843 | 61.4522 | 61.4835
3173.0625 | 123.3032 | -61.5326 | 61.5784 | 1.1978 | 1.1088 | 1.1189 | 1.5042 | 1.7576 | 1.1432 | 1.2054 | 61.5737 | 0.24405 | 61.4775 | -0.03768 | 0.039079 | 61.676 | -0.001436 | 61.4542 | 62.7304 | 62.6414 | 62.6515 | 63.0368 | 63.2902 | 62.6758 | 62.738 | 123.1063 | 61.7766 | 123.0101 | 61.4949 | 61.5717 | 123.2086 | 61.5312 | 122.9868 | 61.5346 | 61.5752 | 61.4384 | 61.4789
3174.0625 | 123.3215 | -61.5463 | 61.5738 | 1.1886 | 1.0996 | 1.1189 | 1.4676 | 1.7393 | 1.1478 | 1.2054 | 61.5783 | 0.23948 | 61.4684 | -0.033101 | 0.039079 | 61.6669 | -0.001436 | 61.4542 | 62.7349 | 62.6459 | 62.6652 | 63.0139 | 63.2856 | 62.6941 | 62.7518 | 123.1246 | 61.7858 | 123.0147 | 61.5132 | 61.5854 | 123.2132 | 61.5449 | 123.0006 | 61.5392 | 61.5797 | 61.4293 | 61.4698
3175.0625 | 123.317 | -61.5372 | 61.6013 | 1.2207 | 1.1317 | 1.151 | 1.4676 | 1.7393 | 1.1798 | 1.2466 | 61.5691 | 0.23948 | 61.4684 | -0.033101 | 0.043657 | 61.6715 | 0.007721 | 61.4634 | 62.7578 | 62.6688 | 62.6881 | 63.0047 | 63.2764 | 62.717 | 62.7838 | 123.1063 | 61.7766 | 123.0055 | 61.5041 | 61.5808 | 123.2086 | 61.5449 | 123.0006 | 61.5255 | 61.5614 | 61.4247 | 61.4606
3176.0625 | 123.3261 | -61.5646 | 61.5967 | 1.1474 | 1.0584 | 1.0777 | 1.4676 | 1.7072 | 1.0974 | 1.1642 | 61.5783 | 0.24863 | 61.4775 | -0.042259 | 0.043657 | 61.6669 | -0.001436 | 61.4496 | 62.712 | 62.623 | 62.6423 | 63.0322 | 63.2719 | 62.662 | 62.7289 | 123.1429 | 61.8133 | 123.0421 | 61.5224 | 61.6083 | 123.2315 | 61.5632 | 123.0143 | 61.5346 | 61.5797 | 61.4339 | 61.4789
3177.0625 | 123.3902 | -61.5555 | 61.5509 | 1.1016 | 1.0401 | 1.0319 | 1.4493 | 1.666 | 1.0562 | 1.1139 | 61.5829 | 0.25321 | 61.4729 | -0.046838 | 0.039079 | 61.6577 | 0.003143 | 61.4496 | 62.6571 | 62.5956 | 62.5874 | 63.0047 | 63.2215 | 62.6117 | 62.6694 | 123.1384 | 61.8087 | 123.0284 | 61.5086 | 61.5946 | 123.2132 | 61.5586 | 123.0051 | 61.5438 | 61.5797 | 61.4339 | 61.4698
3178.0625 | 123.3353 | -61.5417 | 61.6058 | 1.1199 | 1.0218 | 1.0502 | 1.4401 | 1.6614 | 1.0745 | 1.1413 | 61.5737 | 0.24405 | 61.4867 | -0.042259 | 0.039079 | 61.6531 | 0.003143 | 61.4451 | 62.6617 | 62.5635 | 62.592 | 62.9819 | 63.2032 | 62.6163 | 62.6831 | 123.1155 | 61.7858 | 123.0284 | 61.4995 | 61.5808 | 123.1949 | 61.5449 | 122.9868 | 61.5346 | 61.5706 | 61.4476 | 61.4835
3179.0625 | 123.317 | -61.5829 | 61.5967 | 1.1657 | 1.0767 | 1.0869 | 1.4401 | 1.579 | 1.1203 | 1.1871 | 61.5783 | 0.23948 | 61.4775 | -0.042259 | 0.048236 | 61.6623 | 0.003143 | 61.4542 | 62.7487 | 62.6597 | 62.6698 | 63.023 | 63.162 | 62.7032 | 62.7701 | 123.1613 | 61.8224 | 123.0605 | 61.5407 | 61.6312 | 123.2452 | 61.5861 | 123.0372 | 61.5301 | 61.5752 | 61.4293 | 61.4744
3180.0625 | 123.3261 | -61.5555 | 61.5967 | 1.1016 | 1.008 | 1.0319 | 1.4676 | 1.5928 | 1.0516 | 1.1139 | 61.5829 | 0.24405 | 61.4821 | -0.033101 | 0.039079 | 61.6623 | -0.001436 | 61.4496 | 62.6571 | 62.5635 | 62.5874 | 63.0231 | 63.1483 | 62.6071 | 62.6694 | 123.1384 | 61.7995 | 123.0376 | 61.5224 | 61.5946 | 123.2178 | 61.554 | 123.0051 | 61.5438 | 61.5843 | 61.443 | 61.4835
3181.0625 | 123.2483 | -61.5738 | 61.5921 | 1.0833 | 0.98513 | 1.009 | 1.463 | 1.5973 | 1.0379 | 1.0956 | 61.5783 | 0.24405 | 61.4775 | -0.033101 | 0.034501 | 61.6623 | -0.006014 | 61.4451 | 62.6571 | 62.5589 | 62.5828 | 63.0368 | 63.1711 | 62.6117 | 62.6694 | 123.1521 | 61.8178 | 123.0513 | 61.5407 | 61.6083 | 123.2361 | 61.5678 | 123.0189 | 61.5438 | 61.5843 | 61.443 | 61.4835
3182.0625 | 123.2849 | -61.5601 | 61.5967 | 1.0467 | 1.0034 | 0.98156 | 1.4493 | 1.579 | 1.0104 | 1.0681 | 61.5875 | 0.24863 | 61.4775 | -0.028522 | 0.034501 | 61.6577 | -0.006014 | 61.4451 | 62.6067 | 62.5635 | 62.5416 | 63.0093 | 63.1391 | 62.5705 | 62.6282 | 123.1475 | 61.8087 | 123.0376 | 61.5315 | 61.5946 | 123.2178 | 61.554 | 123.0051 | 61.553 | 61.5935 | 61.443 | 61.4835
3183.0781 | 123.2483 | -61.5601 | 61.6241 | 1.065 | 0.97598 | 0.99987 | 1.4447 | 1.5836 | 1.0287 | 1.0818 | 61.5829 | 0.24863 | 61.4867 | -0.033101 | 0.034501 | 61.6577 | -0.001436 | 61.4588 | 62.6251 | 62.536 | 62.5599 | 63.0047 | 63.1437 | 62.5888 | 62.6419 | 123.1429 | 61.8087 | 123.0467 | 61.527 | 61.5946 | 123.2178 | 61.5586 | 123.0189 | 61.5484 | 61.5843 | 61.4522 | 61.4881
3184.0625 | 123.2437 | -61.5692 | 61.5692 | 1.065 | 0.96682 | 0.98614 | 1.4218 | 1.579 | 1.015 | 1.0727 | 61.5829 | 0.24863 | 61.4958 | -0.042259 | 0.039079 | 61.6623 | 0.003143 | 61.4451 | 62.6342 | 62.536 | 62.5554 | 62.991 | 63.1483 | 62.5842 | 62.6419 | 123.1521 | 61.8178 | 123.065 | 61.527 | 61.6083 | 123.2315 | 61.5724 | 123.0143 | 61.5438 | 61.5797 | 61.4567 | 61.4927
3185.0938 | 123.317 | -61.5646 | 61.5829 | 1.0146 | 0.92561 | 0.95409 | 1.4218 | 1.5745 | 0.96463 | 1.036 | 61.5829 | 0.24863 | 61.5233 | -0.03768 | 0.043657 | 61.6623 | 0.003143 | 61.4588 | 62.5793 | 62.4902 | 62.5187 | 62.9864 | 63.1391 | 62.5293 | 62.6007 | 123.1475 | 61.8133 | 123.0879 | 61.527 | 61.6083 | 123.2269 | 61.5678 | 123.0234 | 61.5392 | 61.5797 | 61.4796 | 61.5202
3186.0625 | 123.2941 | -61.5463 | 61.5829 | 0.96885 | 0.87982 | 0.89914 | 1.3577 | 1.4921 | 0.93258 | 0.98568 | 61.5966 | 0.24863 | 61.5324 | -0.033101 | 0.039079 | 61.6531 | 0.003143 | 61.4496 | 62.5152 | 62.4261 | 62.4455 | 62.904 | 63.0384 | 62.4789 | 62.532 | 123.1429 | 61.795 | 123.0788 | 61.5132 | 61.5854 | 123.1995 | 61.5495 | 122.996 | 61.5575 | 61.5935 | 61.4934 | 61.5293
3187.0938 | 123.3719 | -61.5372 | 61.5738 | 1.033 | 0.93019 | 0.96324 | 1.376 | 1.5195 | 0.98295 | 0.88954 | 61.592 | 0.24405 | 61.5233 | -0.03768 | 0.039079 | 61.6531 | 0.003143 | 61.4496 | 62.5701 | 62.4674 | 62.5004 | 62.9132 | 63.0567 | 62.5201 | 62.4267 | 123.1292 | 61.7812 | 123.0605 | 61.4995 | 61.5762 | 123.1903 | 61.5403 | 122.9868 | 61.553 | 61.5889 | 61.4842 | 61.5202
3188.0625 | 123.2758 | -61.5601 | 61.5967 | 0.98717 | 0.93477 | 0.92204 | 1.3485 | 1.5104 | 0.94632 | 0.99942 | 61.592 | 0.24405 | 61.5233 | -0.042259 | 0.043657 | 61.6531 | -0.006014 | 61.4496 | 62.5472 | 62.4948 | 62.4821 | 62.9086 | 63.0704 | 62.5064 | 62.5595 | 123.1521 | 61.8041 | 123.0834 | 61.5178 | 61.6037 | 123.2132 | 61.554 | 123.0097 | 61.5484 | 61.5981 | 61.4796 | 61.5293
3189.0625 | 123.3078 | -61.528 | 61.6058 | 0.98259 | 0.93019 | 0.92204 | 1.3485 | 1.5058 | 0.94174 | 0.99484 | 61.592 | 0.23948 | 61.5096 | -0.028522 | 0.034501 | 61.6577 | -0.001436 | 61.4451 | 62.5106 | 62.4582 | 62.4501 | 62.8765 | 63.0338 | 62.4698 | 62.5229 | 123.1201 | 61.7675 | 123.0376 | 61.4995 | 61.5625 | 123.1857 | 61.5266 | 122.9731 | 61.5575 | 61.5935 | 61.4751 | 61.511
3190.0781 | 123.2712 | -61.5555 | 61.5784 | 1.0284 | 0.92561 | 0.95409 | 1.344 | 1.5012 | 0.96921 | 0.94906 | 61.5875 | 0.24405 | 61.4958 | -0.03768 | 0.034501 | 61.6577 | -0.001436 | 61.4451 | 62.5839 | 62.4811 | 62.5096 | 62.8994 | 63.0567 | 62.5247 | 62.5045 | 123.1429 | 61.7995 | 123.0513 | 61.5178 | 61.59 | 123.2132 | 61.554 | 123.0006 | 61.553 | 61.5889 | 61.4613 | 61.4973
3191.0625 | 123.2529 | -61.5829 | 61.5829 | 1.0467 | 0.95308 | 0.97698 | 1.3485 | 1.4783 | 1.0058 | 1.004 | 61.5829 | 0.24405 | 61.4867 | -0.03768 | 0.039079 | 61.6486 | -0.001436 | 61.4451 | 62.6296 | 62.536 | 62.5599 | 62.9315 | 63.0613 | 62.5888 | 62.5869 | 123.1658 | 61.827 | 123.0696 | 61.5453 | 61.622 | 123.2315 | 61.5815 | 123.028 | 61.5438 | 61.5843 | 61.4476 | 61.4881
3192.0625 | 123.3856 | -61.528 | 61.5509 | 1.0558 | 0.96682 | 0.98156 | 1.3577 | 1.5012 | 1.0058 | 1.0269 | 61.5783 | 0.25321 | 61.5004 | -0.03768 | 0.034501 | 61.6623 | 0.007721 | 61.4451 | 62.5839 | 62.4948 | 62.5096 | 62.8857 | 63.0292 | 62.5339 | 62.5549 | 123.1063 | 61.7812 | 123.0284 | 61.4903 | 61.5625 | 123.1903 | 61.5357 | 122.9731 | 61.5438 | 61.5706 | 61.4659 | 61.4927
3193.0938 | 123.3215 | -61.528 | 61.5875 | 1.1199 | 1.0263 | 1.0457 | 1.4081 | 1.5836 | 1.0654 | 1.0772 | 61.5829 | 0.24863 | 61.5141 | -0.033101 | 0.034501 | 61.6577 | 0.007721 | 61.4588 | 62.648 | 62.5544 | 62.5737 | 62.9361 | 63.1116 | 62.5934 | 62.6053 | 123.1109 | 61.7766 | 123.0422 | 61.4949 | 61.5625 | 123.1857 | 61.5357 | 122.9868 | 61.5484 | 61.5752 | 61.4796 | 61.5064
3194.0625 | 123.2758 | -61.5921 | 61.5692 | 1.0101 | 1.0172 | 0.94035 | 1.3623 | 1.4966 | 0.96921 | 1.0269 | 61.5875 | 0.24405 | 61.5233 | -0.03768 | 0.039079 | 61.6486 | -0.006014 | 61.4496 | 62.6022 | 62.6093 | 62.5325 | 62.9544 | 63.0887 | 62.5613 | 62.619 | 123.1796 | 61.8362 | 123.1154 | 61.5544 | 61.6312 | 123.2407 | 61.5861 | 123.0417 | 61.5484 | 61.5935 | 61.4842 | 61.5293
3195.0625 | 123.3078 | -61.5555 | 61.5921 | 0.91391 | 0.92103 | 0.8442 | 1.2753 | 1.4005 | 0.87307 | 0.93075 | 61.6012 | 0.24405 | 61.5324 | -0.03768 | 0.034501 | 61.6577 | -0.006014 | 61.4451 | 62.4694 | 62.4765 | 62.3997 | 62.8308 | 62.956 | 62.4285 | 62.4862 | 123.1567 | 61.7995 | 123.0879 | 61.5178 | 61.59 | 123.2132 | 61.5495 | 123.0006 | 61.5667 | 61.6072 | 61.4979 | 61.5385
3196.0625 | 123.2483 | -61.5509 | 61.5829 | 0.98717 | 0.90272 | 0.91746 | 1.2753 | 1.3776 | 0.94174 | 0.98111 | 61.6012 | 0.25779 | 61.5187 | -0.042259 | 0.043657 | 61.6531 | -0.006014 | 61.4542 | 62.5381 | 62.4536 | 62.4684 | 62.8262 | 62.9285 | 62.4926 | 62.532 | 123.1521 | 61.8087 | 123.0696 | 61.5086 | 61.5946 | 123.204 | 61.5449 | 123.0051 | 61.5575 | 61.6072 | 61.4751 | 61.5247
3197.0938 | 123.3261 | -61.5692 | 61.615 | 0.9597 | 0.87524 | 0.89914 | 1.2432 | 1.3547 | 0.91885 | 0.98111 | 61.5875 | 0.24405 | 61.5096 | -0.046838 | 0.043657 | 61.6486 | 0.007721 | 61.4451 | 62.5289 | 62.4445 | 62.4684 | 62.8124 | 62.9239 | 62.4881 | 62.5503 | 123.1567 | 61.8133 | 123.0788 | 61.5224 | 61.6129 | 123.2178 | 61.5769 | 123.0143 | 61.5438 | 61.5797 | 61.4659 | 61.5018
3198.0625 | 123.2758 | -61.5509 | 61.6058 | 0.97801 | 0.88898 | 0.9083 | 1.289 | 1.4234 | 0.93258 | 0.99484 | 61.592 | 0.23948 | 61.4912 | -0.042259 | 0.039079 | 61.6577 | 0.003143 | 61.4405 | 62.5289 | 62.4399 | 62.4592 | 62.8399 | 62.9743 | 62.4835 | 62.5457 | 123.1429 | 61.7904 | 123.0421 | 61.5086 | 61.59 | 123.2086 | 61.554 | 122.9914 | 61.553 | 61.5889 | 61.4522 | 61.4881
3199.0938 | 123.3719 | -61.5601 | 61.5601 | 0.88644 | 0.80198 | 0.82588 | 1.2249 | 1.3868 | 0.83644 | 0.91243 | 61.6012 | 0.24405 | 61.4912 | -0.042259 | 0.039079 | 61.6486 | 0.003143 | 61.4313 | 62.4465 | 62.362 | 62.3859 | 62.785 | 62.9468 | 62.3965 | 62.4725 | 123.1613 | 61.8041 | 123.0513 | 61.5178 | 61.5991 | 123.2086 | 61.5632 | 122.9914 | 61.5621 | 61.5981 | 61.4522 | 61.4881
3200.0625 | 123.2986 | -61.5784 | 61.6058 | 0.94138 | 0.82946 | 0.87167 | 1.2249 | 1.4325 | 0.90054 | 0.94906 | 61.592 | 0.24405 | 61.5187 | -0.03768 | 0.039079 | 61.6531 | -0.001436 | 61.4359 | 62.5198 | 62.4078 | 62.45 | 62.8033 | 63.0109 | 62.4789 | 62.5274 | 123.1704 | 61.8224 | 123.0971 | 61.5407 | 61.6174 | 123.2315 | 61.5769 | 123.0143 | 61.553 | 61.5935 | 61.4796 | 61.5202
3201.0938 | 123.3032 | -61.5326 | 61.6196 | 0.92307 | 0.81114 | 0.85794 | 1.2158 | 1.4051 | 0.88222 | 0.94448 | 61.5966 | 0.24405 | 61.5279 | -0.033101 | 0.039079 | 61.6531 | 0.003143 | 61.4496 | 62.4557 | 62.3437 | 62.3905 | 62.7483 | 62.9377 | 62.4148 | 62.4771 | 123.1292 | 61.7766 | 123.0605 | 61.4995 | 61.5717 | 123.1857 | 61.5357 | 122.9822 | 61.5575 | 61.5935 | 61.4888 | 61.5247
3202.0625 | 123.381 | -61.5372 | 61.5509 | 0.95054 | 0.80656 | 0.88083 | 1.2249 | 1.428 | 0.90969 | 0.97195 | 61.592 | 0.24863 | 61.5279 | -0.042259 | 0.034501 | 61.644 | 0.003143 | 61.4313 | 62.4877 | 62.3437 | 62.418 | 62.7621 | 62.9651 | 62.4469 | 62.5091 | 123.1292 | 61.7858 | 123.065 | 61.4949 | 61.5717 | 123.1812 | 61.5403 | 122.9685 | 61.5575 | 61.5889 | 61.4934 | 61.5247
3203.0625 | 123.262 | -61.5738 | 61.5784 | 0.95512 | 0.80656 | 0.88541 | 1.1974 | 1.428 | 0.90969 | 0.97195 | 61.5966 | 0.24405 | 61.5233 | -0.03768 | 0.029923 | 61.6531 | -0.006014 | 61.4405 | 62.5289 | 62.3804 | 62.4592 | 62.7712 | 63.0018 | 62.4835 | 62.5457 | 123.1704 | 61.8178 | 123.0971 | 61.5361 | 61.6037 | 123.2269 | 61.5678 | 123.0143 | 61.5667 | 61.6026 | 61.4934 | 61.5293
3204.0781 | 123.2941 | -61.5555 | 61.6058 | 1.0467 | 0.89814 | 0.97698 | 1.2936 | 1.5333 | 1.0013 | 1.0635 | 61.5875 | 0.24405 | 61.4912 | -0.033101 | 0.039079 | 61.6486 | -0.001436 | 61.4451 | 62.6022 | 62.4536 | 62.5325 | 62.8491 | 63.0887 | 62.5567 | 62.619 | 123.1429 | 61.7995 | 123.0467 | 61.5224 | 61.5946 | 123.204 | 61.554 | 123.0006 | 61.5484 | 61.5889 | 61.4522 | 61.4927
3205.0625 | 123.2986 | -61.5692 | 61.5784 | 1.1016 | 0.85693 | 1.0273 | 1.2753 | 1.4509 | 1.0562 | 0.83003 | 61.5829 | 0.24863 | 61.4867 | -0.03768 | 0.029923 | 61.6577 | -0.006014 | 61.4359 | 62.6708 | 62.4261 | 62.5966 | 62.8445 | 63.0201 | 62.6254 | 62.3992 | 123.1521 | 61.8178 | 123.0559 | 61.5315 | 61.5991 | 123.2269 | 61.5632 | 123.0051 | 61.553 | 61.5889 | 61.4567 | 61.4927
3206.0625 | 123.2803 | -61.5692 | 61.5784 | 1.1657 | 0.92103 | 1.0914 | 1.344 | 1.5516 | 1.1157 | 0.89412 | 61.5829 | 0.24405 | 61.5233 | -0.033101 | 0.039079 | 61.6623 | 0.003143 | 61.4405 | 62.7349 | 62.4902 | 62.6607 | 62.9132 | 63.1208 | 62.6849 | 62.4633 | 123.1521 | 61.8133 | 123.0925 | 61.5361 | 61.6083 | 123.2315 | 61.5724 | 123.0097 | 61.5438 | 61.5797 | 61.4842 | 61.5202
3207.0625 | 123.4039 | -61.5738 | 61.5189 | 1.1016 | 0.93935 | 1.0365 | 1.3989 | 1.547 | 1.0654 | 0.88954 | 61.5875 | 0.24863 | 61.5141 | -0.042259 | 0.034501 | 61.6531 | -0.001436 | 61.4451 | 62.6754 | 62.5131 | 62.6103 | 62.9727 | 63.1208 | 62.6392 | 62.4633 | 123.1613 | 61.8224 | 123.0879 | 61.5315 | 61.6083 | 123.2269 | 61.5724 | 123.0189 | 61.553 | 61.5889 | 61.4796 | 61.5156
3208.0781 | 123.2986 | -61.5372 | 61.5738 | 1.0375 | 0.87982 | 0.95866 | 1.3302 | 1.4188 | 0.98752 | 0.83461 | 61.592 | 0.24405 | 61.5004 | -0.03768 | 0.048236 | 61.6531 | 0.003143 | 61.4451 | 62.5747 | 62.417 | 62.4958 | 62.8674 | 62.956 | 62.5247 | 62.3718 | 123.1292 | 61.7812 | 123.0376 | 61.4995 | 61.5854 | 123.1903 | 61.5403 | 122.9822 | 61.5438 | 61.5889 | 61.4522 | 61.4973
3209.0625 | 123.2941 | -61.5738 | 61.5692 | 1.033 | 0.87066 | 0.95866 | 1.3485 | 1.428 | 0.98752 | 0.83461 | 61.5875 | 0.24863 | 61.4912 | -0.033101 | 0.039079 | 61.6531 | 0.007721 | 61.4359 | 62.6067 | 62.4445 | 62.5325 | 62.9223 | 63.0018 | 62.5613 | 62.4084 | 123.1613 | 61.8224 | 123.065 | 61.5407 | 61.6129 | 123.2269 | 61.5815 | 123.0097 | 61.5484 | 61.5797 | 61.4522 | 61.4835
3210.0625 | 123.3765 | -61.5234 | 61.5417 | 0.98717 | 0.8844 | 0.99987 | 1.3531 | 1.4783 | 0.93716 | 0.86207 | 61.5875 | 0.25321 | 61.4867 | -0.03768 | 0.039079 | 61.6531 | 0.003143 | 61.4313 | 62.5106 | 62.4078 | 62.5233 | 62.8765 | 63.0018 | 62.4606 | 62.3855 | 123.1109 | 61.7766 | 123.0101 | 61.4858 | 61.5625 | 123.1766 | 61.5266 | 122.9548 | 61.5484 | 61.5843 | 61.4476 | 61.4835
3211.0625 | 123.3719 | -61.5509 | 61.5509 | 1.0787 | 0.9714 | 1.0136 | 1.4401 | 1.6019 | 1.0333 | 0.93075 | 61.5829 | 0.23948 | 61.4775 | -0.033101 | 0.039079 | 61.6577 | -0.001436 | 61.4359 | 62.6296 | 62.5223 | 62.5645 | 62.991 | 63.1528 | 62.5842 | 62.4816 | 123.1338 | 61.7904 | 123.0284 | 61.5178 | 61.59 | 123.2086 | 61.5495 | 122.9868 | 61.5438 | 61.5843 | 61.4384 | 61.4789
3212.0625 | 123.3673 | -61.5234 | 61.5921 | 0.96885 | 0.88898 | 0.9083 | 1.3302 | 1.428 | 0.92801 | 0.80714 | 61.592 | 0.23948 | 61.5187 | -0.03768 | 0.039079 | 61.6531 | 0.003143 | 61.4496 | 62.4923 | 62.4124 | 62.4317 | 62.8537 | 62.9514 | 62.4514 | 62.3306 | 123.1155 | 61.7629 | 123.0422 | 61.4858 | 61.5625 | 123.1766 | 61.5266 | 122.9731 | 61.553 | 61.5889 | 61.4796 | 61.5156
3213.0625 | 123.381 | -61.5555 | 61.5417 | 0.9597 | 0.8844 | 0.88999 | 1.3119 | 1.4325 | 0.90969 | 0.77051 | 61.6012 | 0.24405 | 61.5324 | -0.033101 | 0.034501 | 61.6394 | -0.006014 | 61.4313 | 62.5152 | 62.4399 | 62.4455 | 62.8674 | 62.988 | 62.4652 | 62.326 | 123.1567 | 61.7995 | 123.0879 | 61.5224 | 61.59 | 123.1949 | 61.5495 | 122.9868 | 61.5667 | 61.6072 | 61.4979 | 61.5385
3214.0625 | 123.3856 | -61.5417 | 61.5372 | 1.0101 | 0.9714 | 0.94493 | 1.3714 | 1.4783 | 0.96921 | 1.0177 | 61.592 | 0.2349 | 61.5187 | -0.03768 | 0.039079 | 61.6577 | -0.001436 | 61.4359 | 62.5518 | 62.5131 | 62.4867 | 62.9132 | 63.0201 | 62.511 | 62.5595 | 123.1338 | 61.7766 | 123.0605 | 61.5041 | 61.5808 | 123.1995 | 61.5403 | 122.9777 | 61.553 | 61.5935 | 61.4796 | 61.5202
3215.0625 | 123.3261 | -61.5646 | 61.615 | 1.0513 | 1.008 | 0.98614 | 1.3394 | 1.4051 | 1.0104 | 1.0727 | 61.592 | 0.25321 | 61.5233 | -0.042259 | 0.043657 | 61.6623 | 0.003143 | 61.4496 | 62.6159 | 62.5727 | 62.5508 | 62.904 | 62.9697 | 62.5751 | 62.6373 | 123.1567 | 61.8178 | 123.0879 | 61.5224 | 61.6083 | 123.2269 | 61.5678 | 123.0143 | 61.5484 | 61.5889 | 61.4796 | 61.5202
3216.0625 | 123.3627 | -61.5784 | 61.5646 | 1.0421 | 1.0172 | 0.97698 | 1.3302 | 1.428 | 1.0013 | 1.0635 | 61.5875 | 0.24863 | 61.4912 | -0.042259 | 0.029923 | 61.6623 | 0.007721 | 61.4451 | 62.6205 | 62.5956 | 62.5553 | 62.9086 | 63.0063 | 62.5796 | 62.6419 | 123.1658 | 61.827 | 123.0696 | 61.5361 | 61.6083 | 123.2407 | 61.5861 | 123.0234 | 61.5575 | 61.5797 | 61.4613 | 61.4835
3217.0625 | 123.3902 | -61.528 | 61.5646 | 1.0238 | 1.0676 | 0.95409 | 1.3256 | 1.4051 | 0.96921 | 1.036 | 61.5783 | 0.25321 | 61.4867 | -0.03768 | 0.039079 | 61.6577 | 0.012299 | 61.4405 | 62.5518 | 62.5956 | 62.4821 | 62.8537 | 62.9331 | 62.4972 | 62.5641 | 123.1063 | 61.7812 | 123.0147 | 61.4903 | 61.5671 | 123.1857 | 61.5403 | 122.9685 | 61.5392 | 61.566 | 61.4476 | 61.4744
3218.0625 | 123.3261 | -61.5463 | 61.5509 | 1.0742 | 1.1271 | 0.99529 | 1.3394 | 1.3822 | 1.0242 | 1.0772 | 61.5783 | 0.24405 | 61.4958 | -0.03768 | 0.043657 | 61.6623 | -0.001436 | 61.4496 | 62.6205 | 62.6734 | 62.5416 | 62.8857 | 62.9285 | 62.5705 | 62.6236 | 123.1246 | 61.7904 | 123.0421 | 61.5086 | 61.59 | 123.2086 | 61.5449 | 122.996 | 61.5346 | 61.5797 | 61.4522 | 61.4973
3219.0625 | 123.3536 | -61.5646 | 61.5555 | 1.0238 | 1.1271 | 0.95866 | 1.3348 | 1.341 | 0.97837 | 1.0498 | 61.5875 | 0.24863 | 61.5141 | -0.042259 | 0.039079 | 61.6577 | -0.001436 | 61.4451 | 62.5884 | 62.6917 | 62.5233 | 62.8994 | 62.9056 | 62.543 | 62.6144 | 123.1521 | 61.8133 | 123.0788 | 61.5224 | 61.6037 | 123.2224 | 61.5632 | 123.0097 | 61.5484 | 61.5889 | 61.4751 | 61.5156
3220.0625 | 123.2941 | -61.5417 | 61.6104 | 1.033 | 1.2003 | 0.96782 | 1.4035 | 1.3776 | 0.9921 | 1.0589 | 61.5875 | 0.24405 | 61.5233 | -0.03768 | 0.034501 | 61.6623 | -0.001436 | 61.4588 | 62.5747 | 62.7421 | 62.5096 | 62.9452 | 62.9194 | 62.5339 | 62.6007 | 123.1292 | 61.7858 | 123.065 | 61.5041 | 61.5762 | 123.204 | 61.5403 | 123.0006 | 61.553 | 61.5889 | 61.4888 | 61.5247
3221.0625 | 123.3215 | -61.5555 | 61.5601 | 0.84981 | 1.0172 | 0.78926 | 1.3256 | 1.3593 | 0.81355 | 0.87123 | 61.5966 | 0.24863 | 61.5279 | -0.03768 | 0.039079 | 61.644 | -0.001436 | 61.4451 | 62.4053 | 62.5727 | 62.3447 | 62.8811 | 62.9148 | 62.369 | 62.4267 | 123.1521 | 61.8041 | 123.0834 | 61.5178 | 61.5946 | 123.1995 | 61.554 | 123.0006 | 61.5575 | 61.5981 | 61.4888 | 61.5293
3222.0938 | 123.2986 | -61.5646 | 61.5921 | 0.97801 | 0.97598 | 0.91288 | 1.3211 | 1.4234 | 0.93258 | 0.99942 | 61.592 | 0.24405 | 61.5187 | -0.03768 | 0.034501 | 61.6577 | -0.001436 | 61.4496 | 62.5426 | 62.5406 | 62.4775 | 62.8857 | 62.988 | 62.4972 | 62.5641 | 123.1567 | 61.8087 | 123.0834 | 61.527 | 61.5991 | 123.2224 | 61.5632 | 123.0143 | 61.5575 | 61.5935 | 61.4842 | 61.5202
3223.0625 | 123.3215 | -61.5555 | 61.5601 | 1.0513 | 1.0355 | 0.97698 | 1.4584 | 1.5928 | 1.0013 | 1.0681 | 61.5783 | 0.23948 | 61.4912 | -0.03768 | 0.039079 | 61.6623 | -0.001436 | 61.4496 | 62.6067 | 62.591 | 62.5325 | 63.0139 | 63.1483 | 62.5567 | 62.6236 | 123.1338 | 61.795 | 123.0467 | 61.5178 | 61.5946 | 123.2178 | 61.554 | 123.0051 | 61.5392 | 61.5797 | 61.4522 | 61.4927
3224.0938 | 123.3902 | -61.528 | 61.5555 | 0.84981 | 0.85235 | 0.77552 | 1.2936 | 1.2906 | 0.80897 | 0.86207 | 61.6012 | 0.24863 | 61.4958 | -0.03768 | 0.029923 | 61.6486 | 0.003143 | 61.4405 | 62.3778 | 62.3804 | 62.3035 | 62.8216 | 62.8186 | 62.337 | 62.3901 | 123.1292 | 61.7766 | 123.0238 | 61.4903 | 61.5579 | 123.1766 | 61.5312 | 122.9685 | 61.5713 | 61.5981 | 61.4659 | 61.4927
3225.0625 | 123.3078 | -61.5601 | 61.615 | 0.88644 | 0.83861 | 0.81673 | 1.3073 | 1.2723 | 0.84102 | 0.90328 | 61.5966 | 0.24405 | 61.5141 | -0.033101 | 0.039079 | 61.6486 | -0.001436 | 61.4451 | 62.4465 | 62.3987 | 62.3768 | 62.8674 | 62.8324 | 62.4011 | 62.4633 | 123.1567 | 61.8041 | 123.0742 | 61.527 | 61.5991 | 123.2086 | 61.5586 | 123.0051 | 61.5575 | 61.5981 | 61.4751 | 61.5156
3226.0625 | 123.436 | -61.5051 | 61.5784 | 1.065 | 1.0447 | 0.99987 | 1.4996 | 1.5287 | 1.0242 | 1.091 | 61.592 | 0.24405 | 61.5233 | -0.033101 | 0.039079 | 61.6669 | 0.007721 | 61.4588 | 62.5701 | 62.5498 | 62.505 | 63.0047 | 63.0338 | 62.5293 | 62.5961 | 123.0972 | 61.7492 | 123.0284 | 61.472 | 61.5442 | 123.172 | 61.5128 | 122.9639 | 61.553 | 61.5843 | 61.4842 | 61.5156
3227.0625 | 123.3215 | -61.5189 | 61.6058 | 0.92765 | 0.92561 | 0.86251 | 1.3165 | 1.3227 | 0.89138 | 0.94906 | 61.6012 | 0.24863 | 61.537 | -0.042259 | 0.039079 | 61.6486 | 0.003143 | 61.4496 | 62.4465 | 62.4445 | 62.3814 | 62.8353 | 62.8415 | 62.4102 | 62.4679 | 123.1201 | 61.7675 | 123.0559 | 61.4766 | 61.5579 | 123.1674 | 61.522 | 122.9685 | 61.5621 | 61.5981 | 61.4979 | 61.5339
3228.0625 | 123.3398 | -61.5097 | 61.5921 | 0.93223 | 0.99429 | 0.86251 | 1.3211 | 1.2769 | 0.8868 | 0.94906 | 61.5966 | 0.24405 | 61.5279 | -0.03768 | 0.039079 | 61.6486 | -0.006014 | 61.4359 | 62.4419 | 62.504 | 62.3722 | 62.8308 | 62.7866 | 62.3965 | 62.4588 | 123.1063 | 61.7538 | 123.0376 | 61.472 | 61.5488 | 123.1583 | 61.5037 | 122.9456 | 61.5575 | 61.6026 | 61.4888 | 61.5339
3229.0625 | 123.3444 | -61.5189 | 61.6104 | 0.95054 | 1.008 | 0.86709 | 1.289 | 1.2998 | 0.89596 | 0.95364 | 61.592 | 0.24863 | 61.5141 | -0.03768 | 0.043657 | 61.6531 | 0.003143 | 61.4496 | 62.4694 | 62.5269 | 62.386 | 62.8079 | 62.8186 | 62.4148 | 62.4725 | 123.1109 | 61.7675 | 123.033 | 61.4812 | 61.5625 | 123.172 | 61.522 | 122.9685 | 61.5484 | 61.5889 | 61.4705 | 61.511
3230.0625 | 123.4314 | -61.5097 | 61.5463 | 1.0238 | 1.0172 | 0.95866 | 1.2753 | 1.3181 | 0.98295 | 1.0498 | 61.5875 | 0.24863 | 61.4912 | -0.03768 | 0.039079 | 61.6531 | -0.001436 | 61.4451 | 62.5335 | 62.5269 | 62.4684 | 62.785 | 62.8278 | 62.4927 | 62.5595 | 123.0972 | 61.7583 | 123.0009 | 61.472 | 61.5488 | 123.1628 | 61.5083 | 122.9548 | 61.5484 | 61.5889 | 61.4522 | 61.4927
3231.0625 | 123.3078 | -61.5829 | 61.5875 | 1.3397 | 1.2644 | 1.27 | 1.6278 | 1.7805 | 1.2897 | 1.3474 | 61.5691 | 0.24405 | 61.4775 | -0.033101 | 0.039079 | 61.6806 | -0.001436 | 61.4725 | 62.9226 | 62.8474 | 62.853 | 63.2108 | 63.3634 | 62.8726 | 62.9303 | 123.1521 | 61.827 | 123.0605 | 61.5498 | 61.622 | 123.2636 | 61.5815 | 123.0555 | 61.5301 | 61.5706 | 61.4384 | 61.4789
3232.1094 | 123.3856 | -61.5784 | 61.5509 | 1.4038 | 1.3972 | 1.3295 | 1.7102 | 1.8262 | 1.3584 | 1.416 | 61.56 | 0.24405 | 61.4867 | -0.03768 | 0.039079 | 61.6852 | 0.003143 | 61.4634 | 62.9822 | 62.9756 | 62.9079 | 63.2886 | 63.4046 | 62.9367 | 62.9944 | 123.1384 | 61.8224 | 123.065 | 61.5407 | 61.6174 | 123.2636 | 61.5815 | 123.0418 | 61.5209 | 61.5568 | 61.4476 | 61.4835
3233.0625 | 123.2712 | -61.5738 | 61.6196 | 1.3946 | 1.4293 | 1.3204 | 1.6736 | 1.8583 | 1.3538 | 1.4069 | 61.5691 | 0.24405 | 61.505 | -0.03768 | 0.043657 | 61.676 | 0.003143 | 61.4771 | 62.9684 | 63.0031 | 62.8942 | 63.2474 | 63.4321 | 62.9276 | 62.9807 | 123.1429 | 61.8178 | 123.0788 | 61.5361 | 61.6174 | 123.2498 | 61.5769 | 123.0509 | 61.5255 | 61.566 | 61.4613 | 61.5018
3234.0938 | 123.3902 | -61.5555 | 61.5784 | 1.0467 | 1.1317 | 0.97698 | 1.3668 | 1.3868 | 1.0013 | 1.0635 | 61.5966 | 0.24863 | 61.5324 | -0.03768 | 0.039079 | 61.6623 | -0.001436 | 61.4542 | 62.6022 | 62.6871 | 62.5325 | 62.9223 | 62.9422 | 62.5567 | 62.619 | 123.1521 | 61.8041 | 123.0879 | 61.5178 | 61.5946 | 123.2178 | 61.554 | 123.0097 | 61.5575 | 61.5981 | 61.4934 | 61.5339
3235.0625 | 123.2941 | -61.5738 | 61.6333 | 1.4175 | 1.4064 | 1.3478 | 1.7148 | 1.8903 | 1.3767 | 1.4298 | 61.5646 | 0.24405 | 61.5004 | -0.028522 | 0.039079 | 61.6715 | -0.001436 | 61.4725 | 62.9913 | 62.9802 | 62.9216 | 63.2886 | 63.4641 | 62.9505 | 63.0036 | 123.1384 | 61.8178 | 123.0742 | 61.5453 | 61.6129 | 123.2452 | 61.5724 | 123.0463 | 61.5255 | 61.566 | 61.4613 | 61.5018
3236.0938 | 123.4085 | -61.528 | 61.5829 | 1.3992 | 1.3423 | 1.325 | 1.7102 | 1.8949 | 1.3492 | 1.4115 | 61.5737 | 0.24863 | 61.4958 | -0.028522 | 0.034501 | 61.6806 | -0.006014 | 61.468 | 62.9272 | 62.8703 | 62.853 | 63.2382 | 63.4229 | 62.8772 | 62.9395 | 123.1017 | 61.7766 | 123.0238 | 61.4995 | 61.5625 | 123.2086 | 61.522 | 122.996 | 61.5392 | 61.5797 | 61.4613 | 61.5018
3237.0625 | 123.2803 | -61.5692 | 61.5784 | 1.3077 | 1.2003 | 1.238 | 1.5362 | 1.6889 | 1.2714 | 1.3245 | 61.5737 | 0.24863 | 61.4958 | -0.03768 | 0.034501 | 61.6715 | 0.007721 | 61.4588 | 62.8769 | 62.7696 | 62.8072 | 63.1055 | 63.2581 | 62.8406 | 62.8937 | 123.1429 | 61.8178 | 123.065 | 61.5315 | 61.6037 | 123.2407 | 61.5769 | 123.028 | 61.5392 | 61.566 | 61.4613 | 61.4881
3238.1094 | 123.2712 | -61.5509 | 61.6013 | 1.4633 | 1.2644 | 1.3936 | 1.6278 | 1.8583 | 1.4179 | 1.4847 | 61.5737 | 0.23948 | 61.4821 | -0.03768 | 0.048236 | 61.6852 | -0.001436 | 61.4634 | 63.0142 | 62.8153 | 62.9445 | 63.1787 | 63.4092 | 62.9688 | 63.0356 | 123.1246 | 61.7904 | 123.033 | 61.5132 | 61.5991 | 123.2361 | 61.5495 | 123.0143 | 61.5255 | 61.5752 | 61.4339 | 61.4835
3239.0625 | 123.3307 | -61.5692 | 61.5921 | 1.4816 | 1.2507 | 1.4165 | 1.6461 | 1.8674 | 1.4362 | 1.4939 | 61.5691 | 0.24863 | 61.505 | -0.033101 | 0.034501 | 61.676 | -0.001436 | 61.4634 | 63.0508 | 62.8199 | 62.9857 | 63.2153 | 63.4367 | 63.0054 | 63.0631 | 123.1384 | 61.8178 | 123.0742 | 61.5361 | 61.6037 | 123.2452 | 61.5678 | 123.0326 | 61.5346 | 61.5706 | 61.4705 | 61.5064
3240.0625 | 123.2849 | -61.5601 | 61.6287 | 1.2161 | 1.0813 | 1.1418 | 1.4676 | 1.5836 | 1.1707 | 1.2375 | 61.5875 | 0.25321 | 61.5187 | -0.033101 | 0.039079 | 61.6715 | -0.001436 | 61.4542 | 62.7761 | 62.6413 | 62.7019 | 63.0276 | 63.1437 | 62.7307 | 62.7975 | 123.1475 | 61.8133 | 123.0788 | 61.527 | 61.5991 | 123.2315 | 61.5586 | 123.0143 | 61.5484 | 61.5889 | 61.4796 | 61.5202
3241.0781 | 123.3948 | -61.5417 | 61.5829 | 1.1795 | 1.1225 | 1.1098 | 1.4538 | 1.6111 | 1.1386 | 1.1871 | 61.5966 | 0.24405 | 61.5279 | -0.033101 | 0.048236 | 61.6715 | 0.007721 | 61.4496 | 62.7212 | 62.6642 | 62.6515 | 62.9956 | 63.1528 | 62.6804 | 62.7289 | 123.1384 | 61.7858 | 123.0696 | 61.5086 | 61.59 | 123.2132 | 61.5495 | 122.9914 | 61.5484 | 61.5889 | 61.4796 | 61.5202
3242.0625 | 123.3536 | -61.5601 | 61.5601 | 1.184 | 1.1225 | 1.1235 | 1.4264 | 1.5653 | 1.1478 | 1.2054 | 61.592 | 0.24863 | 61.5279 | -0.03768 | 0.039079 | 61.6669 | 0.003143 | 61.4359 | 62.7441 | 62.6826 | 62.6836 | 62.9864 | 63.1254 | 62.7078 | 62.7655 | 123.1521 | 61.8087 | 123.0879 | 61.5224 | 61.5991 | 123.2269 | 61.5632 | 122.996 | 61.553 | 61.5889 | 61.4888 | 61.5247
3243.0938 | 123.4268 | -61.5326 | 61.5555 | 1.4725 | 1.3789 | 1.4074 | 1.6507 | 1.8903 | 1.4271 | 1.4939 | 61.5691 | 0.24863 | 61.505 | -0.03768 | 0.039079 | 61.6852 | 0.003143 | 61.4542 | 63.0051 | 62.9115 | 62.94 | 63.1833 | 63.4229 | 62.9596 | 63.0265 | 123.1017 | 61.7812 | 123.0376 | 61.4949 | 61.5717 | 123.2178 | 61.5357 | 122.9868 | 61.5301 | 61.566 | 61.4659 | 61.5018
3244.0625 | 123.317 | -61.5555 | 61.6241 | 1.4679 | 1.4384 | 1.4028 | 1.7102 | 1.9636 | 1.4133 | 1.4847 | 61.5737 | 0.24863 | 61.4958 | -0.03768 | 0.039079 | 61.6806 | 0.003143 | 61.4588 | 63.0234 | 62.9939 | 62.9583 | 63.2657 | 63.5191 | 62.9688 | 63.0402 | 123.1292 | 61.8041 | 123.0513 | 61.5178 | 61.5946 | 123.2361 | 61.5586 | 123.0143 | 61.5346 | 61.5706 | 61.4567 | 61.4927
3245.0625 | 123.2986 | -61.5784 | 61.6058 | 1.4221 | 1.411 | 1.3478 | 1.6644 | 1.9453 | 1.3813 | 1.4527 | 61.5783 | 0.24405 | 61.4729 | -0.03768 | 0.048236 | 61.6852 | 0.007721 | 61.4542 | 63.0005 | 62.9893 | 62.9262 | 63.2428 | 63.5236 | 62.9596 | 63.031 | 123.1567 | 61.8224 | 123.0513 | 61.5407 | 61.6266 | 123.2636 | 61.5861 | 123.0326 | 61.5301 | 61.5706 | 61.4247 | 61.4652
3246.0781 | 123.4177 | -61.5463 | 61.5784 | 1.2573 | 1.182 | 1.1876 | 1.3943 | 1.5653 | 1.2164 | 1.2741 | 61.5875 | 0.23948 | 61.505 | -0.023943 | 0.043657 | 61.6715 | 0.003143 | 61.4451 | 62.8036 | 62.7283 | 62.7339 | 62.9406 | 63.1116 | 62.7628 | 62.8204 | 123.1338 | 61.7858 | 123.0513 | 61.5224 | 61.59 | 123.2178 | 61.5495 | 122.9914 | 61.5438 | 61.5843 | 61.4613 | 61.5018
3247.0625 | 123.3078 | -61.5875 | 61.5738 | 1.3763 | 1.2278 | 1.3021 | 1.4355 | 1.6385 | 1.3309 | 1.3931 | 61.5737 | 0.24405 | 61.5096 | -0.033101 | 0.039079 | 61.6715 | -0.001436 | 61.4313 | 62.9639 | 62.8153 | 62.8896 | 63.023 | 63.2261 | 62.9184 | 62.9807 | 123.1613 | 61.8316 | 123.0971 | 61.5544 | 61.6266 | 123.259 | 61.5861 | 123.0189 | 61.5346 | 61.5752 | 61.4705 | 61.511
3248.0625 | 123.317 | -61.5372 | 61.6013 | 1.3077 | 1.1958 | 1.2334 | 1.4126 | 1.6157 | 1.2576 | 1.3245 | 61.5829 | 0.25321 | 61.5141 | -0.03768 | 0.039079 | 61.676 | -0.001436 | 61.4542 | 62.8448 | 62.7329 | 62.7706 | 62.9498 | 63.1528 | 62.7948 | 62.8616 | 123.1201 | 61.7904 | 123.0513 | 61.4995 | 61.5762 | 123.2132 | 61.5357 | 122.9914 | 61.5438 | 61.5843 | 61.4751 | 61.5156
3249.0938 | 123.3261 | -61.528 | 61.5875 | 1.2298 | 1.1225 | 1.1693 | 1.376 | 1.5058 | 1.1844 | 1.2558 | 61.5875 | 0.23948 | 61.5233 | -0.03768 | 0.043657 | 61.6577 | -0.001436 | 61.4451 | 62.7578 | 62.6505 | 62.6973 | 62.904 | 63.0338 | 62.7124 | 62.7838 | 123.1155 | 61.7675 | 123.0513 | 61.4903 | 61.5717 | 123.1857 | 61.5266 | 122.9731 | 61.5438 | 61.5889 | 61.4796 | 61.5247
3250.0625 | 123.3261 | -61.5784 | 61.5921 | 1.1474 | 1.0813 | 1.0823 | 1.3256 | 1.3364 | 1.102 | 1.1688 | 61.5966 | 0.24405 | 61.5279 | -0.033101 | 0.039079 | 61.6623 | -0.001436 | 61.4359 | 62.7258 | 62.6597 | 62.6607 | 62.904 | 62.9148 | 62.6804 | 62.7472 | 123.175 | 61.8224 | 123.1062 | 61.5453 | 61.6174 | 123.2407 | 61.5769 | 123.0143 | 61.5575 | 61.5981 | 61.4888 | 61.5293
3251.0625 | 123.2758 | -61.5509 | 61.6241 | 1.1703 | 1.0813 | 1.1052 | 1.3302 | 1.3547 | 1.1295 | 1.1871 | 61.5875 | 0.24405 | 61.5233 | -0.03768 | 0.048236 | 61.6669 | -0.001436 | 61.4359 | 62.7212 | 62.6322 | 62.6561 | 62.8811 | 62.9056 | 62.6804 | 62.738 | 123.1384 | 61.795 | 123.0742 | 61.5132 | 61.5991 | 123.2178 | 61.5495 | 122.9868 | 61.5392 | 61.5889 | 61.4751 | 61.5247
3252.1094 | 123.4268 | -61.5417 | 61.5784 | 1.2161 | 1.0996 | 1.1464 | 1.3394 | 1.4097 | 1.1752 | 1.2375 | 61.5783 | 0.24863 | 61.5141 | -0.042259 | 0.034501 | 61.6623 | 0.003143 | 61.4451 | 62.7578 | 62.6414 | 62.6881 | 62.8811 | 62.9514 | 62.717 | 62.7792 | 123.1201 | 61.7904 | 123.0559 | 61.4995 | 61.5762 | 123.204 | 61.5449 | 122.9868 | 61.5438 | 61.5752 | 61.4796 | 61.511
3253.0625 | 123.2895 | -61.5509 | 61.6241 | 1.097 | 0.96224 | 1.0365 | 1.1929 | 1.2723 | 1.0608 | 1.123 | 61.5875 | 0.24863 | 61.5096 | -0.03768 | 0.039079 | 61.6577 | -0.001436 | 61.4268 | 62.648 | 62.5131 | 62.5874 | 62.7438 | 62.8232 | 62.6117 | 62.6739 | 123.1384 | 61.7995 | 123.0605 | 61.5132 | 61.59 | 123.2086 | 61.5495 | 122.9777 | 61.5484 | 61.5889 | 61.4705 | 61.511
3254.0625 | 123.3353 | -61.5417 | 61.6058 | 1.0696 | 0.94393 | 1.009 | 1.1837 | 1.2815 | 1.0287 | 1.0956 | 61.5966 | 0.24863 | 61.5096 | -0.03768 | 0.043657 | 61.6577 | -0.006014 | 61.4359 | 62.6113 | 62.4857 | 62.5508 | 62.7255 | 62.8232 | 62.5705 | 62.6373 | 123.1384 | 61.7904 | 123.0513 | 61.5041 | 61.5854 | 123.1995 | 61.5357 | 122.9777 | 61.553 | 61.6026 | 61.4659 | 61.5156
3255.0938 | 123.2941 | -61.5555 | 61.6058 | 1.0192 | 0.90272 | 0.95409 | 1.1562 | 1.2448 | 0.97379 | 1.0452 | 61.5966 | 0.24405 | 61.5324 | -0.033101 | 0.039079 | 61.6623 | -0.001436 | 61.4313 | 62.5747 | 62.4582 | 62.5096 | 62.7117 | 62.8003 | 62.5293 | 62.6007 | 123.1521 | 61.7995 | 123.0879 | 61.5224 | 61.5946 | 123.2178 | 61.554 | 122.9868 | 61.5575 | 61.5981 | 61.4934 | 61.5339
3256.0625 | 123.2986 | -61.5372 | 61.615 | 0.94596 | 0.84319 | 0.88083 | 1.0876 | 1.167 | 0.90054 | 0.96737 | 61.6058 | 0.24863 | 61.537 | -0.033101 | 0.043657 | 61.6486 | -0.001436 | 61.4268 | 62.4831 | 62.3804 | 62.418 | 62.6247 | 62.7042 | 62.4377 | 62.5045 | 123.1429 | 61.7858 | 123.0742 | 61.5041 | 61.5808 | 123.1857 | 61.5357 | 122.9639 | 61.5621 | 61.6072 | 61.4934 | 61.5385
3257.0625 | 123.4131 | -61.5555 | 61.5692 | 1.0421 | 0.88898 | 0.97698 | 1.1379 | 1.1899 | 0.99668 | 1.0635 | 61.6012 | 0.24863 | 61.5324 | -0.03768 | 0.039079 | 61.644 | 0.003143 | 61.4313 | 62.5976 | 62.4445 | 62.5325 | 62.6934 | 62.7454 | 62.5522 | 62.619 | 123.1567 | 61.8041 | 123.0879 | 61.5178 | 61.5946 | 123.1995 | 61.5586 | 122.9868 | 61.5621 | 61.5981 | 61.4934 | 61.5293
3258.0625 | 123.2986 | -61.5326 | 61.6333 | 1.0284 | 0.86608 | 0.94493 | 1.1288 | 1.1899 | 0.97837 | 1.0406 | 61.6058 | 0.24863 | 61.537 | -0.028522 | 0.039079 | 61.6486 | 0.007721 | 61.4313 | 62.561 | 62.3987 | 62.4775 | 62.6614 | 62.7225 | 62.511 | 62.5732 | 123.1384 | 61.7812 | 123.0696 | 61.5041 | 61.5717 | 123.1812 | 61.5403 | 122.9639 | 61.5667 | 61.5981 | 61.4979 | 61.5293
3259.0781 | 123.3398 | -61.5463 | 61.6287 | 1.1383 | 0.9485 | 1.0777 | 1.2203 | 1.2723 | 1.0974 | 1.1642 | 61.5966 | 0.24863 | 61.5279 | -0.028522 | 0.039079 | 61.6577 | 0.007721 | 61.4451 | 62.6846 | 62.4948 | 62.624 | 62.7667 | 62.8186 | 62.6437 | 62.7106 | 123.1429 | 61.795 | 123.0742 | 61.5178 | 61.5854 | 123.204 | 61.554 | 122.9914 | 61.5575 | 61.5889 | 61.4888 | 61.5202
3260.0625 | 123.3215 | -61.5555 | 61.6013 | 1.1657 | 0.97598 | 1.1143 | 1.2524 | 1.3227 | 1.134 | 1.1963 | 61.5966 | 0.24863 | 61.5324 | -0.028522 | 0.043657 | 61.6623 | 0.003143 | 61.4359 | 62.7212 | 62.5315 | 62.6698 | 62.8079 | 62.8782 | 62.6895 | 62.7518 | 123.1521 | 61.8041 | 123.0879 | 61.527 | 61.5991 | 123.2178 | 61.5586 | 122.9914 | 61.553 | 61.5935 | 61.4888 | 61.5293
3261.0781 | 123.3124 | -61.5601 | 61.6196 | 1.1337 | 0.92561 | 1.0594 | 1.2066 | 1.2448 | 1.0928 | 1.1597 | 61.6012 | 0.24863 | 61.5233 | -0.033101 | 0.039079 | 61.6577 | -0.001436 | 61.4359 | 62.6937 | 62.4857 | 62.6195 | 62.7667 | 62.8049 | 62.6529 | 62.7197 | 123.1613 | 61.8087 | 123.0834 | 61.527 | 61.5991 | 123.2178 | 61.5586 | 122.996 | 61.5621 | 61.6026 | 61.4842 | 61.5247
3262.0625 | 123.2574 | -61.5646 | 61.5967 | 1.1337 | 0.93019 | 1.0594 | 1.1745 | 1.2174 | 1.0837 | 1.1505 | 61.592 | 0.24405 | 61.5324 | -0.03768 | 0.039079 | 61.6577 | -0.001436 | 61.4313 | 62.6983 | 62.4948 | 62.624 | 62.7392 | 62.782 | 62.6483 | 62.7151 | 123.1567 | 61.8087 | 123.0971 | 61.527 | 61.6037 | 123.2224 | 61.5632 | 122.996 | 61.553 | 61.5935 | 61.4934 | 61.5339
3263.0938 | 123.381 | -61.528 | 61.6013 | 1.1474 | 0.95766 | 1.0777 | 1.1974 | 1.2769 | 1.102 | 1.1642 | 61.5966 | 0.24863 | 61.5279 | -0.03768 | 0.043657 | 61.6577 | 0.003143 | 61.4451 | 62.6754 | 62.4857 | 62.6057 | 62.7255 | 62.8049 | 62.63 | 62.6922 | 123.1246 | 61.7766 | 123.0559 | 61.4903 | 61.5717 | 123.1857 | 61.5312 | 122.9731 | 61.553 | 61.5935 | 61.4842 | 61.5247
3264.0625 | 123.2895 | -61.5509 | 61.6196 | 1.1566 | 1.063 | 1.0823 | 1.2386 | 1.3044 | 1.1066 | 1.1734 | 61.6058 | 0.25321 | 61.5279 | -0.033101 | 0.043657 | 61.6669 | 0.007721 | 61.4405 | 62.7075 | 62.6139 | 62.6332 | 62.7896 | 62.8553 | 62.6575 | 62.7243 | 123.1567 | 61.8041 | 123.0788 | 61.5178 | 61.5946 | 123.2178 | 61.5586 | 122.9914 | 61.5621 | 61.5981 | 61.4842 | 61.5202
3265.0625 | 123.3444 | -61.5372 | 61.5829 | 1.1245 | 1.0859 | 1.0594 | 1.202 | 1.2815 | 1.0837 | 1.1505 | 61.5966 | 0.24863 | 61.5279 | -0.03768 | 0.039079 | 61.6669 | 0.007721 | 61.4451 | 62.6617 | 62.623 | 62.5966 | 62.7392 | 62.8186 | 62.6208 | 62.6877 | 123.1338 | 61.7858 | 123.065 | 61.4995 | 61.5762 | 123.204 | 61.5449 | 122.9822 | 61.5575 | 61.5889 | 61.4888 | 61.5202
3266.0625 | 123.2941 | -61.5646 | 61.5967 | 1.1886 | 1.0538 | 1.1235 | 1.1333 | 1.2036 | 0.77692 | 1.2054 | 61.5966 | 0.24863 | 61.5279 | -0.033101 | 0.039079 | 61.6623 | 0.003143 | 61.4405 | 62.7533 | 62.6185 | 62.6881 | 62.698 | 62.7683 | 62.3416 | 62.7701 | 123.1613 | 61.8133 | 123.0925 | 61.5315 | 61.6037 | 123.2269 | 61.5678 | 123.0051 | 61.5575 | 61.5935 | 61.4888 | 61.5247
3267.1094 | 123.2895 | -61.5372 | 61.615 | 1.184 | 1.0538 | 1.1235 | 1.1654 | 1.1762 | 0.79981 | 1.21 | 61.592 | 0.23948 | 61.5233 | -0.03768 | 0.048236 | 61.6577 | 0.003143 | 61.4496 | 62.7212 | 62.591 | 62.6607 | 62.7026 | 62.7133 | 62.337 | 62.7472 | 123.1292 | 61.7766 | 123.0605 | 61.4995 | 61.5854 | 123.1949 | 61.5403 | 122.9868 | 61.5438 | 61.5889 | 61.4751 | 61.5202
3268.0625 | 123.3261 | -61.5967 | 61.5921 | 1.5961 | 1.498 | 1.5264 | 1.6095 | 1.7393 | 1.3034 | 1.6175 | 61.5737 | 0.24405 | 61.505 | -0.023943 | 0.043657 | 61.6898 | -0.001436 | 61.4817 | 63.1928 | 63.0946 | 63.1231 | 63.2062 | 63.3359 | 62.9001 | 63.2142 | 123.1704 | 61.8407 | 123.1017 | 61.5727 | 61.6403 | 123.2864 | 61.5952 | 123.0784 | 61.5301 | 61.5752 | 61.4613 | 61.5064
3269.0938 | 123.3124 | -61.5601 | 61.6013 | 1.3718 | 1.2278 | 1.3021 | 1.3211 | 1.2906 | 0.98295 | 1.384 | 61.5829 | 0.24405 | 61.5004 | -0.028522 | 0.039079 | 61.6669 | 0.003143 | 61.4496 | 62.9318 | 62.7879 | 62.8621 | 62.8811 | 62.8507 | 62.543 | 62.944 | 123.1429 | 61.8041 | 123.0605 | 61.5315 | 61.5991 | 123.2269 | 61.5632 | 123.0097 | 61.5438 | 61.5797 | 61.4613 | 61.4973
3270.0625 | 123.2803 | -61.5784 | 61.5875 | 1.3718 | 1.3148 | 1.3021 | 1.3623 | 1.4234 | 1.0745 | 1.3931 | 61.5829 | 0.24405 | 61.505 | -0.03768 | 0.043657 | 61.6715 | -0.010593 | 61.4542 | 62.9501 | 62.8932 | 62.8804 | 62.9406 | 63.0018 | 62.6529 | 62.9715 | 123.1613 | 61.8224 | 123.0833 | 61.5407 | 61.622 | 123.2498 | 61.5678 | 123.0326 | 61.5392 | 61.5935 | 61.4613 | 61.5156
3271.0938 | 123.3078 | -61.5555 | 61.6241 | 1.3168 | 1.3423 | 1.2517 | 1.376 | 1.4692 | 1.0928 | 1.3474 | 61.592 | 0.24405 | 61.5141 | -0.03768 | 0.039079 | 61.6669 | 0.003143 | 61.4542 | 62.8723 | 62.8978 | 62.8072 | 62.9315 | 63.0246 | 62.6483 | 62.9028 | 123.1475 | 61.7995 | 123.0696 | 61.5178 | 61.5946 | 123.2224 | 61.5586 | 123.0097 | 61.553 | 61.5889 | 61.4751 | 61.511
3272.0625 | 123.2986 | -61.5234 | 61.5784 | 1.3031 | 1.3285 | 1.238 | 1.3943 | 1.4417 | 1.0699 | 1.3245 | 61.592 | 0.24405 | 61.5187 | -0.03768 | 0.043657 | 61.6715 | -0.001436 | 61.4542 | 62.8265 | 62.852 | 62.7614 | 62.9178 | 62.9651 | 62.5934 | 62.8479 | 123.1155 | 61.7675 | 123.0422 | 61.4858 | 61.5671 | 123.1949 | 61.522 | 122.9777 | 61.5484 | 61.5935 | 61.4751 | 61.5202
3273.0625 | 123.2803 | -61.5738 | 61.6241 | 1.2252 | 1.237 | 1.1555 | 1.3348 | 1.3318 | 1.1707 | 1.2421 | 61.5966 | 0.24405 | 61.5233 | -0.033101 | 0.039079 | 61.6623 | 0.003143 | 61.4451 | 62.799 | 62.8108 | 62.7293 | 62.9086 | 62.9056 | 62.7445 | 62.8159 | 123.1704 | 61.8178 | 123.0971 | 61.5407 | 61.6129 | 123.2361 | 61.5769 | 123.0189 | 61.5575 | 61.5935 | 61.4842 | 61.5202
3274.0625 | 123.2391 | -61.5692 | 61.5921 | 1.2115 | 1.2141 | 1.1281 | 1.3256 | 1.2998 | 1.1523 | 1.2283 | 61.5875 | 0.23948 | 61.5279 | -0.042259 | 0.034501 | 61.6623 | 0.003143 | 61.4496 | 62.7807 | 62.7833 | 62.6973 | 62.8949 | 62.869 | 62.7216 | 62.7975 | 123.1567 | 61.8087 | 123.0971 | 61.527 | 61.6037 | 123.2315 | 61.5724 | 123.0189 | 61.553 | 61.5843 | 61.4934 | 61.5247
3275.0781 | 123.3444 | -61.5509 | 61.6241 | 1.3031 | 1.2644 | 1.2288 | 1.3897 | 1.4051 | 1.2485 | 1.3153 | 61.5829 | 0.24863 | 61.5187 | -0.03768 | 0.043657 | 61.6669 | -0.001436 | 61.4542 | 62.854 | 62.8153 | 62.7797 | 62.9406 | 62.956 | 62.7994 | 62.8662 | 123.1338 | 61.7995 | 123.0696 | 61.5132 | 61.5946 | 123.2178 | 61.5495 | 123.0051 | 61.5392 | 61.5843 | 61.4751 | 61.5202
3276.0625 | 123.2849 | -61.5967 | 61.5692 | 1.3305 | 1.3331 | 1.27 | 1.4401 | 1.5378 | 1.2943 | 1.3519 | 61.5737 | 0.24405 | 61.505 | -0.042259 | 0.043657 | 61.6715 | 0.003143 | 61.4588 | 62.9272 | 62.9298 | 62.8667 | 63.0368 | 63.1345 | 62.891 | 62.9486 | 123.1704 | 61.8407 | 123.1017 | 61.5544 | 61.6403 | 123.2681 | 61.5998 | 123.0555 | 61.5301 | 61.5706 | 61.4613 | 61.5018
3277.0625 | 123.3673 | -61.5646 | 61.5417 | 1.4175 | 1.3698 | 1.3433 | 1.4309 | 1.5104 | 1.015 | 1.4343 | 61.5783 | 0.24863 | 61.505 | -0.03768 | 0.029923 | 61.6715 | 0.007721 | 61.4588 | 62.9822 | 62.9344 | 62.9079 | 62.9956 | 63.075 | 62.5796 | 62.999 | 123.1429 | 61.8133 | 123.0696 | 61.527 | 61.5946 | 123.2361 | 61.5724 | 123.0234 | 61.5484 | 61.5706 | 61.4751 | 61.4973
3278.0781 | 123.3215 | -61.5601 | 61.5967 | 1.3672 | 1.3102 | 1.3021 | 1.3668 | 1.4005 | 0.93258 | 1.3886 | 61.5829 | 0.24863 | 61.5096 | -0.033101 | 0.039079 | 61.6669 | 0.003143 | 61.4542 | 62.9272 | 62.8703 | 62.8621 | 62.9269 | 62.9606 | 62.4926 | 62.9486 | 123.1429 | 61.8087 | 123.0696 | 61.527 | 61.5991 | 123.2269 | 61.5632 | 123.0143 | 61.5438 | 61.5797 | 61.4705 | 61.5064
3279.0625 | 123.2574 | -61.5875 | 61.5784 | 1.5045 | 1.4384 | 1.4348 | 1.495 | 1.6614 | 1.1203 | 1.5305 | 61.5829 | 0.25779 | 61.5096 | -0.03768 | 0.039079 | 61.6852 | -0.001436 | 61.4634 | 63.092 | 63.026 | 63.0224 | 63.0826 | 63.249 | 62.7078 | 63.118 | 123.1704 | 61.8453 | 123.0971 | 61.5498 | 61.6266 | 123.2727 | 61.5861 | 123.0509 | 61.5438 | 61.5843 | 61.4705 | 61.511
3280.0938 | 123.2849 | -61.5738 | 61.5875 | 1.4633 | 1.443 | 1.3845 | 1.5225 | 1.7118 | 1.4133 | 1.4801 | 61.5783 | 0.24863 | 61.505 | -0.033101 | 0.039079 | 61.6806 | -0.001436 | 61.4634 | 63.0371 | 63.0168 | 62.9583 | 63.0963 | 63.2856 | 62.9871 | 63.0539 | 123.1521 | 61.8224 | 123.0788 | 61.5407 | 61.6129 | 123.2544 | 61.5724 | 123.0372 | 61.5392 | 61.5797 | 61.4659 | 61.5064
3281.0625 | 123.4177 | -61.5829 | 61.4914 | 1.5961 | 1.5666 | 1.5356 | 1.5637 | 1.7667 | 1.2714 | 1.622 | 61.5737 | 0.25779 | 61.505 | -0.046838 | 0.039079 | 61.6852 | -0.001436 | 61.468 | 63.179 | 63.1496 | 63.1185 | 63.1467 | 63.3497 | 62.8543 | 63.205 | 123.1567 | 61.8407 | 123.0879 | 61.5361 | 61.622 | 123.2681 | 61.5815 | 123.0509 | 61.5346 | 61.5752 | 61.4659 | 61.5064
3282.1094 | 123.3124 | -61.5967 | 61.5326 | 1.4633 | 1.5529 | 1.3891 | 1.5454 | 1.7026 | 1.4133 | 1.4847 | 61.5646 | 0.24863 | 61.5004 | -0.033101 | 0.039079 | 61.676 | 0.003143 | 61.4634 | 63.06 | 63.1496 | 62.9857 | 63.1421 | 63.2993 | 63.01 | 63.0814 | 123.1613 | 61.8453 | 123.0971 | 61.5636 | 61.6358 | 123.2727 | 61.5998 | 123.0601 | 61.5255 | 61.5614 | 61.4613 | 61.4973
3283.0625 | 123.4177 | -61.5463 | 61.5326 | 1.5045 | 1.6124 | 1.4303 | 1.6187 | 1.7896 | 1.4499 | 1.5213 | 61.5691 | 0.24405 | 61.4958 | -0.042259 | 0.039079 | 61.6852 | 0.007721 | 61.4634 | 63.0508 | 63.1588 | 62.9766 | 63.165 | 63.3359 | 62.9963 | 63.0677 | 123.1155 | 61.7904 | 123.0421 | 61.5041 | 61.5854 | 123.2315 | 61.554 | 123.0097 | 61.5301 | 61.5614 | 61.4567 | 61.4881
3284.0625 | 123.3856 | -61.5463 | 61.528 | 1.5274 | 1.6216 | 1.4577 | 1.6095 | 1.8125 | 1.482 | 1.5488 | 61.5646 | 0.24863 | 61.4684 | -0.042259 | 0.034501 | 61.6806 | -0.006014 | 61.4588 | 63.0737 | 63.1679 | 63.0041 | 63.1558 | 63.3588 | 63.0283 | 63.0951 | 123.1109 | 61.795 | 123.0147 | 61.5041 | 61.5808 | 123.2269 | 61.5403 | 123.0051 | 61.5301 | 61.5706 | 61.4339 | 61.4744
3285.0938 | 123.2712 | -61.5784 | 61.5738 | 1.5183 | 1.6033 | 1.4486 | 1.5729 | 1.785 | 1.4683 | 1.5396 | 61.5691 | 0.24405 | 61.5004 | -0.042259 | 0.039079 | 61.6852 | 0.003143 | 61.4588 | 63.0966 | 63.1816 | 63.0269 | 63.1512 | 63.3634 | 63.0466 | 63.118 | 123.1475 | 61.8224 | 123.0788 | 61.5361 | 61.6174 | 123.2636 | 61.5815 | 123.0372 | 61.5301 | 61.566 | 61.4613 | 61.4973
3286.0625 | 123.4131 | -61.5738 | 61.5234 | 1.5137 | 1.5666 | 1.4394 | 1.5546 | 1.7576 | 1.2302 | 1.5351 | 61.5737 | 0.23948 | 61.5004 | -0.03768 | 0.039079 | 61.6852 | 0.003143 | 61.4634 | 63.0875 | 63.1404 | 63.0132 | 63.1284 | 63.3314 | 62.804 | 63.1089 | 123.1475 | 61.8133 | 123.0742 | 61.5361 | 61.6129 | 123.259 | 61.5769 | 123.0372 | 61.5346 | 61.5706 | 61.4613 | 61.4973
3287.0938 | 123.2986 | -61.5692 | 61.5921 | 1.4633 | 1.5804 | 1.3845 | 1.5775 | 1.7576 | 1.2851 | 1.4801 | 61.5829 | 0.24863 | 61.5141 | -0.03768 | 0.039079 | 61.6806 | -0.001436 | 61.4542 | 63.0325 | 63.1496 | 62.9537 | 63.1467 | 63.3268 | 62.8543 | 63.0493 | 123.1521 | 61.8178 | 123.0833 | 61.5315 | 61.6083 | 123.2498 | 61.5678 | 123.0234 | 61.5438 | 61.5843 | 61.4751 | 61.5156
3288.0625 | 123.3948 | -61.5646 | 61.5234 | 1.4313 | 1.5804 | 1.3707 | 1.5958 | 1.7805 | 1.2714 | 1.4481 | 61.5783 | 0.25779 | 61.505 | -0.03768 | 0.039079 | 61.6806 | -0.001436 | 61.4588 | 62.9959 | 63.145 | 62.9354 | 63.1604 | 63.3451 | 62.836 | 63.0127 | 123.1429 | 61.8224 | 123.0696 | 61.527 | 61.6037 | 123.2452 | 61.5632 | 123.0234 | 61.5392 | 61.5797 | 61.4659 | 61.5064
3289.0781 | 123.3215 | -61.5738 | 61.5372 | 1.4175 | 1.4934 | 1.357 | 1.4996 | 1.6981 | 1.1661 | 1.4435 | 61.5783 | 0.24863 | 61.5096 | -0.03768 | 0.029923 | 61.6806 | -0.001436 | 61.4542 | 62.9913 | 63.0672 | 62.9308 | 63.0734 | 63.2719 | 62.7399 | 63.0173 | 123.1521 | 61.8224 | 123.0833 | 61.5361 | 61.6037 | 123.2544 | 61.5724 | 123.028 | 61.5484 | 61.5797 | 61.4796 | 61.511
3290.0625 | 123.349 | -61.5829 | 61.5417 | 1.5824 | 1.53 | 1.5081 | 1.5042 | 1.6935 | 1.1752 | 1.5992 | 61.5691 | 0.24405 | 61.5004 | -0.03768 | 0.039079 | 61.6806 | -0.001436 | 61.4542 | 63.1653 | 63.113 | 63.091 | 63.0871 | 63.2764 | 62.7582 | 63.1821 | 123.1521 | 61.827 | 123.0833 | 61.5453 | 61.622 | 123.2636 | 61.5815 | 123.0372 | 61.5301 | 61.5706 | 61.4613 | 61.5018
3291.0625 | 123.3582 | -61.528 | 61.5555 | 1.5137 | 1.4751 | 1.444 | 1.4538 | 1.634 | 1.1066 | 1.5305 | 61.5737 | 0.24405 | 61.4821 | -0.028522 | 0.034501 | 61.676 | 0.007721 | 61.4405 | 63.0417 | 63.0031 | 62.972 | 62.9819 | 63.162 | 62.6346 | 63.0585 | 123.1017 | 61.7721 | 123.0101 | 61.4995 | 61.5625 | 123.204 | 61.5357 | 122.9685 | 61.5392 | 61.566 | 61.4476 | 61.4744
3292.1094 | 123.3307 | -61.5921 | 61.5646 | 1.4908 | 1.443 | 1.4119 | 1.4676 | 1.634 | 1.0745 | 1.5076 | 61.5783 | 0.24405 | 61.4821 | -0.033101 | 0.039079 | 61.676 | 0.003143 | 61.4542 | 63.0829 | 63.0351 | 63.004 | 63.0597 | 63.2261 | 62.6666 | 63.0997 | 123.1704 | 61.8362 | 123.0742 | 61.559 | 61.6312 | 123.2681 | 61.5952 | 123.0463 | 61.5392 | 61.5752 | 61.443 | 61.4789
3293.0625 | 123.3353 | -61.5738 | 61.5234 | 1.5045 | 1.4659 | 1.4394 | 1.4859 | 1.666 | 1.1844 | 1.5213 | 61.5646 | 0.24863 | 61.4958 | -0.042259 | 0.034501 | 61.676 | 0.003143 | 61.4588 | 63.0783 | 63.0397 | 63.0132 | 63.0597 | 63.2398 | 62.7582 | 63.0951 | 123.1384 | 61.8224 | 123.0696 | 61.5315 | 61.6083 | 123.2498 | 61.5769 | 123.0326 | 61.5301 | 61.5614 | 61.4613 | 61.4927
3294.0625 | 123.4085 | -61.5738 | 61.5555 | 1.4725 | 1.5254 | 1.4074 | 1.5408 | 1.7026 | 1.2622 | 1.4984 | 61.5691 | 0.24863 | 61.4775 | -0.03768 | 0.043657 | 61.6806 | -0.001436 | 61.4542 | 63.0463 | 63.0992 | 62.9812 | 63.1146 | 63.2764 | 62.836 | 63.0722 | 123.1429 | 61.8224 | 123.0513 | 61.5361 | 61.6174 | 123.2544 | 61.5724 | 123.028 | 61.5255 | 61.5706 | 61.4339 | 61.4789
3295.0625 | 123.3536 | -61.5555 | 61.5601 | 1.4404 | 1.5392 | 1.3753 | 1.5362 | 1.7118 | 1.3538 | 1.4618 | 61.5737 | 0.25321 | 61.4729 | -0.033101 | 0.043657 | 61.676 | 0.007721 | 61.4588 | 62.9959 | 63.0947 | 62.9308 | 63.0917 | 63.2673 | 62.9093 | 63.0173 | 123.1292 | 61.8087 | 123.0284 | 61.5224 | 61.5991 | 123.2315 | 61.5632 | 123.0143 | 61.5301 | 61.566 | 61.4293 | 61.4652
3296.0625 | 123.2849 | -61.5601 | 61.5692 | 1.445 | 1.4796 | 1.3845 | 1.5134 | 1.6935 | 1.2576 | 1.471 | 61.5783 | 0.25321 | 61.4775 | -0.03768 | 0.043657 | 61.6806 | -0.001436 | 61.4588 | 63.0051 | 63.0397 | 62.9445 | 63.0734 | 63.2535 | 62.8177 | 63.031 | 123.1384 | 61.8133 | 123.0376 | 61.5224 | 61.6037 | 123.2407 | 61.5586 | 123.0189 | 61.5346 | 61.5797 | 61.4339 | 61.4789
3297.0625 | 123.4085 | -61.5372 | 61.5463 | 1.4816 | 1.4751 | 1.4119 | 1.5637 | 1.721 | 1.276 | 1.503 | 61.5737 | 0.25321 | 61.4912 | -0.042259 | 0.043657 | 61.6852 | 0.007721 | 61.4588 | 63.0188 | 63.0122 | 62.9491 | 63.1009 | 63.2581 | 62.8131 | 63.0402 | 123.1109 | 61.7904 | 123.0284 | 61.4949 | 61.5808 | 123.2224 | 61.5449 | 122.996 | 61.5301 | 61.566 | 61.4476 | 61.4835
3298.0625 | 123.4177 | -61.5601 | 61.5646 | 1.4954 | 1.4339 | 1.4211 | 1.5866 | 1.7301 | 1.3034 | 1.5168 | 61.5646 | 0.24405 | 61.4775 | -0.03768 | 0.043657 | 61.6852 | -0.001436 | 61.4542 | 63.0554 | 62.9939 | 62.9812 | 63.1467 | 63.2902 | 62.8635 | 63.0768 | 123.1246 | 61.8041 | 123.0376 | 61.5224 | 61.6037 | 123.2452 | 61.5586 | 123.0143 | 61.5209 | 61.566 | 61.4339 | 61.4789
3299.0625 | 123.3948 | -61.5417 | 61.5601 | 1.5045 | 1.4155 | 1.4348 | 1.5775 | 1.721 | 1.2897 | 1.5168 | 61.5646 | 0.25321 | 61.4867 | -0.033101 | 0.039079 | 61.6806 | 0.003143 | 61.4634 | 63.0463 | 62.9573 | 62.9766 | 63.1192 | 63.2627 | 62.8314 | 63.0585 | 123.1063 | 61.795 | 123.0284 | 61.5086 | 61.5808 | 123.2224 | 61.5449 | 123.0051 | 61.5255 | 61.5614 | 61.4476 | 61.4835
3300.0781 | 123.3765 | -61.5509 | 61.528 | 1.4908 | 1.4018 | 1.4119 | 1.55 | 1.7026 | 1.2576 | 1.5076 | 61.5737 | 0.24405 | 61.4867 | -0.042259 | 0.043657 | 61.676 | -0.001436 | 61.4542 | 63.0417 | 62.9527 | 62.9628 | 63.1009 | 63.2535 | 62.8086 | 63.0585 | 123.1246 | 61.795 | 123.0376 | 61.5086 | 61.5946 | 123.2269 | 61.5495 | 123.0051 | 61.5301 | 61.5752 | 61.443 | 61.4881
3301.0625 | 123.2849 | -61.5646 | 61.5967 | 1.5183 | 1.4659 | 1.4532 | 1.6003 | 1.7347 | 1.3217 | 1.5351 | 61.5691 | 0.24405 | 61.4867 | -0.033101 | 0.039079 | 61.6898 | -0.001436 | 61.4817 | 63.0829 | 63.0305 | 63.0178 | 63.165 | 63.2993 | 62.8864 | 63.0997 | 123.1338 | 61.8087 | 123.0513 | 61.5315 | 61.6037 | 123.2544 | 61.5632 | 123.0463 | 61.5301 | 61.5706 | 61.4476 | 61.4881
3302.0938 | 123.3673 | -61.5646 | 61.5189 | 1.5091 | 1.4842 | 1.4257 | 1.6232 | 1.7484 | 1.3446 | 1.5122 | 61.5737 | 0.25321 | 61.4867 | -0.033101 | 0.039079 | 61.6806 | 0.007721 | 61.468 | 63.0737 | 63.0489 | 62.9903 | 63.1879 | 63.3131 | 62.9093 | 63.0768 | 123.1384 | 61.8178 | 123.0513 | 61.5315 | 61.6037 | 123.2452 | 61.5724 | 123.0326 | 61.5346 | 61.566 | 61.4476 | 61.4789
3303.0625 | 123.3536 | -61.5463 | 61.5463 | 1.445 | 1.5025 | 1.3753 | 1.6187 | 1.7255 | 1.3584 | 1.4527 | 61.5691 | 0.24863 | 61.4867 | -0.042259 | 0.034501 | 61.6806 | -0.010593 | 61.4542 | 62.9913 | 63.0489 | 62.9216 | 63.165 | 63.2719 | 62.9047 | 62.999 | 123.1155 | 61.795 | 123.033 | 61.5041 | 61.5808 | 123.2269 | 61.5357 | 123.0006 | 61.5346 | 61.5797 | 61.4522 | 61.4973
3304.0625 | 123.3994 | -61.5372 | 61.5417 | 1.4999 | 1.498 | 1.4348 | 1.6324 | 1.7301 | 1.3584 | 1.5213 | 61.5646 | 0.24863 | 61.4958 | -0.03768 | 0.043657 | 61.6852 | 0.003143 | 61.4634 | 63.0371 | 63.0351 | 62.972 | 63.1696 | 63.2673 | 62.8955 | 63.0585 | 123.1017 | 61.7858 | 123.033 | 61.4995 | 61.5808 | 123.2224 | 61.5403 | 123.0006 | 61.5209 | 61.5614 | 61.4522 | 61.4927
3305.0938 | 123.3627 | -61.5509 | 61.5372 | 1.4816 | 1.498 | 1.4074 | 1.6003 | 1.7164 | 1.3767 | 1.4939 | 61.5691 | 0.24863 | 61.4912 | -0.033101 | 0.039079 | 61.6852 | 0.007721 | 61.4634 | 63.0325 | 63.0489 | 62.9583 | 63.1513 | 63.2673 | 62.9276 | 63.0448 | 123.1201 | 61.7995 | 123.0421 | 61.5178 | 61.59 | 123.2361 | 61.5586 | 123.0143 | 61.5301 | 61.5614 | 61.4522 | 61.4835
3306.0625 | 123.2712 | -61.5875 | 61.5738 | 1.4725 | 1.4888 | 1.3982 | 1.6095 | 1.7072 | 1.3446 | 1.4939 | 61.5783 | 0.25321 | 61.4958 | -0.033101 | 0.034501 | 61.676 | -0.001436 | 61.4542 | 63.06 | 63.0763 | 62.9857 | 63.197 | 63.2947 | 62.9322 | 63.0814 | 123.1658 | 61.8407 | 123.0833 | 61.5544 | 61.622 | 123.2636 | 61.5861 | 123.0418 | 61.5438 | 61.5797 | 61.4613 | 61.4973
3307.0625 | 123.349 | -61.5372 | 61.6516 | 1.3946 | 1.5071 | 1.3204 | 1.6049 | 1.7026 | 1.3126 | 1.416 | 61.5691 | 0.24863 | 61.505 | -0.03768 | 0.043657 | 61.6806 | -0.001436 | 61.4725 | 62.9318 | 63.0443 | 62.8575 | 63.1421 | 63.2398 | 62.8498 | 62.9532 | 123.1063 | 61.7858 | 123.0422 | 61.4995 | 61.5808 | 123.2178 | 61.5357 | 123.0097 | 61.5255 | 61.5706 | 61.4613 | 61.5064
3308.0938 | 123.4451 | -61.528 | 61.5417 | 1.4175 | 1.5163 | 1.3524 | 1.6187 | 1.7118 | 1.3126 | 1.4435 | 61.5737 | 0.23948 | 61.505 | -0.033101 | 0.043657 | 61.6806 | -0.001436 | 61.4634 | 62.9456 | 63.0443 | 62.8804 | 63.1467 | 63.2398 | 62.8406 | 62.9715 | 123.1017 | 61.7675 | 123.033 | 61.4949 | 61.5717 | 123.2086 | 61.5266 | 122.9914 | 61.5301 | 61.5752 | 61.4613 | 61.5064
3309.0625 | 123.4451 | -61.5555 | 61.5372 | 1.3534 | 1.4613 | 1.2837 | 1.6278 | 1.6798 | 1.2348 | 1.3703 | 61.5691 | 0.24863 | 61.5096 | -0.033101 | 0.039079 | 61.6806 | -0.001436 | 61.4588 | 62.9089 | 63.0168 | 62.8392 | 63.1833 | 63.2352 | 62.7902 | 62.9257 | 123.1246 | 61.8041 | 123.065 | 61.5224 | 61.5946 | 123.2361 | 61.554 | 123.0143 | 61.5301 | 61.5706 | 61.4705 | 61.511
3310.0625 | 123.436 | -61.5555 | 61.5601 | 1.3626 | 1.4522 | 1.2929 | 1.6324 | 1.6752 | 1.2622 | 1.3794 | 61.5783 | 0.25779 | 61.5004 | -0.03768 | 0.034501 | 61.676 | 0.003143 | 61.468 | 62.9181 | 63.0077 | 62.8484 | 63.1879 | 63.2307 | 62.8177 | 62.9349 | 123.1338 | 61.8133 | 123.0559 | 61.5178 | 61.59 | 123.2315 | 61.5586 | 123.0234 | 61.5438 | 61.5752 | 61.4659 | 61.4973
3311.0625 | 123.4543 | -61.5372 | 61.5326 | 1.3351 | 1.4201 | 1.2746 | 1.6141 | 1.6431 | 1.2851 | 1.3519 | 61.5737 | 0.25779 | 61.5141 | -0.042259 | 0.043657 | 61.676 | 0.003143 | 61.4542 | 62.8723 | 62.9573 | 62.8118 | 63.1513 | 63.1803 | 62.8223 | 62.8891 | 123.1109 | 61.795 | 123.0513 | 61.4949 | 61.5808 | 123.2132 | 61.5403 | 122.9914 | 61.5301 | 61.5706 | 61.4705 | 61.511
3312.0625 | 123.3032 | -61.5463 | 61.615 | 1.3214 | 1.4155 | 1.2563 | 1.6416 | 1.6477 | 1.363 | 1.3382 | 61.5737 | 0.24405 | 61.5004 | -0.033101 | 0.043657 | 61.6852 | -0.001436 | 61.4634 | 62.8677 | 62.9619 | 62.8026 | 63.1879 | 63.194 | 62.9093 | 62.8845 | 123.1201 | 61.7904 | 123.0467 | 61.5132 | 61.59 | 123.2315 | 61.5449 | 123.0097 | 61.5301 | 61.5752 | 61.4567 | 61.5018
3313.0781 | 123.4039 | -61.5555 | 61.5417 | 1.2939 | 1.4247 | 1.2196 | 1.6324 | 1.6111 | 1.3263 | 1.3062 | 61.5737 | 0.24863 | 61.5096 | -0.042259 | 0.034501 | 61.6806 | -0.001436 | 61.4634 | 62.8494 | 62.9802 | 62.7751 | 63.1879 | 63.1666 | 62.8818 | 62.8616 | 123.1292 | 61.8041 | 123.065 | 61.5132 | 61.59 | 123.2361 | 61.554 | 123.0189 | 61.5392 | 61.5752 | 61.4751 | 61.511
3314.0625 | 123.4543 | -61.528 | 61.5326 | 1.326 | 1.4384 | 1.2471 | 1.6416 | 1.6385 | 1.3126 | 1.3382 | 61.5829 | 0.24863 | 61.5004 | -0.033101 | 0.043657 | 61.6852 | -0.001436 | 61.4634 | 62.854 | 62.9665 | 62.7751 | 63.1696 | 63.1666 | 62.8406 | 62.8662 | 123.1109 | 61.7766 | 123.0284 | 61.4949 | 61.5717 | 123.2132 | 61.5266 | 122.9914 | 61.5392 | 61.5843 | 61.4567 | 61.5018
3315.0625 | 123.3627 | -61.5417 | 61.5555 | 1.3351 | 1.3972 | 1.27 | 1.5775 | 1.5928 | 1.2576 | 1.3657 | 61.5737 | 0.25321 | 61.5004 | -0.03768 | 0.039079 | 61.676 | -0.001436 | 61.4634 | 62.8769 | 62.939 | 62.8118 | 63.1192 | 63.1345 | 62.7994 | 62.9074 | 123.1155 | 61.795 | 123.0421 | 61.5041 | 61.5808 | 123.2178 | 61.5403 | 123.0051 | 61.5346 | 61.5752 | 61.4613 | 61.5018
3316.0625 | 123.4543 | -61.528 | 61.5555 | 1.3168 | 1.3606 | 1.2517 | 1.5546 | 1.5516 | 1.2393 | 1.3428 | 61.5783 | 0.24863 | 61.5141 | -0.03768 | 0.039079 | 61.676 | 0.003143 | 61.4588 | 62.8448 | 62.8886 | 62.7797 | 63.0826 | 63.0796 | 62.7674 | 62.8708 | 123.1063 | 61.7766 | 123.0422 | 61.4903 | 61.5671 | 123.204 | 61.5312 | 122.9868 | 61.5392 | 61.5752 | 61.4751 | 61.511
3317.0938 | 123.3627 | -61.5646 | 61.5097 | 1.3305 | 1.3789 | 1.2609 | 1.5958 | 1.5516 | 1.2714 | 1.3565 | 61.5783 | 0.25321 | 61.5141 | -0.03768 | 0.043657 | 61.6623 | 0.003143 | 61.4542 | 62.8952 | 62.9435 | 62.8255 | 63.1604 | 63.1162 | 62.836 | 62.9212 | 123.1429 | 61.8178 | 123.0788 | 61.527 | 61.6083 | 123.2269 | 61.5678 | 123.0189 | 61.5346 | 61.5752 | 61.4705 | 61.511
3318.0625 | 123.4222 | -61.5417 | 61.528 | 1.3305 | 1.3652 | 1.2609 | 1.5775 | 1.5333 | 1.2622 | 1.3519 | 61.5875 | 0.24863 | 61.5141 | -0.033101 | 0.043657 | 61.6715 | -0.001436 | 61.4542 | 62.8723 | 62.9069 | 62.8026 | 63.1192 | 63.075 | 62.804 | 62.8937 | 123.1292 | 61.7904 | 123.0559 | 61.5086 | 61.5854 | 123.2132 | 61.5403 | 122.996 | 61.5438 | 61.5889 | 61.4705 | 61.5156
3319.0625 | 123.3353 | -61.5143 | 61.5463 | 1.2939 | 1.3789 | 1.2334 | 1.6232 | 1.5699 | 1.3355 | 1.3199 | 61.5783 | 0.25321 | 61.5187 | -0.03768 | 0.039079 | 61.676 | -0.001436 | 61.4451 | 62.8082 | 62.8932 | 62.7477 | 63.1375 | 63.0842 | 62.8498 | 62.8342 | 123.0926 | 61.7675 | 123.033 | 61.4766 | 61.5534 | 123.1903 | 61.5128 | 122.9594 | 61.5392 | 61.5797 | 61.4796 | 61.5202
3320.0781 | 123.3856 | -61.5463 | 61.528 | 1.3443 | 1.3881 | 1.27 | 1.6003 | 1.5287 | 1.3996 | 1.3565 | 61.5783 | 0.24405 | 61.5096 | -0.042259 | 0.034501 | 61.676 | -0.006014 | 61.4542 | 62.8906 | 62.9344 | 62.8163 | 63.1467 | 63.075 | 62.9459 | 62.9028 | 123.1246 | 61.7904 | 123.0559 | 61.5041 | 61.5808 | 123.2224 | 61.5403 | 123.0006 | 61.5438 | 61.5843 | 61.4751 | 61.5156
3321.0625 | 123.3856 | -61.5692 | 61.5738 | 1.3305 | 1.356 | 1.2563 | 1.5408 | 1.4463 | 1.3492 | 1.3428 | 61.5829 | 0.24405 | 61.5141 | -0.033101 | 0.034501 | 61.6715 | 0.003143 | 61.4451 | 62.8998 | 62.9252 | 62.8255 | 63.11 | 63.0155 | 62.9184 | 62.912 | 123.1521 | 61.8133 | 123.0833 | 61.5361 | 61.6037 | 123.2407 | 61.5724 | 123.0143 | 61.5484 | 61.5797 | 61.4796 | 61.511
3322.1094 | 123.3902 | -61.5555 | 61.5601 | 1.3397 | 1.356 | 1.2746 | 1.5546 | 1.4097 | 1.2989 | 1.3657 | 61.5783 | 0.24863 | 61.5141 | -0.042259 | 0.039079 | 61.6715 | -0.006014 | 61.4451 | 62.8952 | 62.9115 | 62.8301 | 63.11 | 62.9651 | 62.8543 | 62.9212 | 123.1338 | 61.8041 | 123.0696 | 61.5132 | 61.5946 | 123.2269 | 61.5495 | 123.0006 | 61.5392 | 61.5843 | 61.4751 | 61.5202
3323.0625 | 123.4085 | -61.528 | 61.5417 | 1.3397 | 1.3377 | 1.27 | 1.5042 | 1.373 | 1.2531 | 1.3611 | 61.592 | 0.25321 | 61.5096 | -0.033101 | 0.048236 | 61.6715 | 0.003143 | 61.4496 | 62.8677 | 62.8657 | 62.798 | 63.0322 | 62.901 | 62.7811 | 62.8891 | 123.1201 | 61.7812 | 123.0376 | 61.4949 | 61.5763 | 123.1995 | 61.5312 | 122.9777 | 61.5438 | 61.5889 | 61.4613 | 61.5064
3324.0625 | 123.436 | -61.5601 | 61.5555 | 1.3809 | 1.3606 | 1.3066 | 1.5408 | 1.4188 | 1.2805 | 1.4069 | 61.5783 | 0.24405 | 61.5141 | -0.03768 | 0.034501 | 61.6669 | 0.003143 | 61.4451 | 62.941 | 62.9207 | 62.8667 | 63.1009 | 62.9789 | 62.8406 | 62.9669 | 123.1384 | 61.8041 | 123.0742 | 61.5224 | 61.5946 | 123.2269 | 61.5632 | 123.0051 | 61.5438 | 61.5752 | 61.4796 | 61.511
3325.0625 | 123.4497 | -61.4822 | 61.5692 | 1.3443 | 1.2965 | 1.2746 | 1.4493 | 1.3547 | 1.221 | 1.3611 | 61.5875 | 0.24863 | 61.5141 | -0.033101 | 0.039079 | 61.6669 | 0.003143 | 61.4359 | 62.8265 | 62.7787 | 62.7568 | 62.9315 | 62.837 | 62.7033 | 62.8433 | 123.0697 | 61.7309 | 122.9964 | 61.4491 | 61.5213 | 123.1491 | 61.4854 | 122.9182 | 61.5484 | 61.5843 | 61.4751 | 61.511
3326.0938 | 123.3627 | -61.5738 | 61.5509 | 1.3489 | 1.269 | 1.2792 | 1.3943 | 1.3318 | 1.1798 | 1.3748 | 61.5829 | 0.24405 | 61.5096 | -0.028522 | 0.039079 | 61.6669 | 0.003143 | 61.4451 | 62.9227 | 62.8428 | 62.853 | 62.9681 | 62.9056 | 62.7536 | 62.9486 | 123.1567 | 61.8178 | 123.0833 | 61.5453 | 61.6129 | 123.2407 | 61.5769 | 123.0189 | 61.5438 | 61.5797 | 61.4705 | 61.5064
3327.0625 | 123.262 | -61.5738 | 61.6013 | 1.4313 | 1.3057 | 1.357 | 1.4676 | 1.3685 | 1.2256 | 1.4435 | 61.5875 | 0.24863 | 61.5096 | -0.042259 | 0.039079 | 61.6715 | -0.001436 | 61.4451 | 63.0051 | 62.8794 | 62.9308 | 63.0414 | 62.9422 | 62.7994 | 63.0173 | 123.1613 | 61.8224 | 123.0833 | 61.5315 | 61.6129 | 123.2452 | 61.5724 | 123.0189 | 61.5484 | 61.5889 | 61.4705 | 61.511
3328.0625 | 123.3856 | -61.5417 | 61.5509 | 1.3946 | 1.2965 | 1.3204 | 1.4172 | 1.3547 | 1.1569 | 1.4115 | 61.5783 | 0.24863 | 61.5141 | -0.033101 | 0.048236 | 61.6715 | 0.007721 | 61.4496 | 62.9364 | 62.8382 | 62.8621 | 62.959 | 62.8965 | 62.6987 | 62.9532 | 123.1201 | 61.7904 | 123.0559 | 61.5086 | 61.59 | 123.2132 | 61.5495 | 122.9914 | 61.5301 | 61.5706 | 61.4659 | 61.5064
3329.0781 | 123.4039 | -61.5692 | 61.5509 | 1.3763 | 1.3285 | 1.3021 | 1.4722 | 1.3135 | 1.1936 | 1.3931 | 61.5783 | 0.24863 | 61.5096 | -0.033101 | 0.043657 | 61.6715 | -0.006014 | 61.4451 | 62.9455 | 62.8978 | 62.8713 | 63.0414 | 62.8827 | 62.7628 | 62.9624 | 123.1475 | 61.8178 | 123.0788 | 61.5361 | 61.6129 | 123.2407 | 61.5632 | 123.0143 | 61.5346 | 61.5843 | 61.4659 | 61.5156
3330.0625 | 123.4039 | -61.5326 | 61.5646 | 1.3992 | 1.3331 | 1.325 | 1.4447 | 1.3135 | 1.1569 | 1.4115 | 61.5829 | 0.24863 | 61.5096 | -0.033101 | 0.043657 | 61.6715 | -0.001436 | 61.4451 | 62.9318 | 62.8657 | 62.8575 | 62.9773 | 62.8461 | 62.6895 | 62.944 | 123.1155 | 61.7812 | 123.0422 | 61.4995 | 61.5763 | 123.204 | 61.5312 | 122.9777 | 61.5392 | 61.5843 | 61.4659 | 61.511
3331.0781 | 123.4406 | -61.5646 | 61.5143 | 1.3534 | 1.2828 | 1.2792 | 1.4126 | 1.3456 | 1.1523 | 1.3703 | 61.5829 | 0.25321 | 61.5141 | -0.03768 | 0.039079 | 61.6715 | -0.001436 | 61.4359 | 62.9181 | 62.8474 | 62.8438 | 62.9773 | 62.9102 | 62.717 | 62.9349 | 123.1475 | 61.8178 | 123.0788 | 61.527 | 61.6037 | 123.2361 | 61.5632 | 123.0005 | 61.5438 | 61.5843 | 61.4751 | 61.5156
3332.0625 | 123.1934 | -61.5921 | 61.5051 | 1.2664 | 1.2507 | 1.1968 | 1.3989 | 1.3181 | 1.1295 | 1.2924 | 61.592 | 0.24863 | 61.5187 | -0.033101 | 0.039079 | 61.6669 | -0.001436 | 61.4451 | 62.8585 | 62.8428 | 62.7889 | 62.991 | 62.9102 | 62.7216 | 62.8845 | 123.1841 | 61.8407 | 123.1108 | 61.559 | 61.6312 | 123.259 | 61.5907 | 123.0372 | 61.553 | 61.5935 | 61.4796 | 61.5202
3333.0625 | 123.3994 | -61.5189 | 61.5601 | 1.3443 | 1.324 | 1.2746 | 1.495 | 1.3318 | 1.2164 | 1.3611 | 61.5783 | 0.25321 | 61.5141 | -0.03768 | 0.043657 | 61.6715 | 0.003143 | 61.4542 | 62.8631 | 62.8428 | 62.7934 | 63.0139 | 62.8507 | 62.7353 | 62.88 | 123.0972 | 61.7721 | 123.033 | 61.4812 | 61.5625 | 123.1903 | 61.522 | 122.9731 | 61.5346 | 61.5752 | 61.4705 | 61.511
3334.0938 | 123.3994 | -61.5417 | 61.5417 | 1.326 | 1.2736 | 1.2517 | 1.4676 | 1.2815 | 1.1844 | 1.3474 | 61.5829 | 0.24863 | 61.5141 | -0.03768 | 0.034501 | 61.6669 | 0.007721 | 61.4405 | 62.8677 | 62.8153 | 62.7934 | 63.0093 | 62.8232 | 62.7261 | 62.8891 | 123.1246 | 61.7904 | 123.0559 | 61.5041 | 61.5762 | 123.2086 | 61.5495 | 122.9822 | 61.5484 | 61.5752 | 61.4796 | 61.5064
3335.0625 | 123.4085 | -61.5372 | 61.5738 | 1.413 | 1.3469 | 1.3478 | 1.5637 | 1.3227 | 1.221 | 1.4343 | 61.5829 | 0.24863 | 61.505 | -0.046838 | 0.039079 | 61.6669 | 0.007721 | 61.4496 | 62.9501 | 62.884 | 62.885 | 63.1009 | 62.8598 | 62.7582 | 62.9715 | 123.1201 | 61.7858 | 123.0422 | 61.4903 | 61.5762 | 123.204 | 61.5449 | 122.9868 | 61.5438 | 61.5752 | 61.4659 | 61.4973
3336.0625 | 123.3948 | -61.5555 | 61.5601 | 1.413 | 1.3698 | 1.3387 | 1.5591 | 1.3776 | 1.2439 | 1.4252 | 61.5783 | 0.24863 | 61.505 | -0.03768 | 0.048236 | 61.6715 | 0.007721 | 61.4588 | 62.9684 | 62.9252 | 62.8942 | 63.1146 | 62.9331 | 62.7994 | 62.9807 | 123.1338 | 61.8041 | 123.0605 | 61.5178 | 61.6037 | 123.2269 | 61.5632 | 123.0143 | 61.5301 | 61.5706 | 61.4567 | 61.4973
3337.0938 | 123.3353 | -61.5875 | 61.5784 | 1.4175 | 1.3972 | 1.3387 | 1.582 | 1.3685 | 1.2897 | 1.4298 | 61.5783 | 0.25321 | 61.505 | -0.028522 | 0.039079 | 61.6806 | 0.003143 | 61.4451 | 63.0051 | 62.9848 | 62.9262 | 63.1696 | 62.956 | 62.8772 | 63.0173 | 123.1658 | 61.8407 | 123.0925 | 61.559 | 61.6266 | 123.2681 | 61.5907 | 123.0326 | 61.5392 | 61.5752 | 61.4659 | 61.5018
3338.0625 | 123.3856 | -61.5509 | 61.5829 | 1.3718 | 1.3835 | 1.3066 | 1.5683 | 1.3135 | 1.3217 | 1.3977 | 61.5829 | 0.25321 | 61.505 | -0.03768 | 0.043657 | 61.676 | 0.003143 | 61.4451 | 62.9227 | 62.9344 | 62.8575 | 63.1192 | 62.8644 | 62.8727 | 62.9486 | 123.1338 | 61.8041 | 123.0559 | 61.5132 | 61.5946 | 123.2269 | 61.554 | 122.996 | 61.5392 | 61.5797 | 61.4613 | 61.5018
3339.0625 | 123.2803 | -61.5738 | 61.5967 | 1.3763 | 1.3835 | 1.3112 | 1.5408 | 1.3272 | 1.3309 | 1.3886 | 61.5829 | 0.24863 | 61.505 | -0.033101 | 0.039079 | 61.676 | 0.003143 | 61.4542 | 62.9501 | 62.9573 | 62.885 | 63.1146 | 62.901 | 62.9047 | 62.9624 | 123.1567 | 61.8224 | 123.0788 | 61.5407 | 61.6129 | 123.2498 | 61.5769 | 123.028 | 61.5438 | 61.5797 | 61.4659 | 61.5018
3340.0625 | 123.2849 | -61.5784 | 61.6196 | 1.3351 | 1.3789 | 1.27 | 1.5088 | 1.3044 | 1.2989 | 1.3703 | 61.5829 | 0.25321 | 61.505 | -0.03768 | 0.043657 | 61.676 | 0.003143 | 61.4542 | 62.9135 | 62.9573 | 62.8484 | 63.0871 | 62.8827 | 62.8772 | 62.9486 | 123.1613 | 61.8316 | 123.0833 | 61.5407 | 61.622 | 123.2544 | 61.5815 | 123.0326 | 61.5392 | 61.5797 | 61.4613 | 61.5018
3341.0938 | 123.3902 | -61.5692 | 61.5555 | 1.3534 | 1.4201 | 1.2883 | 1.5271 | 1.3044 | 1.3034 | 1.3748 | 61.5829 | 0.24863 | 61.5004 | -0.046838 | 0.043657 | 61.6715 | 0.007721 | 61.4588 | 62.9227 | 62.9893 | 62.8575 | 63.0963 | 62.8736 | 62.8726 | 62.944 | 123.1521 | 61.8178 | 123.0696 | 61.5224 | 61.6129 | 123.2407 | 61.5769 | 123.028 | 61.5392 | 61.5752 | 61.4567 | 61.4927
3342.0625 | 123.317 | -61.5784 | 61.6104 | 1.3534 | 1.411 | 1.2837 | 1.5317 | 1.2677 | 1.3126 | 1.3748 | 61.5783 | 0.23948 | 61.5004 | -0.03768 | 0.039079 | 61.6715 | -0.001436 | 61.4634 | 62.9318 | 62.9893 | 62.8621 | 63.11 | 62.8461 | 62.891 | 62.9532 | 123.1567 | 61.8178 | 123.0788 | 61.5407 | 61.6174 | 123.2498 | 61.5769 | 123.0418 | 61.5392 | 61.5797 | 61.4613 | 61.5018
3343.0625 | 123.3078 | -61.5875 | 61.6287 | 1.3946 | 1.4018 | 1.325 | 1.5271 | 1.2403 | 1.3492 | 1.4115 | 61.5829 | 0.24405 | 61.5004 | -0.03768 | 0.043657 | 61.6715 | 0.007721 | 61.468 | 62.9822 | 62.9893 | 62.9125 | 63.1146 | 62.8278 | 62.9367 | 62.999 | 123.1704 | 61.8316 | 123.0879 | 61.5498 | 61.6312 | 123.259 | 61.5952 | 123.0555 | 61.5392 | 61.5752 | 61.4567 | 61.4927
3344.0781 | 123.3994 | -61.5555 | 61.5509 | 1.4633 | 1.3789 | 1.4028 | 1.3989 | 1.2723 | 1.4271 | 1.4893 | 61.5783 | 0.25321 | 61.4867 | -0.03768 | 0.043657 | 61.676 | 0.012299 | 61.4542 | 63.0188 | 62.9344 | 62.9583 | 62.9544 | 62.8278 | 62.9825 | 63.0448 | 123.1338 | 61.8087 | 123.0421 | 61.5178 | 61.5991 | 123.2315 | 61.5678 | 123.0097 | 61.5346 | 61.566 | 61.443 | 61.4744
3345.0625 | 123.2758 | -61.5875 | 61.6013 | 1.4221 | 1.4064 | 1.3387 | 1.4172 | 1.254 | 1.3675 | 1.4298 | 61.5783 | 0.24405 | 61.4958 | -0.042259 | 0.039079 | 61.6715 | 0.003143 | 61.4634 | 63.0096 | 62.9939 | 62.9262 | 63.0047 | 62.8415 | 62.9551 | 63.0173 | 123.1658 | 61.8316 | 123.0833 | 61.5453 | 61.6266 | 123.259 | 61.5907 | 123.0509 | 61.5392 | 61.5752 | 61.4567 | 61.4927
3346.0625 | 123.3078 | -61.5738 | 61.6196 | 1.413 | 1.3926 | 1.3341 | 1.4218 | 1.286 | 1.3538 | 1.4252 | 61.5829 | 0.24863 | 61.4958 | -0.03768 | 0.039079 | 61.6806 | 0.003143 | 61.4542 | 62.9867 | 62.9664 | 62.9079 | 62.9956 | 62.8598 | 62.9276 | 62.999 | 123.1567 | 61.8224 | 123.0696 | 61.5361 | 61.6129 | 123.2544 | 61.5769 | 123.028 | 61.5438 | 61.5797 | 61.4567 | 61.4927
3347.1094 | 123.4177 | -61.5555 | 61.5555 | 1.4542 | 1.4155 | 1.3845 | 1.4172 | 1.2952 | 1.4087 | 1.4755 | 61.5783 | 0.24863 | 61.4958 | -0.033101 | 0.048236 | 61.676 | -0.006014 | 61.4542 | 63.0096 | 62.971 | 62.94 | 62.9727 | 62.8507 | 62.9642 | 63.031 | 123.1338 | 61.8041 | 123.0513 | 61.5224 | 61.6037 | 123.2315 | 61.5495 | 123.0097 | 61.5301 | 61.5843 | 61.4476 | 61.5018
3348.0625 | 123.3215 | -61.5646 | 61.615 | 1.4679 | 1.4201 | 1.3891 | 1.376 | 1.2906 | 1.4133 | 1.4801 | 61.5829 | 0.25321 | 61.4867 | -0.042259 | 0.048236 | 61.676 | -0.001436 | 61.4634 | 63.0325 | 62.9848 | 62.9537 | 62.9406 | 62.8553 | 62.978 | 63.0448 | 123.1475 | 61.8178 | 123.0513 | 61.5224 | 61.6129 | 123.2407 | 61.5632 | 123.028 | 61.5346 | 61.5843 | 61.4384 | 61.4881
3349.0938 | 123.3856 | -61.5463 | 61.5784 | 1.5137 | 1.4522 | 1.444 | 1.3623 | 1.2723 | 1.4728 | 1.5305 | 61.5737 | 0.24405 | 61.4912 | -0.033101 | 0.043657 | 61.6806 | 0.007721 | 61.4634 | 63.06 | 62.9985 | 62.9903 | 62.9086 | 62.8186 | 63.0192 | 63.0768 | 123.1201 | 61.7904 | 123.0376 | 61.5132 | 61.59 | 123.2269 | 61.554 | 123.0097 | 61.5301 | 61.566 | 61.4476 | 61.4835
3350.0625 | 123.2941 | -61.5692 | 61.6104 | 1.5595 | 1.5117 | 1.4852 | 1.4081 | 1.2952 | 1.5049 | 1.5808 | 61.5737 | 0.24863 | 61.4912 | -0.033101 | 0.043657 | 61.6898 | -0.001436 | 61.4588 | 63.1287 | 63.0809 | 63.0544 | 62.9773 | 62.8644 | 63.0741 | 63.1501 | 123.1429 | 61.8178 | 123.0605 | 61.5361 | 61.6129 | 123.259 | 61.5678 | 123.028 | 61.5301 | 61.5752 | 61.4476 | 61.4927
3351.0625 | 123.2849 | -61.5646 | 61.5875 | 1.5228 | 1.53 | 1.4532 | 1.4035 | 1.2998 | 1.4774 | 1.5488 | 61.5737 | 0.25321 | 61.4867 | -0.033101 | 0.043657 | 61.6806 | -0.001436 | 61.4588 | 63.0875 | 63.0947 | 63.0178 | 62.9681 | 62.8644 | 63.042 | 63.1134 | 123.1384 | 61.8178 | 123.0513 | 61.5315 | 61.6083 | 123.2452 | 61.5632 | 123.0234 | 61.5301 | 61.5752 | 61.443 | 61.4881
3352.0938 | 123.4406 | -61.5372 | 61.5509 | 1.4771 | 1.4613 | 1.4028 | 1.3623 | 1.2906 | 1.4316 | 1.4984 | 61.5783 | 0.24863 | 61.4958 | -0.033101 | 0.043657 | 61.6806 | -0.001436 | 61.4634 | 63.0142 | 62.9985 | 62.94 | 62.8994 | 62.8278 | 62.9688 | 63.0356 | 123.1155 | 61.7858 | 123.033 | 61.5041 | 61.5808 | 123.2178 | 61.5357 | 123.0006 | 61.5346 | 61.5797 | 61.4522 | 61.4973
3353.0625 | 123.3444 | -61.5326 | 61.6196 | 1.4908 | 1.4339 | 1.4165 | 1.3256 | 1.2586 | 1.4454 | 1.503 | 61.5783 | 0.25321 | 61.4912 | -0.033101 | 0.034501 | 61.676 | -0.001436 | 61.4588 | 63.0234 | 62.9665 | 62.9491 | 62.8582 | 62.7912 | 62.978 | 63.0356 | 123.1109 | 61.7858 | 123.0238 | 61.4995 | 61.5671 | 123.2086 | 61.5312 | 122.9914 | 61.5438 | 61.5797 | 61.4567 | 61.4927
3354.0625 | 123.3261 | -61.5555 | 61.6104 | 1.5595 | 1.4293 | 1.4898 | 1.376 | 1.3089 | 1.514 | 1.59 | 61.5737 | 0.24863 | 61.4821 | -0.03768 | 0.043657 | 61.676 | 0.007721 | 61.4634 | 63.1149 | 62.9848 | 63.0453 | 62.9315 | 62.8644 | 63.0695 | 63.1455 | 123.1292 | 61.8041 | 123.0376 | 61.5178 | 61.5991 | 123.2315 | 61.5632 | 123.0189 | 61.5301 | 61.566 | 61.4384 | 61.4744
3355.0625 | 123.2574 | -61.5875 | 61.5921 | 1.6236 | 1.4705 | 1.5539 | 1.4081 | 1.3272 | 1.5736 | 1.6358 | 61.5737 | 0.24863 | 61.4867 | -0.028522 | 0.043657 | 61.6852 | -0.001436 | 61.468 | 63.2111 | 63.058 | 63.1414 | 62.9956 | 62.9148 | 63.1611 | 63.2233 | 123.1613 | 61.8362 | 123.0742 | 61.559 | 61.6312 | 123.2727 | 61.5861 | 123.0555 | 61.5301 | 61.5752 | 61.443 | 61.4881
3356.0781 | 123.3627 | -61.5463 | 61.5417 | 1.5778 | 1.4659 | 1.5127 | 1.3852 | 1.2586 | 1.5324 | 1.5992 | 61.5737 | 0.25321 | 61.4912 | -0.033101 | 0.039079 | 61.6852 | 0.007721 | 61.4588 | 63.1241 | 63.0122 | 63.059 | 62.9315 | 62.8049 | 63.0787 | 63.1455 | 123.1201 | 61.7995 | 123.0376 | 61.5132 | 61.5854 | 123.2315 | 61.554 | 123.0051 | 61.5346 | 61.566 | 61.4522 | 61.4835
3357.0625 | 123.2986 | -61.5738 | 61.5784 | 1.564 | 1.4613 | 1.4944 | 1.376 | 1.254 | 1.5186 | 1.5854 | 61.5691 | 0.24863 | 61.5004 | -0.042259 | 0.048236 | 61.6715 | -0.006014 | 61.4542 | 63.1378 | 63.0351 | 63.0682 | 62.9498 | 62.8278 | 63.0924 | 63.1592 | 123.1429 | 61.8224 | 123.0742 | 61.5315 | 61.622 | 123.2452 | 61.5678 | 123.028 | 61.5209 | 61.5752 | 61.4522 | 61.5064
3358.0781 | 123.3353 | -61.5372 | 61.528 | 1.5503 | 1.4568 | 1.4852 | 1.4401 | 1.286 | 1.5095 | 1.5671 | 61.5783 | 0.24405 | 61.5096 | -0.023943 | 0.039079 | 61.6806 | 0.003143 | 61.4588 | 63.0875 | 62.9939 | 63.0224 | 62.9773 | 62.8232 | 63.0466 | 63.1043 | 123.1155 | 61.7812 | 123.0467 | 61.5132 | 61.5762 | 123.2178 | 61.5403 | 122.996 | 61.5392 | 61.5752 | 61.4705 | 61.5064
3359.0625 | 123.2803 | -61.5875 | 61.6013 | 1.4542 | 1.4247 | 1.3799 | 1.4355 | 1.2494 | 1.4133 | 1.4755 | 61.5875 | 0.24405 | 61.5233 | -0.042259 | 0.043657 | 61.6715 | -0.001436 | 61.4634 | 63.0417 | 63.0122 | 62.9674 | 63.023 | 62.8369 | 63.0008 | 63.0631 | 123.175 | 61.8316 | 123.1108 | 61.5453 | 61.6312 | 123.259 | 61.5861 | 123.0509 | 61.5438 | 61.5889 | 61.4796 | 61.5247
3360.0625 | 123.3078 | -61.5509 | 61.6058 | 1.5091 | 1.4476 | 1.4394 | 1.4767 | 1.2815 | 1.4591 | 1.5305 | 61.5829 | 0.25321 | 61.5141 | -0.03768 | 0.048236 | 61.676 | -0.006014 | 61.468 | 63.06 | 62.9985 | 62.9903 | 63.0276 | 62.8324 | 63.01 | 63.0814 | 123.1338 | 61.8041 | 123.065 | 61.5132 | 61.5991 | 123.2269 | 61.5449 | 123.0189 | 61.5346 | 61.5889 | 61.4659 | 61.5202
3361.0938 | 123.436 | -61.5005 | 61.5417 | 1.4587 | 1.4705 | 1.3891 | 1.4813 | 1.3135 | 1.4133 | 1.4801 | 61.5737 | 0.24863 | 61.5096 | -0.033101 | 0.034501 | 61.6806 | 0.003143 | 61.4588 | 62.9593 | 62.971 | 62.8896 | 62.9819 | 62.8141 | 62.9139 | 62.9807 | 123.0743 | 61.7492 | 123.0101 | 61.4674 | 61.535 | 123.1812 | 61.5037 | 122.9594 | 61.5392 | 61.5706 | 61.4751 | 61.5064
3362.0625 | 123.3124 | -61.5784 | 61.5784 | 1.3992 | 1.4384 | 1.3387 | 1.4584 | 1.2815 | 1.3584 | 1.4206 | 61.5829 | 0.24405 | 61.5096 | -0.03768 | 0.039079 | 61.6715 | 0.007721 | 61.4496 | 62.9776 | 63.0168 | 62.9171 | 63.0368 | 62.8598 | 62.9367 | 62.999 | 123.1613 | 61.8224 | 123.0879 | 61.5407 | 61.6174 | 123.2498 | 61.5861 | 123.028 | 61.5438 | 61.5752 | 61.4705 | 61.5018
3363.0938 | 123.3444 | -61.5326 | 61.5875 | 1.4084 | 1.4568 | 1.3433 | 1.4813 | 1.2723 | 1.3675 | 1.4298 | 61.5646 | 0.24405 | 61.4912 | -0.03768 | 0.039079 | 61.676 | 0.003143 | 61.4588 | 62.941 | 62.9893 | 62.8759 | 63.0139 | 62.8049 | 62.9001 | 62.9624 | 123.0972 | 61.7766 | 123.0238 | 61.4949 | 61.5717 | 123.2086 | 61.5357 | 122.9914 | 61.5255 | 61.5614 | 61.4522 | 61.4881
3364.0625 | 123.3627 | -61.5646 | 61.5921 | 1.4404 | 1.4568 | 1.3707 | 1.4813 | 1.2723 | 1.3996 | 1.471 | 61.5737 | 0.24405 | 61.4912 | -0.03768 | 0.048236 | 61.6806 | 0.003143 | 61.4634 | 63.0051 | 63.0214 | 62.9354 | 63.0459 | 62.837 | 62.9642 | 63.0356 | 123.1384 | 61.8087 | 123.0559 | 61.527 | 61.6129 | 123.2452 | 61.5678 | 123.028 | 61.5255 | 61.5706 | 61.443 | 61.4881
3365.0625 | 123.3124 | -61.5738 | 61.5738 | 1.445 | 1.3743 | 1.3799 | 1.4813 | 1.2632 | 1.395 | 1.471 | 61.5829 | 0.25321 | 61.505 | -0.03768 | 0.043657 | 61.6715 | 0.003143 | 61.4496 | 63.0188 | 62.9481 | 62.9537 | 63.0551 | 62.8369 | 62.9688 | 63.0448 | 123.1567 | 61.827 | 123.0788 | 61.5361 | 61.6174 | 123.2452 | 61.5769 | 123.0234 | 61.5392 | 61.5797 | 61.4613 | 61.5018
3366.0781 | 123.3994 | -61.5601 | 61.5463 | 1.4908 | 1.4064 | 1.4211 | 1.4493 | 1.2448 | 1.4454 | 1.5122 | 61.5737 | 0.25321 | 61.5141 | -0.028522 | 0.052814 | 61.6806 | -0.006014 | 61.4496 | 63.0508 | 62.9664 | 62.9812 | 63.0093 | 62.8049 | 63.0054 | 63.0722 | 123.1338 | 61.8133 | 123.0742 | 61.5315 | 61.6129 | 123.2407 | 61.554 | 123.0097 | 61.5209 | 61.5797 | 61.4613 | 61.5202
3367.0625 | 123.3673 | -61.6241 | 61.5326 | 1.6052 | 1.4705 | 1.531 | 1.4401 | 1.2677 | 1.5507 | 1.6266 | 61.5829 | 0.25321 | 61.5187 | -0.03768 | 0.034501 | 61.676 | -0.001436 | 61.4496 | 63.2294 | 63.0946 | 63.1551 | 63.0642 | 62.8919 | 63.1748 | 63.2508 | 123.207 | 61.8774 | 123.1429 | 61.5865 | 61.6586 | 123.3002 | 61.6227 | 123.0738 | 61.5484 | 61.5843 | 61.4842 | 61.5202
3368.0938 | 123.2895 | -61.6058 | 61.5692 | 1.5457 | 1.4247 | 1.476 | 1.4218 | 1.2311 | 1.5003 | 1.5671 | 61.5829 | 0.24863 | 61.5141 | -0.03768 | 0.039079 | 61.6852 | 0.007721 | 61.4542 | 63.1516 | 63.0305 | 63.0819 | 63.0276 | 62.8369 | 63.1061 | 63.1729 | 123.1887 | 61.8545 | 123.12 | 61.5682 | 61.6449 | 123.291 | 61.6136 | 123.0601 | 61.5438 | 61.5752 | 61.4751 | 61.5064
3369.0625 | 123.3398 | -61.5738 | 61.5921 | 1.5274 | 1.3652 | 1.4577 | 1.4722 | 1.2174 | 1.4774 | 1.5442 | 61.5829 | 0.25321 | 61.5233 | -0.03768 | 0.039079 | 61.6806 | 0.003143 | 61.4542 | 63.1012 | 62.939 | 63.0315 | 63.0459 | 62.7912 | 63.0512 | 63.118 | 123.1567 | 61.827 | 123.0971 | 61.5361 | 61.6129 | 123.2544 | 61.5769 | 123.028 | 61.5438 | 61.5797 | 61.4842 | 61.5202
3370.0781 | 123.2803 | -61.5692 | 61.615 | 1.532 | 1.3835 | 1.4669 | 1.4813 | 1.2586 | 1.5003 | 1.558 | 61.5829 | 0.25321 | 61.5187 | -0.03768 | 0.043657 | 61.6806 | 0.007721 | 61.4542 | 63.1012 | 62.9527 | 63.0361 | 63.0505 | 62.8278 | 63.0695 | 63.1272 | 123.1521 | 61.8224 | 123.0879 | 61.5315 | 61.6129 | 123.2498 | 61.5769 | 123.0234 | 61.5392 | 61.5752 | 61.4751 | 61.511
3371.0625 | 123.3215 | -61.5646 | 61.5784 | 1.5045 | 1.3606 | 1.4348 | 1.4493 | 1.2128 | 1.4545 | 1.5213 | 61.592 | 0.25779 | 61.5141 | -0.03768 | 0.043657 | 61.6806 | 0.003143 | 61.4496 | 63.0692 | 62.9252 | 62.9995 | 63.0139 | 62.7774 | 63.0192 | 63.086 | 123.1567 | 61.8224 | 123.0788 | 61.527 | 61.6083 | 123.2452 | 61.5678 | 123.0143 | 61.5484 | 61.5889 | 61.4705 | 61.511
3372.0938 | 123.2712 | -61.5692 | 61.5829 | 1.5045 | 1.3881 | 1.4394 | 1.463 | 1.2403 | 1.4591 | 1.5168 | 61.5783 | 0.24863 | 61.5141 | -0.033101 | 0.043657 | 61.6806 | -0.001436 | 61.4542 | 63.0737 | 62.9573 | 63.0086 | 63.0322 | 62.8095 | 63.0283 | 63.086 | 123.1475 | 61.8178 | 123.0833 | 61.5361 | 61.6129 | 123.2498 | 61.5678 | 123.0234 | 61.5346 | 61.5797 | 61.4705 | 61.5156
3373.0625 | 123.3078 | -61.5555 | 61.5921 | 1.5045 | 1.3972 | 1.4303 | 1.4355 | 1.2494 | 1.4591 | 1.5259 | 61.5829 | 0.25779 | 61.5187 | -0.033101 | 0.048236 | 61.676 | 0.003143 | 61.4496 | 63.06 | 62.9527 | 62.9857 | 62.991 | 62.8049 | 63.0146 | 63.0814 | 123.1384 | 61.8133 | 123.0742 | 61.5224 | 61.6037 | 123.2315 | 61.5586 | 123.0051 | 61.5346 | 61.5797 | 61.4705 | 61.5156
3374.0938 | 123.3994 | -61.5417 | 61.5601 | 1.5595 | 1.4293 | 1.4898 | 1.4309 | 1.2586 | 1.514 | 1.5808 | 61.5783 | 0.23948 | 61.5141 | -0.033101 | 0.043657 | 61.6852 | -0.001436 | 61.4496 | 63.1012 | 62.971 | 63.0315 | 62.9727 | 62.8003 | 63.0558 | 63.1226 | 123.1201 | 61.7812 | 123.0559 | 61.5086 | 61.5854 | 123.2269 | 61.5403 | 122.9914 | 61.5346 | 61.5797 | 61.4705 | 61.5156
3375.0625 | 123.3261 | -61.5738 | 61.5692 | 1.5595 | 1.3881 | 1.4898 | 1.4447 | 1.254 | 1.5232 | 1.5808 | 61.5875 | 0.24863 | 61.5096 | -0.033101 | 0.043657 | 61.6806 | 0.003143 | 61.4588 | 63.1333 | 62.9619 | 63.0636 | 63.0185 | 62.8278 | 63.097 | 63.1546 | 123.1613 | 61.8224 | 123.0833 | 61.5407 | 61.6174 | 123.2544 | 61.5769 | 123.0326 | 61.5438 | 61.5843 | 61.4659 | 61.5064
3376.0781 | 123.3124 | -61.5921 | 61.6333 | 1.4954 | 1.3514 | 1.4257 | 1.376 | 1.1624 | 1.4454 | 1.5122 | 61.5875 | 0.25321 | 61.5141 | -0.03768 | 0.034501 | 61.6806 | 0.003143 | 61.4542 | 63.0875 | 62.9435 | 63.0178 | 62.9681 | 62.7545 | 63.0375 | 63.1043 | 123.1796 | 61.8453 | 123.1062 | 61.5544 | 61.6266 | 123.2727 | 61.5952 | 123.0463 | 61.553 | 61.5843 | 61.4796 | 61.511
3377.0625 | 123.2758 | -61.5829 | 61.5692 | 1.5228 | 1.3698 | 1.4532 | 1.3897 | 1.1762 | 1.4774 | 1.5488 | 61.5783 | 0.25321 | 61.5141 | -0.03768 | 0.039079 | 61.676 | 0.003143 | 61.4542 | 63.1058 | 62.9527 | 63.0361 | 62.9727 | 62.7591 | 63.0604 | 63.1317 | 123.1613 | 61.8362 | 123.0971 | 61.5453 | 61.622 | 123.259 | 61.5861 | 123.0372 | 61.5392 | 61.5752 | 61.4751 | 61.511
3378.0938 | 123.317 | -61.5372 | 61.5921 | 1.4542 | 1.3469 | 1.3891 | 1.3577 | 1.1029 | 1.4179 | 1.4847 | 61.592 | 0.25779 | 61.5279 | -0.033101 | 0.039079 | 61.6669 | 0.003143 | 61.4451 | 62.9913 | 62.884 | 62.9262 | 62.8949 | 62.6401 | 62.9551 | 63.0219 | 123.1292 | 61.795 | 123.065 | 61.5041 | 61.5762 | 123.204 | 61.5403 | 122.9822 | 61.553 | 61.5889 | 61.4888 | 61.5247
3379.0625 | 123.3032 | -61.5463 | 61.5738 | 1.4771 | 1.3743 | 1.4165 | 1.3852 | 1.0938 | 1.4408 | 1.5076 | 61.5783 | 0.24863 | 61.5187 | -0.033101 | 0.039079 | 61.6715 | 0.003143 | 61.4588 | 63.0234 | 62.9207 | 62.9629 | 62.9315 | 62.6401 | 62.9871 | 63.0539 | 123.1246 | 61.795 | 123.065 | 61.5132 | 61.5854 | 123.2178 | 61.5495 | 123.0051 | 61.5392 | 61.5752 | 61.4796 | 61.5156
3380.0781 | 123.4039 | -61.5555 | 61.5692 | 1.5412 | 1.4293 | 1.476 | 1.4081 | 1.0663 | 1.5003 | 1.5671 | 61.5783 | 0.25321 | 61.5141 | -0.042259 | 0.043657 | 61.676 | 0.003143 | 61.4451 | 63.0966 | 62.9848 | 63.0315 | 62.9635 | 62.6218 | 63.0558 | 63.1226 | 123.1338 | 61.8087 | 123.0696 | 61.5132 | 61.5991 | 123.2315 | 61.5586 | 123.0006 | 61.5346 | 61.5752 | 61.4705 | 61.511
3381.0625 | 123.2849 | -61.5829 | 61.5829 | 1.5183 | 1.4247 | 1.4577 | 1.3577 | 1.0388 | 1.4866 | 1.5488 | 61.5783 | 0.24405 | 61.5141 | -0.028522 | 0.034501 | 61.6669 | 0.003143 | 61.4496 | 63.1012 | 63.0076 | 63.0407 | 62.9406 | 62.6218 | 63.0695 | 63.1317 | 123.1613 | 61.827 | 123.0971 | 61.5544 | 61.6174 | 123.2498 | 61.5861 | 123.0326 | 61.5438 | 61.5752 | 61.4796 | 61.511
3382.1094 | 123.3582 | -61.5509 | 61.5738 | 1.5503 | 1.4018 | 1.476 | 1.3668 | 1.0617 | 1.3675 | 1.5671 | 61.5783 | 0.24405 | 61.5096 | -0.042259 | 0.043657 | 61.6669 | -0.001436 | 61.4542 | 63.1012 | 62.9527 | 63.0269 | 62.9177 | 62.6126 | 62.9184 | 63.118 | 123.1292 | 61.795 | 123.0605 | 61.5086 | 61.5946 | 123.2178 | 61.5495 | 123.0051 | 61.5346 | 61.5797 | 61.4659 | 61.511
3383.0625 | 123.3261 | -61.5692 | 61.5784 | 1.5412 | 1.411 | 1.4715 | 1.3668 | 1.0159 | 1.3263 | 1.5717 | 61.5875 | 0.24863 | 61.5096 | -0.03768 | 0.039079 | 61.676 | 0.007721 | 61.4588 | 63.1104 | 62.9802 | 63.0407 | 62.9361 | 62.5852 | 62.8955 | 63.1409 | 123.1567 | 61.8178 | 123.0788 | 61.5315 | 61.6083 | 123.2452 | 61.5769 | 123.028 | 61.5484 | 61.5797 | 61.4705 | 61.5018
3384.0781 | 123.2803 | -61.5646 | 61.6104 | 1.4908 | 1.3926 | 1.4165 | 1.3348 | 1.08 | 1.4362 | 1.503 | 61.5875 | 0.24405 | 61.5096 | -0.03768 | 0.043657 | 61.6806 | -0.001436 | 61.4496 | 63.0554 | 62.9573 | 62.9812 | 62.8994 | 62.6447 | 63.0008 | 63.0677 | 123.1521 | 61.8087 | 123.0742 | 61.527 | 61.6083 | 123.2452 | 61.5632 | 123.0143 | 61.5438 | 61.5889 | 61.4659 | 61.511
3385.0625 | 123.2758 | -61.5555 | 61.5829 | 1.4633 | 1.3423 | 1.3936 | 1.289 | 1.0709 | 1.4225 | 1.4847 | 61.5875 | 0.24863 | 61.5233 | -0.033101 | 0.039079 | 61.676 | 0.003143 | 61.4496 | 63.0188 | 62.8978 | 62.9491 | 62.8445 | 62.6264 | 62.978 | 63.0402 | 123.1429 | 61.8041 | 123.0788 | 61.5224 | 61.5946 | 123.2315 | 61.5586 | 123.0051 | 61.5484 | 61.5843 | 61.4842 | 61.5202
3386.0781 | 123.4177 | -61.5372 | 61.5692 | 1.4816 | 1.3285 | 1.4211 | 1.2707 | 1.0572 | 1.4362 | 1.5122 | 61.5829 | 0.24863 | 61.5096 | -0.03768 | 0.039079 | 61.676 | 0.003143 | 61.4542 | 63.0188 | 62.8657 | 62.9583 | 62.8079 | 62.5943 | 62.9734 | 63.0493 | 123.1201 | 61.7858 | 123.0467 | 61.4995 | 61.5762 | 123.2132 | 61.5403 | 122.9914 | 61.5438 | 61.5797 | 61.4705 | 61.5064
3387.0625 | 123.2895 | -61.5829 | 61.615 | 1.5686 | 1.3926 | 1.4944 | 1.3348 | 1.1029 | 1.4271 | 1.5854 | 61.5829 | 0.25321 | 61.5096 | -0.033101 | 0.043657 | 61.6715 | -0.006014 | 61.4588 | 63.1516 | 62.9756 | 63.0773 | 62.9177 | 62.6859 | 63.01 | 63.1684 | 123.1658 | 61.8362 | 123.0925 | 61.5498 | 61.6266 | 123.2544 | 61.5769 | 123.0418 | 61.5392 | 61.5889 | 61.4659 | 61.5156
3388.0938 | 123.2758 | -61.5555 | 61.615 | 1.5137 | 1.3698 | 1.4486 | 1.3348 | 1.0663 | 1.4271 | 1.5351 | 61.5875 | 0.24405 | 61.5187 | -0.033101 | 0.039079 | 61.6852 | 0.003143 | 61.4496 | 63.0692 | 62.9252 | 63.0041 | 62.8903 | 62.6218 | 62.9825 | 63.0905 | 123.1429 | 61.7995 | 123.0742 | 61.5224 | 61.5946 | 123.2407 | 61.5586 | 123.0051 | 61.5484 | 61.5843 | 61.4796 | 61.5156
3389.0625 | 123.3582 | -61.5463 | 61.5829 | 1.5091 | 1.3148 | 1.4303 | 1.3165 | 1.0755 | 1.4591 | 1.5305 | 61.592 | 0.24863 | 61.5141 | -0.033101 | 0.043657 | 61.6669 | 0.003143 | 61.4451 | 63.0554 | 62.8611 | 62.9766 | 62.8628 | 62.6218 | 63.0054 | 63.0768 | 123.1384 | 61.795 | 123.0605 | 61.5132 | 61.59 | 123.2132 | 61.5495 | 122.9914 | 61.5484 | 61.5889 | 61.4705 | 61.511
3390.0781 | 123.3765 | -61.528 | 61.5692 | 1.5366 | 1.2599 | 1.4715 | 1.3165 | 1.0892 | 1.4957 | 1.5534 | 61.5829 | 0.25321 | 61.5096 | -0.033101 | 0.043657 | 61.676 | 0.003143 | 61.4542 | 63.0646 | 62.7879 | 62.9995 | 62.8445 | 62.6172 | 63.0237 | 63.0814 | 123.1109 | 61.7812 | 123.0376 | 61.4949 | 61.5717 | 123.204 | 61.5312 | 122.9822 | 61.5392 | 61.5797 | 61.4659 | 61.5064
3391.0625 | 123.3215 | -61.5555 | 61.5967 | 1.564 | 1.269 | 1.4898 | 1.3027 | 1.0846 | 1.5232 | 1.5808 | 61.5875 | 0.25779 | 61.5233 | -0.033101 | 0.039079 | 61.676 | -0.001436 | 61.4496 | 63.1195 | 62.8245 | 63.0453 | 62.8582 | 62.6401 | 63.0787 | 63.1363 | 123.1429 | 61.8133 | 123.0788 | 61.5224 | 61.5946 | 123.2315 | 61.554 | 123.0051 | 61.5484 | 61.5889 | 61.4842 | 61.5247
3392.1094 | 123.3398 | -61.5555 | 61.5875 | 1.5686 | 1.2828 | 1.4989 | 1.2707 | 1.0755 | 1.5232 | 1.5854 | 61.5829 | 0.24863 | 61.5187 | -0.033101 | 0.039079 | 61.676 | -0.001436 | 61.4542 | 63.1241 | 62.8382 | 63.0544 | 62.8262 | 62.6309 | 63.0787 | 63.1409 | 123.1384 | 61.8041 | 123.0742 | 61.5224 | 61.5946 | 123.2315 | 61.554 | 123.0097 | 61.5438 | 61.5843 | 61.4796 | 61.5202
3393.0625 | 123.3078 | -61.5829 | 61.6058 | 1.5961 | 1.2965 | 1.5356 | 1.3119 | 1.0663 | 1.5552 | 1.622 | 61.5875 | 0.24863 | 61.5141 | -0.033101 | 0.039079 | 61.676 | 0.003143 | 61.4634 | 63.179 | 62.8794 | 63.1185 | 62.8949 | 62.6493 | 63.1382 | 63.205 | 123.1704 | 61.8316 | 123.0971 | 61.5498 | 61.622 | 123.259 | 61.5861 | 123.0463 | 61.5484 | 61.5843 | 61.4751 | 61.511
3394.0781 | 123.3994 | -61.528 | 61.5875 | 1.5412 | 1.2507 | 1.4715 | 1.2661 | 0.98848 | 1.4957 | 1.5625 | 61.592 | 0.24863 | 61.5141 | -0.042259 | 0.039079 | 61.6715 | -0.001436 | 61.4542 | 63.0692 | 62.7787 | 62.9995 | 62.7941 | 62.5165 | 63.0237 | 63.0905 | 123.1201 | 61.7766 | 123.0422 | 61.4858 | 61.5671 | 123.1995 | 61.5266 | 122.9822 | 61.553 | 61.5935 | 61.4751 | 61.5156
3395.0625 | 123.2849 | -61.5646 | 61.5829 | 1.4908 | 1.2278 | 1.4211 | 1.2432 | 0.97475 | 1.4454 | 1.5122 | 61.5875 | 0.25321 | 61.5187 | -0.033101 | 0.048236 | 61.6669 | -0.001436 | 61.4451 | 63.0554 | 62.7924 | 62.9857 | 62.8079 | 62.5394 | 63.01 | 63.0768 | 123.1521 | 61.8178 | 123.0834 | 61.5315 | 61.6129 | 123.2315 | 61.5632 | 123.0097 | 61.5392 | 61.5889 | 61.4705 | 61.5202
3396.0938 | 123.2986 | -61.5784 | 61.5921 | 1.5091 | 1.2187 | 1.4532 | 1.2661 | 0.99306 | 1.4591 | 1.5305 | 61.592 | 0.24405 | 61.5187 | -0.033101 | 0.043657 | 61.676 | 0.007721 | 61.4634 | 63.0875 | 62.797 | 63.0315 | 62.8445 | 62.5714 | 63.0375 | 63.1089 | 123.1704 | 61.8224 | 123.0971 | 61.5453 | 61.622 | 123.2544 | 61.5861 | 123.0418 | 61.5484 | 61.5843 | 61.4751 | 61.511
3397.0625 | 123.2895 | -61.5555 | 61.6104 | 1.6007 | 1.2644 | 1.531 | 1.2799 | 1.0388 | 1.5507 | 1.6129 | 61.5875 | 0.24405 | 61.5141 | -0.03768 | 0.043657 | 61.676 | -0.001436 | 61.4588 | 63.1562 | 62.8199 | 63.0865 | 62.8353 | 62.5943 | 63.1061 | 63.1684 | 123.1429 | 61.7995 | 123.0696 | 61.5178 | 61.5991 | 123.2315 | 61.554 | 123.0143 | 61.5438 | 61.5889 | 61.4705 | 61.5156
3398.0625 | 123.317 | -61.5829 | 61.6058 | 1.619 | 1.3057 | 1.5447 | 1.2524 | 1.0434 | 1.5736 | 1.6449 | 61.5829 | 0.25321 | 61.5141 | -0.023943 | 0.043657 | 61.676 | -0.001436 | 61.4634 | 63.2019 | 62.8886 | 63.1277 | 62.8353 | 62.6264 | 63.1565 | 63.2279 | 123.1658 | 61.8362 | 123.0971 | 61.559 | 61.6266 | 123.259 | 61.5815 | 123.0463 | 61.5392 | 61.5843 | 61.4705 | 61.5156
3399.0938 | 123.3307 | -61.5417 | 61.615 | 1.6098 | 1.3057 | 1.5401 | 1.1745 | 0.99306 | 1.5644 | 1.6266 | 61.5829 | 0.25321 | 61.5141 | -0.03768 | 0.039079 | 61.676 | 0.003143 | 61.4634 | 63.1516 | 62.8474 | 63.0819 | 62.7163 | 62.5348 | 63.1061 | 63.1684 | 123.1246 | 61.795 | 123.0559 | 61.5041 | 61.5808 | 123.2178 | 61.5449 | 123.0051 | 61.5438 | 61.5797 | 61.4751 | 61.511
3400.0625 | 123.3353 | -61.5646 | 61.5829 | 1.6236 | 1.3011 | 1.5493 | 1.2295 | 0.99306 | 1.4454 | 1.6449 | 61.5875 | 0.24863 | 61.5141 | -0.03768 | 0.043657 | 61.676 | 0.003143 | 61.4634 | 63.1882 | 62.8657 | 63.1139 | 62.7941 | 62.5577 | 63.01 | 63.2096 | 123.1521 | 61.8133 | 123.0788 | 61.527 | 61.6083 | 123.2407 | 61.5678 | 123.028 | 61.5438 | 61.5843 | 61.4705 | 61.511
3401.0781 | 123.3398 | -61.5646 | 61.5921 | 1.5183 | 1.2644 | 1.4394 | 1.2295 | 0.97475 | 1.4591 | 1.5305 | 61.5875 | 0.25321 | 61.5187 | -0.03768 | 0.048236 | 61.676 | -0.001436 | 61.4542 | 63.0829 | 62.8291 | 63.0041 | 62.7941 | 62.5394 | 63.0237 | 63.0951 | 123.1521 | 61.8178 | 123.0834 | 61.527 | 61.6129 | 123.2407 | 61.5632 | 123.0189 | 61.5392 | 61.5889 | 61.4705 | 61.5202
3402.0625 | 123.3582 | -61.5509 | 61.5601 | 1.4633 | 1.2232 | 1.3936 | 1.1974 | 0.95643 | 1.3446 | 1.4847 | 61.5875 | 0.24863 | 61.5187 | -0.042259 | 0.039079 | 61.6669 | 0.003143 | 61.4496 | 63.0142 | 62.7741 | 62.9445 | 62.7483 | 62.5073 | 62.8955 | 63.0356 | 123.1384 | 61.7995 | 123.0696 | 61.5086 | 61.59 | 123.2178 | 61.554 | 123.0006 | 61.5484 | 61.5843 | 61.4796 | 61.5156
3403.0625 | 123.262 | -61.5692 | 61.5967 | 1.3901 | 1.2324 | 1.3112 | 1.2066 | 0.87861 | 1.3034 | 1.416 | 61.5875 | 0.24863 | 61.5233 | -0.033101 | 0.034501 | 61.6669 | -0.006014 | 61.4359 | 62.9593 | 62.8016 | 62.8804 | 62.7758 | 62.4478 | 62.8726 | 62.9852 | 123.1567 | 61.8178 | 123.0925 | 61.5361 | 61.6037 | 123.2361 | 61.5632 | 123.0051 | 61.553 | 61.5935 | 61.4888 | 61.5293
3404.0625 | 123.2712 | -61.5738 | 61.5829 | 1.3809 | 1.1912 | 1.3158 | 1.1562 | 0.87861 | 1.3355 | 1.3977 | 61.5966 | 0.24405 | 61.5324 | -0.033101 | 0.039079 | 61.6577 | -0.010593 | 61.4405 | 62.9547 | 62.765 | 62.8896 | 62.73 | 62.4524 | 62.9093 | 62.9715 | 123.1704 | 61.8178 | 123.1062 | 61.5407 | 61.6129 | 123.2315 | 61.5632 | 123.0143 | 61.5575 | 61.6072 | 61.4934 | 61.543
3405.0781 | 123.317 | -61.5738 | 61.6013 | 1.4084 | 1.2507 | 1.3387 | 1.2341 | 0.95643 | 1.363 | 1.4298 | 61.5875 | 0.24863 | 61.5187 | -0.03768 | 0.039079 | 61.6715 | 0.012299 | 61.4496 | 62.9822 | 62.8245 | 62.9125 | 62.8079 | 62.5302 | 62.9367 | 63.0036 | 123.1613 | 61.8224 | 123.0925 | 61.5361 | 61.6129 | 123.2452 | 61.5861 | 123.0234 | 61.5484 | 61.5752 | 61.4796 | 61.5064
3406.0625 | 123.262 | -61.5921 | 61.5967 | 1.4587 | 1.2461 | 1.3936 | 1.289 | 0.97932 | 1.4042 | 1.4847 | 61.5783 | 0.25321 | 61.5096 | -0.03768 | 0.043657 | 61.676 | 0.003143 | 61.4496 | 63.0508 | 62.8382 | 62.9857 | 62.8811 | 62.5714 | 62.9963 | 63.0768 | 123.1704 | 61.8453 | 123.1017 | 61.5544 | 61.6358 | 123.2681 | 61.5952 | 123.0417 | 61.5346 | 61.5752 | 61.4659 | 61.5064
3407.0938 | 123.3444 | -61.5463 | 61.6013 | 1.4496 | 1.2187 | 1.3799 | 1.2158 | 0.95186 | 1.3034 | 1.4664 | 61.592 | 0.25779 | 61.5004 | -0.028522 | 0.048236 | 61.6669 | 0.003143 | 61.4496 | 62.9959 | 62.765 | 62.9262 | 62.7621 | 62.4982 | 62.8498 | 63.0127 | 123.1384 | 61.8041 | 123.0467 | 61.5178 | 61.5946 | 123.2132 | 61.5495 | 122.996 | 61.5438 | 61.5889 | 61.4522 | 61.4973
3408.0625 | 123.2849 | -61.6104 | 61.5738 | 1.4954 | 1.3057 | 1.4257 | 1.2249 | 0.91523 | 1.3126 | 1.5259 | 61.5737 | 0.24405 | 61.4958 | -0.03768 | 0.043657 | 61.6669 | 0.007721 | 61.4634 | 63.1058 | 62.9161 | 63.0361 | 62.8353 | 62.5256 | 62.923 | 63.1363 | 123.1841 | 61.8545 | 123.1062 | 61.5727 | 61.6541 | 123.2773 | 61.6181 | 123.0738 | 61.5301 | 61.566 | 61.4522 | 61.4881
3409.0938 | 123.2986 | -61.5784 | 61.6104 | 1.5824 | 1.3148 | 1.5173 | 1.2249 | 0.93812 | 1.2989 | 1.6083 | 61.5783 | 0.25321 | 61.505 | -0.03768 | 0.048236 | 61.6715 | 0.003143 | 61.4542 | 63.1607 | 62.8932 | 63.0956 | 62.8033 | 62.5165 | 62.8772 | 63.1867 | 123.1567 | 61.8316 | 123.0833 | 61.5407 | 61.6266 | 123.2498 | 61.5815 | 123.0326 | 61.5301 | 61.5752 | 61.4567 | 61.5018
3410.0625 | 123.2803 | -61.5738 | 61.5829 | 1.564 | 1.3194 | 1.5081 | 1.2295 | 0.9427 | 1.3217 | 1.59 | 61.5783 | 0.24405 | 61.5187 | -0.042259 | 0.039079 | 61.6715 | 0.003143 | 61.4496 | 63.1378 | 62.8932 | 63.0819 | 62.8033 | 62.5165 | 62.8955 | 63.1638 | 123.1521 | 61.8178 | 123.0925 | 61.5315 | 61.6129 | 123.2452 | 61.5769 | 123.0234 | 61.5392 | 61.5752 | 61.4796 | 61.5156
3411.0781 | 123.2483 | -61.5417 | 61.6058 | 1.4404 | 1.2599 | 1.3753 | 1.2112 | 0.91065 | 1.3446 | 1.4618 | 61.5875 | 0.24863 | 61.5279 | -0.033101 | 0.039079 | 61.6715 | 0.007721 | 61.4542 | 62.9822 | 62.8016 | 62.9171 | 62.7529 | 62.4524 | 62.8864 | 63.0036 | 123.1292 | 61.7904 | 123.0696 | 61.5086 | 61.5808 | 123.2132 | 61.5495 | 122.996 | 61.5484 | 61.5797 | 61.4888 | 61.5202
3412.0625 | 123.4085 | -61.5692 | 61.5234 | 1.4816 | 1.2324 | 1.4028 | 1.1654 | 0.95643 | 1.4316 | 1.4984 | 61.5966 | 0.24405 | 61.5233 | -0.03768 | 0.039079 | 61.6715 | 0.003143 | 61.4496 | 63.0508 | 62.8016 | 62.972 | 62.7346 | 62.5256 | 63.0008 | 63.0677 | 123.1658 | 61.8133 | 123.0925 | 61.5315 | 61.6083 | 123.2407 | 61.5724 | 123.0189 | 61.5575 | 61.5935 | 61.4842 | 61.5202
3413.0781 | 123.3398 | -61.5875 | 61.5921 | 1.4084 | 1.1912 | 1.3433 | 1.1517 | 0.89234 | 1.3172 | 1.4206 | 61.6012 | 0.25321 | 61.5279 | -0.028522 | 0.043657 | 61.6669 | 0.007721 | 61.4542 | 62.9959 | 62.7787 | 62.9308 | 62.7392 | 62.4799 | 62.9047 | 63.0081 | 123.1887 | 61.8407 | 123.1154 | 61.559 | 61.6312 | 123.2544 | 61.5952 | 123.0418 | 61.5575 | 61.5935 | 61.4842 | 61.5202
3414.0625 | 123.2803 | -61.5692 | 61.5784 | 1.5457 | 1.2141 | 1.4715 | 1.202 | 0.90608 | 1.3172 | 1.558 | 61.592 | 0.25779 | 61.5096 | -0.03768 | 0.029923 | 61.676 | 0.003143 | 61.4588 | 63.1149 | 62.7833 | 63.0407 | 62.7712 | 62.4753 | 62.8864 | 63.1272 | 123.1613 | 61.827 | 123.0788 | 61.5315 | 61.5991 | 123.2452 | 61.5724 | 123.028 | 61.5621 | 61.5889 | 61.4796 | 61.5064
3415.0781 | 123.3032 | -61.5601 | 61.5875 | 1.5686 | 1.2507 | 1.4944 | 1.2936 | 0.9839 | 1.3767 | 1.59 | 61.5829 | 0.24863 | 61.4958 | -0.03768 | 0.043657 | 61.676 | 0.003143 | 61.4496 | 63.1287 | 62.8108 | 63.0544 | 62.8536 | 62.544 | 62.9367 | 63.1501 | 123.1429 | 61.8087 | 123.0559 | 61.5224 | 61.6037 | 123.2361 | 61.5632 | 123.0097 | 61.5392 | 61.5797 | 61.4522 | 61.4927
3416.0625 | 123.3032 | -61.5829 | 61.5692 | 1.4267 | 1.182 | 1.357 | 1.2203 | 0.92897 | 1.3767 | 1.4481 | 61.5875 | 0.25321 | 61.5233 | -0.03768 | 0.034501 | 61.6669 | 0.003143 | 61.4451 | 63.0096 | 62.765 | 62.9399 | 62.8033 | 62.5119 | 62.9596 | 63.031 | 123.1704 | 61.8362 | 123.1062 | 61.5453 | 61.6174 | 123.2498 | 61.5861 | 123.028 | 61.553 | 61.5843 | 61.4888 | 61.5202
3417.1094 | 123.3032 | -61.5417 | 61.6013 | 1.3946 | 1.1774 | 1.3295 | 1.202 | 0.92897 | 1.3538 | 1.416 | 61.592 | 0.25321 | 61.5187 | -0.03768 | 0.039079 | 61.6669 | 0.003143 | 61.4634 | 62.9364 | 62.7192 | 62.8713 | 62.7438 | 62.4707 | 62.8955 | 62.9578 | 123.1338 | 61.795 | 123.0605 | 61.5041 | 61.5808 | 123.2086 | 61.5449 | 123.0051 | 61.553 | 61.5889 | 61.4796 | 61.5156
3418.0625 | 123.2803 | -61.5967 | 61.6013 | 1.3901 | 1.182 | 1.3204 | 1.2158 | 0.96101 | 1.3401 | 1.416 | 61.5966 | 0.24863 | 61.5279 | -0.028522 | 0.039079 | 61.6623 | 0.003143 | 61.4405 | 62.9867 | 62.7787 | 62.9171 | 62.8124 | 62.5577 | 62.9367 | 63.0127 | 123.1933 | 61.8453 | 123.1246 | 61.5682 | 61.6358 | 123.259 | 61.5998 | 123.0372 | 61.5575 | 61.5935 | 61.4888 | 61.5247
3419.0781 | 123.3124 | -61.5738 | 61.5875 | 1.3534 | 1.1683 | 1.2837 | 1.1654 | 0.92439 | 1.308 | 1.3748 | 61.6012 | 0.25779 | 61.5279 | -0.028522 | 0.039079 | 61.6669 | -0.001436 | 61.4542 | 62.9272 | 62.7421 | 62.8575 | 62.7392 | 62.4982 | 62.8818 | 62.9486 | 123.175 | 61.8316 | 123.1017 | 61.5453 | 61.6129 | 123.2407 | 61.5724 | 123.028 | 61.5621 | 61.6026 | 61.4888 | 61.5293
3420.0625 | 123.2941 | -61.5829 | 61.5829 | 1.358 | 1.2003 | 1.2837 | 1.1654 | 0.93354 | 1.3172 | 1.3748 | 61.5966 | 0.25321 | 61.5233 | -0.03768 | 0.043657 | 61.6623 | 0.007721 | 61.4634 | 62.941 | 62.7833 | 62.8667 | 62.7483 | 62.5165 | 62.9001 | 62.9578 | 123.1796 | 61.8362 | 123.1062 | 61.5453 | 61.6266 | 123.2452 | 61.5907 | 123.0463 | 61.553 | 61.5889 | 61.4796 | 61.5156
3421.0781 | 123.3444 | -61.5509 | 61.6104 | 1.413 | 1.269 | 1.3341 | 1.1883 | 0.97932 | 1.363 | 1.4206 | 61.592 | 0.24405 | 61.5233 | -0.03768 | 0.039079 | 61.6669 | -0.001436 | 61.4588 | 62.9639 | 62.8199 | 62.885 | 62.7392 | 62.5302 | 62.9139 | 62.9715 | 123.1429 | 61.795 | 123.0742 | 61.5132 | 61.59 | 123.2178 | 61.5495 | 123.0097 | 61.553 | 61.5935 | 61.4842 | 61.5247
3422.0625 | 123.3673 | -61.5417 | 61.5509 | 1.4587 | 1.2095 | 1.3799 | 1.1883 | 1.0068 | 1.4087 | 1.4801 | 61.5829 | 0.25321 | 61.505 | -0.033101 | 0.039079 | 61.6715 | -0.001436 | 61.4496 | 63.0005 | 62.7512 | 62.9216 | 62.73 | 62.5485 | 62.9505 | 63.0219 | 123.1246 | 61.795 | 123.0467 | 61.5086 | 61.5808 | 123.2132 | 61.5403 | 122.9914 | 61.5438 | 61.5843 | 61.4659 | 61.5064
3423.0781 | 123.2895 | -61.5372 | 61.5921 | 1.4679 | 1.15 | 1.3936 | 1.1379 | 0.92897 | 1.4133 | 1.4939 | 61.5875 | 0.25321 | 61.5004 | -0.028522 | 0.048236 | 61.6669 | 0.007721 | 61.4588 | 63.0051 | 62.6871 | 62.9308 | 62.6751 | 62.4661 | 62.9505 | 63.031 | 123.1246 | 61.7904 | 123.0376 | 61.5086 | 61.5854 | 123.204 | 61.5449 | 122.996 | 61.5392 | 61.5797 | 61.4522 | 61.4927
3424.0625 | 123.2666 | -61.5784 | 61.5921 | 1.5228 | 1.1866 | 1.4486 | 1.1517 | 0.91523 | 1.482 | 1.5351 | 61.5829 | 0.25321 | 61.5141 | -0.028522 | 0.034501 | 61.6669 | 0.007721 | 61.4542 | 63.1012 | 62.765 | 63.0269 | 62.73 | 62.4936 | 63.0604 | 63.1134 | 123.1613 | 61.8316 | 123.0925 | 61.5498 | 61.6129 | 123.2452 | 61.5861 | 123.0326 | 61.5484 | 61.5752 | 61.4796 | 61.5064
3425.0781 | 123.3353 | -61.5784 | 61.615 | 1.4999 | 1.1866 | 1.4211 | 1.1425 | 0.95643 | 1.4499 | 1.5122 | 61.5966 | 0.25321 | 61.5187 | -0.03768 | 0.048236 | 61.6715 | -0.001436 | 61.4496 | 63.0783 | 62.765 | 62.9995 | 62.7209 | 62.5348 | 63.0283 | 63.0905 | 123.175 | 61.8316 | 123.0971 | 61.5407 | 61.6266 | 123.2498 | 61.5769 | 123.028 | 61.5484 | 61.5981 | 61.4705 | 61.5202
3426.0625 | 123.3215 | -61.5967 | 61.5692 | 1.4587 | 1.1866 | 1.3845 | 1.1288 | 0.93812 | 1.4042 | 1.4755 | 61.6012 | 0.24405 | 61.5187 | -0.03768 | 0.029923 | 61.6669 | 0.007721 | 61.4451 | 63.0554 | 62.7833 | 62.9812 | 62.7254 | 62.5348 | 63.0008 | 63.0722 | 123.1979 | 61.8407 | 123.1154 | 61.559 | 61.6266 | 123.2636 | 61.6044 | 123.0417 | 61.5713 | 61.5935 | 61.4888 | 61.511
3427.0625 | 123.3994 | -61.528 | 61.5509 | 1.5137 | 1.1774 | 1.444 | 1.1013 | 0.87403 | 1.2164 | 1.5488 | 61.5875 | 0.24863 | 61.5096 | -0.03768 | 0.039079 | 61.6715 | -0.001436 | 61.4542 | 63.0417 | 62.7055 | 62.972 | 62.6293 | 62.402 | 62.7445 | 63.0768 | 123.1155 | 61.7766 | 123.0376 | 61.4903 | 61.5671 | 123.1995 | 61.5266 | 122.9822 | 61.5484 | 61.5889 | 61.4705 | 61.511
3428.0938 | 123.2803 | -61.5921 | 61.5784 | 1.4404 | 1.1958 | 1.3662 | 1.1929 | 0.84198 | 1.2805 | 1.4572 | 61.5966 | 0.25321 | 61.5096 | -0.042259 | 0.039079 | 61.676 | 0.007721 | 61.4451 | 63.0325 | 62.7879 | 62.9583 | 62.785 | 62.4341 | 62.8726 | 63.0493 | 123.1887 | 61.8453 | 123.1017 | 61.5498 | 61.6312 | 123.2681 | 61.5998 | 123.0372 | 61.5575 | 61.5889 | 61.4705 | 61.5018
3429.0625 | 123.2849 | -61.5738 | 61.5967 | 1.4771 | 1.2415 | 1.3936 | 1.2158 | 0.88777 | 1.2943 | 1.4893 | 61.592 | 0.25321 | 61.5233 | -0.033101 | 0.039079 | 61.6715 | 0.007721 | 61.4451 | 63.0508 | 62.8153 | 62.9674 | 62.7895 | 62.4616 | 62.8681 | 63.0631 | 123.1658 | 61.827 | 123.0971 | 61.5407 | 61.6129 | 123.2452 | 61.5815 | 123.0189 | 61.553 | 61.5843 | 61.4842 | 61.5156
3430.0938 | 123.3398 | -61.5601 | 61.5738 | 1.4404 | 1.2049 | 1.3616 | 1.17 | 0.82825 | 1.2622 | 1.4481 | 61.5966 | 0.24863 | 61.5233 | -0.03768 | 0.043657 | 61.6669 | 0.003143 | 61.4451 | 63.0005 | 62.765 | 62.9216 | 62.73 | 62.3883 | 62.8223 | 63.0081 | 123.1567 | 61.8087 | 123.0834 | 61.5224 | 61.6037 | 123.2269 | 61.5632 | 123.0051 | 61.553 | 61.5935 | 61.4796 | 61.5202
3431.0625 | 123.2803 | -61.5829 | 61.5829 | 1.5824 | 1.237 | 1.5127 | 1.1791 | 0.86487 | 1.2576 | 1.6037 | 61.592 | 0.24863 | 61.5187 | -0.03768 | 0.043657 | 61.6715 | 0.003143 | 61.4542 | 63.1653 | 62.8199 | 63.0956 | 62.7621 | 62.4478 | 62.8406 | 63.1867 | 123.175 | 61.8316 | 123.1017 | 61.5453 | 61.6266 | 123.2544 | 61.5861 | 123.0372 | 61.5484 | 61.5889 | 61.4751 | 61.5156
3432.0625 | 123.3856 | -61.5692 | 61.5601 | 1.4679 | 1.2644 | 1.4028 | 1.202 | 0.89234 | 1.2027 | 1.4893 | 61.6012 | 0.25321 | 61.5324 | -0.03768 | 0.048236 | 61.6669 | 0.003143 | 61.4496 | 63.0371 | 62.8337 | 62.972 | 62.7712 | 62.4616 | 62.7719 | 63.0585 | 123.1704 | 61.8224 | 123.1017 | 61.5315 | 61.6175 | 123.2361 | 61.5724 | 123.0189 | 61.553 | 61.5981 | 61.4842 | 61.5293
3433.0938 | 123.3261 | -61.5509 | 61.5967 | 1.4862 | 1.2828 | 1.4211 | 1.1517 | 0.84656 | 1.189 | 1.503 | 61.592 | 0.25321 | 61.5233 | -0.042259 | 0.039079 | 61.6715 | 0.003143 | 61.4359 | 63.0371 | 62.8337 | 62.972 | 62.7026 | 62.3975 | 62.7399 | 63.0539 | 123.1429 | 61.8041 | 123.0742 | 61.5086 | 61.59 | 123.2224 | 61.554 | 122.9868 | 61.553 | 61.5889 | 61.4842 | 61.5202
3434.0625 | 123.3444 | -61.5784 | 61.6058 | 1.4404 | 1.2828 | 1.3616 | 1.0784 | 0.78247 | 1.0974 | 1.4527 | 61.5966 | 0.25779 | 61.5233 | -0.03768 | 0.039079 | 61.6623 | -0.001436 | 61.4405 | 63.0188 | 62.8611 | 62.94 | 62.6568 | 62.3608 | 62.6758 | 63.031 | 123.175 | 61.8362 | 123.1017 | 61.5407 | 61.6174 | 123.2407 | 61.5769 | 123.0189 | 61.5575 | 61.5981 | 61.4842 | 61.5247
3435.0938 | 123.2666 | -61.5921 | 61.5875 | 1.4404 | 1.3148 | 1.3662 | 1.1059 | 0.80078 | 1.0791 | 1.4618 | 61.5875 | 0.25321 | 61.5004 | -0.03768 | 0.043657 | 61.6669 | 0.003143 | 61.4496 | 63.0325 | 62.9069 | 62.9583 | 62.698 | 62.3929 | 62.6712 | 63.0539 | 123.1796 | 61.8453 | 123.0925 | 61.5544 | 61.6358 | 123.259 | 61.5952 | 123.0417 | 61.5438 | 61.5843 | 61.4567 | 61.4973
3436.0625 | 123.2849 | -61.5921 | 61.5738 | 1.4038 | 1.3331 | 1.325 | 1.1562 | 0.93354 | 1.3401 | 1.4115 | 61.5829 | 0.25779 | 61.505 | -0.03768 | 0.043657 | 61.6669 | -0.001436 | 61.4451 | 62.9959 | 62.9252 | 62.9171 | 62.7483 | 62.5256 | 62.9322 | 63.0036 | 123.175 | 61.8499 | 123.0971 | 61.5544 | 61.6358 | 123.259 | 61.5907 | 123.0372 | 61.5392 | 61.5843 | 61.4613 | 61.5064
3437.0938 | 123.2758 | -61.5463 | 61.6241 | 1.3443 | 1.3652 | 1.2792 | 1.17 | 0.91981 | 1.2989 | 1.3657 | 61.592 | 0.25779 | 61.5187 | -0.03768 | 0.048236 | 61.6715 | 0.007721 | 61.4405 | 62.8906 | 62.9115 | 62.8255 | 62.7163 | 62.4661 | 62.8452 | 62.912 | 123.1384 | 61.8041 | 123.065 | 61.5086 | 61.5946 | 123.2178 | 61.554 | 122.9868 | 61.5438 | 61.5843 | 61.4705 | 61.511
3438.0625 | 123.2391 | -61.5921 | 61.5784 | 1.3031 | 1.3469 | 1.238 | 1.2066 | 0.9015 | 1.2668 | 1.329 | 61.5966 | 0.25321 | 61.5141 | -0.03768 | 0.039079 | 61.6669 | 0.003143 | 61.4451 | 62.8952 | 62.939 | 62.8301 | 62.7987 | 62.4936 | 62.8589 | 62.9211 | 123.1887 | 61.8453 | 123.1062 | 61.5544 | 61.6312 | 123.259 | 61.5952 | 123.0372 | 61.5575 | 61.5935 | 61.4751 | 61.511
3439.0938 | 123.3215 | -61.5326 | 61.6287 | 1.3672 | 1.3377 | 1.3021 | 1.2203 | 0.93812 | 1.3172 | 1.3886 | 61.592 | 0.24863 | 61.5233 | -0.03768 | 0.048236 | 61.6715 | 0.003143 | 61.4451 | 62.8998 | 62.8703 | 62.8347 | 62.7529 | 62.4707 | 62.8498 | 62.9212 | 123.1246 | 61.7812 | 123.0559 | 61.4949 | 61.5808 | 123.204 | 61.5357 | 122.9777 | 61.5438 | 61.5889 | 61.4751 | 61.5202
3440.0625 | 123.2941 | -61.615 | 61.5738 | 1.4313 | 1.3377 | 1.3524 | 1.257 | 0.97932 | 1.3767 | 1.4435 | 61.5829 | 0.25321 | 61.5233 | -0.033101 | 0.034501 | 61.676 | 0.003143 | 61.4542 | 63.0463 | 62.9527 | 62.9674 | 62.872 | 62.5943 | 62.9917 | 63.0585 | 123.1979 | 61.8682 | 123.1383 | 61.5819 | 61.6495 | 123.291 | 61.6181 | 123.0692 | 61.5484 | 61.5797 | 61.4888 | 61.5202
3441.0938 | 123.3307 | -61.5509 | 61.5921 | 1.3992 | 1.2782 | 1.3341 | 1.2341 | 0.90608 | 1.3538 | 1.4206 | 61.592 | 0.25321 | 61.5279 | -0.03768 | 0.039079 | 61.6669 | -0.001436 | 61.4451 | 62.9501 | 62.8291 | 62.885 | 62.785 | 62.457 | 62.9047 | 62.9715 | 123.1429 | 61.8041 | 123.0788 | 61.5132 | 61.59 | 123.2178 | 61.5495 | 122.996 | 61.553 | 61.5935 | 61.4888 | 61.5293
3442.0625 | 123.317 | -61.5829 | 61.5692 | 1.3901 | 1.2278 | 1.3204 | 1.2295 | 0.96101 | 1.3492 | 1.4069 | 61.592 | 0.25321 | 61.4958 | -0.033101 | 0.043657 | 61.6623 | -0.001436 | 61.4451 | 62.973 | 62.8108 | 62.9033 | 62.8124 | 62.544 | 62.9322 | 62.9898 | 123.175 | 61.8362 | 123.0788 | 61.5498 | 61.6266 | 123.2452 | 61.5815 | 123.028 | 61.5484 | 61.5935 | 61.4522 | 61.4973
3443.0781 | 123.3444 | -61.5555 | 61.5875 | 1.4587 | 1.237 | 1.3845 | 1.1837 | 0.95643 | 1.4042 | 1.4755 | 61.5875 | 0.25321 | 61.5233 | -0.03768 | 0.052814 | 61.6669 | 0.003143 | 61.4588 | 63.0142 | 62.7925 | 62.94 | 62.7392 | 62.5119 | 62.9596 | 63.031 | 123.1429 | 61.8087 | 123.0788 | 61.5178 | 61.6083 | 123.2224 | 61.5586 | 123.0143 | 61.5346 | 61.5843 | 61.4705 | 61.5202
3444.0625 | 123.2712 | -61.6013 | 61.5784 | 1.4404 | 1.269 | 1.3799 | 1.1883 | 0.97017 | 1.4042 | 1.4618 | 61.592 | 0.24863 | 61.5233 | -0.042259 | 0.039079 | 61.6715 | 0.003143 | 61.4451 | 63.0417 | 62.8703 | 62.9812 | 62.7895 | 62.5714 | 63.0054 | 63.0631 | 123.1933 | 61.8499 | 123.1245 | 61.559 | 61.6403 | 123.2727 | 61.6044 | 123.0463 | 61.553 | 61.5889 | 61.4842 | 61.5202
3445.0938 | 123.2941 | -61.5555 | 61.5555 | 1.4404 | 1.2782 | 1.3707 | 1.2066 | 0.9839 | 1.395 | 1.4618 | 61.592 | 0.25321 | 61.5233 | -0.033101 | 0.043657 | 61.676 | -0.001436 | 61.4542 | 62.9959 | 62.8337 | 62.9262 | 62.7621 | 62.5394 | 62.9505 | 63.0173 | 123.1475 | 61.8087 | 123.0788 | 61.5224 | 61.5991 | 123.2315 | 61.554 | 123.0097 | 61.5484 | 61.5935 | 61.4796 | 61.5247
3446.0625 | 123.2758 | -61.5829 | 61.5784 | 1.4404 | 1.2187 | 1.3799 | 1.1379 | 0.95186 | 1.3904 | 1.4664 | 61.5829 | 0.25321 | 61.5004 | -0.033101 | 0.043657 | 61.6669 | -0.001436 | 61.4496 | 63.0234 | 62.8016 | 62.9628 | 62.7209 | 62.5348 | 62.9734 | 63.0493 | 123.1658 | 61.8362 | 123.0833 | 61.5498 | 61.6266 | 123.2498 | 61.5815 | 123.0326 | 61.5392 | 61.5843 | 61.4567 | 61.5018
3447.1094 | 123.3215 | -61.5463 | 61.6058 | 1.3901 | 1.269 | 1.325 | 1.1608 | 0.89692 | 1.3584 | 1.4115 | 61.6012 | 0.25321 | 61.5187 | -0.023943 | 0.043657 | 61.676 | 0.003143 | 61.4496 | 62.9364 | 62.8153 | 62.8713 | 62.7071 | 62.4432 | 62.9047 | 62.9578 | 123.1475 | 61.7995 | 123.065 | 61.5224 | 61.59 | 123.2224 | 61.5495 | 122.996 | 61.5575 | 61.5981 | 61.4751 | 61.5156
3448.0625 | 123.3032 | -61.5692 | 61.5646 | 1.3351 | 1.3331 | 1.2654 | 1.1425 | 0.93354 | 1.2851 | 1.3565 | 61.6012 | 0.25779 | 61.5233 | -0.042259 | 0.043657 | 61.6715 | -0.001436 | 61.4496 | 62.9043 | 62.9023 | 62.8346 | 62.7117 | 62.5028 | 62.8543 | 62.9257 | 123.1704 | 61.827 | 123.0925 | 61.527 | 61.6129 | 123.2407 | 61.5678 | 123.0189 | 61.5575 | 61.6026 | 61.4796 | 61.5247
3449.0781 | 123.3078 | -61.5555 | 61.6379 | 1.3809 | 1.356 | 1.3112 | 1.202 | 0.95643 | 1.3446 | 1.4069 | 61.5875 | 0.25321 | 61.5279 | -0.033101 | 0.048236 | 61.6669 | -0.001436 | 61.4542 | 62.9364 | 62.9115 | 62.8667 | 62.7575 | 62.5119 | 62.9001 | 62.9624 | 123.1429 | 61.8087 | 123.0834 | 61.5224 | 61.6037 | 123.2224 | 61.554 | 123.0097 | 61.5392 | 61.5889 | 61.4796 | 61.5293
3450.0625 | 123.381 | -61.5967 | 61.5326 | 1.3214 | 1.324 | 1.2609 | 1.202 | 0.93812 | 1.2851 | 1.3428 | 61.5829 | 0.25321 | 61.505 | -0.03768 | 0.039079 | 61.6623 | -0.001436 | 61.4405 | 62.9181 | 62.9206 | 62.8575 | 62.7987 | 62.5348 | 62.8818 | 62.9395 | 123.1796 | 61.8499 | 123.1017 | 61.559 | 61.6358 | 123.259 | 61.5952 | 123.0372 | 61.5438 | 61.5843 | 61.4659 | 61.5064
3451.0781 | 123.317 | -61.5646 | 61.5601 | 1.2802 | 1.2828 | 1.2059 | 1.1517 | 0.91981 | 1.2302 | 1.297 | 61.6012 | 0.24863 | 61.5096 | -0.033101 | 0.039079 | 61.6577 | -0.001436 | 61.4451 | 62.8448 | 62.8474 | 62.7705 | 62.7163 | 62.4844 | 62.7948 | 62.8616 | 123.1658 | 61.8133 | 123.0742 | 61.5315 | 61.6037 | 123.2224 | 61.5632 | 123.0097 | 61.5621 | 61.6026 | 61.4705 | 61.511
3452.0625 | 123.349 | -61.5463 | 61.5784 | 1.3077 | 1.2965 | 1.2425 | 1.1471 | 0.9427 | 1.2668 | 1.3336 | 61.592 | 0.24863 | 61.5279 | -0.042259 | 0.043657 | 61.6715 | -0.010593 | 61.4542 | 62.854 | 62.8428 | 62.7889 | 62.6934 | 62.489 | 62.8131 | 62.88 | 123.1384 | 61.795 | 123.0742 | 61.5041 | 61.59 | 123.2178 | 61.5357 | 123.0006 | 61.5484 | 61.6026 | 61.4842 | 61.5385
3453.0938 | 123.2803 | -61.5738 | 61.5829 | 1.2573 | 1.2782 | 1.1968 | 1.1104 | 0.87861 | 1.221 | 1.2787 | 61.6012 | 0.25321 | 61.5279 | -0.03768 | 0.039079 | 61.6669 | 0.003143 | 61.4496 | 62.8311 | 62.852 | 62.7705 | 62.6842 | 62.4524 | 62.7948 | 62.8525 | 123.175 | 61.827 | 123.1017 | 61.5361 | 61.6129 | 123.2407 | 61.5769 | 123.0234 | 61.5621 | 61.5981 | 61.4888 | 61.5247
3454.0625 | 123.3353 | -61.5738 | 61.5784 | 1.2985 | 1.3102 | 1.2242 | 1.0921 | 0.88319 | 1.2485 | 1.3062 | 61.5966 | 0.25321 | 61.505 | -0.03768 | 0.039079 | 61.6577 | -0.001436 | 61.4542 | 62.8723 | 62.884 | 62.798 | 62.6659 | 62.457 | 62.8223 | 62.8799 | 123.1704 | 61.827 | 123.0788 | 61.5361 | 61.6129 | 123.2315 | 61.5724 | 123.028 | 61.5575 | 61.5981 | 61.4659 | 61.5064
3455.0781 | 123.3398 | -61.5509 | 61.5967 | 1.3214 | 1.324 | 1.2517 | 1.1196 | 0.90608 | 1.2805 | 1.3428 | 61.592 | 0.25321 | 61.5141 | -0.033101 | 0.043657 | 61.6715 | -0.006014 | 61.4496 | 62.8723 | 62.8749 | 62.8026 | 62.6705 | 62.457 | 62.8314 | 62.8937 | 123.1429 | 61.8041 | 123.065 | 61.5178 | 61.5946 | 123.2224 | 61.5449 | 123.0006 | 61.5484 | 61.5981 | 61.4705 | 61.5202
3456.0625 | 123.3215 | -61.5738 | 61.5601 | 1.3077 | 1.2553 | 1.2334 | 1.0876 | 0.89692 | 1.2668 | 1.3245 | 61.592 | 0.25321 | 61.5279 | -0.033101 | 0.039079 | 61.6623 | -0.006014 | 61.4496 | 62.8814 | 62.8291 | 62.8072 | 62.6613 | 62.4707 | 62.8406 | 62.8983 | 123.1658 | 61.827 | 123.1017 | 61.5407 | 61.6129 | 123.2361 | 61.5678 | 123.0234 | 61.553 | 61.5981 | 61.4888 | 61.5339
3457.0938 | 123.4726 | -61.5097 | 61.5738 | 1.3305 | 1.2324 | 1.2654 | 1.0555 | 0.88777 | 1.2897 | 1.3474 | 61.6012 | 0.25779 | 61.537 | -0.033101 | 0.043657 | 61.6715 | 0.003143 | 61.4451 | 62.8402 | 62.7421 | 62.7751 | 62.5652 | 62.3975 | 62.7994 | 62.8571 | 123.1109 | 61.7675 | 123.0467 | 61.4766 | 61.5534 | 123.1812 | 61.5128 | 122.9548 | 61.5575 | 61.5981 | 61.4934 | 61.5339
3458.0625 | 123.3856 | -61.5463 | 61.5463 | 1.3122 | 1.2003 | 1.2425 | 1.0464 | 0.89234 | 1.2668 | 1.3336 | 61.592 | 0.25321 | 61.5187 | -0.028522 | 0.039079 | 61.6623 | 0.003143 | 61.4405 | 62.8586 | 62.7467 | 62.7889 | 62.5927 | 62.4387 | 62.8131 | 62.88 | 123.1384 | 61.7995 | 123.065 | 61.5178 | 61.5854 | 123.2086 | 61.5495 | 122.9868 | 61.553 | 61.5889 | 61.4796 | 61.5156
3459.0781 | 123.3261 | -61.5555 | 61.5921 | 1.2802 | 1.1591 | 1.2059 | 1.0235 | 0.86487 | 1.2393 | 1.297 | 61.5966 | 0.25321 | 61.5187 | -0.028522 | 0.039079 | 61.6577 | 0.003143 | 61.4405 | 62.8357 | 62.7146 | 62.7614 | 62.5789 | 62.4204 | 62.7948 | 62.8525 | 123.1521 | 61.8087 | 123.0742 | 61.527 | 61.5946 | 123.2132 | 61.5586 | 122.996 | 61.5575 | 61.5935 | 61.4796 | 61.5156
3460.0625 | 123.3078 | -61.5555 | 61.5692 | 1.3214 | 1.15 | 1.238 | 1.0372 | 0.84656 | 1.2668 | 1.2741 | 61.592 | 0.25321 | 61.5187 | -0.033101 | 0.039079 | 61.6577 | -0.006014 | 61.4359 | 62.8769 | 62.7055 | 62.7934 | 62.5927 | 62.402 | 62.8223 | 62.8296 | 123.1475 | 61.8087 | 123.0742 | 61.5224 | 61.5946 | 123.2132 | 61.5495 | 122.9914 | 61.553 | 61.5981 | 61.4796 | 61.5247
3461.0781 | 123.2803 | -61.5692 | 61.5921 | 1.2939 | 1.182 | 1.2288 | 1.0464 | 0.83283 | 1.2439 | 1.2695 | 61.5966 | 0.24405 | 61.5324 | -0.033101 | 0.039079 | 61.6531 | 0.003143 | 61.4496 | 62.8631 | 62.7512 | 62.798 | 62.6156 | 62.402 | 62.8131 | 62.8387 | 123.1658 | 61.8133 | 123.1017 | 61.5361 | 61.6083 | 123.2224 | 61.5724 | 123.0189 | 61.5575 | 61.5935 | 61.4934 | 61.5293
3462.0625 | 123.3536 | -61.5555 | 61.5692 | 1.3305 | 1.2553 | 1.2517 | 1.083 | 0.82825 | 1.2851 | 1.3474 | 61.5966 | 0.24863 | 61.5279 | -0.042259 | 0.043657 | 61.6669 | 0.007721 | 61.4313 | 62.886 | 62.8108 | 62.8072 | 62.6385 | 62.3837 | 62.8406 | 62.9028 | 123.1521 | 61.8041 | 123.0834 | 61.5132 | 61.5991 | 123.2224 | 61.5632 | 122.9868 | 61.553 | 61.5889 | 61.4842 | 61.5202
3463.0938 | 123.4314 | -61.5509 | 61.5738 | 1.2893 | 1.2553 | 1.2105 | 1.0921 | 0.84656 | 1.2393 | 1.3062 | 61.592 | 0.24863 | 61.5279 | -0.03768 | 0.039079 | 61.6577 | 0.003143 | 61.4313 | 62.8402 | 62.8062 | 62.7614 | 62.643 | 62.3975 | 62.7902 | 62.8571 | 123.1429 | 61.7995 | 123.0788 | 61.5132 | 61.59 | 123.2086 | 61.554 | 122.9822 | 61.553 | 61.5889 | 61.4888 | 61.5247
3464.0625 | 123.436 | -61.5601 | 61.5143 | 1.3031 | 1.2461 | 1.2334 | 1.1104 | 0.87403 | 1.2576 | 1.3153 | 61.592 | 0.25321 | 61.5324 | -0.03768 | 0.043657 | 61.6669 | -0.006014 | 61.4359 | 62.8631 | 62.8062 | 62.7934 | 62.6705 | 62.4341 | 62.8177 | 62.8754 | 123.1521 | 61.8133 | 123.0925 | 61.5224 | 61.6037 | 123.2269 | 61.554 | 122.996 | 61.5484 | 61.5981 | 61.4888 | 61.5385
3465.0938 | 123.2391 | -61.5784 | 61.5692 | 1.326 | 1.2507 | 1.2609 | 1.1333 | 0.90608 | 1.276 | 1.3428 | 61.5966 | 0.24863 | 61.5187 | -0.033101 | 0.039079 | 61.6669 | 0.003143 | 61.4451 | 62.9043 | 62.8291 | 62.8392 | 62.7117 | 62.4844 | 62.8543 | 62.9212 | 123.175 | 61.827 | 123.0971 | 61.5453 | 61.6174 | 123.2452 | 61.5815 | 123.0234 | 61.5575 | 61.5935 | 61.4796 | 61.5156
3466.0625 | 123.4177 | -61.5646 | 61.5417 | 1.2436 | 1.2828 | 1.183 | 1.0967 | 0.91523 | 1.2027 | 1.265 | 61.5966 | 0.25321 | 61.5141 | -0.03768 | 0.034501 | 61.6577 | 0.003143 | 61.4451 | 62.8082 | 62.8474 | 62.7477 | 62.6613 | 62.4799 | 62.7673 | 62.8296 | 123.1613 | 61.8178 | 123.0788 | 61.527 | 61.5991 | 123.2224 | 61.5678 | 123.0097 | 61.5621 | 61.5935 | 61.4796 | 61.511
3467.1094 | 123.3032 | -61.5372 | 61.5784 | 1.239 | 1.2507 | 1.1739 | 1.0876 | 0.90608 | 1.1981 | 1.2512 | 61.5966 | 0.24863 | 61.505 | -0.033101 | 0.043657 | 61.6577 | -0.001436 | 61.4496 | 62.7761 | 62.7879 | 62.711 | 62.6247 | 62.4432 | 62.7353 | 62.7884 | 123.1338 | 61.7858 | 123.0422 | 61.5041 | 61.5808 | 123.1949 | 61.5357 | 122.9868 | 61.553 | 61.5981 | 61.4613 | 61.5064
3468.0625 | 123.3032 | -61.5509 | 61.6425 | 1.2436 | 1.2232 | 1.183 | 1.0738 | 0.88777 | 1.2073 | 1.265 | 61.592 | 0.25321 | 61.505 | -0.023943 | 0.048236 | 61.6531 | -0.001436 | 61.4542 | 62.7945 | 62.7741 | 62.7339 | 62.6247 | 62.4387 | 62.7582 | 62.8159 | 123.1429 | 61.8041 | 123.0559 | 61.527 | 61.5991 | 123.204 | 61.5495 | 123.0051 | 61.5438 | 61.5935 | 61.4567 | 61.5064
3469.0938 | 123.2803 | -61.5646 | 61.5921 | 1.2893 | 1.269 | 1.2151 | 1.0784 | 0.91523 | 1.2348 | 1.3062 | 61.592 | 0.25321 | 61.5187 | -0.03768 | 0.034501 | 61.6623 | 0.003143 | 61.4496 | 62.854 | 62.8337 | 62.7797 | 62.643 | 62.4799 | 62.7994 | 62.8708 | 123.1567 | 61.8178 | 123.0834 | 61.527 | 61.5991 | 123.2269 | 61.5678 | 123.0143 | 61.5575 | 61.5889 | 61.4842 | 61.5156
3470.0625 | 123.3856 | -61.5372 | 61.5417 | 1.2802 | 1.2461 | 1.2059 | 1.0921 | 0.88319 | 1.2302 | 1.2878 | 61.592 | 0.26237 | 61.5324 | -0.033101 | 0.039079 | 61.6577 | 0.003143 | 61.4451 | 62.8174 | 62.7833 | 62.7431 | 62.6293 | 62.4204 | 62.7674 | 62.825 | 123.1292 | 61.7995 | 123.0696 | 61.5041 | 61.5762 | 123.1949 | 61.5403 | 122.9822 | 61.553 | 61.5889 | 61.4934 | 61.5293
3471.0781 | 123.3398 | -61.5463 | 61.6013 | 1.271 | 1.2553 | 1.2013 | 1.1608 | 0.88319 | 1.221 | 1.3016 | 61.6012 | 0.25321 | 61.5324 | -0.03768 | 0.048236 | 61.6669 | -0.001436 | 61.4496 | 62.8174 | 62.8016 | 62.7477 | 62.7071 | 62.4295 | 62.7673 | 62.8479 | 123.1475 | 61.7995 | 123.0788 | 61.5086 | 61.5946 | 123.2132 | 61.5449 | 122.996 | 61.553 | 61.6026 | 61.4842 | 61.5339
3472.0625 | 123.4497 | -61.496 | 61.5784 | 1.2207 | 1.237 | 1.1647 | 1.1013 | 0.83283 | 1.1844 | 1.2466 | 61.6104 | 0.25779 | 61.537 | -0.033101 | 0.039079 | 61.6577 | 0.003143 | 61.4451 | 62.7166 | 62.7329 | 62.6607 | 62.5973 | 62.3288 | 62.6804 | 62.7426 | 123.1063 | 61.7538 | 123.033 | 61.4629 | 61.5351 | 123.1537 | 61.4991 | 122.941 | 61.5713 | 61.6072 | 61.4979 | 61.5339
3473.0938 | 123.2849 | -61.5509 | 61.6196 | 1.239 | 1.2324 | 1.183 | 1.0876 | 0.84198 | 1.1936 | 1.265 | 61.6012 | 0.25321 | 61.5324 | -0.03768 | 0.043657 | 61.6623 | 0.003143 | 61.4496 | 62.7899 | 62.7833 | 62.7339 | 62.6385 | 62.3929 | 62.7445 | 62.8159 | 123.1521 | 61.8041 | 123.0834 | 61.5132 | 61.5946 | 123.2132 | 61.554 | 123.0006 | 61.5575 | 61.5981 | 61.4888 | 61.5293
3474.0625 | 123.4268 | -61.5509 | 61.5463 | 1.2024 | 1.1774 | 1.1327 | 1.0601 | 0.82825 | 1.1569 | 1.2192 | 61.6058 | 0.25321 | 61.537 | -0.042259 | 0.039079 | 61.6623 | 0.003143 | 61.4405 | 62.7533 | 62.7283 | 62.6836 | 62.611 | 62.3792 | 62.7078 | 62.7701 | 123.1567 | 61.8041 | 123.0879 | 61.5086 | 61.59 | 123.2132 | 61.554 | 122.9914 | 61.5667 | 61.6026 | 61.4979 | 61.5339
3475.0781 | 123.3353 | -61.5463 | 61.5646 | 1.2207 | 1.1958 | 1.151 | 1.0647 | 0.84656 | 1.1707 | 1.2466 | 61.592 | 0.25321 | 61.5187 | -0.033101 | 0.039079 | 61.6623 | 0.007721 | 61.4405 | 62.767 | 62.7421 | 62.6973 | 62.611 | 62.3929 | 62.717 | 62.793 | 123.1384 | 61.7995 | 123.065 | 61.5132 | 61.5854 | 123.2086 | 61.554 | 122.9868 | 61.553 | 61.5843 | 61.4796 | 61.511
3476.0625 | 123.4085 | -61.5326 | 61.5372 | 1.3031 | 1.2736 | 1.2334 | 1.1196 | 0.86945 | 1.2668 | 1.329 | 61.592 | 0.25779 | 61.505 | -0.03768 | 0.039079 | 61.6623 | 0.003143 | 61.4451 | 62.8357 | 62.8062 | 62.766 | 62.6522 | 62.402 | 62.7994 | 62.8616 | 123.1246 | 61.7904 | 123.0376 | 61.4949 | 61.5717 | 123.1949 | 61.5357 | 122.9777 | 61.553 | 61.5889 | 61.4659 | 61.5018
3477.0938 | 123.3078 | -61.5417 | 61.5875 | 1.2939 | 1.2828 | 1.2288 | 1.1288 | 0.89234 | 1.2485 | 1.3153 | 61.5875 | 0.24863 | 61.505 | -0.028522 | 0.039079 | 61.6669 | -0.001436 | 61.4451 | 62.8357 | 62.8245 | 62.7706 | 62.6705 | 62.4341 | 62.7902 | 62.8571 | 123.1292 | 61.7904 | 123.0467 | 61.5132 | 61.5808 | 123.2086 | 61.5403 | 122.9868 | 61.5484 | 61.5889 | 61.4659 | 61.5064
3478.0625 | 123.3307 | -61.5372 | 61.5738 | 1.3077 | 1.2965 | 1.2288 | 1.1288 | 0.88777 | 1.2576 | 1.329 | 61.5966 | 0.25321 | 61.5141 | -0.03768 | 0.039079 | 61.6623 | 0.007721 | 61.4451 | 62.8448 | 62.8337 | 62.766 | 62.6659 | 62.4249 | 62.7948 | 62.8662 | 123.1338 | 61.7904 | 123.0513 | 61.4995 | 61.5762 | 123.1995 | 61.5449 | 122.9822 | 61.5575 | 61.5889 | 61.4751 | 61.5064
3479.0781 | 123.2712 | -61.5784 | 61.5692 | 1.3077 | 1.237 | 1.2425 | 1.1196 | 0.88319 | 1.2668 | 1.3382 | 61.5966 | 0.25321 | 61.5233 | -0.042259 | 0.043657 | 61.6623 | -0.006014 | 61.4542 | 62.886 | 62.8153 | 62.8209 | 62.698 | 62.4616 | 62.8452 | 62.9166 | 123.175 | 61.8316 | 123.1017 | 61.5361 | 61.622 | 123.2407 | 61.5724 | 123.0326 | 61.553 | 61.6026 | 61.4796 | 61.5293
3480.0625 | 123.381 | -61.5143 | 61.5509 | 1.3305 | 1.2919 | 1.2563 | 1.1471 | 0.91523 | 1.276 | 1.3382 | 61.5966 | 0.25321 | 61.5279 | -0.03768 | 0.039079 | 61.6669 | 0.003143 | 61.4451 | 62.8448 | 62.8062 | 62.7706 | 62.6614 | 62.4295 | 62.7902 | 62.8525 | 123.1109 | 61.7675 | 123.0422 | 61.4766 | 61.5534 | 123.1812 | 61.5174 | 122.9594 | 61.5575 | 61.5935 | 61.4888 | 61.5247
3481.0781 | 123.2803 | -61.5829 | 61.5692 | 1.2802 | 1.2965 | 1.2105 | 1.1288 | 0.88319 | 1.2302 | 1.2878 | 61.5966 | 0.25321 | 61.5233 | -0.03768 | 0.043657 | 61.6577 | -0.001436 | 61.4542 | 62.8631 | 62.8794 | 62.7934 | 62.7117 | 62.4661 | 62.8131 | 62.8708 | 123.1796 | 61.8362 | 123.1062 | 61.5453 | 61.6266 | 123.2407 | 61.5815 | 123.0372 | 61.553 | 61.5981 | 61.4796 | 61.5247
3482.0625 | 123.4131 | -61.5097 | 61.5784 | 1.2298 | 1.2599 | 1.1647 | 1.1333 | 0.84198 | 1.1798 | 1.2421 | 61.6012 | 0.25321 | 61.5096 | -0.033101 | 0.043657 | 61.6623 | 0.003143 | 61.4451 | 62.7395 | 62.7696 | 62.6744 | 62.643 | 62.3517 | 62.6895 | 62.7518 | 123.1109 | 61.7629 | 123.0193 | 61.4766 | 61.5534 | 123.172 | 61.5128 | 122.9548 | 61.5575 | 61.5981 | 61.4659 | 61.5064
3483.0938 | 123.3719 | -61.5326 | 61.5921 | 1.1749 | 1.2049 | 1.1143 | 1.0876 | 0.83741 | 1.1295 | 1.1963 | 61.592 | 0.24405 | 61.5187 | -0.03768 | 0.034501 | 61.6577 | -0.001436 | 61.4451 | 62.7075 | 62.7375 | 62.6469 | 62.6201 | 62.37 | 62.662 | 62.7289 | 123.1246 | 61.7766 | 123.0513 | 61.4949 | 61.5671 | 123.1903 | 61.5312 | 122.9777 | 61.5575 | 61.5935 | 61.4842 | 61.5202
3484.0625 | 123.3627 | -61.5326 | 61.5509 | 1.1383 | 1.2003 | 1.0731 | 1.115 | 0.84656 | 1.0882 | 1.1642 | 61.6012 | 0.25321 | 61.5279 | -0.033101 | 0.034501 | 61.6577 | -0.001436 | 61.4359 | 62.6708 | 62.7329 | 62.6057 | 62.6476 | 62.3792 | 62.6208 | 62.6968 | 123.1338 | 61.7858 | 123.0605 | 61.4995 | 61.5671 | 123.1903 | 61.5312 | 122.9685 | 61.5667 | 61.6026 | 61.4934 | 61.5293
3485.0781 | 123.3215 | -61.5646 | 61.5829 | 1.1795 | 1.2049 | 1.1143 | 1.0921 | 0.85114 | 1.134 | 1.1917 | 61.6058 | 0.24863 | 61.5324 | -0.03768 | 0.039079 | 61.6531 | 0.003143 | 61.4359 | 62.7441 | 62.7696 | 62.679 | 62.6568 | 62.4158 | 62.6987 | 62.7563 | 123.1704 | 61.8133 | 123.0971 | 61.527 | 61.6037 | 123.2178 | 61.5678 | 123.0005 | 61.5667 | 61.6026 | 61.4934 | 61.5293
3486.0625 | 123.3719 | -61.5601 | 61.5738 | 1.2252 | 1.1774 | 1.1601 | 1.0601 | 0.85572 | 1.1844 | 1.1139 | 61.6012 | 0.25779 | 61.5324 | -0.03768 | 0.048236 | 61.6623 | -0.006014 | 61.4222 | 62.7853 | 62.7375 | 62.7202 | 62.6201 | 62.4158 | 62.7445 | 62.6739 | 123.1613 | 61.8178 | 123.0925 | 61.5224 | 61.6083 | 123.2224 | 61.554 | 122.9822 | 61.553 | 61.6072 | 61.4842 | 61.5385
3487.0938 | 123.2391 | -61.5646 | 61.6058 | 1.1886 | 1.2324 | 1.1143 | 1.1059 | 0.87403 | 1.1386 | 1.1917 | 61.6012 | 0.25321 | 61.5324 | -0.03768 | 0.039079 | 61.6623 | -0.006014 | 61.4268 | 62.7533 | 62.797 | 62.679 | 62.6705 | 62.4387 | 62.7032 | 62.7563 | 123.1658 | 61.8178 | 123.0971 | 61.527 | 61.6037 | 123.2269 | 61.5586 | 122.9914 | 61.5621 | 61.6072 | 61.4934 | 61.5385
3488.0625 | 123.3994 | -61.5509 | 61.5555 | 0.73078 | 1.2415 | 2.4101 | 1.1242 | 0.80078 | 0.68993 | 0.75678 | 61.5966 | 0.25321 | 61.5187 | -0.033101 | 0.039079 | 61.6531 | 0.007721 | 61.4268 | 62.2817 | 62.7925 | 63.961 | 62.6751 | 62.3517 | 62.2408 | 62.3077 | 123.1475 | 61.8041 | 123.0696 | 61.5178 | 61.59 | 123.204 | 61.5586 | 122.9777 | 61.5575 | 61.5889 | 61.4796 | 61.511
3489.0938 | 123.4543 | -61.5417 | 61.4914 | 0.7674 | 1.2141 | 2.4101 | 1.115 | 0.79621 | 0.73571 | 0.7934 | 61.5966 | 0.25321 | 61.5096 | -0.03768 | 0.039079 | 61.6623 | 0.007721 | 61.4222 | 62.3092 | 62.7558 | 63.9518 | 62.6568 | 62.338 | 62.2775 | 62.3351 | 123.1384 | 61.795 | 123.0513 | 61.5041 | 61.5808 | 123.204 | 61.5495 | 122.9639 | 61.5575 | 61.5889 | 61.4705 | 61.5018
3490.0625 | 123.3902 | -61.5601 | 61.5555 | 1.2619 | 1.2187 | 1.2013 | 1.1242 | 0.87403 | 1.2164 | 1.2741 | 61.592 | 0.25321 | 61.5096 | -0.03768 | 0.039079 | 61.6577 | 0.003143 | 61.4359 | 62.8219 | 62.7787 | 62.7614 | 62.6842 | 62.4341 | 62.7765 | 62.8342 | 123.1521 | 61.8133 | 123.0696 | 61.5224 | 61.5991 | 123.2178 | 61.5632 | 122.996 | 61.553 | 61.5889 | 61.4705 | 61.5064
3491.0625 | 123.3627 | -61.5646 | 61.5646 | 1.4175 | 1.3194 | 1.3524 | 1.257 | 0.91981 | 1.3767 | 1.4389 | 61.5875 | 0.25779 | 61.4958 | -0.03768 | 0.043657 | 61.676 | -0.001436 | 61.4359 | 62.9822 | 62.884 | 62.9171 | 62.8216 | 62.4844 | 62.9413 | 63.0036 | 123.1521 | 61.8224 | 123.0605 | 61.527 | 61.6083 | 123.2407 | 61.5632 | 123.0005 | 61.5438 | 61.5889 | 61.4522 | 61.4973
3492.1094 | 123.4085 | -61.5372 | 61.5417 | 1.3168 | 1.3057 | 1.2471 | 1.1791 | 0.8603 | 1.2714 | 1.3428 | 61.592 | 0.25321 | 61.5279 | -0.042259 | 0.043657 | 61.6623 | 0.003143 | 61.4313 | 62.854 | 62.8428 | 62.7843 | 62.7163 | 62.3975 | 62.8086 | 62.88 | 123.1292 | 61.7904 | 123.065 | 61.4949 | 61.5808 | 123.1995 | 61.5403 | 122.9685 | 61.5484 | 61.5889 | 61.4842 | 61.5247
3493.0625 | 123.3994 | -61.5555 | 61.5784 | 1.3305 | 1.3331 | 1.2654 | 1.202 | 0.86487 | 1.2943 | 1.3565 | 61.592 | 0.25321 | 61.5233 | -0.042259 | 0.043657 | 61.6715 | 0.003143 | 61.4451 | 62.886 | 62.8886 | 62.8209 | 62.7575 | 62.4204 | 62.8498 | 62.912 | 123.1475 | 61.8087 | 123.0788 | 61.5132 | 61.5991 | 123.2269 | 61.5586 | 123.0006 | 61.5484 | 61.5889 | 61.4796 | 61.5202
3494.0781 | 123.3994 | -61.5738 | 61.5234 | 1.3855 | 1.3423 | 1.3158 | 1.2478 | 0.90608 | 1.3492 | 1.4023 | 61.592 | 0.25321 | 61.5233 | -0.033101 | 0.039079 | 61.6715 | -0.001436 | 61.4405 | 62.9593 | 62.9161 | 62.8896 | 62.8216 | 62.4799 | 62.923 | 62.9761 | 123.1658 | 61.827 | 123.0971 | 61.5407 | 61.6129 | 123.2452 | 61.5724 | 123.0143 | 61.553 | 61.5935 | 61.4842 | 61.5247
3495.0625 | 123.3261 | -61.5463 | 61.5555 | 1.3214 | 1.3469 | 1.2517 | 1.17 | 0.92439 | 1.2714 | 1.3382 | 61.5966 | 0.25779 | 61.5233 | -0.03768 | 0.043657 | 61.6669 | 0.012299 | 61.4451 | 62.8677 | 62.8932 | 62.798 | 62.7163 | 62.4707 | 62.8177 | 62.8845 | 123.1429 | 61.8041 | 123.0696 | 61.5086 | 61.59 | 123.2132 | 61.5586 | 122.9914 | 61.553 | 61.5843 | 61.4796 | 61.511
3496.0625 | 123.3765 | -61.5646 | 61.5509 | 1.2985 | 1.3331 | 1.2334 | 1.1471 | 0.91523 | 1.2576 | 1.329 | 61.5875 | 0.25321 | 61.5141 | -0.03768 | 0.039079 | 61.6669 | -0.001436 | 61.4268 | 62.8631 | 62.8978 | 62.798 | 62.7117 | 62.4799 | 62.8223 | 62.8937 | 123.1521 | 61.8178 | 123.0788 | 61.527 | 61.6037 | 123.2315 | 61.5632 | 122.9914 | 61.5484 | 61.5889 | 61.4751 | 61.5156
3497.1094 | 123.3307 | -61.5555 | 61.5738 | 1.2985 | 1.2736 | 1.2288 | 1.1196 | 0.91523 | 1.2576 | 1.3153 | 61.6012 | 0.24863 | 61.505 | -0.03768 | 0.043657 | 61.6623 | -0.006014 | 61.4405 | 62.854 | 62.8291 | 62.7843 | 62.6751 | 62.4707 | 62.8131 | 62.8708 | 123.1567 | 61.8041 | 123.0605 | 61.5178 | 61.5991 | 123.2178 | 61.5495 | 122.996 | 61.5575 | 61.6072 | 61.4613 | 61.511
3498.0625 | 123.3902 | -61.5509 | 61.5601 | 1.2802 | 1.2415 | 1.2013 | 1.1104 | 0.9015 | 1.2256 | 1.297 | 61.592 | 0.25321 | 61.5187 | -0.03768 | 0.039079 | 61.6623 | 0.003143 | 61.4268 | 62.8311 | 62.7925 | 62.7522 | 62.6614 | 62.4524 | 62.7765 | 62.8479 | 123.1429 | 61.8041 | 123.0696 | 61.5132 | 61.59 | 123.2132 | 61.554 | 122.9777 | 61.553 | 61.5889 | 61.4796 | 61.5156
3499.0781 | 123.2849 | -61.5601 | 61.6013 | 1.3214 | 1.3377 | 1.2471 | 1.1562 | 0.94728 | 1.2851 | 1.3382 | 61.6058 | 0.25779 | 61.5233 | -0.028522 | 0.043657 | 61.6623 | -0.001436 | 61.4405 | 62.8814 | 62.8978 | 62.8072 | 62.7163 | 62.5073 | 62.8452 | 62.8983 | 123.1658 | 61.8178 | 123.0834 | 61.5315 | 61.6037 | 123.2224 | 61.5586 | 123.0006 | 61.5621 | 61.6072 | 61.4796 | 61.5247
3500.0625 | 123.3353 | -61.5372 | 61.5784 | 1.326 | 1.3514 | 1.2563 | 1.1745 | 0.94728 | 1.276 | 1.3474 | 61.592 | 0.25779 | 61.5233 | -0.03768 | 0.039079 | 61.6623 | 0.003143 | 61.4451 | 62.8631 | 62.8886 | 62.7934 | 62.7117 | 62.4844 | 62.8131 | 62.8845 | 123.1292 | 61.795 | 123.0605 | 61.4995 | 61.5762 | 123.1995 | 61.5403 | 122.9822 | 61.553 | 61.5889 | 61.4842 | 61.5202
3501.0938 | 123.3765 | -61.5509 | 61.528 | 1.3672 | 1.356 | 1.2929 | 1.2249 | 0.96101 | 1.3217 | 1.3886 | 61.5875 | 0.25779 | 61.5004 | -0.03768 | 0.039079 | 61.676 | -0.001436 | 61.4405 | 62.9181 | 62.9069 | 62.8438 | 62.7758 | 62.5119 | 62.8727 | 62.9395 | 123.1384 | 61.8087 | 123.0513 | 61.5132 | 61.59 | 123.2269 | 61.5495 | 122.9914 | 61.5484 | 61.5889 | 61.4613 | 61.5018
3502.0625 | 123.3948 | -61.5326 | 61.5692 | 1.4679 | 1.3148 | 1.3936 | 1.2112 | 0.91523 | 1.0608 | 1.4847 | 61.5875 | 0.25779 | 61.5187 | -0.03768 | 0.048236 | 61.6623 | 0.003143 | 61.4451 | 63.0005 | 62.8474 | 62.9262 | 62.7438 | 62.4478 | 62.5934 | 63.0173 | 123.1201 | 61.7904 | 123.0513 | 61.4949 | 61.5808 | 123.1949 | 61.5357 | 122.9777 | 61.5392 | 61.5843 | 61.4705 | 61.5156
3503.0781 | 123.3261 | -61.5875 | 61.5646 | 1.4267 | 1.3423 | 1.357 | 1.2753 | 0.95186 | 1.3767 | 1.4389 | 61.592 | 0.25779 | 61.5233 | -0.042259 | 0.039079 | 61.6715 | -0.006014 | 61.4542 | 63.0142 | 62.9298 | 62.9445 | 62.8628 | 62.5394 | 62.9642 | 63.0264 | 123.1796 | 61.8453 | 123.1108 | 61.5453 | 61.6266 | 123.259 | 61.5815 | 123.0418 | 61.553 | 61.5981 | 61.4842 | 61.5293
3504.0625 | 123.381 | -61.5646 | 61.5463 | 1.5274 | 1.3423 | 1.4577 | 1.2066 | 0.92439 | 1.0608 | 1.5396 | 61.592 | 0.25321 | 61.5233 | -0.033101 | 0.034501 | 61.6623 | 0.007721 | 61.4588 | 63.0921 | 62.9069 | 63.0224 | 62.7712 | 62.489 | 62.6254 | 63.1043 | 123.1567 | 61.8178 | 123.0879 | 61.5315 | 61.5991 | 123.2269 | 61.5724 | 123.0234 | 61.5575 | 61.5843 | 61.4888 | 61.5156
3505.0781 | 123.2758 | -61.5692 | 61.5692 | 1.5457 | 1.3789 | 1.4806 | 1.2249 | 0.92439 | 1.0516 | 1.558 | 61.5875 | 0.25321 | 61.4912 | -0.03768 | 0.039079 | 61.6715 | -0.001436 | 61.4634 | 63.1149 | 62.9481 | 63.0498 | 62.7941 | 62.4936 | 62.6208 | 63.1272 | 123.1567 | 61.8224 | 123.0605 | 61.5315 | 61.6083 | 123.2407 | 61.5678 | 123.0326 | 61.5484 | 61.5889 | 61.4522 | 61.4927
3506.0625 | 123.3856 | -61.5326 | 61.5463 | 1.4954 | 1.3423 | 1.4257 | 1.2249 | 0.91981 | 1.0379 | 1.5213 | 61.5875 | 0.25321 | 61.5096 | -0.033101 | 0.039079 | 61.6715 | 0.003143 | 61.4542 | 63.028 | 62.8749 | 62.9583 | 62.7575 | 62.4524 | 62.5705 | 63.0539 | 123.1201 | 61.7858 | 123.0422 | 61.4995 | 61.5717 | 123.204 | 61.5357 | 122.9868 | 61.5484 | 61.5843 | 61.4705 | 61.5064
3507.1094 | 123.3124 | -61.5921 | 61.5829 | 1.4862 | 1.3331 | 1.4119 | 1.1745 | 0.88319 | 1.015 | 1.503 | 61.6012 | 0.25779 | 61.5233 | -0.03768 | 0.039079 | 61.6577 | 0.003143 | 61.4496 | 63.0783 | 62.9252 | 63.004 | 62.7667 | 62.4753 | 62.6071 | 63.0951 | 123.1933 | 61.8499 | 123.1154 | 61.5544 | 61.6312 | 123.2498 | 61.5952 | 123.0417 | 61.5621 | 61.5981 | 61.4842 | 61.5202
3508.0625 | 123.3673 | -61.5646 | 61.5097 | 1.4908 | 1.3148 | 1.4211 | 1.1333 | 0.87403 | 0.98752 | 1.5076 | 61.5966 | 0.24863 | 61.5233 | -0.03768 | 0.039079 | 61.6623 | 0.003143 | 61.4542 | 63.0554 | 62.8794 | 62.9857 | 62.698 | 62.4387 | 62.5522 | 63.0722 | 123.1613 | 61.8133 | 123.0879 | 61.527 | 61.6037 | 123.2269 | 61.5678 | 123.0189 | 61.5575 | 61.5935 | 61.4842 | 61.5202
3509.0781 | 123.2803 | -61.5738 | 61.5829 | 1.4633 | 1.3102 | 1.4394 | 1.115 | 0.84198 | 0.96463 | 1.4801 | 61.592 | 0.25779 | 61.5324 | -0.03768 | 0.043657 | 61.6669 | 0.007721 | 61.4496 | 63.0371 | 62.884 | 63.0132 | 62.6888 | 62.4158 | 62.5384 | 63.0539 | 123.1658 | 61.8316 | 123.1062 | 61.5361 | 61.6174 | 123.2407 | 61.5815 | 123.0234 | 61.5484 | 61.5843 | 61.4888 | 61.5247
3510.0625 | 123.381 | -61.5326 | 61.528 | 1.4908 | 1.2828 | 1.4257 | 1.083 | 0.82367 | 0.90054 | 1.5168 | 61.5875 | 0.24863 | 61.505 | -0.03768 | 0.039079 | 61.6623 | -0.001436 | 61.4405 | 63.0234 | 62.8153 | 62.9583 | 62.6156 | 62.3563 | 62.4331 | 63.0493 | 123.1201 | 61.7812 | 123.0376 | 61.4949 | 61.5717 | 123.1949 | 61.5312 | 122.9731 | 61.5484 | 61.5889 | 61.4659 | 61.5064
3511.0781 | 123.3307 | -61.5738 | 61.5555 | 1.4496 | 1.2873 | 1.3845 | 1.1517 | 0.89234 | 0.93258 | 1.4755 | 61.592 | 0.25321 | 61.4958 | -0.03768 | 0.039079 | 61.6715 | 0.003143 | 61.4451 | 63.0234 | 62.8611 | 62.9583 | 62.7254 | 62.4661 | 62.5064 | 63.0493 | 123.1658 | 61.827 | 123.0696 | 61.5361 | 61.6129 | 123.2452 | 61.5769 | 123.0189 | 61.553 | 61.5889 | 61.4567 | 61.4927
3512.0625 | 123.3948 | -61.5143 | 61.5784 | 1.4267 | 1.2736 | 1.3524 | 1.1242 | 0.89692 | 0.91427 | 1.4481 | 61.5829 | 0.25321 | 61.5141 | -0.03768 | 0.039079 | 61.6669 | -0.001436 | 61.4451 | 62.941 | 62.7879 | 62.8667 | 62.6385 | 62.4112 | 62.4286 | 62.9624 | 123.0972 | 61.7675 | 123.0284 | 61.4766 | 61.5534 | 123.1812 | 61.5128 | 122.9594 | 61.5438 | 61.5843 | 61.4751 | 61.5156
3513.0781 | 123.3032 | -61.5692 | 61.5875 | 1.3214 | 1.2049 | 1.2517 | 1.0967 | 0.83741 | 0.90511 | 1.3428 | 61.6012 | 0.25321 | 61.5279 | -0.028522 | 0.034501 | 61.6623 | -0.001436 | 61.4405 | 62.8906 | 62.7741 | 62.8209 | 62.6659 | 62.4066 | 62.4743 | 62.912 | 123.1704 | 61.8224 | 123.0971 | 61.5407 | 61.6037 | 123.2315 | 61.5678 | 123.0097 | 61.5667 | 61.6026 | 61.4934 | 61.5293
3514.0625 | 123.4085 | -61.528 | 61.5875 | 0.68957 | 1.2828 | 2.5383 | 1.1791 | 0.85572 | 0.84102 | 0.70642 | 61.592 | 0.24405 | 61.5324 | -0.03768 | 0.043657 | 61.6531 | -0.001436 | 61.4451 | 62.2176 | 62.8108 | 64.0663 | 62.7071 | 62.3837 | 62.369 | 62.2344 | 123.1201 | 61.7721 | 123.0605 | 61.4903 | 61.5717 | 123.1812 | 61.5266 | 122.9731 | 61.5484 | 61.5935 | 61.4888 | 61.5339
3515.0625 | 123.4222 | -61.5509 | 61.5417 | 0.65752 | 1.2782 | 2.5932 | 1.1379 | 0.84198 | 0.81355 | 0.68353 | 61.6058 | 0.26237 | 61.537 | -0.033101 | 0.043657 | 61.6669 | -0.001436 | 61.4405 | 62.2084 | 62.8291 | 64.1441 | 62.6888 | 62.3929 | 62.3644 | 62.2344 | 123.1567 | 61.8133 | 123.0879 | 61.5178 | 61.5946 | 123.2178 | 61.5495 | 122.9914 | 61.5621 | 61.6072 | 61.4934 | 61.5385
3516.0781 | 123.3353 | -61.5509 | 61.5326 | 0.65294 | 1.1774 | 2.6253 | 1.1837 | 0.80536 | 0.80897 | 0.66063 | 61.5966 | 0.25779 | 61.5416 | -0.03768 | 0.039079 | 61.6669 | -0.006014 | 61.4313 | 62.2038 | 62.7283 | 64.1762 | 62.7346 | 62.3563 | 62.3599 | 62.2115 | 123.1475 | 61.8087 | 123.0925 | 61.5132 | 61.59 | 123.2178 | 61.5449 | 122.9822 | 61.5575 | 61.6026 | 61.5025 | 61.5476
3517.0625 | 123.2986 | -61.5463 | 61.6425 | 0.63463 | 1.1683 | 2.6344 | 1.1791 | 0.80078 | 0.79065 | 0.66063 | 61.6058 | 0.25321 | 61.5324 | -0.042259 | 0.039079 | 61.6623 | 0.003143 | 61.4451 | 62.181 | 62.7146 | 64.1808 | 62.7255 | 62.3471 | 62.337 | 62.207 | 123.1521 | 61.7995 | 123.0788 | 61.5041 | 61.5854 | 123.2086 | 61.5495 | 122.9914 | 61.5667 | 61.6026 | 61.4934 | 61.5293
3518.0781 | 123.2346 | -61.5601 | 61.6196 | 0.62547 | 1.1912 | 2.6711 | 1.1791 | 0.78247 | 0.73114 | 0.6469 | 61.592 | 0.25321 | 61.5279 | -0.033101 | 0.034501 | 61.6577 | 0.003143 | 61.4405 | 62.1855 | 62.7512 | 64.2311 | 62.7392 | 62.3425 | 62.2912 | 62.207 | 123.1521 | 61.8133 | 123.0879 | 61.527 | 61.5946 | 123.2178 | 61.5632 | 123.0006 | 61.5575 | 61.5889 | 61.4934 | 61.5247
3519.0625 | 123.4039 | -61.5372 | 61.5555 | 0.66668 | 1.2919 | 2.7306 | 1.202 | 0.76874 | 0.70824 | 0.68353 | 61.592 | 0.25779 | 61.4958 | -0.03768 | 0.039079 | 61.6623 | 0.003143 | 61.4313 | 62.2038 | 62.8291 | 64.2678 | 62.7392 | 62.3059 | 62.2454 | 62.2207 | 123.1292 | 61.795 | 123.033 | 61.4995 | 61.5762 | 123.1995 | 61.5403 | 122.9685 | 61.553 | 61.5889 | 61.4567 | 61.4927
3520.0938 | 123.3078 | -61.5829 | 61.5784 | 0.68499 | 1.3469 | 2.8038 | 1.2112 | 0.76874 | 0.68535 | 0.69726 | 61.5966 | 0.25779 | 61.5141 | -0.042259 | 0.039079 | 61.6577 | -0.001436 | 61.4405 | 62.2679 | 62.9298 | 64.3868 | 62.7941 | 62.3517 | 62.2683 | 62.2802 | 123.1796 | 61.8407 | 123.0971 | 61.5407 | 61.622 | 123.2407 | 61.5815 | 123.0234 | 61.5575 | 61.5981 | 61.4751 | 61.5156
3521.0625 | 123.3948 | -61.5417 | 61.5601 | 0.6621 | 1.3194 | 2.9275 | 1.2341 | 0.78247 | 0.63041 | 0.68353 | 61.5966 | 0.25779 | 61.5233 | -0.03768 | 0.043657 | 61.6577 | 0.003143 | 61.4313 | 62.2038 | 62.8611 | 64.4692 | 62.7758 | 62.3242 | 62.1722 | 62.2253 | 123.1384 | 61.7995 | 123.065 | 61.5041 | 61.5854 | 123.1995 | 61.5449 | 122.9731 | 61.553 | 61.5935 | 61.4796 | 61.5202
3522.1094 | 123.2941 | -61.5463 | 61.5784 | 0.65294 | 1.269 | 2.9778 | 1.2615 | 0.78705 | 0.64415 | 0.66521 | 61.6104 | 0.25779 | 61.5279 | -0.028522 | 0.039079 | 61.6577 | 0.003143 | 61.4405 | 62.1993 | 62.8153 | 64.5242 | 62.8079 | 62.3334 | 62.1905 | 62.2115 | 123.1567 | 61.8041 | 123.0742 | 61.5178 | 61.5854 | 123.204 | 61.5495 | 122.9868 | 61.5713 | 61.6072 | 61.4888 | 61.5247
3523.0625 | 123.3673 | -61.5189 | 61.5326 | 0.64837 | 1.2965 | 2.9275 | 1.2615 | 0.81452 | 0.60752 | 0.66521 | 61.6012 | 0.25321 | 61.5324 | -0.042259 | 0.043657 | 61.6623 | -0.006014 | 61.4313 | 62.1672 | 62.8154 | 64.4463 | 62.7804 | 62.3334 | 62.1264 | 62.1841 | 123.1201 | 61.7721 | 123.0513 | 61.4766 | 61.5625 | 123.1812 | 61.5128 | 122.9502 | 61.5575 | 61.6072 | 61.4888 | 61.5385
3524.0781 | 123.2574 | -61.5738 | 61.5829 | 0.60258 | 1.2828 | 2.932 | 1.2615 | 0.78247 | 0.54342 | 0.62859 | 61.6012 | 0.25779 | 61.537 | -0.033101 | 0.043657 | 61.6715 | 0.007721 | 61.4268 | 62.1764 | 62.8565 | 64.5058 | 62.8353 | 62.3563 | 62.1172 | 62.2024 | 123.175 | 61.8316 | 123.1108 | 61.5407 | 61.6174 | 123.2452 | 61.5815 | 123.0005 | 61.5575 | 61.5935 | 61.4934 | 61.5293
3525.0625 | 123.436 | -61.528 | 61.5692 | 0.60258 | 1.3057 | 2.9046 | 1.257 | 0.76416 | 0.60294 | 0.62859 | 61.592 | 0.25779 | 61.5096 | -0.03768 | 0.034501 | 61.6623 | -0.001436 | 61.4313 | 62.1306 | 62.8337 | 64.4326 | 62.785 | 62.2922 | 62.131 | 62.1566 | 123.1201 | 61.7858 | 123.0376 | 61.4903 | 61.5625 | 123.1903 | 61.5266 | 122.9594 | 61.5575 | 61.5935 | 61.4751 | 61.511
3526.0781 | 123.2758 | -61.5692 | 61.6058 | 0.65294 | 1.4064 | 2.7672 | 1.2707 | 0.76874 | 0.63041 | 0.66979 | 61.5966 | 0.25321 | 61.5233 | -0.03768 | 0.039079 | 61.6623 | -0.001436 | 61.4405 | 62.2222 | 62.9756 | 64.3364 | 62.8399 | 62.338 | 62.1996 | 62.239 | 123.1658 | 61.8224 | 123.0925 | 61.5315 | 61.6083 | 123.2315 | 61.5678 | 123.0097 | 61.5575 | 61.5981 | 61.4842 | 61.5247
3527.0625 | 123.3078 | -61.5555 | 61.5601 | 0.73535 | 1.4888 | 2.7306 | 1.3485 | 0.84198 | 0.75403 | 0.74762 | 61.592 | 0.24863 | 61.5279 | -0.03768 | 0.039079 | 61.6623 | -0.001436 | 61.4451 | 62.2908 | 63.0443 | 64.2861 | 62.904 | 62.3975 | 62.3095 | 62.3031 | 123.1475 | 61.8041 | 123.0834 | 61.5178 | 61.5946 | 123.2178 | 61.554 | 123.0006 | 61.553 | 61.5935 | 61.4888 | 61.5293
3528.0938 | 123.2666 | -61.5875 | 61.5555 | 0.7262 | 1.4064 | 2.8542 | 1.3852 | 0.90608 | 0.76776 | 0.74304 | 61.5966 | 0.25321 | 61.5279 | -0.03768 | 0.034501 | 61.6623 | -0.006014 | 61.4496 | 62.3137 | 62.9939 | 64.4417 | 62.9727 | 62.4936 | 62.3553 | 62.3306 | 123.1841 | 61.8407 | 123.1154 | 61.5498 | 61.622 | 123.2498 | 61.5815 | 123.0372 | 61.5621 | 61.6026 | 61.4934 | 61.5339
3529.0625 | 123.3627 | -61.5555 | 61.5326 | 0.69415 | 1.3606 | 2.7764 | 1.3531 | 0.88777 | 0.77234 | 0.72473 | 61.5875 | 0.25779 | 61.5141 | -0.03768 | 0.034501 | 61.6623 | -0.001436 | 61.4405 | 62.2496 | 62.9161 | 64.3319 | 62.9086 | 62.4432 | 62.3278 | 62.2802 | 123.1429 | 61.8133 | 123.0696 | 61.5178 | 61.59 | 123.2178 | 61.554 | 122.996 | 61.553 | 61.5889 | 61.4796 | 61.5156
3530.0781 | 123.3353 | -61.5738 | 61.5784 | 0.67584 | 1.4659 | 2.845 | 1.3531 | 0.82825 | 0.69451 | 0.69268 | 61.5966 | 0.24863 | 61.5096 | -0.028522 | 0.039079 | 61.6623 | -0.001436 | 61.4451 | 62.2496 | 63.0397 | 64.4188 | 62.9269 | 62.402 | 62.2683 | 62.2665 | 123.1704 | 61.8224 | 123.0833 | 61.5453 | 61.6129 | 123.2361 | 61.5724 | 123.0189 | 61.5575 | 61.5981 | 61.4705 | 61.511
3531.0625 | 123.3994 | -61.5417 | 61.5417 | 0.66668 | 1.4247 | 2.8863 | 1.3897 | 0.87861 | 0.7174 | 0.6881 | 61.5829 | 0.25779 | 61.5324 | -0.033101 | 0.039079 | 61.6623 | -0.006014 | 61.4359 | 62.2084 | 62.9664 | 64.428 | 62.9315 | 62.4204 | 62.2591 | 62.2299 | 123.1246 | 61.7995 | 123.0742 | 61.5086 | 61.5808 | 123.204 | 61.5357 | 122.9777 | 61.5438 | 61.5889 | 61.4934 | 61.5385
3532.0938 | 123.2574 | -61.5509 | 61.6241 | 0.64837 | 1.3194 | 2.8679 | 1.4172 | 0.93354 | 0.74029 | 0.67437 | 61.5966 | 0.25779 | 61.5279 | -0.03768 | 0.043657 | 61.6623 | 0.003143 | 61.4451 | 62.1993 | 62.8703 | 64.4188 | 62.9681 | 62.4844 | 62.2912 | 62.2253 | 123.1475 | 61.8087 | 123.0788 | 61.5132 | 61.5946 | 123.2132 | 61.554 | 122.996 | 61.553 | 61.5935 | 61.4842 | 61.5247
3533.0625 | 123.3994 | -61.5234 | 61.5234 | 0.65752 | 1.4201 | 2.8588 | 1.4355 | 0.89234 | 0.74487 | 0.66521 | 61.592 | 0.25321 | 61.5141 | -0.042259 | 0.048236 | 61.6623 | 0.007721 | 61.4451 | 62.181 | 62.9436 | 64.3822 | 62.959 | 62.4158 | 62.2683 | 62.1886 | 123.1155 | 61.7766 | 123.0376 | 61.4812 | 61.5717 | 123.1857 | 61.5312 | 122.9685 | 61.5438 | 61.5843 | 61.4659 | 61.5064
3534.0781 | 123.3124 | -61.528 | 61.5967 | 0.68499 | 1.4384 | 2.8405 | 1.4218 | 0.85572 | 0.73571 | 0.70184 | 61.592 | 0.24863 | 61.505 | -0.033101 | 0.043657 | 61.6669 | 0.007721 | 61.4359 | 62.213 | 62.9665 | 64.3685 | 62.9498 | 62.3837 | 62.2637 | 62.2299 | 123.1201 | 61.7766 | 123.033 | 61.4949 | 61.5717 | 123.1949 | 61.5357 | 122.9639 | 61.5484 | 61.5843 | 61.4613 | 61.4973
3535.0625 | 123.4085 | -61.5372 | 61.5646 | 0.73078 | 1.5025 | 2.9046 | 1.4218 | 0.86487 | 0.75861 | 0.7522 | 61.5966 | 0.25779 | 61.5233 | -0.03768 | 0.029923 | 61.6669 | 0.003143 | 61.4359 | 62.2679 | 63.0397 | 64.4417 | 62.959 | 62.402 | 62.2958 | 62.2894 | 123.1338 | 61.795 | 123.0605 | 61.4995 | 61.5671 | 123.204 | 61.5403 | 122.9731 | 61.5667 | 61.5935 | 61.4934 | 61.5202
3536.0938 | 123.3765 | -61.5738 | 61.5601 | 0.79487 | 1.5025 | 2.8725 | 1.4722 | 0.89234 | 0.79523 | 0.80714 | 61.5966 | 0.25321 | 61.5324 | -0.033101 | 0.043657 | 61.6715 | 0.003143 | 61.4496 | 62.3687 | 63.0763 | 64.4463 | 63.0459 | 62.4661 | 62.369 | 62.3809 | 123.1704 | 61.827 | 123.1062 | 61.5407 | 61.6174 | 123.2452 | 61.5769 | 123.0234 | 61.553 | 61.5935 | 61.4888 | 61.5293
3537.0625 | 123.381 | -61.5417 | 61.5692 | 0.74451 | 1.4568 | 2.8359 | 1.4447 | 0.86487 | 0.76318 | 0.77051 | 61.5966 | 0.24863 | 61.5233 | -0.046838 | 0.039079 | 61.6806 | 0.003143 | 61.4496 | 62.2863 | 62.9985 | 64.3776 | 62.9864 | 62.4066 | 62.3049 | 62.3123 | 123.1384 | 61.7904 | 123.065 | 61.4949 | 61.5808 | 123.2224 | 61.5449 | 122.9914 | 61.5575 | 61.5935 | 61.4842 | 61.5202
3538.0625 | 123.4268 | -61.5646 | 61.5234 | 0.75367 | 1.5209 | 2.9091 | 1.4813 | 0.90608 | 0.84559 | 0.76593 | 61.5829 | 0.25321 | 61.5187 | -0.046838 | 0.039079 | 61.6806 | -0.001436 | 61.4451 | 62.3183 | 63.0855 | 64.4738 | 63.0459 | 62.4707 | 62.4102 | 62.3306 | 123.1475 | 61.8178 | 123.0834 | 61.5178 | 61.6037 | 123.2452 | 61.5632 | 123.0097 | 61.5438 | 61.5843 | 61.4796 | 61.5202
3539.0781 | 123.2574 | -61.5692 | 61.5829 | 0.70331 | 1.5025 | 2.8359 | 1.4126 | 0.87403 | 0.83186 | 0.72015 | 61.5875 | 0.25321 | 61.5096 | -0.033101 | 0.029923 | 61.6623 | -0.001436 | 61.4496 | 62.2725 | 63.0718 | 64.4051 | 62.9818 | 62.4432 | 62.4011 | 62.2894 | 123.1567 | 61.8224 | 123.0788 | 61.5361 | 61.5991 | 123.2315 | 61.5678 | 123.0189 | 61.5575 | 61.5889 | 61.4796 | 61.511
3540.0625 | 123.3856 | -61.5509 | 61.5326 | 0.72162 | 1.4613 | 2.8954 | 1.4264 | 0.84656 | 0.83186 | 0.72931 | 61.5875 | 0.25321 | 61.5004 | -0.033101 | 0.043657 | 61.6669 | -0.001436 | 61.4451 | 62.2725 | 63.0122 | 64.4463 | 62.9773 | 62.3975 | 62.3828 | 62.2802 | 123.1384 | 61.8041 | 123.0513 | 61.5178 | 61.5946 | 123.2178 | 61.5495 | 122.996 | 61.5438 | 61.5889 | 61.4567 | 61.5018
3541.0781 | 123.2437 | -61.5784 | 61.6058 | 0.69873 | 1.3652 | 2.6482 | 1.376 | 0.78705 | 0.78608 | 0.72015 | 61.5966 | 0.25779 | 61.5233 | -0.033101 | 0.043657 | 61.6623 | 0.003143 | 61.4451 | 62.2771 | 62.9435 | 64.2265 | 62.9544 | 62.3654 | 62.3644 | 62.2985 | 123.175 | 61.8362 | 123.1017 | 61.5453 | 61.622 | 123.2407 | 61.5815 | 123.0234 | 61.553 | 61.5935 | 61.4796 | 61.5202
3542.0625 | 123.3582 | -61.5509 | 61.5417 | 0.67584 | 1.3972 | 2.465 | 1.344 | 0.77332 | 0.74487 | 0.73846 | 61.6058 | 0.25321 | 61.5324 | -0.033101 | 0.034501 | 61.6531 | 0.003143 | 61.4451 | 62.2267 | 62.9481 | 64.0159 | 62.8949 | 62.3242 | 62.2958 | 62.2894 | 123.1567 | 61.8041 | 123.0834 | 61.5178 | 61.5854 | 123.204 | 61.554 | 122.996 | 61.5713 | 61.6026 | 61.4979 | 61.5293
3543.0781 | 123.2895 | -61.5646 | 61.6104 | 0.63005 | 1.4018 | 2.5474 | 1.2936 | 0.76874 | 0.64415 | 0.66063 | 61.6012 | 0.25321 | 61.5279 | -0.028522 | 0.039079 | 61.6623 | 0.003143 | 61.4496 | 62.1947 | 62.9664 | 64.1121 | 62.8582 | 62.3334 | 62.2088 | 62.2253 | 123.1658 | 61.8178 | 123.0925 | 61.5361 | 61.6037 | 123.2269 | 61.5678 | 123.0143 | 61.5621 | 61.5981 | 61.4888 | 61.5247
3544.0625 | 123.317 | -61.5784 | 61.5646 | 0.61174 | 1.4476 | 2.6848 | 1.3531 | 0.79621 | 0.62583 | 0.6881 | 61.592 | 0.25779 | 61.505 | -0.03768 | 0.043657 | 61.6623 | -0.001436 | 61.4542 | 62.1901 | 63.026 | 64.2632 | 62.9315 | 62.3746 | 62.2042 | 62.2665 | 123.1704 | 61.8362 | 123.0833 | 61.5407 | 61.622 | 123.2407 | 61.5769 | 123.0326 | 61.5484 | 61.5935 | 61.4613 | 61.5064
3545.0781 | 123.2895 | -61.5417 | 61.6013 | 0.63005 | 1.4201 | 2.5886 | 1.3256 | 0.75958 | 0.59836 | 0.65148 | 61.6104 | 0.25321 | 61.5187 | -0.033101 | 0.039079 | 61.6577 | 0.003143 | 61.4451 | 62.1718 | 62.9619 | 64.1304 | 62.8674 | 62.3013 | 62.1401 | 62.1932 | 123.1521 | 61.795 | 123.0605 | 61.5086 | 61.5808 | 123.1995 | 61.5449 | 122.9868 | 61.5713 | 61.6072 | 61.4796 | 61.5156
3546.0625 | 123.2941 | -61.5875 | 61.6058 | 0.62547 | 1.3606 | 2.4742 | 1.2753 | 0.75043 | 0.57547 | 0.63316 | 61.5966 | 0.25779 | 61.5233 | -0.033101 | 0.039079 | 61.6577 | -0.006014 | 61.4359 | 62.213 | 62.9481 | 64.0617 | 62.8628 | 62.3379 | 62.163 | 62.2207 | 123.1841 | 61.8453 | 123.1108 | 61.5544 | 61.6266 | 123.2452 | 61.5815 | 123.0234 | 61.5575 | 61.6026 | 61.4842 | 61.5293
3547.0938 | 123.2941 | -61.5601 | 61.615 | 0.62089 | 1.3835 | 2.3368 | 1.2844 | 0.72296 | 0.57089 | 0.63316 | 61.6058 | 0.25321 | 61.5279 | -0.03768 | 0.048236 | 61.6531 | -0.001436 | 61.4405 | 62.181 | 62.9436 | 63.8969 | 62.8445 | 62.283 | 62.131 | 62.1932 | 123.1658 | 61.8133 | 123.0879 | 61.5224 | 61.6083 | 123.2132 | 61.5586 | 123.0006 | 61.5575 | 61.6072 | 61.4796 | 61.5293
3548.0625 | 123.317 | -61.5692 | 61.5738 | 0.59342 | 1.3835 | 2.4238 | 1.2524 | 0.7138 | 0.55258 | 0.61027 | 61.6058 | 0.25779 | 61.5416 | -0.042259 | 0.043657 | 61.6531 | -0.001436 | 61.4359 | 62.1626 | 62.9527 | 63.993 | 62.8216 | 62.283 | 62.1218 | 62.1795 | 123.175 | 61.827 | 123.1108 | 61.527 | 61.6129 | 123.2224 | 61.5678 | 123.0051 | 61.5621 | 61.6072 | 61.4979 | 61.543
3549.0938 | 123.2437 | -61.5784 | 61.5875 | 0.54306 | 1.3011 | 2.4284 | 1.202 | 0.70007 | 0.51595 | 0.56449 | 61.592 | 0.25321 | 61.5324 | -0.03768 | 0.043657 | 61.6577 | -0.001436 | 61.4405 | 62.1214 | 62.8794 | 64.0068 | 62.7804 | 62.2784 | 62.0943 | 62.1429 | 123.1704 | 61.8316 | 123.1108 | 61.5407 | 61.622 | 123.2361 | 61.5769 | 123.0189 | 61.5484 | 61.5935 | 61.4888 | 61.5339
3550.0625 | 123.2849 | -61.5967 | 61.5967 | 0.55222 | 1.3835 | 2.5337 | 1.2112 | 0.68176 | 0.52511 | 0.56907 | 61.6012 | 0.25779 | 61.5141 | -0.033101 | 0.039079 | 61.6577 | 0.007721 | 61.4268 | 62.1489 | 62.9802 | 64.1304 | 62.8079 | 62.2784 | 62.1218 | 62.1658 | 123.1979 | 61.8545 | 123.1108 | 61.5636 | 61.6358 | 123.2544 | 61.6044 | 123.0234 | 61.5621 | 61.5935 | 61.4751 | 61.5064
3551.0781 | 123.2803 | -61.5509 | 61.5921 | 0.57969 | 1.4613 | 2.6253 | 1.2432 | 0.70007 | 0.54342 | 0.61027 | 61.5966 | 0.25321 | 61.5279 | -0.033101 | 0.043657 | 61.6623 | -0.001436 | 61.4359 | 62.1306 | 63.0122 | 64.1762 | 62.7941 | 62.251 | 62.0943 | 62.1612 | 123.1475 | 61.8041 | 123.0788 | 61.5178 | 61.5946 | 123.2132 | 61.5495 | 122.9868 | 61.553 | 61.5981 | 61.4842 | 61.5293
3552.0625 | 123.3994 | -61.5555 | 61.5646 | 0.60716 | 1.5071 | 2.726 | 1.1974 | 0.66802 | 0.46101 | 0.62859 | 61.6104 | 0.25321 | 61.5416 | -0.03768 | 0.034501 | 61.6577 | 0.003143 | 61.4313 | 62.1626 | 63.0626 | 64.2815 | 62.7529 | 62.2235 | 62.0165 | 62.1841 | 123.1658 | 61.8087 | 123.0971 | 61.5178 | 61.59 | 123.2132 | 61.5586 | 122.9868 | 61.5759 | 61.6072 | 61.5071 | 61.5385
3553.0625 | 123.3261 | -61.5463 | 61.6058 | 0.64379 | 1.585 | 2.7901 | 1.2203 | 0.65429 | 0.50679 | 0.67895 | 61.6104 | 0.25779 | 61.5416 | -0.028522 | 0.043657 | 61.6577 | -0.006014 | 61.4405 | 62.1901 | 63.1313 | 64.3364 | 62.7667 | 62.2006 | 62.0531 | 62.2253 | 123.1567 | 61.8041 | 123.0879 | 61.5178 | 61.59 | 123.204 | 61.5403 | 122.9868 | 61.5667 | 61.6164 | 61.4979 | 61.5476
3554.0938 | 123.2895 | -61.5509 | 61.6104 | 0.63463 | 1.5254 | 2.726 | 1.2203 | 0.64971 | 0.55716 | 0.64232 | 61.6058 | 0.25321 | 61.5324 | -0.03768 | 0.039079 | 61.6669 | 0.003143 | 61.4405 | 62.1855 | 63.0763 | 64.2769 | 62.7712 | 62.2006 | 62.1081 | 62.1932 | 123.1567 | 61.8041 | 123.0834 | 61.5132 | 61.59 | 123.2178 | 61.554 | 122.9914 | 61.5667 | 61.6026 | 61.4934 | 61.5293
3555.0625 | 123.3307 | -61.5692 | 61.5829 | 0.65294 | 1.5346 | 2.7123 | 1.2478 | 0.63598 | 0.52969 | 0.66521 | 61.6012 | 0.25779 | 61.5324 | -0.03768 | 0.034501 | 61.6577 | -0.001436 | 61.4359 | 62.2222 | 63.1038 | 64.2815 | 62.817 | 62.2052 | 62.0989 | 62.2344 | 123.1704 | 61.827 | 123.1017 | 61.5315 | 61.6037 | 123.2269 | 61.5678 | 123.0051 | 61.5667 | 61.6026 | 61.4979 | 61.5339
3556.0938 | 123.3032 | -61.5372 | 61.6013 | 0.65752 | 1.4613 | 2.8496 | 1.2478 | 0.62682 | 0.56631 | 0.62859 | 61.6012 | 0.25779 | 61.5233 | -0.033101 | 0.043657 | 61.6623 | -0.006014 | 61.4542 | 62.1947 | 62.9985 | 64.3868 | 62.785 | 62.164 | 62.1035 | 62.1658 | 123.1384 | 61.795 | 123.0605 | 61.5041 | 61.5808 | 123.1995 | 61.5312 | 122.9914 | 61.5575 | 61.6072 | 61.4796 | 61.5293
3557.0625 | 123.2758 | -61.5875 | 61.5829 | 0.68041 | 1.5392 | 2.9687 | 1.3119 | 0.65429 | 0.58921 | 0.62859 | 61.5966 | 0.25321 | 61.505 | -0.03768 | 0.043657 | 61.6623 | 0.003143 | 61.4496 | 62.2679 | 63.1267 | 64.5562 | 62.8994 | 62.2418 | 62.1767 | 62.2161 | 123.1841 | 61.8407 | 123.0925 | 61.5498 | 61.6312 | 123.2498 | 61.5907 | 123.0372 | 61.553 | 61.5935 | 61.4613 | 61.5018
3558.0938 | 123.2666 | -61.5372 | 61.5646 | 0.65294 | 1.5712 | 3.0053 | 1.344 | 0.66802 | 0.55258 | 0.66521 | 61.5966 | 0.25779 | 61.5141 | -0.033101 | 0.043657 | 61.6623 | 0.007721 | 61.4588 | 62.1901 | 63.1084 | 64.5425 | 62.8811 | 62.2052 | 62.0897 | 62.2024 | 123.1338 | 61.795 | 123.0513 | 61.5041 | 61.5808 | 123.1995 | 61.5449 | 122.996 | 61.553 | 61.5889 | 61.4705 | 61.5064
3559.0625 | 123.3948 | -61.5234 | 61.5692 | 0.65294 | 1.5437 | 3.0419 | 1.3577 | 0.6726 | 0.68077 | 0.67437 | 61.5966 | 0.25779 | 61.5233 | -0.028522 | 0.039079 | 61.6623 | 0.012299 | 61.4405 | 62.1764 | 63.0672 | 64.5654 | 62.8811 | 62.196 | 62.2042 | 62.1978 | 123.1201 | 61.7812 | 123.0467 | 61.4949 | 61.5625 | 123.1857 | 61.5357 | 122.9639 | 61.5575 | 61.5843 | 61.4842 | 61.511
3560.0938 | 123.3124 | -61.5509 | 61.6104 | 0.65752 | 1.5437 | 3.161 | 1.3806 | 0.68176 | 0.7174 | 0.67895 | 61.592 | 0.25321 | 61.5279 | -0.03768 | 0.039079 | 61.6623 | -0.001436 | 61.4405 | 62.2084 | 63.0947 | 64.7119 | 62.9315 | 62.2327 | 62.2683 | 62.2298 | 123.1429 | 61.8041 | 123.0788 | 61.5132 | 61.59 | 123.2132 | 61.5495 | 122.9914 | 61.553 | 61.5935 | 61.4888 | 61.5293
3561.0625 | 123.317 | -61.5829 | 61.5738 | 0.68041 | 1.53 | 3.2205 | 1.4035 | 0.68176 | 0.64415 | 0.70642 | 61.6058 | 0.25779 | 61.5233 | -0.03768 | 0.043657 | 61.6715 | -0.001436 | 61.4451 | 62.2634 | 63.113 | 64.8034 | 62.9864 | 62.2647 | 62.2271 | 62.2894 | 123.1887 | 61.8407 | 123.1062 | 61.5453 | 61.6266 | 123.2544 | 61.5815 | 123.028 | 61.5621 | 61.6072 | 61.4796 | 61.5247
3562.0938 | 123.3307 | -61.5555 | 61.5829 | 0.68957 | 1.5804 | 3.2159 | 1.4218 | 0.69091 | 0.58921 | 0.70184 | 61.5966 | 0.24863 | 61.5279 | -0.03768 | 0.048236 | 61.6623 | 0.007721 | 61.4496 | 62.2451 | 63.1359 | 64.7714 | 62.9773 | 62.2464 | 62.1447 | 62.2573 | 123.1521 | 61.8041 | 123.0834 | 61.5178 | 61.6037 | 123.2178 | 61.5632 | 123.0051 | 61.5484 | 61.5889 | 61.4796 | 61.5202
3563.0625 | 123.2437 | -61.5921 | 61.5921 | 0.66668 | 1.4842 | 3.1839 | 1.4355 | 0.68634 | 0.63499 | 0.6881 | 61.6012 | 0.24863 | 61.5233 | -0.03768 | 0.039079 | 61.6715 | 0.003143 | 61.4451 | 62.2588 | 63.0763 | 64.776 | 63.0276 | 62.2784 | 62.2271 | 62.2802 | 123.1933 | 61.8407 | 123.1154 | 61.5544 | 61.6312 | 123.2636 | 61.5952 | 123.0372 | 61.5621 | 61.5981 | 61.4842 | 61.5202
3564.0781 | 123.2803 | -61.5463 | 61.5738 | 0.65752 | 1.5804 | 3.1518 | 1.4218 | 0.71838 | 0.61668 | 0.66979 | 61.592 | 0.25321 | 61.505 | -0.028522 | 0.048236 | 61.6623 | 0.003143 | 61.4451 | 62.2038 | 63.1267 | 64.6981 | 62.9681 | 62.2647 | 62.163 | 62.2161 | 123.1384 | 61.7995 | 123.0513 | 61.5178 | 61.5946 | 123.2086 | 61.5495 | 122.9914 | 61.5438 | 61.5889 | 61.4567 | 61.5018
3565.0625 | 123.2437 | -61.5738 | 61.5738 | 0.63005 | 1.5712 | 3.0419 | 1.4172 | 0.69091 | 0.60752 | 0.6469 | 61.592 | 0.26237 | 61.4958 | -0.03768 | 0.043657 | 61.6669 | 0.012299 | 61.4405 | 62.2038 | 63.145 | 64.6157 | 62.991 | 62.2647 | 62.1813 | 62.2207 | 123.1658 | 61.8362 | 123.0696 | 61.5361 | 61.6174 | 123.2407 | 61.5861 | 123.0143 | 61.5484 | 61.5797 | 61.4522 | 61.4835
3566.0781 | 123.2986 | -61.5601 | 61.5646 | 0.62089 | 1.5575 | 2.9824 | 1.4126 | 0.65429 | 0.57089 | 0.64232 | 61.592 | 0.25321 | 61.5141 | -0.033101 | 0.039079 | 61.6669 | 0.003143 | 61.4405 | 62.181 | 63.1175 | 64.5425 | 62.9727 | 62.2143 | 62.131 | 62.2024 | 123.1521 | 61.8133 | 123.0742 | 61.527 | 61.5991 | 123.2269 | 61.5632 | 123.0006 | 61.553 | 61.5889 | 61.4751 | 61.511
3567.0625 | 123.3994 | -61.5463 | 61.5784 | 0.61174 | 1.5117 | 3.1152 | 1.3531 | 0.62682 | 0.50222 | 0.62401 | 61.5875 | 0.25321 | 61.5233 | -0.03768 | 0.043657 | 61.6669 | 0.003143 | 61.4359 | 62.1581 | 63.058 | 64.6615 | 62.8994 | 62.1731 | 62.0485 | 62.1703 | 123.1338 | 61.7995 | 123.0696 | 61.5086 | 61.59 | 123.2132 | 61.5495 | 122.9822 | 61.5438 | 61.5843 | 61.4796 | 61.5202
3568.0781 | 123.3307 | -61.5646 | 61.6058 | 0.58427 | 1.4888 | 2.8817 | 1.289 | 0.57189 | 0.45643 | 0.61485 | 61.6058 | 0.25321 | 61.537 | -0.033101 | 0.043657 | 61.6623 | -0.001436 | 61.4313 | 62.1489 | 63.0534 | 64.4463 | 62.8536 | 62.1365 | 62.0211 | 62.1795 | 123.1704 | 61.8178 | 123.1017 | 61.5315 | 61.6083 | 123.2269 | 61.5632 | 122.996 | 61.5621 | 61.6072 | 61.4934 | 61.5385
3569.0625 | 123.262 | -61.6333 | 61.5463 | 0.57511 | 1.5712 | 2.8634 | 1.2753 | 0.58562 | 0.48848 | 0.59196 | 61.6104 | 0.25779 | 61.537 | -0.03768 | 0.048236 | 61.6577 | 0.003143 | 61.4268 | 62.2084 | 63.2045 | 64.4967 | 62.9086 | 62.2189 | 62.1218 | 62.2253 | 123.2437 | 61.8911 | 123.1703 | 61.5956 | 61.6815 | 123.291 | 61.6364 | 123.0601 | 61.5621 | 61.6072 | 61.4888 | 61.5339
3570.0781 | 123.2849 | -61.5417 | 61.615 | 0.50186 | 1.5346 | 2.8267 | 1.17 | 0.53984 | 0.4427 | 0.52787 | 61.6149 | 0.26237 | 61.5416 | -0.03768 | 0.043657 | 61.6531 | -0.001436 | 61.4268 | 62.0436 | 63.0763 | 64.3685 | 62.7117 | 62.0816 | 61.9844 | 62.0696 | 123.1567 | 61.8041 | 123.0834 | 61.5041 | 61.5854 | 123.1949 | 61.5403 | 122.9685 | 61.5713 | 61.6164 | 61.4979 | 61.543
3571.0625 | 123.2483 | -61.5738 | 61.6196 | 0.60258 | 1.4796 | 2.7764 | 1.2112 | 0.55357 | 0.45185 | 0.41799 | 61.6058 | 0.25779 | 61.5462 | -0.033101 | 0.052814 | 61.6577 | 0.003143 | 61.4268 | 62.1764 | 63.0534 | 64.3502 | 62.785 | 62.1274 | 62.0256 | 61.9918 | 123.1796 | 61.8316 | 123.12 | 61.5407 | 61.6266 | 123.2315 | 61.5769 | 123.0005 | 61.553 | 61.6026 | 61.4934 | 61.543
3572.0938 | 123.3948 | -61.5189 | 61.615 | 0.59342 | 1.4613 | 2.8771 | 1.1883 | 0.53526 | 0.41523 | 0.41341 | 61.6012 | 0.25321 | 61.537 | -0.033101 | 0.043657 | 61.6577 | -0.001436 | 61.4451 | 62.1123 | 62.9802 | 64.396 | 62.7071 | 62.0541 | 61.9341 | 61.9323 | 123.1201 | 61.7721 | 123.0559 | 61.4858 | 61.5625 | 123.1766 | 61.5174 | 122.9639 | 61.5575 | 61.6026 | 61.4934 | 61.5385
3573.0625 | 123.2712 | -61.5784 | 61.5875 | 0.54306 | 1.5025 | 2.813 | 1.1562 | 0.50779 | 0.39233 | 0.51413 | 61.6012 | 0.25779 | 61.5187 | -0.033101 | 0.034501 | 61.6531 | -0.001436 | 61.4405 | 62.1214 | 63.0809 | 64.3914 | 62.7346 | 62.0862 | 61.9707 | 62.0925 | 123.1796 | 61.8362 | 123.0971 | 61.5453 | 61.6129 | 123.2315 | 61.5769 | 123.0189 | 61.5667 | 61.6026 | 61.4842 | 61.5202
3574.0781 | 123.2803 | -61.5326 | 61.5921 | 0.52475 | 1.5483 | 2.9091 | 1.1883 | 0.52611 | 0.38318 | 0.55534 | 61.6012 | 0.25779 | 61.505 | -0.03768 | 0.048236 | 61.6577 | 0.007721 | 61.4405 | 62.0573 | 63.0809 | 64.4417 | 62.7209 | 62.0587 | 61.9158 | 62.0879 | 123.1338 | 61.7904 | 123.0376 | 61.4949 | 61.5808 | 123.1903 | 61.5403 | 122.9731 | 61.553 | 61.5935 | 61.4567 | 61.4973
3575.0625 | 123.3765 | -61.5784 | 61.5417 | 0.4927 | 1.5529 | 3.0145 | 1.1654 | 0.47117 | 0.35113 | 0.51413 | 61.5966 | 0.25779 | 61.5233 | -0.03768 | 0.034501 | 61.6577 | -0.001436 | 61.4313 | 62.0711 | 63.1313 | 64.5928 | 62.7438 | 62.0495 | 61.9295 | 62.0925 | 123.175 | 61.8362 | 123.1017 | 61.5407 | 61.6129 | 123.2361 | 61.5769 | 123.0097 | 61.5621 | 61.5981 | 61.4888 | 61.5247
3576.0938 | 123.2346 | -61.5646 | 61.5921 | 0.45607 | 1.5392 | 2.9137 | 1.1333 | 0.42997 | 0.32366 | 0.47751 | 61.6012 | 0.24863 | 61.5416 | -0.033101 | 0.043657 | 61.6577 | 0.003143 | 61.4313 | 62.0207 | 63.1038 | 64.4784 | 62.698 | 61.9946 | 61.8883 | 62.0421 | 123.1658 | 61.8133 | 123.1062 | 61.5315 | 61.6083 | 123.2224 | 61.5678 | 122.996 | 61.5575 | 61.5981 | 61.4979 | 61.5385
3577.0625 | 123.4406 | -61.5463 | 61.5509 | 0.47896 | 1.5758 | 2.8588 | 1.17 | 0.45744 | 0.34655 | 0.50955 | 61.6058 | 0.25779 | 61.5416 | -0.03768 | 0.043657 | 61.6623 | 0.003143 | 61.4359 | 62.0253 | 63.1221 | 64.4051 | 62.7163 | 62.0038 | 61.8929 | 62.0559 | 123.1521 | 61.8041 | 123.0879 | 61.5086 | 61.59 | 123.2086 | 61.5495 | 122.9822 | 61.5621 | 61.6026 | 61.4979 | 61.5385
3578.0781 | 123.4039 | -61.5509 | 61.5784 | 0.48812 | 1.5758 | 2.8908 | 1.1562 | 0.42081 | 0.30535 | 0.51871 | 61.6195 | 0.26237 | 61.537 | -0.028522 | 0.043657 | 61.6623 | 0.003143 | 61.4405 | 62.039 | 63.1267 | 64.4417 | 62.7071 | 61.9717 | 61.8562 | 62.0696 | 123.1704 | 61.8133 | 123.0879 | 61.5224 | 61.5946 | 123.2132 | 61.554 | 122.9914 | 61.5759 | 61.6164 | 61.4934 | 61.5339
3579.0625 | 123.3948 | -61.528 | 61.5784 | 0.50186 | 1.5987 | 3.0328 | 1.17 | 0.42539 | 0.30992 | 0.52329 | 61.6104 | 0.25321 | 61.5324 | -0.033101 | 0.039079 | 61.6623 | 0.012299 | 61.4451 | 62.0299 | 63.1267 | 64.5608 | 62.698 | 61.9534 | 61.8379 | 62.0513 | 123.1384 | 61.7812 | 123.0605 | 61.4949 | 61.5671 | 123.1903 | 61.5403 | 122.9731 | 61.5713 | 61.5981 | 61.4934 | 61.5202
3580.0938 | 123.2666 | -61.5555 | 61.5875 | 0.53848 | 1.6628 | 3.019 | 1.2203 | 0.4849 | 0.33739 | 0.54618 | 61.6012 | 0.25779 | 61.5462 | -0.03768 | 0.039079 | 61.6577 | 0.003143 | 61.4496 | 62.094 | 63.2183 | 64.5745 | 62.7758 | 62.0404 | 61.8929 | 62.1017 | 123.1567 | 61.8133 | 123.1017 | 61.5178 | 61.5946 | 123.2132 | 61.5586 | 123.0051 | 61.5621 | 61.5981 | 61.5071 | 61.543
3581.0625 | 123.3765 | -61.5417 | 61.5326 | 0.55222 | 1.6536 | 3.0099 | 1.2249 | 0.51237 | 0.3145 | 0.56907 | 61.6058 | 0.26237 | 61.5324 | -0.033101 | 0.043657 | 61.6531 | -0.001436 | 61.4451 | 62.094 | 63.1954 | 64.5516 | 62.7667 | 62.0541 | 61.8562 | 62.1108 | 123.1475 | 61.8041 | 123.0742 | 61.5086 | 61.5854 | 123.1949 | 61.5403 | 122.9868 | 61.5621 | 61.6072 | 61.4888 | 61.5339
3582.1094 | 123.317 | -61.5601 | 61.5967 | 0.56595 | 1.6857 | 3.0282 | 1.2158 | 0.51695 | 0.3145 | 0.56449 | 61.6012 | 0.25779 | 61.5096 | -0.033101 | 0.039079 | 61.6623 | 0.003143 | 61.4496 | 62.126 | 63.2458 | 64.5883 | 62.7758 | 62.077 | 61.8746 | 62.1246 | 123.1613 | 61.8178 | 123.0696 | 61.527 | 61.5991 | 123.2224 | 61.5632 | 123.0097 | 61.5621 | 61.5981 | 61.4705 | 61.5064
3583.0625 | 123.4451 | -61.5646 | 61.5326 | 0.58885 | 1.6445 | 3.1152 | 1.2203 | 0.51695 | 0.33282 | 0.57365 | 61.592 | 0.25779 | 61.505 | -0.028522 | 0.034501 | 61.6623 | 0.003143 | 61.4451 | 62.1535 | 63.2091 | 64.6798 | 62.785 | 62.0816 | 61.8975 | 62.1383 | 123.1567 | 61.8224 | 123.0696 | 61.5361 | 61.5991 | 123.2269 | 61.5678 | 123.0097 | 61.5575 | 61.5889 | 61.4705 | 61.5018
3584.0781 | 123.3215 | -61.5601 | 61.5692 | 0.61632 | 1.704 | 3.2205 | 1.2753 | 0.53526 | 0.39233 | 0.63774 | 61.6012 | 0.24863 | 61.5233 | -0.033101 | 0.043657 | 61.6669 | 0.003143 | 61.4542 | 62.1764 | 63.2641 | 64.7806 | 62.8353 | 62.0953 | 61.9524 | 62.1978 | 123.1613 | 61.8087 | 123.0834 | 61.527 | 61.6037 | 123.2269 | 61.5632 | 123.0143 | 61.5575 | 61.5981 | 61.4796 | 61.5202
3585.0625 | 123.3948 | -61.5784 | 61.5646 | 0.63005 | 1.672 | 3.2342 | 1.2615 | 0.53068 | 0.33739 | 0.64232 | 61.6012 | 0.26237 | 61.5233 | -0.028522 | 0.043657 | 61.6715 | 0.007721 | 61.4451 | 62.2084 | 63.2503 | 64.8126 | 62.8399 | 62.1091 | 61.9158 | 62.2207 | 123.1796 | 61.8407 | 123.1017 | 61.5498 | 61.622 | 123.2498 | 61.5861 | 123.0234 | 61.5575 | 61.5935 | 61.4796 | 61.5156
3586.0781 | 123.2803 | -61.5601 | 61.6013 | 0.6621 | 1.6765 | 3.1747 | 1.2799 | 0.52611 | 0.33739 | 0.68353 | 61.5966 | 0.25779 | 61.5279 | -0.03768 | 0.039079 | 61.6669 | -0.001436 | 61.4451 | 62.2222 | 63.2366 | 64.7348 | 62.8399 | 62.0862 | 61.8975 | 62.2436 | 123.1567 | 61.8178 | 123.0879 | 61.5224 | 61.5991 | 123.2269 | 61.5586 | 123.0051 | 61.5575 | 61.5981 | 61.4888 | 61.5293
3587.0625 | 123.436 | -61.5555 | 61.5738 | 0.68499 | 1.6903 | 3.0786 | 1.2844 | 0.6314 | 0.36486 | 0.64232 | 61.6012 | 0.25321 | 61.5324 | -0.033101 | 0.039079 | 61.6669 | -0.001436 | 61.4451 | 62.2405 | 63.2458 | 64.634 | 62.8399 | 62.1869 | 61.9203 | 62.1978 | 123.1567 | 61.8087 | 123.0879 | 61.5224 | 61.5946 | 123.2224 | 61.554 | 123.0006 | 61.5621 | 61.6026 | 61.4934 | 61.5339
3588.0781 | 123.2986 | -61.5555 | 61.5875 | 0.70788 | 1.6536 | 3.1152 | 1.344 | 0.67718 | 0.45643 | 0.69726 | 61.6012 | 0.25779 | 61.5279 | -0.028522 | 0.043657 | 61.6669 | 0.003143 | 61.4359 | 62.2634 | 63.2091 | 64.6707 | 62.8994 | 62.2327 | 62.0119 | 62.2527 | 123.1567 | 61.8133 | 123.0834 | 61.527 | 61.5991 | 123.2224 | 61.5586 | 122.9914 | 61.5575 | 61.5981 | 61.4842 | 61.5247
3589.0625 | 123.3765 | -61.5601 | 61.5189 | 0.68957 | 1.6445 | 3.0099 | 1.3348 | 0.70007 | 0.45643 | 0.67895 | 61.5966 | 0.25321 | 61.5324 | -0.042259 | 0.034501 | 61.6623 | 0.007721 | 61.4359 | 62.2496 | 63.2045 | 64.5699 | 62.8949 | 62.2601 | 62.0165 | 62.239 | 123.1567 | 61.8133 | 123.0925 | 61.5178 | 61.5946 | 123.2224 | 61.5678 | 122.996 | 61.5621 | 61.5889 | 61.4979 | 61.5247
3590.0938 | 123.317 | -61.5692 | 61.5829 | 0.69873 | 1.6903 | 2.607 | 1.289 | 0.67718 | 0.42896 | 0.6469 | 61.592 | 0.25779 | 61.5233 | -0.033101 | 0.039079 | 61.6577 | -0.001436 | 61.4313 | 62.2679 | 63.2595 | 64.1762 | 62.8582 | 62.2464 | 61.9982 | 62.2161 | 123.1613 | 61.827 | 123.0925 | 61.5361 | 61.6083 | 123.2269 | 61.5678 | 123.0005 | 61.553 | 61.5935 | 61.4842 | 61.5247
3591.0625 | 123.4177 | -61.5601 | 61.5555 | 0.67126 | 1.6903 | 2.7123 | 1.289 | 0.68176 | 0.43812 | 0.6881 | 61.592 | 0.25779 | 61.505 | -0.033101 | 0.034501 | 61.6623 | -0.006014 | 61.4268 | 62.2313 | 63.2503 | 64.2723 | 62.8491 | 62.2418 | 61.9982 | 62.2482 | 123.1521 | 61.8178 | 123.065 | 61.527 | 61.5946 | 123.2224 | 61.554 | 122.9868 | 61.5575 | 61.5981 | 61.4705 | 61.511
3592.1094 | 123.3719 | -61.5555 | 61.5509 | 0.71246 | 1.8597 | 2.8908 | 1.3211 | 0.6726 | 0.47017 | 0.6881 | 61.592 | 0.25779 | 61.4958 | -0.033101 | 0.048236 | 61.6577 | 0.003143 | 61.4405 | 62.2679 | 63.4152 | 64.4463 | 62.8765 | 62.2281 | 62.0256 | 62.2436 | 123.1475 | 61.8133 | 123.0513 | 61.5224 | 61.6037 | 123.2132 | 61.5586 | 122.996 | 61.5438 | 61.5889 | 61.4476 | 61.4927
3593.0625 | 123.3582 | -61.5829 | 61.4822 | 0.69415 | 1.8047 | 2.8634 | 1.3485 | 0.68176 | 0.46101 | 0.71557 | 61.592 | 0.26237 | 61.505 | -0.03768 | 0.043657 | 61.6669 | 0.003143 | 61.4451 | 62.2771 | 63.3877 | 64.4463 | 62.9315 | 62.2647 | 62.044 | 62.2985 | 123.175 | 61.8453 | 123.0879 | 61.5453 | 61.6266 | 123.2498 | 61.5861 | 123.028 | 61.5484 | 61.5889 | 61.4613 | 61.5018
3594.0781 | 123.3948 | -61.5921 | 61.5738 | 0.64379 | 1.7773 | 3.0511 | 1.3211 | 0.66802 | 0.46101 | 0.67437 | 61.5966 | 0.25321 | 61.5233 | -0.033101 | 0.039079 | 61.6669 | 0.003143 | 61.4359 | 62.2359 | 63.3694 | 64.6432 | 62.9132 | 62.2601 | 62.0531 | 62.2665 | 123.1887 | 61.8453 | 123.1154 | 61.559 | 61.6312 | 123.259 | 61.5952 | 123.028 | 61.5575 | 61.5935 | 61.4842 | 61.5202
3595.0625 | 123.3765 | -61.5601 | 61.5372 | 0.64379 | 1.7773 | 2.9366 | 1.3256 | 0.6726 | 0.45185 | 0.66063 | 61.592 | 0.25779 | 61.537 | -0.033101 | 0.039079 | 61.6623 | 0.003143 | 61.4359 | 62.2038 | 63.3373 | 64.4967 | 62.8857 | 62.2327 | 62.0119 | 62.2207 | 123.1521 | 61.8178 | 123.0971 | 61.527 | 61.5991 | 123.2224 | 61.5632 | 122.996 | 61.553 | 61.5889 | 61.4979 | 61.5339
3596.0781 | 123.2941 | -61.6058 | 61.5921 | 0.66668 | 1.7864 | 3.0511 | 1.3668 | 0.66344 | 0.46559 | 0.67895 | 61.6058 | 0.26237 | 61.537 | -0.033101 | 0.043657 | 61.6669 | -0.006014 | 61.4405 | 62.2725 | 63.3923 | 64.6569 | 62.9727 | 62.2693 | 62.0714 | 62.2848 | 123.2116 | 61.8682 | 123.1429 | 61.5727 | 61.6495 | 123.2727 | 61.5998 | 123.0463 | 61.5621 | 61.6118 | 61.4934 | 61.543
3597.0625 | 123.4039 | -61.5601 | 61.5555 | 0.69873 | 1.7086 | 3.0328 | 1.3256 | 0.62682 | 0.42438 | 0.59654 | 61.5966 | 0.25779 | 61.537 | -0.042259 | 0.039079 | 61.6715 | 0.003143 | 61.4451 | 62.2588 | 63.2686 | 64.5928 | 62.8857 | 62.1869 | 61.9844 | 62.1566 | 123.1567 | 61.8178 | 123.0971 | 61.5178 | 61.5991 | 123.2315 | 61.5632 | 123.0051 | 61.5575 | 61.5935 | 61.4979 | 61.5339
3598.0938 | 123.3582 | -61.5601 | 61.5509 | 0.63463 | 1.7361 | 3.0328 | 1.3256 | 0.62224 | 0.40607 | 0.65606 | 61.6012 | 0.26237 | 61.5279 | -0.03768 | 0.043657 | 61.6623 | 0.003143 | 61.4451 | 62.1947 | 63.2961 | 64.5928 | 62.8857 | 62.1823 | 61.9661 | 62.2161 | 123.1613 | 61.8224 | 123.0879 | 61.5224 | 61.6037 | 123.2224 | 61.5632 | 123.0051 | 61.5575 | 61.5981 | 61.4842 | 61.5247
3599.0625 | 123.3902 | -61.5417 | 61.5463 | 0.64379 | 1.7269 | 3.0694 | 1.3531 | 0.60851 | 0.42896 | 0.65606 | 61.592 | 0.25321 | 61.5141 | -0.033101 | 0.043657 | 61.6577 | 0.003143 | 61.4405 | 62.1855 | 63.2687 | 64.6111 | 62.8949 | 62.1503 | 61.9707 | 62.1978 | 123.1338 | 61.795 | 123.0559 | 61.5086 | 61.5854 | 123.1995 | 61.5449 | 122.9822 | 61.5484 | 61.5889 | 61.4705 | 61.511
3600.0938 | 123.3398 | -61.5784 | 61.5463 | 0.71246 | 1.7132 | 3.1884 | 1.4218 | 0.65887 | 0.52053 | 0.72931 | 61.5875 | 0.25779 | 61.5004 | -0.033101 | 0.048236 | 61.6715 | 0.007721 | 61.4451 | 62.2908 | 63.2915 | 64.7668 | 63.0002 | 62.2372 | 62.0989 | 62.3077 | 123.1658 | 61.8362 | 123.0788 | 61.5453 | 61.6266 | 123.2498 | 61.5861 | 123.0234 | 61.5392 | 61.5797 | 61.4522 | 61.4927
3601.0625 | 123.3536 | -61.5326 | 61.5555 | 0.69873 | 1.6949 | 3.1518 | 1.4035 | 0.64513 | 0.51137 | 0.71557 | 61.5875 | 0.25779 | 61.4912 | -0.03768 | 0.039079 | 61.6669 | -0.006014 | 61.4359 | 62.2313 | 63.2274 | 64.6844 | 62.9361 | 62.1777 | 62.044 | 62.2482 | 123.1201 | 61.7904 | 123.0238 | 61.4949 | 61.5717 | 123.1995 | 61.5266 | 122.9685 | 61.5484 | 61.5935 | 61.4522 | 61.4973
3602.0625 | 123.4177 | -61.5143 | 61.5601 | 0.63463 | 1.6994 | 3.0602 | 1.3027 | 0.61767 | 0.4427 | 0.65148 | 61.5966 | 0.25779 | 61.5004 | -0.028522 | 0.039079 | 61.6623 | 0.012299 | 61.4451 | 62.1489 | 63.2137 | 64.5745 | 62.817 | 62.1319 | 61.957 | 62.1658 | 123.1109 | 61.7721 | 123.0147 | 61.4858 | 61.5534 | 123.1766 | 61.5266 | 122.9594 | 61.5575 | 61.5843 | 61.4613 | 61.4881
3603.0938 | 123.4039 | -61.5601 | 61.5601 | 0.66668 | 1.6536 | 3.0831 | 1.3073 | 0.64513 | 0.49306 | 0.69268 | 61.592 | 0.25321 | 61.5233 | -0.03768 | 0.039079 | 61.6623 | 0.003143 | 61.4405 | 62.2267 | 63.2137 | 64.6432 | 62.8674 | 62.2052 | 62.0531 | 62.2527 | 123.1521 | 61.8133 | 123.0834 | 61.5224 | 61.5991 | 123.2224 | 61.5632 | 123.0006 | 61.553 | 61.5889 | 61.4842 | 61.5202
3604.0625 | 123.3765 | -61.5417 | 61.5509 | 0.63463 | 1.617 | 2.9916 | 1.2844 | 0.61309 | 0.47475 | 0.66063 | 61.592 | 0.25779 | 61.537 | -0.042259 | 0.043657 | 61.6623 | -0.001436 | 61.4313 | 62.1764 | 63.1588 | 64.5333 | 62.8262 | 62.1548 | 62.0165 | 62.2024 | 123.1338 | 61.7995 | 123.0788 | 61.4995 | 61.5854 | 123.204 | 61.5403 | 122.9731 | 61.5484 | 61.5935 | 61.4934 | 61.5385
3605.0781 | 123.3719 | -61.5463 | 61.5509 | 0.61174 | 1.6582 | 2.9091 | 1.3302 | 0.61767 | 0.4427 | 0.63316 | 61.6012 | 0.25779 | 61.5324 | -0.033101 | 0.043657 | 61.6577 | 0.003143 | 61.4359 | 62.1581 | 63.2045 | 64.4555 | 62.8765 | 62.164 | 61.989 | 62.1795 | 123.1475 | 61.8041 | 123.0788 | 61.5132 | 61.59 | 123.204 | 61.5495 | 122.9822 | 61.5575 | 61.5981 | 61.4888 | 61.5293
3606.0625 | 123.3902 | -61.5784 | 61.5234 | 0.598 | 1.7177 | 2.8954 | 1.3577 | 0.58104 | 0.45643 | 0.61943 | 61.6104 | 0.25779 | 61.537 | -0.03768 | 0.039079 | 61.6669 | 0.003143 | 61.4359 | 62.1764 | 63.2961 | 64.4738 | 62.9361 | 62.1594 | 62.0348 | 62.1978 | 123.1887 | 61.8362 | 123.1154 | 61.5407 | 61.6174 | 123.2452 | 61.5815 | 123.0143 | 61.5713 | 61.6072 | 61.4979 | 61.5339
3607.1094 | 123.3673 | -61.5372 | 61.5417 | 0.54764 | 1.7223 | 2.5658 | 1.3348 | 0.549 | 0.4427 | 0.55991 | 61.6058 | 0.25779 | 61.537 | -0.033101 | 0.039079 | 61.6577 | -0.001436 | 61.4359 | 62.0848 | 63.2595 | 64.1029 | 62.872 | 62.0862 | 61.9799 | 62.0971 | 123.1429 | 61.795 | 123.0742 | 61.5041 | 61.5762 | 123.1949 | 61.5357 | 122.9731 | 61.5667 | 61.6072 | 61.4979 | 61.5385
3608.0625 | 123.3856 | -61.5509 | 61.5463 | 0.57969 | 1.759 | 2.8313 | 1.3256 | 0.53984 | 0.42438 | 0.61027 | 61.6012 | 0.25779 | 61.5324 | -0.033101 | 0.043657 | 61.6669 | -0.006014 | 61.4451 | 62.1306 | 63.3099 | 64.3822 | 62.8765 | 62.0907 | 61.9753 | 62.1612 | 123.1521 | 61.8087 | 123.0834 | 61.5178 | 61.5946 | 123.2178 | 61.5449 | 122.996 | 61.5575 | 61.6072 | 61.4888 | 61.5385
3609.0938 | 123.3353 | -61.5372 | 61.5692 | 0.60716 | 1.846 | 2.7901 | 1.344 | 0.53526 | 0.40607 | 0.61943 | 61.6012 | 0.26237 | 61.5141 | -0.03768 | 0.039079 | 61.6577 | -0.001436 | 61.4405 | 62.1443 | 63.3831 | 64.3273 | 62.8811 | 62.0724 | 61.9432 | 62.1566 | 123.1384 | 61.7995 | 123.0513 | 61.4995 | 61.5762 | 123.1949 | 61.5357 | 122.9777 | 61.5621 | 61.6026 | 61.4751 | 61.5156
3610.0625 | 123.3582 | -61.5646 | 61.5692 | 0.68499 | 1.9421 | 2.8908 | 1.4493 | 0.55815 | 0.44728 | 0.70642 | 61.592 | 0.25779 | 61.505 | -0.033101 | 0.039079 | 61.6623 | -0.001436 | 61.4405 | 62.2496 | 63.5067 | 64.4555 | 63.0139 | 62.1228 | 62.0119 | 62.2711 | 123.1567 | 61.8224 | 123.0696 | 61.5315 | 61.6037 | 123.2269 | 61.5632 | 123.0051 | 61.553 | 61.5935 | 61.4659 | 61.5064
3611.0938 | 123.3627 | -61.5875 | 61.4822 | 0.67584 | 1.9467 | 2.8359 | 1.4584 | 0.549 | 0.42438 | 0.70184 | 61.5966 | 0.25321 | 61.5004 | -0.03768 | 0.029923 | 61.6715 | 0.007721 | 61.4542 | 62.2634 | 63.5342 | 64.4234 | 63.0459 | 62.1365 | 62.0119 | 62.2894 | 123.1841 | 61.8407 | 123.0879 | 61.5498 | 61.6174 | 123.259 | 61.5952 | 123.0418 | 61.5667 | 61.5889 | 61.4705 | 61.4927
3612.0625 | 123.349 | -61.5601 | 61.6058 | 0.68957 | 1.9421 | 2.8679 | 1.4538 | 0.57189 | 0.4427 | 0.70184 | 61.5966 | 0.25779 | 61.5187 | -0.033101 | 0.048236 | 61.6623 | 0.007721 | 61.4542 | 62.2496 | 63.5022 | 64.428 | 63.0139 | 62.1319 | 62.0028 | 62.2619 | 123.1567 | 61.8178 | 123.0788 | 61.527 | 61.6083 | 123.2224 | 61.5678 | 123.0143 | 61.5484 | 61.5889 | 61.4705 | 61.511
3613.0781 | 123.3902 | -61.5417 | 61.5372 | 0.71704 | 2.0291 | 3.019 | 1.5042 | 0.57646 | 0.47932 | 0.73846 | 61.5875 | 0.25779 | 61.5233 | -0.033101 | 0.039079 | 61.676 | 0.003143 | 61.4313 | 62.2588 | 63.5709 | 64.5608 | 63.0459 | 62.1182 | 62.0211 | 62.2802 | 123.1292 | 61.7995 | 123.065 | 61.5086 | 61.5808 | 123.2178 | 61.5449 | 122.9731 | 61.5484 | 61.5843 | 61.4842 | 61.5202
3614.0625 | 123.3902 | -61.5646 | 61.5601 | 0.71704 | 2.0886 | 2.9549 | 1.4859 | 0.55815 | 0.48848 | 0.73389 | 61.5966 | 0.26237 | 61.5233 | -0.028522 | 0.039079 | 61.6669 | 0.003143 | 61.4359 | 62.2817 | 63.6533 | 64.5196 | 63.0505 | 62.1228 | 62.0531 | 62.2985 | 123.1613 | 61.827 | 123.0879 | 61.5361 | 61.6037 | 123.2315 | 61.5678 | 123.0005 | 61.5575 | 61.5935 | 61.4842 | 61.5202
3615.0781 | 123.349 | -61.5646 | 61.5463 | 0.72162 | 2.0795 | 2.8817 | 1.4722 | 0.55357 | 0.48848 | 0.73846 | 61.592 | 0.26237 | 61.5279 | -0.03768 | 0.039079 | 61.6715 | -0.001436 | 61.4359 | 62.2863 | 63.6441 | 64.4463 | 63.0368 | 62.1182 | 62.0531 | 62.3031 | 123.1567 | 61.827 | 123.0925 | 61.527 | 61.6037 | 123.2361 | 61.5632 | 123.0005 | 61.553 | 61.5935 | 61.4888 | 61.5293
3616.0625 | 123.4039 | -61.5372 | 61.5692 | 0.68957 | 2.0703 | 2.845 | 1.4447 | 0.56731 | 0.40607 | 0.70184 | 61.5966 | 0.25779 | 61.5279 | -0.033101 | 0.034501 | 61.6806 | 0.003143 | 61.4405 | 62.2267 | 63.6075 | 64.3822 | 62.9819 | 62.1045 | 61.9432 | 62.239 | 123.1338 | 61.795 | 123.065 | 61.5041 | 61.5717 | 123.2178 | 61.5403 | 122.9777 | 61.5621 | 61.5935 | 61.4934 | 61.5247
3617.0938 | 123.3032 | -61.5417 | 61.5875 | 0.68499 | 2.1161 | 2.9961 | 1.495 | 0.52153 | 0.41523 | 0.69726 | 61.592 | 0.25779 | 61.5279 | -0.033101 | 0.043657 | 61.6623 | 0.003143 | 61.4496 | 62.2267 | 63.6578 | 64.5379 | 63.0368 | 62.0633 | 61.957 | 62.239 | 123.1338 | 61.7995 | 123.0696 | 61.5086 | 61.5854 | 123.204 | 61.5449 | 122.9914 | 61.5484 | 61.5889 | 61.4842 | 61.5247
3618.0625 | 123.4497 | -61.5326 | 61.5509 | 0.64837 | 2.1069 | 3.0694 | 1.463 | 0.56731 | 0.4198 | 0.68353 | 61.5829 | 0.25321 | 61.505 | -0.046838 | 0.039079 | 61.6669 | 0.003143 | 61.4542 | 62.181 | 63.6395 | 64.602 | 62.9956 | 62.0999 | 61.9524 | 62.2161 | 123.1155 | 61.7858 | 123.0376 | 61.4858 | 61.5717 | 123.1995 | 61.5357 | 122.9868 | 61.5438 | 61.5797 | 61.4659 | 61.5018
3619.0938 | 123.3856 | -61.5189 | 61.5463 | 0.6621 | 2.1665 | 3.1198 | 1.4767 | 0.49406 | 0.40607 | 0.67895 | 61.592 | 0.25321 | 61.5004 | -0.03768 | 0.043657 | 61.6623 | -0.001436 | 61.4405 | 62.181 | 63.6853 | 64.6386 | 62.9956 | 62.0129 | 61.9249 | 62.1978 | 123.1109 | 61.7721 | 123.0193 | 61.4812 | 61.5625 | 123.1812 | 61.5174 | 122.9594 | 61.5484 | 61.5935 | 61.4567 | 61.5018
3620.0625 | 123.349 | -61.5646 | 61.5784 | 0.67584 | 2.1894 | 3.0877 | 1.4905 | 0.49406 | 0.4198 | 0.69268 | 61.592 | 0.25321 | 61.505 | -0.03768 | 0.039079 | 61.6715 | 0.003143 | 61.4496 | 62.2405 | 63.754 | 64.6523 | 63.0551 | 62.0587 | 61.9844 | 62.2573 | 123.1567 | 61.8178 | 123.0696 | 61.527 | 61.6037 | 123.2361 | 61.5678 | 123.0143 | 61.553 | 61.5889 | 61.4659 | 61.5018
3621.0781 | 123.4314 | -61.5372 | 61.5555 | 0.68499 | 2.1848 | 2.9275 | 1.4538 | 0.49864 | 0.41065 | 0.69726 | 61.592 | 0.25321 | 61.5096 | -0.03768 | 0.043657 | 61.6715 | -0.001436 | 61.4496 | 62.2222 | 63.722 | 64.4646 | 62.991 | 62.0358 | 61.9478 | 62.2344 | 123.1292 | 61.7904 | 123.0467 | 61.4995 | 61.5808 | 123.2086 | 61.5357 | 122.9868 | 61.5484 | 61.5935 | 61.4659 | 61.511
3622.0625 | 123.349 | -61.5646 | 61.5921 | 0.71704 | 2.2306 | 3.3579 | 1.4813 | 0.52611 | 0.43354 | 0.73389 | 61.5875 | 0.25779 | 61.5141 | -0.028522 | 0.043657 | 61.6669 | 0.003143 | 61.4542 | 62.2817 | 63.7952 | 64.9225 | 63.0459 | 62.0907 | 61.9982 | 62.2985 | 123.1521 | 61.8224 | 123.0788 | 61.5361 | 61.6083 | 123.2315 | 61.5678 | 123.0189 | 61.5438 | 61.5843 | 61.4705 | 61.511
3623.0938 | 123.3627 | -61.5601 | 61.5463 | 0.77656 | 2.3038 | 3.4632 | 1.4813 | 0.55357 | 0.46559 | 0.7934 | 61.5829 | 0.25779 | 61.4912 | -0.033101 | 0.039079 | 61.676 | -0.001436 | 61.4496 | 62.3366 | 63.8639 | 65.0232 | 63.0414 | 62.1136 | 62.0256 | 62.3535 | 123.1429 | 61.8178 | 123.0513 | 61.527 | 61.5991 | 123.2361 | 61.5586 | 123.0097 | 61.5438 | 61.5843 | 61.4522 | 61.4927
3624.0625 | 123.4314 | -61.5555 | 61.5601 | 0.6621 | 2.2489 | 3.2113 | 1.4309 | 0.53526 | 0.4198 | 0.67895 | 61.5875 | 0.25779 | 61.505 | -0.042259 | 0.039079 | 61.6623 | -0.001436 | 61.4542 | 62.2176 | 63.8044 | 64.7668 | 62.9864 | 62.0907 | 61.9753 | 62.2344 | 123.1429 | 61.8133 | 123.0605 | 61.5132 | 61.5946 | 123.2178 | 61.554 | 123.0097 | 61.5484 | 61.5889 | 61.4659 | 61.5064
3625.0938 | 123.3994 | -61.5234 | 61.5784 | 0.67584 | 2.2809 | 3.4357 | 1.4081 | 0.53068 | 0.45643 | 0.69268 | 61.5875 | 0.25779 | 61.505 | -0.042259 | 0.043657 | 61.676 | -0.001436 | 61.4496 | 62.1993 | 63.8044 | 64.9591 | 62.9315 | 62.0541 | 61.9799 | 62.2161 | 123.1109 | 61.7812 | 123.0284 | 61.4812 | 61.5671 | 123.1995 | 61.522 | 122.9731 | 61.5438 | 61.5889 | 61.4613 | 61.5064
3626.0625 | 123.3627 | -61.5555 | 61.5463 | 0.71704 | 2.345 | 3.4311 | 1.4447 | 0.55815 | 0.45185 | 0.73389 | 61.5875 | 0.25321 | 61.4912 | -0.033101 | 0.048236 | 61.676 | 0.003143 | 61.4542 | 62.2725 | 63.9005 | 64.9866 | 63.0002 | 62.1136 | 62.0073 | 62.2894 | 123.1429 | 61.8087 | 123.0467 | 61.5224 | 61.6037 | 123.2315 | 61.5586 | 123.0097 | 61.5392 | 61.5843 | 61.443 | 61.4881
3627.0938 | 123.3673 | -61.5829 | 61.5509 | 0.68041 | 2.2535 | 3.2663 | 1.4172 | 0.52611 | 0.4198 | 0.70642 | 61.5829 | 0.25779 | 61.5004 | -0.028522 | 0.039079 | 61.6715 | -0.001436 | 61.4405 | 62.2634 | 63.8364 | 64.8492 | 63.0002 | 62.1091 | 62.0028 | 62.2894 | 123.1658 | 61.8407 | 123.0833 | 61.5544 | 61.622 | 123.2544 | 61.5815 | 123.0234 | 61.5438 | 61.5843 | 61.4613 | 61.5018
3628.0625 | 123.4131 | -61.5417 | 61.5784 | 0.68957 | 2.226 | 2.987 | 1.4126 | 0.53068 | 0.43812 | 0.71099 | 61.5966 | 0.25321 | 61.505 | -0.03768 | 0.048236 | 61.6623 | -0.001436 | 61.4451 | 62.2313 | 63.7677 | 64.5287 | 62.9544 | 62.0724 | 61.9799 | 62.2527 | 123.1384 | 61.795 | 123.0467 | 61.5041 | 61.59 | 123.204 | 61.5403 | 122.9868 | 61.5484 | 61.5981 | 61.4567 | 61.5064
3629.0781 | 123.4222 | -61.528 | 61.5005 | 0.67584 | 2.2489 | 2.9229 | 1.3623 | 0.50322 | 0.39691 | 0.70184 | 61.5966 | 0.25321 | 61.505 | -0.042259 | 0.043657 | 61.6669 | -0.001436 | 61.4451 | 62.2039 | 63.7769 | 64.4509 | 62.8903 | 62.0312 | 61.9249 | 62.2299 | 123.1246 | 61.7812 | 123.033 | 61.4858 | 61.5717 | 123.1949 | 61.5266 | 122.9731 | 61.553 | 61.5981 | 61.4613 | 61.5064
3630.0625 | 123.349 | -61.5692 | 61.5601 | 0.73535 | 2.2672 | 2.8496 | 1.3714 | 0.49864 | 0.40149 | 0.66979 | 61.592 | 0.25321 | 61.4958 | -0.042259 | 0.039079 | 61.6715 | 0.003143 | 61.4405 | 62.3046 | 63.8364 | 64.4188 | 62.9406 | 62.0679 | 61.9707 | 62.239 | 123.1613 | 61.8224 | 123.065 | 61.527 | 61.6083 | 123.2407 | 61.5724 | 123.0097 | 61.553 | 61.5889 | 61.4567 | 61.4927
3631.0938 | 123.4451 | -61.5646 | 61.5372 | 0.73535 | 2.2855 | 3.1289 | 1.3852 | 0.48033 | 0.33739 | 0.67437 | 61.5966 | 0.25779 | 61.5004 | -0.03768 | 0.039079 | 61.6715 | -0.001436 | 61.4405 | 62.3 | 63.8502 | 64.6936 | 62.9498 | 62.045 | 61.902 | 62.239 | 123.1613 | 61.8224 | 123.065 | 61.527 | 61.6037 | 123.2361 | 61.5632 | 123.0051 | 61.5575 | 61.5981 | 61.4613 | 61.5018
3632.0625 | 123.3536 | -61.5372 | 61.5875 | 0.75367 | 2.2901 | 3.2754 | 1.4538 | 0.53526 | 0.36486 | 0.68353 | 61.5875 | 0.25321 | 61.5004 | -0.033101 | 0.039079 | 61.6715 | 0.003143 | 61.4542 | 62.2908 | 63.8273 | 64.8126 | 62.991 | 62.0724 | 61.902 | 62.2207 | 123.1246 | 61.7904 | 123.0376 | 61.5041 | 61.5762 | 123.2086 | 61.5403 | 122.9914 | 61.5484 | 61.5843 | 61.4613 | 61.4973
3633.0781 | 123.436 | -61.5601 | 61.5417 | 0.73535 | 2.3267 | 3.1427 | 1.4584 | 0.58104 | 0.39233 | 0.70184 | 61.5829 | 0.24863 | 61.505 | -0.033101 | 0.034501 | 61.6715 | -0.006014 | 61.4451 | 62.2954 | 63.8868 | 64.7027 | 63.0185 | 62.1411 | 61.9524 | 62.2619 | 123.1429 | 61.8087 | 123.065 | 61.527 | 61.5946 | 123.2315 | 61.554 | 123.0051 | 61.5484 | 61.5889 | 61.4705 | 61.511
3634.0625 | 123.3994 | -61.5692 | 61.5509 | 0.71246 | 2.2947 | 3.3945 | 1.3806 | 0.549 | 0.39233 | 0.63316 | 61.592 | 0.25321 | 61.505 | -0.033101 | 0.043657 | 61.6669 | 0.003143 | 61.4496 | 62.2817 | 63.8639 | 64.9637 | 62.9498 | 62.1182 | 61.9615 | 62.2024 | 123.1613 | 61.8224 | 123.0742 | 61.5361 | 61.6129 | 123.2361 | 61.5724 | 123.0189 | 61.5484 | 61.5889 | 61.4613 | 61.5018
3635.0625 | 123.3261 | -61.5417 | 61.5875 | 0.73535 | 2.2672 | 3.3853 | 1.3989 | 0.52153 | 0.46101 | 0.60112 | 61.5875 | 0.25779 | 61.5004 | -0.03768 | 0.043657 | 61.6806 | 0.003143 | 61.4542 | 62.2771 | 63.809 | 64.9271 | 62.9406 | 62.0633 | 62.0028 | 62.1429 | 123.1292 | 61.7995 | 123.0421 | 61.5041 | 61.5854 | 123.2224 | 61.5449 | 122.996 | 61.5438 | 61.5843 | 61.4567 | 61.4973
3636.0781 | 123.3994 | -61.5646 | 61.5234 | 0.81319 | 2.4733 | 3.6097 | 1.6507 | 0.6726 | 0.6121 | 0.84834 | 61.5737 | 0.24863 | 61.4958 | -0.03768 | 0.043657 | 61.6806 | 0.003143 | 61.4588 | 62.3778 | 64.0379 | 65.1743 | 63.2153 | 62.2372 | 62.1767 | 62.413 | 123.1384 | 61.8133 | 123.0605 | 61.527 | 61.6083 | 123.2452 | 61.5678 | 123.0234 | 61.5301 | 61.5706 | 61.4522 | 61.4927
3637.0625 | 123.4314 | -61.5509 | 61.5417 | 0.82234 | 2.5602 | 3.6051 | 1.6782 | 0.67718 | 0.63041 | 0.90785 | 61.5783 | 0.25321 | 61.4912 | -0.03768 | 0.039079 | 61.6806 | 0.007721 | 61.4634 | 62.3732 | 64.1111 | 65.156 | 63.2291 | 62.2281 | 62.1813 | 62.4588 | 123.1292 | 61.8041 | 123.0421 | 61.5132 | 61.59 | 123.2315 | 61.5586 | 123.0143 | 61.5392 | 61.5706 | 61.4522 | 61.4835
3638.0938 | 123.3765 | -61.5646 | 61.5326 | 0.81777 | 2.606 | 3.4448 | 1.6141 | 0.68176 | 0.58921 | 0.90785 | 61.5783 | 0.25779 | 61.5004 | -0.042259 | 0.043657 | 61.6806 | -0.001436 | 61.4451 | 62.3824 | 64.1707 | 65.0095 | 63.1787 | 62.2464 | 62.1538 | 62.4725 | 123.1429 | 61.8224 | 123.065 | 61.5224 | 61.6083 | 123.2452 | 61.5632 | 123.0097 | 61.5346 | 61.5797 | 61.4567 | 61.5018
3639.0625 | 123.3765 | -61.5784 | 61.5555 | 0.73993 | 2.5145 | 3.335 | 1.4172 | 0.57189 | 0.4427 | 0.76593 | 61.5829 | 0.24863 | 61.5004 | -0.03768 | 0.039079 | 61.6806 | 0.003143 | 61.4542 | 62.3183 | 64.0928 | 64.9133 | 62.9956 | 62.1503 | 62.0211 | 62.3443 | 123.1613 | 61.827 | 123.0788 | 61.5407 | 61.6174 | 123.259 | 61.5815 | 123.0326 | 61.5438 | 61.5797 | 61.4613 | 61.4973
3640.0938 | 123.4406 | -61.5372 | 61.528 | 0.86355 | 2.6564 | 3.6143 | 1.6507 | 0.69549 | 0.58921 | 0.9399 | 61.5737 | 0.26695 | 61.4958 | -0.03768 | 0.043657 | 61.6898 | 0.007721 | 61.4588 | 62.4007 | 64.1936 | 65.1514 | 63.1879 | 62.2327 | 62.1264 | 62.4771 | 123.1109 | 61.8041 | 123.033 | 61.4995 | 61.5808 | 123.2269 | 61.5449 | 122.996 | 61.5301 | 61.566 | 61.4522 | 61.4881
3641.0625 | 123.3627 | -61.5784 | 61.5326 | 0.88644 | 2.6518 | 3.6188 | 1.7926 | 0.75958 | 0.68993 | 1.0315 | 61.5737 | 0.25779 | 61.505 | -0.03768 | 0.039079 | 61.6852 | -0.001436 | 61.4725 | 62.4648 | 64.2302 | 65.1972 | 63.371 | 62.338 | 62.2683 | 62.6098 | 123.1521 | 61.8362 | 123.0833 | 61.5407 | 61.6174 | 123.2636 | 61.5769 | 123.0509 | 61.5346 | 61.5752 | 61.4659 | 61.5064
3642.1094 | 123.3032 | -61.5875 | 61.5646 | 0.88644 | 2.6152 | 3.5593 | 1.7606 | 0.73669 | 0.66246 | 0.94448 | 61.5783 | 0.25321 | 61.5096 | -0.033101 | 0.043657 | 61.6898 | 0.003143 | 61.468 | 62.474 | 64.2027 | 65.1468 | 63.3481 | 62.3242 | 62.25 | 62.532 | 123.1658 | 61.8407 | 123.0971 | 61.5544 | 61.6312 | 123.2773 | 61.5907 | 123.0555 | 61.5346 | 61.5752 | 61.4659 | 61.5064
3643.0625 | 123.349 | -61.5921 | 61.5463 | 0.90475 | 2.6976 | 3.7791 | 1.8476 | 0.74585 | 0.67619 | 0.95364 | 61.5737 | 0.26237 | 61.5096 | -0.03768 | 0.043657 | 61.6852 | 0.003143 | 61.4725 | 62.4969 | 64.2897 | 65.3712 | 63.4397 | 62.3379 | 62.2683 | 62.5457 | 123.1658 | 61.8545 | 123.1017 | 61.5544 | 61.6358 | 123.2773 | 61.5952 | 123.0646 | 61.5301 | 61.5706 | 61.4659 | 61.5064
3644.0938 | 123.3261 | -61.5738 | 61.5372 | 0.92765 | 2.6839 | 3.7516 | 1.843 | 0.75043 | 0.64415 | 0.91701 | 61.5737 | 0.26237 | 61.5004 | -0.03768 | 0.034501 | 61.6898 | 0.003143 | 61.4771 | 62.5014 | 64.2577 | 65.3254 | 63.4168 | 62.3242 | 62.2179 | 62.4908 | 123.1475 | 61.8362 | 123.0742 | 61.5361 | 61.6083 | 123.2636 | 61.5769 | 123.0509 | 61.5392 | 61.5706 | 61.4659 | 61.4973
3645.0625 | 123.3627 | -61.5784 | 61.5326 | 0.88186 | 2.6335 | 3.5227 | 1.7743 | 0.71838 | 0.63041 | 0.86207 | 61.5783 | 0.25321 | 61.4958 | -0.028522 | 0.048236 | 61.6852 | 0.003143 | 61.4771 | 62.4602 | 64.2119 | 65.1011 | 63.3527 | 62.2968 | 62.2088 | 62.4404 | 123.1567 | 61.8316 | 123.0742 | 61.5498 | 61.6266 | 123.2636 | 61.5815 | 123.0555 | 61.5301 | 61.5752 | 61.4476 | 61.4927
3646.0781 | 123.3856 | -61.5921 | 61.5143 | 0.87271 | 2.6518 | 3.66 | 1.7606 | 0.70465 | 0.66246 | 0.92617 | 61.5737 | 0.25321 | 61.4821 | -0.042259 | 0.039079 | 61.6898 | -0.001436 | 61.4817 | 62.4648 | 64.2439 | 65.2521 | 63.3527 | 62.2967 | 62.2546 | 62.5183 | 123.1658 | 61.8453 | 123.0742 | 61.5498 | 61.6312 | 123.2819 | 61.5907 | 123.0738 | 61.5346 | 61.5752 | 61.443 | 61.4835
3647.0625 | 123.381 | -61.5646 | 61.5601 | 0.84981 | 2.6152 | 3.8157 | 1.7606 | 0.70465 | 0.63041 | 0.90785 | 61.5691 | 0.26237 | 61.4775 | -0.042259 | 0.039079 | 61.6852 | 0.003143 | 61.4725 | 62.4145 | 64.1798 | 65.3803 | 63.3252 | 62.2693 | 62.195 | 62.4725 | 123.1338 | 61.827 | 123.0421 | 61.5224 | 61.6037 | 123.2498 | 61.5678 | 123.0372 | 61.5301 | 61.566 | 61.4384 | 61.4744
3648.0781 | 123.4131 | -61.5738 | 61.5005 | 0.86813 | 2.6015 | 3.6555 | 1.7469 | 0.68634 | 0.60752 | 0.90328 | 61.5783 | 0.25321 | 61.4958 | -0.033101 | 0.039079 | 61.6806 | 0.003143 | 61.468 | 62.4419 | 64.1752 | 65.2293 | 63.3207 | 62.2601 | 62.1813 | 62.4771 | 123.1521 | 61.827 | 123.0696 | 61.5407 | 61.6129 | 123.2544 | 61.5769 | 123.0418 | 61.5392 | 61.5752 | 61.4567 | 61.4927
3649.0625 | 123.349 | -61.5601 | 61.5143 | 0.8956 | 2.6381 | 3.6784 | 1.7057 | 0.68634 | 0.57547 | 0.88039 | 61.5691 | 0.26237 | 61.5004 | -0.033101 | 0.043657 | 61.6898 | -0.001436 | 61.4771 | 62.4557 | 64.1981 | 65.2384 | 63.2657 | 62.2464 | 62.1355 | 62.4404 | 123.1292 | 61.8224 | 123.0605 | 61.527 | 61.6037 | 123.2498 | 61.5586 | 123.0372 | 61.5255 | 61.5706 | 61.4567 | 61.5018
3650.0781 | 123.317 | -61.6013 | 61.5646 | 0.88186 | 2.6152 | 3.7791 | 1.6736 | 0.68176 | 0.60752 | 0.85292 | 61.5829 | 0.25779 | 61.5141 | -0.033101 | 0.043657 | 61.6898 | -0.001436 | 61.468 | 62.4831 | 64.2164 | 65.3803 | 63.2749 | 62.283 | 62.2088 | 62.4542 | 123.1841 | 61.859 | 123.1154 | 61.5682 | 61.6449 | 123.291 | 61.5998 | 123.0692 | 61.5392 | 61.5843 | 61.4705 | 61.5156
3651.0625 | 123.3261 | -61.5829 | 61.5189 | 0.88186 | 2.6564 | 3.6692 | 1.6965 | 0.68634 | 0.59378 | 0.88497 | 61.5829 | 0.25779 | 61.5141 | -0.033101 | 0.039079 | 61.6898 | -0.001436 | 61.4588 | 62.4648 | 64.2394 | 65.2521 | 63.2794 | 62.2693 | 62.1767 | 62.4679 | 123.1658 | 61.8407 | 123.0971 | 61.5498 | 61.622 | 123.2727 | 61.5815 | 123.0418 | 61.5438 | 61.5843 | 61.4751 | 61.5156
3652.0938 | 123.3398 | -61.5967 | 61.5967 | 0.8956 | 2.6747 | 3.7791 | 1.6828 | 0.65887 | 0.58463 | 0.88954 | 61.5829 | 0.25779 | 61.5096 | -0.033101 | 0.043657 | 61.6806 | 0.003143 | 61.4725 | 62.4923 | 64.2714 | 65.3758 | 63.2794 | 62.2555 | 62.1813 | 62.4862 | 123.1796 | 61.8545 | 123.1062 | 61.5636 | 61.6403 | 123.2773 | 61.5998 | 123.0692 | 61.5392 | 61.5797 | 61.4659 | 61.5064
3653.0625 | 123.3627 | -61.5967 | 61.5234 | 0.94596 | 2.7846 | 3.8661 | 1.724 | 0.70007 | 0.63041 | 0.98111 | 61.5737 | 0.25779 | 61.5004 | -0.03768 | 0.043657 | 61.6898 | -0.001436 | 61.4771 | 62.5426 | 64.3813 | 65.4628 | 63.3206 | 62.2967 | 62.2271 | 62.5778 | 123.1704 | 61.8545 | 123.0971 | 61.559 | 61.6403 | 123.2864 | 61.5952 | 123.0738 | 61.5301 | 61.5752 | 61.4567 | 61.5018
3654.0781 | 123.2666 | -61.6013 | 61.5601 | 0.95512 | 2.867 | 3.8203 | 1.7881 | 0.74127 | 0.67162 | 1.0589 | 61.5737 | 0.26237 | 61.4912 | -0.03768 | 0.039079 | 61.6943 | -0.006014 | 61.4771 | 62.5564 | 64.4683 | 65.4215 | 63.3893 | 62.3425 | 62.2729 | 62.6602 | 123.175 | 61.8636 | 123.0925 | 61.5636 | 61.6403 | 123.2956 | 61.5952 | 123.0784 | 61.5346 | 61.5797 | 61.4522 | 61.4973
3655.0625 | 123.3719 | -61.5601 | 61.5509 | 1.0055 | 2.9723 | 3.7974 | 1.8567 | 0.76416 | 0.64415 | 1.1047 | 61.5691 | 0.25321 | 61.4821 | -0.03768 | 0.043657 | 61.6943 | 0.007721 | 61.4771 | 62.5655 | 64.5324 | 65.3575 | 63.4168 | 62.3242 | 62.2042 | 62.6648 | 123.1292 | 61.8133 | 123.0421 | 61.5224 | 61.6037 | 123.2544 | 61.5678 | 123.0372 | 61.5255 | 61.5614 | 61.4384 | 61.4744
3656.0938 | 123.4131 | -61.5601 | 61.5189 | 0.98259 | 2.9861 | 3.6875 | 1.7972 | 0.73211 | 0.6121 | 1.0635 | 61.5691 | 0.26237 | 61.4729 | -0.03768 | 0.043657 | 61.6989 | -0.006014 | 61.4725 | 62.5426 | 64.5461 | 65.2476 | 63.3573 | 62.2922 | 62.1722 | 62.6236 | 123.1292 | 61.8224 | 123.033 | 61.5224 | 61.6037 | 123.259 | 61.554 | 123.0326 | 61.5255 | 61.5752 | 61.4293 | 61.4789
3657.0625 | 123.4497 | -61.5463 | 61.5463 | 0.98259 | 3.0364 | 3.0053 | 1.7698 | 0.71838 | 0.58921 | 1.0635 | 61.5783 | 0.25779 | 61.5004 | -0.03768 | 0.039079 | 61.6852 | 0.003143 | 61.468 | 62.5289 | 64.5828 | 64.5516 | 63.3161 | 62.2647 | 62.1355 | 62.6098 | 123.1246 | 61.8041 | 123.0467 | 61.5086 | 61.5854 | 123.2315 | 61.5495 | 123.0143 | 61.5392 | 61.5752 | 61.4613 | 61.4973
3658.0781 | 123.317 | -61.6013 | 61.5463 | 2.3195 | 2.2352 | 3.0694 | 1.8293 | 0.77332 | 0.63041 | 1.0956 | 61.5691 | 0.25779 | 61.5004 | -0.03768 | 0.048236 | 61.6898 | 0.003143 | 61.4771 | 63.9207 | 63.8364 | 64.6707 | 63.4305 | 62.3746 | 62.2317 | 62.6968 | 123.1704 | 61.859 | 123.1017 | 61.5636 | 61.6495 | 123.291 | 61.6044 | 123.0784 | 61.5209 | 61.566 | 61.4522 | 61.4973
3659.0625 | 123.3215 | -61.5601 | 61.5143 | 2.3515 | 2.2626 | 3.0923 | 1.8751 | 0.80994 | 0.63499 | 1.0498 | 61.5737 | 0.26237 | 61.4958 | -0.033101 | 0.039079 | 61.6989 | -0.001436 | 61.4863 | 63.9116 | 63.8227 | 64.6524 | 63.4351 | 62.37 | 62.195 | 62.6098 | 123.1338 | 61.8224 | 123.0559 | 61.527 | 61.5991 | 123.259 | 61.5586 | 123.0463 | 61.5346 | 61.5752 | 61.4567 | 61.4973
3660.0625 | 123.381 | -61.5829 | 61.5417 | 2.3515 | 2.2489 | 3.1472 | 1.8751 | 0.78705 | 0.67162 | 1.0223 | 61.5691 | 0.24863 | 61.5004 | -0.033101 | 0.039079 | 61.6943 | 0.003143 | 61.4817 | 63.9345 | 63.8318 | 64.7302 | 63.458 | 62.37 | 62.2546 | 62.6053 | 123.1521 | 61.8316 | 123.0833 | 61.5498 | 61.622 | 123.2773 | 61.5861 | 123.0646 | 61.5301 | 61.566 | 61.4613 | 61.4973
3661.0938 | 123.436 | -61.5738 | 61.528 | 2.2874 | 2.1802 | 3.2434 | 1.7789 | 0.72754 | 0.67162 | 0.95822 | 61.5691 | 0.25779 | 61.5096 | -0.03768 | 0.039079 | 61.6989 | -0.006014 | 61.4817 | 63.8612 | 63.754 | 64.8172 | 63.3527 | 62.3013 | 62.2454 | 62.532 | 123.1429 | 61.8316 | 123.0833 | 61.5361 | 61.6129 | 123.2727 | 61.5678 | 123.0555 | 61.5301 | 61.5752 | 61.4705 | 61.5156
3662.0625 | 123.381 | -61.5372 | 61.5372 | 1.8662 | 2.6152 | 3.1289 | 1.8384 | 0.75958 | 0.72656 | 1.0315 | 61.5646 | 0.25779 | 61.5004 | -0.033101 | 0.048236 | 61.6898 | 0.007721 | 61.4817 | 63.4034 | 64.1524 | 64.6661 | 63.3756 | 62.2968 | 62.2637 | 62.5686 | 123.1017 | 61.795 | 123.0376 | 61.5041 | 61.5854 | 123.2269 | 61.5449 | 123.0189 | 61.5163 | 61.5569 | 61.4522 | 61.4927
3663.0938 | 123.3582 | -61.5921 | 61.5326 | 1.0696 | 3.2883 | 2.9732 | 1.8613 | 0.77332 | 0.74945 | 1.1047 | 61.5646 | 0.25779 | 61.4729 | -0.033101 | 0.039079 | 61.6989 | 0.003143 | 61.468 | 62.6617 | 64.8804 | 64.5654 | 63.4534 | 62.3654 | 62.3416 | 62.6968 | 123.1567 | 61.8499 | 123.065 | 61.559 | 61.6312 | 123.291 | 61.5952 | 123.0601 | 61.5255 | 61.5614 | 61.4339 | 61.4698
3664.0625 | 123.3398 | -61.6013 | 61.5417 | 2.0127 | 2.519 | 2.8725 | 1.7972 | 0.73669 | 0.75403 | 1.0086 | 61.5646 | 0.26237 | 61.4867 | -0.042259 | 0.039079 | 61.6943 | 0.003143 | 61.4725 | 63.614 | 64.1203 | 64.4738 | 63.3985 | 62.3379 | 62.3553 | 62.6098 | 123.1658 | 61.8636 | 123.0879 | 61.559 | 61.6403 | 123.2956 | 61.6044 | 123.0738 | 61.5255 | 61.5614 | 61.4476 | 61.4835
3665.0781 | 123.3582 | -61.5921 | 61.528 | 2.4065 | 2.3084 | 2.9778 | 1.7743 | 0.7138 | 0.7174 | 0.99026 | 61.56 | 0.25321 | 61.4775 | -0.033101 | 0.039079 | 61.6898 | -0.006014 | 61.4817 | 63.9986 | 63.9005 | 64.5699 | 63.3664 | 62.3059 | 62.3095 | 62.5824 | 123.1521 | 61.8453 | 123.0696 | 61.559 | 61.6312 | 123.2819 | 61.5861 | 123.0738 | 61.5209 | 61.566 | 61.4384 | 61.4835
3666.0625 | 123.3902 | -61.5692 | 61.5463 | 2.3973 | 2.3038 | 2.8222 | 1.8201 | 0.70465 | 0.6533 | 0.96737 | 61.5737 | 0.25321 | 61.5004 | -0.03768 | 0.043657 | 61.6943 | 0.007721 | 61.4771 | 63.9665 | 63.873 | 64.3914 | 63.3893 | 62.2739 | 62.2225 | 62.5366 | 123.1429 | 61.8224 | 123.0696 | 61.5315 | 61.6129 | 123.2636 | 61.5769 | 123.0463 | 61.5301 | 61.566 | 61.4567 | 61.4927
3667.0938 | 123.2758 | -61.6196 | 61.5463 | 2.3882 | 2.2947 | 2.4467 | 1.8247 | 0.71838 | 0.69451 | 0.95822 | 61.5783 | 0.25779 | 61.5096 | -0.042259 | 0.043657 | 61.6898 | -0.001436 | 61.4725 | 64.0077 | 63.9142 | 64.0663 | 63.4443 | 62.3379 | 62.3141 | 62.5778 | 123.1979 | 61.8774 | 123.1291 | 61.5773 | 61.6632 | 123.3093 | 61.6181 | 123.0921 | 61.5346 | 61.5797 | 61.4659 | 61.511
3668.0625 | 123.349 | -61.5372 | 61.5417 | 2.4065 | 2.3084 | 1.7828 | 1.8201 | 0.73211 | 0.72198 | 0.98568 | 61.5829 | 0.26237 | 61.5096 | -0.03768 | 0.043657 | 61.6806 | -0.001436 | 61.4542 | 63.9436 | 63.8456 | 63.32 | 63.3573 | 62.2693 | 62.2591 | 62.5229 | 123.1201 | 61.7995 | 123.0467 | 61.4995 | 61.5808 | 123.2178 | 61.5357 | 122.9914 | 61.5392 | 61.5843 | 61.4659 | 61.511
3669.0938 | 123.3765 | -61.5967 | 61.496 | 2.4431 | 2.3405 | 1.9843 | 1.843 | 0.76416 | 0.74029 | 0.97195 | 61.5783 | 0.25779 | 61.5096 | -0.03768 | 0.043657 | 61.6943 | 0.003143 | 61.4634 | 64.0398 | 63.9371 | 63.581 | 63.4397 | 62.3608 | 62.337 | 62.5686 | 123.175 | 61.8545 | 123.1062 | 61.559 | 61.6403 | 123.291 | 61.5998 | 123.0601 | 61.5346 | 61.5752 | 61.4659 | 61.5064
3670.0625 | 123.3536 | -61.5601 | 61.5509 | 1.2573 | 3.2791 | 2.0896 | 1.8522 | 0.755 | 0.72198 | 1.0635 | 61.5829 | 0.25321 | 61.5096 | -0.03768 | 0.039079 | 61.6943 | 0.003143 | 61.4634 | 62.8174 | 64.8392 | 63.6496 | 63.4122 | 62.3151 | 62.282 | 62.6236 | 123.1429 | 61.8133 | 123.0696 | 61.5224 | 61.5991 | 123.2544 | 61.5632 | 123.0234 | 61.5438 | 61.5797 | 61.4705 | 61.5064
3671.0938 | 123.3765 | -61.5784 | 61.496 | 2.5209 | 2.4229 | 2.8405 | 1.9529 | 0.76874 | 0.76318 | 0.99026 | 61.5646 | 0.26237 | 61.4912 | -0.03768 | 0.034501 | 61.6943 | -0.001436 | 61.4725 | 64.0993 | 64.0013 | 64.4188 | 63.5313 | 62.3471 | 62.3416 | 62.5686 | 123.1429 | 61.8407 | 123.0696 | 61.5407 | 61.6129 | 123.2727 | 61.5769 | 123.0509 | 61.5301 | 61.566 | 61.4567 | 61.4927
3672.0625 | 123.349 | -61.5738 | 61.528 | 2.5804 | 2.4824 | 2.9504 | 2.0261 | 0.79621 | 0.76318 | 1.0452 | 61.56 | 0.25321 | 61.4729 | -0.033101 | 0.039079 | 61.6943 | 0.012299 | 61.4863 | 64.1542 | 64.0562 | 64.5241 | 63.5999 | 62.37 | 62.337 | 62.619 | 123.1338 | 61.827 | 123.0467 | 61.5407 | 61.6129 | 123.2681 | 61.5861 | 123.0601 | 61.5209 | 61.5477 | 61.4339 | 61.4606
3673.0938 | 123.4222 | -61.5829 | 61.496 | 2.6262 | 2.5328 | 3.0511 | 2.0124 | 0.80536 | 0.79523 | 1.0269 | 61.5508 | 0.26237 | 61.4592 | -0.03768 | 0.039079 | 61.7035 | -0.001436 | 61.4817 | 64.2092 | 64.1157 | 64.634 | 63.5954 | 62.3883 | 62.3782 | 62.6098 | 123.1338 | 61.8453 | 123.0421 | 61.5453 | 61.622 | 123.2864 | 61.5815 | 123.0646 | 61.5118 | 61.5523 | 61.4201 | 61.4606
3674.0625 | 123.4131 | -61.5921 | 61.528 | 1.1108 | 3.618 | 3.0465 | 1.9987 | 0.78705 | 0.69909 | 1.1139 | 61.56 | 0.26237 | 61.4775 | -0.033101 | 0.039079 | 61.6989 | 0.007721 | 61.4771 | 62.7029 | 65.2101 | 64.6386 | 63.5908 | 62.3792 | 62.2912 | 62.706 | 123.1521 | 61.8545 | 123.0696 | 61.559 | 61.6312 | 123.291 | 61.5998 | 123.0692 | 61.5209 | 61.5523 | 61.4384 | 61.4698
3675.0938 | 123.3948 | -61.5692 | 61.5143 | 1.0833 | 3.6546 | 2.7031 | 1.9712 | 0.78247 | 0.7174 | 1.0223 | 61.5646 | 0.25779 | 61.5004 | -0.03768 | 0.039079 | 61.6943 | -0.001436 | 61.4634 | 62.6525 | 65.2238 | 64.2723 | 63.5404 | 62.3517 | 62.2866 | 62.5915 | 123.1338 | 61.827 | 123.0696 | 61.5315 | 61.6083 | 123.2636 | 61.5678 | 123.0326 | 61.5255 | 61.566 | 61.4613 | 61.5018
3676.0625 | 123.3444 | -61.5967 | 61.5326 | 1.0833 | 3.6225 | 2.5383 | 1.9849 | 0.79621 | 0.69909 | 0.97195 | 61.5691 | 0.26237 | 61.5096 | -0.033101 | 0.039079 | 61.6898 | -0.001436 | 61.468 | 62.68 | 65.2192 | 64.135 | 63.5816 | 62.3929 | 62.2958 | 62.5686 | 123.1658 | 61.859 | 123.1062 | 61.5636 | 61.6358 | 123.2864 | 61.5952 | 123.0646 | 61.5301 | 61.5706 | 61.4705 | 61.511
3677.1094 | 123.3215 | -61.6013 | 61.5189 | 1.1108 | 3.6592 | 3.1381 | 2.0033 | 0.82367 | 0.7174 | 1.0498 | 61.5737 | 0.25321 | 61.4958 | -0.03768 | 0.039079 | 61.7081 | -0.001436 | 61.468 | 62.712 | 65.2604 | 64.7393 | 63.6045 | 62.4249 | 62.3187 | 62.651 | 123.175 | 61.8545 | 123.0971 | 61.5636 | 61.6403 | 123.3093 | 61.5998 | 123.0692 | 61.5346 | 61.5752 | 61.4567 | 61.4973
3678.0625 | 123.349 | -61.5967 | 61.5234 | 1.1337 | 3.6958 | 3.2617 | 2.0307 | 0.86487 | 0.78608 | 1.1093 | 61.5691 | 0.26237 | 61.4958 | -0.03768 | 0.034501 | 61.6989 | -0.001436 | 61.4817 | 62.7304 | 65.2925 | 64.8584 | 63.6274 | 62.4616 | 62.3828 | 62.706 | 123.1658 | 61.859 | 123.0925 | 61.559 | 61.6312 | 123.2956 | 61.5952 | 123.0784 | 61.5346 | 61.5706 | 61.4613 | 61.4973
3679.0781 | 123.3856 | -61.5646 | 61.4822 | 1.1108 | 3.7004 | 3.3624 | 2.0078 | 0.87403 | 0.81355 | 1.1047 | 61.56 | 0.25779 | 61.4912 | -0.033101 | 0.043657 | 61.7035 | 0.003143 | 61.468 | 62.6754 | 65.265 | 64.9271 | 63.5725 | 62.4387 | 62.3782 | 62.6694 | 123.1246 | 61.8224 | 123.0559 | 61.5315 | 61.6083 | 123.2681 | 61.5678 | 123.0326 | 61.5163 | 61.5568 | 61.4476 | 61.4881
3680.0625 | 123.3261 | -61.5784 | 61.5005 | 1.1428 | 3.7462 | 3.2617 | 2.0216 | 0.89692 | 0.82728 | 1.1917 | 61.5554 | 0.25321 | 61.4821 | -0.033101 | 0.048236 | 61.7035 | -0.001436 | 61.4771 | 62.7212 | 65.3245 | 64.8401 | 63.5999 | 62.4753 | 62.4057 | 62.7701 | 123.1338 | 61.8316 | 123.0605 | 61.5453 | 61.6266 | 123.2819 | 61.5769 | 123.0555 | 61.5072 | 61.5568 | 61.4339 | 61.4835
3681.0781 | 123.3765 | -61.5967 | 61.5692 | 1.1428 | 3.5905 | 3.1976 | 2.0033 | 0.87403 | 0.79981 | 1.1688 | 61.5554 | 0.25321 | 61.4729 | -0.042259 | 0.048236 | 61.7035 | 0.007721 | 61.4771 | 62.7395 | 65.1872 | 64.7943 | 63.5999 | 62.4707 | 62.3965 | 62.7655 | 123.1521 | 61.8499 | 123.0696 | 61.5544 | 61.6449 | 123.3002 | 61.6044 | 123.0738 | 61.5072 | 61.5477 | 61.4247 | 61.4652
3682.0625 | 123.3902 | -61.5601 | 61.5326 | 2.6812 | 2.5694 | 3.019 | 1.9895 | 0.87861 | 0.80897 | 1.1459 | 61.5554 | 0.25321 | 61.4684 | -0.042259 | 0.043657 | 61.7035 | 0.007721 | 61.4725 | 64.2412 | 64.1295 | 64.5791 | 63.5496 | 62.4387 | 62.369 | 62.706 | 123.1155 | 61.8133 | 123.0284 | 61.5178 | 61.6037 | 123.2636 | 61.5678 | 123.0326 | 61.5118 | 61.5477 | 61.4247 | 61.4606
3683.0781 | 123.4085 | -61.5921 | 61.528 | 2.6995 | 2.6244 | 3.0511 | 2.0078 | 0.86487 | 0.79065 | 1.1871 | 61.56 | 0.25779 | 61.4867 | -0.03768 | 0.043657 | 61.7035 | 0.003143 | 61.4725 | 64.2916 | 64.2165 | 64.6432 | 63.5999 | 62.457 | 62.3828 | 62.7792 | 123.1521 | 61.8499 | 123.0788 | 61.5544 | 61.6358 | 123.2956 | 61.5952 | 123.0646 | 61.5163 | 61.5568 | 61.443 | 61.4835
3684.0625 | 123.3765 | -61.6013 | 61.5234 | 2.6766 | 2.574 | 2.8588 | 1.9758 | 0.8603 | 0.77234 | 1.1459 | 61.56 | 0.26237 | 61.4912 | -0.03768 | 0.043657 | 61.6989 | 0.007721 | 61.4817 | 64.2778 | 64.1752 | 64.46 | 63.577 | 62.4616 | 62.3736 | 62.7472 | 123.1612 | 61.8636 | 123.0925 | 61.5636 | 61.6449 | 123.3002 | 61.609 | 123.083 | 61.5163 | 61.5523 | 61.4476 | 61.4835
3685.0938 | 123.3536 | -61.5967 | 61.528 | 2.6812 | 2.574 | 2.6436 | 1.93 | 0.82367 | 0.74487 | 1.1368 | 61.5737 | 0.25779 | 61.5004 | -0.033101 | 0.043657 | 61.6989 | 0.007721 | 61.4817 | 64.2779 | 64.1707 | 64.2403 | 63.5267 | 62.4204 | 62.3416 | 62.7334 | 123.1704 | 61.8545 | 123.0971 | 61.5636 | 61.6403 | 123.2956 | 61.6044 | 123.0784 | 61.5301 | 61.566 | 61.4567 | 61.4927
3686.0625 | 123.3719 | -61.5555 | 61.5417 | 2.6262 | 2.519 | 2.3277 | 1.93 | 0.84198 | 0.72656 | 1.0818 | 61.5737 | 0.26237 | 61.5096 | -0.028522 | 0.039079 | 61.6898 | 0.003143 | 61.4817 | 64.1817 | 64.0745 | 63.8831 | 63.4855 | 62.3975 | 62.282 | 62.6373 | 123.1292 | 61.8179 | 123.065 | 61.527 | 61.5946 | 123.2452 | 61.5586 | 123.0372 | 61.5346 | 61.5706 | 61.4705 | 61.5064
3687.0938 | 123.3856 | -61.5784 | 61.5051 | 2.6308 | 2.5282 | 2.4009 | 2.017 | 0.87403 | 0.77692 | 1.1139 | 61.56 | 0.26695 | 61.505 | -0.03768 | 0.034501 | 61.6989 | 0.003143 | 61.468 | 64.2092 | 64.1066 | 63.9793 | 63.5954 | 62.4524 | 62.3553 | 62.6922 | 123.1384 | 61.8453 | 123.0833 | 61.5407 | 61.6129 | 123.2773 | 61.5815 | 123.0463 | 61.5255 | 61.5568 | 61.4705 | 61.5018
3688.0625 | 123.3627 | -61.5829 | 61.5234 | 2.6491 | 2.5511 | 3.2709 | 2.0719 | 0.86487 | 0.74029 | 1.0864 | 61.5554 | 0.25321 | 61.4912 | -0.033101 | 0.043657 | 61.7035 | -0.006014 | 61.4771 | 64.2321 | 64.134 | 64.8538 | 63.6549 | 62.4478 | 62.3232 | 62.6694 | 123.1384 | 61.8362 | 123.0742 | 61.5498 | 61.6266 | 123.2864 | 61.5769 | 123.0601 | 61.5118 | 61.5614 | 61.4476 | 61.4973
3689.0938 | 123.381 | -61.6058 | 61.4822 | 2.6995 | 2.5969 | 3.4174 | 2.1086 | 0.86945 | 0.77692 | 1.1185 | 61.5554 | 0.26237 | 61.4638 | -0.03768 | 0.039079 | 61.7081 | 0.003143 | 61.4771 | 64.3053 | 64.2027 | 65.0232 | 63.7144 | 62.4753 | 62.3828 | 62.7243 | 123.1612 | 61.8682 | 123.0696 | 61.5682 | 61.6449 | 123.3139 | 61.609 | 123.083 | 61.5163 | 61.5523 | 61.4247 | 61.4606
3690.0625 | 123.381 | -61.5921 | 61.5417 | 2.7086 | 2.6015 | 3.3258 | 2.0399 | 0.88319 | 0.76318 | 1.1185 | 61.5554 | 0.26695 | 61.4638 | -0.033101 | 0.043657 | 61.7127 | 0.007721 | 61.4771 | 64.3007 | 64.1936 | 64.9179 | 63.632 | 62.4753 | 62.3553 | 62.7106 | 123.1475 | 61.8591 | 123.0559 | 61.559 | 61.6358 | 123.3048 | 61.5998 | 123.0692 | 61.5118 | 61.5477 | 61.4201 | 61.4561
3691.0781 | 123.3948 | -61.5921 | 61.5097 | 2.7086 | 2.6106 | 2.7077 | 2.0307 | 0.85572 | 0.77692 | 1.1322 | 61.5646 | 0.26237 | 61.4684 | -0.03768 | 0.043657 | 61.7081 | -0.006014 | 61.4725 | 64.3007 | 64.2027 | 64.2998 | 63.6228 | 62.4478 | 62.369 | 62.7243 | 123.1567 | 61.8545 | 123.0605 | 61.5544 | 61.6358 | 123.3002 | 61.5861 | 123.0646 | 61.5209 | 61.5706 | 61.4247 | 61.4744
3692.0625 | 123.2712 | -61.5829 | 61.5646 | 2.6949 | 2.5969 | 2.4009 | 2.0765 | 0.85572 | 0.76776 | 1.1047 | 61.56 | 0.25321 | 61.4912 | -0.042259 | 0.043657 | 61.6989 | 0.003143 | 61.4817 | 64.2779 | 64.1798 | 63.9839 | 63.6595 | 62.4387 | 62.3507 | 62.6877 | 123.1429 | 61.8362 | 123.0742 | 61.5407 | 61.6266 | 123.2819 | 61.5861 | 123.0646 | 61.5163 | 61.5568 | 61.4476 | 61.4881
3693.0625 | 123.349 | -61.5829 | 61.5326 | 2.6949 | 2.5877 | 2.5429 | 2.0902 | 0.84198 | 0.72656 | 1.091 | 61.56 | 0.25779 | 61.5004 | -0.033101 | 0.034501 | 61.6989 | 0.007721 | 61.4725 | 64.2779 | 64.1707 | 64.1258 | 63.6732 | 62.4249 | 62.3095 | 62.6739 | 123.1429 | 61.8407 | 123.0833 | 61.5498 | 61.6174 | 123.2819 | 61.5907 | 123.0555 | 61.5255 | 61.5523 | 61.4659 | 61.4927
3694.0781 | 123.3261 | -61.6058 | 61.5417 | 2.759 | 2.6518 | 2.6436 | 2.1589 | 0.87861 | 0.79065 | 1.1871 | 61.5691 | 0.25779 | 61.5004 | -0.033101 | 0.052814 | 61.7035 | 0.003143 | 61.4771 | 64.3648 | 64.2577 | 64.2494 | 63.7648 | 62.4844 | 62.3965 | 62.793 | 123.175 | 61.8636 | 123.1062 | 61.5727 | 61.6586 | 123.3093 | 61.609 | 123.083 | 61.5163 | 61.566 | 61.4476 | 61.4973
3695.0625 | 123.3902 | -61.5738 | 61.5372 | 2.7224 | 2.6198 | 2.3643 | 2.2001 | 0.85114 | 0.74945 | 1.2512 | 61.5737 | 0.25779 | 61.5004 | -0.033101 | 0.039079 | 61.6989 | 0.007721 | 61.468 | 64.2962 | 64.1936 | 63.9381 | 63.7739 | 62.4249 | 62.3232 | 62.825 | 123.1475 | 61.8316 | 123.0742 | 61.5407 | 61.6129 | 123.2727 | 61.5815 | 123.0418 | 61.5346 | 61.566 | 61.4613 | 61.4927
3696.0938 | 123.3719 | -61.5875 | 61.5189 | 2.7544 | 2.661 | 2.291 | 2.2551 | 0.88777 | 0.80897 | 1.3107 | 61.56 | 0.25779 | 61.4867 | -0.033101 | 0.043657 | 61.6989 | 0.003143 | 61.4771 | 64.3419 | 64.2485 | 63.8786 | 63.8426 | 62.4753 | 62.3965 | 62.8983 | 123.1475 | 61.8453 | 123.0742 | 61.5544 | 61.6312 | 123.2864 | 61.5907 | 123.0646 | 61.5163 | 61.5568 | 61.443 | 61.4835
3697.0625 | 123.2986 | -61.5784 | 61.5967 | 2.7453 | 2.6427 | 2.2956 | 2.2459 | 0.89234 | 0.82728 | 1.3107 | 61.5646 | 0.25779 | 61.4912 | -0.033101 | 0.043657 | 61.6989 | 0.007721 | 61.4771 | 64.3236 | 64.221 | 63.874 | 63.8243 | 62.4707 | 62.4057 | 62.8891 | 123.1429 | 61.8362 | 123.0696 | 61.5453 | 61.622 | 123.2773 | 61.5861 | 123.0555 | 61.5209 | 61.5569 | 61.4476 | 61.4835
3698.0625 | 123.3948 | -61.5829 | 61.5143 | 2.727 | 2.6244 | 2.2407 | 2.191 | 0.82367 | 0.77234 | 1.2283 | 61.56 | 0.26237 | 61.4729 | -0.028522 | 0.048236 | 61.6943 | 0.007721 | 61.4725 | 64.3099 | 64.2073 | 63.8236 | 63.7739 | 62.4066 | 62.3553 | 62.8113 | 123.1429 | 61.8453 | 123.0559 | 61.5544 | 61.6312 | 123.2773 | 61.5907 | 123.0555 | 61.5118 | 61.5523 | 61.4247 | 61.4652
3699.0781 | 123.4314 | -61.5829 | 61.4914 | 2.7224 | 2.6472 | 2.5291 | 2.1681 | 0.80078 | 0.71282 | 1.2604 | 61.5554 | 0.25779 | 61.4592 | -0.03768 | 0.048236 | 61.7081 | 0.003143 | 61.4771 | 64.3053 | 64.2302 | 64.1121 | 63.751 | 62.3837 | 62.2958 | 62.8433 | 123.1384 | 61.8407 | 123.0421 | 61.5453 | 61.6312 | 123.291 | 61.5861 | 123.0601 | 61.5072 | 61.5523 | 61.411 | 61.4561
3700.0625 | 123.4039 | -61.5555 | 61.5372 | 2.7911 | 2.7113 | 2.7626 | 2.1406 | 0.80078 | 0.76776 | 1.2329 | 61.5554 | 0.25779 | 61.4729 | -0.033101 | 0.043657 | 61.7035 | 0.012299 | 61.4817 | 64.3465 | 64.2668 | 64.3181 | 63.6961 | 62.3563 | 62.3232 | 62.7884 | 123.1109 | 61.8133 | 123.0284 | 61.5224 | 61.5991 | 123.259 | 61.5678 | 123.0372 | 61.5118 | 61.5431 | 61.4293 | 61.4606
3701.0938 | 123.317 | -61.6058 | 61.5417 | 2.8964 | 2.7938 | 3.1472 | 2.2047 | 0.84198 | 0.79981 | 1.2695 | 61.5554 | 0.25779 | 61.4821 | -0.03768 | 0.039079 | 61.7172 | 0.007721 | 61.4909 | 64.5022 | 64.3996 | 64.7531 | 63.8105 | 62.4478 | 62.4056 | 62.8754 | 123.1612 | 61.8636 | 123.0879 | 61.5682 | 61.6449 | 123.3231 | 61.6136 | 123.0967 | 61.5163 | 61.5477 | 61.443 | 61.4744
3702.0625 | 123.2849 | -61.6058 | 61.5738 | 2.8872 | 2.7892 | 3.2525 | 2.2642 | 0.85572 | 0.81812 | 1.1734 | 61.5554 | 0.25321 | 61.4867 | -0.033101 | 0.048236 | 61.7081 | 0.007721 | 61.4863 | 64.493 | 64.395 | 64.8584 | 63.8701 | 62.4616 | 62.424 | 62.7792 | 123.1612 | 61.859 | 123.0925 | 61.5727 | 61.6541 | 123.3139 | 61.6136 | 123.0921 | 61.5072 | 61.5477 | 61.4384 | 61.4789
3703.0781 | 123.3627 | -61.6104 | 61.5143 | 2.9101 | 2.8167 | 3.2251 | 2.2184 | 0.8603 | 0.81355 | 1.1825 | 61.5554 | 0.25779 | 61.4821 | -0.042259 | 0.039079 | 61.7081 | 0.003143 | 61.4863 | 64.5205 | 64.4271 | 64.8355 | 63.8289 | 62.4707 | 62.424 | 62.793 | 123.1658 | 61.8682 | 123.0925 | 61.5682 | 61.6495 | 123.3185 | 61.6136 | 123.0967 | 61.5163 | 61.5523 | 61.443 | 61.4789
3704.0625 | 123.4314 | -61.5829 | 61.5143 | 2.9559 | 2.8533 | 3.0831 | 2.2368 | 0.84656 | 0.78608 | 1.1917 | 61.5554 | 0.26237 | 61.4867 | -0.033101 | 0.048236 | 61.7172 | 0.012299 | 61.4771 | 64.5388 | 64.4362 | 64.6661 | 63.8197 | 62.4295 | 62.369 | 62.7746 | 123.1384 | 61.8453 | 123.0696 | 61.5498 | 61.6312 | 123.3002 | 61.5952 | 123.0601 | 61.5072 | 61.5431 | 61.4384 | 61.4744
3705.0781 | 123.3627 | -61.615 | 61.5234 | 2.9788 | 2.8762 | 3.1243 | 2.2871 | 0.83283 | 0.76776 | 1.178 | 61.5554 | 0.26237 | 61.4775 | -0.033101 | 0.039079 | 61.7172 | -0.006014 | 61.4909 | 64.5938 | 64.4912 | 64.7393 | 63.9021 | 62.4478 | 62.3828 | 62.793 | 123.1704 | 61.8774 | 123.0925 | 61.5819 | 61.6541 | 123.3322 | 61.609 | 123.1058 | 61.5163 | 61.5614 | 61.4384 | 61.4835
3706.0625 | 123.3261 | -61.6196 | 61.528 | 2.9742 | 2.8716 | 2.8679 | 2.3054 | 0.86487 | 0.79981 | 1.1505 | 61.5508 | 0.25779 | 61.4684 | -0.03768 | 0.043657 | 61.7081 | -0.006014 | 61.4909 | 64.5938 | 64.4912 | 64.4875 | 63.925 | 62.4844 | 62.4194 | 62.7701 | 123.1704 | 61.8774 | 123.0879 | 61.5819 | 61.6632 | 123.3276 | 61.6136 | 123.1104 | 61.5072 | 61.5568 | 61.4247 | 61.4744
3707.0938 | 123.3444 | -61.5921 | 61.4822 | 2.9971 | 2.8991 | 2.9229 | 2.2825 | 0.85114 | 0.8227 | 1.1459 | 61.5463 | 0.26695 | 61.4546 | -0.033101 | 0.043657 | 61.7081 | 0.003143 | 61.4909 | 64.5892 | 64.4912 | 64.515 | 63.8746 | 62.4432 | 62.4148 | 62.738 | 123.1384 | 61.8591 | 123.0467 | 61.559 | 61.6358 | 123.3002 | 61.5952 | 123.083 | 61.5026 | 61.5431 | 61.411 | 61.4515
3708.0625 | 123.3902 | -61.5692 | 61.496 | 3.0978 | 2.9907 | 2.9961 | 2.3009 | 0.85114 | 0.79523 | 1.1551 | 61.5463 | 0.26237 | 61.4592 | -0.03768 | 0.043657 | 61.7127 | 0.003143 | 61.4909 | 64.667 | 64.5599 | 64.5654 | 63.8701 | 62.4204 | 62.3644 | 62.7243 | 123.1155 | 61.8316 | 123.0284 | 61.5315 | 61.6129 | 123.2819 | 61.5724 | 123.0601 | 61.5026 | 61.5431 | 61.4155 | 61.4561
3709.0938 | 123.4039 | -61.615 | 61.4777 | 3.1527 | 3.0548 | 3.2938 | 2.278 | 0.8603 | 0.84559 | 1.1597 | 61.5417 | 0.26237 | 61.4775 | -0.033101 | 0.039079 | 61.7127 | 0.007721 | 61.4863 | 64.7677 | 64.6697 | 64.9087 | 63.893 | 62.4753 | 62.4606 | 62.7746 | 123.1567 | 61.8774 | 123.0925 | 61.5819 | 61.6541 | 123.3276 | 61.6227 | 123.1013 | 61.5026 | 61.534 | 61.4384 | 61.4698
3710.0625 | 123.4177 | -61.5829 | 61.5097 | 3.1299 | 3.0319 | 3.0465 | 2.2505 | 0.85114 | 0.85933 | 1.1368 | 61.56 | 0.26237 | 61.4867 | -0.033101 | 0.043657 | 61.7172 | 0.003143 | 61.4954 | 64.7128 | 64.6148 | 64.6295 | 63.8334 | 62.4341 | 62.4423 | 62.7197 | 123.1429 | 61.8453 | 123.0696 | 61.5498 | 61.6266 | 123.3002 | 61.5861 | 123.0784 | 61.5163 | 61.5568 | 61.443 | 61.4835
3711.0938 | 123.4039 | -61.5829 | 61.5738 | 3.1344 | 3.0364 | 3.1472 | 2.2551 | 0.87403 | 0.85475 | 1.178 | 61.5463 | 0.26695 | 61.4775 | -0.03768 | 0.039079 | 61.7127 | 0.003143 | 61.5092 | 64.7174 | 64.6194 | 64.7302 | 63.838 | 62.457 | 62.4377 | 62.7609 | 123.1292 | 61.8499 | 123.0605 | 61.5453 | 61.622 | 123.2956 | 61.5861 | 123.0921 | 61.5072 | 61.5431 | 61.4384 | 61.4744
3712.0625 | 123.3536 | -61.6058 | 61.5646 | 3.1436 | 3.0502 | 3.1427 | 2.3146 | 0.87861 | 0.7815 | 1.1825 | 61.5463 | 0.25779 | 61.4638 | -0.033101 | 0.043657 | 61.7127 | 0.007721 | 61.4909 | 64.7494 | 64.656 | 64.7485 | 63.9204 | 62.4844 | 62.3873 | 62.7884 | 123.1521 | 61.8636 | 123.0696 | 61.5727 | 61.6495 | 123.3185 | 61.6136 | 123.0967 | 61.5026 | 61.5385 | 61.4201 | 61.4561
3713.0781 | 123.3536 | -61.6104 | 61.5143 | 3.1711 | 3.0731 | 3.2068 | 2.3283 | 0.87403 | 0.75403 | 1.1825 | 61.5371 | 0.26237 | 61.4775 | -0.03768 | 0.039079 | 61.7172 | 0.003143 | 61.4909 | 64.7815 | 64.6835 | 64.8172 | 63.9387 | 62.4844 | 62.3644 | 62.793 | 123.1475 | 61.8728 | 123.0879 | 61.5727 | 61.6495 | 123.3276 | 61.6136 | 123.1013 | 61.498 | 61.534 | 61.4384 | 61.4744
3714.0625 | 123.4085 | -61.5646 | 61.5189 | 3.1253 | 3.0319 | 3.1014 | 2.3238 | 0.86945 | 0.7815 | 1.1505 | 61.5508 | 0.26237 | 61.4867 | -0.03768 | 0.048236 | 61.7172 | 0.007721 | 61.5 | 64.6899 | 64.5965 | 64.6661 | 63.8884 | 62.4341 | 62.3461 | 62.7151 | 123.1155 | 61.827 | 123.0513 | 61.527 | 61.6129 | 123.2819 | 61.5724 | 123.0646 | 61.5026 | 61.5431 | 61.4384 | 61.4789
3715.0625 | 123.4268 | -61.5646 | 61.5417 | 3.1207 | 3.0181 | 2.9229 | 2.3558 | 0.88319 | 0.80439 | 1.1734 | 61.5508 | 0.25779 | 61.4775 | -0.033101 | 0.043657 | 61.7127 | 0.007721 | 61.4909 | 64.6853 | 64.5828 | 64.4875 | 63.9204 | 62.4478 | 62.369 | 62.738 | 123.1155 | 61.8224 | 123.0421 | 61.5315 | 61.6083 | 123.2773 | 61.5724 | 123.0555 | 61.5072 | 61.5431 | 61.4339 | 61.4698
3716.0938 | 123.3627 | -61.5646 | 61.5417 | 3.0703 | 2.9678 | 2.8817 | 2.2917 | 0.8603 | 0.76776 | 1.091 | 61.5417 | 0.26695 | 61.4592 | -0.03768 | 0.048236 | 61.7172 | 0.003143 | 61.5 | 64.635 | 64.5324 | 64.4463 | 63.8563 | 62.4249 | 62.3324 | 62.6556 | 123.1063 | 61.8316 | 123.0238 | 61.527 | 61.6129 | 123.2819 | 61.5678 | 123.0646 | 61.4934 | 61.5385 | 61.411 | 61.4561
3717.0625 | 123.3032 | -61.6013 | 61.5784 | 3.1024 | 2.9998 | 2.8679 | 2.2322 | 0.83283 | 0.76776 | 1.0956 | 61.5463 | 0.25779 | 61.4775 | -0.028522 | 0.043657 | 61.7081 | 0.003143 | 61.4909 | 64.7036 | 64.6011 | 64.4692 | 63.8334 | 62.4341 | 62.369 | 62.6968 | 123.1475 | 61.859 | 123.0788 | 61.5727 | 61.6449 | 123.3093 | 61.6044 | 123.0921 | 61.5026 | 61.5431 | 61.4339 | 61.4744
3718.0625 | 123.4314 | -61.5738 | 61.5234 | 3.1711 | 3.0777 | 2.6527 | 2.2368 | 0.85114 | 0.79523 | 1.1688 | 61.5554 | 0.26237 | 61.4821 | -0.033101 | 0.039079 | 61.7081 | 0.007721 | 61.4909 | 64.7448 | 64.6514 | 64.2265 | 63.8106 | 62.4249 | 62.369 | 62.7426 | 123.1292 | 61.8362 | 123.0559 | 61.5407 | 61.6129 | 123.2819 | 61.5815 | 123.0646 | 61.5163 | 61.5477 | 61.443 | 61.4744
3719.0938 | 123.3902 | -61.6058 | 61.5234 | 3.226 | 3.1143 | 2.6161 | 2.2322 | 0.8191 | 0.68993 | 1.1642 | 61.56 | 0.26237 | 61.4912 | -0.042259 | 0.034501 | 61.7035 | -0.001436 | 61.4909 | 64.8318 | 64.7201 | 64.222 | 63.838 | 62.4249 | 62.2958 | 62.7701 | 123.1658 | 61.8682 | 123.0971 | 61.5636 | 61.6403 | 123.3093 | 61.6044 | 123.0967 | 61.5255 | 61.5614 | 61.4567 | 61.4927
3720.0625 | 123.4039 | -61.5875 | 61.528 | 3.2214 | 3.1189 | 2.5978 | 2.2963 | 0.82825 | 0.71282 | 1.2146 | 61.5417 | 0.26237 | 61.4546 | -0.023943 | 0.048236 | 61.7172 | 0.003143 | 61.4954 | 64.8089 | 64.7064 | 64.1853 | 63.8838 | 62.4158 | 62.3003 | 62.8021 | 123.1292 | 61.8499 | 123.0421 | 61.5636 | 61.6358 | 123.3048 | 61.5907 | 123.083 | 61.4934 | 61.5385 | 61.4064 | 61.4515
3721.0781 | 123.3353 | -61.6058 | 61.4914 | 3.1939 | 3.0914 | 2.7855 | 2.2184 | 0.83283 | 0.77234 | 1.2237 | 61.5463 | 0.25321 | 61.4638 | -0.042259 | 0.043657 | 61.7172 | -0.001436 | 61.4863 | 64.7998 | 64.6972 | 64.3914 | 63.8243 | 62.4387 | 62.3782 | 62.8296 | 123.1521 | 61.859 | 123.0696 | 61.5636 | 61.6495 | 123.3231 | 61.6044 | 123.0921 | 61.5026 | 61.5477 | 61.4201 | 61.4652
3722.0625 | 123.2941 | -61.6013 | 61.5875 | 1.4038 | 4.3414 | 2.8908 | 2.2322 | 0.82825 | 0.74487 | 1.3336 | 61.5508 | 0.26237 | 61.4912 | -0.023943 | 0.043657 | 61.7172 | 0.003143 | 61.4909 | 63.0051 | 65.9427 | 64.4921 | 63.8334 | 62.4295 | 62.3461 | 62.9349 | 123.1521 | 61.8636 | 123.0925 | 61.5773 | 61.6449 | 123.3185 | 61.6044 | 123.0921 | 61.5072 | 61.5477 | 61.4476 | 61.4881
3723.0938 | 123.4314 | -61.5601 | 61.5372 | 1.8479 | 3.9568 | 3.2297 | 2.3466 | 0.87403 | 0.8227 | 1.3382 | 61.5463 | 0.26695 | 61.4867 | -0.042259 | 0.048236 | 61.7172 | 0.007721 | 61.5 | 63.408 | 65.5168 | 64.7897 | 63.9067 | 62.4341 | 62.3828 | 62.8983 | 123.1063 | 61.827 | 123.0467 | 61.5178 | 61.6083 | 123.2773 | 61.5678 | 123.0601 | 61.498 | 61.5385 | 61.4384 | 61.4789
3724.0625 | 123.4543 | -61.5555 | 61.5097 | 1.3946 | 4.3506 | 3.3716 | 2.3833 | 0.88319 | 0.82728 | 1.4115 | 61.5417 | 0.26237 | 61.4592 | -0.03768 | 0.048236 | 61.7172 | 0.003143 | 61.4909 | 62.9501 | 65.906 | 64.9271 | 63.9388 | 62.4387 | 62.3828 | 62.9669 | 123.0972 | 61.8179 | 123.0147 | 61.5178 | 61.6037 | 123.2727 | 61.5586 | 123.0463 | 61.4934 | 61.5385 | 61.411 | 61.4561
3725.0938 | 123.3902 | -61.6104 | 61.5097 | 2.965 | 3.3799 | 3.2297 | 2.3695 | 0.8603 | 0.84559 | 1.3519 | 61.5279 | 0.25779 | 61.45 | -0.033101 | 0.034501 | 61.7218 | 0.003143 | 61.4954 | 64.5754 | 64.9903 | 64.8401 | 63.9799 | 62.4707 | 62.456 | 62.9624 | 123.1384 | 61.8682 | 123.0605 | 61.5773 | 61.6449 | 123.3322 | 61.6136 | 123.1058 | 61.4934 | 61.5248 | 61.4155 | 61.4469
3726.0625 | 123.3856 | -61.6241 | 61.5326 | 3.2855 | 3.1921 | 3.0969 | 2.3604 | 0.86945 | 0.84102 | 1.265 | 61.5417 | 0.25779 | 61.4729 | -0.033101 | 0.048236 | 61.7172 | 0.003143 | 61.5046 | 64.9097 | 64.8163 | 64.721 | 63.9845 | 62.4936 | 62.4652 | 62.8891 | 123.1658 | 61.8819 | 123.0971 | 61.591 | 61.6724 | 123.3414 | 61.6273 | 123.1287 | 61.4934 | 61.5385 | 61.4247 | 61.4698
3727.0938 | 123.381 | -61.5875 | 61.5234 | 3.2214 | 3.1189 | 3.2388 | 2.3054 | 0.83741 | 0.79065 | 1.2878 | 61.5508 | 0.26237 | 61.4821 | -0.03768 | 0.039079 | 61.7218 | 0.003143 | 61.5 | 64.8089 | 64.7064 | 64.8263 | 63.893 | 62.4249 | 62.3782 | 62.8754 | 123.1384 | 61.8499 | 123.0696 | 61.5498 | 61.6266 | 123.3093 | 61.5907 | 123.0875 | 61.5118 | 61.5477 | 61.443 | 61.4789
3728.0625 | 123.3444 | -61.6013 | 61.5463 | 3.2306 | 3.1372 | 3.2113 | 2.2047 | 0.8191 | 0.75861 | 1.2237 | 61.5463 | 0.25779 | 61.4821 | -0.03768 | 0.048236 | 61.7172 | 0.003143 | 61.5092 | 64.8318 | 64.7384 | 64.8126 | 63.806 | 62.4204 | 62.3599 | 62.825 | 123.1475 | 61.859 | 123.0833 | 61.5636 | 61.6495 | 123.3185 | 61.6044 | 123.1104 | 61.498 | 61.5431 | 61.4339 | 61.4789
3729.0781 | 123.4085 | -61.5738 | 61.5189 | 3.2626 | 3.1601 | 3.193 | 2.2413 | 0.85114 | 0.77234 | 1.1917 | 61.5417 | 0.26237 | 61.4546 | -0.03768 | 0.048236 | 61.7172 | 0.003143 | 61.4954 | 64.8364 | 64.7339 | 64.7668 | 63.8151 | 62.4249 | 62.3461 | 62.7655 | 123.1155 | 61.8362 | 123.0284 | 61.5361 | 61.622 | 123.291 | 61.5769 | 123.0692 | 61.4934 | 61.5385 | 61.4064 | 61.4515
3730.0625 | 123.3856 | -61.5692 | 61.5189 | 3.2535 | 3.1555 | 3.1243 | 2.2551 | 0.85114 | 0.75861 | 1.178 | 61.5417 | 0.25321 | 61.4638 | -0.033101 | 0.043657 | 61.7127 | -0.001436 | 61.5 | 64.8227 | 64.7247 | 64.6936 | 63.8243 | 62.4204 | 62.3278 | 62.7472 | 123.1109 | 61.8224 | 123.033 | 61.5361 | 61.6129 | 123.2819 | 61.5678 | 123.0692 | 61.498 | 61.5431 | 61.4201 | 61.4652
3731.0781 | 123.4177 | -61.5784 | 61.5097 | 3.1711 | 3.0639 | 3.1793 | 2.278 | 0.8603 | 0.77692 | 1.178 | 61.5463 | 0.25779 | 61.4821 | -0.033101 | 0.039079 | 61.7172 | 0.007721 | 61.4909 | 64.7494 | 64.6423 | 64.7577 | 63.8563 | 62.4387 | 62.3553 | 62.7563 | 123.1246 | 61.8362 | 123.0605 | 61.5453 | 61.6174 | 123.2956 | 61.5861 | 123.0692 | 61.5072 | 61.5385 | 61.443 | 61.4744
3732.0625 | 123.3353 | -61.6104 | 61.5738 | 3.2855 | 3.183 | 3.1427 | 2.3238 | 0.86945 | 0.75861 | 1.2604 | 61.5463 | 0.26237 | 61.4867 | -0.033101 | 0.039079 | 61.7218 | 0.003143 | 61.5 | 64.8959 | 64.7934 | 64.7531 | 63.9342 | 62.4799 | 62.369 | 62.8708 | 123.1567 | 61.8728 | 123.0971 | 61.5773 | 61.6495 | 123.3322 | 61.6136 | 123.1104 | 61.5072 | 61.5431 | 61.4476 | 61.4835
3733.0781 | 123.381 | -61.5921 | 61.5143 | 3.2764 | 3.1738 | 3.1106 | 2.3238 | 0.8603 | 0.70366 | 1.2375 | 61.5463 | 0.25321 | 61.4958 | -0.028522 | 0.039079 | 61.7172 | 0.003143 | 61.4909 | 64.8685 | 64.7659 | 64.7027 | 63.9159 | 62.4524 | 62.2958 | 62.8296 | 123.1384 | 61.8453 | 123.0879 | 61.5636 | 61.6312 | 123.3093 | 61.5952 | 123.083 | 61.5072 | 61.5431 | 61.4567 | 61.4927
3734.0625 | 123.3124 | -61.6333 | 61.5738 | 3.2764 | 3.1692 | 3.1198 | 2.3558 | 0.84198 | 0.74029 | 1.2833 | 61.5417 | 0.25321 | 61.4638 | -0.033101 | 0.043657 | 61.7127 | 0.003143 | 61.5046 | 64.9097 | 64.8025 | 64.7531 | 63.9891 | 62.4753 | 62.3736 | 62.9166 | 123.175 | 61.8865 | 123.0971 | 61.6002 | 61.677 | 123.346 | 61.6364 | 123.1379 | 61.498 | 61.5385 | 61.4201 | 61.4606
3735.0781 | 123.381 | -61.6058 | 61.5143 | 3.3313 | 3.2333 | 3.1472 | 2.3238 | 0.83741 | 0.74945 | 1.2924 | 61.5417 | 0.25779 | 61.4546 | -0.033101 | 0.048236 | 61.7172 | 0.003143 | 61.5046 | 64.9371 | 64.8392 | 64.7531 | 63.9296 | 62.4432 | 62.3553 | 62.8983 | 123.1475 | 61.8636 | 123.0605 | 61.5727 | 61.6541 | 123.3231 | 61.609 | 123.1104 | 61.4934 | 61.5385 | 61.4064 | 61.4515
3736.0625 | 123.2849 | -61.6196 | 61.5372 | 3.345 | 3.2379 | 3.4677 | 2.2551 | 0.82367 | 0.7174 | 1.2741 | 61.5371 | 0.26695 | 61.4729 | -0.033101 | 0.039079 | 61.7264 | 0.003143 | 61.5092 | 64.9646 | 64.8575 | 65.0873 | 63.8746 | 62.4432 | 62.337 | 62.8937 | 123.1567 | 61.8865 | 123.0925 | 61.5865 | 61.6586 | 123.346 | 61.6227 | 123.1287 | 61.498 | 61.534 | 61.4339 | 61.4698
3737.0938 | 123.2712 | -61.647 | 61.528 | 3.3542 | 3.2471 | 3.3624 | 2.223 | 0.81452 | 0.68077 | 1.2421 | 61.5508 | 0.25779 | 61.4821 | -0.028522 | 0.039079 | 61.7172 | -0.001436 | 61.4954 | 65.0012 | 64.8941 | 65.0095 | 63.8701 | 62.4616 | 62.3278 | 62.8891 | 123.1979 | 61.9048 | 123.1291 | 61.6185 | 61.6861 | 123.3643 | 61.6456 | 123.1425 | 61.5118 | 61.5523 | 61.443 | 61.4835
3738.0625 | 123.381 | -61.5829 | 61.5463 | 3.3221 | 3.2242 | 3.3166 | 2.2276 | 0.76874 | 0.66246 | 1.2146 | 61.5463 | 0.25321 | 61.4867 | -0.03768 | 0.039079 | 61.7172 | 0.003143 | 61.5 | 64.9051 | 64.8071 | 64.8996 | 63.8105 | 62.3517 | 62.2454 | 62.7975 | 123.1292 | 61.8362 | 123.0696 | 61.5453 | 61.622 | 123.3002 | 61.5861 | 123.083 | 61.5072 | 61.5431 | 61.4476 | 61.4835
3739.0938 | 123.4222 | -61.5784 | 61.5005 | 3.3084 | 3.2013 | 3.3899 | 2.2505 | 0.78247 | 0.61668 | 1.2054 | 61.5417 | 0.26237 | 61.4821 | -0.03768 | 0.043657 | 61.7264 | -0.001436 | 61.5046 | 64.8868 | 64.7797 | 64.9683 | 63.8289 | 62.3608 | 62.195 | 62.7838 | 123.12 | 61.8407 | 123.0605 | 61.5407 | 61.622 | 123.3048 | 61.5769 | 123.083 | 61.498 | 61.5431 | 61.4384 | 61.4835
3740.0625 | 123.3307 | -61.5921 | 61.5555 | 3.3221 | 3.2196 | 3.5456 | 2.2505 | 0.78705 | 0.56173 | 1.2512 | 61.5417 | 0.25779 | 61.4684 | -0.033101 | 0.043657 | 61.7127 | -0.001436 | 61.5 | 64.9142 | 64.8117 | 65.1377 | 63.8426 | 62.3792 | 62.1538 | 62.8433 | 123.1338 | 61.8499 | 123.0605 | 61.559 | 61.6358 | 123.3048 | 61.5907 | 123.0921 | 61.498 | 61.5431 | 61.4247 | 61.4698
3741.0781 | 123.4085 | -61.5646 | 61.5234 | 3.2489 | 3.1463 | 3.3853 | 2.2047 | 0.73669 | 0.59836 | 1.1963 | 61.5417 | 0.26237 | 61.4546 | -0.033101 | 0.048236 | 61.7172 | -0.001436 | 61.5046 | 64.8135 | 64.711 | 64.95 | 63.7693 | 62.3013 | 62.163 | 62.7609 | 123.1063 | 61.827 | 123.0193 | 61.5315 | 61.6129 | 123.2819 | 61.5632 | 123.0692 | 61.4934 | 61.5431 | 61.4064 | 61.4561
3742.0625 | 123.3078 | -61.615 | 61.5738 | 3.1711 | 3.0731 | 3.2938 | 2.2551 | 0.76874 | 0.51137 | 1.2329 | 61.5463 | 0.26237 | 61.4821 | -0.028522 | 0.043657 | 61.7127 | 0.007721 | 61.5046 | 64.786 | 64.6881 | 64.9087 | 63.8701 | 62.3837 | 62.1264 | 62.8479 | 123.1612 | 61.8774 | 123.0971 | 61.5865 | 61.6586 | 123.3276 | 61.6227 | 123.1196 | 61.5026 | 61.5385 | 61.4384 | 61.4744
3743.0938 | 123.3948 | -61.5875 | 61.5463 | 3.1711 | 3.0685 | 3.2205 | 2.2368 | 0.755 | 0.4839 | 1.2283 | 61.5554 | 0.25779 | 61.4912 | -0.03768 | 0.043657 | 61.7127 | 0.003143 | 61.4909 | 64.7586 | 64.656 | 64.808 | 63.8243 | 62.3425 | 62.0714 | 62.8159 | 123.1429 | 61.8453 | 123.0788 | 61.5498 | 61.6312 | 123.3002 | 61.5907 | 123.0784 | 61.5118 | 61.5523 | 61.4476 | 61.4881
3744.0625 | 123.381 | -61.5692 | 61.5326 | 3.0291 | 2.9357 | 3.2205 | 2.2276 | 0.73211 | 0.47475 | 1.2558 | 61.5508 | 0.25779 | 61.4729 | -0.03768 | 0.052814 | 61.7127 | 0.003143 | 61.4909 | 64.5983 | 64.5049 | 64.7897 | 63.7968 | 62.3013 | 62.044 | 62.825 | 123.12 | 61.827 | 123.0421 | 61.5315 | 61.622 | 123.2819 | 61.5724 | 123.0601 | 61.498 | 61.5477 | 61.4201 | 61.4698
3745.0781 | 123.4222 | -61.5784 | 61.5189 | 3.107 | 3.0135 | 3.2388 | 2.2505 | 0.755 | 0.60294 | 1.2375 | 61.5508 | 0.25779 | 61.4546 | -0.03768 | 0.043657 | 61.7127 | 0.003143 | 61.4863 | 64.6853 | 64.5919 | 64.8172 | 63.8289 | 62.3334 | 62.1813 | 62.8159 | 123.1292 | 61.8362 | 123.033 | 61.5407 | 61.622 | 123.291 | 61.5815 | 123.0646 | 61.5072 | 61.5477 | 61.411 | 61.4515
3746.0625 | 123.2803 | -61.5967 | 61.5601 | 3.139 | 3.0364 | 3.4311 | 2.2413 | 0.75043 | 0.64415 | 1.3519 | 61.5417 | 0.25321 | 61.4775 | -0.03768 | 0.043657 | 61.7218 | 0.003143 | 61.4954 | 64.7357 | 64.6331 | 65.0278 | 63.838 | 62.3471 | 62.2408 | 62.9486 | 123.1384 | 61.8499 | 123.0742 | 61.559 | 61.6403 | 123.3185 | 61.5998 | 123.0921 | 61.498 | 61.5385 | 61.4339 | 61.4744
3747.0938 | 123.3856 | -61.6058 | 61.5326 | 3.1207 | 3.0181 | 3.4952 | 2.2322 | 0.75043 | 0.70366 | 1.4023 | 61.5463 | 0.25321 | 61.4867 | -0.033101 | 0.048236 | 61.7172 | 0.007721 | 61.5 | 64.7265 | 64.624 | 65.101 | 63.838 | 62.3563 | 62.3095 | 63.0081 | 123.1521 | 61.859 | 123.0925 | 61.5727 | 61.6541 | 123.3231 | 61.6136 | 123.1058 | 61.498 | 61.5385 | 61.4384 | 61.4789
3748.0625 | 123.2483 | -61.6241 | 61.5646 | 3.139 | 3.0364 | 3.3075 | 2.2047 | 0.74127 | 0.67162 | 1.4252 | 61.5463 | 0.26237 | 61.4775 | -0.033101 | 0.048236 | 61.7127 | 0.012299 | 61.4863 | 64.7632 | 64.6606 | 64.9316 | 63.8289 | 62.3654 | 62.2958 | 63.0493 | 123.1704 | 61.8865 | 123.1017 | 61.591 | 61.6724 | 123.3368 | 61.6364 | 123.1104 | 61.498 | 61.534 | 61.4293 | 61.4652
3749.0938 | 123.3627 | -61.5875 | 61.528 | 3.1527 | 3.0364 | 3.3258 | 2.2184 | 0.71838 | 0.63041 | 1.4115 | 61.5463 | 0.26695 | 61.45 | -0.033101 | 0.048236 | 61.7172 | 0.007721 | 61.4909 | 64.7403 | 64.624 | 64.9133 | 63.806 | 62.3059 | 62.2179 | 62.999 | 123.1338 | 61.8545 | 123.0376 | 61.5544 | 61.6358 | 123.3048 | 61.5952 | 123.0784 | 61.498 | 61.5385 | 61.4018 | 61.4423
3750.0625 | 123.3032 | -61.6104 | 61.5646 | 3.1848 | 3.096 | 3.1243 | 2.1543 | 0.70465 | 0.6121 | 1.4618 | 61.5554 | 0.25779 | 61.4821 | -0.028522 | 0.048236 | 61.7218 | 0.007721 | 61.4909 | 64.7952 | 64.7064 | 64.7348 | 63.7648 | 62.3151 | 62.2225 | 63.0722 | 123.1658 | 61.8682 | 123.0925 | 61.5819 | 61.6586 | 123.3322 | 61.6181 | 123.1013 | 61.5072 | 61.5477 | 61.4339 | 61.4744
3751.0781 | 123.4268 | -61.5738 | 61.5097 | 3.2031 | 3.1051 | 3.2251 | 2.1772 | 0.7138 | 0.61668 | 1.4481 | 61.5554 | 0.26237 | 61.4912 | -0.033101 | 0.048236 | 61.7218 | 0.003143 | 61.4909 | 64.7769 | 64.6789 | 64.7989 | 63.751 | 62.2876 | 62.1905 | 63.0219 | 123.1292 | 61.8362 | 123.065 | 61.5407 | 61.622 | 123.2956 | 61.5769 | 123.0646 | 61.5072 | 61.5523 | 61.443 | 61.4881
3752.0625 | 123.3582 | -61.6013 | 61.4914 | 3.2306 | 3.1234 | 3.1793 | 2.2093 | 0.74585 | 0.6121 | 1.4801 | 61.5463 | 0.26237 | 61.4729 | -0.028522 | 0.039079 | 61.7218 | -0.001436 | 61.4863 | 64.8318 | 64.7247 | 64.7805 | 63.8105 | 62.3471 | 62.2134 | 63.0814 | 123.1475 | 61.8636 | 123.0742 | 61.5727 | 61.6403 | 123.3231 | 61.5998 | 123.0875 | 61.5072 | 61.5477 | 61.4339 | 61.4744
3753.0938 | 123.4039 | -61.5692 | 61.5143 | 3.2809 | 3.183 | 3.2571 | 2.2688 | 0.76416 | 0.52969 | 1.5259 | 61.5417 | 0.25779 | 61.4592 | -0.03768 | 0.043657 | 61.7218 | -0.001436 | 61.4954 | 64.8502 | 64.7522 | 64.8263 | 63.838 | 62.3334 | 62.0989 | 63.0951 | 123.1109 | 61.827 | 123.0284 | 61.5315 | 61.6129 | 123.291 | 61.5678 | 123.0646 | 61.498 | 61.5431 | 61.4155 | 61.4606
3754.0625 | 123.2941 | -61.615 | 61.5646 | 3.3405 | 3.2379 | 3.3533 | 2.278 | 0.76874 | 0.6533 | 1.5671 | 61.5417 | 0.25779 | 61.4684 | -0.033101 | 0.048236 | 61.731 | 0.007721 | 61.5092 | 64.9554 | 64.8529 | 64.9683 | 63.893 | 62.3837 | 62.2683 | 63.1821 | 123.1567 | 61.8728 | 123.0833 | 61.5819 | 61.6632 | 123.346 | 61.6227 | 123.1242 | 61.4934 | 61.534 | 61.4201 | 61.4606
3755.0938 | 123.2895 | -61.6196 | 61.5601 | 3.2993 | 3.2059 | 3.4128 | 2.3054 | 0.8191 | 0.67162 | 1.5671 | 61.5508 | 0.25779 | 61.4821 | -0.03768 | 0.052814 | 61.7172 | 0.003143 | 61.4954 | 64.9188 | 64.8254 | 65.0324 | 63.925 | 62.4387 | 62.2912 | 63.1867 | 123.1704 | 61.8774 | 123.1017 | 61.5819 | 61.6724 | 123.3368 | 61.6227 | 123.115 | 61.498 | 61.5477 | 61.4293 | 61.4789
3756.0625 | 123.2666 | -61.615 | 61.5784 | 3.2901 | 3.1921 | 3.3395 | 2.278 | 0.80994 | 0.64415 | 1.5351 | 61.5508 | 0.25779 | 61.4867 | -0.028522 | 0.048236 | 61.7218 | 0.007721 | 61.4954 | 64.9051 | 64.8071 | 64.9545 | 63.893 | 62.4249 | 62.2591 | 63.1501 | 123.1658 | 61.8728 | 123.1017 | 61.5865 | 61.6632 | 123.3368 | 61.6227 | 123.1104 | 61.5026 | 61.5431 | 61.4384 | 61.4789
3757.0938 | 123.2758 | -61.6745 | 61.5417 | 3.2901 | 3.1967 | 3.4677 | 2.2734 | 0.80994 | 0.64872 | 1.4664 | 61.5417 | 0.26237 | 61.4821 | -0.03768 | 0.043657 | 61.7218 | 0.003143 | 61.4954 | 64.9646 | 64.8712 | 65.1422 | 63.9479 | 62.4844 | 62.3232 | 63.1409 | 123.2162 | 61.9369 | 123.1566 | 61.6368 | 61.7182 | 123.3963 | 61.6776 | 123.1699 | 61.498 | 61.5385 | 61.4384 | 61.4789
3758.0625 | 123.4222 | -61.5784 | 61.528 | 3.3267 | 3.2196 | 3.2892 | 2.2551 | 0.79621 | 0.65788 | 1.4572 | 61.5417 | 0.26237 | 61.4455 | -0.033101 | 0.043657 | 61.7218 | 0.007721 | 61.4954 | 64.9051 | 64.798 | 64.8675 | 63.8334 | 62.3746 | 62.2363 | 63.0356 | 123.12 | 61.8407 | 123.0238 | 61.5453 | 61.622 | 123.3002 | 61.5861 | 123.0738 | 61.498 | 61.534 | 61.4018 | 61.4377
3759.0938 | 123.4085 | -61.5509 | 61.5051 | 3.3542 | 3.2471 | 2.8725 | 2.3054 | 0.80536 | 0.64415 | 1.5076 | 61.5417 | 0.25321 | 61.45 | -0.03768 | 0.039079 | 61.7172 | -0.001436 | 61.4863 | 64.9051 | 64.798 | 64.4234 | 63.8563 | 62.3563 | 62.195 | 63.0585 | 123.0926 | 61.8041 | 123.0009 | 61.5132 | 61.59 | 123.2681 | 61.5495 | 123.0372 | 61.5026 | 61.5431 | 61.411 | 61.4515
3760.0625 | 123.3398 | -61.5829 | 61.5509 | 3.3908 | 3.2883 | 3.074 | 2.3238 | 0.80536 | 0.65788 | 1.503 | 61.5463 | 0.26237 | 61.4592 | -0.033101 | 0.043657 | 61.7218 | -0.001436 | 61.4909 | 64.9738 | 64.8712 | 64.6569 | 63.9067 | 62.3883 | 62.2408 | 63.086 | 123.1292 | 61.8453 | 123.0421 | 61.5498 | 61.6266 | 123.3048 | 61.5815 | 123.0738 | 61.5026 | 61.5477 | 61.4155 | 61.4606
3761.0938 | 123.4406 | -61.5875 | 61.5326 | 3.4137 | 3.3066 | 3.4952 | 2.3009 | 0.82367 | 0.68077 | 1.4984 | 61.5417 | 0.26695 | 61.4729 | -0.028522 | 0.048236 | 61.731 | 0.003143 | 61.5 | 65.0012 | 64.8941 | 65.0827 | 63.8884 | 62.4112 | 62.2683 | 63.086 | 123.1292 | 61.8545 | 123.0605 | 61.559 | 61.6358 | 123.3185 | 61.5907 | 123.0875 | 61.4934 | 61.5385 | 61.4247 | 61.4698
3762.0625 | 123.3627 | -61.6241 | 61.4914 | 3.4229 | 3.3203 | 3.3762 | 2.2505 | 0.75958 | 0.63041 | 1.4206 | 61.5417 | 0.26237 | 61.4775 | -0.028522 | 0.043657 | 61.7172 | 0.007721 | 61.4954 | 65.047 | 64.9445 | 65.0003 | 63.8746 | 62.3837 | 62.2546 | 63.0448 | 123.1658 | 61.8865 | 123.1017 | 61.5956 | 61.6678 | 123.3414 | 61.6319 | 123.1196 | 61.498 | 61.534 | 61.4339 | 61.4698
3763.0938 | 123.349 | -61.5967 | 61.5097 | 3.3634 | 3.2745 | 3.3029 | 2.1864 | 0.7138 | 0.54342 | 1.2741 | 61.5417 | 0.26237 | 61.4592 | -0.033101 | 0.043657 | 61.7172 | 0.003143 | 61.4863 | 64.96 | 64.8712 | 64.8996 | 63.7831 | 62.3105 | 62.1401 | 62.8708 | 123.1384 | 61.859 | 123.0559 | 61.5636 | 61.6403 | 123.3139 | 61.5998 | 123.083 | 61.498 | 61.5385 | 61.4155 | 61.4561
3764.0625 | 123.2849 | -61.6196 | 61.5509 | 3.3634 | 3.27 | 3.4632 | 2.2276 | 0.73211 | 0.52969 | 1.2329 | 61.5463 | 0.26237 | 61.4546 | -0.028522 | 0.043657 | 61.7172 | 0.003143 | 61.5 | 64.9829 | 64.8895 | 65.0827 | 63.8472 | 62.3517 | 62.1493 | 62.8525 | 123.1658 | 61.8819 | 123.0742 | 61.591 | 61.6632 | 123.3368 | 61.6227 | 123.1196 | 61.5026 | 61.5431 | 61.411 | 61.4515
3765.0938 | 123.2712 | -61.6104 | 61.5601 | 3.3313 | 3.2288 | 3.3762 | 2.2047 | 0.70922 | 0.50679 | 1.1917 | 61.5554 | 0.25321 | 61.4867 | -0.033101 | 0.052814 | 61.7081 | 0.007721 | 61.4909 | 64.9417 | 64.8392 | 64.9866 | 63.8151 | 62.3196 | 62.1172 | 62.8021 | 123.1658 | 61.8636 | 123.0971 | 61.5773 | 61.6632 | 123.3185 | 61.6181 | 123.1013 | 61.5026 | 61.5477 | 61.4339 | 61.4789
3766.0625 | 123.2712 | -61.6058 | 61.5784 | 3.3313 | 3.2333 | 3.335 | 2.1498 | 0.69091 | 0.50679 | 1.2375 | 61.5508 | 0.25779 | 61.4912 | -0.033101 | 0.048236 | 61.7218 | 0.003143 | 61.4954 | 64.9371 | 64.8392 | 64.9408 | 63.7556 | 62.2967 | 62.1126 | 62.8433 | 123.1567 | 61.8636 | 123.0971 | 61.5727 | 61.6541 | 123.3276 | 61.609 | 123.1013 | 61.5026 | 61.5477 | 61.443 | 61.4881
3767.1094 | 123.3536 | -61.6196 | 61.5555 | 3.3084 | 3.2104 | 3.1701 | 2.1177 | 0.7138 | 0.52511 | 1.1963 | 61.5463 | 0.26695 | 61.4638 | -0.03768 | 0.043657 | 61.7127 | -0.006014 | 61.4954 | 64.928 | 64.83 | 64.7897 | 63.7373 | 62.3334 | 62.1447 | 62.8158 | 123.1658 | 61.8865 | 123.0833 | 61.5819 | 61.6632 | 123.3322 | 61.6136 | 123.115 | 61.5026 | 61.5523 | 61.4201 | 61.4698
3768.0625 | 123.3994 | -61.5829 | 61.5463 | 3.313 | 3.2196 | 3.0831 | 2.1543 | 0.67718 | 0.53426 | 1.1963 | 61.5417 | 0.25779 | 61.4638 | -0.03768 | 0.039079 | 61.7127 | 0.003143 | 61.4909 | 64.8959 | 64.8025 | 64.6661 | 63.7373 | 62.2601 | 62.1172 | 62.7792 | 123.1246 | 61.8407 | 123.0467 | 61.5453 | 61.622 | 123.2956 | 61.5861 | 123.0738 | 61.5026 | 61.5385 | 61.4247 | 61.4606
3769.0781 | 123.4085 | -61.6104 | 61.5326 | 3.2901 | 3.1967 | 3.0969 | 2.1727 | 0.66344 | 0.48848 | 1.1871 | 61.56 | 0.26695 | 61.4867 | -0.033101 | 0.043657 | 61.7081 | 0.007721 | 61.4817 | 64.9005 | 64.8071 | 64.7073 | 63.7831 | 62.2739 | 62.0989 | 62.7975 | 123.1704 | 61.8774 | 123.0971 | 61.5773 | 61.6541 | 123.3185 | 61.6181 | 123.0921 | 61.5163 | 61.5523 | 61.443 | 61.4789
3770.0625 | 123.2895 | -61.6104 | 61.5372 | 3.2947 | 3.1921 | 3.1381 | 2.1864 | 0.65429 | 0.46559 | 1.2329 | 61.5508 | 0.26237 | 61.4775 | -0.03768 | 0.039079 | 61.7081 | 0.003143 | 61.4863 | 64.9051 | 64.8025 | 64.7485 | 63.7968 | 62.2647 | 62.076 | 62.8433 | 123.1612 | 61.8728 | 123.0879 | 61.5727 | 61.6495 | 123.3185 | 61.6136 | 123.0967 | 61.5118 | 61.5477 | 61.4384 | 61.4744
3771.0625 | 123.3078 | -61.615 | 61.5692 | 3.3084 | 3.2013 | 3.3991 | 2.1269 | 0.64513 | 0.46559 | 1.2283 | 61.5508 | 0.25779 | 61.4638 | -0.033101 | 0.048236 | 61.7172 | 0.007721 | 61.5 | 64.9234 | 64.8163 | 65.014 | 63.7419 | 62.2601 | 62.0806 | 62.8433 | 123.1658 | 61.8728 | 123.0788 | 61.5819 | 61.6632 | 123.3322 | 61.6227 | 123.115 | 61.5026 | 61.5431 | 61.4155 | 61.4561
3772.0938 | 123.3398 | -61.6104 | 61.5326 | 3.2901 | 3.183 | 3.28 | 2.2139 | 0.67718 | 0.4839 | 1.265 | 61.5554 | 0.26237 | 61.4912 | -0.033101 | 0.043657 | 61.7218 | 0.003143 | 61.4909 | 64.9005 | 64.7934 | 64.8904 | 63.8243 | 62.2876 | 62.0943 | 62.8754 | 123.1658 | 61.8728 | 123.1017 | 61.5773 | 61.6541 | 123.3322 | 61.6136 | 123.1013 | 61.5118 | 61.5523 | 61.4476 | 61.4881
3773.0625 | 123.2986 | -61.6196 | 61.5738 | 3.3038 | 3.1967 | 3.454 | 2.2642 | 0.70007 | 0.53426 | 1.2695 | 61.5371 | 0.25779 | 61.4729 | -0.03768 | 0.039079 | 61.7172 | 0.003143 | 61.5 | 64.9234 | 64.8163 | 65.0736 | 63.8838 | 62.3196 | 62.1538 | 62.8891 | 123.1567 | 61.8774 | 123.0925 | 61.5819 | 61.6586 | 123.3368 | 61.6227 | 123.1196 | 61.498 | 61.534 | 61.4339 | 61.4698
3774.0938 | 123.2758 | -61.6058 | 61.5738 | 3.3221 | 3.2196 | 3.193 | 2.2597 | 0.70465 | 0.53884 | 1.2695 | 61.5417 | 0.26237 | 61.4729 | -0.033101 | 0.039079 | 61.7218 | 0.007721 | 61.5046 | 64.928 | 64.8254 | 64.7989 | 63.8655 | 62.3105 | 62.1447 | 62.8754 | 123.1475 | 61.8682 | 123.0788 | 61.5727 | 61.6449 | 123.3276 | 61.6136 | 123.1104 | 61.5026 | 61.534 | 61.4339 | 61.4652
3775.0625 | 123.2941 | -61.6333 | 61.5555 | 3.3176 | 3.2196 | 3.3716 | 2.2963 | 0.70007 | 0.4839 | 1.329 | 61.5508 | 0.26237 | 61.4867 | -0.033101 | 0.043657 | 61.7172 | 0.003143 | 61.5092 | 64.9509 | 64.8529 | 65.0049 | 63.9296 | 62.3334 | 62.1172 | 62.9623 | 123.1841 | 61.8957 | 123.12 | 61.6002 | 61.677 | 123.3505 | 61.6364 | 123.1425 | 61.5072 | 61.5477 | 61.443 | 61.4835
3776.0781 | 123.4222 | -61.5875 | 61.528 | 3.2947 | 3.1967 | 3.248 | 2.2551 | 0.70922 | 0.4839 | 1.2833 | 61.5463 | 0.26237 | 61.4684 | -0.033101 | 0.048236 | 61.7172 | 0.003143 | 61.5046 | 64.8822 | 64.7842 | 64.8355 | 63.8426 | 62.2967 | 62.0714 | 62.8708 | 123.1338 | 61.8499 | 123.0559 | 61.5544 | 61.6358 | 123.3048 | 61.5907 | 123.0921 | 61.498 | 61.5431 | 61.4201 | 61.4652
3777.0625 | 123.3353 | -61.6013 | 61.5417 | 3.3038 | 3.2059 | 3.5181 | 2.2368 | 0.68176 | 0.47932 | 1.21 | 61.5463 | 0.26237 | 61.4684 | -0.033101 | 0.048236 | 61.7218 | 0.012299 | 61.5 | 64.9051 | 64.8071 | 65.1194 | 63.838 | 62.283 | 62.0806 | 62.8113 | 123.1475 | 61.8636 | 123.0696 | 61.5682 | 61.6495 | 123.3231 | 61.6136 | 123.1013 | 61.498 | 61.534 | 61.4201 | 61.4561
3778.0781 | 123.4589 | -61.5692 | 61.5097 | 3.2809 | 3.1692 | 3.1564 | 2.2505 | 0.64055 | 0.49764 | 1.2146 | 61.56 | 0.25321 | 61.4867 | -0.033101 | 0.043657 | 61.7218 | 0.007721 | 61.4909 | 64.8502 | 64.7384 | 64.7256 | 63.8197 | 62.2098 | 62.0669 | 62.7838 | 123.1292 | 61.8224 | 123.0559 | 61.5361 | 61.6129 | 123.291 | 61.5769 | 123.0601 | 61.5163 | 61.5523 | 61.443 | 61.4789
3779.0625 | 123.3627 | -61.6104 | 61.5738 | 3.3542 | 3.2471 | 3.2205 | 2.1956 | 0.59478 | 0.45185 | 1.3245 | 61.5463 | 0.25779 | 61.4821 | -0.028522 | 0.043657 | 61.7172 | 0.007721 | 61.5 | 64.9646 | 64.8575 | 64.8309 | 63.806 | 62.2052 | 62.0623 | 62.9349 | 123.1567 | 61.8682 | 123.0925 | 61.5819 | 61.6541 | 123.3276 | 61.6181 | 123.1104 | 61.5026 | 61.5385 | 61.4384 | 61.4744
3780.1094 | 123.3398 | -61.5784 | 61.5646 | 3.2123 | 3.1097 | 3.1198 | 2.1727 | 0.58562 | 0.53426 | 1.3474 | 61.5554 | 0.26695 | 61.4684 | -0.03768 | 0.039079 | 61.7172 | 0.003143 | 61.4909 | 64.7906 | 64.6881 | 64.6981 | 63.751 | 62.164 | 62.1126 | 62.9257 | 123.1338 | 61.8453 | 123.0467 | 61.5407 | 61.6174 | 123.2956 | 61.5815 | 123.0692 | 61.5163 | 61.5523 | 61.4293 | 61.4652
3781.0625 | 123.349 | -61.5829 | 61.5692 | 3.1665 | 3.0777 | 3.0373 | 2.2825 | 0.63598 | 0.59836 | 1.3657 | 61.56 | 0.26237 | 61.4912 | -0.028522 | 0.043657 | 61.7081 | -0.006014 | 61.4954 | 64.7494 | 64.6606 | 64.6203 | 63.8655 | 62.2189 | 62.1813 | 62.9486 | 123.1429 | 61.8453 | 123.0742 | 61.5544 | 61.6266 | 123.291 | 61.5769 | 123.0784 | 61.5163 | 61.566 | 61.4476 | 61.4973
3782.0938 | 123.3948 | -61.5784 | 61.5234 | 3.1344 | 3.0319 | 2.7443 | 2.3329 | 0.6726 | 0.57547 | 1.3565 | 61.5463 | 0.26237 | 61.45 | -0.033101 | 0.039079 | 61.7127 | 0.003143 | 61.4863 | 64.7128 | 64.6102 | 64.3227 | 63.9113 | 62.251 | 62.1538 | 62.9349 | 123.1246 | 61.8407 | 123.0284 | 61.5453 | 61.6174 | 123.291 | 61.5815 | 123.0646 | 61.5072 | 61.5431 | 61.411 | 61.4469
3783.0625 | 123.2849 | -61.615 | 61.5417 | 3.2077 | 3.1005 | 2.8863 | 2.31 | 0.62224 | 0.42438 | 1.3794 | 61.56 | 0.27611 | 61.4958 | -0.03768 | 0.043657 | 61.7218 | 0.003143 | 61.5 | 64.8227 | 64.7155 | 64.5012 | 63.925 | 62.2372 | 62.0394 | 62.9944 | 123.175 | 61.8911 | 123.1108 | 61.5773 | 61.6586 | 123.3368 | 61.6181 | 123.115 | 61.5163 | 61.5568 | 61.4522 | 61.4927
3784.0938 | 123.349 | -61.6013 | 61.528 | 3.258 | 3.1601 | 2.8359 | 2.2688 | 0.63598 | 0.39233 | 1.3931 | 61.5508 | 0.26237 | 61.4729 | -0.028522 | 0.048236 | 61.7127 | 0.003143 | 61.4954 | 64.8593 | 64.7613 | 64.4371 | 63.8701 | 62.2372 | 61.9936 | 62.9944 | 123.1521 | 61.8636 | 123.0742 | 61.5727 | 61.6495 | 123.3139 | 61.6044 | 123.0967 | 61.5026 | 61.5477 | 61.4247 | 61.4698
3785.0625 | 123.4406 | -61.5967 | 61.5326 | 3.1802 | 3.0731 | 2.8405 | 2.1956 | 0.59935 | 0.42896 | 1.3657 | 61.5417 | 0.25779 | 61.4684 | -0.028522 | 0.043657 | 61.7127 | 0.003143 | 61.4954 | 64.7769 | 64.6698 | 64.4372 | 63.7922 | 62.196 | 62.0256 | 62.9624 | 123.1384 | 61.8545 | 123.065 | 61.5682 | 61.6403 | 123.3093 | 61.5998 | 123.0921 | 61.498 | 61.5385 | 61.4247 | 61.4652
3786.0781 | 123.317 | -61.5967 | 61.5601 | 3.0795 | 2.9769 | 2.9595 | 2.2368 | 0.57646 | 0.43354 | 1.4252 | 61.5646 | 0.26237 | 61.4912 | -0.03768 | 0.048236 | 61.7127 | 0.003143 | 61.4909 | 64.6762 | 64.5736 | 64.5562 | 63.8334 | 62.1731 | 62.0302 | 63.0219 | 123.1613 | 61.859 | 123.0879 | 61.559 | 61.6449 | 123.3093 | 61.5998 | 123.0875 | 61.5163 | 61.5614 | 61.443 | 61.4881
3787.0625 | 123.3902 | -61.6013 | 61.5051 | 3.0245 | 2.9357 | 3.0831 | 2.2642 | 0.64055 | 0.40149 | 1.4481 | 61.5508 | 0.25779 | 61.4729 | -0.03768 | 0.043657 | 61.7127 | -0.001436 | 61.5092 | 64.6258 | 64.537 | 64.6844 | 63.8655 | 62.2418 | 62.0027 | 63.0493 | 123.1521 | 61.859 | 123.0742 | 61.5636 | 61.6449 | 123.3139 | 61.5998 | 123.1104 | 61.5072 | 61.5523 | 61.4293 | 61.4744
3788.1094 | 123.4451 | -61.5646 | 61.5326 | 3.1207 | 3.0181 | 3.5181 | 2.2597 | 0.63598 | 0.45643 | 1.384 | 61.5508 | 0.26237 | 61.4684 | -0.03768 | 0.043657 | 61.7127 | 0.012299 | 61.5046 | 64.6853 | 64.5828 | 65.0827 | 63.8243 | 62.2006 | 62.0211 | 62.9486 | 123.1155 | 61.827 | 123.033 | 61.527 | 61.6083 | 123.2773 | 61.5769 | 123.0692 | 61.5072 | 61.5385 | 61.4247 | 61.4561
3789.0625 | 123.4039 | -61.6058 | 61.5005 | 3.107 | 2.9998 | 3.5776 | 2.1727 | 0.61309 | 0.50222 | 1.297 | 61.5554 | 0.26237 | 61.4867 | -0.033101 | 0.039079 | 61.7172 | -0.001436 | 61.5046 | 64.7128 | 64.6056 | 65.1835 | 63.7785 | 62.2189 | 62.1081 | 62.9028 | 123.1612 | 61.8682 | 123.0925 | 61.5727 | 61.6449 | 123.3231 | 61.6044 | 123.1104 | 61.5163 | 61.5568 | 61.4476 | 61.4881
3790.0938 | 123.2803 | -61.6562 | 61.5555 | 3.0474 | 2.954 | 3.4861 | 2.1772 | 0.60393 | 0.51595 | 1.3245 | 61.5463 | 0.26237 | 61.4821 | -0.03768 | 0.039079 | 61.7172 | -0.006014 | 61.5 | 64.7036 | 64.6102 | 65.1422 | 63.8334 | 62.2601 | 62.1721 | 62.9807 | 123.2024 | 61.9186 | 123.1383 | 61.6185 | 61.6953 | 123.3734 | 61.6502 | 123.1562 | 61.5072 | 61.5523 | 61.443 | 61.4881
3791.0625 | 123.4543 | -61.6241 | 61.4548 | 1.4679 | 4.0346 | 3.4357 | 2.2505 | 0.61309 | 0.47475 | 1.3794 | 61.5508 | 0.26695 | 61.4775 | -0.03768 | 0.048236 | 61.7081 | 0.007721 | 61.4863 | 63.092 | 65.6588 | 65.0598 | 63.8746 | 62.2372 | 62.0989 | 63.0036 | 123.175 | 61.8911 | 123.1017 | 61.5865 | 61.6724 | 123.3322 | 61.6319 | 123.1104 | 61.5026 | 61.5431 | 61.4293 | 61.4698
3792.0938 | 123.349 | -61.5921 | 61.5509 | 1.3443 | 4.03 | 3.0831 | 2.2001 | 0.56273 | 0.43354 | 1.3931 | 61.5737 | 0.25779 | 61.5004 | -0.028522 | 0.039079 | 61.7035 | 0.003143 | 61.4909 | 62.9364 | 65.6221 | 64.6752 | 63.7922 | 62.1548 | 62.0256 | 62.9852 | 123.1658 | 61.8499 | 123.0925 | 61.5636 | 61.6312 | 123.2956 | 61.5952 | 123.083 | 61.5346 | 61.5706 | 61.4613 | 61.4973
3793.0625 | 123.4177 | -61.5829 | 61.5097 | 1.326 | 4.0804 | 3.2709 | 2.2001 | 0.56273 | 0.42896 | 1.4252 | 61.5508 | 0.26695 | 61.4592 | -0.033101 | 0.039079 | 61.7127 | 0.003143 | 61.4863 | 62.9089 | 65.6634 | 64.8538 | 63.7831 | 62.1457 | 62.0119 | 63.0081 | 123.1338 | 61.8499 | 123.0421 | 61.5498 | 61.622 | 123.2956 | 61.5861 | 123.0692 | 61.5118 | 61.5477 | 61.4201 | 61.4561
3794.0938 | 123.3948 | -61.6104 | 61.4914 | 1.3214 | 4.0713 | 3.4265 | 2.1956 | 0.54442 | 0.30992 | 1.4298 | 61.5554 | 0.26237 | 61.5004 | -0.033101 | 0.043657 | 61.7127 | -0.001436 | 61.4817 | 62.9318 | 65.6817 | 65.0369 | 63.806 | 62.1548 | 61.9203 | 63.0402 | 123.1658 | 61.8728 | 123.1108 | 61.5773 | 61.6541 | 123.3231 | 61.609 | 123.0921 | 61.5118 | 61.5568 | 61.4567 | 61.5018
3795.0625 | 123.3719 | -61.5967 | 61.4868 | 1.2985 | 4.2407 | 3.5044 | 2.1818 | 0.53068 | 0.36944 | 1.4481 | 61.5554 | 0.26695 | 61.4867 | -0.03768 | 0.039079 | 61.7081 | -0.001436 | 61.4909 | 62.8952 | 65.8374 | 65.101 | 63.7785 | 62.1274 | 61.9661 | 63.0448 | 123.1521 | 61.8636 | 123.0833 | 61.559 | 61.6358 | 123.3048 | 61.5952 | 123.0875 | 61.5163 | 61.5568 | 61.4476 | 61.4881
3796.1094 | 123.3673 | -61.5875 | 61.5463 | 1.3397 | 4.2086 | 3.4815 | 2.1956 | 0.56273 | 0.4198 | 1.4801 | 61.5554 | 0.26237 | 61.4638 | -0.033101 | 0.048236 | 61.7081 | 0.003143 | 61.4909 | 62.9272 | 65.7961 | 65.069 | 63.7831 | 62.1503 | 62.0073 | 63.0677 | 123.1429 | 61.8499 | 123.0513 | 61.5544 | 61.6358 | 123.2956 | 61.5907 | 123.0784 | 61.5072 | 61.5523 | 61.4155 | 61.4606
3797.0625 | 123.3261 | -61.6241 | 61.5234 | 1.4267 | 4.1903 | 3.6188 | 2.2322 | 0.55357 | 0.34197 | 1.4389 | 61.5554 | 0.27153 | 61.4912 | -0.033101 | 0.039079 | 61.7081 | 0.003143 | 61.4817 | 63.0508 | 65.8145 | 65.243 | 63.8563 | 62.1777 | 61.9661 | 63.0631 | 123.1796 | 61.8957 | 123.1154 | 61.591 | 61.6632 | 123.3322 | 61.6273 | 123.1058 | 61.5163 | 61.5523 | 61.4522 | 61.4881
3798.0938 | 123.4039 | -61.5646 | 61.5143 | 3.1344 | 3.0273 | 3.4998 | 2.2871 | 0.57189 | 0.42438 | 1.1825 | 61.5554 | 0.26237 | 61.4867 | -0.028522 | 0.039079 | 61.7127 | 0.003143 | 61.4817 | 64.6991 | 64.5919 | 65.0644 | 63.8518 | 62.1365 | 61.989 | 62.7472 | 123.12 | 61.827 | 123.0513 | 61.5361 | 61.6037 | 123.2773 | 61.5678 | 123.0463 | 61.5163 | 61.5523 | 61.4476 | 61.4835
3799.0625 | 123.3994 | -61.6104 | 61.5189 | 3.1207 | 3.041 | 3.6097 | 2.2551 | 0.55815 | 0.41523 | 1.2833 | 61.5463 | 0.25779 | 61.4638 | -0.028522 | 0.043657 | 61.7081 | -0.001436 | 61.4954 | 64.7311 | 64.6514 | 65.2201 | 63.8655 | 62.1686 | 62.0256 | 62.8937 | 123.1567 | 61.8682 | 123.0742 | 61.5819 | 61.6541 | 123.3185 | 61.609 | 123.1058 | 61.5026 | 61.5477 | 61.4201 | 61.4652
3800.0938 | 123.3902 | -61.6196 | 61.5005 | 3.1207 | 3.0135 | 3.4998 | 2.2597 | 0.56731 | 0.43354 | 1.3016 | 61.5508 | 0.25779 | 61.4912 | -0.033101 | 0.034501 | 61.7081 | 0.003143 | 61.4909 | 64.7403 | 64.6331 | 65.1194 | 63.8792 | 62.1869 | 62.0531 | 62.9211 | 123.1704 | 61.8774 | 123.1108 | 61.5865 | 61.6541 | 123.3276 | 61.6227 | 123.1104 | 61.5163 | 61.5477 | 61.4567 | 61.4881
3801.0625 | 123.3582 | -61.6058 | 61.4868 | 3.1665 | 3.0639 | 3.4403 | 2.3054 | 0.6314 | 0.41523 | 1.2604 | 61.5463 | 0.26695 | 61.4821 | -0.033101 | 0.039079 | 61.7127 | 0.007721 | 61.4909 | 64.7723 | 64.6698 | 65.0461 | 63.9113 | 62.2372 | 62.0211 | 62.8662 | 123.1521 | 61.8728 | 123.0879 | 61.5727 | 61.6449 | 123.3185 | 61.6136 | 123.0967 | 61.5072 | 61.5385 | 61.443 | 61.4744
3802.0938 | 123.3536 | -61.6241 | 61.4548 | 3.1527 | 3.0502 | 3.573 | 2.31 | 0.60851 | 0.43812 | 1.1368 | 61.5417 | 0.26695 | 61.4684 | -0.033101 | 0.039079 | 61.7172 | 0.003143 | 61.4909 | 64.7769 | 64.6743 | 65.1972 | 63.9342 | 62.2327 | 62.0623 | 62.7609 | 123.1658 | 61.8911 | 123.0925 | 61.591 | 61.6632 | 123.3414 | 61.6273 | 123.115 | 61.5026 | 61.5385 | 61.4293 | 61.4652
3803.0625 | 123.3398 | -61.5921 | 61.5234 | 3.1161 | 3.0135 | 3.4403 | 2.3558 | 0.62682 | 0.4198 | 1.3016 | 61.5554 | 0.26237 | 61.4912 | -0.03768 | 0.048236 | 61.7172 | 0.003143 | 61.4909 | 64.7082 | 64.6057 | 65.0324 | 63.9479 | 62.2189 | 62.0119 | 62.8937 | 123.1475 | 61.8545 | 123.0833 | 61.5544 | 61.6403 | 123.3093 | 61.5952 | 123.083 | 61.5072 | 61.5523 | 61.443 | 61.4881
3804.0625 | 123.3627 | -61.615 | 61.5189 | 3.1299 | 3.0273 | 3.5227 | 2.3421 | 0.61309 | 0.42438 | 1.0956 | 61.5508 | 0.26237 | 61.4729 | -0.028522 | 0.043657 | 61.7127 | 0.007721 | 61.4909 | 64.7448 | 64.6423 | 65.1377 | 63.9571 | 62.2281 | 62.0394 | 62.7106 | 123.1658 | 61.8774 | 123.0879 | 61.5865 | 61.6586 | 123.3276 | 61.6227 | 123.1058 | 61.5072 | 61.5431 | 61.4293 | 61.4652
3805.0938 | 123.3124 | -61.6241 | 61.5234 | 3.1619 | 3.0593 | 3.4815 | 2.3421 | 0.72296 | 0.42438 | 1.2695 | 61.5508 | 0.25779 | 61.4867 | -0.033101 | 0.043657 | 61.7127 | 0.003143 | 61.4863 | 64.786 | 64.6835 | 65.1056 | 63.9662 | 62.3471 | 62.0485 | 62.8937 | 123.175 | 61.8819 | 123.1108 | 61.591 | 61.6678 | 123.3368 | 61.6273 | 123.1104 | 61.5072 | 61.5477 | 61.443 | 61.4835
3806.0625 | 123.2758 | -61.6241 | 61.5784 | 3.1756 | 3.0593 | 3.6463 | 2.3787 | 0.76874 | 0.42896 | 1.0956 | 61.5463 | 0.26237 | 61.4821 | -0.033101 | 0.039079 | 61.7172 | 0.003143 | 61.4909 | 64.7998 | 64.6835 | 65.2704 | 64.0028 | 62.3929 | 62.0531 | 62.7197 | 123.1704 | 61.8865 | 123.1062 | 61.591 | 61.6632 | 123.3414 | 61.6273 | 123.115 | 61.5072 | 61.5431 | 61.443 | 61.4789
3807.0938 | 123.3719 | -61.6058 | 61.5051 | 3.1848 | 3.0914 | 3.802 | 2.4519 | 0.75958 | 0.45185 | 1.1276 | 61.5417 | 0.26695 | 61.4775 | -0.033101 | 0.043657 | 61.7218 | 0.003143 | 61.4863 | 64.7906 | 64.6972 | 65.4078 | 64.0578 | 62.3654 | 62.0577 | 62.7334 | 123.1475 | 61.8728 | 123.0833 | 61.5727 | 61.6495 | 123.3276 | 61.609 | 123.0921 | 61.498 | 61.5385 | 61.4339 | 61.4744
3808.0625 | 123.4039 | -61.615 | 61.5005 | 3.2397 | 3.1418 | 3.8249 | 2.4474 | 0.74127 | 0.48848 | 1.1413 | 61.5371 | 0.26237 | 61.4775 | -0.03768 | 0.048236 | 61.7218 | -0.001436 | 61.5092 | 64.8547 | 64.7567 | 65.4399 | 64.0624 | 62.3563 | 62.1035 | 62.7563 | 123.1521 | 61.8774 | 123.0925 | 61.5773 | 61.6632 | 123.3368 | 61.6136 | 123.1242 | 61.4889 | 61.5385 | 61.4293 | 61.4789
3809.1094 | 123.3215 | -61.6104 | 61.5829 | 3.1665 | 3.0868 | 3.6921 | 2.3741 | 0.70465 | 0.4427 | 0.96737 | 61.5463 | 0.25779 | 61.4821 | -0.033101 | 0.039079 | 61.7127 | 0.012299 | 61.5 | 64.7769 | 64.6972 | 65.3025 | 63.9845 | 62.3151 | 62.0531 | 62.5778 | 123.1567 | 61.8682 | 123.0925 | 61.5773 | 61.6495 | 123.3231 | 61.6227 | 123.1104 | 61.5072 | 61.534 | 61.443 | 61.4698
3810.0625 | 123.3994 | -61.5967 | 61.5051 | 3.1344 | 3.096 | 3.6692 | 2.3787 | 0.70922 | 0.43812 | 0.95822 | 61.5463 | 0.26237 | 61.4821 | -0.03768 | 0.039079 | 61.7172 | 0.007721 | 61.5092 | 64.7311 | 64.6926 | 65.2659 | 63.9754 | 62.3059 | 62.0348 | 62.5549 | 123.1429 | 61.859 | 123.0788 | 61.559 | 61.6358 | 123.3139 | 61.6044 | 123.1058 | 61.5072 | 61.5385 | 61.443 | 61.4744
3811.0781 | 123.2941 | -61.5921 | 61.5555 | 2.3195 | 3.6683 | 3.8157 | 2.365 | 0.68634 | 0.4427 | 0.99484 | 61.5508 | 0.25779 | 61.4729 | -0.03768 | 0.039079 | 61.7172 | 0.003143 | 61.5 | 63.9116 | 65.2604 | 65.4078 | 63.9571 | 62.2784 | 62.0348 | 62.5869 | 123.1429 | 61.8499 | 123.065 | 61.5544 | 61.6312 | 123.3093 | 61.5952 | 123.0921 | 61.5118 | 61.5477 | 61.4339 | 61.4698
3812.0625 | 123.3719 | -61.5875 | 61.5234 | 3.0474 | 2.9815 | 3.7333 | 2.2459 | 0.55815 | 0.38776 | 0.91243 | 61.5554 | 0.25779 | 61.4912 | -0.03768 | 0.048236 | 61.7172 | 0.003143 | 61.4954 | 64.635 | 64.569 | 65.3208 | 63.8334 | 62.1457 | 61.9753 | 62.5 | 123.1429 | 61.8453 | 123.0788 | 61.5498 | 61.6358 | 123.3048 | 61.5907 | 123.083 | 61.5072 | 61.5523 | 61.443 | 61.4881
3813.0938 | 123.381 | -61.5875 | 61.4822 | 3.0932 | 2.9861 | 3.7837 | 2.2276 | 0.56273 | 0.38318 | 1.1185 | 61.5508 | 0.26237 | 61.4592 | -0.042259 | 0.043657 | 61.7127 | 0.003143 | 61.5 | 64.6807 | 64.5736 | 65.3712 | 63.8151 | 62.1503 | 61.9707 | 62.706 | 123.1384 | 61.8499 | 123.0467 | 61.5453 | 61.6312 | 123.3002 | 61.5907 | 123.0875 | 61.5072 | 61.5477 | 61.4155 | 61.4561
3814.0625 | 123.2849 | -61.6013 | 61.5692 | 3.0795 | 2.9861 | 3.8707 | 2.2139 | 0.61767 | 0.3786 | 1.0772 | 61.56 | 0.25779 | 61.5004 | -0.028522 | 0.048236 | 61.7127 | 0.003143 | 61.4954 | 64.6807 | 64.5873 | 65.4719 | 63.8151 | 62.2189 | 61.9799 | 62.6785 | 123.1612 | 61.859 | 123.1017 | 61.5727 | 61.6495 | 123.3139 | 61.6044 | 123.0967 | 61.5118 | 61.5568 | 61.4522 | 61.4973
3815.0938 | 123.3856 | -61.5829 | 61.5417 | 3.1299 | 3.0364 | 3.9989 | 2.2001 | 0.61767 | 0.37402 | 1.1459 | 61.5508 | 0.27153 | 61.45 | -0.028522 | 0.048236 | 61.7218 | -0.001436 | 61.5046 | 64.7128 | 64.6194 | 65.5818 | 63.7831 | 62.2006 | 61.957 | 62.7289 | 123.1338 | 61.8545 | 123.033 | 61.5544 | 61.6312 | 123.3048 | 61.5815 | 123.0875 | 61.5026 | 61.5523 | 61.4018 | 61.4515
3816.0625 | 123.3902 | -61.5829 | 61.4868 | 3.1711 | 3.1189 | 4.0401 | 2.2184 | 0.64513 | 0.39233 | 1.0223 | 61.5417 | 0.25321 | 61.4821 | -0.033101 | 0.048236 | 61.7172 | -0.006014 | 61.4863 | 64.754 | 64.7018 | 65.623 | 63.8014 | 62.2281 | 61.9753 | 62.6053 | 123.1246 | 61.8362 | 123.065 | 61.5498 | 61.6312 | 123.3002 | 61.5769 | 123.0692 | 61.4934 | 61.5477 | 61.4339 | 61.4881
3817.1094 | 123.2712 | -61.6241 | 61.5784 | 3.226 | 3.1234 | 4.1316 | 2.2093 | 0.66802 | 0.41523 | 1.2146 | 61.5371 | 0.25779 | 61.4775 | -0.03768 | 0.043657 | 61.7218 | 0.007721 | 61.4954 | 64.8501 | 64.7476 | 65.7558 | 63.8334 | 62.2922 | 62.0394 | 62.8387 | 123.1612 | 61.8819 | 123.1017 | 61.5865 | 61.6678 | 123.346 | 61.6319 | 123.1196 | 61.4934 | 61.5294 | 61.4339 | 61.4698
3818.0625 | 123.3536 | -61.6241 | 61.5097 | 3.2306 | 3.1326 | 4.0675 | 2.2322 | 0.69091 | 0.42438 | 1.3245 | 61.5417 | 0.26695 | 61.45 | -0.03768 | 0.043657 | 61.7172 | 0.003143 | 61.4954 | 64.8547 | 64.7567 | 65.6917 | 63.8563 | 62.3151 | 62.0485 | 62.9486 | 123.1658 | 61.8911 | 123.0742 | 61.5865 | 61.6678 | 123.3414 | 61.6273 | 123.1196 | 61.498 | 61.5385 | 61.4064 | 61.4469
3819.0938 | 123.2529 | -61.6104 | 61.5326 | 3.1802 | 3.0731 | 4.1133 | 2.1864 | 0.67718 | 0.40149 | 1.2512 | 61.5508 | 0.27153 | 61.4821 | -0.028522 | 0.043657 | 61.7218 | 0.003143 | 61.5 | 64.7906 | 64.6835 | 65.7237 | 63.7968 | 62.2876 | 62.0119 | 62.8616 | 123.1612 | 61.8819 | 123.0925 | 61.5819 | 61.6541 | 123.3322 | 61.6136 | 123.1104 | 61.5072 | 61.5477 | 61.4384 | 61.4789
3820.0625 | 123.2895 | -61.6104 | 61.5829 | 3.1802 | 3.0822 | 4.008 | 2.223 | 0.66802 | 0.38776 | 1.2787 | 61.5417 | 0.26237 | 61.4684 | -0.028522 | 0.048236 | 61.7127 | -0.001436 | 61.5 | 64.7906 | 64.6926 | 65.6184 | 63.8334 | 62.2784 | 61.9982 | 62.8891 | 123.1521 | 61.8728 | 123.0788 | 61.5819 | 61.6586 | 123.3231 | 61.609 | 123.1104 | 61.4934 | 61.5431 | 61.4201 | 61.4698
3821.0781 | 123.2986 | -61.615 | 61.5372 | 3.1939 | 3.0868 | 4.0446 | 2.2047 | 0.66802 | 0.35113 | 1.3016 | 61.5463 | 0.26695 | 61.4638 | -0.03768 | 0.039079 | 61.7172 | 0.003143 | 61.4954 | 64.8089 | 64.7018 | 65.6596 | 63.8197 | 62.283 | 61.9661 | 62.9166 | 123.1612 | 61.8819 | 123.0788 | 61.5773 | 61.6541 | 123.3322 | 61.6181 | 123.1104 | 61.5072 | 61.5431 | 61.4247 | 61.4606
3822.0625 | 123.2941 | -61.6013 | 61.5601 | 2.8689 | 3.2013 | 3.9989 | 2.2413 | 0.71838 | 0.38776 | 1.3336 | 61.5508 | 0.26695 | 61.4821 | -0.028522 | 0.052814 | 61.7172 | 0.007721 | 61.5092 | 64.4701 | 64.8025 | 65.6001 | 63.8426 | 62.3196 | 61.989 | 62.9349 | 123.1521 | 61.8682 | 123.0833 | 61.5727 | 61.6541 | 123.3185 | 61.609 | 123.1104 | 61.498 | 61.5431 | 61.4293 | 61.4744
3823.0938 | 123.3719 | -61.615 | 61.5097 | 2.9192 | 2.8075 | 3.9164 | 2.2917 | 0.6726 | 0.39691 | 1.2329 | 61.5508 | 0.26695 | 61.4684 | -0.046838 | 0.043657 | 61.7081 | 0.007721 | 61.5046 | 64.5342 | 64.4225 | 65.5314 | 63.9067 | 62.2876 | 62.0119 | 62.8479 | 123.1658 | 61.8819 | 123.0833 | 61.5682 | 61.6586 | 123.3231 | 61.6227 | 123.1196 | 61.5072 | 61.5431 | 61.4247 | 61.4606
3824.0625 | 123.3856 | -61.6241 | 61.5417 | 3.0703 | 2.9632 | 4.0584 | 2.1727 | 0.56731 | 0.36944 | 1.123 | 61.5417 | 0.26237 | 61.4775 | -0.033101 | 0.043657 | 61.7172 | 0.012299 | 61.4954 | 64.6945 | 64.5873 | 65.6825 | 63.7968 | 62.1915 | 61.9936 | 62.7472 | 123.1658 | 61.8865 | 123.1017 | 61.591 | 61.6678 | 123.3414 | 61.6364 | 123.1196 | 61.498 | 61.5294 | 61.4339 | 61.4652
3825.1094 | 123.3444 | -61.615 | 61.528 | 3.0886 | 2.9769 | 4.1271 | 2.136 | 0.59935 | 0.34655 | 0.92617 | 61.56 | 0.25779 | 61.505 | -0.033101 | 0.043657 | 61.7081 | -0.006014 | 61.5 | 64.7036 | 64.5919 | 65.742 | 63.751 | 62.2143 | 61.9615 | 62.5412 | 123.175 | 61.8728 | 123.12 | 61.5819 | 61.6586 | 123.3231 | 61.609 | 123.115 | 61.5163 | 61.566 | 61.4613 | 61.511
3826.0625 | 123.3627 | -61.5738 | 61.5051 | 3.1115 | 2.9998 | 4.3056 | 2.1543 | 0.57189 | 0.36486 | 0.95822 | 61.5508 | 0.26695 | 61.4592 | -0.03768 | 0.043657 | 61.7127 | 0.016878 | 61.5046 | 64.6853 | 64.5736 | 65.8794 | 63.7281 | 62.1457 | 61.9387 | 62.532 | 123.1246 | 61.8407 | 123.033 | 61.5361 | 61.6174 | 123.2865 | 61.5907 | 123.0784 | 61.5072 | 61.534 | 61.4155 | 61.4423
3827.0781 | 123.3307 | -61.6196 | 61.5326 | 1.4404 | 3.7736 | 4.356 | 2.1315 | 0.58104 | 0.32824 | 0.94906 | 61.5508 | 0.26695 | 61.4821 | -0.03768 | 0.039079 | 61.7081 | -0.001436 | 61.5 | 63.06 | 65.3932 | 65.9756 | 63.751 | 62.2006 | 61.9478 | 62.5686 | 123.1704 | 61.8865 | 123.1017 | 61.5819 | 61.6586 | 123.3276 | 61.6181 | 123.1196 | 61.5118 | 61.5523 | 61.443 | 61.4835
3828.0625 | 123.3307 | -61.5921 | 61.5417 | 1.3397 | 3.7874 | 4.1774 | 2.0994 | 0.59935 | 0.34197 | 0.89412 | 61.5646 | 0.26237 | 61.505 | -0.03768 | 0.043657 | 61.7035 | 0.003143 | 61.4863 | 62.9318 | 65.3795 | 65.7695 | 63.6915 | 62.1915 | 61.9341 | 62.4862 | 123.1567 | 61.8545 | 123.0971 | 61.5544 | 61.6358 | 123.2956 | 61.5952 | 123.0784 | 61.5209 | 61.5614 | 61.4613 | 61.5018
3829.0781 | 123.4177 | -61.5738 | 61.5005 | 1.3443 | 3.824 | 3.976 | 2.1086 | 0.5902 | 0.33282 | 1.1322 | 61.5508 | 0.26237 | 61.4592 | -0.033101 | 0.048236 | 61.7081 | 0.003143 | 61.4863 | 62.9181 | 65.3978 | 65.5498 | 63.6824 | 62.164 | 61.9066 | 62.706 | 123.1246 | 61.8362 | 123.033 | 61.5407 | 61.622 | 123.2819 | 61.5769 | 123.0601 | 61.5026 | 61.5477 | 61.411 | 61.4561
3830.0781 | 123.3902 | -61.6196 | 61.4914 | 1.3489 | 3.911 | 4.1133 | 2.1772 | 0.55815 | 0.34197 | 0.98568 | 61.56 | 0.26695 | 61.4867 | -0.028522 | 0.039079 | 61.7081 | -0.001436 | 61.4863 | 62.9684 | 65.5306 | 65.7329 | 63.7968 | 62.1777 | 61.9615 | 62.6053 | 123.1796 | 61.8865 | 123.1062 | 61.591 | 61.6586 | 123.3276 | 61.6181 | 123.1058 | 61.5209 | 61.5614 | 61.4476 | 61.4881
3831.0781 | 123.3398 | -61.615 | 61.5005 | 1.3168 | 4.0758 | 4.0492 | 2.2139 | 0.56731 | 0.37402 | 0.91701 | 61.5508 | 0.25779 | 61.4592 | -0.042259 | 0.043657 | 61.7081 | -0.001436 | 61.4909 | 62.9318 | 65.6908 | 65.6642 | 63.8289 | 62.1823 | 61.989 | 62.532 | 123.1658 | 61.8728 | 123.0742 | 61.5727 | 61.6586 | 123.3231 | 61.6136 | 123.1058 | 61.5072 | 61.5523 | 61.4155 | 61.4606
3832.0625 | 123.4314 | -61.5646 | 61.5234 | 1.3809 | 4.0621 | 3.8752 | 2.2047 | 0.62682 | 0.38776 | 0.93075 | 61.5554 | 0.27153 | 61.4958 | -0.042259 | 0.039079 | 61.7035 | 0.007721 | 61.4863 | 62.9455 | 65.6267 | 65.4399 | 63.7693 | 62.1915 | 61.9524 | 62.4954 | 123.12 | 61.8362 | 123.0605 | 61.5224 | 61.6037 | 123.2681 | 61.5724 | 123.0509 | 61.5163 | 61.5477 | 61.4567 | 61.4881
3833.1094 | 123.3215 | -61.6013 | 61.5601 | 1.3672 | 4.117 | 3.9668 | 2.1772 | 0.549 | 0.30535 | 0.90785 | 61.5554 | 0.25321 | 61.4775 | -0.033101 | 0.039079 | 61.7035 | -0.001436 | 61.4954 | 62.9684 | 65.7183 | 65.5681 | 63.7785 | 62.1503 | 61.9066 | 62.5091 | 123.1567 | 61.8545 | 123.0788 | 61.5682 | 61.6403 | 123.3048 | 61.5998 | 123.0967 | 61.5163 | 61.5568 | 61.4384 | 61.4789
3834.0625 | 123.3856 | -61.5967 | 61.5372 | 2.8689 | 3.0731 | 3.7928 | 2.136 | 0.57189 | 0.36029 | 0.93532 | 61.5508 | 0.26695 | 61.4729 | -0.028522 | 0.039079 | 61.7081 | 0.003143 | 61.4817 | 64.4656 | 64.6698 | 65.3895 | 63.7327 | 62.1686 | 61.957 | 62.532 | 123.1475 | 61.8636 | 123.0696 | 61.5682 | 61.6358 | 123.3048 | 61.5998 | 123.0784 | 61.5118 | 61.5477 | 61.4339 | 61.4698
3835.0938 | 123.4039 | -61.6013 | 61.5326 | 2.9925 | 2.8991 | 3.8935 | 2.1269 | 0.58104 | 0.3786 | 0.96279 | 61.5554 | 0.25321 | 61.4912 | -0.03768 | 0.034501 | 61.7127 | 0.007721 | 61.4817 | 64.5938 | 64.5003 | 65.4948 | 63.7281 | 62.1823 | 61.9799 | 62.564 | 123.1567 | 61.8545 | 123.0925 | 61.5636 | 61.6358 | 123.3139 | 61.609 | 123.083 | 61.5209 | 61.5477 | 61.4567 | 61.4835
3836.0781 | 123.4131 | -61.5692 | 61.5326 | 1.706 | 3.4852 | 3.8066 | 2.1406 | 0.57189 | 0.35113 | 1.1688 | 61.5554 | 0.26237 | 61.4684 | -0.033101 | 0.048236 | 61.7081 | 0.007721 | 61.4863 | 63.2752 | 65.0544 | 65.3758 | 63.7098 | 62.1411 | 61.9203 | 62.738 | 123.1246 | 61.8316 | 123.0376 | 61.5361 | 61.6175 | 123.2773 | 61.5769 | 123.0555 | 61.5072 | 61.5477 | 61.4201 | 61.4606
3837.0781 | 123.3582 | -61.6013 | 61.5005 | 2.4202 | 2.8716 | 3.7333 | 2.1498 | 0.56731 | 0.3786 | 1.1688 | 61.56 | 0.26695 | 61.4912 | -0.028522 | 0.048236 | 61.6989 | -0.001436 | 61.4817 | 64.0215 | 64.4729 | 65.3346 | 63.751 | 62.1686 | 61.9799 | 62.7701 | 123.1612 | 61.8682 | 123.0925 | 61.5727 | 61.6495 | 123.3002 | 61.5998 | 123.083 | 61.5118 | 61.5614 | 61.443 | 61.4927
3838.0625 | 123.3124 | -61.5921 | 61.5189 | 2.64 | 2.6839 | 3.8569 | 2.1498 | 0.56731 | 0.39233 | 1.2375 | 61.56 | 0.26237 | 61.4729 | -0.033101 | 0.039079 | 61.7081 | -0.001436 | 61.4909 | 64.2321 | 64.276 | 65.449 | 63.7419 | 62.1594 | 61.9844 | 62.8296 | 123.1521 | 61.8545 | 123.065 | 61.559 | 61.6312 | 123.3002 | 61.5907 | 123.083 | 61.5209 | 61.5614 | 61.4339 | 61.4744
3839.0625 | 123.3902 | -61.5555 | 61.5509 | 2.7178 | 2.6198 | 3.8249 | 2.0857 | 0.53526 | 0.35571 | 1.2421 | 61.56 | 0.26237 | 61.4958 | -0.033101 | 0.039079 | 61.7172 | 0.003143 | 61.4863 | 64.2733 | 64.1753 | 65.3804 | 63.6412 | 62.0907 | 61.9112 | 62.7975 | 123.1155 | 61.8179 | 123.0513 | 61.5224 | 61.5946 | 123.2727 | 61.5586 | 123.0418 | 61.5209 | 61.5568 | 61.4567 | 61.4927
3840.0938 | 123.4039 | -61.6104 | 61.5234 | 2.5163 | 2.8487 | 4.0492 | 2.0902 | 0.49864 | 0.35571 | 1.2741 | 61.56 | 0.26237 | 61.4958 | -0.033101 | 0.039079 | 61.7081 | 0.003143 | 61.4909 | 64.1268 | 64.4591 | 65.6596 | 63.7007 | 62.1091 | 61.9661 | 62.8845 | 123.1704 | 61.8728 | 123.1062 | 61.5773 | 61.6495 | 123.3185 | 61.6136 | 123.1013 | 61.5209 | 61.5568 | 61.4567 | 61.4927
3841.0781 | 123.4451 | -61.5738 | 61.528 | 2.5988 | 2.8579 | 4.0813 | 2.0811 | 0.47575 | 0.34197 | 1.178 | 61.5554 | 0.25779 | 61.4729 | -0.033101 | 0.039079 | 61.7081 | 0.007721 | 61.4954 | 64.1726 | 64.4317 | 65.6551 | 63.6549 | 62.0495 | 61.9158 | 62.7518 | 123.1292 | 61.8316 | 123.0467 | 61.5407 | 61.6129 | 123.2819 | 61.5815 | 123.0692 | 61.5163 | 61.5477 | 61.4339 | 61.4652
3842.0938 | 123.4222 | -61.5555 | 61.5417 | 2.7865 | 2.7297 | 4.0034 | 2.0719 | 0.44828 | 0.33282 | 1.2466 | 61.5554 | 0.26237 | 61.4958 | -0.028522 | 0.043657 | 61.7172 | 0.003143 | 61.4863 | 64.342 | 64.2851 | 65.5589 | 63.6274 | 62.0038 | 61.8883 | 62.8021 | 123.1109 | 61.8179 | 123.0513 | 61.527 | 61.5991 | 123.2727 | 61.5586 | 123.0418 | 61.5118 | 61.5523 | 61.4522 | 61.4927
3843.0625 | 123.3215 | -61.5692 | 61.5372 | 2.727 | 2.7022 | 3.9531 | 2.049 | 0.42997 | 0.29619 | 1.2558 | 61.5646 | 0.26237 | 61.4958 | -0.033101 | 0.039079 | 61.7035 | 0.003143 | 61.4909 | 64.2962 | 64.2714 | 65.5223 | 63.6183 | 61.9992 | 61.8654 | 62.825 | 123.1338 | 61.8316 | 123.065 | 61.5361 | 61.6083 | 123.2727 | 61.5724 | 123.0601 | 61.5255 | 61.5614 | 61.4567 | 61.4927
3844.0938 | 123.3994 | -61.5601 | 61.5692 | 2.8139 | 2.7251 | 3.976 | 2.0307 | 0.39335 | 0.29161 | 1.2695 | 61.5508 | 0.25779 | 61.4821 | -0.033101 | 0.043657 | 61.7035 | 0.012299 | 61.5 | 64.374 | 64.2851 | 65.536 | 63.5908 | 61.9534 | 61.8517 | 62.8296 | 123.1109 | 61.8178 | 123.0421 | 61.527 | 61.6037 | 123.2636 | 61.5724 | 123.0601 | 61.5072 | 61.5385 | 61.4384 | 61.4698
3845.0625 | 123.2986 | -61.6058 | 61.5738 | 2.7911 | 2.7159 | 3.976 | 2.0445 | 0.3613 | 0.27787 | 1.2787 | 61.5646 | 0.27153 | 61.5004 | -0.03768 | 0.048236 | 61.7035 | 0.012299 | 61.4863 | 64.3969 | 64.3218 | 65.5818 | 63.6503 | 61.9671 | 61.8837 | 62.8845 | 123.1704 | 61.8774 | 123.1062 | 61.5682 | 61.6541 | 123.3093 | 61.6181 | 123.0921 | 61.5163 | 61.5523 | 61.4522 | 61.4881
3846.1094 | 123.3215 | -61.6058 | 61.5829 | 2.7956 | 2.7068 | 3.9256 | 2.0674 | 0.36588 | 0.23667 | 1.2833 | 61.5554 | 0.26237 | 61.4729 | -0.033101 | 0.052814 | 61.7035 | -0.001436 | 61.4909 | 64.4015 | 64.3126 | 65.5314 | 63.6732 | 61.9717 | 61.8425 | 62.8891 | 123.1612 | 61.8682 | 123.0788 | 61.5727 | 61.6586 | 123.3093 | 61.6044 | 123.0967 | 61.5026 | 61.5568 | 61.4201 | 61.4744
3847.0625 | 123.2712 | -61.5921 | 61.6058 | 2.6537 | 2.8075 | 3.8798 | 2.0902 | 0.37046 | 0.28703 | 1.3107 | 61.5646 | 0.26695 | 61.5004 | -0.028522 | 0.052814 | 61.7081 | 0.007721 | 61.4909 | 64.2458 | 64.3996 | 65.4719 | 63.6823 | 61.9626 | 61.8791 | 62.9028 | 123.1567 | 61.8591 | 123.0925 | 61.5636 | 61.6449 | 123.3002 | 61.5998 | 123.083 | 61.5118 | 61.5569 | 61.4476 | 61.4927
3848.0938 | 123.4543 | -61.5646 | 61.5417 | 2.7453 | 2.693 | 3.7974 | 2.0582 | 0.37046 | 0.2504 | 1.2604 | 61.56 | 0.26237 | 61.4729 | -0.033101 | 0.048236 | 61.7081 | 0.007721 | 61.4817 | 64.3099 | 64.2577 | 65.362 | 63.6228 | 61.9351 | 61.815 | 62.825 | 123.1246 | 61.827 | 123.0376 | 61.5315 | 61.6129 | 123.2727 | 61.5724 | 123.0463 | 61.5118 | 61.5523 | 61.4247 | 61.4652
3849.0625 | 123.3948 | -61.5509 | 61.5646 | 2.759 | 2.6656 | 3.6829 | 2.0078 | 0.34299 | 0.21836 | 1.1871 | 61.5691 | 0.26237 | 61.5004 | -0.03768 | 0.052814 | 61.7035 | -0.001436 | 61.4817 | 64.3099 | 64.2165 | 65.2338 | 63.5587 | 61.8939 | 61.7693 | 62.738 | 123.1201 | 61.8133 | 123.0513 | 61.5132 | 61.6037 | 123.2544 | 61.5495 | 123.0326 | 61.5163 | 61.5706 | 61.4476 | 61.5018
3850.0781 | 123.3948 | -61.6058 | 61.528 | 2.7041 | 2.6518 | 3.9348 | 2.0399 | 0.32925 | 0.22293 | 1.2375 | 61.5554 | 0.26237 | 61.4729 | -0.033101 | 0.039079 | 61.7035 | 0.003143 | 61.4863 | 64.3099 | 64.2577 | 65.5406 | 63.6457 | 61.9351 | 61.8288 | 62.8433 | 123.1612 | 61.8682 | 123.0788 | 61.5727 | 61.6449 | 123.3093 | 61.609 | 123.0921 | 61.5163 | 61.5523 | 61.4339 | 61.4698
3851.0625 | 123.2529 | -61.6241 | 61.5463 | 1.3672 | 3.7095 | 3.9531 | 2.0811 | 0.35214 | 0.24583 | 1.3474 | 61.5646 | 0.25779 | 61.5004 | -0.033101 | 0.043657 | 61.7081 | 0.003143 | 61.4909 | 62.9913 | 65.3337 | 65.5772 | 63.7052 | 61.9763 | 61.87 | 62.9715 | 123.1887 | 61.8819 | 123.1245 | 61.591 | 61.6678 | 123.3322 | 61.6273 | 123.115 | 61.5209 | 61.5614 | 61.4567 | 61.4973
3852.0938 | 123.3994 | -61.528 | 61.5326 | 1.1749 | 3.096 | 4.0263 | 2.0399 | 0.31552 | 0.19546 | 1.1368 | 61.5646 | 0.25779 | 61.5004 | -0.033101 | 0.039079 | 61.6989 | -0.001436 | 61.4817 | 62.7029 | 64.624 | 65.5543 | 63.5679 | 61.8435 | 61.7235 | 62.6648 | 123.0926 | 61.7858 | 123.0284 | 61.4949 | 61.5671 | 123.2269 | 61.5266 | 123.0097 | 61.5255 | 61.566 | 61.4613 | 61.5018
3853.0625 | 123.3353 | -61.5738 | 61.5784 | 1.1154 | 3.0593 | 3.6646 | 2.0811 | 0.30179 | 0.2092 | 0.97653 | 61.5691 | 0.26237 | 61.4958 | -0.03768 | 0.048236 | 61.6898 | -0.001436 | 61.4725 | 62.6892 | 64.6331 | 65.2384 | 63.6549 | 61.8756 | 61.783 | 62.5503 | 123.1429 | 61.8362 | 123.0696 | 61.5361 | 61.622 | 123.2636 | 61.5724 | 123.0463 | 61.5209 | 61.5706 | 61.4476 | 61.4973
3854.1094 | 123.2437 | -61.6196 | 61.5601 | 2.4614 | 2.4091 | 3.7058 | 2.0033 | 0.27432 | 0.22293 | 0.86665 | 61.5691 | 0.26695 | 61.5096 | -0.033101 | 0.039079 | 61.6943 | 0.003143 | 61.4725 | 64.081 | 64.0287 | 65.3254 | 63.6228 | 61.8939 | 61.8425 | 62.4862 | 123.1887 | 61.8865 | 123.1291 | 61.5865 | 61.6586 | 123.3139 | 61.6227 | 123.0921 | 61.5301 | 61.566 | 61.4705 | 61.5064
3855.0625 | 123.262 | -61.5555 | 61.6058 | 2.3927 | 2.2993 | 3.66 | 1.9758 | 0.24685 | 0.18631 | 0.79798 | 61.5691 | 0.26695 | 61.5004 | -0.03768 | 0.043657 | 61.6898 | -0.001436 | 61.4817 | 63.9482 | 63.8547 | 65.2155 | 63.5313 | 61.8023 | 61.7418 | 62.3535 | 123.1246 | 61.8224 | 123.0559 | 61.5178 | 61.5991 | 123.2452 | 61.554 | 123.0372 | 61.5255 | 61.5706 | 61.4567 | 61.5018
3856.0781 | 123.4085 | -61.5601 | 61.5601 | 2.3332 | 2.2306 | 3.7196 | 2.0033 | 0.29721 | 0.18631 | 1.0223 | 61.5737 | 0.25779 | 61.4958 | -0.03768 | 0.039079 | 61.6943 | 0.003143 | 61.4863 | 63.8933 | 63.7906 | 65.2796 | 63.5633 | 61.8573 | 61.7464 | 62.5824 | 123.1338 | 61.8178 | 123.0559 | 61.5224 | 61.5991 | 123.2544 | 61.5632 | 123.0463 | 61.5346 | 61.5706 | 61.4567 | 61.4927
3857.0625 | 123.3444 | -61.5784 | 61.528 | 2.411 | 2.3038 | 3.7196 | 2.0307 | 0.31552 | 0.20004 | 1.2237 | 61.5691 | 0.26237 | 61.505 | -0.033101 | 0.039079 | 61.6989 | 0.003143 | 61.4863 | 63.9894 | 63.8822 | 65.2979 | 63.6091 | 61.8939 | 61.7784 | 62.8021 | 123.1475 | 61.8407 | 123.0833 | 61.5453 | 61.6174 | 123.2773 | 61.5815 | 123.0646 | 61.5301 | 61.566 | 61.4659 | 61.5018
3858.0938 | 123.3582 | -61.6058 | 61.5143 | 2.4889 | 2.3954 | 3.7516 | 2.0857 | 0.39792 | 0.33282 | 2.2538 | 61.5508 | 0.26237 | 61.4592 | -0.03768 | 0.039079 | 61.7081 | 0.012299 | 61.5046 | 64.0947 | 64.0012 | 65.3574 | 63.6915 | 62.0038 | 61.9387 | 63.8597 | 123.1567 | 61.8682 | 123.065 | 61.5682 | 61.6449 | 123.3139 | 61.6181 | 123.1104 | 61.5118 | 61.5385 | 61.4201 | 61.4469
3859.0625 | 123.3398 | -61.6058 | 61.5555 | 2.5438 | 2.4412 | 3.8935 | 2.0902 | 0.4025 | 0.33739 | 2.35 | 61.5554 | 0.25779 | 61.4867 | -0.03768 | 0.048236 | 61.7081 | 0.007721 | 61.5 | 64.1497 | 64.047 | 65.4994 | 63.6961 | 62.0083 | 61.9432 | 63.9558 | 123.1612 | 61.8636 | 123.0925 | 61.5682 | 61.6541 | 123.3139 | 61.6136 | 123.1058 | 61.5072 | 61.5477 | 61.4384 | 61.4789
3860.1094 | 123.3261 | -61.6013 | 61.5189 | 2.5896 | 2.487 | 3.9393 | 2.0674 | 0.38877 | 0.32824 | 2.3546 | 61.5554 | 0.26237 | 61.4775 | -0.042259 | 0.043657 | 61.7081 | 0.003143 | 61.5046 | 64.1909 | 64.0882 | 65.5406 | 63.6686 | 61.99 | 61.9295 | 63.9558 | 123.1567 | 61.8636 | 123.0788 | 61.559 | 61.6449 | 123.3093 | 61.6044 | 123.1058 | 61.5118 | 61.5523 | 61.4339 | 61.4744
3861.0625 | 123.3261 | -61.6058 | 61.5555 | 1.4084 | 3.3295 | 3.8523 | 2.1223 | 0.33383 | 0.3145 | 2.4278 | 61.5508 | 0.26237 | 61.4592 | -0.033101 | 0.052814 | 61.7081 | 0.003143 | 61.5092 | 63.0142 | 64.9353 | 65.4582 | 63.7281 | 61.9397 | 61.9203 | 64.0336 | 123.1567 | 61.8682 | 123.065 | 61.5727 | 61.6586 | 123.3139 | 61.609 | 123.115 | 61.498 | 61.5477 | 61.4064 | 61.4561
3862.0938 | 123.2895 | -61.5875 | 61.5829 | 1.3443 | 3.3112 | 4.0858 | 2.0765 | 0.27432 | 0.2733 | 2.2767 | 61.56 | 0.26695 | 61.4958 | -0.028522 | 0.043657 | 61.7172 | 0.003143 | 61.4909 | 62.9318 | 64.8987 | 65.6734 | 63.664 | 61.8618 | 61.8608 | 63.8643 | 123.1475 | 61.8545 | 123.0833 | 61.559 | 61.6312 | 123.3048 | 61.5907 | 123.0784 | 61.5163 | 61.5568 | 61.4522 | 61.4927
3863.0781 | 123.2803 | -61.5921 | 61.6379 | 1.326 | 3.3753 | 4.0538 | 2.049 | 0.26516 | 0.24583 | 2.1852 | 61.56 | 0.26695 | 61.4912 | -0.042259 | 0.048236 | 61.7081 | 0.007721 | 61.4954 | 62.9181 | 64.9674 | 65.6459 | 63.6411 | 61.8573 | 61.8379 | 63.7773 | 123.1521 | 61.8591 | 123.0833 | 61.5498 | 61.6403 | 123.3002 | 61.5998 | 123.0875 | 61.5118 | 61.5523 | 61.443 | 61.4835
3864.0938 | 123.4085 | -61.5463 | 61.5829 | 1.3534 | 3.357 | 4.008 | 2.0811 | 0.28805 | 0.25956 | 2.4095 | 61.5417 | 0.26237 | 61.4729 | -0.033101 | 0.052814 | 61.7081 | 0.003143 | 61.5046 | 62.8998 | 64.9033 | 65.5543 | 63.6274 | 61.8344 | 61.8059 | 63.9558 | 123.088 | 61.8087 | 123.0193 | 61.5132 | 61.5991 | 123.2544 | 61.5495 | 123.0509 | 61.4889 | 61.5385 | 61.4201 | 61.4698
3865.0625 | 123.3078 | -61.5875 | 61.5463 | 1.358 | 3.531 | 3.9668 | 2.0261 | 0.30179 | 0.27787 | 2.2813 | 61.5554 | 0.25779 | 61.4958 | -0.03768 | 0.039079 | 61.7035 | 0.003143 | 61.4954 | 62.9455 | 65.1185 | 65.5543 | 63.6137 | 61.8893 | 61.8654 | 63.8688 | 123.1429 | 61.8453 | 123.0833 | 61.5498 | 61.6266 | 123.291 | 61.5907 | 123.083 | 61.5163 | 61.5523 | 61.4567 | 61.4927
3866.1094 | 123.2803 | -61.6058 | 61.5875 | 1.2802 | 3.389 | 3.8844 | 2.0857 | 0.27432 | 0.21836 | 2.1256 | 61.5554 | 0.26237 | 61.4775 | -0.03768 | 0.043657 | 61.7081 | -0.001436 | 61.4771 | 62.886 | 64.9948 | 65.4902 | 63.6915 | 61.8802 | 61.8242 | 63.7315 | 123.1612 | 61.8682 | 123.0833 | 61.5682 | 61.6495 | 123.3139 | 61.6044 | 123.083 | 61.5118 | 61.5568 | 61.4339 | 61.4789
3867.0625 | 123.317 | -61.5784 | 61.5646 | 1.2344 | 3.2883 | 3.6692 | 1.9758 | 0.24227 | 0.22751 | 2.2813 | 61.5646 | 0.26237 | 61.5096 | -0.033101 | 0.039079 | 61.7035 | 0.003143 | 61.4817 | 62.8128 | 64.8666 | 65.2476 | 63.5542 | 61.8206 | 61.8059 | 63.8597 | 123.1429 | 61.8407 | 123.0879 | 61.5453 | 61.6174 | 123.2819 | 61.5815 | 123.0601 | 61.5255 | 61.5614 | 61.4705 | 61.5064
3868.0938 | 123.3307 | -61.5921 | 61.5601 | 1.2848 | 3.476 | 3.8523 | 1.9712 | 0.28347 | 0.23209 | 2.4553 | 61.56 | 0.26695 | 61.4775 | -0.03768 | 0.043657 | 61.7035 | 0.003143 | 61.4863 | 62.8769 | 65.0681 | 65.4444 | 63.5633 | 61.8756 | 61.8242 | 64.0474 | 123.1521 | 61.8591 | 123.0696 | 61.5544 | 61.6358 | 123.2956 | 61.5952 | 123.0784 | 61.5163 | 61.5568 | 61.4339 | 61.4744
3869.0625 | 123.4085 | -61.6013 | 61.5143 | 1.2436 | 3.3295 | 3.7974 | 1.9666 | 0.25143 | 0.22293 | 2.4553 | 61.5646 | 0.26695 | 61.4958 | -0.033101 | 0.039079 | 61.7081 | 0.007721 | 61.4725 | 62.8448 | 64.9307 | 65.3987 | 63.5679 | 61.8527 | 61.8242 | 64.0565 | 123.1658 | 61.8682 | 123.0971 | 61.5682 | 61.6403 | 123.3093 | 61.609 | 123.0738 | 61.5255 | 61.5569 | 61.4567 | 61.4881
3870.0938 | 123.2666 | -61.5921 | 61.5738 | 1.2481 | 3.3249 | 3.9668 | 2.0445 | 0.26974 | 0.22293 | 2.4278 | 61.5554 | 0.26237 | 61.4729 | -0.028522 | 0.043657 | 61.7081 | 0.007721 | 61.4863 | 62.8402 | 64.917 | 65.5589 | 63.6366 | 61.8618 | 61.815 | 64.0199 | 123.1475 | 61.8545 | 123.065 | 61.5636 | 61.6358 | 123.3002 | 61.5998 | 123.0784 | 61.5118 | 61.5477 | 61.4293 | 61.4652
3871.0625 | 123.3032 | -61.6058 | 61.5692 | 1.326 | 3.3524 | 3.7699 | 2.0033 | 0.2789 | 0.20462 | 2.4599 | 61.5646 | 0.26695 | 61.5004 | -0.033101 | 0.043657 | 61.6989 | 0.003143 | 61.4863 | 62.9318 | 64.9582 | 65.3758 | 63.6091 | 61.8847 | 61.8105 | 64.0657 | 123.1704 | 61.8728 | 123.1062 | 61.5727 | 61.6495 | 123.3048 | 61.609 | 123.0921 | 61.5209 | 61.5614 | 61.4567 | 61.4973
3872.1094 | 123.3398 | -61.5784 | 61.5784 | 2.4156 | 2.345 | 3.4861 | 1.9437 | 0.21938 | 0.18173 | 2.2264 | 61.56 | 0.25779 | 61.4775 | -0.033101 | 0.043657 | 61.6989 | 0.003143 | 61.4771 | 63.994 | 63.9234 | 65.0644 | 63.5221 | 61.7978 | 61.7601 | 63.8047 | 123.1384 | 61.8362 | 123.0559 | 61.5453 | 61.622 | 123.2773 | 61.5815 | 123.0555 | 61.5163 | 61.5568 | 61.4339 | 61.4744
3873.0625 | 123.3994 | -61.5784 | 61.4914 | 1.2573 | 3.1784 | 3.6463 | 1.9575 | 0.19192 | 0.099318 | 2.2538 | 61.5646 | 0.26237 | 61.4958 | -0.03768 | 0.039079 | 61.7035 | 0.007721 | 61.468 | 62.8357 | 64.7568 | 65.2247 | 63.5358 | 61.7703 | 61.6777 | 63.8322 | 123.1429 | 61.8407 | 123.0742 | 61.5407 | 61.6174 | 123.2819 | 61.5861 | 123.0463 | 61.5255 | 61.5569 | 61.4567 | 61.4881
3874.0938 | 123.3948 | -61.5875 | 61.5143 | 2.5255 | 2.4504 | 3.7058 | 1.9163 | 0.26059 | 0.15884 | 2.2767 | 61.5554 | 0.26237 | 61.4958 | -0.03768 | 0.043657 | 61.7035 | 0.012299 | 61.4725 | 64.113 | 64.0379 | 65.2934 | 63.5038 | 61.8481 | 61.7464 | 63.8643 | 123.1429 | 61.8499 | 123.0833 | 61.5498 | 61.6312 | 123.291 | 61.5998 | 123.0601 | 61.5118 | 61.5431 | 61.4522 | 61.4835
3875.0625 | 123.4177 | -61.5967 | 61.4914 | 2.5026 | 2.4458 | 3.7012 | 1.9712 | 0.29263 | 0.19546 | 2.1669 | 61.5508 | 0.26237 | 61.4638 | -0.03768 | 0.043657 | 61.7035 | 0.003143 | 61.4817 | 64.0993 | 64.0425 | 65.2979 | 63.5679 | 61.8893 | 61.7921 | 63.7635 | 123.1475 | 61.859 | 123.0605 | 61.559 | 61.6403 | 123.3002 | 61.5998 | 123.0784 | 61.5072 | 61.5477 | 61.4201 | 61.4606
3876.0938 | 123.3261 | -61.6013 | 61.5829 | 1.3946 | 3.2883 | 3.747 | 1.9621 | 0.29263 | 0.15884 | 2.2493 | 61.56 | 0.25779 | 61.505 | -0.03768 | 0.034501 | 61.7035 | 0.007721 | 61.4771 | 62.9959 | 64.8895 | 65.3483 | 63.5633 | 61.8939 | 61.7601 | 63.8505 | 123.1612 | 61.859 | 123.1062 | 61.5636 | 61.6358 | 123.3048 | 61.609 | 123.0784 | 61.5255 | 61.5523 | 61.4705 | 61.4973
3877.0625 | 123.23 | -61.5875 | 61.5967 | 2.498 | 2.3954 | 3.6005 | 1.898 | 0.30636 | 0.15426 | 1.8876 | 61.56 | 0.27153 | 61.4958 | -0.028522 | 0.043657 | 61.7035 | 0.003143 | 61.4771 | 64.0856 | 63.9829 | 65.188 | 63.4855 | 61.8939 | 61.7418 | 63.4751 | 123.1475 | 61.8591 | 123.0833 | 61.559 | 61.6312 | 123.291 | 61.5907 | 123.0646 | 61.5163 | 61.5568 | 61.4522 | 61.4927
3878.1094 | 123.4177 | -61.6013 | 61.528 | 1.2115 | 3.3112 | 3.834 | 1.9987 | 0.30636 | 0.14052 | 1.7914 | 61.5646 | 0.26237 | 61.4684 | -0.03768 | 0.043657 | 61.7035 | 0.003143 | 61.4725 | 62.8128 | 64.9124 | 65.4353 | 63.5999 | 61.9076 | 61.7418 | 63.3927 | 123.1658 | 61.8636 | 123.0696 | 61.5636 | 61.6449 | 123.3048 | 61.6044 | 123.0738 | 61.5209 | 61.5614 | 61.4247 | 61.4652
3879.0625 | 123.3078 | -61.615 | 61.5784 | 1.3489 | 3.5401 | 3.9805 | 2.136 | 0.38877 | 0.2092 | 2.6155 | 61.5554 | 0.26237 | 61.4958 | -0.033101 | 0.048236 | 61.7127 | 0.003143 | 61.5 | 62.9638 | 65.1551 | 65.5955 | 63.751 | 62.0038 | 61.8242 | 64.2305 | 123.1704 | 61.8774 | 123.1108 | 61.5819 | 61.6632 | 123.3276 | 61.6181 | 123.115 | 61.5072 | 61.5523 | 61.4476 | 61.4927
3880.0938 | 123.436 | -61.5784 | 61.5372 | 2.5621 | 2.4687 | 3.7241 | 2.0948 | 0.32468 | 0.15884 | 2.4232 | 61.5463 | 0.26237 | 61.4684 | -0.033101 | 0.039079 | 61.7035 | 0.003143 | 61.4909 | 64.1405 | 64.047 | 65.3025 | 63.6732 | 61.903 | 61.7372 | 64.0016 | 123.1246 | 61.8407 | 123.0467 | 61.5453 | 61.6174 | 123.2819 | 61.5815 | 123.0692 | 61.5072 | 61.5431 | 61.4293 | 61.4652
3881.0625 | 123.3215 | -61.6104 | 61.5601 | 1.3397 | 3.4623 | 3.7516 | 2.104 | 0.29263 | 0.15426 | 2.5743 | 61.5554 | 0.26237 | 61.4821 | -0.028522 | 0.048236 | 61.7127 | 0.007721 | 61.5 | 62.9501 | 65.0727 | 65.362 | 63.7144 | 61.903 | 61.7647 | 64.1847 | 123.1658 | 61.8728 | 123.0925 | 61.5819 | 61.6586 | 123.3231 | 61.6181 | 123.1104 | 61.5072 | 61.5477 | 61.4339 | 61.4744
3882.0625 | 123.3078 | -61.5921 | 61.5555 | 1.3534 | 3.476 | 3.7562 | 2.1406 | 0.3201 | 0.18173 | 2.5652 | 61.5646 | 0.26695 | 61.5096 | -0.033101 | 0.034501 | 61.7127 | -0.001436 | 61.4817 | 62.9455 | 65.0681 | 65.3483 | 63.7327 | 61.9122 | 61.7738 | 64.1573 | 123.1567 | 61.8591 | 123.1017 | 61.559 | 61.6266 | 123.3048 | 61.5907 | 123.0738 | 61.5301 | 61.566 | 61.4751 | 61.511
3883.0781 | 123.3673 | -61.5875 | 61.5463 | 1.3397 | 3.5081 | 3.7196 | 2.1223 | 0.32925 | 0.15426 | 2.5926 | 61.5554 | 0.26237 | 61.4729 | -0.03768 | 0.034501 | 61.7127 | -0.006014 | 61.5 | 62.9272 | 65.0956 | 65.3071 | 63.7098 | 61.9168 | 61.7418 | 64.1801 | 123.1429 | 61.8499 | 123.0605 | 61.5498 | 61.622 | 123.3002 | 61.5815 | 123.0875 | 61.5209 | 61.5614 | 61.4384 | 61.4789
3884.0625 | 123.3078 | -61.615 | 61.5692 | 1.3168 | 3.4211 | 3.7012 | 2.1406 | 0.34299 | 0.19089 | 2.5697 | 61.5508 | 0.26237 | 61.4867 | -0.033101 | 0.048236 | 61.7127 | -0.001436 | 61.4909 | 62.9318 | 65.0361 | 65.3162 | 63.7556 | 61.958 | 61.8059 | 64.1847 | 123.1658 | 61.8774 | 123.1017 | 61.5819 | 61.6632 | 123.3276 | 61.6136 | 123.1058 | 61.5026 | 61.5523 | 61.4384 | 61.4881
3885.0781 | 123.3994 | -61.5692 | 61.5372 | 1.3534 | 3.2608 | 3.6646 | 2.2413 | 0.33383 | 0.22293 | 2.6155 | 61.5508 | 0.27153 | 61.4867 | -0.03768 | 0.039079 | 61.7035 | 0.003143 | 61.4954 | 62.9227 | 64.83 | 65.2338 | 63.8106 | 61.903 | 61.7921 | 64.1847 | 123.12 | 61.8407 | 123.0559 | 61.5315 | 61.6083 | 123.2727 | 61.5724 | 123.0646 | 61.5118 | 61.5477 | 61.4476 | 61.4835
3886.0625 | 123.3032 | -61.5921 | 61.5921 | 1.3443 | 3.2242 | 3.802 | 2.2505 | 0.30179 | 0.1451 | 2.5606 | 61.5554 | 0.26695 | 61.4958 | -0.028522 | 0.048236 | 61.7081 | 0.012299 | 61.4909 | 62.9364 | 64.8163 | 65.3941 | 63.8426 | 61.8939 | 61.7372 | 64.1527 | 123.1475 | 61.8591 | 123.0879 | 61.5636 | 61.6403 | 123.3002 | 61.6044 | 123.083 | 61.5072 | 61.5431 | 61.4476 | 61.4835
3887.1094 | 123.4039 | -61.5738 | 61.5189 | 1.3626 | 3.2608 | 3.7928 | 2.2734 | 0.30179 | 0.12221 | 2.5606 | 61.5508 | 0.26237 | 61.4867 | -0.03768 | 0.048236 | 61.7035 | -0.001436 | 61.4909 | 62.9364 | 64.8346 | 65.3666 | 63.8472 | 61.8756 | 61.696 | 64.1344 | 123.1246 | 61.8362 | 123.0605 | 61.5361 | 61.622 | 123.2773 | 61.5724 | 123.0646 | 61.5026 | 61.5523 | 61.4384 | 61.4881
3888.0625 | 123.2986 | -61.5921 | 61.5601 | 2.5163 | 2.4961 | 3.7653 | 2.4153 | 0.37046 | 0.26872 | 2.6338 | 61.5417 | 0.26695 | 61.4775 | -0.03768 | 0.052814 | 61.7172 | -0.006014 | 61.4954 | 64.1084 | 64.0882 | 65.3574 | 64.0074 | 61.9626 | 61.8608 | 64.2259 | 123.1338 | 61.8591 | 123.0696 | 61.5544 | 61.6449 | 123.3093 | 61.5861 | 123.0875 | 61.4889 | 61.5477 | 61.4247 | 61.4835
3889.0938 | 123.3765 | -61.5921 | 61.5051 | 1.3077 | 3.27 | 3.7608 | 2.3695 | 0.29721 | 0.18173 | 2.4919 | 61.5554 | 0.26237 | 61.4912 | -0.033101 | 0.039079 | 61.7081 | 0.003143 | 61.4863 | 62.8998 | 64.8621 | 65.3529 | 63.9616 | 61.8893 | 61.7738 | 64.084 | 123.1475 | 61.8545 | 123.0833 | 61.559 | 61.6312 | 123.3002 | 61.5952 | 123.0784 | 61.5163 | 61.5523 | 61.4522 | 61.4881
3890.0781 | 123.3215 | -61.6058 | 61.5646 | 2.4935 | 2.3954 | 3.6692 | 2.2597 | 0.31094 | 0.21378 | 2.5514 | 61.5554 | 0.26237 | 61.4775 | -0.03768 | 0.048236 | 61.7081 | 0.003143 | 61.4863 | 64.0993 | 64.0012 | 65.275 | 63.8655 | 61.9168 | 61.8196 | 64.1573 | 123.1612 | 61.8682 | 123.0833 | 61.5682 | 61.6541 | 123.3139 | 61.609 | 123.0921 | 61.5072 | 61.5523 | 61.4293 | 61.4744
3891.0781 | 123.3398 | -61.6379 | 61.4914 | 1.3077 | 3.2379 | 3.8386 | 2.3009 | 0.34757 | 0.17715 | 2.2996 | 61.56 | 0.26695 | 61.505 | -0.03768 | 0.039079 | 61.7081 | 0.003143 | 61.4909 | 62.9455 | 64.8758 | 65.4765 | 63.9387 | 61.9854 | 61.815 | 63.9375 | 123.1979 | 61.9048 | 123.1429 | 61.6002 | 61.677 | 123.346 | 61.641 | 123.1287 | 61.5209 | 61.5568 | 61.4659 | 61.5018
3892.0625 | 123.2574 | -61.5875 | 61.5967 | 1.2298 | 3.215 | 3.834 | 2.2276 | 0.28805 | 0.12221 | 2.002 | 61.5554 | 0.25779 | 61.4775 | -0.03768 | 0.048236 | 61.6989 | 0.007721 | 61.4863 | 62.8173 | 64.8025 | 65.4216 | 63.8151 | 61.8756 | 61.7097 | 63.5896 | 123.1429 | 61.8453 | 123.065 | 61.5498 | 61.6358 | 123.2864 | 61.5952 | 123.0738 | 61.5072 | 61.5477 | 61.4293 | 61.4698
3893.1094 | 123.317 | -61.5784 | 61.5646 | 1.326 | 3.3478 | 3.802 | 2.2917 | 0.34757 | 0.23667 | 2.643 | 61.5554 | 0.25779 | 61.4958 | -0.033101 | 0.048236 | 61.7081 | -0.006014 | 61.5046 | 62.9043 | 64.9262 | 65.3803 | 63.8701 | 61.9259 | 61.815 | 64.2214 | 123.1338 | 61.8362 | 123.0742 | 61.5453 | 61.6266 | 123.2864 | 61.5724 | 123.083 | 61.5072 | 61.5614 | 61.4476 | 61.5018
3894.0625 | 123.2849 | -61.615 | 61.5601 | 1.3351 | 3.3386 | 3.747 | 2.3421 | 0.35672 | 0.21378 | 2.6933 | 61.5508 | 0.26695 | 61.4684 | -0.033101 | 0.043657 | 61.7127 | 0.003143 | 61.5046 | 62.9501 | 64.9536 | 65.362 | 63.9571 | 61.9717 | 61.8288 | 64.3083 | 123.1658 | 61.8819 | 123.0833 | 61.5819 | 61.6586 | 123.3276 | 61.6181 | 123.1196 | 61.5072 | 61.5477 | 61.4247 | 61.4652
3895.0938 | 123.4222 | -61.5646 | 61.5234 | 1.3672 | 3.2562 | 3.889 | 2.3054 | 0.36588 | 0.15884 | 2.7025 | 61.5508 | 0.26695 | 61.4775 | -0.042259 | 0.048236 | 61.7081 | 0.007721 | 61.5 | 62.9318 | 64.8209 | 65.4536 | 63.8701 | 61.9305 | 61.7235 | 64.2671 | 123.1155 | 61.8316 | 123.0421 | 61.5224 | 61.6129 | 123.2727 | 61.5724 | 123.0646 | 61.5026 | 61.5431 | 61.4293 | 61.4698
3896.0625 | 123.3627 | -61.6104 | 61.5326 | 1.3031 | 3.27 | 3.889 | 2.278 | 0.37961 | 0.18631 | 2.5011 | 61.56 | 0.25779 | 61.4912 | -0.028522 | 0.039079 | 61.7127 | -0.006014 | 61.5 | 62.9135 | 64.8804 | 65.4994 | 63.8884 | 61.99 | 61.7967 | 64.1115 | 123.1704 | 61.8682 | 123.1017 | 61.5819 | 61.6495 | 123.3231 | 61.6044 | 123.1104 | 61.5209 | 61.566 | 61.4522 | 61.4973
3897.0625 | 123.3078 | -61.5921 | 61.5601 | 1.3122 | 3.2333 | 3.8707 | 2.2688 | 0.38419 | 0.2092 | 2.5468 | 61.5554 | 0.25779 | 61.4729 | -0.028522 | 0.048236 | 61.7127 | 0.012299 | 61.5 | 62.9043 | 64.8254 | 65.4628 | 63.8609 | 61.9763 | 61.8013 | 64.1389 | 123.1475 | 61.8499 | 123.065 | 61.5636 | 61.6403 | 123.3048 | 61.6044 | 123.0921 | 61.5072 | 61.5431 | 61.4247 | 61.4606
3898.0938 | 123.2666 | -61.6013 | 61.5875 | 1.3397 | 3.4531 | 3.7241 | 2.3741 | 0.39335 | 0.15884 | 2.4232 | 61.5554 | 0.26237 | 61.4912 | -0.033101 | 0.043657 | 61.7127 | 0.003143 | 61.5137 | 62.941 | 65.0544 | 65.3254 | 63.9754 | 61.9946 | 61.7601 | 64.0245 | 123.1567 | 61.8636 | 123.0925 | 61.5682 | 61.6449 | 123.3139 | 61.6044 | 123.115 | 61.5118 | 61.5523 | 61.4476 | 61.4881
3899.0625 | 123.2941 | -61.6058 | 61.5967 | 1.2207 | 3.3386 | 3.4815 | 2.3238 | 0.34299 | 0.071848 | 1.5442 | 61.5691 | 0.26237 | 61.505 | -0.028522 | 0.043657 | 61.7035 | 0.003143 | 61.4909 | 62.8265 | 64.9445 | 65.0873 | 63.9296 | 61.9488 | 61.6777 | 63.1501 | 123.175 | 61.8682 | 123.1108 | 61.5773 | 61.6495 | 123.3093 | 61.609 | 123.0967 | 61.5255 | 61.566 | 61.4613 | 61.5018
3900.0781 | 123.4406 | -61.5692 | 61.5509 | 1.152 | 3.1967 | 3.3624 | 2.2597 | 0.33841 | 0.099318 | 1.5351 | 61.5737 | 0.26695 | 61.4821 | -0.03768 | 0.048236 | 61.6943 | -0.001436 | 61.4863 | 62.7212 | 64.7659 | 64.9316 | 63.8289 | 61.9076 | 61.6685 | 63.1043 | 123.1429 | 61.8362 | 123.0513 | 61.5315 | 61.6175 | 123.2636 | 61.5678 | 123.0555 | 61.5255 | 61.5752 | 61.4339 | 61.4835
3901.0625 | 123.3215 | -61.6241 | 61.5326 | 1.2893 | 3.4119 | 3.7425 | 2.3192 | 0.45744 | 0.28703 | 2.9543 | 61.5554 | 0.26237 | 61.4912 | -0.028522 | 0.039079 | 61.7035 | 0.007721 | 61.5046 | 62.9135 | 65.0361 | 65.3666 | 63.9433 | 62.0816 | 61.9112 | 64.5784 | 123.1796 | 61.8865 | 123.1154 | 61.5956 | 61.6632 | 123.3276 | 61.6319 | 123.1287 | 61.5163 | 61.5477 | 61.4522 | 61.4835
3902.0625 | 123.3032 | -61.6058 | 61.5601 | 1.2664 | 3.357 | 3.715 | 2.3695 | 0.44828 | 0.28245 | 3.0047 | 61.5463 | 0.26237 | 61.4684 | -0.03768 | 0.043657 | 61.7218 | 0.007721 | 61.5092 | 62.8723 | 64.9628 | 65.3208 | 63.9754 | 62.0541 | 61.8883 | 64.6105 | 123.1521 | 61.8682 | 123.0742 | 61.5682 | 61.6495 | 123.3276 | 61.6136 | 123.115 | 61.5026 | 61.5385 | 61.4247 | 61.4606
3903.0938 | 123.2712 | -61.6379 | 61.5463 | 1.3031 | 3.3982 | 3.5273 | 2.365 | 0.44828 | 0.25956 | 2.9039 | 61.5508 | 0.26695 | 61.4958 | -0.033101 | 0.043657 | 61.7127 | 0.007721 | 61.5092 | 62.941 | 65.036 | 65.1651 | 64.0028 | 62.0862 | 61.8974 | 64.5418 | 123.1887 | 61.9048 | 123.1337 | 61.6048 | 61.6815 | 123.3505 | 61.6456 | 123.147 | 61.5072 | 61.5431 | 61.4522 | 61.4881
3904.0625 | 123.3765 | -61.5829 | 61.5143 | 1.3305 | 3.3066 | 3.8386 | 2.365 | 0.42539 | 0.22751 | 2.556 | 61.5508 | 0.25779 | 61.4592 | -0.03768 | 0.043657 | 61.7081 | 0.007721 | 61.5092 | 62.9135 | 64.8895 | 65.4216 | 63.9479 | 62.0083 | 61.8105 | 64.1389 | 123.1338 | 61.8407 | 123.0421 | 61.5453 | 61.6266 | 123.291 | 61.5907 | 123.0921 | 61.5072 | 61.5431 | 61.4155 | 61.4515
3905.0781 | 123.3582 | -61.615 | 61.5097 | 1.3992 | 3.3799 | 3.9027 | 2.397 | 0.48033 | 0.28245 | 3.0367 | 61.5554 | 0.27153 | 61.4867 | -0.033101 | 0.048236 | 61.7218 | 0.012299 | 61.5183 | 63.0142 | 64.9948 | 65.5177 | 64.012 | 62.0953 | 61.8974 | 64.6517 | 123.1704 | 61.8865 | 123.1017 | 61.5819 | 61.6632 | 123.3368 | 61.6273 | 123.1333 | 61.5072 | 61.5431 | 61.4384 | 61.4744
3906.0625 | 123.3078 | -61.6104 | 61.5738 | 1.3305 | 3.2608 | 3.7287 | 2.3375 | 0.42539 | 0.21378 | 2.5285 | 61.5554 | 0.26237 | 61.4729 | -0.03768 | 0.048236 | 61.7081 | 0.003143 | 61.5046 | 62.941 | 64.8712 | 65.3391 | 63.9479 | 62.0358 | 61.8242 | 64.1389 | 123.1658 | 61.8728 | 123.0833 | 61.5727 | 61.6586 | 123.3185 | 61.6136 | 123.115 | 61.5072 | 61.5523 | 61.4247 | 61.4698
3907.0938 | 123.3948 | -61.5601 | 61.5372 | 1.2298 | 3.183 | 3.7287 | 2.3192 | 0.39335 | 0.12679 | 1.7273 | 61.5691 | 0.25779 | 61.5004 | -0.03768 | 0.043657 | 61.7035 | 0.007721 | 61.4817 | 62.7899 | 64.743 | 65.2888 | 63.8792 | 61.9534 | 61.6868 | 63.2874 | 123.1292 | 61.8178 | 123.0605 | 61.5224 | 61.6037 | 123.2636 | 61.5678 | 123.0418 | 61.5255 | 61.5614 | 61.4567 | 61.4927
3908.0625 | 123.3536 | -61.5967 | 61.5372 | 1.1978 | 3.0914 | 3.8294 | 2.223 | 0.36588 | 0.067269 | 1.3703 | 61.5783 | 0.27153 | 61.4821 | -0.028522 | 0.048236 | 61.6943 | -0.001436 | 61.4909 | 62.7945 | 64.6881 | 65.4261 | 63.8197 | 61.9626 | 61.6639 | 62.9669 | 123.175 | 61.8682 | 123.0788 | 61.5682 | 61.6449 | 123.291 | 61.5952 | 123.0875 | 61.5301 | 61.5797 | 61.4339 | 61.4835
3909.0781 | 123.4177 | -61.5692 | 61.5509 | 1.1383 | 3.2013 | 3.7012 | 2.1772 | 0.32468 | 0.039799 | 1.3519 | 61.5783 | 0.25779 | 61.5004 | -0.042259 | 0.043657 | 61.6943 | 0.007721 | 61.4817 | 62.7075 | 64.7705 | 65.2705 | 63.7465 | 61.8939 | 61.609 | 62.9212 | 123.1475 | 61.827 | 123.0696 | 61.527 | 61.6129 | 123.2636 | 61.5769 | 123.0509 | 61.5346 | 61.5706 | 61.4567 | 61.4927
3910.0625 | 123.3215 | -61.5875 | 61.5646 | 1.1108 | 3.1005 | 3.7241 | 2.1452 | 0.32468 | 0.00775 | 1.3062 | 61.5783 | 0.27153 | 61.5004 | -0.03768 | 0.043657 | 61.6898 | 0.003143 | 61.4909 | 62.6983 | 64.6881 | 65.3117 | 63.7327 | 61.9122 | 61.5953 | 62.8937 | 123.1658 | 61.8591 | 123.0879 | 61.5498 | 61.6312 | 123.2773 | 61.5907 | 123.0784 | 61.5346 | 61.5752 | 61.4567 | 61.4973
3911.0938 | 123.4039 | -61.5601 | 61.5189 | 0.59342 | 3.0364 | 3.7425 | 2.1498 | 0.31094 | 0.43812 | 1.2421 | 61.5783 | 0.26695 | 61.5141 | -0.042259 | 0.039079 | 61.6898 | -0.006014 | 61.4817 | 62.1535 | 64.5965 | 65.3025 | 63.7098 | 61.871 | 61.9982 | 62.8021 | 123.1384 | 61.827 | 123.0742 | 61.5178 | 61.5991 | 123.2498 | 61.554 | 123.0418 | 61.5392 | 61.5843 | 61.4751 | 61.5202
3912.0625 | 123.2941 | -61.5829 | 61.5829 | 0.73993 | 3.2791 | 3.6692 | 2.2734 | 0.4437 | 0.6121 | 2.9451 | 61.5508 | 0.26237 | 61.4912 | -0.028522 | 0.039079 | 61.7218 | 0.007721 | 61.5092 | 62.3229 | 64.8621 | 65.2521 | 63.8563 | 62.0266 | 62.195 | 64.5281 | 123.1338 | 61.8453 | 123.0742 | 61.5544 | 61.622 | 123.3048 | 61.5907 | 123.0921 | 61.5118 | 61.5431 | 61.4522 | 61.4835
3913.1094 | 123.3078 | -61.6196 | 61.5189 | 0.71246 | 3.2791 | 3.5959 | 2.397 | 0.43912 | 0.61668 | 3.023 | 61.5554 | 0.25779 | 61.4867 | -0.03768 | 0.043657 | 61.7127 | 0.012299 | 61.5 | 62.332 | 64.8987 | 65.2155 | 64.0166 | 62.0587 | 62.2362 | 64.6425 | 123.175 | 61.8774 | 123.1062 | 61.5819 | 61.6632 | 123.3322 | 61.6319 | 123.1196 | 61.5118 | 61.5431 | 61.443 | 61.4744
3914.0625 | 123.2895 | -61.5921 | 61.6013 | 0.54764 | 3.096 | 3.5914 | 2.3054 | 0.30636 | 0.42896 | 1.2146 | 61.5783 | 0.26237 | 61.5096 | -0.033101 | 0.052814 | 61.6898 | 0.003143 | 61.4863 | 62.1397 | 64.6881 | 65.1835 | 63.8975 | 61.8985 | 62.0211 | 62.8067 | 123.1704 | 61.8545 | 123.1017 | 61.559 | 61.6449 | 123.2819 | 61.5952 | 123.0784 | 61.5255 | 61.5752 | 61.4567 | 61.5064
3915.0625 | 123.3536 | -61.5875 | 61.5784 | 0.56138 | 3.009 | 3.8935 | 2.3421 | 0.33841 | 0.45185 | 1.1597 | 61.5737 | 0.25321 | 61.505 | -0.033101 | 0.043657 | 61.6943 | 0.007721 | 61.4771 | 62.1489 | 64.5965 | 65.4811 | 63.9296 | 61.9259 | 62.0394 | 62.7472 | 123.1613 | 61.8407 | 123.0925 | 61.5544 | 61.6312 | 123.2819 | 61.5952 | 123.0646 | 61.5301 | 61.566 | 61.4613 | 61.4973
3916.0625 | 123.3032 | -61.6013 | 61.5601 | 0.55222 | 2.9311 | 3.9302 | 2.4153 | 0.33841 | 0.47475 | 1.1688 | 61.5737 | 0.26237 | 61.5096 | -0.033101 | 0.048236 | 61.6989 | 0.007721 | 61.4817 | 62.1535 | 64.5324 | 65.5314 | 64.0166 | 61.9397 | 62.076 | 62.7701 | 123.175 | 61.8636 | 123.1108 | 61.5682 | 61.6495 | 123.3002 | 61.609 | 123.083 | 61.5255 | 61.566 | 61.4613 | 61.5018
3917.0625 | 123.2712 | -61.6058 | 61.5784 | 1.0192 | 3.1326 | 4.008 | 2.5023 | 0.48033 | 0.40607 | 3.0138 | 61.5508 | 0.26695 | 61.4684 | -0.03768 | 0.043657 | 61.7172 | 0.003143 | 61.5046 | 62.6251 | 64.7384 | 65.6138 | 64.1081 | 62.0862 | 62.0119 | 64.6196 | 123.1567 | 61.8728 | 123.0742 | 61.5682 | 61.6495 | 123.3231 | 61.609 | 123.1104 | 61.5072 | 61.5477 | 61.4247 | 61.4652
3918.0938 | 123.2986 | -61.6608 | 61.5463 | 0.73078 | 3.041 | 3.9256 | 2.4748 | 0.47117 | 0.64872 | 2.5514 | 61.56 | 0.25321 | 61.4958 | -0.033101 | 0.043657 | 61.7127 | -0.001436 | 61.4909 | 62.3915 | 64.7018 | 65.5864 | 64.1356 | 62.1319 | 62.3095 | 64.2122 | 123.2208 | 61.914 | 123.1566 | 61.6277 | 61.7044 | 123.3734 | 61.6593 | 123.1516 | 61.5163 | 61.5614 | 61.4522 | 61.4973
3919.0625 | 123.2758 | -61.6287 | 61.5692 | 0.81777 | 3.128 | 3.9256 | 2.4932 | 0.50779 | 0.74945 | 3.1603 | 61.5417 | 0.26237 | 61.4638 | -0.028522 | 0.052814 | 61.7127 | 0.003143 | 61.5046 | 62.4465 | 64.7567 | 65.5543 | 64.1219 | 62.1365 | 62.3782 | 64.789 | 123.1704 | 61.8911 | 123.0925 | 61.6002 | 61.6815 | 123.3414 | 61.6319 | 123.1333 | 61.4889 | 61.5385 | 61.411 | 61.4606
3920.0781 | 123.4085 | -61.5967 | 61.496 | 1.0925 | 3.2013 | 3.9714 | 2.5069 | 0.54442 | 0.48848 | 3.1878 | 61.5554 | 0.26237 | 61.4867 | -0.03768 | 0.034501 | 61.7172 | 0.003143 | 61.5 | 62.6891 | 64.798 | 65.5681 | 64.1036 | 62.1411 | 62.0852 | 64.7845 | 123.1521 | 61.859 | 123.0833 | 61.559 | 61.6312 | 123.3139 | 61.5998 | 123.0967 | 61.5209 | 61.5523 | 61.4522 | 61.4835
3921.0625 | 123.2758 | -61.6058 | 61.5509 | 0.80403 | 3.1647 | 3.9119 | 2.4336 | 0.55815 | 0.7174 | 2.9772 | 61.5508 | 0.26695 | 61.4592 | -0.03768 | 0.043657 | 61.7172 | 0.007721 | 61.4954 | 62.4099 | 64.7705 | 65.5177 | 64.0395 | 62.164 | 62.3232 | 64.583 | 123.1567 | 61.8728 | 123.065 | 61.5682 | 61.6495 | 123.3231 | 61.6136 | 123.1013 | 61.5072 | 61.5431 | 61.4155 | 61.4515
3922.0938 | 123.4406 | -61.5829 | 61.5234 | 0.79945 | 3.183 | 3.6646 | 2.5069 | 0.56273 | 0.70824 | 3.1512 | 61.5554 | 0.26237 | 61.4821 | -0.033101 | 0.039079 | 61.7264 | 0.003143 | 61.5 | 62.3824 | 64.7659 | 65.2476 | 64.0898 | 62.1457 | 62.2912 | 64.7341 | 123.1384 | 61.8453 | 123.065 | 61.5498 | 61.622 | 123.3093 | 61.5861 | 123.083 | 61.5163 | 61.5523 | 61.443 | 61.4789
3923.0625 | 123.3856 | -61.6013 | 61.4777 | 0.79945 | 3.2059 | 3.7241 | 2.484 | 0.52611 | 0.72656 | 3.2015 | 61.5463 | 0.26695 | 61.4592 | -0.042259 | 0.039079 | 61.7172 | 0.003143 | 61.4909 | 62.4007 | 64.8071 | 65.3254 | 64.0853 | 62.1274 | 62.3278 | 64.8028 | 123.1475 | 61.8682 | 123.0605 | 61.559 | 61.6403 | 123.3185 | 61.6044 | 123.0921 | 61.5072 | 61.5431 | 61.4201 | 61.4561
3924.0781 | 123.3994 | -61.5921 | 61.5005 | 0.79945 | 3.183 | 3.9393 | 2.4291 | 0.49864 | 0.70366 | 3.2519 | 61.56 | 0.26237 | 61.4867 | -0.033101 | 0.039079 | 61.7172 | -0.001436 | 61.4954 | 62.3916 | 64.7751 | 65.5314 | 64.0212 | 62.0907 | 62.2958 | 64.844 | 123.1521 | 61.8545 | 123.0788 | 61.559 | 61.6312 | 123.3093 | 61.5907 | 123.0875 | 61.5209 | 61.5614 | 61.4476 | 61.4881
3925.0625 | 123.2941 | -61.6013 | 61.5509 | 0.68957 | 3.0135 | 3.7699 | 2.4062 | 0.43455 | 0.62125 | 2.4782 | 61.56 | 0.26695 | 61.4775 | -0.033101 | 0.048236 | 61.7081 | 0.003143 | 61.5 | 62.2908 | 64.6148 | 65.3712 | 64.0074 | 62.0358 | 62.2225 | 64.0794 | 123.1612 | 61.8682 | 123.0788 | 61.5682 | 61.6495 | 123.3093 | 61.6044 | 123.1013 | 61.5118 | 61.5568 | 61.4293 | 61.4744
3926.1094 | 123.4039 | -61.6058 | 61.5372 | 0.95054 | 3.1097 | 4.063 | 2.4291 | 0.48033 | 0.57547 | 3.2702 | 61.5463 | 0.26695 | 61.4867 | -0.03768 | 0.039079 | 61.7218 | 0.007721 | 61.4954 | 62.5564 | 64.7155 | 65.6688 | 64.0349 | 62.0862 | 62.1813 | 64.876 | 123.1521 | 61.8728 | 123.0925 | 61.5682 | 61.6449 | 123.3276 | 61.6136 | 123.1013 | 61.5072 | 61.5385 | 61.4476 | 61.4789
3927.0625 | 123.3124 | -61.6333 | 61.5417 | 0.78572 | 3.1326 | 3.9622 | 2.4291 | 0.51695 | 0.67162 | 3.2427 | 61.5463 | 0.26695 | 61.4729 | -0.033101 | 0.048236 | 61.7218 | 0.007721 | 61.5046 | 62.419 | 64.7659 | 65.5955 | 64.0624 | 62.1503 | 62.3049 | 64.876 | 123.1796 | 61.9002 | 123.1062 | 61.6002 | 61.6815 | 123.3551 | 61.641 | 123.1379 | 61.498 | 61.5385 | 61.4247 | 61.4652
3928.0938 | 123.317 | -61.5967 | 61.5463 | 0.59342 | 2.9311 | 3.8249 | 2.3009 | 0.38877 | 0.49306 | 1.8052 | 61.5646 | 0.25779 | 61.4958 | -0.028522 | 0.039079 | 61.7035 | -0.006014 | 61.4817 | 62.1901 | 64.5278 | 65.4215 | 63.8975 | 61.9854 | 62.0897 | 63.4019 | 123.1613 | 61.8545 | 123.0925 | 61.5682 | 61.6358 | 123.3002 | 61.5907 | 123.0784 | 61.5255 | 61.5706 | 61.4567 | 61.5018
3929.0625 | 123.3215 | -61.5601 | 61.6013 | 0.59342 | 2.8899 | 3.4952 | 2.3009 | 0.35672 | 0.41065 | 1.2924 | 61.5783 | 0.26695 | 61.5004 | -0.03768 | 0.043657 | 61.6852 | -0.001436 | 61.4771 | 62.1535 | 64.45 | 65.0553 | 63.8609 | 61.9168 | 61.9707 | 62.8525 | 123.1384 | 61.827 | 123.0605 | 61.5224 | 61.6037 | 123.2452 | 61.5586 | 123.0372 | 61.5346 | 61.5797 | 61.4567 | 61.5018
3930.0938 | 123.3948 | -61.5463 | 61.5555 | 0.57511 | 2.8121 | 3.8935 | 2.3695 | 0.38877 | 0.4839 | 1.329 | 61.5737 | 0.27153 | 61.5096 | -0.03768 | 0.039079 | 61.6989 | 0.003143 | 61.4817 | 62.1214 | 64.3584 | 65.4399 | 63.9159 | 61.9351 | 62.0302 | 62.8754 | 123.1201 | 61.8179 | 123.0559 | 61.5086 | 61.5854 | 123.2452 | 61.5495 | 123.028 | 61.5346 | 61.5706 | 61.4705 | 61.5064
3931.0625 | 123.2941 | -61.5967 | 61.5738 | 0.52017 | 2.7617 | 3.5914 | 2.2825 | 0.34757 | 0.42438 | 1.329 | 61.5829 | 0.26695 | 61.5141 | -0.033101 | 0.043657 | 61.6806 | -0.001436 | 61.4771 | 62.1169 | 64.3584 | 65.188 | 63.8792 | 61.9442 | 62.0211 | 62.9257 | 123.1796 | 61.8636 | 123.1108 | 61.5636 | 61.6403 | 123.2773 | 61.5952 | 123.0738 | 61.5392 | 61.5843 | 61.4705 | 61.5156
3932.0781 | 123.2849 | -61.5692 | 61.5784 | 0.598 | 2.7663 | 3.5868 | 2.2184 | 0.33841 | 0.35571 | 1.3382 | 61.5875 | 0.26237 | 61.505 | -0.033101 | 0.043657 | 61.6852 | 0.007721 | 61.4771 | 62.1672 | 64.3355 | 65.156 | 63.7877 | 61.9076 | 61.9249 | 62.9074 | 123.1567 | 61.8316 | 123.0742 | 61.5361 | 61.6129 | 123.2544 | 61.5769 | 123.0463 | 61.5438 | 61.5797 | 61.4613 | 61.4973
3933.0625 | 123.3353 | -61.5738 | 61.5875 | 0.51101 | 2.7663 | 3.3991 | 2.2413 | 0.39335 | 0.39691 | 1.3703 | 61.5875 | 0.25779 | 61.5096 | -0.03768 | 0.039079 | 61.6852 | 0.007721 | 61.4725 | 62.0848 | 64.3401 | 64.9729 | 63.8151 | 61.9671 | 61.9707 | 62.944 | 123.1613 | 61.8316 | 123.0833 | 61.5361 | 61.6129 | 123.259 | 61.5815 | 123.0463 | 61.5484 | 61.5797 | 61.4705 | 61.5018
3934.0938 | 123.4222 | -61.5875 | 61.5601 | 0.54764 | 2.7709 | 3.7562 | 2.3238 | 0.40708 | 0.4427 | 1.4023 | 61.5691 | 0.26695 | 61.4912 | -0.028522 | 0.048236 | 61.6943 | 0.003143 | 61.4725 | 62.1352 | 64.3584 | 65.3437 | 63.9113 | 61.9946 | 62.0302 | 62.9898 | 123.1567 | 61.8545 | 123.0788 | 61.559 | 61.6358 | 123.2819 | 61.5907 | 123.0601 | 61.5209 | 61.566 | 61.443 | 61.4881
3935.0625 | 123.262 | -61.5967 | 61.5646 | 0.58427 | 2.7159 | 3.7425 | 2.3512 | 0.43912 | 0.47932 | 1.3382 | 61.5783 | 0.26237 | 61.5233 | -0.042259 | 0.039079 | 61.6943 | 0.003143 | 61.4771 | 62.1809 | 64.3126 | 65.3391 | 63.9479 | 62.0358 | 62.076 | 62.9349 | 123.175 | 61.859 | 123.12 | 61.5544 | 61.6358 | 123.291 | 61.5998 | 123.0738 | 61.5392 | 61.5752 | 61.4842 | 61.5202
3936.0938 | 123.4131 | -61.5646 | 61.5692 | 0.55222 | 2.7068 | 3.8844 | 2.3329 | 0.38419 | 0.46559 | 1.2924 | 61.5783 | 0.25779 | 61.4775 | -0.028522 | 0.043657 | 61.6898 | 0.003143 | 61.4725 | 62.1169 | 64.2714 | 65.449 | 63.8975 | 61.9488 | 62.0302 | 62.8571 | 123.1429 | 61.8224 | 123.0421 | 61.5361 | 61.6083 | 123.2544 | 61.5678 | 123.0372 | 61.5346 | 61.5752 | 61.4339 | 61.4744
3937.0625 | 123.3536 | -61.5692 | 61.5692 | 0.5568 | 2.7113 | 3.8432 | 2.31 | 0.37046 | 0.47017 | 1.3199 | 61.5783 | 0.26695 | 61.5187 | -0.033101 | 0.043657 | 61.6898 | 0.003143 | 61.4863 | 62.126 | 64.2806 | 65.4124 | 63.8792 | 61.9397 | 62.0394 | 62.8891 | 123.1475 | 61.8362 | 123.0879 | 61.5361 | 61.6129 | 123.259 | 61.5724 | 123.0555 | 61.5346 | 61.5752 | 61.4751 | 61.5156
3938.0781 | 123.3948 | -61.5555 | 61.5372 | 0.56595 | 2.6656 | 3.8066 | 2.2871 | 0.37046 | 0.47475 | 1.3794 | 61.5737 | 0.26237 | 61.4821 | -0.033101 | 0.043657 | 61.6943 | 0.003143 | 61.4771 | 62.1214 | 64.221 | 65.362 | 63.8426 | 61.9259 | 62.0302 | 62.9349 | 123.1292 | 61.8179 | 123.0376 | 61.5224 | 61.5991 | 123.2498 | 61.5586 | 123.0326 | 61.5301 | 61.5706 | 61.4384 | 61.4789
3939.0625 | 123.3032 | -61.5784 | 61.5738 | 0.58885 | 2.5419 | 3.6371 | 2.2505 | 0.36588 | 0.49764 | 1.3565 | 61.5829 | 0.26695 | 61.5233 | -0.023943 | 0.043657 | 61.6943 | 0.003143 | 61.4725 | 62.1672 | 64.1203 | 65.2155 | 63.8289 | 61.9442 | 62.076 | 62.9349 | 123.1613 | 61.8453 | 123.1017 | 61.5544 | 61.622 | 123.2727 | 61.5815 | 123.0509 | 61.5392 | 61.5797 | 61.4796 | 61.5202
3940.0781 | 123.3261 | -61.5692 | 61.5921 | 0.56138 | 2.4824 | 3.6875 | 2.2322 | 0.36588 | 0.48848 | 1.3336 | 61.5737 | 0.26237 | 61.4867 | -0.033101 | 0.039079 | 61.6943 | 0.012299 | 61.4817 | 62.1306 | 64.0516 | 65.2567 | 63.8014 | 61.9351 | 62.0577 | 62.9028 | 123.1429 | 61.8316 | 123.0559 | 61.5361 | 61.6083 | 123.2636 | 61.5815 | 123.0509 | 61.5346 | 61.5614 | 61.4476 | 61.4744
3941.0625 | 123.3673 | -61.5829 | 61.528 | 0.78572 | 2.5007 | 3.8157 | 2.2093 | 0.35672 | 0.38318 | 1.2375 | 61.5875 | 0.26237 | 61.5233 | -0.03768 | 0.039079 | 61.6852 | 0.003143 | 61.468 | 62.3687 | 64.0837 | 65.3987 | 63.7922 | 61.9397 | 61.9661 | 62.8204 | 123.1704 | 61.8453 | 123.1062 | 61.5453 | 61.622 | 123.2681 | 61.5861 | 123.0509 | 61.5484 | 61.5843 | 61.4842 | 61.5202
3942.0938 | 123.3078 | -61.5875 | 61.6104 | 0.57511 | 2.5053 | 4.0172 | 2.1635 | 0.38419 | 0.49306 | 1.2421 | 61.5691 | 0.26237 | 61.4867 | -0.033101 | 0.048236 | 61.6943 | 0.007721 | 61.4725 | 62.1626 | 64.0928 | 65.6047 | 63.751 | 61.9717 | 62.0806 | 62.8296 | 123.1567 | 61.8499 | 123.0742 | 61.5544 | 61.6358 | 123.2819 | 61.5952 | 123.0601 | 61.5209 | 61.5614 | 61.4384 | 61.4789
3943.0625 | 123.2895 | -61.615 | 61.5738 | 0.56595 | 2.6015 | 3.8661 | 2.1727 | 0.41166 | 0.4839 | 1.3062 | 61.5783 | 0.26237 | 61.5141 | -0.033101 | 0.043657 | 61.6806 | -0.006014 | 61.4725 | 62.1809 | 64.2164 | 65.4811 | 63.7877 | 62.0266 | 62.0989 | 62.9211 | 123.1933 | 61.8774 | 123.1291 | 61.5819 | 61.6586 | 123.2956 | 61.609 | 123.0875 | 61.5346 | 61.5843 | 61.4705 | 61.5202
3944.0625 | 123.3902 | -61.5372 | 61.5234 | 0.52475 | 2.5786 | 3.8249 | 2.2139 | 0.40708 | 0.45185 | 1.329 | 61.5691 | 0.27153 | 61.4912 | -0.03768 | 0.043657 | 61.6898 | 0.003143 | 61.4771 | 62.0619 | 64.1157 | 65.362 | 63.751 | 61.9442 | 61.989 | 62.8662 | 123.1063 | 61.8087 | 123.0284 | 61.4995 | 61.5808 | 123.2269 | 61.5403 | 123.0143 | 61.5255 | 61.566 | 61.4476 | 61.4881
3945.0781 | 123.3444 | -61.5784 | 61.5829 | 0.57053 | 2.5145 | 3.9119 | 2.2597 | 0.42081 | 0.50222 | 1.3519 | 61.5783 | 0.26237 | 61.5141 | -0.03768 | 0.052814 | 61.6898 | 0.003143 | 61.4725 | 62.1489 | 64.0928 | 65.4902 | 63.838 | 61.9992 | 62.0806 | 62.9303 | 123.1567 | 61.8407 | 123.0925 | 61.5407 | 61.6312 | 123.2681 | 61.5815 | 123.0509 | 61.5255 | 61.5752 | 61.4613 | 61.511
3946.0625 | 123.3444 | -61.5646 | 61.5372 | 0.54764 | 2.4687 | 3.8661 | 2.1681 | 0.40708 | 0.46559 | 1.3153 | 61.5737 | 0.26237 | 61.4867 | -0.03768 | 0.048236 | 61.6943 | 0.003143 | 61.468 | 62.1123 | 64.0333 | 65.4307 | 63.7327 | 61.9717 | 62.0302 | 62.8799 | 123.1384 | 61.827 | 123.0513 | 61.527 | 61.6129 | 123.259 | 61.5678 | 123.0326 | 61.5255 | 61.5706 | 61.4384 | 61.4835
3947.0938 | 123.4268 | -61.5417 | 61.5372 | 0.54306 | 2.4824 | 3.8157 | 2.1727 | 0.4025 | 0.46559 | 1.3153 | 61.5691 | 0.26695 | 61.5141 | -0.03768 | 0.048236 | 61.6852 | 0.003143 | 61.468 | 62.0848 | 64.0242 | 65.3575 | 63.7144 | 61.9442 | 62.0073 | 62.8571 | 123.1109 | 61.8087 | 123.0559 | 61.5041 | 61.59 | 123.2269 | 61.5449 | 123.0097 | 61.5209 | 61.566 | 61.4659 | 61.511
3948.7031 | 123.4039 | -61.5555 | 61.5326 | 0.56138 | 2.487 | 3.7562 | 2.3695 | 0.4437 | 0.47932 | 1.3199 | 61.5783 | 0.26695 | 61.4867 | -0.023943 | 0.043657 | 61.6943 | 0.007721 | 61.468 | 62.1169 | 64.0425 | 65.3117 | 63.925 | 61.9992 | 62.0348 | 62.8754 | 123.1338 | 61.8224 | 123.0421 | 61.5315 | 61.5991 | 123.2498 | 61.5632 | 123.0234 | 61.5346 | 61.5706 | 61.443 | 61.4789
3949.3438 | 123.3994 | -61.5417 | 61.5875 | 0.51101 | 2.345 | 3.7653 | 2.2963 | 0.38419 | 0.43354 | 1.2833 | 61.5875 | 0.27153 | 61.5233 | -0.023943 | 0.043657 | 61.6943 | 0.003143 | 61.4771 | 62.0528 | 63.8868 | 65.3071 | 63.838 | 61.9259 | 61.9753 | 62.825 | 123.1292 | 61.8133 | 123.065 | 61.5178 | 61.5854 | 123.2361 | 61.5449 | 123.0189 | 61.5438 | 61.5843 | 61.4796 | 61.5202
3950.7188 | 123.3627 | -61.5738 | 61.5372 | 0.57969 | 2.5923 | 4.0217 | 2.2825 | 0.42081 | 0.51137 | 1.4435 | 61.5783 | 0.26695 | 61.4867 | -0.028522 | 0.048236 | 61.6898 | -0.001436 | 61.4725 | 62.1535 | 64.1661 | 65.5955 | 63.8563 | 61.9946 | 62.0852 | 63.0173 | 123.1521 | 61.8407 | 123.0605 | 61.5453 | 61.622 | 123.2636 | 61.5724 | 123.0463 | 61.5301 | 61.5797 | 61.4384 | 61.4881
3951.1562 | 123.2895 | -61.6104 | 61.5738 | 0.598 | 2.6015 | 3.9989 | 2.2642 | 0.42539 | 0.51137 | 1.4755 | 61.5783 | 0.26695 | 61.5096 | -0.028522 | 0.048236 | 61.6989 | 0.003143 | 61.4725 | 62.2084 | 64.2119 | 65.6093 | 63.8746 | 62.0358 | 62.1218 | 63.086 | 123.1887 | 61.8774 | 123.12 | 61.5819 | 61.6586 | 123.3093 | 61.6136 | 123.083 | 61.5301 | 61.5752 | 61.4613 | 61.5064
3952.9219 | 123.3353 | -61.5829 | 61.5051 | 0.58427 | 2.5282 | 4.1957 | 2.1681 | 0.40708 | 0.49764 | 1.3382 | 61.5646 | 0.26237 | 61.4867 | -0.033101 | 0.043657 | 61.6898 | 0.003143 | 61.4817 | 62.1672 | 64.1111 | 65.7787 | 63.751 | 61.99 | 62.0806 | 62.9212 | 123.1475 | 61.8453 | 123.0696 | 61.5498 | 61.6266 | 123.2727 | 61.5861 | 123.0646 | 61.5209 | 61.5614 | 61.443 | 61.4835
3953.8438 | 123.3582 | -61.5692 | 61.5234 | 0.58885 | 2.5465 | 4.2782 | 2.2047 | 0.42081 | 0.48848 | 1.3977 | 61.5737 | 0.26695 | 61.5096 | -0.03768 | 0.048236 | 61.6943 | 0.003143 | 61.4771 | 62.1581 | 64.1157 | 65.8474 | 63.7739 | 61.99 | 62.0577 | 62.9669 | 123.1429 | 61.8362 | 123.0788 | 61.5315 | 61.6175 | 123.2636 | 61.5724 | 123.0463 | 61.5255 | 61.5706 | 61.4613 | 61.5064
3954.3125 | 123.2895 | -61.5601 | 61.5967 | 0.60258 | 2.5694 | 4.1316 | 2.2413 | 0.42539 | 0.51137 | 1.4343 | 61.5691 | 0.26237 | 61.4867 | -0.042259 | 0.048236 | 61.6943 | 0.007721 | 61.4863 | 62.1626 | 64.1295 | 65.6917 | 63.8014 | 61.9855 | 62.0714 | 62.9944 | 123.1292 | 61.8224 | 123.0467 | 61.5178 | 61.6083 | 123.2544 | 61.5678 | 123.0463 | 61.5209 | 61.5614 | 61.4384 | 61.4789
3955.4531 | 123.3032 | -61.5875 | 61.5875 | 0.67126 | 2.6244 | 4.095 | 2.2551 | 0.48033 | 0.62125 | 2.4232 | 61.5691 | 0.26237 | 61.5004 | -0.03768 | 0.043657 | 61.7127 | 0.007721 | 61.4909 | 62.2588 | 64.2119 | 65.6825 | 63.8426 | 62.0679 | 62.2088 | 64.0108 | 123.1567 | 61.8499 | 123.0879 | 61.5498 | 61.6312 | 123.3002 | 61.5952 | 123.0784 | 61.5255 | 61.5614 | 61.4567 | 61.4927
3959.3438 | 123.3582 | -61.5967 | 61.5601 | 0.7903 | 2.6381 | 3.7196 | 2.5389 | 0.51237 | 0.7174 | 2.6064 | 61.56 | 0.26695 | 61.4912 | -0.03768 | 0.039079 | 61.7081 | -0.001436 | 61.4863 | 62.387 | 64.2348 | 65.3162 | 64.1356 | 62.1091 | 62.3141 | 64.203 | 123.1567 | 61.8636 | 123.0879 | 61.559 | 61.6358 | 123.3048 | 61.5952 | 123.083 | 61.5209 | 61.5614 | 61.4522 | 61.4927
3959.7656 | 123.4131 | -61.5784 | 61.5463 | 0.70331 | 2.5877 | 3.6646 | 2.5344 | 0.48948 | 0.63957 | 1.6816 | 61.5783 | 0.26237 | 61.505 | -0.033101 | 0.043657 | 61.7035 | -0.001436 | 61.4725 | 62.2817 | 64.1661 | 65.243 | 64.1127 | 62.0679 | 62.2179 | 63.2599 | 123.1567 | 61.8407 | 123.0833 | 61.5453 | 61.622 | 123.2819 | 61.5769 | 123.0509 | 61.5346 | 61.5797 | 61.4613 | 61.5064
3960.1875 | 123.4085 | -61.5921 | 61.4822 | 0.69415 | 2.6244 | 3.5547 | 2.5252 | 0.50322 | 0.62583 | 1.7777 | 61.5691 | 0.26695 | 61.505 | -0.033101 | 0.043657 | 61.7035 | -0.006014 | 61.4817 | 62.2863 | 64.2165 | 65.1468 | 64.1173 | 62.0953 | 62.2179 | 63.3698 | 123.1613 | 61.8591 | 123.0971 | 61.559 | 61.6358 | 123.2956 | 61.5861 | 123.0738 | 61.5255 | 61.5752 | 61.4613 | 61.511
3961.1094 | 123.4177 | -61.5875 | 61.5143 | 0.63005 | 2.7113 | 3.6051 | 2.4107 | 0.49864 | 0.56173 | 1.7777 | 61.5691 | 0.26237 | 61.4684 | -0.042259 | 0.039079 | 61.6852 | 0.003143 | 61.4817 | 62.2176 | 64.2989 | 65.1926 | 63.9983 | 62.0862 | 62.1493 | 63.3652 | 123.1567 | 61.8499 | 123.0559 | 61.5453 | 61.6266 | 123.2727 | 61.5907 | 123.0692 | 61.5301 | 61.566 | 61.4293 | 61.4652
3962.0625 | 123.3261 | -61.6058 | 61.5555 | 0.78572 | 2.8624 | 3.6509 | 2.3924 | 0.56731 | 0.72656 | 3.9615 | 61.5508 | 0.26237 | 61.4867 | -0.03768 | 0.043657 | 61.7218 | 0.007721 | 61.5092 | 62.3916 | 64.4683 | 65.2567 | 63.9983 | 62.1731 | 62.3324 | 65.5673 | 123.1567 | 61.8682 | 123.0925 | 61.5682 | 61.6495 | 123.3276 | 61.6136 | 123.115 | 61.5072 | 61.5431 | 61.443 | 61.4789
3963.0938 | 123.4039 | -61.5646 | 61.5234 | 0.81777 | 2.8533 | 3.7837 | 2.3924 | 0.58104 | 0.74945 | 4.0531 | 61.5463 | 0.26237 | 61.4592 | -0.03768 | 0.048236 | 61.7172 | -0.001436 | 61.5046 | 62.3824 | 64.4179 | 65.3483 | 63.9571 | 62.1457 | 62.3141 | 65.6177 | 123.1109 | 61.827 | 123.0238 | 61.527 | 61.6129 | 123.2819 | 61.5632 | 123.0692 | 61.498 | 61.5477 | 61.411 | 61.4606
3964.0625 | 123.2895 | -61.6013 | 61.5555 | 0.70788 | 2.7617 | 3.9073 | 2.3878 | 0.51695 | 0.63499 | 2.7345 | 61.5646 | 0.26237 | 61.4958 | -0.03768 | 0.048236 | 61.7081 | 0.003143 | 61.5046 | 62.3091 | 64.363 | 65.5085 | 63.9891 | 62.1182 | 62.2362 | 64.3358 | 123.1658 | 61.8636 | 123.0971 | 61.5636 | 61.6495 | 123.3093 | 61.6044 | 123.1058 | 61.5163 | 61.5614 | 61.4476 | 61.4927
3965.0625 | 123.2849 | -61.6241 | 61.5646 | 0.80861 | 2.8533 | 4.1133 | 2.4474 | 0.59478 | 0.72198 | 3.7601 | 61.5463 | 0.26237 | 61.4638 | -0.03768 | 0.043657 | 61.7172 | 0.003143 | 61.5183 | 62.4328 | 64.4774 | 65.7375 | 64.0715 | 62.2189 | 62.3461 | 65.3842 | 123.1704 | 61.8865 | 123.0879 | 61.5865 | 61.6678 | 123.3414 | 61.6273 | 123.1425 | 61.5026 | 61.5431 | 61.4201 | 61.4606
3966.0625 | 123.3856 | -61.5921 | 61.4914 | 0.79945 | 2.7709 | 4.1728 | 2.4291 | 0.58562 | 0.67619 | 2.8536 | 61.5508 | 0.26237 | 61.4958 | -0.03768 | 0.043657 | 61.7081 | 0.003143 | 61.5092 | 62.3916 | 64.363 | 65.7649 | 64.0212 | 62.1777 | 62.2683 | 64.4457 | 123.1429 | 61.8545 | 123.0879 | 61.5544 | 61.6358 | 123.3002 | 61.5952 | 123.1013 | 61.5072 | 61.5477 | 61.4522 | 61.4927
3967.0625 | 123.2941 | -61.5967 | 61.5738 | 0.7903 | 2.6793 | 4.1408 | 2.3421 | 0.55815 | 0.69909 | 2.9451 | 61.5554 | 0.26237 | 61.4821 | -0.033101 | 0.043657 | 61.7127 | 0.003143 | 61.5 | 62.387 | 64.276 | 65.7375 | 63.9387 | 62.1548 | 62.2958 | 64.5418 | 123.1521 | 61.859 | 123.0788 | 61.5636 | 61.6403 | 123.3093 | 61.5998 | 123.0967 | 61.5118 | 61.5523 | 61.4384 | 61.4789
3968.0938 | 123.3078 | -61.5738 | 61.5784 | 0.71246 | 2.6289 | 3.9348 | 2.2688 | 0.54442 | 0.63041 | 2.8215 | 61.5508 | 0.26237 | 61.4729 | -0.03768 | 0.043657 | 61.7081 | 0.003143 | 61.5 | 62.2863 | 64.2027 | 65.5085 | 63.8426 | 62.1182 | 62.2042 | 64.3953 | 123.1246 | 61.8362 | 123.0467 | 61.5361 | 61.6174 | 123.2819 | 61.5769 | 123.0738 | 61.5072 | 61.5477 | 61.4293 | 61.4698
3969.0625 | 123.2941 | -61.5875 | 61.5967 | 0.60258 | 2.5236 | 4.0675 | 2.2734 | 0.50779 | 0.53426 | 1.2146 | 61.5829 | 0.26695 | 61.5187 | -0.03768 | 0.043657 | 61.6943 | -0.006014 | 61.4863 | 62.1901 | 64.1111 | 65.6551 | 63.8609 | 62.0953 | 62.1218 | 62.8021 | 123.1704 | 61.8545 | 123.1062 | 61.5498 | 61.6312 | 123.2819 | 61.5815 | 123.0738 | 61.5392 | 61.5889 | 61.4751 | 61.5247
3970.0625 | 123.2803 | -61.5738 | 61.6013 | 0.6621 | 2.5145 | 3.8935 | 2.278 | 0.53984 | 0.57547 | 1.4206 | 61.5691 | 0.26695 | 61.4775 | -0.03768 | 0.048236 | 61.6943 | -0.001436 | 61.4954 | 62.2359 | 64.0883 | 65.4673 | 63.8518 | 62.1136 | 62.1493 | 62.9944 | 123.1429 | 61.8407 | 123.0513 | 61.5361 | 61.622 | 123.2681 | 61.5724 | 123.0692 | 61.5209 | 61.5706 | 61.4293 | 61.4789
3971.0625 | 123.2895 | -61.5784 | 61.5692 | 0.64837 | 2.5282 | 3.889 | 2.3512 | 0.49864 | 0.58005 | 1.9013 | 61.5783 | 0.26695 | 61.5096 | -0.033101 | 0.039079 | 61.6989 | 0.012299 | 61.4954 | 62.2267 | 64.1066 | 65.4673 | 63.9296 | 62.077 | 62.1584 | 63.4797 | 123.1567 | 61.8453 | 123.0879 | 61.5453 | 61.6174 | 123.2773 | 61.5907 | 123.0738 | 61.5392 | 61.566 | 61.4705 | 61.4973
3972.0625 | 123.317 | -61.6013 | 61.5967 | 0.58885 | 2.4824 | 3.8752 | 2.3878 | 0.45286 | 0.52511 | 1.7228 | 61.5783 | 0.26695 | 61.505 | -0.023943 | 0.043657 | 61.6943 | 0.003143 | 61.4863 | 62.1901 | 64.0837 | 65.4765 | 63.9891 | 62.0541 | 62.1264 | 63.324 | 123.1796 | 61.8682 | 123.1062 | 61.5773 | 61.6449 | 123.2956 | 61.6044 | 123.0875 | 61.5346 | 61.5752 | 61.4613 | 61.5018
3973.0625 | 123.3582 | -61.5921 | 61.5784 | 0.57511 | 2.5328 | 4.063 | 2.2597 | 0.39792 | 0.48848 | 1.5717 | 61.5783 | 0.26695 | 61.5233 | -0.028522 | 0.048236 | 61.6898 | 0.003143 | 61.4863 | 62.1672 | 64.1249 | 65.6551 | 63.8518 | 61.99 | 62.0806 | 63.1638 | 123.1704 | 61.8591 | 123.1154 | 61.5636 | 61.6403 | 123.2819 | 61.5952 | 123.0784 | 61.5301 | 61.5752 | 61.4751 | 61.5202
3974.0625 | 123.2712 | -61.5509 | 61.615 | 0.598 | 2.4275 | 4.0904 | 2.1635 | 0.47117 | 0.51137 | 1.6266 | 61.5646 | 0.26695 | 61.5004 | -0.019364 | 0.048236 | 61.6943 | 0.007721 | 61.4771 | 62.1489 | 63.9784 | 65.6413 | 63.7144 | 62.0221 | 62.0623 | 63.1775 | 123.1155 | 61.8179 | 123.0513 | 61.5315 | 61.5991 | 123.2452 | 61.5586 | 123.028 | 61.5163 | 61.5569 | 61.4522 | 61.4927
3975.0938 | 123.4451 | -61.5372 | 61.5463 | 0.60258 | 2.2993 | 4.0904 | 2.0902 | 0.48033 | 0.51595 | 1.622 | 61.5783 | 0.26695 | 61.5141 | -0.033101 | 0.043657 | 61.6943 | 0.007721 | 61.4817 | 62.1398 | 63.8364 | 65.6276 | 63.6274 | 62.0175 | 62.0531 | 63.1592 | 123.1155 | 61.8041 | 123.0513 | 61.5041 | 61.5808 | 123.2315 | 61.5449 | 123.0189 | 61.5346 | 61.5706 | 61.4705 | 61.5064
3976.0625 | 123.2895 | -61.6196 | 61.5509 | 0.65752 | 2.5557 | 4.2507 | 2.2459 | 0.58562 | 0.58005 | 1.6129 | 61.5646 | 0.25779 | 61.4821 | -0.03768 | 0.048236 | 61.6943 | 0.007721 | 61.4863 | 62.2771 | 64.1752 | 65.8702 | 63.8655 | 62.2052 | 62.1996 | 63.2325 | 123.1841 | 61.8774 | 123.1017 | 61.5819 | 61.6678 | 123.3139 | 61.6273 | 123.1058 | 61.5163 | 61.5569 | 61.4339 | 61.4744
3977.0938 | 123.3994 | -61.5646 | 61.5646 | 0.61632 | 2.5831 | 4.1133 | 2.0765 | 0.57646 | 0.54342 | 1.4984 | 61.5737 | 0.26237 | 61.4867 | -0.028522 | 0.043657 | 61.6943 | 0.007721 | 61.4863 | 62.181 | 64.1478 | 65.678 | 63.6411 | 62.1411 | 62.1081 | 63.0631 | 123.1384 | 61.827 | 123.0513 | 61.5361 | 61.6083 | 123.259 | 61.5724 | 123.0509 | 61.5301 | 61.566 | 61.443 | 61.4789
3978.0625 | 123.3215 | -61.5967 | 61.5463 | 0.60716 | 2.6198 | 4.1087 | 2.0307 | 0.60393 | 0.52511 | 1.6678 | 61.5783 | 0.27153 | 61.505 | -0.033101 | 0.039079 | 61.7035 | 0.003143 | 61.4725 | 62.2038 | 64.2165 | 65.7054 | 63.6274 | 62.2006 | 62.1218 | 63.2645 | 123.175 | 61.8682 | 123.1017 | 61.5636 | 61.6358 | 123.3002 | 61.5998 | 123.0692 | 61.5392 | 61.5752 | 61.4659 | 61.5018
3979.0625 | 123.3307 | -61.5646 | 61.6196 | 0.57969 | 2.4961 | 3.9119 | 2.1223 | 0.55815 | 0.50679 | 1.7136 | 61.5691 | 0.25321 | 61.4912 | -0.028522 | 0.048236 | 61.6898 | 0.012299 | 61.4771 | 62.1443 | 64.0608 | 65.4765 | 63.6869 | 62.1228 | 62.0714 | 63.2782 | 123.1338 | 61.8178 | 123.0559 | 61.5361 | 61.6129 | 123.2544 | 61.5769 | 123.0418 | 61.5209 | 61.5569 | 61.443 | 61.4789
3980.0781 | 123.3582 | -61.5601 | 61.5829 | 0.58885 | 2.5557 | 4.0858 | 2.2413 | 0.58104 | 0.51595 | 1.7457 | 61.5737 | 0.26695 | 61.505 | -0.033101 | 0.048236 | 61.6943 | 0.007721 | 61.4725 | 62.1489 | 64.1157 | 65.6459 | 63.8014 | 62.1411 | 62.076 | 63.3057 | 123.1338 | 61.827 | 123.065 | 61.527 | 61.6083 | 123.2544 | 61.5678 | 123.0326 | 61.5255 | 61.566 | 61.4567 | 61.4973
3981.0625 | 123.3124 | -61.6196 | 61.5509 | 0.79945 | 2.7342 | 4.1454 | 2.3375 | 0.69549 | 0.70824 | 3.9386 | 61.5463 | 0.26695 | 61.45 | -0.028522 | 0.039079 | 61.7218 | -0.001436 | 61.5 | 62.419 | 64.3538 | 65.7649 | 63.9571 | 62.3151 | 62.3278 | 65.5582 | 123.1658 | 61.8865 | 123.0696 | 61.591 | 61.6586 | 123.3414 | 61.6181 | 123.1196 | 61.5072 | 61.5477 | 61.411 | 61.4515
3982.0781 | 123.3444 | -61.6425 | 61.4822 | 0.88186 | 2.6472 | 4.2232 | 2.3741 | 0.69549 | 0.76318 | 4.1767 | 61.5508 | 0.26237 | 61.4867 | -0.033101 | 0.039079 | 61.7355 | -0.001436 | 61.5 | 62.5243 | 64.2897 | 65.8657 | 64.0166 | 62.3379 | 62.4056 | 65.8191 | 123.1933 | 61.9048 | 123.1291 | 61.6094 | 61.6815 | 123.378 | 61.641 | 123.1425 | 61.5118 | 61.5523 | 61.4476 | 61.4881
3983.0625 | 123.2849 | -61.647 | 61.5417 | 0.8315 | 2.7113 | 4.3606 | 2.2642 | 0.755 | 0.75861 | 3.8699 | 61.5463 | 0.26237 | 61.4409 | -0.023943 | 0.043657 | 61.7218 | 0.003143 | 61.5092 | 62.4785 | 64.3584 | 66.0076 | 63.9113 | 62.402 | 62.4056 | 65.517 | 123.1933 | 61.9094 | 123.0879 | 61.6231 | 61.6907 | 123.3688 | 61.6502 | 123.1562 | 61.5026 | 61.5431 | 61.3972 | 61.4377
3984.0781 | 123.4177 | -61.5784 | 61.5555 | 0.67584 | 2.5557 | 4.2782 | 1.9895 | 0.60851 | 0.59378 | 2.4873 | 61.5646 | 0.27153 | 61.5004 | -0.033101 | 0.057392 | 61.7035 | 0.007721 | 61.4817 | 62.2542 | 64.134 | 65.8565 | 63.5679 | 62.1869 | 62.1722 | 64.0657 | 123.1429 | 61.8499 | 123.0788 | 61.5453 | 61.6358 | 123.2819 | 61.5861 | 123.0601 | 61.5072 | 61.5569 | 61.443 | 61.4927
3985.0625 | 123.2986 | -61.6013 | 61.5372 | 0.7903 | 2.6244 | 4.2644 | 2.0719 | 0.6726 | 0.69909 | 4.1538 | 61.5417 | 0.27153 | 61.45 | -0.028522 | 0.039079 | 61.7218 | 0.007721 | 61.5046 | 62.3916 | 64.2256 | 65.8657 | 63.6732 | 62.2739 | 62.3003 | 65.755 | 123.1429 | 61.8728 | 123.0513 | 61.5727 | 61.6403 | 123.3231 | 61.609 | 123.1058 | 61.5026 | 61.534 | 61.411 | 61.4423
3986.0938 | 123.3673 | -61.5875 | 61.4594 | 0.74909 | 2.4733 | 4.2553 | 2.0765 | 0.62682 | 0.66246 | 3.9066 | 61.56 | 0.26695 | 61.4867 | -0.03768 | 0.039079 | 61.7218 | -0.001436 | 61.4817 | 62.3366 | 64.0608 | 65.8428 | 63.664 | 62.2143 | 62.25 | 65.4941 | 123.1475 | 61.8545 | 123.0742 | 61.5498 | 61.6266 | 123.3093 | 61.5861 | 123.0692 | 61.5209 | 61.5614 | 61.4476 | 61.4881
3987.0625 | 123.3261 | -61.6196 | 61.5509 | 1.3168 | 2.7663 | 4.388 | 2.2413 | 0.67718 | 0.22751 | 3.9844 | 61.5463 | 0.26237 | 61.4546 | -0.028522 | 0.043657 | 61.7218 | 0.007721 | 61.5137 | 62.9364 | 64.3859 | 66.0076 | 63.8609 | 62.2967 | 61.8471 | 65.604 | 123.1658 | 61.8819 | 123.0742 | 61.591 | 61.6632 | 123.3414 | 61.6273 | 123.1333 | 61.5026 | 61.5385 | 61.411 | 61.4469
3988.0938 | 123.4039 | -61.5738 | 61.5417 | 0.68041 | 2.5511 | 4.4613 | 2.3741 | 0.66802 | 0.58005 | 2.35 | 61.5646 | 0.26237 | 61.4912 | -0.033101 | 0.048236 | 61.7035 | 0.003143 | 61.4863 | 62.2542 | 64.1249 | 66.0351 | 63.9479 | 62.2418 | 62.1538 | 63.9238 | 123.1384 | 61.8362 | 123.065 | 61.5407 | 61.622 | 123.2773 | 61.5769 | 123.0601 | 61.5163 | 61.5614 | 61.443 | 61.4881
3989.0625 | 123.2666 | -61.6196 | 61.5601 | 0.69415 | 2.6564 | 4.5529 | 2.2642 | 0.69091 | 0.60752 | 2.4187 | 61.56 | 0.26695 | 61.4729 | -0.033101 | 0.043657 | 61.7127 | 0.003143 | 61.5046 | 62.3137 | 64.276 | 66.1724 | 63.8838 | 62.3105 | 62.2271 | 64.0382 | 123.1796 | 61.8865 | 123.0925 | 61.5865 | 61.6632 | 123.3322 | 61.6227 | 123.1242 | 61.5163 | 61.5568 | 61.4293 | 61.4698
3990.0781 | 123.3994 | -61.5463 | 61.5326 | 0.62089 | 2.4687 | 4.4659 | 2.0261 | 0.61309 | 0.53884 | 2.3179 | 61.56 | 0.26237 | 61.4958 | -0.03768 | 0.039079 | 61.7081 | 0.007721 | 61.4909 | 62.1672 | 64.015 | 66.0122 | 63.5725 | 62.1594 | 62.0852 | 63.8643 | 123.1063 | 61.8087 | 123.0421 | 61.5086 | 61.5854 | 123.2544 | 61.554 | 123.0372 | 61.5209 | 61.5523 | 61.4567 | 61.4881
3991.0625 | 123.3719 | -61.5784 | 61.5051 | 0.68957 | 2.5099 | 4.5483 | 1.9575 | 0.66802 | 0.60752 | 2.3912 | 61.5554 | 0.25779 | 61.4867 | -0.028522 | 0.043657 | 61.7081 | -0.006014 | 61.4863 | 62.2679 | 64.0882 | 66.1267 | 63.5358 | 62.2464 | 62.1859 | 63.9696 | 123.1338 | 61.8362 | 123.065 | 61.5498 | 61.622 | 123.2864 | 61.5724 | 123.0646 | 61.5118 | 61.5614 | 61.443 | 61.4927
3992.0938 | 123.4497 | -61.5692 | 61.5189 | 1.1932 | 2.6152 | 4.4979 | 2.2459 | 0.69549 | 0.14968 | 2.4278 | 61.5508 | 0.26695 | 61.4958 | -0.033101 | 0.043657 | 61.7081 | 0.003143 | 61.5046 | 62.7624 | 64.1844 | 66.0671 | 63.8151 | 62.2647 | 61.7189 | 63.997 | 123.12 | 61.8362 | 123.065 | 61.5361 | 61.6129 | 123.2773 | 61.5724 | 123.0738 | 61.5072 | 61.5477 | 61.4522 | 61.4927
3993.0625 | 123.3353 | -61.6241 | 61.5646 | 0.72162 | 2.6106 | 4.5117 | 2.2505 | 0.69091 | 0.66246 | 2.6979 | 61.5554 | 0.26237 | 61.4958 | -0.033101 | 0.039079 | 61.7127 | -0.001436 | 61.4954 | 62.3458 | 64.2348 | 66.1358 | 63.8746 | 62.3151 | 62.2866 | 64.3221 | 123.1796 | 61.8865 | 123.12 | 61.591 | 61.6632 | 123.3368 | 61.6227 | 123.1196 | 61.5163 | 61.5568 | 61.4567 | 61.4973
3994.0938 | 123.349 | -61.5921 | 61.5097 | 1.1886 | 2.5053 | 4.443 | 2.1772 | 0.64971 | 0.19546 | 2.5697 | 61.56 | 0.26237 | 61.5004 | -0.03768 | 0.043657 | 61.7218 | -0.010593 | 61.5 | 62.7807 | 64.0974 | 66.0351 | 63.7693 | 62.2418 | 61.7876 | 64.1618 | 123.1521 | 61.8545 | 123.0925 | 61.5544 | 61.6358 | 123.3139 | 61.5815 | 123.0921 | 61.5163 | 61.5706 | 61.4567 | 61.511
3995.0625 | 123.3124 | -61.6104 | 61.5875 | 0.7262 | 2.2352 | 4.3514 | 2.2505 | 0.63598 | 0.64415 | 2.5468 | 61.56 | 0.26695 | 61.4958 | -0.028522 | 0.048236 | 61.7127 | 0.007721 | 61.5 | 62.3366 | 63.8456 | 65.9618 | 63.8609 | 62.2464 | 62.2546 | 64.1573 | 123.1704 | 61.8774 | 123.1062 | 61.5819 | 61.6586 | 123.3231 | 61.6181 | 123.1104 | 61.5118 | 61.5523 | 61.4476 | 61.4881
3996.0938 | 123.3948 | -61.5555 | 61.496 | 0.70331 | 2.2993 | 4.3835 | 2.2184 | 0.66802 | 0.61668 | 2.5148 | 61.5554 | 0.27153 | 61.4867 | -0.033101 | 0.048236 | 61.6989 | 0.003143 | 61.4909 | 62.2588 | 63.8547 | 65.9389 | 63.7739 | 62.2235 | 62.1722 | 64.0703 | 123.1109 | 61.827 | 123.0421 | 61.5224 | 61.6037 | 123.2544 | 61.5586 | 123.0463 | 61.5072 | 61.5523 | 61.4384 | 61.4835
3997.0625 | 123.3032 | -61.6196 | 61.5601 | 0.73993 | 2.3771 | 4.4109 | 2.3421 | 0.73669 | 0.548 | 2.524 | 61.5554 | 0.27153 | 61.4958 | -0.028522 | 0.043657 | 61.7127 | 0.012299 | 61.5092 | 62.3595 | 63.9967 | 66.0305 | 63.9616 | 62.3563 | 62.1676 | 64.1435 | 123.175 | 61.8911 | 123.1154 | 61.591 | 61.6632 | 123.3322 | 61.6319 | 123.1287 | 61.5118 | 61.5431 | 61.4522 | 61.4835
3998.0938 | 123.2758 | -61.6104 | 61.5555 | 0.94138 | 1.878 | 4.6536 | 2.5481 | 0.95643 | 0.85475 | 4.6116 | 61.5371 | 0.26237 | 61.4546 | -0.023943 | 0.043657 | 61.731 | 0.012299 | 61.5229 | 62.5518 | 63.4884 | 66.264 | 64.1585 | 62.5668 | 62.4652 | 66.222 | 123.1475 | 61.8728 | 123.065 | 61.5865 | 61.6541 | 123.3414 | 61.6227 | 123.1333 | 61.4934 | 61.5248 | 61.411 | 61.4423
3999.0625 | 123.2849 | -61.6287 | 61.5189 | 0.9368 | 1.9284 | 4.5803 | 2.4886 | 0.91981 | 0.84559 | 4.7077 | 61.5463 | 0.25779 | 61.4729 | -0.033101 | 0.043657 | 61.731 | 0.003143 | 61.5275 | 62.5655 | 63.5571 | 66.2091 | 64.1173 | 62.5485 | 62.4743 | 66.3365 | 123.175 | 61.8865 | 123.1017 | 61.5956 | 61.6724 | 123.3597 | 61.6319 | 123.1562 | 61.5026 | 61.5431 | 61.4293 | 61.4698
4000.0938 | 123.4406 | -61.5692 | 61.5234 | 0.71246 | 1.7818 | 4.704 | 2.2825 | 0.755 | 0.64872 | 2.7895 | 61.5554 | 0.26695 | 61.4684 | -0.033101 | 0.043657 | 61.7081 | -0.001436 | 61.5092 | 62.2817 | 63.3511 | 66.2732 | 63.8518 | 62.3242 | 62.2179 | 64.3587 | 123.1246 | 61.8362 | 123.0376 | 61.5361 | 61.6129 | 123.2773 | 61.5678 | 123.0784 | 61.5118 | 61.5568 | 61.4247 | 61.4698
4001.0625 | 123.4497 | -61.5921 | 61.4868 | 0.71704 | 1.7086 | 4.6124 | 2.4382 | 0.74585 | 0.63957 | 2.73 | 61.5646 | 0.26695 | 61.5004 | -0.042259 | 0.029923 | 61.7035 | 0.007721 | 61.5046 | 62.3091 | 63.3007 | 66.2045 | 64.0303 | 62.3379 | 62.2317 | 64.3221 | 123.1567 | 61.8591 | 123.0925 | 61.5498 | 61.622 | 123.2956 | 61.5998 | 123.0967 | 61.5346 | 61.5569 | 61.4705 | 61.4927
4002.0781 | 123.349 | -61.5967 | 61.5509 | 0.84524 | 1.9055 | 4.617 | 2.5847 | 0.84198 | 0.77692 | 4.195 | 61.5371 | 0.26695 | 61.4592 | -0.033101 | 0.052814 | 61.7264 | 0.003143 | 61.5275 | 62.4419 | 63.5022 | 66.2136 | 64.1814 | 62.4387 | 62.3736 | 65.7917 | 123.1338 | 61.8636 | 123.0559 | 61.5636 | 61.6495 | 123.3231 | 61.5998 | 123.1242 | 61.4843 | 61.534 | 61.4064 | 61.4561
4003.0625 | 123.317 | -61.5875 | 61.5417 | 0.84524 | 1.8368 | 4.53 | 2.4794 | 0.88319 | 0.76318 | 4.5979 | 61.5508 | 0.26695 | 61.4867 | -0.033101 | 0.043657 | 61.731 | 0.003143 | 61.5275 | 62.4328 | 63.4243 | 66.1175 | 64.0669 | 62.4707 | 62.3507 | 66.1854 | 123.1384 | 61.8545 | 123.0742 | 61.5544 | 61.6312 | 123.3185 | 61.5907 | 123.115 | 61.5072 | 61.5477 | 61.443 | 61.4835
4004.0938 | 123.3673 | -61.5784 | 61.5234 | 0.8315 | 1.6674 | 4.4979 | 2.3283 | 0.76416 | 0.74487 | 4.1034 | 61.5508 | 0.26695 | 61.45 | -0.03768 | 0.039079 | 61.7218 | 0.007721 | 61.5137 | 62.4099 | 63.2457 | 66.0763 | 63.9067 | 62.3425 | 62.3232 | 65.6818 | 123.1292 | 61.8453 | 123.0284 | 61.5407 | 61.6174 | 123.3002 | 61.5861 | 123.0921 | 61.5118 | 61.5431 | 61.411 | 61.4423
4005.0625 | 123.3124 | -61.6058 | 61.5417 | 0.85897 | 1.7681 | 4.6353 | 2.4153 | 0.8191 | 0.78608 | 4.1538 | 61.5554 | 0.26695 | 61.4821 | -0.033101 | 0.048236 | 61.7218 | 0.007721 | 61.5183 | 62.4648 | 63.3739 | 66.2411 | 64.0212 | 62.4249 | 62.3919 | 65.7596 | 123.1612 | 61.8728 | 123.0879 | 61.5727 | 61.6541 | 123.3276 | 61.6136 | 123.1242 | 61.5072 | 61.5477 | 61.4339 | 61.4744
4006.0938 | 123.4268 | -61.5829 | 61.528 | 0.79945 | 1.6491 | 4.6902 | 2.4611 | 0.74127 | 0.72656 | 4.1217 | 61.5417 | 0.26237 | 61.4684 | -0.028522 | 0.043657 | 61.7218 | 0.007721 | 61.5092 | 62.3824 | 63.232 | 66.2732 | 64.0441 | 62.3242 | 62.3095 | 65.7047 | 123.1246 | 61.8453 | 123.0513 | 61.5544 | 61.6266 | 123.3048 | 61.5907 | 123.0921 | 61.498 | 61.534 | 61.4247 | 61.4606
4007.0625 | 123.3444 | -61.6058 | 61.5601 | 0.63921 | 1.4476 | 4.4979 | 2.397 | 0.60851 | 0.58463 | 2.5148 | 61.5737 | 0.25779 | 61.5004 | -0.03768 | 0.052814 | 61.6989 | 0.007721 | 61.5046 | 62.245 | 63.0534 | 66.1038 | 64.0028 | 62.2143 | 62.1905 | 64.1206 | 123.1796 | 61.8636 | 123.1062 | 61.5682 | 61.6586 | 123.3048 | 61.6136 | 123.1104 | 61.5209 | 61.566 | 61.4476 | 61.4927
4008.0625 | 123.3078 | -61.6241 | 61.5417 | 0.78114 | 1.7086 | 4.6994 | 2.4519 | 0.73211 | 0.72198 | 4.0347 | 61.5554 | 0.26695 | 61.4958 | -0.033101 | 0.052814 | 61.7218 | 0.003143 | 61.5183 | 62.4053 | 63.3327 | 66.3235 | 64.0761 | 62.3563 | 62.3461 | 65.6589 | 123.1796 | 61.8911 | 123.12 | 61.591 | 61.677 | 123.346 | 61.6273 | 123.1425 | 61.5026 | 61.5523 | 61.443 | 61.4927
4009.0938 | 123.2803 | -61.6196 | 61.6013 | 0.66668 | 1.5804 | 4.6948 | 2.3054 | 0.57646 | 0.58921 | 2.6338 | 61.5691 | 0.26695 | 61.4775 | -0.033101 | 0.048236 | 61.7035 | 0.003143 | 61.5092 | 62.2862 | 63.1999 | 66.3144 | 63.925 | 62.196 | 62.2088 | 64.2534 | 123.1887 | 61.8865 | 123.0971 | 61.5865 | 61.6678 | 123.3231 | 61.6227 | 123.1287 | 61.5209 | 61.566 | 61.4293 | 61.4744
4010.0625 | 123.3124 | -61.6241 | 61.5509 | 0.83608 | 1.7498 | 4.7955 | 2.3146 | 0.66802 | 0.76776 | 4.1492 | 61.5463 | 0.26695 | 61.4821 | -0.033101 | 0.039079 | 61.7218 | 0.007721 | 61.5046 | 62.4602 | 63.3739 | 66.4197 | 63.9387 | 62.2922 | 62.3919 | 65.7733 | 123.1704 | 61.8911 | 123.1062 | 61.591 | 61.6632 | 123.346 | 61.6319 | 123.1287 | 61.5072 | 61.5385 | 61.443 | 61.4744
4011.0938 | 123.4451 | -61.5692 | 61.528 | 0.8315 | 1.7544 | 4.8322 | 2.1406 | 0.62224 | 0.75861 | 4.1996 | 61.5508 | 0.26237 | 61.4684 | -0.028522 | 0.039079 | 61.7218 | 0.003143 | 61.5046 | 62.4007 | 63.3236 | 66.4014 | 63.7098 | 62.1915 | 62.3278 | 65.7688 | 123.12 | 61.8316 | 123.0376 | 61.5407 | 61.6083 | 123.291 | 61.5724 | 123.0738 | 61.5118 | 61.5477 | 61.4293 | 61.4652
4012.0625 | 123.349 | -61.5738 | 61.5784 | 0.86813 | 1.7406 | 4.9741 | 2.0124 | 0.65429 | 0.79981 | 4.0897 | 61.5508 | 0.26695 | 61.4821 | -0.033101 | 0.048236 | 61.7218 | 0.012299 | 61.5 | 62.4419 | 63.3144 | 66.5479 | 63.5862 | 62.2281 | 62.3736 | 65.6635 | 123.1246 | 61.8407 | 123.0559 | 61.5407 | 61.622 | 123.2956 | 61.5861 | 123.0738 | 61.5026 | 61.5385 | 61.4339 | 61.4698
4013.0938 | 123.3307 | -61.6104 | 61.5555 | 0.78114 | 1.5804 | 4.7955 | 2.0948 | 0.58562 | 0.70824 | 3.9752 | 61.5554 | 0.26695 | 61.4775 | -0.028522 | 0.048236 | 61.7081 | 0.007721 | 61.5092 | 62.3916 | 63.1908 | 66.4059 | 63.7052 | 62.196 | 62.3187 | 65.5856 | 123.1658 | 61.8774 | 123.0879 | 61.5819 | 61.6586 | 123.3185 | 61.6181 | 123.1196 | 61.5072 | 61.5477 | 61.4293 | 61.4698
4014.0625 | 123.3353 | -61.5921 | 61.5738 | 0.75367 | 1.4384 | 4.7177 | 2.1406 | 0.61309 | 0.66246 | 3.5449 | 61.56 | 0.26237 | 61.4821 | -0.028522 | 0.043657 | 61.7127 | 0.003143 | 61.5 | 62.3458 | 63.0305 | 66.3098 | 63.7327 | 62.2052 | 62.2546 | 65.137 | 123.1521 | 61.8545 | 123.0742 | 61.5636 | 61.6358 | 123.3048 | 61.5952 | 123.0921 | 61.5163 | 61.5568 | 61.4384 | 61.4789
4015.0938 | 123.3078 | -61.5967 | 61.5921 | 0.68957 | 1.5209 | 4.7681 | 2.2963 | 0.58562 | 0.61668 | 2.817 | 61.5646 | 0.27153 | 61.4958 | -0.028522 | 0.048236 | 61.7035 | -0.001436 | 61.4817 | 62.2863 | 63.1175 | 66.3647 | 63.893 | 62.1823 | 62.2134 | 64.4136 | 123.1613 | 61.8682 | 123.0925 | 61.5682 | 61.6449 | 123.3002 | 61.5952 | 123.0784 | 61.5163 | 61.566 | 61.4476 | 61.4973
4016.0781 | 123.4131 | -61.5646 | 61.5372 | 0.61174 | 1.5437 | 4.6811 | 2.2688 | 0.50322 | 0.54342 | 2.5148 | 61.5646 | 0.26695 | 61.4958 | -0.033101 | 0.048236 | 61.7035 | 0.007721 | 61.4817 | 62.1764 | 63.1084 | 66.2457 | 63.8334 | 62.0679 | 62.1081 | 64.0794 | 123.1292 | 61.8316 | 123.0605 | 61.5315 | 61.6129 | 123.2681 | 61.5724 | 123.0463 | 61.5163 | 61.5569 | 61.4476 | 61.4881
4017.0938 | 123.3353 | -61.5829 | 61.5921 | 0.56595 | 1.5346 | 4.6536 | 2.1727 | 0.42539 | 0.48848 | 2.3774 | 61.5691 | 0.27153 | 61.5096 | -0.033101 | 0.048236 | 61.6943 | -0.001436 | 61.4817 | 62.1489 | 63.1175 | 66.2365 | 63.7556 | 62.0083 | 62.0714 | 63.9604 | 123.1521 | 61.8545 | 123.0925 | 61.5498 | 61.6312 | 123.2773 | 61.5815 | 123.0646 | 61.5209 | 61.5706 | 61.4613 | 61.511
4018.0625 | 123.3032 | -61.6196 | 61.5829 | 0.68499 | 1.6307 | 4.8001 | 2.2459 | 0.45744 | 0.61668 | 3.8287 | 61.56 | 0.26237 | 61.4912 | -0.03768 | 0.043657 | 61.7218 | 0.012299 | 61.5046 | 62.3046 | 63.2503 | 66.4197 | 63.8655 | 62.077 | 62.2362 | 65.4483 | 123.1796 | 61.8819 | 123.1108 | 61.5819 | 61.6632 | 123.3414 | 61.6319 | 123.1242 | 61.5163 | 61.5477 | 61.4476 | 61.4789
4019.0781 | 123.4039 | -61.5875 | 61.5326 | 0.78114 | 1.6994 | 4.9833 | 2.1269 | 0.53068 | 0.70824 | 4.4834 | 61.5508 | 0.26237 | 61.4821 | -0.033101 | 0.048236 | 61.7172 | 0.007721 | 61.5046 | 62.3687 | 63.287 | 66.5708 | 63.7144 | 62.1182 | 62.2958 | 66.0709 | 123.1384 | 61.8499 | 123.0696 | 61.5544 | 61.6358 | 123.3048 | 61.5952 | 123.0921 | 61.5026 | 61.5431 | 61.4339 | 61.4744
4020.0625 | 123.2849 | -61.6608 | 61.5417 | 0.78572 | 1.7223 | 5.0245 | 1.9804 | 0.57189 | 0.70824 | 4.4422 | 61.5508 | 0.27153 | 61.4684 | -0.03768 | 0.048236 | 61.7218 | 0.003143 | 61.5092 | 62.4465 | 63.3831 | 66.6852 | 63.6411 | 62.2327 | 62.369 | 66.103 | 123.2116 | 61.9323 | 123.1291 | 61.6231 | 61.709 | 123.3826 | 61.6639 | 123.1699 | 61.5026 | 61.5477 | 61.4201 | 61.4652
4021.1094 | 123.2986 | -61.6058 | 61.5738 | 0.72162 | 1.6033 | 4.9649 | 2.0536 | 0.47117 | 0.6533 | 4.195 | 61.5554 | 0.25779 | 61.4912 | -0.033101 | 0.043657 | 61.7127 | 0.003143 | 61.5 | 62.3275 | 63.2091 | 66.5708 | 63.6595 | 62.077 | 62.2591 | 65.8008 | 123.1612 | 61.8636 | 123.0971 | 61.5727 | 61.6495 | 123.3185 | 61.609 | 123.1058 | 61.5118 | 61.5523 | 61.4476 | 61.4881
4022.0625 | 123.3582 | -61.5692 | 61.5784 | 0.58427 | 1.356 | 4.8734 | 1.9849 | 0.4025 | 0.51595 | 2.4965 | 61.5691 | 0.25779 | 61.4912 | -0.03768 | 0.043657 | 61.6943 | 0.007721 | 61.4817 | 62.1535 | 62.9252 | 66.4426 | 63.5542 | 61.9717 | 62.0852 | 64.0657 | 123.1384 | 61.827 | 123.0605 | 61.5315 | 61.6129 | 123.2636 | 61.5769 | 123.0509 | 61.5255 | 61.5614 | 61.4476 | 61.4835
4023.0625 | 123.2712 | -61.5967 | 61.5875 | 0.67126 | 1.3469 | 5.029 | 2.1727 | 0.47575 | 0.57547 | 2.7437 | 61.5691 | 0.26695 | 61.505 | -0.033101 | 0.048236 | 61.7081 | 0.007721 | 61.4909 | 62.2679 | 62.9435 | 66.6257 | 63.7693 | 62.0724 | 62.1722 | 64.3404 | 123.1658 | 61.8636 | 123.1017 | 61.5636 | 61.6449 | 123.3048 | 61.6044 | 123.0875 | 61.5209 | 61.5614 | 61.4567 | 61.4973
4024.0781 | 123.3765 | -61.5738 | 61.5509 | 0.63005 | 1.2507 | 4.9008 | 2.2184 | 0.47575 | 0.55716 | 2.6018 | 61.5691 | 0.25779 | 61.4912 | -0.033101 | 0.039079 | 61.6989 | 0.007721 | 61.4863 | 62.2038 | 62.8245 | 66.4746 | 63.7922 | 62.0495 | 62.1309 | 64.1756 | 123.1429 | 61.8316 | 123.065 | 61.5407 | 61.6129 | 123.2727 | 61.5815 | 123.0601 | 61.5301 | 61.5614 | 61.4522 | 61.4835
4025.0625 | 123.2758 | -61.5967 | 61.5921 | 0.74909 | 1.3423 | 4.8917 | 2.3466 | 0.549 | 0.66246 | 3.989 | 61.56 | 0.27153 | 61.4821 | -0.028522 | 0.048236 | 61.7127 | 0.003143 | 61.5092 | 62.3458 | 62.939 | 66.4884 | 63.9433 | 62.1457 | 62.2591 | 65.5856 | 123.1567 | 61.8682 | 123.0788 | 61.5682 | 61.6449 | 123.3093 | 61.5998 | 123.1058 | 61.5118 | 61.5568 | 61.4339 | 61.4789
4026.1094 | 123.2803 | -61.6379 | 61.5601 | 0.75367 | 1.3835 | 4.9192 | 2.3375 | 0.53984 | 0.67162 | 4.1172 | 61.56 | 0.26695 | 61.4958 | -0.033101 | 0.048236 | 61.7218 | 0.007721 | 61.5046 | 62.3915 | 63.0214 | 66.557 | 63.9754 | 62.1777 | 62.3095 | 65.755 | 123.1979 | 61.9048 | 123.1337 | 61.6048 | 61.6861 | 123.3597 | 61.6456 | 123.1425 | 61.5118 | 61.5523 | 61.4476 | 61.4881
4027.0625 | 123.3032 | -61.6013 | 61.5829 | 0.78572 | 1.443 | 4.9833 | 2.4016 | 0.59935 | 0.70824 | 4.0393 | 61.5463 | 0.26695 | 61.45 | -0.03768 | 0.048236 | 61.7172 | -0.001436 | 61.5137 | 62.387 | 63.0443 | 66.5845 | 64.0028 | 62.2006 | 62.3095 | 65.6406 | 123.1475 | 61.8682 | 123.0513 | 61.5636 | 61.6495 | 123.3185 | 61.5998 | 123.115 | 61.498 | 61.5477 | 61.4018 | 61.4515
4028.0938 | 123.4268 | -61.5738 | 61.5555 | 0.83608 | 1.5712 | 4.9558 | 2.3833 | 0.61309 | 0.75403 | 4.6162 | 61.5463 | 0.26237 | 61.4821 | -0.033101 | 0.048236 | 61.7218 | 0.012299 | 61.5229 | 62.4099 | 63.145 | 66.5296 | 63.9571 | 62.1869 | 62.3278 | 66.19 | 123.12 | 61.8362 | 123.0559 | 61.5407 | 61.622 | 123.2956 | 61.5861 | 123.0967 | 61.498 | 61.534 | 61.4339 | 61.4698
4029.0625 | 123.3627 | -61.5875 | 61.5143 | 0.84981 | 1.6353 | 4.9146 | 2.3558 | 0.65429 | 0.76776 | 4.8039 | 61.5417 | 0.27153 | 61.4592 | -0.028522 | 0.043657 | 61.7264 | 0.007721 | 61.5321 | 62.4373 | 63.2229 | 66.5021 | 63.9433 | 62.2418 | 62.3553 | 66.3914 | 123.1292 | 61.8591 | 123.0467 | 61.559 | 61.6312 | 123.3139 | 61.5952 | 123.1196 | 61.498 | 61.534 | 61.4155 | 61.4515
4030.0781 | 123.349 | -61.5921 | 61.5005 | 0.84524 | 1.617 | 4.9329 | 2.4153 | 0.63598 | 0.77692 | 4.7306 | 61.5417 | 0.26237 | 61.4729 | -0.03768 | 0.043657 | 61.731 | 0.007721 | 61.5275 | 62.4373 | 63.2091 | 66.525 | 64.0074 | 62.2281 | 62.369 | 66.3227 | 123.1338 | 61.8545 | 123.065 | 61.5544 | 61.6358 | 123.3231 | 61.5998 | 123.1196 | 61.498 | 61.534 | 61.4293 | 61.4652
4031.0625 | 123.2803 | -61.6241 | 61.5555 | 0.91391 | 1.585 | 5.0428 | 2.4474 | 0.65429 | 0.8227 | 4.9779 | 61.5463 | 0.26695 | 61.4821 | -0.03768 | 0.048236 | 61.7264 | 0.007721 | 61.5275 | 62.5381 | 63.2091 | 66.6669 | 64.0715 | 62.2784 | 62.4468 | 66.602 | 123.1704 | 61.8911 | 123.1062 | 61.5865 | 61.6724 | 123.3505 | 61.6319 | 123.1516 | 61.498 | 61.5385 | 61.4339 | 61.4744
4032.0781 | 123.3673 | -61.6104 | 61.528 | 0.79487 | 1.5163 | 5.0107 | 2.4245 | 0.54442 | 0.74029 | 4.5704 | 61.5371 | 0.27153 | 61.4592 | -0.033101 | 0.043657 | 61.7264 | 0.007721 | 61.5183 | 62.4053 | 63.1267 | 66.6211 | 64.0349 | 62.1548 | 62.3507 | 66.1808 | 123.1475 | 61.8819 | 123.0696 | 61.5773 | 61.6541 | 123.3368 | 61.6181 | 123.1287 | 61.4934 | 61.5294 | 61.4155 | 61.4515
4033.0625 | 123.2941 | -61.6241 | 61.5738 | 0.7674 | 1.3514 | 5.084 | 2.4611 | 0.56273 | 0.69451 | 4.5246 | 61.5463 | 0.26695 | 61.4867 | -0.033101 | 0.057392 | 61.7264 | 0.016878 | 61.5183 | 62.3916 | 62.9756 | 66.7081 | 64.0853 | 62.1869 | 62.3187 | 66.1488 | 123.1704 | 61.8911 | 123.1108 | 61.591 | 61.6815 | 123.3505 | 61.641 | 123.1425 | 61.4889 | 61.5294 | 61.4293 | 61.4698
4034.0781 | 123.3627 | -61.5921 | 61.5005 | 0.7903 | 1.324 | 5.1939 | 2.4016 | 0.61767 | 0.72198 | 4.4102 | 61.5417 | 0.27153 | 61.4684 | -0.033101 | 0.043657 | 61.731 | -0.001436 | 61.5183 | 62.3824 | 62.9161 | 66.786 | 63.9937 | 62.2098 | 62.3141 | 66.0023 | 123.1338 | 61.8636 | 123.0605 | 61.559 | 61.6358 | 123.3231 | 61.5907 | 123.1104 | 61.498 | 61.5431 | 61.4247 | 61.4698
4035.0625 | 123.2849 | -61.5784 | 61.5875 | 0.598 | 1.1958 | 5.0977 | 2.2001 | 0.55357 | 0.53884 | 2.4736 | 61.5737 | 0.27153 | 61.5096 | -0.028522 | 0.043657 | 61.6989 | 0.012299 | 61.5046 | 62.1764 | 62.7741 | 66.6761 | 63.7785 | 62.1319 | 62.1172 | 64.052 | 123.1521 | 61.8499 | 123.0879 | 61.5498 | 61.622 | 123.2773 | 61.5907 | 123.083 | 61.5301 | 61.5614 | 61.4659 | 61.4973
4036.125 | 123.3124 | -61.5784 | 61.5692 | 0.56138 | 1.1866 | 5.0107 | 2.191 | 0.50779 | 0.52053 | 2.3637 | 61.5737 | 0.27611 | 61.4958 | -0.03768 | 0.048236 | 61.6989 | 0.003143 | 61.4817 | 62.1397 | 62.765 | 66.5891 | 63.7693 | 62.0862 | 62.0989 | 63.9421 | 123.1521 | 61.8545 | 123.0742 | 61.5407 | 61.6266 | 123.2773 | 61.5815 | 123.0601 | 61.5255 | 61.5706 | 61.4476 | 61.4927
4037.0625 | 123.3078 | -61.5829 | 61.5921 | 0.60258 | 1.1774 | 4.9466 | 2.1452 | 0.549 | 0.51137 | 2.4141 | 61.5691 | 0.26695 | 61.5096 | -0.028522 | 0.043657 | 61.6943 | 0.007721 | 61.4954 | 62.1855 | 62.7604 | 66.5296 | 63.7281 | 62.1319 | 62.0943 | 63.997 | 123.1521 | 61.8499 | 123.0925 | 61.5544 | 61.6266 | 123.2773 | 61.5907 | 123.0784 | 61.5255 | 61.5614 | 61.4659 | 61.5018
4038.0781 | 123.3948 | -61.5875 | 61.5234 | 0.84524 | 1.3057 | 4.9466 | 2.3146 | 0.66802 | 0.79065 | 4.3049 | 61.5508 | 0.27153 | 61.4729 | -0.03768 | 0.039079 | 61.7172 | 0.007721 | 61.5092 | 62.4328 | 62.8932 | 66.5342 | 63.9021 | 62.2555 | 62.3782 | 65.8924 | 123.1384 | 61.8591 | 123.0605 | 61.5498 | 61.6266 | 123.3048 | 61.5952 | 123.0967 | 61.5118 | 61.5431 | 61.4339 | 61.4652
4039.0625 | 123.2986 | -61.6058 | 61.5784 | 0.81319 | 1.2965 | 4.8551 | 2.3558 | 0.62682 | 0.74487 | 4.0988 | 61.5508 | 0.26695 | 61.4775 | -0.028522 | 0.039079 | 61.7218 | 0.003143 | 61.4954 | 62.419 | 62.9023 | 66.4609 | 63.9616 | 62.2327 | 62.3507 | 65.7047 | 123.1567 | 61.8728 | 123.0833 | 61.5773 | 61.6449 | 123.3276 | 61.609 | 123.1013 | 61.5118 | 61.5477 | 61.4384 | 61.4744
4040.0781 | 123.4314 | -61.5738 | 61.5143 | 0.63921 | 1.1866 | 4.9008 | 2.2368 | 0.54442 | 0.58463 | 2.2859 | 61.5646 | 0.26237 | 61.5096 | -0.03768 | 0.039079 | 61.6989 | 0.007721 | 61.4771 | 62.213 | 62.7604 | 66.4746 | 63.8106 | 62.1182 | 62.1584 | 63.8597 | 123.1384 | 61.8362 | 123.0833 | 61.5361 | 61.6129 | 123.2727 | 61.5815 | 123.0509 | 61.5255 | 61.5569 | 61.4705 | 61.5018
4041.0625 | 123.349 | -61.5555 | 61.5463 | 0.61632 | 1.2507 | 5.1023 | 2.0765 | 0.53984 | 0.52053 | 2.3912 | 61.5737 | 0.26695 | 61.4912 | -0.028522 | 0.048236 | 61.6989 | 0.007721 | 61.4771 | 62.1718 | 62.8062 | 66.6578 | 63.632 | 62.0953 | 62.076 | 63.9467 | 123.1292 | 61.8224 | 123.0467 | 61.527 | 61.6037 | 123.2544 | 61.5632 | 123.0326 | 61.5255 | 61.566 | 61.443 | 61.4835
4042.0625 | 123.3215 | -61.5967 | 61.5555 | 0.75825 | 1.4293 | 5.0382 | 2.1269 | 0.67718 | 0.67619 | 4.1172 | 61.5508 | 0.26237 | 61.4912 | -0.033101 | 0.048236 | 61.7127 | 0.012299 | 61.4954 | 62.3549 | 63.026 | 66.6349 | 63.7236 | 62.2739 | 62.2729 | 65.7138 | 123.1475 | 61.859 | 123.0879 | 61.5636 | 61.6449 | 123.3093 | 61.609 | 123.0921 | 61.5026 | 61.5385 | 61.443 | 61.4789
4043.0781 | 123.4131 | -61.5417 | 61.5417 | 0.63005 | 1.2919 | 5.3175 | 1.843 | 0.53526 | 0.548 | 2.4049 | 61.56 | 0.27153 | 61.4775 | -0.033101 | 0.048236 | 61.7035 | 0.007721 | 61.4725 | 62.1718 | 62.8337 | 66.8592 | 63.3848 | 62.077 | 62.0897 | 63.9467 | 123.1017 | 61.8133 | 123.0193 | 61.5086 | 61.59 | 123.2452 | 61.5495 | 123.0143 | 61.5118 | 61.5523 | 61.4293 | 61.4698
4044.0625 | 123.2529 | -61.5967 | 61.5692 | 0.62089 | 1.2141 | 5.1344 | 1.9987 | 0.51695 | 0.53884 | 2.8536 | 61.5691 | 0.26237 | 61.505 | -0.03768 | 0.043657 | 61.7035 | 0.003143 | 61.4817 | 62.2176 | 62.8108 | 66.731 | 63.5954 | 62.1136 | 62.1355 | 64.4503 | 123.1658 | 61.859 | 123.1017 | 61.559 | 61.6403 | 123.3002 | 61.5998 | 123.0784 | 61.5255 | 61.566 | 61.4613 | 61.5018
4045.0781 | 123.3719 | -61.5921 | 61.5097 | 0.66668 | 1.269 | 5.2442 | 1.9987 | 0.60851 | 0.59836 | 3.1145 | 61.5508 | 0.27153 | 61.4821 | -0.033101 | 0.043657 | 61.7081 | -0.001436 | 61.4863 | 62.2588 | 62.8611 | 66.8363 | 63.5908 | 62.2006 | 62.1905 | 64.7066 | 123.1429 | 61.8636 | 123.0742 | 61.559 | 61.6358 | 123.3002 | 61.5907 | 123.0784 | 61.5072 | 61.5523 | 61.4384 | 61.4835
4046.0625 | 123.3765 | -61.647 | 61.4685 | 0.85897 | 1.4842 | 5.4045 | 2.0948 | 0.6726 | 0.76318 | 4.2591 | 61.5417 | 0.26695 | 61.4729 | -0.033101 | 0.048236 | 61.7172 | 0.007721 | 61.5 | 62.506 | 63.1313 | 67.0515 | 63.7419 | 62.3196 | 62.4102 | 65.9061 | 123.1887 | 61.914 | 123.12 | 61.6139 | 61.6953 | 123.3643 | 61.6548 | 123.147 | 61.4934 | 61.534 | 61.4247 | 61.4652
4047.0938 | 123.3261 | -61.6104 | 61.5372 | 0.88644 | 1.6033 | 5.5327 | 2.1543 | 0.7138 | 0.81812 | 4.9046 | 61.5463 | 0.26237 | 61.4729 | -0.028522 | 0.039079 | 61.7401 | -0.001436 | 61.5092 | 62.4969 | 63.2137 | 67.1431 | 63.7648 | 62.3242 | 62.4285 | 66.515 | 123.1567 | 61.8728 | 123.0833 | 61.5819 | 61.6495 | 123.3505 | 61.609 | 123.1196 | 61.5072 | 61.5477 | 61.4339 | 61.4744
4048.0625 | 123.349 | -61.615 | 61.5555 | 0.90018 | 1.6262 | 5.258 | 2.1452 | 0.7138 | 0.83644 | 4.7764 | 61.5371 | 0.26695 | 61.4546 | -0.042259 | 0.039079 | 61.731 | 0.007721 | 61.5092 | 62.5152 | 63.2412 | 66.873 | 63.7602 | 62.3288 | 62.4514 | 66.3914 | 123.1521 | 61.8819 | 123.0696 | 61.5727 | 61.6541 | 123.346 | 61.6227 | 123.1242 | 61.498 | 61.5294 | 61.4155 | 61.4469
4049.0781 | 123.3627 | -61.5738 | 61.5326 | 0.80861 | 1.5163 | 5.2076 | 2.1177 | 0.60393 | 0.74945 | 4.8817 | 61.5463 | 0.26695 | 61.4684 | -0.033101 | 0.048236 | 61.7264 | 0.007721 | 61.5046 | 62.3824 | 63.0901 | 66.7814 | 63.6915 | 62.1777 | 62.3232 | 66.4555 | 123.12 | 61.8407 | 123.0421 | 61.5407 | 61.622 | 123.3002 | 61.5815 | 123.0784 | 61.498 | 61.5385 | 61.4201 | 61.4606
4050.0625 | 123.317 | -61.615 | 61.5509 | 0.8315 | 1.4568 | 5.0657 | 2.3009 | 0.6314 | 0.75861 | 4.9138 | 61.5417 | 0.26695 | 61.4638 | -0.033101 | 0.043657 | 61.7264 | 0.012299 | 61.5092 | 62.4465 | 63.0717 | 66.6807 | 63.9158 | 62.2464 | 62.3736 | 66.5287 | 123.1567 | 61.8819 | 123.0788 | 61.5819 | 61.6586 | 123.3414 | 61.6273 | 123.1242 | 61.498 | 61.5294 | 61.4201 | 61.4515
4051.1094 | 123.3627 | -61.5784 | 61.528 | 0.90475 | 1.2965 | 5.0702 | 2.2597 | 0.62682 | 0.73571 | 4.8268 | 61.5508 | 0.27153 | 61.4821 | -0.03768 | 0.043657 | 61.731 | 0.007721 | 61.5046 | 62.4831 | 62.8749 | 66.6486 | 63.838 | 62.2052 | 62.3141 | 66.4051 | 123.1292 | 61.8499 | 123.0605 | 61.5407 | 61.622 | 123.3093 | 61.5861 | 123.083 | 61.5072 | 61.5431 | 61.4384 | 61.4744
4052.0625 | 123.3582 | -61.5921 | 61.5372 | 1.3718 | 1.3377 | 5.1023 | 2.223 | 0.60851 | 0.18173 | 4.4102 | 61.5508 | 0.26695 | 61.4821 | -0.03768 | 0.043657 | 61.7172 | 0.003143 | 61.5 | 62.9639 | 62.9298 | 66.6944 | 63.8151 | 62.2006 | 61.7738 | 66.0023 | 123.1429 | 61.8591 | 123.0742 | 61.5544 | 61.6358 | 123.3093 | 61.5952 | 123.0921 | 61.5072 | 61.5477 | 61.4384 | 61.4789
4053.0781 | 123.4039 | -61.615 | 61.5417 | 0.83608 | 1.1454 | 4.9466 | 2.1818 | 0.58562 | 0.67162 | 4.2728 | 61.5554 | 0.26695 | 61.4684 | -0.033101 | 0.043657 | 61.7172 | 0.012299 | 61.5 | 62.4511 | 62.7604 | 66.5616 | 63.7968 | 62.2006 | 62.2866 | 65.8878 | 123.1704 | 61.8819 | 123.0833 | 61.5819 | 61.6586 | 123.3322 | 61.6273 | 123.115 | 61.5118 | 61.5431 | 61.4247 | 61.4561
4054.0625 | 123.317 | -61.6241 | 61.5555 | 0.92307 | 1.4018 | 5.203 | 2.1452 | 0.6726 | 0.84102 | 4.488 | 61.5554 | 0.26695 | 61.4821 | -0.03768 | 0.048236 | 61.7218 | 0.003143 | 61.5046 | 62.5472 | 63.026 | 66.8272 | 63.7693 | 62.2967 | 62.4652 | 66.1121 | 123.1796 | 61.8911 | 123.1062 | 61.5865 | 61.6724 | 123.346 | 61.6273 | 123.1287 | 61.5072 | 61.5523 | 61.4339 | 61.4789
4055.0938 | 123.3398 | -61.5967 | 61.5646 | 1.1657 | 1.53 | 5.0061 | 2.1727 | 0.61767 | 0.49306 | 4.6894 | 61.5417 | 0.26695 | 61.4546 | -0.033101 | 0.039079 | 61.7172 | 0.007721 | 61.5092 | 62.7624 | 63.1267 | 66.6028 | 63.7693 | 62.2143 | 62.0897 | 66.2861 | 123.1384 | 61.8636 | 123.0513 | 61.5636 | 61.6358 | 123.3139 | 61.6044 | 123.1058 | 61.5026 | 61.534 | 61.4155 | 61.4469
4056.0625 | 123.3902 | -61.6241 | 61.5143 | 0.91391 | 1.5346 | 4.9283 | 2.1177 | 0.53526 | 0.76318 | 4.7764 | 61.5417 | 0.27153 | 61.4775 | -0.03768 | 0.039079 | 61.731 | 0.003143 | 61.5092 | 62.5381 | 63.1587 | 66.5525 | 63.7419 | 62.1594 | 62.3873 | 66.4006 | 123.1658 | 61.8957 | 123.1017 | 61.5865 | 61.6632 | 123.3551 | 61.6273 | 123.1333 | 61.5026 | 61.5385 | 61.4384 | 61.4744
4057.0781 | 123.3032 | -61.6379 | 61.5417 | 0.87271 | 1.5254 | 4.8459 | 2.1635 | 0.52153 | 0.76318 | 4.9641 | 61.5463 | 0.27153 | 61.4638 | -0.033101 | 0.039079 | 61.731 | 0.007721 | 61.5092 | 62.5106 | 63.1633 | 66.4838 | 63.8014 | 62.1594 | 62.4011 | 66.602 | 123.1841 | 61.9094 | 123.1017 | 61.6048 | 61.677 | 123.3688 | 61.6456 | 123.147 | 61.5072 | 61.5385 | 61.4247 | 61.4561
4058.0625 | 123.3032 | -61.6241 | 61.528 | 0.91391 | 1.4293 | 4.8779 | 2.1635 | 0.47575 | 0.80439 | 4.9504 | 61.5554 | 0.26237 | 61.4867 | -0.028522 | 0.043657 | 61.731 | 0.003143 | 61.5 | 62.5381 | 63.0534 | 66.5021 | 63.7877 | 62.0999 | 62.4285 | 66.5745 | 123.1796 | 61.8865 | 123.1108 | 61.5956 | 61.6678 | 123.3551 | 61.6273 | 123.1242 | 61.5118 | 61.5523 | 61.443 | 61.4835
4059.0781 | 123.2849 | -61.6058 | 61.528 | 0.90018 | 1.3835 | 4.7772 | 2.223 | 0.48948 | 0.81355 | 4.8726 | 61.5463 | 0.26695 | 61.4546 | -0.033101 | 0.043657 | 61.7264 | 0.007721 | 61.5046 | 62.506 | 62.9893 | 66.3831 | 63.8289 | 62.0953 | 62.4194 | 66.4784 | 123.1521 | 61.8728 | 123.0605 | 61.5727 | 61.6495 | 123.3322 | 61.6136 | 123.1104 | 61.5026 | 61.5385 | 61.411 | 61.4469
4060.0625 | 123.3627 | -61.6104 | 61.5784 | 0.82234 | 1.3926 | 4.9466 | 2.136 | 0.43912 | 0.73114 | 4.2637 | 61.5554 | 0.27153 | 61.4958 | -0.028522 | 0.034501 | 61.7172 | 0.003143 | 61.4863 | 62.4328 | 63.0031 | 66.557 | 63.7464 | 62.0495 | 62.3415 | 65.8741 | 123.1658 | 61.8819 | 123.1062 | 61.5819 | 61.6449 | 123.3276 | 61.6136 | 123.0967 | 61.5209 | 61.5523 | 61.4613 | 61.4927
4061.1094 | 123.2391 | -61.5738 | 61.5875 | 0.6621 | 1.2553 | 5.029 | 2.0261 | 0.37503 | 0.58463 | 2.6109 | 61.5646 | 0.27153 | 61.4775 | -0.03768 | 0.043657 | 61.6989 | 0.003143 | 61.4725 | 62.2359 | 62.8291 | 66.6028 | 63.5999 | 61.9488 | 62.1584 | 64.1847 | 123.1384 | 61.8453 | 123.0513 | 61.5361 | 61.6174 | 123.2727 | 61.5769 | 123.0463 | 61.5209 | 61.5614 | 61.4339 | 61.4744
4062.0625 | 123.2574 | -61.6104 | 61.5234 | 0.90018 | 1.4339 | 5.3679 | 2.2093 | 0.46659 | 0.77692 | 4.5063 | 61.5508 | 0.26237 | 61.4912 | -0.033101 | 0.039079 | 61.7218 | -0.001436 | 61.5046 | 62.5106 | 63.0443 | 66.9783 | 63.8197 | 62.077 | 62.3873 | 66.1167 | 123.1612 | 61.8728 | 123.1017 | 61.5773 | 61.6495 | 123.3322 | 61.609 | 123.115 | 61.5118 | 61.5523 | 61.4522 | 61.4927
4063.0938 | 123.3353 | -61.615 | 61.5555 | 0.73078 | 1.2232 | 5.084 | 2.2276 | 0.37503 | 0.63499 | 3.3938 | 61.5646 | 0.26695 | 61.4867 | -0.028522 | 0.043657 | 61.7035 | 0.003143 | 61.4863 | 62.3458 | 62.8382 | 66.699 | 63.8426 | 61.99 | 62.25 | 65.0088 | 123.1796 | 61.8819 | 123.1017 | 61.5865 | 61.6586 | 123.3185 | 61.6181 | 123.1013 | 61.5209 | 61.5614 | 61.443 | 61.4835
4064.0625 | 123.2986 | -61.5967 | 61.6013 | 0.45607 | 0.87982 | 3.4906 | 2.0078 | 0.1324 | 0.3786 | 2.2355 | 61.5966 | 0.26695 | 61.5233 | -0.033101 | 0.043657 | 61.676 | 0.003143 | 61.4542 | 62.0528 | 62.4765 | 65.0873 | 63.6045 | 61.7291 | 61.9753 | 63.8322 | 123.1933 | 61.8636 | 123.12 | 61.5636 | 61.6403 | 123.2727 | 61.5998 | 123.0509 | 61.553 | 61.5935 | 61.4796 | 61.5202
4065.0938 | 123.317 | -61.5555 | 61.5921 | 0.40113 | 0.96682 | 2.1033 | 1.811 | 0.077466 | 0.33282 | 2.144 | 61.6104 | 0.26695 | 61.5416 | -0.03768 | 0.043657 | 61.6623 | 0.007721 | 61.4542 | 61.9566 | 62.5223 | 63.6588 | 63.3664 | 61.6329 | 61.8883 | 63.6994 | 123.1658 | 61.8224 | 123.0971 | 61.5178 | 61.5991 | 123.2178 | 61.5632 | 123.0097 | 61.5667 | 61.6026 | 61.4979 | 61.5339
4066.0625 | 123.4268 | -61.5005 | 61.5829 | 0.32788 | 0.74704 | 1.8561 | 1.5912 | -0.014093 | 0.20004 | 2.0204 | 61.6149 | 0.26237 | 61.5508 | -0.033101 | 0.048236 | 61.6577 | -0.001436 | 61.4359 | 61.8284 | 62.2476 | 63.3566 | 63.0917 | 61.4865 | 61.7006 | 63.5209 | 123.1155 | 61.7629 | 123.0513 | 61.4674 | 61.5488 | 123.1583 | 61.4991 | 122.9365 | 61.5667 | 61.6164 | 61.5025 | 61.5522
4067.0938 | 123.349 | -61.5417 | 61.5875 | 0.32788 | 0.70125 | 2.0163 | 1.6461 | -0.032405 | 0.2092 | 2.0341 | 61.6149 | 0.26237 | 61.5508 | -0.033101 | 0.043657 | 61.6531 | 0.007721 | 61.4268 | 61.8696 | 62.243 | 63.5581 | 63.1879 | 61.5093 | 61.7509 | 63.5758 | 123.1567 | 61.8041 | 123.0925 | 61.5086 | 61.5854 | 123.1949 | 61.5495 | 122.9685 | 61.5713 | 61.6072 | 61.5071 | 61.543
4068.0625 | 123.2895 | -61.5784 | 61.6104 | 0.30499 | 0.73788 | 2.2269 | 1.5591 | -0.050716 | 0.24125 | 2.0616 | 61.6104 | 0.26695 | 61.5508 | -0.033101 | 0.048236 | 61.6486 | 0.003143 | 61.4451 | 61.8834 | 62.3162 | 63.8053 | 63.1375 | 61.5277 | 61.8196 | 63.6399 | 123.1887 | 61.8453 | 123.1291 | 61.5453 | 61.6266 | 123.2269 | 61.5815 | 123.0234 | 61.5621 | 61.6072 | 61.5025 | 61.5476
4069.0938 | 123.3261 | -61.5875 | 61.615 | 0.38282 | 0.93477 | 2.2956 | 1.5729 | -0.009515 | 0.3145 | 3.4167 | 61.6012 | 0.26695 | 61.5233 | -0.033101 | 0.048236 | 61.6715 | 0.003143 | 61.4542 | 61.9703 | 62.5223 | 63.8831 | 63.1604 | 61.578 | 61.902 | 65.0042 | 123.1887 | 61.8545 | 123.1108 | 61.5544 | 61.6358 | 123.259 | 61.5907 | 123.0418 | 61.553 | 61.5981 | 61.4751 | 61.5202
4070.0625 | 123.2941 | -61.5738 | 61.6104 | 0.39655 | 0.89356 | 2.2681 | 1.5775 | 0.017953 | 0.34197 | 3.5128 | 61.6104 | 0.27153 | 61.537 | -0.03768 | 0.043657 | 61.6715 | 0.007721 | 61.4542 | 61.9703 | 62.4673 | 63.8419 | 63.1512 | 61.5917 | 61.9158 | 65.0866 | 123.1841 | 61.8453 | 123.1108 | 61.5361 | 61.6174 | 123.2452 | 61.5815 | 123.028 | 61.5667 | 61.6026 | 61.4934 | 61.5293
4071.0938 | 123.2574 | -61.5875 | 61.5875 | 0.39198 | 0.94393 | 2.5291 | 1.6919 | -0.018671 | 0.31908 | 3.4808 | 61.592 | 0.25779 | 61.505 | -0.033101 | 0.048236 | 61.6669 | 0.003143 | 61.4542 | 61.9795 | 62.5314 | 64.1166 | 63.2794 | 61.5689 | 61.9066 | 65.0683 | 123.1796 | 61.8453 | 123.0925 | 61.5544 | 61.6358 | 123.2544 | 61.5907 | 123.0418 | 61.5438 | 61.5889 | 61.4567 | 61.5018
4072.0625 | 123.2986 | -61.5784 | 61.5875 | 0.39655 | 0.87524 | 2.5932 | 1.6782 | -0.014093 | 0.34197 | 3.4121 | 61.6058 | 0.26695 | 61.5324 | -0.028522 | 0.039079 | 61.6715 | -0.001436 | 61.4542 | 61.9749 | 62.4536 | 64.1716 | 63.2566 | 61.5643 | 61.9203 | 64.9905 | 123.1841 | 61.8453 | 123.1108 | 61.5498 | 61.6174 | 123.2498 | 61.5769 | 123.0326 | 61.5667 | 61.6072 | 61.4934 | 61.5339
4073.0781 | 123.2986 | -61.5601 | 61.6241 | 0.42402 | 0.98513 | 2.4788 | 1.6278 | -0.050716 | 0.37402 | 3.7463 | 61.5966 | 0.26695 | 61.5096 | -0.028522 | 0.043657 | 61.6715 | 0.012299 | 61.4634 | 61.9841 | 62.5452 | 64.0388 | 63.1879 | 61.5093 | 61.9341 | 65.3064 | 123.1567 | 61.827 | 123.0696 | 61.5315 | 61.6037 | 123.2315 | 61.5724 | 123.0234 | 61.553 | 61.5843 | 61.4659 | 61.4973
4074.0625 | 123.3261 | -61.5555 | 61.5967 | 0.26836 | 0.74246 | 2.5108 | 1.3806 | -0.12854 | 0.2092 | 1.8876 | 61.6195 | 0.26695 | 61.5508 | -0.033101 | 0.039079 | 61.6531 | 0.007721 | 61.4268 | 61.8238 | 62.2979 | 64.0663 | 62.9361 | 61.4269 | 61.7647 | 63.4431 | 123.175 | 61.8224 | 123.1062 | 61.5224 | 61.5946 | 123.2086 | 61.5632 | 122.9822 | 61.5804 | 61.6118 | 61.5117 | 61.543
4075.0938 | 123.3124 | -61.5417 | 61.647 | 0.78114 | 0.83861 | 2.4696 | 1.4767 | -0.08734 | -0.27611 | 1.9013 | 61.6149 | 0.26695 | 61.5279 | -0.033101 | 0.043657 | 61.6577 | 0.007721 | 61.4268 | 62.3229 | 62.3804 | 64.0114 | 63.0185 | 61.4544 | 61.2656 | 63.4431 | 123.1567 | 61.8087 | 123.0696 | 61.5086 | 61.5854 | 123.1995 | 61.5495 | 122.9685 | 61.5713 | 61.6072 | 61.4842 | 61.5202
4076.0625 | 123.3719 | -61.5463 | 61.5921 | 0.87728 | 0.92103 | 2.4009 | 1.4538 | -0.055294 | -0.23033 | 2.9406 | 61.6104 | 0.27153 | 61.5416 | -0.033101 | 0.043657 | 61.6715 | -0.001436 | 61.4405 | 62.4236 | 62.4674 | 63.9472 | 63.0002 | 61.491 | 61.316 | 64.4869 | 123.1567 | 61.8179 | 123.0879 | 61.5132 | 61.59 | 123.2178 | 61.5449 | 122.9868 | 61.5667 | 61.6118 | 61.4979 | 61.543
4077.0938 | 123.3124 | -61.5463 | 61.6425 | 0.53391 | 0.68293 | 2.4742 | 1.2158 | -0.11939 | -0.11129 | 2.1348 | 61.6149 | 0.26695 | 61.5279 | -0.033101 | 0.043657 | 61.6531 | 0.007721 | 61.4313 | 62.0802 | 62.2293 | 64.0205 | 62.7621 | 61.4269 | 61.435 | 63.6811 | 123.1613 | 61.8133 | 123.0742 | 61.5132 | 61.59 | 123.1995 | 61.554 | 122.9777 | 61.5713 | 61.6072 | 61.4842 | 61.5202
4078.0625 | 123.3215 | -61.5646 | 61.5921 | 0.64379 | 0.90729 | 3.1839 | 1.6782 | 0.26516 | 0.53884 | 3.6685 | 61.5829 | 0.26237 | 61.5279 | -0.033101 | 0.043657 | 61.6898 | -0.006014 | 61.4588 | 62.2084 | 62.4719 | 64.7485 | 63.2428 | 61.8298 | 62.1035 | 65.2331 | 123.1475 | 61.827 | 123.0925 | 61.5315 | 61.6083 | 123.2544 | 61.5586 | 123.0234 | 61.5392 | 61.5889 | 61.4842 | 61.5339
4079.0938 | 123.3719 | -61.5417 | 61.5921 | 0.97801 | 0.73788 | 2.7855 | 1.7011 | 0.031687 | -0.079239 | 3.6456 | 61.592 | 0.27153 | 61.4958 | -0.033101 | 0.043657 | 61.6715 | -0.001436 | 61.4542 | 62.5198 | 62.2796 | 64.3273 | 63.2428 | 61.5734 | 61.4625 | 65.1874 | 123.1338 | 61.8133 | 123.0376 | 61.5086 | 61.5854 | 123.2132 | 61.5403 | 122.996 | 61.5484 | 61.5935 | 61.4522 | 61.4973
4080.0625 | 123.2895 | -61.5829 | 61.6058 | 0.99632 | 0.85235 | 2.9961 | 1.6873 | 0.022531 | -0.04719 | 3.5907 | 61.5966 | 0.26237 | 61.5324 | -0.033101 | 0.039079 | 61.676 | 0.003143 | 61.4634 | 62.5793 | 62.4353 | 64.5791 | 63.2703 | 61.6055 | 61.5358 | 65.1736 | 123.1796 | 61.8453 | 123.1154 | 61.5498 | 61.622 | 123.259 | 61.5861 | 123.0463 | 61.5575 | 61.5935 | 61.4934 | 61.5293
4081.1094 | 123.3444 | -61.5738 | 61.6104 | 0.99632 | 0.85693 | 3.0694 | 1.6278 | 0.082044 | -0.010563 | 3.3618 | 61.592 | 0.26695 | 61.4958 | -0.033101 | 0.043657 | 61.6806 | 0.012299 | 61.4634 | 62.5701 | 62.4307 | 64.6432 | 63.2016 | 61.6558 | 61.5632 | 64.9355 | 123.1658 | 61.8407 | 123.0696 | 61.5407 | 61.6174 | 123.2544 | 61.5861 | 123.0372 | 61.5484 | 61.5797 | 61.4522 | 61.4835
4082.0625 | 123.2529 | -61.6058 | 61.5601 | 1.0604 | 0.87524 | 3.2617 | 1.3943 | 0.10036 | 0.030642 | 3.7143 | 61.592 | 0.26695 | 61.5233 | -0.033101 | 0.043657 | 61.6852 | 0.003143 | 61.4634 | 62.6663 | 62.4811 | 64.8675 | 63.0002 | 61.7062 | 61.6365 | 65.3201 | 123.1979 | 61.8728 | 123.1291 | 61.5727 | 61.6495 | 123.291 | 61.609 | 123.0692 | 61.5484 | 61.5889 | 61.4796 | 61.5202
4083.0938 | 123.3536 | -61.5372 | 61.5875 | 1.0604 | 0.93019 | 3.1976 | 1.2936 | 0.06831 | -0.015142 | 3.8333 | 61.592 | 0.26695 | 61.5233 | -0.042259 | 0.048236 | 61.6852 | 0.012299 | 61.4725 | 62.5976 | 62.4674 | 64.7348 | 62.8308 | 61.6055 | 61.522 | 65.3705 | 123.1292 | 61.8041 | 123.0605 | 61.4949 | 61.5854 | 123.2224 | 61.5495 | 123.0097 | 61.5438 | 61.5797 | 61.4751 | 61.511
4084.0625 | 123.3353 | -61.5692 | 61.5784 | 0.97801 | 0.82488 | 3.3258 | 1.4309 | 0.06831 | -0.015142 | 3.6548 | 61.5966 | 0.26237 | 61.505 | -0.033101 | 0.043657 | 61.676 | 0.007721 | 61.468 | 62.5472 | 62.3941 | 64.895 | 63.0002 | 61.6375 | 61.5541 | 65.224 | 123.1658 | 61.8316 | 123.0742 | 61.5361 | 61.6129 | 123.2452 | 61.5769 | 123.0372 | 61.553 | 61.5889 | 61.4613 | 61.4973
4085.0781 | 123.2849 | -61.5784 | 61.5829 | 0.50186 | 0.74246 | 3.1656 | 1.4264 | 0.072888 | 0.42896 | 3.4945 | 61.5966 | 0.26695 | 61.5279 | -0.028522 | 0.048236 | 61.6715 | 0.007721 | 61.4634 | 62.0802 | 62.3208 | 64.7439 | 63.0047 | 61.6513 | 62.0073 | 65.0729 | 123.175 | 61.8453 | 123.1062 | 61.5498 | 61.6266 | 123.2498 | 61.5861 | 123.0418 | 61.5484 | 61.5889 | 61.4796 | 61.5202
4086.0625 | 123.317 | -61.5875 | 61.5921 | 0.4927 | 0.72872 | 3.1564 | 1.5134 | 0.086622 | 0.4427 | 3.7921 | 61.592 | 0.26695 | 61.5096 | -0.028522 | 0.048236 | 61.6852 | 0.003143 | 61.4725 | 62.0802 | 62.3162 | 64.7439 | 63.1009 | 61.6741 | 62.0302 | 65.3796 | 123.1796 | 61.8545 | 123.0971 | 61.559 | 61.6358 | 123.2727 | 61.5907 | 123.0601 | 61.5438 | 61.5889 | 61.4613 | 61.5064
4087.0781 | 123.3078 | -61.5738 | 61.6058 | 0.49728 | 0.66462 | 3.1152 | 1.463 | 0.063733 | 0.43354 | 3.5952 | 61.5875 | 0.26695 | 61.5324 | -0.03768 | 0.052814 | 61.6715 | 0.007721 | 61.468 | 62.0711 | 62.2384 | 64.689 | 63.0368 | 61.6375 | 62.0073 | 65.169 | 123.1613 | 61.8407 | 123.1062 | 61.5361 | 61.6266 | 123.2452 | 61.5815 | 123.0418 | 61.5346 | 61.5797 | 61.4796 | 61.5247
4088.0625 | 123.317 | -61.5646 | 61.6104 | 0.34161 | 0.45399 | 3.0923 | 1.4309 | -0.059872 | 0.2733 | 2.2905 | 61.6104 | 0.26695 | 61.537 | -0.033101 | 0.043657 | 61.6623 | 0.012299 | 61.4588 | 61.9062 | 62.0186 | 64.6569 | 62.9956 | 61.5048 | 61.8379 | 63.8551 | 123.175 | 61.8316 | 123.1017 | 61.5315 | 61.6083 | 123.2269 | 61.5769 | 123.0234 | 61.5667 | 61.5981 | 61.4934 | 61.5247
4089.0781 | 123.3948 | -61.5509 | 61.5784 | 0.86813 | 0.60967 | 3.0373 | 1.4401 | -0.046138 | -0.079239 | 3.3663 | 61.5966 | 0.26695 | 61.5233 | -0.028522 | 0.048236 | 61.6806 | 0.007721 | 61.4496 | 62.419 | 62.1606 | 64.5883 | 62.991 | 61.5048 | 61.4717 | 64.9172 | 123.1475 | 61.8179 | 123.0742 | 61.5224 | 61.5991 | 123.2315 | 61.5586 | 123.0006 | 61.5484 | 61.5889 | 61.4751 | 61.5156
4090.0625 | 123.3536 | -61.5646 | 61.5738 | 0.64379 | 0.55473 | 3.0236 | 1.3806 | -0.032405 | 0.12679 | 3.4304 | 61.6012 | 0.26695 | 61.5279 | -0.019364 | 0.043657 | 61.676 | 0.007721 | 61.4588 | 62.2084 | 62.1194 | 64.5883 | 62.9452 | 61.5322 | 61.6914 | 64.9951 | 123.1658 | 61.8316 | 123.0925 | 61.5453 | 61.6083 | 123.2407 | 61.5724 | 123.0234 | 61.5575 | 61.5935 | 61.4842 | 61.5202
4091.1094 | 123.3353 | -61.5417 | 61.6196 | 0.69415 | 0.42194 | 3.0328 | 1.4218 | -0.10565 | -0.17081 | 2.4141 | 61.6104 | 0.27153 | 61.5462 | -0.033101 | 0.043657 | 61.6577 | 0.003143 | 61.4405 | 62.2359 | 61.9637 | 64.5745 | 62.9635 | 61.4361 | 61.3709 | 63.9558 | 123.1521 | 61.8133 | 123.0879 | 61.5086 | 61.5854 | 123.1995 | 61.5449 | 122.9822 | 61.5667 | 61.6072 | 61.5025 | 61.543
4092.0625 | 123.3307 | -61.5601 | 61.5921 | 0.35535 | 0.47689 | 2.9458 | 1.4493 | -0.069028 | 0.27787 | 2.8536 | 61.6104 | 0.27153 | 61.5416 | -0.033101 | 0.039079 | 61.6623 | 0.003143 | 61.4634 | 61.9154 | 62.0369 | 64.5058 | 63.0093 | 61.491 | 61.8379 | 64.4136 | 123.1704 | 61.8316 | 123.1017 | 61.527 | 61.5991 | 123.2224 | 61.5632 | 123.0234 | 61.5713 | 61.6072 | 61.5025 | 61.5385
4093.0938 | 123.2849 | -61.5646 | 61.6287 | 0.47896 | 0.54557 | 2.9458 | 1.3989 | -0.009515 | 0.40149 | 3.7326 | 61.6012 | 0.25779 | 61.5233 | -0.033101 | 0.052814 | 61.6806 | -0.001436 | 61.4725 | 62.0436 | 62.1102 | 64.5104 | 62.9635 | 61.5551 | 61.9661 | 65.2972 | 123.1658 | 61.8224 | 123.0879 | 61.5315 | 61.6174 | 123.2452 | 61.5632 | 123.0372 | 61.5484 | 61.6026 | 61.4705 | 61.5247
4094.0625 | 123.349 | -61.5646 | 61.6241 | 0.45149 | 0.54099 | 3.0145 | 1.495 | -0.023249 | 0.34655 | 3.3206 | 61.6058 | 0.26237 | 61.537 | -0.033101 | 0.048236 | 61.6715 | 0.003143 | 61.4634 | 62.0161 | 62.1056 | 64.5791 | 63.0597 | 61.5414 | 61.9112 | 64.8852 | 123.1704 | 61.827 | 123.1017 | 61.5315 | 61.6129 | 123.2361 | 61.5678 | 123.028 | 61.5575 | 61.6026 | 61.4888 | 61.5339
4095.0938 | 123.3536 | -61.5417 | 61.6196 | 0.36451 | 0.55015 | 3.2617 | 1.4218 | -0.055294 | 0.26414 | 2.2264 | 61.6058 | 0.27153 | 61.5233 | -0.046838 | 0.043657 | 61.6577 | 0.007721 | 61.4496 | 61.9063 | 62.0919 | 64.8034 | 62.9635 | 61.4865 | 61.8059 | 63.7681 | 123.1475 | 61.8133 | 123.065 | 61.4949 | 61.5854 | 123.1995 | 61.5495 | 122.9914 | 61.5621 | 61.5981 | 61.4796 | 61.5156
4096.0625 | 123.3948 | -61.5601 | 61.5463 | 0.37366 | 0.48604 | 3.2022 | 1.5866 | -0.018671 | 0.29619 | 2.9085 | 61.6058 | 0.26695 | 61.5324 | -0.03768 | 0.039079 | 61.6715 | 0.012299 | 61.4588 | 61.9337 | 62.0461 | 64.7622 | 63.1467 | 61.5414 | 61.8562 | 64.4686 | 123.1658 | 61.827 | 123.0925 | 61.5224 | 61.5991 | 123.2315 | 61.5724 | 123.0189 | 61.5667 | 61.5935 | 61.4934 | 61.5202
4097.0938 | 123.3353 | -61.5326 | 61.5875 | 0.26836 | 0.30289 | 3.2022 | 1.4859 | -0.11481 | 0.19546 | 2.0844 | 61.6149 | 0.27153 | 61.5233 | -0.033101 | 0.039079 | 61.6623 | 0.003143 | 61.4496 | 61.801 | 61.8355 | 64.7348 | 63.0185 | 61.4178 | 61.7281 | 63.617 | 123.1475 | 61.8041 | 123.0559 | 61.4995 | 61.5717 | 123.1949 | 61.5357 | 122.9822 | 61.5759 | 61.6118 | 61.4842 | 61.5202
4098.0625 | 123.2986 | -61.5417 | 61.5921 | 0.29125 | 0.36699 | 3.2663 | 1.495 | -0.12396 | 0.22293 | 2.5652 | 61.6149 | 0.26237 | 61.5508 | -0.028522 | 0.043657 | 61.6669 | 0.007721 | 61.4542 | 61.833 | 61.9087 | 64.808 | 63.0368 | 61.4178 | 61.7647 | 64.1069 | 123.1567 | 61.8041 | 123.0925 | 61.5132 | 61.5854 | 123.2086 | 61.5495 | 122.996 | 61.5713 | 61.6072 | 61.5071 | 61.543
4099.0625 | 123.3124 | -61.5601 | 61.5875 | 0.33246 | 0.49978 | 3.3121 | 1.5683 | -0.11939 | 0.2733 | 3.0138 | 61.6058 | 0.26237 | 61.5096 | -0.033101 | 0.048236 | 61.6715 | 0.007721 | 61.468 | 61.8925 | 62.0598 | 64.8721 | 63.1284 | 61.4407 | 61.8334 | 64.5739 | 123.1658 | 61.8224 | 123.0696 | 61.527 | 61.6083 | 123.2315 | 61.5678 | 123.028 | 61.5575 | 61.5981 | 61.4613 | 61.5018
4100.0781 | 123.5138 | -61.5234 | 61.647 | 0.30499 | 0.54557 | 3.2754 | 1.5775 | -0.10565 | 0.24125 | 2.8353 | 61.6058 | 0.27153 | 61.5416 | -0.033101 | 0.048236 | 61.6669 | 0.012299 | 61.4542 | 61.8284 | 62.069 | 64.7989 | 63.1009 | 61.4178 | 61.7647 | 64.3587 | 123.1292 | 61.795 | 123.065 | 61.4903 | 61.5717 | 123.1903 | 61.5357 | 122.9777 | 61.5575 | 61.5935 | 61.4934 | 61.5293
4101.0625 | 123.3994 | -61.5372 | 61.5417 | 0.34619 | 0.48604 | 3.3212 | 1.4538 | -0.059872 | 0.29161 | 2.9039 | 61.6012 | 0.27153 | 61.505 | -0.03768 | 0.043657 | 61.6669 | -0.001436 | 61.468 | 61.8834 | 62.0232 | 64.8584 | 62.991 | 61.4773 | 61.8288 | 64.4411 | 123.1384 | 61.8087 | 123.0422 | 61.4995 | 61.5808 | 123.204 | 61.5357 | 123.0051 | 61.5575 | 61.6026 | 61.4613 | 61.5064
4102.0938 | 123.2895 | -61.5601 | 61.5784 | 0.3874 | 0.50436 | 3.4128 | 1.4996 | -0.018671 | 0.32824 | 2.8078 | 61.6058 | 0.27153 | 61.537 | -0.033101 | 0.043657 | 61.6715 | -0.001436 | 61.4588 | 61.9475 | 62.0644 | 64.9729 | 63.0597 | 61.5414 | 61.8883 | 64.3679 | 123.1658 | 61.8316 | 123.0971 | 61.527 | 61.6037 | 123.2315 | 61.5586 | 123.0189 | 61.5621 | 61.6072 | 61.4934 | 61.5385
4103.0625 | 123.2895 | -61.5829 | 61.5921 | 0.29583 | 0.42652 | 3.3487 | 1.3943 | -0.069028 | 0.24583 | 2.2081 | 61.6012 | 0.26237 | 61.5233 | -0.033101 | 0.039079 | 61.6577 | 0.003143 | 61.4542 | 61.8788 | 62.0095 | 64.9316 | 62.9773 | 61.5139 | 61.8288 | 63.791 | 123.1841 | 61.8453 | 123.1062 | 61.5498 | 61.622 | 123.2407 | 61.5861 | 123.0372 | 61.5621 | 61.5981 | 61.4842 | 61.5202
4104.0625 | 123.2574 | -61.5555 | 61.6013 | 0.23631 | 0.35326 | 3.1839 | 1.4767 | -0.14685 | 0.18173 | 2.1485 | 61.6195 | 0.27153 | 61.5508 | -0.028522 | 0.048236 | 61.6623 | 0.003143 | 61.4451 | 61.7918 | 61.9087 | 64.7393 | 63.0322 | 61.4086 | 61.7372 | 63.704 | 123.175 | 61.827 | 123.1062 | 61.527 | 61.6037 | 123.2178 | 61.5586 | 123.0006 | 61.5713 | 61.6164 | 61.5025 | 61.5476
4105.0781 | 123.317 | -61.528 | 61.6287 | 0.16306 | 0.18842 | 3.3304 | 1.3394 | -0.1789 | 0.11305 | 1.0452 | 61.6241 | 0.26237 | 61.5416 | -0.033101 | 0.052814 | 61.644 | 0.003143 | 61.4451 | 61.6911 | 61.7164 | 64.8584 | 62.8674 | 61.3491 | 61.6411 | 62.5732 | 123.1521 | 61.7904 | 123.0696 | 61.4949 | 61.5808 | 123.172 | 61.5312 | 122.9731 | 61.5713 | 61.6209 | 61.4888 | 61.5385
4106.0625 | 123.3398 | -61.5417 | 61.5875 | 0.29583 | 0.37157 | 3.3441 | 1.3531 | -0.12396 | 0.24125 | 2.1714 | 61.6149 | 0.26237 | 61.5462 | -0.033101 | 0.048236 | 61.6577 | 0.003143 | 61.4451 | 61.8376 | 61.9133 | 64.8859 | 62.8949 | 61.4178 | 61.783 | 63.7132 | 123.1567 | 61.8041 | 123.0879 | 61.5086 | 61.59 | 123.1995 | 61.5449 | 122.9868 | 61.5667 | 61.6118 | 61.4979 | 61.543
4107.0938 | 123.3765 | -61.5051 | 61.5738 | 0.3233 | 0.46773 | 2.7443 | 1.3668 | -0.14228 | 0.26414 | 2.2538 | 61.6287 | 0.27153 | 61.5462 | -0.028522 | 0.039079 | 61.6531 | 0.003143 | 61.4634 | 61.8284 | 61.9729 | 64.2494 | 62.872 | 61.3629 | 61.7693 | 63.759 | 123.1338 | 61.7767 | 123.0513 | 61.4766 | 61.5442 | 123.1583 | 61.5083 | 122.9685 | 61.5896 | 61.6255 | 61.5071 | 61.543
4108.0625 | 123.2346 | -61.5417 | 61.6104 | 0.20884 | 0.33952 | 2.6436 | 1.2524 | -0.1377 | 0.14052 | 0.99484 | 61.6378 | 0.26237 | 61.5553 | -0.042259 | 0.039079 | 61.6348 | -0.001436 | 61.4405 | 61.7506 | 61.8813 | 64.1853 | 62.7941 | 61.404 | 61.6823 | 62.5366 | 123.1796 | 61.8041 | 123.0971 | 61.4995 | 61.5808 | 123.1766 | 61.5403 | 122.9822 | 61.5987 | 61.6393 | 61.5163 | 61.5568
4109.0781 | 123.3078 | -61.5326 | 61.6287 | 0.22258 | 0.39447 | 2.6299 | 1.2341 | -0.13312 | 0.17715 | 1.558 | 61.6287 | 0.25779 | 61.5645 | -0.033101 | 0.043657 | 61.6394 | -0.001436 | 61.4451 | 61.7552 | 61.9271 | 64.1624 | 62.7667 | 61.3995 | 61.7097 | 63.0905 | 123.1613 | 61.7904 | 123.0971 | 61.4995 | 61.5763 | 123.172 | 61.5312 | 122.9777 | 61.585 | 61.6301 | 61.5208 | 61.5659
4110.0625 | 123.2758 | -61.5417 | 61.615 | 0.1539 | 0.29373 | 2.6482 | 1.1379 | -0.12854 | 0.099318 | 0.81629 | 61.6378 | 0.25779 | 61.5462 | -0.042259 | 0.048236 | 61.6394 | 0.003143 | 61.4359 | 61.6956 | 61.8355 | 64.1899 | 62.6797 | 61.4132 | 61.6411 | 62.358 | 123.1796 | 61.7995 | 123.0879 | 61.4995 | 61.59 | 123.1812 | 61.5449 | 122.9777 | 61.5896 | 61.6347 | 61.4979 | 61.543
4111.0938 | 123.3353 | -61.5143 | 61.647 | 0.1539 | 0.18842 | 3.1564 | 1.2249 | -0.18348 | 0.085583 | 0.75678 | 61.6378 | 0.26695 | 61.5782 | -0.028522 | 0.043657 | 61.644 | 0.007721 | 61.4405 | 61.6682 | 61.7027 | 64.6707 | 62.7392 | 61.3308 | 61.5999 | 62.2711 | 123.1521 | 61.7812 | 123.0925 | 61.4858 | 61.5579 | 123.1583 | 61.522 | 122.9548 | 61.5942 | 61.6301 | 61.5346 | 61.5705
4112.0625 | 123.2941 | -61.5784 | 61.6058 | 0.16764 | 0.2571 | 2.6665 | 1.3897 | -0.19263 | 0.1039 | 0.95822 | 61.6287 | 0.26695 | 61.537 | -0.03768 | 0.039079 | 61.644 | 0.007721 | 61.4268 | 61.746 | 61.8355 | 64.2449 | 62.9681 | 61.3857 | 61.6823 | 62.5366 | 123.207 | 61.8453 | 123.1154 | 61.5407 | 61.6174 | 123.2224 | 61.5861 | 123.0051 | 61.5896 | 61.6209 | 61.4979 | 61.5293
4113.0781 | 123.317 | -61.528 | 61.6196 | 0.20884 | 0.28 | 2.7947 | 1.4126 | -0.15601 | 0.14968 | 1.2237 | 61.6332 | 0.26695 | 61.5645 | -0.033101 | 0.043657 | 61.6486 | -0.006014 | 61.4405 | 61.7369 | 61.808 | 64.3227 | 62.9406 | 61.372 | 61.6777 | 62.7518 | 123.1613 | 61.795 | 123.0925 | 61.4949 | 61.5717 | 123.1766 | 61.522 | 122.9685 | 61.5896 | 61.6393 | 61.5208 | 61.5705
4114.0625 | 123.2346 | -61.615 | 61.5417 | 0.58427 | 0.5593 | 3.8661 | 1.9025 | 0.28347 | 0.54342 | 2.0524 | 61.5875 | 0.26695 | 61.4912 | -0.033101 | 0.039079 | 61.676 | 0.003143 | 61.4725 | 62.1993 | 62.1743 | 65.4811 | 63.5175 | 61.8985 | 62.1584 | 63.6674 | 123.2025 | 61.8819 | 123.1062 | 61.5819 | 61.6541 | 123.291 | 61.6181 | 123.0875 | 61.5484 | 61.5843 | 61.4522 | 61.4881
4115.0781 | 123.3215 | -61.5463 | 61.5921 | 0.50644 | 0.45857 | 3.6646 | 1.7606 | 0.19192 | 0.45643 | 2.0799 | 61.6104 | 0.26695 | 61.5416 | -0.028522 | 0.043657 | 61.676 | -0.001436 | 61.4588 | 62.0528 | 62.0049 | 65.2109 | 63.3069 | 61.7382 | 62.0028 | 63.6262 | 123.1567 | 61.8133 | 123.0879 | 61.5178 | 61.59 | 123.2224 | 61.5449 | 123.0051 | 61.5667 | 61.6118 | 61.4979 | 61.543
4116.0625 | 123.3902 | -61.5234 | 61.5509 | 0.42402 | 0.51809 | 3.5959 | 1.7423 | 0.14156 | 0.3786 | 2.2538 | 61.5966 | 0.25779 | 61.5004 | -0.03768 | 0.039079 | 61.6715 | -0.001436 | 61.4542 | 61.9475 | 62.0415 | 65.1194 | 63.2657 | 61.665 | 61.902 | 63.7773 | 123.1201 | 61.7812 | 123.0238 | 61.4858 | 61.5625 | 123.1949 | 61.522 | 122.9777 | 61.5575 | 61.5981 | 61.4613 | 61.5018
4117.0938 | 123.4451 | -61.5463 | 61.5509 | 0.45607 | 0.50436 | 2.7123 | 1.6919 | 0.13698 | 0.40149 | 2.4141 | 61.6104 | 0.26695 | 61.5508 | -0.03768 | 0.043657 | 61.6577 | 0.007721 | 61.4451 | 62.0024 | 62.0507 | 64.2586 | 63.2382 | 61.6833 | 61.9478 | 63.9604 | 123.1567 | 61.8133 | 123.0971 | 61.5086 | 61.59 | 123.204 | 61.554 | 122.9914 | 61.5667 | 61.6026 | 61.5071 | 61.543
4118.0625 | 123.3627 | -61.5646 | 61.5555 | 0.45607 | 0.46315 | 3.3762 | 1.7331 | 0.095778 | 0.38776 | 2.5423 | 61.5875 | 0.26695 | 61.5096 | -0.033101 | 0.039079 | 61.6715 | -0.001436 | 61.4542 | 62.0207 | 62.0278 | 64.9408 | 63.2978 | 61.6604 | 61.9524 | 64.1069 | 123.1521 | 61.8316 | 123.0742 | 61.5315 | 61.6037 | 123.2361 | 61.5632 | 123.0189 | 61.5484 | 61.5889 | 61.4705 | 61.511
4119.0938 | 123.2986 | -61.5738 | 61.5784 | 0.4927 | 0.60509 | 2.8313 | 1.6553 | 0.10036 | 0.40607 | 2.643 | 61.6012 | 0.26695 | 61.537 | -0.028522 | 0.048236 | 61.6715 | 0.012299 | 61.4359 | 62.0665 | 62.1789 | 64.4051 | 63.2291 | 61.6741 | 61.9799 | 64.2168 | 123.175 | 61.8407 | 123.1108 | 61.5453 | 61.622 | 123.2452 | 61.5861 | 123.0097 | 61.553 | 61.5889 | 61.4888 | 61.5247
4120.0625 | 123.349 | -61.5463 | 61.5417 | 0.48354 | 0.64172 | 2.7764 | 1.7469 | 0.14156 | 0.42438 | 2.6842 | 61.592 | 0.26695 | 61.5324 | -0.033101 | 0.048236 | 61.6715 | -0.001436 | 61.4451 | 62.0299 | 62.188 | 64.3227 | 63.2932 | 61.6879 | 61.9707 | 64.2305 | 123.1384 | 61.8133 | 123.0788 | 61.5132 | 61.5946 | 123.2178 | 61.5449 | 122.9914 | 61.5438 | 61.5935 | 61.4842 | 61.5339
4121.1094 | 123.3444 | -61.5875 | 61.5692 | 0.51101 | 0.59136 | 2.7947 | 1.7057 | 0.19192 | 0.44728 | 2.7025 | 61.6058 | 0.26237 | 61.537 | -0.033101 | 0.043657 | 61.6715 | 0.003143 | 61.4451 | 62.0985 | 62.1789 | 64.3822 | 63.2932 | 61.7794 | 62.0348 | 64.29 | 123.1933 | 61.8499 | 123.1246 | 61.5544 | 61.6312 | 123.259 | 61.5907 | 123.0326 | 61.5621 | 61.6026 | 61.4934 | 61.5339
4122.0625 | 123.3627 | -61.5646 | 61.5463 | 0.57053 | 0.63257 | 2.9229 | 1.7331 | 0.28347 | 0.50222 | 2.8215 | 61.592 | 0.27153 | 61.5279 | -0.033101 | 0.048236 | 61.6715 | 0.003143 | 61.4496 | 62.1352 | 62.1972 | 64.4875 | 63.2978 | 61.8481 | 62.0669 | 64.3862 | 123.1567 | 61.8362 | 123.0925 | 61.5315 | 61.6129 | 123.2361 | 61.5678 | 123.0143 | 61.5438 | 61.5889 | 61.4796 | 61.5247
4123.0625 | 123.3673 | -61.5601 | 61.5555 | 0.56138 | 0.4952 | 2.8863 | 1.8842 | 0.26974 | 0.48848 | 2.8124 | 61.592 | 0.25779 | 61.5004 | -0.028522 | 0.052814 | 61.6806 | 0.003143 | 61.4588 | 62.1214 | 62.0553 | 64.4463 | 63.4443 | 61.8298 | 62.0485 | 64.3724 | 123.1521 | 61.8178 | 123.0605 | 61.5315 | 61.6129 | 123.2407 | 61.5632 | 123.0189 | 61.5392 | 61.5889 | 61.4476 | 61.4973
4124.0938 | 123.3032 | -61.5829 | 61.5875 | 0.56595 | 0.54099 | 3.0419 | 1.7331 | 0.24227 | 0.50222 | 2.8856 | 61.6012 | 0.26695 | 61.537 | -0.03768 | 0.048236 | 61.6715 | 0.003143 | 61.4542 | 62.1489 | 62.1239 | 64.6249 | 63.3161 | 61.8252 | 62.0852 | 64.4686 | 123.1841 | 61.8499 | 123.12 | 61.5453 | 61.6312 | 123.2544 | 61.5861 | 123.0372 | 61.553 | 61.5981 | 61.4888 | 61.5339
4125.0625 | 123.3856 | -61.5646 | 61.5189 | 0.53848 | 0.51809 | 3.0648 | 1.55 | 0.1736 | 0.46559 | 2.8261 | 61.592 | 0.26237 | 61.5096 | -0.03768 | 0.048236 | 61.6715 | -0.001436 | 61.4451 | 62.1031 | 62.0827 | 64.6295 | 63.1146 | 61.7382 | 62.0302 | 64.3907 | 123.1567 | 61.827 | 123.0742 | 61.527 | 61.6129 | 123.2361 | 61.5632 | 123.0097 | 61.5438 | 61.5935 | 61.4613 | 61.511
4126.1094 | 123.3444 | -61.5784 | 61.5463 | 0.53391 | 0.50436 | 2.9458 | 1.6003 | 0.10493 | 0.45643 | 3.0367 | 61.6058 | 0.27153 | 61.537 | -0.033101 | 0.039079 | 61.676 | 0.012299 | 61.4588 | 62.1123 | 62.0827 | 64.5241 | 63.1787 | 61.6833 | 62.0348 | 64.6151 | 123.1841 | 61.8499 | 123.1154 | 61.5453 | 61.6174 | 123.2544 | 61.5907 | 123.0372 | 61.5667 | 61.5935 | 61.4979 | 61.5247
4127.0625 | 123.3719 | -61.5326 | 61.5463 | 0.49728 | 0.50436 | 2.8267 | 1.6736 | 0.086622 | 0.43812 | 3.0321 | 61.5966 | 0.27153 | 61.5096 | -0.028522 | 0.048236 | 61.6715 | 0.003143 | 61.4588 | 62.0299 | 62.037 | 64.3593 | 63.2062 | 61.6192 | 61.9707 | 64.5647 | 123.1292 | 61.8041 | 123.0422 | 61.5041 | 61.5808 | 123.204 | 61.5357 | 122.9914 | 61.5484 | 61.5935 | 61.4613 | 61.5064
4128.0781 | 123.2849 | -61.5738 | 61.5555 | 0.50644 | 0.54557 | 2.8588 | 1.6232 | 0.15529 | 0.43812 | 3.0642 | 61.5966 | 0.26695 | 61.5416 | -0.03768 | 0.039079 | 61.6715 | 0.007721 | 61.4496 | 62.0802 | 62.1194 | 64.4326 | 63.197 | 61.7291 | 62.0119 | 64.638 | 123.1704 | 61.8407 | 123.1154 | 61.5361 | 61.6129 | 123.2452 | 61.5815 | 123.0234 | 61.5575 | 61.5889 | 61.5025 | 61.5339
4129.0625 | 123.3582 | -61.5692 | 61.5555 | 0.47896 | 0.60967 | 2.9366 | 1.5637 | 0.15987 | 0.4198 | 2.9268 | 61.6058 | 0.27611 | 61.5187 | -0.033101 | 0.039079 | 61.6715 | 0.003143 | 61.4451 | 62.0482 | 62.1789 | 64.5058 | 63.1329 | 61.7291 | 61.989 | 64.496 | 123.175 | 61.8453 | 123.0879 | 61.5361 | 61.6083 | 123.2407 | 61.5724 | 123.0143 | 61.5667 | 61.6026 | 61.4796 | 61.5156
4130.0938 | 123.3856 | -61.5326 | 61.5463 | 0.41487 | 0.50894 | 2.6802 | 1.495 | 0.082044 | 0.36029 | 2.5056 | 61.6058 | 0.26695 | 61.5187 | -0.028522 | 0.043657 | 61.6577 | 0.003143 | 61.4405 | 61.9475 | 62.0415 | 64.2128 | 63.0276 | 61.6146 | 61.8929 | 64.0382 | 123.1384 | 61.7995 | 123.0513 | 61.5041 | 61.5763 | 123.1903 | 61.5357 | 122.9731 | 61.5621 | 61.6026 | 61.4751 | 61.5156
4131.0625 | 123.3994 | -61.5234 | 61.5784 | 0.44692 | 0.51809 | 2.8817 | 1.495 | 0.13698 | 0.38318 | 2.4919 | 61.6012 | 0.27153 | 61.5462 | -0.03768 | 0.048236 | 61.6623 | 0.007721 | 61.4451 | 61.9704 | 62.0415 | 64.4051 | 63.0185 | 61.6604 | 61.9066 | 64.0153 | 123.1246 | 61.795 | 123.0696 | 61.4858 | 61.5717 | 123.1857 | 61.5312 | 122.9685 | 61.553 | 61.5935 | 61.4979 | 61.5385
4132.0938 | 123.3902 | -61.5738 | 61.4868 | 0.45149 | 0.58678 | 2.9046 | 1.376 | 0.10951 | 0.3786 | 2.4599 | 61.6012 | 0.26695 | 61.505 | -0.033101 | 0.043657 | 61.6669 | 0.003143 | 61.4451 | 62.0253 | 62.1606 | 64.4784 | 62.9498 | 61.6833 | 61.9524 | 64.0336 | 123.175 | 61.8407 | 123.0788 | 61.5407 | 61.6174 | 123.2407 | 61.5769 | 123.0189 | 61.5575 | 61.5981 | 61.4613 | 61.5018
4133.0625 | 123.3536 | -61.5372 | 61.5463 | 0.46981 | 0.57304 | 2.813 | 1.3348 | 0.095778 | 0.39691 | 2.2584 | 61.6012 | 0.26695 | 61.5279 | -0.03768 | 0.039079 | 61.6623 | 0.007721 | 61.4405 | 62.007 | 62.1102 | 64.3502 | 62.872 | 61.6329 | 61.9341 | 63.7956 | 123.1384 | 61.8041 | 123.065 | 61.4995 | 61.5762 | 123.1995 | 61.5449 | 122.9777 | 61.5621 | 61.5935 | 61.4888 | 61.5202
4134.0781 | 123.3765 | -61.5326 | 61.5509 | 0.46065 | 0.42652 | 2.845 | 1.4264 | 0.57646 | 0.40149 | 2.3958 | 61.6104 | 0.27153 | 61.5416 | -0.033101 | 0.048236 | 61.676 | 0.007721 | 61.4405 | 61.9932 | 61.9591 | 64.3776 | 62.959 | 62.1091 | 61.9341 | 63.9284 | 123.1429 | 61.8041 | 123.0742 | 61.4995 | 61.5808 | 123.2086 | 61.5403 | 122.9731 | 61.5621 | 61.6026 | 61.4934 | 61.5339
4135.0625 | 123.3719 | -61.5601 | 61.5646 | 0.41487 | 0.36241 | 2.8313 | 1.2753 | 0.4025 | 0.37402 | 2.7345 | 61.6012 | 0.26695 | 61.5096 | -0.03768 | 0.043657 | 61.6669 | 0.003143 | 61.4451 | 61.9749 | 61.9225 | 64.3914 | 62.8353 | 61.9626 | 61.9341 | 64.2946 | 123.1613 | 61.827 | 123.0696 | 61.5224 | 61.6037 | 123.2269 | 61.5632 | 123.0051 | 61.5575 | 61.5981 | 61.4659 | 61.5064
4136.0938 | 123.3719 | -61.5738 | 61.5417 | 0.42402 | 0.30747 | 2.7489 | 1.115 | 0.27432 | 0.35113 | 2.8673 | 61.6104 | 0.26695 | 61.537 | -0.033101 | 0.048236 | 61.6715 | 0.003143 | 61.4359 | 61.9978 | 61.8813 | 64.3227 | 62.6888 | 61.8481 | 61.9249 | 64.4411 | 123.1841 | 61.8407 | 123.1108 | 61.5407 | 61.622 | 123.2452 | 61.5769 | 123.0097 | 61.5621 | 61.6072 | 61.4888 | 61.5339
4137.0625 | 123.3856 | -61.5601 | 61.5417 | 0.4286 | 0.2571 | 2.5749 | 1.202 | 0.53984 | 0.36944 | 2.8582 | 61.6104 | 0.26237 | 61.5508 | -0.028522 | 0.048236 | 61.6669 | 0.007721 | 61.4359 | 61.9887 | 61.8172 | 64.135 | 62.7621 | 62.0999 | 61.9295 | 64.4182 | 123.1704 | 61.8224 | 123.1108 | 61.5315 | 61.6083 | 123.2269 | 61.5678 | 122.996 | 61.5621 | 61.6026 | 61.5025 | 61.543
4138.0938 | 123.3994 | -61.5463 | 61.5234 | 0.46065 | 0.22505 | 2.0942 | 1.3623 | 0.58562 | 0.41523 | 2.588 | 61.6058 | 0.27153 | 61.5187 | -0.033101 | 0.048236 | 61.6577 | 0.003143 | 61.4405 | 62.007 | 61.7714 | 63.6405 | 62.9086 | 62.1319 | 61.9616 | 64.1344 | 123.1521 | 61.8179 | 123.065 | 61.5132 | 61.5946 | 123.204 | 61.5495 | 122.9868 | 61.5575 | 61.6026 | 61.4705 | 61.5156
4139.0625 | 123.3353 | -61.5646 | 61.5509 | 0.48354 | 0.24794 | 2.607 | 1.2799 | 0.64055 | 0.42896 | 2.4324 | 61.6058 | 0.26695 | 61.5324 | -0.033101 | 0.039079 | 61.6715 | 0.003143 | 61.4359 | 62.0482 | 61.8126 | 64.1716 | 62.8445 | 62.2052 | 61.9936 | 63.997 | 123.1704 | 61.8316 | 123.0971 | 61.5315 | 61.6037 | 123.2361 | 61.5678 | 123.0005 | 61.5667 | 61.6026 | 61.4934 | 61.5293
4140.0781 | 123.3032 | -61.5875 | 61.5738 | 0.46523 | 0.21131 | 2.7397 | 1.1196 | 0.37503 | 0.40607 | 2.5148 | 61.6058 | 0.26695 | 61.5508 | -0.03768 | 0.029923 | 61.6577 | -0.001436 | 61.4359 | 62.0528 | 61.7988 | 64.3273 | 62.7071 | 61.9626 | 61.9936 | 64.1023 | 123.1933 | 61.8545 | 123.1383 | 61.5498 | 61.6174 | 123.2452 | 61.5861 | 123.0234 | 61.5759 | 61.6072 | 61.5208 | 61.5522
4141.0625 | 123.3902 | -61.5601 | 61.5417 | 0.4927 | 0.30747 | 2.7993 | 1.1837 | 0.56273 | 0.43812 | 2.5331 | 61.5966 | 0.27153 | 61.505 | -0.033101 | 0.048236 | 61.6715 | 0.007721 | 61.4359 | 62.0528 | 61.8675 | 64.3593 | 62.7438 | 62.1228 | 61.9982 | 64.0932 | 123.1567 | 61.8316 | 123.065 | 61.527 | 61.6083 | 123.2315 | 61.5678 | 122.996 | 61.5484 | 61.5889 | 61.4567 | 61.4973
4142.0781 | 123.2849 | -61.5646 | 61.6104 | 0.41487 | 0.11974 | 2.6848 | 1.0784 | 0.46202 | 0.34655 | 2.4553 | 61.6195 | 0.26695 | 61.5508 | -0.033101 | 0.052814 | 61.6623 | 0.003143 | 61.4313 | 61.9795 | 61.6844 | 64.2494 | 62.643 | 62.0267 | 61.9112 | 64.0199 | 123.1841 | 61.8316 | 123.1154 | 61.5315 | 61.6174 | 123.2269 | 61.5678 | 122.996 | 61.5667 | 61.6164 | 61.4979 | 61.5476
4143.0625 | 123.3627 | -61.5417 | 61.5417 | 0.46065 | 0.25252 | 2.6756 | 1.0326 | 0.49864 | 0.39691 | 2.6796 | 61.6012 | 0.25779 | 61.537 | -0.03768 | 0.039079 | 61.6577 | 0.003143 | 61.4405 | 62.0024 | 61.7943 | 64.2174 | 62.5744 | 62.0404 | 61.9387 | 64.2214 | 123.1429 | 61.7995 | 123.0788 | 61.5041 | 61.5808 | 123.1995 | 61.5449 | 122.9822 | 61.5621 | 61.5981 | 61.4979 | 61.5339
4144.0781 | 123.3353 | -61.5463 | 61.5784 | 0.46523 | 0.20674 | 2.5062 | 1.083 | 0.50322 | 0.41065 | 2.6979 | 61.6058 | 0.26237 | 61.5279 | -0.028522 | 0.043657 | 61.6669 | 0.007721 | 61.4313 | 62.0116 | 61.7531 | 64.0526 | 62.6293 | 62.0495 | 61.957 | 64.2442 | 123.1521 | 61.8087 | 123.0742 | 61.5178 | 61.59 | 123.2132 | 61.554 | 122.9777 | 61.5621 | 61.5981 | 61.4842 | 61.5202
4145.0625 | 123.3948 | -61.5509 | 61.5829 | 0.48354 | 0.18384 | 2.5749 | 1.1425 | 0.50322 | 0.3786 | 2.8078 | 61.6149 | 0.27153 | 61.5462 | -0.03768 | 0.043657 | 61.6623 | 0.003143 | 61.4405 | 62.0344 | 61.7347 | 64.1258 | 62.6934 | 62.0541 | 61.9295 | 64.3587 | 123.1658 | 61.8224 | 123.0971 | 61.5132 | 61.5946 | 123.2132 | 61.554 | 122.9914 | 61.5713 | 61.6118 | 61.5025 | 61.543
4146.1094 | 123.2803 | -61.5692 | 61.5646 | 0.47439 | 0.24794 | 2.4971 | 1.1288 | 0.4849 | 0.39233 | 3.0138 | 61.6058 | 0.27153 | 61.5141 | -0.042259 | 0.039079 | 61.6669 | 0.007721 | 61.4405 | 62.0436 | 61.8172 | 64.0663 | 62.698 | 62.0541 | 61.9615 | 64.583 | 123.175 | 61.8407 | 123.0833 | 61.527 | 61.6083 | 123.2361 | 61.5769 | 123.0097 | 61.5667 | 61.5981 | 61.4751 | 61.5064
4147.0625 | 123.3353 | -61.5784 | 61.5875 | 0.48354 | 0.18384 | 2.3597 | 1.0555 | 0.49864 | 0.41523 | 3.0962 | 61.6058 | 0.27153 | 61.5187 | -0.033101 | 0.048236 | 61.6669 | 0.007721 | 61.4268 | 62.0619 | 61.7622 | 63.9381 | 62.6339 | 62.077 | 61.9936 | 64.6746 | 123.1841 | 61.8499 | 123.0971 | 61.5453 | 61.6266 | 123.2452 | 61.5861 | 123.0051 | 61.5575 | 61.5981 | 61.4705 | 61.511
4148.0625 | 123.3948 | -61.5555 | 61.5601 | 0.50644 | 0.15179 | 1.9843 | 1.0464 | 0.21938 | 0.43354 | 2.8536 | 61.6058 | 0.27611 | 61.5508 | -0.03768 | 0.034501 | 61.6623 | 0.007721 | 61.4313 | 62.0619 | 61.7073 | 63.5398 | 62.6018 | 61.7749 | 61.989 | 64.4091 | 123.1613 | 61.8316 | 123.1062 | 61.5178 | 61.59 | 123.2178 | 61.5632 | 122.9868 | 61.5713 | 61.5981 | 61.5163 | 61.543
4149.0938 | 123.4085 | -61.5509 | 61.5463 | 0.51559 | 0.041898 | 2.465 | 1.0692 | 0.2789 | 0.45643 | 2.7712 | 61.6012 | 0.27153 | 61.5141 | -0.033101 | 0.052814 | 61.6577 | 0.007721 | 61.4359 | 62.0665 | 61.5928 | 64.0159 | 62.6201 | 61.8298 | 62.0073 | 64.3221 | 123.1521 | 61.8224 | 123.065 | 61.5178 | 61.6037 | 123.2086 | 61.5586 | 122.9868 | 61.5484 | 61.5935 | 61.4613 | 61.5064
4150.0625 | 123.3765 | -61.528 | 61.5509 | 0.46523 | -0.026784 | 2.4559 | 0.89984 | 0.14614 | 0.39233 | 2.6842 | 61.6195 | 0.26237 | 61.5599 | -0.028522 | 0.039079 | 61.6577 | 0.007721 | 61.4268 | 61.9932 | 61.5012 | 63.9839 | 62.4279 | 61.6742 | 61.9204 | 64.2122 | 123.1475 | 61.7904 | 123.0879 | 61.4995 | 61.5671 | 123.1857 | 61.5357 | 122.9548 | 61.5804 | 61.6118 | 61.5208 | 61.5522
4151.1094 | 123.381 | -61.5372 | 61.5601 | 0.46065 | -0.008469 | 2.378 | 0.87695 | 0.040843 | 0.3786 | 2.675 | 61.6058 | 0.26695 | 61.5279 | -0.03768 | 0.039079 | 61.6531 | -0.001436 | 61.4405 | 61.9978 | 61.5287 | 63.9152 | 62.4141 | 61.578 | 61.9158 | 64.2122 | 123.1429 | 61.8041 | 123.065 | 61.4995 | 61.5762 | 123.1903 | 61.5357 | 122.9777 | 61.5667 | 61.6072 | 61.4888 | 61.5293
4152.0625 | 123.4039 | -61.5417 | 61.6058 | 0.71704 | 0.028162 | 2.0896 | 0.86321 | 0.004219 | 0.1451 | 2.6613 | 61.6241 | 0.26695 | 61.5645 | -0.033101 | 0.039079 | 61.6486 | 0.003143 | 61.4268 | 62.2588 | 61.5699 | 63.6313 | 62.405 | 61.546 | 61.6868 | 64.203 | 123.1658 | 61.8087 | 123.1062 | 61.5086 | 61.5808 | 123.1903 | 61.5449 | 122.9685 | 61.585 | 61.6209 | 61.5254 | 61.5614
4153.0781 | 123.3444 | -61.6058 | 61.5509 | 0.47439 | 0.023583 | 2.0804 | 0.80827 | 0.045421 | 0.33739 | 2.6338 | 61.6195 | 0.25779 | 61.5508 | -0.028522 | 0.039079 | 61.6486 | -0.001436 | 61.4313 | 62.0802 | 61.6294 | 63.6863 | 62.4141 | 61.6513 | 61.9432 | 64.2397 | 123.2253 | 61.8636 | 123.1566 | 61.5773 | 61.6449 | 123.2544 | 61.6044 | 123.0372 | 61.5804 | 61.6209 | 61.5117 | 61.5522
4154.0625 | 123.3719 | -61.528 | 61.5784 | 0.3874 | 0.023583 | 1.9797 | 0.82658 | 0.36588 | 0.32824 | 2.5926 | 61.6149 | 0.26237 | 61.5233 | -0.033101 | 0.043657 | 61.6531 | 0.007721 | 61.4359 | 61.9154 | 61.5516 | 63.5077 | 62.3546 | 61.8939 | 61.8563 | 64.1206 | 123.1429 | 61.7904 | 123.0513 | 61.4949 | 61.5717 | 123.1812 | 61.5357 | 122.9639 | 61.5713 | 61.6072 | 61.4796 | 61.5156
4155.0781 | 123.3948 | -61.528 | 61.5509 | 0.37366 | 0.078529 | 2.0484 | 0.95936 | 0.33841 | 0.31908 | 2.4278 | 61.6241 | 0.26695 | 61.5645 | -0.033101 | 0.034501 | 61.6531 | -0.001436 | 61.4268 | 61.9017 | 61.6065 | 63.5764 | 62.4874 | 61.8664 | 61.8471 | 63.9558 | 123.1521 | 61.795 | 123.0925 | 61.4949 | 61.5625 | 123.1812 | 61.5266 | 122.9548 | 61.5896 | 61.6255 | 61.53 | 61.5659
4156.0625 | 123.317 | -61.5372 | 61.6241 | 0.34619 | 0.064792 | 2.085 | 0.89068 | 0.31552 | 0.29161 | 2.1714 | 61.6241 | 0.27153 | 61.5553 | -0.03768 | 0.048236 | 61.6531 | 0.003143 | 61.4268 | 61.8834 | 61.602 | 63.6222 | 62.4279 | 61.8527 | 61.8288 | 63.7086 | 123.1613 | 61.8087 | 123.0925 | 61.4995 | 61.5854 | 123.1903 | 61.5403 | 122.9639 | 61.5759 | 61.6209 | 61.5071 | 61.5522
4157.0781 | 123.4085 | -61.5234 | 61.5829 | 0.65294 | 0.051056 | 1.9614 | 0.89984 | 0.30179 | -0.051769 | 1.8967 | 61.6195 | 0.26695 | 61.5462 | -0.033101 | 0.039079 | 61.6486 | 0.007721 | 61.4222 | 62.1764 | 61.5745 | 63.4848 | 62.4233 | 61.8252 | 61.4717 | 63.4202 | 123.1429 | 61.7904 | 123.0696 | 61.4903 | 61.5625 | 123.172 | 61.5312 | 122.9456 | 61.5804 | 61.6118 | 61.5071 | 61.5385
4158.0625 | 123.4726 | -61.5143 | 61.5784 | 0.33246 | 0.019004 | 1.9431 | 0.93189 | 0.30636 | 0.22751 | 1.8739 | 61.6332 | 0.27153 | 61.5737 | -0.033101 | 0.052814 | 61.6394 | 0.003143 | 61.4313 | 61.8467 | 61.5333 | 63.4573 | 62.4462 | 61.8206 | 61.7418 | 63.3881 | 123.1475 | 61.7858 | 123.0879 | 61.4812 | 61.5671 | 123.1537 | 61.5174 | 122.9456 | 61.5804 | 61.6301 | 61.5208 | 61.5705
4159.0781 | 123.3398 | -61.5326 | 61.5738 | 0.30499 | -0.008469 | 1.9293 | 0.84032 | 0.2789 | 0.2504 | 1.9196 | 61.6287 | 0.27153 | 61.5462 | -0.03768 | 0.039079 | 61.6394 | -0.001436 | 61.4176 | 61.8376 | 61.5241 | 63.4619 | 62.3729 | 61.8115 | 61.783 | 63.4522 | 123.1613 | 61.8041 | 123.0788 | 61.4949 | 61.5717 | 123.172 | 61.5312 | 122.9502 | 61.5896 | 61.6301 | 61.5071 | 61.5476
4160.0625 | 123.4131 | -61.5143 | 61.6058 | 0.36451 | 0.037319 | 1.8149 | 0.85405 | 0.34757 | 0.30535 | 2.6338 | 61.6149 | 0.26237 | 61.537 | -0.028522 | 0.043657 | 61.6486 | 0.007721 | 61.4268 | 61.8788 | 61.5516 | 63.3291 | 62.3683 | 61.8618 | 61.8196 | 64.1481 | 123.1292 | 61.7767 | 123.0513 | 61.4858 | 61.5579 | 123.1628 | 61.522 | 122.941 | 61.5713 | 61.6072 | 61.4934 | 61.5293
4161.0938 | 123.2803 | -61.5601 | 61.6196 | 0.41029 | 0.019004 | 1.9614 | 0.97767 | 0.37961 | 0.36944 | 2.7208 | 61.6241 | 0.27153 | 61.5599 | -0.028522 | 0.034501 | 61.6486 | 0.003143 | 61.4313 | 61.9703 | 61.5791 | 63.5214 | 62.5377 | 61.9397 | 61.9295 | 64.2809 | 123.1842 | 61.8316 | 123.12 | 61.5315 | 61.5946 | 123.2086 | 61.5632 | 122.9914 | 61.5896 | 61.6209 | 61.5254 | 61.5568
4162.0625 | 123.4222 | -61.5234 | 61.5921 | 0.58427 | 0.051056 | 1.9705 | 0.75791 | 0.036265 | 0.15884 | 2.7391 | 61.6195 | 0.26695 | 61.5416 | -0.03768 | 0.048236 | 61.644 | 0.007721 | 61.4313 | 62.1077 | 61.5745 | 63.494 | 62.2813 | 61.5597 | 61.6823 | 64.2626 | 123.1429 | 61.7904 | 123.065 | 61.4858 | 61.5717 | 123.1674 | 61.5312 | 122.9548 | 61.5713 | 61.6118 | 61.4934 | 61.5339
4163.0781 | 123.4085 | -61.5509 | 61.5692 | 0.45607 | 0.051056 | 1.8698 | 0.69381 | 0.017953 | 0.27787 | 2.7254 | 61.6195 | 0.27153 | 61.5416 | -0.033101 | 0.048236 | 61.644 | 0.003143 | 61.4176 | 62.007 | 61.602 | 63.4207 | 62.2447 | 61.5689 | 61.8288 | 64.2763 | 123.1704 | 61.8224 | 123.0925 | 61.5178 | 61.5991 | 123.1949 | 61.554 | 122.9685 | 61.5713 | 61.6164 | 61.4934 | 61.5385
4164.0625 | 123.3124 | -61.5509 | 61.6379 | 0.42402 | 0.078529 | 1.8332 | 0.72128 | 0.33383 | 0.32366 | 2.7162 | 61.6241 | 0.26695 | 61.5553 | -0.028522 | 0.048236 | 61.6486 | 0.003143 | 61.4268 | 61.9749 | 61.6294 | 63.3841 | 62.2722 | 61.8847 | 61.8746 | 64.2671 | 123.175 | 61.8179 | 123.1062 | 61.5224 | 61.5991 | 123.1995 | 61.554 | 122.9777 | 61.5759 | 61.6209 | 61.5071 | 61.5522
4165.0938 | 123.3353 | -61.528 | 61.6379 | 0.38282 | -0.054257 | 1.8423 | 0.74875 | 0.34299 | 0.33739 | 2.5102 | 61.6149 | 0.27153 | 61.5324 | -0.033101 | 0.043657 | 61.6486 | 0.007721 | 61.4313 | 61.9108 | 61.4738 | 63.3703 | 62.2768 | 61.871 | 61.8654 | 64.0382 | 123.1429 | 61.7995 | 123.0605 | 61.4949 | 61.5717 | 123.1766 | 61.5357 | 122.9594 | 61.5713 | 61.6072 | 61.4888 | 61.5247
4166.0625 | 123.2986 | -61.5646 | 61.6104 | 0.78572 | 0.009846 | 1.7416 | 0.75791 | 0.082044 | -0.033455 | 2.7254 | 61.6195 | 0.27153 | 61.5324 | -0.03768 | 0.039079 | 61.6486 | 0.003143 | 61.4313 | 62.3504 | 61.5745 | 63.3062 | 62.3225 | 61.6467 | 61.5312 | 64.29 | 123.1841 | 61.8362 | 123.0971 | 61.527 | 61.6037 | 123.2132 | 61.5678 | 122.996 | 61.5804 | 61.6164 | 61.4934 | 61.5293
4167.0781 | 123.3444 | -61.5417 | 61.5784 | 0.82234 | 0.046477 | 1.5173 | 0.76706 | -0.059872 | -0.083817 | 2.7986 | 61.6287 | 0.27611 | 61.5691 | -0.042259 | 0.043657 | 61.6531 | 0.003143 | 61.4268 | 62.3641 | 61.5882 | 63.059 | 62.3088 | 61.4819 | 61.4579 | 64.3404 | 123.1704 | 61.8179 | 123.1108 | 61.4995 | 61.5854 | 123.1949 | 61.5449 | 122.9685 | 61.585 | 61.6255 | 61.5254 | 61.5659
4168.0625 | 123.3124 | -61.5097 | 61.615 | 0.73535 | 0.028162 | 1.5493 | 0.79911 | 0.14614 | -0.060926 | 3.0962 | 61.6149 | 0.26695 | 61.537 | -0.033101 | 0.039079 | 61.6486 | 0.012299 | 61.4359 | 62.2451 | 61.5379 | 63.059 | 62.3088 | 61.6558 | 61.4488 | 64.6059 | 123.1246 | 61.7767 | 123.0467 | 61.4766 | 61.5488 | 123.1583 | 61.522 | 122.9456 | 61.5759 | 61.6026 | 61.4979 | 61.5247
4169.0938 | 123.4268 | -61.4914 | 61.6013 | 0.73078 | -0.022205 | 1.5356 | 0.822 | 0.21023 | -0.19828 | 3.1008 | 61.6149 | 0.27611 | 61.5462 | -0.033101 | 0.043657 | 61.644 | 0.003143 | 61.4405 | 62.2222 | 61.4692 | 63.027 | 62.3134 | 61.7016 | 61.2931 | 64.5922 | 123.1063 | 61.7675 | 123.0376 | 61.4583 | 61.5351 | 123.1354 | 61.4945 | 122.9319 | 61.5713 | 61.6118 | 61.5025 | 61.543
4170.0625 | 123.317 | -61.5417 | 61.6653 | 0.69873 | -0.049678 | 1.5814 | 0.81743 | 0.23312 | -0.1296 | 2.7803 | 61.6332 | 0.27153 | 61.5691 | -0.033101 | 0.048236 | 61.6486 | 0.003143 | 61.4176 | 62.2405 | 61.4921 | 63.1231 | 62.3592 | 61.7749 | 61.4121 | 64.3221 | 123.175 | 61.8133 | 123.1108 | 61.5086 | 61.59 | 123.1903 | 61.5449 | 122.9593 | 61.585 | 61.6301 | 61.5208 | 61.5659
4171.0938 | 123.4543 | -61.5326 | 61.5921 | 0.30499 | -0.013048 | 1.3478 | 0.93647 | 0.23769 | 0.2504 | 2.968 | 61.6287 | 0.27153 | 61.5416 | -0.028522 | 0.043657 | 61.644 | 0.003143 | 61.4359 | 61.8376 | 61.5195 | 62.8804 | 62.4691 | 61.7703 | 61.783 | 64.5006 | 123.1613 | 61.8041 | 123.0742 | 61.5041 | 61.5763 | 123.1766 | 61.5357 | 122.9685 | 61.585 | 61.6255 | 61.4979 | 61.5385
4172.0625 | 123.349 | -61.5097 | 61.6104 | 0.31872 | -0.14583 | 1.4119 | 0.83116 | 0.2148 | 0.26872 | 2.6613 | 61.6287 | 0.27153 | 61.5462 | -0.023943 | 0.048236 | 61.6486 | 0.003143 | 61.4176 | 61.8284 | 61.3639 | 62.9217 | 62.3409 | 61.7245 | 61.7784 | 64.171 | 123.1384 | 61.7812 | 123.0559 | 61.4858 | 61.5579 | 123.1583 | 61.5128 | 122.9273 | 61.5804 | 61.6255 | 61.4979 | 61.543
4173.0625 | 123.4177 | -61.5143 | 61.5784 | 0.30499 | -0.14125 | 1.4394 | 0.73043 | 0.21023 | 0.26414 | 2.1256 | 61.6378 | 0.27153 | 61.5691 | -0.033101 | 0.048236 | 61.6348 | 0.003143 | 61.4176 | 61.8193 | 61.373 | 62.9537 | 62.2447 | 61.7245 | 61.7784 | 63.6399 | 123.1521 | 61.7858 | 123.0834 | 61.4812 | 61.5625 | 123.1491 | 61.5174 | 122.9319 | 61.5896 | 61.6347 | 61.5208 | 61.5659
4174.0781 | 123.3673 | -61.496 | 61.5967 | 0.3233 | -0.16415 | 1.4119 | 0.74875 | 0.2148 | 0.29161 | 1.8464 | 61.6287 | 0.27153 | 61.5462 | -0.03768 | 0.052814 | 61.6394 | 0.003143 | 61.4359 | 61.8193 | 61.3318 | 62.9079 | 62.2447 | 61.7108 | 61.7876 | 63.3424 | 123.1246 | 61.7675 | 123.0422 | 61.4583 | 61.5488 | 123.1354 | 61.4991 | 122.9319 | 61.5759 | 61.6255 | 61.4934 | 61.543
4175.0625 | 123.3078 | -61.5417 | 61.6516 | 0.28667 | -0.058836 | 1.1418 | 0.68923 | 0.2148 | 0.24583 | 2.2081 | 61.6332 | 0.27153 | 61.5462 | -0.03768 | 0.048236 | 61.6348 | 0.007721 | 61.4176 | 61.8284 | 61.4829 | 62.6836 | 62.231 | 61.7566 | 61.7876 | 63.7498 | 123.175 | 61.8133 | 123.0879 | 61.5041 | 61.59 | 123.1766 | 61.5495 | 122.9593 | 61.585 | 61.6255 | 61.4979 | 61.5385
4176.0938 | 123.1522 | -61.5555 | 61.5738 | 0.25005 | -0.23283 | 1.2425 | 0.65718 | 0.13698 | 0.21836 | 2.1073 | 61.6424 | 0.27153 | 61.5737 | -0.028522 | 0.043657 | 61.6303 | -0.001436 | 61.4039 | 61.8055 | 61.3227 | 62.798 | 62.2127 | 61.6925 | 61.7738 | 63.6628 | 123.1979 | 61.827 | 123.1291 | 61.527 | 61.5991 | 123.1857 | 61.554 | 122.9593 | 61.5987 | 61.6438 | 61.53 | 61.5751
4177.0625 | 123.3398 | -61.528 | 61.615 | 0.33703 | -0.031363 | 2.0758 | 0.74875 | 0.23312 | 0.30992 | 2.6155 | 61.6149 | 0.26695 | 61.5553 | -0.028522 | 0.048236 | 61.6486 | 0.007721 | 61.4222 | 61.8651 | 61.4967 | 63.6039 | 62.2768 | 61.7611 | 61.8379 | 64.1435 | 123.1429 | 61.795 | 123.0834 | 61.4995 | 61.5763 | 123.1766 | 61.5357 | 122.9502 | 61.5667 | 61.6072 | 61.5071 | 61.5476
4178.0938 | 123.3902 | -61.5509 | 61.6013 | 0.37824 | -0.072572 | 2.2498 | 0.73959 | 0.21023 | 0.33739 | 3.0504 | 61.6058 | 0.27153 | 61.5233 | -0.033101 | 0.039079 | 61.6577 | 0.007721 | 61.4313 | 61.9291 | 61.4783 | 63.8007 | 62.2905 | 61.7611 | 61.8883 | 64.6013 | 123.1567 | 61.8224 | 123.0742 | 61.5178 | 61.59 | 123.2086 | 61.5586 | 122.9822 | 61.5667 | 61.5981 | 61.4842 | 61.5156
4179.0625 | 123.2986 | -61.5738 | 61.6241 | 0.36451 | -0.067994 | 2.0163 | 0.76248 | 0.086622 | 0.33282 | 2.8948 | 61.6195 | 0.27153 | 61.537 | -0.033101 | 0.043657 | 61.6486 | 0.007721 | 61.4222 | 61.9383 | 61.5058 | 63.5901 | 62.3363 | 61.6604 | 61.9066 | 64.4686 | 123.1933 | 61.8453 | 123.1108 | 61.5407 | 61.6174 | 123.2224 | 61.5815 | 122.996 | 61.5759 | 61.6118 | 61.4934 | 61.5293
4180.0781 | 123.3078 | -61.5692 | 61.6379 | 0.30956 | -0.18704 | 2.433 | 0.69381 | -0.036983 | 0.2733 | 2.2859 | 61.6287 | 0.26695 | 61.5691 | -0.028522 | 0.043657 | 61.644 | 0.007721 | 61.4222 | 61.8788 | 61.3822 | 64.0022 | 62.263 | 61.5322 | 61.8425 | 63.8551 | 123.1979 | 61.8362 | 123.1383 | 61.5407 | 61.6129 | 123.2132 | 61.5769 | 122.9914 | 61.585 | 61.6209 | 61.5254 | 61.5614
4181.0625 | 123.4131 | -61.5372 | 61.5509 | 0.3233 | -0.19162 | 2.6253 | 0.68923 | -0.069028 | 0.28703 | 2.6476 | 61.6241 | 0.27153 | 61.5599 | -0.033101 | 0.039079 | 61.6486 | 0.003143 | 61.4222 | 61.8605 | 61.3455 | 64.1624 | 62.2264 | 61.4681 | 61.8242 | 64.1847 | 123.1613 | 61.8087 | 123.0971 | 61.5041 | 61.5762 | 123.1857 | 61.5403 | 122.9593 | 61.585 | 61.6209 | 61.5208 | 61.5568
4182.0781 | 123.3765 | -61.5234 | 61.5967 | 0.26378 | -0.16415 | 2.6711 | 0.78538 | -0.06445 | 0.22293 | 2.6476 | 61.6241 | 0.26695 | 61.537 | -0.028522 | 0.048236 | 61.6486 | 0.007721 | 61.4222 | 61.7872 | 61.3593 | 64.1945 | 62.3088 | 61.459 | 61.7464 | 64.171 | 123.1475 | 61.7904 | 123.0605 | 61.4949 | 61.5717 | 123.172 | 61.5312 | 122.9456 | 61.5759 | 61.6164 | 61.4888 | 61.5293
4183.0625 | 123.4131 | -61.5005 | 61.5967 | 0.20426 | -0.19162 | 2.7306 | 0.5885 | -0.12396 | 0.15884 | 2.1165 | 61.6287 | 0.27611 | 61.5324 | -0.03768 | 0.048236 | 61.6394 | -0.001436 | 61.4176 | 61.7048 | 61.3089 | 64.2311 | 62.0891 | 61.3766 | 61.6594 | 63.617 | 123.1292 | 61.7767 | 123.033 | 61.4629 | 61.5488 | 123.14 | 61.4991 | 122.9181 | 61.5804 | 61.6301 | 61.4842 | 61.5339
4184.0938 | 123.2895 | -61.5417 | 61.6516 | 0.22715 | -0.22367 | 2.7077 | 0.63429 | 0.017953 | 0.18631 | 1.8922 | 61.6332 | 0.26695 | 61.5645 | -0.03768 | 0.052814 | 61.6394 | 0.007721 | 61.4268 | 61.7689 | 61.3181 | 64.2494 | 62.176 | 61.5597 | 61.7281 | 63.4339 | 123.175 | 61.8087 | 123.1062 | 61.5041 | 61.5946 | 123.1812 | 61.5495 | 122.9685 | 61.5804 | 61.6255 | 61.5117 | 61.5568
4185.0625 | 123.2529 | -61.5509 | 61.6013 | 0.29125 | -0.090888 | 2.639 | 0.66634 | 0.031687 | 0.25498 | 1.9563 | 61.6241 | 0.26695 | 61.5645 | -0.03768 | 0.043657 | 61.6394 | 0.003143 | 61.4176 | 61.8422 | 61.46 | 64.1899 | 62.2172 | 61.5826 | 61.8059 | 63.5072 | 123.175 | 61.8179 | 123.1154 | 61.5132 | 61.5946 | 123.1903 | 61.554 | 122.9685 | 61.5804 | 61.6209 | 61.5208 | 61.5614
4186.1094 | 123.3215 | -61.5326 | 61.6379 | 0.34619 | -0.026784 | 2.6207 | 0.73959 | 0.077466 | 0.30535 | 2.6338 | 61.6149 | 0.27153 | 61.5416 | -0.028522 | 0.043657 | 61.644 | 0.003143 | 61.4313 | 61.8788 | 61.5058 | 64.1533 | 62.2722 | 61.6101 | 61.8379 | 64.1664 | 123.1475 | 61.8041 | 123.0742 | 61.5041 | 61.5763 | 123.1766 | 61.5357 | 122.9639 | 61.5713 | 61.6118 | 61.4979 | 61.5385
4187.0625 | 123.2712 | -61.5738 | 61.6104 | 0.26836 | -0.00389 | 2.5062 | 0.77164 | 0.008797 | 0.23667 | 2.7712 | 61.6149 | 0.27153 | 61.5233 | -0.03768 | 0.048236 | 61.6486 | 0.007721 | 61.4222 | 61.8422 | 61.5699 | 64.08 | 62.3454 | 61.5826 | 61.8105 | 64.345 | 123.1887 | 61.8453 | 123.0971 | 61.5361 | 61.622 | 123.2224 | 61.5815 | 122.996 | 61.5667 | 61.6072 | 61.4751 | 61.5156
4188.0938 | 123.2849 | -61.5463 | 61.5921 | 0.28209 | -0.0451 | 2.4879 | 0.76248 | -0.004937 | 0.24583 | 2.7391 | 61.6241 | 0.26695 | 61.5599 | -0.028522 | 0.048236 | 61.6486 | 0.003143 | 61.4405 | 61.8284 | 61.5012 | 64.0342 | 62.3088 | 61.5414 | 61.7922 | 64.2855 | 123.1704 | 61.8133 | 123.1062 | 61.5178 | 61.5946 | 123.1949 | 61.5495 | 122.9868 | 61.5759 | 61.6209 | 61.5117 | 61.5568
4189.0625 | 123.3078 | -61.5417 | 61.6013 | 0.2592 | -0.18704 | 2.8267 | 0.74875 | -0.032405 | 0.21836 | 2.5423 | 61.6241 | 0.27153 | 61.5645 | -0.033101 | 0.043657 | 61.644 | 0.003143 | 61.4359 | 61.801 | 61.3547 | 64.3685 | 62.2905 | 61.5093 | 61.7601 | 64.084 | 123.1658 | 61.8133 | 123.1062 | 61.5086 | 61.5854 | 123.1857 | 61.5449 | 122.9777 | 61.5804 | 61.6209 | 61.5208 | 61.5614
4190.0781 | 123.3444 | -61.5509 | 61.6333 | 0.25462 | -0.49382 | 2.9412 | 0.67549 | -0.10107 | 0.20462 | 1.9883 | 61.6287 | 0.26695 | 61.5324 | -0.028522 | 0.039079 | 61.6394 | 0.003143 | 61.4222 | 61.8055 | 61.0571 | 64.4921 | 62.2264 | 61.4498 | 61.7555 | 63.5392 | 123.1796 | 61.8179 | 123.0834 | 61.5224 | 61.59 | 123.1903 | 61.554 | 122.9731 | 61.5896 | 61.6255 | 61.4934 | 61.5293
4191.0625 | 123.3994 | -61.5234 | 61.5646 | 0.28209 | -0.55793 | 2.8863 | 0.67091 | -0.11023 | 0.24583 | 1.8372 | 61.6378 | 0.26695 | 61.5691 | -0.033101 | 0.048236 | 61.6394 | 0.003143 | 61.4176 | 61.8055 | 60.9655 | 64.4097 | 62.1944 | 61.4132 | 61.7693 | 63.3607 | 123.1613 | 61.7904 | 123.0925 | 61.4903 | 61.5717 | 123.1628 | 61.5266 | 122.941 | 61.5896 | 61.6347 | 61.5208 | 61.5659
4192.0781 | 123.2803 | -61.528 | 61.6287 | 0.34619 | -0.6495 | 2.726 | 0.6526 | -0.036983 | 0.3145 | 1.9196 | 61.6378 | 0.27153 | 61.5691 | -0.028522 | 0.043657 | 61.6394 | 0.007721 | 61.4359 | 61.8742 | 60.8785 | 64.254 | 62.1806 | 61.491 | 61.8425 | 63.4476 | 123.1658 | 61.7995 | 123.0971 | 61.4995 | 61.5717 | 123.1674 | 61.5357 | 122.9639 | 61.5942 | 61.6301 | 61.5254 | 61.5614
4193.0625 | 123.2986 | -61.528 | 61.6287 | 0.30499 | -0.59914 | 2.726 | 0.60681 | -0.12396 | 0.26414 | 1.5396 | 61.6287 | 0.27153 | 61.537 | -0.03768 | 0.043657 | 61.6348 | 0.007721 | 61.4268 | 61.833 | 60.9289 | 64.254 | 62.1348 | 61.4041 | 61.7922 | 63.0677 | 123.1567 | 61.7995 | 123.065 | 61.4903 | 61.5717 | 123.1628 | 61.5357 | 122.9548 | 61.585 | 61.6209 | 61.4934 | 61.5293
4194.0938 | 123.2941 | -61.5097 | 61.6379 | 0.3233 | -0.78229 | 2.8542 | 0.56561 | -0.19721 | 0.2733 | 1.0956 | 61.6332 | 0.26695 | 61.5691 | -0.03768 | 0.043657 | 61.6257 | 0.007721 | 61.4222 | 61.833 | 60.7274 | 64.3639 | 62.0753 | 61.3125 | 61.783 | 62.6053 | 123.143 | 61.7767 | 123.0788 | 61.472 | 61.5534 | 123.1354 | 61.5174 | 122.9319 | 61.5896 | 61.6255 | 61.5254 | 61.5614
4195.0625 | 123.349 | -61.5143 | 61.6241 | 0.33703 | -0.87387 | 2.8496 | 0.51067 | -0.18805 | 0.29161 | 1.7823 | 61.6378 | 0.26237 | 61.5828 | -0.028522 | 0.043657 | 61.6303 | 0.007721 | 61.4222 | 61.8513 | 60.6404 | 64.3639 | 62.0249 | 61.3262 | 61.8059 | 63.2966 | 123.1521 | 61.7767 | 123.0971 | 61.4858 | 61.5579 | 123.1445 | 61.522 | 122.9365 | 61.5942 | 61.6301 | 61.5392 | 61.5751
4196.1094 | 123.349 | -61.5189 | 61.6608 | 0.31872 | -0.95628 | 2.7947 | 0.48778 | -0.23841 | 0.28245 | 2.2584 | 61.6332 | 0.27611 | 61.5691 | -0.033101 | 0.052814 | 61.6394 | 0.007721 | 61.4268 | 61.8376 | 60.5626 | 64.3135 | 62.0066 | 61.2804 | 61.8013 | 63.7773 | 123.1521 | 61.795 | 123.0879 | 61.4858 | 61.5717 | 123.1583 | 61.5266 | 122.9456 | 61.5804 | 61.6255 | 61.5163 | 61.5614
4197.0625 | 123.3307 | -61.5234 | 61.6241 | 0.24547 | -0.99749 | 2.6665 | 0.44657 | -0.25215 | 0.20004 | 2.2905 | 61.6332 | 0.26237 | 61.5508 | -0.028522 | 0.048236 | 61.6303 | 0.007721 | 61.4268 | 61.7689 | 60.5259 | 64.1899 | 61.97 | 61.2713 | 61.7235 | 63.8139 | 123.1567 | 61.7858 | 123.0742 | 61.4949 | 61.5717 | 123.1537 | 61.5312 | 122.9502 | 61.585 | 61.6255 | 61.5025 | 61.543
4198.0781 | 123.5184 | -61.4548 | 61.6837 | 0.28209 | -0.89676 | 2.6161 | 0.44199 | -0.30708 | 0.24583 | 2.6109 | 61.6287 | 0.27153 | 61.5599 | -0.033101 | 0.043657 | 61.6348 | 0.003143 | 61.4222 | 61.7369 | 60.558 | 64.0709 | 61.8968 | 61.1477 | 61.7006 | 64.0657 | 123.0834 | 61.7263 | 123.0147 | 61.4217 | 61.4984 | 123.0896 | 61.4579 | 122.877 | 61.585 | 61.6255 | 61.5163 | 61.5568
4199.0625 | 123.3032 | -61.5051 | 61.6241 | 0.2592 | -1.144 | 2.6299 | 0.46488 | -0.37575 | 0.20462 | 2.524 | 61.6424 | 0.26695 | 61.5828 | -0.028522 | 0.043657 | 61.6303 | 0.007721 | 61.413 | 61.7643 | 60.3611 | 64.135 | 61.97 | 61.1294 | 61.7097 | 64.0291 | 123.1475 | 61.7721 | 123.0879 | 61.4766 | 61.5488 | 123.1354 | 61.5128 | 122.9181 | 61.5987 | 61.6347 | 61.5392 | 61.5751
4200.0781 | 123.3078 | -61.496 | 61.5738 | 0.26836 | -1.0891 | 2.5291 | 0.54729 | -0.37575 | 0.20004 | 2.4919 | 61.6378 | 0.27153 | 61.5645 | -0.033101 | 0.048236 | 61.6394 | -0.001436 | 61.4176 | 61.7643 | 60.4069 | 64.0251 | 62.0433 | 61.1202 | 61.696 | 63.9879 | 123.1338 | 61.7675 | 123.0605 | 61.4629 | 61.5442 | 123.1354 | 61.4945 | 122.9136 | 61.5896 | 61.6393 | 61.5163 | 61.5659
4201.0625 | 123.3353 | -61.5051 | 61.6196 | 0.218 | -1.0753 | 2.3185 | 0.51982 | -0.3025 | 0.18173 | 2.4965 | 61.6332 | 0.27153 | 61.5462 | -0.033101 | 0.048236 | 61.6348 | 0.007721 | 61.4176 | 61.7231 | 60.4298 | 63.8236 | 62.025 | 61.2026 | 61.6869 | 64.0016 | 123.1384 | 61.7767 | 123.0513 | 61.472 | 61.5534 | 123.14 | 61.5128 | 122.9227 | 61.585 | 61.6255 | 61.4979 | 61.5385
4202.0781 | 123.349 | -61.4868 | 61.6287 | 0.30041 | -1.0753 | 2.0346 | 0.45115 | -0.27504 | 0.25956 | 2.5743 | 61.6241 | 0.26695 | 61.5691 | -0.033101 | 0.039079 | 61.6348 | -0.001436 | 61.413 | 61.7872 | 60.4115 | 63.5215 | 61.938 | 61.2118 | 61.7464 | 64.0611 | 123.1109 | 61.7538 | 123.0559 | 61.4537 | 61.5259 | 123.1216 | 61.4854 | 122.8998 | 61.585 | 61.6255 | 61.53 | 61.5705
4203.0625 | 123.2941 | -61.5234 | 61.6699 | 0.34619 | -1.0982 | 2.5886 | 0.36873 | -0.32539 | 0.31908 | 2.4553 | 61.6424 | 0.27153 | 61.5782 | -0.03768 | 0.043657 | 61.6303 | -0.006014 | 61.4176 | 61.8696 | 60.4252 | 64.1121 | 61.8922 | 61.198 | 61.8425 | 63.9787 | 123.1658 | 61.795 | 123.1017 | 61.4858 | 61.5671 | 123.1537 | 61.5174 | 122.941 | 61.5987 | 61.6484 | 61.5346 | 61.5842
4204.0781 | 123.4268 | -61.5005 | 61.6058 | 0.34619 | -1.1394 | 2.5429 | 0.35958 | -0.29793 | 0.30992 | 2.6155 | 61.6287 | 0.26695 | 61.5599 | -0.028522 | 0.048236 | 61.6394 | 0.003143 | 61.4222 | 61.8467 | 60.3611 | 64.0434 | 61.8601 | 61.2026 | 61.8105 | 64.1161 | 123.1292 | 61.7675 | 123.0605 | 61.472 | 61.5488 | 123.14 | 61.5037 | 122.9227 | 61.5804 | 61.6255 | 61.5117 | 61.5568
4205.0625 | 123.2986 | -61.5326 | 61.6562 | 0.41029 | -1.0753 | 2.3048 | 0.47404 | -0.23841 | 0.36486 | 2.5102 | 61.6287 | 0.26695 | 61.537 | -0.033101 | 0.039079 | 61.6348 | 0.003143 | 61.4268 | 61.9429 | 60.4573 | 63.8374 | 62.0066 | 61.2942 | 61.8975 | 64.0428 | 123.1613 | 61.7995 | 123.0696 | 61.4995 | 61.5717 | 123.1674 | 61.5357 | 122.9594 | 61.5896 | 61.6255 | 61.4979 | 61.5339
4206.0938 | 123.3719 | -61.5051 | 61.6379 | 0.28209 | -1.0616 | 1.5676 | 0.42825 | -0.32997 | 0.24125 | 2.2126 | 61.6378 | 0.27611 | 61.5828 | -0.03768 | 0.048236 | 61.6211 | -0.001436 | 61.4039 | 61.7872 | 60.4435 | 63.0727 | 61.9334 | 61.1752 | 61.7464 | 63.7178 | 123.143 | 61.7812 | 123.0879 | 61.4674 | 61.5534 | 123.1262 | 61.5037 | 122.909 | 61.5896 | 61.6393 | 61.5346 | 61.5842
4207.0625 | 123.2666 | -61.5234 | 61.6287 | 0.24089 | -0.9746 | 1.737 | 0.65718 | -0.3666 | 0.2092 | 1.7777 | 61.6516 | 0.27611 | 61.592 | -0.028522 | 0.043657 | 61.6211 | 0.003143 | 61.3993 | 61.7643 | 60.5488 | 63.2605 | 62.1806 | 61.1568 | 61.7326 | 63.3011 | 123.175 | 61.7995 | 123.1154 | 61.4949 | 61.5671 | 123.1445 | 61.5266 | 122.9227 | 61.6079 | 61.6484 | 61.5483 | 61.5888
4208.0938 | 123.4634 | -61.4685 | 61.6287 | 0.30499 | -0.97002 | 1.5401 | 0.68923 | -0.32539 | 0.26414 | 1.7777 | 61.647 | 0.26695 | 61.5828 | -0.03768 | 0.039079 | 61.6257 | 0.007721 | 61.4084 | 61.7735 | 60.4985 | 63.0087 | 62.1577 | 61.1431 | 61.7326 | 63.2462 | 123.1155 | 61.7355 | 123.0513 | 61.4308 | 61.5076 | 123.0942 | 61.4762 | 122.8769 | 61.6079 | 61.6393 | 61.5437 | 61.5751
4209.0625 | 123.3261 | -61.5097 | 61.6516 | 0.33703 | -0.9746 | 1.8927 | 0.6526 | -0.34371 | 0.30992 | 1.677 | 61.647 | 0.26695 | 61.5462 | -0.033101 | 0.043657 | 61.6211 | 0.007721 | 61.4039 | 61.8467 | 60.5351 | 63.4024 | 62.1623 | 61.166 | 61.8196 | 63.1867 | 123.1567 | 61.7767 | 123.0559 | 61.4766 | 61.5534 | 123.1308 | 61.5174 | 122.9136 | 61.6033 | 61.6393 | 61.5025 | 61.5385
4210.0781 | 123.3673 | -61.5234 | 61.6379 | 0.35535 | -0.87387 | 1.3982 | 0.68465 | -0.3666 | 0.30535 | 1.7686 | 61.6424 | 0.26695 | 61.5737 | -0.03768 | 0.043657 | 61.6211 | 0.003143 | 61.3947 | 61.8788 | 60.6496 | 62.9216 | 62.2081 | 61.1568 | 61.8288 | 63.292 | 123.1658 | 61.7904 | 123.0971 | 61.4858 | 61.5671 | 123.1445 | 61.5266 | 122.9181 | 61.5987 | 61.6393 | 61.53 | 61.5705
4211.0625 | 123.3261 | -61.5051 | 61.647 | 0.30499 | -0.98834 | 1.7965 | 0.68465 | -0.32539 | 0.25956 | 1.5992 | 61.6607 | 0.26237 | 61.592 | -0.033101 | 0.034501 | 61.6211 | 0.007721 | 61.4039 | 61.8101 | 60.5168 | 63.3017 | 62.1898 | 61.1797 | 61.7647 | 63.1043 | 123.1658 | 61.7675 | 123.0971 | 61.472 | 61.5396 | 123.1262 | 61.5128 | 122.909 | 61.6262 | 61.653 | 61.5575 | 61.5842
4212.0938 | 123.3994 | -61.4868 | 61.6287 | 0.17679 | -1.1669 | 1.8652 | 0.38247 | -0.38033 | 0.14052 | 1.6037 | 61.6561 | 0.26695 | 61.5874 | -0.033101 | 0.043657 | 61.6119 | 0.003143 | 61.3947 | 61.6636 | 60.3199 | 63.352 | 61.8693 | 61.1065 | 61.6273 | 63.0906 | 123.143 | 61.7538 | 123.0742 | 61.4537 | 61.5305 | 123.0988 | 61.49 | 122.8815 | 61.6125 | 61.653 | 61.5437 | 61.5842
4213.0625 | 123.2803 | -61.5097 | 61.6791 | 0.16306 | -1.1806 | 1.9705 | 0.50151 | -0.45358 | 0.12221 | 1.7411 | 61.6516 | 0.26695 | 61.5599 | -0.028522 | 0.052814 | 61.6211 | 0.003143 | 61.4084 | 61.6728 | 60.3291 | 63.4802 | 62.0112 | 61.0561 | 61.6319 | 63.2508 | 123.1613 | 61.7767 | 123.0696 | 61.4812 | 61.5625 | 123.1308 | 61.5128 | 122.9181 | 61.5987 | 61.6484 | 61.5071 | 61.5568
4214.0781 | 123.3627 | -61.496 | 61.6058 | 0.20426 | -1.4371 | 2.52 | 0.56561 | -0.44442 | 0.16799 | 1.8967 | 61.647 | 0.26695 | 61.5691 | -0.03768 | 0.048236 | 61.6211 | 0.012299 | 61.4039 | 61.7002 | 60.0589 | 64.0159 | 62.0616 | 61.0516 | 61.664 | 63.3927 | 123.143 | 61.7629 | 123.065 | 61.4583 | 61.5442 | 123.1171 | 61.5083 | 122.8998 | 61.5987 | 61.6347 | 61.5208 | 61.5568
4215.0625 | 123.2849 | -61.5372 | 61.6653 | 0.18595 | -1.3592 | 1.998 | 0.62971 | -0.45815 | 0.1451 | 2.0799 | 61.6561 | 0.27153 | 61.5965 | -0.028522 | 0.043657 | 61.6211 | 0.003143 | 61.3993 | 61.7231 | 60.178 | 63.5352 | 62.1669 | 61.079 | 61.6823 | 63.617 | 123.1933 | 61.8087 | 123.1337 | 61.5086 | 61.5808 | 123.1583 | 61.5403 | 122.9365 | 61.6125 | 61.653 | 61.5529 | 61.5934
4216.0625 | 123.2941 | -61.5051 | 61.6333 | 0.16306 | -1.4462 | 1.9064 | 0.56561 | -0.50393 | 0.11305 | 2.1119 | 61.6561 | 0.27153 | 61.6011 | -0.028522 | 0.043657 | 61.6165 | 0.003143 | 61.3993 | 61.6682 | 60.0589 | 63.4116 | 62.0707 | 61.0012 | 61.6182 | 63.617 | 123.1613 | 61.7767 | 123.1063 | 61.4766 | 61.5488 | 123.1216 | 61.5083 | 122.9044 | 61.6125 | 61.653 | 61.5575 | 61.598
4217.0781 | 123.4177 | -61.5005 | 61.6241 | 0.10354 | -1.4508 | 2.4467 | 0.56103 | -0.52682 | 0.058113 | 2.0616 | 61.647 | 0.26695 | 61.5553 | -0.028522 | 0.039079 | 61.6211 | 0.007721 | 61.3947 | 61.6041 | 60.0498 | 63.9473 | 62.0616 | 60.9737 | 61.5587 | 63.5621 | 123.1475 | 61.7675 | 123.0559 | 61.472 | 61.5396 | 123.1216 | 61.5083 | 122.8953 | 61.6079 | 61.6393 | 61.5163 | 61.5476
4218.0625 | 123.2574 | -61.5005 | 61.6699 | 0.089802 | -1.5378 | 2.2132 | 0.45572 | -0.50393 | 0.048956 | 2.0936 | 61.6516 | 0.26237 | 61.5645 | -0.028522 | 0.052814 | 61.6211 | -0.001436 | 61.4039 | 61.5904 | 59.9628 | 63.7137 | 61.9563 | 60.9966 | 61.5495 | 63.5942 | 123.1521 | 61.7629 | 123.065 | 61.472 | 61.5534 | 123.1216 | 61.4991 | 122.9044 | 61.5987 | 61.653 | 61.5117 | 61.5659
4219.0938 | 123.381 | -61.4731 | 61.6333 | 0.13101 | -1.3684 | 2.3963 | 0.41452 | -0.41695 | 0.090161 | 2.0066 | 61.6561 | 0.27153 | 61.592 | -0.028522 | 0.048236 | 61.6165 | 0.016878 | 61.3993 | 61.6041 | 60.1047 | 63.8694 | 61.8876 | 61.0561 | 61.5632 | 63.4797 | 123.1292 | 61.7446 | 123.065 | 61.4446 | 61.5213 | 123.0896 | 61.49 | 122.8724 | 61.6079 | 61.6393 | 61.5437 | 61.5751
4220.0625 | 123.3353 | -61.4868 | 61.6699 | 0.16306 | -1.3867 | 2.0117 | 0.37331 | -0.38033 | 0.12221 | 1.7869 | 61.6607 | 0.26695 | 61.6011 | -0.033101 | 0.048236 | 61.6119 | 0.003143 | 61.4039 | 61.6499 | 60.1001 | 63.4986 | 61.8601 | 61.1065 | 61.609 | 63.2737 | 123.1475 | 61.7538 | 123.0879 | 61.4537 | 61.5351 | 123.0988 | 61.49 | 122.8907 | 61.6125 | 61.6576 | 61.5529 | 61.598
4221.0938 | 123.4634 | -61.4777 | 61.6058 | 0.17221 | -1.3226 | 2.3368 | 0.27259 | -0.41695 | 0.13595 | 1.7731 | 61.647 | 0.26695 | 61.5737 | -0.033101 | 0.043657 | 61.6211 | 0.007721 | 61.4039 | 61.6499 | 60.1551 | 63.8145 | 61.7502 | 61.0607 | 61.6136 | 63.2508 | 123.1246 | 61.7446 | 123.0513 | 61.4446 | 61.5213 | 123.0988 | 61.4854 | 122.8815 | 61.6033 | 61.6393 | 61.53 | 61.5659
4222.0625 | 123.2941 | -61.5097 | 61.6882 | 0.15848 | -1.4737 | 2.5291 | 0.35042 | -0.46731 | 0.11763 | 1.6861 | 61.6516 | 0.27153 | 61.5599 | -0.033101 | 0.048236 | 61.6165 | 0.012299 | 61.3993 | 61.6682 | 60.036 | 64.0388 | 61.8601 | 61.0424 | 61.6273 | 63.1959 | 123.1613 | 61.7812 | 123.0696 | 61.4766 | 61.5579 | 123.1262 | 61.522 | 122.909 | 61.6033 | 61.6393 | 61.5117 | 61.5476
4223.0781 | 123.4222 | -61.4822 | 61.6287 | 0.17679 | -1.4645 | 2.6894 | 0.29548 | -0.54514 | 0.14052 | 1.2741 | 61.6424 | 0.27153 | 61.592 | -0.028522 | 0.043657 | 61.6211 | 0.007721 | 61.3947 | 61.659 | 60.0177 | 64.1716 | 61.7777 | 60.9371 | 61.6228 | 62.7563 | 123.1246 | 61.7538 | 123.0742 | 61.4537 | 61.5259 | 123.1033 | 61.49 | 122.8769 | 61.5987 | 61.6347 | 61.5483 | 61.5842
4224.0625 | 123.3627 | -61.4731 | 61.6882 | 0.089802 | -1.3592 | 2.7031 | 0.30006 | -0.61838 | 0.058113 | 1.5351 | 61.6607 | 0.26237 | 61.5965 | -0.03768 | 0.048236 | 61.6165 | 0.003143 | 61.4084 | 61.5629 | 60.1139 | 64.1762 | 61.7731 | 60.8547 | 61.5312 | 63.0081 | 123.1338 | 61.7355 | 123.0696 | 61.4354 | 61.5213 | 123.0896 | 61.4762 | 122.8815 | 61.6125 | 61.6576 | 61.5483 | 61.5934
4225.0781 | 123.3673 | -61.5005 | 61.6058 | 0.071489 | -1.405 | 2.7123 | 0.30463 | -0.60007 | 0.030642 | 1.7228 | 61.647 | 0.26237 | 61.5782 | -0.028522 | 0.039079 | 61.6211 | 0.003143 | 61.3993 | 61.572 | 60.0955 | 64.2128 | 61.8052 | 60.9005 | 61.5312 | 63.2233 | 123.1475 | 61.7629 | 123.0788 | 61.472 | 61.5396 | 123.1216 | 61.5037 | 122.8998 | 61.6079 | 61.6438 | 61.5392 | 61.5751
4226.0625 | 123.2758 | -61.5234 | 61.647 | 0.03944 | -1.4966 | 2.6207 | 0.30006 | -0.58176 | 0.003172 | 1.764 | 61.6561 | 0.27153 | 61.5737 | -0.033101 | 0.039079 | 61.6165 | 0.003143 | 61.3947 | 61.5629 | 60.0269 | 64.1441 | 61.8235 | 60.9417 | 61.5266 | 63.2874 | 123.1796 | 61.795 | 123.0971 | 61.4903 | 61.5625 | 123.14 | 61.5266 | 122.9181 | 61.6171 | 61.653 | 61.5346 | 61.5705
4227.0781 | 123.3994 | -61.4639 | 61.6196 | -0.029236 | -1.5149 | 2.5017 | 0.35042 | -0.51309 | -0.04719 | 1.2695 | 61.6607 | 0.26695 | 61.5737 | -0.03768 | 0.039079 | 61.6165 | 0.003143 | 61.3993 | 61.4347 | 59.949 | 63.9656 | 61.8143 | 60.9508 | 61.4167 | 62.7335 | 123.1246 | 61.7309 | 123.0376 | 61.4262 | 61.503 | 123.0804 | 61.4671 | 122.8632 | 61.6216 | 61.6576 | 61.5346 | 61.5705
4228.0625 | 123.3444 | -61.4594 | 61.6608 | 0.053175 | -1.4737 | 2.4696 | 0.35958 | -0.51309 | 0.003172 | 1.3245 | 61.6653 | 0.26695 | 61.5965 | -0.03768 | 0.057392 | 61.6074 | 0.012299 | 61.3947 | 61.5125 | 59.9857 | 63.929 | 61.8189 | 60.9463 | 61.4625 | 62.7838 | 123.1246 | 61.7263 | 123.0559 | 61.4217 | 61.5167 | 123.0667 | 61.4716 | 122.8541 | 61.6079 | 61.653 | 61.5392 | 61.5842
4229.0938 | 123.4131 | -61.4502 | 61.6699 | 0.11269 | -1.5332 | 2.0301 | 0.25885 | -0.51767 | 0.044377 | 0.55076 | 61.6653 | 0.26695 | 61.6149 | -0.03768 | 0.052814 | 61.5982 | 0.003143 | 61.3993 | 61.5629 | 59.917 | 63.4803 | 61.709 | 60.9325 | 61.4946 | 62.001 | 123.1155 | 61.7171 | 123.0651 | 61.4125 | 61.503 | 123.0484 | 61.4533 | 122.8495 | 61.6125 | 61.6622 | 61.562 | 61.6117
4230.0625 | 123.3353 | -61.496 | 61.6745 | 0.062332 | -1.6202 | 2.3048 | 0.34126 | -0.61838 | 0.021485 | 0.5004 | 61.6653 | 0.27153 | 61.5828 | -0.033101 | 0.043657 | 61.6074 | 0.003143 | 61.3993 | 61.5583 | 59.8758 | 63.8007 | 61.8372 | 60.8776 | 61.5175 | 61.9964 | 123.1613 | 61.7675 | 123.0788 | 61.4629 | 61.5396 | 123.1033 | 61.4991 | 122.8953 | 61.6216 | 61.6622 | 61.5392 | 61.5797
4231.1094 | 123.3353 | -61.4777 | 61.6516 | 0.13101 | -1.5653 | 2.4879 | 0.23138 | -0.62754 | 0.076426 | 0.66063 | 61.6653 | 0.25779 | 61.5691 | -0.033101 | 0.048236 | 61.6119 | -0.001436 | 61.3901 | 61.6087 | 59.9124 | 63.9656 | 61.709 | 60.8501 | 61.5541 | 62.1383 | 123.143 | 61.7355 | 123.0467 | 61.4446 | 61.5259 | 123.0896 | 61.4762 | 122.8678 | 61.6171 | 61.6667 | 61.5208 | 61.5705
4232.0625 | 123.3078 | -61.4868 | 61.6608 | 0.10354 | -1.6111 | 2.5291 | 0.14439 | -0.65043 | 0.067269 | 0.66521 | 61.679 | 0.27153 | 61.6057 | -0.03768 | 0.048236 | 61.5982 | 0.012299 | 61.3901 | 61.5904 | 59.8758 | 64.0159 | 61.6312 | 60.8364 | 61.5541 | 62.152 | 123.1658 | 61.7583 | 123.0925 | 61.4491 | 61.5351 | 123.085 | 61.4991 | 122.8769 | 61.6308 | 61.6667 | 61.5575 | 61.5934
4233.0781 | 123.3124 | -61.496 | 61.6928 | 0.10812 | -1.6935 | 2.7397 | 0.13065 | -0.75114 | 0.067269 | 0.71557 | 61.6745 | 0.26695 | 61.5965 | -0.028522 | 0.043657 | 61.6028 | 0.012299 | 61.3947 | 61.6041 | 59.8025 | 64.2357 | 61.6266 | 60.7448 | 61.5632 | 62.2115 | 123.1704 | 61.7629 | 123.0925 | 61.4674 | 61.5396 | 123.0988 | 61.5083 | 122.8907 | 61.6308 | 61.6622 | 61.5529 | 61.5842
4234.0625 | 123.3536 | -61.5097 | 61.6745 | 0.15848 | -1.8034 | 2.7306 | 0.07571 | -0.89764 | 0.10848 | 0.73846 | 61.6653 | 0.26695 | 61.5965 | -0.03768 | 0.048236 | 61.6028 | 0.007721 | 61.381 | 61.6682 | 59.7063 | 64.2403 | 61.5854 | 60.6121 | 61.6182 | 62.2482 | 123.175 | 61.7767 | 123.1062 | 61.472 | 61.5579 | 123.1125 | 61.5174 | 122.8907 | 61.6171 | 61.6576 | 61.5483 | 61.5888
4235.0625 | 123.3398 | -61.4777 | 61.6745 | 0.17221 | -1.7438 | 2.7535 | 0.12607 | -0.88848 | 0.1451 | 0.52329 | 61.6653 | 0.26695 | 61.5782 | -0.023943 | 0.052814 | 61.6074 | 0.012299 | 61.3856 | 61.6499 | 59.7338 | 64.2311 | 61.6037 | 60.5892 | 61.6228 | 62.0009 | 123.143 | 61.7446 | 123.0559 | 61.4537 | 61.5305 | 123.085 | 61.49 | 122.8632 | 61.6125 | 61.653 | 61.5254 | 61.5659
4236.1094 | 123.3032 | -61.4731 | 61.6653 | 0.11727 | -1.6248 | 2.3506 | -0.28141 | -0.87475 | 0.076426 | 0.49124 | 61.679 | 0.27153 | 61.5965 | -0.033101 | 0.048236 | 61.5982 | -0.001436 | 61.3672 | 61.5904 | 59.8483 | 63.8236 | 61.1917 | 60.5983 | 61.5495 | 61.9643 | 123.1521 | 61.7446 | 123.0696 | 61.44 | 61.5213 | 123.0713 | 61.4716 | 122.8403 | 61.6308 | 61.6805 | 61.5483 | 61.598
4237.0625 | 123.3032 | -61.4731 | 61.6745 | 0.048597 | -1.7713 | 1.9843 | -0.38672 | -0.94342 | 0.021485 | 0.38594 | 61.6836 | 0.26695 | 61.624 | -0.033101 | 0.048236 | 61.5891 | 0.007721 | 61.3718 | 61.5217 | 59.7018 | 63.4574 | 61.0864 | 60.5297 | 61.4946 | 61.859 | 123.1567 | 61.74 | 123.0971 | 61.44 | 61.5213 | 123.0621 | 61.4808 | 122.8449 | 61.6354 | 61.6759 | 61.5758 | 61.6163
4238.0781 | 123.3261 | -61.4914 | 61.6516 | 0.080646 | -1.8263 | 1.7828 | 0.039082 | -0.75572 | 0.035221 | 0.39968 | 61.6882 | 0.26695 | 61.6194 | -0.03768 | 0.052814 | 61.5891 | 0.003143 | 61.3764 | 61.572 | 59.6651 | 63.2742 | 61.5305 | 60.7357 | 61.5266 | 61.8911 | 123.1796 | 61.7583 | 123.1108 | 61.4537 | 61.5442 | 123.0804 | 61.4945 | 122.8678 | 61.6354 | 61.685 | 61.5666 | 61.6163
4239.0625 | 123.2529 | -61.5005 | 61.647 | 0.03944 | -1.9087 | 2.0255 | 0.13981 | -0.73741 | 0.012329 | 0.67437 | 61.679 | 0.26695 | 61.5828 | -0.03768 | 0.048236 | 61.5982 | 0.003143 | 61.3901 | 61.54 | 59.5919 | 63.526 | 61.6404 | 60.7631 | 61.5129 | 62.1749 | 123.1796 | 61.7675 | 123.0834 | 61.4629 | 61.5488 | 123.0988 | 61.5037 | 122.8907 | 61.6308 | 61.6759 | 61.5346 | 61.5797
4240.0625 | 123.3215 | -61.5143 | 61.6653 | 0.021127 | -1.9041 | 2.0713 | 0.15812 | -0.72368 | -0.015142 | 0.78424 | 61.6745 | 0.26695 | 61.5828 | -0.03768 | 0.048236 | 61.6028 | 0.003143 | 61.3856 | 61.5354 | 59.6102 | 63.5855 | 61.6724 | 60.7906 | 61.4991 | 62.2985 | 123.1887 | 61.7812 | 123.0971 | 61.4766 | 61.5625 | 123.1171 | 61.5174 | 122.8998 | 61.6262 | 61.6713 | 61.5346 | 61.5797
4241.0938 | 123.2895 | -61.4777 | 61.6882 | -0.024657 | -1.8858 | 2.1766 | 0.18102 | -0.75114 | -0.056347 | 0.80256 | 61.679 | 0.27153 | 61.5874 | -0.023943 | 0.048236 | 61.5982 | 0.007721 | 61.3947 | 61.453 | 59.5919 | 63.6542 | 61.6587 | 60.7265 | 61.4213 | 62.2802 | 123.1567 | 61.7492 | 123.065 | 61.4537 | 61.5259 | 123.0759 | 61.4854 | 122.8724 | 61.6308 | 61.6713 | 61.5392 | 61.5797
4242.0625 | 123.2758 | -61.5005 | 61.6608 | -0.084176 | -1.8766 | 2.1171 | 0.2268 | -0.87475 | -0.10671 | 0.99026 | 61.6699 | 0.26695 | 61.6103 | -0.033101 | 0.039079 | 61.5936 | 0.007721 | 61.381 | 61.4164 | 59.6239 | 63.6176 | 61.7273 | 60.6258 | 61.3938 | 62.4908 | 123.1704 | 61.7675 | 123.1108 | 61.4674 | 61.5396 | 123.0942 | 61.5083 | 122.8815 | 61.6308 | 61.6622 | 61.5712 | 61.6026
4243.0781 | 123.3261 | -61.4731 | 61.6791 | -0.21237 | -1.7667 | 1.7553 | 0.18559 | -0.91595 | -0.24864 | 1.1047 | 61.6836 | 0.26695 | 61.6194 | -0.028522 | 0.048236 | 61.6028 | 0.007721 | 61.3856 | 61.2607 | 59.7063 | 63.2284 | 61.6587 | 60.5571 | 61.2244 | 62.5778 | 123.1567 | 61.74 | 123.0925 | 61.4446 | 61.5213 | 123.0759 | 61.4808 | 122.8586 | 61.6354 | 61.6759 | 61.5712 | 61.6117
4244.0625 | 123.2574 | -61.528 | 61.6837 | -0.31767 | -1.8537 | 1.6729 | 0.13065 | -0.9892 | -0.35394 | 1.0269 | 61.6882 | 0.26695 | 61.624 | -0.03768 | 0.039079 | 61.5936 | 0.003143 | 61.3764 | 61.2103 | 59.6743 | 63.2009 | 61.6587 | 60.5388 | 61.1741 | 62.5549 | 123.2162 | 61.795 | 123.152 | 61.4903 | 61.5671 | 123.1216 | 61.5312 | 122.9044 | 61.6491 | 61.685 | 61.5849 | 61.6209
4245.0781 | 123.3215 | -61.4639 | 61.702 | -0.21237 | -1.8446 | 2.0392 | -0.043331 | -0.96173 | -0.24406 | 0.93075 | 61.6882 | 0.27153 | 61.624 | -0.033101 | 0.039079 | 61.5891 | -0.001436 | 61.3901 | 61.2516 | 59.6194 | 63.5031 | 61.4206 | 60.5022 | 61.2199 | 62.3947 | 123.1521 | 61.7355 | 123.0879 | 61.4308 | 61.503 | 123.053 | 61.4625 | 122.8541 | 61.6491 | 61.6896 | 61.5849 | 61.6255
4246.0625 | 123.3444 | -61.4594 | 61.6287 | -0.18032 | -1.8995 | 2.085 | -0.17611 | -1.0075 | -0.20743 | 0.83003 | 61.6836 | 0.27611 | 61.6149 | -0.042259 | 0.048236 | 61.5891 | -0.001436 | 61.3901 | 61.279 | 59.5598 | 63.5444 | 61.2832 | 60.4518 | 61.2519 | 62.2894 | 123.143 | 61.7355 | 123.0742 | 61.4171 | 61.5076 | 123.0484 | 61.4579 | 122.8495 | 61.6354 | 61.685 | 61.5666 | 61.6163
4247.0781 | 123.2712 | -61.5005 | 61.6974 | -0.18032 | -1.8079 | 2.1354 | -0.23563 | -1.0212 | -0.21201 | 0.82545 | 61.6836 | 0.27153 | 61.6103 | -0.028522 | 0.052814 | 61.5982 | 0.003143 | 61.3901 | 61.3202 | 59.6926 | 63.6359 | 61.2649 | 60.4793 | 61.2885 | 62.326 | 123.1842 | 61.7721 | 123.1108 | 61.472 | 61.5534 | 123.0988 | 61.5037 | 122.8907 | 61.6308 | 61.6805 | 61.5575 | 61.6071
4248.0625 | 123.3536 | -61.5051 | 61.6196 | -0.10249 | -1.6339 | 2.0438 | -0.21274 | -0.99378 | -0.13876 | 0.79798 | 61.679 | 0.26695 | 61.5828 | -0.023943 | 0.043657 | 61.5891 | 0.003143 | 61.3901 | 61.4026 | 59.8712 | 63.5489 | 61.2924 | 60.5114 | 61.3664 | 62.3031 | 123.1842 | 61.7721 | 123.0879 | 61.4812 | 61.5488 | 123.0942 | 61.5083 | 122.8953 | 61.6354 | 61.6759 | 61.5392 | 61.5797
4249.0938 | 123.262 | -61.5051 | 61.6745 | -0.065863 | -1.6111 | 2.0392 | -0.40503 | -1.035 | -0.11587 | 0.94906 | 61.6745 | 0.27153 | 61.592 | -0.023943 | 0.039079 | 61.5891 | 0.007721 | 61.3856 | 61.4393 | 59.8941 | 63.5443 | 61.1001 | 60.4701 | 61.3893 | 62.4542 | 123.1796 | 61.7767 | 123.0971 | 61.4812 | 61.5442 | 123.0942 | 61.5128 | 122.8907 | 61.6354 | 61.6667 | 61.5529 | 61.5842
4250.0625 | 123.3444 | -61.4777 | 61.647 | -0.047549 | -1.5836 | 2.0438 | -0.47829 | -1.0991 | -0.097553 | 1.0269 | 61.679 | 0.27153 | 61.5828 | -0.03768 | 0.043657 | 61.5891 | 0.003143 | 61.3672 | 61.4301 | 59.8941 | 63.5215 | 60.9994 | 60.3786 | 61.3801 | 62.5045 | 123.1567 | 61.7492 | 123.0605 | 61.44 | 61.5213 | 123.0667 | 61.4808 | 122.8449 | 61.6354 | 61.6759 | 61.5392 | 61.5797
4251.1094 | 123.3124 | -61.5143 | 61.6745 | -0.047549 | -1.5515 | 1.531 | -0.33636 | -1.1357 | -0.10213 | 0.83918 | 61.6836 | 0.27611 | 61.6194 | -0.03768 | 0.039079 | 61.5845 | 0.003143 | 61.3672 | 61.4667 | 59.9628 | 63.0453 | 61.1779 | 60.3786 | 61.4122 | 62.3535 | 123.1979 | 61.7904 | 123.1337 | 61.4766 | 61.5534 | 123.0988 | 61.5174 | 122.8815 | 61.6445 | 61.6805 | 61.5804 | 61.6163
4252.0625 | 123.1979 | -61.5189 | 61.6287 | -0.052128 | -1.8949 | 1.6867 | -0.28141 | -1.1265 | -0.092974 | 0.69726 | 61.6882 | 0.26695 | 61.624 | -0.033101 | 0.039079 | 61.5845 | 0.003143 | 61.3764 | 61.4667 | 59.6239 | 63.2055 | 61.2374 | 60.3923 | 61.4259 | 62.2161 | 123.207 | 61.7858 | 123.1429 | 61.4858 | 61.5579 | 123.1033 | 61.522 | 122.8953 | 61.6491 | 61.685 | 61.5849 | 61.6209
4253.0781 | 123.349 | -61.4822 | 61.6562 | -0.27189 | -1.8537 | 1.9156 | -0.21731 | -1.0945 | -0.35394 | 0.52787 | 61.7019 | 0.27611 | 61.6286 | -0.033101 | 0.043657 | 61.5845 | -0.001436 | 61.3627 | 61.2103 | 59.6285 | 63.3978 | 61.2649 | 60.3877 | 61.1283 | 62.0101 | 123.1842 | 61.7583 | 123.1108 | 61.4491 | 61.5259 | 123.0667 | 61.4808 | 122.8449 | 61.6583 | 61.7034 | 61.5849 | 61.63
4254.0625 | 123.381 | -61.4914 | 61.6745 | -0.32225 | -1.8904 | 1.9476 | -0.24479 | -1.067 | -0.37226 | 0.63316 | 61.6882 | 0.27153 | 61.624 | -0.03768 | 0.039079 | 61.5845 | 0.003143 | 61.3627 | 61.1691 | 59.601 | 63.439 | 61.2466 | 60.4244 | 61.1191 | 62.1246 | 123.1796 | 61.7629 | 123.1154 | 61.4537 | 61.5305 | 123.0759 | 61.4945 | 122.8541 | 61.6491 | 61.685 | 61.5849 | 61.6209
4255.0781 | 123.2849 | -61.4731 | 61.702 | -0.249 | -1.7484 | 1.9889 | -0.29057 | -1.0899 | -0.30358 | 0.68353 | 61.6882 | 0.26695 | 61.6149 | -0.028522 | 0.043657 | 61.5891 | 0.007721 | 61.3718 | 61.2241 | 59.7247 | 63.4619 | 61.1825 | 60.3832 | 61.1695 | 62.1566 | 123.1613 | 61.74 | 123.0879 | 61.4446 | 61.5167 | 123.0621 | 61.4808 | 122.8449 | 61.6445 | 61.6805 | 61.5712 | 61.6071
4256.0625 | 123.4406 | -61.4456 | 61.6516 | -0.25816 | -1.7164 | 1.9705 | -0.093694 | -1.0396 | -0.299 | 0.74304 | 61.6836 | 0.27153 | 61.5965 | -0.033101 | 0.043657 | 61.5891 | -0.001436 | 61.3627 | 61.1875 | 59.7293 | 63.4162 | 61.3519 | 60.4061 | 61.1466 | 62.1887 | 123.1292 | 61.7171 | 123.0422 | 61.4125 | 61.4893 | 123.0347 | 61.4442 | 122.8083 | 61.64 | 61.685 | 61.5529 | 61.598
4257.0938 | 123.3032 | -61.4456 | 61.702 | -0.42756 | -1.9316 | 1.6683 | -0.14864 | -1.0716 | -0.47756 | 0.6881 | 61.6928 | 0.27153 | 61.6011 | -0.033101 | 0.052814 | 61.5845 | 0.003143 | 61.3489 | 61.0181 | 59.514 | 63.114 | 61.297 | 60.374 | 60.9681 | 62.1337 | 123.1384 | 61.7171 | 123.0467 | 61.4125 | 61.4984 | 123.0301 | 61.4488 | 122.7945 | 61.64 | 61.6896 | 61.5483 | 61.598
4258.0625 | 123.2529 | -61.5143 | 61.6699 | -0.46418 | -1.9774 | 1.4257 | 0.15812 | -1.0121 | -0.50961 | 0.81629 | 61.6928 | 0.27153 | 61.5965 | -0.033101 | 0.039079 | 61.5799 | 0.003143 | 61.3535 | 61.0501 | 59.5369 | 62.94 | 61.6724 | 60.5022 | 61.0047 | 62.3306 | 123.2071 | 61.7858 | 123.1108 | 61.4812 | 61.5534 | 123.0942 | 61.5174 | 122.8678 | 61.6537 | 61.6896 | 61.5575 | 61.5934
4259.0938 | 123.2803 | -61.4914 | 61.6653 | -0.40924 | -1.753 | 1.4715 | -0.006703 | -1.0487 | -0.45009 | 0.86207 | 61.679 | 0.27153 | 61.624 | -0.033101 | 0.048236 | 61.5845 | 0.003143 | 61.3535 | 61.0822 | 59.7384 | 62.9629 | 61.4847 | 60.4427 | 61.0413 | 62.3535 | 123.1704 | 61.7629 | 123.1154 | 61.4583 | 61.5396 | 123.0759 | 61.4945 | 122.8449 | 61.6308 | 61.6759 | 61.5758 | 61.6209
4260.0625 | 123.2895 | -61.4914 | 61.6837 | -0.43213 | -1.7851 | 1.3341 | -0.26768 | -1.0579 | -0.4684 | 0.82087 | 61.6973 | 0.27153 | 61.6332 | -0.033101 | 0.039079 | 61.5799 | 0.003143 | 61.3535 | 61.0593 | 59.7063 | 62.8255 | 61.2237 | 60.4335 | 61.023 | 62.3123 | 123.1887 | 61.7629 | 123.1246 | 61.4583 | 61.5305 | 123.0713 | 61.4945 | 122.8449 | 61.6583 | 61.6942 | 61.5941 | 61.63
4261.1094 | 123.2574 | -61.4914 | 61.6791 | -0.18032 | -2.2063 | 1.2837 | -0.28141 | -1.1632 | -0.57828 | 0.56449 | 61.7019 | 0.26695 | 61.6332 | -0.033101 | 0.039079 | 61.5753 | 0.012299 | 61.3443 | 61.3111 | 59.2851 | 62.7751 | 61.21 | 60.3282 | 60.9131 | 62.0559 | 123.1933 | 61.7583 | 123.1246 | 61.4583 | 61.5305 | 123.0667 | 61.5037 | 122.8357 | 61.6628 | 61.6896 | 61.5941 | 61.6209
4262.0625 | 123.2849 | -61.5326 | 61.6516 | -0.35888 | -2.2155 | 1.1418 | -0.38214 | -1.2227 | -0.49129 | 0.45919 | 61.7111 | 0.27153 | 61.6332 | -0.033101 | 0.043657 | 61.5707 | -0.001436 | 61.3352 | 61.1737 | 59.3171 | 62.6744 | 61.1505 | 60.3099 | 61.0413 | 61.9918 | 123.2437 | 61.8041 | 123.1658 | 61.4995 | 61.5763 | 123.1033 | 61.5312 | 122.8678 | 61.6674 | 61.7125 | 61.5895 | 61.6346
4263.0625 | 123.2895 | -61.4914 | 61.6837 | -0.28563 | -2.1239 | 1.2059 | -0.39587 | -1.3051 | -0.41346 | 0.4363 | 61.6973 | 0.26695 | 61.6377 | -0.03768 | 0.043657 | 61.5662 | -0.001436 | 61.3489 | 61.2058 | 59.3675 | 62.6973 | 61.0955 | 60.1863 | 61.0779 | 61.9277 | 123.1887 | 61.7583 | 123.1291 | 61.4537 | 61.5351 | 123.0576 | 61.49 | 122.8403 | 61.6537 | 61.6988 | 61.5941 | 61.6392
4264.0938 | 123.3582 | -61.441 | 61.6608 | -0.26273 | -2.1147 | 1.1006 | -0.56528 | -1.3829 | -0.37226 | 0.33558 | 61.7019 | 0.27611 | 61.6149 | -0.033101 | 0.039079 | 61.5753 | 0.003143 | 61.3581 | 61.1783 | 59.3263 | 62.5416 | 60.8758 | 60.0581 | 61.0688 | 61.7766 | 123.143 | 61.7171 | 123.0559 | 61.4079 | 61.4801 | 123.0164 | 61.4442 | 122.7991 | 61.6628 | 61.6988 | 61.5758 | 61.6117
4265.0625 | 123.2758 | -61.4777 | 61.6928 | -0.25816 | -2.1376 | 1.3204 | -0.86746 | -1.4012 | -0.39057 | 0.21655 | 61.7019 | 0.26695 | 61.6103 | -0.033101 | 0.039079 | 61.5707 | 0.007721 | 61.3443 | 61.2195 | 59.34 | 62.798 | 60.6102 | 60.0764 | 61.0871 | 61.6942 | 123.1796 | 61.7446 | 123.0879 | 61.4446 | 61.5167 | 123.0484 | 61.4854 | 122.822 | 61.6628 | 61.6942 | 61.5712 | 61.6026
4266.1094 | 123.3673 | -61.4227 | 61.7065 | -0.60611 | -2.0598 | 1.3158 | -0.21731 | -1.3142 | -0.66527 | 0.38137 | 61.7019 | 0.26695 | 61.6057 | -0.03768 | 0.043657 | 61.5753 | 0.003143 | 61.3443 | 60.8166 | 59.3629 | 62.7385 | 61.2054 | 60.1085 | 60.7575 | 61.8041 | 123.1247 | 61.6897 | 123.0284 | 61.385 | 61.4664 | 122.998 | 61.4259 | 122.7671 | 61.6583 | 61.6988 | 61.562 | 61.6026
4267.0625 | 123.2941 | -61.4639 | 61.6837 | -0.33599 | -2.5406 | 1.4486 | -0.45539 | -1.4104 | -0.38141 | 0.45919 | 61.7065 | 0.26695 | 61.6377 | -0.033101 | 0.039079 | 61.5707 | -0.001436 | 61.3489 | 61.1279 | 58.9234 | 62.9125 | 61.0085 | 60.0536 | 61.0825 | 61.9231 | 123.1704 | 61.7309 | 123.1017 | 61.4308 | 61.503 | 123.0347 | 61.4625 | 122.8129 | 61.6674 | 61.7079 | 61.5987 | 61.6392
4268.0781 | 123.3215 | -61.4868 | 61.7111 | -0.2902 | -2.6184 | 1.4303 | -0.84915 | -1.4378 | -0.32189 | 0.12957 | 61.7157 | 0.27153 | 61.6561 | -0.033101 | 0.048236 | 61.5616 | 0.003143 | 61.3398 | 61.1966 | 58.8684 | 62.9171 | 60.6377 | 60.049 | 61.1649 | 61.6164 | 123.2025 | 61.7583 | 123.1429 | 61.4537 | 61.5351 | 123.0484 | 61.49 | 122.8266 | 61.6674 | 61.7125 | 61.6078 | 61.6529
4269.0625 | 123.2941 | -61.4868 | 61.702 | -0.3131 | -2.6504 | 1.5081 | -0.88577 | -1.4333 | -0.3631 | -0.19548 | 61.7202 | 0.27153 | 61.6561 | -0.033101 | 0.043657 | 61.5616 | 0.007721 | 61.3306 | 61.1737 | 58.8364 | 62.9949 | 60.601 | 60.0536 | 61.1237 | 61.2913 | 123.2071 | 61.7583 | 123.1429 | 61.4537 | 61.5305 | 123.0484 | 61.4945 | 122.8174 | 61.6766 | 61.7125 | 61.6124 | 61.6483
4270.0781 | 123.3215 | -61.4273 | 61.7111 | -0.28563 | -2.6917 | 1.3158 | -0.35925 | -1.3829 | -0.69732 | -0.41524 | 61.7065 | 0.27153 | 61.6194 | -0.028522 | 0.048236 | 61.5524 | 0.007721 | 61.3352 | 61.1417 | 58.7357 | 62.7431 | 61.0681 | 60.0444 | 60.73 | 61.0121 | 123.1338 | 61.6988 | 123.0467 | 61.3988 | 61.4755 | 122.9797 | 61.435 | 122.7625 | 61.6583 | 61.6988 | 61.5712 | 61.6117
4271.0625 | 123.2849 | -61.4456 | 61.7065 | -0.50539 | -2.6962 | 1.5356 | -0.1349 | -1.328 | -0.58286 | -0.5709 | 61.7157 | 0.27153 | 61.6286 | -0.03768 | 0.048236 | 61.5524 | -0.001436 | 61.3352 | 60.9402 | 58.7494 | 62.9812 | 61.3107 | 60.1177 | 60.8628 | 60.8747 | 123.1613 | 61.7171 | 123.0742 | 61.4079 | 61.4939 | 122.998 | 61.4442 | 122.7808 | 61.6674 | 61.7171 | 61.5804 | 61.63
4272.0781 | 123.3856 | -61.4319 | 61.6974 | -0.79383 | -2.5909 | 1.4394 | -0.21731 | -1.3692 | -0.8713 | -0.62125 | 61.7294 | 0.27153 | 61.6606 | -0.042259 | 0.048236 | 61.557 | 0.007721 | 61.3352 | 60.6381 | 58.841 | 62.8713 | 61.2146 | 60.0627 | 60.5606 | 60.8106 | 123.1613 | 61.7034 | 123.0925 | 61.3896 | 61.4801 | 122.9889 | 61.4396 | 122.7671 | 61.6812 | 61.7217 | 61.6124 | 61.6529
4273.0625 | 123.317 | -61.441 | 61.6608 | -0.72515 | -2.5451 | 1.563 | -0.31804 | -1.4058 | -0.82094 | 0.17993 | 61.7202 | 0.26695 | 61.6561 | -0.03768 | 0.043657 | 61.5662 | 0.003143 | 61.3398 | 60.7159 | 58.8959 | 63.0041 | 61.123 | 60.0352 | 60.6201 | 61.621 | 123.1613 | 61.708 | 123.0971 | 61.4034 | 61.4847 | 123.0072 | 61.4442 | 122.7808 | 61.6766 | 61.7171 | 61.6124 | 61.6529
4274.0938 | 123.2986 | -61.4319 | 61.7203 | -0.62901 | -2.4536 | 1.6409 | -0.48745 | -1.3097 | -0.7019 | 0.31727 | 61.7157 | 0.26695 | 61.6469 | -0.033101 | 0.052814 | 61.5616 | 0.007721 | 61.3443 | 60.8029 | 58.9783 | 63.0728 | 60.9444 | 60.1222 | 60.73 | 61.7492 | 123.1475 | 61.6988 | 123.0788 | 61.3988 | 61.4847 | 122.9935 | 61.4396 | 122.7762 | 61.6628 | 61.7079 | 61.5941 | 61.6392
4275.0625 | 123.3215 | -61.4548 | 61.6928 | -0.63816 | -2.3482 | 1.65 | -0.36383 | -1.2318 | -0.72021 | -0.048983 | 61.7157 | 0.26695 | 61.6469 | -0.028522 | 0.048236 | 61.557 | 0.012299 | 61.3398 | 60.8166 | 59.1065 | 63.1048 | 61.0909 | 60.2229 | 60.7346 | 61.4058 | 123.1704 | 61.7217 | 123.1017 | 61.4263 | 61.503 | 123.0118 | 61.4671 | 122.7945 | 61.6674 | 61.7034 | 61.5987 | 61.6346
4276.1094 | 123.2803 | -61.4548 | 61.734 | -0.50081 | -2.5085 | 1.5814 | -0.60191 | -1.3371 | -0.59202 | 0.63316 | 61.7019 | 0.26237 | 61.6103 | -0.03768 | 0.039079 | 61.5662 | -0.001436 | 61.3581 | 60.954 | 58.9463 | 63.0361 | 60.8529 | 60.1177 | 60.8628 | 62.0879 | 123.1567 | 61.7171 | 123.0651 | 61.4171 | 61.4939 | 123.0209 | 61.4533 | 122.8129 | 61.6628 | 61.7034 | 61.5712 | 61.6117
4277.0625 | 123.2895 | -61.4777 | 61.6882 | -0.50539 | -2.5909 | 1.4486 | -0.77589 | -1.3463 | -0.59202 | 0.64232 | 61.7019 | 0.26695 | 61.6286 | -0.033101 | 0.048236 | 61.5616 | 0.007721 | 61.3443 | 60.9723 | 58.8867 | 62.9262 | 60.7018 | 60.1314 | 60.8856 | 62.12 | 123.1796 | 61.7446 | 123.1063 | 61.4446 | 61.5259 | 123.0392 | 61.4854 | 122.822 | 61.6537 | 61.6942 | 61.5804 | 61.6209
4278.0938 | 123.3353 | -61.4319 | 61.734 | -0.54202 | -2.6321 | 1.5493 | -0.32262 | -1.3371 | -0.62865 | 0.65148 | 61.7111 | 0.27153 | 61.6469 | -0.03768 | 0.052814 | 61.5662 | 0.003143 | 61.3443 | 60.8899 | 58.7998 | 62.9812 | 61.1093 | 60.0948 | 60.8032 | 62.0834 | 123.143 | 61.7034 | 123.0788 | 61.3942 | 61.4847 | 122.998 | 61.435 | 122.7762 | 61.6583 | 61.7079 | 61.5941 | 61.6438
4279.0625 | 123.3353 | -61.4685 | 61.7157 | -0.44587 | -2.6459 | 1.4577 | -0.35009 | -1.3554 | -0.52792 | 0.52329 | 61.7157 | 0.27153 | 61.6469 | -0.033101 | 0.048236 | 61.5662 | 0.012299 | 61.3443 | 61.0226 | 58.8226 | 62.9262 | 61.1184 | 60.1131 | 60.9406 | 61.9918 | 123.1842 | 61.74 | 123.1154 | 61.4354 | 61.5167 | 123.0347 | 61.4808 | 122.8129 | 61.6674 | 61.7034 | 61.5987 | 61.6346
4280.0781 | 123.4222 | -61.4365 | 61.6653 | -0.39551 | -2.5497 | 1.5401 | -0.72095 | -1.3417 | -0.52334 | 0.39052 | 61.6973 | 0.27611 | 61.6149 | -0.028522 | 0.048236 | 61.5707 | 0.003143 | 61.3443 | 61.041 | 58.8867 | 62.9766 | 60.7155 | 60.0948 | 60.9131 | 61.827 | 123.1338 | 61.7126 | 123.0513 | 61.4079 | 61.4847 | 123.0072 | 61.4396 | 122.7808 | 61.6491 | 61.6942 | 61.5666 | 61.6117
4281.0625 | 123.349 | -61.441 | 61.702 | -0.56033 | -2.6504 | 1.3112 | -0.76216 | -1.3188 | -0.67901 | -0.085608 | 61.7202 | 0.28069 | 61.6332 | -0.028522 | 0.039079 | 61.5478 | 0.012299 | 61.3352 | 60.8807 | 58.7906 | 62.7523 | 60.6789 | 60.1222 | 60.762 | 61.3554 | 123.1613 | 61.7217 | 123.0742 | 61.4125 | 61.4801 | 122.9889 | 61.4533 | 122.7762 | 61.6812 | 61.7079 | 61.5941 | 61.6209
4282.0938 | 123.2803 | -61.4273 | 61.734 | -0.59238 | -2.6504 | 1.3295 | -0.8583 | -1.4104 | -0.69274 | 0.47751 | 61.7157 | 0.27153 | 61.6515 | -0.033101 | 0.043657 | 61.5616 | 0.007721 | 61.3306 | 60.8349 | 58.7769 | 62.7568 | 60.569 | 60.0169 | 60.7346 | 61.9048 | 123.143 | 61.6988 | 123.0788 | 61.3942 | 61.471 | 122.9889 | 61.435 | 122.7579 | 61.672 | 61.7079 | 61.6078 | 61.6438
4283.0625 | 123.3398 | -61.4594 | 61.7111 | -0.57406 | -2.7146 | 1.1922 | -0.29973 | -1.3737 | -0.69732 | 0.16619 | 61.7202 | 0.27153 | 61.6515 | -0.033101 | 0.048236 | 61.5662 | 0.007721 | 61.3306 | 60.8853 | 58.7448 | 62.6515 | 61.1596 | 60.0856 | 60.762 | 61.6255 | 123.1796 | 61.7309 | 123.1108 | 61.4262 | 61.5076 | 123.0255 | 61.4671 | 122.79 | 61.672 | 61.7125 | 61.6032 | 61.6438
4284.0781 | 123.4131 | -61.4319 | 61.6745 | -0.62901 | -2.7008 | 1.4852 | -0.29973 | -1.4104 | -0.74311 | 0.042581 | 61.7111 | 0.27611 | 61.6149 | -0.033101 | 0.043657 | 61.5616 | 0.003143 | 61.326 | 60.8029 | 58.7311 | 62.9171 | 61.1322 | 60.0215 | 60.6888 | 61.4745 | 123.143 | 61.708 | 123.0467 | 61.3988 | 61.4755 | 122.9935 | 61.435 | 122.7579 | 61.6674 | 61.7079 | 61.5712 | 61.6117
4285.0625 | 123.3307 | -61.4273 | 61.7249 | -0.66105 | -2.6642 | 1.5401 | -0.34551 | -1.4836 | -0.82094 | -0.30078 | 61.7111 | 0.26695 | 61.6194 | -0.028522 | 0.043657 | 61.5524 | 0.007721 | 61.326 | 60.7663 | 58.7631 | 62.9675 | 61.0818 | 59.9437 | 60.6064 | 61.1265 | 123.1384 | 61.6943 | 123.0467 | 61.3988 | 61.471 | 122.9797 | 61.435 | 122.7533 | 61.6674 | 61.7034 | 61.5758 | 61.6117
4286.0938 | 123.4222 | -61.4136 | 61.6699 | -0.75262 | -2.9389 | 1.3387 | -0.47829 | -1.5569 | -0.89877 | -0.28705 | 61.7294 | 0.27153 | 61.6606 | -0.03768 | 0.043657 | 61.5478 | -0.001436 | 61.3306 | 60.661 | 58.4747 | 62.7523 | 60.9353 | 59.8567 | 60.5148 | 61.1265 | 123.143 | 61.6851 | 123.0742 | 61.3759 | 61.4572 | 122.9614 | 61.4121 | 122.7442 | 61.6857 | 61.7308 | 61.617 | 61.6621
4287.0625 | 123.3673 | -61.4136 | 61.7065 | -0.77551 | -2.7649 | 1.2425 | -0.42792 | -1.621 | -0.90793 | -0.20922 | 61.734 | 0.27153 | 61.6652 | -0.033101 | 0.048236 | 61.5478 | 0.003143 | 61.3215 | 60.6381 | 58.6487 | 62.6561 | 60.9856 | 59.7926 | 60.5056 | 61.2044 | 123.1475 | 61.6851 | 123.0788 | 61.3805 | 61.4618 | 122.9614 | 61.4167 | 122.735 | 61.6857 | 61.7308 | 61.617 | 61.6621
4288.0781 | 123.4085 | -61.4182 | 61.6837 | -0.76178 | -2.8794 | 1.2242 | -0.95903 | -1.6988 | -0.91251 | -0.3191 | 61.7248 | 0.27611 | 61.6469 | -0.033101 | 0.039079 | 61.5387 | 0.007721 | 61.3215 | 60.6564 | 58.5388 | 62.6424 | 60.4591 | 59.7194 | 60.5056 | 61.0991 | 123.143 | 61.6943 | 123.0651 | 61.3851 | 61.4572 | 122.9568 | 61.4259 | 122.7396 | 61.6857 | 61.7171 | 61.6078 | 61.6392
4289.0625 | 123.3261 | -61.4365 | 61.6928 | -0.66105 | -2.7878 | 1.3387 | -0.95445 | -1.653 | -0.81178 | 0.001377 | 61.7248 | 0.27153 | 61.6377 | -0.028522 | 0.048236 | 61.5524 | 0.003143 | 61.3352 | 60.7754 | 58.6487 | 62.7751 | 60.482 | 59.7835 | 60.6247 | 61.4378 | 123.1613 | 61.708 | 123.0742 | 61.4079 | 61.4847 | 122.9889 | 61.4396 | 122.7717 | 61.6766 | 61.7217 | 61.5895 | 61.6346
4290.0781 | 123.4222 | -61.4227 | 61.6882 | -0.59238 | -2.5909 | 1.5493 | -0.52407 | -1.6164 | -0.9995 | -0.12223 | 61.7202 | 0.27153 | 61.6515 | -0.033101 | 0.048236 | 61.557 | 0.007721 | 61.3306 | 60.8304 | 58.8318 | 62.972 | 60.8987 | 59.8064 | 60.4232 | 61.3005 | 123.143 | 61.6943 | 123.0742 | 61.3896 | 61.471 | 122.9797 | 61.4304 | 122.7533 | 61.672 | 61.7125 | 61.6032 | 61.6438
4291.0625 | 123.3444 | -61.4548 | 61.6516 | -0.57864 | -2.4673 | 1.5905 | -0.41419 | -1.5386 | -0.91251 | 0.083784 | 61.7157 | 0.27153 | 61.6515 | -0.03768 | 0.043657 | 61.5524 | -0.001436 | 61.3306 | 60.8761 | 58.9875 | 63.0453 | 61.0406 | 59.9162 | 60.5423 | 61.5386 | 123.1704 | 61.7263 | 123.1063 | 61.4171 | 61.4984 | 123.0072 | 61.4533 | 122.7854 | 61.672 | 61.7171 | 61.6078 | 61.6529
4292.0781 | 123.3902 | -61.4456 | 61.6745 | -0.66563 | -2.4444 | 1.4944 | -0.4325 | -1.566 | -0.80262 | -0.15428 | 61.7111 | 0.26695 | 61.6377 | -0.028522 | 0.043657 | 61.5616 | 0.007721 | 61.3215 | 60.78 | 59.0012 | 62.94 | 61.0131 | 59.8796 | 60.643 | 61.2913 | 123.1567 | 61.7126 | 123.0834 | 61.4171 | 61.4893 | 123.0072 | 61.4533 | 122.7671 | 61.6674 | 61.7034 | 61.5941 | 61.63
4293.0625 | 123.3124 | -61.4273 | 61.6974 | -0.61527 | -2.3574 | 1.2883 | -0.29973 | -1.5111 | -0.91708 | -0.17259 | 61.7157 | 0.27153 | 61.6286 | -0.033101 | 0.048236 | 61.5478 | 0.007721 | 61.3306 | 60.812 | 59.0699 | 62.7156 | 61.1276 | 59.9162 | 60.5102 | 61.2547 | 123.143 | 61.6988 | 123.0559 | 61.3942 | 61.4755 | 122.9752 | 61.435 | 122.7579 | 61.6674 | 61.7079 | 61.5804 | 61.6209
4294.0781 | 123.3948 | -61.4502 | 61.702 | -0.67479 | -2.3895 | 1.1098 | -0.30888 | -1.5477 | -0.8713 | -0.058139 | 61.7157 | 0.26695 | 61.6469 | -0.042259 | 0.043657 | 61.557 | -0.001436 | 61.3306 | 60.7754 | 59.0607 | 62.56 | 61.1413 | 59.9025 | 60.5789 | 61.3921 | 123.1659 | 61.7171 | 123.0971 | 61.4079 | 61.4939 | 123.0072 | 61.4488 | 122.7808 | 61.672 | 61.7171 | 61.6032 | 61.6483
4295.0625 | 123.3444 | -61.4594 | 61.6882 | -0.71599 | -2.3025 | 1.2013 | -0.26768 | -1.566 | -0.81636 | 0.079206 | 61.7157 | 0.27153 | 61.6515 | -0.042259 | 0.048236 | 61.5616 | 0.012299 | 61.3306 | 60.7434 | 59.1569 | 62.6607 | 61.1917 | 59.8933 | 60.643 | 61.5386 | 123.175 | 61.7309 | 123.1108 | 61.4171 | 61.5076 | 123.0209 | 61.4716 | 122.79 | 61.6674 | 61.7034 | 61.6032 | 61.6392
4296.0938 | 123.4039 | -61.4502 | 61.6379 | -0.66563 | -2.1834 | 1.3891 | -0.24021 | -1.5248 | -0.766 | 0.13414 | 61.7111 | 0.27153 | 61.6286 | -0.033101 | 0.048236 | 61.5524 | 0.003143 | 61.3352 | 60.7846 | 59.2668 | 62.8392 | 61.21 | 59.9254 | 60.6842 | 61.5843 | 123.1613 | 61.7217 | 123.0788 | 61.4171 | 61.4984 | 123.0026 | 61.4533 | 122.7854 | 61.6628 | 61.7079 | 61.5804 | 61.6255
4297.0625 | 123.3215 | -61.441 | 61.702 | -0.66105 | -2.1285 | 1.4211 | -0.26768 | -1.5477 | -0.74768 | 0.07005 | 61.7065 | 0.27611 | 61.6194 | -0.023943 | 0.039079 | 61.5662 | 0.007721 | 61.3398 | 60.78 | 59.3126 | 62.8621 | 61.1734 | 59.8933 | 60.6934 | 61.5111 | 123.1475 | 61.7171 | 123.0605 | 61.4171 | 61.4801 | 123.0072 | 61.4488 | 122.7808 | 61.6674 | 61.6988 | 61.5804 | 61.6117
4298.0938 | 123.317 | -61.4594 | 61.7203 | -0.70684 | -1.9819 | 1.4852 | -0.15779 | -1.5386 | -0.766 | 0.005955 | 61.7157 | 0.27153 | 61.6332 | -0.03768 | 0.039079 | 61.5662 | 0.003143 | 61.3352 | 60.7525 | 59.4774 | 62.9446 | 61.3016 | 59.9208 | 60.6934 | 61.4653 | 123.175 | 61.7309 | 123.0925 | 61.4217 | 61.4984 | 123.0255 | 61.4625 | 122.7945 | 61.6766 | 61.7125 | 61.5941 | 61.63
4299.0625 | 123.3353 | -61.4456 | 61.7294 | -0.84877 | -2.1926 | 1.3112 | -0.25394 | -1.7583 | -0.90793 | -0.003201 | 61.7248 | 0.26237 | 61.6606 | -0.03768 | 0.048236 | 61.5524 | -0.001436 | 61.3306 | 60.5969 | 59.2531 | 62.7568 | 61.1917 | 59.6873 | 60.5377 | 61.4424 | 123.1704 | 61.708 | 123.1063 | 61.4079 | 61.4939 | 122.998 | 61.4442 | 122.7762 | 61.6766 | 61.7263 | 61.6124 | 61.6621
4300.0781 | 123.4268 | -61.441 | 61.6745 | -0.73889 | -2.0827 | 1.4257 | -0.16695 | -1.685 | -0.83467 | 0.30354 | 61.7202 | 0.27153 | 61.6469 | -0.023943 | 0.039079 | 61.557 | 0.007721 | 61.3306 | 60.7022 | 59.3584 | 62.8667 | 61.2741 | 59.756 | 60.6064 | 61.7446 | 123.1613 | 61.7126 | 123.0879 | 61.4171 | 61.4801 | 122.998 | 61.4488 | 122.7717 | 61.6812 | 61.7125 | 61.6078 | 61.6392
4301.0625 | 123.2574 | -61.4914 | 61.6882 | -0.73431 | -2.0873 | 1.2654 | -0.070802 | -1.621 | -0.78889 | 0.15704 | 61.7065 | 0.26695 | 61.6103 | -0.028522 | 0.043657 | 61.5662 | 0.003143 | 61.3352 | 60.7571 | 59.4041 | 62.7568 | 61.4206 | 59.8704 | 60.7025 | 61.6484 | 123.1979 | 61.7583 | 123.1017 | 61.4629 | 61.5351 | 123.0576 | 61.4945 | 122.8266 | 61.6628 | 61.7034 | 61.5666 | 61.6071
4302.0938 | 123.3215 | -61.4319 | 61.7386 | -0.6931 | -2.0369 | 1.3021 | -0.16237 | -1.5935 | -0.75226 | 0.056315 | 61.7019 | 0.27611 | 61.624 | -0.033101 | 0.048236 | 61.5616 | 0.012299 | 61.3443 | 60.7388 | 59.395 | 62.7339 | 61.2695 | 59.8384 | 60.6796 | 61.4882 | 123.1338 | 61.708 | 123.0559 | 61.3988 | 61.4801 | 122.9935 | 61.4442 | 122.7762 | 61.6537 | 61.6896 | 61.5758 | 61.6117
4303.0625 | 123.3307 | -61.4456 | 61.6974 | -0.6519 | -2.0644 | 1.4944 | -0.14864 | -1.5477 | -0.73853 | -0.08103 | 61.7202 | 0.27153 | 61.6469 | -0.033101 | 0.048236 | 61.5707 | 0.007721 | 61.3398 | 60.7937 | 59.3813 | 62.94 | 61.297 | 59.8979 | 60.7071 | 61.3646 | 123.1659 | 61.7171 | 123.0925 | 61.4125 | 61.4939 | 123.0164 | 61.4533 | 122.7854 | 61.672 | 61.7125 | 61.5987 | 61.6392
4304.0781 | 123.4314 | -61.4319 | 61.6974 | -0.68852 | -2.101 | 1.4669 | -0.066223 | -1.5065 | -0.77058 | -0.43813 | 61.7157 | 0.27153 | 61.6469 | -0.028522 | 0.048236 | 61.5616 | 0.012299 | 61.3306 | 60.7434 | 59.3309 | 62.8988 | 61.3657 | 59.9254 | 60.6613 | 60.9938 | 123.1475 | 61.7034 | 123.0788 | 61.4034 | 61.4801 | 122.9935 | 61.4442 | 122.7625 | 61.6674 | 61.7034 | 61.5987 | 61.6346
4305.0625 | 123.317 | -61.4182 | 61.734 | -0.76178 | -2.4902 | 1.3753 | -0.24021 | -1.6072 | -0.85299 | -0.77233 | 61.7248 | 0.27153 | 61.6332 | -0.023943 | 0.048236 | 61.5478 | 0.007721 | 61.3352 | 60.6564 | 58.928 | 62.7935 | 61.1779 | 59.8109 | 60.5652 | 60.6458 | 123.143 | 61.6897 | 123.0513 | 61.3942 | 61.4664 | 122.966 | 61.4259 | 122.7533 | 61.6766 | 61.7171 | 61.5849 | 61.6255
4306.1094 | 123.436 | -61.4182 | 61.6699 | -0.67937 | -2.3528 | 1.2883 | -0.20816 | -1.5614 | -0.77515 | -0.19548 | 61.7202 | 0.26695 | 61.6332 | -0.033101 | 0.048236 | 61.5616 | 0.003143 | 61.3352 | 60.7388 | 59.0653 | 62.7065 | 61.21 | 59.8567 | 60.643 | 61.2227 | 123.1384 | 61.6851 | 123.0513 | 61.3851 | 61.4664 | 122.9797 | 61.4213 | 122.7533 | 61.672 | 61.7171 | 61.5849 | 61.63
4307.0625 | 123.317 | -61.4548 | 61.7203 | -0.73431 | -2.3895 | 1.357 | -0.43708 | -1.6942 | -0.81178 | -0.30536 | 61.7294 | 0.27153 | 61.6652 | -0.028522 | 0.048236 | 61.5524 | 0.003143 | 61.3306 | 60.7205 | 59.0653 | 62.8118 | 61.0177 | 59.7606 | 60.643 | 61.1494 | 123.1842 | 61.7263 | 123.12 | 61.4263 | 61.503 | 123.0072 | 61.4579 | 122.7854 | 61.6812 | 61.7263 | 61.617 | 61.6621
4308.0938 | 123.4451 | -61.4136 | 61.6882 | -0.66105 | -2.1376 | 1.4394 | -0.40961 | -1.6759 | -0.766 | -0.27331 | 61.7111 | 0.27153 | 61.6561 | -0.033101 | 0.043657 | 61.5524 | 0.007721 | 61.326 | 60.7525 | 59.276 | 62.853 | 61.004 | 59.7377 | 60.6476 | 61.1403 | 123.1247 | 61.6851 | 123.0696 | 61.3805 | 61.4572 | 122.966 | 61.4213 | 122.7396 | 61.6674 | 61.7034 | 61.6124 | 61.6483
4309.0625 | 123.2986 | -61.4548 | 61.7294 | -0.76178 | -2.2063 | 0.92661 | -0.23563 | -1.653 | -0.81636 | -0.63499 | 61.7202 | 0.26695 | 61.6423 | -0.028522 | 0.048236 | 61.5478 | 0.003143 | 61.326 | 60.693 | 59.2485 | 62.3814 | 61.2191 | 59.8018 | 60.6384 | 60.8198 | 123.175 | 61.7217 | 123.0971 | 61.4263 | 61.503 | 123.0026 | 61.4579 | 122.7808 | 61.672 | 61.7171 | 61.5941 | 61.6392
4310.0781 | 123.4085 | -61.4273 | 61.6882 | -0.70684 | -2.1926 | 0.56948 | -0.07538 | -1.6255 | -0.766 | -0.53427 | 61.7202 | 0.27611 | 61.6332 | -0.028522 | 0.048236 | 61.5478 | 0.003143 | 61.3352 | 60.7205 | 59.2347 | 61.9968 | 61.3519 | 59.8018 | 60.6613 | 60.893 | 123.1475 | 61.7034 | 123.0605 | 61.3988 | 61.4755 | 122.9752 | 61.4305 | 122.7625 | 61.672 | 61.7171 | 61.5849 | 61.63
4311.0625 | 123.2437 | -61.4639 | 61.7065 | -0.7572 | -2.2796 | 0.57864 | -0.084537 | -1.6576 | -0.81178 | -0.67161 | 61.7248 | 0.26695 | 61.6698 | -0.03768 | 0.048236 | 61.5524 | 0.003143 | 61.3306 | 60.7067 | 59.1844 | 62.0426 | 61.3794 | 59.8063 | 60.6521 | 60.7923 | 123.1887 | 61.7309 | 123.1337 | 61.4262 | 61.5122 | 123.0164 | 61.4671 | 122.7945 | 61.6766 | 61.7217 | 61.6216 | 61.6667
4312.0781 | 123.3719 | -61.441 | 61.6745 | -0.72057 | -2.1605 | 0.72973 | -0.20358 | -1.6896 | -0.81636 | -0.7998 | 61.7294 | 0.27611 | 61.6652 | -0.033101 | 0.039079 | 61.5478 | 0.007721 | 61.3443 | 60.7205 | 59.2805 | 62.1708 | 61.2375 | 59.7514 | 60.6247 | 60.6412 | 123.1704 | 61.7171 | 123.1063 | 61.4079 | 61.4801 | 122.9889 | 61.4488 | 122.7854 | 61.6903 | 61.7217 | 61.6261 | 61.6575
4313.0625 | 123.3032 | -61.4502 | 61.734 | -0.6931 | -2.0735 | 0.83504 | -0.20816 | -1.6759 | -0.77058 | 0.038003 | 61.7111 | 0.27153 | 61.6332 | -0.042259 | 0.043657 | 61.557 | 0.003143 | 61.3627 | 60.7571 | 59.3767 | 62.2852 | 61.242 | 59.7743 | 60.6796 | 61.4882 | 123.1613 | 61.7217 | 123.0834 | 61.4079 | 61.4939 | 123.0072 | 61.4533 | 122.8129 | 61.6674 | 61.7079 | 61.5895 | 61.63
4314.0781 | 123.436 | -61.409 | 61.6882 | -0.83961 | -2.2521 | 0.45044 | -0.45539 | -1.7766 | -0.90335 | 0.001377 | 61.7294 | 0.26695 | 61.6469 | -0.033101 | 0.048236 | 61.5478 | 0.007721 | 61.3398 | 60.5694 | 59.1569 | 61.8594 | 60.9536 | 59.6324 | 60.5056 | 61.4104 | 123.1384 | 61.6759 | 123.0559 | 61.3759 | 61.4572 | 122.9568 | 61.4167 | 122.7488 | 61.6812 | 61.7217 | 61.5987 | 61.6392
4315.0625 | 123.3032 | -61.4456 | 61.7386 | -0.73889 | -2.1285 | 0.54201 | -0.47829 | -1.6805 | -0.80262 | 0.1845 | 61.7248 | 0.27611 | 61.6652 | -0.033101 | 0.052814 | 61.5524 | -0.001436 | 61.3443 | 60.7067 | 59.3172 | 61.9876 | 60.9673 | 59.7651 | 60.643 | 61.6301 | 123.1704 | 61.7217 | 123.1108 | 61.4125 | 61.4984 | 122.998 | 61.4442 | 122.79 | 61.672 | 61.7263 | 61.6124 | 61.6667
4316.0938 | 123.436 | -61.4136 | 61.6516 | -0.79841 | -2.275 | 0.45044 | -0.56528 | -1.7262 | -0.87588 | 0.17535 | 61.7386 | 0.26695 | 61.6606 | -0.03768 | 0.048236 | 61.5433 | 0.012299 | 61.3398 | 60.6152 | 59.1386 | 61.864 | 60.8483 | 59.6873 | 60.5377 | 61.5889 | 123.1521 | 61.6805 | 123.0742 | 61.3759 | 61.4618 | 122.9568 | 61.4259 | 122.7533 | 61.6903 | 61.7263 | 61.6124 | 61.6483
4317.0625 | 123.2254 | -61.409 | 61.7477 | -0.88539 | -2.7649 | 0.23067 | -0.64311 | -1.7903 | -0.94455 | 0.07005 | 61.7248 | 0.27611 | 61.6469 | -0.033101 | 0.043657 | 61.5433 | 0.003143 | 61.3398 | 60.5236 | 58.6441 | 61.6397 | 60.7659 | 59.6187 | 60.4644 | 61.479 | 123.1338 | 61.6851 | 123.0559 | 61.3759 | 61.4527 | 122.9523 | 61.4121 | 122.7488 | 61.6812 | 61.7217 | 61.6032 | 61.6438
4318.0781 | 123.3856 | -61.441 | 61.6745 | -0.72973 | -2.4765 | 0.3085 | -0.40503 | -1.5935 | -0.8713 | 0.29896 | 61.7248 | 0.26695 | 61.6423 | -0.033101 | 0.039079 | 61.5433 | 0.003143 | 61.3398 | 60.7113 | 58.9646 | 61.7495 | 61.036 | 59.8476 | 60.5697 | 61.74 | 123.1659 | 61.708 | 123.0834 | 61.4079 | 61.4801 | 122.9843 | 61.4442 | 122.7808 | 61.6857 | 61.7217 | 61.6032 | 61.6392
4319.0625 | 123.2712 | -61.4456 | 61.7157 | -0.69768 | -2.362 | 0.63358 | -0.31346 | -1.5294 | -0.77515 | 0.27149 | 61.7294 | 0.26237 | 61.6423 | -0.03768 | 0.048236 | 61.5478 | 0.012299 | 61.3398 | 60.7479 | 59.0836 | 62.0792 | 61.1322 | 59.9162 | 60.6705 | 61.7171 | 123.175 | 61.708 | 123.0879 | 61.4079 | 61.4939 | 122.9935 | 61.4579 | 122.7854 | 61.6812 | 61.7171 | 61.5941 | 61.63
4320.0781 | 123.3444 | -61.4365 | 61.6653 | -0.68852 | -2.2704 | 0.89456 | -0.29973 | -1.5431 | -0.73853 | 0.45462 | 61.7157 | 0.27153 | 61.6561 | -0.033101 | 0.039079 | 61.5616 | 0.003143 | 61.3489 | 60.7479 | 59.1661 | 62.331 | 61.1367 | 59.8933 | 60.6979 | 61.8911 | 123.1521 | 61.708 | 123.0925 | 61.4034 | 61.4755 | 122.998 | 61.4396 | 122.7854 | 61.6766 | 61.7125 | 61.617 | 61.6529
4321.0625 | 123.349 | -61.441 | 61.6928 | -0.63358 | -2.1056 | 0.92204 | -0.199 | -1.5294 | -0.75226 | 0.47293 | 61.7202 | 0.27153 | 61.6194 | -0.028522 | 0.043657 | 61.5662 | 0.003143 | 61.3398 | 60.8075 | 59.3355 | 62.3631 | 61.242 | 59.9116 | 60.6888 | 61.914 | 123.1613 | 61.7126 | 123.0605 | 61.4125 | 61.4847 | 123.0072 | 61.4442 | 122.7808 | 61.6766 | 61.7171 | 61.5758 | 61.6163
4322.0938 | 123.3994 | -61.441 | 61.6745 | -0.5878 | -2.0231 | 1.096 | -0.070802 | -1.3921 | -0.69732 | 0.53244 | 61.7019 | 0.27153 | 61.6149 | -0.03768 | 0.057392 | 61.5707 | 0.007721 | 61.3398 | 60.8532 | 59.4179 | 62.5371 | 61.3702 | 60.049 | 60.7437 | 61.9735 | 123.143 | 61.7126 | 123.0559 | 61.4034 | 61.4984 | 123.0118 | 61.4488 | 122.7808 | 61.6445 | 61.6942 | 61.5575 | 61.6071
4323.0625 | 123.3215 | -61.4777 | 61.7065 | -0.62901 | -1.9911 | 1.2334 | -0.057066 | -1.3737 | -0.71106 | 0.5004 | 61.7065 | 0.27153 | 61.6515 | -0.033101 | 0.039079 | 61.5662 | 0.012299 | 61.3489 | 60.8487 | 59.4866 | 62.711 | 61.4206 | 60.1039 | 60.7666 | 61.9781 | 123.1842 | 61.7492 | 123.1291 | 61.4446 | 61.5167 | 123.0438 | 61.49 | 122.8266 | 61.6674 | 61.6942 | 61.6124 | 61.6392
4324.0938 | 123.4268 | -61.441 | 61.6791 | -0.61069 | -2.0323 | 0.9083 | -0.034174 | -1.4104 | -0.67443 | 0.40884 | 61.7111 | 0.27153 | 61.6469 | -0.042259 | 0.043657 | 61.5753 | 0.007721 | 61.3489 | 60.8303 | 59.4087 | 62.3493 | 61.4069 | 60.0307 | 60.7666 | 61.8499 | 123.1521 | 61.7126 | 123.0879 | 61.3988 | 61.4847 | 123.0164 | 61.4488 | 122.79 | 61.6674 | 61.7034 | 61.6032 | 61.6392
4325.0625 | 123.2803 | -61.4456 | 61.7294 | -0.62443 | -2.1376 | 0.716 | -0.199 | -1.4562 | -0.68817 | -0.099343 | 61.7111 | 0.26695 | 61.624 | -0.028522 | 0.043657 | 61.5524 | -0.001436 | 61.3489 | 60.8212 | 59.308 | 62.1616 | 61.2466 | 59.9895 | 60.7575 | 61.3463 | 123.1567 | 61.7126 | 123.0696 | 61.4171 | 61.4893 | 122.998 | 61.4442 | 122.7945 | 61.6674 | 61.7125 | 61.5804 | 61.6255
4326.1094 | 123.3719 | -61.4548 | 61.702 | -0.6931 | -2.1834 | 0.73431 | -0.45082 | -1.5386 | -0.77058 | -0.37861 | 61.7157 | 0.28069 | 61.6286 | -0.03768 | 0.043657 | 61.5433 | 0.007721 | 61.326 | 60.7617 | 59.2714 | 62.1891 | 61.004 | 59.9162 | 60.6842 | 61.0762 | 123.1704 | 61.7355 | 123.0834 | 61.4171 | 61.4984 | 122.998 | 61.4625 | 122.7808 | 61.672 | 61.7079 | 61.5849 | 61.6209
4327.0625 | 123.4177 | -61.3998 | 61.6837 | -0.70684 | -2.2429 | 0.93119 | -0.40503 | -1.4699 | -0.766 | -0.88679 | 61.7248 | 0.26695 | 61.6652 | -0.028522 | 0.048236 | 61.5478 | 0.007721 | 61.3215 | 60.693 | 59.1569 | 62.331 | 60.9948 | 59.93 | 60.6338 | 60.5131 | 123.1247 | 61.6668 | 123.0651 | 61.3713 | 61.4481 | 122.9477 | 61.4076 | 122.7213 | 61.6766 | 61.7171 | 61.617 | 61.6575
4328.0781 | 123.3261 | -61.4319 | 61.702 | -0.73889 | -2.2475 | 0.81215 | -0.27683 | -1.5935 | -0.80262 | -0.92341 | 61.7294 | 0.27153 | 61.6698 | -0.033101 | 0.039079 | 61.5387 | 0.003143 | 61.3215 | 60.693 | 59.1844 | 62.244 | 61.1551 | 59.8384 | 60.6293 | 60.5085 | 123.1613 | 61.7034 | 123.1017 | 61.3988 | 61.471 | 122.9706 | 61.435 | 122.7533 | 61.6903 | 61.7263 | 61.6307 | 61.6667
4329.0625 | 123.4131 | -61.3998 | 61.6928 | -0.77094 | -2.2384 | 0.6519 | -0.3272 | -1.6301 | -0.83925 | -0.82269 | 61.7294 | 0.27153 | 61.6423 | -0.028522 | 0.048236 | 61.5433 | 0.003143 | 61.326 | 60.6289 | 59.1615 | 62.0517 | 61.0726 | 59.7697 | 60.5606 | 60.5771 | 123.1292 | 61.6714 | 123.0422 | 61.3713 | 61.4481 | 122.9431 | 61.403 | 122.7259 | 61.6812 | 61.7263 | 61.5941 | 61.6392
4330.0938 | 123.4177 | -61.3953 | 61.6699 | -0.75262 | -2.22 | 0.77552 | -0.23563 | -1.621 | -0.86672 | -0.78607 | 61.7202 | 0.27611 | 61.6286 | -0.033101 | 0.048236 | 61.5433 | 0.003143 | 61.326 | 60.6426 | 59.1752 | 62.1708 | 61.1596 | 59.7743 | 60.5285 | 60.6092 | 123.1155 | 61.6714 | 123.0239 | 61.3622 | 61.4435 | 122.9385 | 61.3984 | 122.7213 | 61.672 | 61.7171 | 61.5804 | 61.6255
4331.0625 | 123.2895 | -61.4502 | 61.6837 | -0.84877 | -2.2933 | 1.1464 | -0.41877 | -1.8041 | -0.96745 | -0.56174 | 61.7248 | 0.26695 | 61.6698 | -0.033101 | 0.039079 | 61.5433 | 0.012299 | 61.3169 | 60.6014 | 59.1569 | 62.5966 | 61.0314 | 59.6461 | 60.4827 | 60.8885 | 123.175 | 61.7171 | 123.12 | 61.4171 | 61.4893 | 122.9935 | 61.4625 | 122.7671 | 61.6857 | 61.7125 | 61.6307 | 61.6575
4332.0781 | 123.4177 | -61.4365 | 61.6608 | -0.8213 | -2.2521 | 1.4944 | -0.25852 | -1.7491 | -0.93998 | -0.44271 | 61.7157 | 0.27611 | 61.6606 | -0.028522 | 0.048236 | 61.5524 | 0.003143 | 61.3215 | 60.6152 | 59.1844 | 62.9308 | 61.1779 | 59.6873 | 60.4965 | 60.9938 | 123.1521 | 61.7126 | 123.0971 | 61.4079 | 61.4847 | 122.9889 | 61.4396 | 122.7579 | 61.6674 | 61.7125 | 61.6124 | 61.6575
4333.0625 | 123.3124 | -61.3953 | 61.6608 | -0.86708 | -2.2109 | 1.4028 | -0.23105 | -1.7766 | -0.93998 | -0.68993 | 61.7157 | 0.27611 | 61.6286 | -0.03768 | 0.043657 | 61.5433 | -0.001436 | 61.326 | 60.5282 | 59.1844 | 62.7981 | 61.1642 | 59.6187 | 60.4553 | 60.7053 | 123.1109 | 61.6714 | 123.0239 | 61.3576 | 61.4389 | 122.9385 | 61.3938 | 122.7213 | 61.672 | 61.7171 | 61.5849 | 61.63
4334.0938 | 123.3673 | -61.4319 | 61.6882 | -0.87166 | -2.1697 | 1.3478 | -0.199 | -1.7675 | -0.97203 | -0.76776 | 61.7248 | 0.27153 | 61.6286 | -0.03768 | 0.043657 | 61.5478 | 0.003143 | 61.326 | 60.5602 | 59.2622 | 62.7797 | 61.2329 | 59.6644 | 60.4599 | 60.6641 | 123.1567 | 61.7034 | 123.0605 | 61.3942 | 61.4755 | 122.9797 | 61.435 | 122.7579 | 61.6812 | 61.7217 | 61.5849 | 61.6255
4335.0625 | 123.2529 | -61.4548 | 61.6882 | -0.67479 | -2.2063 | 1.4577 | -0.12574 | -1.7583 | -1.0911 | -0.79522 | 61.7248 | 0.27153 | 61.6606 | -0.033101 | 0.043657 | 61.5478 | 0.003143 | 61.3215 | 60.78 | 59.2485 | 62.9125 | 61.329 | 59.6965 | 60.3637 | 60.6595 | 123.1796 | 61.7263 | 123.1154 | 61.4217 | 61.4984 | 123.0026 | 61.4579 | 122.7762 | 61.6812 | 61.7217 | 61.617 | 61.6575
4336.0938 | 123.2986 | -61.4639 | 61.7294 | -0.85792 | -2.3116 | 1.2288 | -0.40961 | -1.8727 | -0.97203 | -0.5068 | 61.7386 | 0.28069 | 61.6698 | -0.03768 | 0.039079 | 61.5433 | 0.012299 | 61.3169 | 60.606 | 59.1523 | 62.6927 | 61.0543 | 59.5912 | 60.4919 | 60.9571 | 123.2025 | 61.7446 | 123.1337 | 61.4262 | 61.503 | 123.0072 | 61.4762 | 122.7808 | 61.6995 | 61.7263 | 61.6307 | 61.6575
4337.0625 | 123.4222 | -61.4136 | 61.6974 | -0.84419 | -2.3116 | 1.2517 | -0.68432 | -1.9551 | -0.91708 | 0.065472 | 61.7202 | 0.27153 | 61.6286 | -0.033101 | 0.048236 | 61.5478 | 0.003143 | 61.3306 | 60.5694 | 59.102 | 62.6653 | 60.7293 | 59.4584 | 60.4965 | 61.479 | 123.1338 | 61.6851 | 123.0422 | 61.3805 | 61.4618 | 122.9614 | 61.4167 | 122.7442 | 61.672 | 61.7171 | 61.5804 | 61.6255
4338.0781 | 123.3948 | -61.441 | 61.6516 | -0.8625 | -2.3666 | 1.0411 | -0.21274 | -1.9185 | -0.94913 | -0.55258 | 61.7248 | 0.27153 | 61.6423 | -0.03768 | 0.048236 | 61.5478 | 0.007721 | 61.3215 | 60.5785 | 59.0745 | 62.4821 | 61.2283 | 59.5225 | 60.4919 | 60.8885 | 123.1659 | 61.7126 | 123.0834 | 61.4034 | 61.4893 | 122.9889 | 61.4488 | 122.7625 | 61.6766 | 61.7171 | 61.5941 | 61.6346
4339.0625 | 123.4222 | -61.4044 | 61.6974 | -0.89913 | -2.4169 | 0.75263 | -0.33636 | -2.033 | -0.98118 | -0.52969 | 61.734 | 0.26695 | 61.6698 | -0.033101 | 0.048236 | 61.5387 | 0.007721 | 61.3123 | 60.5053 | 58.9875 | 62.157 | 61.0681 | 59.3714 | 60.4232 | 60.8747 | 123.1384 | 61.6714 | 123.0742 | 61.3713 | 61.4527 | 122.9431 | 61.4121 | 122.7167 | 61.6857 | 61.7263 | 61.6216 | 61.6621
4340.0938 | 123.4543 | -61.3724 | 61.6974 | -0.82588 | -2.4444 | 0.67021 | -0.43708 | -1.9963 | -0.94913 | -0.90052 | 61.7431 | 0.26695 | 61.679 | -0.033101 | 0.048236 | 61.5387 | 0.003143 | 61.3077 | 60.5465 | 58.928 | 62.0426 | 60.9353 | 59.376 | 60.4232 | 60.4719 | 123.1155 | 61.6393 | 123.0513 | 61.3393 | 61.4206 | 122.9111 | 61.3755 | 122.6801 | 61.6949 | 61.74 | 61.6307 | 61.6758
4341.0625 | 123.3994 | -61.3953 | 61.6974 | -0.72973 | -2.22 | 0.87167 | -0.37298 | -1.9597 | -0.83925 | -0.78149 | 61.7202 | 0.27611 | 61.6332 | -0.028522 | 0.039079 | 61.5433 | 0.007721 | 61.3215 | 60.6655 | 59.1752 | 62.2669 | 61.0223 | 59.4355 | 60.556 | 60.6138 | 123.1155 | 61.6714 | 123.0284 | 61.3667 | 61.4343 | 122.9385 | 61.403 | 122.7167 | 61.6812 | 61.7125 | 61.5941 | 61.6255
4342.0781 | 123.2803 | -61.4594 | 61.6974 | -0.71142 | -2.1514 | 0.83046 | -0.3272 | -1.9872 | -0.79805 | -0.63041 | 61.7248 | 0.26695 | 61.6286 | -0.028522 | 0.043657 | 61.5478 | 0.007721 | 61.3169 | 60.7479 | 59.308 | 62.2898 | 61.1322 | 59.4722 | 60.6613 | 60.8289 | 123.1842 | 61.7263 | 123.0879 | 61.4308 | 61.503 | 123.0072 | 61.4671 | 122.7762 | 61.6812 | 61.7171 | 61.5849 | 61.6209
4343.0625 | 123.3444 | -61.441 | 61.6928 | -0.77551 | -2.1239 | 0.70226 | -0.48745 | -2.033 | -0.90793 | -0.63041 | 61.734 | 0.27153 | 61.6744 | -0.023943 | 0.039079 | 61.5433 | 0.007721 | 61.3169 | 60.6655 | 59.3172 | 62.1433 | 60.9536 | 59.4081 | 60.5331 | 60.8106 | 123.175 | 61.7126 | 123.1154 | 61.4171 | 61.4801 | 122.9843 | 61.4488 | 122.7579 | 61.6949 | 61.7263 | 61.6353 | 61.6667
4344.0781 | 123.3307 | -61.4456 | 61.6699 | -0.74346 | -1.9636 | 0.72973 | -0.50118 | -1.9506 | -0.86214 | -0.016936 | 61.7248 | 0.27153 | 61.6469 | -0.03768 | 0.048236 | 61.5524 | 0.003143 | 61.3169 | 60.7022 | 59.482 | 62.1754 | 60.9444 | 59.495 | 60.5835 | 61.4287 | 123.1704 | 61.7171 | 123.0925 | 61.4079 | 61.4939 | 122.998 | 61.4488 | 122.7625 | 61.6766 | 61.7217 | 61.5987 | 61.6438
4345.0625 | 123.3627 | -61.4182 | 61.6699 | -0.79841 | -2.0277 | 0.61527 | -0.34551 | -2.0147 | -0.8713 | -0.094765 | 61.7202 | 0.27153 | 61.6332 | -0.03768 | 0.039079 | 61.5433 | 0.007721 | 61.326 | 60.6197 | 59.3904 | 62.0334 | 61.0726 | 59.4035 | 60.5469 | 61.3234 | 123.1384 | 61.6897 | 123.0513 | 61.3805 | 61.4572 | 122.9614 | 61.4259 | 122.7442 | 61.6812 | 61.7125 | 61.5941 | 61.6255
4346.0938 | 123.2986 | -61.4273 | 61.7203 | -0.84419 | -2.0644 | 0.54201 | -0.29973 | -2.033 | -0.99492 | -0.10392 | 61.7386 | 0.26237 | 61.6652 | -0.042259 | 0.034501 | 61.5478 | 0.003143 | 61.326 | 60.5831 | 59.3629 | 61.9693 | 61.1276 | 59.3943 | 60.4324 | 61.3234 | 123.1659 | 61.6897 | 123.0925 | 61.385 | 61.4618 | 122.9752 | 61.4305 | 122.7533 | 61.7041 | 61.7354 | 61.6307 | 61.6621
4347.0625 | 123.3856 | -61.4456 | 61.6837 | -0.91287 | -2.0918 | 0.72973 | -0.40045 | -2.152 | -0.99492 | 0.051737 | 61.7248 | 0.26695 | 61.6377 | -0.03768 | 0.052814 | 61.5478 | 0.003143 | 61.3352 | 60.5328 | 59.3538 | 62.1754 | 61.0452 | 59.2936 | 60.4507 | 61.4974 | 123.1704 | 61.7126 | 123.0834 | 61.4079 | 61.4984 | 122.9935 | 61.4488 | 122.7808 | 61.672 | 61.7217 | 61.5849 | 61.6346
4348.0938 | 123.4726 | -61.4456 | 61.6608 | -0.71599 | -1.9728 | 0.94951 | -0.43708 | -2.0559 | -0.92166 | 0.17993 | 61.7157 | 0.27611 | 61.6423 | -0.03768 | 0.039079 | 61.5478 | 0.003143 | 61.3398 | 60.7296 | 59.4728 | 62.3951 | 61.0085 | 59.3898 | 60.524 | 61.6255 | 123.1613 | 61.7217 | 123.0879 | 61.4079 | 61.4847 | 122.9935 | 61.4488 | 122.7854 | 61.6766 | 61.7125 | 61.6032 | 61.6392
4349.0625 | 123.4085 | -61.4456 | 61.6608 | -0.73889 | -1.9682 | 1.1372 | -0.3043 | -1.8727 | -0.8301 | 0.17077 | 61.7202 | 0.27153 | 61.6515 | -0.028522 | 0.043657 | 61.557 | 0.003143 | 61.3489 | 60.7067 | 59.4774 | 62.5828 | 61.1413 | 59.5729 | 60.6155 | 61.6164 | 123.1659 | 61.7171 | 123.0971 | 61.4171 | 61.4893 | 123.0026 | 61.4488 | 122.7945 | 61.6766 | 61.7171 | 61.6078 | 61.6483
4350.0625 | 123.3902 | -61.4456 | 61.647 | -0.5237 | -2.0415 | 1.1098 | -0.20358 | -1.9414 | -0.98576 | 0.23486 | 61.6973 | 0.26237 | 61.624 | -0.03768 | 0.043657 | 61.5616 | 0.003143 | 61.3443 | 60.9219 | 59.4042 | 62.5554 | 61.242 | 59.5042 | 60.4599 | 61.6805 | 123.143 | 61.708 | 123.0696 | 61.4079 | 61.4893 | 123.0072 | 61.4488 | 122.79 | 61.6537 | 61.6942 | 61.5804 | 61.6209
4351.1094 | 123.2712 | -61.4365 | 61.7065 | -0.74804 | -2.1697 | 0.93119 | -0.27683 | -1.9872 | -0.89419 | -0.54343 | 61.7294 | 0.26695 | 61.6561 | -0.03768 | 0.043657 | 61.5387 | 0.003143 | 61.3123 | 60.6884 | 59.2668 | 62.3677 | 61.1596 | 59.4493 | 60.5423 | 60.893 | 123.1659 | 61.7034 | 123.0925 | 61.3988 | 61.4801 | 122.9752 | 61.4396 | 122.7488 | 61.6857 | 61.7263 | 61.6124 | 61.6529
4352.0625 | 123.4222 | -61.3998 | 61.6608 | -0.9266 | -2.3345 | 0.63816 | -0.23105 | -2.0101 | -1.0682 | -0.55258 | 61.7386 | 0.27611 | 61.6698 | -0.03768 | 0.043657 | 61.5387 | -0.001436 | 61.3169 | 60.4732 | 59.0653 | 62.038 | 61.1688 | 59.3898 | 60.3317 | 60.8473 | 123.1384 | 61.6759 | 123.0696 | 61.3622 | 61.4435 | 122.9385 | 61.3984 | 122.7167 | 61.6949 | 61.74 | 61.6261 | 61.6712
4353.0781 | 123.3307 | -61.4273 | 61.702 | -0.87166 | -2.3391 | 0.5008 | -0.23105 | -2.1016 | -1.0911 | -0.021514 | 61.7248 | 0.27153 | 61.6377 | -0.03768 | 0.048236 | 61.5433 | 0.003143 | 61.326 | 60.5556 | 59.0882 | 61.9281 | 61.1963 | 59.3257 | 60.3362 | 61.4058 | 123.1521 | 61.6988 | 123.0651 | 61.3896 | 61.4755 | 122.9706 | 61.4305 | 122.7533 | 61.6766 | 61.7217 | 61.5895 | 61.6346
4354.0625 | 123.3719 | -61.4319 | 61.6791 | -0.98154 | -2.3253 | 0.78468 | -0.26768 | -2.0971 | -1.0315 | 0.001377 | 61.7248 | 0.26695 | 61.6652 | -0.033101 | 0.043657 | 61.5478 | 0.007721 | 61.3169 | 60.4503 | 59.1065 | 62.2166 | 61.1642 | 59.3348 | 60.4003 | 61.4333 | 123.1567 | 61.6988 | 123.0971 | 61.3988 | 61.4755 | 122.9797 | 61.4396 | 122.7488 | 61.6812 | 61.7171 | 61.6216 | 61.6575
4355.0781 | 123.2758 | -61.4365 | 61.7157 | -1.0548 | -2.4673 | 0.54201 | -0.28599 | -2.152 | -1.1185 | -0.076452 | 61.7294 | 0.27153 | 61.6606 | -0.033101 | 0.039079 | 61.5433 | 0.007721 | 61.3123 | 60.3817 | 58.9692 | 61.9785 | 61.1505 | 59.2845 | 60.3179 | 61.36 | 123.1659 | 61.708 | 123.0971 | 61.4034 | 61.4755 | 122.9797 | 61.4442 | 122.7488 | 61.6903 | 61.7217 | 61.6216 | 61.6529
4356.0625 | 123.381 | -61.409 | 61.647 | -1.0777 | -2.5085 | 0.71142 | -0.1349 | -2.1108 | -1.1689 | -0.58921 | 61.7386 | 0.26237 | 61.6423 | -0.03768 | 0.039079 | 61.5433 | 0.007721 | 61.3123 | 60.3313 | 58.9005 | 62.1204 | 61.2741 | 59.2982 | 60.2401 | 60.8198 | 123.1476 | 61.6714 | 123.0513 | 61.3713 | 61.4481 | 122.9523 | 61.4167 | 122.7213 | 61.6995 | 61.7308 | 61.6032 | 61.6346
4357.0781 | 123.2529 | -61.4502 | 61.7065 | -0.9907 | -2.3208 | 1.1372 | -0.62022 | -2.1474 | -1.0544 | 0.12041 | 61.734 | 0.26695 | 61.6652 | -0.033101 | 0.039079 | 61.5478 | 0.003143 | 61.3169 | 60.4595 | 59.1294 | 62.5874 | 60.83 | 59.3028 | 60.3958 | 61.5706 | 123.1842 | 61.7171 | 123.1154 | 61.4171 | 61.4893 | 122.998 | 61.4533 | 122.7671 | 61.6949 | 61.7308 | 61.6261 | 61.6621
4358.0625 | 123.3444 | -61.4273 | 61.6653 | -1.009 | -2.362 | 0.94035 | -0.57901 | -1.9872 | -1.0727 | 0.092941 | 61.7248 | 0.27153 | 61.6423 | -0.03768 | 0.039079 | 61.5478 | 0.003143 | 61.3169 | 60.4183 | 59.0653 | 62.3677 | 60.8483 | 59.4401 | 60.3546 | 61.5202 | 123.1521 | 61.6988 | 123.0696 | 61.3896 | 61.4664 | 122.9752 | 61.4305 | 122.7442 | 61.6857 | 61.7217 | 61.6032 | 61.6392
4359.0938 | 123.3765 | -61.4456 | 61.647 | -1.0273 | -2.3253 | 1.1464 | -0.45082 | -1.8315 | -1.0682 | -0.96004 | 61.7294 | 0.27153 | 61.6332 | -0.028522 | 0.043657 | 61.5387 | 0.012299 | 61.3077 | 60.4183 | 59.1203 | 62.592 | 60.9948 | 59.6141 | 60.3774 | 60.4856 | 123.175 | 61.7171 | 123.0788 | 61.4171 | 61.4893 | 122.9843 | 61.4579 | 122.7533 | 61.6857 | 61.7171 | 61.5895 | 61.6209
4360.0625 | 123.3856 | -61.441 | 61.6653 | -0.99528 | -2.481 | 1.0731 | -0.43708 | -1.7262 | -1.0361 | -1.0379 | 61.7431 | 0.27153 | 61.6698 | -0.03768 | 0.043657 | 61.5387 | 0.003143 | 61.3169 | 60.4458 | 58.96 | 62.5142 | 61.004 | 59.7148 | 60.4049 | 60.4032 | 123.1842 | 61.7126 | 123.1108 | 61.4034 | 61.4847 | 122.9797 | 61.4442 | 122.7579 | 61.6995 | 61.74 | 61.6261 | 61.6667
4361.0938 | 123.349 | -61.4182 | 61.7432 | -1.0594 | -2.5634 | 0.99529 | -0.50576 | -1.8773 | -1.0956 | -0.96462 | 61.7386 | 0.26695 | 61.6469 | -0.028522 | 0.048236 | 61.5341 | 0.007721 | 61.3169 | 60.3588 | 58.8547 | 62.4134 | 60.9124 | 59.5408 | 60.3225 | 60.4535 | 123.1567 | 61.6851 | 123.0651 | 61.3896 | 61.4664 | 122.9523 | 61.4259 | 122.735 | 61.6903 | 61.7308 | 61.5987 | 61.6392
4362.0625 | 123.3948 | -61.409 | 61.6425 | -1.0823 | -2.5039 | 0.88541 | -0.3684 | -1.8361 | -1.1231 | -0.87763 | 61.7386 | 0.26237 | 61.6469 | -0.033101 | 0.039079 | 61.5387 | 0.007721 | 61.3123 | 60.3267 | 58.9051 | 62.2944 | 61.0406 | 59.5729 | 60.2859 | 60.5314 | 123.1476 | 61.6714 | 123.0559 | 61.3759 | 61.4481 | 122.9477 | 61.4167 | 122.7213 | 61.6995 | 61.7308 | 61.6078 | 61.6392
4363.0781 | 123.3078 | -61.4456 | 61.7203 | -1.1006 | -2.3986 | 0.93577 | -0.47829 | -1.8499 | -1.1323 | -0.84101 | 61.7431 | 0.27611 | 61.679 | -0.03768 | 0.043657 | 61.5433 | 0.003143 | 61.3169 | 60.345 | 59.047 | 62.3814 | 60.9673 | 59.5958 | 60.3133 | 60.6046 | 123.1887 | 61.7217 | 123.1246 | 61.4079 | 61.4893 | 122.9889 | 61.4488 | 122.7625 | 61.6995 | 61.74 | 61.6353 | 61.6758
4364.0625 | 123.381 | -61.441 | 61.6699 | -1.0731 | -2.4215 | 0.74805 | -0.40045 | -1.7079 | -1.114 | -0.83185 | 61.734 | 0.27153 | 61.6377 | -0.03768 | 0.039079 | 61.5387 | 0.003143 | 61.3123 | 60.3679 | 59.0195 | 62.1891 | 61.0406 | 59.7331 | 60.3271 | 60.6092 | 123.175 | 61.7126 | 123.0788 | 61.4034 | 61.4801 | 122.9797 | 61.4442 | 122.7533 | 61.6949 | 61.7308 | 61.5987 | 61.6346
4365.0781 | 123.2986 | -61.4365 | 61.702 | -1.064 | -2.3666 | 0.59696 | -0.40503 | -1.6667 | -1.1094 | -0.86848 | 61.734 | 0.27611 | 61.6423 | -0.033101 | 0.039079 | 61.5387 | 0.003143 | 61.3123 | 60.3725 | 59.0699 | 62.0334 | 61.0314 | 59.7697 | 60.3271 | 60.568 | 123.1704 | 61.7126 | 123.0788 | 61.4034 | 61.4755 | 122.9752 | 61.4396 | 122.7488 | 61.6949 | 61.7308 | 61.6032 | 61.6392
4366.0625 | 123.3994 | -61.377 | 61.7203 | -1.1372 | -2.4352 | 0.52828 | -0.2631 | -1.8361 | -1.1735 | -0.95546 | 61.734 | 0.27611 | 61.6744 | -0.033101 | 0.039079 | 61.525 | 0.012299 | 61.3123 | 60.2397 | 58.9417 | 61.9052 | 61.1139 | 59.5408 | 60.2035 | 60.4215 | 123.1109 | 61.6531 | 123.0513 | 61.3439 | 61.416 | 122.9019 | 61.3893 | 122.6893 | 61.6949 | 61.7217 | 61.6353 | 61.6621
4367.0781 | 123.2666 | -61.4594 | 61.7294 | -1.1235 | -2.4856 | 0.48707 | -0.28141 | -1.9872 | -1.1597 | -0.32825 | 61.7386 | 0.27611 | 61.6744 | -0.028522 | 0.043657 | 61.5341 | 0.007721 | 61.3123 | 60.3359 | 58.9737 | 61.9464 | 61.1779 | 59.4722 | 60.2996 | 61.1311 | 123.1979 | 61.7355 | 123.1337 | 61.4308 | 61.503 | 122.9935 | 61.4671 | 122.7717 | 61.6949 | 61.7308 | 61.6307 | 61.6667
4368.0625 | 123.3444 | -61.4319 | 61.7065 | -1.0411 | -2.4536 | 0.55117 | -0.25394 | -1.946 | -1.0819 | -0.34199 | 61.7248 | 0.27153 | 61.6377 | -0.033101 | 0.043657 | 61.5387 | 0.007721 | 61.3169 | 60.3908 | 58.9783 | 61.9831 | 61.1779 | 59.4859 | 60.35 | 61.0899 | 123.1567 | 61.7034 | 123.0696 | 61.3988 | 61.4755 | 122.9706 | 61.4396 | 122.7488 | 61.6812 | 61.7171 | 61.5941 | 61.63
4369.0781 | 123.2849 | -61.4182 | 61.702 | -1.0731 | -2.4352 | 0.76178 | -0.21274 | -1.946 | -1.1185 | -1.134 | 61.7386 | 0.27153 | 61.6561 | -0.03768 | 0.043657 | 61.5341 | 0.007721 | 61.3077 | 60.345 | 58.9829 | 62.1799 | 61.2054 | 59.4722 | 60.2996 | 60.2841 | 123.1567 | 61.6897 | 123.0742 | 61.3805 | 61.4618 | 122.9523 | 61.4259 | 122.7259 | 61.6949 | 61.7308 | 61.6124 | 61.6483
4370.0625 | 123.3856 | -61.441 | 61.6699 | -1.0456 | -2.362 | 0.79841 | -0.17611 | -1.9048 | -1.0865 | -1.0699 | 61.7386 | 0.27153 | 61.6698 | -0.028522 | 0.043657 | 61.5341 | -0.001436 | 61.3077 | 60.3954 | 59.0791 | 62.2395 | 61.2649 | 59.5363 | 60.3546 | 60.3711 | 123.1796 | 61.7126 | 123.1108 | 61.4125 | 61.4847 | 122.9752 | 61.4396 | 122.7488 | 61.6949 | 61.74 | 61.6261 | 61.6712
4371.1094 | 123.2208 | -61.496 | 61.6608 | -1.1372 | -2.4215 | 0.81215 | -0.23105 | -1.9323 | -1.1872 | -0.96462 | 61.734 | 0.27153 | 61.6469 | -0.028522 | 0.039079 | 61.5341 | 0.012299 | 61.3031 | 60.3588 | 59.0745 | 62.3081 | 61.2649 | 59.5637 | 60.3088 | 60.5314 | 123.2299 | 61.7675 | 123.1429 | 61.4674 | 61.5351 | 123.0301 | 61.5083 | 122.7991 | 61.6949 | 61.7217 | 61.6078 | 61.6346
4372.0625 | 123.3856 | -61.4044 | 61.6974 | -1.2013 | -2.4078 | 0.80757 | -0.17153 | -1.9597 | -1.2742 | -1.1477 | 61.7386 | 0.27153 | 61.6606 | -0.033101 | 0.048236 | 61.5387 | 0.007721 | 61.3123 | 60.2031 | 58.9966 | 62.212 | 61.2329 | 59.4447 | 60.1302 | 60.2567 | 123.143 | 61.6759 | 123.0651 | 61.3713 | 61.4527 | 122.9431 | 61.4121 | 122.7167 | 61.6903 | 61.7308 | 61.6124 | 61.6529
4373.0781 | 123.3078 | -61.4273 | 61.6974 | -1.2059 | -2.4398 | 0.74805 | -0.098273 | -1.9323 | -1.2376 | -1.102 | 61.7477 | 0.27153 | 61.6744 | -0.033101 | 0.039079 | 61.5341 | 0.007721 | 61.3123 | 60.2214 | 58.9875 | 62.1754 | 61.329 | 59.495 | 60.1897 | 60.3253 | 123.175 | 61.6988 | 123.1017 | 61.3942 | 61.4664 | 122.9614 | 61.435 | 122.7396 | 61.7086 | 61.74 | 61.6353 | 61.6667
4374.0625 | 123.3444 | -61.3953 | 61.702 | -1.2242 | -2.4352 | 0.82588 | -0.35009 | -2.0284 | -1.2742 | -1.1386 | 61.7386 | 0.27611 | 61.6469 | -0.03768 | 0.039079 | 61.5295 | 0.007721 | 61.3169 | 60.1711 | 58.96 | 62.2211 | 61.0452 | 59.3669 | 60.1211 | 60.2567 | 123.1338 | 61.6714 | 123.0422 | 61.3576 | 61.4343 | 122.9248 | 61.403 | 122.7121 | 61.6995 | 61.7308 | 61.6078 | 61.6392
4375.0781 | 123.3307 | -61.4227 | 61.6928 | -1.1784 | -2.4307 | 0.49623 | -0.23105 | -1.9368 | -1.2238 | -1.102 | 61.734 | 0.27153 | 61.6744 | -0.033101 | 0.043657 | 61.5295 | 0.003143 | 61.3077 | 60.2443 | 58.9921 | 61.919 | 61.1917 | 59.4859 | 60.1989 | 60.3208 | 123.1567 | 61.6943 | 123.0971 | 61.3896 | 61.4664 | 122.9523 | 61.4259 | 122.7305 | 61.6903 | 61.7308 | 61.6307 | 61.6712
4376.0625 | 123.3994 | -61.409 | 61.7249 | -1.1876 | -2.4352 | 0.40923 | -0.093694 | -1.9277 | -1.2238 | -1.0058 | 61.7431 | 0.27153 | 61.6835 | -0.033101 | 0.048236 | 61.5387 | 0.007721 | 61.3169 | 60.2214 | 58.9738 | 61.8182 | 61.3153 | 59.4813 | 60.1852 | 60.4032 | 123.1521 | 61.6805 | 123.0925 | 61.3759 | 61.4572 | 122.9477 | 61.4167 | 122.7259 | 61.6949 | 61.7354 | 61.6353 | 61.6758
4377.0781 | 123.2666 | -61.4502 | 61.7249 | -1.2059 | -2.4581 | 0.56033 | -0.18069 | -1.9597 | -1.2513 | -0.8639 | 61.7477 | 0.28069 | 61.6469 | -0.028522 | 0.043657 | 61.5387 | 0.007721 | 61.3169 | 60.2443 | 58.9921 | 62.0105 | 61.2695 | 59.4905 | 60.1989 | 60.5863 | 123.1979 | 61.7309 | 123.0971 | 61.4217 | 61.4939 | 122.9889 | 61.4579 | 122.7671 | 61.7041 | 61.74 | 61.6032 | 61.6392
4378.0625 | 123.3902 | -61.4136 | 61.7111 | -1.1876 | -2.449 | 0.54201 | -0.35467 | -2.0238 | -1.2193 | -0.81354 | 61.7386 | 0.26695 | 61.6469 | -0.03768 | 0.039079 | 61.5387 | 0.003143 | 61.3077 | 60.226 | 58.9646 | 61.9556 | 61.0589 | 59.3898 | 60.1943 | 60.6 | 123.1521 | 61.6805 | 123.0605 | 61.3759 | 61.4527 | 122.9523 | 61.4167 | 122.7213 | 61.6995 | 61.7354 | 61.6078 | 61.6438
4379.0781 | 123.2574 | -61.4685 | 61.7386 | -1.1693 | -2.4902 | 0.43212 | -0.27683 | -1.9643 | -1.2055 | -0.78149 | 61.7386 | 0.27153 | 61.6835 | -0.03768 | 0.039079 | 61.5295 | -0.001436 | 61.3123 | 60.2993 | 58.9783 | 61.9006 | 61.1917 | 59.5042 | 60.263 | 60.687 | 123.2071 | 61.74 | 123.152 | 61.4308 | 61.5076 | 122.998 | 61.4671 | 122.7808 | 61.6995 | 61.74 | 61.6445 | 61.685
4380.0625 | 123.3627 | -61.409 | 61.6974 | -1.215 | -2.4993 | 0.17114 | -0.61106 | -1.9689 | -1.2513 | -0.95088 | 61.7569 | 0.27153 | 61.6881 | -0.033101 | 0.043657 | 61.525 | 0.007721 | 61.3077 | 60.194 | 58.9097 | 61.5801 | 60.7979 | 59.4401 | 60.1577 | 60.4581 | 123.1659 | 61.6805 | 123.0971 | 61.3759 | 61.4527 | 122.934 | 61.4167 | 122.7167 | 61.7132 | 61.7491 | 61.6445 | 61.6804
4381.1094 | 123.3032 | -61.4365 | 61.7111 | -1.2791 | -2.5863 | 0.001736 | -0.62938 | -2.0604 | -1.3154 | -1.0837 | 61.7569 | 0.27153 | 61.6744 | -0.028522 | 0.048236 | 61.5204 | 0.003143 | 61.2986 | 60.1573 | 58.8501 | 61.4382 | 60.8071 | 59.376 | 60.1211 | 60.3528 | 123.1933 | 61.708 | 123.1108 | 61.4079 | 61.4847 | 122.9568 | 61.4396 | 122.735 | 61.7086 | 61.7537 | 61.6261 | 61.6712
4382.0625 | 123.3902 | -61.3998 | 61.6928 | -1.2242 | -2.5131 | 0.21693 | -0.61564 | -2.0696 | -1.2605 | -1.2714 | 61.7477 | 0.27611 | 61.6561 | -0.033101 | 0.043657 | 61.5204 | 0.007721 | 61.3031 | 60.1756 | 58.8868 | 61.6168 | 60.7842 | 59.3302 | 60.1394 | 60.1285 | 123.1476 | 61.6759 | 123.0559 | 61.3667 | 61.4435 | 122.9202 | 61.4076 | 122.703 | 61.7041 | 61.74 | 61.6124 | 61.6483
4383.0938 | 123.4268 | -61.4136 | 61.6745 | -1.2242 | -2.4307 | 0.36345 | -0.45539 | -2.0467 | -1.2605 | -1.2851 | 61.7477 | 0.26695 | 61.6881 | -0.03768 | 0.039079 | 61.5295 | -0.001436 | 61.2986 | 60.1894 | 58.9829 | 61.777 | 60.9582 | 59.3669 | 60.1531 | 60.1285 | 123.1613 | 61.6805 | 123.1017 | 61.3759 | 61.4527 | 122.9431 | 61.4121 | 122.7121 | 61.7086 | 61.7491 | 61.649 | 61.6895
4384.0625 | 123.3582 | -61.4273 | 61.6745 | -1.2425 | -2.4444 | 0.4367 | -0.47829 | -2.0421 | -1.2834 | -1.0562 | 61.7431 | 0.26695 | 61.6927 | -0.03768 | 0.043657 | 61.525 | 0.003143 | 61.3031 | 60.1848 | 58.9829 | 61.864 | 60.949 | 59.3852 | 60.144 | 60.3711 | 123.1704 | 61.6943 | 123.12 | 61.3896 | 61.471 | 122.9523 | 61.4305 | 122.7305 | 61.6995 | 61.74 | 61.649 | 61.6895
4385.0781 | 123.262 | -61.441 | 61.7477 | -1.2883 | -2.4627 | 0.14825 | -0.33178 | -2.0375 | -1.3291 | -0.87763 | 61.7431 | 0.27611 | 61.6698 | -0.023943 | 0.043657 | 61.5295 | 0.007721 | 61.2894 | 60.1527 | 58.9783 | 61.5893 | 61.1093 | 59.4035 | 60.1119 | 60.5634 | 123.1842 | 61.7171 | 123.1108 | 61.4171 | 61.4847 | 122.9706 | 61.4488 | 122.7305 | 61.6995 | 61.7354 | 61.6261 | 61.6621
4386.0625 | 123.3948 | -61.3998 | 61.7249 | -1.3753 | -2.6138 | -0.04405 | -0.33636 | -2.184 | -1.4207 | -1.0928 | 61.7523 | 0.26695 | 61.6561 | -0.033101 | 0.043657 | 61.5158 | 0.012299 | 61.294 | 60.0246 | 58.786 | 61.3558 | 61.0635 | 59.2158 | 59.9791 | 60.307 | 123.1521 | 61.6668 | 123.0559 | 61.3667 | 61.4435 | 122.9156 | 61.4121 | 122.6938 | 61.7086 | 61.74 | 61.6124 | 61.6438
4387.0938 | 123.3261 | -61.4182 | 61.7111 | -1.4165 | -2.6504 | -0.039471 | -0.46455 | -2.445 | -1.4528 | -0.70366 | 61.7569 | 0.26695 | 61.6835 | -0.033101 | 0.039079 | 61.5112 | 0.007721 | 61.2986 | 60.0017 | 58.7677 | 61.3787 | 60.9536 | 58.9732 | 59.9654 | 60.7145 | 123.175 | 61.6851 | 123.1017 | 61.3851 | 61.4572 | 122.9294 | 61.4259 | 122.7167 | 61.7178 | 61.7491 | 61.6445 | 61.6758
4388.0625 | 123.3719 | -61.3998 | 61.7203 | -1.3432 | -2.6413 | 0.070415 | -0.44624 | -2.4358 | -1.3932 | -0.27789 | 61.7431 | 0.27153 | 61.6881 | -0.033101 | 0.043657 | 61.525 | 0.007721 | 61.2986 | 60.0566 | 58.7586 | 61.4703 | 60.9536 | 58.964 | 60.0066 | 61.122 | 123.143 | 61.6714 | 123.088 | 61.3667 | 61.4435 | 122.9248 | 61.4076 | 122.6984 | 61.6995 | 61.7354 | 61.6445 | 61.6804
4389.0781 | 123.2895 | -61.4182 | 61.7249 | -1.3387 | -2.6367 | 0.047522 | -0.40503 | -2.4038 | -1.3841 | -0.19091 | 61.7523 | 0.27611 | 61.6561 | -0.028522 | 0.043657 | 61.5204 | 0.007721 | 61.2986 | 60.0795 | 58.7814 | 61.4657 | 61.0131 | 59.0144 | 60.0341 | 61.2272 | 123.1704 | 61.6943 | 123.0742 | 61.3896 | 61.4618 | 122.9385 | 61.4259 | 122.7167 | 61.7086 | 61.7446 | 61.6124 | 61.6483
4390.0625 | 123.381 | -61.4182 | 61.6745 | -1.3203 | -2.5818 | -0.13104 | -0.33636 | -2.3122 | -1.3703 | -0.24127 | 61.7431 | 0.26237 | 61.6881 | -0.033101 | 0.039079 | 61.5295 | 0.007721 | 61.294 | 60.0978 | 58.8364 | 61.2871 | 61.0818 | 59.1059 | 60.0478 | 61.1769 | 123.1613 | 61.6805 | 123.1063 | 61.3851 | 61.4572 | 122.9477 | 61.4259 | 122.7121 | 61.7041 | 61.7354 | 61.649 | 61.6804
4391.0938 | 123.3444 | -61.3815 | 61.7386 | -1.2471 | -2.655 | -0.057786 | -0.29057 | -2.2207 | -1.2879 | -0.42439 | 61.7523 | 0.27153 | 61.6835 | -0.028522 | 0.039079 | 61.525 | 0.003143 | 61.3077 | 60.1344 | 58.7265 | 61.3237 | 61.091 | 59.1609 | 60.0936 | 60.9571 | 123.1338 | 61.6531 | 123.0651 | 61.353 | 61.4206 | 122.9065 | 61.3847 | 122.6893 | 61.7132 | 61.7491 | 61.6445 | 61.6804
4392.0625 | 123.3307 | -61.3953 | 61.7249 | -1.2929 | -2.623 | -0.039471 | -0.18069 | -2.2436 | -1.3337 | -1.0699 | 61.7431 | 0.26695 | 61.6561 | -0.033101 | 0.039079 | 61.525 | -0.001436 | 61.3031 | 60.1024 | 58.7723 | 61.3558 | 61.2146 | 59.1517 | 60.0615 | 60.3253 | 123.1384 | 61.6622 | 123.0513 | 61.3622 | 61.4343 | 122.9202 | 61.3938 | 122.6984 | 61.7041 | 61.7446 | 61.617 | 61.6575
4393.0781 | 123.2941 | -61.4319 | 61.702 | -1.2974 | -2.6367 | 0.23525 | -0.15779 | -2.2527 | -1.3337 | -1.0928 | 61.7477 | 0.27153 | 61.6835 | -0.028522 | 0.039079 | 61.5295 | 0.007721 | 61.3031 | 60.1344 | 58.7952 | 61.6671 | 61.2741 | 59.1792 | 60.0982 | 60.3391 | 123.1796 | 61.7034 | 123.1154 | 61.4034 | 61.471 | 122.9614 | 61.4396 | 122.735 | 61.7086 | 61.74 | 61.6445 | 61.6758
4394.0625 | 123.3398 | -61.3907 | 61.702 | -1.2837 | -2.6871 | 0.25356 | -0.15321 | -2.2115 | -1.3475 | -1.134 | 61.7477 | 0.27611 | 61.6698 | -0.03768 | 0.043657 | 61.5295 | 0.003143 | 61.3169 | 60.107 | 58.7036 | 61.6442 | 61.2375 | 59.1792 | 60.0432 | 60.2567 | 123.1384 | 61.6668 | 123.0605 | 61.353 | 61.4343 | 122.9202 | 61.3938 | 122.7076 | 61.7041 | 61.7446 | 61.6261 | 61.6667
4395.0938 | 123.2712 | -61.4456 | 61.7111 | -1.1921 | -2.5039 | 0.95409 | -0.093694 | -2.1566 | -1.2238 | -1.0928 | 61.7386 | 0.27611 | 61.6561 | -0.033101 | 0.043657 | 61.5387 | -0.001436 | 61.326 | 60.2535 | 58.9417 | 62.3997 | 61.3519 | 59.289 | 60.2218 | 60.3528 | 123.1842 | 61.7217 | 123.1017 | 61.4125 | 61.4893 | 122.9843 | 61.4442 | 122.7717 | 61.6949 | 61.74 | 61.6124 | 61.6575
4396.0625 | 123.3994 | -61.3586 | 61.6974 | -1.2242 | -2.5955 | 1.064 | -0.199 | -2.326 | -1.265 | -1.0608 | 61.7523 | 0.27611 | 61.679 | -0.033101 | 0.048236 | 61.5295 | 0.003143 | 61.3306 | 60.1344 | 58.7631 | 62.4226 | 61.1596 | 59.0327 | 60.0936 | 60.2979 | 123.1109 | 61.6347 | 123.0376 | 61.3255 | 61.4069 | 122.8882 | 61.3618 | 122.6893 | 61.7041 | 61.7491 | 61.6307 | 61.6758
4397.0938 | 123.2895 | -61.4502 | 61.7294 | -1.2608 | -2.6642 | 0.87625 | -0.22647 | -2.3763 | -1.3017 | -1.1386 | 61.734 | 0.26695 | 61.6606 | -0.03768 | 0.039079 | 61.525 | 0.007721 | 61.3215 | 60.1894 | 58.786 | 62.3264 | 61.2237 | 59.0739 | 60.1485 | 60.3116 | 123.1842 | 61.7171 | 123.1108 | 61.4125 | 61.4893 | 122.9752 | 61.4579 | 122.7717 | 61.6949 | 61.7263 | 61.6216 | 61.6529
4398.0625 | 123.3673 | -61.4182 | 61.6791 | -1.2562 | -2.6504 | 0.7801 | -0.093694 | -2.2848 | -1.2925 | -1.3767 | 61.7477 | 0.27153 | 61.6561 | -0.033101 | 0.043657 | 61.525 | 0.007721 | 61.3077 | 60.1619 | 58.7677 | 62.1983 | 61.3245 | 59.1334 | 60.1256 | 60.0415 | 123.1659 | 61.6897 | 123.0742 | 61.3851 | 61.4618 | 122.9431 | 61.4259 | 122.7259 | 61.7041 | 61.74 | 61.6124 | 61.6483
4399.0781 | 123.3215 | -61.409 | 61.734 | -1.2608 | -2.655 | 0.74805 | -0.25852 | -2.2436 | -1.3062 | -1.4591 | 61.7569 | 0.27153 | 61.6927 | -0.033101 | 0.034501 | 61.525 | 0.003143 | 61.3077 | 60.1482 | 58.754 | 62.157 | 61.1505 | 59.1654 | 60.1028 | 59.9499 | 123.1659 | 61.6805 | 123.1017 | 61.3759 | 61.4435 | 122.934 | 61.4121 | 122.7167 | 61.7224 | 61.7537 | 61.6582 | 61.6895
4400.0625 | 123.381 | -61.4227 | 61.6837 | -1.183 | -2.6321 | 0.77094 | -0.098273 | -1.978 | -1.2238 | -1.6285 | 61.7477 | 0.27153 | 61.6469 | -0.03768 | 0.043657 | 61.5295 | -0.001436 | 61.2986 | 60.2397 | 58.7906 | 62.1937 | 61.3245 | 59.4447 | 60.1989 | 59.7943 | 123.1704 | 61.6943 | 123.0696 | 61.385 | 61.4664 | 122.9523 | 61.4213 | 122.7213 | 61.7041 | 61.7491 | 61.6032 | 61.6483
4401.1094 | 123.381 | -61.4502 | 61.6928 | -1.1647 | -2.6276 | 0.20319 | -0.052488 | -1.9048 | -1.1964 | -1.5644 | 61.7431 | 0.28069 | 61.6835 | -0.03768 | 0.039079 | 61.525 | 0.003143 | 61.2986 | 60.2855 | 58.8226 | 61.6534 | 61.3977 | 59.5454 | 60.2538 | 59.8858 | 123.1933 | 61.7309 | 123.1337 | 61.4125 | 61.4893 | 122.9752 | 61.4533 | 122.7488 | 61.7041 | 61.74 | 61.6445 | 61.6804
4402.0625 | 123.3856 | -61.409 | 61.6653 | -1.1006 | -2.6047 | 0.15283 | 0.029925 | -1.8636 | -1.1506 | -1.4682 | 61.7431 | 0.26695 | 61.6835 | -0.033101 | 0.052814 | 61.5204 | 0.007721 | 61.3077 | 60.3084 | 58.8043 | 61.5618 | 61.4389 | 59.5454 | 60.2584 | 59.9408 | 123.1521 | 61.6759 | 123.0925 | 61.3759 | 61.4618 | 122.9294 | 61.4167 | 122.7167 | 61.6903 | 61.7354 | 61.6307 | 61.6758
4403.0938 | 123.1934 | -61.4502 | 61.6653 | -1.2562 | -2.6962 | 0.08873 | -0.11201 | -2.1566 | -1.2971 | -1.839 | 61.7477 | 0.27153 | 61.6561 | -0.03768 | 0.043657 | 61.5204 | 0.007721 | 61.3031 | 60.194 | 58.754 | 61.5389 | 61.3382 | 59.2936 | 60.1531 | 59.6111 | 123.1979 | 61.7217 | 123.1063 | 61.4125 | 61.4939 | 122.9706 | 61.4579 | 122.7533 | 61.7041 | 61.74 | 61.6124 | 61.6483
4404.0625 | 123.3948 | -61.3724 | 61.6928 | -1.2791 | -2.71 | -0.053207 | -0.17611 | -2.2573 | -1.3154 | -1.7658 | 61.7569 | 0.26237 | 61.6927 | -0.03768 | 0.039079 | 61.5204 | 0.003143 | 61.2894 | 60.0932 | 58.6624 | 61.3192 | 61.1963 | 59.1151 | 60.057 | 59.6066 | 123.1292 | 61.6347 | 123.0651 | 61.3347 | 61.4115 | 122.8928 | 61.3755 | 122.6618 | 61.7178 | 61.7537 | 61.6536 | 61.6895
4405.0781 | 123.3078 | -61.409 | 61.7706 | -1.2517 | -2.7237 | 0.19404 | -0.21731 | -2.3122 | -1.3017 | -1.8482 | 61.7614 | 0.27153 | 61.6835 | -0.03768 | 0.039079 | 61.5158 | -0.001436 | 61.2986 | 60.1573 | 58.6853 | 61.603 | 61.1917 | 59.0968 | 60.1073 | 59.5608 | 123.1704 | 61.6805 | 123.0925 | 61.3713 | 61.4481 | 122.9248 | 61.4076 | 122.7076 | 61.7224 | 61.7629 | 61.6445 | 61.685
4406.0625 | 123.2529 | -61.4319 | 61.7432 | -1.2196 | -2.6321 | 0.33597 | -0.12116 | -2.2527 | -1.2605 | -1.8162 | 61.7431 | 0.27153 | 61.6652 | -0.033101 | 0.039079 | 61.5158 | -0.006014 | 61.2986 | 60.2123 | 58.7998 | 61.7679 | 61.3107 | 59.1792 | 60.1714 | 59.6157 | 123.175 | 61.7034 | 123.0971 | 61.3988 | 61.471 | 122.9477 | 61.4259 | 122.7305 | 61.7041 | 61.7491 | 61.6261 | 61.6712
4407.0938 | 123.2986 | -61.4365 | 61.7523 | -1.2105 | -2.6962 | 0.36802 | -0.11201 | -2.2069 | -1.2422 | -1.8116 | 61.7569 | 0.27611 | 61.7018 | -0.03768 | 0.052814 | 61.5204 | 0.003143 | 61.2894 | 60.226 | 58.7402 | 61.8045 | 61.3245 | 59.2295 | 60.1943 | 59.6249 | 123.1933 | 61.7126 | 123.1383 | 61.3988 | 61.4893 | 122.9568 | 61.4396 | 122.7259 | 61.7041 | 61.7537 | 61.649 | 61.6987
4408.0625 | 123.4314 | -61.4044 | 61.7065 | -1.2059 | -2.7146 | 0.3955 | -0.084537 | -2.2252 | -1.2467 | -1.688 | 61.7523 | 0.27611 | 61.6561 | -0.03768 | 0.043657 | 61.525 | 0.012299 | 61.2894 | 60.1985 | 58.6899 | 61.7999 | 61.3199 | 59.1792 | 60.1577 | 59.7164 | 123.1567 | 61.6805 | 123.0605 | 61.3667 | 61.4481 | 122.9294 | 61.4167 | 122.6938 | 61.7086 | 61.74 | 61.6124 | 61.6438
4409.0781 | 123.3261 | -61.4227 | 61.734 | -1.215 | -2.6001 | 0.88083 | 0.057396 | -2.152 | -1.2467 | -1.308 | 61.7477 | 0.27611 | 61.6606 | -0.028522 | 0.043657 | 61.525 | 0.007721 | 61.3077 | 60.2077 | 58.8226 | 62.3036 | 61.4801 | 59.2707 | 60.176 | 60.1147 | 123.1704 | 61.6988 | 123.0834 | 61.3942 | 61.4664 | 122.9477 | 61.4304 | 122.7305 | 61.7041 | 61.74 | 61.617 | 61.6529
4410.0625 | 123.4039 | -61.4273 | 61.6791 | -1.1097 | -2.4536 | 1.0914 | 0.25427 | -1.9139 | -1.146 | -1.2164 | 61.7386 | 0.26695 | 61.6744 | -0.033101 | 0.039079 | 61.5341 | 0.007721 | 61.3077 | 60.3176 | 58.9737 | 62.5188 | 61.6816 | 59.5134 | 60.2813 | 60.2109 | 123.1659 | 61.6943 | 123.1017 | 61.3942 | 61.4664 | 122.9614 | 61.435 | 122.735 | 61.6995 | 61.7308 | 61.6353 | 61.6667
4411.1094 | 123.349 | -61.4227 | 61.6837 | -1.0502 | -2.4856 | 1.1647 | 0.34584 | -1.8224 | -1.0819 | -0.98751 | 61.7248 | 0.26695 | 61.6286 | -0.03768 | 0.043657 | 61.5478 | 0.007721 | 61.326 | 60.3725 | 58.9371 | 62.5874 | 61.7686 | 59.6003 | 60.3408 | 60.4352 | 123.1475 | 61.6897 | 123.0513 | 61.385 | 61.4664 | 122.9706 | 61.4304 | 122.7488 | 61.6812 | 61.7171 | 61.5849 | 61.6209
4412.0625 | 123.3902 | -61.4594 | 61.6562 | -1.0502 | -2.5589 | 1.2013 | 0.28632 | -1.8636 | -1.1048 | -0.98293 | 61.7248 | 0.27611 | 61.6744 | -0.033101 | 0.039079 | 61.5433 | 0.007721 | 61.3169 | 60.4091 | 58.9005 | 62.6607 | 61.7457 | 59.5958 | 60.3546 | 60.4764 | 123.1842 | 61.7355 | 123.1337 | 61.4262 | 61.4984 | 123.0026 | 61.4671 | 122.7762 | 61.6857 | 61.7171 | 61.6353 | 61.6667
4413.0781 | 123.3398 | -61.4182 | 61.6974 | -1.1235 | -2.6092 | 1.2471 | 0.23138 | -1.9506 | -1.1735 | -0.60752 | 61.7294 | 0.27611 | 61.6698 | -0.033101 | 0.039079 | 61.5433 | 0.012299 | 61.326 | 60.2947 | 58.8089 | 62.6653 | 61.6495 | 59.4676 | 60.2447 | 60.8106 | 123.1475 | 61.6943 | 123.088 | 61.3851 | 61.4572 | 122.9614 | 61.4305 | 122.7442 | 61.6903 | 61.7171 | 61.6307 | 61.6575
4414.0625 | 123.3765 | -61.4182 | 61.6516 | -1.1052 | -2.5589 | 1.2059 | 0.30463 | -1.7217 | -1.1506 | -0.5068 | 61.7157 | 0.26695 | 61.6286 | -0.028522 | 0.048236 | 61.5478 | 0.003143 | 61.326 | 60.313 | 58.8593 | 62.6241 | 61.7228 | 59.6965 | 60.2676 | 60.9114 | 123.1338 | 61.6851 | 123.0467 | 61.3896 | 61.4664 | 122.966 | 61.4213 | 122.7442 | 61.6674 | 61.7125 | 61.5804 | 61.6255
4415.0781 | 123.3353 | -61.4182 | 61.734 | -1.1555 | -2.6459 | 1.0045 | 0.19475 | -2.0147 | -1.2101 | -0.88221 | 61.734 | 0.27611 | 61.6744 | -0.03768 | 0.039079 | 61.5341 | 0.003143 | 61.3123 | 60.2626 | 58.7723 | 62.4226 | 61.6129 | 59.4035 | 60.2081 | 60.5359 | 123.1521 | 61.6943 | 123.0925 | 61.3805 | 61.4572 | 122.9523 | 61.4213 | 122.7305 | 61.6949 | 61.7308 | 61.6353 | 61.6712
4416.0625 | 123.3215 | -61.4456 | 61.6928 | -1.1509 | -2.7878 | 0.6931 | -0.28141 | -2.0742 | -1.1735 | -0.93715 | 61.7386 | 0.27153 | 61.6469 | -0.033101 | 0.039079 | 61.5295 | 0.007721 | 61.3031 | 60.2947 | 58.6578 | 62.1387 | 61.1642 | 59.3714 | 60.2721 | 60.5085 | 123.1842 | 61.7171 | 123.0925 | 61.4125 | 61.4847 | 122.9752 | 61.4533 | 122.7488 | 61.6995 | 61.7308 | 61.6078 | 61.6392
4417.0938 | 123.3444 | -61.409 | 61.7249 | -1.0456 | -3.058 | 1.1647 | -0.061645 | -1.8361 | -1.0865 | -1.0974 | 61.7523 | 0.28069 | 61.6652 | -0.03768 | 0.043657 | 61.5341 | 0.003143 | 61.3123 | 60.3634 | 58.351 | 62.5737 | 61.3474 | 59.5729 | 60.3225 | 60.3116 | 123.1613 | 61.6897 | 123.0742 | 61.3713 | 61.4527 | 122.9431 | 61.4121 | 122.7213 | 61.7086 | 61.7491 | 61.6216 | 61.6621
4418.0625 | 123.3032 | -61.4319 | 61.7203 | -1.0227 | -2.9984 | 0.79383 | -0.17153 | -1.8224 | -1.0727 | -1.2118 | 61.7477 | 0.26237 | 61.6698 | -0.03768 | 0.039079 | 61.5295 | 0.003143 | 61.3123 | 60.4091 | 58.4334 | 62.2257 | 61.2604 | 59.6095 | 60.3591 | 60.22 | 123.1796 | 61.6943 | 123.1017 | 61.3942 | 61.471 | 122.9614 | 61.435 | 122.7442 | 61.7086 | 61.7446 | 61.6307 | 61.6667
4419.0625 | 123.3536 | -61.4273 | 61.734 | -1.0456 | -2.9343 | 0.74347 | -0.20358 | -2.0009 | -1.0819 | -1.3721 | 61.7386 | 0.27153 | 61.6698 | -0.03768 | 0.052814 | 61.5295 | 0.007721 | 61.3031 | 60.3817 | 58.493 | 62.1708 | 61.2237 | 59.4264 | 60.3454 | 60.0552 | 123.1659 | 61.6988 | 123.0971 | 61.3896 | 61.4801 | 122.9568 | 61.435 | 122.7305 | 61.6857 | 61.7308 | 61.617 | 61.6621
4420.0781 | 123.2712 | -61.3998 | 61.7477 | -0.99528 | -2.8428 | 1.0869 | -0.07538 | -1.9872 | -1.0407 | -1.2942 | 61.7386 | 0.27611 | 61.679 | -0.033101 | 0.043657 | 61.5341 | 0.003143 | 61.3077 | 60.4046 | 58.5571 | 62.4867 | 61.3245 | 59.4126 | 60.3591 | 60.1056 | 123.1384 | 61.6759 | 123.0788 | 61.3667 | 61.4435 | 122.934 | 61.403 | 122.7076 | 61.6949 | 61.7354 | 61.6353 | 61.6758
4421.0625 | 123.3994 | -61.4273 | 61.6837 | -0.87166 | -2.6504 | 1.3616 | 0.34126 | -1.4836 | -0.90335 | -0.96462 | 61.7111 | 0.28069 | 61.6194 | -0.033101 | 0.039079 | 61.5478 | 0.012299 | 61.326 | 60.5556 | 58.7769 | 62.7889 | 61.7686 | 59.9437 | 60.524 | 60.4627 | 123.1384 | 61.708 | 123.0467 | 61.3942 | 61.4664 | 122.9752 | 61.4396 | 122.7533 | 61.672 | 61.6988 | 61.5804 | 61.6071
4422.0938 | 123.2941 | -61.4777 | 61.7294 | -0.74804 | -2.2384 | 1.4532 | 0.49693 | -1.1128 | -0.79347 | -0.70366 | 61.7157 | 0.27153 | 61.6515 | -0.028522 | 0.052814 | 61.5707 | 0.003143 | 61.3443 | 60.7296 | 59.2393 | 62.9308 | 61.9746 | 60.3649 | 60.6842 | 60.774 | 123.1933 | 61.7492 | 123.1291 | 61.4491 | 61.5305 | 123.0484 | 61.4808 | 122.822 | 61.6628 | 61.7125 | 61.5987 | 61.6483
4423.0625 | 123.2483 | -61.5189 | 61.7157 | -0.77551 | -2.1285 | 1.5493 | 0.50609 | -1.0899 | -0.80262 | -0.7586 | 61.7065 | 0.27153 | 61.6194 | -0.03768 | 0.039079 | 61.5662 | 0.003143 | 61.3443 | 60.7433 | 59.3904 | 63.0682 | 62.0249 | 60.4289 | 60.7162 | 60.7603 | 123.2254 | 61.7904 | 123.1383 | 61.4812 | 61.5579 | 123.085 | 61.522 | 122.8632 | 61.6674 | 61.7034 | 61.5804 | 61.6163
4424.0781 | 123.3124 | -61.4502 | 61.7157 | -0.83503 | -2.5039 | 1.4623 | 0.40994 | -1.1357 | -0.8713 | -0.95546 | 61.7111 | 0.27611 | 61.6332 | -0.042259 | 0.048236 | 61.5662 | 0.003143 | 61.3398 | 60.6152 | 58.9463 | 62.9125 | 61.8601 | 60.3145 | 60.5789 | 60.4947 | 123.1613 | 61.7263 | 123.0834 | 61.4079 | 61.4984 | 123.0164 | 61.4533 | 122.79 | 61.6628 | 61.7079 | 61.5849 | 61.63
4425.0625 | 123.3307 | -61.4456 | 61.7203 | -0.89913 | -2.6367 | 1.3341 | 0.355 | -1.1677 | -0.96287 | -0.90968 | 61.7248 | 0.27611 | 61.6561 | -0.03768 | 0.043657 | 61.5524 | 0.012299 | 61.3398 | 60.5465 | 58.8089 | 62.7797 | 61.8006 | 60.2779 | 60.4828 | 60.5359 | 123.1704 | 61.7217 | 123.1017 | 61.4079 | 61.4893 | 122.998 | 61.4579 | 122.7854 | 61.6812 | 61.7125 | 61.6124 | 61.6438
4426.0938 | 123.4268 | -61.4273 | 61.7111 | -0.9907 | -2.8565 | 1.1235 | 0.69381 | -1.566 | -1.0224 | -0.68077 | 61.7248 | 0.27153 | 61.6377 | -0.03768 | 0.048236 | 61.5478 | 0.012299 | 61.326 | 60.4366 | 58.5708 | 62.5508 | 62.1211 | 59.8613 | 60.4049 | 60.7465 | 123.1521 | 61.6988 | 123.0651 | 61.3896 | 61.4755 | 122.9752 | 61.4396 | 122.7533 | 61.6766 | 61.7125 | 61.5895 | 61.6255
4427.0625 | 123.2986 | -61.4822 | 61.7065 | -0.96323 | -2.9298 | 1.151 | 0.7808 | -1.6347 | -0.99492 | -0.74486 | 61.7248 | 0.27153 | 61.6652 | -0.033101 | 0.043657 | 61.557 | 0.003143 | 61.326 | 60.519 | 58.5525 | 62.6332 | 62.263 | 59.8475 | 60.4873 | 60.7374 | 123.2071 | 61.7538 | 123.1475 | 61.4491 | 61.5259 | 123.0392 | 61.4854 | 122.8083 | 61.6812 | 61.7217 | 61.6216 | 61.6621
4428.0625 | 123.4497 | -61.409 | 61.6699 | -1.0227 | -2.9435 | 1.0731 | 0.69839 | -1.7217 | -1.059 | -0.80438 | 61.7248 | 0.27153 | 61.6377 | -0.033101 | 0.043657 | 61.5433 | 0.003143 | 61.3215 | 60.3863 | 58.4655 | 62.4821 | 62.1074 | 59.6873 | 60.35 | 60.6046 | 123.1338 | 61.6805 | 123.0467 | 61.3759 | 61.4527 | 122.9523 | 61.4121 | 122.7305 | 61.6812 | 61.7217 | 61.5941 | 61.6346
4429.0625 | 123.2941 | -61.4365 | 61.7157 | -1.0731 | -2.8702 | 0.81215 | 0.68465 | -1.5935 | -1.1048 | -0.59379 | 61.7294 | 0.27153 | 61.6652 | -0.03768 | 0.052814 | 61.5478 | 0.003143 | 61.3443 | 60.3634 | 58.5662 | 62.2486 | 62.1211 | 59.843 | 60.3317 | 60.8427 | 123.1659 | 61.708 | 123.1017 | 61.3988 | 61.4893 | 122.9843 | 61.4396 | 122.7808 | 61.6766 | 61.7263 | 61.6124 | 61.6621
4430.0781 | 123.2941 | -61.4273 | 61.7432 | -1.0868 | -2.7787 | 0.72058 | 0.56103 | -1.772 | -1.1231 | -0.77691 | 61.7294 | 0.27153 | 61.6423 | -0.028522 | 0.048236 | 61.5387 | 0.003143 | 61.3306 | 60.3405 | 58.6487 | 62.1479 | 61.9883 | 59.6553 | 60.3042 | 60.6504 | 123.1567 | 61.6988 | 123.0696 | 61.3988 | 61.4755 | 122.966 | 61.4305 | 122.7579 | 61.6812 | 61.7263 | 61.5941 | 61.6392
4431.0625 | 123.4085 | -61.4044 | 61.7157 | -1.0456 | -2.916 | 0.66105 | 0.67549 | -1.7675 | -1.0865 | -0.93257 | 61.7386 | 0.27153 | 61.6698 | -0.033101 | 0.043657 | 61.5433 | 0.012299 | 61.3306 | 60.3588 | 58.4884 | 62.0655 | 62.0799 | 59.637 | 60.3179 | 60.4718 | 123.143 | 61.6759 | 123.0742 | 61.3713 | 61.4481 | 122.9477 | 61.4167 | 122.735 | 61.6949 | 61.7263 | 61.6261 | 61.6575
4432.0938 | 123.2849 | -61.4273 | 61.7432 | -1.1006 | -2.9298 | 0.68395 | 0.47862 | -1.8407 | -1.1414 | -0.97377 | 61.734 | 0.27153 | 61.6423 | -0.028522 | 0.048236 | 61.5341 | 0.003143 | 61.3306 | 60.3267 | 58.4976 | 62.1113 | 61.9059 | 59.5866 | 60.2859 | 60.4535 | 123.1613 | 61.6988 | 123.0696 | 61.3988 | 61.4755 | 122.9614 | 61.4305 | 122.7579 | 61.6857 | 61.7308 | 61.5941 | 61.6392
4433.0625 | 123.3582 | -61.4136 | 61.7523 | -1.1647 | -2.9069 | 0.5237 | 0.32295 | -1.9735 | -1.2101 | -1.0608 | 61.7523 | 0.27153 | 61.6835 | -0.033101 | 0.043657 | 61.5387 | -0.001436 | 61.3306 | 60.2489 | 58.5067 | 61.9373 | 61.7365 | 59.4401 | 60.2035 | 60.3528 | 123.1659 | 61.6851 | 123.0971 | 61.3805 | 61.4572 | 122.9523 | 61.4121 | 122.7442 | 61.7086 | 61.7537 | 61.6399 | 61.685
4434.0781 | 123.4589 | -61.377 | 61.7615 | -1.0685 | -2.8702 | 0.71142 | 0.36416 | -1.9918 | -1.114 | -1.0608 | 61.734 | 0.27611 | 61.6515 | -0.033101 | 0.039079 | 61.5341 | 0.003143 | 61.3215 | 60.3084 | 58.5067 | 62.0884 | 61.7411 | 59.3852 | 60.263 | 60.3162 | 123.1109 | 61.6531 | 123.0284 | 61.3439 | 61.416 | 122.9111 | 61.3801 | 122.6984 | 61.6949 | 61.7308 | 61.6124 | 61.6483
4435.0625 | 123.3215 | -61.4319 | 61.702 | -1.0319 | -2.8199 | 0.88541 | 0.54272 | -1.9597 | -1.0682 | -1.1111 | 61.7386 | 0.27611 | 61.6698 | -0.03768 | 0.048236 | 61.5433 | 0.007721 | 61.3352 | 60.4 | 58.612 | 62.3173 | 61.9746 | 59.4722 | 60.3637 | 60.3208 | 123.1704 | 61.708 | 123.1017 | 61.3942 | 61.4801 | 122.9752 | 61.4396 | 122.7671 | 61.6903 | 61.7308 | 61.6216 | 61.6621
4436.0938 | 123.3353 | -61.4319 | 61.6882 | -1.0502 | -2.8748 | 0.86709 | 0.50609 | -2.1154 | -1.1048 | -1.1615 | 61.7386 | 0.27153 | 61.6377 | -0.03768 | 0.034501 | 61.5433 | 0.003143 | 61.3123 | 60.3817 | 58.5571 | 62.299 | 61.938 | 59.3165 | 60.3271 | 60.2704 | 123.1704 | 61.7034 | 123.0696 | 61.3942 | 61.4664 | 122.9752 | 61.435 | 122.7442 | 61.7041 | 61.7354 | 61.6032 | 61.6346
4437.0625 | 123.317 | -61.4319 | 61.7477 | -1.096 | -2.7741 | 0.65648 | 0.66176 | -1.9048 | -1.1414 | -1.1294 | 61.7523 | 0.27153 | 61.6835 | -0.033101 | 0.052814 | 61.5341 | 0.007721 | 61.3215 | 60.3359 | 58.6578 | 62.0884 | 62.0936 | 59.5271 | 60.2905 | 60.3025 | 123.1842 | 61.7034 | 123.1154 | 61.3988 | 61.4847 | 122.966 | 61.4396 | 122.7533 | 61.6995 | 61.7446 | 61.6307 | 61.6758
4438.0625 | 123.2803 | -61.4365 | 61.7432 | -1.0914 | -2.8244 | 0.46875 | 0.57019 | -1.7537 | -1.1414 | -1.2027 | 61.7294 | 0.27153 | 61.6515 | -0.03768 | 0.052814 | 61.5433 | -0.001436 | 61.3215 | 60.345 | 58.612 | 61.9052 | 62.0066 | 59.6827 | 60.295 | 60.2338 | 123.1659 | 61.708 | 123.0879 | 61.3988 | 61.4893 | 122.9797 | 61.435 | 122.7579 | 61.6766 | 61.7308 | 61.5987 | 61.6529
4439.0938 | 123.317 | -61.4319 | 61.7615 | -1.1509 | -2.8702 | 0.26272 | 0.17644 | -1.827 | -1.1872 | -1.2576 | 61.7477 | 0.27611 | 61.6881 | -0.033101 | 0.039079 | 61.5295 | 0.003143 | 61.3077 | 60.2809 | 58.5617 | 61.6946 | 61.6083 | 59.6049 | 60.2447 | 60.1743 | 123.1796 | 61.708 | 123.12 | 61.3988 | 61.471 | 122.9614 | 61.435 | 122.7396 | 61.7086 | 61.7446 | 61.649 | 61.685
4440.0625 | 123.3215 | -61.4365 | 61.7432 | -1.1235 | -3.003 | 0.45044 | 0.17186 | -1.827 | -1.1506 | -1.3904 | 61.7431 | 0.27611 | 61.6606 | -0.03768 | 0.048236 | 61.5295 | 0.007721 | 61.3077 | 60.313 | 58.4334 | 61.8869 | 61.6083 | 59.6095 | 60.2859 | 60.0461 | 123.1796 | 61.7126 | 123.0971 | 61.3988 | 61.4847 | 122.966 | 61.4442 | 122.7442 | 61.6949 | 61.7354 | 61.6124 | 61.6529
4441.0938 | 123.4039 | -61.4319 | 61.6882 | -1.0685 | -3.0488 | 0.36345 | 0.13523 | -1.6942 | -1.1002 | -1.1615 | 61.7431 | 0.27153 | 61.6835 | -0.03768 | 0.043657 | 61.5341 | 0.007721 | 61.3077 | 60.3634 | 58.3831 | 61.7953 | 61.5671 | 59.7377 | 60.3317 | 60.2704 | 123.175 | 61.7034 | 123.1154 | 61.3942 | 61.4755 | 122.966 | 61.4396 | 122.7396 | 61.6995 | 61.7354 | 61.6399 | 61.6758
4442.0625 | 123.3307 | -61.3907 | 61.7386 | -1.0823 | -3.0122 | 0.26272 | 0.27716 | -1.7537 | -1.1277 | -1.0516 | 61.7386 | 0.28069 | 61.679 | -0.028522 | 0.043657 | 61.5295 | 0.003143 | 61.3169 | 60.3084 | 58.3785 | 61.6534 | 61.6679 | 59.637 | 60.263 | 60.3391 | 123.1292 | 61.6714 | 123.0696 | 61.3622 | 61.4343 | 122.9202 | 61.3938 | 122.7076 | 61.6949 | 61.7354 | 61.6353 | 61.6758
4443.0625 | 123.3078 | -61.4273 | 61.7203 | -0.98154 | -2.8977 | 0.49623 | 0.5244 | -1.7812 | -1.0315 | -0.99209 | 61.734 | 0.27153 | 61.6332 | -0.033101 | 0.039079 | 61.5341 | 0.012299 | 61.3169 | 60.4458 | 58.5296 | 61.9235 | 61.9517 | 59.6461 | 60.3958 | 60.4352 | 123.1613 | 61.6988 | 123.0605 | 61.3942 | 61.4664 | 122.9614 | 61.4396 | 122.7442 | 61.6949 | 61.7217 | 61.5941 | 61.6209
4444.0781 | 123.3902 | -61.3998 | 61.7477 | -1.0136 | -3.0168 | 0.54659 | 0.60224 | -1.7125 | -1.0453 | -1.1752 | 61.7477 | 0.27611 | 61.679 | -0.033101 | 0.043657 | 61.5433 | 0.003143 | 61.3169 | 60.3863 | 58.3831 | 61.9464 | 62.0021 | 59.6873 | 60.3546 | 60.2246 | 123.1476 | 61.6759 | 123.0788 | 61.3667 | 61.4435 | 122.9431 | 61.403 | 122.7167 | 61.7041 | 61.7446 | 61.6353 | 61.6758
4445.0625 | 123.3078 | -61.4182 | 61.7432 | -1.0182 | -3.0625 | 0.42755 | 0.51525 | -1.5798 | -1.0636 | -1.2576 | 61.7431 | 0.27153 | 61.6606 | -0.028522 | 0.052814 | 61.5341 | 0.003143 | 61.3123 | 60.4 | 58.3556 | 61.8457 | 61.9334 | 59.8384 | 60.3546 | 60.1605 | 123.1613 | 61.6897 | 123.0788 | 61.3896 | 61.471 | 122.9523 | 61.4213 | 122.7305 | 61.6903 | 61.74 | 61.6078 | 61.6575
4446.0938 | 123.3902 | -61.4182 | 61.6882 | -1.0044 | -3.0351 | 0.75721 | 0.37331 | -1.5248 | -1.0315 | -1.1523 | 61.7294 | 0.26237 | 61.6515 | -0.033101 | 0.048236 | 61.5433 | 0.012299 | 61.3215 | 60.4137 | 58.3831 | 62.1754 | 61.7915 | 59.8933 | 60.3866 | 60.2658 | 123.1475 | 61.6805 | 123.0696 | 61.3851 | 61.4664 | 122.9614 | 61.4305 | 122.7396 | 61.6812 | 61.7171 | 61.6032 | 61.6392
4447.0625 | 123.3032 | -61.4365 | 61.7432 | -1.0777 | -3.1312 | 0.67937 | 0.63887 | -1.5019 | -1.1185 | -1.1432 | 61.7431 | 0.27611 | 61.6744 | -0.03768 | 0.043657 | 61.5295 | -0.001436 | 61.3169 | 60.3588 | 58.3052 | 62.1158 | 62.0753 | 59.9345 | 60.3179 | 60.2933 | 123.1796 | 61.7126 | 123.1108 | 61.3988 | 61.4801 | 122.966 | 61.435 | 122.7533 | 61.6995 | 61.7446 | 61.6307 | 61.6758
4448.0781 | 123.4177 | -61.4227 | 61.6928 | -1.0548 | -3.0946 | 1.0914 | 0.68923 | -1.4562 | -1.0956 | -1.1569 | 61.7294 | 0.27611 | 61.6332 | -0.03768 | 0.043657 | 61.5433 | 0.003143 | 61.3169 | 60.3679 | 58.3281 | 62.5142 | 62.112 | 59.9666 | 60.3271 | 60.2658 | 123.1521 | 61.6988 | 123.0559 | 61.385 | 61.4664 | 122.966 | 61.4259 | 122.7396 | 61.6857 | 61.7263 | 61.5895 | 61.63
4449.0625 | 123.317 | -61.4319 | 61.7203 | -1.064 | -3.0396 | 1.0594 | 0.70754 | -1.4882 | -1.1048 | -1.1249 | 61.734 | 0.27153 | 61.6423 | -0.033101 | 0.043657 | 61.5387 | 0.003143 | 61.326 | 60.3679 | 58.3922 | 62.4913 | 62.1394 | 59.9437 | 60.3271 | 60.307 | 123.1659 | 61.7034 | 123.0742 | 61.3988 | 61.4755 | 122.9706 | 61.435 | 122.7579 | 61.6903 | 61.7308 | 61.5987 | 61.6392
4450.0781 | 123.3948 | -61.3907 | 61.702 | -1.128 | -3.0168 | 0.98614 | 0.70296 | -1.5981 | -1.1643 | -1.3858 | 61.7386 | 0.27153 | 61.6744 | -0.03768 | 0.043657 | 61.5341 | 0.012299 | 61.3077 | 60.2626 | 58.3739 | 62.3768 | 62.0937 | 59.7926 | 60.2264 | 60.0049 | 123.1292 | 61.6622 | 123.0651 | 61.353 | 61.4343 | 122.9248 | 61.403 | 122.6984 | 61.6949 | 61.7263 | 61.6307 | 61.6621
4451.0625 | 123.3948 | -61.409 | 61.6653 | -1.1326 | -2.8794 | 0.93577 | 0.86779 | -1.4882 | -1.1781 | -1.4911 | 61.7386 | 0.27153 | 61.6652 | -0.033101 | 0.043657 | 61.5341 | 0.003143 | 61.3123 | 60.2764 | 58.5296 | 62.3448 | 62.2768 | 59.9208 | 60.2309 | 59.9179 | 123.1476 | 61.6805 | 123.0742 | 61.3759 | 61.4527 | 122.9431 | 61.4121 | 122.7213 | 61.6949 | 61.7354 | 61.6216 | 61.6621
4452.0781 | 123.3948 | -61.3953 | 61.7203 | -1.0777 | -2.971 | 1.0182 | 0.37331 | -1.4653 | -1.1185 | -1.6697 | 61.7386 | 0.27153 | 61.6469 | -0.033101 | 0.048236 | 61.5387 | 0.007721 | 61.3123 | 60.3176 | 58.4243 | 62.4134 | 61.7686 | 59.93 | 60.2767 | 59.7256 | 123.1338 | 61.6668 | 123.0422 | 61.3622 | 61.4435 | 122.934 | 61.403 | 122.7076 | 61.6903 | 61.7308 | 61.5987 | 61.6392
4453.0625 | 123.3124 | -61.4273 | 61.7432 | -1.1235 | -3.1129 | 0.78468 | 0.52898 | -1.4928 | -1.1552 | -1.8619 | 61.7523 | 0.27153 | 61.6744 | -0.023943 | 0.043657 | 61.5341 | 0.007721 | 61.3077 | 60.3038 | 58.3144 | 62.212 | 61.9563 | 59.9345 | 60.2721 | 59.5654 | 123.1796 | 61.6988 | 123.1017 | 61.4034 | 61.471 | 122.9614 | 61.435 | 122.735 | 61.7086 | 61.7446 | 61.6307 | 61.6667
4454.0781 | 123.3856 | -61.377 | 61.6974 | -1.1235 | -3.1175 | 0.7801 | 0.86779 | -1.447 | -1.1643 | -1.9718 | 61.7431 | 0.27611 | 61.6744 | -0.023943 | 0.043657 | 61.5341 | 0.007721 | 61.3169 | 60.2535 | 58.2595 | 62.1571 | 62.2447 | 59.93 | 60.2126 | 59.4051 | 123.1201 | 61.6531 | 123.0513 | 61.353 | 61.4206 | 122.9111 | 61.3847 | 122.6938 | 61.6995 | 61.7354 | 61.6307 | 61.6667
4455.0625 | 123.3078 | -61.409 | 61.702 | -1.0502 | -3.058 | 0.54659 | 1.0189 | -1.2685 | -1.0911 | -1.9398 | 61.7294 | 0.27611 | 61.6377 | -0.028522 | 0.048236 | 61.5433 | 0.003143 | 61.3169 | 60.3588 | 58.351 | 61.9556 | 62.4279 | 60.1405 | 60.3179 | 59.4692 | 123.1384 | 61.6851 | 123.0467 | 61.3805 | 61.4572 | 122.9523 | 61.4121 | 122.7259 | 61.6812 | 61.7263 | 61.5895 | 61.6346
4456.0938 | 123.3948 | -61.3953 | 61.7432 | -1.183 | -3.1724 | 0.16657 | 0.75791 | -1.5019 | -1.233 | -2.0176 | 61.7477 | 0.27153 | 61.6881 | -0.028522 | 0.048236 | 61.525 | 0.007721 | 61.2986 | 60.2123 | 58.2228 | 61.5618 | 62.1532 | 59.8933 | 60.1623 | 59.3777 | 123.143 | 61.6668 | 123.0834 | 61.3667 | 61.4435 | 122.9202 | 61.403 | 122.6938 | 61.6995 | 61.74 | 61.6399 | 61.6804
4457.0625 | 123.2849 | -61.4044 | 61.7157 | -1.2105 | -3.1037 | 0.25814 | 0.69839 | -1.5157 | -1.2467 | -1.9672 | 61.7523 | 0.27153 | 61.679 | -0.033101 | 0.048236 | 61.5295 | -0.001436 | 61.2986 | 60.194 | 58.3007 | 61.6626 | 62.1028 | 59.8888 | 60.1577 | 59.4372 | 123.1567 | 61.6759 | 123.0834 | 61.3713 | 61.4527 | 122.934 | 61.403 | 122.703 | 61.7041 | 61.7537 | 61.6307 | 61.6804
4458.0781 | 123.4222 | -61.3724 | 61.7111 | -1.1738 | -3.1358 | 0.36345 | 0.68923 | -1.5248 | -1.2147 | -1.9352 | 61.7477 | 0.27153 | 61.6515 | -0.033101 | 0.039079 | 61.525 | 0.007721 | 61.3077 | 60.1985 | 58.2366 | 61.7358 | 62.0616 | 59.8476 | 60.1577 | 59.4372 | 123.1201 | 61.6439 | 123.0239 | 61.3393 | 61.4115 | 122.8973 | 61.3801 | 122.6801 | 61.7086 | 61.74 | 61.6124 | 61.6438
4459.0625 | 123.2986 | -61.4319 | 61.7157 | -1.1738 | -3.2365 | 0.28103 | 0.89068 | -1.5477 | -1.2147 | -1.9855 | 61.7569 | 0.27153 | 61.6973 | -0.033101 | 0.043657 | 61.5295 | 0.007721 | 61.3031 | 60.2581 | 58.1954 | 61.7129 | 62.3226 | 59.8842 | 60.2172 | 59.4463 | 123.1888 | 61.7034 | 123.1292 | 61.3988 | 61.4755 | 122.9614 | 61.4396 | 122.735 | 61.7132 | 61.7491 | 61.6536 | 61.6895
4460.0781 | 123.2666 | -61.4136 | 61.7752 | -1.1921 | -3.3006 | 0.36802 | 0.73959 | -1.6576 | -1.2467 | -1.9901 | 61.7431 | 0.26695 | 61.6698 | -0.028522 | 0.043657 | 61.525 | 0.012299 | 61.3031 | 60.2214 | 58.1129 | 61.7816 | 62.1532 | 59.756 | 60.1668 | 59.4234 | 123.1567 | 61.6805 | 123.0834 | 61.3851 | 61.4572 | 122.9385 | 61.4259 | 122.7167 | 61.6995 | 61.7308 | 61.6261 | 61.6575
4461.0625 | 123.2529 | -61.4548 | 61.7249 | -1.0868 | -3.1541 | 0.64732 | 1.0143 | -1.4607 | -1.1323 | -1.8665 | 61.7386 | 0.27153 | 61.6744 | -0.03768 | 0.039079 | 61.5433 | 0.007721 | 61.3077 | 60.3679 | 58.3007 | 62.1021 | 62.4691 | 59.994 | 60.3225 | 59.5883 | 123.1933 | 61.7263 | 123.1291 | 61.4171 | 61.4939 | 122.998 | 61.4625 | 122.7625 | 61.6995 | 61.7308 | 61.6353 | 61.6667
4462.0781 | 123.3948 | -61.3815 | 61.7111 | -1.128 | -3.3052 | 0.71142 | 0.80827 | -1.5798 | -1.1689 | -1.8803 | 61.734 | 0.26695 | 61.6698 | -0.033101 | 0.048236 | 61.5341 | 0.007721 | 61.3077 | 60.2535 | 58.0763 | 62.093 | 62.1898 | 59.8018 | 60.2126 | 59.5013 | 123.1155 | 61.6485 | 123.0513 | 61.3484 | 61.4298 | 122.9156 | 61.3893 | 122.6893 | 61.6857 | 61.7263 | 61.6216 | 61.6621
4463.0625 | 123.2986 | -61.4273 | 61.7203 | -1.0411 | -3.1816 | 0.85336 | 1.0143 | -1.3097 | -1.0773 | -1.7475 | 61.7294 | 0.27153 | 61.6561 | -0.033101 | 0.043657 | 61.5433 | 0.007721 | 61.3123 | 60.3862 | 58.2457 | 62.2807 | 62.4416 | 60.1177 | 60.35 | 59.6798 | 123.1567 | 61.6988 | 123.0834 | 61.3942 | 61.471 | 122.9706 | 61.435 | 122.7396 | 61.6857 | 61.7217 | 61.6124 | 61.6483
4464.0938 | 123.3078 | -61.3907 | 61.7615 | -1.064 | -3.1724 | 0.40465 | 0.86321 | -1.3509 | -1.1002 | -1.7887 | 61.7523 | 0.26695 | 61.6744 | -0.028522 | 0.048236 | 61.5341 | 0.012299 | 61.3077 | 60.3267 | 58.2183 | 61.7953 | 62.2539 | 60.0398 | 60.2905 | 59.602 | 123.143 | 61.6576 | 123.0651 | 61.3622 | 61.4389 | 122.9248 | 61.403 | 122.6984 | 61.7041 | 61.74 | 61.6261 | 61.6621
4465.0625 | 123.2803 | -61.4365 | 61.734 | -1.1235 | -3.3602 | 1.0136 | 0.30006 | -1.4928 | -1.1689 | -1.7841 | 61.7477 | 0.26695 | 61.6561 | -0.033101 | 0.048236 | 61.5295 | 0.003143 | 61.3123 | 60.313 | 58.0763 | 62.4501 | 61.7365 | 59.9437 | 60.2676 | 59.6524 | 123.1842 | 61.7034 | 123.0925 | 61.4034 | 61.4847 | 122.966 | 61.4396 | 122.7488 | 61.6995 | 61.7446 | 61.6078 | 61.6529
4466.0625 | 123.3902 | -61.4319 | 61.6974 | -1.0823 | -3.1862 | 1.151 | 0.51982 | -1.273 | -1.1277 | -1.7292 | 61.7431 | 0.26695 | 61.6698 | -0.046838 | 0.039079 | 61.5341 | 0.007721 | 61.3077 | 60.3496 | 58.2457 | 62.5829 | 61.9517 | 60.1589 | 60.3042 | 59.7027 | 123.175 | 61.6988 | 123.1017 | 61.385 | 61.471 | 122.966 | 61.4396 | 122.7396 | 61.7041 | 61.7354 | 61.6307 | 61.6621
4467.0938 | 123.3307 | -61.441 | 61.7386 | -1.096 | -3.2732 | 1.0823 | 0.51982 | -1.2685 | -1.1414 | -1.6971 | 61.734 | 0.27153 | 61.6423 | -0.033101 | 0.043657 | 61.5387 | 0.007721 | 61.3169 | 60.345 | 58.1679 | 62.5233 | 61.9609 | 60.1726 | 60.2996 | 59.7439 | 123.175 | 61.7126 | 123.0834 | 61.4079 | 61.4847 | 122.9797 | 61.4488 | 122.7579 | 61.6903 | 61.7263 | 61.5987 | 61.6346
4468.0625 | 123.2712 | -61.441 | 61.702 | -1.1189 | -3.3281 | 0.89914 | 0.42368 | -1.36 | -1.1597 | -1.6925 | 61.7477 | 0.27611 | 61.6835 | -0.03768 | 0.043657 | 61.5387 | 0.007721 | 61.3123 | 60.3221 | 58.1129 | 62.3402 | 61.8647 | 60.081 | 60.2813 | 59.7485 | 123.1888 | 61.7171 | 123.1246 | 61.4034 | 61.4847 | 122.9797 | 61.4488 | 122.7533 | 61.7041 | 61.74 | 61.6399 | 61.6758
4469.0781 | 123.3582 | -61.4182 | 61.7386 | -1.183 | -3.4105 | 0.69768 | 0.23138 | -1.3875 | -1.2284 | -1.5781 | 61.7431 | 0.26695 | 61.6515 | -0.033101 | 0.052814 | 61.5387 | 0.007721 | 61.3123 | 60.2352 | 58.0076 | 62.1158 | 61.6495 | 60.0307 | 60.1897 | 59.8401 | 123.1613 | 61.6851 | 123.0696 | 61.3851 | 61.471 | 122.9568 | 61.4259 | 122.7305 | 61.6903 | 61.7354 | 61.5987 | 61.6438
4470.0625 | 123.2758 | -61.4365 | 61.7294 | -1.1784 | -3.438 | 0.80757 | 0.28174 | -1.4195 | -1.2147 | -1.3812 | 61.7523 | 0.27611 | 61.6835 | -0.028522 | 0.048236 | 61.5295 | 0.007721 | 61.3215 | 60.2581 | 57.9985 | 62.244 | 61.7182 | 60.0169 | 60.2218 | 60.0552 | 123.1888 | 61.7126 | 123.12 | 61.4079 | 61.4847 | 122.966 | 61.4442 | 122.7579 | 61.7041 | 61.7446 | 61.6353 | 61.6758
4471.0938 | 123.2895 | -61.4136 | 61.7386 | -1.2196 | -3.5021 | 0.82131 | 0.26343 | -1.5248 | -1.2605 | -1.2714 | 61.7431 | 0.27153 | 61.6561 | -0.03768 | 0.043657 | 61.5295 | 0.003143 | 61.3215 | 60.194 | 57.9115 | 62.2349 | 61.677 | 59.8888 | 60.1531 | 60.1422 | 123.1567 | 61.6851 | 123.0696 | 61.3759 | 61.4572 | 122.9431 | 61.4167 | 122.735 | 61.6995 | 61.74 | 61.6124 | 61.6529
4472.0625 | 123.3856 | -61.409 | 61.7157 | -1.1738 | -3.4334 | 0.75721 | 0.24054 | -1.4882 | -1.2238 | -1.2347 | 61.7523 | 0.27153 | 61.6835 | -0.033101 | 0.048236 | 61.5295 | 0.003143 | 61.3169 | 60.2352 | 57.9756 | 62.1662 | 61.6495 | 59.9208 | 60.1852 | 60.1743 | 123.1613 | 61.6805 | 123.0925 | 61.3759 | 61.4572 | 122.9385 | 61.4121 | 122.7259 | 61.7041 | 61.7491 | 61.6353 | 61.6804
4473.0781 | 123.2758 | -61.4319 | 61.7523 | -1.2562 | -3.406 | 0.6519 | 0.14897 | -1.6667 | -1.2971 | -1.3767 | 61.7523 | 0.28069 | 61.6469 | -0.03768 | 0.039079 | 61.5341 | 0.007721 | 61.3123 | 60.1756 | 58.0259 | 62.0838 | 61.5809 | 59.7651 | 60.1348 | 60.0552 | 123.1842 | 61.7126 | 123.0788 | 61.3942 | 61.471 | 122.966 | 61.4396 | 122.7442 | 61.7132 | 61.7446 | 61.6078 | 61.6392
4474.0625 | 123.3215 | -61.409 | 61.7432 | -1.2334 | -3.3235 | 0.6931 | 0.11234 | -1.6667 | -1.2925 | -1.5552 | 61.7569 | 0.27611 | 61.679 | -0.028522 | 0.043657 | 61.5295 | 0.003143 | 61.3031 | 60.1756 | 58.0855 | 62.1021 | 61.5213 | 59.7423 | 60.1165 | 59.8538 | 123.1659 | 61.6851 | 123.088 | 61.3805 | 61.4527 | 122.9385 | 61.4121 | 122.7121 | 61.7132 | 61.7537 | 61.6353 | 61.6758
4475.0781 | 123.3398 | -61.3998 | 61.7294 | -1.1555 | -3.2091 | 0.55575 | 0.33668 | -1.5889 | -1.1872 | -1.5872 | 61.7294 | 0.27611 | 61.6469 | -0.028522 | 0.043657 | 61.5295 | 0.003143 | 61.3077 | 60.2443 | 58.1908 | 61.9556 | 61.7365 | 59.8109 | 60.2126 | 59.8126 | 123.1292 | 61.6759 | 123.0467 | 61.3713 | 61.4435 | 122.9294 | 61.403 | 122.7076 | 61.6857 | 61.7263 | 61.6032 | 61.6438
4476.0625 | 123.3765 | -61.4273 | 61.7249 | -1.1326 | -3.2777 | 0.25356 | 0.3962 | -1.5523 | -1.1689 | -1.4499 | 61.7477 | 0.27153 | 61.6835 | -0.028522 | 0.043657 | 61.5295 | 0.007721 | 61.3031 | 60.2947 | 58.1496 | 61.6809 | 61.8235 | 59.875 | 60.2584 | 59.9774 | 123.175 | 61.6988 | 123.1108 | 61.3988 | 61.471 | 122.9568 | 61.435 | 122.7305 | 61.7041 | 61.74 | 61.6399 | 61.6758
4477.0938 | 123.3215 | -61.4365 | 61.702 | -1.1509 | -3.2869 | 0.16199 | 0.33211 | -1.6255 | -1.2101 | -1.3538 | 61.7386 | 0.26695 | 61.6744 | -0.033101 | 0.043657 | 61.5341 | 0.003143 | 61.3031 | 60.2855 | 58.1496 | 61.5984 | 61.7686 | 59.8109 | 60.2264 | 60.0827 | 123.175 | 61.7034 | 123.1108 | 61.4034 | 61.4801 | 122.9706 | 61.4396 | 122.7396 | 61.6949 | 61.7354 | 61.6307 | 61.6712
4478.0625 | 123.2986 | -61.4319 | 61.7157 | -1.1097 | -3.2869 | 0.17572 | 0.37789 | -1.5889 | -1.1552 | -1.2576 | 61.7477 | 0.27153 | 61.6606 | -0.033101 | 0.043657 | 61.5295 | 0.003143 | 61.3031 | 60.3222 | 58.145 | 61.6076 | 61.8098 | 59.843 | 60.2767 | 60.1743 | 123.1796 | 61.7034 | 123.0925 | 61.3988 | 61.4755 | 122.9614 | 61.435 | 122.735 | 61.7041 | 61.7446 | 61.617 | 61.6575
4479.0938 | 123.2666 | -61.4365 | 61.734 | -1.1006 | -3.319 | 0.070415 | 0.46488 | -1.5798 | -1.1414 | -1.3446 | 61.7477 | 0.27153 | 61.6927 | -0.033101 | 0.048236 | 61.5295 | 0.007721 | 61.3031 | 60.3359 | 58.1175 | 61.5069 | 61.9013 | 59.8567 | 60.295 | 60.0919 | 123.1842 | 61.708 | 123.1292 | 61.4034 | 61.4847 | 122.966 | 61.4442 | 122.7396 | 61.6995 | 61.74 | 61.6445 | 61.685
4480.0625 | 123.3582 | -61.3861 | 61.7569 | -1.128 | -3.4151 | 0.056679 | 0.44199 | -1.6576 | -1.1689 | -1.3995 | 61.7523 | 0.27153 | 61.6606 | -0.033101 | 0.048236 | 61.525 | 0.003143 | 61.3031 | 60.2581 | 57.971 | 61.4428 | 61.8281 | 59.7285 | 60.2172 | 59.9866 | 123.1384 | 61.6576 | 123.0467 | 61.353 | 61.4343 | 122.9111 | 61.3893 | 122.6893 | 61.7041 | 61.7491 | 61.6124 | 61.6575
4481.0938 | 123.3078 | -61.4182 | 61.7798 | -1.1601 | -3.5387 | 0.11162 | 0.41452 | -1.6942 | -1.2009 | -1.3126 | 61.7477 | 0.27153 | 61.6652 | -0.028522 | 0.043657 | 61.5295 | 0.007721 | 61.3031 | 60.2581 | 57.8794 | 61.5298 | 61.8327 | 59.7239 | 60.2172 | 60.1056 | 123.1659 | 61.6897 | 123.0834 | 61.3896 | 61.4618 | 122.9477 | 61.4259 | 122.7213 | 61.7041 | 61.74 | 61.6216 | 61.6575
4482.0625 | 123.3902 | -61.4044 | 61.7157 | -1.1189 | -3.4517 | 0.020051 | 0.67091 | -1.685 | -1.1735 | -1.2851 | 61.7431 | 0.27611 | 61.6835 | -0.03768 | 0.043657 | 61.525 | 0.003143 | 61.3031 | 60.2855 | 57.9527 | 61.4245 | 62.0753 | 59.7194 | 60.2309 | 60.1193 | 123.1476 | 61.6805 | 123.088 | 61.3667 | 61.4481 | 122.9294 | 61.4076 | 122.7076 | 61.6995 | 61.74 | 61.6399 | 61.6804
4483.0781 | 123.2803 | -61.4044 | 61.7569 | -1.1189 | -3.4701 | 0.10704 | 0.65718 | -1.5843 | -1.1735 | -1.3354 | 61.7477 | 0.26695 | 61.6561 | -0.033101 | 0.057392 | 61.5341 | 0.003143 | 61.3077 | 60.2855 | 57.9344 | 61.5115 | 62.0616 | 59.8201 | 60.2309 | 60.069 | 123.1521 | 61.6714 | 123.0605 | 61.3713 | 61.4618 | 122.9385 | 61.4076 | 122.7121 | 61.6903 | 61.7446 | 61.5987 | 61.6529
4484.0625 | 123.2712 | -61.4822 | 61.7157 | -0.87166 | -3.1816 | 0.62443 | 1.0051 | -1.1403 | -0.92624 | -1.3217 | 61.734 | 0.28069 | 61.6606 | -0.028522 | 0.043657 | 61.5478 | -0.001436 | 61.3215 | 60.6106 | 58.3006 | 62.1067 | 62.4874 | 60.342 | 60.556 | 60.1605 | 123.2162 | 61.7629 | 123.1429 | 61.4537 | 61.5259 | 123.0301 | 61.4808 | 122.8037 | 61.6903 | 61.7354 | 61.617 | 61.6621
4485.0938 | 123.3124 | -61.4502 | 61.7203 | -1.0319 | -3.2915 | 0.35887 | 0.8449 | -1.3829 | -1.0682 | -1.6056 | 61.7477 | 0.27611 | 61.679 | -0.028522 | 0.043657 | 61.5341 | 0.007721 | 61.3123 | 60.4183 | 58.1587 | 61.8091 | 62.2951 | 60.0673 | 60.382 | 59.8446 | 123.1979 | 61.7263 | 123.1291 | 61.4217 | 61.4939 | 122.9843 | 61.4579 | 122.7625 | 61.7041 | 61.74 | 61.6353 | 61.6712
4486.0625 | 123.3353 | -61.4136 | 61.7065 | -1.009 | -3.2365 | 0.22609 | 0.8861 | -1.3463 | -1.0499 | -1.5506 | 61.734 | 0.26237 | 61.6469 | -0.03768 | 0.043657 | 61.5387 | 0.003143 | 61.3077 | 60.4046 | 58.177 | 61.6397 | 62.2997 | 60.0673 | 60.3637 | 59.8629 | 123.1475 | 61.6759 | 123.0605 | 61.3759 | 61.4572 | 122.9523 | 61.4167 | 122.7213 | 61.6903 | 61.7308 | 61.6032 | 61.6438
4487.0781 | 123.2712 | -61.4273 | 61.734 | -1.1189 | -3.4197 | -0.11731 | 0.68465 | -1.5065 | -1.1643 | -1.6559 | 61.7569 | 0.27153 | 61.6835 | -0.033101 | 0.043657 | 61.5295 | 0.003143 | 61.2986 | 60.3084 | 58.0076 | 61.31 | 62.112 | 59.9208 | 60.263 | 59.7714 | 123.1842 | 61.6988 | 123.1108 | 61.3942 | 61.471 | 122.9568 | 61.4305 | 122.7259 | 61.7132 | 61.7537 | 61.6399 | 61.6804
4488.0625 | 123.3261 | -61.3815 | 61.7294 | -1.0914 | -3.3647 | -0.2043 | 1.2158 | -1.3966 | -1.1368 | -1.6422 | 61.7523 | 0.27611 | 61.6835 | -0.028522 | 0.048236 | 61.5295 | -0.001436 | 61.3031 | 60.2901 | 58.0168 | 61.1772 | 62.5973 | 59.9849 | 60.2447 | 59.7393 | 123.1338 | 61.6576 | 123.0651 | 61.353 | 61.4298 | 122.9111 | 61.3801 | 122.6847 | 61.7041 | 61.7537 | 61.6353 | 61.685
4489.0781 | 123.2941 | -61.4044 | 61.7844 | -1.128 | -3.2503 | -0.22719 | 0.822 | -1.4562 | -1.1781 | -1.6147 | 61.7386 | 0.27153 | 61.6561 | -0.033101 | 0.048236 | 61.5295 | 0.007721 | 61.3031 | 60.2764 | 58.1541 | 61.1772 | 62.2264 | 59.9483 | 60.2264 | 59.7897 | 123.143 | 61.6759 | 123.0605 | 61.3713 | 61.4527 | 122.934 | 61.4121 | 122.7076 | 61.6903 | 61.7308 | 61.6078 | 61.6483
4490.0625 | 123.2712 | -61.4182 | 61.7386 | -1.1052 | -3.1862 | -0.35997 | 0.69839 | -1.4149 | -1.146 | -1.3629 | 61.7477 | 0.27153 | 61.6881 | -0.023943 | 0.043657 | 61.525 | -0.001436 | 61.294 | 60.313 | 58.232 | 61.0582 | 62.1165 | 60.0032 | 60.2721 | 60.0552 | 123.1659 | 61.6897 | 123.1063 | 61.3942 | 61.4618 | 122.9431 | 61.4167 | 122.7121 | 61.7041 | 61.7491 | 61.6445 | 61.6895
4491.0938 | 123.3261 | -61.4502 | 61.7523 | -1.0823 | -3.1633 | -0.29129 | 1.1379 | -1.3142 | -1.1414 | -1.4636 | 61.7386 | 0.28069 | 61.6561 | -0.033101 | 0.034501 | 61.5295 | 0.003143 | 61.3031 | 60.3679 | 58.2869 | 61.1589 | 62.5881 | 60.136 | 60.3088 | 59.9866 | 123.1887 | 61.7309 | 123.1063 | 61.4171 | 61.4847 | 122.9797 | 61.4533 | 122.7533 | 61.7041 | 61.7354 | 61.6216 | 61.6529
4492.0625 | 123.3032 | -61.4044 | 61.7249 | -1.0411 | -3.1679 | -0.18599 | 0.96394 | -1.3005 | -1.0819 | -1.5003 | 61.7386 | 0.28526 | 61.6652 | -0.03768 | 0.052814 | 61.5387 | 0.007721 | 61.3077 | 60.3634 | 58.2366 | 61.2184 | 62.3684 | 60.1039 | 60.3225 | 59.9042 | 123.143 | 61.6897 | 123.0696 | 61.3667 | 61.4572 | 122.9431 | 61.4121 | 122.7121 | 61.6857 | 61.7308 | 61.6124 | 61.6575
4493.0781 | 123.3948 | -61.3953 | 61.6928 | -1.0273 | -3.145 | 0.23982 | 1.2844 | -1.2822 | -1.0773 | -1.5415 | 61.7386 | 0.27153 | 61.6698 | -0.03768 | 0.043657 | 61.5387 | 0.007721 | 61.3123 | 60.3679 | 58.2503 | 61.6351 | 62.6797 | 60.1131 | 60.3179 | 59.8538 | 123.1338 | 61.6668 | 123.0651 | 61.3576 | 61.4389 | 122.934 | 61.403 | 122.7076 | 61.6949 | 61.7308 | 61.6261 | 61.6621
4494.0625 | 123.3398 | -61.4456 | 61.7203 | -0.92202 | -3.0946 | 0.29477 | 1.4538 | -1.0396 | -0.95829 | -1.427 | 61.7248 | 0.28069 | 61.6377 | -0.028522 | 0.043657 | 61.5433 | 0.003143 | 61.3306 | 60.5236 | 58.351 | 61.7404 | 62.8995 | 60.4061 | 60.4873 | 60.0186 | 123.1704 | 61.7263 | 123.0834 | 61.4171 | 61.4893 | 122.9889 | 61.4488 | 122.7762 | 61.6812 | 61.7217 | 61.5941 | 61.6346
4495.0781 | 123.4451 | -61.3998 | 61.6791 | -0.85335 | -3.0625 | 0.40465 | 1.2386 | -0.98462 | -0.88504 | -1.253 | 61.7294 | 0.27611 | 61.6561 | -0.033101 | 0.043657 | 61.5478 | 0.012299 | 61.3306 | 60.5465 | 58.3373 | 61.8045 | 62.6385 | 60.4152 | 60.5148 | 60.1468 | 123.1292 | 61.6759 | 123.0559 | 61.3667 | 61.4435 | 122.9477 | 61.4121 | 122.7305 | 61.6857 | 61.7171 | 61.6124 | 61.6438
4496.0625 | 123.2803 | -61.4685 | 61.7111 | -0.90829 | -3.1679 | 0.38634 | 1.2341 | -1.0899 | -0.94455 | -1.1477 | 61.7294 | 0.28069 | 61.6377 | -0.028522 | 0.043657 | 61.5433 | 0.003143 | 61.3215 | 60.5602 | 58.3007 | 61.8548 | 62.7026 | 60.3786 | 60.524 | 60.3208 | 123.1979 | 61.7492 | 123.1063 | 61.44 | 61.5122 | 123.0118 | 61.4716 | 122.79 | 61.6857 | 61.7263 | 61.5941 | 61.6346
4497.0781 | 123.381 | -61.3907 | 61.7065 | -0.85792 | -3.1587 | 0.60611 | 1.4172 | -1.035 | -0.90335 | -1.2164 | 61.734 | 0.26695 | 61.6606 | -0.023943 | 0.052814 | 61.5433 | 0.012299 | 61.3443 | 60.5328 | 58.232 | 61.9968 | 62.8079 | 60.3557 | 60.4873 | 60.1743 | 123.1247 | 61.6576 | 123.0513 | 61.3667 | 61.4435 | 122.934 | 61.403 | 122.735 | 61.6812 | 61.7217 | 61.6078 | 61.6483
4498.0625 | 123.317 | -61.4136 | 61.7157 | -0.8625 | -3.2777 | 0.17572 | 0.822 | -1.2089 | -0.90335 | -1.2759 | 61.734 | 0.27153 | 61.6423 | -0.033101 | 0.048236 | 61.5341 | 0.007721 | 61.3306 | 60.5511 | 58.1358 | 61.5893 | 62.2356 | 60.2046 | 60.5102 | 60.1376 | 123.1475 | 61.6851 | 123.0559 | 61.3805 | 61.4618 | 122.9477 | 61.4213 | 122.7442 | 61.6857 | 61.7263 | 61.5941 | 61.6346
4499.0781 | 123.4177 | -61.3907 | 61.7111 | -0.89455 | -3.3602 | 0.12536 | 0.909 | -1.2044 | -0.9354 | -1.2302 | 61.7386 | 0.27153 | 61.6698 | -0.033101 | 0.048236 | 61.5433 | 0.003143 | 61.3215 | 60.4961 | 58.0305 | 61.516 | 62.2997 | 60.1863 | 60.4553 | 60.1605 | 123.1292 | 61.6622 | 123.0605 | 61.3576 | 61.4389 | 122.934 | 61.3938 | 122.7121 | 61.6903 | 61.7354 | 61.6216 | 61.6667
4500.0625 | 123.349 | -61.4227 | 61.7249 | -1.0044 | -3.4792 | 0.10704 | 0.9731 | -1.2273 | -1.0499 | -1.4087 | 61.7386 | 0.27153 | 61.6561 | -0.028522 | 0.048236 | 61.5387 | -0.001436 | 61.3169 | 60.4183 | 57.9435 | 61.5298 | 62.3958 | 60.1955 | 60.3729 | 60.014 | 123.1613 | 61.6943 | 123.0788 | 61.3942 | 61.471 | 122.9614 | 61.4213 | 122.7396 | 61.6903 | 61.74 | 61.6078 | 61.6575
4501.1094 | 123.317 | -61.4136 | 61.734 | -0.97696 | -3.3327 | 0.074994 | 1.4218 | -1.1769 | -1.0178 | -1.1935 | 61.734 | 0.27153 | 61.679 | -0.028522 | 0.043657 | 61.5433 | -0.006014 | 61.3215 | 60.4366 | 58.0809 | 61.4886 | 62.8354 | 60.2367 | 60.3958 | 60.22 | 123.1475 | 61.6851 | 123.0925 | 61.3851 | 61.4572 | 122.9568 | 61.4076 | 122.735 | 61.6903 | 61.74 | 61.6353 | 61.685
4502.0625 | 123.3032 | -61.409 | 61.7569 | -1.1967 | -3.5067 | -0.42407 | 1.257 | -1.2959 | -1.233 | -1.2668 | 61.7477 | 0.27153 | 61.6835 | -0.033101 | 0.048236 | 61.5295 | 0.007721 | 61.3077 | 60.2123 | 57.9023 | 60.9849 | 62.666 | 60.1131 | 60.176 | 60.1422 | 123.1567 | 61.6805 | 123.0925 | 61.3759 | 61.4572 | 122.9385 | 61.4167 | 122.7167 | 61.6995 | 61.74 | 61.6353 | 61.6758
4503.0938 | 123.3398 | -61.4227 | 61.7615 | -1.128 | -3.4655 | -0.3554 | 1.3211 | -1.2089 | -1.1872 | -1.2942 | 61.7523 | 0.27611 | 61.6515 | -0.033101 | 0.057392 | 61.5341 | 0.003143 | 61.3077 | 60.2947 | 57.9573 | 61.0673 | 62.7438 | 60.2138 | 60.2355 | 60.1285 | 123.175 | 61.6988 | 123.0742 | 61.3896 | 61.4801 | 122.9568 | 61.4259 | 122.7305 | 61.6949 | 61.7491 | 61.5941 | 61.6483
4504.0625 | 123.2941 | -61.4319 | 61.7523 | -1.1784 | -3.4838 | -0.36455 | 1.2386 | -1.3005 | -1.2284 | -1.3858 | 61.7477 | 0.28069 | 61.6881 | -0.03768 | 0.039079 | 61.5341 | 0.003143 | 61.3077 | 60.2535 | 57.9481 | 61.0673 | 62.6705 | 60.1314 | 60.2035 | 60.0461 | 123.1796 | 61.7126 | 123.12 | 61.3942 | 61.471 | 122.966 | 61.435 | 122.7396 | 61.7086 | 61.7446 | 61.649 | 61.685
4505.0938 | 123.3124 | -61.409 | 61.7111 | -1.1464 | -3.4014 | -0.41034 | 1.2295 | -1.2959 | -1.1872 | -1.4682 | 61.7477 | 0.28069 | 61.6606 | -0.033101 | 0.048236 | 61.5295 | 0.007721 | 61.3077 | 60.2626 | 58.0076 | 60.9987 | 62.6385 | 60.1131 | 60.2218 | 59.9408 | 123.1567 | 61.6897 | 123.0696 | 61.3759 | 61.4572 | 122.9385 | 61.4167 | 122.7167 | 61.6995 | 61.74 | 61.6124 | 61.6529
4506.0625 | 123.2758 | -61.4136 | 61.7249 | -1.1555 | -3.4243 | -0.4195 | 1.1791 | -1.3692 | -1.2101 | -1.7612 | 61.7386 | 0.27611 | 61.6652 | -0.033101 | 0.048236 | 61.5295 | 0.007721 | 61.3031 | 60.2581 | 57.9893 | 60.9941 | 62.5927 | 60.0444 | 60.2035 | 59.6524 | 123.1521 | 61.6897 | 123.0788 | 61.3805 | 61.4618 | 122.9431 | 61.4213 | 122.7167 | 61.6903 | 61.7308 | 61.617 | 61.6575
4507.0781 | 123.262 | -61.4365 | 61.7661 | -1.1693 | -3.4288 | -0.56601 | 1.083 | -1.4378 | -1.2193 | -1.8162 | 61.7523 | 0.27611 | 61.7018 | -0.033101 | 0.052814 | 61.5295 | 0.003143 | 61.3031 | 60.2672 | 58.0076 | 60.8705 | 62.5194 | 59.9986 | 60.2172 | 59.6203 | 123.1888 | 61.7126 | 123.1383 | 61.4034 | 61.4893 | 122.966 | 61.4396 | 122.7396 | 61.6995 | 61.7491 | 61.649 | 61.6987
4508.0625 | 123.2941 | -61.4227 | 61.7249 | -1.0823 | -3.4472 | -0.49275 | 1.2661 | -1.3325 | -1.1277 | -1.6559 | 61.7477 | 0.27153 | 61.6606 | -0.03768 | 0.052814 | 61.5341 | 0.007721 | 61.3123 | 60.3405 | 57.9756 | 60.93 | 62.6888 | 60.0902 | 60.295 | 59.7668 | 123.1704 | 61.6943 | 123.0834 | 61.385 | 61.4755 | 122.9568 | 61.4304 | 122.735 | 61.6949 | 61.74 | 61.6078 | 61.6529
4509.0938 | 123.2437 | -61.4136 | 61.7523 | -1.0868 | -3.3693 | -0.31877 | 1.0235 | -1.36 | -1.1323 | -1.3675 | 61.7431 | 0.27153 | 61.6561 | -0.023943 | 0.048236 | 61.5387 | 0.003143 | 61.3123 | 60.3267 | 58.0443 | 61.0948 | 62.437 | 60.0536 | 60.2813 | 60.0461 | 123.1567 | 61.6851 | 123.0696 | 61.3896 | 61.4618 | 122.9523 | 61.4167 | 122.7259 | 61.6949 | 61.74 | 61.6078 | 61.6529
4510.0625 | 123.3078 | -61.409 | 61.7523 | -1.2059 | -3.5662 | -0.51565 | 0.9502 | -1.5981 | -1.2467 | -1.3812 | 61.7569 | 0.27611 | 61.6927 | -0.033101 | 0.048236 | 61.525 | 0.003143 | 61.2986 | 60.2031 | 57.8428 | 60.8934 | 62.3592 | 59.8109 | 60.1623 | 60.0278 | 123.1659 | 61.6851 | 123.1017 | 61.3759 | 61.4572 | 122.934 | 61.4121 | 122.7076 | 61.7086 | 61.7537 | 61.6445 | 61.6895
4511.1094 | 123.3261 | -61.4182 | 61.7661 | -1.1693 | -3.5433 | -0.3554 | 1.0418 | -1.5202 | -1.2055 | -1.2347 | 61.7523 | 0.27153 | 61.6515 | -0.03768 | 0.052814 | 61.5204 | 0.012299 | 61.3123 | 60.2489 | 57.8748 | 61.0628 | 62.4599 | 59.8979 | 60.2126 | 60.1834 | 123.1704 | 61.6897 | 123.0696 | 61.3805 | 61.471 | 122.9385 | 61.4305 | 122.7305 | 61.6995 | 61.74 | 61.5987 | 61.6392
4512.0625 | 123.2849 | -61.4456 | 61.7294 | -1.0868 | -3.3785 | -0.21804 | 1.202 | -1.3921 | -1.1185 | -0.95546 | 61.7386 | 0.27153 | 61.6698 | -0.033101 | 0.048236 | 61.5341 | 0.003143 | 61.3169 | 60.3588 | 58.0671 | 61.2276 | 62.6476 | 60.0536 | 60.3271 | 60.4902 | 123.1842 | 61.7171 | 123.1154 | 61.4125 | 61.4939 | 122.9797 | 61.4488 | 122.7625 | 61.6903 | 61.7354 | 61.6216 | 61.6667
4513.0781 | 123.3582 | -61.4227 | 61.7157 | -1.1418 | -3.4975 | 0.15283 | 1.2158 | -1.4653 | -1.1781 | -1.1294 | 61.7386 | 0.27153 | 61.6561 | -0.028522 | 0.048236 | 61.5295 | 0.012299 | 61.326 | 60.2809 | 57.9252 | 61.5756 | 62.6385 | 59.9574 | 60.2447 | 60.2933 | 123.1613 | 61.6943 | 123.0788 | 61.3942 | 61.471 | 122.9523 | 61.435 | 122.7488 | 61.6903 | 61.7263 | 61.6078 | 61.6438
4514.0625 | 123.2941 | -61.4685 | 61.7249 | -0.97238 | -3.3144 | 0.3955 | 1.7881 | -1.2135 | -1.0087 | -0.75402 | 61.7202 | 0.28069 | 61.6515 | -0.03768 | 0.052814 | 61.5524 | 0.012299 | 61.3306 | 60.4961 | 58.1541 | 61.864 | 63.2566 | 60.255 | 60.4599 | 60.7145 | 123.1887 | 61.7492 | 123.12 | 61.4308 | 61.5213 | 123.0209 | 61.4808 | 122.7991 | 61.6674 | 61.7079 | 61.5987 | 61.6392
4515.0781 | 123.4039 | -61.4273 | 61.7111 | -0.98154 | -3.3968 | 0.20319 | 1.2386 | -1.4012 | -1.0178 | -0.87763 | 61.734 | 0.27153 | 61.6652 | -0.033101 | 0.048236 | 61.5387 | 0.003143 | 61.3215 | 60.4458 | 58.0305 | 61.6305 | 62.666 | 60.0261 | 60.4095 | 60.5497 | 123.1613 | 61.6988 | 123.0925 | 61.3942 | 61.4755 | 122.966 | 61.4305 | 122.7488 | 61.6857 | 61.7308 | 61.617 | 61.6621
4516.0625 | 123.3307 | -61.4319 | 61.6837 | -0.99985 | -3.4563 | -0.098993 | 1.2524 | -1.3692 | -1.0361 | -1.0974 | 61.7386 | 0.26695 | 61.6515 | -0.028522 | 0.043657 | 61.5387 | 0.007721 | 61.3123 | 60.432 | 57.9756 | 61.3329 | 62.6843 | 60.0627 | 60.3958 | 60.3345 | 123.1704 | 61.6988 | 123.0834 | 61.4034 | 61.4755 | 122.9706 | 61.4396 | 122.7442 | 61.6949 | 61.7308 | 61.6078 | 61.6438
4517.0938 | 123.2941 | -61.4182 | 61.7569 | -0.90829 | -3.3831 | -0.17225 | 1.2615 | -1.3051 | -0.94913 | -1.1798 | 61.7386 | 0.27153 | 61.6744 | -0.03768 | 0.048236 | 61.5433 | 0.003143 | 61.3123 | 60.5099 | 58.0351 | 61.2459 | 62.6797 | 60.1131 | 60.469 | 60.2384 | 123.1567 | 61.6897 | 123.0925 | 61.3805 | 61.4664 | 122.9614 | 61.4213 | 122.7305 | 61.6903 | 61.7354 | 61.6261 | 61.6712
4518.0625 | 123.2758 | -61.4594 | 61.7203 | -0.83503 | -3.2869 | -0.24093 | 1.376 | -1.2135 | -0.86672 | -1.2988 | 61.734 | 0.27153 | 61.6423 | -0.028522 | 0.039079 | 61.5433 | -0.001436 | 61.326 | 60.6243 | 58.1724 | 61.2184 | 62.8354 | 60.2458 | 60.5926 | 60.1605 | 123.1933 | 61.7309 | 123.1017 | 61.4308 | 61.4984 | 123.0026 | 61.4579 | 122.7854 | 61.6949 | 61.7354 | 61.6032 | 61.6438
4519.0781 | 123.2254 | -61.409 | 61.7477 | -0.94949 | -3.3647 | -0.3554 | 1.756 | -1.1906 | -0.98118 | -1.4041 | 61.7431 | 0.27153 | 61.6698 | -0.028522 | 0.048236 | 61.5387 | 0.012299 | 61.3215 | 60.4595 | 58.0443 | 61.0536 | 63.165 | 60.2184 | 60.4278 | 60.0049 | 123.1521 | 61.6805 | 123.0788 | 61.3805 | 61.4572 | 122.9477 | 61.4213 | 122.7305 | 61.6949 | 61.7308 | 61.6216 | 61.6575
4520.0625 | 123.2803 | -61.4594 | 61.7294 | -0.97238 | -3.3281 | 0.24898 | 1.2982 | -1.2456 | -1.0132 | -1.34 | 61.7431 | 0.28069 | 61.6377 | -0.033101 | 0.039079 | 61.5387 | 0.012299 | 61.3306 | 60.487 | 58.1312 | 61.7083 | 62.7575 | 60.2138 | 60.4461 | 60.1193 | 123.2025 | 61.74 | 123.0971 | 61.4262 | 61.4984 | 122.998 | 61.4716 | 122.79 | 61.7041 | 61.7308 | 61.5987 | 61.6255
4521.0938 | 123.4085 | -61.3907 | 61.6791 | -0.93576 | -3.3693 | 0.38634 | 1.3485 | -1.2273 | -0.96745 | -1.2576 | 61.7386 | 0.26695 | 61.6744 | -0.028522 | 0.048236 | 61.5433 | 0.003143 | 61.326 | 60.4549 | 58.0214 | 61.777 | 62.7392 | 60.1634 | 60.4232 | 60.1331 | 123.1292 | 61.6576 | 123.0651 | 61.3622 | 61.4389 | 122.934 | 61.3938 | 122.7167 | 61.6903 | 61.7354 | 61.6261 | 61.6712
4522.0625 | 123.3032 | -61.4456 | 61.7203 | -0.92202 | -3.3235 | 0.23067 | 1.495 | -1.2685 | -0.95829 | -1.1935 | 61.734 | 0.27611 | 61.6377 | -0.033101 | 0.052814 | 61.5433 | 0.007721 | 61.3352 | 60.5236 | 58.1221 | 61.6763 | 62.9407 | 60.1772 | 60.4873 | 60.2521 | 123.1796 | 61.7217 | 123.0834 | 61.4125 | 61.4984 | 122.9889 | 61.4533 | 122.7808 | 61.6812 | 61.7263 | 61.5849 | 61.63
4523.0781 | 123.349 | -61.4136 | 61.7661 | -1.0502 | -3.438 | -0.22262 | 1.4218 | -1.3463 | -1.0956 | -1.2485 | 61.7477 | 0.27611 | 61.6835 | -0.028522 | 0.048236 | 61.5341 | 0.003143 | 61.3398 | 60.3634 | 57.9756 | 61.191 | 62.8354 | 60.0673 | 60.3179 | 60.1651 | 123.1613 | 61.6897 | 123.0971 | 61.3851 | 61.4618 | 122.9477 | 61.4167 | 122.7533 | 61.6995 | 61.7446 | 61.6353 | 61.6804
4524.0625 | 123.3215 | -61.4548 | 61.7157 | -1.0731 | -3.5571 | -0.51107 | 1.5134 | -1.3371 | -1.1094 | -1.1752 | 61.7431 | 0.27153 | 61.6515 | -0.033101 | 0.039079 | 61.5387 | -0.001436 | 61.326 | 60.3817 | 57.8977 | 60.9437 | 62.9681 | 60.1177 | 60.3454 | 60.2796 | 123.1979 | 61.7263 | 123.1063 | 61.4217 | 61.4939 | 122.9935 | 61.4533 | 122.7808 | 61.7041 | 61.7446 | 61.6124 | 61.6529
4525.0938 | 123.3353 | -61.4044 | 61.7615 | -1.1418 | -3.6853 | -0.63011 | 1.4401 | -1.4882 | -1.1826 | -1.2714 | 61.7569 | 0.27611 | 61.6927 | -0.033101 | 0.048236 | 61.5295 | -0.001436 | 61.326 | 60.2626 | 57.7192 | 60.7743 | 62.8445 | 59.9162 | 60.2218 | 60.1331 | 123.1613 | 61.6805 | 123.0971 | 61.3713 | 61.4527 | 122.934 | 61.403 | 122.7305 | 61.7086 | 61.7583 | 61.6445 | 61.6941
4526.0625 | 123.3353 | -61.4136 | 61.6974 | -1.1647 | -3.6624 | -0.41034 | 1.4493 | -1.4974 | -1.2009 | -1.0745 | 61.7386 | 0.27611 | 61.6561 | -0.033101 | 0.048236 | 61.5387 | 0.007721 | 61.3169 | 60.2489 | 57.7512 | 61.0032 | 62.8628 | 59.9162 | 60.2126 | 60.3391 | 123.1521 | 61.6897 | 123.0696 | 61.3805 | 61.4618 | 122.9523 | 61.4213 | 122.7305 | 61.6903 | 61.7308 | 61.6078 | 61.6483
4527.0781 | 123.317 | -61.4319 | 61.7249 | -1.1876 | -3.6441 | -0.45612 | 1.3943 | -1.5157 | -1.2238 | -1.0196 | 61.7477 | 0.27611 | 61.6744 | -0.028522 | 0.039079 | 61.5295 | 0.007721 | 61.3123 | 60.2443 | 57.7878 | 60.9758 | 62.8262 | 59.9162 | 60.208 | 60.4123 | 123.1796 | 61.708 | 123.1063 | 61.4034 | 61.471 | 122.9614 | 61.4396 | 122.7442 | 61.7086 | 61.74 | 61.6353 | 61.6667
4528.0625 | 123.3124 | -61.4273 | 61.6974 | -1.2288 | -3.6807 | -0.70337 | 1.3394 | -1.5248 | -1.2696 | -0.93715 | 61.7477 | 0.27153 | 61.679 | -0.028522 | 0.043657 | 61.525 | 0.007721 | 61.3077 | 60.1985 | 57.7466 | 60.7239 | 62.7667 | 59.9025 | 60.1577 | 60.4902 | 123.175 | 61.6988 | 123.1063 | 61.3988 | 61.471 | 122.9523 | 61.435 | 122.735 | 61.7041 | 61.74 | 61.6353 | 61.6712
4529.0625 | 123.2986 | -61.4365 | 61.7157 | -1.1235 | -3.5616 | -0.56601 | 1.6141 | -1.0899 | -1.1552 | -1.0699 | 61.7431 | 0.27611 | 61.6561 | -0.028522 | 0.039079 | 61.5341 | 0.003143 | 61.3215 | 60.313 | 57.8748 | 60.8705 | 63.0505 | 60.3465 | 60.2813 | 60.3665 | 123.1796 | 61.7126 | 123.0925 | 61.4079 | 61.4755 | 122.9706 | 61.4396 | 122.7579 | 61.7041 | 61.74 | 61.617 | 61.6529
4530.0938 | 123.2895 | -61.4227 | 61.702 | -1.009 | -3.4517 | -0.63011 | 1.6828 | -0.91595 | -1.0499 | -1.0928 | 61.734 | 0.27611 | 61.679 | -0.028522 | 0.048236 | 61.5341 | 0.012299 | 61.3169 | 60.4137 | 57.971 | 60.7926 | 63.1055 | 60.5068 | 60.3729 | 60.3299 | 123.1567 | 61.6988 | 123.1017 | 61.3942 | 61.471 | 122.9568 | 61.435 | 122.7396 | 61.6857 | 61.7217 | 61.6307 | 61.6667
4531.0625 | 123.3444 | -61.4136 | 61.7249 | -0.99528 | -3.3876 | -0.56601 | 1.7331 | -0.91137 | -1.027 | -1.3721 | 61.7431 | 0.27153 | 61.6515 | -0.033101 | 0.043657 | 61.5387 | 0.007721 | 61.326 | 60.4183 | 58.0259 | 60.8476 | 63.1467 | 60.5022 | 60.3866 | 60.0415 | 123.1567 | 61.6851 | 123.0651 | 61.3805 | 61.4572 | 122.9523 | 61.4213 | 122.7396 | 61.6995 | 61.7354 | 61.6078 | 61.6438
4532.0938 | 123.2391 | -61.4548 | 61.7203 | -1.0182 | -3.4563 | -0.78578 | 1.7469 | -0.90222 | -1.0544 | -1.5872 | 61.7431 | 0.27153 | 61.6469 | -0.033101 | 0.048236 | 61.5341 | -0.001436 | 61.3215 | 60.4366 | 57.9985 | 60.669 | 63.2016 | 60.5526 | 60.4003 | 59.8675 | 123.1979 | 61.7263 | 123.1017 | 61.4217 | 61.503 | 122.9889 | 61.4533 | 122.7762 | 61.6949 | 61.7446 | 61.5987 | 61.6483
4533.0625 | 123.4039 | -61.3953 | 61.6928 | -0.99985 | -3.438 | -0.65758 | 1.7331 | -0.83355 | -1.0315 | -1.5232 | 61.7431 | 0.27611 | 61.679 | -0.03768 | 0.048236 | 61.5387 | 0.007721 | 61.3215 | 60.3954 | 57.9573 | 60.7377 | 63.1284 | 60.5617 | 60.3637 | 59.8721 | 123.1384 | 61.6714 | 123.0742 | 61.3576 | 61.4435 | 122.934 | 61.403 | 122.7167 | 61.6949 | 61.7354 | 61.6307 | 61.6712
4534.0781 | 123.2941 | -61.4502 | 61.7111 | -1.128 | -3.6349 | -0.44697 | 1.3989 | -1.2501 | -1.1735 | -1.3675 | 61.7477 | 0.27611 | 61.6698 | -0.033101 | 0.043657 | 61.5295 | 0.003143 | 61.3077 | 60.3221 | 57.8153 | 61.0032 | 62.8491 | 60.2001 | 60.2767 | 60.0827 | 123.1979 | 61.7263 | 123.12 | 61.4171 | 61.4939 | 122.9797 | 61.4533 | 122.7579 | 61.7041 | 61.7446 | 61.6261 | 61.6667
4535.0625 | 123.3994 | -61.4136 | 61.6699 | -1.1372 | -3.7173 | -0.2684 | 1.4218 | -1.2593 | -1.1735 | -1.2393 | 61.7386 | 0.28069 | 61.6561 | -0.03768 | 0.043657 | 61.5341 | 0.007721 | 61.3123 | 60.2764 | 57.6963 | 61.1452 | 62.8354 | 60.1543 | 60.2401 | 60.1743 | 123.1521 | 61.6943 | 123.0696 | 61.3759 | 61.4572 | 122.9477 | 61.4213 | 122.7259 | 61.6949 | 61.7308 | 61.6124 | 61.6483
4536.1094 | 123.3353 | -61.4182 | 61.7249 | -1.1921 | -3.7906 | -0.40118 | 1.3714 | -1.328 | -1.2284 | -1.1661 | 61.7523 | 0.27153 | 61.6927 | -0.028522 | 0.043657 | 61.5295 | -0.001436 | 61.3123 | 60.226 | 57.6276 | 61.017 | 62.7896 | 60.0902 | 60.1897 | 60.2521 | 123.1704 | 61.6897 | 123.1108 | 61.3896 | 61.4618 | 122.9477 | 61.4167 | 122.7305 | 61.7086 | 61.7537 | 61.649 | 61.6941
4537.0625 | 123.3765 | -61.4136 | 61.6791 | -1.1052 | -3.6944 | -0.24093 | 1.5042 | -1.2318 | -1.1368 | -1.2485 | 61.7386 | 0.27611 | 61.6606 | -0.042259 | 0.039079 | 61.525 | -0.001436 | 61.3215 | 60.3084 | 57.7192 | 61.1726 | 62.9178 | 60.1817 | 60.2767 | 60.1651 | 123.1521 | 61.6897 | 123.0742 | 61.3713 | 61.4527 | 122.9385 | 61.4121 | 122.735 | 61.6995 | 61.74 | 61.6216 | 61.6621
4538.0938 | 123.3856 | -61.4044 | 61.7065 | -1.1326 | -3.7219 | -0.37829 | 1.4493 | -1.4378 | -1.1689 | -1.4453 | 61.7386 | 0.27153 | 61.6561 | -0.03768 | 0.043657 | 61.5295 | 0.007721 | 61.3077 | 60.2718 | 57.6825 | 61.0261 | 62.8537 | 59.9666 | 60.2355 | 59.9591 | 123.143 | 61.6759 | 123.0605 | 61.3667 | 61.4481 | 122.934 | 61.4121 | 122.7121 | 61.6949 | 61.7308 | 61.6124 | 61.6483
4539.0625 | 123.349 | -61.4227 | 61.6974 | -1.1921 | -3.8821 | -0.51107 | 1.8934 | -1.3463 | -1.2193 | -1.4911 | 61.7614 | 0.28069 | 61.6835 | -0.028522 | 0.048236 | 61.525 | 0.003143 | 61.3031 | 60.2306 | 57.5406 | 60.9117 | 63.3161 | 60.0764 | 60.2035 | 59.9316 | 123.1842 | 61.7034 | 123.1063 | 61.3942 | 61.471 | 122.9477 | 61.4259 | 122.7259 | 61.7132 | 61.7583 | 61.6353 | 61.6804
4540.0781 | 123.3856 | -61.4319 | 61.7157 | -1.1509 | -3.9737 | -0.94603 | 1.8705 | -1.3325 | -1.1781 | -1.3858 | 61.7431 | 0.27611 | 61.6561 | -0.03768 | 0.048236 | 61.525 | 0.003143 | 61.3123 | 60.2809 | 57.4582 | 60.4858 | 63.3024 | 60.0993 | 60.2538 | 60.0461 | 123.175 | 61.708 | 123.0879 | 61.3942 | 61.4801 | 122.9568 | 61.435 | 122.7442 | 61.6949 | 61.74 | 61.6078 | 61.6529
4541.0625 | 123.3124 | -61.4182 | 61.7477 | -1.1555 | -3.9508 | -1.0513 | 1.898 | -1.1952 | -1.1964 | -1.4499 | 61.7477 | 0.27153 | 61.6652 | -0.028522 | 0.052814 | 61.5295 | 0.007721 | 61.3077 | 60.2626 | 57.4673 | 60.3668 | 63.3161 | 60.2229 | 60.2218 | 59.9682 | 123.1659 | 61.6897 | 123.0834 | 61.3896 | 61.471 | 122.9477 | 61.4259 | 122.7259 | 61.6949 | 61.74 | 61.6124 | 61.6575
4542.0781 | 123.2483 | -61.4685 | 61.734 | -1.0685 | -3.8364 | -0.84073 | 1.7148 | -0.76946 | -1.1048 | -1.3309 | 61.7431 | 0.28069 | 61.6835 | -0.033101 | 0.048236 | 61.5341 | 0.003143 | 61.3123 | 60.4 | 57.6321 | 60.6278 | 63.1833 | 60.699 | 60.3637 | 60.1376 | 123.2116 | 61.7492 | 123.152 | 61.4354 | 61.5167 | 123.0026 | 61.4716 | 122.7808 | 61.6949 | 61.74 | 61.6353 | 61.6804
4543.0625 | 123.3444 | -61.3953 | 61.734 | -1.0548 | -3.8226 | -0.84988 | 1.7698 | -0.76488 | -1.0865 | -1.221 | 61.7431 | 0.27153 | 61.6515 | -0.028522 | 0.043657 | 61.5341 | 0.012299 | 61.3215 | 60.3405 | 57.5726 | 60.5454 | 63.165 | 60.6304 | 60.3088 | 60.1743 | 123.1384 | 61.6668 | 123.0467 | 61.3667 | 61.4389 | 122.9294 | 61.4076 | 122.7167 | 61.6995 | 61.7308 | 61.6078 | 61.6392
4544.0938 | 123.4039 | -61.3815 | 61.6928 | -1.0731 | -3.9325 | -0.9323 | 1.7469 | -0.80608 | -1.1048 | -1.1889 | 61.734 | 0.27611 | 61.6515 | -0.03768 | 0.039079 | 61.5387 | 0.007721 | 61.3077 | 60.3084 | 57.449 | 60.4492 | 63.1284 | 60.5755 | 60.2767 | 60.1926 | 123.1155 | 61.6576 | 123.033 | 61.3439 | 61.4206 | 122.9202 | 61.3893 | 122.6893 | 61.6949 | 61.7263 | 61.6124 | 61.6438
4545.0625 | 123.3673 | -61.4227 | 61.6837 | -1.064 | -3.9005 | -0.74916 | 1.7606 | -0.81981 | -1.0956 | -1.2302 | 61.7477 | 0.27153 | 61.6744 | -0.028522 | 0.043657 | 61.5387 | 0.007721 | 61.3031 | 60.3588 | 57.5223 | 60.6736 | 63.1833 | 60.6029 | 60.3271 | 60.1926 | 123.1704 | 61.6943 | 123.0971 | 61.3942 | 61.4664 | 122.9614 | 61.4304 | 122.7259 | 61.7041 | 61.74 | 61.6307 | 61.6667
4546.0938 | 123.3124 | -61.4502 | 61.702 | -1.0731 | -3.8638 | -0.36913 | 1.669 | -0.92968 | -1.1048 | -1.2118 | 61.734 | 0.28069 | 61.6423 | -0.03768 | 0.043657 | 61.5478 | -0.001436 | 61.3123 | 60.3771 | 57.5864 | 61.0811 | 63.1192 | 60.5205 | 60.3454 | 60.2384 | 123.1842 | 61.7309 | 123.0925 | 61.4125 | 61.4939 | 122.998 | 61.4488 | 122.7625 | 61.6903 | 61.7354 | 61.5987 | 61.6438
4547.0625 | 123.3765 | -61.4227 | 61.6928 | -1.064 | -3.9005 | -0.34624 | 2.0353 | -0.86101 | -1.0956 | -1.2027 | 61.7248 | 0.27153 | 61.6515 | -0.033101 | 0.043657 | 61.5387 | 0.007721 | 61.3077 | 60.3588 | 57.5223 | 61.0765 | 63.458 | 60.5617 | 60.3271 | 60.22 | 123.1475 | 61.6943 | 123.0742 | 61.3896 | 61.4664 | 122.9614 | 61.4304 | 122.7305 | 61.6812 | 61.7171 | 61.6078 | 61.6438
4548.0938 | 123.2758 | -61.4548 | 61.7569 | -1.1326 | -3.9417 | -0.50649 | 1.9163 | -0.91137 | -1.1689 | -1.4224 | 61.7523 | 0.28069 | 61.6881 | -0.028522 | 0.048236 | 61.5295 | 0.007721 | 61.3123 | 60.3221 | 57.5131 | 60.9483 | 63.371 | 60.5434 | 60.2859 | 60.0323 | 123.2071 | 61.7355 | 123.1429 | 61.4263 | 61.503 | 122.9843 | 61.4625 | 122.7671 | 61.7041 | 61.7446 | 61.6399 | 61.6804
4549.0625 | 123.3444 | -61.3998 | 61.7249 | -1.2288 | -4.0287 | -1.5184 | 1.8476 | -1.0396 | -1.2605 | -1.7475 | 61.7523 | 0.28526 | 61.6515 | -0.033101 | 0.048236 | 61.5204 | 0.007721 | 61.2894 | 60.1711 | 57.3712 | 59.8815 | 63.2474 | 60.3603 | 60.1394 | 59.6524 | 123.1521 | 61.6851 | 123.0513 | 61.3667 | 61.4481 | 122.9202 | 61.4076 | 122.6893 | 61.7041 | 61.7446 | 61.6032 | 61.6438
4550.0781 | 123.3627 | -61.3998 | 61.702 | -1.3249 | -4.0149 | -1.4222 | 1.7789 | -1.0487 | -1.3612 | -2.0313 | 61.7569 | 0.28069 | 61.6927 | -0.033101 | 0.043657 | 61.5158 | 0.003143 | 61.2848 | 60.0749 | 57.3849 | 59.9776 | 63.1788 | 60.3511 | 60.0387 | 59.3685 | 123.1567 | 61.6805 | 123.0925 | 61.3667 | 61.4435 | 122.9156 | 61.403 | 122.6847 | 61.7132 | 61.7537 | 61.649 | 61.6895
4551.0625 | 123.3856 | -61.3953 | 61.7249 | -1.2105 | -3.8638 | -1.207 | 1.8796 | -0.99378 | -1.2513 | -2.0176 | 61.7614 | 0.28069 | 61.6881 | -0.028522 | 0.039079 | 61.5295 | 0.012299 | 61.2894 | 60.1848 | 57.5314 | 60.1882 | 63.2749 | 60.4015 | 60.144 | 59.3777 | 123.1567 | 61.6759 | 123.0834 | 61.3667 | 61.4343 | 122.9248 | 61.4076 | 122.6847 | 61.7224 | 61.7491 | 61.649 | 61.6758
4552.0938 | 123.3856 | -61.3815 | 61.6974 | -1.302 | -4.0699 | -2.141 | 1.8064 | -1.0853 | -1.3337 | -1.8528 | 61.766 | 0.27611 | 61.6606 | -0.042259 | 0.034501 | 61.5112 | 0.003143 | 61.2894 | 60.0795 | 57.3117 | 59.2405 | 63.1879 | 60.2962 | 60.0478 | 59.5287 | 123.1476 | 61.6576 | 123.0422 | 61.3393 | 61.416 | 122.8928 | 61.3847 | 122.6709 | 61.7315 | 61.7629 | 61.6261 | 61.6575
4553.0625 | 123.317 | -61.409 | 61.7386 | -1.2746 | -3.9005 | -1.3261 | 1.843 | -0.9892 | -1.3108 | -1.7658 | 61.7569 | 0.27611 | 61.6835 | -0.028522 | 0.043657 | 61.5204 | 0.003143 | 61.2986 | 60.1344 | 57.5085 | 60.0829 | 63.252 | 60.4198 | 60.0982 | 59.6432 | 123.1659 | 61.6851 | 123.0925 | 61.3805 | 61.4527 | 122.9294 | 61.4121 | 122.7076 | 61.7132 | 61.7537 | 61.6399 | 61.6804
4554.0625 | 123.3902 | -61.3907 | 61.702 | -1.3661 | -4.0424 | -1.6832 | 1.8339 | -0.92511 | -1.407 | -1.7933 | 61.766 | 0.27611 | 61.7018 | -0.033101 | 0.043657 | 61.5204 | 0.007721 | 61.2986 | 60.0246 | 57.3483 | 59.7075 | 63.2245 | 60.4656 | 59.9837 | 59.5974 | 123.1567 | 61.6668 | 123.0925 | 61.3576 | 61.4343 | 122.9111 | 61.3984 | 122.6893 | 61.7224 | 61.7583 | 61.6582 | 61.6941
4555.0781 | 123.4039 | -61.3907 | 61.702 | -1.3799 | -3.992 | -1.6466 | 1.8384 | -0.77861 | -1.407 | -1.7063 | 61.7523 | 0.27611 | 61.6606 | -0.03768 | 0.039079 | 61.5158 | 0.003143 | 61.294 | 60.0108 | 57.3986 | 59.7441 | 63.2291 | 60.6121 | 59.9837 | 59.6844 | 123.143 | 61.6668 | 123.0513 | 61.353 | 61.4298 | 122.9065 | 61.3938 | 122.6847 | 61.7132 | 61.7491 | 61.6216 | 61.6575
4556.0625 | 123.4222 | -61.3815 | 61.7111 | -1.3661 | -3.9966 | -1.8205 | 2.0536 | -1.035 | -1.3978 | -1.688 | 61.766 | 0.28069 | 61.6973 | -0.033101 | 0.048236 | 61.5204 | 0.007721 | 61.2894 | 60.0154 | 57.3849 | 59.561 | 63.4352 | 60.3466 | 59.9837 | 59.6936 | 123.1476 | 61.6622 | 123.0788 | 61.3484 | 61.4298 | 122.9019 | 61.3893 | 122.6709 | 61.7178 | 61.7583 | 61.649 | 61.6895
4557.0781 | 123.3902 | -61.4136 | 61.7157 | -1.3753 | -4.1111 | -1.8526 | 1.5912 | -1.122 | -1.4116 | -1.3721 | 61.7614 | 0.28069 | 61.6835 | -0.03768 | 0.048236 | 61.5112 | 0.003143 | 61.2986 | 60.0383 | 57.3025 | 59.561 | 63.0048 | 60.2916 | 60.002 | 60.0415 | 123.175 | 61.6943 | 123.0971 | 61.3759 | 61.4618 | 122.9248 | 61.4167 | 122.7121 | 61.7132 | 61.7583 | 61.6353 | 61.6804
4558.0625 | 123.4268 | -61.3724 | 61.7386 | -1.3661 | -4.1706 | -1.8618 | 1.9483 | -1.1403 | -1.407 | -1.0837 | 61.7523 | 0.28069 | 61.6652 | -0.028522 | 0.043657 | 61.5204 | 0.003143 | 61.3031 | 60.0063 | 57.2018 | 59.5106 | 63.3207 | 60.2321 | 59.9654 | 60.2887 | 123.1247 | 61.6531 | 123.0376 | 61.3439 | 61.416 | 122.8928 | 61.3755 | 122.6755 | 61.7086 | 61.7491 | 61.6216 | 61.6621
4559.0781 | 123.3856 | -61.4136 | 61.6791 | -1.2974 | -4.0607 | -0.95061 | 2.0902 | -1.0258 | -1.3383 | -1.0608 | 61.7477 | 0.27611 | 61.6881 | -0.03768 | 0.048236 | 61.5387 | -0.001436 | 61.3215 | 60.1161 | 57.3529 | 60.463 | 63.5038 | 60.3878 | 60.0753 | 60.3528 | 123.1613 | 61.6897 | 123.1017 | 61.3759 | 61.4618 | 122.9523 | 61.4121 | 122.735 | 61.6995 | 61.7491 | 61.6399 | 61.6895
4560.0625 | 123.4222 | -61.3724 | 61.7065 | -1.3615 | -4.1798 | -1.1154 | 2.3238 | -1.1082 | -1.3932 | -1.1203 | 61.7477 | 0.27153 | 61.6561 | -0.03768 | 0.043657 | 61.5387 | 0.003143 | 61.326 | 60.0108 | 57.1926 | 60.2569 | 63.6961 | 60.2642 | 59.9791 | 60.2521 | 123.1201 | 61.6439 | 123.0284 | 61.3347 | 61.416 | 122.9111 | 61.3755 | 122.6984 | 61.7041 | 61.7446 | 61.6124 | 61.6529
4561.0938 | 123.3032 | -61.4319 | 61.7065 | -1.3844 | -4.2988 | -1.903 | 2.2093 | -0.83813 | -1.4253 | -1.0104 | 61.7569 | 0.27153 | 61.679 | -0.03768 | 0.043657 | 61.5204 | 0.003143 | 61.3123 | 60.0474 | 57.1331 | 59.5289 | 63.6412 | 60.5938 | 60.0066 | 60.4215 | 123.1888 | 61.7034 | 123.1108 | 61.3942 | 61.4755 | 122.9523 | 61.435 | 122.7442 | 61.7132 | 61.7537 | 61.6353 | 61.6758
4562.0625 | 123.3765 | -61.3678 | 61.7477 | -1.4302 | -4.2668 | -2.0907 | 2.049 | -1.0304 | -1.4619 | -1.1157 | 61.766 | 0.27153 | 61.711 | -0.033101 | 0.039079 | 61.5112 | 0.007721 | 61.3123 | 59.9376 | 57.101 | 59.2771 | 63.4168 | 60.3374 | 59.9059 | 60.2521 | 123.1338 | 61.6393 | 123.0788 | 61.3347 | 61.4069 | 122.879 | 61.3755 | 122.6801 | 61.7269 | 61.7583 | 61.6719 | 61.7033
4563.0938 | 123.4268 | -61.3861 | 61.7157 | -1.4943 | -4.3171 | -2.0357 | 2.0719 | -1.1403 | -1.526 | -1.5323 | 61.766 | 0.27611 | 61.6744 | -0.033101 | 0.048236 | 61.5158 | 0.007721 | 61.3077 | 59.8918 | 57.069 | 59.3504 | 63.458 | 60.2458 | 59.8601 | 59.8538 | 123.1521 | 61.6622 | 123.0605 | 61.353 | 61.4343 | 122.9019 | 61.3938 | 122.6938 | 61.7178 | 61.7583 | 61.6261 | 61.6667
4564.0625 | 123.4589 | -61.3678 | 61.7249 | -1.357 | -4.0974 | -2.1685 | 2.0124 | -0.96631 | -1.3978 | -1.6285 | 61.7614 | 0.27611 | 61.6973 | -0.028522 | 0.043657 | 61.5112 | 0.012299 | 61.3215 | 60.0108 | 57.2704 | 59.1993 | 63.3802 | 60.4015 | 59.97 | 59.7393 | 123.1292 | 61.6439 | 123.0651 | 61.3393 | 61.4115 | 122.879 | 61.3801 | 122.6893 | 61.7178 | 61.7491 | 61.6536 | 61.685
4565.0781 | 123.3994 | -61.3861 | 61.7249 | -1.302 | -3.905 | -2.0724 | 1.3943 | -0.83355 | -1.3383 | -1.6834 | 61.766 | 0.28069 | 61.7018 | -0.033101 | 0.048236 | 61.5204 | 0.007721 | 61.3123 | 60.0841 | 57.4811 | 59.3137 | 62.7804 | 60.5526 | 60.0478 | 59.7027 | 123.1521 | 61.6668 | 123.088 | 61.353 | 61.4343 | 122.9065 | 61.3938 | 122.6984 | 61.7178 | 61.7583 | 61.6536 | 61.6941
4566.0625 | 123.2849 | -61.441 | 61.7249 | -1.215 | -3.8318 | -1.0834 | 1.2386 | -0.71452 | -1.2559 | -1.7887 | 61.7523 | 0.28069 | 61.6652 | -0.042259 | 0.043657 | 61.5204 | 0.003143 | 61.3123 | 60.226 | 57.6093 | 60.3576 | 62.6797 | 60.7265 | 60.1852 | 59.6524 | 123.1933 | 61.7217 | 123.1063 | 61.3988 | 61.4847 | 122.9614 | 61.4442 | 122.7533 | 61.7086 | 61.7491 | 61.6216 | 61.6621
4567.0781 | 123.3536 | -61.3724 | 61.7111 | -1.2334 | -4.0104 | -2.1731 | 1.0967 | -0.84728 | -1.2696 | -1.8345 | 61.7706 | 0.27153 | 61.711 | -0.028522 | 0.048236 | 61.5112 | 0.007721 | 61.2986 | 60.139 | 57.362 | 59.1993 | 62.4691 | 60.5251 | 60.1028 | 59.5379 | 123.143 | 61.6439 | 123.0834 | 61.3439 | 61.4206 | 122.8836 | 61.3801 | 122.6709 | 61.7224 | 61.7629 | 61.6628 | 61.7033
4568.0625 | 123.349 | -61.3678 | 61.7432 | -1.27 | -4.1477 | -2.1594 | 2.0399 | -1.0258 | -1.3017 | -1.8665 | 61.7614 | 0.27611 | 61.6973 | -0.028522 | 0.043657 | 61.5158 | 0.003143 | 61.3169 | 60.0978 | 57.2201 | 59.2084 | 63.4077 | 60.342 | 60.0661 | 59.5013 | 123.1292 | 61.6439 | 123.0651 | 61.3393 | 61.4115 | 122.8836 | 61.3709 | 122.6847 | 61.7178 | 61.7583 | 61.6536 | 61.6941
4569.0938 | 123.381 | -61.3953 | 61.7386 | -1.2608 | -4.2942 | -2.2143 | 1.7698 | -1.0945 | -1.2925 | -1.6513 | 61.7614 | 0.27611 | 61.6698 | -0.033101 | 0.048236 | 61.5158 | 0.007721 | 61.2894 | 60.1344 | 57.101 | 59.181 | 63.165 | 60.3008 | 60.1028 | 59.7439 | 123.1567 | 61.6714 | 123.0651 | 61.3622 | 61.4435 | 122.9111 | 61.403 | 122.6847 | 61.7132 | 61.7537 | 61.6216 | 61.6621
4570.0625 | 123.4543 | -61.3541 | 61.7432 | -1.2379 | -4.2988 | -2.6722 | 1.7743 | -0.99835 | -1.2742 | -1.5735 | 61.7706 | 0.28069 | 61.7018 | -0.033101 | 0.043657 | 61.5066 | 0.003143 | 61.2986 | 60.1161 | 57.0552 | 58.6819 | 63.1284 | 60.3557 | 60.0799 | 59.7806 | 123.1247 | 61.6347 | 123.0559 | 61.321 | 61.3977 | 122.8607 | 61.3572 | 122.6526 | 61.7269 | 61.7675 | 61.6582 | 61.6987
4571.1094 | 123.3948 | -61.4044 | 61.7294 | -1.2379 | -4.253 | -2.4936 | 1.4584 | -1.0487 | -1.2788 | -1.4407 | 61.766 | 0.28069 | 61.6744 | -0.028522 | 0.052814 | 61.5112 | 0.007721 | 61.2986 | 60.1665 | 57.1514 | 58.9108 | 62.8628 | 60.3557 | 60.1256 | 59.9637 | 123.1704 | 61.6851 | 123.0788 | 61.3759 | 61.4572 | 122.9156 | 61.4121 | 122.703 | 61.7132 | 61.7583 | 61.6216 | 61.6667
4572.0625 | 123.4131 | -61.3632 | 61.734 | -1.2974 | -4.2347 | -1.3215 | 1.6782 | -1.035 | -1.3337 | -1.5277 | 61.7569 | 0.27611 | 61.6698 | -0.03768 | 0.048236 | 61.525 | 0.007721 | 61.3123 | 60.0658 | 57.1285 | 60.0417 | 63.0414 | 60.3282 | 60.0295 | 59.8355 | 123.1201 | 61.6393 | 123.033 | 61.3255 | 61.4115 | 122.8882 | 61.3709 | 122.6755 | 61.7086 | 61.7491 | 61.6216 | 61.6621
4573.0938 | 123.4085 | -61.3907 | 61.6974 | -1.3112 | -4.1248 | -1.1109 | 1.4905 | -1.0258 | -1.3429 | -1.6651 | 61.7614 | 0.27611 | 61.6973 | -0.033101 | 0.043657 | 61.5204 | 0.003143 | 61.3031 | 60.0795 | 57.2659 | 60.2798 | 62.8812 | 60.3649 | 60.0478 | 59.7256 | 123.1521 | 61.6668 | 123.088 | 61.3576 | 61.4343 | 122.9111 | 61.3938 | 122.6938 | 61.7178 | 61.7583 | 61.6536 | 61.6941
4574.0625 | 123.3994 | -61.3953 | 61.7386 | -1.3112 | -4.0745 | -1.1704 | 1.3119 | -1.1403 | -1.3429 | -1.8162 | 61.7569 | 0.28069 | 61.6698 | -0.033101 | 0.048236 | 61.5204 | 0.007721 | 61.3077 | 60.0841 | 57.3208 | 60.2249 | 62.7072 | 60.255 | 60.0524 | 59.5791 | 123.1521 | 61.6759 | 123.0651 | 61.3622 | 61.4435 | 122.9156 | 61.403 | 122.703 | 61.7086 | 61.7491 | 61.6216 | 61.6621
4575.0938 | 123.349 | -61.3998 | 61.702 | -1.2929 | -4.0332 | -1.6557 | 1.3989 | -0.95715 | -1.3337 | -1.7338 | 61.7614 | 0.28069 | 61.6835 | -0.033101 | 0.039079 | 61.5204 | -0.001436 | 61.2986 | 60.107 | 57.3666 | 59.7441 | 62.7987 | 60.4427 | 60.0661 | 59.6661 | 123.1613 | 61.6805 | 123.0834 | 61.3667 | 61.4389 | 122.9202 | 61.3984 | 122.6984 | 61.7224 | 61.7629 | 61.6445 | 61.685
4576.0625 | 123.2712 | -61.409 | 61.7798 | -1.3661 | -4.0653 | -1.729 | 1.7972 | -0.75572 | -1.407 | -1.807 | 61.7614 | 0.27611 | 61.6973 | -0.028522 | 0.052814 | 61.525 | 0.007721 | 61.3077 | 60.0429 | 57.3437 | 59.68 | 63.2062 | 60.6533 | 60.002 | 59.602 | 123.1704 | 61.6851 | 123.1063 | 61.3805 | 61.4618 | 122.934 | 61.4167 | 122.7167 | 61.7086 | 61.7537 | 61.6445 | 61.6895
4577.0781 | 123.3627 | -61.4136 | 61.6882 | -1.3707 | -4.0241 | -1.6282 | 1.8155 | -0.62754 | -1.4161 | -1.6742 | 61.7569 | 0.27611 | 61.6606 | -0.033101 | 0.043657 | 61.525 | 0.007721 | 61.3031 | 60.0429 | 57.3895 | 59.7853 | 63.2291 | 60.786 | 59.9974 | 59.7393 | 123.1704 | 61.6897 | 123.0742 | 61.3805 | 61.4572 | 122.9385 | 61.4213 | 122.7167 | 61.7132 | 61.7491 | 61.617 | 61.6529
4578.0625 | 123.4543 | -61.3724 | 61.7249 | -1.3432 | -4.1477 | -1.349 | 1.4676 | -0.60465 | -1.3703 | -1.775 | 61.7569 | 0.27611 | 61.6835 | -0.028522 | 0.043657 | 61.5158 | 0.007721 | 61.3123 | 60.0291 | 57.2247 | 60.0234 | 62.8399 | 60.7677 | 60.002 | 59.5974 | 123.1292 | 61.6485 | 123.0559 | 61.3439 | 61.416 | 122.8882 | 61.3801 | 122.6847 | 61.7132 | 61.7491 | 61.6399 | 61.6758
4579.0938 | 123.381 | -61.4044 | 61.7065 | -1.3432 | -4.1844 | -1.3444 | 1.4264 | -0.75572 | -1.3749 | -1.839 | 61.7614 | 0.28069 | 61.6973 | -0.028522 | 0.043657 | 61.5204 | -0.006014 | 61.3123 | 60.0612 | 57.2201 | 60.06 | 62.8308 | 60.6487 | 60.0295 | 59.5654 | 123.1659 | 61.6851 | 123.1017 | 61.3759 | 61.4481 | 122.9248 | 61.3984 | 122.7167 | 61.7178 | 61.7675 | 61.6536 | 61.7033
4580.0625 | 123.3948 | -61.3815 | 61.7477 | -1.3936 | -4.2164 | -2.0724 | 1.4126 | -0.8015 | -1.4253 | -1.9077 | 61.7569 | 0.27611 | 61.6744 | -0.03768 | 0.048236 | 61.5112 | 0.003143 | 61.3031 | 59.9879 | 57.1651 | 59.3092 | 62.7942 | 60.58 | 59.9562 | 59.4738 | 123.1384 | 61.6576 | 123.0559 | 61.3439 | 61.4298 | 122.8928 | 61.3847 | 122.6847 | 61.7086 | 61.7537 | 61.6261 | 61.6712
4581.1094 | 123.3536 | -61.3953 | 61.6928 | -1.3478 | -4.2072 | -2.4295 | 1.5317 | -0.64585 | -1.3841 | -1.8711 | 61.7706 | 0.28069 | 61.7064 | -0.033101 | 0.043657 | 61.5066 | -0.001436 | 61.3077 | 60.0475 | 57.188 | 58.9658 | 62.9269 | 60.7494 | 60.0112 | 59.5242 | 123.1659 | 61.6759 | 123.1017 | 61.3622 | 61.4389 | 122.9019 | 61.3938 | 122.703 | 61.7269 | 61.772 | 61.6628 | 61.7079
4582.0625 | 123.436 | -61.3403 | 61.7798 | -1.2929 | -4.2897 | -2.5073 | 1.6782 | -0.60923 | -1.3246 | -1.5644 | 61.766 | 0.27611 | 61.6881 | -0.028522 | 0.052814 | 61.5158 | 0.007721 | 61.3123 | 60.0475 | 57.0507 | 58.833 | 63.0185 | 60.7311 | 60.0158 | 59.776 | 123.1064 | 61.6164 | 123.0284 | 61.3118 | 61.3931 | 122.8561 | 61.3481 | 122.6526 | 61.7132 | 61.7583 | 61.6353 | 61.6804
4583.0781 | 123.349 | -61.4044 | 61.7157 | -1.2929 | -4.3629 | -2.2876 | 1.495 | -0.71452 | -1.3246 | -1.6422 | 61.766 | 0.27153 | 61.6744 | -0.03768 | 0.052814 | 61.5158 | -0.001436 | 61.2986 | 60.1115 | 57.0415 | 59.1169 | 62.8995 | 60.6899 | 60.0799 | 59.7622 | 123.1704 | 61.6759 | 123.0788 | 61.3667 | 61.4572 | 122.9202 | 61.403 | 122.703 | 61.7132 | 61.7675 | 61.6216 | 61.6758
4584.0625 | 123.3948 | -61.377 | 61.7294 | -1.2013 | -4.2942 | -2.2006 | 1.7606 | -0.55887 | -1.2422 | -1.4728 | 61.7614 | 0.27153 | 61.7064 | -0.028522 | 0.048236 | 61.5204 | 0.012299 | 61.3031 | 60.1756 | 57.0827 | 59.1764 | 63.1375 | 60.8181 | 60.1348 | 59.9042 | 123.1384 | 61.6485 | 123.0834 | 61.3484 | 61.4252 | 122.8973 | 61.3893 | 122.6801 | 61.7132 | 61.7491 | 61.6582 | 61.6941
4585.0781 | 123.3444 | -61.4182 | 61.6974 | -1.2242 | -4.3538 | -2.1868 | 1.8613 | -0.43984 | -1.2559 | -1.4682 | 61.7523 | 0.28069 | 61.6606 | -0.033101 | 0.048236 | 61.5204 | -0.001436 | 61.2986 | 60.194 | 57.0644 | 59.2313 | 63.2795 | 60.9783 | 60.1623 | 59.9499 | 123.1704 | 61.6988 | 123.0788 | 61.3851 | 61.4664 | 122.9385 | 61.4167 | 122.7167 | 61.7041 | 61.7537 | 61.6124 | 61.6621
4586.0625 | 123.381 | -61.3724 | 61.7249 | -1.2334 | -4.3675 | -2.8828 | 2.017 | -0.38949 | -1.2788 | -1.4499 | 61.7706 | 0.27611 | 61.6927 | -0.028522 | 0.052814 | 61.5158 | 0.007721 | 61.3123 | 60.139 | 57.0049 | 58.4896 | 63.3894 | 60.9829 | 60.0936 | 59.9225 | 123.143 | 61.6485 | 123.0651 | 61.3439 | 61.4252 | 122.8882 | 61.3801 | 122.6847 | 61.7178 | 61.7629 | 61.6399 | 61.685
4587.0781 | 123.4543 | -61.3861 | 61.647 | -1.1693 | -4.2256 | -3.1392 | 1.5775 | -0.29793 | -1.1964 | -1.601 | 61.766 | 0.27611 | 61.7018 | -0.03768 | 0.048236 | 61.5112 | 0.003143 | 61.294 | 60.2169 | 57.1605 | 58.2469 | 62.9636 | 61.0882 | 60.1897 | 59.7851 | 123.1521 | 61.6622 | 123.088 | 61.3484 | 61.4343 | 122.8973 | 61.3893 | 122.6801 | 61.7178 | 61.7629 | 61.6536 | 61.6987
4588.0625 | 123.3948 | -61.3861 | 61.7386 | -1.1143 | -4.0607 | -2.956 | 1.4126 | -0.29793 | -1.1506 | -1.5552 | 61.766 | 0.27611 | 61.6698 | -0.028522 | 0.043657 | 61.5158 | 0.003143 | 61.294 | 60.2718 | 57.3254 | 58.4301 | 62.7987 | 61.0882 | 60.2355 | 59.8309 | 123.1521 | 61.6622 | 123.0559 | 61.3576 | 61.4298 | 122.9019 | 61.3893 | 122.6801 | 61.7224 | 61.7629 | 61.6261 | 61.6667
4589.0938 | 123.3948 | -61.3907 | 61.7065 | -1.2105 | -4.1523 | -2.8553 | 0.93189 | -0.32539 | -1.2467 | -1.7246 | 61.7752 | 0.27611 | 61.711 | -0.03768 | 0.048236 | 61.5021 | -0.001436 | 61.2894 | 60.1802 | 57.2384 | 58.5354 | 62.3226 | 61.0653 | 60.144 | 59.6661 | 123.1659 | 61.6668 | 123.1017 | 61.353 | 61.4389 | 122.8928 | 61.3893 | 122.6801 | 61.7269 | 61.7766 | 61.6628 | 61.7124
4590.0625 | 123.3627 | -61.4227 | 61.7065 | -1.1693 | -4.1615 | -2.0266 | 0.87237 | -0.27046 | -1.2055 | -1.5872 | 61.7614 | 0.28069 | 61.6835 | -0.03768 | 0.039079 | 61.5158 | 0.003143 | 61.294 | 60.2535 | 57.2613 | 59.3961 | 62.2951 | 61.1523 | 60.2172 | 59.8355 | 123.1842 | 61.7034 | 123.1063 | 61.385 | 61.4618 | 122.9385 | 61.4259 | 122.7167 | 61.7224 | 61.7583 | 61.6445 | 61.6804
4591.0938 | 123.2803 | -61.4227 | 61.7752 | -1.1418 | -4.2072 | -1.6878 | 1.6507 | -0.32997 | -1.1872 | -1.4911 | 61.7523 | 0.27153 | 61.6606 | -0.028522 | 0.043657 | 61.5204 | 0.012299 | 61.3123 | 60.2809 | 57.2155 | 59.735 | 63.0734 | 61.0928 | 60.2355 | 59.9316 | 123.175 | 61.6943 | 123.0834 | 61.3942 | 61.4664 | 122.9431 | 61.435 | 122.735 | 61.7086 | 61.74 | 61.617 | 61.6483
4592.0625 | 123.3765 | -61.4227 | 61.6882 | -1.2242 | -4.3675 | -1.2162 | 1.4767 | -0.48105 | -1.2605 | -1.3034 | 61.7569 | 0.28526 | 61.6881 | -0.042259 | 0.043657 | 61.5341 | 0.003143 | 61.2986 | 60.1985 | 57.0552 | 60.2066 | 62.8995 | 60.9417 | 60.1623 | 60.1193 | 123.1796 | 61.708 | 123.1108 | 61.3805 | 61.4664 | 122.9568 | 61.4259 | 122.7213 | 61.7132 | 61.7537 | 61.6445 | 61.685
4593.0938 | 123.3765 | -61.4182 | 61.7111 | -1.3387 | -4.5186 | -2.4844 | 1.2936 | -0.57718 | -1.3703 | -0.77233 | 61.766 | 0.28069 | 61.679 | -0.033101 | 0.039079 | 61.5158 | -0.001436 | 61.294 | 60.0795 | 56.8995 | 58.9337 | 62.7117 | 60.841 | 60.0478 | 60.6458 | 123.1842 | 61.6988 | 123.0971 | 61.3851 | 61.4572 | 122.934 | 61.4167 | 122.7121 | 61.7269 | 61.7675 | 61.6399 | 61.6804
4594.0625 | 123.3719 | -61.4044 | 61.7203 | -1.2654 | -4.5232 | -2.5485 | 1.4767 | -0.4902 | -1.3062 | -0.68535 | 61.7614 | 0.28069 | 61.679 | -0.023943 | 0.043657 | 61.5204 | 0.012299 | 61.294 | 60.139 | 56.8812 | 58.8559 | 62.8811 | 60.9142 | 60.0982 | 60.7191 | 123.1659 | 61.6851 | 123.0834 | 61.3805 | 61.4481 | 122.9248 | 61.4167 | 122.6984 | 61.7178 | 61.7491 | 61.6353 | 61.6667
4595.0938 | 123.3994 | -61.377 | 61.6791 | -1.1693 | -4.5049 | -3.3269 | 1.5271 | -0.41695 | -1.2147 | -1.0608 | 61.7752 | 0.27611 | 61.711 | -0.046838 | 0.043657 | 61.5158 | 0.003143 | 61.2894 | 60.2077 | 56.8721 | 58.05 | 62.904 | 60.96 | 60.1623 | 60.3162 | 123.1521 | 61.6531 | 123.088 | 61.3301 | 61.4206 | 122.8928 | 61.3801 | 122.6664 | 61.7315 | 61.772 | 61.6673 | 61.7079
4596.0625 | 123.317 | -61.3861 | 61.7706 | -1.2059 | -4.4637 | -2.5302 | 1.6232 | -0.46273 | -1.2422 | -0.82727 | 61.7614 | 0.26695 | 61.6652 | -0.028522 | 0.048236 | 61.5204 | 0.012299 | 61.3077 | 60.1802 | 56.9224 | 58.8559 | 63.0093 | 60.9234 | 60.144 | 60.5588 | 123.1476 | 61.6531 | 123.0513 | 61.3576 | 61.4343 | 122.9065 | 61.3984 | 122.6938 | 61.7132 | 61.7491 | 61.617 | 61.6529
4597.0781 | 123.2666 | -61.4456 | 61.7432 | -1.183 | -4.3904 | -2.0495 | 1.7469 | -0.4902 | -1.2284 | -0.78149 | 61.7523 | 0.28069 | 61.6927 | -0.028522 | 0.048236 | 61.525 | 0.007721 | 61.294 | 60.2626 | 57.0552 | 59.3961 | 63.1925 | 60.9554 | 60.2172 | 60.6641 | 123.1979 | 61.7263 | 123.1383 | 61.4171 | 61.4939 | 122.9706 | 61.4533 | 122.7396 | 61.7041 | 61.7446 | 61.6445 | 61.685
4598.0625 | 123.4085 | -61.4273 | 61.6699 | -1.1143 | -4.2713 | -1.3398 | 1.9483 | -0.37575 | -1.1597 | -0.89137 | 61.7431 | 0.28069 | 61.6698 | -0.033101 | 0.039079 | 61.5341 | -0.001436 | 61.3077 | 60.313 | 57.156 | 60.0875 | 63.3756 | 61.0516 | 60.2676 | 60.5359 | 123.1704 | 61.708 | 123.0971 | 61.3942 | 61.4664 | 122.9614 | 61.4259 | 122.735 | 61.7041 | 61.7446 | 61.6307 | 61.6712
4599.0781 | 123.2666 | -61.4456 | 61.7157 | -1.1097 | -4.3034 | -1.4634 | 1.8888 | -0.36202 | -1.1506 | -0.97835 | 61.7386 | 0.28069 | 61.6515 | -0.033101 | 0.048236 | 61.5295 | 0.007721 | 61.3077 | 60.3359 | 57.1422 | 59.9822 | 63.3344 | 61.0836 | 60.295 | 60.4673 | 123.1842 | 61.7263 | 123.0971 | 61.4125 | 61.4939 | 122.9752 | 61.4533 | 122.7533 | 61.6903 | 61.7308 | 61.6032 | 61.6438
4600.0625 | 123.3902 | -61.3998 | 61.6837 | -1.2242 | -4.4453 | -2.1731 | 1.8476 | -0.52225 | -1.2742 | -0.88679 | 61.7614 | 0.27611 | 61.6973 | -0.033101 | 0.039079 | 61.525 | 0.003143 | 61.294 | 60.1756 | 56.9545 | 59.2267 | 63.2474 | 60.8776 | 60.1256 | 60.5131 | 123.1613 | 61.6759 | 123.0971 | 61.3667 | 61.4389 | 122.9248 | 61.403 | 122.6938 | 61.7224 | 61.7583 | 61.6582 | 61.6941
4601.1094 | 123.3536 | -61.4365 | 61.6928 | -1.2288 | -4.427 | -1.7107 | 1.9575 | -0.53598 | -1.2742 | -0.83185 | 61.7477 | 0.27153 | 61.6561 | -0.033101 | 0.048236 | 61.5204 | 0.003143 | 61.3077 | 60.2077 | 57.0094 | 59.7258 | 63.3939 | 60.9005 | 60.1623 | 60.6046 | 123.1842 | 61.708 | 123.0925 | 61.4034 | 61.4847 | 122.9568 | 61.4396 | 122.7442 | 61.6995 | 61.7446 | 61.6078 | 61.6529
4602.0625 | 123.3719 | -61.4136 | 61.6882 | -1.0731 | -4.3217 | -2.1136 | 2.3833 | -0.33913 | -1.114 | -0.90052 | 61.7431 | 0.28526 | 61.6652 | -0.03768 | 0.039079 | 61.5295 | -0.001436 | 61.3077 | 60.3405 | 57.0919 | 59.3 | 63.7968 | 61.0744 | 60.2996 | 60.5131 | 123.1567 | 61.6988 | 123.0788 | 61.3759 | 61.4527 | 122.9431 | 61.4121 | 122.7213 | 61.7041 | 61.7446 | 61.6261 | 61.6667
4603.0781 | 123.3536 | -61.4182 | 61.7432 | -1.1372 | -4.3767 | -2.3562 | 2.3375 | -0.36202 | -1.1643 | -0.98293 | 61.7569 | 0.27611 | 61.6973 | -0.033101 | 0.039079 | 61.5295 | 0.007721 | 61.3169 | 60.2809 | 57.0415 | 59.0619 | 63.7556 | 61.0561 | 60.2538 | 60.4352 | 123.175 | 61.6943 | 123.1154 | 61.3851 | 61.4572 | 122.9477 | 61.4259 | 122.735 | 61.7178 | 61.7491 | 61.6582 | 61.6895
4604.0625 | 123.3765 | -61.4136 | 61.702 | -1.2013 | -4.3904 | -1.99 | 1.4859 | -0.49478 | -1.2376 | -1.1752 | 61.7477 | 0.27153 | 61.6652 | -0.03768 | 0.043657 | 61.5204 | 0.007721 | 61.3031 | 60.2123 | 57.0232 | 59.4236 | 62.8995 | 60.9188 | 60.176 | 60.2384 | 123.1613 | 61.6851 | 123.0788 | 61.3759 | 61.4572 | 122.934 | 61.4213 | 122.7167 | 61.7041 | 61.74 | 61.6216 | 61.6575
4605.0781 | 123.2986 | -61.4136 | 61.7432 | -1.1967 | -4.4453 | -2.9835 | 1.495 | -0.48562 | -1.2238 | -1.1203 | 61.7706 | 0.27611 | 61.6973 | -0.028522 | 0.039079 | 61.5066 | 0.007721 | 61.2986 | 60.2168 | 56.9682 | 58.4301 | 62.9086 | 60.928 | 60.1897 | 60.2933 | 123.1842 | 61.6897 | 123.1108 | 61.3851 | 61.4527 | 122.9202 | 61.4213 | 122.7121 | 61.7315 | 61.7629 | 61.6582 | 61.6895
4606.0625 | 123.3627 | -61.4182 | 61.7157 | -1.2288 | -4.4133 | -2.3242 | 1.4401 | -0.54514 | -1.2559 | -1.0699 | 61.766 | 0.27611 | 61.6973 | -0.028522 | 0.039079 | 61.5204 | 0.007721 | 61.3169 | 60.1894 | 57.0049 | 59.094 | 62.8583 | 60.873 | 60.1623 | 60.3482 | 123.1842 | 61.6943 | 123.1154 | 61.3896 | 61.4572 | 122.9385 | 61.4259 | 122.735 | 61.7269 | 61.7583 | 61.6582 | 61.6895
4607.0938 | 123.4177 | -61.3953 | 61.6928 | -1.1189 | -4.3446 | -2.718 | 1.5408 | -0.42153 | -1.1506 | -1.0379 | 61.7569 | 0.28069 | 61.6652 | -0.033101 | 0.039079 | 61.5158 | 0.007721 | 61.3077 | 60.2764 | 57.0507 | 58.6773 | 62.9361 | 60.9737 | 60.2447 | 60.3574 | 123.1521 | 61.6759 | 123.0605 | 61.3622 | 61.4343 | 122.9111 | 61.403 | 122.703 | 61.7178 | 61.7491 | 61.6261 | 61.6575
4608.0625 | 123.3261 | -61.4044 | 61.6791 | -1.1601 | -4.2805 | -1.9671 | 1.463 | -0.42611 | -1.2009 | -1.0012 | 61.7569 | 0.28069 | 61.6881 | -0.03768 | 0.048236 | 61.525 | 0.007721 | 61.3077 | 60.2443 | 57.1239 | 59.4374 | 62.8674 | 60.9783 | 60.2035 | 60.4032 | 123.1613 | 61.6851 | 123.0925 | 61.3667 | 61.4527 | 122.9294 | 61.4121 | 122.7121 | 61.7086 | 61.7491 | 61.6399 | 61.6804
4609.0938 | 123.3398 | -61.4136 | 61.6882 | -1.1097 | -4.4133 | -2.0312 | 2.2688 | -0.33455 | -1.146 | -1.0562 | 61.7523 | 0.28069 | 61.6927 | -0.03768 | 0.043657 | 61.5341 | -0.001436 | 61.3169 | 60.3038 | 57.0003 | 59.3824 | 63.6824 | 61.079 | 60.2676 | 60.3574 | 123.1659 | 61.6943 | 123.1063 | 61.3759 | 61.4572 | 122.9477 | 61.4121 | 122.7305 | 61.7086 | 61.7537 | 61.649 | 61.6941
4610.0625 | 123.3307 | -61.409 | 61.6928 | -1.183 | -4.569 | -2.8828 | 2.5206 | -0.35744 | -1.2055 | -1.2988 | 61.7569 | 0.28526 | 61.6652 | -0.028522 | 0.039079 | 61.525 | 0.012299 | 61.2986 | 60.226 | 56.84 | 58.5262 | 63.9296 | 61.0516 | 60.2035 | 60.1102 | 123.1659 | 61.6943 | 123.0742 | 61.3805 | 61.4481 | 122.934 | 61.4213 | 122.7076 | 61.7178 | 61.7446 | 61.6261 | 61.6529
4611.1094 | 123.3719 | -61.4227 | 61.6745 | -1.2242 | -4.5736 | -1.729 | 2.4428 | -0.50851 | -1.2513 | -1.2347 | 61.7386 | 0.27611 | 61.6561 | -0.033101 | 0.043657 | 61.525 | 0.007721 | 61.3077 | 60.1985 | 56.8492 | 59.6938 | 63.8655 | 60.9142 | 60.1714 | 60.188 | 123.1613 | 61.6988 | 123.0788 | 61.3896 | 61.4664 | 122.9477 | 61.4304 | 122.7305 | 61.6949 | 61.7308 | 61.6124 | 61.6483
4612.0625 | 123.4177 | -61.3953 | 61.6653 | -1.2013 | -4.5003 | -2.2372 | 2.4199 | -0.39406 | -1.2284 | -1.1249 | 61.7523 | 0.27611 | 61.6698 | -0.03768 | 0.043657 | 61.5295 | 0.012299 | 61.2986 | 60.194 | 56.895 | 59.1581 | 63.8152 | 61.0012 | 60.1668 | 60.2704 | 123.1476 | 61.6714 | 123.0651 | 61.3576 | 61.4389 | 122.9248 | 61.4076 | 122.6938 | 61.7086 | 61.74 | 61.6261 | 61.6575
4613.0938 | 123.349 | -61.4273 | 61.7249 | -1.2562 | -4.4774 | -3.1071 | 2.3787 | -0.38033 | -1.2971 | -1.1249 | 61.7706 | 0.27611 | 61.7064 | -0.028522 | 0.052814 | 61.5204 | 0.007721 | 61.2894 | 60.1711 | 56.9499 | 58.3202 | 63.806 | 61.047 | 60.1302 | 60.3025 | 123.1979 | 61.7034 | 123.1337 | 61.3988 | 61.4801 | 122.9477 | 61.435 | 122.7167 | 61.7178 | 61.7629 | 61.6536 | 61.6987
4614.0625 | 123.3398 | -61.3907 | 61.7661 | -1.1647 | -4.4682 | -2.9103 | 1.9483 | -0.34371 | -1.1964 | -1.3171 | 61.766 | 0.27153 | 61.7018 | -0.028522 | 0.048236 | 61.5204 | 0.007721 | 61.2986 | 60.226 | 56.9224 | 58.4804 | 63.339 | 61.047 | 60.1943 | 60.0735 | 123.1567 | 61.6622 | 123.0925 | 61.3622 | 61.4389 | 122.9111 | 61.3984 | 122.6893 | 61.7178 | 61.7583 | 61.6536 | 61.6941
4615.0938 | 123.2803 | -61.4365 | 61.7111 | -1.1555 | -4.5827 | -2.4661 | 2.3466 | -0.36202 | -1.1872 | -1.4362 | 61.7569 | 0.28069 | 61.6652 | -0.033101 | 0.043657 | 61.5204 | 0.003143 | 61.3077 | 60.2809 | 56.8538 | 58.9703 | 63.7831 | 61.0744 | 60.2493 | 60.0003 | 123.1933 | 61.7171 | 123.1017 | 61.4034 | 61.4801 | 122.9568 | 61.4396 | 122.7442 | 61.7132 | 61.7537 | 61.6216 | 61.6621
4616.0625 | 123.2803 | -61.4319 | 61.7569 | -1.1097 | -4.5369 | -2.0449 | 2.4382 | -0.41237 | -1.1414 | -1.7063 | 61.7569 | 0.27611 | 61.6744 | -0.033101 | 0.043657 | 61.5204 | 0.012299 | 61.3123 | 60.3222 | 56.895 | 59.387 | 63.8701 | 61.0195 | 60.2905 | 59.7256 | 123.1888 | 61.708 | 123.1063 | 61.3988 | 61.4755 | 122.9523 | 61.4442 | 122.7442 | 61.7132 | 61.7446 | 61.6307 | 61.6621
4617.0781 | 123.3032 | -61.4227 | 61.734 | -1.0273 | -4.514 | -3.272 | 2.4245 | -0.32082 | -1.0682 | -1.839 | 61.7706 | 0.26695 | 61.7018 | -0.028522 | 0.034501 | 61.5158 | 0.003143 | 61.2848 | 60.3954 | 56.9087 | 58.1508 | 63.8472 | 61.1019 | 60.3546 | 59.5837 | 123.1933 | 61.6897 | 123.1246 | 61.3942 | 61.4572 | 122.9385 | 61.4259 | 122.7076 | 61.7361 | 61.7675 | 61.6673 | 61.6987
4618.0625 | 123.3582 | -61.4044 | 61.702 | -0.9266 | -4.427 | -2.8645 | 2.6946 | -0.16059 | -0.95829 | -1.7292 | 61.7569 | 0.28069 | 61.6881 | -0.033101 | 0.043657 | 61.525 | 0.007721 | 61.3031 | 60.4778 | 56.9774 | 58.5399 | 64.099 | 61.2438 | 60.4461 | 59.6752 | 123.1613 | 61.6851 | 123.0925 | 61.3713 | 61.4481 | 122.9294 | 61.4121 | 122.7076 | 61.7132 | 61.7491 | 61.6445 | 61.6804
4619.0781 | 123.3719 | -61.4044 | 61.7249 | -1.0044 | -4.4866 | -3.1667 | 2.6763 | -0.27046 | -1.0361 | -1.8574 | 61.7523 | 0.27611 | 61.6606 | -0.033101 | 0.043657 | 61.5158 | 0.007721 | 61.2986 | 60.4 | 56.9179 | 58.2378 | 64.0807 | 61.134 | 60.3683 | 59.5471 | 123.1567 | 61.6805 | 123.0651 | 61.3713 | 61.4481 | 122.9202 | 61.4121 | 122.703 | 61.7086 | 61.7446 | 61.617 | 61.6529
4620.0625 | 123.3627 | -61.409 | 61.7065 | -1.1189 | -4.656 | -3.4551 | 2.3329 | -0.45815 | -1.1414 | -1.9718 | 61.766 | 0.28069 | 61.679 | -0.028522 | 0.048236 | 61.5112 | 0.012299 | 61.2848 | 60.2901 | 56.753 | 57.9539 | 63.7419 | 60.9508 | 60.2676 | 59.4372 | 123.175 | 61.6897 | 123.088 | 61.3805 | 61.4572 | 122.9202 | 61.4213 | 122.6938 | 61.7178 | 61.7537 | 61.6307 | 61.6667
4621.1094 | 123.2758 | -61.4227 | 61.7203 | -1.1555 | -4.7247 | -3.5055 | 2.3741 | -0.45815 | -1.1735 | -1.981 | 61.7752 | 0.27611 | 61.7018 | -0.033101 | 0.052814 | 61.5066 | 0.012299 | 61.2894 | 60.2672 | 56.6981 | 57.9173 | 63.7968 | 60.9646 | 60.2493 | 59.4418 | 123.1979 | 61.6988 | 123.1246 | 61.3896 | 61.4755 | 122.9294 | 61.435 | 122.7121 | 61.7224 | 61.7629 | 61.649 | 61.6895
4622.0625 | 123.3353 | -61.3724 | 61.7249 | -1.0868 | -4.6972 | -3.4093 | 2.5573 | -0.37117 | -1.1231 | -2.0405 | 61.7752 | 0.28069 | 61.711 | -0.023943 | 0.039079 | 61.5112 | 0.003143 | 61.2986 | 60.2855 | 56.6752 | 57.9631 | 63.9296 | 61.0012 | 60.2493 | 59.3319 | 123.1476 | 61.6531 | 123.0834 | 61.3484 | 61.4115 | 122.8836 | 61.3755 | 122.6709 | 61.7361 | 61.772 | 61.6719 | 61.7079
4623.0781 | 123.2666 | -61.409 | 61.734 | -1.0502 | -4.6926 | -3.2079 | 2.6168 | -0.30708 | -1.0865 | -1.981 | 61.7706 | 0.28069 | 61.6835 | -0.033101 | 0.043657 | 61.5158 | 0.003143 | 61.3031 | 60.3588 | 56.7164 | 58.2011 | 64.0258 | 61.1019 | 60.3225 | 59.428 | 123.1796 | 61.6897 | 123.0925 | 61.3759 | 61.4527 | 122.9248 | 61.4121 | 122.7121 | 61.7269 | 61.7675 | 61.6399 | 61.6804
4624.0625 | 123.3673 | -61.3998 | 61.7386 | -1.0319 | -4.7247 | -3.4826 | 2.7129 | -0.3025 | -1.0682 | -1.6376 | 61.7614 | 0.28069 | 61.6606 | -0.033101 | 0.043657 | 61.525 | 0.007721 | 61.2986 | 60.3679 | 56.6752 | 57.9173 | 64.1128 | 61.0973 | 60.3317 | 59.7622 | 123.1613 | 61.6805 | 123.0605 | 61.3667 | 61.4435 | 122.9248 | 61.4076 | 122.6984 | 61.7178 | 61.7537 | 61.617 | 61.6529
4625.0938 | 123.3444 | -61.4182 | 61.702 | -1.0136 | -4.6148 | -3.4688 | 2.6946 | -0.22926 | -1.0453 | -1.3538 | 61.7523 | 0.27153 | 61.6835 | -0.03768 | 0.052814 | 61.5204 | 0.012299 | 61.294 | 60.4046 | 56.8034 | 57.9493 | 64.1128 | 61.1889 | 60.3729 | 60.0644 | 123.1704 | 61.6897 | 123.1017 | 61.3805 | 61.471 | 122.9385 | 61.4305 | 122.7121 | 61.6995 | 61.74 | 61.6307 | 61.6712
4626.0625 | 123.3444 | -61.3815 | 61.7935 | -0.99985 | -4.6789 | -3.6749 | 2.223 | -0.37575 | -1.0453 | -1.2668 | 61.7706 | 0.28526 | 61.7064 | -0.033101 | 0.052814 | 61.5204 | 0.003143 | 61.3031 | 60.3817 | 56.7027 | 57.7066 | 63.6046 | 61.0058 | 60.3363 | 60.1148 | 123.1521 | 61.6668 | 123.088 | 61.3484 | 61.4343 | 122.9019 | 61.3847 | 122.6847 | 61.7178 | 61.7675 | 61.6536 | 61.7033
4627.0781 | 123.3582 | -61.4273 | 61.6974 | -0.88539 | -4.6102 | -3.3223 | 2.7541 | -0.26588 | -0.91708 | -0.9463 | 61.7477 | 0.27611 | 61.6835 | -0.03768 | 0.039079 | 61.525 | 0.012299 | 61.3169 | 60.5419 | 56.8171 | 58.105 | 64.1814 | 61.1614 | 60.5102 | 60.481 | 123.175 | 61.7034 | 123.1108 | 61.3896 | 61.4664 | 122.9523 | 61.4396 | 122.7442 | 61.7086 | 61.7354 | 61.6445 | 61.6712
4628.0625 | 123.3856 | -61.3815 | 61.7203 | -0.87166 | -4.4957 | -3.2079 | 2.4932 | -0.22468 | -0.90793 | -0.83643 | 61.7386 | 0.27611 | 61.6469 | -0.03768 | 0.048236 | 61.5295 | 0.012299 | 61.3077 | 60.5099 | 56.8858 | 58.1737 | 63.8747 | 61.1569 | 60.4736 | 60.5451 | 123.1201 | 61.6576 | 123.0284 | 61.3439 | 61.4298 | 122.9111 | 61.3938 | 122.6893 | 61.6903 | 61.7263 | 61.5987 | 61.6346
4629.0781 | 123.3078 | -61.4136 | 61.7477 | -0.83961 | -4.4224 | -3.0201 | 2.5618 | -0.31624 | -0.8713 | -0.76318 | 61.7477 | 0.27611 | 61.6561 | -0.03768 | 0.039079 | 61.525 | 0.003143 | 61.3123 | 60.574 | 56.9911 | 58.3934 | 63.9754 | 61.0973 | 60.5423 | 60.6504 | 123.1613 | 61.6897 | 123.0696 | 61.3759 | 61.4527 | 122.9385 | 61.4167 | 122.7259 | 61.7086 | 61.7446 | 61.617 | 61.6529
4630.0625 | 123.3856 | -61.4456 | 61.6699 | -0.62901 | -4.134 | -1.9671 | 3.5691 | 0.008797 | -0.64696 | -0.59379 | 61.7248 | 0.27153 | 61.6698 | -0.028522 | 0.048236 | 61.557 | 0.003143 | 61.3352 | 60.8166 | 57.3116 | 59.4786 | 65.0147 | 61.4544 | 60.7987 | 60.8518 | 123.1704 | 61.7171 | 123.1154 | 61.4171 | 61.4939 | 123.0026 | 61.4488 | 122.7808 | 61.6766 | 61.7217 | 61.6216 | 61.6667
4631.0938 | 123.3307 | -61.4319 | 61.7157 | -0.70684 | -4.2301 | -1.8526 | 3.7568 | -0.073606 | -0.74311 | -0.67161 | 61.7294 | 0.27611 | 61.6561 | -0.033101 | 0.048236 | 61.5524 | 0.007721 | 61.3535 | 60.725 | 57.2017 | 59.5793 | 65.1887 | 61.3583 | 60.6888 | 60.7603 | 123.1613 | 61.708 | 123.0879 | 61.3988 | 61.4801 | 122.9843 | 61.4396 | 122.7854 | 61.6812 | 61.7217 | 61.6078 | 61.6483
4632.0625 | 123.4406 | -61.4182 | 61.6882 | -0.67479 | -4.1981 | -1.6969 | 3.5599 | -0.050716 | -0.72479 | -0.66246 | 61.7157 | 0.28069 | 61.624 | -0.042259 | 0.048236 | 61.5616 | 0.012299 | 61.3627 | 60.7434 | 57.2201 | 59.7212 | 64.9781 | 61.3674 | 60.6934 | 60.7557 | 123.1338 | 61.6988 | 123.0422 | 61.3759 | 61.4664 | 122.9797 | 61.4305 | 122.7808 | 61.6674 | 61.7034 | 61.5758 | 61.6117
4633.0938 | 123.3765 | -61.4456 | 61.6699 | -0.81672 | -4.34 | -2.4203 | 3.2852 | -0.11481 | -0.84383 | -0.9692 | 61.7386 | 0.28526 | 61.6606 | -0.033101 | 0.043657 | 61.5478 | 0.003143 | 61.3306 | 60.6289 | 57.1056 | 59.0253 | 64.7309 | 61.3308 | 60.6018 | 60.4764 | 123.1842 | 61.7309 | 123.1063 | 61.4125 | 61.4893 | 122.9935 | 61.4488 | 122.7762 | 61.6949 | 61.7354 | 61.617 | 61.6575
4634.0625 | 123.3948 | -61.409 | 61.7065 | -0.80756 | -4.4545 | -3.2949 | 3.1708 | -0.12854 | -0.85757 | -1.1294 | 61.7569 | 0.28069 | 61.6927 | -0.03768 | 0.048236 | 61.5295 | 0.012299 | 61.3215 | 60.6014 | 56.9545 | 58.1141 | 64.5798 | 61.2805 | 60.5514 | 60.2796 | 123.1659 | 61.6897 | 123.1017 | 61.3713 | 61.4572 | 122.9385 | 61.4213 | 122.7305 | 61.7086 | 61.7446 | 61.6445 | 61.6804
4635.0938 | 123.3536 | -61.409 | 61.6882 | -0.88082 | -4.4591 | -3.4414 | 3.1937 | -0.18805 | -0.91251 | -1.1706 | 61.7431 | 0.27153 | 61.6515 | -0.028522 | 0.043657 | 61.5295 | 0.003143 | 61.3215 | 60.5282 | 56.9499 | 57.9676 | 64.6027 | 61.2209 | 60.4965 | 60.2384 | 123.1521 | 61.6805 | 123.0605 | 61.3805 | 61.4527 | 122.9385 | 61.4121 | 122.7305 | 61.6995 | 61.74 | 61.6078 | 61.6483
4636.0625 | 123.4085 | -61.3815 | 61.702 | -0.77094 | -4.4911 | -2.8828 | 3.0609 | -0.22926 | -0.81178 | -1.1798 | 61.7477 | 0.28069 | 61.6744 | -0.023943 | 0.048236 | 61.5295 | 0.012299 | 61.3077 | 60.6106 | 56.8904 | 58.4987 | 64.4424 | 61.1523 | 60.5697 | 60.2017 | 123.1292 | 61.6622 | 123.0559 | 61.3576 | 61.4298 | 122.9111 | 61.3938 | 122.6893 | 61.6995 | 61.7354 | 61.6261 | 61.6621
4637.0938 | 123.4039 | -61.4319 | 61.6745 | -0.60153 | -4.2805 | -1.9121 | 3.2257 | -0.091918 | -0.63322 | -1.2622 | 61.7386 | 0.27153 | 61.6652 | -0.03768 | 0.052814 | 61.5478 | -0.001436 | 61.3352 | 60.8304 | 57.1514 | 59.5198 | 64.6576 | 61.34 | 60.7987 | 60.1697 | 123.1704 | 61.7034 | 123.0971 | 61.3942 | 61.4847 | 122.9797 | 61.4304 | 122.7671 | 61.6857 | 61.74 | 61.6124 | 61.6667
4638.0625 | 123.4543 | -61.4044 | 61.6928 | -0.66563 | -4.4133 | -2.3883 | 3.9445 | -0.059872 | -0.7019 | -1.4224 | 61.7294 | 0.27153 | 61.6286 | -0.028522 | 0.043657 | 61.5433 | 0.007721 | 61.3306 | 60.7388 | 56.9911 | 59.0161 | 65.349 | 61.3445 | 60.7025 | 59.982 | 123.1338 | 61.6759 | 123.033 | 61.3759 | 61.4481 | 122.9477 | 61.4121 | 122.735 | 61.6857 | 61.7217 | 61.5849 | 61.6209
4639.0781 | 123.3673 | -61.4136 | 61.647 | -0.65648 | -4.4362 | -2.6493 | 3.6286 | -0.06445 | -0.7019 | -1.5048 | 61.7386 | 0.27611 | 61.6698 | -0.033101 | 0.048236 | 61.5433 | 0.003143 | 61.3169 | 60.7571 | 56.9774 | 58.7643 | 65.0422 | 61.3491 | 60.7117 | 59.9087 | 123.1521 | 61.6897 | 123.0834 | 61.3805 | 61.4618 | 122.9568 | 61.4167 | 122.7305 | 61.6903 | 61.7354 | 61.6216 | 61.6667
4640.0625 | 123.3902 | -61.409 | 61.702 | -0.63816 | -4.3217 | -2.6859 | 3.2395 | -0.046138 | -0.67901 | -1.4224 | 61.7523 | 0.28069 | 61.6744 | -0.028522 | 0.048236 | 61.5387 | 0.007721 | 61.3123 | 60.7708 | 57.0873 | 58.7231 | 64.6484 | 61.3629 | 60.73 | 59.9866 | 123.1613 | 61.6897 | 123.0834 | 61.3805 | 61.4572 | 122.9477 | 61.4167 | 122.7213 | 61.7041 | 61.7446 | 61.6261 | 61.6667
4641.0625 | 123.2437 | -61.441 | 61.7569 | -0.63358 | -4.3126 | -3.2216 | 3.4592 | 0.031687 | -0.66527 | -1.0424 | 61.7386 | 0.28069 | 61.6377 | -0.028522 | 0.048236 | 61.5478 | 0.012299 | 61.3169 | 60.8075 | 57.1285 | 58.2194 | 64.9003 | 61.4727 | 60.7758 | 60.3986 | 123.1796 | 61.7217 | 123.0788 | 61.4125 | 61.4893 | 122.9889 | 61.4533 | 122.7579 | 61.6903 | 61.7263 | 61.5895 | 61.6255
4642.0938 | 123.4177 | -61.4227 | 61.647 | -0.60153 | -4.3171 | -3.0385 | 4.059 | -0.009515 | -0.63322 | -0.99667 | 61.7386 | 0.26695 | 61.6744 | -0.033101 | 0.043657 | 61.5433 | 0.007721 | 61.3352 | 60.8212 | 57.1056 | 58.3843 | 65.4817 | 61.4132 | 60.7895 | 60.4261 | 123.1613 | 61.6897 | 123.0971 | 61.3896 | 61.4664 | 122.966 | 61.4304 | 122.7579 | 61.6949 | 61.7308 | 61.6307 | 61.6667
4643.0625 | 123.3948 | -61.4182 | 61.6928 | -0.6519 | -4.3446 | -3.217 | 3.6469 | -0.1377 | -0.68817 | -0.98751 | 61.734 | 0.27611 | 61.6652 | -0.033101 | 0.048236 | 61.5478 | 0.007721 | 61.3306 | 60.7663 | 57.0735 | 58.2011 | 65.0651 | 61.2805 | 60.73 | 60.4306 | 123.1521 | 61.6943 | 123.0834 | 61.3851 | 61.4664 | 122.966 | 61.4259 | 122.7488 | 61.6857 | 61.7263 | 61.617 | 61.6575
4644.0781 | 123.4085 | -61.4136 | 61.6837 | -0.71599 | -4.4408 | -3.5558 | 3.6469 | -0.22468 | -0.75226 | -0.89594 | 61.7386 | 0.27153 | 61.6423 | -0.028522 | 0.043657 | 61.5387 | 0.007721 | 61.3077 | 60.6976 | 56.9728 | 57.8577 | 65.0605 | 61.1889 | 60.6613 | 60.5176 | 123.1521 | 61.6851 | 123.0559 | 61.3851 | 61.4572 | 122.9523 | 61.4213 | 122.7213 | 61.6949 | 61.7308 | 61.5987 | 61.6346
4645.0625 | 123.4131 | -61.3998 | 61.7111 | -0.8625 | -4.5781 | -3.597 | 3.2669 | -0.34828 | -0.90793 | -0.84101 | 61.7523 | 0.28526 | 61.6835 | -0.028522 | 0.052814 | 61.5295 | 0.007721 | 61.3123 | 60.5373 | 56.8217 | 57.8028 | 64.6668 | 61.0516 | 60.4919 | 60.5588 | 123.1521 | 61.6851 | 123.0834 | 61.3713 | 61.4527 | 122.9294 | 61.4076 | 122.7121 | 61.6995 | 61.7446 | 61.6307 | 61.6758
4646.0625 | 123.3261 | -61.4044 | 61.7569 | -0.94949 | -4.5873 | -3.0568 | 2.9602 | -0.43527 | -0.99034 | -0.82269 | 61.7614 | 0.27611 | 61.6973 | -0.028522 | 0.048236 | 61.5295 | 0.007721 | 61.3123 | 60.4549 | 56.8171 | 58.3476 | 64.3646 | 60.9692 | 60.4141 | 60.5817 | 123.1659 | 61.6805 | 123.1017 | 61.3759 | 61.4527 | 122.934 | 61.4121 | 122.7167 | 61.7132 | 61.7537 | 61.649 | 61.6895
4647.0938 | 123.4268 | -61.409 | 61.7157 | -0.85792 | -4.4866 | -2.9881 | 3.2257 | -0.22468 | -0.88504 | -0.72197 | 61.7431 | 0.27153 | 61.6652 | -0.028522 | 0.048236 | 61.5387 | 0.003143 | 61.326 | 60.5511 | 56.9224 | 58.4209 | 64.6347 | 61.1843 | 60.524 | 60.687 | 123.1521 | 61.6805 | 123.0742 | 61.3805 | 61.4572 | 122.9477 | 61.4121 | 122.735 | 61.6949 | 61.74 | 61.617 | 61.6621
4648.0625 | 123.4222 | -61.377 | 61.7203 | -0.72515 | -4.4362 | -3.4505 | 3.1433 | -0.096496 | -0.75226 | -0.82727 | 61.7431 | 0.28069 | 61.6423 | -0.023943 | 0.048236 | 61.5341 | 0.007721 | 61.326 | 60.6518 | 56.9408 | 57.9264 | 64.5203 | 61.2805 | 60.6247 | 60.5497 | 123.1201 | 61.6576 | 123.0193 | 61.353 | 61.4252 | 122.9111 | 61.3847 | 122.703 | 61.6949 | 61.7354 | 61.5941 | 61.6346
4649.0938 | 123.3948 | -61.4136 | 61.6974 | -0.61527 | -4.4041 | -3.3406 | 3.5096 | 0.017953 | -0.6378 | -0.82727 | 61.734 | 0.28069 | 61.6744 | -0.028522 | 0.043657 | 61.5341 | 0.007721 | 61.3306 | 60.7983 | 57.0094 | 58.0729 | 64.9232 | 61.4315 | 60.7758 | 60.5863 | 123.1475 | 61.6943 | 123.088 | 61.3851 | 61.4572 | 122.9477 | 61.4213 | 122.7442 | 61.6903 | 61.7263 | 61.6307 | 61.6667
4650.0625 | 123.3307 | -61.409 | 61.7477 | -0.71142 | -4.4682 | -3.2765 | 3.2395 | -0.19263 | -0.74768 | -0.9051 | 61.7386 | 0.28069 | 61.679 | -0.033101 | 0.052814 | 61.5295 | 0.007721 | 61.326 | 60.6976 | 56.9408 | 58.1325 | 64.6484 | 61.2164 | 60.6613 | 60.5039 | 123.1476 | 61.6897 | 123.088 | 61.3759 | 61.4618 | 122.9385 | 61.4167 | 122.735 | 61.6857 | 61.7308 | 61.6261 | 61.6712
4651.0938 | 123.4268 | -61.3907 | 61.6699 | -0.63358 | -4.3812 | -3.1026 | 3.4958 | -0.036983 | -0.66527 | -1.1981 | 61.734 | 0.28069 | 61.6469 | -0.03768 | 0.048236 | 61.5387 | 0.007721 | 61.326 | 60.7571 | 57.0094 | 58.2881 | 64.8865 | 61.3537 | 60.7254 | 60.1926 | 123.1247 | 61.6714 | 123.0376 | 61.353 | 61.4389 | 122.9294 | 61.3984 | 122.7167 | 61.6857 | 61.7263 | 61.5987 | 61.6392
4652.0625 | 123.2849 | -61.4182 | 61.7249 | -0.63816 | -4.395 | -2.9835 | 3.5783 | -0.009515 | -0.66527 | -1.015 | 61.7431 | 0.27153 | 61.6744 | -0.042259 | 0.043657 | 61.5478 | 0.007721 | 61.3352 | 60.78 | 57.0232 | 58.4346 | 64.9964 | 61.4086 | 60.7529 | 60.4032 | 123.1613 | 61.6897 | 123.0925 | 61.3759 | 61.4618 | 122.966 | 61.4259 | 122.7533 | 61.6995 | 61.7354 | 61.6307 | 61.6667
4653.0938 | 123.3765 | -61.4182 | 61.702 | -0.69768 | -4.5827 | -3.2079 | 3.4867 | -0.050716 | -0.72937 | -0.68993 | 61.7431 | 0.28069 | 61.6744 | -0.03768 | 0.043657 | 61.5387 | 0.007721 | 61.3306 | 60.7205 | 56.8354 | 58.2103 | 64.9048 | 61.3674 | 60.6888 | 60.7282 | 123.1613 | 61.6988 | 123.0925 | 61.3805 | 61.4618 | 122.9568 | 61.4259 | 122.7488 | 61.6995 | 61.7354 | 61.6307 | 61.6667
4654.0625 | 123.4177 | -61.4044 | 61.7294 | -0.6519 | -4.6102 | -3.1712 | 3.4134 | -0.11939 | -0.68359 | -0.80896 | 61.734 | 0.27611 | 61.6423 | -0.028522 | 0.043657 | 61.5387 | 0.003143 | 61.3306 | 60.7525 | 56.7942 | 58.2332 | 64.8179 | 61.285 | 60.7208 | 60.5955 | 123.1384 | 61.6805 | 123.0467 | 61.3759 | 61.4481 | 122.9431 | 61.4076 | 122.735 | 61.6903 | 61.7308 | 61.5987 | 61.6392
4655.0781 | 123.3673 | -61.4319 | 61.6745 | -0.5878 | -4.5232 | -2.5485 | 3.4913 | -0.023249 | -0.60575 | -0.89137 | 61.734 | 0.28069 | 61.6744 | -0.03768 | 0.057392 | 61.5524 | 0.007721 | 61.3306 | 60.8441 | 56.9087 | 58.8833 | 64.9232 | 61.4086 | 60.8261 | 60.5405 | 123.1659 | 61.7126 | 123.1063 | 61.3942 | 61.4893 | 122.9843 | 61.4396 | 122.7625 | 61.6766 | 61.7263 | 61.617 | 61.6667
4656.0625 | 123.3032 | -61.4227 | 61.7203 | -0.60611 | -4.5094 | -2.5943 | 3.4592 | -0.009515 | -0.6378 | -0.87763 | 61.7294 | 0.27153 | 61.6515 | -0.028522 | 0.048236 | 61.557 | 0.012299 | 61.3352 | 60.8166 | 56.9133 | 58.8284 | 64.8819 | 61.4132 | 60.7849 | 60.5451 | 123.1521 | 61.6943 | 123.0742 | 61.3942 | 61.471 | 122.9797 | 61.435 | 122.7579 | 61.6812 | 61.7171 | 61.6032 | 61.6392
4657.0781 | 123.4039 | -61.4182 | 61.6791 | -0.60153 | -4.4453 | -2.6447 | 3.624 | 0.077466 | -0.6378 | -0.9463 | 61.7248 | 0.28069 | 61.6377 | -0.03768 | 0.052814 | 61.5478 | 0.007721 | 61.3306 | 60.8166 | 56.9728 | 58.7735 | 65.0422 | 61.4956 | 60.7803 | 60.4718 | 123.143 | 61.6988 | 123.0559 | 61.3805 | 61.471 | 122.966 | 61.4259 | 122.7488 | 61.672 | 61.7171 | 61.5849 | 61.63
4658.0625 | 123.2712 | -61.3998 | 61.7752 | -0.61527 | -4.4911 | -3.2811 | 3.5279 | 0.06831 | -0.64238 | -1.0928 | 61.7431 | 0.27611 | 61.6881 | -0.023943 | 0.043657 | 61.5433 | -0.001436 | 61.3306 | 60.7846 | 56.9087 | 58.1187 | 64.9277 | 61.4682 | 60.7575 | 60.307 | 123.143 | 61.6759 | 123.088 | 61.3759 | 61.4435 | 122.9431 | 61.3984 | 122.7305 | 61.6995 | 61.7446 | 61.6445 | 61.6895
4659.0781 | 123.4085 | -61.4044 | 61.7111 | -0.53744 | -4.4087 | -3.3498 | 3.9354 | 0.13698 | -0.56913 | -1.2347 | 61.734 | 0.28526 | 61.6515 | -0.03768 | 0.048236 | 61.5478 | 0.003143 | 61.3352 | 60.867 | 56.9957 | 58.0546 | 65.3398 | 61.5414 | 60.8353 | 60.1697 | 123.1384 | 61.6897 | 123.0559 | 61.3667 | 61.4527 | 122.9523 | 61.4076 | 122.7396 | 61.6857 | 61.7308 | 61.6032 | 61.6483
4660.0625 | 123.3215 | -61.4136 | 61.734 | -0.49165 | -4.4637 | -3.7985 | 4.1048 | 0.19192 | -0.50961 | -1.1065 | 61.734 | 0.27153 | 61.6377 | -0.023943 | 0.048236 | 61.5478 | 0.012299 | 61.326 | 60.9219 | 56.9499 | 57.6151 | 65.5184 | 61.6055 | 60.904 | 60.307 | 123.1475 | 61.6851 | 123.0513 | 61.3896 | 61.4618 | 122.9614 | 61.4259 | 122.7396 | 61.6857 | 61.7217 | 61.5895 | 61.6255
4661.0938 | 123.4451 | -61.377 | 61.7111 | -0.55575 | -4.5919 | -4.0274 | 3.8621 | 0.15529 | -0.58286 | -1.0653 | 61.7477 | 0.27611 | 61.6835 | -0.033101 | 0.039079 | 61.5341 | 0.007721 | 61.326 | 60.8212 | 56.7851 | 57.3495 | 65.2391 | 61.5322 | 60.7941 | 60.3116 | 123.1247 | 61.6531 | 123.0605 | 61.3439 | 61.416 | 122.9111 | 61.3847 | 122.703 | 61.7086 | 61.74 | 61.6445 | 61.6758
4662.0625 | 123.3078 | -61.4273 | 61.7386 | -0.49623 | -4.5003 | -3.6611 | 4.1094 | 0.20565 | -0.51419 | -1.102 | 61.734 | 0.28069 | 61.6423 | -0.033101 | 0.048236 | 61.5478 | 0.003143 | 61.3398 | 60.9311 | 56.927 | 57.7662 | 65.5367 | 61.633 | 60.9131 | 60.3253 | 123.1613 | 61.708 | 123.0696 | 61.3942 | 61.4755 | 122.9752 | 61.4305 | 122.7671 | 61.6857 | 61.7308 | 61.5941 | 61.6392
4663.0781 | 123.3765 | -61.409 | 61.6974 | -0.47792 | -4.3675 | -3.5146 | 4.0453 | 0.19192 | -0.50503 | -1.0287 | 61.7248 | 0.28069 | 61.6377 | -0.03768 | 0.052814 | 61.5433 | 0.007721 | 61.3489 | 60.9311 | 57.0415 | 57.8944 | 65.4543 | 61.6009 | 60.904 | 60.3803 | 123.1338 | 61.6897 | 123.0467 | 61.3713 | 61.4618 | 122.9523 | 61.4167 | 122.7579 | 61.672 | 61.7171 | 61.5849 | 61.63
4664.0625 | 123.3261 | -61.4365 | 61.7157 | -0.43671 | -4.1752 | -2.2555 | 3.8484 | 0.19192 | -0.4684 | -0.91884 | 61.734 | 0.27611 | 61.6561 | -0.033101 | 0.052814 | 61.5524 | 0.007721 | 61.3627 | 60.9997 | 57.2613 | 59.1809 | 65.2849 | 61.6284 | 60.9681 | 60.5176 | 123.1704 | 61.7126 | 123.0925 | 61.4034 | 61.4893 | 122.9889 | 61.4442 | 122.7991 | 61.6812 | 61.7263 | 61.6032 | 61.6483
4665.0781 | 123.4406 | -61.4182 | 61.6974 | -0.53744 | -4.4499 | -3.4368 | 3.5783 | 0.14614 | -0.55997 | -0.96462 | 61.7248 | 0.27611 | 61.6423 | -0.033101 | 0.048236 | 61.5433 | 0.003143 | 61.3398 | 60.8807 | 56.9682 | 57.9814 | 64.9964 | 61.5643 | 60.8582 | 60.4535 | 123.143 | 61.6943 | 123.0605 | 61.3851 | 61.4664 | 122.9614 | 61.4213 | 122.7579 | 61.6766 | 61.7217 | 61.5941 | 61.6392
4666.0625 | 123.2803 | -61.4456 | 61.702 | -0.53744 | -4.3629 | -3.6291 | 3.8804 | 0.19649 | -0.55539 | -1.0562 | 61.734 | 0.27153 | 61.6515 | -0.023943 | 0.043657 | 61.5387 | 0.007721 | 61.3398 | 60.9082 | 57.0827 | 57.8165 | 65.3261 | 61.6421 | 60.8902 | 60.3894 | 123.1796 | 61.7171 | 123.0971 | 61.4217 | 61.4893 | 122.9843 | 61.4533 | 122.7854 | 61.6903 | 61.7263 | 61.6078 | 61.6438
4667.0938 | 123.3673 | -61.4182 | 61.7249 | -0.5878 | -4.4453 | -4.0137 | 4.4207 | 0.27432 | -0.61491 | -0.96004 | 61.7386 | 0.28526 | 61.679 | -0.028522 | 0.043657 | 61.5478 | 0.007721 | 61.326 | 60.8304 | 56.9728 | 57.4045 | 65.8389 | 61.6925 | 60.8032 | 60.4581 | 123.1567 | 61.7034 | 123.0971 | 61.3896 | 61.4618 | 122.966 | 61.4259 | 122.7442 | 61.6949 | 61.7308 | 61.6353 | 61.6712
4668.0625 | 123.2803 | -61.4136 | 61.7523 | -0.5878 | -4.5644 | -4.2335 | 4.1231 | 0.23312 | -0.61949 | -0.93715 | 61.7431 | 0.27611 | 61.6423 | -0.028522 | 0.048236 | 61.5341 | 0.012299 | 61.326 | 60.8258 | 56.8492 | 57.1801 | 65.5367 | 61.6467 | 60.7941 | 60.4764 | 123.1567 | 61.6897 | 123.0559 | 61.3851 | 61.4618 | 122.9477 | 61.4259 | 122.7396 | 61.6949 | 61.7308 | 61.5941 | 61.63
4669.0625 | 123.3078 | -61.4365 | 61.7386 | -0.5878 | -4.5598 | -4.3067 | 4.2513 | 0.1736 | -0.61491 | -0.9692 | 61.7431 | 0.28069 | 61.6698 | -0.03768 | 0.052814 | 61.5478 | 0.007721 | 61.3398 | 60.8487 | 56.8766 | 57.1297 | 65.6878 | 61.6101 | 60.8216 | 60.4673 | 123.1796 | 61.7171 | 123.1063 | 61.3988 | 61.4893 | 122.9843 | 61.4442 | 122.7762 | 61.6903 | 61.7354 | 61.617 | 61.6621
4670.0938 | 123.2803 | -61.4639 | 61.7432 | -0.49165 | -4.4133 | -3.5146 | 4.6542 | 0.2789 | -0.51876 | -0.80438 | 61.7248 | 0.27153 | 61.6652 | -0.033101 | 0.052814 | 61.5524 | 0.003143 | 61.3535 | 60.9723 | 57.0506 | 57.9493 | 66.1181 | 61.7428 | 60.9452 | 60.6595 | 123.1887 | 61.7355 | 123.1291 | 61.4308 | 61.5167 | 123.0164 | 61.4671 | 122.8174 | 61.672 | 61.7217 | 61.6124 | 61.6621
4671.0625 | 123.3948 | -61.4227 | 61.6882 | -0.55575 | -4.3446 | -3.4231 | 4.526 | 0.13698 | -0.59202 | -0.7586 | 61.7202 | 0.27611 | 61.6332 | -0.033101 | 0.043657 | 61.5387 | 0.012299 | 61.3489 | 60.867 | 57.0781 | 57.9997 | 65.9487 | 61.5597 | 60.8307 | 60.6641 | 123.143 | 61.6988 | 123.0559 | 61.3896 | 61.4664 | 122.9614 | 61.435 | 122.7717 | 61.6766 | 61.7079 | 61.5895 | 61.6209
4672.0938 | 123.3765 | -61.409 | 61.6974 | -0.51455 | -4.3538 | -3.9542 | 4.4161 | 0.15529 | -0.5325 | -0.67619 | 61.7386 | 0.28069 | 61.6652 | -0.033101 | 0.048236 | 61.5478 | 0.003143 | 61.3443 | 60.8945 | 57.0552 | 57.4548 | 65.8251 | 61.5643 | 60.8765 | 60.7328 | 123.1476 | 61.6897 | 123.0742 | 61.3759 | 61.4572 | 122.9568 | 61.4121 | 122.7533 | 61.6903 | 61.7354 | 61.617 | 61.6621
4673.0625 | 123.3307 | -61.4273 | 61.7111 | -0.50081 | -4.221 | -3.6062 | 4.3017 | 0.18734 | -0.53708 | -0.67161 | 61.7386 | 0.27611 | 61.6652 | -0.028522 | 0.048236 | 61.5433 | -0.001436 | 61.3627 | 60.9265 | 57.2063 | 57.8211 | 65.729 | 61.6146 | 60.8902 | 60.7557 | 123.1659 | 61.7034 | 123.0925 | 61.3988 | 61.4755 | 122.9706 | 61.4259 | 122.79 | 61.6903 | 61.74 | 61.617 | 61.6667
4674.0781 | 123.2712 | -61.4639 | 61.7294 | -0.46876 | -3.7997 | -2.6172 | 4.3841 | 0.28347 | -0.50045 | -0.47933 | 61.7157 | 0.27611 | 61.6194 | -0.042259 | 0.048236 | 61.5662 | 0.007721 | 61.3718 | 60.9952 | 57.6642 | 58.8467 | 65.848 | 61.7474 | 60.9635 | 60.9846 | 123.1796 | 61.74 | 123.0834 | 61.4217 | 61.5122 | 123.0301 | 61.4716 | 122.8357 | 61.6674 | 61.7079 | 61.5712 | 61.6117
4675.0625 | 123.4589 | -61.4365 | 61.6745 | -0.41382 | -3.7814 | -2.5623 | 4.4985 | 0.36588 | -0.44093 | -0.41066 | 61.7111 | 0.28069 | 61.6423 | -0.028522 | 0.043657 | 61.5707 | 0.007721 | 61.3627 | 61.0226 | 57.655 | 58.8742 | 65.935 | 61.8023 | 60.9955 | 61.0258 | 123.1475 | 61.7171 | 123.0788 | 61.4079 | 61.4801 | 123.0072 | 61.4442 | 122.7991 | 61.6674 | 61.7034 | 61.5987 | 61.6346
4676.0938 | 123.3673 | -61.4136 | 61.6974 | -0.43213 | -3.9508 | -2.576 | 4.3383 | 0.24227 | -0.45925 | -0.91884 | 61.7202 | 0.28069 | 61.6515 | -0.033101 | 0.039079 | 61.5707 | 0.007721 | 61.3535 | 60.9814 | 57.4627 | 58.8376 | 65.7519 | 61.6558 | 60.9543 | 60.4947 | 123.1338 | 61.6943 | 123.0651 | 61.3805 | 61.4527 | 122.9843 | 61.4213 | 122.7671 | 61.6812 | 61.7125 | 61.6124 | 61.6438
4677.0625 | 123.2941 | -61.4456 | 61.6928 | -0.4596 | -4.0516 | -2.6355 | 4.2833 | 0.2789 | -0.50045 | -1.1706 | 61.7111 | 0.28069 | 61.6286 | -0.033101 | 0.043657 | 61.557 | 0.003143 | 61.3535 | 60.986 | 57.3941 | 58.8101 | 65.729 | 61.7245 | 60.9452 | 60.275 | 123.1567 | 61.7263 | 123.0742 | 61.4125 | 61.4893 | 123.0026 | 61.4488 | 122.7991 | 61.6674 | 61.7079 | 61.5849 | 61.6255
4678.0938 | 123.2849 | -61.4365 | 61.6928 | -0.51455 | -4.2988 | -2.9652 | 3.6973 | 0.14156 | -0.5325 | -1.3263 | 61.7431 | 0.28069 | 61.6698 | -0.033101 | 0.043657 | 61.5524 | 0.003143 | 61.326 | 60.9219 | 57.1376 | 58.4713 | 65.1338 | 61.578 | 60.904 | 60.1102 | 123.1796 | 61.7171 | 123.1063 | 61.4034 | 61.4801 | 122.9889 | 61.4396 | 122.7625 | 61.6995 | 61.74 | 61.6261 | 61.6667
4679.0625 | 123.2986 | -61.4548 | 61.7111 | -0.44587 | -4.1615 | -3.1071 | 4.0865 | 0.29263 | -0.48214 | -1.2393 | 61.7202 | 0.27611 | 61.6515 | -0.03768 | 0.052814 | 61.5478 | 0.007721 | 61.3489 | 61.0089 | 57.2933 | 58.3476 | 65.5412 | 61.7474 | 60.9726 | 60.2155 | 123.175 | 61.7309 | 123.1063 | 61.4171 | 61.5076 | 123.0026 | 61.4625 | 122.8037 | 61.6674 | 61.7125 | 61.5987 | 61.6438
4680.0938 | 123.3215 | -61.4456 | 61.6837 | -0.38635 | -3.8547 | -2.6996 | 3.9583 | 0.38877 | -0.41346 | -0.95546 | 61.7111 | 0.28069 | 61.6194 | -0.033101 | 0.043657 | 61.557 | 0.003143 | 61.3535 | 61.0593 | 57.5909 | 58.746 | 65.4039 | 61.8344 | 61.0322 | 60.4902 | 123.1567 | 61.7263 | 123.0651 | 61.4125 | 61.4893 | 123.0026 | 61.4488 | 122.7991 | 61.6674 | 61.7079 | 61.5758 | 61.6163
4681.0625 | 123.349 | -61.441 | 61.6882 | -0.30852 | -3.8684 | -2.9469 | 4.4756 | 0.56731 | -0.33563 | -0.69451 | 61.7065 | 0.27611 | 61.6469 | -0.033101 | 0.043657 | 61.5662 | 0.003143 | 61.3489 | 61.1325 | 57.5726 | 58.4942 | 65.9167 | 62.0083 | 61.1054 | 60.7465 | 123.1475 | 61.7171 | 123.0879 | 61.4079 | 61.4847 | 123.0072 | 61.4442 | 122.79 | 61.6628 | 61.7034 | 61.6032 | 61.6438
4682.0938 | 123.3078 | -61.4502 | 61.7203 | -0.44129 | -4.0561 | -2.8919 | 4.2925 | 0.35672 | -0.46382 | -0.70366 | 61.7202 | 0.27153 | 61.6377 | -0.033101 | 0.052814 | 61.5616 | 0.016878 | 61.3581 | 61.0089 | 57.3941 | 58.5583 | 65.7427 | 61.8069 | 60.9864 | 60.7465 | 123.1704 | 61.7217 | 123.0879 | 61.4171 | 61.503 | 123.0118 | 61.4671 | 122.8083 | 61.6674 | 61.7034 | 61.5849 | 61.6209
4683.0625 | 123.2941 | -61.4731 | 61.7111 | -0.40009 | -4.1477 | -2.7729 | 4.2467 | 0.26516 | -0.42262 | -0.56174 | 61.7157 | 0.28069 | 61.6286 | -0.033101 | 0.052814 | 61.5616 | 0.007721 | 61.3535 | 61.073 | 57.3254 | 58.7002 | 65.7198 | 61.7382 | 61.0505 | 60.9113 | 123.1887 | 61.7538 | 123.1017 | 61.44 | 61.5259 | 123.0347 | 61.4808 | 122.8266 | 61.6628 | 61.7079 | 61.5758 | 61.6209
4684.0625 | 123.2254 | -61.4914 | 61.6882 | -0.28563 | -4.0287 | -2.9927 | 4.7229 | 0.45744 | -0.30358 | -0.33741 | 61.7202 | 0.27611 | 61.6469 | -0.033101 | 0.039079 | 61.5753 | 0.003143 | 61.3627 | 61.2058 | 57.4627 | 58.4987 | 66.2143 | 61.9488 | 61.1878 | 61.154 | 123.2116 | 61.7675 | 123.1383 | 61.4583 | 61.5305 | 123.0667 | 61.4945 | 122.8541 | 61.6812 | 61.7171 | 61.6078 | 61.6438
4685.0625 | 123.3765 | -61.4456 | 61.6608 | -0.45503 | -4.2439 | -3.3773 | 4.0819 | 0.22396 | -0.47298 | -0.32367 | 61.7202 | 0.27611 | 61.624 | -0.033101 | 0.039079 | 61.5524 | 0.003143 | 61.3398 | 60.9906 | 57.2017 | 58.0683 | 65.5275 | 61.6696 | 60.9726 | 61.1219 | 123.1659 | 61.7217 | 123.0696 | 61.4125 | 61.4847 | 122.998 | 61.4488 | 122.7854 | 61.6812 | 61.7171 | 61.5849 | 61.6209
4686.0938 | 123.3032 | -61.4685 | 61.7203 | -0.39093 | -4.1798 | -3.3452 | 4.0727 | 0.21938 | -0.4272 | -0.3603 | 61.7248 | 0.27153 | 61.6469 | -0.03768 | 0.048236 | 61.5524 | 0.003143 | 61.3443 | 61.0776 | 57.2887 | 58.1233 | 65.5412 | 61.6879 | 61.0413 | 61.1082 | 123.1933 | 61.74 | 123.1154 | 61.4308 | 61.5167 | 123.0209 | 61.4716 | 122.8129 | 61.6766 | 61.7217 | 61.5987 | 61.6438
4687.0625 | 123.2941 | -61.4456 | 61.702 | -0.3543 | -4.0561 | -3.3406 | 3.5096 | 0.22854 | -0.3631 | -0.68077 | 61.734 | 0.28069 | 61.6744 | -0.028522 | 0.039079 | 61.5478 | 0.003143 | 61.3443 | 61.0913 | 57.3895 | 58.105 | 64.9552 | 61.6742 | 61.0825 | 60.7648 | 123.1796 | 61.7263 | 123.12 | 61.4171 | 61.4847 | 122.9935 | 61.4488 | 122.79 | 61.6949 | 61.7308 | 61.6353 | 61.6712
4688.0938 | 123.317 | -61.4548 | 61.7157 | -0.37261 | -4.0241 | -2.75 | 4.2009 | 0.28347 | -0.44551 | -0.84101 | 61.7157 | 0.27611 | 61.6194 | -0.028522 | 0.048236 | 61.5616 | 0.007721 | 61.3581 | 61.0822 | 57.4307 | 58.7048 | 65.6557 | 61.7382 | 61.0093 | 60.6138 | 123.1704 | 61.7309 | 123.0742 | 61.4263 | 61.503 | 123.0164 | 61.4625 | 122.8129 | 61.6674 | 61.7079 | 61.5712 | 61.6117
4689.0625 | 123.3215 | -61.4502 | 61.7111 | -0.45503 | -3.9875 | -2.2967 | 4.5764 | 0.25143 | -0.48672 | -0.80438 | 61.7157 | 0.28984 | 61.6515 | -0.033101 | 0.039079 | 61.5616 | 0.012299 | 61.3672 | 60.9952 | 57.4627 | 59.1535 | 66.0266 | 61.7016 | 60.9635 | 60.6458 | 123.1659 | 61.74 | 123.1017 | 61.4171 | 61.4893 | 123.0118 | 61.4625 | 122.8174 | 61.6766 | 61.7034 | 61.6124 | 61.6392
4690.0781 | 123.3307 | -61.441 | 61.7065 | -0.49623 | -3.9875 | -2.3242 | 4.7 | 0.21023 | -0.5325 | -0.63041 | 61.7157 | 0.27611 | 61.6515 | -0.028522 | 0.048236 | 61.5707 | 0.003143 | 61.3764 | 60.9448 | 57.4536 | 59.1168 | 66.141 | 61.6513 | 60.9085 | 60.8106 | 123.1567 | 61.7171 | 123.0925 | 61.4125 | 61.4893 | 123.0118 | 61.4442 | 122.8174 | 61.6674 | 61.7125 | 61.6032 | 61.6483
4691.0625 | 123.3948 | -61.4548 | 61.6516 | -0.42756 | -4.0332 | -2.7592 | 5.0296 | 0.26516 | -0.45467 | -0.44271 | 61.7019 | 0.27611 | 61.6103 | -0.033101 | 0.039079 | 61.5662 | -0.001436 | 61.3627 | 61.0272 | 57.4215 | 58.6956 | 66.4844 | 61.7199 | 61.0001 | 61.0121 | 123.1567 | 61.7309 | 123.0651 | 61.4217 | 61.4939 | 123.0209 | 61.4533 | 122.8174 | 61.6628 | 61.7034 | 61.5712 | 61.6117
4692.0781 | 123.381 | -61.4456 | 61.7111 | -0.40466 | -4.1111 | -2.7225 | 4.8923 | 0.29721 | -0.43635 | -0.37861 | 61.7019 | 0.27611 | 61.6423 | -0.023943 | 0.043657 | 61.5753 | 0.012299 | 61.3718 | 61.041 | 57.3345 | 58.7231 | 66.3379 | 61.7428 | 61.0093 | 61.067 | 123.1475 | 61.7217 | 123.0879 | 61.4217 | 61.4893 | 123.0209 | 61.4579 | 122.8174 | 61.6583 | 61.6896 | 61.5987 | 61.63
4693.0625 | 123.2529 | -61.496 | 61.6791 | -0.23984 | -3.9737 | -2.4341 | 4.7183 | 0.4849 | -0.26695 | -0.14512 | 61.7019 | 0.27611 | 61.6332 | -0.028522 | 0.048236 | 61.5845 | 0.016878 | 61.3856 | 61.2561 | 57.5222 | 59.0619 | 66.2143 | 61.9809 | 61.229 | 61.3508 | 123.1979 | 61.7721 | 123.1291 | 61.4674 | 61.5442 | 123.0804 | 61.5129 | 122.8815 | 61.6537 | 61.685 | 61.5849 | 61.6163
4694.1094 | 123.3078 | -61.441 | 61.734 | -0.35888 | -4.0836 | -2.6996 | 4.027 | 0.22854 | -0.39515 | -0.14512 | 61.7202 | 0.27153 | 61.6194 | -0.028522 | 0.048236 | 61.5662 | 0.003143 | 61.3672 | 61.0822 | 57.3574 | 58.7414 | 65.468 | 61.6696 | 61.0459 | 61.2959 | 123.1613 | 61.7126 | 123.0605 | 61.4125 | 61.4893 | 123.0072 | 61.4442 | 122.8083 | 61.672 | 61.7171 | 61.5712 | 61.6163
4695.0625 | 123.3078 | -61.4456 | 61.7065 | -0.43671 | -4.1615 | -2.837 | 4.3978 | 0.21938 | -0.46382 | -0.22295 | 61.7248 | 0.27611 | 61.6515 | -0.028522 | 0.048236 | 61.557 | 0.003143 | 61.3672 | 61.0089 | 57.2842 | 58.6086 | 65.8434 | 61.665 | 60.9818 | 61.2227 | 123.1704 | 61.7217 | 123.0971 | 61.4171 | 61.4939 | 123.0026 | 61.4488 | 122.8129 | 61.6766 | 61.7217 | 61.6032 | 61.6483
4696.0781 | 123.2666 | -61.4685 | 61.702 | -0.45503 | -4.1889 | -3.0339 | 3.9491 | 0.2148 | -0.49129 | -0.18633 | 61.7294 | 0.27611 | 61.6606 | -0.033101 | 0.043657 | 61.557 | 0.007721 | 61.3627 | 61.0135 | 57.2796 | 58.4346 | 65.4176 | 61.6833 | 60.9772 | 61.2822 | 123.1979 | 61.7446 | 123.1291 | 61.4354 | 61.5122 | 123.0255 | 61.4762 | 122.8312 | 61.6857 | 61.7217 | 61.617 | 61.6529
4697.0625 | 123.2346 | -61.441 | 61.6974 | -0.47792 | -4.4087 | -3.6611 | 3.8942 | 0.16903 | -0.50961 | -0.28247 | 61.7248 | 0.27153 | 61.6332 | -0.03768 | 0.039079 | 61.5478 | 0.012299 | 61.3443 | 60.9631 | 57.0323 | 57.7799 | 65.3352 | 61.6101 | 60.9314 | 61.1586 | 123.1659 | 61.7126 | 123.0742 | 61.4034 | 61.4801 | 122.9889 | 61.4533 | 122.7854 | 61.6857 | 61.7125 | 61.5941 | 61.6209
4698.0781 | 123.3261 | -61.4273 | 61.7386 | -0.50539 | -4.4041 | -3.4734 | 3.7019 | 0.12782 | -0.5325 | -0.26874 | 61.7248 | 0.27611 | 61.6515 | -0.023943 | 0.052814 | 61.5524 | 0.007721 | 61.3489 | 60.9219 | 57.0232 | 57.9539 | 65.1292 | 61.5551 | 60.8948 | 61.1586 | 123.1521 | 61.7034 | 123.0788 | 61.4034 | 61.4801 | 122.9797 | 61.435 | 122.7762 | 61.672 | 61.7171 | 61.5987 | 61.6438
4699.0625 | 123.4268 | -61.4365 | 61.6562 | -0.47792 | -4.2851 | -3.3315 | 4.0086 | 0.19192 | -0.50045 | -0.23669 | 61.7294 | 0.28069 | 61.6606 | -0.033101 | 0.048236 | 61.557 | 0.003143 | 61.3627 | 60.9585 | 57.1514 | 58.105 | 65.4451 | 61.6284 | 60.936 | 61.1998 | 123.1659 | 61.7171 | 123.0971 | 61.4034 | 61.4847 | 122.9935 | 61.4396 | 122.7991 | 61.6812 | 61.7263 | 61.6124 | 61.6575
4700.0781 | 123.2254 | -61.4365 | 61.7203 | -0.56491 | -4.2897 | -2.9057 | 4.1185 | -0.004937 | -0.5966 | -0.26416 | 61.7248 | 0.27153 | 61.6606 | -0.033101 | 0.052814 | 61.557 | 0.016878 | 61.3672 | 60.8716 | 57.1468 | 58.5308 | 65.555 | 61.4315 | 60.8399 | 61.1723 | 123.1613 | 61.708 | 123.0971 | 61.4034 | 61.4893 | 122.9935 | 61.4533 | 122.8037 | 61.672 | 61.7079 | 61.6078 | 61.6438
4701.0625 | 123.3444 | -61.441 | 61.6516 | -0.51455 | -4.2301 | -2.5531 | 4.2467 | 0.077466 | -0.53708 | -0.2962 | 61.7111 | 0.27611 | 61.624 | -0.028522 | 0.039079 | 61.5707 | 0.003143 | 61.3581 | 60.9265 | 57.2109 | 58.8879 | 65.6878 | 61.5185 | 60.904 | 61.1448 | 123.1521 | 61.7171 | 123.0651 | 61.4125 | 61.4801 | 123.0118 | 61.4442 | 122.7991 | 61.672 | 61.7079 | 61.5849 | 61.6209
4702.1094 | 123.3948 | -61.4227 | 61.6379 | -0.49623 | -4.2072 | -3.3819 | 4.4848 | 0.24227 | -0.51876 | -0.19091 | 61.7157 | 0.28526 | 61.624 | -0.042259 | 0.048236 | 61.5616 | 0.007721 | 61.3581 | 60.9265 | 57.2155 | 58.0409 | 65.9075 | 61.665 | 60.904 | 61.2318 | 123.1384 | 61.708 | 123.0467 | 61.3805 | 61.471 | 122.9843 | 61.4304 | 122.7808 | 61.6674 | 61.7079 | 61.5758 | 61.6163
4703.0625 | 123.262 | -61.4868 | 61.7203 | -0.5237 | -4.3538 | -3.478 | 4.3246 | 0.0912 | -0.54624 | -0.27331 | 61.7248 | 0.27611 | 61.6606 | -0.033101 | 0.052814 | 61.5524 | 0.007721 | 61.3535 | 60.9631 | 57.133 | 58.0088 | 65.8114 | 61.578 | 60.9406 | 61.2135 | 123.2116 | 61.7629 | 123.1475 | 61.4537 | 61.5396 | 123.0392 | 61.4945 | 122.8403 | 61.672 | 61.7171 | 61.6078 | 61.6529
4704.0938 | 123.317 | -61.4639 | 61.6562 | -0.50997 | -4.3355 | -3.1941 | 4.3337 | 0.1324 | -0.5325 | -0.48391 | 61.7202 | 0.28069 | 61.6606 | -0.03768 | 0.043657 | 61.557 | 0.012299 | 61.3535 | 60.954 | 57.1285 | 58.2698 | 65.7976 | 61.5963 | 60.9314 | 60.98 | 123.1842 | 61.7446 | 123.1246 | 61.4262 | 61.5076 | 123.0209 | 61.4762 | 122.8174 | 61.6766 | 61.7079 | 61.617 | 61.6483
4705.0625 | 123.3215 | -61.4319 | 61.6608 | -0.4825 | -4.3675 | -3.1117 | 4.1643 | 0.14156 | -0.50961 | -0.63499 | 61.7202 | 0.27611 | 61.6423 | -0.033101 | 0.043657 | 61.5524 | -0.006014 | 61.3535 | 60.9494 | 57.0644 | 58.3202 | 65.5962 | 61.5734 | 60.9223 | 60.7969 | 123.1521 | 61.708 | 123.0742 | 61.3988 | 61.4755 | 122.9843 | 61.4259 | 122.7854 | 61.6766 | 61.7263 | 61.5987 | 61.6483
4706.0938 | 123.4222 | -61.4227 | 61.6608 | -0.50539 | -4.3721 | -3.1483 | 4.3749 | 0.1324 | -0.53708 | -0.5709 | 61.7202 | 0.27611 | 61.6286 | -0.033101 | 0.043657 | 61.5524 | 0.003143 | 61.3535 | 60.9173 | 57.0506 | 58.2744 | 65.7976 | 61.5551 | 60.8857 | 60.8518 | 123.143 | 61.6988 | 123.0513 | 61.3896 | 61.4664 | 122.9752 | 61.4259 | 122.7762 | 61.6766 | 61.7171 | 61.5849 | 61.6255
4707.0625 | 123.4314 | -61.409 | 61.6699 | -0.54202 | -4.5049 | -3.2765 | 4.3795 | 0.10493 | -0.56913 | -0.64414 | 61.7157 | 0.28069 | 61.6515 | -0.033101 | 0.048236 | 61.5478 | 0.007721 | 61.3535 | 60.867 | 56.9041 | 58.1325 | 65.7885 | 61.5139 | 60.8399 | 60.7649 | 123.1247 | 61.6897 | 123.0605 | 61.3759 | 61.4572 | 122.9568 | 61.4167 | 122.7625 | 61.6674 | 61.7079 | 61.6032 | 61.6438
4708.0938 | 123.381 | -61.4365 | 61.647 | -0.48707 | -4.4362 | -3.2353 | 3.4455 | 0.045421 | -0.48672 | -0.63499 | 61.734 | 0.27611 | 61.6698 | -0.03768 | 0.048236 | 61.5478 | -0.001436 | 61.3489 | 60.9494 | 57.0003 | 58.2011 | 64.8819 | 61.4819 | 60.9497 | 60.8015 | 123.1704 | 61.7126 | 123.1063 | 61.3988 | 61.4847 | 122.9843 | 61.435 | 122.7854 | 61.6857 | 61.7354 | 61.6216 | 61.6712
4709.0625 | 123.2712 | -61.4639 | 61.6791 | -0.33599 | -4.3217 | -3.2353 | 4.32 | 0.14156 | -0.34936 | -0.64414 | 61.7202 | 0.27611 | 61.6515 | -0.033101 | 0.043657 | 61.557 | 0.003143 | 61.3443 | 61.1279 | 57.1422 | 58.2286 | 65.7839 | 61.6055 | 61.1146 | 60.8198 | 123.1842 | 61.74 | 123.1154 | 61.4308 | 61.5076 | 123.0209 | 61.4671 | 122.8083 | 61.6766 | 61.7171 | 61.6078 | 61.6483
4710.1094 | 123.2758 | -61.4365 | 61.7386 | -0.43213 | -4.4453 | -3.4597 | 4.4756 | 0.10951 | -0.45009 | -0.88221 | 61.7202 | 0.28069 | 61.6377 | -0.028522 | 0.048236 | 61.5433 | 0.012299 | 61.3581 | 61.0043 | 56.9911 | 57.9768 | 65.9121 | 61.546 | 60.9864 | 60.5543 | 123.1567 | 61.7171 | 123.0742 | 61.4079 | 61.4847 | 122.9797 | 61.4488 | 122.7945 | 61.672 | 61.7079 | 61.5895 | 61.6255
4711.0625 | 123.4222 | -61.3907 | 61.6562 | -0.43671 | -4.4453 | -3.5421 | 4.3932 | 0.10493 | -0.4684 | -0.95088 | 61.7248 | 0.27611 | 61.6469 | -0.028522 | 0.048236 | 61.5478 | 0.007721 | 61.3489 | 60.954 | 56.9453 | 57.8486 | 65.7839 | 61.4956 | 60.9223 | 60.4398 | 123.1155 | 61.6668 | 123.0376 | 61.3622 | 61.4389 | 122.9385 | 61.3984 | 122.7396 | 61.6766 | 61.7171 | 61.5987 | 61.6392
4712.0938 | 123.2941 | -61.4456 | 61.6745 | -0.31767 | -4.4453 | -3.3773 | 3.8896 | 0.22854 | -0.34936 | -1.2759 | 61.7294 | 0.28069 | 61.6744 | -0.033101 | 0.043657 | 61.5524 | 0.003143 | 61.326 | 61.1279 | 57.0003 | 58.0683 | 65.3352 | 61.6742 | 61.0963 | 60.1697 | 123.175 | 61.7263 | 123.12 | 61.4125 | 61.4893 | 122.998 | 61.4488 | 122.7717 | 61.6857 | 61.7263 | 61.6307 | 61.6712
4713.0625 | 123.4177 | -61.4365 | 61.6653 | -0.38177 | -4.5736 | -3.5009 | 3.7797 | 0.15071 | -0.41346 | -1.4133 | 61.7431 | 0.28069 | 61.679 | -0.028522 | 0.048236 | 61.5433 | 0.003143 | 61.326 | 61.0547 | 56.8629 | 57.9356 | 65.2162 | 61.5872 | 61.023 | 60.0232 | 123.1796 | 61.7171 | 123.1154 | 61.4079 | 61.4847 | 122.9797 | 61.4396 | 122.7625 | 61.6949 | 61.74 | 61.6307 | 61.6758
4714.0938 | 123.2529 | -61.4456 | 61.7065 | -0.39093 | -4.6102 | -3.6611 | 3.9125 | 0.21938 | -0.41804 | -1.308 | 61.7294 | 0.27611 | 61.6606 | -0.033101 | 0.043657 | 61.5341 | 0.007721 | 61.3215 | 61.0547 | 56.8354 | 57.7845 | 65.3581 | 61.665 | 61.0276 | 60.1376 | 123.175 | 61.7217 | 123.1063 | 61.4125 | 61.4893 | 122.9797 | 61.4533 | 122.7671 | 61.6857 | 61.7217 | 61.617 | 61.6529
4715.0625 | 123.3765 | -61.4136 | 61.6653 | -0.39093 | -4.6239 | -3.7298 | 3.9903 | 0.18734 | -0.40888 | -0.98751 | 61.7294 | 0.28069 | 61.6377 | -0.033101 | 0.048236 | 61.5478 | 0.003143 | 61.3306 | 61.0226 | 56.7897 | 57.6837 | 65.4039 | 61.6009 | 61.0047 | 60.4261 | 123.143 | 61.6943 | 123.0513 | 61.3805 | 61.4618 | 122.9614 | 61.4167 | 122.7442 | 61.6812 | 61.7263 | 61.5895 | 61.6346
4716.0781 | 123.2849 | -61.4548 | 61.702 | -0.44587 | -4.8345 | -3.7115 | 4.3703 | 0.0912 | -0.48672 | -0.79522 | 61.7294 | 0.27611 | 61.6469 | -0.023943 | 0.048236 | 61.5387 | 0.007721 | 61.3306 | 61.0089 | 56.6202 | 57.7433 | 65.8251 | 61.546 | 60.9681 | 60.6595 | 123.1842 | 61.7309 | 123.1017 | 61.4308 | 61.503 | 122.9935 | 61.4625 | 122.7854 | 61.6812 | 61.7217 | 61.5987 | 61.6392
4717.0625 | 123.4314 | -61.4273 | 61.6791 | -0.44587 | -4.8849 | -3.739 | 4.1414 | 0.0912 | -0.47298 | -0.71282 | 61.7386 | 0.27611 | 61.679 | -0.028522 | 0.048236 | 61.5433 | 0.007721 | 61.3169 | 60.9814 | 56.5424 | 57.6883 | 65.5687 | 61.5185 | 60.9543 | 60.7145 | 123.1659 | 61.7034 | 123.1063 | 61.3988 | 61.4755 | 122.9706 | 61.435 | 122.7442 | 61.6903 | 61.7308 | 61.6307 | 61.6712
4718.125 | 123.2986 | -61.441 | 61.7203 | -0.50997 | -4.8803 | -3.8077 | 4.2925 | 0.10493 | -0.54166 | -0.32825 | 61.734 | 0.27611 | 61.6744 | -0.028522 | 0.048236 | 61.5433 | 0.007721 | 61.3352 | 60.9311 | 56.5607 | 57.6334 | 65.7335 | 61.546 | 60.8994 | 61.1128 | 123.175 | 61.7171 | 123.1154 | 61.4125 | 61.4893 | 122.9843 | 61.4488 | 122.7762 | 61.6857 | 61.7263 | 61.6261 | 61.6667
4719.0625 | 123.3765 | -61.4273 | 61.6516 | -0.4596 | -4.8986 | -3.7298 | 4.4207 | 0.049999 | -0.48672 | -0.42897 | 61.734 | 0.27611 | 61.6377 | -0.03768 | 0.043657 | 61.5478 | 0.003143 | 61.326 | 60.9677 | 56.5287 | 57.6975 | 65.848 | 61.4773 | 60.9406 | 60.9983 | 123.1613 | 61.7034 | 123.0651 | 61.3896 | 61.471 | 122.9752 | 61.4305 | 122.7533 | 61.6903 | 61.7308 | 61.5941 | 61.6346
4720.0781 | 123.4177 | -61.441 | 61.6425 | -0.35888 | -4.917 | -3.4276 | 4.4344 | 0.19649 | -0.39057 | -0.49764 | 61.7202 | 0.27611 | 61.624 | -0.028522 | 0.043657 | 61.5478 | 0.003143 | 61.326 | 61.0822 | 56.5241 | 58.0134 | 65.8755 | 61.6375 | 61.0505 | 60.9434 | 123.1613 | 61.7171 | 123.0651 | 61.4125 | 61.4847 | 122.9889 | 61.4442 | 122.7671 | 61.6766 | 61.7171 | 61.5804 | 61.6209
4721.0625 | 123.4451 | -61.4136 | 61.6928 | -0.39093 | -4.8758 | -4.1007 | 4.4344 | 0.21938 | -0.41804 | -0.73571 | 61.734 | 0.27611 | 61.6698 | -0.033101 | 0.043657 | 61.5478 | 0.007721 | 61.3215 | 61.0226 | 56.5378 | 57.3129 | 65.848 | 61.633 | 60.9955 | 60.6779 | 123.1475 | 61.6897 | 123.0834 | 61.3805 | 61.4572 | 122.9614 | 61.4213 | 122.735 | 61.6903 | 61.7263 | 61.6261 | 61.6621
4722.0938 | 123.3856 | -61.4227 | 61.647 | -0.3131 | -4.7842 | -4.0641 | 4.0178 | 0.21938 | -0.33563 | -0.81354 | 61.7431 | 0.28526 | 61.679 | -0.03768 | 0.048236 | 61.5433 | 0.003143 | 61.3123 | 61.1096 | 56.6386 | 57.3587 | 65.4405 | 61.6421 | 61.0871 | 60.6092 | 123.1659 | 61.708 | 123.1017 | 61.385 | 61.471 | 122.966 | 61.4259 | 122.735 | 61.6949 | 61.74 | 61.6307 | 61.6758
4723.0625 | 123.4818 | -61.377 | 61.6837 | -0.25816 | -4.7613 | -4.0457 | 4.0865 | 0.26516 | -0.28069 | -0.79065 | 61.7202 | 0.28069 | 61.6469 | -0.028522 | 0.048236 | 61.5524 | 0.007721 | 61.3215 | 61.1188 | 56.6157 | 57.3312 | 65.4634 | 61.6421 | 61.0963 | 60.5863 | 123.0972 | 61.6576 | 123.0239 | 61.3484 | 61.4252 | 122.9294 | 61.3847 | 122.6984 | 61.672 | 61.7125 | 61.5987 | 61.6392
4724.0781 | 123.317 | -61.4685 | 61.7065 | -0.37719 | -4.9124 | -4.2518 | 3.7385 | 0.11867 | -0.41346 | -0.6533 | 61.7386 | 0.28526 | 61.6469 | -0.033101 | 0.048236 | 61.5387 | 0.007721 | 61.3123 | 61.0913 | 56.5561 | 57.2167 | 65.207 | 61.5872 | 61.055 | 60.8152 | 123.2071 | 61.7538 | 123.1154 | 61.4354 | 61.5167 | 123.0072 | 61.4762 | 122.7808 | 61.6903 | 61.7308 | 61.5987 | 61.6392
4725.0625 | 123.4131 | -61.409 | 61.6974 | -0.38635 | -4.9032 | -4.2426 | 3.6561 | 0.063733 | -0.41804 | -0.64414 | 61.7431 | 0.27153 | 61.6332 | -0.033101 | 0.043657 | 61.5478 | 0.007721 | 61.326 | 61.0226 | 56.5058 | 57.1664 | 65.0651 | 61.4727 | 60.991 | 60.7649 | 123.1521 | 61.6805 | 123.0422 | 61.3759 | 61.4527 | 122.9568 | 61.4167 | 122.735 | 61.6995 | 61.7354 | 61.5895 | 61.6255
4726.1094 | 123.4314 | -61.3861 | 61.7157 | -0.43213 | -4.917 | -4.412 | 3.0197 | -0.041561 | -0.45467 | -0.53427 | 61.7431 | 0.28526 | 61.6561 | -0.03768 | 0.043657 | 61.5341 | 0.012299 | 61.3169 | 60.954 | 56.4691 | 56.9741 | 64.4058 | 61.3445 | 60.9314 | 60.8518 | 123.1292 | 61.6714 | 123.0422 | 61.3484 | 61.4298 | 122.9202 | 61.3984 | 122.703 | 61.6995 | 61.7308 | 61.6124 | 61.6438
4727.0625 | 123.4314 | -61.3998 | 61.6928 | -0.27647 | -4.6468 | -3.684 | 3.0517 | 0.10951 | -0.31274 | -0.50222 | 61.734 | 0.28069 | 61.6698 | -0.033101 | 0.048236 | 61.5433 | 0.012299 | 61.3215 | 61.1234 | 56.753 | 57.7158 | 64.4516 | 61.5094 | 61.0871 | 60.8976 | 123.1338 | 61.6805 | 123.0696 | 61.3667 | 61.4481 | 122.9431 | 61.4121 | 122.7213 | 61.6857 | 61.7217 | 61.6216 | 61.6575
4728.0938 | 123.4085 | -61.4136 | 61.6516 | -0.249 | -4.5598 | -3.5558 | 3.3448 | 0.28347 | -0.27153 | -0.47475 | 61.734 | 0.28069 | 61.6698 | -0.03768 | 0.048236 | 61.5433 | 0.003143 | 61.326 | 61.1646 | 56.8538 | 57.8577 | 64.7583 | 61.697 | 61.142 | 60.9388 | 123.1475 | 61.6943 | 123.0834 | 61.3759 | 61.4618 | 122.9568 | 61.4167 | 122.7396 | 61.6857 | 61.7308 | 61.6216 | 61.6667
4729.0625 | 123.3032 | -61.4365 | 61.7432 | -0.26731 | -4.656 | -3.6154 | 3.4363 | 0.30179 | -0.28985 | -0.37861 | 61.7294 | 0.28069 | 61.6698 | -0.028522 | 0.048236 | 61.5524 | 0.003143 | 61.3398 | 61.1692 | 56.7805 | 57.8211 | 64.8728 | 61.7382 | 61.1466 | 61.0579 | 123.1659 | 61.7171 | 123.1063 | 61.4079 | 61.4847 | 122.9889 | 61.4396 | 122.7762 | 61.6812 | 61.7263 | 61.6216 | 61.6667
4730.0938 | 123.3261 | -61.4456 | 61.6882 | -0.37261 | -4.7384 | -3.8443 | 4.0178 | 0.41166 | -0.39973 | -0.64872 | 61.7248 | 0.28526 | 61.6377 | -0.033101 | 0.039079 | 61.5478 | 0.003143 | 61.3352 | 61.073 | 56.7072 | 57.6013 | 65.4634 | 61.8573 | 61.0459 | 60.7969 | 123.1704 | 61.7309 | 123.0834 | 61.4125 | 61.4847 | 122.9935 | 61.4488 | 122.7808 | 61.6857 | 61.7217 | 61.5987 | 61.6346
4731.0625 | 123.3032 | -61.4502 | 61.6837 | -0.33141 | -4.656 | -3.8718 | 4.1094 | 0.59478 | -0.36768 | -0.63957 | 61.7294 | 0.27611 | 61.624 | -0.03768 | 0.043657 | 61.557 | 0.007721 | 61.3306 | 61.1188 | 56.7942 | 57.5784 | 65.5596 | 62.045 | 61.0825 | 60.8106 | 123.1796 | 61.7263 | 123.0742 | 61.4125 | 61.4939 | 123.0072 | 61.4579 | 122.7808 | 61.6857 | 61.7217 | 61.5804 | 61.6163
4732.0938 | 123.4268 | -61.4044 | 61.702 | -0.39093 | -4.8849 | -4.6181 | 4.0224 | 0.2789 | -0.42262 | -0.84101 | 61.7431 | 0.28069 | 61.679 | -0.028522 | 0.043657 | 61.5387 | 0.003143 | 61.3169 | 61.0135 | 56.5195 | 56.7863 | 65.4268 | 61.6833 | 60.9818 | 60.5634 | 123.1476 | 61.6851 | 123.0834 | 61.3759 | 61.4481 | 122.9431 | 61.4076 | 122.7213 | 61.6995 | 61.74 | 61.6353 | 61.6758
4733.0625 | 123.3856 | -61.3953 | 61.7111 | -0.31767 | -4.8071 | -4.586 | 3.4684 | 0.33841 | -0.34479 | -1.0104 | 61.7523 | 0.28069 | 61.6881 | -0.03768 | 0.048236 | 61.5341 | 0.007721 | 61.3169 | 61.0776 | 56.5882 | 56.8092 | 64.8636 | 61.7337 | 61.0505 | 60.3849 | 123.1476 | 61.6759 | 123.0834 | 61.3576 | 61.4435 | 122.9294 | 61.403 | 122.7121 | 61.7041 | 61.7446 | 61.6399 | 61.6804
4734.1094 | 123.2803 | -61.4456 | 61.6928 | -0.19864 | -4.6605 | -4.2747 | 2.7999 | 0.41624 | -0.22117 | -1.0287 | 61.7477 | 0.27611 | 61.6744 | -0.03768 | 0.043657 | 61.5295 | 0.007721 | 61.3306 | 61.247 | 56.7851 | 57.1709 | 64.2455 | 61.8619 | 61.2244 | 60.4169 | 123.1933 | 61.7217 | 123.12 | 61.4079 | 61.4893 | 122.9752 | 61.4533 | 122.7762 | 61.7041 | 61.74 | 61.6307 | 61.6667
4735.0625 | 123.4085 | -61.3998 | 61.6928 | -0.15285 | -4.6377 | -4.2014 | 2.5893 | 0.4025 | -0.17539 | -1.1065 | 61.734 | 0.28526 | 61.6469 | -0.028522 | 0.039079 | 61.5341 | 0.007721 | 61.3123 | 61.247 | 56.7622 | 57.1984 | 63.9891 | 61.8023 | 61.2245 | 60.2933 | 123.1338 | 61.6851 | 123.0467 | 61.3713 | 61.4389 | 122.934 | 61.4076 | 122.7121 | 61.6949 | 61.7263 | 61.6078 | 61.6392
4736.0781 | 123.3582 | -61.4227 | 61.6745 | -0.22611 | -4.7933 | -4.3159 | 3.1662 | 0.34299 | -0.2578 | -1.102 | 61.7386 | 0.27611 | 61.6515 | -0.028522 | 0.048236 | 61.5295 | 0.012299 | 61.3215 | 61.1966 | 56.6294 | 57.1068 | 64.5889 | 61.7657 | 61.1649 | 60.3208 | 123.1613 | 61.6988 | 123.0742 | 61.3942 | 61.471 | 122.9523 | 61.435 | 122.7442 | 61.6903 | 61.7263 | 61.6032 | 61.6392
4737.0625 | 123.3994 | -61.4502 | 61.6882 | -0.28563 | -4.9124 | -4.3479 | 3.4958 | 0.34299 | -0.31274 | -0.83643 | 61.7477 | 0.27153 | 61.6835 | -0.028522 | 0.043657 | 61.5341 | 0.003143 | 61.3123 | 61.1646 | 56.5378 | 57.1023 | 64.946 | 61.7932 | 61.1375 | 60.6138 | 123.1979 | 61.7217 | 123.1337 | 61.4217 | 61.4939 | 122.9843 | 61.4533 | 122.7625 | 61.7041 | 61.7446 | 61.6399 | 61.6804
4738.0781 | 123.3902 | -61.4136 | 61.6928 | -0.24442 | -4.9719 | -4.4349 | 3.8621 | 0.38877 | -0.27611 | -0.85016 | 61.7477 | 0.28526 | 61.679 | -0.033101 | 0.039079 | 61.5387 | 0.007721 | 61.326 | 61.1692 | 56.4417 | 56.9786 | 65.2757 | 61.8023 | 61.1375 | 60.5634 | 123.1613 | 61.6988 | 123.0925 | 61.3805 | 61.4527 | 122.9523 | 61.4213 | 122.7396 | 61.7086 | 61.74 | 61.6399 | 61.6712
4739.0625 | 123.262 | -61.3998 | 61.734 | -0.16201 | -4.8162 | -4.3525 | 3.5783 | 0.549 | -0.18454 | -0.9692 | 61.7386 | 0.28069 | 61.6377 | -0.03768 | 0.043657 | 61.5387 | 0.007721 | 61.3306 | 61.2378 | 56.5836 | 57.0473 | 64.9781 | 61.9488 | 61.2153 | 60.4306 | 123.1384 | 61.6805 | 123.0376 | 61.3622 | 61.4435 | 122.9385 | 61.4076 | 122.7305 | 61.6949 | 61.7308 | 61.5941 | 61.63
4740.0938 | 123.3994 | -61.441 | 61.6837 | -0.14827 | -4.7292 | -4.1739 | 3.0105 | 0.60851 | -0.16623 | -1.0196 | 61.7386 | 0.28069 | 61.6423 | -0.03768 | 0.043657 | 61.5387 | 0.007721 | 61.3398 | 61.2928 | 56.7118 | 57.2671 | 64.4516 | 62.0496 | 61.2748 | 60.4215 | 123.1796 | 61.7217 | 123.0834 | 61.4034 | 61.4847 | 122.9797 | 61.4488 | 122.7808 | 61.6949 | 61.7308 | 61.5987 | 61.6346
4741.0625 | 123.2849 | -61.4502 | 61.7203 | -0.12538 | -4.4133 | -3.3086 | 3.3997 | 0.67718 | -0.14791 | -0.66246 | 61.7248 | 0.27611 | 61.6652 | -0.028522 | 0.043657 | 61.5524 | 0.003143 | 61.3443 | 61.3248 | 57.0369 | 58.1416 | 64.8499 | 62.1274 | 61.3023 | 60.7877 | 123.175 | 61.7263 | 123.1154 | 61.4217 | 61.4939 | 123.0026 | 61.4533 | 122.7945 | 61.6812 | 61.7217 | 61.6216 | 61.6621
4742.1094 | 123.3444 | -61.4319 | 61.7294 | -0.25358 | -4.6422 | -3.13 | 3.8301 | 0.53068 | -0.28069 | -0.77691 | 61.734 | 0.28069 | 61.6606 | -0.023943 | 0.052814 | 61.5478 | -0.001436 | 61.3535 | 61.1783 | 56.7897 | 58.3019 | 65.262 | 61.9626 | 61.1512 | 60.655 | 123.1659 | 61.7126 | 123.0925 | 61.4079 | 61.4847 | 122.9797 | 61.4304 | 122.7854 | 61.6812 | 61.7354 | 61.6078 | 61.6621
4743.0625 | 123.2849 | -61.4456 | 61.7523 | -0.24442 | -4.6972 | -2.924 | 3.711 | 0.51237 | -0.27611 | -0.77233 | 61.7248 | 0.28069 | 61.6377 | -0.033101 | 0.043657 | 61.557 | 0.012299 | 61.3489 | 61.2012 | 56.7484 | 58.5216 | 65.1567 | 61.958 | 61.1695 | 60.6733 | 123.1704 | 61.7263 | 123.0834 | 61.4125 | 61.4893 | 123.0026 | 61.4579 | 122.7945 | 61.6812 | 61.7125 | 61.5941 | 61.6255
4744.0938 | 123.4085 | -61.4365 | 61.6608 | -0.10249 | -4.4774 | -2.6218 | 2.8457 | 0.57646 | -0.12502 | -0.63041 | 61.7248 | 0.28526 | 61.624 | -0.033101 | 0.043657 | 61.557 | 0.007721 | 61.3581 | 61.334 | 56.9591 | 58.8147 | 64.2822 | 62.0129 | 61.3114 | 60.8061 | 123.1613 | 61.7217 | 123.0605 | 61.4034 | 61.4801 | 122.9935 | 61.4442 | 122.7945 | 61.6812 | 61.7171 | 61.5804 | 61.6163
4745.0625 | 123.4177 | -61.4227 | 61.6974 | -0.047549 | -4.569 | -2.4707 | 3.1296 | 0.60393 | -0.065504 | -0.63041 | 61.7157 | 0.28069 | 61.6423 | -0.03768 | 0.043657 | 61.5616 | 0.007721 | 61.3535 | 61.3752 | 56.8538 | 58.952 | 64.5523 | 62.0267 | 61.3572 | 60.7923 | 123.1384 | 61.7034 | 123.0651 | 61.385 | 61.4664 | 122.9843 | 61.4304 | 122.7762 | 61.672 | 61.7079 | 61.5987 | 61.6346
4746.0938 | 123.3627 | -61.4319 | 61.6608 | -0.21237 | -4.8529 | -2.5577 | 4.0544 | 0.45286 | -0.23948 | -0.64872 | 61.7248 | 0.28069 | 61.6606 | -0.033101 | 0.043657 | 61.5753 | 0.007721 | 61.3489 | 61.2195 | 56.579 | 58.8742 | 65.4863 | 61.8847 | 61.1924 | 60.7832 | 123.1567 | 61.7126 | 123.0925 | 61.3988 | 61.4755 | 123.0072 | 61.4396 | 122.7808 | 61.6812 | 61.7171 | 61.617 | 61.6529
4747.0625 | 123.3307 | -61.4273 | 61.7203 | -0.18948 | -5.0085 | -3.1896 | 3.8163 | 0.50779 | -0.21201 | -0.60752 | 61.7294 | 0.28069 | 61.6698 | -0.033101 | 0.043657 | 61.5478 | 0.007721 | 61.3398 | 61.2378 | 56.4188 | 58.2378 | 65.2436 | 61.9351 | 61.2153 | 60.8198 | 123.1567 | 61.708 | 123.0971 | 61.3942 | 61.471 | 122.9752 | 61.435 | 122.7671 | 61.6857 | 61.7217 | 61.6261 | 61.6621
4748.0938 | 123.3536 | -61.4365 | 61.7065 | -0.25816 | -5.1184 | -4.2838 | 3.6652 | 0.52611 | -0.28069 | -0.59379 | 61.7294 | 0.28069 | 61.6377 | -0.033101 | 0.052814 | 61.5387 | 0.007721 | 61.326 | 61.1783 | 56.318 | 57.1526 | 65.1017 | 61.9626 | 61.1558 | 60.8427 | 123.1659 | 61.7171 | 123.0742 | 61.4034 | 61.4893 | 122.9752 | 61.4442 | 122.7625 | 61.6766 | 61.7217 | 61.5849 | 61.63
4749.0625 | 123.3444 | -61.441 | 61.7157 | -0.38635 | -5.1688 | -4.1556 | 3.8575 | 0.30636 | -0.40888 | -0.58921 | 61.7386 | 0.27153 | 61.6515 | -0.03768 | 0.039079 | 61.5387 | 0.007721 | 61.3169 | 61.0547 | 56.2722 | 57.2854 | 65.2986 | 61.7474 | 61.0322 | 60.8518 | 123.1796 | 61.7126 | 123.0925 | 61.4034 | 61.4801 | 122.9797 | 61.4488 | 122.7579 | 61.6995 | 61.7308 | 61.6124 | 61.6438
4750.1094 | 123.3215 | -61.4594 | 61.734 | -0.27189 | -4.9032 | -3.8214 | 4.5443 | 0.42539 | -0.29442 | -0.49764 | 61.734 | 0.28526 | 61.6606 | -0.033101 | 0.043657 | 61.557 | 0.007721 | 61.3352 | 61.1875 | 56.5561 | 57.638 | 66.0037 | 61.8847 | 61.1649 | 60.9617 | 123.1933 | 61.7446 | 123.12 | 61.4262 | 61.503 | 123.0164 | 61.4671 | 122.7945 | 61.6903 | 61.7263 | 61.617 | 61.6529
4751.0625 | 123.3902 | -61.4044 | 61.6745 | -0.34514 | -5.2192 | -4.4395 | 4.3887 | 0.25601 | -0.38141 | -0.7174 | 61.7477 | 0.28526 | 61.6835 | -0.023943 | 0.043657 | 61.5433 | 0.012299 | 61.3123 | 61.0593 | 56.1853 | 56.9649 | 65.7931 | 61.6604 | 61.023 | 60.687 | 123.1521 | 61.6897 | 123.088 | 61.3805 | 61.4481 | 122.9477 | 61.4167 | 122.7167 | 61.7041 | 61.7354 | 61.6399 | 61.6712
4752.0781 | 123.3398 | -61.4273 | 61.7157 | -0.28563 | -5.1093 | -3.6383 | 4.3291 | 0.28805 | -0.30816 | -0.72655 | 61.7294 | 0.27153 | 61.6423 | -0.03768 | 0.043657 | 61.5524 | 0.007721 | 61.3306 | 61.1417 | 56.318 | 57.7891 | 65.7564 | 61.7154 | 61.1191 | 60.7008 | 123.1567 | 61.6988 | 123.0696 | 61.3896 | 61.471 | 122.9797 | 61.435 | 122.7579 | 61.6857 | 61.7217 | 61.5987 | 61.6346
4753.0781 | 123.2849 | -61.4365 | 61.702 | -0.18032 | -4.8208 | -3.4368 | 4.0498 | 0.35214 | -0.20743 | -0.91426 | 61.7294 | 0.28069 | 61.6332 | -0.028522 | 0.043657 | 61.5478 | 0.003143 | 61.3443 | 61.2561 | 56.6157 | 57.9997 | 65.4863 | 61.7886 | 61.229 | 60.5222 | 123.1659 | 61.7171 | 123.0696 | 61.4079 | 61.4801 | 122.9843 | 61.4396 | 122.7808 | 61.6857 | 61.7263 | 61.5895 | 61.63
4754.0938 | 123.3078 | -61.4548 | 61.7523 | -0.033814 | -4.5186 | -2.9286 | 4.3337 | 0.65887 | -0.060926 | -1.0287 | 61.7202 | 0.27611 | 61.6377 | -0.033101 | 0.052814 | 61.557 | 0.012299 | 61.3443 | 61.421 | 56.9362 | 58.5262 | 65.7885 | 62.1136 | 61.3938 | 60.4261 | 123.175 | 61.7309 | 123.0925 | 61.4217 | 61.5076 | 123.0118 | 61.4671 | 122.7991 | 61.6674 | 61.7079 | 61.5849 | 61.6255
4755.0625 | 123.4314 | -61.4548 | 61.6608 | -0.038393 | -4.5461 | -3.1026 | 4.2284 | 0.60393 | -0.065504 | -1.1661 | 61.7202 | 0.27153 | 61.6515 | -0.033101 | 0.048236 | 61.5616 | 0.012299 | 61.3398 | 61.4164 | 56.9087 | 58.3522 | 65.6832 | 62.0587 | 61.3893 | 60.2887 | 123.175 | 61.7263 | 123.1063 | 61.4217 | 61.503 | 123.0164 | 61.4671 | 122.7945 | 61.672 | 61.7079 | 61.6032 | 61.6392
4756.0625 | 123.3719 | -61.4639 | 61.6791 | 0.021127 | -4.6926 | -3.4231 | 3.6973 | 0.56273 | -0.015142 | -1.1523 | 61.7248 | 0.27611 | 61.6606 | -0.033101 | 0.048236 | 61.557 | 0.003143 | 61.3352 | 61.4851 | 56.7713 | 58.0409 | 65.1612 | 62.0267 | 61.4488 | 60.3116 | 123.1887 | 61.74 | 123.1246 | 61.4308 | 61.5122 | 123.0209 | 61.4671 | 122.7991 | 61.6766 | 61.7217 | 61.6124 | 61.6575
4757.0938 | 123.3948 | -61.4319 | 61.7111 | -0.033814 | -4.775 | -3.8122 | 3.7019 | 0.53068 | -0.060926 | -1.1386 | 61.7294 | 0.28069 | 61.6332 | -0.028522 | 0.043657 | 61.5433 | 0.003143 | 61.3352 | 61.3981 | 56.6569 | 57.6196 | 65.1338 | 61.9626 | 61.371 | 60.2933 | 123.1613 | 61.7126 | 123.0651 | 61.4034 | 61.4755 | 122.9752 | 61.435 | 122.7671 | 61.6857 | 61.7263 | 61.5895 | 61.63
4758.0625 | 123.3124 | -61.4319 | 61.7294 | -0.061284 | -4.7475 | -3.8443 | 4.6863 | 0.60851 | -0.070082 | -1.0058 | 61.7248 | 0.28984 | 61.6332 | -0.028522 | 0.052814 | 61.5524 | 0.007721 | 61.3535 | 61.3706 | 56.6843 | 57.5876 | 66.1181 | 62.0404 | 61.3618 | 60.4261 | 123.1567 | 61.7217 | 123.0651 | 61.4034 | 61.4847 | 122.9843 | 61.4396 | 122.7854 | 61.672 | 61.7171 | 61.5804 | 61.6255
4759.0938 | 123.2941 | -61.4502 | 61.7432 | -0.079598 | -4.7888 | -3.6062 | 4.5352 | 0.59935 | -0.10671 | -0.76776 | 61.7248 | 0.27611 | 61.6561 | -0.033101 | 0.043657 | 61.5524 | 0.012299 | 61.3489 | 61.3706 | 56.6614 | 57.844 | 65.9854 | 62.0495 | 61.3435 | 60.6824 | 123.175 | 61.7263 | 123.1063 | 61.4171 | 61.4939 | 123.0026 | 61.4625 | 122.7991 | 61.6812 | 61.7125 | 61.6124 | 61.6438
4760.0625 | 123.3856 | -61.4777 | 61.6699 | 0.1539 | -4.5736 | -3.5009 | 4.2421 | 1.0205 | 0.11763 | -0.66704 | 61.7248 | 0.28069 | 61.6515 | -0.028522 | 0.048236 | 61.5616 | 0.007721 | 61.3627 | 61.6316 | 56.9041 | 57.9768 | 65.7198 | 62.4982 | 61.5953 | 60.8106 | 123.2025 | 61.7583 | 123.1291 | 61.4491 | 61.5259 | 123.0392 | 61.4854 | 122.8403 | 61.6766 | 61.7171 | 61.6032 | 61.6438
4761.0938 | 123.3719 | -61.4456 | 61.6882 | 0.094381 | -4.5781 | -3.6749 | 4.8373 | 1.0755 | 0.058113 | -0.64872 | 61.7111 | 0.27611 | 61.624 | -0.03768 | 0.039079 | 61.5662 | 0.003143 | 61.3672 | 61.54 | 56.8675 | 57.7707 | 66.283 | 62.5211 | 61.5037 | 60.7969 | 123.1567 | 61.7217 | 123.0696 | 61.4079 | 61.4847 | 123.0118 | 61.4488 | 122.8129 | 61.672 | 61.7079 | 61.5849 | 61.6209
4762.0625 | 123.2895 | -61.4594 | 61.6974 | 0.080646 | -4.6148 | -4.0366 | 4.9427 | 1.0938 | 0.035221 | -0.73113 | 61.7157 | 0.28069 | 61.6194 | -0.028522 | 0.048236 | 61.5616 | 0.003143 | 61.3672 | 61.54 | 56.8446 | 57.4228 | 66.402 | 62.5531 | 61.4946 | 60.7282 | 123.175 | 61.74 | 123.0788 | 61.4308 | 61.5076 | 123.0209 | 61.4625 | 122.8266 | 61.6674 | 61.7125 | 61.5712 | 61.6163
4763.1094 | 123.3673 | -61.4227 | 61.6562 | 0.034862 | -4.6972 | -4.1236 | 4.906 | 1.0434 | 0.00775 | -0.86848 | 61.7111 | 0.28069 | 61.6469 | -0.03768 | 0.048236 | 61.5616 | -0.001436 | 61.3581 | 61.4576 | 56.7256 | 57.2991 | 66.3288 | 62.4661 | 61.4305 | 60.5543 | 123.1338 | 61.7034 | 123.0696 | 61.385 | 61.471 | 122.9843 | 61.4213 | 122.7808 | 61.6628 | 61.7125 | 61.5987 | 61.6483
4764.0625 | 123.3078 | -61.4731 | 61.6745 | 0.044018 | -4.7155 | -4.0549 | 4.2788 | 1.0022 | 0.016907 | -0.90052 | 61.734 | 0.28526 | 61.6606 | -0.033101 | 0.048236 | 61.5616 | -0.001436 | 61.3581 | 61.5171 | 56.7576 | 57.4182 | 65.7519 | 62.4753 | 61.49 | 60.5726 | 123.2071 | 61.7583 | 123.1337 | 61.44 | 61.5213 | 123.0347 | 61.4716 | 122.8312 | 61.6857 | 61.7354 | 61.6124 | 61.6621
4765.0938 | 123.3627 | -61.4319 | 61.7157 | 0.01197 | -4.8208 | -4.3113 | 4.0361 | 0.93812 | -0.005985 | -0.98751 | 61.734 | 0.28526 | 61.6744 | -0.028522 | 0.043657 | 61.5478 | 0.012299 | 61.3489 | 61.4439 | 56.6111 | 57.1206 | 65.468 | 62.37 | 61.4259 | 60.4444 | 123.1659 | 61.7171 | 123.1063 | 61.4034 | 61.4755 | 122.9797 | 61.4442 | 122.7808 | 61.6903 | 61.7217 | 61.6307 | 61.6621
4766.0625 | 123.3719 | -61.441 | 61.6516 | 0.13101 | -4.6377 | -4.0457 | 4.1689 | 0.9839 | 0.081005 | -0.87305 | 61.7248 | 0.28069 | 61.6606 | -0.028522 | 0.043657 | 61.557 | 0.003143 | 61.3398 | 61.572 | 56.8034 | 57.3953 | 65.6099 | 62.4249 | 61.522 | 60.568 | 123.1659 | 61.7217 | 123.1017 | 61.4125 | 61.4847 | 122.998 | 61.4442 | 122.7808 | 61.6812 | 61.7217 | 61.617 | 61.6575
4767.0938 | 123.3078 | -61.4227 | 61.7432 | -0.070441 | -4.9215 | -3.3635 | 4.4115 | 0.53526 | -0.092974 | -1.1111 | 61.7248 | 0.28526 | 61.6606 | -0.028522 | 0.043657 | 61.5616 | 0.007721 | 61.3398 | 61.3523 | 56.5012 | 58.0592 | 65.8343 | 61.958 | 61.3298 | 60.3116 | 123.1475 | 61.708 | 123.0834 | 61.3942 | 61.4664 | 122.9843 | 61.4304 | 122.7625 | 61.6812 | 61.7171 | 61.617 | 61.6529
4768.0625 | 123.3261 | -61.441 | 61.702 | -0.14369 | -4.9948 | -4.3525 | 4.2559 | 0.46659 | -0.17081 | -1.1386 | 61.7386 | 0.28069 | 61.6515 | -0.03768 | 0.043657 | 61.5478 | 0.003143 | 61.3215 | 61.2973 | 56.4462 | 57.0885 | 65.6969 | 61.9076 | 61.2702 | 60.3025 | 123.1796 | 61.7217 | 123.0925 | 61.4034 | 61.4847 | 122.9889 | 61.4442 | 122.7625 | 61.6949 | 61.7354 | 61.6078 | 61.6483
4769.1094 | 123.2986 | -61.4182 | 61.7065 | -0.10707 | -4.8574 | -4.2884 | 4.0498 | 0.53984 | -0.1296 | -1.1661 | 61.734 | 0.28069 | 61.6423 | -0.033101 | 0.048236 | 61.5478 | 0.012299 | 61.3352 | 61.3111 | 56.5607 | 57.1297 | 65.468 | 61.958 | 61.2886 | 60.2521 | 123.1521 | 61.6988 | 123.0605 | 61.3851 | 61.4664 | 122.966 | 61.4305 | 122.7533 | 61.6857 | 61.7217 | 61.5941 | 61.63
4770.0625 | 123.3215 | -61.4365 | 61.702 | -0.015501 | -4.6972 | -4.2472 | 3.6607 | 0.60393 | -0.028877 | -1.1111 | 61.7248 | 0.28069 | 61.6377 | -0.033101 | 0.043657 | 61.5478 | 0.007721 | 61.326 | 61.421 | 56.7393 | 57.1893 | 65.0971 | 62.0404 | 61.4076 | 60.3253 | 123.1613 | 61.7171 | 123.0742 | 61.4034 | 61.4801 | 122.9843 | 61.4442 | 122.7625 | 61.6812 | 61.7171 | 61.5941 | 61.63
4771.0781 | 123.2986 | -61.4182 | 61.7477 | -0.052128 | -4.9627 | -4.0824 | 4.407 | 0.51237 | -0.083817 | -1.1615 | 61.734 | 0.27611 | 61.6332 | -0.033101 | 0.048236 | 61.5478 | 0.003143 | 61.3306 | 61.366 | 56.4554 | 57.3358 | 65.8251 | 61.9305 | 61.3343 | 60.2567 | 123.1521 | 61.6943 | 123.0513 | 61.3851 | 61.4664 | 122.966 | 61.4213 | 122.7488 | 61.6857 | 61.7308 | 61.5849 | 61.63
4772.0625 | 123.4222 | -61.3998 | 61.6653 | -0.1208 | -5.0223 | -4.3205 | 3.5599 | 0.38419 | -0.14334 | -1.1935 | 61.734 | 0.28526 | 61.6698 | -0.03768 | 0.043657 | 61.5341 | 0.012299 | 61.3169 | 61.279 | 56.3776 | 57.0794 | 64.9598 | 61.784 | 61.2565 | 60.2063 | 123.1338 | 61.6851 | 123.0696 | 61.3622 | 61.4435 | 122.934 | 61.4121 | 122.7167 | 61.6903 | 61.7217 | 61.6261 | 61.6575
4773.0781 | 123.3307 | -61.4273 | 61.7203 | -0.084176 | -5.0543 | -3.9908 | 4.0132 | 0.41166 | -0.10213 | -1.4133 | 61.7431 | 0.27153 | 61.6698 | -0.028522 | 0.039079 | 61.5433 | 0.012299 | 61.3352 | 61.3431 | 56.373 | 57.4365 | 65.4405 | 61.839 | 61.3252 | 60.014 | 123.1704 | 61.6988 | 123.0971 | 61.3988 | 61.4664 | 122.9706 | 61.4396 | 122.7625 | 61.7041 | 61.7308 | 61.6307 | 61.6575
4774.0625 | 123.3765 | -61.4227 | 61.6608 | -0.065863 | -4.9811 | -3.9679 | 4.2925 | 0.48948 | -0.088396 | -1.3858 | 61.734 | 0.28069 | 61.6698 | -0.033101 | 0.048236 | 61.5433 | 0.007721 | 61.326 | 61.3569 | 56.4417 | 57.4548 | 65.7152 | 61.9122 | 61.3343 | 60.0369 | 123.1567 | 61.7034 | 123.0925 | 61.3896 | 61.471 | 122.966 | 61.4304 | 122.7488 | 61.6857 | 61.7263 | 61.6216 | 61.6621
4775.1094 | 123.4543 | -61.3861 | 61.7157 | -0.065863 | -4.9719 | -3.8809 | 3.418 | 0.41166 | -0.097553 | -1.34 | 61.7477 | 0.28069 | 61.679 | -0.028522 | 0.048236 | 61.5387 | 0.007721 | 61.326 | 61.3202 | 56.4142 | 57.5052 | 64.8041 | 61.7978 | 61.2886 | 60.0461 | 123.1338 | 61.6668 | 123.0651 | 61.3576 | 61.4343 | 122.9248 | 61.3938 | 122.7121 | 61.6995 | 61.74 | 61.6307 | 61.6712
4776.0625 | 123.3719 | -61.4319 | 61.6699 | -0.19864 | -5.0681 | -4.0595 | 3.5142 | 0.37503 | -0.22575 | -1.0699 | 61.7477 | 0.27611 | 61.6698 | -0.033101 | 0.043657 | 61.5387 | 0.003143 | 61.3306 | 61.2332 | 56.3638 | 57.3724 | 64.946 | 61.8069 | 61.2061 | 60.362 | 123.1796 | 61.708 | 123.1017 | 61.3988 | 61.4755 | 122.9706 | 61.435 | 122.7625 | 61.7041 | 61.7446 | 61.6261 | 61.6667
4777.0938 | 123.3261 | -61.409 | 61.6974 | -0.27647 | -5.123 | -4.3846 | 3.9537 | 0.34757 | -0.30816 | -0.98751 | 61.7477 | 0.27153 | 61.6652 | -0.033101 | 0.043657 | 61.5295 | 0.003143 | 61.326 | 61.1325 | 56.286 | 57.0244 | 65.3627 | 61.7566 | 61.1008 | 60.4215 | 123.1567 | 61.6805 | 123.0742 | 61.3759 | 61.4527 | 122.9385 | 61.4121 | 122.735 | 61.7041 | 61.7446 | 61.6216 | 61.6621
4778.0625 | 123.4085 | -61.4273 | 61.6699 | -0.21237 | -5.1459 | -4.4258 | 3.8759 | 0.54442 | -0.2349 | -0.91884 | 61.7386 | 0.27611 | 61.6515 | -0.033101 | 0.039079 | 61.5387 | 0.003143 | 61.3306 | 61.2149 | 56.2814 | 57.0015 | 65.3032 | 61.9717 | 61.1924 | 60.5085 | 123.1659 | 61.7034 | 123.0788 | 61.3942 | 61.4664 | 122.966 | 61.4305 | 122.7579 | 61.6995 | 61.7354 | 61.6124 | 61.6483
4779.0781 | 123.2712 | -61.4182 | 61.7249 | -0.1849 | -5.1367 | -3.8809 | 4.2696 | 0.58562 | -0.21201 | -0.91884 | 61.7248 | 0.27611 | 61.6332 | -0.028522 | 0.039079 | 61.5433 | 0.007721 | 61.326 | 61.2333 | 56.2814 | 57.5372 | 65.6878 | 62.0038 | 61.2061 | 60.4993 | 123.143 | 61.6943 | 123.0513 | 61.3896 | 61.4572 | 122.9614 | 61.4259 | 122.7442 | 61.6857 | 61.7171 | 61.5941 | 61.6255
4780.0625 | 123.3856 | -61.4273 | 61.647 | -0.16201 | -5.2146 | -3.9404 | 4.1918 | 0.58562 | -0.18454 | -1.1386 | 61.734 | 0.28526 | 61.6377 | -0.028522 | 0.043657 | 61.5433 | 0.012299 | 61.3306 | 61.2653 | 56.2127 | 57.4869 | 65.6191 | 62.0129 | 61.2428 | 60.2887 | 123.1613 | 61.7126 | 123.0651 | 61.3988 | 61.471 | 122.9706 | 61.4396 | 122.7579 | 61.6903 | 61.7217 | 61.5941 | 61.6255
4781.0938 | 123.3261 | -61.4456 | 61.702 | -0.061284 | -5.2192 | -4.5128 | 4.2742 | 0.755 | -0.088396 | -1.1203 | 61.7386 | 0.28069 | 61.6515 | -0.023943 | 0.039079 | 61.5433 | 0.007721 | 61.3306 | 61.3843 | 56.2265 | 56.9329 | 65.7198 | 62.2006 | 61.3572 | 60.3253 | 123.1842 | 61.7263 | 123.0971 | 61.4217 | 61.4847 | 122.9889 | 61.4533 | 122.7762 | 61.6995 | 61.7308 | 61.6124 | 61.6438
4782.0625 | 123.3444 | -61.4456 | 61.6882 | -0.024657 | -5.1276 | -4.4441 | 4.3383 | 0.80536 | -0.056347 | -0.89594 | 61.7386 | 0.27611 | 61.6515 | -0.028522 | 0.043657 | 61.5387 | 0.007721 | 61.3306 | 61.421 | 56.318 | 57.0015 | 65.7839 | 62.251 | 61.3893 | 60.5497 | 123.1842 | 61.7217 | 123.0971 | 61.4171 | 61.4893 | 122.9843 | 61.4533 | 122.7762 | 61.6949 | 61.7308 | 61.6078 | 61.6438
4783.0938 | 123.381 | -61.4456 | 61.6745 | -0.024657 | -5.1642 | -4.6593 | 4.5947 | 0.85114 | -0.056347 | -0.83643 | 61.7386 | 0.27153 | 61.6698 | -0.03768 | 0.048236 | 61.5524 | 0.003143 | 61.326 | 61.421 | 56.2814 | 56.7863 | 66.0403 | 62.2968 | 61.3893 | 60.6092 | 123.1842 | 61.7171 | 123.1154 | 61.4079 | 61.4939 | 122.998 | 61.4488 | 122.7717 | 61.6903 | 61.7354 | 61.6216 | 61.6667
4784.0625 | 123.3856 | -61.4182 | 61.6882 | -0.006344 | -5.1551 | -4.6959 | 4.0911 | 0.90608 | -0.033455 | -0.83185 | 61.7477 | 0.28069 | 61.6744 | -0.033101 | 0.043657 | 61.5433 | 0.007721 | 61.3352 | 61.4118 | 56.2631 | 56.7222 | 65.5092 | 62.3242 | 61.3847 | 60.5863 | 123.1659 | 61.6988 | 123.0925 | 61.3851 | 61.4618 | 122.9614 | 61.4259 | 122.7533 | 61.7041 | 61.74 | 61.6307 | 61.6667
4785.0625 | 123.4131 | -61.3953 | 61.6837 | -0.097912 | -5.3748 | -4.9157 | 3.7797 | 0.76874 | -0.1296 | -0.87305 | 61.7386 | 0.28069 | 61.6515 | -0.033101 | 0.048236 | 61.5387 | 0.007721 | 61.3398 | 61.2974 | 56.0204 | 56.4796 | 65.175 | 62.164 | 61.2657 | 60.5222 | 123.1338 | 61.6759 | 123.0467 | 61.3622 | 61.4435 | 122.934 | 61.403 | 122.735 | 61.6903 | 61.7308 | 61.6032 | 61.6438
4786.0938 | 123.3673 | -61.4548 | 61.6837 | -0.088755 | -5.4252 | -5.0439 | 4.0407 | 0.80536 | -0.11587 | -0.76776 | 61.7431 | 0.28526 | 61.6561 | -0.028522 | 0.043657 | 61.5387 | 0.007721 | 61.3352 | 61.366 | 56.0296 | 56.4109 | 65.4955 | 62.2601 | 61.3389 | 60.687 | 123.1979 | 61.74 | 123.1108 | 61.4263 | 61.4984 | 122.9935 | 61.4625 | 122.79 | 61.6995 | 61.7354 | 61.6124 | 61.6483
4787.0625 | 123.4131 | -61.3953 | 61.6837 | -0.033814 | -5.4756 | -4.7051 | 3.6103 | 0.88319 | -0.065504 | -0.8639 | 61.7477 | 0.28984 | 61.6698 | -0.033101 | 0.043657 | 61.5433 | 0.003143 | 61.3443 | 61.3614 | 55.9197 | 56.6902 | 65.0056 | 62.2785 | 61.3298 | 60.5314 | 123.143 | 61.6851 | 123.0651 | 61.3622 | 61.4389 | 122.9385 | 61.3984 | 122.7396 | 61.7041 | 61.7446 | 61.6261 | 61.6667
4788.0781 | 123.3444 | -61.4639 | 61.6745 | -0.061284 | -5.3977 | -4.3754 | 4.1002 | 0.85114 | -0.079239 | -0.88221 | 61.734 | 0.27611 | 61.6698 | -0.028522 | 0.052814 | 61.5433 | -0.001436 | 61.3352 | 61.4026 | 56.0662 | 57.0885 | 65.5641 | 62.3151 | 61.3847 | 60.5817 | 123.1979 | 61.74 | 123.1337 | 61.4354 | 61.5167 | 123.0072 | 61.4625 | 122.7991 | 61.6812 | 61.7354 | 61.617 | 61.6712
4789.0625 | 123.3582 | -61.4456 | 61.6745 | -0.10249 | -5.3474 | -4.4487 | 4.2513 | 0.83741 | -0.12044 | -0.8639 | 61.7294 | 0.27611 | 61.6561 | -0.033101 | 0.048236 | 61.5478 | 0.003143 | 61.3489 | 61.3431 | 56.0982 | 56.997 | 65.6969 | 62.283 | 61.3252 | 60.5817 | 123.175 | 61.7217 | 123.1017 | 61.4125 | 61.4939 | 122.9935 | 61.4488 | 122.7945 | 61.6812 | 61.7263 | 61.6078 | 61.6529
4790.0938 | 123.2803 | -61.4502 | 61.734 | -0.17574 | -5.3657 | -4.1968 | 4.1964 | 0.72296 | -0.1937 | -0.7586 | 61.734 | 0.27611 | 61.6423 | -0.028522 | 0.057392 | 61.5478 | 0.007721 | 61.3489 | 61.2745 | 56.0845 | 57.2534 | 65.6466 | 62.1732 | 61.2565 | 60.6916 | 123.1842 | 61.7263 | 123.0925 | 61.4217 | 61.5076 | 122.998 | 61.4579 | 122.7991 | 61.6766 | 61.7263 | 61.5849 | 61.6346
4791.0625 | 123.3627 | -61.409 | 61.6928 | -0.15743 | -5.4985 | -4.2106 | 4.2742 | 0.71838 | -0.17539 | -0.59379 | 61.7386 | 0.28069 | 61.6515 | -0.028522 | 0.057392 | 61.5524 | 0.003143 | 61.3443 | 61.2516 | 55.9105 | 57.1984 | 65.6832 | 62.1274 | 61.2336 | 60.8152 | 123.1476 | 61.6897 | 123.0605 | 61.3805 | 61.4664 | 122.9614 | 61.4121 | 122.7533 | 61.6812 | 61.7354 | 61.5941 | 61.6483
4792.0938 | 123.4039 | -61.409 | 61.6516 | -0.16201 | -5.6175 | -4.3571 | 4.3978 | 0.63598 | -0.18454 | -0.64414 | 61.7386 | 0.28069 | 61.6744 | -0.028522 | 0.048236 | 61.5433 | 0.003143 | 61.3352 | 61.247 | 55.7915 | 57.0519 | 65.8068 | 62.045 | 61.2245 | 60.7649 | 123.1476 | 61.6897 | 123.0834 | 61.3805 | 61.4572 | 122.9523 | 61.4121 | 122.7442 | 61.6903 | 61.7354 | 61.6261 | 61.6712
4793.0625 | 123.4039 | -61.4182 | 61.7065 | -0.10249 | -5.5534 | -4.5677 | 4.3841 | 0.68176 | -0.13418 | -0.73571 | 61.734 | 0.27611 | 61.6744 | -0.028522 | 0.057392 | 61.5433 | 0.003143 | 61.3306 | 61.3157 | 55.8647 | 56.8504 | 65.8022 | 62.0999 | 61.284 | 60.6824 | 123.1521 | 61.6943 | 123.0925 | 61.3896 | 61.4755 | 122.9614 | 61.4213 | 122.7488 | 61.6766 | 61.7308 | 61.617 | 61.6712
4794.0781 | 123.2803 | -61.4548 | 61.7157 | -0.1849 | -5.6954 | -4.728 | 4.233 | 0.61309 | -0.21201 | -0.76776 | 61.7386 | 0.28069 | 61.6515 | -0.028522 | 0.039079 | 61.5387 | 0.003143 | 61.3215 | 61.2699 | 55.7594 | 56.7268 | 65.6878 | 62.0679 | 61.2428 | 60.687 | 123.1933 | 61.7355 | 123.1063 | 61.4263 | 61.4939 | 122.9935 | 61.4579 | 122.7762 | 61.6995 | 61.7354 | 61.6124 | 61.6483
4795.0625 | 123.3307 | -61.4365 | 61.734 | -0.20321 | -5.8098 | -4.7096 | 4.3566 | 0.60851 | -0.2349 | -0.67619 | 61.7386 | 0.27611 | 61.6469 | -0.033101 | 0.048236 | 61.5387 | 0.003143 | 61.3306 | 61.2332 | 55.6266 | 56.7268 | 65.7931 | 62.045 | 61.2016 | 60.7603 | 123.175 | 61.7126 | 123.0834 | 61.4034 | 61.4847 | 122.9752 | 61.4396 | 122.7671 | 61.6903 | 61.7354 | 61.5987 | 61.6438
4796.0938 | 123.2941 | -61.4594 | 61.6974 | -0.18032 | -5.8053 | -4.641 | 4.3841 | 0.58104 | -0.20286 | -0.55258 | 61.7523 | 0.27611 | 61.6744 | -0.033101 | 0.048236 | 61.5524 | 0.003143 | 61.3169 | 61.279 | 55.6541 | 56.8184 | 65.8434 | 62.0404 | 61.2565 | 60.9068 | 123.2116 | 61.7355 | 123.1337 | 61.4262 | 61.5076 | 123.0118 | 61.4625 | 122.7762 | 61.7041 | 61.7491 | 61.6261 | 61.6712
4797.0625 | 123.3765 | -61.4136 | 61.6974 | -0.17574 | -5.8602 | -4.7417 | 3.5096 | 0.60851 | -0.20743 | -0.5709 | 61.7569 | 0.27611 | 61.6835 | -0.03768 | 0.048236 | 61.5387 | 0.007721 | 61.326 | 61.2378 | 55.5534 | 56.6719 | 64.9232 | 62.0221 | 61.2061 | 60.8427 | 123.1704 | 61.6897 | 123.0971 | 61.3759 | 61.4618 | 122.9523 | 61.4213 | 122.7396 | 61.7086 | 61.7491 | 61.6353 | 61.6758
4798.1094 | 123.4314 | -61.3998 | 61.6882 | -0.17574 | -5.8694 | -4.8745 | 3.4684 | 0.75043 | -0.19828 | -0.5709 | 61.7523 | 0.28069 | 61.6835 | -0.033101 | 0.048236 | 61.5295 | 0.003143 | 61.3306 | 61.2241 | 55.5305 | 56.5254 | 64.8682 | 62.1503 | 61.2016 | 60.8289 | 123.1521 | 61.6805 | 123.0834 | 61.3667 | 61.4481 | 122.9294 | 61.403 | 122.7305 | 61.7041 | 61.7491 | 61.6353 | 61.6804
4799.0625 | 123.381 | -61.4182 | 61.702 | -0.2902 | -6.0205 | -5.1034 | 3.7477 | 0.48948 | -0.31732 | -0.73571 | 61.7523 | 0.27611 | 61.6881 | -0.028522 | 0.048236 | 61.5295 | 0.007721 | 61.3306 | 61.1279 | 55.3977 | 56.3147 | 65.1658 | 61.9076 | 61.1008 | 60.6824 | 123.1704 | 61.6943 | 123.1063 | 61.3896 | 61.4664 | 122.9477 | 61.4259 | 122.7488 | 61.7041 | 61.7446 | 61.6399 | 61.6804
4800.0781 | 123.2483 | -61.4639 | 61.6608 | -0.2902 | -6.0388 | -5.2179 | 4.0086 | 0.51695 | -0.32189 | -0.67161 | 61.7477 | 0.28069 | 61.6744 | -0.028522 | 0.039079 | 61.5295 | 0.007721 | 61.326 | 61.1737 | 55.4252 | 56.2461 | 65.4726 | 61.9809 | 61.142 | 60.7923 | 123.2116 | 61.7446 | 123.1383 | 61.4354 | 61.503 | 122.9935 | 61.4716 | 122.79 | 61.7086 | 61.74 | 61.6353 | 61.6667
4801.0625 | 123.3856 | -61.4044 | 61.7157 | -0.36346 | -6.0617 | -5.2179 | 3.7293 | 0.52153 | -0.39515 | -0.64414 | 61.7477 | 0.27611 | 61.6515 | -0.033101 | 0.043657 | 61.5295 | 0.007721 | 61.3215 | 61.041 | 55.3428 | 56.1865 | 65.1338 | 61.9259 | 61.0093 | 60.7603 | 123.1521 | 61.6805 | 123.0559 | 61.3713 | 61.4481 | 122.934 | 61.4121 | 122.7259 | 61.7041 | 61.74 | 61.6078 | 61.6438
4802.0781 | 123.3261 | -61.441 | 61.7157 | -0.3131 | -6.0388 | -5.3461 | 4.1872 | 0.73669 | -0.35394 | -0.59836 | 61.7477 | 0.27611 | 61.6561 | -0.033101 | 0.043657 | 61.5295 | 0.012299 | 61.3123 | 61.1279 | 55.4023 | 56.095 | 65.6282 | 62.1777 | 61.0871 | 60.8427 | 123.1888 | 61.7171 | 123.0971 | 61.4079 | 61.4847 | 122.9706 | 61.4533 | 122.7533 | 61.7041 | 61.7354 | 61.6124 | 61.6438
4803.0625 | 123.4039 | -61.3998 | 61.702 | -0.25358 | -6.0571 | -5.2408 | 3.9674 | 0.80994 | -0.28069 | -0.7174 | 61.7477 | 0.28069 | 61.6561 | -0.033101 | 0.043657 | 61.5341 | 0.007721 | 61.3123 | 61.1463 | 55.3428 | 56.1591 | 65.3673 | 62.2098 | 61.1192 | 60.6824 | 123.1476 | 61.6805 | 123.0559 | 61.3667 | 61.4435 | 122.934 | 61.4076 | 122.7121 | 61.7041 | 61.74 | 61.6124 | 61.6483
4804.0938 | 123.3307 | -61.4136 | 61.702 | -0.25358 | -6.1532 | -5.3827 | 3.4226 | 0.76416 | -0.28985 | -0.79065 | 61.7523 | 0.28069 | 61.679 | -0.033101 | 0.043657 | 61.5204 | 0.012299 | 61.3031 | 61.16 | 55.2603 | 56.0309 | 64.8362 | 62.1777 | 61.1237 | 60.6229 | 123.1659 | 61.6943 | 123.0925 | 61.3805 | 61.4572 | 122.934 | 61.4259 | 122.7167 | 61.7086 | 61.74 | 61.6353 | 61.6667
4805.0625 | 123.3444 | -61.3998 | 61.7111 | -0.249 | -6.2128 | -5.6071 | 3.4638 | 0.80536 | -0.28069 | -1.047 | 61.766 | 0.27611 | 61.6973 | -0.033101 | 0.052814 | 61.5158 | 0.007721 | 61.3031 | 61.1508 | 55.1871 | 55.7928 | 64.8636 | 62.2052 | 61.1192 | 60.3528 | 123.1659 | 61.6759 | 123.0971 | 61.3667 | 61.4527 | 122.9156 | 61.4076 | 122.703 | 61.7132 | 61.7583 | 61.6445 | 61.6895
4806.0938 | 123.3261 | -61.4182 | 61.7294 | -0.23526 | -6.2036 | -5.3644 | 4.0224 | 0.8191 | -0.26695 | -1.0379 | 61.766 | 0.27611 | 61.7018 | -0.03768 | 0.048236 | 61.5204 | 0.003143 | 61.2986 | 61.1829 | 55.2145 | 56.0538 | 65.4405 | 62.2372 | 61.1512 | 60.3803 | 123.1842 | 61.6943 | 123.12 | 61.3805 | 61.4664 | 122.9385 | 61.4213 | 122.7167 | 61.7178 | 61.7629 | 61.6536 | 61.6987
4807.0625 | 123.349 | -61.3998 | 61.6974 | -0.23984 | -6.1349 | -5.3827 | 4.0224 | 0.78705 | -0.26238 | -1.0196 | 61.7569 | 0.27153 | 61.6927 | -0.033101 | 0.048236 | 61.525 | 0.007721 | 61.3077 | 61.16 | 55.2649 | 56.0171 | 65.4222 | 62.1869 | 61.1375 | 60.3803 | 123.1567 | 61.6714 | 123.0925 | 61.3667 | 61.4481 | 122.9248 | 61.4076 | 122.7076 | 61.7086 | 61.7491 | 61.6445 | 61.685
4808.0938 | 123.4085 | -61.409 | 61.6974 | -0.2902 | -6.0662 | -5.3781 | 3.885 | 0.69549 | -0.31274 | -0.98293 | 61.7569 | 0.28526 | 61.6835 | -0.042259 | 0.048236 | 61.525 | 0.003143 | 61.294 | 61.1188 | 55.3428 | 56.0309 | 65.294 | 62.1045 | 61.0963 | 60.4261 | 123.1659 | 61.6943 | 123.0925 | 61.3667 | 61.4572 | 122.934 | 61.4121 | 122.703 | 61.7086 | 61.7537 | 61.6353 | 61.6804
4809.0625 | 123.3719 | -61.377 | 61.7203 | -0.27189 | -5.9792 | -5.5246 | 4.0041 | 0.78247 | -0.28985 | -0.85016 | 61.7431 | 0.27611 | 61.6606 | -0.03768 | 0.043657 | 61.525 | 0.003143 | 61.3169 | 61.1051 | 55.3977 | 55.8523 | 65.381 | 62.1594 | 61.0871 | 60.5268 | 123.1201 | 61.6531 | 123.0376 | 61.3393 | 61.4206 | 122.9019 | 61.3801 | 122.6938 | 61.6995 | 61.74 | 61.617 | 61.6575
4810.0938 | 123.3902 | -61.3998 | 61.6745 | -0.26731 | -6.0571 | -5.2866 | 3.4043 | 0.84198 | -0.30358 | -0.66246 | 61.7523 | 0.27611 | 61.6606 | -0.033101 | 0.043657 | 61.525 | 0.007721 | 61.3077 | 61.1325 | 55.3428 | 56.1133 | 64.8041 | 62.2418 | 61.0963 | 60.7374 | 123.1521 | 61.6759 | 123.0605 | 61.3667 | 61.4435 | 122.9248 | 61.4076 | 122.7076 | 61.7086 | 61.7446 | 61.617 | 61.6529
4811.0625 | 123.3353 | -61.3907 | 61.7157 | -0.30394 | -6.1029 | -5.4285 | 3.331 | 0.9015 | -0.33105 | -0.7174 | 61.7706 | 0.27611 | 61.7018 | -0.033101 | 0.039079 | 61.525 | 0.003143 | 61.3031 | 61.0867 | 55.2878 | 55.9622 | 64.7217 | 62.2922 | 61.0596 | 60.6733 | 123.1613 | 61.6668 | 123.0925 | 61.3576 | 61.4298 | 122.9156 | 61.3938 | 122.6938 | 61.7315 | 61.7675 | 61.6628 | 61.6987
4812.0781 | 123.317 | -61.4227 | 61.7157 | -0.26731 | -5.9518 | -5.5109 | 3.5233 | 1.0022 | -0.29442 | -0.76776 | 61.7614 | 0.27611 | 61.6973 | -0.033101 | 0.048236 | 61.525 | 0.007721 | 61.3031 | 61.1554 | 55.471 | 55.9118 | 64.946 | 62.4249 | 61.1283 | 60.655 | 123.1842 | 61.6988 | 123.12 | 61.3896 | 61.471 | 122.9477 | 61.4304 | 122.7259 | 61.7132 | 61.7537 | 61.649 | 61.6895
4813.0625 | 123.3078 | -61.4044 | 61.7523 | -0.26273 | -6.025 | -5.4697 | 3.6332 | 1.0205 | -0.29442 | -0.74486 | 61.7569 | 0.28069 | 61.6606 | -0.028522 | 0.048236 | 61.5341 | 0.007721 | 61.3169 | 61.1417 | 55.3794 | 55.9347 | 65.0376 | 62.4249 | 61.11 | 60.6596 | 123.1613 | 61.6851 | 123.0651 | 61.3759 | 61.4527 | 122.9385 | 61.4121 | 122.7213 | 61.7086 | 61.7491 | 61.6124 | 61.6529
4814.0781 | 123.3582 | -61.409 | 61.6745 | -0.26731 | -6.0113 | -5.6208 | 3.7156 | 0.99306 | -0.29442 | -0.83185 | 61.7523 | 0.28069 | 61.6561 | -0.033101 | 0.039079 | 61.5295 | 0.007721 | 61.3031 | 61.1417 | 55.3977 | 55.7882 | 65.1246 | 62.4021 | 61.1146 | 60.5771 | 123.1613 | 61.6897 | 123.0651 | 61.3759 | 61.4481 | 122.9385 | 61.4167 | 122.7121 | 61.7132 | 61.7446 | 61.617 | 61.6483
4815.0625 | 123.4222 | -61.3632 | 61.7157 | -0.23526 | -5.9335 | -5.5109 | 3.8347 | 1.0755 | -0.2578 | -0.69908 | 61.7477 | 0.28526 | 61.6835 | -0.028522 | 0.039079 | 61.5341 | 0.012299 | 61.3215 | 61.128 | 55.4298 | 55.8523 | 65.1979 | 62.4387 | 61.1054 | 60.6641 | 123.1109 | 61.6485 | 123.0468 | 61.3347 | 61.4023 | 122.8973 | 61.3755 | 122.6847 | 61.7086 | 61.7354 | 61.6445 | 61.6712
4816.0938 | 123.3032 | -61.4182 | 61.702 | -0.24442 | -5.8602 | -5.488 | 3.9125 | 1.0663 | -0.26695 | -0.72197 | 61.7523 | 0.27153 | 61.6927 | -0.042259 | 0.048236 | 61.5295 | 0.007721 | 61.3169 | 61.1737 | 55.558 | 55.9301 | 65.3306 | 62.4845 | 61.1512 | 60.6962 | 123.1704 | 61.6897 | 123.1108 | 61.3759 | 61.4664 | 122.9477 | 61.4259 | 122.735 | 61.7041 | 61.7446 | 61.6445 | 61.685
4817.0625 | 123.3765 | -61.3861 | 61.7294 | -0.23526 | -5.8007 | -5.5201 | 3.624 | 1.0617 | -0.25322 | -0.81354 | 61.7523 | 0.27611 | 61.6652 | -0.028522 | 0.052814 | 61.5295 | 0.007721 | 61.3215 | 61.1508 | 55.5854 | 55.8661 | 65.0102 | 62.4478 | 61.1329 | 60.5726 | 123.1384 | 61.6622 | 123.0513 | 61.3576 | 61.4389 | 122.9156 | 61.3938 | 122.7076 | 61.6995 | 61.7446 | 61.6124 | 61.6575
4818.0938 | 123.3856 | -61.377 | 61.7203 | -0.19864 | -5.7183 | -5.4514 | 3.6652 | 0.97475 | -0.22575 | -0.74029 | 61.7477 | 0.27153 | 61.6606 | -0.028522 | 0.043657 | 61.5341 | 0.007721 | 61.3169 | 61.1783 | 55.6587 | 55.9256 | 65.0422 | 62.3517 | 61.1512 | 60.6367 | 123.1247 | 61.6485 | 123.0376 | 61.3484 | 61.4206 | 122.9111 | 61.3847 | 122.6938 | 61.7041 | 61.74 | 61.617 | 61.6529
4819.0625 | 123.381 | -61.4319 | 61.7065 | -0.27647 | -5.9564 | -5.6025 | 4.7504 | 0.99764 | -0.299 | -0.77233 | 61.7431 | 0.28526 | 61.6698 | -0.028522 | 0.043657 | 61.5341 | 0.012299 | 61.326 | 61.1554 | 55.4755 | 55.8294 | 66.1822 | 62.4295 | 61.1329 | 60.6596 | 123.175 | 61.7171 | 123.1017 | 61.4034 | 61.4755 | 122.966 | 61.4442 | 122.7579 | 61.6995 | 61.7308 | 61.6261 | 61.6575
4820.0938 | 123.436 | -61.4182 | 61.6882 | -0.19406 | -5.8419 | -5.3323 | 4.0041 | 1.1716 | -0.21659 | -0.62583 | 61.7523 | 0.27611 | 61.6881 | -0.03768 | 0.043657 | 61.5341 | 0.012299 | 61.3215 | 61.2241 | 55.5763 | 56.0858 | 65.4222 | 62.5898 | 61.2016 | 60.7923 | 123.1704 | 61.6943 | 123.1063 | 61.3805 | 61.4618 | 122.9523 | 61.4305 | 122.7396 | 61.7086 | 61.74 | 61.6445 | 61.6758
4821.0625 | 123.3673 | -61.3998 | 61.7157 | -0.24442 | -5.9243 | -5.4651 | 4.4024 | 1.1121 | -0.27153 | -0.62125 | 61.7477 | 0.28069 | 61.679 | -0.033101 | 0.048236 | 61.5295 | 0.012299 | 61.3306 | 61.1554 | 55.4755 | 55.9347 | 65.8022 | 62.5119 | 61.1283 | 60.7786 | 123.1476 | 61.6805 | 123.0788 | 61.3667 | 61.4481 | 122.9294 | 61.4121 | 122.7305 | 61.6995 | 61.7354 | 61.6307 | 61.6667
4822.0938 | 123.4039 | -61.3861 | 61.6974 | -0.20779 | -5.8785 | -5.4972 | 3.798 | 1.167 | -0.22117 | -0.58463 | 61.7477 | 0.28069 | 61.6515 | -0.033101 | 0.048236 | 61.5341 | 0.012299 | 61.3215 | 61.1783 | 55.5076 | 55.8889 | 65.1841 | 62.5531 | 61.1649 | 60.8015 | 123.1338 | 61.6668 | 123.0376 | 61.353 | 61.4343 | 122.9202 | 61.3984 | 122.7076 | 61.6995 | 61.7354 | 61.6032 | 61.6392
4823.0625 | 123.2574 | -61.4365 | 61.7386 | -0.17117 | -5.7915 | -5.4193 | 3.9262 | 1.2769 | -0.1937 | -0.53427 | 61.7431 | 0.27153 | 61.6515 | -0.03768 | 0.039079 | 61.5387 | 0.012299 | 61.3352 | 61.2653 | 55.6449 | 56.0171 | 65.3627 | 62.7134 | 61.2428 | 60.9022 | 123.1796 | 61.708 | 123.0879 | 61.3988 | 61.4755 | 122.9752 | 61.4488 | 122.7717 | 61.7041 | 61.7308 | 61.6124 | 61.6392
4824.0938 | 123.3627 | -61.4365 | 61.6928 | -0.249 | -5.8785 | -5.4834 | 4.4482 | 1.1579 | -0.28069 | -0.53885 | 61.7431 | 0.28069 | 61.6835 | -0.028522 | 0.048236 | 61.5433 | 0.016878 | 61.3077 | 61.1875 | 55.5579 | 55.953 | 65.8846 | 62.5943 | 61.1558 | 60.8976 | 123.1796 | 61.7171 | 123.12 | 61.4079 | 61.4847 | 122.9797 | 61.4533 | 122.7442 | 61.6949 | 61.7263 | 61.6353 | 61.6667
4825.0625 | 123.3215 | -61.4365 | 61.7569 | -0.3131 | -5.9518 | -5.575 | 4.4436 | 1.1121 | -0.33563 | -0.52511 | 61.7431 | 0.28069 | 61.6881 | -0.023943 | 0.052814 | 61.5387 | 0.007721 | 61.3306 | 61.1234 | 55.4847 | 55.8615 | 65.8801 | 62.5485 | 61.1008 | 60.9113 | 123.1796 | 61.7171 | 123.1246 | 61.4125 | 61.4893 | 122.9752 | 61.4442 | 122.7671 | 61.6903 | 61.7354 | 61.6353 | 61.6804
4826.1094 | 123.3902 | -61.4136 | 61.7111 | -0.28563 | -5.9243 | -5.5017 | 4.5535 | 1.1258 | -0.31732 | -0.38319 | 61.7431 | 0.27611 | 61.6469 | -0.03768 | 0.052814 | 61.5387 | 0.003143 | 61.3215 | 61.1279 | 55.4893 | 55.9118 | 65.9671 | 62.5394 | 61.0963 | 61.0304 | 123.1567 | 61.6897 | 123.0605 | 61.3759 | 61.4664 | 122.9523 | 61.4167 | 122.735 | 61.6903 | 61.74 | 61.5941 | 61.6438
4827.0625 | 123.2483 | -61.4365 | 61.6882 | -0.23069 | -5.9335 | -5.4285 | 4.6863 | 1.2311 | -0.27611 | -0.39235 | 61.7386 | 0.27153 | 61.6423 | -0.033101 | 0.039079 | 61.5433 | 0.007721 | 61.326 | 61.2058 | 55.503 | 56.008 | 66.1227 | 62.6676 | 61.1604 | 61.0441 | 123.175 | 61.708 | 123.0788 | 61.4034 | 61.4755 | 122.9797 | 61.4442 | 122.7625 | 61.6995 | 61.7308 | 61.6032 | 61.6346
4828.0938 | 123.2803 | -61.4319 | 61.7386 | -0.22611 | -5.9564 | -5.3278 | 4.3978 | 1.167 | -0.24864 | -0.52053 | 61.7523 | 0.27611 | 61.6698 | -0.03768 | 0.052814 | 61.5387 | 0.016878 | 61.326 | 61.2058 | 55.4755 | 56.1041 | 65.8297 | 62.5989 | 61.1832 | 60.9113 | 123.1842 | 61.708 | 123.1017 | 61.3942 | 61.4847 | 122.9706 | 61.4488 | 122.7579 | 61.6995 | 61.7354 | 61.617 | 61.6529
4829.0625 | 123.3124 | -61.4273 | 61.7294 | -0.17117 | -6.0067 | -5.4148 | 4.1826 | 1.2311 | -0.20743 | -0.55258 | 61.7477 | 0.28526 | 61.6881 | -0.033101 | 0.048236 | 61.5387 | 0.007721 | 61.3352 | 61.2561 | 55.4206 | 56.0126 | 65.6099 | 62.6584 | 61.2199 | 60.8747 | 123.175 | 61.7126 | 123.1154 | 61.3942 | 61.4755 | 122.966 | 61.435 | 122.7625 | 61.6995 | 61.74 | 61.6399 | 61.6804
4830.0781 | 123.3536 | -61.4227 | 61.7065 | -0.14827 | -6.0891 | -5.3278 | 4.1139 | 1.3181 | -0.16623 | -0.60294 | 61.7431 | 0.28526 | 61.6606 | -0.033101 | 0.052814 | 61.5387 | 0.007721 | 61.3306 | 61.2745 | 55.3336 | 56.095 | 65.5367 | 62.7408 | 61.2565 | 60.8198 | 123.1659 | 61.708 | 123.0834 | 61.3896 | 61.4755 | 122.9614 | 61.4304 | 122.7533 | 61.6903 | 61.7354 | 61.6078 | 61.6529
4831.0625 | 123.2574 | -61.4502 | 61.7203 | -0.15285 | -6.0205 | -5.4834 | 3.9537 | 1.1808 | -0.17081 | -0.6533 | 61.7431 | 0.28526 | 61.6561 | -0.028522 | 0.039079 | 61.5387 | 0.003143 | 61.326 | 61.2973 | 55.4297 | 55.9668 | 65.4039 | 62.6309 | 61.2794 | 60.7969 | 123.1933 | 61.7355 | 123.1063 | 61.4217 | 61.4893 | 122.9889 | 61.4533 | 122.7762 | 61.7041 | 61.74 | 61.617 | 61.6529
4832.0781 | 123.3078 | -61.409 | 61.7294 | -0.15743 | -6.1395 | -5.4422 | 4.3887 | 1.1899 | -0.17996 | -0.96004 | 61.7431 | 0.28069 | 61.6652 | -0.023943 | 0.052814 | 61.5341 | 0.012299 | 61.3215 | 61.2516 | 55.2695 | 55.9668 | 65.7976 | 62.5989 | 61.229 | 60.449 | 123.1521 | 61.6897 | 123.0742 | 61.3851 | 61.4618 | 122.9431 | 61.4213 | 122.7305 | 61.6903 | 61.7308 | 61.6124 | 61.6529
4833.0625 | 123.2803 | -61.4319 | 61.7706 | -0.065863 | -6.1075 | -5.3598 | 4.2971 | 1.3685 | -0.097553 | -0.99667 | 61.7477 | 0.28069 | 61.6881 | -0.028522 | 0.048236 | 61.5341 | 0.007721 | 61.3215 | 61.366 | 55.3244 | 56.0721 | 65.729 | 62.8003 | 61.3343 | 60.4352 | 123.1796 | 61.7126 | 123.12 | 61.4034 | 61.4801 | 122.966 | 61.4396 | 122.7533 | 61.6995 | 61.74 | 61.6399 | 61.6804
4834.0781 | 123.349 | -61.4227 | 61.6974 | -0.1208 | -6.0205 | -5.3644 | 3.3631 | 1.1167 | -0.14334 | -1.1065 | 61.7523 | 0.28069 | 61.6927 | -0.03768 | 0.048236 | 61.5341 | 0.003143 | 61.2986 | 61.3019 | 55.4023 | 56.0583 | 64.7858 | 62.5394 | 61.2794 | 60.3162 | 123.175 | 61.7034 | 123.1154 | 61.385 | 61.471 | 122.9568 | 61.4259 | 122.7213 | 61.7041 | 61.7491 | 61.6445 | 61.6895
4835.0625 | 123.3856 | -61.3861 | 61.6974 | -0.07502 | -5.819 | -5.2774 | 3.0105 | 1.3181 | -0.10213 | -1.047 | 61.7431 | 0.27153 | 61.6515 | -0.028522 | 0.052814 | 61.525 | 0.007721 | 61.3215 | 61.3111 | 55.5671 | 56.1087 | 64.3966 | 62.7042 | 61.284 | 60.3391 | 123.1292 | 61.6576 | 123.0376 | 61.3576 | 61.4389 | 122.9111 | 61.3938 | 122.7076 | 61.6903 | 61.7354 | 61.5987 | 61.6438
4836.1094 | 123.3582 | -61.3953 | 61.702 | -0.084176 | -5.8465 | -5.4285 | 1.93 | 1.2677 | -0.10213 | -1.221 | 61.7569 | 0.28526 | 61.6698 | -0.028522 | 0.043657 | 61.5112 | 0.007721 | 61.2986 | 61.3111 | 55.5488 | 55.9668 | 63.3253 | 62.663 | 61.2931 | 60.1743 | 123.1521 | 61.6805 | 123.0651 | 61.3667 | 61.4389 | 122.9065 | 61.403 | 122.6938 | 61.7132 | 61.7491 | 61.6261 | 61.6621
4837.0625 | 123.2895 | -61.3907 | 61.7615 | -0.006344 | -5.732 | -5.3919 | 1.8522 | 1.3959 | -0.038034 | -1.6147 | 61.766 | 0.27611 | 61.7018 | -0.033101 | 0.048236 | 61.5158 | 0.007721 | 61.3123 | 61.3843 | 55.6587 | 55.9988 | 63.2429 | 62.7866 | 61.3527 | 59.776 | 123.1567 | 61.6668 | 123.0925 | 61.3576 | 61.4389 | 122.9065 | 61.3984 | 122.703 | 61.7178 | 61.7583 | 61.6536 | 61.6941
4838.0938 | 123.2849 | -61.4365 | 61.7615 | -0.10249 | -5.8785 | -5.6849 | 3.1937 | 1.3135 | -0.1296 | -1.6697 | 61.7706 | 0.27611 | 61.6973 | -0.028522 | 0.048236 | 61.5204 | 0.012299 | 61.3077 | 61.334 | 55.5579 | 55.7516 | 64.6301 | 62.75 | 61.3069 | 59.7668 | 123.2071 | 61.7126 | 123.1337 | 61.4079 | 61.4847 | 122.9568 | 61.4488 | 122.7442 | 61.7224 | 61.7583 | 61.649 | 61.685
4839.0625 | 123.3032 | -61.4044 | 61.7569 | -0.16201 | -5.764 | -5.6895 | 3.4455 | 1.254 | -0.18912 | -1.601 | 61.7523 | 0.27611 | 61.6652 | -0.028522 | 0.052814 | 61.5204 | 0.012299 | 61.3169 | 61.2424 | 55.6404 | 55.715 | 64.8499 | 62.6584 | 61.2153 | 59.8034 | 123.1567 | 61.6805 | 123.0696 | 61.3759 | 61.4572 | 122.9248 | 61.4167 | 122.7213 | 61.6995 | 61.74 | 61.6124 | 61.6529
4840.0938 | 123.3582 | -61.4456 | 61.7203 | -0.17117 | -5.677 | -5.4285 | 4.0636 | 1.1899 | -0.19828 | -1.4865 | 61.7431 | 0.27611 | 61.6561 | -0.028522 | 0.039079 | 61.5387 | 0.007721 | 61.3169 | 61.2745 | 55.7686 | 56.0171 | 65.5092 | 62.6355 | 61.2473 | 59.9591 | 123.1887 | 61.7217 | 123.1017 | 61.4171 | 61.4847 | 122.9843 | 61.4533 | 122.7625 | 61.7041 | 61.7354 | 61.617 | 61.6483
4841.0625 | 123.3261 | -61.4227 | 61.7569 | -0.047549 | -5.4893 | -5.2866 | 3.4592 | 1.4325 | -0.079239 | -0.91426 | 61.7386 | 0.27153 | 61.679 | -0.028522 | 0.048236 | 61.5387 | 0.012299 | 61.3215 | 61.3752 | 55.9334 | 56.1362 | 64.8819 | 62.8553 | 61.3435 | 60.5085 | 123.1613 | 61.6943 | 123.1017 | 61.3942 | 61.471 | 122.9614 | 61.435 | 122.7442 | 61.6903 | 61.7263 | 61.6307 | 61.6667
4842.0781 | 123.3856 | -61.3907 | 61.6974 | -0.042971 | -5.5443 | -5.4102 | 3.4958 | 1.6111 | -0.074661 | -0.81812 | 61.7431 | 0.28526 | 61.679 | -0.03768 | 0.048236 | 61.5478 | 0.012299 | 61.3169 | 61.3477 | 55.8464 | 55.9805 | 64.8865 | 63.0018 | 61.316 | 60.5726 | 123.1338 | 61.676 | 123.0696 | 61.353 | 61.4389 | 122.9385 | 61.403 | 122.7076 | 61.6949 | 61.7308 | 61.6307 | 61.6667
4843.0625 | 123.2529 | -61.4548 | 61.7386 | -0.097912 | -5.9243 | -5.5109 | 4.6405 | 1.84 | -0.12502 | -0.93715 | 61.734 | 0.28069 | 61.6561 | -0.028522 | 0.043657 | 61.5433 | 0.016878 | 61.3398 | 61.3569 | 55.5305 | 55.9439 | 66.0952 | 63.2948 | 61.3298 | 60.5176 | 123.1887 | 61.7355 | 123.1108 | 61.4263 | 61.4984 | 122.998 | 61.4717 | 122.7945 | 61.6903 | 61.7171 | 61.6124 | 61.6392
4844.0625 | 123.2758 | -61.4182 | 61.7615 | -0.097912 | -6.0388 | -5.5384 | 4.6405 | 1.9224 | -0.12502 | -0.84559 | 61.7386 | 0.27153 | 61.6423 | -0.03768 | 0.043657 | 61.5524 | 0.007721 | 61.326 | 61.3202 | 55.3794 | 55.8798 | 66.0586 | 63.3405 | 61.2931 | 60.5726 | 123.1567 | 61.6897 | 123.0605 | 61.3805 | 61.4618 | 122.9706 | 61.4259 | 122.7442 | 61.6949 | 61.7308 | 61.5987 | 61.6346
4845.0938 | 123.4085 | -61.3907 | 61.6837 | -0.11165 | -6.0708 | -5.4514 | 4.9289 | 2.0643 | -0.1296 | -0.85474 | 61.7386 | 0.28069 | 61.6515 | -0.033101 | 0.043657 | 61.5433 | 0.007721 | 61.3398 | 61.279 | 55.3199 | 55.9393 | 66.3196 | 63.455 | 61.2611 | 60.5359 | 123.1292 | 61.6714 | 123.0422 | 61.3576 | 61.4343 | 122.934 | 61.3984 | 122.7305 | 61.6949 | 61.7308 | 61.6078 | 61.6438
4846.0625 | 123.4314 | -61.409 | 61.6562 | -0.029236 | -5.9335 | -5.2545 | 4.6176 | 2.1101 | -0.056347 | -0.92341 | 61.7431 | 0.27611 | 61.6744 | -0.042259 | 0.039079 | 61.5433 | 0.007721 | 61.3306 | 61.3798 | 55.4755 | 56.1545 | 66.0266 | 63.5191 | 61.3526 | 60.4856 | 123.1521 | 61.6851 | 123.0834 | 61.3667 | 61.4481 | 122.9523 | 61.4167 | 122.7396 | 61.7041 | 61.7354 | 61.6353 | 61.6667
4847.0781 | 123.4222 | -61.4182 | 61.702 | -0.097912 | -6.1532 | -5.314 | 4.0636 | 1.9773 | -0.13418 | -0.99209 | 61.734 | 0.28069 | 61.6835 | -0.033101 | 0.052814 | 61.5433 | 0.007721 | 61.326 | 61.3202 | 55.2649 | 56.1041 | 65.4817 | 63.3955 | 61.284 | 60.4261 | 123.1521 | 61.6988 | 123.1017 | 61.3851 | 61.471 | 122.9614 | 61.4259 | 122.7442 | 61.6812 | 61.7263 | 61.6307 | 61.6758
4848.0625 | 123.3124 | -61.4182 | 61.7294 | -0.15285 | -6.2814 | -5.2133 | 4.4299 | 1.8537 | -0.17539 | -1.0928 | 61.7386 | 0.28526 | 61.6515 | -0.028522 | 0.043657 | 61.5387 | 0.012299 | 61.326 | 61.2653 | 55.1367 | 56.2049 | 65.848 | 63.2719 | 61.2428 | 60.3253 | 123.1567 | 61.7034 | 123.0696 | 61.3896 | 61.4618 | 122.9568 | 61.4305 | 122.7442 | 61.6949 | 61.7263 | 61.6078 | 61.6392
4849.0625 | 123.3994 | -61.3861 | 61.734 | -0.19864 | -6.3318 | -5.4926 | 4.5672 | 1.7896 | -0.22575 | -1.1065 | 61.7431 | 0.27611 | 61.6561 | -0.033101 | 0.043657 | 61.5341 | 0.012299 | 61.3352 | 61.1875 | 55.0543 | 55.8935 | 65.9533 | 63.1757 | 61.1604 | 60.2796 | 123.1292 | 61.6622 | 123.0422 | 61.353 | 61.4298 | 122.9202 | 61.3984 | 122.7213 | 61.6995 | 61.7308 | 61.6124 | 61.6438
4850.0781 | 123.4314 | -61.3953 | 61.7203 | -0.21237 | -6.341 | -5.5384 | 4.5123 | 1.6935 | -0.24406 | -1.2118 | 61.7477 | 0.28526 | 61.6927 | -0.033101 | 0.039079 | 61.5387 | 0.007721 | 61.326 | 61.1829 | 55.0543 | 55.8569 | 65.9075 | 63.0887 | 61.1512 | 60.1834 | 123.143 | 61.6805 | 123.088 | 61.3622 | 61.4343 | 122.934 | 61.403 | 122.7213 | 61.7086 | 61.74 | 61.6536 | 61.685
4851.0625 | 123.4543 | -61.3541 | 61.7981 | -0.14827 | -6.2723 | -5.4102 | 3.2807 | 1.7622 | -0.16623 | -1.3721 | 61.7569 | 0.28526 | 61.6927 | -0.033101 | 0.048236 | 61.525 | 0.007721 | 61.326 | 61.2058 | 55.0818 | 55.9439 | 64.6347 | 63.1162 | 61.1878 | 59.982 | 123.1109 | 61.6393 | 123.0468 | 61.321 | 61.4023 | 122.879 | 61.3618 | 122.6801 | 61.7086 | 61.7491 | 61.6445 | 61.685
4852.0938 | 123.3032 | -61.3907 | 61.7523 | -0.10707 | -6.1853 | -5.456 | 2.7541 | 1.7255 | -0.13876 | -1.4041 | 61.7614 | 0.27611 | 61.6652 | -0.028522 | 0.048236 | 61.5204 | 0.003143 | 61.326 | 61.2836 | 55.2054 | 55.9347 | 64.1448 | 63.1162 | 61.2519 | 59.9866 | 123.1521 | 61.6668 | 123.0559 | 61.3622 | 61.4389 | 122.9111 | 61.3938 | 122.7167 | 61.7132 | 61.7583 | 61.617 | 61.6621
4853.0625 | 123.3307 | -61.3998 | 61.7432 | -0.21695 | -6.3547 | -5.5842 | 3.6927 | 1.6065 | -0.23948 | -1.427 | 61.7614 | 0.28069 | 61.6652 | -0.033101 | 0.043657 | 61.5204 | 0.003143 | 61.326 | 61.1829 | 55.0451 | 55.8157 | 65.0926 | 63.0063 | 61.1604 | 59.9728 | 123.1613 | 61.6805 | 123.0651 | 61.3667 | 61.4435 | 122.9202 | 61.403 | 122.7259 | 61.7178 | 61.7583 | 61.6216 | 61.6621
4854.0781 | 123.3673 | -61.4182 | 61.6974 | -0.13912 | -6.286 | -5.6345 | 3.9583 | 1.927 | -0.15707 | -1.5003 | 61.7569 | 0.28069 | 61.6881 | -0.03768 | 0.052814 | 61.5341 | 0.007721 | 61.3169 | 61.279 | 55.1321 | 55.7836 | 65.3764 | 63.3451 | 61.2611 | 59.9179 | 123.175 | 61.6988 | 123.1063 | 61.3805 | 61.471 | 122.9523 | 61.4259 | 122.735 | 61.7041 | 61.7491 | 61.6353 | 61.6804
4855.0625 | 123.2986 | -61.409 | 61.7615 | -0.15285 | -6.3089 | -5.662 | 4.1094 | 2.0826 | -0.17996 | -1.2897 | 61.7523 | 0.28069 | 61.6881 | -0.023943 | 0.052814 | 61.5341 | 0.007721 | 61.3352 | 61.2561 | 55.1001 | 55.747 | 65.5184 | 63.4916 | 61.229 | 60.1193 | 123.1613 | 61.6897 | 123.0971 | 61.3851 | 61.4618 | 122.9431 | 61.4167 | 122.7442 | 61.6995 | 61.7446 | 61.6353 | 61.6804
4856.1094 | 123.3948 | -61.4548 | 61.6745 | 0.002813 | -6.199 | -5.3232 | 4.6954 | 2.2749 | -0.024298 | -0.88221 | 61.734 | 0.28069 | 61.6469 | -0.033101 | 0.048236 | 61.5433 | 0.007721 | 61.3443 | 61.4576 | 55.2557 | 56.1316 | 66.1502 | 63.7297 | 61.4305 | 60.5726 | 123.1887 | 61.7355 | 123.1017 | 61.4217 | 61.503 | 122.998 | 61.4625 | 122.7991 | 61.6857 | 61.7263 | 61.5987 | 61.6392
4857.0625 | 123.317 | -61.441 | 61.7249 | 0.062332 | -6.1441 | -4.8653 | 4.6222 | 1.9727 | 0.012329 | -0.80896 | 61.734 | 0.27611 | 61.6332 | -0.028522 | 0.043657 | 61.5478 | 0.007721 | 61.3443 | 61.5034 | 55.297 | 56.5757 | 66.0632 | 63.4138 | 61.4534 | 60.6321 | 123.175 | 61.7171 | 123.0742 | 61.4125 | 61.4847 | 122.9889 | 61.4488 | 122.7854 | 61.6903 | 61.7263 | 61.5895 | 61.6255
4858.0781 | 123.3902 | -61.409 | 61.6745 | 0.021127 | -6.167 | -4.4441 | 4.5031 | 1.9911 | -0.010563 | -0.89594 | 61.734 | 0.28069 | 61.6606 | -0.028522 | 0.048236 | 61.5524 | -0.001436 | 61.3398 | 61.4301 | 55.242 | 56.9649 | 65.9121 | 63.4001 | 61.3984 | 60.5131 | 123.143 | 61.6897 | 123.0696 | 61.3805 | 61.4572 | 122.9614 | 61.4076 | 122.7488 | 61.6857 | 61.7354 | 61.6124 | 61.6621
4859.0625 | 123.349 | -61.4365 | 61.7157 | 0.10812 | -6.1532 | -4.7234 | 4.9198 | 2.2566 | 0.076426 | -0.85932 | 61.7294 | 0.28526 | 61.6652 | -0.028522 | 0.043657 | 61.557 | 0.003143 | 61.3535 | 61.5446 | 55.2832 | 56.7131 | 66.3562 | 63.693 | 61.5129 | 60.5771 | 123.1659 | 61.7217 | 123.1017 | 61.4079 | 61.4801 | 122.9935 | 61.4396 | 122.79 | 61.6857 | 61.7263 | 61.6216 | 61.6621
4860.0781 | 123.4222 | -61.4319 | 61.6882 | 0.2592 | -5.9518 | -4.5448 | 4.4619 | 2.4397 | 0.23209 | -0.85932 | 61.7202 | 0.27611 | 61.6377 | -0.03768 | 0.052814 | 61.557 | 0.007721 | 61.3535 | 61.6911 | 55.4801 | 56.8871 | 65.8938 | 63.8716 | 61.664 | 60.5726 | 123.1521 | 61.708 | 123.0696 | 61.3942 | 61.4847 | 122.9889 | 61.4396 | 122.7854 | 61.6674 | 61.7125 | 61.5849 | 61.63
4861.0625 | 123.3536 | -61.441 | 61.6882 | 0.14017 | -5.9884 | -5.227 | 5.0342 | 2.3436 | 0.1039 | -0.82269 | 61.7202 | 0.28069 | 61.6286 | -0.033101 | 0.039079 | 61.557 | 0.003143 | 61.3489 | 61.5812 | 55.4526 | 56.214 | 66.4753 | 63.7846 | 61.5449 | 60.6183 | 123.1613 | 61.7217 | 123.0696 | 61.4079 | 61.4801 | 122.998 | 61.4442 | 122.79 | 61.6812 | 61.7171 | 61.5895 | 61.6255
4862.0781 | 123.4314 | -61.4182 | 61.6699 | 0.19968 | -5.8739 | -5.4193 | 5.0022 | 2.339 | 0.15884 | -0.68535 | 61.7157 | 0.27153 | 61.6515 | -0.033101 | 0.039079 | 61.557 | 0.007721 | 61.3489 | 61.6178 | 55.5442 | 55.9988 | 66.4203 | 63.7571 | 61.577 | 60.7328 | 123.1338 | 61.6897 | 123.0696 | 61.3851 | 61.4572 | 122.9752 | 61.4259 | 122.7671 | 61.6766 | 61.7079 | 61.6124 | 61.6438
4863.0625 | 123.2849 | -61.4319 | 61.7432 | 0.17221 | -5.993 | -5.4926 | 4.9427 | 2.2245 | 0.13137 | -0.91884 | 61.734 | 0.28069 | 61.6744 | -0.028522 | 0.048236 | 61.5478 | 0.007721 | 61.3398 | 61.6041 | 55.4389 | 55.9393 | 66.3745 | 63.6564 | 61.5633 | 60.513 | 123.1659 | 61.7126 | 123.1063 | 61.4034 | 61.4801 | 122.9797 | 61.4396 | 122.7717 | 61.6857 | 61.7263 | 61.6261 | 61.6667
4864.0781 | 123.3261 | -61.4365 | 61.6699 | 0.071489 | -6.1945 | -5.4605 | 3.5462 | 2.1009 | 0.030642 | -1.1752 | 61.7523 | 0.28069 | 61.6698 | -0.033101 | 0.043657 | 61.5341 | 0.003143 | 61.3215 | 61.508 | 55.242 | 55.9759 | 64.9827 | 63.5374 | 61.4671 | 60.2612 | 123.1888 | 61.7171 | 123.1063 | 61.4034 | 61.4801 | 122.9706 | 61.4396 | 122.7579 | 61.7086 | 61.7491 | 61.6261 | 61.6667
4865.0625 | 123.3627 | -61.4227 | 61.7386 | 0.29583 | -5.8556 | -5.0622 | 3.1982 | 2.3481 | 0.25498 | -0.85016 | 61.734 | 0.28526 | 61.6332 | -0.033101 | 0.052814 | 61.5524 | 0.007721 | 61.3398 | 61.7186 | 55.5671 | 56.3605 | 64.621 | 63.7709 | 61.6777 | 60.5726 | 123.1567 | 61.708 | 123.0559 | 61.3896 | 61.4755 | 122.9752 | 61.4304 | 122.7625 | 61.6812 | 61.7263 | 61.5804 | 61.6255
4866.0938 | 123.3856 | -61.4365 | 61.6653 | 0.35993 | -5.7732 | -4.412 | 3.3402 | 2.3069 | 0.3145 | -0.80438 | 61.7248 | 0.28069 | 61.6469 | -0.033101 | 0.043657 | 61.557 | 0.003143 | 61.3398 | 61.7964 | 55.6633 | 57.0244 | 64.7766 | 63.7434 | 61.751 | 60.6321 | 123.1613 | 61.7171 | 123.0834 | 61.4034 | 61.4801 | 122.9935 | 61.4396 | 122.7762 | 61.6812 | 61.7217 | 61.6032 | 61.6438
4867.0625 | 123.3353 | -61.4548 | 61.7386 | 0.35993 | -5.8373 | -4.76 | 3.6103 | 2.3024 | 0.32366 | -0.6533 | 61.734 | 0.27611 | 61.6652 | -0.033101 | 0.052814 | 61.5524 | 0.007721 | 61.3535 | 61.8147 | 55.6175 | 56.6948 | 65.0651 | 63.7571 | 61.7784 | 60.8015 | 123.1887 | 61.7309 | 123.12 | 61.4217 | 61.5076 | 123.0072 | 61.4625 | 122.8083 | 61.6812 | 61.7263 | 61.6124 | 61.6575
4868.0938 | 123.4222 | -61.4365 | 61.6882 | 0.29125 | -5.8831 | -4.2884 | 3.8942 | 2.1559 | 0.25498 | -0.67161 | 61.7248 | 0.28069 | 61.6652 | -0.033101 | 0.052814 | 61.557 | 0.003143 | 61.3627 | 61.7277 | 55.5534 | 57.148 | 65.3306 | 63.5923 | 61.6914 | 60.7648 | 123.1613 | 61.7171 | 123.1017 | 61.4034 | 61.4893 | 122.9935 | 61.4396 | 122.7991 | 61.672 | 61.7217 | 61.6124 | 61.6621
4869.0625 | 123.2712 | -61.4502 | 61.7386 | 0.34619 | -5.9838 | -4.1373 | 4.0132 | 2.1604 | 0.30992 | -0.81812 | 61.7202 | 0.28069 | 61.624 | -0.033101 | 0.052814 | 61.5662 | 0.016878 | 61.3581 | 61.7964 | 55.4664 | 57.3129 | 65.4634 | 63.6106 | 61.7601 | 60.6321 | 123.1704 | 61.7309 | 123.0742 | 61.4171 | 61.503 | 123.0164 | 61.4671 | 122.8083 | 61.6674 | 61.7034 | 61.5712 | 61.6071
4870.0938 | 123.4451 | -61.3998 | 61.6882 | 0.31414 | -6.0846 | -5.2041 | 3.4089 | 2.2062 | 0.27787 | -1.0699 | 61.734 | 0.28069 | 61.6606 | -0.028522 | 0.043657 | 61.5478 | 0.007721 | 61.3306 | 61.714 | 55.3153 | 56.1957 | 64.8087 | 63.6061 | 61.6777 | 60.3299 | 123.1338 | 61.6805 | 123.0605 | 61.3713 | 61.4435 | 122.9477 | 61.4076 | 122.7305 | 61.6903 | 61.7263 | 61.617 | 61.6529
4871.0625 | 123.262 | -61.4685 | 61.6837 | 0.218 | -6.1441 | -5.401 | 4.7595 | 2.3298 | 0.19089 | -1.2897 | 61.7294 | 0.28069 | 61.6698 | -0.028522 | 0.048236 | 61.5524 | 0.012299 | 61.3352 | 61.6865 | 55.3244 | 56.0675 | 66.228 | 63.7983 | 61.6594 | 60.1788 | 123.1979 | 61.7492 | 123.1383 | 61.44 | 61.5167 | 123.0209 | 61.4808 | 122.8037 | 61.6812 | 61.7171 | 61.6216 | 61.6575
4872.0625 | 123.2986 | -61.4548 | 61.7294 | 0.17221 | -6.1761 | -5.401 | 4.7229 | 2.2016 | 0.14052 | -1.3492 | 61.734 | 0.28526 | 61.6698 | -0.033101 | 0.052814 | 61.5524 | 0.007721 | 61.3352 | 61.627 | 55.2786 | 56.0538 | 66.1777 | 63.6564 | 61.5953 | 60.1056 | 123.1887 | 61.74 | 123.1246 | 61.4217 | 61.5076 | 123.0072 | 61.4625 | 122.79 | 61.6812 | 61.7263 | 61.617 | 61.6621
4873.0938 | 123.3994 | -61.4273 | 61.7203 | 0.19511 | -6.0525 | -5.2637 | 4.6359 | 2.3848 | 0.15426 | -1.2897 | 61.7294 | 0.28069 | 61.6332 | -0.03768 | 0.048236 | 61.5524 | 0.012299 | 61.3443 | 61.6224 | 55.3748 | 56.1636 | 66.0632 | 63.8121 | 61.5816 | 60.1376 | 123.1567 | 61.708 | 123.0605 | 61.3896 | 61.4755 | 122.9797 | 61.4396 | 122.7717 | 61.6812 | 61.7171 | 61.5849 | 61.6209
4874.0625 | 123.3078 | -61.4594 | 61.6837 | 0.24089 | -6.0525 | -5.2682 | 4.9655 | 2.6503 | 0.20462 | -1.1752 | 61.7294 | 0.28526 | 61.6606 | -0.033101 | 0.043657 | 61.557 | 0.003143 | 61.3443 | 61.7002 | 55.4068 | 56.1911 | 66.4249 | 64.1096 | 61.664 | 60.2841 | 123.1887 | 61.7446 | 123.12 | 61.4262 | 61.503 | 123.0164 | 61.4625 | 122.8037 | 61.6857 | 61.7263 | 61.617 | 61.6575
4875.0781 | 123.3902 | -61.4182 | 61.6699 | 0.19968 | -6.0525 | -5.14 | 5.0434 | 2.6503 | 0.16799 | -1.2942 | 61.7248 | 0.28526 | 61.6561 | -0.028522 | 0.048236 | 61.557 | 0.003143 | 61.3398 | 61.6178 | 55.3656 | 56.2781 | 66.4615 | 64.0684 | 61.5861 | 60.1239 | 123.143 | 61.7034 | 123.0742 | 61.3896 | 61.4664 | 122.9752 | 61.4213 | 122.7579 | 61.6766 | 61.7217 | 61.6078 | 61.6529
4876.0625 | 123.3627 | -61.4365 | 61.647 | 0.218 | -5.8373 | -5.2408 | 4.9152 | 2.7189 | 0.18631 | -1.047 | 61.7111 | 0.28069 | 61.624 | -0.033101 | 0.048236 | 61.5707 | 0.012299 | 61.3398 | 61.6545 | 55.5992 | 56.1957 | 66.3516 | 64.1554 | 61.6228 | 60.3894 | 123.1475 | 61.7171 | 123.0605 | 61.4034 | 61.4847 | 123.0072 | 61.4488 | 122.7762 | 61.6628 | 61.6988 | 61.5758 | 61.6117
4877.0781 | 123.4131 | -61.4456 | 61.6837 | 0.33246 | -5.7503 | -5.0256 | 3.94 | 2.7785 | 0.29161 | -1.0562 | 61.7294 | 0.28526 | 61.6652 | -0.028522 | 0.052814 | 61.5616 | 0.007721 | 61.3352 | 61.7781 | 55.6953 | 56.42 | 65.3856 | 64.2241 | 61.7372 | 60.3894 | 123.175 | 61.7309 | 123.1108 | 61.4171 | 61.4984 | 123.0072 | 61.4533 | 122.7808 | 61.6766 | 61.7217 | 61.6124 | 61.6575
4878.0625 | 123.3719 | -61.4548 | 61.6241 | 0.47439 | -5.4893 | -3.8947 | 4.9747 | 3.0989 | 0.43812 | -1.047 | 61.6928 | 0.27611 | 61.6194 | -0.028522 | 0.048236 | 61.5799 | 0.007721 | 61.3581 | 61.9292 | 55.9655 | 57.5601 | 66.4295 | 64.5537 | 61.8929 | 60.4077 | 123.1475 | 61.7309 | 123.0742 | 61.4263 | 61.503 | 123.0347 | 61.4625 | 122.8129 | 61.6445 | 61.685 | 61.5712 | 61.6117
4879.0781 | 123.381 | -61.4456 | 61.6653 | 0.35535 | -6.0525 | -4.9019 | 5.0983 | 2.9799 | 0.31908 | -1.0196 | 61.7111 | 0.28069 | 61.6194 | -0.028522 | 0.052814 | 61.5707 | 0.007721 | 61.3535 | 61.801 | 55.3931 | 56.5437 | 66.5439 | 64.4255 | 61.7647 | 60.4261 | 123.1567 | 61.7263 | 123.0651 | 61.4171 | 61.4984 | 123.0164 | 61.4533 | 122.7991 | 61.6583 | 61.7034 | 61.5666 | 61.6117
4880.0625 | 123.3307 | -61.4594 | 61.7065 | 0.38282 | -6.1258 | -4.8974 | 5.2448 | 3.0257 | 0.35113 | -0.98293 | 61.7157 | 0.28069 | 61.6561 | -0.028522 | 0.039079 | 61.5707 | -0.001436 | 61.3718 | 61.8422 | 55.3336 | 56.562 | 66.7042 | 64.485 | 61.8105 | 60.4764 | 123.175 | 61.74 | 123.1154 | 61.4308 | 61.4984 | 123.0301 | 61.4579 | 122.8312 | 61.6766 | 61.7171 | 61.617 | 61.6575
4881.0938 | 123.317 | -61.4639 | 61.6699 | 0.40113 | -5.938 | -5.0118 | 4.9976 | 2.9387 | 0.36486 | -0.84101 | 61.7065 | 0.28069 | 61.6286 | -0.028522 | 0.043657 | 61.5662 | 0.003143 | 61.3672 | 61.8651 | 55.5259 | 56.4521 | 66.4615 | 64.4026 | 61.8288 | 60.6229 | 123.1704 | 61.7446 | 123.0925 | 61.4354 | 61.5076 | 123.0301 | 61.4671 | 122.8312 | 61.6628 | 61.7034 | 61.5849 | 61.6255
4882.0625 | 123.3353 | -61.4548 | 61.6837 | 0.46981 | -5.6129 | -4.8699 | 4.645 | 3.0028 | 0.42896 | -0.73113 | 61.7157 | 0.28526 | 61.624 | -0.028522 | 0.048236 | 61.5753 | -0.001436 | 61.3627 | 61.9246 | 55.8418 | 56.5849 | 66.0998 | 64.4576 | 61.8837 | 60.7236 | 123.1704 | 61.74 | 123.0788 | 61.4263 | 61.503 | 123.0301 | 61.4533 | 122.8174 | 61.6674 | 61.7171 | 61.5758 | 61.6255
4883.0938 | 123.2895 | -61.5143 | 61.6333 | 0.52933 | -5.5672 | -4.6455 | 5.5104 | 3.2363 | 0.48848 | -0.22753 | 61.6928 | 0.27611 | 61.624 | -0.03768 | 0.043657 | 61.5891 | 0.003143 | 61.381 | 62.0436 | 55.9471 | 56.8687 | 67.0247 | 64.7505 | 62.0028 | 61.2868 | 123.2071 | 61.7904 | 123.1383 | 61.4766 | 61.5579 | 123.1033 | 61.5174 | 122.8953 | 61.6491 | 61.6896 | 61.5804 | 61.6209
4884.0625 | 123.317 | -61.4868 | 61.6791 | 0.43776 | -5.851 | -4.6959 | 5.6523 | 3.3049 | 0.40607 | -0.23211 | 61.6928 | 0.27153 | 61.6103 | -0.028522 | 0.048236 | 61.5845 | 0.012299 | 61.3856 | 61.9246 | 55.6358 | 56.7909 | 67.1391 | 64.7917 | 61.8929 | 61.2547 | 123.1796 | 61.7583 | 123.0971 | 61.4583 | 61.5351 | 123.0713 | 61.4991 | 122.8724 | 61.6445 | 61.6805 | 61.562 | 61.598
4885.0938 | 123.262 | -61.4594 | 61.7249 | 0.42402 | -5.9151 | -4.3754 | 5.2769 | 3.2408 | 0.3786 | -0.23211 | 61.6928 | 0.27153 | 61.6149 | -0.023943 | 0.048236 | 61.5799 | 0.012299 | 61.3764 | 61.8834 | 55.5442 | 57.0839 | 66.7362 | 64.7002 | 61.838 | 61.2272 | 123.1521 | 61.7309 | 123.0742 | 61.4354 | 61.5076 | 123.0392 | 61.4716 | 122.8357 | 61.6445 | 61.6805 | 61.5666 | 61.6026
4886.0625 | 123.3765 | -61.4731 | 61.647 | 0.43776 | -5.8281 | -4.3525 | 5.4051 | 3.1676 | 0.40149 | -0.45644 | 61.7065 | 0.28069 | 61.6332 | -0.033101 | 0.039079 | 61.5845 | 0.007721 | 61.3718 | 61.9108 | 55.6449 | 57.1206 | 66.8782 | 64.6407 | 61.8746 | 61.0166 | 123.1796 | 61.7538 | 123.1063 | 61.44 | 61.5122 | 123.0576 | 61.4808 | 122.8449 | 61.6674 | 61.6988 | 61.5941 | 61.6255
4887.0781 | 123.4177 | -61.4365 | 61.6516 | 0.45149 | -5.7457 | -4.4304 | 5.1945 | 3.1905 | 0.41523 | -0.56174 | 61.7065 | 0.27611 | 61.6377 | -0.033101 | 0.048236 | 61.5753 | 0.003143 | 61.3764 | 61.888 | 55.6907 | 57.0061 | 66.6309 | 64.6269 | 61.8517 | 60.8747 | 123.143 | 61.7126 | 123.0742 | 61.4034 | 61.4847 | 123.0118 | 61.4396 | 122.8129 | 61.6583 | 61.7034 | 61.5895 | 61.6346
4888.0625 | 123.3856 | -61.4639 | 61.6562 | 0.35077 | -5.8556 | -4.4304 | 5.1121 | 3.2317 | 0.31908 | -0.77691 | 61.6973 | 0.27611 | 61.6103 | -0.033101 | 0.043657 | 61.5707 | 0.003143 | 61.3718 | 61.8147 | 55.6083 | 57.0336 | 66.576 | 64.6956 | 61.783 | 60.687 | 123.1613 | 61.74 | 123.0742 | 61.4308 | 61.5076 | 123.0347 | 61.4671 | 122.8357 | 61.6537 | 61.6942 | 61.5666 | 61.6071
4889.0781 | 123.3627 | -61.4502 | 61.6653 | 0.35993 | -5.8098 | -4.6501 | 5.1441 | 3.3599 | 0.3145 | -0.69451 | 61.7019 | 0.28069 | 61.6286 | -0.033101 | 0.048236 | 61.5707 | 0.012299 | 61.3718 | 61.8101 | 55.6404 | 56.8001 | 66.5943 | 64.8101 | 61.7647 | 60.7557 | 123.1521 | 61.7309 | 123.0788 | 61.4171 | 61.4984 | 123.0209 | 61.4625 | 122.822 | 61.6537 | 61.6896 | 61.5804 | 61.6163
4890.0625 | 123.3353 | -61.4731 | 61.6837 | 0.35535 | -5.8419 | -4.9569 | 5.1121 | 3.3553 | 0.30992 | -0.82727 | 61.7111 | 0.27611 | 61.6469 | -0.023943 | 0.057392 | 61.5662 | 0.007721 | 61.3764 | 61.8284 | 55.6312 | 56.5162 | 66.5851 | 64.8284 | 61.783 | 60.6458 | 123.1842 | 61.7492 | 123.12 | 61.4491 | 61.5305 | 123.0392 | 61.4808 | 122.8495 | 61.6537 | 61.7034 | 61.5895 | 61.6392
4891.1094 | 123.3124 | -61.4456 | 61.7249 | 0.43776 | -5.851 | -4.934 | 5.0022 | 3.5109 | 0.40149 | -1.0837 | 61.7065 | 0.28069 | 61.6103 | -0.033101 | 0.048236 | 61.5707 | 0.007721 | 61.381 | 61.8834 | 55.5946 | 56.5116 | 66.4478 | 64.9566 | 61.8471 | 60.362 | 123.1521 | 61.7263 | 123.0559 | 61.4125 | 61.4939 | 123.0164 | 61.4533 | 122.8266 | 61.6583 | 61.6988 | 61.562 | 61.6026
4892.0625 | 123.2712 | -61.4685 | 61.7065 | 0.52933 | -5.7091 | -4.934 | 5.1945 | 3.5979 | 0.49306 | -0.9692 | 61.7019 | 0.27611 | 61.6377 | -0.028522 | 0.039079 | 61.5799 | 0.007721 | 61.381 | 61.9978 | 55.7594 | 56.5345 | 66.663 | 65.0664 | 61.9616 | 60.4993 | 123.1704 | 61.7446 | 123.1063 | 61.44 | 61.5076 | 123.0484 | 61.4762 | 122.8495 | 61.6628 | 61.6942 | 61.5987 | 61.63
4893.0938 | 123.2895 | -61.4639 | 61.6837 | 0.52933 | -5.6038 | -5.1217 | 5.0159 | 3.5704 | 0.49764 | -1.134 | 61.7111 | 0.28526 | 61.6469 | -0.028522 | 0.039079 | 61.5799 | 0.003143 | 61.381 | 61.9933 | 55.8601 | 56.3422 | 66.4798 | 65.0344 | 61.9616 | 60.3299 | 123.175 | 61.7492 | 123.1108 | 61.4354 | 61.503 | 123.0438 | 61.4671 | 122.8449 | 61.672 | 61.7079 | 61.6078 | 61.6438
4894.0625 | 123.3032 | -61.4594 | 61.7065 | 0.57053 | -5.6908 | -5.1812 | 5.2998 | 3.6208 | 0.52053 | -0.92799 | 61.6973 | 0.27611 | 61.6103 | -0.033101 | 0.048236 | 61.5845 | 0.007721 | 61.3856 | 62.0299 | 55.7686 | 56.2781 | 66.7591 | 65.0802 | 61.9799 | 60.5314 | 123.1567 | 61.7355 | 123.0696 | 61.4262 | 61.5076 | 123.0438 | 61.4671 | 122.8449 | 61.6491 | 61.6896 | 61.562 | 61.6026
4895.0781 | 123.4268 | -61.441 | 61.647 | 0.44692 | -5.8877 | -5.3506 | 5.3227 | 3.5155 | 0.39691 | -0.87763 | 61.7111 | 0.28069 | 61.6377 | -0.03768 | 0.048236 | 61.5707 | 0.003143 | 61.3718 | 61.888 | 55.5534 | 56.0904 | 66.7637 | 64.9566 | 61.838 | 60.5634 | 123.1521 | 61.7217 | 123.0788 | 61.4034 | 61.4893 | 123.0118 | 61.4442 | 122.8129 | 61.6628 | 61.7079 | 61.5895 | 61.6346
4896.0625 | 123.2803 | -61.4548 | 61.6928 | 0.41029 | -5.9426 | -4.8745 | 4.9289 | 3.4926 | 0.36486 | -0.88221 | 61.7065 | 0.28984 | 61.6377 | -0.028522 | 0.052814 | 61.5753 | 0.003143 | 61.3764 | 61.8651 | 55.5122 | 56.5803 | 66.3837 | 64.9474 | 61.8196 | 60.5726 | 123.1613 | 61.7446 | 123.0925 | 61.4263 | 61.5076 | 123.0301 | 61.4579 | 122.8312 | 61.6537 | 61.7034 | 61.5849 | 61.6346
4897.0781 | 123.3994 | -61.4822 | 61.6379 | 0.39198 | -5.9197 | -5.314 | 5.048 | 3.5888 | 0.36029 | -0.96004 | 61.7065 | 0.28069 | 61.6286 | -0.03768 | 0.043657 | 61.5753 | 0.012299 | 61.3718 | 61.8742 | 55.5625 | 56.1682 | 66.5302 | 65.071 | 61.8425 | 60.5222 | 123.1887 | 61.7629 | 123.1108 | 61.4446 | 61.5259 | 123.0576 | 61.4945 | 122.8541 | 61.6628 | 61.6942 | 61.5849 | 61.6163
4898.0625 | 123.2849 | -61.4502 | 61.7203 | 0.47439 | -5.8098 | -5.2362 | 5.1212 | 3.7673 | 0.43354 | -1.1477 | 61.7202 | 0.28069 | 61.6515 | -0.023943 | 0.039079 | 61.5753 | 0.012299 | 61.381 | 61.9246 | 55.6404 | 56.214 | 66.5714 | 65.2175 | 61.8837 | 60.3025 | 123.1704 | 61.7309 | 123.1017 | 61.4263 | 61.4893 | 123.0255 | 61.4625 | 122.8312 | 61.6812 | 61.7079 | 61.6124 | 61.6392
4899.0781 | 123.3856 | -61.4548 | 61.6699 | 0.44692 | -5.9106 | -5.2637 | 4.8786 | 3.8177 | 0.41065 | -1.1661 | 61.7019 | 0.28984 | 61.6103 | -0.03768 | 0.048236 | 61.5753 | 0.012299 | 61.3718 | 61.9017 | 55.5442 | 56.1911 | 66.3333 | 65.2724 | 61.8654 | 60.2887 | 123.1567 | 61.7446 | 123.0651 | 61.4171 | 61.503 | 123.0301 | 61.4671 | 122.8266 | 61.6537 | 61.6896 | 61.562 | 61.598
4900.0625 | 123.2895 | -61.4548 | 61.7249 | 0.37824 | -6.025 | -5.4651 | 5.0617 | 3.6391 | 0.34197 | -0.89594 | 61.7248 | 0.28069 | 61.6332 | -0.028522 | 0.048236 | 61.5707 | 0.003143 | 61.3764 | 61.833 | 55.4297 | 55.9897 | 66.5165 | 65.0939 | 61.7967 | 60.5588 | 123.1796 | 61.7355 | 123.0879 | 61.4263 | 61.503 | 123.0255 | 61.4579 | 122.8312 | 61.6766 | 61.7217 | 61.5849 | 61.63
4901.0938 | 123.4039 | -61.4319 | 61.647 | 0.41029 | -5.8968 | -5.3278 | 5.2128 | 3.7902 | 0.36029 | -0.9051 | 61.7019 | 0.28069 | 61.6469 | -0.033101 | 0.043657 | 61.5753 | 0.007721 | 61.3764 | 61.8422 | 55.5351 | 56.1041 | 66.6447 | 65.2221 | 61.7922 | 60.5268 | 123.1338 | 61.7126 | 123.0788 | 61.3988 | 61.4755 | 123.0072 | 61.4396 | 122.8083 | 61.6583 | 61.6942 | 61.6032 | 61.6392
4902.0625 | 123.3078 | -61.4594 | 61.7249 | 0.51101 | -5.9106 | -5.0576 | 4.7504 | 3.8131 | 0.47475 | -0.87763 | 61.7065 | 0.28069 | 61.6149 | -0.033101 | 0.048236 | 61.5799 | 0.012299 | 61.381 | 61.9704 | 55.5488 | 56.4017 | 66.2097 | 65.2724 | 61.9341 | 60.5817 | 123.1659 | 61.74 | 123.0742 | 61.4262 | 61.5076 | 123.0392 | 61.4716 | 122.8403 | 61.6583 | 61.6942 | 61.5666 | 61.6026
4903.0781 | 123.3902 | -61.4777 | 61.6562 | 0.5568 | -5.7137 | -4.6227 | 4.6267 | 3.9413 | 0.51595 | -0.90968 | 61.6882 | 0.28069 | 61.6377 | -0.03768 | 0.043657 | 61.5799 | 0.007721 | 61.3718 | 62.0345 | 55.764 | 56.855 | 66.1044 | 65.4189 | 61.9936 | 60.568 | 123.1659 | 61.7583 | 123.1154 | 61.44 | 61.5213 | 123.0576 | 61.4854 | 122.8495 | 61.6445 | 61.6805 | 61.5941 | 61.63
4904.0625 | 123.3994 | -61.441 | 61.6791 | 0.52933 | -5.8007 | -4.7234 | 4.9014 | 3.7169 | 0.48848 | -0.78607 | 61.6973 | 0.28069 | 61.6286 | -0.033101 | 0.052814 | 61.5753 | 0.007721 | 61.381 | 61.9704 | 55.6404 | 56.7177 | 66.3425 | 65.158 | 61.9295 | 60.655 | 123.1384 | 61.7217 | 123.0696 | 61.4079 | 61.4939 | 123.0164 | 61.4488 | 122.822 | 61.6445 | 61.6896 | 61.5758 | 61.6209
4905.0781 | 123.3856 | -61.4777 | 61.6241 | 0.47896 | -5.9884 | -5.0256 | 5.5607 | 3.8039 | 0.42896 | -0.79065 | 61.6973 | 0.28069 | 61.6103 | -0.033101 | 0.043657 | 61.5707 | 0.007721 | 61.3627 | 61.9566 | 55.4893 | 56.4521 | 67.0384 | 65.2816 | 61.9066 | 60.687 | 123.175 | 61.7583 | 123.0879 | 61.4446 | 61.5213 | 123.0484 | 61.4854 | 122.8403 | 61.6537 | 61.6896 | 61.5666 | 61.6026
4906.0625 | 123.2986 | -61.4868 | 61.702 | 0.45149 | -6.0983 | -5.1034 | 5.1533 | 3.9825 | 0.41523 | -0.97835 | 61.7065 | 0.28069 | 61.6469 | -0.033101 | 0.039079 | 61.5799 | 0.007721 | 61.3718 | 61.9383 | 55.3885 | 56.3834 | 66.6401 | 65.4693 | 61.902 | 60.5085 | 123.1933 | 61.7675 | 123.1337 | 61.4537 | 61.5259 | 123.0667 | 61.4945 | 122.8586 | 61.6674 | 61.6988 | 61.6078 | 61.6392
4907.0938 | 123.3078 | -61.4639 | 61.6974 | 0.3874 | -6.1212 | -5.282 | 5.5333 | 3.9916 | 0.33739 | -1.1661 | 61.7019 | 0.27611 | 61.6103 | -0.028522 | 0.039079 | 61.5845 | 0.007721 | 61.3764 | 61.8513 | 55.3427 | 56.182 | 66.9972 | 65.4555 | 61.8013 | 60.2979 | 123.1659 | 61.74 | 123.0742 | 61.4354 | 61.503 | 123.0484 | 61.4716 | 122.8403 | 61.6628 | 61.6942 | 61.5712 | 61.6026
4908.0625 | 123.2574 | -61.4731 | 61.702 | 0.28209 | -6.1853 | -5.2362 | 5.3135 | 3.7353 | 0.23209 | -1.0379 | 61.7111 | 0.28069 | 61.6377 | -0.028522 | 0.052814 | 61.5707 | 0.007721 | 61.3581 | 61.7552 | 55.2878 | 56.2369 | 66.7866 | 65.2083 | 61.7052 | 60.4352 | 123.1842 | 61.7538 | 123.1108 | 61.4446 | 61.5259 | 123.0438 | 61.4808 | 122.8312 | 61.6583 | 61.7034 | 61.5849 | 61.63
4909.0938 | 123.3902 | -61.4456 | 61.6745 | 0.26378 | -6.2265 | -5.6574 | 4.3246 | 3.9825 | 0.22751 | -1.102 | 61.7202 | 0.28069 | 61.6561 | -0.028522 | 0.048236 | 61.5616 | 0.007721 | 61.3535 | 61.7094 | 55.2191 | 55.7882 | 65.7702 | 65.4281 | 61.6731 | 60.3437 | 123.1659 | 61.7263 | 123.1017 | 61.4171 | 61.4939 | 123.0072 | 61.4533 | 122.7991 | 61.672 | 61.7125 | 61.6078 | 61.6483
4910.0625 | 123.4085 | -61.4456 | 61.6837 | 0.35535 | -5.9151 | -5.5475 | 4.1094 | 4.0282 | 0.32366 | -0.90052 | 61.7202 | 0.28069 | 61.6332 | -0.028522 | 0.057392 | 61.5616 | 0.003143 | 61.3489 | 61.801 | 55.5305 | 55.8981 | 65.555 | 65.4739 | 61.7693 | 60.5451 | 123.1659 | 61.7263 | 123.0788 | 61.4171 | 61.503 | 123.0072 | 61.4488 | 122.7945 | 61.6628 | 61.7171 | 61.5758 | 61.63
4911.1094 | 123.3307 | -61.4548 | 61.7111 | 0.3233 | -5.938 | -5.14 | 4.4115 | 4.0099 | 0.29619 | -0.9692 | 61.7157 | 0.27153 | 61.6561 | -0.028522 | 0.048236 | 61.5616 | 0.003143 | 61.3581 | 61.7781 | 55.5167 | 56.3147 | 65.8663 | 65.4647 | 61.751 | 60.4856 | 123.1704 | 61.7263 | 123.1108 | 61.4263 | 61.503 | 123.0164 | 61.4579 | 122.8129 | 61.6674 | 61.7125 | 61.6078 | 61.6529
4912.0625 | 123.4039 | -61.4594 | 61.6791 | 0.35077 | -6.1258 | -4.8699 | 4.9655 | 4.0557 | 0.30992 | -1.4774 | 61.7157 | 0.28069 | 61.6469 | -0.028522 | 0.048236 | 61.5707 | 0.007721 | 61.3581 | 61.8101 | 55.3336 | 56.5895 | 66.4249 | 65.5151 | 61.7693 | 59.982 | 123.175 | 61.74 | 123.1063 | 61.4308 | 61.5076 | 123.0301 | 61.4671 | 122.8174 | 61.6674 | 61.7079 | 61.5987 | 61.6392
4913.0938 | 123.3719 | -61.4365 | 61.6562 | 0.3874 | -6.1578 | -4.7737 | 5.1853 | 3.9916 | 0.35113 | -1.546 | 61.7065 | 0.28526 | 61.6149 | -0.033101 | 0.039079 | 61.5753 | 0.016878 | 61.3581 | 61.8239 | 55.2786 | 56.6627 | 66.6218 | 65.4281 | 61.7876 | 59.8904 | 123.143 | 61.7217 | 123.0513 | 61.4034 | 61.4755 | 123.0118 | 61.4533 | 122.7945 | 61.6674 | 61.6896 | 61.5758 | 61.598
4914.0625 | 123.436 | -61.4273 | 61.6608 | 0.43776 | -6.0617 | -5.0988 | 5.1258 | 4.0786 | 0.40149 | -1.514 | 61.7111 | 0.28069 | 61.6469 | -0.033101 | 0.048236 | 61.5707 | 0.007721 | 61.3535 | 61.8651 | 55.3656 | 56.3285 | 66.5531 | 65.5059 | 61.8288 | 59.9133 | 123.1384 | 61.708 | 123.0742 | 61.3942 | 61.4755 | 122.998 | 61.435 | 122.7808 | 61.6628 | 61.7034 | 61.5987 | 61.6392
4915.0938 | 123.3627 | -61.4685 | 61.6516 | 0.40571 | -6.1716 | -5.2087 | 4.8557 | 4.1427 | 0.35571 | -1.2576 | 61.7157 | 0.27611 | 61.624 | -0.028522 | 0.039079 | 61.5662 | 0.007721 | 61.3489 | 61.8742 | 55.2969 | 56.2598 | 66.3242 | 65.6112 | 61.8242 | 60.2109 | 123.1842 | 61.7446 | 123.0925 | 61.44 | 61.5076 | 123.0347 | 61.4762 | 122.8174 | 61.6766 | 61.7079 | 61.5849 | 61.6163
4916.0625 | 123.2666 | -61.4639 | 61.7111 | 0.40113 | -6.1578 | -5.2774 | 4.9152 | 4.3029 | 0.36944 | -1.0379 | 61.7065 | 0.28069 | 61.624 | -0.028522 | 0.052814 | 61.5753 | 0.007721 | 61.3581 | 61.8651 | 55.3061 | 56.1865 | 66.3791 | 65.7669 | 61.8334 | 60.4261 | 123.1704 | 61.7446 | 123.0879 | 61.4354 | 61.5167 | 123.0392 | 61.4716 | 122.822 | 61.6537 | 61.6988 | 61.5712 | 61.6163
4917.0938 | 123.3994 | -61.4594 | 61.6699 | 0.46065 | -6.0754 | -5.6025 | 4.2559 | 3.8817 | 0.41523 | -1.0562 | 61.7294 | 0.28069 | 61.6606 | -0.033101 | 0.052814 | 61.5616 | 0.007721 | 61.3352 | 61.92 | 55.3839 | 55.8569 | 65.7152 | 65.3411 | 61.8746 | 60.4032 | 123.1887 | 61.74 | 123.12 | 61.4262 | 61.5122 | 123.0209 | 61.4671 | 122.7945 | 61.6766 | 61.7217 | 61.6078 | 61.6529
4918.0625 | 123.2895 | -61.441 | 61.7065 | 0.45607 | -6.0937 | -5.7536 | 4.2605 | 3.7719 | 0.42896 | -1.0928 | 61.7202 | 0.28069 | 61.6561 | -0.028522 | 0.048236 | 61.5662 | 0.012299 | 61.3398 | 61.8971 | 55.3473 | 55.6875 | 65.7015 | 65.2129 | 61.87 | 60.3482 | 123.1613 | 61.7217 | 123.0971 | 61.4125 | 61.4893 | 123.0072 | 61.4533 | 122.7808 | 61.672 | 61.7079 | 61.6078 | 61.6438
4919.0781 | 123.3994 | -61.4273 | 61.6379 | 0.42402 | -6.0937 | -5.9047 | 4.1368 | 3.8634 | 0.38776 | -0.93257 | 61.7202 | 0.28984 | 61.624 | -0.028522 | 0.039079 | 61.5662 | 0.003143 | 61.3489 | 61.8513 | 55.3336 | 55.5226 | 65.5641 | 65.2907 | 61.8151 | 60.4947 | 123.1475 | 61.7171 | 123.0513 | 61.3988 | 61.4664 | 122.9935 | 61.4305 | 122.7762 | 61.6812 | 61.7171 | 61.5849 | 61.6209
4920.0625 | 123.4268 | -61.4365 | 61.6699 | 0.38282 | -6.2128 | -5.9092 | 4.6771 | 4.248 | 0.35571 | -0.85474 | 61.7202 | 0.27611 | 61.6423 | -0.028522 | 0.043657 | 61.5707 | -0.001436 | 61.3535 | 61.8193 | 55.2237 | 55.5272 | 66.1136 | 65.6844 | 61.7922 | 60.5817 | 123.1567 | 61.7126 | 123.0788 | 61.4079 | 61.4801 | 123.0072 | 61.435 | 122.79 | 61.6766 | 61.7217 | 61.5987 | 61.6438
4921.0938 | 123.3032 | -61.4594 | 61.702 | 0.35535 | -6.3227 | -5.9504 | 5.1487 | 3.6391 | 0.30992 | -0.8639 | 61.7202 | 0.27153 | 61.6561 | -0.033101 | 0.039079 | 61.5616 | 0.007721 | 61.3398 | 61.8147 | 55.1367 | 55.5089 | 66.608 | 65.0985 | 61.7693 | 60.5955 | 123.1796 | 61.7309 | 123.1154 | 61.4262 | 61.4984 | 123.0209 | 61.4671 | 122.7991 | 61.6812 | 61.7125 | 61.617 | 61.6483
4922.0625 | 123.436 | -61.377 | 61.7111 | 0.36451 | -6.3318 | -5.9092 | 5.0067 | 3.6117 | 0.33282 | -0.92799 | 61.7157 | 0.28069 | 61.6286 | -0.03768 | 0.048236 | 61.5662 | 0.003143 | 61.3489 | 61.7415 | 55.0451 | 55.4677 | 66.3837 | 64.9886 | 61.7098 | 60.449 | 123.0926 | 61.6576 | 123.0055 | 61.3393 | 61.4252 | 122.9431 | 61.3801 | 122.7259 | 61.6674 | 61.7125 | 61.5804 | 61.6255
4923.0938 | 123.4085 | -61.4502 | 61.6974 | 0.33246 | -6.3547 | -5.9871 | 4.9701 | 4.1335 | 0.29619 | -1.0653 | 61.7111 | 0.27153 | 61.6469 | -0.03768 | 0.043657 | 61.5662 | 0.007721 | 61.3535 | 61.7827 | 55.0955 | 55.4631 | 66.4203 | 65.5837 | 61.7464 | 60.3849 | 123.1613 | 61.7217 | 123.0971 | 61.4125 | 61.4939 | 123.0164 | 61.4579 | 122.8037 | 61.6674 | 61.7034 | 61.6032 | 61.6392
4924.0625 | 123.3856 | -61.4639 | 61.6653 | 0.38282 | -6.2448 | -6.0237 | 5.0663 | 4.2068 | 0.34655 | -1.0837 | 61.7202 | 0.28069 | 61.6515 | -0.042259 | 0.048236 | 61.5616 | 0.016878 | 61.3398 | 61.8467 | 55.2191 | 55.4402 | 66.5302 | 65.6707 | 61.8105 | 60.3803 | 123.1842 | 61.7446 | 123.1154 | 61.4217 | 61.5122 | 123.0255 | 61.4808 | 122.8037 | 61.672 | 61.7034 | 61.6032 | 61.6346
4925.0781 | 123.3719 | -61.4273 | 61.647 | 0.37366 | -6.2265 | -5.9459 | 5.0205 | 4.2938 | 0.33282 | -1.1706 | 61.7111 | 0.29442 | 61.6194 | -0.03768 | 0.052814 | 61.5662 | 0.003143 | 61.3443 | 61.801 | 55.2008 | 55.4814 | 66.4478 | 65.7211 | 61.7601 | 60.2567 | 123.1384 | 61.7217 | 123.0467 | 61.3896 | 61.4801 | 122.9935 | 61.4305 | 122.7717 | 61.6583 | 61.7079 | 61.5666 | 61.6163
4926.0625 | 123.4268 | -61.4273 | 61.6653 | 0.38282 | -6.2952 | -5.9459 | 4.7458 | 4.4036 | 0.34197 | -1.1615 | 61.7202 | 0.27611 | 61.624 | -0.028522 | 0.057392 | 61.5662 | 0.012299 | 61.3535 | 61.8101 | 55.1321 | 55.4814 | 66.1731 | 65.8309 | 61.7693 | 60.2658 | 123.1475 | 61.7034 | 123.0513 | 61.3988 | 61.4847 | 122.9935 | 61.4396 | 122.7808 | 61.6628 | 61.7079 | 61.5666 | 61.6117
4927.0781 | 123.3902 | -61.4548 | 61.6241 | 0.50186 | -5.9289 | -5.6208 | 3.5096 | 3.9092 | 0.46101 | -0.7998 | 61.7248 | 0.28984 | 61.6561 | -0.028522 | 0.043657 | 61.5616 | 0.003143 | 61.3535 | 61.9566 | 55.5259 | 55.834 | 64.9644 | 65.364 | 61.9158 | 60.655 | 123.1796 | 61.7446 | 123.1108 | 61.4263 | 61.4984 | 123.0164 | 61.4579 | 122.8083 | 61.6812 | 61.7217 | 61.6124 | 61.6529
4928.0625 | 123.3124 | -61.4548 | 61.7294 | 0.40113 | -6.2906 | -5.7902 | 3.4913 | 4.5181 | 0.36486 | -0.81354 | 61.7248 | 0.27611 | 61.6515 | -0.028522 | 0.039079 | 61.557 | 0.007721 | 61.3535 | 61.8559 | 55.1642 | 55.6646 | 64.946 | 65.9729 | 61.8196 | 60.6412 | 123.1796 | 61.7309 | 123.1063 | 61.4263 | 61.4939 | 123.0118 | 61.4625 | 122.8083 | 61.6857 | 61.7171 | 61.6124 | 61.6438
4929.0938 | 123.3398 | -61.4182 | 61.6837 | 0.41029 | -6.3135 | -5.8909 | 3.7614 | 4.5639 | 0.36029 | -0.91884 | 61.7157 | 0.28526 | 61.6377 | -0.028522 | 0.048236 | 61.5616 | 0.003143 | 61.3535 | 61.8284 | 55.1047 | 55.5272 | 65.1796 | 65.982 | 61.7784 | 60.4993 | 123.1338 | 61.7034 | 123.0559 | 61.3896 | 61.4664 | 122.9797 | 61.4213 | 122.7717 | 61.6674 | 61.7125 | 61.5895 | 61.6346
4930.0625 | 123.4222 | -61.4227 | 61.6882 | 0.31872 | -6.2586 | -5.8955 | 3.7339 | 4.5868 | 0.2733 | -0.98293 | 61.7248 | 0.27611 | 61.6606 | -0.028522 | 0.039079 | 61.5616 | 0.003143 | 61.3627 | 61.7415 | 55.1642 | 55.5272 | 65.1567 | 66.0095 | 61.696 | 60.4398 | 123.1475 | 61.6988 | 123.0834 | 61.3942 | 61.4618 | 122.9843 | 61.4259 | 122.7854 | 61.6857 | 61.7217 | 61.6216 | 61.6575
4931.1094 | 123.4131 | -61.4548 | 61.6608 | 0.27294 | -6.2769 | -6.01 | 3.9308 | 4.6875 | 0.22751 | -0.91884 | 61.7202 | 0.28526 | 61.6515 | -0.042259 | 0.039079 | 61.5616 | 0.003143 | 61.3535 | 61.7277 | 55.1779 | 55.4448 | 65.3856 | 66.1422 | 61.6823 | 60.5359 | 123.175 | 61.74 | 123.1063 | 61.4125 | 61.4939 | 123.0164 | 61.4579 | 122.8083 | 61.6812 | 61.7171 | 61.6124 | 61.6483
4932.0625 | 123.3948 | -61.3998 | 61.6425 | 0.29125 | -6.2128 | -4.9798 | 4.2284 | 4.7332 | 0.25498 | -1.0791 | 61.7111 | 0.28069 | 61.6194 | -0.03768 | 0.048236 | 61.5707 | 0.003143 | 61.3672 | 61.6911 | 55.1871 | 56.4201 | 65.6282 | 66.1331 | 61.6548 | 60.3208 | 123.1109 | 61.6805 | 123.0193 | 61.3622 | 61.4481 | 122.9706 | 61.403 | 122.7671 | 61.6628 | 61.7079 | 61.5712 | 61.6163
4933.0938 | 123.3444 | -61.4548 | 61.6425 | 0.26378 | -6.2402 | -5.4056 | 4.4436 | 4.7928 | 0.22293 | -1.1798 | 61.7157 | 0.28069 | 61.6561 | -0.028522 | 0.043657 | 61.5707 | 0.012299 | 61.3718 | 61.7186 | 55.2145 | 56.0492 | 65.8984 | 66.2475 | 61.6777 | 60.275 | 123.1704 | 61.7355 | 123.1108 | 61.4263 | 61.4984 | 123.0255 | 61.4671 | 122.8266 | 61.672 | 61.7034 | 61.6124 | 61.6438
4934.0625 | 123.381 | -61.4365 | 61.6562 | 0.33703 | -5.9747 | -5.6116 | 4.1689 | 4.8157 | 0.30077 | -1.0333 | 61.7065 | 0.28526 | 61.624 | -0.033101 | 0.048236 | 61.5753 | 0.003143 | 61.3718 | 61.7735 | 55.4618 | 55.8248 | 65.6053 | 66.2521 | 61.7372 | 60.4032 | 123.143 | 61.7217 | 123.0605 | 61.4034 | 61.4847 | 123.0118 | 61.4396 | 122.8083 | 61.6583 | 61.7034 | 61.5758 | 61.6209
4935.0625 | 123.436 | -61.4273 | 61.6699 | 0.30956 | -6.112 | -5.9276 | 4.32 | 4.8019 | 0.26872 | -1.047 | 61.7157 | 0.28526 | 61.6377 | -0.028522 | 0.052814 | 61.5662 | 0.012299 | 61.3718 | 61.7369 | 55.3153 | 55.4998 | 65.7473 | 66.2292 | 61.696 | 60.3803 | 123.143 | 61.7126 | 123.0651 | 61.3988 | 61.4801 | 122.9935 | 61.4396 | 122.7991 | 61.6628 | 61.7034 | 61.5849 | 61.6255
4936.1094 | 123.3673 | -61.4685 | 61.6699 | 0.40113 | -6.1349 | -5.923 | 3.212 | 4.8477 | 0.36029 | -1.0379 | 61.7248 | 0.27611 | 61.6652 | -0.028522 | 0.039079 | 61.557 | 0.003143 | 61.3535 | 61.8696 | 55.3336 | 55.5455 | 64.6805 | 66.3162 | 61.8288 | 60.4306 | 123.1933 | 61.7446 | 123.1337 | 61.44 | 61.5076 | 123.0255 | 61.4716 | 122.822 | 61.6857 | 61.7217 | 61.6261 | 61.6621
4937.0625 | 123.3948 | -61.4365 | 61.6699 | 0.43776 | -6.2631 | -5.7994 | 5.1212 | 5.0079 | 0.39233 | -1.2714 | 61.6928 | 0.28069 | 61.6103 | -0.03768 | 0.043657 | 61.5753 | 0.007721 | 61.3672 | 61.8742 | 55.1733 | 55.6371 | 66.5577 | 66.4444 | 61.8288 | 60.1651 | 123.1292 | 61.7171 | 123.0467 | 61.3988 | 61.4801 | 123.0118 | 61.4442 | 122.8037 | 61.6491 | 61.685 | 61.5666 | 61.6026
4938.0938 | 123.349 | -61.4731 | 61.6516 | 0.46981 | -6.2219 | -5.108 | 5.4966 | 5.1682 | 0.42896 | -1.1111 | 61.6882 | 0.28526 | 61.6286 | -0.028522 | 0.048236 | 61.5891 | 0.007721 | 61.3764 | 61.9429 | 55.2512 | 56.3651 | 66.9697 | 66.6412 | 61.902 | 60.362 | 123.1613 | 61.7583 | 123.1017 | 61.4446 | 61.5213 | 123.0621 | 61.4808 | 122.8495 | 61.64 | 61.6805 | 61.5804 | 61.6209
4939.0625 | 123.381 | -61.4594 | 61.6699 | 0.52475 | -6.0113 | -5.5521 | 5.4371 | 5.2872 | 0.47475 | -0.88221 | 61.6928 | 0.28984 | 61.6332 | -0.03768 | 0.043657 | 61.5845 | 0.003143 | 61.3764 | 61.9841 | 55.4481 | 55.9072 | 66.8965 | 66.7465 | 61.9341 | 60.5771 | 123.1521 | 61.7492 | 123.0925 | 61.4217 | 61.503 | 123.0438 | 61.4625 | 122.8357 | 61.6491 | 61.6896 | 61.5895 | 61.63
4940.0938 | 123.3902 | -61.4868 | 61.6379 | 0.44692 | -6.1624 | -5.8497 | 5.0708 | 5.3192 | 0.42438 | -1.0699 | 61.6973 | 0.28526 | 61.6103 | -0.03768 | 0.052814 | 61.5753 | 0.003143 | 61.3627 | 61.9337 | 55.3244 | 55.6371 | 66.5577 | 66.806 | 61.9112 | 60.4169 | 123.1842 | 61.7721 | 123.0971 | 61.4491 | 61.5396 | 123.0621 | 61.49 | 122.8495 | 61.6445 | 61.6942 | 61.5575 | 61.6071
4941.0625 | 123.2803 | -61.5051 | 61.6791 | 0.41029 | -6.199 | -6.0008 | 5.1762 | 5.3375 | 0.38318 | -1.3538 | 61.7065 | 0.28069 | 61.6469 | -0.033101 | 0.048236 | 61.5707 | 0.003143 | 61.3535 | 61.9154 | 55.3061 | 55.5043 | 66.6813 | 66.8427 | 61.8883 | 60.1514 | 123.2116 | 61.7858 | 123.152 | 61.472 | 61.5534 | 123.0759 | 61.5083 | 122.8586 | 61.6583 | 61.7034 | 61.5987 | 61.6438
4942.0625 | 123.3582 | -61.4319 | 61.647 | 0.4927 | -6.1212 | -5.8177 | 5.1258 | 5.4383 | 0.45185 | -1.3446 | 61.7019 | 0.27611 | 61.6286 | -0.028522 | 0.048236 | 61.5845 | 0.007721 | 61.3581 | 61.9246 | 55.3107 | 55.6142 | 66.5577 | 66.8701 | 61.8837 | 60.0873 | 123.1338 | 61.708 | 123.0605 | 61.4034 | 61.4801 | 123.0164 | 61.4396 | 122.79 | 61.6537 | 61.6942 | 61.5804 | 61.6209
4943.0938 | 123.3582 | -61.4639 | 61.6013 | 0.53848 | -6.0754 | -5.2087 | 4.9106 | 5.3925 | 0.48848 | -1.1706 | 61.6928 | 0.27611 | 61.6057 | -0.028522 | 0.048236 | 61.5845 | 0.012299 | 61.3672 | 62.0024 | 55.3885 | 56.2552 | 66.3745 | 66.8564 | 61.9524 | 60.2933 | 123.1567 | 61.74 | 123.0696 | 61.4354 | 61.5122 | 123.0484 | 61.4762 | 122.8312 | 61.6445 | 61.6805 | 61.5575 | 61.5934
4944.0625 | 123.3444 | -61.4731 | 61.6562 | 0.598 | -6.0708 | -4.9065 | 4.9655 | 5.3192 | 0.55716 | -1.0928 | 61.7019 | 0.28526 | 61.6286 | -0.028522 | 0.043657 | 61.5891 | 0.012299 | 61.3764 | 62.0711 | 55.4023 | 56.5666 | 66.4386 | 66.7923 | 62.0302 | 60.3803 | 123.175 | 61.7583 | 123.1017 | 61.4446 | 61.5167 | 123.0621 | 61.4854 | 122.8495 | 61.6583 | 61.6896 | 61.5849 | 61.6163
4945.0938 | 123.3536 | -61.4822 | 61.647 | 0.49728 | -6.1899 | -4.7188 | 5.3822 | 5.2506 | 0.45643 | -1.1569 | 61.6928 | 0.27611 | 61.6011 | -0.033101 | 0.048236 | 61.5891 | 0.003143 | 61.3672 | 61.9795 | 55.2924 | 56.7634 | 66.8644 | 66.7328 | 61.9387 | 60.3253 | 123.175 | 61.7583 | 123.0834 | 61.4491 | 61.5305 | 123.0713 | 61.4854 | 122.8495 | 61.6445 | 61.6896 | 61.5529 | 61.598
4946.0625 | 123.4131 | -61.4594 | 61.6333 | 0.51101 | -6.1212 | -4.9981 | 5.5012 | 5.3467 | 0.47017 | -1.1432 | 61.6928 | 0.27611 | 61.6103 | -0.028522 | 0.043657 | 61.5936 | 0.016878 | 61.3764 | 61.9704 | 55.3382 | 56.4613 | 66.9606 | 66.806 | 61.9295 | 60.3162 | 123.1521 | 61.7355 | 123.0696 | 61.4308 | 61.503 | 123.053 | 61.4762 | 122.8357 | 61.6491 | 61.6759 | 61.5666 | 61.5934
4947.0938 | 123.3582 | -61.4822 | 61.5967 | 0.60716 | -5.851 | -5.1492 | 5.0296 | 5.3925 | 0.55716 | -0.67161 | 61.6928 | 0.28984 | 61.624 | -0.033101 | 0.048236 | 61.5891 | 0.003143 | 61.381 | 62.0894 | 55.6312 | 56.333 | 66.5119 | 66.8747 | 62.0394 | 60.8106 | 123.175 | 61.7721 | 123.1063 | 61.4491 | 61.5305 | 123.0713 | 61.4854 | 122.8632 | 61.6445 | 61.6896 | 61.5758 | 61.6209
4948.0625 | 123.317 | -61.4182 | 61.647 | 0.58885 | -6.0021 | -5.2866 | 5.0296 | 5.3192 | 0.548 | -0.73113 | 61.6882 | 0.28526 | 61.5965 | -0.028522 | 0.043657 | 61.5891 | 0.007721 | 61.381 | 62.007 | 55.416 | 56.1316 | 66.4478 | 66.7374 | 61.9662 | 60.687 | 123.1063 | 61.7034 | 123.0147 | 61.3896 | 61.4618 | 123.0072 | 61.4259 | 122.7991 | 61.6445 | 61.6805 | 61.5529 | 61.5888
4949.0938 | 123.3582 | -61.4502 | 61.6425 | 0.60258 | -6.0937 | -5.2499 | 5.2403 | 5.333 | 0.55258 | -1.0287 | 61.6928 | 0.27611 | 61.6194 | -0.033101 | 0.043657 | 61.5891 | 0.003143 | 61.3718 | 62.0528 | 55.3565 | 56.2003 | 66.6904 | 66.7832 | 62.0028 | 60.4215 | 123.143 | 61.7263 | 123.0696 | 61.4171 | 61.4939 | 123.0392 | 61.4533 | 122.822 | 61.6491 | 61.6896 | 61.5758 | 61.6163
4950.0625 | 123.3398 | -61.4822 | 61.6196 | 0.598 | -6.0159 | -4.5036 | 5.048 | 5.3925 | 0.55258 | -1.0104 | 61.6882 | 0.28069 | 61.6149 | -0.033101 | 0.043657 | 61.5845 | 0.003143 | 61.381 | 62.0802 | 55.4664 | 56.9786 | 66.5302 | 66.8747 | 62.0348 | 60.4718 | 123.1704 | 61.7629 | 123.0971 | 61.4491 | 61.5259 | 123.0667 | 61.4854 | 122.8632 | 61.6445 | 61.685 | 61.5712 | 61.6117
4951.0938 | 123.2849 | -61.4914 | 61.6745 | 0.51559 | -6.0891 | -4.9111 | 4.7549 | 5.365 | 0.47475 | -1.0516 | 61.6973 | 0.27153 | 61.6057 | -0.03768 | 0.048236 | 61.5753 | 0.007721 | 61.3627 | 62.007 | 55.4023 | 56.5803 | 66.2463 | 66.8564 | 61.9661 | 60.4398 | 123.1887 | 61.7629 | 123.0971 | 61.4537 | 61.5396 | 123.0667 | 61.4991 | 122.8541 | 61.6491 | 61.6896 | 61.5575 | 61.598
4952.0625 | 123.381 | -61.4685 | 61.6104 | 0.4927 | -6.08 | -4.4624 | 4.8373 | 5.4383 | 0.44728 | -0.85474 | 61.6973 | 0.28069 | 61.6332 | -0.033101 | 0.052814 | 61.5936 | 0.003143 | 61.3718 | 61.9612 | 55.3885 | 57.0061 | 66.3059 | 66.9068 | 61.9158 | 60.6138 | 123.1659 | 61.7492 | 123.1017 | 61.4354 | 61.5213 | 123.0621 | 61.4716 | 122.8403 | 61.6445 | 61.6942 | 61.5804 | 61.63
4953.0781 | 123.4177 | -61.4639 | 61.6196 | 0.52933 | -5.9335 | -5.0118 | 5.1578 | 5.5848 | 0.4839 | -0.95546 | 61.679 | 0.28526 | 61.6011 | -0.028522 | 0.043657 | 61.5936 | 0.003143 | 61.3672 | 61.9933 | 55.5305 | 56.4521 | 66.6218 | 67.0487 | 61.9478 | 60.5085 | 123.143 | 61.7492 | 123.0651 | 61.4354 | 61.5076 | 123.0576 | 61.4671 | 122.8312 | 61.6354 | 61.6759 | 61.5575 | 61.598
4954.0625 | 123.3032 | -61.4914 | 61.6699 | 0.50186 | -6.025 | -5.3369 | 5.2219 | 5.5619 | 0.47017 | -0.78149 | 61.6882 | 0.28069 | 61.6011 | -0.033101 | 0.048236 | 61.5891 | 0.012299 | 61.3718 | 61.9933 | 55.4664 | 56.1545 | 66.7133 | 67.0533 | 61.9616 | 60.7099 | 123.1796 | 61.7721 | 123.0925 | 61.4583 | 61.5396 | 123.0804 | 61.5037 | 122.8632 | 61.64 | 61.6759 | 61.5529 | 61.5888
4955.0938 | 123.2712 | -61.5005 | 61.6699 | 0.49728 | -6.0571 | -5.0988 | 5.0205 | 5.4245 | 0.46101 | -0.80438 | 61.6973 | 0.27611 | 61.6377 | -0.033101 | 0.048236 | 61.5891 | 0.012299 | 61.3672 | 61.9978 | 55.4435 | 56.4017 | 66.521 | 66.9251 | 61.9616 | 60.6962 | 123.1979 | 61.7767 | 123.1383 | 61.4674 | 61.5488 | 123.0896 | 61.5128 | 122.8678 | 61.6491 | 61.685 | 61.5895 | 61.6255
4956.0625 | 123.4131 | -61.4502 | 61.6425 | 0.52017 | -6.0983 | -4.9935 | 4.8282 | 5.4016 | 0.47017 | -1.1523 | 61.6973 | 0.27611 | 61.6057 | -0.033101 | 0.052814 | 61.5799 | 0.012299 | 61.3718 | 61.9704 | 55.3519 | 56.4567 | 66.2784 | 66.8518 | 61.9204 | 60.2979 | 123.1475 | 61.7263 | 123.0559 | 61.4171 | 61.503 | 123.0301 | 61.4625 | 122.822 | 61.6445 | 61.685 | 61.5529 | 61.5934
4957.0938 | 123.4085 | -61.4868 | 61.6241 | 0.45149 | -5.993 | -5.4239 | 4.8373 | 5.3284 | 0.40607 | -1.1844 | 61.7065 | 0.28526 | 61.624 | -0.033101 | 0.039079 | 61.5891 | 0.003143 | 61.3672 | 61.9383 | 55.4938 | 56.0629 | 66.3242 | 66.8152 | 61.8929 | 60.3024 | 123.1933 | 61.7721 | 123.1108 | 61.4537 | 61.5259 | 123.0759 | 61.49 | 122.8541 | 61.6674 | 61.7034 | 61.5849 | 61.6209
4958.0625 | 123.3765 | -61.4685 | 61.6379 | 0.47896 | -5.9747 | -5.5063 | 4.9152 | 5.4016 | 0.43812 | -1.0974 | 61.7019 | 0.28526 | 61.6423 | -0.028522 | 0.052814 | 61.5845 | -0.001436 | 61.3718 | 61.9475 | 55.4938 | 55.9622 | 66.3837 | 66.8701 | 61.9066 | 60.3711 | 123.1704 | 61.7538 | 123.1108 | 61.44 | 61.5213 | 123.053 | 61.4671 | 122.8403 | 61.6491 | 61.7034 | 61.5895 | 61.6438
4959.0625 | 123.3353 | -61.4319 | 61.7065 | 0.4286 | -6.0708 | -5.5017 | 4.9655 | 5.4291 | 0.39691 | -1.1615 | 61.7019 | 0.27611 | 61.6103 | -0.028522 | 0.048236 | 61.5799 | 0.007721 | 61.3764 | 61.8605 | 55.3611 | 55.9301 | 66.3974 | 66.861 | 61.8288 | 60.2704 | 123.1338 | 61.708 | 123.0422 | 61.4034 | 61.4801 | 123.0118 | 61.4396 | 122.8083 | 61.6537 | 61.6942 | 61.562 | 61.6026
4960.0938 | 123.3215 | -61.4731 | 61.6791 | 0.43318 | -6.1395 | -5.2957 | 4.7137 | 5.3421 | 0.39233 | -1.2851 | 61.7065 | 0.28069 | 61.6377 | -0.03768 | 0.048236 | 61.5845 | 0.003143 | 61.3672 | 61.9063 | 55.3336 | 56.1774 | 66.1868 | 66.8152 | 61.8654 | 60.188 | 123.1796 | 61.7538 | 123.1108 | 61.4354 | 61.5213 | 123.0576 | 61.4762 | 122.8403 | 61.6583 | 61.7034 | 61.5895 | 61.6346
4961.0625 | 123.4177 | -61.4273 | 61.6608 | 0.44692 | -6.0708 | -5.0851 | 4.6954 | 5.5069 | 0.42896 | -1.4636 | 61.7065 | 0.27611 | 61.6423 | -0.023943 | 0.048236 | 61.5799 | 0.007721 | 61.3764 | 61.8742 | 55.3565 | 56.3422 | 66.1227 | 66.9342 | 61.8563 | 59.9637 | 123.1338 | 61.7034 | 123.0696 | 61.4034 | 61.4755 | 123.0072 | 61.435 | 122.8037 | 61.6583 | 61.6988 | 61.5941 | 61.6346
4962.0781 | 123.3032 | -61.4822 | 61.6882 | 0.4927 | -6.0342 | -4.9706 | 4.9152 | 5.6717 | 0.47017 | -1.688 | 61.6928 | 0.28069 | 61.6057 | -0.03768 | 0.052814 | 61.5891 | 0.007721 | 61.381 | 61.9749 | 55.448 | 56.5116 | 66.3974 | 67.154 | 61.9524 | 59.7943 | 123.175 | 61.7629 | 123.0879 | 61.4446 | 61.5351 | 123.0713 | 61.49 | 122.8632 | 61.64 | 61.685 | 61.5529 | 61.598
4963.0625 | 123.3627 | -61.4777 | 61.6562 | 0.41945 | -6.0479 | -5.195 | 5.199 | 5.7999 | 0.38776 | -1.7154 | 61.6973 | 0.28526 | 61.6057 | -0.03768 | 0.043657 | 61.5799 | 0.012299 | 61.3856 | 61.8971 | 55.4297 | 56.2827 | 66.6767 | 67.2776 | 61.8654 | 59.7622 | 123.175 | 61.7629 | 123.0834 | 61.44 | 61.5213 | 123.0576 | 61.49 | 122.8632 | 61.6537 | 61.685 | 61.562 | 61.5934
4964.0781 | 123.3398 | -61.4868 | 61.6425 | 0.4927 | -6.1349 | -4.8836 | 5.2769 | 5.7358 | 0.46101 | -1.6788 | 61.6973 | 0.28069 | 61.6286 | -0.033101 | 0.043657 | 61.5936 | 0.003143 | 61.381 | 61.9795 | 55.3519 | 56.6032 | 66.7637 | 67.2226 | 61.9478 | 59.808 | 123.1842 | 61.7675 | 123.1154 | 61.4537 | 61.5305 | 123.0804 | 61.49 | 122.8678 | 61.6537 | 61.6942 | 61.5849 | 61.6255
4965.0625 | 123.4222 | -61.4456 | 61.5784 | 0.48812 | -6.0617 | -5.2774 | 5.3685 | 5.6443 | 0.46101 | -1.7154 | 61.7065 | 0.28069 | 61.6423 | -0.028522 | 0.048236 | 61.5891 | 0.007721 | 61.3718 | 61.9337 | 55.384 | 56.1682 | 66.8141 | 67.0899 | 61.9066 | 59.7302 | 123.1521 | 61.7263 | 123.0879 | 61.4171 | 61.4939 | 123.0347 | 61.4533 | 122.8174 | 61.6583 | 61.6988 | 61.5941 | 61.6346
4966.1094 | 123.317 | -61.4548 | 61.6562 | 0.54306 | -5.9792 | -4.9935 | 5.1075 | 5.7862 | 0.52511 | -1.688 | 61.6973 | 0.28526 | 61.6149 | -0.033101 | 0.048236 | 61.5891 | 0.007721 | 61.3901 | 61.9978 | 55.4755 | 56.4613 | 66.5622 | 67.241 | 61.9799 | 59.7668 | 123.1521 | 61.74 | 123.0696 | 61.4217 | 61.503 | 123.0438 | 61.4625 | 122.8449 | 61.6491 | 61.6896 | 61.5666 | 61.6071
4967.0625 | 123.2849 | -61.4914 | 61.6516 | 0.56595 | -5.9014 | -4.9706 | 5.2448 | 5.9235 | 0.54342 | -1.5827 | 61.679 | 0.27611 | 61.5874 | -0.023943 | 0.043657 | 61.5982 | 0.007721 | 61.3764 | 62.0573 | 55.59 | 56.5208 | 66.7362 | 67.4149 | 62.0348 | 59.9087 | 123.1704 | 61.7675 | 123.0788 | 61.4675 | 61.5351 | 123.0896 | 61.4991 | 122.8678 | 61.6354 | 61.6713 | 61.5437 | 61.5797
4968.0781 | 123.3856 | -61.4822 | 61.6287 | 0.59342 | -5.9564 | -5.0301 | 5.4234 | 5.951 | 0.548 | -1.427 | 61.6882 | 0.28069 | 61.624 | -0.023943 | 0.039079 | 61.5936 | 0.012299 | 61.3764 | 62.0757 | 55.5259 | 56.4521 | 66.9056 | 67.4332 | 62.0302 | 60.0552 | 123.1704 | 61.7629 | 123.1063 | 61.4583 | 61.5213 | 123.0759 | 61.4945 | 122.8586 | 61.6491 | 61.6759 | 61.5849 | 61.6117
4969.0625 | 123.2986 | -61.4868 | 61.6287 | 0.52017 | -6.0891 | -5.1492 | 5.5195 | 5.8823 | 0.47932 | -1.3126 | 61.6973 | 0.28069 | 61.6332 | -0.033101 | 0.039079 | 61.5891 | 0.007721 | 61.3856 | 62.007 | 55.3977 | 56.3376 | 67.0064 | 67.3691 | 61.9661 | 60.1743 | 123.1842 | 61.7675 | 123.12 | 61.4537 | 61.5259 | 123.0759 | 61.4945 | 122.8724 | 61.6583 | 61.6896 | 61.5941 | 61.6255
4970.0781 | 123.3627 | -61.5051 | 61.6699 | 0.51559 | -6.0891 | -5.3781 | 5.3272 | 5.9785 | 0.47475 | -1.1477 | 61.6836 | 0.28069 | 61.6103 | -0.028522 | 0.048236 | 61.5936 | 0.003143 | 61.381 | 62.0207 | 55.416 | 56.127 | 66.8324 | 67.4836 | 61.9799 | 60.3574 | 123.1887 | 61.7858 | 123.1154 | 61.4766 | 61.5534 | 123.0988 | 61.5083 | 122.8861 | 61.6354 | 61.6805 | 61.562 | 61.6071
4971.0625 | 123.3536 | -61.4777 | 61.6425 | 0.52933 | -6.0113 | -5.3827 | 5.1441 | 6.1021 | 0.4839 | -0.84101 | 61.679 | 0.28984 | 61.592 | -0.028522 | 0.043657 | 61.5982 | 0.007721 | 61.3718 | 62.007 | 55.4664 | 56.095 | 66.6218 | 67.5797 | 61.9616 | 60.6367 | 123.1567 | 61.7675 | 123.0696 | 61.4491 | 61.5213 | 123.0759 | 61.4854 | 122.8495 | 61.6354 | 61.6713 | 61.5483 | 61.5842
4972.0781 | 123.3078 | -61.5051 | 61.6928 | 0.598 | -5.9747 | -5.3323 | 4.8557 | 6.2394 | 0.57089 | -1.1798 | 61.6882 | 0.28069 | 61.6332 | -0.023943 | 0.048236 | 61.5845 | 0.007721 | 61.3764 | 62.1031 | 55.5305 | 56.1728 | 66.3608 | 67.7445 | 62.076 | 60.3253 | 123.1933 | 61.7858 | 123.1383 | 61.4812 | 61.5534 | 123.0896 | 61.5128 | 122.8815 | 61.64 | 61.6805 | 61.5849 | 61.6255
4973.0625 | 123.2712 | -61.5005 | 61.6608 | 0.62089 | -5.8739 | -5.3232 | 4.9243 | 6.3126 | 0.58005 | -1.2851 | 61.6973 | 0.27611 | 61.6332 | -0.033101 | 0.043657 | 61.5936 | 0.003143 | 61.3764 | 62.1214 | 55.6266 | 56.1774 | 66.4249 | 67.8132 | 62.0806 | 60.2155 | 123.1979 | 61.7767 | 123.1337 | 61.4674 | 61.5442 | 123.0942 | 61.5037 | 122.8769 | 61.6537 | 61.6942 | 61.5895 | 61.63
4974.0781 | 123.3353 | -61.4548 | 61.6837 | 0.60258 | -6.0067 | -5.314 | 5.6065 | 6.2623 | 0.55716 | -1.4179 | 61.6928 | 0.28069 | 61.6103 | -0.033101 | 0.048236 | 61.5891 | 0.012299 | 61.3901 | 62.0574 | 55.4481 | 56.1408 | 67.0613 | 67.7171 | 62.0119 | 60.0369 | 123.1475 | 61.7355 | 123.0651 | 61.4217 | 61.503 | 123.0438 | 61.4671 | 122.8449 | 61.6445 | 61.6805 | 61.562 | 61.598
4975.0625 | 123.3444 | -61.4914 | 61.6333 | 0.55222 | -6.0708 | -5.3003 | 5.3181 | 6.2348 | 0.51595 | -1.4499 | 61.6882 | 0.28984 | 61.5965 | -0.033101 | 0.043657 | 61.5982 | 0.007721 | 61.381 | 62.0436 | 55.4206 | 56.1911 | 66.8095 | 67.7262 | 62.0073 | 60.0415 | 123.1796 | 61.7812 | 123.0879 | 61.4583 | 61.5351 | 123.0896 | 61.4991 | 122.8724 | 61.6445 | 61.6805 | 61.5529 | 61.5888
4976.0938 | 123.2758 | -61.5051 | 61.6928 | 0.53391 | -6.1212 | -5.1629 | 5.5836 | 6.2302 | 0.48848 | -1.4591 | 61.6882 | 0.28069 | 61.624 | -0.028522 | 0.048236 | 61.5936 | 0.012299 | 61.3993 | 62.039 | 55.3839 | 56.3422 | 67.0888 | 67.7354 | 61.9936 | 60.0461 | 123.1933 | 61.7858 | 123.1291 | 61.4766 | 61.5534 | 123.0988 | 61.5174 | 122.9044 | 61.64 | 61.6759 | 61.5758 | 61.6117
4977.0625 | 123.2666 | -61.496 | 61.6516 | 0.53848 | -6.0617 | -5.108 | 5.0388 | 6.2486 | 0.51595 | -1.4316 | 61.6882 | 0.28069 | 61.6286 | -0.028522 | 0.043657 | 61.5936 | 0.003143 | 61.3856 | 62.0345 | 55.4343 | 56.388 | 66.5348 | 67.7445 | 62.0119 | 60.0644 | 123.1842 | 61.7767 | 123.1246 | 61.4674 | 61.5396 | 123.0896 | 61.4991 | 122.8815 | 61.6445 | 61.685 | 61.5849 | 61.6255
4978.0938 | 123.3032 | -61.5097 | 61.647 | 0.55222 | -6.0479 | -5.0118 | 4.6267 | 6.2165 | 0.51595 | -1.3767 | 61.6928 | 0.27611 | 61.6103 | -0.042259 | 0.048236 | 61.5845 | 0.003143 | 61.3993 | 62.0619 | 55.4618 | 56.4979 | 66.1364 | 67.7262 | 62.0257 | 60.1331 | 123.2025 | 61.7858 | 123.12 | 61.4674 | 61.5579 | 123.0942 | 61.5128 | 122.909 | 61.6445 | 61.6896 | 61.562 | 61.6071
4979.0625 | 123.2666 | -61.5005 | 61.6562 | 0.52933 | -5.9243 | -5.2911 | 4.2559 | 6.2898 | 0.49306 | -1.4545 | 61.6882 | 0.28069 | 61.6057 | -0.03768 | 0.043657 | 61.5845 | 0.003143 | 61.3901 | 62.0299 | 55.5762 | 56.2094 | 65.7564 | 67.7903 | 61.9936 | 60.0461 | 123.1887 | 61.7812 | 123.1063 | 61.4629 | 61.5442 | 123.085 | 61.5037 | 122.8907 | 61.6445 | 61.685 | 61.562 | 61.6026
4980.0938 | 123.3307 | -61.4685 | 61.6653 | 0.51101 | -5.9518 | -5.2133 | 4.5993 | 6.3126 | 0.47475 | -1.5323 | 61.6928 | 0.28069 | 61.6286 | -0.028522 | 0.048236 | 61.5891 | 0.007721 | 61.3901 | 61.9795 | 55.5167 | 56.2552 | 66.0678 | 67.7812 | 61.9433 | 59.9362 | 123.1613 | 61.7492 | 123.0971 | 61.44 | 61.5167 | 123.0576 | 61.4762 | 122.8586 | 61.6445 | 61.685 | 61.5804 | 61.6209
4981.0625 | 123.2986 | -61.5143 | 61.6379 | 0.57969 | -5.6908 | -4.9111 | 5.4325 | 6.4637 | 0.53426 | -1.4316 | 61.6882 | 0.28526 | 61.6194 | -0.033101 | 0.043657 | 61.6074 | 0.003143 | 61.4039 | 62.094 | 55.8235 | 56.6032 | 66.9468 | 67.978 | 62.0485 | 60.0827 | 123.2025 | 61.7995 | 123.1337 | 61.4812 | 61.5579 | 123.1216 | 61.5174 | 122.9181 | 61.6445 | 61.685 | 61.5758 | 61.6163
4982.0781 | 123.3398 | -61.4685 | 61.6745 | 0.48354 | -5.9472 | -5.2041 | 5.6661 | 6.3905 | 0.43354 | -1.4316 | 61.6882 | 0.28069 | 61.6057 | -0.023943 | 0.048236 | 61.5891 | 0.012299 | 61.3993 | 61.952 | 55.5213 | 56.2644 | 67.1346 | 67.859 | 61.902 | 60.0369 | 123.1567 | 61.7492 | 123.0742 | 61.4446 | 61.5167 | 123.0576 | 61.4808 | 122.8678 | 61.64 | 61.6759 | 61.5575 | 61.5934
4983.0625 | 123.262 | -61.5051 | 61.6562 | 0.66668 | -5.6679 | -5.1034 | 5.4325 | 6.6514 | 0.61668 | -1.3675 | 61.6699 | 0.28069 | 61.5828 | -0.033101 | 0.043657 | 61.5982 | 0.003143 | 61.3901 | 62.1718 | 55.8372 | 56.4017 | 66.9377 | 68.1565 | 62.1218 | 60.1376 | 123.175 | 61.7858 | 123.0879 | 61.472 | 61.5488 | 123.1033 | 61.5083 | 122.8953 | 61.6262 | 61.6667 | 61.5392 | 61.5797
4984.0781 | 123.3444 | -61.4777 | 61.6928 | 0.61632 | -5.9609 | -4.9203 | 5.1304 | 6.5782 | 0.57089 | -1.482 | 61.679 | 0.27611 | 61.624 | -0.033101 | 0.043657 | 61.5891 | 0.003143 | 61.381 | 62.094 | 55.5167 | 56.5574 | 66.608 | 68.0558 | 62.0486 | 59.9957 | 123.1567 | 61.7538 | 123.1017 | 61.4446 | 61.5213 | 123.0667 | 61.4808 | 122.8586 | 61.6354 | 61.6759 | 61.5804 | 61.6209
4985.0625 | 123.3261 | -61.5005 | 61.6791 | 0.63463 | -5.9976 | -4.5402 | 4.9701 | 6.537 | 0.58921 | -1.5644 | 61.6882 | 0.27153 | 61.6286 | -0.028522 | 0.048236 | 61.6028 | 0.012299 | 61.3856 | 62.1352 | 55.503 | 56.9603 | 66.4707 | 68.0375 | 62.0898 | 59.9362 | 123.1887 | 61.7721 | 123.1291 | 61.472 | 61.5488 | 123.1033 | 61.5128 | 122.8861 | 61.64 | 61.6759 | 61.5804 | 61.6163
4986.0938 | 123.2712 | -61.5143 | 61.6974 | 0.61632 | -5.732 | -4.2747 | 4.7778 | 6.6835 | 0.57089 | -1.5094 | 61.6836 | 0.28069 | 61.592 | -0.033101 | 0.043657 | 61.6074 | 0.007721 | 61.3947 | 62.1306 | 55.7823 | 57.2396 | 66.2921 | 68.1977 | 62.0852 | 60.0049 | 123.1979 | 61.795 | 123.1062 | 61.4812 | 61.5579 | 123.1216 | 61.522 | 122.909 | 61.64 | 61.6759 | 61.5483 | 61.5842
4987.0625 | 123.2941 | -61.4868 | 61.6608 | 0.55222 | -5.8556 | -4.3159 | 4.3612 | 6.6743 | 0.50679 | -1.4636 | 61.679 | 0.28069 | 61.592 | -0.028522 | 0.048236 | 61.5982 | 0.012299 | 61.3764 | 62.039 | 55.6312 | 57.1709 | 65.848 | 68.1611 | 61.9936 | 60.0232 | 123.1658 | 61.7675 | 123.0788 | 61.4583 | 61.5351 | 123.085 | 61.4991 | 122.8632 | 61.6308 | 61.6667 | 61.5437 | 61.5797
4988.0781 | 123.4497 | -61.441 | 61.6333 | 0.51101 | -5.8602 | -4.9477 | 4.1277 | 6.7063 | 0.47017 | -1.3675 | 61.6928 | 0.28984 | 61.6286 | -0.033101 | 0.052814 | 61.5891 | 0.012299 | 61.3672 | 61.9521 | 55.5808 | 56.4933 | 65.5687 | 68.1474 | 61.9112 | 60.0735 | 123.1338 | 61.7309 | 123.0696 | 61.4079 | 61.4939 | 123.0301 | 61.4533 | 122.8083 | 61.64 | 61.6805 | 61.5758 | 61.6163
4989.0625 | 123.3215 | -61.5005 | 61.6882 | 0.43318 | -5.9426 | -5.0439 | 4.0819 | 6.6331 | 0.39691 | -1.3904 | 61.6928 | 0.28526 | 61.624 | -0.028522 | 0.048236 | 61.5891 | 0.007721 | 61.3764 | 61.9337 | 55.5579 | 56.4567 | 65.5824 | 68.1337 | 61.8975 | 60.1102 | 123.1933 | 61.7858 | 123.1246 | 61.472 | 61.5488 | 123.0896 | 61.5083 | 122.8769 | 61.6445 | 61.685 | 61.5758 | 61.6163
4990.0781 | 123.3765 | -61.4273 | 61.6562 | 0.39198 | -6.08 | -5.2362 | 3.6973 | 6.5644 | 0.34655 | -1.3904 | 61.7019 | 0.28069 | 61.6103 | -0.028522 | 0.048236 | 61.5799 | 0.012299 | 61.3627 | 61.8193 | 55.3473 | 56.1911 | 65.1246 | 67.9917 | 61.7739 | 60.0369 | 123.1292 | 61.708 | 123.0376 | 61.3988 | 61.4755 | 123.0072 | 61.4396 | 122.79 | 61.6537 | 61.6896 | 61.562 | 61.598
4991.0625 | 123.2803 | -61.4914 | 61.6974 | 0.39655 | -6.1899 | -5.0714 | 3.0609 | 6.4637 | 0.35571 | -1.3767 | 61.7157 | 0.28526 | 61.6515 | -0.023943 | 0.043657 | 61.5707 | 0.003143 | 61.3581 | 61.8879 | 55.3015 | 56.42 | 64.5523 | 67.9551 | 61.8471 | 60.1147 | 123.2071 | 61.7767 | 123.1429 | 61.4675 | 61.5351 | 123.0621 | 61.4945 | 122.8495 | 61.672 | 61.7125 | 61.6078 | 61.6483
4992.0781 | 123.3719 | -61.4365 | 61.6928 | 0.39198 | -6.1945 | -5.195 | 2.5344 | 6.3813 | 0.34655 | -1.2851 | 61.7111 | 0.28526 | 61.6377 | -0.033101 | 0.06197 | 61.5707 | 0.003143 | 61.3627 | 61.8284 | 55.242 | 56.2415 | 63.9708 | 67.8178 | 61.783 | 60.1514 | 123.1475 | 61.7217 | 123.0742 | 61.4034 | 61.4984 | 123.0072 | 61.4396 | 122.7991 | 61.6491 | 61.7079 | 61.5758 | 61.6346
4993.0625 | 123.3124 | -61.4502 | 61.7157 | 0.34619 | -6.3639 | -4.7234 | 2.7724 | 6.2486 | 0.30992 | -1.2851 | 61.7111 | 0.28069 | 61.6194 | -0.03768 | 0.048236 | 61.5753 | 0.007721 | 61.3581 | 61.7964 | 55.0863 | 56.7268 | 64.2226 | 67.6988 | 61.7601 | 60.1651 | 123.1613 | 61.7309 | 123.0696 | 61.4125 | 61.4984 | 123.0255 | 61.4579 | 122.8083 | 61.6628 | 61.7034 | 61.5712 | 61.6117
4994.0781 | 123.3856 | -61.4685 | 61.6928 | 0.23631 | -6.4692 | -4.8058 | 2.3741 | 5.9281 | 0.18631 | -1.34 | 61.7202 | 0.28069 | 61.6561 | -0.028522 | 0.052814 | 61.5662 | -0.001436 | 61.3398 | 61.7048 | 54.9993 | 56.6627 | 63.8426 | 67.3966 | 61.6548 | 60.1285 | 123.1887 | 61.7492 | 123.1246 | 61.44 | 61.5213 | 123.0347 | 61.4671 | 122.8083 | 61.6674 | 61.7217 | 61.6032 | 61.6575
4995.0625 | 123.3398 | -61.4548 | 61.6791 | 0.35993 | -6.3456 | -5.3781 | 2.5435 | 6.3218 | 0.32366 | -0.96004 | 61.7248 | 0.28526 | 61.6561 | -0.028522 | 0.048236 | 61.5753 | 0.007721 | 61.3535 | 61.8147 | 55.1092 | 56.0767 | 63.9983 | 67.7766 | 61.7784 | 60.4947 | 123.1796 | 61.74 | 123.1108 | 61.4263 | 61.503 | 123.0301 | 61.4625 | 122.8083 | 61.6766 | 61.7171 | 61.6078 | 61.6483
4996.0938 | 123.3948 | -61.4319 | 61.6653 | 0.43318 | -6.2357 | -5.6116 | 2.6855 | 6.4042 | 0.39233 | -0.95088 | 61.7157 | 0.28526 | 61.6377 | -0.033101 | 0.048236 | 61.5753 | 0.012299 | 61.3581 | 61.8651 | 55.1962 | 55.8203 | 64.1173 | 67.8361 | 61.8242 | 60.481 | 123.1475 | 61.7171 | 123.0696 | 61.3988 | 61.4801 | 123.0072 | 61.4442 | 122.79 | 61.6674 | 61.7034 | 61.5895 | 61.6255
4997.0625 | 123.2986 | -61.4502 | 61.7065 | 0.47439 | -5.9472 | -5.5979 | 2.6992 | 6.363 | 0.43354 | -0.98751 | 61.7019 | 0.28069 | 61.6194 | -0.028522 | 0.043657 | 61.5753 | 0.012299 | 61.3718 | 61.9246 | 55.503 | 55.8523 | 64.1494 | 67.8132 | 61.8837 | 60.4627 | 123.1521 | 61.7309 | 123.0696 | 61.4217 | 61.4939 | 123.0255 | 61.4625 | 122.822 | 61.6583 | 61.6896 | 61.5758 | 61.6071
4998.0938 | 123.2895 | -61.4456 | 61.7065 | 0.52933 | -5.8922 | -5.488 | 2.0582 | 6.45 | 0.47932 | -1.1065 | 61.7111 | 0.28526 | 61.6469 | -0.023943 | 0.048236 | 61.5662 | 0.007721 | 61.3627 | 61.9749 | 55.5534 | 55.9576 | 63.5038 | 67.8956 | 61.9249 | 60.3391 | 123.1567 | 61.7309 | 123.0925 | 61.4217 | 61.4939 | 123.0118 | 61.4533 | 122.8083 | 61.6628 | 61.7034 | 61.5987 | 61.6392
4999.0625 | 123.317 | -61.4319 | 61.7203 | 0.55222 | -5.8465 | -5.6025 | 1.8384 | 6.4363 | 0.49764 | -1.1935 | 61.7202 | 0.28526 | 61.6561 | -0.033101 | 0.048236 | 61.5662 | 0.012299 | 61.3581 | 61.9841 | 55.5854 | 55.8294 | 63.2703 | 67.8681 | 61.9295 | 60.2384 | 123.1521 | 61.7171 | 123.0879 | 61.3988 | 61.4801 | 122.998 | 61.4442 | 122.79 | 61.672 | 61.7079 | 61.6078 | 61.6438
5000.0781 | 123.436 | -61.4136 | 61.6882 | 0.48354 | -6.1716 | -5.5613 | 2.4336 | 6.2669 | 0.4427 | -1.2851 | 61.7202 | 0.28526 | 61.624 | -0.028522 | 0.048236 | 61.5662 | 0.007721 | 61.3581 | 61.8971 | 55.242 | 55.8523 | 63.8472 | 67.6804 | 61.8563 | 60.1285 | 123.1338 | 61.6988 | 123.0376 | 61.3851 | 61.4618 | 122.9797 | 61.4213 | 122.7717 | 61.672 | 61.7125 | 61.5758 | 61.6163
5001.0625 | 123.4268 | -61.4548 | 61.6516 | 0.45149 | -6.4097 | -4.9798 | 3.4363 | 6.3813 | 0.40607 | -1.3538 | 61.7019 | 0.28526 | 61.6286 | -0.033101 | 0.043657 | 61.5753 | 0.003143 | 61.3627 | 61.9063 | 55.0451 | 56.475 | 64.8911 | 67.8361 | 61.8608 | 60.101 | 123.1567 | 61.74 | 123.0834 | 61.4217 | 61.4984 | 123.0301 | 61.4579 | 122.8174 | 61.6583 | 61.6988 | 61.5849 | 61.6255
5002.0938 | 123.3032 | -61.4227 | 61.6425 | 0.4927 | -6.2448 | -4.6501 | 3.4638 | 6.4729 | 0.44728 | -1.3171 | 61.7019 | 0.27611 | 61.6377 | -0.023943 | 0.048236 | 61.5845 | 0.003143 | 61.3718 | 61.9154 | 55.1779 | 56.7726 | 64.8865 | 67.8956 | 61.87 | 60.1056 | 123.1247 | 61.6988 | 123.0605 | 61.3988 | 61.471 | 123.0072 | 61.4259 | 122.7945 | 61.6537 | 61.6988 | 61.5895 | 61.6346
5003.0625 | 123.3307 | -61.4868 | 61.6974 | 0.52017 | -6.2219 | -4.6593 | 3.6012 | 6.5507 | 0.47932 | -1.1981 | 61.7065 | 0.28526 | 61.6286 | -0.033101 | 0.043657 | 61.5845 | 0.012299 | 61.381 | 62.007 | 55.2649 | 56.8275 | 65.088 | 68.0375 | 61.9661 | 60.2887 | 123.1933 | 61.7721 | 123.1154 | 61.4537 | 61.5305 | 123.0713 | 61.4991 | 122.8678 | 61.6628 | 61.6942 | 61.5849 | 61.6163
5004.0781 | 123.4085 | -61.4777 | 61.6379 | 0.4286 | -6.4646 | -4.815 | 3.9079 | 6.537 | 0.38776 | -1.221 | 61.6882 | 0.28069 | 61.6011 | -0.028522 | 0.048236 | 61.5845 | 0.012299 | 61.3718 | 61.9063 | 55.0131 | 56.6627 | 65.3856 | 68.0146 | 61.8654 | 60.2567 | 123.1659 | 61.7583 | 123.0788 | 61.4491 | 61.5259 | 123.0621 | 61.49 | 122.8495 | 61.64 | 61.6759 | 61.5529 | 61.5888
5005.0625 | 123.2849 | -61.4822 | 61.702 | 0.4286 | -6.428 | -5.0027 | 3.8759 | 6.6194 | 0.39233 | -1.2073 | 61.6973 | 0.28526 | 61.6332 | -0.028522 | 0.043657 | 61.5845 | 0.016878 | 61.3672 | 61.9108 | 55.0543 | 56.4796 | 65.3581 | 68.1016 | 61.8746 | 60.275 | 123.1796 | 61.7675 | 123.1154 | 61.4537 | 61.5259 | 123.0667 | 61.4991 | 122.8495 | 61.6537 | 61.6805 | 61.5895 | 61.6163
5006.1094 | 123.349 | -61.4182 | 61.7065 | 0.51559 | -6.1303 | -5.14 | 3.624 | 6.5187 | 0.47017 | -1.1706 | 61.7019 | 0.27153 | 61.6469 | -0.028522 | 0.048236 | 61.5936 | 0.007721 | 61.3764 | 61.9337 | 55.2878 | 56.2781 | 65.0422 | 67.9368 | 61.8883 | 60.2475 | 123.1201 | 61.6897 | 123.0651 | 61.3896 | 61.4664 | 123.0118 | 61.4259 | 122.7945 | 61.6537 | 61.6942 | 61.5987 | 61.6392
5007.0625 | 123.317 | -61.4548 | 61.7203 | 0.39655 | -6.3868 | -5.6528 | 4.0132 | 6.4225 | 0.36029 | -1.1569 | 61.6928 | 0.28984 | 61.6423 | -0.028522 | 0.048236 | 61.5799 | 0.012299 | 61.3764 | 61.8513 | 55.068 | 55.8019 | 65.468 | 67.8773 | 61.8151 | 60.2979 | 123.1475 | 61.7446 | 123.0971 | 61.4263 | 61.503 | 123.0347 | 61.4671 | 122.8312 | 61.6445 | 61.6805 | 61.5941 | 61.63
5008.0938 | 123.4131 | -61.4456 | 61.6516 | 0.42402 | -6.3639 | -5.8131 | 3.7522 | 6.6102 | 0.40149 | -1.1706 | 61.7019 | 0.28526 | 61.6103 | -0.033101 | 0.052814 | 61.5753 | 0.007721 | 61.3627 | 61.8696 | 55.0818 | 55.6325 | 65.1979 | 68.0558 | 61.8471 | 60.275 | 123.1475 | 61.7309 | 123.0559 | 61.4125 | 61.4984 | 123.0209 | 61.4533 | 122.8083 | 61.6491 | 61.6942 | 61.5575 | 61.6026
5009.0625 | 123.3078 | -61.4319 | 61.7432 | 0.12185 | -6.3776 | -5.8497 | 2.9968 | 6.5644 | 0.85475 | -1.2942 | 61.7111 | 0.28526 | 61.6469 | -0.028522 | 0.052814 | 61.5707 | 0.016878 | 61.3535 | 61.5537 | 55.0543 | 55.5822 | 64.4287 | 67.9963 | 62.2866 | 60.1376 | 123.143 | 61.7171 | 123.0788 | 61.4034 | 61.4847 | 123.0026 | 61.4488 | 122.7854 | 61.6583 | 61.6942 | 61.5941 | 61.63
5010.0938 | 123.2437 | -61.4365 | 61.7294 | 0.45607 | -6.4325 | -6.0145 | 3.6927 | 6.7292 | 0.41065 | -1.3034 | 61.7111 | 0.28069 | 61.6561 | -0.028522 | 0.048236 | 61.5753 | 0.012299 | 61.3627 | 61.8925 | 55.0039 | 55.4219 | 65.1292 | 68.1657 | 61.8471 | 60.1331 | 123.1475 | 61.7171 | 123.0925 | 61.4079 | 61.4847 | 123.0118 | 61.4488 | 122.7991 | 61.6628 | 61.6988 | 61.6078 | 61.6438
5011.0625 | 123.3261 | -61.4456 | 61.6974 | 0.47896 | -6.4554 | -6.1702 | 3.7065 | 6.656 | 0.44728 | -1.0974 | 61.7157 | 0.28069 | 61.6377 | -0.023943 | 0.039079 | 61.5753 | 0.007721 | 61.3627 | 61.9246 | 54.9902 | 55.2754 | 65.1521 | 68.1016 | 61.8929 | 60.3482 | 123.1613 | 61.7263 | 123.0834 | 61.4217 | 61.4847 | 123.0209 | 61.4533 | 122.8083 | 61.6766 | 61.7079 | 61.5987 | 61.63
5012.0938 | 123.4222 | -61.4456 | 61.6562 | 0.48812 | -6.4509 | -5.9917 | 3.8301 | 6.7796 | 0.4427 | -1.0058 | 61.7065 | 0.28069 | 61.6149 | -0.033101 | 0.048236 | 61.5799 | 0.007721 | 61.3718 | 61.9337 | 54.9948 | 55.454 | 65.2757 | 68.2252 | 61.8883 | 60.4398 | 123.1521 | 61.7263 | 123.0605 | 61.4125 | 61.4939 | 123.0255 | 61.4533 | 122.8174 | 61.6583 | 61.6988 | 61.5666 | 61.6071
5013.0625 | 123.3948 | -61.4731 | 61.6837 | 0.52933 | -5.906 | -6.0329 | 3.7614 | 6.8849 | 0.49306 | -0.85932 | 61.7065 | 0.28069 | 61.6377 | -0.028522 | 0.048236 | 61.5845 | 0.012299 | 61.3718 | 62.0024 | 55.5671 | 55.4402 | 65.2345 | 68.358 | 61.9661 | 60.6138 | 123.1796 | 61.7538 | 123.1108 | 61.4446 | 61.5213 | 123.0576 | 61.4854 | 122.8449 | 61.6583 | 61.6942 | 61.5895 | 61.6255
5014.0781 | 123.3398 | -61.4731 | 61.647 | 0.60258 | -5.8831 | -5.9321 | 3.2852 | 6.8803 | 0.55716 | -0.79065 | 61.6973 | 0.28984 | 61.6286 | -0.03768 | 0.048236 | 61.5845 | 0.007721 | 61.3672 | 62.0757 | 55.59 | 55.541 | 64.7583 | 68.3534 | 62.0302 | 60.6824 | 123.1704 | 61.7629 | 123.1017 | 61.4354 | 61.5213 | 123.0576 | 61.4808 | 122.8403 | 61.6491 | 61.6896 | 61.5804 | 61.6209
5015.0625 | 123.3078 | -61.5051 | 61.6837 | 0.61174 | -6.0754 | -5.9413 | 3.0059 | 6.9032 | 0.57089 | -0.81354 | 61.6973 | 0.28069 | 61.6194 | -0.033101 | 0.048236 | 61.5799 | 0.007721 | 61.3627 | 62.1169 | 55.4297 | 55.5638 | 64.5111 | 68.4083 | 62.076 | 60.6916 | 123.2025 | 61.7858 | 123.1246 | 61.472 | 61.5534 | 123.085 | 61.5128 | 122.8678 | 61.6491 | 61.6896 | 61.5712 | 61.6117
5016.1094 | 123.4818 | -61.4594 | 61.6333 | 0.58427 | -6.1029 | -6.01 | 2.777 | 6.9124 | 0.548 | -0.70366 | 61.7019 | 0.28069 | 61.6377 | -0.023943 | 0.043657 | 61.5799 | 0.003143 | 61.3581 | 62.0436 | 55.3565 | 55.4494 | 64.2364 | 68.3717 | 62.0074 | 60.7557 | 123.1613 | 61.74 | 123.0971 | 61.4354 | 61.503 | 123.0392 | 61.4625 | 122.8174 | 61.6583 | 61.6988 | 61.5941 | 61.6346
5017.0625 | 123.4406 | -61.4777 | 61.6379 | 0.64837 | -5.7961 | -5.8818 | 2.136 | 6.8803 | 0.6121 | -0.77233 | 61.7019 | 0.27611 | 61.6194 | -0.033101 | 0.048236 | 61.5707 | 0.012299 | 61.3627 | 62.126 | 55.6816 | 55.5959 | 63.6137 | 68.358 | 62.0898 | 60.7053 | 123.1796 | 61.7538 | 123.0971 | 61.4446 | 61.5259 | 123.0484 | 61.49 | 122.8403 | 61.6537 | 61.6896 | 61.5712 | 61.6071
5018.0781 | 123.3948 | -61.4456 | 61.6425 | 0.75367 | -5.4802 | -5.7902 | 1.7514 | 6.9169 | 0.69909 | -0.74029 | 61.7019 | 0.28526 | 61.6423 | -0.03768 | 0.048236 | 61.5753 | 0.007721 | 61.3581 | 62.1993 | 55.9655 | 55.6554 | 63.1971 | 68.3626 | 62.1447 | 60.7053 | 123.1475 | 61.7309 | 123.0879 | 61.4079 | 61.4939 | 123.0209 | 61.4533 | 122.8037 | 61.6537 | 61.6942 | 61.5941 | 61.6346
5019.0625 | 123.436 | -61.4227 | 61.6608 | 0.72162 | -5.6038 | -5.9276 | 2.4291 | 6.9444 | 0.68993 | -0.80896 | 61.7111 | 0.28069 | 61.6332 | -0.028522 | 0.052814 | 61.5891 | 0.012299 | 61.3535 | 62.1443 | 55.8189 | 55.4952 | 63.8518 | 68.3671 | 62.1127 | 60.6138 | 123.1338 | 61.7034 | 123.0559 | 61.3942 | 61.4755 | 123.0118 | 61.435 | 122.7762 | 61.6583 | 61.6988 | 61.5804 | 61.6209
5020.0938 | 123.3078 | -61.4868 | 61.6974 | 0.63921 | -5.6496 | -5.7856 | 3.244 | 6.8208 | 0.59378 | -0.92341 | 61.6973 | 0.28069 | 61.6057 | -0.028522 | 0.048236 | 61.5891 | 0.007721 | 61.3672 | 62.126 | 55.8372 | 55.7012 | 64.7308 | 68.3076 | 62.0806 | 60.5634 | 123.1842 | 61.7675 | 123.0925 | 61.4583 | 61.5351 | 123.0759 | 61.4945 | 122.8541 | 61.6491 | 61.6896 | 61.5575 | 61.598
5021.0625 | 123.2758 | -61.4685 | 61.6928 | 0.59342 | -5.8831 | -5.9047 | 3.4775 | 7.0772 | 0.55258 | -1.0653 | 61.7019 | 0.28069 | 61.6377 | -0.033101 | 0.052814 | 61.5799 | 0.012299 | 61.3627 | 62.0619 | 55.5854 | 55.5638 | 64.946 | 68.5457 | 62.0211 | 60.4032 | 123.1704 | 61.7492 | 123.1063 | 61.4354 | 61.5213 | 123.0484 | 61.4808 | 122.8312 | 61.6491 | 61.6896 | 61.5849 | 61.6255
5022.0781 | 123.4314 | -61.4456 | 61.6379 | 0.62089 | -5.8694 | -5.8589 | 2.9327 | 7.0909 | 0.57547 | -1.221 | 61.7019 | 0.27611 | 61.6149 | -0.042259 | 0.043657 | 61.5753 | -0.001436 | 61.3627 | 62.0665 | 55.5763 | 55.5867 | 64.3783 | 68.5365 | 62.0211 | 60.2246 | 123.1475 | 61.7217 | 123.0605 | 61.4034 | 61.4893 | 123.0209 | 61.4442 | 122.8083 | 61.6583 | 61.7034 | 61.5712 | 61.6163
5023.0625 | 123.3856 | -61.4594 | 61.6608 | 0.60716 | -5.8098 | -5.9184 | 2.8274 | 6.9124 | 0.56173 | -1.2668 | 61.7019 | 0.28526 | 61.6194 | -0.028522 | 0.043657 | 61.5753 | 0.007721 | 61.3718 | 62.0665 | 55.6495 | 55.541 | 64.2867 | 68.3717 | 62.0211 | 60.1926 | 123.1613 | 61.7446 | 123.0788 | 61.4308 | 61.503 | 123.0347 | 61.4671 | 122.8312 | 61.6583 | 61.6942 | 61.5758 | 61.6117
5024.0781 | 123.3261 | -61.4731 | 61.6516 | 0.58427 | -5.8922 | -5.8955 | 3.3173 | 6.9948 | 0.54342 | -0.98293 | 61.7019 | 0.28526 | 61.6469 | -0.03768 | 0.043657 | 61.5845 | 0.007721 | 61.3672 | 62.0574 | 55.5808 | 55.5776 | 64.7904 | 68.4678 | 62.0165 | 60.4902 | 123.175 | 61.7583 | 123.12 | 61.4354 | 61.5167 | 123.0576 | 61.4808 | 122.8403 | 61.6583 | 61.6942 | 61.6032 | 61.6392
5025.0625 | 123.3902 | -61.4456 | 61.647 | 0.53391 | -5.9472 | -5.9459 | 3.6515 | 6.9352 | 0.53426 | -0.87763 | 61.6928 | 0.27611 | 61.6057 | -0.028522 | 0.048236 | 61.5845 | -0.001436 | 61.3901 | 61.9795 | 55.4984 | 55.4998 | 65.0971 | 68.3809 | 61.9799 | 60.568 | 123.1384 | 61.7217 | 123.0513 | 61.4171 | 61.4939 | 123.0301 | 61.4442 | 122.8357 | 61.6445 | 61.6942 | 61.5575 | 61.6071
5026.0938 | 123.4131 | -61.496 | 61.702 | 0.4927 | -6.1166 | -5.9733 | 3.8484 | 7.0314 | 0.45185 | -0.8639 | 61.6928 | 0.28984 | 61.6286 | -0.03768 | 0.048236 | 61.5799 | 0.007721 | 61.3764 | 61.9887 | 55.3794 | 55.5226 | 65.3444 | 68.5274 | 61.9478 | 60.6321 | 123.1887 | 61.7858 | 123.1246 | 61.4583 | 61.5442 | 123.0759 | 61.5037 | 122.8724 | 61.6445 | 61.685 | 61.5804 | 61.6209
5027.0625 | 123.3627 | -61.4777 | 61.6608 | 0.55222 | -6.1212 | -5.9367 | 3.2074 | 7.1504 | 0.49764 | -0.84559 | 61.7065 | 0.28069 | 61.6423 | -0.033101 | 0.048236 | 61.5753 | -0.001436 | 61.3764 | 62.0299 | 55.3565 | 55.5409 | 64.6851 | 68.6281 | 61.9753 | 60.6321 | 123.1842 | 61.7583 | 123.12 | 61.4446 | 61.5259 | 123.053 | 61.4762 | 122.8541 | 61.6583 | 61.7079 | 61.5941 | 61.6438
5028.0938 | 123.3994 | -61.496 | 61.6333 | 0.57511 | -5.9838 | -5.9184 | 3.1158 | 7.1138 | 0.53884 | -0.81812 | 61.6928 | 0.28526 | 61.6103 | -0.033101 | 0.043657 | 61.5845 | 0.007721 | 61.3764 | 62.0711 | 55.5121 | 55.5776 | 64.6118 | 68.6098 | 62.0348 | 60.6779 | 123.1887 | 61.7812 | 123.1063 | 61.4629 | 61.5396 | 123.0804 | 61.5037 | 122.8724 | 61.6491 | 61.685 | 61.5666 | 61.6026
5029.0625 | 123.3719 | -61.4777 | 61.6333 | 0.64379 | -5.7824 | -5.7994 | 3.386 | 7.2374 | 0.6121 | -0.99209 | 61.6973 | 0.28069 | 61.6194 | -0.033101 | 0.048236 | 61.5891 | 0.003143 | 61.3901 | 62.1214 | 55.6953 | 55.6783 | 64.8636 | 68.7151 | 62.0898 | 60.4856 | 123.175 | 61.7583 | 123.0971 | 61.4446 | 61.5259 | 123.0667 | 61.4808 | 122.8678 | 61.6491 | 61.6942 | 61.5712 | 61.6163
5030.0938 | 123.4131 | -61.4456 | 61.6379 | 0.55222 | -6.0846 | -5.8909 | 3.8484 | 7.1596 | 0.50222 | -1.102 | 61.7019 | 0.28526 | 61.6377 | -0.033101 | 0.048236 | 61.5845 | -0.001436 | 61.3856 | 61.9978 | 55.3611 | 55.5547 | 65.294 | 68.6052 | 61.9478 | 60.3437 | 123.1475 | 61.7309 | 123.0834 | 61.4125 | 61.4939 | 123.0301 | 61.4442 | 122.8312 | 61.6537 | 61.7034 | 61.5895 | 61.6392
5031.0625 | 123.349 | -61.4777 | 61.647 | 0.51101 | -6.2677 | -5.8131 | 4.32 | 7.0909 | 0.47932 | -1.1706 | 61.6973 | 0.28069 | 61.6286 | -0.028522 | 0.043657 | 61.5845 | 0.003143 | 61.3901 | 61.9887 | 55.2099 | 55.6646 | 65.7976 | 68.5686 | 61.957 | 60.307 | 123.175 | 61.7583 | 123.1063 | 61.4491 | 61.5213 | 123.0621 | 61.4808 | 122.8678 | 61.6537 | 61.6942 | 61.5849 | 61.6255
5032.0781 | 123.3948 | -61.4777 | 61.5875 | 0.62089 | -5.8281 | -5.5796 | 4.4024 | 7.3564 | 0.59378 | -1.1706 | 61.6836 | 0.27611 | 61.5874 | -0.033101 | 0.043657 | 61.5982 | 0.007721 | 61.3856 | 62.0986 | 55.6495 | 55.8981 | 65.88 | 68.8341 | 62.0714 | 60.307 | 123.1613 | 61.7538 | 123.065 | 61.4446 | 61.5213 | 123.0759 | 61.4854 | 122.8632 | 61.64 | 61.6759 | 61.5437 | 61.5797
5033.0625 | 123.3536 | -61.5097 | 61.6333 | 0.60716 | -5.938 | -5.6437 | 4.1231 | 7.3702 | 0.57089 | -1.0837 | 61.6973 | 0.28526 | 61.624 | -0.033101 | 0.043657 | 61.5891 | 0.007721 | 61.3856 | 62.1169 | 55.5717 | 55.866 | 65.6328 | 68.8799 | 62.0806 | 60.4261 | 123.2071 | 61.795 | 123.1337 | 61.4766 | 61.5534 | 123.0988 | 61.5174 | 122.8953 | 61.6537 | 61.6896 | 61.5804 | 61.6163
5034.0938 | 123.3124 | -61.5417 | 61.6516 | 0.59342 | -6.0754 | -5.6895 | 4.0361 | 7.4709 | 0.55716 | -1.0287 | 61.6836 | 0.28526 | 61.6194 | -0.03768 | 0.048236 | 61.5936 | 0.007721 | 61.3764 | 62.1352 | 55.4663 | 55.8523 | 65.5779 | 69.0126 | 62.0989 | 60.513 | 123.2254 | 61.827 | 123.1612 | 61.5041 | 61.59 | 123.1354 | 61.5495 | 122.9181 | 61.6354 | 61.6759 | 61.5712 | 61.6117
5035.0625 | 123.3765 | -61.4731 | 61.6333 | 0.57969 | -6.1349 | -5.694 | 3.9903 | 7.4251 | 0.548 | -1.1294 | 61.6882 | 0.27611 | 61.6011 | -0.028522 | 0.039079 | 61.5936 | 0.007721 | 61.3718 | 62.0528 | 55.3382 | 55.779 | 65.4634 | 68.8982 | 62.0211 | 60.3437 | 123.1613 | 61.7492 | 123.0742 | 61.4446 | 61.5122 | 123.0667 | 61.4808 | 122.8449 | 61.6491 | 61.6805 | 61.562 | 61.5934
5036.1094 | 123.3673 | -61.5005 | 61.6241 | 0.60716 | -5.8877 | -5.4651 | 3.9857 | 7.5395 | 0.59836 | -1.0837 | 61.6973 | 0.28069 | 61.6286 | -0.023943 | 0.039079 | 61.5936 | 0.003143 | 61.381 | 62.1077 | 55.6129 | 56.0354 | 65.4863 | 69.0401 | 62.0989 | 60.4169 | 123.1979 | 61.7812 | 123.1291 | 61.4766 | 61.5396 | 123.0942 | 61.5037 | 122.8815 | 61.6583 | 61.6942 | 61.5895 | 61.6255
5037.0625 | 123.4085 | -61.4822 | 61.6379 | 0.57511 | -5.9014 | -5.6345 | 3.6927 | 7.567 | 0.55258 | -1.102 | 61.6882 | 0.28069 | 61.6286 | -0.033101 | 0.043657 | 61.5891 | 0.003143 | 61.381 | 62.0573 | 55.5808 | 55.8477 | 65.175 | 69.0492 | 62.0348 | 60.3803 | 123.1704 | 61.7629 | 123.1108 | 61.4491 | 61.5259 | 123.0713 | 61.4854 | 122.8632 | 61.6445 | 61.685 | 61.5849 | 61.6255
5038.0781 | 123.3032 | -61.5143 | 61.6425 | 0.60716 | -5.764 | -5.4834 | 3.853 | 7.4846 | 0.59378 | -1.1065 | 61.6882 | 0.28069 | 61.5965 | -0.023943 | 0.043657 | 61.5936 | 0.007721 | 61.381 | 62.1214 | 55.7502 | 56.0309 | 65.3673 | 68.9989 | 62.1081 | 60.4077 | 123.2025 | 61.795 | 123.1108 | 61.4903 | 61.5579 | 123.1079 | 61.522 | 122.8953 | 61.6445 | 61.6805 | 61.5529 | 61.5888
5039.0625 | 123.3765 | -61.4731 | 61.6379 | 0.67126 | -5.6725 | -5.2316 | 3.5187 | 7.6586 | 0.6533 | -0.98293 | 61.679 | 0.28526 | 61.5965 | -0.033101 | 0.048236 | 61.5982 | -0.001436 | 61.3856 | 62.1443 | 55.8006 | 56.2415 | 64.9918 | 69.1316 | 62.1264 | 60.4902 | 123.1521 | 61.7583 | 123.0696 | 61.44 | 61.5213 | 123.0713 | 61.4716 | 122.8586 | 61.6308 | 61.6805 | 61.5483 | 61.598
5040.0781 | 123.3124 | -61.5097 | 61.6333 | 0.72162 | -5.8281 | -5.4193 | 2.8823 | 7.6631 | 0.7174 | -0.8639 | 61.6928 | 0.27611 | 61.624 | -0.033101 | 0.048236 | 61.5982 | 0.007721 | 61.3718 | 62.2313 | 55.6816 | 56.0904 | 64.392 | 69.1728 | 62.2271 | 60.6458 | 123.2025 | 61.7858 | 123.1337 | 61.4766 | 61.5579 | 123.1079 | 61.5174 | 122.8815 | 61.6445 | 61.685 | 61.5758 | 61.6163
5041.0625 | 123.3307 | -61.4731 | 61.6608 | 0.71704 | -5.9197 | -5.3506 | 3.0746 | 7.7227 | 0.72656 | -0.9463 | 61.6882 | 0.27611 | 61.624 | -0.028522 | 0.048236 | 61.5936 | 0.003143 | 61.3901 | 62.1901 | 55.5534 | 56.1224 | 64.5477 | 69.1957 | 62.1996 | 60.5268 | 123.1613 | 61.7492 | 123.0971 | 61.4446 | 61.5213 | 123.0667 | 61.4762 | 122.8632 | 61.64 | 61.685 | 61.5758 | 61.6209
5042.0781 | 123.3078 | -61.5051 | 61.6425 | 0.70331 | -5.938 | -5.227 | 3.3448 | 7.8096 | 0.69909 | -0.95546 | 61.679 | 0.28984 | 61.592 | -0.028522 | 0.043657 | 61.5936 | -0.001436 | 61.3901 | 62.2084 | 55.5671 | 56.2781 | 64.8499 | 69.3148 | 62.2042 | 60.5497 | 123.1842 | 61.795 | 123.0971 | 61.4766 | 61.5488 | 123.0988 | 61.5037 | 122.8953 | 61.6354 | 61.6805 | 61.5483 | 61.5934
5043.0625 | 123.349 | -61.4548 | 61.6196 | 0.61632 | -6.1166 | -5.4605 | 3.5462 | 7.8051 | 0.68993 | -0.98293 | 61.6973 | 0.28069 | 61.6332 | -0.028522 | 0.048236 | 61.5891 | 0.012299 | 61.3856 | 62.0711 | 55.3382 | 55.9942 | 65.001 | 69.2598 | 62.1447 | 60.4718 | 123.1521 | 61.7355 | 123.0879 | 61.4263 | 61.503 | 123.0438 | 61.4671 | 122.8403 | 61.6491 | 61.685 | 61.5849 | 61.6209
5044.0781 | 123.3078 | -61.4914 | 61.6837 | 0.56595 | -6.2494 | -5.5567 | 2.7679 | 7.7776 | 0.62583 | -1.015 | 61.6928 | 0.28069 | 61.6332 | -0.03768 | 0.048236 | 61.5891 | -0.001436 | 61.3627 | 62.0573 | 55.242 | 55.9347 | 64.2593 | 69.269 | 62.1172 | 60.4764 | 123.1842 | 61.7721 | 123.1246 | 61.4537 | 61.5396 | 123.0804 | 61.49 | 122.8541 | 61.6445 | 61.6942 | 61.5849 | 61.6346
5045.0625 | 123.3994 | -61.4502 | 61.6379 | 0.65294 | -6.0617 | -5.401 | 2.8411 | 7.8005 | 0.69451 | -1.0241 | 61.6882 | 0.28526 | 61.6011 | -0.023943 | 0.043657 | 61.5936 | 0.012299 | 61.381 | 62.1031 | 55.3885 | 56.0492 | 64.2913 | 69.2507 | 62.1447 | 60.4261 | 123.1384 | 61.7355 | 123.0513 | 61.4263 | 61.4939 | 123.0438 | 61.4625 | 122.8312 | 61.6445 | 61.6759 | 61.5575 | 61.5888
5046.0625 | 123.3032 | -61.4822 | 61.6882 | 0.61632 | -6.1716 | -5.0576 | 2.8594 | 7.8142 | 0.63957 | -1.0287 | 61.6836 | 0.27611 | 61.6057 | -0.028522 | 0.048236 | 61.5936 | 0.007721 | 61.3764 | 62.0986 | 55.3107 | 56.4246 | 64.3417 | 69.2965 | 62.1218 | 60.4535 | 123.1659 | 61.7583 | 123.0879 | 61.4537 | 61.5305 | 123.0759 | 61.49 | 122.8586 | 61.6354 | 61.6759 | 61.5575 | 61.598
5047.0938 | 123.381 | -61.4685 | 61.6425 | 0.55222 | -6.2402 | -5.4926 | 3.3219 | 7.8051 | 0.57089 | -1.0699 | 61.6973 | 0.28526 | 61.6332 | -0.028522 | 0.043657 | 61.5891 | 0.012299 | 61.381 | 62.0207 | 55.2283 | 55.9759 | 64.7904 | 69.2736 | 62.0394 | 60.3986 | 123.1659 | 61.7538 | 123.1017 | 61.44 | 61.5122 | 123.0576 | 61.4808 | 122.8495 | 61.6537 | 61.685 | 61.5895 | 61.6209
5048.0625 | 123.3948 | -61.4273 | 61.6379 | 0.52933 | -6.2586 | -5.5704 | 3.5554 | 7.86 | 0.548 | -1.1294 | 61.6973 | 0.28984 | 61.6332 | -0.033101 | 0.052814 | 61.5891 | -0.001436 | 61.3718 | 61.9566 | 55.1688 | 55.8569 | 64.9827 | 69.2873 | 61.9753 | 60.2979 | 123.1247 | 61.7171 | 123.0605 | 61.3942 | 61.4801 | 123.0164 | 61.4259 | 122.7991 | 61.6445 | 61.6988 | 61.5804 | 61.6346
5049.0781 | 123.3994 | -61.4731 | 61.6058 | 0.57511 | -6.2402 | -5.195 | 3.3539 | 7.9195 | 0.6121 | -1.1203 | 61.6928 | 0.28069 | 61.5965 | -0.03768 | 0.034501 | 61.5936 | 0.003143 | 61.3718 | 62.0482 | 55.2328 | 56.2781 | 64.827 | 69.3926 | 62.0852 | 60.3528 | 123.1659 | 61.7538 | 123.0696 | 61.4354 | 61.5076 | 123.0667 | 61.4762 | 122.8449 | 61.6583 | 61.6896 | 61.562 | 61.5934
5050.0625 | 123.3994 | -61.4594 | 61.6379 | 0.5568 | -6.3822 | -4.8974 | 3.5462 | 7.8829 | 0.58921 | -1.1661 | 61.6882 | 0.28526 | 61.5965 | -0.033101 | 0.043657 | 61.6028 | 0.003143 | 61.3764 | 62.0161 | 55.0772 | 56.562 | 65.0056 | 69.3422 | 62.0486 | 60.2933 | 123.1475 | 61.7446 | 123.0559 | 61.4262 | 61.503 | 123.0621 | 61.4625 | 122.8357 | 61.6445 | 61.685 | 61.5529 | 61.5934
5051.0625 | 123.3627 | -61.4777 | 61.6516 | 0.59342 | -6.3684 | -5.1309 | 3.6927 | 7.9287 | 0.64415 | -1.1294 | 61.6836 | 0.28526 | 61.6194 | -0.03768 | 0.043657 | 61.5982 | 0.003143 | 61.3856 | 62.0711 | 55.1092 | 56.3468 | 65.1704 | 69.4063 | 62.1218 | 60.3482 | 123.1613 | 61.7629 | 123.0971 | 61.44 | 61.5213 | 123.0759 | 61.4808 | 122.8632 | 61.64 | 61.6805 | 61.5758 | 61.6163
5052.0781 | 123.4406 | -61.4594 | 61.6425 | 0.61174 | -6.2631 | -5.5933 | 3.7293 | 8.0019 | 0.63957 | -1.1203 | 61.6973 | 0.27611 | 61.624 | -0.03768 | 0.048236 | 61.5982 | 0.007721 | 61.3764 | 62.0711 | 55.1962 | 55.866 | 65.1887 | 69.4613 | 62.0989 | 60.3391 | 123.1567 | 61.7355 | 123.0834 | 61.4217 | 61.5076 | 123.0576 | 61.4671 | 122.8357 | 61.6491 | 61.6896 | 61.5758 | 61.6163
5053.0625 | 123.4177 | -61.4319 | 61.6745 | 0.65294 | -6.1761 | -5.3415 | 3.2349 | 8.0156 | 0.68993 | -1.134 | 61.6973 | 0.28984 | 61.6286 | -0.028522 | 0.039079 | 61.5936 | 0.007721 | 61.3718 | 62.0848 | 55.2557 | 56.0904 | 64.6668 | 69.4475 | 62.1218 | 60.2979 | 123.1292 | 61.7217 | 123.0605 | 61.4034 | 61.471 | 123.0255 | 61.4396 | 122.8037 | 61.6583 | 61.6896 | 61.5895 | 61.6209
5054.0781 | 123.3765 | -61.5005 | 61.6333 | 0.53391 | -6.3364 | -4.934 | 3.5966 | 7.9149 | 0.63957 | -1.2027 | 61.679 | 0.28984 | 61.592 | -0.033101 | 0.043657 | 61.6028 | 0.012299 | 61.3764 | 62.0345 | 55.1642 | 56.5666 | 65.0971 | 69.4155 | 62.1401 | 60.2979 | 123.1796 | 61.7904 | 123.0925 | 61.4674 | 61.5442 | 123.1033 | 61.5128 | 122.8769 | 61.6354 | 61.6667 | 61.5483 | 61.5797
5055.0625 | 123.4177 | -61.4319 | 61.6608 | 0.6621 | -6.2036 | -5.2545 | 3.7477 | 7.9882 | 0.62125 | -1.1523 | 61.6973 | 0.28526 | 61.6011 | -0.028522 | 0.057392 | 61.5891 | 0.003143 | 61.381 | 62.094 | 55.2283 | 56.1774 | 65.1795 | 69.4201 | 62.0531 | 60.2796 | 123.1292 | 61.7171 | 123.033 | 61.4034 | 61.4893 | 123.0209 | 61.435 | 122.8129 | 61.64 | 61.6942 | 61.5437 | 61.598
5056.0938 | 123.349 | -61.4822 | 61.6516 | 0.56595 | -6.3272 | -5.5842 | 3.7751 | 7.979 | 0.53426 | -1.1752 | 61.6973 | 0.28526 | 61.6286 | -0.028522 | 0.043657 | 61.5891 | 0.012299 | 61.3627 | 62.0482 | 55.155 | 55.8981 | 65.2574 | 69.4613 | 62.0165 | 60.307 | 123.1796 | 61.7675 | 123.1108 | 61.4537 | 61.5259 | 123.0713 | 61.4945 | 122.8449 | 61.6537 | 61.685 | 61.5849 | 61.6163
5057.0625 | 123.3902 | -61.4456 | 61.6608 | 0.60716 | -6.2494 | -5.4285 | 3.0288 | 8.0294 | 0.57089 | -1.0882 | 61.7019 | 0.28069 | 61.6286 | -0.03768 | 0.052814 | 61.5891 | 0.007721 | 61.3718 | 62.0528 | 55.1962 | 56.0171 | 64.4745 | 69.475 | 62.0165 | 60.3574 | 123.1475 | 61.7263 | 123.0742 | 61.4079 | 61.4984 | 123.0347 | 61.4533 | 122.8174 | 61.6491 | 61.6942 | 61.5758 | 61.6209
5058.0781 | 123.4085 | -61.4777 | 61.6241 | 0.58885 | -6.2036 | -5.3003 | 3.0609 | 8.0843 | 0.57089 | -1.1157 | 61.6882 | 0.28984 | 61.6057 | -0.028522 | 0.057392 | 61.5936 | 0.007721 | 61.3718 | 62.0665 | 55.2741 | 56.1774 | 64.5386 | 69.562 | 62.0486 | 60.362 | 123.1659 | 61.7675 | 123.0834 | 61.4491 | 61.5351 | 123.0713 | 61.4854 | 122.8495 | 61.6308 | 61.6805 | 61.5483 | 61.598
5059.0625 | 123.2895 | -61.4594 | 61.6745 | 0.53391 | -6.2128 | -5.4102 | 2.8686 | 8.0706 | 0.548 | -1.1889 | 61.6973 | 0.28069 | 61.5965 | -0.028522 | 0.048236 | 61.5936 | 0.007721 | 61.3764 | 61.9933 | 55.2466 | 56.0492 | 64.3279 | 69.5299 | 62.0074 | 60.2704 | 123.1567 | 61.74 | 123.0559 | 61.4308 | 61.5076 | 123.053 | 61.4671 | 122.8357 | 61.6491 | 61.6896 | 61.5483 | 61.5888
5060.0938 | 123.4589 | -61.4319 | 61.6516 | 0.5568 | -6.2036 | -5.3461 | 2.8961 | 8.0568 | 0.60294 | -1.0837 | 61.6882 | 0.27611 | 61.6332 | -0.028522 | 0.052814 | 61.5845 | 0.003143 | 61.3764 | 61.9887 | 55.2283 | 56.0858 | 64.3279 | 69.4887 | 62.0348 | 60.3482 | 123.1201 | 61.708 | 123.0651 | 61.4034 | 61.4847 | 123.0164 | 61.435 | 122.8083 | 61.6354 | 61.685 | 61.5804 | 61.63
5061.0625 | 123.317 | -61.4548 | 61.6882 | 0.57511 | -6.2173 | -5.4834 | 2.7633 | 8.066 | 0.6121 | -0.98293 | 61.7019 | 0.28526 | 61.6377 | -0.019364 | 0.057392 | 61.5891 | 0.007721 | 61.381 | 62.0299 | 55.2374 | 55.9713 | 64.2181 | 69.5208 | 62.0669 | 60.4718 | 123.1567 | 61.74 | 123.0925 | 61.4354 | 61.5122 | 123.0438 | 61.4625 | 122.8357 | 61.6445 | 61.6942 | 61.5804 | 61.63
5062.0938 | 123.4406 | -61.4594 | 61.6608 | 0.68957 | -6.025 | -5.5063 | 3.0655 | 8.1621 | 0.73114 | -0.75402 | 61.6836 | 0.27611 | 61.6194 | -0.033101 | 0.039079 | 61.5936 | 0.007721 | 61.3947 | 62.1489 | 55.4343 | 55.953 | 64.5248 | 69.6215 | 62.1905 | 60.7053 | 123.143 | 61.7355 | 123.0788 | 61.4262 | 61.4984 | 123.053 | 61.4671 | 122.8541 | 61.6445 | 61.6759 | 61.5804 | 61.6117
5063.0625 | 123.3856 | -61.4639 | 61.6562 | 0.60716 | -6.286 | -5.6208 | 3.299 | 8.1072 | 0.62583 | -1.0562 | 61.6882 | 0.28526 | 61.5965 | -0.023943 | 0.048236 | 61.5936 | 0.012299 | 61.381 | 62.0711 | 55.1779 | 55.8431 | 64.7629 | 69.5711 | 62.0898 | 60.4077 | 123.1521 | 61.7492 | 123.0605 | 61.44 | 61.5122 | 123.0576 | 61.4762 | 122.8449 | 61.64 | 61.6759 | 61.5483 | 61.5842
5064.0781 | 123.436 | -61.4365 | 61.6791 | 0.58885 | -6.3822 | -5.749 | 2.8961 | 7.9516 | 0.60752 | -1.3675 | 61.6928 | 0.28526 | 61.6149 | -0.023943 | 0.043657 | 61.5753 | 0.007721 | 61.3672 | 62.0253 | 55.0543 | 55.6875 | 64.3325 | 69.388 | 62.044 | 60.069 | 123.1292 | 61.7217 | 123.0513 | 61.4125 | 61.4801 | 123.0118 | 61.4442 | 122.8037 | 61.6491 | 61.685 | 61.5712 | 61.6071
5065.0625 | 123.3215 | -61.441 | 61.7477 | 0.58885 | -6.4234 | -5.7169 | 2.8411 | 8.0019 | 0.58463 | -1.3629 | 61.7065 | 0.28526 | 61.6423 | -0.023943 | 0.048236 | 61.5799 | 0.007721 | 61.381 | 62.0299 | 55.0176 | 55.7241 | 64.2822 | 69.443 | 62.0257 | 60.0781 | 123.1475 | 61.7263 | 123.0834 | 61.4171 | 61.4893 | 123.0209 | 61.4488 | 122.822 | 61.6583 | 61.6988 | 61.5941 | 61.6346
5066.1094 | 123.3536 | -61.4777 | 61.6562 | 0.58427 | -6.2769 | -5.5063 | 3.0151 | 7.9561 | 0.57089 | -1.015 | 61.6973 | 0.27611 | 61.624 | -0.028522 | 0.043657 | 61.5891 | 0.003143 | 61.3901 | 62.0619 | 55.2008 | 55.9713 | 64.4928 | 69.4338 | 62.0486 | 60.4627 | 123.175 | 61.7538 | 123.1017 | 61.4491 | 61.5213 | 123.0667 | 61.4808 | 122.8678 | 61.6537 | 61.6942 | 61.5804 | 61.6209
5067.0625 | 123.2346 | -61.4777 | 61.7111 | 0.58885 | -6.2402 | -5.401 | 3.0563 | 8.0568 | 0.60294 | -1.1798 | 61.6882 | 0.28069 | 61.6103 | -0.023943 | 0.048236 | 61.5891 | 0.016878 | 61.3901 | 62.0665 | 55.2374 | 56.0766 | 64.534 | 69.5345 | 62.0806 | 60.2979 | 123.1659 | 61.7583 | 123.0879 | 61.4537 | 61.5259 | 123.0667 | 61.4945 | 122.8678 | 61.64 | 61.6713 | 61.562 | 61.5934
5068.0781 | 123.3994 | -61.3998 | 61.647 | 0.30041 | -6.5333 | -5.6391 | 2.7633 | 7.5304 | 0.34197 | -1.2897 | 61.7019 | 0.28069 | 61.6194 | -0.028522 | 0.052814 | 61.5662 | 0.012299 | 61.3718 | 61.7002 | 54.8666 | 55.7607 | 64.1631 | 68.9302 | 61.7418 | 60.1102 | 123.1018 | 61.6805 | 123.0193 | 61.3713 | 61.4527 | 122.966 | 61.4121 | 122.7717 | 61.6491 | 61.6896 | 61.5666 | 61.6071
5069.0625 | 123.3582 | -61.4456 | 61.702 | 0.4927 | -6.3913 | -5.5063 | 2.7541 | 7.773 | 0.50222 | -1.0928 | 61.7111 | 0.28069 | 61.6423 | -0.033101 | 0.057392 | 61.5845 | 0.012299 | 61.381 | 61.9383 | 55.0543 | 55.9393 | 64.1997 | 69.2186 | 61.9478 | 60.3528 | 123.1567 | 61.7263 | 123.0879 | 61.4125 | 61.503 | 123.0301 | 61.4579 | 122.8266 | 61.6537 | 61.6988 | 61.5849 | 61.63
5070.0938 | 123.3536 | -61.4365 | 61.7111 | 0.51101 | -6.2448 | -5.5063 | 2.0261 | 7.6723 | 0.52053 | -1.0928 | 61.7111 | 0.28984 | 61.6515 | -0.033101 | 0.052814 | 61.5707 | 0.003143 | 61.3718 | 61.9475 | 55.1916 | 55.9301 | 63.4626 | 69.1088 | 61.957 | 60.3437 | 123.1475 | 61.7263 | 123.0879 | 61.4034 | 61.4893 | 123.0072 | 61.4396 | 122.8083 | 61.6583 | 61.7079 | 61.5987 | 61.6483
5071.0625 | 123.317 | -61.4914 | 61.7432 | 0.58885 | -6.341 | -5.5338 | 2.3695 | 7.9287 | 0.61668 | -1.1111 | 61.7065 | 0.28069 | 61.6149 | -0.033101 | 0.039079 | 61.5891 | 0.012299 | 61.3856 | 62.0802 | 55.1504 | 55.9576 | 63.8609 | 69.4201 | 62.1081 | 60.3803 | 123.1979 | 61.7721 | 123.1063 | 61.4583 | 61.5305 | 123.0804 | 61.5037 | 122.8769 | 61.6674 | 61.6942 | 61.5758 | 61.6026
5072.0938 | 123.3215 | -61.4548 | 61.6882 | 0.56595 | -5.9564 | -5.3278 | 2.3833 | 7.979 | 0.57547 | -1.0882 | 61.6928 | 0.28526 | 61.6103 | -0.033101 | 0.048236 | 61.5845 | 0.012299 | 61.381 | 62.0207 | 55.4984 | 56.127 | 63.838 | 69.4338 | 62.0302 | 60.3665 | 123.1475 | 61.74 | 123.0651 | 61.4217 | 61.503 | 123.0392 | 61.4671 | 122.8357 | 61.6445 | 61.6805 | 61.562 | 61.598
5073.0625 | 123.262 | -61.4914 | 61.6745 | 0.59342 | -5.8373 | -5.4285 | 2.8961 | 8.0477 | 0.61668 | -1.0928 | 61.6973 | 0.28526 | 61.6286 | -0.033101 | 0.048236 | 61.5982 | 0.007721 | 61.3901 | 62.0848 | 55.6541 | 56.0629 | 64.3875 | 69.5391 | 62.1081 | 60.3986 | 123.1887 | 61.7767 | 123.12 | 61.4583 | 61.5396 | 123.0896 | 61.4991 | 122.8815 | 61.6491 | 61.6896 | 61.5804 | 61.6209
5074.0938 | 123.349 | -61.4868 | 61.6379 | 0.65752 | -5.7091 | -5.4376 | 3.4317 | 8.0981 | 0.68077 | -1.2714 | 61.6836 | 0.28984 | 61.6332 | -0.033101 | 0.052814 | 61.5982 | 0.012299 | 61.4039 | 62.1443 | 55.7777 | 56.0492 | 64.9186 | 69.5849 | 62.1676 | 60.2155 | 123.1704 | 61.7767 | 123.12 | 61.4537 | 61.5396 | 123.085 | 61.4991 | 122.8907 | 61.6308 | 61.6713 | 61.5804 | 61.6209
5075.0625 | 123.2986 | -61.5097 | 61.6974 | 0.61632 | -5.7045 | -5.5155 | 3.4134 | 8.1026 | 0.63041 | -1.1249 | 61.6928 | 0.28069 | 61.6011 | -0.028522 | 0.048236 | 61.5936 | 0.012299 | 61.4039 | 62.126 | 55.8052 | 55.9942 | 64.9231 | 69.6123 | 62.1401 | 60.3849 | 123.2025 | 61.7904 | 123.1108 | 61.4812 | 61.5579 | 123.1033 | 61.522 | 122.9136 | 61.6445 | 61.6805 | 61.5529 | 61.5888
5076.1094 | 123.2483 | -61.496 | 61.6562 | 0.58885 | -5.8556 | -5.3781 | 3.3631 | 8.0935 | 0.58463 | -0.98751 | 61.6836 | 0.28069 | 61.592 | -0.028522 | 0.043657 | 61.6028 | 0.007721 | 61.3947 | 62.0848 | 55.6404 | 56.1179 | 64.859 | 69.5894 | 62.0806 | 60.5085 | 123.1796 | 61.7767 | 123.0879 | 61.4674 | 61.5396 | 123.0988 | 61.5037 | 122.8907 | 61.64 | 61.6759 | 61.5483 | 61.5842
5077.0625 | 123.3627 | -61.4502 | 61.6882 | 0.60716 | -5.8968 | -5.3415 | 3.592 | 8.0935 | 0.58921 | -0.85016 | 61.6882 | 0.28984 | 61.6149 | -0.033101 | 0.052814 | 61.6028 | 0.007721 | 61.4039 | 62.0574 | 55.5534 | 56.1087 | 65.0422 | 69.5437 | 62.0394 | 60.6 | 123.1384 | 61.74 | 123.0651 | 61.4171 | 61.503 | 123.053 | 61.4579 | 122.8541 | 61.6354 | 61.6805 | 61.562 | 61.6071
5078.0781 | 123.3948 | -61.4548 | 61.6241 | 0.60258 | -5.8922 | -5.488 | 3.5828 | 8.1942 | 0.57547 | -0.80438 | 61.6882 | 0.27611 | 61.6149 | -0.033101 | 0.048236 | 61.5936 | 0.012299 | 61.3856 | 62.0574 | 55.5625 | 55.9668 | 65.0376 | 69.649 | 62.0302 | 60.6504 | 123.143 | 61.7309 | 123.0696 | 61.4217 | 61.503 | 123.0484 | 61.4671 | 122.8403 | 61.64 | 61.6759 | 61.5666 | 61.6026
5079.0625 | 123.2437 | -61.4777 | 61.7111 | 0.57053 | -5.9655 | -5.3827 | 3.5279 | 8.1347 | 0.548 | -0.91426 | 61.6836 | 0.28526 | 61.6011 | -0.028522 | 0.048236 | 61.5891 | 0.003143 | 61.3947 | 62.0482 | 55.5122 | 56.095 | 65.0056 | 69.6123 | 62.0257 | 60.5634 | 123.1613 | 61.7629 | 123.0788 | 61.4491 | 61.5259 | 123.0667 | 61.4808 | 122.8724 | 61.6354 | 61.6805 | 61.5529 | 61.598
5080.0781 | 123.3902 | -61.5097 | 61.6745 | 0.48354 | -5.9792 | -5.1446 | 3.1891 | 8.0523 | 0.45643 | -0.83185 | 61.679 | 0.28069 | 61.592 | -0.042259 | 0.039079 | 61.5891 | 0.003143 | 61.381 | 61.9932 | 55.5305 | 56.3651 | 64.6988 | 69.562 | 61.9661 | 60.6779 | 123.1887 | 61.7904 | 123.1017 | 61.4674 | 61.5488 | 123.0988 | 61.5128 | 122.8907 | 61.64 | 61.6759 | 61.5529 | 61.5888
5081.0625 | 123.3032 | -61.5051 | 61.647 | 0.41945 | -5.9335 | -5.0759 | 2.951 | 8.1988 | 0.41523 | -0.85016 | 61.6836 | 0.28069 | 61.624 | -0.033101 | 0.043657 | 61.5891 | 0.003143 | 61.3764 | 61.9246 | 55.5717 | 56.4292 | 64.4561 | 69.7039 | 61.9204 | 60.655 | 123.1887 | 61.7858 | 123.1291 | 61.472 | 61.5488 | 123.0942 | 61.5083 | 122.8815 | 61.64 | 61.6805 | 61.5804 | 61.6209
5082.0781 | 123.4314 | -61.4777 | 61.6241 | 0.40113 | -5.9151 | -5.543 | 3.1982 | 8.24 | 0.41065 | -0.7586 | 61.6928 | 0.28069 | 61.6332 | -0.03768 | 0.043657 | 61.5891 | 0.012299 | 61.3764 | 61.8788 | 55.5625 | 55.9347 | 64.6759 | 69.7176 | 61.8883 | 60.7191 | 123.1704 | 61.7583 | 123.1108 | 61.44 | 61.5213 | 123.0667 | 61.49 | 122.8541 | 61.6491 | 61.6805 | 61.5895 | 61.6209
5083.0625 | 123.3856 | -61.441 | 61.6425 | 0.37366 | -5.9838 | -5.6528 | 3.1296 | 8.2766 | 0.36944 | -0.87305 | 61.6928 | 0.28069 | 61.6103 | -0.028522 | 0.048236 | 61.5891 | 0.007721 | 61.381 | 61.8147 | 55.4572 | 55.7882 | 64.5706 | 69.7176 | 61.8105 | 60.568 | 123.1338 | 61.7217 | 123.0513 | 61.4125 | 61.4893 | 123.0301 | 61.4488 | 122.822 | 61.6445 | 61.685 | 61.562 | 61.6026
5084.0938 | 123.3627 | -61.4594 | 61.6516 | 0.45149 | -5.9197 | -5.6025 | 3.0746 | 8.2766 | 0.4427 | -1.1157 | 61.6882 | 0.28526 | 61.6011 | -0.028522 | 0.052814 | 61.5891 | 0.007721 | 61.3764 | 61.9108 | 55.5396 | 55.8569 | 64.534 | 69.7359 | 61.902 | 60.3437 | 123.1475 | 61.7446 | 123.0605 | 61.4308 | 61.5122 | 123.0484 | 61.4671 | 122.8357 | 61.6354 | 61.6805 | 61.5483 | 61.5934
5085.0625 | 123.4222 | -61.3998 | 61.6745 | 0.45149 | -5.9518 | -5.6528 | 3.0609 | 8.1759 | 0.43812 | -1.1477 | 61.7019 | 0.28526 | 61.6286 | -0.028522 | 0.052814 | 61.5845 | 0.007721 | 61.381 | 61.8513 | 55.4481 | 55.747 | 64.4607 | 69.5757 | 61.838 | 60.2521 | 123.1018 | 61.6851 | 123.0284 | 61.3713 | 61.4527 | 122.9843 | 61.4076 | 122.7808 | 61.6491 | 61.6942 | 61.5758 | 61.6209
5086.1094 | 123.381 | -61.4822 | 61.5829 | 0.47439 | -5.8831 | -5.6895 | 3.3127 | 8.2537 | 0.47475 | -1.2073 | 61.6928 | 0.28069 | 61.624 | -0.03768 | 0.043657 | 61.5936 | 0.007721 | 61.3672 | 61.9566 | 55.5991 | 55.7928 | 64.7949 | 69.7359 | 61.957 | 60.275 | 123.175 | 61.7629 | 123.1063 | 61.4446 | 61.5259 | 123.0759 | 61.49 | 122.8495 | 61.6491 | 61.685 | 61.5804 | 61.6163
5087.0625 | 123.4039 | -61.4685 | 61.6379 | 0.35077 | -5.9243 | -5.5658 | 3.4134 | 8.2857 | 0.61668 | -1.3721 | 61.6973 | 0.27611 | 61.6011 | -0.028522 | 0.043657 | 61.5936 | 0.003143 | 61.3856 | 61.8193 | 55.5442 | 55.9027 | 64.8819 | 69.7543 | 62.0852 | 60.0964 | 123.1659 | 61.7446 | 123.0696 | 61.44 | 61.5122 | 123.0621 | 61.4716 | 122.8541 | 61.6537 | 61.6942 | 61.5575 | 61.598
5088.0781 | 123.381 | -61.4685 | 61.615 | 0.36908 | -6.0159 | -5.6986 | 3.4501 | 8.1988 | 0.3786 | -1.4224 | 61.6882 | 0.28069 | 61.6057 | -0.033101 | 0.048236 | 61.5845 | 0.007721 | 61.3764 | 61.8376 | 55.4526 | 55.7699 | 64.9186 | 69.6673 | 61.8471 | 60.0461 | 123.1567 | 61.7492 | 123.0742 | 61.4354 | 61.5167 | 123.053 | 61.4762 | 122.8449 | 61.64 | 61.6805 | 61.5575 | 61.598
5089.0625 | 123.4039 | -61.4365 | 61.6653 | 0.43776 | -5.906 | -5.6437 | 3.5508 | 8.3269 | 0.40149 | -1.5369 | 61.7019 | 0.28069 | 61.6332 | -0.028522 | 0.048236 | 61.5891 | 0.012299 | 61.3764 | 61.8742 | 55.5305 | 55.7928 | 64.9873 | 69.7634 | 61.838 | 59.8996 | 123.1384 | 61.7171 | 123.0696 | 61.4079 | 61.4847 | 123.0255 | 61.4488 | 122.8129 | 61.6537 | 61.6896 | 61.5849 | 61.6209
5090.0938 | 123.3307 | -61.4822 | 61.6241 | 0.41487 | -6.0342 | -5.6528 | 3.5554 | 8.359 | 0.3786 | -1.3309 | 61.6928 | 0.27611 | 61.6332 | -0.028522 | 0.048236 | 61.5845 | 0.007721 | 61.3718 | 61.8971 | 55.448 | 55.8294 | 65.0376 | 69.8412 | 61.8608 | 60.1514 | 123.175 | 61.7583 | 123.1154 | 61.4537 | 61.5305 | 123.0667 | 61.49 | 122.8541 | 61.6445 | 61.685 | 61.5849 | 61.6255
5091.0625 | 123.3124 | -61.4822 | 61.6928 | 0.37366 | -6.0571 | -5.6437 | 3.4546 | 8.3681 | 0.34197 | -1.427 | 61.6928 | 0.28526 | 61.6011 | -0.033101 | 0.048236 | 61.5845 | 0.007721 | 61.3764 | 61.8559 | 55.4252 | 55.8386 | 64.9369 | 69.8504 | 61.8242 | 60.0552 | 123.175 | 61.7675 | 123.0834 | 61.4491 | 61.5305 | 123.0667 | 61.49 | 122.8586 | 61.6445 | 61.685 | 61.5529 | 61.5934
5092.0781 | 123.3307 | -61.4731 | 61.6287 | 0.28209 | -6.2219 | -6.0512 | 2.777 | 8.1164 | 0.24125 | -1.5872 | 61.7065 | 0.28526 | 61.6149 | -0.033101 | 0.039079 | 61.5753 | 0.007721 | 61.3672 | 61.7552 | 55.2512 | 55.4219 | 64.2501 | 69.5894 | 61.7143 | 59.8858 | 123.1796 | 61.7583 | 123.0879 | 61.44 | 61.5122 | 123.0484 | 61.4808 | 122.8403 | 61.6674 | 61.6988 | 61.5758 | 61.6071
5093.0625 | 123.4451 | -61.4182 | 61.6653 | 0.23173 | -6.2952 | -6.1336 | 2.7679 | 7.7455 | 0.20462 | -1.6239 | 61.7202 | 0.28984 | 61.6469 | -0.028522 | 0.043657 | 61.5662 | 0.003143 | 61.3581 | 61.6499 | 55.123 | 55.2846 | 64.186 | 69.1637 | 61.6228 | 59.7943 | 123.1384 | 61.708 | 123.0651 | 61.3896 | 61.4618 | 122.9843 | 61.4213 | 122.7762 | 61.6766 | 61.7171 | 61.6032 | 61.6438
5094.0938 | 123.3856 | -61.4456 | 61.6608 | -0.10249 | -6.4325 | -6.2343 | 2.484 | 7.5579 | 0.56173 | -1.7246 | 61.7248 | 0.28069 | 61.6652 | -0.033101 | 0.034501 | 61.5616 | 0.007721 | 61.3443 | 61.3431 | 55.0131 | 55.2113 | 63.9296 | 69.0035 | 62.0074 | 59.721 | 123.1704 | 61.7263 | 123.1108 | 61.4125 | 61.4801 | 123.0072 | 61.4533 | 122.79 | 61.6903 | 61.7171 | 61.6307 | 61.6575
5095.0625 | 123.4085 | -61.4182 | 61.6516 | 0.34619 | -5.9884 | -5.8818 | 2.5847 | 7.7318 | 0.35571 | -1.546 | 61.7019 | 0.27611 | 61.6286 | -0.033101 | 0.048236 | 61.5845 | 0.007721 | 61.3535 | 61.7643 | 55.4297 | 55.5364 | 64.0029 | 69.15 | 61.7739 | 59.8721 | 123.1201 | 61.6943 | 123.0467 | 61.3851 | 61.4664 | 123.0026 | 61.4259 | 122.7717 | 61.6537 | 61.6942 | 61.5804 | 61.6209
5096.0938 | 123.2803 | -61.4914 | 61.6837 | 0.41945 | -6.0662 | -5.8085 | 2.6992 | 7.8829 | 0.43354 | -1.3995 | 61.7065 | 0.28069 | 61.6103 | -0.033101 | 0.039079 | 61.5891 | 0.003143 | 61.3718 | 61.9108 | 55.4252 | 55.6829 | 64.1906 | 69.3743 | 61.9249 | 60.0919 | 123.1979 | 61.7721 | 123.1017 | 61.4583 | 61.5305 | 123.0804 | 61.4945 | 122.8632 | 61.6674 | 61.7034 | 61.5712 | 61.6071
5097.0625 | 123.3948 | -61.4365 | 61.6333 | 0.52475 | -5.9609 | -5.7444 | 2.4291 | 8.1621 | 0.52969 | -1.3217 | 61.7019 | 0.28526 | 61.6332 | -0.03768 | 0.043657 | 61.5845 | 0.003143 | 61.3718 | 61.9612 | 55.4755 | 55.6921 | 63.8655 | 69.5986 | 61.9661 | 60.1147 | 123.1384 | 61.7217 | 123.0696 | 61.3988 | 61.4801 | 123.0209 | 61.4396 | 122.8083 | 61.6583 | 61.6988 | 61.5895 | 61.63
5098.0781 | 123.4085 | -61.4685 | 61.6104 | 0.62547 | -5.9609 | -5.8772 | 2.7404 | 8.185 | 0.62125 | -1.308 | 61.6973 | 0.28526 | 61.6332 | -0.028522 | 0.048236 | 61.5845 | 0.003143 | 61.3627 | 62.094 | 55.5076 | 55.5913 | 64.2089 | 69.6535 | 62.0898 | 60.1605 | 123.1659 | 61.7538 | 123.1017 | 61.44 | 61.5167 | 123.053 | 61.4716 | 122.8312 | 61.6491 | 61.6942 | 61.5849 | 61.63
5099.0625 | 123.4177 | -61.4685 | 61.6287 | 0.63463 | -6.1349 | -6.1794 | 2.6351 | 8.1759 | 0.62583 | -1.3492 | 61.7065 | 0.27611 | 61.6469 | -0.028522 | 0.034501 | 61.5799 | 0.007721 | 61.3718 | 62.1031 | 55.3336 | 55.2891 | 64.1036 | 69.6444 | 62.0943 | 60.1193 | 123.175 | 61.7446 | 123.1154 | 61.44 | 61.503 | 123.0484 | 61.4762 | 122.8403 | 61.672 | 61.6988 | 61.6124 | 61.6392
5100.0781 | 123.3032 | -61.496 | 61.6699 | 0.63005 | -6.2631 | -6.2389 | 2.5573 | 8.2583 | 0.62583 | -1.4362 | 61.7111 | 0.28069 | 61.624 | -0.033101 | 0.043657 | 61.5753 | 0.007721 | 61.3718 | 62.126 | 55.2328 | 55.2571 | 64.0532 | 69.7542 | 62.1218 | 60.0598 | 123.2071 | 61.7767 | 123.12 | 61.4629 | 61.5396 | 123.0713 | 61.5037 | 122.8678 | 61.6674 | 61.7034 | 61.5804 | 61.6163
5101.0625 | 123.3307 | -61.4548 | 61.7203 | 0.53391 | -6.4142 | -6.3167 | 2.5481 | 8.1759 | 0.52053 | -1.5094 | 61.7065 | 0.28069 | 61.6149 | -0.033101 | 0.052814 | 61.5662 | 0.012299 | 61.3764 | 61.9887 | 55.0405 | 55.138 | 64.0029 | 69.6306 | 61.9753 | 59.9454 | 123.1613 | 61.7355 | 123.0696 | 61.4217 | 61.5076 | 123.0209 | 61.4671 | 122.8312 | 61.6537 | 61.6942 | 61.562 | 61.6026
5102.0781 | 123.3719 | -61.4594 | 61.6745 | 0.4286 | -6.5562 | -6.5319 | 2.1131 | 7.9607 | 0.41523 | -1.6285 | 61.7248 | 0.28984 | 61.6515 | -0.023943 | 0.048236 | 61.5616 | 0.007721 | 61.3581 | 61.888 | 54.9032 | 54.9274 | 63.5725 | 69.4201 | 61.8746 | 59.8309 | 123.1842 | 61.7492 | 123.1108 | 61.4354 | 61.5076 | 123.0209 | 61.4671 | 122.8174 | 61.6766 | 61.7171 | 61.6032 | 61.6438
5103.0625 | 123.4085 | -61.4319 | 61.6653 | 0.54764 | -6.3364 | -6.1519 | 2.4245 | 7.9012 | 0.53426 | -1.6101 | 61.7157 | 0.28526 | 61.6469 | -0.028522 | 0.048236 | 61.5753 | 0.003143 | 61.3581 | 61.9795 | 55.0955 | 55.28 | 63.8564 | 69.3331 | 61.9661 | 59.8217 | 123.1475 | 61.7171 | 123.0788 | 61.4034 | 61.4801 | 123.0072 | 61.435 | 122.79 | 61.6674 | 61.7125 | 61.5987 | 61.6438
5104.0781 | 123.317 | -61.4594 | 61.6608 | 0.48812 | -6.6203 | -6.3671 | 2.2642 | 7.8005 | 0.47017 | -1.7292 | 61.7157 | 0.27611 | 61.6561 | -0.033101 | 0.039079 | 61.5662 | 0.003143 | 61.3535 | 61.9475 | 54.8391 | 55.0923 | 63.7236 | 69.2598 | 61.9295 | 59.7302 | 123.175 | 61.7355 | 123.1154 | 61.4262 | 61.4984 | 123.0255 | 61.4625 | 122.8129 | 61.6766 | 61.7125 | 61.617 | 61.6529
5105.0625 | 123.3994 | -61.441 | 61.6608 | 0.57969 | -6.4875 | -6.2893 | 2.3787 | 7.6036 | 0.55716 | -1.601 | 61.7157 | 0.28069 | 61.6194 | -0.028522 | 0.052814 | 61.5662 | 0.012299 | 61.3627 | 62.0207 | 54.9535 | 55.1518 | 63.8197 | 69.0447 | 61.9982 | 59.8401 | 123.1567 | 61.7217 | 123.0605 | 61.4125 | 61.4939 | 123.0072 | 61.4533 | 122.8037 | 61.6628 | 61.7034 | 61.5666 | 61.6071
5106.0938 | 123.3719 | -61.5005 | 61.6882 | 0.5568 | -6.515 | -6.2984 | 2.3833 | 7.7318 | 0.548 | -1.4316 | 61.7202 | 0.28526 | 61.6332 | -0.033101 | 0.039079 | 61.5616 | 0.007721 | 61.3627 | 62.0573 | 54.9856 | 55.2021 | 63.8838 | 69.2324 | 62.0485 | 60.069 | 123.2208 | 61.7858 | 123.1337 | 61.4674 | 61.5396 | 123.0621 | 61.5083 | 122.8632 | 61.6812 | 61.7125 | 61.5941 | 61.6255
5107.0625 | 123.3948 | -61.4319 | 61.6562 | 0.5568 | -6.4646 | -6.1473 | 2.223 | 8.034 | 0.57547 | -1.34 | 61.7157 | 0.28069 | 61.6515 | -0.03768 | 0.052814 | 61.5753 | 0.012299 | 61.3672 | 61.9887 | 54.9673 | 55.2846 | 63.6549 | 69.4658 | 62.0074 | 60.0919 | 123.1475 | 61.7126 | 123.0834 | 61.3942 | 61.4847 | 123.0072 | 61.4442 | 122.7991 | 61.6628 | 61.7034 | 61.5987 | 61.6392
5108.0781 | 123.2574 | -61.4777 | 61.6653 | 0.47439 | -6.2631 | -6.0832 | 2.2047 | 7.9241 | 0.50222 | -1.1844 | 61.7157 | 0.28069 | 61.6469 | -0.033101 | 0.048236 | 61.5753 | 0.007721 | 61.3627 | 61.952 | 55.2145 | 55.3944 | 63.6824 | 69.4017 | 61.9799 | 60.2933 | 123.1933 | 61.7583 | 123.1246 | 61.4446 | 61.5259 | 123.053 | 61.4854 | 122.8403 | 61.6674 | 61.7079 | 61.5987 | 61.6392
5109.0625 | 123.4131 | -61.4319 | 61.6562 | 0.38282 | -6.4142 | -6.1931 | 2.1223 | 7.8875 | 0.41523 | -1.2805 | 61.7157 | 0.28984 | 61.624 | -0.03768 | 0.052814 | 61.5662 | 0.007721 | 61.3672 | 61.8147 | 55.0177 | 55.2388 | 63.5542 | 69.3193 | 61.8471 | 60.1514 | 123.1475 | 61.7217 | 123.0559 | 61.3942 | 61.4847 | 122.998 | 61.4396 | 122.7991 | 61.6628 | 61.7079 | 61.5712 | 61.6163
5110.0938 | 123.3444 | -61.4594 | 61.6699 | 0.36451 | -6.341 | -6.2068 | 1.9208 | 7.947 | 0.47017 | -1.1615 | 61.7157 | 0.28069 | 61.6194 | -0.028522 | 0.043657 | 61.5753 | 0.007721 | 61.3718 | 61.8239 | 55.1184 | 55.2525 | 63.3802 | 69.4063 | 61.9295 | 60.2979 | 123.175 | 61.74 | 123.0788 | 61.4308 | 61.503 | 123.0347 | 61.4671 | 122.8312 | 61.672 | 61.7079 | 61.5758 | 61.6117
5111.0625 | 123.3261 | -61.4502 | 61.6608 | 0.43318 | -6.373 | -6.2984 | 1.8842 | 8.1072 | 0.43354 | -1.0012 | 61.7157 | 0.28069 | 61.6606 | -0.023943 | 0.043657 | 61.5707 | 0.007721 | 61.3718 | 61.8834 | 55.0772 | 55.1518 | 63.3344 | 69.5574 | 61.8837 | 60.449 | 123.1659 | 61.7309 | 123.1108 | 61.4263 | 61.4939 | 123.0209 | 61.4579 | 122.822 | 61.672 | 61.7079 | 61.617 | 61.6529
5112.0938 | 123.3765 | -61.4731 | 61.6333 | 0.41029 | -6.5058 | -6.3763 | 1.8934 | 8.1713 | 0.40149 | -0.91426 | 61.7157 | 0.28069 | 61.6561 | -0.042259 | 0.048236 | 61.5753 | 0.007721 | 61.3672 | 61.8834 | 54.9673 | 55.0968 | 63.3665 | 69.6444 | 61.8746 | 60.5588 | 123.1887 | 61.7538 | 123.1291 | 61.4308 | 61.5213 | 123.0484 | 61.4808 | 122.8403 | 61.6674 | 61.7079 | 61.6078 | 61.6483
5113.0625 | 123.3856 | -61.4548 | 61.6745 | 0.40571 | -6.3318 | -6.2297 | 1.9071 | 8.2308 | 0.42438 | -0.77233 | 61.7019 | 0.28526 | 61.624 | -0.033101 | 0.043657 | 61.5753 | 0.012299 | 61.3764 | 61.8605 | 55.123 | 55.225 | 63.3619 | 69.6856 | 61.8792 | 60.6824 | 123.1567 | 61.74 | 123.0788 | 61.4217 | 61.4984 | 123.0301 | 61.4671 | 122.8312 | 61.6583 | 61.6896 | 61.5804 | 61.6117
5114.0938 | 123.3398 | -61.4639 | 61.6516 | 0.50186 | -6.1212 | -5.9871 | 1.7377 | 8.4094 | 0.52511 | -0.72655 | 61.7019 | 0.28069 | 61.6149 | -0.033101 | 0.043657 | 61.5799 | 0.003143 | 61.3764 | 61.9658 | 55.3427 | 55.4769 | 63.2016 | 69.8733 | 61.989 | 60.7374 | 123.1659 | 61.7446 | 123.0788 | 61.4308 | 61.5076 | 123.0438 | 61.4671 | 122.8403 | 61.6583 | 61.6988 | 61.5712 | 61.6117
5115.0625 | 123.4085 | -61.4273 | 61.647 | 0.54764 | -6.2082 | -5.9871 | 1.9712 | 8.5787 | 0.58463 | -0.80896 | 61.7111 | 0.28526 | 61.6423 | -0.033101 | 0.048236 | 61.5891 | 0.007721 | 61.3901 | 61.9749 | 55.2191 | 55.4402 | 63.3985 | 70.006 | 62.0119 | 60.6183 | 123.1384 | 61.7126 | 123.0696 | 61.3942 | 61.4755 | 123.0164 | 61.435 | 122.8174 | 61.6628 | 61.7034 | 61.5941 | 61.6346
5116.1094 | 123.4131 | -61.4777 | 61.6425 | 0.57969 | -6.2173 | -5.9733 | 1.8888 | 8.8671 | 0.58005 | -0.83643 | 61.7065 | 0.28526 | 61.6423 | -0.023943 | 0.043657 | 61.5891 | 0.012299 | 61.3764 | 62.0574 | 55.2603 | 55.5043 | 63.3665 | 70.3448 | 62.0577 | 60.6412 | 123.1842 | 61.7629 | 123.12 | 61.4537 | 61.5213 | 123.0667 | 61.49 | 122.8541 | 61.6628 | 61.6942 | 61.5987 | 61.63
5117.0625 | 123.3536 | -61.4731 | 61.6562 | 0.598 | -6.2677 | -5.9504 | 1.9483 | 8.7985 | 0.60752 | -0.91426 | 61.7019 | 0.28069 | 61.6103 | -0.019364 | 0.048236 | 61.5845 | 0.012299 | 61.3764 | 62.0711 | 55.2054 | 55.5226 | 63.4214 | 70.2716 | 62.0806 | 60.5588 | 123.175 | 61.7538 | 123.0834 | 61.4537 | 61.5213 | 123.0576 | 61.4854 | 122.8495 | 61.6537 | 61.6896 | 61.562 | 61.598
5118.0938 | 123.3398 | -61.4914 | 61.6379 | 0.58885 | -6.1945 | -5.9504 | 1.811 | 8.6199 | 0.62125 | -0.97835 | 61.6973 | 0.28069 | 61.6103 | -0.03768 | 0.048236 | 61.5845 | 0.012299 | 61.3718 | 62.0802 | 55.2969 | 55.5409 | 63.3024 | 70.1113 | 62.1126 | 60.513 | 123.1887 | 61.7721 | 123.1017 | 61.4537 | 61.5396 | 123.0759 | 61.5037 | 122.8632 | 61.6491 | 61.685 | 61.562 | 61.598
5119.0625 | 123.3948 | -61.4685 | 61.6562 | 0.47439 | -6.3089 | -6.0054 | 1.7285 | 8.4643 | 0.43812 | -1.1798 | 61.7111 | 0.28984 | 61.6469 | -0.028522 | 0.048236 | 61.5707 | 0.007721 | 61.3672 | 61.9429 | 55.1596 | 55.4631 | 63.1971 | 69.9328 | 61.9066 | 60.2887 | 123.1796 | 61.7583 | 123.1154 | 61.44 | 61.5167 | 123.0392 | 61.4762 | 122.8357 | 61.6628 | 61.7034 | 61.5987 | 61.6392
5120.0781 | 123.3673 | -61.4731 | 61.6379 | 0.41487 | -6.3501 | -6.0649 | 1.811 | 8.3636 | 0.37402 | -1.1432 | 61.7202 | 0.28984 | 61.6515 | -0.028522 | 0.043657 | 61.5753 | 0.003143 | 61.3535 | 61.888 | 55.123 | 55.4082 | 63.284 | 69.8367 | 61.8471 | 60.3299 | 123.1933 | 61.7629 | 123.1246 | 61.4446 | 61.5167 | 123.0484 | 61.4762 | 122.8266 | 61.6766 | 61.7171 | 61.6078 | 61.6483
5121.0625 | 123.4039 | -61.4136 | 61.6791 | 0.46065 | -6.3913 | -6.1611 | 1.8476 | 8.5879 | 0.40607 | -0.91884 | 61.7065 | 0.28069 | 61.6149 | -0.028522 | 0.043657 | 61.5753 | 0.003143 | 61.3718 | 61.8742 | 55.0222 | 55.2525 | 63.2612 | 70.0015 | 61.8196 | 60.4947 | 123.1201 | 61.6943 | 123.0284 | 61.3851 | 61.4572 | 122.9889 | 61.4167 | 122.7854 | 61.6628 | 61.7034 | 61.5712 | 61.6117
5122.0781 | 123.2803 | -61.4685 | 61.6974 | 0.35535 | -6.6478 | -6.3305 | 1.6187 | 8.3407 | 0.31908 | -1.2027 | 61.7111 | 0.28984 | 61.6332 | -0.033101 | 0.043657 | 61.5662 | 0.012299 | 61.3535 | 61.8239 | 54.8208 | 55.138 | 63.0872 | 69.8092 | 61.7876 | 60.2658 | 123.1796 | 61.7583 | 123.1017 | 61.4354 | 61.5122 | 123.0347 | 61.4808 | 122.822 | 61.6674 | 61.6988 | 61.5895 | 61.6209
5123.0625 | 123.3444 | -61.4731 | 61.6745 | 0.45607 | -6.6569 | -6.3625 | 1.5591 | 8.5742 | 0.41523 | -1.2485 | 61.7248 | 0.28526 | 61.6515 | -0.033101 | 0.043657 | 61.5707 | -0.001436 | 61.3535 | 61.9292 | 54.8162 | 55.1106 | 63.0322 | 70.0472 | 61.8883 | 60.2246 | 123.1979 | 61.7583 | 123.1246 | 61.44 | 61.5167 | 123.0438 | 61.4716 | 122.8266 | 61.6812 | 61.7263 | 61.6078 | 61.6529
5124.0781 | 123.2986 | -61.4731 | 61.6928 | 0.5568 | -6.5379 | -6.2893 | 1.5775 | 8.6428 | 0.50679 | -1.0562 | 61.7202 | 0.28526 | 61.6515 | -0.033101 | 0.048236 | 61.5753 | 0.003143 | 61.3764 | 62.0299 | 54.9352 | 55.1838 | 63.0505 | 70.1159 | 61.9799 | 60.4169 | 123.1933 | 61.7583 | 123.1246 | 61.44 | 61.5213 | 123.0484 | 61.4762 | 122.8495 | 61.672 | 61.7171 | 61.6032 | 61.6483
5125.0625 | 123.3536 | -61.4548 | 61.6562 | 0.51559 | -6.5608 | -6.4358 | 1.495 | 8.5513 | 0.4839 | -1.134 | 61.7111 | 0.28526 | 61.624 | -0.033101 | 0.048236 | 61.5707 | 0.007721 | 61.3581 | 61.9704 | 54.894 | 55.019 | 62.9498 | 70.006 | 61.9387 | 60.3208 | 123.1659 | 61.74 | 123.0788 | 61.4217 | 61.503 | 123.0255 | 61.4625 | 122.8129 | 61.6628 | 61.7034 | 61.5758 | 61.6163
5126.0938 | 123.317 | -61.4914 | 61.6791 | 0.58427 | -6.721 | -6.509 | 1.5408 | 8.5604 | 0.548 | -1.2118 | 61.7111 | 0.28526 | 61.624 | -0.023943 | 0.043657 | 61.5707 | 0.003143 | 61.3581 | 62.0757 | 54.7704 | 54.9824 | 63.0322 | 70.0518 | 62.0394 | 60.2796 | 123.2025 | 61.7767 | 123.1154 | 61.4675 | 61.5351 | 123.0621 | 61.4945 | 122.8495 | 61.6674 | 61.7079 | 61.5804 | 61.6209
5127.0625 | 123.3719 | -61.4777 | 61.647 | 0.68957 | -6.634 | -6.5182 | 1.4996 | 8.6611 | 0.6533 | -1.1981 | 61.7202 | 0.28069 | 61.6561 | -0.03768 | 0.043657 | 61.5753 | -0.001436 | 61.3581 | 62.1672 | 54.8436 | 54.9595 | 62.9773 | 70.1388 | 62.131 | 60.2796 | 123.1979 | 61.7583 | 123.1337 | 61.44 | 61.5213 | 123.053 | 61.4762 | 122.8357 | 61.6766 | 61.7217 | 61.6124 | 61.6575
5128.0781 | 123.2941 | -61.4777 | 61.6745 | 0.5568 | -6.7073 | -6.6189 | 1.3394 | 8.4734 | 0.51137 | -1.2485 | 61.7294 | 0.28526 | 61.6652 | -0.028522 | 0.043657 | 61.5662 | 0.007721 | 61.3535 | 62.0345 | 54.7704 | 54.8587 | 62.817 | 69.9511 | 61.989 | 60.2292 | 123.2071 | 61.7629 | 123.1429 | 61.4491 | 61.5213 | 123.0438 | 61.4854 | 122.8312 | 61.6857 | 61.7217 | 61.6216 | 61.6575
5129.0625 | 123.4177 | -61.4548 | 61.6379 | 0.57511 | -6.6111 | -6.5823 | 1.4676 | 8.533 | 0.53884 | -1.134 | 61.7157 | 0.28526 | 61.6515 | -0.042259 | 0.048236 | 61.5662 | 0.003143 | 61.3672 | 62.0299 | 54.8437 | 54.8725 | 62.9223 | 69.9877 | 61.9936 | 60.3208 | 123.1704 | 61.74 | 123.1063 | 61.4125 | 61.503 | 123.0209 | 61.4579 | 122.822 | 61.6674 | 61.7125 | 61.6032 | 61.6483
5130.0781 | 123.3627 | -61.4731 | 61.6562 | 0.70331 | -6.3868 | -6.422 | 1.4401 | 8.7619 | 0.68535 | -1.0608 | 61.7111 | 0.28069 | 61.6286 | -0.03768 | 0.052814 | 61.5799 | 0.003143 | 61.3672 | 62.1764 | 55.0863 | 55.051 | 62.9132 | 70.2349 | 62.1584 | 60.4123 | 123.1842 | 61.7538 | 123.1017 | 61.4354 | 61.5259 | 123.053 | 61.4762 | 122.8403 | 61.6583 | 61.7079 | 61.5758 | 61.6255
5131.0625 | 123.3536 | -61.4365 | 61.647 | 0.57969 | -6.6478 | -6.5182 | 1.3394 | 8.5604 | 0.54342 | -1.0699 | 61.7111 | 0.27611 | 61.6194 | -0.03768 | 0.048236 | 61.5662 | 0.007721 | 61.3581 | 62.0162 | 54.7887 | 54.9183 | 62.7758 | 69.9969 | 61.9799 | 60.3665 | 123.1475 | 61.7126 | 123.0559 | 61.3988 | 61.4847 | 123.0026 | 61.4442 | 122.7945 | 61.6628 | 61.7034 | 61.5712 | 61.6117
5132.0938 | 123.3765 | -61.4594 | 61.6379 | 0.57969 | -6.6615 | -6.1931 | 1.1929 | 8.5238 | 0.54342 | -1.0333 | 61.7111 | 0.28069 | 61.6149 | -0.033101 | 0.039079 | 61.5662 | 0.007721 | 61.3489 | 62.039 | 54.7979 | 55.2662 | 62.6522 | 69.9832 | 62.0028 | 60.4261 | 123.1704 | 61.74 | 123.0742 | 61.4262 | 61.4984 | 123.0255 | 61.4671 | 122.8083 | 61.672 | 61.7034 | 61.5758 | 61.6071
5133.0625 | 123.381 | -61.4319 | 61.6333 | 0.52475 | -6.8401 | -5.8863 | 0.70754 | 8.4918 | 0.4839 | -1.1661 | 61.7202 | 0.28526 | 61.6332 | -0.033101 | 0.048236 | 61.5616 | 0.007721 | 61.3535 | 61.9566 | 54.5918 | 55.5455 | 62.1394 | 69.9236 | 61.9158 | 60.2658 | 123.1521 | 61.7171 | 123.0651 | 61.3988 | 61.4801 | 122.9935 | 61.4396 | 122.7854 | 61.672 | 61.7125 | 61.5849 | 61.6255
5134.0938 | 123.2666 | -61.4548 | 61.6928 | 0.63005 | -6.7622 | -5.7215 | 0.58392 | 8.6749 | 0.60294 | -1.1798 | 61.7202 | 0.28069 | 61.6561 | -0.033101 | 0.048236 | 61.5707 | 0.007721 | 61.3489 | 62.0848 | 54.6925 | 55.7333 | 62.0387 | 70.1296 | 62.0577 | 60.275 | 123.175 | 61.7355 | 123.1108 | 61.4217 | 61.503 | 123.0255 | 61.4625 | 122.8037 | 61.672 | 61.7125 | 61.6078 | 61.6483
5135.0625 | 123.3856 | -61.4273 | 61.6241 | 0.70788 | -6.5745 | -5.7902 | 1.1196 | 8.8488 | 0.68077 | -1.1203 | 61.7111 | 0.28984 | 61.6515 | -0.023943 | 0.052814 | 61.5753 | 0.003143 | 61.3627 | 62.1352 | 54.8528 | 55.6371 | 62.5469 | 70.2761 | 62.1081 | 60.307 | 123.1384 | 61.7171 | 123.0788 | 61.4034 | 61.4801 | 123.0026 | 61.4305 | 122.79 | 61.6583 | 61.7079 | 61.5987 | 61.6483
5136.1094 | 123.2712 | -61.4639 | 61.6516 | 0.75367 | -6.4051 | -5.9779 | 1.4447 | 9.0228 | 0.72656 | -1.102 | 61.7111 | 0.28069 | 61.6423 | -0.033101 | 0.048236 | 61.5799 | 0.012299 | 61.3672 | 62.2176 | 55.0589 | 55.486 | 62.9086 | 70.4867 | 62.1905 | 60.362 | 123.175 | 61.7446 | 123.1063 | 61.4308 | 61.5122 | 123.0438 | 61.4762 | 122.8312 | 61.6628 | 61.6988 | 61.5941 | 61.63
5137.0625 | 123.381 | -61.4456 | 61.6058 | 0.68499 | -6.4738 | -5.9871 | 1.6232 | 8.89 | 0.68535 | -1.2256 | 61.7065 | 0.28069 | 61.6286 | -0.03768 | 0.048236 | 61.5845 | 0.007721 | 61.3627 | 62.1306 | 54.9719 | 55.4585 | 63.0689 | 70.3357 | 62.131 | 60.22 | 123.1521 | 61.7263 | 123.0742 | 61.4079 | 61.4939 | 123.0301 | 61.4533 | 122.8083 | 61.6583 | 61.6988 | 61.5804 | 61.6209
5138.0938 | 123.2437 | -61.5051 | 61.6745 | 0.66668 | -6.4967 | -5.9596 | 1.7423 | 8.7207 | 0.64872 | -1.221 | 61.7019 | 0.28526 | 61.6149 | -0.033101 | 0.039079 | 61.5845 | 0.003143 | 61.3581 | 62.1718 | 55.0085 | 55.5455 | 63.2474 | 70.2258 | 62.1539 | 60.2841 | 123.2071 | 61.7904 | 123.12 | 61.472 | 61.5442 | 123.0896 | 61.5083 | 122.8632 | 61.6628 | 61.6988 | 61.5758 | 61.6117
5139.0625 | 123.3765 | -61.4685 | 61.6379 | 0.56595 | -6.6615 | -5.7398 | 1.4676 | 8.6428 | 0.54342 | -1.2576 | 61.7111 | 0.27153 | 61.6057 | -0.033101 | 0.029923 | 61.5753 | 0.003143 | 61.3627 | 62.0345 | 54.807 | 55.7287 | 62.9361 | 70.1113 | 62.0119 | 60.2109 | 123.1796 | 61.74 | 123.0742 | 61.4354 | 61.4984 | 123.0438 | 61.4716 | 122.8312 | 61.6812 | 61.7079 | 61.5758 | 61.6026
5140.0781 | 123.3124 | -61.4639 | 61.6928 | 0.68041 | -6.3547 | -6.097 | 1.4859 | 8.8534 | 0.63041 | -1.0379 | 61.7065 | 0.28526 | 61.6149 | -0.033101 | 0.043657 | 61.5799 | 0.012299 | 61.3672 | 62.1443 | 55.1092 | 55.367 | 62.9498 | 70.3173 | 62.0943 | 60.4261 | 123.1704 | 61.7492 | 123.0788 | 61.4308 | 61.5076 | 123.0438 | 61.4762 | 122.8312 | 61.6628 | 61.6942 | 61.5712 | 61.6026
5141.0625 | 123.4497 | -61.4044 | 61.6837 | 0.56138 | -6.5241 | -6.1702 | 1.2936 | 8.7573 | 0.51595 | -1.1889 | 61.7157 | 0.28069 | 61.6423 | -0.028522 | 0.052814 | 61.5707 | 0.012299 | 61.3581 | 61.9658 | 54.8803 | 55.2342 | 62.698 | 70.1617 | 61.9204 | 60.2155 | 123.1201 | 61.6851 | 123.0467 | 61.3759 | 61.4572 | 122.9752 | 61.4167 | 122.7625 | 61.6628 | 61.7034 | 61.5895 | 61.63
5142.0938 | 123.2986 | -61.4502 | 61.6699 | 0.58885 | -6.3639 | -6.0649 | 1.1104 | 8.7619 | 0.55716 | -1.221 | 61.7111 | 0.28069 | 61.6561 | -0.033101 | 0.048236 | 61.5707 | 0.012299 | 61.3627 | 62.039 | 55.0863 | 55.3853 | 62.5606 | 70.212 | 62.0074 | 60.2292 | 123.1613 | 61.7309 | 123.1063 | 61.4171 | 61.4984 | 123.0209 | 61.4625 | 122.8129 | 61.6628 | 61.6988 | 61.6078 | 61.6438
5143.0625 | 123.2574 | -61.4731 | 61.6699 | 0.54764 | -6.5653 | -6.2435 | 1.2615 | 8.7756 | 0.50679 | -1.4041 | 61.7202 | 0.28069 | 61.6561 | -0.028522 | 0.048236 | 61.5753 | -0.001436 | 61.3489 | 62.0207 | 54.9077 | 55.2296 | 62.7346 | 70.2487 | 61.9799 | 60.069 | 123.1933 | 61.7538 | 123.1291 | 61.4446 | 61.5213 | 123.0484 | 61.4716 | 122.822 | 61.672 | 61.7217 | 61.6078 | 61.6575
5144.0781 | 123.349 | -61.4502 | 61.7065 | 0.64379 | -6.5424 | -6.2847 | 1.1196 | 8.9129 | 0.60752 | -1.2576 | 61.7157 | 0.28526 | 61.6423 | -0.023943 | 0.043657 | 61.5753 | 0.012299 | 61.3581 | 62.094 | 54.9078 | 55.1655 | 62.5698 | 70.3631 | 62.0577 | 60.1926 | 123.1659 | 61.7355 | 123.0925 | 61.4263 | 61.4939 | 123.0255 | 61.4625 | 122.8083 | 61.672 | 61.7034 | 61.5987 | 61.63
5145.0625 | 123.2758 | -61.4639 | 61.6882 | 0.48354 | -6.5745 | -6.4266 | 0.909 | 8.7023 | 0.45185 | -1.3354 | 61.7157 | 0.27611 | 61.624 | -0.028522 | 0.048236 | 61.5616 | 0.007721 | 61.3581 | 61.9475 | 54.8894 | 55.0373 | 62.3729 | 70.1663 | 61.9158 | 60.1285 | 123.1796 | 61.74 | 123.0879 | 61.4354 | 61.5122 | 123.0255 | 61.4716 | 122.822 | 61.6674 | 61.7079 | 61.5758 | 61.6163
5146.0938 | 123.2758 | -61.4319 | 61.7615 | 0.31872 | -6.9316 | -6.4907 | 0.87237 | 8.2857 | 0.30992 | -1.4636 | 61.7294 | 0.28069 | 61.6332 | -0.028522 | 0.039079 | 61.5524 | 0.007721 | 61.3443 | 61.7506 | 54.5002 | 54.9412 | 62.3043 | 69.7176 | 61.7418 | 59.9682 | 123.1613 | 61.7126 | 123.0651 | 61.4034 | 61.471 | 122.9843 | 61.4396 | 122.7762 | 61.6903 | 61.7217 | 61.5941 | 61.6255
5147.0625 | 123.3398 | -61.4502 | 61.6974 | 0.3233 | -6.9271 | -6.4953 | 0.822 | 8.2308 | 0.31908 | -1.4087 | 61.734 | 0.28526 | 61.6423 | -0.033101 | 0.043657 | 61.557 | -0.001436 | 61.3398 | 61.7735 | 54.5231 | 54.9549 | 62.2722 | 69.681 | 61.7693 | 60.0415 | 123.1842 | 61.7355 | 123.0925 | 61.4171 | 61.4939 | 123.0072 | 61.4488 | 122.79 | 61.6903 | 61.7354 | 61.5987 | 61.6438
5148.0938 | 123.2346 | -61.4685 | 61.7065 | 0.50186 | -6.6844 | -6.5045 | 0.8449 | 8.24 | 0.47475 | -1.5369 | 61.7248 | 0.28526 | 61.6561 | -0.033101 | 0.048236 | 61.557 | 0.012299 | 61.3535 | 61.9704 | 54.7841 | 54.964 | 62.3134 | 69.7085 | 61.9433 | 59.9316 | 123.1933 | 61.7538 | 123.1246 | 61.4354 | 61.5167 | 123.0255 | 61.4808 | 122.822 | 61.6766 | 61.7125 | 61.6078 | 61.6438
5149.0625 | 123.2895 | -61.4777 | 61.6791 | 0.64379 | -6.3822 | -6.5228 | 0.75791 | 8.3498 | 0.63499 | -1.5048 | 61.7294 | 0.28069 | 61.6698 | -0.028522 | 0.048236 | 61.5616 | 0.012299 | 61.3627 | 62.1214 | 55.0955 | 54.9549 | 62.2356 | 69.8275 | 62.1126 | 59.9728 | 123.2071 | 61.7583 | 123.1475 | 61.4491 | 61.5259 | 123.0392 | 61.49 | 122.8403 | 61.6812 | 61.7171 | 61.6216 | 61.6575
5150.0781 | 123.2758 | -61.4639 | 61.7203 | 0.69415 | -6.3639 | -6.509 | 0.91358 | 8.4277 | 0.74945 | -1.4362 | 61.7157 | 0.28069 | 61.6332 | -0.028522 | 0.057392 | 61.5662 | 0.003143 | 61.3581 | 62.1581 | 55.1001 | 54.9549 | 62.3775 | 69.8916 | 62.2134 | 60.0278 | 123.1796 | 61.7446 | 123.0971 | 61.4354 | 61.5213 | 123.0301 | 61.4671 | 122.822 | 61.6583 | 61.7125 | 61.5758 | 61.63
5151.0625 | 123.3398 | -61.441 | 61.6516 | 0.48812 | -6.3181 | -6.4312 | 0.77164 | 8.1759 | 0.53884 | -1.5232 | 61.7248 | 0.28069 | 61.6286 | -0.028522 | 0.043657 | 61.5616 | 0.003143 | 61.3535 | 61.9292 | 55.123 | 55.0098 | 62.2127 | 69.6169 | 61.9799 | 59.9179 | 123.1659 | 61.7217 | 123.0696 | 61.4125 | 61.4847 | 123.0026 | 61.4442 | 122.7945 | 61.6812 | 61.7217 | 61.5849 | 61.6255
5152.0938 | 123.3948 | -61.4182 | 61.7249 | 0.50186 | -6.1258 | -6.2664 | 0.025347 | 8.4231 | 0.49764 | -1.601 | 61.7248 | 0.27611 | 61.6606 | -0.028522 | 0.043657 | 61.5524 | 0.007721 | 61.3489 | 61.92 | 55.2924 | 55.1518 | 61.4435 | 69.8412 | 61.9158 | 59.8172 | 123.143 | 61.6943 | 123.0788 | 61.3896 | 61.4618 | 122.9706 | 61.4259 | 122.7671 | 61.6812 | 61.7171 | 61.617 | 61.6529
5153.0625 | 123.3353 | -61.4548 | 61.6974 | 0.65752 | -6.1212 | -6.303 | 0.40994 | 8.6978 | 0.62583 | -1.4774 | 61.7202 | 0.28526 | 61.6561 | -0.028522 | 0.048236 | 61.5707 | 0.007721 | 61.3535 | 62.1123 | 55.3336 | 55.1518 | 61.8647 | 70.1525 | 62.0806 | 59.9774 | 123.175 | 61.74 | 123.1108 | 61.4263 | 61.503 | 123.0255 | 61.4625 | 122.8083 | 61.672 | 61.7125 | 61.6078 | 61.6483
5154.0781 | 123.2803 | -61.4594 | 61.7203 | 0.76282 | -6.0479 | -6.1702 | 0.68465 | 8.8122 | 0.73571 | -1.3675 | 61.7202 | 0.28984 | 61.6561 | -0.028522 | 0.052814 | 61.5799 | 0.012299 | 61.3672 | 62.2222 | 55.4114 | 55.2891 | 62.144 | 70.2716 | 62.1951 | 60.0919 | 123.1796 | 61.7492 | 123.1154 | 61.4308 | 61.5122 | 123.0392 | 61.4716 | 122.8266 | 61.6674 | 61.7079 | 61.6032 | 61.6438
5155.0625 | 123.3353 | -61.4502 | 61.7065 | 0.61632 | -6.0662 | -6.3625 | 0.77622 | 8.6611 | 0.64415 | -1.3858 | 61.7248 | 0.28069 | 61.6469 | -0.028522 | 0.048236 | 61.5707 | 0.007721 | 61.3718 | 62.0665 | 55.384 | 55.0877 | 62.2264 | 70.1113 | 62.0943 | 60.0644 | 123.175 | 61.7309 | 123.0971 | 61.4217 | 61.4984 | 123.0209 | 61.4579 | 122.822 | 61.6766 | 61.7171 | 61.5987 | 61.6392
5156.0938 | 123.4131 | -61.4319 | 61.6379 | 0.47439 | -6.2128 | -6.39 | 0.91815 | 8.652 | 0.68993 | -1.4362 | 61.7157 | 0.28526 | 61.6423 | -0.033101 | 0.043657 | 61.5707 | 0.003143 | 61.3581 | 61.9063 | 55.2191 | 55.0419 | 62.35 | 70.0839 | 62.1218 | 59.9957 | 123.1475 | 61.7171 | 123.0742 | 61.3988 | 61.4755 | 123.0026 | 61.435 | 122.79 | 61.672 | 61.7125 | 61.5987 | 61.6392
5157.0625 | 123.3124 | -61.4548 | 61.6882 | 0.57969 | -6.2677 | -6.3076 | 1.0784 | 8.6795 | 0.59378 | -1.3858 | 61.7065 | 0.28069 | 61.6194 | -0.019364 | 0.043657 | 61.5753 | 0.012299 | 61.3672 | 62.0345 | 55.1871 | 55.1472 | 62.5332 | 70.1342 | 62.0486 | 60.069 | 123.1613 | 61.7355 | 123.0742 | 61.4354 | 61.4984 | 123.0301 | 61.4671 | 122.822 | 61.6628 | 61.6942 | 61.5758 | 61.6071
5158.0938 | 123.4039 | -61.4365 | 61.6699 | 0.45607 | -6.2586 | -6.3076 | 1.0738 | 8.4048 | 0.4427 | -1.5186 | 61.7202 | 0.28069 | 61.6103 | -0.028522 | 0.048236 | 61.5662 | 0.007721 | 61.3581 | 61.8925 | 55.1779 | 55.1289 | 62.5103 | 69.8412 | 61.8792 | 59.9179 | 123.1567 | 61.7171 | 123.0467 | 61.4079 | 61.4847 | 123.0026 | 61.4442 | 122.7945 | 61.672 | 61.7125 | 61.562 | 61.6026
5159.0625 | 123.3536 | -61.4273 | 61.7111 | 0.39655 | -6.4051 | -6.5502 | 0.9731 | 8.3178 | 0.3786 | -1.5964 | 61.7248 | 0.28526 | 61.6469 | -0.023943 | 0.052814 | 61.557 | 0.012299 | 61.3489 | 61.8239 | 55.0222 | 54.8771 | 62.4004 | 69.7451 | 61.8059 | 59.8309 | 123.1521 | 61.7126 | 123.0742 | 61.4034 | 61.4801 | 122.9843 | 61.4396 | 122.7762 | 61.672 | 61.7125 | 61.5941 | 61.6346
5160.0938 | 123.2941 | -61.4456 | 61.6882 | 0.40571 | -6.5241 | -6.3625 | 1.0006 | 8.4277 | 0.38776 | -1.6147 | 61.7294 | 0.28069 | 61.6561 | -0.028522 | 0.048236 | 61.5616 | 0.012299 | 61.3535 | 61.8513 | 54.9215 | 55.0831 | 62.4462 | 69.8733 | 61.8334 | 59.8309 | 123.175 | 61.7263 | 123.1017 | 61.4171 | 61.4939 | 123.0072 | 61.4579 | 122.7991 | 61.6812 | 61.7171 | 61.6078 | 61.6438
5161.0625 | 123.262 | -61.4914 | 61.7203 | 0.37366 | -6.6203 | -6.3167 | 0.92273 | 8.4643 | 0.42896 | -1.7154 | 61.7294 | 0.28069 | 61.6652 | -0.028522 | 0.048236 | 61.557 | 0.003143 | 61.3581 | 61.8651 | 54.8711 | 55.1747 | 62.4141 | 69.9557 | 61.9204 | 59.776 | 123.2208 | 61.7721 | 123.1566 | 61.4629 | 61.5396 | 123.0484 | 61.4945 | 122.8495 | 61.6812 | 61.7263 | 61.617 | 61.6621
5162.0625 | 123.3078 | -61.4319 | 61.7203 | 0.33246 | -6.7714 | -6.1061 | 0.73043 | 8.3636 | 0.42438 | -1.6971 | 61.7386 | 0.28984 | 61.6744 | -0.028522 | 0.052814 | 61.557 | 0.007721 | 61.3398 | 61.7643 | 54.6605 | 55.3258 | 62.1623 | 69.7955 | 61.8563 | 59.7348 | 123.1704 | 61.7217 | 123.1063 | 61.4034 | 61.4847 | 122.9889 | 61.4396 | 122.7717 | 61.6857 | 61.7308 | 61.6216 | 61.6667
5163.0938 | 123.2712 | -61.4822 | 61.7111 | 0.41945 | -6.9087 | -5.8726 | 0.75333 | 8.4643 | 0.39233 | -1.6193 | 61.7202 | 0.28984 | 61.6698 | -0.033101 | 0.052814 | 61.557 | 0.016878 | 61.3398 | 61.9017 | 54.5735 | 55.6096 | 62.2356 | 69.9465 | 61.8746 | 59.8629 | 123.2025 | 61.7721 | 123.152 | 61.4491 | 61.5351 | 123.0392 | 61.4991 | 122.822 | 61.6674 | 61.7034 | 61.617 | 61.6529
5164.0625 | 123.349 | -61.4502 | 61.6837 | 0.36908 | -6.8904 | -5.9779 | 0.85863 | 8.5879 | 0.47017 | -1.5689 | 61.7248 | 0.28984 | 61.6469 | -0.033101 | 0.052814 | 61.557 | 0.007721 | 61.3581 | 61.8193 | 54.5598 | 55.4723 | 62.3088 | 70.0381 | 61.9204 | 59.8813 | 123.175 | 61.74 | 123.0971 | 61.4171 | 61.503 | 123.0072 | 61.4579 | 122.8083 | 61.672 | 61.7171 | 61.5941 | 61.6392
5165.0781 | 123.4451 | -61.4136 | 61.6516 | 0.46981 | -6.7073 | -6.0695 | 0.84948 | 8.5055 | 0.50679 | -1.2439 | 61.7111 | 0.28526 | 61.624 | -0.023943 | 0.048236 | 61.5662 | 0.007721 | 61.3627 | 61.8834 | 54.7063 | 55.3441 | 62.263 | 69.9191 | 61.9204 | 60.1697 | 123.1247 | 61.6988 | 123.0376 | 61.3896 | 61.4618 | 122.9797 | 61.4213 | 122.7762 | 61.6628 | 61.7034 | 61.5758 | 61.6163
5166.0625 | 123.2941 | -61.4685 | 61.7065 | 0.60716 | -6.895 | -6.2618 | 1.0097 | 8.5284 | 0.57547 | -1.2759 | 61.7294 | 0.28069 | 61.6377 | -0.033101 | 0.052814 | 61.557 | 0.003143 | 61.3581 | 62.0757 | 54.5735 | 55.2067 | 62.4782 | 69.9969 | 62.044 | 60.1926 | 123.1979 | 61.7492 | 123.1063 | 61.4354 | 61.5213 | 123.0255 | 61.4716 | 122.8266 | 61.6766 | 61.7263 | 61.5849 | 61.6346
5167.0938 | 123.2712 | -61.4456 | 61.7249 | 0.56138 | -6.9957 | -6.5915 | 1.0235 | 8.5192 | 0.53426 | -1.3629 | 61.734 | 0.28069 | 61.6698 | -0.033101 | 0.048236 | 61.5616 | 0.007721 | 61.3535 | 62.007 | 54.4499 | 54.8542 | 62.4691 | 69.9648 | 61.9799 | 60.0827 | 123.1796 | 61.7263 | 123.1154 | 61.4125 | 61.4939 | 123.0072 | 61.4533 | 122.7991 | 61.6857 | 61.7263 | 61.6216 | 61.6621
5168.0625 | 123.3124 | -61.4502 | 61.7065 | 0.58427 | -7.1652 | -6.5731 | 0.91815 | 8.5146 | 0.55716 | -1.3904 | 61.7294 | 0.28526 | 61.6652 | -0.023943 | 0.048236 | 61.5524 | 0.003143 | 61.3581 | 62.0345 | 54.285 | 54.8771 | 62.3683 | 69.9648 | 62.0074 | 60.0598 | 123.1796 | 61.7355 | 123.1154 | 61.4263 | 61.4984 | 123.0026 | 61.4533 | 122.8083 | 61.6812 | 61.7263 | 61.617 | 61.6621
5169.0938 | 123.2941 | -61.4456 | 61.7386 | 0.52475 | -7.2201 | -6.5411 | 0.909 | 8.4322 | 0.51595 | -1.6513 | 61.7248 | 0.28526 | 61.6377 | -0.028522 | 0.043657 | 61.5524 | 0.007721 | 61.3443 | 61.9704 | 54.2255 | 54.9045 | 62.3546 | 69.8779 | 61.9616 | 59.7943 | 123.1704 | 61.7309 | 123.0834 | 61.4171 | 61.4893 | 122.998 | 61.4533 | 122.79 | 61.6812 | 61.7171 | 61.5941 | 61.63
5170.0625 | 123.3032 | -61.4456 | 61.6882 | 0.57511 | -7.1743 | -6.2297 | 1.0143 | 8.4506 | 0.53884 | -1.7063 | 61.7202 | 0.28069 | 61.6377 | -0.028522 | 0.048236 | 61.557 | 0.003143 | 61.3398 | 62.0207 | 54.2713 | 55.2159 | 62.4599 | 69.8962 | 61.9845 | 59.7393 | 123.1659 | 61.7263 | 123.0834 | 61.4171 | 61.4939 | 123.0026 | 61.4488 | 122.7854 | 61.672 | 61.7171 | 61.5895 | 61.6346
5171.1094 | 123.2758 | -61.4227 | 61.7432 | 0.50644 | -7.2567 | -6.216 | 0.62513 | 8.3269 | 0.49306 | -1.7063 | 61.734 | 0.28526 | 61.6744 | -0.019364 | 0.048236 | 61.5524 | 0.016878 | 61.3398 | 61.9292 | 54.166 | 55.2067 | 62.0479 | 69.7497 | 61.9158 | 59.7164 | 123.1567 | 61.708 | 123.0971 | 61.4034 | 61.471 | 122.9752 | 61.4396 | 122.7625 | 61.6857 | 61.7171 | 61.6261 | 61.6575
5172.0625 | 123.3353 | -61.441 | 61.7203 | 0.42402 | -7.362 | -5.9688 | 0.35042 | 8.2857 | 0.41065 | -1.6147 | 61.7431 | 0.28984 | 61.679 | -0.028522 | 0.052814 | 61.5616 | 0.007721 | 61.3398 | 61.8651 | 54.079 | 55.4723 | 61.7915 | 69.7268 | 61.8517 | 59.8263 | 123.1842 | 61.7309 | 123.12 | 61.4125 | 61.4939 | 123.0026 | 61.4488 | 122.7808 | 61.6903 | 61.7354 | 61.6261 | 61.6712
5173.0781 | 123.3215 | -61.4273 | 61.7249 | 0.41029 | -7.3712 | -6.0283 | 0.51982 | 8.3086 | 0.40607 | -1.5598 | 61.7294 | 0.28069 | 61.6469 | -0.023943 | 0.039079 | 61.5478 | 0.007721 | 61.3443 | 61.8376 | 54.0561 | 55.399 | 61.9471 | 69.7359 | 61.8334 | 59.8675 | 123.1567 | 61.708 | 123.0742 | 61.4034 | 61.4664 | 122.9752 | 61.435 | 122.7717 | 61.6903 | 61.7217 | 61.6078 | 61.6392
5174.0625 | 123.3307 | -61.4456 | 61.6882 | 0.51559 | -7.1743 | -6.1565 | 0.42368 | 8.4597 | 0.49306 | -1.4087 | 61.7248 | 0.28069 | 61.6377 | -0.033101 | 0.043657 | 61.557 | 0.003143 | 61.3398 | 61.9612 | 54.2713 | 55.2891 | 61.8693 | 69.9053 | 61.9387 | 60.0369 | 123.1704 | 61.7263 | 123.0834 | 61.4125 | 61.4893 | 123.0026 | 61.4488 | 122.7854 | 61.6812 | 61.7217 | 61.5941 | 61.6346
5175.0781 | 123.3307 | -61.4182 | 61.7203 | 0.51101 | -7.0141 | -6.3991 | 0.37789 | 8.5558 | 0.50222 | -1.34 | 61.7294 | 0.28069 | 61.6698 | -0.03768 | 0.043657 | 61.557 | 0.012299 | 61.3535 | 61.9292 | 54.4041 | 55.019 | 61.796 | 69.974 | 61.9204 | 60.0781 | 123.1475 | 61.6988 | 123.088 | 61.3805 | 61.4618 | 122.9752 | 61.4305 | 122.7717 | 61.6857 | 61.7171 | 61.6261 | 61.6575
5176.0625 | 123.3994 | -61.4365 | 61.6699 | 0.56595 | -6.8859 | -6.4404 | 0.25885 | 8.6062 | 0.55716 | -1.3126 | 61.734 | 0.28526 | 61.6698 | -0.03768 | 0.039079 | 61.557 | 0.003143 | 61.3398 | 62.0024 | 54.5506 | 54.9961 | 61.6953 | 70.0427 | 61.9936 | 60.1239 | 123.1704 | 61.7217 | 123.1063 | 61.3988 | 61.4755 | 122.9935 | 61.4396 | 122.7762 | 61.6949 | 61.7308 | 61.6307 | 61.6667
5177.0781 | 123.3078 | -61.4456 | 61.7432 | 0.7262 | -7.2109 | -6.4861 | 0.50151 | 8.6703 | 0.69909 | -1.3858 | 61.734 | 0.28069 | 61.6606 | -0.023943 | 0.043657 | 61.557 | 0.007721 | 61.3489 | 62.1718 | 54.2347 | 54.9595 | 61.9471 | 70.1159 | 62.1447 | 60.0598 | 123.1796 | 61.7263 | 123.1063 | 61.4217 | 61.4893 | 123.0026 | 61.4533 | 122.7945 | 61.6903 | 61.7263 | 61.617 | 61.6529
5178.0625 | 123.2986 | -61.4548 | 61.7065 | 0.67584 | -7.2293 | -6.5457 | 0.7167 | 8.6337 | 0.64872 | -1.4316 | 61.7386 | 0.28984 | 61.6606 | -0.033101 | 0.039079 | 61.557 | 0.007721 | 61.3443 | 62.1306 | 54.2255 | 54.9091 | 62.1715 | 70.0884 | 62.1035 | 60.0232 | 123.1933 | 61.7446 | 123.1154 | 61.4217 | 61.4939 | 123.0118 | 61.4625 | 122.7991 | 61.6995 | 61.7308 | 61.6216 | 61.6529
5179.0781 | 123.3719 | -61.4182 | 61.702 | 0.61632 | -7.2979 | -6.5594 | 0.69839 | 8.5879 | 0.58921 | -1.4499 | 61.7294 | 0.28069 | 61.6377 | -0.028522 | 0.048236 | 61.5616 | 0.003143 | 61.3443 | 62.0345 | 54.1202 | 54.8588 | 62.1165 | 70.006 | 62.0074 | 59.9682 | 123.1475 | 61.6988 | 123.0559 | 61.3896 | 61.4664 | 122.9797 | 61.4213 | 122.7625 | 61.6812 | 61.7263 | 61.5895 | 61.6346
5180.0625 | 123.3673 | -61.4548 | 61.6837 | 0.76282 | -6.7897 | -6.184 | 0.81285 | 8.6382 | 0.73571 | -1.308 | 61.7065 | 0.28069 | 61.6286 | -0.028522 | 0.057392 | 61.5662 | 0.012299 | 61.3581 | 62.2176 | 54.6651 | 55.2708 | 62.2676 | 70.093 | 62.1905 | 60.1468 | 123.1613 | 61.7355 | 123.0834 | 61.4263 | 61.5122 | 123.0209 | 61.4671 | 122.8129 | 61.6491 | 61.6942 | 61.5712 | 61.6163
5181.1094 | 123.4268 | -61.4456 | 61.6516 | 0.73535 | -6.2219 | -5.9917 | 0.048239 | 8.6749 | 0.71282 | -1.1844 | 61.7202 | 0.28069 | 61.6194 | -0.033101 | 0.043657 | 61.5707 | 0.007721 | 61.3581 | 62.181 | 55.2237 | 55.454 | 61.4939 | 70.1205 | 62.1584 | 60.2612 | 123.1659 | 61.7263 | 123.0651 | 61.4125 | 61.4893 | 123.0164 | 61.4533 | 122.8037 | 61.6766 | 61.7125 | 61.5758 | 61.6117
5182.0625 | 123.317 | -61.441 | 61.7065 | 0.67126 | -6.5287 | -6.1199 | -0.079959 | 8.5055 | 0.63957 | -1.2851 | 61.7202 | 0.28069 | 61.6561 | -0.028522 | 0.048236 | 61.557 | 0.012299 | 61.3443 | 62.1123 | 54.9123 | 55.3212 | 61.3611 | 69.9465 | 62.0806 | 60.156 | 123.1613 | 61.7217 | 123.0971 | 61.4125 | 61.4893 | 122.998 | 61.4533 | 122.7854 | 61.672 | 61.7079 | 61.6078 | 61.6438
5183.0781 | 123.3215 | -61.4594 | 61.7203 | 0.73078 | -6.6523 | -6.2114 | 0.16728 | 8.7069 | 0.72198 | -1.2668 | 61.7202 | 0.28984 | 61.6515 | -0.028522 | 0.052814 | 61.5662 | 0.007721 | 61.3535 | 62.1901 | 54.807 | 55.2479 | 61.6266 | 70.1663 | 62.1813 | 60.1926 | 123.1796 | 61.7492 | 123.1108 | 61.4308 | 61.5122 | 123.0255 | 61.4671 | 122.8129 | 61.6674 | 61.7125 | 61.5987 | 61.6438
5184.0625 | 123.3261 | -61.4365 | 61.7203 | 0.79487 | -7.0141 | -6.5502 | 0.17644 | 8.8626 | 0.76318 | -1.0974 | 61.7294 | 0.28526 | 61.6652 | -0.028522 | 0.052814 | 61.5662 | 0.012299 | 61.3581 | 62.2313 | 54.4224 | 54.8862 | 61.6129 | 70.299 | 62.1996 | 60.3391 | 123.1659 | 61.7217 | 123.1017 | 61.4079 | 61.4893 | 123.0026 | 61.4488 | 122.7945 | 61.6766 | 61.7171 | 61.6124 | 61.6529
5185.0781 | 123.4177 | -61.4182 | 61.6928 | 0.64379 | -6.7714 | -6.1427 | -0.15779 | 8.8214 | 0.62583 | -1.2027 | 61.7248 | 0.28069 | 61.6606 | -0.028522 | 0.048236 | 61.5616 | 0.003143 | 61.3443 | 62.0619 | 54.6468 | 55.2754 | 61.2604 | 70.2395 | 62.044 | 60.2155 | 123.143 | 61.6988 | 123.0788 | 61.3896 | 61.4664 | 122.9797 | 61.4213 | 122.7625 | 61.6766 | 61.7217 | 61.6124 | 61.6575
5186.0625 | 123.3444 | -61.4319 | 61.6562 | 0.54306 | -6.7531 | -6.1427 | -0.25394 | 8.7527 | 0.51595 | -1.3126 | 61.7294 | 0.28526 | 61.6515 | -0.028522 | 0.043657 | 61.5662 | 0.007721 | 61.3352 | 61.9749 | 54.6788 | 55.2891 | 61.1779 | 70.1846 | 61.9478 | 60.1193 | 123.1613 | 61.7171 | 123.0834 | 61.4034 | 61.4755 | 122.998 | 61.4396 | 122.7671 | 61.6857 | 61.7217 | 61.6078 | 61.6438
5187.0781 | 123.4085 | -61.4227 | 61.6882 | 0.52475 | -6.9316 | -6.0466 | 0.27716 | 8.8214 | 0.51595 | -1.1523 | 61.7248 | 0.28069 | 61.6332 | -0.014785 | 0.057392 | 61.5616 | 0.012299 | 61.3535 | 61.9475 | 54.4911 | 55.3761 | 61.6999 | 70.2441 | 61.9387 | 60.2704 | 123.1475 | 61.7034 | 123.0559 | 61.4079 | 61.4801 | 122.9843 | 61.435 | 122.7762 | 61.6674 | 61.7125 | 61.5758 | 61.6209
5188.0625 | 123.2758 | -61.4868 | 61.7249 | 0.49728 | -7.1102 | -5.9825 | 0.23596 | 8.6795 | 0.45185 | -1.2347 | 61.7248 | 0.28069 | 61.6377 | -0.023943 | 0.052814 | 61.5616 | 0.012299 | 61.3443 | 61.9841 | 54.3766 | 55.5043 | 61.7228 | 70.1663 | 61.9387 | 60.2521 | 123.2116 | 61.7675 | 123.1246 | 61.4629 | 61.5396 | 123.0484 | 61.4991 | 122.8312 | 61.672 | 61.7125 | 61.5849 | 61.6255
5189.0781 | 123.381 | -61.4456 | 61.702 | 0.51559 | -6.8675 | -5.8268 | 0.3962 | 8.8214 | 0.47017 | -1.3126 | 61.7202 | 0.28069 | 61.6377 | -0.028522 | 0.048236 | 61.557 | 0.007721 | 61.3581 | 61.9612 | 54.5781 | 55.6188 | 61.8418 | 70.267 | 61.9158 | 60.1331 | 123.1659 | 61.7263 | 123.0834 | 61.4171 | 61.4939 | 123.0026 | 61.4533 | 122.8037 | 61.672 | 61.7125 | 61.5895 | 61.63
5190.0625 | 123.3444 | -61.4227 | 61.7249 | 0.34619 | -6.895 | -6.2435 | 0.45572 | 8.6428 | 0.38776 | -1.3904 | 61.734 | 0.28984 | 61.6652 | -0.033101 | 0.052814 | 61.5478 | 0.003143 | 61.3443 | 61.7689 | 54.5277 | 55.1793 | 61.8785 | 70.0656 | 61.8105 | 60.0323 | 123.1567 | 61.7126 | 123.0879 | 61.3896 | 61.4755 | 122.9706 | 61.4259 | 122.7671 | 61.6812 | 61.7308 | 61.6124 | 61.6621
5191.0938 | 123.381 | -61.441 | 61.6791 | 0.41487 | -6.8446 | -6.3808 | 0.62055 | 8.771 | 0.3786 | -1.2897 | 61.7386 | 0.28526 | 61.6652 | -0.023943 | 0.048236 | 61.5524 | 0.007721 | 61.3535 | 61.8559 | 54.5964 | 55.0602 | 62.0616 | 70.2121 | 61.8196 | 60.1514 | 123.1796 | 61.7263 | 123.1063 | 61.4171 | 61.4893 | 122.9935 | 61.4488 | 122.7945 | 61.6903 | 61.7308 | 61.617 | 61.6575
5192.0625 | 123.3444 | -61.4182 | 61.7615 | 0.44234 | -7.0232 | -6.335 | 0.49235 | 8.8534 | 0.41523 | -1.3263 | 61.7294 | 0.28069 | 61.6652 | -0.028522 | 0.052814 | 61.557 | 0.016878 | 61.3535 | 61.8605 | 54.3949 | 55.0831 | 61.9105 | 70.2716 | 61.8334 | 60.0919 | 123.1475 | 61.6988 | 123.0834 | 61.3896 | 61.471 | 122.9752 | 61.435 | 122.7717 | 61.6766 | 61.7125 | 61.6124 | 61.6483
5193.0938 | 123.3994 | -61.4365 | 61.6837 | 0.47439 | -7.1377 | -6.3717 | 0.20849 | 8.8855 | 0.43812 | -1.3767 | 61.734 | 0.28069 | 61.6515 | -0.023943 | 0.052814 | 61.5524 | 0.012299 | 61.3489 | 61.9108 | 54.2988 | 55.0648 | 61.6449 | 70.3219 | 61.8746 | 60.0598 | 123.1704 | 61.7171 | 123.0879 | 61.4125 | 61.4893 | 122.9889 | 61.4488 | 122.7854 | 61.6812 | 61.7217 | 61.5987 | 61.6392
5194.0625 | 123.3307 | -61.4365 | 61.7294 | 0.37824 | -7.2064 | -6.4678 | 0.020768 | 8.6474 | 0.35571 | -1.4453 | 61.7431 | 0.28526 | 61.6469 | -0.028522 | 0.043657 | 61.5433 | 0.007721 | 61.3443 | 61.8147 | 54.2301 | 54.9686 | 61.4572 | 70.0839 | 61.7922 | 59.9911 | 123.1796 | 61.7217 | 123.0834 | 61.4079 | 61.4801 | 122.9797 | 61.4442 | 122.7808 | 61.6995 | 61.7354 | 61.6032 | 61.6392
5195.0938 | 123.4177 | -61.441 | 61.6928 | 0.29125 | -7.0049 | -6.7517 | 0.043661 | 8.4139 | 0.25956 | -1.4682 | 61.734 | 0.28526 | 61.6515 | -0.033101 | 0.048236 | 61.5433 | 0.007721 | 61.3306 | 61.7323 | 54.4361 | 54.6893 | 61.4847 | 69.855 | 61.7006 | 59.9728 | 123.175 | 61.7263 | 123.0925 | 61.4079 | 61.4893 | 122.9843 | 61.4488 | 122.7717 | 61.6857 | 61.7263 | 61.6032 | 61.6438
5196.0625 | 123.2391 | -61.4822 | 61.6562 | 0.23173 | -6.9957 | -6.7563 | -0.066223 | 8.4689 | 0.20004 | -1.5094 | 61.7386 | 0.28069 | 61.6561 | -0.033101 | 0.048236 | 61.5387 | 0.012299 | 61.3443 | 61.714 | 54.4865 | 54.726 | 61.416 | 69.9511 | 61.6823 | 59.9728 | 123.2208 | 61.7629 | 123.1383 | 61.4491 | 61.5305 | 123.0209 | 61.4945 | 122.8266 | 61.6903 | 61.7263 | 61.6078 | 61.6438
5197.0625 | 123.349 | -61.409 | 61.7157 | 0.31872 | -6.9271 | -6.564 | -0.13948 | 8.6657 | 0.27787 | -1.4499 | 61.7386 | 0.28984 | 61.6881 | -0.033101 | 0.048236 | 61.5433 | 0.012299 | 61.3443 | 61.7277 | 54.4819 | 54.845 | 61.2695 | 70.0747 | 61.6869 | 59.9591 | 123.1476 | 61.6988 | 123.0971 | 61.3759 | 61.4572 | 122.9523 | 61.4213 | 122.7533 | 61.6903 | 61.7263 | 61.6399 | 61.6758
5198.0625 | 123.3078 | -61.4548 | 61.702 | 0.46065 | -6.8859 | -6.683 | -0.057066 | 8.7985 | 0.46101 | -1.3126 | 61.7386 | 0.28984 | 61.6606 | -0.023943 | 0.043657 | 61.5433 | 0.012299 | 61.3443 | 61.9154 | 54.5689 | 54.7718 | 61.3977 | 70.2533 | 61.9158 | 60.1422 | 123.1933 | 61.7446 | 123.1154 | 61.4308 | 61.4984 | 122.998 | 61.4671 | 122.7991 | 61.6949 | 61.7263 | 61.617 | 61.6483
5199.0625 | 123.3215 | -61.4182 | 61.7065 | 0.53391 | -7.0415 | -6.7288 | 0.057396 | 8.7527 | 0.51595 | -1.4041 | 61.7294 | 0.28526 | 61.6332 | -0.033101 | 0.052814 | 61.5478 | 0.012299 | 61.3443 | 61.9521 | 54.3766 | 54.6893 | 61.4755 | 70.1709 | 61.9341 | 60.014 | 123.1475 | 61.7034 | 123.0513 | 61.3851 | 61.471 | 122.966 | 61.4305 | 122.7625 | 61.6766 | 61.7171 | 61.5804 | 61.6209
5200.0781 | 123.3856 | -61.4273 | 61.6699 | 0.59342 | -7.1102 | -6.7746 | 0.061975 | 8.6749 | 0.6533 | -1.3309 | 61.734 | 0.28984 | 61.6469 | -0.028522 | 0.043657 | 61.5524 | 0.007721 | 61.3398 | 62.0207 | 54.3171 | 54.6527 | 61.4893 | 70.1022 | 62.0806 | 60.0964 | 123.1613 | 61.7171 | 123.0742 | 61.3988 | 61.471 | 122.9797 | 61.435 | 122.7671 | 61.6903 | 61.7263 | 61.6032 | 61.6392
5201.0625 | 123.3948 | -61.409 | 61.6837 | 0.48354 | -7.2659 | -6.7929 | 0.029925 | 8.5696 | 0.47932 | -1.308 | 61.7431 | 0.28069 | 61.679 | -0.023943 | 0.043657 | 61.5478 | 0.012299 | 61.3489 | 61.8925 | 54.1431 | 54.6161 | 61.4389 | 69.9786 | 61.8883 | 60.101 | 123.1521 | 61.6897 | 123.088 | 61.3851 | 61.4527 | 122.9568 | 61.4213 | 122.7579 | 61.6995 | 61.7308 | 61.6353 | 61.6667
5202.0938 | 123.3902 | -61.4502 | 61.6699 | 0.46523 | -7.1606 | -6.6327 | 0.28174 | 8.6337 | 0.45185 | -1.3034 | 61.7386 | 0.28526 | 61.6698 | -0.033101 | 0.043657 | 61.5524 | 0.007721 | 61.3443 | 61.9154 | 54.2896 | 54.8175 | 61.7319 | 70.0839 | 61.902 | 60.1468 | 123.1887 | 61.7355 | 123.12 | 61.4171 | 61.4939 | 123.0026 | 61.4579 | 122.7945 | 61.6949 | 61.7308 | 61.6261 | 61.6621
5203.0625 | 123.2986 | -61.4594 | 61.7157 | 0.39655 | -7.1926 | -6.4953 | 0.31837 | 8.5879 | 0.3786 | -1.2439 | 61.734 | 0.28984 | 61.6652 | -0.033101 | 0.048236 | 61.5478 | 0.003143 | 61.3398 | 61.8559 | 54.2667 | 54.9641 | 61.7777 | 70.0472 | 61.838 | 60.2155 | 123.1933 | 61.7492 | 123.1246 | 61.4262 | 61.5076 | 123.0072 | 61.4625 | 122.7991 | 61.6857 | 61.7308 | 61.617 | 61.6621
5204.0781 | 123.3627 | -61.4365 | 61.6653 | 0.35993 | -7.3529 | -6.6739 | 0.12607 | 8.446 | 0.38318 | -1.34 | 61.7431 | 0.28526 | 61.6606 | -0.023943 | 0.048236 | 61.5433 | -0.001436 | 61.3352 | 61.7964 | 54.0836 | 54.7626 | 61.5625 | 69.8824 | 61.8196 | 60.0964 | 123.1796 | 61.7217 | 123.0971 | 61.4125 | 61.4847 | 122.9797 | 61.435 | 122.7717 | 61.6949 | 61.7446 | 61.6124 | 61.6621
5205.0625 | 123.381 | -61.4319 | 61.6745 | 0.36908 | -7.3071 | -6.216 | 0.13981 | 8.5101 | 0.35571 | -1.3858 | 61.734 | 0.28069 | 61.6377 | -0.028522 | 0.052814 | 61.5478 | 0.007721 | 61.3398 | 61.801 | 54.1248 | 55.2159 | 61.5717 | 69.942 | 61.7876 | 60.0461 | 123.1659 | 61.7126 | 123.0696 | 61.4034 | 61.4847 | 122.9797 | 61.4396 | 122.7717 | 61.6812 | 61.7263 | 61.5849 | 61.63
5206.1094 | 123.3307 | -61.4594 | 61.6928 | 0.27752 | -7.3758 | -6.5777 | 0.19475 | 8.4048 | 0.27787 | -1.4728 | 61.734 | 0.28526 | 61.6469 | -0.033101 | 0.043657 | 61.5387 | 0.003143 | 61.3352 | 61.7369 | 54.0836 | 54.8816 | 61.6541 | 69.8641 | 61.7372 | 59.9866 | 123.1933 | 61.7446 | 123.1063 | 61.4262 | 61.503 | 122.998 | 61.4625 | 122.7945 | 61.6903 | 61.7308 | 61.6032 | 61.6438
5207.0625 | 123.3719 | -61.4136 | 61.6928 | 0.26378 | -7.3483 | -6.4541 | 0.089445 | 8.5146 | 0.26872 | -1.5232 | 61.7431 | 0.28526 | 61.6469 | -0.028522 | 0.048236 | 61.5478 | 0.003143 | 61.3352 | 61.6774 | 54.0653 | 54.9595 | 61.503 | 69.9282 | 61.6823 | 59.8904 | 123.1567 | 61.6988 | 123.0605 | 61.3851 | 61.4618 | 122.9614 | 61.4167 | 122.7488 | 61.6949 | 61.74 | 61.5987 | 61.6438
5208.0938 | 123.3536 | -61.409 | 61.6745 | 0.28667 | -7.4078 | -6.4404 | -0.006703 | 8.6474 | 0.25956 | -1.5048 | 61.7477 | 0.28984 | 61.6698 | -0.033101 | 0.057392 | 61.5524 | 0.003143 | 61.3352 | 61.6957 | 54.0012 | 54.9686 | 61.4023 | 70.0564 | 61.6686 | 59.9042 | 123.1567 | 61.6988 | 123.0788 | 61.3759 | 61.4664 | 122.9614 | 61.4121 | 122.7442 | 61.6903 | 61.7446 | 61.6124 | 61.6667
5209.0625 | 123.3765 | -61.4227 | 61.6653 | 0.23631 | -7.5132 | -6.5136 | -0.12116 | 8.4734 | 0.20462 | -1.5048 | 61.7477 | 0.28069 | 61.6881 | -0.028522 | 0.048236 | 61.5341 | 0.003143 | 61.3352 | 61.659 | 53.9096 | 54.9091 | 61.3016 | 69.8962 | 61.6273 | 59.9179 | 123.1704 | 61.7034 | 123.1108 | 61.3942 | 61.471 | 122.9568 | 61.4259 | 122.7579 | 61.6995 | 61.7446 | 61.6399 | 61.685
5210.0938 | 123.349 | -61.441 | 61.6653 | 0.26378 | -7.4765 | -6.3717 | -0.089116 | 8.4048 | 0.24583 | -1.4636 | 61.7431 | 0.28984 | 61.679 | -0.028522 | 0.048236 | 61.5387 | 0.007721 | 61.3443 | 61.7048 | 53.9645 | 55.0694 | 61.3519 | 69.8458 | 61.6869 | 59.9774 | 123.1842 | 61.7309 | 123.12 | 61.4125 | 61.4893 | 122.9797 | 61.4488 | 122.7854 | 61.6949 | 61.7354 | 61.6307 | 61.6712
5211.0625 | 123.3856 | -61.4273 | 61.6882 | 0.28667 | -7.5544 | -6.4495 | 0.080288 | 8.3865 | 0.2504 | -1.4087 | 61.7431 | 0.28526 | 61.6835 | -0.028522 | 0.057392 | 61.5387 | 0.007721 | 61.3443 | 61.714 | 53.8729 | 54.9778 | 61.5076 | 69.8138 | 61.6777 | 60.0186 | 123.1704 | 61.7126 | 123.1108 | 61.3988 | 61.4847 | 122.966 | 61.435 | 122.7717 | 61.6857 | 61.7354 | 61.6261 | 61.6758
5212.0781 | 123.2391 | -61.4594 | 61.7111 | 0.31872 | -7.4307 | -6.5274 | 0.24054 | 8.4597 | 0.30077 | -1.395 | 61.7386 | 0.28526 | 61.6698 | -0.033101 | 0.048236 | 61.5433 | -0.001436 | 61.3398 | 61.7781 | 54.0286 | 54.932 | 61.6999 | 69.9191 | 61.7601 | 60.0644 | 123.1979 | 61.7446 | 123.1291 | 61.4262 | 61.5076 | 123.0026 | 61.4579 | 122.7991 | 61.6903 | 61.74 | 61.6216 | 61.6712
5213.0625 | 123.3582 | -61.4319 | 61.6837 | 0.34161 | -7.3804 | -5.9917 | 0.084867 | 8.4414 | 0.30992 | -1.3721 | 61.7294 | 0.28984 | 61.6469 | -0.033101 | 0.043657 | 61.5478 | 0.007721 | 61.3489 | 61.7735 | 54.0515 | 55.4402 | 61.5168 | 69.8733 | 61.7418 | 60.0598 | 123.1613 | 61.7217 | 123.0788 | 61.3988 | 61.4755 | 122.9797 | 61.4396 | 122.7808 | 61.6857 | 61.7217 | 61.6032 | 61.6392
5214.0781 | 123.3124 | -61.4502 | 61.7111 | 0.29583 | -7.4124 | -5.8772 | 0.094024 | 8.4094 | 0.26414 | -1.395 | 61.7386 | 0.28526 | 61.6423 | -0.033101 | 0.043657 | 61.5478 | 0.012299 | 61.3489 | 61.746 | 54.0378 | 55.573 | 61.5442 | 69.8595 | 61.7143 | 60.0552 | 123.1887 | 61.7355 | 123.0925 | 61.4171 | 61.4939 | 122.998 | 61.4625 | 122.7991 | 61.6949 | 61.7263 | 61.5987 | 61.63
5215.0625 | 123.3444 | -61.4227 | 61.6791 | 0.24547 | -7.362 | -5.9092 | 0.20849 | 8.5238 | 0.26872 | -1.3995 | 61.734 | 0.28984 | 61.6469 | -0.033101 | 0.048236 | 61.5524 | 0.012299 | 61.3489 | 61.6682 | 54.0607 | 55.5135 | 61.6312 | 69.9465 | 61.6914 | 60.0232 | 123.1567 | 61.7126 | 123.0696 | 61.3896 | 61.471 | 122.9752 | 61.435 | 122.7717 | 61.6857 | 61.7217 | 61.5987 | 61.6346
5216.1094 | 123.3215 | -61.4639 | 61.6745 | 0.26378 | -7.2476 | -5.8222 | 0.51067 | 8.6199 | 0.2504 | -1.3629 | 61.7386 | 0.28526 | 61.6606 | -0.03768 | 0.048236 | 61.557 | 0.007721 | 61.3352 | 61.7277 | 54.2163 | 55.6417 | 61.9746 | 70.0839 | 61.7143 | 60.101 | 123.2025 | 61.7492 | 123.1246 | 61.4262 | 61.5122 | 123.0209 | 61.4716 | 122.7991 | 61.6903 | 61.7308 | 61.6124 | 61.6529
5217.0625 | 123.3948 | -61.4456 | 61.6791 | 0.28209 | -7.3117 | -6.0878 | 0.46488 | 8.2812 | 0.34197 | -1.4545 | 61.734 | 0.29442 | 61.679 | -0.033101 | 0.048236 | 61.5478 | 0.007721 | 61.3306 | 61.7277 | 54.1339 | 55.3578 | 61.9105 | 69.7268 | 61.7876 | 59.9911 | 123.1796 | 61.74 | 123.1246 | 61.4125 | 61.4939 | 122.9935 | 61.4533 | 122.7762 | 61.6857 | 61.7263 | 61.6307 | 61.6712
5218.0781 | 123.2529 | -61.4777 | 61.6745 | 0.27752 | -7.3987 | -5.9962 | 0.47404 | 8.0385 | 0.2733 | -1.4682 | 61.7431 | 0.28526 | 61.6744 | -0.033101 | 0.048236 | 61.5433 | 0.007721 | 61.3398 | 61.7552 | 54.079 | 55.4814 | 61.9517 | 69.5162 | 61.751 | 60.0094 | 123.2208 | 61.7629 | 123.152 | 61.4446 | 61.5259 | 123.0209 | 61.4854 | 122.8174 | 61.6949 | 61.7354 | 61.6261 | 61.6667
5219.0625 | 123.3765 | -61.4365 | 61.6837 | 0.40571 | -7.3804 | -6.0145 | 0.38705 | 8.066 | 0.39233 | -1.395 | 61.7431 | 0.28984 | 61.6698 | -0.033101 | 0.052814 | 61.5387 | 0.012299 | 61.3352 | 61.8422 | 54.0561 | 55.4219 | 61.8235 | 69.5025 | 61.8288 | 60.0415 | 123.1796 | 61.7263 | 123.1063 | 61.4034 | 61.4893 | 122.9752 | 61.4488 | 122.7717 | 61.6903 | 61.7308 | 61.617 | 61.6575
5220.0938 | 123.4131 | -61.4273 | 61.6699 | 0.45607 | -7.3895 | -5.8955 | 0.061975 | 8.1896 | 0.43812 | -1.3492 | 61.734 | 0.28069 | 61.6652 | -0.033101 | 0.043657 | 61.5478 | 0.007721 | 61.3306 | 61.8834 | 54.0378 | 55.5318 | 61.4893 | 69.6169 | 61.8654 | 60.0781 | 123.1613 | 61.708 | 123.0925 | 61.3942 | 61.471 | 122.9752 | 61.435 | 122.7579 | 61.6903 | 61.7263 | 61.6216 | 61.6575
5221.0625 | 123.2483 | -61.441 | 61.702 | 0.46981 | -7.3941 | -5.6116 | 0.10318 | 8.2445 | 0.63041 | -1.482 | 61.7386 | 0.28526 | 61.6423 | -0.028522 | 0.048236 | 61.5478 | 0.012299 | 61.3443 | 61.9108 | 54.0469 | 55.8294 | 61.5442 | 69.6856 | 62.0715 | 59.9591 | 123.1796 | 61.7263 | 123.0834 | 61.4125 | 61.4893 | 122.9889 | 61.4533 | 122.7854 | 61.6903 | 61.7263 | 61.5941 | 61.63
5222.0781 | 123.2986 | -61.4502 | 61.6928 | 0.54764 | -7.4445 | -5.9688 | 0.30463 | 8.1393 | 0.57089 | -1.5506 | 61.7294 | 0.28984 | 61.6423 | -0.023943 | 0.048236 | 61.5433 | 0.007721 | 61.3398 | 61.9978 | 54.0057 | 55.4814 | 61.7548 | 69.5894 | 62.0211 | 59.8996 | 123.1796 | 61.74 | 123.0925 | 61.4263 | 61.4984 | 122.9935 | 61.4579 | 122.79 | 61.6812 | 61.7217 | 61.5941 | 61.6346
5223.0625 | 123.4085 | -61.4227 | 61.6791 | 0.57511 | -7.5315 | -6.0878 | 0.46488 | 8.2491 | 0.64415 | -1.6239 | 61.734 | 0.28984 | 61.6332 | -0.03768 | 0.039079 | 61.5478 | 0.012299 | 61.3352 | 61.9978 | 53.8913 | 55.3349 | 61.8876 | 69.6719 | 62.0669 | 59.7989 | 123.1567 | 61.7126 | 123.0559 | 61.385 | 61.4618 | 122.9706 | 61.435 | 122.7579 | 61.6949 | 61.7217 | 61.5941 | 61.6209
5224.0781 | 123.4039 | -61.4227 | 61.6562 | 0.61174 | -7.504 | -6.1382 | 0.45115 | 8.2857 | 0.59378 | -1.7475 | 61.734 | 0.28526 | 61.6423 | -0.028522 | 0.039079 | 61.5433 | 0.007721 | 61.3215 | 62.0345 | 53.9187 | 55.2846 | 61.8739 | 69.7085 | 62.0165 | 59.6752 | 123.1567 | 61.708 | 123.0651 | 61.3942 | 61.4618 | 122.966 | 61.4304 | 122.7442 | 61.6949 | 61.7263 | 61.6032 | 61.6346
5225.0625 | 123.3627 | -61.4227 | 61.6653 | 0.5568 | -7.5269 | -6.097 | 0.35958 | 8.2583 | 0.53426 | -1.6651 | 61.734 | 0.28526 | 61.6698 | -0.033101 | 0.048236 | 61.5433 | 0.012299 | 61.3215 | 61.9795 | 53.8958 | 55.3258 | 61.7823 | 69.681 | 61.957 | 59.7577 | 123.1567 | 61.708 | 123.0925 | 61.3896 | 61.471 | 122.966 | 61.435 | 122.7442 | 61.6857 | 61.7217 | 61.6216 | 61.6575
5226.0938 | 123.3124 | -61.4227 | 61.6974 | 0.55222 | -7.4445 | -5.7765 | 0.42368 | 8.272 | 0.52053 | -1.6056 | 61.7431 | 0.28526 | 61.679 | -0.028522 | 0.052814 | 61.5478 | 0.012299 | 61.3352 | 61.9749 | 53.9783 | 55.6463 | 61.8464 | 69.6947 | 61.9433 | 59.8172 | 123.1659 | 61.708 | 123.1017 | 61.3942 | 61.4755 | 122.9706 | 61.435 | 122.7579 | 61.6903 | 61.7308 | 61.6261 | 61.6667
5227.0625 | 123.3765 | -61.4273 | 61.6928 | 0.55222 | -7.4857 | -5.8543 | 0.42825 | 8.2445 | 0.52053 | -1.4636 | 61.734 | 0.27611 | 61.6698 | -0.033101 | 0.048236 | 61.557 | 0.012299 | 61.3352 | 61.9795 | 53.9416 | 55.573 | 61.8556 | 69.6719 | 61.9478 | 59.9637 | 123.1613 | 61.7034 | 123.0971 | 61.3942 | 61.4755 | 122.9843 | 61.4396 | 122.7625 | 61.6857 | 61.7217 | 61.6216 | 61.6575
5228.0781 | 123.2895 | -61.4822 | 61.6974 | 0.53391 | -7.5635 | -6.1199 | 0.37331 | 8.2354 | 0.50222 | -1.3583 | 61.7386 | 0.28526 | 61.6698 | -0.033101 | 0.043657 | 61.557 | 0.003143 | 61.3352 | 62.0161 | 53.9187 | 55.3624 | 61.8556 | 69.7176 | 61.9845 | 60.1239 | 123.2208 | 61.7675 | 123.152 | 61.4491 | 61.5259 | 123.0392 | 61.4854 | 122.8174 | 61.6949 | 61.7354 | 61.6261 | 61.6667
5229.0625 | 123.349 | -61.4227 | 61.6837 | 0.53848 | -7.6597 | -6.2572 | 0.4191 | 8.0797 | 0.50679 | -1.4316 | 61.7431 | 0.28984 | 61.6561 | -0.033101 | 0.048236 | 61.5524 | -0.001436 | 61.326 | 61.9612 | 53.7631 | 55.1655 | 61.8418 | 69.5025 | 61.9295 | 59.9911 | 123.1659 | 61.7126 | 123.0788 | 61.3896 | 61.471 | 122.9752 | 61.4213 | 122.7488 | 61.6949 | 61.7446 | 61.6078 | 61.6575
5230.0938 | 123.3398 | -61.4639 | 61.6699 | 0.60716 | -7.5452 | -6.1611 | 0.32295 | 8.0568 | 0.58005 | -1.6376 | 61.734 | 0.28984 | 61.6423 | -0.033101 | 0.048236 | 61.5433 | 0.007721 | 61.3306 | 62.0711 | 53.9187 | 55.3029 | 61.7869 | 69.5208 | 62.044 | 59.8263 | 123.1979 | 61.7538 | 123.1063 | 61.4308 | 61.5122 | 123.0072 | 61.4716 | 122.7945 | 61.6857 | 61.7263 | 61.5941 | 61.6346
5231.0625 | 123.3124 | -61.4273 | 61.734 | 0.57511 | -7.4811 | -6.3625 | 0.10318 | 8.0477 | 0.55716 | -1.7612 | 61.7431 | 0.28984 | 61.6515 | -0.033101 | 0.043657 | 61.5387 | 0.007721 | 61.3352 | 62.0024 | 53.9462 | 55.0648 | 61.5305 | 69.475 | 61.9845 | 59.6661 | 123.1704 | 61.7171 | 123.0788 | 61.3942 | 61.471 | 122.966 | 61.435 | 122.7625 | 61.6995 | 61.7354 | 61.6078 | 61.6438
5232.0781 | 123.3902 | -61.4044 | 61.6562 | 0.598 | -7.5269 | -6.2343 | 0.007033 | 8.0385 | 0.57089 | -1.8207 | 61.7386 | 0.28984 | 61.6561 | -0.033101 | 0.039079 | 61.5387 | 0.007721 | 61.3215 | 62.0024 | 53.8775 | 55.1701 | 61.4115 | 69.443 | 61.9753 | 59.5837 | 123.143 | 61.6943 | 123.0605 | 61.3713 | 61.4435 | 122.9431 | 61.4121 | 122.7259 | 61.6995 | 61.7308 | 61.617 | 61.6483
5233.0625 | 123.3902 | -61.4365 | 61.7065 | 0.52017 | -7.6826 | -6.3763 | 0.07571 | 8.1072 | 0.4839 | -1.8619 | 61.7431 | 0.28526 | 61.679 | -0.033101 | 0.052814 | 61.5295 | -0.001436 | 61.3215 | 61.9566 | 53.7539 | 55.0602 | 61.5122 | 69.5437 | 61.9204 | 59.5745 | 123.1796 | 61.7217 | 123.1154 | 61.4034 | 61.4893 | 122.966 | 61.435 | 122.7579 | 61.6903 | 61.7446 | 61.6261 | 61.6804
5234.0938 | 123.3444 | -61.4365 | 61.6791 | 0.50644 | -7.7284 | -6.4083 | 0.089445 | 8.1438 | 0.47017 | -1.7292 | 61.7477 | 0.28984 | 61.6881 | -0.033101 | 0.043657 | 61.5387 | 0.012299 | 61.3169 | 61.9429 | 53.7081 | 55.0282 | 61.5259 | 69.5803 | 61.9066 | 59.7073 | 123.1842 | 61.7263 | 123.1246 | 61.4034 | 61.4801 | 122.9752 | 61.4488 | 122.7533 | 61.7041 | 61.7354 | 61.6445 | 61.6758
5235.0625 | 123.3582 | -61.4136 | 61.6882 | 0.51101 | -7.7421 | -6.4175 | 0.094024 | 8.0248 | 0.47017 | -1.6468 | 61.7523 | 0.28984 | 61.6835 | -0.023943 | 0.039079 | 61.5478 | 0.003143 | 61.3123 | 61.9246 | 53.6715 | 54.9961 | 61.5076 | 69.4384 | 61.8837 | 59.7668 | 123.1659 | 61.7034 | 123.0971 | 61.3896 | 61.4527 | 122.9614 | 61.4167 | 122.7259 | 61.7132 | 61.7491 | 61.6445 | 61.6804
5236.0938 | 123.3582 | -61.441 | 61.7111 | 0.48812 | -7.6871 | -6.1519 | -0.01586 | 7.9744 | 0.50679 | -1.6239 | 61.7477 | 0.28984 | 61.6835 | -0.028522 | 0.034501 | 61.5387 | 0.007721 | 61.3169 | 61.9292 | 53.7539 | 55.2891 | 61.4252 | 69.4155 | 61.9478 | 59.8172 | 123.1888 | 61.7309 | 123.1246 | 61.4125 | 61.4755 | 122.9797 | 61.4488 | 122.7579 | 61.7132 | 61.74 | 61.649 | 61.6758
5237.0625 | 123.4039 | -61.3998 | 61.6837 | 0.54764 | -7.6734 | -6.1199 | 0.18559 | 8.0568 | 0.52053 | -1.6239 | 61.7386 | 0.28526 | 61.6515 | -0.033101 | 0.043657 | 61.5478 | 0.012299 | 61.326 | 61.9475 | 53.7264 | 55.28 | 61.5854 | 69.4567 | 61.9204 | 59.776 | 123.1384 | 61.6851 | 123.0513 | 61.3667 | 61.4435 | 122.9477 | 61.4121 | 122.7259 | 61.6949 | 61.7263 | 61.6078 | 61.6392
5238.0781 | 123.3536 | -61.4548 | 61.7065 | 0.58427 | -7.5086 | -6.097 | 0.14439 | 8.0981 | 0.55258 | -1.6925 | 61.734 | 0.28526 | 61.6423 | -0.028522 | 0.043657 | 61.5478 | 0.012299 | 61.326 | 62.039 | 53.9462 | 55.3578 | 61.5992 | 69.5528 | 62.0074 | 59.7622 | 123.1887 | 61.74 | 123.0971 | 61.4263 | 61.4984 | 123.0026 | 61.4671 | 122.7808 | 61.6903 | 61.7217 | 61.5987 | 61.63
5239.0625 | 123.3719 | -61.4273 | 61.6562 | 0.63921 | -7.591 | -6.2572 | 0.17644 | 8.0477 | 0.60752 | -1.6788 | 61.7431 | 0.28526 | 61.6469 | -0.033101 | 0.039079 | 61.5433 | 0.016878 | 61.3215 | 62.0665 | 53.8363 | 55.1701 | 61.6037 | 69.475 | 62.0348 | 59.7485 | 123.1704 | 61.7126 | 123.0742 | 61.3942 | 61.4664 | 122.9706 | 61.4442 | 122.7488 | 61.7041 | 61.7263 | 61.6078 | 61.63
5240.0781 | 123.3719 | -61.4227 | 61.7065 | 0.70331 | -7.4124 | -6.4724 | 0.22222 | 8.2033 | 0.68993 | -1.6147 | 61.7386 | 0.28984 | 61.6561 | -0.023943 | 0.048236 | 61.5524 | 0.003143 | 61.3352 | 62.126 | 54.0103 | 54.9503 | 61.645 | 69.6261 | 62.1127 | 59.808 | 123.1613 | 61.7126 | 123.0788 | 61.3988 | 61.471 | 122.9752 | 61.4259 | 122.7579 | 61.6903 | 61.7354 | 61.6078 | 61.6529
5241.0625 | 123.4085 | -61.409 | 61.6928 | 0.63005 | -7.4353 | -6.4907 | -0.01586 | 8.1576 | 0.60294 | -1.4865 | 61.7431 | 0.28069 | 61.679 | -0.033101 | 0.052814 | 61.5478 | 0.007721 | 61.326 | 62.039 | 53.9737 | 54.9183 | 61.3931 | 69.5666 | 62.0119 | 59.9225 | 123.1521 | 61.6897 | 123.088 | 61.3759 | 61.4618 | 122.9568 | 61.4167 | 122.735 | 61.6903 | 61.7354 | 61.6261 | 61.6712
5242.0781 | 123.2758 | -61.4456 | 61.7065 | 0.52017 | -7.8016 | -6.2206 | -0.10285 | 7.9104 | 0.48848 | -1.5872 | 61.7569 | 0.28069 | 61.6927 | -0.028522 | 0.043657 | 61.5387 | 0.012299 | 61.326 | 61.9658 | 53.644 | 55.225 | 61.3428 | 69.356 | 61.9341 | 59.8584 | 123.2025 | 61.7263 | 123.1383 | 61.4171 | 61.4893 | 122.9843 | 61.4579 | 122.7717 | 61.7132 | 61.7446 | 61.649 | 61.6804
5243.0625 | 123.3856 | -61.409 | 61.6562 | 0.52475 | -7.7833 | -6.3167 | 0.13065 | 7.9699 | 0.49764 | -1.7063 | 61.7523 | 0.28069 | 61.6881 | -0.033101 | 0.039079 | 61.5433 | 0.007721 | 61.3352 | 61.9337 | 53.6257 | 55.0923 | 61.5396 | 69.3789 | 61.9066 | 59.7027 | 123.1613 | 61.6897 | 123.0971 | 61.3759 | 61.4481 | 122.9523 | 61.4167 | 122.7442 | 61.7132 | 61.7446 | 61.649 | 61.6804
5244.0938 | 123.3078 | -61.4502 | 61.7111 | 0.56595 | -7.623 | -6.4816 | 0.37789 | 8.066 | 0.52511 | -1.5918 | 61.7386 | 0.28526 | 61.6698 | -0.033101 | 0.052814 | 61.5387 | 0.007721 | 61.3398 | 62.0162 | 53.8272 | 54.9686 | 61.8281 | 69.5162 | 61.9753 | 59.8584 | 123.1887 | 61.7355 | 123.12 | 61.4171 | 61.503 | 122.9889 | 61.4579 | 122.79 | 61.6857 | 61.7308 | 61.617 | 61.6621
5245.0625 | 123.4314 | -61.4273 | 61.6653 | 0.63921 | -7.2979 | -6.3396 | 0.46488 | 7.979 | 0.61668 | -1.427 | 61.7294 | 0.28069 | 61.6469 | -0.028522 | 0.043657 | 61.5478 | 0.007721 | 61.3535 | 62.0665 | 54.1294 | 55.0877 | 61.8922 | 69.4063 | 62.044 | 60.0003 | 123.1567 | 61.708 | 123.0742 | 61.3988 | 61.471 | 122.9752 | 61.435 | 122.7808 | 61.6857 | 61.7217 | 61.6032 | 61.6392
5246.1094 | 123.3353 | -61.4548 | 61.7111 | 0.60258 | -7.4674 | -6.5274 | 0.49693 | 8.1438 | 0.57089 | -1.5232 | 61.7431 | 0.28984 | 61.6606 | -0.033101 | 0.043657 | 61.5478 | 0.003143 | 61.3535 | 62.0574 | 53.9874 | 54.9274 | 61.9517 | 69.5986 | 62.0257 | 59.9316 | 123.1979 | 61.7446 | 123.1154 | 61.4217 | 61.4984 | 123.0026 | 61.4579 | 122.8083 | 61.6995 | 61.74 | 61.617 | 61.6575
5247.0625 | 123.4039 | -61.4044 | 61.6699 | 0.4927 | -7.4124 | -6.5182 | 0.45572 | 8.0156 | 0.53426 | -1.6376 | 61.7431 | 0.28526 | 61.6835 | -0.033101 | 0.043657 | 61.5433 | 0.012299 | 61.3352 | 61.8971 | 53.992 | 54.8862 | 61.8601 | 69.4201 | 61.9387 | 59.7668 | 123.1476 | 61.6897 | 123.088 | 61.3713 | 61.4481 | 122.9477 | 61.4167 | 122.7396 | 61.6995 | 61.7308 | 61.6399 | 61.6712
5248.0781 | 123.3261 | -61.4182 | 61.702 | 0.57969 | -7.3254 | -6.2893 | 0.51982 | 8.24 | 0.54342 | -1.5232 | 61.7386 | 0.27611 | 61.6698 | -0.033101 | 0.048236 | 61.5433 | 0.012299 | 61.3581 | 61.9978 | 54.0927 | 55.1289 | 61.938 | 69.6581 | 61.9616 | 59.895 | 123.1567 | 61.6943 | 123.088 | 61.3851 | 61.4664 | 122.9614 | 61.4305 | 122.7762 | 61.6903 | 61.7263 | 61.6216 | 61.6575
5249.0625 | 123.3902 | -61.4136 | 61.6791 | 0.44692 | -7.3666 | -6.2893 | 0.45572 | 7.9744 | 0.40607 | -1.5369 | 61.7386 | 0.27611 | 61.6652 | -0.028522 | 0.039079 | 61.5478 | 0.012299 | 61.3489 | 61.8605 | 54.0469 | 55.1243 | 61.8693 | 69.388 | 61.8196 | 59.8767 | 123.1521 | 61.6897 | 123.0788 | 61.3851 | 61.4527 | 122.9614 | 61.4259 | 122.7625 | 61.6995 | 61.7263 | 61.6261 | 61.6529
5250.0625 | 123.3856 | -61.4182 | 61.6699 | 0.34619 | -7.3254 | -6.2252 | 0.42825 | 7.9836 | 0.30992 | -1.6239 | 61.7386 | 0.28526 | 61.6561 | -0.033101 | 0.039079 | 61.5433 | 0.012299 | 61.3489 | 61.7643 | 54.0927 | 55.193 | 61.8464 | 69.4018 | 61.7281 | 59.7943 | 123.1567 | 61.7034 | 123.0742 | 61.3851 | 61.4572 | 122.9614 | 61.4305 | 122.7671 | 61.6995 | 61.7263 | 61.617 | 61.6438
5251.1094 | 123.4085 | -61.4227 | 61.6562 | 0.37366 | -7.4857 | -6.2435 | 0.28632 | 7.947 | 0.33739 | -1.6697 | 61.7477 | 0.28526 | 61.6606 | -0.028522 | 0.043657 | 61.5433 | 0.007721 | 61.3443 | 61.7964 | 53.9371 | 55.1793 | 61.709 | 69.3697 | 61.7601 | 59.7531 | 123.1704 | 61.708 | 123.0834 | 61.3942 | 61.4664 | 122.966 | 61.4304 | 122.7671 | 61.7041 | 61.74 | 61.617 | 61.6529
5252.0625 | 123.3856 | -61.4319 | 61.6608 | 0.37366 | -7.5315 | -6.2984 | 0.38247 | 7.9378 | 0.47475 | -1.6834 | 61.7431 | 0.28526 | 61.6835 | -0.028522 | 0.039079 | 61.5387 | 0.003143 | 61.3443 | 61.8055 | 53.9004 | 55.1335 | 61.8144 | 69.3697 | 61.9066 | 59.7485 | 123.175 | 61.7171 | 123.1154 | 61.4034 | 61.471 | 122.9706 | 61.435 | 122.7762 | 61.7041 | 61.74 | 61.6445 | 61.6804
5253.0781 | 123.3032 | -61.4594 | 61.702 | 0.46065 | -7.4307 | -6.5869 | 0.40078 | 8.2445 | 0.4427 | -1.8207 | 61.7431 | 0.28069 | 61.6835 | -0.03768 | 0.039079 | 61.5433 | 0.007721 | 61.3489 | 61.92 | 54.0286 | 54.8725 | 61.8601 | 69.7039 | 61.902 | 59.6386 | 123.2025 | 61.74 | 123.1429 | 61.4217 | 61.4984 | 123.0026 | 61.4671 | 122.8083 | 61.7041 | 61.7354 | 61.6445 | 61.6758
5254.0625 | 123.4177 | -61.4182 | 61.6562 | 0.50644 | -7.2659 | -6.4449 | 0.40536 | 8.2812 | 0.47017 | -1.7566 | 61.7386 | 0.28526 | 61.6561 | -0.042259 | 0.052814 | 61.5478 | 0.003143 | 61.3535 | 61.9246 | 54.1523 | 54.9732 | 61.8235 | 69.6993 | 61.8883 | 59.6615 | 123.1567 | 61.7034 | 123.0742 | 61.3759 | 61.471 | 122.966 | 61.4213 | 122.7717 | 61.6857 | 61.7354 | 61.6032 | 61.6529
5255.0625 | 123.3902 | -61.4456 | 61.6882 | 0.54306 | -7.0965 | -6.2068 | 0.32295 | 8.2079 | 0.50222 | -1.7246 | 61.734 | 0.28526 | 61.6515 | -0.03768 | 0.048236 | 61.5524 | 0.003143 | 61.3581 | 61.9887 | 54.3491 | 55.2388 | 61.7686 | 69.6535 | 61.9478 | 59.721 | 123.1796 | 61.7309 | 123.0971 | 61.4079 | 61.4939 | 122.998 | 61.4488 | 122.8037 | 61.6857 | 61.7308 | 61.6032 | 61.6483
5256.0938 | 123.3398 | -61.4182 | 61.7111 | 0.61632 | -7.1881 | -6.0786 | 0.46488 | 8.391 | 0.57547 | -1.4957 | 61.7248 | 0.28526 | 61.6744 | -0.023943 | 0.043657 | 61.557 | 0.007721 | 61.3581 | 62.0345 | 54.2301 | 55.3395 | 61.883 | 69.8092 | 61.9936 | 59.9225 | 123.143 | 61.7034 | 123.0925 | 61.3942 | 61.4618 | 122.9752 | 61.4259 | 122.7762 | 61.6812 | 61.7171 | 61.6307 | 61.6667
5257.0625 | 123.4268 | -61.4365 | 61.6516 | 0.54306 | -7.0553 | -6.4175 | 0.28632 | 8.3636 | 0.63957 | -1.4865 | 61.7386 | 0.29442 | 61.679 | -0.028522 | 0.043657 | 61.5524 | 0.003143 | 61.3581 | 61.9795 | 54.3812 | 55.019 | 61.7228 | 69.8 | 62.076 | 59.9499 | 123.175 | 61.7309 | 123.1154 | 61.4079 | 61.4801 | 122.9889 | 61.4396 | 122.7945 | 61.6949 | 61.7354 | 61.6353 | 61.6758
5258.0938 | 123.3078 | -61.4548 | 61.6974 | 0.63005 | -6.2677 | -6.303 | 0.30463 | 8.2903 | 0.59836 | -1.601 | 61.734 | 0.28984 | 61.6698 | -0.033101 | 0.048236 | 61.5524 | 0.003143 | 61.3718 | 62.0848 | 55.1871 | 55.1518 | 61.7594 | 69.7451 | 62.0531 | 59.8538 | 123.1887 | 61.7446 | 123.1246 | 61.4217 | 61.503 | 123.0072 | 61.4579 | 122.8266 | 61.6857 | 61.7308 | 61.6216 | 61.6667
5259.0625 | 123.3078 | -61.4822 | 61.6837 | 0.54764 | -6.4188 | -6.4495 | 0.42825 | 8.5833 | 0.50679 | -1.6056 | 61.7294 | 0.28069 | 61.6652 | -0.033101 | 0.039079 | 61.5616 | 0.007721 | 61.3535 | 62.0299 | 55.0634 | 55.0327 | 61.9105 | 70.0656 | 61.989 | 59.8767 | 123.2116 | 61.7629 | 123.1475 | 61.4491 | 61.5213 | 123.0438 | 61.49 | 122.8357 | 61.6903 | 61.7217 | 61.6261 | 61.6575
5260.0781 | 123.3124 | -61.4594 | 61.7203 | 0.56595 | -6.4829 | -6.2481 | 0.43283 | 8.4872 | 0.52969 | -1.6239 | 61.7248 | 0.28526 | 61.6377 | -0.023943 | 0.043657 | 61.5616 | 0.012299 | 61.3581 | 62.0253 | 54.9764 | 55.2113 | 61.8922 | 69.9465 | 61.989 | 59.8355 | 123.1842 | 61.7446 | 123.0971 | 61.4354 | 61.503 | 123.0209 | 61.4716 | 122.8174 | 61.6812 | 61.7125 | 61.5941 | 61.6255
5261.0625 | 123.4131 | -61.4548 | 61.6379 | 0.57969 | -6.4051 | -6.2206 | 0.4603 | 8.4734 | 0.58005 | -1.6468 | 61.7248 | 0.28984 | 61.6332 | -0.042259 | 0.048236 | 61.557 | 0.012299 | 61.3535 | 62.0345 | 55.0497 | 55.2342 | 61.9151 | 69.9282 | 62.0348 | 59.808 | 123.1796 | 61.7446 | 123.0879 | 61.4125 | 61.503 | 123.0118 | 61.4671 | 122.8083 | 61.6766 | 61.7125 | 61.5849 | 61.6209
5262.0781 | 123.262 | -61.4456 | 61.7065 | 0.58885 | -6.3959 | -6.2709 | 0.50151 | 8.4094 | 0.548 | -1.688 | 61.734 | 0.28526 | 61.6698 | -0.033101 | 0.043657 | 61.5524 | 0.007721 | 61.3627 | 62.0345 | 55.0497 | 55.1747 | 61.9471 | 69.855 | 61.9936 | 59.7576 | 123.1796 | 61.7309 | 123.1154 | 61.4125 | 61.4893 | 122.998 | 61.4533 | 122.8083 | 61.6903 | 61.7263 | 61.6261 | 61.6621
5263.0625 | 123.2437 | -61.4822 | 61.7249 | 0.63005 | -6.4371 | -6.3625 | 0.44657 | 8.2949 | 0.60294 | -1.6834 | 61.7386 | 0.28069 | 61.6652 | -0.028522 | 0.039079 | 61.557 | 0.003143 | 61.3489 | 62.1123 | 55.0451 | 55.1197 | 61.9288 | 69.7771 | 62.0852 | 59.7988 | 123.2208 | 61.7629 | 123.1475 | 61.4537 | 61.5213 | 123.0392 | 61.4854 | 122.8312 | 61.6995 | 61.7354 | 61.6261 | 61.6621
5264.0938 | 123.2941 | -61.4319 | 61.7111 | 0.60258 | -6.4646 | -6.3076 | 0.40078 | 8.5009 | 0.58921 | -1.7017 | 61.7294 | 0.28069 | 61.6332 | -0.03768 | 0.048236 | 61.557 | 0.007721 | 61.3535 | 62.0345 | 54.9673 | 55.1243 | 61.8327 | 69.9328 | 62.0211 | 59.7302 | 123.1613 | 61.7126 | 123.0651 | 61.3942 | 61.4801 | 122.9889 | 61.4396 | 122.7854 | 61.6812 | 61.7217 | 61.5849 | 61.6255
5265.0625 | 123.2895 | -61.4548 | 61.7294 | 0.56595 | -6.6432 | -6.3076 | 0.34126 | 8.5101 | 0.60294 | -1.6971 | 61.7202 | 0.28984 | 61.6423 | -0.028522 | 0.048236 | 61.5524 | 0.007721 | 61.3443 | 62.0207 | 54.8116 | 55.1472 | 61.796 | 69.9648 | 62.0577 | 59.7576 | 123.175 | 61.7446 | 123.0971 | 61.4263 | 61.503 | 123.0072 | 61.4625 | 122.7991 | 61.672 | 61.7125 | 61.5941 | 61.6346
5266.1094 | 123.3261 | -61.4319 | 61.7523 | 0.40571 | -7.5223 | -6.3717 | -0.21731 | 8.185 | 0.42438 | -1.807 | 61.7523 | 0.28526 | 61.6927 | -0.028522 | 0.052814 | 61.5387 | 0.012299 | 61.326 | 61.8376 | 53.9096 | 55.0602 | 61.2146 | 69.6169 | 61.8563 | 59.6249 | 123.1842 | 61.7171 | 123.1246 | 61.4034 | 61.4847 | 122.9706 | 61.4442 | 122.7579 | 61.6995 | 61.74 | 61.6399 | 61.6804
5267.0625 | 123.2758 | -61.4685 | 61.6882 | 0.52017 | -7.449 | -5.9596 | 0.81743 | 8.3315 | 0.4839 | -1.5232 | 61.734 | 0.28526 | 61.6698 | -0.033101 | 0.048236 | 61.5524 | 0.007721 | 61.3352 | 61.9887 | 54.0195 | 55.5089 | 62.2859 | 69.8 | 61.9524 | 59.9454 | 123.2025 | 61.7538 | 123.1383 | 61.4354 | 61.5167 | 123.0209 | 61.4762 | 122.8037 | 61.6857 | 61.7263 | 61.6216 | 61.6621
5268.0781 | 123.2895 | -61.4594 | 61.7432 | 0.60716 | -7.0827 | -5.9733 | 0.46488 | 8.446 | 0.57089 | -1.4636 | 61.7248 | 0.28526 | 61.6332 | -0.033101 | 0.043657 | 61.557 | 0.007721 | 61.3535 | 62.0665 | 54.3766 | 55.486 | 61.9242 | 69.9053 | 62.0302 | 59.9957 | 123.1842 | 61.7446 | 123.0925 | 61.4262 | 61.503 | 123.0164 | 61.4671 | 122.8129 | 61.6812 | 61.7171 | 61.5895 | 61.6255
5269.0625 | 123.3719 | -61.4502 | 61.6974 | 0.57053 | -6.547 | -6.2023 | 0.31379 | 8.4231 | 0.53426 | -1.4682 | 61.7248 | 0.28984 | 61.6332 | -0.033101 | 0.052814 | 61.557 | 0.012299 | 61.3352 | 62.0207 | 54.9032 | 55.2479 | 61.764 | 69.8733 | 61.9845 | 59.982 | 123.175 | 61.74 | 123.0834 | 61.4171 | 61.503 | 123.0072 | 61.4625 | 122.7854 | 61.672 | 61.7125 | 61.5804 | 61.6209
5270.0781 | 123.436 | -61.4365 | 61.6837 | 0.60258 | -6.2265 | -6.1656 | 0.76706 | 8.1759 | 0.56631 | -1.427 | 61.7294 | 0.28526 | 61.6606 | -0.028522 | 0.048236 | 61.5616 | 0.007721 | 61.3443 | 62.039 | 55.21 | 55.2708 | 62.2035 | 69.6123 | 62.0028 | 60.0094 | 123.1659 | 61.7217 | 123.0971 | 61.4079 | 61.4847 | 122.998 | 61.4442 | 122.7808 | 61.6812 | 61.7217 | 61.6124 | 61.6529
5271.0625 | 123.3902 | -61.4639 | 61.6562 | 0.52933 | -6.2769 | -6.1885 | 0.57477 | 8.1942 | 0.48848 | -1.6422 | 61.7202 | 0.28984 | 61.6606 | -0.03768 | 0.043657 | 61.5616 | 0.007721 | 61.3398 | 61.9933 | 55.1871 | 55.2754 | 62.0387 | 69.6581 | 61.9524 | 59.8217 | 123.1842 | 61.7538 | 123.1246 | 61.4262 | 61.5076 | 123.0255 | 61.4716 | 122.8037 | 61.6766 | 61.7125 | 61.617 | 61.6529
5272.0781 | 123.2758 | -61.4502 | 61.7065 | 0.59342 | -6.1395 | -6.0145 | -0.011281 | 8.2583 | 0.55716 | -1.4911 | 61.7248 | 0.28526 | 61.6377 | -0.028522 | 0.048236 | 61.557 | 0.012299 | 61.3443 | 62.0436 | 55.3107 | 55.4356 | 61.4389 | 69.7085 | 62.0074 | 59.9591 | 123.175 | 61.7355 | 123.0879 | 61.4217 | 61.4984 | 123.0072 | 61.4625 | 122.7945 | 61.6766 | 61.7125 | 61.5895 | 61.6255
5273.0625 | 123.3307 | -61.4777 | 61.6837 | 0.68957 | -6.1395 | -5.6574 | 0.70754 | 8.4231 | 0.64872 | -1.3538 | 61.7111 | 0.28984 | 61.6194 | -0.028522 | 0.048236 | 61.5707 | 0.012299 | 61.3627 | 62.1672 | 55.3382 | 55.8202 | 62.1852 | 69.9007 | 62.1264 | 60.1239 | 123.1887 | 61.7675 | 123.0971 | 61.4491 | 61.5259 | 123.0484 | 61.49 | 122.8403 | 61.6628 | 61.6988 | 61.5712 | 61.6071
5274.0938 | 123.3444 | -61.4594 | 61.7157 | 0.77656 | -6.1166 | -5.694 | 0.79911 | 8.4918 | 0.73571 | -1.2576 | 61.7157 | 0.28526 | 61.6469 | -0.019364 | 0.052814 | 61.5753 | 0.007721 | 61.3627 | 62.2359 | 55.3427 | 55.7653 | 62.2585 | 69.9511 | 62.1951 | 60.2017 | 123.175 | 61.7446 | 123.1063 | 61.44 | 61.5122 | 123.0347 | 61.4671 | 122.822 | 61.6628 | 61.7079 | 61.5941 | 61.6392
5275.0625 | 123.2712 | -61.4777 | 61.7111 | 0.63921 | -7.1011 | -5.9917 | 0.61139 | 8.7069 | 0.59836 | -1.395 | 61.7248 | 0.28069 | 61.6652 | -0.028522 | 0.048236 | 61.5616 | 0.007721 | 61.3443 | 62.1169 | 54.3766 | 55.486 | 62.0891 | 70.1846 | 62.076 | 60.0827 | 123.2025 | 61.7583 | 123.1429 | 61.4491 | 61.5259 | 123.0392 | 61.4854 | 122.822 | 61.6766 | 61.7171 | 61.617 | 61.6575
5276.1094 | 123.3032 | -61.4456 | 61.6791 | 0.58427 | -7.3575 | -6.2893 | 0.47862 | 8.2629 | 0.56173 | -1.6925 | 61.734 | 0.29442 | 61.6515 | -0.033101 | 0.052814 | 61.5524 | 0.003143 | 61.3352 | 62.0299 | 54.0881 | 55.1564 | 61.9242 | 69.7085 | 62.0074 | 59.7531 | 123.1796 | 61.74 | 123.0971 | 61.4125 | 61.4984 | 122.998 | 61.4488 | 122.7808 | 61.6812 | 61.7308 | 61.5987 | 61.6483
5277.0625 | 123.3536 | -61.4136 | 61.7157 | 0.60716 | -7.3163 | -6.4037 | -0.16695 | 8.2629 | 0.56631 | -1.8162 | 61.7386 | 0.28526 | 61.6515 | -0.028522 | 0.043657 | 61.5433 | 0.012299 | 61.3398 | 62.0207 | 54.0973 | 55.0098 | 61.2466 | 69.6764 | 61.9799 | 59.5974 | 123.1521 | 61.6988 | 123.0651 | 61.3851 | 61.4572 | 122.9568 | 61.4259 | 122.7533 | 61.6949 | 61.7263 | 61.6078 | 61.6392
5278.0625 | 123.3307 | -61.441 | 61.7432 | 0.70331 | -7.1148 | -5.8863 | 0.15354 | 8.5284 | 0.66246 | -1.8207 | 61.7386 | 0.28069 | 61.6286 | -0.019364 | 0.048236 | 61.557 | 0.003143 | 61.3443 | 62.1443 | 54.3262 | 55.5547 | 61.5946 | 69.9694 | 62.1035 | 59.6203 | 123.1796 | 61.7217 | 123.0696 | 61.4217 | 61.4893 | 122.998 | 61.4442 | 122.7854 | 61.6903 | 61.7354 | 61.5804 | 61.6255
5279.0938 | 123.2986 | -61.4319 | 61.702 | 0.68041 | -7.2567 | -5.6803 | -0.22189 | 8.3361 | 0.63499 | -1.9443 | 61.7248 | 0.28526 | 61.6423 | -0.033101 | 0.043657 | 61.5524 | 0.003143 | 61.3306 | 62.1123 | 54.1751 | 55.7516 | 61.21 | 69.768 | 62.0669 | 59.4875 | 123.1567 | 61.7171 | 123.0742 | 61.3988 | 61.4755 | 122.9843 | 61.435 | 122.7625 | 61.6812 | 61.7217 | 61.5987 | 61.6392
5280.0625 | 123.3444 | -61.441 | 61.6974 | 0.60716 | -7.4399 | -6.1702 | -0.16237 | 8.2857 | 0.57089 | -2.0451 | 61.7386 | 0.28526 | 61.6652 | -0.028522 | 0.052814 | 61.5433 | 0.007721 | 61.326 | 62.0482 | 54.0012 | 55.2708 | 61.2787 | 69.7268 | 62.0119 | 59.396 | 123.1796 | 61.7263 | 123.1063 | 61.4125 | 61.4939 | 122.9843 | 61.4488 | 122.7671 | 61.6857 | 61.7308 | 61.6124 | 61.6575
5281.0938 | 123.3582 | -61.4182 | 61.7111 | 0.63921 | -7.4628 | -6.097 | -0.13032 | 8.3086 | 0.59836 | -1.9535 | 61.7431 | 0.28526 | 61.6881 | -0.028522 | 0.048236 | 61.5433 | 0.007721 | 61.326 | 62.0574 | 53.9554 | 55.3212 | 61.2878 | 69.7268 | 62.0165 | 59.4646 | 123.1613 | 61.7034 | 123.1063 | 61.3896 | 61.4664 | 122.9614 | 61.4259 | 122.7442 | 61.6949 | 61.7354 | 61.6399 | 61.6804
5282.0625 | 123.2803 | -61.4319 | 61.7294 | 0.61174 | -7.4353 | -6.129 | -0.047909 | 8.4139 | 0.57547 | -1.839 | 61.7477 | 0.28526 | 61.679 | -0.028522 | 0.043657 | 61.5524 | 0.007721 | 61.3352 | 62.0436 | 53.9966 | 55.3029 | 61.384 | 69.8458 | 62.0074 | 59.5928 | 123.1796 | 61.7171 | 123.1108 | 61.4034 | 61.4755 | 122.9843 | 61.4396 | 122.7671 | 61.7041 | 61.74 | 61.6353 | 61.6712
5283.0938 | 123.381 | -61.4182 | 61.7386 | 0.57969 | -7.5406 | -6.1244 | 0.002454 | 8.4734 | 0.548 | -1.72 | 61.7431 | 0.29442 | 61.679 | -0.03768 | 0.048236 | 61.5433 | 0.007721 | 61.3306 | 61.9978 | 53.8775 | 55.2937 | 61.4206 | 69.8916 | 61.9662 | 59.6981 | 123.1613 | 61.7126 | 123.0971 | 61.3805 | 61.4664 | 122.9614 | 61.4259 | 122.7488 | 61.6949 | 61.7354 | 61.6307 | 61.6712
5284.0625 | 123.3353 | -61.4639 | 61.702 | 0.70331 | -7.2888 | -5.8451 | 0.19475 | 8.7893 | 0.66704 | -1.7795 | 61.7294 | 0.28526 | 61.6606 | -0.033101 | 0.052814 | 61.557 | 0.007721 | 61.3443 | 62.1672 | 54.1751 | 55.6188 | 61.6587 | 70.2533 | 62.131 | 59.6844 | 123.1933 | 61.7492 | 123.1246 | 61.4308 | 61.5167 | 123.0209 | 61.4716 | 122.8083 | 61.6766 | 61.7217 | 61.6078 | 61.6529
5285.0938 | 123.2895 | -61.4365 | 61.7477 | 0.69415 | -7.4078 | -5.9138 | 0.039082 | 8.3315 | 0.65788 | -1.9169 | 61.734 | 0.28069 | 61.6469 | -0.033101 | 0.052814 | 61.5478 | 0.007721 | 61.3352 | 62.1306 | 54.0286 | 55.5226 | 61.4755 | 69.768 | 62.0943 | 59.5196 | 123.1704 | 61.7171 | 123.0834 | 61.4034 | 61.4893 | 122.9843 | 61.4442 | 122.7717 | 61.6812 | 61.7263 | 61.5941 | 61.6392
5286.0625 | 123.317 | -61.4685 | 61.7111 | 0.68041 | -7.3437 | -5.8268 | 0.048239 | 8.4963 | 0.63957 | -1.926 | 61.7431 | 0.28984 | 61.6377 | -0.028522 | 0.043657 | 61.5524 | 0.007721 | 61.3352 | 62.1489 | 54.1248 | 55.6417 | 61.5167 | 69.9648 | 62.1081 | 59.5425 | 123.2116 | 61.7583 | 123.1063 | 61.44 | 61.5122 | 123.0209 | 61.4762 | 122.8037 | 61.6995 | 61.7354 | 61.5941 | 61.63
5287.0781 | 123.3536 | -61.4182 | 61.7065 | 0.71704 | -7.2522 | -5.6574 | 0.23596 | 8.6978 | 0.67619 | -1.9031 | 61.7294 | 0.28526 | 61.6377 | -0.019364 | 0.052814 | 61.5707 | 0.012299 | 61.3443 | 62.1352 | 54.166 | 55.7607 | 61.6541 | 70.1159 | 62.0943 | 59.515 | 123.1475 | 61.7034 | 123.0559 | 61.3988 | 61.471 | 122.9889 | 61.4305 | 122.7625 | 61.6766 | 61.7171 | 61.5849 | 61.6255
5288.0625 | 123.2666 | -61.4502 | 61.7157 | 0.68957 | -7.3895 | -5.9001 | 0.33211 | 8.771 | 0.64415 | -1.9855 | 61.7294 | 0.28069 | 61.6469 | -0.028522 | 0.039079 | 61.557 | 0.007721 | 61.3352 | 62.1398 | 54.0607 | 55.5501 | 61.7823 | 70.2212 | 62.0943 | 59.4646 | 123.1796 | 61.7309 | 123.0971 | 61.4217 | 61.4893 | 123.0072 | 61.4579 | 122.7854 | 61.6903 | 61.7217 | 61.6078 | 61.6392
5289.0781 | 123.3078 | -61.4227 | 61.7569 | 0.67584 | -7.449 | -5.9962 | 0.080288 | 8.5696 | 0.63499 | -2.2282 | 61.7386 | 0.28069 | 61.6698 | -0.03768 | 0.048236 | 61.5433 | 0.012299 | 61.3398 | 62.0986 | 53.9737 | 55.4265 | 61.503 | 69.9923 | 62.0577 | 59.1945 | 123.1613 | 61.7034 | 123.0925 | 61.385 | 61.471 | 122.966 | 61.435 | 122.7625 | 61.6903 | 61.7263 | 61.6216 | 61.6575
5290.0625 | 123.2941 | -61.4594 | 61.702 | 0.68499 | -7.3483 | -5.7994 | 0.20391 | 8.7069 | 0.63499 | -2.1595 | 61.7431 | 0.28984 | 61.679 | -0.033101 | 0.052814 | 61.5478 | -0.001436 | 61.3443 | 62.1443 | 54.111 | 55.66 | 61.6633 | 70.1663 | 62.0943 | 59.2998 | 123.2025 | 61.7492 | 123.1383 | 61.4262 | 61.5122 | 123.0072 | 61.4579 | 122.8037 | 61.6903 | 61.7446 | 61.6261 | 61.6804
5291.1094 | 123.2849 | -61.4777 | 61.7477 | 0.68499 | -7.3483 | -5.4789 | 0.21307 | 8.5925 | 0.64415 | -1.9993 | 61.734 | 0.28526 | 61.6698 | -0.033101 | 0.052814 | 61.557 | -0.001436 | 61.3489 | 62.1627 | 54.1293 | 55.9988 | 61.6907 | 70.0701 | 62.1218 | 59.4784 | 123.2116 | 61.7629 | 123.1475 | 61.4446 | 61.5305 | 123.0347 | 61.4762 | 122.8266 | 61.6812 | 61.7354 | 61.617 | 61.6712
5292.0625 | 123.317 | -61.4456 | 61.734 | 0.74451 | -7.4078 | -5.4697 | 0.31379 | 8.5513 | 0.70366 | -2.1412 | 61.7386 | 0.28526 | 61.6698 | -0.028522 | 0.052814 | 61.557 | 0.012299 | 61.3581 | 62.1901 | 54.0378 | 55.9759 | 61.7594 | 69.9969 | 62.1493 | 59.3044 | 123.1842 | 61.7309 | 123.1154 | 61.4171 | 61.4984 | 123.0026 | 61.4579 | 122.8037 | 61.6857 | 61.7263 | 61.617 | 61.6575
5293.0938 | 123.23 | -61.4365 | 61.7249 | 0.75367 | -7.3987 | -5.2866 | 0.21307 | 8.6199 | 0.7174 | -2.2007 | 61.734 | 0.28526 | 61.6515 | -0.033101 | 0.048236 | 61.5616 | 0.012299 | 61.3535 | 62.1901 | 54.0378 | 56.1499 | 61.6495 | 70.0564 | 62.1539 | 59.2357 | 123.1704 | 61.7217 | 123.0879 | 61.4034 | 61.4847 | 122.998 | 61.4488 | 122.79 | 61.6857 | 61.7217 | 61.6032 | 61.6392
5294.0625 | 123.2666 | -61.4456 | 61.7386 | 0.63005 | -7.2567 | -5.543 | 0.094024 | 8.5513 | 0.59378 | -2.1 | 61.734 | 0.28526 | 61.6377 | -0.033101 | 0.043657 | 61.5524 | 0.012299 | 61.3535 | 62.0757 | 54.1889 | 55.9027 | 61.5396 | 69.9969 | 62.0394 | 59.3456 | 123.1796 | 61.7309 | 123.0834 | 61.4125 | 61.4893 | 122.998 | 61.4579 | 122.7991 | 61.6903 | 61.7217 | 61.5941 | 61.6255
5295.0781 | 123.3719 | -61.4227 | 61.6974 | 0.68499 | -6.9866 | -5.6345 | 0.21764 | 8.5604 | 0.64872 | -2.0039 | 61.7202 | 0.28069 | 61.6332 | -0.033101 | 0.052814 | 61.5616 | 0.007721 | 61.3627 | 62.1077 | 54.4361 | 55.7882 | 61.6404 | 69.9832 | 62.0715 | 59.4189 | 123.143 | 61.7034 | 123.0559 | 61.3896 | 61.4755 | 122.9843 | 61.4304 | 122.7854 | 61.6674 | 61.7125 | 61.5804 | 61.6255
5296.0625 | 123.3719 | -61.4456 | 61.6882 | 0.62089 | -6.8584 | -5.662 | 0.13065 | 8.3544 | 0.57089 | -2.0359 | 61.734 | 0.28526 | 61.6423 | -0.028522 | 0.048236 | 61.5524 | 0.007721 | 61.3443 | 62.0665 | 54.5872 | 55.7836 | 61.5763 | 69.8 | 62.0165 | 59.4097 | 123.1796 | 61.7309 | 123.0879 | 61.4171 | 61.4939 | 122.998 | 61.4533 | 122.79 | 61.6857 | 61.7263 | 61.5941 | 61.6346
5297.0938 | 123.3124 | -61.4639 | 61.7065 | 0.60258 | -6.689 | -5.5704 | 0.039082 | 8.5284 | 0.56631 | -2.0725 | 61.7294 | 0.28069 | 61.6606 | -0.033101 | 0.043657 | 61.5524 | 0.007721 | 61.3443 | 62.0665 | 54.775 | 55.8935 | 61.503 | 69.9923 | 62.0302 | 59.3914 | 123.1933 | 61.7446 | 123.1246 | 61.4308 | 61.5076 | 123.0164 | 61.4716 | 122.8083 | 61.6857 | 61.7217 | 61.617 | 61.6529
5298.0625 | 123.317 | -61.4319 | 61.6837 | 0.65752 | -6.6249 | -5.4972 | 0.094024 | 8.5604 | 0.62125 | -2.1092 | 61.7386 | 0.28069 | 61.6744 | -0.023943 | 0.048236 | 61.5616 | 0.012299 | 61.3489 | 62.0894 | 54.807 | 55.9347 | 61.5259 | 69.9923 | 62.0531 | 59.3227 | 123.1704 | 61.7126 | 123.1063 | 61.4079 | 61.4801 | 122.9935 | 61.4442 | 122.7808 | 61.6903 | 61.7263 | 61.6261 | 61.6621
5299.0781 | 123.4131 | -61.4227 | 61.7065 | 0.50186 | -6.7302 | -5.7673 | 0.002454 | 8.2583 | 0.46559 | -2.1733 | 61.7431 | 0.28984 | 61.679 | -0.023943 | 0.048236 | 61.5524 | 0.003143 | 61.3352 | 61.9246 | 54.6926 | 55.6554 | 61.4252 | 69.681 | 61.8883 | 59.2495 | 123.1659 | 61.7126 | 123.1017 | 61.3988 | 61.471 | 122.9752 | 61.4259 | 122.7579 | 61.6949 | 61.74 | 61.6307 | 61.6758
5300.0625 | 123.2986 | -61.4273 | 61.6974 | 0.62547 | -6.4967 | -5.4605 | 0.21307 | 8.3819 | 0.58463 | -2.0908 | 61.734 | 0.28526 | 61.6698 | -0.028522 | 0.048236 | 61.5616 | 0.012299 | 61.3489 | 62.0528 | 54.9307 | 55.9668 | 61.6404 | 69.8092 | 62.0119 | 59.3365 | 123.1613 | 61.7126 | 123.0971 | 61.3988 | 61.4755 | 122.9889 | 61.4396 | 122.7762 | 61.6857 | 61.7217 | 61.6216 | 61.6575
5301.1094 | 123.4131 | -61.4182 | 61.6837 | 0.63921 | -6.6157 | -5.4468 | 0.28174 | 8.2857 | 0.60294 | -1.9993 | 61.7248 | 0.28526 | 61.6332 | -0.028522 | 0.048236 | 61.5616 | 0.007721 | 61.3489 | 62.0574 | 54.8025 | 55.9714 | 61.6999 | 69.7039 | 62.0211 | 59.4189 | 123.143 | 61.7034 | 123.0513 | 61.3896 | 61.4664 | 122.9797 | 61.4259 | 122.7671 | 61.6766 | 61.7171 | 61.5849 | 61.6255
5302.0625 | 123.3444 | -61.4685 | 61.6974 | 0.61632 | -6.808 | -5.488 | 0.24969 | 8.6199 | 0.57547 | -2.1412 | 61.7248 | 0.28526 | 61.6286 | -0.028522 | 0.048236 | 61.5616 | 0.003143 | 61.3489 | 62.0848 | 54.6605 | 55.9805 | 61.7182 | 70.0884 | 62.044 | 59.3273 | 123.1933 | 61.7538 | 123.0971 | 61.44 | 61.5167 | 123.0301 | 61.4716 | 122.8174 | 61.6766 | 61.7217 | 61.5804 | 61.6255
5303.0781 | 123.4222 | -61.441 | 61.7111 | 0.71246 | -6.8813 | -5.3552 | 0.31837 | 8.2629 | 0.68077 | -2.2099 | 61.7248 | 0.28984 | 61.6332 | -0.03768 | 0.048236 | 61.5616 | 0.007721 | 61.3581 | 62.1535 | 54.5598 | 56.0858 | 61.7594 | 69.7039 | 62.1218 | 59.2312 | 123.1659 | 61.7309 | 123.0742 | 61.4034 | 61.4893 | 123.0026 | 61.4488 | 122.7991 | 61.6766 | 61.7171 | 61.5849 | 61.6255
5304.0625 | 123.3032 | -61.4456 | 61.7111 | 0.68499 | -7.1743 | -5.3644 | 0.27716 | 8.533 | 0.64415 | -2.1504 | 61.7248 | 0.28526 | 61.6423 | -0.028522 | 0.043657 | 61.557 | 0.012299 | 61.3443 | 62.1306 | 54.2713 | 56.0812 | 61.7228 | 69.9786 | 62.0898 | 59.2953 | 123.1704 | 61.7309 | 123.0879 | 61.4171 | 61.4893 | 123.0026 | 61.4579 | 122.79 | 61.6812 | 61.7125 | 61.5987 | 61.63
5305.0781 | 123.4039 | -61.4136 | 61.6928 | 0.68499 | -7.3025 | -5.456 | 0.23138 | 8.4414 | 0.64415 | -2.1687 | 61.7386 | 0.28526 | 61.6606 | -0.033101 | 0.048236 | 61.5524 | 0.007721 | 61.3398 | 62.0986 | 54.111 | 55.9576 | 61.645 | 69.855 | 62.0577 | 59.2449 | 123.1521 | 61.6988 | 123.0742 | 61.3805 | 61.4618 | 122.966 | 61.4213 | 122.7533 | 61.6903 | 61.7308 | 61.6124 | 61.6529
5306.0625 | 123.2483 | -61.4685 | 61.7111 | 0.67584 | -7.3575 | -5.4514 | 0.24511 | 8.4597 | 0.63957 | -2.1321 | 61.7431 | 0.28984 | 61.6744 | -0.033101 | 0.052814 | 61.5524 | 0.012299 | 61.3489 | 62.1443 | 54.111 | 56.0171 | 61.7136 | 69.9282 | 62.1081 | 59.3365 | 123.2116 | 61.7583 | 123.1429 | 61.4354 | 61.5213 | 123.0209 | 61.4808 | 122.8174 | 61.6903 | 61.7308 | 61.6216 | 61.6621
5307.0781 | 123.381 | -61.4502 | 61.7065 | 0.64837 | -7.3208 | -5.5155 | 0.17644 | 8.2766 | 0.6121 | -1.981 | 61.7431 | 0.28526 | 61.6698 | -0.033101 | 0.052814 | 61.5478 | 0.012299 | 61.3489 | 62.0986 | 54.1294 | 55.9347 | 61.6266 | 69.7268 | 62.0623 | 59.4692 | 123.1933 | 61.7355 | 123.12 | 61.4171 | 61.503 | 122.998 | 61.4625 | 122.7991 | 61.6903 | 61.7308 | 61.617 | 61.6575
5308.0625 | 123.3444 | -61.4182 | 61.7477 | 0.54306 | -7.2705 | -5.6208 | -0.01586 | 7.6494 | 0.50222 | -2.0405 | 61.7523 | 0.28984 | 61.679 | -0.033101 | 0.048236 | 61.5433 | 0.003143 | 61.3489 | 61.9612 | 54.1477 | 55.7974 | 61.4023 | 69.0676 | 61.9204 | 59.3777 | 123.1704 | 61.708 | 123.0971 | 61.3851 | 61.4664 | 122.9614 | 61.4213 | 122.7671 | 61.7041 | 61.7491 | 61.6307 | 61.6758
5309.0781 | 123.381 | -61.4227 | 61.7157 | 0.48354 | -7.3437 | -5.6299 | -0.18984 | 7.8371 | 0.4427 | -2.0405 | 61.7431 | 0.28526 | 61.6606 | -0.028522 | 0.048236 | 61.5387 | 0.003143 | 61.3489 | 61.9063 | 54.079 | 55.7928 | 61.2329 | 69.2598 | 61.8654 | 59.3822 | 123.1659 | 61.708 | 123.0834 | 61.3942 | 61.471 | 122.9614 | 61.4259 | 122.7717 | 61.6949 | 61.74 | 61.6124 | 61.6575
5310.0625 | 123.2803 | -61.4502 | 61.7432 | 0.51559 | -7.2155 | -5.6162 | -0.10285 | 8.1621 | 0.47932 | -1.9581 | 61.7386 | 0.28526 | 61.6515 | -0.033101 | 0.048236 | 61.5478 | 0.007721 | 61.3489 | 61.9658 | 54.2347 | 55.834 | 61.3473 | 69.6123 | 61.9295 | 59.4921 | 123.1887 | 61.7355 | 123.1017 | 61.4171 | 61.4984 | 122.998 | 61.4579 | 122.7991 | 61.6903 | 61.7308 | 61.6032 | 61.6438
5311.1094 | 123.2895 | -61.4639 | 61.6928 | 0.41029 | -6.2998 | -5.5704 | -0.079959 | 8.0202 | 0.38318 | -2.0268 | 61.7294 | 0.28984 | 61.6377 | -0.028522 | 0.043657 | 61.5524 | 0.007721 | 61.3489 | 61.8742 | 55.1642 | 55.8935 | 61.384 | 69.4842 | 61.8471 | 59.4372 | 123.1933 | 61.7538 | 123.1017 | 61.4354 | 61.5076 | 123.0164 | 61.4716 | 122.8129 | 61.6857 | 61.7217 | 61.5941 | 61.63
5312.0625 | 123.2803 | -61.4548 | 61.7294 | 0.52017 | -7.037 | -5.3369 | 0.24969 | 8.2812 | 0.47932 | -2.1504 | 61.7386 | 0.28984 | 61.6561 | -0.023943 | 0.048236 | 61.557 | 0.007721 | 61.3535 | 61.9749 | 54.4178 | 56.1179 | 61.7045 | 69.7359 | 61.9341 | 59.3044 | 123.1933 | 61.7446 | 123.1108 | 61.4308 | 61.503 | 123.0118 | 61.4625 | 122.8083 | 61.6903 | 61.7308 | 61.6078 | 61.6483
5313.0938 | 123.4406 | -61.4273 | 61.702 | 0.62089 | -7.5269 | -5.5063 | 0.080288 | 7.7501 | 0.58005 | -2.0451 | 61.7431 | 0.28526 | 61.6835 | -0.033101 | 0.043657 | 61.5478 | 0.007721 | 61.3352 | 62.0482 | 53.9004 | 55.921 | 61.5076 | 69.1774 | 62.0074 | 59.3822 | 123.1704 | 61.7126 | 123.1108 | 61.3942 | 61.471 | 122.9752 | 61.435 | 122.7625 | 61.6995 | 61.7354 | 61.6399 | 61.6758
5314.0625 | 123.2895 | -61.4365 | 61.734 | 0.87728 | -6.5928 | -5.5842 | 0.10776 | 7.9653 | 0.84102 | -1.981 | 61.7248 | 0.28526 | 61.6698 | -0.033101 | 0.048236 | 61.5616 | 0.007721 | 61.3443 | 62.3137 | 54.8437 | 55.8523 | 61.5442 | 69.4018 | 62.2775 | 59.4555 | 123.1613 | 61.7217 | 123.1063 | 61.4034 | 61.4847 | 122.998 | 61.4442 | 122.7808 | 61.6766 | 61.7171 | 61.6216 | 61.6621
5315.0781 | 123.3994 | -61.4319 | 61.6882 | 0.84981 | -6.5058 | -5.9047 | -0.17153 | 8.1209 | 0.80897 | -1.9947 | 61.7294 | 0.28526 | 61.6698 | -0.033101 | 0.039079 | 61.5524 | 0.012299 | 61.3352 | 62.2817 | 54.9261 | 55.5272 | 61.2604 | 69.5528 | 62.2409 | 59.4372 | 123.1613 | 61.7171 | 123.1017 | 61.3988 | 61.471 | 122.9843 | 61.4442 | 122.7671 | 61.6903 | 61.7171 | 61.6307 | 61.6575
5316.0625 | 123.3307 | -61.4227 | 61.7249 | 0.73078 | -6.5058 | -5.7307 | -0.13948 | 8.0202 | 0.68993 | -2.1321 | 61.7431 | 0.28526 | 61.6698 | -0.023943 | 0.043657 | 61.5524 | 0.003143 | 61.3398 | 62.1535 | 54.9169 | 55.6921 | 61.2832 | 69.443 | 62.1127 | 59.2907 | 123.1659 | 61.708 | 123.0925 | 61.3988 | 61.4664 | 122.9752 | 61.4259 | 122.7625 | 61.6995 | 61.74 | 61.6261 | 61.6667
5317.0938 | 123.3078 | -61.4365 | 61.7523 | 0.66668 | -6.5058 | -5.5658 | 0.07571 | 8.1759 | 0.61668 | -2.1412 | 61.7248 | 0.28526 | 61.6377 | -0.023943 | 0.043657 | 61.5616 | -0.001436 | 61.3398 | 62.1031 | 54.9307 | 55.8706 | 61.5122 | 69.6123 | 62.0531 | 59.2953 | 123.1613 | 61.7217 | 123.0742 | 61.4125 | 61.4801 | 122.998 | 61.435 | 122.7762 | 61.6812 | 61.7263 | 61.5941 | 61.6392
5318.0625 | 123.317 | -61.4136 | 61.7203 | 0.63005 | -6.3959 | -5.5567 | 0.039082 | 8.0523 | 0.58921 | -2.1687 | 61.7294 | 0.28526 | 61.6377 | -0.033101 | 0.057392 | 61.5616 | 0.007721 | 61.3443 | 62.0436 | 55.0177 | 55.8569 | 61.4527 | 69.4658 | 62.0028 | 59.2449 | 123.143 | 61.6988 | 123.0513 | 61.3805 | 61.471 | 122.9752 | 61.4213 | 122.7579 | 61.672 | 61.7217 | 61.5804 | 61.63
5319.0938 | 123.4177 | -61.4273 | 61.7111 | 0.56595 | -7.0186 | -5.7032 | -0.034174 | 8.3132 | 0.52969 | -2.3655 | 61.734 | 0.28984 | 61.6515 | -0.028522 | 0.052814 | 61.5524 | 0.007721 | 61.3352 | 61.9933 | 54.4087 | 55.7241 | 61.3931 | 69.7405 | 61.957 | 59.0618 | 123.1613 | 61.7171 | 123.0788 | 61.3988 | 61.4801 | 122.9797 | 61.435 | 122.7625 | 61.6812 | 61.7263 | 61.5987 | 61.6438
5320.0625 | 123.3719 | -61.409 | 61.7111 | 0.47439 | -7.5177 | -5.9871 | -0.18069 | 7.9195 | 0.43812 | -2.3564 | 61.7523 | 0.28526 | 61.6652 | -0.033101 | 0.048236 | 61.5341 | 0.012299 | 61.3215 | 61.8834 | 53.8913 | 55.4219 | 61.2283 | 69.3285 | 61.8471 | 59.0526 | 123.1613 | 61.6943 | 123.0742 | 61.3759 | 61.4572 | 122.9431 | 61.4213 | 122.7305 | 61.7041 | 61.74 | 61.617 | 61.6529
5321.1094 | 123.3307 | -61.4548 | 61.7203 | 0.64379 | -7.5727 | -5.8909 | -0.093694 | 8.0111 | 0.60294 | -2.0451 | 61.7477 | 0.28526 | 61.6881 | -0.028522 | 0.048236 | 61.5478 | 0.012299 | 61.3215 | 62.0986 | 53.8821 | 55.5638 | 61.3611 | 69.4658 | 62.0577 | 59.4097 | 123.2025 | 61.74 | 123.1429 | 61.4263 | 61.503 | 123.0026 | 61.4671 | 122.7762 | 61.6995 | 61.7354 | 61.6399 | 61.6758
5322.0625 | 123.2483 | -61.4273 | 61.7477 | 0.58885 | -7.5223 | -5.6574 | -0.011281 | 8.034 | 0.56631 | -2.1458 | 61.7523 | 0.28984 | 61.6881 | -0.023943 | 0.048236 | 61.5433 | 0.003143 | 61.3352 | 62.0162 | 53.905 | 55.7699 | 61.416 | 69.4613 | 61.9936 | 59.2815 | 123.1796 | 61.7171 | 123.1154 | 61.4034 | 61.4755 | 122.9706 | 61.4305 | 122.7625 | 61.7041 | 61.7491 | 61.6399 | 61.685
5323.0781 | 123.3902 | -61.441 | 61.702 | 0.65294 | -7.6917 | -5.7627 | -0.15779 | 7.8188 | 0.61668 | -2.1687 | 61.7569 | 0.28069 | 61.679 | -0.033101 | 0.052814 | 61.5387 | 0.007721 | 61.3215 | 62.094 | 53.7493 | 55.6783 | 61.2832 | 69.2598 | 62.0577 | 59.2724 | 123.1979 | 61.7217 | 123.12 | 61.4079 | 61.4939 | 122.9797 | 61.4488 | 122.7625 | 61.7041 | 61.7491 | 61.6261 | 61.6712
5324.0625 | 123.317 | -61.4273 | 61.7294 | 0.67126 | -7.678 | -5.6528 | -0.199 | 7.7227 | 0.63957 | -2.2236 | 61.7431 | 0.28069 | 61.679 | -0.028522 | 0.048236 | 61.5433 | 0.007721 | 61.326 | 62.0986 | 53.7493 | 55.7745 | 61.2283 | 69.15 | 62.0669 | 59.2037 | 123.1704 | 61.708 | 123.1063 | 61.3988 | 61.4755 | 122.9706 | 61.435 | 122.7533 | 61.6949 | 61.7354 | 61.6307 | 61.6712
5325.0938 | 123.317 | -61.4044 | 61.734 | 0.54306 | -7.7146 | -5.8177 | -0.26768 | 7.6174 | 0.52053 | -2.1458 | 61.7477 | 0.28526 | 61.6561 | -0.033101 | 0.048236 | 61.5387 | 0.012299 | 61.3215 | 61.9475 | 53.6898 | 55.5868 | 61.1367 | 69.0218 | 61.9249 | 59.2586 | 123.1521 | 61.6897 | 123.0605 | 61.3713 | 61.4527 | 122.9431 | 61.4167 | 122.7259 | 61.6995 | 61.7354 | 61.6078 | 61.6438
5326.0625 | 123.3444 | -61.4273 | 61.734 | 0.35993 | -7.6368 | -5.6574 | -0.20816 | 7.5166 | 0.33739 | -2.2831 | 61.7523 | 0.28526 | 61.6606 | -0.028522 | 0.048236 | 61.5387 | 0.007721 | 61.3215 | 61.7872 | 53.7905 | 55.7699 | 61.2191 | 68.944 | 61.7647 | 59.1442 | 123.1796 | 61.7126 | 123.0879 | 61.3988 | 61.4755 | 122.966 | 61.435 | 122.7488 | 61.7041 | 61.7446 | 61.6124 | 61.6529
5327.0781 | 123.381 | -61.409 | 61.6837 | 0.29125 | -7.4262 | -5.662 | -0.20358 | 6.4363 | 0.30077 | -2.512 | 61.7614 | 0.28526 | 61.6652 | -0.033101 | 0.043657 | 61.525 | 0.007721 | 61.2986 | 61.7002 | 53.9828 | 55.747 | 61.2054 | 67.8452 | 61.7098 | 58.897 | 123.1704 | 61.6943 | 123.0742 | 61.3759 | 61.4527 | 122.934 | 61.4167 | 122.7076 | 61.7178 | 61.7537 | 61.6216 | 61.6575
5328.0625 | 123.3902 | -61.3907 | 61.6974 | 0.46523 | -6.3959 | -5.6803 | -0.28141 | 6.4179 | 0.43354 | -2.4983 | 61.7569 | 0.28984 | 61.6744 | -0.028522 | 0.048236 | 61.5295 | 0.007721 | 61.3123 | 61.8559 | 54.9948 | 55.7104 | 61.1093 | 67.8086 | 61.8242 | 58.8924 | 123.1476 | 61.6805 | 123.0651 | 61.3622 | 61.4389 | 122.9202 | 61.3984 | 122.703 | 61.7086 | 61.7491 | 61.6261 | 61.6667
5329.0938 | 123.3673 | -61.3861 | 61.7065 | 0.50186 | -7.1743 | -5.7719 | -0.4325 | 6.45 | 0.46559 | -2.4617 | 61.766 | 0.28069 | 61.7018 | -0.033101 | 0.043657 | 61.5204 | 0.007721 | 61.3031 | 61.888 | 54.2118 | 55.6142 | 60.9536 | 67.8361 | 61.8517 | 58.9244 | 123.1521 | 61.6668 | 123.088 | 61.353 | 61.4298 | 122.9065 | 61.3938 | 122.6893 | 61.7224 | 61.7583 | 61.6582 | 61.6941
5330.0625 | 123.2666 | -61.4365 | 61.702 | 0.42402 | -7.5223 | -5.7215 | -0.28141 | 7.2832 | 0.43812 | -2.3747 | 61.7706 | 0.28526 | 61.6973 | -0.028522 | 0.039079 | 61.5295 | 0.003143 | 61.3077 | 61.8605 | 53.9142 | 55.7149 | 61.155 | 68.7196 | 61.8746 | 59.0618 | 123.2071 | 61.7217 | 123.1337 | 61.4079 | 61.4755 | 122.966 | 61.4396 | 122.7442 | 61.7315 | 61.7675 | 61.6582 | 61.6941
5331.0938 | 123.3673 | -61.4044 | 61.702 | 0.3874 | -7.536 | -5.8406 | -0.29515 | 7.654 | 0.39233 | -2.1 | 61.766 | 0.28984 | 61.6927 | -0.033101 | 0.039079 | 61.5341 | 0.007721 | 61.3077 | 61.7918 | 53.8684 | 55.5639 | 61.1093 | 69.0584 | 61.7968 | 59.3044 | 123.1704 | 61.6943 | 123.0971 | 61.3713 | 61.4435 | 122.9385 | 61.4121 | 122.7121 | 61.7269 | 61.7583 | 61.6536 | 61.685
5332.0625 | 123.4131 | -61.3724 | 61.7157 | 0.25462 | -7.6276 | -5.8726 | -0.25394 | 7.6174 | 0.26414 | -2.1412 | 61.7614 | 0.28069 | 61.679 | -0.028522 | 0.057392 | 61.5341 | 0.007721 | 61.3123 | 61.627 | 53.7448 | 55.4998 | 61.1184 | 68.9897 | 61.6365 | 59.2312 | 123.1338 | 61.6531 | 123.0513 | 61.3439 | 61.4298 | 122.9065 | 61.3801 | 122.6847 | 61.7041 | 61.7537 | 61.6216 | 61.6712
5333.0781 | 123.3719 | -61.409 | 61.6745 | 0.22715 | -7.5406 | -5.8497 | -0.33178 | 7.5624 | 0.23209 | -2.0771 | 61.7569 | 0.28069 | 61.6698 | -0.028522 | 0.048236 | 61.5295 | 0.012299 | 61.3077 | 61.6362 | 53.8684 | 55.5593 | 61.0772 | 68.9714 | 61.6411 | 59.3319 | 123.1659 | 61.6897 | 123.0788 | 61.3805 | 61.4572 | 122.9385 | 61.4213 | 122.7167 | 61.7086 | 61.7446 | 61.6216 | 61.6575
5334.0625 | 123.4131 | -61.3998 | 61.734 | 0.40571 | -7.5864 | -5.7902 | -0.52865 | 6.4042 | 0.45643 | -2.2419 | 61.7614 | 0.28526 | 61.6606 | -0.028522 | 0.052814 | 61.5204 | 0.012299 | 61.3031 | 61.8056 | 53.8134 | 55.6096 | 60.8712 | 67.804 | 61.8563 | 59.1579 | 123.1613 | 61.6851 | 123.0605 | 61.3713 | 61.4527 | 122.9202 | 61.4121 | 122.703 | 61.7086 | 61.7491 | 61.6078 | 61.6483
5335.0938 | 123.3536 | -61.4456 | 61.7569 | 0.50186 | -7.4078 | -5.8955 | -0.47829 | 6.6331 | 0.51137 | -2.2511 | 61.7614 | 0.28526 | 61.6652 | -0.033101 | 0.043657 | 61.5295 | 0.007721 | 61.2986 | 61.9475 | 54.0378 | 55.5501 | 60.9673 | 68.0787 | 61.957 | 59.1945 | 123.2071 | 61.7309 | 123.1108 | 61.4125 | 61.4893 | 122.9752 | 61.4533 | 122.7442 | 61.7178 | 61.7537 | 61.6216 | 61.6575
5336.0625 | 123.3353 | -61.4273 | 61.7615 | 0.52475 | -7.33 | -5.7078 | -0.28141 | 7.828 | 0.52511 | -2.1733 | 61.7477 | 0.28526 | 61.6652 | -0.028522 | 0.052814 | 61.5387 | 0.012299 | 61.326 | 61.9521 | 54.0973 | 55.7195 | 61.1459 | 69.2553 | 61.9524 | 59.2541 | 123.175 | 61.7126 | 123.0925 | 61.3988 | 61.4801 | 122.966 | 61.4396 | 122.7533 | 61.6949 | 61.7354 | 61.6124 | 61.6529
5337.0938 | 123.3765 | -61.4273 | 61.7111 | 0.27294 | -7.3346 | -5.5475 | -0.31804 | 8.0614 | 0.24125 | -2.2007 | 61.7523 | 0.28069 | 61.679 | -0.028522 | 0.043657 | 61.5341 | 0.012299 | 61.3123 | 61.7002 | 54.0927 | 55.8798 | 61.1093 | 69.4887 | 61.6686 | 59.2266 | 123.1796 | 61.708 | 123.1063 | 61.3988 | 61.471 | 122.9614 | 61.4396 | 122.7396 | 61.7086 | 61.74 | 61.6353 | 61.6667
5338.0625 | 123.4222 | -61.3861 | 61.7157 | 0.27294 | -7.3758 | -4.9019 | -0.3684 | 6.2074 | 0.2504 | -2.1458 | 61.7614 | 0.29442 | 61.7018 | -0.028522 | 0.043657 | 61.5295 | 0.007721 | 61.3031 | 61.659 | 54.0103 | 56.4842 | 61.0177 | 67.5935 | 61.6365 | 59.2403 | 123.1476 | 61.6805 | 123.088 | 61.3576 | 61.4298 | 122.9156 | 61.3938 | 122.6893 | 61.7178 | 61.7537 | 61.6582 | 61.6941
5339.0781 | 123.3765 | -61.4182 | 61.6562 | 0.55222 | -7.3071 | -4.8699 | -0.34551 | 6.8483 | 0.51595 | -2.0542 | 61.7523 | 0.28526 | 61.6881 | -0.03768 | 0.052814 | 61.5387 | 0.003143 | 61.3169 | 61.9704 | 54.111 | 56.5483 | 61.0726 | 68.2664 | 61.9341 | 59.3639 | 123.1704 | 61.7034 | 123.1063 | 61.3805 | 61.471 | 122.9568 | 61.4213 | 122.735 | 61.6995 | 61.7491 | 61.6353 | 61.685
5340.0625 | 123.4406 | -61.3632 | 61.7432 | 0.41945 | -7.3712 | -5.2453 | -0.34551 | 6.1524 | 0.39233 | -2.1046 | 61.7569 | 0.28984 | 61.6881 | -0.033101 | 0.043657 | 61.525 | 0.012299 | 61.3031 | 61.7827 | 53.992 | 56.1179 | 61.0177 | 67.5156 | 61.7556 | 59.2586 | 123.1201 | 61.6531 | 123.0513 | 61.3301 | 61.4069 | 122.8882 | 61.3755 | 122.6664 | 61.7132 | 61.7446 | 61.6445 | 61.6758
5341.0625 | 123.3215 | -61.4044 | 61.7386 | 0.26378 | -7.4628 | -5.4056 | -0.26768 | 5.9464 | 0.24583 | -2.2374 | 61.766 | 0.28069 | 61.6698 | -0.019364 | 0.052814 | 61.5158 | 0.007721 | 61.3123 | 61.6682 | 53.9416 | 55.9988 | 61.1367 | 67.3508 | 61.6502 | 59.1671 | 123.1704 | 61.6851 | 123.0742 | 61.3851 | 61.4572 | 122.9202 | 61.4121 | 122.7167 | 61.7132 | 61.7583 | 61.617 | 61.6621
5342.0938 | 123.436 | -61.3907 | 61.7294 | 0.15848 | -7.5315 | -5.2866 | -0.27226 | 5.9876 | 0.12679 | -2.2511 | 61.7614 | 0.28526 | 61.6652 | -0.023943 | 0.048236 | 61.5341 | 0.003143 | 61.2986 | 61.5492 | 53.8592 | 56.1041 | 61.1184 | 67.3783 | 61.5175 | 59.1396 | 123.1521 | 61.676 | 123.0559 | 61.3667 | 61.4389 | 122.9248 | 61.3938 | 122.6893 | 61.7132 | 61.7583 | 61.617 | 61.6621
5343.0625 | 123.3673 | -61.3678 | 61.7523 | 0.076067 | -7.4994 | -5.5796 | -0.29973 | 5.9418 | 0.048956 | -2.274 | 61.7752 | 0.28526 | 61.679 | -0.023943 | 0.048236 | 61.5204 | 0.007721 | 61.3123 | 61.4439 | 53.8684 | 55.7882 | 61.0681 | 67.3096 | 61.4168 | 59.0938 | 123.143 | 61.6531 | 123.0468 | 61.3439 | 61.416 | 122.8882 | 61.3755 | 122.6801 | 61.7269 | 61.7675 | 61.6307 | 61.6712
5344.0938 | 123.3673 | -61.4044 | 61.7386 | 0.016548 | -7.5544 | -5.2224 | -0.33178 | 5.8594 | -0.001406 | -2.361 | 61.7706 | 0.29442 | 61.6927 | -0.033101 | 0.048236 | 61.5158 | 0.007721 | 61.294 | 61.421 | 53.8501 | 56.182 | 61.0726 | 67.2638 | 61.403 | 59.0435 | 123.175 | 61.6988 | 123.0971 | 61.3713 | 61.4527 | 122.9202 | 61.4121 | 122.6984 | 61.7224 | 61.7629 | 61.6445 | 61.685
5345.0625 | 123.4039 | -61.3586 | 61.7249 | 0.085224 | -7.5086 | -5.1858 | -0.40503 | 6.0197 | 0.058113 | -2.3381 | 61.7706 | 0.28984 | 61.7018 | -0.019364 | 0.043657 | 61.5158 | 0.007721 | 61.3169 | 61.4439 | 53.8501 | 56.1728 | 60.9536 | 67.3783 | 61.4168 | 59.0206 | 123.1292 | 61.6485 | 123.0605 | 61.3393 | 61.4023 | 122.8744 | 61.3664 | 122.6755 | 61.7269 | 61.7629 | 61.6582 | 61.6941
5346.1094 | 123.349 | -61.3907 | 61.7065 | 0.10354 | -7.5589 | -5.2728 | -0.31804 | 6.1112 | 0.058113 | -2.3243 | 61.766 | 0.28526 | 61.6881 | -0.033101 | 0.039079 | 61.5204 | 0.007721 | 61.3077 | 61.4942 | 53.8317 | 56.1179 | 61.0726 | 67.5019 | 61.4488 | 59.0664 | 123.1567 | 61.676 | 123.0788 | 61.3576 | 61.4298 | 122.9111 | 61.3984 | 122.6984 | 61.7269 | 61.7583 | 61.649 | 61.6804
5347.0625 | 123.468 | -61.3815 | 61.6882 | 0.11727 | -7.5498 | -5.2728 | -0.16695 | 7.5991 | 0.09474 | -2.2465 | 61.7523 | 0.28526 | 61.6561 | -0.028522 | 0.052814 | 61.5341 | 0.007721 | 61.326 | 61.4988 | 53.8317 | 56.1087 | 61.2146 | 68.9806 | 61.4763 | 59.135 | 123.1338 | 61.6668 | 123.0376 | 61.353 | 61.4343 | 122.9156 | 61.3893 | 122.7076 | 61.6995 | 61.7446 | 61.6032 | 61.6483
5348.0938 | 123.3948 | -61.441 | 61.6699 | 0.11269 | -7.6963 | -5.3278 | -0.30888 | 7.8875 | 0.090161 | -2.2328 | 61.7523 | 0.28984 | 61.679 | -0.033101 | 0.052814 | 61.5387 | 0.007721 | 61.3306 | 61.5537 | 53.7447 | 56.1133 | 61.1322 | 69.3285 | 61.5312 | 59.2083 | 123.1933 | 61.7309 | 123.12 | 61.4079 | 61.4939 | 122.9797 | 61.4488 | 122.7717 | 61.6995 | 61.7446 | 61.6261 | 61.6712
5349.0625 | 123.3994 | -61.4182 | 61.702 | 0.19511 | -7.4811 | -5.2499 | -0.26768 | 8.1164 | 0.16799 | -2.1549 | 61.7477 | 0.28526 | 61.679 | -0.033101 | 0.052814 | 61.5341 | 0.012299 | 61.3398 | 61.6133 | 53.9371 | 56.1682 | 61.1505 | 69.5345 | 61.5861 | 59.2632 | 123.1659 | 61.7034 | 123.0971 | 61.3851 | 61.471 | 122.9523 | 61.4305 | 122.7579 | 61.6949 | 61.7354 | 61.6261 | 61.6667
5350.0938 | 123.3398 | -61.3998 | 61.6882 | 0.19053 | -7.6368 | -5.1629 | -0.27683 | 7.8325 | 0.16799 | -2.2602 | 61.7523 | 0.28526 | 61.679 | -0.023943 | 0.048236 | 61.5387 | 0.003143 | 61.3352 | 61.5904 | 53.7631 | 56.2369 | 61.123 | 69.2324 | 61.5678 | 59.1396 | 123.1521 | 61.6851 | 123.0788 | 61.3759 | 61.4481 | 122.9385 | 61.403 | 122.735 | 61.7041 | 61.7491 | 61.6307 | 61.6758
5351.0625 | 123.381 | -61.3678 | 61.734 | 0.016548 | -7.6917 | -5.1629 | -0.26768 | 7.5487 | -0.01972 | -2.2557 | 61.7523 | 0.28984 | 61.6698 | -0.028522 | 0.043657 | 61.5295 | 0.012299 | 61.3306 | 61.3843 | 53.6761 | 56.2049 | 61.1001 | 68.9165 | 61.3481 | 59.1121 | 123.1201 | 61.6576 | 123.0376 | 61.3393 | 61.4115 | 122.8973 | 61.3801 | 122.6984 | 61.7086 | 61.74 | 61.6261 | 61.6575
5352.0781 | 123.4039 | -61.409 | 61.702 | 0.080646 | -7.7055 | -5.1675 | -0.48287 | 5.8961 | 0.062691 | -2.3152 | 61.7752 | 0.28526 | 61.6881 | -0.03768 | 0.048236 | 61.5158 | 0.007721 | 61.2986 | 61.4896 | 53.7035 | 56.2415 | 60.9261 | 67.305 | 61.4717 | 59.0938 | 123.1842 | 61.6943 | 123.0971 | 61.3713 | 61.4572 | 122.9248 | 61.4167 | 122.7076 | 61.7269 | 61.7675 | 61.6399 | 61.6804
5353.0625 | 123.4497 | -61.3815 | 61.6974 | 0.16764 | -7.5818 | -5.1217 | -0.23563 | 8.1255 | 0.14052 | -2.2923 | 61.7569 | 0.28526 | 61.6927 | -0.033101 | 0.048236 | 61.5433 | 0.007721 | 61.3443 | 61.5492 | 53.7997 | 56.2598 | 61.1459 | 69.507 | 61.5221 | 59.0892 | 123.1384 | 61.6668 | 123.0742 | 61.3484 | 61.4298 | 122.9248 | 61.3893 | 122.7259 | 61.7086 | 61.7491 | 61.6445 | 61.685
5354.0938 | 123.3719 | -61.4273 | 61.6928 | 0.16306 | -7.6001 | -5.0988 | -0.30888 | 8.1942 | 0.12679 | -2.2374 | 61.7523 | 0.28984 | 61.6881 | -0.033101 | 0.043657 | 61.5387 | 0.007721 | 61.3489 | 61.5904 | 53.8272 | 56.3285 | 61.1184 | 69.6215 | 61.5541 | 59.19 | 123.1796 | 61.7171 | 123.1154 | 61.3942 | 61.471 | 122.966 | 61.435 | 122.7762 | 61.7086 | 61.7446 | 61.6445 | 61.6804
5355.0625 | 123.3627 | -61.4273 | 61.6974 | 0.24547 | -7.623 | -4.9889 | -0.27226 | 8.1896 | 0.2092 | -2.2786 | 61.7431 | 0.28526 | 61.6561 | -0.028522 | 0.048236 | 61.5387 | 0.003143 | 61.3352 | 61.6728 | 53.8043 | 56.4384 | 61.1551 | 69.6169 | 61.6365 | 59.1488 | 123.1704 | 61.7126 | 123.0834 | 61.3988 | 61.4755 | 122.966 | 61.4305 | 122.7625 | 61.6949 | 61.74 | 61.6078 | 61.6529
5356.1094 | 123.3856 | -61.4273 | 61.6562 | 0.36908 | -7.5498 | -4.8287 | -0.16695 | 8.3819 | 0.34197 | -2.3381 | 61.734 | 0.28526 | 61.6515 | -0.03768 | 0.048236 | 61.5433 | 0.007721 | 61.3306 | 61.7964 | 53.8775 | 56.5986 | 61.2604 | 69.8092 | 61.7693 | 59.0892 | 123.1613 | 61.7126 | 123.0788 | 61.3896 | 61.4755 | 122.9706 | 61.435 | 122.7579 | 61.6857 | 61.7263 | 61.6032 | 61.6438
5357.0625 | 123.3902 | -61.4182 | 61.7249 | 0.19053 | -7.8016 | -5.0485 | -0.34093 | 8.0843 | 0.15426 | -2.361 | 61.7523 | 0.29442 | 61.6927 | -0.028522 | 0.048236 | 61.5295 | 0.007721 | 61.3443 | 61.6087 | 53.6165 | 56.3697 | 61.0772 | 69.5025 | 61.5724 | 59.0572 | 123.1704 | 61.7126 | 123.1108 | 61.3896 | 61.4664 | 122.9477 | 61.4259 | 122.7625 | 61.7041 | 61.7446 | 61.6445 | 61.685
5358.0781 | 123.4085 | -61.4136 | 61.6608 | 0.076067 | -7.797 | -4.9798 | -0.20358 | 8.1301 | 0.035221 | -2.3289 | 61.7569 | 0.28984 | 61.6881 | -0.028522 | 0.039079 | 61.5387 | 0.012299 | 61.3398 | 61.4896 | 53.6165 | 56.4338 | 61.21 | 69.5437 | 61.4488 | 59.0847 | 123.1704 | 61.7034 | 123.1017 | 61.3851 | 61.4527 | 122.9523 | 61.4259 | 122.7533 | 61.7178 | 61.7446 | 61.649 | 61.6758
5359.0625 | 123.4177 | -61.3953 | 61.7065 | -0.029236 | -7.7284 | -5.0073 | -0.22647 | 7.979 | -0.060926 | -2.3518 | 61.7523 | 0.28984 | 61.6652 | -0.028522 | 0.039079 | 61.525 | 0.012299 | 61.3398 | 61.366 | 53.6669 | 56.388 | 61.1688 | 69.3743 | 61.3343 | 59.0435 | 123.1476 | 61.6851 | 123.0605 | 61.3667 | 61.4343 | 122.9202 | 61.4076 | 122.735 | 61.7132 | 61.74 | 61.6261 | 61.6529
5360.0938 | 123.4085 | -61.4182 | 61.702 | 0.062332 | -7.6688 | -4.8241 | -0.20358 | 7.4938 | 0.035221 | -2.3976 | 61.7477 | 0.28526 | 61.6652 | -0.03768 | 0.048236 | 61.5341 | 0.012299 | 61.3306 | 61.4805 | 53.7493 | 56.594 | 61.2146 | 68.9119 | 61.4534 | 59.0206 | 123.1659 | 61.7034 | 123.0834 | 61.3805 | 61.4664 | 122.9523 | 61.4305 | 122.7488 | 61.6995 | 61.7354 | 61.617 | 61.6529
5361.0625 | 123.2712 | -61.4044 | 61.7615 | 0.11269 | -7.6322 | -4.8378 | -0.51034 | 6.2119 | 0.085583 | -2.4342 | 61.7706 | 0.28526 | 61.7018 | -0.028522 | 0.057392 | 61.5204 | 0.007721 | 61.3169 | 61.5171 | 53.7722 | 56.5666 | 60.8941 | 67.6163 | 61.49 | 58.9702 | 123.175 | 61.6897 | 123.1063 | 61.3759 | 61.4618 | 122.9248 | 61.4121 | 122.7213 | 61.7132 | 61.7629 | 61.6445 | 61.6941
5362.0781 | 123.3627 | -61.4227 | 61.6974 | 0.27752 | -7.3071 | -4.6822 | -0.43708 | 6.3447 | 0.26414 | -2.4571 | 61.7569 | 0.28984 | 61.7018 | -0.03768 | 0.043657 | 61.5341 | 0.007721 | 61.3306 | 61.7002 | 54.1156 | 56.7406 | 60.9856 | 67.7674 | 61.6869 | 58.9656 | 123.1796 | 61.7126 | 123.1246 | 61.385 | 61.4664 | 122.9568 | 61.4304 | 122.7533 | 61.7132 | 61.7491 | 61.6582 | 61.6941
5363.0625 | 123.4406 | -61.3815 | 61.7111 | 0.23631 | -7.2567 | -4.7188 | -0.40045 | 6.4637 | 0.22293 | -2.4891 | 61.7523 | 0.29442 | 61.679 | -0.028522 | 0.048236 | 61.525 | 0.007721 | 61.326 | 61.6178 | 54.1248 | 56.6627 | 60.9811 | 67.8453 | 61.6045 | 58.8924 | 123.1338 | 61.676 | 123.0605 | 61.353 | 61.4298 | 122.9065 | 61.3893 | 122.7076 | 61.7041 | 61.7446 | 61.6307 | 61.6712
5364.0781 | 123.3948 | -61.409 | 61.6837 | 0.218 | -7.2384 | -4.7325 | -0.35009 | 6.1524 | 0.19089 | -2.3747 | 61.7523 | 0.28526 | 61.6561 | -0.03768 | 0.039079 | 61.525 | 0.007721 | 61.3123 | 61.627 | 54.1706 | 56.6765 | 61.0589 | 67.5614 | 61.5999 | 59.0343 | 123.1613 | 61.6943 | 123.0651 | 61.3713 | 61.4481 | 122.934 | 61.4167 | 122.7213 | 61.7132 | 61.7446 | 61.617 | 61.6483
5365.0625 | 123.3536 | -61.4182 | 61.7294 | 0.11727 | -7.2888 | -4.6501 | -0.1349 | 6.189 | 0.085583 | -2.361 | 61.7569 | 0.28526 | 61.6835 | -0.033101 | 0.057392 | 61.5295 | 0.003143 | 61.3215 | 61.5354 | 54.1294 | 56.768 | 61.2833 | 67.6072 | 61.5037 | 59.0572 | 123.175 | 61.7034 | 123.1017 | 61.3851 | 61.4755 | 122.9477 | 61.4213 | 122.7396 | 61.6995 | 61.7537 | 61.6261 | 61.6804
5366.0625 | 123.317 | -61.4365 | 61.7661 | 0.034862 | -7.4353 | -4.7509 | -0.16237 | 6.4729 | 0.016907 | -2.4663 | 61.7614 | 0.28984 | 61.7064 | -0.023943 | 0.052814 | 61.525 | 0.012299 | 61.3169 | 61.4713 | 54.0012 | 56.6856 | 61.2741 | 67.9093 | 61.4534 | 58.9702 | 123.1979 | 61.7263 | 123.1429 | 61.4125 | 61.4893 | 122.9614 | 61.4488 | 122.7533 | 61.7086 | 61.7491 | 61.6536 | 61.6941
5367.0938 | 123.3994 | -61.4136 | 61.7065 | 0.098959 | -7.4307 | -4.673 | -0.079959 | 6.2211 | 0.058113 | -2.5166 | 61.7523 | 0.28984 | 61.6927 | -0.033101 | 0.052814 | 61.525 | 0.007721 | 61.3169 | 61.5125 | 53.9828 | 56.7406 | 61.3336 | 67.6347 | 61.4717 | 58.897 | 123.1659 | 61.7034 | 123.1063 | 61.3805 | 61.4664 | 122.9385 | 61.4213 | 122.7305 | 61.6995 | 61.7446 | 61.6399 | 61.685
5368.0625 | 123.436 | -61.377 | 61.6974 | 0.048597 | -7.4719 | -4.815 | 0.007033 | 7.6174 | 0.012329 | -2.5075 | 61.7569 | 0.28069 | 61.6606 | -0.023943 | 0.048236 | 61.5295 | 0.007721 | 61.3352 | 61.4256 | 53.905 | 56.562 | 61.384 | 68.9943 | 61.3893 | 58.8695 | 123.1338 | 61.6576 | 123.0376 | 61.353 | 61.4252 | 122.9065 | 61.3847 | 122.7121 | 61.7086 | 61.7491 | 61.6124 | 61.6529
5369.0938 | 123.3994 | -61.4044 | 61.6882 | 0.18137 | -7.1881 | -4.6364 | 0.20391 | 7.654 | 0.14968 | -2.4067 | 61.7431 | 0.28526 | 61.6515 | -0.019364 | 0.048236 | 61.5433 | 0.016878 | 61.3306 | 61.5858 | 54.2164 | 56.768 | 61.6083 | 69.0584 | 61.5541 | 58.9977 | 123.1476 | 61.6897 | 123.0559 | 61.3851 | 61.4527 | 122.9477 | 61.4213 | 122.735 | 61.6949 | 61.7263 | 61.6032 | 61.6346
5370.0625 | 123.3902 | -61.4182 | 61.6974 | 0.28667 | -6.3089 | -4.467 | 0.19475 | 7.9424 | 0.25498 | -2.3152 | 61.734 | 0.28069 | 61.6698 | -0.023943 | 0.048236 | 61.5616 | 0.007721 | 61.3489 | 61.7048 | 55.1092 | 56.9512 | 61.6129 | 69.3606 | 61.6731 | 59.103 | 123.1521 | 61.6988 | 123.088 | 61.3942 | 61.4664 | 122.9797 | 61.4259 | 122.7671 | 61.6857 | 61.7263 | 61.6216 | 61.6621
5371.0625 | 123.4222 | -61.4136 | 61.6974 | 0.26836 | -6.3181 | -4.4899 | 0.11692 | 7.9058 | 0.22293 | -2.3518 | 61.734 | 0.28984 | 61.6652 | -0.033101 | 0.048236 | 61.557 | 0.003143 | 61.3489 | 61.6819 | 55.0955 | 56.9237 | 61.5305 | 69.3194 | 61.6365 | 59.0618 | 123.1475 | 61.7034 | 123.0788 | 61.3805 | 61.4618 | 122.9706 | 61.4167 | 122.7625 | 61.6857 | 61.7308 | 61.617 | 61.6621
5372.0781 | 123.381 | -61.3998 | 61.6562 | 0.24547 | -6.9545 | -4.5357 | 0.007033 | 7.8737 | 0.20462 | -2.4571 | 61.7386 | 0.28526 | 61.6469 | -0.033101 | 0.048236 | 61.5524 | 0.007721 | 61.326 | 61.6453 | 54.4453 | 56.8642 | 61.4069 | 69.2736 | 61.6045 | 58.9427 | 123.1384 | 61.6851 | 123.0467 | 61.3667 | 61.4481 | 122.9523 | 61.4076 | 122.7259 | 61.6903 | 61.7308 | 61.5987 | 61.6392
5373.0625 | 123.381 | -61.3998 | 61.6837 | 0.23173 | -7.1789 | -4.6776 | -0.19442 | 7.9561 | 0.19089 | -2.4617 | 61.7386 | 0.28526 | 61.6515 | -0.019364 | 0.048236 | 61.5433 | 0.012299 | 61.3352 | 61.6316 | 54.2209 | 56.7222 | 61.2054 | 69.356 | 61.5907 | 58.9382 | 123.1384 | 61.6851 | 123.0513 | 61.3805 | 61.4481 | 122.9431 | 61.4121 | 122.735 | 61.6903 | 61.7263 | 61.6032 | 61.6392
5374.0781 | 123.381 | -61.4365 | 61.6516 | 0.27294 | -7.2751 | -4.5677 | -0.19442 | 8.1026 | 0.23209 | -2.5029 | 61.7386 | 0.28069 | 61.6469 | -0.033101 | 0.048236 | 61.5433 | 0.012299 | 61.3306 | 61.7094 | 54.1614 | 56.8688 | 61.242 | 69.5391 | 61.6686 | 58.9336 | 123.175 | 61.7171 | 123.0834 | 61.4034 | 61.4847 | 122.9797 | 61.4488 | 122.7671 | 61.6903 | 61.7263 | 61.5987 | 61.6346
5375.0625 | 123.317 | -61.4136 | 61.7157 | 0.28667 | -7.4674 | -4.6684 | -0.15321 | 8.1576 | 0.2504 | -2.5624 | 61.7386 | 0.29442 | 61.6561 | -0.033101 | 0.048236 | 61.5433 | 0.007721 | 61.3443 | 61.7002 | 53.9462 | 56.7451 | 61.2604 | 69.5711 | 61.664 | 58.8512 | 123.1521 | 61.708 | 123.0696 | 61.3805 | 61.4618 | 122.9568 | 61.4213 | 122.7579 | 61.6903 | 61.7308 | 61.6078 | 61.6483
5376.0938 | 123.3948 | -61.3998 | 61.6608 | 0.19968 | -7.5452 | -4.7142 | 0.011611 | 8.2354 | 0.17715 | -2.5624 | 61.7386 | 0.28984 | 61.6835 | -0.033101 | 0.048236 | 61.5433 | 0.007721 | 61.326 | 61.5995 | 53.8546 | 56.6856 | 61.4115 | 69.6352 | 61.577 | 58.8374 | 123.1384 | 61.6897 | 123.0834 | 61.3667 | 61.4481 | 122.9431 | 61.4076 | 122.7259 | 61.6903 | 61.7308 | 61.6353 | 61.6758
5377.0625 | 123.2758 | -61.4273 | 61.7203 | 0.18137 | -7.3163 | -4.6776 | -0.006703 | 8.2079 | 0.15884 | -2.4617 | 61.7477 | 0.28984 | 61.6744 | -0.03768 | 0.043657 | 61.5478 | 0.007721 | 61.3398 | 61.6087 | 54.111 | 56.7497 | 61.4206 | 69.6352 | 61.5861 | 58.9656 | 123.175 | 61.7171 | 123.1017 | 61.3896 | 61.471 | 122.9752 | 61.435 | 122.7671 | 61.7041 | 61.74 | 61.6307 | 61.6667
5378.0938 | 123.3582 | -61.4456 | 61.7111 | 0.16764 | -7.3392 | -4.7234 | -0.070802 | 8.2537 | 0.13595 | -2.4159 | 61.7431 | 0.28526 | 61.6606 | -0.028522 | 0.048236 | 61.5524 | 0.012299 | 61.3398 | 61.6133 | 54.1065 | 56.7222 | 61.3748 | 69.6993 | 61.5816 | 59.0297 | 123.1887 | 61.7309 | 123.1063 | 61.4171 | 61.4939 | 122.998 | 61.4579 | 122.7854 | 61.6949 | 61.7308 | 61.6124 | 61.6483
5379.0625 | 123.381 | -61.409 | 61.7111 | 0.22258 | -7.362 | -4.5952 | 0.061975 | 8.2766 | 0.20462 | -2.3518 | 61.7431 | 0.28069 | 61.6515 | -0.028522 | 0.048236 | 61.5478 | 0.012299 | 61.3489 | 61.6316 | 54.0469 | 56.8138 | 61.471 | 69.6856 | 61.6136 | 59.0572 | 123.1521 | 61.6897 | 123.0605 | 61.3805 | 61.4572 | 122.9568 | 61.4213 | 122.7579 | 61.6949 | 61.7308 | 61.6032 | 61.6392
5380.0781 | 123.3536 | -61.4319 | 61.6974 | 0.26378 | -7.4033 | -4.6364 | 0.007033 | 8.2262 | 0.22751 | -2.3289 | 61.7431 | 0.28984 | 61.6515 | -0.028522 | 0.048236 | 61.5478 | 0.012299 | 61.3398 | 61.6957 | 54.0286 | 56.7955 | 61.4389 | 69.6581 | 61.6594 | 59.103 | 123.175 | 61.7217 | 123.0834 | 61.4034 | 61.4801 | 122.9797 | 61.4442 | 122.7717 | 61.6949 | 61.7308 | 61.6032 | 61.6392
5381.0625 | 123.2483 | -61.4227 | 61.7111 | 0.26836 | -7.4353 | -4.7051 | -0.10285 | 8.1896 | 0.23209 | -2.3793 | 61.7386 | 0.28984 | 61.679 | -0.023943 | 0.043657 | 61.5387 | 0.012299 | 61.3215 | 61.6911 | 53.9874 | 56.7177 | 61.3199 | 69.6123 | 61.6548 | 59.0435 | 123.1613 | 61.7126 | 123.1017 | 61.3988 | 61.4664 | 122.9614 | 61.435 | 122.7442 | 61.6949 | 61.7263 | 61.6353 | 61.6667
5382.0781 | 123.3902 | -61.441 | 61.6699 | 0.24089 | -7.4674 | -4.7692 | -0.084537 | 8.0202 | 0.21378 | -2.4434 | 61.7431 | 0.28984 | 61.6927 | -0.03768 | 0.048236 | 61.5433 | 0.012299 | 61.3306 | 61.6819 | 53.9737 | 56.6719 | 61.3565 | 69.4613 | 61.6548 | 58.9977 | 123.1842 | 61.7309 | 123.1337 | 61.4034 | 61.4893 | 122.9843 | 61.4533 | 122.7717 | 61.6949 | 61.7308 | 61.6445 | 61.6804
5383.0625 | 123.4222 | -61.4044 | 61.702 | 0.25462 | -7.1972 | -4.412 | 0.039082 | 8.0797 | 0.46559 | -2.3564 | 61.7386 | 0.28984 | 61.679 | -0.028522 | 0.048236 | 61.5524 | 0.012299 | 61.3443 | 61.659 | 54.2072 | 56.9924 | 61.4435 | 69.4842 | 61.87 | 59.048 | 123.143 | 61.6943 | 123.0834 | 61.3759 | 61.4527 | 122.9568 | 61.4167 | 122.7488 | 61.6903 | 61.7263 | 61.6307 | 61.6667
5384.0938 | 123.4909 | -61.4502 | 61.6791 | 0.26378 | -7.3483 | -4.586 | -0.18984 | 7.979 | 0.24125 | -2.4479 | 61.7386 | 0.28069 | 61.6744 | -0.028522 | 0.048236 | 61.5478 | 0.003143 | 61.3352 | 61.714 | 54.1019 | 56.8642 | 61.2604 | 69.4292 | 61.6914 | 59.0022 | 123.1887 | 61.7309 | 123.1246 | 61.4217 | 61.4984 | 122.998 | 61.4533 | 122.7854 | 61.6903 | 61.7354 | 61.6261 | 61.6712
5385.0625 | 123.3124 | -61.4273 | 61.7249 | 0.31872 | -7.3117 | -4.5357 | -0.199 | 7.6494 | 0.29161 | -2.4571 | 61.7386 | 0.28984 | 61.6561 | -0.033101 | 0.06197 | 61.5433 | 0.007721 | 61.3398 | 61.746 | 54.1156 | 56.8916 | 61.2283 | 69.0767 | 61.7189 | 58.9702 | 123.1659 | 61.7171 | 123.0834 | 61.3942 | 61.4893 | 122.9706 | 61.435 | 122.7671 | 61.6766 | 61.7308 | 61.5941 | 61.6483
5386.1094 | 123.3353 | -61.4319 | 61.6699 | 0.1539 | -7.4994 | -4.7554 | -0.32262 | 7.5991 | 0.12221 | -2.5349 | 61.7477 | 0.28526 | 61.6515 | -0.028522 | 0.048236 | 61.5341 | 0.007721 | 61.326 | 61.5858 | 53.9325 | 56.6765 | 61.1093 | 69.0309 | 61.5541 | 58.897 | 123.1796 | 61.7171 | 123.0834 | 61.4034 | 61.4801 | 122.966 | 61.4396 | 122.7579 | 61.6995 | 61.74 | 61.6032 | 61.6438
5387.0625 | 123.3444 | -61.4227 | 61.7157 | 0.2592 | -7.4307 | -4.641 | -0.18069 | 7.8737 | 0.22751 | -2.4708 | 61.7431 | 0.28526 | 61.6469 | -0.033101 | 0.052814 | 61.5524 | 0.016878 | 61.3306 | 61.6819 | 53.992 | 56.7818 | 61.242 | 69.2965 | 61.6502 | 58.9519 | 123.1659 | 61.708 | 123.0696 | 61.3896 | 61.4755 | 122.9752 | 61.4396 | 122.7533 | 61.6903 | 61.7263 | 61.5941 | 61.63
5388.0781 | 123.349 | -61.4365 | 61.6837 | 0.24089 | -7.4628 | -4.6822 | -0.093694 | 8.1576 | 0.21378 | -2.4479 | 61.734 | 0.28069 | 61.6469 | -0.033101 | 0.048236 | 61.5433 | 0.007721 | 61.3215 | 61.6774 | 53.9737 | 56.7543 | 61.3428 | 69.594 | 61.6502 | 58.9885 | 123.1704 | 61.7171 | 123.0834 | 61.4034 | 61.4847 | 122.9797 | 61.4442 | 122.7579 | 61.6857 | 61.7263 | 61.5987 | 61.6392
5389.0625 | 123.4634 | -61.3632 | 61.7111 | 0.14932 | -7.5635 | -4.7463 | -0.11659 | 7.7867 | 0.13137 | -2.4479 | 61.7523 | 0.28984 | 61.6835 | -0.028522 | 0.048236 | 61.5433 | 0.007721 | 61.3215 | 61.5125 | 53.7997 | 56.6169 | 61.2466 | 69.15 | 61.4946 | 58.9153 | 123.1155 | 61.6531 | 123.0468 | 61.3347 | 61.4115 | 122.9065 | 61.3709 | 122.6847 | 61.7041 | 61.7446 | 61.6353 | 61.6758
5390.0781 | 123.3719 | -61.4319 | 61.6928 | 0.19053 | -7.4353 | -4.7692 | -0.025017 | 7.947 | 0.19089 | -2.4251 | 61.7477 | 0.28984 | 61.679 | -0.03768 | 0.048236 | 61.5387 | 0.003143 | 61.326 | 61.6224 | 53.9966 | 56.6627 | 61.4069 | 69.3789 | 61.6228 | 59.0068 | 123.1796 | 61.7217 | 123.1108 | 61.3942 | 61.4801 | 122.9706 | 61.435 | 122.7579 | 61.6995 | 61.7446 | 61.6307 | 61.6758
5391.0625 | 123.3261 | -61.409 | 61.7249 | 0.076067 | -7.4033 | -4.7234 | -0.16237 | 7.7959 | 0.071848 | -2.5029 | 61.7431 | 0.29442 | 61.6561 | -0.028522 | 0.048236 | 61.5387 | 0.003143 | 61.3306 | 61.4851 | 54.0057 | 56.6856 | 61.2466 | 69.2049 | 61.4808 | 58.9061 | 123.1521 | 61.7034 | 123.0651 | 61.3805 | 61.4572 | 122.9477 | 61.4121 | 122.7396 | 61.6949 | 61.74 | 61.6078 | 61.6529
5392.0938 | 123.4222 | -61.3998 | 61.7065 | 0.080646 | -7.5452 | -4.7737 | -0.17153 | 7.6952 | 0.039799 | -2.5166 | 61.7477 | 0.27611 | 61.6561 | -0.033101 | 0.052814 | 61.5341 | 0.012299 | 61.326 | 61.4805 | 53.8546 | 56.6261 | 61.2283 | 69.095 | 61.4396 | 58.8832 | 123.1476 | 61.6759 | 123.0559 | 61.3667 | 61.4527 | 122.934 | 61.4121 | 122.7259 | 61.6949 | 61.7354 | 61.6032 | 61.6438
5393.0625 | 123.3353 | -61.4502 | 61.7432 | 0.12643 | -7.4582 | -4.8241 | -0.098273 | 7.7547 | 0.090161 | -2.5258 | 61.7569 | 0.28984 | 61.6881 | -0.028522 | 0.043657 | 61.5387 | 0.007721 | 61.326 | 61.5766 | 53.992 | 56.6261 | 61.3519 | 69.2049 | 61.5404 | 58.9244 | 123.2071 | 61.74 | 123.1383 | 61.4217 | 61.4939 | 122.9889 | 61.4579 | 122.7762 | 61.7132 | 61.7491 | 61.6445 | 61.6804
5394.0781 | 123.4222 | -61.3815 | 61.6562 | 0.057754 | -7.5498 | -4.9477 | -0.13032 | 7.7089 | 0.030642 | -2.5075 | 61.7523 | 0.28984 | 61.6927 | -0.033101 | 0.034501 | 61.5387 | 0.003143 | 61.3077 | 61.4393 | 53.8317 | 56.4338 | 61.2512 | 69.0905 | 61.4122 | 58.8741 | 123.1338 | 61.6714 | 123.0742 | 61.3484 | 61.416 | 122.9202 | 61.3847 | 122.6893 | 61.7178 | 61.7491 | 61.6582 | 61.6895
5395.0625 | 123.3948 | -61.3678 | 61.734 | 0.044018 | -7.6597 | -4.9981 | -0.089116 | 7.7272 | 0.012329 | -2.48 | 61.7431 | 0.28526 | 61.6606 | -0.033101 | 0.043657 | 61.5387 | 0.012299 | 61.3215 | 61.4118 | 53.7081 | 56.3697 | 61.2787 | 69.095 | 61.3801 | 58.8878 | 123.1109 | 61.6531 | 123.0284 | 61.3347 | 61.4115 | 122.9065 | 61.3801 | 122.6893 | 61.6995 | 61.7308 | 61.617 | 61.6483
5396.1094 | 123.3627 | -61.3815 | 61.7432 | 0.03944 | -7.6597 | -4.9294 | -0.14864 | 7.6631 | 0.003172 | -2.5029 | 61.7477 | 0.28526 | 61.6606 | -0.033101 | 0.043657 | 61.5387 | 0.007721 | 61.3169 | 61.421 | 53.7219 | 56.4521 | 61.2329 | 69.0447 | 61.3847 | 58.8786 | 123.1292 | 61.6668 | 123.0422 | 61.3484 | 61.4252 | 122.9202 | 61.3893 | 122.6984 | 61.7041 | 61.74 | 61.617 | 61.6529
5397.0625 | 123.4406 | -61.3815 | 61.7111 | 0.025705 | -7.6001 | -4.8378 | -0.061645 | 7.9195 | -0.010563 | -2.4296 | 61.7569 | 0.27611 | 61.6881 | -0.023943 | 0.048236 | 61.5433 | 0.016878 | 61.326 | 61.4072 | 53.7814 | 56.5437 | 61.3199 | 69.301 | 61.371 | 58.9519 | 123.1384 | 61.6576 | 123.0696 | 61.3576 | 61.4298 | 122.9248 | 61.3984 | 122.7076 | 61.7086 | 61.74 | 61.6399 | 61.6712
5398.0938 | 123.3948 | -61.4182 | 61.6928 | 0.11269 | -7.536 | -4.8333 | -0.029595 | 7.8096 | 0.076426 | -2.3243 | 61.7523 | 0.28526 | 61.6835 | -0.033101 | 0.048236 | 61.5433 | 0.007721 | 61.3123 | 61.5308 | 53.8821 | 56.5849 | 61.3886 | 69.2278 | 61.4946 | 59.0938 | 123.1704 | 61.7034 | 123.1017 | 61.3851 | 61.4664 | 122.9614 | 61.4259 | 122.7305 | 61.7041 | 61.7446 | 61.6353 | 61.6758
5399.0625 | 123.3994 | -61.3998 | 61.7249 | 0.19053 | -7.4124 | -4.7646 | 0.034504 | 7.5853 | 0.15884 | -2.4571 | 61.7431 | 0.28984 | 61.6561 | -0.028522 | 0.048236 | 61.5433 | 0.003143 | 61.3215 | 61.5904 | 53.9874 | 56.6353 | 61.4343 | 68.9852 | 61.5587 | 58.9427 | 123.143 | 61.6897 | 123.0559 | 61.3713 | 61.4481 | 122.9431 | 61.403 | 122.7213 | 61.6949 | 61.74 | 61.6078 | 61.6529
5400.0781 | 123.3627 | -61.4456 | 61.6653 | 0.26378 | -7.0415 | -4.5448 | 0.12607 | 7.7501 | 0.23209 | -2.3243 | 61.7386 | 0.28069 | 61.6423 | -0.033101 | 0.039079 | 61.557 | 0.003143 | 61.3306 | 61.7094 | 54.4041 | 56.9008 | 61.5717 | 69.1957 | 61.6777 | 59.1213 | 123.1842 | 61.7263 | 123.0879 | 61.4125 | 61.4847 | 123.0026 | 61.4488 | 122.7762 | 61.6995 | 61.7354 | 61.6032 | 61.6392
5401.0625 | 123.2529 | -61.441 | 61.7111 | 0.26378 | -6.9179 | -4.5128 | 0.048239 | 7.8646 | 0.22293 | -2.3014 | 61.7386 | 0.28526 | 61.6698 | -0.028522 | 0.052814 | 61.557 | 0.003143 | 61.3352 | 61.7048 | 54.5231 | 56.9283 | 61.4893 | 69.3056 | 61.664 | 59.1396 | 123.1796 | 61.7263 | 123.1108 | 61.4125 | 61.4939 | 122.998 | 61.4442 | 122.7762 | 61.6857 | 61.7354 | 61.617 | 61.6667
5402.0938 | 123.381 | -61.4273 | 61.6699 | 0.218 | -7.1148 | -4.5219 | 0.020768 | 8.0568 | 0.18173 | -2.2282 | 61.7477 | 0.28984 | 61.679 | -0.028522 | 0.043657 | 61.5478 | 0.007721 | 61.326 | 61.6453 | 54.3125 | 56.9054 | 61.4481 | 69.4842 | 61.609 | 59.1991 | 123.175 | 61.7171 | 123.1063 | 61.3988 | 61.471 | 122.9752 | 61.435 | 122.7533 | 61.7041 | 61.74 | 61.6353 | 61.6712
5403.0625 | 123.436 | -61.4136 | 61.6699 | 0.20426 | -7.2247 | -4.5128 | -0.038752 | 8.1118 | 0.16799 | -2.2465 | 61.7386 | 0.28526 | 61.6515 | -0.028522 | 0.043657 | 61.5478 | 0.007721 | 61.3306 | 61.6178 | 54.1889 | 56.9008 | 61.3748 | 69.5254 | 61.5816 | 59.1671 | 123.1521 | 61.6988 | 123.0651 | 61.3851 | 61.4572 | 122.9614 | 61.4213 | 122.7442 | 61.6949 | 61.7308 | 61.6078 | 61.6438
5404.0938 | 123.3948 | -61.3998 | 61.6882 | 0.21342 | -6.9912 | -4.4395 | 0.020768 | 8.0935 | 0.18631 | -2.3976 | 61.7294 | 0.28984 | 61.6423 | -0.028522 | 0.048236 | 61.5524 | 0.003143 | 61.3352 | 61.6133 | 54.4087 | 56.9603 | 61.4206 | 69.4933 | 61.5861 | 59.0023 | 123.1292 | 61.6897 | 123.0422 | 61.3713 | 61.4481 | 122.9523 | 61.403 | 122.735 | 61.6812 | 61.7263 | 61.5941 | 61.6392
5405.0625 | 123.4039 | -61.3953 | 61.7157 | 0.18595 | -6.95 | -4.4441 | -0.12574 | 7.9332 | 0.14968 | -2.4754 | 61.7386 | 0.28526 | 61.6652 | -0.033101 | 0.039079 | 61.5433 | 0.012299 | 61.3398 | 61.5812 | 54.4453 | 56.9512 | 61.2695 | 69.3285 | 61.5449 | 58.9198 | 123.1338 | 61.6805 | 123.0605 | 61.3622 | 61.4343 | 122.9385 | 61.4076 | 122.735 | 61.6995 | 61.7263 | 61.6261 | 61.6529
5406.1094 | 123.3902 | -61.441 | 61.702 | 0.19511 | -6.8767 | -4.3983 | -0.13948 | 7.947 | 0.16342 | -2.4113 | 61.7477 | 0.27611 | 61.679 | -0.028522 | 0.048236 | 61.5478 | 0.012299 | 61.326 | 61.6361 | 54.5643 | 57.0427 | 61.3016 | 69.388 | 61.6045 | 59.0297 | 123.1888 | 61.7171 | 123.12 | 61.4125 | 61.4893 | 122.9889 | 61.4533 | 122.7671 | 61.6995 | 61.7354 | 61.6307 | 61.6667
5407.0625 | 123.3856 | -61.4182 | 61.7157 | 0.20884 | -7.0736 | -4.4212 | -0.13948 | 8.1072 | 0.16342 | -2.4617 | 61.7386 | 0.28526 | 61.6652 | -0.033101 | 0.043657 | 61.5524 | 0.012299 | 61.3352 | 61.627 | 54.3446 | 56.997 | 61.2787 | 69.5254 | 61.5816 | 58.9565 | 123.1567 | 61.7034 | 123.0834 | 61.3851 | 61.4618 | 122.9706 | 61.4305 | 122.7533 | 61.6949 | 61.7263 | 61.6216 | 61.6529
5408.0938 | 123.3627 | -61.4319 | 61.6791 | 0.13559 | -7.1881 | -4.4761 | -0.070802 | 8.1347 | 0.1039 | -2.4022 | 61.7386 | 0.28526 | 61.6423 | -0.03768 | 0.048236 | 61.5433 | 0.007721 | 61.3352 | 61.5675 | 54.2438 | 56.9557 | 61.3611 | 69.5666 | 61.5358 | 59.0297 | 123.1704 | 61.7171 | 123.0742 | 61.3942 | 61.4801 | 122.9752 | 61.4396 | 122.7671 | 61.6903 | 61.7308 | 61.5941 | 61.6346
5409.0625 | 123.4177 | -61.4227 | 61.6882 | 0.14017 | -7.2247 | -4.4212 | 0.007033 | 8.2354 | 0.09474 | -2.3839 | 61.7386 | 0.28526 | 61.6423 | -0.028522 | 0.048236 | 61.5524 | 0.007721 | 61.3352 | 61.5629 | 54.198 | 57.0015 | 61.4298 | 69.6581 | 61.5175 | 59.0389 | 123.1613 | 61.708 | 123.0651 | 61.3942 | 61.471 | 122.9752 | 61.4304 | 122.7579 | 61.6903 | 61.7308 | 61.5941 | 61.6346
5410.0938 | 123.3994 | -61.4227 | 61.6837 | 0.15848 | -7.3437 | -4.3663 | -0.006703 | 8.3361 | 0.11305 | -2.3747 | 61.7386 | 0.28069 | 61.6377 | -0.023943 | 0.043657 | 61.5478 | 0.003143 | 61.326 | 61.5812 | 54.079 | 57.0565 | 61.416 | 69.7588 | 61.5358 | 59.048 | 123.1613 | 61.7034 | 123.0605 | 61.3988 | 61.4664 | 122.9706 | 61.4259 | 122.7488 | 61.6949 | 61.7354 | 61.5941 | 61.6346
5411.0625 | 123.3124 | -61.4273 | 61.7249 | 0.17679 | -7.362 | -4.3525 | -0.01586 | 8.2217 | 0.14052 | -2.3243 | 61.7477 | 0.28984 | 61.6744 | -0.028522 | 0.039079 | 61.5524 | 0.016878 | 61.3352 | 61.6041 | 54.0653 | 57.0748 | 61.4114 | 69.649 | 61.5678 | 59.103 | 123.175 | 61.7171 | 123.1017 | 61.3988 | 61.4664 | 122.9797 | 61.4442 | 122.7625 | 61.7086 | 61.7308 | 61.6353 | 61.6575
5412.0938 | 123.381 | -61.4227 | 61.6974 | 0.10812 | -7.4674 | -4.5448 | 0.01619 | 8.3224 | 0.071848 | -2.3976 | 61.7431 | 0.28984 | 61.6835 | -0.03768 | 0.043657 | 61.5433 | 0.003143 | 61.3352 | 61.5308 | 53.9554 | 56.8779 | 61.4389 | 69.7451 | 61.4946 | 59.0251 | 123.1659 | 61.7126 | 123.1063 | 61.385 | 61.4664 | 122.966 | 61.4259 | 122.7579 | 61.6995 | 61.74 | 61.6399 | 61.6804
5413.0625 | 123.3994 | -61.4136 | 61.6928 | 0.17221 | -7.0644 | -4.5128 | 0.094024 | 8.4048 | 0.13137 | -2.361 | 61.7386 | 0.28526 | 61.6744 | -0.028522 | 0.048236 | 61.5616 | 0.003143 | 61.3489 | 61.5858 | 54.3491 | 56.9008 | 61.5076 | 69.8183 | 61.5449 | 59.0526 | 123.1521 | 61.6988 | 123.088 | 61.3851 | 61.4618 | 122.9752 | 61.4167 | 122.7625 | 61.6903 | 61.7354 | 61.6261 | 61.6712
5414.0938 | 123.3719 | -61.441 | 61.6974 | 0.19968 | -6.9042 | -4.3846 | 0.15812 | 8.3636 | 0.16342 | -2.4571 | 61.7386 | 0.28984 | 61.6744 | -0.033101 | 0.048236 | 61.5524 | 0.007721 | 61.3489 | 61.6407 | 54.5369 | 57.0565 | 61.5992 | 69.8046 | 61.6045 | 58.9839 | 123.1796 | 61.7309 | 123.1154 | 61.4079 | 61.4893 | 122.9935 | 61.4488 | 122.79 | 61.6903 | 61.7308 | 61.6261 | 61.6667
5415.0625 | 123.3719 | -61.4182 | 61.6837 | 0.19511 | -6.9362 | -4.4304 | 0.039082 | 8.3544 | 0.15426 | -2.4205 | 61.7294 | 0.28984 | 61.6515 | -0.033101 | 0.043657 | 61.5524 | 0.016878 | 61.3535 | 61.6133 | 54.4819 | 56.9878 | 61.4572 | 69.7726 | 61.5724 | 58.9977 | 123.1475 | 61.708 | 123.0696 | 61.3851 | 61.4618 | 122.9706 | 61.435 | 122.7717 | 61.6857 | 61.7125 | 61.6078 | 61.6346
5416.0938 | 123.3032 | -61.4639 | 61.6928 | 0.1539 | -7.0232 | -4.4349 | -0.006703 | 8.2537 | 0.11763 | -2.4479 | 61.7386 | 0.28526 | 61.6377 | -0.033101 | 0.048236 | 61.5524 | 0.007721 | 61.3398 | 61.6178 | 54.4407 | 57.029 | 61.4572 | 69.7176 | 61.5816 | 59.016 | 123.2025 | 61.7492 | 123.1017 | 61.4308 | 61.5122 | 123.0164 | 61.4716 | 122.8037 | 61.6903 | 61.7308 | 61.5895 | 61.63
5417.0625 | 123.4085 | -61.4136 | 61.702 | 0.12185 | -7.2705 | -4.499 | -0.057066 | 8.2308 | 0.085583 | -2.4479 | 61.7431 | 0.29442 | 61.6469 | -0.028522 | 0.048236 | 61.5478 | 0.007721 | 61.3398 | 61.5354 | 54.1431 | 56.9145 | 61.3565 | 69.6444 | 61.4992 | 58.9656 | 123.1567 | 61.708 | 123.0605 | 61.3851 | 61.4618 | 122.9614 | 61.4213 | 122.7533 | 61.6949 | 61.7354 | 61.5987 | 61.6392
5418.0938 | 123.3902 | -61.4273 | 61.6882 | 0.14474 | -7.3025 | -4.3342 | -0.038752 | 8.2079 | 0.10848 | -2.4067 | 61.7386 | 0.28526 | 61.6423 | -0.028522 | 0.048236 | 61.557 | 0.007721 | 61.3352 | 61.572 | 54.1248 | 57.0931 | 61.3886 | 69.6352 | 61.5358 | 59.0206 | 123.1659 | 61.7126 | 123.0696 | 61.3988 | 61.4755 | 122.9843 | 61.435 | 122.7625 | 61.6903 | 61.7308 | 61.5941 | 61.6346
5419.0625 | 123.381 | -61.3953 | 61.6516 | 0.14474 | -7.1514 | -4.2609 | 0.025347 | 8.3224 | 0.11763 | -2.4479 | 61.734 | 0.29442 | 61.6698 | -0.028522 | 0.052814 | 61.5524 | 0.007721 | 61.3352 | 61.54 | 54.2438 | 57.1343 | 61.4206 | 69.7176 | 61.5129 | 58.9473 | 123.1292 | 61.6897 | 123.0651 | 61.3667 | 61.4481 | 122.9477 | 61.403 | 122.7305 | 61.6812 | 61.7263 | 61.617 | 61.6621
5420.0781 | 123.3856 | -61.4136 | 61.6653 | 0.076067 | -7.3712 | -4.2976 | 0.043661 | 8.3041 | 0.035221 | -2.5029 | 61.7386 | 0.29442 | 61.6835 | -0.028522 | 0.048236 | 61.5524 | 0.003143 | 61.3352 | 61.4896 | 54.0424 | 57.116 | 61.4572 | 69.7176 | 61.4488 | 58.9107 | 123.1521 | 61.708 | 123.0971 | 61.3851 | 61.4618 | 122.966 | 61.4167 | 122.7488 | 61.6903 | 61.7354 | 61.6353 | 61.6804
5421.0625 | 123.4451 | -61.4136 | 61.702 | 0.11269 | -7.2796 | -4.3846 | 0.07571 | 8.3269 | 0.085583 | -2.5761 | 61.7431 | 0.28984 | 61.679 | -0.028522 | 0.048236 | 61.5524 | 0.012299 | 61.3352 | 61.5263 | 54.1339 | 57.029 | 61.4893 | 69.7405 | 61.4992 | 58.8374 | 123.1567 | 61.7034 | 123.0925 | 61.3851 | 61.4618 | 122.966 | 61.4259 | 122.7488 | 61.6949 | 61.7308 | 61.6307 | 61.6667
5422.0938 | 123.4039 | -61.409 | 61.6653 | 0.18137 | -7.069 | -4.3434 | 0.10776 | 8.2857 | 0.14968 | -2.4891 | 61.7386 | 0.28526 | 61.6698 | -0.033101 | 0.039079 | 61.5524 | 0.003143 | 61.3352 | 61.5904 | 54.34 | 57.0656 | 61.5168 | 69.6947 | 61.5587 | 58.9198 | 123.1476 | 61.6943 | 123.0788 | 61.3759 | 61.4481 | 122.9614 | 61.4121 | 122.7442 | 61.6995 | 61.7354 | 61.6307 | 61.6667
5423.0625 | 123.4177 | -61.4136 | 61.6745 | 0.10354 | -7.2934 | -4.5265 | 0.089445 | 8.2583 | 0.071848 | -2.3426 | 61.7386 | 0.28526 | 61.6515 | -0.023943 | 0.048236 | 61.5433 | 0.012299 | 61.3306 | 61.5171 | 54.1202 | 56.8871 | 61.503 | 69.6719 | 61.4854 | 59.0709 | 123.1521 | 61.6988 | 123.0651 | 61.3896 | 61.4618 | 122.9568 | 61.4259 | 122.7442 | 61.6903 | 61.7263 | 61.6032 | 61.6392
5424.0781 | 123.2941 | -61.4365 | 61.7157 | -0.047549 | -7.5956 | -4.5769 | -0.093694 | 8.1347 | 0.030642 | -2.5578 | 61.7386 | 0.28526 | 61.6561 | -0.028522 | 0.043657 | 61.5433 | 0.007721 | 61.3352 | 61.3889 | 53.8409 | 56.8596 | 61.3428 | 69.5711 | 61.4671 | 58.8786 | 123.175 | 61.7217 | 123.0925 | 61.4079 | 61.4801 | 122.9797 | 61.4442 | 122.7717 | 61.6949 | 61.7308 | 61.6124 | 61.6483
5425.0625 | 123.4177 | -61.3998 | 61.6882 | -0.033814 | -7.4124 | -4.4349 | 0.11234 | 8.3636 | -0.033455 | -2.5807 | 61.7431 | 0.28526 | 61.6423 | -0.028522 | 0.043657 | 61.5433 | 0.012299 | 61.326 | 61.366 | 53.9874 | 56.9649 | 61.5122 | 69.7634 | 61.3664 | 58.8191 | 123.143 | 61.6851 | 123.0422 | 61.3713 | 61.4435 | 122.9431 | 61.4121 | 122.7259 | 61.6995 | 61.7308 | 61.5987 | 61.63
5426.0938 | 123.4085 | -61.4319 | 61.6241 | 0.094381 | -7.1285 | -4.4304 | 0.089445 | 8.3498 | 0.067269 | -2.5761 | 61.7431 | 0.28526 | 61.679 | -0.028522 | 0.039079 | 61.5478 | -0.001436 | 61.326 | 61.5263 | 54.3034 | 57.0015 | 61.5213 | 69.7817 | 61.4992 | 58.8558 | 123.175 | 61.7171 | 123.1108 | 61.4034 | 61.471 | 122.9797 | 61.4304 | 122.7579 | 61.7041 | 61.7446 | 61.6399 | 61.6804
5427.0625 | 123.4634 | -61.4136 | 61.6653 | 0.17679 | -6.9179 | -4.3571 | 0.14439 | 8.4963 | 0.13595 | -2.4663 | 61.7386 | 0.28526 | 61.6652 | -0.028522 | 0.052814 | 61.557 | 0.007721 | 61.3352 | 61.5904 | 54.4957 | 57.0565 | 61.558 | 69.9099 | 61.5495 | 58.9473 | 123.1521 | 61.6988 | 123.0788 | 61.3851 | 61.4664 | 122.9706 | 61.4213 | 122.7488 | 61.6857 | 61.7308 | 61.6124 | 61.6575
5428.0781 | 123.3902 | -61.441 | 61.647 | 0.13559 | -6.9179 | -4.4075 | 0.052818 | 8.3041 | 0.1039 | -2.4388 | 61.7294 | 0.28984 | 61.6377 | -0.028522 | 0.048236 | 61.557 | 0.012299 | 61.3352 | 61.5766 | 54.5231 | 57.0336 | 61.4939 | 69.7451 | 61.5449 | 59.0023 | 123.1704 | 61.7309 | 123.0788 | 61.4125 | 61.4893 | 122.998 | 61.4533 | 122.7762 | 61.6812 | 61.7171 | 61.5895 | 61.6255
5429.0625 | 123.4726 | -61.3678 | 61.7294 | 0.15848 | -6.7439 | -4.412 | -0.079959 | 8.3498 | 0.12221 | -2.4342 | 61.7294 | 0.28526 | 61.6423 | -0.028522 | 0.052814 | 61.557 | 0.007721 | 61.3398 | 61.5263 | 54.6239 | 56.9558 | 61.2878 | 69.7176 | 61.49 | 58.9336 | 123.0972 | 61.6531 | 123.0101 | 61.3393 | 61.4206 | 122.9248 | 61.3755 | 122.7076 | 61.6766 | 61.7217 | 61.5895 | 61.6346
5430.0938 | 123.3673 | -61.4319 | 61.6699 | 0.19053 | -6.602 | -4.4258 | -0.057066 | 8.3865 | 0.15884 | -2.4708 | 61.7294 | 0.28526 | 61.6377 | -0.033101 | 0.048236 | 61.557 | 0.012299 | 61.3398 | 61.6224 | 54.8299 | 57.0061 | 61.3748 | 69.8183 | 61.5907 | 58.961 | 123.1613 | 61.7171 | 123.0696 | 61.3988 | 61.4801 | 122.9889 | 61.4442 | 122.7717 | 61.6812 | 61.7171 | 61.5895 | 61.6255
5431.0625 | 123.3307 | -61.4548 | 61.7203 | 0.15848 | -6.7164 | -4.5814 | -0.052488 | 8.4414 | 0.12221 | -2.4708 | 61.7386 | 0.28526 | 61.6469 | -0.028522 | 0.048236 | 61.5478 | 0.007721 | 61.3398 | 61.6133 | 54.7383 | 56.8733 | 61.4023 | 69.8962 | 61.577 | 58.9839 | 123.1933 | 61.74 | 123.1017 | 61.4263 | 61.503 | 123.0026 | 61.4625 | 122.7945 | 61.6903 | 61.7308 | 61.5987 | 61.6392
5432.0781 | 123.4131 | -61.3998 | 61.6791 | 0.12643 | -6.9271 | -4.673 | -0.10285 | 8.391 | 0.09474 | -2.4754 | 61.7431 | 0.28069 | 61.6744 | -0.03768 | 0.048236 | 61.5478 | -0.001436 | 61.3215 | 61.5263 | 54.4728 | 56.7268 | 61.297 | 69.7909 | 61.4946 | 58.9244 | 123.143 | 61.6805 | 123.0742 | 61.3622 | 61.4481 | 122.9477 | 61.3984 | 122.7213 | 61.6949 | 61.7446 | 61.6261 | 61.6758
5433.0625 | 123.436 | -61.4273 | 61.6699 | 0.15848 | -7.0278 | -4.7188 | -0.10743 | 8.3269 | 0.11763 | -2.4891 | 61.7431 | 0.28984 | 61.6744 | -0.033101 | 0.048236 | 61.5478 | 0.012299 | 61.3306 | 61.5858 | 54.3995 | 56.7085 | 61.3199 | 69.7543 | 61.5449 | 58.9382 | 123.1704 | 61.7171 | 123.1017 | 61.3942 | 61.4755 | 122.9752 | 61.4396 | 122.7579 | 61.6949 | 61.7308 | 61.6261 | 61.6621
5434.0625 | 123.4131 | -61.4319 | 61.6882 | 0.14474 | -6.9774 | -4.5402 | -0.14406 | 8.2857 | 0.1039 | -2.4983 | 61.7477 | 0.28526 | 61.679 | -0.023943 | 0.048236 | 61.5524 | 0.012299 | 61.3352 | 61.5766 | 54.4545 | 56.8916 | 61.2878 | 69.7176 | 61.5358 | 58.9336 | 123.1796 | 61.7171 | 123.1108 | 61.4079 | 61.4801 | 122.9843 | 61.4442 | 122.7671 | 61.6995 | 61.7354 | 61.6307 | 61.6667
5435.0781 | 123.3032 | -61.4319 | 61.6882 | 0.15848 | -6.9683 | -4.5173 | -0.23105 | 8.0843 | 0.12221 | -2.4754 | 61.7386 | 0.29442 | 61.6561 | -0.028522 | 0.052814 | 61.5433 | 0.007721 | 61.3306 | 61.5904 | 54.4636 | 56.9145 | 61.2008 | 69.5162 | 61.5541 | 58.9565 | 123.1704 | 61.7263 | 123.0879 | 61.4034 | 61.4847 | 122.9752 | 61.4396 | 122.7625 | 61.6857 | 61.7308 | 61.6032 | 61.6483
5436.0625 | 123.349 | -61.3998 | 61.7157 | 0.19511 | -6.9866 | -4.5173 | -0.23563 | 7.9882 | 0.16799 | -2.5532 | 61.7386 | 0.28526 | 61.6515 | -0.033101 | 0.057392 | 61.5478 | 0.012299 | 61.3352 | 61.5949 | 54.4133 | 56.8825 | 61.1642 | 69.388 | 61.5678 | 58.8466 | 123.1384 | 61.6851 | 123.0513 | 61.3667 | 61.4572 | 122.9477 | 61.4121 | 122.735 | 61.6812 | 61.7263 | 61.5941 | 61.6392
5437.0938 | 123.3948 | -61.4365 | 61.6699 | 0.17679 | -7.0324 | -4.5906 | -0.23563 | 8.185 | 0.14968 | -2.5395 | 61.7386 | 0.28984 | 61.6469 | -0.03768 | 0.043657 | 61.5478 | 0.003143 | 61.3398 | 61.6133 | 54.4041 | 56.8459 | 61.2008 | 69.6215 | 61.5861 | 58.897 | 123.175 | 61.7263 | 123.0834 | 61.3988 | 61.4801 | 122.9843 | 61.4396 | 122.7762 | 61.6949 | 61.7354 | 61.6032 | 61.6438
5438.0625 | 123.3765 | -61.409 | 61.6653 | 0.20426 | -7.0965 | -4.586 | -0.25394 | 8.2583 | 0.16799 | -2.567 | 61.7386 | 0.29442 | 61.6469 | -0.028522 | 0.039079 | 61.5478 | 0.012299 | 61.3352 | 61.6133 | 54.3125 | 56.823 | 61.1551 | 69.6673 | 61.577 | 58.842 | 123.1476 | 61.7034 | 123.0559 | 61.3805 | 61.4481 | 122.9568 | 61.4213 | 122.7442 | 61.6995 | 61.7263 | 61.6078 | 61.6346
5439.0781 | 123.4222 | -61.4227 | 61.647 | 0.24089 | -7.0415 | -4.6364 | -0.22647 | 8.3315 | 0.2092 | -2.5487 | 61.7386 | 0.28984 | 61.6469 | -0.028522 | 0.039079 | 61.5478 | 0.007721 | 61.326 | 61.6636 | 54.3812 | 56.7863 | 61.1963 | 69.7543 | 61.6319 | 58.8741 | 123.1613 | 61.7126 | 123.0696 | 61.3942 | 61.4618 | 122.9706 | 61.4304 | 122.7488 | 61.6995 | 61.7308 | 61.6078 | 61.6392
5440.0625 | 123.4085 | -61.3998 | 61.6928 | 0.30041 | -6.9362 | -4.6043 | -0.13948 | 8.5192 | 0.2504 | -2.5624 | 61.7386 | 0.28984 | 61.6744 | -0.033101 | 0.043657 | 61.5524 | 0.003143 | 61.3352 | 61.7002 | 54.4636 | 56.7955 | 61.2604 | 69.9191 | 61.6502 | 58.8374 | 123.1384 | 61.6897 | 123.0742 | 61.3667 | 61.4435 | 122.9523 | 61.403 | 122.735 | 61.6949 | 61.7354 | 61.6307 | 61.6712
5441.0938 | 123.2895 | -61.4502 | 61.6791 | 0.3233 | -6.7714 | -4.6227 | -0.07538 | 8.1621 | 0.29161 | -2.5853 | 61.7386 | 0.28984 | 61.679 | -0.033101 | 0.048236 | 61.5478 | 0.012299 | 61.3398 | 61.7735 | 54.6788 | 56.8275 | 61.3748 | 69.6123 | 61.7418 | 58.8649 | 123.1887 | 61.74 | 123.1291 | 61.4171 | 61.4984 | 122.998 | 61.4625 | 122.79 | 61.6903 | 61.7263 | 61.6307 | 61.6667
5442.0625 | 123.3673 | -61.4273 | 61.702 | 0.29583 | -6.6523 | -4.4716 | -0.070802 | 8.0752 | 0.25956 | -2.5304 | 61.7386 | 0.28526 | 61.6698 | -0.033101 | 0.043657 | 61.5616 | 0.012299 | 61.3352 | 61.7231 | 54.775 | 56.9557 | 61.3565 | 69.5025 | 61.6869 | 58.897 | 123.1659 | 61.7126 | 123.0971 | 61.3942 | 61.471 | 122.9889 | 61.4396 | 122.7625 | 61.6949 | 61.7263 | 61.6261 | 61.6575
5443.0781 | 123.349 | -61.4639 | 61.7157 | 0.3233 | -6.1853 | -4.2793 | -0.057066 | 8.185 | 0.28703 | -2.5395 | 61.7248 | 0.28526 | 61.6652 | -0.028522 | 0.039079 | 61.5616 | 0.007721 | 61.3489 | 61.7872 | 55.2786 | 57.1847 | 61.4069 | 69.649 | 61.751 | 58.9244 | 123.1887 | 61.7492 | 123.1291 | 61.4354 | 61.503 | 123.0255 | 61.4716 | 122.8129 | 61.6857 | 61.7171 | 61.6261 | 61.6575
5444.0625 | 123.349 | -61.4365 | 61.6974 | 0.30956 | -6.2357 | -4.4304 | -0.15321 | 8.2033 | 0.27787 | -2.5944 | 61.7202 | 0.28984 | 61.6332 | -0.023943 | 0.043657 | 61.557 | 0.012299 | 61.3443 | 61.746 | 55.2008 | 57.0061 | 61.2832 | 69.6398 | 61.7143 | 58.842 | 123.1567 | 61.7263 | 123.0696 | 61.4125 | 61.4801 | 122.9935 | 61.4488 | 122.7808 | 61.6766 | 61.7079 | 61.5895 | 61.6209
5445.0938 | 123.317 | -61.4731 | 61.6882 | 0.20884 | -6.1212 | -4.5128 | -0.35009 | 8.1301 | 0.17715 | -2.6265 | 61.7294 | 0.28526 | 61.6423 | -0.033101 | 0.043657 | 61.5524 | 0.003143 | 61.3398 | 61.6819 | 55.3519 | 56.9603 | 61.123 | 69.6032 | 61.6502 | 58.8466 | 123.2025 | 61.7583 | 123.1154 | 61.44 | 61.5167 | 123.0255 | 61.4762 | 122.8129 | 61.6857 | 61.7263 | 61.5987 | 61.6392
5446.0625 | 123.4085 | -61.3907 | 61.702 | 0.14017 | -6.3913 | -4.5998 | -0.44624 | 7.8692 | 0.09474 | -2.686 | 61.7431 | 0.28526 | 61.6469 | -0.03768 | 0.048236 | 61.5478 | 0.012299 | 61.3306 | 61.5309 | 54.9993 | 56.7909 | 60.9444 | 69.2598 | 61.4854 | 58.7047 | 123.1338 | 61.676 | 123.0376 | 61.353 | 61.4389 | 122.9385 | 61.403 | 122.7213 | 61.6949 | 61.7308 | 61.5987 | 61.6346
5447.0938 | 123.4451 | -61.4044 | 61.6699 | 0.14932 | -6.2586 | -4.5906 | -0.47829 | 7.8646 | 0.10848 | -2.6814 | 61.7477 | 0.28069 | 61.6561 | -0.033101 | 0.039079 | 61.5433 | 0.003143 | 61.3215 | 61.5537 | 55.1459 | 56.8138 | 60.9261 | 69.269 | 61.5129 | 58.723 | 123.1521 | 61.6851 | 123.0605 | 61.3713 | 61.4435 | 122.9477 | 61.4076 | 122.7259 | 61.7086 | 61.7446 | 61.617 | 61.6529
5448.0625 | 123.3444 | -61.4044 | 61.6837 | 0.17679 | -5.7137 | -4.5082 | -0.45539 | 7.9241 | 0.14052 | -2.6769 | 61.734 | 0.29442 | 61.6561 | -0.023943 | 0.043657 | 61.557 | 0.007721 | 61.3352 | 61.5812 | 55.6907 | 56.8962 | 60.949 | 69.3285 | 61.5449 | 58.7276 | 123.1384 | 61.6988 | 123.0605 | 61.3805 | 61.4481 | 122.9614 | 61.4121 | 122.7396 | 61.6903 | 61.7263 | 61.6124 | 61.6483
5449.0781 | 123.2803 | -61.4639 | 61.702 | 0.13559 | -6.2677 | -4.6135 | -0.4325 | 7.8966 | 0.099318 | -2.7272 | 61.7477 | 0.28984 | 61.6835 | -0.028522 | 0.043657 | 61.5387 | 0.012299 | 61.326 | 61.5995 | 55.1962 | 56.8504 | 61.0314 | 69.3605 | 61.5632 | 58.7367 | 123.2116 | 61.7538 | 123.1475 | 61.4354 | 61.5076 | 123.0026 | 61.4762 | 122.79 | 61.7041 | 61.7354 | 61.6399 | 61.6712
5450.0625 | 123.3582 | -61.4319 | 61.6745 | 0.094381 | -6.5699 | -4.7371 | -0.41877 | 7.7272 | 0.062691 | -2.6402 | 61.7477 | 0.28984 | 61.6835 | -0.033101 | 0.048236 | 61.5387 | 0.007721 | 61.3215 | 61.5263 | 54.862 | 56.6948 | 61.0131 | 69.1591 | 61.4946 | 58.7917 | 123.1796 | 61.7217 | 123.1154 | 61.3988 | 61.4801 | 122.9706 | 61.4396 | 122.7533 | 61.6995 | 61.74 | 61.6353 | 61.6758
5451.0938 | 123.2849 | -61.4044 | 61.7157 | 0.03944 | -6.8584 | -4.6639 | -0.42792 | 6.6972 | 0.00775 | -2.4617 | 61.766 | 0.28526 | 61.7018 | -0.019364 | 0.043657 | 61.5387 | 0.007721 | 61.3215 | 61.4439 | 54.546 | 56.7406 | 60.9765 | 68.1016 | 61.4122 | 58.9427 | 123.1704 | 61.6897 | 123.1063 | 61.3851 | 61.4481 | 122.9431 | 61.4121 | 122.7259 | 61.7224 | 61.7583 | 61.6582 | 61.6941
5452.0625 | 123.3994 | -61.4227 | 61.6562 | 0.062332 | -7.0003 | -4.7737 | -0.29973 | 7.7272 | 0.026064 | -2.4617 | 61.7386 | 0.28526 | 61.6652 | -0.03768 | 0.043657 | 61.5387 | 0.007721 | 61.3215 | 61.4851 | 54.4224 | 56.649 | 61.123 | 69.15 | 61.4488 | 58.961 | 123.1613 | 61.708 | 123.0879 | 61.385 | 61.4664 | 122.9614 | 61.4304 | 122.7442 | 61.6949 | 61.7308 | 61.6216 | 61.6575
5453.0625 | 123.4085 | -61.4136 | 61.6608 | 0.098959 | -7.069 | -4.7005 | -0.24479 | 7.8051 | 0.062691 | -2.5624 | 61.7431 | 0.28984 | 61.6515 | -0.028522 | 0.043657 | 61.5387 | 0.007721 | 61.326 | 61.5125 | 54.3446 | 56.7131 | 61.1688 | 69.2186 | 61.4763 | 58.8512 | 123.1567 | 61.7034 | 123.0651 | 61.3851 | 61.4572 | 122.9523 | 61.4213 | 122.7396 | 61.6995 | 61.7354 | 61.6078 | 61.6438
5454.0625 | 123.349 | -61.4319 | 61.6699 | 0.14017 | -6.8355 | -4.7188 | -0.29515 | 7.8325 | 0.11305 | -2.5899 | 61.7431 | 0.28526 | 61.6423 | -0.033101 | 0.034501 | 61.5433 | 0.012299 | 61.326 | 61.5721 | 54.5964 | 56.7131 | 61.1367 | 69.2644 | 61.5449 | 58.842 | 123.175 | 61.7171 | 123.0742 | 61.3988 | 61.4664 | 122.9752 | 61.4442 | 122.7579 | 61.7086 | 61.7308 | 61.6078 | 61.63
5455.0781 | 123.2941 | -61.4594 | 61.7294 | 0.16764 | -6.7897 | -4.8333 | -0.29057 | 8.0156 | 0.12679 | -2.5624 | 61.7477 | 0.28526 | 61.6515 | -0.033101 | 0.043657 | 61.5387 | 0.003143 | 61.3306 | 61.627 | 54.6697 | 56.6261 | 61.1688 | 69.475 | 61.5861 | 58.897 | 123.2071 | 61.7446 | 123.1108 | 61.4262 | 61.503 | 122.998 | 61.4625 | 122.79 | 61.7041 | 61.7446 | 61.6078 | 61.6483
5456.0625 | 123.2849 | -61.4273 | 61.734 | 0.218 | -6.8263 | -4.7554 | -0.22189 | 8.0385 | 0.19089 | -2.5304 | 61.7477 | 0.28984 | 61.6606 | -0.028522 | 0.048236 | 61.5433 | 0.007721 | 61.3352 | 61.6453 | 54.601 | 56.6719 | 61.2054 | 69.4658 | 61.6182 | 58.897 | 123.175 | 61.7171 | 123.0879 | 61.3988 | 61.4755 | 122.9706 | 61.435 | 122.7625 | 61.6995 | 61.74 | 61.6124 | 61.6529
5457.0625 | 123.3627 | -61.4548 | 61.7569 | 0.19053 | -6.7805 | -4.8012 | -0.14864 | 8.066 | 0.16342 | -2.567 | 61.7431 | 0.28526 | 61.679 | -0.033101 | 0.057392 | 61.5387 | 0.007721 | 61.3352 | 61.6453 | 54.6742 | 56.6536 | 61.3061 | 69.5208 | 61.6182 | 58.8878 | 123.1979 | 61.74 | 123.1337 | 61.4217 | 61.5122 | 122.9935 | 61.4625 | 122.79 | 61.6857 | 61.7354 | 61.6216 | 61.6712
5458.0781 | 123.3078 | -61.496 | 61.7203 | 0.15848 | -6.7989 | -4.934 | -0.20358 | 7.9699 | 0.12679 | -2.654 | 61.7477 | 0.29442 | 61.679 | -0.03768 | 0.048236 | 61.5387 | 0.007721 | 61.3306 | 61.6545 | 54.6971 | 56.562 | 61.2924 | 69.4658 | 61.6228 | 58.842 | 123.2437 | 61.7904 | 123.1749 | 61.4583 | 61.5442 | 123.0347 | 61.5037 | 122.8266 | 61.6995 | 61.74 | 61.6307 | 61.6712
5459.0625 | 123.3994 | -61.4273 | 61.6837 | 0.098959 | -6.6844 | -4.9477 | -0.25852 | 8.0385 | 0.058113 | -2.7181 | 61.7477 | 0.28526 | 61.6881 | -0.033101 | 0.043657 | 61.5433 | 0.012299 | 61.3398 | 61.5263 | 54.7429 | 56.4796 | 61.1688 | 69.4658 | 61.4854 | 58.7092 | 123.175 | 61.7126 | 123.1154 | 61.3942 | 61.471 | 122.9706 | 61.4396 | 122.7671 | 61.7041 | 61.7354 | 61.6445 | 61.6758
5460.0781 | 123.4085 | -61.4273 | 61.6608 | 0.062332 | -6.7989 | -4.8974 | -0.31346 | 7.8692 | 0.030642 | -2.773 | 61.7523 | 0.28526 | 61.6881 | -0.028522 | 0.034501 | 61.5387 | 0.007721 | 61.3306 | 61.4896 | 54.6285 | 56.5299 | 61.1138 | 69.2965 | 61.4579 | 58.6543 | 123.1796 | 61.7126 | 123.1154 | 61.3988 | 61.4618 | 122.966 | 61.435 | 122.7579 | 61.7178 | 61.7446 | 61.6536 | 61.6804
5461.0625 | 123.2986 | -61.4136 | 61.7249 | -0.010922 | -6.8492 | -4.8791 | -0.51492 | 7.5395 | -0.033455 | -2.7593 | 61.7614 | 0.28069 | 61.7018 | -0.028522 | 0.043657 | 61.5295 | 0.012299 | 61.3306 | 61.4027 | 54.5644 | 56.5345 | 60.8987 | 68.9531 | 61.3801 | 58.6543 | 123.175 | 61.6943 | 123.1154 | 61.3851 | 61.4572 | 122.9431 | 61.4259 | 122.7442 | 61.7178 | 61.7491 | 61.6582 | 61.6895
5462.0938 | 123.3444 | -61.4365 | 61.6928 | 0.021127 | -6.5882 | -4.8653 | -0.50118 | 7.5716 | -0.005985 | -2.7272 | 61.7614 | 0.28984 | 61.6881 | -0.028522 | 0.048236 | 61.5341 | 0.007721 | 61.326 | 61.4576 | 54.8482 | 56.5711 | 60.9353 | 69.008 | 61.4305 | 58.7092 | 123.1979 | 61.7263 | 123.1246 | 61.4079 | 61.4847 | 122.9706 | 61.4442 | 122.7625 | 61.7132 | 61.7537 | 61.6399 | 61.6804
5463.0625 | 123.349 | -61.4365 | 61.702 | 0.01197 | -6.602 | -4.9065 | -0.45082 | 7.5853 | -0.015142 | -2.6631 | 61.7614 | 0.29442 | 61.6881 | -0.033101 | 0.048236 | 61.5295 | 0.007721 | 61.3123 | 61.4484 | 54.8345 | 56.5299 | 60.9856 | 69.0218 | 61.4213 | 58.7733 | 123.1979 | 61.7309 | 123.1246 | 61.4034 | 61.4847 | 122.966 | 61.4442 | 122.7488 | 61.7132 | 61.7537 | 61.6399 | 61.6804
5464.0781 | 123.2712 | -61.4502 | 61.7065 | -0.001765 | -6.7119 | -4.8882 | -0.51034 | 7.5945 | -0.038034 | -2.6631 | 61.7569 | 0.28526 | 61.6927 | -0.028522 | 0.052814 | 61.5341 | 0.012299 | 61.3215 | 61.4484 | 54.7383 | 56.562 | 60.9399 | 69.0447 | 61.4122 | 58.7871 | 123.2071 | 61.7355 | 123.1429 | 61.4217 | 61.503 | 122.9843 | 61.4625 | 122.7717 | 61.7041 | 61.7446 | 61.6399 | 61.6804
5465.0625 | 123.3765 | -61.441 | 61.6974 | 0.007391 | -6.254 | -4.8378 | -0.47371 | 7.6631 | -0.028877 | -2.5761 | 61.7569 | 0.29442 | 61.679 | -0.028522 | 0.052814 | 61.5478 | 0.007721 | 61.3215 | 61.4484 | 55.1871 | 56.6032 | 60.9673 | 69.1042 | 61.4122 | 58.8649 | 123.1979 | 61.7355 | 123.12 | 61.4125 | 61.4939 | 122.9889 | 61.4488 | 122.7625 | 61.7041 | 61.7491 | 61.6261 | 61.6712
5466.1094 | 123.349 | -61.4319 | 61.6745 | -0.079598 | -6.0388 | -4.8653 | -0.53781 | 7.5166 | -0.10671 | -2.6265 | 61.7523 | 0.28526 | 61.6881 | -0.028522 | 0.048236 | 61.5341 | 0.012299 | 61.3215 | 61.3523 | 55.3931 | 56.5666 | 60.8941 | 68.9485 | 61.3252 | 58.8054 | 123.1842 | 61.7171 | 123.12 | 61.4034 | 61.4801 | 122.966 | 61.4442 | 122.7533 | 61.7041 | 61.74 | 61.6399 | 61.6758
5467.0625 | 123.4314 | -61.3998 | 61.7065 | -0.13912 | -6.2448 | -5.0118 | -0.62022 | 7.4434 | -0.14791 | -2.7089 | 61.7569 | 0.28984 | 61.6835 | -0.028522 | 0.052814 | 61.5341 | 0.016878 | 61.326 | 61.2607 | 55.155 | 56.388 | 60.7796 | 68.8432 | 61.2519 | 58.6909 | 123.1567 | 61.6897 | 123.0834 | 61.3713 | 61.4527 | 122.934 | 61.4167 | 122.7259 | 61.7041 | 61.74 | 61.6307 | 61.6667
5468.0938 | 123.3948 | -61.4044 | 61.6882 | -0.093333 | -6.2448 | -5.1446 | -0.57444 | 7.3839 | -0.11129 | -2.6448 | 61.7477 | 0.29442 | 61.6606 | -0.028522 | 0.034501 | 61.5387 | 0.012299 | 61.3215 | 61.3111 | 55.1596 | 56.2598 | 60.83 | 68.7883 | 61.2931 | 58.7596 | 123.1521 | 61.6988 | 123.0651 | 61.3759 | 61.4389 | 122.9431 | 61.4167 | 122.7259 | 61.7132 | 61.7354 | 61.6261 | 61.6483
5469.0625 | 123.3719 | -61.3907 | 61.702 | 0.053175 | -6.0617 | -5.0622 | -0.56986 | 6.3905 | 0.012329 | -2.6814 | 61.7569 | 0.28526 | 61.6561 | -0.028522 | 0.048236 | 61.5295 | 0.007721 | 61.3169 | 61.4439 | 55.329 | 56.3285 | 60.8208 | 67.7812 | 61.403 | 58.7093 | 123.1476 | 61.676 | 123.0467 | 61.3622 | 61.4389 | 122.9202 | 61.3984 | 122.7076 | 61.7086 | 61.7491 | 61.6078 | 61.6483
5470.0781 | 123.2574 | -61.4456 | 61.7386 | 0.071489 | -5.8739 | -5.0576 | -0.58359 | 6.331 | 0.044377 | -2.7364 | 61.7614 | 0.28069 | 61.6606 | -0.033101 | 0.048236 | 61.525 | 0.012299 | 61.3169 | 61.5171 | 55.5717 | 56.388 | 60.862 | 67.7766 | 61.49 | 58.7092 | 123.2071 | 61.7263 | 123.1063 | 61.4125 | 61.4939 | 122.9706 | 61.4579 | 122.7625 | 61.7132 | 61.7491 | 61.6124 | 61.6483
5471.0625 | 123.4085 | -61.3998 | 61.6882 | 0.044018 | -5.9014 | -5.1126 | -0.63853 | 5.9693 | 0.012329 | -2.7409 | 61.7523 | 0.28526 | 61.6744 | -0.033101 | 0.048236 | 61.5295 | 0.012299 | 61.3169 | 61.4439 | 55.4984 | 56.2873 | 60.7613 | 67.3691 | 61.4122 | 58.6589 | 123.1521 | 61.6851 | 123.0742 | 61.3667 | 61.4481 | 122.9294 | 61.4121 | 122.7167 | 61.7041 | 61.74 | 61.6261 | 61.6621
5472.0938 | 123.3994 | -61.4227 | 61.6653 | 0.057754 | -6.0525 | -5.2774 | -0.63853 | 6.9627 | 0.021485 | -2.7593 | 61.7614 | 0.28984 | 61.6881 | -0.023943 | 0.039079 | 61.5295 | 0.007721 | 61.3215 | 61.4805 | 55.3702 | 56.1453 | 60.7842 | 68.3854 | 61.4442 | 58.6635 | 123.1842 | 61.7126 | 123.1108 | 61.3988 | 61.4618 | 122.9523 | 61.4304 | 122.7442 | 61.7224 | 61.7537 | 61.649 | 61.6804
5473.0625 | 123.3994 | -61.4136 | 61.6928 | -0.042971 | -6.0983 | -5.195 | -0.57901 | 6.331 | -0.051769 | -2.7318 | 61.766 | 0.28984 | 61.6973 | -0.03768 | 0.052814 | 61.525 | 0.012299 | 61.3123 | 61.3706 | 55.3153 | 56.2186 | 60.8346 | 67.7445 | 61.3618 | 58.6818 | 123.1796 | 61.7034 | 123.1108 | 61.3759 | 61.4664 | 122.9385 | 61.4259 | 122.7259 | 61.7132 | 61.7537 | 61.6445 | 61.685
5474.0781 | 123.4497 | -61.4227 | 61.6562 | 0.021127 | -6.4738 | -5.2224 | -0.53781 | 6.6468 | -0.001406 | -2.6906 | 61.7706 | 0.28526 | 61.7018 | -0.033101 | 0.048236 | 61.525 | 0.012299 | 61.3123 | 61.4439 | 54.949 | 56.2003 | 60.8849 | 68.0696 | 61.4213 | 58.7321 | 123.1933 | 61.708 | 123.1246 | 61.3896 | 61.471 | 122.9477 | 61.435 | 122.735 | 61.7224 | 61.7583 | 61.6536 | 61.6895
5475.0625 | 123.4085 | -61.3678 | 61.6791 | 0.044018 | -7.0736 | -5.314 | -0.59275 | 7.3106 | 0.021485 | -2.8325 | 61.766 | 0.28526 | 61.7018 | -0.033101 | 0.043657 | 61.5341 | 0.007721 | 61.3169 | 61.4118 | 54.2942 | 56.0538 | 60.775 | 68.6784 | 61.3893 | 58.5353 | 123.1338 | 61.6531 | 123.0696 | 61.3347 | 61.4115 | 122.9019 | 61.3755 | 122.6847 | 61.7224 | 61.7583 | 61.6582 | 61.6941
5476.1094 | 123.3582 | -61.4044 | 61.702 | 0.10354 | -6.286 | -5.2911 | -0.57901 | 7.3198 | 0.062691 | -2.7226 | 61.7614 | 0.28984 | 61.6881 | -0.028522 | 0.048236 | 61.5387 | 0.007721 | 61.326 | 61.508 | 55.1184 | 56.1133 | 60.8254 | 68.7242 | 61.4671 | 58.6818 | 123.1659 | 61.6943 | 123.0925 | 61.3759 | 61.4527 | 122.9431 | 61.4121 | 122.7305 | 61.7132 | 61.7537 | 61.6399 | 61.6804
5477.0625 | 123.4543 | -61.3953 | 61.7065 | 0.053175 | -6.428 | -5.4056 | -0.6248 | 7.3473 | 0.039799 | -2.8005 | 61.7523 | 0.28526 | 61.6698 | -0.028522 | 0.043657 | 61.5295 | 0.007721 | 61.3306 | 61.4484 | 54.9673 | 55.9897 | 60.7705 | 68.7425 | 61.4351 | 58.5948 | 123.1476 | 61.6805 | 123.0651 | 61.3667 | 61.4389 | 122.9248 | 61.403 | 122.7259 | 61.7086 | 61.7446 | 61.6261 | 61.6621
5478.0938 | 123.4085 | -61.4182 | 61.6882 | -0.047549 | -6.4646 | -5.4697 | -0.61106 | 7.361 | -0.060926 | -2.9012 | 61.7614 | 0.28984 | 61.6698 | -0.033101 | 0.048236 | 61.525 | 0.007721 | 61.3123 | 61.3706 | 54.9536 | 55.9485 | 60.8071 | 68.7792 | 61.3572 | 58.517 | 123.1796 | 61.708 | 123.088 | 61.3851 | 61.4664 | 122.9431 | 61.4259 | 122.7305 | 61.7132 | 61.7537 | 61.6216 | 61.6621
5479.0625 | 123.4177 | -61.3724 | 61.7386 | -0.079598 | -6.3135 | -5.5292 | -0.66601 | 7.2511 | -0.079239 | -2.9195 | 61.7614 | 0.28526 | 61.6698 | -0.028522 | 0.048236 | 61.5295 | 0.016878 | 61.3169 | 61.2928 | 55.0589 | 55.8432 | 60.7064 | 68.6235 | 61.2931 | 58.4529 | 123.1338 | 61.6576 | 123.0422 | 61.3439 | 61.4206 | 122.9019 | 61.3893 | 122.6893 | 61.7132 | 61.7446 | 61.6216 | 61.6529
5480.0781 | 123.4039 | -61.377 | 61.6791 | 0.01197 | -6.3822 | -5.2591 | -0.53781 | 7.393 | -0.001406 | -2.8737 | 61.7523 | 0.28984 | 61.6561 | -0.033101 | 0.039079 | 61.5341 | 0.016878 | 61.3169 | 61.3889 | 54.9948 | 56.1179 | 60.8391 | 68.77 | 61.3755 | 58.5032 | 123.1292 | 61.6668 | 123.033 | 61.3439 | 61.416 | 122.9111 | 61.3938 | 122.6938 | 61.7132 | 61.7354 | 61.617 | 61.6392
5481.0625 | 123.2574 | -61.4273 | 61.7249 | -0.065863 | -7.1377 | -5.1904 | -0.55154 | 7.3885 | -0.042612 | -2.9332 | 61.7706 | 0.28984 | 61.679 | -0.023943 | 0.048236 | 61.525 | 0.012299 | 61.3077 | 61.3614 | 54.2896 | 56.2369 | 60.8758 | 68.8158 | 61.3847 | 58.4941 | 123.1979 | 61.7171 | 123.1063 | 61.4034 | 61.4755 | 122.9523 | 61.4396 | 122.735 | 61.7224 | 61.7583 | 61.6307 | 61.6667
5482.0781 | 123.4131 | -61.3953 | 61.7065 | -0.065863 | -7.3941 | -5.2957 | -0.59275 | 7.4754 | -0.070082 | -2.9149 | 61.7614 | 0.28526 | 61.7018 | -0.033101 | 0.048236 | 61.5204 | 0.012299 | 61.3169 | 61.3294 | 54.0012 | 56.0996 | 60.8025 | 68.8707 | 61.3252 | 58.4803 | 123.1567 | 61.6805 | 123.0971 | 61.3622 | 61.4435 | 122.9156 | 61.4076 | 122.7121 | 61.7132 | 61.7491 | 61.6536 | 61.6895
5483.0625 | 123.4039 | -61.3861 | 61.7111 | -0.056706 | -7.362 | -5.3552 | -0.57444 | 7.5075 | -0.070082 | -2.9241 | 61.7614 | 0.28526 | 61.7064 | -0.028522 | 0.052814 | 61.5204 | 0.007721 | 61.3169 | 61.3294 | 54.0241 | 56.0309 | 60.8117 | 68.8936 | 61.316 | 58.462 | 123.1476 | 61.6714 | 123.0925 | 61.3576 | 61.4389 | 122.9065 | 61.3938 | 122.703 | 61.7086 | 61.7537 | 61.6536 | 61.6987
5484.0625 | 123.3948 | -61.3861 | 61.7477 | -0.10707 | -7.4994 | -5.575 | -0.753 | 7.361 | -0.11129 | -2.9561 | 61.7752 | 0.28526 | 61.7156 | -0.023943 | 0.048236 | 61.5158 | 0.003143 | 61.3077 | 61.279 | 53.8867 | 55.8111 | 60.6331 | 68.7471 | 61.2748 | 58.43 | 123.1613 | 61.6714 | 123.1017 | 61.3622 | 61.4343 | 122.9019 | 61.3893 | 122.6938 | 61.7269 | 61.772 | 61.6673 | 61.7124
5485.0625 | 123.3627 | -61.377 | 61.7569 | -0.052128 | -7.5086 | -5.3919 | -0.66143 | 7.3793 | -0.060926 | -2.9012 | 61.7752 | 0.28526 | 61.7064 | -0.019364 | 0.043657 | 61.5158 | 0.003143 | 61.3077 | 61.3248 | 53.8684 | 55.9851 | 60.7155 | 68.7563 | 61.316 | 58.4758 | 123.1521 | 61.6622 | 123.0834 | 61.3576 | 61.4206 | 122.8928 | 61.3801 | 122.6847 | 61.7315 | 61.772 | 61.6628 | 61.7033
5486.1094 | 123.381 | -61.4044 | 61.7111 | 0.007391 | -7.5406 | -5.2911 | -0.55612 | 7.48 | -0.005985 | -2.86 | 61.7569 | 0.29442 | 61.679 | -0.033101 | 0.048236 | 61.5295 | 0.007721 | 61.2986 | 61.4118 | 53.8638 | 56.1133 | 60.8483 | 68.8844 | 61.3984 | 58.5444 | 123.1613 | 61.6988 | 123.0834 | 61.3713 | 61.4527 | 122.934 | 61.4121 | 122.703 | 61.7086 | 61.7491 | 61.6307 | 61.6712
5487.0625 | 123.4222 | -61.3907 | 61.7203 | -0.020079 | -7.5681 | -5.0897 | -0.52865 | 7.48 | -0.024298 | -2.8554 | 61.766 | 0.28984 | 61.6652 | -0.033101 | 0.048236 | 61.5295 | 0.007721 | 61.3123 | 61.3706 | 53.8226 | 56.301 | 60.862 | 68.8707 | 61.3664 | 58.5353 | 123.1567 | 61.6805 | 123.0559 | 61.3576 | 61.4389 | 122.9202 | 61.3984 | 122.703 | 61.7178 | 61.7583 | 61.617 | 61.6575
5488.0781 | 123.349 | -61.4182 | 61.7065 | -0.052128 | -7.449 | -5.1217 | -0.54239 | 7.4892 | -0.060926 | -2.8783 | 61.7614 | 0.28984 | 61.679 | -0.028522 | 0.048236 | 61.5295 | 0.007721 | 61.3077 | 61.366 | 53.9691 | 56.2964 | 60.8758 | 68.9073 | 61.3572 | 58.5399 | 123.1796 | 61.708 | 123.0971 | 61.3896 | 61.4664 | 122.9477 | 61.4259 | 122.7259 | 61.7132 | 61.7537 | 61.6307 | 61.6712
5489.0625 | 123.2895 | -61.4044 | 61.7706 | -0.084176 | -7.2201 | -5.2362 | -0.6248 | 7.4617 | -0.083817 | -2.8096 | 61.766 | 0.28984 | 61.6652 | -0.028522 | 0.043657 | 61.525 | 0.012299 | 61.3077 | 61.3202 | 54.1843 | 56.1682 | 60.7796 | 68.8661 | 61.3206 | 58.5948 | 123.1704 | 61.6943 | 123.0696 | 61.3759 | 61.4481 | 122.9294 | 61.4167 | 122.7121 | 61.7224 | 61.7537 | 61.6216 | 61.6529
5490.0938 | 123.4589 | -61.3815 | 61.7294 | -0.084176 | -7.417 | -5.3827 | -0.71637 | 7.3335 | -0.083817 | -2.9607 | 61.7706 | 0.28526 | 61.6835 | -0.028522 | 0.048236 | 61.5158 | 0.003143 | 61.3077 | 61.2974 | 53.9645 | 55.9988 | 60.6652 | 68.7151 | 61.2977 | 58.4208 | 123.1521 | 61.6668 | 123.0651 | 61.353 | 61.4298 | 122.8973 | 61.3847 | 122.6893 | 61.7224 | 61.7675 | 61.6353 | 61.6804
5491.0625 | 123.2986 | -61.409 | 61.7386 | -0.093333 | -7.4719 | -5.4285 | -0.69348 | 7.2466 | -0.088396 | -2.892 | 61.7798 | 0.28984 | 61.7064 | -0.019364 | 0.048236 | 61.5112 | 0.012299 | 61.3077 | 61.3157 | 53.9371 | 55.9805 | 60.7155 | 68.6555 | 61.3206 | 58.517 | 123.1888 | 61.6988 | 123.1154 | 61.3896 | 61.4572 | 122.9202 | 61.4213 | 122.7167 | 61.7315 | 61.7675 | 61.6582 | 61.6941
5492.0938 | 123.3719 | -61.4182 | 61.7065 | -0.11165 | -7.4719 | -5.4972 | -0.69806 | 7.2649 | -0.11129 | -2.805 | 61.7706 | 0.28526 | 61.7156 | -0.028522 | 0.048236 | 61.5158 | 0.012299 | 61.294 | 61.3065 | 53.9462 | 55.921 | 60.7201 | 68.683 | 61.3069 | 58.6131 | 123.1888 | 61.7034 | 123.1337 | 61.3896 | 61.4664 | 122.934 | 61.4305 | 122.7121 | 61.7224 | 61.7583 | 61.6673 | 61.7033
5493.0625 | 123.3719 | -61.3907 | 61.7523 | -0.052128 | -7.449 | -5.5704 | -0.63853 | 7.3335 | -0.04719 | -2.9424 | 61.766 | 0.28984 | 61.7156 | -0.028522 | 0.043657 | 61.5204 | 0.007721 | 61.3031 | 61.3386 | 53.9416 | 55.8203 | 60.7522 | 68.7242 | 61.3435 | 58.4483 | 123.1567 | 61.6805 | 123.1063 | 61.3622 | 61.4343 | 122.9111 | 61.3984 | 122.6938 | 61.7224 | 61.7583 | 61.6719 | 61.7079
5494.0938 | 123.381 | -61.409 | 61.7157 | -0.001765 | -7.5132 | -5.5201 | -0.69348 | 7.274 | 0.003172 | -2.9103 | 61.766 | 0.29442 | 61.7064 | -0.028522 | 0.048236 | 61.5204 | 0.012299 | 61.2986 | 61.4072 | 53.8958 | 55.8889 | 60.7155 | 68.683 | 61.4122 | 58.4987 | 123.175 | 61.7034 | 123.1154 | 61.3805 | 61.4572 | 122.9294 | 61.4213 | 122.7076 | 61.7178 | 61.7537 | 61.6582 | 61.6941
5495.0625 | 123.3444 | -61.3678 | 61.7615 | -0.047549 | -7.5773 | -5.4605 | -0.62938 | 7.2511 | -0.038034 | -2.8966 | 61.7706 | 0.28069 | 61.6744 | -0.028522 | 0.048236 | 61.5158 | 0.003143 | 61.3077 | 61.3202 | 53.7905 | 55.9073 | 60.7384 | 68.6189 | 61.3298 | 58.4712 | 123.1384 | 61.6485 | 123.0422 | 61.3393 | 61.416 | 122.8836 | 61.3709 | 122.6755 | 61.7224 | 61.7675 | 61.6261 | 61.6712
5496.1094 | 123.3398 | -61.4182 | 61.702 | 0.01197 | -7.5498 | -5.5155 | -0.70721 | 7.2878 | 0.026064 | -2.86 | 61.766 | 0.28984 | 61.6698 | -0.028522 | 0.043657 | 61.5158 | 0.007721 | 61.3077 | 61.4301 | 53.8684 | 55.9027 | 60.7109 | 68.7059 | 61.4442 | 58.5582 | 123.1842 | 61.708 | 123.088 | 61.3896 | 61.4618 | 122.934 | 61.4259 | 122.7259 | 61.7224 | 61.7583 | 61.6261 | 61.6621
5497.0625 | 123.2895 | -61.4136 | 61.7523 | 0.025705 | -7.5498 | -5.6803 | -0.6889 | 7.3335 | 0.030642 | -2.9241 | 61.7798 | 0.28526 | 61.679 | -0.033101 | 0.043657 | 61.5204 | 0.007721 | 61.3123 | 61.4393 | 53.8638 | 55.7333 | 60.7247 | 68.7471 | 61.4442 | 58.4895 | 123.1933 | 61.6988 | 123.0925 | 61.3805 | 61.4572 | 122.934 | 61.4213 | 122.7259 | 61.7361 | 61.772 | 61.6353 | 61.6712
5498.0781 | 123.3765 | -61.3907 | 61.7111 | -0.093333 | -7.6139 | -5.8497 | -0.72095 | 7.1596 | -0.065504 | -2.8462 | 61.7706 | 0.28984 | 61.6835 | -0.033101 | 0.043657 | 61.5158 | 0.012299 | 61.2986 | 61.2974 | 53.7768 | 55.541 | 60.6697 | 68.5503 | 61.3252 | 58.5444 | 123.1613 | 61.6805 | 123.0742 | 61.3576 | 61.4343 | 122.9065 | 61.403 | 122.6893 | 61.7269 | 61.7583 | 61.6399 | 61.6712
5499.0625 | 123.3078 | -61.409 | 61.7706 | 0.071489 | -7.5956 | -5.7261 | -0.60649 | 7.1596 | 0.081005 | -2.8691 | 61.7706 | 0.28526 | 61.6835 | -0.033101 | 0.048236 | 61.5158 | 0.012299 | 61.3031 | 61.4805 | 53.8134 | 55.6829 | 60.8025 | 68.5686 | 61.49 | 58.5399 | 123.1796 | 61.6943 | 123.0925 | 61.3759 | 61.4572 | 122.9248 | 61.4213 | 122.7121 | 61.7224 | 61.7583 | 61.6353 | 61.6712
5500.0781 | 123.3719 | -61.3815 | 61.7157 | 0.076067 | -7.7833 | -5.8314 | -0.73926 | 7.0314 | 0.1039 | -2.9332 | 61.7706 | 0.28526 | 61.679 | -0.033101 | 0.052814 | 61.5158 | 0.007721 | 61.2986 | 61.4576 | 53.5982 | 55.5501 | 60.6423 | 68.4129 | 61.4854 | 58.4483 | 123.1521 | 61.6668 | 123.0605 | 61.3484 | 61.4343 | 122.8973 | 61.3893 | 122.6801 | 61.7178 | 61.7629 | 61.6261 | 61.6712
5501.0625 | 123.317 | -61.3998 | 61.7477 | -0.001765 | -7.8016 | -5.7673 | -0.73011 | 7.0177 | 0.026064 | -2.9973 | 61.7752 | 0.29442 | 61.679 | -0.023943 | 0.048236 | 61.5112 | 0.003143 | 61.294 | 61.3981 | 53.5982 | 55.6325 | 60.6697 | 68.4175 | 61.4259 | 58.4025 | 123.175 | 61.6943 | 123.0788 | 61.3759 | 61.4481 | 122.9111 | 61.403 | 122.6938 | 61.7269 | 61.772 | 61.6307 | 61.6758
5502.0781 | 123.3902 | -61.3907 | 61.7249 | 0.03944 | -7.1606 | -5.7032 | -0.64311 | 7.1046 | 0.076426 | -2.9927 | 61.7706 | 0.28984 | 61.6835 | -0.033101 | 0.048236 | 61.5204 | 0.012299 | 61.3077 | 61.4301 | 54.2301 | 55.6875 | 60.7476 | 68.4953 | 61.4671 | 58.3979 | 123.1613 | 61.6805 | 123.0742 | 61.3576 | 61.4389 | 122.9111 | 61.403 | 122.6984 | 61.7224 | 61.7583 | 61.6353 | 61.6712
5503.0625 | 123.2758 | -61.4319 | 61.7523 | 0.11727 | -6.9316 | -5.6299 | -0.58817 | 7.2191 | 0.081005 | -2.9195 | 61.766 | 0.28984 | 61.6698 | -0.023943 | 0.043657 | 61.5158 | 0.012299 | 61.3077 | 61.5492 | 54.5002 | 55.8019 | 60.8437 | 68.651 | 61.5129 | 58.5124 | 123.1979 | 61.7217 | 123.1017 | 61.4079 | 61.4755 | 122.9477 | 61.4442 | 122.7396 | 61.7224 | 61.7537 | 61.6261 | 61.6575
5504.0781 | 123.3994 | -61.4182 | 61.7203 | 0.076067 | -7.5269 | -5.9001 | -0.71179 | 7.1184 | 0.039799 | -3.0294 | 61.7706 | 0.28984 | 61.6698 | -0.033101 | 0.043657 | 61.5158 | -0.001436 | 61.2986 | 61.4942 | 53.8913 | 55.5181 | 60.7064 | 68.5365 | 61.458 | 58.3888 | 123.1888 | 61.708 | 123.088 | 61.3851 | 61.4618 | 122.934 | 61.4167 | 122.7167 | 61.7269 | 61.772 | 61.6261 | 61.6712
5505.0625 | 123.2666 | -61.3907 | 61.7706 | 0.007391 | -7.765 | -5.868 | -0.70721 | 7.068 | -0.01972 | -3.2125 | 61.7798 | 0.28984 | 61.6835 | -0.023943 | 0.052814 | 61.5112 | 0.016878 | 61.2986 | 61.3981 | 53.6257 | 55.5227 | 60.6835 | 68.4587 | 61.371 | 58.1782 | 123.1704 | 61.6805 | 123.0742 | 61.3667 | 61.4435 | 122.9019 | 61.4076 | 122.6893 | 61.7269 | 61.7629 | 61.6307 | 61.6667
5506.0938 | 123.2986 | -61.3953 | 61.7661 | -0.18948 | -7.8886 | -5.8772 | -0.67516 | 7.0909 | -0.15249 | -3.2766 | 61.7798 | 0.28984 | 61.6973 | -0.028522 | 0.052814 | 61.5158 | 0.003143 | 61.2894 | 61.2058 | 53.5067 | 55.5181 | 60.7201 | 68.4862 | 61.2428 | 58.1187 | 123.175 | 61.6851 | 123.0925 | 61.3667 | 61.4481 | 122.9111 | 61.3984 | 122.6847 | 61.7269 | 61.7766 | 61.6445 | 61.6941
5507.0625 | 123.3032 | -61.4227 | 61.7981 | -0.20321 | -7.971 | -5.8772 | -0.71637 | 7.068 | -0.17081 | -3.1484 | 61.7843 | 0.28984 | 61.7064 | -0.023943 | 0.048236 | 61.5021 | 0.016878 | 61.294 | 61.2195 | 53.4517 | 55.5455 | 60.7064 | 68.4907 | 61.2519 | 58.2743 | 123.2071 | 61.7126 | 123.1292 | 61.3988 | 61.471 | 122.9248 | 61.4396 | 122.7167 | 61.7361 | 61.7675 | 61.6582 | 61.6895
5508.0781 | 123.3444 | -61.3815 | 61.7111 | -0.024657 | -7.8886 | -5.5842 | -0.59275 | 7.2603 | -0.042612 | -3.1393 | 61.7798 | 0.27611 | 61.7064 | -0.03768 | 0.043657 | 61.5158 | 0.007721 | 61.294 | 61.3569 | 53.4929 | 55.7974 | 60.7888 | 68.6418 | 61.3389 | 58.2423 | 123.1613 | 61.6576 | 123.088 | 61.3439 | 61.4252 | 122.8973 | 61.3893 | 122.6755 | 61.7361 | 61.772 | 61.6628 | 61.6987
5509.0625 | 123.2712 | -61.4227 | 61.7752 | -0.038393 | -7.9619 | -5.6071 | -0.66143 | 7.187 | -0.056347 | -3.1393 | 61.7843 | 0.30358 | 61.7202 | -0.028522 | 0.048236 | 61.5021 | 0.007721 | 61.3077 | 61.3843 | 53.4609 | 55.8157 | 60.7613 | 68.6098 | 61.3664 | 58.2835 | 123.2071 | 61.7263 | 123.1429 | 61.3942 | 61.471 | 122.9248 | 61.4304 | 122.7305 | 61.7361 | 61.7766 | 61.6719 | 61.7124
5510.0781 | 123.3719 | -61.4044 | 61.734 | -0.10707 | -8.0672 | -5.7536 | -0.83083 | 6.9536 | -0.12502 | -3.2491 | 61.7935 | 0.29442 | 61.7202 | -0.033101 | 0.048236 | 61.5021 | 0.003143 | 61.2986 | 61.2974 | 53.3372 | 55.6509 | 60.5736 | 68.358 | 61.2794 | 58.1553 | 123.1979 | 61.6988 | 123.1246 | 61.3713 | 61.4527 | 122.9065 | 61.4076 | 122.703 | 61.7453 | 61.7904 | 61.6719 | 61.717
5511.0625 | 123.2941 | -61.3953 | 61.7386 | -0.19864 | -8.0992 | -5.8451 | -0.78505 | 7.0543 | -0.20743 | -3.2262 | 61.7843 | 0.29442 | 61.7202 | -0.028522 | 0.043657 | 61.5021 | 0.007721 | 61.2894 | 61.1966 | 53.296 | 55.5501 | 60.6102 | 68.4495 | 61.1878 | 58.169 | 123.1796 | 61.6897 | 123.1154 | 61.3667 | 61.4389 | 122.8973 | 61.403 | 122.6847 | 61.7407 | 61.7766 | 61.6765 | 61.7124
5512.0781 | 123.3536 | -61.3586 | 61.734 | -0.10249 | -7.8428 | -5.8635 | -0.78047 | 6.9902 | -0.12044 | -2.9973 | 61.7752 | 0.28526 | 61.6927 | -0.033101 | 0.043657 | 61.4975 | 0.007721 | 61.2848 | 61.2562 | 53.5158 | 55.4952 | 60.5782 | 68.3488 | 61.2382 | 58.3613 | 123.1338 | 61.6439 | 123.0513 | 61.3255 | 61.4023 | 122.8561 | 61.3664 | 122.6435 | 61.7315 | 61.7675 | 61.649 | 61.685
5513.0625 | 123.4314 | -61.377 | 61.6974 | -0.13454 | -7.797 | -5.8039 | -0.84457 | 6.9627 | -0.04719 | -3.0523 | 61.7752 | 0.28984 | 61.679 | -0.033101 | 0.048236 | 61.5021 | 0.007721 | 61.2848 | 61.2424 | 53.5799 | 55.573 | 60.5324 | 68.3397 | 61.3298 | 58.3247 | 123.1521 | 61.6668 | 123.0559 | 61.3439 | 61.4252 | 122.879 | 61.3847 | 122.6618 | 61.7269 | 61.7675 | 61.6307 | 61.6712
5514.0781 | 123.381 | -61.3861 | 61.6928 | -0.15743 | -7.6551 | -5.6712 | -0.84915 | 7.0405 | -0.17539 | -2.9882 | 61.7752 | 0.28984 | 61.679 | -0.033101 | 0.043657 | 61.5112 | 0.012299 | 61.294 | 61.2287 | 53.731 | 55.715 | 60.537 | 68.4266 | 61.2107 | 58.3979 | 123.1613 | 61.676 | 123.0651 | 61.353 | 61.4298 | 122.8973 | 61.3984 | 122.6801 | 61.7315 | 61.7629 | 61.6353 | 61.6667
5515.0625 | 123.2666 | -61.377 | 61.7706 | -0.18948 | -7.8016 | -5.7627 | -0.95903 | 7.0314 | -0.21201 | -2.9149 | 61.7752 | 0.29442 | 61.6973 | -0.033101 | 0.048236 | 61.5066 | 0.012299 | 61.2894 | 61.1875 | 53.5753 | 55.6142 | 60.4179 | 68.4083 | 61.1649 | 58.462 | 123.1521 | 61.6714 | 123.0742 | 61.3439 | 61.4252 | 122.8836 | 61.3893 | 122.6664 | 61.7269 | 61.7629 | 61.649 | 61.685
5516.1094 | 123.3856 | -61.3586 | 61.7249 | -0.18032 | -7.7925 | -5.7261 | -0.93614 | 7.0726 | -0.20286 | -2.9515 | 61.7798 | 0.28984 | 61.6973 | -0.028522 | 0.048236 | 61.5112 | 0.012299 | 61.294 | 61.1783 | 53.5662 | 55.6325 | 60.4225 | 68.4312 | 61.1558 | 58.4071 | 123.1384 | 61.6485 | 123.0559 | 61.3301 | 61.4069 | 122.8699 | 61.3709 | 122.6526 | 61.7315 | 61.7675 | 61.649 | 61.685
5517.0625 | 123.262 | -61.3907 | 61.7981 | -0.24442 | -7.8154 | -5.8131 | -0.96361 | 7.1138 | -0.27153 | -2.9744 | 61.7843 | 0.28526 | 61.7293 | -0.033101 | 0.048236 | 61.5066 | 0.012299 | 61.2894 | 61.1463 | 53.5753 | 55.5776 | 60.4271 | 68.5045 | 61.1192 | 58.4163 | 123.175 | 61.676 | 123.12 | 61.3576 | 61.4389 | 122.8973 | 61.403 | 122.6801 | 61.7361 | 61.772 | 61.6811 | 61.717
5518.0938 | 123.3078 | -61.4182 | 61.7798 | -0.34057 | -7.7741 | -5.8955 | -0.9865 | 7.1641 | -0.3631 | -2.9882 | 61.7981 | 0.28984 | 61.7293 | -0.028522 | 0.043657 | 61.4975 | 0.007721 | 61.2894 | 61.0776 | 53.644 | 55.5226 | 60.4317 | 68.5823 | 61.0551 | 58.43 | 123.2162 | 61.708 | 123.1475 | 61.3896 | 61.4618 | 122.9156 | 61.4259 | 122.7076 | 61.7544 | 61.7904 | 61.6857 | 61.7216
5519.0625 | 123.3215 | -61.3907 | 61.8027 | -0.3131 | -7.8291 | -5.9138 | -1.0002 | 7.1184 | -0.33105 | -3.0614 | 61.7935 | 0.28984 | 61.7247 | -0.028522 | 0.048236 | 61.5066 | 0.012299 | 61.2986 | 61.0776 | 53.5616 | 55.4769 | 60.3905 | 68.5091 | 61.0596 | 58.3293 | 123.1842 | 61.6805 | 123.1154 | 61.3622 | 61.4389 | 122.8973 | 61.403 | 122.6893 | 61.7453 | 61.7812 | 61.6765 | 61.7124
5520.0938 | 123.4177 | -61.3632 | 61.7249 | -0.20321 | -7.6276 | -5.7124 | -0.7942 | 7.3656 | -0.21659 | -2.86 | 61.7752 | 0.28069 | 61.6927 | -0.033101 | 0.048236 | 61.5158 | 0.007721 | 61.3031 | 61.16 | 53.7356 | 55.6509 | 60.569 | 68.7288 | 61.1466 | 58.5032 | 123.1384 | 61.6439 | 123.0559 | 61.3301 | 61.4115 | 122.879 | 61.3709 | 122.6664 | 61.7269 | 61.7675 | 61.6445 | 61.685
5521.0625 | 123.2895 | -61.4227 | 61.7477 | -0.15743 | -7.8199 | -5.5933 | -0.82625 | 7.2237 | -0.17539 | -2.9699 | 61.7752 | 0.28984 | 61.679 | -0.033101 | 0.043657 | 61.5158 | 0.007721 | 61.3031 | 61.2653 | 53.6028 | 55.8294 | 60.5965 | 68.6464 | 61.2473 | 58.4529 | 123.1979 | 61.7126 | 123.1017 | 61.3896 | 61.4664 | 122.9385 | 61.4304 | 122.7259 | 61.7315 | 61.7675 | 61.6353 | 61.6712
5522.0938 | 123.3673 | -61.3541 | 61.7477 | -0.249 | -7.8703 | -5.8085 | -1.0598 | 6.9856 | -0.27153 | -3.1164 | 61.7752 | 0.28069 | 61.6835 | -0.033101 | 0.048236 | 61.5021 | 0.007721 | 61.294 | 61.1051 | 53.4838 | 55.5456 | 60.2943 | 68.3397 | 61.0825 | 58.2377 | 123.1292 | 61.6347 | 123.0376 | 61.321 | 61.4023 | 122.8561 | 61.3618 | 122.6481 | 61.7269 | 61.7675 | 61.6353 | 61.6758
5523.0625 | 123.3719 | -61.409 | 61.702 | -0.1849 | -7.9207 | -5.9138 | -1.0735 | 7.0314 | -0.20286 | -3.0889 | 61.7843 | 0.28526 | 61.6881 | -0.028522 | 0.048236 | 61.4975 | 0.003143 | 61.2894 | 61.2241 | 53.4883 | 55.4952 | 60.3355 | 68.4404 | 61.2061 | 58.3201 | 123.1933 | 61.6943 | 123.0971 | 61.3805 | 61.4572 | 122.9065 | 61.4121 | 122.6984 | 61.7361 | 61.7812 | 61.6399 | 61.685
5524.0938 | 123.4039 | -61.377 | 61.7249 | -0.21695 | -7.8199 | -5.9138 | -1.0689 | 7.0909 | -0.24406 | -3.153 | 61.7843 | 0.28984 | 61.7018 | -0.028522 | 0.052814 | 61.5066 | 0.016878 | 61.2894 | 61.16 | 53.557 | 55.4631 | 60.308 | 68.4679 | 61.1329 | 58.224 | 123.1613 | 61.6668 | 123.0788 | 61.3484 | 61.4298 | 122.8836 | 61.3938 | 122.6664 | 61.7315 | 61.7675 | 61.649 | 61.685
5525.0625 | 123.3032 | -61.377 | 61.7889 | -0.39551 | -7.8611 | -6.0558 | -1.1239 | 7.4159 | -0.42262 | -3.2079 | 61.7843 | 0.28984 | 61.7247 | -0.033101 | 0.052814 | 61.5066 | 0.012299 | 61.2986 | 60.9814 | 53.5158 | 55.3212 | 60.2531 | 68.7929 | 60.9543 | 58.169 | 123.1613 | 61.6668 | 123.1017 | 61.3439 | 61.4298 | 122.8836 | 61.3893 | 122.6755 | 61.7315 | 61.772 | 61.6719 | 61.7124
5526.0938 | 123.3673 | -61.3861 | 61.734 | -0.40924 | -7.9298 | -5.955 | -0.96819 | 7.1733 | -0.43178 | -3.1438 | 61.7889 | 0.28526 | 61.7247 | -0.028522 | 0.052814 | 61.4975 | 0.012299 | 61.2894 | 60.9769 | 53.4563 | 55.4311 | 60.4179 | 68.5594 | 60.9543 | 58.2423 | 123.175 | 61.6714 | 123.1108 | 61.3576 | 61.4389 | 122.8836 | 61.3984 | 122.6755 | 61.7361 | 61.7766 | 61.6719 | 61.7124
5527.0625 | 123.2712 | -61.3586 | 61.7935 | -0.39551 | -8.1404 | -5.9276 | -1.0872 | 6.9902 | -0.42262 | -3.2079 | 61.8027 | 0.28526 | 61.7385 | -0.028522 | 0.043657 | 61.4975 | 0.007721 | 61.2894 | 60.9631 | 53.2182 | 55.4311 | 60.2714 | 68.3488 | 60.936 | 58.1507 | 123.1613 | 61.6439 | 123.0971 | 61.3301 | 61.4023 | 122.8561 | 61.3664 | 122.6481 | 61.759 | 61.7949 | 61.6948 | 61.7308
5528.0781 | 123.3124 | -61.4136 | 61.7798 | -0.40466 | -8.1267 | -5.8772 | -1.0506 | 6.9536 | -0.4272 | -3.2171 | 61.7935 | 0.28526 | 61.7385 | -0.033101 | 0.052814 | 61.4929 | 0.012299 | 61.2986 | 61.0089 | 53.2869 | 55.5364 | 60.363 | 68.3671 | 60.9864 | 58.1965 | 123.2071 | 61.6988 | 123.152 | 61.3805 | 61.4664 | 122.9065 | 61.4259 | 122.7121 | 61.7407 | 61.7812 | 61.6857 | 61.7262
5529.0625 | 123.2986 | -61.3998 | 61.7889 | -0.33599 | -8.145 | -5.7902 | -1.014 | 7.0634 | -0.3631 | -3.1118 | 61.7935 | 0.28984 | 61.7247 | -0.028522 | 0.052814 | 61.5021 | 0.012299 | 61.294 | 61.0639 | 53.2548 | 55.6096 | 60.3859 | 68.4633 | 61.0367 | 58.2881 | 123.1933 | 61.6897 | 123.1246 | 61.3713 | 61.4527 | 122.9019 | 61.4121 | 122.6938 | 61.7407 | 61.7812 | 61.6719 | 61.7124
5530.0781 | 123.3353 | -61.377 | 61.7203 | -0.249 | -7.9619 | -5.9276 | -1.1513 | 6.949 | -0.27611 | -3.0294 | 61.7889 | 0.28526 | 61.7247 | -0.033101 | 0.043657 | 61.4975 | 0.012299 | 61.2894 | 61.128 | 53.4151 | 55.4494 | 60.2256 | 68.3259 | 61.1008 | 58.3476 | 123.1659 | 61.6622 | 123.1017 | 61.3439 | 61.4206 | 122.8744 | 61.3893 | 122.6664 | 61.7453 | 61.7766 | 61.6811 | 61.7124
5531.0625 | 123.4039 | -61.3815 | 61.702 | -0.20321 | -7.4124 | -5.8589 | -1.0231 | 7.0451 | -0.2349 | -2.9378 | 61.7843 | 0.29442 | 61.7156 | -0.028522 | 0.039079 | 61.5112 | 0.003143 | 61.294 | 61.1783 | 53.9691 | 55.5227 | 60.3584 | 68.4266 | 61.1466 | 58.4437 | 123.1659 | 61.676 | 123.0971 | 61.353 | 61.4206 | 122.8928 | 61.3847 | 122.6755 | 61.7453 | 61.7812 | 61.6765 | 61.7124
5532.0781 | 123.3627 | -61.3907 | 61.7569 | -0.19864 | -7.4124 | -5.9596 | -0.9865 | 7.0817 | -0.22575 | -3.0111 | 61.7843 | 0.28984 | 61.7156 | -0.028522 | 0.048236 | 61.5066 | 0.007721 | 61.294 | 61.1921 | 53.9783 | 55.4311 | 60.4042 | 68.4724 | 61.1649 | 58.3796 | 123.175 | 61.6805 | 123.1063 | 61.3622 | 61.4389 | 122.8973 | 61.3984 | 122.6847 | 61.7361 | 61.7766 | 61.6673 | 61.7079
5533.0625 | 123.2986 | -61.3953 | 61.7798 | -0.38177 | -7.5773 | -6.1107 | -1.0048 | 7.0863 | -0.41804 | -3.0385 | 61.7935 | 0.28526 | 61.7293 | -0.028522 | 0.052814 | 61.4929 | 0.007721 | 61.2894 | 61.0135 | 53.818 | 55.2846 | 60.3904 | 68.4816 | 60.9772 | 58.3567 | 123.1888 | 61.6805 | 123.1246 | 61.3667 | 61.4481 | 122.8882 | 61.403 | 122.6847 | 61.7407 | 61.7858 | 61.6765 | 61.7216
5534.0781 | 123.4406 | -61.322 | 61.7661 | -0.47792 | -7.5727 | -6.2893 | -1.101 | 6.9215 | -0.50045 | -3.2033 | 61.7935 | 0.28984 | 61.7293 | -0.028522 | 0.043657 | 61.4929 | 0.012299 | 61.2848 | 60.8441 | 53.7493 | 55.0328 | 60.2211 | 68.2435 | 60.8216 | 58.1187 | 123.1155 | 61.6119 | 123.0513 | 61.2935 | 61.3657 | 122.8149 | 61.3343 | 122.6069 | 61.7498 | 61.7812 | 61.6857 | 61.717
5535.0625 | 123.3032 | -61.4044 | 61.8027 | -0.49165 | -7.6047 | -6.2526 | -1.0689 | 6.9627 | -0.51876 | -3.1438 | 61.7935 | 0.28526 | 61.7293 | -0.033101 | 0.052814 | 61.4929 | 0.012299 | 61.2757 | 60.9128 | 53.7997 | 55.1518 | 60.3355 | 68.3671 | 60.8857 | 58.2606 | 123.1979 | 61.6897 | 123.1337 | 61.3713 | 61.4572 | 122.8973 | 61.4167 | 122.6801 | 61.7407 | 61.7812 | 61.6765 | 61.717
5536.0938 | 123.4177 | -61.3541 | 61.7203 | -0.55575 | -7.6001 | -6.2709 | -1.1055 | 6.949 | -0.57371 | -3.0935 | 61.7935 | 0.299 | 61.7247 | -0.033101 | 0.048236 | 61.4929 | 0.007721 | 61.2711 | 60.7983 | 53.7539 | 55.0831 | 60.2485 | 68.303 | 60.7804 | 58.2606 | 123.1476 | 61.6531 | 123.0788 | 61.321 | 61.4023 | 122.847 | 61.3618 | 122.6252 | 61.7453 | 61.7858 | 61.6765 | 61.717
5537.0625 | 123.3353 | -61.3861 | 61.7752 | -0.53286 | -7.623 | -6.2252 | -1.0048 | 7.0268 | -0.55539 | -3.034 | 61.8027 | 0.28526 | 61.7293 | -0.028522 | 0.052814 | 61.4975 | 0.007721 | 61.2894 | 60.8533 | 53.7631 | 55.1609 | 60.3813 | 68.4129 | 60.8307 | 58.3522 | 123.1888 | 61.6714 | 123.1154 | 61.3576 | 61.4389 | 122.8836 | 61.3938 | 122.6755 | 61.7498 | 61.7949 | 61.6765 | 61.7216
5538.0938 | 123.2986 | -61.3907 | 61.8073 | -0.37719 | -7.7192 | -6.1199 | -1.0048 | 6.9261 | -0.40431 | -3.0523 | 61.7935 | 0.28069 | 61.7293 | -0.033101 | 0.057392 | 61.4975 | 0.012299 | 61.2986 | 61.0135 | 53.6715 | 55.2708 | 60.3859 | 68.3168 | 60.9864 | 58.3384 | 123.1842 | 61.6714 | 123.12 | 61.3576 | 61.4481 | 122.8882 | 61.403 | 122.6893 | 61.7361 | 61.7812 | 61.6719 | 61.717
5539.0625 | 123.2895 | -61.3815 | 61.7935 | -0.47792 | -7.9527 | -6.0237 | -1.1742 | 7.0131 | -0.49587 | -3.1713 | 61.7981 | 0.29442 | 61.7385 | -0.033101 | 0.043657 | 61.4883 | 0.012299 | 61.2848 | 60.9036 | 53.4288 | 55.3578 | 60.2073 | 68.3946 | 60.8857 | 58.2102 | 123.1796 | 61.676 | 123.12 | 61.3484 | 61.4252 | 122.8699 | 61.3938 | 122.6664 | 61.7544 | 61.7858 | 61.6948 | 61.7262
5540.0938 | 123.4451 | -61.3495 | 61.7523 | -0.4825 | -7.8657 | -5.9367 | -1.133 | 7.2328 | -0.50961 | -3.2171 | 61.7981 | 0.28984 | 61.7339 | -0.028522 | 0.043657 | 61.4975 | 0.007721 | 61.2848 | 60.867 | 53.4838 | 55.4128 | 60.2165 | 68.5823 | 60.8399 | 58.1324 | 123.1476 | 61.6393 | 123.0834 | 61.321 | 61.3931 | 122.847 | 61.3572 | 122.6343 | 61.7544 | 61.7904 | 61.6902 | 61.7262
5541.0625 | 123.2895 | -61.4136 | 61.7477 | -0.47334 | -7.6001 | -5.9413 | -1.1513 | 7.3015 | -0.50503 | -3.2949 | 61.8027 | 0.28526 | 61.7339 | -0.028522 | 0.043657 | 61.4975 | 0.012299 | 61.294 | 60.9402 | 53.8134 | 55.4723 | 60.2622 | 68.7151 | 60.9085 | 58.1187 | 123.2162 | 61.6988 | 123.1475 | 61.3851 | 61.4572 | 122.9111 | 61.4259 | 122.7076 | 61.759 | 61.7904 | 61.6902 | 61.7216
5542.0781 | 123.3994 | -61.3403 | 61.7432 | -0.51912 | -7.7009 | -6.0329 | -1.1605 | 7.3198 | -0.54166 | -3.4231 | 61.7981 | 0.28984 | 61.7247 | -0.028522 | 0.048236 | 61.4929 | 0.007721 | 61.2848 | 60.8212 | 53.6394 | 55.3075 | 60.1798 | 68.6601 | 60.7987 | 57.9172 | 123.1384 | 61.6302 | 123.0651 | 61.3118 | 61.3886 | 122.8332 | 61.3481 | 122.6252 | 61.7498 | 61.7904 | 61.6765 | 61.717
5543.0625 | 123.2803 | -61.3861 | 61.7935 | -0.52828 | -7.6917 | -6.0237 | -1.1147 | 7.3015 | -0.55081 | -3.3682 | 61.7889 | 0.28984 | 61.7247 | -0.023943 | 0.052814 | 61.4975 | 0.007721 | 61.2894 | 60.8578 | 53.6944 | 55.3624 | 60.2714 | 68.6876 | 60.8353 | 58.0179 | 123.175 | 61.676 | 123.1108 | 61.3622 | 61.4389 | 122.8836 | 61.3938 | 122.6755 | 61.7361 | 61.7812 | 61.6719 | 61.717
5544.0938 | 123.3948 | -61.3358 | 61.7477 | -0.52828 | -7.7146 | -6.0603 | -1.1055 | 7.1779 | -0.55081 | -3.4185 | 61.8027 | 0.28069 | 61.7293 | -0.028522 | 0.052814 | 61.4929 | 0.007721 | 61.2803 | 60.8075 | 53.6211 | 55.2754 | 60.2302 | 68.5136 | 60.7849 | 57.9172 | 123.1384 | 61.6164 | 123.0651 | 61.3072 | 61.3886 | 122.8287 | 61.3435 | 122.616 | 61.7498 | 61.7949 | 61.6765 | 61.7216
5545.0625 | 123.2941 | -61.3815 | 61.7935 | -0.57406 | -7.71 | -6.2023 | -1.1834 | 7.1138 | -0.5966 | -3.446 | 61.8027 | 0.28526 | 61.7247 | -0.023943 | 0.048236 | 61.4883 | 0.007721 | 61.2894 | 60.8075 | 53.6715 | 55.1793 | 60.1982 | 68.4953 | 60.7849 | 57.9355 | 123.1842 | 61.6668 | 123.1063 | 61.3576 | 61.4298 | 122.8699 | 61.3893 | 122.6709 | 61.7544 | 61.7949 | 61.6765 | 61.717
5546.1094 | 123.381 | -61.3403 | 61.7615 | -0.59696 | -7.7146 | -6.2755 | -1.2063 | 7.1138 | -0.61949 | -3.3224 | 61.8027 | 0.28984 | 61.7156 | -0.028522 | 0.048236 | 61.4883 | 0.012299 | 61.2848 | 60.7434 | 53.6257 | 55.0648 | 60.1341 | 68.4541 | 60.7208 | 58.018 | 123.143 | 61.6302 | 123.0559 | 61.3118 | 61.3886 | 122.8287 | 61.3526 | 122.6252 | 61.7544 | 61.7904 | 61.6673 | 61.7033
5547.0625 | 123.3444 | -61.377 | 61.8164 | -0.55117 | -7.6505 | -6.2297 | -1.0506 | 7.3152 | -0.56455 | -3.391 | 61.7935 | 0.28984 | 61.6973 | -0.028522 | 0.048236 | 61.4929 | 0.012299 | 61.2894 | 60.8258 | 53.7264 | 55.1472 | 60.3264 | 68.6922 | 60.8124 | 57.9859 | 123.1704 | 61.6668 | 123.0742 | 61.3484 | 61.4252 | 122.8699 | 61.3893 | 122.6664 | 61.7453 | 61.7812 | 61.649 | 61.685
5548.0781 | 123.4039 | -61.3678 | 61.7065 | -0.4825 | -7.5177 | -6.1611 | -1.0002 | 7.4068 | -0.50045 | -3.3956 | 61.7843 | 0.29442 | 61.6881 | -0.033101 | 0.043657 | 61.4975 | 0.003143 | 61.294 | 60.8853 | 53.8501 | 55.2067 | 60.3676 | 68.7746 | 60.8673 | 57.9722 | 123.1521 | 61.6622 | 123.0559 | 61.3347 | 61.4115 | 122.8653 | 61.3709 | 122.6618 | 61.7407 | 61.7812 | 61.6445 | 61.685
5549.0625 | 123.2941 | -61.3632 | 61.7844 | -0.52828 | -7.6047 | -6.2068 | -1.0186 | 7.3473 | -0.55081 | -3.4597 | 61.8027 | 0.28984 | 61.7064 | -0.033101 | 0.052814 | 61.4883 | 0.012299 | 61.2848 | 60.8349 | 53.7585 | 55.1564 | 60.3447 | 68.7105 | 60.8124 | 57.9035 | 123.1659 | 61.6531 | 123.0696 | 61.3301 | 61.416 | 122.8516 | 61.3755 | 122.6481 | 61.7498 | 61.7904 | 61.6536 | 61.6941
5550.0781 | 123.3948 | -61.3449 | 61.7432 | -0.54202 | -7.4994 | -6.2755 | -1.0277 | 7.5212 | -0.56455 | -3.4551 | 61.7798 | 0.299 | 61.7064 | -0.028522 | 0.048236 | 61.4975 | 0.012299 | 61.294 | 60.8029 | 53.8455 | 55.0694 | 60.3172 | 68.8661 | 60.7804 | 57.8898 | 123.1247 | 61.6439 | 123.0513 | 61.3164 | 61.3931 | 122.8424 | 61.3572 | 122.6389 | 61.7315 | 61.7675 | 61.6582 | 61.6941
5551.0625 | 123.3078 | -61.3907 | 61.7615 | -0.59238 | -7.4857 | -6.3625 | -1.0689 | 7.5487 | -0.61949 | -3.3727 | 61.7981 | 0.299 | 61.7293 | -0.033101 | 0.052814 | 61.4929 | 0.007721 | 61.294 | 60.7983 | 53.905 | 55.0282 | 60.3218 | 68.9394 | 60.7712 | 58.0179 | 123.1888 | 61.6897 | 123.12 | 61.3576 | 61.4435 | 122.8836 | 61.3984 | 122.6847 | 61.7453 | 61.7904 | 61.6765 | 61.7216
5552.0781 | 123.4268 | -61.3541 | 61.7569 | -0.60611 | -7.5086 | -6.3854 | -1.1467 | 7.535 | -0.6378 | -3.3819 | 61.8027 | 0.28984 | 61.7385 | -0.028522 | 0.048236 | 61.4929 | 0.012299 | 61.294 | 60.748 | 53.8455 | 54.9687 | 60.2073 | 68.889 | 60.7163 | 57.9722 | 123.1567 | 61.6439 | 123.0925 | 61.3255 | 61.4023 | 122.847 | 61.3664 | 122.6481 | 61.7544 | 61.7904 | 61.6902 | 61.7262
5553.0625 | 123.3261 | -61.3907 | 61.7661 | -0.57406 | -7.5498 | -6.3213 | -1.1513 | 7.4159 | -0.60118 | -3.3544 | 61.7981 | 0.28984 | 61.7339 | -0.028522 | 0.039079 | 61.4929 | 0.007721 | 61.3031 | 60.8166 | 53.8409 | 55.0694 | 60.2394 | 68.8066 | 60.7895 | 58.0363 | 123.1888 | 61.6805 | 123.1246 | 61.3622 | 61.4298 | 122.8836 | 61.3984 | 122.6938 | 61.759 | 61.7904 | 61.6948 | 61.7262
5554.0938 | 123.4131 | -61.3632 | 61.7203 | -0.46876 | -7.5177 | -6.2847 | -1.1971 | 7.5716 | -0.49587 | -3.3865 | 61.7889 | 0.28984 | 61.7202 | -0.033101 | 0.052814 | 61.4975 | 0.007721 | 61.3031 | 60.8945 | 53.8455 | 55.0785 | 60.1661 | 68.9348 | 60.8673 | 57.9767 | 123.1521 | 61.6531 | 123.0834 | 61.3301 | 61.416 | 122.8607 | 61.3709 | 122.6664 | 61.7361 | 61.7812 | 61.6673 | 61.7124
5555.0625 | 123.3353 | -61.3678 | 61.7752 | -0.49623 | -7.6047 | -6.5228 | -1.3024 | 7.361 | -0.52334 | -3.4323 | 61.8027 | 0.28526 | 61.7064 | -0.028522 | 0.039079 | 61.4975 | 0.012299 | 61.294 | 60.8716 | 53.7631 | 54.845 | 60.0654 | 68.7288 | 60.8445 | 57.9355 | 123.1705 | 61.6531 | 123.0742 | 61.3393 | 61.4069 | 122.8653 | 61.3801 | 122.6618 | 61.7636 | 61.7904 | 61.6673 | 61.6941
5556.1094 | 123.3032 | -61.3861 | 61.8118 | -0.51455 | -7.5635 | -6.5365 | -1.307 | 7.4297 | -0.54624 | -3.4826 | 61.7981 | 0.28069 | 61.711 | -0.023943 | 0.052814 | 61.4838 | 0.012299 | 61.2803 | 60.8716 | 53.8226 | 54.8496 | 60.0791 | 68.8158 | 60.8399 | 57.9035 | 123.1842 | 61.6668 | 123.0971 | 61.3622 | 61.4389 | 122.8699 | 61.3984 | 122.6664 | 61.7453 | 61.7858 | 61.6582 | 61.6987
5557.0625 | 123.3032 | -61.3815 | 61.8118 | -0.53286 | -7.6871 | -6.4633 | -1.3116 | 7.3976 | -0.55539 | -3.4826 | 61.7935 | 0.28526 | 61.7018 | -0.028522 | 0.052814 | 61.4929 | 0.012299 | 61.2803 | 60.8487 | 53.6944 | 54.9183 | 60.07 | 68.7792 | 60.8261 | 57.8989 | 123.175 | 61.6668 | 123.0834 | 61.353 | 61.4343 | 122.8744 | 61.3938 | 122.6618 | 61.7407 | 61.7812 | 61.649 | 61.6895
5558.0781 | 123.3078 | -61.3907 | 61.8118 | -0.55575 | -7.852 | -6.3534 | -1.2795 | 7.4022 | -0.58286 | -3.5147 | 61.7889 | 0.28069 | 61.7064 | -0.028522 | 0.052814 | 61.4929 | 0.007721 | 61.2757 | 60.8349 | 53.5387 | 55.0373 | 60.1112 | 68.7929 | 60.8078 | 57.876 | 123.1796 | 61.6714 | 123.0971 | 61.3622 | 61.4435 | 122.8836 | 61.3984 | 122.6664 | 61.7361 | 61.7812 | 61.6536 | 61.6987
5559.0625 | 123.2986 | -61.3907 | 61.7752 | -0.53744 | -7.9665 | -6.2389 | -1.2521 | 7.4709 | -0.55539 | -3.4414 | 61.8072 | 0.29442 | 61.7202 | -0.033101 | 0.043657 | 61.4929 | 0.012299 | 61.2894 | 60.8532 | 53.4242 | 55.1518 | 60.1386 | 68.8616 | 60.8353 | 57.9493 | 123.1979 | 61.6851 | 123.1108 | 61.3576 | 61.4343 | 122.8836 | 61.403 | 122.6801 | 61.7636 | 61.7949 | 61.6765 | 61.7079
5560.0781 | 123.3765 | -61.3541 | 61.7935 | -0.38177 | -7.9436 | -6.2847 | -1.2017 | 7.4709 | -0.40431 | -3.4689 | 61.7981 | 0.28526 | 61.7339 | -0.033101 | 0.048236 | 61.5021 | 0.007721 | 61.2894 | 60.9723 | 53.4105 | 55.0694 | 60.1524 | 68.8249 | 60.9498 | 57.8852 | 123.1521 | 61.6393 | 123.088 | 61.321 | 61.4023 | 122.8561 | 61.3618 | 122.6435 | 61.7498 | 61.7904 | 61.6857 | 61.7262
5561.0625 | 123.3078 | -61.3632 | 61.7935 | -0.39093 | -7.9939 | -6.3808 | -1.1788 | 7.4205 | -0.42262 | -3.5604 | 61.7935 | 0.28526 | 61.7339 | -0.033101 | 0.048236 | 61.4883 | 0.012299 | 61.2894 | 60.9723 | 53.3693 | 54.9824 | 60.1844 | 68.7837 | 60.9406 | 57.8028 | 123.1567 | 61.6485 | 123.0971 | 61.3301 | 61.4115 | 122.8516 | 61.3755 | 122.6526 | 61.7453 | 61.7812 | 61.6857 | 61.7216
5562.0938 | 123.3582 | -61.3358 | 61.7798 | -0.37719 | -8.0672 | -6.3534 | -1.2429 | 7.3427 | -0.39973 | -3.5696 | 61.8027 | 0.28984 | 61.7385 | -0.033101 | 0.057392 | 61.4929 | 0.016878 | 61.2894 | 60.9586 | 53.2686 | 54.9824 | 60.0929 | 68.6784 | 60.936 | 57.7662 | 123.1384 | 61.6256 | 123.0742 | 61.3027 | 61.3931 | 122.8287 | 61.3526 | 122.6252 | 61.7453 | 61.7858 | 61.6811 | 61.7216
5563.0625 | 123.3353 | -61.3586 | 61.8027 | -0.37261 | -7.8795 | -6.3763 | -1.2429 | 7.3518 | -0.38599 | -3.4139 | 61.7935 | 0.28526 | 61.7247 | -0.033101 | 0.052814 | 61.4883 | 0.007721 | 61.2848 | 60.986 | 53.4792 | 54.9824 | 60.1157 | 68.7105 | 60.9727 | 57.9447 | 123.1521 | 61.6439 | 123.0834 | 61.3255 | 61.4115 | 122.847 | 61.3664 | 122.6435 | 61.7407 | 61.7858 | 61.6719 | 61.717
5564.0781 | 123.2712 | -61.377 | 61.8027 | -0.5237 | -7.9527 | -6.4312 | -1.2704 | 7.3335 | -0.54166 | -3.4185 | 61.8027 | 0.28526 | 61.7064 | -0.023943 | 0.057392 | 61.4883 | 0.003143 | 61.2848 | 60.8533 | 53.4242 | 54.9458 | 60.1066 | 68.7105 | 60.8353 | 57.9584 | 123.1796 | 61.6622 | 123.0834 | 61.353 | 61.4343 | 122.8653 | 61.3801 | 122.6618 | 61.7453 | 61.7995 | 61.649 | 61.7033
5565.0625 | 123.3124 | -61.377 | 61.7569 | -0.59238 | -8.0718 | -6.3213 | -1.2704 | 7.242 | -0.62865 | -3.3865 | 61.8027 | 0.29442 | 61.711 | -0.028522 | 0.043657 | 61.4838 | 0.007721 | 61.2803 | 60.7846 | 53.3052 | 55.0556 | 60.1066 | 68.6189 | 60.7483 | 57.9905 | 123.1796 | 61.6714 | 123.088 | 61.3484 | 61.4206 | 122.8607 | 61.3847 | 122.6572 | 61.759 | 61.7949 | 61.6673 | 61.7033
5566.1094 | 123.2758 | -61.3724 | 61.8164 | -0.58322 | -8.1176 | -6.2526 | -1.1788 | 7.2694 | -0.61033 | -3.3498 | 61.7981 | 0.28526 | 61.7064 | -0.019364 | 0.043657 | 61.4929 | 0.007721 | 61.2894 | 60.7892 | 53.2548 | 55.1197 | 60.1936 | 68.6418 | 60.762 | 58.0225 | 123.1704 | 61.6576 | 123.0788 | 61.353 | 61.416 | 122.8653 | 61.3801 | 122.6618 | 61.7544 | 61.7904 | 61.6628 | 61.6987
5567.0625 | 123.3124 | -61.3815 | 61.7981 | -0.55575 | -8.3099 | -6.129 | -1.0231 | 7.3473 | -0.58286 | -3.3224 | 61.7981 | 0.28526 | 61.7156 | -0.028522 | 0.048236 | 61.4929 | 0.003143 | 61.2848 | 60.8258 | 53.0717 | 55.2525 | 60.3584 | 68.7288 | 60.7987 | 58.0592 | 123.1796 | 61.6668 | 123.0971 | 61.353 | 61.4298 | 122.8744 | 61.3847 | 122.6664 | 61.7498 | 61.7949 | 61.6673 | 61.7124
5568.0625 | 123.3261 | -61.3724 | 61.7798 | -0.53286 | -8.3282 | -6.01 | -1.0048 | 7.567 | -0.55539 | -3.3086 | 61.7981 | 0.28069 | 61.711 | -0.03768 | 0.048236 | 61.4975 | 0.012299 | 61.2848 | 60.8395 | 53.0442 | 55.3624 | 60.3676 | 68.9394 | 60.817 | 58.0637 | 123.1704 | 61.6531 | 123.0834 | 61.3347 | 61.4206 | 122.8699 | 61.3847 | 122.6572 | 61.7498 | 61.7858 | 61.6628 | 61.6987
5569.0781 | 123.262 | -61.3632 | 61.8073 | -0.60153 | -8.4839 | -6.0466 | -1.0094 | 7.5716 | -0.61949 | -3.2674 | 61.8027 | 0.28984 | 61.7385 | -0.028522 | 0.052814 | 61.4883 | 0.016878 | 61.2803 | 60.7617 | 52.8794 | 55.3166 | 60.3538 | 68.9348 | 60.7437 | 58.0958 | 123.1659 | 61.6531 | 123.1017 | 61.3347 | 61.416 | 122.8516 | 61.3801 | 122.6435 | 61.7498 | 61.7858 | 61.6857 | 61.7216
5570.0625 | 123.3353 | -61.377 | 61.7752 | -0.64274 | -8.4839 | -6.1061 | -1.0369 | 7.6403 | -0.66527 | -3.3773 | 61.8027 | 0.28984 | 61.7339 | -0.028522 | 0.052814 | 61.4929 | 0.007721 | 61.2848 | 60.7342 | 52.8931 | 55.2708 | 60.3401 | 69.0172 | 60.7117 | 57.9996 | 123.1796 | 61.6668 | 123.1108 | 61.3484 | 61.4298 | 122.8699 | 61.3847 | 122.6618 | 61.7498 | 61.7949 | 61.6811 | 61.7262
5571.0938 | 123.4497 | -61.3586 | 61.7386 | -0.62443 | -8.4198 | -6.1611 | -1.0231 | 7.5624 | -0.65154 | -3.4002 | 61.8072 | 0.29442 | 61.7385 | -0.028522 | 0.048236 | 61.4929 | 0.007721 | 61.2757 | 60.7342 | 52.9389 | 55.1976 | 60.3355 | 68.9211 | 60.7071 | 57.9584 | 123.1659 | 61.6531 | 123.0971 | 61.3301 | 61.4069 | 122.8516 | 61.3664 | 122.6343 | 61.759 | 61.7995 | 61.6902 | 61.7308
5572.0625 | 123.2895 | -61.377 | 61.7752 | -0.59238 | -8.3053 | -6.1565 | -1.1651 | 7.6219 | -0.61491 | -3.4506 | 61.7981 | 0.28984 | 61.7247 | -0.028522 | 0.052814 | 61.4883 | 0.012299 | 61.2665 | 60.7846 | 53.0717 | 55.2205 | 60.2119 | 68.9989 | 60.762 | 57.9264 | 123.175 | 61.6668 | 123.1017 | 61.3484 | 61.4298 | 122.8653 | 61.3893 | 122.6435 | 61.7453 | 61.7858 | 61.6719 | 61.7124
5573.0938 | 123.2712 | -61.3815 | 61.7981 | -0.61527 | -8.2687 | -6.1336 | -1.2704 | 7.5441 | -0.63322 | -3.5284 | 61.8027 | 0.28984 | 61.711 | -0.028522 | 0.048236 | 61.4883 | 0.007721 | 61.2711 | 60.7663 | 53.1129 | 55.2479 | 60.1112 | 68.9256 | 60.7483 | 57.8531 | 123.1842 | 61.6714 | 123.0925 | 61.353 | 61.4298 | 122.8699 | 61.3893 | 122.6526 | 61.7544 | 61.7949 | 61.6628 | 61.7033
5574.0625 | 123.3307 | -61.3678 | 61.7661 | -0.67021 | -8.3373 | -6.01 | -1.1971 | 7.5121 | -0.69274 | -3.3315 | 61.7981 | 0.28526 | 61.7018 | -0.033101 | 0.048236 | 61.4975 | 0.003143 | 61.2711 | 60.6976 | 53.0305 | 55.3578 | 60.1707 | 68.8799 | 60.6751 | 58.0363 | 123.1659 | 61.6531 | 123.0696 | 61.3347 | 61.416 | 122.8653 | 61.3709 | 122.6389 | 61.7498 | 61.7949 | 61.6536 | 61.6987
5575.0781 | 123.317 | -61.3861 | 61.8256 | -0.70684 | -8.5617 | -6.0329 | -1.101 | 7.4526 | -0.72937 | -3.3727 | 61.7981 | 0.28526 | 61.7064 | -0.033101 | 0.048236 | 61.4929 | 0.016878 | 61.2803 | 60.6793 | 52.8244 | 55.3532 | 60.2851 | 68.8387 | 60.6567 | 58.0134 | 123.1842 | 61.6714 | 123.0925 | 61.353 | 61.4343 | 122.879 | 61.403 | 122.6664 | 61.7498 | 61.7812 | 61.6582 | 61.6895
5576.0625 | 123.3124 | -61.409 | 61.7752 | -0.63358 | -8.5022 | -5.9276 | -1.101 | 7.48 | -0.65154 | -3.3819 | 61.8027 | 0.28984 | 61.7064 | -0.033101 | 0.048236 | 61.4838 | -0.001436 | 61.2711 | 60.7754 | 52.9068 | 55.4814 | 60.308 | 68.889 | 60.7575 | 58.0271 | 123.2116 | 61.6988 | 123.1154 | 61.3759 | 61.4572 | 122.8928 | 61.4076 | 122.6801 | 61.7544 | 61.8041 | 61.6582 | 61.7079
5577.0781 | 123.2849 | -61.377 | 61.7935 | -0.62443 | -8.2824 | -5.7215 | -1.1788 | 7.5212 | -0.6378 | -3.5055 | 61.7935 | 0.28069 | 61.7293 | -0.019364 | 0.048236 | 61.4929 | 0.007721 | 61.2711 | 60.7525 | 53.0946 | 55.6554 | 60.1982 | 68.8982 | 60.7392 | 57.8714 | 123.1704 | 61.6576 | 123.1063 | 61.3576 | 61.4252 | 122.8699 | 61.3847 | 122.6481 | 61.7453 | 61.7858 | 61.6811 | 61.7216
5578.0625 | 123.317 | -61.3541 | 61.8027 | -0.59696 | -8.3831 | -5.8268 | -1.2337 | 7.3793 | -0.61491 | -3.5559 | 61.8027 | 0.28984 | 61.7476 | -0.023943 | 0.043657 | 61.4929 | 0.007721 | 61.2757 | 60.7571 | 52.9709 | 55.5272 | 60.1203 | 68.7334 | 60.7392 | 57.7982 | 123.1567 | 61.6439 | 123.1017 | 61.3301 | 61.3977 | 122.847 | 61.3618 | 122.6297 | 61.759 | 61.7949 | 61.704 | 61.7399
5579.0938 | 123.3215 | -61.3815 | 61.7889 | -0.67479 | -8.3282 | -5.8863 | -1.2841 | 7.3244 | -0.7019 | -3.6154 | 61.8027 | 0.28984 | 61.743 | -0.023943 | 0.052814 | 61.4838 | 0.016878 | 61.2665 | 60.7067 | 53.0534 | 55.4952 | 60.0974 | 68.7059 | 60.6796 | 57.7662 | 123.1842 | 61.6714 | 123.1246 | 61.3576 | 61.4343 | 122.8653 | 61.3984 | 122.6481 | 61.7498 | 61.7858 | 61.6902 | 61.7262
5580.0625 | 123.3215 | -61.3861 | 61.7706 | -0.74346 | -8.2915 | -6.1382 | -1.4123 | 7.2374 | -0.766 | -3.6932 | 61.8072 | 0.28069 | 61.7476 | -0.03768 | 0.043657 | 61.4792 | 0.007721 | 61.2619 | 60.6426 | 53.0946 | 55.2479 | 59.9738 | 68.6235 | 60.6201 | 57.6929 | 123.1933 | 61.6668 | 123.1337 | 61.3484 | 61.4298 | 122.8653 | 61.3938 | 122.648 | 61.7636 | 61.7995 | 61.704 | 61.7399
5581.0938 | 123.3582 | -61.3724 | 61.7706 | -0.77094 | -8.3602 | -6.3717 | -1.4627 | 7.242 | -0.79805 | -3.7298 | 61.8027 | 0.28526 | 61.7247 | -0.028522 | 0.043657 | 61.4746 | 0.007721 | 61.2574 | 60.6014 | 53.0121 | 55.0007 | 59.9097 | 68.6143 | 60.5743 | 57.6425 | 123.175 | 61.6576 | 123.0971 | 61.3439 | 61.416 | 122.847 | 61.3801 | 122.6297 | 61.759 | 61.7949 | 61.6811 | 61.717
5582.0625 | 123.2986 | -61.3678 | 61.7981 | -0.78009 | -7.9481 | -6.477 | -1.4077 | 7.1504 | -0.79805 | -3.6749 | 61.8072 | 0.28984 | 61.7064 | -0.033101 | 0.043657 | 61.4792 | 0.007721 | 61.2619 | 60.5877 | 53.4197 | 54.8908 | 59.9601 | 68.5182 | 60.5698 | 57.6929 | 123.175 | 61.6576 | 123.0742 | 61.3347 | 61.4115 | 122.847 | 61.3755 | 122.6297 | 61.7636 | 61.7995 | 61.6628 | 61.6987
5583.0781 | 123.2803 | -61.3815 | 61.8164 | -0.80756 | -8.0351 | -6.5365 | -1.4947 | 6.8986 | -0.81636 | -3.6428 | 61.8072 | 0.28984 | 61.711 | -0.023943 | 0.043657 | 61.4792 | 0.012299 | 61.2665 | 60.574 | 53.3464 | 54.845 | 59.8868 | 68.2802 | 60.5652 | 57.7387 | 123.1888 | 61.6714 | 123.0925 | 61.3576 | 61.4252 | 122.8607 | 61.3938 | 122.6481 | 61.7636 | 61.7949 | 61.6673 | 61.6987
5584.0625 | 123.4268 | -61.3495 | 61.7615 | -0.73431 | -7.9848 | -6.6464 | -1.4947 | 7.0634 | -0.75226 | -3.6703 | 61.8027 | 0.28984 | 61.7156 | -0.023943 | 0.048236 | 61.4792 | 0.007721 | 61.2528 | 60.6152 | 53.3647 | 54.7031 | 59.8548 | 68.4129 | 60.5972 | 57.6792 | 123.1521 | 61.6393 | 123.0651 | 61.3255 | 61.3977 | 122.8287 | 61.3572 | 122.6023 | 61.7544 | 61.7949 | 61.6673 | 61.7079
5585.0781 | 123.3536 | -61.3541 | 61.7706 | -0.76178 | -7.8749 | -6.7609 | -1.5359 | 7.1092 | -0.77973 | -3.8122 | 61.8072 | 0.29442 | 61.7293 | -0.028522 | 0.052814 | 61.4792 | 0.007721 | 61.2665 | 60.5923 | 53.4792 | 54.5932 | 59.8181 | 68.4633 | 60.5743 | 57.5418 | 123.1613 | 61.6485 | 123.0834 | 61.3255 | 61.4069 | 122.8332 | 61.3618 | 122.6206 | 61.7544 | 61.7995 | 61.6765 | 61.7216
5586.0625 | 123.3902 | -61.3403 | 61.7386 | -0.83045 | -7.8016 | -6.7975 | -1.4856 | 7.0772 | -0.84841 | -3.7344 | 61.8164 | 0.28984 | 61.7339 | -0.03768 | 0.048236 | 61.4746 | 0.012299 | 61.2619 | 60.5099 | 53.5387 | 54.5428 | 59.8548 | 68.4175 | 60.4919 | 57.6059 | 123.1567 | 61.6302 | 123.0742 | 61.3027 | 61.3886 | 122.8149 | 61.3526 | 122.6023 | 61.7682 | 61.8041 | 61.6857 | 61.7216
5587.0781 | 123.2117 | -61.3586 | 61.8164 | -0.83045 | -7.9527 | -6.77 | -1.4535 | 7.274 | -0.85299 | -3.7207 | 61.8164 | 0.28526 | 61.7522 | -0.028522 | 0.048236 | 61.4792 | 0.016878 | 61.2619 | 60.5282 | 53.4059 | 54.5886 | 59.9051 | 68.6327 | 60.5057 | 57.638 | 123.175 | 61.6439 | 123.1108 | 61.3301 | 61.4069 | 122.8378 | 61.3755 | 122.6206 | 61.7682 | 61.7995 | 61.704 | 61.7353
5588.0625 | 123.262 | -61.3861 | 61.7844 | -0.88082 | -8.2458 | -6.7746 | -1.4581 | 7.2145 | -0.90793 | -3.6749 | 61.821 | 0.28984 | 61.7522 | -0.028522 | 0.043657 | 61.4746 | 0.007721 | 61.2619 | 60.5053 | 53.1403 | 54.6115 | 59.928 | 68.6006 | 60.4782 | 57.7112 | 123.2071 | 61.676 | 123.1383 | 61.3576 | 61.4298 | 122.8607 | 61.3938 | 122.648 | 61.7773 | 61.8132 | 61.7085 | 61.7445
5589.0938 | 123.3673 | -61.3312 | 61.734 | -0.90829 | -8.3282 | -6.77 | -1.5725 | 7.0772 | -0.92624 | -3.6795 | 61.8255 | 0.28984 | 61.7476 | -0.033101 | 0.052814 | 61.47 | 0.016878 | 61.2574 | 60.4229 | 53.003 | 54.5612 | 59.7586 | 68.4083 | 60.4049 | 57.6517 | 123.1567 | 61.621 | 123.0788 | 61.2981 | 61.384 | 122.8012 | 61.3481 | 122.5885 | 61.7727 | 61.8087 | 61.6948 | 61.7308
5590.0625 | 123.2941 | -61.3678 | 61.7981 | -0.88082 | -8.406 | -6.7105 | -1.5863 | 7.0405 | -0.89419 | -3.8031 | 61.821 | 0.28984 | 61.7339 | -0.028522 | 0.043657 | 61.47 | 0.003143 | 61.2619 | 60.487 | 52.9618 | 54.6573 | 59.7815 | 68.4083 | 60.4736 | 57.5647 | 123.1888 | 61.6576 | 123.1017 | 61.3393 | 61.4115 | 122.8378 | 61.3709 | 122.6297 | 61.7773 | 61.8178 | 61.6902 | 61.7308
5591.1094 | 123.2986 | -61.3586 | 61.8256 | -0.8625 | -8.5113 | -6.5182 | -1.5176 | 7.0314 | -0.8713 | -3.9221 | 61.8072 | 0.28526 | 61.7247 | -0.028522 | 0.057392 | 61.47 | 0.007721 | 61.2711 | 60.4961 | 52.8473 | 54.8404 | 59.841 | 68.39 | 60.4873 | 57.4365 | 123.1659 | 61.6439 | 123.0834 | 61.3301 | 61.416 | 122.8287 | 61.3664 | 122.6297 | 61.7498 | 61.7995 | 61.6673 | 61.717
5592.0625 | 123.2529 | -61.3632 | 61.7844 | -0.80298 | -8.2412 | -6.4358 | -1.4993 | 7.1001 | -0.83467 | -3.8992 | 61.8118 | 0.28526 | 61.7202 | -0.03768 | 0.052814 | 61.47 | 0.007721 | 61.2574 | 60.5602 | 53.122 | 54.9274 | 59.8639 | 68.4633 | 60.5285 | 57.464 | 123.175 | 61.6485 | 123.0834 | 61.3255 | 61.416 | 122.8332 | 61.3709 | 122.6206 | 61.759 | 61.8041 | 61.6673 | 61.7124
5593.0781 | 123.3215 | -61.3586 | 61.7844 | -0.74346 | -8.4152 | -6.3808 | -1.426 | 7.2053 | -0.77973 | -3.9999 | 61.8072 | 0.29442 | 61.7202 | -0.028522 | 0.052814 | 61.47 | 0.007721 | 61.2619 | 60.6152 | 52.9435 | 54.9778 | 59.9326 | 68.564 | 60.5789 | 57.3587 | 123.1659 | 61.6531 | 123.0788 | 61.3301 | 61.4115 | 122.8287 | 61.3664 | 122.6206 | 61.7544 | 61.7995 | 61.6673 | 61.7124
5594.0625 | 123.2391 | -61.3953 | 61.7981 | -0.72057 | -8.5434 | -6.2068 | -1.3665 | 7.242 | -0.74768 | -3.7939 | 61.8118 | 0.28984 | 61.7202 | -0.033101 | 0.039079 | 61.4792 | 0.012299 | 61.2619 | 60.6747 | 52.8519 | 55.1884 | 60.0287 | 68.6372 | 60.6476 | 57.6013 | 123.2071 | 61.6851 | 123.1154 | 61.3622 | 61.4343 | 122.8744 | 61.4076 | 122.6572 | 61.7727 | 61.7995 | 61.6811 | 61.7079
5595.0938 | 123.2803 | -61.3632 | 61.8118 | -0.68852 | -8.5342 | -6.0786 | -1.3574 | 7.187 | -0.72021 | -3.8214 | 61.8118 | 0.28984 | 61.743 | -0.023943 | 0.048236 | 61.4883 | 0.012299 | 61.2665 | 60.6747 | 52.829 | 55.2846 | 60.0059 | 68.5503 | 60.643 | 57.5418 | 123.175 | 61.6531 | 123.1063 | 61.3393 | 61.4115 | 122.8516 | 61.3755 | 122.6297 | 61.7636 | 61.7995 | 61.6948 | 61.7308
5596.0625 | 123.3856 | -61.3632 | 61.7386 | -0.6931 | -8.6258 | -6.1702 | -1.4306 | 7.0634 | -0.72479 | -3.7344 | 61.821 | 0.28984 | 61.7522 | -0.028522 | 0.052814 | 61.4746 | 0.012299 | 61.2528 | 60.6701 | 52.7374 | 55.193 | 59.9326 | 68.4267 | 60.6384 | 57.6288 | 123.1842 | 61.6531 | 123.1154 | 61.3347 | 61.416 | 122.8378 | 61.3755 | 122.616 | 61.7682 | 61.8087 | 61.6994 | 61.7399
5597.0781 | 123.2895 | -61.3724 | 61.7935 | -0.77551 | -8.0306 | -6.3579 | -1.426 | 7.2694 | -0.79347 | -3.7573 | 61.8072 | 0.28526 | 61.7476 | -0.042259 | 0.048236 | 61.4838 | 0.007721 | 61.2711 | 60.5969 | 53.3418 | 55.0144 | 59.9463 | 68.6418 | 60.5789 | 57.6151 | 123.1796 | 61.6576 | 123.12 | 61.3301 | 61.4206 | 122.8561 | 61.3801 | 122.6435 | 61.759 | 61.7995 | 61.6994 | 61.7399
5598.0625 | 123.2712 | -61.3953 | 61.7935 | -0.67479 | -7.6917 | -6.3763 | -1.2704 | 7.242 | -0.7019 | -3.7207 | 61.8027 | 0.28526 | 61.7339 | -0.028522 | 0.048236 | 61.4838 | 0.003143 | 61.2665 | 60.7205 | 53.7035 | 55.019 | 60.1249 | 68.6372 | 60.6934 | 57.6746 | 123.1979 | 61.6805 | 123.1292 | 61.3667 | 61.4435 | 122.879 | 61.3984 | 122.6618 | 61.7544 | 61.7995 | 61.6857 | 61.7308
5599.0938 | 123.3261 | -61.3632 | 61.8164 | -0.62443 | -7.4353 | -6.4449 | -1.2795 | 7.2237 | -0.64696 | -3.7985 | 61.8027 | 0.29442 | 61.7064 | -0.028522 | 0.06197 | 61.4838 | 0.003143 | 61.2848 | 60.7388 | 53.9279 | 54.9183 | 60.0837 | 68.5869 | 60.7163 | 57.5647 | 123.1659 | 61.6576 | 123.0696 | 61.3347 | 61.4252 | 122.847 | 61.3664 | 122.6481 | 61.7407 | 61.7995 | 61.6445 | 61.7033
5600.0625 | 123.2895 | -61.3998 | 61.7844 | -0.65648 | -7.6688 | -6.4816 | -1.3024 | 7.3015 | -0.68359 | -3.7573 | 61.7935 | 0.28526 | 61.7064 | -0.023943 | 0.052814 | 61.4929 | 0.012299 | 61.2803 | 60.7434 | 53.731 | 54.9183 | 60.0974 | 68.7013 | 60.7163 | 57.6425 | 123.1933 | 61.6851 | 123.1063 | 61.3759 | 61.4527 | 122.8928 | 61.4121 | 122.6801 | 61.7407 | 61.7812 | 61.6536 | 61.6941
5601.1094 | 123.3078 | -61.3403 | 61.8576 | -0.83961 | -8.2183 | -6.4358 | -1.3848 | 7.274 | -0.8713 | -3.8122 | 61.8118 | 0.28984 | 61.7247 | -0.019364 | 0.057392 | 61.4792 | 0.007721 | 61.2711 | 60.5007 | 53.122 | 54.9046 | 59.9555 | 68.6143 | 60.469 | 57.5281 | 123.1521 | 61.6302 | 123.0651 | 61.321 | 61.3977 | 122.8195 | 61.3481 | 122.6114 | 61.7544 | 61.8041 | 61.6673 | 61.717
5602.0625 | 123.262 | -61.377 | 61.7798 | -0.85792 | -8.3099 | -6.4633 | -1.4489 | 7.1962 | -0.88504 | -3.8214 | 61.821 | 0.29442 | 61.7522 | -0.028522 | 0.043657 | 61.4792 | 0.012299 | 61.2574 | 60.519 | 53.0671 | 54.9137 | 59.928 | 68.5731 | 60.4919 | 57.5556 | 123.1979 | 61.6714 | 123.1292 | 61.3484 | 61.4206 | 122.8561 | 61.3893 | 122.6343 | 61.7773 | 61.8087 | 61.7085 | 61.7399
5603.0781 | 123.3627 | -61.3358 | 61.8256 | -0.79841 | -8.1679 | -6.5045 | -1.4764 | 7.1504 | -0.8301 | -3.8031 | 61.8164 | 0.28984 | 61.7293 | -0.019364 | 0.057392 | 61.4746 | 0.003143 | 61.2619 | 60.5373 | 53.1678 | 54.8313 | 59.8594 | 68.4862 | 60.5057 | 57.5327 | 123.1521 | 61.6256 | 123.0651 | 61.3164 | 61.3931 | 122.8104 | 61.3389 | 122.5977 | 61.759 | 61.8132 | 61.6719 | 61.7262
5604.0625 | 123.3032 | -61.3998 | 61.7889 | -0.70684 | -7.8382 | -6.4678 | -1.394 | 7.1092 | -0.72937 | -3.858 | 61.8072 | 0.28526 | 61.7202 | -0.023943 | 0.048236 | 61.4746 | 0.007721 | 61.2757 | 60.693 | 53.5616 | 54.932 | 60.0059 | 68.5091 | 60.6705 | 57.5418 | 123.2071 | 61.6851 | 123.12 | 61.3759 | 61.4481 | 122.8744 | 61.4076 | 122.6755 | 61.759 | 61.7995 | 61.6719 | 61.7124
5605.0938 | 123.3078 | -61.3678 | 61.8164 | -0.70684 | -8.2274 | -6.3534 | -1.4123 | 7.1504 | -0.73853 | -3.8626 | 61.8072 | 0.28984 | 61.7156 | -0.033101 | 0.048236 | 61.4838 | 0.012299 | 61.2665 | 60.661 | 53.1404 | 55.0144 | 59.9555 | 68.5182 | 60.6293 | 57.5052 | 123.175 | 61.6576 | 123.0834 | 61.3347 | 61.416 | 122.8516 | 61.3801 | 122.6343 | 61.759 | 61.7949 | 61.6673 | 61.7033
5606.0625 | 123.4039 | -61.3678 | 61.7477 | -0.63816 | -8.287 | -6.2893 | -1.3619 | 7.361 | -0.66069 | -3.8351 | 61.7981 | 0.28984 | 61.7156 | -0.023943 | 0.052814 | 61.4792 | 0.007721 | 61.2665 | 60.7296 | 53.0808 | 55.0785 | 60.0059 | 68.7288 | 60.7071 | 57.5327 | 123.1659 | 61.6576 | 123.0834 | 61.3439 | 61.4206 | 122.847 | 61.3755 | 122.6343 | 61.7453 | 61.7904 | 61.6628 | 61.7079
5607.0781 | 123.381 | -61.3495 | 61.7889 | -0.64732 | -8.3328 | -6.4312 | -1.4581 | 7.3702 | -0.68817 | -3.7573 | 61.8027 | 0.28526 | 61.7339 | -0.028522 | 0.052814 | 61.4792 | 0.012299 | 61.2711 | 60.7022 | 53.0167 | 54.9183 | 59.8914 | 68.7196 | 60.6613 | 57.5922 | 123.1521 | 61.6348 | 123.0834 | 61.321 | 61.4023 | 122.8287 | 61.3618 | 122.6206 | 61.7498 | 61.7904 | 61.6811 | 61.7216
5608.0625 | 123.2758 | -61.3953 | 61.7752 | -0.77551 | -8.0168 | -6.5136 | -1.4856 | 7.4297 | -0.81178 | -3.8214 | 61.8164 | 0.28526 | 61.7522 | -0.019364 | 0.043657 | 61.4838 | 0.007721 | 61.2619 | 60.6198 | 53.3784 | 54.8816 | 59.9097 | 68.8249 | 60.5835 | 57.5739 | 123.2117 | 61.6805 | 123.1475 | 61.3759 | 61.4389 | 122.879 | 61.403 | 122.6572 | 61.7727 | 61.8087 | 61.7085 | 61.7445
5609.0781 | 123.3765 | -61.3358 | 61.7752 | -0.8213 | -7.8795 | -6.738 | -1.4764 | 7.3839 | -0.85299 | -3.8992 | 61.821 | 0.27611 | 61.7522 | -0.028522 | 0.048236 | 61.4746 | 0.003143 | 61.2619 | 60.5145 | 53.4563 | 54.5978 | 59.8594 | 68.7196 | 60.4828 | 57.4365 | 123.1567 | 61.6119 | 123.088 | 61.3072 | 61.384 | 122.8104 | 61.3389 | 122.5977 | 61.7727 | 61.8178 | 61.704 | 61.7491
5610.0625 | 123.2803 | -61.377 | 61.7889 | -0.71599 | -7.9115 | -6.6968 | -1.4581 | 7.4709 | -0.75226 | -3.8718 | 61.8164 | 0.28526 | 61.743 | -0.028522 | 0.048236 | 61.4838 | 0.007721 | 61.2574 | 60.661 | 53.4654 | 54.6802 | 59.9189 | 68.8478 | 60.6247 | 57.5052 | 123.1933 | 61.6622 | 123.12 | 61.3484 | 61.4252 | 122.8607 | 61.3847 | 122.6343 | 61.7682 | 61.8087 | 61.6948 | 61.7353
5611.1094 | 123.2895 | -61.3861 | 61.7981 | -0.73889 | -7.9665 | -6.6739 | -1.4398 | 7.4663 | -0.766 | -3.8351 | 61.8072 | 0.299 | 61.7293 | -0.028522 | 0.052814 | 61.4792 | 0.012299 | 61.2574 | 60.6472 | 53.4197 | 54.7122 | 59.9463 | 68.8524 | 60.6201 | 57.551 | 123.1933 | 61.6851 | 123.1154 | 61.3576 | 61.4389 | 122.8653 | 61.3984 | 122.6435 | 61.7544 | 61.7949 | 61.6765 | 61.717
5612.0625 | 123.2849 | -61.3586 | 61.7798 | -0.85335 | -7.9619 | -6.5502 | -1.4352 | 7.4846 | -0.89419 | -3.8763 | 61.8118 | 0.28984 | 61.7202 | -0.023943 | 0.039079 | 61.4792 | 0.012299 | 61.2574 | 60.5053 | 53.3968 | 54.8084 | 59.9235 | 68.8432 | 60.4645 | 57.4823 | 123.1705 | 61.6485 | 123.0788 | 61.3347 | 61.3977 | 122.8378 | 61.3709 | 122.616 | 61.7727 | 61.7995 | 61.6811 | 61.7079
5613.0781 | 123.3261 | -61.3861 | 61.8164 | -0.9907 | -8.3557 | -6.509 | -1.5084 | 7.3106 | -0.98118 | -3.9084 | 61.8072 | 0.28526 | 61.7247 | -0.028522 | 0.057392 | 61.47 | 0.012299 | 61.2665 | 60.3954 | 53.0305 | 54.8771 | 59.8777 | 68.6967 | 60.4049 | 57.4777 | 123.1933 | 61.6714 | 123.1108 | 61.3576 | 61.4435 | 122.8561 | 61.3984 | 122.6526 | 61.7498 | 61.7949 | 61.6673 | 61.7124
5614.0625 | 123.2849 | -61.3632 | 61.7935 | -0.93576 | -8.3465 | -6.4541 | -1.4123 | 7.274 | -0.9354 | -3.9175 | 61.8164 | 0.28984 | 61.7247 | -0.03768 | 0.043657 | 61.4746 | 0.012299 | 61.2574 | 60.4275 | 53.0167 | 54.9091 | 59.9509 | 68.6372 | 60.4278 | 57.4457 | 123.1796 | 61.6531 | 123.088 | 61.3255 | 61.4069 | 122.8378 | 61.3755 | 122.6206 | 61.7727 | 61.8041 | 61.6811 | 61.7124
5615.0938 | 123.2574 | -61.3724 | 61.8027 | -0.97238 | -8.4014 | -6.5594 | -1.3803 | 7.4938 | -0.99492 | -3.9633 | 61.8164 | 0.29442 | 61.7339 | -0.023943 | 0.048236 | 61.4746 | 0.012299 | 61.2619 | 60.4 | 52.9709 | 54.813 | 59.9921 | 68.8661 | 60.3775 | 57.4091 | 123.1888 | 61.6668 | 123.1063 | 61.3484 | 61.4206 | 122.847 | 61.3847 | 122.6343 | 61.7682 | 61.8041 | 61.6857 | 61.7216
5616.0625 | 123.3536 | -61.3312 | 61.7523 | -0.99985 | -8.548 | -6.6556 | -1.4077 | 7.5075 | -1.027 | -4.0228 | 61.821 | 0.29442 | 61.7614 | -0.033101 | 0.048236 | 61.4746 | 0.012299 | 61.2528 | 60.3313 | 52.7832 | 54.6756 | 59.9235 | 68.8387 | 60.3042 | 57.3083 | 123.1521 | 61.6256 | 123.0925 | 61.2981 | 61.3794 | 122.8058 | 61.3435 | 122.584 | 61.7727 | 61.8087 | 61.7131 | 61.7491
5617.0938 | 123.2758 | -61.3541 | 61.8576 | -1.0548 | -8.7906 | -6.6556 | -1.4627 | 7.2053 | -1.0819 | -4.0045 | 61.8255 | 0.28984 | 61.7659 | -0.028522 | 0.043657 | 61.4654 | 0.016878 | 61.2619 | 60.2993 | 52.5634 | 54.6985 | 59.8914 | 68.5594 | 60.2722 | 57.3495 | 123.1796 | 61.6439 | 123.12 | 61.3255 | 61.3977 | 122.8195 | 61.3709 | 122.616 | 61.7819 | 61.8087 | 61.7223 | 61.7491
5618.0625 | 123.3215 | -61.3495 | 61.7981 | -1.064 | -8.8456 | -6.6647 | -1.5222 | 7.1916 | -1.0773 | -3.9954 | 61.821 | 0.28984 | 61.7568 | -0.033101 | 0.043657 | 61.4654 | 0.007721 | 61.2665 | 60.2855 | 52.5039 | 54.6848 | 59.8273 | 68.5411 | 60.2722 | 57.3541 | 123.1705 | 61.6393 | 123.1063 | 61.3164 | 61.3931 | 122.8149 | 61.3572 | 122.616 | 61.7773 | 61.8132 | 61.7131 | 61.7491
5619.0781 | 123.2758 | -61.3495 | 61.8256 | -1.0594 | -8.9646 | -6.6647 | -1.5039 | 7.187 | -1.0819 | -4.0366 | 61.8164 | 0.28984 | 61.7339 | -0.023943 | 0.048236 | 61.4654 | 0.007721 | 61.2574 | 60.2901 | 52.3849 | 54.6848 | 59.8456 | 68.5365 | 60.2676 | 57.3129 | 123.1659 | 61.6393 | 123.0834 | 61.3255 | 61.3977 | 122.8149 | 61.3572 | 122.6069 | 61.7682 | 61.8087 | 61.6857 | 61.7262
5620.0625 | 123.2849 | -61.3861 | 61.7935 | -1.064 | -9.0379 | -6.4633 | -1.3345 | 7.2374 | -1.0865 | -4.0412 | 61.8255 | 0.28069 | 61.7339 | -0.033101 | 0.052814 | 61.47 | 0.003143 | 61.2528 | 60.3222 | 52.3482 | 54.9229 | 60.0516 | 68.6235 | 60.2996 | 57.345 | 123.2117 | 61.6668 | 123.12 | 61.353 | 61.4389 | 122.8561 | 61.3893 | 122.6389 | 61.7727 | 61.8224 | 61.6811 | 61.7308
5621.1094 | 123.381 | -61.3495 | 61.8118 | -1.0411 | -9.189 | -5.9962 | -1.2887 | 7.2923 | -1.0453 | -3.9313 | 61.8301 | 0.299 | 61.7522 | -0.028522 | 0.06197 | 61.4746 | 0.016878 | 61.2619 | 60.3084 | 52.1605 | 55.3533 | 60.0608 | 68.6418 | 60.3042 | 57.4182 | 123.1796 | 61.6485 | 123.1017 | 61.321 | 61.4115 | 122.8241 | 61.3664 | 122.6114 | 61.7682 | 61.8132 | 61.6902 | 61.7353
5622.0625 | 123.3124 | -61.3678 | 61.8027 | -0.87624 | -9.0928 | -5.9138 | -1.2749 | 7.2511 | -0.88504 | -3.9313 | 61.8255 | 0.29442 | 61.743 | -0.033101 | 0.048236 | 61.4654 | 0.003143 | 61.2665 | 60.4916 | 52.275 | 55.454 | 60.0929 | 68.6189 | 60.4828 | 57.4365 | 123.1933 | 61.6622 | 123.1108 | 61.3347 | 61.416 | 122.8332 | 61.3709 | 122.6343 | 61.7773 | 61.8224 | 61.6948 | 61.7399
5623.0781 | 123.2666 | -61.3907 | 61.8073 | -0.75262 | -8.9326 | -5.923 | -1.2154 | 7.4068 | -0.78431 | -3.9359 | 61.8118 | 0.28984 | 61.7156 | -0.028522 | 0.057392 | 61.4792 | 0.007721 | 61.2848 | 60.6381 | 52.4581 | 55.4677 | 60.1753 | 68.7975 | 60.6064 | 57.4548 | 123.2025 | 61.6805 | 123.1063 | 61.3622 | 61.4481 | 122.8699 | 61.3984 | 122.6755 | 61.7544 | 61.8041 | 61.6582 | 61.7079
5624.0625 | 123.2986 | -61.3632 | 61.7844 | -0.73889 | -9.102 | -5.9367 | -1.3345 | 7.068 | -0.766 | -3.9496 | 61.8118 | 0.28984 | 61.7293 | -0.028522 | 0.052814 | 61.47 | 0.007721 | 61.2665 | 60.6243 | 52.2612 | 55.4265 | 60.0288 | 68.4312 | 60.5972 | 57.4136 | 123.175 | 61.6531 | 123.0925 | 61.3347 | 61.416 | 122.8332 | 61.3709 | 122.6297 | 61.759 | 61.8041 | 61.6765 | 61.7216
5625.0938 | 123.2712 | -61.3815 | 61.8118 | -0.72973 | -8.9921 | -5.9184 | -1.2704 | 7.2923 | -0.71106 | -3.8809 | 61.8164 | 0.29442 | 61.7522 | -0.033101 | 0.048236 | 61.4792 | 0.007721 | 61.2665 | 60.6518 | 52.3894 | 55.4631 | 60.1112 | 68.6739 | 60.6705 | 57.5006 | 123.1979 | 61.676 | 123.1337 | 61.3484 | 61.4298 | 122.8607 | 61.3893 | 122.6481 | 61.7682 | 61.8087 | 61.704 | 61.7445
5626.0625 | 123.3215 | -61.3724 | 61.7798 | -0.71142 | -8.9921 | -5.9276 | -1.1971 | 7.3106 | -0.69274 | -3.7985 | 61.8118 | 0.28526 | 61.7385 | -0.033101 | 0.057392 | 61.4792 | 0.007721 | 61.2665 | 60.661 | 52.3803 | 55.4448 | 60.1753 | 68.683 | 60.6796 | 57.5739 | 123.1842 | 61.6576 | 123.1108 | 61.3393 | 61.4298 | 122.8516 | 61.3801 | 122.6389 | 61.7544 | 61.8041 | 61.6811 | 61.7308
5627.0781 | 123.2712 | -61.3815 | 61.7889 | -0.66563 | -8.9921 | -5.8955 | -1.2337 | 6.7979 | -0.65612 | -3.826 | 61.8118 | 0.28984 | 61.7202 | -0.023943 | 0.048236 | 61.4792 | 0.007721 | 61.2665 | 60.7159 | 52.3894 | 55.486 | 60.1478 | 68.1794 | 60.7254 | 57.5556 | 123.1933 | 61.6714 | 123.1017 | 61.3576 | 61.4298 | 122.8607 | 61.3893 | 122.6481 | 61.7636 | 61.8041 | 61.6719 | 61.7124
5628.0625 | 123.317 | -61.3815 | 61.7661 | -0.59696 | -8.8593 | -5.9138 | -1.2383 | 6.5415 | -0.62407 | -3.8351 | 61.821 | 0.299 | 61.7293 | -0.028522 | 0.048236 | 61.4746 | 0.012299 | 61.2574 | 60.7846 | 52.5222 | 55.4677 | 60.1432 | 67.9231 | 60.7575 | 57.5464 | 123.2025 | 61.6805 | 123.1108 | 61.353 | 61.4298 | 122.8561 | 61.3938 | 122.6389 | 61.7727 | 61.8087 | 61.6811 | 61.717
5629.0938 | 123.2895 | -61.3632 | 61.7889 | -0.56033 | -8.754 | -6.1427 | -1.2566 | 6.331 | -0.58286 | -3.8489 | 61.8255 | 0.28984 | 61.7568 | -0.033101 | 0.048236 | 61.47 | 0.007721 | 61.2574 | 60.8029 | 52.6092 | 55.2205 | 60.1066 | 67.6942 | 60.7804 | 57.5144 | 123.1888 | 61.6531 | 123.12 | 61.3301 | 61.4115 | 122.8332 | 61.3709 | 122.6206 | 61.7773 | 61.8178 | 61.7085 | 61.7491
5630.0625 | 123.3078 | -61.3724 | 61.7752 | -0.62443 | -8.8044 | -6.0329 | -1.3207 | 6.6377 | -0.64696 | -3.8489 | 61.821 | 0.28984 | 61.7614 | -0.023943 | 0.048236 | 61.4746 | 0.007721 | 61.2574 | 60.7479 | 52.568 | 55.3395 | 60.0516 | 68.0101 | 60.7254 | 57.5235 | 123.1933 | 61.6622 | 123.1337 | 61.3484 | 61.4206 | 122.847 | 61.3801 | 122.6297 | 61.7727 | 61.8132 | 61.7131 | 61.7536
5631.0938 | 123.2941 | -61.3724 | 61.7752 | -0.57864 | -8.841 | -6.2068 | -1.3574 | 7.0314 | -0.60118 | -3.7619 | 61.8118 | 0.28526 | 61.7156 | -0.023943 | 0.043657 | 61.47 | 0.012299 | 61.2711 | 60.7937 | 52.5314 | 55.1655 | 60.015 | 68.4038 | 60.7712 | 57.6105 | 123.1842 | 61.6576 | 123.088 | 61.3484 | 61.416 | 122.8424 | 61.3847 | 122.6435 | 61.7682 | 61.7995 | 61.6719 | 61.7033
5632.0625 | 123.2574 | -61.3586 | 61.7981 | -0.92202 | -8.8593 | -6.0512 | -1.3803 | 7.1596 | -0.94455 | -3.826 | 61.8164 | 0.28526 | 61.7247 | -0.023943 | 0.052814 | 61.4746 | 0.007721 | 61.2482 | 60.4366 | 52.4993 | 55.3075 | 59.9784 | 68.5182 | 60.4141 | 57.5327 | 123.175 | 61.6439 | 123.0834 | 61.3347 | 61.4115 | 122.8332 | 61.3664 | 122.6069 | 61.7636 | 61.8087 | 61.6719 | 61.717
5633.0938 | 123.2895 | -61.3632 | 61.821 | -0.97696 | -8.9188 | -6.0832 | -1.3894 | 7.1962 | -0.9995 | -3.8672 | 61.821 | 0.29442 | 61.7614 | -0.028522 | 0.048236 | 61.47 | 0.007721 | 61.2528 | 60.3863 | 52.4444 | 55.28 | 59.9738 | 68.5594 | 60.3637 | 57.496 | 123.1842 | 61.6576 | 123.1246 | 61.3347 | 61.4115 | 122.8332 | 61.3709 | 122.616 | 61.7727 | 61.8132 | 61.7131 | 61.7536
5634.0625 | 123.2941 | -61.3495 | 61.8118 | -0.95407 | -8.7952 | -6.3167 | -1.4398 | 7.068 | -0.98576 | -3.8397 | 61.8301 | 0.28984 | 61.7522 | -0.019364 | 0.052814 | 61.4654 | 0.012299 | 61.2528 | 60.3954 | 52.5543 | 55.0328 | 59.9097 | 68.4175 | 60.3637 | 57.5098 | 123.1796 | 61.6393 | 123.1017 | 61.3301 | 61.4023 | 122.8149 | 61.3618 | 122.6023 | 61.7773 | 61.8178 | 61.6994 | 61.7399
5635.0938 | 123.4085 | -61.3358 | 61.7889 | -0.91744 | -8.5388 | -6.4175 | -1.5176 | 6.775 | -0.94455 | -3.9221 | 61.821 | 0.28984 | 61.7293 | -0.028522 | 0.052814 | 61.4654 | 0.012299 | 61.2528 | 60.4183 | 52.7969 | 54.9183 | 59.8181 | 68.1108 | 60.3912 | 57.4136 | 123.1567 | 61.6256 | 123.0651 | 61.3072 | 61.3886 | 122.8012 | 61.3481 | 122.5885 | 61.7682 | 61.8087 | 61.6765 | 61.717
5636.0625 | 123.3398 | -61.377 | 61.734 | -0.87166 | -8.6487 | -6.5411 | -1.481 | 7.0543 | -0.90793 | -3.9221 | 61.8118 | 0.28069 | 61.7202 | -0.033101 | 0.039079 | 61.4654 | 0.007721 | 61.2528 | 60.5053 | 52.7283 | 54.8359 | 59.896 | 68.4312 | 60.469 | 57.4548 | 123.1888 | 61.6576 | 123.0971 | 61.3439 | 61.416 | 122.8424 | 61.3847 | 122.6297 | 61.7727 | 61.8041 | 61.6811 | 61.7124
5637.0625 | 123.3078 | -61.3586 | 61.7752 | -0.88997 | -8.5296 | -6.6006 | -1.5313 | 6.9948 | -0.90793 | -3.9221 | 61.821 | 0.28984 | 61.7339 | -0.028522 | 0.048236 | 61.47 | 0.007721 | 61.2482 | 60.4687 | 52.829 | 54.758 | 59.8273 | 68.3534 | 60.4507 | 57.4365 | 123.1796 | 61.6485 | 123.0925 | 61.3301 | 61.4069 | 122.8287 | 61.3664 | 122.6069 | 61.7727 | 61.8132 | 61.6857 | 61.7262
5638.0938 | 123.2666 | -61.3358 | 61.8118 | -0.84877 | -8.5022 | -6.6876 | -1.5084 | 7.0634 | -0.8713 | -4.0137 | 61.8164 | 0.28984 | 61.7293 | -0.028522 | 0.043657 | 61.47 | 0.016878 | 61.2574 | 60.487 | 52.8336 | 54.6482 | 59.8273 | 68.3992 | 60.4645 | 57.3221 | 123.1521 | 61.6256 | 123.0651 | 61.3072 | 61.3794 | 122.8058 | 61.3526 | 122.5931 | 61.7727 | 61.7995 | 61.6857 | 61.7124
5639.0625 | 123.2529 | -61.3678 | 61.8118 | -0.86708 | -8.5342 | -6.7838 | -1.4672 | 6.8528 | -0.88504 | -3.8489 | 61.8255 | 0.28984 | 61.7568 | -0.023943 | 0.048236 | 61.47 | 0.012299 | 61.2436 | 60.5007 | 52.8336 | 54.584 | 59.9006 | 68.2206 | 60.4828 | 57.5189 | 123.1933 | 61.6576 | 123.1246 | 61.3439 | 61.416 | 122.8378 | 61.3801 | 122.6114 | 61.7773 | 61.8132 | 61.7085 | 61.7445
5640.0938 | 123.3627 | -61.3449 | 61.7844 | -0.88539 | -8.374 | -6.6464 | -1.4489 | 6.7063 | -0.90793 | -3.9542 | 61.8255 | 0.28984 | 61.7659 | -0.033101 | 0.043657 | 61.4654 | 0.007721 | 61.2482 | 60.4595 | 52.9709 | 54.6985 | 59.896 | 68.0513 | 60.437 | 57.3907 | 123.1705 | 61.6348 | 123.1109 | 61.3118 | 61.3886 | 122.8104 | 61.3526 | 122.5931 | 61.7819 | 61.8178 | 61.7223 | 61.7582
5641.0625 | 123.3856 | -61.3312 | 61.7706 | -0.93576 | -8.5022 | -6.5548 | -1.513 | 6.569 | -0.96287 | -4.0137 | 61.8301 | 0.28984 | 61.7614 | -0.028522 | 0.048236 | 61.4654 | 0.012299 | 61.2436 | 60.3954 | 52.829 | 54.7764 | 59.8181 | 67.9002 | 60.3683 | 57.3175 | 123.1613 | 61.621 | 123.0925 | 61.3027 | 61.3794 | 122.7966 | 61.3435 | 122.5748 | 61.7819 | 61.8178 | 61.7131 | 61.7491
5642.0781 | 123.2941 | -61.3495 | 61.8027 | -0.8625 | -8.841 | -6.2023 | -1.4535 | 6.4729 | -0.88046 | -4.1052 | 61.8255 | 0.28984 | 61.7614 | -0.033101 | 0.048236 | 61.4654 | 0.007721 | 61.2619 | 60.487 | 52.5085 | 55.1472 | 59.896 | 67.8224 | 60.469 | 57.2442 | 123.175 | 61.6393 | 123.1108 | 61.3164 | 61.3977 | 122.8149 | 61.3572 | 122.6114 | 61.7773 | 61.8178 | 61.7131 | 61.7536
5643.0625 | 123.2712 | -61.3907 | 61.7935 | -0.72515 | -8.8273 | -6.1061 | -1.3894 | 6.4591 | -0.73853 | -4.0732 | 61.821 | 0.28984 | 61.7293 | -0.033101 | 0.048236 | 61.47 | 0.007721 | 61.2482 | 60.6655 | 52.5634 | 55.2846 | 60.0013 | 67.8498 | 60.6522 | 57.3175 | 123.2117 | 61.6805 | 123.12 | 61.3576 | 61.4389 | 122.8607 | 61.3984 | 122.6389 | 61.7727 | 61.8132 | 61.6811 | 61.7216
5644.0938 | 123.3078 | -61.3586 | 61.8256 | -0.71599 | -8.754 | -6.4907 | -1.4581 | 6.4866 | -0.72937 | -4.0915 | 61.821 | 0.29442 | 61.7293 | -0.028522 | 0.057392 | 61.4654 | 0.007721 | 61.2574 | 60.6426 | 52.6046 | 54.8679 | 59.9006 | 67.8453 | 60.6293 | 57.2671 | 123.1796 | 61.6531 | 123.088 | 61.3301 | 61.416 | 122.8241 | 61.3664 | 122.616 | 61.7636 | 61.8132 | 61.6719 | 61.7216
5645.0625 | 123.3902 | -61.3083 | 61.7661 | -0.78467 | -8.3282 | -6.7059 | -1.5222 | 6.5232 | -0.79347 | -4.0595 | 61.8164 | 0.299 | 61.7247 | -0.03768 | 0.043657 | 61.4654 | 0.003143 | 61.2482 | 60.5236 | 52.9801 | 54.6024 | 59.7861 | 67.8315 | 60.5148 | 57.2488 | 123.1247 | 61.6073 | 123.033 | 61.2706 | 61.3519 | 122.7737 | 61.3114 | 122.5565 | 61.7727 | 61.8132 | 61.6811 | 61.7216
5646.0938 | 123.4543 | -61.3266 | 61.7661 | -0.88082 | -8.2687 | -6.6784 | -1.4718 | 6.6606 | -0.88046 | -4.0686 | 61.8164 | 0.28984 | 61.7385 | -0.023943 | 0.048236 | 61.47 | 0.016878 | 61.2436 | 60.4458 | 53.0579 | 54.6482 | 59.8548 | 67.9872 | 60.4461 | 57.258 | 123.143 | 61.6164 | 123.0651 | 61.3027 | 61.3748 | 122.7966 | 61.3435 | 122.5702 | 61.7682 | 61.7995 | 61.6902 | 61.7216
5647.0625 | 123.2437 | -61.3815 | 61.7981 | -0.9907 | -8.3785 | -6.683 | -1.5725 | 6.6056 | -0.9995 | -4.1648 | 61.8301 | 0.299 | 61.7568 | -0.028522 | 0.057392 | 61.4517 | 0.007721 | 61.2436 | 60.3908 | 53.003 | 54.6985 | 59.809 | 67.9872 | 60.382 | 57.2168 | 123.2117 | 61.6805 | 123.1383 | 61.353 | 61.4389 | 122.8332 | 61.3893 | 122.6252 | 61.7727 | 61.8224 | 61.6994 | 61.7491
5648.0781 | 123.2986 | -61.3541 | 61.7889 | -0.99985 | -8.4655 | -6.7105 | -1.5771 | 6.7521 | -1.0041 | -3.9816 | 61.8301 | 0.28984 | 61.7659 | -0.033101 | 0.048236 | 61.4563 | 0.007721 | 61.2528 | 60.3542 | 52.8885 | 54.6436 | 59.7769 | 68.1062 | 60.35 | 57.3724 | 123.1842 | 61.6439 | 123.12 | 61.321 | 61.4023 | 122.8104 | 61.3618 | 122.6069 | 61.7819 | 61.8224 | 61.7177 | 61.7582
5649.0625 | 123.262 | -61.3541 | 61.8073 | -1.1097 | -8.5159 | -6.7654 | -1.6641 | 6.6606 | -1.1231 | -4.0549 | 61.8301 | 0.29442 | 61.7659 | -0.028522 | 0.048236 | 61.4563 | 0.003143 | 61.2299 | 60.2443 | 52.8382 | 54.5886 | 59.6899 | 68.0146 | 60.231 | 57.2992 | 123.1842 | 61.6485 | 123.12 | 61.3255 | 61.4023 | 122.8104 | 61.3572 | 122.584 | 61.7819 | 61.827 | 61.7177 | 61.7628
5650.0938 | 123.3032 | -61.3358 | 61.8073 | -1.1097 | -8.6029 | -6.7975 | -1.6687 | 6.6102 | -1.1277 | -4.1007 | 61.8347 | 0.29442 | 61.7751 | -0.028522 | 0.057392 | 61.4517 | 0.007721 | 61.2436 | 60.226 | 52.7328 | 54.5383 | 59.6671 | 67.946 | 60.2081 | 57.2351 | 123.1705 | 61.6302 | 123.1109 | 61.3072 | 61.3931 | 122.7875 | 61.3435 | 122.5794 | 61.7773 | 61.827 | 61.7177 | 61.7674
5651.0625 | 123.3719 | -61.3403 | 61.734 | -1.1921 | -8.7906 | -6.7059 | -1.7282 | 6.5415 | -1.2101 | -4.0961 | 61.8347 | 0.28984 | 61.7705 | -0.033101 | 0.043657 | 61.4517 | 0.007721 | 61.2391 | 60.1482 | 52.5497 | 54.6344 | 59.6121 | 67.8819 | 60.1302 | 57.2442 | 123.175 | 61.6302 | 123.1109 | 61.3072 | 61.384 | 122.792 | 61.3481 | 122.5794 | 61.791 | 61.827 | 61.7269 | 61.7628
5652.0781 | 123.2986 | -61.3449 | 61.8073 | -1.2654 | -8.8456 | -6.6922 | -1.7511 | 6.6331 | -1.2879 | -4.0915 | 61.8393 | 0.28984 | 61.7476 | -0.028522 | 0.048236 | 61.4563 | 0.003143 | 61.2436 | 60.0795 | 52.4993 | 54.6527 | 59.5938 | 67.978 | 60.057 | 57.2534 | 123.1842 | 61.6348 | 123.0925 | 61.3164 | 61.3931 | 122.8012 | 61.3481 | 122.5885 | 61.791 | 61.8361 | 61.6994 | 61.7445
5653.0625 | 123.2666 | -61.3861 | 61.8164 | -1.1189 | -8.8364 | -6.6235 | -1.7191 | 6.5873 | -1.146 | -4.1144 | 61.8347 | 0.28984 | 61.743 | -0.028522 | 0.039079 | 61.4517 | 0.012299 | 61.2436 | 60.2672 | 52.5497 | 54.7626 | 59.667 | 67.9734 | 60.2401 | 57.2717 | 123.2208 | 61.676 | 123.1292 | 61.3576 | 61.4252 | 122.8378 | 61.3984 | 122.6297 | 61.7956 | 61.8224 | 61.704 | 61.7308
5654.0938 | 123.3398 | -61.3632 | 61.8164 | -1.0777 | -8.9463 | -6.6189 | -1.742 | 6.6148 | -1.1002 | -4.3296 | 61.8301 | 0.29442 | 61.743 | -0.03768 | 0.048236 | 61.4426 | 0.012299 | 61.2482 | 60.2855 | 52.4169 | 54.7443 | 59.6213 | 67.978 | 60.263 | 57.0336 | 123.1933 | 61.6576 | 123.1063 | 61.3255 | 61.4115 | 122.8058 | 61.3755 | 122.6114 | 61.7819 | 61.8178 | 61.6948 | 61.7308
5655.0625 | 123.3398 | -61.3541 | 61.8118 | -1.0823 | -8.8181 | -6.6327 | -1.7374 | 6.6056 | -1.114 | -4.4807 | 61.8301 | 0.29442 | 61.743 | -0.033101 | 0.048236 | 61.4563 | 0.003143 | 61.2482 | 60.2718 | 52.536 | 54.7214 | 59.6167 | 67.9597 | 60.2401 | 56.8734 | 123.1842 | 61.6485 | 123.0971 | 61.321 | 61.4023 | 122.8104 | 61.3572 | 122.6023 | 61.7819 | 61.827 | 61.6948 | 61.7399
5656.0625 | 123.3902 | -61.3449 | 61.7661 | -0.99528 | -8.6121 | -6.6189 | -1.7511 | 6.6377 | -1.0224 | -4.618 | 61.8393 | 0.29442 | 61.7476 | -0.03768 | 0.048236 | 61.4517 | 0.007721 | 61.2436 | 60.3496 | 52.7328 | 54.726 | 59.5938 | 67.9826 | 60.3225 | 56.7269 | 123.1842 | 61.6393 | 123.0925 | 61.3072 | 61.3931 | 122.7966 | 61.3526 | 122.5885 | 61.791 | 61.8316 | 61.6994 | 61.7399
5657.0938 | 123.4177 | -61.3312 | 61.734 | -1.0044 | -8.7677 | -6.6327 | -1.8061 | 6.5324 | -1.0315 | -4.4807 | 61.8347 | 0.28526 | 61.7797 | -0.033101 | 0.043657 | 61.4471 | 0.016878 | 61.2345 | 60.3267 | 52.5634 | 54.6985 | 59.5251 | 67.8636 | 60.2996 | 56.8505 | 123.1659 | 61.6164 | 123.1109 | 61.2981 | 61.3748 | 122.7783 | 61.3481 | 122.5657 | 61.791 | 61.8178 | 61.736 | 61.7628
5658.0625 | 123.3124 | -61.377 | 61.7798 | -1.0365 | -8.841 | -6.6464 | -1.8061 | 6.569 | -1.0636 | -4.3708 | 61.8393 | 0.28526 | 61.7705 | -0.028522 | 0.043657 | 61.4471 | 0.012299 | 61.2436 | 60.3405 | 52.5359 | 54.7306 | 59.5709 | 67.946 | 60.3134 | 57.0062 | 123.2162 | 61.6622 | 123.1475 | 61.3484 | 61.4206 | 122.8241 | 61.3893 | 122.6206 | 61.7956 | 61.827 | 61.7269 | 61.7582
5659.0938 | 123.3353 | -61.3358 | 61.7844 | -1.1143 | -8.9372 | -6.6968 | -1.8152 | 6.5919 | -1.1506 | -4.3982 | 61.8393 | 0.28984 | 61.7385 | -0.028522 | 0.048236 | 61.4471 | -0.001436 | 61.2299 | 60.2214 | 52.3986 | 54.639 | 59.5205 | 67.9277 | 60.1852 | 56.9375 | 123.175 | 61.6256 | 123.0742 | 61.3072 | 61.384 | 122.7829 | 61.3343 | 122.5656 | 61.791 | 61.8407 | 61.6902 | 61.7399
5660.0625 | 123.2574 | -61.3541 | 61.8027 | -1.1326 | -9.0242 | -6.8204 | -1.8335 | 6.5599 | -1.1643 | -4.4898 | 61.8439 | 0.29442 | 61.7568 | -0.023943 | 0.039079 | 61.4426 | 0.012299 | 61.2345 | 60.2214 | 52.3299 | 54.5337 | 59.5205 | 67.9139 | 60.1897 | 56.8643 | 123.1979 | 61.6485 | 123.1108 | 61.3301 | 61.3931 | 122.7966 | 61.3664 | 122.5885 | 61.8048 | 61.8316 | 61.7177 | 61.7445
5661.0625 | 123.4406 | -61.3037 | 61.7889 | -1.128 | -8.9692 | -6.8891 | -1.8473 | 6.6423 | -1.146 | -4.499 | 61.8393 | 0.28984 | 61.7843 | -0.033101 | 0.048236 | 61.4517 | 0.007721 | 61.2299 | 60.1757 | 52.3345 | 54.4147 | 59.4565 | 67.946 | 60.1577 | 56.8047 | 123.143 | 61.5936 | 123.088 | 61.2706 | 61.3519 | 122.7554 | 61.3114 | 122.5336 | 61.791 | 61.8316 | 61.736 | 61.7765
5662.0781 | 123.3307 | -61.3358 | 61.8073 | -1.0273 | -8.8822 | -6.8341 | -1.8793 | 6.8574 | -1.0499 | -4.5219 | 61.8484 | 0.28526 | 61.7705 | -0.033101 | 0.052814 | 61.4517 | 0.012299 | 61.2482 | 60.3084 | 52.4535 | 54.5016 | 59.4564 | 68.1932 | 60.2859 | 56.8139 | 123.1842 | 61.621 | 123.1063 | 61.3027 | 61.3886 | 122.7875 | 61.3481 | 122.584 | 61.7956 | 61.8361 | 61.7177 | 61.7582
5663.0625 | 123.2941 | -61.3358 | 61.7981 | -1.0227 | -8.7861 | -6.857 | -1.9022 | 6.7842 | -1.0453 | -4.6226 | 61.8439 | 0.28984 | 61.7339 | -0.033101 | 0.052814 | 61.4609 | 0.007721 | 61.2436 | 60.313 | 52.5497 | 54.4787 | 59.4336 | 68.1199 | 60.2905 | 56.7132 | 123.1796 | 61.6256 | 123.0696 | 61.3027 | 61.3886 | 122.7966 | 61.3435 | 122.5794 | 61.791 | 61.8361 | 61.6811 | 61.7262
5664.0938 | 123.4177 | -61.3037 | 61.7889 | -0.94034 | -8.8502 | -6.8112 | -1.8885 | 6.656 | -0.95829 | -4.5585 | 61.8347 | 0.28984 | 61.7568 | -0.033101 | 0.048236 | 61.4563 | 0.012299 | 61.2391 | 60.3634 | 52.4535 | 54.4925 | 59.4152 | 67.9597 | 60.3454 | 56.7452 | 123.1384 | 61.5936 | 123.0605 | 61.2706 | 61.3519 | 122.76 | 61.316 | 122.5428 | 61.7865 | 61.8224 | 61.7085 | 61.7445
5665.0625 | 123.2758 | -61.3586 | 61.8027 | -0.96323 | -8.9509 | -6.8295 | -1.8106 | 6.7384 | -0.98118 | -4.5219 | 61.8393 | 0.28984 | 61.7751 | -0.033101 | 0.039079 | 61.4609 | 0.016878 | 61.2391 | 60.3954 | 52.4077 | 54.5291 | 59.548 | 68.097 | 60.3775 | 56.8368 | 123.1979 | 61.6485 | 123.1337 | 61.3255 | 61.3977 | 122.8195 | 61.3755 | 122.5977 | 61.8002 | 61.8224 | 61.736 | 61.7582
5666.0938 | 123.2895 | -61.3312 | 61.8164 | -0.99528 | -8.9463 | -6.7746 | -1.687 | 6.8757 | -1.0178 | -4.4898 | 61.8347 | 0.28984 | 61.7614 | -0.028522 | 0.052814 | 61.4563 | 0.012299 | 61.2528 | 60.3359 | 52.3849 | 54.5566 | 59.6442 | 68.2069 | 60.3134 | 56.8414 | 123.1659 | 61.621 | 123.0925 | 61.3027 | 61.384 | 122.7875 | 61.3435 | 122.584 | 61.7819 | 61.8224 | 61.7085 | 61.7491
5667.0625 | 123.2391 | -61.3541 | 61.8073 | -1.0685 | -9.015 | -6.857 | -1.5909 | 6.9352 | -1.0682 | -4.5814 | 61.8301 | 0.29442 | 61.7476 | -0.028522 | 0.048236 | 61.4517 | 0.016878 | 61.2391 | 60.2855 | 52.3391 | 54.4971 | 59.7632 | 68.2893 | 60.2859 | 56.7727 | 123.1842 | 61.6485 | 123.1017 | 61.3255 | 61.4023 | 122.8058 | 61.3709 | 122.5931 | 61.7819 | 61.8132 | 61.6994 | 61.7308
5668.0938 | 123.317 | -61.3495 | 61.8347 | -1.0502 | -8.0626 | -6.8845 | -1.6779 | 6.6148 | -1.0544 | -4.4211 | 61.8301 | 0.28984 | 61.7476 | -0.019364 | 0.052814 | 61.4563 | 0.007721 | 61.2482 | 60.2993 | 53.2869 | 54.465 | 59.6716 | 67.9643 | 60.2951 | 56.9283 | 123.1796 | 61.6393 | 123.0971 | 61.3301 | 61.4023 | 122.8058 | 61.3572 | 122.5977 | 61.7773 | 61.8224 | 61.6948 | 61.7399
5669.0625 | 123.3124 | -61.3724 | 61.7981 | -1.2105 | -8.7586 | -6.9761 | -1.8564 | 6.5049 | -1.233 | -4.5264 | 61.853 | 0.28984 | 61.7843 | -0.033101 | 0.048236 | 61.4426 | 0.007721 | 61.2253 | 60.1619 | 52.6138 | 54.3963 | 59.516 | 67.8773 | 60.1394 | 56.8459 | 123.2254 | 61.6622 | 123.1566 | 61.3393 | 61.4206 | 122.8149 | 61.3801 | 122.5977 | 61.8048 | 61.8453 | 61.736 | 61.7765
5670.0938 | 123.2941 | -61.3449 | 61.8301 | -1.1189 | -8.8502 | -6.9715 | -1.8106 | 6.6514 | -1.146 | -4.5814 | 61.8393 | 0.28526 | 61.7705 | -0.033101 | 0.048236 | 61.4426 | 0.007721 | 61.2253 | 60.226 | 52.4947 | 54.3734 | 59.5343 | 67.9963 | 60.1989 | 56.7635 | 123.1842 | 61.6302 | 123.1154 | 61.3118 | 61.3931 | 122.7875 | 61.3526 | 122.5702 | 61.791 | 61.8316 | 61.7223 | 61.7628
5671.0625 | 123.4543 | -61.3312 | 61.8118 | -1.1693 | -9.0104 | -7.0264 | -1.9297 | 6.2119 | -1.1918 | -4.6592 | 61.8393 | 0.29442 | 61.743 | -0.033101 | 0.052814 | 61.438 | 0.007721 | 61.2207 | 60.1619 | 52.3208 | 54.3048 | 59.4015 | 67.5431 | 60.1394 | 56.672 | 123.1705 | 61.6256 | 123.0742 | 61.2981 | 61.384 | 122.7692 | 61.3389 | 122.5519 | 61.7865 | 61.8316 | 61.6902 | 61.7353
5672.0938 | 123.3032 | -61.3403 | 61.7981 | -1.128 | -9.0471 | -7.0539 | -1.9755 | 6.0746 | -1.1597 | -4.7004 | 61.853 | 0.28984 | 61.7659 | -0.028522 | 0.052814 | 61.438 | 0.007721 | 61.2253 | 60.2123 | 52.2933 | 54.2864 | 59.3649 | 67.4149 | 60.1806 | 56.6399 | 123.1933 | 61.6302 | 123.1063 | 61.3118 | 61.3931 | 122.7783 | 61.3481 | 122.5656 | 61.8002 | 61.8453 | 61.7131 | 61.7582
5673.0625 | 123.3124 | -61.3312 | 61.8118 | -1.1418 | -8.9417 | -7.1821 | -1.9571 | 6.1845 | -1.1552 | -4.6867 | 61.8622 | 0.299 | 61.7934 | -0.028522 | 0.048236 | 61.4334 | 0.012299 | 61.2253 | 60.1894 | 52.3894 | 54.1491 | 59.374 | 67.5156 | 60.176 | 56.6445 | 123.1933 | 61.6302 | 123.1246 | 61.3027 | 61.3794 | 122.7646 | 61.3435 | 122.5565 | 61.8139 | 61.8499 | 61.7452 | 61.7811
5674.1094 | 123.3582 | -61.3129 | 61.7798 | -1.0502 | -8.8776 | -7.0722 | -1.8564 | 6.07 | -1.0865 | -4.5356 | 61.8484 | 0.28526 | 61.7751 | -0.033101 | 0.039079 | 61.438 | 0.003143 | 61.2253 | 60.2627 | 52.4352 | 54.2407 | 59.4565 | 67.3829 | 60.2264 | 56.7773 | 123.1613 | 61.5981 | 123.088 | 61.2798 | 61.3519 | 122.7508 | 61.316 | 122.5382 | 61.8094 | 61.8453 | 61.736 | 61.772
5675.0625 | 123.3215 | -61.3083 | 61.821 | -1.0823 | -8.7906 | -7.0127 | -1.8747 | 6.189 | -1.114 | -4.5173 | 61.8439 | 0.28984 | 61.743 | -0.023943 | 0.052814 | 61.4426 | 0.003143 | 61.2299 | 60.226 | 52.5176 | 54.2956 | 59.4336 | 67.4973 | 60.1943 | 56.791 | 123.1521 | 61.5981 | 123.0513 | 61.2843 | 61.3611 | 122.7508 | 61.3114 | 122.5382 | 61.791 | 61.8407 | 61.6902 | 61.7399
5676.0781 | 123.3856 | -61.3083 | 61.8118 | -1.0456 | -8.7265 | -6.7975 | -1.8564 | 6.2898 | -1.0544 | -4.4074 | 61.8393 | 0.28984 | 61.7476 | -0.033101 | 0.048236 | 61.4517 | 0.012299 | 61.2345 | 60.2627 | 52.5818 | 54.5108 | 59.4519 | 67.598 | 60.2539 | 56.9009 | 123.1476 | 61.5981 | 123.0559 | 61.2752 | 61.3565 | 122.76 | 61.3206 | 122.5428 | 61.791 | 61.827 | 61.6994 | 61.7353
5677.0625 | 123.3032 | -61.3083 | 61.8118 | -1.0227 | -8.6624 | -6.8066 | -1.8473 | 6.2669 | -1.0407 | -4.4623 | 61.8439 | 0.29442 | 61.7705 | -0.033101 | 0.052814 | 61.4563 | 0.012299 | 61.2345 | 60.2855 | 52.6459 | 54.5016 | 59.461 | 67.5752 | 60.2676 | 56.8459 | 123.1521 | 61.6027 | 123.0788 | 61.2752 | 61.3611 | 122.7646 | 61.3206 | 122.5428 | 61.791 | 61.8316 | 61.7177 | 61.7582
5678.0938 | 123.3124 | -61.3541 | 61.8301 | -1.0594 | -8.7357 | -6.7929 | -1.8473 | 6.2302 | -1.0865 | -4.5035 | 61.8439 | 0.28526 | 61.7705 | -0.023943 | 0.048236 | 61.4471 | 0.007721 | 61.2391 | 60.2947 | 52.6184 | 54.5612 | 59.5068 | 67.5843 | 60.2676 | 56.8505 | 123.1979 | 61.6393 | 123.1246 | 61.3301 | 61.4023 | 122.8012 | 61.3618 | 122.5931 | 61.7956 | 61.8361 | 61.7223 | 61.7628
5679.0625 | 123.381 | -61.3174 | 61.7569 | -1.1235 | -8.896 | -6.7838 | -1.8473 | 6.3172 | -1.1506 | -4.444 | 61.8347 | 0.29442 | 61.743 | -0.033101 | 0.048236 | 61.438 | 0.012299 | 61.2253 | 60.194 | 52.4215 | 54.5337 | 59.4702 | 67.6347 | 60.1669 | 56.8734 | 123.1521 | 61.6119 | 123.0605 | 61.2843 | 61.3657 | 122.7554 | 61.3297 | 122.5428 | 61.7865 | 61.8224 | 61.6948 | 61.7308
5680.0781 | 123.4451 | -61.3083 | 61.8027 | -1.1052 | -8.8044 | -6.7242 | -1.8656 | 6.2989 | -1.1277 | -4.4532 | 61.8393 | 0.29442 | 61.7476 | -0.028522 | 0.048236 | 61.4471 | 0.007721 | 61.2345 | 60.2031 | 52.5039 | 54.5841 | 59.4427 | 67.6072 | 60.1806 | 56.8551 | 123.1476 | 61.6027 | 123.0559 | 61.2798 | 61.3565 | 122.7554 | 61.316 | 122.5428 | 61.791 | 61.8316 | 61.6994 | 61.7399
5681.0625 | 123.2941 | -61.3403 | 61.821 | -1.0868 | -8.754 | -6.8066 | -1.861 | 6.3081 | -1.1094 | -4.5951 | 61.8484 | 0.28526 | 61.7797 | -0.028522 | 0.057392 | 61.4517 | 0.012299 | 61.2345 | 60.2535 | 52.5863 | 54.5337 | 59.4793 | 67.6484 | 60.231 | 56.7452 | 123.1888 | 61.6256 | 123.12 | 61.3118 | 61.3977 | 122.792 | 61.3526 | 122.5748 | 61.791 | 61.8361 | 61.7223 | 61.7674
5682.1094 | 123.3902 | -61.3174 | 61.7798 | -1.1509 | -8.9051 | -6.8158 | -1.9617 | 6.5095 | -1.1781 | -4.6775 | 61.8439 | 0.28526 | 61.7659 | -0.033101 | 0.052814 | 61.4426 | 0.012299 | 61.2253 | 60.1665 | 52.4123 | 54.5016 | 59.3557 | 67.8269 | 60.1394 | 56.6399 | 123.1613 | 61.6027 | 123.0834 | 61.2843 | 61.3703 | 122.76 | 61.3297 | 122.5428 | 61.791 | 61.8316 | 61.7131 | 61.7536
5683.0625 | 123.3673 | -61.3449 | 61.8256 | -1.128 | -9.0425 | -6.8707 | -2.0167 | 6.4134 | -1.1689 | -4.6775 | 61.8439 | 0.28984 | 61.7568 | -0.033101 | 0.048236 | 61.438 | 0.012299 | 61.2253 | 60.2169 | 52.3024 | 54.4742 | 59.3282 | 67.7583 | 60.176 | 56.6674 | 123.1888 | 61.6348 | 123.1017 | 61.3118 | 61.3931 | 122.7829 | 61.3572 | 122.5702 | 61.7956 | 61.8316 | 61.7085 | 61.7445
5684.0625 | 123.3078 | -61.3129 | 61.8118 | -1.1418 | -9.0791 | -6.8845 | -1.9892 | 6.5553 | -1.1689 | -4.5127 | 61.8439 | 0.28526 | 61.7522 | -0.028522 | 0.043657 | 61.4517 | 0.007721 | 61.2345 | 60.1711 | 52.2338 | 54.4284 | 59.3237 | 67.8681 | 60.144 | 56.8002 | 123.1567 | 61.5981 | 123.0651 | 61.2843 | 61.3565 | 122.7646 | 61.3206 | 122.5473 | 61.8002 | 61.8361 | 61.7085 | 61.7445
5685.1094 | 123.3215 | -61.3312 | 61.7844 | -1.1555 | -9.221 | -6.9303 | -2.0121 | 6.5187 | -1.1872 | -4.5768 | 61.853 | 0.29442 | 61.7843 | -0.028522 | 0.043657 | 61.4471 | 0.007721 | 61.2207 | 60.1757 | 52.1101 | 54.4009 | 59.3191 | 67.8498 | 60.144 | 56.7544 | 123.1842 | 61.6256 | 123.1154 | 61.3027 | 61.3748 | 122.7783 | 61.3389 | 122.5519 | 61.8094 | 61.8453 | 61.7406 | 61.7765
5686.0625 | 123.3536 | -61.29 | 61.8393 | -1.4897 | -9.1753 | -6.9211 | -2.0945 | 6.5278 | -1.5214 | -4.5814 | 61.853 | 0.28984 | 61.7934 | -0.023943 | 0.043657 | 61.438 | 0.012299 | 61.2207 | 59.8002 | 52.1147 | 54.3689 | 59.1955 | 67.8178 | 59.7685 | 56.7086 | 123.143 | 61.5798 | 123.0834 | 61.266 | 61.3336 | 122.728 | 61.3023 | 122.5107 | 61.8094 | 61.8407 | 61.7498 | 61.7811
5687.0781 | 123.3902 | -61.3174 | 61.821 | -1.595 | -9.0425 | -7.0402 | -2.1357 | 6.4408 | -1.6313 | -4.5447 | 61.8484 | 0.28984 | 61.7522 | -0.028522 | 0.043657 | 61.4426 | 0.016878 | 61.2162 | 59.7224 | 52.275 | 54.2773 | 59.1817 | 67.7583 | 59.6861 | 56.7727 | 123.1659 | 61.6073 | 123.0697 | 61.2889 | 61.3611 | 122.76 | 61.3343 | 122.5336 | 61.8048 | 61.8316 | 61.7085 | 61.7353
5688.0625 | 123.2941 | -61.3266 | 61.8759 | -1.6225 | -9.0516 | -7.1088 | -2.0899 | 6.5507 | -1.6588 | -4.4532 | 61.8622 | 0.29442 | 61.7659 | -0.028522 | 0.048236 | 61.4334 | 0.016878 | 61.2162 | 59.7041 | 52.275 | 54.2178 | 59.2367 | 67.8773 | 59.6678 | 56.8734 | 123.1888 | 61.621 | 123.0925 | 61.2981 | 61.3748 | 122.76 | 61.3435 | 122.5428 | 61.8139 | 61.8453 | 61.7177 | 61.7491
5689.0938 | 123.2758 | -61.3174 | 61.853 | -1.4485 | -8.8502 | -7.0539 | -1.9251 | 6.656 | -1.4848 | -4.2517 | 61.8393 | 0.28984 | 61.7659 | -0.028522 | 0.052814 | 61.4471 | 0.012299 | 61.2253 | 59.8689 | 52.4673 | 54.2636 | 59.3924 | 67.9734 | 59.8326 | 57.0657 | 123.1567 | 61.6073 | 123.0834 | 61.2889 | 61.3703 | 122.7646 | 61.3297 | 122.5428 | 61.7865 | 61.827 | 61.7131 | 61.7536
5690.0625 | 123.3673 | -61.3083 | 61.7569 | -1.4302 | -8.8273 | -7.0402 | -1.8656 | 6.5965 | -1.4665 | -4.1785 | 61.853 | 0.28984 | 61.7751 | -0.033101 | 0.039079 | 61.4471 | 0.007721 | 61.2207 | 59.8781 | 52.481 | 54.2681 | 59.4427 | 67.9048 | 59.8418 | 57.1298 | 123.1613 | 61.5981 | 123.0834 | 61.2752 | 61.3474 | 122.7554 | 61.316 | 122.529 | 61.8139 | 61.8453 | 61.736 | 61.7674
5691.0781 | 123.3765 | -61.3403 | 61.7706 | -1.3066 | -9.0425 | -6.8295 | -1.9068 | 6.4958 | -1.3429 | -4.2701 | 61.8393 | 0.28984 | 61.7843 | -0.033101 | 0.043657 | 61.438 | 0.012299 | 61.2253 | 60.0337 | 52.2979 | 54.5108 | 59.4336 | 67.8361 | 59.9975 | 57.0703 | 123.1796 | 61.6302 | 123.1246 | 61.3072 | 61.384 | 122.7783 | 61.3526 | 122.5656 | 61.7956 | 61.827 | 61.7406 | 61.772
5692.0625 | 123.4222 | -61.3174 | 61.7569 | -1.2379 | -9.0608 | -6.7013 | -1.9342 | 6.2898 | -1.2696 | -4.4395 | 61.8393 | 0.28984 | 61.7614 | -0.028522 | 0.039079 | 61.438 | 0.007721 | 61.2207 | 60.0795 | 52.2567 | 54.6161 | 59.3832 | 67.6072 | 60.0478 | 56.878 | 123.1567 | 61.6073 | 123.0788 | 61.2889 | 61.3565 | 122.7554 | 61.3252 | 122.5382 | 61.8002 | 61.8316 | 61.7223 | 61.7536
5693.1094 | 123.2803 | -61.3632 | 61.8301 | -1.1921 | -9.0516 | -6.6464 | -1.8793 | 6.3401 | -1.2238 | -4.4303 | 61.8347 | 0.29442 | 61.7476 | -0.028522 | 0.052814 | 61.4471 | 0.007721 | 61.2299 | 60.1711 | 52.3116 | 54.7168 | 59.4839 | 67.7033 | 60.1394 | 56.9329 | 123.1979 | 61.6576 | 123.1108 | 61.3347 | 61.416 | 122.8103 | 61.3709 | 122.5931 | 61.7819 | 61.827 | 61.6948 | 61.7399
5694.0625 | 123.2666 | -61.3358 | 61.8713 | -1.1784 | -8.9234 | -6.6327 | -1.9297 | 6.3767 | -1.2101 | -4.444 | 61.8393 | 0.29442 | 61.7522 | -0.028522 | 0.043657 | 61.4471 | 0.016878 | 61.2253 | 60.1573 | 52.4123 | 54.7031 | 59.4061 | 67.7125 | 60.1257 | 56.8917 | 123.175 | 61.6302 | 123.088 | 61.3072 | 61.3794 | 122.7829 | 61.3526 | 122.5611 | 61.7956 | 61.8224 | 61.7085 | 61.7353
5695.0938 | 123.2986 | -61.322 | 61.8484 | -1.2562 | -8.9555 | -6.7059 | -2.0487 | 6.1021 | -1.2788 | -4.5219 | 61.853 | 0.28984 | 61.7888 | -0.023943 | 0.048236 | 61.438 | 0.012299 | 61.2162 | 60.0658 | 52.3665 | 54.6161 | 59.2733 | 67.4241 | 60.0432 | 56.8002 | 123.175 | 61.6119 | 123.1109 | 61.2981 | 61.3703 | 122.76 | 61.3343 | 122.5382 | 61.8048 | 61.8407 | 61.7406 | 61.7765
5696.0625 | 123.3078 | -61.29 | 61.8805 | -1.3341 | -8.9738 | -6.944 | -2.1357 | 5.9876 | -1.352 | -4.7141 | 61.8576 | 0.28984 | 61.7843 | -0.028522 | 0.048236 | 61.4288 | 0.007721 | 61.2162 | 59.9559 | 52.3162 | 54.346 | 59.1543 | 67.2776 | 59.9379 | 56.5758 | 123.1476 | 61.5798 | 123.0742 | 61.2615 | 61.3382 | 122.7188 | 61.2977 | 122.5061 | 61.8094 | 61.8499 | 61.736 | 61.7765
5697.0938 | 123.3948 | -61.29 | 61.8164 | -1.2883 | -8.928 | -6.9761 | -2.1265 | 5.9556 | -1.32 | -4.7645 | 61.853 | 0.28526 | 61.7568 | -0.023943 | 0.052814 | 61.4334 | 0.012299 | 61.2253 | 60.0017 | 52.362 | 54.3139 | 59.1634 | 67.2455 | 59.97 | 56.5255 | 123.143 | 61.5752 | 123.0468 | 61.266 | 61.3428 | 122.7234 | 61.3023 | 122.5153 | 61.8002 | 61.8407 | 61.704 | 61.7445
5698.0625 | 123.3536 | -61.3541 | 61.7844 | -1.3478 | -9.1112 | -7.0356 | -2.1586 | 5.8961 | -1.3795 | -4.7691 | 61.853 | 0.28984 | 61.7705 | -0.028522 | 0.048236 | 61.438 | 0.003143 | 61.2162 | 60.0063 | 52.2429 | 54.3185 | 59.1955 | 67.2501 | 59.9746 | 56.585 | 123.2071 | 61.6439 | 123.1246 | 61.3255 | 61.4023 | 122.792 | 61.3572 | 122.5702 | 61.8048 | 61.8499 | 61.7223 | 61.7674
5699.0938 | 123.3948 | -61.3083 | 61.8164 | -1.357 | -9.2027 | -7.031 | -1.98 | 6.0975 | -1.3841 | -4.7325 | 61.8622 | 0.28984 | 61.798 | -0.023943 | 0.052814 | 61.4288 | 0.012299 | 61.2299 | 59.9513 | 52.1056 | 54.2773 | 59.3283 | 67.4058 | 59.9242 | 56.5758 | 123.1705 | 61.5981 | 123.1063 | 61.2843 | 61.3611 | 122.7371 | 61.3206 | 122.5382 | 61.8094 | 61.8499 | 61.7452 | 61.7857
5700.0625 | 123.2849 | -61.3312 | 61.8484 | -1.2837 | -9.3493 | -7.2508 | -1.9709 | 6.331 | -1.3062 | -4.7965 | 61.8576 | 0.28526 | 61.7888 | -0.028522 | 0.048236 | 61.4334 | 0.007721 | 61.2299 | 60.0475 | 51.9819 | 54.0804 | 59.3603 | 67.6621 | 60.0249 | 56.5346 | 123.1888 | 61.6164 | 123.12 | 61.3027 | 61.3794 | 122.7646 | 61.3389 | 122.5611 | 61.8094 | 61.8499 | 61.7406 | 61.7811
5701.1094 | 123.3994 | -61.3129 | 61.7798 | -1.2837 | -9.395 | -7.2325 | -1.9526 | 6.5003 | -1.3062 | -4.7965 | 61.8484 | 0.28984 | 61.7614 | -0.033101 | 0.039079 | 61.4288 | 0.007721 | 61.2207 | 60.0292 | 51.9178 | 54.0804 | 59.3603 | 67.8132 | 60.0066 | 56.5163 | 123.1613 | 61.6027 | 123.0742 | 61.2798 | 61.3519 | 122.7417 | 61.3206 | 122.5336 | 61.8094 | 61.8407 | 61.7223 | 61.7536
5702.0625 | 123.3124 | -61.322 | 61.8622 | -1.3844 | -9.4225 | -7.0447 | -1.8747 | 6.1799 | -1.4024 | -5.0712 | 61.8576 | 0.28984 | 61.7659 | -0.033101 | 0.057392 | 61.4242 | 0.012299 | 61.2116 | 59.9376 | 51.8995 | 54.2773 | 59.4473 | 67.5019 | 59.9196 | 56.2508 | 123.1796 | 61.6119 | 123.088 | 61.2889 | 61.3794 | 122.7463 | 61.3343 | 122.5336 | 61.8002 | 61.8453 | 61.7086 | 61.7536
5703.0938 | 123.2529 | -61.3358 | 61.8896 | -1.4211 | -9.3813 | -6.9074 | -1.8976 | 6.1524 | -1.4528 | -5.0712 | 61.8622 | 0.29442 | 61.7934 | -0.023943 | 0.052814 | 61.438 | 0.012299 | 61.2162 | 59.9147 | 51.9544 | 54.4284 | 59.4381 | 67.4882 | 59.883 | 56.2645 | 123.1979 | 61.6302 | 123.1292 | 61.3118 | 61.3886 | 122.7737 | 61.3481 | 122.5519 | 61.8094 | 61.8499 | 61.7406 | 61.7811
5704.0625 | 123.317 | -61.3358 | 61.8027 | -1.4165 | -9.1157 | -7.0173 | -2.0075 | 6.1845 | -1.4436 | -4.8606 | 61.8622 | 0.28984 | 61.7934 | -0.023943 | 0.048236 | 61.4242 | 0.012299 | 61.2162 | 59.9193 | 52.22 | 54.3185 | 59.3282 | 67.5202 | 59.8922 | 56.4751 | 123.1979 | 61.6256 | 123.1292 | 61.3118 | 61.384 | 122.76 | 61.3481 | 122.5519 | 61.8139 | 61.8499 | 61.7452 | 61.7811
5705.0938 | 123.3856 | -61.2991 | 61.7752 | -1.5035 | -8.1954 | -7.031 | -2.067 | 6.4088 | -1.5306 | -4.737 | 61.8393 | 0.299 | 61.7522 | -0.023943 | 0.052814 | 61.438 | 0.012299 | 61.2253 | 59.7957 | 53.1037 | 54.2681 | 59.2321 | 67.7079 | 59.7685 | 56.5621 | 123.1384 | 61.5981 | 123.0513 | 61.2752 | 61.3519 | 122.7371 | 61.3114 | 122.5245 | 61.7865 | 61.827 | 61.6994 | 61.7399
5706.0625 | 123.4085 | -61.3174 | 61.7523 | -1.4531 | -8.2366 | -6.9669 | -2.0808 | 6.5095 | -1.4573 | -4.6958 | 61.8393 | 0.29442 | 61.7522 | -0.028522 | 0.043657 | 61.4471 | 0.007721 | 61.2345 | 59.8643 | 53.0808 | 54.3505 | 59.2367 | 67.8269 | 59.8601 | 56.6216 | 123.1567 | 61.6119 | 123.0697 | 61.2889 | 61.3611 | 122.7646 | 61.3252 | 122.5519 | 61.7956 | 61.8316 | 61.7085 | 61.7445
5707.0938 | 123.3536 | -61.3266 | 61.7432 | -1.3661 | -8.3831 | -6.8982 | -2.0167 | 6.2119 | -1.3795 | -4.7599 | 61.8484 | 0.28984 | 61.7751 | -0.028522 | 0.048236 | 61.438 | 0.003143 | 61.2207 | 59.9605 | 52.9435 | 54.4284 | 59.3099 | 67.5385 | 59.9471 | 56.5667 | 123.175 | 61.6164 | 123.1017 | 61.2981 | 61.3748 | 122.7646 | 61.3297 | 122.5473 | 61.8002 | 61.8453 | 61.7269 | 61.772
5708.0625 | 123.3261 | -61.3174 | 61.8668 | -1.3203 | -9.0058 | -6.9852 | -1.9755 | 6.1982 | -1.3429 | -4.7187 | 61.8576 | 0.28984 | 61.7797 | -0.03768 | 0.048236 | 61.438 | 0.007721 | 61.2253 | 59.9971 | 52.3116 | 54.3322 | 59.342 | 67.5156 | 59.9746 | 56.5987 | 123.175 | 61.6073 | 123.0971 | 61.2798 | 61.3657 | 122.7554 | 61.3252 | 122.5428 | 61.8094 | 61.8499 | 61.7314 | 61.772
5709.0625 | 123.381 | -61.3403 | 61.7706 | -1.2746 | -9.1157 | -6.9303 | -1.9388 | 6.276 | -1.2971 | -4.6775 | 61.8484 | 0.28984 | 61.7522 | -0.028522 | 0.048236 | 61.4471 | 0.012299 | 61.2345 | 60.0658 | 52.2246 | 54.4101 | 59.4015 | 67.6164 | 60.0432 | 56.6628 | 123.1888 | 61.6302 | 123.0925 | 61.3118 | 61.3886 | 122.7875 | 61.3526 | 122.5748 | 61.8002 | 61.8361 | 61.704 | 61.7399
5710.0625 | 123.3353 | -61.3174 | 61.8347 | -1.3432 | -9.2348 | -6.9303 | -1.9342 | 6.2669 | -1.352 | -4.705 | 61.8576 | 0.29442 | 61.7843 | -0.028522 | 0.052814 | 61.4334 | 0.012299 | 61.2162 | 59.9742 | 52.0827 | 54.3872 | 59.3832 | 67.5843 | 59.9654 | 56.6125 | 123.175 | 61.6119 | 123.1017 | 61.2889 | 61.3703 | 122.7508 | 61.3297 | 122.5336 | 61.8048 | 61.8453 | 61.7314 | 61.772
5711.0625 | 123.2986 | -61.3358 | 61.8256 | -1.4256 | -9.2119 | -6.9898 | -2.0304 | 6.1295 | -1.4528 | -4.7141 | 61.8576 | 0.28526 | 61.7797 | -0.028522 | 0.043657 | 61.4288 | 0.007721 | 61.2207 | 59.9101 | 52.1239 | 54.346 | 59.3054 | 67.4653 | 59.883 | 56.6216 | 123.1933 | 61.621 | 123.1154 | 61.3072 | 61.3794 | 122.7646 | 61.3435 | 122.5565 | 61.8139 | 61.8499 | 61.736 | 61.772
5712.0938 | 123.4177 | -61.2991 | 61.821 | -1.4852 | -9.3309 | -7.1226 | -2.1265 | 6.0837 | -1.5031 | -4.9705 | 61.853 | 0.28984 | 61.7614 | -0.033101 | 0.048236 | 61.4197 | 0.012299 | 61.2116 | 59.814 | 51.9682 | 54.1766 | 59.1726 | 67.3829 | 59.796 | 56.3286 | 123.1521 | 61.589 | 123.0605 | 61.266 | 61.3474 | 122.7188 | 61.3114 | 122.5107 | 61.8048 | 61.8407 | 61.7131 | 61.7491
5713.0625 | 123.2666 | -61.3174 | 61.8759 | -1.5355 | -9.2577 | -7.2279 | -2.0899 | 6.2531 | -1.5626 | -5.0483 | 61.8713 | 0.28069 | 61.798 | -0.023943 | 0.039079 | 61.4288 | 0.012299 | 61.207 | 59.7819 | 52.0598 | 54.0896 | 59.2275 | 67.5706 | 59.7548 | 56.2691 | 123.1888 | 61.5981 | 123.1154 | 61.2935 | 61.3565 | 122.7463 | 61.3297 | 122.5244 | 61.8323 | 61.859 | 61.7589 | 61.7857
5714.1094 | 123.3536 | -61.3266 | 61.7798 | -1.5172 | -9.1661 | -7.1455 | -2.0624 | 6.5782 | -1.5489 | -5.0712 | 61.8622 | 0.28526 | 61.7659 | -0.028522 | 0.039079 | 61.4288 | 0.007721 | 61.2116 | 59.8094 | 52.1605 | 54.1811 | 59.2642 | 67.9048 | 59.7777 | 56.2554 | 123.1888 | 61.6119 | 123.0925 | 61.2981 | 61.3657 | 122.7554 | 61.3343 | 122.5382 | 61.8231 | 61.8545 | 61.7269 | 61.7582
5715.0625 | 123.2986 | -61.322 | 61.8713 | -1.5722 | -9.2439 | -7.1592 | -2.0579 | 6.5599 | -1.6038 | -5.2223 | 61.853 | 0.28526 | 61.7705 | -0.023943 | 0.048236 | 61.4242 | 0.007721 | 61.207 | 59.7499 | 52.0781 | 54.1628 | 59.2642 | 67.8819 | 59.7182 | 56.0997 | 123.175 | 61.6073 | 123.0925 | 61.2981 | 61.3703 | 122.7463 | 61.3297 | 122.529 | 61.8048 | 61.8453 | 61.7223 | 61.7628
5716.0938 | 123.381 | -61.2991 | 61.8347 | -1.6225 | -9.2989 | -7.2416 | -2.0762 | 6.4958 | -1.6496 | -5.3276 | 61.8668 | 0.29442 | 61.798 | -0.028522 | 0.048236 | 61.4197 | 0.007721 | 61.2116 | 59.6766 | 52.0002 | 54.0575 | 59.2229 | 67.7949 | 59.6495 | 55.9715 | 123.1659 | 61.5936 | 123.0971 | 61.2706 | 61.3474 | 122.7188 | 61.3069 | 122.5107 | 61.8185 | 61.859 | 61.7498 | 61.7903
5717.0781 | 123.349 | -61.3129 | 61.8484 | -1.6454 | -9.3172 | -7.2966 | -2.1403 | 6.4134 | -1.6725 | -5.3459 | 61.8622 | 0.29442 | 61.7705 | -0.033101 | 0.048236 | 61.4242 | 0.003143 | 61.207 | 59.6675 | 51.9957 | 54.0163 | 59.1726 | 67.7262 | 59.6403 | 55.9669 | 123.175 | 61.6073 | 123.0834 | 61.2798 | 61.3611 | 122.7371 | 61.316 | 122.5199 | 61.8139 | 61.859 | 61.7223 | 61.7674
5718.0781 | 123.3719 | -61.3083 | 61.8027 | -1.65 | -9.2119 | -7.2462 | -2.1265 | 6.4363 | -1.6771 | -5.3093 | 61.8576 | 0.28984 | 61.7751 | -0.033101 | 0.043657 | 61.4288 | 0.007721 | 61.207 | 59.6583 | 52.0964 | 54.0621 | 59.1817 | 67.7445 | 59.6312 | 55.999 | 123.1659 | 61.5981 | 123.0834 | 61.2752 | 61.3519 | 122.7371 | 61.316 | 122.5153 | 61.8139 | 61.8499 | 61.7314 | 61.7674
5719.0625 | 123.3398 | -61.2946 | 61.8439 | -1.6729 | -9.189 | -7.2187 | -2.1403 | 6.3081 | -1.7 | -5.3139 | 61.8759 | 0.28984 | 61.8071 | -0.028522 | 0.039079 | 61.4288 | 0.007721 | 61.2024 | 59.6217 | 52.1056 | 54.0758 | 59.1543 | 67.6026 | 59.5946 | 55.9807 | 123.1705 | 61.5844 | 123.1017 | 61.266 | 61.3336 | 122.7234 | 61.3023 | 122.497 | 61.8368 | 61.8682 | 61.7681 | 61.7994
5720.0938 | 123.3994 | -61.2946 | 61.8256 | -1.6637 | -9.1478 | -7.2325 | -2.1357 | 6.2714 | -1.6954 | -5.3185 | 61.8713 | 0.28526 | 61.7705 | -0.033101 | 0.052814 | 61.4242 | 0.003143 | 61.207 | 59.6308 | 52.1468 | 54.0621 | 59.1589 | 67.566 | 59.5991 | 55.9761 | 123.1659 | 61.5798 | 123.0651 | 61.2615 | 61.3474 | 122.7188 | 61.2977 | 122.5016 | 61.8185 | 61.8682 | 61.7177 | 61.7674
5721.0625 | 123.3078 | -61.2991 | 61.8759 | -1.563 | -9.1249 | -7.2462 | -2.1861 | 6.0288 | -1.5855 | -5.3093 | 61.8668 | 0.28984 | 61.7797 | -0.028522 | 0.048236 | 61.4288 | 0.012299 | 61.2024 | 59.7361 | 52.1742 | 54.0529 | 59.1131 | 67.3279 | 59.7136 | 55.9898 | 123.1659 | 61.589 | 123.0788 | 61.2706 | 61.3474 | 122.728 | 61.3114 | 122.5016 | 61.8185 | 61.8545 | 61.7314 | 61.7674
5722.1094 | 123.3765 | -61.3083 | 61.8118 | -1.5218 | -8.4106 | -7.2004 | -2.2181 | 5.7724 | -1.5581 | -5.0529 | 61.8622 | 0.299 | 61.7797 | -0.023943 | 0.048236 | 61.4288 | 0.012299 | 61.207 | 59.7865 | 52.8977 | 54.1079 | 59.0902 | 67.0807 | 59.7502 | 56.2554 | 123.1705 | 61.6073 | 123.088 | 61.2843 | 61.3565 | 122.7371 | 61.3206 | 122.5153 | 61.8139 | 61.8499 | 61.7314 | 61.7674
5723.0625 | 123.2574 | -61.3129 | 61.8805 | -1.5035 | -8.6487 | -7.2553 | -2.2181 | 5.864 | -1.5443 | -5.0667 | 61.8668 | 0.28984 | 61.7934 | -0.019364 | 0.052814 | 61.4288 | 0.003143 | 61.2024 | 59.8094 | 52.6642 | 54.0575 | 59.0947 | 67.1769 | 59.7685 | 56.2462 | 123.1796 | 61.6027 | 123.1063 | 61.2935 | 61.3657 | 122.7417 | 61.316 | 122.5153 | 61.8139 | 61.8636 | 61.7406 | 61.7903
5724.0938 | 123.381 | -61.2671 | 61.8164 | -1.6591 | -8.5571 | -7.2279 | -2.2227 | 6.0975 | -1.6908 | -5.0621 | 61.8622 | 0.28984 | 61.7751 | -0.028522 | 0.052814 | 61.4288 | 0.003143 | 61.2207 | 59.6079 | 52.71 | 54.0392 | 59.0444 | 67.3646 | 59.5763 | 56.205 | 123.1293 | 61.5569 | 123.0422 | 61.2386 | 61.3199 | 122.6959 | 61.2702 | 122.4878 | 61.8094 | 61.859 | 61.7223 | 61.772
5725.0781 | 123.317 | -61.2991 | 61.8484 | -1.6912 | -8.9051 | -7.2553 | -2.2502 | 6.0563 | -1.7137 | -4.9705 | 61.8668 | 0.28984 | 61.7705 | -0.028522 | 0.048236 | 61.4242 | 0.007721 | 61.207 | 59.6079 | 52.394 | 54.0438 | 59.049 | 67.3554 | 59.5854 | 56.3286 | 123.1659 | 61.589 | 123.0697 | 61.2706 | 61.3474 | 122.7234 | 61.3069 | 122.5061 | 61.8185 | 61.859 | 61.7223 | 61.7628
5726.0781 | 123.4085 | -61.2671 | 61.8118 | -1.682 | -8.9601 | -7.3607 | -2.2639 | 6.3081 | -1.7183 | -5.117 | 61.8576 | 0.28984 | 61.7751 | -0.028522 | 0.052814 | 61.4242 | 0.016878 | 61.207 | 59.5851 | 52.307 | 53.9064 | 59.0032 | 67.5752 | 59.5488 | 56.1501 | 123.1247 | 61.5569 | 123.0422 | 61.2386 | 61.3199 | 122.6913 | 61.284 | 122.4741 | 61.8048 | 61.8407 | 61.7223 | 61.7582
5727.0625 | 123.4177 | -61.29 | 61.7935 | -1.6866 | -9.102 | -7.3744 | -2.3005 | 6.2257 | -1.7229 | -5.1216 | 61.8805 | 0.29442 | 61.8026 | -0.033101 | 0.048236 | 61.4197 | 0.003143 | 61.1978 | 59.6034 | 52.188 | 53.9156 | 58.9894 | 67.5156 | 59.5671 | 56.1684 | 123.1705 | 61.5844 | 123.0925 | 61.2569 | 61.3382 | 122.7096 | 61.2931 | 122.4878 | 61.8323 | 61.8773 | 61.7543 | 61.7994
5728.0781 | 123.4314 | -61.2305 | 61.853 | -1.595 | -9.189 | -7.3561 | -2.2685 | 6.2074 | -1.6313 | -5.2177 | 61.8668 | 0.28526 | 61.7934 | -0.028522 | 0.039079 | 61.4288 | 0.007721 | 61.2116 | 59.6354 | 52.0415 | 53.8744 | 58.962 | 67.4378 | 59.5992 | 56.0127 | 123.0972 | 61.5157 | 123.0239 | 61.2019 | 61.2695 | 122.6593 | 61.2382 | 122.4421 | 61.8277 | 61.859 | 61.7543 | 61.7857
5729.0625 | 123.3078 | -61.2854 | 61.8439 | -1.5584 | -9.221 | -7.3469 | -2.2731 | 6.0425 | -1.5947 | -5.2635 | 61.8622 | 0.29442 | 61.7751 | -0.023943 | 0.048236 | 61.4197 | 0.016878 | 61.2116 | 59.727 | 52.0644 | 53.9385 | 59.0123 | 67.3279 | 59.6907 | 56.0219 | 123.1476 | 61.5798 | 123.0605 | 61.2615 | 61.3336 | 122.7051 | 61.3023 | 122.497 | 61.8139 | 61.8453 | 61.7269 | 61.7582
5730.1094 | 123.2712 | -61.3174 | 61.8347 | -1.5676 | -9.3447 | -7.3332 | -2.3051 | 6.0929 | -1.6038 | -5.3322 | 61.8713 | 0.28984 | 61.7797 | -0.028522 | 0.048236 | 61.4105 | 0.007721 | 61.207 | 59.7499 | 51.9728 | 53.9843 | 59.0123 | 67.4103 | 59.7136 | 55.9852 | 123.1888 | 61.6073 | 123.0971 | 61.2889 | 61.3657 | 122.7279 | 61.3252 | 122.5244 | 61.8231 | 61.8636 | 61.7314 | 61.772
5731.0625 | 123.317 | -61.3129 | 61.8805 | -1.6134 | -9.4591 | -7.3927 | -2.36 | 6.0792 | -1.6405 | -5.3734 | 61.8713 | 0.28526 | 61.8117 | -0.033101 | 0.052814 | 61.4151 | 0.007721 | 61.2024 | 59.6995 | 51.8537 | 53.9202 | 58.9528 | 67.392 | 59.6724 | 55.9395 | 123.1842 | 61.5981 | 123.1246 | 61.2798 | 61.3657 | 122.7279 | 61.3206 | 122.5153 | 61.8185 | 61.8636 | 61.7589 | 61.804
5732.0938 | 123.3215 | -61.3037 | 61.8713 | -1.563 | -9.3859 | -7.3881 | -2.3509 | 6.1341 | -1.5901 | -5.3185 | 61.8713 | 0.28984 | 61.8026 | -0.028522 | 0.048236 | 61.4151 | 0.007721 | 61.207 | 59.7407 | 51.9178 | 53.9156 | 58.9528 | 67.4378 | 59.7136 | 55.9853 | 123.175 | 61.5936 | 123.1063 | 61.2752 | 61.3519 | 122.7188 | 61.3114 | 122.5107 | 61.8231 | 61.8636 | 61.7543 | 61.7948
5733.0781 | 123.4131 | -61.2762 | 61.8164 | -1.5447 | -9.3218 | -7.3927 | -2.3326 | 6.2119 | -1.5855 | -5.2498 | 61.8668 | 0.28984 | 61.7705 | -0.028522 | 0.052814 | 61.4151 | 0.007721 | 61.2116 | 59.7316 | 51.9545 | 53.8835 | 58.9437 | 67.4882 | 59.6907 | 56.0265 | 123.143 | 61.5661 | 123.0468 | 61.2477 | 61.3291 | 122.6913 | 61.284 | 122.4878 | 61.8139 | 61.859 | 61.7177 | 61.7628
5734.0938 | 123.3215 | -61.3083 | 61.8576 | -1.5813 | -9.1661 | -7.3561 | -2.3051 | 6.3401 | -1.6222 | -5.1857 | 61.8622 | 0.29442 | 61.7751 | -0.028522 | 0.043657 | 61.4197 | 0.007721 | 61.2207 | 59.727 | 52.1422 | 53.9522 | 59.0032 | 67.6484 | 59.6861 | 56.1226 | 123.1705 | 61.6027 | 123.0834 | 61.2798 | 61.3519 | 122.728 | 61.316 | 122.529 | 61.8185 | 61.8545 | 61.7314 | 61.7674
5735.0625 | 123.3353 | -61.3129 | 61.8805 | -1.6042 | -9.1661 | -7.3332 | -2.2914 | 6.4042 | -1.6084 | -5.1948 | 61.8713 | 0.28526 | 61.798 | -0.028522 | 0.052814 | 61.4242 | 0.003143 | 61.2207 | 59.7087 | 52.1468 | 53.9797 | 59.0215 | 67.7171 | 59.7044 | 56.118 | 123.1842 | 61.5981 | 123.1109 | 61.2843 | 61.3657 | 122.7371 | 61.316 | 122.5336 | 61.8185 | 61.8682 | 61.7452 | 61.7948
5736.1094 | 123.4131 | -61.29 | 61.7752 | -1.6271 | -9.2165 | -7.3973 | -2.3326 | 6.1204 | -1.645 | -5.2452 | 61.8713 | 0.28526 | 61.8117 | -0.033101 | 0.048236 | 61.4105 | 0.003143 | 61.2162 | 59.6629 | 52.0735 | 53.8927 | 58.9574 | 67.4103 | 59.6449 | 56.0448 | 123.1613 | 61.5752 | 123.1017 | 61.2569 | 61.3382 | 122.7005 | 61.2931 | 122.5061 | 61.8231 | 61.8682 | 61.7635 | 61.8086
5737.0625 | 123.3444 | -61.2854 | 61.853 | -1.65 | -9.2806 | -7.4019 | -2.3555 | 5.951 | -1.6725 | -5.3047 | 61.8759 | 0.29442 | 61.7934 | -0.028522 | 0.052814 | 61.4105 | 0.003143 | 61.2116 | 59.6354 | 52.0048 | 53.8835 | 58.9299 | 67.2364 | 59.6129 | 55.9807 | 123.1613 | 61.5798 | 123.0788 | 61.2569 | 61.3382 | 122.6959 | 61.2885 | 122.497 | 61.8231 | 61.8728 | 61.7406 | 61.7903
5738.0938 | 123.349 | -61.2717 | 61.8347 | -1.6408 | -9.2714 | -7.4156 | -2.36 | 5.9006 | -1.6634 | -5.3734 | 61.8713 | 0.28984 | 61.7843 | -0.023943 | 0.052814 | 61.4151 | 0.007721 | 61.2162 | 59.6308 | 52.0003 | 53.8561 | 58.9116 | 67.1723 | 59.6083 | 55.8983 | 123.143 | 61.5615 | 123.0559 | 61.2477 | 61.3245 | 122.6868 | 61.2794 | 122.4878 | 61.8185 | 61.8636 | 61.7314 | 61.7765
5739.0625 | 123.381 | -61.3174 | 61.7935 | -1.6225 | -9.2165 | -7.4339 | -2.3372 | 5.8365 | -1.6588 | -5.323 | 61.8805 | 0.28984 | 61.7934 | -0.023943 | 0.048236 | 61.4105 | 0.003143 | 61.2024 | 59.6949 | 52.101 | 53.8835 | 58.9803 | 67.154 | 59.6587 | 55.9944 | 123.1979 | 61.6073 | 123.1109 | 61.2935 | 61.3657 | 122.7279 | 61.3206 | 122.5199 | 61.8323 | 61.8773 | 61.7452 | 61.7903
5740.0625 | 123.3444 | -61.3129 | 61.8164 | -1.5859 | -8.9051 | -7.4522 | -2.3326 | 5.7953 | -1.6176 | -5.2498 | 61.8759 | 0.29442 | 61.8071 | -0.028522 | 0.043657 | 61.4151 | 0.007721 | 61.2207 | 59.727 | 52.4078 | 53.8606 | 58.9803 | 67.1082 | 59.6953 | 56.0631 | 123.1888 | 61.6073 | 123.12 | 61.2843 | 61.3565 | 122.7279 | 61.3206 | 122.5336 | 61.8323 | 61.8682 | 61.7635 | 61.7994
5741.0938 | 123.3353 | -61.2808 | 61.853 | -1.5309 | -8.7311 | -7.4797 | -2.2914 | 6.0654 | -1.5626 | -5.2315 | 61.8713 | 0.28984 | 61.798 | -0.033101 | 0.052814 | 61.4197 | 0.007721 | 61.2207 | 59.7499 | 52.5497 | 53.8011 | 58.9895 | 67.3463 | 59.7182 | 56.0493 | 123.1522 | 61.5707 | 123.0788 | 61.2477 | 61.3336 | 122.7005 | 61.2885 | 122.5016 | 61.8185 | 61.8636 | 61.7452 | 61.7903
5742.0625 | 123.3994 | -61.3083 | 61.8164 | -1.4943 | -8.5983 | -7.4705 | -2.328 | 6.0609 | -1.5214 | -5.1033 | 61.8576 | 0.28984 | 61.7614 | -0.028522 | 0.043657 | 61.4197 | 0.012299 | 61.2162 | 59.814 | 52.71 | 53.8377 | 58.9803 | 67.3691 | 59.7869 | 56.205 | 123.1659 | 61.5981 | 123.0697 | 61.2798 | 61.3519 | 122.728 | 61.3206 | 122.5245 | 61.8139 | 61.8453 | 61.7177 | 61.7491
5743.0781 | 123.4268 | -61.2946 | 61.8347 | -1.5401 | -8.8273 | -7.3698 | -2.3005 | 6.1478 | -1.5718 | -5.0896 | 61.853 | 0.28526 | 61.7751 | -0.028522 | 0.048236 | 61.4197 | 0.012299 | 61.2253 | 59.7545 | 52.4673 | 53.9247 | 58.994 | 67.4424 | 59.7228 | 56.205 | 123.1476 | 61.5798 | 123.0697 | 61.266 | 61.3428 | 122.7142 | 61.3069 | 122.5199 | 61.8048 | 61.8407 | 61.7269 | 61.7628
5744.0625 | 123.3353 | -61.2991 | 61.8576 | -1.6591 | -9.2027 | -7.3973 | -2.296 | 6.1753 | -1.6817 | -5.1674 | 61.8759 | 0.28984 | 61.8071 | -0.023943 | 0.043657 | 61.4242 | 0.007721 | 61.2024 | 59.64 | 52.0964 | 53.9018 | 59.0032 | 67.4744 | 59.6175 | 56.1318 | 123.175 | 61.589 | 123.1063 | 61.2752 | 61.3428 | 122.7234 | 61.3069 | 122.5016 | 61.8323 | 61.8682 | 61.7635 | 61.7994
5745.1094 | 123.317 | -61.2854 | 61.8576 | -1.6225 | -9.2943 | -7.3423 | -2.2593 | 6.2165 | -1.645 | -5.1994 | 61.8759 | 0.28069 | 61.8071 | -0.019364 | 0.048236 | 61.4151 | 0.012299 | 61.2024 | 59.6629 | 51.9911 | 53.9431 | 59.0261 | 67.5019 | 59.6404 | 56.086 | 123.1613 | 61.5661 | 123.0925 | 61.266 | 61.3336 | 122.7005 | 61.2977 | 122.4878 | 61.8277 | 61.8636 | 61.7589 | 61.7948
5746.0625 | 123.317 | -61.3312 | 61.8301 | -1.595 | -9.3721 | -7.3378 | -2.2547 | 6.1341 | -1.6267 | -5.1674 | 61.8668 | 0.28984 | 61.7705 | -0.028522 | 0.039079 | 61.4197 | 0.007721 | 61.1978 | 59.7361 | 51.959 | 53.9934 | 59.0764 | 67.4653 | 59.7044 | 56.1638 | 123.1979 | 61.621 | 123.1017 | 61.3027 | 61.3703 | 122.7508 | 61.3389 | 122.529 | 61.8277 | 61.859 | 61.7314 | 61.7628
5747.0781 | 123.2895 | -61.3083 | 61.8805 | -1.6408 | -9.4637 | -7.3515 | -2.2868 | 6.0975 | -1.6496 | -5.2177 | 61.8668 | 0.299 | 61.7797 | -0.028522 | 0.048236 | 61.4151 | 0.012299 | 61.2024 | 59.6675 | 51.8446 | 53.9568 | 59.0215 | 67.4058 | 59.6587 | 56.0905 | 123.175 | 61.6073 | 123.088 | 61.2798 | 61.3565 | 122.7234 | 61.3206 | 122.5107 | 61.8185 | 61.8545 | 61.7314 | 61.7674
5748.0625 | 123.3856 | -61.3083 | 61.8164 | -1.6958 | -9.6331 | -7.1775 | -2.2868 | 6.038 | -1.7183 | -5.2315 | 61.8759 | 0.28984 | 61.8026 | -0.033101 | 0.043657 | 61.4242 | 0.003143 | 61.1887 | 59.6125 | 51.6751 | 54.1308 | 59.0215 | 67.3463 | 59.59 | 56.0768 | 123.1842 | 61.5981 | 123.1109 | 61.2752 | 61.3519 | 122.7325 | 61.3114 | 122.497 | 61.8323 | 61.8728 | 61.7589 | 61.7994
5749.0781 | 123.381 | -61.29 | 61.8301 | -1.6271 | -9.5416 | -6.9852 | -2.2044 | 6.2714 | -1.645 | -5.1582 | 61.8713 | 0.28984 | 61.8071 | -0.033101 | 0.043657 | 61.4288 | 0.016878 | 61.2116 | 59.6629 | 51.7484 | 54.3048 | 59.0856 | 67.5614 | 59.6449 | 56.1318 | 123.1613 | 61.5798 | 123.0971 | 61.2569 | 61.3336 | 122.7188 | 61.3069 | 122.5016 | 61.8277 | 61.8545 | 61.7635 | 61.7903
5750.0625 | 123.2391 | -61.3632 | 61.8393 | -1.5767 | -9.5278 | -7.0173 | -2.3005 | 6.1387 | -1.6084 | -5.1857 | 61.8668 | 0.28526 | 61.7751 | -0.028522 | 0.048236 | 61.4151 | 0.012299 | 61.2024 | 59.7865 | 51.8354 | 54.346 | 59.0627 | 67.5019 | 59.7548 | 56.1775 | 123.23 | 61.6485 | 123.1383 | 61.3347 | 61.4115 | 122.7783 | 61.3755 | 122.5656 | 61.8185 | 61.8545 | 61.7269 | 61.7628
5751.0938 | 123.3719 | -61.2854 | 61.8439 | -1.5493 | -9.4042 | -7.1271 | -2.3509 | 6.1616 | -1.5764 | -5.1674 | 61.8576 | 0.29442 | 61.7705 | -0.023943 | 0.052814 | 61.4242 | 0.012299 | 61.2116 | 59.7361 | 51.8812 | 54.1583 | 58.9345 | 67.447 | 59.709 | 56.118 | 123.143 | 61.5798 | 123.0559 | 61.2615 | 61.3382 | 122.7096 | 61.2977 | 122.497 | 61.8048 | 61.8453 | 61.7177 | 61.7582
5752.0625 | 123.3948 | -61.2808 | 61.8256 | -1.6042 | -9.537 | -7.1134 | -2.4196 | 5.9098 | -1.6313 | -5.2086 | 61.8713 | 0.28984 | 61.7888 | -0.028522 | 0.043657 | 61.4151 | 0.012299 | 61.2024 | 59.6766 | 51.7438 | 54.1674 | 58.8613 | 67.1906 | 59.6495 | 56.0722 | 123.1522 | 61.5707 | 123.0697 | 61.2523 | 61.3245 | 122.6959 | 61.2931 | 122.4832 | 61.8277 | 61.859 | 61.7452 | 61.7765
5753.0781 | 123.3124 | -61.29 | 61.853 | -1.6317 | -9.5461 | -7.1775 | -2.4379 | 5.8457 | -1.6496 | -5.2635 | 61.8759 | 0.28984 | 61.8163 | -0.023943 | 0.057392 | 61.4151 | 0.012299 | 61.207 | 59.6583 | 51.7438 | 54.1125 | 58.8521 | 67.1357 | 59.6404 | 56.0265 | 123.1659 | 61.5798 | 123.1063 | 61.266 | 61.3474 | 122.7051 | 61.3023 | 122.497 | 61.8185 | 61.8636 | 61.7589 | 61.804
5754.0625 | 123.3032 | -61.29 | 61.8484 | -1.6454 | -9.0379 | -7.4843 | -2.4425 | 6.0288 | -1.6588 | -5.172 | 61.8668 | 0.29442 | 61.7843 | -0.028522 | 0.048236 | 61.4151 | 0.007721 | 61.2024 | 59.6446 | 52.2521 | 53.8057 | 58.8475 | 67.3188 | 59.6312 | 56.118 | 123.1567 | 61.5844 | 123.0742 | 61.2615 | 61.3382 | 122.7051 | 61.2977 | 122.4924 | 61.8185 | 61.859 | 61.736 | 61.7765
5755.0938 | 123.3261 | -61.29 | 61.7935 | -1.6454 | -9.0837 | -7.5072 | -2.4058 | 6.0837 | -1.6588 | -5.2406 | 61.8668 | 0.29442 | 61.7659 | -0.033101 | 0.043657 | 61.4105 | 0.012299 | 61.2024 | 59.6446 | 52.2063 | 53.7828 | 58.8841 | 67.3737 | 59.6312 | 56.0493 | 123.1567 | 61.5844 | 123.0559 | 61.2569 | 61.3336 | 122.7005 | 61.3023 | 122.4924 | 61.8231 | 61.8545 | 61.7223 | 61.7536
5756.0625 | 123.3536 | -61.2762 | 61.8393 | -1.6454 | -9.1844 | -7.466 | -2.4058 | 6.1982 | -1.6542 | -5.2452 | 61.8805 | 0.28526 | 61.7888 | -0.033101 | 0.048236 | 61.4242 | 0.012299 | 61.207 | 59.6308 | 52.0918 | 53.8103 | 58.8704 | 67.4744 | 59.622 | 56.031 | 123.1567 | 61.5615 | 123.0651 | 61.2431 | 61.3245 | 122.7005 | 61.2885 | 122.4832 | 61.8323 | 61.8682 | 61.7406 | 61.7765
5757.0938 | 123.4268 | -61.2625 | 61.8164 | -1.6729 | -9.2165 | -7.4934 | -2.4196 | 6.2577 | -1.6725 | -5.2681 | 61.8713 | 0.28526 | 61.8163 | -0.033101 | 0.043657 | 61.4197 | 0.007721 | 61.1978 | 59.5896 | 52.046 | 53.7691 | 58.8429 | 67.5202 | 59.59 | 55.9944 | 123.1338 | 61.5478 | 123.0788 | 61.2294 | 61.3062 | 122.6822 | 61.2702 | 122.4604 | 61.8277 | 61.8636 | 61.7726 | 61.8086
5758.0625 | 123.3444 | -61.2946 | 61.8256 | -1.6637 | -9.3401 | -7.5575 | -2.4379 | 6.2257 | -1.7091 | -5.2589 | 61.8713 | 0.28984 | 61.7888 | -0.033101 | 0.048236 | 61.4151 | 0.003143 | 61.1978 | 59.6308 | 51.9545 | 53.737 | 58.8567 | 67.5202 | 59.5854 | 56.0356 | 123.1659 | 61.5844 | 123.0834 | 61.2615 | 61.3428 | 122.7096 | 61.2977 | 122.4924 | 61.8231 | 61.8682 | 61.7406 | 61.7857
5759.0781 | 123.381 | -61.2579 | 61.8118 | -1.6775 | -9.4317 | -7.5575 | -2.4654 | 6.2302 | -1.7183 | -5.2544 | 61.8622 | 0.28984 | 61.7751 | -0.023943 | 0.052814 | 61.4059 | 0.012299 | 61.1978 | 59.5805 | 51.8263 | 53.7004 | 58.7926 | 67.4882 | 59.5396 | 56.0036 | 123.1201 | 61.5478 | 123.033 | 61.234 | 61.3107 | 122.6639 | 61.2702 | 122.4558 | 61.8094 | 61.8499 | 61.7223 | 61.7628
5760.0625 | 123.381 | -61.29 | 61.7935 | -1.6637 | -9.5004 | -7.5942 | -2.502 | 6.1158 | -1.6954 | -5.3185 | 61.8805 | 0.29442 | 61.7888 | -0.033101 | 0.039079 | 61.4151 | 0.012299 | 61.1887 | 59.6263 | 51.7896 | 53.6958 | 58.788 | 67.4058 | 59.5946 | 55.9715 | 123.1705 | 61.5844 | 123.0788 | 61.2569 | 61.3291 | 122.7051 | 61.3023 | 122.4787 | 61.8414 | 61.8682 | 61.7498 | 61.7765
5761.0938 | 123.4177 | -61.2808 | 61.7661 | -1.6729 | -9.5004 | -7.5804 | -2.4745 | 6.2211 | -1.7183 | -5.3414 | 61.8805 | 0.28984 | 61.8209 | -0.028522 | 0.052814 | 61.4105 | 0.012299 | 61.1887 | 59.6079 | 51.7805 | 53.7004 | 58.8063 | 67.5019 | 59.5625 | 55.9395 | 123.1613 | 61.5707 | 123.1017 | 61.2523 | 61.3336 | 122.6913 | 61.2931 | 122.4695 | 61.8277 | 61.8682 | 61.7681 | 61.8086
5762.0625 | 123.3994 | -61.2854 | 61.8027 | -1.6683 | -9.4317 | -7.5438 | -2.4654 | 6.2806 | -1.6954 | -5.3368 | 61.8713 | 0.29442 | 61.7888 | -0.023943 | 0.048236 | 61.4105 | 0.003143 | 61.2024 | 59.6171 | 51.8537 | 53.7416 | 58.82 | 67.566 | 59.59 | 55.9486 | 123.1567 | 61.5798 | 123.0742 | 61.2615 | 61.3336 | 122.6959 | 61.2885 | 122.4878 | 61.8231 | 61.8682 | 61.7406 | 61.7857
5763.0781 | 123.4406 | -61.3037 | 61.7935 | -1.6225 | -9.3172 | -7.5713 | -2.4699 | 6.0654 | -1.645 | -5.2589 | 61.8713 | 0.28984 | 61.7797 | -0.033101 | 0.048236 | 61.4197 | 0.007721 | 61.1933 | 59.6812 | 51.9865 | 53.7324 | 58.8338 | 67.3691 | 59.6587 | 56.0448 | 123.175 | 61.5936 | 123.0834 | 61.2706 | 61.3519 | 122.7234 | 61.3114 | 122.497 | 61.8231 | 61.8636 | 61.7314 | 61.772
5764.0625 | 123.2529 | -61.2991 | 61.8942 | -1.7965 | -9.2165 | -7.6812 | -2.5432 | 6.1799 | -1.819 | -5.1628 | 61.8759 | 0.28984 | 61.7888 | -0.033101 | 0.048236 | 61.4105 | 0.012299 | 61.1978 | 59.5026 | 52.0827 | 53.618 | 58.7559 | 67.479 | 59.4801 | 56.1363 | 123.175 | 61.589 | 123.088 | 61.266 | 61.3474 | 122.7096 | 61.3114 | 122.497 | 61.8277 | 61.8636 | 61.7406 | 61.7765
5765.1094 | 123.3856 | -61.2946 | 61.8301 | -1.824 | -9.2668 | -7.7086 | -2.5936 | 6.0746 | -1.8648 | -5.172 | 61.8805 | 0.28526 | 61.8163 | -0.028522 | 0.043657 | 61.4151 | 0.007721 | 61.1841 | 59.4706 | 52.0277 | 53.5859 | 58.701 | 67.3691 | 59.4297 | 56.1226 | 123.175 | 61.5798 | 123.1109 | 61.266 | 61.3382 | 122.7096 | 61.3023 | 122.4787 | 61.8368 | 61.8728 | 61.7726 | 61.8086
5766.0625 | 123.2941 | -61.2671 | 61.8622 | -1.8835 | -9.2897 | -7.7269 | -2.5936 | 6.0105 | -1.9152 | -5.2544 | 61.8896 | 0.28984 | 61.8026 | -0.023943 | 0.048236 | 61.4014 | 0.016878 | 61.1978 | 59.3836 | 51.9774 | 53.5401 | 58.6735 | 67.2776 | 59.3519 | 56.0127 | 123.1567 | 61.5569 | 123.0697 | 61.2431 | 61.3153 | 122.6684 | 61.284 | 122.4649 | 61.8414 | 61.8728 | 61.7543 | 61.7857
5767.0938 | 123.349 | -61.2854 | 61.853 | -1.8881 | -9.3859 | -7.6125 | -2.6073 | 6.0197 | -1.9152 | -5.2727 | 61.8851 | 0.28984 | 61.7888 | -0.03768 | 0.048236 | 61.4105 | 0.007721 | 61.1978 | 59.3973 | 51.8995 | 53.6729 | 58.6781 | 67.3051 | 59.3702 | 56.0127 | 123.1705 | 61.5752 | 123.0742 | 61.2477 | 61.3336 | 122.6959 | 61.2931 | 122.4832 | 61.8368 | 61.8773 | 61.7406 | 61.7811
5768.0625 | 123.3902 | -61.2762 | 61.8164 | -1.9247 | -9.4134 | -7.6079 | -2.6439 | 5.9235 | -1.9518 | -5.2315 | 61.8759 | 0.28984 | 61.7934 | -0.03768 | 0.048236 | 61.4105 | 0.003143 | 61.1933 | 59.3516 | 51.8629 | 53.6683 | 58.6323 | 67.1998 | 59.3244 | 56.0448 | 123.1522 | 61.5661 | 123.0697 | 61.2386 | 61.3245 | 122.6868 | 61.2794 | 122.4695 | 61.8277 | 61.8728 | 61.7452 | 61.7903
5769.0938 | 123.3353 | -61.2717 | 61.8759 | -1.9247 | -9.4591 | -7.6171 | -2.6531 | 5.9052 | -1.9472 | -5.1857 | 61.8896 | 0.29442 | 61.8209 | -0.028522 | 0.057392 | 61.4059 | 0.012299 | 61.1978 | 59.347 | 51.8125 | 53.6546 | 58.6186 | 67.1769 | 59.3244 | 56.086 | 123.1613 | 61.5661 | 123.0925 | 61.2431 | 61.3291 | 122.6776 | 61.284 | 122.4695 | 61.8323 | 61.8773 | 61.7635 | 61.8086
5770.0625 | 123.317 | -61.2854 | 61.8759 | -1.943 | -9.5416 | -7.7041 | -2.6714 | 5.9006 | -1.9747 | -5.2361 | 61.8896 | 0.28984 | 61.8026 | -0.023943 | 0.052814 | 61.4059 | 0.003143 | 61.1887 | 59.3424 | 51.7438 | 53.5813 | 58.614 | 67.186 | 59.3107 | 56.0493 | 123.175 | 61.5752 | 123.088 | 61.2615 | 61.3382 | 122.6913 | 61.2885 | 122.4741 | 61.8368 | 61.8865 | 61.7498 | 61.7994
5771.0625 | 123.4131 | -61.2808 | 61.8073 | -1.9659 | -9.3996 | -7.7269 | -2.6897 | 5.9327 | -1.9838 | -5.1857 | 61.8851 | 0.28984 | 61.7934 | -0.028522 | 0.048236 | 61.4014 | 0.007721 | 61.1933 | 59.3149 | 51.8812 | 53.5539 | 58.5911 | 67.2135 | 59.297 | 56.0951 | 123.1659 | 61.5707 | 123.0742 | 61.2523 | 61.3291 | 122.6822 | 61.2885 | 122.4741 | 61.8368 | 61.8773 | 61.7452 | 61.7857
5772.0938 | 123.2437 | -61.2991 | 61.8576 | -1.9613 | -9.3309 | -7.7956 | -2.676 | 5.9647 | -1.9976 | -5.2086 | 61.8851 | 0.30358 | 61.8117 | -0.03768 | 0.048236 | 61.4059 | 0.007721 | 61.2024 | 59.3378 | 51.9682 | 53.5035 | 58.6232 | 67.2639 | 59.3015 | 56.0905 | 123.1842 | 61.6027 | 123.1109 | 61.2615 | 61.3474 | 122.7051 | 61.3069 | 122.5016 | 61.8368 | 61.8773 | 61.7635 | 61.804
5773.0625 | 123.4085 | -61.2762 | 61.8027 | -1.8835 | -9.4912 | -7.7636 | -2.6348 | 6.1158 | -1.9106 | -5.2223 | 61.8851 | 0.299 | 61.8117 | -0.033101 | 0.043657 | 61.4014 | 0.007721 | 61.207 | 59.3928 | 51.785 | 53.5127 | 58.6415 | 67.392 | 59.3657 | 56.0539 | 123.1613 | 61.5752 | 123.088 | 61.2431 | 61.3199 | 122.6776 | 61.284 | 122.4832 | 61.8414 | 61.8773 | 61.7681 | 61.804
5774.0781 | 123.3902 | -61.3083 | 61.8118 | -1.8514 | -9.5553 | -7.791 | -2.621 | 6.07 | -1.8831 | -5.3414 | 61.8759 | 0.28984 | 61.7934 | -0.033101 | 0.039079 | 61.4014 | -0.001436 | 61.2024 | 59.4569 | 51.753 | 53.5172 | 58.6873 | 67.3783 | 59.4252 | 55.9669 | 123.1842 | 61.5981 | 123.1017 | 61.2752 | 61.3474 | 122.7096 | 61.3069 | 122.5107 | 61.8368 | 61.8773 | 61.7543 | 61.7948
5775.0625 | 123.3398 | -61.29 | 61.8439 | -1.8514 | -9.4179 | -7.8185 | -2.6622 | 6.0334 | -1.8694 | -5.3139 | 61.8805 | 0.28526 | 61.8209 | -0.023943 | 0.043657 | 61.4014 | 0.007721 | 61.2024 | 59.4385 | 51.872 | 53.4715 | 58.6277 | 67.3234 | 59.4206 | 55.9761 | 123.1705 | 61.5752 | 123.1109 | 61.266 | 61.3336 | 122.6913 | 61.2977 | 122.4924 | 61.8368 | 61.8728 | 61.7772 | 61.8132
5776.1094 | 123.3948 | -61.2717 | 61.8347 | -1.8148 | -9.3538 | -7.878 | -2.6531 | 5.9235 | -1.8419 | -5.3826 | 61.8851 | 0.28526 | 61.7934 | -0.033101 | 0.043657 | 61.4059 | 0.007721 | 61.1978 | 59.4569 | 51.9178 | 53.3936 | 58.6186 | 67.1952 | 59.4297 | 55.8891 | 123.1567 | 61.5569 | 123.0651 | 61.2386 | 61.3153 | 122.6776 | 61.2794 | 122.4695 | 61.8414 | 61.8773 | 61.7498 | 61.7857
5777.0625 | 123.381 | -61.2854 | 61.7981 | -1.7644 | -9.3309 | -7.9147 | -2.5798 | 5.9327 | -1.787 | -5.5794 | 61.8851 | 0.29442 | 61.7888 | -0.03768 | 0.048236 | 61.4059 | 0.007721 | 61.1887 | 59.521 | 51.9545 | 53.3707 | 58.7056 | 67.2181 | 59.4984 | 55.706 | 123.1705 | 61.5798 | 123.0742 | 61.2477 | 61.3336 | 122.6913 | 61.2931 | 122.4741 | 61.8368 | 61.8773 | 61.7406 | 61.7811
5778.0938 | 123.262 | -61.2854 | 61.8622 | -1.7003 | -9.0837 | -7.9376 | -2.6577 | 5.9327 | -1.732 | -5.6069 | 61.8851 | 0.28984 | 61.8255 | -0.023943 | 0.048236 | 61.4059 | 0.007721 | 61.1887 | 59.5851 | 52.2017 | 53.3478 | 58.6277 | 67.2181 | 59.5534 | 55.6785 | 123.1705 | 61.5752 | 123.1109 | 61.2615 | 61.3336 | 122.6913 | 61.2931 | 122.4741 | 61.8368 | 61.8773 | 61.7772 | 61.8177
5779.0625 | 123.2849 | -61.3312 | 61.8713 | -1.7324 | -9.0608 | -7.9055 | -2.6439 | 6.0471 | -1.7641 | -5.5611 | 61.8805 | 0.28984 | 61.7888 | -0.028522 | 0.052814 | 61.4151 | 0.012299 | 61.1887 | 59.5988 | 52.2704 | 53.4257 | 58.6873 | 67.3783 | 59.5671 | 55.7701 | 123.2117 | 61.621 | 123.12 | 61.3027 | 61.384 | 122.7463 | 61.3435 | 122.5199 | 61.8277 | 61.8682 | 61.736 | 61.7765
5780.0781 | 123.3856 | -61.2991 | 61.8256 | -1.8743 | -8.983 | -7.9009 | -2.6577 | 6.0242 | -1.9014 | -5.4879 | 61.8805 | 0.28984 | 61.7934 | -0.028522 | 0.043657 | 61.4105 | 0.021456 | 61.1887 | 59.4248 | 52.3162 | 53.3982 | 58.6415 | 67.3234 | 59.3977 | 55.8113 | 123.1796 | 61.589 | 123.0925 | 61.2706 | 61.3428 | 122.7096 | 61.3206 | 122.4878 | 61.8368 | 61.859 | 61.7498 | 61.772
5781.0625 | 123.3353 | -61.29 | 61.8576 | -1.8835 | -9.0745 | -7.8964 | -2.7126 | 5.8091 | -1.9106 | -5.4146 | 61.8942 | 0.28526 | 61.8255 | -0.033101 | 0.048236 | 61.4059 | 0.003143 | 61.1841 | 59.4065 | 52.2155 | 53.3936 | 58.5774 | 67.099 | 59.3794 | 55.8754 | 123.1842 | 61.5752 | 123.1154 | 61.2569 | 61.3382 | 122.6959 | 61.2931 | 122.4741 | 61.846 | 61.8911 | 61.7772 | 61.8223
5782.0781 | 123.3032 | -61.2854 | 61.8896 | -1.9751 | -9.4042 | -7.8597 | -2.7446 | 6.0197 | -1.9884 | -5.3597 | 61.8851 | 0.29442 | 61.7934 | -0.019364 | 0.052814 | 61.4014 | 0.007721 | 61.1795 | 59.3103 | 51.8812 | 53.4257 | 58.5408 | 67.3051 | 59.297 | 55.9257 | 123.1705 | 61.5798 | 123.0788 | 61.266 | 61.3382 | 122.6868 | 61.2931 | 122.4649 | 61.8323 | 61.8773 | 61.7406 | 61.7857
5783.0625 | 123.3673 | -61.2671 | 61.8164 | -1.9247 | -9.5187 | -7.8735 | -2.795 | 5.9235 | -1.9472 | -5.497 | 61.8851 | 0.29442 | 61.8117 | -0.033101 | 0.052814 | 61.4014 | 0.012299 | 61.175 | 59.3424 | 51.7484 | 53.3936 | 58.4721 | 67.1906 | 59.3199 | 55.7701 | 123.1522 | 61.5615 | 123.0788 | 61.234 | 61.3199 | 122.6684 | 61.2794 | 122.442 | 61.8323 | 61.8728 | 61.7589 | 61.7994
5784.0938 | 123.4085 | -61.2625 | 61.8301 | -1.9247 | -9.6194 | -7.9513 | -2.8454 | 5.8777 | -1.9472 | -5.8037 | 61.8896 | 0.28069 | 61.8346 | -0.028522 | 0.052814 | 61.3968 | 0.003143 | 61.1795 | 59.3378 | 51.6431 | 53.3112 | 58.4171 | 67.1403 | 59.3153 | 55.4588 | 123.1522 | 61.5432 | 123.0971 | 61.234 | 61.3153 | 122.6593 | 61.2657 | 122.442 | 61.8368 | 61.8865 | 61.7818 | 61.8315
5785.0625 | 123.3856 | -61.2671 | 61.8256 | -1.8835 | -9.363 | -7.9238 | -2.8042 | 5.8457 | -1.906 | -5.8633 | 61.8851 | 0.29442 | 61.7934 | -0.033101 | 0.052814 | 61.4014 | 0.012299 | 61.1933 | 59.3836 | 51.9041 | 53.3433 | 58.4629 | 67.1128 | 59.3611 | 55.4038 | 123.1522 | 61.5615 | 123.0605 | 61.234 | 61.3199 | 122.6684 | 61.2794 | 122.4604 | 61.8323 | 61.8728 | 61.7406 | 61.7811
5786.0938 | 123.4039 | -61.2534 | 61.8439 | -1.8331 | -9.3401 | -7.9101 | -2.7446 | 6.0013 | -1.8648 | -5.8266 | 61.8805 | 0.28984 | 61.7934 | -0.033101 | 0.057392 | 61.4059 | 0.003143 | 61.1841 | 59.4202 | 51.9133 | 53.3433 | 58.5087 | 67.2547 | 59.3885 | 55.4267 | 123.1338 | 61.5432 | 123.0468 | 61.2203 | 61.3107 | 122.6593 | 61.2565 | 122.4375 | 61.8231 | 61.8773 | 61.736 | 61.7903
5787.0625 | 123.3261 | -61.2717 | 61.8668 | -1.9018 | -9.4179 | -8.0429 | -2.8728 | 5.7999 | -1.9243 | -5.877 | 61.8942 | 0.28984 | 61.8255 | -0.033101 | 0.052814 | 61.3968 | 0.012299 | 61.1841 | 59.3699 | 51.8537 | 53.2288 | 58.3988 | 67.0716 | 59.3473 | 55.3947 | 123.1659 | 61.5615 | 123.0971 | 61.2386 | 61.3245 | 122.6684 | 61.284 | 122.4558 | 61.8414 | 61.8819 | 61.7726 | 61.8132
5788.0938 | 123.4039 | -61.2762 | 61.8759 | -1.9613 | -9.4912 | -8.0429 | -2.8774 | 5.832 | -1.9976 | -5.9777 | 61.8988 | 0.29442 | 61.83 | -0.033101 | 0.048236 | 61.3922 | 0.012299 | 61.1887 | 59.3149 | 51.785 | 53.2334 | 58.3988 | 67.1082 | 59.2787 | 55.2985 | 123.175 | 61.5707 | 123.1063 | 61.2431 | 61.3245 | 122.6684 | 61.2885 | 122.4649 | 61.8506 | 61.8865 | 61.7818 | 61.8177
5789.0625 | 123.4085 | -61.2396 | 61.8942 | -1.9247 | -9.5828 | -8.0612 | -2.8499 | 5.8182 | -1.9472 | -5.8587 | 61.8942 | 0.28984 | 61.798 | -0.019364 | 0.052814 | 61.3968 | 0.007721 | 61.1933 | 59.3149 | 51.6568 | 53.1784 | 58.3897 | 67.0579 | 59.2924 | 55.3809 | 123.1338 | 61.5295 | 123.0376 | 61.2203 | 61.2924 | 122.6364 | 61.2473 | 122.4329 | 61.8414 | 61.8865 | 61.7452 | 61.7903
5790.0938 | 123.4085 | -61.2625 | 61.7889 | -1.8743 | -9.7705 | -7.965 | -2.8087 | 6.0013 | -1.9106 | -5.79 | 61.8896 | 0.299 | 61.798 | -0.03768 | 0.039079 | 61.3876 | 0.012299 | 61.1887 | 59.3882 | 51.492 | 53.2975 | 58.4538 | 67.2639 | 59.3519 | 55.4725 | 123.1522 | 61.5615 | 123.0605 | 61.2248 | 61.3016 | 122.6501 | 61.2748 | 122.4512 | 61.8506 | 61.8773 | 61.7589 | 61.7857
5791.0625 | 123.3536 | -61.2671 | 61.8622 | -1.856 | -9.7156 | -7.846 | -2.7355 | 6.038 | -1.8877 | -5.671 | 61.8896 | 0.299 | 61.8209 | -0.028522 | 0.052814 | 61.4014 | 0.007721 | 61.1887 | 59.4111 | 51.5515 | 53.4211 | 58.5316 | 67.3051 | 59.3794 | 55.5961 | 123.1567 | 61.5661 | 123.088 | 61.2386 | 61.3199 | 122.6684 | 61.2748 | 122.4558 | 61.8368 | 61.8819 | 61.7681 | 61.8132
5792.0938 | 123.3856 | -61.2808 | 61.8256 | -1.9613 | -9.83 | -7.9513 | -2.8271 | 6.0883 | -1.9838 | -5.8358 | 61.8988 | 0.29442 | 61.8346 | -0.028522 | 0.048236 | 61.3876 | 0.012299 | 61.1841 | 59.3195 | 51.4508 | 53.3295 | 58.4538 | 67.3691 | 59.297 | 55.445 | 123.1796 | 61.5752 | 123.1154 | 61.2523 | 61.3291 | 122.6684 | 61.2931 | 122.4649 | 61.8506 | 61.8865 | 61.7864 | 61.8223
5793.0625 | 123.2849 | -61.2808 | 61.8759 | -1.9934 | -9.7751 | -7.9559 | -2.8179 | 6.2028 | -2.0113 | -5.8358 | 61.8942 | 0.28984 | 61.8071 | -0.028522 | 0.039079 | 61.3968 | 0.007721 | 61.1978 | 59.2875 | 51.5057 | 53.3249 | 58.4629 | 67.4836 | 59.2695 | 55.445 | 123.175 | 61.5707 | 123.088 | 61.2523 | 61.3199 | 122.6776 | 61.2885 | 122.4787 | 61.8551 | 61.8865 | 61.7681 | 61.7994
5794.0781 | 123.3261 | -61.2717 | 61.8256 | -1.9476 | -9.7385 | -7.9879 | -2.8591 | 6.2577 | -1.9793 | -5.7717 | 61.8896 | 0.28526 | 61.8026 | -0.028522 | 0.043657 | 61.3968 | 0.003143 | 61.1933 | 59.3241 | 51.5332 | 53.2837 | 58.4126 | 67.5294 | 59.2924 | 55.5 | 123.1613 | 61.5569 | 123.0742 | 61.2431 | 61.3153 | 122.6684 | 61.2748 | 122.4649 | 61.846 | 61.8865 | 61.7589 | 61.7994
5795.0625 | 123.4177 | -61.2671 | 61.8347 | -1.8514 | -9.5553 | -7.9284 | -2.8042 | 6.1524 | -1.874 | -5.6939 | 61.8896 | 0.28526 | 61.83 | -0.033101 | 0.048236 | 61.3922 | 0.007721 | 61.207 | 59.4157 | 51.7118 | 53.3387 | 58.4629 | 67.4195 | 59.3931 | 55.5732 | 123.1567 | 61.5524 | 123.0971 | 61.234 | 61.3153 | 122.6593 | 61.2748 | 122.4741 | 61.8414 | 61.8819 | 61.7818 | 61.8223
5796.0938 | 123.3948 | -61.2854 | 61.8347 | -1.8606 | -9.3859 | -7.9742 | -2.8179 | 6.2989 | -1.874 | -5.7488 | 61.8851 | 0.29442 | 61.8209 | -0.033101 | 0.052814 | 61.4014 | 0.007721 | 61.2024 | 59.4248 | 51.8995 | 53.3112 | 58.4675 | 67.5843 | 59.4114 | 55.5366 | 123.1705 | 61.5798 | 123.1063 | 61.2523 | 61.3382 | 122.6868 | 61.2931 | 122.4878 | 61.8323 | 61.8773 | 61.7681 | 61.8132
5797.0625 | 123.3398 | -61.2213 | 61.8301 | -1.9338 | -9.3126 | -7.965 | -2.8179 | 6.3996 | -1.961 | -5.5932 | 61.8851 | 0.28984 | 61.7934 | -0.023943 | 0.043657 | 61.4014 | 0.007721 | 61.2024 | 59.2875 | 51.9087 | 53.2563 | 58.4034 | 67.6209 | 59.2604 | 55.6282 | 123.1064 | 61.5112 | 123.0147 | 61.1974 | 61.265 | 122.6227 | 61.229 | 122.4237 | 61.8414 | 61.8773 | 61.7498 | 61.7857
5798.0938 | 123.4543 | -61.2396 | 61.8301 | -2.0071 | -9.3035 | -7.9742 | -2.8316 | 6.3538 | -2.0205 | -5.6984 | 61.8851 | 0.28984 | 61.7888 | -0.033101 | 0.048236 | 61.4014 | 0.012299 | 61.2024 | 59.2325 | 51.9362 | 53.2654 | 58.408 | 67.5935 | 59.2191 | 55.5412 | 123.1247 | 61.5295 | 123.0285 | 61.2065 | 61.2879 | 122.641 | 61.2519 | 122.442 | 61.8368 | 61.8728 | 61.7406 | 61.7765
5799.0625 | 123.3948 | -61.2442 | 61.8668 | -1.9522 | -9.0608 | -8.0383 | -2.8362 | 6.2165 | -1.9747 | -5.6389 | 61.8851 | 0.29442 | 61.8163 | -0.023943 | 0.048236 | 61.4059 | 0.016878 | 61.1887 | 59.292 | 52.1834 | 53.2059 | 58.408 | 67.4607 | 59.2695 | 55.6053 | 123.1293 | 61.5386 | 123.0605 | 61.2203 | 61.2924 | 122.6501 | 61.2611 | 122.4329 | 61.8368 | 61.8682 | 61.7681 | 61.7994
5800.0781 | 123.381 | -61.2991 | 61.8073 | -1.9567 | -9.2897 | -8.0383 | -2.8866 | 6.0837 | -1.9747 | -5.6527 | 61.8896 | 0.28984 | 61.8255 | -0.033101 | 0.052814 | 61.3968 | 0.003143 | 61.1841 | 59.3424 | 52.0094 | 53.2608 | 58.4126 | 67.3829 | 59.3244 | 55.6465 | 123.1888 | 61.589 | 123.1246 | 61.266 | 61.3519 | 122.6959 | 61.3023 | 122.4832 | 61.8368 | 61.8865 | 61.7726 | 61.8223
5801.0625 | 123.3902 | -61.2396 | 61.8713 | -1.9476 | -9.3859 | -8.0658 | -2.9003 | 5.777 | -1.961 | -5.79 | 61.8896 | 0.28984 | 61.8117 | -0.028522 | 0.052814 | 61.3922 | 0.016878 | 61.1795 | 59.292 | 51.8537 | 53.1739 | 58.3393 | 67.0166 | 59.2787 | 55.4496 | 123.1293 | 61.5295 | 123.0513 | 61.2111 | 61.2924 | 122.6318 | 61.2565 | 122.4192 | 61.8368 | 61.8728 | 61.7589 | 61.7948
5802.0938 | 123.349 | -61.2946 | 61.8256 | -1.9201 | -9.3859 | -8.052 | -2.8912 | 5.7267 | -1.9335 | -5.7122 | 61.8851 | 0.28984 | 61.7888 | -0.033101 | 0.052814 | 61.3922 | -0.001436 | 61.1841 | 59.3744 | 51.9087 | 53.2425 | 58.4034 | 67.0212 | 59.3611 | 55.5824 | 123.1796 | 61.5844 | 123.0834 | 61.2615 | 61.3474 | 122.6868 | 61.2931 | 122.4787 | 61.8323 | 61.8865 | 61.736 | 61.7903
5803.0625 | 123.2895 | -61.2946 | 61.8851 | -1.8926 | -9.3813 | -8.0703 | -2.9049 | 5.7038 | -1.9106 | -5.7442 | 61.8942 | 0.28984 | 61.8071 | -0.023943 | 0.048236 | 61.3922 | 0.012299 | 61.1841 | 59.4019 | 51.9132 | 53.2242 | 58.3897 | 66.9983 | 59.384 | 55.5503 | 123.1888 | 61.5844 | 123.1017 | 61.2706 | 61.3428 | 122.6868 | 61.3069 | 122.4787 | 61.846 | 61.8819 | 61.7589 | 61.7948
5804.0938 | 123.3353 | -61.3129 | 61.8713 | -1.8972 | -9.4317 | -8.1436 | -2.8866 | 5.9098 | -1.9152 | -5.7259 | 61.8942 | 0.299 | 61.8392 | -0.028522 | 0.052814 | 61.3922 | 0.007721 | 61.1841 | 59.4156 | 51.8812 | 53.1693 | 58.4263 | 67.2227 | 59.3977 | 55.5869 | 123.2071 | 61.6119 | 123.1521 | 61.2843 | 61.3657 | 122.7051 | 61.3206 | 122.497 | 61.8414 | 61.8865 | 61.7864 | 61.8315
5805.0625 | 123.381 | -61.2671 | 61.821 | -1.8835 | -9.3401 | -8.1344 | -2.9186 | 5.7953 | -1.9014 | -5.6481 | 61.8896 | 0.28984 | 61.8163 | -0.028522 | 0.048236 | 61.3922 | 0.003143 | 61.1933 | 59.3836 | 51.927 | 53.1327 | 58.3485 | 67.0624 | 59.3657 | 55.619 | 123.1567 | 61.5569 | 123.0834 | 61.2386 | 61.3153 | 122.6593 | 61.2702 | 122.4604 | 61.8414 | 61.8865 | 61.7681 | 61.8132
5806.0938 | 123.317 | -61.2991 | 61.853 | -1.8652 | -9.3355 | -8.0887 | -2.9095 | 5.8686 | -1.8923 | -5.5336 | 61.8851 | 0.299 | 61.7888 | -0.033101 | 0.039079 | 61.3922 | 0.012299 | 61.1841 | 59.434 | 51.9636 | 53.2105 | 58.3897 | 67.1677 | 59.4069 | 55.7655 | 123.1842 | 61.5981 | 123.088 | 61.266 | 61.3382 | 122.6913 | 61.3114 | 122.4832 | 61.846 | 61.8728 | 61.7498 | 61.7765
5807.0625 | 123.2758 | -61.2671 | 61.8851 | -1.8972 | -9.4225 | -8.139 | -2.9873 | 5.7862 | -1.906 | -5.5245 | 61.8851 | 0.28526 | 61.798 | -0.023943 | 0.057392 | 61.3876 | 0.007721 | 61.1841 | 59.3699 | 51.8446 | 53.1281 | 58.2798 | 67.0533 | 59.3611 | 55.7426 | 123.1522 | 61.5524 | 123.0651 | 61.2431 | 61.3245 | 122.6547 | 61.2748 | 122.4512 | 61.8277 | 61.8773 | 61.7406 | 61.7903
5808.0938 | 123.23 | -61.2579 | 61.8942 | -1.8423 | -9.4179 | -8.1299 | -2.9232 | 5.832 | -1.8694 | -5.5107 | 61.8942 | 0.28526 | 61.83 | -0.028522 | 0.043657 | 61.4014 | 0.012299 | 61.1933 | 59.4157 | 51.84 | 53.1281 | 58.3347 | 67.0899 | 59.3885 | 55.7472 | 123.1522 | 61.5432 | 123.088 | 61.2294 | 61.3016 | 122.6593 | 61.2702 | 122.4512 | 61.8506 | 61.8819 | 61.7864 | 61.8177
5809.0625 | 123.3307 | -61.2808 | 61.8484 | -1.8697 | -9.4042 | -8.1299 | -2.8774 | 6.0883 | -1.8877 | -5.5107 | 61.8942 | 0.29442 | 61.8255 | -0.028522 | 0.048236 | 61.4014 | 0.012299 | 61.1841 | 59.4111 | 51.8766 | 53.151 | 58.4034 | 67.3691 | 59.3931 | 55.7701 | 123.175 | 61.5752 | 123.1063 | 61.2523 | 61.3291 | 122.6822 | 61.2931 | 122.4649 | 61.846 | 61.8819 | 61.7772 | 61.8132
5810.0938 | 123.3627 | -61.2808 | 61.8164 | -1.9201 | -9.5828 | -8.0887 | -2.8957 | 6.2577 | -1.9472 | -5.5748 | 61.8851 | 0.28984 | 61.8026 | -0.033101 | 0.052814 | 61.3968 | 0.016878 | 61.1841 | 59.3607 | 51.698 | 53.1922 | 58.3851 | 67.5385 | 59.3336 | 55.706 | 123.1659 | 61.5707 | 123.0834 | 61.2477 | 61.3336 | 122.6776 | 61.2977 | 122.4649 | 61.8323 | 61.8682 | 61.7498 | 61.7857
5811.0625 | 123.2803 | -61.2717 | 61.8896 | -1.8881 | -9.7201 | -8.1665 | -2.9324 | 6.1341 | -1.9289 | -5.7625 | 61.8942 | 0.28984 | 61.7934 | -0.023943 | 0.048236 | 61.3922 | 0.007721 | 61.1933 | 59.3836 | 51.5515 | 53.1052 | 58.3393 | 67.4058 | 59.3428 | 55.5091 | 123.1659 | 61.5615 | 123.0651 | 61.2477 | 61.3199 | 122.6639 | 61.2794 | 122.4649 | 61.846 | 61.8865 | 61.7452 | 61.7857
5812.0938 | 123.3078 | -61.322 | 61.8576 | -1.8469 | -9.7247 | -8.1482 | -2.9553 | 6.1662 | -1.874 | -5.8037 | 61.8942 | 0.28984 | 61.8163 | -0.033101 | 0.052814 | 61.3968 | 0.007721 | 61.1887 | 59.4752 | 51.5973 | 53.1738 | 58.3668 | 67.4882 | 59.4481 | 55.5183 | 123.2162 | 61.6119 | 123.1383 | 61.2889 | 61.3748 | 122.7188 | 61.3297 | 122.5107 | 61.8414 | 61.8865 | 61.7635 | 61.8086
5813.0625 | 123.3032 | -61.2762 | 61.8668 | -1.8194 | -9.7842 | -8.1528 | -2.9781 | 6.1753 | -1.8511 | -5.8816 | 61.9034 | 0.28984 | 61.8346 | -0.028522 | 0.048236 | 61.3922 | 0.003143 | 61.1841 | 59.4569 | 51.492 | 53.1235 | 58.2981 | 67.4516 | 59.4252 | 55.3947 | 123.1796 | 61.5661 | 123.1109 | 61.2477 | 61.3245 | 122.6684 | 61.2794 | 122.4604 | 61.8551 | 61.9002 | 61.7864 | 61.8315
5814.0781 | 123.3856 | -61.2579 | 61.8668 | -1.7828 | -9.7934 | -8.1482 | -2.9919 | 6.0746 | -1.8099 | -5.8541 | 61.8896 | 0.29442 | 61.8026 | -0.023943 | 0.052814 | 61.3968 | 0.012299 | 61.1887 | 59.4752 | 51.4645 | 53.1098 | 58.2661 | 67.3325 | 59.4481 | 55.4038 | 123.1476 | 61.5524 | 123.0605 | 61.234 | 61.3107 | 122.6547 | 61.2702 | 122.4466 | 61.8368 | 61.8773 | 61.7498 | 61.7903
5815.0625 | 123.2986 | -61.29 | 61.8896 | -1.7873 | -9.7476 | -8.1344 | -3.0056 | 6.0929 | -1.8144 | -6.0098 | 61.8896 | 0.28984 | 61.798 | -0.023943 | 0.052814 | 61.3968 | 0.012299 | 61.1887 | 59.5026 | 51.5424 | 53.1555 | 58.2844 | 67.3829 | 59.4755 | 55.2802 | 123.1796 | 61.5798 | 123.088 | 61.266 | 61.3428 | 122.6867 | 61.3023 | 122.4787 | 61.8368 | 61.8773 | 61.7452 | 61.7857
5816.1094 | 123.3536 | -61.2717 | 61.8393 | -1.7507 | -9.4866 | -8.2718 | -2.9873 | 6.1387 | -1.7732 | -5.8862 | 61.8896 | 0.28984 | 61.798 | -0.033101 | 0.043657 | 61.3968 | 0.003143 | 61.1841 | 59.521 | 51.785 | 52.9999 | 58.2844 | 67.4104 | 59.4984 | 55.3855 | 123.1613 | 61.5615 | 123.0697 | 61.2386 | 61.3153 | 122.6684 | 61.2748 | 122.4558 | 61.846 | 61.8865 | 61.7543 | 61.7948
5817.0625 | 123.2895 | -61.2991 | 61.8805 | -1.7003 | -9.6011 | -8.194 | -2.9644 | 6.1662 | -1.7366 | -5.9411 | 61.8942 | 0.28984 | 61.8346 | -0.028522 | 0.048236 | 61.3922 | 0.003143 | 61.1841 | 59.5988 | 51.698 | 53.1052 | 58.3347 | 67.4653 | 59.5625 | 55.358 | 123.1934 | 61.589 | 123.1337 | 61.2706 | 61.3474 | 122.6913 | 61.3023 | 122.4832 | 61.846 | 61.8911 | 61.7864 | 61.8315
5818.0938 | 123.2803 | -61.2808 | 61.853 | -1.7599 | -9.6515 | -8.194 | -2.9369 | 6.2806 | -1.8007 | -6.0006 | 61.8896 | 0.28984 | 61.8163 | -0.033101 | 0.043657 | 61.4014 | 0.007721 | 61.1887 | 59.521 | 51.6294 | 53.0869 | 58.3439 | 67.5614 | 59.4801 | 55.2802 | 123.1705 | 61.5707 | 123.0971 | 61.2477 | 61.3245 | 122.6822 | 61.2885 | 122.4695 | 61.846 | 61.8819 | 61.7726 | 61.8086
5819.0625 | 123.2712 | -61.2854 | 61.8942 | -1.8743 | -9.8438 | -8.2855 | -2.8912 | 6.2577 | -1.9106 | -6.0876 | 61.8942 | 0.29442 | 61.8026 | -0.023943 | 0.048236 | 61.3968 | 0.016878 | 61.1887 | 59.4111 | 51.4416 | 52.9999 | 58.3942 | 67.5431 | 59.3748 | 55.1978 | 123.1796 | 61.5798 | 123.088 | 61.2615 | 61.3336 | 122.6822 | 61.3023 | 122.4741 | 61.846 | 61.8773 | 61.7543 | 61.7857
5820.0938 | 123.436 | -61.2625 | 61.8301 | -1.9155 | -9.885 | -8.2901 | -2.9278 | 6.1341 | -1.9518 | -6.0555 | 61.8988 | 0.28526 | 61.798 | -0.033101 | 0.052814 | 61.3968 | 0.012299 | 61.1841 | 59.347 | 51.3775 | 52.9724 | 58.3347 | 67.3966 | 59.3107 | 55.207 | 123.1613 | 61.5478 | 123.0605 | 61.2294 | 61.3153 | 122.6593 | 61.2748 | 122.4466 | 61.846 | 61.8865 | 61.7452 | 61.7857
5821.0625 | 123.3307 | -61.2625 | 61.8851 | -1.9567 | -9.9445 | -8.2581 | -2.8225 | 6.0975 | -1.9976 | -5.8129 | 61.8988 | 0.29442 | 61.83 | -0.023943 | 0.048236 | 61.3785 | 0.007721 | 61.1841 | 59.3058 | 51.318 | 53.0044 | 58.44 | 67.36 | 59.2649 | 55.4496 | 123.1613 | 61.5569 | 123.0926 | 61.2386 | 61.3107 | 122.641 | 61.2702 | 122.4466 | 61.8506 | 61.8911 | 61.7818 | 61.8223
5822.0781 | 123.3856 | -61.2488 | 61.8301 | -1.9613 | -9.8941 | -8.3038 | -2.882 | 5.9739 | -1.993 | -5.6847 | 61.8988 | 0.299 | 61.83 | -0.028522 | 0.043657 | 61.3968 | 0.007721 | 61.1795 | 59.2875 | 51.3546 | 52.9449 | 58.3668 | 67.2227 | 59.2558 | 55.5641 | 123.1476 | 61.5478 | 123.0788 | 61.2203 | 61.2924 | 122.6456 | 61.2565 | 122.4283 | 61.8551 | 61.8911 | 61.7864 | 61.8223
5823.0625 | 123.3261 | -61.2717 | 61.8713 | -1.9338 | -9.711 | -8.2031 | -2.9553 | 5.9281 | -1.9747 | -5.6206 | 61.8942 | 0.28526 | 61.798 | -0.03768 | 0.043657 | 61.3922 | 0.012299 | 61.1887 | 59.3378 | 51.5607 | 53.0685 | 58.3164 | 67.1998 | 59.297 | 55.651 | 123.1659 | 61.5569 | 123.0697 | 61.234 | 61.3153 | 122.6639 | 61.284 | 122.4604 | 61.8506 | 61.8819 | 61.7543 | 61.7857
5824.0938 | 123.3948 | -61.235 | 61.8576 | -1.8697 | -9.7797 | -8.1207 | -2.9919 | 5.9739 | -1.9106 | -5.7763 | 61.8896 | 0.299 | 61.8026 | -0.023943 | 0.057392 | 61.3876 | 0.012299 | 61.1841 | 59.3653 | 51.4554 | 53.1143 | 58.2432 | 67.2089 | 59.3245 | 55.4588 | 123.1247 | 61.534 | 123.0376 | 61.2111 | 61.2924 | 122.6227 | 61.2473 | 122.4192 | 61.8323 | 61.8773 | 61.7452 | 61.7903
5825.0625 | 123.317 | -61.2762 | 61.8896 | -1.8743 | -9.7293 | -8.1985 | -3.0194 | 6.0151 | -1.9106 | -5.9411 | 61.8988 | 0.28984 | 61.8255 | -0.033101 | 0.048236 | 61.3968 | 0.016878 | 61.175 | 59.4019 | 51.5469 | 53.0777 | 58.2569 | 67.2913 | 59.3657 | 55.3352 | 123.175 | 61.5661 | 123.1017 | 61.2431 | 61.3245 | 122.673 | 61.2931 | 122.4512 | 61.8506 | 61.8819 | 61.7772 | 61.8086
5826.1094 | 123.4085 | -61.2671 | 61.8347 | -1.8789 | -9.5919 | -8.2443 | -3.056 | 5.9876 | -1.9243 | -6.051 | 61.8942 | 0.29442 | 61.8392 | -0.033101 | 0.048236 | 61.3876 | 0.007721 | 61.1658 | 59.3882 | 51.6752 | 53.0228 | 58.2111 | 67.2547 | 59.3428 | 55.2161 | 123.1613 | 61.5615 | 123.1063 | 61.234 | 61.3153 | 122.6547 | 61.2748 | 122.4329 | 61.846 | 61.8865 | 61.791 | 61.8315
5827.0625 | 123.2986 | -61.29 | 61.9034 | -1.8423 | -9.6698 | -8.2031 | -3.0148 | 5.9556 | -1.8831 | -5.8816 | 61.8896 | 0.28526 | 61.8071 | -0.028522 | 0.057392 | 61.3876 | 0.012299 | 61.1795 | 59.4477 | 51.6202 | 53.0869 | 58.2752 | 67.2455 | 59.4069 | 55.4084 | 123.1796 | 61.5752 | 123.0971 | 61.2615 | 61.3474 | 122.6776 | 61.3023 | 122.4695 | 61.8323 | 61.8773 | 61.7498 | 61.7948
5828.0938 | 123.3902 | -61.2579 | 61.8484 | -1.8514 | -9.7705 | -8.1985 | -2.9873 | 6.0792 | -1.8877 | -5.7809 | 61.8851 | 0.299 | 61.8026 | -0.03768 | 0.052814 | 61.3922 | 0.007721 | 61.1795 | 59.4065 | 51.4874 | 53.0594 | 58.2706 | 67.3371 | 59.3702 | 55.4771 | 123.143 | 61.5569 | 123.0605 | 61.2203 | 61.3107 | 122.6501 | 61.2657 | 122.4375 | 61.8323 | 61.8773 | 61.7498 | 61.7948
5829.0625 | 123.2941 | -61.2854 | 61.8576 | -1.7965 | -9.7614 | -8.194 | -2.969 | 6.1158 | -1.8282 | -5.8862 | 61.8896 | 0.28984 | 61.83 | -0.023943 | 0.048236 | 61.3968 | 0.012299 | 61.1887 | 59.4889 | 51.5241 | 53.0914 | 58.3164 | 67.4012 | 59.4572 | 55.3992 | 123.175 | 61.5752 | 123.1154 | 61.2615 | 61.3336 | 122.6822 | 61.2977 | 122.4741 | 61.8414 | 61.8773 | 61.7818 | 61.8177
5830.0938 | 123.3582 | -61.2762 | 61.8484 | -1.7782 | -9.5736 | -8.226 | -2.9827 | 6.1066 | -1.819 | -5.8953 | 61.8942 | 0.299 | 61.8209 | -0.028522 | 0.043657 | 61.3968 | -0.001436 | 61.1933 | 59.4981 | 51.7026 | 53.0502 | 58.2935 | 67.3829 | 59.4572 | 55.3809 | 123.1705 | 61.5752 | 123.0971 | 61.2477 | 61.3199 | 122.673 | 61.2748 | 122.4695 | 61.8506 | 61.8957 | 61.7772 | 61.8223
5831.0625 | 123.2986 | -61.3129 | 61.8301 | -1.8789 | -9.6011 | -8.313 | -3.0285 | 5.9739 | -1.9014 | -6.0189 | 61.8942 | 0.29442 | 61.8163 | -0.028522 | 0.048236 | 61.3876 | 0.007721 | 61.1841 | 59.434 | 51.7118 | 52.9999 | 58.2844 | 67.2867 | 59.4114 | 55.2939 | 123.2071 | 61.6073 | 123.1292 | 61.2843 | 61.3611 | 122.7005 | 61.3206 | 122.497 | 61.846 | 61.8865 | 61.7681 | 61.8086
5832.0938 | 123.2803 | -61.2717 | 61.8713 | -1.8194 | -9.5004 | -8.2581 | -2.9598 | 6.0471 | -1.8465 | -6.1975 | 61.8896 | 0.29442 | 61.8117 | -0.023943 | 0.048236 | 61.3922 | 0.007721 | 61.1933 | 59.4523 | 51.7713 | 53.0136 | 58.3118 | 67.3188 | 59.4252 | 55.0742 | 123.1613 | 61.5661 | 123.0834 | 61.2477 | 61.3199 | 122.6639 | 61.2794 | 122.4649 | 61.8414 | 61.8819 | 61.7635 | 61.804
5833.0781 | 123.3627 | -61.2625 | 61.8484 | -1.8743 | -9.5049 | -8.2306 | -2.9507 | 6.0105 | -1.8923 | -6.2112 | 61.8942 | 0.29442 | 61.8117 | -0.033101 | 0.048236 | 61.3968 | 0.012299 | 61.1978 | 59.3882 | 51.7576 | 53.0319 | 58.3118 | 67.273 | 59.3702 | 55.0513 | 123.1567 | 61.5569 | 123.0742 | 61.2294 | 61.3107 | 122.6593 | 61.2748 | 122.4604 | 61.846 | 61.8819 | 61.7635 | 61.7994
5834.0938 | 123.3353 | -61.2762 | 61.821 | -1.9979 | -9.6102 | -8.3084 | -3.0972 | 6.1204 | -2.0296 | -6.2295 | 61.9034 | 0.28984 | 61.8255 | -0.033101 | 0.048236 | 61.3785 | 0.012299 | 61.1841 | 59.2783 | 51.666 | 52.9678 | 58.1791 | 67.3966 | 59.2466 | 55.0467 | 123.1796 | 61.5661 | 123.1017 | 61.2431 | 61.3245 | 122.6547 | 61.2885 | 122.4604 | 61.8551 | 61.8911 | 61.7772 | 61.8132
5835.0625 | 123.317 | -61.2671 | 61.8759 | -2.0163 | -9.8438 | -8.3817 | -3.0285 | 5.8823 | -2.0296 | -5.9411 | 61.9125 | 0.299 | 61.8438 | -0.028522 | 0.048236 | 61.383 | 0.012299 | 61.1887 | 59.2508 | 51.4233 | 52.8854 | 58.2386 | 67.1494 | 59.2375 | 55.326 | 123.1796 | 61.5661 | 123.1109 | 61.2386 | 61.3153 | 122.6501 | 61.2794 | 122.4558 | 61.8643 | 61.9002 | 61.7955 | 61.8315
5836.1094 | 123.3353 | -61.2717 | 61.8896 | -1.9384 | -10.004 | -8.3908 | -3.088 | 5.9922 | -1.9655 | -6.1837 | 61.908 | 0.28984 | 61.8438 | -0.028522 | 0.048236 | 61.3785 | 0.003143 | 61.1795 | 59.3332 | 51.2676 | 52.8808 | 58.1836 | 67.2639 | 59.3061 | 55.0879 | 123.1796 | 61.5615 | 123.1154 | 61.2431 | 61.3199 | 122.6501 | 61.2748 | 122.4512 | 61.8597 | 61.9048 | 61.7955 | 61.8406
5837.0625 | 123.2666 | -61.2762 | 61.8942 | -1.8285 | -9.9582 | -8.4458 | -3.0835 | 5.8274 | -1.8557 | -6.3348 | 61.8988 | 0.28984 | 61.8163 | -0.033101 | 0.052814 | 61.3785 | 0.003143 | 61.1704 | 59.4477 | 51.318 | 52.8305 | 58.1928 | 67.1036 | 59.4206 | 54.9414 | 123.175 | 61.5661 | 123.0925 | 61.2431 | 61.3291 | 122.6547 | 61.2794 | 122.4466 | 61.846 | 61.8957 | 61.7635 | 61.8132
5838.0938 | 123.3078 | -61.2305 | 61.8805 | -2.03 | -9.9033 | -8.5465 | -3.1018 | 5.8961 | -2.0479 | -6.4859 | 61.9125 | 0.29442 | 61.8163 | -0.028522 | 0.048236 | 61.3785 | 0.007721 | 61.1658 | 59.2005 | 51.3272 | 52.684 | 58.1287 | 67.1265 | 59.1825 | 54.7446 | 123.143 | 61.5249 | 123.0468 | 61.2019 | 61.2787 | 122.6089 | 61.2382 | 122.3963 | 61.8643 | 61.9048 | 61.7681 | 61.8086
5839.0625 | 123.3444 | -61.2167 | 61.8759 | -2.0437 | -9.5599 | -8.5099 | -3.0377 | 6.1204 | -2.0754 | -6.5729 | 61.9034 | 0.29442 | 61.8209 | -0.028522 | 0.048236 | 61.3785 | 0.012299 | 61.1795 | 59.173 | 51.6569 | 52.7068 | 58.1791 | 67.3371 | 59.1413 | 54.6439 | 123.1201 | 61.5112 | 123.0376 | 61.1882 | 61.265 | 122.5952 | 61.229 | 122.3963 | 61.8551 | 61.8911 | 61.7726 | 61.8086
5840.0625 | 123.2803 | -61.2625 | 61.8942 | -2.0895 | -9.711 | -8.4366 | -3.0422 | 6.189 | -2.1075 | -6.6965 | 61.9125 | 0.299 | 61.8484 | -0.028522 | 0.043657 | 61.383 | 0.016878 | 61.1704 | 59.173 | 51.5515 | 52.8259 | 58.2203 | 67.4516 | 59.155 | 54.566 | 123.175 | 61.5615 | 123.1109 | 61.234 | 61.3062 | 122.6455 | 61.2794 | 122.4329 | 61.8689 | 61.8957 | 61.8047 | 61.8315
5841.0938 | 123.3765 | -61.2579 | 61.8164 | -2.0987 | -9.6331 | -8.4046 | -3.088 | 6.1112 | -2.1258 | -6.4584 | 61.9034 | 0.299 | 61.8117 | -0.033101 | 0.052814 | 61.3785 | 0.007721 | 61.1658 | 59.1593 | 51.6248 | 52.8534 | 58.1699 | 67.3692 | 59.1322 | 54.7995 | 123.1613 | 61.5569 | 123.0697 | 61.2248 | 61.3107 | 122.6364 | 61.2657 | 122.4237 | 61.8506 | 61.8957 | 61.7589 | 61.804
5842.0625 | 123.436 | -61.2488 | 61.8484 | -2.1353 | -9.6423 | -8.4183 | -3.0743 | 6.1936 | -2.1716 | -6.3257 | 61.9034 | 0.29442 | 61.8026 | -0.028522 | 0.048236 | 61.383 | 0.012299 | 61.1658 | 59.1135 | 51.6065 | 52.8305 | 58.1745 | 67.4424 | 59.0772 | 54.9231 | 123.1522 | 61.5432 | 123.0513 | 61.2203 | 61.297 | 122.6318 | 61.2611 | 122.4146 | 61.8551 | 61.8911 | 61.7543 | 61.7903
5843.1094 | 123.2803 | -61.2625 | 61.9125 | -2.1902 | -9.7659 | -8.5007 | -3.1063 | 6.189 | -2.2219 | -6.1837 | 61.908 | 0.28526 | 61.83 | -0.028522 | 0.048236 | 61.383 | 0.012299 | 61.1704 | 59.0723 | 51.4966 | 52.7618 | 58.1562 | 67.4516 | 59.0406 | 55.0788 | 123.1705 | 61.5478 | 123.0926 | 61.234 | 61.3107 | 122.6455 | 61.2748 | 122.4329 | 61.8597 | 61.8957 | 61.7818 | 61.8177
5844.0625 | 123.3353 | -61.2534 | 61.8942 | -2.1216 | -9.7659 | -8.5099 | -3.0926 | 6.2119 | -2.1441 | -6.344 | 61.908 | 0.299 | 61.8438 | -0.028522 | 0.048236 | 61.383 | 0.012299 | 61.1704 | 59.1318 | 51.4874 | 52.7435 | 58.1607 | 67.4653 | 59.1093 | 54.9094 | 123.1613 | 61.5524 | 123.0971 | 61.2248 | 61.3016 | 122.6364 | 61.2657 | 122.4237 | 61.8597 | 61.8957 | 61.7955 | 61.8315
5845.0781 | 123.3673 | -61.2991 | 61.8301 | -2.1261 | -9.7201 | -8.4733 | -3.088 | 6.2257 | -2.1532 | -6.3989 | 61.9034 | 0.299 | 61.8209 | -0.023943 | 0.043657 | 61.383 | 0.012299 | 61.1704 | 59.173 | 51.579 | 52.8259 | 58.2111 | 67.5248 | 59.1459 | 54.9002 | 123.2025 | 61.5981 | 123.12 | 61.2752 | 61.3428 | 122.6822 | 61.3114 | 122.4695 | 61.8597 | 61.8911 | 61.7772 | 61.8086
5846.0625 | 123.3078 | -61.2213 | 61.908 | -2.117 | -9.7385 | -8.4549 | -3.1247 | 6.1982 | -2.1487 | -6.6782 | 61.908 | 0.29442 | 61.8117 | -0.028522 | 0.052814 | 61.3785 | 0.003143 | 61.1704 | 59.1043 | 51.4829 | 52.7664 | 58.0967 | 67.4195 | 59.0726 | 54.5431 | 123.1293 | 61.5157 | 123.033 | 61.1928 | 61.2741 | 122.5998 | 61.2245 | 122.3917 | 61.8551 | 61.9048 | 61.7589 | 61.8086
5847.0938 | 123.4177 | -61.2671 | 61.8393 | -2.0987 | -9.6698 | -8.5877 | -3.1888 | 6.0242 | -2.1304 | -6.8567 | 61.9125 | 0.29442 | 61.8346 | -0.03768 | 0.039079 | 61.3693 | 0.012299 | 61.1658 | 59.1684 | 51.5973 | 52.6794 | 58.0783 | 67.2913 | 59.1367 | 54.4104 | 123.1796 | 61.5615 | 123.1017 | 61.2294 | 61.3062 | 122.6364 | 61.2794 | 122.4329 | 61.8735 | 61.9002 | 61.7955 | 61.8223
5848.0625 | 123.2758 | -61.2762 | 61.8988 | -2.149 | -9.6377 | -8.6015 | -3.2391 | 5.9601 | -2.167 | -6.257 | 61.9125 | 0.28069 | 61.8484 | -0.023943 | 0.043657 | 61.3785 | 0.012299 | 61.175 | 59.1272 | 51.6385 | 52.6748 | 58.0371 | 67.2364 | 59.1093 | 55.0193 | 123.1888 | 61.5569 | 123.1246 | 61.2523 | 61.3199 | 122.6547 | 61.2885 | 122.4512 | 61.8689 | 61.9002 | 61.8047 | 61.8361
5849.0781 | 123.3719 | -61.2946 | 61.8393 | -2.149 | -9.7842 | -8.5877 | -3.2391 | 6.1066 | -2.1716 | -6.3211 | 61.9034 | 0.28984 | 61.8255 | -0.033101 | 0.039079 | 61.383 | 0.007721 | 61.1795 | 59.1455 | 51.5103 | 52.7068 | 58.0554 | 67.4012 | 59.123 | 54.9735 | 123.1979 | 61.5844 | 123.12 | 61.2615 | 61.3336 | 122.6776 | 61.3023 | 122.4741 | 61.8643 | 61.8957 | 61.7864 | 61.8177
5850.0625 | 123.4268 | -61.235 | 61.8576 | -2.2818 | -9.9811 | -8.7251 | -3.3261 | 6.1112 | -2.3135 | -6.4813 | 61.908 | 0.28984 | 61.83 | -0.033101 | 0.043657 | 61.3785 | 0.012299 | 61.1795 | 58.9532 | 51.2539 | 52.51 | 57.9089 | 67.3463 | 58.9216 | 54.7537 | 123.143 | 61.5249 | 123.0651 | 61.2019 | 61.2787 | 122.6135 | 61.2473 | 122.4146 | 61.8643 | 61.8957 | 61.7864 | 61.8177
5851.0938 | 123.3856 | -61.2396 | 61.8256 | -2.1307 | -10.0223 | -8.7251 | -3.4223 | 5.9601 | -2.1578 | -6.344 | 61.9171 | 0.28984 | 61.83 | -0.023943 | 0.048236 | 61.3739 | 0.012299 | 61.1612 | 59.1089 | 51.2173 | 52.5145 | 57.8174 | 67.1998 | 59.0818 | 54.8957 | 123.1567 | 61.5295 | 123.0697 | 61.2157 | 61.2879 | 122.6135 | 61.2519 | 122.4008 | 61.8689 | 61.9048 | 61.7818 | 61.8177
5852.0625 | 123.4222 | -61.2396 | 61.8576 | -2.1765 | -10.0498 | -8.693 | -3.4543 | 5.8045 | -2.2036 | -6.2707 | 61.9171 | 0.29442 | 61.8484 | -0.028522 | 0.043657 | 61.3647 | 0.012299 | 61.1704 | 59.0631 | 51.1898 | 52.5466 | 57.7853 | 67.0441 | 59.036 | 54.9689 | 123.1567 | 61.534 | 123.088 | 61.2111 | 61.2833 | 122.6043 | 61.2519 | 122.41 | 61.8735 | 61.9048 | 61.8047 | 61.8361
5853.0938 | 123.3719 | -61.2579 | 61.8805 | -2.1078 | -10.0269 | -8.6976 | -3.3398 | 5.9373 | -2.1395 | -6.5683 | 61.908 | 0.28984 | 61.83 | -0.028522 | 0.048236 | 61.3693 | 0.012299 | 61.1612 | 59.1501 | 51.231 | 52.5603 | 57.9181 | 67.1952 | 59.1184 | 54.6896 | 123.1659 | 61.5478 | 123.088 | 61.2294 | 61.3062 | 122.6272 | 61.2702 | 122.4192 | 61.8597 | 61.8957 | 61.7818 | 61.8177
5854.0625 | 123.3765 | -61.2534 | 61.8759 | -2.1261 | -10.004 | -8.748 | -3.2666 | 5.9327 | -2.1487 | -6.8247 | 61.9125 | 0.299 | 61.8117 | -0.023943 | 0.048236 | 61.3647 | 0.012299 | 61.1658 | 59.1272 | 51.2493 | 52.5054 | 57.9868 | 67.186 | 59.1047 | 54.4287 | 123.1659 | 61.5524 | 123.0651 | 61.2294 | 61.3016 | 122.6181 | 61.2657 | 122.4192 | 61.8643 | 61.9002 | 61.7635 | 61.7994
5855.0938 | 123.3536 | -61.2625 | 61.8759 | -2.0437 | -9.8804 | -8.7526 | -3.3582 | 6.0105 | -2.0754 | -6.9162 | 61.908 | 0.28526 | 61.8209 | -0.023943 | 0.052814 | 61.3693 | 0.007721 | 61.1612 | 59.2188 | 51.3821 | 52.51 | 57.9044 | 67.273 | 59.1871 | 54.3463 | 123.1705 | 61.5478 | 123.0834 | 61.2386 | 61.3153 | 122.6318 | 61.2702 | 122.4237 | 61.8551 | 61.9002 | 61.7681 | 61.8132
5856.0625 | 123.2803 | -61.2534 | 61.8942 | -2.0117 | -9.8758 | -8.7388 | -3.3444 | 6.0609 | -2.0434 | -6.9529 | 61.9217 | 0.28069 | 61.8529 | -0.028522 | 0.048236 | 61.3693 | 0.012299 | 61.1612 | 59.2417 | 51.3775 | 52.5145 | 57.9089 | 67.3142 | 59.21 | 54.3005 | 123.175 | 61.534 | 123.1063 | 61.2248 | 61.3016 | 122.6227 | 61.2657 | 122.4146 | 61.8735 | 61.9094 | 61.8047 | 61.8406
5857.0781 | 123.3902 | -61.2534 | 61.8301 | -1.9613 | -9.7568 | -8.7068 | -3.349 | 6.0105 | -1.9838 | -6.7743 | 61.9125 | 0.29442 | 61.83 | -0.033101 | 0.048236 | 61.3739 | 0.016878 | 61.1612 | 59.292 | 51.4966 | 52.5466 | 57.9044 | 67.2639 | 59.2695 | 54.479 | 123.1659 | 61.5478 | 123.0834 | 61.2203 | 61.3016 | 122.6272 | 61.2702 | 122.4146 | 61.8643 | 61.8957 | 61.7818 | 61.8132
5858.0625 | 123.3444 | -61.2442 | 61.8713 | -1.8652 | -9.6286 | -8.7388 | -3.4085 | 5.9601 | -1.8877 | -6.55 | 61.908 | 0.28984 | 61.8026 | -0.023943 | 0.048236 | 61.3739 | 0.012299 | 61.175 | 59.379 | 51.6156 | 52.5054 | 57.8357 | 67.2043 | 59.3565 | 54.6942 | 123.1522 | 61.534 | 123.0468 | 61.2203 | 61.2924 | 122.6181 | 61.2565 | 122.4192 | 61.8597 | 61.8957 | 61.7543 | 61.7903
5859.0625 | 123.3948 | -61.2762 | 61.8713 | -2.0254 | -9.6011 | -8.7617 | -3.3948 | 5.9052 | -2.0525 | -6.6187 | 61.9034 | 0.28984 | 61.8209 | -0.023943 | 0.043657 | 61.3693 | 0.012299 | 61.1658 | 59.2508 | 51.6752 | 52.5145 | 57.8815 | 67.1815 | 59.2237 | 54.6576 | 123.1796 | 61.5661 | 123.0971 | 61.2523 | 61.3199 | 122.6455 | 61.2885 | 122.442 | 61.8597 | 61.8911 | 61.7772 | 61.8086
5860.0938 | 123.2941 | -61.2991 | 61.8393 | -2.03 | -9.482 | -8.7251 | -3.3215 | 5.9601 | -2.0571 | -6.5225 | 61.908 | 0.28984 | 61.8529 | -0.028522 | 0.039079 | 61.383 | 0.007721 | 61.1704 | 59.2691 | 51.8171 | 52.5741 | 57.9776 | 67.2593 | 59.242 | 54.7766 | 123.2071 | 61.589 | 123.1521 | 61.2706 | 61.3382 | 122.6822 | 61.3069 | 122.4695 | 61.8689 | 61.9002 | 61.8139 | 61.8452
5861.0625 | 123.3902 | -61.2442 | 61.8576 | -1.9613 | -9.4775 | -8.7434 | -3.3078 | 5.9418 | -1.9976 | -6.5454 | 61.9125 | 0.29442 | 61.8438 | -0.023943 | 0.048236 | 61.383 | 0.007721 | 61.1658 | 59.2829 | 51.7667 | 52.5008 | 57.9364 | 67.186 | 59.2466 | 54.6988 | 123.1567 | 61.5386 | 123.088 | 61.2203 | 61.2924 | 122.6272 | 61.2519 | 122.41 | 61.8643 | 61.9048 | 61.7955 | 61.8361
5862.0781 | 123.3948 | -61.2396 | 61.8301 | -1.9842 | -9.5004 | -8.7113 | -3.3444 | 5.8594 | -2.0113 | -6.5775 | 61.9125 | 0.299 | 61.8484 | -0.033101 | 0.052814 | 61.3739 | 0.012299 | 61.1612 | 59.2554 | 51.7393 | 52.5283 | 57.8952 | 67.0991 | 59.2283 | 54.6622 | 123.1522 | 61.5386 | 123.088 | 61.2065 | 61.2924 | 122.6135 | 61.2519 | 122.4008 | 61.8597 | 61.9002 | 61.7955 | 61.8361
5863.0625 | 123.381 | -61.2534 | 61.8576 | -2.0849 | -9.5645 | -8.78 | -3.3994 | 5.9235 | -2.1212 | -6.6416 | 61.9125 | 0.28984 | 61.8255 | -0.033101 | 0.057392 | 61.3739 | 0.012299 | 61.1704 | 59.1684 | 51.6889 | 52.4733 | 57.854 | 67.1769 | 59.1322 | 54.6118 | 123.1659 | 61.5432 | 123.0788 | 61.2203 | 61.3107 | 122.6272 | 61.2657 | 122.4237 | 61.8551 | 61.9002 | 61.7681 | 61.8132
5864.0625 | 123.4268 | -61.2122 | 61.8576 | -2.1353 | -9.6194 | -8.835 | -3.4726 | 5.7908 | -2.1532 | -6.5225 | 61.9125 | 0.299 | 61.8163 | -0.028522 | 0.048236 | 61.3647 | 0.007721 | 61.1658 | 59.0769 | 51.5928 | 52.3772 | 57.7395 | 67.0029 | 59.0589 | 54.6896 | 123.1247 | 61.5112 | 123.0285 | 61.1836 | 61.2604 | 122.5769 | 61.2199 | 122.378 | 61.8643 | 61.9048 | 61.7681 | 61.8086
5865.0938 | 123.3856 | -61.2442 | 61.8164 | -2.117 | -9.6011 | -8.7938 | -3.468 | 5.6534 | -2.1487 | -6.2341 | 61.9034 | 0.29442 | 61.8117 | -0.028522 | 0.043657 | 61.3785 | 0.007721 | 61.1566 | 59.1272 | 51.6431 | 52.4504 | 57.7762 | 66.8976 | 59.0955 | 55.0101 | 123.1476 | 61.5386 | 123.0559 | 61.2157 | 61.2879 | 122.6227 | 61.2519 | 122.4008 | 61.8597 | 61.8957 | 61.7681 | 61.804
5866.0625 | 123.381 | -61.2213 | 61.8713 | -2.1857 | -9.6423 | -8.8121 | -3.4909 | 5.8228 | -2.2219 | -6.3989 | 61.9125 | 0.28984 | 61.8209 | -0.019364 | 0.048236 | 61.3693 | -0.001436 | 61.1566 | 59.0357 | 51.579 | 52.4092 | 57.7304 | 67.0441 | 58.9994 | 54.8224 | 123.1338 | 61.5112 | 123.0422 | 61.2019 | 61.2695 | 122.5906 | 61.2199 | 122.378 | 61.8643 | 61.914 | 61.7726 | 61.8223
5867.0938 | 123.349 | -61.2625 | 61.8301 | -2.149 | -9.6469 | -8.7617 | -3.4726 | 5.8915 | -2.1807 | -6.6416 | 61.9125 | 0.29442 | 61.8163 | -0.033101 | 0.048236 | 61.3693 | 0.007721 | 61.1566 | 59.1135 | 51.6156 | 52.5008 | 57.7899 | 67.154 | 59.0818 | 54.621 | 123.175 | 61.5569 | 123.0788 | 61.2294 | 61.3107 | 122.6318 | 61.2702 | 122.4192 | 61.8643 | 61.9048 | 61.7681 | 61.8086
5868.0625 | 123.3627 | -61.2122 | 61.853 | -2.1261 | -9.798 | -8.7846 | -3.4726 | 5.9144 | -2.1487 | -6.8979 | 61.9171 | 0.28984 | 61.8529 | -0.028522 | 0.043657 | 61.3693 | 0.012299 | 61.1612 | 59.086 | 51.4142 | 52.4276 | 57.7395 | 67.1265 | 59.0635 | 54.3142 | 123.1293 | 61.502 | 123.0651 | 61.1836 | 61.2558 | 122.5815 | 61.2245 | 122.3734 | 61.8735 | 61.9048 | 61.8093 | 61.8406
5869.0938 | 123.4085 | -61.2625 | 61.8118 | -2.149 | -9.6881 | -8.7938 | -3.4543 | 5.9556 | -2.1807 | -6.9254 | 61.9171 | 0.299 | 61.8575 | -0.033101 | 0.048236 | 61.3739 | 0.003143 | 61.1566 | 59.1135 | 51.5744 | 52.4688 | 57.8082 | 67.2181 | 59.0818 | 54.3371 | 123.1796 | 61.5615 | 123.12 | 61.2294 | 61.3107 | 122.6364 | 61.2657 | 122.4192 | 61.8689 | 61.914 | 61.8093 | 61.8544
5870.0625 | 123.3673 | -61.2442 | 61.853 | -2.1445 | -9.6927 | -8.8121 | -3.4589 | 5.9052 | -2.167 | -6.6736 | 61.9217 | 0.29442 | 61.8575 | -0.023943 | 0.048236 | 61.3739 | 0.007721 | 61.1521 | 59.0998 | 51.5515 | 52.4321 | 57.7853 | 67.1494 | 59.0772 | 54.5706 | 123.1659 | 61.5386 | 123.1017 | 61.2203 | 61.2924 | 122.6181 | 61.2519 | 122.3963 | 61.8735 | 61.914 | 61.8093 | 61.8498
5871.1094 | 123.3673 | -61.2488 | 61.8484 | -2.117 | -9.8071 | -8.9174 | -3.4772 | 5.7175 | -2.1441 | -6.637 | 61.9171 | 0.29442 | 61.8346 | -0.028522 | 0.048236 | 61.3693 | 0.012299 | 61.1612 | 59.1318 | 51.4416 | 52.3314 | 57.7716 | 66.9663 | 59.1047 | 54.6118 | 123.1659 | 61.5432 | 123.0834 | 61.2203 | 61.297 | 122.6181 | 61.2611 | 122.41 | 61.8689 | 61.9048 | 61.7864 | 61.8223
5872.0625 | 123.2803 | -61.2625 | 61.8896 | -2.0941 | -9.7842 | -8.9815 | -3.5413 | 5.4657 | -2.1212 | -6.431 | 61.9125 | 0.29442 | 61.8255 | -0.028522 | 0.048236 | 61.3693 | 0.003143 | 61.1612 | 59.1684 | 51.4783 | 52.281 | 57.7212 | 66.7282 | 59.1413 | 54.8316 | 123.175 | 61.5569 | 123.088 | 61.234 | 61.3107 | 122.6318 | 61.2657 | 122.4237 | 61.8643 | 61.9094 | 61.7772 | 61.8223
5873.0938 | 123.3627 | -61.2396 | 61.8439 | -2.1857 | -9.8026 | -8.9632 | -3.5962 | 5.2689 | -2.2128 | -6.3806 | 61.9217 | 0.29442 | 61.8255 | -0.028522 | 0.043657 | 61.3693 | 0.007721 | 61.1521 | 59.054 | 51.4371 | 52.2765 | 57.6434 | 66.5085 | 59.0269 | 54.859 | 123.1613 | 61.534 | 123.0651 | 61.2111 | 61.2833 | 122.6089 | 61.2473 | 122.3917 | 61.878 | 61.914 | 61.7818 | 61.8177
5874.0625 | 123.4268 | -61.2305 | 61.853 | -2.1582 | -9.6881 | -8.9082 | -3.5734 | 5.0812 | -2.1945 | -6.3485 | 61.9171 | 0.29442 | 61.8209 | -0.023943 | 0.043657 | 61.3693 | 0.007721 | 61.1612 | 59.0723 | 51.5424 | 52.3222 | 57.6571 | 66.3116 | 59.036 | 54.8819 | 123.1476 | 61.5249 | 123.0513 | 61.2065 | 61.2741 | 122.5998 | 61.2382 | 122.3917 | 61.8735 | 61.9094 | 61.7772 | 61.8132
5875.0781 | 123.3948 | -61.2488 | 61.8301 | -2.117 | -9.7568 | -8.9494 | -3.523 | 5.3559 | -2.1487 | -6.4905 | 61.9171 | 0.29442 | 61.8209 | -0.028522 | 0.048236 | 61.3647 | -0.001436 | 61.1612 | 59.1318 | 51.492 | 52.2993 | 57.7258 | 66.6046 | 59.1001 | 54.7583 | 123.1659 | 61.5432 | 123.0697 | 61.2203 | 61.297 | 122.6135 | 61.2473 | 122.41 | 61.8689 | 61.9186 | 61.7726 | 61.8223
5876.0625 | 123.3124 | -61.235 | 61.8942 | -2.0941 | -9.7476 | -8.9906 | -3.5321 | 5.2872 | -2.1349 | -6.8521 | 61.9217 | 0.28526 | 61.8438 | -0.033101 | 0.052814 | 61.3647 | 0.012299 | 61.1612 | 59.141 | 51.4874 | 52.2444 | 57.7029 | 66.5222 | 59.1001 | 54.3829 | 123.1567 | 61.5203 | 123.0788 | 61.2019 | 61.2879 | 122.5998 | 61.2473 | 122.3963 | 61.8689 | 61.9094 | 61.791 | 61.8315
5877.0781 | 123.4177 | -61.2305 | 61.8393 | -2.1261 | -9.7934 | -9.0502 | -3.4497 | 5.3375 | -2.1578 | -7.017 | 61.9263 | 0.29442 | 61.8575 | -0.019364 | 0.043657 | 61.3647 | 0.003143 | 61.1566 | 59.1043 | 51.4371 | 52.1803 | 57.7807 | 66.568 | 59.0726 | 54.2135 | 123.1567 | 61.5249 | 123.088 | 61.2111 | 61.2741 | 122.5952 | 61.2336 | 122.3871 | 61.8826 | 61.9231 | 61.8138 | 61.8544
5878.0625 | 123.3215 | -61.1984 | 61.9171 | -2.1445 | -9.7064 | -9.0364 | -3.4909 | 5.1865 | -2.1716 | -6.6599 | 61.9308 | 0.299 | 61.8621 | -0.028522 | 0.043657 | 61.3601 | 0.003143 | 61.1612 | 59.054 | 51.492 | 52.162 | 57.7075 | 66.3849 | 59.0269 | 54.5386 | 123.1293 | 61.4974 | 123.0605 | 61.1699 | 61.2421 | 122.5586 | 61.2016 | 122.3596 | 61.8872 | 61.9277 | 61.8184 | 61.8589
5879.0781 | 123.4268 | -61.2259 | 61.8576 | -2.1673 | -9.7201 | -9.0914 | -3.5779 | 5.0674 | -2.1899 | -6.4355 | 61.9308 | 0.28984 | 61.8667 | -0.033101 | 0.039079 | 61.3647 | 0.012299 | 61.1566 | 59.0585 | 51.5058 | 52.1345 | 57.648 | 66.2933 | 59.036 | 54.7904 | 123.1567 | 61.5157 | 123.0926 | 61.1928 | 61.265 | 122.5906 | 61.2382 | 122.3825 | 61.8918 | 61.9186 | 61.8276 | 61.8544
5880.0625 | 123.4543 | -61.2076 | 61.8713 | -2.1902 | -9.711 | -9.1005 | -3.61 | 4.9118 | -2.2128 | -6.5637 | 61.9217 | 0.29442 | 61.8484 | -0.028522 | 0.048236 | 61.3556 | -0.001436 | 61.1521 | 59.0173 | 51.4966 | 52.1071 | 57.5976 | 66.1194 | 58.9948 | 54.6439 | 123.1293 | 61.502 | 123.0559 | 61.1791 | 61.2558 | 122.5632 | 61.2061 | 122.3596 | 61.8735 | 61.9231 | 61.8001 | 61.8498
5881.0938 | 123.2895 | -61.2717 | 61.853 | -2.1902 | -9.8529 | -9.0868 | -3.6054 | 5.278 | -2.2173 | -6.5866 | 61.9217 | 0.29442 | 61.8255 | -0.028522 | 0.057392 | 61.3647 | -0.001436 | 61.1566 | 59.0814 | 51.4187 | 52.1849 | 57.6663 | 66.5497 | 59.0543 | 54.6851 | 123.1934 | 61.5661 | 123.0971 | 61.2431 | 61.3291 | 122.6364 | 61.2702 | 122.4283 | 61.8643 | 61.9231 | 61.7681 | 61.8269
5882.0625 | 123.3353 | -61.2305 | 61.9034 | -2.1948 | -9.8987 | -9.0593 | -3.5505 | 5.3879 | -2.2173 | -6.6644 | 61.9217 | 0.29442 | 61.83 | -0.023943 | 0.052814 | 61.3556 | 0.012299 | 61.1566 | 59.0357 | 51.3318 | 52.1712 | 57.68 | 66.6184 | 59.0131 | 54.566 | 123.1522 | 61.5249 | 123.0605 | 61.2065 | 61.2833 | 122.586 | 61.2428 | 122.3871 | 61.8689 | 61.9094 | 61.7772 | 61.8177
5883.0938 | 123.3994 | -61.2671 | 61.821 | -2.2085 | -9.8621 | -8.9906 | -3.5276 | 5.5115 | -2.2357 | -6.5042 | 61.9125 | 0.29442 | 61.8117 | -0.033101 | 0.039079 | 61.3647 | 0.007721 | 61.1521 | 59.0585 | 51.405 | 52.2765 | 57.7395 | 66.7786 | 59.0314 | 54.7629 | 123.1796 | 61.5615 | 123.0788 | 61.234 | 61.3062 | 122.6318 | 61.2748 | 122.4192 | 61.8735 | 61.9048 | 61.7726 | 61.804
5884.0625 | 123.3948 | -61.2259 | 61.8668 | -2.236 | -9.9903 | -9.0044 | -3.5962 | 5.4611 | -2.2723 | -6.431 | 61.9217 | 0.28984 | 61.83 | -0.023943 | 0.052814 | 61.3601 | 0.016878 | 61.1612 | 58.9899 | 51.2356 | 52.2215 | 57.6296 | 66.687 | 58.9536 | 54.7949 | 123.1476 | 61.5157 | 123.0559 | 61.2019 | 61.2787 | 122.586 | 61.2428 | 122.3871 | 61.8689 | 61.9048 | 61.7772 | 61.8132
5885.0938 | 123.3994 | -61.235 | 61.8576 | -2.204 | -9.972 | -8.9815 | -3.5962 | 5.539 | -2.2357 | -6.4218 | 61.9217 | 0.28984 | 61.8438 | -0.023943 | 0.048236 | 61.3647 | 0.007721 | 61.1475 | 59.0311 | 51.2631 | 52.2536 | 57.6388 | 66.774 | 58.9994 | 54.8132 | 123.1567 | 61.5249 | 123.0788 | 61.2111 | 61.2833 | 122.5998 | 61.2428 | 122.3825 | 61.8735 | 61.914 | 61.7955 | 61.8361
5886.0625 | 123.2666 | -61.2488 | 61.9034 | -2.2223 | -10.0681 | -9.041 | -3.6512 | 5.4932 | -2.2494 | -6.4493 | 61.9308 | 0.29442 | 61.8621 | -0.023943 | 0.052814 | 61.3647 | 0.012299 | 61.1566 | 59.0265 | 51.1806 | 52.2078 | 57.5976 | 66.742 | 58.9994 | 54.7995 | 123.1796 | 61.5432 | 123.1109 | 61.2248 | 61.3016 | 122.6135 | 61.2611 | 122.4054 | 61.878 | 61.9186 | 61.8093 | 61.8498
5887.0625 | 123.4177 | -61.1984 | 61.8622 | -2.1719 | -10.1368 | -9.0593 | -3.6466 | 5.5664 | -2.1945 | -6.4951 | 61.9308 | 0.28984 | 61.8667 | -0.019364 | 0.043657 | 61.3556 | 0.007721 | 61.1566 | 59.0265 | 51.0616 | 52.1391 | 57.5518 | 66.7649 | 59.004 | 54.7034 | 123.1293 | 61.4883 | 123.0651 | 61.1791 | 61.2421 | 122.554 | 61.2061 | 122.3551 | 61.8872 | 61.9231 | 61.823 | 61.8589
5888.0938 | 123.317 | -61.2396 | 61.9217 | -2.2085 | -10.0956 | -8.9403 | -3.523 | 5.626 | -2.2448 | -6.6141 | 61.9217 | 0.299 | 61.8621 | -0.023943 | 0.052814 | 61.3647 | 0.003143 | 61.1658 | 59.0311 | 51.144 | 52.2993 | 57.7166 | 66.8656 | 58.9948 | 54.6255 | 123.1613 | 61.5386 | 123.1017 | 61.2157 | 61.2924 | 122.6043 | 61.2428 | 122.4054 | 61.8689 | 61.9185 | 61.8093 | 61.8589
5889.0625 | 123.3719 | -61.2167 | 61.8942 | -2.1765 | -10.059 | -8.8808 | -3.468 | 5.7129 | -2.2128 | -6.8659 | 61.9217 | 0.28526 | 61.8484 | -0.023943 | 0.048236 | 61.3647 | 0.016878 | 61.1521 | 59.0402 | 51.1578 | 52.336 | 57.7487 | 66.9297 | 59.004 | 54.3509 | 123.1384 | 61.502 | 123.0651 | 61.1928 | 61.265 | 122.5815 | 61.2336 | 122.3688 | 61.8735 | 61.9048 | 61.8001 | 61.8315
5890.0781 | 123.4451 | -61.2534 | 61.8484 | -2.03 | -9.9491 | -8.8029 | -3.5093 | 5.4932 | -2.0617 | -6.8705 | 61.9171 | 0.29442 | 61.8255 | -0.028522 | 0.052814 | 61.3693 | 0.007721 | 61.1475 | 59.2234 | 51.3043 | 52.4504 | 57.7441 | 66.7465 | 59.1917 | 54.3829 | 123.1705 | 61.5478 | 123.0788 | 61.2248 | 61.3062 | 122.6227 | 61.2611 | 122.4008 | 61.8643 | 61.9094 | 61.7726 | 61.8177
5891.0625 | 123.2803 | -61.2717 | 61.8668 | -2.0575 | -9.9811 | -8.7938 | -3.468 | 5.6992 | -2.0983 | -6.8109 | 61.9171 | 0.29442 | 61.8209 | -0.019364 | 0.048236 | 61.3647 | 0.007721 | 61.1658 | 59.2142 | 51.2905 | 52.4779 | 57.8036 | 66.9709 | 59.1734 | 54.4607 | 123.1888 | 61.5661 | 123.0925 | 61.2523 | 61.3199 | 122.6364 | 61.2794 | 122.4375 | 61.8689 | 61.9094 | 61.7726 | 61.8132
5892.0938 | 123.3627 | -61.2579 | 61.8347 | -2.0575 | -9.8941 | -8.7159 | -3.4177 | 5.658 | -2.0983 | -6.4401 | 61.9171 | 0.29442 | 61.8255 | -0.028522 | 0.048236 | 61.3693 | 0.003143 | 61.1521 | 59.2005 | 51.3638 | 52.542 | 57.8403 | 66.9159 | 59.1596 | 54.8178 | 123.175 | 61.5524 | 123.0834 | 61.2294 | 61.3062 | 122.6272 | 61.2611 | 122.41 | 61.8689 | 61.914 | 61.7772 | 61.8223
5893.0625 | 123.2895 | -61.3083 | 61.8942 | -2.1124 | -9.7476 | -8.8716 | -3.4955 | 5.5893 | -2.1441 | -6.3806 | 61.9125 | 0.28984 | 61.8255 | -0.023943 | 0.043657 | 61.3647 | -0.001436 | 61.1475 | 59.1959 | 51.5607 | 52.4367 | 57.8128 | 66.8976 | 59.1642 | 54.9277 | 123.2208 | 61.5981 | 123.1337 | 61.2843 | 61.3519 | 122.673 | 61.3069 | 122.4558 | 61.8689 | 61.914 | 61.7818 | 61.8269
5894.0938 | 123.3856 | -61.2213 | 61.8713 | -2.1307 | -9.711 | -8.9357 | -3.5413 | 5.452 | -2.1624 | -6.4218 | 61.9171 | 0.299 | 61.8484 | -0.03768 | 0.052814 | 61.3739 | 0.012299 | 61.1521 | 59.0906 | 51.5103 | 52.2856 | 57.68 | 66.6733 | 59.0589 | 54.7995 | 123.1384 | 61.5203 | 123.0697 | 61.1836 | 61.2741 | 122.5952 | 61.2336 | 122.3734 | 61.8643 | 61.9048 | 61.7955 | 61.8361
5895.0625 | 123.5138 | -61.1938 | 61.8988 | -2.1765 | -9.8071 | -8.9632 | -3.5688 | 5.5344 | -2.2128 | -6.3577 | 61.9217 | 0.28526 | 61.8575 | -0.023943 | 0.043657 | 61.3693 | 0.012299 | 61.1612 | 59.0173 | 51.3867 | 52.2307 | 57.6251 | 66.7282 | 58.9811 | 54.8361 | 123.1155 | 61.4791 | 123.0514 | 61.1699 | 61.2375 | 122.5632 | 61.2061 | 122.3551 | 61.878 | 61.9094 | 61.8138 | 61.8452
5896.1094 | 123.349 | -61.2488 | 61.8439 | -2.291 | -9.8483 | -8.922 | -3.5413 | 5.5069 | -2.3181 | -6.3531 | 61.9308 | 0.28984 | 61.8529 | -0.023943 | 0.043657 | 61.3601 | 0.007721 | 61.1475 | 58.9578 | 51.4004 | 52.3268 | 57.7075 | 66.7557 | 58.9307 | 54.8957 | 123.1796 | 61.5386 | 123.1017 | 61.2248 | 61.2924 | 122.6089 | 61.2565 | 122.3963 | 61.8872 | 61.9231 | 61.8093 | 61.8452
5897.0625 | 123.3765 | -61.2076 | 61.8668 | -2.2681 | -10.0636 | -8.9677 | -3.5367 | 5.3971 | -2.3135 | -6.4859 | 61.9217 | 0.29442 | 61.8667 | -0.023943 | 0.048236 | 61.3601 | 0.007721 | 61.1429 | 58.9395 | 51.144 | 52.2398 | 57.6709 | 66.6046 | 58.8941 | 54.7217 | 123.1293 | 61.502 | 123.0742 | 61.1836 | 61.2558 | 122.5677 | 61.2153 | 122.3505 | 61.8735 | 61.914 | 61.8184 | 61.8589
5898.0938 | 123.3765 | -61.2259 | 61.8759 | -2.2955 | -10.1689 | -8.9906 | -3.523 | 4.9484 | -2.3364 | -6.5225 | 61.9308 | 0.299 | 61.8484 | -0.033101 | 0.048236 | 61.3556 | 0.007721 | 61.1429 | 58.9304 | 51.057 | 52.2353 | 57.7029 | 66.1743 | 58.8895 | 54.7034 | 123.1567 | 61.5249 | 123.0742 | 61.1928 | 61.2741 | 122.5815 | 61.2336 | 122.3688 | 61.8826 | 61.9231 | 61.8001 | 61.8406
5899.0625 | 123.3215 | -61.2396 | 61.9034 | -2.2955 | -10.091 | -8.9586 | -3.5596 | 5.1682 | -2.3272 | -6.6141 | 61.9217 | 0.28984 | 61.8392 | -0.028522 | 0.039079 | 61.351 | 0.007721 | 61.1475 | 58.9441 | 51.1486 | 52.281 | 57.68 | 66.4078 | 58.9124 | 54.6255 | 123.1613 | 61.5295 | 123.0788 | 61.2111 | 61.2787 | 122.5906 | 61.2473 | 122.3871 | 61.8826 | 61.914 | 61.8001 | 61.8315
5900.0781 | 123.4085 | -61.2442 | 61.8484 | -2.3139 | -10.0498 | -9.1143 | -3.61 | 5.6992 | -2.3455 | -6.6553 | 61.9217 | 0.299 | 61.8255 | -0.033101 | 0.048236 | 61.3693 | 0.007721 | 61.1475 | 58.9304 | 51.1944 | 52.1299 | 57.6342 | 66.9434 | 58.8987 | 54.5889 | 123.1659 | 61.5432 | 123.0697 | 61.2111 | 61.2924 | 122.6135 | 61.2519 | 122.3917 | 61.8735 | 61.914 | 61.7772 | 61.8177
5901.0625 | 123.2666 | -61.2442 | 61.8988 | -2.4192 | -9.9628 | -9.2379 | -3.6741 | 5.5893 | -2.4554 | -6.669 | 61.9263 | 0.29442 | 61.8346 | -0.028522 | 0.048236 | 61.3556 | 0.007721 | 61.1383 | 58.825 | 51.2814 | 52.0063 | 57.5701 | 66.8335 | 58.7888 | 54.5752 | 123.1705 | 61.5386 | 123.0788 | 61.2157 | 61.2924 | 122.5998 | 61.2519 | 122.3825 | 61.878 | 61.9186 | 61.7864 | 61.8269
5902.0938 | 123.3719 | -61.2442 | 61.8668 | -2.442 | -9.9766 | -9.1463 | -3.6283 | 5.4749 | -2.4783 | -6.6049 | 61.9308 | 0.29442 | 61.8438 | -0.03768 | 0.043657 | 61.3556 | 0.016878 | 61.1338 | 58.8022 | 51.2676 | 52.0979 | 57.6159 | 66.7191 | 58.7659 | 54.6393 | 123.1751 | 61.5386 | 123.088 | 61.2065 | 61.2879 | 122.5998 | 61.2611 | 122.378 | 61.8872 | 61.914 | 61.8001 | 61.8269
5903.0625 | 123.2758 | -61.2717 | 61.8713 | -2.5199 | -9.9491 | -9.1143 | -3.7107 | 5.2414 | -2.547 | -6.5958 | 61.94 | 0.29442 | 61.8621 | -0.028522 | 0.048236 | 61.351 | 0.007721 | 61.1383 | 58.7518 | 51.3226 | 52.1574 | 57.561 | 66.5131 | 58.7247 | 54.6759 | 123.2117 | 61.5661 | 123.1338 | 61.2431 | 61.3199 | 122.6227 | 61.2794 | 122.41 | 61.8918 | 61.9323 | 61.8138 | 61.8544
5904.0938 | 123.4222 | -61.203 | 61.8805 | -2.5153 | -9.9857 | -9.1005 | -3.7199 | 5.2506 | -2.5516 | -6.6828 | 61.9354 | 0.28984 | 61.8758 | -0.033101 | 0.052814 | 61.351 | 0.007721 | 61.1383 | 58.6877 | 51.2173 | 52.1025 | 57.4831 | 66.4536 | 58.6514 | 54.5202 | 123.1384 | 61.4928 | 123.0788 | 61.1699 | 61.2558 | 122.554 | 61.2107 | 122.3413 | 61.8826 | 61.9277 | 61.823 | 61.8681
5905.0625 | 123.3032 | -61.2671 | 61.9263 | -2.3139 | -9.8667 | -9.0181 | -3.7107 | 5.571 | -2.3455 | -6.6416 | 61.9263 | 0.29442 | 61.8712 | -0.028522 | 0.048236 | 61.3647 | 0.007721 | 61.1521 | 58.9532 | 51.4004 | 52.249 | 57.5564 | 66.8381 | 58.9215 | 54.6255 | 123.1934 | 61.5615 | 123.1383 | 61.2386 | 61.3153 | 122.6318 | 61.2748 | 122.4192 | 61.878 | 61.9186 | 61.823 | 61.8635
5906.1094 | 123.4177 | -61.2167 | 61.8805 | -2.236 | -9.8758 | -9.0456 | -3.7199 | 5.6946 | -2.2677 | -6.6919 | 61.9308 | 0.28984 | 61.8438 | -0.033101 | 0.052814 | 61.3601 | 0.012299 | 61.1521 | 58.9807 | 51.3409 | 52.1712 | 57.4969 | 66.9114 | 58.949 | 54.5248 | 123.1476 | 61.5066 | 123.0605 | 61.1836 | 61.2695 | 122.5769 | 61.229 | 122.3688 | 61.878 | 61.9186 | 61.791 | 61.8315
5907.0625 | 123.4406 | -61.2167 | 61.8851 | -2.1399 | -9.9811 | -9.1188 | -3.7336 | 5.7953 | -2.1761 | -7.2688 | 61.9263 | 0.28984 | 61.83 | -0.028522 | 0.052814 | 61.3601 | 0.007721 | 61.1521 | 59.0769 | 51.2356 | 52.0979 | 57.4831 | 67.0121 | 59.0406 | 53.948 | 123.143 | 61.5066 | 123.0468 | 61.1882 | 61.2695 | 122.5769 | 61.2245 | 122.3688 | 61.8735 | 61.9186 | 61.7772 | 61.8223
5908.0938 | 123.3215 | -61.235 | 61.8301 | -2.0712 | -10.0681 | -9.215 | -3.8755 | 5.246 | -2.1029 | -7.0811 | 61.9354 | 0.29442 | 61.8346 | -0.028522 | 0.043657 | 61.3601 | 0.003143 | 61.1475 | 59.1638 | 51.1669 | 52.0201 | 57.3595 | 66.481 | 59.1322 | 54.154 | 123.1705 | 61.5295 | 123.0697 | 61.2065 | 61.2787 | 122.5952 | 61.2382 | 122.3825 | 61.8918 | 61.9323 | 61.791 | 61.8315
5909.0625 | 123.381 | -61.2213 | 61.8988 | -2.0712 | -9.9857 | -9.2196 | -3.8847 | 5.4245 | -2.1029 | -6.9437 | 61.9217 | 0.29442 | 61.83 | -0.023943 | 0.048236 | 61.3556 | 0.012299 | 61.1429 | 59.1501 | 51.2356 | 52.0017 | 57.3366 | 66.6458 | 59.1184 | 54.2776 | 123.143 | 61.5157 | 123.0514 | 61.1974 | 61.2695 | 122.5769 | 61.2336 | 122.3642 | 61.8735 | 61.9094 | 61.7818 | 61.8177
5910.0781 | 123.4039 | -61.2076 | 61.8668 | -2.1078 | -9.9857 | -9.3066 | -3.9351 | 5.0812 | -2.1349 | -6.9162 | 61.9217 | 0.29442 | 61.8529 | -0.033101 | 0.048236 | 61.351 | 0.003143 | 61.1383 | 59.0998 | 51.2219 | 51.901 | 57.2725 | 66.2888 | 59.0726 | 54.2913 | 123.1293 | 61.502 | 123.0605 | 61.1745 | 61.2558 | 122.5586 | 61.2107 | 122.3459 | 61.8735 | 61.9185 | 61.8047 | 61.8498
5911.0625 | 123.3902 | -61.2213 | 61.8851 | -2.1307 | -9.8621 | -9.2837 | -3.8664 | 4.8889 | -2.1578 | -6.8384 | 61.9263 | 0.28984 | 61.8758 | -0.023943 | 0.043657 | 61.3556 | 0.003143 | 61.1429 | 59.0906 | 51.3592 | 51.9376 | 57.3549 | 66.1102 | 59.0635 | 54.3829 | 123.1476 | 61.5112 | 123.0971 | 61.1974 | 61.265 | 122.5769 | 61.2245 | 122.3642 | 61.8826 | 61.9231 | 61.8322 | 61.8727
5912.0781 | 123.262 | -61.2579 | 61.8622 | -2.2223 | -9.9582 | -9.2928 | -3.8801 | 5.2139 | -2.2494 | -6.8521 | 61.9354 | 0.29442 | 61.8712 | -0.028522 | 0.039079 | 61.3556 | 0.003143 | 61.1429 | 59.0357 | 51.2997 | 51.9651 | 57.3778 | 66.4719 | 59.0085 | 54.4058 | 123.1934 | 61.5524 | 123.1292 | 61.2294 | 61.297 | 122.6135 | 61.2611 | 122.4008 | 61.8963 | 61.9323 | 61.8322 | 61.8681
5913.0625 | 123.262 | -61.2122 | 61.9308 | -2.3688 | -10.0269 | -9.2745 | -3.7565 | 5.2048 | -2.3867 | -6.93 | 61.9354 | 0.28984 | 61.8712 | -0.023943 | 0.048236 | 61.3464 | 0.007721 | 61.1338 | 58.8434 | 51.1852 | 51.9376 | 57.4557 | 66.4169 | 58.8254 | 54.2822 | 123.1476 | 61.502 | 123.0834 | 61.1882 | 61.2604 | 122.5586 | 61.2199 | 122.3459 | 61.8872 | 61.9277 | 61.823 | 61.8635
5914.0781 | 123.3765 | -61.2396 | 61.8668 | -2.4054 | -10.1048 | -9.2104 | -3.8252 | 4.8706 | -2.428 | -6.9666 | 61.9354 | 0.29442 | 61.8529 | -0.03768 | 0.048236 | 61.351 | 0.007721 | 61.1292 | 58.8342 | 51.1349 | 52.0292 | 57.4145 | 66.1102 | 58.8117 | 54.273 | 123.1751 | 61.534 | 123.0926 | 61.2019 | 61.2879 | 122.5906 | 61.2473 | 122.3688 | 61.8872 | 61.9277 | 61.8047 | 61.8452
5915.0625 | 123.3902 | -61.2213 | 61.8668 | -2.3413 | -10.2055 | -9.0731 | -3.8343 | 4.747 | -2.3776 | -6.8659 | 61.94 | 0.29442 | 61.8392 | -0.028522 | 0.043657 | 61.3464 | 0.007721 | 61.1383 | 58.88 | 51.0158 | 52.1483 | 57.387 | 65.9683 | 58.8437 | 54.3554 | 123.1613 | 61.5157 | 123.0605 | 61.1928 | 61.265 | 122.5677 | 61.229 | 122.3596 | 61.8963 | 61.9323 | 61.7955 | 61.8315
5916.0938 | 123.3307 | -61.203 | 61.9629 | -2.442 | -10.3429 | -9.1555 | -3.8847 | 4.7561 | -2.4692 | -6.9483 | 61.9446 | 0.28526 | 61.8484 | -0.033101 | 0.048236 | 61.3373 | 0.012299 | 61.1475 | 58.761 | 50.8601 | 52.0475 | 57.3183 | 65.9591 | 58.7338 | 54.2547 | 123.1476 | 61.4883 | 123.0514 | 61.1699 | 61.2512 | 122.5403 | 61.2153 | 122.3505 | 61.8963 | 61.9323 | 61.8001 | 61.8361
5917.0625 | 123.3948 | -61.2259 | 61.8942 | -2.5336 | -10.439 | -9.2516 | -3.8618 | 4.6325 | -2.579 | -7.0765 | 61.9446 | 0.29442 | 61.8484 | -0.023943 | 0.048236 | 61.3373 | 0.007721 | 61.1246 | 58.6923 | 50.7869 | 51.9743 | 57.3641 | 65.8584 | 58.6469 | 54.1494 | 123.1705 | 61.5203 | 123.0742 | 61.2019 | 61.2741 | 122.5631 | 61.2336 | 122.3505 | 61.8963 | 61.9369 | 61.8001 | 61.8406
5918.0781 | 123.3582 | -61.235 | 61.8576 | -2.5565 | -10.3062 | -9.2379 | -3.7977 | 4.7607 | -2.5974 | -7.1909 | 61.9446 | 0.29442 | 61.8758 | -0.03768 | 0.043657 | 61.3373 | 0.007721 | 61.1292 | 58.6785 | 50.9288 | 51.9972 | 57.4373 | 65.9958 | 58.6377 | 54.0441 | 123.1796 | 61.5295 | 123.1109 | 61.1974 | 61.2787 | 122.5723 | 61.2428 | 122.3642 | 61.9009 | 61.9369 | 61.8322 | 61.8681
5919.0625 | 123.3444 | -61.235 | 61.8759 | -2.5565 | -10.1918 | -9.1875 | -3.8297 | 4.8935 | -2.5928 | -7.0215 | 61.9583 | 0.29442 | 61.8804 | -0.033101 | 0.048236 | 61.3418 | 0.007721 | 61.1429 | 58.6785 | 51.0433 | 52.0475 | 57.4053 | 66.1285 | 58.6423 | 54.2135 | 123.1934 | 61.5295 | 123.1154 | 61.2019 | 61.2833 | 122.5769 | 61.2428 | 122.378 | 61.9101 | 61.9506 | 61.8322 | 61.8727
5920.0781 | 123.3948 | -61.2076 | 61.8484 | -2.584 | -10.0544 | -9.1188 | -3.8801 | 4.9805 | -2.6111 | -6.9025 | 61.9492 | 0.299 | 61.8758 | -0.023943 | 0.043657 | 61.3418 | 0.003143 | 61.1429 | 58.6236 | 51.1532 | 52.0887 | 57.3275 | 66.188 | 58.5965 | 54.3051 | 123.1567 | 61.5066 | 123.0834 | 61.1836 | 61.2512 | 122.5494 | 61.2107 | 122.3505 | 61.9055 | 61.946 | 61.8322 | 61.8727
5921.0625 | 123.2895 | -61.2122 | 61.9308 | -2.5702 | -10.0315 | -9.1829 | -3.8801 | 4.9209 | -2.6157 | -6.8842 | 61.9446 | 0.28984 | 61.8758 | -0.023943 | 0.052814 | 61.3464 | 0.007721 | 61.1429 | 58.6419 | 51.1807 | 52.0292 | 57.332 | 66.1331 | 58.5965 | 54.328 | 123.1567 | 61.502 | 123.088 | 61.1882 | 61.265 | 122.5586 | 61.2199 | 122.3551 | 61.8918 | 61.9369 | 61.823 | 61.8681
5922.0938 | 123.3124 | -61.2259 | 61.9263 | -2.6114 | -9.9262 | -9.1829 | -3.8481 | 4.8981 | -2.6523 | -6.8979 | 61.9446 | 0.28984 | 61.8621 | -0.028522 | 0.057392 | 61.3418 | 0.007721 | 61.1475 | 58.6144 | 51.2997 | 52.043 | 57.3778 | 66.1239 | 58.5736 | 54.328 | 123.1705 | 61.5157 | 123.088 | 61.1974 | 61.2833 | 122.5677 | 61.2336 | 122.3734 | 61.8872 | 61.9369 | 61.8047 | 61.8544
5923.0625 | 123.3856 | -61.235 | 61.8942 | -2.6481 | -9.8667 | -9.2013 | -3.8297 | 4.6417 | -2.6706 | -6.9208 | 61.94 | 0.28984 | 61.8575 | -0.019364 | 0.048236 | 61.3373 | 0.003143 | 61.1475 | 58.587 | 51.3684 | 52.0338 | 57.4053 | 65.8767 | 58.5644 | 54.3142 | 123.1751 | 61.5249 | 123.0926 | 61.2157 | 61.2833 | 122.5723 | 61.2382 | 122.3825 | 61.8918 | 61.9369 | 61.8093 | 61.8544
5924.0781 | 123.4131 | -61.2122 | 61.853 | -2.616 | -9.7568 | -9.2333 | -3.8114 | 4.4632 | -2.6431 | -7.0307 | 61.9492 | 0.29442 | 61.8484 | -0.033101 | 0.043657 | 61.3418 | 0.003143 | 61.1475 | 58.5961 | 51.4554 | 51.9789 | 57.4007 | 65.6753 | 58.569 | 54.1815 | 123.1613 | 61.5066 | 123.0605 | 61.1791 | 61.2558 | 122.554 | 61.2153 | 122.3596 | 61.9055 | 61.946 | 61.8047 | 61.8452
5925.0625 | 123.3353 | -61.2396 | 61.8988 | -2.6206 | -9.9674 | -9.302 | -3.8343 | 4.8294 | -2.6614 | -7.0673 | 61.94 | 0.299 | 61.8484 | -0.028522 | 0.048236 | 61.3464 | 0.007721 | 61.1383 | 58.619 | 51.2722 | 51.9376 | 57.4053 | 66.069 | 58.5782 | 54.1723 | 123.1796 | 61.5386 | 123.088 | 61.2111 | 61.2879 | 122.586 | 61.2473 | 122.378 | 61.8918 | 61.9323 | 61.8001 | 61.8406
5926.1094 | 123.317 | -61.2488 | 61.8759 | -2.5794 | -10.1002 | -9.2654 | -3.7611 | 4.985 | -2.6065 | -7.1543 | 61.9354 | 0.299 | 61.8621 | -0.033101 | 0.048236 | 61.3327 | 0.012299 | 61.1338 | 58.6694 | 51.1486 | 51.9834 | 57.4877 | 66.2338 | 58.6423 | 54.0945 | 123.1842 | 61.5478 | 123.1109 | 61.2157 | 61.297 | 122.5815 | 61.2611 | 122.3825 | 61.8872 | 61.9231 | 61.8138 | 61.8498
5927.0625 | 123.3902 | -61.2167 | 61.8851 | -2.5199 | -9.6972 | -9.1738 | -3.7473 | 5.0079 | -2.5516 | -7.1543 | 61.94 | 0.28984 | 61.8667 | -0.033101 | 0.048236 | 61.351 | 0.007721 | 61.1338 | 58.6969 | 51.5195 | 52.043 | 57.4694 | 66.2247 | 58.6652 | 54.0624 | 123.1567 | 61.5066 | 123.0834 | 61.1836 | 61.265 | 122.5677 | 61.2245 | 122.3505 | 61.8918 | 61.9323 | 61.8184 | 61.8589
5928.0781 | 123.3719 | -61.2167 | 61.8759 | -2.5931 | -9.4408 | -9.2882 | -3.8435 | 5.127 | -2.634 | -7.3191 | 61.94 | 0.299 | 61.8758 | -0.028522 | 0.048236 | 61.3418 | -0.001436 | 61.1338 | 58.6236 | 51.7759 | 51.9285 | 57.3733 | 66.3437 | 58.5828 | 53.8976 | 123.1567 | 61.5157 | 123.0926 | 61.1882 | 61.265 | 122.5586 | 61.2153 | 122.3505 | 61.8918 | 61.9414 | 61.8276 | 61.8773
5929.0625 | 123.3673 | -61.2396 | 61.8576 | -2.6481 | -9.6744 | -9.2837 | -3.8435 | 5.2506 | -2.6752 | -7.3512 | 61.9446 | 0.28984 | 61.8712 | -0.028522 | 0.057392 | 61.351 | 0.007721 | 61.1338 | 58.5915 | 51.5653 | 51.956 | 57.3961 | 66.4902 | 58.5644 | 53.8885 | 123.1842 | 61.5295 | 123.1109 | 61.2111 | 61.297 | 122.5906 | 61.2473 | 122.3734 | 61.8872 | 61.9369 | 61.8139 | 61.8635
5930.0938 | 123.349 | -61.2213 | 61.8759 | -2.6939 | -10.0956 | -9.3111 | -3.8618 | 5.333 | -2.721 | -7.0582 | 61.9446 | 0.29442 | 61.8712 | -0.028522 | 0.039079 | 61.3464 | 0.003143 | 61.1383 | 58.5275 | 51.1257 | 51.9102 | 57.3595 | 66.5543 | 58.5003 | 54.1631 | 123.1659 | 61.5157 | 123.0926 | 61.1928 | 61.2604 | 122.5677 | 61.2245 | 122.3596 | 61.9055 | 61.9414 | 61.8322 | 61.8681
5931.0625 | 123.2986 | -61.2305 | 61.9217 | -2.6664 | -10.0544 | -9.2379 | -3.7931 | 5.4474 | -2.6889 | -6.9849 | 61.9354 | 0.28984 | 61.8575 | -0.019364 | 0.048236 | 61.3556 | 0.007721 | 61.1521 | 58.5641 | 51.1761 | 51.9926 | 57.4374 | 66.6779 | 58.5415 | 54.2456 | 123.1659 | 61.5203 | 123.088 | 61.2111 | 61.2787 | 122.586 | 61.2382 | 122.3825 | 61.8872 | 61.9277 | 61.8093 | 61.8498
5932.0938 | 123.3215 | -61.2671 | 61.8942 | -2.6893 | -9.8575 | -9.3478 | -3.8801 | 5.159 | -2.721 | -7.1314 | 61.9354 | 0.29442 | 61.8529 | -0.019364 | 0.043657 | 61.3373 | 0.016878 | 61.1383 | 58.5778 | 51.4096 | 51.9193 | 57.387 | 66.4261 | 58.5461 | 54.1357 | 123.2025 | 61.5615 | 123.12 | 61.2477 | 61.3107 | 122.6043 | 61.284 | 122.4054 | 61.8918 | 61.9186 | 61.8093 | 61.8361
5933.0625 | 123.3765 | -61.2076 | 61.9171 | -2.6618 | -9.8026 | -9.2974 | -3.8618 | 5.0766 | -2.6935 | -6.8979 | 61.9354 | 0.29442 | 61.8529 | -0.019364 | 0.048236 | 61.351 | 0.003143 | 61.1383 | 58.5458 | 51.405 | 51.9102 | 57.3458 | 66.2842 | 58.5141 | 54.3097 | 123.143 | 61.502 | 123.0605 | 61.1882 | 61.2558 | 122.5586 | 61.2107 | 122.3459 | 61.8872 | 61.9323 | 61.8047 | 61.8498
5934.0781 | 123.3536 | -61.2167 | 61.8576 | -2.6755 | -9.8255 | -9.3066 | -3.8206 | 5.0308 | -2.7027 | -6.9391 | 61.9308 | 0.29442 | 61.8438 | -0.033101 | 0.052814 | 61.3418 | 0.007721 | 61.1338 | 58.5412 | 51.3913 | 51.9102 | 57.3961 | 66.2476 | 58.5141 | 54.2776 | 123.1476 | 61.5112 | 123.0605 | 61.1836 | 61.2695 | 122.5586 | 61.2245 | 122.3505 | 61.878 | 61.9231 | 61.791 | 61.8361
5935.0625 | 123.381 | -61.2167 | 61.8942 | -2.6527 | -9.8255 | -9.3523 | -3.7977 | 5.0491 | -2.6752 | -7.0811 | 61.9308 | 0.29442 | 61.8484 | -0.028522 | 0.048236 | 61.3418 | 0.012299 | 61.1338 | 58.5641 | 51.3913 | 51.8644 | 57.419 | 66.2659 | 58.5416 | 54.1357 | 123.1476 | 61.5112 | 123.0651 | 61.1882 | 61.265 | 122.5586 | 61.229 | 122.3505 | 61.8826 | 61.9186 | 61.8001 | 61.8361
5936.0938 | 123.1979 | -61.2991 | 61.8622 | -2.6801 | -10.0315 | -9.3661 | -3.816 | 5.1224 | -2.7072 | -7.2047 | 61.9446 | 0.299 | 61.8758 | -0.028522 | 0.048236 | 61.3418 | 0.012299 | 61.1292 | 58.619 | 51.2676 | 51.933 | 57.4831 | 66.4215 | 58.5919 | 54.0945 | 123.2437 | 61.5981 | 123.175 | 61.2706 | 61.3474 | 122.641 | 61.3114 | 122.4283 | 61.8963 | 61.9323 | 61.8276 | 61.8635
5937.0625 | 123.4222 | -61.1755 | 61.8805 | -2.6618 | -10.1185 | -9.3707 | -3.8572 | 5.0079 | -2.6935 | -7.223 | 61.9537 | 0.299 | 61.8804 | -0.028522 | 0.043657 | 61.3418 | 0.007721 | 61.1292 | 58.5137 | 51.057 | 51.8049 | 57.3183 | 66.1835 | 58.482 | 53.9526 | 123.1293 | 61.4745 | 123.0559 | 61.147 | 61.2192 | 122.5174 | 61.1833 | 122.3047 | 61.9101 | 61.946 | 61.8367 | 61.8727
5938.0938 | 123.4039 | -61.2259 | 61.8988 | -2.6572 | -10.0819 | -9.4348 | -3.8664 | 5.0217 | -2.6798 | -7.0765 | 61.9446 | 0.28526 | 61.8758 | -0.033101 | 0.048236 | 61.3327 | 0.012299 | 61.1246 | 58.5687 | 51.144 | 51.7911 | 57.3595 | 66.2476 | 58.5461 | 54.1494 | 123.1705 | 61.5112 | 123.1017 | 61.1928 | 61.2741 | 122.5586 | 61.2382 | 122.3505 | 61.8963 | 61.9323 | 61.8276 | 61.8635
5939.0625 | 123.3902 | -61.2259 | 61.8484 | -2.6298 | -9.8392 | -9.4805 | -3.8847 | 5.1407 | -2.6614 | -7.0811 | 61.94 | 0.28984 | 61.8804 | -0.028522 | 0.048236 | 61.3464 | 0.007721 | 61.1338 | 58.5961 | 51.3867 | 51.7453 | 57.3412 | 66.3666 | 58.5644 | 54.1448 | 123.1659 | 61.5157 | 123.1063 | 61.1974 | 61.2741 | 122.5723 | 61.2336 | 122.3596 | 61.8918 | 61.9323 | 61.8322 | 61.8727
5940.0781 | 123.3719 | -61.2076 | 61.8759 | -2.6984 | -9.917 | -9.5263 | -3.9579 | 5.0903 | -2.7347 | -7.2688 | 61.9446 | 0.29442 | 61.8621 | -0.023943 | 0.039079 | 61.3373 | 0.012299 | 61.1338 | 58.5091 | 51.2906 | 51.6812 | 57.2496 | 66.2979 | 58.4729 | 53.9388 | 123.1522 | 61.502 | 123.0697 | 61.1836 | 61.2467 | 122.5448 | 61.2199 | 122.3413 | 61.9055 | 61.9323 | 61.823 | 61.8498
5941.0625 | 123.3353 | -61.2076 | 61.9492 | -2.7488 | -9.9811 | -9.5721 | -3.9396 | 5.0079 | -2.7805 | -7.4519 | 61.9492 | 0.299 | 61.8529 | -0.033101 | 0.048236 | 61.3281 | 0.007721 | 61.12 | 58.4588 | 51.2264 | 51.6355 | 57.268 | 66.2155 | 58.4271 | 53.7557 | 123.1567 | 61.5066 | 123.0605 | 61.1745 | 61.2558 | 122.5357 | 61.2153 | 122.3276 | 61.9009 | 61.9414 | 61.8047 | 61.8452
5942.0781 | 123.3719 | -61.203 | 61.8713 | -2.6939 | -9.9857 | -9.5355 | -3.8435 | 5.0537 | -2.7301 | -7.3603 | 61.9446 | 0.28526 | 61.8575 | -0.019364 | 0.048236 | 61.3327 | 0.012299 | 61.12 | 58.5091 | 51.2173 | 51.6675 | 57.3595 | 66.2567 | 58.4729 | 53.8427 | 123.1476 | 61.4883 | 123.0605 | 61.1836 | 61.2512 | 122.5357 | 61.2153 | 122.323 | 61.8963 | 61.9323 | 61.8093 | 61.8452
5943.0625 | 123.3902 | -61.2213 | 61.8851 | -2.6298 | -9.9628 | -9.4439 | -3.7336 | 5.1315 | -2.6614 | -7.2596 | 61.9446 | 0.28984 | 61.8484 | -0.028522 | 0.039079 | 61.3373 | 0.012299 | 61.1246 | 58.5916 | 51.2585 | 51.7774 | 57.4877 | 66.3528 | 58.5599 | 53.9617 | 123.1659 | 61.5112 | 123.0697 | 61.1928 | 61.2604 | 122.5586 | 61.2336 | 122.3459 | 61.9055 | 61.9323 | 61.8093 | 61.8361
5944.0938 | 123.3765 | -61.2305 | 61.8896 | -2.6527 | -10.0086 | -9.4668 | -3.8297 | 5.2368 | -2.6889 | -7.3741 | 61.9446 | 0.29442 | 61.8529 | -0.028522 | 0.052814 | 61.3464 | 0.007721 | 61.1292 | 58.5778 | 51.2219 | 51.7637 | 57.4007 | 66.4673 | 58.5415 | 53.8564 | 123.1751 | 61.5249 | 123.0834 | 61.2019 | 61.2833 | 122.5769 | 61.2382 | 122.3596 | 61.8918 | 61.9369 | 61.8001 | 61.8452
5945.0625 | 123.4131 | -61.2122 | 61.908 | -2.7259 | -10.0223 | -9.5447 | -3.9167 | 5.2002 | -2.7622 | -7.5892 | 61.94 | 0.299 | 61.8712 | -0.019364 | 0.043657 | 61.3327 | 0.007721 | 61.12 | 58.4863 | 51.1898 | 51.6675 | 57.2954 | 66.4124 | 58.45 | 53.6229 | 123.1522 | 61.5112 | 123.0834 | 61.1928 | 61.2558 | 122.5448 | 61.2199 | 122.3322 | 61.8963 | 61.9323 | 61.8276 | 61.8635
5946.1094 | 123.3856 | -61.2259 | 61.8759 | -2.6984 | -10.059 | -9.4943 | -3.9305 | 4.985 | -2.721 | -7.3649 | 61.9492 | 0.28984 | 61.885 | -0.023943 | 0.048236 | 61.3327 | 0.003143 | 61.1154 | 58.5275 | 51.1669 | 51.7316 | 57.2954 | 66.2109 | 58.5049 | 53.861 | 123.1751 | 61.5157 | 123.1109 | 61.2019 | 61.2741 | 122.5586 | 61.229 | 122.3413 | 61.9009 | 61.946 | 61.8367 | 61.8818
5947.0625 | 123.3444 | -61.2122 | 61.9125 | -2.7167 | -10.0315 | -9.4714 | -3.9259 | 5.0354 | -2.7439 | -7.3191 | 61.9537 | 0.29442 | 61.885 | -0.028522 | 0.048236 | 61.3373 | 0.003143 | 61.1154 | 58.4954 | 51.1807 | 51.7408 | 57.2863 | 66.2476 | 58.4683 | 53.893 | 123.1659 | 61.5066 | 123.0971 | 61.1836 | 61.2604 | 122.5494 | 61.2153 | 122.3276 | 61.9055 | 61.9506 | 61.8367 | 61.8818
5948.0781 | 123.3536 | -61.2305 | 61.8668 | -2.6252 | -9.8758 | -9.3798 | -3.8893 | 5.3421 | -2.6569 | -7.2321 | 61.9446 | 0.299 | 61.8758 | -0.028522 | 0.043657 | 61.3418 | 0.012299 | 61.12 | 58.6053 | 51.3546 | 51.8506 | 57.3412 | 66.5726 | 58.5736 | 53.9983 | 123.1751 | 61.5295 | 123.1063 | 61.2019 | 61.2741 | 122.5723 | 61.2428 | 122.3505 | 61.9009 | 61.9323 | 61.8322 | 61.8635
5949.0625 | 123.381 | -61.2076 | 61.8805 | -2.6618 | -9.917 | -9.4393 | -3.9259 | 5.0903 | -2.6889 | -7.255 | 61.94 | 0.28526 | 61.8712 | -0.028522 | 0.048236 | 61.3373 | 0.012299 | 61.1246 | 58.5458 | 51.2906 | 51.7682 | 57.2817 | 66.2979 | 58.5187 | 53.9526 | 123.1476 | 61.4928 | 123.0788 | 61.1791 | 61.2558 | 122.5448 | 61.2199 | 122.3322 | 61.8918 | 61.9277 | 61.823 | 61.8589
5950.0625 | 123.3078 | -61.203 | 61.9308 | -2.6984 | -10.0178 | -9.5355 | -3.9488 | 5.246 | -2.7301 | -7.3557 | 61.9446 | 0.299 | 61.8575 | -0.028522 | 0.052814 | 61.3464 | 0.016878 | 61.1246 | 58.5046 | 51.1852 | 51.6675 | 57.2542 | 66.449 | 58.4729 | 53.8473 | 123.1476 | 61.502 | 123.0605 | 61.1745 | 61.2558 | 122.5494 | 61.2199 | 122.3276 | 61.8918 | 61.9277 | 61.8047 | 61.8406
5951.1094 | 123.4177 | -61.203 | 61.8896 | -2.6847 | -9.8896 | -9.508 | -3.9442 | 4.9347 | -2.7072 | -7.2917 | 61.94 | 0.28984 | 61.8484 | -0.033101 | 0.052814 | 61.3373 | 0.007721 | 61.1246 | 58.5183 | 51.3134 | 51.695 | 57.2588 | 66.1377 | 58.4958 | 53.9113 | 123.143 | 61.4928 | 123.0514 | 61.1699 | 61.2558 | 122.5403 | 61.2107 | 122.3276 | 61.8872 | 61.9323 | 61.7955 | 61.8406
5952.0625 | 123.2712 | -61.2076 | 61.94 | -2.6893 | -9.9079 | -9.4805 | -3.9534 | 4.9164 | -2.7255 | -7.3374 | 61.9446 | 0.28526 | 61.8484 | -0.028522 | 0.043657 | 61.3373 | 0.007721 | 61.1246 | 58.5183 | 51.2997 | 51.727 | 57.2542 | 66.1239 | 58.482 | 53.8701 | 123.1522 | 61.4928 | 123.0559 | 61.1791 | 61.2512 | 122.5448 | 61.2153 | 122.3322 | 61.9009 | 61.9369 | 61.8047 | 61.8406
5953.0781 | 123.4406 | -61.1893 | 61.9263 | -2.6939 | -10.0956 | -9.508 | -3.9625 | 5.0308 | -2.7164 | -7.5389 | 61.9492 | 0.29442 | 61.8667 | -0.033101 | 0.043657 | 61.3373 | 0.012299 | 61.1246 | 58.4954 | 51.0937 | 51.6812 | 57.2267 | 66.2201 | 58.4729 | 53.6504 | 123.1384 | 61.4837 | 123.0559 | 61.1562 | 61.2329 | 122.5265 | 61.2016 | 122.3139 | 61.9055 | 61.9369 | 61.823 | 61.8544
5954.0625 | 123.2666 | -61.2305 | 61.9446 | -2.7122 | -10.1368 | -9.4164 | -3.8984 | 4.9209 | -2.7347 | -7.3283 | 61.9583 | 0.299 | 61.8941 | -0.033101 | 0.052814 | 61.3235 | 0.003143 | 61.1246 | 58.5183 | 51.0937 | 51.814 | 57.332 | 66.1514 | 58.4958 | 53.9022 | 123.1888 | 61.5295 | 123.1246 | 61.1974 | 61.2833 | 122.554 | 61.2336 | 122.3551 | 61.9055 | 61.9552 | 61.8413 | 61.891
5955.0938 | 123.3582 | -61.2076 | 61.8896 | -2.703 | -9.972 | -9.3844 | -3.8847 | 4.9896 | -2.7301 | -7.4061 | 61.9446 | 0.28984 | 61.8712 | -0.03768 | 0.048236 | 61.3327 | 0.007721 | 61.1292 | 58.5046 | 51.2356 | 51.8232 | 57.3229 | 66.1972 | 58.4775 | 53.8015 | 123.1522 | 61.4974 | 123.0788 | 61.1699 | 61.2558 | 122.5403 | 61.2153 | 122.3368 | 61.8963 | 61.9369 | 61.823 | 61.8635
5956.0625 | 123.2574 | -61.2488 | 61.8988 | -2.6847 | -9.8209 | -9.4805 | -3.9396 | 4.9438 | -2.7072 | -7.4519 | 61.94 | 0.28984 | 61.8484 | -0.028522 | 0.048236 | 61.3373 | 0.012299 | 61.1246 | 58.5641 | 51.4279 | 51.7682 | 57.3091 | 66.1926 | 58.5415 | 53.7969 | 123.1888 | 61.5386 | 123.0971 | 61.2203 | 61.297 | 122.586 | 61.2611 | 122.3734 | 61.8918 | 61.9277 | 61.8001 | 61.8361
5957.0938 | 123.3673 | -61.1847 | 61.9125 | -2.7717 | -9.8667 | -9.7003 | -4.0266 | 4.7928 | -2.8034 | -7.722 | 61.9492 | 0.30358 | 61.8529 | -0.028522 | 0.052814 | 61.3281 | 0.012299 | 61.12 | 58.413 | 51.318 | 51.4844 | 57.1581 | 65.9775 | 58.3813 | 53.4627 | 123.1339 | 61.4883 | 123.0376 | 61.1562 | 61.2375 | 122.5128 | 61.197 | 122.3047 | 61.8964 | 61.9369 | 61.8001 | 61.8406
5958.0625 | 123.3124 | -61.203 | 61.9583 | -2.8129 | -9.9766 | -9.7507 | -4.0953 | 4.6325 | -2.84 | -7.6671 | 61.9629 | 0.299 | 61.9033 | -0.028522 | 0.048236 | 61.3235 | 0.016878 | 61.1154 | 58.3901 | 51.2264 | 51.4523 | 57.1077 | 65.8355 | 58.363 | 53.5359 | 123.1659 | 61.502 | 123.1063 | 61.1745 | 61.2512 | 122.5265 | 61.2199 | 122.3184 | 61.9147 | 61.946 | 61.8551 | 61.8864
5959.0781 | 123.4085 | -61.1984 | 61.8988 | -2.7625 | -9.8117 | -9.563 | -4.022 | 4.7516 | -2.7851 | -7.5435 | 61.9583 | 0.299 | 61.8941 | -0.033101 | 0.048236 | 61.3373 | 0.007721 | 61.12 | 58.4359 | 51.3867 | 51.6355 | 57.1764 | 65.95 | 58.4134 | 53.655 | 123.1567 | 61.4974 | 123.0926 | 61.1653 | 61.2467 | 122.5357 | 61.2061 | 122.3184 | 61.9101 | 61.9506 | 61.8459 | 61.8864
5960.0625 | 123.3307 | -61.235 | 61.9171 | -2.7351 | -9.7476 | -9.4531 | -4.0037 | 4.7195 | -2.7622 | -7.429 | 61.9492 | 0.28984 | 61.8667 | -0.033101 | 0.052814 | 61.3327 | 0.012299 | 61.12 | 58.5 | 51.4874 | 51.782 | 57.2313 | 65.9546 | 58.4729 | 53.806 | 123.1842 | 61.5249 | 123.1017 | 61.2019 | 61.2879 | 122.5677 | 61.2473 | 122.3551 | 61.8964 | 61.9369 | 61.8139 | 61.8544
5961.1094 | 123.4039 | -61.1984 | 61.8759 | -2.7854 | -10.0361 | -9.5767 | -4.0266 | 4.6142 | -2.808 | -7.4519 | 61.9492 | 0.28984 | 61.8621 | -0.028522 | 0.052814 | 61.3281 | 0.003143 | 61.1154 | 58.413 | 51.1623 | 51.6217 | 57.1718 | 65.8126 | 58.3905 | 53.7465 | 123.1476 | 61.4883 | 123.0605 | 61.1699 | 61.2512 | 122.5265 | 61.2016 | 122.3139 | 61.8964 | 61.946 | 61.8093 | 61.8589
5962.0625 | 123.3078 | -61.2076 | 61.9263 | -2.758 | -9.9949 | -9.5584 | -4.022 | 4.6325 | -2.7851 | -7.4565 | 61.9492 | 0.29442 | 61.8575 | -0.023943 | 0.039079 | 61.3281 | 0.007721 | 61.1292 | 58.4496 | 51.2127 | 51.6492 | 57.1855 | 65.8401 | 58.4225 | 53.7511 | 123.1567 | 61.502 | 123.0651 | 61.1836 | 61.2467 | 122.5357 | 61.2153 | 122.3368 | 61.9101 | 61.9414 | 61.8184 | 61.8498
5963.0938 | 123.2941 | -61.2213 | 61.9263 | -2.7076 | -9.9628 | -9.508 | -3.9854 | 4.7332 | -2.7439 | -7.6671 | 61.9492 | 0.28984 | 61.8575 | -0.033101 | 0.052814 | 61.3327 | 0.003143 | 61.12 | 58.5137 | 51.2585 | 51.7133 | 57.2359 | 65.9546 | 58.4775 | 53.5543 | 123.1705 | 61.5112 | 123.0788 | 61.1882 | 61.2741 | 122.554 | 61.2245 | 122.3413 | 61.8964 | 61.946 | 61.8047 | 61.8544
5964.0625 | 123.349 | -61.2213 | 61.9354 | -2.7625 | -10.0773 | -9.5401 | -3.9992 | 4.6783 | -2.7896 | -7.8319 | 61.9583 | 0.28984 | 61.8667 | -0.023943 | 0.052814 | 61.3281 | 0.016878 | 61.1063 | 58.4588 | 51.144 | 51.6812 | 57.2222 | 65.8996 | 58.4317 | 53.3894 | 123.1796 | 61.5112 | 123.088 | 61.1974 | 61.2741 | 122.5494 | 61.2382 | 122.3276 | 61.9055 | 61.9414 | 61.8139 | 61.8498
5965.0625 | 123.3765 | -61.203 | 61.8988 | -2.7396 | -10.0864 | -9.476 | -3.9442 | 4.7653 | -2.7759 | -7.8502 | 61.9583 | 0.29442 | 61.8804 | -0.023943 | 0.048236 | 61.3327 | 0.007721 | 61.1109 | 58.4634 | 51.1166 | 51.727 | 57.2588 | 65.9683 | 58.4271 | 53.3528 | 123.1613 | 61.4974 | 123.0834 | 61.1791 | 61.2512 | 122.5357 | 61.2107 | 122.3139 | 61.9101 | 61.9506 | 61.8322 | 61.8727
5966.0625 | 123.3078 | -61.2305 | 61.9171 | -2.7854 | -10.1093 | -9.5126 | -3.9625 | 4.8157 | -2.8171 | -7.7724 | 61.9583 | 0.28984 | 61.8896 | -0.028522 | 0.048236 | 61.3235 | 0.007721 | 61.1109 | 58.445 | 51.1211 | 51.7179 | 57.2679 | 66.0461 | 58.4134 | 53.4581 | 123.1888 | 61.5203 | 123.12 | 61.2019 | 61.2787 | 122.554 | 61.2382 | 122.3413 | 61.9101 | 61.9506 | 61.8413 | 61.8818
5967.0625 | 123.3719 | -61.203 | 61.8805 | -2.7213 | -10.1093 | -9.4577 | -3.8664 | 4.8019 | -2.7576 | -7.7083 | 61.9583 | 0.29442 | 61.8941 | -0.023943 | 0.048236 | 61.3281 | 0.012299 | 61.12 | 58.4817 | 51.0937 | 51.7453 | 57.3366 | 66.0049 | 58.4454 | 53.4947 | 123.1613 | 61.4974 | 123.0971 | 61.1791 | 61.2512 | 122.5311 | 61.2153 | 122.323 | 61.9101 | 61.946 | 61.8459 | 61.8818
5968.0938 | 123.2986 | -61.2167 | 61.9675 | -2.7076 | -10.2055 | -9.5172 | -3.8297 | 4.7516 | -2.7393 | -8.0837 | 61.9537 | 0.28526 | 61.8804 | -0.023943 | 0.048236 | 61.3281 | 0.016878 | 61.12 | 58.5091 | 51.0112 | 51.6996 | 57.387 | 65.9683 | 58.4775 | 53.1331 | 123.1705 | 61.502 | 123.0971 | 61.1928 | 61.265 | 122.5448 | 61.2336 | 122.3368 | 61.9055 | 61.9369 | 61.8322 | 61.8635
5969.0625 | 123.3124 | -61.235 | 61.9308 | -2.7213 | -10.2925 | -9.6362 | -3.9122 | 4.7241 | -2.753 | -7.9372 | 61.9537 | 0.28984 | 61.8667 | -0.023943 | 0.048236 | 61.3281 | 0.012299 | 61.12 | 58.5137 | 50.9426 | 51.5988 | 57.3229 | 65.9591 | 58.482 | 53.2979 | 123.1888 | 61.5249 | 123.1017 | 61.2111 | 61.2833 | 122.5631 | 61.2473 | 122.3551 | 61.9055 | 61.9414 | 61.8184 | 61.8544
5970.0938 | 123.2712 | -61.2122 | 61.9537 | -2.7488 | -10.3337 | -9.682 | -3.9259 | 4.779 | -2.7805 | -8.2714 | 61.9583 | 0.28984 | 61.8712 | -0.028522 | 0.052814 | 61.3189 | 0.007721 | 61.1154 | 58.4634 | 50.8785 | 51.5302 | 57.2863 | 65.9912 | 58.4317 | 52.9408 | 123.1705 | 61.502 | 123.0834 | 61.1836 | 61.265 | 122.5311 | 61.2199 | 122.3276 | 61.9055 | 61.9506 | 61.8184 | 61.8635
5971.0625 | 123.3398 | -61.2305 | 61.8851 | -2.79 | -10.233 | -9.682 | -3.9854 | 4.7012 | -2.8217 | -8.1295 | 61.9583 | 0.299 | 61.8896 | -0.033101 | 0.039079 | 61.3281 | 0.007721 | 61.1063 | 58.4405 | 50.9975 | 51.5485 | 57.2451 | 65.9317 | 58.4088 | 53.101 | 123.1888 | 61.5295 | 123.12 | 61.1974 | 61.2695 | 122.5586 | 61.2382 | 122.3368 | 61.9192 | 61.9506 | 61.8505 | 61.8818
5972.0938 | 123.2986 | -61.1847 | 61.9537 | -2.8358 | -10.178 | -9.6225 | -3.9854 | 4.5868 | -2.8629 | -7.6259 | 61.9629 | 0.28984 | 61.9124 | -0.028522 | 0.048236 | 61.3281 | 0.012299 | 61.12 | 58.3489 | 51.0067 | 51.5622 | 57.1993 | 65.7714 | 58.3218 | 53.5588 | 123.1476 | 61.4745 | 123.0971 | 61.1562 | 61.2329 | 122.5128 | 61.197 | 122.3047 | 61.9147 | 61.9506 | 61.8642 | 61.9001
5973.0625 | 123.3124 | -61.2305 | 61.9446 | -2.8587 | -10.0956 | -9.6042 | -3.9717 | 4.5272 | -2.8812 | -7.6259 | 61.9629 | 0.28984 | 61.8667 | -0.03768 | 0.043657 | 61.3235 | 0.003143 | 61.1063 | 58.3718 | 51.1349 | 51.6263 | 57.2588 | 65.7577 | 58.3493 | 53.6046 | 123.1934 | 61.5203 | 123.0971 | 61.1928 | 61.2741 | 122.554 | 61.2336 | 122.3368 | 61.9192 | 61.9598 | 61.823 | 61.8635
5974.0625 | 123.2986 | -61.2076 | 61.94 | -2.8266 | -10.0544 | -9.6683 | -3.9671 | 4.5227 | -2.8675 | -7.5892 | 61.9537 | 0.28984 | 61.8667 | -0.023943 | 0.052814 | 61.3235 | 0.003143 | 61.12 | 58.3809 | 51.1532 | 51.5393 | 57.2405 | 65.7302 | 58.3401 | 53.6183 | 123.1613 | 61.4974 | 123.0742 | 61.1836 | 61.2604 | 122.5311 | 61.2107 | 122.3276 | 61.9009 | 61.9506 | 61.8139 | 61.8635
5975.0938 | 123.2574 | -61.1984 | 61.9675 | -2.8129 | -10.1139 | -9.7095 | -3.9259 | 4.5456 | -2.8446 | -7.7174 | 61.9537 | 0.29442 | 61.8804 | -0.033101 | 0.048236 | 61.3235 | 0.012299 | 61.1063 | 58.3855 | 51.0845 | 51.4889 | 57.2725 | 65.744 | 58.3538 | 53.481 | 123.1522 | 61.4928 | 123.0788 | 61.1653 | 61.2467 | 122.5219 | 61.2107 | 122.3047 | 61.9055 | 61.9414 | 61.8322 | 61.8681
5976.0625 | 123.2803 | -61.2625 | 61.8988 | -2.7351 | -9.9766 | -9.5675 | -3.7702 | 4.9896 | -2.7668 | -7.5206 | 61.9537 | 0.29442 | 61.8941 | -0.028522 | 0.048236 | 61.3327 | 0.007721 | 61.1246 | 58.5274 | 51.286 | 51.695 | 57.4923 | 66.2521 | 58.4958 | 53.742 | 123.2163 | 61.5569 | 123.1566 | 61.234 | 61.3107 | 122.5952 | 61.2702 | 122.3871 | 61.9055 | 61.946 | 61.8459 | 61.8864
5977.0781 | 123.2391 | -61.1938 | 61.9446 | -2.8724 | -10.059 | -9.6637 | -3.8297 | 4.9621 | -2.9133 | -7.6716 | 61.9583 | 0.299 | 61.8941 | -0.023943 | 0.048236 | 61.3327 | 0.007721 | 61.1109 | 58.3214 | 51.1349 | 51.5302 | 57.3641 | 66.156 | 58.2806 | 53.5222 | 123.1522 | 61.4928 | 123.088 | 61.1699 | 61.2421 | 122.5265 | 61.2016 | 122.3047 | 61.9101 | 61.9506 | 61.8459 | 61.8864
5978.0625 | 123.2803 | -61.2259 | 61.9308 | -2.8907 | -10.0407 | -9.6408 | -3.8572 | 4.9118 | -2.9224 | -7.6259 | 61.9492 | 0.29442 | 61.8758 | -0.028522 | 0.048236 | 61.3281 | 0.016878 | 61.1154 | 58.3352 | 51.1852 | 51.5851 | 57.3687 | 66.1377 | 58.3035 | 53.6 | 123.1751 | 61.5203 | 123.1017 | 61.1974 | 61.2741 | 122.554 | 61.2428 | 122.3413 | 61.9009 | 61.9323 | 61.8276 | 61.8589
5979.0781 | 123.2483 | -61.2167 | 61.9537 | -2.8953 | -9.9491 | -9.6088 | -3.871 | 4.9438 | -2.9224 | -7.6304 | 61.9583 | 0.29442 | 61.8621 | -0.023943 | 0.052814 | 61.3327 | 0.012299 | 61.12 | 58.3214 | 51.2677 | 51.608 | 57.3458 | 66.1606 | 58.2943 | 53.5863 | 123.1751 | 61.5112 | 123.0788 | 61.1928 | 61.2695 | 122.5494 | 61.229 | 122.3368 | 61.9055 | 61.946 | 61.8093 | 61.8498
5980.0625 | 123.2895 | -61.2167 | 61.9308 | -2.8724 | -9.7385 | -9.5767 | -4.0266 | 4.5181 | -2.9087 | -7.5755 | 61.9537 | 0.28984 | 61.8575 | -0.023943 | 0.048236 | 61.3235 | 0.007721 | 61.1109 | 58.3443 | 51.4783 | 51.64 | 57.1901 | 65.7348 | 58.3081 | 53.6412 | 123.1705 | 61.5066 | 123.0742 | 61.1928 | 61.265 | 122.5403 | 61.2245 | 122.3276 | 61.9055 | 61.946 | 61.8093 | 61.8498
5981.1094 | 123.3215 | -61.2213 | 61.9034 | -2.8129 | -9.6652 | -9.4897 | -3.9625 | 4.6966 | -2.84 | -7.5847 | 61.9492 | 0.299 | 61.8575 | -0.033101 | 0.039079 | 61.3281 | 0.012299 | 61.1246 | 58.4084 | 51.5561 | 51.7316 | 57.2588 | 65.9179 | 58.3813 | 53.6367 | 123.1705 | 61.5203 | 123.0788 | 61.1882 | 61.2604 | 122.5494 | 61.2336 | 122.3459 | 61.9101 | 61.9369 | 61.8184 | 61.8452
5982.0625 | 123.2803 | -61.235 | 61.8988 | -2.7534 | -9.5004 | -9.3157 | -3.8572 | 4.7607 | -2.7851 | -7.6167 | 61.9537 | 0.299 | 61.8529 | -0.028522 | 0.052814 | 61.3373 | 0.007721 | 61.12 | 58.4817 | 51.7347 | 51.9193 | 57.3778 | 65.9958 | 58.45 | 53.6183 | 123.1888 | 61.534 | 123.088 | 61.2065 | 61.2879 | 122.5723 | 61.2428 | 122.3551 | 61.9009 | 61.946 | 61.8001 | 61.8452
5983.0781 | 123.2574 | -61.2305 | 61.9583 | -2.7763 | -9.6515 | -9.4073 | -3.8435 | 4.7149 | -2.808 | -7.754 | 61.9537 | 0.29442 | 61.8758 | -0.028522 | 0.052814 | 61.3281 | 0.012299 | 61.12 | 58.4542 | 51.579 | 51.8232 | 57.387 | 65.9454 | 58.4225 | 53.4764 | 123.1842 | 61.5249 | 123.1063 | 61.2019 | 61.2833 | 122.5586 | 61.2428 | 122.3505 | 61.9009 | 61.9414 | 61.823 | 61.8635
5984.0625 | 123.2529 | -61.2076 | 61.9354 | -2.8999 | -9.9949 | -9.5859 | -3.8893 | 4.6737 | -2.9316 | -7.8868 | 61.9629 | 0.29442 | 61.8987 | -0.028522 | 0.043657 | 61.3281 | 0.012299 | 61.1109 | 58.3077 | 51.2127 | 51.6217 | 57.3183 | 65.8813 | 58.276 | 53.3208 | 123.1705 | 61.502 | 123.1063 | 61.1791 | 61.2512 | 122.5357 | 61.2199 | 122.3184 | 61.9192 | 61.9506 | 61.8551 | 61.8864
5985.0781 | 123.3032 | -61.2213 | 61.9629 | -2.8953 | -10.0452 | -9.5355 | -3.8435 | 4.6966 | -2.9316 | -7.69 | 61.9629 | 0.28526 | 61.8941 | -0.023943 | 0.052814 | 61.3281 | 0.007721 | 61.1109 | 58.326 | 51.1761 | 51.6858 | 57.3778 | 65.9179 | 58.2897 | 53.5314 | 123.1842 | 61.5066 | 123.1154 | 61.1974 | 61.2741 | 122.5494 | 61.229 | 122.3322 | 61.9101 | 61.9552 | 61.8413 | 61.8864
5986.0625 | 123.2346 | -61.235 | 61.9537 | -2.9502 | -10.178 | -9.6454 | -3.9167 | 4.5089 | -2.9865 | -7.7449 | 61.9675 | 0.29442 | 61.8941 | -0.028522 | 0.048236 | 61.3189 | 0.012299 | 61.1109 | 58.2848 | 51.057 | 51.5897 | 57.3183 | 65.744 | 58.2485 | 53.4902 | 123.2025 | 61.5295 | 123.1292 | 61.2065 | 61.2833 | 122.554 | 61.2473 | 122.3459 | 61.9192 | 61.9552 | 61.8459 | 61.8818
5987.0781 | 123.2758 | -61.2122 | 61.9675 | -2.8907 | -10.233 | -9.6545 | -3.8847 | 4.6051 | -2.927 | -7.8593 | 61.9492 | 0.28984 | 61.8758 | -0.023943 | 0.052814 | 61.3281 | 0.012299 | 61.1109 | 58.3214 | 50.9792 | 51.5576 | 57.3275 | 65.8172 | 58.2852 | 53.3528 | 123.1613 | 61.502 | 123.088 | 61.1882 | 61.265 | 122.5403 | 61.2245 | 122.323 | 61.8964 | 61.9369 | 61.823 | 61.8635
5988.0625 | 123.2986 | -61.2213 | 61.94 | -2.8816 | -10.091 | -9.6591 | -3.9671 | 4.6783 | -2.9178 | -7.8868 | 61.9537 | 0.29442 | 61.8621 | -0.023943 | 0.043657 | 61.3235 | 0.012299 | 61.1017 | 58.3397 | 51.1303 | 51.5622 | 57.2542 | 65.8996 | 58.3035 | 53.3345 | 123.1751 | 61.5157 | 123.0834 | 61.1974 | 61.265 | 122.5448 | 61.2336 | 122.323 | 61.9101 | 61.9414 | 61.8184 | 61.8498
5989.0938 | 123.1796 | -61.1893 | 61.9583 | -2.9548 | -10.1872 | -9.8239 | -4.0175 | 4.6051 | -2.9819 | -8.0058 | 61.9583 | 0.28984 | 61.8712 | -0.033101 | 0.048236 | 61.3189 | 0.003143 | 61.1109 | 58.2344 | 51.0021 | 51.3653 | 57.1718 | 65.7943 | 58.2073 | 53.1834 | 123.1476 | 61.4791 | 123.0605 | 61.1562 | 61.2375 | 122.5082 | 61.1924 | 122.3001 | 61.9101 | 61.9552 | 61.823 | 61.8681
5990.0625 | 123.2529 | -61.2259 | 61.94 | -2.9136 | -10.1368 | -9.7553 | -3.9808 | 4.5547 | -2.9453 | -7.8868 | 61.9675 | 0.299 | 61.8621 | -0.028522 | 0.048236 | 61.3281 | 0.007721 | 61.1109 | 58.3123 | 51.0891 | 51.4706 | 57.2451 | 65.7806 | 58.2806 | 53.3391 | 123.1934 | 61.5249 | 123.088 | 61.1974 | 61.2741 | 122.554 | 61.2336 | 122.3368 | 61.9192 | 61.9598 | 61.8138 | 61.8544
5991.0938 | 123.3902 | -61.1938 | 61.9034 | -2.9823 | -9.9949 | -9.7278 | -4.0129 | 4.5044 | -3.0186 | -7.8685 | 61.9629 | 0.299 | 61.885 | -0.023943 | 0.048236 | 61.3144 | 0.003143 | 61.1109 | 58.2116 | 51.199 | 51.4661 | 57.181 | 65.6982 | 58.1753 | 53.3253 | 123.1567 | 61.4928 | 123.0788 | 61.1699 | 61.2421 | 122.5082 | 61.197 | 122.3047 | 61.9147 | 61.9598 | 61.8367 | 61.8818
5992.0625 | 123.2803 | -61.2167 | 61.9308 | -3.0876 | -10.1139 | -9.7873 | -4.077 | 4.4448 | -3.1193 | -7.9326 | 61.9675 | 0.28984 | 61.8987 | -0.033101 | 0.043657 | 61.3144 | 0.007721 | 61.1017 | 58.1291 | 51.1028 | 51.4294 | 57.1398 | 65.6616 | 58.0974 | 53.2841 | 123.1842 | 61.5066 | 123.1154 | 61.1836 | 61.2604 | 122.5311 | 61.2245 | 122.3184 | 61.9238 | 61.9598 | 61.8551 | 61.891
5993.0781 | 123.2162 | -61.2076 | 61.9629 | -3.1609 | -10.2742 | -9.7873 | -4.0816 | 4.5227 | -3.1834 | -7.983 | 61.9812 | 0.28984 | 61.9033 | -0.03768 | 0.048236 | 61.3189 | 0.012299 | 61.0971 | 58.0467 | 50.9334 | 51.4203 | 57.126 | 65.7302 | 58.0242 | 53.2246 | 123.1888 | 61.4974 | 123.1109 | 61.1699 | 61.2558 | 122.5265 | 61.2199 | 122.3047 | 61.933 | 61.9689 | 61.8551 | 61.891
5994.0625 | 123.317 | -61.1664 | 61.94 | -3.2295 | -10.2742 | -9.7644 | -4.0816 | 4.4952 | -3.2566 | -7.8868 | 61.9766 | 0.28984 | 61.9124 | -0.019364 | 0.048236 | 61.3098 | 0.012299 | 61.1063 | 57.9369 | 50.8922 | 51.402 | 57.0848 | 65.6616 | 57.9097 | 53.2796 | 123.143 | 61.4562 | 123.0788 | 61.147 | 61.2146 | 122.4762 | 61.1787 | 122.2727 | 61.9284 | 61.9643 | 61.8642 | 61.9001
5995.0781 | 123.349 | -61.1755 | 61.9583 | -3.2341 | -10.4711 | -9.9338 | -4.1045 | 4.3945 | -3.2704 | -8.0562 | 61.9721 | 0.28984 | 61.8896 | -0.033101 | 0.048236 | 61.3144 | 0.012299 | 61.1063 | 57.9414 | 50.7045 | 51.2417 | 57.0711 | 65.57 | 57.9052 | 53.1193 | 123.1476 | 61.4654 | 123.0651 | 61.1424 | 61.2238 | 122.4899 | 61.1878 | 122.2818 | 61.9238 | 61.9598 | 61.8413 | 61.8773
5996.0625 | 123.2986 | -61.2213 | 61.9308 | -3.1837 | -10.4482 | -9.9109 | -4.0724 | 4.4219 | -3.2154 | -8.0516 | 61.9721 | 0.29442 | 61.8804 | -0.028522 | 0.048236 | 61.3098 | 0.007721 | 61.088 | 58.0376 | 50.7731 | 51.3104 | 57.1489 | 65.6433 | 58.0059 | 53.1697 | 123.1934 | 61.5157 | 123.1017 | 61.1928 | 61.2695 | 122.5311 | 61.229 | 122.3093 | 61.9238 | 61.9643 | 61.8322 | 61.8727
5997.0938 | 123.3078 | -61.203 | 61.9492 | -3.1105 | -10.4344 | -9.8652 | -3.8893 | 4.4128 | -3.1422 | -8.0608 | 61.9675 | 0.28984 | 61.8758 | -0.028522 | 0.052814 | 61.3144 | 0.003143 | 61.1017 | 58.0925 | 50.7686 | 51.3379 | 57.3137 | 65.6158 | 58.0608 | 53.1422 | 123.1705 | 61.4928 | 123.0788 | 61.1745 | 61.2558 | 122.5174 | 61.2061 | 122.3047 | 61.9147 | 61.9643 | 61.823 | 61.8727
5998.0625 | 123.3032 | -61.2076 | 61.9171 | -3.1059 | -10.4299 | -9.7553 | -3.8893 | 4.4174 | -3.133 | -7.9967 | 61.9629 | 0.28984 | 61.8712 | -0.033101 | 0.057392 | 61.3144 | 0.007721 | 61.0971 | 58.1017 | 50.7777 | 51.4523 | 57.3183 | 65.625 | 58.0746 | 53.2109 | 123.1705 | 61.4974 | 123.0788 | 61.1745 | 61.265 | 122.5219 | 61.2153 | 122.3047 | 61.9055 | 61.9552 | 61.8139 | 61.8635
5999.0781 | 123.3307 | -61.171 | 61.9812 | -3.0647 | -10.4024 | -9.682 | -3.9305 | 4.4128 | -3.0964 | -7.9601 | 61.9629 | 0.28984 | 61.8896 | -0.023943 | 0.048236 | 61.3189 | 0.007721 | 61.1017 | 58.1063 | 50.7686 | 51.489 | 57.2405 | 65.5838 | 58.0746 | 53.2109 | 123.1339 | 61.4608 | 123.0605 | 61.147 | 61.2192 | 122.4899 | 61.1787 | 122.2727 | 61.9147 | 61.9552 | 61.8413 | 61.8818
6000.0625 | 123.2986 | -61.1938 | 61.9354 | -3.0647 | -10.4161 | -9.7003 | -3.9717 | 4.367 | -3.0872 | -7.928 | 61.9675 | 0.28984 | 61.9079 | -0.023943 | 0.043657 | 61.3144 | 0.003143 | 61.1017 | 58.1291 | 50.7777 | 51.4935 | 57.2222 | 65.5609 | 58.1066 | 53.2658 | 123.1613 | 61.4837 | 123.1017 | 61.1699 | 61.2375 | 122.5082 | 61.197 | 122.2956 | 61.9238 | 61.9643 | 61.8642 | 61.9047
6001.1094 | 123.3765 | -61.171 | 61.9446 | -3.0922 | -10.1734 | -9.7415 | -4.0266 | 4.3304 | -3.1284 | -7.9646 | 61.9675 | 0.29442 | 61.9079 | -0.033101 | 0.052814 | 61.3144 | 0.012299 | 61.0926 | 58.0788 | 50.9975 | 51.4294 | 57.1443 | 65.5013 | 58.0425 | 53.2063 | 123.1384 | 61.4654 | 123.0788 | 61.1379 | 61.2238 | 122.4853 | 61.1833 | 122.2635 | 61.9147 | 61.9552 | 61.8551 | 61.8956
6002.0625 | 123.2712 | -61.2213 | 61.9537 | -3.1151 | -10.3154 | -9.8606 | -4.0358 | 4.3167 | -3.1422 | -8.0471 | 61.9721 | 0.29442 | 61.9124 | -0.023943 | 0.043657 | 61.3189 | 0.007721 | 61.0971 | 58.1062 | 50.9059 | 51.3607 | 57.1855 | 65.538 | 58.0791 | 53.1743 | 123.1934 | 61.5157 | 123.1338 | 61.1974 | 61.265 | 122.5403 | 61.229 | 122.3184 | 61.9284 | 61.9643 | 61.8688 | 61.9047
6003.0781 | 123.3765 | -61.1801 | 61.8988 | -3.0968 | -10.3566 | -9.8377 | -4.0083 | 4.1885 | -3.1284 | -8.015 | 61.9721 | 0.29442 | 61.9033 | -0.028522 | 0.057392 | 61.3052 | 0.012299 | 61.1017 | 58.0834 | 50.8235 | 51.3424 | 57.1718 | 65.3686 | 58.0517 | 53.1651 | 123.1522 | 61.4745 | 123.0834 | 61.1516 | 61.2375 | 122.4853 | 61.1924 | 122.2818 | 61.9147 | 61.9598 | 61.8459 | 61.891
6004.0625 | 123.3032 | -61.2076 | 61.9446 | -3.1105 | -10.2604 | -9.8468 | -3.99 | 4.1198 | -3.1468 | -8.0699 | 61.9721 | 0.29442 | 61.885 | -0.023943 | 0.048236 | 61.3144 | 0.007721 | 61.1063 | 58.0971 | 50.9471 | 51.3607 | 57.2176 | 65.3274 | 58.0608 | 53.1376 | 123.1796 | 61.502 | 123.0926 | 61.1836 | 61.2558 | 122.5219 | 61.2153 | 122.3139 | 61.9238 | 61.9643 | 61.8367 | 61.8773
6005.0938 | 123.2758 | -61.1847 | 61.9949 | -3.138 | -10.2147 | -9.8697 | -4.0266 | 4.2846 | -3.1742 | -8.0471 | 61.9675 | 0.28984 | 61.885 | -0.028522 | 0.048236 | 61.3052 | 0.012299 | 61.1063 | 58.0467 | 50.97 | 51.315 | 57.1581 | 65.4693 | 58.0105 | 53.1376 | 123.1522 | 61.4745 | 123.0697 | 61.1562 | 61.2329 | 122.4899 | 61.197 | 122.291 | 61.9192 | 61.9552 | 61.8367 | 61.8727
6006.0625 | 123.3719 | -61.1847 | 61.9034 | -3.1471 | -10.1231 | -9.8514 | -4.0358 | 4.0603 | -3.1788 | -8.0745 | 61.9675 | 0.29442 | 61.8712 | -0.033101 | 0.043657 | 61.3144 | 0.007721 | 61.0926 | 58.0376 | 51.0616 | 51.3333 | 57.1489 | 65.245 | 58.0059 | 53.1102 | 123.1522 | 61.4791 | 123.0559 | 61.1516 | 61.2283 | 122.4991 | 61.1924 | 122.2772 | 61.9238 | 61.9598 | 61.8276 | 61.8635
6007.0781 | 123.3398 | -61.203 | 61.9354 | -3.0556 | -9.9308 | -9.7141 | -3.9763 | 3.9367 | -3.0643 | -7.7953 | 61.9629 | 0.30358 | 61.8712 | -0.028522 | 0.06197 | 61.3189 | 0.007721 | 61.1063 | 58.1475 | 51.2722 | 51.4889 | 57.2267 | 65.1397 | 58.1387 | 53.4078 | 123.1659 | 61.5066 | 123.0742 | 61.1745 | 61.265 | 122.5219 | 61.2107 | 122.3093 | 61.9009 | 61.9552 | 61.8093 | 61.8635
6008.0625 | 123.3078 | -61.1893 | 61.9308 | -3.0601 | -10.0315 | -9.737 | -3.9579 | 4.0054 | -3.046 | -7.896 | 61.9721 | 0.28984 | 61.8987 | -0.033101 | 0.052814 | 61.3189 | 0.012299 | 61.1154 | 58.1291 | 51.1578 | 51.4523 | 57.2313 | 65.1946 | 58.1432 | 53.2933 | 123.1613 | 61.4791 | 123.088 | 61.1562 | 61.2421 | 122.5082 | 61.2016 | 122.3047 | 61.9192 | 61.9598 | 61.8459 | 61.8864
6009.0625 | 123.2574 | -61.2122 | 61.9492 | -3.1105 | -10.146 | -9.8331 | -3.9808 | 3.9779 | -3.1193 | -8.0928 | 61.9766 | 0.29442 | 61.917 | -0.028522 | 0.043657 | 61.3052 | 0.003143 | 61.1109 | 58.1017 | 51.0662 | 51.3791 | 57.2313 | 65.19 | 58.0929 | 53.1193 | 123.1888 | 61.5066 | 123.1292 | 61.1836 | 61.2558 | 122.5174 | 61.2153 | 122.323 | 61.933 | 61.9735 | 61.8734 | 61.9139
6010.0625 | 123.3032 | -61.2213 | 61.9171 | -3.051 | -9.972 | -9.6545 | -3.9122 | 4.042 | -3.0552 | -8.0745 | 61.9721 | 0.29442 | 61.9033 | -0.03768 | 0.043657 | 61.3189 | 0.003143 | 61.1154 | 58.1703 | 51.2493 | 51.5668 | 57.3092 | 65.2633 | 58.1661 | 53.1468 | 123.1934 | 61.5157 | 123.1246 | 61.1836 | 61.265 | 122.5403 | 61.2245 | 122.3368 | 61.9284 | 61.9689 | 61.8596 | 61.9001
6011.0938 | 123.3353 | -61.171 | 61.9492 | -3.1013 | -10.0223 | -9.6957 | -3.9854 | 3.9321 | -3.1147 | -7.9784 | 61.9721 | 0.299 | 61.8987 | -0.019364 | 0.048236 | 61.3144 | 0.012299 | 61.1154 | 58.0696 | 51.1486 | 51.4752 | 57.1855 | 65.1031 | 58.0562 | 53.1926 | 123.143 | 61.47 | 123.0697 | 61.1516 | 61.2192 | 122.4853 | 61.1833 | 122.2864 | 61.9238 | 61.9598 | 61.8505 | 61.8864
6012.0625 | 123.2758 | -61.1893 | 61.9308 | -3.17 | -10.0864 | -9.8056 | -4.0404 | 4.042 | -3.1697 | -8.1707 | 61.9766 | 0.29442 | 61.8987 | -0.033101 | 0.048236 | 61.3144 | 0.007721 | 61.1109 | 58.0193 | 51.1028 | 51.3836 | 57.1489 | 65.2312 | 58.0196 | 53.0186 | 123.1659 | 61.4837 | 123.088 | 61.1562 | 61.2375 | 122.5036 | 61.197 | 122.3001 | 61.9284 | 61.9689 | 61.8505 | 61.891
6013.0781 | 123.4039 | -61.171 | 61.9263 | -3.2433 | -10.0498 | -9.856 | -4.1273 | 3.8863 | -3.2109 | -8.0699 | 61.9721 | 0.28984 | 61.8804 | -0.033101 | 0.043657 | 61.3052 | 0.007721 | 61.1109 | 57.9277 | 51.1211 | 51.315 | 57.0436 | 65.0573 | 57.9601 | 53.101 | 123.143 | 61.4608 | 123.0514 | 61.1379 | 61.2146 | 122.4762 | 61.1787 | 122.2818 | 61.9284 | 61.9643 | 61.8367 | 61.8727
6014.0625 | 123.3353 | -61.1755 | 61.9537 | -3.376 | -10.2559 | -10.0346 | -4.2006 | 3.8039 | -3.3574 | -8.1936 | 61.9812 | 0.29442 | 61.8941 | -0.023943 | 0.052814 | 61.2961 | 0.012299 | 61.1017 | 57.7995 | 50.9197 | 51.141 | 56.9749 | 64.9795 | 57.8182 | 52.982 | 123.1568 | 61.47 | 123.0697 | 61.1516 | 61.2284 | 122.4716 | 61.1878 | 122.2772 | 61.9284 | 61.9689 | 61.8413 | 61.8818
6015.0781 | 123.3765 | -61.1389 | 61.9354 | -3.4218 | -10.3383 | -10.0712 | -4.2464 | 3.7444 | -3.4215 | -8.2714 | 61.9858 | 0.28984 | 61.8987 | -0.033101 | 0.052814 | 61.3006 | 0.012299 | 61.0971 | 57.7171 | 50.8006 | 51.0677 | 56.8925 | 64.8833 | 57.7175 | 52.8675 | 123.1247 | 61.4288 | 123.0376 | 61.1058 | 61.1917 | 122.4395 | 61.1512 | 122.236 | 61.933 | 61.9735 | 61.8459 | 61.8864
6016.0625 | 123.2849 | -61.2076 | 61.9263 | -3.3898 | -10.2879 | -10.0208 | -4.2464 | 3.6986 | -3.3894 | -8.2302 | 61.9812 | 0.28984 | 61.9124 | -0.028522 | 0.043657 | 61.2961 | 0.007721 | 61.088 | 57.8178 | 50.9197 | 51.1868 | 56.9612 | 64.9062 | 57.8182 | 52.9774 | 123.1888 | 61.4974 | 123.12 | 61.1791 | 61.2512 | 122.5036 | 61.2153 | 122.2956 | 61.9376 | 61.9735 | 61.8688 | 61.9047
6017.0938 | 123.3078 | -61.1755 | 61.9583 | -3.3989 | -10.2788 | -10.0071 | -4.2601 | 3.7353 | -3.394 | -8.2027 | 61.9858 | 0.29442 | 61.9262 | -0.028522 | 0.043657 | 61.3006 | 0.007721 | 61.0971 | 57.7766 | 50.8968 | 51.1684 | 56.9154 | 64.9108 | 57.7815 | 52.9728 | 123.1613 | 61.47 | 123.1017 | 61.147 | 61.2192 | 122.4762 | 61.1833 | 122.2727 | 61.9421 | 61.9781 | 61.8825 | 61.9185
6018.0625 | 123.2941 | -61.1984 | 61.9629 | -3.4951 | -10.4024 | -10.1124 | -4.3288 | 3.7215 | -3.4856 | -8.2989 | 61.9995 | 0.299 | 61.9399 | -0.03768 | 0.048236 | 61.2915 | 0.007721 | 61.0926 | 57.7034 | 50.796 | 51.086 | 56.8696 | 64.9199 | 57.7129 | 52.8996 | 123.198 | 61.4974 | 123.1383 | 61.1607 | 61.2467 | 122.4899 | 61.2061 | 122.291 | 61.9513 | 61.9918 | 61.8917 | 61.9322
6019.0938 | 123.3948 | -61.1526 | 61.94 | -3.4447 | -10.32 | -10.03 | -4.3288 | 3.4331 | -3.4444 | -8.221 | 61.9858 | 0.29442 | 61.9262 | -0.028522 | 0.048236 | 61.2869 | 0.012299 | 61.0926 | 57.7079 | 50.8327 | 51.1227 | 56.8238 | 64.5858 | 57.7083 | 52.9316 | 123.1384 | 61.4471 | 123.0788 | 61.1241 | 61.2009 | 122.4395 | 61.1649 | 122.2452 | 61.9376 | 61.9735 | 61.8779 | 61.9139
6020.0625 | 123.3261 | -61.1801 | 61.972 | -3.4447 | -10.2055 | -9.9155 | -4.2784 | 3.488 | -3.4489 | -8.1523 | 61.9904 | 0.29442 | 61.8987 | -0.023943 | 0.052814 | 61.2961 | 0.012299 | 61.0834 | 57.7354 | 50.9746 | 51.2646 | 56.9017 | 64.6682 | 57.7312 | 53.0278 | 123.1705 | 61.4745 | 123.0788 | 61.1562 | 61.2329 | 122.4762 | 61.1924 | 122.2635 | 61.9376 | 61.9781 | 61.8459 | 61.8864
6021.1094 | 123.262 | -61.1801 | 62.0132 | -3.4493 | -10.2742 | -10.0025 | -4.283 | 3.3782 | -3.4627 | -8.2897 | 61.9858 | 0.29442 | 61.8987 | -0.028522 | 0.048236 | 61.2961 | 0.003143 | 61.0926 | 57.7308 | 50.9059 | 51.1776 | 56.8971 | 64.5583 | 57.7174 | 52.8904 | 123.1659 | 61.4745 | 123.0788 | 61.1516 | 61.2284 | 122.4762 | 61.1833 | 122.2727 | 61.9376 | 61.9826 | 61.8505 | 61.8956
6022.0625 | 123.3261 | -61.1755 | 61.9675 | -3.4676 | -10.3062 | -10.1124 | -4.3334 | 3.2042 | -3.4901 | -8.3263 | 61.9858 | 0.299 | 61.9033 | -0.028522 | 0.048236 | 61.2961 | 0.016878 | 61.0788 | 57.7079 | 50.8693 | 51.0631 | 56.8422 | 64.3797 | 57.6854 | 52.8492 | 123.1613 | 61.4745 | 123.0788 | 61.147 | 61.2238 | 122.4716 | 61.1924 | 122.2544 | 61.9376 | 61.9689 | 61.8551 | 61.8864
6023.0781 | 123.3948 | -61.1298 | 61.9354 | -3.5775 | -10.3932 | -10.1948 | -4.3883 | 3.2454 | -3.5863 | -8.4041 | 61.9995 | 0.28984 | 61.9079 | -0.028522 | 0.043657 | 61.2869 | 0.007721 | 61.0788 | 57.5523 | 50.7365 | 50.9349 | 56.7414 | 64.3752 | 57.5435 | 52.7256 | 123.1293 | 61.4196 | 123.0376 | 61.1012 | 61.1734 | 122.4167 | 61.1375 | 122.2086 | 61.9559 | 61.9918 | 61.8642 | 61.9001
6024.0625 | 123.3078 | -61.1526 | 61.9629 | -3.518 | -10.3429 | -10.1032 | -4.338 | 3.2454 | -3.5359 | -8.3172 | 61.9949 | 0.299 | 61.9216 | -0.019364 | 0.052814 | 61.2869 | 0.003143 | 61.0742 | 57.6347 | 50.8098 | 51.0494 | 56.8147 | 64.3981 | 57.6167 | 52.8355 | 123.1476 | 61.4516 | 123.0743 | 61.1333 | 61.2055 | 122.4395 | 61.1558 | 122.2269 | 61.9421 | 61.9918 | 61.8688 | 61.9185
6025.0781 | 123.4085 | -61.1618 | 61.9492 | -3.4493 | -10.2971 | -10.0712 | -4.3059 | 3.2912 | -3.4718 | -8.2622 | 61.9995 | 0.29442 | 61.9262 | -0.033101 | 0.048236 | 61.2915 | 0.012299 | 61.0834 | 57.7125 | 50.8647 | 51.0906 | 56.8559 | 64.453 | 57.69 | 52.8996 | 123.1613 | 61.4562 | 123.088 | 61.1287 | 61.21 | 122.4533 | 61.1741 | 122.2452 | 61.9513 | 61.9872 | 61.8779 | 61.9139
6026.0625 | 123.2895 | -61.1893 | 61.9858 | -3.4356 | -10.2147 | -9.975 | -4.2647 | 3.3141 | -3.4535 | -8.2439 | 61.9904 | 0.28984 | 61.9308 | -0.028522 | 0.052814 | 61.2915 | 0.007721 | 61.0971 | 57.7537 | 50.9746 | 51.2142 | 56.9246 | 64.5034 | 57.7358 | 52.9454 | 123.1796 | 61.4791 | 123.12 | 61.1607 | 61.2421 | 122.4807 | 61.197 | 122.2864 | 61.9376 | 61.9827 | 61.8779 | 61.923
6027.0938 | 123.3765 | -61.1481 | 61.972 | -3.3944 | -10.178 | -10.0025 | -4.2647 | 3.3507 | -3.4169 | -8.2119 | 61.9858 | 0.29442 | 61.9033 | -0.033101 | 0.048236 | 61.2869 | 0.007721 | 61.0971 | 57.7537 | 50.97 | 51.1456 | 56.8834 | 64.4988 | 57.7312 | 52.9362 | 123.1339 | 61.4425 | 123.0514 | 61.115 | 61.1963 | 122.435 | 61.1558 | 122.2452 | 61.9376 | 61.9781 | 61.8551 | 61.8956
6028.0625 | 123.2849 | -61.1893 | 62.0178 | -3.3669 | -10.2925 | -10.0758 | -4.3013 | 3.3507 | -3.3848 | -8.3584 | 61.9812 | 0.299 | 61.9079 | -0.028522 | 0.048236 | 61.2915 | 0.003143 | 61.1017 | 57.8224 | 50.8968 | 51.1135 | 56.8879 | 64.54 | 57.8044 | 52.8309 | 123.1705 | 61.4883 | 123.0971 | 61.1607 | 61.2375 | 122.4807 | 61.1924 | 122.291 | 61.933 | 61.9781 | 61.8596 | 61.9047
6029.0781 | 123.381 | -61.1755 | 61.9308 | -3.3577 | -10.2742 | -10.0483 | -4.251 | 3.369 | -3.3711 | -8.3034 | 61.9858 | 0.28984 | 61.885 | -0.033101 | 0.043657 | 61.2915 | 0.007721 | 61.0834 | 57.8178 | 50.9014 | 51.1272 | 56.9246 | 64.5446 | 57.8044 | 52.8721 | 123.1613 | 61.4654 | 123.0605 | 61.1424 | 61.2192 | 122.467 | 61.1833 | 122.2589 | 61.9421 | 61.9781 | 61.8413 | 61.8773
6030.0625 | 123.2895 | -61.1755 | 61.9766 | -3.3577 | -10.2192 | -9.975 | -4.2235 | 3.337 | -3.3711 | -8.189 | 61.9766 | 0.299 | 61.8987 | -0.028522 | 0.052814 | 61.2961 | 0.012299 | 61.0834 | 57.8178 | 50.9563 | 51.2005 | 56.952 | 64.5125 | 57.8044 | 52.9866 | 123.1522 | 61.4745 | 123.0742 | 61.147 | 61.2284 | 122.4716 | 61.1878 | 122.2589 | 61.9238 | 61.9643 | 61.8459 | 61.8864
6031.1094 | 123.2849 | -61.1801 | 61.9858 | -3.3852 | -10.1414 | -9.8743 | -4.196 | 3.2408 | -3.394 | -8.1432 | 61.9858 | 0.299 | 61.9262 | -0.028522 | 0.052814 | 61.2961 | 0.012299 | 61.088 | 57.7949 | 51.0387 | 51.3058 | 56.9841 | 64.421 | 57.7861 | 53.0369 | 123.1659 | 61.4791 | 123.1063 | 61.1516 | 61.2329 | 122.4762 | 61.1924 | 122.2681 | 61.933 | 61.9735 | 61.8734 | 61.9139
6032.0625 | 123.2986 | -61.1801 | 62.0087 | -3.4447 | -10.2421 | -9.9567 | -4.2784 | 3.0806 | -3.4627 | -8.2393 | 61.9949 | 0.29442 | 61.9308 | -0.023943 | 0.052814 | 61.3006 | 0.007721 | 61.088 | 57.7354 | 50.938 | 51.2234 | 56.9017 | 64.2607 | 57.7174 | 52.9408 | 123.1751 | 61.4745 | 123.1109 | 61.1562 | 61.2329 | 122.4807 | 61.1878 | 122.2681 | 61.9421 | 61.9872 | 61.8779 | 61.923
6033.0781 | 123.3627 | -61.1755 | 61.94 | -3.3852 | -10.2467 | -9.9979 | -4.3151 | 3.0211 | -3.4169 | -8.2485 | 61.9904 | 0.29442 | 61.9308 | -0.033101 | 0.043657 | 61.2915 | 0.007721 | 61.088 | 57.7903 | 50.9288 | 51.1776 | 56.8605 | 64.1966 | 57.7587 | 52.927 | 123.1659 | 61.47 | 123.1063 | 61.1424 | 61.2192 | 122.467 | 61.1833 | 122.2635 | 61.9467 | 61.9827 | 61.8871 | 61.923
6034.0625 | 123.2574 | -61.1755 | 61.9995 | -3.3989 | -10.3291 | -10.1078 | -4.4021 | 3.0211 | -3.4306 | -8.3401 | 61.9949 | 0.28984 | 61.9216 | -0.028522 | 0.052814 | 61.2869 | -0.001436 | 61.0834 | 57.7766 | 50.8464 | 51.0677 | 56.7735 | 64.1966 | 57.7449 | 52.8355 | 123.1705 | 61.4654 | 123.0971 | 61.147 | 61.2284 | 122.4624 | 61.1741 | 122.2589 | 61.9421 | 61.9964 | 61.8688 | 61.923
6035.0938 | 123.4406 | -61.1389 | 61.9995 | -3.3989 | -10.3108 | -10.0895 | -4.3883 | 3.0119 | -3.426 | -8.3126 | 61.9949 | 0.28984 | 61.8987 | -0.023943 | 0.052814 | 61.2915 | 0.007721 | 61.0834 | 57.74 | 50.8281 | 51.0494 | 56.7506 | 64.1509 | 57.7129 | 52.8263 | 123.1339 | 61.4288 | 123.0376 | 61.115 | 61.1917 | 122.4304 | 61.1466 | 122.2223 | 61.9421 | 61.9872 | 61.8459 | 61.891
6036.0625 | 123.3353 | -61.2076 | 61.9354 | -3.3989 | -10.2742 | -10.0712 | -4.338 | 2.9341 | -3.4352 | -8.3492 | 61.9812 | 0.28984 | 61.8987 | -0.028522 | 0.043657 | 61.2961 | 0.012299 | 61.0742 | 57.8087 | 50.9334 | 51.1364 | 56.8696 | 64.1417 | 57.7724 | 52.8584 | 123.1888 | 61.4974 | 123.1063 | 61.1791 | 61.2512 | 122.5036 | 61.2199 | 122.2818 | 61.9376 | 61.9689 | 61.8551 | 61.8864
6037.0781 | 123.4268 | -61.1435 | 61.9308 | -3.4722 | -10.2971 | -10.1765 | -4.425 | 2.8929 | -3.5085 | -8.427 | 61.9949 | 0.29442 | 61.8987 | -0.028522 | 0.048236 | 61.2823 | -0.001436 | 61.0788 | 57.6713 | 50.8464 | 50.967 | 56.7185 | 64.0364 | 57.635 | 52.7165 | 123.1384 | 61.4379 | 123.0422 | 61.115 | 61.1917 | 122.4258 | 61.1421 | 122.2223 | 61.9467 | 61.9964 | 61.8505 | 61.9001
6038.0625 | 123.3353 | -61.1298 | 62.0132 | -3.5363 | -10.4528 | -10.3322 | -4.4616 | 2.7922 | -3.5725 | -8.6788 | 62.0087 | 0.29442 | 61.917 | -0.023943 | 0.057392 | 61.2823 | 0.012299 | 61.0651 | 57.5935 | 50.677 | 50.7976 | 56.6682 | 63.922 | 57.5572 | 52.4509 | 123.1384 | 61.4242 | 123.0468 | 61.1058 | 61.1872 | 122.4121 | 61.1421 | 122.1948 | 61.9513 | 61.9964 | 61.8596 | 61.9047
6039.0781 | 123.3536 | -61.1618 | 61.9675 | -3.4722 | -10.4528 | -10.2269 | -4.4112 | 2.87 | -3.5085 | -8.6514 | 61.9995 | 0.29442 | 61.9262 | -0.028522 | 0.048236 | 61.2823 | 0.012299 | 61.0697 | 57.6896 | 50.7091 | 50.9349 | 56.7506 | 64.0318 | 57.6534 | 52.5104 | 123.1613 | 61.4562 | 123.088 | 61.1333 | 61.21 | 122.4441 | 61.1741 | 122.2315 | 61.9513 | 61.9872 | 61.8779 | 61.9139
6040.0625 | 123.3032 | -61.171 | 61.9812 | -3.4447 | -10.3932 | -10.1032 | -4.3196 | 2.9295 | -3.4901 | -8.4454 | 62.0041 | 0.28526 | 61.9399 | -0.028522 | 0.048236 | 61.2869 | 0.007721 | 61.0742 | 57.7262 | 50.7777 | 51.0677 | 56.8513 | 64.1005 | 57.6808 | 52.7256 | 123.1751 | 61.4562 | 123.1109 | 61.1424 | 61.2192 | 122.4579 | 61.1787 | 122.2452 | 61.9559 | 61.9964 | 61.8917 | 61.9322
6041.1094 | 123.3856 | -61.171 | 61.9675 | -3.5409 | -10.4207 | -10.1444 | -4.3563 | 2.9295 | -3.5863 | -8.4637 | 61.9949 | 0.28984 | 61.9353 | -0.033101 | 0.043657 | 61.2823 | 0.007721 | 61.0605 | 57.6301 | 50.7503 | 51.0265 | 56.8147 | 64.1005 | 57.5847 | 52.7073 | 123.1659 | 61.4608 | 123.1063 | 61.1379 | 61.2146 | 122.4533 | 61.1787 | 122.2315 | 61.9513 | 61.9872 | 61.8917 | 61.9276
6042.0625 | 123.2941 | -61.1618 | 61.9858 | -3.4127 | -10.2147 | -9.9567 | -4.2693 | 3.0165 | -3.4535 | -8.5278 | 61.9904 | 0.29442 | 61.9262 | -0.019364 | 0.043657 | 61.2915 | 0.016878 | 61.0834 | 57.7491 | 50.9472 | 51.2051 | 56.8925 | 64.1783 | 57.7083 | 52.634 | 123.1522 | 61.4562 | 123.088 | 61.1424 | 61.2055 | 122.4533 | 61.1787 | 122.2452 | 61.9467 | 61.9735 | 61.8825 | 61.9093
6043.0781 | 123.4406 | -61.1664 | 61.94 | -3.3944 | -10.2467 | -9.9384 | -4.2555 | 3.131 | -3.4352 | -8.5186 | 61.9949 | 0.28984 | 61.9079 | -0.028522 | 0.048236 | 61.3006 | 0.016878 | 61.0742 | 57.772 | 50.9197 | 51.228 | 56.9108 | 64.2973 | 57.7312 | 52.6478 | 123.1613 | 61.4562 | 123.0743 | 61.1379 | 61.2146 | 122.467 | 61.1833 | 122.2406 | 61.9467 | 61.9781 | 61.8596 | 61.891
6044.0625 | 123.2574 | -61.1847 | 62.0041 | -3.4768 | -10.2559 | -9.975 | -4.3059 | 3.1447 | -3.5085 | -8.5781 | 61.9995 | 0.299 | 61.8987 | -0.023943 | 0.048236 | 61.2869 | 0.007721 | 61.0788 | 57.7079 | 50.9288 | 51.2097 | 56.8788 | 64.3294 | 57.6762 | 52.6066 | 123.1842 | 61.4837 | 123.0834 | 61.1607 | 61.2329 | 122.4716 | 61.1924 | 122.2635 | 61.9513 | 61.9918 | 61.8505 | 61.891
6045.0938 | 123.3856 | -61.1847 | 61.9263 | -3.4722 | -10.2879 | -9.943 | -4.2647 | 3.1767 | -3.5085 | -8.5827 | 61.9858 | 0.299 | 61.8941 | -0.028522 | 0.048236 | 61.2823 | 0.003143 | 61.0788 | 57.7125 | 50.8968 | 51.2417 | 56.92 | 64.3614 | 57.6762 | 52.602 | 123.1705 | 61.4837 | 123.0788 | 61.1562 | 61.2329 | 122.467 | 61.1878 | 122.2635 | 61.9376 | 61.9826 | 61.8459 | 61.891
6046.0625 | 123.3032 | -61.1801 | 61.9675 | -3.376 | -10.1185 | -9.7598 | -4.1228 | 3.2088 | -3.4123 | -8.2164 | 61.9858 | 0.299 | 61.8941 | -0.028522 | 0.048236 | 61.3006 | 0.007721 | 61.0788 | 57.8041 | 51.0616 | 51.4203 | 57.0573 | 64.3889 | 57.7678 | 52.9637 | 123.1659 | 61.4791 | 123.0742 | 61.1516 | 61.2284 | 122.4807 | 61.1878 | 122.2589 | 61.9376 | 61.9781 | 61.8459 | 61.8864
6047.0781 | 123.349 | -61.1847 | 61.908 | -3.3577 | -10.1551 | -9.7965 | -4.0633 | 3.2637 | -3.3986 | -8.1981 | 61.9858 | 0.28984 | 61.8941 | -0.028522 | 0.043657 | 61.3052 | 0.007721 | 61.0697 | 57.827 | 51.0296 | 51.3882 | 57.1214 | 64.4484 | 57.7861 | 52.9866 | 123.1705 | 61.4745 | 123.0788 | 61.1562 | 61.2283 | 122.4899 | 61.1924 | 122.2544 | 61.9421 | 61.9781 | 61.8505 | 61.8864
6048.0625 | 123.2712 | -61.1938 | 61.9766 | -3.4813 | -10.2925 | -9.943 | -4.1457 | 3.2591 | -3.5268 | -8.395 | 61.9904 | 0.29442 | 61.9262 | -0.023943 | 0.057392 | 61.2961 | 0.003143 | 61.0788 | 57.7125 | 50.9014 | 51.2509 | 57.0482 | 64.453 | 57.6671 | 52.7989 | 123.1842 | 61.4883 | 123.12 | 61.1699 | 61.2512 | 122.4899 | 61.197 | 122.2727 | 61.933 | 61.9872 | 61.8688 | 61.923
6049.0938 | 123.381 | -61.1252 | 61.9537 | -3.6324 | -10.4344 | -10.062 | -4.251 | 3.2134 | -3.6687 | -8.4591 | 62.0041 | 0.29442 | 61.9445 | -0.028522 | 0.048236 | 61.2915 | 0.012299 | 61.0697 | 57.4928 | 50.6907 | 51.0632 | 56.8742 | 64.3386 | 57.4565 | 52.6661 | 123.1293 | 61.4196 | 123.0697 | 61.0967 | 61.1734 | 122.4167 | 61.1375 | 122.1948 | 61.9559 | 61.9918 | 61.8963 | 61.9322
6050.0625 | 123.2483 | -61.203 | 61.9949 | -3.6233 | -10.4802 | -10.0575 | -4.251 | 3.1722 | -3.655 | -8.5415 | 61.9904 | 0.28984 | 61.9079 | -0.019364 | 0.048236 | 61.2823 | 0.021456 | 61.0742 | 57.5797 | 50.7228 | 51.1455 | 56.952 | 64.3752 | 57.548 | 52.6615 | 123.1934 | 61.4928 | 123.1109 | 61.1836 | 61.2512 | 122.4853 | 61.2245 | 122.2772 | 61.9421 | 61.9689 | 61.8596 | 61.8864
6051.1094 | 123.3902 | -61.1618 | 61.94 | -3.6004 | -10.4848 | -10.0803 | -4.2922 | 3.0531 | -3.6366 | -8.5094 | 61.9995 | 0.299 | 61.8941 | -0.028522 | 0.052814 | 61.2869 | 0.016878 | 61.0651 | 57.5614 | 50.677 | 51.0815 | 56.8696 | 64.2149 | 57.5252 | 52.6524 | 123.1613 | 61.4608 | 123.0559 | 61.1333 | 61.2146 | 122.4487 | 61.1787 | 122.2269 | 61.9467 | 61.9826 | 61.8413 | 61.8773
6052.0625 | 123.2895 | -61.1389 | 61.9904 | -3.637 | -10.5214 | -10.0987 | -4.3334 | 2.9982 | -3.6687 | -8.5781 | 61.9995 | 0.29442 | 61.9262 | -0.023943 | 0.043657 | 61.2777 | 0.007721 | 61.0742 | 57.5019 | 50.6175 | 51.0403 | 56.8055 | 64.1371 | 57.4702 | 52.5608 | 123.1384 | 61.4333 | 123.0651 | 61.115 | 61.1826 | 122.4167 | 61.1466 | 122.2132 | 61.9559 | 61.9918 | 61.8825 | 61.9185
6053.0938 | 123.4543 | -61.1298 | 61.9629 | -3.4997 | -10.407 | -10.0025 | -4.2739 | 3.0211 | -3.5359 | -8.4911 | 61.9995 | 0.299 | 61.9308 | -0.03768 | 0.048236 | 61.2823 | 0.012299 | 61.0742 | 57.6301 | 50.7228 | 51.1273 | 56.8559 | 64.1509 | 57.5938 | 52.6386 | 123.1293 | 61.4288 | 123.0605 | 61.0921 | 61.178 | 122.4121 | 61.1421 | 122.204 | 61.9513 | 61.9872 | 61.8825 | 61.9185
6054.0625 | 123.2849 | -61.1572 | 62.0041 | -3.5454 | -10.5306 | -10.1399 | -4.3517 | 2.9707 | -3.5771 | -8.8208 | 61.9995 | 0.28984 | 61.9216 | -0.028522 | 0.052814 | 61.2869 | 0.016878 | 61.0697 | 57.6118 | 50.6266 | 51.0174 | 56.8055 | 64.128 | 57.5801 | 52.3365 | 123.1568 | 61.4471 | 123.0788 | 61.1287 | 61.21 | 122.4441 | 61.1741 | 122.2269 | 61.9467 | 61.9826 | 61.8688 | 61.9047
6055.0781 | 123.4039 | -61.1343 | 61.9492 | -3.5729 | -10.5626 | -10.1628 | -4.4021 | 2.8059 | -3.6092 | -8.6697 | 61.9949 | 0.29442 | 61.9079 | -0.033101 | 0.048236 | 61.2732 | 0.012299 | 61.0742 | 57.5614 | 50.5717 | 50.9716 | 56.7323 | 63.9403 | 57.5252 | 52.4647 | 123.1293 | 61.4288 | 123.0422 | 61.1012 | 61.1826 | 122.4075 | 61.1466 | 122.2086 | 61.9467 | 61.9826 | 61.8596 | 61.8956
6056.0625 | 123.4039 | -61.1481 | 61.94 | -3.5958 | -10.5855 | -10.1628 | -4.3654 | 2.783 | -3.6366 | -8.7109 | 62.0041 | 0.28984 | 61.9033 | -0.033101 | 0.043657 | 61.2777 | 0.012299 | 61.0651 | 57.5523 | 50.5625 | 50.9853 | 56.7826 | 63.9311 | 57.5114 | 52.4372 | 123.1522 | 61.4379 | 123.0514 | 61.115 | 61.1917 | 122.4258 | 61.1604 | 122.2132 | 61.9604 | 61.9918 | 61.8596 | 61.891
6057.0781 | 123.317 | -61.1481 | 61.9995 | -3.5683 | -10.5672 | -10.1261 | -4.3425 | 2.87 | -3.6046 | -8.5964 | 62.0041 | 0.29442 | 61.9399 | -0.028522 | 0.048236 | 61.2823 | 0.007721 | 61.0697 | 57.5797 | 50.5808 | 51.0219 | 56.8055 | 64.0181 | 57.5435 | 52.5516 | 123.1522 | 61.4425 | 123.088 | 61.1195 | 61.1963 | 122.4304 | 61.1558 | 122.2177 | 61.9559 | 61.9964 | 61.8917 | 61.9322
6058.0625 | 123.3032 | -61.1526 | 61.9766 | -3.5912 | -10.5352 | -10.0346 | -4.2418 | 2.9295 | -3.6458 | -8.5369 | 62.0041 | 0.29442 | 61.9353 | -0.03768 | 0.048236 | 61.2869 | 0.003143 | 61.0742 | 57.5614 | 50.6175 | 51.1181 | 56.9108 | 64.0822 | 57.5068 | 52.6157 | 123.1568 | 61.4471 | 123.088 | 61.115 | 61.2009 | 122.4395 | 61.1558 | 122.2269 | 61.9559 | 62.001 | 61.8871 | 61.9322
6059.0781 | 123.4085 | -61.1252 | 61.94 | -3.6233 | -10.4619 | -10.0895 | -4.338 | 2.8746 | -3.6641 | -8.688 | 61.9949 | 0.29442 | 61.9079 | -0.03768 | 0.048236 | 61.2869 | 0.012299 | 61.0788 | 57.5019 | 50.6633 | 51.0357 | 56.7872 | 63.9998 | 57.4611 | 52.4372 | 123.1201 | 61.4196 | 123.0331 | 61.0875 | 61.1734 | 122.4121 | 61.1375 | 122.204 | 61.9467 | 61.9826 | 61.8596 | 61.8956
6060.0625 | 123.3307 | -61.1618 | 61.9492 | -3.6278 | -10.4665 | -10.0941 | -4.37 | 2.8792 | -3.6687 | -8.6422 | 61.9949 | 0.29442 | 61.9124 | -0.028522 | 0.039079 | 61.2823 | 0.012299 | 61.0742 | 57.534 | 50.6953 | 51.0677 | 56.7918 | 64.041 | 57.4931 | 52.5196 | 123.1568 | 61.4562 | 123.0743 | 61.1333 | 61.2009 | 122.4441 | 61.1741 | 122.236 | 61.9559 | 61.9826 | 61.8734 | 61.9001
6061.0625 | 123.349 | -61.1481 | 61.9263 | -3.5958 | -10.4161 | -9.9979 | -4.3151 | 2.9387 | -3.6458 | -8.6697 | 61.9995 | 0.29442 | 61.9216 | -0.028522 | 0.048236 | 61.2869 | 0.003143 | 61.0697 | 57.5523 | 50.732 | 51.1501 | 56.833 | 64.0868 | 57.5023 | 52.4784 | 123.1476 | 61.4425 | 123.0697 | 61.1195 | 61.1963 | 122.435 | 61.1512 | 122.2177 | 61.9513 | 61.9964 | 61.8734 | 61.9185
6062.0938 | 123.3078 | -61.171 | 61.9949 | -3.637 | -10.3062 | -10.0391 | -4.3746 | 2.8197 | -3.6733 | -8.569 | 62.0041 | 0.28984 | 61.9399 | -0.028522 | 0.052814 | 61.2915 | 0.016878 | 61.0697 | 57.534 | 50.8647 | 51.1318 | 56.7964 | 63.9906 | 57.4977 | 52.602 | 123.1751 | 61.4608 | 123.1109 | 61.1424 | 61.2238 | 122.4624 | 61.1878 | 122.2406 | 61.9513 | 61.9872 | 61.8871 | 61.923
6063.0625 | 123.3765 | -61.1526 | 61.94 | -3.6736 | -10.3291 | -10.0437 | -4.3654 | 2.8609 | -3.7053 | -8.5964 | 61.9949 | 0.29442 | 61.9216 | -0.028522 | 0.043657 | 61.2777 | 0.007721 | 61.0742 | 57.479 | 50.8235 | 51.1089 | 56.7872 | 64.0135 | 57.4473 | 52.5562 | 123.1476 | 61.4471 | 123.0743 | 61.1241 | 61.1963 | 122.4304 | 61.1604 | 122.2269 | 61.9513 | 61.9872 | 61.8779 | 61.9139
6064.0781 | 123.262 | -61.1984 | 61.9583 | -3.7652 | -10.3886 | -10.1032 | -4.4158 | 2.8426 | -3.8106 | -8.6468 | 61.9995 | 0.29442 | 61.9079 | -0.033101 | 0.052814 | 61.2823 | 0.012299 | 61.0742 | 57.4332 | 50.8098 | 51.0952 | 56.7826 | 64.041 | 57.3878 | 52.5516 | 123.198 | 61.4928 | 123.1063 | 61.1653 | 61.2512 | 122.4807 | 61.2107 | 122.2727 | 61.9467 | 61.9872 | 61.8551 | 61.8956
6065.0625 | 123.2986 | -61.171 | 62.0178 | -3.9026 | -10.4894 | -10.2085 | -4.4799 | 2.8471 | -3.9388 | -8.7612 | 62.0087 | 0.299 | 61.9124 | -0.033101 | 0.043657 | 61.2732 | 0.012299 | 61.0559 | 57.2684 | 50.6816 | 50.9624 | 56.6911 | 64.0181 | 57.2321 | 52.4097 | 123.1796 | 61.47 | 123.0834 | 61.1379 | 61.2146 | 122.4441 | 61.1833 | 122.2269 | 61.965 | 61.9964 | 61.8688 | 61.9001
6066.0625 | 123.3582 | -61.1252 | 61.972 | -4.0628 | -10.7824 | -10.4833 | -4.5806 | 2.6961 | -4.1082 | -9.2832 | 62.0178 | 0.299 | 61.9262 | -0.033101 | 0.057392 | 61.2594 | 0.007721 | 61.0376 | 57.0624 | 50.3428 | 50.6419 | 56.5446 | 63.8212 | 57.017 | 51.842 | 123.143 | 61.4242 | 123.0514 | 61.0921 | 61.1826 | 122.3846 | 61.1329 | 122.1628 | 61.9605 | 62.0101 | 61.8688 | 61.9185
6067.0781 | 123.3398 | -61.1252 | 61.9904 | -3.9804 | -10.755 | -10.5153 | -4.6081 | 2.4443 | -4.0258 | -9.0726 | 62.0224 | 0.28526 | 61.9353 | -0.033101 | 0.052814 | 61.264 | 0.012299 | 61.0468 | 57.1448 | 50.3702 | 50.6099 | 56.5171 | 63.5695 | 57.0994 | 52.0526 | 123.1476 | 61.4104 | 123.0605 | 61.0921 | 61.178 | 122.3892 | 61.1375 | 122.172 | 61.9696 | 62.0101 | 61.8825 | 61.923
6068.0625 | 123.2849 | -61.1938 | 62.0087 | -4.0262 | -10.6954 | -10.4924 | -4.5852 | 2.5038 | -4.0579 | -8.9535 | 62.0224 | 0.29442 | 61.9628 | -0.028522 | 0.039079 | 61.2594 | 0.016878 | 61.0376 | 57.1677 | 50.4984 | 50.7014 | 56.6087 | 63.6976 | 57.136 | 52.2403 | 123.2163 | 61.4883 | 123.1567 | 61.1653 | 61.2329 | 122.4533 | 61.2107 | 122.2315 | 61.9833 | 62.0055 | 61.9237 | 61.9459
6069.0938 | 123.2666 | -61.1526 | 62.027 | -4.0353 | -10.5947 | -10.3825 | -4.5257 | 2.5358 | -4.0808 | -8.9673 | 62.0224 | 0.29442 | 61.9491 | -0.023943 | 0.048236 | 61.264 | 0.012299 | 61.0422 | 57.1173 | 50.558 | 50.7701 | 56.627 | 63.6885 | 57.0719 | 52.1854 | 123.1751 | 61.4471 | 123.1017 | 61.1287 | 61.2009 | 122.4167 | 61.1649 | 122.1948 | 61.9742 | 62.0101 | 61.9008 | 61.9368
6070.0625 | 123.2758 | -61.1618 | 61.9812 | -4.0033 | -10.6725 | -10.3871 | -4.5577 | 2.4214 | -4.0395 | -8.8757 | 62.0178 | 0.29442 | 61.9262 | -0.028522 | 0.057392 | 61.264 | 0.007721 | 61.033 | 57.1585 | 50.4893 | 50.7747 | 56.6041 | 63.5832 | 57.1223 | 52.2861 | 123.1796 | 61.4562 | 123.088 | 61.1333 | 61.2192 | 122.4258 | 61.1695 | 122.1948 | 61.9605 | 62.0101 | 61.8688 | 61.9185
6071.0938 | 123.317 | -61.1389 | 61.9858 | -4.0307 | -10.613 | -10.3459 | -4.5348 | 2.4351 | -4.0624 | -8.8849 | 62.0178 | 0.299 | 61.917 | -0.028522 | 0.039079 | 61.264 | 0.012299 | 61.0559 | 57.1082 | 50.5259 | 50.793 | 56.6041 | 63.574 | 57.0765 | 52.2541 | 123.1568 | 61.4379 | 123.0559 | 61.1104 | 61.178 | 122.4029 | 61.1512 | 122.1948 | 61.9788 | 62.0055 | 61.8779 | 61.9047
6072.0625 | 123.2437 | -61.1893 | 61.9904 | -4.1681 | -10.7137 | -10.3917 | -4.5669 | 2.3664 | -4.1952 | -8.9398 | 62.0178 | 0.29442 | 61.9628 | -0.033101 | 0.052814 | 61.2594 | 0.003143 | 61.0376 | 57.0212 | 50.4755 | 50.7976 | 56.6224 | 63.5557 | 56.9941 | 52.2495 | 123.2071 | 61.4837 | 123.1521 | 61.1562 | 61.2421 | 122.4487 | 61.1924 | 122.2269 | 61.965 | 62.0147 | 61.91 | 61.9597
6073.0781 | 123.3948 | -61.116 | 61.9583 | -4.0262 | -10.7229 | -10.323 | -4.4662 | 2.371 | -4.0533 | -8.9077 | 62.027 | 0.29442 | 61.9537 | -0.028522 | 0.048236 | 61.264 | 0.012299 | 61.0422 | 57.0899 | 50.3931 | 50.793 | 56.6499 | 63.4871 | 57.0627 | 52.2083 | 123.143 | 61.4104 | 123.0697 | 61.0875 | 61.1643 | 122.38 | 61.1283 | 122.1582 | 61.9788 | 62.0147 | 61.9054 | 61.9414
6074.0625 | 123.2391 | -61.171 | 61.9858 | -4.0399 | -10.7687 | -10.3276 | -4.4158 | 2.3619 | -4.0716 | -8.9123 | 62.0224 | 0.29442 | 61.9262 | -0.028522 | 0.039079 | 61.2732 | 0.012299 | 61.0422 | 57.1311 | 50.4023 | 50.8434 | 56.7552 | 63.5328 | 57.0994 | 52.2586 | 123.1934 | 61.4654 | 123.0971 | 61.1424 | 61.21 | 122.4441 | 61.1833 | 122.2131 | 61.9833 | 62.0101 | 61.8871 | 61.9139
6075.0781 | 123.3124 | -61.1755 | 62.0224 | -4.0124 | -10.7229 | -10.2085 | -4.3929 | 2.3664 | -4.0579 | -8.8437 | 62.0133 | 0.29442 | 61.9262 | -0.033101 | 0.048236 | 61.2594 | 0.016878 | 61.0468 | 57.1631 | 50.4526 | 50.967 | 56.7826 | 63.542 | 57.1177 | 52.3319 | 123.1888 | 61.47 | 123.1017 | 61.1424 | 61.2238 | 122.435 | 61.1924 | 122.2223 | 61.965 | 61.9964 | 61.8779 | 61.9093
6076.0625 | 123.3627 | -61.1206 | 61.9583 | -4.0857 | -10.7229 | -10.2406 | -4.4524 | 2.4168 | -4.1403 | -8.8299 | 62.0178 | 0.299 | 61.9399 | -0.028522 | 0.048236 | 61.264 | 0.007721 | 61.0468 | 57.0349 | 50.3977 | 50.88 | 56.6682 | 63.5374 | 56.9803 | 52.2907 | 123.1384 | 61.4196 | 123.0605 | 61.0921 | 61.1688 | 122.3846 | 61.1283 | 122.1674 | 61.9696 | 62.0101 | 61.8917 | 61.9322
6077.0938 | 123.2574 | -61.1801 | 61.9812 | -4.072 | -10.7 | -10.2726 | -4.4524 | 2.5084 | -4.0991 | -8.862 | 62.027 | 0.28984 | 61.9628 | -0.033101 | 0.039079 | 61.264 | 0.003143 | 61.0422 | 57.1082 | 50.4801 | 50.9075 | 56.7277 | 63.6885 | 57.0811 | 52.3181 | 123.2071 | 61.47 | 123.1429 | 61.147 | 61.2192 | 122.4441 | 61.1833 | 122.2223 | 61.9879 | 62.0239 | 61.9237 | 61.9597
6078.0625 | 123.2803 | -61.1435 | 61.9812 | -4.0445 | -10.6908 | -10.2452 | -4.4021 | 2.5679 | -4.0762 | -8.9902 | 62.0178 | 0.299 | 61.9308 | -0.033101 | 0.048236 | 61.264 | 0.012299 | 61.0468 | 57.099 | 50.4526 | 50.8983 | 56.7414 | 63.7114 | 57.0673 | 52.1533 | 123.1613 | 61.4425 | 123.0743 | 61.1104 | 61.1917 | 122.4075 | 61.1558 | 122.1903 | 61.9696 | 62.0055 | 61.8825 | 61.9185
6079.0781 | 123.3536 | -61.1389 | 61.9858 | -3.9575 | -10.5489 | -10.1444 | -4.3105 | 2.5862 | -4.0075 | -8.9764 | 62.0178 | 0.28984 | 61.9124 | -0.033101 | 0.052814 | 61.2732 | 0.016878 | 61.0513 | 57.1814 | 50.59 | 50.9945 | 56.8284 | 63.7251 | 57.1314 | 52.1625 | 123.1568 | 61.4288 | 123.0514 | 61.1058 | 61.1917 | 122.4121 | 61.1558 | 122.1903 | 61.965 | 62.001 | 61.8596 | 61.8956
6080.0625 | 123.2437 | -61.1801 | 61.9583 | -3.93 | -10.4482 | -10.1078 | -4.283 | 2.6549 | -3.9617 | -9.0909 | 62.0087 | 0.29442 | 61.9216 | -0.019364 | 0.048236 | 61.2732 | 0.012299 | 61.0559 | 57.2501 | 50.7319 | 51.0723 | 56.8971 | 63.835 | 57.2184 | 52.0892 | 123.1888 | 61.4745 | 123.1017 | 61.1608 | 61.2284 | 122.4533 | 61.1924 | 122.236 | 61.9604 | 61.9964 | 61.8734 | 61.9093
6081.1094 | 123.317 | -61.1481 | 61.9766 | -4.0262 | -10.4848 | -10.2452 | -4.3609 | 2.5084 | -4.067 | -9.1412 | 62.027 | 0.29442 | 61.9628 | -0.028522 | 0.043657 | 61.2686 | 0.007721 | 61.0422 | 57.1219 | 50.6633 | 50.9029 | 56.7872 | 63.6564 | 57.0811 | 52.0068 | 123.1751 | 61.4425 | 123.1109 | 61.1195 | 61.1917 | 122.4167 | 61.1558 | 122.1903 | 61.9833 | 62.0193 | 61.9192 | 61.9551
6082.0625 | 123.262 | -61.1572 | 61.9949 | -4.0857 | -10.5764 | -10.3276 | -4.4158 | 2.4305 | -4.1311 | -9.1824 | 62.0178 | 0.29442 | 61.9399 | -0.028522 | 0.043657 | 61.264 | 0.007721 | 61.0513 | 57.0715 | 50.5808 | 50.8296 | 56.7414 | 63.5878 | 57.0261 | 51.9748 | 123.1751 | 61.4516 | 123.0971 | 61.1287 | 61.2009 | 122.4212 | 61.1649 | 122.2086 | 61.9742 | 62.0101 | 61.8963 | 61.9322
6083.0938 | 123.3215 | -61.1618 | 62.0132 | -4.1177 | -10.6176 | -10.3642 | -4.425 | 2.4168 | -4.1632 | -9.187 | 62.0178 | 0.299 | 61.9262 | -0.023943 | 0.048236 | 61.264 | 0.007721 | 61.0468 | 57.0441 | 50.5442 | 50.7976 | 56.7369 | 63.5786 | 56.9986 | 51.9748 | 123.1796 | 61.4608 | 123.088 | 61.1379 | 61.21 | 122.4258 | 61.1695 | 122.2086 | 61.9696 | 62.0101 | 61.8779 | 61.9185
6084.0625 | 123.3078 | -61.1389 | 61.9904 | -4.1681 | -10.7046 | -10.4695 | -4.5074 | 2.3161 | -4.2089 | -9.0863 | 62.027 | 0.29442 | 61.9399 | -0.023943 | 0.052814 | 61.2549 | 0.012299 | 61.0422 | 56.9708 | 50.4343 | 50.6694 | 56.6316 | 63.455 | 56.93 | 52.0526 | 123.1659 | 61.4333 | 123.0788 | 61.115 | 61.1917 | 122.3938 | 61.1512 | 122.1811 | 61.9742 | 62.0147 | 61.8871 | 61.9276
6085.0781 | 123.4039 | -61.1252 | 61.9766 | -4.1086 | -10.7275 | -10.4833 | -4.4845 | 2.3024 | -4.1494 | -9.1 | 62.027 | 0.28984 | 61.9582 | -0.028522 | 0.052814 | 61.2594 | 0.007721 | 61.0513 | 57.0166 | 50.3977 | 50.6419 | 56.6407 | 63.4275 | 56.9758 | 52.0252 | 123.1522 | 61.415 | 123.0834 | 61.0967 | 61.178 | 122.3846 | 61.1329 | 122.1765 | 61.9742 | 62.0193 | 61.9054 | 61.9505
6086.0625 | 123.349 | -61.1618 | 61.9583 | -3.9666 | -10.5352 | -10.3139 | -4.3196 | 2.3527 | -4.0121 | -8.894 | 62.0087 | 0.299 | 61.9399 | -0.028522 | 0.043657 | 61.264 | 0.012299 | 61.0513 | 57.1952 | 50.6266 | 50.8479 | 56.8422 | 63.5145 | 57.1497 | 52.2678 | 123.1705 | 61.4608 | 123.1017 | 61.1333 | 61.2055 | 122.4258 | 61.1741 | 122.2131 | 61.965 | 61.9964 | 61.8963 | 61.9276
6087.0938 | 123.3902 | -61.1206 | 61.9583 | -3.9666 | -10.5947 | -10.3139 | -4.3151 | 2.3619 | -3.9983 | -9.1962 | 62.0087 | 0.28984 | 61.917 | -0.023943 | 0.048236 | 61.2686 | 0.007721 | 61.0468 | 57.154 | 50.5259 | 50.8067 | 56.8055 | 63.4825 | 57.1223 | 51.9244 | 123.1293 | 61.4104 | 123.0376 | 61.0967 | 61.1688 | 122.3892 | 61.1283 | 122.1674 | 61.9604 | 62.001 | 61.8688 | 61.9093
6088.0625 | 123.2803 | -61.1298 | 62.0087 | -4.0674 | -10.7458 | -10.4833 | -4.4341 | 2.2612 | -4.1082 | -9.3701 | 62.027 | 0.29442 | 61.9491 | -0.03768 | 0.052814 | 61.2549 | 0.007721 | 61.0376 | 57.0624 | 50.384 | 50.6465 | 56.6957 | 63.3909 | 57.0215 | 51.7596 | 123.1568 | 61.4242 | 123.0788 | 61.0921 | 61.1826 | 122.3846 | 61.1375 | 122.1674 | 61.9742 | 62.0193 | 61.8963 | 61.9414
6089.0938 | 123.2803 | -61.1343 | 62.0087 | -4.1177 | -10.7504 | -10.5153 | -4.4524 | 2.1879 | -4.154 | -9.3701 | 62.0407 | 0.28984 | 61.972 | -0.023943 | 0.052814 | 61.2503 | 0.021456 | 61.0513 | 57.0166 | 50.384 | 50.619 | 56.6819 | 63.3222 | 56.9803 | 51.7642 | 123.1751 | 61.4242 | 123.1063 | 61.1104 | 61.1872 | 122.3846 | 61.1558 | 122.1857 | 61.9879 | 62.0193 | 61.9192 | 61.9505
6090.0625 | 123.3124 | -61.1298 | 62.0132 | -4.191 | -10.8832 | -10.6527 | -4.489 | 2.1467 | -4.2227 | -9.4709 | 62.0316 | 0.29442 | 61.9582 | -0.028522 | 0.043657 | 61.2457 | 0.012299 | 61.0285 | 56.9388 | 50.2466 | 50.4771 | 56.6407 | 63.2765 | 56.9071 | 51.6589 | 123.1613 | 61.4242 | 123.088 | 61.1012 | 61.1734 | 122.3755 | 61.1421 | 122.1582 | 61.9879 | 62.0193 | 61.9146 | 61.9459
6091.1094 | 123.317 | -61.1389 | 62.0407 | -4.1086 | -10.7778 | -10.5336 | -4.4387 | 2.2016 | -4.1311 | -9.3244 | 62.0224 | 0.28526 | 61.9308 | -0.023943 | 0.052814 | 61.2549 | 0.003143 | 61.0376 | 57.0303 | 50.3611 | 50.6053 | 56.7002 | 63.3406 | 57.0078 | 51.8146 | 123.1613 | 61.4242 | 123.0697 | 61.115 | 61.1917 | 122.3938 | 61.1421 | 122.1765 | 61.9696 | 62.0193 | 61.8779 | 61.9276
6092.0625 | 123.2895 | -61.1664 | 61.9812 | -4.0948 | -10.7641 | -10.5062 | -4.4295 | 2.0643 | -4.1357 | -9.306 | 62.027 | 0.29442 | 61.9353 | -0.028522 | 0.048236 | 61.2503 | 0.012299 | 61.0285 | 57.0715 | 50.4023 | 50.6602 | 56.7369 | 63.2307 | 57.0307 | 51.8603 | 123.1934 | 61.4608 | 123.1017 | 61.1379 | 61.2146 | 122.4167 | 61.1787 | 122.1948 | 61.9788 | 62.0147 | 61.8871 | 61.923
6093.0781 | 123.4268 | -61.1023 | 61.9995 | -4.2459 | -10.9244 | -10.6939 | -4.5715 | 1.9636 | -4.2868 | -9.4892 | 62.0407 | 0.299 | 61.9765 | -0.023943 | 0.048236 | 61.2411 | 0.003143 | 61.0239 | 56.8564 | 50.1779 | 50.4084 | 56.5308 | 63.0659 | 56.8155 | 51.6131 | 123.143 | 61.4013 | 123.0788 | 61.0784 | 61.1505 | 122.3434 | 61.1054 | 122.1262 | 61.9925 | 62.0376 | 61.9283 | 61.9734
6094.0625 | 123.3307 | -61.1389 | 62.0316 | -4.1544 | -10.7229 | -10.4421 | -4.4478 | 2.0735 | -4.1952 | -9.274 | 62.0316 | 0.28984 | 61.9353 | -0.028522 | 0.048236 | 61.2549 | 0.007721 | 61.0422 | 56.9846 | 50.416 | 50.6969 | 56.6911 | 63.2124 | 56.9437 | 51.8649 | 123.1705 | 61.4288 | 123.0743 | 61.1104 | 61.1872 | 122.3938 | 61.1466 | 122.1811 | 61.9833 | 62.0239 | 61.8871 | 61.9276
6095.0781 | 123.4039 | -61.1252 | 61.9675 | -4.0811 | -10.5397 | -10.2452 | -4.3609 | 2.1513 | -4.1174 | -9.1687 | 62.0224 | 0.28984 | 61.9582 | -0.033101 | 0.048236 | 61.2594 | 0.012299 | 61.0468 | 57.0441 | 50.5854 | 50.88 | 56.7643 | 63.2765 | 57.0078 | 51.9565 | 123.1476 | 61.415 | 123.0834 | 61.0921 | 61.1734 | 122.3846 | 61.1375 | 122.172 | 61.9742 | 62.0101 | 61.91 | 61.9459
6096.0625 | 123.2574 | -61.1343 | 61.9858 | -4.1406 | -10.7687 | -10.3917 | -4.4158 | 2.1604 | -4.1677 | -9.3106 | 62.0224 | 0.28984 | 61.9308 | -0.033101 | 0.052814 | 61.2549 | 0.007721 | 61.033 | 56.9937 | 50.3656 | 50.7426 | 56.7185 | 63.2948 | 56.9666 | 51.8237 | 123.1568 | 61.4242 | 123.0651 | 61.1012 | 61.1872 | 122.3892 | 61.1421 | 122.1674 | 61.9696 | 62.0147 | 61.8779 | 61.923
6097.0938 | 123.381 | -61.1114 | 61.9949 | -4.2368 | -10.8786 | -10.529 | -4.4707 | 2.0643 | -4.2822 | -9.4159 | 62.027 | 0.29442 | 61.9445 | -0.033101 | 0.052814 | 61.2457 | 0.012299 | 61.0239 | 56.8747 | 50.2329 | 50.5824 | 56.6407 | 63.1758 | 56.8293 | 51.6955 | 123.1384 | 61.4059 | 123.0559 | 61.0783 | 61.1643 | 122.3571 | 61.1237 | 122.1353 | 61.9742 | 62.0147 | 61.8917 | 61.9322
6098.0625 | 123.3032 | -61.1389 | 62.0224 | -4.1361 | -10.7046 | -10.3322 | -4.3563 | 2.0689 | -4.1723 | -9.0314 | 62.027 | 0.28984 | 61.9628 | -0.028522 | 0.048236 | 61.2594 | 0.007721 | 61.0422 | 57.0029 | 50.4343 | 50.8067 | 56.7826 | 63.2078 | 56.9666 | 52.1076 | 123.1659 | 61.4288 | 123.1017 | 61.1104 | 61.1872 | 122.3983 | 61.1466 | 122.1811 | 61.9788 | 62.0193 | 61.9146 | 61.9551
6099.0781 | 123.3215 | -61.1572 | 61.9583 | -4.0536 | -10.5855 | -10.1536 | -4.2372 | 2.0963 | -4.0899 | -9.0268 | 62.0178 | 0.28526 | 61.917 | -0.028522 | 0.043657 | 61.2686 | 0.007721 | 61.0376 | 57.1036 | 50.5717 | 51.0036 | 56.92 | 63.2536 | 57.0673 | 52.1304 | 123.1751 | 61.4425 | 123.0743 | 61.1287 | 61.2009 | 122.4258 | 61.1649 | 122.1948 | 61.9742 | 62.0101 | 61.8734 | 61.9093
6100.0625 | 123.2803 | -61.1572 | 61.9995 | -4.1681 | -10.6359 | -10.2406 | -4.3288 | 1.9727 | -4.1998 | -9.0039 | 62.0224 | 0.299 | 61.9537 | -0.019364 | 0.039079 | 61.2549 | 0.012299 | 61.0422 | 56.9891 | 50.5213 | 50.9166 | 56.8284 | 63.13 | 56.9574 | 52.1533 | 123.1796 | 61.4562 | 123.1109 | 61.1379 | 61.1963 | 122.4121 | 61.1695 | 122.1994 | 61.9833 | 62.0101 | 61.9146 | 61.9414
6101.1094 | 123.3261 | -61.1618 | 61.9629 | -4.2414 | -10.6863 | -10.3367 | -4.3929 | 1.8674 | -4.273 | -9.0863 | 62.027 | 0.28984 | 61.9491 | -0.03768 | 0.052814 | 61.2549 | 0.012299 | 61.0376 | 56.9205 | 50.4755 | 50.8251 | 56.7689 | 63.0293 | 56.8888 | 52.0755 | 123.1888 | 61.4516 | 123.1109 | 61.1241 | 61.2146 | 122.4167 | 61.1741 | 122.1994 | 61.9742 | 62.0147 | 61.8963 | 61.9368
6102.0625 | 123.3215 | -61.1206 | 61.9949 | -4.3009 | -10.7275 | -10.4237 | -4.457 | 1.8674 | -4.3371 | -9.155 | 62.0316 | 0.28984 | 61.9262 | -0.028522 | 0.052814 | 61.2594 | 0.012299 | 61.0376 | 56.8197 | 50.3931 | 50.6969 | 56.6636 | 62.9881 | 56.7835 | 51.9656 | 123.1522 | 61.4104 | 123.0468 | 61.0921 | 61.1734 | 122.38 | 61.1329 | 122.1582 | 61.9788 | 62.0193 | 61.8734 | 61.9139
6103.0781 | 123.3719 | -61.1298 | 61.9583 | -4.2276 | -10.7504 | -10.3871 | -4.3975 | 1.7713 | -4.2685 | -9.3564 | 62.0362 | 0.29442 | 61.9582 | -0.033101 | 0.048236 | 61.2549 | 0.012299 | 61.0193 | 56.9021 | 50.3794 | 50.7426 | 56.7323 | 62.9011 | 56.8613 | 51.7734 | 123.1659 | 61.4242 | 123.088 | 61.0967 | 61.178 | 122.3846 | 61.1421 | 122.1491 | 61.9879 | 62.0239 | 61.91 | 61.9459
6104.0625 | 123.3261 | -61.1069 | 62.0087 | -4.2597 | -10.7687 | -10.4512 | -4.4433 | 1.6477 | -4.3051 | -9.3976 | 62.0316 | 0.28984 | 61.9353 | -0.028522 | 0.057392 | 61.2457 | 0.012299 | 61.033 | 56.8472 | 50.3382 | 50.6557 | 56.6636 | 62.7546 | 56.8018 | 51.7093 | 123.1385 | 61.3967 | 123.0422 | 61.0784 | 61.1643 | 122.3526 | 61.1192 | 122.1399 | 61.9742 | 62.0193 | 61.8779 | 61.923
6105.0781 | 123.4451 | -61.1481 | 61.9812 | -4.3329 | -10.7595 | -10.4878 | -4.489 | 1.6798 | -4.3783 | -9.2603 | 62.0362 | 0.28984 | 61.9445 | -0.028522 | 0.048236 | 61.2457 | 0.012299 | 61.0239 | 56.8152 | 50.3885 | 50.6602 | 56.659 | 62.8278 | 56.7697 | 51.8878 | 123.1842 | 61.4379 | 123.0926 | 61.1195 | 61.1963 | 122.3938 | 61.1604 | 122.1719 | 61.9879 | 62.0239 | 61.8963 | 61.9322
6106.0625 | 123.2849 | -61.1206 | 62.027 | -4.3512 | -10.8236 | -10.5336 | -4.4707 | 1.7072 | -4.3829 | -9.2786 | 62.0362 | 0.29442 | 61.9765 | -0.023943 | 0.043657 | 61.2503 | 0.012299 | 61.0285 | 56.7694 | 50.297 | 50.587 | 56.6499 | 62.8278 | 56.7377 | 51.842 | 123.1568 | 61.415 | 123.0971 | 61.0967 | 61.1643 | 122.3709 | 61.1329 | 122.1491 | 61.9925 | 62.0239 | 61.9329 | 61.9642
6107.0781 | 123.3948 | -61.1298 | 61.9217 | -4.397 | -10.874 | -10.584 | -4.5257 | 1.6798 | -4.447 | -9.3152 | 62.0362 | 0.29442 | 61.9308 | -0.028522 | 0.048236 | 61.2457 | 0.003143 | 61.0239 | 56.7327 | 50.2558 | 50.5458 | 56.6041 | 62.8095 | 56.6827 | 51.8146 | 123.1659 | 61.4242 | 123.0605 | 61.1012 | 61.178 | 122.3755 | 61.1329 | 122.1536 | 61.9879 | 62.033 | 61.8825 | 61.9276
6108.0625 | 123.436 | -61.1023 | 62.0087 | -4.4703 | -11.0251 | -10.7442 | -4.6722 | 1.5745 | -4.5065 | -9.4617 | 62.0453 | 0.28526 | 61.9674 | -0.033101 | 0.052814 | 61.2274 | 0.012299 | 61.0101 | 56.632 | 50.0772 | 50.3581 | 56.4301 | 62.6768 | 56.5958 | 51.6406 | 123.1476 | 61.3876 | 123.0697 | 61.0692 | 61.1551 | 122.3297 | 61.1146 | 122.1124 | 61.9925 | 62.033 | 61.9146 | 61.9551
6109.0938 | 123.381 | -61.1114 | 62.0041 | -4.4611 | -10.9381 | -10.671 | -4.6813 | 1.6111 | -4.4928 | -9.393 | 62.0499 | 0.299 | 61.9582 | -0.03768 | 0.048236 | 61.2365 | 0.007721 | 61.0193 | 56.6503 | 50.1733 | 50.4405 | 56.4301 | 62.7225 | 56.6186 | 51.7184 | 123.1613 | 61.4104 | 123.0697 | 61.0738 | 61.1597 | 122.348 | 61.1192 | 122.1307 | 62.0017 | 62.0422 | 61.91 | 61.9505
6110.0625 | 123.4085 | -61.1114 | 61.9858 | -4.3787 | -10.7641 | -10.5382 | -4.6172 | 1.6843 | -4.415 | -9.2832 | 62.0362 | 0.28984 | 61.9308 | -0.023943 | 0.052814 | 61.2503 | 0.007721 | 61.0239 | 56.7327 | 50.3473 | 50.5732 | 56.4942 | 62.7958 | 56.6965 | 51.8283 | 123.1476 | 61.4013 | 123.0422 | 61.0875 | 61.1643 | 122.3617 | 61.1192 | 122.1353 | 61.9833 | 62.0284 | 61.8779 | 61.923
6111.0938 | 123.3078 | -61.1618 | 61.9949 | -4.4382 | -10.8603 | -10.6527 | -4.7134 | 1.5516 | -4.4882 | -9.3473 | 62.0499 | 0.28984 | 61.9628 | -0.028522 | 0.043657 | 61.2365 | 0.007721 | 61.0147 | 56.7236 | 50.3015 | 50.5091 | 56.4484 | 62.7134 | 56.6736 | 51.8146 | 123.2117 | 61.4516 | 123.1246 | 61.1333 | 61.2055 | 122.3983 | 61.1695 | 122.1765 | 62.0062 | 62.0422 | 61.9192 | 61.9551
6112.0625 | 123.381 | -61.116 | 61.9766 | -4.4794 | -10.9381 | -10.703 | -4.7271 | 1.5195 | -4.5157 | -9.4846 | 62.0499 | 0.29442 | 61.9537 | -0.028522 | 0.048236 | 61.232 | 0.012299 | 61.0193 | 56.6366 | 50.1779 | 50.413 | 56.3889 | 62.6356 | 56.6003 | 51.6314 | 123.1659 | 61.4104 | 123.0697 | 61.0875 | 61.1643 | 122.348 | 61.1283 | 122.1353 | 62.0017 | 62.0376 | 61.9054 | 61.9414
6113.0781 | 123.3719 | -61.116 | 61.972 | -4.4703 | -10.9061 | -10.6069 | -4.6447 | 1.6477 | -4.5157 | -9.5945 | 62.0316 | 0.28984 | 61.9491 | -0.023943 | 0.048236 | 61.2411 | 0.012299 | 61.0147 | 56.6458 | 50.21 | 50.5091 | 56.4713 | 62.7637 | 56.6003 | 51.5216 | 123.1476 | 61.4059 | 123.0651 | 61.0921 | 61.1643 | 122.3571 | 61.1283 | 122.1307 | 61.9833 | 62.0193 | 61.9008 | 61.9368
6114.0625 | 123.436 | -61.1069 | 61.9995 | -4.4748 | -10.8191 | -10.5107 | -4.6081 | 1.7301 | -4.5203 | -9.5121 | 62.0453 | 0.29442 | 61.972 | -0.023943 | 0.052814 | 61.2365 | 0.012299 | 61.0193 | 56.632 | 50.2878 | 50.5961 | 56.4988 | 62.837 | 56.5866 | 51.5948 | 123.1522 | 61.4013 | 123.0788 | 61.0829 | 61.1597 | 122.3434 | 61.1192 | 122.1262 | 61.9925 | 62.033 | 61.9192 | 61.9597
6115.0781 | 123.2941 | -61.1526 | 61.9995 | -4.4245 | -10.787 | -10.4833 | -4.6081 | 1.6477 | -4.4608 | -9.5029 | 62.0362 | 0.29442 | 61.9399 | -0.028522 | 0.043657 | 61.2411 | 0.012299 | 61.0147 | 56.7282 | 50.3656 | 50.6694 | 56.5446 | 62.8004 | 56.6919 | 51.6497 | 123.1888 | 61.4471 | 123.0926 | 61.1241 | 61.1963 | 122.3938 | 61.1649 | 122.1674 | 61.9925 | 62.0239 | 61.8963 | 61.9276
6116.0625 | 123.2895 | -61.1481 | 62.0407 | -4.3604 | -10.7412 | -10.4283 | -4.576 | 1.6477 | -4.3967 | -9.4205 | 62.0407 | 0.29442 | 61.9491 | -0.033101 | 0.048236 | 61.2503 | 0.007721 | 61.0285 | 56.7877 | 50.4069 | 50.7198 | 56.572 | 62.7958 | 56.7514 | 51.7276 | 123.1888 | 61.4425 | 123.0971 | 61.115 | 61.1963 | 122.3983 | 61.1558 | 122.1765 | 61.9925 | 62.033 | 61.9008 | 61.9414
6117.0781 | 123.4131 | -61.1389 | 61.9537 | -4.2368 | -10.6267 | -10.3047 | -4.4387 | 1.6157 | -4.2639 | -9.3198 | 62.0362 | 0.28984 | 61.9674 | -0.033101 | 0.043657 | 61.2503 | 0.007721 | 61.0239 | 56.9021 | 50.5122 | 50.8342 | 56.7002 | 62.7546 | 56.875 | 51.8191 | 123.1751 | 61.4288 | 123.1063 | 61.1058 | 61.1826 | 122.3892 | 61.1466 | 122.1628 | 61.9925 | 62.0284 | 61.9237 | 61.9597
6118.0625 | 123.4131 | -61.116 | 61.9583 | -4.2505 | -10.6313 | -10.291 | -4.4066 | 1.6385 | -4.2822 | -9.393 | 62.027 | 0.28984 | 61.9353 | -0.028522 | 0.043657 | 61.2549 | 0.016878 | 61.0376 | 56.8655 | 50.4847 | 50.8251 | 56.7094 | 62.7546 | 56.8338 | 51.723 | 123.143 | 61.4059 | 123.0514 | 61.0875 | 61.1597 | 122.3709 | 61.1329 | 122.1536 | 61.9833 | 62.0101 | 61.8917 | 61.9185
6119.0781 | 123.349 | -61.1343 | 61.9446 | -4.2505 | -10.5947 | -10.2726 | -4.4478 | 1.6477 | -4.2914 | -9.3381 | 62.0362 | 0.29442 | 61.9445 | -0.033101 | 0.048236 | 61.2503 | 0.012299 | 61.0285 | 56.8838 | 50.5396 | 50.8617 | 56.6865 | 62.782 | 56.843 | 51.7962 | 123.1705 | 61.4288 | 123.0788 | 61.1012 | 61.1826 | 122.3846 | 61.1466 | 122.1628 | 61.9879 | 62.0239 | 61.8963 | 61.9322
6120.0625 | 123.4039 | -61.1114 | 61.972 | -4.3283 | -10.6908 | -10.4237 | -4.544 | 1.4692 | -4.3738 | -9.3427 | 62.0362 | 0.299 | 61.9674 | -0.028522 | 0.048236 | 61.2457 | 0.012299 | 61.0239 | 56.7831 | 50.4206 | 50.6877 | 56.5675 | 62.5806 | 56.7377 | 51.7688 | 123.1476 | 61.4104 | 123.0788 | 61.0829 | 61.1597 | 122.3571 | 61.1237 | 122.1353 | 61.9879 | 62.0239 | 61.9191 | 61.9551
6121.0938 | 123.317 | -61.1618 | 61.9812 | -4.2505 | -10.494 | -10.2314 | -4.4616 | 1.5928 | -4.2914 | -9.1916 | 62.027 | 0.299 | 61.9353 | -0.028522 | 0.043657 | 61.2549 | 0.007721 | 61.0285 | 56.9113 | 50.6678 | 50.9304 | 56.7002 | 62.7546 | 56.8704 | 51.9702 | 123.1888 | 61.4608 | 123.0971 | 61.1333 | 61.2055 | 122.4167 | 61.1695 | 122.1903 | 61.9833 | 62.0193 | 61.8917 | 61.9276
6122.0625 | 123.3902 | -61.1206 | 61.9904 | -4.2597 | -10.5581 | -10.236 | -4.4433 | 1.5928 | -4.2959 | -9.3289 | 62.0224 | 0.29442 | 61.9674 | -0.033101 | 0.048236 | 61.2503 | 0.007721 | 61.0285 | 56.8609 | 50.5625 | 50.8846 | 56.6773 | 62.7134 | 56.8247 | 51.7917 | 123.143 | 61.415 | 123.088 | 61.0875 | 61.1688 | 122.3709 | 61.1283 | 122.1491 | 61.9742 | 62.0147 | 61.9191 | 61.9597
6123.0781 | 123.2758 | -61.1298 | 61.9858 | -4.3512 | -10.7 | -10.3871 | -4.5348 | 1.5607 | -4.3829 | -9.4342 | 62.0407 | 0.28526 | 61.9537 | -0.033101 | 0.048236 | 61.2411 | 0.007721 | 61.0193 | 56.7785 | 50.4298 | 50.7426 | 56.5949 | 62.6905 | 56.7468 | 51.6955 | 123.1705 | 61.415 | 123.0834 | 61.0967 | 61.178 | 122.3709 | 61.1375 | 122.1491 | 61.9925 | 62.033 | 61.9054 | 61.9459
6124.0625 | 123.3902 | -61.1343 | 61.9858 | -4.191 | -10.5581 | -10.2223 | -4.4341 | 1.6431 | -4.2181 | -9.3335 | 62.0224 | 0.299 | 61.9262 | -0.033101 | 0.043657 | 61.2549 | 0.012299 | 61.0285 | 56.9433 | 50.5763 | 50.9121 | 56.7002 | 62.7775 | 56.9162 | 51.8008 | 123.1568 | 61.4333 | 123.0605 | 61.1012 | 61.178 | 122.3892 | 61.1466 | 122.1628 | 61.9788 | 62.0101 | 61.8825 | 61.9139
6125.0938 | 123.3444 | -61.1389 | 61.9125 | -4.1452 | -10.4573 | -10.1032 | -4.4021 | 1.666 | -4.1861 | -9.2832 | 62.027 | 0.28984 | 61.9628 | -0.03768 | 0.052814 | 61.2594 | 0.007721 | 61.0239 | 56.9937 | 50.6816 | 51.0357 | 56.7369 | 62.8049 | 56.9529 | 51.8558 | 123.1659 | 61.4288 | 123.1017 | 61.1012 | 61.1917 | 122.3983 | 61.1466 | 122.1628 | 61.9742 | 62.0193 | 61.91 | 61.9551
6126.0625 | 123.2849 | -61.1572 | 61.9812 | -4.0491 | -10.2879 | -9.9109 | -4.3059 | 1.6981 | -4.0853 | -9.1321 | 62.0178 | 0.28984 | 61.9353 | -0.028522 | 0.039079 | 61.2549 | 0.016878 | 61.0422 | 57.1082 | 50.8693 | 51.2463 | 56.8513 | 62.8553 | 57.0719 | 52.0251 | 123.1751 | 61.4471 | 123.0926 | 61.1287 | 61.1963 | 122.4121 | 61.1741 | 122.1994 | 61.9788 | 62.001 | 61.8963 | 61.9185
6127.0938 | 123.3719 | -61.1298 | 61.972 | -4.1132 | -10.3337 | -9.9659 | -4.3654 | 1.6157 | -4.154 | -9.2008 | 62.0178 | 0.28984 | 61.9262 | -0.033101 | 0.043657 | 61.2549 | 0.003143 | 61.0376 | 57.0166 | 50.7961 | 51.1639 | 56.7643 | 62.7454 | 56.9758 | 51.929 | 123.1476 | 61.4196 | 123.0559 | 61.0967 | 61.1734 | 122.3846 | 61.1329 | 122.1674 | 61.9742 | 62.0147 | 61.8825 | 61.923
6128.0625 | 123.436 | -61.0931 | 61.9949 | -4.1589 | -10.3978 | -9.9979 | -4.3975 | 1.6019 | -4.1952 | -9.2877 | 62.027 | 0.29442 | 61.9628 | -0.019364 | 0.052814 | 61.2549 | 0.012299 | 61.0422 | 56.9342 | 50.6953 | 51.0952 | 56.6957 | 62.6951 | 56.8979 | 51.8054 | 123.1201 | 61.3876 | 123.0559 | 61.0738 | 61.146 | 122.348 | 61.1054 | 122.1353 | 61.9742 | 62.0147 | 61.91 | 61.9505
6129.0938 | 123.3627 | -61.0931 | 61.9766 | -4.2551 | -10.3978 | -9.9934 | -4.425 | 1.5058 | -4.2959 | -9.3335 | 62.027 | 0.29442 | 61.9308 | -0.033101 | 0.043657 | 61.2549 | 0.012299 | 61.033 | 56.8381 | 50.6953 | 51.0998 | 56.6682 | 62.5989 | 56.7972 | 51.7596 | 123.1201 | 61.3876 | 123.0239 | 61.06 | 61.1368 | 122.348 | 61.1054 | 122.1262 | 61.9833 | 62.0147 | 61.8871 | 61.9185
6130.0625 | 123.3444 | -61.1252 | 61.9949 | -4.3421 | -10.4436 | -10.0346 | -4.4387 | 1.547 | -4.3783 | -9.3656 | 62.0407 | 0.28984 | 61.9353 | -0.028522 | 0.052814 | 61.2503 | 0.012299 | 61.033 | 56.7831 | 50.6816 | 51.0906 | 56.6865 | 62.6722 | 56.7468 | 51.7596 | 123.1659 | 61.415 | 123.0605 | 61.0967 | 61.178 | 122.3755 | 61.1375 | 122.1582 | 61.9879 | 62.0284 | 61.8825 | 61.923
6131.1094 | 123.3856 | -61.1389 | 61.9766 | -4.3558 | -10.4482 | -10.0162 | -4.4158 | 1.5973 | -4.3967 | -9.3885 | 62.0316 | 0.29442 | 61.9628 | -0.028522 | 0.052814 | 61.2457 | 0.012299 | 61.0239 | 56.7831 | 50.6907 | 51.1227 | 56.7231 | 62.7363 | 56.7423 | 51.7505 | 123.1705 | 61.4333 | 123.1017 | 61.1104 | 61.1917 | 122.3846 | 61.1512 | 122.1628 | 61.9788 | 62.0193 | 61.91 | 61.9505
6132.0625 | 123.3582 | -61.1069 | 62.0224 | -4.3055 | -10.3886 | -9.9521 | -4.3654 | 1.6981 | -4.3509 | -9.3381 | 62.0224 | 0.28526 | 61.9308 | -0.023943 | 0.048236 | 61.2549 | 0.007721 | 61.0422 | 56.8014 | 50.7182 | 51.1547 | 56.7414 | 62.8049 | 56.756 | 51.7688 | 123.1293 | 61.3921 | 123.0376 | 61.0829 | 61.1551 | 122.3617 | 61.1146 | 122.1491 | 61.9742 | 62.0147 | 61.8825 | 61.923
6133.0938 | 123.4131 | -61.1389 | 61.972 | -4.2551 | -10.3658 | -9.9109 | -4.2922 | 1.6523 | -4.2959 | -9.2694 | 62.0178 | 0.28984 | 61.9353 | -0.023943 | 0.043657 | 61.2594 | 0.007721 | 61.0422 | 56.8838 | 50.7732 | 51.228 | 56.8467 | 62.7912 | 56.843 | 51.8695 | 123.1568 | 61.4288 | 123.0743 | 61.115 | 61.1826 | 122.3983 | 61.1466 | 122.1811 | 61.9742 | 62.0101 | 61.8917 | 61.9276
6134.0625 | 123.3307 | -61.1114 | 61.9812 | -4.2688 | -10.4299 | -9.943 | -4.3242 | 1.5607 | -4.3005 | -9.3518 | 62.0224 | 0.29442 | 61.9628 | -0.028522 | 0.048236 | 61.2503 | 0.007721 | 61.0468 | 56.8426 | 50.6816 | 51.1685 | 56.7872 | 62.6722 | 56.8109 | 51.7596 | 123.1339 | 61.4059 | 123.0743 | 61.0829 | 61.1597 | 122.3617 | 61.1192 | 122.1582 | 61.9742 | 62.0147 | 61.9146 | 61.9551
6135.0781 | 123.3627 | -61.1252 | 61.9812 | -4.2185 | -10.3062 | -9.8285 | -4.3151 | 1.4875 | -4.2547 | -9.2465 | 62.0178 | 0.28984 | 61.9353 | -0.028522 | 0.039079 | 61.2549 | 0.016878 | 61.0376 | 56.9067 | 50.819 | 51.2967 | 56.8101 | 62.6127 | 56.8705 | 51.8787 | 123.143 | 61.415 | 123.0605 | 61.0967 | 61.1643 | 122.38 | 61.1421 | 122.1628 | 61.9788 | 62.001 | 61.8963 | 61.9185
6136.0625 | 123.2849 | -61.1618 | 61.9858 | -4.104 | -10.0361 | -9.5447 | -4.2006 | 1.634 | -4.1403 | -9.0314 | 62.0224 | 0.29442 | 61.9353 | -0.028522 | 0.048236 | 61.2777 | 0.012299 | 61.0513 | 57.0578 | 51.1257 | 51.6172 | 56.9612 | 62.7958 | 57.0215 | 52.1304 | 123.1842 | 61.4562 | 123.0971 | 61.1333 | 61.21 | 122.4395 | 61.1741 | 122.2131 | 61.9742 | 62.0101 | 61.8871 | 61.923
6137.0781 | 123.3307 | -61.1206 | 61.9492 | -4.017 | -9.9353 | -9.4073 | -4.0816 | 1.7438 | -4.0579 | -8.9718 | 62.0041 | 0.29442 | 61.9399 | -0.033101 | 0.048236 | 61.2777 | 0.003143 | 61.0559 | 57.1036 | 51.1853 | 51.7133 | 57.039 | 62.8644 | 57.0627 | 52.1488 | 123.1247 | 61.415 | 123.0605 | 61.0875 | 61.1688 | 122.3983 | 61.1237 | 122.1765 | 61.9559 | 62.001 | 61.8917 | 61.9368
6138.0625 | 123.3719 | -61.1252 | 61.9766 | -4.0948 | -10.0223 | -9.508 | -4.1182 | 1.753 | -4.1265 | -9.0726 | 62.0087 | 0.29442 | 61.9124 | -0.028522 | 0.048236 | 61.2686 | 0.012299 | 61.0559 | 57.0303 | 51.1028 | 51.6172 | 57.007 | 62.8782 | 56.9986 | 52.0526 | 123.1339 | 61.4196 | 123.0376 | 61.0967 | 61.1734 | 122.3938 | 61.1375 | 122.1811 | 61.9604 | 61.9964 | 61.8642 | 61.9001
6139.0781 | 123.3719 | -61.171 | 61.9217 | -4.1223 | -9.9674 | -9.4485 | -4.0953 | 1.7942 | -4.1632 | -9.0634 | 62.0087 | 0.29442 | 61.9353 | -0.03768 | 0.048236 | 61.2686 | 0.007721 | 61.0468 | 57.0486 | 51.2036 | 51.7225 | 57.0757 | 62.9652 | 57.0078 | 52.1076 | 123.1796 | 61.4654 | 123.1063 | 61.1333 | 61.2192 | 122.4395 | 61.1787 | 122.2177 | 61.9604 | 62.001 | 61.8871 | 61.9276
6140.0625 | 123.3719 | -61.1252 | 61.9812 | -3.9666 | -9.6927 | -9.1738 | -3.9579 | 1.8262 | -3.9892 | -8.8345 | 61.9949 | 0.28984 | 61.9216 | -0.033101 | 0.052814 | 61.2777 | 0.012299 | 61.0697 | 57.1585 | 51.4325 | 51.9514 | 57.1672 | 62.9514 | 57.136 | 52.2907 | 123.1201 | 61.415 | 123.0468 | 61.0921 | 61.178 | 122.4029 | 61.1375 | 122.1948 | 61.9421 | 61.9826 | 61.8688 | 61.9093
6141.1094 | 123.381 | -61.1618 | 61.94 | -3.8659 | -9.6148 | -9.0959 | -3.9122 | 1.8034 | -3.9022 | -8.807 | 61.9904 | 0.28984 | 61.8987 | -0.028522 | 0.048236 | 61.2869 | 0.012299 | 61.0788 | 57.2959 | 51.547 | 52.0659 | 57.2496 | 62.9652 | 57.2596 | 52.3548 | 123.1522 | 61.4516 | 123.0605 | 61.1333 | 61.21 | 122.4487 | 61.1741 | 122.2406 | 61.9421 | 61.9781 | 61.8505 | 61.8864
6142.0625 | 123.3124 | -61.1343 | 61.9812 | -3.9666 | -9.6972 | -9.1555 | -3.99 | 1.7026 | -3.9938 | -8.894 | 61.9995 | 0.28984 | 61.9353 | -0.028522 | 0.048236 | 61.2823 | 0.021456 | 61.0788 | 57.1677 | 51.4371 | 51.9789 | 57.1443 | 62.837 | 57.1406 | 52.2403 | 123.1339 | 61.4242 | 123.0697 | 61.1058 | 61.1826 | 122.4167 | 61.1558 | 122.2132 | 61.9513 | 61.9781 | 61.8871 | 61.9139
6143.0781 | 123.381 | -61.1435 | 61.94 | -4.0262 | -9.7293 | -9.215 | -4.0129 | 1.7026 | -4.0624 | -9.0176 | 62.0041 | 0.299 | 61.9262 | -0.028522 | 0.048236 | 61.2777 | 0.012299 | 61.0697 | 57.1173 | 51.4142 | 51.9285 | 57.1306 | 62.8461 | 57.0811 | 52.1259 | 123.1476 | 61.4425 | 123.0697 | 61.115 | 61.1917 | 122.4212 | 61.1558 | 122.2132 | 61.9559 | 61.9918 | 61.8779 | 61.9139
6144.0625 | 123.3582 | -61.1252 | 61.9583 | -4.0536 | -9.7568 | -9.2837 | -4.0633 | 1.6294 | -4.0945 | -9.0176 | 62.0041 | 0.28984 | 61.917 | -0.019364 | 0.048236 | 61.2732 | 0.012299 | 61.0697 | 57.0715 | 51.3684 | 51.8415 | 57.0619 | 62.7546 | 57.0307 | 52.1076 | 123.1293 | 61.415 | 123.0422 | 61.1058 | 61.1734 | 122.3983 | 61.1375 | 122.1948 | 61.9559 | 61.9918 | 61.8688 | 61.9047
6145.0781 | 123.3673 | -61.1801 | 61.908 | -3.9163 | -9.5782 | -9.0456 | -3.9351 | 1.6752 | -3.9617 | -8.8162 | 62.0041 | 0.29442 | 61.9308 | -0.033101 | 0.048236 | 61.2869 | 0.007721 | 61.0742 | 57.2638 | 51.6019 | 52.1345 | 57.2451 | 62.8553 | 57.2184 | 52.3639 | 123.1842 | 61.4745 | 123.1109 | 61.147 | 61.2284 | 122.467 | 61.1878 | 122.2544 | 61.9559 | 61.9964 | 61.8825 | 61.923
6146.0625 | 123.3398 | -61.1526 | 61.9583 | -3.9529 | -9.6698 | -9.1097 | -3.9671 | 1.6065 | -3.9938 | -8.8665 | 61.9949 | 0.299 | 61.9079 | -0.028522 | 0.048236 | 61.2823 | 0.007721 | 61.0834 | 57.1997 | 51.4829 | 52.043 | 57.1855 | 62.7592 | 57.1589 | 52.2861 | 123.1476 | 61.4516 | 123.0605 | 61.1241 | 61.2009 | 122.435 | 61.1604 | 122.236 | 61.9467 | 61.9872 | 61.8596 | 61.9001
6147.0938 | 123.3582 | -61.1389 | 61.972 | -3.9438 | -9.6194 | -9.0914 | -3.9396 | 1.5928 | -3.9663 | -8.8482 | 62.0041 | 0.28984 | 61.9124 | -0.019364 | 0.052814 | 61.2777 | 0.007721 | 61.0742 | 57.1952 | 51.5195 | 52.0475 | 57.1993 | 62.7317 | 57.1726 | 52.2907 | 123.143 | 61.4288 | 123.0514 | 61.1196 | 61.1917 | 122.4167 | 61.1466 | 122.2132 | 61.9513 | 61.9964 | 61.8596 | 61.9047
6148.0625 | 123.3856 | -61.1618 | 61.9171 | -3.9071 | -9.6469 | -9.041 | -3.9259 | 1.4783 | -3.948 | -8.8299 | 62.0087 | 0.29442 | 61.9262 | -0.028522 | 0.048236 | 61.2823 | 0.003143 | 61.0697 | 57.2547 | 51.5149 | 52.1208 | 57.2359 | 62.6401 | 57.2138 | 52.3319 | 123.1705 | 61.4562 | 123.088 | 61.1333 | 61.21 | 122.4441 | 61.1649 | 122.2315 | 61.9604 | 62.0055 | 61.8779 | 61.923
6149.0781 | 123.3765 | -61.171 | 61.8942 | -3.898 | -9.6102 | -8.9723 | -3.871 | 1.6752 | -3.948 | -8.8482 | 61.9858 | 0.30358 | 61.9033 | -0.028522 | 0.048236 | 61.2823 | 0.003143 | 61.0651 | 57.273 | 51.5607 | 52.1986 | 57.3 | 62.8461 | 57.223 | 52.3227 | 123.1568 | 61.4745 | 123.0742 | 61.1424 | 61.2192 | 122.4533 | 61.1741 | 122.236 | 61.9376 | 61.9826 | 61.8551 | 61.9001
6150.0625 | 123.3398 | -61.116 | 61.9675 | -4.0262 | -9.656 | -9.0364 | -3.9808 | 1.5561 | -4.067 | -8.894 | 62.0041 | 0.28984 | 61.9216 | -0.019364 | 0.048236 | 61.2732 | 0.007721 | 61.0651 | 57.0899 | 51.46 | 52.0796 | 57.1352 | 62.6722 | 57.049 | 52.222 | 123.1201 | 61.4059 | 123.0376 | 61.0967 | 61.1643 | 122.3892 | 61.1237 | 122.1811 | 61.9559 | 61.9964 | 61.8734 | 61.9139
6151.1094 | 123.3719 | -61.1389 | 61.9537 | -3.8797 | -9.5049 | -8.835 | -3.8389 | 1.666 | -3.9159 | -8.7841 | 61.9949 | 0.29442 | 61.9216 | -0.033101 | 0.039079 | 61.2823 | 0.012299 | 61.0605 | 57.2593 | 51.634 | 52.3039 | 57.3 | 62.8049 | 57.223 | 52.3548 | 123.1339 | 61.4333 | 123.0605 | 61.1058 | 61.178 | 122.4212 | 61.1512 | 122.1994 | 61.9559 | 61.9826 | 61.8825 | 61.9093
6152.0625 | 123.349 | -61.1435 | 61.9675 | -3.9483 | -9.5645 | -8.922 | -3.9396 | 1.5195 | -3.98 | -8.8665 | 61.9995 | 0.29442 | 61.8987 | -0.028522 | 0.043657 | 61.2823 | 0.021456 | 61.0651 | 57.1952 | 51.579 | 52.2215 | 57.2039 | 62.663 | 57.1635 | 52.2769 | 123.143 | 61.4379 | 123.0422 | 61.115 | 61.1872 | 122.4258 | 61.1649 | 122.2086 | 61.9559 | 61.9781 | 61.8551 | 61.8773
6153.0625 | 123.2574 | -61.203 | 61.9629 | -3.9163 | -9.482 | -8.7754 | -3.8618 | 1.579 | -3.9434 | -8.7979 | 61.9995 | 0.29442 | 61.9262 | -0.019364 | 0.048236 | 61.2869 | 0.012299 | 61.0605 | 57.2867 | 51.721 | 52.4276 | 57.3412 | 62.782 | 57.2596 | 52.4051 | 123.2025 | 61.4974 | 123.1292 | 61.1836 | 61.2512 | 122.4899 | 61.2153 | 122.2635 | 61.9513 | 61.9872 | 61.8779 | 61.9139
6154.0938 | 123.3536 | -61.1801 | 61.9629 | -3.985 | -9.4134 | -8.6793 | -3.8206 | 1.5653 | -4.0212 | -8.7979 | 61.9904 | 0.29442 | 61.9033 | -0.028522 | 0.048236 | 61.2823 | 0.007721 | 61.0697 | 57.1952 | 51.7668 | 52.5008 | 57.3595 | 62.7454 | 57.1589 | 52.3822 | 123.1705 | 61.4745 | 123.0834 | 61.1516 | 61.2284 | 122.4624 | 61.1878 | 122.2498 | 61.9421 | 61.9827 | 61.8551 | 61.8956
6155.0625 | 123.3994 | -61.1389 | 61.9446 | -3.9666 | -9.3126 | -8.5831 | -3.7931 | 1.547 | -4.0121 | -8.7155 | 61.9904 | 0.28526 | 61.8987 | -0.023943 | 0.043657 | 61.2869 | 0.012299 | 61.0697 | 57.1723 | 51.8263 | 52.5558 | 57.3458 | 62.6859 | 57.1268 | 52.4235 | 123.1293 | 61.4242 | 123.0376 | 61.115 | 61.1826 | 122.4258 | 61.1512 | 122.2086 | 61.9467 | 61.9781 | 61.8551 | 61.8864
6156.1094 | 123.3627 | -61.1664 | 61.9125 | -3.9209 | -9.2256 | -8.4595 | -3.7061 | 1.5745 | -3.9663 | -8.688 | 61.9904 | 0.28984 | 61.9308 | -0.023943 | 0.039079 | 61.2869 | 0.003143 | 61.0742 | 57.2455 | 51.9408 | 52.7069 | 57.4603 | 62.7408 | 57.2001 | 52.4784 | 123.1568 | 61.4562 | 123.0971 | 61.1424 | 61.2055 | 122.4533 | 61.1695 | 122.2406 | 61.9513 | 61.9872 | 61.8917 | 61.9276
6157.0625 | 123.3856 | -61.1298 | 61.9583 | -3.7744 | -9.0287 | -8.2535 | -3.5779 | 1.6981 | -3.8152 | -8.5049 | 61.9812 | 0.28984 | 61.885 | -0.023943 | 0.048236 | 61.2961 | 0.007721 | 61.0834 | 57.3554 | 52.101 | 52.8763 | 57.5518 | 62.8278 | 57.3146 | 52.6249 | 123.111 | 61.4196 | 123.0147 | 61.1058 | 61.178 | 122.4258 | 61.1375 | 122.2132 | 61.933 | 61.9735 | 61.8367 | 61.8773
6158.0938 | 123.3994 | -61.1618 | 61.94 | -3.7423 | -8.9601 | -8.1482 | -3.5459 | 1.7622 | -3.7786 | -8.4637 | 61.9766 | 0.28984 | 61.8941 | -0.033101 | 0.052814 | 61.3052 | 0.012299 | 61.0834 | 57.4195 | 52.2017 | 53.0136 | 57.6159 | 62.924 | 57.3832 | 52.6981 | 123.1384 | 61.4516 | 123.0559 | 61.1287 | 61.2146 | 122.467 | 61.1741 | 122.2452 | 61.9238 | 61.9643 | 61.8413 | 61.8818
6159.0625 | 123.4634 | -61.1298 | 61.9629 | -3.7835 | -8.9051 | -8.1161 | -3.5779 | 1.6935 | -3.8198 | -8.427 | 61.9766 | 0.29442 | 61.9124 | -0.028522 | 0.048236 | 61.3006 | 0.003143 | 61.088 | 57.3462 | 52.2247 | 53.0136 | 57.5518 | 62.8232 | 57.31 | 52.7027 | 123.1064 | 61.4242 | 123.0422 | 61.1012 | 61.178 | 122.4304 | 61.1329 | 122.2177 | 61.9284 | 61.9735 | 61.8642 | 61.9093
6160.0938 | 123.349 | -61.1801 | 61.9125 | -3.7286 | -8.7494 | -7.9238 | -3.4726 | 1.8354 | -3.7648 | -8.2851 | 61.9675 | 0.299 | 61.8667 | -0.023943 | 0.043657 | 61.3144 | 0.016878 | 61.088 | 57.4515 | 52.4307 | 53.2563 | 57.7075 | 63.0155 | 57.4153 | 52.895 | 123.1476 | 61.4791 | 123.0468 | 61.1562 | 61.2238 | 122.4945 | 61.197 | 122.2681 | 61.9238 | 61.9506 | 61.823 | 61.8498
6161.0625 | 123.3032 | -61.1664 | 61.9217 | -3.6278 | -8.5159 | -7.6628 | -3.3856 | 1.8446 | -3.6595 | -8.1066 | 61.9675 | 0.28984 | 61.9033 | -0.028522 | 0.048236 | 61.3189 | 0.007721 | 61.0971 | 57.5385 | 52.6505 | 53.5035 | 57.7807 | 63.0109 | 57.5068 | 53.0598 | 123.1339 | 61.4562 | 123.0697 | 61.1379 | 61.2146 | 122.4853 | 61.1741 | 122.2635 | 61.9192 | 61.9598 | 61.8551 | 61.8956
6162.0781 | 123.4131 | -61.2122 | 61.853 | -3.6233 | -8.4839 | -7.6125 | -3.3719 | 1.8583 | -3.6641 | -8.1066 | 61.9537 | 0.29442 | 61.8804 | -0.028522 | 0.043657 | 61.3189 | -0.001436 | 61.0971 | 57.5889 | 52.7283 | 53.5997 | 57.8403 | 63.0705 | 57.548 | 53.1056 | 123.1659 | 61.5066 | 123.0926 | 61.1836 | 61.2558 | 122.5311 | 61.2107 | 122.3093 | 61.9101 | 61.9552 | 61.8367 | 61.8818
6163.0625 | 123.3719 | -61.2122 | 61.8896 | -3.4859 | -8.374 | -7.4889 | -3.2757 | 1.8034 | -3.5222 | -8.0654 | 61.9446 | 0.29442 | 61.8529 | -0.033101 | 0.052814 | 61.3235 | 0.012299 | 61.1063 | 57.7262 | 52.8382 | 53.7233 | 57.9364 | 63.0155 | 57.69 | 53.1468 | 123.1567 | 61.5066 | 123.0651 | 61.1791 | 61.265 | 122.5357 | 61.2245 | 122.3184 | 61.8918 | 61.9323 | 61.8001 | 61.8406
6164.0938 | 123.3719 | -61.171 | 61.8896 | -3.6004 | -8.5892 | -7.6995 | -3.4177 | 1.6706 | -3.6366 | -8.2576 | 61.9629 | 0.29442 | 61.9079 | -0.028522 | 0.052814 | 61.3189 | 0.007721 | 61.088 | 57.5706 | 52.5818 | 53.4715 | 57.7533 | 62.8416 | 57.5343 | 52.9133 | 123.1339 | 61.4654 | 123.0788 | 61.1424 | 61.2238 | 122.4899 | 61.1787 | 122.2589 | 61.9101 | 61.9552 | 61.8551 | 61.9001
6165.0625 | 123.3673 | -61.1801 | 61.9171 | -3.5821 | -8.5296 | -7.6216 | -3.3902 | 1.6843 | -3.6138 | -8.2073 | 61.9583 | 0.29442 | 61.8621 | -0.023943 | 0.048236 | 61.3189 | 0.007721 | 61.0926 | 57.5981 | 52.6505 | 53.5585 | 57.7899 | 62.8644 | 57.5664 | 52.9728 | 123.1384 | 61.4745 | 123.0422 | 61.1562 | 61.2284 | 122.4991 | 61.1878 | 122.2727 | 61.9101 | 61.9506 | 61.8138 | 61.8544
6166.0938 | 123.3536 | -61.2213 | 61.8759 | -3.3989 | -8.3007 | -7.3881 | -3.2437 | 1.8491 | -3.4398 | -7.9738 | 61.9446 | 0.29442 | 61.8621 | -0.03768 | 0.043657 | 61.3235 | 0.012299 | 61.1063 | 57.8224 | 52.9206 | 53.8332 | 57.9776 | 63.0704 | 57.7815 | 53.2475 | 123.1659 | 61.5157 | 123.0834 | 61.1836 | 61.265 | 122.5448 | 61.2336 | 122.3276 | 61.9009 | 61.9323 | 61.8184 | 61.8498
6167.0625 | 123.3902 | -61.2213 | 61.8851 | -3.4081 | -8.1633 | -7.2279 | -3.1704 | 1.927 | -3.4444 | -7.9418 | 61.9446 | 0.28984 | 61.885 | -0.033101 | 0.043657 | 61.3327 | 0.012299 | 61.1154 | 57.8132 | 53.058 | 53.9934 | 58.0509 | 63.1483 | 57.777 | 53.2796 | 123.1659 | 61.5112 | 123.1063 | 61.1882 | 61.265 | 122.554 | 61.2336 | 122.3368 | 61.9009 | 61.9323 | 61.8413 | 61.8727
6168.0938 | 123.3902 | -61.235 | 61.8622 | -3.3394 | -7.9893 | -7.0173 | -3.001 | 2.0963 | -3.3757 | -7.7632 | 61.9308 | 0.28984 | 61.8392 | -0.028522 | 0.048236 | 61.3464 | 0.003143 | 61.12 | 57.8956 | 53.2457 | 54.2178 | 58.234 | 63.3314 | 57.8594 | 53.4718 | 123.1659 | 61.5249 | 123.0742 | 61.2065 | 61.2833 | 122.5815 | 61.2382 | 122.3551 | 61.8826 | 61.9277 | 61.791 | 61.8361
6169.0625 | 123.3353 | -61.2442 | 61.8851 | -3.376 | -8.0489 | -7.0585 | -3.0194 | 2.0643 | -3.4123 | -7.7861 | 61.94 | 0.29442 | 61.8667 | -0.028522 | 0.048236 | 61.3373 | 0.012299 | 61.1154 | 57.8682 | 53.1953 | 54.1857 | 58.2248 | 63.3085 | 57.8319 | 53.4581 | 123.1842 | 61.5386 | 123.1109 | 61.2157 | 61.2924 | 122.5815 | 61.2565 | 122.3596 | 61.8918 | 61.9277 | 61.8184 | 61.8544
6170.0781 | 123.3215 | -61.2488 | 61.853 | -3.2753 | -7.8932 | -6.8616 | -2.9415 | 2.0963 | -3.307 | -7.69 | 61.9308 | 0.29442 | 61.8575 | -0.028522 | 0.039079 | 61.3418 | 0.012299 | 61.1292 | 57.9735 | 53.3556 | 54.3872 | 58.3073 | 63.3451 | 57.9418 | 53.5588 | 123.1796 | 61.5432 | 123.1063 | 61.2203 | 61.2879 | 122.5906 | 61.2611 | 122.378 | 61.8918 | 61.9186 | 61.8184 | 61.8452
6171.0625 | 123.3673 | -61.203 | 61.9354 | -3.1837 | -7.8199 | -6.7792 | -2.9049 | 2.0963 | -3.2154 | -7.6671 | 61.9263 | 0.299 | 61.8438 | -0.028522 | 0.052814 | 61.3464 | 0.012299 | 61.1338 | 58.0193 | 53.3831 | 54.4238 | 58.2981 | 63.2993 | 57.9876 | 53.5359 | 123.1293 | 61.502 | 123.0468 | 61.1745 | 61.2558 | 122.5494 | 61.2153 | 122.3368 | 61.8735 | 61.914 | 61.791 | 61.8315
6172.0781 | 123.2849 | -61.2488 | 61.8622 | -3.1517 | -7.7696 | -6.7197 | -2.8774 | 2.078 | -3.1925 | -7.5938 | 61.9308 | 0.29442 | 61.8712 | -0.028522 | 0.043657 | 61.351 | 0.012299 | 61.1246 | 58.0971 | 53.4792 | 54.5291 | 58.3714 | 63.3268 | 58.0562 | 53.655 | 123.1796 | 61.5432 | 123.12 | 61.2203 | 61.2924 | 122.5998 | 61.2611 | 122.3734 | 61.8872 | 61.9186 | 61.8276 | 61.8589
6173.0625 | 123.4222 | -61.1893 | 61.8668 | -3.2799 | -7.9573 | -6.912 | -3.001 | 1.9819 | -3.3116 | -7.7861 | 61.94 | 0.29442 | 61.8484 | -0.028522 | 0.048236 | 61.3373 | 0.007721 | 61.12 | 57.9094 | 53.232 | 54.2773 | 58.1882 | 63.1712 | 57.8777 | 53.4032 | 123.1293 | 61.4837 | 123.0376 | 61.1607 | 61.2375 | 122.5265 | 61.197 | 122.3093 | 61.8918 | 61.9323 | 61.8001 | 61.8406
6174.0781 | 123.3215 | -61.2442 | 61.8668 | -3.2982 | -7.9252 | -6.8891 | -2.9919 | 1.9086 | -3.3299 | -7.722 | 61.9354 | 0.28984 | 61.8346 | -0.028522 | 0.048236 | 61.3464 | 0.007721 | 61.1109 | 57.946 | 53.319 | 54.3551 | 58.2523 | 63.1529 | 57.9143 | 53.5222 | 123.1796 | 61.534 | 123.0788 | 61.2157 | 61.2924 | 122.5906 | 61.2519 | 122.3551 | 61.8872 | 61.9277 | 61.7864 | 61.8269
6175.0625 | 123.3353 | -61.2396 | 61.8484 | -3.2524 | -7.7238 | -6.7151 | -2.8957 | 1.9361 | -3.2978 | -7.6121 | 61.94 | 0.28984 | 61.8712 | -0.019364 | 0.048236 | 61.3373 | 0.003143 | 61.1246 | 57.9872 | 53.5158 | 54.5245 | 58.3439 | 63.1757 | 57.9418 | 53.6275 | 123.1796 | 61.5295 | 123.1109 | 61.2203 | 61.2879 | 122.5769 | 61.2428 | 122.3642 | 61.8918 | 61.9369 | 61.823 | 61.8681
6176.1094 | 123.3719 | -61.2259 | 61.8576 | -3.2158 | -7.6276 | -6.6281 | -2.882 | 1.927 | -3.2521 | -7.6121 | 61.9217 | 0.28984 | 61.83 | -0.028522 | 0.048236 | 61.3418 | 0.012299 | 61.1383 | 58.0101 | 53.5983 | 54.5978 | 58.3439 | 63.1529 | 57.9738 | 53.6138 | 123.1476 | 61.5157 | 123.0559 | 61.1974 | 61.2741 | 122.5677 | 61.2382 | 122.3642 | 61.8735 | 61.9094 | 61.7818 | 61.8177
6177.0625 | 123.3536 | -61.2396 | 61.8896 | -3.1151 | -7.6368 | -6.5731 | -2.795 | 1.9911 | -3.1468 | -7.6259 | 61.9308 | 0.299 | 61.8392 | -0.033101 | 0.043657 | 61.351 | 0.007721 | 61.1292 | 58.1246 | 53.6028 | 54.6665 | 58.4446 | 63.2307 | 58.0929 | 53.6138 | 123.1705 | 61.5386 | 123.0788 | 61.2065 | 61.2833 | 122.5906 | 61.2473 | 122.3688 | 61.8872 | 61.9231 | 61.7955 | 61.8315
6178.0625 | 123.3627 | -61.2442 | 61.8484 | -3.0556 | -7.5544 | -6.4633 | -2.7172 | 2.046 | -3.0918 | -7.5755 | 61.9171 | 0.299 | 61.8575 | -0.028522 | 0.043657 | 61.3556 | 0.012299 | 61.1429 | 58.1887 | 53.6898 | 54.781 | 58.527 | 63.2902 | 58.1524 | 53.6687 | 123.1613 | 61.5432 | 123.1017 | 61.2157 | 61.2879 | 122.5998 | 61.2565 | 122.3871 | 61.8735 | 61.9048 | 61.8138 | 61.8452
6179.0781 | 123.3215 | -61.2305 | 61.8622 | -3.0876 | -7.5544 | -6.4449 | -2.708 | 2.0597 | -3.1147 | -7.5938 | 61.9171 | 0.28984 | 61.8255 | -0.028522 | 0.048236 | 61.3556 | 0.003143 | 61.1429 | 58.1429 | 53.6761 | 54.7855 | 58.5225 | 63.2902 | 58.1158 | 53.6367 | 123.1476 | 61.5203 | 123.0559 | 61.2019 | 61.2787 | 122.586 | 61.2336 | 122.3734 | 61.8689 | 61.914 | 61.7772 | 61.8223
6180.0625 | 123.3627 | -61.2305 | 61.8347 | -3.2936 | -7.8016 | -6.6876 | -2.8637 | 1.8674 | -3.3391 | -7.7678 | 61.9354 | 0.299 | 61.8484 | -0.03768 | 0.043657 | 61.3373 | 0.007721 | 61.12 | 57.9368 | 53.4289 | 54.5429 | 58.3668 | 63.0979 | 57.8914 | 53.4627 | 123.1659 | 61.5295 | 123.0788 | 61.1928 | 61.2741 | 122.5677 | 61.2382 | 122.3505 | 61.8918 | 61.9277 | 61.8047 | 61.8406
6181.1094 | 123.3444 | -61.2442 | 61.8576 | -3.289 | -7.8291 | -6.651 | -2.7996 | 1.9041 | -3.3207 | -7.7861 | 61.9354 | 0.299 | 61.8575 | -0.028522 | 0.052814 | 61.3464 | 0.012299 | 61.1292 | 57.9552 | 53.4151 | 54.5932 | 58.4446 | 63.1483 | 57.9235 | 53.4581 | 123.1796 | 61.5432 | 123.1017 | 61.2157 | 61.297 | 122.5906 | 61.2565 | 122.3734 | 61.8826 | 61.9231 | 61.8047 | 61.8452
6182.0625 | 123.3398 | -61.2488 | 61.8439 | -3.17 | -7.6459 | -6.4358 | -2.6943 | 2.0048 | -3.1971 | -7.603 | 61.9171 | 0.28984 | 61.8209 | -0.028522 | 0.043657 | 61.3556 | 0.007721 | 61.1338 | 58.0788 | 53.6028 | 54.813 | 58.5545 | 63.2536 | 58.0517 | 53.6458 | 123.1659 | 61.5386 | 123.0697 | 61.2203 | 61.2924 | 122.6043 | 61.2565 | 122.3825 | 61.8735 | 61.9094 | 61.7772 | 61.8132
6183.0781 | 123.1934 | -61.2854 | 61.8118 | -3.2021 | -7.6643 | -6.4404 | -2.7172 | 2.0094 | -3.2383 | -7.6396 | 61.9308 | 0.28984 | 61.8575 | -0.028522 | 0.039079 | 61.3556 | 0.007721 | 61.1246 | 58.0833 | 53.6211 | 54.845 | 58.5682 | 63.2948 | 58.0471 | 53.6458 | 123.2163 | 61.5752 | 123.1429 | 61.2569 | 61.3245 | 122.641 | 61.2931 | 122.41 | 61.8918 | 61.9231 | 61.8184 | 61.8498
6184.0625 | 123.3215 | -61.2396 | 61.8668 | -3.0968 | -7.4857 | -6.2526 | -2.589 | 2.1375 | -3.133 | -7.5526 | 61.9263 | 0.29442 | 61.8392 | -0.033101 | 0.048236 | 61.3601 | 0.007721 | 61.1383 | 58.1429 | 53.7539 | 54.987 | 58.6506 | 63.3772 | 58.1066 | 53.687 | 123.1659 | 61.534 | 123.0788 | 61.2065 | 61.2879 | 122.5998 | 61.2473 | 122.378 | 61.878 | 61.9186 | 61.791 | 61.8315
6185.0781 | 123.3765 | -61.2488 | 61.8393 | -3.1105 | -7.5086 | -6.2526 | -2.5981 | 2.1284 | -3.1468 | -7.4885 | 61.9171 | 0.29442 | 61.8163 | -0.028522 | 0.052814 | 61.3647 | 0.007721 | 61.1383 | 58.1383 | 53.7402 | 54.9961 | 58.6506 | 63.3772 | 58.102 | 53.7603 | 123.1659 | 61.5432 | 123.0651 | 61.2203 | 61.3016 | 122.6135 | 61.2565 | 122.3871 | 61.8643 | 61.9094 | 61.7635 | 61.8086
6186.0625 | 123.3353 | -61.2579 | 61.8896 | -3.1837 | -7.5589 | -6.303 | -2.6668 | 2.1009 | -3.22 | -7.5343 | 61.9354 | 0.29442 | 61.8621 | -0.019364 | 0.048236 | 61.3601 | 0.012299 | 61.1383 | 58.0742 | 53.699 | 54.9549 | 58.5911 | 63.3589 | 58.0379 | 53.7236 | 123.1934 | 61.5524 | 123.12 | 61.2386 | 61.3062 | 122.6181 | 61.2702 | 122.3963 | 61.8872 | 61.9231 | 61.8138 | 61.8498
6187.0938 | 123.3032 | -61.2854 | 61.8576 | -3.0556 | -7.4216 | -6.097 | -2.4791 | 2.2657 | -3.0781 | -7.4656 | 61.9125 | 0.30358 | 61.8163 | -0.033101 | 0.039079 | 61.3647 | 0.007721 | 61.1429 | 58.2298 | 53.8638 | 55.1884 | 58.8063 | 63.5511 | 58.2073 | 53.8198 | 123.1979 | 61.589 | 123.1017 | 61.2523 | 61.3245 | 122.6501 | 61.2931 | 122.4283 | 61.8735 | 61.9048 | 61.7772 | 61.8086
6188.0625 | 123.3353 | -61.2671 | 61.8484 | -3.0464 | -7.4307 | -6.0603 | -2.4608 | 2.1696 | -3.0781 | -7.3832 | 61.9171 | 0.299 | 61.8117 | -0.028522 | 0.048236 | 61.3647 | 0.012299 | 61.1475 | 58.2207 | 53.8364 | 55.2068 | 58.8063 | 63.4367 | 58.189 | 53.8839 | 123.1842 | 61.5661 | 123.0788 | 61.2386 | 61.3153 | 122.6318 | 61.2794 | 122.4146 | 61.8689 | 61.9048 | 61.7635 | 61.7994
6189.0938 | 123.3673 | -61.2579 | 61.821 | -2.8953 | -7.2247 | -5.7948 | -2.2822 | 2.3939 | -2.9178 | -7.3008 | 61.908 | 0.29442 | 61.8529 | -0.033101 | 0.043657 | 61.3785 | 0.012299 | 61.1475 | 58.3626 | 54.0333 | 55.4632 | 58.9757 | 63.6518 | 58.3401 | 53.9571 | 123.1659 | 61.5524 | 123.1109 | 61.2248 | 61.3016 | 122.6364 | 61.2702 | 122.4054 | 61.8643 | 61.8957 | 61.8093 | 61.8406
6190.0625 | 123.3582 | -61.2671 | 61.8439 | -2.8037 | -7.1148 | -5.7307 | -2.2547 | 2.3527 | -2.84 | -7.1177 | 61.8942 | 0.29442 | 61.798 | -0.028522 | 0.043657 | 61.3785 | 0.007721 | 61.1658 | 58.4634 | 54.1523 | 55.5364 | 59.0123 | 63.6198 | 58.4271 | 54.1494 | 123.1613 | 61.5615 | 123.0651 | 61.2386 | 61.3107 | 122.6455 | 61.2748 | 122.4329 | 61.8506 | 61.8865 | 61.7543 | 61.7903
6191.0938 | 123.317 | -61.2625 | 61.8576 | -2.671 | -6.8859 | -5.4605 | -2.0624 | 2.5541 | -2.7072 | -6.9712 | 61.8896 | 0.299 | 61.8026 | -0.028522 | 0.048236 | 61.3876 | 0.007721 | 61.1795 | 58.5915 | 54.3767 | 55.802 | 59.2001 | 63.8167 | 58.5553 | 54.2913 | 123.1522 | 61.5615 | 123.0651 | 61.234 | 61.3107 | 122.6501 | 61.2702 | 122.442 | 61.8414 | 61.8819 | 61.7543 | 61.7948
6192.0625 | 123.3032 | -61.2717 | 61.8439 | -2.7396 | -7.0507 | -5.6162 | -2.1769 | 2.4488 | -2.7622 | -7.0902 | 61.8988 | 0.28984 | 61.8346 | -0.028522 | 0.043657 | 61.3876 | 0.007721 | 61.1612 | 58.532 | 54.221 | 55.6555 | 59.0948 | 63.7205 | 58.5095 | 54.1815 | 123.1705 | 61.5615 | 123.1063 | 61.2431 | 61.3153 | 122.6593 | 61.2794 | 122.4329 | 61.8551 | 61.8911 | 61.791 | 61.8269
6193.0938 | 123.3307 | -61.2717 | 61.8027 | -2.6481 | -6.95 | -5.4743 | -2.0441 | 2.5816 | -2.6843 | -7.1177 | 61.8851 | 0.29442 | 61.7934 | -0.033101 | 0.048236 | 61.3922 | 0.007721 | 61.1658 | 58.6236 | 54.3217 | 55.7974 | 59.2275 | 63.8533 | 58.5873 | 54.154 | 123.1567 | 61.5661 | 123.0651 | 61.2386 | 61.3199 | 122.6639 | 61.2794 | 122.4375 | 61.8368 | 61.8773 | 61.7452 | 61.7857
6194.0625 | 123.3765 | -61.2671 | 61.8301 | -2.6527 | -7.0141 | -5.4102 | -1.9983 | 2.632 | -2.6889 | -7.1085 | 61.8896 | 0.29442 | 61.798 | -0.033101 | 0.048236 | 61.3876 | 0.007721 | 61.1704 | 58.6144 | 54.253 | 55.8569 | 59.2687 | 63.8991 | 58.5782 | 54.1586 | 123.1567 | 61.5615 | 123.0651 | 61.234 | 61.3153 | 122.6547 | 61.2748 | 122.4375 | 61.8414 | 61.8819 | 61.7498 | 61.7903
6195.0938 | 123.349 | -61.2854 | 61.8301 | -2.6572 | -6.9957 | -5.3049 | -1.9617 | 2.6228 | -2.6935 | -7.1497 | 61.8988 | 0.29442 | 61.8255 | -0.033101 | 0.043657 | 61.3922 | 0.003143 | 61.1658 | 58.6282 | 54.2897 | 55.9805 | 59.3237 | 63.9082 | 58.5919 | 54.1357 | 123.1842 | 61.5798 | 123.1109 | 61.2523 | 61.3291 | 122.6776 | 61.2885 | 122.4512 | 61.8551 | 61.8957 | 61.7818 | 61.8223
6196.0625 | 123.349 | -61.2717 | 61.8347 | -2.6023 | -6.8217 | -5.2682 | -1.9342 | 2.6549 | -2.6386 | -7.0444 | 61.8851 | 0.29442 | 61.7843 | -0.028522 | 0.048236 | 61.3922 | 0.012299 | 61.1795 | 58.6694 | 54.4499 | 56.0034 | 59.3374 | 63.9265 | 58.6331 | 54.2272 | 123.1567 | 61.5661 | 123.0559 | 61.2431 | 61.3199 | 122.6639 | 61.284 | 122.4512 | 61.8368 | 61.8728 | 61.736 | 61.772
6197.0781 | 123.3536 | -61.2762 | 61.7935 | -2.6664 | -6.8446 | -5.2866 | -1.9526 | 2.5816 | -2.7072 | -7.0994 | 61.8896 | 0.29442 | 61.8071 | -0.03768 | 0.052814 | 61.3922 | 0.003143 | 61.1704 | 58.6099 | 54.4316 | 55.9897 | 59.3237 | 63.8579 | 58.569 | 54.1769 | 123.1659 | 61.5707 | 123.0834 | 61.2386 | 61.3291 | 122.6684 | 61.2794 | 122.4466 | 61.8368 | 61.8865 | 61.7543 | 61.804
6198.0625 | 123.3582 | -61.2488 | 61.8301 | -2.6984 | -6.8859 | -5.401 | -2.0029 | 2.4626 | -2.7301 | -7.0078 | 61.8896 | 0.28984 | 61.8255 | -0.033101 | 0.052814 | 61.3922 | 0.012299 | 61.175 | 58.5503 | 54.3629 | 55.8478 | 59.2459 | 63.7114 | 58.5187 | 54.241 | 123.1384 | 61.5386 | 123.0742 | 61.2157 | 61.3016 | 122.641 | 61.2611 | 122.4237 | 61.8368 | 61.8773 | 61.7726 | 61.8132
6199.0781 | 123.2437 | -61.3083 | 61.8393 | -2.6664 | -6.8217 | -5.282 | -1.9846 | 2.4488 | -2.6981 | -6.9712 | 61.8805 | 0.28984 | 61.7888 | -0.033101 | 0.052814 | 61.3876 | 0.003143 | 61.175 | 58.6419 | 54.4865 | 56.0263 | 59.3237 | 63.7571 | 58.6102 | 54.3371 | 123.1888 | 61.5981 | 123.0971 | 61.2752 | 61.3611 | 122.6959 | 61.3114 | 122.4832 | 61.8277 | 61.8773 | 61.736 | 61.7857
6200.0625 | 123.3582 | -61.2854 | 61.8027 | -2.5519 | -6.7027 | -5.1034 | -1.8839 | 2.4992 | -2.5836 | -6.9712 | 61.8851 | 0.299 | 61.8163 | -0.028522 | 0.039079 | 61.3968 | 0.012299 | 61.1795 | 58.7335 | 54.5827 | 56.182 | 59.4015 | 63.7846 | 58.7018 | 54.3142 | 123.1705 | 61.5844 | 123.1017 | 61.2569 | 61.3245 | 122.6822 | 61.2977 | 122.4649 | 61.846 | 61.8728 | 61.7772 | 61.804
6201.0938 | 123.2849 | -61.2854 | 61.8622 | -2.6298 | -6.7531 | -5.2316 | -1.9892 | 2.4168 | -2.6614 | -6.962 | 61.8896 | 0.299 | 61.798 | -0.028522 | 0.048236 | 61.3922 | 0.016878 | 61.175 | 58.6556 | 54.5323 | 56.0538 | 59.2962 | 63.7022 | 58.624 | 54.3234 | 123.175 | 61.5844 | 123.0834 | 61.2569 | 61.3336 | 122.6776 | 61.3023 | 122.4604 | 61.8414 | 61.8728 | 61.7498 | 61.7811
6202.0625 | 123.3398 | -61.2717 | 61.8073 | -2.5931 | -6.6752 | -5.108 | -1.8747 | 2.4809 | -2.6248 | -6.9254 | 61.8759 | 0.29442 | 61.7797 | -0.028522 | 0.052814 | 61.3968 | 0.012299 | 61.175 | 58.6785 | 54.5964 | 56.1637 | 59.3969 | 63.7526 | 58.6468 | 54.3463 | 123.1476 | 61.5661 | 123.0513 | 61.2431 | 61.3245 | 122.6684 | 61.284 | 122.4466 | 61.8231 | 61.8636 | 61.7269 | 61.7674
6203.0938 | 123.3444 | -61.2717 | 61.8347 | -2.6435 | -6.776 | -5.2087 | -1.948 | 2.3848 | -2.6752 | -6.9986 | 61.8896 | 0.29442 | 61.8255 | -0.028522 | 0.043657 | 61.3922 | 0.016878 | 61.1704 | 58.6282 | 54.4957 | 56.063 | 59.3237 | 63.6564 | 58.5965 | 54.273 | 123.1613 | 61.5661 | 123.0971 | 61.2431 | 61.3153 | 122.6639 | 61.2885 | 122.442 | 61.846 | 61.8728 | 61.7818 | 61.8086
6204.0625 | 123.3719 | -61.2442 | 61.8118 | -2.616 | -6.7393 | -5.14 | -1.9251 | 2.3802 | -2.6523 | -6.9574 | 61.8759 | 0.299 | 61.7888 | -0.028522 | 0.048236 | 61.3968 | 0.012299 | 61.1795 | 58.6282 | 54.5049 | 56.1042 | 59.3191 | 63.6244 | 58.5919 | 54.2868 | 123.1201 | 61.5432 | 123.033 | 61.2157 | 61.2924 | 122.641 | 61.2565 | 122.4237 | 61.8277 | 61.8636 | 61.7406 | 61.7765
6205.0781 | 123.2666 | -61.2946 | 61.8256 | -2.6527 | -6.7989 | -5.1767 | -1.9526 | 2.3436 | -2.6889 | -7.0765 | 61.8759 | 0.29442 | 61.7888 | -0.028522 | 0.048236 | 61.3876 | 0.012299 | 61.1704 | 58.6419 | 54.4957 | 56.1179 | 59.342 | 63.6381 | 58.6056 | 54.2181 | 123.1705 | 61.589 | 123.0834 | 61.266 | 61.3428 | 122.6822 | 61.3069 | 122.4649 | 61.8277 | 61.8636 | 61.7406 | 61.7765
6206.0625 | 123.3444 | -61.2625 | 61.8439 | -2.5748 | -6.7027 | -5.0897 | -1.8198 | 2.4534 | -2.6019 | -7.0215 | 61.8896 | 0.28984 | 61.8117 | -0.023943 | 0.057392 | 61.3922 | -0.006014 | 61.175 | 58.6877 | 54.5598 | 56.1728 | 59.4427 | 63.7159 | 58.6606 | 54.241 | 123.1522 | 61.5524 | 123.0742 | 61.2386 | 61.3199 | 122.6547 | 61.2565 | 122.4375 | 61.8323 | 61.8957 | 61.7543 | 61.8177
6207.0938 | 123.2986 | -61.2854 | 61.8256 | -2.5931 | -6.6935 | -5.0576 | -1.8015 | 2.426 | -2.6294 | -7.0215 | 61.8759 | 0.28526 | 61.7934 | -0.023943 | 0.043657 | 61.3922 | 0.003143 | 61.175 | 58.6923 | 54.5919 | 56.2278 | 59.4839 | 63.7114 | 58.656 | 54.2639 | 123.1613 | 61.5707 | 123.0788 | 61.2615 | 61.3291 | 122.6776 | 61.2885 | 122.4604 | 61.8323 | 61.8728 | 61.7498 | 61.7903
6208.0625 | 123.3582 | -61.2762 | 61.8118 | -2.5016 | -6.5333 | -4.8516 | -1.6504 | 2.6137 | -2.5287 | -6.9071 | 61.8668 | 0.29442 | 61.7888 | -0.028522 | 0.043657 | 61.4105 | 0.007721 | 61.1841 | 58.7747 | 54.743 | 56.4247 | 59.6259 | 63.8899 | 58.7476 | 54.3692 | 123.143 | 61.5707 | 123.0651 | 61.2477 | 61.3199 | 122.6868 | 61.284 | 122.4604 | 61.8231 | 61.859 | 61.7452 | 61.7811
6209.0938 | 123.4222 | -61.2534 | 61.821 | -2.4787 | -6.5104 | -4.847 | -1.6321 | 2.664 | -2.5195 | -6.9803 | 61.8759 | 0.29442 | 61.8117 | -0.033101 | 0.048236 | 61.4059 | 0.012299 | 61.1887 | 58.7747 | 54.743 | 56.4064 | 59.6213 | 63.9174 | 58.7338 | 54.273 | 123.1293 | 61.5478 | 123.0651 | 61.2203 | 61.3016 | 122.6593 | 61.2657 | 122.442 | 61.8277 | 61.8636 | 61.7635 | 61.7994
6210.0625 | 123.3444 | -61.3083 | 61.8027 | -2.5107 | -6.4692 | -4.8104 | -1.6183 | 2.6091 | -2.5424 | -6.8888 | 61.8668 | 0.29442 | 61.7751 | -0.03768 | 0.043657 | 61.4105 | 0.012299 | 61.1887 | 58.7976 | 54.8391 | 56.4979 | 59.69 | 63.9174 | 58.7659 | 54.4195 | 123.175 | 61.6027 | 123.0834 | 61.2706 | 61.3519 | 122.7188 | 61.3206 | 122.497 | 61.8231 | 61.8545 | 61.7314 | 61.7628
6211.1094 | 123.2941 | -61.3312 | 61.7889 | -2.6755 | -6.4417 | -4.7921 | -1.6275 | 2.6137 | -2.4096 | -6.8476 | 61.8759 | 0.29442 | 61.8071 | -0.028522 | 0.048236 | 61.4059 | -0.001436 | 61.1795 | 58.6556 | 54.8895 | 56.5391 | 59.7037 | 63.9448 | 58.9215 | 54.4836 | 123.2071 | 61.6256 | 123.1383 | 61.3027 | 61.3794 | 122.7371 | 61.3297 | 122.5107 | 61.8277 | 61.8773 | 61.7589 | 61.8086
6212.0625 | 123.3765 | -61.2854 | 61.7981 | -2.671 | -6.4142 | -4.728 | -1.5634 | 2.6228 | -2.4051 | -6.843 | 61.8668 | 0.29442 | 61.8026 | -0.033101 | 0.052814 | 61.4105 | 0.003143 | 61.1887 | 58.6144 | 54.8712 | 56.5574 | 59.722 | 63.9082 | 58.8803 | 54.4424 | 123.1522 | 61.5798 | 123.088 | 61.2523 | 61.3382 | 122.6959 | 61.2885 | 122.4741 | 61.8139 | 61.8636 | 61.7498 | 61.7994
6213.0938 | 123.3673 | -61.2991 | 61.7752 | -2.442 | -6.2036 | -4.4304 | -1.3711 | 2.7373 | -2.2448 | -6.6416 | 61.8484 | 0.299 | 61.7568 | -0.033101 | 0.048236 | 61.4105 | 0.007721 | 61.1978 | 58.8571 | 55.0955 | 56.8688 | 59.928 | 64.0364 | 59.0543 | 54.6576 | 123.1476 | 61.5981 | 123.0559 | 61.266 | 61.3474 | 122.7096 | 61.3069 | 122.497 | 61.8002 | 61.8407 | 61.7085 | 61.7491
6214.0625 | 123.2574 | -61.2991 | 61.8439 | -2.3825 | -6.2448 | -4.4624 | -1.4489 | 2.6228 | -2.3593 | -6.6919 | 61.8622 | 0.28526 | 61.8026 | -0.033101 | 0.048236 | 61.4197 | 0.012299 | 61.1978 | 58.9166 | 55.0543 | 56.8367 | 59.8502 | 63.9219 | 58.9399 | 54.6072 | 123.1613 | 61.5844 | 123.1017 | 61.266 | 61.3474 | 122.7188 | 61.3114 | 122.497 | 61.8139 | 61.8499 | 61.7543 | 61.7903
6215.0781 | 123.3032 | -61.3403 | 61.821 | -2.4054 | -6.2677 | -4.4532 | -1.4398 | 2.6091 | -2.4417 | -6.7697 | 61.8576 | 0.29442 | 61.7751 | -0.023943 | 0.048236 | 61.4197 | 0.007721 | 61.1978 | 58.9349 | 55.0726 | 56.8871 | 59.9006 | 63.9494 | 58.8986 | 54.5706 | 123.1979 | 61.6348 | 123.1154 | 61.3164 | 61.3886 | 122.76 | 61.3481 | 122.5382 | 61.8094 | 61.8499 | 61.7269 | 61.7674
6216.0625 | 123.3078 | -61.2991 | 61.7981 | -2.3001 | -6.1075 | -4.2609 | -1.2658 | 2.7739 | -2.341 | -6.5683 | 61.8484 | 0.28984 | 61.7614 | -0.023943 | 0.057392 | 61.4197 | 0.012299 | 61.2207 | 58.999 | 55.1917 | 57.0382 | 60.0333 | 64.073 | 58.9582 | 54.7308 | 123.1476 | 61.589 | 123.0605 | 61.2752 | 61.3565 | 122.7188 | 61.3114 | 122.5199 | 61.791 | 61.8361 | 61.704 | 61.7491
6217.0938 | 123.4268 | -61.3266 | 61.7523 | -2.3139 | -6.1258 | -4.2289 | -1.2154 | 2.8242 | -2.3501 | -6.6049 | 61.8576 | 0.29442 | 61.798 | -0.033101 | 0.048236 | 61.4242 | -0.001436 | 61.207 | 59.0127 | 55.2008 | 57.0977 | 60.1112 | 64.1508 | 58.9765 | 54.7217 | 123.1842 | 61.621 | 123.1246 | 61.2935 | 61.3748 | 122.7508 | 61.3252 | 122.5336 | 61.8094 | 61.859 | 61.7498 | 61.7994
6218.0625 | 123.4131 | -61.2762 | 61.8164 | -2.3871 | -6.1899 | -4.2564 | -1.2612 | 2.7739 | -2.428 | -6.6416 | 61.8576 | 0.28984 | 61.7705 | -0.028522 | 0.048236 | 61.4242 | 0.003143 | 61.2116 | 58.8891 | 55.0864 | 57.0199 | 60.015 | 64.0501 | 58.8483 | 54.6347 | 123.1338 | 61.5661 | 123.0468 | 61.2477 | 61.3245 | 122.7005 | 61.2794 | 122.4878 | 61.8094 | 61.8545 | 61.7223 | 61.7674
6219.0938 | 123.2895 | -61.3266 | 61.8347 | -2.4604 | -6.2631 | -4.3113 | -1.3711 | 2.6274 | -2.492 | -6.637 | 61.8668 | 0.28526 | 61.7751 | -0.03768 | 0.052814 | 61.4197 | 0.012299 | 61.2024 | 58.8662 | 55.0635 | 57.0153 | 59.9555 | 63.954 | 58.8346 | 54.6896 | 123.1934 | 61.6119 | 123.1017 | 61.2889 | 61.3794 | 122.7463 | 61.3389 | 122.529 | 61.8139 | 61.8545 | 61.7223 | 61.7628
6220.0625 | 123.3902 | -61.2991 | 61.7844 | -2.497 | -6.1258 | -4.0961 | -1.2108 | 2.7647 | -2.2448 | -6.4905 | 61.8576 | 0.28984 | 61.7888 | -0.028522 | 0.052814 | 61.4242 | 0.007721 | 61.207 | 58.8021 | 55.1734 | 57.203 | 60.0883 | 64.0639 | 59.0543 | 54.8087 | 123.1567 | 61.589 | 123.088 | 61.2706 | 61.3519 | 122.7234 | 61.3069 | 122.5061 | 61.8048 | 61.8499 | 61.736 | 61.7811
6221.1094 | 123.3673 | -61.3174 | 61.7477 | -2.3596 | -5.9289 | -3.8306 | -0.96361 | 2.9478 | -2.1212 | -6.344 | 61.8347 | 0.28984 | 61.7476 | -0.023943 | 0.048236 | 61.4334 | 0.003143 | 61.2116 | 58.9578 | 55.3886 | 57.4869 | 60.3538 | 64.2653 | 59.1962 | 54.9735 | 123.1521 | 61.6073 | 123.0651 | 61.2935 | 61.3657 | 122.7508 | 61.3206 | 122.529 | 61.7865 | 61.8316 | 61.6994 | 61.7445
6222.0625 | 123.3948 | -61.2854 | 61.7249 | -2.2864 | -5.764 | -3.7939 | -0.89493 | 3.0394 | -2.0525 | -6.2204 | 61.8347 | 0.29442 | 61.7385 | -0.033101 | 0.048236 | 61.4426 | 0.007721 | 61.2253 | 58.999 | 55.5214 | 57.4915 | 60.3905 | 64.3248 | 59.2329 | 55.065 | 123.1201 | 61.5798 | 123.0239 | 61.2523 | 61.3336 | 122.728 | 61.2931 | 122.5107 | 61.7865 | 61.827 | 61.6902 | 61.7308
6223.0625 | 123.3627 | -61.3358 | 61.7615 | -2.0895 | -5.5946 | -3.6932 | -0.90409 | 3.0531 | -2.0251 | -6.1654 | 61.8301 | 0.28984 | 61.7705 | -0.028522 | 0.048236 | 61.4517 | 0.012299 | 61.2299 | 59.2462 | 55.7411 | 57.6426 | 60.4317 | 64.3889 | 59.3107 | 55.1703 | 123.1659 | 61.6256 | 123.1063 | 61.3072 | 61.384 | 122.7875 | 61.3481 | 122.5656 | 61.7819 | 61.8178 | 61.7223 | 61.7582
6224.0938 | 123.3994 | -61.2991 | 61.7615 | -2.1628 | -5.5992 | -3.5879 | -0.78963 | 3.0715 | -1.9655 | -6.2295 | 61.8301 | 0.29442 | 61.7247 | -0.028522 | 0.043657 | 61.4517 | 0.007721 | 61.2299 | 59.1364 | 55.6999 | 57.7112 | 60.5095 | 64.3706 | 59.3336 | 55.0696 | 123.1293 | 61.5936 | 123.0239 | 61.2706 | 61.3428 | 122.7508 | 61.3069 | 122.529 | 61.7865 | 61.8224 | 61.6811 | 61.717
6225.0625 | 123.3994 | -61.2854 | 61.7477 | -2.2452 | -5.7183 | -3.6108 | -0.75758 | 2.9845 | -2.1166 | -6.3943 | 61.8393 | 0.29442 | 61.7614 | -0.023943 | 0.057392 | 61.438 | 0.007721 | 61.2253 | 59.0402 | 55.5671 | 57.6746 | 60.5278 | 64.2699 | 59.1688 | 54.8911 | 123.1247 | 61.5798 | 123.0468 | 61.2615 | 61.3428 | 122.7234 | 61.2931 | 122.5107 | 61.7819 | 61.8316 | 61.704 | 61.7536
6226.1094 | 123.3627 | -61.3403 | 61.734 | -2.2635 | -5.7045 | -3.5329 | -0.74384 | 3.0303 | -2.0571 | -6.3669 | 61.8301 | 0.29442 | 61.7568 | -0.028522 | 0.043657 | 61.4426 | 0.003143 | 61.2162 | 59.0768 | 55.6358 | 57.8074 | 60.5965 | 64.3706 | 59.2832 | 54.9735 | 123.1705 | 61.6348 | 123.0971 | 61.3118 | 61.384 | 122.7829 | 61.3435 | 122.5565 | 61.7865 | 61.827 | 61.7131 | 61.7536
6227.0625 | 123.3765 | -61.3037 | 61.7523 | -2.03 | -5.4252 | -3.3223 | -0.5607 | 3.1722 | -1.8694 | -6.1105 | 61.8255 | 0.28984 | 61.7339 | -0.028522 | 0.052814 | 61.4471 | 0.012299 | 61.2345 | 59.2737 | 55.8785 | 57.9814 | 60.743 | 64.4759 | 59.4343 | 55.1932 | 123.1293 | 61.5936 | 123.0376 | 61.2752 | 61.3565 | 122.7508 | 61.316 | 122.5382 | 61.7727 | 61.8132 | 61.6811 | 61.7216
6228.0781 | 123.3765 | -61.3495 | 61.734 | -1.8972 | -5.3703 | -3.2674 | -0.5607 | 3.1813 | -1.8465 | -6.0876 | 61.821 | 0.29442 | 61.7476 | -0.028522 | 0.048236 | 61.4609 | 0.007721 | 61.2391 | 59.4523 | 55.9792 | 58.0821 | 60.7888 | 64.5308 | 59.503 | 55.2619 | 123.1705 | 61.6439 | 123.0971 | 61.321 | 61.3977 | 122.8104 | 61.3572 | 122.5885 | 61.7727 | 61.8132 | 61.6994 | 61.7399
6229.0625 | 123.4177 | -61.3358 | 61.7477 | -1.8285 | -5.2008 | -3.13 | -0.51034 | 3.1813 | -1.787 | -5.9777 | 61.821 | 0.28984 | 61.7202 | -0.028522 | 0.052814 | 61.47 | 0.016878 | 61.2482 | 59.5072 | 56.1349 | 58.2057 | 60.8254 | 64.5171 | 59.5488 | 55.358 | 123.1567 | 61.6256 | 123.0559 | 61.3072 | 61.3886 | 122.8058 | 61.3526 | 122.584 | 61.7682 | 61.8041 | 61.6673 | 61.7033
6230.0938 | 123.3536 | -61.3174 | 61.7615 | -1.8469 | -5.1551 | -3.13 | -0.52865 | 3.1127 | -1.819 | -5.9731 | 61.8118 | 0.30358 | 61.7156 | -0.033101 | 0.048236 | 61.4654 | 0.007721 | 61.2436 | 59.4706 | 56.1624 | 58.1874 | 60.7888 | 64.4301 | 59.4984 | 55.3443 | 123.1293 | 61.621 | 123.033 | 61.2843 | 61.3657 | 122.7829 | 61.3252 | 122.5611 | 61.7636 | 61.8041 | 61.6673 | 61.7079
6231.0625 | 123.4314 | -61.3449 | 61.7615 | -1.8102 | -5.123 | -2.9927 | -0.33178 | 3.2775 | -1.613 | -5.9045 | 61.8164 | 0.299 | 61.7568 | -0.028522 | 0.048236 | 61.47 | 0.012299 | 61.2528 | 59.5347 | 56.2219 | 58.3522 | 61.0131 | 64.6224 | 59.7319 | 55.4404 | 123.1613 | 61.6439 | 123.1017 | 61.3164 | 61.3931 | 122.8149 | 61.3572 | 122.5977 | 61.7682 | 61.8041 | 61.7085 | 61.7445
6232.0781 | 123.2712 | -61.377 | 61.7615 | -1.7736 | -5.0131 | -2.8828 | -0.30888 | 3.2912 | -1.5626 | -5.7946 | 61.8072 | 0.299 | 61.711 | -0.03768 | 0.043657 | 61.4654 | 0.012299 | 61.2482 | 59.6034 | 56.3638 | 58.4942 | 61.0681 | 64.6681 | 59.8143 | 55.5824 | 123.1842 | 61.676 | 123.088 | 61.3393 | 61.4206 | 122.8424 | 61.3893 | 122.6252 | 61.7636 | 61.7949 | 61.6673 | 61.6987
6233.0625 | 123.3536 | -61.3541 | 61.7249 | -1.6042 | -4.7704 | -2.6081 | -0.10285 | 3.4056 | -1.5764 | -5.6069 | 61.7889 | 0.29442 | 61.7156 | -0.028522 | 0.039079 | 61.4746 | -0.001436 | 61.2619 | 59.7499 | 56.5836 | 58.746 | 61.2512 | 64.7597 | 59.7777 | 55.7472 | 123.143 | 61.6485 | 123.0696 | 61.3255 | 61.3931 | 122.8287 | 61.3526 | 122.616 | 61.7498 | 61.7904 | 61.6765 | 61.717
6234.0938 | 123.3353 | -61.377 | 61.734 | -1.7461 | -4.8758 | -2.7042 | -0.16237 | 3.3416 | -1.645 | -5.6801 | 61.7935 | 0.29442 | 61.711 | -0.028522 | 0.043657 | 61.4746 | -0.001436 | 61.2528 | 59.6308 | 56.5012 | 58.6727 | 61.2146 | 64.7185 | 59.7319 | 55.6968 | 123.1704 | 61.6714 | 123.088 | 61.3484 | 61.4206 | 122.8516 | 61.3755 | 122.6297 | 61.7498 | 61.7949 | 61.6673 | 61.7124
6235.0625 | 123.4039 | -61.3495 | 61.734 | -1.5996 | -4.7521 | -2.5485 | -0.038752 | 3.5338 | -1.4802 | -5.5657 | 61.7889 | 0.29442 | 61.711 | -0.028522 | 0.052814 | 61.4883 | 0.007721 | 61.2665 | 59.7499 | 56.5974 | 58.8009 | 61.3107 | 64.8833 | 59.8693 | 55.7838 | 123.1384 | 61.6439 | 123.0605 | 61.321 | 61.4023 | 122.8378 | 61.3572 | 122.616 | 61.7361 | 61.7812 | 61.6582 | 61.7033
6236.0938 | 123.2712 | -61.3724 | 61.7569 | -1.7278 | -4.9032 | -2.6767 | -0.12116 | 3.3782 | -1.4528 | -5.6664 | 61.8027 | 0.28984 | 61.7202 | -0.023943 | 0.048236 | 61.4746 | 0.012299 | 61.2619 | 59.6446 | 56.4691 | 58.6956 | 61.2512 | 64.7506 | 59.9196 | 55.706 | 123.175 | 61.6622 | 123.0925 | 61.3484 | 61.4206 | 122.847 | 61.3847 | 122.6343 | 61.7544 | 61.7904 | 61.6719 | 61.7079
6237.0625 | 123.3582 | -61.3632 | 61.7249 | -1.5584 | -4.862 | -2.6126 | -0.098273 | 3.4148 | -1.494 | -5.6115 | 61.7889 | 0.28984 | 61.7018 | -0.023943 | 0.048236 | 61.4792 | 0.003143 | 61.2665 | 59.8048 | 56.5012 | 58.7506 | 61.2649 | 64.778 | 59.8693 | 55.7518 | 123.1521 | 61.6531 | 123.0651 | 61.3393 | 61.4115 | 122.8424 | 61.3664 | 122.6297 | 61.7407 | 61.7858 | 61.6536 | 61.6987
6238.0938 | 123.3627 | -61.3861 | 61.7249 | -1.6179 | -4.7338 | -2.4341 | 0.094024 | 3.5704 | -1.4756 | -5.5932 | 61.7981 | 0.299 | 61.7247 | -0.023943 | 0.043657 | 61.4975 | 0.012299 | 61.2665 | 59.7682 | 56.6523 | 58.952 | 61.4801 | 64.9566 | 59.9105 | 55.793 | 123.1842 | 61.6851 | 123.1108 | 61.3622 | 61.4298 | 122.8836 | 61.3984 | 122.6526 | 61.7544 | 61.7858 | 61.6811 | 61.7124
6239.0625 | 123.3719 | -61.3541 | 61.7203 | -1.6408 | -4.6605 | -2.3975 | 0.13065 | 3.5292 | -1.5214 | -5.5703 | 61.7889 | 0.299 | 61.6973 | -0.028522 | 0.052814 | 61.4929 | 0.012299 | 61.2757 | 59.7132 | 56.6935 | 58.9566 | 61.4847 | 64.8833 | 59.8326 | 55.7838 | 123.143 | 61.6531 | 123.0513 | 61.3255 | 61.4069 | 122.847 | 61.3664 | 122.6297 | 61.7361 | 61.7766 | 61.6445 | 61.685
6240.0781 | 123.3902 | -61.3632 | 61.702 | -1.6683 | -4.7018 | -2.4524 | 0.10318 | 3.5201 | -1.5169 | -5.6115 | 61.7935 | 0.29442 | 61.7018 | -0.028522 | 0.048236 | 61.4883 | 0.003143 | 61.2619 | 59.6949 | 56.6615 | 58.9108 | 61.4664 | 64.8833 | 59.8464 | 55.7518 | 123.1567 | 61.6576 | 123.0651 | 61.3347 | 61.4115 | 122.8516 | 61.3664 | 122.6252 | 61.7453 | 61.7904 | 61.6536 | 61.6987
6241.0625 | 123.317 | -61.3678 | 61.7477 | -1.5493 | -4.6285 | -2.3105 | 0.2268 | 3.6162 | -1.407 | -5.4787 | 61.7889 | 0.30816 | 61.711 | -0.033101 | 0.043657 | 61.4975 | 0.012299 | 61.2757 | 59.8185 | 56.7393 | 59.0573 | 61.5946 | 64.984 | 59.9608 | 55.8891 | 123.1567 | 61.676 | 123.0788 | 61.3347 | 61.4115 | 122.8653 | 61.3801 | 122.6435 | 61.7453 | 61.7766 | 61.6673 | 61.6987
6242.0781 | 123.2712 | -61.4319 | 61.702 | -1.4485 | -4.4911 | -2.1502 | 0.30921 | 3.6025 | -1.1735 | -5.4009 | 61.7798 | 0.299 | 61.6835 | -0.028522 | 0.052814 | 61.4975 | 0.007721 | 61.2757 | 59.9833 | 56.9408 | 59.2817 | 61.7411 | 65.0344 | 60.2584 | 56.031 | 123.2116 | 61.7309 | 123.1154 | 61.4034 | 61.4847 | 122.9294 | 61.4396 | 122.7076 | 61.7269 | 61.772 | 61.6307 | 61.6758
6243.0625 | 123.381 | -61.3861 | 61.6974 | -1.4256 | -4.4728 | -2.0907 | 0.40536 | 3.7078 | -1.1643 | -5.4512 | 61.766 | 0.29442 | 61.7018 | -0.033101 | 0.048236 | 61.5021 | 0.003143 | 61.2803 | 59.9605 | 56.9133 | 59.2954 | 61.7915 | 65.0939 | 60.2218 | 55.9349 | 123.1521 | 61.6805 | 123.088 | 61.353 | 61.4343 | 122.8882 | 61.3893 | 122.6664 | 61.7178 | 61.7629 | 61.6536 | 61.6987
6244.0781 | 123.317 | -61.4044 | 61.6928 | -1.4073 | -4.4362 | -2.0357 | 0.49235 | 3.7993 | -1.059 | -5.41 | 61.7706 | 0.29442 | 61.679 | -0.028522 | 0.048236 | 61.5066 | 0.003143 | 61.2711 | 59.9971 | 56.9682 | 59.3687 | 61.8968 | 65.2038 | 60.3454 | 55.9944 | 123.175 | 61.6988 | 123.0834 | 61.3759 | 61.4527 | 122.9111 | 61.4076 | 122.6755 | 61.7224 | 61.7675 | 61.6307 | 61.6758
6245.0625 | 123.3673 | -61.3861 | 61.7065 | -1.4531 | -4.482 | -2.0953 | 0.38705 | 3.6483 | -1.2147 | -5.4283 | 61.7843 | 0.29442 | 61.7202 | -0.028522 | 0.048236 | 61.4975 | 0.003143 | 61.2848 | 59.933 | 56.9041 | 59.2908 | 61.7732 | 65.0344 | 60.1714 | 55.9578 | 123.1704 | 61.6805 | 123.1063 | 61.3576 | 61.4343 | 122.8836 | 61.3893 | 122.6709 | 61.7361 | 61.7812 | 61.6719 | 61.717
6246.0625 | 123.3353 | -61.3861 | 61.7523 | -1.4531 | -4.3675 | -2.0037 | 0.49235 | 3.7261 | -1.1231 | -5.3826 | 61.7706 | 0.299 | 61.679 | -0.023943 | 0.052814 | 61.5066 | 0.007721 | 61.2894 | 59.933 | 57.0186 | 59.3824 | 61.8785 | 65.1122 | 60.263 | 56.0036 | 123.1567 | 61.6851 | 123.0651 | 61.3622 | 61.4389 | 122.8928 | 61.3938 | 122.6755 | 61.7178 | 61.7629 | 61.6261 | 61.6712
6247.0781 | 123.2483 | -61.4273 | 61.7111 | -1.2425 | -4.1523 | -1.7427 | 0.63887 | 3.8222 | -0.95371 | -5.1628 | 61.7614 | 0.299 | 61.6744 | -0.023943 | 0.048236 | 61.5112 | 0.007721 | 61.2894 | 60.1848 | 57.275 | 59.6846 | 62.0662 | 65.2495 | 60.4736 | 56.2645 | 123.1888 | 61.7263 | 123.1017 | 61.4034 | 61.4755 | 122.9385 | 61.435 | 122.7167 | 61.7132 | 61.7537 | 61.6261 | 61.6667
6248.0625 | 123.3398 | -61.3907 | 61.7157 | -1.3341 | -4.2805 | -1.8709 | 0.5885 | 3.781 | -0.94455 | -5.3001 | 61.7706 | 0.29442 | 61.7018 | -0.033101 | 0.048236 | 61.5112 | 0.007721 | 61.2803 | 60.0566 | 57.1102 | 59.5198 | 61.9792 | 65.1717 | 60.4461 | 56.0905 | 123.1613 | 61.6851 | 123.0925 | 61.3576 | 61.4389 | 122.9019 | 61.3984 | 122.6709 | 61.7224 | 61.7629 | 61.6536 | 61.6941
6249.0938 | 123.3902 | -61.3907 | 61.647 | -1.2196 | -4.047 | -1.6054 | 0.79911 | 4.0237 | -0.8072 | -5.085 | 61.7477 | 0.29442 | 61.6652 | -0.028522 | 0.043657 | 61.525 | 0.012299 | 61.3031 | 60.1711 | 57.3437 | 59.7853 | 62.1898 | 65.4144 | 60.5835 | 56.3057 | 123.1384 | 61.6851 | 123.0559 | 61.3622 | 61.4343 | 122.9156 | 61.403 | 122.6938 | 61.7041 | 61.7354 | 61.6216 | 61.6529
6250.0625 | 123.3444 | -61.3815 | 61.7203 | -1.2654 | -4.0699 | -1.642 | 0.74875 | 3.8268 | -0.8301 | -5.1262 | 61.7569 | 0.299 | 61.7064 | -0.019364 | 0.048236 | 61.5158 | 0.007721 | 61.2986 | 60.1161 | 57.3117 | 59.7395 | 62.1303 | 65.2083 | 60.5514 | 56.2554 | 123.1384 | 61.6805 | 123.088 | 61.3622 | 61.4298 | 122.8973 | 61.3893 | 122.6801 | 61.7086 | 61.7491 | 61.6582 | 61.6987
6251.0938 | 123.2849 | -61.4182 | 61.702 | -1.1693 | -3.9325 | -1.5 | 0.86779 | 4.0008 | -0.71564 | -5.0209 | 61.7477 | 0.28984 | 61.6469 | -0.028522 | 0.039079 | 61.5204 | 0.012299 | 61.3077 | 60.2489 | 57.4856 | 59.9181 | 62.2859 | 65.4189 | 60.7025 | 56.3973 | 123.1659 | 61.708 | 123.0651 | 61.3896 | 61.4572 | 122.9385 | 61.4305 | 122.7259 | 61.7086 | 61.7354 | 61.6078 | 61.6346
6252.0625 | 123.3627 | -61.4044 | 61.6653 | -1.1143 | -3.8959 | -1.3902 | 1.0235 | 4.1244 | -0.63322 | -4.998 | 61.7477 | 0.28984 | 61.6835 | -0.028522 | 0.057392 | 61.5295 | 0.012299 | 61.3077 | 60.2901 | 57.5085 | 60.0143 | 62.4279 | 65.5288 | 60.7712 | 56.4064 | 123.1521 | 61.6943 | 123.088 | 61.3759 | 61.4618 | 122.934 | 61.4167 | 122.7121 | 61.6903 | 61.7354 | 61.6261 | 61.6712
6253.0781 | 123.2117 | -61.4777 | 61.6516 | -1.064 | -3.8501 | -1.3169 | 1.17 | 4.1381 | -0.55539 | -4.8744 | 61.7431 | 0.28984 | 61.6423 | -0.028522 | 0.048236 | 61.5341 | 0.007721 | 61.3169 | 60.4137 | 57.6276 | 60.1608 | 62.6476 | 65.6158 | 60.9223 | 56.6033 | 123.2208 | 61.7675 | 123.12 | 61.4491 | 61.5259 | 123.0118 | 61.4854 | 122.7945 | 61.6949 | 61.7354 | 61.5941 | 61.6346
6254.0625 | 123.3902 | -61.3907 | 61.6699 | -1.1876 | -3.9005 | -1.4497 | 1.028 | 3.9596 | -0.6378 | -4.9476 | 61.7477 | 0.299 | 61.6835 | -0.028522 | 0.048236 | 61.525 | 0.012299 | 61.2986 | 60.2031 | 57.4902 | 59.941 | 62.4187 | 65.3503 | 60.7529 | 56.4431 | 123.1384 | 61.6897 | 123.0742 | 61.3622 | 61.4389 | 122.9156 | 61.403 | 122.6893 | 61.6995 | 61.7354 | 61.6353 | 61.6712
6255.0781 | 123.2666 | -61.4548 | 61.6882 | -1.0456 | -3.8318 | -1.3581 | 1.0372 | 3.987 | -0.77515 | -4.8698 | 61.7431 | 0.30358 | 61.6515 | -0.028522 | 0.048236 | 61.5341 | 0.007721 | 61.3077 | 60.4091 | 57.623 | 60.0967 | 62.492 | 65.4418 | 60.6796 | 56.585 | 123.1979 | 61.7584 | 123.1063 | 61.4263 | 61.503 | 122.9889 | 61.4625 | 122.7625 | 61.6949 | 61.7354 | 61.6032 | 61.6438
6256.0625 | 123.2986 | -61.3998 | 61.7065 | -1.0319 | -3.7814 | -1.2574 | 1.1562 | 4.0969 | -0.69732 | -4.8194 | 61.7431 | 0.28984 | 61.679 | -0.028522 | 0.048236 | 61.5433 | 0.003143 | 61.3123 | 60.3679 | 57.6184 | 60.1425 | 62.5561 | 65.4968 | 60.7025 | 56.5804 | 123.143 | 61.6897 | 123.0788 | 61.3713 | 61.4481 | 122.9431 | 61.403 | 122.7121 | 61.6949 | 61.74 | 61.6307 | 61.6758
6257.0781 | 123.3948 | -61.4594 | 61.6287 | -0.89913 | -3.7265 | -1.2665 | 1.0372 | 3.9596 | -0.70648 | -4.7737 | 61.7386 | 0.29442 | 61.6515 | -0.023943 | 0.048236 | 61.5341 | 0.007721 | 61.3169 | 60.5602 | 57.7329 | 60.1928 | 62.4965 | 65.4189 | 60.7529 | 56.6857 | 123.1979 | 61.7538 | 123.1108 | 61.4354 | 61.5076 | 122.9935 | 61.4671 | 122.7762 | 61.6903 | 61.7308 | 61.6032 | 61.6438
6258.0625 | 123.3765 | -61.4182 | 61.6837 | -0.62901 | -3.5754 | -1.0834 | 1.1929 | 4.1427 | -0.50961 | -4.6455 | 61.734 | 0.299 | 61.6423 | -0.028522 | 0.052814 | 61.5478 | 0.012299 | 61.3306 | 60.7891 | 57.8428 | 60.3348 | 62.611 | 65.5608 | 60.9085 | 56.7727 | 123.1521 | 61.7172 | 123.0605 | 61.3896 | 61.471 | 122.966 | 61.4305 | 122.7488 | 61.6812 | 61.7217 | 61.5895 | 61.63
6259.0938 | 123.3582 | -61.4365 | 61.6516 | -0.70684 | -3.5067 | -0.90483 | 1.4309 | 4.3487 | -0.39057 | -4.6088 | 61.7294 | 0.299 | 61.6561 | -0.033101 | 0.048236 | 61.5524 | 0.012299 | 61.3352 | 60.7296 | 57.9298 | 60.5316 | 62.8674 | 65.7852 | 61.0459 | 56.8276 | 123.1659 | 61.7355 | 123.0925 | 61.4034 | 61.4847 | 122.9889 | 61.4488 | 122.7717 | 61.6812 | 61.7171 | 61.6078 | 61.6438
6260.0625 | 123.4222 | -61.3907 | 61.6653 | -0.63358 | -3.4975 | -0.89109 | 1.4172 | 4.3167 | -0.36768 | -4.5997 | 61.7157 | 0.28526 | 61.624 | -0.028522 | 0.057392 | 61.5524 | 0.012299 | 61.3306 | 60.7571 | 57.8932 | 60.4996 | 62.8079 | 65.7073 | 61.023 | 56.791 | 123.1063 | 61.676 | 123.0147 | 61.3622 | 61.4481 | 122.9431 | 61.403 | 122.7213 | 61.6583 | 61.7034 | 61.5666 | 61.6117
6261.1094 | 123.3765 | -61.4365 | 61.6745 | -0.8625 | -3.5616 | -0.91398 | 1.4401 | 4.2571 | -0.41346 | -4.7004 | 61.734 | 0.23032 | 61.6652 | -0.023943 | 0.048236 | 61.5478 | 0.007721 | 61.3306 | 60.574 | 57.8748 | 60.5225 | 62.8766 | 65.6936 | 61.023 | 56.7361 | 123.1704 | 61.6668 | 123.1017 | 61.4125 | 61.4847 | 122.9843 | 61.4442 | 122.7671 | 61.6857 | 61.7263 | 61.617 | 61.6575
6262.0625 | 123.3765 | -61.3861 | 61.6791 | -0.64732 | -3.5708 | -0.96893 | 1.2799 | 4.161 | -0.44551 | -4.7233 | 61.7248 | 0.22116 | 61.6332 | -0.028522 | 0.052814 | 61.5478 | 0.007721 | 61.3306 | 60.7388 | 57.8153 | 60.4172 | 62.666 | 65.5471 | 60.9406 | 56.6628 | 123.1109 | 61.6073 | 123.0193 | 61.3576 | 61.4389 | 122.934 | 61.3938 | 122.7167 | 61.672 | 61.7171 | 61.5804 | 61.6255
6263.0938 | 123.3444 | -61.4685 | 61.6013 | -0.6931 | -3.5158 | -0.8453 | 1.5454 | 4.3533 | -0.35852 | -4.6913 | 61.734 | 0.23032 | 61.6652 | -0.023943 | 0.043657 | 61.5524 | 0.003143 | 61.3306 | 60.7754 | 57.9527 | 60.6232 | 63.0139 | 65.8218 | 61.11 | 56.7773 | 123.2025 | 61.6988 | 123.1337 | 61.4446 | 61.5122 | 123.0209 | 61.4716 | 122.7991 | 61.6903 | 61.7308 | 61.6216 | 61.6621
6264.0625 | 123.3948 | -61.4044 | 61.647 | -0.79841 | -3.4929 | -0.86362 | 1.495 | 4.1885 | -0.41804 | -4.737 | 61.7294 | 0.22116 | 61.6286 | -0.019364 | 0.043657 | 61.557 | 0.003143 | 61.3352 | 60.606 | 57.9115 | 60.5408 | 62.8995 | 65.5929 | 60.9864 | 56.6674 | 123.1338 | 61.6256 | 123.033 | 61.3851 | 61.4481 | 122.9614 | 61.4076 | 122.7396 | 61.6857 | 61.7263 | 61.5849 | 61.6255
6265.0625 | 123.3994 | -61.3998 | 61.6608 | -0.84419 | -3.525 | -0.88651 | 1.4859 | 4.1427 | -0.45009 | -4.7645 | 61.7294 | 0.23032 | 61.6561 | -0.033101 | 0.052814 | 61.5433 | 0.007721 | 61.326 | 60.5557 | 57.8748 | 60.5133 | 62.8857 | 65.5425 | 60.9498 | 56.6353 | 123.1292 | 61.6302 | 123.0559 | 61.3667 | 61.4527 | 122.9431 | 61.4076 | 122.7259 | 61.6766 | 61.7217 | 61.6032 | 61.6483
6266.1094 | 123.3765 | -61.4136 | 61.6379 | -0.7572 | -3.4426 | -0.79494 | 1.5408 | 4.1839 | -0.50045 | -4.7553 | 61.7157 | 0.21658 | 61.6332 | -0.033101 | 0.048236 | 61.5524 | 0.007721 | 61.3306 | 60.6564 | 57.971 | 60.6186 | 62.9544 | 65.5975 | 60.9131 | 56.6582 | 123.1292 | 61.6302 | 123.0467 | 61.3805 | 61.4618 | 122.966 | 61.4213 | 122.7442 | 61.6674 | 61.7079 | 61.5849 | 61.6255
6267.0625 | 123.4131 | -61.3953 | 61.6562 | -0.77551 | -3.2961 | -0.64385 | 1.6873 | 4.2709 | -0.45009 | -4.5905 | 61.7294 | 0.22574 | 61.6423 | -0.028522 | 0.052814 | 61.5616 | 0.007721 | 61.3352 | 60.6198 | 58.0992 | 60.7514 | 63.0826 | 65.6661 | 60.9452 | 56.8047 | 123.1247 | 61.621 | 123.0376 | 61.3667 | 61.4481 | 122.9568 | 61.403 | 122.7305 | 61.6766 | 61.7217 | 61.5895 | 61.6346
6268.0781 | 123.3673 | -61.4365 | 61.6333 | -0.78925 | -3.264 | -0.57517 | 1.724 | 4.248 | -0.40888 | -4.5585 | 61.7157 | 0.22574 | 61.6332 | -0.033101 | 0.043657 | 61.5616 | 0.007721 | 61.3352 | 60.6472 | 58.1725 | 60.8613 | 63.1604 | 65.6844 | 61.0276 | 56.878 | 123.1521 | 61.6622 | 123.0696 | 61.4034 | 61.4801 | 122.998 | 61.4442 | 122.7717 | 61.672 | 61.7079 | 61.5895 | 61.6255
6269.0625 | 123.4451 | -61.4044 | 61.6562 | -0.66105 | -3.1404 | -0.42865 | 1.8567 | 4.3853 | -0.2578 | -4.4349 | 61.7111 | 0.22116 | 61.6194 | -0.023943 | 0.057392 | 61.5707 | 0.007721 | 61.3443 | 60.7434 | 58.264 | 60.9758 | 63.2612 | 65.7897 | 61.1466 | 56.9695 | 123.1155 | 61.6256 | 123.0239 | 61.3805 | 61.4618 | 122.9752 | 61.4121 | 122.7488 | 61.6537 | 61.7034 | 61.562 | 61.6117
6270.0625 | 123.3078 | -61.4502 | 61.6837 | -0.61985 | -3.1175 | -0.3554 | 1.9208 | 4.4265 | -0.2349 | -4.4211 | 61.7111 | 0.22574 | 61.6286 | -0.023943 | 0.043657 | 61.5662 | 0.016878 | 61.3535 | 60.8303 | 58.3327 | 61.0948 | 63.371 | 65.8767 | 61.2153 | 57.0291 | 123.1613 | 61.6759 | 123.0788 | 61.4263 | 61.4939 | 123.0164 | 61.4671 | 122.8037 | 61.6674 | 61.6942 | 61.5849 | 61.6117
6271.1094 | 123.4314 | -61.4639 | 61.615 | -0.59696 | -3.0809 | -0.27756 | 2.0124 | 4.5089 | -0.28069 | -4.4166 | 61.7019 | 0.22116 | 61.6057 | -0.033101 | 0.048236 | 61.5662 | 0.003143 | 61.3443 | 60.867 | 58.3831 | 61.1864 | 63.4763 | 65.9729 | 61.1832 | 57.0474 | 123.1659 | 61.6851 | 123.0696 | 61.4308 | 61.5122 | 123.0301 | 61.4671 | 122.8083 | 61.6537 | 61.6988 | 61.5575 | 61.6026
6272.0625 | 123.4177 | -61.4136 | 61.6699 | -0.66563 | -3.1312 | -0.31877 | 2.0399 | 4.5044 | -0.31274 | -4.4761 | 61.7065 | 0.23032 | 61.6423 | -0.028522 | 0.052814 | 61.5753 | 0.007721 | 61.3489 | 60.7479 | 58.2824 | 61.0948 | 63.4535 | 65.9179 | 61.1008 | 56.9375 | 123.1201 | 61.6439 | 123.0559 | 61.3851 | 61.4664 | 122.9889 | 61.4213 | 122.7625 | 61.6537 | 61.6988 | 61.5895 | 61.6346
6273.0938 | 123.349 | -61.4639 | 61.6425 | -0.60153 | -2.9984 | -0.17683 | 2.1635 | 4.5959 | -0.24864 | -4.325 | 61.6973 | 0.22574 | 61.6057 | -0.033101 | 0.048236 | 61.5753 | 0.007721 | 61.3581 | 60.8624 | 58.4655 | 61.2871 | 63.6274 | 66.0598 | 61.2153 | 57.1389 | 123.1613 | 61.6897 | 123.0696 | 61.4308 | 61.5122 | 123.0392 | 61.4716 | 122.822 | 61.6491 | 61.6896 | 61.5575 | 61.598
6274.0625 | 123.3673 | -61.4365 | 61.647 | -0.59696 | -3.0076 | -0.19972 | 2.0948 | 4.4769 | -0.24406 | -4.3067 | 61.7111 | 0.22574 | 61.6423 | -0.03768 | 0.052814 | 61.5753 | 0.007721 | 61.3535 | 60.8395 | 58.4289 | 61.2367 | 63.5313 | 65.9133 | 61.1924 | 57.1298 | 123.1475 | 61.6622 | 123.0788 | 61.3988 | 61.4893 | 123.0118 | 61.4442 | 122.79 | 61.6583 | 61.7034 | 61.5895 | 61.6346
6275.0938 | 123.2666 | -61.4731 | 61.6974 | -0.61069 | -3.0763 | -0.24093 | 2.0765 | 4.4586 | -0.16623 | -4.3799 | 61.7019 | 0.22574 | 61.6103 | -0.023943 | 0.052814 | 61.5753 | 0.007721 | 61.3581 | 60.8624 | 58.3968 | 61.2322 | 63.5496 | 65.9317 | 61.3069 | 57.0931 | 123.175 | 61.6988 | 123.0834 | 61.4491 | 61.5259 | 123.0484 | 61.4808 | 122.8312 | 61.6491 | 61.6942 | 61.5575 | 61.6026
6276.0625 | 123.3124 | -61.4365 | 61.6974 | -0.61985 | -3.0259 | -0.19972 | 2.0994 | 4.3807 | -0.18912 | -4.3937 | 61.7157 | 0.2349 | 61.6561 | -0.028522 | 0.048236 | 61.5707 | 0.007721 | 61.3535 | 60.8166 | 58.4106 | 61.2367 | 63.5359 | 65.8172 | 61.2473 | 57.0428 | 123.1521 | 61.6714 | 123.0925 | 61.4079 | 61.4847 | 123.0072 | 61.4442 | 122.79 | 61.6674 | 61.7079 | 61.6078 | 61.6483
6277.0781 | 123.3398 | -61.4777 | 61.6104 | -0.4184 | -2.8473 | -0.012 | 2.2734 | 4.5547 | -0.074661 | -4.2472 | 61.6836 | 0.212 | 61.5965 | -0.023943 | 0.048236 | 61.5891 | 0.007721 | 61.3627 | 61.0593 | 58.6303 | 61.4657 | 63.751 | 66.0324 | 61.403 | 57.2305 | 123.1613 | 61.6897 | 123.0742 | 61.4537 | 61.5259 | 123.0667 | 61.4854 | 122.8403 | 61.6354 | 61.6759 | 61.5483 | 61.5888
6278.0625 | 123.3948 | -61.4319 | 61.6516 | -0.34057 | -2.7054 | 0.056679 | 2.31 | 4.5822 | -0.092974 | -4.1922 | 61.6928 | 0.22574 | 61.6332 | -0.033101 | 0.048236 | 61.5845 | 0.012299 | 61.3718 | 61.0913 | 58.7265 | 61.4886 | 63.7419 | 66.0141 | 61.3389 | 57.2397 | 123.1247 | 61.6576 | 123.0651 | 61.3988 | 61.4801 | 123.0164 | 61.4442 | 122.8037 | 61.6445 | 61.6805 | 61.5849 | 61.6209
6279.0781 | 123.4039 | -61.4868 | 61.6058 | -0.43213 | -2.742 | 0.029208 | 2.3466 | 4.5959 | -0.14334 | -4.2289 | 61.6973 | 0.22574 | 61.5828 | -0.028522 | 0.048236 | 61.5845 | 0.012299 | 61.3672 | 61.0547 | 58.7448 | 61.516 | 63.8335 | 66.0827 | 61.3435 | 57.258 | 123.1842 | 61.7126 | 123.0696 | 61.4583 | 61.5351 | 123.0713 | 61.4991 | 122.8541 | 61.6491 | 61.685 | 61.5346 | 61.5705
6280.0625 | 123.2758 | -61.4914 | 61.6608 | -0.50997 | -2.7558 | 0.001736 | 2.2963 | 4.5456 | -0.23948 | -4.2884 | 61.7019 | 0.2349 | 61.6286 | -0.023943 | 0.048236 | 61.5799 | 0.003143 | 61.3581 | 60.9814 | 58.7356 | 61.4931 | 63.7877 | 66.0369 | 61.2519 | 57.203 | 123.1933 | 61.7263 | 123.12 | 61.4675 | 61.5396 | 123.0713 | 61.4945 | 122.8495 | 61.6537 | 61.6988 | 61.5804 | 61.6255
6281.1094 | 123.381 | -61.4548 | 61.6333 | -0.45045 | -2.71 | 0.070415 | 2.4153 | 4.6829 | -0.12502 | -4.2197 | 61.6973 | 0.22116 | 61.5965 | -0.028522 | 0.043657 | 61.5936 | 0.012299 | 61.3672 | 61.0043 | 58.7448 | 61.5252 | 63.8701 | 66.1377 | 61.3298 | 57.2351 | 123.1521 | 61.6759 | 123.0513 | 61.4263 | 61.4984 | 123.0484 | 61.4671 | 122.822 | 61.6537 | 61.685 | 61.5529 | 61.5842
6282.0625 | 123.3032 | -61.441 | 61.6928 | -0.49623 | -2.7603 | 0.033786 | 2.3924 | 4.6371 | -0.1296 | -4.2792 | 61.6973 | 0.23032 | 61.6194 | -0.033101 | 0.052814 | 61.5845 | 0.021456 | 61.3672 | 60.9448 | 58.6807 | 61.4748 | 63.8335 | 66.0782 | 61.3114 | 57.1618 | 123.1384 | 61.6714 | 123.0605 | 61.4079 | 61.4939 | 123.0255 | 61.4625 | 122.8083 | 61.6445 | 61.6759 | 61.5666 | 61.598
6283.0781 | 123.3948 | -61.4777 | 61.6516 | -0.46418 | -2.7008 | 0.10704 | 2.4657 | 4.66 | -0.13876 | -4.2884 | 61.6882 | 0.22116 | 61.5965 | -0.033101 | 0.048236 | 61.5845 | 0.003143 | 61.3627 | 61.0135 | 58.7768 | 61.5847 | 63.9433 | 66.1377 | 61.3389 | 57.1893 | 123.1659 | 61.6988 | 123.0742 | 61.4446 | 61.5259 | 123.0621 | 61.4808 | 122.8403 | 61.64 | 61.685 | 61.5483 | 61.5934
6284.0625 | 123.3032 | -61.4914 | 61.6653 | -0.34057 | -2.5039 | 0.3726 | 2.6717 | 4.7928 | -0.038034 | -4.0595 | 61.679 | 0.22574 | 61.6011 | -0.028522 | 0.048236 | 61.5982 | 0.016878 | 61.3764 | 61.1508 | 58.9875 | 61.864 | 64.1631 | 66.2842 | 61.4534 | 57.4319 | 123.1704 | 61.7171 | 123.0925 | 61.4629 | 61.5396 | 123.0896 | 61.5083 | 122.8678 | 61.6308 | 61.6622 | 61.5529 | 61.5842
6285.0938 | 123.3994 | -61.4685 | 61.6058 | -0.19864 | -2.3482 | 0.53285 | 2.9144 | 5.1041 | 0.17257 | -3.9175 | 61.6699 | 0.22574 | 61.592 | -0.023943 | 0.043657 | 61.6074 | 0.012299 | 61.3947 | 61.2699 | 59.1203 | 62.0014 | 64.3829 | 66.5726 | 61.6411 | 57.551 | 123.1384 | 61.6942 | 123.0605 | 61.4446 | 61.5122 | 123.0759 | 61.4808 | 122.8632 | 61.6262 | 61.6576 | 61.5483 | 61.5797
6286.0625 | 123.2529 | -61.5097 | 61.6653 | -0.22611 | -2.3528 | 0.51454 | 2.7908 | 4.9072 | 0.11763 | -3.8992 | 61.6745 | 0.22116 | 61.5874 | -0.019364 | 0.052814 | 61.5982 | 0.007721 | 61.3901 | 61.2836 | 59.1569 | 62.0242 | 64.3005 | 66.4169 | 61.6273 | 57.6105 | 123.1842 | 61.7309 | 123.0971 | 61.4903 | 61.5625 | 123.1079 | 61.5174 | 122.8998 | 61.6216 | 61.6667 | 61.5346 | 61.5797
6287.0781 | 123.4085 | -61.4639 | 61.6333 | -0.15285 | -2.3895 | 0.48249 | 2.7679 | 4.9209 | 0.10848 | -3.9587 | 61.6745 | 0.22116 | 61.6057 | -0.028522 | 0.048236 | 61.6074 | 0.007721 | 61.3856 | 61.3111 | 59.0745 | 61.9464 | 64.2318 | 66.3849 | 61.5724 | 57.5052 | 123.1384 | 61.6851 | 123.0696 | 61.4354 | 61.5122 | 123.0713 | 61.4716 | 122.8495 | 61.6262 | 61.6667 | 61.5575 | 61.598
6288.0625 | 123.2849 | -61.5051 | 61.6653 | -0.10707 | -2.275 | 0.63358 | 2.9373 | 5.0629 | 0.19089 | -3.8489 | 61.6653 | 0.22574 | 61.5737 | -0.028522 | 0.048236 | 61.6119 | 0.007721 | 61.3993 | 61.3981 | 59.2301 | 62.1387 | 64.4424 | 66.568 | 61.696 | 57.6563 | 123.1704 | 61.7309 | 123.0788 | 61.4766 | 61.5534 | 123.1171 | 61.5128 | 122.9044 | 61.6171 | 61.6576 | 61.5254 | 61.5659
6289.0781 | 123.3765 | -61.4914 | 61.5738 | 0.085224 | -2.1285 | 0.81215 | 3.0746 | 5.2231 | 0.36029 | -3.7024 | 61.6607 | 0.22574 | 61.5965 | -0.028522 | 0.048236 | 61.6211 | 0.016878 | 61.3993 | 61.5766 | 59.3629 | 62.3035 | 64.566 | 66.7145 | 61.8517 | 57.789 | 123.1521 | 61.7171 | 123.0879 | 61.4629 | 61.5396 | 123.1125 | 61.5083 | 122.8907 | 61.6125 | 61.6438 | 61.5483 | 61.5797
6290.0625 | 123.2803 | -61.5097 | 61.6379 | 0.080646 | -2.0506 | 0.88999 | 3.1433 | 5.2322 | 0.51595 | -3.5971 | 61.647 | 0.22574 | 61.5508 | -0.023943 | 0.048236 | 61.6211 | 0.012299 | 61.4039 | 61.5904 | 59.4591 | 62.3997 | 64.653 | 66.742 | 62.0257 | 57.9126 | 123.1567 | 61.7354 | 123.0605 | 61.4858 | 61.5579 | 123.1308 | 61.522 | 122.9136 | 61.5987 | 61.6347 | 61.5025 | 61.5385
6291.1094 | 123.4085 | -61.4731 | 61.6058 | -0.11165 | -2.1559 | 0.77552 | 3.0426 | 5.0629 | 0.34655 | -3.7298 | 61.6653 | 0.23032 | 61.6057 | -0.023943 | 0.052814 | 61.6074 | 0.007721 | 61.3947 | 61.3614 | 59.3171 | 62.2486 | 64.5157 | 66.5359 | 61.8196 | 57.7432 | 123.1384 | 61.7034 | 123.0788 | 61.4491 | 61.5259 | 123.0804 | 61.4808 | 122.8678 | 61.6125 | 61.6576 | 61.5529 | 61.598
6292.0625 | 123.2941 | -61.4594 | 61.6608 | -0.28105 | -2.4169 | 0.53743 | 2.9052 | 4.9255 | 0.15426 | -4.0412 | 61.6745 | 0.22116 | 61.5737 | -0.028522 | 0.052814 | 61.6028 | 0.012299 | 61.3947 | 61.1783 | 59.0424 | 61.9968 | 64.3646 | 66.3849 | 61.6136 | 57.4182 | 123.1338 | 61.6805 | 123.033 | 61.4308 | 61.5122 | 123.0621 | 61.4716 | 122.8541 | 61.6216 | 61.6622 | 61.5208 | 61.5614
6293.0781 | 123.3948 | -61.4685 | 61.6241 | -0.097912 | -2.3391 | 0.61985 | 2.9693 | 5.0171 | 0.25956 | -3.9954 | 61.6745 | 0.22574 | 61.6103 | -0.028522 | 0.048236 | 61.6028 | 0.007721 | 61.3856 | 61.3706 | 59.1294 | 62.0884 | 64.4378 | 66.4856 | 61.7281 | 57.4731 | 123.143 | 61.6942 | 123.0788 | 61.44 | 61.5167 | 123.0713 | 61.4762 | 122.8541 | 61.6262 | 61.6667 | 61.562 | 61.6026
6294.0625 | 123.2437 | -61.4685 | 61.647 | -0.26273 | -2.481 | 0.47791 | 2.7999 | 4.8202 | 0.12221 | -4.1464 | 61.6836 | 0.22574 | 61.5874 | -0.028522 | 0.052814 | 61.6028 | 0.007721 | 61.3856 | 61.2058 | 58.9875 | 61.9464 | 64.2684 | 66.2887 | 61.5907 | 57.3221 | 123.1521 | 61.6942 | 123.0559 | 61.44 | 61.5213 | 123.0713 | 61.4762 | 122.8541 | 61.6308 | 61.6759 | 61.5346 | 61.5797
6295.0781 | 123.3307 | -61.5051 | 61.6333 | 0.094381 | -2.0048 | 0.96782 | 3.212 | 5.1865 | 0.51595 | -3.6566 | 61.6516 | 0.22574 | 61.5645 | -0.033101 | 0.048236 | 61.6257 | 0.003143 | 61.4268 | 61.5995 | 59.5003 | 62.4729 | 64.7171 | 66.6916 | 62.0211 | 57.8485 | 123.1567 | 61.7309 | 123.0696 | 61.472 | 61.5534 | 123.1308 | 61.5083 | 122.9319 | 61.6033 | 61.6484 | 61.5163 | 61.5614
6296.0625 | 123.3765 | -61.5143 | 61.5692 | 0.26836 | -1.8995 | 1.0548 | 3.157 | 5.0537 | 0.53426 | -3.5376 | 61.6516 | 0.23032 | 61.5874 | -0.033101 | 0.039079 | 61.6257 | 0.007721 | 61.4222 | 61.7826 | 59.6148 | 62.5691 | 64.6713 | 66.568 | 62.0485 | 57.9767 | 123.1658 | 61.7446 | 123.1017 | 61.4812 | 61.5534 | 123.14 | 61.522 | 122.9365 | 61.6125 | 61.6438 | 61.5483 | 61.5797
6297.0781 | 123.3856 | -61.4822 | 61.6196 | 0.10354 | -2.014 | 0.88999 | 3.0059 | 4.8248 | 0.35113 | -3.6657 | 61.6607 | 0.22574 | 61.5737 | -0.023943 | 0.052814 | 61.6211 | 0.012299 | 61.4084 | 61.5858 | 59.4682 | 62.3722 | 64.4882 | 66.307 | 61.8334 | 57.8165 | 123.143 | 61.708 | 123.0559 | 61.4583 | 61.5351 | 123.1033 | 61.4945 | 122.8907 | 61.6079 | 61.6484 | 61.5208 | 61.5614
6298.0625 | 123.2712 | -61.528 | 61.6104 | 0.007391 | -2.0735 | 0.82588 | 3.0151 | 4.8019 | 0.33282 | -3.7481 | 61.6653 | 0.21658 | 61.5691 | -0.023943 | 0.029923 | 61.6074 | 0.007721 | 61.3993 | 61.5354 | 59.4545 | 62.3539 | 64.5431 | 66.3299 | 61.8608 | 57.7799 | 123.1933 | 61.7446 | 123.0971 | 61.5041 | 61.5579 | 123.1354 | 61.5357 | 122.9273 | 61.6354 | 61.6576 | 61.5392 | 61.5614
6299.0938 | 123.2986 | -61.5051 | 61.6425 | 0.11727 | -1.9636 | 1.0411 | 3.2715 | 5.0949 | 0.53884 | -3.5879 | 61.6561 | 0.23032 | 61.5828 | -0.033101 | 0.052814 | 61.6211 | 0.016878 | 61.4084 | 61.6224 | 59.5415 | 62.5462 | 64.7766 | 66.6 | 62.044 | 57.9172 | 123.1613 | 61.7354 | 123.0879 | 61.472 | 61.5579 | 123.1262 | 61.522 | 122.9136 | 61.6033 | 61.6393 | 61.53 | 61.5659
6300.0625 | 123.3215 | -61.5189 | 61.6196 | 0.094381 | -1.9682 | 1.0502 | 3.2486 | 4.9988 | 0.51595 | -3.5879 | 61.6516 | 0.22116 | 61.5645 | -0.033101 | 0.052814 | 61.6257 | 0.007721 | 61.4176 | 61.6132 | 59.5507 | 62.5691 | 64.7675 | 66.5176 | 62.0348 | 57.9309 | 123.1704 | 61.74 | 123.0834 | 61.4858 | 61.5717 | 123.1445 | 61.5266 | 122.9365 | 61.5987 | 61.6438 | 61.5117 | 61.5568
6301.1094 | 123.3032 | -61.5051 | 61.6241 | 0.021127 | -2.0506 | 1.0045 | 3.2074 | 4.9484 | 0.52511 | -3.6291 | 61.6516 | 0.22574 | 61.5645 | -0.028522 | 0.052814 | 61.6211 | 0.012299 | 61.4039 | 61.5263 | 59.4545 | 62.5096 | 64.7125 | 66.4535 | 62.0302 | 57.876 | 123.1567 | 61.7309 | 123.0696 | 61.4766 | 61.5579 | 123.1262 | 61.5174 | 122.909 | 61.5987 | 61.6393 | 61.5117 | 61.5522
6302.0625 | 123.2574 | -61.5189 | 61.6241 | -0.056706 | -2.1468 | 0.93577 | 3.1387 | 4.9026 | 0.43812 | -3.7756 | 61.6653 | 0.2349 | 61.6103 | -0.033101 | 0.043657 | 61.6165 | 0.007721 | 61.3947 | 61.4622 | 59.3721 | 62.4546 | 64.6576 | 66.4215 | 61.957 | 57.7432 | 123.1842 | 61.7538 | 123.1291 | 61.4858 | 61.5625 | 123.1354 | 61.5266 | 122.9136 | 61.6216 | 61.6576 | 61.5666 | 61.6026
6303.0781 | 123.2483 | -61.5005 | 61.6379 | -0.052128 | -2.0781 | 0.89914 | 3.125 | 4.8797 | 0.35113 | -3.7756 | 61.6607 | 0.22116 | 61.5645 | -0.028522 | 0.043657 | 61.6119 | 0.012299 | 61.3993 | 61.4484 | 59.4225 | 62.3997 | 64.6255 | 66.3803 | 61.8517 | 57.7249 | 123.1613 | 61.7217 | 123.065 | 61.472 | 61.5442 | 123.1125 | 61.5128 | 122.8998 | 61.6171 | 61.6484 | 61.5208 | 61.5522
6304.0625 | 123.23 | -61.5601 | 61.6287 | 0.089802 | -1.9819 | 0.99987 | 3.2532 | 5.0217 | 0.41523 | -3.7207 | 61.6561 | 0.23032 | 61.5691 | -0.014785 | 0.039079 | 61.6211 | 0.007721 | 61.4039 | 61.6499 | 59.5781 | 62.5599 | 64.8132 | 66.5817 | 61.9753 | 57.8394 | 123.2162 | 61.7904 | 123.1291 | 61.5453 | 61.5991 | 123.1812 | 61.5678 | 122.9639 | 61.6171 | 61.6484 | 61.53 | 61.5614
6305.0938 | 123.2803 | -61.4868 | 61.6562 | -0.042971 | -2.1468 | 0.84878 | 3.125 | 4.8477 | 0.28245 | -3.8992 | 61.6607 | 0.23032 | 61.5737 | -0.023943 | 0.048236 | 61.6165 | 0.012299 | 61.3993 | 61.4438 | 59.34 | 62.3356 | 64.6118 | 66.3345 | 61.7693 | 57.5876 | 123.1475 | 61.7171 | 123.0605 | 61.4629 | 61.5351 | 123.1033 | 61.4991 | 122.8861 | 61.6125 | 61.6484 | 61.5254 | 61.5614
6306.0625 | 123.4039 | -61.4822 | 61.5463 | 0.021127 | -2.0369 | 0.97698 | 3.2532 | 4.9301 | 0.41065 | -3.7436 | 61.6561 | 0.22116 | 61.5737 | -0.033101 | 0.048236 | 61.6257 | 0.003143 | 61.4084 | 61.5034 | 59.4454 | 62.4592 | 64.7354 | 66.4123 | 61.8929 | 57.7387 | 123.1384 | 61.7034 | 123.0559 | 61.4491 | 61.5305 | 123.1079 | 61.4854 | 122.8907 | 61.6079 | 61.653 | 61.5254 | 61.5705
6307.0938 | 123.2986 | -61.4868 | 61.6425 | 0.19053 | -1.8492 | 1.2059 | 3.418 | 5.04 | 0.57547 | -3.5421 | 61.647 | 0.23032 | 61.5737 | -0.028522 | 0.052814 | 61.6211 | 0.007721 | 61.4176 | 61.6773 | 59.6377 | 62.6927 | 64.9048 | 66.5268 | 62.0623 | 57.9447 | 123.1338 | 61.7171 | 123.0605 | 61.4583 | 61.5396 | 123.1079 | 61.4945 | 122.9044 | 61.5942 | 61.6393 | 61.5208 | 61.5659
6308.0625 | 123.2391 | -61.5372 | 61.5967 | 0.10354 | -1.9362 | 1.1464 | 3.3997 | 5.0354 | 0.49764 | -3.6703 | 61.6378 | 0.22116 | 61.5599 | -0.028522 | 0.048236 | 61.6303 | 0.003143 | 61.413 | 61.6407 | 59.601 | 62.6836 | 64.9369 | 66.5726 | 62.0348 | 57.8669 | 123.175 | 61.7583 | 123.0971 | 61.5086 | 61.5854 | 123.1674 | 61.5403 | 122.9502 | 61.5896 | 61.6347 | 61.5117 | 61.5568
6309.0781 | 123.3124 | -61.5051 | 61.6058 | 0.218 | -1.8171 | 1.2837 | 3.505 | 5.1086 | 0.63041 | -3.533 | 61.6424 | 0.2349 | 61.5737 | -0.019364 | 0.048236 | 61.6303 | 0.016878 | 61.4268 | 61.7231 | 59.688 | 62.7889 | 65.0101 | 66.6138 | 62.1355 | 57.9722 | 123.1475 | 61.74 | 123.0788 | 61.4858 | 61.5534 | 123.1354 | 61.522 | 122.9319 | 61.5942 | 61.6255 | 61.5254 | 61.5568
6310.0625 | 123.2666 | -61.5372 | 61.6013 | 0.28667 | -1.6889 | 1.3662 | 3.5599 | 5.1178 | 0.65788 | -3.4368 | 61.6287 | 0.22116 | 61.5462 | -0.028522 | 0.043657 | 61.6348 | 0.003143 | 61.4268 | 61.8238 | 59.8483 | 62.9033 | 65.0971 | 66.655 | 62.1951 | 58.1003 | 123.1658 | 61.7583 | 123.0834 | 61.5086 | 61.5808 | 123.172 | 61.5403 | 122.9639 | 61.585 | 61.6255 | 61.5025 | 61.543
6311.0938 | 123.2391 | -61.528 | 61.6608 | 0.20426 | -1.8034 | 1.2746 | 3.5279 | 5.0766 | 0.548 | -3.6383 | 61.6561 | 0.2349 | 61.5782 | -0.028522 | 0.043657 | 61.6257 | 0.016878 | 61.4176 | 61.7323 | 59.7247 | 62.8026 | 65.0559 | 66.6046 | 62.076 | 57.8897 | 123.1842 | 61.7629 | 123.1062 | 61.4995 | 61.5717 | 123.1537 | 61.5449 | 122.9456 | 61.6125 | 61.6393 | 61.5346 | 61.5614
6312.0625 | 123.2849 | -61.5326 | 61.6196 | 0.030283 | -2.0506 | 1.064 | 3.331 | 4.8569 | 0.39691 | -3.8718 | 61.6516 | 0.21658 | 61.5553 | -0.028522 | 0.052814 | 61.6119 | 0.007721 | 61.3993 | 61.5629 | 59.482 | 62.5966 | 64.8636 | 66.3894 | 61.9295 | 57.6608 | 123.1842 | 61.7492 | 123.0879 | 61.5041 | 61.5854 | 123.1445 | 61.5403 | 122.9319 | 61.5987 | 61.6438 | 61.5025 | 61.5476
6313.0781 | 123.2437 | -61.5326 | 61.6241 | 0.03944 | -2.101 | 1.0273 | 3.3356 | 4.866 | 0.59378 | -3.913 | 61.6653 | 0.23032 | 61.6011 | -0.033101 | 0.043657 | 61.6165 | 0.007721 | 61.4084 | 61.572 | 59.4316 | 62.5599 | 64.8682 | 66.3986 | 62.1264 | 57.6196 | 123.1979 | 61.7629 | 123.1337 | 61.4995 | 61.5763 | 123.1491 | 61.5403 | 122.941 | 61.6216 | 61.6576 | 61.5575 | 61.5934
6314.0625 | 123.2437 | -61.5601 | 61.615 | 0.20426 | -1.8263 | 1.2425 | 3.5371 | 5.0812 | 0.73571 | -3.7619 | 61.647 | 0.23032 | 61.5416 | -0.033101 | 0.052814 | 61.6257 | 0.007721 | 61.4176 | 61.7643 | 59.7338 | 62.8026 | 65.0971 | 66.6412 | 62.2958 | 57.7982 | 123.207 | 61.7904 | 123.1017 | 61.527 | 61.6129 | 123.1857 | 61.5678 | 122.9777 | 61.5942 | 61.6393 | 61.4888 | 61.5339
6315.0938 | 123.2986 | -61.5051 | 61.6241 | 0.16764 | -1.8858 | 1.1968 | 3.473 | 5.0217 | 0.67619 | -3.8626 | 61.6561 | 0.2349 | 61.5874 | -0.023943 | 0.052814 | 61.6257 | 0.007721 | 61.413 | 61.6728 | 59.6193 | 62.7019 | 64.9781 | 66.5268 | 62.1813 | 57.6425 | 123.1613 | 61.74 | 123.0925 | 61.4812 | 61.5579 | 123.1308 | 61.5128 | 122.9181 | 61.6033 | 61.6484 | 61.5346 | 61.5797
6316.0625 | 123.3536 | -61.5189 | 61.6013 | 0.30041 | -1.7255 | 1.3616 | 3.6607 | 5.2094 | 0.77692 | -3.8077 | 61.6378 | 0.22574 | 61.5279 | -0.033101 | 0.052814 | 61.6348 | 0.007721 | 61.4222 | 61.8193 | 59.7933 | 62.8804 | 65.1795 | 66.7282 | 62.2958 | 57.7112 | 123.1567 | 61.7446 | 123.0467 | 61.4858 | 61.5717 | 123.1537 | 61.5266 | 122.941 | 61.585 | 61.6301 | 61.4751 | 61.5202
6317.0781 | 123.262 | -61.5326 | 61.647 | 0.35077 | -1.6339 | 1.4715 | 3.7431 | 5.2368 | 0.8227 | -3.6428 | 61.6332 | 0.2349 | 61.5737 | -0.023943 | 0.052814 | 61.6394 | 0.007721 | 61.4313 | 61.8834 | 59.8986 | 63.0041 | 65.2757 | 66.7694 | 62.3553 | 57.8897 | 123.1658 | 61.7675 | 123.1062 | 61.5086 | 61.5854 | 123.172 | 61.5403 | 122.9639 | 61.5804 | 61.6255 | 61.5208 | 61.5659
6318.0625 | 123.2391 | -61.5692 | 61.5875 | 0.37366 | -1.5882 | 1.531 | 3.8392 | 5.3421 | 0.93258 | -3.5833 | 61.6287 | 0.22574 | 61.537 | -0.023943 | 0.048236 | 61.644 | 0.007721 | 61.4405 | 61.9429 | 59.9811 | 63.1002 | 65.4084 | 66.9113 | 62.5018 | 57.9859 | 123.1979 | 61.795 | 123.1062 | 61.5453 | 61.6175 | 123.2132 | 61.5769 | 123.0097 | 61.5804 | 61.6209 | 61.4888 | 61.5293
6319.0781 | 123.2117 | -61.5189 | 61.6333 | 0.46065 | -1.4828 | 1.6455 | 3.8896 | 5.3604 | 0.99668 | -3.4918 | 61.6332 | 0.23032 | 61.5553 | -0.023943 | 0.052814 | 61.6486 | 0.007721 | 61.4496 | 61.9795 | 60.036 | 63.1643 | 65.4085 | 66.8793 | 62.5155 | 58.0271 | 123.1521 | 61.7492 | 123.0742 | 61.4949 | 61.5717 | 123.1674 | 61.5266 | 122.9685 | 61.5804 | 61.6255 | 61.5025 | 61.5476
6320.0625 | 123.2346 | -61.5509 | 61.6058 | 0.33246 | -1.5973 | 1.5264 | 3.7477 | 5.1636 | 0.84102 | -3.62 | 61.6332 | 0.23032 | 61.5462 | -0.033101 | 0.048236 | 61.6394 | 0.003143 | 61.4313 | 61.8834 | 59.9536 | 63.0773 | 65.2986 | 66.7145 | 62.3919 | 57.9309 | 123.1842 | 61.7812 | 123.0971 | 61.5178 | 61.5991 | 123.1903 | 61.554 | 122.9822 | 61.585 | 61.6301 | 61.4979 | 61.543
6321.0938 | 123.3398 | -61.4868 | 61.6791 | 0.34161 | -1.5927 | 1.5173 | 3.7431 | 5.1407 | 0.89138 | -3.5879 | 61.6332 | 0.2349 | 61.5737 | -0.023943 | 0.052814 | 61.6394 | 0.012299 | 61.4313 | 61.8284 | 59.8941 | 63.0041 | 65.2299 | 66.6275 | 62.3782 | 57.8989 | 123.1201 | 61.7217 | 123.0605 | 61.4629 | 61.5396 | 123.1262 | 61.4991 | 122.9182 | 61.5804 | 61.6209 | 61.5208 | 61.5614
6322.0625 | 123.2758 | -61.5463 | 61.6104 | 0.33703 | -1.6156 | 1.5173 | 3.7843 | 5.2002 | 0.89596 | -3.5879 | 61.6287 | 0.22116 | 61.537 | -0.033101 | 0.057392 | 61.6486 | 0.012299 | 61.4222 | 61.8834 | 59.9307 | 63.0636 | 65.3306 | 66.7465 | 62.4423 | 57.9584 | 123.175 | 61.7675 | 123.0834 | 61.5132 | 61.6037 | 123.1949 | 61.5586 | 122.9685 | 61.5713 | 61.6164 | 61.4796 | 61.5247
6323.0781 | 123.3078 | -61.5326 | 61.6241 | 0.43318 | -1.4874 | 1.6775 | 3.885 | 5.2048 | 1.0379 | -3.4597 | 61.6287 | 0.2349 | 61.5645 | -0.023943 | 0.052814 | 61.6486 | 0.007721 | 61.4405 | 61.9658 | 60.0452 | 63.2101 | 65.4176 | 66.7374 | 62.5705 | 58.0729 | 123.1613 | 61.7675 | 123.0971 | 61.5086 | 61.5854 | 123.1812 | 61.5403 | 122.9731 | 61.5759 | 61.6209 | 61.5117 | 61.5568
6324.0625 | 123.2391 | -61.5555 | 61.6058 | 0.12643 | -1.8537 | 1.3204 | 3.5828 | 4.9621 | 0.67162 | -3.8718 | 61.6424 | 0.23032 | 61.5599 | -0.033101 | 0.052814 | 61.6303 | 0.007721 | 61.4222 | 61.6819 | 59.7017 | 62.8759 | 65.1383 | 66.5176 | 62.2271 | 57.6837 | 123.1979 | 61.7858 | 123.1154 | 61.5224 | 61.6083 | 123.1857 | 61.5632 | 122.9777 | 61.5896 | 61.6347 | 61.5071 | 61.5522
6325.0781 | 123.3444 | -61.4868 | 61.6287 | 0.098959 | -1.8904 | 1.2563 | 3.5416 | 4.8981 | 0.59836 | -3.9999 | 61.6516 | 0.22574 | 61.5508 | -0.019364 | 0.057392 | 61.6257 | 0.016878 | 61.4176 | 61.5858 | 59.5965 | 62.7431 | 65.0284 | 66.3849 | 62.0852 | 57.4869 | 123.1384 | 61.7126 | 123.0376 | 61.4675 | 61.5442 | 123.1125 | 61.5037 | 122.9044 | 61.5942 | 61.6347 | 61.4934 | 61.5339
6326.0625 | 123.3353 | -61.5005 | 61.5738 | 0.14932 | -1.8766 | 1.2563 | 3.5783 | 4.9805 | 0.55716 | -4.0045 | 61.647 | 0.23032 | 61.5874 | -0.028522 | 0.048236 | 61.6303 | 0.012299 | 61.4084 | 61.6499 | 59.6239 | 62.7568 | 65.0788 | 66.481 | 62.0577 | 57.496 | 123.1475 | 61.7309 | 123.0879 | 61.472 | 61.5488 | 123.1308 | 61.5128 | 122.909 | 61.5987 | 61.6347 | 61.5392 | 61.5751
6327.0781 | 123.317 | -61.4914 | 61.6287 | 0.18595 | -1.7988 | 1.3433 | 3.624 | 4.953 | 0.59836 | -3.8946 | 61.647 | 0.21658 | 61.5553 | -0.023943 | 0.048236 | 61.6348 | 0.003143 | 61.4176 | 61.6773 | 59.6926 | 62.8347 | 65.1154 | 66.4444 | 62.0898 | 57.5967 | 123.1384 | 61.708 | 123.0467 | 61.4675 | 61.5396 | 123.1262 | 61.4945 | 122.909 | 61.5987 | 61.6438 | 61.5071 | 61.5522
6328.0625 | 123.2849 | -61.5646 | 61.5784 | 0.57511 | -1.3272 | 1.8606 | 4.1643 | 5.4657 | 1.1157 | -3.4002 | 61.6241 | 0.22574 | 61.5279 | -0.028522 | 0.043657 | 61.6577 | 0.007721 | 61.4359 | 62.1397 | 60.2375 | 63.4253 | 65.7289 | 67.0304 | 62.6804 | 58.1644 | 123.1887 | 61.7904 | 123.0925 | 61.5361 | 61.6083 | 123.2224 | 61.5724 | 123.0005 | 61.5804 | 61.6164 | 61.4842 | 61.5202
6329.0938 | 123.262 | -61.5463 | 61.5921 | 0.64837 | -1.2219 | 1.9431 | 4.2696 | 5.5481 | 1.2439 | -3.3178 | 61.6058 | 0.23032 | 61.5187 | -0.023943 | 0.048236 | 61.6623 | 0.016878 | 61.4451 | 62.1947 | 60.3245 | 63.4894 | 65.8159 | 67.0945 | 62.7902 | 58.2285 | 123.1521 | 61.7766 | 123.065 | 61.5224 | 61.5946 | 123.2086 | 61.5632 | 122.9914 | 61.5575 | 61.5889 | 61.4705 | 61.5018
6330.0625 | 123.2437 | -61.5646 | 61.5875 | 0.57053 | -1.2631 | 1.8698 | 4.1735 | 5.3513 | 1.1661 | -3.4094 | 61.6149 | 0.22574 | 61.5324 | -0.028522 | 0.052814 | 61.6486 | 0.012299 | 61.4405 | 62.1352 | 60.3016 | 63.4344 | 65.7381 | 66.9159 | 62.7307 | 58.1553 | 123.1796 | 61.7904 | 123.0971 | 61.5361 | 61.6174 | 123.2132 | 61.5769 | 123.0051 | 61.5621 | 61.6026 | 61.4796 | 61.5202
6331.0938 | 123.3673 | -61.5234 | 61.5463 | 0.51559 | -1.3592 | 1.8011 | 4.1277 | 5.3513 | 1.2164 | -3.4506 | 61.6195 | 0.22116 | 61.5416 | -0.028522 | 0.043657 | 61.6486 | 0.003143 | 61.4405 | 62.039 | 60.1642 | 63.3246 | 65.6511 | 66.8747 | 62.7399 | 58.0729 | 123.1429 | 61.7446 | 123.065 | 61.4949 | 61.5671 | 123.172 | 61.5266 | 122.9639 | 61.5759 | 61.6164 | 61.4979 | 61.5385
6332.0625 | 123.2895 | -61.5829 | 61.5875 | 0.58427 | -1.3043 | 1.8561 | 4.2009 | 5.4474 | 1.221 | -3.446 | 61.6149 | 0.22116 | 61.5279 | -0.033101 | 0.039079 | 61.6623 | 0.012299 | 61.4405 | 62.1672 | 60.2787 | 63.439 | 65.7839 | 67.0304 | 62.804 | 58.137 | 123.1979 | 61.8041 | 123.1108 | 61.5498 | 61.622 | 123.2452 | 61.5952 | 123.0234 | 61.5759 | 61.6026 | 61.4888 | 61.5156
6333.0781 | 123.2803 | -61.5509 | 61.6058 | 0.65752 | -1.2035 | 1.9797 | 4.2696 | 5.4932 | 1.3675 | -3.3041 | 61.6149 | 0.22574 | 61.5462 | -0.023943 | 0.048236 | 61.6623 | 0.012299 | 61.4542 | 62.2084 | 60.3474 | 63.5306 | 65.8205 | 67.0441 | 62.9184 | 58.2468 | 123.1658 | 61.7766 | 123.0971 | 61.527 | 61.5991 | 123.2132 | 61.5632 | 123.0051 | 61.5667 | 61.6026 | 61.4979 | 61.5339
6334.0625 | 123.23 | -61.5738 | 61.5738 | 0.89102 | -0.96086 | 2.2453 | 4.5535 | 5.7541 | 1.6468 | -3.0752 | 61.6012 | 0.22574 | 61.505 | -0.033101 | 0.052814 | 61.676 | 0.012299 | 61.4725 | 62.4648 | 60.6129 | 63.819 | 66.1273 | 67.3279 | 63.2206 | 58.4986 | 123.175 | 61.7995 | 123.0788 | 61.5407 | 61.6266 | 123.2498 | 61.5861 | 123.0463 | 61.5484 | 61.5889 | 61.4522 | 61.4927
6335.0781 | 123.2803 | -61.5692 | 61.6013 | 0.74909 | -1.1257 | 2.0758 | 4.3612 | 5.4795 | 1.4133 | -3.2537 | 61.6104 | 0.2349 | 61.5508 | -0.023943 | 0.052814 | 61.6715 | 0.016878 | 61.4542 | 62.3183 | 60.4435 | 63.6451 | 65.9304 | 67.0487 | 62.9825 | 58.3155 | 123.1796 | 61.8041 | 123.12 | 61.5453 | 61.622 | 123.2407 | 61.5861 | 123.0234 | 61.5575 | 61.5935 | 61.4979 | 61.5339
6336.0625 | 123.4131 | -61.5051 | 61.5601 | 0.67126 | -1.2219 | 1.9522 | 4.2376 | 5.3787 | 1.3401 | -3.3361 | 61.6058 | 0.22574 | 61.5187 | -0.033101 | 0.043657 | 61.6623 | 0.007721 | 61.4405 | 62.1764 | 60.2833 | 63.4573 | 65.7427 | 66.8839 | 62.8452 | 58.169 | 123.1109 | 61.7309 | 123.0238 | 61.472 | 61.5488 | 123.1674 | 61.5128 | 122.9456 | 61.5621 | 61.5981 | 61.4751 | 61.511
6337.0938 | 123.2895 | -61.5189 | 61.5875 | 0.63005 | -1.2905 | 1.9019 | 4.2238 | 5.3879 | 1.3309 | -3.3727 | 61.6195 | 0.2349 | 61.5599 | -0.023943 | 0.048236 | 61.6623 | 0.007721 | 61.4359 | 62.1489 | 60.2283 | 63.4207 | 65.7427 | 66.9068 | 62.8498 | 58.1461 | 123.1384 | 61.7538 | 123.0788 | 61.4949 | 61.5671 | 123.1812 | 61.5266 | 122.9548 | 61.5713 | 61.6118 | 61.5117 | 61.5522
6338.0625 | 123.2574 | -61.6196 | 61.5555 | 0.62547 | -1.2997 | 1.8927 | 4.2284 | 5.3604 | 1.3492 | -3.3773 | 61.6195 | 0.21658 | 61.5141 | -0.028522 | 0.048236 | 61.6577 | 0.007721 | 61.4405 | 62.245 | 60.3199 | 63.5123 | 65.848 | 66.98 | 62.9688 | 58.2423 | 123.2391 | 61.8362 | 123.1337 | 61.591 | 61.6678 | 123.2773 | 61.6273 | 123.0601 | 61.5713 | 61.6118 | 61.4659 | 61.5064
6339.0938 | 123.3398 | -61.5372 | 61.5646 | 0.63463 | -1.2356 | 1.9522 | 4.265 | 5.3604 | 1.3813 | -3.327 | 61.6195 | 0.23032 | 61.5553 | -0.023943 | 0.039079 | 61.6577 | 0.007721 | 61.4496 | 62.1718 | 60.3016 | 63.4894 | 65.8022 | 66.8976 | 62.9184 | 58.2102 | 123.1567 | 61.7675 | 123.0925 | 61.5132 | 61.5762 | 123.1949 | 61.5449 | 122.9868 | 61.5804 | 61.6118 | 61.5163 | 61.5476
6340.0625 | 123.4085 | -61.5234 | 61.5189 | 0.68499 | -1.1532 | 2.0575 | 4.3612 | 5.4291 | 1.4179 | -3.2583 | 61.6058 | 0.21658 | 61.5096 | -0.023943 | 0.048236 | 61.6715 | 0.012299 | 61.4588 | 62.2084 | 60.3703 | 63.581 | 65.8846 | 66.9525 | 62.9413 | 58.2652 | 123.1292 | 61.74 | 123.033 | 61.4995 | 61.5717 | 123.1949 | 61.5357 | 122.9822 | 61.5575 | 61.5935 | 61.4613 | 61.4973
6341.1094 | 123.3627 | -61.5509 | 61.5005 | 0.73993 | -1.0433 | 2.1537 | 4.3841 | 5.3925 | 1.5049 | -3.0752 | 61.6058 | 0.22116 | 61.5416 | -0.028522 | 0.052814 | 61.6715 | 0.012299 | 61.4542 | 62.2908 | 60.5076 | 63.7046 | 65.935 | 66.9434 | 63.0558 | 58.4757 | 123.1567 | 61.7721 | 123.0925 | 61.5224 | 61.6037 | 123.2224 | 61.5632 | 123.0051 | 61.553 | 61.5935 | 61.4888 | 61.5293
6342.0625 | 123.317 | -61.5784 | 61.5555 | 0.71704 | -1.0662 | 2.1445 | 4.4482 | 5.4932 | 1.5186 | -3.1301 | 61.6058 | 0.22574 | 61.5096 | -0.033101 | 0.048236 | 61.6715 | 0.012299 | 61.4634 | 62.2954 | 60.5122 | 63.7229 | 66.0265 | 67.0716 | 63.097 | 58.4483 | 123.1841 | 61.8041 | 123.0879 | 61.5453 | 61.6266 | 123.2498 | 61.5907 | 123.0418 | 61.5575 | 61.5935 | 61.4613 | 61.4973
6343.0938 | 123.3994 | -61.5326 | 61.5005 | 0.7262 | -1.0799 | 2.1033 | 4.4161 | 5.4337 | 1.4499 | -3.2079 | 61.6058 | 0.22574 | 61.5324 | -0.033101 | 0.043657 | 61.6669 | 0.012299 | 61.4496 | 62.2588 | 60.4527 | 63.6359 | 65.9487 | 66.9663 | 62.9825 | 58.3247 | 123.1384 | 61.7583 | 123.065 | 61.4995 | 61.5763 | 123.1995 | 61.5449 | 122.9822 | 61.5621 | 61.5935 | 61.4888 | 61.5202
6344.0625 | 123.3627 | -61.5555 | 61.5143 | 0.84981 | -0.92881 | 2.2407 | 4.5168 | 5.4886 | 1.6148 | -3.0385 | 61.5966 | 0.22116 | 61.5279 | -0.019364 | 0.052814 | 61.6806 | 0.007721 | 61.4588 | 62.4053 | 60.6267 | 63.7962 | 66.0723 | 67.0441 | 63.1702 | 58.517 | 123.1521 | 61.7766 | 123.0834 | 61.5361 | 61.6083 | 123.2361 | 61.5632 | 123.0143 | 61.5438 | 61.5889 | 61.4751 | 61.5202
6345.0781 | 123.3215 | -61.5372 | 61.5646 | 0.67584 | -1.0891 | 2.0804 | 4.32 | 5.2597 | 1.3034 | -3.2445 | 61.6195 | 0.22116 | 61.5187 | -0.019364 | 0.043657 | 61.6715 | 0.007721 | 61.4496 | 62.213 | 60.4481 | 63.6176 | 65.8571 | 66.7969 | 62.8406 | 58.2926 | 123.1567 | 61.7583 | 123.0559 | 61.5178 | 61.5808 | 123.2086 | 61.5449 | 122.9868 | 61.5759 | 61.6118 | 61.4751 | 61.511
6346.0625 | 123.2803 | -61.5875 | 61.5555 | 0.81319 | -0.96086 | 2.1995 | 4.494 | 5.4062 | 1.5552 | -3.1209 | 61.6058 | 0.23032 | 61.5416 | -0.023943 | 0.048236 | 61.6715 | 0.003143 | 61.4542 | 62.4007 | 60.6267 | 63.787 | 66.0815 | 66.9937 | 63.1428 | 58.4666 | 123.1933 | 61.8178 | 123.1291 | 61.5636 | 61.6358 | 123.259 | 61.5907 | 123.0418 | 61.5575 | 61.6026 | 61.4934 | 61.5385
6347.0781 | 123.3078 | -61.5738 | 61.5738 | 0.80403 | -0.95628 | 2.1812 | 4.4802 | 5.4154 | 1.4133 | -3.1484 | 61.6058 | 0.2349 | 61.505 | -0.023943 | 0.048236 | 61.6669 | 0.003143 | 61.4588 | 62.3778 | 60.6175 | 63.7549 | 66.054 | 66.9892 | 62.9871 | 58.4254 | 123.1796 | 61.8087 | 123.0788 | 61.5498 | 61.622 | 123.2407 | 61.5769 | 123.0326 | 61.5575 | 61.6026 | 61.4567 | 61.5018
6348.0625 | 123.317 | -61.5692 | 61.5463 | 0.77198 | -1.0021 | 2.1445 | 4.4161 | 5.3375 | 1.4133 | -3.1942 | 61.6012 | 0.22574 | 61.5141 | -0.023943 | 0.043657 | 61.6715 | 0.012299 | 61.4542 | 62.3412 | 60.5671 | 63.7137 | 65.9853 | 66.9068 | 62.9825 | 58.375 | 123.1704 | 61.795 | 123.0833 | 61.5453 | 61.6129 | 123.2407 | 61.5815 | 123.0234 | 61.5575 | 61.5889 | 61.4705 | 61.5018
6349.0781 | 123.3032 | -61.5463 | 61.5875 | 0.71704 | -1.057 | 2.0621 | 4.3291 | 5.246 | 1.4133 | -3.2217 | 61.6149 | 0.2349 | 61.5462 | -0.033101 | 0.048236 | 61.6623 | 0.012299 | 61.4496 | 62.2634 | 60.4893 | 63.6084 | 65.8755 | 66.7923 | 62.9596 | 58.3247 | 123.1613 | 61.7812 | 123.0925 | 61.5132 | 61.5946 | 123.2086 | 61.5586 | 122.996 | 61.5667 | 61.6026 | 61.4979 | 61.5339
6350.0625 | 123.4177 | -61.5417 | 61.528 | 0.66668 | -1.1165 | 2.0117 | 4.2559 | 5.1956 | 1.395 | -3.2629 | 61.6058 | 0.22116 | 61.5141 | -0.023943 | 0.048236 | 61.6623 | 0.003143 | 61.4405 | 62.2084 | 60.4252 | 63.5535 | 65.7976 | 66.7374 | 62.9367 | 58.2789 | 123.1475 | 61.7629 | 123.0559 | 61.5178 | 61.59 | 123.204 | 61.5449 | 122.9822 | 61.5575 | 61.6026 | 61.4659 | 61.511
6351.1094 | 123.3627 | -61.5417 | 61.5005 | 0.63005 | -1.144 | 1.9934 | 4.2376 | 5.0903 | 1.3721 | -3.2858 | 61.6104 | 0.22116 | 61.5233 | -0.03768 | 0.043657 | 61.6669 | 0.016878 | 61.4405 | 62.1718 | 60.3977 | 63.5352 | 65.7793 | 66.6321 | 62.9139 | 58.256 | 123.1521 | 61.7629 | 123.065 | 61.5041 | 61.5854 | 123.2086 | 61.5586 | 122.9822 | 61.5667 | 61.5935 | 61.4796 | 61.5064
6352.0625 | 123.3536 | -61.5417 | 61.5326 | 0.598 | -1.1715 | 1.9385 | 4.1139 | 4.9209 | 1.2714 | -3.3361 | 61.6241 | 0.23032 | 61.5645 | -0.028522 | 0.048236 | 61.6577 | 0.007721 | 61.4359 | 62.1398 | 60.3703 | 63.4802 | 65.6557 | 66.4627 | 62.8131 | 58.2056 | 123.1658 | 61.7721 | 123.1062 | 61.5132 | 61.59 | 123.1995 | 61.5495 | 122.9777 | 61.5759 | 61.6164 | 61.5163 | 61.5568
6353.0938 | 123.3032 | -61.5234 | 61.5829 | 0.4927 | -1.3226 | 1.8103 | 4.0132 | 4.834 | 1.0882 | -3.5055 | 61.6195 | 0.22574 | 61.5233 | -0.028522 | 0.048236 | 61.6486 | 0.012299 | 61.4405 | 62.0161 | 60.2008 | 63.3337 | 65.5367 | 66.3574 | 62.6117 | 58.0179 | 123.1429 | 61.7492 | 123.0467 | 61.4949 | 61.5717 | 123.172 | 61.5357 | 122.9639 | 61.5713 | 61.6072 | 61.4751 | 61.511
6354.0625 | 123.4222 | -61.528 | 61.5417 | 0.44234 | -1.3867 | 1.7599 | 3.9995 | 4.8431 | 1.0608 | -3.6337 | 61.6241 | 0.2349 | 61.5462 | -0.028522 | 0.039079 | 61.6486 | 0.003143 | 61.4313 | 61.9704 | 60.1413 | 63.2879 | 65.5275 | 66.3711 | 62.5888 | 57.8943 | 123.1521 | 61.7629 | 123.0742 | 61.4995 | 61.5671 | 123.1766 | 61.5312 | 122.9594 | 61.585 | 61.6209 | 61.5071 | 61.543
6355.0938 | 123.2208 | -61.5463 | 61.5829 | 0.50186 | -1.286 | 1.8423 | 4.0636 | 4.8569 | 1.134 | -3.5055 | 61.6241 | 0.22574 | 61.5462 | -0.023943 | 0.048236 | 61.6486 | 0.003143 | 61.4496 | 62.0482 | 60.2604 | 63.3887 | 65.6099 | 66.4032 | 62.6804 | 58.0408 | 123.1704 | 61.7721 | 123.0925 | 61.5224 | 61.5946 | 123.1949 | 61.5495 | 122.996 | 61.5759 | 61.6209 | 61.4979 | 61.543
6356.0625 | 123.349 | -61.5326 | 61.5509 | 0.3874 | -1.4142 | 1.6958 | 3.8942 | 4.692 | 0.98752 | -3.652 | 61.6195 | 0.212 | 61.5279 | -0.028522 | 0.039079 | 61.644 | 0.012299 | 61.4451 | 61.92 | 60.1184 | 63.2284 | 65.4268 | 66.2246 | 62.5201 | 57.8806 | 123.1521 | 61.7446 | 123.0605 | 61.5041 | 61.5717 | 123.1766 | 61.5449 | 122.9777 | 61.5804 | 61.6072 | 61.4888 | 61.5156
6357.0625 | 123.4039 | -61.5143 | 61.5417 | 0.36908 | -1.4462 | 1.7141 | 3.9674 | 4.8019 | 1.0425 | -3.7024 | 61.6332 | 0.23032 | 61.5599 | -0.023943 | 0.043657 | 61.6486 | 0.007721 | 61.4451 | 61.8834 | 60.0681 | 63.2284 | 65.4817 | 66.3162 | 62.5567 | 57.8119 | 123.1475 | 61.7446 | 123.0742 | 61.4903 | 61.5579 | 123.1628 | 61.522 | 122.9594 | 61.5896 | 61.6255 | 61.5163 | 61.5522
6358.0781 | 123.2986 | -61.5189 | 61.6058 | 0.43776 | -1.3775 | 1.7828 | 4.0407 | 4.8431 | 1.1661 | -3.5879 | 61.6287 | 0.22574 | 61.5462 | -0.023943 | 0.048236 | 61.6394 | 0.007721 | 61.4496 | 61.9566 | 60.1413 | 63.3017 | 65.5595 | 66.362 | 62.6849 | 57.9309 | 123.1475 | 61.7446 | 123.065 | 61.4949 | 61.5671 | 123.1583 | 61.5266 | 122.9685 | 61.5804 | 61.6209 | 61.4979 | 61.5385
6359.0625 | 123.3994 | -61.5372 | 61.5143 | 0.58885 | -1.2081 | 1.9476 | 4.1918 | 4.9484 | 1.3355 | -3.4002 | 61.6104 | 0.22574 | 61.5187 | -0.033101 | 0.039079 | 61.6623 | 0.007721 | 61.4405 | 62.126 | 60.3291 | 63.4848 | 65.7289 | 66.4856 | 62.8727 | 58.137 | 123.1475 | 61.7629 | 123.0559 | 61.5041 | 61.5762 | 123.1995 | 61.5449 | 122.9777 | 61.5713 | 61.6026 | 61.4796 | 61.511
6360.0781 | 123.2986 | -61.5692 | 61.5326 | 0.85439 | -0.86929 | 2.2865 | 4.4985 | 5.1956 | 1.6193 | -3.0523 | 61.6104 | 0.2349 | 61.5416 | -0.028522 | 0.052814 | 61.676 | 0.012299 | 61.4634 | 62.4236 | 60.6999 | 63.8557 | 66.0678 | 66.7648 | 63.1886 | 58.517 | 123.1796 | 61.8041 | 123.1108 | 61.5407 | 61.622 | 123.2452 | 61.5815 | 123.0326 | 61.5575 | 61.5981 | 61.4888 | 61.5293
6361.0625 | 123.3856 | -61.528 | 61.5921 | 0.63921 | -1.1165 | 2.0255 | 4.2833 | 5.0079 | 1.4133 | -3.3132 | 61.6104 | 0.22574 | 61.5233 | -0.023943 | 0.048236 | 61.6577 | 0.012299 | 61.4542 | 62.1672 | 60.4115 | 63.5535 | 65.8114 | 66.5359 | 62.9413 | 58.2148 | 123.1384 | 61.7538 | 123.0513 | 61.5041 | 61.5763 | 123.1857 | 61.5403 | 122.9822 | 61.5621 | 61.5981 | 61.4751 | 61.511
6362.0781 | 123.2941 | -61.5509 | 61.5646 | 0.79487 | -0.95171 | 2.1445 | 4.3703 | 5.0629 | 1.4362 | -3.1438 | 61.6104 | 0.21658 | 61.5141 | -0.019364 | 0.048236 | 61.6715 | 0.007721 | 61.4634 | 62.3458 | 60.5992 | 63.6954 | 65.9212 | 66.6138 | 62.9871 | 58.4071 | 123.1613 | 61.7675 | 123.065 | 61.5315 | 61.5991 | 123.2224 | 61.5586 | 123.0143 | 61.5621 | 61.6026 | 61.4659 | 61.5064
6363.0625 | 123.3627 | -61.5601 | 61.5234 | 0.90933 | -0.80976 | 2.2773 | 4.4573 | 5.1224 | 1.5827 | -2.947 | 61.6058 | 0.2349 | 61.5279 | -0.033101 | 0.039079 | 61.6715 | 0.003143 | 61.4588 | 62.4694 | 60.7503 | 63.8374 | 66.0174 | 66.6824 | 63.1428 | 58.6131 | 123.1658 | 61.795 | 123.0879 | 61.527 | 61.5991 | 123.2315 | 61.5632 | 123.0189 | 61.5667 | 61.6026 | 61.4888 | 61.5247
6364.0938 | 123.2758 | -61.5692 | 61.5646 | 0.82234 | -0.89676 | 2.172 | 4.352 | 5.0217 | 1.4774 | -3.0706 | 61.6104 | 0.22574 | 61.505 | -0.033101 | 0.039079 | 61.6669 | 0.012299 | 61.4542 | 62.3916 | 60.6725 | 63.7412 | 65.9212 | 66.5909 | 63.0466 | 58.4986 | 123.1796 | 61.795 | 123.0742 | 61.5361 | 61.6083 | 123.2361 | 61.5815 | 123.0234 | 61.5713 | 61.5981 | 61.4659 | 61.4927
6365.0625 | 123.381 | -61.5509 | 61.5555 | 0.75367 | -0.9746 | 2.0896 | 4.2376 | 4.8614 | 1.3584 | -3.1576 | 61.6195 | 0.22574 | 61.5279 | -0.033101 | 0.048236 | 61.6623 | 0.003143 | 61.4451 | 62.3046 | 60.5763 | 63.6405 | 65.7885 | 66.4123 | 62.9093 | 58.3933 | 123.1704 | 61.7766 | 123.0788 | 61.5178 | 61.5991 | 123.2132 | 61.554 | 122.996 | 61.5713 | 61.6164 | 61.4796 | 61.5247
6366.1094 | 123.2941 | -61.5234 | 61.5967 | 0.57053 | -1.2219 | 1.8515 | 4.059 | 4.7149 | 1.1707 | -3.478 | 61.6287 | 0.23032 | 61.5645 | -0.028522 | 0.048236 | 61.6486 | 0.012299 | 61.4496 | 62.094 | 60.3016 | 63.3749 | 65.5824 | 66.2384 | 62.6941 | 58.0454 | 123.1521 | 61.7538 | 123.0879 | 61.4949 | 61.5717 | 123.172 | 61.5357 | 122.9731 | 61.5804 | 61.6164 | 61.5163 | 61.5522
6367.0625 | 123.3948 | -61.5189 | 61.5417 | 0.54306 | -1.2676 | 1.8194 | 4.0865 | 4.7882 | 1.1295 | -3.565 | 61.6195 | 0.21658 | 61.5141 | -0.028522 | 0.043657 | 61.6486 | 0.012299 | 61.4496 | 62.0619 | 60.2512 | 63.3383 | 65.6053 | 66.307 | 62.6483 | 57.9538 | 123.1384 | 61.7354 | 123.033 | 61.4903 | 61.5625 | 123.1674 | 61.5312 | 122.9685 | 61.5759 | 61.6072 | 61.4705 | 61.5018
6368.0938 | 123.2941 | -61.5417 | 61.5875 | 0.50186 | -1.2722 | 1.8194 | 4.0773 | 4.7745 | 1.1569 | -3.5513 | 61.6378 | 0.22574 | 61.5553 | -0.028522 | 0.057392 | 61.6531 | 0.016878 | 61.4496 | 62.0436 | 60.2695 | 63.3612 | 65.6191 | 66.3162 | 62.6987 | 57.9905 | 123.1796 | 61.7675 | 123.0971 | 61.5132 | 61.5991 | 123.1949 | 61.5586 | 122.9914 | 61.5804 | 61.6209 | 61.4979 | 61.5385
6369.0625 | 123.2529 | -61.5509 | 61.6058 | 0.46065 | -1.2722 | 1.7874 | 3.9949 | 4.6417 | 1.1249 | -3.5009 | 61.6287 | 0.22574 | 61.5416 | -0.028522 | 0.043657 | 61.6486 | 0.007721 | 61.4405 | 62.0116 | 60.2787 | 63.3383 | 65.5458 | 66.1926 | 62.6758 | 58.05 | 123.1796 | 61.7766 | 123.0925 | 61.5224 | 61.5946 | 123.1995 | 61.5586 | 122.9914 | 61.585 | 61.6209 | 61.4979 | 61.5339
6370.0938 | 123.2803 | -61.5326 | 61.5921 | 0.62089 | -1.0936 | 2.0255 | 4.1918 | 4.8202 | 1.2897 | -3.3498 | 61.6195 | 0.22574 | 61.5279 | -0.019364 | 0.043657 | 61.6577 | 0.007721 | 61.4496 | 62.1535 | 60.4389 | 63.5581 | 65.7244 | 66.3528 | 62.8223 | 58.1827 | 123.1521 | 61.7583 | 123.0605 | 61.5132 | 61.5763 | 123.1903 | 61.5403 | 122.9822 | 61.5759 | 61.6118 | 61.4842 | 61.5202
6371.0625 | 123.4039 | -61.5326 | 61.5738 | 0.58885 | -1.2264 | 1.9019 | 4.1597 | 4.8477 | 1.3904 | -3.4551 | 61.6287 | 0.23032 | 61.5599 | -0.028522 | 0.043657 | 61.6531 | 0.007721 | 61.4542 | 62.1214 | 60.3062 | 63.4344 | 65.6923 | 66.3803 | 62.923 | 58.0774 | 123.1613 | 61.7629 | 123.0925 | 61.5041 | 61.5763 | 123.1857 | 61.5403 | 122.9868 | 61.585 | 61.6209 | 61.5163 | 61.5522
6372.0938 | 123.262 | -61.5555 | 61.5738 | 0.57969 | -1.1761 | 1.9705 | 4.1964 | 4.8706 | 1.4271 | -3.3682 | 61.6149 | 0.22116 | 61.537 | -0.019364 | 0.057392 | 61.6669 | 0.007721 | 61.468 | 62.1352 | 60.3794 | 63.526 | 65.7518 | 66.4261 | 62.9825 | 58.1873 | 123.1704 | 61.7766 | 123.0925 | 61.5361 | 61.6129 | 123.2224 | 61.5632 | 123.0234 | 61.5575 | 61.6072 | 61.4796 | 61.5293
6373.0625 | 123.2986 | -61.5509 | 61.5555 | 0.90018 | -0.75024 | 2.4055 | 4.5901 | 5.1819 | 1.7063 | -2.9241 | 61.6012 | 0.2349 | 61.5096 | -0.028522 | 0.039079 | 61.6806 | 0.007721 | 61.4863 | 62.4511 | 60.8007 | 63.9564 | 66.141 | 66.7328 | 63.2572 | 58.6268 | 123.1521 | 61.7858 | 123.0605 | 61.5224 | 61.59 | 123.2315 | 61.5586 | 123.0372 | 61.5621 | 61.5935 | 61.4705 | 61.5018
6374.0938 | 123.2849 | -61.5417 | 61.5921 | 0.67126 | -1.025 | 2.1354 | 4.352 | 4.9713 | 1.4591 | -3.2491 | 61.6104 | 0.23032 | 61.5508 | -0.023943 | 0.048236 | 61.6623 | 0.007721 | 61.4634 | 62.213 | 60.5168 | 63.6771 | 65.8938 | 66.5131 | 63.0008 | 58.2926 | 123.1521 | 61.7721 | 123.0925 | 61.5178 | 61.59 | 123.204 | 61.5495 | 123.0051 | 61.5621 | 61.6026 | 61.5025 | 61.543
6375.0625 | 123.4314 | -61.5509 | 61.5097 | 0.68957 | -1.0021 | 2.1445 | 4.352 | 4.9759 | 1.5049 | -3.2125 | 61.6012 | 0.23032 | 61.5141 | -0.023943 | 0.048236 | 61.6669 | 0.012299 | 61.4634 | 62.2405 | 60.5488 | 63.6954 | 65.9029 | 66.5268 | 63.0558 | 58.3384 | 123.1521 | 61.7812 | 123.065 | 61.527 | 61.5991 | 123.2178 | 61.5632 | 123.0143 | 61.553 | 61.5889 | 61.4659 | 61.5018
6376.0938 | 123.2895 | -61.5601 | 61.5646 | 0.81777 | -0.85555 | 2.2636 | 4.4207 | 4.9576 | 1.5965 | -3.0385 | 61.6012 | 0.23032 | 61.5233 | -0.023943 | 0.052814 | 61.6623 | 0.007721 | 61.4634 | 62.3778 | 60.7045 | 63.8236 | 65.9808 | 66.5176 | 63.1565 | 58.5215 | 123.1613 | 61.7904 | 123.0834 | 61.5361 | 61.6129 | 123.2224 | 61.5678 | 123.0234 | 61.5484 | 61.5935 | 61.4705 | 61.5156
6377.0625 | 123.3261 | -61.5829 | 61.5829 | 0.96885 | -0.70445 | 2.4192 | 4.5443 | 5.0354 | 1.5461 | -3.0248 | 61.6058 | 0.23032 | 61.5324 | -0.033101 | 0.052814 | 61.676 | 0.012299 | 61.468 | 62.5518 | 60.8785 | 64.0022 | 66.1273 | 66.6183 | 63.129 | 58.5582 | 123.1887 | 61.8133 | 123.1154 | 61.5498 | 61.6358 | 123.259 | 61.5952 | 123.0509 | 61.553 | 61.5935 | 61.4796 | 61.5202
6378.0938 | 123.2483 | -61.5784 | 61.5692 | 1.0375 | -0.66782 | 2.4788 | 4.5809 | 5.0583 | 1.6789 | -2.9241 | 61.592 | 0.22574 | 61.505 | -0.033101 | 0.052814 | 61.6852 | 0.012299 | 61.4634 | 62.6159 | 60.9106 | 64.0571 | 66.1593 | 66.6367 | 63.2572 | 58.6543 | 123.1704 | 61.8041 | 123.0833 | 61.5453 | 61.6312 | 123.2636 | 61.5907 | 123.0418 | 61.5392 | 61.5797 | 61.4522 | 61.4927
6379.0625 | 123.2666 | -61.5967 | 61.5921 | 0.84066 | -0.85555 | 2.2956 | 4.4024 | 4.866 | 1.5415 | -3.0935 | 61.6058 | 0.23032 | 61.5141 | -0.033101 | 0.048236 | 61.676 | 0.012299 | 61.4588 | 62.4373 | 60.7411 | 63.8923 | 65.9991 | 66.4627 | 63.1382 | 58.5032 | 123.2025 | 61.827 | 123.1108 | 61.5636 | 61.6449 | 123.2727 | 61.609 | 123.0555 | 61.5575 | 61.5935 | 61.4659 | 61.5018
6380.0938 | 123.3627 | -61.5417 | 61.5372 | 0.94138 | -0.7365 | 2.3918 | 4.4802 | 4.9438 | 1.6605 | -2.9699 | 61.6012 | 0.23032 | 61.5096 | -0.033101 | 0.048236 | 61.6715 | 0.007721 | 61.468 | 62.4831 | 60.8052 | 63.9335 | 66.022 | 66.4856 | 63.2023 | 58.5719 | 123.1429 | 61.7721 | 123.0513 | 61.5086 | 61.59 | 123.2132 | 61.5495 | 123.0097 | 61.553 | 61.5935 | 61.4613 | 61.5018
6381.0625 | 123.381 | -61.5509 | 61.5051 | 0.79487 | -1.0204 | 2.1766 | 4.3566 | 4.8706 | 1.6148 | -3.2262 | 61.6104 | 0.2349 | 61.5462 | -0.028522 | 0.048236 | 61.6623 | 0.003143 | 61.4542 | 62.3458 | 60.5305 | 63.7275 | 65.9075 | 66.4215 | 63.1657 | 58.3247 | 123.1613 | 61.7858 | 123.0971 | 61.5224 | 61.5991 | 123.2132 | 61.554 | 123.0051 | 61.5621 | 61.6072 | 61.4979 | 61.543
6382.0625 | 123.2712 | -61.5509 | 61.5509 | 0.91391 | -0.90592 | 2.2819 | 4.4756 | 4.9988 | 1.6926 | -3.1255 | 61.5966 | 0.2349 | 61.5233 | -0.023943 | 0.048236 | 61.676 | 0.007721 | 61.4634 | 62.4648 | 60.645 | 63.8328 | 66.0265 | 66.5497 | 63.2435 | 58.4254 | 123.1475 | 61.7858 | 123.0742 | 61.527 | 61.5991 | 123.2269 | 61.5586 | 123.0143 | 61.5484 | 61.5889 | 61.4751 | 61.5156
6383.0781 | 123.3765 | -61.5097 | 61.5829 | 0.84524 | -0.95171 | 2.2178 | 4.439 | 4.9713 | 1.5827 | -3.2583 | 61.6012 | 0.22574 | 61.5096 | -0.028522 | 0.052814 | 61.6715 | 0.012299 | 61.4634 | 62.3549 | 60.558 | 63.7275 | 65.9487 | 66.481 | 63.0924 | 58.2514 | 123.1109 | 61.7354 | 123.0193 | 61.4812 | 61.5625 | 123.1812 | 61.522 | 122.9731 | 61.5484 | 61.5889 | 61.4567 | 61.4973
6384.0625 | 123.2803 | -61.5326 | 61.5921 | 0.64837 | -1.1715 | 1.998 | 4.2559 | 4.7699 | 1.3675 | -3.4689 | 61.6104 | 0.22574 | 61.5324 | -0.033101 | 0.052814 | 61.6531 | 0.007721 | 61.4451 | 62.181 | 60.3611 | 63.5306 | 65.7885 | 66.3025 | 62.9001 | 58.0637 | 123.1429 | 61.7583 | 123.065 | 61.4995 | 61.5854 | 123.1857 | 61.5403 | 122.9777 | 61.5575 | 61.6026 | 61.4796 | 61.5247
6385.0625 | 123.2803 | -61.5555 | 61.6196 | 0.61632 | -1.1898 | 1.9476 | 4.233 | 4.7561 | 1.3217 | -3.5009 | 61.6287 | 0.23948 | 61.5645 | -0.033101 | 0.048236 | 61.6577 | 0.012299 | 61.4405 | 62.1718 | 60.3657 | 63.5031 | 65.7885 | 66.3116 | 62.8772 | 58.0546 | 123.1842 | 61.795 | 123.12 | 61.5224 | 61.6037 | 123.2132 | 61.5678 | 122.996 | 61.5804 | 61.6164 | 61.5163 | 61.5522
6386.1094 | 123.2758 | -61.5326 | 61.615 | 0.79487 | -0.98376 | 2.0987 | 4.3062 | 4.7836 | 1.5095 | -3.2308 | 61.6104 | 0.22574 | 61.5324 | -0.023943 | 0.052814 | 61.6669 | 0.003143 | 61.4542 | 62.3275 | 60.5488 | 63.6313 | 65.8388 | 66.3162 | 63.0421 | 58.3018 | 123.1429 | 61.7583 | 123.065 | 61.5086 | 61.5854 | 123.1995 | 61.5357 | 122.9868 | 61.5575 | 61.6072 | 61.4796 | 61.5293
6387.0625 | 123.2574 | -61.5509 | 61.5967 | 0.84981 | -0.86013 | 2.2269 | 4.3566 | 4.7882 | 1.5095 | -3.0797 | 61.6104 | 0.23032 | 61.5096 | -0.023943 | 0.048236 | 61.676 | 0.012299 | 61.4634 | 62.4007 | 60.6908 | 63.7778 | 65.9075 | 66.3391 | 63.0604 | 58.4712 | 123.1613 | 61.7812 | 123.0605 | 61.527 | 61.5991 | 123.2269 | 61.5632 | 123.0143 | 61.5621 | 61.5981 | 61.4613 | 61.4973
6388.0938 | 123.3444 | -61.5097 | 61.5692 | 0.79487 | -0.95628 | 2.1491 | 4.3474 | 4.8111 | 1.5003 | -3.2033 | 61.6104 | 0.23032 | 61.5233 | -0.023943 | 0.048236 | 61.6623 | 0.012299 | 61.4588 | 62.3046 | 60.5534 | 63.6588 | 65.8572 | 66.3208 | 63.01 | 58.3064 | 123.1201 | 61.74 | 123.033 | 61.4858 | 61.5579 | 123.172 | 61.522 | 122.9685 | 61.5621 | 61.5981 | 61.4751 | 61.511
6389.0625 | 123.3078 | -61.5738 | 61.5875 | 1.0192 | -0.68156 | 2.3918 | 4.5443 | 4.9347 | 1.6697 | -2.8646 | 61.6012 | 0.22574 | 61.5233 | -0.028522 | 0.052814 | 61.676 | 0.012299 | 61.4634 | 62.593 | 60.8922 | 63.9656 | 66.1181 | 66.5085 | 63.2435 | 58.7092 | 123.175 | 61.7995 | 123.0971 | 61.5453 | 61.6266 | 123.2498 | 61.5861 | 123.0372 | 61.5484 | 61.5889 | 61.4705 | 61.511
6390.0938 | 123.3032 | -61.5189 | 61.6013 | 0.63921 | -1.1028 | 1.9797 | 4.1643 | 4.5959 | 1.2943 | -3.4185 | 61.6287 | 0.23032 | 61.5416 | -0.033101 | 0.048236 | 61.6486 | 0.007721 | 61.4542 | 62.1581 | 60.4161 | 63.4986 | 65.6832 | 66.1148 | 62.8131 | 58.1003 | 123.1475 | 61.7492 | 123.0605 | 61.4858 | 61.5671 | 123.1674 | 61.5266 | 122.9731 | 61.5804 | 61.6209 | 61.4934 | 61.5339
6391.0625 | 123.3536 | -61.5417 | 61.5646 | 0.58427 | -1.1623 | 1.9019 | 4.0498 | 4.4494 | 1.1615 | -3.5009 | 61.6241 | 0.21658 | 61.5324 | -0.023943 | 0.039079 | 61.6486 | 0.012299 | 61.4359 | 62.126 | 60.3794 | 63.4436 | 65.5916 | 65.9912 | 62.7033 | 58.0408 | 123.1658 | 61.7583 | 123.0742 | 61.5178 | 61.5808 | 123.1903 | 61.554 | 122.9777 | 61.585 | 61.6118 | 61.4934 | 61.5202
6392.0938 | 123.262 | -61.5417 | 61.6287 | 0.67584 | -1.0799 | 1.966 | 4.1231 | 4.5227 | 1.2943 | -3.4277 | 61.6195 | 0.23032 | 61.5279 | -0.023943 | 0.048236 | 61.6577 | 0.007721 | 61.4451 | 62.2176 | 60.4618 | 63.5077 | 65.6648 | 66.0644 | 62.836 | 58.1141 | 123.1613 | 61.7721 | 123.0696 | 61.5178 | 61.59 | 123.1995 | 61.5495 | 122.9868 | 61.5713 | 61.6118 | 61.4796 | 61.5202
6393.0625 | 123.262 | -61.5509 | 61.5784 | 0.74909 | -0.95171 | 2.0621 | 4.178 | 4.5318 | 1.3172 | -3.2812 | 61.6195 | 0.2349 | 61.5508 | -0.023943 | 0.048236 | 61.6531 | 0.012299 | 61.4451 | 62.3 | 60.5992 | 63.613 | 65.7289 | 66.0827 | 62.8681 | 58.2697 | 123.1704 | 61.7858 | 123.1017 | 61.527 | 61.5991 | 123.204 | 61.5632 | 122.996 | 61.5713 | 61.6072 | 61.5025 | 61.5385
6394.0781 | 123.2986 | -61.5463 | 61.6058 | 0.75825 | -0.94713 | 2.0163 | 4.1277 | 4.4723 | 1.3996 | -3.2995 | 61.6241 | 0.2349 | 61.5416 | -0.028522 | 0.048236 | 61.6577 | 0.007721 | 61.4496 | 62.3046 | 60.5992 | 63.5626 | 65.674 | 66.0186 | 62.9459 | 58.2468 | 123.1704 | 61.7812 | 123.0879 | 61.5178 | 61.5946 | 123.204 | 61.554 | 122.996 | 61.5759 | 61.6164 | 61.4934 | 61.5339
6395.0625 | 123.2666 | -61.5601 | 61.5875 | 0.68041 | -1.0067 | 1.9522 | 4.0682 | 4.4174 | 1.3172 | -3.4231 | 61.6195 | 0.22116 | 61.5233 | -0.028522 | 0.048236 | 61.6577 | 0.003143 | 61.4451 | 62.2405 | 60.5534 | 63.5123 | 65.6282 | 65.9774 | 62.8772 | 58.137 | 123.1796 | 61.7812 | 123.0834 | 61.5315 | 61.6083 | 123.2178 | 61.5632 | 123.0051 | 61.5713 | 61.6164 | 61.4751 | 61.5202
6396.1094 | 123.3261 | -61.5097 | 61.5967 | 0.60716 | -1.0799 | 1.8698 | 3.9995 | 4.3624 | 1.2027 | -3.5101 | 61.6195 | 0.22574 | 61.537 | -0.033101 | 0.052814 | 61.6486 | 0.012299 | 61.4405 | 62.1169 | 60.4298 | 63.3795 | 65.5092 | 65.8721 | 62.7124 | 57.9996 | 123.1292 | 61.7354 | 123.0467 | 61.4766 | 61.5625 | 123.1583 | 61.522 | 122.9502 | 61.5667 | 61.6072 | 61.4842 | 61.5247
6397.0625 | 123.2666 | -61.5189 | 61.6196 | 0.44234 | -1.2676 | 1.705 | 3.7843 | 4.129 | 1.0287 | -3.6291 | 61.647 | 0.2349 | 61.5691 | -0.033101 | 0.039079 | 61.6348 | 0.012299 | 61.4222 | 61.9612 | 60.2512 | 63.2238 | 65.3032 | 65.6478 | 62.5476 | 57.8897 | 123.1658 | 61.7538 | 123.0879 | 61.4858 | 61.5579 | 123.1537 | 61.5312 | 122.941 | 61.6079 | 61.6347 | 61.53 | 61.5568
6398.0938 | 123.3124 | -61.5509 | 61.6058 | 0.52933 | -1.1349 | 1.8149 | 3.9033 | 4.2205 | 1.0745 | -3.5055 | 61.6378 | 0.2349 | 61.5737 | -0.028522 | 0.048236 | 61.644 | 0.007721 | 61.4268 | 62.0802 | 60.416 | 63.3658 | 65.4542 | 65.7714 | 62.6254 | 58.0454 | 123.1887 | 61.7858 | 123.1246 | 61.5224 | 61.5991 | 123.1949 | 61.5586 | 122.9777 | 61.5896 | 61.6301 | 61.5254 | 61.5659
6399.0625 | 123.2666 | -61.5372 | 61.5921 | 0.58427 | -1.025 | 1.879 | 3.9537 | 4.2617 | 1.1203 | -3.4735 | 61.6287 | 0.22574 | 61.5324 | -0.028522 | 0.052814 | 61.6531 | 0.012299 | 61.4268 | 62.1214 | 60.5122 | 63.4161 | 65.4909 | 65.7989 | 62.6575 | 58.0637 | 123.1658 | 61.7629 | 123.0696 | 61.5086 | 61.59 | 123.1903 | 61.5495 | 122.9639 | 61.5759 | 61.6164 | 61.4796 | 61.5202
6400.0938 | 123.2666 | -61.528 | 61.6013 | 0.50186 | -1.0936 | 1.7782 | 3.8255 | 4.1381 | 1.0516 | -3.4918 | 61.6332 | 0.22574 | 61.5324 | -0.028522 | 0.048236 | 61.6486 | 0.007721 | 61.4313 | 62.0299 | 60.4344 | 63.3062 | 65.3535 | 65.6661 | 62.5796 | 58.0362 | 123.1613 | 61.7538 | 123.0605 | 61.4995 | 61.5763 | 123.1766 | 61.5357 | 122.9594 | 61.585 | 61.6255 | 61.4842 | 61.5247
6401.0625 | 123.3536 | -61.528 | 61.6104 | 0.54764 | -0.99291 | 1.8515 | 3.853 | 4.1335 | 1.0745 | -3.4048 | 61.6332 | 0.22574 | 61.5691 | -0.023943 | 0.048236 | 61.6486 | 0.003143 | 61.4268 | 62.0757 | 60.5351 | 63.3795 | 65.381 | 65.6616 | 62.6025 | 58.1232 | 123.1613 | 61.7538 | 123.0971 | 61.5041 | 61.5763 | 123.1766 | 61.5312 | 122.9548 | 61.585 | 61.6301 | 61.5208 | 61.5659
6402.0938 | 123.3124 | -61.5097 | 61.6241 | 0.45607 | -1.1074 | 1.7782 | 3.7706 | 4.0694 | 1.0242 | -3.5376 | 61.6332 | 0.22574 | 61.5508 | -0.023943 | 0.057392 | 61.644 | 0.016878 | 61.4268 | 61.9658 | 60.4023 | 63.2879 | 65.2803 | 65.5792 | 62.5339 | 57.9722 | 123.143 | 61.7354 | 123.0605 | 61.4858 | 61.5671 | 123.1537 | 61.5266 | 122.9365 | 61.5759 | 61.6164 | 61.4934 | 61.5339
6403.0625 | 123.2391 | -61.5555 | 61.5967 | 0.50186 | -1.057 | 1.8149 | 3.7751 | 4.0466 | 1.0196 | -3.4551 | 61.6378 | 0.22574 | 61.5416 | -0.028522 | 0.048236 | 61.644 | 0.007721 | 61.4222 | 62.0573 | 60.4985 | 63.3703 | 65.3306 | 65.602 | 62.5751 | 58.1003 | 123.1933 | 61.7812 | 123.0971 | 61.527 | 61.6037 | 123.1995 | 61.5632 | 122.9777 | 61.5896 | 61.6301 | 61.4934 | 61.5339
6404.0938 | 123.2574 | -61.5326 | 61.615 | 0.45149 | -1.0936 | 1.7416 | 3.6195 | 3.8543 | 0.93258 | -3.391 | 61.6378 | 0.23032 | 61.5645 | -0.028522 | 0.052814 | 61.6348 | 0.007721 | 61.4176 | 61.9841 | 60.4389 | 63.2742 | 65.1521 | 65.3869 | 62.4652 | 58.1415 | 123.1704 | 61.7629 | 123.0971 | 61.5041 | 61.5854 | 123.1674 | 61.5403 | 122.9502 | 61.585 | 61.6301 | 61.5117 | 61.5568
6405.0625 | 123.381 | -61.5784 | 61.5738 | 0.46523 | -1.057 | 1.7462 | 3.6424 | 3.8955 | 1.0242 | -3.3361 | 61.6287 | 0.22574 | 61.5416 | -0.033101 | 0.057392 | 61.6303 | 0.012299 | 61.4268 | 62.0436 | 60.5214 | 63.3246 | 65.2207 | 65.4739 | 62.6025 | 58.2423 | 123.207 | 61.8041 | 123.12 | 61.5453 | 61.6358 | 123.2086 | 61.5907 | 123.0051 | 61.5713 | 61.6164 | 61.4842 | 61.5293
6406.0938 | 123.3078 | -61.5189 | 61.6425 | 0.45149 | -1.1257 | 1.6775 | 3.6469 | 3.9458 | 1.0837 | -3.4094 | 61.6332 | 0.23032 | 61.5462 | -0.023943 | 0.048236 | 61.644 | 0.007721 | 61.4222 | 61.9704 | 60.3932 | 63.1964 | 65.1658 | 65.4647 | 62.6025 | 58.1095 | 123.1521 | 61.7492 | 123.065 | 61.4949 | 61.5671 | 123.1628 | 61.5266 | 122.941 | 61.585 | 61.6255 | 61.4979 | 61.5385
6407.0625 | 123.4268 | -61.4822 | 61.5829 | 0.39198 | -1.1623 | 1.5951 | 3.5462 | 3.836 | 1.0013 | -3.446 | 61.647 | 0.2349 | 61.5782 | -0.028522 | 0.052814 | 61.6348 | 0.012299 | 61.413 | 61.8742 | 60.3199 | 63.0773 | 65.0284 | 65.3182 | 62.4835 | 58.0363 | 123.1292 | 61.7171 | 123.0605 | 61.4537 | 61.5351 | 123.1171 | 61.4945 | 122.8953 | 61.5942 | 61.6347 | 61.5254 | 61.5659
6408.0938 | 123.2803 | -61.5189 | 61.6516 | 0.30499 | -1.2493 | 1.5035 | 3.4684 | 3.7307 | 0.90969 | -3.5238 | 61.6424 | 0.22116 | 61.5462 | -0.028522 | 0.043657 | 61.6348 | 0.012299 | 61.4222 | 61.8238 | 60.2695 | 63.0224 | 64.9872 | 65.2495 | 62.4286 | 57.995 | 123.1613 | 61.74 | 123.065 | 61.4903 | 61.5625 | 123.1537 | 61.5312 | 122.941 | 61.5987 | 61.6301 | 61.5025 | 61.5339
6409.0625 | 123.2941 | -61.5417 | 61.5829 | 0.22258 | -1.318 | 1.4119 | 3.3493 | 3.5979 | 0.82728 | -3.5604 | 61.6516 | 0.22574 | 61.5691 | -0.023943 | 0.039079 | 61.6211 | 0.012299 | 61.413 | 61.7643 | 60.2237 | 62.9537 | 64.8911 | 65.1397 | 62.369 | 57.9813 | 123.1933 | 61.7675 | 123.1108 | 61.5178 | 61.5808 | 123.1628 | 61.554 | 122.9548 | 61.6125 | 61.6393 | 61.53 | 61.5568
6410.0938 | 123.3215 | -61.5097 | 61.6333 | 0.35535 | -1.1394 | 1.5585 | 3.4592 | 3.6849 | 0.91427 | -3.3636 | 61.6424 | 0.22574 | 61.5782 | -0.028522 | 0.052814 | 61.6257 | 0.007721 | 61.4268 | 61.8651 | 60.3703 | 63.0682 | 64.9689 | 65.1946 | 62.424 | 58.1461 | 123.1521 | 61.7354 | 123.0879 | 61.4812 | 61.5625 | 123.1354 | 61.5174 | 122.9365 | 61.5896 | 61.6347 | 61.5254 | 61.5705
6411.0625 | 123.3215 | -61.5051 | 61.5692 | 0.31872 | -1.1852 | 1.5081 | 3.3722 | 3.5567 | 0.8227 | -3.4231 | 61.6332 | 0.22116 | 61.5416 | -0.023943 | 0.052814 | 61.6303 | 0.012299 | 61.4084 | 61.8238 | 60.3199 | 63.0132 | 64.8774 | 65.0618 | 62.3278 | 58.082 | 123.1384 | 61.7263 | 123.0467 | 61.4812 | 61.5579 | 123.1354 | 61.5174 | 122.9136 | 61.5804 | 61.6209 | 61.4888 | 61.5293
6412.0938 | 123.3536 | -61.5326 | 61.5601 | 0.39198 | -1.0982 | 1.5722 | 3.4134 | 3.6254 | 0.89596 | -3.2995 | 61.6378 | 0.22574 | 61.5553 | -0.028522 | 0.052814 | 61.6303 | 0.007721 | 61.413 | 61.9246 | 60.4344 | 63.1048 | 64.946 | 65.158 | 62.4286 | 58.2331 | 123.1704 | 61.7583 | 123.0879 | 61.5041 | 61.5854 | 123.1628 | 61.5403 | 122.9456 | 61.585 | 61.6301 | 61.5025 | 61.5476
6413.0625 | 123.2849 | -61.5326 | 61.5967 | 0.43318 | -1.0479 | 1.5768 | 3.4363 | 3.63 | 0.97379 | -3.2079 | 61.647 | 0.2349 | 61.5599 | -0.023943 | 0.043657 | 61.6348 | 0.007721 | 61.413 | 61.9658 | 60.4847 | 63.1094 | 64.9689 | 65.1626 | 62.5064 | 58.3247 | 123.1796 | 61.7675 | 123.0925 | 61.5086 | 61.5763 | 123.1674 | 61.5403 | 122.9456 | 61.6033 | 61.6393 | 61.5163 | 61.5522
6414.0781 | 123.2803 | -61.5463 | 61.615 | 0.48812 | -0.98834 | 1.6455 | 3.5096 | 3.7307 | 1.0379 | -3.1759 | 61.6378 | 0.22574 | 61.537 | -0.023943 | 0.043657 | 61.6394 | 0.012299 | 61.4268 | 62.0344 | 60.558 | 63.1918 | 65.0559 | 65.277 | 62.5842 | 58.3705 | 123.1842 | 61.7721 | 123.0834 | 61.5224 | 61.59 | 123.1857 | 61.5586 | 122.9731 | 61.5942 | 61.6255 | 61.4934 | 61.5247
6415.0625 | 123.2849 | -61.528 | 61.6058 | 0.098959 | -1.4691 | 1.1647 | 3.1204 | 3.4011 | 0.70824 | -3.6795 | 61.6653 | 0.2349 | 61.5737 | -0.028522 | 0.052814 | 61.6074 | 0.007721 | 61.3993 | 61.627 | 60.0589 | 62.6927 | 64.6484 | 64.9291 | 62.2363 | 57.8485 | 123.1933 | 61.7629 | 123.1017 | 61.4995 | 61.5808 | 123.1354 | 61.5357 | 122.9273 | 61.6125 | 61.6576 | 61.5208 | 61.5659
6416.0938 | 123.317 | -61.496 | 61.6333 | 0.11727 | -1.405 | 1.1601 | 3.0838 | 3.3416 | 0.7174 | -3.6291 | 61.6653 | 0.2349 | 61.5874 | -0.023943 | 0.052814 | 61.6119 | -0.001436 | 61.413 | 61.6132 | 60.091 | 62.6561 | 64.5798 | 64.8375 | 62.2134 | 57.8669 | 123.1613 | 61.7309 | 123.0834 | 61.472 | 61.5488 | 123.1079 | 61.4945 | 122.909 | 61.6125 | 61.6667 | 61.5346 | 61.5888
6417.0625 | 123.2941 | -61.4731 | 61.6562 | 0.089802 | -1.4096 | 1.1235 | 3.0472 | 3.3324 | 0.68077 | -3.6108 | 61.6561 | 0.22574 | 61.5645 | -0.033101 | 0.048236 | 61.6119 | 0.012299 | 61.4084 | 61.5629 | 60.0635 | 62.5966 | 64.5202 | 64.8055 | 62.1539 | 57.8623 | 123.1292 | 61.6988 | 123.0376 | 61.44 | 61.5213 | 123.085 | 61.4854 | 122.8815 | 61.6079 | 61.6438 | 61.5163 | 61.5522
6418.0781 | 123.2895 | -61.5097 | 61.6333 | 0.002813 | -1.5241 | 1.0365 | 2.9464 | 3.2271 | 0.59836 | -3.6474 | 61.6699 | 0.2349 | 61.6011 | -0.028522 | 0.043657 | 61.6074 | 0.007721 | 61.4084 | 61.5125 | 59.9856 | 62.5462 | 64.4561 | 64.7368 | 62.1081 | 57.8623 | 123.1796 | 61.7446 | 123.1108 | 61.4812 | 61.5534 | 123.1171 | 61.5174 | 122.9181 | 61.6262 | 61.6622 | 61.5575 | 61.5934
6419.0625 | 123.3215 | -61.5005 | 61.6013 | 0.10354 | -1.3959 | 1.1693 | 3.0746 | 3.3324 | 0.73114 | -3.5101 | 61.6607 | 0.22574 | 61.5737 | -0.028522 | 0.048236 | 61.6165 | 0.012299 | 61.413 | 61.6041 | 60.1047 | 62.6698 | 64.5752 | 64.8329 | 62.2317 | 57.9905 | 123.1613 | 61.7263 | 123.0742 | 61.472 | 61.5488 | 123.1171 | 61.5128 | 122.9136 | 61.6125 | 61.6484 | 61.5254 | 61.5614
6420.0781 | 123.3124 | -61.5097 | 61.6333 | 0.31414 | -1.1349 | 1.3936 | 3.2349 | 3.4743 | 0.90054 | -3.1942 | 61.6424 | 0.23032 | 61.5553 | -0.028522 | 0.052814 | 61.6303 | 0.007721 | 61.4176 | 61.8238 | 60.3748 | 62.9033 | 64.7446 | 64.984 | 62.4102 | 58.3155 | 123.1521 | 61.74 | 123.065 | 61.4812 | 61.5625 | 123.14 | 61.5174 | 122.9273 | 61.5896 | 61.6347 | 61.5025 | 61.5476
6421.0625 | 123.3719 | -61.5097 | 61.5921 | 0.17679 | -1.2768 | 1.2471 | 3.0975 | 3.3232 | 0.76776 | -3.3498 | 61.6607 | 0.23032 | 61.5874 | -0.028522 | 0.048236 | 61.6165 | 0.007721 | 61.413 | 61.6865 | 60.2329 | 62.7568 | 64.6072 | 64.8329 | 62.2775 | 58.1599 | 123.1704 | 61.74 | 123.0971 | 61.4812 | 61.5579 | 123.1262 | 61.5174 | 122.9227 | 61.6125 | 61.653 | 61.5392 | 61.5797
6422.0625 | 123.2803 | -61.5463 | 61.5784 | 0.23173 | -1.231 | 1.27 | 3.1296 | 3.3828 | 0.87307 | -3.2995 | 61.6516 | 0.22574 | 61.5599 | -0.023943 | 0.048236 | 61.6303 | 0.007721 | 61.4176 | 61.7781 | 60.3153 | 62.8163 | 64.6759 | 64.9291 | 62.4194 | 58.2468 | 123.1979 | 61.7721 | 123.1062 | 61.5224 | 61.5946 | 123.1766 | 61.554 | 122.9639 | 61.6033 | 61.6438 | 61.5117 | 61.5522
6423.0938 | 123.2803 | -61.4914 | 61.6196 | 0.28209 | -1.2219 | 1.3066 | 3.2303 | 3.5292 | 1.102 | -3.2812 | 61.6424 | 0.23032 | 61.5508 | -0.028522 | 0.048236 | 61.6303 | 0.007721 | 61.413 | 61.7735 | 60.2695 | 62.798 | 64.7217 | 65.0206 | 62.5934 | 58.2102 | 123.1338 | 61.7217 | 123.0422 | 61.4629 | 61.5396 | 123.1216 | 61.4991 | 122.9044 | 61.5942 | 61.6347 | 61.5025 | 61.543
6424.0625 | 123.2895 | -61.5189 | 61.6104 | 0.14932 | -1.3226 | 1.1601 | 2.9739 | 3.2042 | 0.84102 | -3.3453 | 61.6607 | 0.22574 | 61.5874 | -0.023943 | 0.039079 | 61.6257 | 0.012299 | 61.3947 | 61.6682 | 60.1963 | 62.679 | 64.4928 | 64.7231 | 62.3599 | 58.1736 | 123.1796 | 61.7446 | 123.1062 | 61.4949 | 61.5579 | 123.1445 | 61.5312 | 122.9136 | 61.6216 | 61.6484 | 61.5483 | 61.5751
6425.0781 | 123.2986 | -61.5051 | 61.6241 | 0.14017 | -1.3272 | 1.1601 | 2.951 | 3.1539 | 0.81812 | -3.359 | 61.6653 | 0.22574 | 61.5645 | -0.023943 | 0.043657 | 61.6165 | 0.016878 | 61.413 | 61.6453 | 60.178 | 62.6653 | 64.4561 | 64.659 | 62.3233 | 58.1461 | 123.1704 | 61.7309 | 123.0696 | 61.4812 | 61.5488 | 123.1216 | 61.522 | 122.9181 | 61.6216 | 61.6484 | 61.5208 | 61.5476
6426.0625 | 123.3307 | -61.5097 | 61.5738 | 0.26378 | -1.1486 | 1.2929 | 3.0792 | 3.2958 | 0.9509 | -3.153 | 61.6516 | 0.22574 | 61.5599 | -0.028522 | 0.052814 | 61.6257 | 0.007721 | 61.4039 | 61.7735 | 60.3611 | 62.8026 | 64.5889 | 64.8055 | 62.4606 | 58.3567 | 123.1613 | 61.7354 | 123.0696 | 61.4812 | 61.5625 | 123.1354 | 61.5174 | 122.9136 | 61.5987 | 61.6438 | 61.5071 | 61.5522
6427.0938 | 123.262 | -61.5417 | 61.615 | 0.19511 | -1.2173 | 1.1922 | 2.9602 | 3.1767 | 0.90054 | -3.2354 | 61.6653 | 0.22574 | 61.5965 | -0.033101 | 0.048236 | 61.6257 | 0.003143 | 61.4039 | 61.7369 | 60.3245 | 62.7339 | 64.5019 | 64.7185 | 62.4423 | 58.3064 | 123.207 | 61.7675 | 123.1383 | 61.5086 | 61.59 | 123.1674 | 61.5449 | 122.9456 | 61.6171 | 61.6622 | 61.5483 | 61.5934
6428.0625 | 123.3536 | -61.5051 | 61.5692 | 0.13559 | -1.2905 | 1.0777 | 2.8869 | 3.1767 | 0.89138 | -3.327 | 61.6561 | 0.21658 | 61.5645 | -0.03768 | 0.039079 | 61.6211 | 0.007721 | 61.3901 | 61.6407 | 60.2146 | 62.5828 | 64.392 | 64.6819 | 62.3965 | 58.1782 | 123.1613 | 61.7217 | 123.0696 | 61.4674 | 61.5442 | 123.1262 | 61.5128 | 122.8953 | 61.6171 | 61.6484 | 61.5254 | 61.5568
6429.0938 | 123.2758 | -61.5097 | 61.6241 | 0.25462 | -1.1165 | 1.2151 | 2.9739 | 3.2317 | 0.9921 | -3.0935 | 61.6516 | 0.23032 | 61.5645 | -0.028522 | 0.052814 | 61.6211 | 0.003143 | 61.413 | 61.7643 | 60.3932 | 62.7248 | 64.4836 | 64.7414 | 62.5018 | 58.4162 | 123.1613 | 61.74 | 123.0742 | 61.4812 | 61.5625 | 123.1308 | 61.5128 | 122.9227 | 61.5987 | 61.6484 | 61.5117 | 61.5614
6430.0625 | 123.3673 | -61.4868 | 61.5509 | 0.20426 | -1.1669 | 1.1647 | 2.9464 | 3.2134 | 0.90054 | -3.1759 | 61.647 | 0.23032 | 61.5782 | -0.033101 | 0.048236 | 61.6165 | 0.012299 | 61.413 | 61.6911 | 60.3199 | 62.6515 | 64.4332 | 64.7002 | 62.3874 | 58.3109 | 123.1338 | 61.7171 | 123.065 | 61.4537 | 61.5351 | 123.1033 | 61.4991 | 122.8998 | 61.5987 | 61.6347 | 61.53 | 61.5659
6431.0938 | 123.3444 | -61.4822 | 61.6241 | 0.11727 | -1.2722 | 1.0457 | 2.8091 | 3.0577 | 0.84559 | -3.2262 | 61.6607 | 0.22574 | 61.5599 | -0.028522 | 0.052814 | 61.6119 | 0.012299 | 61.4176 | 61.5995 | 60.21 | 62.5279 | 64.2913 | 64.54 | 62.3278 | 58.256 | 123.143 | 61.708 | 123.0422 | 61.4537 | 61.5351 | 123.0942 | 61.4945 | 122.8998 | 61.6079 | 61.6484 | 61.5071 | 61.5476
6432.0625 | 123.3582 | -61.5097 | 61.5921 | 0.17221 | -1.2081 | 1.0914 | 2.8503 | 3.1218 | 0.91885 | -3.185 | 61.6516 | 0.22116 | 61.5782 | -0.033101 | 0.048236 | 61.6211 | 0.012299 | 61.4222 | 61.6819 | 60.3016 | 62.6011 | 64.36 | 64.6315 | 62.4286 | 58.3247 | 123.1613 | 61.7309 | 123.0879 | 61.4766 | 61.5579 | 123.1308 | 61.522 | 122.9319 | 61.6033 | 61.6393 | 61.53 | 61.5659
6433.0938 | 123.3215 | -61.5234 | 61.6058 | -0.061284 | -1.46 | 0.80299 | 2.5389 | 2.783 | 0.62583 | -3.4323 | 61.6699 | 0.2349 | 61.5965 | -0.028522 | 0.048236 | 61.6028 | 0.012299 | 61.3993 | 61.4622 | 60.0635 | 62.3264 | 64.0624 | 64.3065 | 62.1493 | 58.0912 | 123.1933 | 61.7583 | 123.12 | 61.4949 | 61.5717 | 123.1262 | 61.5357 | 122.9227 | 61.6216 | 61.6576 | 61.5483 | 61.5842
6434.0625 | 123.3856 | -61.4777 | 61.5784 | -0.070441 | -1.4462 | 0.78926 | 2.516 | 2.7693 | 0.64872 | -3.391 | 61.6653 | 0.22116 | 61.5828 | -0.033101 | 0.048236 | 61.6028 | 0.012299 | 61.3993 | 61.4072 | 60.0314 | 62.2669 | 63.9937 | 64.247 | 62.1264 | 58.0866 | 123.143 | 61.6988 | 123.0605 | 61.4446 | 61.5259 | 123.0804 | 61.49 | 122.8769 | 61.6171 | 61.653 | 61.5346 | 61.5705
6435.0781 | 123.3353 | -61.4777 | 61.6425 | -0.18032 | -1.5882 | 0.64274 | 2.3558 | 2.5908 | 0.51595 | -3.5101 | 61.6836 | 0.2349 | 61.6194 | -0.028522 | 0.048236 | 61.5936 | 0.003143 | 61.3993 | 61.2973 | 59.8895 | 62.1204 | 63.8335 | 64.0684 | 61.9936 | 57.9676 | 123.1613 | 61.7126 | 123.0971 | 61.4491 | 61.5259 | 123.0713 | 61.4808 | 122.8769 | 61.6354 | 61.6805 | 61.5712 | 61.6163
6436.0625 | 123.3719 | -61.4822 | 61.5967 | -0.006344 | -1.3592 | 0.82588 | 2.4977 | 2.7052 | 0.65788 | -3.2171 | 61.6699 | 0.22574 | 61.5828 | -0.028522 | 0.048236 | 61.6028 | 0.007721 | 61.3856 | 61.4759 | 60.123 | 62.3081 | 63.98 | 64.1875 | 62.1401 | 58.2652 | 123.1521 | 61.708 | 123.065 | 61.4537 | 61.5305 | 123.085 | 61.49 | 122.8678 | 61.6216 | 61.6622 | 61.5346 | 61.5751
6437.0938 | 123.2986 | -61.4777 | 61.6379 | -0.16659 | -1.547 | 0.61985 | 2.2825 | 2.4946 | 0.51137 | -3.4643 | 61.6836 | 0.22574 | 61.5874 | -0.028522 | 0.043657 | 61.5936 | 0.012299 | 61.3764 | 61.3111 | 59.9307 | 62.0975 | 63.7602 | 63.9723 | 61.989 | 58.0134 | 123.1613 | 61.7034 | 123.065 | 61.4491 | 61.5213 | 123.0713 | 61.49 | 122.8541 | 61.64 | 61.6713 | 61.5437 | 61.5751
6438.0625 | 123.3627 | -61.4731 | 61.5875 | -0.1208 | -1.4828 | 0.68853 | 2.3421 | 2.5541 | 0.4839 | -3.4094 | 61.6699 | 0.2349 | 61.6103 | -0.033101 | 0.048236 | 61.5891 | 0.007721 | 61.3764 | 61.3523 | 59.9902 | 62.1616 | 63.8151 | 64.0272 | 61.957 | 58.0637 | 123.143 | 61.708 | 123.0834 | 61.44 | 61.5213 | 123.0621 | 61.4808 | 122.8495 | 61.6216 | 61.6622 | 61.562 | 61.6026
6439.0781 | 123.2803 | -61.4868 | 61.6562 | -0.20779 | -1.6065 | 0.5649 | 2.2093 | 2.4626 | 0.46101 | -3.4826 | 61.679 | 0.22574 | 61.5874 | -0.033101 | 0.034501 | 61.5936 | 0.012299 | 61.381 | 61.279 | 59.8803 | 62.0517 | 63.6961 | 63.9494 | 61.9478 | 58.0042 | 123.1658 | 61.7126 | 123.0742 | 61.4537 | 61.5213 | 123.0804 | 61.4991 | 122.8678 | 61.6445 | 61.6667 | 61.5529 | 61.5751
6440.0625 | 123.3856 | -61.4594 | 61.5967 | -0.15743 | -1.5149 | 0.62443 | 2.2413 | 2.4901 | 0.55258 | -3.3315 | 61.6745 | 0.22574 | 61.5828 | -0.023943 | 0.034501 | 61.5982 | 0.003143 | 61.3764 | 61.3019 | 59.9445 | 62.0838 | 63.7007 | 63.9494 | 62.0119 | 58.1278 | 123.1338 | 61.6851 | 123.0422 | 61.4354 | 61.4939 | 123.0576 | 61.4625 | 122.8357 | 61.64 | 61.6713 | 61.5483 | 61.5797
6441.1094 | 123.262 | -61.4777 | 61.6425 | -0.24442 | -1.6294 | 0.50996 | 2.104 | 2.339 | 0.54342 | -3.3636 | 61.6836 | 0.22574 | 61.6286 | -0.028522 | 0.039079 | 61.5982 | 0.007721 | 61.3764 | 61.2332 | 59.8483 | 61.9876 | 63.5816 | 63.8166 | 62.0211 | 58.1141 | 123.1613 | 61.7034 | 123.1063 | 61.4491 | 61.5167 | 123.0759 | 61.4854 | 122.8541 | 61.6445 | 61.6759 | 61.5895 | 61.6209
6442.0625 | 123.3536 | -61.4594 | 61.6058 | -0.27189 | -1.666 | 0.46418 | 2.0857 | 2.3436 | 0.47017 | -3.4231 | 61.6836 | 0.23032 | 61.5828 | -0.033101 | 0.048236 | 61.5891 | 0.012299 | 61.3672 | 61.1875 | 59.7933 | 61.9235 | 63.545 | 63.8029 | 61.9295 | 58.0363 | 123.143 | 61.6897 | 123.0422 | 61.4262 | 61.5076 | 123.0484 | 61.4716 | 122.8266 | 61.6354 | 61.6713 | 61.5346 | 61.5705
6443.0938 | 123.2849 | -61.4914 | 61.647 | -0.21695 | -1.5927 | 0.54659 | 2.1635 | 2.4351 | 0.48848 | -3.3865 | 61.6836 | 0.2349 | 61.6103 | -0.028522 | 0.052814 | 61.5845 | 0.012299 | 61.3856 | 61.2744 | 59.8987 | 62.038 | 63.6549 | 63.9265 | 61.9799 | 58.1049 | 123.175 | 61.7263 | 123.1017 | 61.4629 | 61.5442 | 123.0759 | 61.5037 | 122.8769 | 61.6308 | 61.6713 | 61.5575 | 61.598
6444.0625 | 123.3994 | -61.4685 | 61.6013 | -0.10707 | -1.4554 | 0.66563 | 2.2505 | 2.4946 | 0.63041 | -3.1805 | 61.679 | 0.22574 | 61.592 | -0.023943 | 0.048236 | 61.5891 | 0.007721 | 61.381 | 61.3614 | 60.0131 | 62.1341 | 63.719 | 63.9631 | 62.0989 | 58.2881 | 123.1475 | 61.6942 | 123.0605 | 61.4446 | 61.5167 | 123.0576 | 61.4762 | 122.8495 | 61.6308 | 61.6713 | 61.5437 | 61.5842
6445.0938 | 123.2849 | -61.4868 | 61.6241 | -0.17574 | -1.5012 | 0.5878 | 2.1727 | 2.4076 | 0.61668 | -3.2537 | 61.679 | 0.22574 | 61.5782 | -0.023943 | 0.043657 | 61.5936 | 0.007721 | 61.3764 | 61.3111 | 59.9857 | 62.0746 | 63.6595 | 63.8945 | 62.1035 | 58.2331 | 123.1658 | 61.7126 | 123.065 | 61.4629 | 61.5305 | 123.0804 | 61.4945 | 122.8632 | 61.6354 | 61.6713 | 61.5346 | 61.5705
6446.0625 | 123.3582 | -61.4731 | 61.615 | -0.4596 | -1.8079 | 0.24898 | 1.7835 | 2.0002 | 0.26872 | -3.565 | 61.7065 | 0.22574 | 61.6423 | -0.028522 | 0.043657 | 61.5662 | 0.007721 | 61.3535 | 61.0135 | 59.6651 | 61.7221 | 63.2566 | 63.4733 | 61.7418 | 57.9081 | 123.1796 | 61.6988 | 123.1154 | 61.4446 | 61.5167 | 123.0392 | 61.4808 | 122.8266 | 61.6628 | 61.6988 | 61.5987 | 61.6346
6447.0938 | 123.2895 | -61.4365 | 61.6837 | -0.69768 | -2.0277 | -0.002842 | 1.4447 | 1.6111 | -0.038034 | -3.8077 | 61.7157 | 0.22574 | 61.6332 | -0.023943 | 0.048236 | 61.557 | 0.012299 | 61.3489 | 60.7388 | 59.4087 | 61.4336 | 62.8811 | 63.0475 | 61.3984 | 57.6288 | 123.1521 | 61.6622 | 123.0696 | 61.4125 | 61.4847 | 122.9935 | 61.4488 | 122.7854 | 61.6674 | 61.7034 | 61.5849 | 61.6209
6448.0625 | 123.317 | -61.4594 | 61.647 | -0.61985 | -2.0003 | 0.052101 | 1.6095 | 1.8491 | 0.076426 | -3.8214 | 61.7065 | 0.22116 | 61.6194 | -0.028522 | 0.043657 | 61.5662 | 0.003143 | 61.3535 | 60.8395 | 59.4591 | 61.5115 | 63.0689 | 63.3085 | 61.5358 | 57.638 | 123.1659 | 61.6805 | 123.0788 | 61.4308 | 61.503 | 123.0255 | 61.4625 | 122.8129 | 61.6628 | 61.7034 | 61.5758 | 61.6163
6449.0625 | 123.2574 | -61.4594 | 61.6791 | -0.55575 | -1.9041 | 0.10247 | 1.6507 | 1.872 | 0.17715 | -3.6886 | 61.7065 | 0.23032 | 61.6469 | -0.03768 | 0.043657 | 61.5616 | 0.012299 | 61.3535 | 60.9036 | 59.5553 | 61.5618 | 63.1101 | 63.3314 | 61.6365 | 57.7707 | 123.1659 | 61.6897 | 123.1063 | 61.4217 | 61.503 | 123.0209 | 61.4716 | 122.8129 | 61.6628 | 61.6942 | 61.6032 | 61.6346
6450.0781 | 123.2437 | -61.441 | 61.6928 | -0.6931 | -2.0369 | -0.039471 | 1.4584 | 1.6706 | 0.044377 | -3.7939 | 61.7111 | 0.23032 | 61.6103 | -0.023943 | 0.048236 | 61.5662 | 0.007721 | 61.3535 | 60.7479 | 59.4042 | 61.4016 | 62.8995 | 63.1116 | 61.4854 | 57.6471 | 123.1521 | 61.6714 | 123.0513 | 61.4171 | 61.4893 | 123.0072 | 61.4488 | 122.7945 | 61.6628 | 61.7034 | 61.562 | 61.6026
6451.0625 | 123.3719 | -61.4227 | 61.6562 | -0.8625 | -2.1559 | -0.22262 | 1.1059 | 1.2265 | -0.12044 | -3.8077 | 61.7202 | 0.22116 | 61.6332 | -0.033101 | 0.048236 | 61.5478 | 0.003143 | 61.3352 | 60.5602 | 59.2668 | 61.2001 | 62.5286 | 62.6493 | 61.3023 | 57.6151 | 123.143 | 61.6439 | 123.0559 | 61.3896 | 61.471 | 122.9706 | 61.4259 | 122.7579 | 61.672 | 61.7171 | 61.5849 | 61.63
6452.0938 | 123.3215 | -61.4456 | 61.7111 | -0.73889 | -2.0644 | -0.085257 | 1.3119 | 1.4783 | -0.056347 | -3.8168 | 61.7248 | 0.23032 | 61.6469 | -0.028522 | 0.048236 | 61.5524 | 0.007721 | 61.3398 | 60.7067 | 59.3813 | 61.3604 | 62.7575 | 62.9239 | 61.3893 | 57.6288 | 123.1704 | 61.6759 | 123.0925 | 61.4171 | 61.4939 | 122.998 | 61.4533 | 122.7854 | 61.6766 | 61.7171 | 61.5987 | 61.6392
6453.0625 | 123.2529 | -61.4822 | 61.7065 | -0.90371 | -2.22 | -0.26382 | 1.1013 | 1.2403 | -0.18912 | -3.9542 | 61.7248 | 0.23032 | 61.6286 | -0.023943 | 0.048236 | 61.5387 | 0.003143 | 61.3306 | 60.5785 | 59.2622 | 61.2184 | 62.5835 | 62.7225 | 61.2931 | 57.5281 | 123.2071 | 61.7126 | 123.1108 | 61.4583 | 61.5305 | 123.0209 | 61.4854 | 122.8129 | 61.6766 | 61.7217 | 61.5804 | 61.6255
6454.0781 | 123.2941 | -61.409 | 61.734 | -1.0136 | -2.2979 | -0.40118 | 0.8861 | 0.99306 | -0.27611 | -3.9954 | 61.734 | 0.2349 | 61.6698 | -0.03768 | 0.048236 | 61.5387 | 0.016878 | 61.326 | 60.3954 | 59.1111 | 61.0078 | 62.2951 | 62.4021 | 61.1329 | 57.4136 | 123.143 | 61.6439 | 123.0788 | 61.3713 | 61.4572 | 122.9477 | 61.4259 | 122.735 | 61.6857 | 61.7171 | 61.6216 | 61.6529
6455.0625 | 123.2803 | -61.4273 | 61.6928 | -0.67021 | -1.9362 | -0.053207 | 1.3165 | 1.4554 | 0.00775 | -3.6337 | 61.7157 | 0.23032 | 61.6286 | -0.028522 | 0.039079 | 61.5616 | 0.007721 | 61.3443 | 60.7571 | 59.4912 | 61.3741 | 62.7438 | 62.8827 | 61.4351 | 57.7936 | 123.143 | 61.6576 | 123.0559 | 61.3988 | 61.4664 | 122.9889 | 61.435 | 122.7717 | 61.6766 | 61.7079 | 61.5895 | 61.6209
6456.1094 | 123.2895 | -61.409 | 61.7432 | -0.97238 | -2.2017 | -0.36455 | 0.79453 | 0.84656 | -0.2349 | -3.771 | 61.7431 | 0.22574 | 61.6377 | -0.023943 | 0.052814 | 61.5387 | 0.007721 | 61.3306 | 60.4366 | 59.2073 | 61.0444 | 62.2035 | 62.2556 | 61.1741 | 57.638 | 123.1521 | 61.6347 | 123.0467 | 61.3851 | 61.4618 | 122.9477 | 61.4167 | 122.7396 | 61.6903 | 61.7354 | 61.5849 | 61.63
6457.0625 | 123.2666 | -61.4731 | 61.6745 | -0.86708 | -2.0827 | -0.26382 | 0.8861 | 0.91523 | -0.18912 | -3.5971 | 61.734 | 0.22574 | 61.6652 | -0.028522 | 0.052814 | 61.5433 | 0.012299 | 61.3352 | 60.606 | 59.3904 | 61.2093 | 62.3592 | 62.3883 | 61.284 | 57.876 | 123.2071 | 61.6988 | 123.1383 | 61.4446 | 61.5259 | 123.0164 | 61.4854 | 122.8083 | 61.6812 | 61.7217 | 61.6124 | 61.6529
6458.0781 | 123.3398 | -61.3861 | 61.7157 | -1.1235 | -2.3574 | -0.55685 | 0.5244 | 0.53068 | -0.38599 | -3.7756 | 61.7386 | 0.23032 | 61.6469 | -0.028522 | 0.052814 | 61.5295 | 0.012299 | 61.3169 | 60.2626 | 59.0287 | 60.8293 | 61.9105 | 61.9168 | 61.0001 | 57.6105 | 123.1247 | 61.6164 | 123.033 | 61.3576 | 61.4389 | 122.9156 | 61.3984 | 122.703 | 61.6857 | 61.7263 | 61.5941 | 61.6346
6459.0625 | 123.3032 | -61.3907 | 61.7523 | -1.2471 | -2.4902 | -0.66674 | 0.41452 | 0.42539 | -0.49587 | -3.9542 | 61.7523 | 0.2349 | 61.6698 | -0.033101 | 0.043657 | 61.5158 | 0.007721 | 61.3123 | 60.1436 | 58.9005 | 60.7239 | 61.8052 | 61.8161 | 60.8948 | 57.4365 | 123.143 | 61.6256 | 123.0605 | 61.3576 | 61.4343 | 122.9065 | 61.3984 | 122.703 | 61.7086 | 61.7446 | 61.6261 | 61.6621
6460.0781 | 123.2071 | -61.3998 | 61.7615 | -1.2334 | -2.4673 | -0.67132 | 0.38247 | 0.37961 | -0.49129 | -3.945 | 61.7569 | 0.23032 | 61.6927 | -0.028522 | 0.052814 | 61.5204 | 0.012299 | 61.326 | 60.1665 | 58.9325 | 60.7285 | 61.7823 | 61.7795 | 60.9085 | 57.4548 | 123.1567 | 61.6302 | 123.0925 | 61.3713 | 61.4527 | 122.9202 | 61.4121 | 122.7259 | 61.7041 | 61.7446 | 61.6399 | 61.6804
6461.0625 | 123.381 | -61.3998 | 61.7065 | -1.3524 | -2.5818 | -0.8041 | 0.28632 | 0.28805 | -0.54624 | -4.119 | 61.7614 | 0.22574 | 61.6652 | -0.028522 | 0.039079 | 61.5158 | 0.003143 | 61.3123 | 60.0475 | 58.8181 | 60.5957 | 61.6862 | 61.6879 | 60.8536 | 57.2809 | 123.1613 | 61.6256 | 123.0651 | 61.3713 | 61.4389 | 122.9156 | 61.403 | 122.7121 | 61.7224 | 61.7583 | 61.6261 | 61.6621
6462.0938 | 123.2712 | -61.4044 | 61.7386 | -1.2974 | -2.5222 | -0.76747 | 0.29548 | 0.31552 | -0.49129 | -4.0091 | 61.7614 | 0.23948 | 61.6927 | -0.033101 | 0.052814 | 61.5158 | 0.012299 | 61.3169 | 60.107 | 58.8822 | 60.6369 | 61.6999 | 61.7199 | 60.9131 | 57.3953 | 123.1659 | 61.6439 | 123.0971 | 61.3713 | 61.4572 | 122.9202 | 61.4167 | 122.7213 | 61.7086 | 61.7491 | 61.6399 | 61.6804
6463.0625 | 123.3307 | -61.3861 | 61.7569 | -1.357 | -2.5451 | -0.82241 | 0.22222 | 0.19192 | -0.55539 | -4.0137 | 61.7569 | 0.23032 | 61.6881 | -0.023943 | 0.048236 | 61.5158 | 0.007721 | 61.3306 | 60.0291 | 58.841 | 60.5637 | 61.6083 | 61.578 | 60.8307 | 57.3724 | 123.143 | 61.6164 | 123.0742 | 61.3622 | 61.4343 | 122.9019 | 61.3938 | 122.7167 | 61.7086 | 61.7491 | 61.6399 | 61.6804
6464.0781 | 123.3261 | -61.377 | 61.7249 | -1.1921 | -2.3666 | -0.63469 | 0.40078 | 0.36588 | -0.43635 | -3.8443 | 61.7431 | 0.22116 | 61.6652 | -0.028522 | 0.052814 | 61.525 | 0.003143 | 61.3352 | 60.1848 | 59.0104 | 60.7423 | 61.7777 | 61.7428 | 60.9406 | 57.5327 | 123.1201 | 61.5981 | 123.0422 | 61.3484 | 61.4298 | 122.9019 | 61.3801 | 122.7121 | 61.6903 | 61.74 | 61.6124 | 61.6621
6465.0625 | 123.2437 | -61.3998 | 61.7798 | -1.302 | -2.4856 | -0.76289 | 0.24054 | 0.18734 | -0.51876 | -3.9221 | 61.7614 | 0.2349 | 61.6973 | -0.033101 | 0.043657 | 61.5112 | 0.012299 | 61.326 | 60.0978 | 58.9142 | 60.637 | 61.6404 | 61.5872 | 60.8811 | 57.4777 | 123.1613 | 61.6347 | 123.0971 | 61.3667 | 61.4435 | 122.9111 | 61.4121 | 122.7259 | 61.7178 | 61.7491 | 61.6536 | 61.685
6466.0938 | 123.3627 | -61.4273 | 61.6928 | -1.0365 | -2.275 | -0.49275 | 0.6526 | 0.70922 | -0.23033 | -3.739 | 61.734 | 0.21658 | 61.6469 | -0.028522 | 0.057392 | 61.5295 | 0.012299 | 61.3306 | 60.3908 | 59.1523 | 60.9346 | 62.0799 | 62.1365 | 61.197 | 57.6883 | 123.1613 | 61.6439 | 123.0742 | 61.3988 | 61.4847 | 122.9568 | 61.4396 | 122.7579 | 61.6766 | 61.7217 | 61.5895 | 61.6346
6467.0625 | 123.3032 | -61.3861 | 61.7249 | -1.2837 | -2.4719 | -0.74458 | 0.29548 | 0.25143 | -0.51876 | -3.8946 | 61.7614 | 0.22574 | 61.679 | -0.028522 | 0.048236 | 61.5204 | 0.007721 | 61.3169 | 60.1024 | 58.9142 | 60.6415 | 61.6816 | 61.6375 | 60.8673 | 57.4915 | 123.1476 | 61.6118 | 123.0651 | 61.3576 | 61.4343 | 122.9065 | 61.3938 | 122.703 | 61.7132 | 61.7537 | 61.6307 | 61.6712
6468.0625 | 123.2712 | -61.3998 | 61.7523 | -1.1693 | -2.3666 | -0.61638 | 0.47404 | 0.46659 | -0.38141 | -3.8306 | 61.7706 | 0.22574 | 61.679 | -0.028522 | 0.052814 | 61.525 | 0.007721 | 61.326 | 60.2306 | 59.0333 | 60.7835 | 61.8739 | 61.8664 | 61.0184 | 57.5693 | 123.1704 | 61.6256 | 123.0788 | 61.3713 | 61.4527 | 122.9248 | 61.4076 | 122.7259 | 61.7178 | 61.7629 | 61.6261 | 61.6712
6469.0781 | 123.3856 | -61.3907 | 61.6882 | -1.1967 | -2.4032 | -0.67132 | 0.42825 | 0.4437 | -0.34936 | -3.8626 | 61.7523 | 0.21658 | 61.6515 | -0.023943 | 0.048236 | 61.5204 | 0.012299 | 61.3215 | 60.194 | 58.9875 | 60.7194 | 61.8189 | 61.8344 | 61.0413 | 57.5281 | 123.143 | 61.6073 | 123.0422 | 61.3667 | 61.4389 | 122.9111 | 61.403 | 122.7121 | 61.7041 | 61.74 | 61.6032 | 61.6392
6470.0625 | 123.2849 | -61.409 | 61.7706 | -1.3432 | -2.481 | -0.8682 | 0.14897 | 0.10493 | -0.52792 | -3.9862 | 61.766 | 0.22574 | 61.7018 | -0.028522 | 0.048236 | 61.5112 | 0.012299 | 61.3031 | 60.0658 | 58.928 | 60.5408 | 61.558 | 61.5139 | 60.8811 | 57.4228 | 123.175 | 61.6347 | 123.1108 | 61.3805 | 61.4572 | 122.9202 | 61.4213 | 122.7121 | 61.7178 | 61.7537 | 61.6536 | 61.6895
6471.0938 | 123.3398 | -61.409 | 61.7294 | -1.4531 | -2.5863 | -0.98266 | 0.002454 | -0.059872 | -0.65154 | -4.0503 | 61.7706 | 0.22574 | 61.679 | -0.028522 | 0.048236 | 61.5066 | 0.012299 | 61.3031 | 59.9559 | 58.8227 | 60.4263 | 61.4115 | 61.3491 | 60.7575 | 57.3587 | 123.1796 | 61.6347 | 123.088 | 61.3805 | 61.4572 | 122.9156 | 61.4213 | 122.7121 | 61.7224 | 61.7583 | 61.6307 | 61.6667
6472.0625 | 123.3032 | -61.3861 | 61.7889 | -1.5722 | -2.7512 | -1.1521 | -0.089116 | -0.10107 | -0.68359 | -4.2151 | 61.7706 | 0.22574 | 61.6835 | -0.023943 | 0.052814 | 61.5021 | 0.007721 | 61.2894 | 59.814 | 58.6349 | 60.234 | 61.297 | 61.285 | 60.7025 | 57.171 | 123.1567 | 61.6118 | 123.0696 | 61.3622 | 61.4389 | 122.8882 | 61.3938 | 122.6755 | 61.7178 | 61.7629 | 61.6307 | 61.6758
6473.0625 | 123.3353 | -61.3953 | 61.7386 | -1.5447 | -2.6825 | -1.1017 | -0.089116 | -0.12396 | -0.72479 | -4.151 | 61.7752 | 0.22574 | 61.7064 | -0.023943 | 0.048236 | 61.5021 | 0.012299 | 61.2986 | 59.8506 | 58.7128 | 60.2936 | 61.3061 | 61.2713 | 60.6705 | 57.2442 | 123.1704 | 61.621 | 123.1017 | 61.3713 | 61.4435 | 122.8973 | 61.4076 | 122.6938 | 61.7269 | 61.7629 | 61.6582 | 61.6941
6474.0781 | 123.4039 | -61.3724 | 61.7065 | -1.4806 | -2.5955 | -1.033 | -0.043331 | -0.078184 | -0.66985 | -4.0412 | 61.7752 | 0.22574 | 61.6744 | -0.033101 | 0.048236 | 61.5021 | 0.012299 | 61.294 | 59.8918 | 58.7769 | 60.3393 | 61.329 | 61.2942 | 60.7025 | 57.3312 | 123.1476 | 61.5981 | 123.0468 | 61.3393 | 61.4206 | 122.8744 | 61.3847 | 122.6664 | 61.7269 | 61.7629 | 61.6261 | 61.6621
6475.0625 | 123.2941 | -61.3907 | 61.7386 | -1.5264 | -2.6733 | -1.0925 | -0.052488 | -0.055294 | -0.66527 | -4.1419 | 61.7706 | 0.23032 | 61.6881 | -0.028522 | 0.048236 | 61.5021 | 0.007721 | 61.294 | 59.8643 | 58.7173 | 60.2981 | 61.3382 | 61.3354 | 60.7254 | 57.2488 | 123.1613 | 61.621 | 123.0788 | 61.3622 | 61.4389 | 122.8928 | 61.3984 | 122.6847 | 61.7224 | 61.7629 | 61.6399 | 61.6804
6476.1094 | 123.3398 | -61.3907 | 61.6699 | -1.2517 | -2.4215 | -0.78578 | 0.355 | 0.42539 | -0.42262 | -3.9221 | 61.7614 | 0.22574 | 61.6835 | -0.033101 | 0.034501 | 61.525 | 0.003143 | 61.3031 | 60.139 | 58.9692 | 60.6049 | 61.7457 | 61.8161 | 60.9681 | 57.4686 | 123.1521 | 61.6164 | 123.0742 | 61.3576 | 61.4252 | 122.9156 | 61.3938 | 122.6938 | 61.7269 | 61.7583 | 61.649 | 61.6804
6477.0625 | 123.3582 | -61.3724 | 61.734 | -1.1464 | -2.2933 | -0.653 | 0.44199 | 0.47575 | -0.32189 | -3.7619 | 61.7477 | 0.22116 | 61.6469 | -0.028522 | 0.048236 | 61.525 | 0.007721 | 61.3215 | 60.226 | 59.0791 | 60.7194 | 61.8144 | 61.8481 | 61.0505 | 57.6105 | 123.1201 | 61.5935 | 123.0193 | 61.3439 | 61.4206 | 122.8973 | 61.3801 | 122.6938 | 61.6995 | 61.74 | 61.5987 | 61.6392
6478.0625 | 123.2758 | -61.4365 | 61.6928 | -1.3158 | -2.4581 | -0.84073 | 0.26801 | 0.28347 | -0.50045 | -3.9633 | 61.7614 | 0.23032 | 61.6927 | -0.019364 | 0.048236 | 61.5158 | 0.012299 | 61.2986 | 60.1207 | 58.9783 | 60.5957 | 61.7045 | 61.7199 | 60.936 | 57.4731 | 123.1979 | 61.6668 | 123.1292 | 61.4171 | 61.4847 | 122.9523 | 61.4488 | 122.735 | 61.7132 | 61.7491 | 61.6445 | 61.6804
6479.0625 | 123.2941 | -61.3998 | 61.7661 | -1.2654 | -2.4261 | -0.8041 | 0.33668 | 0.39792 | -0.40888 | -3.8946 | 61.7523 | 0.22574 | 61.6698 | -0.019364 | 0.043657 | 61.525 | 0.003143 | 61.3215 | 60.1344 | 58.9738 | 60.5957 | 61.7365 | 61.7978 | 60.991 | 57.5052 | 123.1521 | 61.6256 | 123.0696 | 61.3805 | 61.4435 | 122.9248 | 61.403 | 122.7213 | 61.7086 | 61.7491 | 61.6261 | 61.6667
6480.0781 | 123.3261 | -61.4136 | 61.6745 | -1.2288 | -2.3803 | -0.77663 | 0.34584 | 0.4437 | -0.32647 | -3.8214 | 61.7477 | 0.21658 | 61.6652 | -0.019364 | 0.052814 | 61.525 | 0.003143 | 61.3215 | 60.1848 | 59.0333 | 60.6369 | 61.7594 | 61.8573 | 61.0871 | 57.5922 | 123.1613 | 61.6302 | 123.0788 | 61.3942 | 61.4664 | 122.9385 | 61.4167 | 122.735 | 61.6949 | 61.7446 | 61.6124 | 61.6621
6481.0625 | 123.2437 | -61.4182 | 61.702 | -1.1693 | -2.3025 | -0.71253 | 0.38705 | 0.4437 | -0.34021 | -3.7573 | 61.7523 | 0.22574 | 61.6652 | -0.028522 | 0.052814 | 61.525 | 0.012299 | 61.326 | 60.2489 | 59.1157 | 60.7056 | 61.8052 | 61.8619 | 61.0779 | 57.6608 | 123.1704 | 61.6439 | 123.0834 | 61.3896 | 61.471 | 122.9431 | 61.4305 | 122.7442 | 61.6995 | 61.74 | 61.6124 | 61.6529
6482.0781 | 123.3856 | -61.4044 | 61.6745 | -1.128 | -2.2567 | -0.6759 | 0.3962 | 0.44828 | -0.31274 | -3.652 | 61.7431 | 0.22574 | 61.6606 | -0.028522 | 0.052814 | 61.525 | 0.007721 | 61.3123 | 60.2764 | 59.1478 | 60.7285 | 61.8006 | 61.8527 | 61.0917 | 57.7524 | 123.1476 | 61.6302 | 123.0651 | 61.3759 | 61.4572 | 122.9294 | 61.4121 | 122.7167 | 61.6903 | 61.7354 | 61.6078 | 61.6529
6483.0625 | 123.2483 | -61.4365 | 61.702 | -1.128 | -2.2612 | -0.68505 | 0.40536 | 0.4437 | -0.299 | -3.6841 | 61.7477 | 0.22574 | 61.6744 | -0.033101 | 0.057392 | 61.525 | 0.012299 | 61.326 | 60.3084 | 59.1752 | 60.7514 | 61.8418 | 61.8802 | 61.1375 | 57.7524 | 123.1842 | 61.6622 | 123.1108 | 61.4034 | 61.4939 | 122.9614 | 61.4488 | 122.7625 | 61.6903 | 61.7354 | 61.617 | 61.6621
6484.0938 | 123.3536 | -61.3907 | 61.647 | -1.2379 | -2.3528 | -0.83615 | 0.23596 | 0.26974 | -0.34936 | -3.7207 | 61.7614 | 0.22116 | 61.6652 | -0.028522 | 0.048236 | 61.5158 | 0.007721 | 61.3123 | 60.1528 | 59.0379 | 60.5545 | 61.6266 | 61.6604 | 61.0413 | 57.67 | 123.1521 | 61.6118 | 123.0559 | 61.3622 | 61.4389 | 122.9065 | 61.3984 | 122.703 | 61.7132 | 61.7537 | 61.617 | 61.6575
6485.0625 | 123.3261 | -61.409 | 61.6882 | -0.85792 | -1.9362 | -0.42865 | 0.6526 | 0.69549 | -0.060926 | -3.2903 | 61.7294 | 0.22574 | 61.6469 | -0.023943 | 0.052814 | 61.5478 | 0.007721 | 61.3352 | 60.5511 | 59.4728 | 60.9803 | 62.0616 | 62.1045 | 61.3481 | 58.1187 | 123.1384 | 61.6347 | 123.0559 | 61.3851 | 61.4618 | 122.9568 | 61.4167 | 122.7442 | 61.6766 | 61.7217 | 61.5941 | 61.6392
6486.0938 | 123.349 | -61.4227 | 61.6653 | -1.0685 | -2.1285 | -0.62095 | 0.42825 | 0.44828 | -0.19828 | -3.4643 | 61.7431 | 0.21658 | 61.6469 | -0.028522 | 0.052814 | 61.5341 | 0.007721 | 61.3077 | 60.3542 | 59.2943 | 60.8018 | 61.851 | 61.871 | 61.2245 | 57.9584 | 123.1659 | 61.6393 | 123.0696 | 61.3942 | 61.4755 | 122.9568 | 61.4304 | 122.7305 | 61.6903 | 61.7354 | 61.5941 | 61.6392
6487.0625 | 123.3948 | -61.3861 | 61.6562 | -0.88082 | -1.9224 | -0.45154 | 0.57934 | 0.55815 | -0.056347 | -3.2171 | 61.734 | 0.22574 | 61.6652 | -0.028522 | 0.048236 | 61.5433 | 0.012299 | 61.3306 | 60.5053 | 59.4637 | 60.9346 | 61.9655 | 61.9443 | 61.3298 | 58.169 | 123.1201 | 61.6118 | 123.0513 | 61.3576 | 61.4343 | 122.9294 | 61.3984 | 122.7167 | 61.6857 | 61.7217 | 61.617 | 61.6529
6488.0781 | 123.3536 | -61.4273 | 61.6608 | -0.85335 | -1.872 | -0.42407 | 0.58392 | 0.56731 | -0.060926 | -3.1484 | 61.7248 | 0.21658 | 61.6286 | -0.028522 | 0.052814 | 61.5433 | 0.016878 | 61.3306 | 60.574 | 59.5553 | 61.0032 | 62.0112 | 61.9946 | 61.3664 | 58.2789 | 123.1521 | 61.6439 | 123.0559 | 61.3988 | 61.4801 | 122.9706 | 61.4442 | 122.7579 | 61.672 | 61.7079 | 61.5758 | 61.6117
6489.0625 | 123.3856 | -61.3998 | 61.6608 | -0.87166 | -1.9087 | -0.44239 | 0.5885 | 0.60393 | 0.012329 | -3.1667 | 61.7294 | 0.23032 | 61.6606 | -0.033101 | 0.048236 | 61.5387 | 0.012299 | 61.326 | 60.5282 | 59.4912 | 60.9575 | 61.9883 | 62.0038 | 61.4122 | 58.2331 | 123.1292 | 61.6302 | 123.0605 | 61.3667 | 61.4481 | 122.9385 | 61.4121 | 122.7259 | 61.6812 | 61.7171 | 61.6124 | 61.6483
6490.0938 | 123.3582 | -61.4456 | 61.6653 | -0.9907 | -2.0552 | -0.59806 | 0.44199 | 0.45744 | -0.042612 | -3.2858 | 61.7294 | 0.23032 | 61.6332 | -0.028522 | 0.048236 | 61.5433 | 0.012299 | 61.3123 | 60.4549 | 59.3904 | 60.8476 | 61.8876 | 61.9031 | 61.403 | 58.1599 | 123.175 | 61.6759 | 123.0788 | 61.4171 | 61.4939 | 122.9889 | 61.4579 | 122.7579 | 61.6812 | 61.7171 | 61.5849 | 61.6209
6491.0625 | 123.3444 | -61.3998 | 61.7249 | -1.1509 | -2.22 | -0.77205 | 0.24054 | 0.26516 | -0.20286 | -3.4277 | 61.7477 | 0.2349 | 61.6835 | -0.019364 | 0.043657 | 61.5204 | 0.016878 | 61.3077 | 60.2489 | 59.1798 | 60.6278 | 61.6404 | 61.665 | 61.197 | 57.9722 | 123.1476 | 61.6347 | 123.0834 | 61.3805 | 61.4435 | 122.9202 | 61.4167 | 122.7076 | 61.7041 | 61.7308 | 61.6399 | 61.6667
6492.0781 | 123.3673 | -61.3998 | 61.647 | -1.1876 | -2.2429 | -0.82241 | 0.16728 | 0.15987 | -0.2578 | -3.4323 | 61.7477 | 0.22574 | 61.6515 | -0.028522 | 0.043657 | 61.5204 | 0.007721 | 61.2986 | 60.2123 | 59.1569 | 60.5774 | 61.5671 | 61.5597 | 61.142 | 57.9676 | 123.1476 | 61.6256 | 123.0513 | 61.3713 | 61.4435 | 122.9202 | 61.4076 | 122.6984 | 61.7041 | 61.74 | 61.6078 | 61.6438
6493.0625 | 123.381 | -61.3586 | 61.7523 | -1.2105 | -2.2567 | -0.8453 | 0.098602 | 0.082044 | -0.30816 | -3.4231 | 61.7477 | 0.22574 | 61.6835 | -0.023943 | 0.052814 | 61.525 | 0.016878 | 61.3123 | 60.1482 | 59.102 | 60.5133 | 61.4572 | 61.4407 | 61.0505 | 57.9355 | 123.1064 | 61.5844 | 123.0422 | 61.3347 | 61.4115 | 122.8836 | 61.3755 | 122.6709 | 61.6949 | 61.7308 | 61.6307 | 61.6667
6494.0781 | 123.3673 | -61.4182 | 61.6974 | -1.2562 | -2.2841 | -0.90025 | 0.052818 | -0.000359 | -0.33563 | -3.4185 | 61.7523 | 0.22574 | 61.6515 | -0.028522 | 0.039079 | 61.5204 | 0.007721 | 61.3031 | 60.1619 | 59.134 | 60.5179 | 61.471 | 61.4178 | 61.0825 | 57.9996 | 123.1704 | 61.6439 | 123.0696 | 61.3896 | 61.4572 | 122.9385 | 61.4259 | 122.7213 | 61.7132 | 61.7446 | 61.6124 | 61.6438
6495.0625 | 123.3994 | -61.3861 | 61.734 | -1.357 | -2.3482 | -1.0056 | -0.07538 | -0.12854 | -0.51419 | -3.5192 | 61.7706 | 0.22574 | 61.6973 | -0.023943 | 0.048236 | 61.5204 | 0.012299 | 61.2986 | 60.0291 | 59.0379 | 60.3806 | 61.3107 | 61.2576 | 60.8719 | 57.8669 | 123.1567 | 61.6118 | 123.0834 | 61.3622 | 61.4343 | 122.9065 | 61.3984 | 122.6847 | 61.7224 | 61.7583 | 61.649 | 61.685
6496.0625 | 123.2758 | -61.4227 | 61.7111 | -1.302 | -2.2292 | -0.90483 | -0.070802 | -0.21552 | -0.5325 | -3.4826 | 61.7569 | 0.22574 | 61.6698 | -0.023943 | 0.052814 | 61.5112 | 0.003143 | 61.294 | 60.1207 | 59.1935 | 60.5179 | 61.3519 | 61.2072 | 60.8902 | 57.9401 | 123.1796 | 61.6485 | 123.0925 | 61.3988 | 61.4755 | 122.934 | 61.4259 | 122.7167 | 61.7041 | 61.7537 | 61.617 | 61.6667
6497.0781 | 123.3536 | -61.3724 | 61.7249 | -1.3432 | -2.3208 | -0.97351 | -0.098273 | -0.17432 | -0.43635 | -3.4963 | 61.7614 | 0.2349 | 61.6835 | -0.033101 | 0.052814 | 61.5158 | 0.012299 | 61.2894 | 60.0291 | 59.0516 | 60.3989 | 61.2741 | 61.1981 | 60.936 | 57.876 | 123.1338 | 61.6073 | 123.0559 | 61.3393 | 61.4252 | 122.8882 | 61.3847 | 122.6618 | 61.7086 | 61.7491 | 61.6307 | 61.6712
6498.0625 | 123.4131 | -61.3403 | 61.7477 | -1.215 | -2.1376 | -0.81325 | 0.011611 | -0.11481 | -0.40888 | -3.3498 | 61.7569 | 0.21658 | 61.6561 | -0.028522 | 0.052814 | 61.5158 | 0.012299 | 61.3077 | 60.1253 | 59.2027 | 60.5271 | 61.3519 | 61.2255 | 60.9314 | 57.9905 | 123.0972 | 61.5569 | 122.9964 | 61.3118 | 61.3931 | 122.8561 | 61.3526 | 122.6481 | 61.7041 | 61.7446 | 61.6032 | 61.6438
6499.0781 | 123.381 | -61.3861 | 61.6653 | -1.3753 | -2.3025 | -0.9964 | -0.14406 | -0.2613 | -0.56455 | -3.4963 | 61.7614 | 0.22574 | 61.679 | -0.028522 | 0.039079 | 61.5066 | 0.007721 | 61.3031 | 60.0108 | 59.0837 | 60.3897 | 61.242 | 61.1248 | 60.8216 | 57.8898 | 123.1476 | 61.6118 | 123.0651 | 61.3576 | 61.4252 | 122.8928 | 61.3938 | 122.6893 | 61.7224 | 61.7537 | 61.6399 | 61.6712
6500.0625 | 123.3353 | -61.3724 | 61.7203 | -1.4119 | -2.394 | -1.0513 | -0.13032 | -0.20179 | -0.51419 | -3.5696 | 61.7569 | 0.22574 | 61.6744 | -0.019364 | 0.048236 | 61.5066 | 0.007721 | 61.3031 | 59.9605 | 58.9783 | 60.321 | 61.2421 | 61.1706 | 60.8582 | 57.8028 | 123.1292 | 61.5981 | 123.0468 | 61.353 | 61.4206 | 122.879 | 61.3801 | 122.6755 | 61.7086 | 61.7491 | 61.6261 | 61.6667
6501.1094 | 123.3673 | -61.3724 | 61.7111 | -1.5264 | -2.4719 | -1.1887 | -0.35925 | -0.49478 | -0.64696 | -3.5742 | 61.7706 | 0.22574 | 61.6927 | -0.028522 | 0.048236 | 61.4929 | 0.007721 | 61.2803 | 59.846 | 58.9005 | 60.1837 | 61.0131 | 60.8776 | 60.7254 | 57.7982 | 123.143 | 61.5981 | 123.0651 | 61.3439 | 61.4206 | 122.8653 | 61.3801 | 122.6526 | 61.7224 | 61.7629 | 61.6445 | 61.685
6502.0625 | 123.2712 | -61.3495 | 61.7935 | -1.4119 | -2.3299 | -1.0697 | -0.25852 | -0.4078 | -0.56455 | -3.478 | 61.7798 | 0.23032 | 61.6881 | -0.028522 | 0.048236 | 61.5066 | 0.012299 | 61.2986 | 59.9376 | 59.0196 | 60.2798 | 61.091 | 60.9417 | 60.7849 | 57.8715 | 123.1292 | 61.5798 | 123.0376 | 61.321 | 61.3977 | 122.8561 | 61.3618 | 122.6481 | 61.7315 | 61.7675 | 61.6399 | 61.6758
6503.0781 | 123.4039 | -61.3815 | 61.7065 | -1.5081 | -2.3482 | -1.1521 | -0.45082 | -0.66874 | -0.68817 | -3.4735 | 61.7706 | 0.22116 | 61.679 | -0.028522 | 0.048236 | 61.5021 | 0.016878 | 61.2803 | 59.8735 | 59.0333 | 60.2295 | 60.9307 | 60.7128 | 60.6934 | 57.9081 | 123.1521 | 61.6027 | 123.0605 | 61.353 | 61.4298 | 122.8836 | 61.3984 | 122.6618 | 61.7224 | 61.7537 | 61.6307 | 61.6621
6504.0625 | 123.2986 | -61.3815 | 61.7523 | -1.2791 | -2.0918 | -0.92772 | -0.25852 | -0.49478 | -0.51876 | -3.2171 | 61.766 | 0.22574 | 61.6927 | -0.023943 | 0.048236 | 61.5112 | 0.016878 | 61.2894 | 60.1024 | 59.2897 | 60.4538 | 61.123 | 60.8868 | 60.8628 | 58.1645 | 123.1476 | 61.6073 | 123.0742 | 61.3576 | 61.4298 | 122.8928 | 61.3984 | 122.6709 | 61.7178 | 61.7491 | 61.6445 | 61.6758
6505.0781 | 123.3444 | -61.377 | 61.734 | -1.4302 | -2.2246 | -1.1109 | -0.4966 | -0.7603 | -0.65154 | -3.2858 | 61.766 | 0.22116 | 61.6698 | -0.028522 | 0.043657 | 61.5021 | 0.007721 | 61.2848 | 59.9467 | 59.1523 | 60.2661 | 60.8804 | 60.6167 | 60.7254 | 58.0912 | 123.143 | 61.5981 | 123.0468 | 61.3484 | 61.4206 | 122.879 | 61.3847 | 122.6618 | 61.7224 | 61.7583 | 61.6261 | 61.6621
6506.0625 | 123.2529 | -61.3907 | 61.7523 | -1.4577 | -2.2841 | -1.1292 | -0.45997 | -0.66874 | -0.61033 | -3.359 | 61.7798 | 0.2349 | 61.7064 | -0.028522 | 0.048236 | 61.5066 | 0.012299 | 61.294 | 59.933 | 59.1065 | 60.2615 | 60.9307 | 60.7219 | 60.7804 | 58.0317 | 123.1704 | 61.6256 | 123.0971 | 61.3622 | 61.4389 | 122.8973 | 61.403 | 122.6847 | 61.7315 | 61.7675 | 61.6582 | 61.6941
6507.0938 | 123.4085 | -61.377 | 61.6837 | -0.8625 | -1.7118 | -0.46528 | 0.355 | 0.21938 | -0.17996 | -2.979 | 61.7294 | 0.22116 | 61.6423 | -0.028522 | 0.048236 | 61.5341 | 0.007721 | 61.3352 | 60.5145 | 59.6652 | 60.9117 | 61.732 | 61.5963 | 61.197 | 58.3979 | 123.1063 | 61.5981 | 123.0193 | 61.3484 | 61.4252 | 122.9111 | 61.3847 | 122.7121 | 61.6812 | 61.7217 | 61.5941 | 61.6346
6508.0625 | 123.262 | -61.4044 | 61.7844 | -1.4852 | -2.307 | -1.1566 | -0.47371 | -0.67332 | -0.72021 | -3.4368 | 61.7798 | 0.2349 | 61.711 | -0.028522 | 0.052814 | 61.5021 | 0.007721 | 61.2986 | 59.9193 | 59.0974 | 60.2478 | 60.9307 | 60.7311 | 60.6842 | 57.9676 | 123.1842 | 61.6393 | 123.1154 | 61.3759 | 61.4572 | 122.9065 | 61.4121 | 122.703 | 61.7269 | 61.772 | 61.6582 | 61.7033
6509.0781 | 123.3398 | -61.4136 | 61.6974 | -1.096 | -1.927 | -0.7171 | 0.007033 | -0.18348 | -0.41804 | -3.1255 | 61.7431 | 0.22116 | 61.6423 | -0.033101 | 0.052814 | 61.5295 | 0.007721 | 61.3169 | 60.3176 | 59.4866 | 60.6965 | 61.4206 | 61.2301 | 60.9955 | 58.2881 | 123.1567 | 61.6347 | 123.0559 | 61.3805 | 61.4664 | 122.9431 | 61.4213 | 122.7305 | 61.6903 | 61.7354 | 61.5895 | 61.6346
6510.0625 | 123.262 | -61.409 | 61.734 | -1.0823 | -1.9178 | -0.71253 | 0.048239 | -0.096496 | -0.38141 | -3.0752 | 61.7569 | 0.23032 | 61.6881 | -0.023943 | 0.048236 | 61.5295 | 0.012299 | 61.3215 | 60.3267 | 59.4912 | 60.6965 | 61.4572 | 61.3125 | 61.0276 | 58.3338 | 123.1659 | 61.6393 | 123.0971 | 61.3851 | 61.4572 | 122.9385 | 61.4213 | 122.7305 | 61.7086 | 61.7446 | 61.6399 | 61.6758
6511.1094 | 123.3398 | -61.377 | 61.7111 | -1.2883 | -2.0964 | -0.9323 | -0.20358 | -0.37575 | -0.58744 | -3.2674 | 61.7569 | 0.23032 | 61.6606 | -0.023943 | 0.048236 | 61.5066 | 0.012299 | 61.3077 | 60.0887 | 59.2805 | 60.4447 | 61.1734 | 61.0012 | 60.7895 | 58.1095 | 123.1338 | 61.6073 | 123.0376 | 61.353 | 61.4252 | 122.8836 | 61.3893 | 122.6847 | 61.7086 | 61.7446 | 61.6124 | 61.6483
6512.0625 | 123.2483 | -61.4136 | 61.7294 | -1.2379 | -2.0369 | -0.85446 | -0.13948 | -0.32082 | -0.61491 | -3.2171 | 61.766 | 0.23032 | 61.6927 | -0.023943 | 0.052814 | 61.5204 | 0.012299 | 61.3031 | 60.1756 | 59.3767 | 60.5591 | 61.2741 | 61.0928 | 60.7987 | 58.1965 | 123.1796 | 61.6439 | 123.1063 | 61.3896 | 61.4664 | 122.934 | 61.4259 | 122.7167 | 61.7132 | 61.7537 | 61.6399 | 61.6804
6513.0781 | 123.3994 | -61.377 | 61.702 | -1.3478 | -2.1605 | -1.0056 | -0.27683 | -0.45815 | -0.62865 | -3.2903 | 61.7569 | 0.21658 | 61.6652 | -0.028522 | 0.052814 | 61.5112 | 0.007721 | 61.2986 | 60.0291 | 59.2164 | 60.3714 | 61.1001 | 60.9188 | 60.7483 | 58.0866 | 123.1338 | 61.5935 | 123.0422 | 61.3484 | 61.4298 | 122.8882 | 61.3847 | 122.6755 | 61.7041 | 61.7491 | 61.6124 | 61.6575
6514.0625 | 123.3078 | -61.4136 | 61.7752 | -1.595 | -2.4398 | -1.3032 | -0.56528 | -0.70537 | -0.77515 | -3.4735 | 61.7843 | 0.23032 | 61.711 | -0.028522 | 0.052814 | 61.4975 | 0.012299 | 61.2848 | 59.8185 | 58.9738 | 60.1104 | 60.8483 | 60.7082 | 60.6384 | 57.9401 | 123.1979 | 61.6439 | 123.1246 | 61.3851 | 61.4664 | 122.9111 | 61.4259 | 122.6984 | 61.7315 | 61.772 | 61.6582 | 61.6987
6515.0938 | 123.2712 | -61.3953 | 61.7752 | -1.6271 | -2.4398 | -1.3261 | -0.63853 | -0.83355 | -0.85299 | -3.4872 | 61.7843 | 0.22116 | 61.6835 | -0.023943 | 0.043657 | 61.4929 | 0.007721 | 61.2848 | 59.7682 | 58.9554 | 60.0692 | 60.7567 | 60.5617 | 60.5423 | 57.9081 | 123.1796 | 61.6164 | 123.0788 | 61.3713 | 61.4389 | 122.8882 | 61.403 | 122.6801 | 61.7407 | 61.7766 | 61.6399 | 61.6758
6516.0625 | 123.3032 | -61.377 | 61.7889 | -1.4073 | -2.2384 | -1.0788 | -0.31804 | -0.42611 | -0.5966 | -3.2858 | 61.7706 | 0.22574 | 61.6835 | -0.023943 | 0.048236 | 61.5112 | 0.007721 | 61.294 | 59.9696 | 59.1386 | 60.2981 | 61.0589 | 60.9508 | 60.7804 | 58.0912 | 123.1476 | 61.6027 | 123.0605 | 61.353 | 61.4252 | 122.8882 | 61.3847 | 122.6709 | 61.7224 | 61.7629 | 61.6353 | 61.6758
6517.0781 | 123.3765 | -61.3632 | 61.7294 | -1.4119 | -2.1788 | -1.0742 | -0.41877 | -0.60007 | -0.65154 | -3.2445 | 61.7569 | 0.21658 | 61.6744 | -0.023943 | 0.048236 | 61.5021 | 0.007721 | 61.2986 | 59.9513 | 59.1844 | 60.289 | 60.9445 | 60.7631 | 60.7117 | 58.1187 | 123.1201 | 61.5798 | 123.0376 | 61.3393 | 61.4115 | 122.8653 | 61.3709 | 122.6618 | 61.7086 | 61.7491 | 61.6261 | 61.6667
6518.0625 | 123.2437 | -61.4044 | 61.734 | -1.5996 | -2.3345 | -1.2894 | -0.753 | -1.035 | -0.81178 | -3.3453 | 61.7843 | 0.2349 | 61.6973 | -0.023943 | 0.043657 | 61.4975 | 0.007721 | 61.2757 | 59.8048 | 59.0699 | 60.115 | 60.6514 | 60.3694 | 60.5926 | 58.0592 | 123.1888 | 61.6393 | 123.1017 | 61.3805 | 61.4481 | 122.9019 | 61.4121 | 122.6801 | 61.7407 | 61.7766 | 61.6536 | 61.6895
6519.0781 | 123.4085 | -61.3312 | 61.7477 | -1.7095 | -2.4765 | -1.4359 | -0.83541 | -1.0579 | -0.90793 | -3.5147 | 61.7889 | 0.22116 | 61.6973 | -0.023943 | 0.043657 | 61.4883 | 0.007721 | 61.2803 | 59.6217 | 58.8547 | 59.8952 | 60.4958 | 60.2733 | 60.4232 | 57.8165 | 123.1201 | 61.5523 | 123.0284 | 61.3072 | 61.3748 | 122.8195 | 61.3389 | 122.6114 | 61.7453 | 61.7812 | 61.6536 | 61.6895
6520.0625 | 123.2986 | -61.3724 | 61.7569 | -1.4714 | -2.2704 | -1.1658 | -0.42792 | -0.57718 | -0.74311 | -3.3636 | 61.7706 | 0.22574 | 61.6881 | -0.028522 | 0.048236 | 61.5021 | 0.012299 | 61.2986 | 59.9009 | 59.102 | 60.2066 | 60.9445 | 60.7952 | 60.6293 | 58.0088 | 123.143 | 61.5981 | 123.0605 | 61.3439 | 61.4206 | 122.8744 | 61.3847 | 122.6709 | 61.7224 | 61.7583 | 61.6399 | 61.6758
6521.0938 | 123.3124 | -61.3861 | 61.7523 | -1.4531 | -2.2612 | -1.1979 | -0.45082 | -0.58634 | -0.71106 | -3.2674 | 61.7798 | 0.23032 | 61.6835 | -0.023943 | 0.048236 | 61.5066 | 0.012299 | 61.3031 | 59.933 | 59.1249 | 60.1882 | 60.9353 | 60.7998 | 60.6751 | 58.1187 | 123.1659 | 61.6164 | 123.0696 | 61.3622 | 61.4343 | 122.8928 | 61.3984 | 122.6893 | 61.7315 | 61.7675 | 61.6353 | 61.6712
6522.0625 | 123.262 | -61.409 | 61.7661 | -1.4073 | -2.1834 | -1.1338 | -0.40045 | -0.55887 | -0.66985 | -3.2033 | 61.766 | 0.22574 | 61.6744 | -0.028522 | 0.048236 | 61.5066 | 0.016878 | 61.3031 | 60.0017 | 59.2256 | 60.2752 | 61.0085 | 60.8501 | 60.7391 | 58.2057 | 123.175 | 61.6347 | 123.0834 | 61.3805 | 61.4572 | 122.9156 | 61.4259 | 122.7121 | 61.7178 | 61.7491 | 61.6261 | 61.6575
6523.0781 | 123.3398 | -61.3495 | 61.734 | -1.6546 | -2.4398 | -1.3947 | -0.67974 | -0.86101 | -0.86672 | -3.5009 | 61.7843 | 0.23032 | 61.6973 | -0.028522 | 0.048236 | 61.4929 | 0.012299 | 61.2848 | 59.6949 | 58.9097 | 59.9547 | 60.6697 | 60.4885 | 60.4828 | 57.8486 | 123.1338 | 61.5798 | 123.0468 | 61.321 | 61.3977 | 122.8424 | 61.3618 | 122.6343 | 61.7361 | 61.772 | 61.649 | 61.685
6524.0625 | 123.2437 | -61.4044 | 61.7523 | -1.6179 | -2.3849 | -1.3581 | -0.66143 | -0.83355 | -0.84841 | -3.391 | 61.7798 | 0.2349 | 61.6881 | -0.023943 | 0.052814 | 61.4929 | 0.007721 | 61.2848 | 59.7865 | 59.0195 | 60.0463 | 60.743 | 60.5709 | 60.556 | 58.0134 | 123.1842 | 61.6393 | 123.0925 | 61.3805 | 61.4572 | 122.8973 | 61.4121 | 122.6893 | 61.7269 | 61.772 | 61.6353 | 61.6804
6525.0781 | 123.3856 | -61.3998 | 61.734 | -1.7095 | -2.5085 | -1.468 | -0.72095 | -0.87017 | -0.93998 | -3.5147 | 61.7843 | 0.23032 | 61.7064 | -0.028522 | 0.048236 | 61.4883 | 0.007721 | 61.2711 | 59.6903 | 58.8913 | 59.9318 | 60.6789 | 60.5297 | 60.4599 | 57.8852 | 123.1842 | 61.6302 | 123.1063 | 61.3713 | 61.4481 | 122.8882 | 61.4076 | 122.6709 | 61.7361 | 61.7766 | 61.6582 | 61.6987
6526.0625 | 123.3215 | -61.409 | 61.7294 | -1.9842 | -2.7466 | -1.8114 | -1.133 | -1.3097 | -1.1506 | -3.6062 | 61.7981 | 0.22574 | 61.7064 | -0.028522 | 0.043657 | 61.47 | -0.001436 | 61.2665 | 59.4248 | 58.6624 | 59.5976 | 60.276 | 60.0993 | 60.2584 | 57.8028 | 123.2071 | 61.6347 | 123.1154 | 61.3805 | 61.4527 | 122.879 | 61.4076 | 122.6755 | 61.7544 | 61.7995 | 61.6628 | 61.7079
6527.0781 | 123.381 | -61.3174 | 61.7569 | -2.0987 | -2.829 | -1.9121 | -1.2841 | -1.4974 | -1.3017 | -3.7619 | 61.821 | 0.2349 | 61.7339 | -0.028522 | 0.048236 | 61.47 | 0.007721 | 61.2574 | 59.2188 | 58.4884 | 59.4053 | 60.0333 | 59.8201 | 60.0158 | 57.5556 | 123.1384 | 61.5523 | 123.0513 | 61.2889 | 61.3657 | 122.7875 | 61.3252 | 122.5748 | 61.7727 | 61.8132 | 61.6857 | 61.7262
6528.0625 | 123.3078 | -61.3586 | 61.7752 | -1.8652 | -2.5634 | -1.6374 | -0.97734 | -1.1769 | -1.2193 | -3.6062 | 61.7889 | 0.22116 | 61.7018 | -0.033101 | 0.048236 | 61.4838 | 0.016878 | 61.2757 | 59.4935 | 58.7952 | 59.7212 | 60.3813 | 60.1817 | 60.1394 | 57.7524 | 123.1476 | 61.5798 | 123.0605 | 61.3255 | 61.4069 | 122.8424 | 61.3755 | 122.6343 | 61.7407 | 61.772 | 61.6536 | 61.685
6529.0938 | 123.2437 | -61.3312 | 61.8027 | -2.1994 | -2.8794 | -2.022 | -1.4672 | -1.7308 | -1.4665 | -3.8397 | 61.821 | 0.23032 | 61.7476 | -0.028522 | 0.048236 | 61.4563 | 0.007721 | 61.2528 | 59.1318 | 58.4518 | 59.3092 | 59.8639 | 59.6003 | 59.8647 | 57.4915 | 123.1521 | 61.5615 | 123.0788 | 61.3027 | 61.3794 | 122.7875 | 61.3389 | 122.584 | 61.7727 | 61.8132 | 61.6994 | 61.7399
6530.0625 | 123.2529 | -61.3586 | 61.8118 | -2.1582 | -2.8931 | -1.9671 | -1.3162 | -1.5065 | -1.4161 | -3.8672 | 61.8072 | 0.22574 | 61.7156 | -0.028522 | 0.043657 | 61.4563 | 0.007721 | 61.2574 | 59.2005 | 58.4655 | 59.3916 | 60.0425 | 59.8521 | 59.9425 | 57.4915 | 123.1659 | 61.5844 | 123.0742 | 61.3301 | 61.4023 | 122.8149 | 61.3664 | 122.616 | 61.7636 | 61.7995 | 61.6719 | 61.7079
6531.1094 | 123.3948 | -61.3129 | 61.7844 | -2.1124 | -2.8336 | -1.9259 | -1.2749 | -1.4562 | -1.4253 | -3.8122 | 61.8164 | 0.2349 | 61.7385 | -0.023943 | 0.057392 | 61.4609 | 0.012299 | 61.2528 | 59.2005 | 58.4793 | 59.387 | 60.0379 | 59.8567 | 59.8876 | 57.5006 | 123.1293 | 61.5478 | 123.0513 | 61.2889 | 61.3703 | 122.7737 | 61.3252 | 122.5657 | 61.759 | 61.8041 | 61.6811 | 61.7262
6532.0625 | 123.317 | -61.3358 | 61.7889 | -2.2406 | -2.9298 | -2.0678 | -1.4901 | -1.7217 | -1.5397 | -3.8855 | 61.8118 | 0.22116 | 61.7202 | -0.023943 | 0.048236 | 61.4563 | 0.007721 | 61.2482 | 59.0952 | 58.406 | 59.268 | 59.8456 | 59.6141 | 59.796 | 57.4503 | 123.1476 | 61.5569 | 123.0559 | 61.3118 | 61.384 | 122.792 | 61.3435 | 122.584 | 61.7636 | 61.8041 | 61.6719 | 61.7124
6533.0781 | 123.3856 | -61.3129 | 61.7661 | -2.0437 | -2.7191 | -1.8434 | -1.2475 | -1.4974 | -1.4024 | -3.7024 | 61.8118 | 0.2349 | 61.743 | -0.033101 | 0.043657 | 61.4563 | 0.003143 | 61.2528 | 59.2691 | 58.5937 | 59.4694 | 60.0654 | 59.8155 | 59.9105 | 57.6105 | 123.1247 | 61.5478 | 123.0559 | 61.2798 | 61.3565 | 122.7692 | 61.316 | 122.5657 | 61.7682 | 61.8087 | 61.6994 | 61.7399
6534.0625 | 123.2941 | -61.3724 | 61.7569 | -2.4787 | -3.2045 | -2.3471 | -1.7511 | -1.9735 | -1.7458 | -4.1236 | 61.8255 | 0.23032 | 61.7339 | -0.028522 | 0.043657 | 61.4426 | 0.003143 | 61.2253 | 58.8937 | 58.1679 | 59.0253 | 59.6213 | 59.3989 | 59.6266 | 57.2488 | 123.1979 | 61.6027 | 123.1063 | 61.3439 | 61.416 | 122.8149 | 61.3755 | 122.5977 | 61.7819 | 61.8224 | 61.6902 | 61.7308
6535.0938 | 123.3627 | -61.322 | 61.7752 | -2.3642 | -3.0488 | -2.2097 | -1.7191 | -2.0055 | -1.6267 | -3.9404 | 61.8301 | 0.2349 | 61.7614 | -0.028522 | 0.048236 | 61.4426 | 0.012299 | 61.2299 | 58.9578 | 58.2732 | 59.1123 | 59.603 | 59.3165 | 59.6953 | 57.3816 | 123.1521 | 61.5569 | 123.0834 | 61.2935 | 61.3703 | 122.7646 | 61.3343 | 122.5519 | 61.7819 | 61.8178 | 61.7131 | 61.7491
6536.0625 | 123.262 | -61.3174 | 61.8027 | -2.4008 | -3.09 | -2.2509 | -1.7465 | -2.033 | -1.613 | -4.0091 | 61.8255 | 0.22574 | 61.7247 | -0.023943 | 0.043657 | 61.438 | 0.003143 | 61.2299 | 58.9166 | 58.2274 | 59.0665 | 59.5709 | 59.2845 | 59.7044 | 57.3083 | 123.143 | 61.5432 | 123.0422 | 61.2935 | 61.3611 | 122.7554 | 61.3206 | 122.5473 | 61.7819 | 61.8224 | 61.6811 | 61.7216
6537.0781 | 123.3307 | -61.3358 | 61.7752 | -2.5153 | -3.2182 | -2.3837 | -1.8701 | -2.1428 | -1.7137 | -4.0778 | 61.8393 | 0.2349 | 61.7614 | -0.033101 | 0.048236 | 61.4426 | 0.012299 | 61.2253 | 58.8205 | 58.1175 | 58.952 | 59.4656 | 59.1929 | 59.622 | 57.258 | 123.175 | 61.5707 | 123.0971 | 61.3027 | 61.384 | 122.7783 | 61.3481 | 122.5611 | 61.791 | 61.827 | 61.7131 | 61.7491
6538.0625 | 123.4177 | -61.2854 | 61.7844 | -2.6664 | -3.351 | -2.544 | -2.0533 | -2.326 | -1.819 | -4.1785 | 61.8484 | 0.23032 | 61.7568 | -0.019364 | 0.043657 | 61.4288 | 0.007721 | 61.2207 | 58.619 | 57.9344 | 58.7414 | 59.2321 | 58.9594 | 59.4664 | 57.1069 | 123.1338 | 61.5157 | 123.0422 | 61.266 | 61.3291 | 122.7142 | 61.2931 | 122.5061 | 61.8048 | 61.8407 | 61.7131 | 61.7491
6539.0938 | 123.2712 | -61.3541 | 61.8301 | -2.291 | -3.0259 | -2.1319 | -1.4444 | -1.6118 | -1.439 | -3.9221 | 61.8164 | 0.22574 | 61.7202 | -0.028522 | 0.048236 | 61.4563 | 0.007721 | 61.2436 | 59.0631 | 58.3282 | 59.2222 | 59.9097 | 59.7423 | 59.915 | 57.4319 | 123.1705 | 61.5798 | 123.0742 | 61.3255 | 61.4023 | 122.8104 | 61.3618 | 122.5977 | 61.7682 | 61.8087 | 61.6719 | 61.7124
6540.0625 | 123.3765 | -61.3312 | 61.7798 | -2.0529 | -2.7283 | -1.8572 | -1.2475 | -1.4562 | -1.3703 | -3.6795 | 61.8118 | 0.2349 | 61.743 | -0.023943 | 0.052814 | 61.4609 | 0.003143 | 61.2574 | 59.2783 | 58.6029 | 59.474 | 60.0837 | 59.875 | 59.9608 | 57.6517 | 123.143 | 61.5661 | 123.0742 | 61.3072 | 61.384 | 122.792 | 61.3343 | 122.5885 | 61.759 | 61.8087 | 61.6902 | 61.7399
6541.1094 | 123.3307 | -61.322 | 61.7432 | -2.6298 | -3.351 | -2.5485 | -1.9526 | -2.1474 | -1.8373 | -4.1739 | 61.8301 | 0.22574 | 61.743 | -0.03768 | 0.043657 | 61.4288 | 0.003143 | 61.2162 | 58.6923 | 57.971 | 58.7735 | 59.3695 | 59.1746 | 59.4847 | 57.1481 | 123.1521 | 61.5478 | 123.0651 | 61.2843 | 61.3657 | 122.7508 | 61.3252 | 122.5382 | 61.7865 | 61.827 | 61.6994 | 61.7399
6542.0625 | 123.3948 | -61.29 | 61.8027 | -2.8175 | -3.4792 | -2.718 | -2.2731 | -2.5457 | -2.0525 | -4.3204 | 61.8668 | 0.2349 | 61.7888 | -0.023943 | 0.052814 | 61.4242 | 0.012299 | 61.2162 | 58.4725 | 57.8108 | 58.572 | 59.0169 | 58.7443 | 59.2375 | 56.9696 | 123.1567 | 61.5249 | 123.0788 | 61.266 | 61.3428 | 122.7142 | 61.3023 | 122.5061 | 61.8139 | 61.8545 | 61.736 | 61.7765
6543.0781 | 123.3765 | -61.2991 | 61.7798 | -2.8541 | -3.4884 | -2.7637 | -2.3784 | -2.6693 | -2.0388 | -4.2792 | 61.853 | 0.22574 | 61.7659 | -0.028522 | 0.043657 | 61.4197 | 0.007721 | 61.2162 | 58.445 | 57.8108 | 58.5354 | 58.9208 | 58.6298 | 59.2603 | 57.0199 | 123.1521 | 61.5249 | 123.0651 | 61.2706 | 61.3428 | 122.7188 | 61.3069 | 122.5153 | 61.8094 | 61.8453 | 61.7223 | 61.7582
6544.0625 | 123.349 | -61.2534 | 61.8118 | -2.7442 | -3.3785 | -2.6493 | -2.2227 | -2.4816 | -1.9655 | -4.1922 | 61.8484 | 0.22574 | 61.7797 | -0.028522 | 0.052814 | 61.4197 | 0.012299 | 61.2116 | 58.5091 | 57.8749 | 58.6041 | 59.0307 | 58.7717 | 59.2878 | 57.0611 | 123.1018 | 61.4791 | 123.033 | 61.2248 | 61.3062 | 122.673 | 61.2657 | 122.4649 | 61.7956 | 61.8361 | 61.7269 | 61.7674
6545.0781 | 123.3994 | -61.2579 | 61.7661 | -2.6252 | -3.2869 | -2.5257 | -2.0167 | -2.2481 | -1.9014 | -4.1236 | 61.8347 | 0.22574 | 61.743 | -0.033101 | 0.043657 | 61.438 | 0.007721 | 61.2207 | 58.6328 | 57.971 | 58.7323 | 59.2413 | 59.0098 | 59.3565 | 57.1344 | 123.0926 | 61.4837 | 123.001 | 61.2248 | 61.3016 | 122.6959 | 61.2657 | 122.4787 | 61.791 | 61.827 | 61.6994 | 61.7353
6546.0625 | 123.3856 | -61.322 | 61.7615 | -2.616 | -3.2548 | -2.4982 | -2.0029 | -2.2664 | -1.9381 | -4.119 | 61.8347 | 0.23032 | 61.7751 | -0.028522 | 0.052814 | 61.4334 | 0.003143 | 61.2253 | 58.706 | 58.0672 | 58.8238 | 59.3191 | 59.0556 | 59.384 | 57.203 | 123.1567 | 61.5523 | 123.0971 | 61.2935 | 61.3748 | 122.7554 | 61.3252 | 122.5473 | 61.7819 | 61.8316 | 61.7223 | 61.772
6547.0781 | 123.3627 | -61.2717 | 61.7752 | -2.8999 | -3.5342 | -2.8462 | -2.3829 | -2.6281 | -2.112 | -4.2792 | 61.8576 | 0.22116 | 61.7659 | -0.028522 | 0.043657 | 61.4151 | 0.007721 | 61.2162 | 58.3718 | 57.7375 | 58.4255 | 58.8887 | 58.6436 | 59.1596 | 56.9925 | 123.1293 | 61.4928 | 123.0376 | 61.2431 | 61.3153 | 122.6868 | 61.2794 | 122.4878 | 61.8139 | 61.8499 | 61.7223 | 61.7582
6548.0625 | 123.3856 | -61.3083 | 61.7798 | -2.616 | -3.232 | -2.5257 | -2.035 | -2.2756 | -1.874 | -4.032 | 61.8439 | 0.22116 | 61.7614 | -0.028522 | 0.057392 | 61.4426 | 0.016878 | 61.2253 | 58.6923 | 58.0763 | 58.7826 | 59.2733 | 59.0327 | 59.4343 | 57.2763 | 123.1521 | 61.5295 | 123.0697 | 61.2798 | 61.3657 | 122.7508 | 61.3252 | 122.5336 | 61.7865 | 61.827 | 61.704 | 61.7445
6549.0781 | 123.3627 | -61.3129 | 61.7706 | -2.7396 | -3.3831 | -2.6493 | -2.1128 | -2.3077 | -1.9655 | -4.2105 | 61.8484 | 0.23032 | 61.7522 | -0.028522 | 0.052814 | 61.4288 | 0.007721 | 61.2207 | 58.5732 | 57.9298 | 58.6636 | 59.2001 | 59.0052 | 59.3473 | 57.1023 | 123.1613 | 61.5432 | 123.0651 | 61.2843 | 61.3657 | 122.7417 | 61.3206 | 122.5336 | 61.7956 | 61.8407 | 61.6994 | 61.7445
6550.0625 | 123.3948 | -61.2762 | 61.7661 | -2.7625 | -3.4288 | -2.7088 | -2.1494 | -2.3305 | -1.9701 | -4.2517 | 61.853 | 0.22574 | 61.7659 | -0.033101 | 0.052814 | 61.4151 | 0.007721 | 61.2116 | 58.5137 | 57.8474 | 58.5674 | 59.1268 | 58.9457 | 59.3061 | 57.0245 | 123.1293 | 61.502 | 123.0422 | 61.2431 | 61.3291 | 122.6913 | 61.284 | 122.4878 | 61.8002 | 61.8453 | 61.7131 | 61.7582
6551.0938 | 123.2758 | -61.3266 | 61.8118 | -2.5748 | -3.1816 | -2.4707 | -1.9892 | -2.2207 | -1.8602 | -4.0183 | 61.8301 | 0.23032 | 61.743 | -0.028522 | 0.048236 | 61.438 | 0.003143 | 61.2207 | 58.7518 | 58.145 | 58.8559 | 59.3374 | 59.1059 | 59.4664 | 57.3083 | 123.1567 | 61.5569 | 123.0696 | 61.2981 | 61.3748 | 122.7646 | 61.3297 | 122.5473 | 61.7819 | 61.827 | 61.6948 | 61.7399
6552.0625 | 123.3765 | -61.2854 | 61.7844 | -2.7625 | -3.3922 | -2.7042 | -2.1998 | -2.4038 | -1.9426 | -4.1739 | 61.8484 | 0.22116 | 61.7614 | -0.028522 | 0.048236 | 61.4242 | 0.012299 | 61.2162 | 58.5229 | 57.8932 | 58.5812 | 59.0856 | 58.8816 | 59.3428 | 57.1115 | 123.1338 | 61.5066 | 123.0468 | 61.2569 | 61.3336 | 122.7096 | 61.2977 | 122.5016 | 61.8002 | 61.8361 | 61.7131 | 61.7491
6553.0938 | 123.3627 | -61.3174 | 61.7706 | -2.7305 | -3.3235 | -2.6722 | -2.2319 | -2.4999 | -1.9564 | -4.119 | 61.8393 | 0.23032 | 61.7476 | -0.033101 | 0.052814 | 61.4242 | 0.012299 | 61.2116 | 58.587 | 57.9939 | 58.6453 | 59.0856 | 58.8175 | 59.3611 | 57.1985 | 123.1567 | 61.5478 | 123.0651 | 61.2843 | 61.3703 | 122.7417 | 61.3297 | 122.529 | 61.7865 | 61.827 | 61.6948 | 61.7353
6554.0625 | 123.3673 | -61.29 | 61.7798 | -2.7671 | -3.3785 | -2.7088 | -2.2181 | -2.4587 | -2.0113 | -4.2105 | 61.853 | 0.22574 | 61.7614 | -0.033101 | 0.057392 | 61.4242 | 0.007721 | 61.207 | 58.5229 | 57.9115 | 58.5812 | 59.0719 | 58.8313 | 59.2787 | 57.0794 | 123.143 | 61.5157 | 123.0513 | 61.2569 | 61.3474 | 122.7142 | 61.2977 | 122.497 | 61.7956 | 61.8453 | 61.704 | 61.7536
6555.0781 | 123.4177 | -61.29 | 61.7752 | -2.8312 | -3.4517 | -2.7592 | -2.2547 | -2.4679 | -2.0846 | -4.3158 | 61.8576 | 0.22116 | 61.7614 | -0.028522 | 0.048236 | 61.4197 | 0.007721 | 61.1933 | 58.4588 | 57.8382 | 58.5308 | 59.0352 | 58.8221 | 59.2054 | 56.9741 | 123.1476 | 61.5111 | 123.0513 | 61.2615 | 61.3382 | 122.7096 | 61.2977 | 122.4832 | 61.8094 | 61.8499 | 61.7131 | 61.7536
6556.0625 | 123.3902 | -61.2625 | 61.7798 | -2.7946 | -3.4334 | -2.7225 | -2.2227 | -2.4084 | -2.0434 | -4.2655 | 61.853 | 0.22574 | 61.7614 | -0.028522 | 0.048236 | 61.4151 | 0.007721 | 61.207 | 58.4679 | 57.8291 | 58.54 | 59.0398 | 58.8541 | 59.2191 | 56.997 | 123.1155 | 61.4883 | 123.0239 | 61.234 | 61.3107 | 122.6776 | 61.2702 | 122.4695 | 61.8048 | 61.8453 | 61.7131 | 61.7536
6557.0781 | 123.4039 | -61.29 | 61.7661 | -2.8037 | -3.4288 | -2.7454 | -2.2502 | -2.4496 | -2.0846 | -4.206 | 61.8484 | 0.23032 | 61.7659 | -0.033101 | 0.043657 | 61.4197 | 0.007721 | 61.207 | 58.4862 | 57.8611 | 58.5446 | 59.0398 | 58.8404 | 59.2054 | 57.084 | 123.1384 | 61.5203 | 123.0559 | 61.2569 | 61.3336 | 122.7096 | 61.2977 | 122.497 | 61.8048 | 61.8407 | 61.7223 | 61.7582
6558.0625 | 123.4085 | -61.2717 | 61.8027 | -2.9411 | -3.5662 | -2.8828 | -2.3646 | -2.5503 | -2.1853 | -4.3799 | 61.853 | 0.23032 | 61.7705 | -0.033101 | 0.048236 | 61.4151 | 0.012299 | 61.2024 | 58.3306 | 57.7055 | 58.3889 | 58.907 | 58.7214 | 59.0864 | 56.8917 | 123.1247 | 61.502 | 123.0422 | 61.2386 | 61.3199 | 122.6868 | 61.284 | 122.4741 | 61.8048 | 61.8407 | 61.7223 | 61.7582
6559.0625 | 123.4177 | -61.2534 | 61.7844 | -3.0281 | -3.6028 | -2.9972 | -2.5981 | -2.825 | -2.254 | -4.3479 | 61.8622 | 0.23032 | 61.7888 | -0.023943 | 0.048236 | 61.4059 | 0.012299 | 61.1933 | 58.2253 | 57.6505 | 58.2561 | 58.6552 | 58.4284 | 58.9994 | 56.9055 | 123.1155 | 61.4837 | 123.0422 | 61.2294 | 61.3016 | 122.6593 | 61.2657 | 122.4466 | 61.8139 | 61.8499 | 61.7406 | 61.7765
6560.0938 | 123.3719 | -61.2991 | 61.7752 | -2.8312 | -3.4105 | -2.7821 | -2.3097 | -2.5137 | -2.1532 | -4.2151 | 61.853 | 0.23032 | 61.7614 | -0.028522 | 0.052814 | 61.4242 | 0.007721 | 61.207 | 58.4679 | 57.8886 | 58.5171 | 58.9894 | 58.7855 | 59.1459 | 57.084 | 123.1521 | 61.5295 | 123.0605 | 61.2706 | 61.3519 | 122.7234 | 61.3069 | 122.5061 | 61.8002 | 61.8453 | 61.7085 | 61.7536
6561.0625 | 123.3353 | -61.2259 | 61.8439 | -2.8312 | -3.406 | -2.7866 | -2.3005 | -2.4908 | -2.1395 | -4.2014 | 61.8622 | 0.2349 | 61.7934 | -0.028522 | 0.048236 | 61.4197 | 0.016878 | 61.2162 | 58.3947 | 57.8199 | 58.4393 | 58.9254 | 58.7351 | 59.0864 | 57.0245 | 123.0881 | 61.4608 | 123.0193 | 61.1974 | 61.2741 | 122.6456 | 61.2428 | 122.4421 | 61.8139 | 61.8453 | 61.7452 | 61.7765
6562.0781 | 123.3444 | -61.2946 | 61.7752 | -2.909 | -3.4655 | -2.8874 | -2.4425 | -2.6144 | -2.1945 | -4.2334 | 61.8576 | 0.22574 | 61.7705 | -0.033101 | 0.039079 | 61.4105 | 0.007721 | 61.2024 | 58.3855 | 57.8291 | 58.4072 | 58.8521 | 58.6802 | 59.1001 | 57.0611 | 123.1522 | 61.5203 | 123.0651 | 61.2615 | 61.3336 | 122.7051 | 61.3023 | 122.497 | 61.8185 | 61.8499 | 61.7314 | 61.7628
6563.0625 | 123.3856 | -61.2717 | 61.7889 | -2.8358 | -3.3922 | -2.8095 | -2.328 | -2.5091 | -2.1578 | -4.1602 | 61.853 | 0.23032 | 61.7568 | -0.033101 | 0.052814 | 61.4197 | 0.007721 | 61.2116 | 58.4359 | 57.8795 | 58.4621 | 58.9437 | 58.7626 | 59.1138 | 57.1115 | 123.1247 | 61.502 | 123.0285 | 61.2386 | 61.3245 | 122.6913 | 61.2794 | 122.4832 | 61.8002 | 61.8453 | 61.704 | 61.7491
6564.0938 | 123.3948 | -61.2991 | 61.7615 | -3.0235 | -3.5891 | -3.0339 | -2.5798 | -2.738 | -2.2814 | -4.2838 | 61.8668 | 0.23032 | 61.798 | -0.033101 | 0.052814 | 61.4105 | 0.012299 | 61.2116 | 58.2756 | 57.71 | 58.2653 | 58.7193 | 58.5612 | 59.0177 | 57.0153 | 123.1659 | 61.5295 | 123.0971 | 61.266 | 61.3519 | 122.7096 | 61.3114 | 122.5107 | 61.8139 | 61.8545 | 61.7452 | 61.7857
6565.0625 | 123.4039 | -61.2305 | 61.8164 | -3.1059 | -3.6807 | -3.13 | -2.676 | -2.8204 | -2.341 | -4.3845 | 61.8668 | 0.22116 | 61.7751 | -0.033101 | 0.048236 | 61.4105 | 0.012299 | 61.1933 | 58.1246 | 57.5498 | 58.1004 | 58.5545 | 58.4101 | 58.8895 | 56.846 | 123.0972 | 61.4516 | 123.0056 | 61.1974 | 61.2787 | 122.641 | 61.2428 | 122.4237 | 61.8185 | 61.8545 | 61.7269 | 61.7628
6566.1094 | 123.349 | -61.3037 | 61.7752 | -2.9915 | -3.5342 | -2.9789 | -2.5478 | -2.7242 | -2.2906 | -4.2746 | 61.8713 | 0.22574 | 61.7934 | -0.028522 | 0.052814 | 61.4105 | 0.007721 | 61.207 | 58.3123 | 57.7696 | 58.3248 | 58.7559 | 58.5795 | 59.0131 | 57.0291 | 123.175 | 61.5294 | 123.0971 | 61.2752 | 61.3565 | 122.7142 | 61.3114 | 122.5107 | 61.8185 | 61.8636 | 61.7406 | 61.7857
6567.0625 | 123.3902 | -61.2625 | 61.8118 | -3.0327 | -3.5479 | -3.043 | -2.6485 | -2.8341 | -2.2998 | -4.2563 | 61.8668 | 0.22116 | 61.7614 | -0.028522 | 0.043657 | 61.4105 | 0.007721 | 61.2024 | 58.2299 | 57.7146 | 58.2195 | 58.614 | 58.4284 | 58.9628 | 57.0062 | 123.1293 | 61.4837 | 123.0239 | 61.234 | 61.3062 | 122.673 | 61.2702 | 122.4649 | 61.8231 | 61.859 | 61.7177 | 61.7536
6568.0938 | 123.3627 | -61.29 | 61.7798 | -3.0281 | -3.5616 | -3.0385 | -2.6027 | -2.738 | -2.2586 | -4.2838 | 61.8668 | 0.23032 | 61.8026 | -0.023943 | 0.048236 | 61.4014 | 0.003143 | 61.1933 | 58.2619 | 57.7283 | 58.2515 | 58.6873 | 58.552 | 59.0314 | 57.0062 | 123.1567 | 61.5203 | 123.0925 | 61.266 | 61.3382 | 122.6913 | 61.2931 | 122.4832 | 61.8185 | 61.8636 | 61.7543 | 61.7994
6569.0625 | 123.3719 | -61.2625 | 61.7889 | -3.1609 | -3.6624 | -3.185 | -2.8225 | -2.976 | -2.4371 | -4.3982 | 61.8713 | 0.23032 | 61.7751 | -0.023943 | 0.052814 | 61.3876 | 0.012299 | 61.1933 | 58.1017 | 57.6001 | 58.0775 | 58.44 | 58.2865 | 58.8254 | 56.8643 | 123.1338 | 61.4928 | 123.0376 | 61.2386 | 61.3153 | 122.6501 | 61.2748 | 122.4558 | 61.8185 | 61.859 | 61.7223 | 61.7628
6570.0781 | 123.4406 | -61.2625 | 61.7889 | -3.3165 | -3.8226 | -3.3498 | -2.9324 | -3.0584 | -2.5287 | -4.586 | 61.8851 | 0.23032 | 61.8117 | -0.028522 | 0.039079 | 61.3876 | 0.012299 | 61.175 | 57.946 | 57.4399 | 57.9127 | 58.3302 | 58.2041 | 58.7338 | 56.6766 | 123.1476 | 61.4928 | 123.0742 | 61.234 | 61.3016 | 122.6501 | 61.2748 | 122.4375 | 61.846 | 61.8728 | 61.7726 | 61.7994
6571.0625 | 123.2758 | -61.2625 | 61.8851 | -3.463 | -3.96 | -3.5146 | -3.1796 | -3.3377 | -2.6523 | -4.65 | 61.8896 | 0.23032 | 61.798 | -0.03768 | 0.057392 | 61.383 | -0.001436 | 61.1704 | 57.7995 | 57.3025 | 57.7479 | 58.0829 | 57.9248 | 58.6102 | 56.6125 | 123.1522 | 61.4928 | 123.0605 | 61.2248 | 61.3199 | 122.6455 | 61.2611 | 122.4329 | 61.8323 | 61.8911 | 61.7406 | 61.7994
6572.0781 | 123.3215 | -61.235 | 61.8256 | -3.637 | -4.1294 | -3.6932 | -3.3856 | -3.5483 | -2.8766 | -4.8011 | 61.908 | 0.23032 | 61.8255 | -0.028522 | 0.048236 | 61.3693 | 0.007721 | 61.1521 | 57.598 | 57.1056 | 57.5418 | 57.8494 | 57.6868 | 58.3584 | 56.4339 | 123.143 | 61.4654 | 123.0605 | 61.2065 | 61.2833 | 122.6043 | 61.2428 | 122.3871 | 61.8597 | 61.9002 | 61.7772 | 61.8177
6573.0625 | 123.3719 | -61.235 | 61.8301 | -3.5225 | -4.0195 | -3.5833 | -3.2757 | -3.4293 | -2.7301 | -4.6638 | 61.8988 | 0.23032 | 61.8026 | -0.023943 | 0.043657 | 61.383 | 0.012299 | 61.1612 | 57.7125 | 57.2155 | 57.6517 | 57.9593 | 57.8058 | 58.5049 | 56.5713 | 123.1338 | 61.4654 | 123.0376 | 61.2111 | 61.2787 | 122.6181 | 61.2473 | 122.3963 | 61.8551 | 61.8865 | 61.7589 | 61.7903
6574.0938 | 123.4039 | -61.235 | 61.7706 | -3.5638 | -4.0745 | -3.6108 | -3.262 | -3.3926 | -2.7393 | -4.7508 | 61.8942 | 0.23032 | 61.8163 | -0.028522 | 0.052814 | 61.3785 | 0.007721 | 61.1612 | 57.6713 | 57.1606 | 57.6243 | 57.973 | 57.8424 | 58.4958 | 56.4843 | 123.1293 | 61.4654 | 123.0513 | 61.2065 | 61.2879 | 122.6135 | 61.2428 | 122.3963 | 61.8414 | 61.8865 | 61.7635 | 61.8086
6575.0625 | 123.3627 | -61.2259 | 61.8713 | -3.6965 | -4.1935 | -3.7573 | -3.4497 | -3.6215 | -2.9178 | -4.9064 | 61.9125 | 0.23032 | 61.8209 | -0.023943 | 0.043657 | 61.3693 | 0.007721 | 61.1521 | 57.5294 | 57.0324 | 57.4686 | 57.7762 | 57.6044 | 58.3081 | 56.3195 | 123.1384 | 61.4562 | 123.0468 | 61.2019 | 61.2695 | 122.5952 | 61.2336 | 122.378 | 61.8689 | 61.9048 | 61.7772 | 61.8132
6576.1094 | 123.3719 | -61.2305 | 61.8301 | -3.811 | -4.2805 | -3.913 | -3.642 | -3.7863 | -2.9682 | -4.9247 | 61.908 | 0.22116 | 61.8209 | -0.028522 | 0.048236 | 61.3647 | 0.012299 | 61.1429 | 57.4195 | 56.95 | 57.3175 | 57.5884 | 57.4441 | 58.2623 | 56.3057 | 123.1384 | 61.4516 | 123.0513 | 61.2019 | 61.2787 | 122.5952 | 61.2428 | 122.3734 | 61.8597 | 61.8957 | 61.7726 | 61.8086
6577.0625 | 123.3948 | -61.2305 | 61.8347 | -3.7011 | -4.1523 | -3.7848 | -3.5321 | -3.6765 | -2.8675 | -4.7874 | 61.9034 | 0.22574 | 61.8209 | -0.023943 | 0.052814 | 61.3647 | 0.016878 | 61.1612 | 57.5294 | 57.0782 | 57.4457 | 57.6983 | 57.554 | 58.363 | 56.4431 | 123.1338 | 61.4562 | 123.0513 | 61.2065 | 61.2833 | 122.5952 | 61.2473 | 122.3917 | 61.8506 | 61.8865 | 61.7681 | 61.804
6578.0938 | 123.3124 | -61.2488 | 61.8347 | -3.8705 | -4.3538 | -3.9816 | -3.6787 | -3.7726 | -3.014 | -5.0117 | 61.9125 | 0.21658 | 61.8163 | -0.033101 | 0.043657 | 61.351 | 0.012299 | 61.1475 | 57.3783 | 56.895 | 57.2671 | 57.5701 | 57.4762 | 58.2348 | 56.2371 | 123.1613 | 61.4654 | 123.0651 | 61.2157 | 61.2924 | 122.5998 | 61.2611 | 122.3963 | 61.8689 | 61.9002 | 61.7726 | 61.804
6579.0625 | 123.3719 | -61.2534 | 61.8118 | -3.6507 | -4.1569 | -3.7252 | -3.3398 | -3.4247 | -2.8675 | -4.879 | 61.8988 | 0.2349 | 61.83 | -0.023943 | 0.052814 | 61.3693 | 0.007721 | 61.1612 | 57.6026 | 57.0965 | 57.5281 | 57.9135 | 57.8287 | 58.3859 | 56.3744 | 123.1522 | 61.4883 | 123.0834 | 61.2294 | 61.3062 | 122.6227 | 61.2611 | 122.4146 | 61.846 | 61.8911 | 61.7772 | 61.8223
6580.0938 | 123.3673 | -61.2396 | 61.8576 | -3.9026 | -4.3904 | -4.0183 | -3.7015 | -3.8092 | -3.0689 | -5.0438 | 61.9125 | 0.22574 | 61.8163 | -0.03768 | 0.048236 | 61.3556 | 0.012299 | 61.1475 | 57.3371 | 56.8492 | 57.2213 | 57.5381 | 57.4304 | 58.1707 | 56.1959 | 123.1522 | 61.4654 | 123.0559 | 61.2019 | 61.2879 | 122.5952 | 61.2519 | 122.3871 | 61.8643 | 61.9002 | 61.7681 | 61.804
6581.0625 | 123.2712 | -61.2534 | 61.8805 | -3.7377 | -4.1798 | -3.8351 | -3.5459 | -3.6673 | -2.9453 | -4.824 | 61.9171 | 0.2349 | 61.8438 | -0.023943 | 0.043657 | 61.3647 | 0.021456 | 61.1658 | 57.5156 | 57.0736 | 57.4182 | 57.7075 | 57.5861 | 58.308 | 56.4293 | 123.1705 | 61.4883 | 123.0971 | 61.2294 | 61.297 | 122.6181 | 61.2748 | 122.4192 | 61.8735 | 61.8957 | 61.8001 | 61.8223
6582.0781 | 123.3536 | -61.2534 | 61.821 | -3.8659 | -4.3034 | -3.9816 | -3.7061 | -3.823 | -3.0735 | -4.9659 | 61.908 | 0.22574 | 61.8163 | -0.028522 | 0.043657 | 61.3601 | 0.012299 | 61.1475 | 57.3874 | 56.95 | 57.2717 | 57.5472 | 57.4304 | 58.1799 | 56.2874 | 123.1613 | 61.4791 | 123.0697 | 61.2248 | 61.297 | 122.6135 | 61.2657 | 122.4008 | 61.8643 | 61.8957 | 61.7726 | 61.804
6583.0625 | 123.3948 | -61.2259 | 61.8668 | -3.7835 | -4.2301 | -3.8809 | -3.5871 | -3.6993 | -3.0048 | -4.911 | 61.9171 | 0.22574 | 61.8209 | -0.028522 | 0.048236 | 61.3647 | 0.007721 | 61.1566 | 57.4424 | 56.9958 | 57.345 | 57.6388 | 57.5265 | 58.2211 | 56.3149 | 123.143 | 61.4516 | 123.0468 | 61.1974 | 61.2741 | 122.5906 | 61.2336 | 122.3825 | 61.8689 | 61.9094 | 61.7726 | 61.8132
6584.0625 | 123.3902 | -61.2305 | 61.853 | -3.6691 | -4.0928 | -3.771 | -3.4818 | -3.5941 | -2.9087 | -4.7737 | 61.9125 | 0.23032 | 61.8392 | -0.033101 | 0.043657 | 61.3693 | 0.012299 | 61.1658 | 57.5614 | 57.1377 | 57.4594 | 57.7487 | 57.6364 | 58.3218 | 56.4568 | 123.143 | 61.4608 | 123.0697 | 61.1974 | 61.2741 | 122.5998 | 61.2428 | 122.3963 | 61.8689 | 61.9002 | 61.7955 | 61.8269
6585.0938 | 123.2849 | -61.2534 | 61.8668 | -3.5225 | -3.8867 | -3.6337 | -3.4314 | -3.5666 | -2.8125 | -4.4898 | 61.8896 | 0.22116 | 61.7888 | -0.033101 | 0.048236 | 61.3739 | 0.012299 | 61.1704 | 57.7308 | 57.3666 | 57.6197 | 57.8219 | 57.6868 | 58.4408 | 56.7635 | 123.143 | 61.4745 | 123.0422 | 61.2203 | 61.3016 | 122.6272 | 61.2657 | 122.4237 | 61.8414 | 61.8773 | 61.7406 | 61.7765
6586.0625 | 123.2941 | -61.2534 | 61.8759 | -3.6645 | -4.0378 | -3.7802 | -3.5321 | -3.681 | -2.9224 | -4.6684 | 61.9125 | 0.23032 | 61.8209 | -0.028522 | 0.048236 | 61.383 | 0.012299 | 61.1704 | 57.5889 | 57.2155 | 57.4732 | 57.7212 | 57.5723 | 58.3309 | 56.585 | 123.1659 | 61.4837 | 123.0742 | 61.2248 | 61.3016 | 122.6364 | 61.2657 | 122.4237 | 61.8643 | 61.9002 | 61.7726 | 61.8086
6587.0938 | 123.317 | -61.2213 | 61.8439 | -3.6233 | -3.9829 | -3.7252 | -3.5047 | -3.6673 | -2.9041 | -4.6088 | 61.908 | 0.2349 | 61.8209 | -0.028522 | 0.052814 | 61.3739 | 0.012299 | 61.1612 | 57.598 | 57.2384 | 57.4961 | 57.7166 | 57.554 | 58.3172 | 56.6125 | 123.1293 | 61.4562 | 123.0422 | 61.1928 | 61.2741 | 122.5952 | 61.2336 | 122.3825 | 61.8551 | 61.8957 | 61.7681 | 61.8086
6588.0625 | 123.3902 | -61.2488 | 61.8576 | -3.7194 | -4.0607 | -3.8168 | -3.6237 | -3.768 | -3.0094 | -4.6913 | 61.908 | 0.22116 | 61.8071 | -0.028522 | 0.052814 | 61.3601 | 0.012299 | 61.1566 | 57.5294 | 57.1881 | 57.432 | 57.6251 | 57.4808 | 58.2394 | 56.5575 | 123.1567 | 61.4699 | 123.0559 | 61.2203 | 61.3016 | 122.6089 | 61.2611 | 122.4054 | 61.8551 | 61.8957 | 61.7543 | 61.7948
6589.0781 | 123.3719 | -61.2259 | 61.8576 | -3.7881 | -4.1523 | -3.8763 | -3.6374 | -3.823 | -3.1284 | -4.8286 | 61.9171 | 0.23032 | 61.8346 | -0.033101 | 0.048236 | 61.3647 | 0.003143 | 61.1475 | 57.4378 | 57.0736 | 57.3496 | 57.5884 | 57.4029 | 58.0974 | 56.3973 | 123.143 | 61.4562 | 123.0605 | 61.1928 | 61.2741 | 122.5906 | 61.229 | 122.3734 | 61.8689 | 61.914 | 61.7864 | 61.8315
6590.0625 | 123.262 | -61.2259 | 61.908 | -3.9529 | -4.3217 | -4.0412 | -3.8069 | -4.0107 | -3.2841 | -5.0071 | 61.9217 | 0.2349 | 61.8529 | -0.028522 | 0.057392 | 61.3556 | 0.012299 | 61.1566 | 57.273 | 56.9042 | 57.1847 | 57.419 | 57.2152 | 57.9418 | 56.2187 | 123.1476 | 61.4608 | 123.0788 | 61.1974 | 61.2833 | 122.5815 | 61.2382 | 122.3825 | 61.8643 | 61.9094 | 61.7955 | 61.8406
6591.1094 | 123.3948 | -61.2305 | 61.8073 | -3.8476 | -4.2164 | -3.9221 | -3.6741 | -3.8458 | -3.1925 | -4.9339 | 61.908 | 0.23032 | 61.8117 | -0.033101 | 0.039079 | 61.3601 | 0.007721 | 61.1475 | 57.3829 | 57.0141 | 57.3083 | 57.5564 | 57.3846 | 58.0379 | 56.2966 | 123.1384 | 61.4608 | 123.0422 | 61.1974 | 61.2695 | 122.5906 | 61.2382 | 122.378 | 61.8689 | 61.9002 | 61.7726 | 61.804
6592.0625 | 123.3582 | -61.2396 | 61.8713 | -3.6919 | -4.0607 | -3.7573 | -3.4726 | -3.6536 | -3.0552 | -4.7828 | 61.9034 | 0.2349 | 61.8392 | -0.019364 | 0.048236 | 61.3693 | 0.007721 | 61.1704 | 57.5477 | 57.1789 | 57.4823 | 57.767 | 57.5861 | 58.1844 | 56.4568 | 123.143 | 61.4745 | 123.0788 | 61.2203 | 61.2879 | 122.6089 | 61.2473 | 122.41 | 61.8551 | 61.8957 | 61.791 | 61.8315
6593.0938 | 123.2254 | -61.2717 | 61.8942 | -3.7148 | -4.079 | -3.7939 | -3.5276 | -3.6856 | -3.0323 | -4.7645 | 61.908 | 0.23032 | 61.8163 | -0.028522 | 0.052814 | 61.3647 | 0.012299 | 61.1658 | 57.5568 | 57.1926 | 57.4777 | 57.7441 | 57.5861 | 58.2394 | 56.5072 | 123.1796 | 61.502 | 123.088 | 61.2431 | 61.3245 | 122.6364 | 61.284 | 122.4375 | 61.8551 | 61.8957 | 61.7635 | 61.804
6594.0625 | 123.4085 | -61.2122 | 61.8851 | -3.8476 | -4.1981 | -3.9496 | -3.7107 | -3.8825 | -3.1651 | -4.8652 | 61.9125 | 0.21658 | 61.8209 | -0.028522 | 0.048236 | 61.3601 | 0.012299 | 61.1521 | 57.3645 | 57.0141 | 57.2626 | 57.5015 | 57.3297 | 58.0471 | 56.3469 | 123.1247 | 61.4287 | 123.033 | 61.1836 | 61.2604 | 122.5723 | 61.2245 | 122.3642 | 61.8643 | 61.9002 | 61.7726 | 61.8086
6595.0938 | 123.2803 | -61.2305 | 61.908 | -3.8613 | -4.2118 | -3.9404 | -3.6741 | -3.8367 | -3.2063 | -4.9202 | 61.9263 | 0.23948 | 61.8529 | -0.033101 | 0.048236 | 61.3601 | 0.007721 | 61.1521 | 57.3691 | 57.0186 | 57.29 | 57.5564 | 57.3938 | 58.0242 | 56.3103 | 123.1567 | 61.4699 | 123.0834 | 61.1974 | 61.2787 | 122.5906 | 61.2382 | 122.3825 | 61.878 | 61.9186 | 61.8047 | 61.8452
6596.0625 | 123.2758 | -61.2579 | 61.8576 | -3.8568 | -4.1889 | -3.9404 | -3.7107 | -3.9008 | -3.1697 | -4.8652 | 61.9171 | 0.22116 | 61.83 | -0.028522 | 0.048236 | 61.3601 | 0.007721 | 61.1429 | 57.4012 | 57.069 | 57.3175 | 57.5472 | 57.3572 | 58.0883 | 56.3927 | 123.175 | 61.4791 | 123.088 | 61.2294 | 61.3062 | 122.6181 | 61.2657 | 122.4008 | 61.8689 | 61.9094 | 61.7818 | 61.8223
6597.0781 | 123.3536 | -61.235 | 61.8759 | -3.9621 | -4.3217 | -4.0686 | -3.7977 | -3.9145 | -3.2887 | -4.9843 | 61.9217 | 0.22116 | 61.83 | -0.033101 | 0.043657 | 61.351 | 0.003143 | 61.1338 | 57.273 | 56.9133 | 57.1664 | 57.4373 | 57.3205 | 57.9464 | 56.2508 | 123.1567 | 61.4562 | 123.0651 | 61.2019 | 61.2787 | 122.586 | 61.2382 | 122.3688 | 61.878 | 61.9185 | 61.7864 | 61.8269
6598.0625 | 123.381 | -61.2167 | 61.8622 | -4.1132 | -4.4774 | -4.2381 | -3.99 | -4.1114 | -3.4306 | -5.1308 | 61.94 | 0.2349 | 61.8667 | -0.023943 | 0.057392 | 61.3373 | 0.012299 | 61.1292 | 57.1036 | 56.7393 | 56.9787 | 57.2267 | 57.1054 | 57.7861 | 56.086 | 123.1567 | 61.4516 | 123.0834 | 61.1928 | 61.2741 | 122.554 | 61.229 | 122.3459 | 61.8826 | 61.9277 | 61.8093 | 61.8544
6599.0938 | 123.2666 | -61.2213 | 61.9308 | -3.9483 | -4.2805 | -4.0595 | -3.8389 | -3.9786 | -3.3207 | -4.9247 | 61.9217 | 0.22116 | 61.8255 | -0.023943 | 0.052814 | 61.351 | 0.012299 | 61.1521 | 57.273 | 56.9408 | 57.1618 | 57.3824 | 57.2427 | 57.9006 | 56.2966 | 123.143 | 61.4425 | 123.0468 | 61.1974 | 61.2741 | 122.5723 | 61.2336 | 122.3734 | 61.8689 | 61.9094 | 61.7726 | 61.8132
6600.0625 | 123.4085 | -61.203 | 61.8713 | -4.0491 | -4.4179 | -4.1923 | -3.9488 | -4.0335 | -3.3345 | -5.0483 | 61.9263 | 0.22574 | 61.8346 | -0.028522 | 0.052814 | 61.3464 | 0.007721 | 61.1292 | 57.1539 | 56.7851 | 57.0107 | 57.2542 | 57.1695 | 57.8685 | 56.1547 | 123.1293 | 61.4287 | 123.0376 | 61.1745 | 61.2558 | 122.5494 | 61.2107 | 122.3322 | 61.8735 | 61.9186 | 61.7818 | 61.8269
6601.1094 | 123.3078 | -61.235 | 61.9263 | -3.9621 | -4.3126 | -4.1098 | -3.8664 | -3.9466 | -3.2337 | -4.9247 | 61.9217 | 0.22574 | 61.8529 | -0.033101 | 0.052814 | 61.3556 | 0.012299 | 61.1429 | 57.273 | 56.9225 | 57.1252 | 57.3687 | 57.2885 | 58.0013 | 56.3103 | 123.1567 | 61.4608 | 123.088 | 61.2019 | 61.2879 | 122.5906 | 61.2473 | 122.378 | 61.8689 | 61.9094 | 61.8001 | 61.8406
6602.0625 | 123.3444 | -61.1664 | 61.8942 | -4.0582 | -4.395 | -4.2197 | -3.9808 | -4.0335 | -3.3207 | -4.9797 | 61.9354 | 0.23032 | 61.8209 | -0.023943 | 0.048236 | 61.3464 | 0.016878 | 61.1338 | 57.1082 | 56.7714 | 56.9466 | 57.1855 | 57.1328 | 57.8456 | 56.1867 | 123.1018 | 61.3967 | 122.9873 | 61.1424 | 61.2146 | 122.5128 | 61.1833 | 122.3001 | 61.8872 | 61.9186 | 61.7726 | 61.804
6603.0781 | 123.3398 | -61.2259 | 61.853 | -4.0353 | -4.3583 | -4.2243 | -3.99 | -4.0198 | -3.2658 | -4.9385 | 61.9263 | 0.23032 | 61.8346 | -0.03768 | 0.048236 | 61.3556 | 0.003143 | 61.1292 | 57.1906 | 56.8675 | 57.0016 | 57.2359 | 57.2061 | 57.9601 | 56.2874 | 123.1522 | 61.4562 | 123.0605 | 61.1882 | 61.2741 | 122.5815 | 61.229 | 122.3551 | 61.878 | 61.9231 | 61.7864 | 61.8315
6604.0625 | 123.4085 | -61.1526 | 61.8896 | -4.2871 | -4.5964 | -4.4853 | -4.3196 | -4.3586 | -3.5085 | -5.1308 | 61.94 | 0.23032 | 61.8712 | -0.028522 | 0.052814 | 61.3327 | 0.012299 | 61.1154 | 56.8655 | 56.5562 | 56.6674 | 56.833 | 56.7941 | 57.6442 | 56.0219 | 123.0927 | 61.383 | 123.0239 | 61.1241 | 61.2055 | 122.4853 | 61.1649 | 122.2681 | 61.8872 | 61.9277 | 61.8184 | 61.8589
6605.0938 | 123.3673 | -61.2259 | 61.8759 | -4.3192 | -4.6651 | -4.5128 | -4.3059 | -4.3403 | -3.5542 | -5.2269 | 61.9446 | 0.22116 | 61.8346 | -0.028522 | 0.043657 | 61.3418 | 0.007721 | 61.1109 | 56.9067 | 56.5608 | 56.7131 | 56.92 | 56.8856 | 57.6717 | 55.999 | 123.1705 | 61.4471 | 123.0605 | 61.1974 | 61.2695 | 122.5677 | 61.2336 | 122.3368 | 61.9009 | 61.9369 | 61.791 | 61.8269
6606.0625 | 123.2666 | -61.2442 | 61.8988 | -4.1864 | -4.5461 | -4.3663 | -4.1228 | -4.1434 | -3.4489 | -5.1399 | 61.9354 | 0.23032 | 61.8621 | -0.028522 | 0.048236 | 61.3373 | 0.012299 | 61.12 | 57.0578 | 56.6981 | 56.878 | 57.1214 | 57.1008 | 57.7953 | 56.1043 | 123.1796 | 61.4745 | 123.1063 | 61.2157 | 61.2924 | 122.5815 | 61.2565 | 122.3642 | 61.8872 | 61.9231 | 61.8138 | 61.8498
6607.0781 | 123.3261 | -61.1984 | 61.8759 | -4.1589 | -4.4728 | -4.3159 | -4.1228 | -4.1571 | -3.4352 | -5.0804 | 61.9308 | 0.22116 | 61.8438 | -0.028522 | 0.052814 | 61.3327 | 0.016878 | 61.12 | 57.0395 | 56.7256 | 56.8825 | 57.0757 | 57.0413 | 57.7632 | 56.118 | 123.1293 | 61.4196 | 123.0422 | 61.1699 | 61.2512 | 122.5311 | 61.2153 | 122.3184 | 61.878 | 61.914 | 61.791 | 61.8269
6608.0625 | 123.2986 | -61.2213 | 61.8896 | -4.1406 | -4.4362 | -4.2976 | -4.1411 | -4.1755 | -3.4123 | -5.0026 | 61.9308 | 0.23032 | 61.8346 | -0.028522 | 0.052814 | 61.3464 | 0.012299 | 61.1292 | 57.0807 | 56.7851 | 56.9237 | 57.0802 | 57.0459 | 57.809 | 56.2187 | 123.1522 | 61.4516 | 123.0559 | 61.1928 | 61.2741 | 122.5677 | 61.2336 | 122.3505 | 61.878 | 61.9186 | 61.7818 | 61.8223
6609.0938 | 123.3627 | -61.2396 | 61.8576 | -4.0536 | -4.395 | -4.2197 | -4.0037 | -4.0152 | -3.3207 | -4.9751 | 61.9308 | 0.23032 | 61.8575 | -0.028522 | 0.048236 | 61.3464 | 0.012299 | 61.1292 | 57.186 | 56.8446 | 57.0199 | 57.2359 | 57.2244 | 57.9189 | 56.2645 | 123.1705 | 61.4699 | 123.0971 | 61.2111 | 61.2879 | 122.586 | 61.2519 | 122.3688 | 61.8826 | 61.9186 | 61.8093 | 61.8452
6610.0625 | 123.2574 | -61.1938 | 61.9263 | -4.3192 | -4.6743 | -4.5036 | -4.3013 | -4.2808 | -3.5085 | -5.2589 | 61.9446 | 0.22574 | 61.8438 | -0.023943 | 0.052814 | 61.3327 | 0.007721 | 61.1246 | 56.8747 | 56.5196 | 56.6902 | 56.8925 | 56.9131 | 57.6854 | 55.9349 | 123.1384 | 61.4196 | 123.0376 | 61.1699 | 61.2467 | 122.5265 | 61.2016 | 122.3184 | 61.8918 | 61.9369 | 61.791 | 61.8361
6611.0938 | 123.436 | -61.1893 | 61.8759 | -4.3512 | -4.7018 | -4.5448 | -4.3013 | -4.267 | -3.5588 | -5.3047 | 61.94 | 0.23032 | 61.8484 | -0.028522 | 0.052814 | 61.3281 | 0.012299 | 61.1109 | 56.838 | 56.4875 | 56.6445 | 56.8879 | 56.9223 | 57.6305 | 55.8845 | 123.1293 | 61.4196 | 123.0376 | 61.1607 | 61.2421 | 122.5174 | 61.2016 | 122.3001 | 61.8872 | 61.9277 | 61.7955 | 61.8361
6612.0625 | 123.262 | -61.1984 | 61.9171 | -4.3421 | -4.7063 | -4.5494 | -4.3059 | -4.2624 | -3.5222 | -5.2681 | 61.9492 | 0.23032 | 61.885 | -0.028522 | 0.048236 | 61.3327 | 0.012299 | 61.1109 | 56.8563 | 56.4921 | 56.649 | 56.8925 | 56.936 | 57.6762 | 55.9303 | 123.1476 | 61.4287 | 123.0834 | 61.1699 | 61.2467 | 122.5311 | 61.2107 | 122.3093 | 61.9009 | 61.9369 | 61.8367 | 61.8727
6613.0938 | 123.3856 | -61.1618 | 61.9263 | -4.5435 | -4.9124 | -4.7737 | -4.5486 | -4.4913 | -3.6916 | -5.4558 | 61.94 | 0.22574 | 61.8621 | -0.028522 | 0.048236 | 61.3235 | 0.007721 | 61.1017 | 56.6183 | 56.2494 | 56.3881 | 56.6132 | 56.6705 | 57.4702 | 55.706 | 123.1018 | 61.3875 | 123.0239 | 61.1333 | 61.21 | 122.4853 | 61.1695 | 122.2635 | 61.8918 | 61.9323 | 61.8138 | 61.8544
6614.0625 | 123.2895 | -61.2076 | 61.9263 | -4.4108 | -4.7933 | -4.6318 | -4.3746 | -4.3265 | -3.5954 | -5.3642 | 61.9492 | 0.23032 | 61.8484 | -0.019364 | 0.052814 | 61.3281 | 0.012299 | 61.1109 | 56.7968 | 56.4142 | 56.5758 | 56.833 | 56.8811 | 57.6121 | 55.8433 | 123.1567 | 61.4379 | 123.0559 | 61.1882 | 61.2604 | 122.5357 | 61.2199 | 122.3184 | 61.8964 | 61.9369 | 61.7955 | 61.8361
6615.0938 | 123.381 | -61.203 | 61.908 | -4.3421 | -4.688 | -4.5494 | -4.2876 | -4.2395 | -3.5039 | -5.2681 | 61.94 | 0.23948 | 61.8896 | -0.028522 | 0.048236 | 61.3327 | 0.012299 | 61.1063 | 56.8609 | 56.515 | 56.6536 | 56.9154 | 56.9635 | 57.6991 | 55.9349 | 123.143 | 61.4425 | 123.0926 | 61.1745 | 61.2512 | 122.5357 | 61.2153 | 122.3093 | 61.8918 | 61.9277 | 61.8413 | 61.8773
6616.0625 | 123.262 | -61.2259 | 61.9354 | -4.4474 | -4.8116 | -4.673 | -4.4066 | -4.3494 | -3.6275 | -5.3963 | 61.9492 | 0.23032 | 61.8575 | -0.028522 | 0.052814 | 61.3235 | 0.007721 | 61.1109 | 56.7785 | 56.4142 | 56.5529 | 56.8193 | 56.8765 | 57.5984 | 55.8296 | 123.1751 | 61.4562 | 123.0834 | 61.1974 | 61.2787 | 122.5494 | 61.2336 | 122.3368 | 61.8964 | 61.9414 | 61.8047 | 61.8498
6617.1094 | 123.2941 | -61.1938 | 61.9492 | -4.3604 | -4.7292 | -4.5998 | -4.3334 | -4.2716 | -3.4856 | -5.2773 | 61.9354 | 0.22116 | 61.8346 | -0.033101 | 0.052814 | 61.3281 | 0.016878 | 61.1246 | 56.8335 | 56.4646 | 56.5941 | 56.8605 | 56.9223 | 57.7083 | 55.9166 | 123.1293 | 61.415 | 123.0285 | 61.1607 | 61.2467 | 122.5219 | 61.2107 | 122.3184 | 61.8826 | 61.9186 | 61.7818 | 61.8177
6618.0625 | 123.2391 | -61.2076 | 61.9537 | -4.5115 | -4.8758 | -4.7509 | -4.4799 | -4.3998 | -3.6366 | -5.4283 | 61.9492 | 0.23032 | 61.8621 | -0.023943 | 0.052814 | 61.3281 | 0.007721 | 61.12 | 56.6961 | 56.3318 | 56.4567 | 56.7277 | 56.8078 | 57.5709 | 55.7792 | 123.1567 | 61.4379 | 123.0697 | 61.1836 | 61.2604 | 122.5357 | 61.2153 | 122.3276 | 61.8964 | 61.9414 | 61.8093 | 61.8544
6619.0938 | 123.2391 | -61.203 | 61.94 | -4.4703 | -4.8071 | -4.6868 | -4.4524 | -4.3998 | -3.5954 | -5.378 | 61.9537 | 0.2349 | 61.885 | -0.019364 | 0.057392 | 61.3235 | 0.012299 | 61.1109 | 56.7327 | 56.3959 | 56.5162 | 56.7506 | 56.8032 | 57.6076 | 55.825 | 123.1567 | 61.4379 | 123.088 | 61.1836 | 61.2604 | 122.5265 | 61.2153 | 122.3139 | 61.8964 | 61.9414 | 61.8276 | 61.8727
6620.0625 | 123.3078 | -61.2167 | 61.94 | -4.4565 | -4.8162 | -4.7005 | -4.4524 | -4.3723 | -3.5497 | -5.3597 | 61.9537 | 0.2349 | 61.8758 | -0.028522 | 0.052814 | 61.3235 | 0.003143 | 61.1292 | 56.7602 | 56.4005 | 56.5162 | 56.7643 | 56.8444 | 57.6671 | 55.8571 | 123.1705 | 61.4516 | 123.0926 | 61.1882 | 61.2695 | 122.5403 | 61.2199 | 122.3459 | 61.9009 | 61.9506 | 61.823 | 61.8727
6621.0781 | 123.4497 | -61.1664 | 61.9537 | -4.2093 | -4.5507 | -4.4624 | -4.2235 | -4.1617 | -3.3345 | -5.0987 | 61.9354 | 0.22574 | 61.8438 | -0.028522 | 0.043657 | 61.3464 | 0.007721 | 61.1383 | 56.9571 | 56.6157 | 56.704 | 56.9429 | 57.0047 | 57.8319 | 56.0677 | 123.1018 | 61.3921 | 123.0102 | 61.1379 | 61.21 | 122.5128 | 61.1741 | 122.3047 | 61.8918 | 61.9277 | 61.8001 | 61.8361
6622.0625 | 123.3673 | -61.2213 | 61.853 | -4.4245 | -4.775 | -4.6822 | -4.4387 | -4.354 | -3.513 | -5.323 | 61.9446 | 0.23032 | 61.8575 | -0.023943 | 0.048236 | 61.3235 | 0.003143 | 61.1246 | 56.7968 | 56.4463 | 56.5391 | 56.7826 | 56.8673 | 57.7083 | 55.8983 | 123.1659 | 61.4516 | 123.0788 | 61.1974 | 61.2695 | 122.5448 | 61.2245 | 122.3459 | 61.8963 | 61.9414 | 61.8093 | 61.8544
6623.0938 | 123.3902 | -61.1893 | 61.8896 | -4.5161 | -4.8437 | -4.7783 | -4.5806 | -4.4913 | -3.6321 | -5.3597 | 61.9629 | 0.2349 | 61.8896 | -0.028522 | 0.052814 | 61.3281 | 0.012299 | 61.12 | 56.6732 | 56.3456 | 56.4109 | 56.6086 | 56.6979 | 57.5572 | 55.8296 | 123.1522 | 61.4242 | 123.0788 | 61.1607 | 61.2421 | 122.5174 | 61.2016 | 122.3093 | 61.9101 | 61.9506 | 61.8367 | 61.8773
6624.0625 | 123.2574 | -61.1938 | 61.9308 | -4.5802 | -4.8986 | -4.8424 | -4.6172 | -4.5051 | -3.6687 | -5.4421 | 61.9629 | 0.2349 | 61.8896 | -0.033101 | 0.048236 | 61.3189 | 0.012299 | 61.1109 | 56.6137 | 56.2952 | 56.3514 | 56.5766 | 56.6888 | 57.5252 | 55.7518 | 123.1567 | 61.4287 | 123.0834 | 61.1607 | 61.2421 | 122.5128 | 61.2061 | 122.3047 | 61.9147 | 61.9506 | 61.8413 | 61.8773
6625.1094 | 123.381 | -61.1664 | 61.8851 | -4.4565 | -4.743 | -4.7417 | -4.5577 | -4.4547 | -3.5085 | -5.2406 | 61.94 | 0.23032 | 61.8529 | -0.028522 | 0.048236 | 61.3189 | 0.012299 | 61.1109 | 56.7098 | 56.4234 | 56.4247 | 56.6087 | 56.7117 | 57.6579 | 55.9258 | 123.1064 | 61.3967 | 123.0193 | 61.1379 | 61.2146 | 122.4853 | 61.1787 | 122.2772 | 61.8918 | 61.9277 | 61.8047 | 61.8406
6626.0625 | 123.3032 | -61.1984 | 61.9171 | -4.5527 | -4.8437 | -4.8333 | -4.6401 | -4.528 | -3.5771 | -5.323 | 61.9583 | 0.23032 | 61.8575 | -0.028522 | 0.048236 | 61.3144 | 0.003143 | 61.1154 | 56.6457 | 56.3547 | 56.3652 | 56.5583 | 56.6705 | 57.6213 | 55.8754 | 123.1567 | 61.4287 | 123.0559 | 61.1699 | 61.2467 | 122.5128 | 61.2016 | 122.3139 | 61.9101 | 61.9552 | 61.8093 | 61.8544
6627.0938 | 123.3032 | -61.1801 | 61.9446 | -4.3192 | -4.6285 | -4.5952 | -4.3746 | -4.267 | -3.3757 | -5.0758 | 61.9492 | 0.23032 | 61.885 | -0.019364 | 0.052814 | 61.3373 | 0.012299 | 61.1292 | 56.8609 | 56.5516 | 56.5849 | 56.8055 | 56.9131 | 57.8044 | 56.1043 | 123.1293 | 61.4104 | 123.0651 | 61.1608 | 61.2329 | 122.5174 | 61.1924 | 122.3093 | 61.8964 | 61.9369 | 61.8322 | 61.8727
6628.0625 | 123.2666 | -61.2259 | 61.9217 | -4.4108 | -4.7201 | -4.6822 | -4.4707 | -4.3723 | -3.4535 | -5.1994 | 61.9583 | 0.2349 | 61.8712 | -0.028522 | 0.057392 | 61.3281 | 0.012299 | 61.12 | 56.8151 | 56.5058 | 56.5437 | 56.7552 | 56.8536 | 57.7724 | 56.0265 | 123.1842 | 61.4608 | 123.0971 | 61.1974 | 61.2833 | 122.554 | 61.2382 | 122.3459 | 61.9009 | 61.946 | 61.8139 | 61.8589
6629.0938 | 123.2437 | -61.2396 | 61.8988 | -3.9758 | -4.2622 | -4.2381 | -4.0175 | -3.9099 | -3.0369 | -4.7187 | 61.9171 | 0.22574 | 61.8209 | -0.023943 | 0.048236 | 61.3556 | 0.007721 | 61.1521 | 57.2638 | 56.9774 | 57.0016 | 57.2222 | 57.3297 | 58.2027 | 56.5209 | 123.1567 | 61.4654 | 123.0605 | 61.2157 | 61.2879 | 122.5952 | 61.2473 | 122.3917 | 61.8689 | 61.9094 | 61.7726 | 61.8132
6630.0625 | 123.262 | -61.2213 | 61.8988 | -4.1818 | -4.4911 | -4.467 | -4.2327 | -4.0976 | -3.2475 | -4.9659 | 61.94 | 0.23032 | 61.8667 | -0.028522 | 0.052814 | 61.3418 | 0.007721 | 61.1338 | 57.0395 | 56.7302 | 56.7543 | 56.9887 | 57.1237 | 57.9738 | 56.2554 | 123.1613 | 61.4516 | 123.088 | 61.1928 | 61.2741 | 122.5631 | 61.229 | 122.3551 | 61.8872 | 61.9323 | 61.8139 | 61.8589
6631.0938 | 123.2712 | -61.2076 | 61.9034 | -4.2688 | -4.5781 | -4.5677 | -4.338 | -4.18 | -3.275 | -5.0575 | 61.9354 | 0.23032 | 61.8575 | -0.033101 | 0.043657 | 61.3373 | 0.003143 | 61.1383 | 56.9388 | 56.6295 | 56.6399 | 56.8696 | 57.0275 | 57.9326 | 56.1501 | 123.143 | 61.4379 | 123.0651 | 61.1745 | 61.2512 | 122.5448 | 61.2107 | 122.3459 | 61.8918 | 61.9323 | 61.8138 | 61.8544
6632.0625 | 123.2986 | -61.2213 | 61.8851 | -4.1269 | -4.4133 | -4.4258 | -4.196 | -4.0427 | -3.1376 | -4.8881 | 61.9263 | 0.23032 | 61.8392 | -0.023943 | 0.057392 | 61.3464 | 0.021456 | 61.1383 | 57.0944 | 56.808 | 56.7955 | 57.0253 | 57.1786 | 58.0837 | 56.3332 | 123.1476 | 61.4516 | 123.0605 | 61.1974 | 61.2787 | 122.5677 | 61.2428 | 122.3596 | 61.8689 | 61.9048 | 61.7818 | 61.8177
6633.1094 | 123.317 | -61.1984 | 61.9125 | -4.5161 | -4.8208 | -4.8241 | -4.6035 | -4.4593 | -3.5085 | -5.2773 | 61.9537 | 0.23948 | 61.8941 | -0.028522 | 0.048236 | 61.3281 | 0.012299 | 61.12 | 56.6824 | 56.3776 | 56.3743 | 56.5949 | 56.7391 | 57.69 | 55.9212 | 123.1522 | 61.4379 | 123.0926 | 61.1699 | 61.2467 | 122.5265 | 61.2107 | 122.3184 | 61.9055 | 61.9414 | 61.8459 | 61.8818
6634.0625 | 123.2803 | -61.2213 | 61.9034 | -4.0628 | -4.3629 | -4.3846 | -4.1273 | -3.9649 | -3.0598 | -4.8286 | 61.9308 | 0.23032 | 61.8392 | -0.028522 | 0.052814 | 61.3464 | 0.012299 | 61.1429 | 57.1585 | 56.8584 | 56.8367 | 57.094 | 57.2564 | 58.1615 | 56.3927 | 123.1522 | 61.4516 | 123.0605 | 61.1928 | 61.2741 | 122.5677 | 61.2336 | 122.3642 | 61.878 | 61.9186 | 61.7864 | 61.8269
6635.0938 | 123.2529 | -61.2305 | 61.9308 | -4.2047 | -4.514 | -4.5402 | -4.3013 | -4.1297 | -3.1697 | -4.9568 | 61.9354 | 0.23032 | 61.8438 | -0.023943 | 0.052814 | 61.3418 | 0.012299 | 61.1246 | 57.0257 | 56.7164 | 56.6902 | 56.9291 | 57.1008 | 58.0608 | 56.2737 | 123.1659 | 61.4608 | 123.0742 | 61.2065 | 61.2833 | 122.5723 | 61.2428 | 122.3551 | 61.8826 | 61.9231 | 61.791 | 61.8315
6636.0625 | 123.2666 | -61.2305 | 61.8896 | -4.1452 | -4.4316 | -4.4716 | -4.2464 | -4.0976 | -3.1284 | -4.8835 | 61.94 | 0.2349 | 61.8712 | -0.033101 | 0.043657 | 61.3418 | 0.007721 | 61.1246 | 57.0853 | 56.7989 | 56.7589 | 56.9841 | 57.1328 | 58.102 | 56.3469 | 123.1705 | 61.4654 | 123.1017 | 61.1974 | 61.2741 | 122.5723 | 61.2382 | 122.3551 | 61.8963 | 61.9323 | 61.8276 | 61.8635
6637.0938 | 123.2712 | -61.2396 | 61.8851 | -4.1223 | -4.4224 | -4.4304 | -4.1731 | -4.0152 | -3.101 | -4.8881 | 61.9354 | 0.22574 | 61.8255 | -0.028522 | 0.039079 | 61.3556 | 0.003143 | 61.1429 | 57.1173 | 56.8172 | 56.8093 | 57.0665 | 57.2244 | 58.1386 | 56.3515 | 123.1751 | 61.4654 | 123.0651 | 61.2111 | 61.2787 | 122.5952 | 61.2428 | 122.3825 | 61.8963 | 61.9323 | 61.7864 | 61.8223
6638.0625 | 123.349 | -61.2305 | 61.8622 | -4.017 | -4.2988 | -4.3663 | -4.1182 | -3.9557 | -2.9682 | -4.7096 | 61.9263 | 0.23032 | 61.83 | -0.033101 | 0.048236 | 61.3418 | 0.007721 | 61.1292 | 57.2135 | 56.9316 | 56.8642 | 57.1123 | 57.2748 | 58.2623 | 56.5209 | 123.1567 | 61.4608 | 123.0605 | 61.1974 | 61.2787 | 122.5723 | 61.2382 | 122.3596 | 61.878 | 61.9186 | 61.7818 | 61.8223
6639.0781 | 123.3032 | -61.2305 | 61.8988 | -4.0124 | -4.2622 | -4.3525 | -4.1273 | -3.9603 | -2.9407 | -4.6546 | 61.9308 | 0.2349 | 61.8575 | -0.023943 | 0.052814 | 61.351 | 0.007721 | 61.1383 | 57.218 | 56.9683 | 56.878 | 57.1031 | 57.2702 | 58.2897 | 56.5758 | 123.1613 | 61.4654 | 123.088 | 61.2065 | 61.2833 | 122.5815 | 61.2382 | 122.3688 | 61.878 | 61.9231 | 61.8047 | 61.8498
6640.0625 | 123.3307 | -61.2259 | 61.8942 | -4.0994 | -4.3355 | -4.4624 | -4.2601 | -4.1022 | -3.0277 | -4.7233 | 61.9263 | 0.23032 | 61.83 | -0.023943 | 0.048236 | 61.3373 | 0.007721 | 61.1429 | 57.1265 | 56.8904 | 56.7635 | 56.9658 | 57.1237 | 58.1982 | 56.5026 | 123.1522 | 61.4562 | 123.0559 | 61.2019 | 61.2741 | 122.5631 | 61.2336 | 122.3688 | 61.878 | 61.9186 | 61.7818 | 61.8223
6641.1094 | 123.3856 | -61.2122 | 61.8805 | -4.0857 | -4.3492 | -4.4304 | -4.1914 | -4.0381 | -3.0552 | -4.7737 | 61.9263 | 0.23032 | 61.8575 | -0.028522 | 0.043657 | 61.351 | 0.016878 | 61.1429 | 57.1265 | 56.863 | 56.7818 | 57.0207 | 57.174 | 58.157 | 56.4385 | 123.1384 | 61.4425 | 123.0697 | 61.1836 | 61.2558 | 122.5631 | 61.229 | 122.3551 | 61.8826 | 61.9094 | 61.8138 | 61.8406
6642.0625 | 123.2986 | -61.203 | 61.908 | -4.2917 | -4.5598 | -4.6501 | -4.4112 | -4.2487 | -3.22 | -4.9659 | 61.9446 | 0.2349 | 61.8621 | -0.03768 | 0.052814 | 61.3373 | 0.007721 | 61.1338 | 56.9113 | 56.6432 | 56.5529 | 56.7918 | 56.9543 | 57.983 | 56.2371 | 123.1476 | 61.4379 | 123.0651 | 61.1653 | 61.2558 | 122.5403 | 61.2107 | 122.3368 | 61.8918 | 61.9369 | 61.8093 | 61.8544
6643.0938 | 123.2895 | -61.2259 | 61.9125 | -4.2917 | -4.5736 | -4.6547 | -4.4021 | -4.2304 | -3.1925 | -4.9293 | 61.9354 | 0.23032 | 61.8484 | -0.028522 | 0.052814 | 61.3327 | 0.007721 | 61.1383 | 56.9342 | 56.6523 | 56.5712 | 56.8238 | 56.9955 | 58.0333 | 56.2966 | 123.1613 | 61.4562 | 123.0742 | 61.1974 | 61.2787 | 122.5586 | 61.2336 | 122.3642 | 61.8826 | 61.9277 | 61.7955 | 61.8406
6644.0625 | 123.3353 | -61.2259 | 61.8439 | -3.9438 | -4.2897 | -4.3296 | -3.9808 | -3.7222 | -2.8125 | -4.6546 | 61.9125 | 0.23032 | 61.8575 | -0.023943 | 0.048236 | 61.351 | 0.007721 | 61.1429 | 57.2821 | 56.9362 | 56.8963 | 57.2451 | 57.5037 | 58.4134 | 56.5713 | 123.1384 | 61.4562 | 123.0834 | 61.2019 | 61.2741 | 122.5769 | 61.2336 | 122.3688 | 61.8643 | 61.9048 | 61.8093 | 61.8498
6645.0938 | 123.317 | -61.2259 | 61.8805 | -4.0582 | -4.34 | -4.4487 | -4.1594 | -3.9099 | -2.9178 | -4.7233 | 61.9171 | 0.22574 | 61.8346 | -0.028522 | 0.048236 | 61.351 | 0.012299 | 61.1383 | 57.1677 | 56.8859 | 56.7772 | 57.0665 | 57.316 | 58.3081 | 56.5026 | 123.143 | 61.4516 | 123.0605 | 61.1974 | 61.2741 | 122.5769 | 61.2382 | 122.3642 | 61.8689 | 61.9048 | 61.7864 | 61.8223
6646.0625 | 123.2574 | -61.2259 | 61.9263 | -4.104 | -4.3996 | -4.5082 | -4.1914 | -3.9557 | -2.9911 | -4.7691 | 61.9308 | 0.2349 | 61.8621 | -0.033101 | 0.048236 | 61.351 | 0.007721 | 61.1429 | 57.1219 | 56.8263 | 56.7177 | 57.0344 | 57.2702 | 58.2348 | 56.4568 | 123.1567 | 61.4608 | 123.088 | 61.1928 | 61.2741 | 122.5769 | 61.2336 | 122.3688 | 61.8826 | 61.9231 | 61.8138 | 61.8544
6647.0938 | 123.2666 | -61.2579 | 61.8713 | -3.9712 | -4.2576 | -4.3846 | -4.0724 | -3.8321 | -2.8171 | -4.586 | 61.9125 | 0.2349 | 61.8255 | -0.028522 | 0.057392 | 61.3556 | 0.003143 | 61.1475 | 57.2867 | 57.0003 | 56.8734 | 57.1855 | 57.4258 | 58.4408 | 56.672 | 123.1705 | 61.4928 | 123.0834 | 61.2294 | 61.3153 | 122.6135 | 61.2611 | 122.4054 | 61.8551 | 61.9094 | 61.7681 | 61.8223
6648.0625 | 123.2986 | -61.2213 | 61.9034 | -3.8522 | -4.1752 | -4.2426 | -3.8618 | -3.6353 | -2.7347 | -4.5447 | 61.9125 | 0.23032 | 61.8438 | -0.023943 | 0.052814 | 61.3693 | 0.007721 | 61.1566 | 57.3691 | 57.0461 | 56.9787 | 57.3595 | 57.5861 | 58.4866 | 56.6766 | 123.1338 | 61.4516 | 123.0651 | 61.1974 | 61.2741 | 122.5906 | 61.229 | 122.378 | 61.8597 | 61.9048 | 61.791 | 61.8361
6649.1094 | 123.3536 | -61.2167 | 61.8439 | -3.9575 | -4.2897 | -4.3663 | -4.022 | -3.7268 | -2.7759 | -4.618 | 61.9125 | 0.22116 | 61.8346 | -0.023943 | 0.052814 | 61.351 | 0.012299 | 61.1521 | 57.2592 | 56.9271 | 56.8505 | 57.1947 | 57.4899 | 58.4408 | 56.5987 | 123.1293 | 61.4379 | 123.0514 | 61.1928 | 61.2695 | 122.5677 | 61.229 | 122.3688 | 61.8597 | 61.9002 | 61.7818 | 61.8223
6650.0625 | 123.3536 | -61.2442 | 61.8851 | -4.2505 | -4.5736 | -4.6868 | -4.3975 | -4.1114 | -3.0186 | -4.8469 | 61.9492 | 0.2349 | 61.8621 | -0.019364 | 0.052814 | 61.3373 | 0.003143 | 61.1383 | 56.9937 | 56.6707 | 56.5574 | 56.8467 | 57.1328 | 58.2256 | 56.3973 | 123.1934 | 61.4791 | 123.1063 | 61.2248 | 61.297 | 122.5815 | 61.2473 | 122.3825 | 61.8964 | 61.946 | 61.8093 | 61.8589
6651.0938 | 123.2895 | -61.2488 | 61.8851 | -3.8522 | -4.1981 | -4.2793 | -3.9351 | -3.6307 | -2.6111 | -4.4669 | 61.9125 | 0.22574 | 61.8255 | -0.023943 | 0.048236 | 61.3601 | 0.012299 | 61.1658 | 57.3966 | 57.0507 | 56.9695 | 57.3137 | 57.6181 | 58.6377 | 56.7819 | 123.1613 | 61.4745 | 123.0742 | 61.2248 | 61.297 | 122.6089 | 61.2611 | 122.4146 | 61.8643 | 61.9002 | 61.7772 | 61.8132
6652.0625 | 123.3948 | -61.2579 | 61.8439 | -3.9346 | -4.2805 | -4.3479 | -4.0083 | -3.7177 | -2.6889 | -4.5722 | 61.908 | 0.22574 | 61.83 | -0.023943 | 0.048236 | 61.3556 | 0.012299 | 61.1383 | 57.3233 | 56.9774 | 56.91 | 57.2496 | 57.5403 | 58.569 | 56.6857 | 123.1659 | 61.4837 | 123.088 | 61.234 | 61.3062 | 122.6135 | 61.2702 | 122.3963 | 61.8597 | 61.8957 | 61.7818 | 61.8177
6653.0938 | 123.3032 | -61.2167 | 61.8805 | -3.93 | -4.2622 | -4.3479 | -4.0037 | -3.736 | -2.6889 | -4.5722 | 61.9263 | 0.23948 | 61.8529 | -0.023943 | 0.052814 | 61.3601 | 0.012299 | 61.1521 | 57.2867 | 56.9545 | 56.8688 | 57.213 | 57.4808 | 58.5278 | 56.6445 | 123.143 | 61.4562 | 123.0697 | 61.1928 | 61.2695 | 122.5769 | 61.229 | 122.3688 | 61.8735 | 61.914 | 61.8001 | 61.8406
6654.0625 | 123.2712 | -61.2808 | 61.8668 | -3.8797 | -4.1981 | -4.293 | -3.9717 | -3.6765 | -2.6202 | -4.4944 | 61.908 | 0.22574 | 61.8117 | -0.028522 | 0.039079 | 61.3601 | 0.007721 | 61.1429 | 57.4012 | 57.0827 | 56.9878 | 57.3091 | 57.6044 | 58.6606 | 56.7864 | 123.1888 | 61.5066 | 123.0925 | 61.2523 | 61.3199 | 122.641 | 61.2885 | 122.4237 | 61.8689 | 61.9002 | 61.7726 | 61.804
6655.0938 | 123.3307 | -61.2534 | 61.8622 | -3.9117 | -4.2256 | -4.3205 | -3.9992 | -3.7039 | -2.6981 | -4.5356 | 61.9171 | 0.2349 | 61.8346 | -0.028522 | 0.048236 | 61.3556 | 0.007721 | 61.1429 | 57.3416 | 57.0278 | 56.9329 | 57.2542 | 57.5494 | 58.5553 | 56.7178 | 123.1705 | 61.4883 | 123.088 | 61.2248 | 61.3016 | 122.6089 | 61.2611 | 122.3963 | 61.8689 | 61.9094 | 61.7864 | 61.8269
6656.0625 | 123.2941 | -61.2534 | 61.8759 | -3.9529 | -4.2439 | -4.38 | -4.0907 | -3.8184 | -2.7301 | -4.5447 | 61.9217 | 0.23948 | 61.8484 | -0.028522 | 0.048236 | 61.3601 | -0.001436 | 61.1429 | 57.3004 | 57.0095 | 56.8734 | 57.1626 | 57.435 | 58.5232 | 56.7086 | 123.175 | 61.4928 | 123.1017 | 61.2248 | 61.3016 | 122.6135 | 61.2519 | 122.3963 | 61.8735 | 61.9231 | 61.8001 | 61.8498
6657.125 | 123.3627 | -61.2259 | 61.8347 | -4.1086 | -4.395 | -4.5586 | -4.2693 | -3.9786 | -2.8354 | -4.6546 | 61.9171 | 0.23032 | 61.8209 | -0.028522 | 0.048236 | 61.3556 | 0.007721 | 61.1338 | 57.1173 | 56.8309 | 56.6673 | 56.9566 | 57.2473 | 58.3905 | 56.5713 | 123.143 | 61.4562 | 123.0468 | 61.1974 | 61.2741 | 122.5815 | 61.2336 | 122.3596 | 61.8689 | 61.9094 | 61.7726 | 61.8132
6658.0625 | 123.3032 | -61.2305 | 61.8576 | -3.985 | -4.2622 | -4.4304 | -4.0953 | -3.7955 | -2.7347 | -4.5676 | 61.9125 | 0.23032 | 61.8621 | -0.028522 | 0.048236 | 61.351 | 0.012299 | 61.1338 | 57.2455 | 56.9683 | 56.8001 | 57.1352 | 57.435 | 58.4958 | 56.6628 | 123.143 | 61.4608 | 123.0926 | 61.2019 | 61.2787 | 122.5815 | 61.2428 | 122.3642 | 61.8643 | 61.9002 | 61.8138 | 61.8498
6659.0781 | 123.3948 | -61.2442 | 61.8484 | -3.811 | -4.0836 | -4.2564 | -3.9305 | -3.6353 | -2.6111 | -4.3982 | 61.9125 | 0.23032 | 61.8209 | -0.023943 | 0.043657 | 61.3647 | 0.012299 | 61.1658 | 57.4332 | 57.1606 | 56.9878 | 57.3137 | 57.6089 | 58.6331 | 56.846 | 123.1567 | 61.4745 | 123.0651 | 61.2203 | 61.2879 | 122.6089 | 61.2565 | 122.41 | 61.8689 | 61.9002 | 61.7772 | 61.8086
6660.0625 | 123.3398 | -61.235 | 61.8393 | -3.7332 | -4.0195 | -4.1602 | -3.8069 | -3.5025 | -2.5195 | -4.3662 | 61.9034 | 0.22574 | 61.8071 | -0.023943 | 0.057392 | 61.3739 | 0.016878 | 61.1521 | 57.5019 | 57.2155 | 57.0748 | 57.4282 | 57.7325 | 58.7155 | 56.8688 | 123.1384 | 61.4608 | 123.0422 | 61.2111 | 61.2924 | 122.6089 | 61.2519 | 122.3871 | 61.846 | 61.8865 | 61.7498 | 61.7903
6661.0781 | 123.3948 | -61.2167 | 61.8622 | -3.9254 | -4.221 | -4.3571 | -4.0312 | -3.7177 | -2.6706 | -4.4669 | 61.9217 | 0.23032 | 61.8529 | -0.023943 | 0.043657 | 61.3556 | 0.012299 | 61.1429 | 57.2913 | 56.9958 | 56.8596 | 57.1855 | 57.4991 | 58.5461 | 56.7498 | 123.1384 | 61.4471 | 123.0697 | 61.1928 | 61.2604 | 122.5723 | 61.229 | 122.3596 | 61.878 | 61.9094 | 61.8093 | 61.8406
6662.0625 | 123.349 | -61.2625 | 61.8118 | -3.7927 | -4.1111 | -4.2243 | -3.8664 | -3.5712 | -2.5378 | -4.3616 | 61.908 | 0.22116 | 61.8071 | -0.028522 | 0.048236 | 61.3693 | 0.007721 | 61.1429 | 57.4698 | 57.1514 | 57.0382 | 57.3961 | 57.6913 | 58.7247 | 56.9009 | 123.1705 | 61.4837 | 123.0697 | 61.234 | 61.3107 | 122.6318 | 61.2702 | 122.4054 | 61.8597 | 61.9002 | 61.7589 | 61.7994
6663.0938 | 123.349 | -61.2534 | 61.853 | -3.7469 | -4.0607 | -4.1785 | -3.8435 | -3.5437 | -2.4966 | -4.3113 | 61.908 | 0.23032 | 61.8346 | -0.019364 | 0.048236 | 61.3693 | 0.012299 | 61.1566 | 57.5065 | 57.1926 | 57.0748 | 57.4099 | 57.7097 | 58.7567 | 56.9421 | 123.1613 | 61.4837 | 123.088 | 61.234 | 61.3016 | 122.6227 | 61.2657 | 122.41 | 61.8597 | 61.8957 | 61.7864 | 61.8223
6664.0625 | 123.3124 | -61.2488 | 61.8622 | -3.6141 | -3.9096 | -4.0549 | -3.7336 | -3.4155 | -2.3501 | -4.151 | 61.9034 | 0.2349 | 61.8026 | -0.028522 | 0.048236 | 61.383 | 0.012299 | 61.1658 | 57.6347 | 57.3392 | 57.1939 | 57.5152 | 57.8333 | 58.8987 | 57.0978 | 123.1522 | 61.4837 | 123.0513 | 61.2203 | 61.297 | 122.6318 | 61.2611 | 122.4146 | 61.8551 | 61.8911 | 61.7543 | 61.7903
6665.1094 | 123.349 | -61.2579 | 61.8439 | -3.55 | -3.8638 | -4.0045 | -3.6329 | -3.3148 | -2.2677 | -4.0915 | 61.908 | 0.2349 | 61.83 | -0.019364 | 0.034501 | 61.383 | 0.007721 | 61.1521 | 57.7079 | 57.3941 | 57.2534 | 57.6251 | 57.9431 | 58.9902 | 57.1664 | 123.1659 | 61.4928 | 123.088 | 61.2386 | 61.2924 | 122.641 | 61.2657 | 122.41 | 61.8735 | 61.9002 | 61.7955 | 61.8223
6666.0625 | 123.2391 | -61.2671 | 61.8347 | -3.5683 | -3.8684 | -4.0229 | -3.6512 | -3.3331 | -2.2723 | -4.1052 | 61.8805 | 0.22116 | 61.7888 | -0.023943 | 0.048236 | 61.3785 | 0.012299 | 61.1612 | 57.6988 | 57.3987 | 57.2442 | 57.6159 | 57.934 | 58.9948 | 57.1618 | 123.1476 | 61.4883 | 123.0559 | 61.2431 | 61.3153 | 122.6455 | 61.2794 | 122.4283 | 61.8323 | 61.8682 | 61.7406 | 61.7765
6667.0938 | 123.2712 | -61.2534 | 61.8759 | -3.6004 | -3.9096 | -4.0595 | -3.6878 | -3.356 | -2.2998 | -4.1327 | 61.8988 | 0.2349 | 61.8392 | -0.023943 | 0.052814 | 61.383 | 0.012299 | 61.1612 | 57.653 | 57.3437 | 57.1939 | 57.5655 | 57.8974 | 58.9536 | 57.1206 | 123.1522 | 61.4883 | 123.0926 | 61.2294 | 61.3062 | 122.6364 | 61.2657 | 122.4146 | 61.846 | 61.8865 | 61.7864 | 61.8269
6668.0781 | 123.2574 | -61.29 | 61.8576 | -3.3028 | -3.5799 | -3.7985 | -3.468 | -3.15 | -2.0388 | -3.7298 | 61.8896 | 0.22574 | 61.7843 | -0.023943 | 0.052814 | 61.3968 | 0.003143 | 61.1887 | 57.9872 | 57.71 | 57.4915 | 57.8219 | 58.14 | 59.2512 | 57.5601 | 123.1796 | 61.5157 | 123.0742 | 61.266 | 61.3428 | 122.6867 | 61.2931 | 122.4787 | 61.8368 | 61.8865 | 61.7314 | 61.7811
6669.0781 | 123.3215 | -61.2534 | 61.853 | -3.3944 | -3.6761 | -3.8763 | -3.555 | -3.2095 | -2.0937 | -3.8397 | 61.8896 | 0.2349 | 61.8117 | -0.028522 | 0.052814 | 61.3968 | 0.016878 | 61.1841 | 57.859 | 57.5773 | 57.377 | 57.6983 | 58.0438 | 59.1596 | 57.4136 | 123.143 | 61.4883 | 123.0651 | 61.2248 | 61.3062 | 122.6501 | 61.2702 | 122.4375 | 61.8368 | 61.8728 | 61.7589 | 61.7948
6670.0625 | 123.3307 | -61.29 | 61.8118 | -3.3165 | -3.5983 | -3.7893 | -3.4635 | -3.1363 | -2.0434 | -3.7802 | 61.8851 | 0.21658 | 61.7843 | -0.023943 | 0.043657 | 61.3968 | 0.003143 | 61.1841 | 57.9735 | 57.6917 | 57.5006 | 57.8265 | 58.1537 | 59.2466 | 57.5098 | 123.175 | 61.5066 | 123.0742 | 61.266 | 61.3336 | 122.6867 | 61.2931 | 122.4741 | 61.8414 | 61.8819 | 61.7406 | 61.7811
6671.0625 | 123.2849 | -61.2808 | 61.8347 | -3.0922 | -3.3647 | -3.5696 | -3.2391 | -2.9119 | -1.7778 | -3.4963 | 61.8713 | 0.23032 | 61.798 | -0.023943 | 0.048236 | 61.4014 | 0.012299 | 61.1978 | 58.1886 | 57.9161 | 57.7112 | 58.0417 | 58.3689 | 59.503 | 57.7845 | 123.1522 | 61.5111 | 123.0788 | 61.2569 | 61.3291 | 122.6822 | 61.2931 | 122.4787 | 61.8231 | 61.859 | 61.7498 | 61.7857
6672.0938 | 123.2574 | -61.3129 | 61.8439 | -3.0556 | -3.319 | -3.5604 | -3.2162 | -2.8936 | -1.7366 | -3.4139 | 61.8622 | 0.22574 | 61.7705 | -0.028522 | 0.043657 | 61.4105 | 0.016878 | 61.1978 | 58.2573 | 57.9939 | 57.7524 | 58.0966 | 58.4192 | 59.5763 | 57.8989 | 123.175 | 61.5386 | 123.0834 | 61.2843 | 61.3565 | 122.7234 | 61.3297 | 122.5107 | 61.8185 | 61.8453 | 61.7269 | 61.7536
6673.0781 | 123.3215 | -61.2762 | 61.8256 | -3.0143 | -3.2823 | -3.5238 | -3.1842 | -2.857 | -1.7091 | -3.359 | 61.8668 | 0.23032 | 61.7888 | -0.023943 | 0.043657 | 61.4105 | 0.016878 | 61.2024 | 58.2619 | 57.9939 | 57.7525 | 58.0921 | 58.4192 | 59.5671 | 57.9172 | 123.143 | 61.5066 | 123.0651 | 61.2523 | 61.3199 | 122.6868 | 61.2931 | 122.4787 | 61.8231 | 61.8499 | 61.7452 | 61.772
6674.0938 | 123.3032 | -61.2854 | 61.8301 | -3.0418 | -3.2869 | -3.5467 | -3.1979 | -2.8707 | -1.7366 | -3.4048 | 61.8668 | 0.23032 | 61.7705 | -0.028522 | 0.048236 | 61.4059 | 0.012299 | 61.2024 | 58.2436 | 57.9985 | 57.7387 | 58.0875 | 58.4147 | 59.5488 | 57.8806 | 123.1522 | 61.5157 | 123.0559 | 61.2569 | 61.3336 | 122.6913 | 61.2977 | 122.4878 | 61.8185 | 61.8545 | 61.7223 | 61.7582
6675.0625 | 123.381 | -61.29 | 61.7981 | -2.9182 | -3.1679 | -3.4414 | -3.0835 | -2.7426 | -1.5855 | -3.2537 | 61.853 | 0.22574 | 61.7659 | -0.028522 | 0.043657 | 61.4197 | 0.003143 | 61.207 | 58.3718 | 58.1221 | 57.8486 | 58.2065 | 58.5474 | 59.7044 | 58.0363 | 123.143 | 61.5157 | 123.0559 | 61.2615 | 61.3336 | 122.7096 | 61.2931 | 122.497 | 61.8094 | 61.8499 | 61.7223 | 61.7628
6676.0625 | 123.2346 | -61.322 | 61.7935 | -2.8678 | -3.1037 | -3.4047 | -3.0835 | -2.738 | -1.5581 | -3.2033 | 61.8622 | 0.23032 | 61.7751 | -0.028522 | 0.048236 | 61.4197 | 0.007721 | 61.207 | 58.4542 | 58.2183 | 57.9173 | 58.2386 | 58.584 | 59.764 | 58.1187 | 123.1842 | 61.5523 | 123.0971 | 61.2935 | 61.3703 | 122.7417 | 61.3297 | 122.529 | 61.8139 | 61.8545 | 61.7269 | 61.7674
6677.0938 | 123.2254 | -61.29 | 61.8576 | -2.8541 | -3.1083 | -3.3635 | -3.0056 | -2.6739 | -1.5489 | -3.1896 | 61.8484 | 0.22574 | 61.7614 | -0.028522 | 0.048236 | 61.4242 | 0.012299 | 61.2162 | 58.4359 | 58.1816 | 57.9264 | 58.2844 | 58.6161 | 59.7411 | 58.1004 | 123.1384 | 61.5157 | 123.0513 | 61.2615 | 61.3382 | 122.7142 | 61.3023 | 122.5061 | 61.8002 | 61.8361 | 61.7131 | 61.7491
6678.0781 | 123.317 | -61.29 | 61.8347 | -2.8953 | -3.1541 | -3.4276 | -3.0514 | -2.6876 | -1.5764 | -3.2217 | 61.8576 | 0.22574 | 61.7843 | -0.033101 | 0.048236 | 61.4151 | 0.012299 | 61.2162 | 58.3947 | 58.1359 | 57.8623 | 58.2386 | 58.6024 | 59.7136 | 58.0683 | 123.1476 | 61.5157 | 123.0742 | 61.2569 | 61.3382 | 122.7051 | 61.3023 | 122.5061 | 61.8094 | 61.8453 | 61.736 | 61.772
6679.0938 | 123.2529 | -61.3174 | 61.8301 | -2.909 | -3.1679 | -3.4597 | -3.088 | -2.7334 | -1.5993 | -3.1942 | 61.853 | 0.23032 | 61.7568 | -0.023943 | 0.052814 | 61.4242 | 0.007721 | 61.2162 | 58.4084 | 58.1496 | 57.8578 | 58.2294 | 58.584 | 59.7182 | 58.1233 | 123.1705 | 61.5478 | 123.0742 | 61.2935 | 61.3703 | 122.7417 | 61.3252 | 122.5336 | 61.8002 | 61.8453 | 61.704 | 61.7491
6680.0625 | 123.3307 | -61.3037 | 61.7981 | -2.8404 | -3.0809 | -3.3681 | -3.0239 | -2.6876 | -1.5397 | -3.1118 | 61.853 | 0.23032 | 61.7843 | -0.028522 | 0.043657 | 61.4105 | 0.012299 | 61.2162 | 58.4633 | 58.2229 | 57.9356 | 58.2798 | 58.6161 | 59.764 | 58.1919 | 123.1567 | 61.534 | 123.088 | 61.2752 | 61.3474 | 122.7142 | 61.316 | 122.5199 | 61.8094 | 61.8407 | 61.7406 | 61.772
6681.0781 | 123.2758 | -61.2991 | 61.853 | -3.0098 | -3.2594 | -3.5787 | -3.2025 | -2.8753 | -1.6817 | -3.2629 | 61.8576 | 0.23032 | 61.7659 | -0.023943 | 0.048236 | 61.4105 | 0.007721 | 61.2024 | 58.2894 | 58.0397 | 57.7204 | 58.0966 | 58.4238 | 59.6175 | 58.0363 | 123.1567 | 61.5295 | 123.0651 | 61.2752 | 61.3474 | 122.7096 | 61.3069 | 122.5016 | 61.8094 | 61.8499 | 61.7177 | 61.7582
6682.0625 | 123.2483 | -61.3312 | 61.8164 | -2.9686 | -3.2045 | -3.5146 | -3.1796 | -2.857 | -1.6405 | -3.2079 | 61.8668 | 0.2349 | 61.798 | -0.028522 | 0.048236 | 61.4197 | 0.007721 | 61.207 | 58.3626 | 58.1267 | 57.8165 | 58.1516 | 58.4742 | 59.6907 | 58.1233 | 123.1979 | 61.5661 | 123.1292 | 61.3027 | 61.3794 | 122.7508 | 61.3389 | 122.5382 | 61.8185 | 61.859 | 61.7498 | 61.7903
6683.1094 | 123.3353 | -61.2854 | 61.8118 | -3.0464 | -3.264 | -3.5787 | -3.2483 | -2.9394 | -1.7229 | -3.2812 | 61.8668 | 0.23032 | 61.7659 | -0.028522 | 0.048236 | 61.4151 | 0.003143 | 61.207 | 58.239 | 58.0214 | 57.7067 | 58.0371 | 58.346 | 59.5625 | 58.0042 | 123.1522 | 61.5157 | 123.0513 | 61.2569 | 61.3336 | 122.7005 | 61.2885 | 122.4924 | 61.8185 | 61.8636 | 61.7177 | 61.7628
6684.0625 | 123.2254 | -61.3174 | 61.821 | -2.9823 | -3.2091 | -3.5421 | -3.1888 | -2.8524 | -1.6542 | -3.2033 | 61.8668 | 0.2349 | 61.7934 | -0.033101 | 0.052814 | 61.4197 | 0.007721 | 61.1933 | 58.3351 | 58.1084 | 57.7753 | 58.1287 | 58.465 | 59.6632 | 58.1141 | 123.1842 | 61.5523 | 123.1109 | 61.2843 | 61.3703 | 122.7371 | 61.3252 | 122.5107 | 61.8139 | 61.859 | 61.7406 | 61.7857
6685.0781 | 123.3398 | -61.2625 | 61.8118 | -2.9182 | -3.1358 | -3.4643 | -3.1201 | -2.7975 | -1.5855 | -3.1438 | 61.8484 | 0.22574 | 61.7522 | -0.019364 | 0.048236 | 61.4151 | 0.016878 | 61.2024 | 58.3443 | 58.1267 | 57.7982 | 58.1424 | 58.465 | 59.677 | 58.1187 | 123.1109 | 61.4883 | 123.0147 | 61.2431 | 61.3107 | 122.6776 | 61.2794 | 122.4649 | 61.8002 | 61.8316 | 61.704 | 61.7353
6686.0625 | 123.3398 | -61.2579 | 61.8118 | -2.9731 | -3.1724 | -3.5009 | -3.2071 | -2.9028 | -1.7046 | -3.2171 | 61.8668 | 0.23032 | 61.798 | -0.023943 | 0.052814 | 61.4105 | 0.012299 | 61.1978 | 58.2848 | 58.0855 | 57.757 | 58.0509 | 58.3552 | 59.5534 | 58.0409 | 123.1247 | 61.4883 | 123.0559 | 61.234 | 61.3107 | 122.6684 | 61.2702 | 122.4558 | 61.8139 | 61.8545 | 61.7452 | 61.7857
6687.0938 | 123.3078 | -61.2991 | 61.8256 | -2.9045 | -3.09 | -3.4322 | -3.1384 | -2.8433 | -1.645 | -3.1576 | 61.8576 | 0.2349 | 61.7568 | -0.028522 | 0.048236 | 61.4197 | 0.007721 | 61.207 | 58.3947 | 58.2091 | 57.8669 | 58.1607 | 58.4559 | 59.6541 | 58.1416 | 123.1567 | 61.534 | 123.0559 | 61.2706 | 61.3474 | 122.7188 | 61.3069 | 122.5061 | 61.8094 | 61.8499 | 61.7085 | 61.7491
6688.0625 | 123.2208 | -61.2991 | 61.853 | -2.9915 | -3.177 | -3.5375 | -3.2117 | -2.9119 | -1.7046 | -3.2262 | 61.8576 | 0.23948 | 61.7843 | -0.028522 | 0.043657 | 61.4105 | 0.012299 | 61.1887 | 58.3077 | 58.1221 | 57.7616 | 58.0875 | 58.3872 | 59.5946 | 58.0729 | 123.1567 | 61.5386 | 123.0834 | 61.2706 | 61.3428 | 122.7096 | 61.3114 | 122.4878 | 61.8139 | 61.8453 | 61.7406 | 61.772
6689.1094 | 123.2666 | -61.2762 | 61.8301 | -3.1517 | -3.3739 | -3.7115 | -3.3719 | -3.0218 | -1.8007 | -3.3865 | 61.8668 | 0.22574 | 61.7705 | -0.023943 | 0.052814 | 61.4059 | 0.016878 | 61.1887 | 58.1245 | 57.9023 | 57.5647 | 57.9043 | 58.2544 | 59.4755 | 57.8898 | 123.143 | 61.502 | 123.0468 | 61.2523 | 61.3291 | 122.6822 | 61.2931 | 122.4649 | 61.8139 | 61.8499 | 61.7177 | 61.7536
6690.0625 | 123.3994 | -61.2671 | 61.7981 | -3.344 | -3.5754 | -3.8947 | -3.5688 | -3.2324 | -2.0571 | -3.6245 | 61.8805 | 0.22574 | 61.8117 | -0.033101 | 0.039079 | 61.3922 | 0.007721 | 61.1841 | 57.9231 | 57.6917 | 57.3724 | 57.6983 | 58.0347 | 59.21 | 57.6426 | 123.1476 | 61.4928 | 123.0788 | 61.234 | 61.3062 | 122.6593 | 61.2748 | 122.4512 | 61.8414 | 61.8728 | 61.7726 | 61.804
6691.0781 | 123.2437 | -61.2946 | 61.8805 | -3.3394 | -3.5662 | -3.8809 | -3.5413 | -3.1958 | -2.0525 | -3.6245 | 61.8805 | 0.23032 | 61.7934 | -0.023943 | 0.048236 | 61.3968 | 0.016878 | 61.1841 | 57.9551 | 57.7283 | 57.4136 | 57.7533 | 58.0988 | 59.242 | 57.67 | 123.175 | 61.5249 | 123.088 | 61.2706 | 61.3428 | 122.6913 | 61.3114 | 122.4787 | 61.8323 | 61.8636 | 61.7452 | 61.7765
6692.0625 | 123.2941 | -61.3129 | 61.821 | -3.2707 | -3.5067 | -3.8168 | -3.4772 | -3.1134 | -1.9884 | -3.5604 | 61.8713 | 0.2349 | 61.7888 | -0.028522 | 0.048236 | 61.3968 | 0.003143 | 61.1933 | 58.0421 | 57.8062 | 57.496 | 57.8357 | 58.1995 | 59.3244 | 57.7524 | 123.1842 | 61.5478 | 123.1017 | 61.2843 | 61.3611 | 122.7096 | 61.316 | 122.5061 | 61.8231 | 61.8682 | 61.7406 | 61.7857
6693.0781 | 123.2803 | -61.29 | 61.8484 | -3.3165 | -3.5433 | -3.8534 | -3.5276 | -3.1683 | -2.0251 | -3.5971 | 61.8851 | 0.23032 | 61.8071 | -0.028522 | 0.043657 | 61.3968 | 0.012299 | 61.175 | 57.9735 | 57.7467 | 57.4365 | 57.7624 | 58.1217 | 59.2649 | 57.6929 | 123.175 | 61.5203 | 123.0971 | 61.2615 | 61.3336 | 122.6867 | 61.3023 | 122.4649 | 61.8414 | 61.8728 | 61.7635 | 61.7948
6694.0625 | 123.262 | -61.3174 | 61.8118 | -3.1196 | -3.3418 | -3.6474 | -3.3032 | -2.9486 | -1.8465 | -3.3865 | 61.8668 | 0.22574 | 61.7705 | -0.033101 | 0.048236 | 61.4059 | 0.007721 | 61.1933 | 58.1978 | 57.9756 | 57.67 | 58.0142 | 58.3689 | 59.4709 | 57.931 | 123.1842 | 61.5432 | 123.088 | 61.2843 | 61.3657 | 122.7234 | 61.3252 | 122.5107 | 61.8185 | 61.859 | 61.7223 | 61.7628
6695.1094 | 123.2574 | -61.3037 | 61.8576 | -3.0784 | -3.3144 | -3.6245 | -3.2757 | -2.9165 | -1.8099 | -3.3498 | 61.8668 | 0.2349 | 61.7934 | -0.023943 | 0.048236 | 61.4105 | 0.007721 | 61.1978 | 58.2253 | 57.9893 | 57.6792 | 58.028 | 58.3872 | 59.4938 | 57.9539 | 123.1705 | 61.5386 | 123.0971 | 61.2798 | 61.3519 | 122.7142 | 61.3114 | 122.5016 | 61.8185 | 61.859 | 61.7452 | 61.7857
6696.0625 | 123.2849 | -61.3495 | 61.8118 | -2.8266 | -3.0534 | -3.3956 | -3.0377 | -2.6418 | -1.4894 | -3.0248 | 61.8484 | 0.23032 | 61.7522 | -0.023943 | 0.048236 | 61.4242 | 0.012299 | 61.207 | 58.5229 | 58.2961 | 57.9539 | 58.3118 | 58.7076 | 59.8601 | 58.3247 | 123.1979 | 61.5798 | 123.1017 | 61.3255 | 61.3977 | 122.7737 | 61.3618 | 122.5565 | 61.8002 | 61.8361 | 61.704 | 61.7399
6697.0938 | 123.2895 | -61.3358 | 61.8118 | -2.8907 | -3.1037 | -3.4414 | -3.088 | -2.7151 | -1.5718 | -3.1072 | 61.853 | 0.22574 | 61.7614 | -0.019364 | 0.048236 | 61.4242 | 0.007721 | 61.2024 | 58.445 | 58.232 | 57.8944 | 58.2477 | 58.6207 | 59.764 | 58.2286 | 123.1888 | 61.5615 | 123.0971 | 61.3164 | 61.384 | 122.76 | 61.3435 | 122.5382 | 61.8048 | 61.8453 | 61.7131 | 61.7536
6698.0625 | 123.3078 | -61.3037 | 61.8393 | -2.8678 | -3.0763 | -3.4231 | -3.0606 | -2.6693 | -1.5626 | -3.098 | 61.853 | 0.23032 | 61.7705 | -0.023943 | 0.043657 | 61.4197 | 0.012299 | 61.207 | 58.4359 | 58.2274 | 57.8807 | 58.2432 | 58.6344 | 59.7411 | 58.2057 | 123.1567 | 61.534 | 123.0742 | 61.2798 | 61.3474 | 122.7234 | 61.316 | 122.5107 | 61.8094 | 61.8407 | 61.7269 | 61.7582
6699.0625 | 123.262 | -61.3358 | 61.7798 | -2.7717 | -2.9755 | -3.3406 | -2.9873 | -2.5961 | -1.4573 | -2.9607 | 61.8484 | 0.22574 | 61.7476 | -0.033101 | 0.052814 | 61.4288 | -0.001436 | 61.2116 | 58.5641 | 58.3602 | 57.9951 | 58.3485 | 58.7397 | 59.8784 | 58.3751 | 123.1842 | 61.5615 | 123.0834 | 61.3027 | 61.3886 | 122.7646 | 61.3343 | 122.5473 | 61.7956 | 61.8499 | 61.6948 | 61.7491
6700.0938 | 123.3124 | -61.3312 | 61.8073 | -2.7167 | -2.9252 | -3.2811 | -2.9369 | -2.5457 | -1.4024 | -2.8874 | 61.8439 | 0.23032 | 61.7751 | -0.028522 | 0.048236 | 61.4288 | 0.007721 | 61.2162 | 58.6144 | 58.406 | 58.0501 | 58.3942 | 58.7855 | 59.9288 | 58.4437 | 123.175 | 61.5615 | 123.1063 | 61.3027 | 61.3794 | 122.76 | 61.3389 | 122.5473 | 61.7956 | 61.8361 | 61.7269 | 61.7674
6701.0625 | 123.3673 | -61.2762 | 61.7889 | -2.616 | -2.7924 | -3.1667 | -2.8454 | -2.4587 | -1.3429 | -2.7867 | 61.8301 | 0.22116 | 61.743 | -0.028522 | 0.052814 | 61.4334 | 0.003143 | 61.2253 | 58.6602 | 58.4839 | 58.1096 | 58.4309 | 58.8175 | 59.9334 | 58.4895 | 123.1064 | 61.4974 | 123.0193 | 61.2477 | 61.3291 | 122.7096 | 61.2794 | 122.5016 | 61.7773 | 61.827 | 61.6902 | 61.7399
6702.0938 | 123.2986 | -61.3129 | 61.821 | -2.79 | -2.9939 | -3.3406 | -3.0102 | -2.6281 | -1.5031 | -2.9973 | 61.8347 | 0.23032 | 61.7568 | -0.028522 | 0.043657 | 61.4288 | 0.007721 | 61.2116 | 58.5229 | 58.319 | 57.9722 | 58.3027 | 58.6848 | 59.8097 | 58.3155 | 123.1476 | 61.5432 | 123.0697 | 61.2843 | 61.3565 | 122.7417 | 61.3206 | 122.5244 | 61.791 | 61.827 | 61.7131 | 61.7491
6703.0625 | 123.3398 | -61.3174 | 61.7661 | -2.758 | -2.9618 | -3.2949 | -2.9553 | -2.5777 | -1.5214 | -3.0065 | 61.8484 | 0.23032 | 61.7568 | -0.023943 | 0.048236 | 61.4197 | 0.007721 | 61.207 | 58.5595 | 58.3556 | 58.0226 | 58.3622 | 58.7397 | 59.796 | 58.311 | 123.1659 | 61.5478 | 123.0742 | 61.2935 | 61.3657 | 122.7371 | 61.3252 | 122.5244 | 61.8002 | 61.8407 | 61.7085 | 61.7491
6704.1094 | 123.3627 | -61.3403 | 61.7386 | -2.5702 | -2.7466 | -3.1209 | -2.7813 | -2.3809 | -1.3017 | -2.7593 | 61.8301 | 0.23032 | 61.7247 | -0.033101 | 0.043657 | 61.438 | 0.007721 | 61.2345 | 58.7701 | 58.5937 | 58.2195 | 58.5591 | 58.9594 | 60.0387 | 58.5811 | 123.1705 | 61.5706 | 123.0651 | 61.3072 | 61.384 | 122.7783 | 61.3481 | 122.5748 | 61.7865 | 61.8224 | 61.6811 | 61.717
6705.0625 | 123.381 | -61.322 | 61.7569 | -2.6984 | -2.9069 | -3.2536 | -2.8774 | -2.4679 | -1.4116 | -2.9332 | 61.853 | 0.2349 | 61.7843 | -0.028522 | 0.048236 | 61.438 | 0.007721 | 61.2207 | 58.6236 | 58.4152 | 58.0684 | 58.4446 | 58.8541 | 59.9105 | 58.3888 | 123.175 | 61.5569 | 123.1063 | 61.2935 | 61.3703 | 122.76 | 61.3297 | 122.5428 | 61.8048 | 61.8453 | 61.736 | 61.7765
6706.0781 | 123.3398 | -61.3129 | 61.7889 | -2.703 | -2.916 | -3.2811 | -2.9095 | -2.5045 | -1.4207 | -2.9149 | 61.8393 | 0.23032 | 61.7522 | -0.028522 | 0.052814 | 61.438 | 0.007721 | 61.2253 | 58.6099 | 58.3968 | 58.0317 | 58.4034 | 58.8084 | 59.8922 | 58.3979 | 123.1521 | 61.5432 | 123.0651 | 61.2843 | 61.3657 | 122.7508 | 61.3206 | 122.5382 | 61.7865 | 61.8316 | 61.6994 | 61.7445
6707.0781 | 123.2346 | -61.3083 | 61.8164 | -2.7351 | -2.9343 | -3.304 | -2.9461 | -2.5365 | -1.4207 | -2.9287 | 61.8439 | 0.22574 | 61.7705 | -0.019364 | 0.048236 | 61.4334 | 0.007721 | 61.2299 | 58.5732 | 58.374 | 58.0043 | 58.3622 | 58.7717 | 59.8876 | 58.3796 | 123.1521 | 61.534 | 123.0788 | 61.2889 | 61.3565 | 122.7417 | 61.316 | 122.5382 | 61.7956 | 61.8361 | 61.7223 | 61.7628
6708.0938 | 123.2803 | -61.3083 | 61.8256 | -2.8724 | -3.0809 | -3.4276 | -3.0697 | -2.6418 | -1.581 | -3.1164 | 61.8484 | 0.22574 | 61.7614 | -0.033101 | 0.048236 | 61.4242 | 0.012299 | 61.2162 | 58.4359 | 58.2274 | 57.8807 | 58.2386 | 58.6664 | 59.7273 | 58.1919 | 123.1567 | 61.534 | 123.0697 | 61.2752 | 61.3565 | 122.7325 | 61.3206 | 122.5245 | 61.8002 | 61.8361 | 61.7131 | 61.7491
6709.0625 | 123.3948 | -61.3037 | 61.7661 | -2.7305 | -2.9435 | -3.304 | -2.9507 | -2.5228 | -1.4344 | -2.9332 | 61.8393 | 0.23032 | 61.7614 | -0.033101 | 0.043657 | 61.4288 | 0.007721 | 61.2253 | 58.5732 | 58.3602 | 57.9997 | 58.353 | 58.7809 | 59.8693 | 58.3705 | 123.143 | 61.534 | 123.0651 | 61.2706 | 61.3474 | 122.7325 | 61.3114 | 122.529 | 61.7956 | 61.8316 | 61.7177 | 61.7536
6710.1094 | 123.2712 | -61.3541 | 61.7935 | -2.8678 | -3.1037 | -3.446 | -3.0422 | -2.6052 | -1.5581 | -3.098 | 61.8622 | 0.22574 | 61.7888 | -0.033101 | 0.043657 | 61.4242 | 0.003143 | 61.2207 | 58.4862 | 58.2503 | 57.9081 | 58.3118 | 58.7488 | 59.796 | 58.256 | 123.2162 | 61.5798 | 123.1429 | 61.321 | 61.3977 | 122.7783 | 61.3572 | 122.5748 | 61.8185 | 61.859 | 61.7452 | 61.7857
6711.0625 | 123.4039 | -61.3129 | 61.7432 | -2.7076 | -2.9252 | -3.2811 | -2.8912 | -2.4679 | -1.4116 | -2.9287 | 61.8347 | 0.22116 | 61.7476 | -0.019364 | 0.034501 | 61.4288 | 0.012299 | 61.2253 | 58.6053 | 58.3877 | 58.0317 | 58.4217 | 58.845 | 59.9013 | 58.3842 | 123.1476 | 61.534 | 123.0605 | 61.2935 | 61.3474 | 122.7417 | 61.3252 | 122.5382 | 61.8002 | 61.8224 | 61.7131 | 61.7353
6712.0938 | 123.317 | -61.3358 | 61.7661 | -2.7671 | -2.9984 | -3.359 | -2.969 | -2.5045 | -1.439 | -2.9561 | 61.8484 | 0.23948 | 61.7843 | -0.028522 | 0.052814 | 61.438 | 0.007721 | 61.2253 | 58.5686 | 58.3373 | 57.9768 | 58.3668 | 58.8313 | 59.8967 | 58.3796 | 123.1842 | 61.5752 | 123.12 | 61.3072 | 61.3886 | 122.7737 | 61.3435 | 122.5611 | 61.7956 | 61.8407 | 61.7314 | 61.7765
6713.0625 | 123.2895 | -61.3174 | 61.8027 | -2.7122 | -2.9664 | -3.3132 | -2.9049 | -2.4496 | -1.3932 | -2.9332 | 61.8484 | 0.2349 | 61.7522 | -0.028522 | 0.048236 | 61.4334 | 0.012299 | 61.2253 | 58.6053 | 58.3511 | 58.0043 | 58.4126 | 58.8679 | 59.9242 | 58.3842 | 123.1659 | 61.5523 | 123.0697 | 61.2889 | 61.3657 | 122.7508 | 61.3297 | 122.5428 | 61.8002 | 61.8361 | 61.704 | 61.7399
6714.0938 | 123.2254 | -61.3266 | 61.821 | -2.9365 | -3.177 | -3.5146 | -3.1292 | -2.6785 | -1.6313 | -3.1759 | 61.8576 | 0.23032 | 61.7843 | -0.028522 | 0.048236 | 61.4151 | -0.006014 | 61.2207 | 58.3901 | 58.1496 | 57.812 | 58.1974 | 58.6481 | 59.6953 | 58.1507 | 123.1842 | 61.5569 | 123.1109 | 61.2981 | 61.3748 | 122.7417 | 61.3206 | 122.5473 | 61.8094 | 61.8636 | 61.736 | 61.7903
6715.0625 | 123.4039 | -61.2946 | 61.7752 | -2.8678 | -3.0946 | -3.4643 | -3.088 | -2.619 | -1.5581 | -3.0614 | 61.8484 | 0.23032 | 61.7797 | -0.033101 | 0.048236 | 61.4151 | 0.003143 | 61.2253 | 58.4267 | 58.2 | 57.8303 | 58.2065 | 58.6756 | 59.7365 | 58.2331 | 123.143 | 61.5249 | 123.0742 | 61.2615 | 61.3428 | 122.7096 | 61.2977 | 122.5199 | 61.8002 | 61.8453 | 61.7314 | 61.7765
6716.0938 | 123.2803 | -61.3403 | 61.7935 | -2.8129 | -3.0442 | -3.4231 | -3.0148 | -2.5365 | -1.4711 | -2.9744 | 61.8484 | 0.22574 | 61.7568 | -0.033101 | 0.052814 | 61.4242 | 0.003143 | 61.2162 | 58.5274 | 58.2961 | 57.9173 | 58.3256 | 58.8038 | 59.8693 | 58.3659 | 123.1888 | 61.5661 | 123.0971 | 61.3072 | 61.3931 | 122.7646 | 61.3435 | 122.5565 | 61.7956 | 61.8453 | 61.704 | 61.7536
6717.0625 | 123.3444 | -61.2762 | 61.7889 | -2.9365 | -3.177 | -3.5375 | -3.1292 | -2.6602 | -1.5855 | -3.1621 | 61.8576 | 0.22574 | 61.7843 | -0.028522 | 0.048236 | 61.4105 | 0.007721 | 61.207 | 58.3397 | 58.0992 | 57.7387 | 58.147 | 58.6161 | 59.6907 | 58.1141 | 123.1338 | 61.502 | 123.0605 | 61.2477 | 61.3245 | 122.6868 | 61.284 | 122.4832 | 61.8094 | 61.8499 | 61.736 | 61.7765
6718.0938 | 123.2529 | -61.3083 | 61.8622 | -2.9502 | -3.1907 | -3.5467 | -3.1476 | -2.6693 | -1.613 | -3.1621 | 61.853 | 0.23032 | 61.7797 | -0.023943 | 0.039079 | 61.4197 | 0.012299 | 61.1933 | 58.358 | 58.1175 | 57.7616 | 58.1607 | 58.639 | 59.6953 | 58.1461 | 123.1613 | 61.5386 | 123.088 | 61.2843 | 61.3474 | 122.728 | 61.3206 | 122.5016 | 61.8139 | 61.8407 | 61.7406 | 61.7674
6719.0625 | 123.4131 | -61.2808 | 61.8073 | -2.79 | -3.0351 | -3.3773 | -2.9781 | -2.5091 | -1.4573 | -3.034 | 61.8439 | 0.23032 | 61.7522 | -0.028522 | 0.048236 | 61.4288 | 0.016878 | 61.2162 | 58.4908 | 58.2458 | 57.9036 | 58.3027 | 58.7717 | 59.8235 | 58.2469 | 123.1247 | 61.5111 | 123.033 | 61.2523 | 61.3291 | 122.7096 | 61.2977 | 122.497 | 61.7956 | 61.827 | 61.704 | 61.7353
6720.0938 | 123.2483 | -61.3403 | 61.8256 | -2.6527 | -2.884 | -3.272 | -2.882 | -2.3946 | -1.3017 | -2.8005 | 61.8484 | 0.23948 | 61.7797 | -0.023943 | 0.043657 | 61.4334 | 0.016878 | 61.2253 | 58.6877 | 58.4564 | 58.0684 | 58.4583 | 58.9457 | 60.0387 | 58.5399 | 123.1888 | 61.5798 | 123.12 | 61.3164 | 61.384 | 122.7737 | 61.3572 | 122.5656 | 61.8048 | 61.8316 | 61.736 | 61.7628
6721.0625 | 123.3353 | -61.2946 | 61.7523 | -2.6755 | -2.8931 | -3.2949 | -2.882 | -2.3992 | -1.3062 | -2.8096 | 61.8301 | 0.22574 | 61.743 | -0.023943 | 0.052814 | 61.4288 | 0.007721 | 61.2116 | 58.619 | 58.4014 | 57.9997 | 58.4126 | 58.8953 | 59.9883 | 58.4849 | 123.1247 | 61.5203 | 123.0376 | 61.2706 | 61.3474 | 122.7234 | 61.3023 | 122.5061 | 61.7773 | 61.8224 | 61.6902 | 61.7353
6722.0625 | 123.2941 | -61.2991 | 61.8164 | -2.7396 | -2.9664 | -3.3773 | -2.9873 | -2.477 | -1.3658 | -2.8737 | 61.8484 | 0.23948 | 61.7797 | -0.023943 | 0.048236 | 61.4197 | 0.012299 | 61.2162 | 58.5595 | 58.3327 | 57.9219 | 58.3118 | 58.8221 | 59.9334 | 58.4254 | 123.1476 | 61.5386 | 123.0788 | 61.2752 | 61.3474 | 122.7188 | 61.3114 | 122.5153 | 61.8002 | 61.8361 | 61.7314 | 61.7674
6723.0781 | 123.2391 | -61.3586 | 61.7615 | -2.5794 | -2.797 | -3.1987 | -2.8042 | -2.3168 | -1.1964 | -2.6952 | 61.8347 | 0.23032 | 61.7476 | -0.028522 | 0.043657 | 61.438 | -0.001436 | 61.2207 | 58.7792 | 58.5617 | 58.1599 | 58.5545 | 59.0418 | 60.1623 | 58.6635 | 123.1933 | 61.589 | 123.1063 | 61.3301 | 61.4023 | 122.7966 | 61.3572 | 122.5794 | 61.791 | 61.8361 | 61.704 | 61.7491
6724.0625 | 123.3398 | -61.2946 | 61.8073 | -2.8633 | -3.0854 | -3.478 | -3.0835 | -2.5823 | -1.4802 | -2.9836 | 61.8439 | 0.22574 | 61.7522 | -0.033101 | 0.048236 | 61.4242 | 0.012299 | 61.1978 | 58.4313 | 58.2091 | 57.8166 | 58.2111 | 58.7122 | 59.8143 | 58.311 | 123.1384 | 61.5203 | 123.0468 | 61.2615 | 61.3428 | 122.7188 | 61.3069 | 122.4924 | 61.7956 | 61.8316 | 61.704 | 61.7399
6725.1094 | 123.3307 | -61.3312 | 61.7981 | -2.909 | -3.1541 | -3.5421 | -3.1384 | -2.6281 | -1.5352 | -3.0385 | 61.8668 | 0.2349 | 61.7843 | -0.033101 | 0.048236 | 61.4151 | 0.012299 | 61.1978 | 58.4221 | 58.1771 | 57.7891 | 58.1928 | 58.7031 | 59.796 | 58.2926 | 123.1979 | 61.5661 | 123.1154 | 61.2981 | 61.3794 | 122.7463 | 61.3435 | 122.529 | 61.8185 | 61.8545 | 61.736 | 61.772
6726.0625 | 123.3902 | -61.2854 | 61.7981 | -2.8083 | -3.0305 | -3.4185 | -3.0194 | -2.5365 | -1.4573 | -2.9653 | 61.8393 | 0.22574 | 61.7476 | -0.028522 | 0.048236 | 61.4242 | 0.003143 | 61.2116 | 58.4771 | 58.2549 | 57.8669 | 58.266 | 58.7489 | 59.8281 | 58.3201 | 123.1247 | 61.5111 | 123.033 | 61.2569 | 61.3336 | 122.7096 | 61.2885 | 122.497 | 61.791 | 61.8361 | 61.6994 | 61.7445
6727.0938 | 123.3444 | -61.2946 | 61.7889 | -2.671 | -2.8885 | -3.2674 | -2.8912 | -2.3992 | -1.3246 | -2.8142 | 61.8347 | 0.22574 | 61.7568 | -0.033101 | 0.052814 | 61.4288 | 0.016878 | 61.2116 | 58.6236 | 58.406 | 58.0272 | 58.4034 | 58.8953 | 59.97 | 58.4804 | 123.1293 | 61.5203 | 123.0513 | 61.2615 | 61.3474 | 122.7234 | 61.3114 | 122.5061 | 61.7819 | 61.8178 | 61.704 | 61.7399
6728.0625 | 123.3536 | -61.2946 | 61.7844 | -2.7946 | -3.0305 | -3.4002 | -2.9781 | -2.4816 | -1.4161 | -2.9607 | 61.8439 | 0.2349 | 61.7568 | -0.023943 | 0.043657 | 61.4242 | 0.012299 | 61.2162 | 58.5 | 58.2641 | 57.8944 | 58.3164 | 58.8129 | 59.8784 | 58.3339 | 123.1384 | 61.5295 | 123.0513 | 61.2706 | 61.3382 | 122.7188 | 61.3069 | 122.5107 | 61.8002 | 61.8316 | 61.7131 | 61.7445
6729.0938 | 123.262 | -61.3266 | 61.7798 | -2.79 | -3.0168 | -3.4139 | -3.0194 | -2.5045 | -1.4253 | -2.9241 | 61.8439 | 0.2349 | 61.7522 | -0.033101 | 0.048236 | 61.4197 | 0.007721 | 61.2024 | 58.5366 | 58.3098 | 57.9127 | 58.3072 | 58.8221 | 59.9013 | 58.4025 | 123.1705 | 61.5615 | 123.0788 | 61.2935 | 61.3748 | 122.7463 | 61.3343 | 122.529 | 61.7956 | 61.8361 | 61.704 | 61.7445
6730.0625 | 123.2803 | -61.3266 | 61.8073 | -2.877 | -3.1037 | -3.5101 | -3.1109 | -2.5777 | -1.5077 | -3.0019 | 61.8576 | 0.2349 | 61.7934 | -0.023943 | 0.048236 | 61.4242 | 0.012299 | 61.207 | 58.4496 | 58.2229 | 57.8165 | 58.2157 | 58.7488 | 59.8189 | 58.3247 | 123.1842 | 61.5615 | 123.12 | 61.3027 | 61.3748 | 122.7508 | 61.3389 | 122.5336 | 61.8094 | 61.8453 | 61.7452 | 61.7811
6731.0781 | 123.2574 | -61.3174 | 61.7889 | -2.8312 | -3.0534 | -3.4505 | -3.0606 | -2.5594 | -1.4848 | -2.9744 | 61.8439 | 0.22574 | 61.743 | -0.028522 | 0.048236 | 61.4288 | 0.012299 | 61.2116 | 58.4862 | 58.2641 | 57.8669 | 58.2569 | 58.758 | 59.8326 | 58.343 | 123.1613 | 61.5432 | 123.0605 | 61.2889 | 61.3657 | 122.7463 | 61.3297 | 122.529 | 61.7956 | 61.8316 | 61.6948 | 61.7308
6732.0781 | 123.2162 | -61.3312 | 61.8347 | -2.8541 | -3.0854 | -3.4734 | -3.0651 | -2.5594 | -1.4756 | -3.0156 | 61.8576 | 0.2349 | 61.7705 | -0.023943 | 0.048236 | 61.4197 | 0.016878 | 61.2116 | 58.4771 | 58.2457 | 57.8578 | 58.266 | 58.7717 | 59.8555 | 58.3155 | 123.1888 | 61.5661 | 123.1017 | 61.3072 | 61.3794 | 122.7508 | 61.3481 | 122.5428 | 61.8094 | 61.8407 | 61.7223 | 61.7536
6733.0625 | 123.3536 | -61.3083 | 61.7706 | -2.7992 | -3.0396 | -3.4002 | -3.0148 | -2.4999 | -1.439 | -2.9699 | 61.8484 | 0.23032 | 61.7568 | -0.033101 | 0.043657 | 61.4334 | 0.007721 | 61.2116 | 58.5091 | 58.2686 | 57.9081 | 58.2935 | 58.8084 | 59.8693 | 58.3384 | 123.1567 | 61.5386 | 123.0651 | 61.2752 | 61.3519 | 122.7417 | 61.316 | 122.5199 | 61.8048 | 61.8407 | 61.7131 | 61.7491
6734.0938 | 123.3948 | -61.3266 | 61.7569 | -2.8175 | -3.0534 | -3.4505 | -3.056 | -2.5457 | -1.439 | -2.9332 | 61.8439 | 0.22574 | 61.7522 | -0.028522 | 0.048236 | 61.4242 | 0.012299 | 61.2116 | 58.5091 | 58.2732 | 57.8761 | 58.2706 | 58.7809 | 59.8876 | 58.3934 | 123.1705 | 61.5523 | 123.0788 | 61.2981 | 61.3748 | 122.7508 | 61.3389 | 122.5382 | 61.7956 | 61.8316 | 61.704 | 61.7399
6735.0625 | 123.2986 | -61.2991 | 61.8256 | -2.7946 | -3.0396 | -3.4231 | -3.0148 | -2.4999 | -1.4344 | -2.9378 | 61.853 | 0.2349 | 61.7843 | -0.028522 | 0.048236 | 61.4288 | 0.007721 | 61.207 | 58.5046 | 58.2595 | 57.8761 | 58.2844 | 58.7992 | 59.8647 | 58.3613 | 123.1521 | 61.534 | 123.0834 | 61.2706 | 61.3474 | 122.728 | 61.3069 | 122.5061 | 61.8048 | 61.8453 | 61.736 | 61.7765
6736.0625 | 123.349 | -61.3266 | 61.7752 | -2.8129 | -3.058 | -3.4322 | -3.0285 | -2.5045 | -1.4573 | -2.9699 | 61.8393 | 0.23032 | 61.7476 | -0.028522 | 0.052814 | 61.4242 | 0.016878 | 61.2024 | 58.5137 | 58.2686 | 57.8944 | 58.2981 | 58.8221 | 59.8693 | 58.3567 | 123.1659 | 61.5569 | 123.0742 | 61.2981 | 61.3794 | 122.7508 | 61.3435 | 122.529 | 61.7865 | 61.8224 | 61.6948 | 61.7308
6737.0781 | 123.2483 | -61.3037 | 61.8164 | -3.0693 | -3.3235 | -3.7024 | -3.2712 | -2.738 | -1.6908 | -3.2033 | 61.8576 | 0.22574 | 61.7843 | -0.033101 | 0.048236 | 61.4151 | 0.007721 | 61.1841 | 58.2344 | 57.9802 | 57.6014 | 58.0325 | 58.5657 | 59.6129 | 58.1004 | 123.1613 | 61.5294 | 123.088 | 61.2706 | 61.3519 | 122.7188 | 61.3114 | 122.4878 | 61.8094 | 61.8499 | 61.736 | 61.7765
6738.0625 | 123.3261 | -61.2991 | 61.7249 | -3.0556 | -3.3144 | -3.6978 | -3.2666 | -2.7288 | -1.6771 | -3.2033 | 61.8576 | 0.2349 | 61.7843 | -0.028522 | 0.043657 | 61.4151 | 0.007721 | 61.1933 | 58.2436 | 57.9848 | 57.6014 | 58.0325 | 58.5703 | 59.622 | 58.0958 | 123.1567 | 61.534 | 123.0834 | 61.2706 | 61.3428 | 122.7142 | 61.3069 | 122.4924 | 61.8139 | 61.8499 | 61.7406 | 61.7765
6739.0781 | 123.2712 | -61.3266 | 61.8073 | -2.8312 | -3.0671 | -3.4505 | -3.0468 | -2.5549 | -1.5214 | -2.9882 | 61.8393 | 0.21658 | 61.743 | -0.033101 | 0.052814 | 61.4242 | 0.007721 | 61.2116 | 58.4954 | 58.2595 | 57.8761 | 58.2798 | 58.7717 | 59.8052 | 58.3384 | 123.1659 | 61.5432 | 123.0696 | 61.2935 | 61.3794 | 122.7508 | 61.3343 | 122.5382 | 61.7865 | 61.8316 | 61.6902 | 61.7353
6740.0625 | 123.2254 | -61.2991 | 61.8439 | -2.8953 | -3.1312 | -3.5146 | -3.1109 | -2.5961 | -1.5626 | -3.0294 | 61.8576 | 0.2349 | 61.798 | -0.028522 | 0.048236 | 61.4242 | 0.016878 | 61.207 | 58.4038 | 58.1679 | 57.7845 | 58.1882 | 58.7031 | 59.7365 | 58.2698 | 123.1567 | 61.534 | 123.0971 | 61.2706 | 61.3474 | 122.7234 | 61.316 | 122.5061 | 61.8094 | 61.8407 | 61.7498 | 61.7811
6741.0938 | 123.2849 | -61.3129 | 61.8393 | -3.0647 | -3.3098 | -3.6703 | -3.262 | -2.7654 | -1.7687 | -3.2629 | 61.8668 | 0.2349 | 61.7705 | -0.028522 | 0.048236 | 61.4105 | 0.012299 | 61.1978 | 58.2482 | 58.0031 | 57.6426 | 58.0509 | 58.5474 | 59.5442 | 58.05 | 123.1796 | 61.5478 | 123.0834 | 61.2843 | 61.3611 | 122.7234 | 61.3252 | 122.5107 | 61.8185 | 61.8545 | 61.7223 | 61.7582
6742.0625 | 123.2574 | -61.29 | 61.8576 | -2.996 | -3.2457 | -3.6199 | -3.1979 | -2.683 | -1.6954 | -3.1759 | 61.8668 | 0.22574 | 61.7705 | -0.023943 | 0.048236 | 61.4151 | 0.012299 | 61.2024 | 58.2939 | 58.0443 | 57.67 | 58.0921 | 58.6069 | 59.5946 | 58.1141 | 123.1567 | 61.5157 | 123.0605 | 61.266 | 61.3382 | 122.7051 | 61.3023 | 122.4924 | 61.8185 | 61.8545 | 61.7223 | 61.7582
6743.0781 | 123.3261 | -61.2946 | 61.8347 | -3.0052 | -3.264 | -3.652 | -3.2117 | -2.6602 | -1.6679 | -3.153 | 61.8622 | 0.23032 | 61.7934 | -0.028522 | 0.048236 | 61.4151 | 0.021456 | 61.1978 | 58.2894 | 58.0305 | 57.6426 | 58.0829 | 58.6344 | 59.6266 | 58.1416 | 123.1567 | 61.5249 | 123.088 | 61.266 | 61.3428 | 122.7096 | 61.316 | 122.4924 | 61.8139 | 61.8407 | 61.7452 | 61.772
6744.0625 | 123.4131 | -61.29 | 61.7844 | -2.9228 | -3.1587 | -3.5329 | -3.1109 | -2.6052 | -1.5993 | -3.0706 | 61.853 | 0.22116 | 61.7614 | -0.028522 | 0.043657 | 61.4197 | 0.012299 | 61.2024 | 58.3672 | 58.1313 | 57.757 | 58.1791 | 58.6848 | 59.6907 | 58.2194 | 123.143 | 61.5111 | 123.0513 | 61.2615 | 61.3336 | 122.7096 | 61.3023 | 122.4924 | 61.8094 | 61.8407 | 61.7177 | 61.7491
6745.1094 | 123.2895 | -61.3174 | 61.7935 | -2.8449 | -3.1037 | -3.478 | -3.0651 | -2.5274 | -1.494 | -2.9653 | 61.8576 | 0.23032 | 61.7797 | -0.023943 | 0.052814 | 61.4242 | 0.007721 | 61.2024 | 58.4725 | 58.2137 | 57.8394 | 58.2523 | 58.7901 | 59.8235 | 58.3522 | 123.175 | 61.5478 | 123.0971 | 61.2935 | 61.3703 | 122.7417 | 61.3252 | 122.5199 | 61.8048 | 61.8499 | 61.7269 | 61.772
6746.0625 | 123.3261 | -61.3083 | 61.821 | -2.964 | -3.2136 | -3.6062 | -3.2071 | -2.6602 | -1.6405 | -3.0889 | 61.853 | 0.2349 | 61.7568 | -0.033101 | 0.048236 | 61.4197 | 0.016878 | 61.1841 | 58.3443 | 58.0946 | 57.7021 | 58.1012 | 58.6481 | 59.6678 | 58.2194 | 123.1613 | 61.5432 | 123.0651 | 61.2752 | 61.3565 | 122.728 | 61.3252 | 122.4924 | 61.8048 | 61.8361 | 61.7085 | 61.7399
6747.0938 | 123.3307 | -61.29 | 61.7706 | -2.9411 | -3.1953 | -3.5742 | -3.1613 | -2.6327 | -1.5901 | -3.0614 | 61.8576 | 0.23032 | 61.7659 | -0.028522 | 0.052814 | 61.4242 | 0.012299 | 61.1978 | 58.3489 | 58.0947 | 57.7158 | 58.1287 | 58.6573 | 59.6999 | 58.2286 | 123.1476 | 61.5203 | 123.0559 | 61.2615 | 61.3428 | 122.7142 | 61.3023 | 122.4878 | 61.8048 | 61.8453 | 61.7131 | 61.7536
6748.0625 | 123.3215 | -61.3541 | 61.7249 | -2.909 | -3.1633 | -3.5558 | -3.1384 | -2.6052 | -1.5581 | -3.0248 | 61.8576 | 0.2349 | 61.7751 | -0.028522 | 0.043657 | 61.4197 | 0.012299 | 61.207 | 58.445 | 58.1908 | 57.7982 | 58.2157 | 58.7488 | 59.796 | 58.3293 | 123.2117 | 61.589 | 123.1292 | 61.3255 | 61.3977 | 122.7737 | 61.3664 | 122.5611 | 61.8139 | 61.8453 | 61.7314 | 61.7628
6749.0938 | 123.2941 | -61.3083 | 61.7844 | -3.0327 | -3.2869 | -3.6566 | -3.2757 | -2.7471 | -1.7183 | -3.1759 | 61.8576 | 0.23032 | 61.7568 | -0.028522 | 0.048236 | 61.4197 | 0.012299 | 61.1978 | 58.2756 | 58.0214 | 57.6517 | 58.0325 | 58.5612 | 59.59 | 58.1324 | 123.1659 | 61.5386 | 123.0651 | 61.2798 | 61.3565 | 122.728 | 61.3206 | 122.5061 | 61.8094 | 61.8453 | 61.7085 | 61.7445
6750.0625 | 123.2483 | -61.2991 | 61.8484 | -3.138 | -3.4105 | -3.771 | -3.3627 | -2.8341 | -1.8373 | -3.2858 | 61.8713 | 0.2349 | 61.8071 | -0.023943 | 0.052814 | 61.4105 | 0.012299 | 61.2024 | 58.1612 | 57.8886 | 57.5281 | 57.9364 | 58.465 | 59.4618 | 58.0134 | 123.1705 | 61.534 | 123.1063 | 61.2752 | 61.3519 | 122.7096 | 61.3114 | 122.5016 | 61.8185 | 61.859 | 61.7543 | 61.7948
6751.0625 | 123.3536 | -61.2854 | 61.8118 | -3.2616 | -3.525 | -3.8809 | -3.4818 | -2.944 | -1.9381 | -3.4094 | 61.8576 | 0.22574 | 61.7843 | -0.033101 | 0.048236 | 61.3968 | 0.007721 | 61.1887 | 58.0238 | 57.7604 | 57.4045 | 57.8036 | 58.3414 | 59.3473 | 57.876 | 123.143 | 61.5111 | 123.0697 | 61.2523 | 61.3336 | 122.6822 | 61.2931 | 122.4741 | 61.8094 | 61.8499 | 61.736 | 61.7765
6752.0625 | 123.3215 | -61.2671 | 61.8073 | -3.3303 | -3.5983 | -3.9633 | -3.5459 | -3.0081 | -1.9884 | -3.4918 | 61.8759 | 0.22574 | 61.7888 | -0.033101 | 0.048236 | 61.3968 | 0.016878 | 61.1887 | 57.9368 | 57.6688 | 57.3038 | 57.7212 | 58.259 | 59.2787 | 57.7753 | 123.143 | 61.4928 | 123.0559 | 61.234 | 61.3153 | 122.6639 | 61.284 | 122.4558 | 61.8277 | 61.859 | 61.7406 | 61.772
6753.0781 | 123.2483 | -61.2625 | 61.821 | -3.1837 | -3.4517 | -3.8214 | -3.3994 | -2.857 | -1.8236 | -3.3178 | 61.8805 | 0.23948 | 61.8117 | -0.033101 | 0.052814 | 61.4059 | 0.007721 | 61.1933 | 58.0788 | 57.8108 | 57.4411 | 57.8631 | 58.4055 | 59.4389 | 57.9447 | 123.143 | 61.502 | 123.0742 | 61.2294 | 61.3153 | 122.6684 | 61.2702 | 122.4558 | 61.8277 | 61.8728 | 61.7589 | 61.804
6754.0625 | 123.2941 | -61.3083 | 61.8393 | -3.0784 | -3.351 | -3.7207 | -3.317 | -2.77 | -1.7412 | -3.2171 | 61.8622 | 0.22574 | 61.7614 | -0.019364 | 0.039079 | 61.4059 | 0.007721 | 61.2024 | 58.2298 | 57.9573 | 57.5876 | 57.9913 | 58.5383 | 59.5671 | 58.0912 | 123.1705 | 61.534 | 123.0697 | 61.2889 | 61.3474 | 122.7142 | 61.316 | 122.5107 | 61.8231 | 61.8545 | 61.7223 | 61.7536
6755.0938 | 123.2346 | -61.3174 | 61.8393 | -3.0189 | -3.264 | -3.6199 | -3.2666 | -2.7471 | -1.7137 | -3.1576 | 61.8668 | 0.2349 | 61.798 | -0.019364 | 0.048236 | 61.4105 | 0.016878 | 61.207 | 58.2985 | 58.0534 | 57.6975 | 58.0509 | 58.5703 | 59.6037 | 58.1599 | 123.1842 | 61.5523 | 123.1154 | 61.2981 | 61.3657 | 122.7279 | 61.3343 | 122.5244 | 61.8185 | 61.8499 | 61.7498 | 61.7811
6756.0625 | 123.3994 | -61.2991 | 61.7935 | -3.0464 | -3.2777 | -3.6703 | -3.3215 | -2.77 | -1.7091 | -3.1484 | 61.8668 | 0.22116 | 61.7614 | -0.03768 | 0.039079 | 61.4105 | 0.012299 | 61.1887 | 58.2527 | 58.0214 | 57.6288 | 57.9776 | 58.5291 | 59.59 | 58.1507 | 123.1659 | 61.5203 | 123.0605 | 61.2615 | 61.3382 | 122.7096 | 61.3114 | 122.4878 | 61.8277 | 61.8545 | 61.7223 | 61.7491
6757.0938 | 123.349 | -61.3037 | 61.8027 | -3.225 | -3.5067 | -3.8718 | -3.4635 | -2.9119 | -1.8877 | -3.3865 | 61.8713 | 0.22574 | 61.7797 | -0.03768 | 0.052814 | 61.4014 | 0.007721 | 61.1841 | 58.0788 | 57.797 | 57.4319 | 57.8402 | 58.3918 | 59.416 | 57.9172 | 123.175 | 61.5294 | 123.0834 | 61.266 | 61.3565 | 122.7051 | 61.3114 | 122.4878 | 61.8185 | 61.8636 | 61.7269 | 61.772
6758.0625 | 123.3765 | -61.2762 | 61.7935 | -3.1196 | -3.3739 | -3.7665 | -3.4085 | -2.8433 | -1.7641 | -3.2033 | 61.8622 | 0.2349 | 61.798 | -0.028522 | 0.048236 | 61.4059 | 0.003143 | 61.1887 | 58.1566 | 57.9023 | 57.5098 | 57.8677 | 58.433 | 59.5122 | 58.0729 | 123.1384 | 61.5111 | 123.0742 | 61.2477 | 61.3245 | 122.6822 | 61.2794 | 122.4649 | 61.8139 | 61.859 | 61.7498 | 61.7948
6759.0938 | 123.2666 | -61.2808 | 61.8118 | -3.0372 | -3.2777 | -3.6886 | -3.3124 | -2.7517 | -1.6725 | -3.1026 | 61.853 | 0.22574 | 61.7568 | -0.033101 | 0.048236 | 61.4151 | 0.003143 | 61.1933 | 58.2436 | 58.0031 | 57.5922 | 57.9684 | 58.5291 | 59.6083 | 58.1782 | 123.1338 | 61.5066 | 123.0376 | 61.2477 | 61.3291 | 122.6959 | 61.284 | 122.4741 | 61.8048 | 61.8499 | 61.7085 | 61.7536
6760.0625 | 123.2849 | -61.29 | 61.853 | -3.0189 | -3.264 | -3.6703 | -3.3032 | -2.7426 | -1.6588 | -3.0797 | 61.8622 | 0.23032 | 61.7934 | -0.023943 | 0.048236 | 61.4151 | 0.012299 | 61.207 | 58.2711 | 58.026 | 57.6197 | 57.9868 | 58.5474 | 59.6312 | 58.2102 | 123.1522 | 61.5203 | 123.0834 | 61.266 | 61.3382 | 122.7051 | 61.3023 | 122.497 | 61.8139 | 61.8499 | 61.7452 | 61.7811
6761.0938 | 123.262 | -61.3266 | 61.8256 | -3.1151 | -3.3556 | -3.7436 | -3.4039 | -2.8662 | -1.8099 | -3.24 | 61.8713 | 0.2349 | 61.7797 | -0.028522 | 0.048236 | 61.4059 | 0.012299 | 61.1887 | 58.2115 | 57.971 | 57.583 | 57.9227 | 58.4604 | 59.5167 | 58.0866 | 123.1979 | 61.5615 | 123.1063 | 61.2981 | 61.3748 | 122.7325 | 61.3389 | 122.5153 | 61.8231 | 61.859 | 61.7314 | 61.7674
6762.0625 | 123.3353 | -61.2946 | 61.8118 | -3.1013 | -3.3464 | -3.7252 | -3.3856 | -2.8478 | -1.7916 | -3.2033 | 61.8713 | 0.22574 | 61.7705 | -0.033101 | 0.052814 | 61.4059 | 0.012299 | 61.2024 | 58.1932 | 57.9481 | 57.5693 | 57.9089 | 58.4467 | 59.503 | 58.0912 | 123.1659 | 61.5203 | 123.0651 | 61.2615 | 61.3474 | 122.7005 | 61.3069 | 122.497 | 61.8185 | 61.859 | 61.7177 | 61.7582
6763.0625 | 123.4268 | -61.2213 | 61.8393 | -3.1059 | -3.351 | -3.7436 | -3.3948 | -2.8616 | -1.7824 | -3.1805 | 61.8668 | 0.2349 | 61.7934 | -0.028522 | 0.052814 | 61.4059 | 0.012299 | 61.1978 | 58.1154 | 57.8703 | 57.4778 | 57.8265 | 58.3597 | 59.4389 | 58.0409 | 123.0881 | 61.4562 | 123.0147 | 61.1928 | 61.2741 | 122.6272 | 61.2336 | 122.4192 | 61.8139 | 61.8545 | 61.7406 | 61.7811
6764.0938 | 123.3032 | -61.3312 | 61.8027 | -3.0052 | -3.2594 | -3.6154 | -3.2757 | -2.7609 | -1.6908 | -3.1209 | 61.853 | 0.22574 | 61.7659 | -0.028522 | 0.048236 | 61.4105 | 0.007721 | 61.2024 | 58.326 | 58.0717 | 57.7158 | 58.0554 | 58.5703 | 59.6403 | 58.2102 | 123.1842 | 61.5569 | 123.0971 | 61.3027 | 61.3794 | 122.7417 | 61.3389 | 122.5336 | 61.8048 | 61.8453 | 61.7177 | 61.7582
6765.0625 | 123.2712 | -61.3037 | 61.7981 | -3.0693 | -3.3281 | -3.7115 | -3.3444 | -2.7975 | -1.7275 | -3.1209 | 61.8622 | 0.2349 | 61.798 | -0.023943 | 0.048236 | 61.4059 | 0.012299 | 61.207 | 58.2344 | 57.9756 | 57.5922 | 57.9593 | 58.5062 | 59.5763 | 58.1828 | 123.1659 | 61.5386 | 123.1017 | 61.2798 | 61.3519 | 122.7096 | 61.316 | 122.5107 | 61.8139 | 61.8499 | 61.7498 | 61.7857
6766.0938 | 123.2437 | -61.3129 | 61.8027 | -2.9136 | -3.1724 | -3.5558 | -3.2117 | -2.6556 | -1.5993 | -2.9744 | 61.8576 | 0.23032 | 61.7705 | -0.023943 | 0.052814 | 61.4197 | 0.012299 | 61.2162 | 58.3992 | 58.1404 | 57.757 | 58.1012 | 58.6573 | 59.7136 | 58.3384 | 123.1705 | 61.5432 | 123.0834 | 61.2889 | 61.3657 | 122.7325 | 61.3252 | 122.529 | 61.8048 | 61.8453 | 61.7177 | 61.7582
6767.0625 | 123.3856 | -61.2808 | 61.8027 | -3.051 | -3.3327 | -3.7161 | -3.3307 | -2.7609 | -1.6817 | -3.0843 | 61.8576 | 0.22116 | 61.7659 | -0.028522 | 0.048236 | 61.4105 | 0.007721 | 61.2116 | 58.2299 | 57.9481 | 57.5647 | 57.9501 | 58.52 | 59.5991 | 58.1965 | 123.1384 | 61.502 | 123.0468 | 61.2523 | 61.3291 | 122.6913 | 61.2885 | 122.4924 | 61.8094 | 61.8499 | 61.7177 | 61.7582
6768.0938 | 123.3307 | -61.2579 | 61.821 | -3.1334 | -3.4334 | -3.8031 | -3.4177 | -2.8707 | -1.7732 | -3.185 | 61.8713 | 0.23948 | 61.8026 | -0.028522 | 0.052814 | 61.4059 | 0.003143 | 61.1933 | 58.1246 | 57.8245 | 57.4549 | 57.8403 | 58.3872 | 59.4847 | 58.0729 | 123.1293 | 61.4974 | 123.0605 | 61.2294 | 61.3107 | 122.6639 | 61.2611 | 122.4512 | 61.8185 | 61.8682 | 61.7498 | 61.7994
6769.0625 | 123.262 | -61.322 | 61.8118 | -3.0281 | -3.3098 | -3.6886 | -3.3078 | -2.7517 | -1.6817 | -3.0843 | 61.8576 | 0.23032 | 61.7614 | -0.028522 | 0.043657 | 61.4151 | 0.012299 | 61.1978 | 58.2939 | 58.0122 | 57.6334 | 58.0142 | 58.5703 | 59.6403 | 58.2377 | 123.1796 | 61.5523 | 123.0834 | 61.2935 | 61.3657 | 122.7371 | 61.3343 | 122.5199 | 61.8139 | 61.8453 | 61.7177 | 61.7491
6770.0938 | 123.262 | -61.2808 | 61.8439 | -3.1517 | -3.4517 | -3.8214 | -3.4406 | -2.8753 | -1.7961 | -3.2171 | 61.8713 | 0.24405 | 61.8071 | -0.023943 | 0.048236 | 61.3968 | 0.007721 | 61.1933 | 58.1291 | 57.8291 | 57.4594 | 57.8402 | 58.4055 | 59.4847 | 58.0637 | 123.1522 | 61.5249 | 123.088 | 61.2569 | 61.3291 | 122.6776 | 61.2885 | 122.4741 | 61.8231 | 61.8636 | 61.7589 | 61.7994
6771.0625 | 123.3307 | -61.29 | 61.7981 | -3.1059 | -3.3922 | -3.7573 | -3.3811 | -2.825 | -1.7824 | -3.1713 | 61.8713 | 0.23032 | 61.7659 | -0.023943 | 0.043657 | 61.4151 | 0.003143 | 61.1887 | 58.1841 | 57.8978 | 57.5327 | 57.9089 | 58.465 | 59.5076 | 58.1187 | 123.1613 | 61.5203 | 123.0559 | 61.266 | 61.3336 | 122.7051 | 61.2931 | 122.4787 | 61.8277 | 61.8682 | 61.7223 | 61.7628
6772.0938 | 123.4177 | -61.3083 | 61.7432 | -3.0922 | -3.351 | -3.7115 | -3.3902 | -2.8616 | -1.8099 | -3.153 | 61.8668 | 0.23032 | 61.7659 | -0.033101 | 0.052814 | 61.4059 | 0.012299 | 61.1887 | 58.2161 | 57.9573 | 57.5968 | 57.9181 | 58.4467 | 59.4984 | 58.1553 | 123.175 | 61.5386 | 123.0742 | 61.2752 | 61.3611 | 122.7142 | 61.3206 | 122.497 | 61.8139 | 61.8545 | 61.7131 | 61.7536
6773.0625 | 123.3536 | -61.2854 | 61.8347 | -3.2158 | -3.4792 | -3.8718 | -3.5047 | -2.9577 | -1.8877 | -3.2491 | 61.8851 | 0.22574 | 61.8117 | -0.028522 | 0.043657 | 61.4014 | -0.001436 | 61.1887 | 58.0696 | 57.8062 | 57.4136 | 57.7807 | 58.3277 | 59.3977 | 58.0363 | 123.1705 | 61.5111 | 123.0971 | 61.2569 | 61.3291 | 122.6868 | 61.284 | 122.4741 | 61.8414 | 61.8865 | 61.7681 | 61.8132
6774.0938 | 123.2986 | -61.2991 | 61.8347 | -3.2433 | -3.5021 | -3.8901 | -3.5138 | -2.9715 | -1.8923 | -3.2858 | 61.8668 | 0.22574 | 61.7751 | -0.033101 | 0.043657 | 61.3968 | 0.007721 | 61.1841 | 58.0559 | 57.797 | 57.4091 | 57.7853 | 58.3277 | 59.4069 | 58.0134 | 123.1659 | 61.5249 | 123.0742 | 61.266 | 61.3428 | 122.6959 | 61.3069 | 122.4832 | 61.8231 | 61.859 | 61.7314 | 61.7674
6775.0625 | 123.4406 | -61.2259 | 61.8805 | -3.0876 | -3.3785 | -3.7481 | -3.3811 | -2.8387 | -1.7458 | -3.1301 | 61.8713 | 0.23948 | 61.8026 | -0.028522 | 0.052814 | 61.4151 | 0.007721 | 61.1887 | 58.1383 | 57.8474 | 57.4778 | 57.8448 | 58.3872 | 59.4801 | 58.0958 | 123.0972 | 61.4654 | 123.0285 | 61.1974 | 61.2787 | 122.641 | 61.2336 | 122.4146 | 61.8185 | 61.8636 | 61.7498 | 61.7948
6776.0938 | 123.2666 | -61.3037 | 61.8301 | -3.2112 | -3.5067 | -3.8763 | -3.4864 | -2.9394 | -1.8923 | -3.272 | 61.8713 | 0.2349 | 61.7751 | -0.019364 | 0.048236 | 61.4014 | 0.012299 | 61.1933 | 58.0925 | 57.797 | 57.4274 | 57.8174 | 58.3643 | 59.4114 | 58.0317 | 123.175 | 61.5386 | 123.0788 | 61.2843 | 61.3519 | 122.7051 | 61.316 | 122.497 | 61.8231 | 61.859 | 61.7269 | 61.7628
6777.0625 | 123.317 | -61.29 | 61.8073 | -3.1746 | -3.4517 | -3.7802 | -3.4223 | -2.8936 | -1.8694 | -3.2354 | 61.8622 | 0.2349 | 61.7705 | -0.033101 | 0.043657 | 61.3968 | 0.012299 | 61.1933 | 58.1154 | 57.8382 | 57.5098 | 57.8677 | 58.3963 | 59.4206 | 58.0546 | 123.1522 | 61.5249 | 123.0605 | 61.2569 | 61.3336 | 122.6867 | 61.3023 | 122.4832 | 61.8185 | 61.8499 | 61.7269 | 61.7582
6778.0938 | 123.2437 | -61.3266 | 61.8256 | -3.1059 | -3.3922 | -3.7436 | -3.3673 | -2.8204 | -1.7687 | -3.1255 | 61.8759 | 0.2349 | 61.7934 | -0.023943 | 0.039079 | 61.4105 | 0.003143 | 61.1887 | 58.2207 | 57.9344 | 57.583 | 57.9593 | 58.5062 | 59.5579 | 58.2011 | 123.2025 | 61.5615 | 123.12 | 61.3027 | 61.3657 | 122.7371 | 61.3297 | 122.5153 | 61.8368 | 61.8728 | 61.7543 | 61.7903
6779.0625 | 123.3078 | -61.3358 | 61.7706 | -2.8633 | -3.1266 | -3.5238 | -3.1659 | -2.6144 | -1.5123 | -2.8508 | 61.8484 | 0.22574 | 61.7568 | -0.028522 | 0.048236 | 61.4242 | 0.012299 | 61.2024 | 58.4725 | 58.2091 | 57.812 | 58.1699 | 58.7214 | 59.8235 | 58.4849 | 123.1842 | 61.5615 | 123.0925 | 61.3072 | 61.384 | 122.76 | 61.3481 | 122.5382 | 61.8002 | 61.8361 | 61.7085 | 61.7445
6780.1094 | 123.3078 | -61.2946 | 61.8164 | -2.877 | -3.1312 | -3.5101 | -3.1567 | -2.6144 | -1.5214 | -2.8508 | 61.8576 | 0.23948 | 61.7751 | -0.028522 | 0.052814 | 61.4197 | 0.012299 | 61.207 | 58.4176 | 58.1633 | 57.7845 | 58.1378 | 58.6802 | 59.7731 | 58.4437 | 123.1522 | 61.534 | 123.0697 | 61.266 | 61.3474 | 122.7142 | 61.3069 | 122.5016 | 61.8048 | 61.8453 | 61.7223 | 61.7628
6781.0625 | 123.2895 | -61.3541 | 61.7752 | -2.7671 | -3.0305 | -3.391 | -3.0651 | -2.5274 | -1.4436 | -2.7776 | 61.8393 | 0.23032 | 61.7476 | -0.028522 | 0.043657 | 61.4197 | 0.012299 | 61.2116 | 58.587 | 58.3236 | 57.9631 | 58.2889 | 58.8267 | 59.9105 | 58.5765 | 123.1933 | 61.5844 | 123.1017 | 61.3255 | 61.3977 | 122.7737 | 61.3664 | 122.5656 | 61.7956 | 61.827 | 61.704 | 61.7353
6782.0938 | 123.2895 | -61.3403 | 61.7935 | -2.8083 | -3.0809 | -3.4505 | -3.1109 | -2.5777 | -1.4665 | -2.8005 | 61.8439 | 0.22574 | 61.7568 | -0.033101 | 0.043657 | 61.4288 | 0.012299 | 61.2116 | 58.532 | 58.2595 | 57.8898 | 58.2294 | 58.7626 | 59.8738 | 58.5399 | 123.1842 | 61.5661 | 123.0971 | 61.3072 | 61.384 | 122.7691 | 61.3526 | 122.5519 | 61.8002 | 61.8316 | 61.7131 | 61.7445
6783.0625 | 123.3948 | -61.3083 | 61.7661 | -2.8587 | -3.1312 | -3.4963 | -3.1704 | -2.6373 | -1.5443 | -2.86 | 61.853 | 0.23032 | 61.7888 | -0.033101 | 0.043657 | 61.4151 | 0.007721 | 61.2024 | 58.4496 | 58.1771 | 57.812 | 58.1378 | 58.671 | 59.764 | 58.4483 | 123.1613 | 61.5386 | 123.0971 | 61.2752 | 61.3519 | 122.7234 | 61.316 | 122.5107 | 61.8094 | 61.8453 | 61.7452 | 61.7811
6784.0938 | 123.2986 | -61.3403 | 61.7844 | -2.7671 | -3.0305 | -3.3956 | -3.0743 | -2.5457 | -1.4528 | -2.7501 | 61.853 | 0.22574 | 61.743 | -0.028522 | 0.043657 | 61.4288 | 0.007721 | 61.2116 | 58.5732 | 58.3098 | 57.9447 | 58.266 | 58.7946 | 59.8876 | 58.5902 | 123.1933 | 61.5661 | 123.0834 | 61.3118 | 61.384 | 122.7691 | 61.3481 | 122.5519 | 61.8094 | 61.8453 | 61.6994 | 61.7353
6785.0625 | 123.3627 | -61.3083 | 61.8027 | -2.7625 | -3.0259 | -3.4047 | -3.0606 | -2.5228 | -1.4253 | -2.7455 | 61.8484 | 0.23948 | 61.7659 | -0.023943 | 0.043657 | 61.4288 | 0.007721 | 61.2116 | 58.5458 | 58.2824 | 57.9035 | 58.2477 | 58.7855 | 59.883 | 58.5628 | 123.1567 | 61.5478 | 123.0742 | 61.2843 | 61.3519 | 122.7371 | 61.316 | 122.5199 | 61.8048 | 61.8407 | 61.7223 | 61.7582
6786.0625 | 123.3673 | -61.3312 | 61.7477 | -2.7946 | -3.0717 | -3.4368 | -3.0835 | -2.5411 | -1.4528 | -2.7822 | 61.8484 | 0.23032 | 61.7614 | -0.028522 | 0.052814 | 61.4288 | 0.007721 | 61.207 | 58.5366 | 58.2595 | 57.8944 | 58.2477 | 58.7901 | 59.8784 | 58.549 | 123.1796 | 61.5615 | 123.0925 | 61.3027 | 61.384 | 122.76 | 61.3389 | 122.5382 | 61.7956 | 61.8407 | 61.7085 | 61.7536
6787.0938 | 123.2849 | -61.322 | 61.7935 | -2.7625 | -3.0168 | -3.3773 | -3.0377 | -2.5137 | -1.4436 | -2.7638 | 61.8439 | 0.22116 | 61.7476 | -0.033101 | 0.048236 | 61.4288 | 0.007721 | 61.207 | 58.5595 | 58.3053 | 57.9447 | 58.2844 | 58.8084 | 59.8784 | 58.5582 | 123.1659 | 61.5432 | 123.0696 | 61.2889 | 61.3703 | 122.7508 | 61.3297 | 122.529 | 61.7956 | 61.8361 | 61.6994 | 61.7399
6788.0625 | 123.2712 | -61.3312 | 61.8164 | -2.9136 | -3.2136 | -3.5604 | -3.2117 | -2.6739 | -1.5626 | -2.9012 | 61.8576 | 0.23948 | 61.7888 | -0.023943 | 0.039079 | 61.4197 | 0.012299 | 61.1933 | 58.4176 | 58.1175 | 57.7708 | 58.1195 | 58.6573 | 59.7685 | 58.43 | 123.1888 | 61.5707 | 123.12 | 61.3072 | 61.3703 | 122.7508 | 61.3435 | 122.5244 | 61.8185 | 61.8453 | 61.7498 | 61.7765
6789.0781 | 123.2529 | -61.3037 | 61.8439 | -2.9869 | -3.2732 | -3.6245 | -3.2757 | -2.7517 | -1.6405 | -2.9836 | 61.8576 | 0.23032 | 61.7568 | -0.023943 | 0.052814 | 61.4197 | 0.007721 | 61.2024 | 58.3168 | 58.0305 | 57.6792 | 58.028 | 58.552 | 59.6632 | 58.3201 | 123.1613 | 61.534 | 123.0605 | 61.2798 | 61.3565 | 122.7234 | 61.3114 | 122.5061 | 61.8048 | 61.8499 | 61.704 | 61.7491
6790.0625 | 123.4177 | -61.2717 | 61.7523 | -2.8816 | -3.1816 | -3.5192 | -3.1567 | -2.6373 | -1.5077 | -2.8691 | 61.853 | 0.2349 | 61.7751 | -0.028522 | 0.052814 | 61.4242 | 0.007721 | 61.207 | 58.3901 | 58.0901 | 57.7525 | 58.115 | 58.6344 | 59.764 | 58.4025 | 123.1247 | 61.5066 | 123.0468 | 61.2431 | 61.3245 | 122.6959 | 61.2794 | 122.4787 | 61.8002 | 61.8453 | 61.7223 | 61.7674
6791.0938 | 123.2666 | -61.3037 | 61.8439 | -3.0372 | -3.3373 | -3.6749 | -3.3215 | -2.7975 | -1.6908 | -3.0202 | 61.853 | 0.23032 | 61.7659 | -0.023943 | 0.048236 | 61.4151 | 0.016878 | 61.2024 | 58.2665 | 57.9664 | 57.6288 | 57.9822 | 58.5062 | 59.6129 | 58.2835 | 123.1567 | 61.534 | 123.0697 | 61.2798 | 61.3519 | 122.7188 | 61.3206 | 122.5061 | 61.8048 | 61.8361 | 61.7177 | 61.7491
6792.0625 | 123.381 | -61.2762 | 61.7889 | -3.0739 | -3.3647 | -3.7069 | -3.3719 | -2.8616 | -1.732 | -3.0523 | 61.8622 | 0.2349 | 61.7888 | -0.028522 | 0.052814 | 61.4242 | 0.012299 | 61.1978 | 58.2024 | 57.9115 | 57.5693 | 57.9043 | 58.4147 | 59.5442 | 58.224 | 123.1384 | 61.5111 | 123.0651 | 61.2477 | 61.3291 | 122.7005 | 61.2885 | 122.4741 | 61.8094 | 61.8499 | 61.736 | 61.7765
6793.0938 | 123.2803 | -61.2762 | 61.7981 | -2.9502 | -3.2365 | -3.5604 | -3.2574 | -2.77 | -1.6496 | -2.9378 | 61.853 | 0.22574 | 61.7659 | -0.028522 | 0.048236 | 61.4197 | 0.012299 | 61.2024 | 58.326 | 58.0397 | 57.7158 | 58.0188 | 58.5062 | 59.6266 | 58.3384 | 123.1293 | 61.502 | 123.0422 | 61.2477 | 61.3245 | 122.6959 | 61.2885 | 122.4787 | 61.8048 | 61.8407 | 61.7177 | 61.7536
6794.0625 | 123.3536 | -61.3037 | 61.7935 | -2.9915 | -3.264 | -3.5925 | -3.2941 | -2.7929 | -1.6908 | -2.9882 | 61.8576 | 0.23032 | 61.7751 | -0.023943 | 0.052814 | 61.4151 | 0.012299 | 61.1933 | 58.3123 | 58.0397 | 57.7112 | 58.0096 | 58.5108 | 59.6129 | 58.3155 | 123.1613 | 61.534 | 123.0788 | 61.2798 | 61.3565 | 122.7188 | 61.316 | 122.497 | 61.8048 | 61.8453 | 61.7223 | 61.7628
6795.1094 | 123.23 | -61.2854 | 61.8439 | -3.0739 | -3.3418 | -3.6749 | -3.3948 | -2.9119 | -1.8053 | -3.0706 | 61.853 | 0.2349 | 61.7751 | -0.023943 | 0.048236 | 61.4197 | 0.003143 | 61.2024 | 58.2115 | 57.9436 | 57.6105 | 57.8906 | 58.3735 | 59.4801 | 58.2148 | 123.1384 | 61.5203 | 123.0605 | 61.2615 | 61.3336 | 122.7051 | 61.2885 | 122.4878 | 61.8048 | 61.8499 | 61.7269 | 61.772
6796.0625 | 123.1979 | -61.3403 | 61.7706 | -3.1334 | -3.4151 | -3.771 | -3.4314 | -2.9577 | -1.819 | -3.098 | 61.8668 | 0.23032 | 61.7797 | -0.023943 | 0.048236 | 61.4059 | 0.007721 | 61.1841 | 58.2069 | 57.9252 | 57.5693 | 57.9089 | 58.3826 | 59.5213 | 58.2423 | 123.2071 | 61.5706 | 123.12 | 61.3164 | 61.3886 | 122.7463 | 61.3481 | 122.5244 | 61.8185 | 61.859 | 61.7314 | 61.772
6797.0938 | 123.3124 | -61.2808 | 61.8713 | -3.3486 | -3.6532 | -3.9954 | -3.6603 | -3.1546 | -2.0205 | -3.3086 | 61.8805 | 0.23032 | 61.7934 | -0.028522 | 0.052814 | 61.3922 | 0.007721 | 61.1841 | 57.9323 | 57.6276 | 57.2854 | 57.6205 | 58.1263 | 59.2603 | 57.9722 | 123.1613 | 61.5111 | 123.0742 | 61.2523 | 61.3336 | 122.673 | 61.2885 | 122.4649 | 61.8277 | 61.8728 | 61.7406 | 61.7857
6798.0625 | 123.2758 | -61.2991 | 61.821 | -3.4218 | -3.7402 | -4.0595 | -3.729 | -3.2095 | -2.0846 | -3.4185 | 61.8896 | 0.23032 | 61.7843 | -0.033101 | 0.048236 | 61.3876 | 0.007721 | 61.1704 | 57.8773 | 57.5589 | 57.2396 | 57.5701 | 58.0896 | 59.2146 | 57.8806 | 123.1888 | 61.5295 | 123.0834 | 61.266 | 61.3474 | 122.6867 | 61.3069 | 122.4695 | 61.8414 | 61.8819 | 61.736 | 61.7765
6799.0781 | 123.2574 | -61.2534 | 61.8439 | -3.344 | -3.6395 | -3.9725 | -3.6603 | -3.1408 | -2.0388 | -3.3132 | 61.8713 | 0.22574 | 61.8071 | -0.023943 | 0.048236 | 61.3922 | 0.007721 | 61.1795 | 57.9094 | 57.6139 | 57.2809 | 57.593 | 58.1125 | 59.2146 | 57.9401 | 123.1247 | 61.4791 | 123.0605 | 61.2294 | 61.3016 | 122.6456 | 61.2611 | 122.4329 | 61.8231 | 61.8636 | 61.7589 | 61.7994
6800.0625 | 123.3765 | -61.29 | 61.821 | -3.3257 | -3.6028 | -3.9404 | -3.6146 | -3.1225 | -2.0067 | -3.2812 | 61.8805 | 0.22574 | 61.7843 | -0.033101 | 0.043657 | 61.3968 | 0.016878 | 61.175 | 57.9643 | 57.6871 | 57.3495 | 57.6754 | 58.1675 | 59.2832 | 58.0088 | 123.1705 | 61.5157 | 123.0742 | 61.2569 | 61.3336 | 122.6867 | 61.3069 | 122.4649 | 61.8368 | 61.8636 | 61.7406 | 61.7674
6801.0938 | 123.2712 | -61.3129 | 61.8393 | -3.1746 | -3.4655 | -3.7893 | -3.4864 | -2.9852 | -1.874 | -3.1301 | 61.8713 | 0.2349 | 61.7797 | -0.028522 | 0.048236 | 61.4059 | 0.007721 | 61.1795 | 58.1383 | 57.8474 | 57.5235 | 57.8265 | 58.3277 | 59.4389 | 58.1828 | 123.1842 | 61.5478 | 123.0925 | 61.2843 | 61.3611 | 122.7188 | 61.3206 | 122.4924 | 61.8231 | 61.8636 | 61.7314 | 61.772
6802.0625 | 123.3398 | -61.3083 | 61.7935 | -2.9777 | -3.2686 | -3.5879 | -3.2895 | -2.8021 | -1.6863 | -2.9378 | 61.8576 | 0.22116 | 61.7659 | -0.019364 | 0.048236 | 61.4242 | 0.007721 | 61.2024 | 58.3306 | 58.0397 | 57.7204 | 58.0188 | 58.5062 | 59.622 | 58.3705 | 123.1659 | 61.5295 | 123.0742 | 61.2889 | 61.3565 | 122.7325 | 61.316 | 122.5107 | 61.8094 | 61.8499 | 61.7177 | 61.7582
6803.0781 | 123.4177 | -61.2579 | 61.8484 | -2.964 | -3.2457 | -3.5513 | -3.2529 | -2.7883 | -1.6954 | -2.947 | 61.8576 | 0.23032 | 61.7705 | -0.023943 | 0.052814 | 61.4105 | 0.007721 | 61.207 | 58.294 | 58.0122 | 57.7067 | 58.0051 | 58.4696 | 59.5625 | 58.311 | 123.1155 | 61.4883 | 123.0285 | 61.234 | 61.3107 | 122.6684 | 61.2657 | 122.4649 | 61.8048 | 61.8499 | 61.7177 | 61.7628
6804.0625 | 123.262 | -61.3266 | 61.8073 | -3.1609 | -3.438 | -3.7665 | -3.4635 | -2.9898 | -1.8602 | -3.0935 | 61.8668 | 0.23032 | 61.7797 | -0.028522 | 0.048236 | 61.4105 | 0.012299 | 61.1887 | 58.1657 | 57.8886 | 57.5601 | 57.8631 | 58.3368 | 59.4664 | 58.2331 | 123.1934 | 61.5569 | 123.1063 | 61.2981 | 61.3748 | 122.7371 | 61.3389 | 122.5153 | 61.8185 | 61.8545 | 61.7314 | 61.7674
6805.1094 | 123.2849 | -61.2717 | 61.9125 | -3.3257 | -3.6166 | -3.9542 | -3.6329 | -3.1317 | -1.993 | -3.2583 | 61.8713 | 0.22574 | 61.7843 | -0.028522 | 0.048236 | 61.3968 | 0.003143 | 61.1841 | 57.946 | 57.6551 | 57.3175 | 57.6388 | 58.14 | 59.2787 | 58.0134 | 123.143 | 61.4974 | 123.0559 | 61.2431 | 61.3199 | 122.6684 | 61.2748 | 122.4558 | 61.8231 | 61.8682 | 61.736 | 61.7811
6806.0625 | 123.2117 | -61.3174 | 61.8164 | -3.2112 | -3.5067 | -3.8306 | -3.4909 | -2.9943 | -1.9106 | -3.1896 | 61.8713 | 0.23032 | 61.8071 | -0.028522 | 0.052814 | 61.3968 | 0.012299 | 61.175 | 58.1062 | 57.8108 | 57.4869 | 57.8265 | 58.3231 | 59.4068 | 58.1278 | 123.1888 | 61.5478 | 123.1246 | 61.2889 | 61.3703 | 122.7142 | 61.3297 | 122.4924 | 61.8185 | 61.859 | 61.7543 | 61.7948
6807.0938 | 123.2941 | -61.2762 | 61.8576 | -3.257 | -3.5387 | -3.8534 | -3.5459 | -3.0584 | -1.9884 | -3.2354 | 61.8713 | 0.23032 | 61.7797 | -0.028522 | 0.048236 | 61.4014 | 0.016878 | 61.1841 | 58.0192 | 57.7375 | 57.4228 | 57.7304 | 58.2178 | 59.2878 | 58.0409 | 123.1476 | 61.5066 | 123.0559 | 61.2477 | 61.3245 | 122.6776 | 61.2931 | 122.4604 | 61.8231 | 61.8545 | 61.7314 | 61.7628
6808.0625 | 123.2346 | -61.2946 | 61.8484 | -3.2707 | -3.5662 | -3.8855 | -3.5596 | -3.0767 | -2.0205 | -3.2629 | 61.8759 | 0.22574 | 61.7934 | -0.028522 | 0.043657 | 61.4014 | 0.016878 | 61.1795 | 58.0238 | 57.7283 | 57.4091 | 57.7349 | 58.2178 | 59.2741 | 58.0317 | 123.1705 | 61.5203 | 123.088 | 61.266 | 61.3382 | 122.6959 | 61.3114 | 122.4741 | 61.8323 | 61.859 | 61.7498 | 61.7765
6809.0781 | 123.4268 | -61.2534 | 61.821 | -3.289 | -3.5845 | -3.9038 | -3.5779 | -3.0767 | -2.0067 | -3.2354 | 61.8713 | 0.23032 | 61.7888 | -0.023943 | 0.052814 | 61.4014 | 0.007721 | 61.175 | 57.9643 | 57.6688 | 57.3495 | 57.6754 | 58.1766 | 59.2466 | 58.018 | 123.1247 | 61.4837 | 123.0422 | 61.2294 | 61.3062 | 122.6547 | 61.2611 | 122.4283 | 61.8185 | 61.8636 | 61.736 | 61.7811
6810.0625 | 123.381 | -61.2808 | 61.7844 | -3.289 | -3.5799 | -3.8947 | -3.5734 | -3.0859 | -2.0159 | -3.24 | 61.8713 | 0.23032 | 61.7797 | -0.033101 | 0.043657 | 61.3968 | 0.007721 | 61.1841 | 57.9918 | 57.7009 | 57.3862 | 57.7075 | 58.1949 | 59.2649 | 58.0409 | 123.1522 | 61.5111 | 123.0605 | 61.2477 | 61.3245 | 122.6776 | 61.2885 | 122.4649 | 61.8277 | 61.8636 | 61.736 | 61.772
6811.0938 | 123.381 | -61.2808 | 61.7935 | -3.3119 | -3.5983 | -3.9359 | -3.6237 | -3.1225 | -2.0342 | -3.2445 | 61.8805 | 0.23032 | 61.8117 | -0.023943 | 0.043657 | 61.3968 | 0.012299 | 61.1841 | 57.9689 | 57.6826 | 57.345 | 57.6571 | 58.1583 | 59.2466 | 58.0363 | 123.1613 | 61.5111 | 123.0925 | 61.2569 | 61.3245 | 122.6776 | 61.2931 | 122.4649 | 61.8368 | 61.8682 | 61.7681 | 61.7994
6812.0625 | 123.349 | -61.29 | 61.7386 | -3.2753 | -3.5342 | -3.8397 | -3.5825 | -3.1408 | -2.0754 | -3.2766 | 61.8713 | 0.23032 | 61.7797 | -0.028522 | 0.048236 | 61.4014 | 0.012299 | 61.1841 | 58.0147 | 57.7558 | 57.4503 | 57.7075 | 58.1491 | 59.2146 | 58.0134 | 123.1613 | 61.5203 | 123.0697 | 61.2615 | 61.3382 | 122.6913 | 61.3023 | 122.4741 | 61.8231 | 61.859 | 61.7314 | 61.7674
6813.0938 | 123.2986 | -61.2717 | 61.8256 | -3.225 | -3.5021 | -3.8397 | -3.5459 | -3.063 | -1.9564 | -3.1438 | 61.8805 | 0.23032 | 61.798 | -0.033101 | 0.048236 | 61.4014 | 0.007721 | 61.2024 | 58.0467 | 57.7696 | 57.432 | 57.7258 | 58.2087 | 59.3153 | 58.1278 | 123.1522 | 61.502 | 123.0697 | 61.2386 | 61.3199 | 122.673 | 61.2794 | 122.4741 | 61.8323 | 61.8728 | 61.7498 | 61.7903
6814.0625 | 123.2941 | -61.3083 | 61.8347 | -2.9823 | -3.2548 | -3.5558 | -3.3032 | -2.8387 | -1.7458 | -2.9561 | 61.8668 | 0.2349 | 61.7843 | -0.023943 | 0.048236 | 61.4105 | 0.012299 | 61.2162 | 58.326 | 58.0534 | 57.7525 | 58.0051 | 58.4696 | 59.5625 | 58.3522 | 123.175 | 61.5432 | 123.0925 | 61.2843 | 61.3565 | 122.7188 | 61.3206 | 122.5245 | 61.8185 | 61.8545 | 61.736 | 61.772
6815.0938 | 123.3765 | -61.2808 | 61.7889 | -3.3211 | -3.6166 | -3.9496 | -3.642 | -3.1546 | -2.0296 | -3.2445 | 61.8805 | 0.22574 | 61.7843 | -0.019364 | 0.043657 | 61.3922 | 0.007721 | 61.1933 | 57.9597 | 57.6642 | 57.3312 | 57.6388 | 58.1263 | 59.2512 | 58.0363 | 123.1613 | 61.5066 | 123.0651 | 61.2615 | 61.3245 | 122.673 | 61.2885 | 122.4741 | 61.8368 | 61.8728 | 61.7406 | 61.7765
6816.0625 | 123.2437 | -61.3174 | 61.8256 | -3.1563 | -3.438 | -3.771 | -3.4818 | -3.0035 | -1.8785 | -3.0431 | 61.8668 | 0.2349 | 61.8071 | -0.042259 | 0.048236 | 61.4014 | 0.007721 | 61.2024 | 58.1612 | 57.8794 | 57.5464 | 57.8357 | 58.3139 | 59.4389 | 58.2743 | 123.1842 | 61.5523 | 123.1246 | 61.2752 | 61.3657 | 122.7188 | 61.3252 | 122.5199 | 61.8185 | 61.859 | 61.7589 | 61.7994
6817.0938 | 123.4039 | -61.2488 | 61.7844 | -3.2433 | -3.5479 | -3.858 | -3.5367 | -3.0584 | -1.9381 | -3.1621 | 61.8668 | 0.22574 | 61.7705 | -0.033101 | 0.048236 | 61.4014 | 0.012299 | 61.1841 | 58.0055 | 57.7009 | 57.3908 | 57.7121 | 58.1903 | 59.3107 | 58.0866 | 123.1155 | 61.4745 | 123.0193 | 61.2157 | 61.297 | 122.6501 | 61.2611 | 122.4329 | 61.8185 | 61.8545 | 61.7223 | 61.7582
6818.0625 | 123.3215 | -61.2671 | 61.8347 | -3.225 | -3.5113 | -3.8397 | -3.5505 | -3.0676 | -1.9289 | -3.1255 | 61.8759 | 0.2349 | 61.8117 | -0.033101 | 0.052814 | 61.4059 | 0.007721 | 61.1887 | 58.0421 | 57.7558 | 57.4274 | 57.7166 | 58.1995 | 59.3382 | 58.1416 | 123.143 | 61.502 | 123.0788 | 61.234 | 61.3199 | 122.673 | 61.2748 | 122.4558 | 61.8231 | 61.8682 | 61.7589 | 61.804
6819.1094 | 123.349 | -61.2808 | 61.8027 | -3.1517 | -3.4334 | -3.7665 | -3.4726 | -3.0172 | -1.8694 | -3.0477 | 61.8622 | 0.22116 | 61.7659 | -0.033101 | 0.048236 | 61.4059 | 0.007721 | 61.1933 | 58.1291 | 57.8474 | 57.5144 | 57.8082 | 58.2636 | 59.4114 | 58.2331 | 123.143 | 61.502 | 123.0468 | 61.2477 | 61.3291 | 122.6868 | 61.2885 | 122.4741 | 61.8139 | 61.8545 | 61.7177 | 61.7582
6820.0625 | 123.2574 | -61.2854 | 61.8027 | -3.1334 | -3.4151 | -3.7573 | -3.4589 | -2.9852 | -1.8419 | -2.9882 | 61.8713 | 0.2349 | 61.8026 | -0.019364 | 0.048236 | 61.4059 | 0.016878 | 61.1978 | 58.152 | 57.8703 | 57.5281 | 57.8265 | 58.3002 | 59.4435 | 58.2972 | 123.1567 | 61.5203 | 123.088 | 61.266 | 61.3336 | 122.6913 | 61.3023 | 122.4832 | 61.8231 | 61.8545 | 61.7543 | 61.7857
6821.0781 | 123.3536 | -61.2396 | 61.7981 | -3.1975 | -3.4929 | -3.826 | -3.5413 | -3.0767 | -1.8877 | -3.0523 | 61.8668 | 0.23032 | 61.7751 | -0.023943 | 0.052814 | 61.4059 | 0.012299 | 61.1978 | 58.0421 | 57.7467 | 57.4136 | 57.6983 | 58.1629 | 59.3519 | 58.1874 | 123.1064 | 61.4699 | 123.0147 | 61.2157 | 61.2924 | 122.6456 | 61.2519 | 122.4375 | 61.8139 | 61.8545 | 61.7223 | 61.7628
6822.0625 | 123.262 | -61.3129 | 61.8256 | -3.2112 | -3.5021 | -3.8306 | -3.5459 | -3.0813 | -1.8969 | -3.0706 | 61.8805 | 0.23032 | 61.798 | -0.028522 | 0.048236 | 61.4014 | 0.007721 | 61.1978 | 58.1017 | 57.8108 | 57.4823 | 57.767 | 58.2315 | 59.416 | 58.2423 | 123.1934 | 61.5432 | 123.1109 | 61.2843 | 61.3611 | 122.7142 | 61.3206 | 122.5107 | 61.8323 | 61.8728 | 61.7498 | 61.7903
6823.0781 | 123.4039 | -61.2305 | 61.8164 | -3.2982 | -3.6074 | -3.9313 | -3.6146 | -3.1591 | -1.9838 | -3.185 | 61.8759 | 0.22574 | 61.7843 | -0.028522 | 0.057392 | 61.4014 | 0.012299 | 61.1887 | 57.9323 | 57.623 | 57.2992 | 57.6159 | 58.0713 | 59.2466 | 58.0454 | 123.1064 | 61.4562 | 123.0147 | 61.2019 | 61.2879 | 122.6318 | 61.2428 | 122.4192 | 61.8185 | 61.8636 | 61.7269 | 61.772
6824.0625 | 123.3765 | -61.2991 | 61.7615 | -3.1792 | -3.4929 | -3.7939 | -3.4864 | -3.0081 | -1.8511 | -3.0523 | 61.8759 | 0.23032 | 61.798 | -0.028522 | 0.043657 | 61.3968 | 0.012299 | 61.1795 | 58.12 | 57.8062 | 57.5052 | 57.8128 | 58.2911 | 59.4481 | 58.2469 | 123.175 | 61.5295 | 123.0971 | 61.2706 | 61.3428 | 122.6959 | 61.3114 | 122.4787 | 61.8323 | 61.8636 | 61.7543 | 61.7857
6825.0938 | 123.4222 | -61.2946 | 61.7844 | -3.3119 | -3.6166 | -3.9175 | -3.6191 | -3.15 | -1.993 | -3.1896 | 61.8668 | 0.23032 | 61.7797 | -0.023943 | 0.048236 | 61.3922 | 0.007721 | 61.1841 | 57.9826 | 57.678 | 57.377 | 57.6754 | 58.1446 | 59.3016 | 58.1049 | 123.1613 | 61.5249 | 123.0742 | 61.2706 | 61.3428 | 122.6868 | 61.3023 | 122.4787 | 61.8185 | 61.859 | 61.7314 | 61.772
6826.0625 | 123.3582 | -61.2991 | 61.8027 | -3.2936 | -3.6166 | -3.8947 | -3.5917 | -3.1317 | -1.9838 | -3.1667 | 61.8851 | 0.23032 | 61.798 | -0.023943 | 0.048236 | 61.3968 | 0.012299 | 61.1841 | 58.0055 | 57.6826 | 57.4045 | 57.7075 | 58.1674 | 59.3153 | 58.1324 | 123.1842 | 61.5295 | 123.0971 | 61.2752 | 61.3474 | 122.6959 | 61.3114 | 122.4832 | 61.8368 | 61.8728 | 61.7498 | 61.7857
6827.0938 | 123.3444 | -61.2579 | 61.8439 | -3.3348 | -3.6395 | -3.945 | -3.6283 | -3.1775 | -2.0159 | -3.1896 | 61.8668 | 0.2349 | 61.7797 | -0.023943 | 0.052814 | 61.3968 | 0.012299 | 61.1841 | 57.9231 | 57.6185 | 57.3129 | 57.6296 | 58.0805 | 59.242 | 58.0683 | 123.1247 | 61.4928 | 123.0376 | 61.234 | 61.3107 | 122.6547 | 61.2702 | 122.442 | 61.8139 | 61.8545 | 61.7269 | 61.7674
6828.0625 | 123.2986 | -61.2717 | 61.8439 | -3.5225 | -3.8226 | -4.1236 | -3.8435 | -3.3789 | -2.2036 | -3.3636 | 61.8896 | 0.2349 | 61.8026 | -0.033101 | 0.048236 | 61.3876 | 0.016878 | 61.175 | 57.7491 | 57.449 | 57.1481 | 57.4282 | 57.8928 | 59.0681 | 57.9081 | 123.1613 | 61.5066 | 123.0742 | 61.2386 | 61.3199 | 122.6593 | 61.2885 | 122.4466 | 61.8414 | 61.8728 | 61.7543 | 61.7857
6829.0938 | 123.381 | -61.2488 | 61.7844 | -3.4859 | -3.7952 | -4.0915 | -3.8023 | -3.3652 | -2.199 | -3.3361 | 61.8851 | 0.23032 | 61.798 | -0.023943 | 0.052814 | 61.3876 | 0.007721 | 61.175 | 57.7629 | 57.4536 | 57.1572 | 57.4465 | 57.8836 | 59.0497 | 57.9127 | 123.1338 | 61.4791 | 123.0468 | 61.2248 | 61.3016 | 122.6364 | 61.2565 | 122.4237 | 61.8323 | 61.8773 | 61.7452 | 61.7903
6830.0625 | 123.3673 | -61.2625 | 61.8073 | -3.5317 | -3.8318 | -4.1144 | -3.8664 | -3.4247 | -2.2814 | -3.4002 | 61.8942 | 0.23032 | 61.798 | -0.028522 | 0.048236 | 61.383 | 0.007721 | 61.1612 | 57.7308 | 57.4307 | 57.1481 | 57.3961 | 57.8378 | 58.9811 | 57.8623 | 123.1567 | 61.4928 | 123.0605 | 61.234 | 61.3107 | 122.6455 | 61.2702 | 122.4237 | 61.846 | 61.8865 | 61.7498 | 61.7903
6831.0781 | 123.3673 | -61.2488 | 61.8484 | -3.6462 | -3.9554 | -4.2564 | -3.9625 | -3.5208 | -2.3272 | -3.4826 | 61.8988 | 0.2349 | 61.8117 | -0.023943 | 0.048236 | 61.3785 | 0.012299 | 61.1658 | 57.6026 | 57.2934 | 56.9924 | 57.2863 | 57.728 | 58.9216 | 57.7662 | 123.1476 | 61.4837 | 123.0605 | 61.2248 | 61.297 | 122.6272 | 61.2611 | 122.4146 | 61.8506 | 61.8865 | 61.7635 | 61.7994
6832.0625 | 123.317 | -61.2671 | 61.8027 | -3.5317 | -3.8409 | -4.1511 | -3.8664 | -3.4155 | -2.2448 | -3.359 | 61.8896 | 0.22574 | 61.7888 | -0.033101 | 0.048236 | 61.3876 | 0.007721 | 61.1795 | 57.7354 | 57.4262 | 57.116 | 57.4007 | 57.8516 | 59.0223 | 57.9081 | 123.1567 | 61.4928 | 123.0559 | 61.234 | 61.3153 | 122.6547 | 61.2748 | 122.4466 | 61.8414 | 61.8819 | 61.7406 | 61.7811
6833.0938 | 123.2986 | -61.2808 | 61.8118 | -3.463 | -3.7631 | -4.0686 | -3.7885 | -3.3468 | -2.1761 | -3.2903 | 61.8896 | 0.2349 | 61.8255 | -0.028522 | 0.048236 | 61.3876 | 0.016878 | 61.1704 | 57.8178 | 57.5177 | 57.2122 | 57.4923 | 57.934 | 59.1047 | 57.9905 | 123.1705 | 61.5157 | 123.1063 | 61.2523 | 61.3291 | 122.6684 | 61.2977 | 122.4512 | 61.8414 | 61.8728 | 61.7772 | 61.8086
6834.0625 | 123.2941 | -61.235 | 61.8713 | -3.5363 | -3.8364 | -4.1282 | -3.8389 | -3.4247 | -2.2769 | -3.4094 | 61.8896 | 0.2349 | 61.7934 | -0.023943 | 0.048236 | 61.3876 | 0.012299 | 61.1795 | 57.6988 | 57.3987 | 57.1069 | 57.3961 | 57.8104 | 58.9582 | 57.8257 | 123.1247 | 61.4699 | 123.0285 | 61.2111 | 61.2833 | 122.6227 | 61.2473 | 122.4146 | 61.8414 | 61.8773 | 61.7452 | 61.7811
6835.1094 | 123.3627 | -61.2213 | 61.8256 | -3.6965 | -4.0241 | -4.2976 | -4.022 | -3.5803 | -2.4188 | -3.5788 | 61.9034 | 0.2349 | 61.8209 | -0.028522 | 0.043657 | 61.3785 | 0.012299 | 61.1612 | 57.5248 | 57.1972 | 56.9237 | 57.1993 | 57.641 | 58.8025 | 57.6426 | 123.1247 | 61.4562 | 123.0422 | 61.1928 | 61.265 | 122.5998 | 61.2336 | 122.3825 | 61.8597 | 61.8911 | 61.7772 | 61.8086
6836.0625 | 123.2529 | -61.29 | 61.8347 | -3.5134 | -3.8226 | -4.1144 | -3.8297 | -3.3972 | -2.2448 | -3.3727 | 61.8942 | 0.21658 | 61.798 | -0.028522 | 0.043657 | 61.383 | 0.012299 | 61.1841 | 57.7766 | 57.4674 | 57.1756 | 57.4602 | 57.8928 | 59.0452 | 57.9172 | 123.1842 | 61.5066 | 123.088 | 61.2615 | 61.3336 | 122.673 | 61.3023 | 122.4741 | 61.8506 | 61.8819 | 61.7543 | 61.7857
6837.0938 | 123.2483 | -61.2762 | 61.9125 | -3.4584 | -3.7814 | -4.0457 | -3.7656 | -3.3331 | -2.2036 | -3.3361 | 61.8896 | 0.2349 | 61.8163 | -0.033101 | 0.052814 | 61.383 | 0.016878 | 61.1978 | 57.8178 | 57.4948 | 57.2305 | 57.5106 | 57.9431 | 59.0726 | 57.9401 | 123.1659 | 61.5111 | 123.0925 | 61.2431 | 61.3291 | 122.6593 | 61.2931 | 122.4741 | 61.8368 | 61.8728 | 61.7635 | 61.7994
6838.0625 | 123.3032 | -61.2442 | 61.8576 | -3.3852 | -3.7036 | -3.9633 | -3.6924 | -3.2782 | -2.1578 | -3.272 | 61.8759 | 0.22574 | 61.7934 | -0.03768 | 0.048236 | 61.3968 | 0.016878 | 61.1933 | 57.859 | 57.5406 | 57.2809 | 57.5518 | 57.966 | 59.0864 | 57.9722 | 123.1201 | 61.4699 | 123.0376 | 61.2065 | 61.2924 | 122.641 | 61.2611 | 122.4375 | 61.8277 | 61.859 | 61.7452 | 61.7765
6839.0938 | 123.3536 | -61.2625 | 61.853 | -3.3394 | -3.6532 | -3.9267 | -3.6649 | -3.2461 | -2.0983 | -3.1988 | 61.8805 | 0.23948 | 61.8026 | -0.019364 | 0.043657 | 61.3968 | 0.012299 | 61.1887 | 57.9231 | 57.6093 | 57.3358 | 57.5976 | 58.0164 | 59.1642 | 58.0637 | 123.143 | 61.502 | 123.0651 | 61.2431 | 61.3062 | 122.6593 | 61.2748 | 122.4512 | 61.8368 | 61.8682 | 61.7589 | 61.7903
6840.0625 | 123.3307 | -61.2671 | 61.7889 | -3.2707 | -3.5845 | -3.8489 | -3.5917 | -3.1775 | -2.0708 | -3.1621 | 61.8759 | 0.22574 | 61.7888 | -0.033101 | 0.048236 | 61.4059 | 0.007721 | 61.1933 | 57.9964 | 57.6826 | 57.4182 | 57.6754 | 58.0896 | 59.1963 | 58.1049 | 123.143 | 61.4928 | 123.0559 | 61.234 | 61.3153 | 122.673 | 61.2748 | 122.4604 | 61.8277 | 61.8682 | 61.7406 | 61.7811
6841.0781 | 123.4268 | -61.2579 | 61.821 | -3.2478 | -3.5525 | -3.8122 | -3.5505 | -3.1454 | -2.0342 | -3.1347 | 61.8759 | 0.23032 | 61.7843 | -0.028522 | 0.052814 | 61.4014 | 0.016878 | 61.1978 | 58.0101 | 57.7055 | 57.4457 | 57.7075 | 58.1125 | 59.2237 | 58.1233 | 123.1338 | 61.4883 | 123.0422 | 61.2294 | 61.3107 | 122.6593 | 61.2748 | 122.4558 | 61.8231 | 61.859 | 61.7314 | 61.7674
6842.0625 | 123.3444 | -61.3129 | 61.7615 | -3.138 | -3.4609 | -3.7252 | -3.4635 | -3.031 | -1.8785 | -2.979 | 61.8622 | 0.22116 | 61.7751 | -0.033101 | 0.048236 | 61.4014 | 0.012299 | 61.1933 | 58.1749 | 57.852 | 57.5876 | 57.8494 | 58.2819 | 59.4343 | 58.3339 | 123.175 | 61.534 | 123.088 | 61.2798 | 61.3611 | 122.7142 | 61.3252 | 122.5061 | 61.8139 | 61.8499 | 61.7269 | 61.7628
6843.0938 | 123.2574 | -61.322 | 61.8439 | -2.7946 | -3.1129 | -3.3864 | -3.1018 | -2.6556 | -1.4802 | -2.6082 | 61.8484 | 0.2349 | 61.7522 | -0.028522 | 0.052814 | 61.4242 | 0.007721 | 61.2207 | 58.5274 | 58.2091 | 57.9356 | 58.2203 | 58.6664 | 59.8418 | 58.7138 | 123.1705 | 61.5569 | 123.0742 | 61.2935 | 61.3748 | 122.7463 | 61.3297 | 122.5428 | 61.7956 | 61.8407 | 61.6994 | 61.7445
6844.0625 | 123.2666 | -61.322 | 61.7844 | -2.9228 | -3.2594 | -3.5284 | -3.2208 | -2.7654 | -1.581 | -2.7226 | 61.853 | 0.23032 | 61.7659 | -0.028522 | 0.052814 | 61.4242 | 0.012299 | 61.2116 | 58.3992 | 58.0626 | 57.7937 | 58.1012 | 58.5566 | 59.7411 | 58.5994 | 123.175 | 61.5523 | 123.088 | 61.2935 | 61.3748 | 122.7463 | 61.3343 | 122.5336 | 61.8002 | 61.8407 | 61.7131 | 61.7536
6845.0938 | 123.4039 | -61.2808 | 61.7935 | -2.9548 | -3.2915 | -3.5696 | -3.262 | -2.8021 | -1.6176 | -2.7455 | 61.8576 | 0.23032 | 61.7614 | -0.019364 | 0.052814 | 61.4242 | 0.016878 | 61.2116 | 58.326 | 57.9893 | 57.7112 | 58.0188 | 58.4788 | 59.6632 | 58.5353 | 123.1384 | 61.5111 | 123.0422 | 61.2615 | 61.3336 | 122.7051 | 61.2977 | 122.4924 | 61.8048 | 61.8407 | 61.7085 | 61.7445
6846.0625 | 123.2758 | -61.3129 | 61.821 | -3.3074 | -3.6303 | -3.8992 | -3.6191 | -3.1637 | -2.0342 | -3.1209 | 61.8759 | 0.2349 | 61.8117 | -0.023943 | 0.048236 | 61.3968 | 0.003143 | 61.1933 | 58.0055 | 57.6826 | 57.4136 | 57.6937 | 58.1491 | 59.2787 | 58.1919 | 123.1888 | 61.5478 | 123.1246 | 61.2889 | 61.3611 | 122.7096 | 61.316 | 122.5061 | 61.8277 | 61.8728 | 61.7635 | 61.8086
6847.0938 | 123.3215 | -61.2671 | 61.8439 | -3.4035 | -3.7173 | -3.9816 | -3.697 | -3.2782 | -2.1807 | -3.2445 | 61.8805 | 0.2349 | 61.7843 | -0.028522 | 0.048236 | 61.3876 | 0.016878 | 61.1841 | 57.8636 | 57.5498 | 57.2854 | 57.5701 | 57.9889 | 59.0864 | 58.0225 | 123.1476 | 61.502 | 123.0513 | 61.2386 | 61.3153 | 122.6547 | 61.284 | 122.4512 | 61.8323 | 61.8636 | 61.736 | 61.7674
6848.0625 | 123.1842 | -61.3312 | 61.7752 | -3.3394 | -3.6669 | -3.8992 | -3.6191 | -3.2049 | -2.1487 | -3.1988 | 61.8805 | 0.2349 | 61.798 | -0.033101 | 0.052814 | 61.3876 | 0.012299 | 61.1841 | 57.9918 | 57.6642 | 57.4319 | 57.712 | 58.1262 | 59.1825 | 58.1324 | 123.2117 | 61.5661 | 123.1292 | 61.2981 | 61.384 | 122.7188 | 61.3435 | 122.5153 | 61.8277 | 61.8682 | 61.7452 | 61.7857
6849.0781 | 123.436 | -61.2717 | 61.8256 | -3.3394 | -3.6486 | -3.8992 | -3.642 | -3.2232 | -2.1304 | -3.1759 | 61.8851 | 0.23032 | 61.798 | -0.023943 | 0.048236 | 61.3876 | 0.016878 | 61.1933 | 57.9323 | 57.623 | 57.3724 | 57.6296 | 58.0484 | 59.1413 | 58.0958 | 123.1567 | 61.502 | 123.0697 | 61.2477 | 61.3199 | 122.6593 | 61.2885 | 122.4649 | 61.8368 | 61.8682 | 61.7498 | 61.7811
6850.0625 | 123.3444 | -61.2854 | 61.7935 | -3.3898 | -3.7265 | -3.9908 | -3.6878 | -3.2553 | -2.1487 | -3.1988 | 61.8759 | 0.22574 | 61.7843 | -0.033101 | 0.043657 | 61.3922 | 0.016878 | 61.1841 | 57.8956 | 57.5589 | 57.2946 | 57.5976 | 58.0301 | 59.1367 | 58.0866 | 123.1613 | 61.5111 | 123.0697 | 61.2523 | 61.3291 | 122.6776 | 61.3023 | 122.4695 | 61.8323 | 61.859 | 61.7406 | 61.7674
6851.0781 | 123.3307 | -61.2854 | 61.853 | -3.3989 | -3.7173 | -3.9633 | -3.6924 | -3.2782 | -2.1945 | -3.2445 | 61.8851 | 0.23948 | 61.8026 | -0.028522 | 0.052814 | 61.3922 | 0.016878 | 61.175 | 57.8865 | 57.5681 | 57.3221 | 57.593 | 58.0072 | 59.0909 | 58.0409 | 123.1705 | 61.5249 | 123.088 | 61.2569 | 61.3382 | 122.6776 | 61.3023 | 122.4604 | 61.8323 | 61.8682 | 61.7498 | 61.7857
6852.0625 | 123.3398 | -61.2717 | 61.8164 | -3.3623 | -3.6853 | -3.9221 | -3.6329 | -3.2232 | -2.1349 | -3.1942 | 61.8805 | 0.22116 | 61.7888 | -0.028522 | 0.048236 | 61.3922 | 0.003143 | 61.175 | 57.9094 | 57.5864 | 57.3495 | 57.6388 | 58.0484 | 59.1367 | 58.0775 | 123.1522 | 61.4928 | 123.0605 | 61.2431 | 61.3199 | 122.6639 | 61.2748 | 122.4466 | 61.8323 | 61.8773 | 61.7406 | 61.7857
6853.0938 | 123.1888 | -61.29 | 61.8851 | -3.1975 | -3.5113 | -3.7573 | -3.4818 | -3.0813 | -2.0067 | -3.0202 | 61.8668 | 0.2349 | 61.7797 | -0.023943 | 0.052814 | 61.4014 | 0.007721 | 61.1933 | 58.0925 | 57.7787 | 57.5327 | 57.8082 | 58.2087 | 59.2832 | 58.2698 | 123.1567 | 61.5249 | 123.0697 | 61.266 | 61.3428 | 122.6913 | 61.2977 | 122.4832 | 61.8139 | 61.859 | 61.7269 | 61.772
6854.0625 | 123.2529 | -61.3083 | 61.8256 | -3.2204 | -3.5113 | -3.7619 | -3.5138 | -3.1042 | -2.0434 | -3.0568 | 61.8805 | 0.23948 | 61.8117 | -0.023943 | 0.043657 | 61.4014 | 0.012299 | 61.1841 | 58.0879 | 57.797 | 57.5464 | 57.7945 | 58.2041 | 59.2649 | 58.2514 | 123.1888 | 61.5478 | 123.12 | 61.2843 | 61.3519 | 122.7096 | 61.3206 | 122.4924 | 61.8368 | 61.8682 | 61.7681 | 61.7994
6855.0625 | 123.3398 | -61.2717 | 61.8027 | -3.3211 | -3.6395 | -3.8626 | -3.6008 | -3.2141 | -2.1716 | -3.2079 | 61.8759 | 0.23032 | 61.7797 | -0.028522 | 0.052814 | 61.3922 | 0.012299 | 61.1795 | 57.9506 | 57.6322 | 57.4091 | 57.6708 | 58.0576 | 59.1001 | 58.0637 | 123.1476 | 61.502 | 123.0513 | 61.2431 | 61.3245 | 122.6639 | 61.284 | 122.4512 | 61.8231 | 61.8636 | 61.7269 | 61.7674
6856.0938 | 123.2574 | -61.2808 | 61.8484 | -3.2982 | -3.612 | -3.826 | -3.555 | -3.182 | -2.1532 | -3.1896 | 61.8713 | 0.23032 | 61.7843 | -0.028522 | 0.052814 | 61.4014 | 0.012299 | 61.175 | 57.9826 | 57.6688 | 57.4548 | 57.7258 | 58.0988 | 59.1276 | 58.0912 | 123.1522 | 61.5111 | 123.0651 | 61.2523 | 61.3336 | 122.6822 | 61.2931 | 122.4558 | 61.8185 | 61.859 | 61.7314 | 61.772
6857.0625 | 123.2803 | -61.3037 | 61.8164 | -3.3303 | -3.6486 | -3.8718 | -3.6054 | -3.2049 | -2.1807 | -3.2217 | 61.8759 | 0.2349 | 61.8163 | -0.023943 | 0.048236 | 61.3968 | 0.012299 | 61.175 | 57.9735 | 57.6551 | 57.4319 | 57.6983 | 58.0988 | 59.123 | 58.0821 | 123.1796 | 61.5386 | 123.12 | 61.2798 | 61.3519 | 122.7005 | 61.316 | 122.4787 | 61.8277 | 61.8636 | 61.7681 | 61.804
6858.0938 | 123.2758 | -61.2717 | 61.8393 | -3.225 | -3.5387 | -3.7527 | -3.5093 | -3.1271 | -2.1075 | -3.1164 | 61.8759 | 0.23032 | 61.7843 | -0.028522 | 0.048236 | 61.3968 | 0.016878 | 61.1933 | 58.0467 | 57.7329 | 57.5189 | 57.7624 | 58.1446 | 59.1642 | 58.1553 | 123.1476 | 61.502 | 123.0559 | 61.2431 | 61.3199 | 122.6684 | 61.2885 | 122.4649 | 61.8277 | 61.859 | 61.736 | 61.7674
6859.0625 | 123.2758 | -61.2808 | 61.8393 | -3.2021 | -3.5113 | -3.7344 | -3.468 | -3.0859 | -2.1029 | -3.0889 | 61.8759 | 0.23032 | 61.7751 | -0.033101 | 0.043657 | 61.3922 | 0.012299 | 61.1841 | 58.0788 | 57.7696 | 57.5464 | 57.8128 | 58.1949 | 59.1779 | 58.1919 | 123.1567 | 61.5111 | 123.0559 | 61.2477 | 61.3245 | 122.673 | 61.2931 | 122.4649 | 61.8323 | 61.8636 | 61.7314 | 61.7628
6860.0938 | 123.3582 | -61.2488 | 61.8759 | -3.3257 | -3.6441 | -3.8809 | -3.5871 | -3.1866 | -2.1807 | -3.1942 | 61.8851 | 0.2349 | 61.798 | -0.023943 | 0.043657 | 61.3922 | 0.007721 | 61.1841 | 57.9231 | 57.6047 | 57.3679 | 57.6617 | 58.0622 | 59.0681 | 58.0546 | 123.1338 | 61.4837 | 123.0468 | 61.2248 | 61.2924 | 122.641 | 61.2565 | 122.4329 | 61.8414 | 61.8773 | 61.7543 | 61.7903
6861.0625 | 123.2391 | -61.2991 | 61.8439 | -3.1242 | -3.4334 | -3.6383 | -3.3902 | -2.9989 | -2.0251 | -3.0156 | 61.8713 | 0.23032 | 61.8026 | -0.023943 | 0.043657 | 61.4059 | 0.003143 | 61.1795 | 58.1749 | 57.8657 | 57.6609 | 57.9089 | 58.3002 | 59.2741 | 58.2835 | 123.1705 | 61.5295 | 123.1017 | 61.2752 | 61.3428 | 122.7051 | 61.3023 | 122.4787 | 61.8277 | 61.8682 | 61.7589 | 61.7994
6862.0938 | 123.2941 | -61.2534 | 61.8484 | -3.2845 | -3.6074 | -3.8351 | -3.555 | -3.1408 | -2.1487 | -3.153 | 61.8805 | 0.2349 | 61.7797 | -0.028522 | 0.048236 | 61.4014 | 0.012299 | 61.1841 | 57.9689 | 57.6459 | 57.4182 | 57.6983 | 58.1125 | 59.1047 | 58.1004 | 123.1338 | 61.4883 | 123.033 | 61.2248 | 61.3016 | 122.6547 | 61.2657 | 122.4375 | 61.8323 | 61.8682 | 61.7314 | 61.7674
6863.0625 | 123.3124 | -61.29 | 61.8393 | -3.2341 | -3.5616 | -3.7665 | -3.4909 | -3.0767 | -2.1075 | -3.1072 | 61.8759 | 0.22574 | 61.7751 | -0.028522 | 0.057392 | 61.4059 | 0.003143 | 61.1887 | 58.0559 | 57.7283 | 57.5235 | 57.799 | 58.2132 | 59.1825 | 58.1828 | 123.1659 | 61.5157 | 123.0651 | 61.2615 | 61.3474 | 122.6959 | 61.2931 | 122.4787 | 61.8185 | 61.8728 | 61.7177 | 61.772
6864.0781 | 123.4039 | -61.2488 | 61.8256 | -3.1105 | -3.4472 | -3.6428 | -3.3627 | -2.944 | -1.9838 | -3.0111 | 61.8622 | 0.22116 | 61.7659 | -0.033101 | 0.048236 | 61.4105 | 0.012299 | 61.1887 | 58.1383 | 57.8016 | 57.6059 | 57.886 | 58.3048 | 59.2649 | 58.2377 | 123.111 | 61.4699 | 123.0147 | 61.2157 | 61.297 | 122.6593 | 61.2611 | 122.4375 | 61.8139 | 61.8499 | 61.7177 | 61.7536
6865.0625 | 123.3215 | -61.2762 | 61.8164 | -3.1609 | -3.5021 | -3.6932 | -3.4039 | -2.9898 | -2.0205 | -3.0294 | 61.8713 | 0.23032 | 61.798 | -0.023943 | 0.048236 | 61.4014 | 0.012299 | 61.1841 | 58.1154 | 57.7741 | 57.583 | 57.8723 | 58.2865 | 59.2558 | 58.2469 | 123.1476 | 61.5066 | 123.0742 | 61.2523 | 61.3245 | 122.6776 | 61.2885 | 122.4604 | 61.8231 | 61.859 | 61.7498 | 61.7857
6866.0938 | 123.2391 | -61.2946 | 61.8073 | -3.1425 | -3.4701 | -3.6932 | -3.4131 | -3.0081 | -2.0067 | -3.0065 | 61.8713 | 0.22574 | 61.7659 | -0.033101 | 0.052814 | 61.4105 | 0.007721 | 61.1887 | 58.152 | 57.8245 | 57.6014 | 57.8815 | 58.2865 | 59.2878 | 58.2881 | 123.1659 | 61.5203 | 123.0605 | 61.2615 | 61.3474 | 122.7051 | 61.3023 | 122.4832 | 61.8185 | 61.8636 | 61.7131 | 61.7582
6867.0625 | 123.2712 | -61.3174 | 61.8484 | -3.0784 | -3.3968 | -3.6016 | -3.3215 | -2.9257 | -1.9518 | -2.9515 | 61.8713 | 0.22574 | 61.7888 | -0.028522 | 0.052814 | 61.4105 | 0.012299 | 61.1933 | 58.239 | 57.9207 | 57.7158 | 57.9959 | 58.3918 | 59.3656 | 58.3659 | 123.1888 | 61.5432 | 123.1063 | 61.2889 | 61.3703 | 122.7279 | 61.3297 | 122.5107 | 61.8185 | 61.859 | 61.736 | 61.7765
6868.0938 | 123.2849 | -61.2717 | 61.8256 | -3.1975 | -3.5342 | -3.7573 | -3.4497 | -3.0264 | -2.0434 | -3.0614 | 61.8713 | 0.23032 | 61.7843 | -0.028522 | 0.048236 | 61.4105 | 0.012299 | 61.1978 | 58.0742 | 57.7375 | 57.5144 | 57.8219 | 58.2453 | 59.2283 | 58.2102 | 123.143 | 61.502 | 123.0559 | 61.2431 | 61.3199 | 122.6822 | 61.284 | 122.4695 | 61.8231 | 61.859 | 61.736 | 61.772
6869.0625 | 123.3215 | -61.29 | 61.8301 | -3.1929 | -3.5204 | -3.739 | -3.4497 | -3.031 | -2.0525 | -3.0706 | 61.8576 | 0.23032 | 61.7705 | -0.023943 | 0.052814 | 61.4014 | 0.007721 | 61.1887 | 58.0971 | 57.7696 | 57.551 | 57.8402 | 58.259 | 59.2375 | 58.2194 | 123.1476 | 61.5203 | 123.0605 | 61.266 | 61.3428 | 122.6913 | 61.2977 | 122.4787 | 61.8048 | 61.8499 | 61.7177 | 61.7628
6870.1094 | 123.3536 | -61.2762 | 61.7752 | -3.2524 | -3.5891 | -3.7985 | -3.5001 | -3.0905 | -2.1487 | -3.1621 | 61.8805 | 0.2349 | 61.8117 | -0.019364 | 0.048236 | 61.3968 | 0.012299 | 61.1795 | 58.0238 | 57.6871 | 57.4777 | 57.7762 | 58.1858 | 59.1276 | 58.1141 | 123.1567 | 61.5111 | 123.088 | 61.2569 | 61.3245 | 122.673 | 61.2885 | 122.4558 | 61.8323 | 61.8682 | 61.7635 | 61.7994
6871.0625 | 123.2803 | -61.2671 | 61.8439 | -3.2616 | -3.5937 | -3.7939 | -3.5047 | -3.1134 | -2.1532 | -3.1667 | 61.8759 | 0.23032 | 61.7797 | -0.033101 | 0.052814 | 61.4014 | 0.021456 | 61.1795 | 58.0055 | 57.6734 | 57.4732 | 57.7624 | 58.1537 | 59.1138 | 58.1004 | 123.143 | 61.4974 | 123.0468 | 61.234 | 61.3199 | 122.6684 | 61.2885 | 122.4466 | 61.8231 | 61.8545 | 61.7269 | 61.7582
6872.0781 | 123.3261 | -61.2717 | 61.853 | -3.2524 | -3.5845 | -3.7802 | -3.4909 | -3.0951 | -2.1532 | -3.1484 | 61.8759 | 0.23032 | 61.7843 | -0.023943 | 0.043657 | 61.4014 | 0.012299 | 61.1887 | 58.0192 | 57.6871 | 57.4915 | 57.7807 | 58.1766 | 59.1184 | 58.1233 | 123.1476 | 61.502 | 123.0559 | 61.2477 | 61.3153 | 122.673 | 61.284 | 122.4604 | 61.8323 | 61.8636 | 61.7406 | 61.772
6873.0625 | 123.2941 | -61.2854 | 61.8439 | -3.2433 | -3.5616 | -3.7665 | -3.468 | -3.0813 | -2.1487 | -3.1255 | 61.8805 | 0.2349 | 61.8117 | -0.028522 | 0.048236 | 61.3922 | 0.003143 | 61.1795 | 58.0421 | 57.7238 | 57.5189 | 57.8174 | 58.2041 | 59.1367 | 58.1599 | 123.1659 | 61.5203 | 123.0971 | 61.2569 | 61.3336 | 122.6776 | 61.2885 | 122.4649 | 61.8323 | 61.8773 | 61.7635 | 61.8086
6874.0625 | 123.2254 | -61.3037 | 61.8393 | -3.1471 | -3.4884 | -3.6566 | -3.3719 | -2.9852 | -2.08 | -3.0752 | 61.8668 | 0.22574 | 61.7751 | -0.028522 | 0.052814 | 61.4059 | 0.012299 | 61.1841 | 58.1566 | 57.8153 | 57.6471 | 57.9318 | 58.3185 | 59.2237 | 58.2286 | 123.1705 | 61.5294 | 123.0788 | 61.2752 | 61.3565 | 122.7096 | 61.316 | 122.4878 | 61.8139 | 61.8545 | 61.7223 | 61.7628
6875.1094 | 123.3948 | -61.2534 | 61.8301 | -3.2478 | -3.5891 | -3.7756 | -3.468 | -3.0676 | -2.1487 | -3.1576 | 61.8759 | 0.23032 | 61.7843 | -0.028522 | 0.052814 | 61.3922 | 0.007721 | 61.1795 | 58.0055 | 57.6643 | 57.4777 | 57.7853 | 58.1858 | 59.1047 | 58.0958 | 123.1293 | 61.4837 | 123.0376 | 61.2248 | 61.3062 | 122.6456 | 61.2611 | 122.4329 | 61.8231 | 61.8682 | 61.7314 | 61.7765
6876.0625 | 123.2071 | -61.2625 | 61.8256 | -3.3531 | -3.6898 | -3.8901 | -3.5825 | -3.15 | -2.2311 | -3.24 | 61.8851 | 0.2349 | 61.8117 | -0.023943 | 0.048236 | 61.3922 | 0.007721 | 61.1795 | 57.9094 | 57.5727 | 57.3724 | 57.68 | 58.1125 | 59.0314 | 58.0225 | 123.1476 | 61.4974 | 123.0742 | 61.2386 | 61.3107 | 122.6547 | 61.2702 | 122.442 | 61.8368 | 61.8773 | 61.7635 | 61.804
6877.0781 | 123.3353 | -61.2717 | 61.8622 | -3.1563 | -3.4975 | -3.684 | -3.3811 | -2.9715 | -2.0388 | -3.034 | 61.8713 | 0.23032 | 61.7751 | -0.019364 | 0.052814 | 61.4059 | 0.007721 | 61.1978 | 58.1154 | 57.7741 | 57.5876 | 57.8906 | 58.3002 | 59.2329 | 58.2377 | 123.143 | 61.502 | 123.0468 | 61.2523 | 61.3245 | 122.6776 | 61.2794 | 122.4695 | 61.8185 | 61.8636 | 61.7223 | 61.7674
6878.0625 | 123.262 | -61.2762 | 61.8301 | -3.1792 | -3.5113 | -3.7069 | -3.4268 | -3.0127 | -2.0754 | -3.0568 | 61.8713 | 0.2349 | 61.7705 | -0.028522 | 0.048236 | 61.3968 | 0.012299 | 61.1933 | 58.0971 | 57.765 | 57.5693 | 57.8494 | 58.2636 | 59.2008 | 58.2194 | 123.1476 | 61.5111 | 123.0468 | 61.2477 | 61.3245 | 122.673 | 61.2885 | 122.4695 | 61.8231 | 61.859 | 61.7223 | 61.7582
6879.0625 | 123.2712 | -61.2579 | 61.8393 | -3.2341 | -3.5616 | -3.7573 | -3.4635 | -3.0355 | -2.1304 | -3.1072 | 61.8759 | 0.24405 | 61.8026 | -0.03768 | 0.052814 | 61.4105 | 0.003143 | 61.1841 | 58.0238 | 57.6963 | 57.5006 | 57.7945 | 58.2224 | 59.1276 | 58.1507 | 123.1338 | 61.502 | 123.0605 | 61.2203 | 61.3107 | 122.6684 | 61.2611 | 122.442 | 61.8231 | 61.8728 | 61.7498 | 61.7994
6880.1094 | 123.3719 | -61.2717 | 61.7844 | -3.138 | -3.4655 | -3.6749 | -3.3902 | -2.976 | -2.0571 | -3.0019 | 61.8713 | 0.2349 | 61.798 | -0.033101 | 0.043657 | 61.4059 | 0.007721 | 61.1933 | 58.1337 | 57.8062 | 57.5968 | 57.8815 | 58.2956 | 59.2146 | 58.2698 | 123.143 | 61.5066 | 123.0697 | 61.2386 | 61.3153 | 122.6776 | 61.2794 | 122.4649 | 61.8277 | 61.8636 | 61.7543 | 61.7903
6881.0625 | 123.2391 | -61.322 | 61.8301 | -3.17 | -3.4884 | -3.6886 | -3.4177 | -3.0172 | -2.1075 | -3.0385 | 61.8713 | 0.23032 | 61.7659 | -0.028522 | 0.052814 | 61.4059 | 0.007721 | 61.1887 | 58.152 | 57.8337 | 57.6334 | 57.9043 | 58.3048 | 59.2146 | 58.2835 | 123.1934 | 61.5523 | 123.088 | 61.2935 | 61.3748 | 122.7279 | 61.3297 | 122.5107 | 61.8185 | 61.8636 | 61.7131 | 61.7582
6882.0938 | 123.2941 | -61.322 | 61.7981 | -3.0922 | -3.4197 | -3.6062 | -3.3444 | -2.9531 | -2.0251 | -2.9561 | 61.8668 | 0.23032 | 61.7934 | -0.028522 | 0.043657 | 61.4014 | 0.012299 | 61.1887 | 58.2298 | 57.9023 | 57.7158 | 57.9776 | 58.3689 | 59.297 | 58.3659 | 123.1888 | 61.5523 | 123.1154 | 61.2935 | 61.3657 | 122.7234 | 61.3343 | 122.5107 | 61.8231 | 61.8545 | 61.7498 | 61.7811
6883.0625 | 123.3078 | -61.2762 | 61.8576 | -3.17 | -3.4838 | -3.652 | -3.3948 | -3.0172 | -2.1532 | -3.0706 | 61.8713 | 0.23032 | 61.7934 | -0.014785 | 0.048236 | 61.4014 | 0.007721 | 61.207 | 58.1062 | 57.7925 | 57.6243 | 57.8815 | 58.259 | 59.123 | 58.2057 | 123.1476 | 61.5066 | 123.0697 | 61.2615 | 61.3245 | 122.6776 | 61.284 | 122.4832 | 61.8231 | 61.8636 | 61.7452 | 61.7857
6884.0781 | 123.2162 | -61.2946 | 61.8484 | -3.0876 | -3.4014 | -3.5879 | -3.3261 | -2.944 | -2.0479 | -2.9607 | 61.8622 | 0.23032 | 61.7705 | -0.028522 | 0.043657 | 61.4059 | 0.003143 | 61.2024 | 58.207 | 57.8932 | 57.7067 | 57.9684 | 58.3506 | 59.2466 | 58.3339 | 123.1567 | 61.5249 | 123.0651 | 61.266 | 61.3382 | 122.7005 | 61.2977 | 122.497 | 61.8185 | 61.859 | 61.7269 | 61.7674
6885.0625 | 123.4406 | -61.3037 | 61.7661 | -2.877 | -3.1999 | -3.3819 | -3.1155 | -2.7242 | -1.8465 | -2.7593 | 61.8484 | 0.23032 | 61.7614 | -0.023943 | 0.052814 | 61.4197 | 0.007721 | 61.1933 | 58.4267 | 58.1038 | 57.9219 | 58.1882 | 58.5795 | 59.4572 | 58.5444 | 123.1521 | 61.534 | 123.0651 | 61.2798 | 61.3565 | 122.7234 | 61.3114 | 122.497 | 61.7956 | 61.8407 | 61.7085 | 61.7536
6886.0938 | 123.2849 | -61.322 | 61.8484 | -2.8587 | -3.1907 | -3.3681 | -3.0789 | -2.6785 | -1.8099 | -2.7364 | 61.8576 | 0.2349 | 61.7797 | -0.028522 | 0.043657 | 61.4197 | 0.012299 | 61.207 | 58.4633 | 58.1313 | 57.9539 | 58.2431 | 58.6436 | 59.5122 | 58.5857 | 123.1796 | 61.5569 | 123.1017 | 61.2935 | 61.3657 | 122.7417 | 61.3343 | 122.529 | 61.8139 | 61.8453 | 61.736 | 61.7674
6887.0625 | 123.2712 | -61.322 | 61.8256 | -2.964 | -3.2961 | -3.4597 | -3.1704 | -2.7838 | -1.9426 | -2.8646 | 61.8668 | 0.23032 | 61.7751 | -0.033101 | 0.052814 | 61.4151 | 0.016878 | 61.207 | 58.358 | 58.026 | 57.8623 | 58.1516 | 58.5383 | 59.3794 | 58.4575 | 123.1888 | 61.5523 | 123.0971 | 61.2889 | 61.3748 | 122.7371 | 61.3389 | 122.529 | 61.8139 | 61.8499 | 61.7223 | 61.7582
6888.0781 | 123.3948 | -61.2762 | 61.7981 | -3.0876 | -3.4197 | -3.5833 | -3.2849 | -2.8845 | -2.0479 | -2.9744 | 61.8668 | 0.2349 | 61.7659 | -0.033101 | 0.052814 | 61.4105 | 0.021456 | 61.1978 | 58.1886 | 57.8566 | 57.6929 | 57.9913 | 58.3918 | 59.2283 | 58.3018 | 123.143 | 61.5111 | 123.0422 | 61.2431 | 61.3291 | 122.6868 | 61.2977 | 122.4741 | 61.8139 | 61.8453 | 61.7131 | 61.7445
6889.0625 | 123.2849 | -61.3037 | 61.853 | -3.0143 | -3.3373 | -3.5238 | -3.2254 | -2.8204 | -2.0022 | -2.9058 | 61.8668 | 0.22574 | 61.7751 | -0.028522 | 0.048236 | 61.4014 | 0.012299 | 61.1933 | 58.2894 | 57.9664 | 57.7799 | 58.0783 | 58.4833 | 59.3015 | 58.3979 | 123.1705 | 61.5294 | 123.0788 | 61.2752 | 61.3519 | 122.7051 | 61.316 | 122.497 | 61.8185 | 61.8545 | 61.7269 | 61.7628
6890.1094 | 123.2758 | -61.2808 | 61.8439 | -3.0189 | -3.351 | -3.5101 | -3.2117 | -2.8112 | -2.0159 | -2.9287 | 61.8668 | 0.2349 | 61.7888 | -0.028522 | 0.057392 | 61.4059 | 0.016878 | 61.207 | 58.2619 | 57.9298 | 57.7708 | 58.0692 | 58.4696 | 59.2649 | 58.3522 | 123.1476 | 61.5157 | 123.0697 | 61.2523 | 61.3382 | 122.6868 | 61.2977 | 122.4878 | 61.8094 | 61.8499 | 61.7314 | 61.772
6891.0625 | 123.2986 | -61.29 | 61.8439 | -2.9731 | -3.319 | -3.4917 | -3.1521 | -2.7517 | -1.9243 | -2.892 | 61.8576 | 0.23948 | 61.7797 | -0.019364 | 0.052814 | 61.4151 | 0.012299 | 61.2116 | 58.3168 | 57.971 | 57.7982 | 58.1378 | 58.5383 | 59.3656 | 58.3979 | 123.1476 | 61.5295 | 123.0697 | 61.2706 | 61.3428 | 122.7051 | 61.3023 | 122.5016 | 61.8048 | 61.8453 | 61.7269 | 61.7674
6892.0781 | 123.2895 | -61.3174 | 61.8576 | -2.8404 | -3.1679 | -3.3406 | -3.0422 | -2.6418 | -1.8282 | -2.7455 | 61.853 | 0.23032 | 61.7476 | -0.019364 | 0.052814 | 61.4242 | 0.007721 | 61.2116 | 58.4771 | 58.1496 | 57.9768 | 58.2752 | 58.6756 | 59.4893 | 58.5719 | 123.1705 | 61.5478 | 123.0651 | 61.2981 | 61.3703 | 122.7417 | 61.3252 | 122.529 | 61.8002 | 61.8453 | 61.6948 | 61.7399
6893.0625 | 123.2895 | -61.2762 | 61.8301 | -2.8953 | -3.2457 | -3.4139 | -3.1063 | -2.683 | -1.8602 | -2.7959 | 61.8484 | 0.2349 | 61.7568 | -0.028522 | 0.06197 | 61.4197 | 0.012299 | 61.207 | 58.3809 | 58.0306 | 57.8623 | 58.1699 | 58.5932 | 59.416 | 58.4804 | 123.1247 | 61.5111 | 123.033 | 61.2477 | 61.3382 | 122.6959 | 61.2885 | 122.4832 | 61.7865 | 61.8361 | 61.6948 | 61.7445
6894.0781 | 123.3719 | -61.2671 | 61.7981 | -2.996 | -3.351 | -3.5192 | -3.1888 | -2.7654 | -1.9518 | -2.892 | 61.8622 | 0.2349 | 61.8026 | -0.028522 | 0.052814 | 61.4105 | 0.012299 | 61.1887 | 58.2711 | 57.9161 | 57.7479 | 58.0783 | 58.5016 | 59.3153 | 58.3751 | 123.1293 | 61.502 | 123.0697 | 61.2386 | 61.3199 | 122.6776 | 61.2794 | 122.4558 | 61.8094 | 61.8499 | 61.7498 | 61.7903
6895.0625 | 123.2437 | -61.3174 | 61.7981 | -2.9869 | -3.3235 | -3.5101 | -3.1933 | -2.7838 | -1.961 | -2.8829 | 61.8668 | 0.23032 | 61.7797 | -0.028522 | 0.043657 | 61.4151 | 0.003143 | 61.1933 | 58.3306 | 57.9939 | 57.8074 | 58.1241 | 58.5337 | 59.3565 | 58.4346 | 123.1842 | 61.5478 | 123.0971 | 61.2889 | 61.3611 | 122.7325 | 61.3206 | 122.5107 | 61.8231 | 61.8636 | 61.736 | 61.7765
6896.0781 | 123.381 | -61.2946 | 61.8073 | -2.9502 | -3.2777 | -3.4505 | -3.1521 | -2.7426 | -1.9426 | -2.8462 | 61.8576 | 0.22116 | 61.7522 | -0.028522 | 0.048236 | 61.4197 | 0.012299 | 61.2024 | 58.3443 | 58.0168 | 57.844 | 58.1424 | 58.552 | 59.3519 | 58.4483 | 123.1522 | 61.5157 | 123.0468 | 61.266 | 61.3428 | 122.7142 | 61.3069 | 122.497 | 61.8094 | 61.8453 | 61.704 | 61.7399
6897.0625 | 123.2346 | -61.2671 | 61.8576 | -3.0143 | -3.351 | -3.5238 | -3.2208 | -2.7929 | -1.993 | -2.9103 | 61.8622 | 0.22574 | 61.7614 | -0.028522 | 0.048236 | 61.4151 | 0.012299 | 61.207 | 58.2527 | 57.9161 | 57.7433 | 58.0463 | 58.4742 | 59.2741 | 58.3567 | 123.1293 | 61.4928 | 123.0285 | 61.2386 | 61.3153 | 122.6822 | 61.2794 | 122.4741 | 61.8139 | 61.8499 | 61.7131 | 61.7491
6898.0781 | 123.381 | -61.2671 | 61.7889 | -2.9731 | -3.3144 | -3.4826 | -3.175 | -2.7517 | -1.9564 | -2.86 | 61.8576 | 0.2349 | 61.7797 | -0.023943 | 0.048236 | 61.4151 | 0.007721 | 61.1933 | 58.294 | 57.9527 | 57.7845 | 58.0921 | 58.5154 | 59.3107 | 58.4071 | 123.1247 | 61.502 | 123.0468 | 61.2431 | 61.3153 | 122.6822 | 61.2748 | 122.4604 | 61.8094 | 61.8499 | 61.7314 | 61.772
6899.0625 | 123.2849 | -61.3174 | 61.8393 | -3.1792 | -3.5342 | -3.6886 | -3.3627 | -2.944 | -2.1624 | -3.0706 | 61.8668 | 0.2349 | 61.8071 | -0.023943 | 0.048236 | 61.4059 | 0.016878 | 61.1933 | 58.1383 | 57.7833 | 57.6288 | 57.9547 | 58.3735 | 59.155 | 58.2469 | 123.1842 | 61.5523 | 123.1246 | 61.2935 | 61.3657 | 122.7234 | 61.3343 | 122.5107 | 61.8185 | 61.8499 | 61.7589 | 61.7903
6900.1094 | 123.3124 | -61.3174 | 61.7615 | -2.9274 | -3.2732 | -3.4551 | -3.1155 | -2.6968 | -1.9014 | -2.8142 | 61.853 | 0.22116 | 61.7568 | -0.023943 | 0.052814 | 61.4105 | 0.007721 | 61.1978 | 58.3901 | 58.0443 | 57.8623 | 58.2019 | 58.6207 | 59.416 | 58.5032 | 123.1705 | 61.5386 | 123.0742 | 61.2935 | 61.3703 | 122.7279 | 61.3252 | 122.5153 | 61.8002 | 61.8453 | 61.704 | 61.7491
6901.0625 | 123.3078 | -61.2854 | 61.8073 | -2.8541 | -3.2136 | -3.3819 | -3.0239 | -2.6052 | -1.8007 | -2.7318 | 61.853 | 0.2349 | 61.7568 | -0.033101 | 0.052814 | 61.4288 | 0.012299 | 61.2116 | 58.4313 | 58.0718 | 57.9035 | 58.2615 | 58.6802 | 59.4847 | 58.5536 | 123.1384 | 61.5203 | 123.0422 | 61.2523 | 61.3382 | 122.7142 | 61.2977 | 122.497 | 61.8002 | 61.8407 | 61.704 | 61.7445
6902.0625 | 123.2986 | -61.2808 | 61.8347 | -2.8633 | -3.2182 | -3.391 | -3.0514 | -2.6235 | -1.8419 | -2.7455 | 61.853 | 0.23032 | 61.7751 | -0.019364 | 0.048236 | 61.4197 | 0.016878 | 61.2162 | 58.4176 | 58.0626 | 57.8898 | 58.2294 | 58.6573 | 59.4389 | 58.5353 | 123.1338 | 61.5111 | 123.0559 | 61.2615 | 61.3291 | 122.7005 | 61.2977 | 122.497 | 61.8048 | 61.8361 | 61.7269 | 61.7582
6903.0938 | 123.317 | -61.3083 | 61.8027 | -2.6984 | -3.0396 | -3.2124 | -2.8866 | -2.4633 | -1.6908 | -2.5807 | 61.8484 | 0.23948 | 61.7797 | -0.019364 | 0.048236 | 61.4334 | 0.007721 | 61.2299 | 58.6099 | 58.2686 | 58.0958 | 58.4217 | 58.845 | 59.6175 | 58.7276 | 123.1567 | 61.5478 | 123.088 | 61.2889 | 61.3565 | 122.7417 | 61.316 | 122.5382 | 61.8002 | 61.8407 | 61.7314 | 61.772
6904.0625 | 123.2941 | -61.3037 | 61.853 | -2.8404 | -3.1862 | -3.3727 | -3.0285 | -2.6006 | -1.8282 | -2.6997 | 61.8439 | 0.22574 | 61.7614 | -0.028522 | 0.048236 | 61.4242 | 0.003143 | 61.2207 | 58.4633 | 58.1175 | 57.931 | 58.2752 | 58.7031 | 59.4755 | 58.604 | 123.1476 | 61.5294 | 123.0651 | 61.2752 | 61.3519 | 122.728 | 61.3069 | 122.5245 | 61.7956 | 61.8407 | 61.7131 | 61.7582
6905.0938 | 123.3765 | -61.3129 | 61.7844 | -2.8358 | -3.1862 | -3.3452 | -3.0285 | -2.6006 | -1.8236 | -2.7089 | 61.8484 | 0.23032 | 61.7522 | -0.028522 | 0.039079 | 61.4242 | 0.012299 | 61.2116 | 58.4771 | 58.1267 | 57.9676 | 58.2844 | 58.7122 | 59.4893 | 58.604 | 123.1613 | 61.5432 | 123.0651 | 61.2843 | 61.3519 | 122.7371 | 61.3252 | 122.5244 | 61.8094 | 61.8361 | 61.7131 | 61.7399
6906.0625 | 123.3078 | -61.3358 | 61.8027 | -2.7351 | -3.09 | -3.2536 | -2.9232 | -2.4908 | -1.7366 | -2.6311 | 61.853 | 0.22574 | 61.7614 | -0.023943 | 0.052814 | 61.4288 | 0.007721 | 61.2207 | 58.6007 | 58.2457 | 58.0821 | 58.4126 | 58.845 | 59.5991 | 58.7047 | 123.1888 | 61.5615 | 123.0971 | 61.3118 | 61.3886 | 122.7646 | 61.3435 | 122.5565 | 61.8002 | 61.8453 | 61.7085 | 61.7536
6907.0781 | 123.4222 | -61.2762 | 61.7844 | -2.7808 | -3.1404 | -3.2811 | -2.9369 | -2.5045 | -1.7458 | -2.686 | 61.853 | 0.2349 | 61.7843 | -0.023943 | 0.048236 | 61.4242 | 0.007721 | 61.2207 | 58.4954 | 58.1359 | 57.9951 | 58.3393 | 58.7717 | 59.5305 | 58.5902 | 123.1293 | 61.5111 | 123.0605 | 61.2523 | 61.3245 | 122.7005 | 61.284 | 122.497 | 61.8048 | 61.8453 | 61.736 | 61.7765
6908.0625 | 123.2849 | -61.2946 | 61.821 | -2.7946 | -3.145 | -3.304 | -2.969 | -2.5457 | -1.7916 | -2.6952 | 61.853 | 0.23948 | 61.7705 | -0.028522 | 0.043657 | 61.4151 | 0.007721 | 61.2253 | 58.5 | 58.1496 | 57.9905 | 58.3256 | 58.7489 | 59.503 | 58.5994 | 123.1476 | 61.534 | 123.0651 | 61.266 | 61.3382 | 122.7096 | 61.3023 | 122.5199 | 61.8094 | 61.8453 | 61.7269 | 61.7628
6909.0781 | 123.381 | -61.2854 | 61.7569 | -2.6984 | -3.0442 | -3.1987 | -2.8912 | -2.4816 | -1.7504 | -2.6265 | 61.8393 | 0.23032 | 61.7476 | -0.028522 | 0.052814 | 61.438 | 0.007721 | 61.2162 | 58.587 | 58.2412 | 58.0867 | 58.3942 | 58.8038 | 59.535 | 58.6589 | 123.1247 | 61.5157 | 123.033 | 61.2569 | 61.3382 | 122.7234 | 61.2931 | 122.5016 | 61.7865 | 61.8316 | 61.6948 | 61.7399
6910.0625 | 123.2758 | -61.3449 | 61.8073 | -2.7534 | -3.0992 | -3.2536 | -2.9186 | -2.5228 | -1.7687 | -2.6494 | 61.8439 | 0.23032 | 61.7522 | -0.028522 | 0.052814 | 61.4288 | 0.007721 | 61.2207 | 58.5915 | 58.2457 | 58.0913 | 58.4263 | 58.8221 | 59.5762 | 58.6955 | 123.1888 | 61.5752 | 123.0971 | 61.3164 | 61.3977 | 122.7737 | 61.3526 | 122.5656 | 61.791 | 61.8361 | 61.6994 | 61.7445
6911.0781 | 123.3078 | -61.2991 | 61.7706 | -2.7167 | -3.0717 | -3.2262 | -2.8957 | -2.4908 | -1.7366 | -2.6219 | 61.8393 | 0.22116 | 61.7476 | -0.028522 | 0.052814 | 61.4242 | 0.003143 | 61.2162 | 58.5824 | 58.2274 | 58.073 | 58.4034 | 58.8084 | 59.5625 | 58.6772 | 123.1384 | 61.5203 | 123.0468 | 61.2706 | 61.3519 | 122.7234 | 61.3023 | 122.5153 | 61.7865 | 61.8361 | 61.6948 | 61.7445
6912.0625 | 123.3124 | -61.3037 | 61.8118 | -2.584 | -2.9389 | -3.0934 | -2.7584 | -2.3397 | -1.6038 | -2.48 | 61.8439 | 0.2349 | 61.7522 | -0.033101 | 0.052814 | 61.4334 | 0.016878 | 61.2253 | 58.7197 | 58.3648 | 58.2103 | 58.5453 | 58.964 | 59.6999 | 58.8237 | 123.1476 | 61.5386 | 123.0559 | 61.2706 | 61.3565 | 122.7371 | 61.3206 | 122.529 | 61.791 | 61.827 | 61.6994 | 61.7353
6913.0938 | 123.3719 | -61.2854 | 61.7569 | -2.5748 | -2.916 | -3.0705 | -2.7492 | -2.3397 | -1.6313 | -2.4754 | 61.8393 | 0.23032 | 61.7659 | -0.033101 | 0.057392 | 61.438 | 0.016878 | 61.2345 | 58.7106 | 58.3694 | 58.2149 | 58.5362 | 58.9457 | 59.6541 | 58.81 | 123.1247 | 61.5157 | 123.0513 | 61.2523 | 61.3428 | 122.7234 | 61.3023 | 122.5199 | 61.7819 | 61.8224 | 61.7086 | 61.7491
6914.0625 | 123.2666 | -61.3358 | 61.8164 | -2.5016 | -2.8473 | -2.9744 | -2.6577 | -2.2619 | -1.5489 | -2.4205 | 61.8301 | 0.2349 | 61.743 | -0.023943 | 0.052814 | 61.438 | 0.016878 | 61.2207 | 58.8342 | 58.4884 | 58.3614 | 58.6781 | 59.0739 | 59.7869 | 58.9153 | 123.1659 | 61.5707 | 123.0788 | 61.3118 | 61.3886 | 122.7737 | 61.3526 | 122.5565 | 61.7773 | 61.8132 | 61.6902 | 61.7262
6915.1094 | 123.4039 | -61.2946 | 61.7889 | -2.6206 | -2.9618 | -3.0934 | -2.7675 | -2.3809 | -1.7137 | -2.5578 | 61.8347 | 0.22116 | 61.743 | -0.023943 | 0.043657 | 61.438 | 0.016878 | 61.2299 | 58.674 | 58.3327 | 58.2012 | 58.527 | 58.9137 | 59.5808 | 58.7367 | 123.1293 | 61.5157 | 123.0376 | 61.2706 | 61.3382 | 122.7325 | 61.3114 | 122.5245 | 61.791 | 61.8178 | 61.6994 | 61.7262
6916.0625 | 123.2849 | -61.3037 | 61.8164 | -2.5519 | -2.9023 | -3.0247 | -2.6943 | -2.3168 | -1.6405 | -2.4891 | 61.8301 | 0.2349 | 61.7385 | -0.028522 | 0.057392 | 61.4334 | 0.003143 | 61.2207 | 58.7518 | 58.4014 | 58.279 | 58.6094 | 58.9869 | 59.6632 | 58.8146 | 123.1338 | 61.5386 | 123.0422 | 61.2752 | 61.3611 | 122.7371 | 61.3069 | 122.5245 | 61.7727 | 61.827 | 61.6811 | 61.7353
6917.0781 | 123.317 | -61.3129 | 61.7523 | -2.4649 | -2.8199 | -2.9515 | -2.6256 | -2.2344 | -1.5352 | -2.4067 | 61.8301 | 0.23032 | 61.7476 | -0.033101 | 0.057392 | 61.4471 | 0.016878 | 61.2207 | 58.8479 | 58.493 | 58.3614 | 58.6873 | 59.0785 | 59.7777 | 58.9061 | 123.143 | 61.5432 | 123.0605 | 61.2798 | 61.3703 | 122.76 | 61.3297 | 122.5336 | 61.7727 | 61.8132 | 61.6902 | 61.7308
6918.0625 | 123.2803 | -61.3495 | 61.7935 | -2.2452 | -2.5955 | -2.7317 | -2.415 | -2.0055 | -1.2925 | -2.1595 | 61.821 | 0.2349 | 61.7476 | -0.028522 | 0.048236 | 61.4517 | 0.012299 | 61.2528 | 59.1043 | 58.754 | 58.6178 | 58.9345 | 59.344 | 60.057 | 59.19 | 123.1705 | 61.5844 | 123.0971 | 61.321 | 61.3977 | 122.8012 | 61.3618 | 122.6023 | 61.7727 | 61.8087 | 61.6994 | 61.7353
6919.0781 | 123.349 | -61.3037 | 61.7706 | -2.5107 | -2.8748 | -3.0064 | -2.676 | -2.2573 | -1.5581 | -2.4342 | 61.8347 | 0.23032 | 61.7705 | -0.033101 | 0.043657 | 61.4426 | 0.007721 | 61.2162 | 58.793 | 58.4289 | 58.2973 | 58.6277 | 59.0464 | 59.7457 | 58.8695 | 123.1384 | 61.534 | 123.0742 | 61.2706 | 61.3474 | 122.7463 | 61.3114 | 122.5199 | 61.791 | 61.827 | 61.7269 | 61.7628
6920.0625 | 123.3032 | -61.3174 | 61.7935 | -2.5061 | -2.8611 | -3.0064 | -2.6668 | -2.2436 | -1.5397 | -2.4067 | 61.8347 | 0.2349 | 61.7568 | -0.028522 | 0.052814 | 61.4426 | 0.016878 | 61.2345 | 58.8113 | 58.4564 | 58.311 | 58.6506 | 59.0739 | 59.7777 | 58.9107 | 123.1521 | 61.5523 | 123.0742 | 61.2889 | 61.3703 | 122.76 | 61.3343 | 122.5519 | 61.7819 | 61.8178 | 61.704 | 61.7399
6921.0938 | 123.4085 | -61.2854 | 61.7752 | -2.4192 | -2.7649 | -2.9194 | -2.5798 | -2.1657 | -1.4528 | -2.3289 | 61.8255 | 0.23032 | 61.7247 | -0.042259 | 0.048236 | 61.4517 | 0.016878 | 61.2391 | 58.8662 | 58.5205 | 58.366 | 58.7056 | 59.1197 | 59.8326 | 58.9565 | 123.1109 | 61.5157 | 123.0101 | 61.2431 | 61.3336 | 122.7371 | 61.3023 | 122.5245 | 61.7773 | 61.8087 | 61.6765 | 61.7079
6922.0625 | 123.2941 | -61.322 | 61.8301 | -2.5519 | -2.9023 | -3.0522 | -2.7126 | -2.2985 | -1.5901 | -2.4754 | 61.8393 | 0.22116 | 61.7385 | -0.028522 | 0.048236 | 61.4334 | 0.012299 | 61.2253 | 58.7701 | 58.4197 | 58.2698 | 58.6094 | 59.0235 | 59.7319 | 58.8466 | 123.1613 | 61.5432 | 123.0605 | 61.2935 | 61.3703 | 122.7554 | 61.3343 | 122.5473 | 61.791 | 61.827 | 61.6902 | 61.7262
6923.0781 | 123.3627 | -61.3083 | 61.7844 | -2.5061 | -2.8565 | -3.0018 | -2.6714 | -2.2573 | -1.581 | -2.4434 | 61.8301 | 0.22116 | 61.7293 | -0.023943 | 0.048236 | 61.4471 | 0.007721 | 61.2253 | 58.8021 | 58.4518 | 58.3065 | 58.6369 | 59.051 | 59.7273 | 58.8649 | 123.1384 | 61.5295 | 123.0376 | 61.2843 | 61.3565 | 122.7554 | 61.316 | 122.5336 | 61.7819 | 61.8224 | 61.6811 | 61.7216
6924.0625 | 123.2986 | -61.3129 | 61.8027 | -2.442 | -2.8015 | -2.924 | -2.5936 | -2.1795 | -1.526 | -2.3976 | 61.8347 | 0.22116 | 61.743 | -0.028522 | 0.052814 | 61.4517 | 0.012299 | 61.2299 | 58.8708 | 58.5113 | 58.3889 | 58.7193 | 59.1334 | 59.7869 | 58.9153 | 123.1476 | 61.534 | 123.0559 | 61.2843 | 61.3657 | 122.7646 | 61.3252 | 122.5428 | 61.7819 | 61.8224 | 61.6902 | 61.7308
6925.0938 | 123.3215 | -61.3174 | 61.7844 | -2.3734 | -2.71 | -2.8462 | -2.5157 | -2.1154 | -1.4528 | -2.3243 | 61.821 | 0.2349 | 61.7522 | -0.023943 | 0.057392 | 61.4426 | 0.016878 | 61.2391 | 58.9441 | 58.6075 | 58.4713 | 58.8017 | 59.2021 | 59.8647 | 58.9931 | 123.1384 | 61.5523 | 123.0697 | 61.2935 | 61.3748 | 122.76 | 61.3343 | 122.5565 | 61.7636 | 61.8041 | 61.6948 | 61.7353
6926.0625 | 123.2666 | -61.3403 | 61.8164 | -2.3276 | -2.6733 | -2.8141 | -2.4837 | -2.065 | -1.3887 | -2.2648 | 61.821 | 0.22574 | 61.7568 | -0.019364 | 0.052814 | 61.4471 | 0.012299 | 61.2528 | 59.0127 | 58.667 | 58.5262 | 58.8567 | 59.2753 | 59.9517 | 59.0755 | 123.1613 | 61.5661 | 123.0971 | 61.321 | 61.3931 | 122.7875 | 61.3526 | 122.5931 | 61.7682 | 61.8087 | 61.704 | 61.7445
6927.0781 | 123.3856 | -61.3312 | 61.7294 | -2.2314 | -2.5726 | -2.718 | -2.3738 | -1.9597 | -1.2696 | -2.1595 | 61.821 | 0.2349 | 61.7385 | -0.033101 | 0.043657 | 61.4563 | 0.007721 | 61.2482 | 59.0997 | 58.7586 | 58.6132 | 58.9574 | 59.3715 | 60.0616 | 59.1717 | 123.1521 | 61.5661 | 123.0696 | 61.2981 | 61.3748 | 122.7875 | 61.3389 | 122.5794 | 61.7773 | 61.8132 | 61.6948 | 61.7308
6928.0625 | 123.381 | -61.2991 | 61.8027 | -2.3551 | -2.6962 | -2.8553 | -2.5157 | -2.0833 | -1.3841 | -2.2694 | 61.821 | 0.2349 | 61.7339 | -0.028522 | 0.052814 | 61.4563 | 0.003143 | 61.2528 | 58.9441 | 58.6029 | 58.4438 | 58.7834 | 59.2158 | 59.9151 | 59.0297 | 123.1201 | 61.534 | 123.033 | 61.2706 | 61.3519 | 122.7554 | 61.3023 | 122.5519 | 61.7682 | 61.8178 | 61.6811 | 61.7308
6929.0781 | 123.3627 | -61.3312 | 61.734 | -2.2681 | -2.6138 | -2.7546 | -2.4241 | -2.0101 | -1.3383 | -2.2099 | 61.8164 | 0.23032 | 61.7247 | -0.028522 | 0.048236 | 61.4563 | 0.007721 | 61.2528 | 59.0631 | 58.7174 | 58.5766 | 58.907 | 59.3211 | 59.9929 | 59.1213 | 123.1476 | 61.5615 | 123.0559 | 61.3027 | 61.3794 | 122.7875 | 61.3389 | 122.584 | 61.7682 | 61.8087 | 61.6765 | 61.717
6930.0625 | 123.2437 | -61.3815 | 61.7889 | -2.1673 | -2.5314 | -2.6493 | -2.3188 | -1.9002 | -1.2009 | -2.1092 | 61.8164 | 0.22116 | 61.7156 | -0.023943 | 0.048236 | 61.4563 | 0.003143 | 61.2574 | 59.2142 | 58.8501 | 58.7323 | 59.0627 | 59.4813 | 60.1806 | 59.2724 | 123.1979 | 61.6027 | 123.0971 | 61.3576 | 61.4298 | 122.8378 | 61.3847 | 122.6389 | 61.7682 | 61.8132 | 61.6673 | 61.7124
6931.0938 | 123.3627 | -61.322 | 61.7889 | -2.1994 | -2.5726 | -2.6859 | -2.3509 | -1.9231 | -1.233 | -2.1549 | 61.821 | 0.22574 | 61.7293 | -0.023943 | 0.048236 | 61.4609 | 0.012299 | 61.2574 | 59.1226 | 58.7494 | 58.6361 | 58.9711 | 59.3989 | 60.089 | 59.1671 | 123.143 | 61.5478 | 123.0513 | 61.2981 | 61.3703 | 122.7829 | 61.3343 | 122.5794 | 61.7727 | 61.8087 | 61.6811 | 61.717
6932.0625 | 123.3948 | -61.3312 | 61.7432 | -2.149 | -2.5268 | -2.6218 | -2.2822 | -1.8499 | -1.1781 | -2.1092 | 61.8027 | 0.23032 | 61.7293 | -0.033101 | 0.052814 | 61.4654 | 0.012299 | 61.2436 | 59.1821 | 58.8044 | 58.7094 | 59.049 | 59.4813 | 60.1531 | 59.222 | 123.1338 | 61.5615 | 123.0605 | 61.2981 | 61.384 | 122.7966 | 61.3435 | 122.5748 | 61.7498 | 61.7904 | 61.6765 | 61.717
6933.0781 | 123.4085 | -61.3037 | 61.7386 | -2.1948 | -2.5634 | -2.6722 | -2.3372 | -1.9048 | -1.2467 | -2.1458 | 61.8118 | 0.23032 | 61.7385 | -0.033101 | 0.043657 | 61.4563 | 0.003143 | 61.2482 | 59.1089 | 58.7403 | 58.6315 | 58.9666 | 59.3989 | 60.057 | 59.1579 | 123.1155 | 61.534 | 123.0422 | 61.2706 | 61.3474 | 122.76 | 61.3069 | 122.5519 | 61.7682 | 61.8087 | 61.6948 | 61.7353
6934.0625 | 123.3673 | -61.3449 | 61.7432 | -1.9293 | -2.2933 | -2.4112 | -2.0808 | -1.6576 | -0.98576 | -1.8757 | 61.7935 | 0.23032 | 61.7156 | -0.023943 | 0.048236 | 61.4792 | 0.012299 | 61.2619 | 59.4156 | 59.0516 | 58.9337 | 59.2641 | 59.6873 | 60.3591 | 59.4692 | 123.1384 | 61.5752 | 123.0605 | 61.321 | 61.3931 | 122.8241 | 61.3572 | 122.6069 | 61.7453 | 61.7812 | 61.6673 | 61.7033
6935.0938 | 123.2437 | -61.3358 | 61.7569 | -1.9476 | -2.3162 | -2.4295 | -2.0899 | -1.6667 | -0.99492 | -1.894 | 61.8027 | 0.23948 | 61.7247 | -0.028522 | 0.043657 | 61.4654 | 0.016878 | 61.2574 | 59.3882 | 59.0196 | 58.9063 | 59.2458 | 59.669 | 60.3408 | 59.4418 | 123.1384 | 61.5752 | 123.0605 | 61.3072 | 61.3794 | 122.8012 | 61.3526 | 122.5931 | 61.759 | 61.7858 | 61.6811 | 61.7079
6936.0625 | 123.3307 | -61.3678 | 61.7569 | -2.0391 | -2.4078 | -2.5257 | -2.1906 | -1.7491 | -1.0544 | -1.9718 | 61.8072 | 0.23948 | 61.7339 | -0.023943 | 0.057392 | 61.4654 | 0.016878 | 61.2574 | 59.3287 | 58.96 | 58.8421 | 59.1772 | 59.6187 | 60.3134 | 59.396 | 123.175 | 61.6073 | 123.1017 | 61.3439 | 61.4252 | 122.8332 | 61.3847 | 122.6252 | 61.7498 | 61.7904 | 61.6765 | 61.717
6937.0938 | 123.3582 | -61.3495 | 61.734 | -1.9751 | -2.3482 | -2.4707 | -2.1403 | -1.7125 | -1.0315 | -1.9169 | 61.8072 | 0.23032 | 61.7293 | -0.033101 | 0.043657 | 61.47 | 0.007721 | 61.2574 | 59.3744 | 59.0012 | 58.8788 | 59.2092 | 59.637 | 60.3179 | 59.4326 | 123.1567 | 61.5798 | 123.0788 | 61.3164 | 61.3931 | 122.8195 | 61.3572 | 122.6069 | 61.7636 | 61.7995 | 61.6857 | 61.7216
6938.0625 | 123.3765 | -61.3724 | 61.7203 | -1.8331 | -2.1971 | -2.3105 | -1.9846 | -1.5431 | -0.88961 | -1.7704 | 61.7935 | 0.23032 | 61.7156 | -0.028522 | 0.048236 | 61.4746 | 0.007721 | 61.2619 | 59.5393 | 59.1752 | 59.0619 | 59.3878 | 59.8292 | 60.4828 | 59.602 | 123.1659 | 61.6027 | 123.088 | 61.3439 | 61.4206 | 122.847 | 61.3801 | 122.6343 | 61.7453 | 61.7858 | 61.6673 | 61.7079
6939.0938 | 123.4039 | -61.3861 | 61.6791 | -1.7553 | -2.1101 | -2.2143 | -1.893 | -1.4516 | -0.82094 | -1.7063 | 61.7935 | 0.2349 | 61.7293 | -0.028522 | 0.043657 | 61.4838 | 0.016878 | 61.2665 | 59.6308 | 59.276 | 59.1718 | 59.4931 | 59.9345 | 60.5652 | 59.6798 | 123.1796 | 61.621 | 123.1154 | 61.3576 | 61.4298 | 122.8699 | 61.403 | 122.6526 | 61.7498 | 61.7766 | 61.6857 | 61.7124
6940.0625 | 123.4222 | -61.3174 | 61.7432 | -1.7599 | -2.133 | -2.2326 | -1.893 | -1.4562 | -0.81178 | -1.7063 | 61.7981 | 0.23948 | 61.7247 | -0.033101 | 0.052814 | 61.4838 | 0.012299 | 61.2711 | 59.5576 | 59.1844 | 59.0848 | 59.4244 | 59.8613 | 60.5057 | 59.6112 | 123.1155 | 61.5569 | 123.0422 | 61.2843 | 61.3703 | 122.8012 | 61.3297 | 122.5885 | 61.7453 | 61.7858 | 61.6719 | 61.7124
6941.1094 | 123.2941 | -61.3815 | 61.7615 | -1.7003 | -2.0689 | -2.1685 | -1.8289 | -1.3875 | -0.71564 | -1.6468 | 61.7889 | 0.23948 | 61.7247 | -0.019364 | 0.048236 | 61.4883 | 0.016878 | 61.2757 | 59.6812 | 59.3126 | 59.213 | 59.5526 | 59.9941 | 60.6659 | 59.7348 | 123.1704 | 61.621 | 123.1063 | 61.3622 | 61.4298 | 122.8699 | 61.3984 | 122.6572 | 61.7407 | 61.772 | 61.6765 | 61.7079
6942.0625 | 123.349 | -61.3495 | 61.702 | -1.6866 | -2.0552 | -2.1685 | -1.8335 | -1.3829 | -0.70648 | -1.601 | 61.7843 | 0.23948 | 61.711 | -0.033101 | 0.048236 | 61.4883 | 0.007721 | 61.2711 | 59.6629 | 59.2943 | 59.181 | 59.516 | 59.9666 | 60.643 | 59.7485 | 123.1338 | 61.589 | 123.0605 | 61.3164 | 61.3977 | 122.8378 | 61.3572 | 122.6206 | 61.7361 | 61.7766 | 61.6628 | 61.7033
6943.0938 | 123.2529 | -61.3724 | 61.7569 | -1.7507 | -2.1147 | -2.2464 | -1.9159 | -1.4516 | -0.75226 | -1.6468 | 61.7981 | 0.2349 | 61.7202 | -0.028522 | 0.043657 | 61.4792 | 0.003143 | 61.2665 | 59.6217 | 59.2576 | 59.126 | 59.4564 | 59.9208 | 60.6201 | 59.7256 | 123.1704 | 61.6073 | 123.0925 | 61.3439 | 61.416 | 122.8516 | 61.3755 | 122.6389 | 61.7544 | 61.7949 | 61.6765 | 61.717
6944.0625 | 123.3261 | -61.3449 | 61.6974 | -1.682 | -2.0689 | -2.1777 | -1.8427 | -1.3921 | -0.7019 | -1.6056 | 61.7889 | 0.22574 | 61.711 | -0.023943 | 0.048236 | 61.4929 | 0.012299 | 61.2665 | 59.6629 | 59.276 | 59.1672 | 59.5022 | 59.9529 | 60.643 | 59.7393 | 123.1338 | 61.5706 | 123.0559 | 61.321 | 61.3931 | 122.8378 | 61.3572 | 122.6114 | 61.7407 | 61.7766 | 61.6628 | 61.6987
6945.1094 | 123.2666 | -61.4227 | 61.6608 | -1.7141 | -2.0827 | -2.2006 | -1.8518 | -1.4058 | -0.73395 | -1.6285 | 61.7889 | 0.2349 | 61.7064 | -0.033101 | 0.052814 | 61.4883 | 0.012299 | 61.2711 | 59.7086 | 59.3401 | 59.2222 | 59.5709 | 60.0169 | 60.6888 | 59.7943 | 123.2116 | 61.6576 | 123.1292 | 61.3896 | 61.4755 | 122.9111 | 61.435 | 122.6938 | 61.7361 | 61.7766 | 61.6536 | 61.6941
6946.0625 | 123.349 | -61.3586 | 61.7111 | -1.8423 | -2.2155 | -2.3196 | -1.9663 | -1.5202 | -0.85299 | -1.775 | 61.7889 | 0.22574 | 61.6973 | -0.028522 | 0.048236 | 61.4746 | 0.012299 | 61.2574 | 59.5164 | 59.1432 | 59.039 | 59.3923 | 59.8384 | 60.5057 | 59.5837 | 123.1476 | 61.5844 | 123.0559 | 61.3301 | 61.4069 | 122.8332 | 61.3709 | 122.616 | 61.7407 | 61.7766 | 61.649 | 61.685
6947.0938 | 123.2071 | -61.409 | 61.6928 | -1.6591 | -2.046 | -2.1502 | -1.7832 | -1.3325 | -0.6378 | -1.5781 | 61.7752 | 0.23032 | 61.6835 | -0.033101 | 0.048236 | 61.4883 | 0.012299 | 61.2711 | 59.7499 | 59.363 | 59.2588 | 59.6258 | 60.0765 | 60.7712 | 59.8309 | 123.1842 | 61.6393 | 123.0925 | 61.3759 | 61.4572 | 122.8973 | 61.4213 | 122.6801 | 61.7269 | 61.7629 | 61.6353 | 61.6712
6948.0625 | 123.3902 | -61.3586 | 61.6928 | -1.6683 | -2.0506 | -2.1685 | -1.7969 | -1.3325 | -0.64238 | -1.5781 | 61.7752 | 0.22574 | 61.6835 | -0.028522 | 0.048236 | 61.4792 | 0.007721 | 61.2711 | 59.6903 | 59.308 | 59.1901 | 59.5617 | 60.0261 | 60.7163 | 59.7805 | 123.1338 | 61.5844 | 123.0422 | 61.3301 | 61.4069 | 122.8378 | 61.3664 | 122.6297 | 61.7269 | 61.7675 | 61.6353 | 61.6758
6949.0781 | 123.2758 | -61.3953 | 61.7111 | -1.7232 | -2.1056 | -2.2418 | -1.8747 | -1.4058 | -0.68359 | -1.601 | 61.7889 | 0.22574 | 61.6835 | -0.03768 | 0.048236 | 61.4838 | 0.007721 | 61.2619 | 59.672 | 59.2897 | 59.1535 | 59.5205 | 59.9895 | 60.7117 | 59.7943 | 123.1842 | 61.621 | 123.0788 | 61.3576 | 61.4435 | 122.879 | 61.403 | 122.6572 | 61.7407 | 61.7812 | 61.6353 | 61.6758
6950.0625 | 123.262 | -61.3495 | 61.7706 | -1.6591 | -2.0415 | -2.1502 | -1.7969 | -1.3325 | -0.66527 | -1.5552 | 61.7752 | 0.22574 | 61.679 | -0.028522 | 0.057392 | 61.4929 | 0.021456 | 61.2757 | 59.6903 | 59.308 | 59.1993 | 59.5526 | 60.0169 | 60.6842 | 59.7943 | 123.1247 | 61.5752 | 123.0284 | 61.321 | 61.4069 | 122.8424 | 61.3709 | 122.6252 | 61.7178 | 61.7537 | 61.6216 | 61.6575
6951.0781 | 123.2849 | -61.3724 | 61.7432 | -1.4623 | -1.8492 | -1.9533 | -1.6183 | -1.1769 | -0.4684 | -1.3629 | 61.7706 | 0.22574 | 61.6698 | -0.023943 | 0.048236 | 61.5066 | 0.012299 | 61.294 | 59.9101 | 59.5232 | 59.419 | 59.754 | 60.1955 | 60.904 | 60.0095 | 123.143 | 61.5981 | 123.0422 | 61.3484 | 61.4206 | 122.879 | 61.3847 | 122.6664 | 61.7224 | 61.7583 | 61.6216 | 61.6575
6952.0625 | 123.3261 | -61.409 | 61.6653 | -1.2471 | -1.6294 | -1.7427 | -1.4169 | -0.96631 | -0.26238 | -1.134 | 61.7569 | 0.22574 | 61.6561 | -0.028522 | 0.048236 | 61.5158 | 0.007721 | 61.2894 | 60.1619 | 59.7796 | 59.6663 | 59.9921 | 60.4427 | 61.1466 | 60.275 | 123.1659 | 61.6347 | 123.0651 | 61.3805 | 61.4572 | 122.9248 | 61.4167 | 122.6984 | 61.7086 | 61.7491 | 61.6078 | 61.6483
6953.0781 | 123.2803 | -61.4044 | 61.7111 | -1.4211 | -1.7851 | -1.9213 | -1.5817 | -1.122 | -0.39515 | -1.2851 | 61.766 | 0.2349 | 61.6744 | -0.014785 | 0.052814 | 61.5112 | 0.007721 | 61.2894 | 59.9834 | 59.6194 | 59.4831 | 59.8227 | 60.2825 | 61.0093 | 60.1193 | 123.1704 | 61.6393 | 123.0788 | 61.3896 | 61.4572 | 122.9156 | 61.4121 | 122.6938 | 61.7132 | 61.7583 | 61.6216 | 61.6667
6954.0625 | 123.3856 | -61.377 | 61.6608 | -1.4943 | -1.872 | -1.9945 | -1.6504 | -1.1906 | -0.47756 | -1.3629 | 61.7706 | 0.2349 | 61.6881 | -0.03768 | 0.048236 | 61.5066 | 0.012299 | 61.2803 | 59.8826 | 59.5049 | 59.3824 | 59.7266 | 60.1863 | 60.8994 | 60.014 | 123.1476 | 61.6118 | 123.0651 | 61.3393 | 61.4252 | 122.8836 | 61.3893 | 122.6572 | 61.7224 | 61.7583 | 61.6399 | 61.6758
6955.0938 | 123.2712 | -61.4182 | 61.7523 | -1.2562 | -1.6477 | -1.7793 | -1.4123 | -0.94342 | -0.22575 | -1.1294 | 61.7706 | 0.2349 | 61.6973 | -0.019364 | 0.048236 | 61.5112 | 0.012299 | 61.3031 | 60.1619 | 59.7705 | 59.6388 | 60.0059 | 60.4747 | 61.1924 | 60.2887 | 123.1888 | 61.653 | 123.1154 | 61.3988 | 61.4664 | 122.9294 | 61.4305 | 122.7213 | 61.7224 | 61.7583 | 61.649 | 61.685
6956.0625 | 123.3261 | -61.3724 | 61.6608 | -1.302 | -1.7026 | -1.8343 | -1.481 | -0.99835 | -0.26695 | -1.1752 | 61.766 | 0.23032 | 61.6973 | -0.028522 | 0.048236 | 61.5066 | 0.007721 | 61.294 | 60.0703 | 59.6697 | 59.5381 | 59.8914 | 60.374 | 61.1054 | 60.1972 | 123.1384 | 61.6027 | 123.0696 | 61.3439 | 61.4206 | 122.879 | 61.3801 | 122.6664 | 61.7178 | 61.7583 | 61.649 | 61.6895
6957.0781 | 123.317 | -61.3861 | 61.7249 | -1.2746 | -1.6523 | -1.7702 | -1.426 | -0.95257 | -0.26238 | -1.1477 | 61.766 | 0.2349 | 61.6927 | -0.033101 | 0.039079 | 61.5158 | 0.007721 | 61.2986 | 60.1116 | 59.7338 | 59.6159 | 59.9601 | 60.4335 | 61.1237 | 60.2384 | 123.1521 | 61.621 | 123.0788 | 61.353 | 61.4252 | 122.9019 | 61.3938 | 122.6847 | 61.7269 | 61.7583 | 61.6536 | 61.685
6958.0625 | 123.3032 | -61.4456 | 61.6928 | -1.1418 | -1.5241 | -1.6466 | -1.2978 | -0.82897 | -0.15249 | -1.0104 | 61.7614 | 0.2349 | 61.6881 | -0.023943 | 0.048236 | 61.525 | 0.007721 | 61.3031 | 60.3038 | 59.9216 | 59.7991 | 60.1478 | 60.6166 | 61.2931 | 60.4352 | 123.2071 | 61.6805 | 123.1337 | 61.4217 | 61.4939 | 122.9706 | 61.4533 | 122.7488 | 61.7132 | 61.7537 | 61.6399 | 61.6804
6959.0938 | 123.2895 | -61.4273 | 61.6791 | -0.9266 | -1.2951 | -1.4085 | -1.0826 | -0.62296 | 0.021485 | -0.79065 | 61.7523 | 0.22574 | 61.6698 | -0.033101 | 0.048236 | 61.5295 | 0.007721 | 61.3077 | 60.5007 | 60.1322 | 60.0188 | 60.3447 | 60.8043 | 61.4488 | 60.6367 | 123.1796 | 61.653 | 123.0971 | 61.3942 | 61.4755 | 122.9568 | 61.435 | 122.735 | 61.7041 | 61.7446 | 61.6216 | 61.6621
6960.0625 | 123.3307 | -61.3998 | 61.6425 | -0.93118 | -1.3226 | -1.4359 | -1.0918 | -0.62296 | 0.026064 | -0.80896 | 61.7431 | 0.23032 | 61.6652 | -0.028522 | 0.048236 | 61.5387 | 0.007721 | 61.3123 | 60.4687 | 60.0773 | 59.9639 | 60.308 | 60.7769 | 61.4259 | 60.5909 | 123.143 | 61.6302 | 123.0651 | 61.3713 | 61.4481 | 122.9385 | 61.4076 | 122.7121 | 61.6949 | 61.7354 | 61.617 | 61.6575
6961.0938 | 123.2895 | -61.4044 | 61.6837 | -1.0548 | -1.4371 | -1.5504 | -1.2063 | -0.74199 | -0.074661 | -0.90968 | 61.7477 | 0.2349 | 61.6606 | -0.023943 | 0.048236 | 61.525 | 0.012299 | 61.3077 | 60.3496 | 59.9674 | 59.854 | 60.1981 | 60.6624 | 61.3298 | 60.4947 | 123.1521 | 61.6393 | 123.0651 | 61.3805 | 61.4527 | 122.9294 | 61.4167 | 122.7121 | 61.6995 | 61.7354 | 61.6124 | 61.6483
6962.0625 | 123.3078 | -61.3953 | 61.6745 | -1.0685 | -1.4691 | -1.5733 | -1.2154 | -0.74657 | -0.079239 | -0.91884 | 61.7477 | 0.22574 | 61.6561 | -0.023943 | 0.039079 | 61.5204 | 0.003143 | 61.3031 | 60.3267 | 59.9262 | 59.822 | 60.1798 | 60.6487 | 61.316 | 60.4764 | 123.143 | 61.621 | 123.0513 | 61.3713 | 61.4343 | 122.9156 | 61.3984 | 122.6984 | 61.7086 | 61.7446 | 61.617 | 61.6529
6963.0781 | 123.317 | -61.4044 | 61.6974 | -0.97238 | -1.3775 | -1.4726 | -1.1284 | -0.65043 | -0.001406 | -0.83643 | 61.7386 | 0.23032 | 61.6423 | -0.023943 | 0.052814 | 61.5341 | 0.021456 | 61.3169 | 60.432 | 60.0269 | 59.9318 | 60.276 | 60.754 | 61.403 | 60.568 | 123.143 | 61.6347 | 123.0467 | 61.3805 | 61.4572 | 122.9385 | 61.4259 | 122.7213 | 61.6857 | 61.7171 | 61.5895 | 61.6209
6964.0625 | 123.4222 | -61.3907 | 61.6333 | -0.96323 | -1.3638 | -1.468 | -1.1193 | -0.65043 | 0.012329 | -0.79522 | 61.7386 | 0.22574 | 61.6423 | -0.033101 | 0.043657 | 61.5295 | 0.012299 | 61.3077 | 60.4275 | 60.0269 | 59.9227 | 60.2714 | 60.7403 | 61.403 | 60.5955 | 123.1292 | 61.6164 | 123.033 | 61.3576 | 61.4343 | 122.9202 | 61.403 | 122.6984 | 61.6949 | 61.7263 | 61.5987 | 61.63
6965.0625 | 123.3673 | -61.4044 | 61.6837 | -0.75262 | -1.1578 | -1.2482 | -0.91324 | -0.449 | 0.2092 | -0.60294 | 61.7294 | 0.22574 | 61.6332 | -0.028522 | 0.048236 | 61.5433 | 0.012299 | 61.326 | 60.6518 | 60.2467 | 60.1562 | 60.4912 | 60.9554 | 61.6136 | 60.8015 | 123.1338 | 61.6302 | 123.0376 | 61.3759 | 61.4527 | 122.9477 | 61.4167 | 122.7305 | 61.6812 | 61.7171 | 61.5849 | 61.6209
6966.0938 | 123.3124 | -61.4182 | 61.702 | -0.84877 | -1.2539 | -1.3535 | -1.0002 | -0.52225 | 0.14052 | -0.68077 | 61.7294 | 0.23032 | 61.6515 | -0.023943 | 0.048236 | 61.5341 | 0.016878 | 61.3215 | 60.5694 | 60.1642 | 60.0646 | 60.4179 | 60.8959 | 61.5587 | 60.7374 | 123.1475 | 61.6485 | 123.0696 | 61.3942 | 61.4664 | 122.9523 | 61.435 | 122.7396 | 61.6812 | 61.7125 | 61.6032 | 61.6346
6967.0625 | 123.3444 | -61.4273 | 61.6333 | -0.75262 | -1.1532 | -1.2436 | -0.90409 | -0.43984 | 0.2092 | -0.58005 | 61.7294 | 0.23032 | 61.6698 | -0.028522 | 0.048236 | 61.5478 | 0.012299 | 61.3215 | 60.6747 | 60.2741 | 60.1837 | 60.5232 | 60.9875 | 61.6365 | 60.8473 | 123.1567 | 61.6576 | 123.0971 | 61.3988 | 61.4755 | 122.9752 | 61.4396 | 122.7488 | 61.6812 | 61.7171 | 61.6216 | 61.6575
6968.0938 | 123.2254 | -61.4639 | 61.6608 | -0.56033 | -0.96544 | -1.0422 | -0.71179 | -0.25215 | 0.39691 | -0.41066 | 61.7157 | 0.23032 | 61.6469 | -0.023943 | 0.048236 | 61.5524 | 0.012299 | 61.3306 | 60.9036 | 60.4985 | 60.4217 | 60.7521 | 61.2118 | 61.8608 | 61.0533 | 123.1796 | 61.6942 | 123.1108 | 61.44 | 61.5122 | 123.0164 | 61.4762 | 122.7945 | 61.6674 | 61.7034 | 61.5987 | 61.6346
6969.0625 | 123.2529 | -61.4319 | 61.6837 | -0.87166 | -1.2951 | -1.3673 | -1.0231 | -0.54056 | 0.085583 | -0.71282 | 61.7386 | 0.23032 | 61.6652 | -0.033101 | 0.052814 | 61.5433 | 0.003143 | 61.3077 | 60.5602 | 60.1368 | 60.0646 | 60.4088 | 60.8913 | 61.5175 | 60.7191 | 123.1704 | 61.6622 | 123.0971 | 61.3988 | 61.4847 | 122.9752 | 61.435 | 122.7396 | 61.6857 | 61.7354 | 61.6124 | 61.6621
6970.1094 | 123.2895 | -61.4044 | 61.6882 | -0.56491 | -0.94255 | -1.0147 | -0.70263 | -0.27046 | 0.3786 | -0.41066 | 61.7294 | 0.23948 | 61.6561 | -0.023943 | 0.048236 | 61.557 | 0.007721 | 61.3489 | 60.8395 | 60.4619 | 60.3897 | 60.7018 | 61.134 | 61.783 | 60.9938 | 123.1338 | 61.6439 | 123.0605 | 61.3805 | 61.4527 | 122.9614 | 61.4121 | 122.7533 | 61.6812 | 61.7217 | 61.6078 | 61.6483
6971.0625 | 123.3765 | -61.4456 | 61.5967 | -0.51455 | -0.91507 | -0.98266 | -0.66143 | -0.2201 | 0.4198 | -0.36945 | 61.7248 | 0.23032 | 61.6377 | -0.028522 | 0.043657 | 61.557 | 0.003143 | 61.3443 | 60.9311 | 60.5305 | 60.463 | 60.7842 | 61.2255 | 61.8654 | 61.0762 | 123.1704 | 61.6759 | 123.0834 | 61.4171 | 61.4893 | 123.0026 | 61.4488 | 122.79 | 61.6812 | 61.7217 | 61.5941 | 61.6346
6972.0938 | 123.2574 | -61.4227 | 61.6837 | -0.61985 | -1.025 | -1.0697 | -0.74842 | -0.3025 | 0.30077 | -0.48391 | 61.734 | 0.2349 | 61.6606 | -0.028522 | 0.048236 | 61.557 | 0.012299 | 61.3352 | 60.8029 | 60.3978 | 60.3531 | 60.6743 | 61.1202 | 61.7235 | 60.9388 | 123.1567 | 61.6576 | 123.0834 | 61.3942 | 61.471 | 122.9797 | 61.435 | 122.7579 | 61.6857 | 61.7217 | 61.6124 | 61.6483
6973.0625 | 123.317 | -61.4319 | 61.6333 | -0.56033 | -0.96544 | -1.0101 | -0.6889 | -0.25215 | 0.33282 | -0.44728 | 61.7248 | 0.2349 | 61.6469 | -0.033101 | 0.043657 | 61.557 | 0.007721 | 61.3489 | 60.8716 | 60.4664 | 60.4218 | 60.743 | 61.1797 | 61.7647 | 60.9846 | 123.1567 | 61.6668 | 123.0788 | 61.3988 | 61.4755 | 122.9889 | 61.4396 | 122.7808 | 61.6812 | 61.7171 | 61.6032 | 61.6392
6974.0781 | 123.2941 | -61.4822 | 61.6608 | -0.2902 | -0.6724 | -0.73542 | -0.41419 | -0.004937 | 0.64872 | -0.18175 | 61.6973 | 0.2349 | 61.6149 | -0.019364 | 0.052814 | 61.5662 | 0.007721 | 61.3672 | 61.192 | 60.8098 | 60.7468 | 61.068 | 61.4773 | 62.131 | 61.3005 | 123.1796 | 61.7171 | 123.0971 | 61.4629 | 61.5351 | 123.0484 | 61.49 | 122.8495 | 61.6445 | 61.6896 | 61.562 | 61.6071
6975.0625 | 123.3856 | -61.441 | 61.6287 | -0.41382 | -0.81892 | -0.87735 | -0.54239 | -0.11023 | 0.54342 | -0.2962 | 61.7065 | 0.22574 | 61.6103 | -0.033101 | 0.043657 | 61.5524 | 0.012299 | 61.3535 | 61.0272 | 60.6221 | 60.5637 | 60.8987 | 61.3308 | 61.9845 | 61.1448 | 123.1475 | 61.6668 | 123.0513 | 61.4079 | 61.4847 | 122.9935 | 61.4533 | 122.7945 | 61.6628 | 61.6942 | 61.5666 | 61.598
6976.0938 | 123.3261 | -61.4502 | 61.6699 | -0.31767 | -0.70445 | -0.76747 | -0.4325 | -0.014093 | 0.64415 | -0.19548 | 61.7019 | 0.2349 | 61.6011 | -0.028522 | 0.057392 | 61.5616 | 0.012299 | 61.3627 | 61.1325 | 60.7457 | 60.6827 | 61.0177 | 61.4361 | 62.0943 | 61.2547 | 123.1521 | 61.6851 | 123.0513 | 61.4217 | 61.5076 | 123.0118 | 61.4625 | 122.8129 | 61.6445 | 61.6896 | 61.5437 | 61.5888
6977.0625 | 123.3582 | -61.4273 | 61.6013 | -0.33141 | -0.72734 | -0.8041 | -0.47829 | -0.055294 | 0.6533 | -0.19548 | 61.7065 | 0.23032 | 61.5965 | -0.023943 | 0.048236 | 61.5707 | 0.007721 | 61.3489 | 61.0959 | 60.7 | 60.6232 | 60.949 | 61.372 | 62.0806 | 61.2318 | 123.1338 | 61.6576 | 123.0239 | 61.4034 | 61.4755 | 122.998 | 61.435 | 122.7762 | 61.6583 | 61.6988 | 61.5483 | 61.5888
6978.0938 | 123.3124 | -61.4319 | 61.6837 | -0.24442 | -0.6495 | -0.69421 | -0.37298 | 0.049999 | 0.76776 | -0.11765 | 61.6973 | 0.23032 | 61.6057 | -0.023943 | 0.057392 | 61.5799 | 0.012299 | 61.3581 | 61.1875 | 60.7824 | 60.7377 | 61.0589 | 61.4819 | 62.1996 | 61.3142 | 123.1292 | 61.6622 | 123.0376 | 61.4079 | 61.4893 | 123.0118 | 61.4442 | 122.79 | 61.64 | 61.685 | 61.5483 | 61.5934
6979.0625 | 123.3765 | -61.4685 | 61.6058 | -0.3131 | -0.69987 | -0.77663 | -0.45539 | -0.018671 | 0.67619 | -0.18633 | 61.7019 | 0.23032 | 61.6149 | -0.028522 | 0.039079 | 61.5753 | 0.012299 | 61.3443 | 61.1554 | 60.7686 | 60.6919 | 61.0131 | 61.4498 | 62.1447 | 61.2822 | 123.1704 | 61.6988 | 123.0834 | 61.44 | 61.5076 | 123.0438 | 61.4808 | 122.8129 | 61.6628 | 61.6896 | 61.5758 | 61.6026
6980.0938 | 123.2941 | -61.4456 | 61.6653 | -0.40466 | -0.81892 | -0.87278 | -0.53781 | -0.096496 | 0.60294 | -0.26416 | 61.7157 | 0.2349 | 61.6515 | -0.014785 | 0.043657 | 61.5662 | 0.007721 | 61.3535 | 61.041 | 60.6267 | 60.5728 | 60.9078 | 61.3491 | 62.0486 | 61.1815 | 123.1613 | 61.6805 | 123.0971 | 61.4308 | 61.4893 | 123.0118 | 61.4533 | 122.7991 | 61.672 | 61.7079 | 61.6078 | 61.6438
6981.0625 | 123.3719 | -61.4273 | 61.6013 | -0.51455 | -0.93339 | -0.97808 | -0.63853 | -0.2201 | 0.42438 | -0.39235 | 61.7157 | 0.2349 | 61.6515 | -0.03768 | 0.048236 | 61.557 | 0.003143 | 61.3398 | 60.9128 | 60.4939 | 60.4492 | 60.7888 | 61.2072 | 61.8517 | 61.035 | 123.143 | 61.6622 | 123.0788 | 61.3896 | 61.4755 | 122.9843 | 61.4305 | 122.7671 | 61.6674 | 61.7125 | 61.6032 | 61.6483
6982.0781 | 123.2941 | -61.4365 | 61.702 | -0.66563 | -1.0891 | -1.1338 | -0.78963 | -0.31624 | 0.31908 | -0.52969 | 61.7294 | 0.23032 | 61.6423 | -0.028522 | 0.052814 | 61.5433 | 0.007721 | 61.3398 | 60.7708 | 60.3474 | 60.3027 | 60.6468 | 61.1202 | 61.7555 | 60.9068 | 123.1659 | 61.6668 | 123.0788 | 61.4079 | 61.4893 | 122.9797 | 61.4442 | 122.7762 | 61.6766 | 61.7217 | 61.5895 | 61.6346
6983.0625 | 123.2758 | -61.4365 | 61.6333 | -0.49623 | -0.9105 | -0.95977 | -0.62022 | -0.16974 | 0.49306 | -0.36488 | 61.7202 | 0.22574 | 61.6332 | -0.033101 | 0.039079 | 61.5524 | 0.007721 | 61.3489 | 60.9402 | 60.526 | 60.4767 | 60.8162 | 61.2667 | 61.9295 | 61.0716 | 123.1567 | 61.6622 | 123.0696 | 61.4034 | 61.4755 | 122.9889 | 61.4442 | 122.7854 | 61.6812 | 61.7125 | 61.5941 | 61.6255
6984.0781 | 123.2208 | -61.4594 | 61.6608 | -0.45045 | -0.86013 | -0.90483 | -0.55612 | -0.11939 | 0.51595 | -0.33741 | 61.7111 | 0.23032 | 61.6149 | -0.023943 | 0.052814 | 61.5616 | 0.012299 | 61.3535 | 61.0089 | 60.5992 | 60.5545 | 60.9032 | 61.34 | 61.9753 | 61.1219 | 123.1704 | 61.6897 | 123.0742 | 61.4354 | 61.5122 | 123.0209 | 61.4716 | 122.8129 | 61.6583 | 61.6988 | 61.562 | 61.6026
6985.0625 | 123.381 | -61.3861 | 61.6745 | -0.36804 | -0.79603 | -0.83615 | -0.49202 | -0.041561 | 0.63499 | -0.25042 | 61.7019 | 0.22574 | 61.6057 | -0.028522 | 0.048236 | 61.5616 | 0.016878 | 61.3672 | 61.0181 | 60.5901 | 60.55 | 60.8941 | 61.3445 | 62.0211 | 61.1357 | 123.088 | 61.6118 | 122.9918 | 61.3576 | 61.4343 | 122.9477 | 61.403 | 122.7533 | 61.6537 | 61.685 | 61.5575 | 61.5888
6986.0781 | 123.317 | -61.4548 | 61.6699 | -0.36804 | -0.80976 | -0.83615 | -0.4966 | -0.050716 | 0.64415 | -0.23669 | 61.7111 | 0.23032 | 61.6194 | -0.033101 | 0.048236 | 61.5662 | 0.003143 | 61.3535 | 61.0867 | 60.645 | 60.6186 | 60.9582 | 61.4041 | 62.0989 | 61.2181 | 123.1659 | 61.6851 | 123.0742 | 61.4217 | 61.503 | 123.0209 | 61.4579 | 122.8083 | 61.6628 | 61.7079 | 61.5712 | 61.6163
6987.0625 | 123.2849 | -61.4914 | 61.6196 | -0.23069 | -0.63577 | -0.67132 | -0.34551 | 0.0912 | 0.7815 | -0.11765 | 61.7019 | 0.22574 | 61.6149 | -0.033101 | 0.048236 | 61.5707 | 0.007721 | 61.3627 | 61.2607 | 60.8556 | 60.8201 | 61.1459 | 61.5826 | 62.2729 | 61.3737 | 123.1933 | 61.7171 | 123.1063 | 61.4583 | 61.5396 | 123.0621 | 61.4991 | 122.8541 | 61.6537 | 61.6942 | 61.5666 | 61.6071
6988.0938 | 123.2437 | -61.4456 | 61.6608 | -0.26273 | -0.6724 | -0.69421 | -0.37756 | 0.063733 | 0.73114 | -0.1497 | 61.7019 | 0.23032 | 61.6377 | -0.023943 | 0.052814 | 61.5707 | 0.007721 | 61.3627 | 61.1829 | 60.7732 | 60.7514 | 61.0681 | 61.5094 | 62.1768 | 61.2959 | 123.1475 | 61.6759 | 123.0834 | 61.4217 | 61.4984 | 123.0164 | 61.4533 | 122.8083 | 61.6491 | 61.6942 | 61.5849 | 61.63
6989.0625 | 123.3582 | -61.4685 | 61.5875 | -0.084176 | -0.46635 | -0.4836 | -0.199 | 0.22854 | 0.90511 | 0.01969 | 61.6882 | 0.2349 | 61.6194 | -0.023943 | 0.048236 | 61.5753 | 0.012299 | 61.3718 | 61.3843 | 61.0022 | 60.9849 | 61.2695 | 61.697 | 62.3736 | 61.4882 | 123.1567 | 61.7034 | 123.0879 | 61.4446 | 61.5167 | 123.0438 | 61.4808 | 122.8403 | 61.64 | 61.6759 | 61.5712 | 61.6071
6990.0625 | 123.3902 | -61.4365 | 61.6104 | -0.024657 | -0.40225 | -0.41492 | -0.11659 | 0.29721 | 0.96921 | 0.07005 | 61.6882 | 0.23032 | 61.6194 | -0.028522 | 0.057392 | 61.5799 | 0.012299 | 61.3856 | 61.4118 | 61.0342 | 61.0215 | 61.3199 | 61.7337 | 62.4057 | 61.5065 | 123.1247 | 61.6668 | 123.0559 | 61.4079 | 61.4939 | 123.0164 | 61.4488 | 122.822 | 61.6308 | 61.6759 | 61.562 | 61.6071
6991.0625 | 123.3444 | -61.4868 | 61.6013 | -0.070441 | -0.46177 | -0.47444 | -0.15321 | 0.28347 | 0.95548 | 0.01969 | 61.6882 | 0.23032 | 61.6103 | -0.028522 | 0.043657 | 61.5845 | 0.007721 | 61.381 | 61.4164 | 61.025 | 61.0124 | 61.3336 | 61.7703 | 62.4423 | 61.5065 | 123.175 | 61.7171 | 123.0971 | 61.4583 | 61.5305 | 123.0713 | 61.4945 | 122.8678 | 61.6445 | 61.6805 | 61.5666 | 61.6026
6992.0625 | 123.2986 | -61.4319 | 61.6608 | -0.093333 | -0.49382 | -0.49733 | -0.17153 | 0.23769 | 0.90511 | -0.021514 | 61.6882 | 0.22574 | 61.5965 | -0.028522 | 0.052814 | 61.5936 | 0.012299 | 61.381 | 61.3386 | 60.9381 | 60.9346 | 61.2604 | 61.6696 | 62.337 | 61.4104 | 123.1201 | 61.6576 | 123.0284 | 61.4034 | 61.4847 | 123.0255 | 61.4442 | 122.8129 | 61.6354 | 61.6759 | 61.5437 | 61.5842
6993.0938 | 123.2895 | -61.4594 | 61.6516 | -0.17117 | -0.59914 | -0.60264 | -0.27226 | 0.15529 | 0.85017 | -0.071874 | 61.6928 | 0.22574 | 61.592 | -0.023943 | 0.048236 | 61.5707 | 0.012299 | 61.3718 | 61.2882 | 60.8602 | 60.8567 | 61.1871 | 61.6146 | 62.3095 | 61.3875 | 123.1521 | 61.6851 | 123.0513 | 61.4354 | 61.5076 | 123.0301 | 61.4716 | 122.8312 | 61.6445 | 61.6805 | 61.5437 | 61.5797
6994.0625 | 123.2391 | -61.4639 | 61.6653 | -0.24442 | -0.65866 | -0.66674 | -0.33636 | 0.082044 | 0.76318 | -0.15428 | 61.6973 | 0.2349 | 61.6057 | -0.033101 | 0.052814 | 61.5707 | 0.012299 | 61.3489 | 61.2195 | 60.8053 | 60.7972 | 61.1276 | 61.546 | 62.2271 | 61.3096 | 123.1613 | 61.6988 | 123.0696 | 61.4308 | 61.5167 | 123.0347 | 61.4762 | 122.8129 | 61.6445 | 61.685 | 61.5529 | 61.5934
6995.0938 | 123.2437 | -61.4914 | 61.6882 | -0.17574 | -0.57166 | -0.59348 | -0.28141 | 0.14156 | 0.80439 | -0.10392 | 61.6973 | 0.2349 | 61.624 | -0.028522 | 0.057392 | 61.5799 | 0.007721 | 61.3718 | 61.3156 | 60.9197 | 60.8979 | 61.21 | 61.633 | 62.2958 | 61.3875 | 123.1887 | 61.7263 | 123.1154 | 61.4629 | 61.5488 | 123.0713 | 61.4991 | 122.8632 | 61.64 | 61.6896 | 61.5666 | 61.6163
6996.0625 | 123.2483 | -61.5097 | 61.6425 | -0.084176 | -0.48467 | -0.48817 | -0.17611 | 0.24227 | 0.90969 | -0.007779 | 61.6928 | 0.23032 | 61.624 | -0.033101 | 0.048236 | 61.5891 | 0.012299 | 61.3627 | 61.4255 | 61.025 | 61.0215 | 61.3336 | 61.752 | 62.4194 | 61.5019 | 123.2025 | 61.74 | 123.1337 | 61.4766 | 61.5579 | 123.0988 | 61.522 | 122.8724 | 61.6445 | 61.6805 | 61.5758 | 61.6117
6997.0938 | 123.2803 | -61.4822 | 61.6516 | 0.06691 | -0.32441 | -0.31419 | -0.011281 | 0.4025 | 1.0791 | 0.13872 | 61.6882 | 0.2349 | 61.6057 | -0.023943 | 0.048236 | 61.5982 | 0.007721 | 61.3764 | 61.5491 | 61.1578 | 61.1681 | 61.471 | 61.8847 | 62.5613 | 61.621 | 123.1704 | 61.7171 | 123.0879 | 61.4583 | 61.5305 | 123.0804 | 61.49 | 122.8586 | 61.64 | 61.6805 | 61.5575 | 61.598
6998.0625 | 123.2346 | -61.4685 | 61.647 | -0.061284 | -0.46177 | -0.45612 | -0.14406 | 0.2789 | 0.94174 | 0.010533 | 61.6882 | 0.23032 | 61.592 | -0.028522 | 0.052814 | 61.5799 | 0.012299 | 61.3672 | 61.4072 | 61.0067 | 61.0124 | 61.3244 | 61.7474 | 62.4102 | 61.479 | 123.1567 | 61.6988 | 123.0605 | 61.44 | 61.5213 | 123.0484 | 61.4808 | 122.8357 | 61.6354 | 61.6759 | 61.5392 | 61.5797
6999.0781 | 123.2483 | -61.4639 | 61.6882 | -0.12996 | -0.54419 | -0.53854 | -0.23563 | 0.19649 | 0.87307 | -0.067295 | 61.6836 | 0.21658 | 61.592 | -0.028522 | 0.052814 | 61.5799 | 0.012299 | 61.3718 | 61.334 | 60.9197 | 60.9254 | 61.2283 | 61.6604 | 62.337 | 61.3966 | 123.1475 | 61.6805 | 123.0559 | 61.4354 | 61.5167 | 123.0438 | 61.4762 | 122.8357 | 61.6308 | 61.6713 | 61.5392 | 61.5797
7000.0625 | 123.2941 | -61.4822 | 61.6745 | -0.14827 | -0.53503 | -0.53854 | -0.24021 | 0.16445 | 0.83186 | -0.071874 | 61.6928 | 0.22574 | 61.6011 | -0.023943 | 0.043657 | 61.5753 | 0.012299 | 61.3581 | 61.334 | 60.9472 | 60.9437 | 61.242 | 61.6467 | 62.3141 | 61.4104 | 123.175 | 61.708 | 123.0834 | 61.4583 | 61.5259 | 123.0576 | 61.4945 | 122.8403 | 61.6491 | 61.6805 | 61.5575 | 61.5888
7001.0938 | 123.3032 | -61.4502 | 61.6928 | -0.20779 | -0.60372 | -0.59348 | -0.28141 | 0.11867 | 0.70366 | -0.19091 | 61.7019 | 0.2349 | 61.6286 | -0.019364 | 0.043657 | 61.5707 | 0.007721 | 61.3581 | 61.2424 | 60.8465 | 60.8567 | 61.1688 | 61.5689 | 62.1539 | 61.2593 | 123.1521 | 61.6851 | 123.0788 | 61.4308 | 61.4939 | 123.0209 | 61.4579 | 122.8083 | 61.6583 | 61.6942 | 61.5849 | 61.6209
7002.0625 | 123.3353 | -61.4456 | 61.6333 | -0.07502 | -0.48467 | -0.46528 | -0.15321 | 0.26059 | 0.91427 | -0.039826 | 61.6836 | 0.2349 | 61.592 | -0.028522 | 0.048236 | 61.5845 | 0.007721 | 61.3672 | 61.3706 | 60.961 | 60.9803 | 61.2924 | 61.7062 | 62.3599 | 61.4058 | 123.1292 | 61.6805 | 123.0376 | 61.4171 | 61.4939 | 123.0301 | 61.4533 | 122.8129 | 61.6354 | 61.6759 | 61.5437 | 61.5842
7003.0781 | 123.3536 | -61.441 | 61.6516 | 0.044018 | -0.35188 | -0.35082 | -0.061645 | 0.37046 | 1.0562 | 0.097519 | 61.6836 | 0.22116 | 61.5782 | -0.023943 | 0.048236 | 61.5936 | 0.021456 | 61.3764 | 61.4851 | 61.0892 | 61.0902 | 61.3794 | 61.8115 | 62.4972 | 61.5386 | 123.1247 | 61.6622 | 123.0193 | 61.4171 | 61.4893 | 123.0347 | 61.4625 | 122.8174 | 61.6354 | 61.6622 | 61.53 | 61.5568
7004.0625 | 123.2849 | -61.4594 | 61.6425 | -0.029236 | -0.42972 | -0.43323 | -0.12574 | 0.31552 | 0.9921 | 0.005955 | 61.6928 | 0.23032 | 61.6011 | -0.023943 | 0.052814 | 61.5799 | 0.012299 | 61.3718 | 61.4301 | 61.0296 | 61.0261 | 61.3336 | 61.7749 | 62.4515 | 61.4653 | 123.1521 | 61.6897 | 123.0605 | 61.4354 | 61.5122 | 123.0392 | 61.4716 | 122.8312 | 61.64 | 61.6805 | 61.5483 | 61.5888
7005.1094 | 123.2437 | -61.5005 | 61.6608 | -0.079598 | -0.50756 | -0.4836 | -0.13948 | 0.29721 | 0.96463 | -0.039826 | 61.6928 | 0.2349 | 61.6194 | -0.023943 | 0.048236 | 61.5845 | 0.012299 | 61.3718 | 61.421 | 60.993 | 61.017 | 61.3611 | 61.7978 | 62.4652 | 61.4607 | 123.1933 | 61.7354 | 123.12 | 61.4766 | 61.5488 | 123.085 | 61.5128 | 122.8724 | 61.6445 | 61.6805 | 61.5712 | 61.6071
7006.0625 | 123.317 | -61.4685 | 61.6608 | -0.065863 | -0.48924 | -0.47444 | -0.13948 | 0.31552 | 0.98295 | -0.016936 | 61.6973 | 0.23948 | 61.624 | -0.023943 | 0.043657 | 61.5845 | 0.012299 | 61.3718 | 61.4026 | 60.9793 | 60.9941 | 61.329 | 61.784 | 62.4515 | 61.4516 | 123.1659 | 61.708 | 123.0925 | 61.4446 | 61.5122 | 123.053 | 61.4808 | 122.8403 | 61.6537 | 61.685 | 61.5804 | 61.6117
7007.0938 | 123.2803 | -61.4914 | 61.6791 | 0.071489 | -0.33814 | -0.30045 | 0.011611 | 0.46202 | 1.0928 | 0.097519 | 61.679 | 0.23032 | 61.5965 | -0.028522 | 0.052814 | 61.5982 | 0.007721 | 61.3764 | 61.5629 | 61.1532 | 61.1909 | 61.503 | 61.9534 | 62.5842 | 61.5889 | 123.1704 | 61.7217 | 123.0879 | 61.4629 | 61.5442 | 123.0896 | 61.4991 | 122.8678 | 61.6262 | 61.6713 | 61.5437 | 61.5888
7008.0625 | 123.2346 | -61.4639 | 61.6928 | -0.16659 | -0.59456 | -0.5477 | -0.22647 | 0.21938 | 0.85475 | -0.13597 | 61.6882 | 0.22574 | 61.6011 | -0.023943 | 0.052814 | 61.5799 | 0.012299 | 61.3672 | 61.2973 | 60.8694 | 60.9162 | 61.2375 | 61.6833 | 62.3187 | 61.328 | 123.1521 | 61.6897 | 123.0651 | 61.44 | 61.5167 | 123.0438 | 61.4762 | 122.8312 | 61.6354 | 61.6759 | 61.5483 | 61.5888
7009.0938 | 123.4085 | -61.409 | 61.6516 | -0.084176 | -0.50756 | -0.47444 | -0.15321 | 0.29263 | 0.92801 | -0.039826 | 61.6882 | 0.23032 | 61.5965 | -0.028522 | 0.048236 | 61.5845 | 0.016878 | 61.3718 | 61.3248 | 60.9014 | 60.9346 | 61.2558 | 61.7016 | 62.337 | 61.3692 | 123.0972 | 61.6393 | 123.0055 | 61.3805 | 61.4572 | 122.9935 | 61.4259 | 122.7808 | 61.64 | 61.6713 | 61.5483 | 61.5797
7010.0625 | 123.2803 | -61.4731 | 61.6608 | 0.080646 | -0.35188 | -0.30503 | 0.01619 | 0.47117 | 1.1386 | 0.13414 | 61.6836 | 0.24405 | 61.6103 | -0.028522 | 0.048236 | 61.5891 | 0.007721 | 61.381 | 61.5537 | 61.1212 | 61.1681 | 61.4893 | 61.9443 | 62.6117 | 61.6072 | 123.1567 | 61.7171 | 123.0834 | 61.4446 | 61.5213 | 123.0621 | 61.4808 | 122.8541 | 61.6354 | 61.6759 | 61.562 | 61.6026
7011.0938 | 123.3856 | -61.4548 | 61.6196 | 0.1539 | -0.27404 | -0.23635 | 0.084867 | 0.549 | 1.2119 | 0.18908 | 61.6699 | 0.22574 | 61.5828 | -0.028522 | 0.043657 | 61.6074 | 0.012299 | 61.3901 | 61.6087 | 61.1807 | 61.2184 | 61.5396 | 62.0038 | 62.6666 | 61.6439 | 123.1246 | 61.6805 | 123.0376 | 61.4263 | 61.4984 | 123.0621 | 61.4671 | 122.8449 | 61.6262 | 61.6576 | 61.5392 | 61.5705
7012.0625 | 123.2437 | -61.4914 | 61.6745 | 0.17679 | -0.26488 | -0.24093 | 0.11692 | 0.56273 | 1.2393 | 0.22571 | 61.6653 | 0.23032 | 61.5737 | -0.028522 | 0.052814 | 61.6028 | 0.016878 | 61.3856 | 61.6682 | 61.2265 | 61.2505 | 61.6083 | 62.0541 | 62.7307 | 61.7171 | 123.1567 | 61.7217 | 123.065 | 61.4629 | 61.5442 | 123.0942 | 61.5083 | 122.8769 | 61.6125 | 61.6484 | 61.5208 | 61.5568
7013.0781 | 123.3307 | -61.4594 | 61.6425 | -0.029236 | -0.45261 | -0.43781 | -0.093694 | 0.34299 | 1.0242 | 0.028846 | 61.6836 | 0.23032 | 61.592 | -0.019364 | 0.048236 | 61.5936 | 0.012299 | 61.3764 | 61.4301 | 61.0067 | 61.0215 | 61.3657 | 61.8023 | 62.4835 | 61.4882 | 123.143 | 61.6897 | 123.0513 | 61.44 | 61.5076 | 123.053 | 61.4716 | 122.8357 | 61.6354 | 61.6713 | 61.5437 | 61.5797
7014.0625 | 123.2758 | -61.4822 | 61.6562 | 0.007391 | -0.41141 | -0.39202 | -0.066223 | 0.37046 | 1.0425 | 0.056315 | 61.6836 | 0.2349 | 61.6194 | -0.023943 | 0.057392 | 61.5891 | 0.003143 | 61.381 | 61.4896 | 61.0708 | 61.0902 | 61.416 | 61.8527 | 62.5247 | 61.5386 | 123.1659 | 61.7171 | 123.1017 | 61.4583 | 61.5396 | 123.0713 | 61.4854 | 122.8632 | 61.6262 | 61.6805 | 61.562 | 61.6163
7015.1094 | 123.3444 | -61.5005 | 61.6196 | -0.079598 | -0.51672 | -0.46528 | -0.16237 | 0.2789 | 0.96463 | -0.03067 | 61.6882 | 0.23032 | 61.6194 | -0.033101 | 0.048236 | 61.5845 | 0.007721 | 61.3718 | 61.421 | 60.9838 | 61.0353 | 61.3382 | 61.7794 | 62.4652 | 61.4699 | 123.1887 | 61.7309 | 123.12 | 61.4674 | 61.5488 | 123.085 | 61.5083 | 122.8724 | 61.64 | 61.6805 | 61.5712 | 61.6117
7016.0625 | 123.2162 | -61.4868 | 61.6837 | -0.11622 | -0.55335 | -0.52022 | -0.19442 | 0.24227 | 0.8868 | -0.090186 | 61.6928 | 0.22574 | 61.592 | -0.028522 | 0.048236 | 61.5845 | 0.012299 | 61.381 | 61.3706 | 60.9335 | 60.9666 | 61.2924 | 61.7291 | 62.3736 | 61.3966 | 123.1796 | 61.7126 | 123.0788 | 61.4583 | 61.5351 | 123.0713 | 61.4991 | 122.8678 | 61.6445 | 61.6805 | 61.5437 | 61.5797
7017.0938 | 123.381 | -61.4639 | 61.6241 | -0.056706 | -0.47551 | -0.45612 | -0.13032 | 0.30636 | 0.98295 | -0.026092 | 61.679 | 0.23032 | 61.5828 | -0.033101 | 0.048236 | 61.5936 | 0.012299 | 61.3718 | 61.4072 | 60.9884 | 61.0078 | 61.3336 | 61.7703 | 62.4469 | 61.4378 | 123.143 | 61.6942 | 123.0467 | 61.4308 | 61.5122 | 123.0576 | 61.4762 | 122.8357 | 61.6308 | 61.6667 | 61.5346 | 61.5705
7018.0625 | 123.2666 | -61.4731 | 61.6882 | 0.048597 | -0.37935 | -0.35997 | -0.029595 | 0.40708 | 1.0974 | 0.092941 | 61.679 | 0.2349 | 61.6103 | -0.028522 | 0.052814 | 61.5891 | 0.012299 | 61.381 | 61.5217 | 61.0937 | 61.1131 | 61.4435 | 61.8802 | 62.5705 | 61.566 | 123.1521 | 61.708 | 123.0834 | 61.4446 | 61.5259 | 123.0621 | 61.4854 | 122.8541 | 61.6262 | 61.6667 | 61.5575 | 61.598
7019.0938 | 123.3307 | -61.4777 | 61.6196 | 0.23631 | -0.16873 | -0.14478 | 0.1627 | 0.58562 | 1.2576 | 0.28522 | 61.6699 | 0.23032 | 61.6057 | -0.033101 | 0.039079 | 61.6074 | 0.007721 | 61.3947 | 61.714 | 61.3089 | 61.3329 | 61.6404 | 62.0633 | 62.7353 | 61.7629 | 123.1475 | 61.708 | 123.0834 | 61.4446 | 61.5167 | 123.085 | 61.4854 | 122.8724 | 61.6308 | 61.6622 | 61.5666 | 61.598
7020.0625 | 123.2666 | -61.5005 | 61.6379 | 0.076067 | -0.35646 | -0.32334 | 0.011611 | 0.45286 | 1.1386 | 0.11583 | 61.6836 | 0.23032 | 61.5828 | -0.033101 | 0.052814 | 61.5982 | 0.012299 | 61.3718 | 61.5766 | 61.1441 | 61.1772 | 61.5122 | 61.9534 | 62.6392 | 61.6164 | 123.1842 | 61.7309 | 123.0834 | 61.4674 | 61.5534 | 123.0988 | 61.5128 | 122.8724 | 61.6308 | 61.6713 | 61.53 | 61.5705
7021.0938 | 123.4085 | -61.4731 | 61.5829 | 0.218 | -0.1962 | -0.16309 | 0.14439 | 0.56731 | 1.221 | 0.23486 | 61.6699 | 0.23032 | 61.5691 | -0.028522 | 0.048236 | 61.6028 | 0.016878 | 61.3901 | 61.6911 | 61.2769 | 61.31 | 61.6175 | 62.0404 | 62.6941 | 61.7079 | 123.143 | 61.7034 | 123.0422 | 61.4446 | 61.5213 | 123.0759 | 61.49 | 122.8632 | 61.6216 | 61.653 | 61.5208 | 61.5522
7022.0625 | 123.2483 | -61.4685 | 61.6562 | 0.16306 | -0.25115 | -0.21346 | 0.071132 | 0.49864 | 1.1707 | 0.19824 | 61.679 | 0.23032 | 61.5874 | -0.028522 | 0.048236 | 61.6028 | 0.012299 | 61.3856 | 61.6316 | 61.2174 | 61.255 | 61.5396 | 61.9671 | 62.6392 | 61.6667 | 123.1475 | 61.6988 | 123.0559 | 61.44 | 61.5167 | 123.0713 | 61.4808 | 122.8541 | 61.6308 | 61.6667 | 61.5392 | 61.5751
7023.0938 | 123.3673 | -61.4639 | 61.6241 | 0.19053 | -0.2191 | -0.18599 | 0.11692 | 0.55815 | 1.2302 | 0.23944 | 61.6745 | 0.2349 | 61.6103 | -0.023943 | 0.048236 | 61.6028 | 0.007721 | 61.3856 | 61.6545 | 61.2448 | 61.2779 | 61.5808 | 62.0221 | 62.6941 | 61.7034 | 123.1384 | 61.6988 | 123.0742 | 61.44 | 61.5122 | 123.0667 | 61.4716 | 122.8495 | 61.6262 | 61.6667 | 61.562 | 61.6026
7024.0625 | 123.2574 | -61.4777 | 61.6516 | 0.14017 | -0.28778 | -0.25009 | 0.061975 | 0.51237 | 1.1844 | 0.19366 | 61.6699 | 0.23032 | 61.5782 | -0.028522 | 0.057392 | 61.5982 | 0.012299 | 61.3856 | 61.6178 | 61.1899 | 61.2276 | 61.5396 | 61.99 | 62.6621 | 61.6713 | 123.1475 | 61.708 | 123.0559 | 61.4491 | 61.5351 | 123.0759 | 61.49 | 122.8632 | 61.6125 | 61.6576 | 61.5208 | 61.5659
7025.0938 | 123.4039 | -61.496 | 61.6058 | 0.37824 | -0.035942 | -0.007421 | 0.30463 | 0.74127 | 1.3904 | 0.41799 | 61.6561 | 0.21658 | 61.5553 | -0.033101 | 0.043657 | 61.6165 | 0.012299 | 61.3947 | 61.8742 | 61.46 | 61.4886 | 61.8006 | 62.2372 | 62.8864 | 61.914 | 123.1521 | 61.7126 | 123.0513 | 61.4629 | 61.5396 | 123.1125 | 61.5083 | 122.8907 | 61.6125 | 61.6438 | 61.5117 | 61.543
7026.0625 | 123.3078 | -61.4731 | 61.647 | 0.19511 | -0.21452 | -0.17683 | 0.13981 | 0.56731 | 1.2073 | 0.23944 | 61.6745 | 0.23032 | 61.5737 | -0.023943 | 0.052814 | 61.5936 | 0.007721 | 61.3901 | 61.6682 | 61.2586 | 61.2963 | 61.6129 | 62.0404 | 62.6804 | 61.7125 | 123.1475 | 61.7034 | 123.0467 | 61.4491 | 61.5259 | 123.0667 | 61.4808 | 122.8632 | 61.6216 | 61.6667 | 61.5208 | 61.5659
7027.0781 | 123.4039 | -61.4639 | 61.5875 | 0.30499 | -0.12294 | -0.080679 | 0.25427 | 0.69091 | 1.3538 | 0.33558 | 61.6745 | 0.2349 | 61.5965 | -0.023943 | 0.039079 | 61.6119 | 0.007721 | 61.3901 | 61.7689 | 61.341 | 61.3832 | 61.7182 | 62.1548 | 62.8177 | 61.7995 | 123.1384 | 61.6988 | 123.0605 | 61.44 | 61.503 | 123.0759 | 61.4716 | 122.8541 | 61.6354 | 61.6667 | 61.5575 | 61.5888
7028.0625 | 123.2758 | -61.4822 | 61.6699 | 0.13559 | -0.29693 | -0.24551 | 0.094024 | 0.52153 | 1.1798 | 0.15704 | 61.679 | 0.2349 | 61.6057 | -0.023943 | 0.052814 | 61.5936 | 0.012299 | 61.3856 | 61.6178 | 61.1853 | 61.2367 | 61.5763 | 62.0038 | 62.6621 | 61.6393 | 123.1613 | 61.7171 | 123.0879 | 61.4583 | 61.5351 | 123.0759 | 61.4945 | 122.8678 | 61.6262 | 61.6667 | 61.5529 | 61.5934
7029.0938 | 123.3994 | -61.4319 | 61.6425 | 0.025705 | -0.41141 | -0.37829 | -0.029595 | 0.40708 | 1.0837 | 0.07005 | 61.6745 | 0.22574 | 61.592 | -0.023943 | 0.043657 | 61.5936 | 0.016878 | 61.381 | 61.4576 | 61.0205 | 61.0536 | 61.4023 | 61.839 | 62.5156 | 61.5019 | 123.1063 | 61.6576 | 123.0239 | 61.4079 | 61.4755 | 123.0255 | 61.4488 | 122.8129 | 61.6308 | 61.6576 | 61.5483 | 61.5751
7030.0625 | 123.3215 | -61.4822 | 61.6745 | 0.13559 | -0.29236 | -0.25009 | 0.07571 | 0.51237 | 1.1569 | 0.17535 | 61.679 | 0.2349 | 61.5782 | -0.033101 | 0.057392 | 61.6028 | 0.007721 | 61.3856 | 61.6178 | 61.1899 | 61.2322 | 61.5579 | 61.9946 | 62.6392 | 61.6576 | 123.1613 | 61.7171 | 123.0605 | 61.4491 | 61.5396 | 123.085 | 61.49 | 122.8678 | 61.6216 | 61.6713 | 61.5208 | 61.5705
7031.0938 | 123.2483 | -61.4777 | 61.6745 | 0.089802 | -0.35646 | -0.31419 | 0.034504 | 0.46659 | 1.1386 | 0.13414 | 61.6882 | 0.23032 | 61.6103 | -0.028522 | 0.043657 | 61.5982 | 0.012299 | 61.3856 | 61.5675 | 61.1212 | 61.1635 | 61.5122 | 61.9443 | 62.6163 | 61.6118 | 123.1659 | 61.708 | 123.0879 | 61.4491 | 61.5213 | 123.0759 | 61.49 | 122.8632 | 61.6445 | 61.6759 | 61.5666 | 61.598
7032.0625 | 123.2895 | -61.4822 | 61.6882 | 0.089802 | -0.3473 | -0.30503 | 0.029925 | 0.46202 | 1.1157 | 0.12041 | 61.679 | 0.23032 | 61.5828 | -0.033101 | 0.048236 | 61.5982 | 0.016878 | 61.381 | 61.572 | 61.1349 | 61.1772 | 61.5122 | 61.9443 | 62.598 | 61.6026 | 123.1613 | 61.7126 | 123.065 | 61.4491 | 61.5305 | 123.0804 | 61.4991 | 122.8632 | 61.6308 | 61.6622 | 61.5346 | 61.5659
7033.0781 | 123.4222 | -61.441 | 61.6104 | 0.218 | -0.20078 | -0.16767 | 0.15812 | 0.5902 | 1.2393 | 0.24402 | 61.6607 | 0.22116 | 61.5691 | -0.028522 | 0.052814 | 61.5982 | 0.003143 | 61.3901 | 61.659 | 61.2403 | 61.2734 | 61.5992 | 62.0312 | 62.6804 | 61.6851 | 123.1018 | 61.6622 | 123.0101 | 61.4125 | 61.4939 | 123.0392 | 61.4442 | 122.8312 | 61.6079 | 61.6576 | 61.5163 | 61.5659
7034.0625 | 123.3124 | -61.5005 | 61.6287 | 0.27752 | -0.1321 | -0.10357 | 0.20391 | 0.64513 | 1.3126 | 0.32185 | 61.6699 | 0.22574 | 61.5828 | -0.028522 | 0.052814 | 61.6028 | 0.012299 | 61.3901 | 61.7781 | 61.3685 | 61.397 | 61.7045 | 62.1457 | 62.8131 | 61.8224 | 123.1704 | 61.7263 | 123.0834 | 61.472 | 61.5534 | 123.1033 | 61.5128 | 122.8907 | 61.6171 | 61.6576 | 61.53 | 61.5705
7035.0938 | 123.3994 | -61.4639 | 61.615 | 0.27752 | -0.15499 | -0.11731 | 0.20849 | 0.64971 | 1.3309 | 0.29438 | 61.6699 | 0.23032 | 61.6057 | -0.023943 | 0.048236 | 61.6074 | 0.007721 | 61.3901 | 61.7414 | 61.3089 | 61.3466 | 61.6724 | 62.1136 | 62.7948 | 61.7583 | 123.1338 | 61.6942 | 123.0696 | 61.44 | 61.5122 | 123.0713 | 61.4716 | 122.8541 | 61.6216 | 61.6622 | 61.5575 | 61.598
7036.0625 | 123.3124 | -61.4594 | 61.6745 | 0.002813 | -0.44346 | -0.38744 | -0.052488 | 0.38419 | 1.0745 | 0.028846 | 61.6882 | 0.2349 | 61.6011 | -0.023943 | 0.048236 | 61.5936 | 0.012299 | 61.3718 | 61.4622 | 61.0159 | 61.0719 | 61.4069 | 61.8435 | 62.5339 | 61.4882 | 123.1475 | 61.6942 | 123.0605 | 61.4354 | 61.5076 | 123.053 | 61.4716 | 122.8312 | 61.64 | 61.6759 | 61.5529 | 61.5888
7037.0781 | 123.3673 | -61.4456 | 61.615 | 0.048597 | -0.38393 | -0.34624 | -0.006703 | 0.42539 | 1.1157 | 0.083784 | 61.6745 | 0.23032 | 61.5782 | -0.03768 | 0.043657 | 61.5891 | 0.012299 | 61.3856 | 61.4942 | 61.0617 | 61.0994 | 61.4389 | 61.871 | 62.5613 | 61.5294 | 123.1201 | 61.6759 | 123.0239 | 61.4079 | 61.4893 | 123.0347 | 61.4579 | 122.8312 | 61.6308 | 61.6622 | 61.5346 | 61.5659
7038.0625 | 123.2941 | -61.4914 | 61.6379 | 0.19511 | -0.25115 | -0.20888 | 0.11692 | 0.57189 | 1.2668 | 0.22113 | 61.6745 | 0.22574 | 61.5874 | -0.028522 | 0.048236 | 61.6028 | 0.012299 | 61.3856 | 61.6865 | 61.2402 | 61.2825 | 61.6083 | 62.0633 | 62.7582 | 61.7125 | 123.1658 | 61.7171 | 123.0788 | 61.4629 | 61.5396 | 123.0942 | 61.5037 | 122.8769 | 61.6262 | 61.6622 | 61.5392 | 61.5751
7039.0781 | 123.3536 | -61.4639 | 61.615 | 0.34619 | -0.077151 | -0.04405 | 0.27259 | 0.72296 | 1.395 | 0.36763 | 61.6745 | 0.23032 | 61.5737 | -0.023943 | 0.052814 | 61.6028 | 0.012299 | 61.3947 | 61.8101 | 61.3868 | 61.4199 | 61.7365 | 62.1869 | 62.8589 | 61.8316 | 123.1384 | 61.6942 | 123.0376 | 61.44 | 61.5167 | 123.0667 | 61.4762 | 122.8586 | 61.6216 | 61.6622 | 61.5208 | 61.5614
7040.0625 | 123.3261 | -61.5005 | 61.5829 | 0.33246 | -0.095467 | -0.053207 | 0.27716 | 0.70922 | 1.3538 | 0.34016 | 61.6561 | 0.23032 | 61.5645 | -0.028522 | 0.048236 | 61.6165 | 0.012299 | 61.3901 | 61.833 | 61.4051 | 61.4473 | 61.7777 | 62.2098 | 62.8543 | 61.8407 | 123.1567 | 61.7309 | 123.065 | 61.472 | 61.5488 | 123.1171 | 61.5128 | 122.8907 | 61.6079 | 61.6438 | 61.5163 | 61.5522
7041.0781 | 123.3994 | -61.4731 | 61.6013 | 0.2592 | -0.15957 | -0.11731 | 0.20391 | 0.6314 | 1.2805 | 0.27607 | 61.6653 | 0.22574 | 61.5782 | -0.023943 | 0.052814 | 61.6028 | 0.012299 | 61.3901 | 61.7323 | 61.3135 | 61.3558 | 61.677 | 62.1045 | 62.7536 | 61.7492 | 123.1384 | 61.6988 | 123.0513 | 61.4491 | 61.5259 | 123.0759 | 61.4854 | 122.8632 | 61.6125 | 61.653 | 61.5254 | 61.5659
7042.0625 | 123.2895 | -61.4822 | 61.6425 | 0.3874 | -0.040521 | 0.006315 | 0.32295 | 0.75958 | 1.4133 | 0.39968 | 61.6653 | 0.23948 | 61.5965 | -0.019364 | 0.052814 | 61.6165 | 0.012299 | 61.3947 | 61.8696 | 61.4417 | 61.4886 | 61.8052 | 62.2418 | 62.8956 | 61.8819 | 123.1475 | 61.7217 | 123.0788 | 61.4629 | 61.5351 | 123.0988 | 61.4945 | 122.8769 | 61.6125 | 61.653 | 61.5437 | 61.5842
7043.0938 | 123.3078 | -61.4685 | 61.647 | 0.098959 | -0.32899 | -0.30045 | 0.039082 | 0.48033 | 1.1478 | 0.10668 | 61.679 | 0.23032 | 61.5874 | -0.019364 | 0.043657 | 61.5936 | 0.012299 | 61.3856 | 61.5675 | 61.1395 | 61.1681 | 61.5076 | 61.9488 | 62.6163 | 61.5752 | 123.1475 | 61.6988 | 123.0559 | 61.4491 | 61.5122 | 123.0621 | 61.4808 | 122.8541 | 61.6354 | 61.6667 | 61.5437 | 61.5751
7044.0625 | 123.3124 | -61.4914 | 61.6333 | 0.25005 | -0.17788 | -0.14478 | 0.18559 | 0.63598 | 1.3217 | 0.26691 | 61.6653 | 0.2349 | 61.5599 | -0.023943 | 0.048236 | 61.6074 | 0.007721 | 61.381 | 61.7414 | 61.3135 | 61.3466 | 61.677 | 62.1274 | 62.8131 | 61.7583 | 123.1567 | 61.7263 | 123.0513 | 61.4675 | 61.5396 | 123.0988 | 61.4991 | 122.8724 | 61.6171 | 61.6576 | 61.5117 | 61.5522
7045.0938 | 123.3536 | -61.4777 | 61.6058 | 0.13559 | -0.27862 | -0.24093 | 0.07571 | 0.50322 | 1.1569 | 0.13414 | 61.6745 | 0.22574 | 61.5828 | -0.028522 | 0.052814 | 61.5982 | 0.007721 | 61.381 | 61.6132 | 61.199 | 61.2367 | 61.5534 | 61.9809 | 62.6346 | 61.6118 | 123.1521 | 61.7034 | 123.0605 | 61.4491 | 61.5305 | 123.0759 | 61.4854 | 122.8586 | 61.6216 | 61.6667 | 61.53 | 61.5751
7046.0625 | 123.2986 | -61.4456 | 61.6562 | 0.021127 | -0.39309 | -0.37371 | -0.047909 | 0.37961 | 1.0608 | 0.047159 | 61.6882 | 0.2349 | 61.6332 | -0.028522 | 0.048236 | 61.5982 | 0.016878 | 61.3856 | 61.4667 | 61.0525 | 61.0719 | 61.3977 | 61.8252 | 62.5064 | 61.4928 | 123.1338 | 61.6805 | 123.0788 | 61.4171 | 61.4939 | 123.0438 | 61.4625 | 122.8312 | 61.64 | 61.6713 | 61.5849 | 61.6163
7047.0938 | 123.3994 | -61.441 | 61.6196 | 0.10812 | -0.31983 | -0.28672 | 0.034504 | 0.46659 | 1.134 | 0.12499 | 61.6745 | 0.23032 | 61.5874 | -0.028522 | 0.043657 | 61.5936 | 0.007721 | 61.3764 | 61.5492 | 61.1212 | 61.1543 | 61.4755 | 61.9076 | 62.5751 | 61.566 | 123.1155 | 61.6714 | 123.0284 | 61.4125 | 61.4847 | 123.0347 | 61.4488 | 122.8174 | 61.6308 | 61.6667 | 61.5437 | 61.5797
7048.0625 | 123.3353 | -61.4731 | 61.6058 | 0.24089 | -0.17788 | -0.14936 | 0.19933 | 0.62682 | 1.2897 | 0.27149 | 61.6653 | 0.23032 | 61.5691 | -0.028522 | 0.052814 | 61.6028 | 0.007721 | 61.3901 | 61.714 | 61.2952 | 61.3237 | 61.6724 | 62.0999 | 62.7628 | 61.7446 | 123.1384 | 61.7034 | 123.0422 | 61.4446 | 61.5259 | 123.0759 | 61.4808 | 122.8632 | 61.6125 | 61.6576 | 61.5163 | 61.5614
7049.0938 | 123.3627 | -61.4594 | 61.6333 | 0.34161 | -0.090888 | -0.057786 | 0.28632 | 0.72296 | 1.3996 | 0.34474 | 61.6653 | 0.2349 | 61.592 | -0.028522 | 0.052814 | 61.6119 | 0.012299 | 61.4084 | 61.801 | 61.3685 | 61.4016 | 61.7457 | 62.1823 | 62.8589 | 61.8041 | 123.1246 | 61.6942 | 123.0513 | 61.4308 | 61.5122 | 123.0713 | 61.4716 | 122.8678 | 61.6125 | 61.653 | 61.5392 | 61.5797
7050.0625 | 123.2529 | -61.5372 | 61.6104 | 0.29583 | -0.11836 | -0.089836 | 0.25885 | 0.70007 | 1.3401 | 0.28522 | 61.6653 | 0.22574 | 61.5828 | -0.028522 | 0.048236 | 61.6028 | 0.007721 | 61.3993 | 61.833 | 61.4188 | 61.4473 | 61.796 | 62.2372 | 62.8772 | 61.8224 | 123.2025 | 61.7629 | 123.12 | 61.5086 | 61.5854 | 123.14 | 61.5449 | 122.9365 | 61.6171 | 61.6576 | 61.5346 | 61.5751
7051.0938 | 123.2483 | -61.4685 | 61.6791 | 0.26836 | -0.15499 | -0.11273 | 0.24054 | 0.66344 | 1.308 | 0.24402 | 61.6653 | 0.22574 | 61.5782 | -0.023943 | 0.052814 | 61.6074 | 0.007721 | 61.3947 | 61.7369 | 61.3135 | 61.3558 | 61.709 | 62.132 | 62.7765 | 61.7125 | 123.1338 | 61.6942 | 123.0467 | 61.4446 | 61.5213 | 123.0759 | 61.4762 | 122.8632 | 61.6125 | 61.6576 | 61.5254 | 61.5705
7052.0625 | 123.3215 | -61.4548 | 61.6425 | 0.23631 | -0.1962 | -0.14936 | 0.18559 | 0.6314 | 1.276 | 0.21197 | 61.679 | 0.2349 | 61.5965 | -0.028522 | 0.048236 | 61.6028 | 0.007721 | 61.3993 | 61.6911 | 61.2586 | 61.3054 | 61.6404 | 62.0862 | 62.7307 | 61.6667 | 123.1338 | 61.6897 | 123.0513 | 61.4263 | 61.503 | 123.0576 | 61.4625 | 122.8541 | 61.6308 | 61.6713 | 61.5483 | 61.5888
7053.0938 | 123.2712 | -61.5051 | 61.6287 | 0.27294 | -0.15957 | -0.10357 | 0.23596 | 0.66344 | 1.2989 | 0.23944 | 61.6699 | 0.22574 | 61.5737 | -0.023943 | 0.048236 | 61.6028 | 0.012299 | 61.3993 | 61.7781 | 61.3456 | 61.4016 | 61.7411 | 62.1686 | 62.804 | 61.7446 | 123.175 | 61.7309 | 123.0788 | 61.4812 | 61.5534 | 123.1079 | 61.5174 | 122.9044 | 61.6216 | 61.6576 | 61.5254 | 61.5614
7054.0625 | 123.2803 | -61.5005 | 61.6379 | 0.46981 | 0.023583 | 0.084151 | 0.42368 | 0.85114 | 1.5003 | 0.45004 | 61.6561 | 0.23032 | 61.5645 | -0.023943 | 0.057392 | 61.6074 | 0.012299 | 61.3993 | 61.9704 | 61.5241 | 61.5847 | 61.9242 | 62.3517 | 63.0009 | 61.9506 | 123.1567 | 61.7309 | 123.065 | 61.4766 | 61.5579 | 123.1079 | 61.5128 | 122.8998 | 61.5987 | 61.6438 | 61.5071 | 61.5522
7055.0938 | 123.3948 | -61.4822 | 61.5967 | 0.49728 | 0.051056 | 0.1162 | 0.4603 | 0.87861 | 1.514 | 0.45004 | 61.6607 | 0.23948 | 61.5874 | -0.023943 | 0.052814 | 61.6303 | 0.007721 | 61.4039 | 61.9795 | 61.5333 | 61.5984 | 61.9425 | 62.3608 | 62.9963 | 61.9323 | 123.143 | 61.7217 | 123.0696 | 61.4583 | 61.5351 | 123.1125 | 61.49 | 122.8861 | 61.6079 | 61.653 | 61.5346 | 61.5797
7056.0625 | 123.2941 | -61.496 | 61.6745 | 0.4927 | 0.055634 | 0.1162 | 0.4603 | 0.88319 | 1.5003 | 0.43173 | 61.6516 | 0.2349 | 61.5645 | -0.033101 | 0.057392 | 61.6211 | 0.012299 | 61.4039 | 61.9887 | 61.5516 | 61.6122 | 61.9563 | 62.3792 | 62.9963 | 61.9277 | 123.1475 | 61.7309 | 123.0605 | 61.4629 | 61.5534 | 123.1171 | 61.5083 | 122.8998 | 61.5942 | 61.6393 | 61.5071 | 61.5522
7057.0625 | 123.3261 | -61.4914 | 61.6241 | 0.41487 | -0.035942 | 0.029208 | 0.40536 | 0.83283 | 1.4408 | 0.3539 | 61.6607 | 0.2349 | 61.5691 | -0.033101 | 0.043657 | 61.6165 | 0.007721 | 61.4084 | 61.9063 | 61.4555 | 61.5206 | 61.8968 | 62.3242 | 62.9322 | 61.8453 | 123.1521 | 61.7263 | 123.0605 | 61.4583 | 61.5351 | 123.1079 | 61.4991 | 122.8998 | 61.6171 | 61.653 | 61.5254 | 61.5614
7058.0938 | 123.2986 | -61.5234 | 61.6058 | 0.59342 | 0.13805 | 0.20777 | 0.57477 | 1.0022 | 1.6193 | 0.53244 | 61.6516 | 0.23032 | 61.5874 | -0.033101 | 0.052814 | 61.6211 | 0.016878 | 61.413 | 62.1169 | 61.6615 | 61.7312 | 62.0982 | 62.5257 | 63.1428 | 62.0559 | 123.175 | 61.7538 | 123.1108 | 61.4903 | 61.5763 | 123.1445 | 61.5403 | 122.9365 | 61.5987 | 61.6347 | 61.5346 | 61.5705
7059.0625 | 123.2895 | -61.4914 | 61.6425 | 0.59342 | 0.15637 | 0.21235 | 0.55645 | 0.97475 | 1.6056 | 0.55991 | 61.6424 | 0.23032 | 61.5508 | -0.023943 | 0.043657 | 61.6303 | 0.007721 | 61.4176 | 62.0848 | 61.6478 | 61.7037 | 62.0478 | 62.4661 | 63.097 | 62.0513 | 123.1338 | 61.7217 | 123.0422 | 61.4675 | 61.5351 | 123.1216 | 61.4991 | 122.909 | 61.5987 | 61.6347 | 61.5071 | 61.543
7060.1094 | 123.3261 | -61.5005 | 61.6241 | 0.52017 | 0.078529 | 0.13452 | 0.48778 | 0.91523 | 1.5507 | 0.48208 | 61.6561 | 0.23032 | 61.5691 | -0.023943 | 0.048236 | 61.6257 | 0.012299 | 61.413 | 62.0207 | 61.5791 | 61.6351 | 61.9883 | 62.4158 | 63.0512 | 61.9826 | 123.1567 | 61.7309 | 123.0696 | 61.4766 | 61.5488 | 123.1262 | 61.5128 | 122.9136 | 61.6079 | 61.6438 | 61.5208 | 61.5568
7061.0625 | 123.317 | -61.5051 | 61.6241 | 0.60716 | 0.16095 | 0.21693 | 0.57934 | 1.0022 | 1.6468 | 0.56907 | 61.6516 | 0.23032 | 61.5782 | -0.023943 | 0.052814 | 61.6303 | 0.016878 | 61.4176 | 62.1123 | 61.6661 | 61.7221 | 62.0845 | 62.5073 | 63.1519 | 62.0742 | 123.1567 | 61.7354 | 123.0834 | 61.4812 | 61.5579 | 123.1354 | 61.522 | 122.9227 | 61.5987 | 61.6347 | 61.5254 | 61.5614
7062.0938 | 123.3856 | -61.4822 | 61.5738 | 0.60716 | 0.15179 | 0.21235 | 0.56561 | 0.99306 | 1.6193 | 0.52787 | 61.6424 | 0.22574 | 61.5462 | -0.023943 | 0.057392 | 61.6211 | 0.012299 | 61.4176 | 62.0894 | 61.634 | 61.6946 | 62.0478 | 62.4753 | 63.1016 | 62.0101 | 123.1246 | 61.708 | 123.0284 | 61.4583 | 61.5396 | 123.1033 | 61.4945 | 122.8998 | 61.585 | 61.6301 | 61.4888 | 61.5339
7063.0625 | 123.2712 | -61.5189 | 61.6516 | 0.68041 | 0.23421 | 0.29477 | 0.64802 | 1.0709 | 1.6926 | 0.61485 | 61.647 | 0.2349 | 61.5691 | -0.023943 | 0.048236 | 61.6257 | 0.007721 | 61.413 | 62.1993 | 61.7531 | 61.8136 | 62.1669 | 62.5897 | 63.2115 | 62.1337 | 123.1658 | 61.7538 | 123.0879 | 61.4949 | 61.5671 | 123.1445 | 61.5266 | 122.9319 | 61.5987 | 61.6393 | 61.5208 | 61.5614
7064.0938 | 123.2574 | -61.5143 | 61.6241 | 0.60258 | 0.15637 | 0.21235 | 0.56103 | 0.97475 | 1.6102 | 0.52329 | 61.647 | 0.22574 | 61.5599 | -0.028522 | 0.043657 | 61.6257 | 0.012299 | 61.413 | 62.1169 | 61.6707 | 61.7266 | 62.0753 | 62.489 | 63.1245 | 62.0376 | 123.1613 | 61.74 | 123.0742 | 61.4858 | 61.5579 | 123.14 | 61.5266 | 122.9273 | 61.6033 | 61.6347 | 61.5163 | 61.5476
7065.0625 | 123.262 | -61.5372 | 61.5875 | 0.67126 | 0.21589 | 0.28561 | 0.63887 | 1.0526 | 1.6697 | 0.59654 | 61.6424 | 0.22574 | 61.5416 | -0.023943 | 0.048236 | 61.6257 | 0.016878 | 61.4084 | 62.2084 | 61.7531 | 61.8228 | 62.176 | 62.5897 | 63.2069 | 62.1337 | 123.1796 | 61.7629 | 123.0788 | 61.5132 | 61.5854 | 123.1628 | 61.554 | 122.9456 | 61.5942 | 61.6255 | 61.4934 | 61.5247
7066.0781 | 123.3994 | -61.4685 | 61.5875 | 0.56595 | 0.11516 | 0.17114 | 0.52898 | 0.9427 | 1.5873 | 0.49582 | 61.6561 | 0.2349 | 61.5965 | -0.028522 | 0.052814 | 61.6211 | 0.012299 | 61.4084 | 62.0345 | 61.5837 | 61.6396 | 61.9975 | 62.4112 | 63.0558 | 61.9643 | 123.1246 | 61.7034 | 123.0651 | 61.44 | 61.5213 | 123.0896 | 61.4808 | 122.8769 | 61.6033 | 61.6438 | 61.5437 | 61.5842
7067.0625 | 123.2803 | -61.4639 | 61.6196 | 0.54306 | 0.092265 | 0.15283 | 0.50609 | 0.92439 | 1.5644 | 0.46835 | 61.6516 | 0.23032 | 61.5553 | -0.023943 | 0.048236 | 61.6211 | 0.016878 | 61.413 | 62.007 | 61.5562 | 61.6168 | 61.97 | 62.3883 | 63.0283 | 61.9323 | 123.1155 | 61.6942 | 123.0193 | 61.44 | 61.5122 | 123.085 | 61.4808 | 122.8769 | 61.6033 | 61.6347 | 61.5071 | 61.5385
7068.0781 | 123.381 | -61.4594 | 61.615 | 0.54306 | 0.106 | 0.16657 | 0.49693 | 0.91523 | 1.5415 | 0.45919 | 61.6561 | 0.22574 | 61.5599 | -0.028522 | 0.057392 | 61.6211 | 0.007721 | 61.3993 | 62.0024 | 61.5654 | 61.6259 | 61.9563 | 62.3746 | 63.0009 | 61.9185 | 123.1155 | 61.6851 | 123.0193 | 61.4308 | 61.5167 | 123.0804 | 61.4671 | 122.8586 | 61.5987 | 61.6484 | 61.5025 | 61.5522
7069.0625 | 123.2941 | -61.5005 | 61.6516 | 0.48354 | 0.046477 | 0.097887 | 0.45572 | 0.88777 | 1.5049 | 0.41799 | 61.6516 | 0.2349 | 61.5691 | -0.023943 | 0.052814 | 61.6165 | 0.012299 | 61.4084 | 61.9841 | 61.547 | 61.5984 | 61.9563 | 62.3883 | 63.0054 | 61.9185 | 123.1521 | 61.7354 | 123.0696 | 61.4766 | 61.5534 | 123.1171 | 61.5128 | 122.909 | 61.5987 | 61.6393 | 61.5163 | 61.5568
7070.0938 | 123.3582 | -61.4639 | 61.5829 | 0.37824 | -0.049678 | 0.001736 | 0.34584 | 0.76416 | 1.4042 | 0.29896 | 61.6561 | 0.23032 | 61.5782 | -0.033101 | 0.052814 | 61.6119 | 0.007721 | 61.4039 | 61.8422 | 61.4143 | 61.4657 | 61.8098 | 62.2281 | 62.8681 | 61.7629 | 123.1201 | 61.6942 | 123.0422 | 61.4308 | 61.5167 | 123.0759 | 61.4716 | 122.8678 | 61.6033 | 61.6484 | 61.5254 | 61.5705
7071.0625 | 123.2574 | -61.4868 | 61.6379 | 0.48354 | 0.051056 | 0.11162 | 0.43741 | 0.84656 | 1.4728 | 0.39968 | 61.6607 | 0.2349 | 61.5782 | -0.028522 | 0.048236 | 61.6211 | 0.012299 | 61.4222 | 61.9704 | 61.5379 | 61.5984 | 61.9242 | 62.3334 | 62.9596 | 61.8865 | 123.1475 | 61.7217 | 123.065 | 61.4583 | 61.5351 | 123.1079 | 61.4991 | 122.909 | 61.6125 | 61.6484 | 61.53 | 61.5659
7072.0938 | 123.3627 | -61.4777 | 61.5921 | 0.4927 | 0.055634 | 0.11162 | 0.4603 | 0.88319 | 1.5232 | 0.41341 | 61.6607 | 0.22574 | 61.5645 | -0.028522 | 0.052814 | 61.6211 | 0.021456 | 61.4176 | 61.9704 | 61.5333 | 61.5893 | 61.938 | 62.3608 | 63.0009 | 61.8911 | 123.1384 | 61.7034 | 123.0422 | 61.4491 | 61.5305 | 123.0988 | 61.4991 | 122.8953 | 61.6079 | 61.6393 | 61.5117 | 61.543
7073.0625 | 123.2803 | -61.496 | 61.6562 | 0.36908 | -0.063415 | -0.012 | 0.33668 | 0.75958 | 1.3996 | 0.27607 | 61.6653 | 0.22574 | 61.5828 | -0.023943 | 0.057392 | 61.6165 | 0.016878 | 61.413 | 61.8651 | 61.4326 | 61.484 | 61.8327 | 62.2556 | 62.8956 | 61.772 | 123.1613 | 61.7217 | 123.0788 | 61.472 | 61.5534 | 123.1125 | 61.5129 | 122.909 | 61.6079 | 61.6484 | 61.5254 | 61.5659
7074.0781 | 123.349 | -61.4914 | 61.6013 | 0.33703 | -0.08173 | -0.025735 | 0.30463 | 0.72754 | 1.3355 | 0.25776 | 61.6653 | 0.22574 | 61.5691 | -0.028522 | 0.039079 | 61.6119 | 0.007721 | 61.4039 | 61.8284 | 61.4097 | 61.4657 | 61.796 | 62.2189 | 62.8269 | 61.7491 | 123.1567 | 61.7171 | 123.0605 | 61.4629 | 61.5305 | 123.1033 | 61.4991 | 122.8953 | 61.6262 | 61.6576 | 61.53 | 61.5614
7075.0625 | 123.2391 | -61.5051 | 61.6196 | 0.30041 | -0.086309 | -0.048628 | 0.27259 | 0.66344 | 1.2714 | 0.20739 | 61.6699 | 0.22574 | 61.5965 | -0.023943 | 0.048236 | 61.6119 | 0.012299 | 61.4039 | 61.8055 | 61.4188 | 61.4565 | 61.7777 | 62.1686 | 62.7765 | 61.7125 | 123.175 | 61.7309 | 123.1017 | 61.4812 | 61.5534 | 123.1171 | 61.5174 | 122.909 | 61.6216 | 61.6576 | 61.5483 | 61.5842
7076.0625 | 123.262 | -61.4822 | 61.6287 | 0.45607 | 0.023583 | 0.065837 | 0.4191 | 0.83283 | 1.4637 | 0.3539 | 61.6561 | 0.23032 | 61.5691 | -0.028522 | 0.048236 | 61.6119 | 0.007721 | 61.4176 | 61.9383 | 61.5058 | 61.5481 | 61.9013 | 62.3151 | 62.9459 | 61.8361 | 123.1384 | 61.7126 | 123.0513 | 61.4537 | 61.5305 | 123.0942 | 61.49 | 122.8998 | 61.6079 | 61.6484 | 61.5208 | 61.5614
7077.0938 | 123.3719 | -61.5051 | 61.5921 | 0.69415 | 0.25252 | 0.32224 | 0.67091 | 1.0572 | 1.6697 | 0.57365 | 61.6424 | 0.23032 | 61.5691 | -0.023943 | 0.048236 | 61.6303 | 0.016878 | 61.4313 | 62.1993 | 61.7577 | 61.8274 | 62.176 | 62.5623 | 63.1748 | 62.0788 | 123.1475 | 61.7354 | 123.0742 | 61.4812 | 61.5534 | 123.1354 | 61.522 | 122.9365 | 61.5942 | 61.6255 | 61.5208 | 61.5522
7078.0625 | 123.3124 | -61.5051 | 61.615 | 0.73993 | 0.29831 | 0.36802 | 0.7167 | 1.1075 | 1.7201 | 0.63774 | 61.6378 | 0.2349 | 61.5508 | -0.028522 | 0.052814 | 61.6348 | 0.012299 | 61.4222 | 62.2451 | 61.8034 | 61.8732 | 62.2218 | 62.6126 | 63.2252 | 62.1429 | 123.143 | 61.74 | 123.0559 | 61.4766 | 61.5579 | 123.14 | 61.5174 | 122.9273 | 61.585 | 61.6255 | 61.4979 | 61.5385
7079.0781 | 123.3215 | -61.5417 | 61.5509 | 0.85897 | 0.41736 | 0.48249 | 0.84032 | 1.222 | 1.8299 | 0.74762 | 61.6516 | 0.2349 | 61.5553 | -0.033101 | 0.048236 | 61.644 | 0.007721 | 61.4359 | 62.4007 | 61.9591 | 62.0242 | 62.3821 | 62.7637 | 63.3717 | 62.2894 | 123.1933 | 61.7766 | 123.0971 | 61.5086 | 61.59 | 123.1857 | 61.5495 | 122.9777 | 61.6033 | 61.6438 | 61.5071 | 61.5476
7080.0625 | 123.2666 | -61.5234 | 61.6425 | 0.76282 | 0.33036 | 0.39092 | 0.74417 | 1.1304 | 1.7475 | 0.66063 | 61.6332 | 0.2349 | 61.5508 | -0.023943 | 0.057392 | 61.6303 | 0.003143 | 61.4313 | 62.2863 | 61.8538 | 61.9144 | 62.2676 | 62.6538 | 63.271 | 62.1841 | 123.1567 | 61.7583 | 123.0742 | 61.4995 | 61.5808 | 123.1537 | 61.5266 | 122.9548 | 61.5759 | 61.6301 | 61.4934 | 61.5476
7081.0625 | 123.2986 | -61.5234 | 61.6196 | 0.84524 | 0.4082 | 0.47333 | 0.822 | 1.2036 | 1.8254 | 0.73846 | 61.6424 | 0.2349 | 61.5691 | -0.023943 | 0.043657 | 61.6394 | 0.003143 | 61.4496 | 62.3687 | 61.9316 | 61.9968 | 62.3454 | 62.7271 | 63.3488 | 62.2619 | 123.1658 | 61.7583 | 123.0925 | 61.4995 | 61.5671 | 123.1628 | 61.5266 | 122.9731 | 61.5987 | 61.6393 | 61.5254 | 61.5659
7082.0781 | 123.3536 | -61.5005 | 61.5555 | 0.77198 | 0.33952 | 0.40923 | 0.76248 | 1.1487 | 1.7567 | 0.66521 | 61.6332 | 0.23032 | 61.5462 | -0.033101 | 0.048236 | 61.6394 | 0.007721 | 61.4359 | 62.2725 | 61.8401 | 61.9098 | 62.263 | 62.6493 | 63.2572 | 62.1658 | 123.1338 | 61.7309 | 123.0467 | 61.4674 | 61.5488 | 123.14 | 61.5083 | 122.9365 | 61.585 | 61.6255 | 61.4979 | 61.5385
7083.0625 | 123.4085 | -61.4456 | 61.615 | 0.66668 | 0.23879 | 0.30392 | 0.64802 | 1.0297 | 1.6422 | 0.54618 | 61.6516 | 0.23948 | 61.5782 | -0.028522 | 0.048236 | 61.6257 | 0.007721 | 61.4222 | 62.1123 | 61.6844 | 61.7495 | 62.0936 | 62.4753 | 63.0879 | 61.9918 | 123.0972 | 61.6851 | 123.0239 | 61.4171 | 61.4939 | 123.0713 | 61.4533 | 122.8678 | 61.6033 | 61.6438 | 61.53 | 61.5705
7084.0781 | 123.3353 | -61.4822 | 61.6058 | 0.53391 | 0.096844 | 0.16657 | 0.51525 | 0.91065 | 1.4957 | 0.39968 | 61.6516 | 0.23032 | 61.5599 | -0.033101 | 0.057392 | 61.6257 | 0.003143 | 61.4268 | 62.0161 | 61.5791 | 61.6488 | 61.9975 | 62.3929 | 62.978 | 61.8819 | 123.1338 | 61.7126 | 123.0422 | 61.4491 | 61.5396 | 123.1079 | 61.4854 | 122.909 | 61.5942 | 61.6484 | 61.5025 | 61.5568
7085.0625 | 123.2391 | -61.5189 | 61.6287 | 0.64837 | 0.21131 | 0.29935 | 0.63429 | 1.0159 | 1.5965 | 0.50498 | 61.6516 | 0.23948 | 61.5828 | -0.028522 | 0.048236 | 61.6257 | 0.007721 | 61.4268 | 62.1672 | 61.7302 | 61.8182 | 62.1531 | 62.5348 | 63.1153 | 62.0238 | 123.1704 | 61.7583 | 123.1017 | 61.4903 | 61.5671 | 123.1445 | 61.5266 | 122.9456 | 61.6033 | 61.6438 | 61.5346 | 61.5751
7086.0938 | 123.3261 | -61.5234 | 61.5463 | 0.84981 | 0.41278 | 0.49623 | 0.8449 | 1.2174 | 1.7796 | 0.69726 | 61.6287 | 0.23032 | 61.5416 | -0.033101 | 0.043657 | 61.644 | 0.012299 | 61.4359 | 62.3733 | 61.9362 | 62.0197 | 62.3683 | 62.7408 | 63.303 | 62.2207 | 123.1521 | 61.7538 | 123.065 | 61.4903 | 61.5671 | 123.1674 | 61.5357 | 122.9594 | 61.585 | 61.6164 | 61.4979 | 61.5293
7087.0625 | 123.3902 | -61.5005 | 61.5692 | 0.88644 | 0.45399 | 0.53285 | 0.89068 | 1.2494 | 1.8208 | 0.74304 | 61.6378 | 0.23948 | 61.5599 | -0.028522 | 0.052814 | 61.6348 | 0.007721 | 61.4313 | 62.387 | 61.9545 | 62.0334 | 62.3912 | 62.75 | 63.3213 | 62.2436 | 123.1384 | 61.74 | 123.0605 | 61.472 | 61.5534 | 123.1354 | 61.5083 | 122.9319 | 61.585 | 61.6301 | 61.5071 | 61.5522
7088.0781 | 123.3627 | -61.4914 | 61.5234 | 0.86355 | 0.43568 | 0.50996 | 0.87237 | 1.2311 | 1.7979 | 0.71099 | 61.6195 | 0.22116 | 61.5279 | -0.028522 | 0.052814 | 61.644 | 0.007721 | 61.4313 | 62.3549 | 61.9271 | 62.0014 | 62.3638 | 62.7225 | 63.2893 | 62.2024 | 123.1109 | 61.7126 | 123.0193 | 61.4629 | 61.5442 | 123.1354 | 61.4991 | 122.9227 | 61.5667 | 61.6118 | 61.4751 | 61.5202
7089.0625 | 123.4039 | -61.4822 | 61.5967 | 0.81319 | 0.37615 | 0.4596 | 0.81285 | 1.1808 | 1.7659 | 0.66979 | 61.6378 | 0.2349 | 61.5737 | -0.023943 | 0.048236 | 61.6394 | 0.007721 | 61.4176 | 62.2954 | 61.8584 | 61.9418 | 62.2951 | 62.663 | 63.2481 | 62.152 | 123.1201 | 61.7171 | 123.0559 | 61.4583 | 61.5305 | 123.1216 | 61.49 | 122.8998 | 61.5896 | 61.6301 | 61.5254 | 61.5659
7090.1094 | 123.3627 | -61.5234 | 61.5738 | 0.85439 | 0.41736 | 0.49165 | 0.84948 | 1.2128 | 1.7979 | 0.69268 | 61.6332 | 0.22116 | 61.537 | -0.033101 | 0.048236 | 61.6394 | 0.012299 | 61.4268 | 62.3778 | 61.9408 | 62.0151 | 62.3729 | 62.7362 | 63.3213 | 62.2161 | 123.1567 | 61.7446 | 123.0605 | 61.4903 | 61.5717 | 123.1628 | 61.5357 | 122.9502 | 61.585 | 61.6209 | 61.4888 | 61.5247
7091.0625 | 123.3536 | -61.496 | 61.5646 | 0.79487 | 0.3441 | 0.42297 | 0.79911 | 1.1853 | 1.7613 | 0.65148 | 61.647 | 0.23948 | 61.5782 | -0.033101 | 0.052814 | 61.6394 | 0.012299 | 61.4222 | 62.2908 | 61.8401 | 61.9189 | 62.2951 | 62.6813 | 63.2572 | 62.1474 | 123.143 | 61.7354 | 123.0742 | 61.4629 | 61.5488 | 123.1354 | 61.5083 | 122.9181 | 61.5942 | 61.6347 | 61.5254 | 61.5659
7092.0938 | 123.3673 | -61.5097 | 61.5875 | 0.80861 | 0.36699 | 0.45044 | 0.79911 | 1.1808 | 1.7613 | 0.65148 | 61.6332 | 0.23032 | 61.5279 | -0.028522 | 0.052814 | 61.6348 | 0.012299 | 61.4268 | 62.3183 | 61.8767 | 61.9601 | 62.3088 | 62.6905 | 63.271 | 62.1612 | 123.143 | 61.74 | 123.0376 | 61.4812 | 61.5625 | 123.1445 | 61.522 | 122.9365 | 61.5804 | 61.6209 | 61.4751 | 61.5156
7093.0625 | 123.3856 | -61.5372 | 61.5463 | 1.0604 | 0.62341 | 0.70684 | 1.0601 | 1.4188 | 1.9856 | 0.88497 | 61.6287 | 0.2349 | 61.5553 | -0.033101 | 0.043657 | 61.6531 | 0.016878 | 61.4359 | 62.5976 | 62.1606 | 62.244 | 62.5973 | 62.956 | 63.5228 | 62.4221 | 123.1658 | 61.7721 | 123.0925 | 61.5041 | 61.5808 | 123.1903 | 61.554 | 122.9731 | 61.585 | 61.6118 | 61.5117 | 61.5385
7094.0938 | 123.3536 | -61.528 | 61.5326 | 1.0604 | 0.62341 | 0.72058 | 1.0876 | 1.4463 | 1.9765 | 0.89412 | 61.6149 | 0.22574 | 61.5187 | -0.028522 | 0.043657 | 61.6531 | 0.012299 | 61.4496 | 62.5884 | 62.1514 | 62.2486 | 62.6156 | 62.9743 | 63.5045 | 62.4221 | 123.1429 | 61.7538 | 123.0467 | 61.4995 | 61.5717 | 123.1812 | 61.5403 | 122.9777 | 61.5713 | 61.6026 | 61.4751 | 61.5064
7095.0625 | 123.2483 | -61.5646 | 61.615 | 1.1062 | 0.6692 | 0.73889 | 1.1104 | 1.4921 | 2.036 | 0.9399 | 61.6195 | 0.23948 | 61.5553 | -0.023943 | 0.048236 | 61.6531 | 0.012299 | 61.4405 | 62.6708 | 62.2338 | 62.3035 | 62.6751 | 63.0567 | 63.6006 | 62.5045 | 123.1841 | 61.8041 | 123.12 | 61.5407 | 61.6129 | 123.2178 | 61.5769 | 123.0051 | 61.5713 | 61.6072 | 61.5071 | 61.543
7096.0938 | 123.3124 | -61.528 | 61.5601 | 1.1703 | 0.73788 | 0.80757 | 1.1517 | 1.5104 | 2.0909 | 1.004 | 61.6149 | 0.23032 | 61.5141 | -0.033101 | 0.048236 | 61.6577 | 0.016878 | 61.4496 | 62.6983 | 62.2659 | 62.3356 | 62.6797 | 63.0384 | 63.6189 | 62.532 | 123.1429 | 61.7583 | 123.0422 | 61.4949 | 61.5763 | 123.1857 | 61.5449 | 122.9777 | 61.5667 | 61.5981 | 61.4659 | 61.4973
7097.0625 | 123.3948 | -61.5051 | 61.5646 | 0.86813 | 0.42194 | 0.5008 | 0.85405 | 1.2128 | 1.7796 | 0.69268 | 61.6424 | 0.2349 | 61.5737 | -0.028522 | 0.052814 | 61.6394 | 0.026035 | 61.4222 | 62.3733 | 61.9271 | 62.0059 | 62.3592 | 62.7179 | 63.2847 | 62.1978 | 123.1475 | 61.74 | 123.0788 | 61.4766 | 61.5579 | 123.1445 | 61.5312 | 122.9273 | 61.5896 | 61.6164 | 61.5208 | 61.5476
7098.0781 | 123.3307 | -61.5326 | 61.5189 | 1.0192 | 0.58678 | 0.66105 | 1.0143 | 1.3685 | 1.9307 | 0.82545 | 61.6241 | 0.22116 | 61.5279 | -0.028522 | 0.043657 | 61.6486 | 0.007721 | 61.4359 | 62.5518 | 62.1194 | 62.1936 | 62.5469 | 62.901 | 63.4633 | 62.358 | 123.1567 | 61.7538 | 123.0605 | 61.5041 | 61.5763 | 123.1812 | 61.5403 | 122.9685 | 61.5804 | 61.6164 | 61.4842 | 61.5202
7099.0625 | 123.2346 | -61.5601 | 61.5555 | 1.1062 | 0.69667 | 0.77552 | 1.1288 | 1.4783 | 2.0222 | 0.91701 | 61.6195 | 0.23032 | 61.5233 | -0.028522 | 0.039079 | 61.6531 | 0.007721 | 61.4359 | 62.6663 | 62.2567 | 62.3356 | 62.6888 | 63.0384 | 63.5823 | 62.4771 | 123.1796 | 61.7904 | 123.0834 | 61.5315 | 61.5991 | 123.2132 | 61.5678 | 122.996 | 61.5804 | 61.6118 | 61.4842 | 61.5156
7100.1094 | 123.3444 | -61.5646 | 61.5372 | 1.0421 | 0.60967 | 0.70684 | 1.0738 | 1.4325 | 1.9765 | 0.83003 | 61.6332 | 0.2349 | 61.5462 | -0.028522 | 0.048236 | 61.644 | 0.012299 | 61.4268 | 62.6067 | 62.1743 | 62.2715 | 62.6385 | 62.9972 | 63.5411 | 62.3947 | 123.1979 | 61.7995 | 123.1108 | 61.5361 | 61.6129 | 123.2086 | 61.5769 | 122.9914 | 61.585 | 61.6209 | 61.4979 | 61.5339
7101.0625 | 123.4177 | -61.5097 | 61.5646 | 1.097 | 0.6692 | 0.75263 | 1.115 | 1.4646 | 2.0222 | 0.89412 | 61.6195 | 0.22574 | 61.5187 | -0.023943 | 0.048236 | 61.6623 | 0.003143 | 61.4359 | 62.6068 | 62.1789 | 62.2623 | 62.6247 | 62.9743 | 63.5319 | 62.4038 | 123.1292 | 61.7354 | 123.0284 | 61.4858 | 61.5579 | 123.172 | 61.5128 | 122.9456 | 61.5713 | 61.6164 | 61.4705 | 61.5156
7102.0938 | 123.3948 | -61.5372 | 61.5509 | 1.2893 | 0.86151 | 0.93119 | 1.289 | 1.6477 | 2.2191 | 1.0864 | 61.6241 | 0.23948 | 61.5553 | -0.019364 | 0.057392 | 61.6669 | 0.007721 | 61.4496 | 62.8265 | 62.3987 | 62.4684 | 62.8262 | 63.1849 | 63.7563 | 62.6236 | 123.1613 | 61.7766 | 123.0925 | 61.5178 | 61.5946 | 123.204 | 61.5449 | 122.9868 | 61.5667 | 61.6164 | 61.4979 | 61.5476
7103.0625 | 123.3948 | -61.5143 | 61.5646 | 1.3809 | 0.95766 | 1.0273 | 1.3852 | 1.7255 | 2.2832 | 1.1688 | 61.6012 | 0.23032 | 61.505 | -0.028522 | 0.052814 | 61.6715 | 0.016878 | 61.4725 | 62.8952 | 62.4719 | 62.5416 | 62.8994 | 63.2398 | 63.7975 | 62.6831 | 123.1155 | 61.7446 | 123.0193 | 61.4858 | 61.5671 | 123.1857 | 61.5312 | 122.9868 | 61.5484 | 61.5843 | 61.4522 | 61.4881
7104.0938 | 123.3078 | -61.5372 | 61.5784 | 1.0879 | 0.6692 | 0.74805 | 1.1104 | 1.4554 | 1.9948 | 0.8575 | 61.6287 | 0.2349 | 61.5416 | -0.033101 | 0.043657 | 61.6486 | 0.012299 | 61.4405 | 62.6251 | 62.2064 | 62.2852 | 62.6476 | 62.9926 | 63.5319 | 62.3947 | 123.1658 | 61.7721 | 123.0788 | 61.5041 | 61.5808 | 123.1857 | 61.5495 | 122.9777 | 61.585 | 61.6164 | 61.4979 | 61.5293
7105.0625 | 123.2849 | -61.528 | 61.5738 | 1.2893 | 0.87524 | 0.96324 | 1.3119 | 1.6569 | 2.1916 | 1.0635 | 61.6149 | 0.2349 | 61.5233 | -0.023943 | 0.048236 | 61.6623 | 0.012299 | 61.4588 | 62.8174 | 62.4033 | 62.4913 | 62.8399 | 63.1849 | 63.7197 | 62.5915 | 123.1429 | 61.7629 | 123.0513 | 61.5041 | 61.5763 | 123.1903 | 61.5403 | 122.9868 | 61.5667 | 61.6026 | 61.4751 | 61.511
7106.0938 | 123.4451 | -61.5005 | 61.5692 | 1.3809 | 0.96224 | 1.0502 | 1.3943 | 1.7438 | 2.2924 | 1.178 | 61.6058 | 0.23032 | 61.5096 | -0.028522 | 0.057392 | 61.6715 | 0.016878 | 61.4451 | 62.8815 | 62.4628 | 62.5508 | 62.8949 | 63.2444 | 63.7929 | 62.6785 | 123.1063 | 61.7309 | 123.0101 | 61.472 | 61.5579 | 123.172 | 61.5174 | 122.9456 | 61.5484 | 61.5889 | 61.4522 | 61.4927
7107.0625 | 123.4131 | -61.5189 | 61.5417 | 1.5686 | 1.1683 | 1.2471 | 1.6003 | 1.927 | 2.4618 | 1.3565 | 61.6012 | 0.23032 | 61.5279 | -0.028522 | 0.052814 | 61.676 | 0.007721 | 61.468 | 63.0875 | 62.6871 | 62.766 | 63.1192 | 63.4458 | 63.9806 | 62.8754 | 123.1201 | 61.7492 | 123.0467 | 61.4903 | 61.5717 | 123.1949 | 61.5266 | 122.9868 | 61.5484 | 61.5935 | 61.4751 | 61.5202
7108.0938 | 123.3261 | -61.5784 | 61.5189 | 1.5549 | 1.1317 | 1.2196 | 1.5912 | 1.9224 | 2.4572 | 1.3336 | 61.6012 | 0.22574 | 61.5004 | -0.033101 | 0.048236 | 61.6715 | 0.003143 | 61.4725 | 63.1333 | 62.71 | 62.798 | 63.1696 | 63.5008 | 64.0356 | 62.912 | 123.1796 | 61.8041 | 123.0788 | 61.5453 | 61.6266 | 123.2498 | 61.5815 | 123.0509 | 61.553 | 61.5981 | 61.4522 | 61.4973
7109.0625 | 123.3536 | -61.5601 | 61.528 | 1.2985 | 0.85693 | 0.95866 | 1.344 | 1.6889 | 2.2237 | 1.0681 | 61.6104 | 0.23032 | 61.5279 | -0.028522 | 0.048236 | 61.6669 | 0.007721 | 61.4496 | 62.8586 | 62.417 | 62.5187 | 62.904 | 63.249 | 63.7837 | 62.6282 | 123.1704 | 61.7904 | 123.0879 | 61.5315 | 61.6083 | 123.2269 | 61.5678 | 123.0097 | 61.5621 | 61.6026 | 61.4796 | 61.5202
7110.1094 | 123.3261 | -61.5417 | 61.5555 | 1.2161 | 0.78367 | 0.9083 | 1.2753 | 1.6111 | 2.1275 | 0.96279 | 61.6241 | 0.2349 | 61.5279 | -0.023943 | 0.043657 | 61.6623 | 0.012299 | 61.4451 | 62.7578 | 62.3254 | 62.45 | 62.817 | 63.1528 | 63.6693 | 62.5045 | 123.1658 | 61.7766 | 123.0696 | 61.5178 | 61.5854 | 123.204 | 61.554 | 122.9868 | 61.5804 | 61.6118 | 61.4842 | 61.5156
7111.0625 | 123.3856 | -61.496 | 61.5692 | 1.0101 | 0.5593 | 0.66105 | 1.0601 | 1.4188 | 1.9353 | 0.78424 | 61.6241 | 0.23032 | 61.5324 | -0.033101 | 0.048236 | 61.644 | 0.012299 | 61.4359 | 62.506 | 62.0553 | 62.157 | 62.5561 | 62.9148 | 63.4312 | 62.2802 | 123.1201 | 61.7263 | 123.0284 | 61.4629 | 61.5442 | 123.14 | 61.5083 | 122.9319 | 61.5759 | 61.6118 | 61.4842 | 61.5202
7112.0781 | 123.3719 | -61.5005 | 61.5051 | 1.0513 | 0.62799 | 0.72058 | 1.0921 | 1.4417 | 1.9719 | 0.81629 | 61.6241 | 0.23032 | 61.5599 | -0.028522 | 0.048236 | 61.6486 | 0.012299 | 61.4451 | 62.5518 | 62.1285 | 62.2211 | 62.5927 | 62.9422 | 63.4724 | 62.3168 | 123.1246 | 61.7309 | 123.0605 | 61.472 | 61.5488 | 123.1491 | 61.5128 | 122.9456 | 61.5759 | 61.6118 | 61.5117 | 61.5476
7113.0625 | 123.3948 | -61.5234 | 61.5372 | 1.239 | 0.81114 | 0.91746 | 1.2753 | 1.6248 | 2.1413 | 0.99026 | 61.6149 | 0.22574 | 61.5141 | -0.028522 | 0.048236 | 61.6669 | 0.007721 | 61.4451 | 62.7624 | 62.3346 | 62.4409 | 62.7987 | 63.1483 | 63.6647 | 62.5137 | 123.1384 | 61.7492 | 123.0376 | 61.4949 | 61.5717 | 123.1903 | 61.5312 | 122.9685 | 61.5667 | 61.6072 | 61.4659 | 61.5064
7114.0938 | 123.3627 | -61.5509 | 61.5509 | 1.2527 | 0.82946 | 0.92661 | 1.2844 | 1.634 | 2.1459 | 0.99942 | 61.6104 | 0.2349 | 61.5324 | -0.028522 | 0.048236 | 61.6623 | 0.016878 | 61.4542 | 62.8036 | 62.3804 | 62.4775 | 62.8353 | 63.1849 | 63.6968 | 62.5503 | 123.1613 | 61.7858 | 123.0834 | 61.5224 | 61.5991 | 123.2132 | 61.5678 | 123.0051 | 61.5621 | 61.5935 | 61.4842 | 61.5156
7115.0625 | 123.2574 | -61.5372 | 61.5967 | 1.2619 | 0.83861 | 0.94035 | 1.2844 | 1.6294 | 2.1687 | 1.0177 | 61.6149 | 0.2349 | 61.5233 | -0.023943 | 0.052814 | 61.6669 | 0.012299 | 61.4634 | 62.799 | 62.3758 | 62.4775 | 62.8216 | 63.1666 | 63.7059 | 62.5549 | 123.1521 | 61.7721 | 123.0605 | 61.5132 | 61.59 | 123.204 | 61.5495 | 123.0006 | 61.5621 | 61.6026 | 61.4705 | 61.511
7116.0938 | 123.3627 | -61.5417 | 61.5463 | 1.2115 | 0.77909 | 0.87625 | 1.2341 | 1.6019 | 2.1321 | 0.94448 | 61.6058 | 0.22574 | 61.5187 | -0.033101 | 0.043657 | 61.6577 | 0.012299 | 61.4496 | 62.7533 | 62.3208 | 62.418 | 62.7758 | 63.1437 | 63.6739 | 62.4862 | 123.1475 | 61.7675 | 123.0605 | 61.5086 | 61.5854 | 123.1995 | 61.554 | 122.9914 | 61.5621 | 61.5935 | 61.4751 | 61.5064
7117.0625 | 123.3124 | -61.5097 | 61.5784 | 1.0696 | 0.62341 | 0.73889 | 1.115 | 1.46 | 1.9856 | 0.7934 | 61.6332 | 0.2349 | 61.5599 | -0.033101 | 0.052814 | 61.6531 | 0.012299 | 61.4405 | 62.5793 | 62.1331 | 62.2486 | 62.6247 | 62.9697 | 63.4953 | 62.3031 | 123.143 | 61.7446 | 123.0696 | 61.4766 | 61.5625 | 123.1628 | 61.522 | 122.9502 | 61.5804 | 61.6209 | 61.5071 | 61.5476
7118.0781 | 123.381 | -61.5189 | 61.5143 | 1.0558 | 0.61425 | 0.73889 | 1.1013 | 1.4417 | 1.9627 | 0.78424 | 61.6149 | 0.23032 | 61.5233 | -0.033101 | 0.052814 | 61.6486 | 0.003143 | 61.4451 | 62.5747 | 62.1331 | 62.2578 | 62.6202 | 62.9606 | 63.4816 | 62.3031 | 123.1338 | 61.7492 | 123.0422 | 61.4858 | 61.5717 | 123.1674 | 61.522 | 122.9639 | 61.5621 | 61.6118 | 61.4705 | 61.5202
7119.0625 | 123.3719 | -61.5005 | 61.5601 | 1.0055 | 0.57304 | 0.68853 | 1.0326 | 1.373 | 1.8986 | 0.72931 | 61.6332 | 0.2349 | 61.5553 | -0.019364 | 0.052814 | 61.644 | 0.003143 | 61.4405 | 62.506 | 62.0736 | 62.1891 | 62.5332 | 62.8736 | 63.3992 | 62.2299 | 123.1338 | 61.7354 | 123.0559 | 61.4812 | 61.5534 | 123.1445 | 61.5037 | 122.941 | 61.5804 | 61.6301 | 61.5025 | 61.5522
7120.1094 | 123.349 | -61.5326 | 61.5097 | 1.097 | 0.68751 | 0.79383 | 1.1196 | 1.4371 | 1.9673 | 0.81171 | 61.6241 | 0.23032 | 61.537 | -0.028522 | 0.048236 | 61.6577 | 0.012299 | 61.4405 | 62.6296 | 62.2201 | 62.3264 | 62.6522 | 62.9697 | 63.4999 | 62.3443 | 123.1567 | 61.7629 | 123.0696 | 61.5041 | 61.5808 | 123.1903 | 61.5449 | 122.9731 | 61.5759 | 61.6118 | 61.4888 | 61.5247
7121.0625 | 123.3765 | -61.5372 | 61.5143 | 0.99632 | 0.56388 | 0.68395 | 1.0464 | 1.3913 | 1.8895 | 0.68353 | 61.6241 | 0.22574 | 61.5233 | -0.023943 | 0.048236 | 61.6486 | 0.012299 | 61.4359 | 62.5335 | 62.1011 | 62.2211 | 62.5835 | 62.9285 | 63.4266 | 62.2207 | 123.1613 | 61.7629 | 123.0605 | 61.5132 | 61.5854 | 123.1857 | 61.5495 | 122.9731 | 61.5759 | 61.6118 | 61.4751 | 61.511
7122.0781 | 123.3353 | -61.5509 | 61.5234 | 1.0558 | 0.64172 | 0.73889 | 1.1013 | 1.4417 | 1.9398 | 0.77051 | 61.6287 | 0.23032 | 61.5553 | -0.023943 | 0.043657 | 61.644 | -0.001436 | 61.4405 | 62.6067 | 62.1926 | 62.2898 | 62.6522 | 62.9926 | 63.4907 | 62.3214 | 123.1796 | 61.7812 | 123.1062 | 61.527 | 61.5946 | 123.1949 | 61.5495 | 122.9914 | 61.585 | 61.6301 | 61.5117 | 61.5568
7123.0625 | 123.4177 | -61.528 | 61.5738 | 1.0421 | 0.60967 | 0.73889 | 1.1013 | 1.46 | 1.9444 | 0.73389 | 61.6241 | 0.22574 | 61.5279 | -0.028522 | 0.057392 | 61.644 | 0.012299 | 61.4451 | 62.5701 | 62.1377 | 62.2669 | 62.6293 | 62.988 | 63.4724 | 62.2619 | 123.1521 | 61.7538 | 123.0559 | 61.4995 | 61.5854 | 123.172 | 61.5403 | 122.9731 | 61.5667 | 61.6118 | 61.4705 | 61.5156
7124.0938 | 123.3627 | -61.5372 | 61.5143 | 1.1749 | 0.73788 | 0.8442 | 1.2203 | 1.579 | 2.068 | 0.87581 | 61.6241 | 0.23032 | 61.537 | -0.028522 | 0.043657 | 61.6623 | 0.007721 | 61.4451 | 62.7121 | 62.275 | 62.3814 | 62.7575 | 63.1162 | 63.6052 | 62.413 | 123.1613 | 61.7675 | 123.0742 | 61.5086 | 61.5808 | 123.1995 | 61.5449 | 122.9822 | 61.5804 | 61.6164 | 61.4934 | 61.5293
7125.0625 | 123.349 | -61.5326 | 61.5463 | 1.2436 | 0.81572 | 0.94035 | 1.2936 | 1.634 | 2.1321 | 0.94448 | 61.6195 | 0.23948 | 61.5233 | -0.028522 | 0.039079 | 61.6669 | 0.012299 | 61.4451 | 62.7761 | 62.3483 | 62.4729 | 62.8262 | 63.1666 | 63.6647 | 62.4771 | 123.1521 | 61.7721 | 123.0559 | 61.5041 | 61.5717 | 123.1995 | 61.5449 | 122.9777 | 61.5804 | 61.6072 | 61.4842 | 61.511
7126.0781 | 123.3398 | -61.5555 | 61.5417 | 1.0925 | 0.65088 | 0.77552 | 1.1517 | 1.4921 | 1.981 | 0.76135 | 61.6241 | 0.2349 | 61.5187 | -0.028522 | 0.048236 | 61.6486 | 0.012299 | 61.4405 | 62.648 | 62.2064 | 62.331 | 62.7071 | 63.0475 | 63.5365 | 62.3168 | 123.1796 | 61.7904 | 123.0742 | 61.527 | 61.6037 | 123.204 | 61.5678 | 122.996 | 61.5759 | 61.6118 | 61.4705 | 61.5064
7127.0625 | 123.3902 | -61.5234 | 61.5326 | 1.1566 | 0.72872 | 0.87625 | 1.2249 | 1.5516 | 2.0039 | 0.81629 | 61.6241 | 0.23032 | 61.5553 | -0.023943 | 0.048236 | 61.6577 | 0.016878 | 61.4405 | 62.68 | 62.2522 | 62.3997 | 62.7483 | 63.075 | 63.5274 | 62.3397 | 123.1475 | 61.7538 | 123.0788 | 61.4995 | 61.5717 | 123.1812 | 61.5403 | 122.9639 | 61.5759 | 61.6072 | 61.5071 | 61.5385
7128.0781 | 123.3765 | -61.5417 | 61.5417 | 1.2527 | 0.82946 | 0.98614 | 1.3119 | 1.6385 | 2.0863 | 0.91701 | 61.6104 | 0.22574 | 61.5233 | -0.028522 | 0.048236 | 61.6577 | 0.016878 | 61.4496 | 62.7945 | 62.3712 | 62.5279 | 62.8537 | 63.1803 | 63.6281 | 62.4588 | 123.1521 | 61.7675 | 123.065 | 61.5132 | 61.59 | 123.1995 | 61.5586 | 122.9914 | 61.5621 | 61.5935 | 61.4751 | 61.5064
7129.0625 | 123.3398 | -61.528 | 61.5417 | 1.0696 | 0.63714 | 0.78926 | 1.1425 | 1.4646 | 1.9261 | 0.72931 | 61.6241 | 0.23948 | 61.5553 | -0.028522 | 0.048236 | 61.6577 | 0.012299 | 61.4451 | 62.5976 | 62.1652 | 62.3173 | 62.6705 | 62.9926 | 63.4541 | 62.2573 | 123.1521 | 61.7675 | 123.0834 | 61.4995 | 61.5763 | 123.1857 | 61.5403 | 122.9731 | 61.5759 | 61.6118 | 61.5071 | 61.543
7130.0938 | 123.4314 | -61.5005 | 61.5738 | 1.0146 | 0.59136 | 0.72973 | 1.0784 | 1.3959 | 1.8849 | 0.69268 | 61.6195 | 0.22574 | 61.5233 | -0.028522 | 0.048236 | 61.6486 | 0.016878 | 61.4359 | 62.5152 | 62.0919 | 62.2303 | 62.5789 | 62.8965 | 63.3854 | 62.1932 | 123.1201 | 61.7263 | 123.0238 | 61.472 | 61.5488 | 123.1491 | 61.5174 | 122.9365 | 61.5713 | 61.6026 | 61.4751 | 61.5064
7131.0625 | 123.381 | -61.5189 | 61.5417 | 1.2024 | 0.76993 | 0.92204 | 1.2615 | 1.5882 | 2.0818 | 0.86665 | 61.6241 | 0.2349 | 61.5462 | -0.042259 | 0.052814 | 61.6623 | 0.012299 | 61.4451 | 62.7212 | 62.2888 | 62.4409 | 62.7804 | 63.1071 | 63.6006 | 62.3855 | 123.143 | 61.7538 | 123.065 | 61.4766 | 61.5717 | 123.1812 | 61.5312 | 122.9639 | 61.5713 | 61.6118 | 61.4934 | 61.5339
7132.0781 | 123.3398 | -61.528 | 61.528 | 1.0604 | 0.61883 | 0.75263 | 1.115 | 1.4463 | 1.9536 | 0.74304 | 61.6195 | 0.22574 | 61.5187 | -0.023943 | 0.048236 | 61.6531 | 0.007721 | 61.4359 | 62.5884 | 62.1468 | 62.2806 | 62.643 | 62.9743 | 63.4816 | 62.2711 | 123.1475 | 61.7538 | 123.0467 | 61.5041 | 61.5763 | 123.1812 | 61.5357 | 122.9639 | 61.5713 | 61.6118 | 61.4705 | 61.511
7133.0625 | 123.3078 | -61.5051 | 61.5555 | 1.0467 | 0.60967 | 0.73889 | 1.0967 | 1.4188 | 1.9215 | 0.72931 | 61.6332 | 0.2349 | 61.5645 | -0.023943 | 0.043657 | 61.6531 | 0.003143 | 61.4268 | 62.5518 | 62.1148 | 62.244 | 62.6018 | 62.9239 | 63.4266 | 62.2344 | 123.1384 | 61.74 | 123.0696 | 61.4812 | 61.5488 | 123.1583 | 61.5083 | 122.9319 | 61.5896 | 61.6301 | 61.5208 | 61.5614
7134.0781 | 123.2758 | -61.5555 | 61.5692 | 1.1154 | 0.67835 | 0.83046 | 1.17 | 1.4921 | 1.9948 | 0.78882 | 61.6241 | 0.23032 | 61.5141 | -0.028522 | 0.043657 | 61.6623 | 0.003143 | 61.4359 | 62.6708 | 62.2338 | 62.3859 | 62.7255 | 63.0475 | 63.5503 | 62.3443 | 123.1796 | 61.7858 | 123.0696 | 61.527 | 61.5991 | 123.2178 | 61.5586 | 122.9914 | 61.5804 | 61.6209 | 61.4705 | 61.511
7135.0625 | 123.3765 | -61.4822 | 61.6013 | 0.94596 | 0.4952 | 0.63816 | 1.0051 | 1.3456 | 1.8437 | 0.61027 | 61.6332 | 0.22574 | 61.5691 | -0.028522 | 0.048236 | 61.644 | 0.012299 | 61.4222 | 62.4282 | 61.9774 | 62.1204 | 62.4874 | 62.8278 | 63.3259 | 62.0925 | 123.1155 | 61.708 | 123.0513 | 61.4537 | 61.5305 | 123.1262 | 61.4945 | 122.9044 | 61.585 | 61.6209 | 61.5208 | 61.5568
7136.0781 | 123.2162 | -61.5784 | 61.5463 | 0.98259 | 0.55015 | 0.68853 | 1.0509 | 1.3776 | 1.8574 | 0.63774 | 61.6287 | 0.22116 | 61.5279 | -0.023943 | 0.043657 | 61.6486 | 0.007721 | 61.4176 | 62.561 | 62.1285 | 62.2669 | 62.6293 | 62.956 | 63.4358 | 62.2161 | 123.207 | 61.7995 | 123.1062 | 61.5544 | 61.622 | 123.2269 | 61.5861 | 122.996 | 61.585 | 61.6209 | 61.4842 | 61.5202
7137.0625 | 123.3673 | -61.5463 | 61.5646 | 1.0604 | 0.62341 | 0.75721 | 1.115 | 1.4509 | 1.9581 | 0.74304 | 61.6287 | 0.2349 | 61.5599 | -0.028522 | 0.048236 | 61.6486 | 0.012299 | 61.4222 | 62.6067 | 62.1697 | 62.3035 | 62.6614 | 62.9972 | 63.5045 | 62.2894 | 123.175 | 61.7812 | 123.1062 | 61.5178 | 61.5946 | 123.1949 | 61.5586 | 122.9685 | 61.5804 | 61.6164 | 61.5117 | 61.5476
7138.0781 | 123.2162 | -61.5692 | 61.5646 | 1.0879 | 0.66004 | 0.7801 | 1.1425 | 1.4737 | 1.9902 | 0.76593 | 61.6287 | 0.23032 | 61.5233 | -0.019364 | 0.043657 | 61.6486 | 0.012299 | 61.4313 | 62.6571 | 62.2293 | 62.3493 | 62.7117 | 63.043 | 63.5594 | 62.3351 | 123.1979 | 61.7995 | 123.0925 | 61.5498 | 61.6129 | 123.2178 | 61.5815 | 123.0005 | 61.585 | 61.6164 | 61.4796 | 61.511
7139.0625 | 123.3627 | -61.5417 | 61.5463 | 1.1383 | 0.7104 | 0.8442 | 1.1883 | 1.5058 | 2.0085 | 0.80256 | 61.6195 | 0.22574 | 61.5279 | -0.028522 | 0.052814 | 61.6577 | 0.007721 | 61.4359 | 62.68 | 62.2522 | 62.3859 | 62.73 | 63.0475 | 63.5503 | 62.3443 | 123.1613 | 61.7675 | 123.0696 | 61.5132 | 61.5946 | 123.1995 | 61.5495 | 122.9777 | 61.5667 | 61.6118 | 61.4751 | 61.5202
7140.1094 | 123.381 | -61.5097 | 61.5326 | 1.1795 | 0.77451 | 0.89914 | 1.2341 | 1.547 | 2.0222 | 0.80256 | 61.6241 | 0.23032 | 61.5462 | -0.028522 | 0.048236 | 61.6623 | 0.003143 | 61.4359 | 62.6892 | 62.2842 | 62.4088 | 62.7438 | 63.0567 | 63.5319 | 62.3123 | 123.1338 | 61.74 | 123.0559 | 61.4812 | 61.5579 | 123.172 | 61.5128 | 122.9456 | 61.5759 | 61.6209 | 61.4979 | 61.543
7141.0625 | 123.349 | -61.528 | 61.5555 | 1.1978 | 0.7974 | 0.92661 | 1.2478 | 1.5561 | 2.0314 | 0.83461 | 61.6149 | 0.23032 | 61.5141 | -0.023943 | 0.048236 | 61.6669 | 0.007721 | 61.4359 | 62.7258 | 62.3254 | 62.4546 | 62.7758 | 63.0842 | 63.5594 | 62.3626 | 123.1429 | 61.7583 | 123.0422 | 61.5041 | 61.5763 | 123.1949 | 61.5357 | 122.9639 | 61.5667 | 61.6072 | 61.4659 | 61.5064
7142.0781 | 123.2803 | -61.5555 | 61.5555 | 1.1566 | 0.75619 | 0.88999 | 1.2295 | 1.5378 | 1.981 | 0.76593 | 61.6195 | 0.23032 | 61.5416 | -0.03768 | 0.052814 | 61.6531 | 0.016878 | 61.4313 | 62.712 | 62.3117 | 62.4455 | 62.785 | 63.0933 | 63.5365 | 62.3214 | 123.175 | 61.7858 | 123.0971 | 61.5178 | 61.6083 | 123.2086 | 61.5724 | 122.9868 | 61.5667 | 61.6026 | 61.4888 | 61.5247
7143.0625 | 123.3536 | -61.5601 | 61.5417 | 1.1886 | 0.78367 | 0.92661 | 1.2615 | 1.5699 | 2.0177 | 0.80256 | 61.6195 | 0.22574 | 61.5233 | -0.028522 | 0.057392 | 61.6577 | 0.007721 | 61.4359 | 62.7487 | 62.3437 | 62.4867 | 62.8216 | 63.1299 | 63.5777 | 62.3626 | 123.1796 | 61.7858 | 123.0834 | 61.5315 | 61.6175 | 123.2178 | 61.5678 | 122.996 | 61.5621 | 61.6118 | 61.4659 | 61.5156
7144.0938 | 123.3444 | -61.528 | 61.5189 | 1.2939 | 0.87066 | 1.0228 | 1.3531 | 1.666 | 2.123 | 0.92159 | 61.6058 | 0.2349 | 61.5096 | -0.028522 | 0.043657 | 61.6623 | 0.007721 | 61.4405 | 62.8219 | 62.3987 | 62.5508 | 62.8811 | 63.194 | 63.651 | 62.4496 | 123.1338 | 61.7629 | 123.0376 | 61.4995 | 61.5717 | 123.1903 | 61.5357 | 122.9685 | 61.5621 | 61.5981 | 61.4659 | 61.5018
7145.0625 | 123.2712 | -61.5463 | 61.5372 | 1.2115 | 0.78367 | 0.93577 | 1.2707 | 1.5836 | 2.0451 | 0.84834 | 61.6195 | 0.23948 | 61.5462 | -0.028522 | 0.052814 | 61.6577 | 0.003143 | 61.4405 | 62.7578 | 62.33 | 62.4821 | 62.817 | 63.1299 | 63.5915 | 62.3947 | 123.1658 | 61.7858 | 123.0925 | 61.5178 | 61.5991 | 123.204 | 61.5495 | 122.9868 | 61.5667 | 61.6164 | 61.4934 | 61.543
7146.0938 | 123.3719 | -61.5417 | 61.5326 | 1.1886 | 0.78824 | 0.92204 | 1.2524 | 1.5561 | 2.0085 | 0.80714 | 61.6149 | 0.23032 | 61.5141 | -0.023943 | 0.048236 | 61.6577 | 0.007721 | 61.4359 | 62.7304 | 62.33 | 62.4638 | 62.7941 | 63.0979 | 63.5503 | 62.3489 | 123.1567 | 61.7721 | 123.0559 | 61.5178 | 61.59 | 123.1995 | 61.5495 | 122.9777 | 61.5667 | 61.6072 | 61.4659 | 61.5064
7147.0625 | 123.3078 | -61.5234 | 61.5463 | 1.1245 | 0.72414 | 0.86709 | 1.1883 | 1.4829 | 1.9398 | 0.72015 | 61.6195 | 0.23032 | 61.5187 | -0.028522 | 0.048236 | 61.6531 | 0.012299 | 61.4313 | 62.648 | 62.2476 | 62.3905 | 62.7117 | 63.0063 | 63.4633 | 62.2436 | 123.1429 | 61.7538 | 123.0422 | 61.4949 | 61.5717 | 123.1766 | 61.5357 | 122.9548 | 61.5713 | 61.6072 | 61.4705 | 61.5064
7148.0938 | 123.3856 | -61.528 | 61.5005 | 1.2802 | 0.87524 | 1.0136 | 1.3577 | 1.6477 | 2.0909 | 0.87123 | 61.6149 | 0.2349 | 61.537 | -0.033101 | 0.048236 | 61.6623 | 0.007721 | 61.4451 | 62.8082 | 62.4033 | 62.5416 | 62.8857 | 63.1757 | 63.6189 | 62.3992 | 123.1429 | 61.7629 | 123.065 | 61.4949 | 61.5763 | 123.1903 | 61.5357 | 122.9731 | 61.5667 | 61.6072 | 61.4888 | 61.5293
7149.0625 | 123.3444 | -61.5326 | 61.5555 | 1.2115 | 0.80656 | 0.94951 | 1.2844 | 1.5928 | 2.0589 | 0.83461 | 61.6195 | 0.23032 | 61.5141 | -0.019364 | 0.048236 | 61.6623 | 0.012299 | 61.4405 | 62.7441 | 62.3392 | 62.4821 | 62.817 | 63.1254 | 63.5915 | 62.3672 | 123.1521 | 61.7629 | 123.0467 | 61.5132 | 61.5808 | 123.1949 | 61.5449 | 122.9731 | 61.5713 | 61.6072 | 61.4659 | 61.5018
7150.1094 | 123.2895 | -61.5601 | 61.5555 | 1.184 | 0.78367 | 0.92661 | 1.257 | 1.5607 | 2.0222 | 0.78882 | 61.6195 | 0.23032 | 61.5279 | -0.023943 | 0.048236 | 61.6531 | 0.007721 | 61.4451 | 62.7441 | 62.3437 | 62.4867 | 62.817 | 63.1208 | 63.5823 | 62.3489 | 123.1796 | 61.7904 | 123.0879 | 61.5361 | 61.6083 | 123.2132 | 61.5678 | 123.0051 | 61.5713 | 61.6118 | 61.4796 | 61.5202
7151.0625 | 123.3673 | -61.5372 | 61.5601 | 1.0604 | 0.63714 | 0.7801 | 1.1288 | 1.4234 | 1.8803 | 0.66521 | 61.6241 | 0.2349 | 61.5279 | -0.028522 | 0.048236 | 61.6486 | 0.012299 | 61.4359 | 62.5976 | 62.1743 | 62.3173 | 62.6659 | 62.9606 | 63.4175 | 62.2024 | 123.1613 | 61.7721 | 123.065 | 61.5086 | 61.5854 | 123.1857 | 61.5495 | 122.9731 | 61.5759 | 61.6118 | 61.4796 | 61.5156
7152.0781 | 123.2712 | -61.5509 | 61.5372 | 1.1108 | 0.69667 | 0.83962 | 1.1745 | 1.4692 | 1.9444 | 0.72473 | 61.6149 | 0.23032 | 61.5141 | -0.033101 | 0.043657 | 61.6486 | 0.016878 | 61.4405 | 62.6617 | 62.2476 | 62.3905 | 62.7255 | 63.0201 | 63.4953 | 62.2756 | 123.1658 | 61.7812 | 123.065 | 61.5178 | 61.5946 | 123.1995 | 61.5678 | 122.9914 | 61.5713 | 61.5981 | 61.4705 | 61.4973
7153.0625 | 123.3536 | -61.5417 | 61.5509 | 1.1062 | 0.69209 | 0.83504 | 1.17 | 1.4554 | 1.9261 | 0.70642 | 61.6195 | 0.23948 | 61.5462 | -0.033101 | 0.048236 | 61.644 | 0.007721 | 61.4359 | 62.648 | 62.2338 | 62.3768 | 62.7117 | 62.9972 | 63.4678 | 62.2482 | 123.1613 | 61.7812 | 123.0879 | 61.5086 | 61.59 | 123.1857 | 61.5495 | 122.9777 | 61.5713 | 61.6118 | 61.4979 | 61.5385
7154.0781 | 123.2574 | -61.5601 | 61.5509 | 1.2436 | 0.82946 | 0.97698 | 1.3211 | 1.6157 | 2.0772 | 0.83461 | 61.6104 | 0.22116 | 61.5233 | -0.028522 | 0.043657 | 61.6623 | 0.007721 | 61.4405 | 62.8036 | 62.3895 | 62.537 | 62.8811 | 63.1757 | 63.6372 | 62.3947 | 123.1704 | 61.7812 | 123.0834 | 61.5315 | 61.6037 | 123.2224 | 61.5678 | 123.0006 | 61.5667 | 61.6026 | 61.4796 | 61.5156
7155.0625 | 123.4039 | -61.528 | 61.5234 | 1.2939 | 0.87982 | 1.0365 | 1.3897 | 1.666 | 2.1138 | 0.89412 | 61.6012 | 0.22574 | 61.5096 | -0.019364 | 0.048236 | 61.6623 | 0.003143 | 61.4451 | 62.8219 | 62.4078 | 62.5645 | 62.9178 | 63.194 | 63.6418 | 62.4221 | 123.1292 | 61.7538 | 123.0376 | 61.5087 | 61.5763 | 123.1903 | 61.5312 | 122.9731 | 61.553 | 61.5981 | 61.4613 | 61.5064
7156.0781 | 123.3444 | -61.5509 | 61.5189 | 1.2573 | 0.83403 | 1.0045 | 1.3577 | 1.6294 | 2.0634 | 0.84376 | 61.6195 | 0.2349 | 61.5508 | -0.023943 | 0.048236 | 61.6623 | 0.012299 | 61.4405 | 62.8082 | 62.3849 | 62.5554 | 62.9086 | 63.1803 | 63.6143 | 62.3947 | 123.1704 | 61.7858 | 123.1017 | 61.527 | 61.5991 | 123.2132 | 61.5632 | 122.9914 | 61.5713 | 61.6072 | 61.5025 | 61.5385
7157.0625 | 123.3307 | -61.5372 | 61.5463 | 1.2252 | 0.8203 | 0.98156 | 1.3119 | 1.5882 | 2.0268 | 0.80256 | 61.6104 | 0.23032 | 61.505 | -0.028522 | 0.048236 | 61.6577 | 0.016878 | 61.4405 | 62.7624 | 62.3575 | 62.5187 | 62.8491 | 63.1254 | 63.564 | 62.3397 | 123.1475 | 61.7675 | 123.0422 | 61.5086 | 61.5854 | 123.1949 | 61.554 | 122.9777 | 61.5621 | 61.5935 | 61.4567 | 61.4881
7158.0938 | 123.2849 | -61.5875 | 61.5555 | 1.2069 | 0.7974 | 0.96324 | 1.289 | 1.5699 | 2.0085 | 0.78424 | 61.6241 | 0.24405 | 61.5553 | -0.028522 | 0.052814 | 61.6577 | 0.007721 | 61.4405 | 62.7945 | 62.3849 | 62.5508 | 62.8765 | 63.1574 | 63.596 | 62.3718 | 123.2116 | 61.8316 | 123.1429 | 61.559 | 61.6403 | 123.2452 | 61.5952 | 123.028 | 61.5713 | 61.6164 | 61.5025 | 61.5476
7159.0625 | 123.3902 | -61.4914 | 61.5509 | 1.1383 | 0.70583 | 0.89914 | 1.2432 | 1.5149 | 1.9398 | 0.70184 | 61.6195 | 0.23032 | 61.5141 | -0.023943 | 0.048236 | 61.6577 | 0.012299 | 61.4359 | 62.6296 | 62.1972 | 62.3905 | 62.7346 | 63.0063 | 63.4312 | 62.1932 | 123.1109 | 61.7217 | 123.0055 | 61.4675 | 61.5396 | 123.1491 | 61.5037 | 122.9273 | 61.5713 | 61.6072 | 61.4659 | 61.5018
7160.1094 | 123.317 | -61.5646 | 61.528 | 1.2573 | 0.83403 | 1.0273 | 1.3531 | 1.6111 | 2.0589 | 0.81171 | 61.6058 | 0.23032 | 61.5187 | -0.028522 | 0.043657 | 61.6623 | 0.003143 | 61.4405 | 62.8219 | 62.3987 | 62.592 | 62.9177 | 63.1757 | 63.6235 | 62.3764 | 123.1704 | 61.795 | 123.0834 | 61.5361 | 61.6083 | 123.2269 | 61.5678 | 123.0051 | 61.5621 | 61.6026 | 61.4751 | 61.5156
7161.0625 | 123.3124 | -61.5555 | 61.528 | 1.2436 | 0.82946 | 1.009 | 1.344 | 1.6065 | 2.0268 | 0.7934 | 61.6195 | 0.23948 | 61.5416 | -0.028522 | 0.043657 | 61.6669 | 0.012299 | 61.4451 | 62.799 | 62.3849 | 62.5645 | 62.8994 | 63.162 | 63.5823 | 62.3489 | 123.175 | 61.795 | 123.0971 | 61.527 | 61.5991 | 123.2224 | 61.5678 | 123.0006 | 61.5759 | 61.6072 | 61.4979 | 61.5293
7162.0938 | 123.4314 | -61.5417 | 61.5097 | 1.0558 | 0.6463 | 0.80757 | 1.1517 | 1.4325 | 1.8757 | 0.63316 | 61.6195 | 0.23032 | 61.5233 | -0.033101 | 0.048236 | 61.6486 | 0.012299 | 61.4313 | 62.5976 | 62.188 | 62.3493 | 62.6934 | 62.9743 | 63.4175 | 62.1749 | 123.1613 | 61.7721 | 123.065 | 61.5086 | 61.59 | 123.1903 | 61.554 | 122.9731 | 61.5713 | 61.6072 | 61.4751 | 61.511
7163.0625 | 123.3856 | -61.5509 | 61.5646 | 1.1108 | 0.70125 | 0.87625 | 1.1929 | 1.46 | 1.9078 | 0.6881 | 61.6241 | 0.2349 | 61.5508 | -0.028522 | 0.043657 | 61.6486 | 0.012299 | 61.4313 | 62.6617 | 62.2522 | 62.4272 | 62.7438 | 63.0109 | 63.4587 | 62.239 | 123.175 | 61.7858 | 123.1017 | 61.5224 | 61.5946 | 123.1995 | 61.5632 | 122.9822 | 61.5804 | 61.6118 | 61.5071 | 61.5385
7164.0781 | 123.2941 | -61.5601 | 61.5143 | 1.3077 | 0.90729 | 1.0777 | 1.3989 | 1.6614 | 2.1092 | 0.88039 | 61.6104 | 0.23032 | 61.5187 | -0.033101 | 0.043657 | 61.6669 | 0.012299 | 61.4451 | 62.8677 | 62.4674 | 62.6378 | 62.959 | 63.2215 | 63.6693 | 62.4404 | 123.1704 | 61.7904 | 123.0788 | 61.527 | 61.6037 | 123.2269 | 61.5724 | 123.0051 | 61.5667 | 61.5981 | 61.4751 | 61.5064
7165.0625 | 123.2895 | -61.5234 | 61.5692 | 1.326 | 0.93019 | 1.0914 | 1.4218 | 1.6798 | 2.1275 | 0.89412 | 61.6104 | 0.23032 | 61.5141 | -0.023943 | 0.057392 | 61.6577 | 0.012299 | 61.4542 | 62.8494 | 62.4536 | 62.6149 | 62.9452 | 63.2032 | 63.651 | 62.4176 | 123.1338 | 61.7538 | 123.0376 | 61.4995 | 61.5808 | 123.1812 | 61.5357 | 122.9777 | 61.553 | 61.5981 | 61.4567 | 61.5018
7166.0938 | 123.3215 | -61.5601 | 61.5097 | 1.4404 | 1.0401 | 1.2242 | 1.55 | 1.8034 | 2.21 | 0.97195 | 61.6058 | 0.2349 | 61.5279 | -0.028522 | 0.043657 | 61.6715 | 0.007721 | 61.4542 | 63.0005 | 62.6001 | 62.7843 | 63.11 | 63.3634 | 63.77 | 62.532 | 123.1658 | 61.795 | 123.0879 | 61.5315 | 61.6037 | 123.2315 | 61.5678 | 123.0143 | 61.5621 | 61.5981 | 61.4842 | 61.5202
7167.0625 | 123.317 | -61.5372 | 61.5326 | 1.3397 | 0.93019 | 1.1327 | 1.4676 | 1.6935 | 2.1001 | 0.86207 | 61.6104 | 0.22574 | 61.505 | -0.028522 | 0.052814 | 61.6715 | 0.007721 | 61.4496 | 62.8769 | 62.4674 | 62.6698 | 63.0047 | 63.2307 | 63.6372 | 62.3992 | 123.1475 | 61.7629 | 123.0422 | 61.5086 | 61.59 | 123.2086 | 61.5449 | 122.9868 | 61.5575 | 61.6026 | 61.4522 | 61.4973
7168.0938 | 123.4039 | -61.5509 | 61.4868 | 1.4084 | 1.008 | 1.1968 | 1.5271 | 1.7622 | 2.1642 | 0.94448 | 61.6058 | 0.23032 | 61.5324 | -0.033101 | 0.043657 | 61.6715 | 0.012299 | 61.4588 | 62.9593 | 62.5589 | 62.7477 | 63.078 | 63.3131 | 63.7151 | 62.4954 | 123.1567 | 61.7812 | 123.0834 | 61.5178 | 61.5946 | 123.2224 | 61.5632 | 123.0097 | 61.5621 | 61.5935 | 61.4888 | 61.5202
7169.0625 | 123.3627 | -61.5051 | 61.5646 | 1.1657 | 0.75619 | 0.94493 | 1.2936 | 1.5378 | 1.9444 | 0.69726 | 61.6149 | 0.22574 | 61.5279 | -0.023943 | 0.048236 | 61.6531 | 0.007721 | 61.4451 | 62.6709 | 62.2613 | 62.4501 | 62.7987 | 63.043 | 63.4495 | 62.2024 | 123.1201 | 61.7309 | 123.033 | 61.4812 | 61.5534 | 123.1583 | 61.5128 | 122.9502 | 61.5667 | 61.6072 | 61.4796 | 61.5202
7170.1094 | 123.262 | -61.5738 | 61.5463 | 1.2802 | 0.86151 | 1.0502 | 1.3943 | 1.6431 | 2.0726 | 0.82087 | 61.6104 | 0.22574 | 61.5141 | -0.023943 | 0.043657 | 61.6531 | 0.007721 | 61.4451 | 62.854 | 62.4353 | 62.624 | 62.9681 | 63.2169 | 63.6464 | 62.3947 | 123.1841 | 61.7995 | 123.0879 | 61.5498 | 61.6174 | 123.2269 | 61.5815 | 123.0189 | 61.5667 | 61.6026 | 61.4705 | 61.5064
7171.0625 | 123.3765 | -61.5097 | 61.5829 | 1.2207 | 0.80656 | 0.99987 | 1.3302 | 1.579 | 2.0177 | 0.74762 | 61.6241 | 0.2349 | 61.5508 | -0.028522 | 0.048236 | 61.6623 | 0.016878 | 61.4451 | 62.7304 | 62.3163 | 62.5096 | 62.8399 | 63.0887 | 63.5274 | 62.2573 | 123.1338 | 61.7446 | 123.0605 | 61.4812 | 61.5579 | 123.172 | 61.5266 | 122.9548 | 61.5759 | 61.6072 | 61.5025 | 61.5339
7172.0938 | 123.262 | -61.5326 | 61.5875 | 1.2207 | 0.80198 | 0.98156 | 1.3256 | 1.5836 | 2.0222 | 0.75678 | 61.6104 | 0.22116 | 61.5096 | -0.023943 | 0.048236 | 61.6623 | 0.012299 | 61.4359 | 62.7533 | 62.3346 | 62.5142 | 62.8582 | 63.1162 | 63.5548 | 62.2894 | 123.1429 | 61.7538 | 123.0422 | 61.5086 | 61.5808 | 123.1949 | 61.5449 | 122.9685 | 61.5621 | 61.5981 | 61.4613 | 61.4973
7173.0625 | 123.3994 | -61.5189 | 61.5417 | 1.2848 | 0.86608 | 1.0548 | 1.3989 | 1.6569 | 2.0863 | 0.80714 | 61.6104 | 0.2349 | 61.537 | -0.028522 | 0.048236 | 61.6623 | 0.012299 | 61.4542 | 62.8036 | 62.3849 | 62.5737 | 62.9178 | 63.1757 | 63.6052 | 62.326 | 123.1292 | 61.7538 | 123.0559 | 61.4903 | 61.5671 | 123.1812 | 61.5312 | 122.9731 | 61.5621 | 61.5981 | 61.4888 | 61.5247
7174.0781 | 123.2529 | -61.5646 | 61.5417 | 1.2985 | 0.87524 | 1.064 | 1.4172 | 1.6614 | 2.0909 | 0.82545 | 61.6058 | 0.23032 | 61.5187 | -0.028522 | 0.048236 | 61.6577 | 0.007721 | 61.4405 | 62.8631 | 62.4399 | 62.6286 | 62.9818 | 63.2261 | 63.6556 | 62.3901 | 123.1704 | 61.795 | 123.0834 | 61.5361 | 61.6129 | 123.2224 | 61.5724 | 123.0051 | 61.5575 | 61.5981 | 61.4705 | 61.511
7175.0625 | 123.4451 | -61.4868 | 61.5601 | 1.2619 | 0.84319 | 1.0411 | 1.3852 | 1.634 | 2.0543 | 0.77967 | 61.6195 | 0.23948 | 61.5187 | -0.019364 | 0.057392 | 61.6531 | 0.012299 | 61.4496 | 62.7487 | 62.33 | 62.5279 | 62.872 | 63.1208 | 63.5411 | 62.2665 | 123.1063 | 61.7263 | 123.0055 | 61.4675 | 61.5442 | 123.14 | 61.4991 | 122.9365 | 61.5621 | 61.6072 | 61.4613 | 61.5064
7176.0938 | 123.3719 | -61.5189 | 61.5372 | 1.326 | 0.89814 | 1.1006 | 1.4538 | 1.7072 | 2.1092 | 0.82545 | 61.6149 | 0.2349 | 61.537 | -0.028522 | 0.048236 | 61.6623 | 0.007721 | 61.4496 | 62.8448 | 62.417 | 62.6195 | 62.9727 | 63.2261 | 63.6281 | 62.3443 | 123.1338 | 61.7538 | 123.0559 | 61.4903 | 61.5671 | 123.1812 | 61.5266 | 122.9685 | 61.5667 | 61.6072 | 61.4888 | 61.5293
7177.0625 | 123.3582 | -61.5189 | 61.528 | 1.239 | 0.8203 | 1.0228 | 1.3623 | 1.6019 | 2.0314 | 0.75678 | 61.6104 | 0.22574 | 61.505 | -0.033101 | 0.048236 | 61.6531 | 0.012299 | 61.4359 | 62.7578 | 62.3392 | 62.5416 | 62.8811 | 63.1208 | 63.5503 | 62.2756 | 123.1292 | 61.7446 | 123.0238 | 61.4858 | 61.5671 | 123.172 | 61.5312 | 122.9548 | 61.5621 | 61.5981 | 61.4567 | 61.4927
7178.0938 | 123.3673 | -61.5463 | 61.496 | 1.3351 | 0.91187 | 1.1189 | 1.463 | 1.7026 | 2.1047 | 0.83461 | 61.6104 | 0.23032 | 61.5416 | -0.028522 | 0.039079 | 61.6669 | 0.016878 | 61.4405 | 62.8815 | 62.4582 | 62.6652 | 63.0093 | 63.249 | 63.651 | 62.3809 | 123.1567 | 61.7766 | 123.0879 | 61.5178 | 61.5854 | 123.2132 | 61.5632 | 122.9868 | 61.5713 | 61.5935 | 61.5025 | 61.5247
7179.0625 | 123.3673 | -61.5143 | 61.5417 | 1.1886 | 0.75162 | 0.98156 | 1.3211 | 1.5561 | 1.949 | 0.66521 | 61.6149 | 0.23032 | 61.5279 | -0.023943 | 0.048236 | 61.6623 | 0.012299 | 61.4359 | 62.7029 | 62.2659 | 62.4958 | 62.8353 | 63.0704 | 63.4633 | 62.1795 | 123.1292 | 61.7446 | 123.0422 | 61.4903 | 61.5625 | 123.1766 | 61.5266 | 122.9502 | 61.5667 | 61.6026 | 61.4796 | 61.5156
7180.1094 | 123.3765 | -61.5555 | 61.5097 | 1.2252 | 0.79282 | 1.0136 | 1.3577 | 1.5882 | 1.9948 | 0.72473 | 61.6104 | 0.22574 | 61.5233 | -0.028522 | 0.043657 | 61.6577 | 0.012299 | 61.4405 | 62.7807 | 62.3483 | 62.5691 | 62.9132 | 63.1437 | 63.5503 | 62.2802 | 123.1658 | 61.7812 | 123.0788 | 61.527 | 61.5991 | 123.2132 | 61.5678 | 122.996 | 61.5667 | 61.5981 | 61.4796 | 61.511
7181.0625 | 123.3765 | -61.5509 | 61.5189 | 1.4175 | 0.98513 | 1.1968 | 1.5362 | 1.7759 | 2.1916 | 0.92159 | 61.6195 | 0.23948 | 61.5324 | -0.033101 | 0.043657 | 61.6669 | 0.007721 | 61.4542 | 62.9684 | 62.536 | 62.7477 | 63.0872 | 63.3268 | 63.7425 | 62.4725 | 123.1704 | 61.7904 | 123.0834 | 61.5178 | 61.5946 | 123.2178 | 61.5586 | 123.0051 | 61.5759 | 61.6118 | 61.4888 | 61.5247
7182.0938 | 123.381 | -61.5509 | 61.5417 | 1.3534 | 0.92561 | 1.1281 | 1.4722 | 1.7026 | 2.1275 | 0.86665 | 61.6058 | 0.22574 | 61.5096 | -0.023943 | 0.048236 | 61.6577 | 0.003143 | 61.4496 | 62.9043 | 62.4765 | 62.679 | 63.0231 | 63.2535 | 63.6784 | 62.4176 | 123.1567 | 61.7766 | 123.0605 | 61.527 | 61.5991 | 123.2086 | 61.554 | 123.0006 | 61.5575 | 61.6026 | 61.4613 | 61.5064
7183.0625 | 123.3719 | -61.5097 | 61.5463 | 1.2024 | 0.76993 | 0.98156 | 1.3256 | 1.5561 | 1.9673 | 0.68353 | 61.6195 | 0.23948 | 61.5553 | -0.028522 | 0.057392 | 61.6531 | 0.007721 | 61.4405 | 62.7121 | 62.2796 | 62.4913 | 62.8353 | 63.0659 | 63.477 | 62.1932 | 123.1292 | 61.7492 | 123.065 | 61.4812 | 61.5671 | 123.1628 | 61.5174 | 122.9502 | 61.5621 | 61.6118 | 61.4979 | 61.5476
7184.0781 | 123.3582 | -61.5463 | 61.5189 | 1.3397 | 0.91187 | 1.1235 | 1.4767 | 1.6981 | 2.1138 | 0.81629 | 61.6104 | 0.2349 | 61.5096 | -0.028522 | 0.052814 | 61.6715 | 0.012299 | 61.4451 | 62.886 | 62.4582 | 62.6698 | 63.0231 | 63.2444 | 63.6601 | 62.3626 | 123.1567 | 61.7812 | 123.0559 | 61.5178 | 61.5991 | 123.2178 | 61.5586 | 122.9914 | 61.5575 | 61.5981 | 61.4567 | 61.4973
7185.0625 | 123.3948 | -61.4868 | 61.5417 | 1.1611 | 0.73788 | 0.96324 | 1.3073 | 1.5195 | 1.9078 | 0.63774 | 61.6241 | 0.23032 | 61.5233 | -0.028522 | 0.052814 | 61.6577 | 0.012299 | 61.4313 | 62.648 | 62.2247 | 62.4501 | 62.7941 | 63.0063 | 63.3946 | 62.1246 | 123.1109 | 61.7171 | 123.0101 | 61.4583 | 61.5396 | 123.1445 | 61.4991 | 122.9182 | 61.5713 | 61.6118 | 61.4705 | 61.511
7186.0938 | 123.2574 | -61.5646 | 61.5692 | 1.0375 | 0.62799 | 0.84878 | 1.1745 | 1.3913 | 1.775 | 0.50955 | 61.6287 | 0.23032 | 61.5553 | -0.023943 | 0.048236 | 61.644 | 0.007721 | 61.4405 | 62.6022 | 62.1926 | 62.4134 | 62.7392 | 62.956 | 63.3396 | 62.0742 | 123.1933 | 61.795 | 123.12 | 61.5407 | 61.6129 | 123.2086 | 61.5724 | 123.0051 | 61.5804 | 61.6209 | 61.5071 | 61.5476
7187.0625 | 123.3856 | -61.5189 | 61.5555 | 1.1062 | 0.68751 | 0.91288 | 1.2386 | 1.4554 | 1.8437 | 0.58281 | 61.6195 | 0.23032 | 61.5279 | -0.028522 | 0.048236 | 61.6531 | 0.012299 | 61.4405 | 62.6251 | 62.2064 | 62.4317 | 62.7575 | 62.9743 | 63.3625 | 62.1017 | 123.1384 | 61.7492 | 123.0467 | 61.4903 | 61.5671 | 123.172 | 61.5312 | 122.9594 | 61.5713 | 61.6072 | 61.4796 | 61.5156
7188.0938 | 123.3948 | -61.5051 | 61.5234 | 1.2161 | 0.7974 | 1.0319 | 1.3531 | 1.5699 | 1.9353 | 0.69726 | 61.6195 | 0.23032 | 61.5553 | -0.033101 | 0.048236 | 61.6577 | 0.007721 | 61.4588 | 62.7212 | 62.3025 | 62.537 | 62.8582 | 63.075 | 63.4404 | 62.2024 | 123.1246 | 61.7354 | 123.0605 | 61.472 | 61.5534 | 123.1628 | 61.5128 | 122.9639 | 61.5713 | 61.6118 | 61.5071 | 61.5476
7189.0625 | 123.3444 | -61.5326 | 61.5326 | 1.2436 | 0.82946 | 1.0777 | 1.4218 | 1.6157 | 1.9581 | 0.69268 | 61.6104 | 0.22116 | 61.5187 | -0.033101 | 0.057392 | 61.6531 | 0.007721 | 61.4634 | 62.7761 | 62.362 | 62.6103 | 62.9544 | 63.1483 | 63.4907 | 62.2253 | 123.1429 | 61.7538 | 123.0513 | 61.4995 | 61.59 | 123.1857 | 61.5403 | 122.996 | 61.553 | 61.6026 | 61.4613 | 61.511
7190.1094 | 123.3627 | -61.5372 | 61.5097 | 1.1657 | 0.74246 | 0.99071 | 1.3394 | 1.547 | 1.894 | 0.61485 | 61.6195 | 0.2349 | 61.537 | -0.028522 | 0.043657 | 61.6577 | 0.012299 | 61.4496 | 62.7029 | 62.2796 | 62.5279 | 62.8765 | 63.0842 | 63.4312 | 62.152 | 123.1567 | 61.7721 | 123.0742 | 61.5086 | 61.5808 | 123.1949 | 61.5495 | 122.9868 | 61.5759 | 61.6072 | 61.4934 | 61.5247
7191.0625 | 123.3627 | -61.528 | 61.5555 | 1.1154 | 0.67378 | 0.92661 | 1.2844 | 1.4921 | 1.8208 | 0.5416 | 61.6241 | 0.2349 | 61.5508 | -0.033101 | 0.043657 | 61.6486 | 0.016878 | 61.4405 | 62.6434 | 62.2018 | 62.4546 | 62.8124 | 63.0201 | 63.3488 | 62.0696 | 123.1521 | 61.7629 | 123.0788 | 61.4949 | 61.5717 | 123.1766 | 61.5449 | 122.9685 | 61.5804 | 61.6072 | 61.5071 | 61.5339
7192.0625 | 123.3536 | -61.5051 | 61.5784 | 0.99174 | 0.57304 | 0.81215 | 1.1654 | 1.3685 | 1.7018 | 0.4363 | 61.6241 | 0.22574 | 61.5233 | -0.033101 | 0.043657 | 61.6486 | 0.007721 | 61.4359 | 62.4969 | 62.0782 | 62.3173 | 62.6705 | 62.8736 | 63.2069 | 61.9414 | 123.1292 | 61.7309 | 123.0284 | 61.472 | 61.5488 | 123.1537 | 61.5128 | 122.941 | 61.5804 | 61.6164 | 61.4796 | 61.5156
7193.0938 | 123.3582 | -61.5372 | 61.5417 | 1.1428 | 0.71956 | 0.96324 | 1.3165 | 1.5149 | 1.8391 | 0.58281 | 61.6241 | 0.23032 | 61.5462 | -0.023943 | 0.043657 | 61.6486 | 0.003143 | 61.4405 | 62.68 | 62.2567 | 62.5004 | 62.8537 | 63.0521 | 63.3763 | 62.12 | 123.1613 | 61.7675 | 123.0834 | 61.5132 | 61.5808 | 123.1857 | 61.5403 | 122.9777 | 61.5804 | 61.6209 | 61.5025 | 61.543
7194.0625 | 123.3627 | -61.5143 | 61.5692 | 1.033 | 0.60967 | 0.86709 | 1.202 | 1.428 | 1.743 | 0.47293 | 61.6287 | 0.23032 | 61.5279 | -0.023943 | 0.048236 | 61.6486 | 0.003143 | 61.4405 | 62.5472 | 62.124 | 62.3814 | 62.7163 | 62.9422 | 63.2572 | 61.9872 | 123.143 | 61.7446 | 123.0422 | 61.4903 | 61.5625 | 123.1628 | 61.5174 | 122.9548 | 61.5804 | 61.6255 | 61.4796 | 61.5247
7195.0938 | 123.2529 | -61.5463 | 61.5784 | 1.0604 | 0.63714 | 0.88083 | 1.2295 | 1.4554 | 1.775 | 0.51413 | 61.6287 | 0.2349 | 61.5508 | -0.033101 | 0.048236 | 61.6486 | 0.007721 | 61.4496 | 62.6067 | 62.1835 | 62.4272 | 62.7758 | 63.0018 | 63.3213 | 62.0605 | 123.175 | 61.7812 | 123.0971 | 61.5132 | 61.5946 | 123.1949 | 61.554 | 122.996 | 61.5804 | 61.6209 | 61.5025 | 61.543
7196.0625 | 123.3673 | -61.5509 | 61.5692 | 1.1108 | 0.69667 | 0.93119 | 1.2844 | 1.5149 | 1.8208 | 0.56449 | 61.6195 | 0.2349 | 61.5462 | -0.028522 | 0.043657 | 61.6531 | 0.016878 | 61.4451 | 62.6617 | 62.2476 | 62.4821 | 62.8353 | 63.0658 | 63.3717 | 62.1154 | 123.1704 | 61.7858 | 123.0971 | 61.5224 | 61.5946 | 123.204 | 61.5678 | 122.996 | 61.5759 | 61.6026 | 61.5025 | 61.5293
7197.0938 | 123.4039 | -61.5189 | 61.5097 | 0.97801 | 0.54557 | 0.79383 | 1.1517 | 1.3868 | 1.7018 | 0.41799 | 61.6378 | 0.23948 | 61.5645 | 0.012689 | 0.052814 | 61.644 | 0.03977 | 61.619 | 62.4969 | 62.0644 | 62.3127 | 62.6705 | 62.9056 | 63.2206 | 61.9369 | 123.1567 | 61.7583 | 123.0834 | 61.5315 | 61.5717 | 123.1628 | 61.5586 | 123.1379 | 61.585 | 61.5981 | 61.5117 | 61.5247
7198.0625 | 123.381 | -61.5189 | 61.5601 | 0.89102 | 0.46773 | 0.70226 | 1.0692 | 1.286 | 1.6056 | 0.3539 | 61.6561 | 0.24863 | 61.5828 | 0.053901 | 0.094017 | 61.6394 | -0.04722 | 61.6236 | 62.4099 | 61.9866 | 62.2211 | 62.5881 | 62.8049 | 63.1245 | 61.8728 | 123.175 | 61.7675 | 123.1017 | 61.5728 | 61.6129 | 123.1583 | 61.4716 | 123.1425 | 61.5621 | 61.7034 | 61.4888 | 61.63
7199.0938 | 123.2758 | -61.5417 | 61.5692 | 0.87271 | 0.44483 | 0.68395 | 1.0555 | 1.2723 | 1.601 | 0.32643 | 61.6653 | 0.25321 | 61.592 | 0.05848 | 0.089439 | 61.6394 | 0.003143 | 61.4359 | 62.4145 | 61.9866 | 62.2257 | 62.5973 | 62.8141 | 63.1428 | 61.8682 | 123.207 | 61.795 | 123.1337 | 61.6002 | 61.6312 | 123.1812 | 61.5449 | 122.9777 | 61.5759 | 61.6622 | 61.5025 | 61.5888
7200.0625 | 123.3261 | -61.5234 | 61.6104 | 0.9597 | 0.54557 | 0.78468 | 1.1471 | 1.3272 | 1.6605 | 0.40426 | 61.6561 | 0.25779 | 61.592 | 0.05848 | 0.094017 | 61.644 | 0.007721 | 61.4496 | 62.4831 | 62.069 | 62.3081 | 62.6705 | 62.8507 | 63.184 | 61.9277 | 123.1796 | 61.7812 | 123.1154 | 61.5819 | 61.6175 | 123.1674 | 61.5312 | 122.9731 | 61.5621 | 61.6484 | 61.4979 | 61.5842
7201.0938 | 123.381 | -61.5417 | 61.5555 | 0.92765 | 0.49978 | 0.76178 | 1.1196 | 1.3089 | 1.601 | 0.3539 | 61.6561 | 0.25321 | 61.592 | 0.053901 | 0.089439 | 61.644 | -0.033484 | 61.4313 | 62.4694 | 62.0415 | 62.3035 | 62.6614 | 62.8507 | 63.1428 | 61.8956 | 123.1979 | 61.795 | 123.1337 | 61.5956 | 61.6312 | 123.1857 | 61.5083 | 122.9731 | 61.5667 | 61.6896 | 61.5025 | 61.6255
7202.0625 | 123.3627 | -61.5051 | 61.5646 | 0.97801 | 0.5593 | 0.80757 | 1.1608 | 1.341 | 1.6514 | 0.40884 | 61.6424 | 0.23948 | 61.5782 | 0.053901 | 0.080283 | 61.644 | -0.070112 | 61.4359 | 62.4831 | 62.0644 | 62.3127 | 62.6659 | 62.8461 | 63.1565 | 61.914 | 123.1475 | 61.7446 | 123.0834 | 61.559 | 61.5854 | 123.1491 | 61.435 | 122.941 | 61.5621 | 61.7125 | 61.4979 | 61.6483
7203.0781 | 123.3124 | -61.5326 | 61.5326 | 0.93223 | 0.51809 | 0.77094 | 1.1288 | 1.2952 | 1.5965 | 0.36763 | 61.6378 | 0.23948 | 61.5737 | 0.003531 | 0.048236 | 61.6394 | -0.07469 | 61.4313 | 62.4648 | 62.0507 | 62.3035 | 62.6614 | 62.8278 | 63.129 | 61.9002 | 123.1704 | 61.7721 | 123.1062 | 61.5361 | 61.5808 | 123.172 | 61.4579 | 122.9639 | 61.5896 | 61.7125 | 61.5254 | 61.6483
7204.0625 | 123.3582 | -61.5097 | 61.5509 | 0.77198 | 0.38073 | 0.60611 | 0.9502 | 1.1029 | 1.4316 | 0.23486 | 61.6378 | 0.23032 | 61.5508 | -0.001048 | 0.039079 | 61.6348 | 0.003143 | 61.413 | 62.2817 | 61.8904 | 62.1158 | 62.4599 | 62.6126 | 62.9413 | 61.7446 | 123.1475 | 61.74 | 123.0605 | 61.5087 | 61.5488 | 123.1445 | 61.5128 | 122.9227 | 61.5987 | 61.6347 | 61.5117 | 61.5476
7205.0938 | 123.2712 | -61.5646 | 61.5555 | 0.8956 | 0.48604 | 0.72973 | 1.0921 | 1.2448 | 1.5598 | 0.32643 | 61.6332 | 0.23948 | 61.537 | -0.005627 | 0.084861 | 61.6348 | 0.035191 | 61.3947 | 62.4602 | 62.0507 | 62.2944 | 62.6568 | 62.8095 | 63.1245 | 61.8911 | 123.1979 | 61.8041 | 123.1017 | 61.559 | 61.6495 | 123.1995 | 61.5998 | 122.9593 | 61.5484 | 61.5981 | 61.4522 | 61.5018
7206.0625 | 123.381 | -61.5097 | 61.5601 | 1.0146 | 0.61883 | 0.87625 | 1.2524 | 1.2952 | 1.656 | 0.45004 | 61.6287 | 0.24405 | 61.5324 | -0.088049 | 0.048236 | 61.6486 | -0.015171 | 61.6282 | 62.5243 | 62.1285 | 62.386 | 62.7621 | 62.8049 | 63.1657 | 61.9597 | 123.1384 | 61.7538 | 123.0422 | 61.4217 | 61.5579 | 123.1583 | 61.4945 | 123.1379 | 61.5804 | 61.6438 | 61.4842 | 61.5476
7207.0781 | 123.3582 | -61.5372 | 61.5692 | 0.94596 | 0.56388 | 0.79383 | 1.1654 | 1.1991 | 1.601 | 0.3951 | 61.6378 | 0.22574 | 61.5233 | -0.023943 | 0.039079 | 61.6394 | 0.012299 | 61.6328 | 62.4831 | 62.1011 | 62.331 | 62.7026 | 62.7362 | 63.1382 | 61.9323 | 123.175 | 61.7629 | 123.0605 | 61.5132 | 61.5762 | 123.1766 | 61.5495 | 123.1699 | 61.5987 | 61.6255 | 61.4842 | 61.511
7208.0625 | 123.3444 | -61.5189 | 61.5692 | 1.033 | 0.63257 | 0.88541 | 1.2524 | 1.2952 | 1.6789 | 0.47293 | 61.6241 | 0.23032 | 61.5553 | -0.019364 | 0.048236 | 61.6486 | 0.012299 | 61.4176 | 62.5518 | 62.1514 | 62.4043 | 62.7712 | 62.8141 | 63.1977 | 61.9918 | 123.143 | 61.7492 | 123.0742 | 61.4995 | 61.5671 | 123.1674 | 61.5312 | 122.9365 | 61.5759 | 61.6118 | 61.5071 | 61.543
7209.0781 | 123.262 | -61.5417 | 61.6058 | 0.84981 | 0.45399 | 0.68395 | 1.0647 | 1.0892 | 1.5003 | 0.30354 | 61.647 | 0.23032 | 61.5462 | -0.019364 | 0.048236 | 61.6394 | 0.016878 | 61.4084 | 62.3916 | 61.9957 | 62.2257 | 62.6064 | 62.6309 | 63.0421 | 61.8453 | 123.1887 | 61.7721 | 123.0879 | 61.5224 | 61.59 | 123.1812 | 61.5586 | 122.9502 | 61.5987 | 61.6301 | 61.4979 | 61.5293
7210.0625 | 123.3902 | -61.4868 | 61.5738 | 0.76282 | 0.36241 | 0.60611 | 0.98683 | 1.0068 | 1.4042 | 0.19824 | 61.6424 | 0.23032 | 61.537 | -0.019364 | 0.048236 | 61.6257 | 0.012299 | 61.413 | 62.2496 | 61.8492 | 62.0929 | 62.4736 | 62.4936 | 62.891 | 61.6851 | 123.1292 | 61.7171 | 123.0238 | 61.4675 | 61.5351 | 123.1125 | 61.4991 | 122.8998 | 61.5942 | 61.6301 | 61.4888 | 61.5247
7211.0938 | 123.262 | -61.528 | 61.6425 | 0.57511 | 0.19758 | 0.41381 | 0.79453 | 0.82367 | 1.221 | 0.042581 | 61.6607 | 0.22574 | 61.5599 | -0.023943 | 0.048236 | 61.6119 | 0.007721 | 61.3993 | 62.1031 | 61.7256 | 61.9418 | 62.3225 | 62.3517 | 62.749 | 61.5706 | 123.1887 | 61.7538 | 123.0879 | 61.5041 | 61.5763 | 123.14 | 61.5357 | 122.9273 | 61.6125 | 61.653 | 61.5117 | 61.5522
7212.0625 | 123.3444 | -61.5372 | 61.5555 | 0.73535 | 0.33494 | 0.58322 | 0.96852 | 0.9839 | 1.3721 | 0.16619 | 61.6561 | 0.23948 | 61.5782 | -0.023943 | 0.048236 | 61.6257 | 0.007721 | 61.4084 | 62.2725 | 61.8721 | 62.1204 | 62.5057 | 62.5211 | 62.9093 | 61.7034 | 123.1933 | 61.7766 | 123.1154 | 61.5132 | 61.5854 | 123.1628 | 61.5449 | 122.9456 | 61.6079 | 61.6484 | 61.53 | 61.5705
7213.0781 | 123.1934 | -61.5417 | 61.6013 | 0.57511 | 0.193 | 0.43212 | 0.80369 | 0.82825 | 1.2073 | 0.01969 | 61.6561 | 0.23032 | 61.5691 | -0.028522 | 0.048236 | 61.6257 | 0.012299 | 61.413 | 62.1169 | 61.7347 | 61.9739 | 62.3454 | 62.37 | 62.749 | 61.5614 | 123.1979 | 61.7721 | 123.1108 | 61.5132 | 61.59 | 123.1674 | 61.554 | 122.9548 | 61.6079 | 61.6438 | 61.5208 | 61.5568
7214.0625 | 123.3261 | -61.5005 | 61.5417 | 0.66668 | 0.28915 | 0.5237 | 0.89526 | 0.91523 | 1.2943 | 0.11125 | 61.6424 | 0.22574 | 61.5553 | -0.028522 | 0.048236 | 61.6211 | 0.007721 | 61.4222 | 62.1672 | 61.7897 | 62.0242 | 62.3958 | 62.4158 | 62.7948 | 61.6118 | 123.143 | 61.7263 | 123.0559 | 61.472 | 61.5488 | 123.1216 | 61.5083 | 122.9227 | 61.5942 | 61.6347 | 61.5071 | 61.5476
7215.1094 | 123.2712 | -61.5326 | 61.5921 | 0.67126 | 0.28915 | 0.52828 | 0.91358 | 0.93812 | 1.3126 | 0.12041 | 61.6424 | 0.22116 | 61.5553 | -0.028522 | 0.048236 | 61.6303 | 0.007721 | 61.4268 | 62.2039 | 61.8217 | 62.0609 | 62.4462 | 62.4707 | 62.8452 | 61.653 | 123.175 | 61.7538 | 123.0879 | 61.5041 | 61.5808 | 123.1628 | 61.5403 | 122.9594 | 61.5942 | 61.6347 | 61.5071 | 61.5476
7216.0625 | 123.3536 | -61.4868 | 61.5875 | 0.57969 | 0.18842 | 0.4367 | 0.80827 | 0.83283 | 1.1981 | 0.01969 | 61.6561 | 0.2349 | 61.5691 | -0.033101 | 0.052814 | 61.6211 | 0.016878 | 61.4268 | 62.0665 | 61.6752 | 61.9235 | 62.2951 | 62.3196 | 62.6849 | 61.5065 | 123.143 | 61.7217 | 123.0559 | 61.4537 | 61.5396 | 123.1079 | 61.5037 | 122.9136 | 61.6033 | 61.6393 | 61.5163 | 61.5522
7217.0781 | 123.2391 | -61.528 | 61.5967 | 0.74451 | 0.35326 | 0.60611 | 0.9731 | 1.0114 | 1.3721 | 0.16619 | 61.6516 | 0.23948 | 61.5874 | -0.03768 | 0.052814 | 61.6257 | 0.007721 | 61.4268 | 62.2725 | 61.8813 | 62.1341 | 62.5011 | 62.5394 | 62.9001 | 61.6942 | 123.1796 | 61.7675 | 123.1154 | 61.4903 | 61.5808 | 123.1537 | 61.5357 | 122.9548 | 61.5987 | 61.6438 | 61.5346 | 61.5797
7218.0625 | 123.3353 | -61.5051 | 61.5555 | 0.63005 | 0.23879 | 0.48707 | 0.86779 | 0.89234 | 1.2622 | 0.065472 | 61.6561 | 0.24405 | 61.5874 | -0.033101 | 0.048236 | 61.6211 | 0.007721 | 61.413 | 62.1352 | 61.7439 | 61.9922 | 62.3729 | 62.3975 | 62.7674 | 61.5706 | 123.1613 | 61.7492 | 123.0925 | 61.472 | 61.5534 | 123.1262 | 61.5128 | 122.9181 | 61.6079 | 61.6484 | 61.5392 | 61.5797
7219.0938 | 123.262 | -61.5234 | 61.5875 | 0.65294 | 0.26626 | 0.52828 | 0.89526 | 0.92897 | 1.276 | 0.074628 | 61.6516 | 0.2349 | 61.5782 | -0.042259 | 0.048236 | 61.6303 | 0.007721 | 61.4176 | 62.1764 | 61.7897 | 62.0517 | 62.4187 | 62.4524 | 62.7994 | 61.5981 | 123.175 | 61.7583 | 123.1017 | 61.4812 | 61.5717 | 123.1537 | 61.5312 | 122.941 | 61.6033 | 61.6438 | 61.53 | 61.5705
7220.0625 | 123.3353 | -61.4822 | 61.6013 | 0.69873 | 0.30747 | 0.57406 | 0.9502 | 0.97017 | 1.3217 | 0.12499 | 61.6516 | 0.23032 | 61.5599 | -0.028522 | 0.052814 | 61.6303 | 0.007721 | 61.4268 | 62.181 | 61.7897 | 62.0563 | 62.4324 | 62.4524 | 62.804 | 61.6072 | 123.1338 | 61.7126 | 123.0422 | 61.4537 | 61.5351 | 123.1125 | 61.49 | 122.909 | 61.5987 | 61.6438 | 61.5071 | 61.5522
7221.0781 | 123.2986 | -61.5143 | 61.6241 | 0.76282 | 0.36241 | 0.61527 | 1.0051 | 1.0297 | 1.3767 | 0.17535 | 61.6561 | 0.2349 | 61.5508 | -0.033101 | 0.048236 | 61.6303 | 0.007721 | 61.4268 | 62.2771 | 61.8767 | 62.1296 | 62.5194 | 62.544 | 62.891 | 61.6896 | 123.1704 | 61.7492 | 123.065 | 61.4812 | 61.5625 | 123.1445 | 61.522 | 122.941 | 61.6079 | 61.6484 | 61.5025 | 61.543
7222.0625 | 123.262 | -61.5417 | 61.5738 | 0.61632 | 0.24794 | 0.48707 | 0.86779 | 0.89692 | 1.2256 | 0.042581 | 61.6561 | 0.2349 | 61.5645 | -0.03768 | 0.043657 | 61.6257 | 0.003143 | 61.4222 | 62.1581 | 61.7897 | 62.0288 | 62.4095 | 62.4387 | 62.7673 | 61.5843 | 123.1979 | 61.7766 | 123.1062 | 61.5041 | 61.5854 | 123.1674 | 61.5449 | 122.9639 | 61.6125 | 61.653 | 61.5208 | 61.5614
7223.0938 | 123.2162 | -61.5738 | 61.5555 | 0.57511 | 0.18842 | 0.4367 | 0.75791 | 0.91523 | 1.1936 | -0.003201 | 61.6561 | 0.2349 | 61.5874 | -0.03768 | 0.043657 | 61.6165 | 0.003143 | 61.413 | 62.1489 | 61.7622 | 62.0105 | 62.3317 | 62.489 | 62.7673 | 61.5706 | 123.2299 | 61.8087 | 123.1612 | 61.5361 | 61.6174 | 123.1903 | 61.5769 | 122.9868 | 61.6125 | 61.653 | 61.5437 | 61.5842
7224.0625 | 123.3078 | -61.5372 | 61.5784 | 0.5568 | 0.17468 | 0.40923 | 0.73959 | 0.9015 | 1.1844 | -0.007779 | 61.6561 | 0.2349 | 61.592 | -0.042259 | 0.048236 | 61.6211 | 0.012299 | 61.4222 | 62.094 | 61.7119 | 61.9464 | 62.2768 | 62.4387 | 62.7216 | 61.5294 | 123.1933 | 61.7721 | 123.1291 | 61.4949 | 61.5854 | 123.1583 | 61.5495 | 122.9593 | 61.6079 | 61.6438 | 61.5437 | 61.5797
7225.1094 | 123.2666 | -61.4868 | 61.6333 | 0.15848 | -0.18246 | 0.042944 | 0.38705 | 0.41624 | 0.75861 | -0.39235 | 61.6882 | 0.23948 | 61.6194 | -0.042259 | 0.052814 | 61.5936 | 0.012299 | 61.3901 | 61.6453 | 61.3044 | 61.5298 | 61.8739 | 61.9031 | 62.2454 | 61.0945 | 123.175 | 61.7263 | 123.1063 | 61.4446 | 61.5396 | 123.0804 | 61.4991 | 122.8769 | 61.6354 | 61.6759 | 61.5666 | 61.6071
7226.0625 | 123.3032 | -61.5005 | 61.5784 | 0.24547 | -0.090888 | 0.13452 | 0.47404 | 0.51237 | 0.85475 | -0.27789 | 61.679 | 0.2349 | 61.5828 | -0.033101 | 0.039079 | 61.6074 | 0.003143 | 61.3947 | 61.746 | 61.4097 | 61.6351 | 61.9746 | 62.0129 | 62.3553 | 61.2227 | 123.1796 | 61.7354 | 123.0834 | 61.4674 | 61.5396 | 123.1079 | 61.5037 | 122.8953 | 61.64 | 61.6759 | 61.5437 | 61.5797
7227.0781 | 123.2941 | -61.4822 | 61.6287 | 0.25462 | -0.095467 | 0.10704 | 0.4832 | 0.50322 | 0.86391 | -0.27789 | 61.6745 | 0.2349 | 61.5828 | -0.03768 | 0.048236 | 61.6028 | 0.016878 | 61.4039 | 61.7369 | 61.3868 | 61.5893 | 61.9654 | 61.9855 | 62.3461 | 61.2043 | 123.1567 | 61.7171 | 123.065 | 61.4446 | 61.5305 | 123.085 | 61.4991 | 122.8861 | 61.6262 | 61.6576 | 61.5346 | 61.5659
7228.0625 | 123.349 | -61.4914 | 61.5509 | 0.3233 | -0.017627 | 0.20319 | 0.56103 | 0.5902 | 0.9509 | -0.19548 | 61.6653 | 0.22574 | 61.5737 | -0.042259 | 0.048236 | 61.6074 | 0.003143 | 61.3993 | 61.8147 | 61.4738 | 61.6946 | 62.0524 | 62.0816 | 62.4423 | 61.2959 | 123.1567 | 61.7171 | 123.065 | 61.4491 | 61.5396 | 123.0988 | 61.4945 | 122.8907 | 61.6171 | 61.6622 | 61.5254 | 61.5705
7229.0781 | 123.2895 | -61.4685 | 61.6699 | 0.21342 | -0.11836 | 0.084151 | 0.44199 | 0.45744 | 0.81812 | -0.3191 | 61.679 | 0.2349 | 61.6057 | -0.028522 | 0.06197 | 61.6028 | 0.012299 | 61.4039 | 61.6819 | 61.3501 | 61.5527 | 61.9105 | 61.9259 | 62.2866 | 61.1494 | 123.1475 | 61.7034 | 123.0742 | 61.44 | 61.5305 | 123.0713 | 61.4808 | 122.8724 | 61.6171 | 61.6667 | 61.5437 | 61.5934
7230.0625 | 123.2529 | -61.5189 | 61.6196 | 0.14474 | -0.18246 | 0.024629 | 0.36416 | 0.39335 | 0.76318 | -0.36945 | 61.6836 | 0.2349 | 61.6194 | -0.028522 | 0.039079 | 61.5936 | 0.007721 | 61.3947 | 61.6636 | 61.3364 | 61.5435 | 61.883 | 61.9122 | 62.282 | 61.1494 | 123.2025 | 61.7538 | 123.1383 | 61.4903 | 61.5579 | 123.1125 | 61.5266 | 122.9136 | 61.6445 | 61.6759 | 61.5804 | 61.6117
7231.0781 | 123.2895 | -61.4822 | 61.6837 | -0.10249 | -0.42514 | -0.21346 | 0.11692 | 0.14156 | 0.47017 | -0.63499 | 61.7019 | 0.2349 | 61.6332 | -0.028522 | 0.052814 | 61.5799 | 0.007721 | 61.3764 | 61.3797 | 61.0571 | 61.2688 | 61.5992 | 61.6238 | 61.9524 | 60.8473 | 123.1842 | 61.7171 | 123.1154 | 61.4537 | 61.5351 | 123.0621 | 61.49 | 122.8586 | 61.6491 | 61.6942 | 61.5804 | 61.6255
7232.0625 | 123.3353 | -61.528 | 61.647 | 0.13101 | -0.19162 | 0.010893 | 0.35042 | 0.38419 | 0.7174 | -0.40608 | 61.6928 | 0.2349 | 61.6057 | -0.028522 | 0.048236 | 61.5891 | 0.007721 | 61.3947 | 61.659 | 61.3364 | 61.5389 | 61.8784 | 61.9122 | 62.2454 | 61.1219 | 123.2208 | 61.7629 | 123.1337 | 61.4995 | 61.5763 | 123.1171 | 61.5357 | 122.9227 | 61.6445 | 61.685 | 61.5575 | 61.598
7233.0781 | 123.2346 | -61.4868 | 61.6699 | 0.26836 | -0.072572 | 0.14367 | 0.49235 | 0.51237 | 0.84102 | -0.26416 | 61.679 | 0.23032 | 61.5874 | -0.033101 | 0.052814 | 61.5982 | 0.012299 | 61.4084 | 61.7552 | 61.4142 | 61.6305 | 61.9792 | 61.9992 | 62.3278 | 61.2227 | 123.1658 | 61.7171 | 123.0742 | 61.4537 | 61.5396 | 123.085 | 61.4991 | 122.8953 | 61.6262 | 61.6667 | 61.5346 | 61.5751
7234.0625 | 123.262 | -61.4914 | 61.6425 | -0.070441 | -0.39767 | -0.17683 | 0.16728 | 0.18276 | 0.50222 | -0.59836 | 61.6928 | 0.23032 | 61.6011 | -0.028522 | 0.048236 | 61.5845 | 0.003143 | 61.381 | 61.421 | 61.0937 | 61.3146 | 61.6587 | 61.6742 | 61.9936 | 60.893 | 123.1842 | 61.7217 | 123.0925 | 61.4629 | 61.5396 | 123.0759 | 61.4945 | 122.8724 | 61.6445 | 61.6896 | 61.5529 | 61.598
7235.1094 | 123.2574 | -61.4914 | 61.6653 | 0.18137 | -0.15499 | 0.047522 | 0.35958 | 0.49406 | 0.7815 | -0.35114 | 61.6836 | 0.23032 | 61.5874 | -0.023943 | 0.052814 | 61.5936 | 0.016878 | 61.4039 | 61.6728 | 61.3364 | 61.5389 | 61.851 | 61.9855 | 62.2729 | 61.1403 | 123.175 | 61.7217 | 123.0788 | 61.4675 | 61.5442 | 123.085 | 61.5083 | 122.8953 | 61.6308 | 61.6667 | 61.5346 | 61.5705
7236.0625 | 123.262 | -61.5143 | 61.6379 | 0.24547 | -0.090888 | 0.12078 | 0.42368 | 0.56273 | 0.84559 | -0.27789 | 61.6745 | 0.2349 | 61.592 | -0.033101 | 0.052814 | 61.6028 | 0.003143 | 61.3993 | 61.7598 | 61.4234 | 61.6351 | 61.938 | 62.077 | 62.3599 | 61.2364 | 123.1887 | 61.7492 | 123.1062 | 61.4812 | 61.5671 | 123.1171 | 61.5174 | 122.9136 | 61.6216 | 61.6713 | 61.5392 | 61.5888
7237.0781 | 123.2895 | -61.5143 | 61.6882 | 0.16306 | -0.17788 | 0.042944 | 0.38705 | 0.42997 | 0.75861 | -0.38777 | 61.6836 | 0.23948 | 61.6103 | -0.023943 | 0.057392 | 61.5982 | 0.012299 | 61.4039 | 61.6773 | 61.3364 | 61.5572 | 61.9013 | 61.9443 | 62.2729 | 61.1265 | 123.1979 | 61.7538 | 123.1246 | 61.4903 | 61.5717 | 123.1125 | 61.5266 | 122.9181 | 61.6262 | 61.6713 | 61.5529 | 61.598
7238.0625 | 123.2758 | -61.5143 | 61.615 | 0.29125 | -0.049678 | 0.17114 | 0.51982 | 0.55815 | 0.86391 | -0.25958 | 61.6699 | 0.2349 | 61.6057 | -0.033101 | 0.048236 | 61.6028 | 0.012299 | 61.4084 | 61.8055 | 61.4646 | 61.6854 | 62.0341 | 62.0724 | 62.3782 | 61.2547 | 123.1842 | 61.7492 | 123.12 | 61.4812 | 61.5625 | 123.1171 | 61.5266 | 122.9227 | 61.6216 | 61.6576 | 61.5575 | 61.5934
7239.0938 | 123.3124 | -61.4731 | 61.6653 | 0.14932 | -0.16873 | 0.033786 | 0.37789 | 0.39335 | 0.71282 | -0.39692 | 61.679 | 0.2349 | 61.6011 | -0.028522 | 0.052814 | 61.5891 | 0.021456 | 61.3993 | 61.6224 | 61.3044 | 61.5069 | 61.851 | 61.8664 | 62.1859 | 61.0762 | 123.1521 | 61.708 | 123.0742 | 61.4446 | 61.5259 | 123.0621 | 61.4945 | 122.8724 | 61.6262 | 61.6576 | 61.5483 | 61.5797
7240.0625 | 123.3444 | -61.5005 | 61.6013 | 0.10354 | -0.23283 | -0.016578 | 0.33211 | 0.3613 | 0.66246 | -0.46102 | 61.679 | 0.22574 | 61.592 | -0.019364 | 0.039079 | 61.5891 | -0.001436 | 61.3947 | 61.6041 | 61.2677 | 61.484 | 61.8327 | 61.8618 | 62.163 | 61.0395 | 123.1796 | 61.7263 | 123.0925 | 61.4812 | 61.5396 | 123.0896 | 61.4991 | 122.8953 | 61.64 | 61.6805 | 61.5529 | 61.5934
7241.0781 | 123.2986 | -61.4639 | 61.6516 | 0.080646 | -0.2603 | -0.04405 | 0.24969 | 0.37046 | 0.64872 | -0.48391 | 61.6836 | 0.23032 | 61.5965 | -0.023943 | 0.048236 | 61.5982 | 0.016878 | 61.3947 | 61.5446 | 61.2036 | 61.4199 | 61.7136 | 61.8344 | 62.1127 | 60.98 | 123.1475 | 61.6942 | 123.0605 | 61.44 | 61.5122 | 123.0621 | 61.4808 | 122.8586 | 61.6354 | 61.6667 | 61.5483 | 61.5797
7242.0625 | 123.2666 | -61.4822 | 61.6333 | 0.044018 | -0.2832 | -0.053207 | 0.24969 | 0.29721 | 0.58921 | -0.5068 | 61.6882 | 0.23032 | 61.6011 | -0.023943 | 0.043657 | 61.5936 | 0.012299 | 61.3901 | 61.5263 | 61.199 | 61.429 | 61.7319 | 61.7794 | 62.0714 | 60.9754 | 123.1704 | 61.7126 | 123.0834 | 61.4583 | 61.5259 | 123.0759 | 61.4945 | 122.8724 | 61.6445 | 61.6759 | 61.5575 | 61.5888
7243.0781 | 123.3215 | -61.4502 | 61.6699 | 0.062332 | -0.25572 | -0.048628 | 0.27716 | 0.29721 | 0.60752 | -0.48391 | 61.6882 | 0.23948 | 61.6149 | -0.028522 | 0.048236 | 61.5891 | 0.012299 | 61.3947 | 61.5125 | 61.1945 | 61.4016 | 61.7274 | 61.7474 | 62.0577 | 60.9663 | 123.1384 | 61.6897 | 123.0651 | 61.4217 | 61.4984 | 123.0392 | 61.4625 | 122.8449 | 61.64 | 61.6759 | 61.5666 | 61.6026
7244.0625 | 123.3032 | -61.4731 | 61.6333 | -0.006344 | -0.33357 | -0.12189 | 0.16728 | 0.2789 | 0.53884 | -0.55716 | 61.6928 | 0.23948 | 61.624 | -0.023943 | 0.043657 | 61.5891 | 0.012299 | 61.3856 | 61.4667 | 61.1395 | 61.3512 | 61.6404 | 61.752 | 62.0119 | 60.9159 | 123.1659 | 61.7126 | 123.0971 | 61.4491 | 61.5167 | 123.0621 | 61.4854 | 122.8586 | 61.6491 | 61.6805 | 61.5804 | 61.6117
7245.1094 | 123.2666 | -61.4868 | 61.6653 | 0.16306 | -0.16415 | 0.029208 | 0.38247 | 0.4025 | 0.75861 | -0.36945 | 61.6836 | 0.23948 | 61.6103 | -0.028522 | 0.057392 | 61.6028 | 0.012299 | 61.4039 | 61.6499 | 61.3227 | 61.516 | 61.8693 | 61.8893 | 62.2454 | 61.1174 | 123.1704 | 61.7263 | 123.0971 | 61.4583 | 61.5442 | 123.0896 | 61.4991 | 122.8907 | 61.6262 | 61.6713 | 61.5529 | 61.598
7246.0625 | 123.3078 | -61.4685 | 61.6425 | 0.3233 | -0.026784 | 0.19404 | 0.55187 | 0.57646 | 0.91427 | -0.24127 | 61.6699 | 0.2349 | 61.5828 | -0.033101 | 0.048236 | 61.6074 | 0.012299 | 61.4084 | 61.7918 | 61.4417 | 61.6625 | 62.0204 | 62.045 | 62.3828 | 61.2272 | 123.1384 | 61.7034 | 123.0513 | 61.4354 | 61.5167 | 123.0759 | 61.4808 | 122.8769 | 61.6216 | 61.6576 | 61.5346 | 61.5705
7247.0625 | 123.2437 | -61.5189 | 61.6241 | 0.45149 | 0.10142 | 0.32682 | 0.67549 | 0.70007 | 1.0379 | -0.11308 | 61.6561 | 0.2349 | 61.5645 | -0.028522 | 0.052814 | 61.6074 | 0.003143 | 61.4039 | 61.9704 | 61.6203 | 61.8457 | 62.1944 | 62.2189 | 62.5567 | 61.4058 | 123.175 | 61.7538 | 123.0834 | 61.4903 | 61.5717 | 123.1262 | 61.522 | 122.9227 | 61.6033 | 61.653 | 61.5117 | 61.5614
7248.0625 | 123.2712 | -61.5143 | 61.6013 | 0.38282 | 0.041898 | 0.28103 | 0.62055 | 0.64513 | 0.96005 | -0.18175 | 61.6699 | 0.23032 | 61.5691 | -0.023943 | 0.048236 | 61.6074 | 0.003143 | 61.3993 | 61.8971 | 61.5562 | 61.7953 | 62.1348 | 62.1594 | 62.4743 | 61.3325 | 123.1842 | 61.7446 | 123.0834 | 61.4903 | 61.5625 | 123.1216 | 61.5174 | 122.9136 | 61.6216 | 61.6667 | 61.5208 | 61.5659
7249.0938 | 123.2941 | -61.4822 | 61.6425 | 0.3233 | -0.026784 | 0.18488 | 0.52898 | 0.55357 | 0.90054 | -0.22753 | 61.6653 | 0.2349 | 61.5737 | -0.028522 | 0.048236 | 61.5982 | 0.007721 | 61.3947 | 61.8055 | 61.4555 | 61.6671 | 62.0112 | 62.0358 | 62.3828 | 61.2547 | 123.1475 | 61.7171 | 123.0559 | 61.4537 | 61.5305 | 123.0804 | 61.49 | 122.8769 | 61.6171 | 61.6576 | 61.5254 | 61.5659
7250.0625 | 123.3856 | -61.5051 | 61.5555 | 0.30499 | -0.035942 | 0.18946 | 0.51525 | 0.549 | 0.86849 | -0.25042 | 61.6607 | 0.23032 | 61.5645 | -0.028522 | 0.043657 | 61.6074 | 0.007721 | 61.3901 | 61.8101 | 61.4692 | 61.6946 | 62.0204 | 62.0541 | 62.3736 | 61.2547 | 123.1658 | 61.7354 | 123.0696 | 61.4766 | 61.5488 | 123.1125 | 61.5128 | 122.8953 | 61.6171 | 61.653 | 61.5208 | 61.5568
7251.0625 | 123.3124 | -61.4731 | 61.6241 | 0.52017 | 0.17468 | 0.38634 | 0.74417 | 0.76874 | 1.1111 | -0.053561 | 61.6653 | 0.22574 | 61.5599 | -0.028522 | 0.048236 | 61.6211 | 0.016878 | 61.3993 | 61.9933 | 61.6478 | 61.8594 | 62.2173 | 62.2418 | 62.5842 | 61.4195 | 123.1384 | 61.6988 | 123.033 | 61.4446 | 61.5213 | 123.0942 | 61.49 | 122.8724 | 61.6171 | 61.6484 | 61.5117 | 61.543
7252.0781 | 123.2758 | -61.4777 | 61.6699 | 0.39655 | 0.069371 | 0.28561 | 0.62513 | 0.64971 | 0.97837 | -0.15886 | 61.6699 | 0.23032 | 61.5782 | -0.023943 | 0.048236 | 61.6165 | 0.007721 | 61.3993 | 61.8742 | 61.547 | 61.7633 | 62.1028 | 62.1274 | 62.456 | 61.3188 | 123.1475 | 61.708 | 123.0559 | 61.4537 | 61.5259 | 123.0942 | 61.4854 | 122.8769 | 61.6216 | 61.6622 | 61.53 | 61.5705
7253.0625 | 123.2941 | -61.4822 | 61.647 | 0.31414 | -0.017627 | 0.20777 | 0.53356 | 0.55357 | 0.85475 | -0.24127 | 61.679 | 0.23948 | 61.6103 | -0.023943 | 0.043657 | 61.6028 | 0.016878 | 61.3993 | 61.7964 | 61.4646 | 61.69 | 62.0158 | 62.0358 | 62.337 | 61.241 | 123.1613 | 61.7217 | 123.0925 | 61.4583 | 61.5259 | 123.085 | 61.4991 | 122.8815 | 61.6354 | 61.6622 | 61.5666 | 61.5934
7254.0938 | 123.2574 | -61.496 | 61.647 | 0.36451 | 0.023583 | 0.2673 | 0.59308 | 0.62224 | 0.90969 | -0.20922 | 61.6745 | 0.23948 | 61.5874 | -0.033101 | 0.048236 | 61.6074 | 0.012299 | 61.3947 | 61.8605 | 61.5196 | 61.7633 | 62.0891 | 62.1182 | 62.4057 | 61.2868 | 123.1704 | 61.7354 | 123.0834 | 61.4629 | 61.5442 | 123.1033 | 61.5083 | 122.8907 | 61.6262 | 61.6622 | 61.5392 | 61.5751
7255.0625 | 123.3261 | -61.5097 | 61.5829 | 0.38282 | 0.037319 | 0.27645 | 0.60224 | 0.62224 | 0.92801 | -0.19548 | 61.6653 | 0.22574 | 61.5691 | -0.028522 | 0.048236 | 61.6119 | 0.007721 | 61.3901 | 61.8925 | 61.547 | 61.7862 | 62.1119 | 62.1319 | 62.4377 | 61.3142 | 123.175 | 61.7354 | 123.0788 | 61.4812 | 61.5579 | 123.1216 | 61.5174 | 122.8998 | 61.6171 | 61.6576 | 61.5208 | 61.5614
7256.0781 | 123.3032 | -61.4914 | 61.647 | 0.33246 | 0.000689 | 0.22609 | 0.54729 | 0.57646 | 0.87307 | -0.23211 | 61.6653 | 0.22574 | 61.5599 | -0.023943 | 0.043657 | 61.6028 | 0.012299 | 61.3901 | 61.8239 | 61.4921 | 61.7175 | 62.0387 | 62.0679 | 62.3645 | 61.2593 | 123.1567 | 61.7171 | 123.0513 | 61.4675 | 61.5351 | 123.0942 | 61.5037 | 122.8815 | 61.6216 | 61.653 | 61.5163 | 61.5476
7257.0625 | 123.2483 | -61.5051 | 61.6333 | 0.54306 | 0.20216 | 0.4367 | 0.77622 | 0.79621 | 1.0608 | -0.076452 | 61.6516 | 0.23032 | 61.5599 | -0.023943 | 0.048236 | 61.6211 | 0.007721 | 61.3993 | 62.0482 | 61.7073 | 61.9418 | 62.2813 | 62.3013 | 62.5659 | 61.4287 | 123.1567 | 61.7354 | 123.065 | 61.4812 | 61.5534 | 123.1262 | 61.5128 | 122.9044 | 61.6033 | 61.6438 | 61.5117 | 61.5522
7258.0781 | 123.2758 | -61.5143 | 61.6287 | 0.71704 | 0.36241 | 0.63816 | 0.96852 | 0.98848 | 1.2348 | 0.074628 | 61.6516 | 0.23032 | 61.5462 | -0.023943 | 0.048236 | 61.6303 | 0.012299 | 61.4176 | 62.2313 | 61.8767 | 62.1524 | 62.4828 | 62.5028 | 62.749 | 61.5889 | 123.1658 | 61.7446 | 123.0605 | 61.4903 | 61.5625 | 123.1445 | 61.5266 | 122.9319 | 61.6033 | 61.6393 | 61.4979 | 61.5339
7259.0625 | 123.2758 | -61.5097 | 61.615 | 0.55222 | 0.193 | 0.4596 | 0.7808 | 0.80078 | 1.0699 | -0.062717 | 61.6653 | 0.23948 | 61.5965 | -0.028522 | 0.034501 | 61.6211 | 0.003143 | 61.3993 | 62.0619 | 61.7027 | 61.9693 | 62.2905 | 62.3105 | 62.5796 | 61.447 | 123.175 | 61.7492 | 123.1062 | 61.4812 | 61.5442 | 123.1308 | 61.5128 | 122.909 | 61.6308 | 61.6622 | 61.562 | 61.5934
7260.1094 | 123.2758 | -61.5143 | 61.6379 | 0.91391 | 0.53183 | 0.85794 | 1.1883 | 1.2082 | 1.3996 | 0.21197 | 61.6424 | 0.23948 | 61.5645 | -0.033101 | 0.048236 | 61.6394 | 0.012299 | 61.4268 | 62.4282 | 62.0461 | 62.3722 | 62.7026 | 62.7225 | 62.9139 | 61.7263 | 123.1567 | 61.7538 | 123.0788 | 61.4812 | 61.5625 | 123.1537 | 61.5266 | 122.941 | 61.5942 | 61.6301 | 61.5163 | 61.5522
7261.0625 | 123.2803 | -61.496 | 61.6196 | 0.46981 | 0.13347 | 0.3726 | 0.69381 | 0.72296 | 0.9921 | -0.14055 | 61.6607 | 0.23032 | 61.5599 | -0.028522 | 0.048236 | 61.6119 | 0.007721 | 61.3993 | 61.9658 | 61.6294 | 61.8686 | 62.1898 | 62.2189 | 62.4881 | 61.3554 | 123.1567 | 61.7263 | 123.0559 | 61.4674 | 61.5442 | 123.1079 | 61.5037 | 122.8953 | 61.6125 | 61.653 | 61.5117 | 61.5522
7262.0938 | 123.4085 | -61.4777 | 61.5875 | 0.63921 | 0.27084 | 0.57864 | 0.89068 | 0.91523 | 1.134 | -0.03067 | 61.647 | 0.22574 | 61.5508 | -0.028522 | 0.048236 | 61.6257 | 0.007721 | 61.3993 | 62.1169 | 61.7485 | 62.0563 | 62.3683 | 62.3929 | 62.6117 | 61.447 | 123.1246 | 61.7034 | 123.0284 | 61.4491 | 61.5259 | 123.1033 | 61.4854 | 122.8769 | 61.5987 | 61.6393 | 61.5025 | 61.543
7263.0625 | 123.2437 | -61.5005 | 61.615 | 0.45607 | 0.12432 | 0.36802 | 0.68465 | 0.70922 | 0.97379 | -0.15428 | 61.6745 | 0.2349 | 61.5965 | -0.023943 | 0.048236 | 61.6074 | 0.012299 | 61.3856 | 61.9566 | 61.6249 | 61.8686 | 62.1852 | 62.2098 | 62.4743 | 61.3463 | 123.175 | 61.7354 | 123.0971 | 61.4766 | 61.5488 | 123.1079 | 61.5128 | 122.8861 | 61.6262 | 61.6622 | 61.5483 | 61.5842
7264.0938 | 123.262 | -61.4914 | 61.647 | 0.47439 | 0.15179 | 0.38176 | 0.70296 | 0.73211 | 1.0013 | -0.11765 | 61.6653 | 0.23032 | 61.5737 | -0.019364 | 0.048236 | 61.6119 | 0.012299 | 61.3947 | 61.9658 | 61.6432 | 61.8732 | 62.1944 | 62.2235 | 62.4927 | 61.3737 | 123.1567 | 61.7217 | 123.065 | 61.472 | 61.5396 | 123.1033 | 61.5037 | 122.8861 | 61.6171 | 61.653 | 61.5254 | 61.5614
7265.0625 | 123.2941 | -61.4731 | 61.6333 | 0.51101 | 0.18384 | 0.42297 | 0.74417 | 0.76874 | 1.047 | -0.10392 | 61.6561 | 0.23032 | 61.5553 | -0.023943 | 0.052814 | 61.6119 | 0.007721 | 61.4039 | 61.9841 | 61.6569 | 61.8961 | 62.2173 | 62.2418 | 62.5201 | 61.3692 | 123.1292 | 61.7034 | 123.0284 | 61.4491 | 61.5259 | 123.085 | 61.4808 | 122.8769 | 61.6033 | 61.6484 | 61.5025 | 61.5476
7266.0781 | 123.2666 | -61.5097 | 61.6425 | 0.45607 | 0.10142 | 0.38176 | 0.70754 | 0.73211 | 0.97837 | -0.16344 | 61.6561 | 0.23032 | 61.5599 | -0.023943 | 0.052814 | 61.6165 | 0.021456 | 61.3993 | 61.9658 | 61.6111 | 61.8915 | 62.2172 | 62.2418 | 62.4881 | 61.3463 | 123.1658 | 61.74 | 123.0696 | 61.4858 | 61.5625 | 123.1262 | 61.5312 | 122.909 | 61.6033 | 61.6347 | 61.5071 | 61.5385
7267.0625 | 123.3582 | -61.5005 | 61.6013 | 0.12643 | -0.16415 | 0.015472 | 0.31837 | 0.34757 | 0.6533 | -0.43813 | 61.6836 | 0.2349 | 61.592 | -0.033101 | 0.048236 | 61.5936 | 0.003143 | 61.3718 | 61.627 | 61.3364 | 61.516 | 61.8189 | 61.8481 | 62.1539 | 61.0624 | 123.1842 | 61.7354 | 123.0925 | 61.4674 | 61.5488 | 123.0942 | 61.5037 | 122.8724 | 61.6354 | 61.6805 | 61.5437 | 61.5888
7268.0938 | 123.3032 | -61.4594 | 61.6379 | 0.24089 | -0.067994 | 0.12994 | 0.4603 | 0.48033 | 0.76776 | -0.32825 | 61.679 | 0.2349 | 61.6011 | -0.023943 | 0.057392 | 61.5982 | 0.007721 | 61.3856 | 61.7002 | 61.3914 | 61.5893 | 61.9197 | 61.9397 | 62.2271 | 61.1311 | 123.1384 | 61.6942 | 123.0605 | 61.4354 | 61.5167 | 123.0576 | 61.4671 | 122.8449 | 61.6216 | 61.6713 | 61.5437 | 61.5934
7269.0625 | 123.2758 | -61.5051 | 61.6333 | 0.26836 | -0.0451 | 0.16657 | 0.49693 | 0.51237 | 0.79523 | -0.32367 | 61.6699 | 0.2349 | 61.5874 | -0.023943 | 0.048236 | 61.6074 | 0.007721 | 61.381 | 61.7735 | 61.46 | 61.6717 | 62.0021 | 62.0175 | 62.3004 | 61.1815 | 123.175 | 61.74 | 123.0925 | 61.4812 | 61.5534 | 123.1125 | 61.5128 | 122.8861 | 61.6216 | 61.6622 | 61.5392 | 61.5797
7270.0938 | 123.2895 | -61.5417 | 61.6241 | 0.57969 | 0.21589 | 0.52828 | 0.84948 | 0.87861 | 1.0745 | -0.10392 | 61.6561 | 0.2349 | 61.5553 | -0.028522 | 0.048236 | 61.6165 | 0.012299 | 61.3993 | 62.1214 | 61.7576 | 62.07 | 62.3912 | 62.4204 | 62.6163 | 61.4378 | 123.1979 | 61.7766 | 123.0971 | 61.5132 | 61.59 | 123.1583 | 61.554 | 122.941 | 61.6079 | 61.6438 | 61.5071 | 61.543
7271.0625 | 123.2666 | -61.528 | 61.615 | 0.63921 | 0.28 | 0.5878 | 0.91358 | 0.93812 | 1.1386 | -0.035248 | 61.6561 | 0.23948 | 61.5645 | -0.019364 | 0.048236 | 61.6165 | 0.007721 | 61.4039 | 62.1672 | 61.808 | 62.1158 | 62.4416 | 62.4661 | 62.6666 | 61.4928 | 123.1842 | 61.7675 | 123.0925 | 61.5087 | 61.5763 | 123.1445 | 61.5357 | 122.9319 | 61.6079 | 61.6484 | 61.5163 | 61.5568
7272.0938 | 123.2986 | -61.5143 | 61.615 | 0.76282 | 0.38989 | 0.70684 | 1.0326 | 1.0617 | 1.2622 | 0.097519 | 61.6516 | 0.2349 | 61.5782 | -0.028522 | 0.052814 | 61.6303 | 0.012299 | 61.413 | 62.2771 | 61.9042 | 62.2211 | 62.5469 | 62.576 | 62.7765 | 61.6118 | 123.1658 | 61.7492 | 123.0925 | 61.4858 | 61.5671 | 123.1445 | 61.5266 | 122.9273 | 61.5987 | 61.6393 | 61.5254 | 61.5659
7273.0625 | 123.2895 | -61.528 | 61.5875 | 0.81777 | 0.44941 | 0.77094 | 1.083 | 1.1075 | 1.3172 | 0.12041 | 61.6424 | 0.24405 | 61.5553 | -0.023943 | 0.048236 | 61.6348 | 0.016878 | 61.4268 | 62.3458 | 61.9774 | 62.299 | 62.611 | 62.6355 | 62.8452 | 61.6484 | 123.1704 | 61.7721 | 123.0834 | 61.5041 | 61.5763 | 123.1628 | 61.5449 | 122.9548 | 61.5942 | 61.6255 | 61.5071 | 61.5385
7274.0938 | 123.2849 | -61.5189 | 61.647 | 0.60258 | 0.2571 | 0.55575 | 0.85405 | 0.88319 | 1.0928 | -0.062717 | 61.6561 | 0.2349 | 61.5553 | -0.019364 | 0.052814 | 61.6257 | 0.007721 | 61.4039 | 62.1214 | 61.776 | 62.0746 | 62.3729 | 62.402 | 62.6117 | 61.4561 | 123.175 | 61.7538 | 123.0742 | 61.4995 | 61.5717 | 123.1445 | 61.5266 | 122.9227 | 61.6033 | 61.6484 | 61.5025 | 61.5476
7275.0625 | 123.349 | -61.5051 | 61.6196 | 0.80403 | 0.43568 | 0.76178 | 1.0692 | 1.0846 | 1.276 | 0.1021 | 61.6332 | 0.22574 | 61.5279 | -0.028522 | 0.048236 | 61.6303 | 0.016878 | 61.4222 | 62.3092 | 61.9408 | 62.2669 | 62.5744 | 62.5897 | 62.7811 | 61.6072 | 123.1384 | 61.7309 | 123.033 | 61.4766 | 61.5534 | 123.1354 | 61.522 | 122.9273 | 61.585 | 61.6164 | 61.4796 | 61.511
7276.0781 | 123.2803 | -61.5051 | 61.615 | 0.65752 | 0.28458 | 0.59696 | 0.94105 | 0.95186 | 1.1432 | -0.035248 | 61.6516 | 0.2349 | 61.5508 | -0.028522 | 0.052814 | 61.6303 | 0.016878 | 61.4084 | 62.1626 | 61.7897 | 62.1021 | 62.4462 | 62.457 | 62.6483 | 61.4699 | 123.1567 | 61.74 | 123.0559 | 61.4766 | 61.5579 | 123.1354 | 61.522 | 122.9136 | 61.5987 | 61.6347 | 61.4979 | 61.5339
7277.0625 | 123.2712 | -61.5143 | 61.6058 | 0.73993 | 0.38073 | 0.69768 | 1.0326 | 1.048 | 1.2393 | 0.042581 | 61.647 | 0.2349 | 61.5645 | -0.028522 | 0.048236 | 61.6394 | 0.016878 | 61.4084 | 62.2542 | 61.895 | 62.212 | 62.5469 | 62.5623 | 62.7536 | 61.5569 | 123.1613 | 61.7492 | 123.0788 | 61.4858 | 61.5625 | 123.1537 | 61.5312 | 122.9227 | 61.5987 | 61.6301 | 61.5163 | 61.5476
7278.0781 | 123.2895 | -61.528 | 61.5967 | 0.83608 | 0.45399 | 0.77552 | 1.0967 | 1.1212 | 1.308 | 0.1433 | 61.647 | 0.23032 | 61.5737 | -0.028522 | 0.048236 | 61.6348 | 0.012299 | 61.4176 | 62.3641 | 61.982 | 62.3035 | 62.6247 | 62.6493 | 62.836 | 61.6713 | 123.175 | 61.7583 | 123.1017 | 61.4995 | 61.5763 | 123.1628 | 61.5403 | 122.9456 | 61.5987 | 61.6347 | 61.5254 | 61.5614
7279.0625 | 123.2986 | -61.496 | 61.5829 | 0.78114 | 0.42194 | 0.73431 | 1.0418 | 1.0572 | 1.276 | 0.11125 | 61.6516 | 0.2349 | 61.5782 | -0.028522 | 0.057392 | 61.6303 | 0.012299 | 61.413 | 62.2771 | 61.9179 | 62.2303 | 62.5377 | 62.5531 | 62.7719 | 61.6072 | 123.1475 | 61.7309 | 123.0742 | 61.4674 | 61.5534 | 123.1262 | 61.5083 | 122.909 | 61.5942 | 61.6393 | 61.5208 | 61.5659
7280.0625 | 123.349 | -61.496 | 61.5692 | 0.75367 | 0.38989 | 0.6931 | 1.0189 | 1.0343 | 1.2393 | 0.065472 | 61.647 | 0.23032 | 61.5508 | -0.033101 | 0.043657 | 61.6348 | 0.007721 | 61.4176 | 62.2496 | 61.8859 | 62.1891 | 62.5149 | 62.5302 | 62.7353 | 61.5614 | 123.143 | 61.7263 | 123.0467 | 61.4629 | 61.5396 | 123.1308 | 61.5037 | 122.9136 | 61.6033 | 61.6393 | 61.5071 | 61.543
7281.0938 | 123.2849 | -61.5005 | 61.6013 | 0.8315 | 0.46773 | 0.7801 | 1.083 | 1.1212 | 1.3126 | 0.13414 | 61.6378 | 0.22574 | 61.5416 | -0.023943 | 0.052814 | 61.6348 | 0.007721 | 61.4176 | 62.3321 | 61.9683 | 62.2806 | 62.5835 | 62.6218 | 62.8131 | 61.6347 | 123.1384 | 61.7263 | 123.0422 | 61.4766 | 61.5534 | 123.1354 | 61.5083 | 122.9181 | 61.585 | 61.6301 | 61.4888 | 61.5339
7282.0625 | 123.2574 | -61.5234 | 61.6104 | 0.77198 | 0.40363 | 0.716 | 1.0555 | 1.08 | 1.2622 | 0.088362 | 61.647 | 0.2349 | 61.5416 | -0.028522 | 0.048236 | 61.6257 | 0.007721 | 61.413 | 62.2954 | 61.9271 | 62.2394 | 62.5789 | 62.6035 | 62.7857 | 61.6118 | 123.1704 | 61.7583 | 123.065 | 61.4949 | 61.5717 | 123.1491 | 61.5312 | 122.9365 | 61.5987 | 61.6393 | 61.4934 | 61.5339
7283.0781 | 123.2803 | -61.4685 | 61.6608 | 0.5568 | 0.193 | 0.48249 | 0.81743 | 0.84198 | 1.0425 | -0.10392 | 61.6561 | 0.23032 | 61.5737 | -0.023943 | 0.052814 | 61.6257 | 0.016878 | 61.4039 | 62.0253 | 61.6615 | 61.951 | 62.2859 | 62.3105 | 62.511 | 61.3646 | 123.1246 | 61.6988 | 123.0422 | 61.4446 | 61.5213 | 123.0942 | 61.4854 | 122.8724 | 61.6033 | 61.6393 | 61.5208 | 61.5568
7284.0625 | 123.2941 | -61.528 | 61.615 | 0.55222 | 0.19758 | 0.48707 | 0.83116 | 0.85114 | 1.0425 | -0.1085 | 61.6699 | 0.2349 | 61.592 | -0.028522 | 0.048236 | 61.6119 | 0.003143 | 61.3993 | 62.0802 | 61.7256 | 62.0151 | 62.3592 | 62.3792 | 62.5705 | 61.4195 | 123.1979 | 61.7629 | 123.12 | 61.4995 | 61.5763 | 123.14 | 61.5312 | 122.9273 | 61.6216 | 61.6667 | 61.5437 | 61.5888
7285.0625 | 123.3307 | -61.528 | 61.5692 | 0.67584 | 0.31205 | 0.62901 | 0.9502 | 0.97932 | 1.1523 | -0.021514 | 61.6561 | 0.2349 | 61.5737 | -0.028522 | 0.039079 | 61.6211 | 0.012299 | 61.4084 | 62.2039 | 61.8401 | 62.157 | 62.4782 | 62.5073 | 62.6804 | 61.5065 | 123.1842 | 61.7629 | 123.1017 | 61.4995 | 61.5671 | 123.1491 | 61.5403 | 122.9365 | 61.6171 | 61.6438 | 61.5346 | 61.5614
7286.0781 | 123.1934 | -61.5143 | 61.6333 | 0.85897 | 0.49062 | 0.81215 | 1.1288 | 1.1533 | 1.3446 | 0.16619 | 61.6424 | 0.22116 | 61.5416 | -0.033101 | 0.052814 | 61.6348 | 0.007721 | 61.4268 | 62.3733 | 62.0049 | 62.3264 | 62.643 | 62.6676 | 62.8589 | 61.6805 | 123.1567 | 61.7354 | 123.0559 | 61.4812 | 61.5671 | 123.1491 | 61.522 | 122.941 | 61.5896 | 61.6347 | 61.4888 | 61.5339
7287.0625 | 123.2712 | -61.5509 | 61.5921 | 0.94138 | 0.57762 | 0.89914 | 1.2112 | 1.2403 | 1.4133 | 0.23944 | 61.6287 | 0.22574 | 61.5324 | -0.028522 | 0.048236 | 61.6394 | 0.012299 | 61.4268 | 62.4923 | 62.1285 | 62.45 | 62.7621 | 62.7912 | 62.9642 | 61.7903 | 123.1796 | 61.7766 | 123.0834 | 61.5224 | 61.5991 | 123.1903 | 61.5632 | 122.9777 | 61.5804 | 61.6164 | 61.4842 | 61.5202
7288.0938 | 123.2666 | -61.496 | 61.6425 | 0.75825 | 0.39447 | 0.72515 | 1.0189 | 1.0526 | 1.2164 | 0.033424 | 61.647 | 0.22116 | 61.5508 | -0.023943 | 0.048236 | 61.6257 | 0.012299 | 61.4176 | 62.2542 | 61.8904 | 62.2211 | 62.5149 | 62.5485 | 62.7124 | 61.5294 | 123.143 | 61.7171 | 123.0467 | 61.472 | 61.5442 | 123.1216 | 61.5083 | 122.9136 | 61.5987 | 61.6347 | 61.5025 | 61.5385
7289.0625 | 123.2529 | -61.528 | 61.6196 | 0.87728 | 0.49978 | 0.83962 | 1.1517 | 1.1762 | 1.3401 | 0.1433 | 61.6332 | 0.23032 | 61.5782 | -0.019364 | 0.048236 | 61.6394 | 0.003143 | 61.413 | 62.4053 | 62.0278 | 62.3676 | 62.6797 | 62.7042 | 62.8681 | 61.6713 | 123.1613 | 61.7583 | 123.1062 | 61.5087 | 61.5763 | 123.1674 | 61.5312 | 122.941 | 61.585 | 61.6301 | 61.53 | 61.5751
7290.0938 | 123.4039 | -61.4914 | 61.5463 | 1.0192 | 0.65546 | 0.97698 | 1.289 | 1.3044 | 1.4637 | 0.29896 | 61.6332 | 0.2349 | 61.5279 | -0.028522 | 0.052814 | 61.6486 | 0.007721 | 61.4222 | 62.5106 | 62.1469 | 62.4684 | 62.7804 | 62.7958 | 62.9551 | 61.7904 | 123.1246 | 61.7263 | 123.0193 | 61.4629 | 61.5442 | 123.14 | 61.4991 | 122.9136 | 61.5804 | 61.6255 | 61.4751 | 61.5202
7291.0625 | 123.2712 | -61.5646 | 61.5692 | 1.0787 | 0.73788 | 1.0502 | 1.3531 | 1.3776 | 1.5232 | 0.35847 | 61.6195 | 0.22116 | 61.537 | -0.028522 | 0.048236 | 61.6486 | 0.007721 | 61.4268 | 62.6434 | 62.3025 | 62.6149 | 62.9177 | 62.9422 | 63.0878 | 61.9231 | 123.1841 | 61.7858 | 123.1017 | 61.5361 | 61.6129 | 123.2132 | 61.5724 | 122.9914 | 61.5713 | 61.6118 | 61.4888 | 61.5293
7292.0781 | 123.3582 | -61.4914 | 61.6013 | 0.94596 | 0.59136 | 0.92204 | 1.2066 | 1.2265 | 1.3492 | 0.20739 | 61.6332 | 0.2349 | 61.5553 | -0.019364 | 0.052814 | 61.6394 | 0.012299 | 61.4222 | 62.4374 | 62.0827 | 62.4134 | 62.698 | 62.7179 | 62.8406 | 61.6988 | 123.1246 | 61.7263 | 123.0467 | 61.472 | 61.5442 | 123.1308 | 61.5037 | 122.9136 | 61.5804 | 61.6209 | 61.5025 | 61.543
7293.0625 | 123.3398 | -61.5555 | 61.5646 | 1.1795 | 0.82488 | 1.1693 | 1.4401 | 1.4737 | 1.5965 | 0.41799 | 61.6287 | 0.2349 | 61.5416 | -0.033101 | 0.057392 | 61.6577 | 0.016878 | 61.4405 | 62.7349 | 62.3804 | 62.7248 | 62.9956 | 63.0292 | 63.1519 | 61.9735 | 123.1842 | 61.7904 | 123.0971 | 61.5224 | 61.6129 | 123.2132 | 61.5724 | 122.996 | 61.5713 | 61.6118 | 61.4842 | 61.5247
7294.0781 | 123.3444 | -61.528 | 61.5784 | 1.2024 | 0.85693 | 1.183 | 1.4584 | 1.4875 | 1.6285 | 0.45462 | 61.6195 | 0.22574 | 61.5187 | -0.028522 | 0.043657 | 61.6531 | 0.012299 | 61.4451 | 62.7304 | 62.3849 | 62.711 | 62.9864 | 63.0155 | 63.1565 | 61.9826 | 123.1475 | 61.7538 | 123.0467 | 61.4995 | 61.5717 | 123.1812 | 61.5403 | 122.9731 | 61.5759 | 61.6072 | 61.4751 | 61.5064
7295.0625 | 123.3261 | -61.528 | 61.5555 | 0.98717 | 0.66462 | 0.94493 | 1.2112 | 1.2403 | 1.4179 | 0.27607 | 61.6424 | 0.23032 | 61.5462 | -0.028522 | 0.048236 | 61.6394 | 0.012299 | 61.4222 | 62.5152 | 62.1926 | 62.4729 | 62.7392 | 62.7683 | 62.9459 | 61.8041 | 123.1704 | 61.7583 | 123.0742 | 61.4995 | 61.5763 | 123.1674 | 61.5403 | 122.9502 | 61.5942 | 61.6301 | 61.4979 | 61.5339
7296.0781 | 123.3261 | -61.5097 | 61.6058 | 0.85897 | 0.55473 | 0.83962 | 1.0921 | 1.1029 | 1.2805 | 0.15246 | 61.6424 | 0.23948 | 61.5737 | -0.023943 | 0.052814 | 61.6394 | 0.016878 | 61.4176 | 62.3687 | 62.0644 | 62.3493 | 62.6018 | 62.6126 | 62.7902 | 61.6622 | 123.1521 | 61.7492 | 123.0834 | 61.4858 | 61.5625 | 123.1491 | 61.5266 | 122.9273 | 61.5896 | 61.6255 | 61.5208 | 61.5568
7297.0625 | 123.262 | -61.5555 | 61.5829 | 0.91849 | 0.61425 | 0.89456 | 1.1471 | 1.1762 | 1.308 | 0.18908 | 61.6332 | 0.23032 | 61.5416 | -0.023943 | 0.052814 | 61.6394 | 0.012299 | 61.413 | 62.474 | 62.1697 | 62.45 | 62.7026 | 62.7317 | 62.8635 | 61.7446 | 123.1887 | 61.7858 | 123.0971 | 61.5315 | 61.6083 | 123.1949 | 61.5678 | 122.9685 | 61.5804 | 61.6209 | 61.4888 | 61.5293
7298.0781 | 123.2346 | -61.4914 | 61.615 | 0.69873 | 0.41278 | 0.67937 | 0.92273 | 0.95186 | 1.1066 | 0.015112 | 61.6424 | 0.22574 | 61.5462 | -0.019364 | 0.043657 | 61.6211 | 0.012299 | 61.4084 | 62.1901 | 61.9042 | 62.1708 | 62.4141 | 62.4432 | 62.598 | 61.5065 | 123.1338 | 61.7171 | 123.0376 | 61.472 | 61.5351 | 123.1125 | 61.5037 | 122.8998 | 61.5987 | 61.6301 | 61.5025 | 61.5339
7299.0625 | 123.2758 | -61.4914 | 61.6196 | 0.73078 | 0.44026 | 0.68395 | 0.93189 | 0.96559 | 1.1432 | 0.051737 | 61.6516 | 0.2349 | 61.5737 | -0.028522 | 0.048236 | 61.6257 | 0.012299 | 61.4084 | 62.2222 | 61.9316 | 62.1753 | 62.4233 | 62.457 | 62.6346 | 61.5431 | 123.143 | 61.7263 | 123.065 | 61.4629 | 61.5396 | 123.1171 | 61.5037 | 122.8998 | 61.6033 | 61.6393 | 61.5254 | 61.5614
7300.0938 | 123.3536 | -61.496 | 61.5738 | 1.0787 | 0.77451 | 1.0548 | 1.3119 | 1.3364 | 1.4637 | 0.34016 | 61.6332 | 0.23948 | 61.5599 | -0.028522 | 0.052814 | 61.6348 | 0.012299 | 61.4268 | 62.5747 | 62.2705 | 62.5508 | 62.8079 | 62.8324 | 62.9597 | 61.8361 | 123.1292 | 61.7354 | 123.0559 | 61.4674 | 61.5488 | 123.1308 | 61.5083 | 122.9227 | 61.5804 | 61.6209 | 61.5071 | 61.5476
7301.0625 | 123.317 | -61.5372 | 61.5921 | 1.0192 | 0.69667 | 1.009 | 1.2524 | 1.286 | 1.4133 | 0.26691 | 61.6287 | 0.23032 | 61.5324 | -0.023943 | 0.052814 | 61.644 | 0.007721 | 61.4268 | 62.5564 | 62.2338 | 62.5462 | 62.7896 | 62.8232 | 62.9505 | 61.8041 | 123.1658 | 61.7675 | 123.0696 | 61.5132 | 61.59 | 123.1812 | 61.5449 | 122.9639 | 61.5759 | 61.6209 | 61.4796 | 61.5247
7302.0938 | 123.317 | -61.5051 | 61.5829 | 0.98717 | 0.67378 | 0.97698 | 1.2295 | 1.2448 | 1.3721 | 0.23486 | 61.6241 | 0.23032 | 61.5324 | -0.023943 | 0.048236 | 61.6394 | 0.007721 | 61.4268 | 62.4923 | 62.1789 | 62.4821 | 62.7346 | 62.75 | 62.8772 | 61.74 | 123.1292 | 61.7354 | 123.0376 | 61.4812 | 61.5534 | 123.1445 | 61.5128 | 122.9319 | 61.5759 | 61.6164 | 61.4842 | 61.5247
7303.0625 | 123.2712 | -61.5463 | 61.5967 | 1.3077 | 0.99429 | 1.3158 | 1.5546 | 1.579 | 1.6743 | 0.5416 | 61.6195 | 0.2349 | 61.5553 | -0.023943 | 0.043657 | 61.6623 | 0.012299 | 61.4405 | 62.854 | 62.5406 | 62.8621 | 63.1009 | 63.1254 | 63.2206 | 62.0879 | 123.1658 | 61.7812 | 123.1017 | 61.5224 | 61.59 | 123.2086 | 61.5586 | 122.9868 | 61.5759 | 61.6072 | 61.5117 | 61.543
7304.0781 | 123.3856 | -61.4914 | 61.5692 | 1.1474 | 0.83861 | 1.1418 | 1.3897 | 1.4142 | 1.5278 | 0.39052 | 61.6241 | 0.23032 | 61.5324 | -0.028522 | 0.057392 | 61.6486 | 0.021456 | 61.4313 | 62.6388 | 62.33 | 62.6332 | 62.8811 | 62.9056 | 63.0192 | 61.8819 | 123.1155 | 61.7217 | 123.0238 | 61.4629 | 61.5488 | 123.14 | 61.5129 | 122.9227 | 61.5667 | 61.6026 | 61.4751 | 61.511
7305.0625 | 123.3765 | -61.5372 | 61.5097 | 1.0284 | 0.70583 | 1.0136 | 1.2707 | 1.2952 | 1.4133 | 0.26691 | 61.6332 | 0.22574 | 61.5233 | -0.028522 | 0.048236 | 61.644 | 0.012299 | 61.4268 | 62.5655 | 62.243 | 62.5508 | 62.8079 | 62.8324 | 62.9505 | 61.8041 | 123.1704 | 61.7629 | 123.0605 | 61.5086 | 61.5854 | 123.1812 | 61.5495 | 122.9639 | 61.585 | 61.6209 | 61.4751 | 61.511
7306.0938 | 123.3353 | -61.5097 | 61.5646 | 1.2802 | 0.95766 | 1.2654 | 1.5317 | 1.5516 | 1.688 | 0.53702 | 61.6241 | 0.23948 | 61.5187 | -0.028522 | 0.048236 | 61.6623 | 0.012299 | 61.4405 | 62.7899 | 62.4674 | 62.7751 | 63.0414 | 63.0613 | 63.1977 | 62.0467 | 123.1338 | 61.7492 | 123.0284 | 61.4812 | 61.5579 | 123.172 | 61.522 | 122.9502 | 61.5759 | 61.6118 | 61.4705 | 61.5064
7307.0625 | 123.2986 | -61.528 | 61.5875 | 1.2115 | 0.8844 | 1.2105 | 1.4813 | 1.5012 | 1.6102 | 0.45004 | 61.6241 | 0.23948 | 61.5553 | -0.028522 | 0.048236 | 61.6531 | 0.016878 | 61.4359 | 62.7395 | 62.4124 | 62.7385 | 63.0093 | 63.0292 | 63.1382 | 61.9781 | 123.1521 | 61.7675 | 123.0834 | 61.4995 | 61.5763 | 123.1812 | 61.5449 | 122.9639 | 61.5759 | 61.6072 | 61.5071 | 61.5385
7308.0625 | 123.2941 | -61.5509 | 61.5967 | 1.2985 | 0.9714 | 1.2883 | 1.55 | 1.579 | 1.6926 | 0.52329 | 61.6149 | 0.2349 | 61.5187 | -0.019364 | 0.048236 | 61.6669 | 0.016878 | 61.4405 | 62.8494 | 62.5223 | 62.8392 | 63.1009 | 63.1299 | 63.2435 | 62.0742 | 123.1658 | 61.7858 | 123.0696 | 61.5315 | 61.5991 | 123.2178 | 61.5678 | 122.9914 | 61.5667 | 61.5981 | 61.4705 | 61.5018
7309.0938 | 123.2986 | -61.5601 | 61.6058 | 1.3443 | 1.0126 | 1.3204 | 1.5866 | 1.6111 | 1.7384 | 0.57823 | 61.6149 | 0.23032 | 61.5141 | -0.023943 | 0.052814 | 61.6623 | 0.012299 | 61.4405 | 62.9043 | 62.5727 | 62.8804 | 63.1467 | 63.1711 | 63.2984 | 62.1383 | 123.175 | 61.7904 | 123.0742 | 61.5361 | 61.6129 | 123.2224 | 61.5724 | 123.0006 | 61.5621 | 61.6026 | 61.4613 | 61.5018
7310.0625 | 123.3856 | -61.528 | 61.5417 | 1.2436 | 0.92561 | 1.2242 | 1.4859 | 1.5149 | 1.6514 | 0.49582 | 61.6149 | 0.2349 | 61.5462 | -0.028522 | 0.052814 | 61.6577 | 0.007721 | 61.4313 | 62.7716 | 62.4536 | 62.7522 | 63.0139 | 63.043 | 63.1794 | 62.0238 | 123.1429 | 61.7629 | 123.0742 | 61.4995 | 61.5808 | 123.1857 | 61.5357 | 122.9594 | 61.5621 | 61.6072 | 61.4934 | 61.5385
7311.0781 | 123.3719 | -61.528 | 61.5555 | 1.3305 | 1.0034 | 1.3112 | 1.5775 | 1.6019 | 1.7292 | 0.57823 | 61.6149 | 0.2349 | 61.5416 | -0.023943 | 0.043657 | 61.6669 | 0.007721 | 61.4405 | 62.8586 | 62.5315 | 62.8392 | 63.1055 | 63.1299 | 63.2572 | 62.1062 | 123.1429 | 61.7629 | 123.0696 | 61.5041 | 61.5717 | 123.1949 | 61.5357 | 122.9685 | 61.5713 | 61.6072 | 61.4979 | 61.5339
7312.0625 | 123.262 | -61.5326 | 61.5967 | 1.1428 | 0.80656 | 1.1281 | 1.3943 | 1.4234 | 1.5369 | 0.36763 | 61.6241 | 0.22574 | 61.5324 | -0.028522 | 0.048236 | 61.6531 | 0.007721 | 61.4359 | 62.6754 | 62.3392 | 62.6607 | 62.9269 | 62.956 | 63.0695 | 61.9002 | 123.1567 | 61.7583 | 123.065 | 61.5041 | 61.5808 | 123.1857 | 61.5403 | 122.9685 | 61.5759 | 61.6164 | 61.4842 | 61.5247
7313.0938 | 123.1476 | -61.5829 | 61.4777 | 1.1108 | 0.78824 | 1.1098 | 1.3714 | 1.4005 | 1.4911 | 0.32185 | 61.6241 | 0.2349 | 61.537 | -0.028522 | 0.052814 | 61.6531 | 0.003143 | 61.4313 | 62.6937 | 62.3712 | 62.6927 | 62.9544 | 62.9834 | 63.0741 | 61.9048 | 123.207 | 61.8178 | 123.12 | 61.5544 | 61.6358 | 123.2361 | 61.5861 | 123.0143 | 61.5713 | 61.6209 | 61.4842 | 61.5339
7314.0625 | 123.2803 | -61.5143 | 61.6058 | 1.065 | 0.74246 | 1.0502 | 1.3027 | 1.3364 | 1.4362 | 0.27607 | 61.6378 | 0.2349 | 61.5462 | -0.033101 | 0.052814 | 61.6486 | 0.007721 | 61.4359 | 62.5793 | 62.2567 | 62.5645 | 62.817 | 62.8507 | 62.9505 | 61.7904 | 123.1521 | 61.7492 | 123.0605 | 61.4812 | 61.5671 | 123.1628 | 61.522 | 122.9502 | 61.585 | 61.6301 | 61.4934 | 61.5385
7315.0938 | 123.2803 | -61.5234 | 61.5829 | 0.79945 | 0.4952 | 0.78468 | 1.0464 | 1.08 | 1.189 | 0.042581 | 61.6332 | 0.22116 | 61.5324 | -0.028522 | 0.052814 | 61.6348 | 0.007721 | 61.413 | 62.3229 | 62.0186 | 62.3081 | 62.5698 | 62.6035 | 62.7124 | 61.566 | 123.1567 | 61.7446 | 123.0559 | 61.4949 | 61.5763 | 123.1583 | 61.5312 | 122.9365 | 61.5804 | 61.6255 | 61.4796 | 61.5247
7316.0625 | 123.2483 | -61.5417 | 61.6196 | 1.0146 | 0.68751 | 0.99529 | 1.2753 | 1.286 | 1.395 | 0.22113 | 61.6424 | 0.2349 | 61.5553 | -0.028522 | 0.052814 | 61.6394 | 0.012299 | 61.4176 | 62.5564 | 62.2293 | 62.537 | 62.817 | 62.8278 | 62.9367 | 61.7629 | 123.1842 | 61.7766 | 123.0971 | 61.5132 | 61.5946 | 123.1812 | 61.554 | 122.9593 | 61.5896 | 61.6301 | 61.5025 | 61.543
7317.0781 | 123.3627 | -61.4822 | 61.5875 | 0.73993 | 0.43568 | 0.72058 | 0.9731 | 0.99764 | 1.1203 | -0.016936 | 61.6378 | 0.23032 | 61.5462 | -0.023943 | 0.048236 | 61.6211 | 0.012299 | 61.413 | 62.2222 | 61.9179 | 62.2028 | 62.4553 | 62.4799 | 62.6025 | 61.4653 | 123.1201 | 61.7126 | 123.0284 | 61.4583 | 61.5305 | 123.1033 | 61.4945 | 122.8953 | 61.5896 | 61.6255 | 61.4979 | 61.5339
7318.0625 | 123.3398 | -61.5326 | 61.5738 | 0.66668 | 0.37157 | 0.63816 | 0.89068 | 0.91523 | 1.0608 | -0.058139 | 61.647 | 0.23032 | 61.5691 | -0.028522 | 0.043657 | 61.6257 | 0.012299 | 61.4039 | 62.1993 | 61.9042 | 62.1708 | 62.4233 | 62.4478 | 62.5934 | 61.4745 | 123.1796 | 61.7629 | 123.1017 | 61.5041 | 61.5763 | 123.1583 | 61.5449 | 122.9365 | 61.6033 | 61.6347 | 61.5254 | 61.5568
7319.0938 | 123.349 | -61.4731 | 61.5829 | 0.84524 | 0.53641 | 0.82588 | 1.0921 | 1.1167 | 1.2256 | 0.088362 | 61.6378 | 0.23032 | 61.5553 | -0.028522 | 0.048236 | 61.6394 | 0.021456 | 61.4222 | 62.3183 | 62.0095 | 62.299 | 62.5652 | 62.5897 | 62.6987 | 61.5614 | 123.1109 | 61.7034 | 123.0284 | 61.4446 | 61.5213 | 123.1125 | 61.4945 | 122.8953 | 61.5896 | 61.6164 | 61.5071 | 61.5339
7320.0625 | 123.2758 | -61.496 | 61.6058 | 0.75367 | 0.43568 | 0.73889 | 1.0006 | 1.0159 | 1.1386 | 0.001377 | 61.6424 | 0.23948 | 61.5416 | -0.023943 | 0.048236 | 61.6303 | 0.007721 | 61.413 | 62.2496 | 61.9316 | 62.2349 | 62.4965 | 62.5119 | 62.6346 | 61.4973 | 123.1384 | 61.7354 | 123.0376 | 61.472 | 61.5442 | 123.1262 | 61.5037 | 122.909 | 61.5942 | 61.6347 | 61.4934 | 61.5339
7321.0938 | 123.4085 | -61.4639 | 61.5692 | 1.033 | 0.7104 | 1.0365 | 1.2936 | 1.3089 | 1.395 | 0.25318 | 61.6241 | 0.23032 | 61.5691 | -0.023943 | 0.043657 | 61.644 | 0.012299 | 61.4313 | 62.4969 | 62.1743 | 62.5004 | 62.7575 | 62.7729 | 62.8589 | 61.7171 | 123.088 | 61.6942 | 123.033 | 61.44 | 61.5076 | 123.1079 | 61.4762 | 122.8953 | 61.5804 | 61.6118 | 61.5254 | 61.5568
7322.0625 | 123.2574 | -61.5417 | 61.6104 | 1.097 | 0.77909 | 1.0869 | 1.344 | 1.3776 | 1.4545 | 0.32185 | 61.6287 | 0.23032 | 61.5279 | -0.023943 | 0.052814 | 61.6531 | 0.012299 | 61.4313 | 62.6388 | 62.3208 | 62.6286 | 62.8857 | 62.9194 | 62.9963 | 61.8636 | 123.1704 | 61.7721 | 123.0696 | 61.5178 | 61.5946 | 123.1949 | 61.554 | 122.9731 | 61.5759 | 61.6164 | 61.4751 | 61.5156
7323.0938 | 123.262 | -61.5417 | 61.6013 | 1.1795 | 0.86608 | 1.1784 | 1.4355 | 1.4554 | 1.5324 | 0.3951 | 61.6241 | 0.24405 | 61.5324 | -0.023943 | 0.052814 | 61.6486 | 0.016878 | 61.4405 | 62.7212 | 62.4078 | 62.7202 | 62.9773 | 62.9972 | 63.0741 | 61.9368 | 123.1658 | 61.7858 | 123.0742 | 61.5178 | 61.5946 | 123.1903 | 61.5586 | 122.9822 | 61.5713 | 61.6072 | 61.4796 | 61.5156
7324.0625 | 123.2895 | -61.528 | 61.647 | 1.0284 | 0.70125 | 0.99529 | 1.2707 | 1.2952 | 1.395 | 0.25776 | 61.6287 | 0.2349 | 61.5416 | -0.019364 | 0.052814 | 61.644 | 0.016878 | 61.4222 | 62.5564 | 62.2293 | 62.5233 | 62.7987 | 62.8232 | 62.923 | 61.7858 | 123.1567 | 61.7629 | 123.0696 | 61.5087 | 61.5808 | 123.172 | 61.5449 | 122.9502 | 61.5759 | 61.6118 | 61.4888 | 61.5247
7325.0938 | 123.3353 | -61.5143 | 61.5326 | 1.0101 | 0.70583 | 1.0045 | 1.2524 | 1.2769 | 1.3721 | 0.2486 | 61.6241 | 0.22574 | 61.5279 | -0.023943 | 0.048236 | 61.6394 | 0.012299 | 61.4222 | 62.5243 | 62.2201 | 62.5187 | 62.7667 | 62.7912 | 62.8864 | 61.7629 | 123.1384 | 61.74 | 123.0422 | 61.4903 | 61.5625 | 123.1537 | 61.5266 | 122.9365 | 61.5759 | 61.6118 | 61.4796 | 61.5156
7326.0625 | 123.2437 | -61.5326 | 61.6287 | 0.89102 | 0.60967 | 0.85794 | 1.1013 | 1.1304 | 1.2622 | 0.15704 | 61.6378 | 0.2349 | 61.5416 | -0.019364 | 0.048236 | 61.6348 | 0.012299 | 61.4222 | 62.4236 | 62.1423 | 62.3905 | 62.6339 | 62.663 | 62.7948 | 61.6896 | 123.1704 | 61.7675 | 123.0742 | 61.5132 | 61.5808 | 123.1674 | 61.5449 | 122.9548 | 61.5896 | 61.6255 | 61.4934 | 61.5293
7327.0938 | 123.3719 | -61.496 | 61.5875 | 0.75825 | 0.46315 | 0.72058 | 0.9731 | 1.0022 | 1.1249 | 0.01969 | 61.6516 | 0.2349 | 61.5828 | -0.028522 | 0.052814 | 61.6257 | 0.021456 | 61.3993 | 62.2542 | 61.9591 | 62.2165 | 62.4691 | 62.4982 | 62.6208 | 61.5157 | 123.1475 | 61.7309 | 123.0788 | 61.4674 | 61.5488 | 123.1216 | 61.5174 | 122.8953 | 61.5987 | 61.6301 | 61.53 | 61.5614
7328.0625 | 123.2529 | -61.5326 | 61.6608 | 0.90018 | 0.60509 | 0.88083 | 1.1379 | 1.1624 | 1.2576 | 0.15704 | 61.6424 | 0.2349 | 61.5462 | -0.028522 | 0.048236 | 61.6348 | 0.012299 | 61.413 | 62.4328 | 62.1377 | 62.4134 | 62.6705 | 62.695 | 62.7902 | 61.6896 | 123.175 | 61.7675 | 123.0788 | 61.5041 | 61.5808 | 123.1674 | 61.5449 | 122.9456 | 61.5942 | 61.6301 | 61.4979 | 61.5339
7329.0781 | 123.3353 | -61.4868 | 61.5692 | 0.9368 | 0.62799 | 0.91746 | 1.1517 | 1.167 | 1.2851 | 0.17077 | 61.6332 | 0.22574 | 61.5279 | -0.028522 | 0.048236 | 61.6394 | 0.016878 | 61.413 | 62.4236 | 62.1148 | 62.4043 | 62.6385 | 62.6538 | 62.7719 | 61.6576 | 123.1201 | 61.7126 | 123.0147 | 61.4583 | 61.5351 | 123.1262 | 61.5037 | 122.8998 | 61.585 | 61.6164 | 61.4796 | 61.511
7330.0625 | 123.3307 | -61.5051 | 61.5784 | 0.93223 | 0.6463 | 0.91288 | 1.1517 | 1.167 | 1.2805 | 0.18908 | 61.6424 | 0.24405 | 61.5508 | -0.028522 | 0.057392 | 61.644 | 0.016878 | 61.4222 | 62.4374 | 62.1514 | 62.418 | 62.6568 | 62.6721 | 62.7857 | 61.6942 | 123.1475 | 61.7492 | 123.0559 | 61.4766 | 61.5625 | 123.1491 | 61.522 | 122.9273 | 61.585 | 61.6255 | 61.4934 | 61.5339
7331.0938 | 123.3444 | -61.5051 | 61.5784 | 0.57511 | 0.31205 | 0.55575 | 0.76248 | 0.78247 | 0.93716 | -0.11765 | 61.6607 | 0.23032 | 61.5782 | -0.028522 | 0.048236 | 61.6165 | 0.012299 | 61.3947 | 62.0802 | 61.8172 | 62.0609 | 62.2676 | 62.2876 | 62.4423 | 61.3875 | 123.1658 | 61.7354 | 123.0834 | 61.4766 | 61.5534 | 123.1216 | 61.5174 | 122.8998 | 61.6125 | 61.6484 | 61.53 | 61.5659
7332.0625 | 123.262 | -61.5143 | 61.6058 | 0.80403 | 0.51352 | 0.81673 | 1.0097 | 1.0251 | 1.1478 | 0.051737 | 61.6424 | 0.22574 | 61.537 | -0.023943 | 0.057392 | 61.6257 | 0.007721 | 61.4084 | 62.3183 | 62.0278 | 62.331 | 62.524 | 62.5394 | 62.6621 | 61.566 | 123.1567 | 61.74 | 123.0513 | 61.4903 | 61.5717 | 123.14 | 61.522 | 122.9227 | 61.585 | 61.6347 | 61.4796 | 61.5293
7333.0781 | 123.349 | -61.528 | 61.5463 | 0.7674 | 0.49978 | 0.75263 | 0.96852 | 0.99306 | 1.1386 | 0.042581 | 61.6378 | 0.23032 | 61.5508 | -0.028522 | 0.048236 | 61.6303 | 0.003143 | 61.413 | 62.2954 | 62.0278 | 62.2806 | 62.4965 | 62.5211 | 62.6666 | 61.5706 | 123.1658 | 61.7583 | 123.0788 | 61.4995 | 61.5763 | 123.1583 | 61.5312 | 122.941 | 61.5896 | 61.6347 | 61.5025 | 61.5476
7334.0625 | 123.2803 | -61.5417 | 61.6013 | 1.1383 | 0.82488 | 1.1647 | 1.3714 | 1.3959 | 1.4454 | 0.32643 | 61.6241 | 0.2349 | 61.5553 | -0.023943 | 0.039079 | 61.6486 | 0.012299 | 61.4359 | 62.68 | 62.3666 | 62.7064 | 62.9132 | 62.9377 | 62.9871 | 61.8682 | 123.1658 | 61.7766 | 123.0971 | 61.5178 | 61.5808 | 123.1903 | 61.554 | 122.9777 | 61.585 | 61.6118 | 61.5163 | 61.543
7335.0938 | 123.3582 | -61.4777 | 61.5509 | 0.66668 | 0.38989 | 0.64274 | 0.89068 | 0.91065 | 1.0287 | -0.044405 | 61.6516 | 0.2349 | 61.5553 | -0.033101 | 0.048236 | 61.6257 | 0.007721 | 61.3993 | 62.1443 | 61.8675 | 62.1204 | 62.3683 | 62.3883 | 62.5064 | 61.4333 | 123.1292 | 61.7126 | 123.033 | 61.4446 | 61.5259 | 123.1033 | 61.4854 | 122.8769 | 61.6033 | 61.6438 | 61.5071 | 61.5476
7336.0625 | 123.262 | -61.5005 | 61.6333 | 0.52475 | 0.27542 | 0.49623 | 0.71212 | 0.75043 | 0.88222 | -0.17259 | 61.6561 | 0.2349 | 61.5599 | -0.028522 | 0.057392 | 61.6211 | 0.016878 | 61.4039 | 62.0253 | 61.776 | 61.9968 | 62.2127 | 62.251 | 62.3828 | 61.328 | 123.1567 | 61.7354 | 123.0605 | 61.472 | 61.5579 | 123.1216 | 61.5174 | 122.9044 | 61.5987 | 61.6393 | 61.5025 | 61.543
7337.0781 | 123.3582 | -61.5234 | 61.5555 | 1.0879 | 0.77451 | 1.0914 | 1.3256 | 1.3547 | 1.4179 | 0.29438 | 61.6287 | 0.23948 | 61.5324 | -0.028522 | 0.043657 | 61.6486 | 0.012299 | 61.4222 | 62.6113 | 62.2979 | 62.6149 | 62.8491 | 62.8782 | 62.9413 | 61.8178 | 123.1521 | 61.7629 | 123.0559 | 61.4949 | 61.5671 | 123.172 | 61.5357 | 122.9456 | 61.585 | 61.6164 | 61.4888 | 61.5202
7338.0625 | 123.2574 | -61.496 | 61.6287 | 0.71246 | 0.43568 | 0.68853 | 0.90442 | 0.92897 | 1.0608 | -0.007779 | 61.6607 | 0.2349 | 61.5782 | -0.023943 | 0.057392 | 61.6257 | 0.003143 | 61.4176 | 62.2084 | 61.9316 | 62.1845 | 62.4004 | 62.4249 | 62.5568 | 61.4882 | 123.1567 | 61.7309 | 123.0742 | 61.472 | 61.5534 | 123.1216 | 61.4991 | 122.9136 | 61.6033 | 61.6576 | 61.5208 | 61.5751
7339.0781 | 123.3719 | -61.5143 | 61.5921 | 0.62547 | 0.34868 | 0.60153 | 0.83116 | 0.84656 | 0.96463 | -0.090186 | 61.647 | 0.22574 | 61.5508 | -0.028522 | 0.048236 | 61.6211 | 0.016878 | 61.4039 | 62.1398 | 61.863 | 62.1158 | 62.3454 | 62.3608 | 62.4789 | 61.4241 | 123.1613 | 61.74 | 123.065 | 61.4858 | 61.5625 | 123.1354 | 61.5312 | 122.9181 | 61.5987 | 61.6301 | 61.5025 | 61.5339
7340.0625 | 123.2849 | -61.4868 | 61.6196 | 0.64379 | 0.37157 | 0.61527 | 0.84032 | 0.8603 | 0.98295 | -0.062717 | 61.6516 | 0.23032 | 61.5553 | -0.023943 | 0.052814 | 61.6211 | 0.012299 | 61.4084 | 62.1306 | 61.8584 | 62.1021 | 62.3271 | 62.3471 | 62.4698 | 61.4241 | 123.1384 | 61.7171 | 123.0422 | 61.4629 | 61.5396 | 123.1079 | 61.4991 | 122.8953 | 61.5987 | 61.6393 | 61.5025 | 61.543
7341.0781 | 123.349 | -61.5143 | 61.5646 | 0.4927 | 0.22505 | 0.47333 | 0.70296 | 0.72296 | 0.8227 | -0.20922 | 61.6699 | 0.2349 | 61.5828 | -0.023943 | 0.048236 | 61.6119 | 0.007721 | 61.3856 | 62.007 | 61.7393 | 61.9876 | 62.2172 | 62.2372 | 62.337 | 61.3051 | 123.1842 | 61.7492 | 123.0971 | 61.4903 | 61.5625 | 123.1262 | 61.522 | 122.8998 | 61.6216 | 61.6622 | 61.5346 | 61.5751
7342.0625 | 123.2346 | -61.4868 | 61.6425 | 0.46981 | 0.20674 | 0.45502 | 0.68465 | 0.70465 | 0.79981 | -0.22753 | 61.6653 | 0.23032 | 61.5599 | -0.033101 | 0.052814 | 61.6119 | 0.003143 | 61.3901 | 61.9566 | 61.6936 | 61.9418 | 62.1715 | 62.1915 | 62.2866 | 61.2593 | 123.1521 | 61.7171 | 123.0467 | 61.4537 | 61.5396 | 123.0988 | 61.49 | 122.8769 | 61.6125 | 61.6622 | 61.5071 | 61.5568
7343.0781 | 123.3398 | -61.5097 | 61.5921 | 0.62089 | 0.36699 | 0.61069 | 0.81743 | 0.84198 | 0.93258 | -0.099343 | 61.6561 | 0.2349 | 61.5691 | -0.033101 | 0.043657 | 61.6165 | 0.012299 | 61.3947 | 62.1306 | 61.8767 | 62.1204 | 62.3271 | 62.3517 | 62.4423 | 61.4104 | 123.1658 | 61.7446 | 123.0788 | 61.4766 | 61.5534 | 123.1262 | 61.522 | 122.9044 | 61.6125 | 61.6438 | 61.5254 | 61.5568
7344.0625 | 123.2803 | -61.5005 | 61.6287 | 0.68499 | 0.41278 | 0.66105 | 0.87695 | 0.89692 | 1.0104 | -0.048983 | 61.647 | 0.2349 | 61.5553 | -0.028522 | 0.048236 | 61.6257 | 0.012299 | 61.4084 | 62.1855 | 61.9133 | 62.1616 | 62.3775 | 62.3975 | 62.511 | 61.4516 | 123.1475 | 61.7354 | 123.0559 | 61.472 | 61.5488 | 123.1262 | 61.5128 | 122.909 | 61.5987 | 61.6347 | 61.5071 | 61.543
7345.1094 | 123.3353 | -61.5005 | 61.5875 | 0.60258 | 0.33494 | 0.57406 | 0.80369 | 0.82825 | 0.91885 | -0.11765 | 61.6516 | 0.22574 | 61.5462 | -0.028522 | 0.039079 | 61.6211 | 0.016878 | 61.3993 | 62.1031 | 61.8355 | 62.0746 | 62.3042 | 62.3288 | 62.4194 | 61.3829 | 123.1521 | 61.7263 | 123.0467 | 61.472 | 61.5396 | 123.1216 | 61.5174 | 122.8998 | 61.6125 | 61.6347 | 61.5071 | 61.5293
7346.0625 | 123.262 | -61.5097 | 61.6516 | 0.44234 | 0.19758 | 0.41381 | 0.63429 | 0.65887 | 0.77234 | -0.24584 | 61.6699 | 0.2349 | 61.5828 | -0.023943 | 0.048236 | 61.6074 | 0.012299 | 61.3901 | 61.952 | 61.7073 | 61.9235 | 62.144 | 62.1686 | 62.282 | 61.2639 | 123.1796 | 61.7446 | 123.0925 | 61.4858 | 61.5579 | 123.1171 | 61.522 | 122.8998 | 61.6216 | 61.6576 | 61.5346 | 61.5705
7347.0938 | 123.2803 | -61.4868 | 61.6379 | 0.44692 | 0.18384 | 0.41839 | 0.64344 | 0.66802 | 0.77234 | -0.24584 | 61.6653 | 0.2349 | 61.592 | -0.023943 | 0.052814 | 61.6119 | 0.012299 | 61.3947 | 61.9337 | 61.6707 | 61.9052 | 62.1303 | 62.1548 | 62.2592 | 61.241 | 123.1521 | 61.7217 | 123.0788 | 61.4629 | 61.5396 | 123.0988 | 61.4991 | 122.8815 | 61.6125 | 61.653 | 61.5392 | 61.5797
7348.0625 | 123.2712 | -61.4822 | 61.615 | 0.62547 | 0.35326 | 0.61985 | 0.81285 | 0.83741 | 0.94174 | -0.099343 | 61.6516 | 0.22574 | 61.5553 | -0.028522 | 0.048236 | 61.6211 | 0.021456 | 61.4084 | 62.1077 | 61.8355 | 62.1021 | 62.2951 | 62.3196 | 62.424 | 61.3829 | 123.1338 | 61.708 | 123.0376 | 61.4537 | 61.5305 | 123.1033 | 61.5037 | 122.8907 | 61.6033 | 61.6301 | 61.5071 | 61.5339
7349.0938 | 123.349 | -61.4685 | 61.6379 | 0.50644 | 0.24337 | 0.48249 | 0.71212 | 0.72754 | 0.82728 | -0.18633 | 61.6516 | 0.22574 | 61.5599 | -0.019364 | 0.048236 | 61.6119 | 0.012299 | 61.3993 | 61.9749 | 61.7119 | 61.951 | 62.1806 | 62.196 | 62.2958 | 61.2822 | 123.1201 | 61.6942 | 123.0284 | 61.4491 | 61.5167 | 123.0804 | 61.4808 | 122.8678 | 61.6033 | 61.6393 | 61.5117 | 61.5476
7350.0625 | 123.2574 | -61.5326 | 61.615 | 0.54764 | 0.28458 | 0.52828 | 0.74875 | 0.78705 | 0.87764 | -0.1497 | 61.6653 | 0.24405 | 61.5874 | -0.03768 | 0.043657 | 61.6165 | 0.012299 | 61.3947 | 62.0802 | 61.8172 | 62.0609 | 62.2813 | 62.3196 | 62.4102 | 61.3829 | 123.1979 | 61.7766 | 123.12 | 61.4949 | 61.5763 | 123.1491 | 61.5449 | 122.9273 | 61.6216 | 61.653 | 61.5437 | 61.5751
7351.0938 | 123.4222 | -61.4502 | 61.5738 | 0.63463 | 0.36699 | 0.61069 | 0.84032 | 0.86487 | 0.94174 | -0.099343 | 61.6516 | 0.2349 | 61.5645 | -0.023943 | 0.052814 | 61.6165 | 0.007721 | 61.4084 | 62.0848 | 61.8172 | 62.0609 | 62.2905 | 62.3151 | 62.3919 | 61.3509 | 123.1018 | 61.6851 | 123.0147 | 61.4263 | 61.503 | 123.0667 | 61.4579 | 122.8586 | 61.5987 | 61.6438 | 61.5117 | 61.5568
7352.0625 | 123.2849 | -61.5189 | 61.6196 | 0.86813 | 0.60509 | 0.85794 | 1.083 | 1.1029 | 1.1844 | 0.11125 | 61.6332 | 0.23032 | 61.5324 | -0.028522 | 0.048236 | 61.6394 | 0.016878 | 61.4222 | 62.387 | 62.124 | 62.3768 | 62.6018 | 62.6218 | 62.7033 | 61.6301 | 123.1521 | 61.7492 | 123.0513 | 61.4903 | 61.5671 | 123.1583 | 61.5357 | 122.941 | 61.585 | 61.6164 | 61.4842 | 61.5156
7353.0781 | 123.3765 | -61.4914 | 61.5967 | 0.75825 | 0.47231 | 0.74347 | 0.96852 | 0.99764 | 1.0608 | -0.007779 | 61.6516 | 0.23032 | 61.5508 | -0.023943 | 0.043657 | 61.6257 | 0.007721 | 61.4084 | 62.2496 | 61.9637 | 62.2349 | 62.4599 | 62.489 | 62.5522 | 61.4836 | 123.143 | 61.7217 | 123.0422 | 61.4675 | 61.5351 | 123.1171 | 61.4991 | 122.8998 | 61.6079 | 61.6438 | 61.5071 | 61.543
7354.0625 | 123.2712 | -61.4822 | 61.6287 | 0.64837 | 0.36241 | 0.63816 | 0.85405 | 0.87861 | 0.92801 | -0.10392 | 61.6607 | 0.22574 | 61.5782 | -0.023943 | 0.048236 | 61.6257 | 0.012299 | 61.4084 | 62.1306 | 61.8447 | 62.1204 | 62.3363 | 62.3608 | 62.4102 | 61.3783 | 123.143 | 61.708 | 123.0605 | 61.4583 | 61.5305 | 123.1079 | 61.4945 | 122.8907 | 61.6125 | 61.6484 | 61.53 | 61.5659
7355.0938 | 123.3536 | -61.5234 | 61.6013 | 0.64379 | 0.36699 | 0.64732 | 0.87237 | 0.89234 | 0.94174 | -0.094765 | 61.6516 | 0.23948 | 61.5828 | -0.023943 | 0.052814 | 61.6257 | 0.016878 | 61.3947 | 62.1672 | 61.8904 | 62.1708 | 62.3958 | 62.4158 | 62.4652 | 61.4287 | 123.175 | 61.7629 | 123.1062 | 61.4995 | 61.5763 | 123.1491 | 61.5403 | 122.9181 | 61.5987 | 61.6347 | 61.53 | 61.5659
7356.0625 | 123.3124 | -61.5189 | 61.6241 | 0.75825 | 0.48146 | 0.76178 | 0.96394 | 1.0022 | 1.0425 | 0.001377 | 61.647 | 0.2349 | 61.5508 | -0.023943 | 0.048236 | 61.6211 | 0.012299 | 61.4084 | 62.2771 | 62.0003 | 62.2806 | 62.4828 | 62.5211 | 62.5613 | 61.5202 | 123.1658 | 61.7538 | 123.0696 | 61.4949 | 61.5671 | 123.14 | 61.5312 | 122.9273 | 61.5987 | 61.6347 | 61.5025 | 61.5385
7357.0781 | 123.3398 | -61.4822 | 61.6013 | 0.67584 | 0.40363 | 0.67021 | 0.8861 | 0.91065 | 0.96921 | -0.062717 | 61.6378 | 0.22574 | 61.5508 | -0.028522 | 0.039079 | 61.6119 | 0.012299 | 61.3993 | 62.1581 | 61.8859 | 62.1525 | 62.3683 | 62.3929 | 62.4515 | 61.4195 | 123.1201 | 61.708 | 123.033 | 61.4537 | 61.5213 | 123.0942 | 61.4945 | 122.8815 | 61.5987 | 61.6255 | 61.5117 | 61.5385
7358.0625 | 123.2849 | -61.4868 | 61.6333 | 0.63921 | 0.36699 | 0.62901 | 0.84032 | 0.86945 | 0.91427 | -0.099343 | 61.6516 | 0.2349 | 61.5508 | -0.023943 | 0.048236 | 61.6257 | 0.007721 | 61.4084 | 62.126 | 61.8538 | 62.1158 | 62.3271 | 62.3563 | 62.4011 | 61.3875 | 123.1384 | 61.7217 | 123.0376 | 61.4629 | 61.5351 | 123.1125 | 61.4945 | 122.8953 | 61.6033 | 61.6438 | 61.5025 | 61.543
7359.0781 | 123.349 | -61.528 | 61.5601 | 0.92307 | 0.64172 | 0.92204 | 1.1471 | 1.1624 | 1.2119 | 0.13872 | 61.6378 | 0.23032 | 61.5462 | -0.023943 | 0.048236 | 61.6394 | -0.001436 | 61.4222 | 62.4511 | 62.1697 | 62.4501 | 62.6751 | 62.6905 | 62.7399 | 61.6667 | 123.1658 | 61.7583 | 123.0742 | 61.5041 | 61.5763 | 123.1674 | 61.5266 | 122.9502 | 61.5896 | 61.6393 | 61.4979 | 61.5476
7360.0625 | 123.3444 | -61.528 | 61.5326 | 0.81319 | 0.54099 | 0.82588 | 1.028 | 1.0617 | 1.1111 | 0.051737 | 61.6424 | 0.2349 | 61.5691 | -0.028522 | 0.052814 | 61.6303 | 0.007721 | 61.4084 | 62.3412 | 62.069 | 62.3539 | 62.5561 | 62.5897 | 62.6392 | 61.5798 | 123.1704 | 61.7629 | 123.0971 | 61.4995 | 61.5808 | 123.1583 | 61.5357 | 122.9365 | 61.5896 | 61.6347 | 61.5163 | 61.5614
7361.0781 | 123.3902 | -61.4777 | 61.5829 | 0.78114 | 0.49062 | 0.7801 | 0.99599 | 1.0297 | 1.0287 | -0.012357 | 61.647 | 0.2349 | 61.5553 | -0.033101 | 0.048236 | 61.6303 | 0.016878 | 61.4039 | 62.2588 | 61.9683 | 62.2578 | 62.4736 | 62.5073 | 62.5064 | 61.4653 | 123.1246 | 61.7126 | 123.033 | 61.4446 | 61.5259 | 123.1079 | 61.4945 | 122.8815 | 61.5987 | 61.6301 | 61.5071 | 61.5385
7362.0625 | 123.2986 | -61.496 | 61.6333 | 0.56138 | 0.30747 | 0.56948 | 0.75333 | 0.77789 | 0.84102 | -0.15428 | 61.6516 | 0.23032 | 61.5599 | -0.028522 | 0.048236 | 61.6211 | 0.016878 | 61.3947 | 62.0573 | 61.8034 | 62.0655 | 62.2493 | 62.2739 | 62.337 | 61.3417 | 123.1475 | 61.7263 | 123.0559 | 61.4674 | 61.5442 | 123.1171 | 61.5129 | 122.8907 | 61.6033 | 61.6347 | 61.5117 | 61.543
7363.0781 | 123.3582 | -61.5005 | 61.615 | 0.598 | 0.33952 | 0.60153 | 0.77622 | 0.79621 | 0.87307 | -0.12223 | 61.6516 | 0.2349 | 61.5645 | -0.028522 | 0.048236 | 61.6211 | 0.007721 | 61.3993 | 62.0986 | 61.8401 | 62.1021 | 62.2768 | 62.2968 | 62.3736 | 61.3783 | 123.1521 | 61.7354 | 123.065 | 61.472 | 61.5488 | 123.1216 | 61.5083 | 122.8998 | 61.6033 | 61.6438 | 61.5163 | 61.5568
7364.0625 | 123.2758 | -61.496 | 61.6379 | 0.88186 | 0.61425 | 0.90372 | 1.0967 | 1.1212 | 1.1569 | 0.11583 | 61.6378 | 0.23032 | 61.5691 | -0.019364 | 0.06197 | 61.644 | 0.007721 | 61.4222 | 62.3778 | 62.1102 | 62.3997 | 62.5927 | 62.6172 | 62.6529 | 61.6118 | 123.1338 | 61.7263 | 123.065 | 61.4766 | 61.5579 | 123.14 | 61.5037 | 122.9181 | 61.5759 | 61.6301 | 61.5071 | 61.5614
7365.1094 | 123.2986 | -61.5097 | 61.6379 | 0.92765 | 0.65088 | 0.93577 | 1.1471 | 1.167 | 1.1936 | 0.1433 | 61.6378 | 0.22574 | 61.5416 | -0.023943 | 0.052814 | 61.6348 | 0.003143 | 61.4222 | 62.4374 | 62.1606 | 62.4455 | 62.6568 | 62.6767 | 62.7033 | 61.653 | 123.1475 | 61.7354 | 123.0513 | 61.4858 | 61.5625 | 123.1445 | 61.5128 | 122.9319 | 61.585 | 61.6347 | 61.4888 | 61.5385
7366.0625 | 123.2895 | -61.4868 | 61.6241 | 0.73993 | 0.44941 | 0.72973 | 0.9731 | 0.98848 | 1.0333 | -0.003201 | 61.647 | 0.2349 | 61.5508 | -0.023943 | 0.052814 | 61.6211 | 0.012299 | 61.4084 | 62.2267 | 61.9362 | 62.2165 | 62.4599 | 62.4753 | 62.5201 | 61.4836 | 123.1338 | 61.7217 | 123.0376 | 61.4629 | 61.5396 | 123.1079 | 61.4991 | 122.8953 | 61.5942 | 61.6347 | 61.4979 | 61.5385
7367.0781 | 123.3856 | -61.4868 | 61.6196 | 0.84066 | 0.56388 | 0.8442 | 1.0509 | 1.0755 | 1.1066 | 0.074628 | 61.6424 | 0.23948 | 61.5782 | -0.033101 | 0.052814 | 61.6394 | 0.012299 | 61.4084 | 62.3275 | 62.0507 | 62.331 | 62.5377 | 62.5623 | 62.5934 | 61.5614 | 123.1292 | 61.7263 | 123.065 | 61.4537 | 61.5396 | 123.1262 | 61.4991 | 122.8953 | 61.5896 | 61.6301 | 61.5254 | 61.5659
7368.0625 | 123.2758 | -61.4868 | 61.6608 | 0.74451 | 0.46315 | 0.74347 | 0.95478 | 0.97932 | 0.9921 | -0.016936 | 61.6516 | 0.22574 | 61.5508 | -0.023943 | 0.052814 | 61.6257 | 0.007721 | 61.4039 | 62.2313 | 61.95 | 62.2303 | 62.4416 | 62.4661 | 62.4789 | 61.4699 | 123.1384 | 61.7126 | 123.0376 | 61.4629 | 61.5396 | 123.1125 | 61.4945 | 122.8907 | 61.5987 | 61.6438 | 61.4979 | 61.543
7369.0938 | 123.3444 | -61.496 | 61.5692 | 1.0192 | 0.72414 | 1.0457 | 1.2615 | 1.286 | 1.2576 | 0.20282 | 61.6287 | 0.22574 | 61.5233 | -0.019364 | 0.043657 | 61.644 | 0.012299 | 61.4268 | 62.5152 | 62.2201 | 62.5416 | 62.7575 | 62.782 | 62.7536 | 61.6988 | 123.1246 | 61.7217 | 123.0193 | 61.4766 | 61.5396 | 123.14 | 61.5083 | 122.9227 | 61.585 | 61.6164 | 61.4796 | 61.511
7370.0625 | 123.2529 | -61.528 | 61.6013 | 0.72162 | 0.44941 | 0.75263 | 0.9502 | 0.97017 | 0.96463 | -0.048983 | 61.6607 | 0.2349 | 61.5645 | -0.028522 | 0.048236 | 61.6257 | 0.012299 | 61.4084 | 62.2496 | 61.9774 | 62.2806 | 62.4782 | 62.4982 | 62.4926 | 61.479 | 123.1887 | 61.7629 | 123.0925 | 61.4995 | 61.5763 | 123.1537 | 61.5403 | 122.9365 | 61.6125 | 61.6484 | 61.5163 | 61.5522
7371.0625 | 123.2803 | -61.5189 | 61.615 | 0.91391 | 0.62341 | 0.94035 | 1.1517 | 1.1853 | 1.1707 | 0.12041 | 61.647 | 0.2349 | 61.5645 | -0.023943 | 0.048236 | 61.6348 | 0.007721 | 61.413 | 62.4328 | 62.1423 | 62.4592 | 62.6705 | 62.7042 | 62.6895 | 61.6393 | 123.1658 | 61.7538 | 123.0834 | 61.4949 | 61.5671 | 123.1537 | 61.5266 | 122.9319 | 61.5987 | 61.6393 | 61.5163 | 61.5568
7372.0938 | 123.2758 | -61.496 | 61.6241 | 0.91391 | 0.63714 | 0.93119 | 1.1471 | 1.1624 | 1.1615 | 0.12041 | 61.6241 | 0.23032 | 61.537 | -0.028522 | 0.043657 | 61.6348 | 0.016878 | 61.4268 | 62.4099 | 62.1331 | 62.4272 | 62.6431 | 62.6584 | 62.6575 | 61.6164 | 123.1201 | 61.7263 | 123.033 | 61.4674 | 61.5396 | 123.1308 | 61.5129 | 122.9227 | 61.5804 | 61.6072 | 61.4934 | 61.5202
7373.0625 | 123.3261 | -61.5143 | 61.6196 | 0.94138 | 0.66004 | 0.96324 | 1.17 | 1.2036 | 1.2119 | 0.15246 | 61.6332 | 0.23032 | 61.5462 | -0.014785 | 0.052814 | 61.6348 | 0.012299 | 61.4176 | 62.4557 | 62.1743 | 62.4775 | 62.6843 | 62.7179 | 62.7261 | 61.6667 | 123.1475 | 61.7446 | 123.0605 | 61.4995 | 61.5671 | 123.1491 | 61.5266 | 122.9319 | 61.5804 | 61.6209 | 61.4934 | 61.5339
7374.0938 | 123.3032 | -61.496 | 61.5921 | 1.0467 | 0.76535 | 1.0686 | 1.2707 | 1.2998 | 1.2851 | 0.24402 | 61.6332 | 0.23948 | 61.5691 | -0.028522 | 0.048236 | 61.6394 | 0.012299 | 61.4313 | 62.5427 | 62.2613 | 62.5645 | 62.7667 | 62.7958 | 62.7811 | 61.74 | 123.1292 | 61.7354 | 123.065 | 61.4674 | 61.5442 | 123.1354 | 61.5083 | 122.9273 | 61.585 | 61.6209 | 61.5208 | 61.5568
7375.0625 | 123.3215 | -61.528 | 61.5509 | 1.0375 | 0.75619 | 1.0457 | 1.2615 | 1.2723 | 1.2897 | 0.2486 | 61.6332 | 0.22116 | 61.5416 | -0.028522 | 0.048236 | 61.6303 | 0.003143 | 61.413 | 62.5655 | 62.2842 | 62.5737 | 62.7896 | 62.8003 | 62.8177 | 61.7766 | 123.1613 | 61.7492 | 123.0696 | 61.4995 | 61.5763 | 123.1583 | 61.5312 | 122.941 | 61.585 | 61.6301 | 61.4934 | 61.5385
7376.0781 | 123.4085 | -61.4777 | 61.6013 | 1.0375 | 0.76535 | 1.0594 | 1.2753 | 1.2952 | 1.2714 | 0.22571 | 61.6195 | 0.22574 | 61.5279 | -0.023943 | 0.039079 | 61.644 | 0.012299 | 61.4313 | 62.5152 | 62.243 | 62.5371 | 62.7529 | 62.7729 | 62.749 | 61.7034 | 123.0972 | 61.7034 | 123.0055 | 61.4537 | 61.5167 | 123.1216 | 61.49 | 122.909 | 61.5804 | 61.6072 | 61.4888 | 61.5156
7377.0625 | 123.2849 | -61.5417 | 61.615 | 1.0742 | 0.7974 | 1.0869 | 1.2982 | 1.3181 | 1.3172 | 0.26691 | 61.6332 | 0.22574 | 61.5416 | -0.028522 | 0.048236 | 61.6486 | 0.007721 | 61.4222 | 62.6159 | 62.3392 | 62.6286 | 62.8399 | 62.8598 | 62.8589 | 61.8087 | 123.175 | 61.7675 | 123.0834 | 61.5132 | 61.59 | 123.1903 | 61.5495 | 122.9639 | 61.585 | 61.6255 | 61.4934 | 61.5339
7378.0938 | 123.3032 | -61.5463 | 61.6104 | 0.95054 | 0.6692 | 0.9724 | 1.1745 | 1.1945 | 1.189 | 0.13414 | 61.647 | 0.2349 | 61.5645 | -0.033101 | 0.048236 | 61.6394 | 0.012299 | 61.4176 | 62.4969 | 62.2155 | 62.5187 | 62.7209 | 62.7408 | 62.7353 | 61.6805 | 123.1933 | 61.7812 | 123.1108 | 61.5132 | 61.5946 | 123.1857 | 61.5586 | 122.9639 | 61.5987 | 61.6347 | 61.5163 | 61.5522
7379.0625 | 123.262 | -61.5189 | 61.5921 | 0.96885 | 0.69667 | 0.99071 | 1.1974 | 1.2128 | 1.2027 | 0.15704 | 61.647 | 0.2349 | 61.537 | -0.028522 | 0.048236 | 61.6394 | 0.012299 | 61.4176 | 62.4877 | 62.2155 | 62.5096 | 62.7163 | 62.7317 | 62.7216 | 61.6759 | 123.1658 | 61.7538 | 123.0559 | 61.4903 | 61.5671 | 123.1583 | 61.5312 | 122.9365 | 61.5987 | 61.6347 | 61.4888 | 61.5247
7380.1094 | 123.3582 | -61.4868 | 61.5555 | 0.87271 | 0.59136 | 0.88541 | 1.0967 | 1.1212 | 1.1111 | 0.065472 | 61.6424 | 0.22574 | 61.5324 | -0.033101 | 0.057392 | 61.6348 | 0.012299 | 61.4222 | 62.3595 | 62.0782 | 62.3722 | 62.5835 | 62.6081 | 62.598 | 61.5523 | 123.1292 | 61.7126 | 123.0193 | 61.4537 | 61.5442 | 123.1216 | 61.4991 | 122.909 | 61.585 | 61.6301 | 61.4751 | 61.5202
7381.0625 | 123.3078 | -61.5051 | 61.6608 | 1.1245 | 0.83861 | 1.151 | 1.3623 | 1.3913 | 1.363 | 0.2898 | 61.6241 | 0.2349 | 61.5416 | -0.023943 | 0.057392 | 61.644 | 0.021456 | 61.4313 | 62.6296 | 62.3437 | 62.6561 | 62.8674 | 62.8965 | 62.8681 | 61.7949 | 123.1292 | 61.74 | 123.0467 | 61.4812 | 61.5625 | 123.1491 | 61.5266 | 122.9365 | 61.5667 | 61.6026 | 61.4842 | 61.5202
7382.0938 | 123.3673 | -61.496 | 61.5509 | 1.0787 | 0.81572 | 1.1098 | 1.289 | 1.3181 | 1.2943 | 0.23486 | 61.6241 | 0.23948 | 61.5553 | -0.023943 | 0.043657 | 61.6486 | 0.012299 | 61.4268 | 62.5747 | 62.3117 | 62.6057 | 62.785 | 62.8141 | 62.7902 | 61.7308 | 123.1201 | 61.7354 | 123.0513 | 61.472 | 61.5396 | 123.1445 | 61.5083 | 122.9227 | 61.5804 | 61.6118 | 61.5117 | 61.543
7383.0625 | 123.3856 | -61.496 | 61.5875 | 0.98259 | 0.7104 | 1.0136 | 1.1929 | 1.2174 | 1.2302 | 0.17993 | 61.6332 | 0.23032 | 61.5324 | -0.033101 | 0.043657 | 61.6486 | 0.021456 | 61.4268 | 62.4786 | 62.2064 | 62.5096 | 62.6888 | 62.7134 | 62.7262 | 61.6759 | 123.1292 | 61.7263 | 123.0284 | 61.4629 | 61.5396 | 123.1445 | 61.5174 | 122.9227 | 61.5896 | 61.6118 | 61.4888 | 61.511
7384.0938 | 123.3261 | -61.5509 | 61.5601 | 1.1199 | 0.84319 | 1.1464 | 1.3211 | 1.3501 | 1.3584 | 0.30354 | 61.6241 | 0.23032 | 61.5141 | -0.028522 | 0.048236 | 61.6394 | 0.012299 | 61.4268 | 62.6708 | 62.3941 | 62.6973 | 62.872 | 62.901 | 62.9093 | 61.8544 | 123.175 | 61.7812 | 123.065 | 61.5224 | 61.5991 | 123.1903 | 61.5632 | 122.9777 | 61.5759 | 61.6118 | 61.4659 | 61.5018
7385.0625 | 123.262 | -61.5372 | 61.5921 | 0.96885 | 0.7104 | 0.99529 | 1.1883 | 1.2174 | 1.2164 | 0.16161 | 61.6378 | 0.23948 | 61.5553 | -0.033101 | 0.043657 | 61.6348 | 0.007721 | 61.4222 | 62.506 | 62.2476 | 62.5325 | 62.7255 | 62.7545 | 62.7536 | 61.6988 | 123.175 | 61.7766 | 123.0925 | 61.5041 | 61.5808 | 123.172 | 61.5449 | 122.9593 | 61.5942 | 61.6301 | 61.5117 | 61.5476
7386.0938 | 123.3444 | -61.5234 | 61.5646 | 1.239 | 0.96682 | 1.2654 | 1.4538 | 1.4737 | 1.4866 | 0.43173 | 61.6195 | 0.23948 | 61.5416 | -0.033101 | 0.048236 | 61.6486 | 0.007721 | 61.4405 | 62.7624 | 62.4903 | 62.7889 | 62.9773 | 62.9972 | 63.01 | 61.9552 | 123.1429 | 61.7629 | 123.065 | 61.4903 | 61.5717 | 123.172 | 61.5312 | 122.9639 | 61.5713 | 61.6118 | 61.4934 | 61.5339
7387.0625 | 123.3765 | -61.5143 | 61.5646 | 1.2664 | 0.99429 | 1.3021 | 1.5088 | 1.5241 | 1.5049 | 0.44546 | 61.6104 | 0.23032 | 61.5187 | -0.028522 | 0.043657 | 61.6577 | 0.016878 | 61.4451 | 62.7807 | 62.5086 | 62.8163 | 63.0231 | 63.0384 | 63.0192 | 61.9597 | 123.1246 | 61.7446 | 123.033 | 61.4858 | 61.5579 | 123.172 | 61.5312 | 122.9594 | 61.5667 | 61.5935 | 61.4751 | 61.5018
7388.0938 | 123.3856 | -61.4914 | 61.5417 | 0.96427 | 0.68751 | 0.99071 | 1.1883 | 1.2036 | 1.2027 | 0.16161 | 61.6241 | 0.23032 | 61.5279 | -0.023943 | 0.048236 | 61.644 | 0.012299 | 61.4176 | 62.4557 | 62.1789 | 62.4821 | 62.6797 | 62.695 | 62.6941 | 61.653 | 123.1155 | 61.7217 | 123.0193 | 61.4675 | 61.5396 | 123.1354 | 61.5037 | 122.909 | 61.5759 | 61.6118 | 61.4796 | 61.5156
7389.0625 | 123.381 | -61.5051 | 61.5555 | 1.0421 | 0.76535 | 1.0869 | 1.2844 | 1.3135 | 1.2439 | 0.22571 | 61.6332 | 0.2349 | 61.5599 | -0.033101 | 0.052814 | 61.6394 | 0.012299 | 61.4222 | 62.5472 | 62.2705 | 62.592 | 62.7896 | 62.8186 | 62.749 | 61.7308 | 123.1384 | 61.74 | 123.065 | 61.472 | 61.5579 | 123.1445 | 61.5174 | 122.9273 | 61.5804 | 61.6209 | 61.5071 | 61.5476
7390.1094 | 123.3215 | -61.5463 | 61.5463 | 1.0055 | 0.71956 | 1.0411 | 1.2432 | 1.2723 | 1.2302 | 0.17077 | 61.6332 | 0.2349 | 61.5462 | -0.023943 | 0.039079 | 61.6394 | 0.012299 | 61.4222 | 62.5518 | 62.2659 | 62.5874 | 62.7896 | 62.8186 | 62.7765 | 61.7171 | 123.1796 | 61.7812 | 123.0925 | 61.5224 | 61.5854 | 123.1857 | 61.5586 | 122.9685 | 61.5942 | 61.6209 | 61.5071 | 61.5339
7391.0625 | 123.4085 | -61.4914 | 61.5692 | 0.89102 | 0.60967 | 0.91746 | 1.1379 | 1.1624 | 1.1111 | 0.060893 | 61.6424 | 0.2349 | 61.537 | -0.023943 | 0.057392 | 61.6257 | 0.012299 | 61.4176 | 62.3824 | 62.1011 | 62.4089 | 62.6293 | 62.6538 | 62.6025 | 61.5523 | 123.1338 | 61.7263 | 123.0284 | 61.4675 | 61.5488 | 123.1171 | 61.5037 | 122.909 | 61.585 | 61.6301 | 61.4796 | 61.5247
7392.0781 | 123.3536 | -61.5234 | 61.5417 | 0.96427 | 0.68751 | 0.99071 | 1.2203 | 1.254 | 1.1752 | 0.12499 | 61.6287 | 0.23948 | 61.5324 | -0.028522 | 0.052814 | 61.644 | 0.012299 | 61.413 | 62.4877 | 62.2109 | 62.5142 | 62.7438 | 62.7774 | 62.6987 | 61.6484 | 123.1521 | 61.7629 | 123.0559 | 61.4949 | 61.5763 | 123.1674 | 61.5357 | 122.9365 | 61.5759 | 61.6164 | 61.4796 | 61.5202
7393.0625 | 123.349 | -61.4822 | 61.5601 | 0.92765 | 0.66004 | 0.97698 | 1.1837 | 1.2036 | 1.1386 | 0.1021 | 61.6332 | 0.23948 | 61.5645 | -0.028522 | 0.048236 | 61.6348 | 0.012299 | 61.4176 | 62.4099 | 62.1423 | 62.4592 | 62.6659 | 62.6859 | 62.6209 | 61.5843 | 123.1155 | 61.7217 | 123.0467 | 61.4537 | 61.5305 | 123.1171 | 61.4945 | 122.8998 | 61.585 | 61.6209 | 61.5163 | 61.5522
7394.0781 | 123.3078 | -61.5051 | 61.5692 | 0.77198 | 0.48604 | 0.80757 | 1.028 | 1.0572 | 1.0104 | -0.058139 | 61.647 | 0.23948 | 61.5553 | -0.033101 | 0.043657 | 61.6303 | 0.012299 | 61.4084 | 62.2771 | 61.9912 | 62.3127 | 62.5332 | 62.5623 | 62.5155 | 61.447 | 123.1521 | 61.7446 | 123.0605 | 61.472 | 61.5488 | 123.1354 | 61.5174 | 122.9136 | 61.6033 | 61.6347 | 61.5117 | 61.543
7395.0625 | 123.4406 | -61.4685 | 61.5921 | 0.67584 | 0.4082 | 0.70684 | 0.89984 | 0.92897 | 0.89596 | -0.10392 | 61.6516 | 0.22574 | 61.5462 | -0.019364 | 0.052814 | 61.6257 | 0.007721 | 61.4039 | 62.1443 | 61.8767 | 62.1753 | 62.3683 | 62.3975 | 62.3645 | 61.3646 | 123.1201 | 61.6942 | 123.0147 | 61.4491 | 61.5213 | 123.0942 | 61.4762 | 122.8724 | 61.5987 | 61.6438 | 61.4934 | 61.5385
7396.0625 | 123.3765 | -61.4868 | 61.5829 | 0.5568 | 0.29831 | 0.59696 | 0.78538 | 0.80994 | 0.77692 | -0.22295 | 61.6607 | 0.23032 | 61.5645 | -0.023943 | 0.043657 | 61.6119 | 0.007721 | 61.3947 | 62.0436 | 61.7851 | 62.0838 | 62.2722 | 62.2968 | 62.2637 | 61.2639 | 123.1475 | 61.7171 | 123.0513 | 61.4629 | 61.5305 | 123.0988 | 61.4945 | 122.8815 | 61.6171 | 61.653 | 61.5208 | 61.5568
7397.0938 | 123.3353 | -61.4868 | 61.5601 | 0.64379 | 0.37157 | 0.66563 | 0.86321 | 0.89234 | 0.85933 | -0.13597 | 61.6516 | 0.2349 | 61.5874 | -0.028522 | 0.052814 | 61.6165 | 0.007721 | 61.4084 | 62.1306 | 61.8584 | 62.1524 | 62.35 | 62.3792 | 62.3461 | 61.3508 | 123.1384 | 61.7217 | 123.0742 | 61.4583 | 61.5396 | 123.1033 | 61.4945 | 122.8953 | 61.5987 | 61.6438 | 61.5346 | 61.5797
7398.0625 | 123.3353 | -61.5143 | 61.6013 | 0.53391 | 0.28 | 0.57864 | 0.76248 | 0.78247 | 0.73114 | -0.22753 | 61.6607 | 0.2349 | 61.5828 | -0.023943 | 0.043657 | 61.6119 | 0.012299 | 61.3947 | 62.0482 | 61.7943 | 62.0929 | 62.2768 | 62.2968 | 62.2454 | 61.2868 | 123.175 | 61.7492 | 123.0971 | 61.4903 | 61.5579 | 123.1262 | 61.5266 | 122.909 | 61.6171 | 61.6484 | 61.5392 | 61.5705
7399.0938 | 123.3032 | -61.496 | 61.5829 | 0.58427 | 0.31663 | 0.63358 | 0.82658 | 0.85572 | 0.79981 | -0.20006 | 61.6561 | 0.2349 | 61.5645 | -0.033101 | 0.052814 | 61.6119 | 0.007721 | 61.3993 | 62.0802 | 61.8126 | 62.1296 | 62.3226 | 62.3517 | 62.2958 | 61.2959 | 123.1521 | 61.7309 | 123.0605 | 61.4629 | 61.5488 | 123.1079 | 61.5037 | 122.8953 | 61.6033 | 61.6484 | 61.5117 | 61.5568
7400.0625 | 123.3124 | -61.5005 | 61.5967 | 0.89102 | 0.61425 | 0.94035 | 1.1425 | 1.1624 | 1.1249 | 0.07005 | 61.6332 | 0.22574 | 61.537 | -0.033101 | 0.057392 | 61.6348 | 0.007721 | 61.4222 | 62.3916 | 62.1148 | 62.4409 | 62.643 | 62.663 | 62.6254 | 61.5706 | 123.1338 | 61.7263 | 123.0376 | 61.4674 | 61.5579 | 123.1354 | 61.5083 | 122.9227 | 61.5759 | 61.6255 | 61.4796 | 61.5293
7401.0625 | 123.3856 | -61.4914 | 61.5601 | 0.90933 | 0.62799 | 0.94493 | 1.1608 | 1.1808 | 1.1203 | 0.07005 | 61.6332 | 0.23032 | 61.537 | -0.023943 | 0.048236 | 61.6348 | 0.012299 | 61.4176 | 62.4007 | 62.1194 | 62.4363 | 62.6522 | 62.6721 | 62.6117 | 61.5614 | 123.1246 | 61.7217 | 123.0284 | 61.4675 | 61.5396 | 123.1262 | 61.5037 | 122.909 | 61.585 | 61.6209 | 61.4888 | 61.5247
7402.0781 | 123.2803 | -61.528 | 61.5738 | 0.99632 | 0.72872 | 1.0365 | 1.2432 | 1.2677 | 1.1936 | 0.17077 | 61.6332 | 0.23032 | 61.5462 | -0.03768 | 0.043657 | 61.6394 | 0.016878 | 61.4176 | 62.5243 | 62.2567 | 62.5645 | 62.7712 | 62.7958 | 62.7216 | 61.6988 | 123.1613 | 61.7583 | 123.0742 | 61.4903 | 61.5717 | 123.1674 | 61.5449 | 122.9456 | 61.5896 | 61.6164 | 61.5025 | 61.5293
7403.0625 | 123.4177 | -61.5097 | 61.5555 | 1.0604 | 0.7974 | 1.096 | 1.2982 | 1.3318 | 1.2485 | 0.21655 | 61.6332 | 0.2349 | 61.5645 | -0.023943 | 0.048236 | 61.6486 | 0.003143 | 61.4222 | 62.5701 | 62.3071 | 62.6057 | 62.8079 | 62.8415 | 62.7582 | 61.7263 | 123.143 | 61.7446 | 123.0742 | 61.4858 | 61.5579 | 123.1583 | 61.5128 | 122.9319 | 61.585 | 61.6301 | 61.5163 | 61.5614
7404.0781 | 123.2803 | -61.5234 | 61.5738 | 0.79945 | 0.54557 | 0.84878 | 1.0418 | 1.0663 | 1.0196 | -0.003201 | 61.6424 | 0.23032 | 61.5508 | -0.033101 | 0.048236 | 61.6348 | 0.016878 | 61.4084 | 62.3229 | 62.069 | 62.3722 | 62.5652 | 62.5897 | 62.543 | 61.5202 | 123.1658 | 61.7538 | 123.0742 | 61.4903 | 61.5717 | 123.1583 | 61.5403 | 122.9319 | 61.5942 | 61.6255 | 61.5025 | 61.5339
7405.0625 | 123.3124 | -61.5143 | 61.615 | 0.95054 | 0.69209 | 0.99071 | 1.1837 | 1.1991 | 1.1432 | 0.12041 | 61.6287 | 0.22574 | 61.537 | -0.023943 | 0.048236 | 61.6348 | 0.012299 | 61.4176 | 62.4648 | 62.2064 | 62.505 | 62.698 | 62.7133 | 62.6575 | 61.6347 | 123.143 | 61.74 | 123.0513 | 61.4903 | 61.5625 | 123.1491 | 61.5266 | 122.9319 | 61.5804 | 61.6164 | 61.4888 | 61.5247
7406.0781 | 123.2391 | -61.5555 | 61.5738 | 1.2024 | 0.93935 | 1.2654 | 1.4493 | 1.4829 | 1.3675 | 0.33101 | 61.6287 | 0.23032 | 61.5279 | -0.028522 | 0.048236 | 61.644 | 0.007721 | 61.4222 | 62.7578 | 62.4948 | 62.8209 | 63.0047 | 63.0384 | 62.923 | 61.8865 | 123.1842 | 61.7858 | 123.0834 | 61.527 | 61.6037 | 123.1995 | 61.5632 | 122.9777 | 61.5804 | 61.6209 | 61.4796 | 61.5202
7407.0625 | 123.3719 | -61.496 | 61.5738 | 1.0284 | 0.78367 | 1.0914 | 1.2478 | 1.2815 | 1.189 | 0.17993 | 61.6287 | 0.2349 | 61.5599 | -0.023943 | 0.048236 | 61.6394 | 0.003143 | 61.4268 | 62.5243 | 62.2796 | 62.5874 | 62.7438 | 62.7774 | 62.6849 | 61.6759 | 123.1246 | 61.7309 | 123.0559 | 61.472 | 61.5442 | 123.1354 | 61.4991 | 122.9227 | 61.5804 | 61.6255 | 61.5117 | 61.5568
7408.0938 | 123.2758 | -61.5555 | 61.5417 | 1.2573 | 0.99429 | 1.3295 | 1.5042 | 1.5287 | 1.4133 | 0.39052 | 61.6241 | 0.22574 | 61.5233 | -0.023943 | 0.048236 | 61.6486 | 0.012299 | 61.4359 | 62.8128 | 62.5498 | 62.885 | 63.0597 | 63.0842 | 62.9688 | 61.946 | 123.1796 | 61.7812 | 123.0788 | 61.5315 | 61.6037 | 123.204 | 61.5678 | 122.9914 | 61.5759 | 61.6118 | 61.4751 | 61.511
7409.0625 | 123.4222 | -61.5005 | 61.5601 | 1.1245 | 0.86151 | 1.1968 | 1.3852 | 1.3959 | 1.2943 | 0.26691 | 61.6287 | 0.22574 | 61.5279 | -0.028522 | 0.052814 | 61.6531 | 0.007721 | 61.4359 | 62.6251 | 62.3621 | 62.6973 | 62.8857 | 62.8965 | 62.7948 | 61.7675 | 123.1292 | 61.7263 | 123.0284 | 61.472 | 61.5534 | 123.1537 | 61.5083 | 122.9365 | 61.5759 | 61.6209 | 61.4751 | 61.5202
7410.1094 | 123.2346 | -61.5417 | 61.6104 | 0.72162 | 0.45399 | 0.77094 | 0.9731 | 0.99306 | 0.90054 | -0.10392 | 61.6561 | 0.2349 | 61.5691 | -0.028522 | 0.052814 | 61.6257 | 0.007721 | 61.4039 | 62.2634 | 61.9957 | 62.3127 | 62.5148 | 62.5348 | 62.4423 | 61.4378 | 123.1979 | 61.7766 | 123.1108 | 61.5132 | 61.5946 | 123.1674 | 61.5495 | 122.9456 | 61.6033 | 61.6484 | 61.5163 | 61.5614
7411.0625 | 123.3948 | -61.4914 | 61.5967 | 0.68957 | 0.42652 | 0.76178 | 0.93189 | 0.95186 | 0.85933 | -0.12681 | 61.6516 | 0.23948 | 61.5508 | -0.023943 | 0.043657 | 61.6165 | 0.012299 | 61.4039 | 62.181 | 61.9179 | 62.2532 | 62.4233 | 62.4432 | 62.3507 | 61.3646 | 123.143 | 61.7309 | 123.0422 | 61.4675 | 61.5351 | 123.1079 | 61.5037 | 122.8953 | 61.6079 | 61.6393 | 61.5071 | 61.5385
7412.0781 | 123.3444 | -61.4868 | 61.5601 | 0.82234 | 0.54099 | 0.89456 | 1.0692 | 1.0846 | 0.97837 | -0.026092 | 61.6378 | 0.23032 | 61.5416 | -0.028522 | 0.048236 | 61.6348 | 0.007721 | 61.3993 | 62.3092 | 62.0278 | 62.3814 | 62.5561 | 62.5714 | 62.4652 | 61.4607 | 123.1246 | 61.7171 | 123.0284 | 61.4583 | 61.5351 | 123.1216 | 61.4945 | 122.8861 | 61.5896 | 61.6301 | 61.4934 | 61.5339
7413.0625 | 123.3261 | -61.5051 | 61.5555 | 0.98717 | 0.71956 | 1.0548 | 1.2386 | 1.2632 | 1.1523 | 0.12041 | 61.6332 | 0.2349 | 61.5553 | -0.023943 | 0.057392 | 61.6394 | 0.012299 | 61.4313 | 62.4923 | 62.2247 | 62.5599 | 62.7438 | 62.7683 | 62.6575 | 61.6255 | 123.1384 | 61.74 | 123.0605 | 61.4812 | 61.5625 | 123.1445 | 61.5174 | 122.9365 | 61.5759 | 61.6209 | 61.4979 | 61.543
7414.0938 | 123.3673 | -61.5143 | 61.5646 | 0.71246 | 0.44483 | 0.77094 | 0.94105 | 0.96559 | 0.90054 | -0.1085 | 61.6516 | 0.24405 | 61.5782 | -0.028522 | 0.048236 | 61.6211 | 0.016878 | 61.3993 | 62.2267 | 61.9591 | 62.2852 | 62.4553 | 62.4799 | 62.4148 | 61.4058 | 123.1658 | 61.7583 | 123.0925 | 61.4858 | 61.5625 | 123.1354 | 61.5312 | 122.9136 | 61.6033 | 61.6347 | 61.53 | 61.5614
7415.0625 | 123.3902 | -61.5051 | 61.5692 | 0.57511 | 0.31205 | 0.62443 | 0.81743 | 0.83741 | 0.74945 | -0.22295 | 61.6607 | 0.2349 | 61.5553 | -0.028522 | 0.048236 | 61.6165 | 0.007721 | 61.3947 | 62.0802 | 61.8172 | 62.1296 | 62.3226 | 62.3425 | 62.2546 | 61.2822 | 123.1658 | 61.74 | 123.0605 | 61.4766 | 61.5534 | 123.1216 | 61.5128 | 122.8998 | 61.6125 | 61.653 | 61.5071 | 61.5476
7416.0938 | 123.3582 | -61.4914 | 61.5509 | 0.62089 | 0.36699 | 0.67021 | 0.83574 | 0.8603 | 0.78608 | -0.16344 | 61.647 | 0.22574 | 61.5462 | -0.028522 | 0.048236 | 61.6211 | 0.007721 | 61.3947 | 62.1123 | 61.8584 | 62.1616 | 62.3271 | 62.3517 | 62.2775 | 61.328 | 123.1384 | 61.7171 | 123.0376 | 61.4629 | 61.5396 | 123.1125 | 61.4991 | 122.8861 | 61.5987 | 61.6393 | 61.4979 | 61.5385
7417.0625 | 123.3536 | -61.5234 | 61.5784 | 0.62089 | 0.36699 | 0.6931 | 0.85405 | 0.88777 | 0.77692 | -0.19091 | 61.6607 | 0.2349 | 61.5828 | -0.019364 | 0.052814 | 61.6165 | 0.016878 | 61.3901 | 62.1443 | 61.8904 | 62.2165 | 62.3775 | 62.4112 | 62.3004 | 61.3325 | 123.1842 | 61.7583 | 123.1062 | 61.5041 | 61.5763 | 123.14 | 61.5403 | 122.9136 | 61.6079 | 61.6438 | 61.53 | 61.5659
7418.0781 | 123.3719 | -61.4639 | 61.5784 | 0.64837 | 0.37615 | 0.6931 | 0.8861 | 0.91523 | 0.81355 | -0.15886 | 61.647 | 0.2349 | 61.5599 | -0.023943 | 0.043657 | 61.6211 | 0.012299 | 61.3947 | 62.1123 | 61.8401 | 62.157 | 62.35 | 62.3792 | 62.2775 | 61.3051 | 123.1109 | 61.6988 | 123.0238 | 61.44 | 61.5076 | 123.085 | 61.4762 | 122.8586 | 61.6033 | 61.6347 | 61.5163 | 61.5476
7419.0625 | 123.3673 | -61.4502 | 61.6013 | 0.35993 | 0.11516 | 0.40923 | 0.5885 | 0.61767 | 0.53884 | -0.40608 | 61.6653 | 0.23032 | 61.5645 | -0.023943 | 0.043657 | 61.6074 | 0.012299 | 61.381 | 61.8101 | 61.5654 | 61.8594 | 62.0387 | 62.0679 | 61.989 | 61.0441 | 123.1155 | 61.6805 | 123.0147 | 61.4263 | 61.4939 | 123.0576 | 61.4625 | 122.8312 | 61.6216 | 61.653 | 61.5208 | 61.5522
7420.1094 | 123.2483 | -61.4868 | 61.6333 | 0.41487 | 0.17011 | 0.46875 | 0.62971 | 0.66344 | 0.58005 | -0.36488 | 61.6653 | 0.23032 | 61.5782 | -0.023943 | 0.048236 | 61.6074 | 0.012299 | 61.3947 | 61.9017 | 61.6569 | 61.9556 | 62.1165 | 62.1503 | 62.0669 | 61.1219 | 123.1521 | 61.7171 | 123.065 | 61.4629 | 61.5351 | 123.0942 | 61.4991 | 122.8815 | 61.6171 | 61.653 | 61.53 | 61.5659
7421.0625 | 123.3673 | -61.4594 | 61.5875 | 0.54306 | 0.28458 | 0.60153 | 0.76248 | 0.79163 | 0.70366 | -0.24584 | 61.6607 | 0.2349 | 61.5874 | -0.028522 | 0.048236 | 61.6119 | 0.012299 | 61.3993 | 62.0024 | 61.7439 | 62.0609 | 62.2218 | 62.251 | 62.163 | 61.2135 | 123.1201 | 61.6942 | 123.0467 | 61.4308 | 61.5076 | 123.0713 | 61.4716 | 122.8586 | 61.6125 | 61.6484 | 61.5392 | 61.5751
7422.0938 | 123.2574 | -61.5372 | 61.5967 | 0.59342 | 0.3441 | 0.65648 | 0.81285 | 0.83741 | 0.73571 | -0.19091 | 61.6516 | 0.22574 | 61.5645 | -0.028522 | 0.048236 | 61.6119 | 0.012299 | 61.3993 | 62.1306 | 61.8813 | 62.1936 | 62.35 | 62.3746 | 62.2729 | 61.3463 | 123.1887 | 61.7629 | 123.1017 | 61.5086 | 61.5854 | 123.1491 | 61.5495 | 122.9365 | 61.6033 | 61.6393 | 61.5163 | 61.5522
7423.0625 | 123.3627 | -61.4822 | 61.5829 | 0.46065 | 0.22047 | 0.53743 | 0.68007 | 0.70922 | 0.58005 | -0.33283 | 61.6653 | 0.23032 | 61.5553 | -0.019364 | 0.052814 | 61.6074 | 0.012299 | 61.3901 | 61.9429 | 61.7027 | 62.0197 | 62.1623 | 62.1915 | 62.0623 | 61.1494 | 123.1475 | 61.7126 | 123.0376 | 61.4629 | 61.5351 | 123.0896 | 61.4945 | 122.8724 | 61.6125 | 61.653 | 61.5025 | 61.543
7424.0781 | 123.262 | -61.5143 | 61.5967 | 0.54306 | 0.29831 | 0.59238 | 0.75791 | 0.78247 | 0.68993 | -0.23211 | 61.6561 | 0.2349 | 61.5737 | -0.023943 | 0.048236 | 61.6119 | 0.007721 | 61.3901 | 62.0573 | 61.8126 | 62.1067 | 62.2722 | 62.2968 | 62.2042 | 61.2822 | 123.1704 | 61.7492 | 123.0879 | 61.4903 | 61.5625 | 123.1262 | 61.522 | 122.9044 | 61.6079 | 61.6484 | 61.5254 | 61.5659
7425.0781 | 123.3536 | -61.5234 | 61.5005 | 0.80403 | 0.55015 | 0.87167 | 1.0097 | 1.0434 | 0.96921 | -0.039826 | 61.6378 | 0.2349 | 61.5782 | -0.033101 | 0.048236 | 61.6303 | 0.012299 | 61.3993 | 62.3275 | 62.0736 | 62.3951 | 62.5332 | 62.5669 | 62.4926 | 61.4836 | 123.1613 | 61.7583 | 123.1017 | 61.4903 | 61.5717 | 123.1537 | 61.5357 | 122.9227 | 61.5896 | 61.6255 | 61.53 | 61.5659
7426.0938 | 123.349 | -61.4822 | 61.5646 | 0.69415 | 0.46315 | 0.75263 | 0.909 | 0.91981 | 0.85475 | -0.11765 | 61.6516 | 0.23948 | 61.5691 | -0.033101 | 0.043657 | 61.6211 | 0.007721 | 61.3993 | 62.1764 | 61.9454 | 62.2349 | 62.3912 | 62.4021 | 62.337 | 61.3646 | 123.1338 | 61.7217 | 123.0513 | 61.4491 | 61.5259 | 123.1033 | 61.49 | 122.8815 | 61.6079 | 61.6438 | 61.5254 | 61.5614
7427.0625 | 123.3444 | -61.496 | 61.5921 | 0.67584 | 0.44941 | 0.73431 | 0.909 | 0.92897 | 0.81812 | -0.14512 | 61.647 | 0.23032 | 61.5553 | -0.023943 | 0.043657 | 61.6211 | 0.012299 | 61.3993 | 62.1718 | 61.9454 | 62.2303 | 62.405 | 62.4249 | 62.3141 | 61.3508 | 123.143 | 61.7263 | 123.0513 | 61.472 | 61.5396 | 123.1171 | 61.5083 | 122.8953 | 61.6033 | 61.6347 | 61.5117 | 61.543
7428.0938 | 123.3307 | -61.528 | 61.5417 | 0.80403 | 0.56846 | 0.87167 | 1.0189 | 1.0526 | 0.97837 | -0.044405 | 61.6378 | 0.22116 | 61.537 | -0.028522 | 0.048236 | 61.6303 | 0.007721 | 61.413 | 62.332 | 62.0965 | 62.3997 | 62.5469 | 62.5806 | 62.5064 | 61.4836 | 123.1658 | 61.7492 | 123.065 | 61.4995 | 61.5763 | 123.1583 | 61.5357 | 122.941 | 61.5896 | 61.6301 | 61.4888 | 61.5293
7429.0625 | 123.3994 | -61.5097 | 61.5692 | 0.95512 | 0.72414 | 1.009 | 1.1608 | 1.1853 | 1.1523 | 0.13414 | 61.6241 | 0.2349 | 61.5279 | -0.028522 | 0.052814 | 61.644 | 0.012299 | 61.4176 | 62.4648 | 62.2338 | 62.5187 | 62.6705 | 62.695 | 62.6621 | 61.6438 | 123.1338 | 61.7446 | 123.0376 | 61.4812 | 61.5625 | 123.1537 | 61.522 | 122.9273 | 61.5713 | 61.6118 | 61.4751 | 61.5156
7430.0938 | 123.317 | -61.5463 | 61.5601 | 0.83608 | 0.59136 | 0.89456 | 1.0418 | 1.0663 | 1.0104 | -0.007779 | 61.647 | 0.23948 | 61.5553 | -0.028522 | 0.048236 | 61.6257 | 0.007721 | 61.413 | 62.3824 | 62.1377 | 62.4409 | 62.5881 | 62.6126 | 62.5567 | 61.5385 | 123.1933 | 61.7858 | 123.1017 | 61.5178 | 61.5946 | 123.172 | 61.554 | 122.9593 | 61.5987 | 61.6393 | 61.5071 | 61.5476
7431.0625 | 123.3444 | -61.4548 | 61.6058 | 0.73993 | 0.51352 | 0.81215 | 0.9502 | 0.97475 | 0.89596 | -0.1085 | 61.6561 | 0.23032 | 61.5828 | -0.028522 | 0.048236 | 61.6257 | 0.007721 | 61.3993 | 62.1947 | 61.9683 | 62.2669 | 62.405 | 62.4295 | 62.3507 | 61.3463 | 123.1109 | 61.6851 | 123.0376 | 61.4263 | 61.503 | 123.0804 | 61.4625 | 122.8541 | 61.6079 | 61.6484 | 61.5346 | 61.5751
7432.0781 | 123.262 | -61.5326 | 61.5738 | 0.73078 | 0.4952 | 0.78926 | 0.93189 | 0.95643 | 0.8868 | -0.1085 | 61.6561 | 0.2349 | 61.5691 | -0.023943 | 0.052814 | 61.6211 | 0.012299 | 61.4039 | 62.2634 | 62.0278 | 62.3218 | 62.4645 | 62.489 | 62.4194 | 61.4241 | 123.1887 | 61.7675 | 123.1017 | 61.5086 | 61.5854 | 123.1537 | 61.5449 | 122.9365 | 61.6033 | 61.6438 | 61.5163 | 61.5568
7433.0625 | 123.3719 | -61.4868 | 61.5601 | 0.68499 | 0.45399 | 0.73431 | 0.87695 | 0.9015 | 0.85017 | -0.13597 | 61.647 | 0.23032 | 61.5416 | -0.033101 | 0.048236 | 61.6211 | 0.012299 | 61.4039 | 62.1718 | 61.9408 | 62.2211 | 62.3638 | 62.3883 | 62.337 | 61.3508 | 123.1338 | 61.7171 | 123.0284 | 61.4537 | 61.5351 | 123.1079 | 61.4991 | 122.8907 | 61.5987 | 61.6347 | 61.4934 | 61.5293
7434.0938 | 123.4085 | -61.4822 | 61.5921 | 0.61174 | 0.37615 | 0.66563 | 0.81743 | 0.83741 | 0.7815 | -0.21838 | 61.6607 | 0.2349 | 61.5599 | -0.033101 | 0.048236 | 61.6257 | 0.012299 | 61.3993 | 62.094 | 61.8584 | 62.1479 | 62.2997 | 62.3196 | 62.2637 | 61.2639 | 123.143 | 61.7171 | 123.0422 | 61.4491 | 61.5305 | 123.1079 | 61.4945 | 122.8815 | 61.6125 | 61.6484 | 61.5117 | 61.5476
7435.0625 | 123.2941 | -61.496 | 61.615 | 0.73993 | 0.49978 | 0.78926 | 0.93189 | 0.96101 | 0.90511 | -0.090186 | 61.6561 | 0.2349 | 61.5782 | -0.023943 | 0.052814 | 61.6257 | 0.012299 | 61.4084 | 62.2359 | 61.9958 | 62.2852 | 62.4279 | 62.457 | 62.4011 | 61.4058 | 123.1521 | 61.7309 | 123.0742 | 61.472 | 61.5488 | 123.1216 | 61.5083 | 122.9044 | 61.6033 | 61.6438 | 61.5254 | 61.5659
7436.0938 | 123.2803 | -61.5189 | 61.5784 | 0.7262 | 0.48604 | 0.79841 | 0.93647 | 0.96559 | 0.87307 | -0.11765 | 61.6516 | 0.23032 | 61.5508 | -0.028522 | 0.048236 | 61.6257 | 0.007721 | 61.4039 | 62.2451 | 62.0049 | 62.3173 | 62.4553 | 62.4844 | 62.3919 | 61.4012 | 123.1704 | 61.7492 | 123.0696 | 61.4903 | 61.5671 | 123.1445 | 61.5266 | 122.9227 | 61.6033 | 61.6438 | 61.5025 | 61.543
7437.0625 | 123.3353 | -61.4822 | 61.6058 | 0.4927 | 0.27542 | 0.55575 | 0.71212 | 0.74127 | 0.63957 | -0.30536 | 61.6607 | 0.24405 | 61.5737 | -0.028522 | 0.043657 | 61.6119 | 0.012299 | 61.3901 | 61.9749 | 61.7577 | 62.038 | 62.1944 | 62.2235 | 62.1218 | 61.1769 | 123.143 | 61.7263 | 123.0559 | 61.4537 | 61.5259 | 123.0942 | 61.4945 | 122.8724 | 61.6171 | 61.6484 | 61.53 | 61.5614
7438.0938 | 123.3215 | -61.5051 | 61.5417 | 0.63005 | 0.39905 | 0.6931 | 0.86321 | 0.88777 | 0.76318 | -0.18633 | 61.647 | 0.23032 | 61.5645 | -0.023943 | 0.052814 | 61.6211 | 0.012299 | 61.3947 | 62.1352 | 61.9042 | 62.1982 | 62.3683 | 62.3929 | 62.2683 | 61.3188 | 123.1521 | 61.7354 | 123.0696 | 61.4812 | 61.5579 | 123.1262 | 61.5174 | 122.8998 | 61.5942 | 61.6347 | 61.5117 | 61.5522
7439.0625 | 123.3948 | -61.4822 | 61.5509 | 0.72162 | 0.48604 | 0.79841 | 0.95478 | 0.97932 | 0.87307 | -0.12681 | 61.647 | 0.21658 | 61.5508 | -0.023943 | 0.048236 | 61.6211 | 0.012299 | 61.3993 | 62.2039 | 61.9683 | 62.2807 | 62.437 | 62.4616 | 62.3553 | 61.3554 | 123.1292 | 61.6988 | 123.033 | 61.4583 | 61.5305 | 123.1033 | 61.4945 | 122.8815 | 61.5987 | 61.6347 | 61.5025 | 61.5385
7440.1094 | 123.3398 | -61.5097 | 61.5509 | 0.80403 | 0.55015 | 0.86251 | 1.028 | 1.0617 | 0.93258 | -0.058139 | 61.6516 | 0.2349 | 61.5782 | -0.028522 | 0.048236 | 61.6303 | 0.012299 | 61.4039 | 62.3137 | 62.0599 | 62.3722 | 62.5377 | 62.5714 | 62.4423 | 61.4516 | 123.1613 | 61.7446 | 123.0879 | 61.4812 | 61.5579 | 123.14 | 61.522 | 122.9136 | 61.6033 | 61.6393 | 61.53 | 61.5659
7441.0625 | 123.3444 | -61.4914 | 61.5875 | 0.97343 | 0.7333 | 1.0365 | 1.2112 | 1.222 | 1.0882 | 0.088362 | 61.6332 | 0.2349 | 61.5416 | -0.023943 | 0.052814 | 61.6348 | 0.007721 | 61.4222 | 62.4648 | 62.2247 | 62.5279 | 62.7026 | 62.7133 | 62.5796 | 61.5798 | 123.1246 | 61.7263 | 123.033 | 61.4675 | 61.5442 | 123.1262 | 61.4991 | 122.9136 | 61.5804 | 61.6255 | 61.4888 | 61.5339
7442.0938 | 123.3398 | -61.5326 | 61.5601 | 0.82692 | 0.5822 | 0.89456 | 1.0464 | 1.0755 | 0.97379 | -0.03067 | 61.6378 | 0.2349 | 61.5416 | -0.028522 | 0.048236 | 61.6257 | 0.003143 | 61.4084 | 62.3595 | 62.1148 | 62.4272 | 62.5789 | 62.6081 | 62.5064 | 61.5019 | 123.1704 | 61.7675 | 123.0742 | 61.5041 | 61.5808 | 123.1583 | 61.5357 | 122.941 | 61.5896 | 61.6347 | 61.4934 | 61.5385
7443.0625 | 123.4039 | -61.4685 | 61.6058 | 0.63463 | 0.40363 | 0.69768 | 0.84948 | 0.87861 | 0.78608 | -0.17717 | 61.6561 | 0.23032 | 61.5828 | -0.028522 | 0.048236 | 61.6165 | 0.012299 | 61.3993 | 62.1031 | 61.8721 | 62.1662 | 62.318 | 62.3471 | 62.2546 | 61.2913 | 123.1246 | 61.6988 | 123.0513 | 61.44 | 61.5167 | 123.085 | 61.4808 | 122.8678 | 61.6079 | 61.6438 | 61.5346 | 61.5705
7444.0781 | 123.3673 | -61.5051 | 61.5601 | 0.67584 | 0.43568 | 0.72973 | 0.8861 | 0.91981 | 0.84559 | -0.14055 | 61.647 | 0.22574 | 61.5462 | -0.028522 | 0.048236 | 61.6257 | 0.012299 | 61.4039 | 62.181 | 61.9408 | 62.2349 | 62.3912 | 62.4249 | 62.3507 | 61.3646 | 123.1521 | 61.7309 | 123.0513 | 61.4766 | 61.5534 | 123.1308 | 61.5174 | 122.909 | 61.5987 | 61.6347 | 61.4979 | 61.5339
7445.0625 | 123.2803 | -61.4914 | 61.5967 | 0.60258 | 0.36241 | 0.6519 | 0.81743 | 0.83741 | 0.77234 | -0.20922 | 61.6607 | 0.23948 | 61.592 | -0.028522 | 0.048236 | 61.6165 | 0.007721 | 61.3947 | 62.094 | 61.8538 | 62.1433 | 62.3088 | 62.3288 | 62.2637 | 61.2822 | 123.1521 | 61.7309 | 123.0834 | 61.4629 | 61.5396 | 123.1079 | 61.4991 | 122.8861 | 61.6125 | 61.653 | 61.5437 | 61.5842
7446.0781 | 123.3765 | -61.4594 | 61.5601 | 0.61174 | 0.37157 | 0.66105 | 0.81285 | 0.84656 | 0.77234 | -0.17259 | 61.647 | 0.2349 | 61.5553 | -0.028522 | 0.048236 | 61.6211 | 0.012299 | 61.3947 | 62.0711 | 61.8309 | 62.1204 | 62.2722 | 62.3059 | 62.2317 | 61.2868 | 123.1063 | 61.6942 | 123.0147 | 61.4308 | 61.5076 | 123.0804 | 61.4716 | 122.8541 | 61.5987 | 61.6347 | 61.5071 | 61.543
7447.0625 | 123.3673 | -61.5051 | 61.5646 | 0.82234 | 0.57304 | 0.88083 | 1.0372 | 1.0617 | 0.97837 | -0.026092 | 61.6378 | 0.23948 | 61.5462 | -0.028522 | 0.052814 | 61.6257 | 0.012299 | 61.4084 | 62.3275 | 62.0782 | 62.386 | 62.5423 | 62.5669 | 62.4835 | 61.479 | 123.143 | 61.7446 | 123.0513 | 61.4766 | 61.5579 | 123.1308 | 61.5174 | 122.9136 | 61.585 | 61.6255 | 61.4934 | 61.5339
7448.0781 | 123.3627 | -61.496 | 61.528 | 0.90018 | 0.65546 | 0.95409 | 1.115 | 1.135 | 1.0745 | 0.056315 | 61.647 | 0.23032 | 61.5553 | -0.028522 | 0.048236 | 61.6348 | 0.012299 | 61.4084 | 62.3961 | 62.1514 | 62.4501 | 62.611 | 62.6309 | 62.5705 | 61.5523 | 123.143 | 61.7263 | 123.0513 | 61.4674 | 61.5442 | 123.1308 | 61.5083 | 122.9044 | 61.5987 | 61.6347 | 61.5071 | 61.543
7449.0625 | 123.3856 | -61.4914 | 61.5692 | 0.79945 | 0.55015 | 0.87167 | 1.0189 | 1.0434 | 0.96005 | -0.048983 | 61.6378 | 0.2349 | 61.5462 | -0.028522 | 0.039079 | 61.6257 | 0.012299 | 61.4084 | 62.2908 | 62.0415 | 62.3631 | 62.5103 | 62.5348 | 62.4514 | 61.4424 | 123.1292 | 61.7263 | 123.0376 | 61.4629 | 61.5305 | 123.1171 | 61.5037 | 122.8998 | 61.5987 | 61.6255 | 61.5071 | 61.5339
7450.1094 | 123.4039 | -61.4868 | 61.5829 | 1.1062 | 0.84319 | 1.1693 | 1.3485 | 1.3776 | 1.2714 | 0.21197 | 61.6241 | 0.2349 | 61.5233 | -0.019364 | 0.048236 | 61.6486 | 0.007721 | 61.4313 | 62.593 | 62.33 | 62.6561 | 62.8353 | 62.8644 | 62.7582 | 61.6988 | 123.1109 | 61.7217 | 123.0101 | 61.4675 | 61.5351 | 123.1354 | 61.4945 | 122.9182 | 61.5759 | 61.6164 | 61.4751 | 61.5156
7451.0625 | 123.3582 | -61.5189 | 61.5738 | 0.91849 | 0.66004 | 0.98614 | 1.1471 | 1.1624 | 1.0608 | 0.042581 | 61.6424 | 0.23948 | 61.5691 | -0.023943 | 0.048236 | 61.6394 | 0.016878 | 61.4176 | 62.4374 | 62.1789 | 62.505 | 62.6659 | 62.6813 | 62.5796 | 61.5614 | 123.1613 | 61.7583 | 123.0879 | 61.4949 | 61.5671 | 123.1583 | 61.5357 | 122.9365 | 61.5942 | 61.6255 | 61.5208 | 61.5522
7452.0938 | 123.3719 | -61.5005 | 61.5509 | 0.85897 | 0.61425 | 0.92661 | 1.083 | 1.0984 | 1.0242 | 0.001377 | 61.647 | 0.23948 | 61.5691 | -0.028522 | 0.039079 | 61.6257 | 0.007721 | 61.4084 | 62.3595 | 62.1148 | 62.4272 | 62.5835 | 62.5989 | 62.5247 | 61.5019 | 123.1475 | 61.74 | 123.0696 | 61.472 | 61.5396 | 123.1262 | 61.5083 | 122.909 | 61.6079 | 61.6393 | 61.53 | 61.5614
7453.0625 | 123.3582 | -61.4914 | 61.5692 | 0.90933 | 0.66462 | 0.97698 | 1.1196 | 1.1441 | 1.0654 | 0.051737 | 61.6378 | 0.23032 | 61.5324 | -0.023943 | 0.043657 | 61.6303 | 0.012299 | 61.4222 | 62.4007 | 62.156 | 62.4684 | 62.611 | 62.6355 | 62.5568 | 61.5431 | 123.1292 | 61.7217 | 123.0238 | 61.4675 | 61.5351 | 123.1216 | 61.5037 | 122.9136 | 61.5942 | 61.6255 | 61.4888 | 61.5202
7454.0781 | 123.4131 | -61.5051 | 61.5646 | 0.86813 | 0.62341 | 0.93119 | 1.0784 | 1.0938 | 1.0196 | 0.005955 | 61.6424 | 0.23032 | 61.5462 | -0.023943 | 0.048236 | 61.6303 | 0.012299 | 61.413 | 62.3733 | 62.1285 | 62.4363 | 62.5835 | 62.5989 | 62.5247 | 61.5111 | 123.1475 | 61.7354 | 123.0513 | 61.4812 | 61.5534 | 123.1354 | 61.5174 | 122.9181 | 61.5942 | 61.6301 | 61.4979 | 61.5339
7455.0625 | 123.3261 | -61.5097 | 61.5921 | 0.99632 | 0.74704 | 1.0594 | 1.2249 | 1.254 | 1.1569 | 0.12499 | 61.6424 | 0.2349 | 61.5737 | -0.023943 | 0.052814 | 61.6348 | 0.012299 | 61.4176 | 62.506 | 62.2567 | 62.5691 | 62.7346 | 62.7637 | 62.6666 | 61.6347 | 123.1521 | 61.7446 | 123.0834 | 61.4858 | 61.5625 | 123.1445 | 61.522 | 122.9273 | 61.5896 | 61.6301 | 61.5208 | 61.5614
7456.0938 | 123.3948 | -61.5051 | 61.5326 | 0.91849 | 0.66004 | 0.9724 | 1.1562 | 1.1716 | 1.0928 | 0.047159 | 61.6378 | 0.22574 | 61.5462 | -0.023943 | 0.043657 | 61.6394 | 0.007721 | 61.4084 | 62.4236 | 62.1652 | 62.4775 | 62.6614 | 62.6767 | 62.598 | 61.5523 | 123.143 | 61.7309 | 123.0513 | 61.4812 | 61.5488 | 123.1445 | 61.5128 | 122.9136 | 61.5942 | 61.6301 | 61.5025 | 61.5385
7457.0625 | 123.381 | -61.4822 | 61.5738 | 0.65752 | 0.40363 | 0.716 | 0.88153 | 0.90608 | 0.80897 | -0.19091 | 61.6516 | 0.23032 | 61.5462 | -0.023943 | 0.052814 | 61.6257 | 0.016878 | 61.3993 | 62.1398 | 61.8859 | 62.1982 | 62.3638 | 62.3883 | 62.2912 | 61.2913 | 123.1338 | 61.7126 | 123.0284 | 61.4583 | 61.5351 | 123.1079 | 61.4991 | 122.8815 | 61.5987 | 61.6347 | 61.4934 | 61.5293
7458.0781 | 123.3398 | -61.528 | 61.5601 | 0.54764 | 0.29373 | 0.58322 | 0.72586 | 0.76416 | 0.70824 | -0.26874 | 61.6607 | 0.23032 | 61.5691 | -0.033101 | 0.048236 | 61.6119 | 0.012299 | 61.3856 | 62.0757 | 61.8217 | 62.1112 | 62.2539 | 62.2922 | 62.2363 | 61.2593 | 123.1887 | 61.7583 | 123.0971 | 61.4949 | 61.5763 | 123.14 | 61.5403 | 122.9136 | 61.6125 | 61.6484 | 61.5208 | 61.5568
7459.0625 | 123.317 | -61.4914 | 61.5509 | 0.48812 | 0.26168 | 0.55117 | 0.68007 | 0.70007 | 0.66704 | -0.31452 | 61.6607 | 0.2349 | 61.592 | -0.028522 | 0.048236 | 61.6119 | 0.012299 | 61.381 | 61.9795 | 61.7531 | 62.0426 | 62.1715 | 62.1915 | 62.1584 | 61.1769 | 123.1521 | 61.7263 | 123.0834 | 61.4629 | 61.5396 | 123.1033 | 61.5037 | 122.8724 | 61.6125 | 61.6484 | 61.5437 | 61.5797
7460.1094 | 123.3261 | -61.528 | 61.5234 | 0.55222 | 0.29831 | 0.59238 | 0.74875 | 0.76416 | 0.72656 | -0.24127 | 61.6516 | 0.23032 | 61.5599 | -0.028522 | 0.039079 | 61.6165 | 0.007721 | 61.3947 | 62.0802 | 61.8263 | 62.1204 | 62.2768 | 62.2922 | 62.2546 | 61.2867 | 123.1796 | 61.7583 | 123.0879 | 61.4995 | 61.5671 | 123.1445 | 61.5357 | 122.9227 | 61.6125 | 61.6438 | 61.5208 | 61.5522
7461.0625 | 123.3673 | -61.4822 | 61.6058 | 0.56138 | 0.32121 | 0.61069 | 0.75791 | 0.78705 | 0.72656 | -0.25042 | 61.647 | 0.23032 | 61.5508 | -0.033101 | 0.052814 | 61.6119 | 0.007721 | 61.3993 | 62.0436 | 61.8034 | 62.0929 | 62.2401 | 62.2693 | 62.2088 | 61.2318 | 123.1292 | 61.7126 | 123.033 | 61.4491 | 61.5351 | 123.0942 | 61.49 | 122.8815 | 61.5942 | 61.6393 | 61.4979 | 61.543
7462.0781 | 123.3307 | -61.5189 | 61.5738 | 0.41487 | 0.17011 | 0.45502 | 0.60224 | 0.63598 | 0.58005 | -0.39235 | 61.6699 | 0.23032 | 61.5965 | -0.028522 | 0.048236 | 61.6074 | 0.007721 | 61.3856 | 61.9337 | 61.689 | 61.9739 | 62.1211 | 62.1548 | 62.0989 | 61.1265 | 123.1887 | 61.7492 | 123.1154 | 61.4903 | 61.5671 | 123.1262 | 61.5266 | 122.9044 | 61.6216 | 61.6622 | 61.5483 | 61.5888
7463.0625 | 123.3215 | -61.4777 | 61.5921 | 0.46065 | 0.22505 | 0.5008 | 0.62971 | 0.64971 | 0.63499 | -0.32825 | 61.6561 | 0.2349 | 61.5828 | -0.028522 | 0.048236 | 61.6074 | 0.012299 | 61.3856 | 61.9383 | 61.7027 | 61.9785 | 62.1074 | 62.1274 | 62.1126 | 61.1494 | 123.1338 | 61.7126 | 123.0605 | 61.4491 | 61.5259 | 123.085 | 61.49 | 122.8632 | 61.6079 | 61.6438 | 61.5346 | 61.5705
7464.0938 | 123.2666 | -61.5234 | 61.6058 | 0.60258 | 0.37157 | 0.66105 | 0.79911 | 0.8191 | 0.7815 | -0.20006 | 61.6516 | 0.2349 | 61.5553 | -0.033101 | 0.043657 | 61.6119 | 0.016878 | 61.3993 | 62.126 | 61.895 | 62.1845 | 62.3225 | 62.3425 | 62.3049 | 61.3234 | 123.175 | 61.7583 | 123.0788 | 61.4903 | 61.5671 | 123.1354 | 61.5403 | 122.9227 | 61.6079 | 61.6347 | 61.5117 | 61.5385
7465.0625 | 123.2574 | -61.4914 | 61.6653 | 0.63921 | 0.39905 | 0.6931 | 0.83116 | 0.85572 | 0.80439 | -0.15886 | 61.6516 | 0.23948 | 61.5599 | -0.028522 | 0.057392 | 61.6211 | 0.016878 | 61.3993 | 62.1306 | 61.8904 | 62.1845 | 62.3226 | 62.3471 | 62.2958 | 61.3325 | 123.143 | 61.7309 | 123.0513 | 61.4629 | 61.5488 | 123.1125 | 61.5083 | 122.8907 | 61.5942 | 61.6347 | 61.5025 | 61.543
7466.0938 | 123.3078 | -61.5005 | 61.5967 | 0.58427 | 0.34868 | 0.64274 | 0.78538 | 0.80536 | 0.74487 | -0.22753 | 61.6561 | 0.23948 | 61.592 | -0.023943 | 0.043657 | 61.6119 | 0.012299 | 61.3947 | 62.0848 | 61.8492 | 62.1433 | 62.2859 | 62.3059 | 62.2454 | 61.273 | 123.1567 | 61.74 | 123.0925 | 61.4766 | 61.5442 | 123.1125 | 61.5128 | 122.8953 | 61.6125 | 61.6438 | 61.5483 | 61.5797
7467.0625 | 123.3261 | -61.4914 | 61.5829 | 0.52017 | 0.28458 | 0.59238 | 0.7167 | 0.74585 | 0.67162 | -0.27789 | 61.6516 | 0.2349 | 61.5553 | -0.028522 | 0.043657 | 61.6119 | 0.007721 | 61.3947 | 62.0116 | 61.776 | 62.0838 | 62.2081 | 62.2372 | 62.163 | 61.2135 | 123.143 | 61.7263 | 123.0467 | 61.4629 | 61.5351 | 123.1033 | 61.4991 | 122.8861 | 61.6079 | 61.6438 | 61.5117 | 61.5476
7468.0781 | 123.2574 | -61.5509 | 61.5234 | 0.9597 | 0.70583 | 1.0182 | 1.1517 | 1.1716 | 1.1203 | 0.12041 | 61.6424 | 0.23948 | 61.5508 | -0.028522 | 0.048236 | 61.6394 | 0.007721 | 61.413 | 62.5106 | 62.2567 | 62.5691 | 62.7026 | 62.7225 | 62.6712 | 61.6713 | 123.1933 | 61.7904 | 123.1017 | 61.5224 | 61.5991 | 123.1903 | 61.5586 | 122.9639 | 61.5942 | 61.6347 | 61.5025 | 61.543
7469.0625 | 123.3902 | -61.5005 | 61.5509 | 0.75367 | 0.50894 | 0.82131 | 0.93647 | 0.96559 | 0.91885 | -0.062717 | 61.647 | 0.23948 | 61.5782 | -0.033101 | 0.048236 | 61.6211 | 0.007721 | 61.4084 | 62.2542 | 62.0095 | 62.3219 | 62.437 | 62.4661 | 62.4194 | 61.4378 | 123.1475 | 61.74 | 123.0788 | 61.4674 | 61.5488 | 123.1216 | 61.5083 | 122.909 | 61.5987 | 61.6393 | 61.53 | 61.5705
7470.1094 | 123.23 | -61.5601 | 61.5921 | 0.71246 | 0.46315 | 0.77552 | 0.89526 | 0.92439 | 0.86849 | -0.1085 | 61.647 | 0.23032 | 61.5508 | -0.023943 | 0.048236 | 61.6165 | 0.012299 | 61.3993 | 62.2725 | 62.0232 | 62.3356 | 62.4553 | 62.4844 | 62.4285 | 61.4516 | 123.207 | 61.7904 | 123.1108 | 61.5361 | 61.6083 | 123.1766 | 61.5724 | 122.9593 | 61.5987 | 61.6347 | 61.5025 | 61.5385
7471.0625 | 123.2712 | -61.5143 | 61.6196 | 0.85897 | 0.60967 | 0.92204 | 1.0372 | 1.0526 | 1.015 | 0.015112 | 61.6378 | 0.2349 | 61.5508 | -0.023943 | 0.052814 | 61.6257 | 0.012299 | 61.4176 | 62.3733 | 62.124 | 62.4363 | 62.5515 | 62.5669 | 62.5293 | 61.5294 | 123.1521 | 61.7492 | 123.065 | 61.4903 | 61.5671 | 123.14 | 61.5266 | 122.9319 | 61.585 | 61.6255 | 61.4979 | 61.5385
7472.0938 | 123.2483 | -61.5417 | 61.6013 | 0.84981 | 0.59136 | 0.92204 | 1.0143 | 1.048 | 1.0058 | 0.01969 | 61.647 | 0.23948 | 61.5737 | -0.028522 | 0.048236 | 61.6348 | 0.016878 | 61.413 | 62.3916 | 62.1331 | 62.4638 | 62.556 | 62.5897 | 62.5476 | 61.5614 | 123.1887 | 61.7812 | 123.1154 | 61.5132 | 61.59 | 123.1766 | 61.5586 | 122.9548 | 61.5987 | 61.6301 | 61.5254 | 61.5568
7473.0625 | 123.3032 | -61.5189 | 61.5967 | 0.70331 | 0.44483 | 0.77552 | 0.8861 | 0.90608 | 0.85017 | -0.12681 | 61.6424 | 0.22574 | 61.537 | -0.028522 | 0.052814 | 61.6165 | 0.003143 | 61.4039 | 62.2222 | 61.9637 | 62.2944 | 62.405 | 62.4249 | 62.369 | 61.392 | 123.1613 | 61.7446 | 123.0559 | 61.4903 | 61.5717 | 123.1354 | 61.522 | 122.9227 | 61.5896 | 61.6393 | 61.4842 | 61.5339
7474.0781 | 123.3032 | -61.5005 | 61.6104 | 0.61174 | 0.37157 | 0.67479 | 0.78538 | 0.80994 | 0.76776 | -0.18633 | 61.6607 | 0.2349 | 61.5874 | -0.028522 | 0.057392 | 61.6119 | 0.012299 | 61.4039 | 62.1123 | 61.8721 | 62.1753 | 62.2859 | 62.3105 | 62.2683 | 61.3142 | 123.1613 | 61.7354 | 123.0879 | 61.472 | 61.5579 | 123.1125 | 61.5128 | 122.9044 | 61.6033 | 61.6484 | 61.53 | 61.5751
7475.0625 | 123.3261 | -61.5463 | 61.5601 | 0.80861 | 0.5593 | 0.87167 | 0.98225 | 1.0068 | 0.95548 | -0.035248 | 61.6424 | 0.23032 | 61.5416 | -0.023943 | 0.052814 | 61.6303 | 0.007721 | 61.4039 | 62.3549 | 62.1056 | 62.418 | 62.5286 | 62.5531 | 62.5018 | 61.5111 | 123.1887 | 61.7766 | 123.0879 | 61.5224 | 61.5991 | 123.1766 | 61.554 | 122.9502 | 61.5896 | 61.6347 | 61.4888 | 61.5339
7476.0938 | 123.3307 | -61.4914 | 61.5784 | 0.85897 | 0.59593 | 0.92204 | 1.0464 | 1.0755 | 0.99668 | 0.001377 | 61.6378 | 0.23032 | 61.5416 | -0.019364 | 0.052814 | 61.6257 | 0.007721 | 61.4084 | 62.3504 | 62.0873 | 62.4134 | 62.5377 | 62.5669 | 62.4881 | 61.4928 | 123.1292 | 61.7217 | 123.033 | 61.472 | 61.5442 | 123.1171 | 61.4991 | 122.8998 | 61.585 | 61.6301 | 61.4888 | 61.5339
7477.0625 | 123.3536 | -61.496 | 61.5692 | 0.53391 | 0.28 | 0.5878 | 0.73501 | 0.755 | 0.68535 | -0.26416 | 61.6699 | 0.2349 | 61.5874 | -0.033101 | 0.048236 | 61.6119 | 0.003143 | 61.3901 | 62.0299 | 61.776 | 62.0838 | 62.231 | 62.251 | 62.1813 | 61.2318 | 123.1658 | 61.7309 | 123.0834 | 61.4629 | 61.5442 | 123.1079 | 61.4991 | 122.8861 | 61.6216 | 61.6667 | 61.5392 | 61.5842
7478.0781 | 123.3124 | -61.5189 | 61.6196 | 0.5568 | 0.30747 | 0.61985 | 0.76248 | 0.78705 | 0.72198 | -0.23669 | 61.6607 | 0.23948 | 61.5553 | -0.033101 | 0.048236 | 61.6074 | 0.012299 | 61.3993 | 62.0757 | 61.8263 | 62.1387 | 62.2813 | 62.3059 | 62.2408 | 61.2822 | 123.1796 | 61.7583 | 123.0742 | 61.4858 | 61.5671 | 123.1262 | 61.5312 | 122.9181 | 61.6125 | 61.6484 | 61.5071 | 61.543
7479.0625 | 123.2071 | -61.528 | 61.5417 | 0.65752 | 0.38989 | 0.72973 | 0.88153 | 0.91523 | 0.80439 | -0.17259 | 61.6653 | 0.23948 | 61.5737 | -0.028522 | 0.057392 | 61.6165 | 0.012299 | 61.3947 | 62.1855 | 61.9179 | 62.2577 | 62.4095 | 62.4432 | 62.3324 | 61.3554 | 123.1933 | 61.7675 | 123.1017 | 61.4995 | 61.5854 | 123.1445 | 61.5403 | 122.9227 | 61.6079 | 61.653 | 61.5163 | 61.5614
7480.0938 | 123.2758 | -61.5051 | 61.6379 | 0.48812 | 0.23421 | 0.55575 | 0.69381 | 0.71838 | 0.62583 | -0.3191 | 61.6699 | 0.23032 | 61.5737 | -0.023943 | 0.052814 | 61.6074 | 0.016878 | 61.3947 | 61.9932 | 61.7393 | 62.0609 | 62.1989 | 62.2235 | 62.131 | 61.186 | 123.175 | 61.7354 | 123.0788 | 61.4812 | 61.5579 | 123.1125 | 61.522 | 122.8998 | 61.6171 | 61.653 | 61.5208 | 61.5568
7481.0625 | 123.3902 | -61.4868 | 61.5646 | 0.56595 | 0.31205 | 0.63816 | 0.75333 | 0.79163 | 0.70366 | -0.24584 | 61.6607 | 0.23032 | 61.5553 | -0.028522 | 0.048236 | 61.6165 | 0.012299 | 61.3901 | 62.0528 | 61.7989 | 62.125 | 62.2401 | 62.2784 | 62.1905 | 61.241 | 123.1475 | 61.7171 | 123.0422 | 61.4583 | 61.5351 | 123.1033 | 61.4991 | 122.8769 | 61.6125 | 61.6484 | 61.5071 | 61.543
7482.0625 | 123.2941 | -61.5189 | 61.6333 | 0.55222 | 0.30289 | 0.63358 | 0.74875 | 0.77789 | 0.69909 | -0.26416 | 61.6607 | 0.2349 | 61.5828 | -0.028522 | 0.048236 | 61.6074 | 0.021456 | 61.4039 | 62.0711 | 61.8218 | 62.1524 | 62.2676 | 62.2968 | 62.2179 | 61.2547 | 123.1796 | 61.7538 | 123.1017 | 61.4903 | 61.5671 | 123.1262 | 61.5403 | 122.9227 | 61.6125 | 61.6393 | 61.5346 | 61.5614
7483.0938 | 123.2712 | -61.5005 | 61.5784 | 0.53391 | 0.28458 | 0.61069 | 0.73959 | 0.76416 | 0.67162 | -0.28705 | 61.6561 | 0.23032 | 61.5508 | -0.03768 | 0.048236 | 61.6074 | 0.012299 | 61.3856 | 62.0345 | 61.7851 | 62.1112 | 62.2401 | 62.2647 | 62.1722 | 61.2135 | 123.1567 | 61.7309 | 123.0513 | 61.4629 | 61.5488 | 123.1079 | 61.5128 | 122.8861 | 61.6079 | 61.6438 | 61.5025 | 61.5385
7484.0625 | 123.2895 | -61.5005 | 61.6058 | 0.56138 | 0.31663 | 0.63816 | 0.76706 | 0.78705 | 0.68535 | -0.26416 | 61.6699 | 0.2349 | 61.5691 | -0.023943 | 0.048236 | 61.6074 | 0.007721 | 61.3947 | 62.0619 | 61.8172 | 62.1387 | 62.2676 | 62.2876 | 62.1859 | 61.2364 | 123.1704 | 61.7354 | 123.0696 | 61.4766 | 61.5488 | 123.1079 | 61.5083 | 122.8953 | 61.6216 | 61.6622 | 61.5208 | 61.5614
7485.0938 | 123.2712 | -61.5189 | 61.615 | 0.51559 | 0.26626 | 0.59696 | 0.72128 | 0.74585 | 0.64415 | -0.30994 | 61.6607 | 0.23032 | 61.5691 | -0.019364 | 0.052814 | 61.6074 | 0.007721 | 61.3901 | 62.0345 | 61.7851 | 62.1158 | 62.2401 | 62.2647 | 62.163 | 61.2089 | 123.1796 | 61.7492 | 123.0879 | 61.4995 | 61.5717 | 123.1262 | 61.5266 | 122.909 | 61.6079 | 61.653 | 61.5163 | 61.5614
7486.0625 | 123.2712 | -61.5005 | 61.6196 | 0.52933 | 0.25252 | 0.60611 | 0.75333 | 0.78247 | 0.63957 | -0.31452 | 61.6561 | 0.23032 | 61.5645 | -0.028522 | 0.043657 | 61.6119 | 0.012299 | 61.3947 | 62.0299 | 61.7531 | 62.1067 | 62.2539 | 62.283 | 62.1401 | 61.186 | 123.1567 | 61.7309 | 123.065 | 61.472 | 61.5442 | 123.1125 | 61.5128 | 122.8953 | 61.6125 | 61.6438 | 61.5208 | 61.5522
7487.0625 | 123.2391 | -61.5326 | 61.6058 | 0.48354 | 0.22505 | 0.57406 | 0.72128 | 0.74585 | 0.55716 | -0.36488 | 61.6653 | 0.23948 | 61.5828 | -0.023943 | 0.048236 | 61.6074 | 0.012299 | 61.3947 | 62.0161 | 61.7576 | 62.1067 | 62.2539 | 62.2784 | 62.0897 | 61.1677 | 123.1979 | 61.7721 | 123.1154 | 61.5086 | 61.5808 | 123.14 | 61.5449 | 122.9273 | 61.6171 | 61.653 | 61.5346 | 61.5705
7488.0781 | 123.2895 | -61.4594 | 61.6516 | 0.51101 | 0.2571 | 0.60153 | 0.73501 | 0.76416 | 0.64415 | -0.3191 | 61.6699 | 0.2349 | 61.5645 | -0.019364 | 0.057392 | 61.6074 | 0.012299 | 61.3947 | 61.9704 | 61.7165 | 62.0609 | 62.1944 | 62.2235 | 62.1035 | 61.1403 | 123.1292 | 61.6942 | 123.0238 | 61.44 | 61.5167 | 123.0667 | 61.4716 | 122.8541 | 61.6125 | 61.6576 | 61.5071 | 61.5522
7489.0625 | 123.2849 | -61.5097 | 61.6058 | 0.46065 | 0.21131 | 0.54659 | 0.67091 | 0.69091 | 0.55716 | -0.36488 | 61.6607 | 0.23032 | 61.5599 | -0.023943 | 0.043657 | 61.6028 | 0.012299 | 61.3901 | 61.9704 | 61.721 | 62.0563 | 62.1806 | 62.2006 | 62.0669 | 61.1448 | 123.1704 | 61.74 | 123.0696 | 61.4858 | 61.5534 | 123.1125 | 61.522 | 122.8998 | 61.6171 | 61.6484 | 61.5163 | 61.5476
7490.1094 | 123.2941 | -61.4639 | 61.6745 | 0.062332 | -0.15499 | 0.13909 | 0.26343 | 0.28805 | 0.12221 | -0.78149 | 61.6973 | 0.23948 | 61.6194 | -0.028522 | 0.043657 | 61.5753 | 0.021456 | 61.3718 | 61.5263 | 61.3089 | 61.603 | 61.7274 | 61.752 | 61.5861 | 60.6824 | 123.1613 | 61.7034 | 123.0834 | 61.4354 | 61.5076 | 123.0392 | 61.4854 | 122.8357 | 61.6537 | 61.6759 | 61.5758 | 61.598
7491.0625 | 123.2895 | -61.5051 | 61.5921 | 0.4927 | 0.23879 | 0.56033 | 0.68923 | 0.7138 | 0.62583 | -0.3191 | 61.6561 | 0.2349 | 61.5599 | -0.023943 | 0.048236 | 61.6074 | 0.007721 | 61.3901 | 61.9978 | 61.7439 | 62.0655 | 62.1944 | 62.2189 | 62.131 | 61.186 | 123.1613 | 61.74 | 123.065 | 61.4812 | 61.5534 | 123.1125 | 61.5128 | 122.8953 | 61.6079 | 61.6484 | 61.5117 | 61.5522
7492.0781 | 123.2574 | -61.4502 | 61.6928 | 0.053175 | -0.13668 | 0.15741 | 0.24969 | 0.2789 | 0.090161 | -0.78149 | 61.6882 | 0.23032 | 61.5874 | -0.019364 | 0.052814 | 61.5799 | 0.012299 | 61.3627 | 61.5034 | 61.3135 | 61.6076 | 61.6999 | 61.7291 | 61.5404 | 60.6687 | 123.1384 | 61.6805 | 123.0376 | 61.4308 | 61.503 | 123.0301 | 61.4625 | 122.8129 | 61.6354 | 61.6759 | 61.5346 | 61.5751
7493.0625 | 123.23 | -61.496 | 61.6379 | 0.34619 | 0.10142 | 0.42755 | 0.54272 | 0.58104 | 0.43354 | -0.4656 | 61.6745 | 0.2349 | 61.5874 | -0.023943 | 0.052814 | 61.6028 | 0.012299 | 61.381 | 61.8422 | 61.5974 | 61.9235 | 62.0387 | 62.077 | 61.9295 | 61.0304 | 123.1704 | 61.7309 | 123.0834 | 61.472 | 61.5488 | 123.0988 | 61.5083 | 122.8769 | 61.6216 | 61.6622 | 61.5346 | 61.5751
7494.0781 | 123.2574 | -61.5417 | 61.6425 | 0.13559 | -0.067994 | 0.24898 | 0.33668 | 0.37046 | 0.14968 | -0.70824 | 61.6882 | 0.23032 | 61.6149 | -0.023943 | 0.052814 | 61.5845 | 0.003143 | 61.3627 | 61.6773 | 61.4738 | 61.7907 | 61.8784 | 61.9122 | 61.6914 | 60.8335 | 123.2299 | 61.7721 | 123.1566 | 61.5178 | 61.5946 | 123.1262 | 61.5449 | 122.9044 | 61.6354 | 61.685 | 61.562 | 61.6117
7495.0625 | 123.3856 | -61.4685 | 61.615 | 0.3874 | 0.14721 | 0.47333 | 0.58392 | 0.61309 | 0.48848 | -0.41066 | 61.6607 | 0.22574 | 61.5599 | -0.028522 | 0.048236 | 61.6074 | 0.012299 | 61.3856 | 61.8559 | 61.6157 | 61.9418 | 62.0524 | 62.0816 | 61.957 | 61.0578 | 123.1292 | 61.6942 | 123.0284 | 61.44 | 61.5167 | 123.0759 | 61.4808 | 122.8541 | 61.6125 | 61.6484 | 61.5117 | 61.5476
7496.0938 | 123.2803 | -61.4914 | 61.6379 | 0.1539 | -0.058836 | 0.24898 | 0.35958 | 0.38419 | 0.19089 | -0.66246 | 61.6882 | 0.2349 | 61.5828 | -0.023943 | 0.052814 | 61.5845 | 0.007721 | 61.3718 | 61.6453 | 61.4326 | 61.7404 | 61.851 | 61.8756 | 61.6823 | 60.8289 | 123.1796 | 61.7263 | 123.0742 | 61.4675 | 61.5442 | 123.0759 | 61.4991 | 122.8632 | 61.6354 | 61.6805 | 61.53 | 61.5751
7497.0625 | 123.349 | -61.4822 | 61.5921 | 0.25462 | 0.041898 | 0.35887 | 0.46488 | 0.49864 | 0.28703 | -0.56632 | 61.6745 | 0.23948 | 61.6103 | -0.033101 | 0.043657 | 61.5936 | 0.016878 | 61.3764 | 61.7369 | 61.5241 | 61.8411 | 61.9471 | 61.9809 | 61.7693 | 60.9159 | 123.1567 | 61.7217 | 123.0925 | 61.4491 | 61.5259 | 123.0759 | 61.4991 | 122.8586 | 61.6308 | 61.6576 | 61.5666 | 61.5934
7498.0938 | 123.2849 | -61.4914 | 61.6013 | 0.46981 | 0.22505 | 0.56033 | 0.67549 | 0.70007 | 0.53426 | -0.34199 | 61.6653 | 0.23032 | 61.5645 | -0.023943 | 0.048236 | 61.6074 | 0.007721 | 61.381 | 61.9612 | 61.7164 | 62.0517 | 62.1669 | 62.1915 | 62.0257 | 61.1494 | 123.1567 | 61.7217 | 123.0559 | 61.4675 | 61.5396 | 123.0988 | 61.4991 | 122.8724 | 61.6171 | 61.6576 | 61.5163 | 61.5568
7499.0625 | 123.4131 | -61.4868 | 61.5417 | 0.58427 | 0.30289 | 0.67479 | 0.77622 | 0.8191 | 0.67162 | -0.25042 | 61.6561 | 0.22574 | 61.5508 | -0.023943 | 0.048236 | 61.6074 | 0.012299 | 61.3993 | 62.0711 | 61.7897 | 62.1616 | 62.263 | 62.3059 | 62.1584 | 61.2364 | 123.143 | 61.7126 | 123.0376 | 61.4629 | 61.5351 | 123.0942 | 61.4991 | 122.8861 | 61.6079 | 61.6438 | 61.5025 | 61.5385
7500.0938 | 123.3032 | -61.5005 | 61.647 | 0.37824 | 0.15637 | 0.47333 | 0.5885 | 0.61309 | 0.40149 | -0.43355 | 61.6699 | 0.2349 | 61.5965 | -0.028522 | 0.048236 | 61.6074 | 0.016878 | 61.381 | 61.8788 | 61.6569 | 61.9739 | 62.0891 | 62.1136 | 61.902 | 61.067 | 123.1704 | 61.7354 | 123.0971 | 61.472 | 61.5488 | 123.1079 | 61.5174 | 122.8815 | 61.6216 | 61.653 | 61.5483 | 61.5797
7501.0625 | 123.2941 | -61.5189 | 61.5784 | 0.24547 | 0.000689 | 0.32682 | 0.45115 | 0.46659 | 0.26872 | -0.58005 | 61.679 | 0.23032 | 61.5691 | -0.028522 | 0.048236 | 61.5936 | 0.016878 | 61.3718 | 61.7643 | 61.5195 | 61.8457 | 61.97 | 61.9855 | 61.7876 | 60.9388 | 123.1979 | 61.7492 | 123.0879 | 61.4903 | 61.5671 | 123.1125 | 61.5357 | 122.8907 | 61.6308 | 61.6622 | 61.5208 | 61.5522
7502.0938 | 123.2437 | -61.5143 | 61.6013 | 0.46523 | 0.22505 | 0.55575 | 0.66634 | 0.69549 | 0.49764 | -0.35114 | 61.6653 | 0.23032 | 61.5691 | -0.028522 | 0.048236 | 61.6074 | 0.003143 | 61.3856 | 61.9795 | 61.7393 | 62.07 | 62.1806 | 62.2098 | 62.0119 | 61.1631 | 123.1796 | 61.7446 | 123.0834 | 61.4858 | 61.5625 | 123.1216 | 61.5174 | 122.8998 | 61.6171 | 61.6622 | 61.5208 | 61.5659
7503.0625 | 123.3856 | -61.4502 | 61.5738 | 0.24089 | 0.014425 | 0.32682 | 0.43741 | 0.46202 | 0.28245 | -0.56174 | 61.6836 | 0.22574 | 61.5965 | -0.033101 | 0.039079 | 61.5982 | 0.003143 | 61.3764 | 61.6911 | 61.4646 | 61.777 | 61.8876 | 61.9122 | 61.7326 | 60.8885 | 123.1338 | 61.6759 | 123.0467 | 61.4171 | 61.4893 | 123.0484 | 61.4533 | 122.8266 | 61.6445 | 61.6805 | 61.5575 | 61.5934
7504.0625 | 123.3261 | -61.4731 | 61.5646 | 0.3874 | 0.15637 | 0.48249 | 0.60681 | 0.61767 | 0.43354 | -0.42897 | 61.6699 | 0.23032 | 61.5599 | -0.033101 | 0.048236 | 61.6074 | 0.012299 | 61.3764 | 61.8605 | 61.6295 | 61.9556 | 62.0799 | 62.0907 | 61.9066 | 61.0441 | 123.143 | 61.7034 | 123.033 | 61.44 | 61.5213 | 123.0804 | 61.4854 | 122.8495 | 61.6216 | 61.6576 | 61.5117 | 61.5476
7505.0938 | 123.3078 | -61.5005 | 61.615 | 0.53391 | 0.30289 | 0.63816 | 0.73501 | 0.76416 | 0.58463 | -0.28247 | 61.6653 | 0.24405 | 61.5874 | -0.023943 | 0.043657 | 61.6165 | 0.003143 | 61.3947 | 62.0345 | 61.8034 | 62.1387 | 62.2356 | 62.2647 | 62.0852 | 61.2181 | 123.1658 | 61.7446 | 123.0879 | 61.4766 | 61.5442 | 123.1171 | 61.5037 | 122.8953 | 61.6216 | 61.6622 | 61.5437 | 61.5842
7506.0625 | 123.3765 | -61.4502 | 61.5509 | 0.3233 | 0.11058 | 0.4367 | 0.53356 | 0.56273 | 0.30077 | -0.49764 | 61.6653 | 0.22574 | 61.5737 | -0.033101 | 0.043657 | 61.5936 | 0.012299 | 61.3764 | 61.7735 | 61.5608 | 61.8869 | 61.9838 | 62.0129 | 61.751 | 60.9526 | 123.1155 | 61.6759 | 123.0238 | 61.4171 | 61.4939 | 123.0438 | 61.4625 | 122.8266 | 61.6216 | 61.653 | 61.53 | 61.5614
7507.0938 | 123.3307 | -61.4639 | 61.6379 | 0.25462 | 0.051056 | 0.36802 | 0.47862 | 0.49406 | 0.22751 | -0.57547 | 61.6745 | 0.2349 | 61.592 | -0.023943 | 0.052814 | 61.5982 | 0.007721 | 61.3764 | 61.7186 | 61.515 | 61.832 | 61.9425 | 61.958 | 61.6914 | 60.8885 | 123.1384 | 61.6988 | 123.0559 | 61.44 | 61.5167 | 123.0621 | 61.4716 | 122.8403 | 61.6216 | 61.6667 | 61.5392 | 61.5842
7508.0625 | 123.381 | -61.441 | 61.6058 | -0.033814 | -0.22367 | 0.079572 | 0.1627 | 0.19649 | -0.060926 | -0.85474 | 61.6973 | 0.23032 | 61.5965 | -0.023943 | 0.043657 | 61.5753 | 0.012299 | 61.3581 | 61.4072 | 61.2174 | 61.5206 | 61.6037 | 61.6375 | 61.3801 | 60.5863 | 123.1384 | 61.6714 | 123.0376 | 61.4171 | 61.4847 | 123.0164 | 61.4533 | 122.7991 | 61.6537 | 61.685 | 61.5529 | 61.5842
7509.0938 | 123.2208 | -61.5143 | 61.6241 | -0.047549 | -0.23283 | 0.047522 | 0.13523 | 0.15987 | -0.060926 | -0.8639 | 61.6836 | 0.23032 | 61.592 | -0.033101 | 0.052814 | 61.5753 | 0.016878 | 61.3581 | 61.4667 | 61.2815 | 61.5618 | 61.6495 | 61.6742 | 61.4534 | 60.6504 | 123.1979 | 61.7446 | 123.1062 | 61.4812 | 61.5671 | 123.0896 | 61.5312 | 122.8724 | 61.6308 | 61.6667 | 61.5392 | 61.5751
7510.0625 | 123.3582 | -61.4731 | 61.6196 | 0.076067 | -0.13668 | 0.1803 | 0.26343 | 0.29263 | 0.062691 | -0.73571 | 61.7019 | 0.23948 | 61.6194 | -0.023943 | 0.048236 | 61.5845 | 0.012299 | 61.3672 | 61.5492 | 61.3364 | 61.6534 | 61.7365 | 61.7657 | 61.5358 | 60.7374 | 123.175 | 61.7126 | 123.0925 | 61.4491 | 61.5213 | 123.0576 | 61.4854 | 122.8403 | 61.6537 | 61.6896 | 61.5712 | 61.6071
7511.0625 | 123.3673 | -61.4639 | 61.5875 | 0.071489 | -0.11378 | 0.19404 | 0.26801 | 0.30179 | 0.035221 | -0.75402 | 61.6836 | 0.22574 | 61.592 | -0.028522 | 0.048236 | 61.5845 | 0.012299 | 61.3627 | 61.5354 | 61.3501 | 61.658 | 61.7319 | 61.7657 | 61.4991 | 60.7099 | 123.1475 | 61.6897 | 123.0559 | 61.4354 | 61.5122 | 123.0484 | 61.4762 | 122.8266 | 61.6354 | 61.6713 | 61.5437 | 61.5797
7512.0781 | 123.2986 | -61.4731 | 61.647 | -0.084176 | -0.26488 | 0.020051 | 0.10776 | 0.12325 | -0.11129 | -0.92341 | 61.6973 | 0.23032 | 61.6194 | -0.028522 | 0.039079 | 61.5662 | 0.007721 | 61.3581 | 61.3889 | 61.2082 | 61.4931 | 61.5808 | 61.5963 | 61.3618 | 60.5497 | 123.1704 | 61.7034 | 123.0925 | 61.4446 | 61.5122 | 123.0392 | 61.4808 | 122.8312 | 61.6583 | 61.6896 | 61.5804 | 61.6117
7513.0625 | 123.3444 | -61.4319 | 61.6196 | -0.27647 | -0.45719 | -0.17225 | -0.10285 | -0.06445 | -0.31732 | -1.1294 | 61.7157 | 0.22574 | 61.6194 | -0.028522 | 0.048236 | 61.5662 | 0.012299 | 61.3443 | 61.1554 | 60.9747 | 61.2596 | 61.329 | 61.3674 | 61.1146 | 60.3025 | 123.1475 | 61.6576 | 123.0513 | 61.4034 | 61.4801 | 122.998 | 61.4442 | 122.7762 | 61.6674 | 61.7034 | 61.5712 | 61.6071
7514.0781 | 123.2391 | -61.4914 | 61.6516 | -0.12996 | -0.31067 | -0.021157 | 0.039082 | 0.072888 | -0.17081 | -0.96462 | 61.6973 | 0.22574 | 61.5965 | -0.023943 | 0.043657 | 61.5707 | 0.007721 | 61.3443 | 61.3614 | 61.1807 | 61.4702 | 61.5305 | 61.5643 | 61.3206 | 60.5268 | 123.1887 | 61.7171 | 123.0879 | 61.4675 | 61.5351 | 123.0621 | 61.4991 | 122.8357 | 61.6537 | 61.6896 | 61.5529 | 61.5888
7515.0625 | 123.381 | -61.4319 | 61.6196 | 0.03944 | -0.14583 | 0.14825 | 0.22222 | 0.25601 | -0.005985 | -0.7586 | 61.6928 | 0.24405 | 61.6194 | -0.028522 | 0.052814 | 61.5799 | 0.012299 | 61.3581 | 61.4713 | 61.2861 | 61.5801 | 61.6541 | 61.6879 | 61.4259 | 60.6733 | 123.1247 | 61.6759 | 123.0513 | 61.4034 | 61.4847 | 123.0118 | 61.4442 | 122.79 | 61.64 | 61.6805 | 61.5666 | 61.6071
7516.0781 | 123.2712 | -61.5143 | 61.5875 | 0.15848 | -0.031363 | 0.25356 | 0.34126 | 0.37046 | 0.1039 | -0.6533 | 61.6836 | 0.23032 | 61.5828 | -0.028522 | 0.048236 | 61.5936 | 0.007721 | 61.3672 | 61.6728 | 61.4829 | 61.7678 | 61.8555 | 61.8847 | 61.6182 | 60.861 | 123.1979 | 61.7446 | 123.0971 | 61.4858 | 61.5625 | 123.1079 | 61.522 | 122.8815 | 61.6354 | 61.6759 | 61.5346 | 61.5751
7517.0625 | 123.381 | -61.4777 | 61.5738 | 0.18137 | -0.022205 | 0.28561 | 0.36873 | 0.38419 | 0.11305 | -0.63499 | 61.6836 | 0.23032 | 61.5965 | -0.023943 | 0.048236 | 61.5936 | 0.003143 | 61.3627 | 61.659 | 61.4555 | 61.7633 | 61.8464 | 61.8619 | 61.5907 | 60.8427 | 123.1613 | 61.708 | 123.0742 | 61.4537 | 61.5259 | 123.0713 | 61.4808 | 122.8403 | 61.6354 | 61.6805 | 61.5483 | 61.5934
7518.0781 | 123.2803 | -61.4731 | 61.6516 | -0.001765 | -0.17788 | 0.10704 | 0.16728 | 0.20565 | -0.074661 | -0.85016 | 61.6928 | 0.2349 | 61.592 | -0.019364 | 0.043657 | 61.5753 | 0.007721 | 61.3627 | 61.4713 | 61.2952 | 61.5801 | 61.6404 | 61.6787 | 61.3984 | 60.6229 | 123.1659 | 61.708 | 123.065 | 61.4537 | 61.5167 | 123.0484 | 61.4808 | 122.8357 | 61.6491 | 61.685 | 61.5483 | 61.5842
7519.0625 | 123.317 | -61.4639 | 61.6104 | 0.13101 | -0.0451 | 0.23525 | 0.30463 | 0.33841 | 0.081005 | -0.66246 | 61.6836 | 0.2349 | 61.5828 | -0.033101 | 0.048236 | 61.5891 | 0.012299 | 61.3581 | 61.5949 | 61.4188 | 61.6992 | 61.7686 | 61.8023 | 61.5449 | 60.8015 | 123.1475 | 61.6988 | 123.0467 | 61.4308 | 61.5122 | 123.053 | 61.4762 | 122.822 | 61.6354 | 61.6713 | 61.5346 | 61.5705
7520.1094 | 123.2758 | -61.4822 | 61.615 | 0.22258 | 0.037319 | 0.32224 | 0.40078 | 0.42539 | 0.15884 | -0.5709 | 61.6836 | 0.2349 | 61.6057 | -0.028522 | 0.052814 | 61.5936 | 0.016878 | 61.3627 | 61.7048 | 61.5196 | 61.8045 | 61.883 | 61.9076 | 61.6411 | 60.9113 | 123.1659 | 61.7171 | 123.0879 | 61.4537 | 61.5351 | 123.0759 | 61.4991 | 122.8449 | 61.6308 | 61.6667 | 61.5529 | 61.5888
7521.0625 | 123.3536 | -61.4548 | 61.6058 | -0.024657 | -0.18246 | 0.074994 | 0.13981 | 0.16903 | -0.060926 | -0.83643 | 61.6928 | 0.2349 | 61.5874 | -0.033101 | 0.048236 | 61.5799 | 0.012299 | 61.3535 | 61.4301 | 61.2723 | 61.5298 | 61.5946 | 61.6238 | 61.3938 | 60.6183 | 123.1475 | 61.6897 | 123.0422 | 61.4217 | 61.503 | 123.0347 | 61.4671 | 122.8083 | 61.6445 | 61.6805 | 61.5392 | 61.5751
7522.0938 | 123.2758 | -61.4822 | 61.5784 | 0.20884 | 0.005267 | 0.30392 | 0.37789 | 0.39792 | 0.13595 | -0.59379 | 61.679 | 0.23032 | 61.6149 | -0.033101 | 0.043657 | 61.5845 | 0.012299 | 61.3627 | 61.6911 | 61.4875 | 61.7862 | 61.8601 | 61.8802 | 61.6182 | 60.8885 | 123.1613 | 61.7126 | 123.0971 | 61.4491 | 61.5259 | 123.0667 | 61.4945 | 122.8449 | 61.6354 | 61.6667 | 61.5712 | 61.6026
7523.0625 | 123.3307 | -61.4365 | 61.6287 | 0.062332 | -0.1092 | 0.16199 | 0.23138 | 0.27432 | -0.005985 | -0.75402 | 61.6973 | 0.23032 | 61.5874 | -0.023943 | 0.048236 | 61.5845 | 0.012299 | 61.3535 | 61.4988 | 61.3273 | 61.5984 | 61.6678 | 61.7108 | 61.4305 | 60.6824 | 123.1338 | 61.6668 | 123.0239 | 61.4125 | 61.4847 | 123.0209 | 61.4488 | 122.79 | 61.6491 | 61.685 | 61.5392 | 61.5751
7524.0781 | 123.23 | -61.496 | 61.6196 | 0.06691 | -0.10462 | 0.16657 | 0.24054 | 0.27432 | 0.003172 | -0.73571 | 61.6973 | 0.2349 | 61.5965 | -0.028522 | 0.048236 | 61.5799 | 0.012299 | 61.3627 | 61.5629 | 61.3913 | 61.6625 | 61.7365 | 61.7703 | 61.4991 | 60.7603 | 123.1933 | 61.7309 | 123.0925 | 61.4674 | 61.5442 | 123.0759 | 61.5083 | 122.8586 | 61.6491 | 61.685 | 61.5483 | 61.5842
7525.0625 | 123.2849 | -61.4548 | 61.6837 | 0.002813 | -0.17331 | 0.097887 | 0.17186 | 0.20565 | -0.065504 | -0.81354 | 61.7019 | 0.23948 | 61.6149 | -0.019364 | 0.057392 | 61.5753 | 0.012299 | 61.3627 | 61.4576 | 61.2815 | 61.5527 | 61.6266 | 61.6604 | 61.3893 | 60.6412 | 123.1567 | 61.6942 | 123.0696 | 61.4354 | 61.5122 | 123.0301 | 61.4671 | 122.8174 | 61.6445 | 61.6896 | 61.5575 | 61.6026
7526.0938 | 123.2208 | -61.5097 | 61.6379 | 0.16764 | -0.026784 | 0.2673 | 0.35958 | 0.38877 | 0.1039 | -0.63957 | 61.679 | 0.23032 | 61.5828 | -0.028522 | 0.048236 | 61.5845 | 0.007721 | 61.3718 | 61.6773 | 61.4829 | 61.777 | 61.8693 | 61.8985 | 61.6136 | 60.8701 | 123.1887 | 61.74 | 123.0925 | 61.4812 | 61.5579 | 123.0942 | 61.5174 | 122.8815 | 61.6308 | 61.6713 | 61.5346 | 61.5751
7527.0625 | 123.2483 | -61.4639 | 61.6699 | 0.11269 | -0.067994 | 0.21235 | 0.30463 | 0.31552 | 0.039799 | -0.69451 | 61.6928 | 0.23948 | 61.6286 | -0.019364 | 0.057392 | 61.5891 | 0.012299 | 61.3672 | 61.5766 | 61.3959 | 61.6763 | 61.7686 | 61.7794 | 61.5037 | 60.7694 | 123.1567 | 61.7034 | 123.0925 | 61.4446 | 61.5213 | 123.053 | 61.4762 | 122.8312 | 61.6354 | 61.6805 | 61.5712 | 61.6163
7528.0781 | 123.2346 | -61.4914 | 61.6653 | -0.061284 | -0.23283 | 0.042944 | 0.10776 | 0.13698 | -0.1296 | -0.88679 | 61.6928 | 0.23032 | 61.6011 | -0.028522 | 0.043657 | 61.5753 | 0.012299 | 61.3581 | 61.4301 | 61.2586 | 61.5343 | 61.5992 | 61.6284 | 61.3618 | 60.6046 | 123.1842 | 61.7217 | 123.0925 | 61.4629 | 61.5351 | 123.0667 | 61.5037 | 122.8495 | 61.6491 | 61.6805 | 61.5575 | 61.5888
7529.0625 | 123.349 | -61.4548 | 61.6104 | 0.36908 | 0.16553 | 0.46418 | 0.56561 | 0.58104 | 0.30077 | -0.43355 | 61.6699 | 0.23032 | 61.5737 | -0.028522 | 0.052814 | 61.6028 | 0.012299 | 61.381 | 61.8239 | 61.6203 | 61.9189 | 62.0204 | 62.0358 | 61.7555 | 61.0212 | 123.1246 | 61.6851 | 123.0284 | 61.4263 | 61.5076 | 123.0576 | 61.4671 | 122.8357 | 61.6171 | 61.6576 | 61.5208 | 61.5614
7530.0938 | 123.262 | -61.5051 | 61.6425 | 0.25462 | 0.064792 | 0.36802 | 0.45115 | 0.47575 | 0.18173 | -0.56174 | 61.679 | 0.2349 | 61.6011 | -0.019364 | 0.048236 | 61.5891 | 0.007721 | 61.3764 | 61.7598 | 61.5699 | 61.8732 | 61.9563 | 61.9809 | 61.6869 | 60.9434 | 123.1842 | 61.74 | 123.1063 | 61.4858 | 61.5534 | 123.0942 | 61.5128 | 122.8815 | 61.6308 | 61.6713 | 61.5529 | 61.5934
7531.0625 | 123.3582 | -61.4731 | 61.5875 | 0.40113 | 0.18842 | 0.48707 | 0.59766 | 0.62682 | 0.33282 | -0.41981 | 61.6699 | 0.23032 | 61.5645 | -0.028522 | 0.052814 | 61.5982 | 0.003143 | 61.3764 | 61.8742 | 61.6615 | 61.9602 | 62.0707 | 62.0999 | 61.8059 | 61.0533 | 123.143 | 61.7034 | 123.0376 | 61.4446 | 61.5259 | 123.0713 | 61.4762 | 122.8495 | 61.6171 | 61.6667 | 61.5117 | 61.5614
7532.0938 | 123.349 | -61.5051 | 61.5784 | 0.33703 | 0.14263 | 0.44586 | 0.53356 | 0.56273 | 0.24583 | -0.48391 | 61.6745 | 0.23948 | 61.6057 | -0.023943 | 0.048236 | 61.5982 | 0.007721 | 61.381 | 61.8422 | 61.6478 | 61.951 | 62.0387 | 62.0679 | 61.751 | 61.0212 | 123.1796 | 61.7446 | 123.1108 | 61.4812 | 61.5534 | 123.1033 | 61.5128 | 122.8861 | 61.6262 | 61.6667 | 61.5575 | 61.598
7533.0625 | 123.3536 | -61.4594 | 61.5875 | 0.28209 | 0.083107 | 0.3955 | 0.48778 | 0.50779 | 0.20004 | -0.548 | 61.6653 | 0.2349 | 61.5737 | -0.028522 | 0.048236 | 61.5936 | 0.016878 | 61.3764 | 61.7414 | 61.5425 | 61.8548 | 61.9471 | 61.9671 | 61.6594 | 60.9113 | 123.1246 | 61.6942 | 123.033 | 61.4308 | 61.5076 | 123.053 | 61.4762 | 122.8357 | 61.6171 | 61.6484 | 61.5254 | 61.5568
7534.0781 | 123.2986 | -61.4777 | 61.6425 | 0.048597 | -0.11836 | 0.15741 | 0.24511 | 0.26059 | -0.04719 | -0.76776 | 61.6973 | 0.2349 | 61.5965 | -0.028522 | 0.048236 | 61.5753 | 0.012299 | 61.3672 | 61.5263 | 61.3593 | 61.6351 | 61.7228 | 61.7382 | 61.4305 | 60.7099 | 123.175 | 61.7126 | 123.0742 | 61.4491 | 61.5259 | 123.053 | 61.49 | 122.8449 | 61.6491 | 61.685 | 61.5483 | 61.5842
7535.0625 | 123.317 | -61.4594 | 61.5921 | 0.25005 | 0.046477 | 0.34513 | 0.42368 | 0.45744 | 0.21378 | -0.55258 | 61.679 | 0.24405 | 61.6011 | -0.028522 | 0.057392 | 61.6028 | 0.007721 | 61.3764 | 61.7094 | 61.5058 | 61.8045 | 61.883 | 61.9168 | 61.6731 | 60.9068 | 123.1384 | 61.7034 | 123.0605 | 61.4308 | 61.5167 | 123.0621 | 61.4671 | 122.8357 | 61.6216 | 61.6713 | 61.5437 | 61.5934
7536.0781 | 123.23 | -61.4868 | 61.6425 | 0.025705 | -0.15041 | 0.1162 | 0.20391 | 0.22854 | -0.04719 | -0.79065 | 61.6836 | 0.22574 | 61.5874 | -0.023943 | 0.052814 | 61.5707 | 0.007721 | 61.3581 | 61.5125 | 61.3364 | 61.603 | 61.6907 | 61.7154 | 61.4396 | 60.6962 | 123.1704 | 61.7126 | 123.0742 | 61.4629 | 61.5396 | 123.0576 | 61.4945 | 122.8449 | 61.6308 | 61.6759 | 61.5346 | 61.5797
7537.0625 | 123.3765 | -61.4319 | 61.615 | 0.28667 | 0.07395 | 0.37718 | 0.47404 | 0.50779 | 0.22293 | -0.52511 | 61.6745 | 0.2349 | 61.6057 | -0.023943 | 0.048236 | 61.5936 | 0.012299 | 61.3764 | 61.7186 | 61.5058 | 61.8091 | 61.9059 | 61.9397 | 61.6548 | 60.9068 | 123.1063 | 61.6668 | 123.0376 | 61.4079 | 61.4801 | 123.0255 | 61.4442 | 122.8083 | 61.6262 | 61.6622 | 61.5575 | 61.5934
7538.0938 | 123.23 | -61.5326 | 61.6104 | 0.43776 | 0.24337 | 0.54201 | 0.63429 | 0.65429 | 0.37402 | -0.36945 | 61.6653 | 0.22574 | 61.5645 | -0.023943 | 0.052814 | 61.6074 | 0.012299 | 61.3856 | 61.9704 | 61.776 | 62.0746 | 62.1669 | 62.1869 | 61.9066 | 61.1631 | 123.1979 | 61.7583 | 123.0971 | 61.5086 | 61.5854 | 123.14 | 61.5449 | 122.9181 | 61.6125 | 61.653 | 61.5117 | 61.5522
7539.0625 | 123.3307 | -61.4594 | 61.5829 | 0.19511 | 0.005267 | 0.29935 | 0.38247 | 0.41166 | 0.076426 | -0.62583 | 61.6836 | 0.23032 | 61.5874 | -0.028522 | 0.043657 | 61.5982 | 0.012299 | 61.3718 | 61.6545 | 61.4646 | 61.7587 | 61.8418 | 61.871 | 61.5358 | 60.8335 | 123.143 | 61.6897 | 123.0467 | 61.4308 | 61.503 | 123.0576 | 61.4716 | 122.8312 | 61.64 | 61.6713 | 61.5437 | 61.5751
7540.0938 | 123.2758 | -61.4639 | 61.6562 | 0.030283 | -0.14125 | 0.13909 | 0.22222 | 0.25143 | -0.079239 | -0.7998 | 61.6928 | 0.23948 | 61.6194 | -0.023943 | 0.043657 | 61.5707 | 0.012299 | 61.3581 | 61.4942 | 61.3227 | 61.603 | 61.6862 | 61.7154 | 61.3847 | 60.6641 | 123.1567 | 61.7034 | 123.0834 | 61.44 | 61.5076 | 123.0347 | 61.4762 | 122.822 | 61.6491 | 61.6805 | 61.5758 | 61.6071
7541.0625 | 123.3582 | -61.4685 | 61.6058 | 0.20426 | 0.023583 | 0.3085 | 0.39163 | 0.41624 | 0.11305 | -0.60294 | 61.679 | 0.22574 | 61.5691 | -0.03768 | 0.043657 | 61.5936 | 0.003143 | 61.3672 | 61.6728 | 61.4921 | 61.777 | 61.8601 | 61.8847 | 61.5816 | 60.8656 | 123.1475 | 61.6942 | 123.0376 | 61.4308 | 61.5122 | 123.0621 | 61.4716 | 122.8357 | 61.6354 | 61.6759 | 61.5254 | 61.5659
7542.0781 | 123.2208 | -61.4822 | 61.6379 | -0.001765 | -0.20078 | 0.097887 | 0.19475 | 0.23312 | -0.065504 | -0.82727 | 61.7065 | 0.23948 | 61.624 | -0.019364 | 0.052814 | 61.5753 | 0.007721 | 61.3581 | 61.4805 | 61.2815 | 61.5801 | 61.677 | 61.7154 | 61.4167 | 60.655 | 123.1887 | 61.7217 | 123.1063 | 61.4629 | 61.5351 | 123.0576 | 61.49 | 122.8403 | 61.6537 | 61.6988 | 61.5712 | 61.6163
7543.0625 | 123.3353 | -61.4548 | 61.5829 | 0.053175 | -0.1321 | 0.15283 | 0.25427 | 0.28347 | -0.033455 | -0.76318 | 61.6882 | 0.23032 | 61.5828 | -0.028522 | 0.043657 | 61.5845 | 0.012299 | 61.3489 | 61.5079 | 61.3227 | 61.6076 | 61.709 | 61.7382 | 61.4213 | 60.6916 | 123.143 | 61.6851 | 123.0376 | 61.4263 | 61.4984 | 123.0392 | 61.4671 | 122.8037 | 61.6445 | 61.6759 | 61.5392 | 61.5705
7544.0781 | 123.262 | -61.4639 | 61.6287 | 0.062332 | -0.12294 | 0.17114 | 0.27259 | 0.30179 | -0.033455 | -0.77691 | 61.6973 | 0.23032 | 61.6011 | -0.028522 | 0.052814 | 61.5891 | 0.016878 | 61.3627 | 61.5263 | 61.341 | 61.6351 | 61.7365 | 61.7657 | 61.4305 | 60.687 | 123.1613 | 61.6942 | 123.0651 | 61.4354 | 61.5167 | 123.053 | 61.4808 | 122.8266 | 61.6445 | 61.6805 | 61.5483 | 61.5842
7545.0625 | 123.2803 | -61.4548 | 61.6837 | 0.007391 | -0.15957 | 0.12078 | 0.22222 | 0.24227 | -0.079239 | -0.80896 | 61.6973 | 0.2349 | 61.6103 | -0.028522 | 0.048236 | 61.5799 | 0.007721 | 61.3535 | 61.4622 | 61.2952 | 61.5756 | 61.677 | 61.697 | 61.3755 | 60.6458 | 123.1521 | 61.6897 | 123.0651 | 61.4263 | 61.503 | 123.0347 | 61.4625 | 122.8083 | 61.6491 | 61.6896 | 61.562 | 61.6026
7546.0938 | 123.3353 | -61.4685 | 61.6196 | 0.034862 | -0.14583 | 0.14367 | 0.23138 | 0.26059 | -0.065504 | -0.79065 | 61.6882 | 0.2349 | 61.5828 | -0.019364 | 0.048236 | 61.5891 | 0.012299 | 61.3535 | 61.5034 | 61.3227 | 61.6122 | 61.6999 | 61.7291 | 61.403 | 60.6779 | 123.1567 | 61.7034 | 123.0513 | 61.4491 | 61.5167 | 123.0576 | 61.4808 | 122.822 | 61.64 | 61.6759 | 61.5346 | 61.5705
7547.0625 | 123.3078 | -61.4685 | 61.5921 | 0.11727 | -0.067994 | 0.23067 | 0.32753 | 0.35214 | -0.001406 | -0.73113 | 61.6928 | 0.23948 | 61.6103 | -0.028522 | 0.057392 | 61.5891 | 0.003143 | 61.3672 | 61.5858 | 61.4005 | 61.6992 | 61.796 | 61.8207 | 61.4671 | 60.7374 | 123.1613 | 61.708 | 123.0788 | 61.44 | 61.5259 | 123.0576 | 61.4716 | 122.8357 | 61.6354 | 61.6896 | 61.5529 | 61.6071
7548.7812 | 123.3353 | -61.4594 | 61.6287 | 0.22715 | 0.037319 | 0.3314 | 0.43283 | 0.46202 | 0.16342 | -0.58921 | 61.679 | 0.23948 | 61.6057 | -0.023943 | 0.043657 | 61.5936 | 0.012299 | 61.3718 | 61.6865 | 61.4967 | 61.7907 | 61.8922 | 61.9214 | 61.6228 | 60.8701 | 123.1384 | 61.6988 | 123.0651 | 61.4354 | 61.503 | 123.053 | 61.4716 | 122.8312 | 61.6354 | 61.6667 | 61.562 | 61.5934
7549.4219 | 123.2483 | -61.4777 | 61.6241 | -0.061284 | -0.24199 | 0.042944 | 0.13981 | 0.16445 | -0.13418 | -0.89137 | 61.6882 | 0.22574 | 61.592 | -0.023943 | 0.043657 | 61.5753 | 0.007721 | 61.3489 | 61.4164 | 61.2357 | 61.5206 | 61.6175 | 61.6421 | 61.3435 | 60.5863 | 123.1659 | 61.7034 | 123.0696 | 61.4537 | 61.5213 | 123.053 | 61.4854 | 122.8266 | 61.6445 | 61.6805 | 61.5483 | 61.5842
7550.7344 | 123.2941 | -61.4868 | 61.6653 | 0.048597 | -0.1321 | 0.16199 | 0.25427 | 0.27432 | -0.038034 | -0.77691 | 61.6882 | 0.2349 | 61.6011 | -0.023943 | 0.052814 | 61.5845 | 0.016878 | 61.3581 | 61.5354 | 61.3547 | 61.6488 | 61.7411 | 61.7611 | 61.4488 | 60.7099 | 123.175 | 61.7217 | 123.0879 | 61.4629 | 61.5396 | 123.0713 | 61.5037 | 122.8449 | 61.6354 | 61.6713 | 61.5483 | 61.5842
7551.1875 | 123.3398 | -61.4594 | 61.615 | 0.19053 | -0.00389 | 0.29935 | 0.39163 | 0.42081 | 0.09474 | -0.61668 | 61.6745 | 0.22574 | 61.5737 | -0.028522 | 0.052814 | 61.5936 | 0.012299 | 61.3672 | 61.6499 | 61.4555 | 61.7587 | 61.851 | 61.8802 | 61.5541 | 60.8427 | 123.1338 | 61.6851 | 123.033 | 61.4308 | 61.5122 | 123.053 | 61.4716 | 122.8266 | 61.6216 | 61.6622 | 61.5208 | 61.5614
7553.25 | 123.2758 | -61.4456 | 61.6791 | 0.089802 | -0.090888 | 0.20319 | 0.2909 | 0.31094 | 0.00775 | -0.73571 | 61.6928 | 0.23032 | 61.5874 | -0.023943 | 0.06197 | 61.5845 | 0.007721 | 61.3672 | 61.5354 | 61.3547 | 61.6488 | 61.7365 | 61.7566 | 61.4534 | 60.7099 | 123.1384 | 61.6759 | 123.033 | 61.4217 | 61.5076 | 123.0301 | 61.4533 | 122.8129 | 61.6308 | 61.685 | 61.5254 | 61.5797
7554.1406 | 123.2803 | -61.5005 | 61.6699 | 0.25462 | 0.041898 | 0.34055 | 0.46488 | 0.48033 | 0.18173 | -0.5709 | 61.6836 | 0.2349 | 61.5874 | -0.023943 | 0.052814 | 61.5936 | 0.007721 | 61.3764 | 61.7552 | 61.5424 | 61.8411 | 61.9654 | 61.9809 | 61.6823 | 60.9297 | 123.1842 | 61.7354 | 123.0879 | 61.4766 | 61.5534 | 123.0942 | 61.5083 | 122.8769 | 61.6308 | 61.6759 | 61.5346 | 61.5797
7554.7031 | 123.3948 | -61.4594 | 61.6379 | 0.14017 | -0.049678 | 0.23067 | 0.32295 | 0.34757 | 0.081005 | -0.67619 | 61.679 | 0.22574 | 61.5782 | -0.028522 | 0.052814 | 61.5936 | 0.016878 | 61.3672 | 61.5995 | 61.4097 | 61.69 | 61.7823 | 61.8069 | 61.5404 | 60.7832 | 123.1384 | 61.6851 | 123.0376 | 61.4308 | 61.5122 | 123.053 | 61.4762 | 122.8266 | 61.6262 | 61.6622 | 61.5254 | 61.5614
7555.4688 | 123.3765 | -61.4731 | 61.6013 | 0.27752 | 0.07395 | 0.36802 | 0.47404 | 0.49406 | 0.23209 | -0.52969 | 61.679 | 0.2349 | 61.6103 | -0.019364 | 0.048236 | 61.5891 | 0.012299 | 61.3718 | 61.7506 | 61.547 | 61.8411 | 61.9471 | 61.9671 | 61.7052 | 60.9434 | 123.1521 | 61.708 | 123.0834 | 61.4537 | 61.5213 | 123.0621 | 61.4854 | 122.8449 | 61.6308 | 61.6667 | 61.562 | 61.598
7559.6719 | 123.349 | -61.4365 | 61.5921 | -0.070441 | -0.26488 | 0.033786 | 0.11234 | 0.14614 | -0.12502 | -0.91426 | 61.6928 | 0.22116 | 61.5874 | -0.028522 | 0.048236 | 61.5707 | 0.007721 | 61.3535 | 61.366 | 61.1716 | 61.4702 | 61.5488 | 61.5826 | 61.3114 | 60.5222 | 123.1292 | 61.6576 | 123.0239 | 61.4079 | 61.4847 | 123.0072 | 61.4442 | 122.79 | 61.6445 | 61.685 | 61.5392 | 61.5797
7560.2031 | 123.4177 | -61.409 | 61.6196 | -0.065863 | -0.2603 | 0.042944 | 0.11234 | 0.14156 | -0.13876 | -0.9051 | 61.6928 | 0.23032 | 61.6057 | -0.03768 | 0.052814 | 61.5707 | 0.012299 | 61.3535 | 61.3431 | 61.1487 | 61.4519 | 61.5213 | 61.5506 | 61.2702 | 60.5039 | 123.1018 | 61.6393 | 123.0147 | 61.3713 | 61.4618 | 122.9797 | 61.4213 | 122.7625 | 61.64 | 61.6805 | 61.5529 | 61.5934
7561.0625 | 123.3353 | -61.4731 | 61.6287 | 0.025705 | -0.14583 | 0.13452 | 0.20849 | 0.23769 | -0.060926 | -0.78607 | 61.6973 | 0.23032 | 61.6057 | -0.028522 | 0.052814 | 61.5845 | 0.012299 | 61.3672 | 61.4988 | 61.3272 | 61.6076 | 61.6816 | 61.7108 | 61.4122 | 60.687 | 123.1704 | 61.7034 | 123.0788 | 61.4446 | 61.5259 | 123.0576 | 61.4854 | 122.8403 | 61.6445 | 61.685 | 61.5529 | 61.5934
7562.0625 | 123.2758 | -61.4731 | 61.6516 | 0.021127 | -0.15499 | 0.12536 | 0.23596 | 0.25601 | -0.038034 | -0.76776 | 61.6928 | 0.2349 | 61.5874 | -0.019364 | 0.052814 | 61.5891 | 0.012299 | 61.3581 | 61.4942 | 61.3181 | 61.5984 | 61.709 | 61.7291 | 61.435 | 60.7053 | 123.1659 | 61.708 | 123.0605 | 61.4537 | 61.5259 | 123.0621 | 61.4854 | 122.8312 | 61.64 | 61.6805 | 61.5346 | 61.5751
7563.1094 | 123.2803 | -61.4777 | 61.6241 | 0.025705 | -0.1092 | 0.14825 | 0.24969 | 0.2789 | -0.015142 | -0.73571 | 61.6882 | 0.2349 | 61.6103 | -0.023943 | 0.043657 | 61.5799 | 0.007721 | 61.3627 | 61.5034 | 61.3685 | 61.6259 | 61.7274 | 61.7566 | 61.4625 | 60.742 | 123.1659 | 61.7126 | 123.0879 | 61.4537 | 61.5213 | 123.0576 | 61.4854 | 122.8403 | 61.6445 | 61.6805 | 61.5666 | 61.6026
7564.0625 | 123.3948 | -61.4456 | 61.6333 | -0.001765 | -0.095467 | 0.14825 | 0.23596 | 0.26974 | -0.028877 | -0.74029 | 61.6882 | 0.22574 | 61.5874 | -0.023943 | 0.048236 | 61.5799 | 0.007721 | 61.3718 | 61.4439 | 61.3502 | 61.5939 | 61.6816 | 61.7154 | 61.4167 | 60.7053 | 123.1338 | 61.6714 | 123.033 | 61.4217 | 61.4939 | 123.0255 | 61.4533 | 122.8174 | 61.64 | 61.6805 | 61.5392 | 61.5797
7565.0625 | 123.3353 | -61.4502 | 61.6013 | 0.057754 | -0.049678 | 0.21693 | 0.30921 | 0.32925 | 0.016907 | -0.68077 | 61.6836 | 0.2349 | 61.6057 | -0.023943 | 0.048236 | 61.5845 | 0.016878 | 61.3627 | 61.5079 | 61.4005 | 61.6671 | 61.7594 | 61.7794 | 61.4671 | 60.7694 | 123.1338 | 61.6851 | 123.0559 | 61.4263 | 61.4984 | 123.0347 | 61.4671 | 122.8129 | 61.6354 | 61.6667 | 61.5575 | 61.5888
7566.0938 | 123.3215 | -61.5097 | 61.6196 | 0.19511 | -0.017627 | 0.29477 | 0.38705 | 0.41624 | 0.099318 | -0.59836 | 61.6836 | 0.22574 | 61.5737 | -0.019364 | 0.043657 | 61.5936 | 0.012299 | 61.3672 | 61.7048 | 61.4921 | 61.8045 | 61.8968 | 61.9259 | 61.609 | 60.9113 | 123.1933 | 61.7354 | 123.0834 | 61.4903 | 61.5534 | 123.1033 | 61.522 | 122.8769 | 61.64 | 61.6713 | 61.53 | 61.5614
7567.0625 | 123.3582 | -61.4639 | 61.5921 | 0.18595 | -0.008469 | 0.2673 | 0.36873 | 0.38877 | 0.09474 | -0.60294 | 61.6882 | 0.2349 | 61.6103 | -0.028522 | 0.048236 | 61.5891 | 0.007721 | 61.3672 | 61.6499 | 61.4555 | 61.7312 | 61.8327 | 61.8527 | 61.5587 | 60.861 | 123.1521 | 61.6988 | 123.0742 | 61.4354 | 61.5122 | 123.053 | 61.4716 | 122.8312 | 61.64 | 61.6805 | 61.562 | 61.6026
7568.0938 | 123.1934 | -61.4868 | 61.6516 | 0.062332 | -0.040521 | 0.21693 | 0.30921 | 0.33383 | 0.021485 | -0.68077 | 61.6836 | 0.2349 | 61.5874 | -0.028522 | 0.043657 | 61.5845 | 0.012299 | 61.3627 | 61.5491 | 61.4463 | 61.7037 | 61.796 | 61.8206 | 61.5083 | 60.806 | 123.1704 | 61.7217 | 123.0742 | 61.4583 | 61.5305 | 123.0713 | 61.4991 | 122.8495 | 61.64 | 61.6713 | 61.5437 | 61.5751
7569.0625 | 123.3627 | -61.4319 | 61.6058 | 0.20884 | 0.087686 | 0.36802 | 0.45572 | 0.48033 | 0.14968 | -0.548 | 61.679 | 0.2349 | 61.6103 | -0.023943 | 0.048236 | 61.5936 | 0.012299 | 61.3718 | 61.6407 | 61.5196 | 61.7999 | 61.8876 | 61.9122 | 61.5816 | 60.8839 | 123.1109 | 61.6668 | 123.0422 | 61.4079 | 61.4801 | 123.0255 | 61.4442 | 122.8037 | 61.6308 | 61.6667 | 61.562 | 61.598
7570.0938 | 123.3582 | -61.4273 | 61.6104 | 0.016548 | -0.086309 | 0.17114 | 0.26801 | 0.28805 | -0.005985 | -0.72655 | 61.6836 | 0.22574 | 61.5828 | -0.023943 | 0.052814 | 61.5845 | 0.003143 | 61.3627 | 61.4439 | 61.341 | 61.5985 | 61.6953 | 61.7154 | 61.4213 | 60.7008 | 123.1109 | 61.653 | 123.0101 | 61.4034 | 61.4801 | 123.0118 | 61.4305 | 122.79 | 61.6308 | 61.6805 | 61.53 | 61.5797
7571.0625 | 123.3307 | -61.4365 | 61.6287 | 0.016548 | -0.16873 | 0.10704 | 0.20391 | 0.22854 | -0.051769 | -0.7998 | 61.6928 | 0.23948 | 61.624 | -0.028522 | 0.043657 | 61.5845 | 0.007721 | 61.3535 | 61.453 | 61.2677 | 61.5435 | 61.6404 | 61.665 | 61.3847 | 60.6367 | 123.1292 | 61.6759 | 123.0605 | 61.4079 | 61.4801 | 123.0209 | 61.4442 | 122.79 | 61.6491 | 61.685 | 61.5804 | 61.6163
7572.0781 | 123.3261 | -61.4822 | 61.6013 | 0.28209 | 0.078529 | 0.3726 | 0.47404 | 0.50322 | 0.23209 | -0.5068 | 61.6653 | 0.2349 | 61.5737 | -0.023943 | 0.048236 | 61.5982 | 0.007721 | 61.3718 | 61.7643 | 61.5608 | 61.8548 | 61.9563 | 61.9855 | 61.7143 | 60.9754 | 123.1475 | 61.7171 | 123.0559 | 61.4583 | 61.5305 | 123.0804 | 61.49 | 122.8541 | 61.6171 | 61.6576 | 61.5254 | 61.5659
7573.0625 | 123.3398 | -61.4777 | 61.6058 | -0.047549 | -0.23283 | 0.042944 | 0.1215 | 0.14156 | -0.13418 | -0.88221 | 61.7157 | 0.2349 | 61.6332 | -0.019364 | 0.048236 | 61.5753 | 0.016878 | 61.3489 | 61.4301 | 61.2448 | 61.5206 | 61.5992 | 61.6192 | 61.3435 | 60.5955 | 123.1933 | 61.7126 | 123.1108 | 61.4583 | 61.5259 | 123.053 | 61.4945 | 122.8266 | 61.6674 | 61.6988 | 61.5849 | 61.6163
7574.0625 | 123.2758 | -61.4822 | 61.6333 | -0.061284 | -0.24199 | 0.029208 | 0.1215 | 0.14156 | -0.13418 | -0.85932 | 61.6882 | 0.22574 | 61.592 | -0.019364 | 0.043657 | 61.5799 | 0.016878 | 61.3535 | 61.421 | 61.2403 | 61.5114 | 61.6037 | 61.6238 | 61.3481 | 60.6229 | 123.1704 | 61.708 | 123.0742 | 61.4629 | 61.5259 | 123.0621 | 61.4991 | 122.8357 | 61.6445 | 61.6713 | 61.5483 | 61.5751
7575.0625 | 123.3398 | -61.4136 | 61.6608 | -0.07502 | -0.25572 | 0.006315 | 0.094024 | 0.12325 | -0.15707 | -0.90052 | 61.7019 | 0.23032 | 61.6194 | -0.019364 | 0.048236 | 61.5753 | 0.016878 | 61.3535 | 61.3386 | 61.1578 | 61.4199 | 61.5076 | 61.5368 | 61.2565 | 60.5131 | 123.1155 | 61.6439 | 123.033 | 61.3942 | 61.4618 | 122.9889 | 61.4305 | 122.7671 | 61.6537 | 61.685 | 61.5712 | 61.6026
7576.0781 | 123.2758 | -61.4777 | 61.6425 | -0.006344 | -0.1962 | 0.070415 | 0.17186 | 0.19649 | -0.10671 | -0.82727 | 61.6928 | 0.23032 | 61.592 | -0.028522 | 0.043657 | 61.5753 | 0.007721 | 61.3489 | 61.4713 | 61.2815 | 61.5481 | 61.6495 | 61.6742 | 61.371 | 60.6504 | 123.1704 | 61.708 | 123.0696 | 61.4491 | 61.5213 | 123.053 | 61.4854 | 122.8266 | 61.6491 | 61.685 | 61.5483 | 61.5842
7577.0781 | 123.3719 | -61.4365 | 61.6241 | -0.15285 | -0.3473 | -0.066943 | 0.007033 | 0.036265 | -0.25322 | -0.99667 | 61.7065 | 0.2349 | 61.624 | -0.023943 | 0.043657 | 61.5616 | 0.012299 | 61.3443 | 61.2836 | 61.0892 | 61.3695 | 61.4435 | 61.4727 | 61.1832 | 60.4398 | 123.143 | 61.6714 | 123.0605 | 61.4125 | 61.4801 | 122.998 | 61.4488 | 122.7808 | 61.6628 | 61.6942 | 61.5804 | 61.6117
7578.0938 | 123.3398 | -61.4365 | 61.6104 | -0.27647 | -0.38393 | -0.27298 | -0.14864 | -0.11481 | -0.39057 | -1.0882 | 61.7019 | 0.23032 | 61.6103 | -0.028522 | 0.048236 | 61.5616 | 0.012299 | 61.3352 | 61.16 | 61.0525 | 61.1635 | 61.2878 | 61.3217 | 61.0459 | 60.3482 | 123.1384 | 61.6668 | 123.0467 | 61.4079 | 61.4847 | 122.998 | 61.4488 | 122.7717 | 61.6537 | 61.6896 | 61.562 | 61.598
7579.0781 | 123.3032 | -61.4685 | 61.6058 | 0.071489 | -0.049678 | 0.061258 | 0.2268 | 0.25601 | -0.01972 | -0.73571 | 61.6882 | 0.2349 | 61.6103 | -0.023943 | 0.043657 | 61.5845 | 0.003143 | 61.3535 | 61.54 | 61.4188 | 61.5298 | 61.6953 | 61.7245 | 61.4488 | 60.7328 | 123.1567 | 61.7034 | 123.0788 | 61.4446 | 61.5122 | 123.053 | 61.4716 | 122.822 | 61.6445 | 61.685 | 61.5666 | 61.6071
7580.0781 | 123.1842 | -61.5051 | 61.5463 | 0.030283 | -0.11836 | -0.021157 | 0.13065 | 0.16903 | -0.10213 | -0.80438 | 61.6928 | 0.23032 | 61.5965 | -0.028522 | 0.043657 | 61.5753 | 0.012299 | 61.3581 | 61.5354 | 61.3868 | 61.484 | 61.6358 | 61.6742 | 61.403 | 60.7007 | 123.1979 | 61.7354 | 123.1017 | 61.4766 | 61.5488 | 123.0804 | 61.5174 | 122.8632 | 61.6491 | 61.6805 | 61.5529 | 61.5842
7581.0625 | 123.3444 | -61.4731 | 61.6379 | -0.13912 | -0.31983 | -0.19057 | -0.038752 | -0.014093 | -0.299 | -1.0287 | 61.7065 | 0.23032 | 61.6194 | -0.028522 | 0.043657 | 61.5616 | 0.007721 | 61.3489 | 61.334 | 61.1533 | 61.2825 | 61.4343 | 61.459 | 61.1741 | 60.4444 | 123.1796 | 61.7034 | 123.0925 | 61.4446 | 61.5167 | 123.0347 | 61.4808 | 122.822 | 61.6628 | 61.6988 | 61.5758 | 61.6117
7582.1094 | 123.3307 | -61.4639 | 61.5692 | -0.061284 | -0.35646 | -0.10815 | 0.020768 | 0.049999 | -0.24406 | -0.98293 | 61.7065 | 0.23032 | 61.5965 | -0.028522 | 0.052814 | 61.5707 | 0.016878 | 61.3535 | 61.4026 | 61.1075 | 61.3558 | 61.4847 | 61.5139 | 61.2199 | 60.481 | 123.1704 | 61.6942 | 123.0605 | 61.4354 | 61.5167 | 123.0347 | 61.4808 | 122.8174 | 61.6537 | 61.6896 | 61.5437 | 61.5797
7583.0625 | 123.3353 | -61.4456 | 61.5967 | -0.16201 | -0.29693 | -0.19972 | -0.057066 | -0.023249 | -0.28985 | -1.0241 | 61.7019 | 0.2349 | 61.6103 | -0.028522 | 0.052814 | 61.557 | 0.012299 | 61.3398 | 61.2836 | 61.1487 | 61.2459 | 61.3886 | 61.4224 | 61.1558 | 60.4215 | 123.1475 | 61.6805 | 123.0559 | 61.4171 | 61.4984 | 123.0026 | 61.4579 | 122.7854 | 61.6491 | 61.6896 | 61.5575 | 61.598
7584.0938 | 123.2254 | -61.4639 | 61.6699 | -0.07502 | -0.23741 | -0.12189 | 0.020768 | 0.049999 | -0.1937 | -0.90052 | 61.7065 | 0.23032 | 61.5965 | -0.023943 | 0.048236 | 61.5707 | 0.016878 | 61.3489 | 61.3889 | 61.2265 | 61.342 | 61.4847 | 61.5139 | 61.2702 | 60.5634 | 123.1704 | 61.6942 | 123.0605 | 61.44 | 61.5122 | 123.0347 | 61.4808 | 122.8129 | 61.6583 | 61.6896 | 61.5483 | 61.5797
7585.0781 | 123.1979 | -61.5051 | 61.5738 | -0.065863 | -0.23741 | -0.11731 | 0.029925 | 0.06831 | -0.17996 | -0.91884 | 61.7065 | 0.2349 | 61.624 | -0.023943 | 0.043657 | 61.5662 | 0.007721 | 61.3489 | 61.4393 | 61.2677 | 61.3878 | 61.5351 | 61.5734 | 61.3252 | 60.5863 | 123.2116 | 61.74 | 123.1291 | 61.4812 | 61.5488 | 123.0713 | 61.5128 | 122.8541 | 61.6628 | 61.6988 | 61.5804 | 61.6163
7586.0938 | 123.4039 | -61.441 | 61.5967 | 0.002813 | -0.18704 | -0.039471 | 0.10318 | 0.12782 | -0.12044 | -0.83185 | 61.6928 | 0.23032 | 61.5965 | -0.033101 | 0.048236 | 61.5799 | 0.016878 | 61.3489 | 61.4439 | 61.254 | 61.4016 | 61.5442 | 61.5689 | 61.3206 | 60.6092 | 123.1338 | 61.6714 | 123.0376 | 61.4079 | 61.4893 | 123.0209 | 61.4579 | 122.79 | 61.6445 | 61.6759 | 61.5483 | 61.5797
7587.0625 | 123.4085 | -61.4319 | 61.6562 | -0.27647 | -0.48009 | -0.31877 | -0.199 | -0.15143 | -0.4272 | -1.1661 | 61.7157 | 0.23948 | 61.6469 | -0.019364 | 0.043657 | 61.557 | 0.016878 | 61.3306 | 61.1554 | 60.9518 | 61.1131 | 61.2329 | 61.2805 | 61.0047 | 60.2658 | 123.1475 | 61.6714 | 123.0788 | 61.4125 | 61.4755 | 122.9889 | 61.4488 | 122.7625 | 61.672 | 61.6988 | 61.6032 | 61.63
7588.1094 | 123.3398 | -61.4594 | 61.6516 | -0.24442 | -0.43888 | -0.30045 | -0.16237 | -0.12854 | -0.39515 | -1.1432 | 61.7065 | 0.22574 | 61.6103 | -0.019364 | 0.043657 | 61.557 | 0.003143 | 61.3398 | 61.2149 | 61.0205 | 61.1589 | 61.297 | 61.3308 | 61.0642 | 60.3162 | 123.1659 | 61.6851 | 123.0696 | 61.44 | 61.503 | 123.0164 | 61.4625 | 122.7991 | 61.6628 | 61.7034 | 61.5666 | 61.6071
7589.0625 | 123.3673 | -61.4365 | 61.6241 | -0.22153 | -0.37477 | -0.25467 | -0.10285 | -0.073606 | -0.34936 | -1.0837 | 61.7065 | 0.2349 | 61.624 | -0.023943 | 0.052814 | 61.5662 | 0.007721 | 61.3398 | 61.2149 | 61.0617 | 61.1818 | 61.3336 | 61.3629 | 61.0871 | 60.3528 | 123.143 | 61.6714 | 123.0605 | 61.4125 | 61.4893 | 123.0026 | 61.4442 | 122.7762 | 61.6537 | 61.6988 | 61.5712 | 61.6163
7590.0938 | 123.381 | -61.4319 | 61.615 | -0.25816 | -0.48467 | -0.31877 | -0.17611 | -0.12396 | -0.43635 | -1.1752 | 61.7019 | 0.22574 | 61.6103 | -0.019364 | 0.043657 | 61.5524 | 0.012299 | 61.326 | 61.1737 | 60.9472 | 61.1131 | 61.2558 | 61.3079 | 60.9955 | 60.2567 | 123.1338 | 61.6576 | 123.0422 | 61.4125 | 61.4755 | 122.9843 | 61.4442 | 122.7579 | 61.6583 | 61.6896 | 61.5666 | 61.598
7591.0625 | 123.2803 | -61.4273 | 61.6791 | -0.22153 | -0.38851 | -0.27298 | -0.14406 | -0.11023 | -0.39973 | -1.102 | 61.7202 | 0.23948 | 61.6377 | -0.028522 | 0.057392 | 61.5524 | 0.012299 | 61.3398 | 61.2058 | 61.0388 | 61.1543 | 61.2832 | 61.3171 | 61.0276 | 60.3253 | 123.1475 | 61.6668 | 123.0651 | 61.3988 | 61.4847 | 122.9797 | 61.4396 | 122.7671 | 61.6628 | 61.7079 | 61.5804 | 61.6255
7592.0938 | 123.3719 | -61.4319 | 61.6287 | -0.24442 | -0.43888 | -0.29587 | -0.15321 | -0.12396 | -0.44093 | -1.1615 | 61.7065 | 0.22574 | 61.6057 | -0.028522 | 0.043657 | 61.5616 | 0.012299 | 61.3352 | 61.1875 | 60.993 | 61.136 | 61.2787 | 61.3079 | 60.991 | 60.2704 | 123.1384 | 61.6576 | 123.0376 | 61.4034 | 61.4755 | 122.9935 | 61.4442 | 122.7671 | 61.6628 | 61.6942 | 61.562 | 61.5934
7593.0625 | 123.3444 | -61.4182 | 61.6379 | -0.39093 | -0.53503 | -0.43781 | -0.28141 | -0.24299 | -0.56455 | -1.2759 | 61.7202 | 0.2349 | 61.6332 | -0.023943 | 0.048236 | 61.5524 | 0.007721 | 61.3352 | 61.0272 | 60.8831 | 60.9803 | 61.1367 | 61.1752 | 60.8536 | 60.1422 | 123.1384 | 61.653 | 123.0513 | 61.3942 | 61.4664 | 122.9706 | 61.4259 | 122.7533 | 61.672 | 61.7125 | 61.5849 | 61.6255
7594.1094 | 123.3353 | -61.4548 | 61.6241 | -0.28563 | -0.44346 | -0.32334 | -0.18526 | -0.15143 | -0.45009 | -1.1706 | 61.7202 | 0.23032 | 61.6286 | -0.023943 | 0.052814 | 61.5478 | 0.012299 | 61.3398 | 61.1691 | 61.0113 | 61.1314 | 61.2695 | 61.3033 | 61.0047 | 60.2841 | 123.175 | 61.6851 | 123.0834 | 61.4308 | 61.5076 | 123.0026 | 61.4671 | 122.7945 | 61.6674 | 61.7079 | 61.5758 | 61.6163
7595.0625 | 123.3353 | -61.4319 | 61.647 | -0.22153 | -0.36104 | -0.2684 | -0.10743 | -0.078184 | -0.39973 | -1.0928 | 61.7065 | 0.22116 | 61.6057 | -0.028522 | 0.048236 | 61.5616 | 0.016878 | 61.3398 | 61.2104 | 61.0708 | 61.1635 | 61.3245 | 61.3537 | 61.0322 | 60.3391 | 123.1384 | 61.653 | 123.0376 | 61.4034 | 61.4801 | 122.9935 | 61.4488 | 122.7717 | 61.6583 | 61.6896 | 61.5575 | 61.5888
7596.0938 | 123.349 | -61.4456 | 61.6241 | -0.29936 | -0.42972 | -0.3325 | -0.17153 | -0.1377 | -0.43635 | -1.1798 | 61.7111 | 0.23948 | 61.6423 | -0.028522 | 0.043657 | 61.5478 | 0.012299 | 61.3352 | 61.1463 | 61.0159 | 61.1131 | 61.2741 | 61.3079 | 61.0093 | 60.2658 | 123.1567 | 61.6851 | 123.0879 | 61.4171 | 61.4893 | 122.9935 | 61.4579 | 122.7808 | 61.6674 | 61.6988 | 61.5987 | 61.63
7597.0625 | 123.4085 | -61.4182 | 61.647 | -0.27189 | -0.38393 | -0.30961 | -0.15321 | -0.11939 | -0.4272 | -1.1249 | 61.7019 | 0.22116 | 61.6103 | -0.023943 | 0.048236 | 61.5616 | 0.012299 | 61.3443 | 61.1463 | 61.0342 | 61.1085 | 61.2649 | 61.2988 | 60.991 | 60.2933 | 123.1201 | 61.6393 | 123.0284 | 61.3942 | 61.4664 | 122.9797 | 61.4305 | 122.7625 | 61.6537 | 61.6896 | 61.562 | 61.598
7598.0625 | 123.3765 | -61.4365 | 61.6425 | -0.33141 | -0.48924 | -0.37829 | -0.21274 | -0.16974 | -0.52792 | -1.2347 | 61.7157 | 0.23032 | 61.624 | -0.023943 | 0.048236 | 61.5478 | 0.012299 | 61.3306 | 61.1051 | 60.9472 | 61.0582 | 61.2237 | 61.2667 | 60.9085 | 60.2017 | 123.1521 | 61.6668 | 123.0605 | 61.4125 | 61.4847 | 122.9843 | 61.4488 | 122.7671 | 61.6674 | 61.7034 | 61.5758 | 61.6117
7599.0938 | 123.2391 | -61.4639 | 61.6608 | -0.34514 | -0.46177 | -0.38744 | -0.21274 | -0.16974 | -0.50961 | -1.2164 | 61.7157 | 0.23948 | 61.6194 | -0.019364 | 0.048236 | 61.5524 | 0.012299 | 61.3306 | 61.1188 | 61.0022 | 61.0765 | 61.2512 | 61.2942 | 60.9543 | 60.2475 | 123.1796 | 61.7034 | 123.0834 | 61.4446 | 61.5122 | 123.0164 | 61.4762 | 122.7945 | 61.6674 | 61.7034 | 61.5712 | 61.6071
7600.0625 | 123.2437 | -61.4136 | 61.7065 | -0.36346 | -0.48009 | -0.40576 | -0.22647 | -0.18805 | -0.52334 | -1.253 | 61.7157 | 0.23032 | 61.6194 | -0.033101 | 0.048236 | 61.5478 | 0.021456 | 61.3352 | 61.0501 | 60.9335 | 61.0078 | 61.1871 | 61.2255 | 60.8902 | 60.1605 | 123.1292 | 61.6439 | 123.033 | 61.3805 | 61.4618 | 122.9614 | 61.435 | 122.7488 | 61.6674 | 61.6942 | 61.5712 | 61.598
7601.0781 | 123.2254 | -61.4639 | 61.6516 | -0.3543 | -0.47093 | -0.39202 | -0.22647 | -0.17432 | -0.51419 | -1.2485 | 61.7202 | 0.2349 | 61.6469 | -0.023943 | 0.043657 | 61.5524 | 0.007721 | 61.3352 | 61.1096 | 60.993 | 61.0719 | 61.2375 | 61.2896 | 60.9497 | 60.2155 | 123.1842 | 61.6988 | 123.1108 | 61.44 | 61.5076 | 123.0164 | 61.4716 | 122.7991 | 61.6766 | 61.7125 | 61.6032 | 61.6392
7602.0625 | 123.3307 | -61.4273 | 61.6196 | -0.29478 | -0.42056 | -0.35082 | -0.17153 | -0.1377 | -0.45009 | -1.1798 | 61.7111 | 0.22116 | 61.6194 | -0.028522 | 0.048236 | 61.557 | 0.012299 | 61.3398 | 61.1325 | 61.0067 | 61.0765 | 61.2558 | 61.2896 | 60.9772 | 60.2475 | 123.1384 | 61.6485 | 123.0467 | 61.3988 | 61.4755 | 122.9843 | 61.4396 | 122.7671 | 61.6628 | 61.6988 | 61.5712 | 61.6071
7603.1094 | 123.2391 | -61.4639 | 61.6745 | -0.46876 | -0.5854 | -0.51565 | -0.35467 | -0.30708 | -0.59202 | -1.3171 | 61.7294 | 0.2349 | 61.624 | -0.023943 | 0.048236 | 61.5433 | 0.007721 | 61.326 | 60.9952 | 60.8785 | 60.9483 | 61.1093 | 61.1568 | 60.8719 | 60.1468 | 123.1933 | 61.6988 | 123.0879 | 61.44 | 61.5122 | 123.0072 | 61.4716 | 122.79 | 61.6812 | 61.7217 | 61.5758 | 61.6163
7604.0625 | 123.381 | -61.4182 | 61.6241 | -0.4825 | -0.60829 | -0.49275 | -0.33636 | -0.30708 | -0.58286 | -1.3171 | 61.7248 | 0.23032 | 61.6377 | -0.033101 | 0.048236 | 61.5478 | 0.007721 | 61.326 | 60.9357 | 60.8099 | 60.9254 | 61.0818 | 61.1111 | 60.8353 | 60.101 | 123.143 | 61.6485 | 123.0559 | 61.3851 | 61.4664 | 122.966 | 61.4259 | 122.7442 | 61.6766 | 61.7171 | 61.5895 | 61.63
7605.0938 | 123.3673 | -61.409 | 61.6425 | -0.38635 | -0.50756 | -0.4195 | -0.25852 | -0.21094 | -0.41346 | -1.1935 | 61.7202 | 0.22574 | 61.6103 | -0.028522 | 0.043657 | 61.5524 | 0.016878 | 61.326 | 61.0226 | 60.9014 | 60.9895 | 61.1505 | 61.1981 | 60.9955 | 60.2155 | 123.1292 | 61.6347 | 123.0193 | 61.3805 | 61.4527 | 122.9614 | 61.4259 | 122.735 | 61.6766 | 61.7034 | 61.5666 | 61.5934
7606.0625 | 123.3536 | -61.4365 | 61.647 | -0.31767 | -0.44346 | -0.36455 | -0.18984 | -0.15143 | -0.40888 | -1.1294 | 61.7202 | 0.23948 | 61.6469 | -0.028522 | 0.052814 | 61.557 | 0.012299 | 61.3398 | 61.1188 | 60.993 | 61.0719 | 61.2466 | 61.285 | 61.0276 | 60.307 | 123.1567 | 61.6759 | 123.0834 | 61.4079 | 61.4893 | 122.9935 | 61.4488 | 122.7762 | 61.6674 | 61.7079 | 61.5941 | 61.6346
7607.0938 | 123.2666 | -61.441 | 61.6837 | -0.39551 | -0.51672 | -0.2684 | -0.17153 | -0.13312 | -0.4684 | -1.1981 | 61.7157 | 0.2349 | 61.6149 | -0.028522 | 0.052814 | 61.5524 | 0.012299 | 61.3306 | 61.0455 | 60.9243 | 61.1726 | 61.2695 | 61.3079 | 60.9726 | 60.2429 | 123.1567 | 61.6759 | 123.0559 | 61.4125 | 61.4939 | 122.9935 | 61.4533 | 122.7717 | 61.6628 | 61.7034 | 61.562 | 61.6026
7608.0625 | 123.3627 | -61.4227 | 61.6241 | -0.68852 | -0.78687 | -0.68505 | -0.51949 | -0.47647 | -0.80262 | -1.5048 | 61.734 | 0.22574 | 61.6469 | -0.023943 | 0.043657 | 61.5341 | 0.012299 | 61.3077 | 60.7342 | 60.6359 | 60.7377 | 60.9032 | 60.9463 | 60.6201 | 59.9179 | 123.1567 | 61.6485 | 123.0696 | 61.3988 | 61.4664 | 122.9568 | 61.435 | 122.7305 | 61.6903 | 61.7217 | 61.6032 | 61.6346
7609.0938 | 123.2666 | -61.4502 | 61.6653 | -0.44587 | -0.54419 | -0.44697 | -0.29057 | -0.23841 | -0.53708 | -1.2393 | 61.7294 | 0.23948 | 61.6423 | -0.028522 | 0.052814 | 61.5433 | 0.012299 | 61.326 | 61.0043 | 60.906 | 61.0032 | 61.1596 | 61.2118 | 60.9131 | 60.2109 | 123.1796 | 61.6897 | 123.0925 | 61.4217 | 61.503 | 122.9935 | 61.4625 | 122.7762 | 61.6766 | 61.7171 | 61.5895 | 61.63
7610.0625 | 123.349 | -61.4319 | 61.6837 | -0.45503 | -0.56708 | -0.4607 | -0.28141 | -0.24757 | -0.55081 | -1.2622 | 61.7157 | 0.23032 | 61.6057 | -0.028522 | 0.043657 | 61.5478 | 0.012299 | 61.3306 | 60.9769 | 60.8648 | 60.9712 | 61.1505 | 61.1843 | 60.8811 | 60.1697 | 123.1475 | 61.6622 | 123.0376 | 61.4034 | 61.4755 | 122.9797 | 61.4442 | 122.7625 | 61.672 | 61.7034 | 61.562 | 61.5934
7611.0938 | 123.2895 | -61.4502 | 61.6562 | -0.3543 | -0.47551 | -0.35997 | -0.18984 | -0.15143 | -0.39515 | -1.134 | 61.7202 | 0.23948 | 61.6561 | -0.028522 | 0.048236 | 61.557 | 0.016878 | 61.3398 | 61.0959 | 60.9747 | 61.0902 | 61.2604 | 61.2988 | 61.055 | 60.3162 | 123.1704 | 61.6897 | 123.1063 | 61.4217 | 61.4984 | 123.0072 | 61.4671 | 122.79 | 61.672 | 61.7034 | 61.6078 | 61.6392
7612.0625 | 123.2529 | -61.4319 | 61.6837 | -0.35888 | -0.47093 | -0.36455 | -0.19442 | -0.16059 | -0.43178 | -1.1569 | 61.7111 | 0.23032 | 61.6103 | -0.033101 | 0.057392 | 61.5478 | 0.012299 | 61.3398 | 61.073 | 60.961 | 61.0673 | 61.2375 | 61.2713 | 61.0001 | 60.275 | 123.143 | 61.6622 | 123.0422 | 61.3988 | 61.4893 | 122.9797 | 61.4442 | 122.7717 | 61.6537 | 61.6988 | 61.5529 | 61.598
7613.0938 | 123.2117 | -61.5005 | 61.6287 | -0.29478 | -0.42056 | -0.29587 | -0.1349 | -0.10107 | -0.40888 | -1.0974 | 61.7202 | 0.2349 | 61.624 | -0.033101 | 0.052814 | 61.557 | 0.012299 | 61.3443 | 61.2058 | 61.08 | 61.2047 | 61.3656 | 61.3995 | 61.0917 | 60.4032 | 123.2208 | 61.7354 | 123.1246 | 61.4674 | 61.5534 | 123.0576 | 61.5128 | 122.8449 | 61.6674 | 61.7079 | 61.5712 | 61.6117
7614.0625 | 123.3673 | -61.4365 | 61.6104 | -0.18032 | -0.2832 | -0.19057 | -0.011281 | 0.008797 | -0.28527 | -0.96004 | 61.7111 | 0.2349 | 61.6103 | -0.028522 | 0.039079 | 61.5662 | 0.007721 | 61.3443 | 61.2561 | 61.1533 | 61.2459 | 61.4252 | 61.4453 | 61.1512 | 60.4764 | 123.1475 | 61.6714 | 123.0467 | 61.4079 | 61.4755 | 123.0026 | 61.4442 | 122.7808 | 61.672 | 61.7034 | 61.5712 | 61.6026
7615.0938 | 123.2941 | -61.409 | 61.6837 | -0.43213 | -0.54419 | -0.44239 | -0.27226 | -0.23841 | -0.57371 | -1.2576 | 61.7202 | 0.23032 | 61.6194 | -0.028522 | 0.052814 | 61.5478 | 0.012299 | 61.3306 | 60.9769 | 60.8648 | 60.9666 | 61.1367 | 61.1706 | 60.8353 | 60.1514 | 123.1292 | 61.6393 | 123.0284 | 61.3805 | 61.4618 | 122.9568 | 61.4213 | 122.7396 | 61.6674 | 61.7079 | 61.5666 | 61.6071
7616.0625 | 123.3353 | -61.4182 | 61.6653 | -0.40924 | -0.5213 | -0.4195 | -0.24021 | -0.20179 | -0.53708 | -1.2485 | 61.7202 | 0.24405 | 61.6515 | -0.023943 | 0.043657 | 61.5524 | 0.012299 | 61.3443 | 61.0089 | 60.8969 | 60.9987 | 61.1779 | 61.2164 | 60.8811 | 60.1697 | 123.1384 | 61.6622 | 123.0696 | 61.3942 | 61.4618 | 122.9706 | 61.4305 | 122.7625 | 61.6766 | 61.7079 | 61.6078 | 61.6392
7617.0938 | 123.2437 | -61.4227 | 61.6791 | -0.54659 | -0.6724 | -0.55685 | -0.38672 | -0.34371 | -0.66527 | -1.3904 | 61.7248 | 0.23032 | 61.6286 | -0.028522 | 0.052814 | 61.5433 | 0.003143 | 61.3169 | 60.8761 | 60.7503 | 60.8659 | 61.036 | 61.079 | 60.7575 | 60.0323 | 123.1475 | 61.653 | 123.0513 | 61.3942 | 61.4755 | 122.966 | 61.4259 | 122.7396 | 61.672 | 61.7217 | 61.5758 | 61.6255
7618.0625 | 123.3307 | -61.4182 | 61.6379 | -0.44587 | -0.62661 | -0.47902 | -0.31804 | -0.28419 | -0.60575 | -1.3263 | 61.7294 | 0.2349 | 61.6377 | -0.028522 | 0.052814 | 61.5478 | 0.012299 | 61.3306 | 60.9723 | 60.7915 | 60.9391 | 61.1001 | 61.134 | 60.8124 | 60.0919 | 123.1475 | 61.653 | 123.0559 | 61.3896 | 61.471 | 122.966 | 61.4305 | 122.7488 | 61.6766 | 61.7171 | 61.5849 | 61.6255
7619.0781 | 123.2346 | -61.4502 | 61.6745 | -0.35888 | -0.5213 | -0.39202 | -0.22189 | -0.18805 | -0.50503 | -1.2027 | 61.7157 | 0.2349 | 61.624 | -0.028522 | 0.043657 | 61.5524 | 0.003143 | 61.3352 | 61.0913 | 60.9289 | 61.0582 | 61.2283 | 61.2621 | 60.9452 | 60.2475 | 123.1659 | 61.6851 | 123.0742 | 61.4217 | 61.4939 | 123.0026 | 61.4533 | 122.7854 | 61.672 | 61.7125 | 61.5804 | 61.6209
7620.0625 | 123.3307 | -61.4319 | 61.647 | -0.49165 | -0.68613 | -0.55227 | -0.38672 | -0.34371 | -0.64696 | -1.3446 | 61.7202 | 0.23032 | 61.624 | -0.023943 | 0.048236 | 61.5478 | 0.007721 | 61.326 | 60.9402 | 60.7458 | 60.8796 | 61.0452 | 61.0882 | 60.7849 | 60.0873 | 123.1521 | 61.6622 | 123.0559 | 61.4079 | 61.4801 | 122.9797 | 61.4396 | 122.7579 | 61.672 | 61.7125 | 61.5758 | 61.6163
7621.0938 | 123.317 | -61.4273 | 61.6791 | -0.54659 | -0.70903 | -0.62095 | -0.43708 | -0.39864 | -0.68359 | -1.4041 | 61.734 | 0.23948 | 61.6606 | -0.028522 | 0.043657 | 61.5478 | 0.003143 | 61.326 | 60.8807 | 60.7183 | 60.8064 | 60.9902 | 61.0287 | 60.7437 | 60.0232 | 123.1613 | 61.6668 | 123.0879 | 61.3988 | 61.471 | 122.9752 | 61.4305 | 122.7533 | 61.6903 | 61.7308 | 61.617 | 61.6575
7622.0625 | 123.3765 | -61.4365 | 61.6333 | -0.26731 | -0.42056 | -0.32792 | -0.15321 | -0.11939 | -0.3631 | -1.0837 | 61.7019 | 0.22116 | 61.6011 | -0.028522 | 0.052814 | 61.5524 | 0.016878 | 61.3398 | 61.1692 | 61.0159 | 61.1085 | 61.2832 | 61.3171 | 61.0734 | 60.3528 | 123.1384 | 61.6576 | 123.0376 | 61.4079 | 61.4893 | 122.9889 | 61.4533 | 122.7762 | 61.6491 | 61.685 | 61.5483 | 61.5842
7623.1094 | 123.3261 | -61.4319 | 61.6425 | -0.26273 | -0.41141 | -0.30961 | -0.14406 | -0.11939 | -0.44093 | -1.1294 | 61.7157 | 0.24405 | 61.6377 | -0.023943 | 0.043657 | 61.557 | 0.012299 | 61.3352 | 61.1692 | 61.0205 | 61.1223 | 61.2878 | 61.3125 | 60.991 | 60.3025 | 123.1475 | 61.6759 | 123.0696 | 61.4079 | 61.4755 | 122.9889 | 61.4442 | 122.7671 | 61.672 | 61.7034 | 61.5941 | 61.6255
7624.0625 | 123.3124 | -61.4273 | 61.6562 | -0.26731 | -0.43888 | -0.32792 | -0.16695 | -0.13312 | -0.45009 | -1.1523 | 61.7111 | 0.2349 | 61.6103 | -0.023943 | 0.048236 | 61.5616 | 0.012299 | 61.3306 | 61.16 | 60.9884 | 61.0994 | 61.2604 | 61.2942 | 60.9772 | 60.275 | 123.1384 | 61.6622 | 123.0376 | 61.4034 | 61.4755 | 122.9889 | 61.4396 | 122.7579 | 61.6628 | 61.6988 | 61.562 | 61.598
7625.0938 | 123.2437 | -61.4548 | 61.7111 | -0.37719 | -0.53503 | -0.43781 | -0.25852 | -0.23383 | -0.5325 | -1.2347 | 61.7202 | 0.23948 | 61.624 | -0.023943 | 0.052814 | 61.5478 | 0.012299 | 61.3352 | 61.0776 | 60.9197 | 61.017 | 61.1963 | 61.2209 | 60.9223 | 60.22 | 123.175 | 61.6942 | 123.0788 | 61.4308 | 61.5076 | 123.0026 | 61.4671 | 122.79 | 61.6674 | 61.7079 | 61.5712 | 61.6117
7626.0625 | 123.3856 | -61.3953 | 61.6837 | -0.67937 | -0.85555 | -0.74458 | -0.58359 | -0.5314 | -0.85757 | -1.5415 | 61.734 | 0.2349 | 61.6515 | -0.023943 | 0.048236 | 61.5341 | 0.012299 | 61.3077 | 60.7159 | 60.5397 | 60.6507 | 60.8117 | 60.8639 | 60.5377 | 59.8538 | 123.1292 | 61.6302 | 123.0467 | 61.3713 | 61.4435 | 122.9294 | 61.4076 | 122.703 | 61.6857 | 61.7217 | 61.6032 | 61.6392
7627.0781 | 123.2895 | -61.4594 | 61.647 | -0.10707 | -0.27862 | -0.15851 | -0.002124 | 0.036265 | -0.16623 | -0.90968 | 61.6928 | 0.22574 | 61.5965 | -0.023943 | 0.057392 | 61.5662 | 0.016878 | 61.3489 | 61.3523 | 61.1807 | 61.3008 | 61.4572 | 61.4956 | 61.2931 | 60.5497 | 123.1521 | 61.6851 | 123.0559 | 61.4354 | 61.5167 | 123.0255 | 61.4762 | 122.8083 | 61.6354 | 61.6759 | 61.5392 | 61.5797
7628.0625 | 123.381 | -61.4182 | 61.6653 | -0.28105 | -0.44346 | -0.33708 | -0.16237 | -0.12854 | -0.44551 | -1.134 | 61.7202 | 0.23948 | 61.6423 | -0.023943 | 0.048236 | 61.5662 | 0.007721 | 61.3352 | 61.1371 | 60.9747 | 61.0811 | 61.2558 | 61.2896 | 60.9726 | 60.2841 | 123.1384 | 61.6576 | 123.0605 | 61.3942 | 61.4664 | 122.9843 | 61.4259 | 122.7533 | 61.672 | 61.7125 | 61.5941 | 61.6346
7629.0938 | 123.262 | -61.4548 | 61.6837 | -0.40009 | -0.55335 | -0.46528 | -0.29515 | -0.25672 | -0.56913 | -1.253 | 61.7248 | 0.23032 | 61.6194 | -0.033101 | 0.052814 | 61.5478 | 0.007721 | 61.3215 | 61.0547 | 60.9014 | 60.9895 | 61.1596 | 61.198 | 60.8856 | 60.2017 | 123.1796 | 61.6851 | 123.0742 | 61.4217 | 61.5076 | 123.0026 | 61.4625 | 122.7762 | 61.672 | 61.7171 | 61.5666 | 61.6117
7630.0625 | 123.2712 | -61.4136 | 61.6882 | -0.39093 | -0.52587 | -0.45154 | -0.26768 | -0.22926 | -0.53708 | -1.2347 | 61.7157 | 0.23948 | 61.6332 | -0.028522 | 0.048236 | 61.5478 | 0.016878 | 61.3306 | 61.0226 | 60.8877 | 60.962 | 61.1459 | 61.1843 | 60.8765 | 60.1788 | 123.1292 | 61.6531 | 123.0467 | 61.3851 | 61.4618 | 122.9614 | 61.4305 | 122.7442 | 61.6674 | 61.6988 | 61.5849 | 61.6163
7631.1094 | 123.3536 | -61.4319 | 61.6653 | -0.50997 | -0.63119 | -0.5477 | -0.3913 | -0.34828 | -0.61949 | -1.3171 | 61.7294 | 0.23032 | 61.6377 | -0.028522 | 0.057392 | 61.5433 | 0.012299 | 61.3215 | 60.9219 | 60.8007 | 60.8842 | 61.0406 | 61.0836 | 60.8124 | 60.1147 | 123.1613 | 61.6622 | 123.0696 | 61.4034 | 61.4893 | 122.9752 | 61.4442 | 122.7533 | 61.672 | 61.7171 | 61.5804 | 61.6255
7632.0625 | 123.3444 | -61.4136 | 61.647 | -0.63816 | -0.77771 | -0.6759 | -0.51492 | -0.46273 | -0.77058 | -1.4728 | 61.734 | 0.23032 | 61.6332 | -0.019364 | 0.048236 | 61.5341 | 0.012299 | 61.3123 | 60.7754 | 60.6359 | 60.7377 | 60.8987 | 60.9508 | 60.643 | 59.9408 | 123.1475 | 61.6439 | 123.0467 | 61.3942 | 61.4618 | 122.9477 | 61.4259 | 122.7259 | 61.6857 | 61.7217 | 61.5849 | 61.6209
7633.0938 | 123.2391 | -61.4365 | 61.702 | -0.6931 | -0.86013 | -0.74916 | -0.57444 | -0.52682 | -0.8301 | -1.5323 | 61.7431 | 0.2349 | 61.6652 | -0.019364 | 0.057392 | 61.5295 | 0.012299 | 61.3169 | 60.7434 | 60.5763 | 60.6873 | 60.862 | 60.9096 | 60.6064 | 59.9042 | 123.1796 | 61.6714 | 123.1017 | 61.4171 | 61.4939 | 122.966 | 61.4488 | 122.7533 | 61.6857 | 61.7308 | 61.6078 | 61.6529
7634.0625 | 123.3673 | -61.3815 | 61.6882 | -0.67479 | -0.84639 | -0.73542 | -0.56528 | -0.51309 | -0.77058 | -1.4316 | 61.734 | 0.23032 | 61.6286 | -0.019364 | 0.048236 | 61.5387 | 0.012299 | 61.3215 | 60.7067 | 60.5351 | 60.6461 | 60.8163 | 60.8684 | 60.611 | 59.9499 | 123.1155 | 61.6118 | 123.0101 | 61.3622 | 61.4298 | 122.9202 | 61.3938 | 122.703 | 61.6857 | 61.7217 | 61.5804 | 61.6163
7635.0938 | 123.3307 | -61.4273 | 61.6928 | -0.51912 | -0.68156 | -0.56143 | -0.37756 | -0.32539 | -0.60118 | -1.2759 | 61.7386 | 0.23032 | 61.6561 | -0.028522 | 0.052814 | 61.5341 | 0.016878 | 61.3169 | 60.9082 | 60.7458 | 60.8659 | 61.0497 | 61.1019 | 60.8261 | 60.1514 | 123.1659 | 61.6576 | 123.0834 | 61.3988 | 61.4801 | 122.9614 | 61.4442 | 122.7442 | 61.6857 | 61.7217 | 61.6032 | 61.6392
7636.0625 | 123.2391 | -61.4319 | 61.7157 | -0.74346 | -0.91965 | -0.81325 | -0.59733 | -0.54971 | -0.82552 | -1.482 | 61.7431 | 0.2349 | 61.6423 | -0.028522 | 0.052814 | 61.5295 | 0.007721 | 61.3169 | 60.6884 | 60.5122 | 60.6186 | 60.8346 | 60.8822 | 60.6064 | 59.9499 | 123.175 | 61.6668 | 123.0742 | 61.4034 | 61.4847 | 122.9614 | 61.4396 | 122.7488 | 61.6903 | 61.7354 | 61.5895 | 61.6346
7637.0781 | 123.2941 | -61.4044 | 61.6699 | -0.69768 | -0.85555 | -0.75831 | -0.53323 | -0.4902 | -0.69732 | -1.2988 | 61.734 | 0.23032 | 61.6286 | -0.028522 | 0.043657 | 61.5387 | 0.021456 | 61.3215 | 60.7067 | 60.5489 | 60.6461 | 60.8712 | 60.9142 | 60.7071 | 60.1056 | 123.1384 | 61.6347 | 123.033 | 61.3759 | 61.4481 | 122.9431 | 61.4259 | 122.7259 | 61.6903 | 61.7125 | 61.5849 | 61.6071
7638.0625 | 123.2483 | -61.4273 | 61.6608 | -0.55117 | -0.73192 | -0.61638 | -0.35467 | -0.31624 | -0.48672 | -1.0562 | 61.7294 | 0.2349 | 61.6606 | -0.028522 | 0.052814 | 61.5524 | 0.016878 | 61.3306 | 60.8761 | 60.6954 | 60.8109 | 61.0726 | 61.1111 | 60.9406 | 60.3711 | 123.1567 | 61.6622 | 123.0879 | 61.3988 | 61.4801 | 122.9797 | 61.4442 | 122.7579 | 61.6766 | 61.7125 | 61.6078 | 61.6438
7639.0781 | 123.3398 | -61.4136 | 61.6699 | -0.6519 | -0.85097 | -0.72626 | -0.43708 | -0.40322 | -0.55539 | -1.0516 | 61.7248 | 0.23032 | 61.6194 | -0.028522 | 0.052814 | 61.5387 | 0.007721 | 61.3169 | 60.7617 | 60.5626 | 60.6873 | 60.9765 | 61.0104 | 60.8582 | 60.362 | 123.1384 | 61.6439 | 123.033 | 61.3851 | 61.4664 | 122.9523 | 61.4213 | 122.7305 | 61.672 | 61.7171 | 61.5666 | 61.6117
7640.0625 | 123.3902 | -61.3953 | 61.6425 | -0.71599 | -0.90134 | -0.77663 | -0.4966 | -0.449 | -0.58286 | -1.0837 | 61.734 | 0.23948 | 61.6377 | -0.023943 | 0.043657 | 61.5387 | 0.003143 | 61.3123 | 60.6793 | 60.4939 | 60.6186 | 60.8987 | 60.9463 | 60.8124 | 60.3116 | 123.1292 | 61.6347 | 123.033 | 61.3713 | 61.4389 | 122.934 | 61.3984 | 122.7076 | 61.6903 | 61.7308 | 61.5941 | 61.6346
7641.1094 | 123.349 | -61.4182 | 61.6516 | -0.91744 | -1.112 | -0.9964 | -0.70721 | -0.66416 | -0.8301 | -1.3354 | 61.7477 | 0.23032 | 61.6698 | -0.028522 | 0.043657 | 61.5295 | 0.003143 | 61.3031 | 60.5007 | 60.3062 | 60.4218 | 60.7109 | 60.754 | 60.5881 | 60.0827 | 123.1659 | 61.6485 | 123.088 | 61.3896 | 61.4618 | 122.9477 | 61.4213 | 122.7213 | 61.7041 | 61.7446 | 61.6261 | 61.6667
7642.0625 | 123.3994 | -61.4044 | 61.6516 | -0.5878 | -0.77313 | -0.64843 | -0.3684 | -0.32082 | -0.46382 | -0.93715 | 61.7202 | 0.23032 | 61.6194 | -0.019364 | 0.057392 | 61.5433 | 0.012299 | 61.3215 | 60.8166 | 60.6313 | 60.756 | 61.036 | 61.0836 | 60.9406 | 60.4673 | 123.1247 | 61.6347 | 123.0239 | 61.3851 | 61.4618 | 122.9477 | 61.4167 | 122.7259 | 61.6628 | 61.7079 | 61.562 | 61.6071
7643.0938 | 123.3032 | -61.4548 | 61.6379 | -0.60611 | -0.80976 | -0.68963 | -0.40503 | -0.35744 | -0.50045 | -1.0104 | 61.7248 | 0.23948 | 61.6606 | -0.033101 | 0.048236 | 61.5433 | 0.012299 | 61.3169 | 60.8487 | 60.645 | 60.7651 | 61.0497 | 61.0973 | 60.9543 | 60.4444 | 123.1796 | 61.6942 | 123.1154 | 61.4217 | 61.503 | 122.998 | 61.4671 | 122.7717 | 61.6766 | 61.7125 | 61.6124 | 61.6483
7644.0625 | 123.3948 | -61.3815 | 61.6837 | -0.98612 | -1.1669 | -1.0468 | -0.77589 | -0.72368 | -0.8713 | -1.3858 | 61.7431 | 0.23032 | 61.6423 | -0.028522 | 0.048236 | 61.5112 | 0.012299 | 61.294 | 60.3954 | 60.2146 | 60.3348 | 60.6056 | 60.6579 | 60.5102 | 59.9957 | 123.1247 | 61.6118 | 123.0239 | 61.353 | 61.4298 | 122.8928 | 61.3938 | 122.6755 | 61.6949 | 61.7308 | 61.5941 | 61.63
7645.0938 | 123.381 | -61.4365 | 61.5967 | -0.46876 | -0.66324 | -0.54312 | -0.26768 | -0.2201 | -0.37226 | -0.84559 | 61.7157 | 0.2349 | 61.6149 | -0.028522 | 0.052814 | 61.5524 | 0.007721 | 61.3306 | 60.9677 | 60.7732 | 60.8933 | 61.1688 | 61.2164 | 61.0642 | 60.5909 | 123.1521 | 61.6714 | 123.0513 | 61.4079 | 61.4893 | 122.9889 | 61.4442 | 122.7671 | 61.6628 | 61.7079 | 61.562 | 61.6071
7646.0625 | 123.2895 | -61.4182 | 61.6882 | -0.60153 | -0.79145 | -0.68048 | -0.44166 | -0.39864 | -0.51876 | -0.97377 | 61.7294 | 0.23948 | 61.6515 | -0.023943 | 0.048236 | 61.5387 | 0.012299 | 61.3169 | 60.8166 | 60.6267 | 60.7377 | 60.9765 | 61.0195 | 60.8994 | 60.4444 | 123.1475 | 61.6576 | 123.0696 | 61.3942 | 61.4664 | 122.9568 | 61.4305 | 122.735 | 61.6812 | 61.7171 | 61.6032 | 61.6392
7647.0781 | 123.2758 | -61.4365 | 61.6791 | -0.47792 | -0.66324 | -0.54312 | -0.3272 | -0.28419 | -0.36768 | -0.8639 | 61.7202 | 0.2349 | 61.6423 | -0.033101 | 0.052814 | 61.5478 | 0.012299 | 61.326 | 60.9585 | 60.7732 | 60.8933 | 61.1093 | 61.1523 | 61.0688 | 60.5726 | 123.1567 | 61.6714 | 123.0788 | 61.4034 | 61.4893 | 122.9843 | 61.4488 | 122.7625 | 61.6674 | 61.7079 | 61.5895 | 61.63
7648.0625 | 123.3856 | -61.4319 | 61.6425 | -0.4184 | -0.57166 | -0.47902 | -0.2631 | -0.22468 | -0.34479 | -0.79522 | 61.7157 | 0.23032 | 61.6103 | -0.023943 | 0.048236 | 61.557 | 0.012299 | 61.3352 | 61.0135 | 60.8602 | 60.9529 | 61.1688 | 61.2072 | 61.0871 | 60.6367 | 123.1475 | 61.6622 | 123.0422 | 61.4079 | 61.4801 | 122.9889 | 61.4442 | 122.7671 | 61.6674 | 61.7034 | 61.562 | 61.598
7649.0781 | 123.3353 | -61.4639 | 61.5967 | -0.17117 | -0.33814 | -0.22719 | 0.025347 | 0.059155 | -0.051769 | -0.50222 | 61.7019 | 0.22574 | 61.5965 | -0.023943 | 0.048236 | 61.5616 | 0.012299 | 61.3489 | 61.2928 | 61.1258 | 61.2367 | 61.4893 | 61.5231 | 61.4122 | 60.9617 | 123.1659 | 61.6897 | 123.0605 | 61.44 | 61.5122 | 123.0255 | 61.4762 | 122.8129 | 61.6537 | 61.6896 | 61.5483 | 61.5842
7650.0625 | 123.3902 | -61.3907 | 61.6425 | -0.3543 | -0.53045 | -0.41034 | -0.20816 | -0.16974 | -0.26238 | -0.72655 | 61.7111 | 0.2349 | 61.6377 | -0.028522 | 0.048236 | 61.5524 | 0.007721 | 61.3443 | 61.0364 | 60.8602 | 60.9803 | 61.1825 | 61.2209 | 61.1283 | 60.6641 | 123.1018 | 61.6256 | 123.0284 | 61.3622 | 61.4389 | 122.9431 | 61.3984 | 122.735 | 61.6628 | 61.7034 | 61.5895 | 61.63
7651.1094 | 123.3582 | -61.441 | 61.6287 | -0.17117 | -0.33814 | -0.22262 | -0.006703 | 0.031687 | -0.038034 | -0.53885 | 61.7019 | 0.23948 | 61.6103 | -0.028522 | 0.043657 | 61.5753 | 0.016878 | 61.3352 | 61.2699 | 61.1029 | 61.2184 | 61.4343 | 61.4727 | 61.403 | 60.9022 | 123.143 | 61.6805 | 123.0513 | 61.4125 | 61.4847 | 123.0164 | 61.4579 | 122.7762 | 61.6583 | 61.685 | 61.5666 | 61.5934
7652.0625 | 123.3582 | -61.409 | 61.6425 | -0.38177 | -0.53045 | -0.44239 | -0.22189 | -0.18805 | -0.299 | -0.78149 | 61.7202 | 0.22116 | 61.6057 | -0.033101 | 0.057392 | 61.5616 | 0.016878 | 61.3306 | 61.0272 | 60.8785 | 60.9666 | 61.1871 | 61.2209 | 61.11 | 60.6275 | 123.1292 | 61.6302 | 123.0147 | 61.3759 | 61.4664 | 122.9706 | 61.4259 | 122.7396 | 61.6628 | 61.7034 | 61.5483 | 61.5888
7653.0938 | 123.3536 | -61.4456 | 61.6699 | -0.26273 | -0.41598 | -0.32792 | -0.098273 | -0.069028 | -0.1937 | -0.66704 | 61.7065 | 0.22574 | 61.6149 | -0.028522 | 0.039079 | 61.5524 | 0.007721 | 61.3489 | 61.1829 | 61.0296 | 61.1177 | 61.3473 | 61.3766 | 61.2519 | 60.7786 | 123.1521 | 61.6714 | 123.0605 | 61.4171 | 61.4847 | 122.998 | 61.4533 | 122.7945 | 61.6674 | 61.6988 | 61.5758 | 61.6071
7654.0625 | 123.3261 | -61.4685 | 61.6196 | -0.23984 | -0.40225 | -0.29587 | -0.07538 | -0.041561 | -0.15249 | -0.60752 | 61.6973 | 0.23948 | 61.6286 | -0.023943 | 0.052814 | 61.5616 | 0.012299 | 61.3443 | 61.2287 | 61.0663 | 61.1726 | 61.3931 | 61.4269 | 61.316 | 60.861 | 123.1659 | 61.708 | 123.0971 | 61.4446 | 61.5213 | 123.0301 | 61.4808 | 122.8129 | 61.6445 | 61.685 | 61.5758 | 61.6163
7655.0938 | 123.3307 | -61.4685 | 61.5967 | -0.34514 | -0.50298 | -0.41492 | -0.18069 | -0.15143 | -0.2578 | -0.68077 | 61.7111 | 0.2349 | 61.6011 | -0.033101 | 0.043657 | 61.557 | 0.007721 | 61.3398 | 61.1234 | 60.9655 | 61.0536 | 61.2878 | 61.3171 | 61.2107 | 60.7877 | 123.1796 | 61.7034 | 123.0696 | 61.4354 | 61.5122 | 123.0255 | 61.4762 | 122.8083 | 61.6674 | 61.7034 | 61.5575 | 61.5934
7656.0625 | 123.2941 | -61.4365 | 61.6882 | -0.45503 | -0.61745 | -0.52022 | -0.27683 | -0.23841 | -0.34479 | -0.80438 | 61.7111 | 0.23032 | 61.6194 | -0.023943 | 0.052814 | 61.5524 | 0.007721 | 61.3352 | 60.9814 | 60.819 | 60.9162 | 61.1596 | 61.198 | 61.0917 | 60.6321 | 123.1475 | 61.6668 | 123.0559 | 61.4125 | 61.4893 | 122.9889 | 61.4442 | 122.7717 | 61.6583 | 61.7034 | 61.5666 | 61.6117
7657.0938 | 123.2346 | -61.4868 | 61.6425 | -0.43213 | -0.59914 | -0.49275 | -0.2631 | -0.22468 | -0.33563 | -0.7586 | 61.7157 | 0.2349 | 61.6377 | -0.023943 | 0.048236 | 61.5524 | 0.007721 | 61.3352 | 61.0547 | 60.8877 | 60.9941 | 61.2237 | 61.2621 | 61.1512 | 60.7282 | 123.2025 | 61.7217 | 123.1246 | 61.4629 | 61.5351 | 123.0392 | 61.4945 | 122.822 | 61.6674 | 61.7079 | 61.5895 | 61.63
7658.0625 | 123.3444 | -61.4273 | 61.6699 | -0.45045 | -0.60372 | -0.51107 | -0.27226 | -0.23383 | -0.34936 | -0.79065 | 61.7157 | 0.23032 | 61.6332 | -0.028522 | 0.057392 | 61.5524 | 0.012299 | 61.3215 | 60.9769 | 60.8236 | 60.9162 | 61.1551 | 61.1935 | 61.0779 | 60.6367 | 123.143 | 61.6576 | 123.0605 | 61.3988 | 61.4847 | 122.9797 | 61.4396 | 122.7488 | 61.6583 | 61.7034 | 61.5758 | 61.6209
7659.0938 | 123.3261 | -61.441 | 61.6241 | -0.56033 | -0.71819 | -0.63011 | -0.38214 | -0.33913 | -0.45925 | -0.91426 | 61.7248 | 0.22574 | 61.624 | -0.033101 | 0.043657 | 61.5433 | 0.007721 | 61.326 | 60.8807 | 60.7229 | 60.8109 | 61.0589 | 61.1019 | 60.9818 | 60.5268 | 123.1659 | 61.6668 | 123.0651 | 61.4079 | 61.4847 | 122.9843 | 61.4488 | 122.7671 | 61.6812 | 61.7171 | 61.5804 | 61.6163
7660.0625 | 123.3536 | -61.441 | 61.5784 | -0.18948 | -0.3473 | -0.24551 | 0.01619 | 0.045421 | -0.083817 | -0.5068 | 61.7111 | 0.22574 | 61.6057 | -0.033101 | 0.043657 | 61.5753 | 0.016878 | 61.3535 | 61.2516 | 61.0937 | 61.1955 | 61.4572 | 61.4865 | 61.3572 | 60.9342 | 123.1521 | 61.6668 | 123.0467 | 61.4079 | 61.4847 | 123.0164 | 61.4579 | 122.7945 | 61.6674 | 61.6942 | 61.562 | 61.5888
7661.1094 | 123.2849 | -61.441 | 61.6562 | -0.093333 | -0.22367 | -0.14478 | 0.11692 | 0.15071 | 0.026064 | -0.41066 | 61.7019 | 0.23948 | 61.6194 | -0.019364 | 0.052814 | 61.5707 | 0.012299 | 61.3627 | 61.3477 | 61.2174 | 61.2963 | 61.558 | 61.5918 | 61.4671 | 61.0304 | 123.143 | 61.6805 | 123.0605 | 61.4217 | 61.4939 | 123.0118 | 61.4533 | 122.8037 | 61.6491 | 61.6896 | 61.5666 | 61.6071
7662.0625 | 123.3398 | -61.4548 | 61.6241 | -0.34514 | -0.48924 | -0.40118 | -0.13948 | -0.10565 | -0.20743 | -0.63041 | 61.7019 | 0.23032 | 61.6011 | -0.028522 | 0.039079 | 61.5616 | 0.016878 | 61.3352 | 61.1096 | 60.9655 | 61.0536 | 61.3153 | 61.3491 | 61.2473 | 60.8244 | 123.1567 | 61.6851 | 123.0559 | 61.4263 | 61.4939 | 123.0164 | 61.4717 | 122.79 | 61.6628 | 61.685 | 61.562 | 61.5842
7663.0938 | 123.3536 | -61.4365 | 61.6562 | -0.51912 | -0.6724 | -0.57517 | -0.34093 | -0.29793 | -0.41346 | -0.82269 | 61.7202 | 0.2349 | 61.6561 | -0.028522 | 0.052814 | 61.5478 | 0.012299 | 61.3215 | 60.9173 | 60.7641 | 60.8613 | 61.0955 | 61.1385 | 61.023 | 60.6138 | 123.1567 | 61.6714 | 123.0925 | 61.4079 | 61.4893 | 122.9843 | 61.4488 | 122.7579 | 61.6674 | 61.7079 | 61.6032 | 61.6438
7664.0625 | 123.349 | -61.4456 | 61.6608 | -0.51455 | -0.6724 | -0.57517 | -0.31346 | -0.27961 | -0.40431 | -0.81812 | 61.7248 | 0.23032 | 61.624 | -0.023943 | 0.043657 | 61.5524 | 0.012299 | 61.3215 | 60.9311 | 60.7732 | 60.8705 | 61.1322 | 61.166 | 61.0413 | 60.6275 | 123.1704 | 61.6759 | 123.0696 | 61.4217 | 61.4893 | 122.998 | 61.4579 | 122.7671 | 61.6812 | 61.7125 | 61.5804 | 61.6117
7665.0938 | 123.23 | -61.4319 | 61.7111 | -0.62443 | -0.78687 | -0.69421 | -0.44624 | -0.39864 | -0.5325 | -0.96462 | 61.7248 | 0.2349 | 61.6194 | -0.028522 | 0.048236 | 61.5478 | 0.012299 | 61.326 | 60.8075 | 60.645 | 60.7377 | 60.9856 | 61.0332 | 60.8994 | 60.4673 | 123.1567 | 61.6668 | 123.0513 | 61.4034 | 61.4801 | 122.9797 | 61.4442 | 122.7579 | 61.6766 | 61.7125 | 61.5712 | 61.6071
7666.0625 | 123.2941 | -61.3907 | 61.7661 | -0.83961 | -1.0112 | -0.90941 | -0.66143 | -0.61381 | -0.73395 | -1.1935 | 61.7431 | 0.23032 | 61.6561 | -0.023943 | 0.057392 | 61.5341 | 0.021456 | 61.3123 | 60.5511 | 60.3795 | 60.4813 | 60.7293 | 60.7769 | 60.6567 | 60.1972 | 123.1338 | 61.621 | 123.0467 | 61.3667 | 61.4481 | 122.9248 | 61.4121 | 122.703 | 61.6857 | 61.7217 | 61.5987 | 61.6346
7667.0781 | 123.2712 | -61.4365 | 61.6837 | -0.54202 | -0.71361 | -0.60264 | -0.37298 | -0.33913 | -0.44551 | -0.88679 | 61.7294 | 0.24405 | 61.6332 | -0.023943 | 0.048236 | 61.5478 | 0.007721 | 61.3306 | 60.8944 | 60.7229 | 60.8338 | 61.0635 | 61.0973 | 60.991 | 60.5497 | 123.1659 | 61.6805 | 123.0696 | 61.4125 | 61.4847 | 122.9843 | 61.4442 | 122.7671 | 61.6812 | 61.7217 | 61.5849 | 61.6255
7668.0625 | 123.3582 | -61.4044 | 61.6653 | -0.83503 | -0.99291 | -0.90025 | -0.65685 | -0.60923 | -0.74768 | -1.2073 | 61.7386 | 0.23032 | 61.6377 | -0.023943 | 0.043657 | 61.525 | 0.012299 | 61.3123 | 60.5694 | 60.4115 | 60.5042 | 60.7476 | 60.7952 | 60.6567 | 60.1972 | 123.143 | 61.6347 | 123.0422 | 61.3805 | 61.4481 | 122.9294 | 61.4167 | 122.7167 | 61.6949 | 61.7263 | 61.5941 | 61.6255
7669.0938 | 123.3719 | -61.4273 | 61.6241 | -0.62901 | -0.8006 | -0.69421 | -0.45082 | -0.4078 | -0.52334 | -0.99209 | 61.7248 | 0.22574 | 61.624 | -0.023943 | 0.048236 | 61.5387 | 0.012299 | 61.3169 | 60.7983 | 60.6267 | 60.7331 | 60.9765 | 61.0195 | 60.904 | 60.4352 | 123.1521 | 61.653 | 123.0513 | 61.4034 | 61.4755 | 122.966 | 61.4396 | 122.7442 | 61.6766 | 61.7125 | 61.5758 | 61.6117
7670.0625 | 123.3215 | -61.3998 | 61.6516 | -0.40466 | -0.56251 | -0.47902 | -0.21731 | -0.18348 | -0.299 | -0.7174 | 61.7157 | 0.23032 | 61.6377 | -0.028522 | 0.048236 | 61.557 | 0.012299 | 61.3352 | 60.9952 | 60.8373 | 60.9208 | 61.1825 | 61.2164 | 61.1008 | 60.6824 | 123.1155 | 61.6302 | 123.0376 | 61.3713 | 61.4481 | 122.9568 | 61.4121 | 122.735 | 61.6674 | 61.7034 | 61.5895 | 61.6255
7671.1094 | 123.2666 | -61.4639 | 61.6562 | -0.25816 | -0.41141 | -0.31877 | -0.038752 | -0.018671 | -0.11587 | -0.548 | 61.7019 | 0.2349 | 61.6057 | -0.028522 | 0.048236 | 61.5616 | 0.012299 | 61.3398 | 61.2058 | 61.0525 | 61.1452 | 61.4252 | 61.4453 | 61.3481 | 60.9159 | 123.1659 | 61.6988 | 123.0696 | 61.4354 | 61.5122 | 123.0255 | 61.4762 | 122.8037 | 61.6537 | 61.6896 | 61.5575 | 61.5934
7672.0625 | 123.3353 | -61.4319 | 61.6196 | -0.020079 | -0.16415 | -0.071521 | 0.14897 | 0.16903 | 0.039799 | -0.42897 | 61.6882 | 0.23948 | 61.5828 | -0.028522 | 0.048236 | 61.5753 | 0.012299 | 61.3581 | 61.4118 | 61.2677 | 61.3604 | 61.5809 | 61.6009 | 61.4717 | 61.0029 | 123.1201 | 61.6714 | 123.0147 | 61.4034 | 61.4801 | 123.0072 | 61.4442 | 122.79 | 61.64 | 61.6759 | 61.5346 | 61.5705
7673.0938 | 123.3398 | -61.4822 | 61.6013 | -0.44587 | -0.60829 | -0.51107 | -0.24479 | -0.20637 | -0.299 | -0.73571 | 61.7157 | 0.2349 | 61.6332 | -0.028522 | 0.048236 | 61.557 | 0.007721 | 61.3443 | 61.0364 | 60.8739 | 60.9712 | 61.2375 | 61.2759 | 61.1832 | 60.7465 | 123.1979 | 61.7171 | 123.1154 | 61.4537 | 61.5305 | 123.0392 | 61.49 | 122.8266 | 61.6674 | 61.7079 | 61.5849 | 61.6255
7674.0625 | 123.3353 | -61.4365 | 61.647 | -0.57864 | -0.73192 | -0.63927 | -0.36383 | -0.32539 | -0.43178 | -0.87763 | 61.7157 | 0.23948 | 61.6423 | -0.028522 | 0.052814 | 61.5387 | 0.007721 | 61.3306 | 60.8578 | 60.7045 | 60.7972 | 61.0726 | 61.1111 | 61.0047 | 60.5588 | 123.1521 | 61.6759 | 123.0788 | 61.4079 | 61.4893 | 122.9752 | 61.4442 | 122.7671 | 61.6628 | 61.7079 | 61.5895 | 61.6346
7675.0781 | 123.2803 | -61.4639 | 61.6104 | -0.64274 | -0.80976 | -0.71253 | -0.44166 | -0.39864 | -0.50961 | -0.9692 | 61.7248 | 0.22574 | 61.624 | -0.028522 | 0.052814 | 61.5433 | 0.012299 | 61.3215 | 60.8212 | 60.6542 | 60.7514 | 61.0223 | 61.0653 | 60.9543 | 60.4947 | 123.1887 | 61.6897 | 123.0879 | 61.4354 | 61.5167 | 123.0072 | 61.4762 | 122.7854 | 61.672 | 61.7125 | 61.5712 | 61.6117
7676.0625 | 123.3856 | -61.3678 | 61.6791 | -1.1418 | -1.2951 | -1.1979 | -0.89951 | -0.85644 | -0.95829 | -1.4499 | 61.7523 | 0.2349 | 61.6515 | -0.023943 | 0.052814 | 61.5158 | 0.007721 | 61.3031 | 60.226 | 60.0727 | 60.1699 | 60.4683 | 60.5114 | 60.4095 | 59.9179 | 123.1201 | 61.6027 | 123.0193 | 61.3439 | 61.4206 | 122.8836 | 61.3755 | 122.6709 | 61.6995 | 61.7446 | 61.5987 | 61.6438
7677.0938 | 123.2346 | -61.4182 | 61.6974 | -0.84877 | -1.0112 | -0.90941 | -0.60191 | -0.55429 | -0.61949 | -1.1569 | 61.7386 | 0.23948 | 61.6698 | -0.014785 | 0.052814 | 61.5295 | 0.007721 | 61.3077 | 60.5694 | 60.4069 | 60.5087 | 60.8162 | 60.8639 | 60.7987 | 60.2613 | 123.1567 | 61.6576 | 123.088 | 61.4034 | 61.471 | 122.9477 | 61.4259 | 122.7259 | 61.6857 | 61.7308 | 61.617 | 61.6621
7678.0625 | 123.3948 | -61.3678 | 61.6791 | -0.97238 | -1.144 | -1.0422 | -0.70721 | -0.65958 | -0.78431 | -1.2668 | 61.7431 | 0.2349 | 61.6423 | -0.023943 | 0.048236 | 61.525 | 0.016878 | 61.3031 | 60.3954 | 60.2238 | 60.3256 | 60.6606 | 60.7082 | 60.5835 | 60.101 | 123.1109 | 61.6027 | 123.0101 | 61.3439 | 61.416 | 122.8928 | 61.3847 | 122.6709 | 61.6949 | 61.7263 | 61.5941 | 61.6255
7679.0938 | 123.3032 | -61.3953 | 61.702 | -1.2517 | -1.3959 | -1.3261 | -1.0094 | -0.95715 | -1.0682 | -1.5552 | 61.7614 | 0.22574 | 61.6561 | -0.028522 | 0.048236 | 61.5066 | 0.003143 | 61.294 | 60.1436 | 59.9994 | 60.0692 | 60.3859 | 60.4381 | 60.3271 | 59.8401 | 123.1567 | 61.621 | 123.0513 | 61.3667 | 61.4435 | 122.9019 | 61.3984 | 122.6893 | 61.7132 | 61.7583 | 61.6078 | 61.6529
7680.0625 | 123.3353 | -61.409 | 61.6699 | -0.84419 | -1.0067 | -0.92314 | -0.58817 | -0.54514 | -0.65154 | -1.1249 | 61.734 | 0.23948 | 61.6606 | -0.023943 | 0.043657 | 61.525 | 0.016878 | 61.3077 | 60.5648 | 60.4023 | 60.4859 | 60.8208 | 60.8639 | 60.7575 | 60.2841 | 123.143 | 61.6485 | 123.0696 | 61.3851 | 61.4527 | 122.934 | 61.4259 | 122.7167 | 61.6903 | 61.7171 | 61.617 | 61.6438
7681.1094 | 123.4222 | -61.4227 | 61.6333 | -0.55575 | -0.70445 | -0.62553 | -0.3043 | -0.2613 | -0.3631 | -0.83643 | 61.7202 | 0.2349 | 61.6469 | -0.019364 | 0.048236 | 61.557 | 0.007721 | 61.3215 | 60.867 | 60.7183 | 60.7972 | 61.1184 | 61.1614 | 61.0596 | 60.5863 | 123.143 | 61.6576 | 123.0696 | 61.4034 | 61.471 | 122.9797 | 61.4304 | 122.7442 | 61.672 | 61.7125 | 61.5987 | 61.6392
7682.0625 | 123.3902 | -61.4136 | 61.6333 | -0.64732 | -0.80518 | -0.70337 | -0.39587 | -0.35744 | -0.47756 | -0.98293 | 61.7157 | 0.22574 | 61.6194 | -0.023943 | 0.048236 | 61.5524 | 0.012299 | 61.3215 | 60.7663 | 60.6084 | 60.7102 | 61.0177 | 61.0561 | 60.936 | 60.4306 | 123.1292 | 61.6393 | 123.033 | 61.3896 | 61.4618 | 122.966 | 61.4259 | 122.735 | 61.6674 | 61.7034 | 61.5712 | 61.6071
7683.0938 | 123.3032 | -61.4868 | 61.6241 | -0.45045 | -0.61745 | -0.51107 | -0.18069 | -0.14685 | -0.26238 | -0.74944 | 61.7157 | 0.2349 | 61.6194 | -0.028522 | 0.048236 | 61.5524 | 0.012299 | 61.3306 | 61.0364 | 60.8694 | 60.9757 | 61.3061 | 61.34 | 61.2244 | 60.7374 | 123.2025 | 61.7217 | 123.1063 | 61.4583 | 61.5351 | 123.0392 | 61.4991 | 122.8174 | 61.6674 | 61.7034 | 61.5712 | 61.6071
7684.0625 | 123.3902 | -61.3998 | 61.6333 | -0.61527 | -0.7594 | -0.68048 | -0.32262 | -0.27961 | -0.39973 | -0.88679 | 61.7202 | 0.2349 | 61.6515 | -0.023943 | 0.048236 | 61.5478 | 0.012299 | 61.3306 | 60.7846 | 60.6404 | 60.7194 | 61.0772 | 61.1202 | 61.0001 | 60.5131 | 123.1201 | 61.6347 | 123.0513 | 61.3759 | 61.4481 | 122.9477 | 61.4121 | 122.7305 | 61.672 | 61.7079 | 61.6032 | 61.6392
7685.0625 | 123.3536 | -61.4456 | 61.6379 | -0.63358 | -0.78229 | -0.69879 | -0.3684 | -0.31624 | -0.42262 | -0.87305 | 61.7202 | 0.2349 | 61.6332 | -0.023943 | 0.048236 | 61.5524 | 0.012299 | 61.326 | 60.812 | 60.6633 | 60.7468 | 61.0772 | 61.1294 | 61.023 | 60.5726 | 123.1659 | 61.6805 | 123.0788 | 61.4217 | 61.4939 | 122.998 | 61.4579 | 122.7717 | 61.672 | 61.7079 | 61.5849 | 61.6209
7686.1094 | 123.3444 | -61.4456 | 61.6425 | -0.89455 | -1.0341 | -0.95519 | -0.59275 | -0.54514 | -0.66069 | -1.1294 | 61.7294 | 0.2349 | 61.6423 | -0.023943 | 0.052814 | 61.5295 | 0.012299 | 61.3077 | 60.5511 | 60.4115 | 60.4904 | 60.8529 | 60.9005 | 60.7849 | 60.3162 | 123.175 | 61.6805 | 123.0879 | 61.4217 | 61.4984 | 122.9752 | 61.4579 | 122.7533 | 61.6766 | 61.7171 | 61.5895 | 61.63
7687.0625 | 123.3627 | -61.3998 | 61.6699 | -0.66105 | -0.81892 | -0.72168 | -0.3913 | -0.34828 | -0.4272 | -0.87763 | 61.7294 | 0.23948 | 61.6377 | -0.033101 | 0.052814 | 61.5433 | 0.012299 | 61.3169 | 60.7388 | 60.5809 | 60.6782 | 61.0085 | 61.0516 | 60.9726 | 60.5222 | 123.1292 | 61.6393 | 123.0376 | 61.3667 | 61.4527 | 122.9431 | 61.4121 | 122.7167 | 61.6766 | 61.7171 | 61.5849 | 61.6255
7688.0938 | 123.3398 | -61.4044 | 61.6562 | -0.76636 | -0.92423 | -0.83157 | -0.47371 | -0.449 | -0.52334 | -0.98751 | 61.7248 | 0.23032 | 61.6194 | -0.028522 | 0.048236 | 61.5295 | 0.012299 | 61.3123 | 60.6381 | 60.4802 | 60.5728 | 60.9307 | 60.9554 | 60.8811 | 60.4169 | 123.1292 | 61.6347 | 123.0239 | 61.3759 | 61.4527 | 122.934 | 61.4167 | 122.7167 | 61.6766 | 61.7125 | 61.5712 | 61.6071
7689.0625 | 123.349 | -61.4502 | 61.6287 | -0.85335 | -1.0158 | -0.92314 | -0.58359 | -0.53598 | -0.61949 | -1.0699 | 61.734 | 0.2349 | 61.6469 | -0.028522 | 0.034501 | 61.5295 | 0.012299 | 61.3169 | 60.5968 | 60.4344 | 60.5271 | 60.8666 | 60.9142 | 60.8307 | 60.3803 | 123.1842 | 61.6851 | 123.0971 | 61.4217 | 61.4847 | 122.9797 | 61.4625 | 122.7671 | 61.6995 | 61.7217 | 61.6124 | 61.6346
7690.0625 | 123.3902 | -61.4182 | 61.6562 | -0.97238 | -1.1349 | -1.0422 | -0.70263 | -0.65043 | -0.766 | -1.2302 | 61.7523 | 0.23032 | 61.6606 | -0.014785 | 0.048236 | 61.525 | 0.012299 | 61.2986 | 60.4458 | 60.2833 | 60.376 | 60.7155 | 60.7677 | 60.6522 | 60.188 | 123.1704 | 61.6485 | 123.0788 | 61.4034 | 61.4664 | 122.9431 | 61.4305 | 122.7167 | 61.7041 | 61.74 | 61.6124 | 61.6483
7691.1094 | 123.2712 | -61.4136 | 61.7065 | -0.68395 | -0.82808 | -0.74916 | -0.40961 | -0.37117 | -0.45009 | -0.91884 | 61.7248 | 0.2349 | 61.6194 | -0.019364 | 0.048236 | 61.5433 | 0.007721 | 61.326 | 60.7296 | 60.5855 | 60.6644 | 61.004 | 61.0424 | 60.9635 | 60.4947 | 123.1384 | 61.6485 | 123.033 | 61.3942 | 61.4618 | 122.9568 | 61.4213 | 122.7396 | 61.6766 | 61.7171 | 61.5712 | 61.6117
7692.0625 | 123.3719 | -61.3815 | 61.6882 | -0.73889 | -0.90134 | -0.8041 | -0.48287 | -0.44442 | -0.51419 | -0.97377 | 61.7294 | 0.23948 | 61.6561 | -0.023943 | 0.052814 | 61.5387 | 0.016878 | 61.3215 | 60.6426 | 60.4802 | 60.5774 | 60.8987 | 60.9371 | 60.8673 | 60.4078 | 123.1109 | 61.621 | 123.0376 | 61.3576 | 61.4343 | 122.9202 | 61.3984 | 122.703 | 61.6766 | 61.7125 | 61.6032 | 61.6392
7693.0938 | 123.2666 | -61.4319 | 61.6745 | -0.70226 | -0.85555 | -0.75831 | -0.44624 | -0.39864 | -0.48672 | -0.96004 | 61.734 | 0.23948 | 61.624 | -0.023943 | 0.048236 | 61.5387 | 0.007721 | 61.3169 | 60.7296 | 60.5763 | 60.6736 | 60.9856 | 61.0332 | 60.9452 | 60.4718 | 123.1659 | 61.6714 | 123.0559 | 61.4079 | 61.4801 | 122.9706 | 61.4396 | 122.7488 | 61.6857 | 61.7263 | 61.5758 | 61.6163
7694.0625 | 123.3765 | -61.4365 | 61.6562 | -0.73431 | -0.9105 | -0.8041 | -0.45539 | -0.4078 | -0.4684 | -0.89137 | 61.7248 | 0.23032 | 61.6194 | -0.019364 | 0.043657 | 61.5387 | 0.016878 | 61.326 | 60.7022 | 60.526 | 60.6324 | 60.9811 | 61.0287 | 60.9681 | 60.5451 | 123.1613 | 61.6668 | 123.0559 | 61.4171 | 61.4801 | 122.9752 | 61.4533 | 122.7625 | 61.6812 | 61.7079 | 61.5758 | 61.6026
7695.0938 | 123.3902 | -61.377 | 61.6379 | -0.81214 | -0.95171 | -0.87735 | -0.52865 | -0.49936 | -0.55997 | -0.9692 | 61.734 | 0.22574 | 61.6469 | -0.023943 | 0.052814 | 61.5295 | 0.012299 | 61.3169 | 60.5648 | 60.4252 | 60.4996 | 60.8483 | 60.8776 | 60.817 | 60.4078 | 123.1109 | 61.6027 | 123.0239 | 61.353 | 61.4298 | 122.9065 | 61.3893 | 122.6938 | 61.6812 | 61.7217 | 61.5941 | 61.6346
7696.0625 | 123.3765 | -61.4227 | 61.6013 | -0.62443 | -0.76855 | -0.68963 | -0.35009 | -0.3025 | -0.37226 | -0.77233 | 61.7248 | 0.23948 | 61.6515 | -0.033101 | 0.048236 | 61.5387 | 0.021456 | 61.326 | 60.7983 | 60.6542 | 60.7331 | 61.0726 | 61.1202 | 61.0505 | 60.6504 | 123.1475 | 61.6622 | 123.0742 | 61.3896 | 61.471 | 122.9614 | 61.4442 | 122.7488 | 61.6766 | 61.7034 | 61.6032 | 61.63
7697.0781 | 123.2758 | -61.4685 | 61.6608 | -0.27647 | -0.40683 | -0.33708 | -0.002124 | 0.027109 | -0.042612 | -0.42439 | 61.6928 | 0.23032 | 61.592 | -0.023943 | 0.052814 | 61.5707 | 0.007721 | 61.3398 | 61.192 | 61.0617 | 61.1314 | 61.4664 | 61.4956 | 61.4259 | 61.0441 | 123.1613 | 61.6988 | 123.0605 | 61.4446 | 61.5213 | 123.0392 | 61.4762 | 122.8083 | 61.64 | 61.685 | 61.5392 | 61.5842
7698.0625 | 123.2346 | -61.4227 | 61.7203 | -0.35888 | -0.48924 | -0.41492 | -0.10285 | -0.073606 | -0.12502 | -0.47933 | 61.7111 | 0.24405 | 61.6423 | -0.028522 | 0.048236 | 61.5616 | 0.016878 | 61.3443 | 61.0638 | 60.9335 | 61.0078 | 61.3199 | 61.3491 | 61.2977 | 60.9434 | 123.1338 | 61.6668 | 123.0651 | 61.3942 | 61.471 | 122.9843 | 61.4396 | 122.7671 | 61.6628 | 61.6942 | 61.5941 | 61.6255
7699.0938 | 123.3627 | -61.4319 | 61.647 | -0.37719 | -0.50756 | -0.43323 | -0.12116 | -0.082762 | -0.15707 | -0.50222 | 61.7111 | 0.2349 | 61.6057 | -0.023943 | 0.048236 | 61.5662 | 0.016878 | 61.3443 | 61.0547 | 60.9243 | 60.9987 | 61.3107 | 61.3491 | 61.2748 | 60.9297 | 123.143 | 61.6668 | 123.0376 | 61.4079 | 61.4801 | 122.998 | 61.4488 | 122.7762 | 61.6628 | 61.6942 | 61.5575 | 61.5888
7700.0625 | 123.2758 | -61.4548 | 61.6516 | -0.38635 | -0.51214 | -0.44697 | -0.12116 | -0.096496 | -0.14334 | -0.53427 | 61.7019 | 0.2349 | 61.6149 | -0.028522 | 0.048236 | 61.5616 | 0.012299 | 61.3443 | 61.0684 | 60.9426 | 61.0078 | 61.3336 | 61.3583 | 61.3114 | 60.9205 | 123.1567 | 61.6897 | 123.0696 | 61.4263 | 61.503 | 123.0164 | 61.4671 | 122.7991 | 61.6537 | 61.6896 | 61.5666 | 61.6026
7701.1094 | 123.2071 | -61.4594 | 61.6516 | -0.28105 | -0.39767 | -0.33708 | -0.020438 | 0.008797 | -0.065504 | -0.4656 | 61.7111 | 0.23948 | 61.6377 | -0.023943 | 0.048236 | 61.5662 | 0.012299 | 61.3443 | 61.1783 | 61.0617 | 61.1223 | 61.4389 | 61.4681 | 61.3938 | 60.9938 | 123.1704 | 61.6988 | 123.0971 | 61.4354 | 61.5076 | 123.0255 | 61.4716 | 122.8037 | 61.6628 | 61.6988 | 61.5895 | 61.6255
7702.0625 | 123.3627 | -61.4548 | 61.6287 | -0.25358 | -0.38851 | -0.31419 | -0.020438 | 0.013375 | -0.038034 | -0.36488 | 61.7019 | 0.22574 | 61.5965 | -0.033101 | 0.048236 | 61.5616 | 0.012299 | 61.3535 | 61.2012 | 61.0663 | 61.1406 | 61.4343 | 61.4681 | 61.4167 | 61.0899 | 123.1567 | 61.6805 | 123.0513 | 61.4217 | 61.503 | 123.0164 | 61.4671 | 122.8083 | 61.6537 | 61.6896 | 61.5483 | 61.5842
7703.0781 | 123.3582 | -61.4456 | 61.6333 | -0.17117 | -0.29236 | -0.22262 | 0.080288 | 0.10036 | 0.067269 | -0.30078 | 61.6882 | 0.23032 | 61.5874 | -0.033101 | 0.048236 | 61.5753 | 0.007721 | 61.3535 | 61.2745 | 61.1533 | 61.223 | 61.5259 | 61.546 | 61.5129 | 61.1448 | 123.1338 | 61.6759 | 123.033 | 61.4125 | 61.4939 | 123.0209 | 61.4533 | 122.7991 | 61.64 | 61.6805 | 61.5392 | 61.5797
7704.0625 | 123.3673 | -61.4044 | 61.6287 | -0.45045 | -0.58082 | -0.51107 | -0.21731 | -0.1789 | -0.1937 | -0.57547 | 61.7111 | 0.2349 | 61.6377 | -0.028522 | 0.043657 | 61.5616 | 0.016878 | 61.3443 | 60.954 | 60.8236 | 60.8934 | 61.1871 | 61.2255 | 61.2107 | 60.8289 | 123.1155 | 61.6393 | 123.0422 | 61.3759 | 61.4481 | 122.966 | 61.4213 | 122.7488 | 61.6674 | 61.6942 | 61.5941 | 61.6209
7705.0938 | 123.3948 | -61.4182 | 61.6653 | -0.57864 | -0.69987 | -0.64843 | -0.33636 | -0.29335 | -0.31274 | -0.68993 | 61.7202 | 0.2349 | 61.624 | -0.023943 | 0.052814 | 61.5433 | 0.007721 | 61.3306 | 60.8395 | 60.7183 | 60.7697 | 61.0818 | 61.1248 | 61.1054 | 60.7282 | 123.1384 | 61.653 | 123.0422 | 61.3942 | 61.471 | 122.9614 | 61.4259 | 122.7488 | 61.6674 | 61.7125 | 61.5712 | 61.6163
7706.0625 | 123.2437 | -61.4639 | 61.6608 | -0.070441 | -0.20536 | -0.11731 | 0.22222 | 0.26059 | 0.21836 | -0.19091 | 61.6882 | 0.23032 | 61.5782 | -0.033101 | 0.048236 | 61.5799 | 0.016878 | 61.3718 | 61.3935 | 61.2586 | 61.3466 | 61.6862 | 61.7245 | 61.6823 | 61.273 | 123.1521 | 61.6942 | 123.0422 | 61.4308 | 61.5122 | 123.0438 | 61.4808 | 122.8357 | 61.64 | 61.6713 | 61.53 | 61.5614
7707.0938 | 123.3582 | -61.4548 | 61.5829 | -0.35888 | -0.49382 | -0.4195 | -0.10743 | -0.078184 | -0.10213 | -0.4656 | 61.7111 | 0.2349 | 61.6057 | -0.019364 | 0.052814 | 61.557 | 0.012299 | 61.3352 | 61.0959 | 60.9609 | 61.0353 | 61.3473 | 61.3766 | 61.3526 | 60.9892 | 123.1659 | 61.6897 | 123.0605 | 61.4354 | 61.5076 | 123.0118 | 61.4671 | 122.79 | 61.6583 | 61.6988 | 61.5529 | 61.5934
7708.0625 | 123.349 | -61.4273 | 61.6425 | -0.28563 | -0.41141 | -0.35082 | -0.011281 | 0.013375 | -0.042612 | -0.4015 | 61.7019 | 0.23948 | 61.6332 | -0.033101 | 0.048236 | 61.5662 | 0.007721 | 61.3489 | 61.1417 | 61.0159 | 61.0765 | 61.416 | 61.4407 | 61.3847 | 61.0258 | 123.1292 | 61.6668 | 123.0605 | 61.3942 | 61.4755 | 122.9935 | 61.435 | 122.7762 | 61.6537 | 61.6942 | 61.5849 | 61.6255
7709.0781 | 123.3536 | -61.409 | 61.647 | -0.55117 | -0.68156 | -0.6118 | -0.27683 | -0.24757 | -0.31274 | -0.68077 | 61.7111 | 0.2349 | 61.6149 | -0.028522 | 0.043657 | 61.557 | 0.016878 | 61.326 | 60.8578 | 60.7274 | 60.7972 | 61.1322 | 61.1614 | 61.0963 | 60.7282 | 123.1201 | 61.6439 | 123.0239 | 61.3805 | 61.4527 | 122.966 | 61.4259 | 122.735 | 61.6674 | 61.6942 | 61.5712 | 61.598
7710.0625 | 123.3215 | -61.3998 | 61.6653 | -0.44587 | -0.5854 | -0.50191 | -0.17153 | -0.12854 | -0.1937 | -0.56632 | 61.7065 | 0.23032 | 61.6103 | -0.019364 | 0.052814 | 61.5616 | 0.003143 | 61.3443 | 60.954 | 60.8144 | 60.8979 | 61.2283 | 61.2713 | 61.2061 | 60.8335 | 123.1063 | 61.6302 | 123.0101 | 61.3805 | 61.4527 | 122.9614 | 61.403 | 122.7442 | 61.6537 | 61.7034 | 61.5575 | 61.6071
7711.1094 | 123.3948 | -61.4136 | 61.702 | -0.31767 | -0.44804 | -0.36913 | -0.057066 | -0.027827 | -0.074661 | -0.42439 | 61.7111 | 0.2349 | 61.624 | -0.028522 | 0.052814 | 61.5707 | 0.016878 | 61.3443 | 61.0959 | 60.9655 | 61.0444 | 61.3565 | 61.3857 | 61.3389 | 60.9892 | 123.1247 | 61.6485 | 123.0376 | 61.3851 | 61.4664 | 122.9843 | 61.4305 | 122.7579 | 61.6583 | 61.6942 | 61.5712 | 61.6071
7712.0625 | 123.175 | -61.4594 | 61.6882 | -0.19864 | -0.32899 | -0.25467 | 0.057396 | 0.082044 | 0.048956 | -0.30078 | 61.6882 | 0.23032 | 61.5965 | -0.028522 | 0.043657 | 61.5753 | 0.012299 | 61.3581 | 61.2607 | 61.1304 | 61.2047 | 61.5167 | 61.5414 | 61.5083 | 61.1586 | 123.1475 | 61.6897 | 123.0559 | 61.4308 | 61.503 | 123.0347 | 61.4716 | 122.8174 | 61.6445 | 61.6759 | 61.5529 | 61.5842
7713.0938 | 123.3765 | -61.4319 | 61.6425 | -0.20321 | -0.33357 | -0.25924 | 0.052818 | 0.0912 | 0.030642 | -0.30994 | 61.6973 | 0.23032 | 61.5965 | -0.023943 | 0.043657 | 61.5753 | 0.007721 | 61.3535 | 61.2287 | 61.0983 | 61.1726 | 61.4847 | 61.5231 | 61.4625 | 61.1219 | 123.1292 | 61.6622 | 123.0284 | 61.4079 | 61.4755 | 123.0072 | 61.4396 | 122.7854 | 61.6537 | 61.6896 | 61.5529 | 61.5888
7714.0625 | 123.2986 | -61.409 | 61.6928 | -0.042971 | -0.17788 | -0.10815 | 0.21307 | 0.23769 | 0.19089 | -0.1497 | 61.6882 | 0.24405 | 61.5965 | -0.023943 | 0.048236 | 61.5891 | 0.016878 | 61.3627 | 61.366 | 61.2311 | 61.3008 | 61.6221 | 61.6467 | 61.5999 | 61.2593 | 123.0972 | 61.6531 | 123.0055 | 61.3851 | 61.4572 | 122.998 | 61.4259 | 122.7717 | 61.64 | 61.6713 | 61.5483 | 61.5797
7715.0625 | 123.3032 | -61.4639 | 61.6745 | -0.39551 | -0.52587 | -0.45154 | -0.16237 | -0.12396 | -0.15249 | -0.48391 | 61.7111 | 0.2349 | 61.624 | -0.023943 | 0.043657 | 61.557 | 0.007721 | 61.3443 | 61.0684 | 60.9381 | 61.0124 | 61.3016 | 61.34 | 61.3114 | 60.98 | 123.175 | 61.6988 | 123.0879 | 61.44 | 61.5076 | 123.0209 | 61.4716 | 122.8083 | 61.6674 | 61.7034 | 61.5804 | 61.6163
7716.1094 | 123.3444 | -61.4685 | 61.6058 | -0.015501 | -0.15041 | -0.0761 | 0.25427 | 0.29263 | 0.27787 | -0.10392 | 61.6745 | 0.22574 | 61.5782 | -0.023943 | 0.043657 | 61.5799 | 0.012299 | 61.3672 | 61.453 | 61.3181 | 61.3924 | 61.7228 | 61.7611 | 61.7464 | 61.3646 | 123.143 | 61.6942 | 123.0467 | 61.4446 | 61.5122 | 123.0484 | 61.4808 | 122.8357 | 61.6308 | 61.6622 | 61.5346 | 61.5659
7717.0625 | 123.262 | -61.4456 | 61.7111 | -0.54659 | -0.68613 | -0.60264 | -0.30888 | -0.27046 | -0.30358 | -0.66704 | 61.7157 | 0.22116 | 61.624 | -0.019364 | 0.048236 | 61.557 | 0.012299 | 61.3398 | 60.899 | 60.7595 | 60.843 | 61.1367 | 61.1752 | 61.142 | 60.7786 | 123.1613 | 61.6668 | 123.0696 | 61.4263 | 61.4939 | 123.0026 | 61.4579 | 122.7854 | 61.6674 | 61.7034 | 61.5758 | 61.6117
7718.0938 | 123.3307 | -61.4273 | 61.6562 | -0.60611 | -0.74108 | -0.66674 | -0.37298 | -0.33455 | -0.37226 | -0.7174 | 61.7202 | 0.23948 | 61.6515 | -0.023943 | 0.057392 | 61.5478 | 0.016878 | 61.326 | 60.8212 | 60.6862 | 60.7606 | 61.0543 | 61.0928 | 61.0551 | 60.7099 | 123.1475 | 61.6668 | 123.0788 | 61.4034 | 61.4847 | 122.9752 | 61.4442 | 122.7533 | 61.6628 | 61.7034 | 61.5941 | 61.6346
7719.0625 | 123.2574 | -61.4227 | 61.7294 | -0.76636 | -0.9105 | -0.83157 | -0.52865 | -0.48562 | -0.50961 | -0.87305 | 61.7386 | 0.2349 | 61.6377 | -0.028522 | 0.052814 | 61.5387 | 0.016878 | 61.3306 | 60.6564 | 60.5122 | 60.5912 | 60.8941 | 60.9371 | 60.9131 | 60.5497 | 123.1613 | 61.6576 | 123.0605 | 61.3942 | 61.4755 | 122.9614 | 61.4396 | 122.7533 | 61.6857 | 61.7217 | 61.5849 | 61.6209
7720.0938 | 123.3353 | -61.3815 | 61.6882 | -1.0823 | -1.2173 | -1.1429 | -0.83999 | -0.78777 | -0.81178 | -1.1661 | 61.7431 | 0.23032 | 61.6469 | -0.028522 | 0.039079 | 61.5204 | 0.012299 | 61.3169 | 60.2993 | 60.1643 | 60.2386 | 60.5415 | 60.5938 | 60.5697 | 60.2155 | 123.1247 | 61.6118 | 123.0284 | 61.353 | 61.4206 | 122.9019 | 61.3938 | 122.6984 | 61.7041 | 61.7308 | 61.6078 | 61.6346
7721.0625 | 123.2758 | -61.4502 | 61.6516 | -0.52828 | -0.68156 | -0.59348 | -0.2631 | -0.22468 | -0.26238 | -0.64414 | 61.7202 | 0.2349 | 61.6377 | -0.033101 | 0.043657 | 61.5524 | 0.012299 | 61.3489 | 60.9219 | 60.7686 | 60.8567 | 61.1871 | 61.2255 | 61.1878 | 60.806 | 123.1704 | 61.6851 | 123.0879 | 61.4171 | 61.4939 | 123.0026 | 61.4625 | 122.7991 | 61.6766 | 61.7079 | 61.5941 | 61.6255
7722.0938 | 123.2849 | -61.3998 | 61.7294 | -1.0182 | -1.1578 | -1.0834 | -0.80794 | -0.76488 | -0.77515 | -1.1386 | 61.7477 | 0.23948 | 61.6698 | -0.023943 | 0.043657 | 61.5341 | 0.012299 | 61.3123 | 60.3817 | 60.2421 | 60.3164 | 60.5919 | 60.635 | 60.6247 | 60.2613 | 123.1476 | 61.6393 | 123.0696 | 61.3759 | 61.4435 | 122.934 | 61.4121 | 122.7121 | 61.7041 | 61.7354 | 61.6261 | 61.6575
7723.0625 | 123.2208 | -61.4182 | 61.6974 | -1.2562 | -1.3913 | -1.3123 | -1.0186 | -0.97089 | -1.0132 | -1.3858 | 61.7614 | 0.23032 | 61.6515 | -0.028522 | 0.048236 | 61.5112 | 0.012299 | 61.3031 | 60.1619 | 60.0269 | 60.1058 | 60.3996 | 60.4473 | 60.4049 | 60.0323 | 123.1796 | 61.6485 | 123.0696 | 61.3896 | 61.4664 | 122.9294 | 61.4305 | 122.7213 | 61.7132 | 61.7491 | 61.6032 | 61.6392
7724.0938 | 123.3856 | -61.4136 | 61.6745 | -0.77094 | -0.91965 | -0.84073 | -0.50118 | -0.45358 | -0.50045 | -0.88679 | 61.7248 | 0.22574 | 61.6423 | -0.033101 | 0.043657 | 61.5341 | 0.012299 | 61.3215 | 60.6426 | 60.4939 | 60.5728 | 60.9124 | 60.96 | 60.9131 | 60.5268 | 123.1384 | 61.6393 | 123.0559 | 61.3805 | 61.4572 | 122.9477 | 61.4259 | 122.735 | 61.6812 | 61.7125 | 61.5987 | 61.63
7725.0625 | 123.2758 | -61.4365 | 61.6928 | -0.61985 | -0.76397 | -0.68505 | -0.38672 | -0.34371 | -0.3631 | -0.7586 | 61.7294 | 0.24405 | 61.6469 | -0.019364 | 0.052814 | 61.5433 | 0.012299 | 61.3306 | 60.8166 | 60.6725 | 60.7514 | 61.0497 | 61.0928 | 61.0734 | 60.6779 | 123.1659 | 61.6805 | 123.0834 | 61.4171 | 61.4893 | 122.9797 | 61.4488 | 122.7671 | 61.6766 | 61.7171 | 61.5941 | 61.6346
7726.1094 | 123.3582 | -61.377 | 61.6882 | -0.83961 | -0.98376 | -0.91398 | -0.61106 | -0.56345 | -0.57828 | -0.95088 | 61.734 | 0.22574 | 61.6377 | -0.023943 | 0.052814 | 61.5341 | 0.012299 | 61.3215 | 60.5373 | 60.3932 | 60.463 | 60.7659 | 60.8135 | 60.7987 | 60.4261 | 123.1109 | 61.6027 | 123.0147 | 61.353 | 61.4298 | 122.9111 | 61.3893 | 122.6984 | 61.6812 | 61.7217 | 61.5849 | 61.6255
7727.0625 | 123.2666 | -61.4273 | 61.7111 | -0.95865 | -1.0891 | -1.0284 | -0.73011 | -0.68248 | -0.72021 | -1.0974 | 61.7431 | 0.2349 | 61.6332 | -0.019364 | 0.052814 | 61.5204 | 0.007721 | 61.3123 | 60.4687 | 60.3382 | 60.3989 | 60.6972 | 60.7448 | 60.7071 | 60.3299 | 123.1704 | 61.6622 | 123.0605 | 61.4079 | 61.4801 | 122.9477 | 61.435 | 122.7396 | 61.6903 | 61.7354 | 61.5804 | 61.6255
7728.0938 | 123.3765 | -61.4227 | 61.6516 | -0.79383 | -0.93797 | -0.85446 | -0.55154 | -0.50393 | -0.5325 | -0.91884 | 61.7294 | 0.23032 | 61.6332 | -0.028522 | 0.052814 | 61.5341 | 0.012299 | 61.3215 | 60.6289 | 60.4848 | 60.5683 | 60.8712 | 60.9188 | 60.8902 | 60.5039 | 123.1521 | 61.653 | 123.0559 | 61.3942 | 61.4755 | 122.9568 | 61.435 | 122.7442 | 61.6766 | 61.7171 | 61.5804 | 61.6209
7729.0625 | 123.3719 | -61.3678 | 61.6882 | -0.99985 | -1.1394 | -1.0697 | -0.77131 | -0.72368 | -0.73853 | -1.0974 | 61.7569 | 0.23948 | 61.6744 | -0.023943 | 0.043657 | 61.5295 | 0.012299 | 61.3123 | 60.3679 | 60.2284 | 60.2981 | 60.5965 | 60.6441 | 60.6293 | 60.2704 | 123.1247 | 61.6073 | 123.0422 | 61.3439 | 61.4115 | 122.8973 | 61.3801 | 122.6801 | 61.7132 | 61.7446 | 61.6307 | 61.6621
7730.0781 | 123.3627 | -61.4365 | 61.6425 | -0.68395 | -0.81434 | -0.74916 | -0.43708 | -0.39864 | -0.40431 | -0.77691 | 61.7202 | 0.2349 | 61.624 | -0.028522 | 0.048236 | 61.5524 | 0.007721 | 61.326 | 60.7525 | 60.6221 | 60.6873 | 60.9994 | 61.0378 | 61.0322 | 60.6595 | 123.1567 | 61.6714 | 123.0605 | 61.4079 | 61.4847 | 122.9889 | 61.4442 | 122.7625 | 61.672 | 61.7125 | 61.5758 | 61.6163
7731.0625 | 123.2666 | -61.4456 | 61.6928 | -0.64732 | -0.78229 | -0.70337 | -0.40503 | -0.37575 | -0.37226 | -0.76318 | 61.7202 | 0.2349 | 61.6194 | -0.028522 | 0.052814 | 61.5478 | 0.012299 | 61.3352 | 60.7983 | 60.6633 | 60.7422 | 61.0406 | 61.0699 | 61.0734 | 60.6824 | 123.1659 | 61.6805 | 123.0651 | 61.4171 | 61.4984 | 122.9935 | 61.4579 | 122.7808 | 61.6674 | 61.7079 | 61.5666 | 61.6071
7732.0938 | 123.3215 | -61.4594 | 61.6379 | -0.44129 | -0.58082 | -0.49733 | -0.18526 | -0.14228 | -0.17081 | -0.52053 | 61.7157 | 0.23948 | 61.6332 | -0.028522 | 0.048236 | 61.5616 | 0.016878 | 61.3443 | 61.0181 | 60.8785 | 60.962 | 61.2741 | 61.3171 | 61.2885 | 60.9388 | 123.175 | 61.6988 | 123.0925 | 61.4308 | 61.5076 | 123.0209 | 61.4762 | 122.8037 | 61.6674 | 61.6988 | 61.5849 | 61.6163
7733.0625 | 123.2391 | -61.4136 | 61.6791 | -0.66563 | -0.8006 | -0.72626 | -0.43708 | -0.38949 | -0.40888 | -0.78607 | 61.734 | 0.23948 | 61.6423 | -0.033101 | 0.043657 | 61.5433 | 0.012299 | 61.3169 | 60.7479 | 60.613 | 60.6873 | 60.9765 | 61.0241 | 61.0047 | 60.6275 | 123.1475 | 61.6531 | 123.0559 | 61.3805 | 61.4572 | 122.9568 | 61.4259 | 122.7305 | 61.6903 | 61.7217 | 61.5987 | 61.63
7734.0781 | 123.3398 | -61.4685 | 61.6196 | -0.27189 | -0.39767 | -0.31877 | -0.002124 | 0.031687 | -0.01972 | -0.39235 | 61.6973 | 0.23032 | 61.592 | -0.028522 | 0.043657 | 61.5662 | 0.003143 | 61.3443 | 61.1966 | 61.0708 | 61.1497 | 61.4664 | 61.5002 | 61.4488 | 61.0762 | 123.1659 | 61.6988 | 123.0605 | 61.44 | 61.5122 | 123.0347 | 61.4716 | 122.8129 | 61.6537 | 61.6942 | 61.5483 | 61.5888
7735.0625 | 123.2162 | -61.4227 | 61.702 | -0.74804 | -0.89218 | -0.81325 | -0.51492 | -0.47189 | -0.49587 | -0.85474 | 61.7248 | 0.2349 | 61.6286 | -0.019364 | 0.048236 | 61.5387 | 0.007721 | 61.3215 | 60.6747 | 60.5305 | 60.6095 | 60.9078 | 60.9508 | 60.9269 | 60.568 | 123.1475 | 61.6576 | 123.0513 | 61.4034 | 61.471 | 122.9614 | 61.4304 | 122.7442 | 61.6766 | 61.7171 | 61.5804 | 61.6209
7736.1094 | 123.3398 | -61.4502 | 61.647 | -0.35888 | -0.48467 | -0.41034 | -0.093694 | -0.059872 | -0.083817 | -0.43355 | 61.7111 | 0.23948 | 61.6377 | -0.019364 | 0.048236 | 61.5616 | 0.021456 | 61.3489 | 61.0913 | 60.9655 | 61.0399 | 61.3565 | 61.3903 | 61.3664 | 61.0166 | 123.1613 | 61.6897 | 123.0879 | 61.4308 | 61.4984 | 123.0118 | 61.4717 | 122.7991 | 61.6628 | 61.6896 | 61.5895 | 61.6163
7737.0625 | 123.2803 | -61.3815 | 61.7432 | -0.73889 | -0.87387 | -0.79952 | -0.49202 | -0.45815 | -0.47298 | -0.81354 | 61.7294 | 0.23032 | 61.6332 | -0.019364 | 0.052814 | 61.5341 | 0.007721 | 61.3215 | 60.6426 | 60.5077 | 60.582 | 60.8895 | 60.9234 | 60.9086 | 60.568 | 123.1109 | 61.6118 | 123.0147 | 61.3622 | 61.4343 | 122.9156 | 61.3893 | 122.703 | 61.6766 | 61.7217 | 61.5804 | 61.6255
7738.0781 | 123.349 | -61.4136 | 61.6608 | -0.67937 | -0.82808 | -0.75373 | -0.45082 | -0.41237 | -0.42262 | -0.76318 | 61.7202 | 0.2349 | 61.6194 | -0.019364 | 0.043657 | 61.5478 | 0.012299 | 61.3215 | 60.7342 | 60.5855 | 60.6598 | 60.9628 | 61.0012 | 60.991 | 60.6504 | 123.1338 | 61.6485 | 123.033 | 61.3942 | 61.4572 | 122.9614 | 61.4259 | 122.735 | 61.6766 | 61.7079 | 61.5758 | 61.6071
7739.0625 | 123.3261 | -61.4136 | 61.7157 | -1.0731 | -1.2081 | -1.1338 | -0.82625 | -0.77403 | -0.81178 | -1.1569 | 61.7477 | 0.2349 | 61.6561 | -0.028522 | 0.057392 | 61.5204 | 0.007721 | 61.3031 | 60.3405 | 60.2055 | 60.2798 | 60.5873 | 60.6395 | 60.6018 | 60.2567 | 123.1613 | 61.6485 | 123.0696 | 61.3851 | 61.471 | 122.934 | 61.4213 | 122.7167 | 61.6903 | 61.74 | 61.5987 | 61.6483
7740.0938 | 123.3948 | -61.409 | 61.6562 | -0.53744 | -0.67698 | -0.59348 | -0.2631 | -0.22468 | -0.26695 | -0.62125 | 61.7157 | 0.2349 | 61.6423 | -0.014785 | 0.052814 | 61.5478 | 0.012299 | 61.3306 | 60.8716 | 60.732 | 60.8155 | 61.1459 | 61.1843 | 61.142 | 60.7877 | 123.1247 | 61.6439 | 123.0513 | 61.3942 | 61.4618 | 122.9568 | 61.4213 | 122.7396 | 61.6628 | 61.7034 | 61.5895 | 61.63
7741.0625 | 123.2162 | -61.4365 | 61.702 | -0.59696 | -0.72734 | -0.64843 | -0.33178 | -0.29335 | -0.31732 | -0.67161 | 61.7111 | 0.23032 | 61.624 | -0.033101 | 0.043657 | 61.5524 | 0.012299 | 61.3306 | 60.8395 | 60.7091 | 60.788 | 61.1047 | 61.1431 | 61.1191 | 60.7648 | 123.1475 | 61.6668 | 123.0605 | 61.4034 | 61.4801 | 122.9889 | 61.4488 | 122.7671 | 61.6674 | 61.6988 | 61.5804 | 61.6117
7742.0938 | 123.3078 | -61.4136 | 61.6928 | -0.5237 | -0.65408 | -0.57975 | -0.27683 | -0.23383 | -0.22575 | -0.58005 | 61.7111 | 0.23032 | 61.6149 | -0.028522 | 0.048236 | 61.5616 | 0.012299 | 61.3398 | 60.8899 | 60.7595 | 60.8338 | 61.1367 | 61.1797 | 61.1878 | 60.8335 | 123.1247 | 61.6439 | 123.0284 | 61.3851 | 61.4618 | 122.9752 | 61.4259 | 122.7533 | 61.6628 | 61.6988 | 61.5666 | 61.6026
7743.0625 | 123.2712 | -61.4639 | 61.6837 | -0.74346 | -0.86929 | -0.79494 | -0.47371 | -0.42611 | -0.44551 | -0.79522 | 61.7294 | 0.2349 | 61.6606 | -0.028522 | 0.052814 | 61.5341 | 0.012299 | 61.3215 | 60.7205 | 60.5946 | 60.669 | 60.9902 | 61.0378 | 61.0184 | 60.6687 | 123.1933 | 61.6988 | 123.1246 | 61.4354 | 61.5167 | 122.998 | 61.4762 | 122.7854 | 61.6766 | 61.7171 | 61.6078 | 61.6483
7744.0938 | 123.4177 | -61.4822 | 61.5921 | -0.34514 | -0.48924 | -0.40576 | -0.10743 | -0.059872 | -0.024298 | -0.45186 | 61.6973 | 0.24405 | 61.6194 | -0.028522 | 0.043657 | 61.557 | 0.012299 | 61.3398 | 61.1371 | 60.993 | 61.0765 | 61.3748 | 61.4224 | 61.4579 | 61.0304 | 123.1796 | 61.7263 | 123.1017 | 61.4537 | 61.5259 | 123.0392 | 61.4945 | 122.822 | 61.6537 | 61.685 | 61.5758 | 61.6071
7745.0625 | 123.2574 | -61.4044 | 61.7249 | -0.3543 | -0.47093 | -0.41492 | -0.12116 | -0.08734 | -0.088396 | -0.42897 | 61.7019 | 0.23032 | 61.6103 | -0.023943 | 0.048236 | 61.5616 | 0.016878 | 61.3443 | 61.0501 | 60.9335 | 60.9895 | 61.2833 | 61.3171 | 61.316 | 60.9754 | 123.1063 | 61.6347 | 123.0147 | 61.3805 | 61.4527 | 122.966 | 61.4213 | 122.7488 | 61.6537 | 61.685 | 61.562 | 61.5934
7746.0938 | 123.2437 | -61.4548 | 61.6882 | -0.66563 | -0.79145 | -0.73542 | -0.45539 | -0.41695 | -0.41346 | -0.75402 | 61.7248 | 0.23948 | 61.6332 | -0.023943 | 0.048236 | 61.5478 | 0.007721 | 61.3306 | 60.7891 | 60.6633 | 60.7194 | 60.9994 | 61.0378 | 61.0413 | 60.7008 | 123.1796 | 61.6942 | 123.0879 | 61.4308 | 61.503 | 123.0026 | 61.4625 | 122.7854 | 61.6766 | 61.7171 | 61.5849 | 61.6255
7747.0625 | 123.3261 | -61.4182 | 61.6196 | -0.53286 | -0.65866 | -0.59806 | -0.31804 | -0.27504 | -0.2578 | -0.60752 | 61.7111 | 0.24405 | 61.6332 | -0.028522 | 0.048236 | 61.557 | 0.016878 | 61.326 | 60.8853 | 60.7595 | 60.8201 | 61.1001 | 61.1431 | 61.1604 | 60.8106 | 123.1292 | 61.6622 | 123.0513 | 61.3896 | 61.4664 | 122.9752 | 61.435 | 122.7442 | 61.6628 | 61.6942 | 61.5849 | 61.6163
7748.0781 | 123.3673 | -61.4273 | 61.6287 | -0.78467 | -0.9105 | -0.84988 | -0.5607 | -0.51767 | -0.51419 | -0.86848 | 61.734 | 0.23032 | 61.6286 | -0.023943 | 0.048236 | 61.5341 | 0.012299 | 61.3169 | 60.6426 | 60.5168 | 60.5774 | 60.8666 | 60.9096 | 60.9131 | 60.5588 | 123.1613 | 61.6576 | 123.0559 | 61.4034 | 61.4755 | 122.9614 | 61.4396 | 122.7442 | 61.6857 | 61.7217 | 61.5804 | 61.6163
7749.0625 | 123.3673 | -61.409 | 61.6562 | -0.37261 | -0.50298 | -0.42865 | -0.16237 | -0.11939 | -0.083817 | -0.46102 | 61.7065 | 0.22574 | 61.6011 | -0.019364 | 0.052814 | 61.5616 | 0.007721 | 61.3398 | 61.0364 | 60.906 | 60.9803 | 61.2466 | 61.2896 | 61.3252 | 60.948 | 123.1155 | 61.6347 | 123.0101 | 61.3896 | 61.4618 | 122.9706 | 61.4167 | 122.7488 | 61.6537 | 61.6988 | 61.5483 | 61.5934
7750.0781 | 123.3627 | -61.4182 | 61.6241 | -0.42756 | -0.53961 | -0.4836 | -0.21274 | -0.18805 | -0.14334 | -0.49764 | 61.7065 | 0.2349 | 61.6194 | -0.023943 | 0.048236 | 61.5616 | 0.012299 | 61.3443 | 60.9906 | 60.8785 | 60.9346 | 61.2054 | 61.2301 | 61.2748 | 60.9205 | 123.1247 | 61.653 | 123.0376 | 61.3942 | 61.4664 | 122.9797 | 61.4305 | 122.7625 | 61.6583 | 61.6942 | 61.5712 | 61.6071
7751.0625 | 123.2483 | -61.4136 | 61.7111 | -0.60153 | -0.72734 | -0.6759 | -0.3913 | -0.35286 | -0.34021 | -0.68535 | 61.7248 | 0.2349 | 61.6423 | -0.028522 | 0.052814 | 61.5478 | 0.016878 | 61.3398 | 60.812 | 60.6862 | 60.7377 | 61.0223 | 61.0607 | 61.0734 | 60.7282 | 123.1384 | 61.6485 | 123.0559 | 61.3851 | 61.4664 | 122.9614 | 61.4305 | 122.7533 | 61.672 | 61.7079 | 61.5895 | 61.6255
7752.0938 | 123.3398 | -61.4639 | 61.6516 | -0.41382 | -0.52587 | -0.46528 | -0.17153 | -0.15143 | -0.074661 | -0.48391 | 61.7019 | 0.23032 | 61.6057 | -0.028522 | 0.052814 | 61.5524 | 0.012299 | 61.3443 | 61.0501 | 60.9381 | 60.9986 | 61.2924 | 61.3125 | 61.3893 | 60.98 | 123.1659 | 61.6942 | 123.0696 | 61.4354 | 61.5167 | 123.0164 | 61.4762 | 122.8083 | 61.6491 | 61.6896 | 61.5529 | 61.5934
7753.0625 | 123.2529 | -61.4136 | 61.6882 | -0.56491 | -0.69529 | -0.62553 | -0.33178 | -0.3025 | -0.22117 | -0.6533 | 61.7157 | 0.23032 | 61.624 | -0.023943 | 0.052814 | 61.5433 | 0.012299 | 61.3352 | 60.8487 | 60.7183 | 60.788 | 61.0818 | 61.1111 | 61.1924 | 60.7603 | 123.1292 | 61.6439 | 123.0376 | 61.3896 | 61.4664 | 122.9568 | 61.4259 | 122.7488 | 61.6628 | 61.7034 | 61.5712 | 61.6117
7754.0781 | 123.3673 | -61.4182 | 61.647 | -0.67937 | -0.79145 | -0.74 | -0.42792 | -0.38033 | -0.35852 | -0.74486 | 61.7157 | 0.23032 | 61.6332 | -0.033101 | 0.052814 | 61.5433 | 0.007721 | 61.3215 | 60.7388 | 60.6267 | 60.6782 | 60.9902 | 61.0378 | 61.0596 | 60.6733 | 123.1338 | 61.6485 | 123.0513 | 61.3851 | 61.471 | 122.9614 | 61.4259 | 122.7396 | 61.6628 | 61.7079 | 61.5804 | 61.6255
7755.0625 | 123.3627 | -61.3907 | 61.6699 | -0.72057 | -0.83723 | -0.78121 | -0.46913 | -0.42153 | -0.39973 | -0.77691 | 61.7248 | 0.23032 | 61.6286 | -0.023943 | 0.057392 | 61.5433 | 0.003143 | 61.326 | 60.6701 | 60.5535 | 60.6095 | 60.9216 | 60.9692 | 60.991 | 60.6138 | 123.1155 | 61.621 | 123.0193 | 61.3667 | 61.4481 | 122.934 | 61.3938 | 122.7167 | 61.6674 | 61.7217 | 61.5712 | 61.6255
7756.0938 | 123.2483 | -61.4594 | 61.6882 | -1.0136 | -1.1303 | -1.0742 | -0.78047 | -0.74199 | -0.72021 | -1.0745 | 61.7477 | 0.2349 | 61.6377 | -0.019364 | 0.057392 | 61.5204 | 0.007721 | 61.3077 | 60.4458 | 60.3291 | 60.3851 | 60.6789 | 60.7174 | 60.7391 | 60.3849 | 123.2071 | 61.6942 | 123.0971 | 61.44 | 61.5167 | 122.9797 | 61.4671 | 122.7671 | 61.6903 | 61.74 | 61.5804 | 61.63
7757.0625 | 123.2666 | -61.4182 | 61.7157 | -0.75262 | -0.87387 | -0.81783 | -0.51492 | -0.47647 | -0.41804 | -0.80438 | 61.7294 | 0.2349 | 61.6652 | -0.019364 | 0.048236 | 61.5341 | 0.012299 | 61.3215 | 60.6655 | 60.5443 | 60.6003 | 60.9032 | 60.9417 | 61.0001 | 60.6138 | 123.1475 | 61.653 | 123.0834 | 61.3988 | 61.4664 | 122.9523 | 61.4305 | 122.7396 | 61.6812 | 61.7171 | 61.617 | 61.6529
7758.0938 | 123.3398 | -61.4136 | 61.6745 | -1.1326 | -1.2493 | -1.1979 | -0.89951 | -0.85186 | -0.82552 | -1.1844 | 61.7523 | 0.2349 | 61.6423 | -0.023943 | 0.039079 | 61.5112 | 0.016878 | 61.2986 | 60.2809 | 60.1642 | 60.2157 | 60.5141 | 60.5617 | 60.5881 | 60.2292 | 123.1659 | 61.6485 | 123.0559 | 61.3896 | 61.4527 | 122.9248 | 61.4305 | 122.7121 | 61.7132 | 61.7354 | 61.6032 | 61.6255
7759.0625 | 123.3948 | -61.3907 | 61.6653 | -0.83045 | -0.94713 | -0.90483 | -0.6248 | -0.58176 | -0.54624 | -0.88221 | 61.7248 | 0.22574 | 61.6423 | -0.023943 | 0.052814 | 61.5295 | 0.021456 | 61.3123 | 60.5602 | 60.4436 | 60.4859 | 60.7659 | 60.8089 | 60.8445 | 60.5085 | 123.1155 | 61.6164 | 123.033 | 61.3667 | 61.4435 | 122.9202 | 61.4121 | 122.703 | 61.672 | 61.7034 | 61.5895 | 61.6209
7760.0625 | 123.349 | -61.4136 | 61.6562 | -0.33141 | -0.4343 | -0.38287 | -0.10743 | -0.08734 | -0.060926 | -0.36945 | 61.7019 | 0.23948 | 61.6057 | -0.028522 | 0.057392 | 61.5616 | 0.007721 | 61.3443 | 61.0822 | 60.9793 | 61.0307 | 61.3061 | 61.3262 | 61.3526 | 61.0441 | 123.1155 | 61.6531 | 123.0193 | 61.3851 | 61.471 | 122.9752 | 61.4213 | 122.7579 | 61.6445 | 61.6942 | 61.5483 | 61.598
7761.0625 | 123.2437 | -61.4594 | 61.6562 | -0.54659 | -0.6724 | -0.6118 | -0.35925 | -0.32082 | -0.25322 | -0.59836 | 61.7111 | 0.23032 | 61.6103 | -0.033101 | 0.048236 | 61.5478 | 0.016878 | 61.326 | 60.9128 | 60.787 | 60.8476 | 61.1001 | 61.1385 | 61.2061 | 60.861 | 123.1704 | 61.6897 | 123.0696 | 61.4262 | 61.5076 | 123.0072 | 61.4762 | 122.7854 | 61.6628 | 61.6942 | 61.562 | 61.5934
7762.0938 | 123.2986 | -61.4182 | 61.6516 | -0.72515 | -0.84639 | -0.78578 | -0.52865 | -0.4902 | -0.43178 | -0.78149 | 61.7386 | 0.2349 | 61.6561 | -0.023943 | 0.043657 | 61.5341 | 0.012299 | 61.3215 | 60.693 | 60.5718 | 60.6324 | 60.8895 | 60.928 | 60.9864 | 60.6367 | 123.1567 | 61.653 | 123.0742 | 61.3942 | 61.4618 | 122.9523 | 61.4305 | 122.7396 | 61.6949 | 61.7263 | 61.6124 | 61.6438
7763.0625 | 123.3444 | -61.4044 | 61.6699 | -0.62443 | -0.74108 | -0.68048 | -0.43708 | -0.38949 | -0.33563 | -0.66246 | 61.7202 | 0.22574 | 61.624 | -0.028522 | 0.048236 | 61.5387 | 0.021456 | 61.3306 | 60.78 | 60.6633 | 60.7239 | 60.9673 | 61.0149 | 61.0688 | 60.742 | 123.1247 | 61.6302 | 123.0284 | 61.3759 | 61.4527 | 122.9431 | 61.4259 | 122.735 | 61.672 | 61.6988 | 61.5758 | 61.6026
7764.0938 | 123.3948 | -61.4044 | 61.6425 | -0.45503 | -0.56251 | -0.50649 | -0.2631 | -0.2201 | -0.15707 | -0.48849 | 61.6973 | 0.23032 | 61.6149 | -0.033101 | 0.052814 | 61.5524 | 0.012299 | 61.3398 | 60.9494 | 60.8419 | 60.8979 | 61.1413 | 61.1843 | 61.2473 | 60.9159 | 123.1018 | 61.6347 | 123.0193 | 61.3713 | 61.4572 | 122.9568 | 61.4167 | 122.7442 | 61.6445 | 61.685 | 61.562 | 61.6026
7765.0625 | 123.3307 | -61.4502 | 61.6608 | -0.29478 | -0.39767 | -0.33708 | -0.098273 | -0.069028 | 0.026064 | -0.3191 | 61.7019 | 0.2349 | 61.6332 | -0.019364 | 0.048236 | 61.5616 | 0.012299 | 61.3535 | 61.1554 | 61.0525 | 61.1131 | 61.3519 | 61.3812 | 61.4763 | 61.1311 | 123.1521 | 61.6851 | 123.0834 | 61.4308 | 61.4984 | 123.0118 | 61.4625 | 122.8037 | 61.6537 | 61.6896 | 61.5849 | 61.6209
7766.1094 | 123.3536 | -61.441 | 61.6379 | -0.63816 | -0.77771 | -0.69879 | -0.46913 | -0.42153 | -0.35394 | -0.70824 | 61.7157 | 0.2349 | 61.6194 | -0.028522 | 0.048236 | 61.5478 | 0.003143 | 61.3123 | 60.8029 | 60.6633 | 60.7422 | 60.9719 | 61.0195 | 61.0871 | 60.7328 | 123.1567 | 61.6759 | 123.0605 | 61.4125 | 61.4893 | 122.9889 | 61.4442 | 122.7533 | 61.6674 | 61.7125 | 61.5712 | 61.6163
7767.0625 | 123.4039 | -61.4044 | 61.6379 | -0.21237 | -0.31983 | -0.26382 | -0.011281 | 0.008797 | 0.09474 | -0.26416 | 61.6882 | 0.22574 | 61.5782 | -0.023943 | 0.048236 | 61.5662 | 0.007721 | 61.3535 | 61.192 | 61.0846 | 61.1406 | 61.3931 | 61.4132 | 61.4992 | 61.1403 | 123.0926 | 61.6302 | 122.9827 | 61.3805 | 61.4527 | 122.9706 | 61.4121 | 122.7579 | 61.64 | 61.6805 | 61.53 | 61.5705
7768.0938 | 123.3719 | -61.4365 | 61.6425 | -0.33141 | -0.4343 | -0.39202 | -0.13032 | -0.10565 | -0.042612 | -0.3603 | 61.7019 | 0.23948 | 61.6103 | -0.023943 | 0.052814 | 61.5707 | 0.007721 | 61.3352 | 61.1051 | 61.0022 | 61.0444 | 61.3061 | 61.3308 | 61.3939 | 61.0762 | 123.1384 | 61.6759 | 123.0467 | 61.4125 | 61.4893 | 123.0072 | 61.4442 | 122.7717 | 61.6491 | 61.6942 | 61.5575 | 61.6026
7769.0625 | 123.3444 | -61.3907 | 61.647 | -0.40924 | -0.52587 | -0.46528 | -0.21274 | -0.17432 | -0.092974 | -0.44271 | 61.7019 | 0.2349 | 61.624 | -0.019364 | 0.048236 | 61.5524 | 0.012299 | 61.3398 | 60.9814 | 60.8648 | 60.9254 | 61.178 | 61.2164 | 61.2977 | 60.948 | 123.0926 | 61.6256 | 123.0147 | 61.3713 | 61.4389 | 122.9431 | 61.403 | 122.7305 | 61.6537 | 61.6896 | 61.5758 | 61.6117
7770.0781 | 123.4085 | -61.4044 | 61.6379 | -0.57864 | -0.69529 | -0.63469 | -0.38214 | -0.34828 | -0.26695 | -0.6121 | 61.7157 | 0.22574 | 61.6194 | -0.028522 | 0.043657 | 61.5478 | 0.007721 | 61.326 | 60.8258 | 60.7091 | 60.7697 | 61.0223 | 61.0561 | 61.1375 | 60.7923 | 123.1201 | 61.6302 | 123.0239 | 61.3759 | 61.4481 | 122.9523 | 61.4121 | 122.7305 | 61.672 | 61.7079 | 61.5758 | 61.6117
7771.0625 | 123.3032 | -61.4456 | 61.6745 | -0.72973 | -0.85555 | -0.79952 | -0.54697 | -0.49936 | -0.39057 | -0.77233 | 61.7294 | 0.2349 | 61.6332 | -0.028522 | 0.048236 | 61.5341 | 0.012299 | 61.3306 | 60.7159 | 60.5901 | 60.6461 | 60.8987 | 60.9463 | 61.055 | 60.6733 | 123.175 | 61.6805 | 123.0788 | 61.4171 | 61.4939 | 122.9797 | 61.4579 | 122.7762 | 61.6812 | 61.7171 | 61.5849 | 61.6209
7772.0938 | 123.3719 | -61.3724 | 61.6653 | -0.85792 | -0.9746 | -0.92314 | -0.66143 | -0.61838 | -0.56455 | -0.89594 | 61.7386 | 0.24405 | 61.6606 | -0.019364 | 0.043657 | 61.5295 | 0.007721 | 61.3031 | 60.5145 | 60.3978 | 60.4492 | 60.7109 | 60.754 | 60.8078 | 60.4764 | 123.1109 | 61.6164 | 123.033 | 61.353 | 61.416 | 122.9019 | 61.3801 | 122.6755 | 61.6949 | 61.7308 | 61.617 | 61.6529
7773.0625 | 123.3444 | -61.3907 | 61.7111 | -0.9266 | -1.0524 | -0.99182 | -0.74384 | -0.68705 | -0.64238 | -0.9692 | 61.7386 | 0.2349 | 61.6561 | -0.033101 | 0.057392 | 61.525 | 0.012299 | 61.3031 | 60.4641 | 60.3382 | 60.3989 | 60.6468 | 60.7036 | 60.7483 | 60.4215 | 123.1292 | 61.6256 | 123.0467 | 61.3576 | 61.4481 | 122.9156 | 61.403 | 122.6938 | 61.6812 | 61.7263 | 61.5987 | 61.6438
7774.0938 | 123.3398 | -61.3998 | 61.6745 | -1.1784 | -1.286 | -1.2345 | -1.0094 | -0.96173 | -0.88046 | -1.2118 | 61.7477 | 0.2349 | 61.6561 | -0.023943 | 0.052814 | 61.5112 | 0.007721 | 61.2848 | 60.2214 | 60.1139 | 60.1654 | 60.3904 | 60.4381 | 60.5194 | 60.188 | 123.1476 | 61.6347 | 123.0559 | 61.3759 | 61.4527 | 122.9111 | 61.4076 | 122.6847 | 61.6949 | 61.74 | 61.6032 | 61.6483
7775.0625 | 123.3398 | -61.3586 | 61.7111 | -1.1418 | -1.2585 | -1.1979 | -0.94529 | -0.89306 | -0.84841 | -1.1661 | 61.7431 | 0.22574 | 61.6469 | -0.023943 | 0.052814 | 61.5204 | 0.016878 | 61.2986 | 60.2169 | 60.1002 | 60.1608 | 60.4133 | 60.4656 | 60.5102 | 60.1926 | 123.1018 | 61.5844 | 123.0055 | 61.3347 | 61.4115 | 122.879 | 61.3755 | 122.6572 | 61.6903 | 61.7263 | 61.5941 | 61.63
7776.0625 | 123.2025 | -61.4044 | 61.6791 | -0.67479 | -0.8006 | -0.74 | -0.4966 | -0.449 | -0.34021 | -0.70366 | 61.7248 | 0.2349 | 61.6286 | -0.023943 | 0.052814 | 61.5387 | 0.012299 | 61.3215 | 60.7296 | 60.6038 | 60.6644 | 60.9078 | 60.9554 | 61.0642 | 60.7008 | 123.1292 | 61.6393 | 123.033 | 61.3805 | 61.4572 | 122.9431 | 61.4167 | 122.7259 | 61.672 | 61.7125 | 61.5758 | 61.6163
7777.0625 | 123.3902 | -61.3541 | 61.7294 | -1.3844 | -1.4966 | -1.4451 | -1.2108 | -1.1632 | -1.0636 | -1.4133 | 61.766 | 0.23948 | 61.6927 | -0.023943 | 0.048236 | 61.4975 | 0.016878 | 61.2894 | 59.9696 | 59.8575 | 59.909 | 60.1432 | 60.1909 | 60.2905 | 59.9408 | 123.1201 | 61.5935 | 123.0468 | 61.3301 | 61.4023 | 122.8516 | 61.3709 | 122.6435 | 61.7178 | 61.7491 | 61.6445 | 61.6758
7778.0938 | 123.3948 | -61.3129 | 61.7065 | -1.6225 | -1.7301 | -1.6832 | -1.4169 | -1.3783 | -1.3017 | -1.633 | 61.7798 | 0.23032 | 61.679 | -0.023943 | 0.048236 | 61.4929 | 0.016878 | 61.2711 | 59.6904 | 59.5828 | 59.6297 | 59.896 | 59.9345 | 60.0112 | 59.6798 | 123.0926 | 61.5432 | 122.9918 | 61.2889 | 61.3611 | 122.8058 | 61.3297 | 122.584 | 61.7315 | 61.7629 | 61.6307 | 61.6621
7779.0625 | 123.4039 | -61.3724 | 61.6974 | -1.2242 | -1.3317 | -1.2894 | -1.046 | -0.99835 | -0.92166 | -1.2485 | 61.7523 | 0.23032 | 61.6561 | -0.023943 | 0.048236 | 61.5112 | 0.012299 | 61.2894 | 60.1482 | 60.0406 | 60.0829 | 60.3264 | 60.374 | 60.4507 | 60.1239 | 123.1247 | 61.6027 | 123.0284 | 61.3484 | 61.4206 | 122.8836 | 61.3847 | 122.6618 | 61.7041 | 61.74 | 61.6078 | 61.6438
7780.0781 | 123.3261 | -61.409 | 61.6562 | -1.2654 | -1.373 | -1.3215 | -1.0781 | -1.0258 | -0.94913 | -1.2805 | 61.7523 | 0.23948 | 61.6606 | -0.033101 | 0.034501 | 61.5158 | 0.012299 | 61.2894 | 60.1436 | 60.036 | 60.0875 | 60.3309 | 60.3832 | 60.4599 | 60.1285 | 123.1613 | 61.6485 | 123.0696 | 61.3759 | 61.4435 | 122.9248 | 61.4213 | 122.6984 | 61.7178 | 61.74 | 61.6261 | 61.6483
7781.0625 | 123.2437 | -61.4182 | 61.6882 | -1.0273 | -1.1394 | -1.0834 | -0.83541 | -0.79692 | -0.69274 | -1.0562 | 61.7477 | 0.2349 | 61.6606 | -0.033101 | 0.048236 | 61.5158 | 0.007721 | 61.3077 | 60.3908 | 60.2787 | 60.3348 | 60.5827 | 60.6212 | 60.7254 | 60.362 | 123.1659 | 61.653 | 123.0788 | 61.3851 | 61.4664 | 122.934 | 61.4259 | 122.7259 | 61.6995 | 61.74 | 61.6124 | 61.6529
7782.0938 | 123.349 | -61.3678 | 61.6882 | -1.357 | -1.46 | -1.4176 | -1.1971 | -1.154 | -1.0544 | -1.3767 | 61.7569 | 0.23032 | 61.6652 | -0.028522 | 0.048236 | 61.5066 | 0.007721 | 61.2848 | 60.0108 | 59.9078 | 59.9502 | 60.1707 | 60.2138 | 60.3134 | 59.9911 | 123.1247 | 61.5981 | 123.033 | 61.3393 | 61.416 | 122.8744 | 61.3755 | 122.6526 | 61.7086 | 61.7491 | 61.617 | 61.6575
7783.0625 | 123.2758 | -61.3815 | 61.7706 | -1.5493 | -1.6523 | -1.6054 | -1.3894 | -1.3463 | -1.2605 | -1.5689 | 61.7752 | 0.2349 | 61.6698 | -0.019364 | 0.052814 | 61.4883 | 0.012299 | 61.2757 | 59.8323 | 59.7293 | 59.7762 | 59.9921 | 60.0353 | 60.1211 | 59.8126 | 123.1567 | 61.6164 | 123.0513 | 61.3622 | 61.4343 | 122.8699 | 61.3938 | 122.6572 | 61.7224 | 61.7629 | 61.617 | 61.6575
7784.0938 | 123.3307 | -61.4044 | 61.6791 | -1.3982 | -1.5057 | -1.4588 | -1.2246 | -1.1769 | -1.0865 | -1.4133 | 61.766 | 0.23948 | 61.6973 | -0.023943 | 0.052814 | 61.4975 | 0.012299 | 61.2803 | 60.0062 | 59.8987 | 59.9456 | 60.1798 | 60.2275 | 60.3179 | 59.9911 | 123.1704 | 61.6439 | 123.1017 | 61.3805 | 61.4572 | 122.9019 | 61.4167 | 122.6847 | 61.7132 | 61.7537 | 61.6445 | 61.685
7785.0625 | 123.2666 | -61.3678 | 61.7844 | -1.856 | -1.9499 | -1.903 | -1.6458 | -1.5889 | -1.5306 | -1.8619 | 61.7935 | 0.2349 | 61.6973 | -0.023943 | 0.048236 | 61.47 | 0.007721 | 61.2528 | 59.5118 | 59.4179 | 59.4648 | 59.722 | 59.7789 | 59.8372 | 59.5059 | 123.1613 | 61.6027 | 123.0651 | 61.3439 | 61.416 | 122.8378 | 61.3755 | 122.6206 | 61.7453 | 61.7858 | 61.649 | 61.6895
7786.1094 | 123.3261 | -61.3449 | 61.7386 | -1.9979 | -2.1101 | -2.0632 | -1.8061 | -1.7629 | -1.7183 | -2.0084 | 61.7889 | 0.2349 | 61.6973 | -0.033101 | 0.043657 | 61.4609 | 0.012299 | 61.2528 | 59.347 | 59.2348 | 59.2817 | 59.5389 | 59.582 | 59.6266 | 59.3365 | 123.1338 | 61.5798 | 123.0422 | 61.3118 | 61.3886 | 122.8058 | 61.3572 | 122.5977 | 61.7453 | 61.7766 | 61.6536 | 61.685
7787.0625 | 123.3719 | -61.3495 | 61.6608 | -1.183 | -1.2905 | -1.2391 | -0.99566 | -0.94342 | -0.78889 | -1.2027 | 61.7523 | 0.22574 | 61.6561 | -0.023943 | 0.057392 | 61.5112 | 0.012299 | 61.294 | 60.1665 | 60.0589 | 60.1104 | 60.3538 | 60.4061 | 60.5606 | 60.1468 | 123.1018 | 61.5752 | 123.0055 | 61.3255 | 61.4069 | 122.8607 | 61.3618 | 122.6435 | 61.6949 | 61.74 | 61.5987 | 61.6438
7788.0938 | 123.349 | -61.3907 | 61.6745 | -1.1601 | -1.2585 | -1.2116 | -0.96819 | -0.92511 | -0.75226 | -1.1706 | 61.7569 | 0.24405 | 61.679 | -0.028522 | 0.048236 | 61.5204 | 0.007721 | 61.294 | 60.2306 | 60.1322 | 60.1791 | 60.4225 | 60.4656 | 60.6384 | 60.2201 | 123.1476 | 61.6347 | 123.0696 | 61.3622 | 61.4389 | 122.9111 | 61.3984 | 122.6847 | 61.7086 | 61.7491 | 61.6307 | 61.6712
7789.0625 | 123.349 | -61.322 | 61.7249 | -1.5538 | -1.6477 | -1.6145 | -1.3619 | -1.3142 | -1.1918 | -1.5598 | 61.7614 | 0.2349 | 61.6652 | -0.028522 | 0.057392 | 61.4975 | 0.012299 | 61.2757 | 59.7682 | 59.6743 | 59.7075 | 59.9601 | 60.0078 | 60.1302 | 59.7622 | 123.0835 | 61.5569 | 122.9872 | 61.2935 | 61.3794 | 122.8195 | 61.3343 | 122.5977 | 61.7041 | 61.7491 | 61.6078 | 61.6529
7790.0938 | 123.3353 | -61.3907 | 61.6745 | -1.5722 | -1.6843 | -1.6374 | -1.3803 | -1.328 | -1.233 | -1.5872 | 61.766 | 0.23032 | 61.6744 | -0.019364 | 0.039079 | 61.4883 | 0.007721 | 61.2665 | 59.8185 | 59.7064 | 59.7533 | 60.0104 | 60.0627 | 60.1577 | 59.8034 | 123.1567 | 61.621 | 123.0651 | 61.3713 | 61.4298 | 122.879 | 61.3984 | 122.6572 | 61.7269 | 61.7583 | 61.6353 | 61.6667
7791.0625 | 123.2758 | -61.3815 | 61.7294 | -1.5905 | -1.7026 | -1.6511 | -1.4031 | -1.3554 | -1.2605 | -1.6101 | 61.7798 | 0.24405 | 61.7018 | -0.023943 | 0.048236 | 61.4838 | 0.007721 | 61.2757 | 59.7911 | 59.6789 | 59.7304 | 59.9784 | 60.0261 | 60.1211 | 59.7714 | 123.1613 | 61.6256 | 123.0834 | 61.3576 | 61.4298 | 122.8653 | 61.3893 | 122.6572 | 61.7315 | 61.772 | 61.6536 | 61.6941
7792.0938 | 123.3673 | -61.3861 | 61.6699 | -1.3158 | -1.4233 | -1.3673 | -1.1193 | -1.067 | -0.96745 | -1.3263 | 61.7523 | 0.23032 | 61.6881 | -0.023943 | 0.048236 | 61.5021 | 0.012299 | 61.2894 | 60.0703 | 59.9628 | 60.0188 | 60.2668 | 60.3191 | 60.4187 | 60.0598 | 123.1384 | 61.6164 | 123.0742 | 61.3622 | 61.4343 | 122.8882 | 61.3984 | 122.6755 | 61.7041 | 61.74 | 61.6399 | 61.6758
7793.0625 | 123.3627 | -61.3541 | 61.6699 | -1.215 | -1.3226 | -1.2894 | -1.0506 | -1.0167 | -0.88046 | -1.2347 | 61.7523 | 0.22574 | 61.6515 | -0.028522 | 0.048236 | 61.5021 | 0.012299 | 61.2894 | 60.139 | 60.0315 | 60.0646 | 60.3035 | 60.3374 | 60.4736 | 60.1193 | 123.1064 | 61.5798 | 123.0055 | 61.3255 | 61.4023 | 122.8561 | 61.3664 | 122.6435 | 61.7041 | 61.74 | 61.6032 | 61.6392
7794.0781 | 123.3536 | -61.377 | 61.6791 | -1.5767 | -1.6706 | -1.642 | -1.3986 | -1.3554 | -1.2513 | -1.5827 | 61.7614 | 0.2349 | 61.6744 | -0.023943 | 0.052814 | 61.4929 | 0.003143 | 61.2803 | 59.8002 | 59.7064 | 59.735 | 59.9784 | 60.0215 | 60.1256 | 59.7943 | 123.1384 | 61.6118 | 123.0513 | 61.353 | 61.4298 | 122.8699 | 61.3801 | 122.6572 | 61.7086 | 61.7583 | 61.6216 | 61.6712
7795.0625 | 123.3765 | -61.3495 | 61.6928 | -1.3158 | -1.4187 | -1.3718 | -1.1422 | -1.0945 | -0.99034 | -1.3217 | 61.766 | 0.23948 | 61.679 | -0.028522 | 0.052814 | 61.4975 | 0.007721 | 61.2803 | 60.0337 | 59.9307 | 59.9776 | 60.2073 | 60.255 | 60.3591 | 60.0278 | 123.1155 | 61.589 | 123.0284 | 61.321 | 61.4023 | 122.847 | 61.3572 | 122.6297 | 61.7132 | 61.7583 | 61.6261 | 61.6712
7796.1094 | 123.3856 | -61.3678 | 61.6745 | -1.4577 | -1.5607 | -1.5184 | -1.2933 | -1.2547 | -1.0911 | -1.4591 | 61.766 | 0.23032 | 61.6744 | -0.005627 | 0.075705 | 61.4929 | 0.035191 | 61.4634 | 59.9101 | 59.8071 | 59.8494 | 60.0745 | 60.1131 | 60.2767 | 59.9087 | 123.1338 | 61.5981 | 123.0422 | 61.3622 | 61.4435 | 122.8607 | 61.403 | 122.8312 | 61.6903 | 61.7308 | 61.5987 | 61.6392
7797.0625 | 123.317 | -61.3998 | 61.7157 | -1.5081 | -1.6156 | -1.5779 | -1.3345 | -1.2959 | -1.1552 | -1.5232 | 61.7935 | 0.24863 | 61.7293 | 0.05848 | 0.094017 | 61.4883 | 0.016878 | 61.4771 | 59.8918 | 59.7842 | 59.822 | 60.0654 | 60.1039 | 60.2447 | 59.8767 | 123.1933 | 61.6485 | 123.1292 | 61.4583 | 61.4939 | 122.8882 | 61.4167 | 122.877 | 61.6995 | 61.7766 | 61.6353 | 61.7124
7798.0938 | 123.2803 | -61.3861 | 61.7111 | -1.5905 | -1.7026 | -1.6557 | -1.4123 | -1.3646 | -1.2696 | -1.6101 | 61.8072 | 0.25321 | 61.7339 | 0.05848 | 0.084861 | 61.4883 | 0.016878 | 61.294 | 59.7956 | 59.6835 | 59.7304 | 59.9738 | 60.0215 | 60.1165 | 59.776 | 123.1933 | 61.6393 | 123.12 | 61.4446 | 61.471 | 122.8744 | 61.403 | 122.6801 | 61.7224 | 61.7904 | 61.649 | 61.717
7799.0625 | 123.3582 | -61.3403 | 61.734 | -2.117 | -2.2155 | -2.1777 | -1.9526 | -1.9048 | -1.7778 | -2.1275 | 61.8393 | 0.25321 | 61.7659 | 0.05848 | 0.094017 | 61.4609 | 0.007721 | 61.2619 | 59.2234 | 59.1249 | 59.1627 | 59.3878 | 59.4355 | 59.5625 | 59.2129 | 123.1796 | 61.5935 | 123.1063 | 61.3988 | 61.4343 | 122.8012 | 61.3481 | 122.6023 | 61.7453 | 61.8316 | 61.6719 | 61.7582
7800.0781 | 123.2483 | -61.3815 | 61.7615 | -1.9934 | -2.0827 | -2.0495 | -1.8061 | -1.7491 | -1.6222 | -2.0039 | 61.821 | 0.25321 | 61.7568 | 0.053901 | 0.075705 | 61.47 | 0.003143 | 61.2665 | 59.3882 | 59.2989 | 59.3321 | 59.5755 | 59.6324 | 59.7594 | 59.3777 | 123.2025 | 61.6347 | 123.1383 | 61.4354 | 61.4572 | 122.8516 | 61.3847 | 122.6481 | 61.7453 | 61.8178 | 61.6811 | 61.7536
7801.0625 | 123.2986 | -61.3312 | 61.7615 | -1.9934 | -2.0827 | -2.0449 | -1.8061 | -1.7675 | -1.6267 | -1.9901 | 61.8164 | 0.24863 | 61.7476 | 0.053901 | 0.094017 | 61.47 | -0.033484 | 61.2619 | 59.3378 | 59.2485 | 59.2863 | 59.5251 | 59.5637 | 59.7044 | 59.341 | 123.1476 | 61.5798 | 123.0788 | 61.3851 | 61.4252 | 122.8012 | 61.2977 | 122.5931 | 61.7224 | 61.8499 | 61.6536 | 61.7811
7802.0625 | 123.3627 | -61.377 | 61.7386 | -2.0529 | -2.1468 | -2.0998 | -1.8747 | -1.8178 | -1.6771 | -2.0451 | 61.8164 | 0.2349 | 61.743 | 0.003531 | 0.071126 | 61.4654 | -0.065533 | 61.2619 | 59.3241 | 59.2302 | 59.2771 | 59.5022 | 59.5591 | 59.6999 | 59.3319 | 123.1933 | 61.6118 | 123.12 | 61.3805 | 61.4481 | 122.8424 | 61.3114 | 122.6389 | 61.7453 | 61.8819 | 61.6719 | 61.8086
7803.0938 | 123.2391 | -61.3724 | 61.7569 | -1.7965 | -1.8949 | -1.8572 | -1.6183 | -1.5752 | -1.4344 | -1.7933 | 61.7889 | 0.23948 | 61.7202 | -0.005627 | 0.034501 | 61.4792 | 0.035191 | 61.2665 | 59.5759 | 59.4774 | 59.5152 | 59.754 | 59.7972 | 59.9379 | 59.5791 | 123.1613 | 61.6119 | 123.0925 | 61.3667 | 61.4069 | 122.8516 | 61.4076 | 122.6389 | 61.7544 | 61.7537 | 61.6857 | 61.685
7804.0625 | 123.3444 | -61.2991 | 61.7706 | -2.1307 | -2.2246 | -2.1777 | -1.98 | -1.9185 | -1.7961 | -2.1229 | 61.8027 | 0.20742 | 61.6927 | -0.001048 | 0.089439 | 61.4609 | 0.048926 | 61.2391 | 59.1684 | 59.0745 | 59.1215 | 59.3191 | 59.3806 | 59.503 | 59.1762 | 123.1018 | 61.5066 | 122.9918 | 61.2981 | 61.3886 | 122.76 | 61.3481 | 122.5382 | 61.7132 | 61.7537 | 61.6033 | 61.6438
7805.0938 | 123.3353 | -61.3541 | 61.734 | -2.2726 | -2.3757 | -2.3242 | -2.0945 | -2.0421 | -1.961 | -2.2648 | 61.8164 | 0.23032 | 61.7064 | -0.092628 | 0.052814 | 61.4426 | 0.044348 | 61.4313 | 59.0814 | 58.9783 | 59.0299 | 59.2596 | 59.3119 | 59.3931 | 59.0892 | 123.1705 | 61.5844 | 123.0605 | 61.2614 | 61.4069 | 122.7966 | 61.3984 | 122.7854 | 61.7636 | 61.772 | 61.6536 | 61.6621
7806.0625 | 123.3536 | -61.3449 | 61.7432 | -2.0575 | -2.1559 | -2.1182 | -1.8976 | -1.8453 | -1.6725 | -2.0634 | 61.8072 | 0.23948 | 61.711 | -0.097207 | 0.048236 | 61.4609 | 0.012299 | 61.4451 | 59.2874 | 59.189 | 59.2268 | 59.4473 | 59.4996 | 59.6724 | 59.2815 | 123.1521 | 61.5844 | 123.0559 | 61.2477 | 61.3931 | 122.8058 | 61.3572 | 122.79 | 61.759 | 61.7949 | 61.6628 | 61.6987
7807.0781 | 123.2895 | -61.3678 | 61.7935 | -2.5245 | -2.6138 | -2.5806 | -2.3692 | -2.326 | -2.2311 | -2.5212 | 61.8301 | 0.23948 | 61.7293 | -0.014785 | 0.048236 | 61.4288 | 0.007721 | 61.207 | 58.8433 | 58.754 | 58.7872 | 58.9986 | 59.0418 | 59.1367 | 58.8466 | 123.1979 | 61.6073 | 123.0971 | 61.353 | 61.416 | 122.7966 | 61.3755 | 122.5748 | 61.7819 | 61.8224 | 61.6811 | 61.7216
7808.0625 | 123.3353 | -61.3632 | 61.702 | -2.6527 | -2.7512 | -2.7042 | -2.5249 | -2.4725 | -2.3776 | -2.6494 | 61.8347 | 0.22574 | 61.7339 | -0.019364 | 0.048236 | 61.4242 | 0.021456 | 61.2024 | 58.7106 | 58.612 | 58.659 | 58.8383 | 58.8908 | 58.9856 | 58.7138 | 123.1979 | 61.589 | 123.0971 | 61.3439 | 61.4115 | 122.7875 | 61.3847 | 122.5656 | 61.7865 | 61.8132 | 61.6857 | 61.7124
7809.0938 | 123.3536 | -61.2991 | 61.734 | -2.7992 | -2.8885 | -2.8462 | -2.6348 | -2.5869 | -2.5378 | -2.7867 | 61.8484 | 0.23948 | 61.7614 | -0.019364 | 0.039079 | 61.4242 | 0.012299 | 61.1933 | 58.5 | 58.4106 | 58.453 | 58.6644 | 58.7122 | 58.7613 | 58.5124 | 123.1476 | 61.5386 | 123.0605 | 61.2798 | 61.3382 | 122.7234 | 61.3114 | 122.4924 | 61.8094 | 61.8361 | 61.7223 | 61.7491
7810.0625 | 123.349 | -61.2488 | 61.7706 | -3.0006 | -3.0992 | -3.0522 | -2.8591 | -2.8066 | -2.7622 | -2.9973 | 61.853 | 0.23032 | 61.7751 | -0.023943 | 0.052814 | 61.4059 | 0.016878 | 61.1841 | 58.2482 | 58.1496 | 58.1966 | 58.3897 | 58.4421 | 58.4866 | 58.2515 | 123.1018 | 61.4791 | 123.0239 | 61.2248 | 61.3016 | 122.6547 | 61.2657 | 122.4329 | 61.8002 | 61.8361 | 61.7223 | 61.7582
7811.1094 | 123.3536 | -61.2717 | 61.7706 | -3.0784 | -3.177 | -3.13 | -2.9507 | -2.8936 | -2.8904 | -3.0706 | 61.8576 | 0.2349 | 61.7614 | -0.023943 | 0.048236 | 61.4014 | 0.012299 | 61.1841 | 58.1932 | 58.0947 | 58.1416 | 58.321 | 58.378 | 58.3813 | 58.2011 | 123.1293 | 61.5066 | 123.033 | 61.2477 | 61.3199 | 122.673 | 61.284 | 122.4558 | 61.8094 | 61.8453 | 61.7131 | 61.7491
7812.0625 | 123.3307 | -61.3312 | 61.7432 | -2.5428 | -2.6367 | -2.5989 | -2.4013 | -2.3534 | -2.2631 | -2.5349 | 61.8255 | 0.2349 | 61.7339 | -0.028522 | 0.052814 | 61.4288 | 0.012299 | 61.2116 | 58.7884 | 58.6945 | 58.7323 | 58.9299 | 58.9777 | 59.068 | 58.7962 | 123.1567 | 61.5661 | 123.0651 | 61.3027 | 61.384 | 122.76 | 61.3435 | 122.5428 | 61.7727 | 61.8132 | 61.6811 | 61.7216
7813.0938 | 123.2986 | -61.3403 | 61.7432 | -1.9338 | -2.0186 | -1.9854 | -1.7877 | -1.7354 | -1.5489 | -1.9169 | 61.7981 | 0.2349 | 61.7202 | -0.028522 | 0.048236 | 61.4654 | 0.007721 | 61.2619 | 59.4065 | 59.3218 | 59.355 | 59.5526 | 59.6049 | 59.7914 | 59.4235 | 123.1384 | 61.5752 | 123.0605 | 61.3118 | 61.3886 | 122.8058 | 61.3481 | 122.6023 | 61.7498 | 61.7904 | 61.6719 | 61.7124
7814.0625 | 123.349 | -61.3358 | 61.7249 | -1.9979 | -2.0918 | -2.0586 | -1.8289 | -1.7903 | -1.6222 | -1.9993 | 61.7935 | 0.23032 | 61.711 | -0.028522 | 0.052814 | 61.47 | 0.007721 | 61.2665 | 59.3378 | 59.2439 | 59.2771 | 59.5068 | 59.5454 | 59.7136 | 59.3365 | 123.1292 | 61.5661 | 123.0468 | 61.3072 | 61.3886 | 122.8058 | 61.3435 | 122.6023 | 61.7407 | 61.7858 | 61.6582 | 61.7033
7815.0781 | 123.3078 | -61.322 | 61.7294 | -2.3505 | -2.4398 | -2.4066 | -2.2181 | -2.1703 | -2.0434 | -2.3381 | 61.8164 | 0.2349 | 61.7247 | -0.033101 | 0.048236 | 61.4471 | 0.007721 | 61.2436 | 58.9715 | 58.8822 | 58.9154 | 59.1039 | 59.1517 | 59.2787 | 58.984 | 123.1384 | 61.5569 | 123.0468 | 61.2889 | 61.3703 | 122.7692 | 61.3297 | 122.5657 | 61.7682 | 61.8087 | 61.6765 | 61.717
7816.0625 | 123.2895 | -61.2854 | 61.8027 | -2.3047 | -2.3986 | -2.3654 | -2.1723 | -2.1428 | -1.9976 | -2.2877 | 61.8255 | 0.24405 | 61.7385 | -0.023943 | 0.052814 | 61.4426 | 0.007721 | 61.2528 | 58.9807 | 58.8868 | 58.92 | 59.1131 | 59.1426 | 59.2878 | 58.9977 | 123.1109 | 61.5295 | 123.0239 | 61.2615 | 61.3382 | 122.728 | 61.2931 | 122.5382 | 61.7727 | 61.8178 | 61.6857 | 61.7308
7817.0938 | 123.2666 | -61.3174 | 61.7889 | -2.2498 | -2.3437 | -2.3013 | -2.1128 | -2.065 | -1.9289 | -2.2419 | 61.8164 | 0.2349 | 61.743 | -0.033101 | 0.043657 | 61.4471 | 0.003143 | 61.2482 | 59.0677 | 58.9738 | 59.0161 | 59.2046 | 59.2524 | 59.3885 | 59.0755 | 123.1338 | 61.5523 | 123.0605 | 61.2843 | 61.3611 | 122.7646 | 61.3206 | 122.5657 | 61.7727 | 61.8132 | 61.6994 | 61.7399
7818.0625 | 123.3856 | -61.2717 | 61.8073 | -2.3596 | -2.4536 | -2.4112 | -2.2273 | -2.1795 | -2.0296 | -2.3564 | 61.8118 | 0.2349 | 61.7202 | -0.028522 | 0.048236 | 61.4471 | 0.003143 | 61.2528 | 58.912 | 58.8181 | 58.8605 | 59.0444 | 59.0922 | 59.242 | 58.9153 | 123.0835 | 61.5066 | 122.9918 | 61.2431 | 61.3199 | 122.7188 | 61.2748 | 122.5245 | 61.7636 | 61.8087 | 61.6719 | 61.717
7819.0938 | 123.3627 | -61.3174 | 61.7294 | -2.6572 | -2.7466 | -2.7088 | -2.5249 | -2.477 | -2.3684 | -2.6448 | 61.8347 | 0.2349 | 61.743 | -0.019364 | 0.057392 | 61.4334 | 0.012299 | 61.2345 | 58.6602 | 58.5708 | 58.6086 | 58.7926 | 58.8404 | 58.949 | 58.6726 | 123.1521 | 61.5523 | 123.0605 | 61.2981 | 61.3748 | 122.7508 | 61.3297 | 122.5519 | 61.7773 | 61.8224 | 61.6857 | 61.7308
7820.0625 | 123.3353 | -61.3403 | 61.7294 | -2.5428 | -2.6367 | -2.5989 | -2.4287 | -2.3809 | -2.2448 | -2.5487 | 61.8347 | 0.23032 | 61.7614 | -0.033101 | 0.048236 | 61.438 | 0.021456 | 61.2391 | 58.7976 | 58.7036 | 58.7414 | 58.9116 | 58.9594 | 59.0955 | 58.7917 | 123.175 | 61.5706 | 123.1017 | 61.3072 | 61.3886 | 122.7783 | 61.3618 | 122.5794 | 61.7865 | 61.8132 | 61.7131 | 61.7399
7821.1094 | 123.3719 | -61.29 | 61.7523 | -2.9274 | -3.0076 | -2.9789 | -2.7767 | -2.7288 | -2.6431 | -2.9058 | 61.8622 | 0.24405 | 61.7797 | -0.033101 | 0.052814 | 61.4151 | 0.012299 | 61.2116 | 58.3626 | 58.2824 | 58.311 | 58.5133 | 58.5612 | 58.6468 | 58.3842 | 123.1522 | 61.534 | 123.0697 | 61.2569 | 61.3428 | 122.7051 | 61.3023 | 122.5016 | 61.8094 | 61.8499 | 61.7269 | 61.7674
7822.0625 | 123.3948 | -61.3174 | 61.7432 | -2.9228 | -3.0122 | -2.9789 | -2.7904 | -2.7471 | -2.666 | -2.9103 | 61.853 | 0.22574 | 61.7476 | -0.03768 | 0.057392 | 61.4105 | 0.012299 | 61.2207 | 58.3947 | 58.3053 | 58.3385 | 58.527 | 58.5703 | 58.6514 | 58.4071 | 123.1705 | 61.5432 | 123.0651 | 61.2798 | 61.3748 | 122.7279 | 61.3297 | 122.5382 | 61.7956 | 61.8407 | 61.6902 | 61.7353
7823.0938 | 123.3444 | -61.2854 | 61.7523 | -2.8037 | -2.8977 | -2.8507 | -2.6714 | -2.6281 | -2.5516 | -2.7913 | 61.8347 | 0.23032 | 61.7476 | -0.028522 | 0.039079 | 61.4197 | 0.012299 | 61.2207 | 58.4817 | 58.3877 | 58.4347 | 58.614 | 58.6573 | 58.7338 | 58.4941 | 123.1201 | 61.5157 | 123.033 | 61.2569 | 61.3245 | 122.7051 | 61.2977 | 122.5061 | 61.7956 | 61.8224 | 61.7086 | 61.7353
7824.0625 | 123.4039 | -61.2625 | 61.7889 | -2.9411 | -3.0213 | -2.9744 | -2.8133 | -2.7654 | -2.6843 | -2.9195 | 61.8576 | 0.2349 | 61.7659 | -0.028522 | 0.052814 | 61.4151 | 0.007721 | 61.207 | 58.3214 | 58.2412 | 58.2882 | 58.4492 | 58.4971 | 58.5782 | 58.343 | 123.1201 | 61.4974 | 123.0285 | 61.234 | 61.3153 | 122.6776 | 61.2702 | 122.4695 | 61.8048 | 61.8499 | 61.7131 | 61.7582
7825.0781 | 123.3398 | -61.3495 | 61.7157 | -2.5153 | -2.5909 | -2.5577 | -2.36 | -2.3168 | -2.254 | -2.4937 | 61.8301 | 0.23948 | 61.7614 | -0.03768 | 0.048236 | 61.4334 | 0.007721 | 61.2391 | 58.8342 | 58.7586 | 58.7918 | 58.9894 | 59.0327 | 59.0955 | 58.8558 | 123.1796 | 61.589 | 123.1108 | 61.3118 | 61.3977 | 122.7829 | 61.3572 | 122.5885 | 61.7819 | 61.8224 | 61.7131 | 61.7536
7826.0625 | 123.3261 | -61.29 | 61.7661 | -2.6069 | -2.6825 | -2.6539 | -2.4699 | -2.4175 | -2.3547 | -2.5853 | 61.8255 | 0.23032 | 61.743 | -0.023943 | 0.052814 | 61.4288 | 0.016878 | 61.2345 | 58.6831 | 58.6075 | 58.6361 | 58.82 | 58.8725 | 58.9353 | 58.7047 | 123.1155 | 61.5203 | 123.033 | 61.266 | 61.3428 | 122.7188 | 61.3069 | 122.5245 | 61.7727 | 61.8087 | 61.6902 | 61.7262
7827.0938 | 123.3124 | -61.3129 | 61.7661 | -2.2085 | -2.3116 | -2.2693 | -2.0899 | -2.0284 | -1.874 | -2.2053 | 61.8072 | 0.22574 | 61.7202 | -0.033101 | 0.052814 | 61.4517 | 0.012299 | 61.2528 | 59.1043 | 59.0013 | 59.0436 | 59.2229 | 59.2845 | 59.4389 | 59.1076 | 123.1201 | 61.5386 | 123.033 | 61.2798 | 61.3657 | 122.7646 | 61.3252 | 122.5657 | 61.7544 | 61.7949 | 61.6673 | 61.7079
7828.0625 | 123.3994 | -61.2854 | 61.7798 | -2.6206 | -2.7054 | -2.6767 | -2.4974 | -2.4541 | -2.3593 | -2.599 | 61.8347 | 0.23948 | 61.7476 | -0.028522 | 0.057392 | 61.4242 | -0.001436 | 61.2391 | 58.6648 | 58.58 | 58.6087 | 58.788 | 58.8313 | 58.9261 | 58.6864 | 123.1201 | 61.5249 | 123.033 | 61.2569 | 61.3428 | 122.7096 | 61.284 | 122.5245 | 61.7773 | 61.8361 | 61.6902 | 61.7491
7829.0781 | 123.3353 | -61.2946 | 61.7569 | -2.6252 | -2.7146 | -2.6813 | -2.4928 | -2.4541 | -2.3639 | -2.6082 | 61.8393 | 0.24405 | 61.7568 | -0.023943 | 0.048236 | 61.4242 | 0.012299 | 61.2299 | 58.6694 | 58.58 | 58.6132 | 58.8017 | 58.8404 | 58.9307 | 58.6864 | 123.1338 | 61.5386 | 123.0513 | 61.2706 | 61.3428 | 122.7188 | 61.3069 | 122.5245 | 61.791 | 61.827 | 61.7085 | 61.7445
7830.0625 | 123.3627 | -61.2442 | 61.8027 | -2.3734 | -2.449 | -2.4249 | -2.2227 | -2.1749 | -2.0663 | -2.361 | 61.8164 | 0.2349 | 61.7385 | -0.033101 | 0.048236 | 61.4334 | 0.016878 | 61.2482 | 58.8708 | 58.7952 | 58.8193 | 59.0215 | 59.0693 | 59.1779 | 58.8832 | 123.0606 | 61.4791 | 122.9827 | 61.2111 | 61.2924 | 122.6776 | 61.2611 | 122.4924 | 61.7682 | 61.7995 | 61.6902 | 61.7216
7831.1094 | 123.3215 | -61.3266 | 61.7889 | -2.3276 | -2.4169 | -2.3883 | -2.1861 | -2.1383 | -2.0113 | -2.3152 | 61.8164 | 0.2349 | 61.7247 | -0.023943 | 0.048236 | 61.4471 | 0.012299 | 61.2482 | 58.999 | 58.9097 | 58.9383 | 59.1405 | 59.1883 | 59.3153 | 59.0114 | 123.143 | 61.5615 | 123.0513 | 61.3027 | 61.3748 | 122.7737 | 61.3389 | 122.5748 | 61.7682 | 61.8041 | 61.6765 | 61.7124
7832.0625 | 123.3444 | -61.3083 | 61.7798 | -2.5016 | -2.5863 | -2.5577 | -2.3372 | -2.2893 | -2.1761 | -2.4754 | 61.821 | 0.2349 | 61.7293 | -0.028522 | 0.048236 | 61.4426 | 0.016878 | 61.2482 | 58.8067 | 58.7219 | 58.7506 | 58.9711 | 59.019 | 59.1321 | 58.8329 | 123.1293 | 61.5432 | 123.0376 | 61.2798 | 61.3565 | 122.7508 | 61.3252 | 122.5565 | 61.7727 | 61.8041 | 61.6811 | 61.7124
7833.0938 | 123.3215 | -61.2991 | 61.7432 | -2.7351 | -2.8153 | -2.7729 | -2.589 | -2.5411 | -2.46 | -2.7089 | 61.8393 | 0.23948 | 61.7522 | -0.033101 | 0.048236 | 61.4242 | 0.007721 | 61.2253 | 58.5641 | 58.4838 | 58.5262 | 58.7102 | 58.758 | 58.8391 | 58.5902 | 123.1384 | 61.5386 | 123.0513 | 61.266 | 61.3474 | 122.7234 | 61.3069 | 122.5245 | 61.791 | 61.8316 | 61.704 | 61.7445
7834.0625 | 123.3719 | -61.3083 | 61.7661 | -2.1628 | -2.2475 | -2.2143 | -2.0212 | -1.9597 | -1.8419 | -2.1458 | 61.8118 | 0.2349 | 61.7293 | -0.028522 | 0.043657 | 61.4563 | 0.007721 | 61.2619 | 59.1455 | 59.0608 | 59.094 | 59.287 | 59.3486 | 59.4664 | 59.1625 | 123.1201 | 61.5432 | 123.0376 | 61.2798 | 61.3519 | 122.7646 | 61.316 | 122.5702 | 61.7682 | 61.8041 | 61.6857 | 61.7216
7835.0781 | 123.3032 | -61.3129 | 61.7386 | -2.2269 | -2.3116 | -2.2738 | -2.0808 | -2.0421 | -1.8923 | -2.2053 | 61.8118 | 0.2349 | 61.711 | -0.033101 | 0.048236 | 61.4517 | 0.012299 | 61.2574 | 59.086 | 59.0013 | 59.039 | 59.2321 | 59.2707 | 59.4206 | 59.1076 | 123.1247 | 61.5478 | 123.0239 | 61.2798 | 61.3611 | 122.7646 | 61.3252 | 122.5702 | 61.7636 | 61.7995 | 61.6628 | 61.6987
7836.0625 | 123.262 | -61.2946 | 61.8347 | -3.0052 | -3.0809 | -3.0522 | -2.8912 | -2.8433 | -2.7805 | -2.979 | 61.8576 | 0.22574 | 61.7614 | -0.023943 | 0.052814 | 61.4059 | 0.007721 | 61.2162 | 58.2894 | 58.2137 | 58.2424 | 58.4034 | 58.4513 | 58.5141 | 58.3155 | 123.1522 | 61.5203 | 123.0559 | 61.2706 | 61.3474 | 122.7005 | 61.3023 | 122.5107 | 61.8048 | 61.8499 | 61.7085 | 61.7536
7837.0938 | 123.3398 | -61.2946 | 61.7615 | -2.8999 | -2.9801 | -2.9469 | -2.7904 | -2.7471 | -2.6614 | -2.8783 | 61.8439 | 0.2349 | 61.7797 | -0.042259 | 0.048236 | 61.4151 | 0.012299 | 61.2162 | 58.3947 | 58.3144 | 58.3477 | 58.5041 | 58.5474 | 58.6331 | 58.4163 | 123.1384 | 61.5295 | 123.0742 | 61.2523 | 61.3428 | 122.7096 | 61.3069 | 122.5107 | 61.7956 | 61.8316 | 61.7314 | 61.7674
7838.0625 | 123.2895 | -61.2671 | 61.8439 | -2.6801 | -2.7603 | -2.7271 | -2.5707 | -2.5137 | -2.4188 | -2.6585 | 61.8393 | 0.23948 | 61.7705 | -0.023943 | 0.048236 | 61.4242 | 0.016878 | 61.2253 | 58.587 | 58.5068 | 58.54 | 58.6964 | 58.7534 | 58.8483 | 58.6085 | 123.1064 | 61.5066 | 123.0376 | 61.2431 | 61.3153 | 122.6913 | 61.284 | 122.4924 | 61.791 | 61.8224 | 61.7223 | 61.7536
7839.0781 | 123.349 | -61.322 | 61.7294 | -2.5702 | -2.6504 | -2.6218 | -2.4333 | -2.3717 | -2.254 | -2.5487 | 61.821 | 0.23032 | 61.7522 | -0.023943 | 0.039079 | 61.4334 | 0.007721 | 61.2299 | 58.7518 | 58.6716 | 58.7002 | 58.8887 | 58.9503 | 59.068 | 58.7734 | 123.143 | 61.5523 | 123.0742 | 61.2981 | 61.3611 | 122.7554 | 61.3297 | 122.5519 | 61.7819 | 61.8132 | 61.7131 | 61.7445
7840.0625 | 123.3215 | -61.2762 | 61.8027 | -2.4924 | -2.5634 | -2.5394 | -2.3555 | -2.3077 | -2.1853 | -2.4571 | 61.821 | 0.22574 | 61.7247 | -0.028522 | 0.048236 | 61.438 | 0.012299 | 61.2299 | 58.7838 | 58.7128 | 58.7369 | 58.9208 | 58.9686 | 59.0909 | 58.8191 | 123.0972 | 61.502 | 123.001 | 61.2477 | 61.3245 | 122.7142 | 61.2885 | 122.5061 | 61.7727 | 61.8087 | 61.6765 | 61.7124
7841.1094 | 123.3398 | -61.2808 | 61.7889 | -2.8907 | -2.971 | -2.9377 | -2.7538 | -2.7105 | -2.634 | -2.86 | 61.8439 | 0.2349 | 61.7476 | -0.023943 | 0.048236 | 61.4197 | 0.012299 | 61.1978 | 58.3901 | 58.3099 | 58.3431 | 58.527 | 58.5703 | 58.6468 | 58.4208 | 123.1247 | 61.5157 | 123.0285 | 61.2569 | 61.3291 | 122.7005 | 61.2931 | 122.4787 | 61.7956 | 61.8316 | 61.6994 | 61.7353
7842.0625 | 123.262 | -61.2854 | 61.8668 | -3.1059 | -3.1862 | -3.1483 | -2.9736 | -2.9257 | -2.8675 | -3.0797 | 61.8622 | 0.2349 | 61.7614 | -0.023943 | 0.057392 | 61.4014 | 0.016878 | 61.1887 | 58.1795 | 58.0992 | 58.1371 | 58.3118 | 58.3597 | 58.4179 | 58.2057 | 123.1476 | 61.5203 | 123.0468 | 61.2615 | 61.3428 | 122.6868 | 61.3023 | 122.4741 | 61.8048 | 61.8453 | 61.704 | 61.7445
7843.0781 | 123.3765 | -61.2854 | 61.7844 | -2.8953 | -2.971 | -2.9331 | -2.7721 | -2.7197 | -2.6431 | -2.86 | 61.8576 | 0.23948 | 61.7659 | -0.028522 | 0.039079 | 61.4197 | 0.012299 | 61.1933 | 58.3901 | 58.3144 | 58.3523 | 58.5133 | 58.5657 | 58.6423 | 58.4254 | 123.143 | 61.5249 | 123.0513 | 61.2569 | 61.3245 | 122.7051 | 61.2977 | 122.4787 | 61.8185 | 61.8453 | 61.7269 | 61.7536
7844.0625 | 123.2208 | -61.322 | 61.821 | -2.7717 | -2.8565 | -2.8233 | -2.6577 | -2.6098 | -2.5241 | -2.7501 | 61.853 | 0.23948 | 61.7705 | -0.023943 | 0.057392 | 61.4197 | 0.012299 | 61.2024 | 58.5503 | 58.4655 | 58.4988 | 58.6644 | 58.7122 | 58.7979 | 58.5719 | 123.175 | 61.5615 | 123.0925 | 61.2981 | 61.3794 | 122.7417 | 61.3343 | 122.5244 | 61.7956 | 61.8407 | 61.7131 | 61.7582
7845.0781 | 123.3353 | -61.2305 | 61.8118 | -3.2662 | -3.3373 | -3.3086 | -3.1109 | -3.0676 | -3.0369 | -3.2217 | 61.8759 | 0.23032 | 61.7751 | -0.033101 | 0.048236 | 61.3922 | 0.016878 | 61.175 | 57.9643 | 57.8932 | 57.9219 | 58.1195 | 58.1629 | 58.1936 | 58.0088 | 123.1064 | 61.4608 | 123.0056 | 61.1974 | 61.2787 | 122.6227 | 61.2473 | 122.4054 | 61.8277 | 61.859 | 61.7269 | 61.7582
7846.0625 | 123.2529 | -61.3403 | 61.7477 | -2.8953 | -2.9755 | -2.9515 | -2.763 | -2.7242 | -2.6569 | -2.8691 | 61.8393 | 0.22116 | 61.7476 | -0.028522 | 0.048236 | 61.4197 | 0.012299 | 61.1933 | 58.445 | 58.3648 | 58.3889 | 58.5774 | 58.6161 | 58.6835 | 58.4712 | 123.1796 | 61.5615 | 123.088 | 61.3118 | 61.3886 | 122.76 | 61.3526 | 122.5336 | 61.791 | 61.827 | 61.6994 | 61.7353
7847.0938 | 123.3353 | -61.2762 | 61.7523 | -2.8358 | -2.9023 | -2.8736 | -2.6851 | -2.6418 | -2.5699 | -2.7959 | 61.8347 | 0.23032 | 61.7385 | -0.023943 | 0.048236 | 61.4197 | 0.003143 | 61.2024 | 58.4405 | 58.374 | 58.4026 | 58.5911 | 58.6344 | 58.7064 | 58.4804 | 123.1109 | 61.5066 | 123.0147 | 61.2523 | 61.3245 | 122.6959 | 61.2794 | 122.4787 | 61.7865 | 61.8316 | 61.6902 | 61.7353
7848.0625 | 123.2529 | -61.2625 | 61.8484 | -2.9136 | -2.9984 | -2.9606 | -2.795 | -2.7471 | -2.6431 | -2.892 | 61.8484 | 0.24405 | 61.7568 | -0.033101 | 0.052814 | 61.4105 | 0.016878 | 61.1978 | 58.3489 | 58.2641 | 58.3019 | 58.4675 | 58.5154 | 58.6194 | 58.3705 | 123.1109 | 61.5066 | 123.0193 | 61.2294 | 61.3153 | 122.673 | 61.2794 | 122.4604 | 61.7956 | 61.8316 | 61.704 | 61.7399
7849.0938 | 123.3032 | -61.3037 | 61.7477 | -2.7534 | -2.8244 | -2.7958 | -2.6164 | -2.5686 | -2.4371 | -2.7089 | 61.8393 | 0.24405 | 61.7568 | -0.023943 | 0.039079 | 61.4288 | 0.012299 | 61.1978 | 58.5503 | 58.4793 | 58.5079 | 58.6873 | 58.7351 | 58.8666 | 58.5948 | 123.143 | 61.5478 | 123.0605 | 61.2798 | 61.3428 | 122.7325 | 61.316 | 122.5016 | 61.8002 | 61.827 | 61.7177 | 61.7445
7850.0625 | 123.2758 | -61.2946 | 61.821 | -3.0052 | -3.0854 | -3.0568 | -2.8545 | -2.8158 | -2.7164 | -2.979 | 61.8576 | 0.23948 | 61.7934 | -0.023943 | 0.052814 | 61.4105 | 0.012299 | 61.1933 | 58.2894 | 58.2091 | 58.2378 | 58.44 | 58.4788 | 58.5782 | 58.3155 | 123.1522 | 61.534 | 123.088 | 61.2706 | 61.3474 | 122.7051 | 61.3069 | 122.4878 | 61.8048 | 61.8453 | 61.7406 | 61.7811
7851.0938 | 123.3627 | -61.2762 | 61.7798 | -2.9823 | -3.0717 | -3.0293 | -2.8683 | -2.7975 | -2.6569 | -2.9607 | 61.8484 | 0.23032 | 61.7568 | -0.028522 | 0.043657 | 61.4151 | 0.012299 | 61.1704 | 58.2939 | 58.2045 | 58.2469 | 58.408 | 58.4788 | 58.6194 | 58.3155 | 123.1247 | 61.5066 | 123.033 | 61.2477 | 61.3199 | 122.6913 | 61.2885 | 122.4466 | 61.8048 | 61.8361 | 61.7131 | 61.7445
7852.0625 | 123.2666 | -61.3312 | 61.8301 | -2.9136 | -2.9939 | -2.9606 | -2.7813 | -2.7334 | -2.634 | -2.8783 | 61.8484 | 0.23032 | 61.7522 | -0.023943 | 0.048236 | 61.4059 | 0.007721 | 61.1978 | 58.4176 | 58.3373 | 58.3706 | 58.5499 | 58.5978 | 58.6972 | 58.4529 | 123.1796 | 61.5615 | 123.0834 | 61.3072 | 61.3794 | 122.7371 | 61.3389 | 122.529 | 61.8002 | 61.8407 | 61.704 | 61.7445
7853.0781 | 123.3353 | -61.2671 | 61.7798 | -2.8999 | -2.9847 | -2.9423 | -2.7721 | -2.7242 | -2.6065 | -2.8783 | 61.8484 | 0.22116 | 61.7385 | -0.033101 | 0.043657 | 61.4105 | 0.007721 | 61.1978 | 58.3672 | 58.2824 | 58.3248 | 58.495 | 58.5428 | 58.6606 | 58.3888 | 123.1155 | 61.4883 | 123.0056 | 61.234 | 61.3107 | 122.6776 | 61.2748 | 122.4649 | 61.8048 | 61.8407 | 61.6948 | 61.7308
7854.0625 | 123.3536 | -61.3129 | 61.7523 | -3.0693 | -3.1541 | -3.1254 | -2.9827 | -2.9303 | -2.7713 | -3.0431 | 61.8622 | 0.22574 | 61.7568 | -0.023943 | 0.048236 | 61.4105 | 0.012299 | 61.1795 | 58.2436 | 58.1587 | 58.1874 | 58.3301 | 58.3826 | 58.5415 | 58.2698 | 123.175 | 61.5386 | 123.0697 | 61.2889 | 61.3611 | 122.7234 | 61.3252 | 122.4924 | 61.8139 | 61.8499 | 61.7085 | 61.7445
7855.0938 | 123.4039 | -61.2488 | 61.8027 | -3.2021 | -3.2777 | -3.2536 | -3.1292 | -3.0767 | -2.8492 | -3.1621 | 61.8713 | 0.23032 | 61.7797 | -0.023943 | 0.048236 | 61.3968 | 0.012299 | 61.175 | 58.0467 | 57.971 | 57.9951 | 58.1195 | 58.172 | 58.3996 | 58.0866 | 123.1201 | 61.4791 | 123.0285 | 61.2248 | 61.297 | 122.6456 | 61.2611 | 122.4237 | 61.8231 | 61.859 | 61.7314 | 61.7674
7856.0625 | 123.2529 | -61.2991 | 61.7798 | -2.5794 | -2.6642 | -2.631 | -2.4699 | -2.4221 | -2.2173 | -2.5532 | 61.8347 | 0.24863 | 61.7614 | -0.014785 | 0.052814 | 61.4334 | 0.012299 | 61.207 | 58.7197 | 58.6349 | 58.6682 | 58.8292 | 58.877 | 59.0818 | 58.7459 | 123.1338 | 61.5478 | 123.0605 | 61.2843 | 61.3519 | 122.7325 | 61.3114 | 122.5061 | 61.7819 | 61.8224 | 61.7085 | 61.7491
7857.0781 | 123.3215 | -61.2762 | 61.7935 | -3.2295 | -3.3006 | -3.2765 | -3.1247 | -3.0722 | -2.9453 | -3.1942 | 61.8759 | 0.23032 | 61.7751 | -0.023943 | 0.048236 | 61.3968 | 0.012299 | 61.1658 | 58.0467 | 57.9756 | 57.9997 | 58.1516 | 58.2041 | 58.3309 | 58.0821 | 123.1522 | 61.5066 | 123.0513 | 61.2523 | 61.3245 | 122.673 | 61.2885 | 122.442 | 61.8277 | 61.8636 | 61.7269 | 61.7628
7858.0625 | 123.2391 | -61.3358 | 61.7889 | -2.6252 | -2.7237 | -2.6813 | -2.5111 | -2.4633 | -2.286 | -2.6128 | 61.8439 | 0.2349 | 61.7339 | -0.019364 | 0.048236 | 61.4288 | 0.012299 | 61.2116 | 58.7106 | 58.612 | 58.6544 | 58.8246 | 58.8725 | 59.0497 | 58.723 | 123.1796 | 61.5707 | 123.0696 | 61.3164 | 61.384 | 122.7646 | 61.3481 | 122.5473 | 61.7956 | 61.8316 | 61.6857 | 61.7216
7859.0938 | 123.2712 | -61.3358 | 61.7661 | -2.5794 | -2.6733 | -2.631 | -2.4837 | -2.4313 | -2.2586 | -2.5624 | 61.8301 | 0.2349 | 61.7293 | -0.019364 | 0.043657 | 61.4242 | 0.007721 | 61.207 | 58.7564 | 58.6624 | 58.7048 | 58.8521 | 58.9045 | 59.0772 | 58.7734 | 123.1659 | 61.5707 | 123.0651 | 61.3164 | 61.3794 | 122.76 | 61.3435 | 122.5428 | 61.7865 | 61.8224 | 61.6857 | 61.7216
7860.0625 | 123.2712 | -61.3174 | 61.8164 | -2.4649 | -2.5451 | -2.5165 | -2.3692 | -2.3214 | -2.0983 | -2.4342 | 61.8255 | 0.23948 | 61.7156 | -0.028522 | 0.052814 | 61.438 | 0.012299 | 61.2207 | 58.8525 | 58.7723 | 58.8009 | 58.9482 | 58.9961 | 59.2191 | 58.8832 | 123.143 | 61.5569 | 123.033 | 61.2889 | 61.3703 | 122.7554 | 61.3297 | 122.5382 | 61.7727 | 61.8132 | 61.6628 | 61.7033
7861.1094 | 123.317 | -61.3449 | 61.7477 | -2.6069 | -2.6962 | -2.663 | -2.4928 | -2.4496 | -2.2998 | -2.5807 | 61.8393 | 0.23032 | 61.7339 | -0.028522 | 0.043657 | 61.4288 | 0.012299 | 61.2024 | 58.738 | 58.6487 | 58.6819 | 58.8521 | 58.8953 | 59.0452 | 58.7642 | 123.1842 | 61.5752 | 123.0788 | 61.3164 | 61.3886 | 122.7737 | 61.3572 | 122.5473 | 61.7956 | 61.827 | 61.6902 | 61.7216
7862.0625 | 123.3444 | -61.2717 | 61.8027 | -3.0281 | -3.09 | -3.0659 | -2.9049 | -2.8662 | -2.7484 | -2.979 | 61.8668 | 0.23948 | 61.7843 | -0.019364 | 0.043657 | 61.4059 | 0.016878 | 61.1933 | 58.2436 | 58.1817 | 58.2057 | 58.3668 | 58.4055 | 58.5232 | 58.2927 | 123.1384 | 61.5111 | 123.0559 | 61.2523 | 61.3153 | 122.6776 | 61.2885 | 122.4649 | 61.8231 | 61.8499 | 61.7406 | 61.7674
7863.0938 | 123.3673 | -61.2396 | 61.8073 | -3.6095 | -3.6761 | -3.652 | -3.5138 | -3.4521 | -3.4077 | -3.5696 | 61.8988 | 0.23948 | 61.8117 | -0.023943 | 0.048236 | 61.3693 | 0.012299 | 61.1521 | 57.6301 | 57.5635 | 57.5876 | 57.7258 | 57.7875 | 57.8319 | 57.67 | 123.1384 | 61.4791 | 123.0513 | 61.2157 | 61.2879 | 122.6089 | 61.2519 | 122.3917 | 61.8506 | 61.8865 | 61.7635 | 61.7994
7864.0625 | 123.2666 | -61.2442 | 61.9171 | -3.756 | -3.8226 | -3.7893 | -3.6283 | -3.5986 | -3.5542 | -3.7161 | 61.908 | 0.23032 | 61.8071 | -0.033101 | 0.043657 | 61.3601 | 0.007721 | 61.1429 | 57.4882 | 57.4216 | 57.4549 | 57.6159 | 57.6456 | 57.69 | 57.5281 | 123.1522 | 61.4745 | 123.0513 | 61.2111 | 61.2879 | 122.6043 | 61.2519 | 122.3871 | 61.8643 | 61.9002 | 61.7635 | 61.7994
7865.0781 | 123.3398 | -61.2946 | 61.7798 | -2.7671 | -2.8519 | -2.8187 | -2.6393 | -2.5869 | -2.4051 | -2.7409 | 61.8393 | 0.23032 | 61.7385 | -0.023943 | 0.048236 | 61.4197 | 0.012299 | 61.1978 | 58.5274 | 58.4426 | 58.4759 | 58.6552 | 58.7077 | 58.8895 | 58.5536 | 123.1338 | 61.5249 | 123.033 | 61.2706 | 61.3428 | 122.7142 | 61.3069 | 122.4924 | 61.791 | 61.827 | 61.6902 | 61.7262
7866.0625 | 123.2071 | -61.3312 | 61.7706 | -2.236 | -2.3437 | -2.2967 | -2.1082 | -2.065 | -1.819 | -2.2282 | 61.8072 | 0.2349 | 61.711 | -0.023943 | 0.052814 | 61.4471 | 0.012299 | 61.2253 | 59.0952 | 58.9875 | 59.0345 | 59.2229 | 59.2662 | 59.5122 | 59.103 | 123.1384 | 61.5661 | 123.0422 | 61.3072 | 61.384 | 122.7783 | 61.3435 | 122.5565 | 61.7544 | 61.7949 | 61.6582 | 61.6987
7867.0781 | 123.3536 | -61.3174 | 61.734 | -2.4924 | -2.5726 | -2.5394 | -2.3738 | -2.3351 | -2.1212 | -2.4663 | 61.8255 | 0.2349 | 61.7293 | -0.023943 | 0.048236 | 61.4334 | 0.012299 | 61.2162 | 58.825 | 58.7448 | 58.7781 | 58.9437 | 58.9823 | 59.1962 | 58.8512 | 123.143 | 61.5523 | 123.0468 | 61.2935 | 61.3657 | 122.7508 | 61.3297 | 122.5336 | 61.7773 | 61.8132 | 61.6811 | 61.717
7868.0625 | 123.3994 | -61.2259 | 61.8256 | -3.2478 | -3.319 | -3.2949 | -3.1384 | -3.0905 | -2.9545 | -3.2125 | 61.8713 | 0.2349 | 61.7614 | -0.014785 | 0.048236 | 61.3922 | 0.012299 | 61.1704 | 57.978 | 57.9069 | 57.931 | 58.0875 | 58.1354 | 58.2714 | 58.0134 | 123.0972 | 61.4608 | 122.9873 | 61.2111 | 61.2741 | 122.6181 | 61.2382 | 122.3963 | 61.8231 | 61.859 | 61.7131 | 61.7491
7869.0938 | 123.3673 | -61.2671 | 61.8073 | -2.9411 | -3.0213 | -2.9881 | -2.8316 | -2.7929 | -2.6019 | -2.9012 | 61.8484 | 0.23032 | 61.7476 | -0.028522 | 0.048236 | 61.4059 | 0.012299 | 61.1887 | 58.326 | 58.2458 | 58.279 | 58.4355 | 58.4742 | 58.6652 | 58.3659 | 123.1155 | 61.4974 | 123.0147 | 61.2386 | 61.3153 | 122.673 | 61.2794 | 122.4558 | 61.8002 | 61.8361 | 61.6994 | 61.7353
7870.0625 | 123.3719 | -61.29 | 61.7889 | -2.964 | -3.058 | -3.0156 | -2.8362 | -2.7838 | -2.6202 | -2.9424 | 61.853 | 0.23032 | 61.7476 | -0.023943 | 0.052814 | 61.4105 | 0.012299 | 61.1887 | 58.326 | 58.232 | 58.2744 | 58.4538 | 58.5062 | 58.6697 | 58.3476 | 123.143 | 61.5203 | 123.0376 | 61.266 | 61.3428 | 122.7005 | 61.3023 | 122.4787 | 61.8002 | 61.8407 | 61.6948 | 61.7353
7871.0938 | 123.2986 | -61.3266 | 61.7523 | -3.5225 | -3.5891 | -3.5604 | -3.4177 | -3.3743 | -3.2337 | -3.4872 | 61.8805 | 0.23032 | 61.7751 | -0.019364 | 0.039079 | 61.3785 | 0.012299 | 61.1566 | 57.8041 | 57.7375 | 57.7662 | 57.9089 | 57.9523 | 58.0929 | 57.8394 | 123.2071 | 61.5569 | 123.1017 | 61.3072 | 61.3657 | 122.7051 | 61.3389 | 122.4832 | 61.8414 | 61.8682 | 61.736 | 61.7628
7872.0625 | 123.3353 | -61.2579 | 61.8027 | -3.6507 | -3.7219 | -3.6886 | -3.5871 | -3.5437 | -3.3619 | -3.6154 | 61.8851 | 0.22574 | 61.7843 | -0.019364 | 0.052814 | 61.3647 | 0.012299 | 61.1475 | 57.6072 | 57.536 | 57.5693 | 57.6708 | 57.7142 | 57.896 | 57.6426 | 123.143 | 61.4837 | 123.0422 | 61.2386 | 61.3107 | 122.6227 | 61.2702 | 122.4054 | 61.8323 | 61.8728 | 61.7314 | 61.772
7873.0938 | 123.3398 | -61.2671 | 61.8439 | -3.8659 | -3.9234 | -3.9038 | -3.7931 | -3.736 | -3.6 | -3.8214 | 61.8988 | 0.2349 | 61.8071 | -0.028522 | 0.052814 | 61.3601 | 0.012299 | 61.1429 | 57.4012 | 57.3437 | 57.3633 | 57.474 | 57.5311 | 57.6671 | 57.4457 | 123.1659 | 61.502 | 123.0742 | 61.2386 | 61.3199 | 122.6272 | 61.2794 | 122.41 | 61.846 | 61.8865 | 61.7543 | 61.7948
7874.0625 | 123.3582 | -61.2396 | 61.8301 | -3.5912 | -3.6624 | -3.6337 | -3.4955 | -3.443 | -3.3391 | -3.5513 | 61.8896 | 0.23948 | 61.8026 | -0.023943 | 0.052814 | 61.3785 | 0.012299 | 61.1566 | 57.6484 | 57.5773 | 57.6059 | 57.7441 | 57.7966 | 57.9006 | 57.6883 | 123.1293 | 61.4791 | 123.0422 | 61.2157 | 61.2924 | 122.6181 | 61.2519 | 122.3963 | 61.8368 | 61.8773 | 61.7498 | 61.7903
7875.0781 | 123.3078 | -61.2717 | 61.8027 | -3.4081 | -3.4838 | -3.4505 | -3.3032 | -3.2507 | -3.1559 | -3.3682 | 61.8805 | 0.23032 | 61.8026 | -0.019364 | 0.052814 | 61.383 | 0.016878 | 61.1704 | 57.8636 | 57.7879 | 57.8211 | 57.9684 | 58.021 | 58.1158 | 57.9035 | 123.1522 | 61.502 | 123.0742 | 61.2523 | 61.3245 | 122.6547 | 61.2885 | 122.442 | 61.8277 | 61.8636 | 61.7498 | 61.7857
7876.0625 | 123.2529 | -61.2671 | 61.8622 | -3.6553 | -3.7265 | -3.6978 | -3.5734 | -3.53 | -3.3757 | -3.6245 | 61.8942 | 0.23948 | 61.8117 | -0.019364 | 0.048236 | 61.3647 | 0.016878 | 61.1429 | 57.6118 | 57.5406 | 57.5693 | 57.6937 | 57.7371 | 57.8914 | 57.6426 | 123.1613 | 61.5066 | 123.0788 | 61.2477 | 61.3153 | 122.6318 | 61.284 | 122.41 | 61.846 | 61.8773 | 61.7635 | 61.7948
7877.0781 | 123.3582 | -61.2442 | 61.8393 | -3.4172 | -3.4929 | -3.4643 | -3.3124 | -3.2644 | -3.133 | -3.3773 | 61.8713 | 0.23032 | 61.7659 | -0.028522 | 0.048236 | 61.3876 | 0.012299 | 61.1658 | 57.827 | 57.7513 | 57.7799 | 57.9318 | 57.9798 | 58.1112 | 57.8669 | 123.1155 | 61.4745 | 123.0101 | 61.2157 | 61.2924 | 122.6318 | 61.2565 | 122.41 | 61.8231 | 61.859 | 61.7177 | 61.7536
7878.0625 | 123.3536 | -61.2762 | 61.8118 | -3.6553 | -3.7127 | -3.6886 | -3.5413 | -3.4933 | -3.3574 | -3.6108 | 61.8896 | 0.23032 | 61.7888 | -0.023943 | 0.052814 | 61.3647 | 0.026035 | 61.1475 | 57.6209 | 57.5635 | 57.5876 | 57.7349 | 57.7829 | 57.9189 | 57.6654 | 123.1659 | 61.5066 | 123.0651 | 61.2523 | 61.3291 | 122.641 | 61.3023 | 122.4237 | 61.8368 | 61.8636 | 61.736 | 61.7628
7879.0781 | 123.3582 | -61.2579 | 61.7752 | -3.1242 | -3.1953 | -3.1758 | -3.0285 | -2.9898 | -2.7576 | -3.0889 | 61.853 | 0.23032 | 61.7659 | -0.028522 | 0.039079 | 61.3968 | 0.012299 | 61.1795 | 58.1337 | 58.0626 | 58.0821 | 58.2294 | 58.2682 | 58.5003 | 58.169 | 123.111 | 61.4883 | 123.0239 | 61.2294 | 61.297 | 122.6547 | 61.2702 | 122.4375 | 61.8139 | 61.8407 | 61.7269 | 61.7536
7880.0625 | 123.3582 | -61.2762 | 61.7706 | -2.9869 | -3.0854 | -3.0293 | -2.8912 | -2.825 | -2.6386 | -2.9653 | 61.853 | 0.23032 | 61.7568 | -0.028522 | 0.048236 | 61.4059 | 0.012299 | 61.1933 | 58.2894 | 58.1908 | 58.2469 | 58.3851 | 58.4513 | 58.6377 | 58.311 | 123.1293 | 61.5066 | 123.033 | 61.2477 | 61.3245 | 122.6822 | 61.2885 | 122.4695 | 61.8048 | 61.8407 | 61.7085 | 61.7445
7881.1094 | 123.3444 | -61.3083 | 61.7203 | -3.17 | -3.2457 | -3.217 | -3.0514 | -2.9989 | -2.8171 | -3.1347 | 61.8668 | 0.23948 | 61.7797 | -0.03768 | 0.039079 | 61.4014 | 0.007721 | 61.1704 | 58.1383 | 58.0626 | 58.0913 | 58.2569 | 58.3094 | 58.4912 | 58.1736 | 123.175 | 61.5478 | 123.088 | 61.2706 | 61.3474 | 122.7096 | 61.316 | 122.4787 | 61.8277 | 61.859 | 61.7406 | 61.772
7882.0625 | 123.3765 | -61.2808 | 61.7523 | -2.7259 | -2.8061 | -2.7775 | -2.6348 | -2.5777 | -2.3318 | -2.6952 | 61.8484 | 0.2349 | 61.7614 | -0.028522 | 0.052814 | 61.4197 | 0.012299 | 61.2024 | 58.5549 | 58.4747 | 58.5033 | 58.6461 | 58.7031 | 58.949 | 58.5857 | 123.1293 | 61.5157 | 123.0422 | 61.2523 | 61.3336 | 122.7005 | 61.2931 | 122.4832 | 61.7956 | 61.8361 | 61.7085 | 61.7491
7883.0938 | 123.3948 | -61.2396 | 61.821 | -3.4081 | -3.4838 | -3.4643 | -3.3215 | -3.2782 | -3.1422 | -3.3773 | 61.8759 | 0.2349 | 61.7843 | -0.028522 | 0.043657 | 61.383 | 0.016878 | 61.1566 | 57.8315 | 57.7558 | 57.7754 | 57.9181 | 57.9614 | 58.0974 | 57.8623 | 123.1155 | 61.4745 | 123.0239 | 61.2111 | 61.2833 | 122.6227 | 61.2565 | 122.3963 | 61.8323 | 61.859 | 61.7406 | 61.7674
7884.0625 | 123.4634 | -61.1526 | 61.9263 | -3.6691 | -3.7356 | -3.7024 | -3.5688 | -3.5208 | -3.4352 | -3.62 | 61.8851 | 0.23032 | 61.7797 | -0.028522 | 0.043657 | 61.3739 | 0.012299 | 61.1475 | 57.4836 | 57.417 | 57.4503 | 57.5839 | 57.6318 | 57.7175 | 57.5327 | 123.0377 | 61.383 | 122.9323 | 61.1241 | 61.1963 | 122.5265 | 61.1649 | 122.3001 | 61.8414 | 61.8728 | 61.736 | 61.7674
7885.0938 | 123.3398 | -61.2305 | 61.8256 | -3.6462 | -3.699 | -3.6795 | -3.5321 | -3.4842 | -3.4077 | -3.5925 | 61.8896 | 0.22574 | 61.7888 | -0.033101 | 0.048236 | 61.3693 | 0.016878 | 61.1521 | 57.5843 | 57.5315 | 57.551 | 57.6983 | 57.7463 | 57.8227 | 57.638 | 123.1201 | 61.4562 | 123.0193 | 61.1974 | 61.2787 | 122.5998 | 61.2473 | 122.3825 | 61.8414 | 61.8728 | 61.7406 | 61.772
7886.0625 | 123.2574 | -61.2946 | 61.8576 | -2.7854 | -2.8702 | -2.8416 | -2.6943 | -2.6464 | -2.4737 | -2.7501 | 61.8347 | 0.22574 | 61.7339 | -0.023943 | 0.052814 | 61.4197 | 0.021456 | 61.2024 | 58.5091 | 58.4243 | 58.453 | 58.6003 | 58.6481 | 58.8208 | 58.5445 | 123.1293 | 61.5203 | 123.0284 | 61.2706 | 61.3474 | 122.7142 | 61.316 | 122.497 | 61.7819 | 61.8132 | 61.6811 | 61.7124
7887.0781 | 123.3536 | -61.2991 | 61.7294 | -2.9502 | -3.0213 | -3.0018 | -2.8866 | -2.8341 | -2.5974 | -2.9058 | 61.8439 | 0.2349 | 61.7476 | -0.023943 | 0.048236 | 61.4059 | 0.012299 | 61.1795 | 58.3489 | 58.2778 | 58.2973 | 58.4126 | 58.465 | 58.7018 | 58.3934 | 123.143 | 61.534 | 123.0468 | 61.2752 | 61.3474 | 122.7051 | 61.3114 | 122.4787 | 61.7956 | 61.8316 | 61.6994 | 61.7353
7888.0625 | 123.3444 | -61.203 | 61.8301 | -3.4264 | -3.4929 | -3.4688 | -3.3582 | -3.3056 | -3.1605 | -3.391 | 61.8805 | 0.22574 | 61.7751 | -0.023943 | 0.048236 | 61.3785 | 0.012299 | 61.1612 | 57.7766 | 57.7101 | 57.7342 | 57.8448 | 57.8974 | 58.0425 | 57.812 | 123.0835 | 61.4287 | 122.9781 | 61.1791 | 61.2512 | 122.5815 | 61.2153 | 122.3642 | 61.8323 | 61.8682 | 61.7269 | 61.7628
7889.0625 | 123.3673 | -61.2625 | 61.734 | -3.3211 | -3.3876 | -3.3635 | -3.2391 | -3.1912 | -3.0323 | -3.2903 | 61.8668 | 0.22574 | 61.7751 | -0.033101 | 0.043657 | 61.3922 | 0.012299 | 61.1704 | 57.9414 | 57.8749 | 57.899 | 58.0234 | 58.0713 | 58.2302 | 57.9722 | 123.1293 | 61.4883 | 123.0376 | 61.2294 | 61.3062 | 122.6547 | 61.2748 | 122.4329 | 61.8231 | 61.8545 | 61.7314 | 61.7628
7890.0938 | 123.3307 | -61.2396 | 61.7889 | -2.9731 | -3.0488 | -3.0156 | -2.9049 | -2.8478 | -2.6981 | -2.9424 | 61.853 | 0.2349 | 61.7385 | -0.023943 | 0.039079 | 61.4059 | 0.007721 | 61.1887 | 58.2665 | 58.1908 | 58.2241 | 58.3347 | 58.3918 | 58.5415 | 58.2972 | 123.0926 | 61.4745 | 122.9781 | 61.2157 | 61.2787 | 122.6456 | 61.2473 | 122.4283 | 61.8139 | 61.8453 | 61.6994 | 61.7308
7891.0625 | 123.2986 | -61.2854 | 61.853 | -3.3165 | -3.3831 | -3.359 | -3.23 | -3.1775 | -3.0415 | -3.2766 | 61.8713 | 0.22574 | 61.7797 | -0.023943 | 0.052814 | 61.3876 | 0.007721 | 61.1612 | 57.9689 | 57.9023 | 57.9264 | 58.0554 | 58.1079 | 58.2439 | 58.0088 | 123.1567 | 61.5111 | 123.0651 | 61.2615 | 61.3382 | 122.673 | 61.2931 | 122.4466 | 61.8185 | 61.8636 | 61.7269 | 61.772
7892.0781 | 123.3444 | -61.3129 | 61.7249 | -2.9274 | -3.0076 | -2.9835 | -2.8454 | -2.8021 | -2.5928 | -2.9012 | 61.853 | 0.22574 | 61.7568 | -0.028522 | 0.043657 | 61.4059 | 0.016878 | 61.1795 | 58.3855 | 58.3053 | 58.3294 | 58.4675 | 58.5108 | 58.7201 | 58.4117 | 123.1659 | 61.5386 | 123.0697 | 61.2843 | 61.3565 | 122.7188 | 61.3297 | 122.4924 | 61.8094 | 61.8361 | 61.7131 | 61.7399
7893.0625 | 123.3856 | -61.2076 | 61.8576 | -3.8201 | -3.8867 | -3.8626 | -3.7336 | -3.6856 | -3.5588 | -3.7756 | 61.9034 | 0.23948 | 61.8209 | -0.028522 | 0.048236 | 61.3601 | 0.021456 | 61.1338 | 57.3874 | 57.3209 | 57.345 | 57.474 | 57.522 | 57.6488 | 57.432 | 123.111 | 61.4471 | 123.0285 | 61.1791 | 61.2558 | 122.5677 | 61.229 | 122.3413 | 61.8551 | 61.8819 | 61.7726 | 61.7994
7894.0625 | 123.3627 | -61.2396 | 61.8393 | -3.7606 | -3.8318 | -3.8031 | -3.6787 | -3.6261 | -3.4627 | -3.7253 | 61.8988 | 0.23032 | 61.8117 | -0.023943 | 0.052814 | 61.3601 | 0.016878 | 61.1475 | 57.479 | 57.4078 | 57.4365 | 57.561 | 57.6135 | 57.777 | 57.5144 | 123.1384 | 61.4699 | 123.0513 | 61.2157 | 61.2924 | 122.5998 | 61.2565 | 122.3871 | 61.846 | 61.8819 | 61.7589 | 61.7948
7895.0938 | 123.3307 | -61.2442 | 61.853 | -3.7927 | -3.8501 | -3.8214 | -3.7199 | -3.6673 | -3.5222 | -3.7481 | 61.9034 | 0.23032 | 61.8071 | -0.028522 | 0.048236 | 61.3601 | 0.012299 | 61.1429 | 57.4515 | 57.3941 | 57.4228 | 57.5243 | 57.5769 | 57.722 | 57.4961 | 123.1476 | 61.4745 | 123.0513 | 61.2157 | 61.2924 | 122.6043 | 61.2565 | 122.3871 | 61.8551 | 61.8911 | 61.7589 | 61.7948
7896.0625 | 123.262 | -61.2259 | 61.94 | -4.017 | -4.0928 | -4.0595 | -3.9442 | -3.8962 | -3.7923 | -3.9862 | 61.908 | 0.22574 | 61.8163 | -0.023943 | 0.052814 | 61.3464 | 0.007721 | 61.1383 | 57.2089 | 57.1331 | 57.1664 | 57.2817 | 57.3297 | 57.4336 | 57.2397 | 123.1338 | 61.4516 | 123.0422 | 61.2019 | 61.2787 | 122.5723 | 61.2336 | 122.3642 | 61.8551 | 61.9002 | 61.7635 | 61.8086
7897.0938 | 123.3765 | -61.1893 | 61.8805 | -4.4886 | -4.5507 | -4.5219 | -4.4204 | -4.3677 | -4.3005 | -4.4486 | 61.94 | 0.23032 | 61.8392 | -0.023943 | 0.052814 | 61.3235 | 0.007721 | 61.1063 | 56.7007 | 56.6386 | 56.6673 | 56.7689 | 56.8215 | 56.8888 | 56.7407 | 123.1293 | 61.4196 | 123.0285 | 61.1653 | 61.2421 | 122.5128 | 61.197 | 122.2956 | 61.8872 | 61.9323 | 61.7864 | 61.8315
7898.0625 | 123.3673 | -61.1984 | 61.8484 | -3.5088 | -3.5754 | -3.5558 | -3.4268 | -3.3789 | -3.2154 | -3.4643 | 61.8896 | 0.23032 | 61.7934 | -0.023943 | 0.048236 | 61.383 | 0.016878 | 61.1566 | 57.6896 | 57.6231 | 57.6426 | 57.7716 | 57.8195 | 57.983 | 57.7341 | 123.0881 | 61.4287 | 122.9918 | 61.1745 | 61.2467 | 122.5815 | 61.2153 | 122.3551 | 61.8414 | 61.8728 | 61.7452 | 61.7765
7899.0781 | 123.3444 | -61.2808 | 61.8027 | -3.4539 | -3.5204 | -3.5009 | -3.3856 | -3.3468 | -3.1284 | -3.4139 | 61.8805 | 0.23032 | 61.8026 | -0.023943 | 0.052814 | 61.3785 | 0.016878 | 61.1521 | 57.827 | 57.7604 | 57.7799 | 57.8952 | 57.934 | 58.1524 | 57.8669 | 123.1613 | 61.5111 | 123.0834 | 61.2569 | 61.3336 | 122.6593 | 61.2977 | 122.4329 | 61.8277 | 61.8636 | 61.7498 | 61.7857
7900.0625 | 123.3673 | -61.1618 | 61.8851 | -4.2734 | -4.3538 | -4.3159 | -4.2189 | -4.18 | -4.067 | -4.2426 | 61.9308 | 0.23948 | 61.8529 | -0.014785 | 0.052814 | 61.3327 | 0.012299 | 61.1109 | 56.8884 | 56.808 | 56.8459 | 56.9429 | 56.9818 | 57.0948 | 56.9192 | 123.0927 | 61.4013 | 123.0147 | 61.147 | 61.2146 | 122.4945 | 61.1741 | 122.2727 | 61.878 | 61.9186 | 61.8001 | 61.8406
7901.1094 | 123.3627 | -61.2167 | 61.8256 | -3.2341 | -3.3144 | -3.2857 | -3.1704 | -3.1225 | -2.9224 | -3.2033 | 61.8668 | 0.24405 | 61.7843 | -0.023943 | 0.052814 | 61.3922 | 0.007721 | 61.1704 | 57.9826 | 57.9024 | 57.931 | 58.0463 | 58.0942 | 58.2943 | 58.0134 | 123.0835 | 61.4608 | 123.001 | 61.1928 | 61.2695 | 122.6089 | 61.2245 | 122.3871 | 61.8139 | 61.859 | 61.7314 | 61.7765
7902.0625 | 123.3765 | -61.2167 | 61.853 | -3.9392 | -4.0012 | -3.9816 | -3.8664 | -3.823 | -3.7419 | -3.8946 | 61.908 | 0.2349 | 61.8026 | -0.023943 | 0.043657 | 61.3464 | 0.012299 | 61.1383 | 57.2776 | 57.2155 | 57.2351 | 57.3504 | 57.3938 | 57.4748 | 57.3221 | 123.1247 | 61.4516 | 123.0193 | 61.1928 | 61.2604 | 122.5631 | 61.229 | 122.3551 | 61.8643 | 61.8957 | 61.7589 | 61.7903
7903.0781 | 123.3582 | -61.2305 | 61.8164 | -3.6187 | -3.6807 | -3.6566 | -3.5505 | -3.5117 | -3.3894 | -3.5696 | 61.8896 | 0.23032 | 61.7843 | -0.028522 | 0.048236 | 61.3693 | 0.007721 | 61.1475 | 57.6118 | 57.5498 | 57.5739 | 57.68 | 57.7188 | 57.8411 | 57.6609 | 123.1201 | 61.4608 | 123.0147 | 61.2019 | 61.2787 | 122.5998 | 61.2382 | 122.378 | 61.8414 | 61.8819 | 61.736 | 61.7765
7904.0625 | 123.3994 | -61.2442 | 61.7798 | -3.2707 | -3.3693 | -3.3086 | -3.23 | -3.1683 | -2.9728 | -3.24 | 61.8668 | 0.22574 | 61.7659 | -0.023943 | 0.034501 | 61.383 | 0.016878 | 61.1704 | 57.9735 | 57.8749 | 57.9356 | 58.0142 | 58.0759 | 58.2714 | 58.0042 | 123.111 | 61.4699 | 123.0101 | 61.2203 | 61.2787 | 122.6272 | 61.2611 | 122.4146 | 61.8323 | 61.8499 | 61.7314 | 61.7491
7905.0781 | 123.3444 | -61.2442 | 61.821 | -3.3165 | -3.3876 | -3.3635 | -3.2666 | -3.2232 | -3.046 | -3.2766 | 61.8668 | 0.23032 | 61.7659 | -0.028522 | 0.052814 | 61.3876 | 0.012299 | 61.1612 | 57.9277 | 57.8566 | 57.8807 | 57.9776 | 58.021 | 58.1982 | 57.9676 | 123.111 | 61.4745 | 123.0101 | 61.2157 | 61.297 | 122.6318 | 61.2565 | 122.4054 | 61.8139 | 61.8545 | 61.7131 | 61.7536
7906.0625 | 123.2803 | -61.203 | 61.8668 | -3.7744 | -3.8318 | -3.8168 | -3.7107 | -3.6673 | -3.5451 | -3.7298 | 61.8988 | 0.2349 | 61.8071 | -0.019364 | 0.052814 | 61.3601 | 0.016878 | 61.1429 | 57.4286 | 57.3712 | 57.3862 | 57.4923 | 57.5357 | 57.6579 | 57.4732 | 123.1018 | 61.4379 | 123.0101 | 61.1836 | 61.2558 | 122.5632 | 61.2199 | 122.3459 | 61.846 | 61.8819 | 61.7543 | 61.7903
7907.0781 | 123.3398 | -61.2854 | 61.7661 | -3.3623 | -3.4472 | -3.4093 | -3.3307 | -3.2782 | -3.0643 | -3.327 | 61.8805 | 0.23032 | 61.7797 | -0.023943 | 0.043657 | 61.383 | 0.007721 | 61.1612 | 57.9231 | 57.8382 | 57.8761 | 57.9547 | 58.0072 | 58.2211 | 57.9584 | 123.1659 | 61.5157 | 123.0651 | 61.2615 | 61.3291 | 122.6684 | 61.2931 | 122.4466 | 61.8368 | 61.8728 | 61.736 | 61.772
7908.0625 | 123.4085 | -61.2442 | 61.7798 | -3.6095 | -3.6853 | -3.6474 | -3.555 | -3.5025 | -3.3528 | -3.5604 | 61.8942 | 0.2349 | 61.8117 | -0.023943 | 0.048236 | 61.3739 | 0.016878 | 61.1521 | 57.6347 | 57.5589 | 57.5968 | 57.6892 | 57.7417 | 57.8914 | 57.6838 | 123.1384 | 61.4791 | 123.0559 | 61.2203 | 61.2924 | 122.6181 | 61.2611 | 122.3963 | 61.846 | 61.8773 | 61.7635 | 61.7948
7909.0781 | 123.3307 | -61.29 | 61.7889 | -3.2433 | -3.3098 | -3.2857 | -3.1842 | -3.1271 | -2.9133 | -3.2033 | 61.8713 | 0.2349 | 61.7888 | -0.028522 | 0.048236 | 61.3968 | 0.016878 | 61.1704 | 58.0467 | 57.9802 | 58.0043 | 58.1058 | 58.1629 | 58.3767 | 58.0866 | 123.1613 | 61.5249 | 123.0788 | 61.2615 | 61.3382 | 122.6867 | 61.3069 | 122.4604 | 61.8231 | 61.8545 | 61.7406 | 61.772
7910.0625 | 123.3582 | -61.2854 | 61.8301 | -3.3715 | -3.4472 | -3.4139 | -3.3078 | -3.2599 | -3.0369 | -3.3407 | 61.8805 | 0.2349 | 61.7843 | -0.019364 | 0.052814 | 61.383 | 0.016878 | 61.1658 | 57.9139 | 57.8382 | 57.8715 | 57.9776 | 58.0255 | 58.2485 | 57.9447 | 123.1659 | 61.5203 | 123.0697 | 61.266 | 61.3382 | 122.6684 | 61.3023 | 122.4512 | 61.8277 | 61.8636 | 61.7314 | 61.7674
7911.0938 | 123.3124 | -61.3174 | 61.7386 | -2.6298 | -2.71 | -2.6813 | -2.534 | -2.5045 | -2.2128 | -2.5944 | 61.8301 | 0.2349 | 61.7339 | -0.028522 | 0.048236 | 61.4242 | 0.007721 | 61.207 | 58.6877 | 58.6075 | 58.6361 | 58.7834 | 58.8129 | 59.1047 | 58.723 | 123.1476 | 61.5523 | 123.0513 | 61.2889 | 61.3657 | 122.7417 | 61.3252 | 122.5244 | 61.7819 | 61.8224 | 61.6857 | 61.7262
7912.0625 | 123.3856 | -61.2534 | 61.8347 | -3.7927 | -3.8364 | -3.8306 | -3.7153 | -3.6719 | -3.4993 | -3.7436 | 61.8988 | 0.23032 | 61.798 | -0.023943 | 0.043657 | 61.3601 | 0.012299 | 61.1429 | 57.4607 | 57.417 | 57.4228 | 57.5381 | 57.5815 | 57.7541 | 57.5098 | 123.1522 | 61.4837 | 123.0513 | 61.2294 | 61.297 | 122.6135 | 61.2657 | 122.3963 | 61.8551 | 61.8865 | 61.7543 | 61.7857
7913.0781 | 123.2849 | -61.2854 | 61.8439 | -3.9895 | -4.0699 | -4.032 | -3.9396 | -3.8779 | -3.6962 | -3.9542 | 61.9034 | 0.22574 | 61.7934 | -0.023943 | 0.048236 | 61.3556 | 0.012299 | 61.1246 | 57.2959 | 57.2155 | 57.2534 | 57.3458 | 57.4075 | 57.5892 | 57.3312 | 123.1888 | 61.5111 | 123.0788 | 61.2615 | 61.3336 | 122.641 | 61.2977 | 122.41 | 61.8551 | 61.8911 | 61.7452 | 61.7811
7914.0625 | 123.3032 | -61.2396 | 61.8713 | -4.1452 | -4.2027 | -4.1785 | -4.0907 | -4.0427 | -3.8701 | -4.0961 | 61.9171 | 0.23948 | 61.8346 | -0.023943 | 0.052814 | 61.3418 | 0.012299 | 61.12 | 57.0944 | 57.037 | 57.0611 | 57.1489 | 57.1969 | 57.3695 | 57.1435 | 123.1567 | 61.4791 | 123.0742 | 61.2157 | 61.2924 | 122.5815 | 61.2519 | 122.3596 | 61.8643 | 61.9048 | 61.7818 | 61.8223
7915.0938 | 123.2758 | -61.2259 | 61.8759 | -4.2414 | -4.2942 | -4.2838 | -4.1731 | -4.1297 | -4.0258 | -4.1968 | 61.9308 | 0.2349 | 61.8392 | -0.023943 | 0.043657 | 61.3281 | 0.012299 | 61.1154 | 56.9845 | 56.9316 | 56.9421 | 57.0528 | 57.0962 | 57.2001 | 57.0291 | 123.1567 | 61.4608 | 123.0651 | 61.2019 | 61.2695 | 122.554 | 61.2382 | 122.3413 | 61.8872 | 61.9186 | 61.7955 | 61.8269
7916.0625 | 123.2803 | -61.2122 | 61.9034 | -4.2871 | -4.3583 | -4.3205 | -4.2143 | -4.1617 | -4.0945 | -4.2426 | 61.9308 | 0.24405 | 61.8575 | -0.023943 | 0.048236 | 61.3327 | 0.012299 | 61.1063 | 56.925 | 56.8538 | 56.8917 | 56.9978 | 57.0504 | 57.1177 | 56.9696 | 123.143 | 61.4562 | 123.0697 | 61.1882 | 61.2604 | 122.5448 | 61.2245 | 122.3184 | 61.8826 | 61.9186 | 61.8093 | 61.8452
7917.0781 | 123.2529 | -61.235 | 61.8759 | -3.8293 | -3.8913 | -3.8718 | -3.7748 | -3.7268 | -3.4901 | -3.7802 | 61.9034 | 0.2349 | 61.8209 | -0.028522 | 0.048236 | 61.3556 | 0.012299 | 61.1292 | 57.4057 | 57.3437 | 57.3633 | 57.4602 | 57.5082 | 57.7449 | 57.4549 | 123.1384 | 61.4699 | 123.0559 | 61.2065 | 61.2833 | 122.5906 | 61.2473 | 122.3642 | 61.8551 | 61.8911 | 61.7726 | 61.8086
7918.0625 | 123.2986 | -61.1847 | 61.8988 | -4.2322 | -4.2988 | -4.2701 | -4.164 | -4.1159 | -3.9251 | -4.1877 | 61.9217 | 0.23032 | 61.8209 | -0.019364 | 0.043657 | 61.3327 | 0.021456 | 61.1154 | 56.9525 | 56.8859 | 56.9146 | 57.0207 | 57.0687 | 57.2596 | 56.997 | 123.1064 | 61.415 | 123.0056 | 61.1653 | 61.2283 | 122.5174 | 61.2061 | 122.3001 | 61.878 | 61.9002 | 61.7772 | 61.7994
7919.0781 | 123.3536 | -61.2808 | 61.7615 | -4.3604 | -4.4362 | -4.3937 | -4.3288 | -4.267 | -4.0853 | -4.3204 | 61.9263 | 0.23032 | 61.8163 | -0.023943 | 0.043657 | 61.3281 | 0.003143 | 61.1017 | 56.9204 | 56.8446 | 56.8871 | 56.952 | 57.0138 | 57.1955 | 56.9604 | 123.2071 | 61.5111 | 123.0971 | 61.2569 | 61.3245 | 122.6089 | 61.284 | 122.3825 | 61.8826 | 61.9231 | 61.7726 | 61.8132
7920.0625 | 123.2391 | -61.235 | 61.8668 | -4.2459 | -4.3171 | -4.2838 | -4.196 | -4.1388 | -3.9342 | -4.206 | 61.9171 | 0.23032 | 61.83 | -0.023943 | 0.048236 | 61.3327 | 0.007721 | 61.1154 | 56.9891 | 56.9179 | 56.9512 | 57.039 | 57.0962 | 57.3008 | 57.0291 | 123.1522 | 61.4654 | 123.0651 | 61.2111 | 61.2833 | 122.5677 | 61.2428 | 122.3505 | 61.8689 | 61.9094 | 61.7818 | 61.8223
7921.0938 | 123.2803 | -61.2808 | 61.8256 | -3.6004 | -3.6624 | -3.6474 | -3.5505 | -3.5162 | -3.2704 | -3.5559 | 61.8805 | 0.23032 | 61.7797 | -0.028522 | 0.048236 | 61.3693 | 0.016878 | 61.1429 | 57.6804 | 57.6185 | 57.6334 | 57.7304 | 57.7646 | 58.0104 | 57.725 | 123.1613 | 61.5111 | 123.0605 | 61.2523 | 61.3291 | 122.6501 | 61.2977 | 122.4237 | 61.8323 | 61.8636 | 61.7314 | 61.7628
7922.0625 | 123.3398 | -61.1847 | 61.8622 | -4.1544 | -4.2072 | -4.1923 | -4.0724 | -4.0244 | -3.7923 | -4.1007 | 61.9125 | 0.23948 | 61.8163 | -0.028522 | 0.048236 | 61.3464 | 0.012299 | 61.12 | 57.0303 | 56.9774 | 56.9924 | 57.1123 | 57.1603 | 57.3924 | 57.084 | 123.0972 | 61.4242 | 123.001 | 61.1562 | 61.2329 | 122.5311 | 61.197 | 122.3047 | 61.8643 | 61.9002 | 61.7681 | 61.804
7923.0938 | 123.2758 | -61.2259 | 61.8713 | -4.2734 | -4.3263 | -4.3113 | -4.2189 | -4.1755 | -4.0258 | -4.2243 | 61.9217 | 0.23032 | 61.8209 | -0.028522 | 0.048236 | 61.3281 | 0.007721 | 61.1109 | 56.9525 | 56.8996 | 56.9146 | 57.007 | 57.0504 | 57.2001 | 57.0016 | 123.1476 | 61.4562 | 123.0468 | 61.1974 | 61.2741 | 122.554 | 61.2336 | 122.3368 | 61.8735 | 61.914 | 61.7726 | 61.8132
7924.0625 | 123.3307 | -61.2442 | 61.7523 | -3.8613 | -3.9371 | -3.8992 | -3.8481 | -3.7863 | -3.5451 | -3.826 | 61.9034 | 0.23032 | 61.8163 | -0.023943 | 0.043657 | 61.3556 | 0.012299 | 61.1246 | 57.3829 | 57.3071 | 57.345 | 57.3961 | 57.4579 | 57.6991 | 57.4182 | 123.1476 | 61.4745 | 123.0605 | 61.2203 | 61.2879 | 122.5998 | 61.2565 | 122.3688 | 61.8597 | 61.8911 | 61.7726 | 61.804
7925.0938 | 123.3215 | -61.1847 | 61.9034 | -4.4886 | -4.5552 | -4.5219 | -4.4616 | -4.4135 | -4.241 | -4.444 | 61.9446 | 0.23948 | 61.8621 | -0.023943 | 0.048236 | 61.3144 | 0.007721 | 61.1017 | 56.6961 | 56.6295 | 56.6628 | 56.7231 | 56.7712 | 56.9437 | 56.7407 | 123.1293 | 61.4242 | 123.0468 | 61.1607 | 61.2329 | 122.4991 | 61.1924 | 122.2864 | 61.8963 | 61.9369 | 61.8138 | 61.8544
7926.0625 | 123.2941 | -61.1893 | 61.8805 | -4.4291 | -4.4866 | -4.467 | -4.3837 | -4.3311 | -4.1861 | -4.3799 | 61.94 | 0.23948 | 61.8621 | -0.023943 | 0.052814 | 61.3189 | 0.012299 | 61.1017 | 56.7602 | 56.7027 | 56.7223 | 56.8055 | 56.8582 | 57.0032 | 56.8093 | 123.1293 | 61.4287 | 123.0514 | 61.1653 | 61.2421 | 122.5082 | 61.2016 | 122.291 | 61.8872 | 61.9277 | 61.8093 | 61.8498
7927.0781 | 123.23 | -61.2076 | 61.8851 | -4.1544 | -4.2118 | -4.1877 | -4.1136 | -4.0656 | -3.8564 | -4.1052 | 61.9217 | 0.23948 | 61.8392 | -0.019364 | 0.043657 | 61.3373 | 0.003143 | 61.1109 | 57.0532 | 56.9958 | 57.0199 | 57.094 | 57.142 | 57.3512 | 57.1023 | 123.1293 | 61.4471 | 123.0468 | 61.1882 | 61.2512 | 122.5448 | 61.2107 | 122.3184 | 61.878 | 61.9185 | 61.7955 | 61.8361
7928.0625 | 123.349 | -61.2122 | 61.8439 | -4.4108 | -4.4637 | -4.4441 | -4.3609 | -4.3082 | -4.1723 | -4.357 | 61.9308 | 0.23032 | 61.8255 | -0.023943 | 0.043657 | 61.3281 | 0.016878 | 61.1017 | 56.8014 | 56.7485 | 56.7681 | 56.8513 | 56.9039 | 57.0398 | 56.8551 | 123.143 | 61.4425 | 123.0376 | 61.1882 | 61.2558 | 122.5403 | 61.229 | 122.3139 | 61.8872 | 61.914 | 61.7818 | 61.8086
7929.0938 | 123.2391 | -61.2259 | 61.8805 | -3.6599 | -3.7127 | -3.6886 | -3.5917 | -3.5529 | -3.3436 | -3.6016 | 61.8896 | 0.23948 | 61.7934 | -0.023943 | 0.043657 | 61.3739 | 0.012299 | 61.1475 | 57.566 | 57.5132 | 57.5373 | 57.6342 | 57.673 | 57.8823 | 57.6242 | 123.1155 | 61.4654 | 123.0193 | 61.2019 | 61.2695 | 122.5998 | 61.2382 | 122.3734 | 61.846 | 61.8773 | 61.7498 | 61.7811
7930.0625 | 123.3444 | -61.3037 | 61.7523 | -3.9804 | -4.0653 | -4.0274 | -3.9534 | -3.9008 | -3.7007 | -3.9542 | 61.9171 | 0.2349 | 61.8117 | -0.028522 | 0.048236 | 61.3418 | 0.012299 | 61.12 | 57.3233 | 57.2384 | 57.2763 | 57.3503 | 57.4029 | 57.603 | 57.3495 | 123.2208 | 61.5386 | 123.1154 | 61.2752 | 61.3519 | 122.6455 | 61.316 | 122.4237 | 61.8689 | 61.9048 | 61.7635 | 61.7994
7931.1094 | 123.262 | -61.1801 | 61.94 | -4.8594 | -4.9261 | -4.8928 | -4.7958 | -4.7431 | -4.5386 | -4.8149 | 61.9583 | 0.2349 | 61.8804 | -0.023943 | 0.057392 | 61.3006 | 0.021456 | 61.088 | 56.3207 | 56.254 | 56.2873 | 56.3843 | 56.437 | 56.6415 | 56.3653 | 123.1384 | 61.415 | 123.0605 | 61.1562 | 61.2375 | 122.4807 | 61.2016 | 122.2681 | 61.9009 | 61.9369 | 61.823 | 61.8589
7932.0625 | 123.3536 | -61.235 | 61.8256 | -4.1452 | -4.2118 | -4.1785 | -4.0861 | -4.029 | -3.8381 | -4.1052 | 61.9263 | 0.23948 | 61.8346 | -0.033101 | 0.052814 | 61.3464 | 0.016878 | 61.12 | 57.0898 | 57.0232 | 57.0565 | 57.1489 | 57.2061 | 57.3969 | 57.1298 | 123.1613 | 61.4745 | 123.0697 | 61.2019 | 61.2879 | 122.5815 | 61.2519 | 122.3551 | 61.8735 | 61.9094 | 61.7818 | 61.8177
7933.0938 | 123.2437 | -61.2259 | 61.8759 | -4.2047 | -4.2805 | -4.2381 | -4.1457 | -4.0931 | -3.8701 | -4.1648 | 61.9308 | 0.24405 | 61.8529 | -0.028522 | 0.048236 | 61.3373 | 0.016878 | 61.1154 | 57.0212 | 56.9454 | 56.9878 | 57.0802 | 57.1328 | 57.3557 | 57.0611 | 123.1567 | 61.4699 | 123.0788 | 61.1974 | 61.2741 | 122.5631 | 61.2428 | 122.3413 | 61.8826 | 61.914 | 61.8047 | 61.8361
7934.0625 | 123.3353 | -61.1801 | 61.8759 | -4.7083 | -4.7613 | -4.7371 | -4.6859 | -4.6333 | -4.4699 | -4.6592 | 61.9537 | 0.2349 | 61.8758 | -0.028522 | 0.048236 | 61.3052 | 0.012299 | 61.0834 | 56.4718 | 56.4188 | 56.443 | 56.4942 | 56.5469 | 56.7102 | 56.5209 | 123.1339 | 61.415 | 123.0559 | 61.1516 | 61.2284 | 122.4853 | 61.1924 | 122.2635 | 61.9055 | 61.9414 | 61.8276 | 61.8635
7935.0781 | 123.23 | -61.1938 | 61.9263 | -4.9785 | -5.0452 | -5.0164 | -4.9789 | -4.94 | -4.7629 | -4.9431 | 61.9721 | 0.2349 | 61.8941 | -0.023943 | 0.057392 | 61.2961 | 0.012299 | 61.0697 | 56.2154 | 56.1487 | 56.1774 | 56.2149 | 56.2539 | 56.4309 | 56.2508 | 123.1659 | 61.4287 | 123.088 | 61.1699 | 61.2512 | 122.4899 | 61.2061 | 122.2635 | 61.9147 | 61.9598 | 61.8367 | 61.8818
7936.0625 | 123.3444 | -61.1664 | 61.8851 | -4.7999 | -4.8529 | -4.8195 | -4.7958 | -4.7431 | -4.5844 | -4.7462 | 61.9583 | 0.2349 | 61.8758 | -0.023943 | 0.052814 | 61.2961 | 0.007721 | 61.0834 | 56.3665 | 56.3135 | 56.3468 | 56.3706 | 56.4233 | 56.582 | 56.4202 | 123.1247 | 61.4013 | 123.0422 | 61.1424 | 61.2192 | 122.4624 | 61.1741 | 122.2498 | 61.9055 | 61.9506 | 61.823 | 61.8681
7937.0938 | 123.262 | -61.1526 | 61.9354 | -5.5325 | -5.5855 | -5.5613 | -5.5284 | -5.4756 | -5.4085 | -5.4833 | 62.0041 | 0.22574 | 61.9124 | -0.028522 | 0.039079 | 61.264 | 0.003143 | 61.0422 | 55.6202 | 55.5672 | 55.5914 | 55.6243 | 55.6771 | 55.7442 | 55.6694 | 123.1568 | 61.3784 | 123.0651 | 61.1241 | 61.1917 | 122.4167 | 61.1558 | 122.1948 | 61.965 | 62.001 | 61.8734 | 61.9093
7938.0625 | 123.3627 | -61.1069 | 61.908 | -5.5004 | -5.5443 | -5.5338 | -5.4963 | -5.4527 | -5.3856 | -5.4466 | 61.9995 | 0.2349 | 61.9033 | -0.028522 | 0.039079 | 61.2503 | 0.003143 | 61.0376 | 55.6065 | 55.5626 | 55.5731 | 55.6106 | 55.6542 | 55.7213 | 55.6602 | 123.1064 | 61.3418 | 123.0102 | 61.0784 | 61.146 | 122.3571 | 61.11 | 122.1445 | 61.9604 | 61.9964 | 61.8642 | 61.9001
7939.0938 | 123.2712 | -61.1847 | 61.9308 | -5.2349 | -5.2787 | -5.2545 | -5.2308 | -5.1735 | -5.0972 | -5.1765 | 61.9812 | 0.2349 | 61.885 | -0.023943 | 0.052814 | 61.2686 | 0.007721 | 61.0513 | 55.9498 | 55.906 | 55.9302 | 55.9539 | 56.0112 | 56.0875 | 56.0082 | 123.1659 | 61.4196 | 123.0697 | 61.1607 | 61.2375 | 122.4533 | 61.1924 | 122.236 | 61.9284 | 61.9735 | 61.8322 | 61.8773
7940.0625 | 123.3261 | -61.1069 | 61.9354 | -5.4913 | -5.5259 | -5.5246 | -5.4963 | -5.4527 | -5.3719 | -5.4283 | 61.9904 | 0.2349 | 61.8941 | -0.023943 | 0.048236 | 61.264 | 0.012299 | 61.0376 | 55.6156 | 55.5809 | 55.5822 | 55.6106 | 55.6542 | 55.735 | 55.6785 | 123.0972 | 61.3418 | 123.001 | 61.0829 | 61.1551 | 122.3709 | 61.1192 | 122.1445 | 61.9421 | 61.9781 | 61.8459 | 61.8818
7941.0938 | 123.2803 | -61.1069 | 61.9812 | -5.7293 | -5.7732 | -5.7581 | -5.7573 | -5.7137 | -5.6374 | -5.6756 | 62.0133 | 0.23032 | 61.9124 | -0.019364 | 0.052814 | 61.2549 | 0.003143 | 61.033 | 55.3775 | 55.3337 | 55.3487 | 55.3496 | 55.3932 | 55.4695 | 55.4313 | 123.1201 | 61.3372 | 123.0193 | 61.0875 | 61.1597 | 122.3617 | 61.11 | 122.1399 | 61.9604 | 62.0101 | 61.8596 | 61.9093
7942.0625 | 123.349 | -61.116 | 61.8988 | -5.45 | -5.4893 | -5.4697 | -5.4826 | -5.4344 | -5.3307 | -5.3871 | 61.9858 | 0.23032 | 61.8896 | -0.028522 | 0.052814 | 61.2594 | 0.007721 | 61.0468 | 55.666 | 55.6267 | 55.6463 | 55.6334 | 55.6816 | 55.7854 | 55.7289 | 123.1018 | 61.3463 | 123.0056 | 61.0875 | 61.1688 | 122.3755 | 61.1237 | 122.1628 | 61.933 | 61.9781 | 61.8367 | 61.8818
7943.0938 | 123.262 | -61.1664 | 61.9537 | -5.5645 | -5.6129 | -5.5887 | -5.565 | -5.5351 | -5.468 | -5.5107 | 62.0087 | 0.2349 | 61.8987 | -0.028522 | 0.048236 | 61.2549 | 0.016878 | 61.0422 | 55.6019 | 55.5534 | 55.5776 | 55.6014 | 55.6313 | 55.6984 | 55.6556 | 123.1751 | 61.4013 | 123.0651 | 61.1379 | 61.2146 | 122.4212 | 61.1833 | 122.2086 | 61.9604 | 61.9918 | 61.8505 | 61.8818
7944.0625 | 123.3765 | -61.1252 | 61.908 | -5.5737 | -5.6221 | -5.5933 | -5.5787 | -5.526 | -5.4634 | -5.5245 | 62.0041 | 0.22574 | 61.8941 | -0.028522 | 0.043657 | 61.2549 | 0.012299 | 61.0285 | 55.5515 | 55.5031 | 55.5319 | 55.5465 | 55.5992 | 55.6618 | 55.6007 | 123.1293 | 61.3509 | 123.0193 | 61.0967 | 61.1688 | 122.38 | 61.1375 | 122.1536 | 61.9604 | 61.9918 | 61.8505 | 61.8818
7945.0938 | 123.262 | -61.1664 | 61.9766 | -5.6286 | -5.6725 | -5.6437 | -5.6245 | -5.5855 | -5.5413 | -5.5703 | 61.9995 | 0.2349 | 61.9079 | -0.019364 | 0.052814 | 61.2457 | 0.012299 | 61.033 | 55.5378 | 55.4939 | 55.5227 | 55.5419 | 55.5809 | 55.6251 | 55.5961 | 123.1659 | 61.4013 | 123.0743 | 61.147 | 61.2192 | 122.4121 | 61.1787 | 122.1994 | 61.9467 | 61.9872 | 61.8551 | 61.8956
7946.0625 | 123.3582 | -61.1298 | 61.94 | -5.7202 | -5.7686 | -5.749 | -5.7298 | -5.6862 | -5.6557 | -5.6664 | 62.0133 | 0.2349 | 61.9262 | -0.028522 | 0.052814 | 61.2457 | 0.007721 | 61.0285 | 55.4096 | 55.3611 | 55.3808 | 55.3999 | 55.4436 | 55.474 | 55.4634 | 123.143 | 61.3647 | 123.0559 | 61.1012 | 61.1826 | 122.3755 | 61.1375 | 122.1582 | 61.9604 | 62.0055 | 61.8734 | 61.9185
7947.0938 | 123.3902 | -61.116 | 61.9263 | -5.3127 | -5.3611 | -5.3369 | -5.2903 | -5.2467 | -5.175 | -5.2589 | 61.9904 | 0.23948 | 61.9079 | -0.023943 | 0.048236 | 61.2777 | 0.003143 | 61.0559 | 55.8033 | 55.7549 | 55.7791 | 55.8257 | 55.8693 | 55.941 | 55.8571 | 123.1064 | 61.3555 | 123.0239 | 61.0921 | 61.1643 | 122.3938 | 61.1192 | 122.172 | 61.9421 | 61.9872 | 61.8596 | 61.9047
7948.0625 | 123.3261 | -61.1343 | 61.9537 | -5.4729 | -5.5214 | -5.5063 | -5.4551 | -5.4161 | -5.3444 | -5.4238 | 61.9995 | 0.2349 | 61.9079 | -0.028522 | 0.043657 | 61.2686 | 0.007721 | 61.033 | 55.6614 | 55.613 | 55.628 | 55.6792 | 55.7183 | 55.79 | 55.7106 | 123.1339 | 61.3692 | 123.0422 | 61.1058 | 61.178 | 122.4029 | 61.1421 | 122.1674 | 61.9559 | 61.9918 | 61.8642 | 61.9001
7949.0781 | 123.2712 | -61.084 | 61.9995 | -6.2192 | -6.2631 | -6.2389 | -6.2197 | -6.1714 | -6.141 | -6.1608 | 62.0407 | 0.23948 | 61.9537 | -0.023943 | 0.048236 | 61.2228 | 0.007721 | 60.9918 | 54.8648 | 54.8209 | 54.8451 | 54.8643 | 54.9125 | 54.943 | 54.9231 | 123.1247 | 61.3235 | 123.0376 | 61.06 | 61.1322 | 122.3068 | 61.0917 | 122.0758 | 61.9925 | 62.033 | 61.9054 | 61.9459
7950.0625 | 123.3398 | -61.1069 | 61.9537 | -5.8392 | -5.8831 | -5.8772 | -5.8672 | -5.8235 | -5.7748 | -5.79 | 62.0178 | 0.22116 | 61.917 | -0.023943 | 0.039079 | 61.2365 | 0.012299 | 61.0193 | 55.2677 | 55.2238 | 55.2297 | 55.2397 | 55.2834 | 55.3321 | 55.3169 | 123.1247 | 61.328 | 123.0239 | 61.0829 | 61.146 | 122.3434 | 61.1192 | 122.1262 | 61.9788 | 62.0055 | 61.8779 | 61.9047
7951.0938 | 123.262 | -61.1435 | 61.9766 | -5.8713 | -5.9243 | -5.8863 | -5.8901 | -5.8464 | -5.7839 | -5.8175 | 62.0224 | 0.23948 | 61.917 | -0.023943 | 0.043657 | 61.2411 | 0.012299 | 61.0193 | 55.2722 | 55.2192 | 55.2571 | 55.2534 | 55.2971 | 55.3596 | 55.326 | 123.1659 | 61.383 | 123.0605 | 61.1196 | 61.1872 | 122.3846 | 61.1558 | 122.1628 | 61.9788 | 62.0101 | 61.8734 | 61.9047
7952.0625 | 123.4085 | -61.0931 | 61.9492 | -5.9033 | -5.9609 | -5.9321 | -5.945 | -5.8922 | -5.8297 | -5.8541 | 62.0178 | 0.22574 | 61.917 | -0.023943 | 0.043657 | 61.2411 | 0.012299 | 61.0147 | 55.1898 | 55.1322 | 55.161 | 55.1481 | 55.2009 | 55.2634 | 55.239 | 123.111 | 61.3189 | 123.0102 | 61.0692 | 61.1368 | 122.3343 | 61.1054 | 122.1079 | 61.9742 | 62.0055 | 61.8734 | 61.9047
7953.0938 | 123.3124 | -61.1389 | 61.8942 | -5.4958 | -5.5534 | -5.5292 | -5.5055 | -5.4619 | -5.3398 | -5.4512 | 61.9949 | 0.23032 | 61.8896 | -0.023943 | 0.052814 | 61.2594 | 0.003143 | 61.0422 | 55.6431 | 55.5855 | 55.6097 | 55.6334 | 55.6771 | 55.7991 | 55.6877 | 123.1339 | 61.3692 | 123.0285 | 61.115 | 61.1917 | 122.3983 | 61.1421 | 122.1811 | 61.9421 | 61.9918 | 61.8367 | 61.8864
7954.0625 | 123.3444 | -61.1938 | 61.8713 | -5.7202 | -5.7595 | -5.7398 | -5.7115 | -5.6633 | -5.5916 | -5.6572 | 62.0133 | 0.21658 | 61.9033 | -0.033101 | 0.052814 | 61.2503 | 0.003143 | 61.0239 | 55.4737 | 55.4344 | 55.454 | 55.4823 | 55.5306 | 55.6022 | 55.5366 | 123.2071 | 61.4104 | 123.0971 | 61.1607 | 61.2467 | 122.4441 | 61.197 | 122.2177 | 61.9604 | 62.0101 | 61.8505 | 61.9001
7955.0781 | 123.2712 | -61.1206 | 61.9675 | -5.3951 | -5.4618 | -5.4285 | -5.3773 | -5.3245 | -5.2437 | -5.3551 | 61.9904 | 0.2349 | 61.8941 | -0.033101 | 0.043657 | 61.2732 | 0.007721 | 61.0513 | 55.7255 | 55.6588 | 55.6921 | 55.7433 | 55.7961 | 55.8769 | 55.7655 | 123.111 | 61.3555 | 123.0147 | 61.0875 | 61.1643 | 122.3938 | 61.1283 | 122.172 | 61.9467 | 61.9827 | 61.8505 | 61.8864
7956.0625 | 123.2712 | -61.1023 | 62.0132 | -5.9766 | -6.025 | -6.0008 | -5.9908 | -5.9517 | -5.8846 | -5.9228 | 62.0224 | 0.23948 | 61.9216 | -0.023943 | 0.052814 | 61.2411 | 0.012299 | 61.0239 | 55.1257 | 55.0773 | 55.1015 | 55.1115 | 55.1506 | 55.2177 | 55.1795 | 123.1247 | 61.3418 | 123.0239 | 61.0784 | 61.1551 | 122.3434 | 61.1146 | 122.1262 | 61.9696 | 62.0101 | 61.8688 | 61.9093
7957.0781 | 123.2574 | -61.1206 | 61.9583 | -5.4638 | -5.5214 | -5.4789 | -5.4963 | -5.439 | -5.2528 | -5.4192 | 61.9949 | 0.2349 | 61.8941 | -0.019364 | 0.048236 | 61.2594 | 0.007721 | 61.0422 | 55.6568 | 55.5992 | 55.6418 | 55.6243 | 55.6816 | 55.8678 | 55.7014 | 123.1156 | 61.3555 | 123.0147 | 61.1012 | 61.1688 | 122.38 | 61.1283 | 122.1628 | 61.9467 | 61.9872 | 61.8459 | 61.8864
7958.0625 | 123.349 | -61.1252 | 61.9217 | -5.917 | -5.9701 | -5.9367 | -5.9633 | -5.9151 | -5.7015 | -5.8724 | 62.0087 | 0.2349 | 61.917 | -0.033101 | 0.048236 | 61.2274 | 0.016878 | 61.0147 | 55.2081 | 55.1551 | 55.1885 | 55.1619 | 55.2101 | 55.4237 | 55.2528 | 123.1339 | 61.3601 | 123.0422 | 61.0921 | 61.1734 | 122.3526 | 61.1421 | 122.1399 | 61.9604 | 61.9918 | 61.8688 | 61.9001
7959.0781 | 123.2666 | -61.2259 | 61.8851 | -4.919 | -4.9856 | -4.9523 | -4.9561 | -4.8988 | -4.5981 | -4.8744 | 61.9537 | 0.23032 | 61.8621 | -0.028522 | 0.048236 | 61.2915 | 0.012299 | 61.0788 | 56.3069 | 56.2402 | 56.2736 | 56.2698 | 56.3271 | 56.6278 | 56.3515 | 123.1796 | 61.4562 | 123.088 | 61.1974 | 61.2741 | 122.5174 | 61.2382 | 122.3047 | 61.9055 | 61.9414 | 61.8138 | 61.8498
7960.0625 | 123.3856 | -61.1572 | 61.8622 | -4.9464 | -5.0177 | -4.9889 | -4.9835 | -4.9354 | -4.6622 | -4.911 | 61.9629 | 0.22574 | 61.8667 | -0.023943 | 0.048236 | 61.2961 | 0.007721 | 61.0651 | 56.2108 | 56.1395 | 56.1683 | 56.1737 | 56.2218 | 56.495 | 56.2462 | 123.1201 | 61.383 | 123.0239 | 61.1333 | 61.2055 | 122.4533 | 61.1649 | 122.2223 | 61.9147 | 61.9552 | 61.8184 | 61.8589
7961.1094 | 123.2529 | -61.1389 | 61.9583 | -5.9766 | -6.0342 | -5.9962 | -6.0274 | -5.97 | -5.7381 | -5.9274 | 62.0224 | 0.22574 | 61.9216 | -0.023943 | 0.052814 | 61.2365 | 0.012299 | 61.0193 | 55.1624 | 55.1047 | 55.1427 | 55.1115 | 55.1689 | 55.4008 | 55.2116 | 123.1613 | 61.3647 | 123.0605 | 61.115 | 61.1917 | 122.3755 | 61.1512 | 122.1582 | 61.9696 | 62.0101 | 61.8688 | 61.9093
7962.0625 | 123.3444 | -61.0474 | 61.9812 | -6.1826 | -6.2402 | -6.2114 | -6.2426 | -6.2035 | -5.9625 | -6.1425 | 62.0316 | 0.2349 | 61.9308 | -0.028522 | 0.057392 | 61.2274 | 0.007721 | 61.001 | 54.8648 | 54.8071 | 54.8359 | 54.8047 | 54.8439 | 55.0849 | 54.9048 | 123.0789 | 61.2823 | 122.9781 | 61.0188 | 61.1048 | 122.2747 | 61.0551 | 122.0483 | 61.9742 | 62.0239 | 61.8734 | 61.923
7963.0938 | 123.23 | -61.1252 | 61.9812 | -6.1231 | -6.1899 | -6.129 | -6.1922 | -6.1165 | -5.8892 | -6.0876 | 62.0362 | 0.23948 | 61.9353 | -0.023943 | 0.052814 | 61.2228 | 0.007721 | 61.0101 | 55.0021 | 54.9353 | 54.9962 | 54.9329 | 55.0087 | 55.236 | 55.0376 | 123.1613 | 61.3647 | 123.0605 | 61.1012 | 61.178 | 122.348 | 61.1329 | 122.1353 | 61.9833 | 62.0284 | 61.8825 | 61.9276
7964.0625 | 123.3398 | -61.0886 | 61.9308 | -5.7888 | -5.8327 | -5.8085 | -5.8397 | -5.8006 | -5.5092 | -5.7259 | 62.0133 | 0.23948 | 61.917 | -0.028522 | 0.043657 | 61.2503 | 0.016878 | 61.0285 | 55.2997 | 55.2558 | 55.2801 | 55.2489 | 55.2879 | 55.5794 | 55.3626 | 123.1018 | 61.328 | 123.0056 | 61.06 | 61.1322 | 122.3388 | 61.1054 | 122.117 | 61.9696 | 61.9964 | 61.8734 | 61.9001
7965.0938 | 123.2483 | -61.1572 | 61.94 | -5.418 | -5.471 | -5.4468 | -5.4688 | -5.4115 | -5.1017 | -5.3826 | 61.9949 | 0.2349 | 61.9033 | -0.028522 | 0.048236 | 61.264 | 0.003143 | 61.0468 | 55.7392 | 55.6862 | 55.7104 | 55.6884 | 55.7457 | 56.0555 | 55.7747 | 123.1522 | 61.3921 | 123.0605 | 61.1287 | 61.2055 | 122.4212 | 61.1604 | 122.204 | 61.9467 | 61.9918 | 61.8551 | 61.9001
7966.0625 | 123.2529 | -61.1298 | 61.972 | -5.8438 | -5.8968 | -5.8589 | -5.9038 | -5.8464 | -5.5321 | -5.7992 | 62.0133 | 0.2349 | 61.9308 | -0.023943 | 0.048236 | 61.2365 | 0.007721 | 61.0239 | 55.286 | 55.2329 | 55.2709 | 55.226 | 55.2833 | 55.5977 | 55.3306 | 123.143 | 61.3647 | 123.0605 | 61.1058 | 61.178 | 122.3663 | 61.1375 | 122.1536 | 61.965 | 62.0055 | 61.8825 | 61.923
7967.0781 | 123.3032 | -61.0703 | 62.0132 | -5.885 | -5.9243 | -5.9138 | -5.9267 | -5.883 | -5.6557 | -5.8404 | 62.0178 | 0.2349 | 61.9308 | -0.023943 | 0.048236 | 61.2365 | 0.012299 | 61.0239 | 55.1853 | 55.1459 | 55.1564 | 55.1436 | 55.1872 | 55.4145 | 55.2299 | 123.0881 | 61.3051 | 123.001 | 61.0463 | 61.1185 | 122.3068 | 61.0825 | 122.0941 | 61.9696 | 62.0055 | 61.8825 | 61.9185
7968.0625 | 123.3765 | -61.1481 | 61.8759 | -5.7431 | -5.7961 | -5.7673 | -5.7893 | -5.7411 | -5.5092 | -5.7076 | 62.0133 | 0.2349 | 61.9262 | -0.028522 | 0.048236 | 61.2457 | 0.007721 | 61.0285 | 55.405 | 55.352 | 55.3808 | 55.3587 | 55.407 | 55.6389 | 55.4405 | 123.1613 | 61.383 | 123.0743 | 61.1195 | 61.1963 | 122.3938 | 61.1558 | 122.1765 | 61.965 | 62.0055 | 61.8779 | 61.9185
7969.0781 | 123.2849 | -61.1618 | 61.972 | -5.5874 | -5.6313 | -5.6071 | -5.6154 | -5.5763 | -5.3078 | -5.5428 | 62.0087 | 0.2349 | 61.9216 | -0.023943 | 0.057392 | 61.2594 | 0.012299 | 61.0422 | 55.5744 | 55.5305 | 55.5548 | 55.5464 | 55.5855 | 55.854 | 55.619 | 123.1705 | 61.3967 | 123.0834 | 61.1379 | 61.2192 | 122.4212 | 61.1741 | 122.204 | 61.9513 | 61.9964 | 61.8642 | 61.9093
7970.0625 | 123.3536 | -61.1069 | 61.94 | -5.6973 | -5.7411 | -5.7215 | -5.7436 | -5.7091 | -5.4085 | -5.6572 | 62.0133 | 0.2349 | 61.9353 | -0.028522 | 0.052814 | 61.2549 | 0.007721 | 61.0239 | 55.4096 | 55.3657 | 55.3854 | 55.3633 | 55.3978 | 55.6984 | 55.4496 | 123.1201 | 61.3418 | 123.0422 | 61.0784 | 61.1597 | 122.3617 | 61.1146 | 122.1308 | 61.9604 | 62.0055 | 61.8825 | 61.9276
7971.1094 | 123.4268 | -61.116 | 61.9446 | -5.4913 | -5.5443 | -5.5246 | -5.5696 | -5.5076 | -5.1979 | -5.4466 | 61.9995 | 0.23948 | 61.9079 | -0.028522 | 0.057392 | 61.264 | 0.012299 | 61.0376 | 55.6248 | 55.5718 | 55.5914 | 55.5465 | 55.6084 | 55.9182 | 55.6694 | 123.1156 | 61.3555 | 123.0239 | 61.0875 | 61.1734 | 122.38 | 61.1283 | 122.1536 | 61.9421 | 61.9872 | 61.8505 | 61.8956
7972.0625 | 123.2666 | -61.2213 | 61.8713 | -4.7816 | -4.8437 | -4.8104 | -4.8416 | -4.7843 | -4.4241 | -4.737 | 61.9583 | 0.24863 | 61.8804 | -0.023943 | 0.043657 | 61.3006 | 0.012299 | 61.0834 | 56.4397 | 56.3776 | 56.4109 | 56.3797 | 56.437 | 56.7972 | 56.4843 | 123.1796 | 61.4699 | 123.1017 | 61.1974 | 61.265 | 122.5219 | 61.2336 | 122.3047 | 61.9147 | 61.946 | 61.8367 | 61.8681
7973.0781 | 123.262 | -61.1618 | 61.908 | -4.7404 | -4.7933 | -4.7737 | -4.8004 | -4.7431 | -4.3326 | -4.6958 | 61.9537 | 0.24863 | 61.885 | -0.023943 | 0.048236 | 61.3006 | 0.012299 | 61.088 | 56.4214 | 56.3685 | 56.3881 | 56.3614 | 56.4187 | 56.8292 | 56.466 | 123.1155 | 61.4104 | 123.0468 | 61.1379 | 61.21 | 122.4624 | 61.1741 | 122.2498 | 61.9055 | 61.9414 | 61.8367 | 61.8727
7974.0625 | 123.2849 | -61.1069 | 62.0178 | -5.679 | -5.7274 | -5.6986 | -5.7664 | -5.7137 | -5.3947 | -5.6435 | 62.0133 | 0.23948 | 61.9124 | -0.023943 | 0.052814 | 61.2457 | 0.016878 | 61.033 | 55.4279 | 55.3795 | 55.4082 | 55.3404 | 55.3932 | 55.7121 | 55.4634 | 123.1201 | 61.3463 | 123.0193 | 61.0829 | 61.1597 | 122.3526 | 61.1238 | 122.1399 | 61.9604 | 61.9964 | 61.8596 | 61.8956
7975.0781 | 123.2986 | -61.0657 | 62.0544 | -6.8419 | -6.8767 | -6.8524 | -6.9523 | -6.9039 | -6.608 | -6.7835 | 62.0774 | 0.24405 | 61.9857 | -0.023943 | 0.057392 | 61.1862 | 0.007721 | 60.9689 | 54.2238 | 54.189 | 54.2132 | 54.1134 | 54.1618 | 54.4577 | 54.2822 | 123.143 | 61.3097 | 123.0514 | 61.0417 | 61.1231 | 122.2519 | 61.0734 | 122.0346 | 62.02 | 62.0696 | 61.9283 | 61.978
7976.0625 | 123.3948 | -61.0703 | 62.0041 | -6.5397 | -6.5882 | -6.564 | -6.6409 | -6.5926 | -6.3013 | -6.4951 | 62.059 | 0.23032 | 61.9628 | -0.028522 | 0.043657 | 61.2045 | 0.012299 | 60.9781 | 54.5305 | 54.482 | 54.5063 | 54.4293 | 54.4776 | 54.769 | 54.5752 | 123.1293 | 61.3006 | 123.0331 | 61.0417 | 61.1139 | 122.2747 | 61.0825 | 122.0483 | 62.0154 | 62.0467 | 61.9192 | 61.9505
7977.0938 | 123.2803 | -61.1343 | 61.9812 | -6.7961 | -6.8355 | -6.8066 | -6.8744 | -6.8353 | -6.5485 | -6.7469 | 62.0728 | 0.2349 | 61.9674 | -0.019364 | 0.048236 | 61.1862 | 0.016878 | 60.9735 | 54.3382 | 54.2989 | 54.3277 | 54.2599 | 54.2991 | 54.5858 | 54.3875 | 123.2071 | 61.3692 | 123.1017 | 61.115 | 61.1826 | 122.3205 | 61.1512 | 122.1079 | 62.0245 | 62.0559 | 61.9191 | 61.9505
7978.0625 | 123.3673 | -61.0291 | 62.0087 | -6.9792 | -7.0186 | -7.0035 | -7.0576 | -7.0229 | -6.8049 | -6.9254 | 62.0819 | 0.2349 | 61.9765 | -0.033101 | 0.052814 | 61.1724 | 0.007721 | 60.9506 | 54.0498 | 54.0104 | 54.0255 | 53.9715 | 54.0061 | 54.2242 | 54.1037 | 123.111 | 61.2639 | 123.0056 | 60.996 | 61.0819 | 122.2015 | 61.0368 | 121.9797 | 62.0291 | 62.0742 | 61.9237 | 61.9688
7979.0938 | 123.2346 | -61.0977 | 61.9949 | -6.3566 | -6.3959 | -6.3763 | -6.4532 | -6.4049 | -6.1319 | -6.3073 | 62.0499 | 0.2349 | 61.9491 | -0.023943 | 0.048236 | 61.2091 | 0.012299 | 60.9873 | 54.7411 | 54.7018 | 54.7215 | 54.6445 | 54.6928 | 54.9658 | 54.7904 | 123.1476 | 61.3326 | 123.0468 | 61.0738 | 61.146 | 122.3068 | 61.11 | 122.085 | 62.0017 | 62.0376 | 61.9008 | 61.9368
7980.0625 | 123.143 | -61.1206 | 61.9308 | -6.5946 | -6.634 | -6.6098 | -6.7005 | -6.6521 | -6.4249 | -6.5408 | 62.0682 | 0.23032 | 61.9811 | -0.028522 | 0.039079 | 61.1999 | 0.021456 | 60.9781 | 54.526 | 54.4866 | 54.5108 | 54.4201 | 54.4685 | 54.6957 | 54.5798 | 123.1888 | 61.3509 | 123.1017 | 61.0921 | 61.1597 | 122.3205 | 61.1421 | 122.0987 | 62.0291 | 62.0467 | 61.942 | 61.9597
7981.1094 | 123.2574 | -61.1114 | 62.0178 | -6.265 | -6.3043 | -6.2755 | -6.3525 | -6.3042 | -6.0357 | -6.2112 | 62.0453 | 0.24405 | 61.972 | -0.028522 | 0.057392 | 61.2274 | 0.016878 | 61.0056 | 54.8464 | 54.8071 | 54.8359 | 54.759 | 54.8072 | 55.0757 | 54.9002 | 123.1568 | 61.3555 | 123.0834 | 61.0829 | 61.1688 | 122.3388 | 61.1283 | 122.117 | 61.9879 | 62.0284 | 61.9146 | 61.9551
7982.0625 | 123.2849 | -61.1343 | 61.9675 | -6.1597 | -6.2036 | -6.184 | -6.2838 | -6.2401 | -5.9075 | -6.1059 | 62.0407 | 0.24405 | 61.9445 | -0.023943 | 0.039079 | 61.2228 | 0.007721 | 60.9918 | 54.9746 | 54.9307 | 54.9504 | 54.8505 | 54.8942 | 55.2268 | 55.0284 | 123.1751 | 61.3784 | 123.0788 | 61.1104 | 61.1734 | 122.3571 | 61.1421 | 122.1262 | 62.0017 | 62.033 | 61.9054 | 61.9368
7983.0938 | 123.2986 | -61.1252 | 61.9812 | -5.9354 | -5.9884 | -5.955 | -6.0595 | -6.0204 | -5.7061 | -5.8862 | 62.0133 | 0.2349 | 61.9308 | -0.033101 | 0.052814 | 61.232 | 0.012299 | 61.0147 | 55.1898 | 55.1368 | 55.1702 | 55.0657 | 55.1048 | 55.4191 | 55.239 | 123.1384 | 61.3601 | 123.0559 | 61.0921 | 61.178 | 122.3571 | 61.1375 | 122.1399 | 61.9604 | 62.001 | 61.8779 | 61.9185
7984.0625 | 123.2803 | -61.1343 | 61.9583 | -6.3154 | -6.3501 | -6.335 | -6.4258 | -6.3866 | -6.109 | -6.2478 | 62.0453 | 0.23032 | 61.9353 | -0.023943 | 0.043657 | 61.2182 | 0.007721 | 60.9918 | 54.819 | 54.7842 | 54.7993 | 54.7086 | 54.7477 | 55.0254 | 54.8865 | 123.1797 | 61.3647 | 123.0697 | 61.1104 | 61.178 | 122.3526 | 61.1421 | 122.1262 | 62.0017 | 62.0376 | 61.8917 | 61.9276
7985.0938 | 123.3032 | -61.084 | 62.0361 | -5.9033 | -5.9564 | -5.9276 | -6.0137 | -5.9654 | -5.6603 | -5.8587 | 62.0178 | 0.23032 | 61.917 | -0.023943 | 0.052814 | 61.232 | 0.007721 | 61.0193 | 55.1807 | 55.1276 | 55.1564 | 55.0703 | 55.1185 | 55.4237 | 55.2253 | 123.1018 | 61.3143 | 123.001 | 61.06 | 61.1368 | 122.3159 | 61.0917 | 122.1033 | 61.965 | 62.0101 | 61.8642 | 61.9093
7986.0625 | 123.3444 | -61.1206 | 61.9125 | -5.9308 | -5.9792 | -5.9504 | -6.0457 | -5.9975 | -5.6695 | -5.8862 | 62.0316 | 0.2349 | 61.9308 | -0.028522 | 0.048236 | 61.2411 | 0.012299 | 61.0147 | 55.1898 | 55.1414 | 55.1702 | 55.0749 | 55.1231 | 55.4512 | 55.2345 | 123.1522 | 61.3555 | 123.0514 | 61.0921 | 61.1688 | 122.3617 | 61.1329 | 122.1353 | 61.9833 | 62.0193 | 61.8825 | 61.9185
7987.0938 | 123.3215 | -61.0611 | 62.027 | -6.4848 | -6.5333 | -6.509 | -6.6364 | -6.5789 | -6.3516 | -6.4493 | 62.0682 | 0.23948 | 61.9811 | -0.023943 | 0.048236 | 61.2091 | 0.016878 | 60.9873 | 54.5763 | 54.5278 | 54.5521 | 54.4247 | 54.4822 | 54.7095 | 54.6118 | 123.1293 | 61.3006 | 123.0422 | 61.0372 | 61.1093 | 122.2702 | 61.078 | 122.0483 | 62.02 | 62.0513 | 61.9329 | 61.9642
7988.0625 | 123.23 | -61.1481 | 61.9492 | -6.2879 | -6.3272 | -6.303 | -6.3937 | -6.3454 | -6.1136 | -6.2524 | 62.0407 | 0.23948 | 61.9537 | -0.023943 | 0.048236 | 61.2091 | 0.007721 | 60.9964 | 54.8602 | 54.8208 | 54.8451 | 54.7544 | 54.8027 | 55.0345 | 54.8957 | 123.1888 | 61.3875 | 123.1017 | 61.1241 | 61.1963 | 122.3571 | 61.1558 | 122.1445 | 61.9925 | 62.033 | 61.9054 | 61.9459
7989.0938 | 123.2712 | -61.1069 | 61.9995 | -6.5214 | -6.5562 | -6.5411 | -6.6181 | -6.5789 | -6.3699 | -6.4767 | 62.0728 | 0.23032 | 61.9765 | -0.028522 | 0.048236 | 61.1953 | 0.012299 | 60.9873 | 54.5855 | 54.5507 | 54.5658 | 54.4888 | 54.528 | 54.7369 | 54.6301 | 123.1797 | 61.3372 | 123.0834 | 61.0784 | 61.1551 | 122.3022 | 61.1192 | 122.0941 | 62.0245 | 62.0605 | 61.9283 | 61.9642
7990.0625 | 123.2666 | -61.1572 | 61.9812 | -6.6771 | -6.7119 | -6.7013 | -6.792 | -6.7391 | -6.489 | -6.6324 | 62.0682 | 0.24405 | 61.9765 | -0.028522 | 0.052814 | 61.1953 | 0.007721 | 60.9781 | 54.4802 | 54.4454 | 54.4559 | 54.3652 | 54.4181 | 54.6682 | 54.5248 | 123.2254 | 61.4013 | 123.1338 | 61.1287 | 61.21 | 122.3526 | 61.1649 | 122.1353 | 62.0154 | 62.0605 | 61.9237 | 61.9688
7991.1094 | 123.2758 | -61.0291 | 62.0453 | -7.0433 | -7.0782 | -7.0539 | -7.1629 | -7.1191 | -6.869 | -6.9849 | 62.0819 | 0.23948 | 61.9903 | -0.028522 | 0.052814 | 61.1679 | 0.012299 | 60.9506 | 53.9857 | 53.9509 | 53.9752 | 53.8662 | 53.91 | 54.1601 | 54.0441 | 123.111 | 61.2685 | 123.0193 | 61.0005 | 61.0819 | 122.1969 | 61.0414 | 121.9797 | 62.0291 | 62.0696 | 61.9375 | 61.978
7992.0625 | 123.349 | -61.0519 | 61.9858 | -6.4115 | -6.4554 | -6.4266 | -6.499 | -6.4553 | -6.2326 | -6.3669 | 62.0453 | 0.2349 | 61.9491 | -0.023943 | 0.052814 | 61.2091 | 0.007721 | 60.9918 | 54.6404 | 54.5965 | 54.6253 | 54.5529 | 54.5967 | 54.8193 | 54.6851 | 123.0973 | 61.2868 | 123.001 | 61.028 | 61.1048 | 122.261 | 61.0597 | 122.0438 | 61.9925 | 62.0376 | 61.8963 | 61.9414
7993.0938 | 123.2208 | -61.1664 | 61.9537 | -5.8713 | -5.9151 | -5.9001 | -5.9771 | -5.9334 | -5.5916 | -5.8266 | 62.0178 | 0.23032 | 61.9216 | -0.028522 | 0.048236 | 61.2457 | 0.007721 | 61.0147 | 55.2951 | 55.2512 | 55.2663 | 55.1893 | 55.233 | 55.5748 | 55.3397 | 123.1842 | 61.3967 | 123.088 | 61.1379 | 61.2146 | 122.4121 | 61.1741 | 122.1811 | 61.9696 | 62.0101 | 61.8734 | 61.9139
7994.0625 | 123.2803 | -61.0519 | 62.0453 | -7.3272 | -7.3529 | -7.3378 | -7.4651 | -7.4167 | -7.2032 | -7.2688 | 62.0957 | 0.2349 | 61.9949 | -0.023943 | 0.052814 | 61.1541 | 0.003143 | 60.9369 | 53.7248 | 53.699 | 53.7142 | 53.5869 | 53.6353 | 53.8487 | 53.7832 | 123.1476 | 61.2868 | 123.0468 | 61.028 | 61.1048 | 122.2061 | 61.0551 | 121.9888 | 62.0429 | 62.0925 | 61.942 | 61.9917
7995.0938 | 123.2574 | -61.0107 | 62.0956 | -7.9041 | -7.9207 | -7.9101 | -8.0191 | -7.9843 | -7.7755 | -7.8456 | 62.1323 | 0.22574 | 62.0315 | -0.028522 | 0.048236 | 61.1175 | 0.007721 | 60.8957 | 53.1067 | 53.0901 | 53.1007 | 52.9917 | 53.0264 | 53.2352 | 53.1651 | 123.143 | 61.2365 | 123.0422 | 60.9822 | 61.059 | 122.1283 | 61.0185 | 121.9064 | 62.0841 | 62.1246 | 61.9832 | 62.0238
7996.0625 | 123.3307 | -60.9512 | 62.0682 | -7.7484 | -7.7696 | -7.759 | -7.8817 | -7.8378 | -7.6748 | -7.7174 | 62.1186 | 0.23032 | 62.0132 | -0.028522 | 0.048236 | 61.1312 | -0.001436 | 60.9094 | 53.2028 | 53.1817 | 53.1922 | 53.0695 | 53.1134 | 53.2764 | 53.2338 | 123.0698 | 61.1816 | 122.9644 | 60.9227 | 60.9995 | 122.0825 | 60.9498 | 121.8607 | 62.0703 | 62.12 | 61.9649 | 62.0146
7997.0781 | 123.2391 | -61.0062 | 62.114 | -7.5103 | -7.5406 | -7.5301 | -7.6436 | -7.586 | -7.4184 | -7.4656 | 62.114 | 0.2349 | 62.0132 | -0.033101 | 0.052814 | 61.145 | 0.012299 | 60.9323 | 53.4958 | 53.4655 | 53.4761 | 53.3625 | 53.4201 | 53.5878 | 53.5405 | 123.1202 | 61.2411 | 123.0193 | 60.9731 | 61.059 | 122.1511 | 61.0185 | 121.9385 | 62.0612 | 62.1017 | 61.9604 | 62.0009
7998.0625 | 123.3719 | -61.0611 | 61.9949 | -7.3409 | -7.3758 | -7.3469 | -7.4605 | -7.4121 | -7.2307 | -7.3008 | 62.1003 | 0.23032 | 61.9903 | -0.028522 | 0.039079 | 61.1587 | 0.007721 | 60.9415 | 53.7202 | 53.6853 | 53.7142 | 53.6006 | 53.649 | 53.8304 | 53.7603 | 123.1614 | 61.2914 | 123.0514 | 61.0326 | 61.1002 | 122.2198 | 61.0688 | 122.0026 | 62.0612 | 62.0925 | 61.9512 | 61.9826
7999.0781 | 123.2758 | -61.0016 | 62.1323 | -7.5378 | -7.5773 | -7.5575 | -7.6757 | -7.6227 | -7.4459 | -7.4977 | 62.1094 | 0.22574 | 62.004 | -0.023943 | 0.052814 | 61.1404 | 0.007721 | 60.9369 | 53.4638 | 53.4243 | 53.4441 | 53.3259 | 53.3789 | 53.5557 | 53.5039 | 123.111 | 61.2273 | 123.0056 | 60.9776 | 61.0544 | 122.142 | 61.0093 | 121.9385 | 62.0566 | 62.1017 | 61.9512 | 61.9963
8000.0625 | 123.2574 | -61.0565 | 62.0544 | -7.8491 | -7.8886 | -7.8735 | -7.9687 | -7.934 | -7.7435 | -7.7953 | 62.1277 | 0.2349 | 62.0315 | -0.033101 | 0.052814 | 61.1312 | 0.007721 | 60.9048 | 53.2074 | 53.1679 | 53.1831 | 53.0878 | 53.1226 | 53.3131 | 53.2613 | 123.1842 | 61.2914 | 123.088 | 61.0234 | 61.1093 | 122.1878 | 61.0642 | 121.9614 | 62.0749 | 62.12 | 61.9787 | 62.0238
8001.0938 | 123.2483 | -61.0886 | 62.0819 | -7.2722 | -7.3254 | -7.2782 | -7.4193 | -7.3617 | -7.1437 | -7.2413 | 62.1003 | 0.23948 | 62.0086 | -0.023943 | 0.052814 | 61.1633 | 0.012299 | 60.9369 | 53.8163 | 53.7631 | 53.8103 | 53.6693 | 53.7268 | 53.9449 | 53.8473 | 123.1888 | 61.328 | 123.0972 | 61.0646 | 61.1414 | 122.2519 | 61.1009 | 122.0255 | 62.0474 | 62.088 | 61.9558 | 61.9963
8002.0625 | 123.262 | -61.0657 | 62.0453 | -7.3272 | -7.362 | -7.3378 | -7.4605 | -7.4121 | -7.1849 | -7.2733 | 62.1048 | 0.2349 | 62.0223 | -0.028522 | 0.052814 | 61.1541 | 0.007721 | 60.9369 | 53.7385 | 53.7036 | 53.7279 | 53.6052 | 53.6536 | 53.8808 | 53.7923 | 123.1705 | 61.3006 | 123.088 | 61.0372 | 61.1185 | 122.2198 | 61.0734 | 122.0026 | 62.052 | 62.0971 | 61.9695 | 62.0146
8003.0938 | 123.2849 | -61.0519 | 62.027 | -6.9609 | -6.9912 | -6.9669 | -7.0851 | -7.0458 | -6.8095 | -6.9071 | 62.0911 | 0.23948 | 61.9949 | -0.028522 | 0.043657 | 61.1724 | 0.012299 | 60.9598 | 54.091 | 54.0608 | 54.085 | 53.9669 | 54.0061 | 54.2425 | 54.1449 | 123.143 | 61.2914 | 123.0468 | 61.0234 | 61.0956 | 122.2244 | 61.0642 | 122.0117 | 62.0474 | 62.0788 | 61.9512 | 61.9826
8004.0625 | 123.3719 | -61.0703 | 61.9629 | -7.9407 | -7.971 | -7.9513 | -8.074 | -8.0347 | -7.8625 | -7.8822 | 62.1277 | 0.23032 | 62.0406 | -0.033101 | 0.048236 | 61.1267 | 0.007721 | 60.9003 | 53.1296 | 53.0992 | 53.119 | 52.9962 | 53.0356 | 53.2078 | 53.188 | 123.198 | 61.3006 | 123.1109 | 61.0371 | 61.1185 | 122.1969 | 61.078 | 121.9705 | 62.0795 | 62.12 | 61.9924 | 62.0329
8005.0625 | 123.3078 | -61.0565 | 62.0407 | -7.2585 | -7.2934 | -7.2737 | -7.3689 | -7.3159 | -7.1208 | -7.2138 | 62.0911 | 0.23032 | 61.9903 | -0.028522 | 0.052814 | 61.1633 | 0.012299 | 60.9415 | 53.798 | 53.7632 | 53.7829 | 53.6876 | 53.7406 | 53.9357 | 53.8427 | 123.1476 | 61.2868 | 123.0468 | 61.028 | 61.1093 | 122.2198 | 61.0688 | 121.998 | 62.0383 | 62.0788 | 61.9375 | 61.978
8006.1094 | 123.2574 | -61.0107 | 62.1048 | -7.5653 | -7.5956 | -7.5713 | -7.6803 | -7.6364 | -7.455 | -7.516 | 62.1094 | 0.23032 | 62.0132 | -0.023943 | 0.043657 | 61.1496 | 0.016878 | 60.9186 | 53.4455 | 53.4152 | 53.4395 | 53.3305 | 53.3743 | 53.5557 | 53.4948 | 123.1202 | 61.2411 | 123.0239 | 60.9868 | 61.0544 | 122.1603 | 61.0276 | 121.9293 | 62.0658 | 62.0925 | 61.9695 | 61.9963
8007.0625 | 123.3124 | -61.084 | 62.1094 | -7.8033 | -7.8337 | -7.8094 | -7.9138 | -7.8561 | -7.6656 | -7.754 | 62.1323 | 0.2349 | 62.0315 | -0.019364 | 0.052814 | 61.1312 | 0.007721 | 60.9094 | 53.2806 | 53.2503 | 53.2746 | 53.1702 | 53.2278 | 53.4184 | 53.3299 | 123.2163 | 61.3189 | 123.1155 | 61.0646 | 61.1368 | 122.2152 | 61.0917 | 121.9934 | 62.0795 | 62.1246 | 61.9787 | 62.0238
8008.0938 | 123.2346 | -61.0519 | 62.1094 | -7.6568 | -7.6917 | -7.672 | -7.7856 | -7.7417 | -7.5374 | -7.6075 | 62.114 | 0.23948 | 62.0406 | -0.019364 | 0.039079 | 61.1267 | 0.007721 | 60.9186 | 53.3951 | 53.3602 | 53.3799 | 53.2664 | 53.3103 | 53.5145 | 53.4444 | 123.1659 | 61.2914 | 123.0926 | 61.0326 | 61.091 | 122.1786 | 61.0597 | 121.9705 | 62.0749 | 62.1063 | 62.0016 | 62.0329
8009.0625 | 123.2803 | -61.0886 | 62.0499 | -7.3638 | -7.3895 | -7.3744 | -7.4971 | -7.4533 | -7.2215 | -7.31 | 62.1048 | 0.23032 | 62.0223 | -0.028522 | 0.052814 | 61.1587 | 0.007721 | 60.9415 | 53.7247 | 53.699 | 53.7142 | 53.5914 | 53.6353 | 53.867 | 53.7786 | 123.1934 | 61.3189 | 123.1109 | 61.06 | 61.1414 | 122.2473 | 61.0963 | 122.03 | 62.052 | 62.0971 | 61.9695 | 62.0146
8010.0938 | 123.2803 | -60.965 | 62.1368 | -7.666 | -7.7055 | -7.6857 | -7.8039 | -7.7417 | -7.5191 | -7.6304 | 62.114 | 0.2349 | 62.0223 | -0.023943 | 0.048236 | 61.1312 | 0.007721 | 60.9186 | 53.299 | 53.2595 | 53.2792 | 53.1611 | 53.2233 | 53.4458 | 53.3345 | 123.079 | 61.1999 | 122.9873 | 60.941 | 61.0132 | 122.0962 | 60.9727 | 121.8835 | 62.0658 | 62.1063 | 61.9741 | 62.0146
8011.0625 | 123.262 | -61.0703 | 62.0499 | -7.4966 | -7.5406 | -7.5072 | -7.6482 | -7.5998 | -7.368 | -7.461 | 62.1094 | 0.23032 | 62.004 | -0.028522 | 0.048236 | 61.145 | 0.012299 | 60.9232 | 53.5737 | 53.5296 | 53.5631 | 53.422 | 53.4705 | 53.7022 | 53.6092 | 123.1797 | 61.3006 | 123.0743 | 61.0417 | 61.1185 | 122.2152 | 61.0825 | 121.9934 | 62.0612 | 62.0971 | 61.9558 | 61.9917
8012.0938 | 123.2483 | -61.0382 | 62.0544 | -7.6523 | -7.6826 | -7.6628 | -7.7856 | -7.7325 | -7.51 | -7.6121 | 62.1094 | 0.23032 | 62.004 | -0.023943 | 0.048236 | 61.1404 | 0.016878 | 60.9094 | 53.386 | 53.3556 | 53.3754 | 53.2526 | 53.3057 | 53.5282 | 53.4261 | 123.1476 | 61.2685 | 123.0422 | 61.0143 | 61.0864 | 122.1786 | 61.0551 | 121.9476 | 62.0612 | 62.0925 | 61.9558 | 61.9871
8013.0625 | 123.3032 | -61.0611 | 62.0087 | -7.84 | -7.8657 | -7.8597 | -7.9595 | -7.9156 | -7.6794 | -7.7998 | 62.1231 | 0.23032 | 62.0269 | -0.028522 | 0.052814 | 61.1175 | 0.012299 | 60.9048 | 53.2211 | 53.1954 | 53.2014 | 53.1015 | 53.1454 | 53.3817 | 53.2613 | 123.1842 | 61.2914 | 123.088 | 61.0326 | 61.1139 | 122.1786 | 61.0734 | 121.9659 | 62.0703 | 62.1108 | 61.9741 | 62.0146
8014.0781 | 123.2758 | -61.0062 | 62.1048 | -7.6248 | -7.6643 | -7.6308 | -7.7627 | -7.7234 | -7.4825 | -7.5755 | 62.1186 | 0.2349 | 62.0315 | -0.023943 | 0.048236 | 61.1358 | 0.007721 | 60.9232 | 53.3814 | 53.3419 | 53.3754 | 53.2435 | 53.2828 | 53.5237 | 53.4307 | 123.1247 | 61.2411 | 123.0376 | 60.9822 | 61.0544 | 122.142 | 61.0139 | 121.9293 | 62.0703 | 62.1108 | 61.9832 | 62.0238
8015.0625 | 123.2346 | -61.0428 | 62.1048 | -7.753 | -7.7879 | -7.7636 | -7.8863 | -7.8424 | -7.6107 | -7.7083 | 62.1323 | 0.2349 | 62.0406 | -0.019364 | 0.048236 | 61.1312 | 0.012299 | 60.9186 | 53.2898 | 53.2549 | 53.2792 | 53.1565 | 53.2004 | 53.4321 | 53.3345 | 123.1751 | 61.2777 | 123.0834 | 61.0234 | 61.091 | 122.174 | 61.0551 | 121.9614 | 62.0841 | 62.12 | 61.9924 | 62.0283
8016.0625 | 123.3902 | -61.0153 | 62.0087 | -7.3959 | -7.4307 | -7.411 | -7.5612 | -7.5128 | -7.2856 | -7.3557 | 62.1094 | 0.2349 | 62.0132 | -0.023943 | 0.052814 | 61.1496 | 0.016878 | 60.9369 | 53.6195 | 53.5846 | 53.6043 | 53.4541 | 53.5025 | 53.7297 | 53.6596 | 123.1247 | 61.2502 | 123.0285 | 60.9914 | 61.0681 | 122.1649 | 61.0322 | 121.9522 | 62.0566 | 62.0925 | 61.9604 | 61.9963
8017.0625 | 123.3627 | -60.965 | 62.0728 | -7.872 | -7.9024 | -7.8826 | -7.9916 | -7.9523 | -7.7572 | -7.8319 | 62.1323 | 0.23032 | 62.0269 | -0.028522 | 0.057392 | 61.1221 | 0.007721 | 60.9094 | 53.093 | 53.0626 | 53.0823 | 52.9734 | 53.0127 | 53.2078 | 53.1331 | 123.0973 | 61.1953 | 122.9919 | 60.9364 | 61.0224 | 122.0871 | 60.9727 | 121.8744 | 62.0749 | 62.1246 | 61.9695 | 62.0192
8018.0781 | 123.2483 | -61.0611 | 62.0224 | -6.9426 | -6.9774 | -6.9532 | -7.0851 | -7.0321 | -6.7545 | -6.8934 | 62.0774 | 0.23032 | 61.9765 | -0.028522 | 0.052814 | 61.177 | 0.012299 | 60.9598 | 54.1185 | 54.0837 | 54.1079 | 53.976 | 54.029 | 54.3066 | 54.1677 | 123.1385 | 61.2914 | 123.0376 | 61.0326 | 61.1139 | 122.2381 | 61.0734 | 122.0209 | 62.0245 | 62.0651 | 61.9237 | 61.9642
8019.0625 | 123.2346 | -61.0886 | 62.0407 | -7.0433 | -7.0873 | -7.0539 | -7.1858 | -7.1374 | -6.8736 | -7.0032 | 62.0865 | 0.23032 | 61.9994 | -0.023943 | 0.048236 | 61.1724 | 0.007721 | 60.946 | 54.0452 | 54.0012 | 54.0347 | 53.9028 | 53.9512 | 54.215 | 54.0853 | 123.1751 | 61.3189 | 123.088 | 61.0646 | 61.1368 | 122.261 | 61.0963 | 122.0346 | 62.0383 | 62.0788 | 61.9512 | 61.9917
8020.0781 | 123.2712 | -61.0703 | 62.0178 | -6.2879 | -6.3364 | -6.3076 | -6.4349 | -6.382 | -6.0174 | -6.257 | 62.0362 | 0.23948 | 61.9582 | -0.03768 | 0.057392 | 61.2091 | 0.012299 | 61.001 | 54.7824 | 54.7339 | 54.7627 | 54.6353 | 54.6882 | 55.0528 | 54.8133 | 123.1064 | 61.3097 | 123.0285 | 61.0326 | 61.1276 | 122.2793 | 61.0825 | 122.0712 | 61.9788 | 62.0239 | 61.9008 | 61.9459
8021.0625 | 123.349 | -61.0153 | 62.0544 | -7.1257 | -7.1789 | -7.1363 | -7.2911 | -7.2335 | -6.9331 | -7.0902 | 62.0911 | 0.23948 | 61.9903 | -0.028522 | 0.043657 | 61.1679 | 0.012299 | 60.9506 | 53.8896 | 53.8364 | 53.879 | 53.7242 | 53.7818 | 54.0822 | 53.9251 | 123.1064 | 61.2548 | 123.0056 | 60.9868 | 61.059 | 122.1832 | 61.0276 | 121.9659 | 62.0474 | 62.0788 | 61.9466 | 61.978
8022.0625 | 123.2941 | -61.0107 | 62.0773 | -6.9975 | -7.037 | -7.0081 | -7.14 | -7.087 | -6.8369 | -6.9483 | 62.0819 | 0.23032 | 61.9811 | -0.023943 | 0.048236 | 61.1679 | 0.012299 | 60.9598 | 54.0132 | 53.9738 | 54.0026 | 53.8707 | 53.9237 | 54.1738 | 54.0625 | 123.0927 | 61.2411 | 122.9919 | 60.9868 | 61.059 | 122.1786 | 61.023 | 121.9705 | 62.0337 | 62.0696 | 61.9329 | 61.9688
8023.0625 | 123.2666 | -61.0153 | 62.1002 | -7.1486 | -7.1835 | -7.1684 | -7.2774 | -7.2381 | -6.9651 | -7.0994 | 62.1003 | 0.23948 | 61.9949 | -0.023943 | 0.048236 | 61.1633 | 0.012299 | 60.9506 | 53.8667 | 53.8318 | 53.847 | 53.738 | 53.7772 | 54.0502 | 53.916 | 123.1156 | 61.2548 | 123.0102 | 60.9914 | 61.0636 | 122.1786 | 61.0276 | 121.9659 | 62.052 | 62.088 | 61.9466 | 61.9826
8024.0625 | 123.2391 | -61.0565 | 62.0682 | -7.4691 | -7.4948 | -7.4751 | -7.607 | -7.5586 | -7.3039 | -7.4061 | 62.1094 | 0.2349 | 62.0177 | -0.023943 | 0.052814 | 61.1496 | 0.012299 | 60.9277 | 53.5874 | 53.5617 | 53.5814 | 53.4495 | 53.498 | 53.7526 | 53.6504 | 123.1659 | 61.2914 | 123.0743 | 61.0326 | 61.1093 | 122.2061 | 61.0688 | 121.9843 | 62.0566 | 62.0971 | 61.9649 | 62.0054
8025.0781 | 123.3124 | -60.9741 | 62.1002 | -7.3959 | -7.4399 | -7.4202 | -7.5475 | -7.4991 | -7.2536 | -7.3557 | 62.1003 | 0.23032 | 62.004 | -0.019364 | 0.052814 | 61.1496 | 0.016878 | 60.9369 | 53.5783 | 53.5342 | 53.5539 | 53.4266 | 53.4751 | 53.7205 | 53.6184 | 123.0744 | 61.2044 | 122.9781 | 60.9548 | 61.0269 | 122.1237 | 60.991 | 121.911 | 62.0474 | 62.0834 | 61.9512 | 61.9871
8026.0625 | 123.349 | -61.0062 | 62.059 | -7.4279 | -7.4445 | -7.4339 | -7.575 | -7.5265 | -7.3039 | -7.3741 | 62.1094 | 0.23948 | 62.0132 | -0.028522 | 0.057392 | 61.1541 | 0.012299 | 60.9232 | 53.5783 | 53.5617 | 53.5723 | 53.4312 | 53.4796 | 53.7022 | 53.6321 | 123.1156 | 61.2456 | 123.0193 | 60.9776 | 61.0636 | 122.1603 | 61.0185 | 121.9293 | 62.052 | 62.0971 | 61.9558 | 62.0009
8027.0781 | 123.3673 | -61.0016 | 62.0773 | -7.112 | -7.1514 | -7.118 | -7.2499 | -7.2106 | -6.9331 | -7.0582 | 62.0957 | 0.2349 | 62.0132 | -0.028522 | 0.057392 | 61.1587 | 0.007721 | 60.9552 | 53.8896 | 53.8502 | 53.8836 | 53.7517 | 53.7909 | 54.0685 | 53.9434 | 123.0973 | 61.2365 | 123.0148 | 60.9731 | 61.059 | 122.1603 | 61.0093 | 121.9568 | 62.0383 | 62.088 | 61.9558 | 62.0054
8028.0625 | 123.2666 | -61.0748 | 62.0499 | -7.0845 | -7.124 | -7.1043 | -7.2178 | -7.1786 | -6.901 | -7.0307 | 62.0865 | 0.2349 | 61.9903 | -0.019364 | 0.052814 | 61.1724 | 0.012299 | 60.9506 | 53.9903 | 53.9509 | 53.9706 | 53.857 | 53.8962 | 54.1738 | 54.0441 | 123.1613 | 61.3097 | 123.0651 | 61.0555 | 61.1276 | 122.2473 | 61.0871 | 122.0255 | 62.0337 | 62.0742 | 61.9375 | 61.978
8029.0781 | 123.2208 | -61.0062 | 62.1185 | -7.7988 | -7.8199 | -7.8094 | -7.9183 | -7.8699 | -7.7023 | -7.7403 | 62.1231 | 0.23032 | 62.0223 | -0.023943 | 0.052814 | 61.1404 | 0.012299 | 60.914 | 53.2074 | 53.1862 | 53.1968 | 53.0878 | 53.1363 | 53.3039 | 53.2659 | 123.1293 | 61.2365 | 123.0285 | 60.9822 | 61.059 | 122.1466 | 61.0185 | 121.9202 | 62.0703 | 62.1108 | 61.9695 | 62.01
8030.0625 | 123.2071 | -61.0153 | 62.0544 | -7.2173 | -7.243 | -7.2279 | -7.3369 | -7.2885 | -7.0659 | -7.1635 | 62.1048 | 0.23948 | 62.004 | -0.023943 | 0.048236 | 61.1679 | 0.016878 | 60.946 | 53.798 | 53.7723 | 53.7874 | 53.6784 | 53.7269 | 53.9495 | 53.8519 | 123.1202 | 61.2548 | 123.0193 | 60.9914 | 61.0636 | 122.1832 | 61.0322 | 121.9614 | 62.0566 | 62.088 | 61.9558 | 61.9871
8031.1094 | 123.2895 | -61.0062 | 62.0819 | -7.1028 | -7.1423 | -7.118 | -7.2224 | -7.1694 | -6.9239 | -7.0673 | 62.0865 | 0.2349 | 62.0086 | -0.023943 | 0.048236 | 61.1679 | 0.007721 | 60.946 | 53.9033 | 53.8639 | 53.8882 | 53.7838 | 53.8367 | 54.0822 | 53.9388 | 123.0927 | 61.2411 | 123.0148 | 60.9822 | 61.0544 | 122.174 | 61.0139 | 121.9522 | 62.0383 | 62.0788 | 61.9604 | 62.0009
8032.0625 | 123.2941 | -61.1114 | 62.0041 | -6.9014 | -6.9454 | -6.9211 | -7.0164 | -6.968 | -6.7362 | -6.8613 | 62.0819 | 0.23948 | 61.9765 | -0.014785 | 0.048236 | 61.1862 | 0.016878 | 60.9644 | 54.2101 | 54.1661 | 54.1903 | 54.0951 | 54.1434 | 54.3752 | 54.2501 | 123.1934 | 61.3509 | 123.088 | 61.0967 | 61.1597 | 122.2976 | 61.1283 | 122.0758 | 62.0337 | 62.0651 | 61.9283 | 61.9597
8033.0781 | 123.3536 | -61.0336 | 62.0087 | -6.7274 | -6.7668 | -6.7425 | -6.8516 | -6.8078 | -6.5989 | -6.6919 | 62.0682 | 0.2349 | 61.972 | -0.023943 | 0.052814 | 61.1908 | 0.012299 | 60.9689 | 54.3062 | 54.2668 | 54.2911 | 54.1821 | 54.2258 | 54.4348 | 54.3417 | 123.1018 | 61.2685 | 123.0056 | 61.0097 | 61.0864 | 122.2244 | 61.0459 | 122.0026 | 62.0154 | 62.0559 | 61.9192 | 61.9597
8034.0625 | 123.3398 | -61.0657 | 62.0087 | -7.4966 | -7.5177 | -7.5072 | -7.6253 | -7.586 | -7.3451 | -7.4473 | 62.1094 | 0.2349 | 62.0315 | -0.023943 | 0.039079 | 61.145 | 0.012299 | 60.9277 | 53.5691 | 53.5479 | 53.5585 | 53.4404 | 53.4796 | 53.7205 | 53.6184 | 123.1751 | 61.3006 | 123.0972 | 61.0417 | 61.1048 | 122.2107 | 61.078 | 121.9934 | 62.0703 | 62.0971 | 61.9924 | 62.0192
8035.0781 | 123.3536 | -61.0336 | 62.0087 | -7.1349 | -7.1835 | -7.1638 | -7.3277 | -7.2656 | -6.956 | -7.1177 | 62.0957 | 0.23948 | 62.004 | -0.028522 | 0.039079 | 61.1679 | 0.016878 | 60.946 | 53.8987 | 53.8502 | 53.8699 | 53.7059 | 53.7681 | 54.0777 | 53.9159 | 123.1293 | 61.2731 | 123.0376 | 61.0051 | 61.0727 | 122.2015 | 61.0505 | 121.9797 | 62.0566 | 62.0788 | 61.9649 | 61.9871
8036.0625 | 123.2666 | -61.0291 | 62.0956 | -7.6614 | -7.7009 | -7.6766 | -7.8039 | -7.7646 | -7.5557 | -7.6259 | 62.1231 | 0.22574 | 62.0086 | -0.019364 | 0.048236 | 61.1358 | 0.012299 | 60.914 | 53.3676 | 53.3282 | 53.3525 | 53.2252 | 53.2645 | 53.4733 | 53.4032 | 123.1522 | 61.2548 | 123.0376 | 61.0097 | 61.0773 | 122.1649 | 61.0414 | 121.9431 | 62.0749 | 62.1108 | 61.9604 | 61.9963
8037.0938 | 123.3582 | -60.9833 | 62.0499 | -7.8308 | -7.8611 | -7.846 | -7.9595 | -7.9065 | -7.7297 | -7.7953 | 62.1323 | 0.2349 | 62.0269 | -0.028522 | 0.052814 | 61.1221 | 0.012299 | 60.9094 | 53.1525 | 53.1221 | 53.1373 | 53.0237 | 53.0768 | 53.2536 | 53.188 | 123.1156 | 61.2182 | 123.0102 | 60.9548 | 61.0361 | 122.1054 | 60.9956 | 121.8927 | 62.0795 | 62.12 | 61.9741 | 62.0146
8038.0625 | 123.2941 | -61.0565 | 62.0453 | -7.5973 | -7.623 | -7.6171 | -7.7215 | -7.673 | -7.51 | -7.5572 | 62.1186 | 0.2349 | 62.0406 | -0.028522 | 0.052814 | 61.1404 | 0.012299 | 60.9232 | 53.4592 | 53.4335 | 53.4395 | 53.3351 | 53.3835 | 53.5466 | 53.4993 | 123.1751 | 61.2914 | 123.0972 | 61.028 | 61.1093 | 122.1969 | 61.0688 | 121.9797 | 62.0658 | 62.1063 | 61.9878 | 62.0283
8039.0781 | 123.349 | -60.9695 | 62.0728 | -7.7255 | -7.7558 | -7.7361 | -7.8726 | -7.8241 | -7.6382 | -7.6854 | 62.1277 | 0.22574 | 62.0223 | -0.028522 | 0.057392 | 61.1312 | 0.016878 | 60.9094 | 53.244 | 53.2137 | 53.2334 | 53.097 | 53.1455 | 53.3314 | 53.2842 | 123.0973 | 61.1953 | 122.9919 | 60.941 | 61.0269 | 122.1008 | 60.9864 | 121.879 | 62.0703 | 62.1108 | 61.9649 | 62.0054
8040.0625 | 123.2437 | -60.997 | 62.114 | -7.579 | -7.6139 | -7.5942 | -7.7123 | -7.6639 | -7.4916 | -7.5526 | 62.114 | 0.23948 | 62.0086 | -0.028522 | 0.052814 | 61.1404 | 0.012299 | 60.9232 | 53.418 | 53.3831 | 53.4028 | 53.2847 | 53.3331 | 53.5054 | 53.4444 | 123.111 | 61.2365 | 123.0056 | 60.9685 | 61.0498 | 122.1374 | 61.0093 | 121.9202 | 62.0612 | 62.1017 | 61.9558 | 61.9963
8041.1094 | 123.4039 | -60.965 | 62.0728 | -8.1421 | -8.1725 | -8.1528 | -8.2572 | -8.2041 | -8.0502 | -8.0974 | 62.1506 | 0.23948 | 62.0544 | -0.033101 | 0.057392 | 61.1038 | 0.012299 | 60.8957 | 52.8228 | 52.7925 | 52.8122 | 52.7078 | 52.7609 | 52.9148 | 52.8676 | 123.1156 | 61.2044 | 123.0193 | 60.9319 | 61.0224 | 122.0687 | 60.9773 | 121.8607 | 62.0932 | 62.1383 | 61.997 | 62.0421
8042.0625 | 123.23 | -60.9558 | 62.1506 | -8.3756 | -8.3923 | -8.3817 | -8.4861 | -8.4467 | -8.2608 | -8.3263 | 62.1644 | 0.2349 | 62.0773 | -0.023943 | 0.048236 | 61.0946 | 0.012299 | 60.882 | 52.5802 | 52.5635 | 52.5741 | 52.4697 | 52.5091 | 52.695 | 52.6295 | 123.1202 | 61.1907 | 123.0331 | 60.9319 | 61.004 | 122.0504 | 60.9681 | 121.8378 | 62.1161 | 62.1521 | 62.029 | 62.065
8043.0781 | 123.3307 | -60.9604 | 62.1048 | -8.0551 | -8.0901 | -8.0658 | -8.1793 | -8.14 | -7.9312 | -8.015 | 62.1369 | 0.2349 | 62.0315 | -0.028522 | 0.052814 | 61.1221 | 0.012299 | 60.9003 | 52.9052 | 52.8703 | 52.8946 | 52.7811 | 52.8204 | 53.0292 | 52.9454 | 123.0973 | 61.1953 | 122.9919 | 60.9319 | 61.0132 | 122.0825 | 60.9727 | 121.8607 | 62.0841 | 62.1246 | 61.9787 | 62.0192
8044.0625 | 123.2529 | -61.0336 | 62.1323 | -7.8629 | -7.884 | -7.8597 | -7.9916 | -7.9431 | -7.7435 | -7.8227 | 62.1277 | 0.23032 | 62.0269 | -0.028522 | 0.052814 | 61.1221 | 0.012299 | 60.9094 | 53.1708 | 53.1496 | 53.1739 | 53.042 | 53.0905 | 53.2902 | 53.2109 | 123.1614 | 61.2639 | 123.0605 | 61.0051 | 61.0864 | 122.1557 | 61.0459 | 121.9431 | 62.0749 | 62.1154 | 61.9741 | 62.0146
8045.0781 | 123.2803 | -60.9695 | 62.0773 | -8.4718 | -8.4976 | -8.4778 | -8.5822 | -8.5291 | -8.3387 | -8.4316 | 62.1689 | 0.24405 | 62.0818 | -0.028522 | 0.048236 | 61.0809 | 0.012299 | 60.8682 | 52.4978 | 52.4719 | 52.4917 | 52.3873 | 52.4404 | 52.6309 | 52.5379 | 123.1385 | 61.2136 | 123.0514 | 60.941 | 61.0178 | 122.0504 | 60.9818 | 121.8378 | 62.1207 | 62.1566 | 62.0336 | 62.0695
8046.0625 | 123.2666 | -61.0382 | 62.0728 | -8.0643 | -8.0901 | -8.0612 | -8.1793 | -8.1217 | -7.9312 | -8.0333 | 62.1415 | 0.23032 | 62.0498 | -0.028522 | 0.052814 | 61.1084 | 0.007721 | 60.8957 | 52.9739 | 52.9481 | 52.977 | 52.8589 | 52.9166 | 53.107 | 53.0049 | 123.1797 | 61.2685 | 123.088 | 61.0097 | 61.091 | 122.1466 | 61.0459 | 121.9339 | 62.0886 | 62.1337 | 61.997 | 62.0421
8047.0938 | 123.317 | -60.9695 | 62.0773 | -8.3985 | -8.4152 | -8.4046 | -8.509 | -8.4558 | -8.2791 | -8.3492 | 62.146 | 0.23032 | 62.0544 | -0.033101 | 0.043657 | 61.0992 | 0.012299 | 60.8728 | 52.571 | 52.5544 | 52.565 | 52.4606 | 52.5137 | 52.6904 | 52.6203 | 123.1156 | 61.1999 | 123.0239 | 60.9364 | 61.0132 | 122.0687 | 60.9818 | 121.8423 | 62.1024 | 62.1337 | 62.0107 | 62.0421
8048.0625 | 123.3261 | -60.965 | 62.1094 | -8.0048 | -8.0306 | -8.0062 | -8.1152 | -8.0759 | -7.8442 | -7.9738 | 62.1369 | 0.23948 | 62.0452 | -0.019364 | 0.048236 | 61.1084 | 0.012299 | 60.8957 | 52.9602 | 52.9344 | 52.9587 | 52.8497 | 52.8891 | 53.1208 | 52.9912 | 123.1018 | 61.2044 | 123.0102 | 60.9456 | 61.0132 | 122.0733 | 60.9773 | 121.8607 | 62.0886 | 62.1246 | 61.997 | 62.0329
8049.0938 | 123.4039 | -61.0199 | 62.059 | -7.7576 | -7.7833 | -7.7682 | -7.8817 | -7.8241 | -7.6244 | -7.722 | 62.1323 | 0.2349 | 62.0498 | -0.014785 | 0.048236 | 61.1312 | 0.021456 | 60.9048 | 53.2623 | 53.2366 | 53.2517 | 53.1382 | 53.1958 | 53.3955 | 53.2979 | 123.1522 | 61.2548 | 123.0697 | 61.0051 | 61.0681 | 122.1511 | 61.0414 | 121.9247 | 62.0841 | 62.1108 | 62.0016 | 62.0283
8050.0625 | 123.2483 | -61.0199 | 62.0911 | -7.4737 | -7.504 | -7.4889 | -7.6024 | -7.5586 | -7.3406 | -7.4382 | 62.1094 | 0.23032 | 62.0132 | -0.019364 | 0.048236 | 61.145 | 0.007721 | 60.9323 | 53.5462 | 53.5159 | 53.531 | 53.4175 | 53.4613 | 53.6793 | 53.5817 | 123.1293 | 61.2502 | 123.0331 | 61.0005 | 61.0681 | 122.1649 | 61.0276 | 121.9522 | 62.0612 | 62.1017 | 61.9649 | 62.0054
8051.1094 | 123.3078 | -61.0245 | 62.0361 | -7.6751 | -7.7055 | -7.6857 | -7.7901 | -7.7463 | -7.4871 | -7.635 | 62.1094 | 0.2349 | 62.0086 | -0.023943 | 0.052814 | 61.1404 | 0.016878 | 60.9232 | 53.3493 | 53.319 | 53.3387 | 53.2343 | 53.2782 | 53.5374 | 53.3895 | 123.1339 | 61.2594 | 123.0331 | 61.0005 | 61.0773 | 122.1649 | 61.0414 | 121.9476 | 62.0566 | 62.0925 | 61.9558 | 61.9917
8052.0625 | 123.23 | -61.0886 | 62.0316 | -6.3062 | -6.3501 | -6.3305 | -6.412 | -6.3591 | -5.9854 | -6.2707 | 62.0499 | 0.2349 | 61.9537 | -0.028522 | 0.048236 | 61.2136 | 0.007721 | 60.9964 | 54.7824 | 54.7384 | 54.7581 | 54.6765 | 54.7294 | 55.1032 | 54.8178 | 123.1385 | 61.3235 | 123.0422 | 61.06 | 61.1368 | 122.3022 | 61.0963 | 122.085 | 62.0017 | 62.0422 | 61.9054 | 61.9459
8053.0781 | 123.3032 | -61.116 | 61.94 | -5.9079 | -5.9518 | -5.9321 | -6.0183 | -5.97 | -5.5504 | -5.8816 | 62.0178 | 0.2349 | 61.9399 | -0.023943 | 0.048236 | 61.232 | 0.012299 | 61.0101 | 55.2081 | 55.1643 | 55.1839 | 55.0978 | 55.146 | 55.5656 | 55.2345 | 123.1339 | 61.3509 | 123.0559 | 61.0921 | 61.1643 | 122.348 | 61.1283 | 122.1262 | 61.9696 | 62.0055 | 61.8917 | 61.9276
8054.0625 | 123.262 | -61.0703 | 62.027 | -7.0662 | -7.1056 | -7.0814 | -7.1812 | -7.1328 | -6.8369 | -7.0353 | 62.0819 | 0.2349 | 61.9857 | -0.023943 | 0.052814 | 61.1724 | 0.016878 | 60.946 | 54.004 | 53.9646 | 53.9889 | 53.889 | 53.9374 | 54.2333 | 54.035 | 123.1522 | 61.3051 | 123.0559 | 61.0463 | 61.1231 | 122.2427 | 61.0871 | 122.0163 | 62.0291 | 62.0651 | 61.9329 | 61.9688
8055.0781 | 123.3215 | -61.0107 | 62.0407 | -7.3226 | -7.3483 | -7.3332 | -7.4284 | -7.38 | -7.0567 | -7.2779 | 62.0911 | 0.23032 | 61.9903 | -0.033101 | 0.057392 | 61.1541 | 0.012299 | 60.9323 | 53.6881 | 53.6624 | 53.6776 | 53.5823 | 53.6307 | 53.954 | 53.7328 | 123.1018 | 61.2411 | 123.001 | 60.9776 | 61.0681 | 122.1649 | 61.023 | 121.9431 | 62.0337 | 62.0788 | 61.9329 | 61.978
8056.0625 | 123.2254 | -60.9558 | 62.114 | -8.0597 | -8.0809 | -8.0749 | -8.1427 | -8.0942 | -7.8808 | -8.0242 | 62.146 | 0.2349 | 62.0635 | -0.023943 | 0.048236 | 61.1084 | 0.012299 | 60.9003 | 52.8961 | 52.8749 | 52.8809 | 52.8131 | 52.8616 | 53.075 | 52.9316 | 123.1019 | 61.1907 | 123.0193 | 60.9319 | 61.004 | 122.0642 | 60.9681 | 121.8561 | 62.0978 | 62.1337 | 62.0153 | 62.0512
8057.0781 | 123.3078 | -61.0336 | 62.0453 | -7.4508 | -7.4719 | -7.4568 | -7.5475 | -7.4899 | -7.281 | -7.4702 | 62.1048 | 0.2349 | 62.0086 | -0.023943 | 0.048236 | 61.1541 | 0.007721 | 60.9323 | 53.5828 | 53.5617 | 53.5768 | 53.4861 | 53.5437 | 53.7526 | 53.5634 | 123.1385 | 61.2685 | 123.0422 | 61.0097 | 61.0819 | 122.1878 | 61.0414 | 121.9659 | 62.0566 | 62.0971 | 61.9604 | 62.0009
8058.0625 | 123.2758 | -61.0016 | 62.0956 | -7.7713 | -7.7879 | -7.7865 | -7.868 | -7.8241 | -7.5786 | -7.7403 | 62.1231 | 0.2349 | 62.0223 | -0.028522 | 0.052814 | 61.1221 | 0.007721 | 60.9186 | 53.2303 | 53.2137 | 53.2151 | 53.1336 | 53.1775 | 53.4229 | 53.2613 | 123.1247 | 61.2365 | 123.0239 | 60.9731 | 61.0544 | 122.1237 | 61.0093 | 121.9202 | 62.0703 | 62.1154 | 61.9695 | 62.0146
8059.0781 | 123.3582 | -61.0245 | 61.9995 | -7.872 | -7.9024 | -7.8872 | -7.9824 | -7.9294 | -7.748 | -7.9234 | 62.1323 | 0.24405 | 62.0269 | -0.028522 | 0.043657 | 61.1175 | 0.012299 | 60.9094 | 53.1525 | 53.1221 | 53.1373 | 53.042 | 53.0951 | 53.2764 | 53.101 | 123.1568 | 61.2685 | 123.0514 | 60.996 | 61.0681 | 122.142 | 61.0368 | 121.9339 | 62.0886 | 62.12 | 61.9832 | 62.0146
8060.0625 | 123.3398 | -60.9558 | 62.1094 | -8.1742 | -8.1954 | -8.1894 | -8.3029 | -8.2544 | -8.1006 | -8.1569 | 62.1552 | 0.23948 | 62.0681 | -0.028522 | 0.052814 | 61.1038 | 0.012299 | 60.8865 | 52.7816 | 52.7604 | 52.7664 | 52.6529 | 52.7014 | 52.8552 | 52.7989 | 123.111 | 61.1953 | 123.0239 | 60.9273 | 61.0086 | 122.0596 | 60.9681 | 121.8423 | 62.1024 | 62.1429 | 62.0153 | 62.0558
8061.1094 | 123.3307 | -60.9512 | 62.0819 | -8.6274 | -8.6533 | -8.6427 | -8.7333 | -8.6847 | -8.5493 | -8.6193 | 62.1735 | 0.2349 | 62.0818 | -0.033101 | 0.043657 | 61.0809 | 0.012299 | 60.8636 | 52.3238 | 52.298 | 52.3086 | 52.2179 | 52.2665 | 52.402 | 52.3319 | 123.1247 | 61.1861 | 123.0331 | 60.9181 | 60.9949 | 122.0321 | 60.9635 | 121.8149 | 62.1299 | 62.1612 | 62.0382 | 62.0695
8062.0625 | 123.3902 | -60.9558 | 62.0773 | -8.1605 | -8.1908 | -8.1756 | -8.2892 | -8.2361 | -8.1189 | -8.189 | 62.1415 | 0.2349 | 62.0498 | -0.033101 | 0.057392 | 61.0992 | 0.016878 | 60.8865 | 52.7954 | 52.765 | 52.7802 | 52.6666 | 52.7197 | 52.8369 | 52.7668 | 123.0973 | 61.1907 | 123.0056 | 60.9227 | 61.0132 | 122.055 | 60.9727 | 121.8423 | 62.0841 | 62.1246 | 61.9924 | 62.0329
8063.0781 | 123.3215 | -60.9741 | 62.0728 | -8.2749 | -8.3053 | -8.2901 | -8.3945 | -8.3414 | -8.1006 | -8.2531 | 62.146 | 0.22574 | 62.0406 | -0.028522 | 0.048236 | 61.0946 | 0.012299 | 60.8865 | 52.6992 | 52.6688 | 52.684 | 52.5796 | 52.6327 | 52.8735 | 52.7211 | 123.1202 | 61.1999 | 123.0148 | 60.9456 | 61.0224 | 122.0687 | 60.9864 | 121.8607 | 62.0978 | 62.1337 | 61.9924 | 62.0283
8064.0625 | 123.3765 | -60.9695 | 62.0819 | -8.3344 | -8.3648 | -8.3542 | -8.454 | -8.4101 | -8.2288 | -8.3309 | 62.1552 | 0.22116 | 62.0498 | -0.028522 | 0.048236 | 61.0946 | 0.012299 | 60.882 | 52.6351 | 52.6047 | 52.6153 | 52.5155 | 52.5595 | 52.7408 | 52.6386 | 123.1247 | 61.1907 | 123.0193 | 60.941 | 61.0178 | 122.0642 | 60.9818 | 121.8515 | 62.107 | 62.1429 | 62.0016 | 62.0375
8065.0938 | 123.349 | -60.9467 | 62.1185 | -8.4764 | -8.4839 | -8.4824 | -8.5639 | -8.5245 | -8.2791 | -8.4362 | 62.1644 | 0.22574 | 62.0635 | -0.023943 | 0.048236 | 61.09 | 0.007721 | 60.8682 | 52.4703 | 52.4628 | 52.4642 | 52.3827 | 52.4221 | 52.6675 | 52.5105 | 123.111 | 61.1724 | 123.0102 | 60.9227 | 60.9949 | 122.0367 | 60.9544 | 121.8149 | 62.1161 | 62.1566 | 62.0153 | 62.0558
8066.0625 | 123.175 | -60.8963 | 62.1826 | -9.2455 | -9.2623 | -9.2516 | -9.3056 | -9.2661 | -9.1078 | -9.2191 | 62.2101 | 0.23948 | 62.123 | -0.023943 | 0.052814 | 61.0443 | 0.007721 | 60.827 | 51.6508 | 51.634 | 51.6447 | 51.5907 | 51.6302 | 51.7885 | 51.6772 | 123.1064 | 61.1358 | 123.0193 | 60.8724 | 60.9491 | 121.9406 | 60.904 | 121.7233 | 62.1573 | 62.2024 | 62.0702 | 62.1153
8067.0938 | 123.2986 | -60.997 | 62.0728 | -8.8243 | -8.841 | -8.8212 | -8.8844 | -8.8404 | -8.7415 | -8.8345 | 62.1872 | 0.23948 | 62.1093 | -0.028522 | 0.048236 | 61.0763 | 0.012299 | 60.8407 | 52.1727 | 52.156 | 52.1758 | 52.1126 | 52.1566 | 52.2555 | 52.1625 | 123.1843 | 61.2365 | 123.1063 | 60.9685 | 61.0452 | 122.0733 | 61.0093 | 121.8378 | 62.139 | 62.1749 | 62.0611 | 62.097
8068.0625 | 123.3536 | -60.9192 | 62.0911 | -8.6229 | -8.6579 | -8.6244 | -8.6875 | -8.6344 | -8.5218 | -8.6147 | 62.1735 | 0.23032 | 62.0818 | -0.023943 | 0.052814 | 61.0809 | 0.012299 | 60.8682 | 52.2963 | 52.2613 | 52.2948 | 52.2317 | 52.2848 | 52.3974 | 52.3044 | 123.0927 | 61.1495 | 123.001 | 60.8952 | 60.972 | 122.0001 | 60.9315 | 121.7874 | 62.1207 | 62.1612 | 62.029 | 62.0695
8069.0938 | 123.2941 | -60.9146 | 62.1414 | -9.8041 | -9.8163 | -9.8011 | -9.8413 | -9.788 | -9.6847 | -9.7776 | 62.2422 | 0.23032 | 62.1368 | -0.023943 | 0.043657 | 61.0168 | 0.007721 | 60.795 | 51.1105 | 51.0983 | 51.1136 | 51.0733 | 51.1266 | 51.2299 | 51.137 | 123.1568 | 61.1449 | 123.0514 | 60.8907 | 60.9583 | 121.9314 | 60.9223 | 121.7096 | 62.1985 | 62.2345 | 62.0931 | 62.1291
8070.0625 | 123.2895 | -60.9283 | 62.1231 | -9.7034 | -9.7247 | -9.7049 | -9.7497 | -9.7011 | -9.5382 | -9.6769 | 62.2239 | 0.23032 | 62.1185 | -0.019364 | 0.052814 | 61.0214 | 0.012299 | 60.8041 | 51.225 | 51.2036 | 51.2234 | 51.1786 | 51.2273 | 51.3902 | 51.2515 | 123.1522 | 61.1587 | 123.0468 | 60.909 | 60.9812 | 121.9497 | 60.9406 | 121.7325 | 62.1711 | 62.2116 | 62.0657 | 62.1062
8071.1094 | 123.3215 | -60.9421 | 62.146 | -9.8133 | -9.8438 | -9.8239 | -9.8825 | -9.8292 | -9.6755 | -9.7822 | 62.2376 | 0.2349 | 62.1276 | -0.028522 | 0.043657 | 61.0168 | 0.007721 | 60.795 | 51.1288 | 51.0983 | 51.1181 | 51.0596 | 51.1128 | 51.2665 | 51.1599 | 123.1797 | 61.177 | 123.0697 | 60.9136 | 60.9857 | 121.9589 | 60.9498 | 121.737 | 62.194 | 62.2299 | 62.084 | 62.1199
8072.0625 | 123.3398 | -60.9238 | 62.1552 | -9.479 | -9.4912 | -9.4851 | -9.5758 | -9.5271 | -9.3413 | -9.4434 | 62.2193 | 0.22574 | 62.123 | -0.023943 | 0.052814 | 61.0305 | 0.012299 | 60.8179 | 51.4447 | 51.4326 | 51.4386 | 51.348 | 51.3967 | 51.5824 | 51.4804 | 123.1431 | 61.1495 | 123.0468 | 60.8998 | 60.9766 | 121.9543 | 60.9361 | 121.7416 | 62.1665 | 62.207 | 62.0702 | 62.1107
8073.0938 | 123.381 | -60.9467 | 62.1048 | -9.5248 | -9.5507 | -9.5309 | -9.5849 | -9.5317 | -9.3642 | -9.48 | 62.2193 | 0.23032 | 62.1368 | -0.023943 | 0.048236 | 61.0351 | 0.007721 | 60.8041 | 51.4218 | 51.3959 | 51.4157 | 51.3617 | 51.415 | 51.5824 | 51.4666 | 123.166 | 61.177 | 123.0834 | 60.9227 | 60.9949 | 121.9818 | 60.9544 | 121.7508 | 62.1711 | 62.2116 | 62.0885 | 62.1291
8074.0625 | 123.3124 | -60.8871 | 62.1735 | -9.5111 | -9.537 | -9.5126 | -9.5895 | -9.5408 | -9.3459 | -9.4754 | 62.2239 | 0.2349 | 62.1322 | -0.023943 | 0.039079 | 61.0351 | 0.016878 | 60.8133 | 51.3761 | 51.3502 | 51.3745 | 51.2977 | 51.3463 | 51.5413 | 51.4117 | 123.111 | 61.122 | 123.0194 | 60.8632 | 60.9262 | 121.9222 | 60.904 | 121.7004 | 62.1848 | 62.207 | 62.0931 | 62.1153
8075.0938 | 123.2803 | -60.9741 | 62.1231 | -8.8289 | -8.8456 | -8.835 | -8.8981 | -8.8587 | -8.5813 | -8.775 | 62.1827 | 0.2349 | 62.0818 | -0.028522 | 0.052814 | 61.0717 | 0.012299 | 60.8499 | 52.1452 | 52.1285 | 52.1392 | 52.076 | 52.1154 | 52.3928 | 52.1991 | 123.1568 | 61.209 | 123.056 | 60.9456 | 61.0269 | 122.0459 | 60.9864 | 121.824 | 62.1299 | 62.1704 | 62.029 | 62.0695
8076.0625 | 123.3353 | -60.9558 | 62.1094 | -8.1467 | -8.1725 | -8.1436 | -8.2205 | -8.172 | -7.8213 | -8.0974 | 62.1415 | 0.23032 | 62.0406 | -0.028522 | 0.057392 | 61.1129 | 0.007721 | 60.8957 | 52.8091 | 52.7833 | 52.8122 | 52.7353 | 52.7838 | 53.1345 | 52.8584 | 123.0973 | 61.1861 | 122.9964 | 60.9273 | 61.0132 | 122.0687 | 60.9635 | 121.8515 | 62.0841 | 62.1337 | 61.9832 | 62.0329
8077.0938 | 123.2895 | -60.9695 | 62.0773 | -8.632 | -8.6579 | -8.6381 | -8.7058 | -8.6573 | -8.4806 | -8.6147 | 62.1735 | 0.23032 | 62.0727 | -0.028522 | 0.043657 | 61.0855 | 0.021456 | 60.8591 | 52.3375 | 52.3117 | 52.3315 | 52.2637 | 52.3123 | 52.489 | 52.3548 | 123.1431 | 61.1999 | 123.0422 | 60.941 | 61.0132 | 122.055 | 60.991 | 121.8286 | 62.1299 | 62.1521 | 62.029 | 62.0512
8078.0625 | 123.2941 | -60.878 | 62.1735 | -10.0376 | -10.0407 | -10.0483 | -10.0931 | -10.049 | -9.9045 | -10.0111 | 62.2513 | 0.22574 | 62.1459 | -0.019364 | 0.048236 | 61.0031 | 0.012299 | 60.7812 | 50.8404 | 50.8373 | 50.8297 | 50.7849 | 50.829 | 50.9735 | 50.8669 | 123.1293 | 61.1037 | 123.0239 | 60.8586 | 60.9262 | 121.881 | 60.8903 | 121.6592 | 62.2031 | 62.239 | 62.0977 | 62.1336
8079.0938 | 123.3673 | -60.8871 | 62.1597 | -9.8407 | -9.8758 | -9.8377 | -9.9237 | -9.8704 | -9.671 | -9.8051 | 62.233 | 0.23032 | 62.1368 | -0.023943 | 0.048236 | 61.0168 | 0.016878 | 60.795 | 51.0464 | 51.0113 | 51.0495 | 50.9634 | 51.0167 | 51.2162 | 51.0821 | 123.1202 | 61.1175 | 123.0239 | 60.8632 | 60.9354 | 121.9039 | 60.904 | 121.6821 | 62.1848 | 62.2162 | 62.0885 | 62.1199
8080.0625 | 123.3124 | -60.8688 | 62.2238 | -10.3215 | -10.3337 | -10.323 | -10.3907 | -10.342 | -10.1288 | -10.2812 | 62.2605 | 0.22574 | 62.1551 | -0.028522 | 0.048236 | 60.9847 | 0.007721 | 60.7675 | 50.5474 | 50.5351 | 50.5458 | 50.4781 | 50.5269 | 50.74 | 50.5876 | 123.1293 | 61.0946 | 123.0239 | 60.8403 | 60.9171 | 121.8536 | 60.8766 | 121.6363 | 62.2123 | 62.2528 | 62.1069 | 62.1474
8081.1094 | 123.349 | -60.8551 | 62.1414 | -10.0971 | -10.1185 | -10.1078 | -10.1755 | -10.1222 | -9.8907 | -10.0706 | 62.2468 | 0.23032 | 62.1459 | -0.019364 | 0.052814 | 61.0031 | 0.021456 | 60.7767 | 50.758 | 50.7366 | 50.7473 | 50.6796 | 50.7329 | 50.9644 | 50.7845 | 123.1019 | 61.0854 | 123.001 | 60.8357 | 60.9079 | 121.8582 | 60.8766 | 121.6318 | 62.194 | 62.2253 | 62.0931 | 62.1245
8082.0625 | 123.349 | -60.8871 | 62.1918 | -10.6511 | -10.6771 | -10.6527 | -10.7066 | -10.6624 | -10.4584 | -10.62 | 62.2742 | 0.22116 | 62.1826 | -0.023943 | 0.048236 | 60.9664 | 0.007721 | 60.74 | 50.236 | 50.21 | 50.2345 | 50.1805 | 50.2247 | 50.4287 | 50.2672 | 123.1614 | 61.1083 | 123.0697 | 60.8632 | 60.9354 | 121.8536 | 60.8949 | 121.6272 | 62.226 | 62.2665 | 62.1343 | 62.1748
8083.0938 | 123.2941 | -60.8139 | 62.2742 | -10.4084 | -10.4344 | -10.4146 | -10.4777 | -10.4198 | -10.2066 | -10.3957 | 62.2742 | 0.2349 | 62.1688 | -0.019364 | 0.052814 | 60.9802 | 0.016878 | 60.7675 | 50.4055 | 50.3795 | 50.3993 | 50.3362 | 50.3941 | 50.6073 | 50.4183 | 123.0881 | 61.0488 | 122.9827 | 60.7945 | 60.8667 | 121.7941 | 60.8308 | 121.5814 | 62.2214 | 62.2574 | 62.116 | 62.152
8084.0625 | 123.3444 | -60.965 | 62.0865 | -9.36 | -9.4225 | -9.3478 | -9.4705 | -9.3898 | -9.0117 | -9.3427 | 62.2056 | 0.2349 | 62.1047 | -0.028522 | 0.043657 | 61.0488 | 0.012299 | 60.8179 | 51.605 | 51.5424 | 51.6172 | 51.4945 | 51.5752 | 51.9533 | 51.6223 | 123.1705 | 61.1999 | 123.0697 | 60.9364 | 61.0086 | 122.0138 | 60.9773 | 121.7828 | 62.1619 | 62.1933 | 62.0611 | 62.0924
8085.0781 | 123.2483 | -60.8826 | 62.2513 | -10.706 | -10.7275 | -10.703 | -10.7524 | -10.699 | -10.4768 | -10.6749 | 62.2834 | 0.23032 | 62.1917 | -0.023943 | 0.048236 | 60.9664 | 0.003143 | 60.74 | 50.1765 | 50.1551 | 50.1795 | 50.1301 | 50.1835 | 50.4058 | 50.2076 | 123.166 | 61.1129 | 123.0743 | 60.8586 | 60.9308 | 121.849 | 60.8857 | 121.6226 | 62.2352 | 62.2803 | 62.1435 | 62.1886
8086.0625 | 123.3261 | -60.8459 | 62.1964 | -10.5962 | -10.6222 | -10.6069 | -10.6517 | -10.6029 | -10.4264 | -10.5742 | 62.2834 | 0.24405 | 62.178 | -0.028522 | 0.048236 | 60.9664 | 0.012299 | 60.7446 | 50.2498 | 50.2238 | 50.2391 | 50.1942 | 50.243 | 50.4196 | 50.2717 | 123.1293 | 61.09 | 123.0239 | 60.8174 | 60.8942 | 121.8124 | 60.8582 | 121.5906 | 62.2352 | 62.2711 | 62.1298 | 62.1657
8087.0938 | 123.2071 | -60.8963 | 62.1826 | -9.8545 | -9.8896 | -9.856 | -9.9375 | -9.8796 | -9.7122 | -9.8646 | 62.2422 | 0.22574 | 62.1505 | -0.019364 | 0.043657 | 61.0122 | 0.012299 | 60.7858 | 51.0418 | 51.0067 | 51.0403 | 50.9588 | 51.0167 | 51.1841 | 51.0317 | 123.1385 | 61.122 | 123.0468 | 60.8769 | 60.94 | 121.9085 | 60.9086 | 121.6821 | 62.1985 | 62.2299 | 62.1069 | 62.1382
8088.0625 | 123.23 | -60.9055 | 62.2147 | -9.2318 | -9.2668 | -9.2241 | -9.3423 | -9.2845 | -9.1216 | -9.242 | 62.2147 | 0.23948 | 62.1185 | -0.023943 | 0.057392 | 61.0488 | 0.007721 | 60.827 | 51.6737 | 51.6386 | 51.6813 | 51.5632 | 51.621 | 51.7839 | 51.6635 | 123.1202 | 61.1449 | 123.0239 | 60.8815 | 60.9628 | 121.9543 | 60.9132 | 121.7325 | 62.1573 | 62.207 | 62.0611 | 62.1107
8089.0781 | 123.2117 | -60.9512 | 62.1689 | -10.0834 | -10.1231 | -10.0575 | -10.1664 | -10.0993 | -9.9274 | -10.0798 | 62.2513 | 0.23032 | 62.1688 | -0.014785 | 0.052814 | 60.9893 | 0.007721 | 60.7721 | 50.8679 | 50.8282 | 50.8938 | 50.7848 | 50.8519 | 51.0239 | 50.8715 | 123.2026 | 61.1816 | 123.1201 | 60.9364 | 61.004 | 121.9406 | 60.959 | 121.7233 | 62.1985 | 62.2436 | 62.116 | 62.1611
8090.0625 | 123.3307 | -60.9375 | 62.1094 | -9.1219 | -9.1524 | -9.1326 | -9.2461 | -9.1883 | -9.0163 | -9.1092 | 62.2056 | 0.2349 | 62.1139 | -0.023943 | 0.052814 | 61.0534 | 0.012299 | 60.827 | 51.8156 | 51.7851 | 51.8049 | 51.6914 | 51.7492 | 51.9212 | 51.8283 | 123.1431 | 61.1724 | 123.0514 | 60.9136 | 60.9903 | 121.9909 | 60.9498 | 121.7645 | 62.1527 | 62.1933 | 62.0611 | 62.1016
8091.0625 | 123.3261 | -60.9009 | 62.1689 | -9.621 | -9.6286 | -9.6225 | -9.704 | -9.6553 | -9.4832 | -9.6082 | 62.2285 | 0.23948 | 62.1414 | -0.028522 | 0.048236 | 61.0305 | 0.016878 | 60.8133 | 51.2799 | 51.2723 | 51.2784 | 51.1969 | 51.2456 | 51.4176 | 51.2927 | 123.1293 | 61.1404 | 123.0422 | 60.8724 | 60.9491 | 121.9314 | 60.9178 | 121.7142 | 62.1802 | 62.2116 | 62.0931 | 62.1245
8092.0938 | 123.349 | -60.9604 | 62.0773 | -9.1906 | -9.2165 | -9.1829 | -9.2782 | -9.2295 | -9.0208 | -9.1641 | 62.201 | 0.2349 | 62.1093 | -0.033101 | 0.048236 | 61.0443 | 0.007721 | 60.827 | 51.7698 | 51.7439 | 51.7774 | 51.6822 | 51.7309 | 51.9396 | 51.7963 | 123.1614 | 61.1953 | 123.0697 | 60.9273 | 61.0086 | 122.0046 | 60.9681 | 121.7874 | 62.1527 | 62.1933 | 62.0611 | 62.1016
8093.0625 | 123.3719 | -60.9375 | 62.1048 | -9.2455 | -9.2668 | -9.2516 | -9.3606 | -9.3119 | -9.1353 | -9.2282 | 62.2056 | 0.23948 | 62.1139 | -0.028522 | 0.048236 | 61.0443 | 0.007721 | 60.827 | 51.692 | 51.6707 | 51.6859 | 51.5769 | 51.6256 | 51.8022 | 51.7093 | 123.1431 | 61.177 | 123.0514 | 60.909 | 60.9857 | 121.9818 | 60.9452 | 121.7645 | 62.1573 | 62.1978 | 62.0657 | 62.1062
8094.0938 | 123.349 | -60.9787 | 62.0773 | -8.9113 | -8.9509 | -8.9128 | -9.0309 | -8.9777 | -8.7782 | -8.9032 | 62.1872 | 0.23032 | 62.091 | -0.023943 | 0.048236 | 61.0626 | 0.012299 | 60.8407 | 52.0674 | 52.0278 | 52.0659 | 51.9478 | 52.001 | 52.2005 | 52.0755 | 123.1659 | 61.209 | 123.0697 | 60.9548 | 61.0269 | 122.0413 | 60.991 | 121.8194 | 62.139 | 62.1749 | 62.0428 | 62.0787
8095.0625 | 123.3444 | -60.8963 | 62.1552 | -9.4332 | -9.45 | -9.4302 | -9.5391 | -9.495 | -9.2818 | -9.4251 | 62.2056 | 0.23032 | 62.1139 | -0.033101 | 0.048236 | 61.0351 | 0.012299 | 60.8133 | 51.4631 | 51.4463 | 51.4661 | 51.3572 | 51.4013 | 51.6145 | 51.4712 | 123.1019 | 61.1266 | 123.0102 | 60.8632 | 60.9445 | 121.9314 | 60.9086 | 121.7096 | 62.1573 | 62.1933 | 62.0657 | 62.1016
8096.0625 | 123.3673 | -60.9146 | 62.1094 | -9.1311 | -9.1478 | -9.1234 | -9.2003 | -9.1471 | -8.9522 | -9.1046 | 62.1872 | 0.23032 | 62.0956 | -0.033101 | 0.048236 | 61.0488 | 0.012299 | 60.8316 | 51.7835 | 51.7668 | 51.7912 | 51.7143 | 51.7675 | 51.9625 | 51.81 | 123.1019 | 61.1449 | 123.0102 | 60.8815 | 60.9628 | 121.9635 | 60.9269 | 121.7462 | 62.139 | 62.1749 | 62.0473 | 62.0833
8097.0938 | 123.2803 | -60.8826 | 62.2009 | -9.8636 | -9.8804 | -9.8789 | -9.9329 | -9.8933 | -9.6984 | -9.8417 | 62.2422 | 0.23032 | 62.1414 | -0.023943 | 0.052814 | 61.0122 | 0.007721 | 60.795 | 51.019 | 51.0022 | 51.0037 | 50.9497 | 50.9892 | 51.1841 | 51.0409 | 123.1248 | 61.1129 | 123.0239 | 60.8586 | 60.9354 | 121.8948 | 60.8903 | 121.6775 | 62.1894 | 62.2345 | 62.0885 | 62.1336
8098.0625 | 123.262 | -60.9238 | 62.2055 | -10.3993 | -10.4207 | -10.4008 | -10.4686 | -10.4198 | -10.1883 | -10.3728 | 62.2651 | 0.2349 | 62.1734 | -0.033101 | 0.043657 | 60.9802 | 0.021456 | 60.7583 | 50.5245 | 50.5031 | 50.5229 | 50.4552 | 50.504 | 50.7354 | 50.551 | 123.1888 | 61.1587 | 123.0972 | 60.8907 | 60.9674 | 121.9039 | 60.9452 | 121.6821 | 62.2214 | 62.2436 | 62.1298 | 62.152
8099.0938 | 123.317 | -60.8459 | 62.2787 | -10.6831 | -10.7046 | -10.6893 | -10.7204 | -10.6716 | -10.4493 | -10.6475 | 62.2834 | 0.23948 | 62.2009 | -0.023943 | 0.057392 | 60.9619 | 0.007721 | 60.7492 | 50.1628 | 50.1414 | 50.1566 | 50.1256 | 50.1744 | 50.3967 | 50.1985 | 123.1293 | 61.0854 | 123.0468 | 60.822 | 60.9033 | 121.8078 | 60.8537 | 121.5951 | 62.226 | 62.2757 | 62.1435 | 62.1932
8100.0625 | 123.2437 | -60.8551 | 62.2696 | -10.7839 | -10.8053 | -10.7855 | -10.8165 | -10.7677 | -10.5134 | -10.7299 | 62.3017 | 0.23948 | 62.21 | -0.028522 | 0.043657 | 60.9664 | 0.012299 | 60.7355 | 50.0712 | 50.0498 | 50.0697 | 50.0386 | 50.0874 | 50.3417 | 50.1252 | 123.1568 | 61.0946 | 123.0651 | 60.8266 | 60.8988 | 121.8215 | 60.8674 | 121.5906 | 62.2581 | 62.2894 | 62.1664 | 62.1977
8101.1094 | 123.2758 | -60.8139 | 62.2971 | -10.8068 | -10.8374 | -10.8083 | -10.8577 | -10.8135 | -10.5912 | -10.7756 | 62.3017 | 0.24405 | 62.21 | -0.019364 | 0.052814 | 60.9619 | 0.012299 | 60.7446 | 50.0071 | 49.9765 | 50.0056 | 49.9562 | 50.0004 | 50.2227 | 50.0383 | 123.1156 | 61.058 | 123.0239 | 60.7945 | 60.8667 | 121.7758 | 60.8262 | 121.5585 | 62.2489 | 62.2894 | 62.1572 | 62.1977
8102.0625 | 123.2346 | -60.8368 | 62.265 | -10.6053 | -10.6405 | -10.6069 | -10.67 | -10.6212 | -10.4539 | -10.5742 | 62.2834 | 0.23032 | 62.1963 | -0.028522 | 0.048236 | 60.9664 | 0.016878 | 60.7538 | 50.2315 | 50.1963 | 50.2299 | 50.1668 | 50.2156 | 50.3829 | 50.2626 | 123.1202 | 61.0671 | 123.0331 | 60.8083 | 60.885 | 121.8032 | 60.8537 | 121.5906 | 62.2352 | 62.2665 | 62.1481 | 62.1794
8103.0781 | 123.2162 | -60.8368 | 62.2925 | -10.7884 | -10.8099 | -10.7855 | -10.8486 | -10.8089 | -10.6965 | -10.7756 | 62.2971 | 0.24405 | 62.21 | -0.028522 | 0.043657 | 60.9619 | 0.007721 | 60.7538 | 50.0483 | 50.0269 | 50.0513 | 49.9882 | 50.0279 | 50.1403 | 50.0611 | 123.1339 | 61.0808 | 123.0468 | 60.8083 | 60.8804 | 121.7986 | 60.8445 | 121.5906 | 62.2535 | 62.2894 | 62.1664 | 62.2023
8104.0625 | 123.2437 | -60.8368 | 62.265 | -10.8571 | -10.8832 | -10.8587 | -10.9264 | -10.8776 | -10.7744 | -10.8443 | 62.2971 | 0.23948 | 62.2192 | -0.023943 | 0.048236 | 60.9573 | 0.012299 | 60.74 | 49.9797 | 49.9536 | 49.9781 | 49.9104 | 49.9592 | 50.0624 | 49.9925 | 123.1339 | 61.0763 | 123.056 | 60.8128 | 60.885 | 121.7941 | 60.8491 | 121.5768 | 62.2489 | 62.2848 | 62.171 | 62.2069
8105.0781 | 123.2574 | -60.8093 | 62.3154 | -11.2646 | -11.2815 | -11.2708 | -11.3339 | -11.2804 | -11.1864 | -11.2701 | 62.32 | 0.23948 | 62.2421 | -0.023943 | 0.048236 | 60.939 | 0.012299 | 60.7171 | 49.5447 | 49.5278 | 49.5385 | 49.4754 | 49.5289 | 49.6229 | 49.5392 | 123.1293 | 61.0488 | 123.0514 | 60.7854 | 60.8576 | 121.7483 | 60.8216 | 121.5265 | 62.2718 | 62.3077 | 62.1938 | 62.2298
8106.0625 | 123.2483 | -60.8826 | 62.2101 | -10.8388 | -10.8694 | -10.8312 | -10.9127 | -10.8547 | -10.7469 | -10.8214 | 62.3063 | 0.2349 | 62.21 | -0.023943 | 0.048236 | 60.9573 | 0.012299 | 60.7309 | 50.0438 | 50.0131 | 50.0513 | 49.9699 | 50.0279 | 50.1357 | 50.0611 | 123.1889 | 61.1175 | 123.0926 | 60.8586 | 60.9308 | 121.8398 | 60.8949 | 121.6134 | 62.2581 | 62.294 | 62.1618 | 62.1977
8107.0938 | 123.1888 | -60.8597 | 62.2787 | -11.0632 | -11.0846 | -11.0693 | -11.1141 | -11.0607 | -10.9895 | -11.0503 | 62.3109 | 0.24405 | 62.2329 | -0.023943 | 0.052814 | 60.9481 | 0.016878 | 60.7171 | 49.7965 | 49.7751 | 49.7904 | 49.7455 | 49.799 | 49.8701 | 49.8093 | 123.1705 | 61.1037 | 123.0926 | 60.8357 | 60.9125 | 121.8078 | 60.8766 | 121.5768 | 62.2581 | 62.294 | 62.1801 | 62.216
8108.0625 | 123.23 | -60.8276 | 62.2787 | -11.2188 | -11.2495 | -11.2204 | -11.2606 | -11.2026 | -11.1223 | -11.206 | 62.32 | 0.2349 | 62.2421 | -0.023943 | 0.052814 | 60.9435 | 0.016878 | 60.7126 | 49.6088 | 49.5782 | 49.6072 | 49.567 | 49.625 | 49.7053 | 49.6216 | 123.1477 | 61.0625 | 123.0697 | 60.8037 | 60.8805 | 121.7712 | 60.8445 | 121.5402 | 62.2672 | 62.3031 | 62.1893 | 62.2252
8109.0781 | 123.2849 | -60.8414 | 62.2787 | -10.8251 | -10.8328 | -10.8221 | -10.8669 | -10.8181 | -10.7377 | -10.8077 | 62.288 | 0.2349 | 62.2146 | -0.019364 | 0.048236 | 60.9573 | 0.012299 | 60.7446 | 50.0163 | 50.0086 | 50.0193 | 49.9745 | 50.0233 | 50.1036 | 50.0337 | 123.1293 | 61.0763 | 123.056 | 60.822 | 60.8896 | 121.7986 | 60.8537 | 121.586 | 62.2397 | 62.2757 | 62.1664 | 62.2023
8110.0625 | 123.2941 | -60.8826 | 62.1872 | -10.761 | -10.7824 | -10.7488 | -10.8165 | -10.7677 | -10.6828 | -10.7344 | 62.3017 | 0.23032 | 62.2146 | -0.019364 | 0.052814 | 60.9619 | 0.012299 | 60.7492 | 50.1216 | 50.1001 | 50.1337 | 50.066 | 50.1148 | 50.1998 | 50.1481 | 123.1843 | 61.1129 | 123.0972 | 60.8632 | 60.9354 | 121.8444 | 60.8949 | 121.6318 | 62.2489 | 62.2894 | 62.1618 | 62.2023
8111.1094 | 123.2895 | -60.8276 | 62.2879 | -11.315 | -11.3319 | -11.2983 | -11.3751 | -11.3217 | -11.2185 | -11.2792 | 62.3246 | 0.23032 | 62.2283 | -0.028522 | 0.048236 | 60.9298 | 0.016878 | 60.708 | 49.5127 | 49.4958 | 49.5294 | 49.4525 | 49.506 | 49.6092 | 49.5484 | 123.1522 | 61.058 | 123.056 | 60.7991 | 60.8759 | 121.7574 | 60.8445 | 121.5356 | 62.2764 | 62.3077 | 62.1801 | 62.2115
8112.0625 | 123.2712 | -60.8093 | 62.3154 | -11.6171 | -11.6387 | -11.6142 | -11.6864 | -11.633 | -11.5344 | -11.5951 | 62.3383 | 0.23032 | 62.2329 | -0.023943 | 0.052814 | 60.9161 | 0.003143 | 60.6988 | 49.1922 | 49.1707 | 49.1951 | 49.1229 | 49.1764 | 49.275 | 49.2142 | 123.1477 | 61.0396 | 123.0423 | 60.7854 | 60.8621 | 121.7254 | 60.8125 | 121.5082 | 62.2855 | 62.3352 | 62.1801 | 62.2298
8113.0938 | 123.2529 | -60.8276 | 62.2742 | -11.6263 | -11.657 | -11.6188 | -11.6544 | -11.6009 | -11.4382 | -11.5814 | 62.3246 | 0.22574 | 62.2283 | -0.023943 | 0.048236 | 60.9161 | 0.016878 | 60.6942 | 49.2013 | 49.1707 | 49.2089 | 49.1732 | 49.2267 | 49.3894 | 49.2462 | 123.1522 | 61.0534 | 123.056 | 60.8037 | 60.8759 | 121.7437 | 60.8445 | 121.5219 | 62.2764 | 62.3077 | 62.1801 | 62.2115
8114.0625 | 123.3124 | -60.8551 | 62.2559 | -11.2509 | -11.2632 | -11.2479 | -11.3202 | -11.2804 | -11.1727 | -11.2243 | 62.32 | 0.22574 | 62.2192 | -0.028522 | 0.043657 | 60.9298 | 0.012299 | 60.7217 | 49.6042 | 49.5919 | 49.6072 | 49.5349 | 49.5747 | 49.6824 | 49.6308 | 123.1751 | 61.0808 | 123.0743 | 60.8266 | 60.8988 | 121.7849 | 60.8674 | 121.5768 | 62.2764 | 62.3077 | 62.1755 | 62.2069
8115.0781 | 123.3307 | -60.7132 | 62.3474 | -11.8644 | -11.8905 | -11.8706 | -11.9474 | -11.8985 | -11.7999 | -11.8424 | 62.3429 | 0.2349 | 62.2512 | -0.023943 | 0.057392 | 60.8978 | 0.007721 | 60.6897 | 48.8488 | 48.8227 | 48.8426 | 48.7658 | 48.8147 | 48.9133 | 48.8708 | 123.0561 | 60.9481 | 122.9644 | 60.6893 | 60.7706 | 121.611 | 60.7209 | 121.4029 | 62.2855 | 62.3352 | 62.1938 | 62.2435
8116.0625 | 123.2666 | -60.8414 | 62.2559 | -10.9487 | -10.9885 | -10.9365 | -11.0363 | -10.9783 | -10.8522 | -10.9588 | 62.3017 | 0.23032 | 62.1963 | -0.033101 | 0.052814 | 60.9527 | 0.012299 | 60.7309 | 49.8927 | 49.8529 | 49.9048 | 49.8051 | 49.8631 | 49.9892 | 49.8826 | 123.1431 | 61.0717 | 123.0377 | 60.8083 | 60.8942 | 121.7941 | 60.8537 | 121.5722 | 62.2489 | 62.2894 | 62.1435 | 62.184
8117.0938 | 123.262 | -60.7727 | 62.3108 | -11.9147 | -11.9271 | -11.9118 | -11.984 | -11.9259 | -11.8365 | -11.8927 | 62.3567 | 0.2349 | 62.2512 | -0.023943 | 0.052814 | 60.8932 | 0.012299 | 60.6897 | 48.858 | 48.8456 | 48.8609 | 48.7887 | 48.8468 | 48.9362 | 48.88 | 123.1294 | 61.0076 | 123.0239 | 60.7488 | 60.8255 | 121.6659 | 60.785 | 121.4624 | 62.3038 | 62.3444 | 62.1984 | 62.2389
8118.0625 | 123.2574 | -60.8276 | 62.2787 | -10.9578 | -10.9931 | -10.9594 | -11.0455 | -10.9875 | -10.8842 | -10.9633 | 62.3017 | 0.23948 | 62.2009 | -0.019364 | 0.043657 | 60.9527 | 0.007721 | 60.7355 | 49.8698 | 49.8346 | 49.8682 | 49.7822 | 49.8402 | 49.9434 | 49.8643 | 123.1293 | 61.0671 | 123.0285 | 60.8083 | 60.8713 | 121.7803 | 60.8354 | 121.5631 | 62.2581 | 62.294 | 62.1572 | 62.1932
8119.0781 | 123.2483 | -60.9055 | 62.2192 | -9.827 | -9.8483 | -9.8148 | -9.9283 | -9.8842 | -9.7763 | -9.8921 | 62.2376 | 0.2349 | 62.1414 | -0.028522 | 0.052814 | 61.0122 | 0.021456 | 60.8041 | 51.0785 | 51.0571 | 51.0907 | 50.9772 | 51.0213 | 51.1292 | 51.0134 | 123.1431 | 61.1404 | 123.0468 | 60.8769 | 60.9583 | 121.9177 | 60.9269 | 121.7096 | 62.1848 | 62.2162 | 62.0885 | 62.1199
8120.0625 | 123.2483 | -60.8505 | 62.2375 | -9.9048 | -9.9079 | -9.9155 | -9.9604 | -9.93 | -9.8175 | -9.8783 | 62.2468 | 0.23032 | 62.1459 | -0.028522 | 0.048236 | 61.0122 | 0.007721 | 60.795 | 50.9457 | 50.9427 | 50.935 | 50.8902 | 50.9206 | 51.0331 | 50.9722 | 123.0973 | 61.0808 | 122.9965 | 60.822 | 60.8988 | 121.8627 | 60.8582 | 121.6455 | 62.1985 | 62.239 | 62.0977 | 62.1382
8121.1094 | 123.23 | -60.8963 | 62.2696 | -9.9414 | -9.9491 | -9.9521 | -10.0199 | -9.9757 | -9.8678 | -9.9241 | 62.2422 | 0.24863 | 62.1459 | -0.023943 | 0.057392 | 61.0031 | 0.012299 | 60.795 | 50.9549 | 50.9472 | 50.9442 | 50.8764 | 50.9206 | 51.0285 | 50.9722 | 123.1385 | 61.1449 | 123.0422 | 60.8724 | 60.9537 | 121.8994 | 60.9086 | 121.6913 | 62.1848 | 62.2299 | 62.0885 | 62.1336
8122.0625 | 123.3078 | -60.8597 | 62.2375 | -10.0193 | -10.0223 | -10.0162 | -10.084 | -10.0352 | -9.909 | -9.9836 | 62.2468 | 0.22574 | 62.1459 | -0.028522 | 0.052814 | 61.0122 | 0.012299 | 60.7904 | 50.8404 | 50.8373 | 50.8434 | 50.7757 | 50.8244 | 50.9506 | 50.8761 | 123.1064 | 61.0854 | 123.0056 | 60.8312 | 60.9125 | 121.8719 | 60.872 | 121.6501 | 62.194 | 62.2345 | 62.0931 | 62.1336
8123.0781 | 123.3444 | -60.7773 | 62.265 | -11.1639 | -11.1854 | -11.1609 | -11.2149 | -11.1523 | -11.0582 | -11.1236 | 62.3063 | 0.23032 | 62.2146 | -0.019364 | 0.052814 | 60.9344 | 0.003143 | 60.7217 | 49.6134 | 49.5919 | 49.6164 | 49.5624 | 49.625 | 49.7191 | 49.6537 | 123.0836 | 61.0076 | 122.9919 | 60.7579 | 60.8301 | 121.7117 | 60.7804 | 121.499 | 62.2535 | 62.3031 | 62.1618 | 62.2115
8124.0625 | 123.262 | -60.8139 | 62.3199 | -11.2005 | -11.222 | -11.2021 | -11.2561 | -11.2072 | -11.1223 | -11.1556 | 62.32 | 0.23032 | 62.2055 | -0.019364 | 0.048236 | 60.9344 | 0.012299 | 60.7171 | 49.6134 | 49.5919 | 49.6118 | 49.5578 | 49.6067 | 49.6916 | 49.6583 | 123.1339 | 61.0442 | 123.0194 | 60.7945 | 60.8621 | 121.7483 | 60.8262 | 121.531 | 62.2718 | 62.3077 | 62.1572 | 62.1932
8125.0781 | 123.3582 | -60.8002 | 62.2879 | -11.5668 | -11.5929 | -11.5776 | -11.604 | -11.5597 | -11.4748 | -11.5356 | 62.3383 | 0.23032 | 62.2283 | -0.028522 | 0.057392 | 60.9207 | 0.012299 | 60.6988 | 49.2334 | 49.2073 | 49.2226 | 49.1961 | 49.2405 | 49.3253 | 49.2646 | 123.1385 | 61.0305 | 123.0285 | 60.7716 | 60.8576 | 121.7208 | 60.8125 | 121.499 | 62.2809 | 62.326 | 62.171 | 62.216
8126.0625 | 123.1934 | -60.7636 | 62.3428 | -12.1345 | -12.1378 | -12.1407 | -12.2359 | -12.1915 | -12.0288 | -12.0987 | 62.3612 | 0.2349 | 62.2604 | -0.023943 | 0.043657 | 60.8794 | 0.012299 | 60.6622 | 48.6291 | 48.6258 | 48.6228 | 48.5277 | 48.5721 | 48.7347 | 48.6648 | 123.1248 | 60.9984 | 123.0239 | 60.7396 | 60.8072 | 121.643 | 60.7758 | 121.4258 | 62.3176 | 62.3489 | 62.2167 | 62.2481
8127.0781 | 123.3078 | -60.7498 | 62.3474 | -11.8598 | -11.8813 | -11.8568 | -12.0161 | -11.9534 | -11.777 | -11.8378 | 62.3521 | 0.2349 | 62.2512 | -0.023943 | 0.052814 | 60.8932 | 0.016878 | 60.6851 | 48.89 | 48.8685 | 48.893 | 48.7337 | 48.7964 | 48.9728 | 48.912 | 123.1019 | 60.9847 | 123.0011 | 60.7259 | 60.8026 | 121.643 | 60.7667 | 121.4349 | 62.2993 | 62.3352 | 62.1984 | 62.2344
8128.0625 | 123.2849 | -60.7864 | 62.3199 | -11.7087 | -11.7302 | -11.7103 | -11.7689 | -11.7291 | -11.6351 | -11.6775 | 62.3475 | 0.2349 | 62.2375 | -0.028522 | 0.048236 | 60.9069 | 0.012299 | 60.6988 | 49.0777 | 49.0562 | 49.0761 | 49.0176 | 49.0573 | 49.1513 | 49.1089 | 123.1339 | 61.0213 | 123.0239 | 60.7579 | 60.8347 | 121.6934 | 60.7987 | 121.4853 | 62.2993 | 62.3352 | 62.1893 | 62.2252
8129.0938 | 123.2529 | -60.7819 | 62.3657 | -12.1711 | -12.1744 | -12.1773 | -12.1855 | -12.1594 | -12.0105 | -12.117 | 62.3658 | 0.23032 | 62.2604 | -0.019364 | 0.052814 | 60.884 | 0.007721 | 60.6714 | 48.6107 | 48.6075 | 48.6045 | 48.5964 | 48.6224 | 48.7713 | 48.6648 | 123.1477 | 61.0122 | 123.0423 | 60.7625 | 60.8347 | 121.6659 | 60.7896 | 121.4532 | 62.313 | 62.3581 | 62.2076 | 62.2527
8130.0625 | 123.2712 | -60.7498 | 62.3795 | -12.5237 | -12.5361 | -12.5162 | -12.5564 | -12.5211 | -12.4272 | -12.4787 | 62.3933 | 0.23948 | 62.2924 | -0.023943 | 0.048236 | 60.8657 | 0.016878 | 60.6439 | 48.2262 | 48.2137 | 48.2337 | 48.1935 | 48.2287 | 48.3227 | 48.2711 | 123.1431 | 60.9893 | 123.0423 | 60.7259 | 60.7981 | 121.6155 | 60.7667 | 121.3937 | 62.345 | 62.3764 | 62.2442 | 62.2756
8131.1094 | 123.3673 | -60.6949 | 62.3428 | -12.0979 | -12.1378 | -12.0995 | -12.2313 | -12.1686 | -12.0151 | -12.1354 | 62.3658 | 0.2349 | 62.2741 | -0.028522 | 0.048236 | 60.8886 | 0.012299 | 60.6759 | 48.597 | 48.5571 | 48.5954 | 48.4636 | 48.5263 | 48.6798 | 48.5595 | 123.0607 | 60.9298 | 122.969 | 60.6664 | 60.7431 | 121.5835 | 60.7072 | 121.3708 | 62.3176 | 62.3535 | 62.2259 | 62.2618
8132.0625 | 123.2483 | -60.8322 | 62.3016 | -11.1593 | -11.1945 | -11.1517 | -11.2515 | -11.1889 | -10.985 | -11.1373 | 62.3109 | 0.2349 | 62.2192 | -0.023943 | 0.043657 | 60.9344 | 0.012299 | 60.7263 | 49.6729 | 49.6377 | 49.6805 | 49.5807 | 49.6433 | 49.8473 | 49.6949 | 123.1431 | 61.0671 | 123.0514 | 60.8083 | 60.8759 | 121.7666 | 60.8445 | 121.5585 | 62.2672 | 62.2986 | 62.1755 | 62.2069
8133.0781 | 123.3856 | -60.6995 | 62.3337 | -12.6015 | -12.6277 | -12.6032 | -12.6433 | -12.5897 | -12.5508 | -12.5794 | 62.3933 | 0.23948 | 62.3016 | -0.023943 | 0.052814 | 60.8611 | 0.012299 | 60.6439 | 48.098 | 48.0718 | 48.0963 | 48.0561 | 48.1097 | 48.1487 | 48.12 | 123.0927 | 60.9389 | 123.0011 | 60.6755 | 60.7523 | 121.5606 | 60.7118 | 121.3434 | 62.3405 | 62.381 | 62.2488 | 62.2893
8134.0625 | 123.317 | -60.7452 | 62.3062 | -12.4779 | -12.4812 | -12.4658 | -12.5014 | -12.4478 | -12.4043 | -12.4284 | 62.3887 | 0.2349 | 62.297 | -0.023943 | 0.052814 | 60.8703 | 0.012299 | 60.653 | 48.2674 | 48.2641 | 48.2794 | 48.2438 | 48.2974 | 48.341 | 48.3169 | 123.1339 | 60.9801 | 123.0423 | 60.7213 | 60.7981 | 121.6155 | 60.7575 | 121.3983 | 62.3359 | 62.3764 | 62.2442 | 62.2847
8135.0938 | 123.3902 | -60.7636 | 62.265 | -11.4798 | -11.5013 | -11.4677 | -11.5354 | -11.4773 | -11.4245 | -11.4669 | 62.3383 | 0.2349 | 62.2421 | -0.028522 | 0.057392 | 60.9207 | 0.016878 | 60.6988 | 49.2838 | 49.2623 | 49.2959 | 49.2282 | 49.2862 | 49.3391 | 49.2966 | 123.1019 | 60.9984 | 123.0056 | 60.735 | 60.8209 | 121.6842 | 60.7804 | 121.4624 | 62.2809 | 62.3215 | 62.1847 | 62.2252
8136.0625 | 123.2346 | -60.7956 | 62.3108 | -12.5328 | -12.5453 | -12.5345 | -12.5564 | -12.5073 | -12.4546 | -12.497 | 62.3979 | 0.23948 | 62.3062 | -0.028522 | 0.048236 | 60.8566 | 0.012299 | 60.6439 | 48.2628 | 48.2503 | 48.2611 | 48.2392 | 48.2883 | 48.341 | 48.2986 | 123.1934 | 61.0351 | 123.1018 | 60.7671 | 60.8438 | 121.6522 | 60.8079 | 121.4395 | 62.3496 | 62.3856 | 62.2579 | 62.2939
8137.0938 | 123.3307 | -60.7269 | 62.3337 | -12.6702 | -12.6872 | -12.6581 | -12.7166 | -12.6538 | -12.5645 | -12.639 | 62.3979 | 0.2349 | 62.3153 | -0.033101 | 0.048236 | 60.8611 | 0.016878 | 60.6302 | 48.0568 | 48.0397 | 48.0688 | 48.0103 | 48.0731 | 48.1624 | 48.088 | 123.1248 | 60.9618 | 123.0423 | 60.6938 | 60.7752 | 121.5881 | 60.7438 | 121.3571 | 62.3496 | 62.381 | 62.2671 | 62.2985
8138.0625 | 123.2346 | -60.7407 | 62.3611 | -12.5328 | -12.5453 | -12.5345 | -12.5609 | -12.5165 | -12.4638 | -12.5108 | 62.3979 | 0.2349 | 62.3108 | -0.019364 | 0.052814 | 60.8566 | 0.012299 | 60.6485 | 48.2078 | 48.1954 | 48.2062 | 48.1797 | 48.2242 | 48.2769 | 48.2299 | 123.1385 | 60.9756 | 123.0514 | 60.7213 | 60.7935 | 121.5972 | 60.753 | 121.3891 | 62.345 | 62.3856 | 62.2579 | 62.2985
8139.0938 | 123.2483 | -60.8276 | 62.2787 | -11.933 | -11.9683 | -11.9301 | -11.9795 | -11.9214 | -11.8823 | -11.9293 | 62.3658 | 0.2349 | 62.2787 | -0.023943 | 0.052814 | 60.8886 | 0.012299 | 60.6622 | 48.8946 | 48.8593 | 48.8975 | 48.8482 | 48.9063 | 48.9453 | 48.8983 | 123.1934 | 61.0625 | 123.1063 | 60.8037 | 60.8805 | 121.7162 | 60.8399 | 121.4898 | 62.313 | 62.3535 | 62.2259 | 62.2664
8140.0625 | 123.2437 | -60.7544 | 62.3795 | -11.9285 | -11.9363 | -11.9255 | -11.9566 | -11.9214 | -11.8686 | -11.8973 | 62.3567 | 0.2349 | 62.2833 | -0.014785 | 0.057392 | 60.8978 | 0.016878 | 60.6759 | 48.8259 | 48.8181 | 48.8289 | 48.7978 | 48.833 | 48.8858 | 48.8571 | 123.111 | 60.9893 | 123.0377 | 60.7396 | 60.8118 | 121.6522 | 60.7713 | 121.4303 | 62.2993 | 62.3398 | 62.2259 | 62.2664
8141.0938 | 123.317 | -60.8643 | 62.2055 | -10.0513 | -10.0773 | -10.0437 | -10.0977 | -10.0581 | -10.0235 | -10.0614 | 62.2468 | 0.2349 | 62.1734 | -0.028522 | 0.043657 | 60.9985 | 0.012299 | 60.7767 | 50.8129 | 50.787 | 50.8205 | 50.7666 | 50.8061 | 50.8408 | 50.8028 | 123.111 | 61.0992 | 123.0377 | 60.8357 | 60.9079 | 121.8627 | 60.8766 | 121.6409 | 62.2031 | 62.2345 | 62.1298 | 62.1611
8142.0625 | 123.2071 | -60.8047 | 62.2925 | -10.8846 | -10.8877 | -10.8999 | -10.931 | -10.8959 | -10.8568 | -10.8626 | 62.3017 | 0.23948 | 62.2009 | -0.028522 | 0.043657 | 60.9527 | 0.012299 | 60.7355 | 49.9202 | 49.917 | 49.9048 | 49.8738 | 49.9088 | 49.948 | 49.9421 | 123.1065 | 61.0442 | 123.0056 | 60.7762 | 60.8484 | 121.7574 | 60.817 | 121.5402 | 62.2581 | 62.2894 | 62.1572 | 62.1886
8143.0938 | 123.3398 | -60.7819 | 62.2925 | -11.6583 | -11.6753 | -11.66 | -11.7231 | -11.6742 | -11.6076 | -11.6363 | 62.3338 | 0.23032 | 62.2512 | -0.028522 | 0.048236 | 60.9069 | 0.016878 | 60.6942 | 49.1235 | 49.1066 | 49.1219 | 49.0588 | 49.1077 | 49.1742 | 49.1455 | 123.1156 | 61.0122 | 123.0331 | 60.7533 | 60.8301 | 121.6888 | 60.7987 | 121.4761 | 62.2855 | 62.3169 | 62.203 | 62.2344
8144.0625 | 123.2437 | -60.7956 | 62.3795 | -11.7545 | -11.7714 | -11.7561 | -11.7826 | -11.7337 | -11.6992 | -11.7325 | 62.3475 | 0.23948 | 62.2512 | -0.023943 | 0.052814 | 60.9023 | 0.012299 | 60.6851 | 49.0411 | 49.0241 | 49.0395 | 49.013 | 49.0619 | 49.0964 | 49.0631 | 123.1431 | 61.0351 | 123.0468 | 60.7716 | 60.8484 | 121.6979 | 60.8079 | 121.4807 | 62.2947 | 62.3352 | 62.1984 | 62.2389
8145.0781 | 123.3536 | -60.7132 | 62.3199 | -12.2123 | -12.2248 | -12.2186 | -12.2496 | -12.1915 | -12.1662 | -12.1811 | 62.3704 | 0.23032 | 62.265 | -0.028522 | 0.048236 | 60.8749 | 0.003143 | 60.6668 | 48.5009 | 48.4884 | 48.4946 | 48.4636 | 48.5217 | 48.547 | 48.5321 | 123.0836 | 60.9435 | 122.9782 | 60.6847 | 60.7614 | 121.5881 | 60.7163 | 121.38 | 62.3222 | 62.3672 | 62.2167 | 62.2618
8146.0625 | 123.2391 | -60.7544 | 62.3749 | -12.1986 | -12.211 | -12.2002 | -12.2221 | -12.1869 | -12.1387 | -12.1537 | 62.3704 | 0.2349 | 62.265 | -0.023943 | 0.052814 | 60.884 | 0.012299 | 60.6576 | 48.5558 | 48.5434 | 48.5542 | 48.5323 | 48.5675 | 48.6157 | 48.6007 | 123.1248 | 60.9893 | 123.0194 | 60.7305 | 60.8072 | 121.6384 | 60.7667 | 121.412 | 62.3176 | 62.3581 | 62.2122 | 62.2527
8147.0781 | 123.3719 | -60.759 | 62.3016 | -11.4889 | -11.4876 | -11.486 | -11.4987 | -11.4681 | -11.3924 | -11.412 | 62.3292 | 0.22574 | 62.2283 | -0.028522 | 0.057392 | 60.9252 | 0.007721 | 60.7171 | 49.27 | 49.2714 | 49.273 | 49.2602 | 49.2908 | 49.3665 | 49.347 | 123.0882 | 60.9847 | 122.9873 | 60.7304 | 60.8164 | 121.6842 | 60.7667 | 121.4761 | 62.2718 | 62.3215 | 62.171 | 62.2206
8148.0625 | 123.2483 | -60.878 | 62.2421 | -9.8499 | -9.8712 | -9.8514 | -9.8871 | -9.8384 | -9.8266 | -9.8463 | 62.2376 | 0.23032 | 62.1368 | -0.019364 | 0.048236 | 61.0122 | 0.016878 | 60.795 | 51.0281 | 51.0068 | 51.0266 | 50.9909 | 51.0396 | 51.0514 | 51.0317 | 123.1156 | 61.1083 | 123.0148 | 60.8586 | 60.9262 | 121.8902 | 60.8949 | 121.673 | 62.1894 | 62.2207 | 62.0885 | 62.1199
8149.0781 | 123.3032 | -60.7636 | 62.3199 | -11.6309 | -11.657 | -11.6279 | -11.659 | -11.6101 | -11.5893 | -11.5585 | 62.3292 | 0.22574 | 62.2329 | -0.023943 | 0.052814 | 60.9115 | 0.016878 | 60.6897 | 49.1327 | 49.1066 | 49.1356 | 49.1046 | 49.1535 | 49.1742 | 49.205 | 123.0927 | 60.9893 | 122.9965 | 60.7396 | 60.8164 | 121.675 | 60.7804 | 121.4532 | 62.2764 | 62.3123 | 62.1801 | 62.216
8150.0625 | 123.23 | -60.8414 | 62.2742 | -11.3241 | -11.3456 | -11.3166 | -11.3293 | -11.2804 | -11.2597 | -11.3067 | 62.3109 | 0.2349 | 62.2192 | -0.033101 | 0.048236 | 60.9252 | 0.007721 | 60.708 | 49.5173 | 49.4958 | 49.5248 | 49.512 | 49.5609 | 49.5817 | 49.5347 | 123.1522 | 61.0763 | 123.0606 | 60.8083 | 60.8896 | 121.7666 | 60.8491 | 121.5494 | 62.2626 | 62.3031 | 62.171 | 62.2115
8151.0938 | 123.3627 | -60.7544 | 62.3199 | -12.3359 | -12.353 | -12.333 | -12.3686 | -12.3151 | -12.2898 | -12.2452 | 62.375 | 0.23032 | 62.2741 | -0.028522 | 0.052814 | 60.8794 | 0.012299 | 60.653 | 48.4185 | 48.4014 | 48.4214 | 48.3858 | 48.4393 | 48.4646 | 48.5092 | 123.1294 | 60.9847 | 123.0285 | 60.7259 | 60.8072 | 121.6338 | 60.7667 | 121.4074 | 62.3222 | 62.3627 | 62.2213 | 62.2618
8152.0625 | 123.3078 | -60.9238 | 62.1689 | -9.3279 | -9.3447 | -9.3386 | -9.3423 | -9.2936 | -9.3551 | -9.3244 | 62.2101 | 0.2349 | 62.1139 | -0.023943 | 0.057392 | 61.0351 | 0.012299 | 60.8316 | 51.5958 | 51.5791 | 51.5852 | 51.5815 | 51.6302 | 51.5687 | 51.5994 | 123.1339 | 61.1587 | 123.0377 | 60.8998 | 60.9812 | 121.9589 | 60.9361 | 121.7554 | 62.1527 | 62.1978 | 62.0565 | 62.1016
8153.0781 | 123.3124 | -60.91 | 62.146 | -9.067 | -9.0928 | -9.0731 | -9.0904 | -9.0418 | -9.0712 | -9.0542 | 62.201 | 0.23032 | 62.1093 | -0.028522 | 0.057392 | 61.058 | 0.012299 | 60.8316 | 51.8431 | 51.8172 | 51.837 | 51.8196 | 51.8682 | 51.8388 | 51.8558 | 123.111 | 61.1404 | 123.0193 | 60.8815 | 60.9674 | 121.968 | 60.9223 | 121.7416 | 62.1436 | 62.1887 | 62.0519 | 62.097
8154.0625 | 123.2712 | -60.9558 | 62.1185 | -8.98 | -9.0058 | -8.9952 | -9.008 | -8.9548 | -9.0025 | -8.9902 | 62.1964 | 0.2349 | 62.1093 | -0.023943 | 0.048236 | 61.0626 | 0.012299 | 60.8407 | 51.9758 | 51.95 | 51.9606 | 51.9478 | 52.001 | 51.9533 | 51.9657 | 123.1522 | 61.1907 | 123.0651 | 60.9319 | 61.004 | 122.0184 | 60.9681 | 121.7966 | 62.1482 | 62.1841 | 62.0611 | 62.097
8155.0938 | 123.2391 | -60.8322 | 62.2604 | -10.9441 | -10.9564 | -10.9411 | -10.9493 | -10.9096 | -10.9209 | -10.8993 | 62.3017 | 0.23948 | 62.2146 | -0.028522 | 0.048236 | 60.9527 | 0.016878 | 60.7355 | 49.8881 | 49.8758 | 49.8911 | 49.8829 | 49.9226 | 49.9114 | 49.933 | 123.1339 | 61.0717 | 123.0468 | 60.8037 | 60.8805 | 121.7849 | 60.8491 | 121.5677 | 62.2535 | 62.2848 | 62.1664 | 62.1977
8156.0625 | 123.2437 | -60.8414 | 62.2421 | -11.1364 | -11.1442 | -11.1426 | -11.1462 | -11.1065 | -11.1086 | -11.0732 | 62.3063 | 0.23032 | 62.2055 | -0.033101 | 0.043657 | 60.939 | 0.007721 | 60.7217 | 49.705 | 49.6972 | 49.6988 | 49.6952 | 49.7349 | 49.7328 | 49.7681 | 123.1477 | 61.0717 | 123.0468 | 60.8083 | 60.885 | 121.7803 | 60.8491 | 121.5631 | 62.2626 | 62.2986 | 62.1618 | 62.1977
8157.0781 | 123.349 | -60.791 | 62.2742 | -11.3287 | -11.3548 | -11.3349 | -11.3659 | -11.3079 | -11.3421 | -11.293 | 62.3246 | 0.23032 | 62.2192 | -0.028522 | 0.057392 | 60.9344 | 0.012299 | 60.708 | 49.4623 | 49.4362 | 49.4561 | 49.4251 | 49.4831 | 49.4489 | 49.498 | 123.1156 | 61.0213 | 123.0102 | 60.7625 | 60.8484 | 121.7254 | 60.8033 | 121.499 | 62.2672 | 62.3123 | 62.1618 | 62.2069
8158.0625 | 123.2391 | -60.7773 | 62.2879 | -11.6446 | -11.657 | -11.6417 | -11.7048 | -11.6513 | -11.6214 | -11.5768 | 62.3383 | 0.23948 | 62.2375 | -0.023943 | 0.048236 | 60.9069 | 0.026035 | 60.6988 | 49.1327 | 49.1203 | 49.1356 | 49.0725 | 49.126 | 49.1559 | 49.2005 | 123.1156 | 61.0168 | 123.0148 | 60.7533 | 60.8255 | 121.6842 | 60.8033 | 121.4761 | 62.2901 | 62.3123 | 62.1893 | 62.2115
8159.0938 | 123.3536 | -60.7864 | 62.2787 | -11.7957 | -11.8218 | -11.7973 | -11.8742 | -11.8206 | -11.7633 | -11.7371 | 62.3429 | 0.23032 | 62.2329 | -0.023943 | 0.048236 | 60.9023 | 0.012299 | 60.6805 | 48.9907 | 48.9646 | 48.9891 | 48.9123 | 48.9658 | 49.0232 | 49.0494 | 123.1294 | 61.0168 | 123.0194 | 60.7625 | 60.8347 | 121.6888 | 60.7987 | 121.467 | 62.2947 | 62.3306 | 62.1847 | 62.2206
8160.0625 | 123.3444 | -60.7681 | 62.2696 | -11.3333 | -11.3548 | -11.344 | -11.4117 | -11.3674 | -11.3329 | -11.2884 | 62.32 | 0.2349 | 62.2192 | -0.028522 | 0.052814 | 60.9344 | 0.007721 | 60.708 | 49.4349 | 49.4133 | 49.4241 | 49.3564 | 49.4007 | 49.4352 | 49.4797 | 123.0881 | 61.003 | 122.9873 | 60.7396 | 60.8209 | 121.7025 | 60.7758 | 121.4761 | 62.2672 | 62.3123 | 62.1664 | 62.2115
8161.1094 | 123.349 | -60.8093 | 62.265 | -11.5576 | -11.57 | -11.5592 | -11.6223 | -11.578 | -11.5618 | -11.5173 | 62.3292 | 0.23032 | 62.2192 | -0.028522 | 0.057392 | 60.9069 | 0.012299 | 60.7034 | 49.2517 | 49.2393 | 49.2501 | 49.187 | 49.2313 | 49.2475 | 49.292 | 123.1385 | 61.0396 | 123.0285 | 60.7808 | 60.8667 | 121.7162 | 60.8216 | 121.5127 | 62.2718 | 62.3169 | 62.1618 | 62.2069
8162.0625 | 123.2483 | -60.8643 | 62.2375 | -9.3875 | -9.3996 | -9.3981 | -9.4888 | -9.4493 | -9.3963 | -9.3701 | 62.2147 | 0.2349 | 62.1185 | -0.023943 | 0.06197 | 61.0305 | 0.012299 | 60.8179 | 51.4768 | 51.4646 | 51.4661 | 51.3755 | 51.415 | 51.468 | 51.4941 | 123.079 | 61.0992 | 122.9827 | 60.8403 | 60.9262 | 121.8948 | 60.8766 | 121.6821 | 62.1527 | 62.2024 | 62.0565 | 62.1062
8163.0938 | 123.349 | -60.8002 | 62.2604 | -11.727 | -11.7394 | -11.7241 | -11.7918 | -11.7474 | -11.7175 | -11.6638 | 62.3475 | 0.23948 | 62.2604 | -0.028522 | 0.048236 | 60.9069 | 0.016878 | 60.6942 | 49.0732 | 49.0608 | 49.0761 | 49.0084 | 49.0528 | 49.0827 | 49.1364 | 123.1477 | 61.0396 | 123.0606 | 60.7716 | 60.8484 | 121.7071 | 60.817 | 121.4944 | 62.2993 | 62.3306 | 62.2122 | 62.2435
8164.0625 | 123.3582 | -60.7681 | 62.3062 | -11.5988 | -11.6203 | -11.5913 | -11.6727 | -11.6284 | -11.5939 | -11.5356 | 62.3475 | 0.2349 | 62.265 | -0.023943 | 0.048236 | 60.9161 | 0.016878 | 60.6988 | 49.1693 | 49.1478 | 49.1768 | 49.0954 | 49.1398 | 49.1742 | 49.2325 | 123.1156 | 61.003 | 123.0331 | 60.7442 | 60.8164 | 121.6842 | 60.785 | 121.467 | 62.2993 | 62.3306 | 62.2167 | 62.2481
8165.0781 | 123.3032 | -60.7773 | 62.2787 | -11.988 | -12.0187 | -11.9942 | -12.071 | -12.0221 | -11.9876 | -11.9385 | 62.3612 | 0.2349 | 62.2558 | -0.028522 | 0.052814 | 60.8932 | 0.003143 | 60.6668 | 48.7893 | 48.7586 | 48.7831 | 48.7062 | 48.7552 | 48.7897 | 48.8388 | 123.1385 | 61.0122 | 123.0331 | 60.7488 | 60.8301 | 121.6705 | 60.7804 | 121.4441 | 62.3084 | 62.3581 | 62.203 | 62.2527
8166.0625 | 123.2803 | -60.9055 | 62.2284 | -9.7583 | -9.7751 | -9.7598 | -9.8825 | -9.8247 | -9.7854 | -9.7547 | 62.233 | 0.2349 | 62.1368 | -0.023943 | 0.052814 | 61.0168 | 0.012299 | 60.795 | 51.1471 | 51.1304 | 51.1456 | 51.0229 | 51.0808 | 51.12 | 51.1507 | 123.1385 | 61.1404 | 123.0422 | 60.8815 | 60.9583 | 121.9222 | 60.9178 | 121.7004 | 62.1802 | 62.2207 | 62.084 | 62.1245
8167.0781 | 123.3536 | -60.7864 | 62.2925 | -12.1345 | -12.1515 | -12.1361 | -12.1809 | -12.1319 | -12.1158 | -12.0713 | 62.3658 | 0.23032 | 62.2558 | -0.028522 | 0.048236 | 60.884 | 0.016878 | 60.6576 | 48.6519 | 48.6349 | 48.6503 | 48.6055 | 48.6545 | 48.6706 | 48.7152 | 123.1522 | 61.0168 | 123.0423 | 60.7579 | 60.8347 | 121.6705 | 60.8033 | 121.4441 | 62.3176 | 62.3489 | 62.2076 | 62.2389
8168.0625 | 123.381 | -60.7864 | 62.2559 | -11.1364 | -11.1304 | -11.1472 | -11.192 | -11.166 | -11.1498 | -11.0778 | 62.3063 | 0.22574 | 62.21 | -0.028522 | 0.048236 | 60.9344 | 0.012299 | 60.7171 | 49.65 | 49.656 | 49.6393 | 49.5945 | 49.6204 | 49.6367 | 49.7086 | 123.0927 | 61.0122 | 122.9965 | 60.7579 | 60.8347 | 121.7208 | 60.7987 | 121.5036 | 62.2581 | 62.294 | 62.1618 | 62.1977
8169.0781 | 123.3353 | -60.8963 | 62.1048 | -9.9781 | -9.9857 | -9.975 | -10.0657 | -10.0261 | -9.964 | -9.9561 | 62.2468 | 0.23948 | 62.1505 | -0.023943 | 0.048236 | 60.9985 | 0.016878 | 60.7812 | 50.9182 | 50.9106 | 50.9213 | 50.8306 | 50.8702 | 50.9323 | 50.9402 | 123.1431 | 61.1358 | 123.0468 | 60.8724 | 60.9445 | 121.8948 | 60.9132 | 121.6775 | 62.1985 | 62.2299 | 62.1023 | 62.1336
8170.0625 | 123.3902 | -60.8826 | 62.1231 | -9.1769 | -9.1936 | -9.1784 | -9.3194 | -9.2753 | -9.1994 | -9.1916 | 62.2101 | 0.2349 | 62.1185 | -0.019364 | 0.043657 | 61.0351 | 0.012299 | 60.8224 | 51.7057 | 51.689 | 51.7042 | 51.5632 | 51.6073 | 51.6832 | 51.691 | 123.0927 | 61.1175 | 123.001 | 60.8632 | 60.9262 | 121.9177 | 60.8949 | 121.705 | 62.1665 | 62.1978 | 62.0748 | 62.1062
8171.1094 | 123.3582 | -60.8505 | 62.1597 | -10.5504 | -10.5672 | -10.5474 | -10.6517 | -10.6075 | -10.5546 | -10.5238 | 62.2788 | 0.23948 | 62.1963 | -0.028522 | 0.048236 | 60.971 | 0.007721 | 60.7446 | 50.3002 | 50.2833 | 50.3032 | 50.1988 | 50.243 | 50.2959 | 50.3267 | 123.1293 | 61.09 | 123.0468 | 60.822 | 60.8988 | 121.8215 | 60.8582 | 121.5951 | 62.2306 | 62.2711 | 62.1481 | 62.1886
8172.0625 | 123.349 | -60.791 | 62.2742 | -11.2142 | -11.2357 | -11.2113 | -11.2973 | -11.253 | -11.2047 | -11.1694 | 62.3063 | 0.23032 | 62.2238 | -0.028522 | 0.052814 | 60.9344 | 0.007721 | 60.7171 | 49.5768 | 49.5553 | 49.5798 | 49.4937 | 49.538 | 49.5863 | 49.6217 | 123.0973 | 61.0213 | 123.0148 | 60.7625 | 60.8438 | 121.7254 | 60.7987 | 121.5082 | 62.2535 | 62.2986 | 62.171 | 62.216
8173.0938 | 123.349 | -60.8414 | 62.1964 | -11.26 | -11.2907 | -11.2662 | -11.3568 | -11.2988 | -11.2642 | -11.2197 | 62.3109 | 0.2349 | 62.2192 | -0.028522 | 0.057392 | 60.9344 | 0.007721 | 60.7126 | 49.5813 | 49.5507 | 49.5752 | 49.4846 | 49.5426 | 49.5771 | 49.6216 | 123.1522 | 61.0763 | 123.0606 | 60.8128 | 60.8988 | 121.7758 | 60.8491 | 121.5539 | 62.2535 | 62.3031 | 62.1618 | 62.2115
8174.0625 | 123.3032 | -60.7727 | 62.265 | -11.8735 | -11.8951 | -11.8752 | -11.9383 | -11.8893 | -11.8686 | -11.8149 | 62.3475 | 0.23032 | 62.2421 | -0.023943 | 0.043657 | 60.8932 | 0.016878 | 60.6805 | 48.8992 | 48.8776 | 48.8975 | 48.8344 | 48.8834 | 48.9041 | 48.9578 | 123.1202 | 61.003 | 123.0148 | 60.7488 | 60.8164 | 121.6659 | 60.7896 | 121.4532 | 62.3038 | 62.3306 | 62.1984 | 62.2252
8175.0781 | 123.2758 | -60.8139 | 62.2742 | -11.5668 | -11.5929 | -11.5638 | -11.6544 | -11.6101 | -11.5756 | -11.5265 | 62.3292 | 0.22574 | 62.2283 | -0.028522 | 0.043657 | 60.9207 | 0.007721 | 60.6942 | 49.2471 | 49.221 | 49.2501 | 49.1595 | 49.2038 | 49.2383 | 49.2874 | 123.1431 | 61.0396 | 123.0423 | 60.7854 | 60.8576 | 121.7346 | 60.8216 | 121.5082 | 62.2855 | 62.3215 | 62.1847 | 62.2206
8176.0625 | 123.2391 | -60.8322 | 62.2467 | -11.4432 | -11.4784 | -11.4402 | -11.5354 | -11.4773 | -11.4428 | -11.3983 | 62.3338 | 0.2349 | 62.2375 | -0.023943 | 0.052814 | 60.9161 | 0.012299 | 60.7034 | 49.3891 | 49.3538 | 49.392 | 49.2969 | 49.3549 | 49.3894 | 49.4339 | 123.166 | 61.0671 | 123.0697 | 60.8083 | 60.885 | 121.7483 | 60.8445 | 121.5356 | 62.2809 | 62.3215 | 62.1847 | 62.2252
8177.0938 | 123.3627 | -60.7544 | 62.2559 | -11.9559 | -11.9683 | -11.9576 | -12.039 | -11.9809 | -11.9327 | -11.8927 | 62.3567 | 0.23032 | 62.2787 | -0.023943 | 0.052814 | 60.8886 | 0.012299 | 60.6714 | 48.7985 | 48.7861 | 48.7968 | 48.7154 | 48.7735 | 48.8217 | 48.8617 | 123.111 | 60.9847 | 123.0331 | 60.7305 | 60.8072 | 121.643 | 60.7667 | 121.4258 | 62.3038 | 62.3444 | 62.2259 | 62.2664
8178.0625 | 123.2941 | -60.7956 | 62.2833 | -11.8094 | -11.831 | -11.8065 | -11.9016 | -11.8435 | -11.7999 | -11.7508 | 62.3567 | 0.23948 | 62.2604 | -0.028522 | 0.043657 | 60.9023 | 0.012299 | 60.6805 | 48.9862 | 48.9646 | 48.9891 | 48.894 | 48.9521 | 48.9957 | 49.0448 | 123.1522 | 61.0351 | 123.056 | 60.7671 | 60.8392 | 121.6979 | 60.8079 | 121.4761 | 62.313 | 62.3444 | 62.2167 | 62.2481
8179.0781 | 123.2941 | -60.7727 | 62.3428 | -12.2581 | -12.2843 | -12.2598 | -12.3457 | -12.2922 | -12.2578 | -12.1903 | 62.375 | 0.2349 | 62.2879 | -0.028522 | 0.039079 | 60.8749 | 0.012299 | 60.6622 | 48.5146 | 48.4884 | 48.5129 | 48.427 | 48.4805 | 48.515 | 48.5824 | 123.1477 | 61.0076 | 123.0606 | 60.7442 | 60.8118 | 121.6476 | 60.785 | 121.4349 | 62.3359 | 62.3627 | 62.2488 | 62.2756
8180.0625 | 123.2391 | -60.7544 | 62.3337 | -12.0521 | -12.0645 | -12.0537 | -12.1397 | -12.0862 | -12.0517 | -11.9843 | 62.3612 | 0.2349 | 62.2604 | -0.023943 | 0.048236 | 60.8886 | 0.016878 | 60.6805 | 48.7023 | 48.6899 | 48.7007 | 48.6147 | 48.6682 | 48.7027 | 48.7701 | 123.1156 | 60.9893 | 123.0148 | 60.7305 | 60.8026 | 121.643 | 60.7713 | 121.4349 | 62.313 | 62.3444 | 62.2122 | 62.2435
8181.1094 | 123.2574 | -60.7727 | 62.2971 | -11.9788 | -12.0004 | -11.985 | -12.0619 | -12.0129 | -11.9739 | -11.9156 | 62.3612 | 0.23032 | 62.2512 | -0.028522 | 0.048236 | 60.8932 | 0.007721 | 60.6576 | 48.7939 | 48.7723 | 48.7877 | 48.7108 | 48.7598 | 48.7988 | 48.8571 | 123.1339 | 61.003 | 123.0239 | 60.7442 | 60.8209 | 121.6659 | 60.7804 | 121.4303 | 62.313 | 62.3535 | 62.203 | 62.2435
8182.0625 | 123.3124 | -60.7452 | 62.2787 | -12.487 | -12.4949 | -12.4841 | -12.5472 | -12.4982 | -12.4684 | -12.4009 | 62.3887 | 0.23032 | 62.2879 | -0.028522 | 0.048236 | 60.8657 | 0.012299 | 60.6347 | 48.2582 | 48.2503 | 48.2611 | 48.198 | 48.2471 | 48.2769 | 48.3443 | 123.1339 | 60.9756 | 123.0331 | 60.7167 | 60.7935 | 121.611 | 60.7575 | 121.38 | 62.3405 | 62.3764 | 62.2396 | 62.2756
8183.0781 | 123.2437 | -60.7773 | 62.3154 | -12.2718 | -12.2934 | -12.2643 | -12.3686 | -12.3105 | -12.2715 | -12.2086 | 62.3795 | 0.24405 | 62.2787 | -0.023943 | 0.043657 | 60.8749 | 0.012299 | 60.653 | 48.5054 | 48.4838 | 48.5129 | 48.4086 | 48.4668 | 48.5058 | 48.5687 | 123.1568 | 61.0213 | 123.056 | 60.7533 | 60.8209 | 121.6522 | 60.7896 | 121.4303 | 62.3359 | 62.3672 | 62.2351 | 62.2664
8184.0625 | 123.3627 | -60.7681 | 62.2467 | -12.162 | -12.1698 | -12.159 | -12.2404 | -12.1869 | -12.1524 | -12.0942 | 62.3704 | 0.23948 | 62.2879 | -0.033101 | 0.048236 | 60.8794 | 0.003143 | 60.6622 | 48.6062 | 48.5983 | 48.6091 | 48.5277 | 48.5812 | 48.6157 | 48.674 | 123.1385 | 61.0076 | 123.056 | 60.735 | 60.8164 | 121.6476 | 60.7713 | 121.4303 | 62.3222 | 62.3672 | 62.2396 | 62.2847
8185.0938 | 123.1888 | -60.7636 | 62.3474 | -12.3634 | -12.3896 | -12.3651 | -12.4648 | -12.402 | -12.3631 | -12.3093 | 62.3979 | 0.24405 | 62.3016 | -0.014785 | 0.048236 | 60.8657 | 0.016878 | 60.6393 | 48.4001 | 48.374 | 48.3985 | 48.2988 | 48.3615 | 48.4005 | 48.4542 | 123.1614 | 61.0076 | 123.0652 | 60.7488 | 60.8118 | 121.6293 | 60.7804 | 121.4029 | 62.3496 | 62.381 | 62.2534 | 62.2847
8186.0625 | 123.3032 | -60.7315 | 62.3062 | -12.0155 | -12.0462 | -12.0125 | -12.1077 | -12.0541 | -12.0014 | -11.9477 | 62.3612 | 0.2349 | 62.2604 | -0.019364 | 0.052814 | 60.884 | 0.012299 | 60.6668 | 48.7161 | 48.6853 | 48.719 | 48.6238 | 48.6774 | 48.7301 | 48.7839 | 123.0927 | 60.9664 | 122.9919 | 60.7121 | 60.7843 | 121.6155 | 60.7438 | 121.3983 | 62.3084 | 62.3489 | 62.2076 | 62.2481
8187.0781 | 123.2758 | -60.7681 | 62.2971 | -11.8094 | -11.8172 | -11.8019 | -11.8833 | -11.8252 | -11.7908 | -11.7416 | 62.3521 | 0.23032 | 62.2467 | -0.014785 | 0.043657 | 60.9023 | 0.016878 | 60.6759 | 48.9587 | 48.9509 | 48.9662 | 48.8848 | 48.9429 | 48.9774 | 49.0265 | 123.1202 | 60.9984 | 123.0148 | 60.7533 | 60.8118 | 121.6705 | 60.785 | 121.4441 | 62.3084 | 62.3352 | 62.203 | 62.2298
8188.0625 | 123.2117 | -60.7819 | 62.3154 | -12.2398 | -12.2614 | -12.2369 | -12.3183 | -12.2693 | -12.2165 | -12.1583 | 62.3795 | 0.22116 | 62.265 | -0.023943 | 0.048236 | 60.8749 | 0.012299 | 60.653 | 48.5421 | 48.5205 | 48.545 | 48.4636 | 48.5126 | 48.5653 | 48.6236 | 123.1614 | 61.003 | 123.0468 | 60.7579 | 60.8301 | 121.6567 | 60.7942 | 121.4349 | 62.3313 | 62.3672 | 62.2167 | 62.2527
8189.0781 | 123.2849 | -60.7544 | 62.3428 | -12.4 | -12.4216 | -12.3971 | -12.4877 | -12.4387 | -12.3859 | -12.3276 | 62.3795 | 0.23948 | 62.2879 | -0.014785 | 0.043657 | 60.8703 | 0.012299 | 60.6485 | 48.3544 | 48.3328 | 48.3573 | 48.2667 | 48.3157 | 48.3684 | 48.4268 | 123.1339 | 60.9939 | 123.0423 | 60.7396 | 60.7981 | 121.6247 | 60.7667 | 121.4029 | 62.3359 | 62.3672 | 62.2442 | 62.2756
8190.0625 | 123.3398 | -60.7315 | 62.3154 | -12.4 | -12.4171 | -12.3971 | -12.4877 | -12.4249 | -12.3951 | -12.3276 | 62.3841 | 0.23948 | 62.3016 | -0.023943 | 0.057392 | 60.8657 | 0.012299 | 60.6393 | 48.3315 | 48.3144 | 48.3344 | 48.2438 | 48.3066 | 48.3364 | 48.4039 | 123.1156 | 60.971 | 123.0331 | 60.7076 | 60.7889 | 121.5972 | 60.7438 | 121.3708 | 62.3267 | 62.3718 | 62.2442 | 62.2893
8191.1094 | 123.2071 | -60.9375 | 62.1918 | -9.5798 | -9.5965 | -9.5859 | -9.7223 | -9.669 | -9.6069 | -9.5716 | 62.2239 | 0.2349 | 62.123 | -0.019364 | 0.052814 | 61.0122 | 0.012299 | 60.7995 | 51.3577 | 51.341 | 51.3516 | 51.2152 | 51.2685 | 51.3306 | 51.3659 | 123.1614 | 61.1724 | 123.0605 | 60.9181 | 60.9903 | 121.9497 | 60.9498 | 121.737 | 62.1711 | 62.2116 | 62.0702 | 62.1107
8192.0625 | 123.2574 | -60.8276 | 62.2787 | -11.4935 | -11.5059 | -11.4951 | -11.5903 | -11.546 | -11.4657 | -11.4074 | 62.3292 | 0.24405 | 62.2467 | -0.019364 | 0.039079 | 60.9069 | 0.007721 | 60.6942 | 49.3341 | 49.3218 | 49.3325 | 49.2373 | 49.2817 | 49.3619 | 49.4202 | 123.1568 | 61.0717 | 123.0743 | 60.8083 | 60.8667 | 121.7346 | 60.8354 | 121.5219 | 62.2901 | 62.3215 | 62.2076 | 62.2389
8193.0781 | 123.2803 | -60.878 | 62.1918 | -9.9872 | -10.0361 | -9.9842 | -10.0794 | -10.0124 | -10.0189 | -10.0065 | 62.2559 | 0.23948 | 62.1551 | -0.023943 | 0.052814 | 61.0031 | 0.016878 | 60.7858 | 50.8908 | 50.8419 | 50.8938 | 50.7986 | 50.8656 | 50.8591 | 50.8715 | 123.1339 | 61.1175 | 123.0331 | 60.854 | 60.9308 | 121.881 | 60.8949 | 121.6638 | 62.2031 | 62.239 | 62.1023 | 62.1382
8194.0625 | 123.2208 | -60.8322 | 62.2833 | -11.0403 | -11.0388 | -11.0419 | -11.0729 | -11.0332 | -11.0307 | -10.9954 | 62.2971 | 0.23948 | 62.1963 | -0.028522 | 0.048236 | 60.9435 | 0.003143 | 60.7217 | 49.792 | 49.7934 | 49.7904 | 49.7593 | 49.799 | 49.8015 | 49.8368 | 123.1293 | 61.0717 | 123.0285 | 60.8037 | 60.8805 | 121.7758 | 60.8354 | 121.5539 | 62.2489 | 62.294 | 62.1481 | 62.1932
8195.0938 | 123.2895 | -60.878 | 62.2238 | -9.2776 | -9.2897 | -9.2837 | -9.3285 | -9.2799 | -9.291 | -9.2603 | 62.2147 | 0.2349 | 62.123 | -0.014785 | 0.048236 | 61.0351 | 0.016878 | 60.8224 | 51.6004 | 51.5883 | 51.5943 | 51.5495 | 51.5981 | 51.587 | 51.6177 | 123.0927 | 61.1129 | 123.001 | 60.8632 | 60.9262 | 121.9131 | 60.8949 | 121.7004 | 62.1665 | 62.1978 | 62.0748 | 62.1062
8196.0625 | 123.3078 | -60.8368 | 62.2101 | -11.0036 | -11.0114 | -11.0052 | -11.0409 | -10.992 | -11.0033 | -10.9954 | 62.3109 | 0.23948 | 62.2238 | -0.028522 | 0.043657 | 60.9481 | 0.012299 | 60.7263 | 49.8332 | 49.8254 | 49.8316 | 49.7959 | 49.8448 | 49.8335 | 49.8414 | 123.1477 | 61.0763 | 123.0606 | 60.8083 | 60.8804 | 121.7849 | 60.8491 | 121.5631 | 62.2672 | 62.2986 | 62.1801 | 62.2115
8197.0938 | 123.2758 | -60.7727 | 62.3154 | -11.5118 | -11.5242 | -11.518 | -11.604 | -11.5551 | -11.5023 | -11.4441 | 62.3383 | 0.23948 | 62.2421 | -0.023943 | 0.052814 | 60.9161 | 0.021456 | 60.7034 | 49.2609 | 49.2485 | 49.2547 | 49.1687 | 49.2176 | 49.2704 | 49.3286 | 123.111 | 61.0122 | 123.0148 | 60.7488 | 60.8255 | 121.6888 | 60.7942 | 121.4761 | 62.2855 | 62.3169 | 62.1893 | 62.2206
8198.0625 | 123.262 | -60.8276 | 62.2559 | -11.8827 | -11.8951 | -11.8797 | -11.9154 | -11.8573 | -11.8823 | -11.8286 | 62.3521 | 0.24405 | 62.2741 | -0.033101 | 0.048236 | 60.8932 | 0.016878 | 60.6759 | 48.945 | 48.9326 | 48.9479 | 48.9123 | 48.9704 | 48.9453 | 48.999 | 123.1797 | 61.0717 | 123.1018 | 60.7945 | 60.8759 | 121.7208 | 60.8445 | 121.5036 | 62.3038 | 62.3352 | 62.2259 | 62.2573
8199.0781 | 123.2758 | -60.7498 | 62.3474 | -12.107 | -12.1194 | -12.1132 | -12.1306 | -12.0862 | -12.1021 | -12.0438 | 62.375 | 0.2349 | 62.2879 | -0.019364 | 0.052814 | 60.884 | 0.016878 | 60.6622 | 48.6428 | 48.6304 | 48.6366 | 48.6193 | 48.6636 | 48.6477 | 48.706 | 123.1248 | 60.9847 | 123.0377 | 60.7305 | 60.8026 | 121.6338 | 60.7667 | 121.412 | 62.3222 | 62.3581 | 62.2351 | 62.271
8200.0625 | 123.1979 | -60.7819 | 62.3245 | -12.1116 | -12.1286 | -12.1132 | -12.1351 | -12.0816 | -12.1021 | -12.1125 | 62.3658 | 0.24405 | 62.2787 | -0.019364 | 0.043657 | 60.8886 | 0.016878 | 60.6714 | 48.6703 | 48.6533 | 48.6686 | 48.6467 | 48.7003 | 48.6798 | 48.6694 | 123.1477 | 61.0259 | 123.0606 | 60.7625 | 60.8255 | 121.6705 | 60.7987 | 121.4532 | 62.3221 | 62.3489 | 62.2351 | 62.2618
8201.1094 | 123.262 | -60.7498 | 62.3154 | -12.0017 | -12.0324 | -11.9988 | -12.0253 | -11.9671 | -11.9876 | -11.9522 | 62.3658 | 0.23948 | 62.2604 | -0.028522 | 0.048236 | 60.8932 | 0.007721 | 60.6759 | 48.7481 | 48.7174 | 48.751 | 48.7246 | 48.7827 | 48.7622 | 48.7976 | 123.1156 | 60.9893 | 123.0102 | 60.7213 | 60.7981 | 121.643 | 60.7575 | 121.4258 | 62.3176 | 62.3581 | 62.2122 | 62.2527
8202.0625 | 123.2025 | -60.8139 | 62.2375 | -11.9285 | -11.9363 | -11.9255 | -11.9474 | -11.9031 | -11.9098 | -11.879 | 62.3521 | 0.23032 | 62.2512 | -0.033101 | 0.048236 | 60.8932 | 0.007721 | 60.6714 | 48.8854 | 48.8776 | 48.8884 | 48.8665 | 48.9109 | 48.9041 | 48.9349 | 123.166 | 61.0442 | 123.0651 | 60.7808 | 60.8621 | 121.7071 | 60.8216 | 121.4853 | 62.3038 | 62.3444 | 62.203 | 62.2435
8203.0938 | 123.2529 | -60.7544 | 62.3245 | -11.3104 | -11.2953 | -11.3211 | -11.3339 | -11.2988 | -11.3054 | -11.2564 | 62.3154 | 0.2349 | 62.2192 | -0.023943 | 0.048236 | 60.9298 | 0.012299 | 60.7126 | 49.444 | 49.4591 | 49.4332 | 49.4205 | 49.4556 | 49.4489 | 49.498 | 123.0698 | 60.9893 | 122.9736 | 60.7305 | 60.8026 | 121.6842 | 60.7667 | 121.467 | 62.2672 | 62.3031 | 62.171 | 62.2069
8204.0625 | 123.23 | -60.8139 | 62.3108 | -11.8689 | -11.8539 | -11.8797 | -11.8742 | -11.8527 | -11.8503 | -11.8195 | 62.3521 | 0.23032 | 62.2512 | -0.028522 | 0.043657 | 60.8978 | 0.007721 | 60.6714 | 48.945 | 48.96 | 48.9342 | 48.9397 | 48.9612 | 48.9636 | 48.9944 | 123.166 | 61.0442 | 123.0651 | 60.7854 | 60.8576 | 121.7117 | 60.8216 | 121.4853 | 62.3084 | 62.3444 | 62.2076 | 62.2435
8205.0938 | 123.2162 | -60.8093 | 62.3291 | -11.9285 | -11.9317 | -11.9255 | -11.9566 | -11.8939 | -11.9098 | -11.8607 | 62.3567 | 0.23032 | 62.2696 | -0.023943 | 0.043657 | 60.9023 | 0.016878 | 60.6714 | 48.8809 | 48.8776 | 48.8838 | 48.8528 | 48.9154 | 48.8995 | 48.9487 | 123.166 | 61.0396 | 123.0789 | 60.7854 | 60.853 | 121.7117 | 60.8262 | 121.4807 | 62.313 | 62.3398 | 62.2259 | 62.2527
8206.0625 | 123.3856 | -60.7956 | 62.2513 | -11.5164 | -11.5334 | -11.5134 | -11.5537 | -11.5093 | -11.5115 | -11.4669 | 62.3338 | 0.23948 | 62.2421 | -0.023943 | 0.057392 | 60.9161 | 0.012299 | 60.7034 | 49.2792 | 49.2622 | 49.2821 | 49.2419 | 49.2862 | 49.2841 | 49.3286 | 123.1294 | 61.0351 | 123.0377 | 60.7716 | 60.853 | 121.7117 | 60.8079 | 121.499 | 62.2764 | 62.3215 | 62.1847 | 62.2298
8207.0625 | 123.262 | -60.8322 | 62.2971 | -11.6492 | -11.6661 | -11.6417 | -11.691 | -11.6284 | -11.6488 | -11.5951 | 62.3475 | 0.2349 | 62.2558 | -0.028522 | 0.039079 | 60.9069 | 0.012299 | 60.6851 | 49.183 | 49.1661 | 49.1906 | 49.1412 | 49.2038 | 49.1834 | 49.2371 | 123.1797 | 61.0671 | 123.088 | 60.8037 | 60.8713 | 121.7391 | 60.8445 | 121.5173 | 62.3084 | 62.3352 | 62.2167 | 62.2435
8208.0938 | 123.2712 | -60.8093 | 62.2925 | -11.7453 | -11.776 | -11.747 | -11.7918 | -11.7337 | -11.7404 | -11.7462 | 62.3429 | 0.23032 | 62.2421 | -0.023943 | 0.048236 | 60.9069 | 0.012299 | 60.6942 | 49.064 | 49.0333 | 49.0624 | 49.0176 | 49.0757 | 49.0689 | 49.0631 | 123.1522 | 61.0396 | 123.0514 | 60.7854 | 60.8576 | 121.7162 | 60.8216 | 121.5036 | 62.2947 | 62.3306 | 62.1938 | 62.2298
8209.0625 | 123.2162 | -60.7956 | 62.2879 | -12.0612 | -12.0828 | -12.0675 | -12.1031 | -12.045 | -12.0471 | -11.998 | 62.3612 | 0.23032 | 62.2604 | -0.028522 | 0.057392 | 60.8932 | 0.012299 | 60.6668 | 48.7344 | 48.7128 | 48.7281 | 48.6925 | 48.7506 | 48.7484 | 48.7976 | 123.1568 | 61.0259 | 123.056 | 60.7671 | 60.853 | 121.6888 | 60.8079 | 121.4624 | 62.3038 | 62.3489 | 62.203 | 62.2481
8210.0781 | 123.2529 | -60.759 | 62.352 | -12.0155 | -12.0324 | -12.0125 | -12.039 | -11.9946 | -11.9922 | -11.9797 | 62.3658 | 0.2349 | 62.2741 | -0.019364 | 0.048236 | 60.8886 | 0.007721 | 60.6622 | 48.7435 | 48.7265 | 48.7465 | 48.72 | 48.7644 | 48.7668 | 48.7793 | 123.1248 | 60.9939 | 123.0331 | 60.7396 | 60.8072 | 121.6476 | 60.7667 | 121.4212 | 62.3176 | 62.3581 | 62.2259 | 62.2664
8211.0625 | 123.317 | -60.759 | 62.2787 | -12.2077 | -12.2293 | -12.214 | -12.245 | -12.1915 | -12.1891 | -12.1766 | 62.3704 | 0.23032 | 62.265 | -0.028522 | 0.043657 | 60.884 | 0.012299 | 60.6622 | 48.5512 | 48.5296 | 48.545 | 48.514 | 48.5675 | 48.5699 | 48.5824 | 123.1294 | 60.9893 | 123.0239 | 60.7304 | 60.8026 | 121.643 | 60.7713 | 121.4212 | 62.3267 | 62.3581 | 62.2213 | 62.2527
8212.0938 | 123.2574 | -60.7681 | 62.3154 | -12.0017 | -12.0187 | -11.9942 | -12.0253 | -11.9763 | -11.9785 | -11.9705 | 62.3612 | 0.2349 | 62.2558 | -0.028522 | 0.052814 | 60.884 | 0.012299 | 60.6759 | 48.7664 | 48.7494 | 48.7739 | 48.7429 | 48.7918 | 48.7897 | 48.7976 | 123.1294 | 61.003 | 123.0239 | 60.7396 | 60.8209 | 121.6522 | 60.7804 | 121.4441 | 62.3084 | 62.3489 | 62.203 | 62.2435
8213.0625 | 123.2391 | -60.7773 | 62.3199 | -12.2535 | -12.2705 | -12.2552 | -12.2816 | -12.2327 | -12.2349 | -12.2452 | 62.3704 | 0.2349 | 62.2833 | -0.033101 | 0.052814 | 60.8749 | 0.012299 | 60.653 | 48.5238 | 48.5067 | 48.5221 | 48.4956 | 48.5446 | 48.5424 | 48.532 | 123.1477 | 61.0122 | 123.0606 | 60.7442 | 60.8301 | 121.6522 | 60.7896 | 121.4303 | 62.3176 | 62.3581 | 62.2305 | 62.271
8214.0781 | 123.3353 | -60.7407 | 62.2696 | -12.2627 | -12.2751 | -12.2598 | -12.2862 | -12.2418 | -12.2349 | -12.1857 | 62.375 | 0.23948 | 62.265 | -0.019364 | 0.048236 | 60.8703 | 0.007721 | 60.6576 | 48.478 | 48.4655 | 48.4809 | 48.4544 | 48.4988 | 48.5058 | 48.5549 | 123.1156 | 60.9801 | 123.0056 | 60.7213 | 60.7889 | 121.611 | 60.7484 | 121.3983 | 62.3267 | 62.3672 | 62.2167 | 62.2573
8215.0625 | 123.2437 | -60.9741 | 62.1277 | -9.7034 | -9.7614 | -9.6774 | -9.7909 | -9.7011 | -9.703 | -9.741 | 62.2193 | 0.2349 | 62.1322 | -0.023943 | 0.048236 | 61.0122 | 0.007721 | 60.7904 | 51.2708 | 51.2128 | 51.2967 | 51.1832 | 51.2731 | 51.2711 | 51.2331 | 123.1934 | 61.209 | 123.1063 | 60.9502 | 61.0224 | 121.9863 | 60.9818 | 121.7645 | 62.1711 | 62.2116 | 62.084 | 62.1245
8216.1094 | 123.2712 | -60.8505 | 62.2696 | -11.5851 | -11.6158 | -11.5867 | -11.6223 | -11.5643 | -11.5664 | -11.5356 | 62.3338 | 0.2349 | 62.2375 | -0.023943 | 0.048236 | 60.9161 | 0.012299 | 60.6942 | 49.2654 | 49.2348 | 49.2638 | 49.2282 | 49.2862 | 49.2841 | 49.3149 | 123.1843 | 61.0854 | 123.088 | 60.8266 | 60.8988 | 121.7666 | 60.8628 | 121.5448 | 62.2855 | 62.3215 | 62.1893 | 62.2252
8217.0625 | 123.3398 | -60.7361 | 62.2971 | -12.0933 | -12.1194 | -12.0904 | -12.1306 | -12.077 | -12.0792 | -12.0301 | 62.3704 | 0.2349 | 62.2741 | -0.033101 | 0.052814 | 60.8932 | 0.016878 | 60.6576 | 48.6428 | 48.6166 | 48.6457 | 48.6055 | 48.6591 | 48.6569 | 48.706 | 123.1065 | 60.971 | 123.0102 | 60.703 | 60.7889 | 121.6293 | 60.753 | 121.3937 | 62.3176 | 62.3535 | 62.2213 | 62.2573
8218.0781 | 123.2986 | -60.7452 | 62.3337 | -12.4184 | -12.4354 | -12.42 | -12.4419 | -12.3929 | -12.4043 | -12.3505 | 62.375 | 0.2349 | 62.2787 | -0.028522 | 0.052814 | 60.8657 | 0.012299 | 60.653 | 48.3269 | 48.3099 | 48.3252 | 48.3033 | 48.3523 | 48.341 | 48.3947 | 123.1202 | 60.9801 | 123.0239 | 60.7167 | 60.7981 | 121.611 | 60.7575 | 121.3983 | 62.3222 | 62.3627 | 62.2259 | 62.2664
8219.0625 | 123.3536 | -60.7681 | 62.2696 | -12.0612 | -12.0828 | -12.0491 | -12.0802 | -12.0175 | -12.0288 | -12.0163 | 62.3658 | 0.2349 | 62.2696 | -0.019364 | 0.048236 | 60.8932 | 0.021456 | 60.6576 | 48.7069 | 48.6853 | 48.719 | 48.6879 | 48.7506 | 48.7393 | 48.7518 | 123.1339 | 61.003 | 123.0377 | 60.7488 | 60.8164 | 121.6613 | 60.7896 | 121.4257 | 62.3176 | 62.3444 | 62.2213 | 62.2481
8220.0938 | 123.2529 | -60.7956 | 62.3291 | -11.4981 | -11.5196 | -11.4997 | -11.5308 | -11.4681 | -11.4977 | -11.4578 | 62.3383 | 0.2349 | 62.2283 | -0.023943 | 0.048236 | 60.9161 | 0.003143 | 60.6988 | 49.2975 | 49.276 | 49.2959 | 49.2648 | 49.3274 | 49.2979 | 49.3378 | 123.1339 | 61.0305 | 123.0239 | 60.7716 | 60.8438 | 121.7117 | 60.7987 | 121.4944 | 62.2901 | 62.3352 | 62.1801 | 62.2252
8221.0625 | 123.3582 | -60.7727 | 62.2604 | -11.5164 | -11.5288 | -11.5134 | -11.517 | -11.4727 | -11.5023 | -11.4669 | 62.3338 | 0.2349 | 62.2329 | -0.019364 | 0.052814 | 60.9207 | 0.016878 | 60.7034 | 49.2563 | 49.2439 | 49.2593 | 49.2557 | 49.3 | 49.2704 | 49.3058 | 123.1065 | 61.0076 | 123.0056 | 60.7533 | 60.8255 | 121.6934 | 60.7896 | 121.4761 | 62.2809 | 62.3169 | 62.1801 | 62.216
8222.0781 | 123.2712 | -60.8002 | 62.3108 | -11.8003 | -11.8264 | -11.8065 | -11.8467 | -11.7886 | -11.7999 | -11.7645 | 62.3429 | 0.23948 | 62.2558 | -0.019364 | 0.048236 | 60.8978 | 0.007721 | 60.6805 | 48.9999 | 48.9738 | 48.9937 | 48.9535 | 49.0116 | 49.0003 | 49.0356 | 123.1431 | 61.0396 | 123.056 | 60.7808 | 60.8484 | 121.6979 | 60.8079 | 121.4807 | 62.2947 | 62.3352 | 62.2076 | 62.2481
8223.0625 | 123.262 | -60.7727 | 62.3154 | -12.0155 | -12.0279 | -12.0034 | -12.0161 | -11.9717 | -12.0059 | -11.9614 | 62.3521 | 0.22574 | 62.2512 | -0.019364 | 0.043657 | 60.884 | 0.012299 | 60.6668 | 48.7572 | 48.7448 | 48.7693 | 48.7566 | 48.801 | 48.7668 | 48.8113 | 123.1248 | 60.9984 | 123.0239 | 60.7533 | 60.8164 | 121.6567 | 60.785 | 121.4395 | 62.3084 | 62.3398 | 62.2076 | 62.2389
8224.0781 | 123.2529 | -60.8276 | 62.265 | -11.4935 | -11.5288 | -11.486 | -11.517 | -11.4636 | -11.4886 | -11.4853 | 62.3292 | 0.24405 | 62.2512 | -0.023943 | 0.052814 | 60.9161 | 0.012299 | 60.7034 | 49.3341 | 49.2989 | 49.3417 | 49.3106 | 49.3641 | 49.3391 | 49.3424 | 123.1568 | 61.0717 | 123.0789 | 60.8037 | 60.8805 | 121.7437 | 60.8399 | 121.531 | 62.2764 | 62.3169 | 62.1984 | 62.2389
8225.0625 | 123.2986 | -60.8139 | 62.1826 | -11.2509 | -11.2815 | -11.257 | -11.279 | -11.2209 | -11.2551 | -11.2335 | 62.3154 | 0.23032 | 62.21 | -0.019364 | 0.043657 | 60.9344 | 0.012299 | 60.7034 | 49.563 | 49.5324 | 49.5569 | 49.5349 | 49.593 | 49.5588 | 49.5804 | 123.1293 | 61.0442 | 123.0239 | 60.7945 | 60.8576 | 121.7483 | 60.8262 | 121.5173 | 62.2718 | 62.3031 | 62.1664 | 62.1977
8226.1094 | 123.3261 | -60.8185 | 62.2467 | -11.0174 | -11.0434 | -11.0281 | -11.0271 | -10.9875 | -11.0124 | -10.9954 | 62.3017 | 0.23032 | 62.1963 | -0.028522 | 0.039079 | 60.9435 | 0.016878 | 60.7217 | 49.8011 | 49.7751 | 49.7904 | 49.7913 | 49.831 | 49.8061 | 49.8231 | 123.1202 | 61.0488 | 123.0148 | 60.79 | 60.8576 | 121.762 | 60.8354 | 121.5402 | 62.2626 | 62.2848 | 62.1572 | 62.1794
8227.0625 | 123.3673 | -60.8276 | 62.1964 | -10.6465 | -10.6725 | -10.6572 | -10.6746 | -10.6166 | -10.6462 | -10.6154 | 62.2834 | 0.23948 | 62.2009 | -0.033101 | 0.043657 | 60.9619 | 0.007721 | 60.74 | 50.1811 | 50.1551 | 50.1704 | 50.153 | 50.211 | 50.1815 | 50.2122 | 123.111 | 61.0671 | 123.0285 | 60.7945 | 60.8713 | 121.7895 | 60.8354 | 121.5677 | 62.2397 | 62.2757 | 62.1572 | 62.1932
8228.0781 | 123.2391 | -60.8505 | 62.2147 | -8.719 | -8.6991 | -8.7388 | -8.7058 | -8.6939 | -8.737 | -8.72 | 62.1735 | 0.23032 | 62.0681 | -0.019364 | 0.052814 | 61.0717 | 0.016878 | 60.8545 | 52.1315 | 52.1515 | 52.1117 | 52.1447 | 52.1566 | 52.1136 | 52.1305 | 123.024 | 61.0808 | 122.9186 | 60.8312 | 60.9033 | 121.9223 | 60.8674 | 121.705 | 62.1207 | 62.1566 | 62.0153 | 62.0512
8229.0625 | 123.2712 | -60.8322 | 62.2513 | -10.9212 | -10.9381 | -10.9137 | -10.931 | -10.8822 | -10.9117 | -10.8947 | 62.2971 | 0.2349 | 62.1963 | -0.023943 | 0.052814 | 60.9481 | 0.007721 | 60.7217 | 49.911 | 49.8941 | 49.9186 | 49.9012 | 49.95 | 49.9205 | 49.9375 | 123.1293 | 61.0671 | 123.0285 | 60.8083 | 60.885 | 121.7803 | 60.8399 | 121.5539 | 62.2443 | 62.2894 | 62.1435 | 62.1886
8230.0781 | 123.2712 | -60.878 | 62.2147 | -10.7976 | -10.8145 | -10.7946 | -10.8028 | -10.7494 | -10.7881 | -10.7573 | 62.2971 | 0.2349 | 62.2009 | -0.023943 | 0.052814 | 60.9619 | 0.016878 | 60.7355 | 50.0804 | 50.0635 | 50.0834 | 50.0752 | 50.1286 | 50.0899 | 50.1207 | 123.1751 | 61.1129 | 123.0789 | 60.854 | 60.9308 | 121.8398 | 60.8949 | 121.6134 | 62.2443 | 62.2803 | 62.1481 | 62.184
8231.0625 | 123.2895 | -60.8551 | 62.2009 | -10.8617 | -10.874 | -10.8587 | -10.8623 | -10.8089 | -10.8568 | -10.8168 | 62.2834 | 0.23032 | 62.1871 | -0.033101 | 0.048236 | 60.9527 | 0.012299 | 60.7309 | 49.9934 | 49.9811 | 49.9964 | 49.9928 | 50.0462 | 49.9983 | 50.0383 | 123.1385 | 61.0854 | 123.0422 | 60.822 | 60.9033 | 121.8078 | 60.8674 | 121.586 | 62.2352 | 62.2711 | 62.1389 | 62.1748
8232.0781 | 123.2895 | -60.8459 | 62.233 | -10.5275 | -10.5489 | -10.529 | -10.5327 | -10.4793 | -10.5225 | -10.5238 | 62.2742 | 0.23948 | 62.178 | -0.023943 | 0.052814 | 60.9664 | 0.007721 | 60.7538 | 50.3185 | 50.297 | 50.3169 | 50.3133 | 50.3666 | 50.3234 | 50.3221 | 123.1202 | 61.0854 | 123.0239 | 60.822 | 60.8988 | 121.8124 | 60.8537 | 121.5997 | 62.2214 | 62.2665 | 62.1252 | 62.1703
8233.0625 | 123.3353 | -60.8322 | 62.2238 | -10.8113 | -10.8145 | -10.7992 | -10.7982 | -10.7448 | -10.7881 | -10.7299 | 62.2834 | 0.22574 | 62.1917 | -0.028522 | 0.048236 | 60.9527 | 0.007721 | 60.7355 | 50.0209 | 50.0177 | 50.033 | 50.034 | 50.0874 | 50.0441 | 50.1024 | 123.1156 | 61.058 | 123.0239 | 60.8037 | 60.8805 | 121.7849 | 60.8399 | 121.5677 | 62.2352 | 62.2757 | 62.1435 | 62.184
8234.0781 | 123.262 | -60.8047 | 62.2604 | -11.1685 | -11.1854 | -11.1701 | -11.1645 | -11.1202 | -11.1544 | -11.0961 | 62.3154 | 0.24405 | 62.2192 | -0.028522 | 0.048236 | 60.9298 | 0.016878 | 60.7263 | 49.6363 | 49.6194 | 49.6347 | 49.6403 | 49.6845 | 49.6504 | 49.7086 | 123.1202 | 61.0488 | 123.0239 | 60.7762 | 60.853 | 121.7346 | 60.8216 | 121.531 | 62.2672 | 62.2986 | 62.171 | 62.2023
8235.0625 | 123.3261 | -60.8185 | 62.1643 | -10.9945 | -11.0205 | -10.9961 | -11.0088 | -10.9463 | -10.985 | -10.9496 | 62.3109 | 0.2349 | 62.2146 | -0.033101 | 0.048236 | 60.9481 | 0.012299 | 60.7217 | 49.824 | 49.798 | 49.8224 | 49.8097 | 49.8722 | 49.8335 | 49.8689 | 123.1293 | 61.0534 | 123.0331 | 60.7854 | 60.8667 | 121.7666 | 60.8308 | 121.5402 | 62.2626 | 62.2986 | 62.1664 | 62.2023
8236.1094 | 123.3078 | -60.8414 | 62.2375 | -10.8709 | -10.8923 | -10.877 | -10.876 | -10.8272 | -10.8613 | -10.8489 | 62.2926 | 0.23032 | 62.1917 | -0.033101 | 0.052814 | 60.9481 | 0.012299 | 60.7355 | 49.9705 | 49.9491 | 49.9643 | 49.9653 | 50.0141 | 49.98 | 49.9925 | 123.1339 | 61.0717 | 123.0331 | 60.8083 | 60.8942 | 121.7895 | 60.8537 | 121.5768 | 62.2397 | 62.2803 | 62.1389 | 62.1794
8237.0625 | 123.2666 | -60.8688 | 62.2559 | -10.8663 | -10.8832 | -10.8679 | -10.8669 | -10.8135 | -10.8613 | -10.8077 | 62.288 | 0.2349 | 62.1871 | -0.023943 | 0.043657 | 60.9573 | 0.003143 | 60.7217 | 50.0026 | 49.9857 | 50.001 | 50.0019 | 50.0553 | 50.0075 | 50.0611 | 123.1568 | 61.1037 | 123.056 | 60.8449 | 60.9125 | 121.8261 | 60.872 | 121.5906 | 62.2443 | 62.2848 | 62.1435 | 62.184
8238.0781 | 123.2529 | -60.8139 | 62.2696 | -11.5897 | -11.5975 | -11.5821 | -11.5857 | -11.5322 | -11.5527 | -11.4853 | 62.3338 | 0.23948 | 62.2375 | -0.028522 | 0.052814 | 60.9207 | 0.021456 | 60.6988 | 49.2242 | 49.2164 | 49.2318 | 49.2282 | 49.2817 | 49.2612 | 49.3286 | 123.1477 | 61.0534 | 123.0514 | 60.7854 | 60.8667 | 121.7346 | 60.8354 | 121.5127 | 62.2809 | 62.3123 | 62.1847 | 62.216
8239.0625 | 123.317 | -61.0016 | 62.0728 | -8.2749 | -8.3099 | -8.2718 | -8.2984 | -8.2453 | -8.2746 | -8.3263 | 62.146 | 0.2349 | 62.0452 | -0.028522 | 0.048236 | 61.0946 | 0.012299 | 60.8774 | 52.7267 | 52.6917 | 52.7298 | 52.7032 | 52.7563 | 52.727 | 52.6753 | 123.1476 | 61.2365 | 123.0468 | 60.9731 | 61.0498 | 122.0962 | 61.0139 | 121.879 | 62.0978 | 62.1337 | 61.997 | 62.0329
8240.0781 | 123.2758 | -60.9741 | 62.0865 | -8.4718 | -8.4793 | -8.4778 | -8.4952 | -8.4513 | -8.4852 | -8.4408 | 62.1644 | 0.23948 | 62.0681 | -0.028522 | 0.048236 | 61.0855 | 0.016878 | 60.8682 | 52.5023 | 52.4948 | 52.4963 | 52.4789 | 52.5229 | 52.489 | 52.5333 | 123.1385 | 61.2136 | 123.0422 | 60.9456 | 61.0224 | 122.0596 | 60.991 | 121.8423 | 62.1161 | 62.1475 | 62.0199 | 62.0512
8241.0625 | 123.2529 | -60.9787 | 62.1597 | -8.5771 | -8.5983 | -8.5786 | -8.596 | -8.5383 | -8.5813 | -8.569 | 62.1735 | 0.2349 | 62.0773 | -0.019364 | 0.052814 | 61.0763 | 0.016878 | 60.8591 | 52.4016 | 52.3804 | 52.4001 | 52.3827 | 52.4404 | 52.3974 | 52.4097 | 123.1522 | 61.2136 | 123.056 | 60.9593 | 61.0315 | 122.055 | 60.9956 | 121.8378 | 62.1207 | 62.1566 | 62.0245 | 62.0604
8242.0781 | 123.2162 | -60.9283 | 62.1689 | -8.98 | -9.0013 | -8.9815 | -8.9989 | -8.9411 | -8.9796 | -8.9535 | 62.1918 | 0.2349 | 62.1002 | -0.028522 | 0.048236 | 61.058 | 0.012299 | 60.8407 | 51.9484 | 51.9271 | 51.9469 | 51.9295 | 51.9872 | 51.9487 | 51.9748 | 123.1202 | 61.1632 | 123.0285 | 60.8998 | 60.9766 | 121.9863 | 60.9406 | 121.7691 | 62.1436 | 62.1795 | 62.0519 | 62.0879
8243.0625 | 123.2162 | -60.9833 | 62.1368 | -8.8472 | -8.8776 | -8.8487 | -8.8707 | -8.8129 | -8.8285 | -8.9032 | 62.1827 | 0.23948 | 62.0956 | -0.019364 | 0.052814 | 61.0672 | 0.016878 | 60.8362 | 52.1361 | 52.1056 | 52.1346 | 52.1126 | 52.1703 | 52.1547 | 52.0801 | 123.1659 | 61.2228 | 123.0789 | 60.9639 | 61.0361 | 122.0504 | 61.0002 | 121.8194 | 62.1299 | 62.1658 | 62.0428 | 62.0787
8244.0781 | 123.2483 | -60.9695 | 62.146 | -8.3253 | -8.3511 | -8.3313 | -8.3396 | -8.291 | -8.3387 | -8.3538 | 62.1598 | 0.24405 | 62.0635 | -0.019364 | 0.048236 | 61.0946 | 0.012299 | 60.882 | 52.6443 | 52.6185 | 52.6382 | 52.63 | 52.6785 | 52.6309 | 52.6158 | 123.1293 | 61.2136 | 123.0331 | 60.9502 | 61.0178 | 122.0642 | 60.9818 | 121.8515 | 62.1115 | 62.1475 | 62.0153 | 62.0512
8245.0625 | 123.2071 | -60.997 | 62.114 | -8.394 | -8.4289 | -8.4046 | -8.4174 | -8.3597 | -8.3661 | -8.4087 | 62.1644 | 0.23948 | 62.0635 | -0.023943 | 0.043657 | 61.0946 | 0.012299 | 60.8636 | 52.6031 | 52.5681 | 52.5924 | 52.5796 | 52.6373 | 52.6309 | 52.5883 | 123.1614 | 61.2365 | 123.0605 | 60.9731 | 61.0407 | 122.0916 | 61.0093 | 121.8606 | 62.1207 | 62.1521 | 62.0199 | 62.0512
8246.125 | 123.3078 | -60.8963 | 62.1597 | -9.772 | -9.8026 | -9.7736 | -9.7818 | -9.7285 | -9.758 | -9.7181 | 62.2239 | 0.23032 | 62.1414 | -0.033101 | 0.052814 | 61.0122 | 0.012299 | 60.7904 | 51.1243 | 51.0937 | 51.1227 | 51.1145 | 51.1678 | 51.1384 | 51.1782 | 123.1202 | 61.1266 | 123.0377 | 60.8632 | 60.9491 | 121.9085 | 60.9086 | 121.6867 | 62.1711 | 62.2116 | 62.0885 | 62.1291
8247.0625 | 123.1979 | -60.8734 | 62.2055 | -10.2116 | -10.233 | -10.2223 | -10.2167 | -10.168 | -10.1929 | -10.1439 | 62.2605 | 0.24405 | 62.1643 | -0.023943 | 0.052814 | 60.9939 | 0.016878 | 60.7629 | 50.6618 | 50.6404 | 50.6511 | 50.6567 | 50.7054 | 50.6805 | 50.7296 | 123.1339 | 61.1175 | 123.0377 | 60.8495 | 60.9262 | 121.8673 | 60.8903 | 121.6363 | 62.2077 | 62.2436 | 62.1114 | 62.1474
8248.0938 | 123.2483 | -60.8551 | 62.2833 | -10.8571 | -10.8832 | -10.8679 | -10.8577 | -10.7998 | -10.8385 | -10.7756 | 62.288 | 0.2349 | 62.21 | -0.023943 | 0.048236 | 60.9573 | 0.012299 | 60.7309 | 49.998 | 49.9719 | 49.9872 | 49.9974 | 50.0553 | 50.0167 | 50.0795 | 123.1431 | 61.09 | 123.0651 | 60.8312 | 60.9033 | 121.8124 | 60.8674 | 121.586 | 62.2397 | 62.2757 | 62.1618 | 62.1977
8249.0625 | 123.23 | -60.9146 | 62.2238 | -10.4771 | -10.494 | -10.4741 | -10.5143 | -10.461 | -10.4584 | -10.414 | 62.2742 | 0.2349 | 62.178 | -0.023943 | 0.052814 | 60.971 | 0.012299 | 60.7492 | 50.4375 | 50.4207 | 50.4405 | 50.4003 | 50.4536 | 50.4562 | 50.5006 | 123.1888 | 61.1495 | 123.0926 | 60.8907 | 60.9674 | 121.8856 | 60.9269 | 121.6638 | 62.2214 | 62.2619 | 62.1252 | 62.1657
8250.0938 | 123.2483 | -60.8551 | 62.2559 | -10.1841 | -10.2055 | -10.1857 | -10.1939 | -10.136 | -10.1792 | -10.1393 | 62.2559 | 0.2349 | 62.1597 | -0.019364 | 0.048236 | 60.9939 | 0.012299 | 60.7721 | 50.671 | 50.6496 | 50.6694 | 50.6612 | 50.7191 | 50.6759 | 50.7158 | 123.111 | 61.09 | 123.0148 | 60.8357 | 60.9033 | 121.849 | 60.8674 | 121.6272 | 62.2077 | 62.2436 | 62.1114 | 62.1474
8251.0625 | 123.2437 | -60.8551 | 62.2421 | -10.7015 | -10.7183 | -10.703 | -10.6975 | -10.6441 | -10.6874 | -10.6246 | 62.2834 | 0.2349 | 62.1871 | -0.023943 | 0.052814 | 60.9619 | 0.016878 | 60.74 | 50.1536 | 50.1368 | 50.1521 | 50.1576 | 50.211 | 50.1677 | 50.2305 | 123.1385 | 61.09 | 123.0422 | 60.8312 | 60.9079 | 121.817 | 60.872 | 121.5951 | 62.2306 | 62.2665 | 62.1343 | 62.1703
8252.0781 | 123.23 | -60.8322 | 62.2559 | -10.8113 | -10.8328 | -10.8175 | -10.8074 | -10.7723 | -10.8018 | -10.7436 | 62.2926 | 0.23032 | 62.1826 | -0.023943 | 0.048236 | 60.9573 | 0.012299 | 60.74 | 50.0209 | 49.9994 | 50.0147 | 50.0248 | 50.0599 | 50.0304 | 50.0886 | 123.1248 | 61.0625 | 123.0148 | 60.8083 | 60.8805 | 121.7895 | 60.8445 | 121.5722 | 62.2443 | 62.2803 | 62.1343 | 62.1703
8253.0625 | 123.2849 | -60.8688 | 62.2284 | -10.6557 | -10.6725 | -10.6481 | -10.6517 | -10.5983 | -10.6141 | -10.5559 | 62.2788 | 0.22574 | 62.178 | -0.023943 | 0.052814 | 60.9619 | 0.012299 | 60.7492 | 50.2132 | 50.1963 | 50.2207 | 50.2171 | 50.2705 | 50.2547 | 50.3129 | 123.1477 | 61.0946 | 123.0468 | 60.8449 | 60.9216 | 121.8307 | 60.8811 | 121.618 | 62.226 | 62.2665 | 62.1252 | 62.1657
8254.0938 | 123.2758 | -60.91 | 62.1735 | -9.0716 | -9.1203 | -9.0639 | -9.0996 | -9.0235 | -9.0437 | -9.068 | 62.1872 | 0.2349 | 62.1002 | -0.019364 | 0.043657 | 61.0488 | 0.012299 | 60.8362 | 51.8385 | 51.7897 | 51.8461 | 51.8104 | 51.8865 | 51.8663 | 51.8421 | 123.0973 | 61.1449 | 123.0102 | 60.8907 | 60.9537 | 121.9589 | 60.9223 | 121.7462 | 62.1436 | 62.1749 | 62.0565 | 62.0879
8255.0625 | 123.2529 | -60.9329 | 62.1506 | -9.0075 | -9.0196 | -9.009 | -9.0034 | -8.9594 | -8.9705 | -9.0497 | 62.1964 | 0.23948 | 62.0864 | -0.028522 | 0.052814 | 61.058 | 0.012299 | 60.8362 | 51.9255 | 51.9133 | 51.924 | 51.9295 | 51.9735 | 51.9625 | 51.8833 | 123.1293 | 61.1724 | 123.0193 | 60.9044 | 60.9857 | 121.9909 | 60.9452 | 121.7691 | 62.1436 | 62.1841 | 62.0336 | 62.0741
8256.1094 | 123.2529 | -60.8917 | 62.2421 | -9.9323 | -9.9537 | -9.9338 | -9.9466 | -9.8842 | -9.8678 | -9.947 | 62.2468 | 0.23948 | 62.1551 | -0.023943 | 0.052814 | 61.0076 | 0.016878 | 60.7904 | 50.9594 | 50.9381 | 50.9579 | 50.9451 | 51.0076 | 51.0239 | 50.9447 | 123.1385 | 61.1312 | 123.0468 | 60.8678 | 60.9445 | 121.8994 | 60.9086 | 121.6821 | 62.194 | 62.2299 | 62.1023 | 62.1382
8257.0625 | 123.2849 | -60.91 | 62.2284 | -10.3352 | -10.3612 | -10.3413 | -10.3495 | -10.2962 | -10.3074 | -10.2675 | 62.2651 | 0.2349 | 62.1734 | -0.023943 | 0.043657 | 60.9802 | 0.016878 | 60.7583 | 50.5748 | 50.5489 | 50.5687 | 50.5605 | 50.6138 | 50.6027 | 50.6426 | 123.1751 | 61.1449 | 123.0834 | 60.8861 | 60.9537 | 121.8902 | 60.9269 | 121.6684 | 62.2214 | 62.2482 | 62.1298 | 62.1565
8258.0781 | 123.3307 | -60.8597 | 62.2009 | -10.0651 | -10.091 | -10.0666 | -10.0885 | -10.0307 | -10.0464 | -10.0248 | 62.2605 | 0.2349 | 62.1597 | -0.023943 | 0.048236 | 60.9985 | 0.016878 | 60.7767 | 50.7946 | 50.7687 | 50.7931 | 50.7711 | 50.829 | 50.8133 | 50.8349 | 123.1202 | 61.0946 | 123.0194 | 60.8357 | 60.9079 | 121.8582 | 60.8766 | 121.6363 | 62.2123 | 62.2436 | 62.1114 | 62.1428
8259.0625 | 123.2758 | -60.9192 | 62.1689 | -9.1631 | -9.189 | -9.1692 | -9.1591 | -9.1151 | -9.1536 | -9.1412 | 62.1964 | 0.23032 | 62.1139 | -0.023943 | 0.052814 | 61.0351 | 0.012299 | 60.827 | 51.7561 | 51.7302 | 51.75 | 51.7601 | 51.8041 | 51.7656 | 51.778 | 123.1156 | 61.1495 | 123.0331 | 60.8952 | 60.972 | 121.9543 | 60.9315 | 121.7462 | 62.1436 | 62.1841 | 62.0611 | 62.1016
8260.0781 | 123.3307 | -60.91 | 62.1597 | -8.7968 | -8.8273 | -8.8121 | -8.8295 | -8.7717 | -8.7965 | -8.7979 | 62.1781 | 0.2349 | 62.0727 | -0.023943 | 0.048236 | 61.0672 | 0.003143 | 60.8545 | 52.1132 | 52.0828 | 52.098 | 52.0806 | 52.1383 | 52.1135 | 52.1122 | 123.0881 | 61.1449 | 122.9827 | 60.8861 | 60.9583 | 121.9772 | 60.9132 | 121.7645 | 62.1299 | 62.1749 | 62.0244 | 62.0695
8261.0625 | 123.2162 | -60.9695 | 62.1414 | -8.9937 | -9.0104 | -8.9998 | -9.0034 | -8.9503 | -8.975 | -9.0222 | 62.1781 | 0.23032 | 62.0773 | -0.023943 | 0.043657 | 61.058 | 0.016878 | 60.8316 | 51.9758 | 51.9591 | 51.9697 | 51.9661 | 52.0193 | 51.9945 | 51.9473 | 123.1476 | 61.1999 | 123.0468 | 60.9456 | 61.0132 | 122.0275 | 60.9864 | 121.8011 | 62.1344 | 62.1612 | 62.0336 | 62.0604
8262.0781 | 123.3444 | -60.8597 | 62.1597 | -9.4149 | -9.4225 | -9.4073 | -9.4109 | -9.3714 | -9.3642 | -9.3747 | 62.2101 | 0.2349 | 62.1093 | -0.033101 | 0.057392 | 61.0259 | 0.012299 | 60.8179 | 51.4447 | 51.4372 | 51.4524 | 51.4487 | 51.4882 | 51.4955 | 51.485 | 123.0698 | 61.0946 | 122.969 | 60.8266 | 60.9171 | 121.8856 | 60.872 | 121.6775 | 62.1527 | 62.1978 | 62.0519 | 62.097
8263.0625 | 123.2574 | -60.8871 | 62.2055 | -9.4973 | -9.5324 | -9.4989 | -9.5071 | -9.4538 | -9.4878 | -9.4709 | 62.2147 | 0.2349 | 62.1139 | -0.033101 | 0.043657 | 61.0259 | 0.016878 | 60.8133 | 51.3898 | 51.3547 | 51.3883 | 51.3801 | 51.4333 | 51.3993 | 51.4163 | 123.1019 | 61.122 | 123.001 | 60.854 | 60.9308 | 121.9131 | 60.904 | 121.7004 | 62.1711 | 62.1978 | 62.0702 | 62.097
8264.0938 | 123.349 | -60.9238 | 62.146 | -9.0532 | -9.0608 | -9.0593 | -9.0538 | -9.0189 | -9.0391 | -9.0176 | 62.201 | 0.2349 | 62.1002 | -0.023943 | 0.048236 | 61.0534 | 0.026035 | 60.827 | 51.8705 | 51.863 | 51.8644 | 51.87 | 51.9048 | 51.8846 | 51.9061 | 123.1247 | 61.1587 | 123.0239 | 60.8998 | 60.972 | 121.9772 | 60.9498 | 121.7508 | 62.1527 | 62.1749 | 62.0519 | 62.0741
8265.0625 | 123.2574 | -60.9375 | 62.178 | -9.1219 | -9.1341 | -9.1326 | -9.1225 | -9.0739 | -9.1032 | -9.0955 | 62.201 | 0.24405 | 62.1139 | -0.028522 | 0.052814 | 61.0534 | 0.012299 | 60.8316 | 51.8156 | 51.8034 | 51.8049 | 51.815 | 51.8636 | 51.8343 | 51.842 | 123.1385 | 61.1816 | 123.0514 | 60.909 | 60.9903 | 121.9909 | 60.9498 | 121.7691 | 62.1482 | 62.1887 | 62.0611 | 62.1016
8266.1094 | 123.3582 | -60.8047 | 62.2284 | -10.5137 | -10.5214 | -10.5107 | -10.5143 | -10.4747 | -10.4768 | -10.5147 | 62.2697 | 0.23032 | 62.1643 | -0.019364 | 0.052814 | 60.971 | 0.012299 | 60.7492 | 50.291 | 50.2833 | 50.294 | 50.2904 | 50.33 | 50.328 | 50.2901 | 123.0744 | 61.0351 | 122.969 | 60.7854 | 60.8576 | 121.7758 | 60.817 | 121.5539 | 62.2168 | 62.2574 | 62.1114 | 62.152
8267.0625 | 123.2758 | -60.8734 | 62.2742 | -10.6786 | -10.7092 | -10.6801 | -10.6975 | -10.6441 | -10.6324 | -10.6795 | 62.2788 | 0.2349 | 62.1826 | -0.019364 | 0.043657 | 60.9619 | 0.016878 | 60.7492 | 50.1948 | 50.1642 | 50.1933 | 50.1759 | 50.2293 | 50.241 | 50.1939 | 123.1522 | 61.1083 | 123.056 | 60.854 | 60.9171 | 121.8353 | 60.8903 | 121.6226 | 62.2352 | 62.2619 | 62.1389 | 62.1657
8268.0938 | 123.2254 | -60.9238 | 62.2192 | -9.8133 | -9.8575 | -9.8102 | -9.8413 | -9.7743 | -9.7946 | -9.7868 | 62.2376 | 0.2349 | 62.1414 | -0.019364 | 0.052814 | 61.0076 | 0.012299 | 60.795 | 51.1105 | 51.0663 | 51.1136 | 51.0825 | 51.1495 | 51.1292 | 51.137 | 123.1614 | 61.1587 | 123.0651 | 60.9044 | 60.9766 | 121.9314 | 60.9361 | 121.7187 | 62.1848 | 62.2253 | 62.0885 | 62.1291
8269.0625 | 123.262 | -60.8917 | 62.2147 | -9.8178 | -9.8529 | -9.8148 | -9.8322 | -9.7743 | -9.7946 | -9.7684 | 62.2376 | 0.2349 | 62.1551 | -0.019364 | 0.052814 | 61.0076 | 0.012299 | 60.795 | 51.0739 | 51.0388 | 51.0769 | 51.0596 | 51.1174 | 51.0971 | 51.1233 | 123.1293 | 61.1266 | 123.0468 | 60.8724 | 60.9445 | 121.8994 | 60.904 | 121.6867 | 62.1848 | 62.2253 | 62.1023 | 62.1428
8270.0938 | 123.3948 | -60.9055 | 62.1506 | -9.6713 | -9.6881 | -9.6729 | -9.6765 | -9.6278 | -9.6572 | -9.6403 | 62.2239 | 0.23032 | 62.123 | -0.023943 | 0.052814 | 61.0168 | 0.016878 | 60.8041 | 51.2341 | 51.2174 | 51.2326 | 51.229 | 51.2777 | 51.2482 | 51.2652 | 123.1293 | 61.1358 | 123.0285 | 60.8815 | 60.9583 | 121.9222 | 60.9223 | 121.7096 | 62.1711 | 62.207 | 62.0702 | 62.1062
8271.0625 | 123.2391 | -60.8963 | 62.2192 | -10.0055 | -10.0223 | -10.0162 | -10.0153 | -9.9712 | -10.0006 | -9.9699 | 62.2376 | 0.23032 | 62.1459 | -0.033101 | 0.048236 | 60.9985 | 0.007721 | 60.7812 | 50.8908 | 50.874 | 50.8801 | 50.881 | 50.9251 | 50.8957 | 50.9264 | 123.1339 | 61.1266 | 123.0422 | 60.8632 | 60.9445 | 121.8948 | 60.904 | 121.6775 | 62.1894 | 62.2299 | 62.0977 | 62.1382
8272.0625 | 123.2162 | -60.8688 | 62.2284 | -9.9506 | -9.9674 | -9.9521 | -9.9741 | -9.9254 | -9.9365 | -9.9424 | 62.2422 | 0.2349 | 62.1459 | -0.028522 | 0.048236 | 61.0076 | 0.012299 | 60.7858 | 50.9182 | 50.9014 | 50.9167 | 50.8947 | 50.9435 | 50.9323 | 50.9264 | 123.111 | 61.1037 | 123.0148 | 60.8403 | 60.9171 | 121.8765 | 60.8811 | 121.6546 | 62.194 | 62.2299 | 62.0977 | 62.1336
8273.0625 | 123.2758 | -60.8643 | 62.2147 | -10.0376 | -10.0544 | -10.0346 | -10.0382 | -9.994 | -9.996 | -10.0614 | 62.2468 | 0.23948 | 62.1551 | -0.019364 | 0.048236 | 60.9939 | 0.021456 | 60.7767 | 50.8267 | 50.8099 | 50.8297 | 50.8261 | 50.8702 | 50.8682 | 50.8028 | 123.111 | 61.1037 | 123.0194 | 60.8449 | 60.9125 | 121.8582 | 60.8857 | 121.6409 | 62.1985 | 62.2253 | 62.1069 | 62.1336
8274.0625 | 123.2666 | -60.8459 | 62.2925 | -11.0906 | -11.0938 | -11.0922 | -11.0958 | -11.047 | -11.0445 | -10.9862 | 62.3063 | 0.24863 | 62.21 | -0.028522 | 0.048236 | 60.9344 | 0.012299 | 60.7171 | 49.7553 | 49.7522 | 49.7537 | 49.7501 | 49.799 | 49.8015 | 49.8597 | 123.1522 | 61.0946 | 123.056 | 60.8174 | 60.8942 | 121.7803 | 60.8582 | 121.5631 | 62.2581 | 62.294 | 62.1618 | 62.1977
8275.0938 | 123.3673 | -60.7864 | 62.233 | -10.8022 | -10.8191 | -10.8038 | -10.8074 | -10.7494 | -10.7423 | -10.7299 | 62.288 | 0.23032 | 62.1917 | -0.028522 | 0.057392 | 60.9573 | 0.012299 | 60.74 | 49.9843 | 49.9674 | 49.9827 | 49.9791 | 50.037 | 50.0441 | 50.0566 | 123.0744 | 61.0168 | 122.9782 | 60.7579 | 60.8438 | 121.7437 | 60.7987 | 121.5265 | 62.2306 | 62.2757 | 62.1343 | 62.1794
8276.0625 | 123.2437 | -60.9009 | 62.2055 | -10.4451 | -10.4802 | -10.4375 | -10.4594 | -10.3969 | -10.3943 | -10.3865 | 62.2742 | 0.2349 | 62.1688 | -0.033101 | 0.052814 | 60.9756 | 0.016878 | 60.7583 | 50.4558 | 50.4207 | 50.4634 | 50.4415 | 50.504 | 50.5065 | 50.5144 | 123.1751 | 61.1358 | 123.0697 | 60.8678 | 60.9537 | 121.8765 | 60.9178 | 121.6592 | 62.2214 | 62.2574 | 62.116 | 62.152
8277.0781 | 123.381 | -60.8505 | 62.1918 | -10.239 | -10.2604 | -10.2498 | -10.258 | -10.2092 | -10.2204 | -10.1896 | 62.2559 | 0.24405 | 62.1734 | -0.023943 | 0.039079 | 60.9847 | 0.012299 | 60.7675 | 50.6115 | 50.5901 | 50.6008 | 50.5926 | 50.6413 | 50.6302 | 50.6609 | 123.1064 | 61.0946 | 123.0239 | 60.8266 | 60.8896 | 121.8353 | 60.8628 | 121.618 | 62.2168 | 62.2436 | 62.1343 | 62.1611
8278.0625 | 123.2162 | -60.9146 | 62.2147 | -9.7308 | -9.7614 | -9.7278 | -9.7314 | -9.6827 | -9.6893 | -9.7547 | 62.2285 | 0.23032 | 62.1368 | -0.028522 | 0.043657 | 61.0168 | 0.012299 | 60.8041 | 51.1838 | 51.1533 | 51.1868 | 51.1832 | 51.2319 | 51.2253 | 51.1599 | 123.1431 | 61.1449 | 123.0514 | 60.8861 | 60.9583 | 121.9314 | 60.9269 | 121.7187 | 62.1848 | 62.2162 | 62.0931 | 62.1245
8279.0938 | 123.2529 | -60.8963 | 62.233 | -9.8224 | -9.8392 | -9.8285 | -9.855 | -9.8018 | -9.7763 | -9.8188 | 62.2376 | 0.23032 | 62.1322 | -0.014785 | 0.052814 | 61.0122 | 0.012299 | 60.795 | 51.0739 | 51.0571 | 51.0678 | 51.0413 | 51.0945 | 51.12 | 51.0775 | 123.1339 | 61.1266 | 123.0285 | 60.8815 | 60.9491 | 121.9085 | 60.9086 | 121.6913 | 62.1848 | 62.2253 | 62.0794 | 62.1199
8280.0625 | 123.2666 | -60.9329 | 62.1826 | -9.4882 | -9.5049 | -9.4897 | -9.5208 | -9.4813 | -9.4054 | -9.5075 | 62.2193 | 0.23948 | 62.1322 | -0.019364 | 0.052814 | 61.0259 | 0.012299 | 60.8133 | 51.4447 | 51.428 | 51.4432 | 51.4121 | 51.4516 | 51.5275 | 51.4254 | 123.1522 | 61.1724 | 123.0651 | 60.9136 | 60.9857 | 121.9589 | 60.9452 | 121.7462 | 62.1665 | 62.207 | 62.0794 | 62.1199
8281.0938 | 123.3261 | -60.8505 | 62.2147 | -9.7446 | -9.7659 | -9.737 | -9.7497 | -9.6919 | -9.6664 | -9.6631 | 62.2239 | 0.2349 | 62.1322 | -0.023943 | 0.052814 | 61.0214 | 0.021456 | 60.795 | 51.1059 | 51.0846 | 51.1136 | 51.1008 | 51.1586 | 51.1841 | 51.1874 | 123.0744 | 61.0854 | 122.9827 | 60.8266 | 60.9033 | 121.8719 | 60.872 | 121.6455 | 62.1711 | 62.2024 | 62.0794 | 62.1107
8282.0625 | 123.3765 | -60.9238 | 62.1094 | -9.6393 | -9.6789 | -9.6316 | -9.6582 | -9.6003 | -9.5977 | -9.5991 | 62.2101 | 0.23032 | 62.1185 | -0.023943 | 0.052814 | 61.0214 | 0.012299 | 60.8041 | 51.2845 | 51.2448 | 51.2921 | 51.2656 | 51.3234 | 51.3261 | 51.3247 | 123.1339 | 61.1541 | 123.0422 | 60.8998 | 60.9766 | 121.9451 | 60.9361 | 121.7279 | 62.1573 | 62.1978 | 62.0657 | 62.1062
8283.0781 | 123.349 | -60.8643 | 62.1872 | -10.0284 | -10.059 | -10.03 | -10.0382 | -9.9803 | -10.0098 | -9.9882 | 62.2376 | 0.23948 | 62.1459 | -0.028522 | 0.048236 | 61.0031 | 0.012299 | 60.7812 | 50.8358 | 50.8053 | 50.8343 | 50.8261 | 50.8839 | 50.8545 | 50.8761 | 123.1019 | 61.1037 | 123.0102 | 60.8357 | 60.9125 | 121.8673 | 60.8766 | 121.6455 | 62.1894 | 62.2253 | 62.0977 | 62.1336
8284.0625 | 123.1796 | -60.8231 | 62.233 | -10.2665 | -10.2696 | -10.2681 | -10.2534 | -10.2092 | -10.2158 | -10.2034 | 62.2605 | 0.23948 | 62.1688 | -0.019364 | 0.048236 | 60.9893 | 0.012299 | 60.7675 | 50.5565 | 50.5535 | 50.555 | 50.5697 | 50.6139 | 50.6073 | 50.6197 | 123.0836 | 61.0625 | 122.9919 | 60.8037 | 60.8713 | 121.8124 | 60.8354 | 121.5906 | 62.2123 | 62.2482 | 62.1206 | 62.1565
8285.0781 | 123.3627 | -60.7819 | 62.233 | -10.8251 | -10.8374 | -10.8267 | -10.812 | -10.7677 | -10.7881 | -10.7253 | 62.2834 | 0.2349 | 62.1871 | -0.023943 | 0.048236 | 60.9481 | 0.016878 | 60.7355 | 49.9568 | 49.9445 | 49.9552 | 49.9699 | 50.0141 | 49.9938 | 50.0566 | 123.0653 | 61.0168 | 122.969 | 60.7579 | 60.8301 | 121.73 | 60.7987 | 121.5173 | 62.2352 | 62.2665 | 62.1389 | 62.1703
8286.0625 | 123.2391 | -60.8368 | 62.2513 | -10.9533 | -10.9747 | -10.9549 | -10.9585 | -10.8913 | -10.9071 | -10.9267 | 62.2971 | 0.2349 | 62.1963 | -0.023943 | 0.043657 | 60.9481 | 0.016878 | 60.7263 | 49.8835 | 49.8621 | 49.8819 | 49.8783 | 49.9455 | 49.9297 | 49.9101 | 123.1339 | 61.0717 | 123.0331 | 60.8128 | 60.8804 | 121.7849 | 60.8537 | 121.5631 | 62.2535 | 62.2803 | 62.1526 | 62.1794
8287.0938 | 123.2529 | -60.8963 | 62.2284 | -10.2116 | -10.233 | -10.204 | -10.2167 | -10.1634 | -10.1654 | -10.1988 | 62.2651 | 0.24405 | 62.1734 | -0.019364 | 0.057392 | 60.9893 | 0.012299 | 60.7675 | 50.6847 | 50.6633 | 50.6923 | 50.6796 | 50.7329 | 50.7309 | 50.6975 | 123.1614 | 61.1404 | 123.0697 | 60.8769 | 60.9537 | 121.8856 | 60.9086 | 121.6638 | 62.2077 | 62.2528 | 62.116 | 62.1611
8288.0625 | 123.2803 | -60.8871 | 62.2101 | -9.6622 | -9.6927 | -9.6637 | -9.6673 | -9.6049 | -9.5886 | -9.654 | 62.2147 | 0.2349 | 62.1276 | -0.023943 | 0.052814 | 61.0168 | 0.012299 | 60.8041 | 51.225 | 51.1945 | 51.2235 | 51.2198 | 51.2822 | 51.2986 | 51.2332 | 123.1019 | 61.122 | 123.0148 | 60.8632 | 60.94 | 121.9039 | 60.8994 | 121.6913 | 62.1619 | 62.2024 | 62.0748 | 62.1153
8289.0938 | 123.3398 | -60.8414 | 62.2101 | -9.9735 | -9.9857 | -9.9796 | -9.9695 | -9.93 | -9.877 | -9.9378 | 62.2422 | 0.23948 | 62.1459 | -0.023943 | 0.057392 | 61.0076 | 0.012299 | 60.7767 | 50.8679 | 50.8557 | 50.8618 | 50.8719 | 50.9114 | 50.9644 | 50.9035 | 123.0836 | 61.0808 | 122.9873 | 60.8174 | 60.8988 | 121.849 | 60.8537 | 121.618 | 62.1848 | 62.2299 | 62.0885 | 62.1336
8290.0625 | 123.2712 | -60.8459 | 62.2238 | -10.468 | -10.4848 | -10.4741 | -10.464 | -10.4198 | -10.3669 | -10.4185 | 62.2788 | 0.24405 | 62.1826 | -0.023943 | 0.057392 | 60.9756 | 0.016878 | 60.7538 | 50.378 | 50.3611 | 50.3718 | 50.382 | 50.4262 | 50.4791 | 50.4274 | 123.1248 | 61.09 | 123.0285 | 60.822 | 60.9033 | 121.8215 | 60.8628 | 121.5997 | 62.2214 | 62.2619 | 62.1252 | 62.1657
8291.1094 | 123.2437 | -60.8322 | 62.2833 | -9.9048 | -9.9399 | -9.9064 | -9.9146 | -9.8521 | -9.8495 | -9.9012 | 62.2376 | 0.2349 | 62.1322 | -0.028522 | 0.052814 | 61.0031 | 0.007721 | 60.7858 | 50.9274 | 50.8923 | 50.9259 | 50.9176 | 50.9801 | 50.9827 | 50.931 | 123.0698 | 61.0671 | 122.9644 | 60.8037 | 60.885 | 121.8353 | 60.8399 | 121.618 | 62.1848 | 62.2299 | 62.0794 | 62.1245
8292.0625 | 123.317 | -60.8551 | 62.1689 | -10.2345 | -10.2513 | -10.2314 | -10.2351 | -10.1817 | -10.1151 | -10.1713 | 62.2559 | 0.23032 | 62.1459 | -0.028522 | 0.052814 | 60.9847 | 0.012299 | 60.7629 | 50.6206 | 50.6038 | 50.6237 | 50.62 | 50.6734 | 50.74 | 50.6838 | 123.111 | 61.0854 | 123.001 | 60.8266 | 60.9079 | 121.8398 | 60.8674 | 121.618 | 62.2031 | 62.2436 | 62.0931 | 62.1336
8293.0781 | 123.3765 | -60.8505 | 62.2009 | -10.7289 | -10.755 | -10.7214 | -10.7479 | -10.6807 | -10.605 | -10.6658 | 62.2926 | 0.23948 | 62.1963 | -0.023943 | 0.057392 | 60.9527 | 0.012299 | 60.7446 | 50.1216 | 50.0956 | 50.1292 | 50.1027 | 50.1698 | 50.2456 | 50.1848 | 123.1431 | 61.09 | 123.0468 | 60.8266 | 60.9079 | 121.8032 | 60.8628 | 121.5951 | 62.2352 | 62.2803 | 62.1389 | 62.184
8294.0625 | 123.2849 | -60.8276 | 62.2833 | -10.8938 | -10.8923 | -10.8953 | -10.8852 | -10.8455 | -10.811 | -10.8306 | 62.2971 | 0.23948 | 62.2009 | -0.028522 | 0.057392 | 60.9573 | 0.016878 | 60.7355 | 49.9339 | 49.9353 | 49.9323 | 49.9424 | 49.9821 | 50.0167 | 49.9971 | 123.1248 | 61.0671 | 123.0285 | 60.7991 | 60.885 | 121.7849 | 60.8445 | 121.5631 | 62.2397 | 62.2803 | 62.1435 | 62.184
8295.0625 | 123.2941 | -60.8734 | 62.2284 | -10.12 | -10.1414 | -10.1216 | -10.1298 | -10.081 | -10.0418 | -10.0981 | 62.2513 | 0.23032 | 62.1459 | -0.023943 | 0.043657 | 60.9893 | 0.016878 | 60.7767 | 50.7534 | 50.732 | 50.7519 | 50.7437 | 50.7924 | 50.8316 | 50.7753 | 123.1248 | 61.1037 | 123.0194 | 60.8495 | 60.9171 | 121.8627 | 60.8903 | 121.6501 | 62.2077 | 62.2345 | 62.1023 | 62.1291
8296.1094 | 123.2208 | -60.8826 | 62.233 | -10.3306 | -10.3474 | -10.3322 | -10.3358 | -10.2916 | -10.2341 | -10.327 | 62.2605 | 0.24863 | 62.1643 | -0.019364 | 0.052814 | 60.9802 | 0.021456 | 60.7629 | 50.552 | 50.5351 | 50.5504 | 50.5468 | 50.591 | 50.6485 | 50.5556 | 123.1431 | 61.1312 | 123.0468 | 60.8632 | 60.9354 | 121.8627 | 60.904 | 121.6455 | 62.2077 | 62.239 | 62.1114 | 62.1428
8297.0625 | 123.2529 | -60.8643 | 62.2101 | -10.3718 | -10.3886 | -10.378 | -10.3678 | -10.3145 | -10.2662 | -10.359 | 62.2651 | 0.23948 | 62.178 | -0.023943 | 0.057392 | 60.9847 | 0.021456 | 60.7538 | 50.4924 | 50.4756 | 50.4863 | 50.4964 | 50.5498 | 50.5981 | 50.5052 | 123.1293 | 61.1037 | 123.0422 | 60.8403 | 60.9216 | 121.849 | 60.8857 | 121.618 | 62.2077 | 62.2436 | 62.1206 | 62.1565
8298.0781 | 123.3948 | -60.8871 | 62.1643 | -10.3077 | -10.3291 | -10.291 | -10.3221 | -10.2596 | -10.2066 | -10.2858 | 62.2605 | 0.23948 | 62.1551 | -0.014785 | 0.048236 | 60.9847 | 0.021456 | 60.7629 | 50.5794 | 50.558 | 50.5962 | 50.5651 | 50.6276 | 50.6805 | 50.6014 | 123.1476 | 61.1266 | 123.0422 | 60.8724 | 60.9354 | 121.8719 | 60.9086 | 121.6501 | 62.2123 | 62.239 | 62.1069 | 62.1336
8299.0625 | 123.2346 | -60.8459 | 62.2421 | -10.5275 | -10.5489 | -10.5245 | -10.5372 | -10.4885 | -10.4264 | -10.4872 | 62.2788 | 0.23948 | 62.1734 | -0.023943 | 0.057392 | 60.9756 | 0.021456 | 60.7583 | 50.3185 | 50.297 | 50.3215 | 50.3087 | 50.3575 | 50.4196 | 50.3587 | 123.1248 | 61.0854 | 123.0194 | 60.822 | 60.9033 | 121.8215 | 60.8674 | 121.6043 | 62.2214 | 62.2574 | 62.116 | 62.152
8300.0625 | 123.2803 | -60.878 | 62.2513 | -10.3947 | -10.4299 | -10.4054 | -10.4136 | -10.3603 | -10.3074 | -10.3545 | 62.2788 | 0.23948 | 62.178 | -0.019364 | 0.048236 | 60.9802 | 0.012299 | 60.7492 | 50.4833 | 50.4481 | 50.4726 | 50.4644 | 50.5177 | 50.5706 | 50.5235 | 123.1568 | 61.1175 | 123.056 | 60.8586 | 60.9262 | 121.8582 | 60.8903 | 121.6272 | 62.2306 | 62.2665 | 62.1298 | 62.1657
8301.0938 | 123.3444 | -60.7819 | 62.3016 | -11.2371 | -11.2495 | -11.2342 | -11.2423 | -11.1752 | -11.1498 | -11.1739 | 62.3063 | 0.2349 | 62.21 | -0.023943 | 0.048236 | 60.9252 | 0.016878 | 60.7171 | 49.5447 | 49.5324 | 49.5477 | 49.5395 | 49.6067 | 49.6321 | 49.6079 | 123.0881 | 61.0168 | 122.9919 | 60.7579 | 60.8301 | 121.7071 | 60.7987 | 121.499 | 62.2581 | 62.2894 | 62.1618 | 62.1932
8302.0625 | 123.262 | -60.8368 | 62.2238 | -11.0082 | -11.0297 | -11.0052 | -11.0134 | -10.9691 | -10.9163 | -10.9359 | 62.3063 | 0.2349 | 62.1963 | -0.023943 | 0.043657 | 60.9435 | 0.012299 | 60.7309 | 49.8286 | 49.8071 | 49.8316 | 49.8234 | 49.8676 | 49.9205 | 49.9009 | 123.1431 | 61.0717 | 123.0331 | 60.8128 | 60.8804 | 121.7803 | 60.8491 | 121.5677 | 62.2626 | 62.294 | 62.1526 | 62.184
8303.0938 | 123.2712 | -60.8002 | 62.2879 | -11.3745 | -11.4006 | -11.3807 | -11.3797 | -11.3171 | -11.2826 | -11.3021 | 62.3292 | 0.23948 | 62.2375 | -0.023943 | 0.048236 | 60.9252 | 0.012299 | 60.7034 | 49.4257 | 49.3996 | 49.4195 | 49.4205 | 49.4831 | 49.5176 | 49.498 | 123.1294 | 61.0396 | 123.0377 | 60.7762 | 60.8484 | 121.7254 | 60.8125 | 121.5036 | 62.2809 | 62.3169 | 62.1893 | 62.2252
8304.0625 | 123.2712 | -60.8551 | 62.2421 | -10.7839 | -10.8007 | -10.7855 | -10.7799 | -10.7265 | -10.6736 | -10.7161 | 62.288 | 0.23948 | 62.2009 | -0.023943 | 0.052814 | 60.9527 | 0.012299 | 60.7355 | 50.0712 | 50.0544 | 50.0697 | 50.0752 | 50.1286 | 50.1815 | 50.139 | 123.1431 | 61.0946 | 123.056 | 60.8312 | 60.9079 | 121.8078 | 60.8674 | 121.5906 | 62.2352 | 62.2757 | 62.1481 | 62.1886
8305.0781 | 123.2803 | -60.8139 | 62.2879 | -11.0036 | -11.0297 | -11.0098 | -10.9997 | -10.9463 | -10.9025 | -10.9176 | 62.2971 | 0.2349 | 62.2009 | -0.023943 | 0.048236 | 60.9435 | 0.021456 | 60.7217 | 49.8103 | 49.7842 | 49.8041 | 49.8142 | 49.8676 | 49.9114 | 49.8963 | 123.111 | 61.0488 | 123.0148 | 60.79 | 60.8621 | 121.7574 | 60.8354 | 121.5356 | 62.2489 | 62.2757 | 62.1526 | 62.1794
8306.0625 | 123.1888 | -60.8597 | 62.2513 | -11.3791 | -11.4097 | -11.3852 | -11.3797 | -11.3262 | -11.2642 | -11.2838 | 62.32 | 0.2349 | 62.2192 | -0.023943 | 0.043657 | 60.9298 | 0.007721 | 60.7034 | 49.4806 | 49.45 | 49.4744 | 49.48 | 49.5335 | 49.5954 | 49.5759 | 123.1797 | 61.0946 | 123.0789 | 60.8357 | 60.9033 | 121.7895 | 60.8674 | 121.5631 | 62.2764 | 62.3123 | 62.1755 | 62.2115
8307.0781 | 123.2712 | -60.8002 | 62.265 | -11.4798 | -11.5105 | -11.486 | -11.4758 | -11.4178 | -11.2963 | -11.3525 | 62.3246 | 0.2349 | 62.2238 | -0.023943 | 0.052814 | 60.9207 | 0.012299 | 60.6988 | 49.3204 | 49.2897 | 49.3142 | 49.3243 | 49.3824 | 49.5039 | 49.4477 | 123.1248 | 61.0351 | 123.0239 | 60.7762 | 60.853 | 121.7208 | 60.8125 | 121.499 | 62.2718 | 62.3123 | 62.171 | 62.2115
8308.0625 | 123.2483 | -60.7864 | 62.2742 | -11.5759 | -11.5883 | -11.5684 | -11.5628 | -11.5139 | -11.4657 | -11.4669 | 62.3383 | 0.24405 | 62.2467 | -0.028522 | 0.043657 | 60.9115 | 0.016878 | 60.6942 | 49.2105 | 49.1981 | 49.218 | 49.2236 | 49.2725 | 49.3207 | 49.3195 | 123.1248 | 61.0305 | 123.0331 | 60.7579 | 60.8301 | 121.6979 | 60.8033 | 121.4807 | 62.2947 | 62.3215 | 62.203 | 62.2298
8309.0781 | 123.3353 | -60.672 | 62.3795 | -13.389 | -13.4107 | -13.3953 | -13.3805 | -13.3314 | -13.2329 | -13.225 | 62.4345 | 0.2349 | 62.3336 | -0.028522 | 0.048236 | 60.8108 | 0.016878 | 60.5935 | 47.283 | 47.2613 | 47.2767 | 47.2915 | 47.3406 | 47.439 | 47.447 | 123.1065 | 60.9069 | 123.0056 | 60.6435 | 60.7202 | 121.4828 | 60.6889 | 121.2655 | 62.3862 | 62.4176 | 62.2854 | 62.3168
8310.0625 | 123.2391 | -60.7956 | 62.265 | -11.1913 | -11.2128 | -11.1929 | -11.1828 | -11.1294 | -11.0582 | -11.0732 | 62.3109 | 0.23948 | 62.21 | -0.019364 | 0.048236 | 60.9435 | 0.012299 | 60.7126 | 49.6042 | 49.5828 | 49.6026 | 49.6128 | 49.6662 | 49.7374 | 49.7224 | 123.1065 | 61.0351 | 123.0056 | 60.7762 | 60.8438 | 121.7391 | 60.8079 | 121.5082 | 62.2626 | 62.2986 | 62.1618 | 62.1977
8311.1094 | 123.2666 | -60.7864 | 62.2971 | -11.7087 | -11.7257 | -11.7012 | -11.6956 | -11.6513 | -11.5481 | -11.5768 | 62.3383 | 0.2349 | 62.2467 | -0.023943 | 0.052814 | 60.9115 | 0.012299 | 60.6851 | 49.0777 | 49.0608 | 49.0853 | 49.0908 | 49.1352 | 49.2383 | 49.2096 | 123.1248 | 61.0213 | 123.0331 | 60.7625 | 60.8393 | 121.6979 | 60.7987 | 121.4715 | 62.2855 | 62.326 | 62.1938 | 62.2344
8312.0625 | 123.2574 | -60.7727 | 62.3108 | -11.6675 | -11.6936 | -11.6554 | -11.6498 | -11.5826 | -11.4703 | -11.531 | 62.3383 | 0.23948 | 62.2421 | -0.023943 | 0.048236 | 60.9069 | 0.012299 | 60.6897 | 49.1052 | 49.0791 | 49.1173 | 49.1229 | 49.1901 | 49.3024 | 49.2417 | 123.111 | 61.0122 | 123.0148 | 60.7488 | 60.8209 | 121.6796 | 60.785 | 121.4624 | 62.2901 | 62.326 | 62.1938 | 62.2298
8313.0781 | 123.23 | -60.7819 | 62.3337 | -11.8781 | -11.8951 | -11.8752 | -11.8558 | -11.8069 | -11.7495 | -11.7508 | 62.3521 | 0.23948 | 62.2604 | -0.023943 | 0.052814 | 60.8932 | 0.012299 | 60.6851 | 48.9038 | 48.8868 | 48.9067 | 48.926 | 48.9749 | 49.0323 | 49.0311 | 123.1339 | 61.0213 | 123.0423 | 60.7579 | 60.8347 | 121.675 | 60.7942 | 121.467 | 62.2993 | 62.3398 | 62.2076 | 62.2481
8314.0625 | 123.1979 | -60.7864 | 62.2559 | -11.7591 | -11.7898 | -11.7561 | -11.7505 | -11.697 | -11.7083 | -11.673 | 62.3429 | 0.23948 | 62.2558 | -0.023943 | 0.052814 | 60.8978 | 0.012299 | 60.6805 | 49.0274 | 48.9967 | 49.0303 | 49.0359 | 49.0894 | 49.0781 | 49.1135 | 123.1294 | 61.0259 | 123.0423 | 60.7625 | 60.8393 | 121.6842 | 60.7987 | 121.467 | 62.2901 | 62.3306 | 62.203 | 62.2435
8315.0781 | 123.2895 | -60.7681 | 62.3337 | -11.8415 | -11.8539 | -11.8385 | -11.8192 | -11.7657 | -11.7679 | -11.7325 | 62.3429 | 0.2349 | 62.2512 | -0.019364 | 0.06197 | 60.8978 | 0.021456 | 60.6805 | 48.9267 | 48.9143 | 48.9296 | 48.9489 | 49.0024 | 49.0003 | 49.0356 | 123.111 | 61.003 | 123.0194 | 60.7488 | 60.8301 | 121.6659 | 60.7896 | 121.4486 | 62.2809 | 62.3215 | 62.1893 | 62.2298
8316.0625 | 123.317 | -60.7864 | 62.2787 | -11.6995 | -11.6982 | -11.7058 | -11.6727 | -11.6192 | -11.5893 | -11.5722 | 62.3292 | 0.23948 | 62.2329 | -0.023943 | 0.048236 | 60.9115 | 0.007721 | 60.6805 | 49.0869 | 49.0882 | 49.0807 | 49.1137 | 49.1672 | 49.1971 | 49.2142 | 123.1156 | 61.0259 | 123.0194 | 60.7625 | 60.8347 | 121.6979 | 60.7942 | 121.467 | 62.2809 | 62.3215 | 62.1847 | 62.2252
8317.0938 | 123.2117 | -60.7819 | 62.3566 | -11.8415 | -11.8584 | -11.8431 | -11.8284 | -11.7749 | -11.7541 | -11.7142 | 62.3475 | 0.22574 | 62.2512 | -0.023943 | 0.057392 | 60.8978 | 0.016878 | 60.6805 | 48.9404 | 48.9234 | 48.9388 | 48.9535 | 49.007 | 49.0277 | 49.0677 | 123.1294 | 61.0076 | 123.0331 | 60.7579 | 60.8393 | 121.6796 | 60.7987 | 121.4624 | 62.2901 | 62.3306 | 62.1938 | 62.2344
8318.0625 | 123.2346 | -60.8185 | 62.2971 | -11.8552 | -11.8722 | -11.8523 | -11.8238 | -11.7794 | -11.7724 | -11.7462 | 62.3475 | 0.24405 | 62.2467 | -0.028522 | 0.048236 | 60.8978 | 0.016878 | 60.6668 | 48.9633 | 48.9463 | 48.9662 | 48.9947 | 49.039 | 49.046 | 49.0723 | 123.166 | 61.0625 | 123.0651 | 60.79 | 60.8667 | 121.7162 | 60.8354 | 121.4853 | 62.2993 | 62.3306 | 62.1984 | 62.2298
8319.0781 | 123.2208 | -60.8231 | 62.265 | -10.9578 | -10.9839 | -10.9594 | -10.9493 | -10.9005 | -10.8842 | -10.8947 | 62.2971 | 0.23948 | 62.21 | -0.023943 | 0.057392 | 60.9527 | 0.016878 | 60.7263 | 49.8652 | 49.8392 | 49.8636 | 49.8738 | 49.9226 | 49.9388 | 49.9284 | 123.1202 | 61.0625 | 123.0331 | 60.7991 | 60.8805 | 121.7758 | 60.8399 | 121.5494 | 62.2397 | 62.2803 | 62.1526 | 62.1932
8320.0625 | 123.2529 | -60.7407 | 62.352 | -12.6839 | -12.701 | -12.681 | -12.68 | -12.6218 | -12.5828 | -12.552 | 62.3979 | 0.23948 | 62.3108 | -0.028522 | 0.052814 | 60.852 | 0.021456 | 60.6302 | 48.0568 | 48.0397 | 48.0597 | 48.0607 | 48.1189 | 48.1578 | 48.1887 | 123.1385 | 60.9801 | 123.0514 | 60.7121 | 60.7935 | 121.5926 | 60.7621 | 121.3708 | 62.345 | 62.3764 | 62.2579 | 62.2893
8321.1094 | 123.2666 | -60.7727 | 62.352 | -12.3863 | -12.4079 | -12.3834 | -12.3686 | -12.3196 | -12.2944 | -12.2498 | 62.3704 | 0.2349 | 62.2741 | -0.023943 | 0.052814 | 60.8703 | 0.012299 | 60.6485 | 48.3864 | 48.3648 | 48.3893 | 48.4041 | 48.4531 | 48.4783 | 48.5229 | 123.1431 | 61.0076 | 123.0468 | 60.7488 | 60.8255 | 121.643 | 60.785 | 121.4212 | 62.3176 | 62.3581 | 62.2213 | 62.2618
8322.0625 | 123.1934 | -60.7681 | 62.3383 | -12.5557 | -12.5682 | -12.5528 | -12.5426 | -12.4799 | -12.4684 | -12.4101 | 62.3841 | 0.2349 | 62.2741 | -0.023943 | 0.048236 | 60.8566 | 0.016878 | 60.6439 | 48.2124 | 48.2 | 48.2153 | 48.2255 | 48.2883 | 48.2998 | 48.3581 | 123.1522 | 61.003 | 123.0423 | 60.7442 | 60.8164 | 121.6247 | 60.785 | 121.412 | 62.3359 | 62.3672 | 62.2259 | 62.2573
8323.0625 | 123.1979 | -60.759 | 62.3474 | -12.3726 | -12.3896 | -12.3742 | -12.3595 | -12.3105 | -12.2806 | -12.2178 | 62.3704 | 0.23948 | 62.2787 | -0.023943 | 0.039079 | 60.8749 | 0.003143 | 60.6439 | 48.3864 | 48.3694 | 48.3847 | 48.3995 | 48.4485 | 48.4783 | 48.5412 | 123.1294 | 60.9984 | 123.0377 | 60.735 | 60.7981 | 121.6338 | 60.7621 | 121.4029 | 62.3313 | 62.3672 | 62.2396 | 62.2756
8324.0938 | 123.2254 | -60.7361 | 62.3337 | -12.4229 | -12.4308 | -12.42 | -12.3961 | -12.3471 | -12.3035 | -12.259 | 62.375 | 0.23948 | 62.2833 | -0.028522 | 0.052814 | 60.8657 | 0.007721 | 60.6485 | 48.3132 | 48.3053 | 48.3161 | 48.34 | 48.389 | 48.4325 | 48.4771 | 123.111 | 60.9756 | 123.0194 | 60.7076 | 60.7889 | 121.6018 | 60.7438 | 121.3846 | 62.3222 | 62.3672 | 62.2305 | 62.2756
8325.0625 | 123.2346 | -60.7544 | 62.352 | -12.629 | -12.646 | -12.6215 | -12.6205 | -12.5714 | -12.5279 | -12.465 | 62.3979 | 0.23948 | 62.3108 | -0.028522 | 0.048236 | 60.852 | 0.012299 | 60.6302 | 48.1254 | 48.1084 | 48.1329 | 48.1339 | 48.183 | 48.2265 | 48.2894 | 123.1523 | 60.9939 | 123.0652 | 60.7259 | 60.8026 | 121.6064 | 60.7667 | 121.3845 | 62.3496 | 62.3856 | 62.2625 | 62.2985
8326.1094 | 123.2254 | -60.8551 | 62.233 | -10.5733 | -10.613 | -10.5657 | -10.5922 | -10.5251 | -10.5088 | -10.5147 | 62.2742 | 0.23032 | 62.1688 | -0.019364 | 0.048236 | 60.9619 | 0.007721 | 60.7538 | 50.2818 | 50.2421 | 50.2894 | 50.2629 | 50.33 | 50.3463 | 50.3404 | 123.1293 | 61.0854 | 123.0239 | 60.8357 | 60.9033 | 121.817 | 60.8628 | 121.6089 | 62.226 | 62.2665 | 62.1206 | 62.1611
8327.0625 | 123.2117 | -60.8597 | 62.2375 | -10.8571 | -10.8694 | -10.8633 | -10.844 | -10.8043 | -10.7789 | -10.7619 | 62.288 | 0.23032 | 62.1917 | -0.023943 | 0.052814 | 60.9527 | 0.007721 | 60.74 | 50.0026 | 49.9903 | 49.9964 | 50.0157 | 50.0553 | 50.0807 | 50.0978 | 123.1477 | 61.09 | 123.0514 | 60.8357 | 60.9125 | 121.8124 | 60.8674 | 121.5997 | 62.2352 | 62.2803 | 62.1389 | 62.184
8328.0781 | 123.2712 | -60.704 | 62.3978 | -12.542 | -12.5498 | -12.5482 | -12.5289 | -12.4753 | -12.4455 | -12.3826 | 62.3795 | 0.2349 | 62.2833 | -0.033101 | 0.057392 | 60.852 | 0.016878 | 60.6485 | 48.1621 | 48.1542 | 48.1558 | 48.1752 | 48.2287 | 48.2586 | 48.3215 | 123.0836 | 60.9389 | 122.9873 | 60.6709 | 60.7614 | 121.556 | 60.7209 | 121.3525 | 62.3222 | 62.3627 | 62.2259 | 62.2664
8329.0625 | 123.2254 | -60.7315 | 62.3657 | -12.922 | -12.939 | -12.9282 | -12.8952 | -12.8507 | -12.8026 | -12.7443 | 62.4116 | 0.2349 | 62.3108 | -0.023943 | 0.052814 | 60.8291 | 0.012299 | 60.6118 | 47.8095 | 47.7925 | 47.8033 | 47.8363 | 47.8808 | 47.9289 | 47.9872 | 123.1431 | 60.9664 | 123.0423 | 60.7076 | 60.7843 | 121.5606 | 60.7438 | 121.3433 | 62.3588 | 62.3993 | 62.2579 | 62.2985
8330.0781 | 123.2254 | -60.8459 | 62.3016 | -10.88 | -10.8832 | -10.877 | -10.8806 | -10.8272 | -10.8018 | -10.7985 | 62.2971 | 0.24863 | 62.21 | -0.023943 | 0.06197 | 60.9481 | 0.016878 | 60.7355 | 49.9659 | 49.9628 | 49.9689 | 49.9653 | 50.0187 | 50.0441 | 50.0474 | 123.1431 | 61.0946 | 123.056 | 60.822 | 60.9079 | 121.7941 | 60.8628 | 121.5814 | 62.2352 | 62.2803 | 62.1481 | 62.1932
8331.0625 | 123.3765 | -60.8002 | 62.2238 | -11.2234 | -11.2357 | -11.2158 | -11.2286 | -11.1843 | -11.1132 | -11.119 | 62.3109 | 0.23948 | 62.2283 | -0.028522 | 0.048236 | 60.9298 | 0.012299 | 60.7126 | 49.5768 | 49.5644 | 49.5843 | 49.5716 | 49.6159 | 49.687 | 49.6812 | 123.111 | 61.0396 | 123.0285 | 60.7716 | 60.8484 | 121.73 | 60.8125 | 121.5127 | 62.2626 | 62.2986 | 62.1801 | 62.216
8332.0781 | 123.2391 | -60.8002 | 62.2742 | -11.0998 | -11.1213 | -11.0968 | -11.105 | -11.0607 | -10.9895 | -10.9908 | 62.3063 | 0.2349 | 62.2192 | -0.028522 | 0.052814 | 60.939 | 0.012299 | 60.7171 | 49.7004 | 49.6789 | 49.7034 | 49.6952 | 49.7395 | 49.8106 | 49.8094 | 123.1065 | 61.0351 | 123.0194 | 60.7716 | 60.853 | 121.7391 | 60.8125 | 121.5173 | 62.2535 | 62.294 | 62.1664 | 62.2069
8333.0625 | 123.2529 | -60.8231 | 62.2696 | -11.2463 | -11.2724 | -11.2525 | -11.2515 | -11.2118 | -11.1452 | -11.1465 | 62.3109 | 0.24405 | 62.2238 | -0.023943 | 0.052814 | 60.9298 | 0.007721 | 60.7126 | 49.5768 | 49.5507 | 49.5706 | 49.5716 | 49.6113 | 49.6779 | 49.6766 | 123.1339 | 61.0671 | 123.0468 | 60.7991 | 60.8759 | 121.7529 | 60.8308 | 121.5356 | 62.2581 | 62.3031 | 62.171 | 62.216
8334.0938 | 123.2574 | -60.8002 | 62.2742 | -11.3562 | -11.3685 | -11.3486 | -11.3522 | -11.2988 | -11.2047 | -11.2243 | 62.32 | 0.23032 | 62.2238 | -0.023943 | 0.048236 | 60.9252 | 0.012299 | 60.708 | 49.444 | 49.4317 | 49.4516 | 49.448 | 49.5014 | 49.5954 | 49.5759 | 123.1202 | 61.0305 | 123.0239 | 60.7762 | 60.8484 | 121.7254 | 60.8125 | 121.5082 | 62.2718 | 62.3077 | 62.1755 | 62.2115
8335.0625 | 123.2162 | -60.8597 | 62.2559 | -10.8846 | -10.9106 | -10.8862 | -10.8852 | -10.8318 | -10.7927 | -10.7756 | 62.2788 | 0.2349 | 62.1871 | -0.028522 | 0.048236 | 60.9481 | 0.016878 | 60.7309 | 49.9751 | 49.949 | 49.9735 | 49.9745 | 50.0279 | 50.067 | 50.084 | 123.1385 | 61.0946 | 123.0468 | 60.8312 | 60.9079 | 121.8078 | 60.8766 | 121.5906 | 62.2306 | 62.2619 | 62.1389 | 62.1703
8336.1094 | 123.2712 | -60.8322 | 62.2696 | -10.9716 | -10.9931 | -10.9594 | -10.9814 | -10.9234 | -10.8751 | -10.8581 | 62.2926 | 0.23948 | 62.2009 | -0.028522 | 0.052814 | 60.9527 | 0.007721 | 60.7217 | 49.8606 | 49.8392 | 49.8728 | 49.8509 | 49.9088 | 49.9571 | 49.9742 | 123.1248 | 61.0717 | 123.0331 | 60.8037 | 60.885 | 121.7849 | 60.8399 | 121.5539 | 62.2397 | 62.2848 | 62.1481 | 62.1932
8337.0625 | 123.1796 | -60.91 | 62.2055 | -10.1429 | -10.1643 | -10.1444 | -10.1526 | -10.0948 | -10.0555 | -10.0706 | 62.2422 | 0.22574 | 62.1459 | -0.019364 | 0.039079 | 60.9893 | 0.007721 | 60.7721 | 50.7671 | 50.7457 | 50.7656 | 50.7574 | 50.8153 | 50.8545 | 50.8394 | 123.1522 | 61.1358 | 123.056 | 60.8907 | 60.9491 | 121.8994 | 60.9178 | 121.6821 | 62.2031 | 62.2345 | 62.1069 | 62.1382
8338.0938 | 123.23 | -60.8459 | 62.2559 | -10.9487 | -10.9656 | -10.9503 | -10.9493 | -10.8959 | -10.8705 | -10.8672 | 62.288 | 0.23948 | 62.2009 | -0.023943 | 0.052814 | 60.9481 | 0.016878 | 60.7309 | 49.8973 | 49.8804 | 49.8957 | 49.8966 | 49.95 | 49.9754 | 49.9787 | 123.1339 | 61.0854 | 123.0468 | 60.822 | 60.8988 | 121.7941 | 60.8628 | 121.5768 | 62.2352 | 62.2711 | 62.1481 | 62.184
8339.0625 | 123.2254 | -60.8459 | 62.2696 | -10.9441 | -10.961 | -10.9457 | -10.9401 | -10.8776 | -10.8613 | -10.8581 | 62.2971 | 0.2349 | 62.2055 | -0.023943 | 0.048236 | 60.9481 | 0.007721 | 60.7263 | 49.9018 | 49.8849 | 49.9002 | 49.9058 | 49.9684 | 49.9846 | 49.9879 | 123.1431 | 61.0808 | 123.0514 | 60.822 | 60.8942 | 121.7941 | 60.8537 | 121.5722 | 62.2489 | 62.2894 | 62.1572 | 62.1977
8340.0781 | 123.2529 | -60.7864 | 62.3062 | -11.2142 | -11.2449 | -11.225 | -11.2149 | -11.1706 | -11.136 | -11.1465 | 62.3154 | 0.24405 | 62.2238 | -0.019364 | 0.057392 | 60.9435 | 0.016878 | 60.7126 | 49.5722 | 49.5416 | 49.5614 | 49.5716 | 49.6159 | 49.6504 | 49.64 | 123.1019 | 61.0305 | 123.0102 | 60.7671 | 60.8438 | 121.73 | 60.8033 | 121.499 | 62.2581 | 62.2986 | 62.1664 | 62.2069
8341.0625 | 123.3536 | -60.8368 | 62.2513 | -11.3241 | -11.341 | -11.3211 | -11.3293 | -11.2621 | -11.2459 | -11.238 | 62.3063 | 0.24405 | 62.2238 | -0.019364 | 0.052814 | 60.9298 | 0.012299 | 60.7034 | 49.5127 | 49.4958 | 49.5156 | 49.5075 | 49.5747 | 49.5909 | 49.5988 | 123.1431 | 61.0808 | 123.0606 | 60.8174 | 60.8896 | 121.7666 | 60.8491 | 121.5402 | 62.2535 | 62.294 | 62.171 | 62.2115
8342.0938 | 123.2574 | -60.8047 | 62.2833 | -11.3195 | -11.3365 | -11.3166 | -11.3202 | -11.2667 | -11.2459 | -11.2197 | 62.32 | 0.23948 | 62.2146 | -0.023943 | 0.043657 | 60.9252 | 0.012299 | 60.708 | 49.4852 | 49.4683 | 49.4882 | 49.4846 | 49.538 | 49.5588 | 49.585 | 123.1248 | 61.0442 | 123.0194 | 60.7808 | 60.8484 | 121.73 | 60.817 | 121.5127 | 62.2764 | 62.3077 | 62.171 | 62.2023
8343.0625 | 123.3582 | -60.6857 | 62.3657 | -13.0227 | -13.0398 | -13.0335 | -13.0005 | -12.9514 | -12.9399 | -12.8496 | 62.4116 | 0.23948 | 62.3062 | -0.023943 | 0.052814 | 60.8245 | 0.016878 | 60.6073 | 47.663 | 47.6459 | 47.6522 | 47.6853 | 47.7343 | 47.7458 | 47.8362 | 123.0973 | 60.9252 | 122.9919 | 60.6618 | 60.7385 | 121.5102 | 60.7026 | 121.293 | 62.3588 | 62.3947 | 62.2534 | 62.2893
8344.0781 | 123.2162 | -60.7086 | 62.4207 | -12.8304 | -12.8566 | -12.8367 | -12.7761 | -12.7317 | -12.711 | -12.6664 | 62.3979 | 0.2349 | 62.297 | -0.028522 | 0.048236 | 60.8382 | 0.007721 | 60.621 | 47.8782 | 47.852 | 47.872 | 47.9325 | 47.977 | 47.9976 | 48.0422 | 123.1065 | 60.9435 | 123.0056 | 60.6801 | 60.7569 | 121.5469 | 60.7163 | 121.3296 | 62.3496 | 62.3901 | 62.2488 | 62.2893
8345.0625 | 123.2437 | -60.7636 | 62.3337 | -13.0227 | -13.0489 | -13.0244 | -12.9959 | -12.9377 | -12.9079 | -12.845 | 62.407 | 0.2349 | 62.3062 | -0.042259 | 0.043657 | 60.8382 | 0.007721 | 60.6118 | 47.7408 | 47.7146 | 47.7392 | 47.7677 | 47.8259 | 47.8557 | 47.9186 | 123.1706 | 60.9984 | 123.0697 | 60.7213 | 60.8072 | 121.6018 | 60.7713 | 121.3754 | 62.3634 | 62.3993 | 62.2625 | 62.2985
8346.0938 | 123.2529 | -60.7315 | 62.3566 | -12.7846 | -12.8017 | -12.7863 | -12.7395 | -12.695 | -12.6606 | -12.6069 | 62.3887 | 0.24405 | 62.297 | -0.019364 | 0.052814 | 60.8428 | 0.012299 | 60.6302 | 47.9469 | 47.9298 | 47.9452 | 47.992 | 48.0365 | 48.0709 | 48.1246 | 123.1202 | 60.9756 | 123.0285 | 60.7121 | 60.7843 | 121.5743 | 60.7438 | 121.3617 | 62.3359 | 62.3764 | 62.2442 | 62.2847
8347.0625 | 123.2346 | -60.759 | 62.384 | -12.748 | -12.7605 | -12.7543 | -12.7532 | -12.6996 | -12.624 | -12.5566 | 62.3979 | 0.23948 | 62.3062 | -0.023943 | 0.052814 | 60.852 | 0.016878 | 60.621 | 48.011 | 47.9985 | 48.0047 | 48.0057 | 48.0594 | 48.135 | 48.2024 | 123.1568 | 60.9984 | 123.0652 | 60.735 | 60.8118 | 121.611 | 60.7758 | 121.38 | 62.345 | 62.381 | 62.2534 | 62.2893
8348.0938 | 123.2758 | -60.7315 | 62.3199 | -13.0456 | -13.0673 | -13.0427 | -13.0508 | -12.9834 | -12.9262 | -12.8633 | 62.4162 | 0.23032 | 62.3245 | -0.023943 | 0.052814 | 60.8291 | 0.007721 | 60.6073 | 47.6859 | 47.6643 | 47.6888 | 47.6807 | 47.7481 | 47.8053 | 47.8682 | 123.1477 | 60.9618 | 123.056 | 60.7076 | 60.7843 | 121.5606 | 60.7392 | 121.3388 | 62.3634 | 62.4085 | 62.2717 | 62.3168
8349.0625 | 123.2391 | -60.6812 | 62.3795 | -13.5492 | -13.5663 | -13.5509 | -13.559 | -13.5008 | -13.4298 | -13.3577 | 62.4482 | 0.23948 | 62.3611 | -0.028522 | 0.043657 | 60.797 | 0.012299 | 60.5798 | 47.1319 | 47.1148 | 47.1302 | 47.1221 | 47.1804 | 47.2513 | 47.3234 | 123.1294 | 60.9206 | 123.0423 | 60.6526 | 60.7248 | 121.4782 | 60.6935 | 121.2609 | 62.4046 | 62.4359 | 62.3175 | 62.3488
8350.0781 | 123.2162 | -60.6995 | 62.3932 | -13.4897 | -13.5114 | -13.5006 | -13.4858 | -13.4367 | -13.3795 | -13.3074 | 62.4345 | 0.23948 | 62.3428 | -0.019364 | 0.043657 | 60.8016 | 0.016878 | 60.5844 | 47.2098 | 47.1881 | 47.1989 | 47.2137 | 47.2628 | 47.32 | 47.3921 | 123.1339 | 60.9389 | 123.0423 | 60.6801 | 60.7431 | 121.5011 | 60.7163 | 121.2838 | 62.3908 | 62.4176 | 62.2991 | 62.3259
8351.0625 | 123.3078 | -60.704 | 62.3428 | -13.4256 | -13.4519 | -13.4365 | -13.4537 | -13.3909 | -13.3199 | -13.2433 | 62.4345 | 0.23948 | 62.3382 | -0.033101 | 0.052814 | 60.8062 | 0.012299 | 60.589 | 47.2784 | 47.2522 | 47.2676 | 47.2503 | 47.3132 | 47.3841 | 47.4608 | 123.1385 | 60.9435 | 123.0423 | 60.6709 | 60.7569 | 121.5102 | 60.7163 | 121.293 | 62.3817 | 62.4222 | 62.2854 | 62.3259
8352.0781 | 123.2574 | -60.6995 | 62.4161 | -13.5172 | -13.5389 | -13.5189 | -13.5499 | -13.4962 | -13.4023 | -13.3165 | 62.4436 | 0.23032 | 62.3382 | -0.023943 | 0.052814 | 60.7925 | 0.012299 | 60.5844 | 47.1823 | 47.1606 | 47.1806 | 47.1496 | 47.2033 | 47.2971 | 47.3829 | 123.1431 | 60.9298 | 123.0377 | 60.6755 | 60.7523 | 121.4919 | 60.7118 | 121.2838 | 62.3908 | 62.4313 | 62.2854 | 62.3259
8353.0625 | 123.2803 | -60.6766 | 62.384 | -13.3523 | -13.3649 | -13.354 | -13.3759 | -13.3222 | -13.2467 | -13.1975 | 62.4299 | 0.2349 | 62.3245 | -0.023943 | 0.048236 | 60.8108 | 0.012299 | 60.5844 | 47.3242 | 47.3117 | 47.3225 | 47.3007 | 47.3544 | 47.4299 | 47.4791 | 123.1065 | 60.9115 | 123.0011 | 60.6526 | 60.7248 | 121.4874 | 60.6889 | 121.2609 | 62.3817 | 62.4176 | 62.2763 | 62.3122
8354.0781 | 123.2574 | -60.6949 | 62.3795 | -13.5126 | -13.5343 | -13.5097 | -13.5407 | -13.4779 | -13.4023 | -13.3715 | 62.4391 | 0.2349 | 62.3382 | -0.019364 | 0.048236 | 60.8062 | 0.012299 | 60.5844 | 47.1823 | 47.1606 | 47.1852 | 47.1542 | 47.217 | 47.2925 | 47.3234 | 123.1339 | 60.9298 | 123.0331 | 60.6755 | 60.7431 | 121.5011 | 60.7072 | 121.2793 | 62.3908 | 62.4268 | 62.29 | 62.3259
8355.0625 | 123.2483 | -60.7132 | 62.3337 | -13.4668 | -13.5068 | -13.4731 | -13.5133 | -13.455 | -13.352 | -13.3394 | 62.4345 | 0.23032 | 62.3336 | -0.023943 | 0.048236 | 60.797 | 0.012299 | 60.589 | 47.2464 | 47.2064 | 47.2401 | 47.1999 | 47.2582 | 47.3612 | 47.3738 | 123.1477 | 60.9435 | 123.0468 | 60.6893 | 60.7614 | 121.5102 | 60.7255 | 121.3021 | 62.3862 | 62.4222 | 62.2854 | 62.3213
8356.0938 | 123.3215 | -60.7132 | 62.3474 | -12.867 | -12.8887 | -12.8779 | -12.9226 | -12.869 | -12.7064 | -12.7214 | 62.3979 | 0.23948 | 62.3153 | -0.019364 | 0.048236 | 60.8382 | 0.007721 | 60.6118 | 47.8462 | 47.8245 | 47.8353 | 47.7906 | 47.8442 | 48.0068 | 47.9918 | 123.1111 | 60.9527 | 123.0285 | 60.6938 | 60.7614 | 121.5514 | 60.7209 | 121.325 | 62.3496 | 62.3901 | 62.2671 | 62.3076
8357.0625 | 123.2574 | -60.7407 | 62.3245 | -13.9018 | -13.9281 | -13.9081 | -13.9711 | -13.9036 | -13.7686 | -13.724 | 62.462 | 0.24405 | 62.3703 | -0.028522 | 0.048236 | 60.7833 | 0.007721 | 60.5569 | 46.8389 | 46.8126 | 46.8326 | 46.7695 | 46.837 | 46.972 | 47.0167 | 123.2026 | 60.9847 | 123.1109 | 60.7121 | 60.7889 | 121.524 | 60.7484 | 121.2976 | 62.4137 | 62.4542 | 62.322 | 62.3626
8358.0938 | 123.1888 | -60.704 | 62.4023 | -13.714 | -13.7312 | -13.7158 | -13.7605 | -13.6976 | -13.6084 | -13.5592 | 62.4528 | 0.23948 | 62.3611 | -0.028522 | 0.048236 | 60.7925 | 0.007721 | 60.5661 | 46.99 | 46.9729 | 46.9883 | 46.9435 | 47.0064 | 47.0957 | 47.1449 | 123.1568 | 60.9435 | 123.0652 | 60.6755 | 60.7523 | 121.4965 | 60.7118 | 121.2701 | 62.4046 | 62.4451 | 62.3129 | 62.3534
8359.0625 | 123.2758 | -60.7269 | 62.3337 | -13.0135 | -13.0306 | -13.0152 | -13.1012 | -13.0384 | -12.8804 | -12.8816 | 62.4162 | 0.23948 | 62.3153 | -0.028522 | 0.048236 | 60.8245 | 0.007721 | 60.6118 | 47.7134 | 47.6963 | 47.7117 | 47.6257 | 47.6885 | 47.8465 | 47.8453 | 123.1431 | 60.9664 | 123.0423 | 60.6984 | 60.7752 | 121.5514 | 60.7346 | 121.3388 | 62.3679 | 62.4085 | 62.2671 | 62.3076
8360.0938 | 123.2758 | -60.6674 | 62.4023 | -13.9796 | -13.9922 | -13.9813 | -14.0306 | -13.9723 | -13.8785 | -13.8293 | 62.4711 | 0.2349 | 62.3611 | -0.028522 | 0.043657 | 60.7696 | 0.007721 | 60.5615 | 46.6878 | 46.6752 | 46.6861 | 46.6368 | 46.6951 | 46.7889 | 46.8381 | 123.1385 | 60.9023 | 123.0285 | 60.6389 | 60.7111 | 121.437 | 60.6751 | 121.2289 | 62.4275 | 62.4634 | 62.3175 | 62.3534
8361.0625 | 123.3536 | -60.6445 | 62.3657 | -13.3386 | -13.3649 | -13.3403 | -13.4263 | -13.3588 | -13.2101 | -13.1517 | 62.4253 | 0.23032 | 62.3291 | -0.023943 | 0.043657 | 60.8154 | 0.016878 | 60.5935 | 47.3059 | 47.2797 | 47.3042 | 47.2183 | 47.2857 | 47.4345 | 47.4928 | 123.0699 | 60.8748 | 122.9736 | 60.6206 | 60.6882 | 121.4599 | 60.6614 | 121.2381 | 62.3817 | 62.4085 | 62.2854 | 62.3122
8362.0938 | 123.3261 | -60.6812 | 62.3566 | -13.9246 | -13.9555 | -13.9355 | -13.9757 | -13.9265 | -13.8098 | -13.724 | 62.462 | 0.2349 | 62.352 | -0.028522 | 0.048236 | 60.7833 | 0.007721 | 60.5569 | 46.7565 | 46.7256 | 46.7456 | 46.7055 | 46.7546 | 46.8713 | 46.9572 | 123.1431 | 60.916 | 123.0331 | 60.6526 | 60.7294 | 121.4645 | 60.6889 | 121.2381 | 62.4137 | 62.4542 | 62.3037 | 62.3442
8363.0625 | 123.3398 | -60.6537 | 62.3795 | -13.8789 | -13.9098 | -13.8897 | -13.9528 | -13.8899 | -13.7595 | -13.6919 | 62.4528 | 0.23032 | 62.352 | -0.033101 | 0.043657 | 60.7787 | 0.012299 | 60.5615 | 46.7748 | 46.7439 | 46.7639 | 46.7009 | 46.7638 | 46.8942 | 46.9617 | 123.1065 | 60.884 | 123.0056 | 60.6206 | 60.6973 | 121.4324 | 60.666 | 121.2152 | 62.4091 | 62.4405 | 62.3083 | 62.3397
8364.0781 | 123.2437 | -60.6766 | 62.4344 | -14.0757 | -14.0838 | -14.0866 | -14.1268 | -14.073 | -13.9746 | -13.898 | 62.4711 | 0.2349 | 62.3703 | -0.023943 | 0.048236 | 60.7696 | 0.012299 | 60.5569 | 46.6008 | 46.5928 | 46.59 | 46.5498 | 46.6036 | 46.7019 | 46.7786 | 123.1477 | 60.9115 | 123.0469 | 60.6526 | 60.7248 | 121.4462 | 60.6889 | 121.2335 | 62.4229 | 62.4588 | 62.322 | 62.358
8365.0625 | 123.2941 | -60.6445 | 62.3978 | -14.1948 | -14.212 | -14.2057 | -14.2367 | -14.1829 | -14.0845 | -14.0445 | 62.4711 | 0.2349 | 62.3749 | -0.028522 | 0.043657 | 60.765 | 0.007721 | 60.5386 | 46.4498 | 46.4326 | 46.4389 | 46.4079 | 46.4617 | 46.56 | 46.6001 | 123.1156 | 60.8794 | 123.0194 | 60.616 | 60.6882 | 121.4095 | 60.6523 | 121.1831 | 62.4275 | 62.4634 | 62.3312 | 62.3671
8366.1094 | 123.2849 | -60.6354 | 62.4298 | -14.4557 | -14.473 | -14.4575 | -14.5343 | -14.4804 | -14.3638 | -14.3146 | 62.494 | 0.2349 | 62.3977 | -0.019364 | 0.039079 | 60.7467 | 0.016878 | 60.5203 | 46.1796 | 46.1624 | 46.1779 | 46.1011 | 46.1549 | 46.2716 | 46.3208 | 123.1294 | 60.8703 | 123.0331 | 60.616 | 60.6745 | 121.3821 | 60.6523 | 121.1557 | 62.4549 | 62.4771 | 62.3587 | 62.3809
8367.0625 | 123.2437 | -60.6262 | 62.4481 | -14.5519 | -14.5783 | -14.5674 | -14.6121 | -14.5537 | -14.4416 | -14.4016 | 62.494 | 0.23948 | 62.3932 | -0.023943 | 0.048236 | 60.7467 | 0.012299 | 60.5249 | 46.0743 | 46.048 | 46.0588 | 46.0141 | 46.0725 | 46.1846 | 46.2247 | 123.1202 | 60.8657 | 123.0194 | 60.6023 | 60.6745 | 121.3729 | 60.6385 | 121.1511 | 62.4458 | 62.4817 | 62.3449 | 62.3809
8368.0938 | 123.2254 | -60.6674 | 62.4298 | -14.6297 | -14.6561 | -14.6315 | -14.7083 | -14.6498 | -14.5149 | -14.4428 | 62.4986 | 0.2349 | 62.4023 | -0.023943 | 0.052814 | 60.733 | 0.012299 | 60.5157 | 46.0377 | 46.0113 | 46.0359 | 45.9592 | 46.0176 | 46.1525 | 46.2247 | 123.166 | 60.9023 | 123.0697 | 60.6435 | 60.7202 | 121.4004 | 60.6797 | 121.1831 | 62.4458 | 62.4863 | 62.3495 | 62.39
8369.0625 | 123.262 | -60.6674 | 62.4207 | -14.5565 | -14.5737 | -14.5628 | -14.6213 | -14.5674 | -14.4508 | -14.3191 | 62.494 | 0.23948 | 62.3886 | -0.028522 | 0.039079 | 60.7421 | 0.007721 | 60.5249 | 46.111 | 46.0937 | 46.1046 | 46.0462 | 46.1 | 46.2166 | 46.3483 | 123.1614 | 60.9069 | 123.056 | 60.6389 | 60.7065 | 121.4095 | 60.6751 | 121.1923 | 62.4549 | 62.4863 | 62.3495 | 62.3809
8370.0781 | 123.2574 | -60.6445 | 62.471 | -14.41 | -14.4272 | -14.4117 | -14.4564 | -14.398 | -14.286 | -14.2413 | 62.4848 | 0.23948 | 62.384 | -0.023943 | 0.048236 | 60.7467 | 0.007721 | 60.5294 | 46.2346 | 46.2174 | 46.2328 | 46.1881 | 46.2465 | 46.3586 | 46.4032 | 123.1294 | 60.884 | 123.0285 | 60.6206 | 60.6928 | 121.3912 | 60.6523 | 121.174 | 62.4366 | 62.4771 | 62.3358 | 62.3763
8371.0625 | 123.3078 | -60.6491 | 62.4298 | -14.2314 | -14.2532 | -14.2377 | -14.3008 | -14.2332 | -14.1028 | -14.0673 | 62.4711 | 0.23032 | 62.3749 | -0.028522 | 0.048236 | 60.7604 | 0.012299 | 60.5386 | 46.4177 | 46.3959 | 46.4114 | 46.3483 | 46.4159 | 46.5463 | 46.5818 | 123.1202 | 60.8794 | 123.024 | 60.6206 | 60.6973 | 121.4095 | 60.6614 | 121.1877 | 62.4229 | 62.4588 | 62.3266 | 62.3626
8372.0781 | 123.2391 | -60.6583 | 62.4207 | -14.1581 | -14.1845 | -14.1599 | -14.2 | -14.1417 | -14.0571 | -13.9529 | 62.4757 | 0.2349 | 62.3794 | -0.028522 | 0.048236 | 60.7696 | 0.012299 | 60.5432 | 46.5001 | 46.4738 | 46.4984 | 46.4582 | 46.5166 | 46.6012 | 46.7054 | 123.134 | 60.8932 | 123.0377 | 60.6297 | 60.7065 | 121.4278 | 60.6706 | 121.2014 | 62.4275 | 62.4634 | 62.3312 | 62.3671
8373.0625 | 123.3124 | -60.7132 | 62.3245 | -13.801 | -13.8365 | -13.8119 | -13.8841 | -13.8166 | -13.6633 | -13.6599 | 62.462 | 0.23948 | 62.3657 | -0.023943 | 0.048236 | 60.7833 | 0.007721 | 60.5615 | 46.9122 | 46.8767 | 46.9013 | 46.8291 | 46.8966 | 47.0499 | 47.0533 | 123.1752 | 60.9527 | 123.0789 | 60.6893 | 60.7614 | 121.4965 | 60.7209 | 121.2747 | 62.4137 | 62.4542 | 62.3175 | 62.358
8374.0781 | 123.2025 | -60.6171 | 62.4298 | -14.6343 | -14.6515 | -14.6498 | -14.7083 | -14.6498 | -14.492 | -14.4565 | 62.5077 | 0.24405 | 62.4298 | -0.019364 | 0.052814 | 60.7421 | 0.021456 | 60.5203 | 45.9828 | 45.9655 | 45.9673 | 45.9088 | 45.9672 | 46.1251 | 46.1606 | 123.1248 | 60.8611 | 123.0469 | 60.5977 | 60.6699 | 121.3592 | 60.6385 | 121.1373 | 62.4549 | 62.4863 | 62.377 | 62.4083
8375.0625 | 123.2437 | -60.6766 | 62.4115 | -13.7598 | -13.7861 | -13.757 | -13.8154 | -13.7525 | -13.5992 | -13.5363 | 62.4528 | 0.2349 | 62.3657 | -0.023943 | 0.048236 | 60.7925 | 0.012299 | 60.5615 | 46.9168 | 46.8904 | 46.9196 | 46.8611 | 46.924 | 47.0774 | 47.1403 | 123.1294 | 60.9115 | 123.0423 | 60.6526 | 60.7248 | 121.469 | 60.6889 | 121.2381 | 62.4046 | 62.4405 | 62.3175 | 62.3534
8376.0938 | 123.3307 | -60.6033 | 62.4115 | -13.6454 | -13.6717 | -13.6608 | -13.733 | -13.6839 | -13.4985 | -13.4401 | 62.4436 | 0.2349 | 62.352 | -0.019364 | 0.043657 | 60.7879 | 0.012299 | 60.5661 | 46.958 | 46.9317 | 46.9425 | 46.8703 | 46.9195 | 47.1048 | 47.1632 | 123.047 | 60.8382 | 122.9553 | 60.584 | 60.647 | 121.3912 | 60.6156 | 121.1694 | 62.4 | 62.4313 | 62.3083 | 62.3397
8377.0625 | 123.3398 | -60.6308 | 62.3886 | -14.616 | -14.6195 | -14.6177 | -14.635 | -14.572 | -14.4828 | -14.4519 | 62.4986 | 0.22574 | 62.3977 | -0.028522 | 0.052814 | 60.7421 | 0.016878 | 60.5203 | 46.0148 | 46.0113 | 46.0131 | 45.9958 | 46.0588 | 46.148 | 46.1789 | 123.1294 | 60.8565 | 123.0285 | 60.6023 | 60.6836 | 121.3729 | 60.6477 | 121.1511 | 62.4458 | 62.4817 | 62.3449 | 62.3809
8378.0781 | 123.2162 | -60.7315 | 62.3566 | -13.3523 | -13.3832 | -13.3495 | -13.408 | -13.3405 | -13.178 | -13.17 | 62.4299 | 0.23948 | 62.3199 | -0.028522 | 0.052814 | 60.8108 | 0.007721 | 60.589 | 47.3792 | 47.3483 | 47.382 | 47.3235 | 47.391 | 47.5535 | 47.5615 | 123.1614 | 60.971 | 123.0514 | 60.703 | 60.7843 | 121.5423 | 60.7392 | 121.3205 | 62.3771 | 62.4222 | 62.2671 | 62.3122
8379.0625 | 123.349 | -60.6033 | 62.4069 | -14.6068 | -14.6286 | -14.6177 | -14.6487 | -14.5857 | -14.4783 | -14.4428 | 62.4986 | 0.23948 | 62.3977 | -0.023943 | 0.043657 | 60.7375 | 0.012299 | 60.5111 | 45.9965 | 45.9747 | 45.9856 | 45.9546 | 46.0176 | 46.1251 | 46.1606 | 123.1019 | 60.8428 | 123.0011 | 60.5794 | 60.647 | 121.3409 | 60.6156 | 121.1145 | 62.4549 | 62.4863 | 62.3541 | 62.3854
8380.0938 | 123.2437 | -60.6216 | 62.439 | -14.3962 | -14.4226 | -14.4117 | -14.4244 | -14.3797 | -14.2677 | -14.2276 | 62.494 | 0.23948 | 62.3932 | -0.033101 | 0.052814 | 60.7513 | 0.012299 | 60.534 | 46.2254 | 46.1991 | 46.2099 | 46.1973 | 46.2419 | 46.354 | 46.3941 | 123.1156 | 60.8611 | 123.0148 | 60.5885 | 60.6745 | 121.3729 | 60.6339 | 121.1557 | 62.4412 | 62.4817 | 62.3404 | 62.3809
8381.0625 | 123.3124 | -60.6171 | 62.4573 | -13.9842 | -13.9968 | -13.9951 | -14.0306 | -13.9677 | -13.8465 | -13.8064 | 62.462 | 0.23948 | 62.3657 | -0.023943 | 0.048236 | 60.7742 | 0.012299 | 60.5477 | 46.6329 | 46.6203 | 46.622 | 46.5864 | 46.6494 | 46.7706 | 46.8107 | 123.079 | 60.8565 | 122.9828 | 60.5931 | 60.6653 | 121.3912 | 60.6294 | 121.1648 | 62.4137 | 62.4497 | 62.3175 | 62.3534
8382.0938 | 123.2025 | -60.6491 | 62.4527 | -14.4237 | -14.4409 | -14.4346 | -14.461 | -14.4026 | -14.3043 | -14.2551 | 62.494 | 0.24405 | 62.4023 | -0.023943 | 0.052814 | 60.7513 | 0.003143 | 60.5249 | 46.2254 | 46.2082 | 46.2145 | 46.1881 | 46.2465 | 46.3448 | 46.3941 | 123.1431 | 60.8932 | 123.0514 | 60.6252 | 60.7019 | 121.4004 | 60.6523 | 121.174 | 62.4412 | 62.4909 | 62.3495 | 62.3992
8383.0625 | 123.2986 | -60.64 | 62.4527 | -14.41 | -14.4272 | -14.4209 | -14.4473 | -14.3889 | -14.2677 | -14.1452 | 62.4894 | 0.2349 | 62.3886 | -0.028522 | 0.043657 | 60.7467 | 0.012299 | 60.5249 | 46.23 | 46.2128 | 46.2191 | 46.1927 | 46.2511 | 46.3723 | 46.4948 | 123.1294 | 60.8749 | 123.0285 | 60.6114 | 60.6836 | 121.3866 | 60.6523 | 121.1648 | 62.4458 | 62.4771 | 62.3449 | 62.3763
8384.0781 | 123.2483 | -60.6308 | 62.4527 | -14.4969 | -14.5279 | -14.5079 | -14.5205 | -14.4576 | -14.3638 | -14.2642 | 62.494 | 0.23032 | 62.4069 | -0.019364 | 0.052814 | 60.7375 | 0.007721 | 60.5249 | 46.1339 | 46.1029 | 46.1229 | 46.1103 | 46.1732 | 46.267 | 46.3666 | 123.1248 | 60.8611 | 123.0377 | 60.6114 | 60.6836 | 121.3683 | 60.6385 | 121.1557 | 62.4412 | 62.4863 | 62.3541 | 62.3992
8385.0625 | 123.317 | -60.6583 | 62.3566 | -13.8331 | -13.8502 | -13.8394 | -13.8795 | -13.8212 | -13.645 | -13.5775 | 62.4528 | 0.23948 | 62.3565 | -0.023943 | 0.048236 | 60.7879 | 0.012299 | 60.5523 | 46.8252 | 46.808 | 46.8189 | 46.7787 | 46.837 | 47.0133 | 47.0808 | 123.1111 | 60.8977 | 123.0148 | 60.6343 | 60.7065 | 121.4462 | 60.6706 | 121.2106 | 62.4046 | 62.4405 | 62.3083 | 62.3442
8386.1094 | 123.23 | -60.6354 | 62.4527 | -14.8815 | -14.9079 | -14.9016 | -14.9051 | -14.8513 | -14.753 | -14.6305 | 62.5123 | 0.22574 | 62.4115 | -0.028522 | 0.052814 | 60.7238 | 0.021456 | 60.5111 | 45.7538 | 45.7274 | 45.7338 | 45.7302 | 45.7841 | 45.8824 | 46.0049 | 123.1477 | 60.8611 | 123.0469 | 60.6069 | 60.6882 | 121.3592 | 60.6568 | 121.1465 | 62.4595 | 62.4909 | 62.3587 | 62.39
8387.0625 | 123.349 | -60.6033 | 62.4161 | -14.9365 | -14.9583 | -14.952 | -14.9646 | -14.9108 | -14.7988 | -14.6762 | 62.5123 | 0.22574 | 62.4115 | -0.023943 | 0.048236 | 60.7192 | 0.012299 | 60.4974 | 45.6669 | 45.645 | 45.6514 | 45.6387 | 45.6926 | 45.8046 | 45.9271 | 123.1157 | 60.8291 | 123.0148 | 60.5794 | 60.6516 | 121.3226 | 60.6156 | 121.1007 | 62.4641 | 62.5 | 62.3632 | 62.3992
8388.0938 | 123.262 | -60.5804 | 62.5031 | -15.0463 | -15.0682 | -15.0619 | -15.0745 | -15.0252 | -14.9041 | -14.7815 | 62.5215 | 0.24405 | 62.4298 | -0.028522 | 0.052814 | 60.7238 | 0.012299 | 60.4974 | 45.5341 | 45.5122 | 45.5186 | 45.5059 | 45.5552 | 45.6764 | 45.7989 | 123.1019 | 60.8245 | 123.0102 | 60.5519 | 60.6333 | 121.3042 | 60.5927 | 121.0778 | 62.4687 | 62.5092 | 62.377 | 62.4175
8389.0625 | 123.2254 | -60.6354 | 62.4435 | -14.8861 | -14.9079 | -14.8879 | -14.9097 | -14.8513 | -14.7438 | -14.635 | 62.5032 | 0.23032 | 62.4161 | -0.023943 | 0.052814 | 60.7192 | 0.007721 | 60.4974 | 45.7493 | 45.7274 | 45.7475 | 45.7257 | 45.7841 | 45.8916 | 46.0003 | 123.1385 | 60.8657 | 123.0514 | 60.6114 | 60.6882 | 121.3546 | 60.6431 | 121.1328 | 62.4503 | 62.4954 | 62.3632 | 62.4083
8390.0781 | 123.175 | -60.6216 | 62.4664 | -14.6755 | -14.6927 | -14.6956 | -14.6854 | -14.6315 | -14.5286 | -14.4199 | 62.5077 | 0.23948 | 62.4115 | -0.028522 | 0.052814 | 60.733 | 0.016878 | 60.5203 | 45.9461 | 45.9289 | 45.9261 | 45.9363 | 45.9901 | 46.093 | 46.2018 | 123.1294 | 60.8611 | 123.0331 | 60.5931 | 60.6745 | 121.3546 | 60.6385 | 121.1419 | 62.4549 | 62.4909 | 62.3587 | 62.3946
8391.0625 | 123.3078 | -60.5896 | 62.4115 | -14.6206 | -14.6515 | -14.6406 | -14.667 | -14.6132 | -14.4874 | -14.3741 | 62.5032 | 0.23948 | 62.4115 | -0.023943 | 0.052814 | 60.7421 | 0.016878 | 60.5157 | 45.969 | 45.9381 | 45.949 | 45.9226 | 45.9764 | 46.1022 | 46.2155 | 123.0928 | 60.8291 | 123.0011 | 60.5657 | 60.6424 | 121.3317 | 60.6065 | 121.1053 | 62.4503 | 62.4863 | 62.3587 | 62.3946
8392.0781 | 123.23 | -60.6262 | 62.4664 | -14.7121 | -14.7385 | -14.7276 | -14.7632 | -14.7048 | -14.5607 | -14.4428 | 62.4986 | 0.2349 | 62.4161 | -0.023943 | 0.043657 | 60.7284 | 0.012299 | 60.5157 | 45.9141 | 45.8877 | 45.8986 | 45.863 | 45.9215 | 46.0655 | 46.1835 | 123.1248 | 60.8611 | 123.0423 | 60.6023 | 60.6699 | 121.3546 | 60.6385 | 121.1419 | 62.4549 | 62.4863 | 62.3724 | 62.4038
8393.0625 | 123.3124 | -60.6125 | 62.4023 | -14.7121 | -14.7339 | -14.723 | -14.7449 | -14.6865 | -14.5653 | -14.4382 | 62.5123 | 0.2349 | 62.4115 | -0.023943 | 0.039079 | 60.7375 | 0.016878 | 60.5111 | 45.9004 | 45.8785 | 45.8894 | 45.8676 | 45.926 | 46.0472 | 46.1743 | 123.1248 | 60.8474 | 123.024 | 60.5885 | 60.6516 | 121.35 | 60.6294 | 121.1236 | 62.4732 | 62.4954 | 62.3724 | 62.3946
8394.1094 | 123.3078 | -60.6171 | 62.4252 | -14.5702 | -14.5966 | -14.5857 | -14.6121 | -14.5491 | -14.405 | -14.3054 | 62.4894 | 0.22574 | 62.3932 | -0.019364 | 0.048236 | 60.7513 | 0.007721 | 60.5111 | 46.0469 | 46.0205 | 46.0314 | 46.005 | 46.068 | 46.212 | 46.3117 | 123.1065 | 60.8428 | 123.0102 | 60.5977 | 60.6653 | 121.3683 | 60.6248 | 121.1282 | 62.4412 | 62.4817 | 62.3449 | 62.3854
8395.0625 | 123.3215 | -60.585 | 62.4023 | -14.8678 | -14.885 | -14.8787 | -14.9097 | -14.8558 | -14.7163 | -14.5893 | 62.5077 | 0.2349 | 62.4115 | -0.028522 | 0.048236 | 60.7192 | 0.007721 | 60.502 | 45.7172 | 45.7 | 45.7063 | 45.6753 | 45.7292 | 45.8687 | 45.9958 | 123.0928 | 60.8199 | 122.9965 | 60.5565 | 60.6333 | 121.3042 | 60.5927 | 121.087 | 62.4595 | 62.5 | 62.3632 | 62.4038
8396.1094 | 123.2529 | -60.6171 | 62.4573 | -14.822 | -14.853 | -14.8421 | -14.8593 | -14.8101 | -14.666 | -14.5389 | 62.5077 | 0.23948 | 62.4069 | -0.023943 | 0.043657 | 60.7238 | 0.012299 | 60.5065 | 45.7951 | 45.7641 | 45.775 | 45.7577 | 45.807 | 45.9511 | 46.0782 | 123.1248 | 60.8565 | 123.024 | 60.5931 | 60.6607 | 121.3409 | 60.6294 | 121.1236 | 62.4641 | 62.4954 | 62.3632 | 62.3946
8397.0625 | 123.2849 | -60.6308 | 62.4115 | -14.5381 | -14.5691 | -14.5582 | -14.5663 | -14.5033 | -14.3867 | -14.2779 | 62.4894 | 0.23032 | 62.3977 | -0.023943 | 0.052814 | 60.733 | 0.012299 | 60.5203 | 46.0927 | 46.0617 | 46.0726 | 46.0645 | 46.1275 | 46.2441 | 46.3529 | 123.1202 | 60.8611 | 123.0285 | 60.6069 | 60.6836 | 121.3637 | 60.6431 | 121.1511 | 62.4366 | 62.4771 | 62.3449 | 62.3854
8398.0938 | 123.2437 | -60.704 | 62.3795 | -14.0254 | -14.0517 | -14.0271 | -14.0718 | -13.9998 | -13.8602 | -13.8751 | 62.4757 | 0.24405 | 62.3749 | -0.028522 | 0.043657 | 60.7696 | 0.007721 | 60.5569 | 46.6787 | 46.6523 | 46.6769 | 46.6322 | 46.7043 | 46.8439 | 46.829 | 123.1797 | 60.9481 | 123.0789 | 60.6755 | 60.7477 | 121.4736 | 60.7118 | 121.2609 | 62.432 | 62.468 | 62.3312 | 62.3671
8399.0625 | 123.2025 | -60.6308 | 62.4802 | -14.6572 | -14.6836 | -14.6818 | -14.7586 | -14.6956 | -14.5149 | -14.4977 | 62.5077 | 0.23948 | 62.4161 | -0.023943 | 0.048236 | 60.733 | 0.021456 | 60.5157 | 45.9736 | 45.9472 | 45.949 | 45.8722 | 45.9352 | 46.1159 | 46.1331 | 123.1385 | 60.8703 | 123.0469 | 60.6069 | 60.679 | 121.3637 | 60.6523 | 121.1465 | 62.4595 | 62.4863 | 62.3678 | 62.3946
8400.0938 | 123.1934 | -60.6674 | 62.4664 | -14.7533 | -14.7752 | -14.7688 | -14.841 | -14.7872 | -14.5973 | -14.6122 | 62.5123 | 0.23948 | 62.4252 | -0.023943 | 0.043657 | 60.7238 | 0.007721 | 60.5065 | 45.9141 | 45.8923 | 45.8986 | 45.8264 | 45.8803 | 46.0701 | 46.0553 | 123.1797 | 60.9069 | 123.0926 | 60.6435 | 60.7111 | 121.3912 | 60.6751 | 121.174 | 62.4687 | 62.5046 | 62.3816 | 62.4175
8401.0625 | 123.3444 | -60.5988 | 62.4344 | -14.5977 | -14.6286 | -14.6132 | -14.667 | -14.604 | -14.4187 | -14.4611 | 62.4986 | 0.2349 | 62.4069 | -0.019364 | 0.052814 | 60.733 | 0.012299 | 60.5157 | 46.0011 | 45.9701 | 45.9856 | 45.9317 | 45.9947 | 46.18 | 46.1377 | 123.0973 | 60.8337 | 123.0057 | 60.5794 | 60.6516 | 121.3317 | 60.6111 | 121.1145 | 62.4458 | 62.4863 | 62.3541 | 62.3946
8402.0938 | 123.2803 | -60.64 | 62.4298 | -14.6618 | -14.6882 | -14.6864 | -14.7357 | -14.6681 | -14.4874 | -14.5252 | 62.5032 | 0.2349 | 62.4161 | -0.033101 | 0.043657 | 60.7375 | 0.007721 | 60.5111 | 45.9782 | 45.9518 | 45.9535 | 45.9042 | 45.9718 | 46.1525 | 46.1148 | 123.1431 | 60.8749 | 123.056 | 60.6069 | 60.6836 | 121.3775 | 60.6477 | 121.1511 | 62.4595 | 62.4954 | 62.3724 | 62.4083
8403.0625 | 123.2895 | -60.5896 | 62.4344 | -14.9136 | -14.94 | -14.9382 | -15.0104 | -14.952 | -14.7713 | -14.7724 | 62.5032 | 0.2349 | 62.4115 | -0.023943 | 0.052814 | 60.7238 | 0.007721 | 60.4928 | 45.676 | 45.6496 | 45.6514 | 45.5792 | 45.6376 | 45.8183 | 45.8172 | 123.0928 | 60.8245 | 123.0011 | 60.5657 | 60.6424 | 121.3134 | 60.5973 | 121.0824 | 62.4503 | 62.4954 | 62.3587 | 62.4038
8404.0938 | 123.3536 | -60.6033 | 62.4115 | -14.7854 | -14.8118 | -14.81 | -14.8364 | -14.778 | -14.6294 | -14.6442 | 62.5077 | 0.2349 | 62.4206 | -0.023943 | 0.048236 | 60.7238 | 0.012299 | 60.502 | 45.818 | 45.7915 | 45.7933 | 45.7669 | 45.8253 | 45.974 | 45.9591 | 123.1111 | 60.8382 | 123.024 | 60.5794 | 60.6516 | 121.3271 | 60.6156 | 121.1053 | 62.4595 | 62.4954 | 62.3724 | 62.4083
8405.0625 | 123.2895 | -60.5988 | 62.4023 | -14.7167 | -14.7431 | -14.7459 | -14.7815 | -14.7185 | -14.5424 | -14.5801 | 62.5123 | 0.23948 | 62.4161 | -0.023943 | 0.052814 | 60.733 | 0.012299 | 60.5111 | 45.8821 | 45.8557 | 45.8528 | 45.8172 | 45.8803 | 46.0564 | 46.0186 | 123.1111 | 60.8382 | 123.0148 | 60.5748 | 60.6516 | 121.3317 | 60.6111 | 121.1099 | 62.4595 | 62.5 | 62.3632 | 62.4038
8406.0938 | 123.2208 | -60.6354 | 62.4527 | -14.6938 | -14.7065 | -14.7093 | -14.7403 | -14.6865 | -14.4966 | -14.5481 | 62.5032 | 0.24405 | 62.4252 | -0.014785 | 0.048236 | 60.733 | 0.016878 | 60.5111 | 45.9416 | 45.9289 | 45.9261 | 45.8951 | 45.9489 | 46.1388 | 46.0873 | 123.1385 | 60.8794 | 123.0606 | 60.6206 | 60.6836 | 121.3683 | 60.6523 | 121.1465 | 62.4549 | 62.4863 | 62.377 | 62.4083
8407.0625 | 123.3078 | -60.6354 | 62.3978 | -14.5153 | -14.5416 | -14.5307 | -14.5938 | -14.5308 | -14.3455 | -14.3924 | 62.4848 | 0.2349 | 62.4069 | -0.028522 | 0.048236 | 60.7421 | 0.007721 | 60.5157 | 46.1201 | 46.0937 | 46.1046 | 46.0416 | 46.1046 | 46.2899 | 46.243 | 123.1202 | 60.8703 | 123.0423 | 60.6069 | 60.6836 | 121.3775 | 60.6431 | 121.1511 | 62.4366 | 62.4771 | 62.3587 | 62.3992
8408.0938 | 123.317 | -60.6033 | 62.3978 | -14.8357 | -14.8576 | -14.8604 | -14.8914 | -14.8329 | -14.6339 | -14.7174 | 62.5123 | 0.24405 | 62.4161 | -0.028522 | 0.043657 | 60.7284 | 0.012299 | 60.5065 | 45.7676 | 45.7458 | 45.7429 | 45.7119 | 45.7704 | 45.9694 | 45.8859 | 123.1157 | 60.8474 | 123.0194 | 60.5748 | 60.647 | 121.3317 | 60.6156 | 121.1099 | 62.4687 | 62.5 | 62.3724 | 62.4038
8409.0781 | 123.3765 | -60.5988 | 62.439 | -14.7716 | -14.7889 | -14.8009 | -14.8136 | -14.7643 | -14.5698 | -14.6213 | 62.5077 | 0.2349 | 62.4115 | -0.028522 | 0.052814 | 60.733 | 0.012299 | 60.5065 | 45.8271 | 45.8099 | 45.7979 | 45.7852 | 45.8345 | 46.0289 | 45.9774 | 123.1065 | 60.8337 | 123.0102 | 60.5702 | 60.6516 | 121.3317 | 60.6111 | 121.1053 | 62.4549 | 62.4954 | 62.3587 | 62.3992
8410.0625 | 123.3444 | -60.5988 | 62.3932 | -14.7533 | -14.7797 | -14.778 | -14.8136 | -14.746 | -14.5332 | -14.6122 | 62.5077 | 0.2349 | 62.4161 | -0.028522 | 0.048236 | 60.7284 | 0.007721 | 60.502 | 45.8454 | 45.819 | 45.8208 | 45.7852 | 45.8528 | 46.0655 | 45.9866 | 123.1065 | 60.8337 | 123.0148 | 60.5702 | 60.647 | 121.3271 | 60.6065 | 121.1007 | 62.4595 | 62.5 | 62.3678 | 62.4083
8411.1094 | 123.2254 | -60.6216 | 62.4527 | -14.8312 | -14.8667 | -14.8558 | -14.9005 | -14.8421 | -14.6339 | -14.7037 | 62.5123 | 0.24405 | 62.4206 | -0.028522 | 0.048236 | 60.7192 | 0.016878 | 60.502 | 45.7905 | 45.7549 | 45.7658 | 45.7211 | 45.7795 | 45.9877 | 45.9179 | 123.134 | 60.8657 | 123.0423 | 60.5931 | 60.6699 | 121.3409 | 60.6385 | 121.1236 | 62.4641 | 62.4954 | 62.3724 | 62.4038
8412.0625 | 123.3215 | -60.6262 | 62.4481 | -14.9731 | -15.0087 | -15.0023 | -15.0608 | -14.9978 | -14.7804 | -14.8411 | 62.5169 | 0.2349 | 62.4298 | -0.028522 | 0.048236 | 60.7192 | 0.003143 | 60.4928 | 45.6531 | 45.6175 | 45.6239 | 45.5654 | 45.6285 | 45.8458 | 45.7852 | 123.1431 | 60.8611 | 123.056 | 60.5977 | 60.6745 | 121.3454 | 60.6294 | 121.119 | 62.4687 | 62.5138 | 62.3816 | 62.4266
8413.0781 | 123.1979 | -60.6262 | 62.439 | -14.561 | -14.5874 | -14.5903 | -14.6213 | -14.5766 | -14.3455 | -14.4244 | 62.4986 | 0.2349 | 62.4115 | -0.023943 | 0.048236 | 60.7421 | 0.012299 | 60.5203 | 46.0652 | 46.0388 | 46.036 | 46.005 | 46.0496 | 46.2807 | 46.2018 | 123.1248 | 60.8611 | 123.0377 | 60.6023 | 60.6745 | 121.3683 | 60.6385 | 121.1465 | 62.4503 | 62.4863 | 62.3632 | 62.3992
8414.0625 | 123.317 | -60.6491 | 62.4207 | -14.3459 | -14.386 | -14.3751 | -14.429 | -14.3614 | -14.1715 | -14.223 | 62.4894 | 0.23032 | 62.3794 | -0.023943 | 0.048236 | 60.7513 | 0.016878 | 60.534 | 46.3033 | 46.2632 | 46.274 | 46.2201 | 46.2877 | 46.4776 | 46.4261 | 123.1385 | 60.8794 | 123.0285 | 60.6252 | 60.6973 | 121.4004 | 60.666 | 121.1831 | 62.4412 | 62.4725 | 62.3312 | 62.3626
8415.0781 | 123.2162 | -60.6354 | 62.4115 | -14.8312 | -14.8576 | -14.8558 | -14.896 | -14.8421 | -14.6156 | -14.6854 | 62.5123 | 0.23948 | 62.4161 | -0.028522 | 0.043657 | 60.7284 | 0.007721 | 60.4974 | 45.8042 | 45.7778 | 45.7795 | 45.7394 | 45.7933 | 46.0198 | 45.95 | 123.1477 | 60.8749 | 123.0514 | 60.6069 | 60.679 | 121.3638 | 60.6431 | 121.1328 | 62.4687 | 62.5046 | 62.3724 | 62.4083
8416.0625 | 123.3444 | -60.5804 | 62.4664 | -14.8586 | -14.8896 | -14.8925 | -14.896 | -14.8375 | -14.6568 | -14.722 | 62.5215 | 0.23032 | 62.4206 | -0.019364 | 0.057392 | 60.7284 | 0.012299 | 60.502 | 45.7218 | 45.6908 | 45.688 | 45.6845 | 45.7429 | 45.9236 | 45.8584 | 123.1019 | 60.8108 | 123.0011 | 60.5611 | 60.6378 | 121.3088 | 60.5927 | 121.0824 | 62.4641 | 62.5092 | 62.3632 | 62.4083
8417.0938 | 123.2117 | -60.6033 | 62.4664 | -15.0738 | -15.0957 | -15.1077 | -15.1569 | -15.0985 | -14.8629 | -14.9326 | 62.5352 | 0.24405 | 62.4389 | -0.023943 | 0.048236 | 60.7146 | 0.012299 | 60.4928 | 45.5295 | 45.5077 | 45.4957 | 45.4464 | 45.5049 | 45.7405 | 45.6707 | 123.1385 | 60.8474 | 123.0423 | 60.5794 | 60.6516 | 121.318 | 60.6156 | 121.0961 | 62.487 | 62.5229 | 62.3907 | 62.4267
8418.0625 | 123.317 | -60.5988 | 62.4527 | -14.7991 | -14.8209 | -14.8329 | -14.8593 | -14.8101 | -14.5882 | -14.6534 | 62.5123 | 0.24405 | 62.4252 | -0.019364 | 0.048236 | 60.7284 | 0.007721 | 60.502 | 45.7996 | 45.7778 | 45.7658 | 45.7394 | 45.7887 | 46.0106 | 45.9454 | 123.1111 | 60.8428 | 123.024 | 60.5794 | 60.647 | 121.3271 | 60.6065 | 121.1007 | 62.4641 | 62.5046 | 62.377 | 62.4175
8419.0938 | 123.2254 | -60.6354 | 62.4161 | -14.3092 | -14.3402 | -14.343 | -14.342 | -14.279 | -14.0662 | -14.1681 | 62.4757 | 0.2349 | 62.3794 | -0.028522 | 0.052814 | 60.7558 | 0.012299 | 60.534 | 46.3261 | 46.2952 | 46.2924 | 46.2934 | 46.3564 | 46.5692 | 46.4673 | 123.1111 | 60.8703 | 123.0148 | 60.6069 | 60.6882 | 121.3912 | 60.6477 | 121.1694 | 62.4229 | 62.4634 | 62.3266 | 62.3671
8420.0625 | 123.2712 | -60.6354 | 62.4115 | -14.7396 | -14.7614 | -14.7597 | -14.8044 | -14.7368 | -14.5469 | -14.5984 | 62.5077 | 0.2349 | 62.4069 | -0.023943 | 0.048236 | 60.7238 | 0.021456 | 60.5111 | 45.8958 | 45.874 | 45.8757 | 45.831 | 45.8986 | 46.0884 | 46.037 | 123.1431 | 60.8703 | 123.0423 | 60.6114 | 60.6836 | 121.3592 | 60.6568 | 121.1465 | 62.4595 | 62.4863 | 62.3587 | 62.3854
8421.0938 | 123.2071 | -60.6308 | 62.4756 | -14.9136 | -14.94 | -14.952 | -14.9555 | -14.9016 | -14.7301 | -14.7678 | 62.5123 | 0.2349 | 62.4115 | -0.033101 | 0.052814 | 60.7238 | 0.016878 | 60.4974 | 45.7172 | 45.6908 | 45.6788 | 45.6753 | 45.7292 | 45.9007 | 45.863 | 123.1431 | 60.8657 | 123.0423 | 60.5977 | 60.6836 | 121.3546 | 60.6477 | 121.1282 | 62.4595 | 62.4954 | 62.3587 | 62.3946
8422.0625 | 123.3078 | -60.6079 | 62.4435 | -15.1883 | -15.2147 | -15.2084 | -15.2531 | -15.19 | -15.0231 | -15.0471 | 62.5215 | 0.23032 | 62.4344 | -0.023943 | 0.048236 | 60.7101 | 0.012299 | 60.4791 | 45.4196 | 45.3932 | 45.3995 | 45.3548 | 45.4179 | 45.5848 | 45.5608 | 123.1294 | 60.8382 | 123.0423 | 60.584 | 60.6561 | 121.318 | 60.6202 | 121.087 | 62.4732 | 62.5092 | 62.3861 | 62.4221
8423.0938 | 123.2162 | -60.6125 | 62.4802 | -14.8083 | -14.8347 | -14.8375 | -14.8548 | -14.7917 | -14.5973 | -14.6717 | 62.5077 | 0.2349 | 62.4069 | -0.028522 | 0.043657 | 60.7284 | 0.003143 | 60.5111 | 45.8042 | 45.7778 | 45.775 | 45.7577 | 45.8207 | 46.0152 | 45.9408 | 123.1202 | 60.8474 | 123.0194 | 60.584 | 60.6561 | 121.3409 | 60.6156 | 121.1236 | 62.4641 | 62.5046 | 62.3632 | 62.4038
8424.0625 | 123.349 | -60.6125 | 62.4023 | -14.5336 | -14.5645 | -14.5674 | -14.5617 | -14.4988 | -14.3592 | -14.397 | 62.494 | 0.23032 | 62.3932 | -0.028522 | 0.048236 | 60.733 | 0.007721 | 60.5203 | 46.0789 | 46.048 | 46.0451 | 46.0507 | 46.1137 | 46.2533 | 46.2155 | 123.1065 | 60.8428 | 123.0057 | 60.584 | 60.6607 | 121.3454 | 60.6202 | 121.1328 | 62.4458 | 62.4863 | 62.3449 | 62.3854
8425.0781 | 123.3307 | -60.6171 | 62.4023 | -14.2451 | -14.2715 | -14.2835 | -14.2412 | -14.1829 | -14.0433 | -14.1086 | 62.4711 | 0.23948 | 62.3794 | -0.028522 | 0.052814 | 60.7604 | 0.012299 | 60.5294 | 46.3719 | 46.3456 | 46.3336 | 46.3758 | 46.4342 | 46.5737 | 46.5085 | 123.0882 | 60.8565 | 122.9965 | 60.5885 | 60.6699 | 121.3775 | 60.6294 | 121.1465 | 62.4183 | 62.4588 | 62.3266 | 62.3671
8426.0625 | 123.3032 | -60.585 | 62.4435 | -14.6938 | -14.7248 | -14.723 | -14.6991 | -14.6407 | -14.5012 | -14.5572 | 62.5077 | 0.24405 | 62.4115 | -0.019364 | 0.052814 | 60.7284 | 0.021456 | 60.5157 | 45.8912 | 45.8602 | 45.862 | 45.8859 | 45.9444 | 46.0839 | 46.0278 | 123.0928 | 60.8291 | 122.9965 | 60.5657 | 60.6378 | 121.3134 | 60.6065 | 121.1007 | 62.4549 | 62.4863 | 62.3587 | 62.39
8427.0781 | 123.2803 | -60.6033 | 62.4207 | -14.9502 | -14.9858 | -14.9886 | -14.9921 | -14.9428 | -14.753 | -14.8227 | 62.5215 | 0.2349 | 62.4252 | -0.023943 | 0.048236 | 60.7238 | 0.016878 | 60.4882 | 45.6531 | 45.6176 | 45.6147 | 45.6112 | 45.6605 | 45.8504 | 45.7806 | 123.1248 | 60.8382 | 123.0285 | 60.5794 | 60.6516 | 121.3271 | 60.6202 | 121.0916 | 62.4732 | 62.5046 | 62.377 | 62.4083
8428.0625 | 123.2849 | -60.585 | 62.4298 | -15.5088 | -15.5215 | -15.5426 | -15.5278 | -15.4739 | -15.307 | -15.3584 | 62.5535 | 0.23948 | 62.4481 | -0.033101 | 0.052814 | 60.6872 | 0.012299 | 60.4562 | 45.0763 | 45.0635 | 45.0424 | 45.0572 | 45.1112 | 45.2781 | 45.2266 | 123.1385 | 60.8245 | 123.0331 | 60.5519 | 60.6378 | 121.2722 | 60.5973 | 121.0412 | 62.5007 | 62.5412 | 62.3953 | 62.4358
8429.0938 | 123.3124 | -60.553 | 62.471 | -16.31 | -16.3228 | -16.3622 | -16.3702 | -16.307 | -16.0532 | -16.1687 | 62.581 | 0.22574 | 62.4847 | -0.023943 | 0.043657 | 60.6368 | 0.016878 | 60.415 | 44.243 | 44.2302 | 44.1908 | 44.1827 | 44.2459 | 44.4997 | 44.3842 | 123.134 | 60.7787 | 123.0377 | 60.529 | 60.5966 | 121.1898 | 60.5699 | 120.968 | 62.5373 | 62.5641 | 62.4411 | 62.4679
8430.0625 | 123.2895 | -60.5438 | 62.4573 | -15.756 | -15.7733 | -15.8036 | -15.775 | -15.7256 | -15.545 | -15.6056 | 62.5627 | 0.23032 | 62.4573 | -0.023943 | 0.052814 | 60.6643 | 0.007721 | 60.447 | 44.7878 | 44.7705 | 44.7402 | 44.7688 | 44.8182 | 44.9988 | 44.9382 | 123.1065 | 60.7741 | 123.0011 | 60.5199 | 60.5966 | 121.2081 | 60.5515 | 120.9908 | 62.5099 | 62.555 | 62.4044 | 62.4495
8431.1094 | 123.3032 | -60.6216 | 62.4069 | -15.3348 | -15.375 | -15.3686 | -15.3721 | -15.3045 | -15.1376 | -15.2027 | 62.5306 | 0.2349 | 62.4252 | -0.028522 | 0.043657 | 60.6963 | 0.016878 | 60.4699 | 45.2869 | 45.2467 | 45.253 | 45.2495 | 45.3172 | 45.4841 | 45.4189 | 123.1523 | 60.8565 | 123.0469 | 60.5931 | 60.6653 | 121.318 | 60.6385 | 121.0916 | 62.487 | 62.5138 | 62.3816 | 62.4083
8432.0625 | 123.2895 | -60.5255 | 62.4939 | -15.5225 | -15.5444 | -15.5564 | -15.5782 | -15.5242 | -15.2978 | -15.3721 | 62.5489 | 0.23032 | 62.4435 | -0.028522 | 0.043657 | 60.6872 | 0.016878 | 60.4608 | 45.003 | 44.9811 | 44.9692 | 44.9473 | 45.0013 | 45.2277 | 45.1534 | 123.0745 | 60.7558 | 122.969 | 60.497 | 60.5692 | 121.2127 | 60.5424 | 120.9863 | 62.5053 | 62.5321 | 62.3999 | 62.4266
8433.0781 | 123.1979 | -60.6125 | 62.4481 | -15.0738 | -15.1186 | -15.1122 | -15.1157 | -15.039 | -14.8354 | -14.9372 | 62.5215 | 0.2349 | 62.4298 | -0.023943 | 0.043657 | 60.7146 | 0.007721 | 60.4837 | 45.5387 | 45.4939 | 45.5003 | 45.4968 | 45.5735 | 45.7771 | 45.6753 | 123.134 | 60.8474 | 123.0423 | 60.5885 | 60.6561 | 121.3271 | 60.6202 | 121.0961 | 62.4778 | 62.5138 | 62.3861 | 62.4221
8434.0625 | 123.2758 | -60.5347 | 62.5076 | -16.2917 | -16.3136 | -16.3393 | -16.3336 | -16.2658 | -16.0715 | -16.155 | 62.5947 | 0.23032 | 62.4939 | -0.023943 | 0.048236 | 60.6414 | 0.016878 | 60.415 | 44.243 | 44.221 | 44.1954 | 44.2011 | 44.2688 | 44.4631 | 44.3797 | 123.1294 | 60.765 | 123.0286 | 60.5107 | 60.5829 | 121.1761 | 60.5515 | 120.9496 | 62.5465 | 62.5779 | 62.4457 | 62.477
8435.0781 | 123.2849 | -60.5438 | 62.4939 | -16.2001 | -16.2221 | -16.2477 | -16.1734 | -16.1148 | -15.9754 | -16.0589 | 62.5902 | 0.23948 | 62.4893 | -0.028522 | 0.048236 | 60.646 | 0.007721 | 60.4287 | 44.3437 | 44.3218 | 44.2961 | 44.3705 | 44.4291 | 44.5684 | 44.485 | 123.134 | 60.7833 | 123.0331 | 60.5153 | 60.5921 | 121.1898 | 60.5515 | 120.9725 | 62.5419 | 62.5824 | 62.4411 | 62.4816
8436.0625 | 123.3398 | -60.5209 | 62.5076 | -15.4905 | -15.5123 | -15.5197 | -15.5324 | -15.4739 | -15.2566 | -15.3447 | 62.5444 | 0.2349 | 62.4573 | -0.023943 | 0.052814 | 60.6872 | 0.007721 | 60.4699 | 45.0305 | 45.0086 | 45.0012 | 44.9886 | 45.0471 | 45.2643 | 45.1763 | 123.0653 | 60.7558 | 122.9782 | 60.497 | 60.5737 | 121.2081 | 60.5287 | 120.9909 | 62.4916 | 62.5366 | 62.4044 | 62.4495
8437.0781 | 123.2346 | -60.6216 | 62.4481 | -15.1196 | -15.1369 | -15.1489 | -15.1753 | -15.1214 | -14.9086 | -14.9784 | 62.5306 | 0.2349 | 62.4206 | -0.028522 | 0.048236 | 60.7146 | 0.007721 | 60.4837 | 45.502 | 45.4848 | 45.4728 | 45.4464 | 45.5003 | 45.713 | 45.6432 | 123.1523 | 60.8565 | 123.0423 | 60.5931 | 60.6699 | 121.3363 | 60.6294 | 121.1053 | 62.4824 | 62.5229 | 62.3724 | 62.4129
8438.0625 | 123.3353 | -60.5896 | 62.4481 | -15.2615 | -15.2926 | -15.2954 | -15.3263 | -15.2587 | -15.0414 | -15.1203 | 62.5352 | 0.22574 | 62.4344 | -0.028522 | 0.048236 | 60.6963 | 0.007721 | 60.4791 | 45.3281 | 45.297 | 45.2942 | 45.2633 | 45.3309 | 45.5482 | 45.4693 | 123.1248 | 60.8153 | 123.024 | 60.5611 | 60.6378 | 121.2859 | 60.5973 | 121.0687 | 62.487 | 62.5275 | 62.3861 | 62.4267
8439.0938 | 123.2529 | -60.6583 | 62.4069 | -14.6251 | -14.6515 | -14.6544 | -14.635 | -14.5628 | -14.4004 | -14.4931 | 62.4894 | 0.2349 | 62.3932 | -0.028522 | 0.052814 | 60.7375 | 0.016878 | 60.5157 | 46.0331 | 46.0067 | 46.0039 | 46.0233 | 46.0954 | 46.2578 | 46.1651 | 123.1477 | 60.8932 | 123.0514 | 60.6297 | 60.7111 | 121.3958 | 60.6751 | 121.174 | 62.4366 | 62.4725 | 62.3404 | 62.3763
8440.0625 | 123.3261 | -60.6125 | 62.4023 | -14.529 | -14.5462 | -14.5765 | -14.5526 | -14.5033 | -14.2951 | -14.3878 | 62.4848 | 0.22574 | 62.3932 | -0.023943 | 0.048236 | 60.7421 | 0.003143 | 60.5249 | 46.0835 | 46.0663 | 46.036 | 46.0599 | 46.1092 | 46.3174 | 46.2247 | 123.0973 | 60.8382 | 123.0057 | 60.5885 | 60.6607 | 121.3546 | 60.6156 | 121.1373 | 62.4366 | 62.4817 | 62.3449 | 62.39
8441.1094 | 123.1201 | -60.672 | 62.3749 | -15.2203 | -15.2468 | -15.2816 | -15.2485 | -15.1992 | -15.0231 | -15.0883 | 62.5352 | 0.23948 | 62.4389 | -0.023943 | 0.039079 | 60.7055 | 0.007721 | 60.4791 | 45.4517 | 45.4252 | 45.3904 | 45.4235 | 45.4728 | 45.6489 | 45.5837 | 123.2072 | 60.9115 | 123.1109 | 60.6481 | 60.7111 | 121.3775 | 60.6797 | 121.1511 | 62.4961 | 62.5275 | 62.3999 | 62.4312
8442.0625 | 123.2666 | -60.5713 | 62.4619 | -15.4355 | -15.4528 | -15.4923 | -15.4408 | -15.396 | -15.2383 | -15.2943 | 62.5398 | 0.2349 | 62.4481 | -0.023943 | 0.052814 | 60.6872 | 0.007721 | 60.4745 | 45.1358 | 45.1185 | 45.079 | 45.1305 | 45.1753 | 45.333 | 45.277 | 123.1111 | 60.8062 | 123.0194 | 60.5473 | 60.6241 | 121.2585 | 60.579 | 121.0458 | 62.487 | 62.5321 | 62.3953 | 62.4404
8443.0938 | 123.3398 | -60.5301 | 62.4573 | -15.9117 | -15.9473 | -15.973 | -15.9032 | -15.8493 | -15.687 | -15.7796 | 62.5764 | 0.2349 | 62.4756 | -0.019364 | 0.052814 | 60.6689 | 0.012299 | 60.4424 | 44.6184 | 44.5828 | 44.5571 | 44.6269 | 44.6808 | 44.8431 | 44.7505 | 123.1065 | 60.765 | 123.0057 | 60.5107 | 60.5829 | 121.1989 | 60.5424 | 120.9725 | 62.5236 | 62.5641 | 62.4228 | 62.4633
8444.0625 | 123.2986 | -60.4843 | 62.5351 | -16.6396 | -16.6616 | -16.6964 | -16.6083 | -16.5497 | -16.3737 | -16.4846 | 62.613 | 0.23948 | 62.5259 | -0.033101 | 0.043657 | 60.6277 | 0.012299 | 60.3967 | 43.8447 | 43.8227 | 43.7879 | 43.876 | 43.9346 | 44.1106 | 43.9997 | 123.0974 | 60.7238 | 123.0102 | 60.4512 | 60.528 | 121.112 | 60.4966 | 120.881 | 62.5694 | 62.6007 | 62.4823 | 62.5136
8445.0938 | 123.2666 | -60.5576 | 62.5214 | -15.8476 | -15.8832 | -15.9135 | -15.7247 | -15.6661 | -15.5862 | -15.7109 | 62.5627 | 0.2349 | 62.4664 | -0.019364 | 0.052814 | 60.6643 | 0.012299 | 60.4516 | 44.71 | 44.6743 | 44.6441 | 44.8329 | 44.8914 | 44.9713 | 44.8466 | 123.1202 | 60.7925 | 123.024 | 60.5382 | 60.6104 | 121.2218 | 60.5699 | 121.0092 | 62.5099 | 62.5504 | 62.4136 | 62.4541
8446.0625 | 123.3032 | -60.5392 | 62.5122 | -15.8109 | -15.842 | -15.8677 | -15.6331 | -15.5837 | -15.4718 | -15.6697 | 62.5627 | 0.2349 | 62.4573 | -0.014785 | 0.043657 | 60.6689 | 0.016878 | 60.4562 | 44.7283 | 44.6972 | 44.6715 | 44.9061 | 44.9555 | 45.0675 | 44.8695 | 123.1019 | 60.7741 | 122.9965 | 60.5245 | 60.5829 | 121.2081 | 60.5561 | 120.9954 | 62.519 | 62.5458 | 62.4136 | 62.4404
8447.0781 | 123.3307 | -60.4477 | 62.5397 | -16.8823 | -16.8951 | -16.9849 | -16.8601 | -16.8152 | -16.6393 | -16.7318 | 62.6222 | 0.22574 | 62.5214 | -0.019364 | 0.048236 | 60.6093 | 0.016878 | 60.3829 | 43.5654 | 43.5525 | 43.4628 | 43.5875 | 43.6325 | 43.8084 | 43.7158 | 123.0699 | 60.6734 | 122.9691 | 60.4283 | 60.4959 | 121.057 | 60.4646 | 120.8306 | 62.574 | 62.6053 | 62.4731 | 62.5045
8448.0625 | 123.262 | -60.5118 | 62.5168 | -16.4428 | -16.4831 | -16.5041 | -16.3199 | -16.2475 | -16.186 | -16.3061 | 62.5947 | 0.23032 | 62.4893 | -0.023943 | 0.043657 | 60.6414 | 0.016878 | 60.4104 | 44.069 | 44.0287 | 44.0077 | 44.1919 | 44.2642 | 44.3258 | 44.2057 | 123.1065 | 60.7421 | 123.0011 | 60.4878 | 60.5554 | 121.1532 | 60.5287 | 120.9222 | 62.5511 | 62.5779 | 62.4457 | 62.4724
8449.0938 | 123.23 | -60.5255 | 62.5305 | -15.9117 | -15.9428 | -15.973 | -15.743 | -15.6707 | -15.6458 | -15.7704 | 62.5627 | 0.23948 | 62.4802 | -0.019364 | 0.052814 | 60.6689 | 0.012299 | 60.4379 | 44.6138 | 44.5828 | 44.5525 | 44.7825 | 44.8548 | 44.8798 | 44.7551 | 123.0882 | 60.765 | 123.0057 | 60.5061 | 60.5783 | 121.1944 | 60.5378 | 120.9634 | 62.5099 | 62.5504 | 62.4273 | 62.4679
8450.0625 | 123.2529 | -60.5438 | 62.5351 | -15.9574 | -15.9885 | -16.0234 | -15.8254 | -15.7623 | -15.7236 | -15.8162 | 62.5764 | 0.24405 | 62.4847 | -0.019364 | 0.052814 | 60.6597 | 0.012299 | 60.4424 | 44.5864 | 44.5553 | 44.5205 | 44.7184 | 44.7816 | 44.8202 | 44.7276 | 123.1202 | 60.7879 | 123.0286 | 60.5245 | 60.5966 | 121.2035 | 60.5561 | 120.9863 | 62.5236 | 62.5641 | 62.4319 | 62.4724
8451.0938 | 123.2391 | -60.5072 | 62.5854 | -17.0608 | -17.0783 | -17.1406 | -17.057 | -17.0075 | -16.8316 | -16.9058 | 62.6359 | 0.23032 | 62.5305 | -0.023943 | 0.039079 | 60.6002 | 0.016878 | 60.3738 | 43.4464 | 43.4289 | 43.3666 | 43.4502 | 43.4997 | 43.6756 | 43.6014 | 123.1431 | 60.7375 | 123.0377 | 60.4833 | 60.5463 | 121.1074 | 60.5241 | 120.881 | 62.5969 | 62.6191 | 62.4914 | 62.5136
8452.0625 | 123.3078 | -60.4935 | 62.5259 | -17.1341 | -17.1699 | -17.2092 | -17.1303 | -17.0716 | -16.8728 | -16.9882 | 62.6268 | 0.2349 | 62.5305 | -0.019364 | 0.052814 | 60.5956 | 0.012299 | 60.3784 | 43.3594 | 43.3236 | 43.2842 | 43.3632 | 43.4219 | 43.6207 | 43.5052 | 123.1203 | 60.7284 | 123.024 | 60.4741 | 60.5463 | 121.0891 | 60.5058 | 120.8718 | 62.574 | 62.6145 | 62.4777 | 62.5182
8453.0938 | 123.2666 | -60.498 | 62.5488 | -17.0654 | -17.092 | -17.1406 | -17.0662 | -17.0029 | -16.8132 | -16.9241 | 62.6359 | 0.23032 | 62.5305 | -0.023943 | 0.052814 | 60.5956 | 0.007721 | 60.3829 | 43.4326 | 43.406 | 43.3575 | 43.4319 | 43.4951 | 43.6848 | 43.5739 | 123.134 | 60.7284 | 123.0286 | 60.4741 | 60.5509 | 121.0937 | 60.5058 | 120.881 | 62.5831 | 62.6282 | 62.4777 | 62.5228
8454.0625 | 123.3261 | -60.5759 | 62.4756 | -15.5454 | -15.5719 | -15.6067 | -15.3309 | -15.2633 | -15.2474 | -15.4042 | 62.5398 | 0.23032 | 62.4435 | -0.028522 | 0.048236 | 60.6872 | 0.016878 | 60.4653 | 45.0305 | 45.004 | 44.9691 | 45.2449 | 45.3126 | 45.3284 | 45.1717 | 123.1157 | 60.8062 | 123.0194 | 60.5473 | 60.6241 | 121.263 | 60.5927 | 121.0412 | 62.4916 | 62.5229 | 62.3953 | 62.4266
8455.0781 | 123.317 | -60.4431 | 62.6175 | -16.7632 | -16.7807 | -16.8338 | -16.645 | -16.6 | -16.4424 | -16.6037 | 62.613 | 0.23032 | 62.5168 | -0.023943 | 0.048236 | 60.6139 | 0.012299 | 60.3921 | 43.6799 | 43.6624 | 43.6093 | 43.7982 | 43.8431 | 44.0007 | 43.8395 | 123.0562 | 60.6734 | 122.9599 | 60.4192 | 60.4914 | 121.057 | 60.4554 | 120.8352 | 62.5648 | 62.6007 | 62.4685 | 62.5045
8456.0625 | 123.2529 | -60.5347 | 62.558 | -16.2138 | -16.2724 | -16.2706 | -16.1047 | -16.0324 | -15.893 | -16.1001 | 62.5856 | 0.24405 | 62.4893 | -0.028522 | 0.057392 | 60.6505 | 0.012299 | 60.4287 | 44.3208 | 44.2622 | 44.2641 | 44.43 | 44.5023 | 44.6417 | 44.4346 | 123.1202 | 60.7787 | 123.024 | 60.5061 | 60.5921 | 121.1852 | 60.547 | 120.9634 | 62.5282 | 62.5733 | 62.4319 | 62.477
8457.0938 | 123.3124 | -60.4843 | 62.5854 | -17.3539 | -17.3897 | -17.4427 | -17.35 | -17.273 | -16.8361 | -17.2126 | 62.6451 | 0.23948 | 62.558 | -0.028522 | 0.043657 | 60.5819 | 0.012299 | 60.3692 | 43.1305 | 43.0947 | 43.0416 | 43.1343 | 43.2113 | 43.6482 | 43.2718 | 123.1294 | 60.7238 | 123.0423 | 60.4558 | 60.528 | 121.0662 | 60.4966 | 120.8535 | 62.6014 | 62.6328 | 62.5143 | 62.5457
8458.0625 | 123.2986 | -60.5621 | 62.4893 | -15.8155 | -15.842 | -15.8814 | -15.6331 | -15.57 | -15.4901 | -15.6789 | 62.5581 | 0.2349 | 62.471 | -0.023943 | 0.048236 | 60.678 | 0.012299 | 60.447 | 44.7466 | 44.7201 | 44.6807 | 44.929 | 44.9921 | 45.072 | 44.8833 | 123.1202 | 60.797 | 123.0331 | 60.5382 | 60.6104 | 121.2401 | 60.5744 | 121.0092 | 62.5099 | 62.5458 | 62.4228 | 62.4587
8459.1094 | 123.3536 | -60.466 | 62.5488 | -16.6946 | -16.744 | -16.7559 | -16.6495 | -16.5726 | -16.3783 | -16.5716 | 62.6085 | 0.2349 | 62.5168 | -0.028522 | 0.048236 | 60.6231 | 0.003143 | 60.4012 | 43.7714 | 43.722 | 43.7101 | 43.8165 | 43.8934 | 44.0877 | 43.8944 | 123.0745 | 60.7009 | 122.9828 | 60.4375 | 60.5142 | 121.0891 | 60.4691 | 120.8672 | 62.5602 | 62.6053 | 62.4685 | 62.5136
8460.0625 | 123.3353 | -60.498 | 62.5122 | -16.8594 | -16.8997 | -16.9208 | -16.7777 | -16.7053 | -16.5065 | -16.7227 | 62.6222 | 0.23032 | 62.5168 | -0.019364 | 0.052814 | 60.6093 | 0.007721 | 60.3921 | 43.6387 | 43.5983 | 43.5773 | 43.7203 | 43.7927 | 43.9916 | 43.7754 | 123.1202 | 60.7284 | 123.0148 | 60.4787 | 60.5509 | 121.1074 | 60.5058 | 120.8901 | 62.5694 | 62.6145 | 62.464 | 62.5091
8461.0781 | 123.3353 | -60.4523 | 62.5488 | -16.3146 | -16.3411 | -16.3851 | -16.1505 | -16.0873 | -15.9113 | -16.187 | 62.5947 | 0.2349 | 62.4847 | -0.019364 | 0.043657 | 60.6414 | 0.016878 | 60.4196 | 44.1377 | 44.1112 | 44.0672 | 44.3018 | 44.365 | 44.541 | 44.2652 | 123.047 | 60.6872 | 122.937 | 60.4329 | 60.4959 | 121.0937 | 60.4691 | 120.8718 | 62.5511 | 62.5779 | 62.4411 | 62.4679
8462.0625 | 123.2941 | -60.4294 | 62.5763 | -17.569 | -17.6003 | -17.6488 | -17.5561 | -17.4882 | -17.1841 | -17.4231 | 62.6543 | 0.2349 | 62.5488 | -0.019364 | 0.043657 | 60.5773 | 0.016878 | 60.3463 | 42.8603 | 42.8291 | 42.7806 | 42.8733 | 42.9412 | 43.2453 | 43.0062 | 123.0836 | 60.6643 | 122.9782 | 60.41 | 60.473 | 121.0067 | 60.4463 | 120.7757 | 62.6106 | 62.6374 | 62.5052 | 62.532
8463.0938 | 123.2803 | -60.434 | 62.5854 | -17.0792 | -17.0966 | -17.168 | -16.9609 | -16.9159 | -16.6622 | -16.9333 | 62.6314 | 0.23032 | 62.5351 | -0.033101 | 0.043657 | 60.6048 | 0.016878 | 60.3784 | 43.3548 | 43.3373 | 43.2659 | 43.4731 | 43.518 | 43.7718 | 43.5007 | 123.0653 | 60.6643 | 122.9691 | 60.4009 | 60.4776 | 121.0387 | 60.4508 | 120.8123 | 62.5877 | 62.6145 | 62.4914 | 62.5182
8464.0625 | 123.2941 | -60.5576 | 62.5122 | -15.7285 | -15.7642 | -15.8082 | -15.5278 | -15.4647 | -15.3436 | -15.5965 | 62.5535 | 0.23948 | 62.4573 | -0.023943 | 0.043657 | 60.6826 | 0.012299 | 60.4516 | 44.829 | 44.7934 | 44.7494 | 45.0298 | 45.0929 | 45.214 | 44.9611 | 123.1111 | 60.797 | 123.0148 | 60.5336 | 60.6012 | 121.2401 | 60.5699 | 121.0092 | 62.5099 | 62.5412 | 62.4136 | 62.445
8465.0781 | 123.3353 | -60.4935 | 62.558 | -17.2348 | -17.2752 | -17.3283 | -17.2539 | -17.1997 | -16.8865 | -17.1073 | 62.6451 | 0.23032 | 62.5488 | -0.028522 | 0.052814 | 60.591 | 0.016878 | 60.3646 | 43.2587 | 43.2183 | 43.1652 | 43.2396 | 43.2937 | 43.607 | 43.3862 | 123.1386 | 60.7238 | 123.0423 | 60.4649 | 60.5463 | 121.0845 | 60.5103 | 120.8581 | 62.5923 | 62.6282 | 62.496 | 62.532
8466.0625 | 123.3215 | -60.4614 | 62.5854 | -17.3172 | -17.3484 | -17.4061 | -17.3638 | -17.3005 | -16.9506 | -17.1759 | 62.6497 | 0.23032 | 62.5534 | -0.019364 | 0.048236 | 60.5819 | 0.016878 | 60.36 | 43.1442 | 43.113 | 43.0553 | 43.0976 | 43.161 | 43.5108 | 43.2855 | 123.1111 | 60.6917 | 123.0148 | 60.4421 | 60.5097 | 121.0433 | 60.4783 | 120.8215 | 62.6014 | 62.6328 | 62.5052 | 62.5365
8467.1094 | 123.262 | -60.466 | 62.5946 | -17.2989 | -17.3393 | -17.3832 | -17.3088 | -17.2455 | -16.7629 | -17.1576 | 62.6497 | 0.22574 | 62.5488 | -0.028522 | 0.052814 | 60.591 | 0.012299 | 60.36 | 43.1671 | 43.1267 | 43.0828 | 43.1572 | 43.2205 | 43.7031 | 43.3084 | 123.1157 | 60.6917 | 123.0148 | 60.4375 | 60.5188 | 121.057 | 60.4783 | 120.826 | 62.5969 | 62.6374 | 62.496 | 62.5365
8468.0625 | 123.3307 | -60.4294 | 62.5717 | -17.2348 | -17.2752 | -17.3283 | -17.2402 | -17.1723 | -16.8087 | -17.0981 | 62.6314 | 0.23032 | 62.5488 | -0.028522 | 0.048236 | 60.5865 | 0.012299 | 60.36 | 43.1946 | 43.1542 | 43.1011 | 43.1892 | 43.2571 | 43.6207 | 43.3313 | 123.0607 | 60.6597 | 122.9782 | 60.4009 | 60.4776 | 121.0158 | 60.4417 | 120.7894 | 62.5831 | 62.6191 | 62.5006 | 62.5365
8469.0781 | 123.3536 | -60.4614 | 62.5305 | -17.4134 | -17.4492 | -17.4977 | -17.3088 | -17.2364 | -16.5431 | -17.2538 | 62.6405 | 0.23032 | 62.5442 | -0.028522 | 0.048236 | 60.5865 | 0.012299 | 60.3555 | 43.0481 | 43.0122 | 42.9637 | 43.1526 | 43.2251 | 43.9183 | 43.2077 | 123.1019 | 60.6917 | 123.0057 | 60.4329 | 60.5097 | 121.0479 | 60.4737 | 120.8169 | 62.5923 | 62.6282 | 62.496 | 62.532
8470.0625 | 123.3627 | -60.5026 | 62.5442 | -16.8869 | -16.9318 | -16.9711 | -16.8418 | -16.7648 | -16.3463 | -16.741 | 62.6085 | 0.2349 | 62.5076 | -0.028522 | 0.043657 | 60.6139 | 0.016878 | 60.3829 | 43.6158 | 43.5708 | 43.5315 | 43.6608 | 43.7378 | 44.1564 | 43.7616 | 123.1111 | 60.7375 | 123.0102 | 60.4741 | 60.5463 | 121.1165 | 60.5195 | 120.8856 | 62.5648 | 62.5916 | 62.464 | 62.4907
8471.0938 | 123.3032 | -60.4843 | 62.5351 | -16.951 | -16.9867 | -17.0444 | -16.8739 | -16.8106 | -16.2959 | -16.7868 | 62.6222 | 0.23032 | 62.5168 | -0.019364 | 0.043657 | 60.6048 | 0.012299 | 60.3875 | 43.5334 | 43.4976 | 43.4399 | 43.6104 | 43.6737 | 44.1884 | 43.6975 | 123.1065 | 60.7146 | 123.0011 | 60.4649 | 60.528 | 121.0891 | 60.4966 | 120.8718 | 62.5785 | 62.6099 | 62.4731 | 62.5045
8472.0625 | 123.2666 | -60.5988 | 62.4756 | -15.3027 | -15.3521 | -15.3732 | -15.0928 | -15.0115 | -14.8491 | -15.1753 | 62.5352 | 0.2349 | 62.4298 | -0.028522 | 0.052814 | 60.6963 | 0.012299 | 60.4791 | 45.296 | 45.2467 | 45.2255 | 45.5059 | 45.5873 | 45.7496 | 45.4235 | 123.134 | 60.8337 | 123.0285 | 60.5702 | 60.6516 | 121.2951 | 60.6111 | 121.0778 | 62.4824 | 62.5229 | 62.377 | 62.4175
8473.0938 | 123.3353 | -60.6125 | 62.3978 | -14.8037 | -14.8393 | -14.897 | -14.5068 | -14.453 | -14.2265 | -14.6579 | 62.4986 | 0.23948 | 62.4115 | -0.028522 | 0.039079 | 60.733 | 0.016878 | 60.5065 | 45.8088 | 45.7732 | 45.7155 | 46.1057 | 46.1595 | 46.386 | 45.9546 | 123.1111 | 60.852 | 123.024 | 60.584 | 60.6516 | 121.3454 | 60.6294 | 121.119 | 62.4595 | 62.4817 | 62.3724 | 62.3946
8474.0625 | 123.3582 | -60.5438 | 62.4619 | -15.3394 | -15.3612 | -15.4373 | -15.0287 | -14.9703 | -14.7392 | -15.1844 | 62.5215 | 0.2349 | 62.4389 | -0.019364 | 0.048236 | 60.7009 | 0.012299 | 60.4837 | 45.2045 | 45.1826 | 45.1065 | 45.5151 | 45.5735 | 45.8046 | 45.3594 | 123.0653 | 60.7787 | 122.9828 | 60.5245 | 60.5921 | 121.2447 | 60.5561 | 121.0275 | 62.4732 | 62.5092 | 62.3907 | 62.4267
8475.1094 | 123.23 | -60.5988 | 62.5214 | -15.4767 | -15.5215 | -15.5884 | -15.221 | -15.1534 | -15.0643 | -15.3355 | 62.5398 | 0.23948 | 62.4481 | -0.023943 | 0.052814 | 60.6963 | 0.003143 | 60.4699 | 45.122 | 45.0773 | 45.0103 | 45.3777 | 45.4454 | 45.5345 | 45.2633 | 123.1385 | 60.8382 | 123.0469 | 60.5748 | 60.6516 | 121.2951 | 60.6019 | 121.0687 | 62.487 | 62.5366 | 62.3953 | 62.445
8476.0625 | 123.3444 | -60.553 | 62.471 | -15.5591 | -15.5902 | -15.6617 | -15.2806 | -15.2175 | -15.1284 | -15.4088 | 62.5444 | 0.23948 | 62.4481 | -0.028522 | 0.052814 | 60.6963 | 0.012299 | 60.4653 | 44.9939 | 44.9628 | 44.8913 | 45.2724 | 45.3355 | 45.4246 | 45.1442 | 123.0973 | 60.7925 | 123.0011 | 60.5245 | 60.6058 | 121.2493 | 60.5653 | 121.0183 | 62.4916 | 62.5321 | 62.3953 | 62.4358
8477.0938 | 123.3307 | -60.6216 | 62.3795 | -14.6892 | -14.7156 | -14.778 | -14.4106 | -14.3339 | -14.2585 | -14.5435 | 62.4848 | 0.2349 | 62.3794 | -0.033101 | 0.048236 | 60.733 | 0.007721 | 60.5111 | 45.9324 | 45.906 | 45.8436 | 46.211 | 46.2877 | 46.3631 | 46.0782 | 123.1065 | 60.8565 | 123.0011 | 60.5885 | 60.6699 | 121.3546 | 60.6294 | 121.1328 | 62.4366 | 62.4771 | 62.3312 | 62.3717
8478.0625 | 123.3261 | -60.5667 | 62.4664 | -15.1379 | -15.1827 | -15.245 | -14.8319 | -14.7734 | -14.6431 | -15.0013 | 62.5215 | 0.23948 | 62.4252 | -0.03768 | 0.057392 | 60.7101 | 0.012299 | 60.4882 | 45.4288 | 45.384 | 45.3217 | 45.7348 | 45.7933 | 45.9236 | 45.5654 | 123.0882 | 60.8062 | 122.9919 | 60.529 | 60.6241 | 121.2768 | 60.579 | 121.0549 | 62.4641 | 62.5092 | 62.3678 | 62.4129
8479.0625 | 123.2712 | -60.5942 | 62.4435 | -15.1059 | -15.146 | -15.2175 | -14.7998 | -14.7368 | -14.6294 | -14.9601 | 62.5169 | 0.2349 | 62.4206 | -0.028522 | 0.043657 | 60.7146 | 0.012299 | 60.4882 | 45.4883 | 45.4481 | 45.3766 | 45.7944 | 45.8574 | 45.9648 | 45.6341 | 123.1111 | 60.8291 | 123.0148 | 60.5657 | 60.6378 | 121.3088 | 60.6065 | 121.0824 | 62.4732 | 62.5046 | 62.377 | 62.4083
8480.1094 | 123.2986 | -60.5484 | 62.4207 | -16.0078 | -16.0801 | -16.0966 | -16.0269 | -15.9271 | -15.6046 | -15.8986 | 62.581 | 0.2349 | 62.4756 | -0.019364 | 0.043657 | 60.6597 | 0.007721 | 60.4333 | 44.5406 | 44.4683 | 44.4518 | 44.5215 | 44.6213 | 44.9438 | 44.6498 | 123.1294 | 60.7833 | 123.024 | 60.529 | 60.5921 | 121.2081 | 60.5561 | 120.9817 | 62.5373 | 62.5733 | 62.4319 | 62.4679
8481.0625 | 123.317 | -60.466 | 62.5442 | -16.7404 | -16.7761 | -16.8338 | -16.7915 | -16.7145 | -16.2822 | -16.5991 | 62.6039 | 0.23948 | 62.5214 | -0.028522 | 0.048236 | 60.6139 | 0.007721 | 60.3921 | 43.7257 | 43.6899 | 43.6322 | 43.6745 | 43.7515 | 44.1838 | 43.8669 | 123.0699 | 60.7055 | 122.9874 | 60.4375 | 60.5142 | 121.0799 | 60.4737 | 120.8581 | 62.5557 | 62.5962 | 62.4731 | 62.5136
8482.0938 | 123.2941 | -60.4935 | 62.5259 | -16.2688 | -16.2953 | -16.3851 | -16.297 | -16.2292 | -15.687 | -16.1229 | 62.5856 | 0.22574 | 62.4847 | -0.023943 | 0.048236 | 60.6414 | 0.012299 | 60.4241 | 44.2247 | 44.1981 | 44.1084 | 44.1965 | 44.2642 | 44.8065 | 44.3705 | 123.079 | 60.7192 | 122.9782 | 60.4695 | 60.5417 | 121.1349 | 60.5058 | 120.9176 | 62.5373 | 62.5733 | 62.4365 | 62.4724
8483.0625 | 123.3353 | -60.5118 | 62.5031 | -15.6553 | -15.7047 | -15.7395 | -15.6697 | -15.5929 | -14.9407 | -15.5141 | 62.5489 | 0.23032 | 62.4573 | -0.023943 | 0.048236 | 60.6872 | 0.007721 | 60.4608 | 44.8565 | 44.8071 | 44.7723 | 44.842 | 44.9189 | 45.5711 | 44.9977 | 123.0607 | 60.7421 | 122.969 | 60.4878 | 60.56 | 121.199 | 60.5195 | 120.9725 | 62.5007 | 62.5412 | 62.409 | 62.4495
8484.0938 | 123.2986 | -60.5255 | 62.5122 | -16.4336 | -16.4968 | -16.5453 | -16.4984 | -16.4261 | -15.806 | -16.3015 | 62.5947 | 0.2349 | 62.4847 | -0.023943 | 0.052814 | 60.6277 | 0.016878 | 60.4012 | 44.0919 | 44.0287 | 43.9802 | 44.0271 | 44.0994 | 44.7195 | 44.224 | 123.1202 | 60.7604 | 123.0102 | 60.5016 | 60.5783 | 121.1532 | 60.5424 | 120.9268 | 62.5419 | 62.5779 | 62.4319 | 62.4679
8485.0625 | 123.2437 | -60.5118 | 62.5671 | -16.3237 | -16.3686 | -16.4309 | -16.3428 | -16.275 | -15.6412 | -16.1825 | 62.5902 | 0.23032 | 62.4939 | -0.028522 | 0.06197 | 60.6414 | 0.016878 | 60.415 | 44.1881 | 44.1432 | 44.0809 | 44.169 | 44.2368 | 44.8706 | 44.3293 | 123.1019 | 60.7421 | 123.0057 | 60.4833 | 60.5738 | 121.1532 | 60.5287 | 120.9268 | 62.5282 | 62.5733 | 62.4319 | 62.477
8486.0938 | 123.317 | -60.5026 | 62.5534 | -16.6854 | -16.7257 | -16.7972 | -16.5717 | -16.5039 | -15.8701 | -16.5304 | 62.6039 | 0.23948 | 62.5122 | -0.028522 | 0.043657 | 60.6231 | 0.016878 | 60.4012 | 43.8172 | 43.7769 | 43.7055 | 43.9309 | 43.9987 | 44.6325 | 43.9722 | 123.1065 | 60.7421 | 123.0148 | 60.4741 | 60.5463 | 121.1257 | 60.5195 | 120.9039 | 62.5602 | 62.587 | 62.4685 | 62.4953
8487.0625 | 123.2849 | -60.5209 | 62.5214 | -16.4473 | -16.4876 | -16.5453 | -16.416 | -16.3345 | -15.6778 | -16.3015 | 62.5947 | 0.2349 | 62.503 | -0.033101 | 0.052814 | 60.6322 | 0.012299 | 60.415 | 44.0736 | 44.0333 | 43.9756 | 44.1049 | 44.1864 | 44.8431 | 44.2194 | 123.1157 | 60.7558 | 123.024 | 60.4878 | 60.5737 | 121.1532 | 60.5332 | 120.9359 | 62.5419 | 62.5824 | 62.4502 | 62.4907
8488.1094 | 123.2666 | -60.5164 | 62.5259 | -15.7789 | -15.8283 | -15.8952 | -15.5736 | -15.5105 | -15.0551 | -15.6377 | 62.5581 | 0.23948 | 62.4573 | -0.019364 | 0.048236 | 60.6734 | 0.016878 | 60.447 | 44.7375 | 44.6881 | 44.6212 | 44.9428 | 45.0059 | 45.4612 | 44.8787 | 123.0745 | 60.7558 | 122.9736 | 60.497 | 60.5646 | 121.1898 | 60.5332 | 120.9634 | 62.5099 | 62.5412 | 62.409 | 62.4404
8489.0625 | 123.3536 | -60.5347 | 62.5076 | -15.93 | -15.9702 | -16.0554 | -15.8346 | -15.7668 | -15.1696 | -15.7704 | 62.5581 | 0.23032 | 62.4618 | -0.023943 | 0.048236 | 60.6689 | 0.021456 | 60.4424 | 44.6047 | 44.5644 | 44.4792 | 44.7001 | 44.7678 | 45.3651 | 44.7642 | 123.0928 | 60.765 | 122.9965 | 60.5107 | 60.5829 | 121.2035 | 60.5561 | 120.9771 | 62.5099 | 62.5366 | 62.4136 | 62.4404
8490.0781 | 123.317 | -60.5438 | 62.4252 | -15.9346 | -15.9748 | -16.0371 | -15.862 | -15.7943 | -15.1879 | -15.7933 | 62.5581 | 0.2349 | 62.4573 | -0.019364 | 0.052814 | 60.6597 | 0.012299 | 60.4424 | 44.6093 | 44.569 | 44.5067 | 44.6818 | 44.7495 | 45.3559 | 44.7505 | 123.1019 | 60.7787 | 123.0011 | 60.5245 | 60.5966 | 121.2035 | 60.5561 | 120.9863 | 62.5053 | 62.5458 | 62.4044 | 62.445
8491.0625 | 123.1888 | -60.5438 | 62.5442 | -16.0307 | -16.0755 | -16.1562 | -15.8117 | -15.744 | -15.1788 | -15.8711 | 62.5581 | 0.23948 | 62.4573 | -0.019364 | 0.052814 | 60.6551 | 0.007721 | 60.4424 | 44.5131 | 44.4683 | 44.3877 | 44.7322 | 44.7999 | 45.3651 | 44.6727 | 123.1019 | 60.7833 | 123.0011 | 60.5245 | 60.5966 | 121.1989 | 60.5515 | 120.9863 | 62.5053 | 62.5504 | 62.4044 | 62.4495
8492.0938 | 123.2941 | -60.6033 | 62.4069 | -14.8128 | -14.8576 | -14.9337 | -14.429 | -14.3523 | -13.9792 | -14.6762 | 62.494 | 0.2349 | 62.3932 | -0.019364 | 0.048236 | 60.7284 | 0.012299 | 60.5111 | 45.7905 | 45.7458 | 45.6697 | 46.1744 | 46.2511 | 46.6241 | 45.9271 | 123.0973 | 60.8382 | 122.9965 | 60.584 | 60.6516 | 121.3317 | 60.6156 | 121.1145 | 62.4458 | 62.4817 | 62.3449 | 62.3809
8493.0625 | 123.3673 | -60.5209 | 62.4893 | -15.7743 | -15.8191 | -15.8814 | -15.8071 | -15.7302 | -14.9224 | -15.6285 | 62.5489 | 0.23948 | 62.4481 | -0.028522 | 0.057392 | 60.6734 | 0.007721 | 60.447 | 44.7466 | 44.7018 | 44.6395 | 44.7138 | 44.7907 | 45.5986 | 44.8924 | 123.0699 | 60.7604 | 122.969 | 60.4924 | 60.5783 | 121.1944 | 60.5287 | 120.968 | 62.4916 | 62.5412 | 62.3907 | 62.4404
8494.0938 | 123.3078 | -60.5484 | 62.4802 | -15.8338 | -15.8741 | -15.9684 | -15.8666 | -15.7897 | -15.0368 | -15.6743 | 62.5673 | 0.2349 | 62.4756 | -0.028522 | 0.043657 | 60.6643 | 0.007721 | 60.4424 | 44.7146 | 44.6743 | 44.58 | 44.6818 | 44.7587 | 45.5116 | 44.8741 | 123.1157 | 60.7833 | 123.024 | 60.5199 | 60.5921 | 121.2127 | 60.5561 | 120.9908 | 62.5236 | 62.5595 | 62.4319 | 62.4679
8495.0625 | 123.3261 | -60.6812 | 62.3749 | -13.9338 | -13.9739 | -14.0408 | -13.9024 | -13.8212 | -13.352 | -13.7972 | 62.4482 | 0.23948 | 62.3703 | -0.023943 | 0.043657 | 60.7833 | 0.012299 | 60.5569 | 46.7474 | 46.7073 | 46.6403 | 46.7787 | 46.8599 | 47.3292 | 46.8839 | 123.1294 | 60.9206 | 123.0514 | 60.6572 | 60.7248 | 121.4645 | 60.6935 | 121.2381 | 62.4046 | 62.4359 | 62.3266 | 62.358
8496.1094 | 123.2758 | -60.6812 | 62.3703 | -14.3596 | -14.3997 | -14.4666 | -14.342 | -14.2561 | -13.7732 | -14.2139 | 62.4757 | 0.2349 | 62.3977 | -0.033101 | 0.043657 | 60.7558 | 0.016878 | 60.5294 | 46.3216 | 46.2815 | 46.2145 | 46.3392 | 46.425 | 46.908 | 46.4673 | 123.1568 | 60.916 | 123.0789 | 60.6481 | 60.7248 | 121.437 | 60.698 | 121.2106 | 62.432 | 62.4588 | 62.3541 | 62.3809
8497.0625 | 123.3032 | -60.5301 | 62.4985 | -15.463 | -15.5123 | -15.5747 | -15.5003 | -15.4098 | -14.6202 | -15.3263 | 62.5306 | 0.2349 | 62.4344 | -0.028522 | 0.043657 | 60.6872 | 0.016878 | 60.4608 | 45.0671 | 45.0177 | 44.9554 | 45.0298 | 45.1203 | 45.9099 | 45.2037 | 123.0607 | 60.765 | 122.9645 | 60.5016 | 60.5737 | 121.2173 | 60.547 | 120.9909 | 62.487 | 62.5138 | 62.3907 | 62.4175
8498.0625 | 123.3307 | -60.5209 | 62.5031 | -16.0582 | -16.0847 | -16.1745 | -16.0681 | -15.9866 | -14.991 | -15.894 | 62.5673 | 0.23032 | 62.4618 | -0.028522 | 0.048236 | 60.6551 | 0.012299 | 60.4379 | 44.4628 | 44.4362 | 44.3465 | 44.4529 | 44.5343 | 45.5299 | 44.6269 | 123.0882 | 60.7513 | 122.9828 | 60.4924 | 60.5692 | 121.1761 | 60.5332 | 120.9588 | 62.519 | 62.555 | 62.4136 | 62.4495
8499.1094 | 123.2346 | -60.5667 | 62.4802 | -15.2386 | -15.2742 | -15.3457 | -15.2439 | -15.158 | -14.373 | -15.0929 | 62.5215 | 0.23948 | 62.4206 | -0.019364 | 0.052814 | 60.6963 | 0.007721 | 60.4882 | 45.3281 | 45.2925 | 45.221 | 45.3228 | 45.4087 | 46.1937 | 45.4739 | 123.0882 | 60.8062 | 122.9873 | 60.5473 | 60.6195 | 121.263 | 60.5744 | 121.0549 | 62.4687 | 62.5138 | 62.3678 | 62.4129
8500.0625 | 123.2941 | -60.553 | 62.4756 | -15.2295 | -15.2605 | -15.3869 | -15.3126 | -15.2404 | -14.46 | -15.0745 | 62.5261 | 0.23032 | 62.4206 | -0.028522 | 0.048236 | 60.6963 | 0.012299 | 60.4745 | 45.3235 | 45.2925 | 45.166 | 45.2404 | 45.3126 | 46.093 | 45.4784 | 123.079 | 60.7833 | 122.9736 | 60.5245 | 60.6012 | 121.2493 | 60.5653 | 121.0275 | 62.4778 | 62.5138 | 62.3724 | 62.4083
8501.0938 | 123.2529 | -60.5667 | 62.5122 | -15.5729 | -15.6131 | -15.7029 | -15.5736 | -15.5059 | -14.8766 | -15.4225 | 62.5535 | 0.2349 | 62.4435 | -0.023943 | 0.048236 | 60.678 | 0.012299 | 60.4562 | 44.9938 | 44.9536 | 44.8638 | 44.9931 | 45.0608 | 45.6901 | 45.1442 | 123.1202 | 60.8016 | 123.0102 | 60.5428 | 60.6149 | 121.2447 | 60.579 | 121.0229 | 62.5053 | 62.5412 | 62.3953 | 62.4312
8502.0625 | 123.1522 | -60.5713 | 62.5076 | -15.5454 | -15.5856 | -15.6983 | -15.5461 | -15.4784 | -14.9727 | -15.4042 | 62.5444 | 0.2349 | 62.4481 | -0.023943 | 0.048236 | 60.6826 | 0.007721 | 60.4608 | 45.0259 | 44.9857 | 44.873 | 45.0252 | 45.0929 | 45.5986 | 45.1671 | 123.1157 | 60.8062 | 123.0194 | 60.5473 | 60.6195 | 121.2539 | 60.579 | 121.0321 | 62.4961 | 62.5366 | 62.3999 | 62.4404
8503.0625 | 123.3673 | -60.5988 | 62.4069 | -14.8953 | -14.9537 | -15.0207 | -14.7266 | -14.6224 | -14.1853 | -14.7587 | 62.4986 | 0.23948 | 62.4161 | -0.028522 | 0.048236 | 60.7238 | 0.012299 | 60.5111 | 45.7035 | 45.645 | 45.5781 | 45.8722 | 45.9764 | 46.4135 | 45.8401 | 123.0973 | 60.8382 | 123.0148 | 60.5702 | 60.647 | 121.3226 | 60.6111 | 121.1099 | 62.4503 | 62.4863 | 62.3678 | 62.4038
8504.1094 | 123.3215 | -60.5438 | 62.4481 | -15.376 | -15.4162 | -15.4968 | -15.3996 | -15.3182 | -14.5927 | -15.2348 | 62.5352 | 0.2349 | 62.4389 | -0.033101 | 0.052814 | 60.6963 | 0.003143 | 60.4699 | 45.1678 | 45.1276 | 45.047 | 45.1442 | 45.2256 | 45.9511 | 45.309 | 123.079 | 60.7787 | 122.9828 | 60.5107 | 60.5966 | 121.2401 | 60.547 | 121.0137 | 62.4824 | 62.5321 | 62.3861 | 62.4358
8505.0625 | 123.3398 | -60.6171 | 62.3932 | -15.1562 | -15.2101 | -15.2908 | -15.2073 | -15.1259 | -14.4416 | -15.0196 | 62.5169 | 0.23032 | 62.4252 | -0.033101 | 0.052814 | 60.7146 | 0.021456 | 60.4882 | 45.4608 | 45.4069 | 45.3263 | 45.4098 | 45.4911 | 46.1754 | 45.5975 | 123.134 | 60.8474 | 123.0423 | 60.584 | 60.6699 | 121.3317 | 60.6385 | 121.1053 | 62.4641 | 62.4954 | 62.3724 | 62.4038
8506.0938 | 123.3398 | -60.5576 | 62.4893 | -15.3531 | -15.3979 | -15.4923 | -15.4133 | -15.3274 | -14.7026 | -15.2073 | 62.5306 | 0.2349 | 62.4252 | -0.033101 | 0.052814 | 60.6872 | 0.016878 | 60.4653 | 45.2045 | 45.1597 | 45.0653 | 45.1442 | 45.2302 | 45.8549 | 45.3502 | 123.0882 | 60.7925 | 122.9828 | 60.5245 | 60.6104 | 121.2447 | 60.5744 | 121.0229 | 62.4778 | 62.5138 | 62.3724 | 62.4083
8507.0781 | 123.2758 | -60.5988 | 62.4435 | -15.3806 | -15.4345 | -15.5151 | -15.4225 | -15.3411 | -14.6065 | -15.2394 | 62.5261 | 0.2349 | 62.4206 | -0.023943 | 0.052814 | 60.6917 | 0.016878 | 60.4745 | 45.2182 | 45.1643 | 45.0836 | 45.1763 | 45.2577 | 45.9923 | 45.3594 | 123.1248 | 60.8337 | 123.0194 | 60.5748 | 60.6516 | 121.2905 | 60.6156 | 121.0733 | 62.4732 | 62.5092 | 62.3678 | 62.4038
8508.0781 | 123.2941 | -60.5667 | 62.4573 | -15.0006 | -15.0361 | -15.1168 | -14.9738 | -14.8925 | -14.0937 | -14.8411 | 62.5077 | 0.24405 | 62.4023 | -0.033101 | 0.043657 | 60.7146 | 0.012299 | 60.4928 | 45.5661 | 45.5306 | 45.4499 | 45.5929 | 45.6743 | 46.473 | 45.7257 | 123.0745 | 60.8108 | 122.969 | 60.5336 | 60.6104 | 121.2814 | 60.579 | 121.0595 | 62.4641 | 62.4954 | 62.3587 | 62.39
8509.0625 | 123.1979 | -60.7178 | 62.3611 | -13.1509 | -13.1817 | -13.2487 | -13.0692 | -12.988 | -12.299 | -12.9869 | 62.407 | 0.2349 | 62.3108 | -0.028522 | 0.048236 | 60.8199 | 0.012299 | 60.5981 | 47.5669 | 47.536 | 47.469 | 47.6486 | 47.7297 | 48.4188 | 47.7309 | 123.1248 | 60.9527 | 123.0285 | 60.6893 | 60.766 | 121.5377 | 60.7301 | 121.3159 | 62.3588 | 62.3947 | 62.2625 | 62.2985
8510.0781 | 123.3353 | -60.5896 | 62.4298 | -15.1654 | -15.2101 | -15.3366 | -15.0883 | -15.0161 | -14.5378 | -15.015 | 62.5261 | 0.23948 | 62.4435 | -0.019364 | 0.052814 | 60.7055 | 0.007721 | 60.4745 | 45.4242 | 45.3795 | 45.253 | 45.5013 | 45.5735 | 46.0518 | 45.5746 | 123.1157 | 60.8291 | 123.0331 | 60.5702 | 60.6424 | 121.2951 | 60.5973 | 121.0641 | 62.4732 | 62.5183 | 62.3907 | 62.4358
8511.0625 | 123.3124 | -60.4614 | 62.5259 | -16.2093 | -16.2541 | -16.3347 | -16.0635 | -15.9729 | -15.1055 | -16.036 | 62.5673 | 0.23948 | 62.4847 | -0.023943 | 0.048236 | 60.6551 | 0.021456 | 60.4287 | 44.2522 | 44.2073 | 44.1267 | 44.3979 | 44.4886 | 45.3559 | 44.4255 | 123.0287 | 60.7009 | 122.9462 | 60.4375 | 60.5097 | 121.1166 | 60.4829 | 120.8901 | 62.519 | 62.5458 | 62.4365 | 62.4633
8512.1094 | 123.3582 | -60.5667 | 62.4939 | -15.1379 | -15.1689 | -15.2862 | -14.9967 | -14.9108 | -14.2127 | -14.9738 | 62.5123 | 0.2349 | 62.4252 | -0.023943 | 0.043657 | 60.7101 | 0.016878 | 60.4928 | 45.4288 | 45.3978 | 45.2805 | 45.57 | 45.6559 | 46.354 | 45.5929 | 123.079 | 60.8016 | 122.9919 | 60.5428 | 60.6104 | 121.2768 | 60.5836 | 121.0595 | 62.4687 | 62.4954 | 62.3816 | 62.4083
8513.0625 | 123.2803 | -60.5759 | 62.4298 | -14.6434 | -14.6653 | -14.8238 | -14.548 | -14.4896 | -13.8373 | -14.4748 | 62.4803 | 0.22574 | 62.384 | -0.023943 | 0.048236 | 60.7375 | 0.012299 | 60.5157 | 45.9324 | 45.9106 | 45.7521 | 46.0279 | 46.0863 | 46.7386 | 46.1011 | 123.0561 | 60.8016 | 122.9599 | 60.5519 | 60.6241 | 121.3134 | 60.5882 | 121.0916 | 62.432 | 62.468 | 62.3358 | 62.3717
8514.0938 | 123.3032 | -60.6766 | 62.3749 | -13.7232 | -13.7587 | -13.8714 | -13.3896 | -13.3085 | -12.9811 | -13.5638 | 62.4253 | 0.23948 | 62.3291 | -0.023943 | 0.043657 | 60.7879 | 0.012299 | 60.5706 | 46.9534 | 46.9179 | 46.8051 | 47.2869 | 47.3681 | 47.6954 | 47.1128 | 123.1019 | 60.9161 | 123.0056 | 60.6526 | 60.7202 | 121.4645 | 60.6889 | 121.2472 | 62.3817 | 62.413 | 62.2854 | 62.3168
8515.0781 | 123.2849 | -60.6445 | 62.4069 | -14.323 | -14.3585 | -14.4895 | -14.0764 | -13.9998 | -13.6633 | -14.1726 | 62.462 | 0.2349 | 62.3657 | -0.028522 | 0.052814 | 60.7513 | 0.012299 | 60.5294 | 46.3216 | 46.286 | 46.155 | 46.5681 | 46.6448 | 46.9812 | 46.4719 | 123.1065 | 60.8794 | 123.0102 | 60.616 | 60.6973 | 121.3958 | 60.6568 | 121.174 | 62.4091 | 62.4497 | 62.3129 | 62.3534
8516.0781 | 123.2941 | -60.6033 | 62.4115 | -14.4283 | -14.4821 | -14.5948 | -14.1451 | -14.0638 | -13.7686 | -14.2779 | 62.4711 | 0.2349 | 62.3749 | -0.028522 | 0.048236 | 60.7513 | 0.012299 | 60.5294 | 46.1751 | 46.1212 | 46.0085 | 46.4582 | 46.5395 | 46.8347 | 46.3254 | 123.0744 | 60.8382 | 122.9782 | 60.5748 | 60.6516 | 121.3546 | 60.6156 | 121.1328 | 62.4229 | 62.4588 | 62.3266 | 62.3626
8517.0625 | 123.2666 | -60.6262 | 62.4298 | -15.6644 | -15.6955 | -15.8356 | -15.5324 | -15.4601 | -14.84 | -15.4866 | 62.5444 | 0.2349 | 62.4481 | -0.023943 | 0.048236 | 60.678 | 0.012299 | 60.4608 | 44.9618 | 44.9307 | 44.7906 | 45.0938 | 45.1661 | 45.7863 | 45.1396 | 123.1706 | 60.8611 | 123.0743 | 60.6023 | 60.6745 | 121.3042 | 60.6385 | 121.087 | 62.4961 | 62.5321 | 62.3999 | 62.4358
8518.0781 | 123.2758 | -60.6033 | 62.4252 | -16.0078 | -16.0618 | -16.1928 | -16.0543 | -15.9545 | -15.3711 | -15.8574 | 62.5673 | 0.23948 | 62.4756 | -0.033101 | 0.057392 | 60.6597 | 0.012299 | 60.4333 | 44.5955 | 44.5415 | 44.4106 | 44.549 | 44.6488 | 45.2323 | 44.7459 | 123.1706 | 60.8428 | 123.0789 | 60.5702 | 60.6607 | 121.263 | 60.6156 | 121.0366 | 62.5099 | 62.555 | 62.4182 | 62.4633
8519.0625 | 123.2986 | -60.6033 | 62.3886 | -14.4512 | -14.4958 | -14.6589 | -14.1863 | -14.1005 | -13.7274 | -14.2963 | 62.4665 | 0.2349 | 62.384 | -0.023943 | 0.057392 | 60.7558 | 0.012299 | 60.5294 | 46.1522 | 46.1075 | 45.9444 | 46.417 | 46.5029 | 46.8759 | 46.3071 | 123.0699 | 60.8382 | 122.9873 | 60.5794 | 60.6607 | 121.3592 | 60.6156 | 121.1328 | 62.4091 | 62.4542 | 62.3266 | 62.3717
8520.1094 | 123.2254 | -60.6583 | 62.4344 | -14.4512 | -14.5233 | -14.6223 | -14.2229 | -14.1188 | -13.5855 | -14.2963 | 62.4757 | 0.24405 | 62.384 | -0.028522 | 0.052814 | 60.7421 | 0.012299 | 60.5249 | 46.2071 | 46.1349 | 46.0359 | 46.4353 | 46.5395 | 47.0728 | 46.362 | 123.134 | 60.9023 | 123.0423 | 60.6297 | 60.7111 | 121.4004 | 60.6706 | 121.1831 | 62.4229 | 62.4634 | 62.3312 | 62.3717
8521.0625 | 123.2162 | -60.6537 | 62.4298 | -14.8724 | -14.9079 | -15.0527 | -14.9143 | -14.8238 | -14.2814 | -14.7174 | 62.5032 | 0.2349 | 62.3977 | -0.023943 | 0.052814 | 60.7146 | 0.012299 | 60.4974 | 45.7813 | 45.7457 | 45.601 | 45.7394 | 45.8299 | 46.3723 | 45.9362 | 123.1568 | 60.8886 | 123.0514 | 60.6297 | 60.7065 | 121.3683 | 60.666 | 121.1511 | 62.4503 | 62.4909 | 62.3449 | 62.3854
8522.0938 | 123.3353 | -60.7178 | 62.3245 | -14.1719 | -14.2303 | -14.3384 | -14.0489 | -13.9357 | -13.384 | -14.0307 | 62.4574 | 0.23032 | 62.3565 | -0.023943 | 0.043657 | 60.765 | 0.016878 | 60.5432 | 46.5459 | 46.4875 | 46.3793 | 46.6688 | 46.7821 | 47.3337 | 46.687 | 123.1752 | 60.9481 | 123.0743 | 60.6938 | 60.7614 | 121.4828 | 60.7347 | 121.2609 | 62.4137 | 62.4405 | 62.3129 | 62.3397
8523.0781 | 123.381 | -60.6033 | 62.4527 | -15.2066 | -15.2422 | -15.4144 | -15.2485 | -15.1442 | -14.4828 | -15.0517 | 62.5215 | 0.2349 | 62.4252 | -0.028522 | 0.048236 | 60.7009 | 0.012299 | 60.4837 | 45.3967 | 45.3611 | 45.1889 | 45.3548 | 45.4591 | 46.1205 | 45.5517 | 123.1248 | 60.8382 | 123.0285 | 60.5748 | 60.6516 | 121.3042 | 60.6156 | 121.087 | 62.4732 | 62.5092 | 62.377 | 62.4129
8524.0938 | 123.2712 | -60.5576 | 62.5168 | -14.9823 | -15.0133 | -15.2084 | -14.9646 | -14.8925 | -14.2448 | -14.8273 | 62.5032 | 0.2349 | 62.4069 | -0.023943 | 0.048236 | 60.7146 | 0.021456 | 60.4928 | 45.5753 | 45.5443 | 45.3492 | 45.5929 | 45.6651 | 46.3128 | 45.7302 | 123.0607 | 60.7925 | 122.9645 | 60.5336 | 60.6058 | 121.2722 | 60.579 | 121.0504 | 62.4549 | 62.4817 | 62.3587 | 62.3854
8525.0625 | 123.2025 | -60.6628 | 62.4161 | -13.5217 | -13.5572 | -13.7203 | -13.2752 | -13.1803 | -12.7705 | -13.3715 | 62.4253 | 0.24863 | 62.3428 | -0.028522 | 0.052814 | 60.8016 | 0.021456 | 60.5844 | 47.1411 | 47.1057 | 46.9425 | 47.3877 | 47.4825 | 47.8923 | 47.2914 | 123.0882 | 60.9115 | 123.0056 | 60.6343 | 60.7157 | 121.4645 | 60.6843 | 121.2472 | 62.3725 | 62.4039 | 62.29 | 62.3213
8526.0625 | 123.1476 | -60.7361 | 62.3291 | -13.5309 | -13.5618 | -13.7615 | -13.2981 | -13.2169 | -12.798 | -13.3715 | 62.4253 | 0.23948 | 62.3336 | -0.028522 | 0.043657 | 60.797 | 0.016878 | 60.5752 | 47.2052 | 47.1743 | 46.9745 | 47.438 | 47.5192 | 47.9381 | 47.3646 | 123.1614 | 60.9756 | 123.0697 | 60.7076 | 60.7797 | 121.5331 | 60.753 | 121.3113 | 62.3817 | 62.4085 | 62.29 | 62.3168
8527.0781 | 123.2803 | -60.5438 | 62.4939 | -15.3897 | -15.4025 | -15.6479 | -15.3263 | -15.2404 | -14.5607 | -15.1982 | 62.5261 | 0.23948 | 62.4389 | -0.028522 | 0.048236 | 60.6917 | 0.012299 | 60.4608 | 45.1541 | 45.1414 | 44.8959 | 45.2175 | 45.3034 | 45.9831 | 45.3457 | 123.0699 | 60.7833 | 122.9828 | 60.5153 | 60.5921 | 121.2356 | 60.5561 | 121.0046 | 62.4778 | 62.5138 | 62.3907 | 62.4267
8528.0625 | 123.3124 | -60.6262 | 62.4069 | -14.8449 | -14.9308 | -15.0252 | -14.7632 | -14.6361 | -14.0891 | -14.6991 | 62.494 | 0.2349 | 62.4023 | -0.023943 | 0.048236 | 60.7284 | 0.016878 | 60.5065 | 45.7813 | 45.6954 | 45.601 | 45.863 | 45.9901 | 46.5371 | 45.9271 | 123.1202 | 60.8611 | 123.0285 | 60.6023 | 60.6745 | 121.3546 | 60.6431 | 121.1328 | 62.4458 | 62.4771 | 62.3541 | 62.3854
8529.0625 | 123.2437 | -60.6079 | 62.4756 | -14.3871 | -14.4455 | -14.5948 | -14.3008 | -14.1875 | -13.5763 | -14.223 | 62.4711 | 0.2349 | 62.3657 | -0.019364 | 0.048236 | 60.7467 | 0.016878 | 60.5294 | 46.2208 | 46.1624 | 46.0131 | 46.3071 | 46.4205 | 47.0316 | 46.3849 | 123.079 | 60.8428 | 122.9736 | 60.5885 | 60.6561 | 121.3546 | 60.6248 | 121.1373 | 62.4229 | 62.4542 | 62.3175 | 62.3488
8530.0781 | 123.3032 | -60.5667 | 62.4939 | -15.5912 | -15.6268 | -15.8265 | -15.5919 | -15.4967 | -14.7163 | -15.4042 | 62.5352 | 0.23032 | 62.4389 | -0.019364 | 0.048236 | 60.678 | 0.016878 | 60.4562 | 44.9755 | 44.9399 | 44.7402 | 44.9748 | 45.07 | 45.8504 | 45.1625 | 123.1019 | 60.797 | 123.0057 | 60.5473 | 60.6149 | 121.2447 | 60.5836 | 121.0229 | 62.487 | 62.5183 | 62.3907 | 62.4221
8531.0625 | 123.2483 | -60.5392 | 62.5763 | -15.4538 | -15.4986 | -15.6891 | -15.4866 | -15.3823 | -14.7163 | -15.2623 | 62.5352 | 0.2349 | 62.4298 | -0.028522 | 0.057392 | 60.678 | 0.016878 | 60.4699 | 45.0854 | 45.0406 | 44.8501 | 45.0527 | 45.1569 | 45.8229 | 45.277 | 123.0745 | 60.7741 | 122.969 | 60.5107 | 60.5966 | 121.2173 | 60.5561 | 121.0092 | 62.4778 | 62.5183 | 62.3724 | 62.4129
8532.1094 | 123.2758 | -60.5667 | 62.4893 | -15.3165 | -15.3521 | -15.5472 | -15.308 | -15.2129 | -14.5607 | -15.1341 | 62.5215 | 0.22574 | 62.4252 | -0.028522 | 0.048236 | 60.6872 | 0.012299 | 60.4699 | 45.2502 | 45.2146 | 45.0195 | 45.2587 | 45.3538 | 46.006 | 45.4326 | 123.0882 | 60.7924 | 122.9919 | 60.5382 | 60.6149 | 121.2539 | 60.579 | 121.0366 | 62.4732 | 62.5092 | 62.377 | 62.4129
8533.0625 | 123.2346 | -60.5667 | 62.5442 | -15.7239 | -15.7688 | -15.9089 | -15.7201 | -15.6112 | -14.9315 | -15.5415 | 62.5627 | 0.24405 | 62.4618 | -0.019364 | 0.052814 | 60.6689 | 0.012299 | 60.4516 | 44.8428 | 44.798 | 44.6578 | 44.8466 | 44.9555 | 45.6352 | 45.0252 | 123.1294 | 60.8108 | 123.0286 | 60.5473 | 60.6195 | 121.2356 | 60.579 | 121.0183 | 62.5099 | 62.5504 | 62.409 | 62.4495
8534.0938 | 123.2208 | -60.6216 | 62.4847 | -14.094 | -14.157 | -14.2881 | -14.0673 | -13.9631 | -13.4207 | -13.93 | 62.4528 | 0.24405 | 62.3703 | -0.023943 | 0.052814 | 60.765 | 0.016878 | 60.5477 | 46.5276 | 46.4646 | 46.3336 | 46.5544 | 46.6585 | 47.201 | 46.6916 | 123.0744 | 60.8657 | 122.9919 | 60.5977 | 60.6745 | 121.3866 | 60.6385 | 121.1694 | 62.4 | 62.4359 | 62.3175 | 62.3534
8535.0625 | 123.23 | -60.5713 | 62.4893 | -14.9731 | -15.0133 | -15.2221 | -15.0562 | -14.9566 | -14.2951 | -14.8044 | 62.5123 | 0.24405 | 62.4069 | -0.023943 | 0.048236 | 60.7055 | 0.012299 | 60.4837 | 45.5982 | 45.558 | 45.3492 | 45.5151 | 45.6147 | 46.2762 | 45.7669 | 123.0836 | 60.8153 | 122.9782 | 60.5473 | 60.6195 | 121.2768 | 60.5836 | 121.0549 | 62.4641 | 62.5 | 62.3587 | 62.3946
8536.0938 | 123.3627 | -60.5576 | 62.471 | -15.0967 | -15.1369 | -15.332 | -15.1386 | -15.0298 | -14.3318 | -14.9189 | 62.5123 | 0.2349 | 62.4206 | -0.019364 | 0.052814 | 60.7101 | 0.021456 | 60.4882 | 45.4608 | 45.4207 | 45.2256 | 45.4189 | 45.5278 | 46.2258 | 45.6387 | 123.0699 | 60.7925 | 122.9782 | 60.5382 | 60.6104 | 121.2676 | 60.579 | 121.0458 | 62.4595 | 62.4909 | 62.3678 | 62.3992
8537.0625 | 123.23 | -60.6262 | 62.4802 | -15.5912 | -15.6497 | -15.8265 | -15.7109 | -15.5929 | -14.8629 | -15.4225 | 62.5444 | 0.2349 | 62.4527 | -0.023943 | 0.048236 | 60.6734 | 0.012299 | 60.4608 | 45.035 | 44.9765 | 44.7997 | 44.9153 | 45.0333 | 45.7634 | 45.2037 | 123.1706 | 60.8611 | 123.0789 | 60.6023 | 60.6745 | 121.2997 | 60.6385 | 121.087 | 62.4961 | 62.5321 | 62.4044 | 62.4404
8538.1094 | 123.2529 | -60.5484 | 62.4893 | -15.4264 | -15.4757 | -15.68 | -15.4774 | -15.3731 | -14.6935 | -15.2577 | 62.5444 | 0.24405 | 62.4435 | -0.023943 | 0.057392 | 60.6963 | 0.007721 | 60.4653 | 45.122 | 45.0727 | 44.8684 | 45.071 | 45.1753 | 45.8549 | 45.2907 | 123.0928 | 60.7925 | 122.9919 | 60.5245 | 60.6058 | 121.2447 | 60.5561 | 121.0137 | 62.487 | 62.5366 | 62.3861 | 62.4358
8539.0625 | 123.2712 | -60.6171 | 62.4573 | -14.6251 | -14.679 | -14.8879 | -14.6533 | -14.5445 | -13.906 | -14.4611 | 62.4894 | 0.23948 | 62.4023 | -0.023943 | 0.052814 | 60.7284 | 0.012299 | 60.5111 | 45.9919 | 45.9381 | 45.7292 | 45.9638 | 46.0725 | 46.7111 | 46.156 | 123.1065 | 60.8565 | 123.0194 | 60.5931 | 60.6699 | 121.3454 | 60.6294 | 121.1282 | 62.4366 | 62.4771 | 62.3495 | 62.39
8540.0938 | 123.349 | -60.5667 | 62.4298 | -15.3623 | -15.4162 | -15.5976 | -15.4317 | -15.3319 | -14.6477 | -15.1936 | 62.5306 | 0.23948 | 62.4298 | -0.019364 | 0.043657 | 60.6917 | 0.012299 | 60.4653 | 45.2045 | 45.1505 | 44.9691 | 45.1351 | 45.2348 | 45.919 | 45.3731 | 123.0973 | 60.8062 | 122.9965 | 60.5473 | 60.6104 | 121.2585 | 60.579 | 121.0321 | 62.487 | 62.5183 | 62.3861 | 62.4175
8541.0625 | 123.2895 | -60.5988 | 62.4481 | -15.3714 | -15.4299 | -15.5976 | -15.4454 | -15.3319 | -14.6339 | -15.2073 | 62.5306 | 0.2349 | 62.4252 | -0.028522 | 0.048236 | 60.6917 | 0.012299 | 60.4653 | 45.2273 | 45.1688 | 45.0012 | 45.1534 | 45.2668 | 45.9648 | 45.3914 | 123.1294 | 60.8337 | 123.024 | 60.5702 | 60.647 | 121.2905 | 60.6111 | 121.0641 | 62.4824 | 62.5183 | 62.377 | 62.4129
8542.0938 | 123.2117 | -60.585 | 62.5351 | -14.9319 | -14.9858 | -15.1718 | -15.0287 | -14.9153 | -14.2173 | -14.7449 | 62.5077 | 0.2349 | 62.4161 | -0.023943 | 0.048236 | 60.7101 | 0.012299 | 60.4928 | 45.6531 | 45.5992 | 45.4133 | 45.5563 | 45.6697 | 46.3677 | 45.8401 | 123.0928 | 60.8199 | 123.0011 | 60.5611 | 60.6333 | 121.2951 | 60.5973 | 121.0778 | 62.4595 | 62.4954 | 62.3678 | 62.4038
8543.0625 | 123.2391 | -60.5438 | 62.5122 | -15.756 | -15.8145 | -15.9776 | -15.775 | -15.657 | -14.9407 | -15.5827 | 62.5535 | 0.23948 | 62.4527 | -0.019364 | 0.052814 | 60.6734 | 0.012299 | 60.447 | 44.7878 | 44.7293 | 44.5662 | 44.7688 | 44.8868 | 45.6031 | 44.9611 | 123.0973 | 60.7833 | 122.9965 | 60.5245 | 60.5966 | 121.2173 | 60.5561 | 120.9908 | 62.5007 | 62.5412 | 62.3999 | 62.4404
8544.1094 | 123.317 | -60.5392 | 62.4985 | -15.4767 | -15.5352 | -15.712 | -15.5141 | -15.4052 | -14.6294 | -15.2714 | 62.5352 | 0.2349 | 62.4389 | -0.023943 | 0.048236 | 60.6872 | 0.026035 | 60.4562 | 45.0625 | 45.004 | 44.8272 | 45.0252 | 45.1341 | 45.9099 | 45.2678 | 123.0745 | 60.7741 | 122.9782 | 60.5153 | 60.5875 | 121.2264 | 60.5653 | 120.9954 | 62.487 | 62.5092 | 62.3907 | 62.4129
8545.0625 | 123.2437 | -60.5438 | 62.5214 | -15.6003 | -15.6589 | -15.8402 | -15.6148 | -15.4967 | -14.7118 | -15.4042 | 62.5444 | 0.2349 | 62.4481 | -0.028522 | 0.043657 | 60.678 | 0.007721 | 60.4653 | 44.9435 | 44.885 | 44.7036 | 44.929 | 45.0471 | 45.8321 | 45.1396 | 123.0882 | 60.7787 | 122.9919 | 60.5153 | 60.5875 | 121.2218 | 60.5515 | 121.0092 | 62.5007 | 62.5366 | 62.4044 | 62.4404
8546.0938 | 123.3215 | -60.5667 | 62.4664 | -15.3989 | -15.4574 | -15.6525 | -15.395 | -15.2633 | -14.4279 | -15.2165 | 62.5306 | 0.2349 | 62.4298 | -0.023943 | 0.052814 | 60.6872 | 0.021456 | 60.4745 | 45.1678 | 45.1093 | 44.9142 | 45.1717 | 45.3034 | 46.1388 | 45.3502 | 123.0973 | 60.8016 | 122.9965 | 60.5428 | 60.6195 | 121.2539 | 60.5882 | 121.0412 | 62.4778 | 62.5092 | 62.377 | 62.4083
8547.0625 | 123.1888 | -60.6171 | 62.4756 | -15.2615 | -15.32 | -15.5197 | -15.2302 | -15.1168 | -14.2768 | -15.0883 | 62.5261 | 0.2349 | 62.4389 | -0.028522 | 0.043657 | 60.6963 | 0.007721 | 60.4837 | 45.3555 | 45.297 | 45.0973 | 45.3869 | 45.5003 | 46.3402 | 45.5288 | 123.1431 | 60.852 | 123.056 | 60.5885 | 60.6607 | 121.3134 | 60.6248 | 121.1007 | 62.4824 | 62.5183 | 62.3953 | 62.4312
8548.0938 | 123.2437 | -60.6079 | 62.4344 | -14.6022 | -14.6561 | -14.8192 | -14.5846 | -14.4667 | -13.6862 | -14.4153 | 62.4894 | 0.2349 | 62.384 | -0.028522 | 0.052814 | 60.733 | 0.012299 | 60.5157 | 46.0057 | 45.9518 | 45.7887 | 46.0233 | 46.1412 | 46.9217 | 46.1926 | 123.0973 | 60.8428 | 122.9919 | 60.5794 | 60.6607 | 121.3409 | 60.6202 | 121.1236 | 62.4366 | 62.4771 | 62.3312 | 62.3717
8549.0625 | 123.2483 | -60.6125 | 62.4481 | -14.5381 | -14.5966 | -14.7872 | -14.5846 | -14.453 | -13.7549 | -14.3329 | 62.4848 | 0.23948 | 62.3794 | -0.023943 | 0.052814 | 60.7421 | 0.016878 | 60.5203 | 46.0743 | 46.0159 | 45.8253 | 46.0279 | 46.1595 | 46.8576 | 46.2796 | 123.0973 | 60.852 | 122.9919 | 60.5885 | 60.6653 | 121.3546 | 60.6294 | 121.1328 | 62.432 | 62.468 | 62.3266 | 62.3626
8550.1094 | 123.3582 | -60.5484 | 62.4573 | -15.0235 | -15.0682 | -15.2496 | -15.0562 | -14.9291 | -14.2402 | -14.8273 | 62.5169 | 0.24405 | 62.4161 | -0.028522 | 0.048236 | 60.7192 | 0.007721 | 60.4882 | 45.5249 | 45.4802 | 45.2988 | 45.4922 | 45.6193 | 46.3082 | 45.7211 | 123.0653 | 60.7925 | 122.9645 | 60.5199 | 60.5966 | 121.2676 | 60.5561 | 121.0366 | 62.4687 | 62.5092 | 62.3678 | 62.4083
8551.0625 | 123.2437 | -60.6262 | 62.4481 | -14.2543 | -14.3081 | -14.5079 | -14.287 | -14.1783 | -13.439 | -14.0948 | 62.4665 | 0.24863 | 62.3794 | -0.028522 | 0.048236 | 60.7513 | 0.012299 | 60.5294 | 46.3719 | 46.3181 | 46.1184 | 46.3392 | 46.4479 | 47.1872 | 46.5314 | 123.0928 | 60.8749 | 123.0057 | 60.5977 | 60.6745 | 121.3775 | 60.6385 | 121.1557 | 62.4183 | 62.4542 | 62.3312 | 62.3671
8552.0938 | 123.3078 | -60.5621 | 62.4435 | -15.0189 | -15.0774 | -15.2633 | -15.0059 | -14.8787 | -14.1166 | -14.8227 | 62.5123 | 0.2349 | 62.4115 | -0.028522 | 0.052814 | 60.7009 | 0.016878 | 60.4882 | 45.5433 | 45.4848 | 45.2988 | 45.5563 | 45.6834 | 46.4456 | 45.7394 | 123.0745 | 60.797 | 122.9736 | 60.5336 | 60.6149 | 121.263 | 60.579 | 121.0504 | 62.4595 | 62.4954 | 62.3587 | 62.3946
8553.0625 | 123.1979 | -60.5942 | 62.4802 | -15.4538 | -15.5215 | -15.6983 | -15.537 | -15.4189 | -14.6248 | -15.2531 | 62.5306 | 0.23032 | 62.4252 | -0.028522 | 0.043657 | 60.6872 | 0.012299 | 60.4699 | 45.1404 | 45.0727 | 44.8959 | 45.0572 | 45.1753 | 45.9694 | 45.3411 | 123.1248 | 60.8245 | 123.0194 | 60.5657 | 60.6378 | 121.2813 | 60.6065 | 121.0641 | 62.487 | 62.5183 | 62.3816 | 62.4129
8554.0938 | 123.1842 | -60.5621 | 62.5488 | -15.5591 | -15.6177 | -15.8219 | -15.6652 | -15.5471 | -14.7759 | -15.3675 | 62.5444 | 0.2349 | 62.4389 | -0.023943 | 0.052814 | 60.678 | 0.012299 | 60.4562 | 45.003 | 44.9445 | 44.7402 | 44.897 | 45.015 | 45.7863 | 45.1946 | 123.1065 | 60.797 | 123.0011 | 60.5382 | 60.6149 | 121.2401 | 60.5744 | 121.0183 | 62.4916 | 62.5321 | 62.3861 | 62.4267
8555.0625 | 123.2025 | -60.5804 | 62.4893 | -15.4676 | -15.5398 | -15.7532 | -15.6011 | -15.4693 | -14.6568 | -15.2943 | 62.5398 | 0.23032 | 62.4435 | -0.028522 | 0.043657 | 60.6734 | 0.016878 | 60.4608 | 45.1129 | 45.0406 | 44.8272 | 44.9794 | 45.1112 | 45.9236 | 45.2861 | 123.1202 | 60.8108 | 123.024 | 60.5519 | 60.6241 | 121.2539 | 60.5973 | 121.0412 | 62.4961 | 62.5229 | 62.3999 | 62.4266
8556.0781 | 123.2208 | -60.5759 | 62.5031 | -15.1242 | -15.1689 | -15.3869 | -15.1432 | -15.0206 | -14.3043 | -14.928 | 62.5077 | 0.2349 | 62.4206 | -0.023943 | 0.048236 | 60.7055 | 0.021456 | 60.4928 | 45.4517 | 45.4069 | 45.1889 | 45.4327 | 45.5552 | 46.2716 | 45.6478 | 123.0836 | 60.8108 | 122.9965 | 60.5519 | 60.6241 | 121.2814 | 60.5973 | 121.0687 | 62.4595 | 62.4863 | 62.3724 | 62.3992
8557.0625 | 123.2986 | -60.5576 | 62.439 | -14.8953 | -14.9537 | -15.1992 | -15.0654 | -14.9428 | -14.1303 | -14.7312 | 62.5077 | 0.23948 | 62.4161 | -0.028522 | 0.043657 | 60.7101 | 0.021456 | 60.4882 | 45.6623 | 45.6038 | 45.3583 | 45.4922 | 45.6147 | 46.4272 | 45.8264 | 123.0653 | 60.797 | 122.9736 | 60.529 | 60.6012 | 121.2676 | 60.579 | 121.0458 | 62.4641 | 62.4863 | 62.3724 | 62.3946
8558.0938 | 123.3994 | -60.5255 | 62.5122 | -14.9456 | -15.0041 | -15.2542 | -15.0333 | -14.8925 | -14.1486 | -14.7587 | 62.5123 | 0.23948 | 62.4115 | -0.023943 | 0.043657 | 60.7146 | 0.016878 | 60.4928 | 45.5799 | 45.5214 | 45.2713 | 45.4922 | 45.6331 | 46.3769 | 45.7669 | 123.0378 | 60.765 | 122.937 | 60.5016 | 60.5692 | 121.2402 | 60.5424 | 121.0183 | 62.4687 | 62.4954 | 62.3678 | 62.3946
8559.0625 | 123.2346 | -60.6079 | 62.4527 | -14.7716 | -14.8255 | -15.0527 | -14.8593 | -14.7093 | -13.9563 | -14.5572 | 62.5032 | 0.23948 | 62.4023 | -0.023943 | 0.057392 | 60.7192 | 0.016878 | 60.502 | 45.8363 | 45.7824 | 45.5552 | 45.7486 | 45.8986 | 46.6516 | 46.0507 | 123.1111 | 60.8474 | 123.0102 | 60.584 | 60.6653 | 121.3271 | 60.6248 | 121.1099 | 62.4458 | 62.4863 | 62.3449 | 62.3854
8560.0938 | 123.3536 | -60.5759 | 62.4619 | -14.6755 | -14.7111 | -15.0069 | -14.7907 | -14.6498 | -13.8785 | -14.4428 | 62.4894 | 0.2349 | 62.3977 | -0.028522 | 0.052814 | 60.7238 | 0.016878 | 60.5065 | 45.9004 | 45.8648 | 45.5689 | 45.7852 | 45.926 | 46.6974 | 46.1331 | 123.0653 | 60.8108 | 122.9736 | 60.5473 | 60.6287 | 121.2997 | 60.5927 | 121.0824 | 62.4366 | 62.4725 | 62.3449 | 62.3809
8561.0625 | 123.3215 | -60.5484 | 62.4481 | -15.5133 | -15.5673 | -15.8494 | -15.6652 | -15.5151 | -14.6156 | -15.3218 | 62.5398 | 0.2349 | 62.4252 | -0.023943 | 0.048236 | 60.6872 | 0.012299 | 60.4562 | 45.0351 | 44.9811 | 44.699 | 44.8832 | 45.0333 | 45.9328 | 45.2266 | 123.0882 | 60.7833 | 122.9736 | 60.5245 | 60.5966 | 121.2356 | 60.5607 | 121.0046 | 62.4916 | 62.5275 | 62.377 | 62.4129
8562.0938 | 123.2529 | -60.5942 | 62.4619 | -14.9136 | -14.9858 | -15.2038 | -14.983 | -14.8238 | -14.0525 | -14.7266 | 62.5032 | 0.23032 | 62.3886 | -0.023943 | 0.052814 | 60.7146 | 0.007721 | 60.4974 | 45.6806 | 45.6084 | 45.3904 | 45.6112 | 45.7704 | 46.5417 | 45.8676 | 123.0973 | 60.8245 | 122.9828 | 60.5702 | 60.647 | 121.3088 | 60.6019 | 121.0916 | 62.4503 | 62.4954 | 62.3358 | 62.3809
8563.0625 | 123.1888 | -60.6995 | 62.3978 | -14.355 | -14.3997 | -14.6406 | -14.4106 | -14.2561 | -13.4481 | -14.1543 | 62.4711 | 0.22574 | 62.3703 | -0.028522 | 0.052814 | 60.7467 | 0.012299 | 60.534 | 46.3445 | 46.2998 | 46.0588 | 46.2888 | 46.4433 | 47.2513 | 46.5451 | 123.1706 | 60.9252 | 123.0697 | 60.6709 | 60.7523 | 121.4461 | 60.7118 | 121.2335 | 62.4183 | 62.4588 | 62.3175 | 62.358
8564.1094 | 123.2162 | -60.6171 | 62.439 | -14.5381 | -14.5874 | -14.8192 | -14.5846 | -14.4392 | -13.5672 | -14.3466 | 62.4757 | 0.2349 | 62.3886 | -0.023943 | 0.052814 | 60.7421 | 0.007721 | 60.5203 | 46.0789 | 46.0296 | 45.7979 | 46.0324 | 46.1778 | 47.0499 | 46.2704 | 123.0928 | 60.852 | 123.0057 | 60.5931 | 60.6699 | 121.3592 | 60.6248 | 121.1373 | 62.4229 | 62.468 | 62.3358 | 62.3809
8565.0625 | 123.2391 | -60.5988 | 62.4619 | -14.909 | -14.972 | -15.2038 | -14.9601 | -14.8055 | -13.9838 | -14.7037 | 62.5077 | 0.2349 | 62.4115 | -0.028522 | 0.052814 | 60.7146 | 0.012299 | 60.4974 | 45.6898 | 45.6267 | 45.395 | 45.6387 | 45.7933 | 46.615 | 45.895 | 123.1065 | 60.8337 | 123.0102 | 60.5702 | 60.6516 | 121.3134 | 60.6111 | 121.0961 | 62.4549 | 62.4954 | 62.3587 | 62.3992
8566.0781 | 123.2849 | -60.553 | 62.4573 | -15.0143 | -15.0774 | -15.2908 | -15.0974 | -14.9428 | -14.0662 | -14.8502 | 62.5032 | 0.2349 | 62.4115 | -0.023943 | 0.048236 | 60.7009 | 0.021456 | 60.4882 | 45.5387 | 45.4756 | 45.2622 | 45.4556 | 45.6102 | 46.4868 | 45.7028 | 123.0561 | 60.7879 | 122.9645 | 60.529 | 60.6012 | 121.2539 | 60.5744 | 121.0412 | 62.4549 | 62.4817 | 62.3632 | 62.39
8567.0625 | 123.3124 | -60.5896 | 62.4619 | -14.7579 | -14.8118 | -15.0756 | -14.8456 | -14.6956 | -13.8693 | -14.5572 | 62.494 | 0.2349 | 62.3886 | -0.028522 | 0.048236 | 60.7192 | 0.016878 | 60.5065 | 45.8317 | 45.7778 | 45.514 | 45.744 | 45.894 | 46.7203 | 46.0324 | 123.0836 | 60.8245 | 122.9782 | 60.5611 | 60.6378 | 121.3088 | 60.6065 | 121.0961 | 62.4458 | 62.4771 | 62.3404 | 62.3717
8568.0781 | 123.3353 | -60.5804 | 62.439 | -14.7533 | -14.8164 | -15.0802 | -14.7678 | -14.6132 | -13.6954 | -14.516 | 62.4848 | 0.23032 | 62.3932 | -0.019364 | 0.048236 | 60.7284 | 0.016878 | 60.5065 | 45.8271 | 45.7641 | 45.5003 | 45.8127 | 45.9672 | 46.8851 | 46.0644 | 123.0653 | 60.8108 | 122.9736 | 60.5611 | 60.6287 | 121.3088 | 60.5973 | 121.087 | 62.4366 | 62.468 | 62.3449 | 62.3763
8569.0625 | 123.2712 | -60.5988 | 62.384 | -14.8174 | -14.8805 | -15.1443 | -14.8548 | -14.7002 | -13.9014 | -14.6396 | 62.5077 | 0.24405 | 62.4161 | -0.023943 | 0.052814 | 60.7192 | 0.007721 | 60.4974 | 45.7813 | 45.7183 | 45.4545 | 45.744 | 45.8986 | 46.6974 | 45.9591 | 123.1065 | 60.8428 | 123.0148 | 60.5748 | 60.6516 | 121.318 | 60.6065 | 121.0961 | 62.4549 | 62.5 | 62.3632 | 62.4083
8570.0938 | 123.3032 | -60.5988 | 62.4481 | -14.5931 | -14.6561 | -14.8879 | -14.6167 | -14.4484 | -13.6404 | -14.3878 | 62.4894 | 0.23032 | 62.3886 | -0.023943 | 0.052814 | 60.733 | 0.016878 | 60.5111 | 46.0057 | 45.9427 | 45.7109 | 45.9821 | 46.1504 | 46.9583 | 46.2109 | 123.0882 | 60.8291 | 122.9873 | 60.5748 | 60.6516 | 121.3317 | 60.6156 | 121.1099 | 62.4366 | 62.4725 | 62.3358 | 62.3717
8571.0625 | 123.2254 | -60.6216 | 62.439 | -14.6022 | -14.6607 | -14.9108 | -14.5205 | -14.3385 | -13.3566 | -14.3787 | 62.4757 | 0.2349 | 62.3703 | -0.023943 | 0.048236 | 60.7421 | 0.012299 | 60.5203 | 46.0194 | 45.961 | 45.7109 | 46.1011 | 46.2831 | 47.2651 | 46.243 | 123.0973 | 60.8565 | 122.9919 | 60.5977 | 60.6699 | 121.3638 | 60.6339 | 121.1419 | 62.4275 | 62.4634 | 62.322 | 62.358
8572.1094 | 123.3353 | -60.5759 | 62.471 | -14.5931 | -14.6515 | -14.9016 | -14.6396 | -14.485 | -13.6267 | -14.4107 | 62.4803 | 0.2349 | 62.3749 | -0.023943 | 0.048236 | 60.733 | 0.012299 | 60.5111 | 45.9828 | 45.9243 | 45.6743 | 45.9363 | 46.0908 | 46.9492 | 46.1652 | 123.0561 | 60.8108 | 122.9507 | 60.5519 | 60.6241 | 121.3088 | 60.5882 | 121.087 | 62.432 | 62.468 | 62.3266 | 62.3626
8573.0625 | 123.2437 | -60.5988 | 62.4664 | -13.9658 | -14.0059 | -14.3018 | -14.0947 | -13.9448 | -13.0864 | -13.7698 | 62.4528 | 0.24405 | 62.3611 | -0.023943 | 0.048236 | 60.7604 | 0.012299 | 60.5477 | 46.6329 | 46.5928 | 46.2969 | 46.504 | 46.6539 | 47.5123 | 46.829 | 123.0516 | 60.8428 | 122.9599 | 60.5748 | 60.647 | 121.3592 | 60.6111 | 121.1465 | 62.4046 | 62.4405 | 62.3129 | 62.3488
8574.0938 | 123.1659 | -60.6491 | 62.4115 | -14.2497 | -14.3035 | -14.5903 | -14.3969 | -14.247 | -13.439 | -14.0307 | 62.462 | 0.2349 | 62.3749 | -0.033101 | 0.048236 | 60.7513 | 0.016878 | 60.5294 | 46.3994 | 46.3456 | 46.0588 | 46.2522 | 46.4021 | 47.2101 | 46.6184 | 123.1111 | 60.884 | 123.024 | 60.616 | 60.6973 | 121.4004 | 60.666 | 121.1785 | 62.4137 | 62.4451 | 62.3266 | 62.358
8575.0625 | 123.2162 | -60.6308 | 62.4435 | -14.648 | -14.6927 | -14.984 | -14.6808 | -14.5308 | -13.6954 | -14.4382 | 62.4848 | 0.23032 | 62.3749 | -0.019364 | 0.052814 | 60.7238 | 0.012299 | 60.5157 | 45.9828 | 45.9381 | 45.6468 | 45.95 | 46.1 | 46.9354 | 46.1926 | 123.1156 | 60.8611 | 123.0057 | 60.6114 | 60.6836 | 121.3546 | 60.6431 | 121.1465 | 62.432 | 62.4725 | 62.322 | 62.3626
8576.0938 | 123.2391 | -60.6125 | 62.4619 | -13.7873 | -13.8273 | -14.1736 | -13.8795 | -13.7297 | -12.8484 | -13.6004 | 62.4345 | 0.23032 | 62.3291 | -0.028522 | 0.048236 | 60.7742 | 0.007721 | 60.5569 | 46.8252 | 46.7851 | 46.4389 | 46.7329 | 46.8828 | 47.7641 | 47.0121 | 123.047 | 60.8428 | 122.9416 | 60.584 | 60.6607 | 121.3866 | 60.6202 | 121.1694 | 62.3862 | 62.4268 | 62.2808 | 62.3213
8577.0625 | 123.3307 | -60.6216 | 62.3886 | -14.6022 | -14.6607 | -14.9428 | -14.6625 | -14.4942 | -13.6725 | -14.4016 | 62.4848 | 0.23032 | 62.3886 | -0.028522 | 0.048236 | 60.733 | 0.003143 | 60.5111 | 46.0194 | 45.961 | 45.6788 | 45.9592 | 46.1275 | 46.9492 | 46.2201 | 123.1065 | 60.852 | 123.0102 | 60.5931 | 60.6699 | 121.3546 | 60.6248 | 121.1328 | 62.4366 | 62.4817 | 62.3404 | 62.3854
8578.0938 | 123.2986 | -60.5347 | 62.4847 | -15.3897 | -15.4574 | -15.7487 | -15.7476 | -15.5837 | -14.4279 | -15.2027 | 62.5306 | 0.23948 | 62.4389 | -0.019364 | 0.052814 | 60.6872 | 0.007721 | 60.4608 | 45.1449 | 45.0773 | 44.786 | 44.7871 | 44.9509 | 46.1068 | 45.3319 | 123.0653 | 60.7741 | 122.9736 | 60.5153 | 60.5875 | 121.2218 | 60.5424 | 120.9954 | 62.4778 | 62.5229 | 62.3861 | 62.4312
8579.0625 | 123.2162 | -60.5759 | 62.4985 | -15.2341 | -15.3155 | -15.6113 | -15.5782 | -15.4006 | -14.2356 | -15.0745 | 62.5215 | 0.23032 | 62.4252 | -0.023943 | 0.057392 | 60.6917 | 0.012299 | 60.4699 | 45.3418 | 45.2604 | 44.9646 | 44.9977 | 45.1753 | 46.3403 | 45.5013 | 123.0973 | 60.8062 | 123.0011 | 60.5519 | 60.6333 | 121.2676 | 60.5882 | 121.0458 | 62.4641 | 62.5092 | 62.3678 | 62.4129
8580.0781 | 123.3856 | -60.5026 | 62.4847 | -15.4447 | -15.494 | -15.8128 | -15.7293 | -15.5837 | -14.4416 | -15.2439 | 62.5261 | 0.23032 | 62.4298 | -0.023943 | 0.048236 | 60.6734 | 0.007721 | 60.4608 | 45.058 | 45.0086 | 44.6899 | 44.7734 | 44.9189 | 46.061 | 45.2587 | 123.0287 | 60.7329 | 122.9324 | 60.4787 | 60.5509 | 121.1761 | 60.5103 | 120.9634 | 62.4778 | 62.5183 | 62.3816 | 62.4221
8581.0625 | 123.2529 | -60.5438 | 62.4985 | -15.2707 | -15.3246 | -15.6525 | -15.6011 | -15.4281 | -14.3592 | -15.0883 | 62.5306 | 0.23948 | 62.4252 | -0.023943 | 0.048236 | 60.6917 | 0.012299 | 60.4699 | 45.2731 | 45.2192 | 44.8913 | 44.9428 | 45.1157 | 46.1846 | 45.4555 | 123.0745 | 60.7833 | 122.969 | 60.5199 | 60.5921 | 121.2356 | 60.5561 | 121.0137 | 62.4824 | 62.5183 | 62.377 | 62.4129
8582.1094 | 123.2391 | -60.5438 | 62.4985 | -15.3394 | -15.3933 | -15.68 | -15.6468 | -15.4647 | -14.4279 | -15.1386 | 62.5352 | 0.24405 | 62.4389 | -0.023943 | 0.048236 | 60.6826 | 0.012299 | 60.4653 | 45.2045 | 45.1505 | 44.8638 | 44.897 | 45.0791 | 46.1159 | 45.4052 | 123.079 | 60.7879 | 122.9828 | 60.5199 | 60.5921 | 121.2264 | 60.5561 | 121.0092 | 62.487 | 62.5229 | 62.3907 | 62.4267
8583.0625 | 123.1934 | -60.5713 | 62.5351 | -15.4035 | -15.4666 | -15.767 | -15.6789 | -15.5013 | -14.492 | -15.2027 | 62.5352 | 0.2349 | 62.4344 | -0.03768 | 0.052814 | 60.6917 | 0.021456 | 60.4608 | 45.1678 | 45.1047 | 44.8043 | 44.8924 | 45.07 | 46.0793 | 45.3686 | 123.1065 | 60.8062 | 123.0057 | 60.5336 | 60.6241 | 121.263 | 60.5927 | 121.0321 | 62.4824 | 62.5138 | 62.3816 | 62.4129
8584.0938 | 123.1888 | -60.6766 | 62.4161 | -14.4603 | -14.5554 | -14.8604 | -14.8502 | -14.659 | -13.613 | -14.2642 | 62.4757 | 0.22574 | 62.3794 | -0.023943 | 0.052814 | 60.7238 | 0.012299 | 60.5157 | 46.2163 | 46.1212 | 45.8162 | 45.8264 | 46.0176 | 47.0636 | 46.4124 | 123.1523 | 60.9023 | 123.056 | 60.6526 | 60.7294 | 121.4004 | 60.6889 | 121.1923 | 62.4229 | 62.4634 | 62.3266 | 62.3671
8585.0625 | 123.23 | -60.5896 | 62.5122 | -15.257 | -15.32 | -15.68 | -15.5599 | -15.3777 | -14.373 | -15.0288 | 62.5306 | 0.24863 | 62.4298 | -0.023943 | 0.048236 | 60.6917 | 0.016878 | 60.4653 | 45.3326 | 45.2696 | 44.9096 | 45.0297 | 45.2119 | 46.2166 | 45.5608 | 123.1202 | 60.8382 | 123.0194 | 60.5657 | 60.6378 | 121.2813 | 60.6065 | 121.0549 | 62.4824 | 62.5138 | 62.3816 | 62.4129
8586.0938 | 123.2986 | -60.5804 | 62.4527 | -15.0097 | -15.0682 | -15.3686 | -15.2485 | -15.0573 | -14.1486 | -14.777 | 62.5169 | 0.2349 | 62.4206 | -0.023943 | 0.048236 | 60.6963 | 0.007721 | 60.4837 | 45.5707 | 45.5122 | 45.2118 | 45.3319 | 45.5232 | 46.4318 | 45.8035 | 123.0973 | 60.8153 | 123.0011 | 60.5565 | 60.6287 | 121.2768 | 60.5882 | 121.0641 | 62.4687 | 62.5092 | 62.3724 | 62.4129
8587.0625 | 123.2071 | -60.6628 | 62.4481 | -14.474 | -14.5371 | -14.8421 | -14.6854 | -14.4804 | -13.5397 | -14.2688 | 62.4894 | 0.24405 | 62.3749 | -0.033101 | 0.043657 | 60.733 | 0.007721 | 60.5157 | 46.1888 | 46.1258 | 45.8207 | 45.9775 | 46.1824 | 47.1231 | 46.3941 | 123.1523 | 60.9069 | 123.0377 | 60.6297 | 60.7065 | 121.3958 | 60.6706 | 121.1785 | 62.4458 | 62.4817 | 62.3312 | 62.3671
8588.0938 | 123.2071 | -60.6354 | 62.4298 | -14.3642 | -14.4272 | -14.7276 | -14.5846 | -14.3706 | -13.4985 | -14.1589 | 62.4757 | 0.23032 | 62.3611 | -0.023943 | 0.052814 | 60.7421 | 0.007721 | 60.5249 | 46.2712 | 46.2082 | 45.9077 | 46.0507 | 46.2648 | 47.1369 | 46.4765 | 123.1111 | 60.8657 | 122.9965 | 60.6114 | 60.6882 | 121.3775 | 60.6431 | 121.1602 | 62.4229 | 62.468 | 62.3083 | 62.3534
8589.0625 | 123.2849 | -60.5988 | 62.3932 | -14.6206 | -14.6653 | -14.9886 | -14.8364 | -14.6132 | -13.5809 | -14.4107 | 62.4894 | 0.23032 | 62.3932 | -0.023943 | 0.048236 | 60.7192 | 0.007721 | 60.502 | 45.9782 | 45.9335 | 45.6101 | 45.7623 | 45.9856 | 47.0178 | 46.188 | 123.0882 | 60.8291 | 122.9919 | 60.5748 | 60.647 | 121.318 | 60.6065 | 121.1007 | 62.4412 | 62.4817 | 62.3449 | 62.3854
8590.0938 | 123.1796 | -60.6308 | 62.4527 | -14.3275 | -14.3905 | -14.7368 | -14.5617 | -14.3568 | -13.4344 | -14.104 | 62.4757 | 0.2349 | 62.3932 | -0.019364 | 0.052814 | 60.7421 | 0.016878 | 60.5294 | 46.3033 | 46.2403 | 45.894 | 46.0691 | 46.274 | 47.1964 | 46.5268 | 123.1065 | 60.8657 | 123.024 | 60.6114 | 60.6836 | 121.3729 | 60.6477 | 121.1602 | 62.4229 | 62.4588 | 62.3404 | 62.3763
8591.0625 | 123.2254 | -60.5942 | 62.4664 | -14.2222 | -14.2761 | -14.6132 | -14.4015 | -14.1875 | -13.3383 | -14.017 | 62.462 | 0.23948 | 62.3611 | -0.023943 | 0.057392 | 60.7421 | 0.012299 | 60.5294 | 46.3719 | 46.3181 | 45.981 | 46.1927 | 46.4067 | 47.2559 | 46.5772 | 123.0561 | 60.8337 | 122.9553 | 60.5702 | 60.6516 | 121.3363 | 60.6065 | 121.1236 | 62.4046 | 62.4497 | 62.3037 | 62.3488
8592.1094 | 123.2208 | -60.7178 | 62.3657 | -14.1948 | -14.2577 | -14.6544 | -14.374 | -14.1417 | -13.2375 | -14.0124 | 62.4665 | 0.23948 | 62.3611 | -0.033101 | 0.052814 | 60.7558 | 0.012299 | 60.5294 | 46.523 | 46.46 | 46.0634 | 46.3438 | 46.5761 | 47.4802 | 46.7054 | 123.1843 | 60.9572 | 123.0789 | 60.6847 | 60.7706 | 121.4736 | 60.7301 | 121.2472 | 62.4137 | 62.4542 | 62.3083 | 62.3488
8593.0625 | 123.23 | -60.5942 | 62.4435 | -13.7964 | -13.864 | -14.1874 | -13.9436 | -13.7251 | -12.8438 | -13.6233 | 62.4436 | 0.23948 | 62.3428 | -0.023943 | 0.052814 | 60.7696 | 0.021456 | 60.5569 | 46.7977 | 46.7302 | 46.4068 | 46.6505 | 46.8691 | 47.7504 | 46.9709 | 123.0378 | 60.8337 | 122.937 | 60.5702 | 60.647 | 121.3638 | 60.6156 | 121.1511 | 62.3908 | 62.4222 | 62.29 | 62.3213
8594.0938 | 123.1796 | -60.6079 | 62.4115 | -14.2406 | -14.3035 | -14.6177 | -14.3923 | -14.1691 | -13.3291 | -14.0582 | 62.4665 | 0.23032 | 62.3703 | -0.023943 | 0.043657 | 60.7467 | 0.012299 | 60.5249 | 46.3674 | 46.3044 | 45.9902 | 46.2156 | 46.4388 | 47.2788 | 46.5497 | 123.0744 | 60.8382 | 122.9782 | 60.584 | 60.6516 | 121.3546 | 60.6202 | 121.1328 | 62.4229 | 62.4542 | 62.3266 | 62.358
8595.0625 | 123.1796 | -60.6491 | 62.439 | -14.3459 | -14.4226 | -14.7322 | -14.6121 | -14.3523 | -13.4344 | -14.1681 | 62.4803 | 0.23948 | 62.3749 | -0.028522 | 0.057392 | 60.7421 | 0.012299 | 60.5249 | 46.3033 | 46.2265 | 45.9169 | 46.037 | 46.2969 | 47.2147 | 46.481 | 123.1294 | 60.8886 | 123.024 | 60.6206 | 60.7065 | 121.3912 | 60.6614 | 121.174 | 62.4229 | 62.468 | 62.3175 | 62.3626
8596.0938 | 123.262 | -60.6491 | 62.3703 | -13.5996 | -13.6579 | -14.0408 | -13.9207 | -13.6885 | -12.7614 | -13.4218 | 62.4299 | 0.23032 | 62.3245 | -0.023943 | 0.057392 | 60.7879 | 0.012299 | 60.5615 | 47.0495 | 46.9912 | 46.6083 | 46.7284 | 46.9607 | 47.8877 | 47.2273 | 123.079 | 60.8794 | 122.9736 | 60.6252 | 60.7065 | 121.437 | 60.6614 | 121.2106 | 62.3725 | 62.4176 | 62.2671 | 62.3122
8597.0625 | 123.3582 | -60.6262 | 62.4115 | -14.3642 | -14.4134 | -14.7872 | -14.6533 | -14.3614 | -13.4664 | -14.1681 | 62.4711 | 0.2349 | 62.3703 | -0.028522 | 0.048236 | 60.7375 | 0.012299 | 60.5157 | 46.2621 | 46.2128 | 45.8391 | 45.9729 | 46.2648 | 47.1598 | 46.4582 | 123.0973 | 60.8611 | 122.9965 | 60.5977 | 60.6745 | 121.3638 | 60.6385 | 121.1419 | 62.4229 | 62.4588 | 62.322 | 62.358
8598.0938 | 123.2986 | -60.6125 | 62.3795 | -14.0712 | -14.1524 | -14.4529 | -14.3786 | -14.0913 | -13.0864 | -13.8842 | 62.4574 | 0.2349 | 62.3703 | -0.023943 | 0.043657 | 60.7467 | 0.012299 | 60.5386 | 46.5413 | 46.4601 | 46.1596 | 46.2339 | 46.5212 | 47.526 | 46.7283 | 123.0699 | 60.8474 | 122.9828 | 60.5885 | 60.6561 | 121.3592 | 60.6248 | 121.1511 | 62.4137 | 62.4451 | 62.3266 | 62.358
8599.0625 | 123.1979 | -60.6949 | 62.4207 | -14.0757 | -14.1387 | -14.5399 | -14.3099 | -14.0226 | -13.0452 | -13.8705 | 62.4528 | 0.23948 | 62.3611 | -0.023943 | 0.048236 | 60.7558 | 0.012299 | 60.534 | 46.6192 | 46.5562 | 46.155 | 46.385 | 46.6722 | 47.6497 | 46.8244 | 123.1477 | 60.9344 | 123.056 | 60.6709 | 60.7431 | 121.4507 | 60.7072 | 121.2289 | 62.4046 | 62.4405 | 62.3129 | 62.3488
8600.0938 | 123.3078 | -60.6628 | 62.352 | -13.4576 | -13.5389 | -13.8714 | -13.7788 | -13.4733 | -12.4867 | -13.2433 | 62.4253 | 0.23948 | 62.3199 | -0.028522 | 0.057392 | 60.7879 | 0.016878 | 60.5661 | 47.2052 | 47.124 | 46.7914 | 46.884 | 47.1896 | 48.1762 | 47.4196 | 123.0882 | 60.9023 | 122.9828 | 60.6343 | 60.7202 | 121.4507 | 60.6797 | 121.2289 | 62.3679 | 62.4085 | 62.2625 | 62.303
8601.0625 | 123.2483 | -60.5759 | 62.4893 | -15.0006 | -15.0682 | -15.3869 | -15.2073 | -14.8879 | -14.0387 | -14.777 | 62.5077 | 0.23948 | 62.4206 | -0.023943 | 0.048236 | 60.7055 | 0.007721 | 60.4837 | 45.5753 | 45.5077 | 45.1889 | 45.3686 | 45.688 | 46.5371 | 45.7989 | 123.0836 | 60.8153 | 122.9965 | 60.5519 | 60.6241 | 121.2814 | 60.5836 | 121.0595 | 62.4595 | 62.5 | 62.3724 | 62.4129
8602.0938 | 123.3261 | -60.5942 | 62.4069 | -14.561 | -14.6195 | -14.9474 | -14.7357 | -14.4255 | -13.5397 | -14.3146 | 62.4803 | 0.23032 | 62.3886 | -0.023943 | 0.052814 | 60.7375 | 0.007721 | 60.5065 | 46.0331 | 45.9747 | 45.6468 | 45.8585 | 46.1687 | 47.0545 | 46.2796 | 123.0744 | 60.8245 | 122.9828 | 60.5702 | 60.647 | 121.3317 | 60.6019 | 121.1007 | 62.4275 | 62.4725 | 62.3358 | 62.3809
8603.0625 | 123.2025 | -60.6583 | 62.439 | -14.0803 | -14.1341 | -14.4254 | -14.2825 | -14.041 | -13.1093 | -13.8522 | 62.4528 | 0.2349 | 62.352 | -0.028522 | 0.052814 | 60.765 | 0.012299 | 60.5386 | 46.578 | 46.5241 | 46.2328 | 46.3758 | 46.6173 | 47.5489 | 46.8061 | 123.1111 | 60.8932 | 123.0102 | 60.6297 | 60.7111 | 121.4233 | 60.6706 | 121.1969 | 62.4 | 62.4405 | 62.2991 | 62.3397
8604.0938 | 123.2254 | -60.6033 | 62.4664 | -13.9384 | -13.9876 | -14.311 | -14.1222 | -13.9219 | -12.9582 | -13.7148 | 62.4482 | 0.24405 | 62.3611 | -0.019364 | 0.052814 | 60.7604 | 0.012299 | 60.5432 | 46.665 | 46.6157 | 46.2924 | 46.4811 | 46.6814 | 47.6451 | 46.8885 | 123.0516 | 60.8474 | 122.9645 | 60.584 | 60.6561 | 121.3638 | 60.6156 | 121.1465 | 62.3954 | 62.4359 | 62.3083 | 62.3488
8605.0625 | 123.1979 | -60.6079 | 62.4527 | -14.4328 | -14.4867 | -14.7872 | -14.5617 | -14.3339 | -13.3932 | -14.136 | 62.4711 | 0.23948 | 62.3794 | -0.023943 | 0.048236 | 60.7375 | 0.012299 | 60.5203 | 46.1751 | 46.1212 | 45.8208 | 46.0462 | 46.274 | 47.2147 | 46.4719 | 123.079 | 60.8474 | 122.9873 | 60.584 | 60.6561 | 121.3454 | 60.6202 | 121.1282 | 62.4229 | 62.4588 | 62.3312 | 62.3671
8606.0938 | 123.2986 | -60.585 | 62.4481 | -14.4466 | -14.4958 | -14.8146 | -14.6258 | -14.3797 | -13.4344 | -14.2139 | 62.4665 | 0.23032 | 62.3749 | -0.014785 | 0.048236 | 60.7284 | 0.007721 | 60.5203 | 46.1384 | 46.0892 | 45.7704 | 45.9592 | 46.2053 | 47.1506 | 46.3712 | 123.0516 | 60.8153 | 122.9599 | 60.5702 | 60.6333 | 121.3134 | 60.5927 | 121.1053 | 62.4183 | 62.4588 | 62.3266 | 62.3671
8607.0625 | 123.1293 | -60.6537 | 62.4252 | -14.1719 | -14.212 | -14.5857 | -14.3878 | -14.1691 | -13.1872 | -13.9483 | 62.4482 | 0.23032 | 62.3565 | -0.033101 | 0.052814 | 60.7467 | 0.012299 | 60.5249 | 46.4818 | 46.4417 | 46.068 | 46.2659 | 46.4845 | 47.4665 | 46.7054 | 123.1019 | 60.884 | 123.0102 | 60.6206 | 60.7065 | 121.4004 | 60.666 | 121.1785 | 62.3954 | 62.4359 | 62.3037 | 62.3442
8608.0938 | 123.3994 | -60.5026 | 62.5076 | -14.9227 | -14.9858 | -15.3045 | -15.0516 | -14.8101 | -13.8785 | -14.6808 | 62.4986 | 0.23948 | 62.4069 | -0.019364 | 0.048236 | 60.7055 | 0.012299 | 60.4928 | 45.5799 | 45.5168 | 45.1981 | 45.451 | 45.6926 | 46.6241 | 45.8218 | 123.0012 | 60.7421 | 122.9095 | 60.4833 | 60.5509 | 121.2081 | 60.5149 | 120.9954 | 62.4503 | 62.4863 | 62.3587 | 62.3946
8609.0625 | 123.175 | -60.6491 | 62.4023 | -13.8239 | -13.864 | -14.1965 | -13.9894 | -13.6976 | -12.7385 | -13.6004 | 62.4391 | 0.23948 | 62.3428 | -0.019364 | 0.052814 | 60.7742 | 0.012299 | 60.5477 | 46.8252 | 46.7851 | 46.4526 | 46.6597 | 46.9515 | 47.9106 | 47.0487 | 123.0882 | 60.8886 | 122.9919 | 60.6297 | 60.7019 | 121.4233 | 60.6614 | 121.1969 | 62.3862 | 62.4268 | 62.29 | 62.3305
8610.0938 | 123.2254 | -60.6125 | 62.471 | -12.954 | -13.0123 | -13.3312 | -13.2065 | -12.9194 | -11.9144 | -12.7488 | 62.3933 | 0.2349 | 62.2833 | -0.023943 | 0.052814 | 60.8154 | 0.003143 | 60.5981 | 47.6585 | 47.6002 | 47.2813 | 47.406 | 47.6931 | 48.6981 | 47.8637 | 123.0058 | 60.8474 | 122.8958 | 60.5885 | 60.6653 | 121.4278 | 60.6156 | 121.2106 | 62.3405 | 62.3901 | 62.2305 | 62.2801
8611.0625 | 123.2162 | -60.5804 | 62.4573 | -15.028 | -15.1003 | -15.4327 | -15.1615 | -14.9153 | -13.993 | -14.7999 | 62.5077 | 0.2349 | 62.4069 | -0.023943 | 0.057392 | 60.7055 | 0.012299 | 60.4791 | 45.5524 | 45.4802 | 45.1477 | 45.4189 | 45.6651 | 46.5875 | 45.7806 | 123.0882 | 60.8153 | 122.9873 | 60.5565 | 60.6378 | 121.2859 | 60.5927 | 121.0595 | 62.4503 | 62.4954 | 62.3495 | 62.3946
8612.1094 | 123.2025 | -60.5484 | 62.4756 | -14.8586 | -14.9171 | -15.2221 | -14.9692 | -14.6636 | -13.7183 | -14.6122 | 62.4894 | 0.23948 | 62.3977 | -0.028522 | 0.052814 | 60.7146 | 0.012299 | 60.4928 | 45.6898 | 45.6313 | 45.3263 | 45.5792 | 45.8848 | 46.8301 | 45.9362 | 123.0378 | 60.7879 | 122.9461 | 60.5199 | 60.6012 | 121.263 | 60.5607 | 121.0412 | 62.4366 | 62.4771 | 62.3449 | 62.3854
8613.0625 | 123.2071 | -60.6216 | 62.439 | -14.5565 | -14.6103 | -15.0436 | -14.7907 | -14.2882 | -13.4298 | -14.3191 | 62.4848 | 0.23948 | 62.3886 | -0.023943 | 0.052814 | 60.733 | 0.012299 | 60.5157 | 46.0652 | 46.0113 | 45.5781 | 45.831 | 46.3335 | 47.1918 | 46.3025 | 123.1065 | 60.8611 | 123.0102 | 60.5977 | 60.6745 | 121.3546 | 60.6339 | 121.1373 | 62.432 | 62.4725 | 62.3358 | 62.3763
8614.0625 | 123.1934 | -60.6308 | 62.4527 | -14.8266 | -14.8667 | -15.2221 | -14.9967 | -14.4576 | -13.5534 | -14.5664 | 62.4803 | 0.2349 | 62.3886 | -0.028522 | 0.043657 | 60.7146 | 0.007721 | 60.4974 | 45.8042 | 45.7641 | 45.4087 | 45.6341 | 46.1732 | 47.0774 | 46.0644 | 123.1111 | 60.8657 | 123.0194 | 60.6023 | 60.6745 | 121.3454 | 60.6385 | 121.1282 | 62.4366 | 62.4725 | 62.3449 | 62.3809
8615.0938 | 123.2849 | -60.64 | 62.3657 | -13.4393 | -13.5114 | -13.8073 | -13.6689 | -13.2719 | -12.2532 | -13.1883 | 62.4116 | 0.2349 | 62.3062 | -0.019364 | 0.052814 | 60.7925 | 0.016878 | 60.5798 | 47.2006 | 47.1286 | 46.8326 | 46.971 | 47.3681 | 48.3868 | 47.4516 | 123.0515 | 60.8749 | 122.9461 | 60.6206 | 60.6928 | 121.4324 | 60.6568 | 121.2197 | 62.3588 | 62.3947 | 62.2534 | 62.2893
8616.0625 | 123.2391 | -60.6812 | 62.3795 | -14.3779 | -14.4867 | -14.7459 | -14.5572 | -13.954 | -13.0407 | -14.1543 | 62.4711 | 0.23948 | 62.3886 | -0.023943 | 0.048236 | 60.7513 | 0.012299 | 60.534 | 46.3032 | 46.1945 | 45.9352 | 46.124 | 46.7272 | 47.6405 | 46.5268 | 123.1523 | 60.9206 | 123.0697 | 60.6572 | 60.7294 | 121.4324 | 60.6935 | 121.2152 | 62.4229 | 62.4588 | 62.3404 | 62.3763
8617.1094 | 123.2346 | -60.5804 | 62.4802 | -14.9182 | -14.972 | -15.2771 | -14.9738 | -14.6361 | -13.7411 | -14.6625 | 62.4986 | 0.23948 | 62.4161 | -0.023943 | 0.043657 | 60.7146 | 0.012299 | 60.4974 | 45.6623 | 45.6084 | 45.3034 | 45.6066 | 45.9444 | 46.8393 | 45.9179 | 123.079 | 60.8199 | 122.9965 | 60.5565 | 60.6241 | 121.2951 | 60.5927 | 121.0778 | 62.4549 | 62.4863 | 62.3724 | 62.4038
8618.0625 | 123.2941 | -60.6262 | 62.4069 | -14.4191 | -14.4821 | -14.8055 | -14.5068 | -14.0959 | -13.2055 | -14.1681 | 62.462 | 0.23032 | 62.3657 | -0.023943 | 0.048236 | 60.7375 | 0.012299 | 60.5203 | 46.2071 | 46.1441 | 45.8208 | 46.1194 | 46.5303 | 47.4207 | 46.4582 | 123.0882 | 60.8565 | 122.9919 | 60.6023 | 60.6745 | 121.3638 | 60.6385 | 121.1465 | 62.4137 | 62.4497 | 62.3175 | 62.3534
8619.0781 | 123.2895 | -60.704 | 62.3108 | -12.487 | -12.5773 | -12.8779 | -12.7303 | -12.3334 | -11.3009 | -12.2819 | 62.3567 | 0.22574 | 62.2604 | -0.023943 | 0.048236 | 60.8382 | 0.012299 | 60.621 | 48.217 | 48.1267 | 47.8262 | 47.9737 | 48.3707 | 49.4032 | 48.4222 | 123.0607 | 60.9298 | 122.9644 | 60.6801 | 60.7523 | 121.5423 | 60.7163 | 121.325 | 62.3084 | 62.3444 | 62.2122 | 62.2481
8620.0625 | 123.23 | -60.7086 | 62.3383 | -14.4008 | -14.4867 | -14.7643 | -14.4656 | -14.0867 | -13.1917 | -14.1955 | 62.462 | 0.2349 | 62.3657 | -0.023943 | 0.048236 | 60.7467 | 0.012299 | 60.5203 | 46.3078 | 46.2219 | 45.9444 | 46.243 | 46.6219 | 47.5169 | 46.5131 | 123.1706 | 60.9435 | 123.0743 | 60.6847 | 60.7569 | 121.4553 | 60.7209 | 121.2289 | 62.4137 | 62.4497 | 62.3175 | 62.3534
8621.0781 | 123.2895 | -60.6674 | 62.3566 | -12.8396 | -12.9299 | -13.2304 | -13.0279 | -12.6264 | -11.5985 | -12.6298 | 62.3841 | 0.23948 | 62.2924 | -0.023943 | 0.052814 | 60.8382 | 0.007721 | 60.6118 | 47.8279 | 47.7375 | 47.437 | 47.6395 | 48.041 | 49.069 | 48.0376 | 123.0515 | 60.9069 | 122.9599 | 60.6435 | 60.7202 | 121.5057 | 60.6751 | 121.2793 | 62.3313 | 62.3764 | 62.2396 | 62.2847
8622.0625 | 123.2117 | -60.6674 | 62.4207 | -12.9403 | -12.9848 | -13.354 | -13.092 | -12.7362 | -11.6534 | -12.6893 | 62.3887 | 0.24405 | 62.2787 | -0.033101 | 0.048236 | 60.8245 | 0.016878 | 60.5981 | 47.7271 | 47.6826 | 47.3134 | 47.5754 | 47.9312 | 49.014 | 47.9781 | 123.0561 | 60.9115 | 122.9461 | 60.6343 | 60.7157 | 121.4919 | 60.6843 | 121.2655 | 62.3405 | 62.3718 | 62.2305 | 62.2618
8623.0938 | 123.3307 | -60.6033 | 62.3749 | -12.8075 | -12.8749 | -13.2625 | -13.4492 | -12.2922 | -11.5801 | -12.584 | 62.375 | 0.2349 | 62.2696 | -0.028522 | 0.052814 | 60.8291 | 0.012299 | 60.6027 | 47.7958 | 47.7284 | 47.3409 | 47.1542 | 48.3112 | 49.0232 | 48.0193 | 122.9783 | 60.8382 | 122.8729 | 60.5748 | 60.6561 | 121.4324 | 60.6156 | 121.206 | 62.3222 | 62.3627 | 62.2167 | 62.2573
8624.0625 | 123.2162 | -60.5621 | 62.4802 | -15.2203 | -15.2834 | -15.625 | -15.3996 | -14.7734 | -13.9197 | -14.9738 | 62.5077 | 0.23032 | 62.4161 | -0.019364 | 0.048236 | 60.6917 | 0.012299 | 60.4745 | 45.3418 | 45.2787 | 44.9371 | 45.1625 | 45.7887 | 46.6424 | 45.5883 | 123.0699 | 60.7925 | 122.9782 | 60.5428 | 60.6104 | 121.2539 | 60.5744 | 121.0366 | 62.4595 | 62.4954 | 62.3678 | 62.4038
8625.0938 | 123.3215 | -60.6674 | 62.352 | -12.9907 | -13.0627 | -13.441 | -13.2614 | -12.7134 | -11.7221 | -12.6802 | 62.3933 | 0.23948 | 62.2924 | -0.028522 | 0.043657 | 60.8245 | 0.012299 | 60.6073 | 47.6768 | 47.6047 | 47.2264 | 47.406 | 47.9541 | 48.9453 | 47.9873 | 123.0607 | 60.9069 | 122.9599 | 60.6389 | 60.7111 | 121.4919 | 60.6797 | 121.2747 | 62.3496 | 62.381 | 62.2488 | 62.2801
8626.0625 | 123.23 | -60.553 | 62.4985 | -14.3596 | -14.4455 | -14.7551 | -14.5663 | -13.9494 | -13.0498 | -14.0948 | 62.462 | 0.2349 | 62.3611 | -0.023943 | 0.052814 | 60.7421 | 0.016878 | 60.534 | 46.1934 | 46.1075 | 45.7979 | 45.9867 | 46.6036 | 47.5032 | 46.4582 | 123.0149 | 60.7879 | 122.9141 | 60.529 | 60.6058 | 121.2951 | 60.5699 | 121.087 | 62.4091 | 62.4451 | 62.3083 | 62.3442
8627.0938 | 123.2666 | -60.672 | 62.3428 | -13.769 | -13.8823 | -14.1553 | -13.9848 | -13.2673 | -12.2486 | -13.1288 | 62.4162 | 0.2349 | 62.3199 | -0.023943 | 0.048236 | 60.7879 | 0.012299 | 60.5661 | 46.903 | 46.7897 | 46.5167 | 46.6871 | 47.4047 | 48.4234 | 47.5432 | 123.0882 | 60.9069 | 122.9919 | 60.6481 | 60.7202 | 121.4599 | 60.6843 | 121.2381 | 62.3679 | 62.4039 | 62.2717 | 62.3076
8628.0625 | 123.2574 | -60.6308 | 62.4207 | -14.1719 | -14.244 | -14.572 | -14.3237 | -13.6793 | -12.679 | -13.8934 | 62.4436 | 0.23948 | 62.352 | -0.019364 | 0.057392 | 60.7558 | 0.012299 | 60.5386 | 46.4589 | 46.3868 | 46.0588 | 46.3071 | 46.9515 | 47.9518 | 46.7374 | 123.0744 | 60.8703 | 122.9828 | 60.6114 | 60.6882 | 121.3866 | 60.6431 | 121.1694 | 62.3862 | 62.4313 | 62.2946 | 62.3397
8629.0938 | 123.2208 | -60.6537 | 62.3932 | -13.7186 | -13.7999 | -14.0866 | -13.9391 | -13.1711 | -12.0792 | -13.4447 | 62.4253 | 0.24405 | 62.3336 | -0.028522 | 0.052814 | 60.7787 | 0.007721 | 60.5661 | 46.9351 | 46.8538 | 46.5671 | 46.7146 | 47.4825 | 48.5745 | 47.209 | 123.079 | 60.8977 | 122.9873 | 60.6252 | 60.7065 | 121.4324 | 60.6614 | 121.2197 | 62.3725 | 62.4176 | 62.2808 | 62.3259
8630.0625 | 123.2254 | -60.64 | 62.4115 | -14.4374 | -14.5233 | -14.7872 | -14.6808 | -13.8304 | -12.8484 | -14.191 | 62.4665 | 0.24405 | 62.3657 | -0.028522 | 0.048236 | 60.7467 | 0.016878 | 60.5294 | 46.2025 | 46.1166 | 45.8528 | 45.9592 | 46.8096 | 47.7916 | 46.449 | 123.1065 | 60.884 | 123.0057 | 60.6114 | 60.6882 | 121.3866 | 60.6568 | 121.1694 | 62.4183 | 62.4497 | 62.3175 | 62.3488
8631.0938 | 123.3307 | -60.5804 | 62.4252 | -13.9613 | -14.038 | -14.4071 | -14.4061 | -13.2032 | -12.2394 | -13.5683 | 62.4345 | 0.2349 | 62.3336 | -0.028522 | 0.048236 | 60.7742 | 0.016878 | 60.5477 | 46.6192 | 46.5425 | 46.1733 | 46.1744 | 47.3773 | 48.341 | 47.0121 | 123.0149 | 60.8153 | 122.9141 | 60.5519 | 60.6287 | 121.3546 | 60.5973 | 121.1282 | 62.3862 | 62.4176 | 62.2854 | 62.3168
8632.0625 | 123.3261 | -60.6583 | 62.3383 | -13.7095 | -13.7907 | -14.1233 | -14.0306 | -12.8782 | -11.8365 | -13.1334 | 62.4116 | 0.23948 | 62.3108 | -0.023943 | 0.048236 | 60.7833 | 0.007721 | 60.5661 | 46.9488 | 46.8676 | 46.535 | 46.6276 | 47.7801 | 48.8217 | 47.5249 | 123.0699 | 60.8977 | 122.969 | 60.6343 | 60.7065 | 121.4416 | 60.666 | 121.2243 | 62.3634 | 62.4039 | 62.2625 | 62.303
8633.0781 | 123.3398 | -60.6628 | 62.2925 | -13.3569 | -13.4793 | -13.7936 | -13.875 | -12.7454 | -11.7312 | -13.1242 | 62.407 | 0.2349 | 62.3108 | -0.023943 | 0.048236 | 60.8016 | 0.012299 | 60.5752 | 47.3059 | 47.1835 | 46.8692 | 46.7879 | 47.9174 | 48.9316 | 47.5386 | 123.0699 | 60.8977 | 122.9736 | 60.6389 | 60.7111 | 121.4645 | 60.6751 | 121.2381 | 62.3588 | 62.3947 | 62.2625 | 62.2985
8634.0625 | 123.3215 | -60.6903 | 62.2742 | -13.476 | -13.5847 | -13.9035 | -13.7513 | -12.9468 | -11.7587 | -13.2341 | 62.4024 | 0.23032 | 62.3108 | -0.028522 | 0.048236 | 60.797 | 0.012299 | 60.5706 | 47.2143 | 47.1056 | 46.7868 | 46.939 | 47.7435 | 48.9316 | 47.4562 | 123.0927 | 60.9206 | 123.0011 | 60.6618 | 60.7385 | 121.4874 | 60.7026 | 121.2609 | 62.3542 | 62.3901 | 62.2625 | 62.2985
8635.0938 | 123.317 | -60.5301 | 62.439 | -15.0143 | -15.0819 | -15.4694 | -15.4362 | -14.3202 | -13.4298 | -14.7312 | 62.494 | 0.2349 | 62.3886 | -0.019364 | 0.043657 | 60.7055 | 0.007721 | 60.4928 | 45.5158 | 45.4482 | 45.0607 | 45.0939 | 46.2099 | 47.1003 | 45.7989 | 123.0241 | 60.765 | 122.9187 | 60.5107 | 60.5737 | 121.2356 | 60.5378 | 121.0229 | 62.4503 | 62.4863 | 62.3449 | 62.3809
8636.0625 | 123.1796 | -60.1776 | 62.8784 | -21.6438 | -21.7441 | -21.8474 | -21.6218 | -20.7339 | -20.8972 | -21.3878 | 62.8649 | 0.2349 | 62.7686 | -0.019364 | 0.052814 | 60.3301 | 0.012299 | 60.1266 | 38.5338 | 38.4335 | 38.3303 | 38.5558 | 39.4437 | 39.2804 | 38.7898 | 123.0425 | 60.4125 | 122.9462 | 60.1582 | 60.2304 | 120.5077 | 60.1899 | 120.3042 | 62.812 | 62.8526 | 62.7158 | 62.7563
8637.0938 | 123.3215 | -60.173 | 62.8189 | -22.0009 | -22.0875 | -22.1587 | -21.8003 | -21.1826 | -21.3321 | -21.4474 | 62.8786 | 0.2349 | 62.7686 | -0.14758 | 0.048236 | 60.2889 | 0.003143 | 60.035 | 38.1721 | 38.0855 | 38.0143 | 38.3727 | 38.9905 | 38.8409 | 38.7257 | 123.0516 | 60.4079 | 122.9416 | 60.0255 | 60.2213 | 120.4619 | 60.1762 | 120.208 | 62.8304 | 62.8755 | 62.7203 | 62.7654
8638.0625 | 123.1888 | -60.2005 | 62.8693 | -21.7171 | -21.8036 | -21.9206 | -21.608 | -20.9216 | -21.0437 | -21.2276 | 62.8694 | 0.23948 | 62.7732 | -0.143 | 0.048236 | 60.3255 | 0.007721 | 60.0899 | 38.4834 | 38.3969 | 38.2799 | 38.5925 | 39.2789 | 39.1568 | 38.9729 | 123.0699 | 60.44 | 122.9737 | 60.0575 | 60.2487 | 120.526 | 60.2082 | 120.2904 | 62.8212 | 62.8617 | 62.7249 | 62.7654
8639.0938 | 123.1842 | -60.2463 | 62.8052 | -21.0303 | -21.126 | -21.2613 | -21.0632 | -20.2029 | -20.3981 | -20.7332 | 62.8282 | 0.23948 | 62.7228 | -0.14758 | 0.048236 | 60.3621 | 0.007721 | 60.122 | 39.216 | 39.1203 | 38.985 | 39.1831 | 40.0434 | 39.8482 | 39.5131 | 123.0745 | 60.4858 | 122.9691 | 60.0987 | 60.2945 | 120.6084 | 60.254 | 120.3683 | 62.78 | 62.8205 | 62.6746 | 62.7151
8640.0625 | 123.1979 | -60.3607 | 62.7182 | -19.4965 | -19.5829 | -19.5168 | -19.3371 | -18.6784 | -18.782 | -19.1903 | 62.7458 | 0.2349 | 62.6358 | -0.14758 | 0.043657 | 60.4537 | 0.007721 | 60.209 | 40.8642 | 40.7778 | 40.8439 | 41.0236 | 41.6823 | 41.5788 | 41.1704 | 123.1065 | 60.5956 | 122.9965 | 60.2131 | 60.4044 | 120.8144 | 60.3684 | 120.5697 | 62.7022 | 62.7381 | 62.5922 | 62.6281

## Thermal Data
Fire Time | North 25 C
-0.3865 | 347.7329
0.6135 | 347.7939
1.6135 | 347.7322
2.6135 | 347.7837
3.6135 | 347.8136
4.6135 | 347.7679
5.6135 | 347.7384
6.6135 | 347.68
7.6135 | 347.6836
8.6135 | 347.7478
9.6135 | 348.0023
10.6135 | 348.0984
11.6135 | 348.1216
12.6135 | 348.1611
13.6135 | 348.2324
14.6135 | 348.1166
15.6135 | 348.1397
16.6135 | 348.2295
17.6135 | 348.2955
18.6135 | 348.3155
19.6135 | 348.3372
20.6135 | 348.3795
21.6135 | 348.2907
22.6135 | 348.2907
23.6135 | 348.4075
24.6135 | 348.51
25.6135 | 348.5415
26.6135 | 348.4564
27.6135 | 348.4133
28.6135 | 348.4394
29.6135 | 348.4946
30.6135 | 348.6016
31.6135 | 348.7565
32.6135 | 348.6129
33.6135 | 348.6489
34.6135 | 348.6937
35.6135 | 348.7082
36.6135 | 348.6486
37.6135 | 348.6994
38.6135 | 348.7344
39.6135 | 348.7911
40.6135 | 348.6698
41.6135 | 348.6232
42.6135 | 348.6304
43.6135 | 348.6414
44.6135 | 348.6366
45.6135 | 348.4824
46.6135 | 348.4538
47.6135 | 348.4473
48.6135 | 348.4516
49.6135 | 348.4366
50.6135 | 348.4632
51.6135 | 348.3862
52.6135 | 348.2918
53.6135 | 348.2647
54.6135 | 348.2907
55.6135 | 348.2918
56.6135 | 348.2602
57.6135 | 348.1981
58.6135 | 348.1827
59.6135 | 348.1303
60.6135 | 348.0805
61.6135 | 348.0341
62.6135 | 347.95
63.6135 | 347.9127
64.6135 | 347.892
65.6135 | 347.8622
66.6135 | 347.8393
67.6135 | 347.8992
68.6135 | 347.9147
69.6135 | 347.8942
70.6135 | 347.787
71.6135 | 347.7369
72.6135 | 347.7126
73.6135 | 347.7237
74.6135 | 347.8416
75.6135 | 347.9357
76.6135 | 347.9454
77.6135 | 347.8803
78.6135 | 347.8649
79.6135 | 347.9016
80.6135 | 347.9801
81.6135 | 347.9971
82.6135 | 347.9715
83.6135 | 347.9906
84.6135 | 348.0167
85.6135 | 348.1564
86.6135 | 348.2159
87.6135 | 348.318
88.6135 | 348.4285
89.6135 | 348.4907
90.6135 | 348.6098
91.6135 | 348.6621
92.6135 | 348.6732
93.6135 | 348.6557
94.6135 | 348.5104
95.6135 | 348.5487
96.6135 | 348.5185
97.6135 | 348.5458
98.6135 | 348.6076
99.6135 | 348.5411
100.6135 | 348.3814
101.6135 | 348.2425
102.6135 | 348.1684
103.6135 | 348.2372
104.6135 | 348.2113
105.6135 | 348.1951
106.6135 | 348.3677
107.6135 | 348.4318
108.6135 | 348.3389
109.6135 | 348.2442
110.6135 | 348.1794
111.6135 | 348.034
112.6135 | 348.0069
113.6135 | 347.9771
114.6135 | 347.9489
115.6135 | 347.88
116.6135 | 347.8772
117.6135 | 347.8808
118.6135 | 347.8376
119.6135 | 347.6805
120.6135 | 347.6714
121.6135 | 347.768
122.6135 | 347.754
123.6135 | 347.662
124.6135 | 347.7733
125.6135 | 347.8072
126.6135 | 347.8056
127.6135 | 347.8395
128.6135 | 347.7869
129.6135 | 347.698
130.6135 | 347.6933
131.6135 | 347.7416
132.6135 | 347.7849
133.6135 | 347.8136
134.6135 | 347.8862
135.6135 | 347.8485
136.6135 | 347.8385
137.6135 | 347.7806
138.6135 | 347.6718
139.6135 | 347.6602
140.6135 | 347.7216
141.6135 | 347.7089
142.6135 | 347.782
143.6135 | 347.89
144.6135 | 347.9604
145.6135 | 347.9904
146.6135 | 348.0551
147.6135 | 348.1305
148.6135 | 348.1581
149.6135 | 348.0847
150.6135 | 348.0247
151.6135 | 348.0662
152.6135 | 348.1008
153.6135 | 348.2125
154.6135 | 348.1486
155.6135 | 348.0797
156.6135 | 348.0969
157.6135 | 348.1441
158.6135 | 348.1386
159.6135 | 348.1153
160.6135 | 348.1361
161.6135 | 348.1589
162.6135 | 348.1525
163.6135 | 347.9996
164.6135 | 347.7801
165.6135 | 347.7052
166.6135 | 347.6278
167.6135 | 347.6067
168.6135 | 347.6317
169.6135 | 347.6793
170.6135 | 347.664
171.6135 | 347.6343
172.6135 | 347.6594
173.6135 | 347.5963
174.6135 | 347.5908
175.6135 | 347.5698
176.6135 | 347.5775
177.6135 | 347.5385
178.6135 | 347.5414
179.6135 | 347.5379
180.6135 | 347.5191
181.6135 | 347.4785
182.6135 | 347.5677
183.6135 | 347.633
184.6135 | 347.6967
185.6135 | 347.7988
186.6135 | 347.8362
187.6135 | 347.8501
188.6135 | 347.8501
189.6135 | 347.8321
190.6135 | 347.8725
191.6135 | 347.9432
192.6135 | 348.0019
193.6135 | 348.02
194.6135 | 347.9987
195.6135 | 347.9897
196.6135 | 348.1284
197.6135 | 348.1744
198.6135 | 348.1952
199.6135 | 348.1582
200.6135 | 348.2365
201.6135 | 348.2379
202.6135 | 348.1901
203.6135 | 348.1742
204.6135 | 348.1719
205.6135 | 348.2462
206.6135 | 348.3105
207.6135 | 348.3393
208.6135 | 348.3094
209.6135 | 348.4227
210.6135 | 348.3655
211.6135 | 348.4702
212.6135 | 348.4759
213.6135 | 348.3802
214.6135 | 348.3117
215.6135 | 348.3405
216.6135 | 348.3335
217.6135 | 348.3165
218.6135 | 348.2995
219.6135 | 348.2746
220.6135 | 348.2699
221.6135 | 348.2205
222.6135 | 348.2261
223.6135 | 348.2119
224.6135 | 348.167
225.6135 | 348.1534
226.6135 | 348.156
227.6135 | 348.1363
228.6135 | 348.0597
229.6135 | 348.0436
230.6135 | 347.9849
231.6135 | 347.9397
232.6135 | 347.947
233.6135 | 347.8604
234.6135 | 347.784
235.6135 | 347.7446
236.6135 | 347.7822
237.6135 | 347.791
238.6135 | 347.7116
239.6135 | 347.6656
240.6135 | 347.755
241.6135 | 347.7865
242.6135 | 347.679
243.6135 | 347.7019
244.6135 | 347.8416
245.6135 | 348.0296
246.6135 | 348.1287
247.6135 | 348.0714
248.6135 | 348.0319
249.6135 | 348.0525
250.6135 | 348.1286
251.6135 | 348.1279
252.6135 | 348.2085
253.6135 | 348.1874
254.6135 | 348.1924
255.6135 | 348.2334
256.6135 | 348.2338
257.6135 | 348.2118
258.6135 | 348.1635
259.6135 | 348.1444
260.6135 | 348.1569
261.6135 | 348.2435
262.6135 | 348.3004
263.6135 | 348.3242
264.6135 | 348.2636
265.6135 | 348.319
266.6135 | 348.5477
267.6135 | 348.6534
268.6135 | 348.6064
269.6135 | 348.5361
270.6135 | 348.5382
271.6135 | 348.5807
272.6135 | 348.5625
273.6135 | 348.6582
274.6135 | 348.6295
275.6135 | 348.5671
276.6135 | 348.5597
277.6135 | 348.5037
278.6135 | 348.3835
279.6135 | 348.3013
280.6135 | 348.2299
281.6135 | 348.1575
282.6135 | 348.2726
283.6135 | 348.2206
284.6135 | 348.1927
285.6135 | 348.1293
286.6135 | 348.2673
287.6135 | 348.3836
288.6135 | 348.5204
289.6135 | 348.5081
290.6135 | 348.53
291.6135 | 348.4058
292.6135 | 348.475
293.6135 | 348.5361
294.6135 | 348.5379
295.6135 | 348.4795
296.6135 | 348.5471
297.6135 | 348.5893
298.6135 | 348.6647
299.6135 | 348.6332
300.6135 | 348.5016
301.6135 | 348.3427
302.6135 | 348.2343
303.6135 | 348.1477
304.6135 | 348.0505
305.6135 | 348.0449
306.6135 | 348.0363
307.6135 | 347.9068
308.6135 | 347.8907
309.6135 | 347.8929
310.6135 | 347.957
311.6135 | 347.9652
312.6135 | 347.9041
313.6135 | 347.8195
314.6135 | 347.8446
315.6135 | 347.9557
316.6135 | 347.9583
317.6135 | 347.8027
318.6135 | 347.7694
319.6135 | 347.7571
320.6135 | 347.6997
321.6135 | 347.6299
322.6135 | 347.6708
323.6135 | 347.7077
324.6135 | 347.7955
325.6135 | 347.7885
326.6135 | 347.7797
327.6135 | 347.7568
328.6135 | 347.7199
329.6135 | 347.7239
330.6135 | 347.7121
331.6135 | 347.7283
332.6135 | 347.7695
333.6135 | 347.954
334.6135 | 348.0427
335.6135 | 347.9644
336.6135 | 347.9025
337.6135 | 347.9735
338.6135 | 348.0123
339.6135 | 348.0656
340.6135 | 348.1617
341.6135 | 348.1635
342.6135 | 348.1578
343.6135 | 348.2784
344.6135 | 348.3441
345.6135 | 348.321
346.6135 | 348.3943
347.6135 | 348.5215
348.6135 | 348.6984
349.6135 | 348.6642
350.6135 | 348.5901
351.6135 | 348.6011
352.6135 | 348.581
353.6135 | 348.6151
354.6135 | 348.5409
355.6135 | 348.4469
356.6135 | 348.4344
357.6135 | 348.463
358.6135 | 348.5281
359.6135 | 348.6256
360.6135 | 348.5828
361.6135 | 348.4726
362.6135 | 348.3757
363.6135 | 348.4148
364.6135 | 348.3914
365.6135 | 348.3547
366.6135 | 348.4312
367.6135 | 348.509
368.6135 | 348.5209
369.6135 | 348.4279
370.6135 | 348.4903
371.6135 | 348.5069
372.6135 | 348.4635
373.6135 | 348.4296
374.6135 | 348.4988
375.6135 | 348.4911
376.6135 | 348.3462
377.6135 | 348.3584
378.6135 | 348.3213
379.6135 | 348.3063
380.6135 | 348.1815
381.6135 | 348.1621
382.6135 | 348.1529
383.6135 | 348.0983
384.6135 | 348.067
385.6135 | 348.0387
386.6135 | 348.0692
387.6135 | 348.0889
388.6135 | 348.058
389.6135 | 348.135
390.6135 | 348.0903
391.6135 | 347.9895
392.6135 | 347.9938
393.6135 | 347.9388
394.6135 | 347.877
395.6135 | 347.8812
396.6135 | 347.9515
397.6135 | 348.0637
398.6135 | 348.0962
399.6135 | 348.1218
400.6135 | 348.2142
401.6135 | 348.2985
402.6135 | 348.2576
403.6135 | 348.2187
404.6135 | 348.1489
405.6135 | 348.1893
406.6135 | 348.1447
407.6135 | 348.085
408.6135 | 348.1246
409.6135 | 348.2002
410.6135 | 348.2265
411.6135 | 348.2494
412.6135 | 348.2074
413.6135 | 348.1731
414.6135 | 348.1209
415.6135 | 348.066
416.6135 | 348.0993
417.6135 | 348.2351
418.6135 | 348.3289
419.6135 | 348.3592
420.6135 | 348.3778
421.6135 | 348.3519
422.6135 | 348.3129
423.6135 | 348.2093
424.6135 | 348.0978
425.6135 | 348.0913
426.6135 | 348.2337
427.6135 | 348.3702
428.6135 | 348.4257
429.6135 | 348.5017
430.6135 | 348.4359
431.6135 | 348.3244
432.6135 | 348.3218
433.6135 | 348.3348
434.6135 | 348.3889
435.6135 | 348.463
436.6135 | 348.3366
437.6135 | 348.2762
438.6135 | 348.3255
439.6135 | 348.4334
440.6135 | 348.4698
441.6135 | 348.4366
442.6135 | 348.4247
443.6135 | 348.3748
444.6135 | 348.42
445.6135 | 348.4081
446.6135 | 348.3416
447.6135 | 348.4247
448.6135 | 348.4395
449.6135 | 348.4879
450.6135 | 348.3734
451.6135 | 348.3433
452.6135 | 348.3234
453.6135 | 348.3241
454.6135 | 348.3148
455.6135 | 348.2995
456.6135 | 348.1834
457.6135 | 348.0379
458.6135 | 347.9593
459.6135 | 348.0499
460.6135 | 348.1184
461.6135 | 348.1094
462.6135 | 348.1665
463.6135 | 348.205
464.6135 | 348.3014
465.6135 | 348.327
466.6135 | 348.3108
467.6135 | 348.3578
468.6135 | 348.3364
469.6135 | 348.3025
470.6135 | 348.2313
471.6135 | 348.1708
472.6135 | 348.1082
473.6135 | 348.0463
474.6135 | 347.9962
475.6135 | 347.9768
476.6135 | 348.0101
477.6135 | 347.9141
478.6135 | 347.93
479.6135 | 348.1084
480.6135 | 348.7255
481.6135 | 350.2908
482.6135 | 352.6756
483.6135 | 355.4871
484.6135 | 358.7324
485.6135 | 362.2267
486.6135 | 365.826
487.6135 | 369.2551
488.6135 | 372.3343
489.6135 | 374.9884
490.6135 | 377.2672
491.6135 | 378.9722
492.6135 | 380.4172
493.6135 | 381.5094
494.6135 | 382.3514
495.6135 | 383.0327
496.6135 | 383.374
497.6135 | 383.6377
498.6135 | 383.877
499.6135 | 383.9759
500.6135 | 383.8037
501.6135 | 383.492
502.6135 | 383.1873
503.6135 | 382.9006
504.6135 | 382.5613
505.6135 | 382.2437
506.6135 | 381.8458
507.6135 | 381.5414
508.6135 | 381.1267
509.6135 | 380.6881
510.6135 | 380.2491
511.6135 | 379.8023
512.6135 | 379.2843
513.6135 | 378.9198
514.6135 | 378.4181
515.6135 | 377.8525
516.6135 | 377.3877
517.6135 | 376.9518
518.6135 | 376.4152
519.6135 | 375.9253
520.6135 | 375.4757
521.6135 | 374.9984
522.6135 | 374.6277
523.6135 | 374.2916
524.6135 | 373.8242
525.6135 | 373.4373
526.6135 | 373.0945
527.6135 | 372.7745
528.6135 | 372.5623
529.6135 | 372.3401
530.6135 | 372.1273
531.6135 | 371.9662
532.6135 | 371.7858
533.6135 | 371.6152
534.6135 | 371.5961
535.6135 | 371.5299
536.6135 | 371.492
537.6135 | 371.4814
538.6135 | 371.4114
539.6135 | 371.4149
540.6135 | 371.399
541.6135 | 371.4535
542.6135 | 371.5439
543.6135 | 371.6334
544.6135 | 371.6667
545.6135 | 371.7787
546.6135 | 371.938
547.6135 | 372.0116
548.6135 | 372.0081
549.6135 | 372.0821
550.6135 | 372.1779
551.6135 | 372.2548
552.6135 | 372.2824
553.6135 | 372.3223
554.6135 | 372.4654
555.6135 | 372.5083
556.6135 | 372.6174
557.6135 | 372.668
558.6135 | 372.7809
559.6135 | 372.7564
560.6135 | 372.9665
561.6135 | 373.0655
562.6135 | 373.1627
563.6135 | 373.3335
564.6135 | 373.3909
565.6135 | 373.355
566.6135 | 373.4036
567.6135 | 373.4307
568.6135 | 373.6267
569.6135 | 373.6888
570.6135 | 373.6538
571.6135 | 373.6675
572.6135 | 373.701
573.6135 | 373.81
574.6135 | 373.9202
575.6135 | 374.0398
576.6135 | 374.1176
577.6135 | 374.0477
578.6135 | 374.0521
579.6135 | 374.0467
580.6135 | 374.0246
581.6135 | 373.9941
582.6135 | 373.8672
583.6135 | 373.7628
584.6135 | 373.7767
585.6135 | 373.85
586.6135 | 373.8128
587.6135 | 373.8519
588.6135 | 373.8344
589.6135 | 373.6525
590.6135 | 373.5056
591.6135 | 373.4327
592.6135 | 373.4257
593.6135 | 373.4258
594.6135 | 373.4577
595.6135 | 373.4528
596.6135 | 373.586
597.6135 | 373.6535
598.6135 | 373.6572
599.6135 | 373.5583
600.6135 | 373.4366
601.6135 | 373.5316
602.6135 | 373.4902
603.6135 | 373.4792
604.6135 | 373.4488
605.6135 | 373.4991
606.6135 | 373.5115
607.6135 | 373.5157
608.6135 | 373.5833
609.6135 | 373.5633
610.6135 | 373.5565
611.6135 | 373.5305
612.6135 | 373.5882
613.6135 | 373.5373
614.6135 | 373.3816
615.6135 | 373.2803
616.6135 | 373.136
617.6135 | 373.0196
618.6292 | 372.8546
619.6135 | 372.8522
620.6135 | 372.8806
621.6135 | 372.8218
622.6135 | 372.7341
623.6135 | 372.8468
624.6135 | 372.8887
625.6135 | 372.8269
626.6135 | 372.8595
627.6135 | 372.9427
628.6135 | 372.9513
629.6135 | 372.9295
630.6135 | 372.8748
631.6135 | 372.859
632.6135 | 372.926
633.6135 | 373.0183
634.6135 | 373.1529
635.6292 | 373.2468
636.6135 | 373.2887
637.6135 | 373.222
638.6135 | 373.2346
639.6135 | 373.2447
640.6135 | 373.2245
641.6135 | 373.2743
642.6135 | 373.2629
643.6135 | 373.3512
644.6135 | 373.3979
645.6135 | 373.3705
646.6135 | 373.3955
647.6135 | 373.4078
648.6135 | 373.4457
649.6135 | 373.4111
650.6135 | 373.328
651.6135 | 373.2691
652.6135 | 373.3165
653.6135 | 373.2554
654.6135 | 373.2726
655.6135 | 373.4109
656.6135 | 373.4227
657.6135 | 373.4791
658.6135 | 373.4749
659.6135 | 373.4419
660.6135 | 373.3579
661.6135 | 373.3075
662.6135 | 373.2442
663.6135 | 373.1341
664.6135 | 373.1481
665.6292 | 373.0802
666.6135 | 373.0531
667.6135 | 372.9745
668.6135 | 372.8955
669.6135 | 372.8056
670.6135 | 372.8678
671.6135 | 372.9939
672.6135 | 373.1575
673.6135 | 373.2761
674.6135 | 373.3393
675.6135 | 373.3406
676.6135 | 373.3144
677.6135 | 373.2682
678.6135 | 373.339
679.6135 | 373.3732
680.6135 | 373.3892
681.6135 | 373.3771
682.6135 | 373.3308
683.6135 | 373.263
684.6135 | 373.2064
685.6135 | 373.2254
686.6135 | 373.256
687.6135 | 373.2728
688.6135 | 373.4384
689.6135 | 373.5065
690.6135 | 373.5855
691.6135 | 373.6124
692.6135 | 373.5786
693.6135 | 373.6195
694.6135 | 373.7728
695.6135 | 373.7597
696.6135 | 373.6772
697.6135 | 373.5762
698.6135 | 373.4633
699.6135 | 373.467
700.6135 | 373.5329
701.6135 | 373.5922
702.6135 | 373.6699
703.6135 | 373.6774
704.6135 | 373.6412
705.6135 | 373.6479
706.6135 | 373.7242
707.6135 | 373.7517
708.6135 | 373.7206
709.6135 | 373.556
710.6135 | 373.4501
711.6135 | 373.4184
712.6135 | 373.4775
713.6135 | 373.4932
714.6135 | 373.4451
715.6135 | 373.4204
716.6135 | 373.4561
717.6135 | 373.5057
718.6135 | 373.4466
719.6135 | 373.41
720.6135 | 373.4113
721.6135 | 373.366
722.6135 | 373.294
723.6135 | 373.1126
724.6135 | 372.9789
725.6135 | 372.907
726.6135 | 372.9104
727.6135 | 372.9145
728.6135 | 372.9193
729.6135 | 372.8911
730.6135 | 372.8505
731.6135 | 372.7144
732.6135 | 372.615
733.6135 | 372.636
734.6135 | 372.6514
735.6135 | 372.6624
736.6135 | 372.6176
737.6135 | 372.6805
738.6135 | 372.7124
739.6135 | 372.6971
740.6135 | 372.8733
741.6135 | 373.0243
742.6135 | 373.1366
743.6135 | 373.2087
744.6135 | 373.2111
745.6135 | 373.23
746.6135 | 373.2461
747.6135 | 373.2076
748.6135 | 373.2897
749.6135 | 373.3522
750.6135 | 373.5456
751.6135 | 373.5426
752.6135 | 373.4797
753.6135 | 373.415
754.6135 | 373.448
755.6135 | 373.5036
756.6135 | 373.4347
757.6135 | 373.5689
758.6135 | 373.6496
759.6135 | 373.7572
760.6135 | 373.8752
761.6135 | 374.0092
762.6135 | 373.9767
763.6135 | 373.8851
764.6135 | 373.812
765.6135 | 373.7364
766.6135 | 373.6225
767.6135 | 373.6066
768.6135 | 373.5669
769.6135 | 373.5589
770.6135 | 373.5001
771.6135 | 373.4577
772.6135 | 373.5076
773.6135 | 373.4157
774.6135 | 373.4235
775.6135 | 373.4306
776.6135 | 373.3748
777.6135 | 373.2503
778.6135 | 373.2192
779.6135 | 373.2439
780.6135 | 373.2401
781.6135 | 373.2309
782.6135 | 373.2388
783.6135 | 373.2459
784.6135 | 373.2122
785.6135 | 373.1876
786.6135 | 373.2148
787.6135 | 373.2538
788.6135 | 373.2562
789.6135 | 373.2402
790.6135 | 373.1937
791.6135 | 373.1339
792.6135 | 373.1036
793.6135 | 373.1167
794.6135 | 373.1376
795.6135 | 373.1248
796.6135 | 373.1123
797.6135 | 373.0844
798.6135 | 372.9986
799.6135 | 372.9819
800.6135 | 373.0427
801.6135 | 372.935
802.6135 | 372.9177
803.6135 | 372.9614
804.6135 | 372.9592
805.6135 | 372.9287
806.6135 | 373.0053
807.6135 | 373.1137
808.6135 | 373.1727
809.6135 | 373.2071
810.6135 | 373.1715
811.6135 | 373.1577
812.6135 | 373.1795
813.6135 | 373.2012
814.6135 | 373.2602
815.6135 | 373.2394
816.6135 | 373.3833
817.6135 | 373.4931
818.6135 | 373.538
819.6135 | 373.5216
820.6135 | 373.4168
821.6135 | 373.4069
822.6135 | 373.4068
823.6135 | 373.4273
824.6135 | 373.4176
825.6135 | 373.4646
826.6135 | 373.443
827.6135 | 373.4143
828.6135 | 373.2736
829.6135 | 373.0778
830.6135 | 373.052
831.6135 | 373.018
832.6135 | 373.0259
833.6135 | 373.0676
834.6135 | 373.0097
835.6135 | 372.9401
836.6135 | 372.9328
837.6135 | 372.9343
838.6135 | 372.9042
839.6135 | 372.9058
840.6135 | 372.9328
841.6135 | 372.9592
842.6135 | 373.0002
843.6135 | 373.1077
844.6135 | 373.2231
845.6135 | 373.2853
846.6135 | 373.2638
847.6135 | 373.1945
848.6135 | 373.1758
849.6135 | 373.2617
850.6135 | 373.2568
851.6135 | 373.1649
852.6135 | 373.1651
853.6135 | 373.1852
854.6135 | 373.1964
855.6135 | 373.0978
856.6135 | 373.1526
857.6135 | 373.2315
858.6135 | 373.2062
859.6135 | 373.1513
860.6135 | 373.2258
861.6135 | 373.3662
862.6135 | 373.3707
863.6135 | 373.4475
864.6135 | 373.4516
865.6135 | 373.4975
866.6135 | 373.4911
867.6135 | 373.4206
868.6135 | 373.3845
869.6135 | 373.352
870.6135 | 373.2923
871.6135 | 373.2319
872.6135 | 373.2711
873.6135 | 373.2672
874.6135 | 373.2301
875.6135 | 373.3655
876.6135 | 373.4223
877.6135 | 373.3368
878.6135 | 373.4097
879.6135 | 373.4017
880.6135 | 373.406
881.6135 | 373.4121
882.6135 | 373.3239
883.6135 | 373.2999
884.6135 | 373.342
885.6135 | 373.3957
886.6135 | 373.3598
887.6135 | 373.396
888.6135 | 373.5015
889.6135 | 373.5574
890.6135 | 373.6971
891.6135 | 373.7729
892.6135 | 373.6904
893.6135 | 373.5247
894.6135 | 373.4135
895.6135 | 373.3421
896.6135 | 373.3693
897.6135 | 373.3967
898.6135 | 373.4606
899.6135 | 373.3944
900.6135 | 373.3571
901.6135 | 373.327
902.6135 | 373.2038
903.6135 | 373.1866
904.6135 | 373.2536
905.6135 | 373.3307
906.6135 | 373.2118
907.6135 | 373.1507
908.6135 | 373.1173
909.6135 | 373.0984
910.6135 | 373.0017
911.6135 | 373.0063
912.6135 | 373.0136
913.6135 | 372.9749
914.6135 | 372.9435
915.6135 | 372.8773
916.6135 | 372.8687
917.6135 | 373.009
918.6135 | 373.0478
919.6135 | 373.0245
920.6135 | 373.0191
921.6135 | 373.0388
922.6135 | 372.9858
923.6135 | 372.9926
924.6135 | 373.0408
925.6135 | 373.1974
926.6135 | 373.3596
927.6135 | 373.4324
928.6135 | 373.3865
929.6135 | 373.2187
930.6135 | 373.2023
931.6135 | 373.1021
932.6135 | 373.0915
933.6135 | 373.1406
934.6135 | 373.2786
935.6135 | 373.3272
936.6135 | 373.269
937.6135 | 373.3626
938.6135 | 373.3222
939.6135 | 373.1529
940.6135 | 373.1296
941.6135 | 373.0624
942.6135 | 372.9984
943.6135 | 373.0765
944.6135 | 373.0238
945.6135 | 372.9423
946.6135 | 372.9436
947.6135 | 373.0766
948.6135 | 373.2034
949.6135 | 373.2723
950.6135 | 373.3463
951.6135 | 373.2892
952.6135 | 373.1478
953.6135 | 373.0544
954.6135 | 373.0085
955.6135 | 373.0138
956.6135 | 373.0158
957.6135 | 373.0054
958.6135 | 373.1481
959.6135 | 373.242
960.6135 | 373.2614
961.6135 | 373.3065
962.6135 | 373.2776
963.6135 | 373.3986
964.6135 | 373.5205
965.6135 | 373.4332
966.6135 | 373.3393
967.6135 | 373.4214
968.6135 | 373.3929
969.6135 | 373.4168
970.6135 | 373.4161
971.6135 | 373.3803
972.6135 | 373.4058
973.6135 | 373.4348
974.6135 | 373.3887
975.6135 | 373.2543
976.6135 | 373.2436
977.6135 | 373.2671
978.6135 | 373.226
979.6135 | 373.2108
980.6135 | 373.2133
981.6135 | 373.157
982.6135 | 373.0793
983.6135 | 373.1183
984.6135 | 373.0636
985.6135 | 373.1558
986.6135 | 373.1222
987.6135 | 373.1668
988.6135 | 373.1056
989.6135 | 373.0477
990.6135 | 373.1186
991.6135 | 373.193
992.6135 | 373.2298
993.6135 | 373.2951
994.6135 | 373.41
995.6135 | 373.4628
996.6135 | 373.5251
997.6135 | 373.5586
998.6135 | 373.4225
999.6135 | 373.332
1000.6135 | 373.2542
1001.6135 | 373.2664
1002.6135 | 373.221
1003.6135 | 373.254
1004.6135 | 373.2329
1005.6135 | 373.2885
1006.6135 | 373.2158
1007.6135 | 373.1442
1008.6135 | 372.9288
1009.6135 | 372.7955
1010.6135 | 372.7692
1011.6135 | 372.8297
1012.6135 | 372.8484
1013.6135 | 372.8565
1014.6135 | 372.8743
1015.6135 | 372.9596
1016.6135 | 373.0538
1017.6135 | 373.0436
1018.6135 | 373.0522
1019.6135 | 373.1485
1020.6135 | 373.2039
1021.6135 | 373.1638
1022.6135 | 373.0752
1023.6135 | 373.0411
1024.6135 | 373.066
1025.6135 | 373.0011
1026.6135 | 372.9744
1027.6135 | 372.8903
1028.6135 | 372.9104
1029.6135 | 372.9396
1030.6135 | 372.8721
1031.6135 | 372.824
1032.6135 | 372.8624
1033.6135 | 372.9204
1034.6135 | 372.9908
1035.6135 | 372.9426
1036.6135 | 372.9393
1037.6135 | 372.835
1038.6135 | 372.7454
1039.6135 | 372.7863
1040.6135 | 372.9245
1041.6135 | 372.9278
1042.6135 | 373.0066
1043.6135 | 373.1061
1044.6135 | 373.1016
1045.6135 | 373.1712
1046.6135 | 373.1889
1047.6135 | 373.1072
1048.6135 | 373.0744
1049.6135 | 372.9733
1050.6135 | 372.9332
1051.6135 | 372.9178
1052.6135 | 373.0447
1053.6135 | 372.9978
1054.6135 | 373.0216
1055.6135 | 372.9123
1056.6135 | 372.9421
1057.6135 | 373.0203
1058.6135 | 373.0518
1059.6135 | 373.0423
1060.6135 | 373.1298
1061.6135 | 373.1443
1062.6135 | 373.238
1063.6135 | 373.1736
1064.6135 | 373.066
1065.6135 | 373.0316
1066.6135 | 373.0236
1067.6135 | 373.0374
1068.6135 | 373.0935
1069.6135 | 373.0792
1070.6135 | 373.0958
1071.6135 | 373.0189
1072.6135 | 372.9549
1073.6135 | 372.9712
1074.6135 | 372.9917
1075.6135 | 372.9687
1076.6135 | 372.753
1077.6135 | 372.7242
1078.6135 | 372.7129
1079.6135 | 372.7286
1080.6135 | 372.7334
1081.6135 | 372.7275
1082.6135 | 372.7085
1083.6135 | 372.8152
1084.6135 | 372.7533
1085.6135 | 372.6377
1086.6135 | 372.6057
1087.6135 | 372.5199
1088.6135 | 372.471
1089.6135 | 372.438
1090.6135 | 372.3753
1091.6135 | 372.3412
1092.6135 | 372.3237
1093.6135 | 372.4144
1094.6135 | 372.4065
1095.6135 | 372.4627
1096.6135 | 372.6193
1097.6135 | 372.6024
1098.6135 | 372.4853
1099.6135 | 372.537
1100.6135 | 372.5969
1101.6135 | 372.6892
1102.6135 | 372.7191
1103.6135 | 372.6404
1104.6135 | 372.4907
1105.6135 | 372.5164
1106.6135 | 372.5367
1107.6135 | 372.5626
1108.6135 | 372.553
1109.6135 | 372.4527
1110.6135 | 372.4276
1111.6135 | 372.3833
1112.6135 | 372.5438
1113.6135 | 372.6057
1114.6135 | 372.5749
1115.6135 | 372.6292
1116.6135 | 372.545
1117.6135 | 372.5134
1118.6135 | 372.4771
1119.6135 | 372.424
1120.6135 | 372.3471
1121.6135 | 372.3898
1122.6135 | 372.3728
1123.6135 | 372.4105
1124.6135 | 372.4243
1125.6135 | 372.4332
1126.6135 | 372.4604
1127.6135 | 372.3402
1128.6135 | 372.3038
1129.6135 | 372.3113
1130.6135 | 372.3013
1131.6135 | 372.3012
1132.6135 | 372.4665
1133.6135 | 372.5832
1134.6135 | 372.6612
1135.6135 | 372.6454
1136.6135 | 372.677
1137.6135 | 372.5751
1138.6135 | 372.6241
1139.6135 | 372.7204
1140.6135 | 372.7162
1141.6135 | 372.7001
1142.6135 | 372.5924
1143.6135 | 372.6153
1144.6135 | 372.7588
1145.6135 | 372.7383
1146.6135 | 372.7102
1147.6135 | 372.8285
1148.6135 | 372.7838
1149.6135 | 372.6702
1150.6135 | 372.6486
1151.6135 | 372.5865
1152.6135 | 372.5133
1153.6135 | 372.4687
1154.6135 | 372.3769
1155.6135 | 372.3194
1156.6135 | 372.3389
1157.6135 | 372.4205
1158.6135 | 372.4572
1159.6135 | 372.4153
1160.6135 | 372.4598
1161.6135 | 372.487
1162.6135 | 372.4474
1163.6135 | 372.5054
1164.6135 | 372.4497
1165.6135 | 372.4316
1166.6135 | 372.5125
1167.6135 | 372.4886
1168.6135 | 372.5271
1169.6135 | 372.6246
1170.6135 | 372.6277
1171.6135 | 372.5913
1172.6135 | 372.6335
1173.6135 | 372.6882
1174.6135 | 372.8041
1175.6135 | 372.882
1176.6135 | 372.8681
1177.6135 | 372.9099
1178.6135 | 372.9172
1179.6135 | 372.9217
1180.6135 | 372.868
1181.6135 | 372.7775
1182.6135 | 372.8393
1183.6135 | 372.8388
1184.6135 | 372.7992
1185.6135 | 372.7219
1186.6135 | 372.6776
1187.6135 | 372.6578
1188.6135 | 372.6955
1189.6135 | 372.6679
1190.6135 | 372.6049
1191.6135 | 372.56
1192.6135 | 372.532
1193.6135 | 372.4855
1194.6135 | 372.4598
1195.6135 | 372.4352
1196.6135 | 372.3544
1197.6135 | 372.3522
1198.6135 | 372.3369
1199.6135 | 372.4206
1200.6135 | 372.4241
1201.6135 | 372.4219
1202.6135 | 372.3891
1203.6135 | 372.3718
1204.6135 | 372.4883
1205.6135 | 372.5036
1206.6135 | 372.5216
1207.6135 | 372.5448
1208.6135 | 372.5344
1209.6135 | 372.4197
1210.6135 | 372.4728
1211.6135 | 372.4165
1212.6135 | 372.4184
1213.6135 | 372.5429
1214.6135 | 372.619
1215.6135 | 372.6104
1216.6135 | 372.5937
1217.6135 | 372.6314
1218.6135 | 372.5721
1219.6135 | 372.5072
1220.6135 | 372.5415
1221.6135 | 372.6231
1222.6135 | 372.583
1223.6135 | 372.5843
1224.6135 | 372.5672
1225.6135 | 372.5357
1226.6135 | 372.6025
1227.6135 | 372.5446
1228.6135 | 372.5737
1229.6135 | 372.5895
1230.6135 | 372.5871
1231.6135 | 372.4989
1232.6135 | 372.4233
1233.6135 | 372.383
1234.6135 | 372.3847
1235.6135 | 372.4128
1236.6135 | 372.4578
1237.6135 | 372.5287
1238.6135 | 372.5928
1239.6135 | 372.7141
1240.6135 | 372.8722
1241.6135 | 372.9399
1242.6135 | 372.9848
1243.6135 | 373.0653
1244.6135 | 373.0278
1245.6135 | 373.0282
1246.6135 | 373.1689
1247.6135 | 373.175
1248.6135 | 373.1758
1249.6135 | 373.2032
1250.6135 | 373.3108
1251.6135 | 373.4439
1252.6135 | 373.4554
1253.6135 | 373.4808
1254.6135 | 373.5234
1255.6135 | 373.5391
1256.6135 | 373.5934
1257.6135 | 373.5037
1258.6135 | 373.5549
1259.6135 | 373.5094
1260.6135 | 373.4949
1261.6135 | 373.4207
1262.6135 | 373.3732
1263.6135 | 373.4008
1264.6135 | 373.3593
1265.6135 | 373.2545
1266.6135 | 373.1734
1267.6135 | 373.1432
1268.6135 | 373.1028
1269.6135 | 373.0943
1270.6135 | 372.9645
1271.6135 | 372.9619
1272.6135 | 372.829
1273.6135 | 372.901
1274.6135 | 372.9786
1275.6135 | 372.9887
1276.6135 | 373.0049
1277.6135 | 373.0165
1278.6135 | 373.0067
1279.6135 | 372.8535
1280.6135 | 372.8411
1281.6135 | 372.8581
1282.6135 | 372.8684
1283.6135 | 372.8572
1284.6135 | 372.8913
1285.6135 | 372.8832
1286.6135 | 372.9512
1287.6135 | 373.0514
1288.6135 | 373.2239
1289.6135 | 373.3912
1290.6135 | 373.5319
1291.6135 | 373.6759
1292.6135 | 373.7166
1293.6135 | 373.6748
1294.6135 | 373.5724
1295.6135 | 373.5411
1296.6135 | 373.3811
1297.6135 | 373.2871
1298.6135 | 373.3105
1299.6135 | 373.2639
1300.6135 | 373.2274
1301.6135 | 373.1672
1302.6135 | 373.1865
1303.6135 | 373.1983
1304.6135 | 373.1927
1305.6135 | 373.2954
1306.6135 | 373.2907
1307.6135 | 373.2853
1308.6135 | 373.3235
1309.6135 | 373.2307
1310.6135 | 373.0461
1311.6135 | 372.9886
1312.6135 | 372.9986
1313.6135 | 373.0393
1314.6135 | 372.9838
1315.6135 | 372.9838
1316.6135 | 373.0013
1317.6135 | 373.0774
1318.6135 | 373.1133
1319.6135 | 373.1768
1320.6135 | 373.2654
1321.6135 | 373.4591
1322.6135 | 373.5573
1323.6135 | 373.6592
1324.6135 | 373.5759
1325.6135 | 373.4999
1326.6135 | 373.5017
1327.6135 | 373.5971
1328.6135 | 373.656
1329.6135 | 373.6664
1330.6135 | 373.6286
1331.6135 | 373.623
1332.6135 | 373.5162
1333.6135 | 373.3789
1334.6135 | 373.3565
1335.6135 | 373.4056
1336.6135 | 373.4162
1337.6135 | 373.449
1338.6135 | 373.3975
1339.6135 | 373.5628
1340.6135 | 373.7112
1341.6135 | 373.6502
1342.6135 | 373.6587
1343.6135 | 373.6171
1344.6135 | 373.5232
1345.6135 | 373.5171
1346.6135 | 373.4429
1347.6135 | 373.4714
1348.6135 | 373.5546
1349.6135 | 373.4798
1350.6135 | 373.5235
1351.6135 | 373.5514
1352.6135 | 373.6447
1353.6135 | 373.7473
1354.6135 | 373.7922
1355.6135 | 373.7544
1356.6135 | 373.7187
1357.6135 | 373.7608
1358.6135 | 373.7064
1359.6135 | 373.7997
1360.6135 | 373.7898
1361.6135 | 373.8389
1362.6135 | 373.932
1363.6135 | 373.8332
1364.6135 | 373.6042
1365.6135 | 373.4826
1366.6135 | 373.4686
1367.6135 | 373.4779
1368.6135 | 373.5491
1369.6135 | 373.558
1370.6135 | 373.4138
1371.6135 | 373.404
1372.6135 | 373.4843
1373.6135 | 373.4984
1374.6135 | 373.4739
1375.6135 | 373.4542
1376.6135 | 373.4144
1377.6135 | 373.4191
1378.6135 | 373.3996
1379.6135 | 373.375
1380.6135 | 373.374
1381.6135 | 373.284
1382.6135 | 373.1935
1383.6135 | 373.2182
1384.6135 | 373.1348
1385.6135 | 373.091
1386.6135 | 373.0158
1387.6135 | 373.1089
1388.6135 | 373.2679
1389.6135 | 373.3484
1390.6135 | 373.3133
1391.6135 | 373.283
1392.6135 | 373.2245
1393.6135 | 373.2968
1394.6135 | 373.3827
1395.6135 | 373.3213
1396.6135 | 373.3317
1397.6135 | 373.3574
1398.6135 | 373.3181
1399.6135 | 373.2119
1400.6135 | 373.2309
1401.6135 | 373.185
1402.6135 | 373.1387
1403.6135 | 373.0776
1404.6135 | 373.0845
1405.6135 | 373.0909
1406.6135 | 373.0658
1407.6135 | 373.1148
1408.6135 | 373.0498
1409.6135 | 373.0263
1410.6135 | 373.0403
1411.6135 | 373.2093
1412.6135 | 373.1903
1413.6135 | 373.1765
1414.6135 | 373.3007
1415.6135 | 373.4148
1416.6135 | 373.3788
1417.6135 | 373.3021
1418.6135 | 373.3372
1419.6135 | 373.3257
1420.6135 | 373.3363
1421.6135 | 373.4276
1422.6135 | 373.3676
1423.6135 | 373.3609
1424.6135 | 373.4469
1425.6135 | 373.4466
1426.6135 | 373.3971
1427.6135 | 373.3378
1428.6135 | 373.3649
1429.6135 | 373.3684
1430.6135 | 373.3907
1431.6135 | 373.4215
1432.6135 | 373.4643
1433.6135 | 373.4961
1434.6135 | 373.4625
1435.6135 | 373.4379
1436.6135 | 373.4735
1437.6135 | 373.55
1438.6135 | 373.4951
1439.6135 | 373.4286
1440.6135 | 373.5159
1441.6135 | 373.473
1442.6135 | 373.4088
1443.6135 | 373.5079
1444.6135 | 373.5261
1445.6135 | 373.5759
1446.6135 | 373.5295
1447.6135 | 373.4369
1448.6135 | 373.5173
1449.6135 | 373.4918
1450.6135 | 373.4631
1451.6135 | 373.4478
1452.6135 | 373.5429
1453.6135 | 373.596
1454.6135 | 373.6363
1455.6135 | 373.6571
1456.6135 | 373.7844
1457.6135 | 373.8265
1458.6135 | 373.8537
1459.6135 | 373.8006
1460.6135 | 373.7548
1461.6135 | 373.8062
1462.6135 | 373.8557
1463.6135 | 373.7472
1464.6135 | 373.7762
1465.6135 | 373.7623
1466.6135 | 373.8381
1467.6135 | 373.8354
1468.6135 | 373.752
1469.6135 | 373.7631
1470.6135 | 373.6353
1471.6135 | 373.5894
1472.6135 | 373.5625
1473.6135 | 373.4264
1474.6135 | 373.3246
1475.6135 | 373.2691
1476.6135 | 373.178
1477.6135 | 373.1269
1478.6135 | 373.1616
1479.6135 | 373.1371
1480.6135 | 373.1412
1481.6135 | 373.0828
1482.6135 | 373.0809
1483.6135 | 373.058
1484.6135 | 372.9567
1485.6135 | 373.0843
1486.6135 | 373.0717
1487.6135 | 373.1046
1488.6135 | 373.2772
1489.6135 | 373.2784
1490.6135 | 373.2865
1491.6135 | 373.2059
1492.6135 | 373.1702
1493.6135 | 373.0865
1494.6135 | 373.0062
1495.6135 | 373.0876
1496.6135 | 373.1382
1497.6135 | 373.0772
1498.6135 | 373.1315
1499.6135 | 373.2326
1500.6135 | 373.2899
1501.6135 | 373.308
1502.6135 | 373.2428
1503.6135 | 373.2035
1504.6135 | 373.3003
1505.6135 | 373.2898
1506.6135 | 373.2536
1507.6135 | 373.3071
1508.6135 | 373.3663
1509.6135 | 373.4036
1510.6135 | 373.3962
1511.6135 | 373.3551
1512.6135 | 373.2601
1513.6135 | 373.151
1514.6135 | 373.1168
1515.6135 | 373.1644
1516.6135 | 373.1019
1517.6135 | 373.0339
1518.6135 | 373.0325
1519.6135 | 373.1081
1520.6135 | 373.1212
1521.6135 | 373.1945
1522.6135 | 373.2614
1523.6135 | 373.2814
1524.6135 | 373.4097
1525.6135 | 373.5217
1526.6135 | 373.4334
1527.6135 | 373.3909
1528.6135 | 373.2986
1529.6135 | 373.2028
1530.6135 | 373.1861
1531.6135 | 373.164
1532.6135 | 373.1543
1533.6135 | 373.1752
1534.6135 | 373.1763
1535.6135 | 373.1805
1536.6135 | 373.2652
1537.6135 | 373.3651
1538.6135 | 373.4588
1539.6135 | 373.5561
1540.6135 | 373.6525
1541.6135 | 373.5234
1542.6135 | 373.463
1543.6135 | 373.3678
1544.6135 | 373.3727
1545.6135 | 373.3284
1546.6135 | 373.2862
1547.6135 | 373.3117
1548.6135 | 373.1598
1549.6135 | 373.2369
1550.6135 | 373.269
1551.6135 | 373.2982
1552.6135 | 373.2869
1553.6135 | 373.3469
1554.6135 | 373.4212
1555.6135 | 373.3966
1556.6135 | 373.3369
1557.6135 | 373.3239
1558.6135 | 373.3197
1559.6135 | 373.3632
1560.6135 | 373.4264
1561.6135 | 373.5043
1562.6135 | 373.6621
1563.6135 | 373.7747
1564.6135 | 373.7629
1565.6135 | 373.5989
1566.6135 | 373.5245
1567.6135 | 373.5567
1568.6135 | 373.5856
1569.6135 | 373.6008
1570.6135 | 373.576
1571.6135 | 373.4148
1572.6135 | 373.3433
1573.6135 | 373.2282
1574.6135 | 373.3008
1575.6135 | 373.4124
1576.6135 | 373.446
1577.6135 | 373.4466
1578.6135 | 373.4733
1579.6135 | 373.5108
1580.6135 | 373.4702
1581.6135 | 373.3616
1582.6135 | 373.3398
1583.6135 | 373.3082
1584.6135 | 373.3554
1585.6135 | 373.3667
1586.6135 | 373.3653
1587.6135 | 373.3692
1588.6135 | 373.3125
1589.6135 | 373.2614
1590.6135 | 373.2091
1591.6135 | 373.2763
1592.6135 | 373.3641
1593.6135 | 373.3638
1594.6135 | 373.4667
1595.6135 | 373.5264
1596.6135 | 373.5818
1597.6135 | 373.6189
1598.6135 | 373.6922
1599.6135 | 373.6804
1600.6135 | 373.6689
1601.6135 | 373.7513
1602.6135 | 373.8003
1603.6135 | 373.7962
1604.6135 | 373.9143
1605.6135 | 373.9744
1606.6135 | 373.9954
1607.6135 | 373.9799
1608.6135 | 373.9455
1609.6135 | 373.9815
1610.6135 | 373.9917
1611.6135 | 373.9878
1612.6135 | 373.9744
1613.6135 | 373.7821
1614.6135 | 373.6532
1615.6135 | 373.6024
1616.6135 | 373.5887
1617.6135 | 373.5869
1618.6135 | 373.5828
1619.6135 | 373.6792
1620.6135 | 373.5638
1621.6135 | 373.5875
1622.6135 | 373.6674
1623.6135 | 373.5795
1624.6135 | 373.4842
1625.6135 | 373.4384
1626.6135 | 373.5753
1627.6135 | 373.768
1628.6135 | 373.8823
1629.6135 | 373.8832
1630.6135 | 373.7683
1631.6135 | 373.69
1632.6135 | 373.6382
1633.6135 | 373.7807
1634.6135 | 373.8897
1635.6135 | 373.9308
1636.6135 | 374.0463
1637.6135 | 374.1262
1638.6135 | 374.1606
1639.6135 | 374.1974
1640.6135 | 374.2095
1641.6135 | 374.1314
1642.6135 | 374.0734
1643.6135 | 374.1307
1644.6135 | 374.1904
1645.6135 | 374.1494
1646.6135 | 374.0724
1647.6135 | 373.981
1648.6135 | 373.8393
1649.6135 | 373.8445
1650.6135 | 373.8512
1651.6135 | 373.7892
1652.6135 | 373.7832
1653.6135 | 373.7457
1654.6135 | 373.6741
1655.6135 | 373.605
1656.6292 | 373.6453
1657.6135 | 373.4793
1658.6135 | 373.4172
1659.6135 | 373.4892
1660.6135 | 373.539
1661.6135 | 373.5722
1662.6135 | 373.5411
1663.6135 | 373.5066
1664.6135 | 373.4853
1665.6135 | 373.425
1666.6135 | 373.4798
1667.6135 | 373.3485
1668.6135 | 373.408
1669.6135 | 373.4525
1670.6135 | 373.2853
1671.6135 | 373.2802
1672.6135 | 373.1613
1673.6135 | 373.2158
1674.6135 | 373.201
1675.6135 | 373.1696
1676.6135 | 373.1588
1677.6135 | 373.1098
1678.6135 | 373.1187
1679.6135 | 373.1545
1680.6135 | 373.1873
1681.6135 | 373.2206
1682.6135 | 373.3052
1683.6135 | 373.3681
1684.6135 | 373.2221
1685.6135 | 373.1967
1686.6292 | 373.1365
1687.6135 | 373.1955
1688.6135 | 373.0944
1689.6135 | 373.0652
1690.6135 | 373.1313
1691.6135 | 373.0875
1692.6135 | 373.0857
1693.6135 | 373.0295
1694.6135 | 373.0359
1695.6135 | 372.9514
1696.6135 | 372.957
1697.6135 | 373.0057
1698.6135 | 373.0226
1699.6135 | 372.9661
1700.6135 | 372.9586
1701.6135 | 372.8928
1702.6135 | 372.9527
1703.6135 | 373.0874
1704.6135 | 373.1567
1705.6135 | 373.0259
1706.6135 | 372.9364
1707.6135 | 372.9648
1708.6135 | 372.9506
1709.6135 | 372.9693
1710.6135 | 372.9405
1711.6135 | 372.8993
1712.6135 | 372.9013
1713.6135 | 372.9068
1714.6135 | 372.9501
1715.6135 | 372.9772
1716.6135 | 372.9876
1717.6135 | 373.086
1718.6135 | 373.1482
1719.6135 | 373.0916
1720.6135 | 373.1079
1721.6135 | 373.2433
1722.6135 | 373.2374
1723.6135 | 373.2635
1724.6135 | 373.383
1725.6135 | 373.4723
1726.6135 | 373.6291
1727.6135 | 373.7856
1728.6135 | 373.818
1729.6135 | 373.7864
1730.6135 | 373.8808
1731.6135 | 373.7941
1732.6135 | 373.8422
1733.6135 | 373.8148
1734.6135 | 373.6592
1735.6135 | 373.5627
1736.6135 | 373.5995
1737.6135 | 373.6843
1738.6135 | 373.7226
1739.6135 | 373.5715
1740.6135 | 373.5809
1741.6135 | 373.6249
1742.6135 | 373.596
1743.6135 | 373.5236
1744.6135 | 373.5236
1745.6135 | 373.446
1746.6135 | 373.3361
1747.6135 | 373.3449
1748.6135 | 373.3799
1749.6135 | 373.2927
1750.6135 | 373.2725
1751.6135 | 373.27
1752.6135 | 373.2098
1753.6135 | 373.1396
1754.6135 | 373.0772
1755.6135 | 373.069
1756.6135 | 372.964
1757.6135 | 372.8673
1758.6135 | 372.8148
1759.6135 | 372.7988
1760.6135 | 372.7452
1761.6135 | 372.7237
1762.6135 | 372.8202
1763.6135 | 372.8335
1764.6135 | 372.9088
1765.6135 | 372.9272
1766.6135 | 372.977
1767.6135 | 372.963
1768.6135 | 373.0156
1769.6135 | 372.9949
1770.6135 | 373.176
1771.6135 | 373.1682
1772.6135 | 373.1062
1773.6135 | 373.1487
1774.6135 | 373.2453
1775.6135 | 373.2859
1776.6135 | 373.3666
1777.6135 | 373.6179
1778.6135 | 373.7738
1779.6135 | 373.752
1780.6135 | 373.6546
1781.6135 | 373.6215
1782.6135 | 373.5778
1783.6135 | 373.6322
1784.6135 | 373.6857
1785.6135 | 373.6651
1786.6135 | 373.7406
1787.6135 | 373.8818
1788.6135 | 373.9189
1789.6135 | 373.8635
1790.6135 | 373.7458
1791.6135 | 373.7361
1792.6135 | 373.7443
1793.6292 | 373.7565
1794.6135 | 373.829
1795.6135 | 373.7916
1796.6135 | 373.7025
1797.6135 | 373.6496
1798.6135 | 373.6179
1799.6135 | 373.6024
1800.6135 | 373.6
1801.6135 | 373.5986
1802.6135 | 373.607
1803.6135 | 373.5623
1804.6135 | 373.5822
1805.6135 | 373.6692
1806.6135 | 373.6742
1807.6135 | 373.6422
1808.6135 | 373.5802
1809.6135 | 373.5985
1810.6135 | 373.5263
1811.6135 | 373.4829
1812.6135 | 373.5451
1813.6135 | 373.6955
1814.6135 | 373.7267
1815.6135 | 373.7168
1816.6135 | 373.5949
1817.6135 | 373.455
1818.6135 | 373.346
1819.6135 | 373.2872
1820.6135 | 373.3432
1821.6135 | 373.3701
1822.6135 | 373.3735
1823.6135 | 373.3406
1824.6135 | 373.2537
1825.6135 | 373.1764
1826.6135 | 373.1327
1827.6135 | 373.111
1828.6135 | 373.0348
1829.6135 | 373.0031
1830.6135 | 372.993
1831.6135 | 372.8463
1832.6135 | 372.8446
1833.6135 | 373.0082
1834.6135 | 373.056
1835.6135 | 373.047
1836.6135 | 373.1368
1837.6135 | 373.0871
1838.6135 | 372.915
1839.6135 | 372.8925
1840.6135 | 372.8829
1841.6135 | 372.8328
1842.6135 | 372.8539
1843.6135 | 372.9715
1844.6135 | 372.9796
1845.6135 | 372.8539
1846.6135 | 372.8557
1847.6135 | 372.8312
1848.6135 | 372.924
1849.6135 | 372.9282
1850.6135 | 373.0051
1851.6135 | 373.0427
1852.6135 | 373.0431
1853.6135 | 372.9256
1854.6135 | 372.8989
1855.6135 | 372.9062
1856.6135 | 372.8495
1857.6135 | 372.8814
1858.6135 | 372.8954
1859.6135 | 372.9826
1860.6135 | 373.1011
1861.6135 | 373.2285
1862.6135 | 373.1977
1863.6135 | 373.2456
1864.6135 | 373.1763
1865.6135 | 373.1592
1866.6292 | 373.1775
1867.6135 | 373.211
1868.6135 | 373.1994
1869.6135 | 373.1802
1870.6135 | 373.1995
1871.6135 | 373.1332
1872.6135 | 373.1828
1873.6135 | 373.1994
1874.6135 | 373.2907
1875.6135 | 373.2159
1876.6135 | 373.2474
1877.6135 | 373.2349
1878.6135 | 373.1525
1879.6135 | 373.1781
1880.6135 | 373.1458
1881.6135 | 373.0557
1882.6135 | 373.048
1883.6135 | 373.073
1884.6135 | 372.959
1885.6135 | 372.892
1886.6135 | 372.8816
1887.6135 | 372.7952
1888.6135 | 372.6685
1889.6135 | 372.6646
1890.6135 | 372.7537
1891.6135 | 372.7567
1892.6135 | 372.8161
1893.6135 | 372.9426
1894.6135 | 373.0126
1895.6135 | 373.0801
1896.6135 | 373.0666
1897.6135 | 373.0983
1898.6135 | 373.256
1899.6135 | 373.2184
1900.6135 | 373.2502
1901.6135 | 373.269
1902.6135 | 373.2579
1903.6135 | 373.3082
1904.6135 | 373.2712
1905.6135 | 373.2077
1906.6135 | 373.144
1907.6135 | 373.0465
1908.6135 | 372.902
1909.6135 | 372.774
1910.6135 | 372.7607
1911.6135 | 372.8504
1912.6135 | 372.8198
1913.6135 | 372.7253
1914.6135 | 372.599
1915.6135 | 372.6176
1916.6135 | 372.6305
1917.6135 | 372.7196
1918.6135 | 372.6776
1919.6135 | 372.5159
1920.6135 | 372.3789
1921.6135 | 372.3253
1922.6135 | 372.4181
1923.6135 | 372.47
1924.6135 | 372.5274
1925.6135 | 372.5802
1926.6135 | 372.559
1927.6135 | 372.5682
1928.6135 | 372.5792
1929.6135 | 372.464
1930.6135 | 372.4286
1931.6135 | 372.4944
1932.6135 | 372.4389
1933.6135 | 372.4042
1934.6135 | 372.3856
1935.6135 | 372.374
1936.6135 | 372.3268
1937.6135 | 372.294
1938.6135 | 372.3663
1939.6135 | 372.3132
1940.6135 | 372.3447
1941.6135 | 372.3119
1942.6135 | 372.3458
1943.6135 | 372.3847
1944.6135 | 372.4199
1945.6135 | 372.4732
1946.6135 | 372.444
1947.6135 | 372.3618
1948.6135 | 372.4518
1949.6135 | 372.4733
1950.6135 | 372.5461
1951.6135 | 372.6431
1952.6135 | 372.5962
1953.6135 | 372.4446
1954.6135 | 372.4509
1955.6135 | 372.6575
1956.6135 | 372.8133
1957.6135 | 372.8984
1958.6135 | 372.9015
1959.6135 | 372.817
1960.6135 | 372.756
1961.6135 | 372.71
1962.6135 | 372.7565
1963.6135 | 372.8619
1964.6135 | 372.8502
1965.6135 | 372.8122
1966.6135 | 372.7441
1967.6135 | 372.6388
1968.6135 | 372.5939
1969.6135 | 372.5099
1970.6135 | 372.4776
1971.6135 | 372.4636
1972.6135 | 372.4982
1973.6135 | 372.474
1974.6135 | 372.5023
1975.6135 | 372.572
1976.6135 | 372.5737
1977.6135 | 372.5697
1978.6135 | 372.5826
1979.6135 | 372.5267
1980.6135 | 372.4729
1981.6135 | 372.5466
1982.6135 | 372.5245
1983.6135 | 372.5376
1984.6135 | 372.6236
1985.6135 | 372.725
1986.6135 | 372.7049
1987.6135 | 372.5865
1988.6135 | 372.5897
1989.6135 | 372.5386
1990.6135 | 372.5186
1991.6135 | 372.48
1992.6135 | 372.556
1993.6135 | 372.6413
1994.6135 | 372.6467
1995.6135 | 372.6688
1996.6135 | 372.7485
1997.6135 | 372.7215
1998.6135 | 372.6589
1999.6135 | 372.5343
2000.6135 | 372.5202
2001.6135 | 372.5506
2002.6135 | 372.4308
2003.6135 | 372.4243
2004.6135 | 372.3657
2005.6135 | 372.3565
2006.6135 | 372.1711
2007.6135 | 372.1198
2008.6135 | 372.241
2009.6135 | 372.3478
2010.6135 | 372.4072
2011.6135 | 372.5409
2012.6135 | 372.5801
2013.6135 | 372.5881
2014.6135 | 372.7396
2015.6135 | 372.7804
2016.6135 | 372.755
2017.6135 | 372.6486
2018.6135 | 372.654
2019.6135 | 372.8039
2020.6135 | 372.858
2021.6135 | 372.8889
2022.6135 | 372.8591
2023.6135 | 372.7561
2024.6135 | 372.759
2025.6135 | 372.8138
2026.6135 | 372.8042
2027.6135 | 372.8773
2028.6135 | 372.8906
2029.6135 | 372.8869
2030.6135 | 372.774
2031.6135 | 372.7841
2032.6135 | 372.7633
2033.6135 | 372.8167
2034.6135 | 372.8014
2035.6135 | 372.8101
2036.6135 | 372.8437
2037.6135 | 372.8029
2038.6135 | 372.7703
2039.6135 | 372.81
2040.6135 | 372.7868
2041.6135 | 372.8021
2042.6135 | 372.7848
2043.6135 | 372.7758
2044.6135 | 372.7677
2045.6135 | 372.7385
2046.6135 | 372.8036
2047.6135 | 372.7665
2048.6135 | 372.7647
2049.6135 | 372.7473
2050.6135 | 372.8154
2051.6135 | 372.7779
2052.6135 | 372.776
2053.6135 | 372.8062
2054.6135 | 372.7971
2055.6135 | 372.7765
2056.6135 | 372.7442
2057.6135 | 372.631
2058.6135 | 372.7078
2059.6135 | 372.824
2060.6135 | 372.811
2061.6135 | 372.7841
2062.6135 | 372.7354
2063.6135 | 372.6426
2064.6135 | 372.6933
2065.6135 | 372.7439
2066.6135 | 372.8906
2067.6135 | 372.9904
2068.6135 | 373.0698
2069.6135 | 373.0776
2070.6135 | 373.1513
2071.6135 | 373.2092
2072.6135 | 373.1826
2073.6135 | 373.1842
2074.6135 | 373.1865
2075.6135 | 373.2048
2076.6135 | 373.1421
2077.6135 | 373.0725
2078.6135 | 372.9716
2079.6135 | 372.9818
2080.6135 | 372.9885
2081.6135 | 372.9853
2082.6135 | 373.0466
2083.6135 | 373.1892
2084.6135 | 373.2639
2085.6135 | 373.3603
2086.6135 | 373.4496
2087.6135 | 373.5423
2088.6135 | 373.4784
2089.6135 | 373.512
2090.6135 | 373.605
2091.6135 | 373.6057
2092.6135 | 373.4657
2093.6135 | 373.3967
2094.6135 | 373.3452
2095.6135 | 373.335
2096.6135 | 373.307
2097.6135 | 373.3404
2098.6135 | 373.3305
2099.6135 | 373.2664
2100.6135 | 373.1987
2101.6135 | 373.1188
2102.6135 | 373.0647
2103.6135 | 373.0637
2104.6135 | 373.111
2105.6135 | 373.0721
2106.6135 | 372.9671
2107.6135 | 372.8804
2108.6135 | 372.908
2109.6135 | 372.921
2110.6135 | 372.9677
2111.6135 | 373.0668
2112.6135 | 373.0914
2113.6135 | 373.098
2114.6135 | 373.0635
2115.6135 | 373.0273
2116.6135 | 373.0001
2117.6135 | 373.0338
2118.6135 | 373.1227
2119.6135 | 373.1342
2120.6135 | 373.1337
2121.6135 | 373.1055
2122.6135 | 373.1688
2123.6135 | 373.1998
2124.6135 | 373.3407
2125.6135 | 373.3683
2126.6135 | 373.2398
2127.6135 | 373.1962
2128.6135 | 373.2023
2129.6135 | 373.2035
2130.6135 | 373.205
2131.6135 | 373.2366
2132.6135 | 373.1891
2133.6135 | 373.2005
2134.6135 | 373.2187
2135.6135 | 373.1738
2136.6135 | 373.1939
2137.6135 | 373.1446
2138.6135 | 373.148
2139.6135 | 373.1184
2140.6135 | 373.0963
2141.6135 | 373.2691
2142.6135 | 373.2508
2143.6135 | 373.2266
2144.6135 | 373.1687
2145.6135 | 373.1684
2146.6135 | 373.208
2147.6135 | 373.1332
2148.6135 | 373.0988
2149.6135 | 373.0386
2150.6135 | 372.9887
2151.6135 | 372.9161
2152.6135 | 372.8265
2153.6135 | 372.7958
2154.6135 | 372.8359
2155.6135 | 372.9591
2156.6135 | 373.0074
2157.6135 | 372.9057
2158.6135 | 372.8183
2159.6135 | 372.7443
2160.6135 | 372.8057
2161.6135 | 372.8638
2162.6135 | 372.8384
2163.6135 | 372.8988
2164.6135 | 372.9171
2165.6135 | 372.9411
2166.6135 | 372.8596
2167.6135 | 372.8829
2168.6135 | 372.9509
2169.6135 | 372.9399
2170.6135 | 372.8987
2171.6135 | 372.8117
2172.6135 | 372.7559
2173.6135 | 372.8506
2174.6135 | 372.8418
2175.6135 | 372.8596
2176.6135 | 372.8832
2177.6135 | 372.8642
2178.6135 | 372.9634
2179.6135 | 372.981
2180.6135 | 372.9586
2181.6135 | 372.9545
2182.6135 | 372.8999
2183.6135 | 372.9648
2184.6135 | 373.0604
2185.6135 | 373.1212
2186.6135 | 373.0697
2187.6135 | 373.0159
2188.6135 | 373.0471
2189.6135 | 373.0795
2190.6135 | 373.0626
2191.6135 | 372.9874
2192.6135 | 373.0006
2193.6135 | 372.9977
2194.6135 | 373.0476
2195.6135 | 372.9587
2196.6135 | 372.7818
2197.6135 | 372.7992
2198.6135 | 372.8147
2199.6135 | 372.8496
2200.6135 | 372.8388
2201.6135 | 372.823
2202.6135 | 372.8931
2203.6135 | 372.9877
2204.6135 | 373.0893
2205.6135 | 373.1067
2206.6135 | 373.0453
2207.6135 | 372.9496
2208.6135 | 372.8902
2209.6135 | 372.8908
2210.6135 | 372.938
2211.6135 | 373.0033
2212.6135 | 372.9585
2213.6135 | 372.9198
2214.6135 | 372.8725
2215.6135 | 372.8654
2216.6135 | 372.9002
2217.6135 | 372.9364
2218.6135 | 372.9956
2219.6135 | 372.9009
2220.6135 | 372.7629
2221.6135 | 372.7469
2222.6135 | 372.8328
2223.6135 | 372.8876
2224.6135 | 372.9529
2225.6135 | 372.9123
2226.6135 | 372.9373
2227.6135 | 373.01
2228.6135 | 373.0259
2229.6135 | 373.036
2230.6135 | 373.0121
2231.6135 | 373.0155
2232.6135 | 372.9958
2233.6135 | 373.0047
2234.6135 | 373.0786
2235.6135 | 373.1229
2236.6135 | 373.1424
2237.6135 | 373.1011
2238.6135 | 373.0627
2239.6135 | 373.1086
2240.6135 | 373.1264
2241.6135 | 373.0947
2242.6135 | 373.016
2243.6135 | 372.9671
2244.6135 | 373.009
2245.6135 | 372.9639
2246.6135 | 372.9459
2247.6135 | 372.9127
2248.6135 | 372.8842
2249.6135 | 372.8726
2250.6135 | 372.7804
2251.6135 | 372.803
2252.6135 | 372.9112
2253.6135 | 372.819
2254.6135 | 372.7962
2255.6135 | 372.8924
2256.6135 | 373.0156
2257.6135 | 373.2117
2258.6135 | 373.289
2259.6135 | 373.1393
2260.6135 | 373.0531
2261.6135 | 373.0131
2262.6135 | 373.1329
2263.6135 | 373.1723
2264.6135 | 373.1136
2265.6135 | 373.139
2266.6135 | 373.1292
2267.6135 | 373.0297
2268.6135 | 372.9777
2269.6135 | 372.9087
2270.6135 | 372.8922
2271.6135 | 372.7318
2272.6135 | 372.7208
2273.6135 | 372.5448
2274.6135 | 372.6086
2275.6135 | 372.7143
2276.6135 | 372.7637
2277.6135 | 372.8398
2278.6135 | 372.8495
2279.6135 | 372.837
2280.6135 | 372.7117
2281.6135 | 372.4966
2282.6135 | 372.4013
2283.6135 | 372.3379
2284.6135 | 372.384
2285.6135 | 372.469
2286.6135 | 372.5107
2287.6135 | 372.5507
2288.6135 | 372.7271
2289.6135 | 372.8651
2290.6135 | 372.9678
2291.6135 | 373.0672
2292.6135 | 373.1816
2293.6135 | 373.2739
2294.6135 | 373.2249
2295.6135 | 373.109
2296.6135 | 373.0518
2297.6135 | 373.0462
2298.6135 | 373.149
2299.6135 | 373.288
2300.6135 | 373.2765
2301.6135 | 373.2388
2302.6135 | 373.2247
2303.6135 | 373.1992
2304.6135 | 373.1666
2305.6135 | 373.2128
2306.6135 | 373.1473
2307.6135 | 373.1206
2308.6135 | 373.1264
2309.6135 | 373.1225
2310.6135 | 373.1001
2311.6135 | 373.1
2312.6135 | 373.1039
2313.6135 | 373.0357
2314.6135 | 372.9317
2315.6135 | 372.8482
2316.6135 | 372.8365
2317.6135 | 372.8704
2318.6135 | 372.9087
2319.6135 | 372.9018
2320.6135 | 372.893
2321.6135 | 372.972
2322.6135 | 373.0779
2323.6135 | 373.1136
2324.6135 | 373.2216
2325.6135 | 373.2894
2326.6135 | 373.3743
2327.6135 | 373.2713
2328.6135 | 373.0942
2329.6135 | 373.015
2330.6135 | 372.9529
2331.6135 | 372.9193
2332.6135 | 372.8665
2333.6135 | 372.7991
2334.6135 | 372.7316
2335.6135 | 372.7245
2336.6135 | 372.6658
2337.6135 | 372.5874
2338.6135 | 372.4334
2339.6135 | 372.3849
2340.6135 | 372.4664
2341.6135 | 372.4191
2342.6135 | 372.3149
2343.6135 | 372.3138
2344.6135 | 372.262
2345.6135 | 372.1241
2346.6135 | 372.0813
2347.6135 | 372.072
2348.6135 | 372.1234
2349.6135 | 372.0317
2350.6135 | 371.9955
2351.6135 | 371.9408
2352.6135 | 371.9557
2353.6135 | 371.9635
2354.6135 | 371.9427
2355.6135 | 371.9398
2356.6135 | 371.9446
2357.6135 | 371.913
2358.6135 | 371.8826
2359.6135 | 371.8252
2360.6135 | 372.0821
2361.6135 | 372.1556
2362.6135 | 372.2686
2363.6135 | 372.2551
2364.6135 | 372.2856
2365.6135 | 372.2499
2366.6135 | 372.2708
2367.6135 | 372.2541
2368.6135 | 372.2651
2369.6135 | 372.4525
2370.6135 | 372.5109
2371.6135 | 372.5921
2372.6135 | 372.608
2373.6135 | 372.6205
2374.6135 | 372.6584
2375.6135 | 372.636
2376.6135 | 372.555
2377.6135 | 372.5164
2378.6135 | 372.4482
2379.6135 | 372.582
2380.6135 | 372.6533
2381.6135 | 372.5855
2382.6135 | 372.6909
2383.6135 | 372.7953
2384.6135 | 372.9423
2385.6135 | 373.0203
2386.6135 | 372.9999
2387.6135 | 373.0281
2388.6135 | 372.9901
2389.6135 | 372.9945
2390.6135 | 372.9793
2391.6135 | 372.9741
2392.6135 | 372.9043
2393.6135 | 372.8553
2394.6135 | 372.8776
2395.6135 | 372.955
2396.6135 | 372.931
2397.6135 | 372.9765
2398.6135 | 372.892
2399.6135 | 372.9169
2400.6135 | 372.7825
2401.6135 | 372.7924
2402.6135 | 372.8367
2403.6135 | 372.8836
2404.6135 | 372.9262
2405.6135 | 372.8762
2406.6135 | 372.9359
2407.6135 | 372.9011
2408.6135 | 372.9476
2409.6135 | 372.894
2410.6135 | 372.7825
2411.6135 | 372.7125
2412.6135 | 372.7511
2413.6135 | 372.7992
2414.6135 | 372.7196
2415.6135 | 372.7189
2416.6135 | 372.7349
2417.6135 | 372.7845
2418.6135 | 372.7516
2419.6135 | 372.6975
2420.6135 | 372.6979
2421.6135 | 372.6318
2422.6135 | 372.596
2423.6135 | 372.5468
2424.6135 | 372.5481
2425.6135 | 372.5409
2426.6135 | 372.595
2427.6135 | 372.6524
2428.6135 | 372.6544
2429.6135 | 372.5858
2430.6135 | 372.672
2431.6135 | 372.6437
2432.6135 | 372.6485
2433.6135 | 372.655
2434.6135 | 372.5287
2435.6135 | 372.5247
2436.6135 | 372.5835
2437.6135 | 372.5539
2438.6135 | 372.5633
2439.6135 | 372.6309
2440.6135 | 372.6299
2441.6135 | 372.5822
2442.6135 | 372.5341
2443.6135 | 372.6856
2444.6135 | 372.762
2445.6135 | 372.7632
2446.6135 | 372.9138
2447.6135 | 372.943
2448.6135 | 372.8917
2449.6135 | 372.827
2450.6135 | 372.8313
2451.6135 | 372.8928
2452.6135 | 372.9704
2453.6135 | 373.0189
2454.6135 | 373.1119
2455.6135 | 373.1579
2456.6135 | 373.1451
2457.6135 | 373.1499
2458.6135 | 373.0937
2459.6135 | 373.1521
2460.6135 | 373.1004
2461.6135 | 373.038
2462.6135 | 373.1139
2463.6135 | 373.2486
2464.6135 | 373.1809
2465.6135 | 373.124
2466.6135 | 373.1662
2467.6135 | 373.1908
2468.6135 | 373.2663
2469.6135 | 373.2044
2470.6135 | 373.1356
2471.6135 | 373.0675
2472.6135 | 373.0804
2473.6135 | 373.0049
2474.6135 | 372.8766
2475.6135 | 372.7625
2476.6135 | 372.7287
2477.6135 | 372.7076
2478.6135 | 372.6918
2479.6135 | 372.649
2480.6135 | 372.64
2481.6135 | 372.6348
2482.6135 | 372.6089
2483.6135 | 372.5267
2484.6135 | 372.6601
2485.6135 | 372.8175
2486.6135 | 372.7985
2487.6135 | 372.7565
2488.6135 | 372.8931
2489.6135 | 373.045
2490.6135 | 373.1154
2491.6135 | 373.0877
2492.6135 | 373.0751
2493.6135 | 373.0154
2494.6135 | 372.8002
2495.6135 | 372.7677
2496.6135 | 372.7163
2497.6135 | 372.7118
2498.6135 | 372.6268
2499.6135 | 372.6224
2500.6135 | 372.5688
2501.6135 | 372.5433
2502.6135 | 372.4768
2503.6135 | 372.4775
2504.6135 | 372.5778
2505.6135 | 372.5422
2506.6135 | 372.4981
2507.6135 | 372.5516
2508.6135 | 372.5718
2509.6135 | 372.6432
2510.6135 | 372.5942
2511.6135 | 372.6021
2512.6135 | 372.6918
2513.6135 | 372.6674
2514.6135 | 372.5809
2515.6135 | 372.6086
2516.6135 | 372.6614
2517.6135 | 372.621
2518.6135 | 372.551
2519.6135 | 372.5135
2520.6135 | 372.5304
2521.6135 | 372.4836
2522.6135 | 372.4357
2523.6135 | 372.3192
2524.6135 | 372.29
2525.6135 | 372.205
2526.6135 | 372.2073
2527.6135 | 372.4046
2528.6135 | 372.4086
2529.6135 | 372.4823
2530.6135 | 372.3966
2531.6135 | 372.3904
2532.6135 | 372.3151
2533.6135 | 372.1694
2534.6135 | 372.225
2535.6135 | 372.2847
2536.6135 | 372.1901
2537.6135 | 372.2687
2538.6135 | 372.4133
2539.6135 | 372.4148
2540.6135 | 372.4501
2541.6135 | 372.3701
2542.6135 | 372.3885
2543.6135 | 372.4267
2544.6135 | 372.5559
2545.6135 | 372.5817
2546.6135 | 372.5183
2547.6135 | 372.5468
2548.6135 | 372.6518
2549.6135 | 372.7176
2550.6135 | 372.7485
2551.6135 | 372.727
2552.6135 | 372.7906
2553.6135 | 372.8943
2554.6135 | 372.9938
2555.6135 | 373.1987
2556.6135 | 373.2928
2557.6135 | 373.3436
2558.6135 | 373.2718
2559.6135 | 373.1789
2560.6135 | 373.191
2561.6135 | 373.1926
2562.6135 | 373.1535
2563.6135 | 373.2711
2564.6135 | 373.3041
2565.6135 | 373.2831
2566.6135 | 373.3403
2567.6135 | 373.3057
2568.6135 | 373.3529
2569.6135 | 373.4199
2570.6135 | 373.3144
2571.6135 | 373.3151
2572.6135 | 373.4206
2573.6135 | 373.4435
2574.6135 | 373.381
2575.6135 | 373.4435
2576.6135 | 373.5438
2577.6135 | 373.5898
2578.6135 | 373.5612
2579.6135 | 373.4706
2580.6135 | 373.4034
2581.6135 | 373.3377
2582.6135 | 373.2062
2583.6135 | 373.14
2584.6135 | 373.108
2585.6135 | 373.0787
2586.6135 | 373.1255
2587.6135 | 373.186
2588.6135 | 373.0564
2589.6135 | 373.04
2590.6135 | 373.0795
2591.6135 | 373.0334
2592.6135 | 372.9043
2593.6135 | 372.7103
2594.6135 | 372.7022
2595.6135 | 372.6016
2596.6135 | 372.5394
2597.6135 | 372.5342
2598.6135 | 372.5482
2599.6135 | 372.4654
2600.6135 | 372.4414
2601.6135 | 372.5174
2602.6135 | 372.5553
2603.6135 | 372.6646
2604.6135 | 372.662
2605.6135 | 372.547
2606.6135 | 372.5323
2607.6135 | 372.5547
2608.6135 | 372.5203
2609.6135 | 372.4395
2610.6135 | 372.3665
2611.6135 | 372.2787
2612.6135 | 372.2783
2613.6135 | 372.3361
2614.6135 | 372.394
2615.6135 | 372.3784
2616.6135 | 372.4185
2617.6135 | 372.4474
2618.6135 | 372.3859
2619.6135 | 372.3144
2620.6135 | 372.4178
2621.6135 | 372.4643
2622.6135 | 372.304
2623.6135 | 372.2573
2624.6135 | 372.3299
2625.6135 | 372.2912
2626.6135 | 372.2659
2627.6135 | 372.3222
2628.6135 | 372.3551
2629.6135 | 372.2925
2630.6135 | 372.2799
2631.6135 | 372.2878
2632.6135 | 372.2399
2633.6135 | 372.265
2634.6135 | 372.3007
2635.6135 | 372.3687
2636.6135 | 372.4176
2637.6135 | 372.4436
2638.6135 | 372.5382
2639.6135 | 372.4795
2640.6135 | 372.4932
2641.6135 | 372.5135
2642.6135 | 372.5309
2643.6135 | 372.5438
2644.6135 | 372.5099
2645.6135 | 372.4515
2646.6135 | 372.4579
2647.6135 | 372.361
2648.6135 | 372.31
2649.6135 | 372.2268
2650.6135 | 372.1856
2651.6135 | 372.1111
2652.6135 | 372.1907
2653.6135 | 372.1955
2654.6135 | 372.2192
2655.6135 | 372.2896
2656.6135 | 372.2187
2657.6135 | 372.1761
2658.6135 | 372.1673
2659.6135 | 372.1398
2660.6135 | 372.1917
2661.6135 | 372.2555
2662.6135 | 372.2784
2663.6135 | 372.2261
2664.6135 | 372.2021
2665.6135 | 372.2928
2666.6135 | 372.3322
2667.6135 | 372.4371
2668.6135 | 372.4893
2669.6135 | 372.5137
2670.6135 | 372.5769
2671.6135 | 372.7381
2672.6135 | 372.9051
2673.6135 | 372.9857
2674.6135 | 372.958
2675.6135 | 372.9306
2676.6135 | 372.9537
2677.6292 | 373.0303
2678.6135 | 373.1306
2679.6135 | 373.187
2680.6135 | 373.1275
2681.6135 | 373.0275
2682.6135 | 372.9618
2683.6135 | 373.0022
2684.6135 | 372.9013
2685.6135 | 372.9806
2686.6135 | 373.115
2687.6135 | 373.1276
2688.6135 | 373.155
2689.6135 | 373.0583
2690.6135 | 373.0419
2691.6135 | 373.0564
2692.6135 | 373.0692
2693.6135 | 373.1258
2694.6135 | 373.0322
2695.6135 | 373.0306
2696.6135 | 373.0343
2697.6135 | 373.0045
2698.6135 | 372.9283
2699.6135 | 372.9074
2700.6135 | 372.7373
2701.6135 | 372.5906
2702.6135 | 372.6795
2703.6135 | 372.7559
2704.6135 | 372.8503
2705.6135 | 372.9358
2706.6135 | 372.951
2707.6135 | 373.0699
2708.6135 | 373.2312
2709.6135 | 373.3187
2710.6135 | 373.3083
2711.6135 | 373.3432
2712.6135 | 373.3656
2713.6135 | 373.2795
2714.6135 | 373.211
2715.6135 | 373.1508
2716.6135 | 373.0693
2717.6135 | 372.9572
2718.6135 | 372.8118
2719.6135 | 372.6577
2720.6135 | 372.6487
2721.6135 | 372.5955
2722.6135 | 372.5557
2723.6135 | 372.5895
2724.6135 | 372.559
2725.6135 | 372.5755
2726.6135 | 372.6028
2727.6135 | 372.5936
2728.6135 | 372.7149
2729.6135 | 372.7819
2730.6135 | 372.761
2731.6135 | 372.7094
2732.6135 | 372.8064
2733.6135 | 372.8151
2734.6135 | 372.8464
2735.6135 | 372.8995
2736.6135 | 372.944
2737.6135 | 372.9486
2738.6135 | 372.9086
2739.6135 | 372.9613
2740.6135 | 372.9691
2741.6135 | 372.9686
2742.6135 | 373.0127
2743.6135 | 373.1124
2744.6135 | 373.1336
2745.6135 | 373.0572
2746.6135 | 372.981
2747.6135 | 373.0071
2748.6135 | 372.9894
2749.6135 | 372.9473
2750.6135 | 372.9709
2751.6135 | 373.0368
2752.6135 | 373.101
2753.6135 | 373.1227
2754.6135 | 373.1083
2755.6135 | 373.1429
2756.6135 | 373.2116
2757.6135 | 373.2645
2758.6135 | 373.3134
2759.6135 | 373.2895
2760.6135 | 373.3292
2761.6135 | 373.2801
2762.6135 | 373.228
2763.6135 | 373.2118
2764.6135 | 373.3709
2765.6135 | 373.4604
2766.6135 | 373.4119
2767.6135 | 373.4955
2768.6135 | 373.5372
2769.6135 | 373.5675
2770.6135 | 373.6349
2771.6135 | 373.6901
2772.6135 | 373.6709
2773.6135 | 373.6624
2774.6135 | 373.5191
2775.6135 | 373.3441
2776.6135 | 373.2659
2777.6135 | 373.2865
2778.6135 | 373.4892
2779.6135 | 373.5971
2780.6135 | 373.7282
2781.6135 | 373.7555
2782.6135 | 373.6449
2783.6135 | 373.7192
2784.6135 | 373.6799
2785.6135 | 373.7855
2786.6135 | 373.9284
2787.6135 | 373.9009
2788.6135 | 373.6854
2789.6135 | 373.5443
2790.6135 | 373.3829
2791.6135 | 373.2255
2792.6135 | 373.2126
2793.6135 | 373.1553
2794.6135 | 373.041
2795.6135 | 373.0658
2796.6135 | 373.1042
2797.6135 | 373.1479
2798.6135 | 373.0345
2799.6135 | 372.962
2800.6135 | 372.9288
2801.6135 | 372.9306
2802.6135 | 372.9506
2803.6135 | 372.9343
2804.6135 | 372.9495
2805.6135 | 372.957
2806.6135 | 373.0336
2807.6135 | 373.0263
2808.6135 | 373.0385
2809.6135 | 372.9853
2810.6135 | 372.9232
2811.6135 | 372.9477
2812.6135 | 373.0426
2813.6135 | 373.0073
2814.6135 | 373.1099
2815.6135 | 373.2088
2816.6135 | 373.2705
2817.6135 | 373.2433
2818.6135 | 373.2992
2819.6135 | 373.3307
2820.6135 | 373.2556
2821.6135 | 373.1643
2822.6135 | 373.0997
2823.6135 | 373.2391
2824.6135 | 373.3822
2825.6135 | 373.5236
2826.6135 | 373.4941
2827.6135 | 373.4796
2828.6135 | 373.6487
2829.6135 | 373.8338
2830.6135 | 373.8301
2831.6135 | 373.7855
2832.6135 | 373.8639
2833.6135 | 373.829
2834.6135 | 373.7436
2835.6135 | 373.7637
2836.6135 | 373.8044
2837.6135 | 373.7605
2838.6135 | 373.6925
2839.6135 | 373.593
2840.6135 | 373.584
2841.6135 | 373.6711
2842.6135 | 373.592
2843.6135 | 373.637
2844.6135 | 373.6613
2845.6135 | 373.6476
2846.6135 | 373.6983
2847.6135 | 373.7439
2848.6135 | 373.7859
2849.6135 | 373.8273
2850.6135 | 373.898
2851.6135 | 373.9533
2852.6135 | 374.0038
2853.6135 | 374.0117
2854.6135 | 374.0371
2855.6135 | 373.9528
2856.6135 | 374.01
2857.6135 | 373.9309
2858.6135 | 373.8547
2859.6135 | 373.8504
2860.6135 | 373.8827
2861.6135 | 373.8647
2862.6135 | 373.8492
2863.6135 | 373.988
2864.6135 | 374.0502
2865.6135 | 374.1164
2866.6135 | 374.0235
2867.6135 | 373.9552
2868.6135 | 373.9888
2869.6135 | 374.0975
2870.6135 | 374.1063
2871.6135 | 374.0948
2872.6135 | 374.0155
2873.6135 | 373.9089
2874.6135 | 373.8599
2875.6135 | 373.8657
2876.6135 | 373.7755
2877.6135 | 373.7138
2878.6135 | 373.7235
2879.6135 | 373.7055
2880.6135 | 373.6702
2881.6135 | 373.6885
2882.6135 | 373.6101
2883.6135 | 373.6173
2884.6135 | 373.6004
2885.6135 | 373.5744
2886.6135 | 373.4609
2887.6135 | 373.4037
2888.6135 | 373.382
2889.6135 | 373.4284
2890.6135 | 373.4753
2891.6135 | 373.4334
2892.6135 | 373.4948
2893.6135 | 373.4688
2894.6135 | 373.4403
2895.6135 | 373.4152
2896.6135 | 373.5031
2897.6135 | 373.5375
2898.6135 | 373.4633
2899.6135 | 373.4309
2900.6135 | 373.4635
2901.6135 | 373.4842
2902.6135 | 373.4722
2903.6135 | 373.4786
2904.6135 | 373.3928
2905.6135 | 373.4597
2906.6135 | 373.4747
2907.6135 | 373.5489
2908.6135 | 373.5346
2909.6135 | 373.5806
2910.6135 | 373.6561
2911.6135 | 373.6666
2912.6135 | 373.6286
2913.6135 | 373.5541
2914.6135 | 373.6723
2915.6135 | 373.6463
2916.6135 | 373.7128
2917.6135 | 373.7423
2918.6135 | 373.7459
2919.6135 | 373.7153
2920.6135 | 373.8077
2921.6135 | 373.829
2922.6135 | 373.7373
2923.6135 | 373.7611
2924.6135 | 373.7774
2925.6135 | 373.8551
2926.6135 | 373.8076
2927.6135 | 373.7228
2928.6135 | 373.7365
2929.6135 | 373.6999
2930.6135 | 373.7147
2931.6135 | 373.8243
2932.6135 | 373.8825
2933.6135 | 373.8975
2934.6135 | 373.8795
2935.6135 | 373.8257
2936.6135 | 373.8253
2937.6135 | 373.722
2938.6135 | 373.7169
2939.6135 | 373.738
2940.6135 | 373.7934
2941.6135 | 373.9388
2942.6135 | 374.1337
2943.6135 | 374.26
2944.6135 | 374.2979
2945.6135 | 374.3426
2946.6135 | 374.1985
2947.6135 | 374.1048
2948.6135 | 374.0232
2949.6135 | 374.0738
2950.6135 | 374.1611
2951.6135 | 374.1637
2952.6135 | 374.1935
2953.6135 | 374.2167
2954.6135 | 374.1437
2955.6135 | 374.1393
2956.6135 | 374.0815
2957.6135 | 374.0282
2958.6135 | 373.9136
2959.6135 | 373.8363
2960.6135 | 373.8592
2961.6135 | 373.8448
2962.6135 | 373.8772
2963.6135 | 373.8562
2964.6135 | 373.7913
2965.6135 | 373.7715
2966.6135 | 373.7817
2967.6135 | 373.7047
2968.6135 | 373.7142
2969.6135 | 373.7275
2970.6135 | 373.7032
2971.6135 | 373.7006
2972.6135 | 373.7247
2973.6135 | 373.6672
2974.6135 | 373.5708
2975.6135 | 373.573
2976.6135 | 373.6324
2977.6135 | 373.6147
2978.6135 | 373.6529
2979.6135 | 373.8281
2980.6135 | 373.9107
2981.6135 | 374.0298
2982.6135 | 373.9882
2983.6135 | 373.9014
2984.6135 | 373.9099
2985.6135 | 373.995
2986.6135 | 374.1994
2987.6135 | 374.2448
2988.6135 | 374.1219
2989.6135 | 374.0672
2990.6135 | 374.0648
2991.6135 | 374.2019
2992.6135 | 374.1665
2993.6135 | 374.0749
2994.6135 | 374.0241
2995.6135 | 373.9913
2996.6135 | 373.9831
2997.6135 | 373.994
2998.6135 | 373.9894
2999.6135 | 373.9796
3000.6135 | 373.7968
3001.6135 | 373.7262
3002.6135 | 373.6018
3003.6135 | 373.4926
3004.6135 | 373.3756
3005.6135 | 373.3997
3006.6135 | 373.4965
3007.6135 | 373.5056
3008.6135 | 373.4616
3009.6135 | 373.4779
3010.6135 | 373.4832
3011.6135 | 373.4265
3012.6135 | 373.3386
3013.6135 | 373.3598
3014.6135 | 373.4239
3015.6135 | 373.4541
3016.6135 | 373.3886
3017.6135 | 373.352
3018.6135 | 373.4663
3019.6135 | 373.4804
3020.6135 | 373.5085
3021.6135 | 373.6101
3022.6135 | 373.5335
3023.6135 | 373.4573
3024.6135 | 373.4239
3025.6135 | 373.4952
3026.6135 | 373.5083
3027.6135 | 373.5099
3028.6135 | 373.5207
3029.6135 | 373.5087
3030.6135 | 373.4584
3031.6135 | 373.4746
3032.6135 | 373.4631
3033.6135 | 373.467
3034.6135 | 373.5077
3035.6135 | 373.6742
3036.6135 | 373.6798
3037.6135 | 373.5889
3038.6135 | 373.6284
3039.6135 | 373.561
3040.6135 | 373.4948
3041.6135 | 373.4821
3042.6135 | 373.3836
3043.6135 | 373.4525
3044.6135 | 373.4743
3045.6135 | 373.5642
3046.6135 | 373.6038
3047.6135 | 373.7275
3048.6135 | 373.8399
3049.6135 | 373.9953
3050.6135 | 374.0978
3051.6135 | 374.2945
3052.6135 | 374.3271
3053.6135 | 374.3044
3054.6135 | 374.3033
3055.6135 | 374.3988
3056.6135 | 374.4949
3057.6135 | 374.5383
3058.6135 | 374.6618
3059.6135 | 374.6674
3060.6135 | 374.6921
3061.6135 | 374.7094
3062.6135 | 374.7036
3063.6135 | 374.7056
3064.6135 | 374.8049
3065.6135 | 374.8219
3066.6135 | 374.7683
3067.6135 | 374.6645
3068.6135 | 374.625
3069.6135 | 374.5544
3070.6135 | 374.4707
3071.6135 | 374.381
3072.6135 | 374.3104
3073.6135 | 374.3335
3074.6135 | 374.306
3075.6135 | 374.3191
3076.6135 | 374.4258
3077.6135 | 374.4295
3078.6135 | 374.3439
3079.6135 | 374.311
3080.6135 | 374.2581
3081.6135 | 374.2644
3082.6135 | 374.1094
3083.6135 | 373.9205
3084.6135 | 373.8301
3085.6135 | 373.6974
3086.6135 | 373.663
3087.6135 | 373.591
3088.6135 | 373.5377
3089.6135 | 373.538
3090.6135 | 373.5
3091.6135 | 373.4173
3092.6135 | 373.423
3093.6135 | 373.4293
3094.6135 | 373.4799
3095.6135 | 373.5036
3096.6135 | 373.6225
3097.6135 | 373.735
3098.6135 | 373.7657
3099.6135 | 373.6969
3100.6135 | 373.7435
3101.6135 | 373.8424
3102.6135 | 373.8334
3103.6135 | 373.8683
3104.6135 | 374.0079
3105.6135 | 374.0501
3106.6135 | 373.9788
3107.6135 | 374.0652
3108.6135 | 374.0527
3109.6135 | 374.0039
3110.6135 | 373.9862
3111.6135 | 373.8924
3112.6135 | 373.9299
3113.6135 | 374.0409
3114.6135 | 374.0665
3115.6135 | 374.0107
3116.6135 | 374.0464
3117.6135 | 374.1136
3118.6135 | 374.2072
3119.6135 | 374.3626
3120.6135 | 374.323
3121.6135 | 374.2472
3122.6135 | 374.1338
3123.6135 | 374.1311
3124.6135 | 374.0357
3125.6135 | 373.9363
3126.6135 | 373.8314
3127.6135 | 373.6525
3128.6135 | 373.5656
3129.6135 | 373.5723
3130.6135 | 373.6019
3131.6135 | 373.5728
3132.6135 | 373.5324
3133.6135 | 373.5026
3134.6135 | 373.4707
3135.6135 | 373.4198
3136.6135 | 373.385
3137.6135 | 373.4059
3138.6135 | 373.5945
3139.6135 | 373.6201
3140.6135 | 373.6472
3141.6135 | 373.6788
3142.6135 | 373.6596
3143.6135 | 373.6625
3144.6135 | 373.7198
3145.6135 | 373.7542
3146.6135 | 373.7832
3147.6135 | 373.7478
3148.6135 | 373.7326
3149.6135 | 373.7478
3150.6135 | 373.7306
3151.6135 | 373.6206
3152.6135 | 373.684
3153.6135 | 373.6437
3154.6135 | 373.6281
3155.6135 | 373.6134
3156.6135 | 373.5895
3157.6135 | 373.6733
3158.6135 | 373.7535
3159.6135 | 373.7775
3160.6135 | 373.6391
3161.6135 | 373.6699
3162.6135 | 373.6595
3163.6135 | 373.557
3164.6135 | 373.5315
3165.6135 | 373.4581
3166.6135 | 373.4296
3167.6135 | 373.5458
3168.6135 | 373.537
3169.6135 | 373.5785
3170.6135 | 373.5967
3171.6135 | 373.539
3172.6135 | 373.5719
3173.6135 | 373.7127
3174.6135 | 373.7435
3175.6135 | 373.8477
3176.6135 | 373.9001
3177.6135 | 373.8741
3178.6135 | 373.8765
3179.6135 | 373.8365
3180.6135 | 373.7825
3181.6135 | 373.8272
3182.6135 | 373.8736
3183.6135 | 373.7187
3184.6135 | 373.6563
3185.6135 | 373.6081
3186.6135 | 373.5939
3187.6135 | 373.5108
3188.6135 | 373.398
3189.6135 | 373.4799
3190.6135 | 373.5319
3191.6135 | 373.5137
3192.6135 | 373.5005
3193.6135 | 373.5844
3194.6135 | 373.6667
3195.6135 | 373.705
3196.6135 | 373.7537
3197.6135 | 373.8702
3198.6135 | 373.9262
3199.6135 | 373.9245
3200.6135 | 373.9192
3201.6135 | 373.8409
3202.6135 | 373.7439
3203.6135 | 373.6579
3204.6135 | 373.6631
3205.6135 | 373.6387
3206.6135 | 373.6347
3207.6135 | 373.7735
3208.6135 | 373.6691
3209.6135 | 373.5697
3210.6135 | 373.5645
3211.6135 | 373.6225
3212.6135 | 373.6544
3213.6135 | 373.7276
3214.6135 | 373.6899
3215.6135 | 373.6443
3216.6135 | 373.5658
3217.6135 | 373.4546
3218.6135 | 373.4562
3219.6135 | 373.508
3220.6135 | 373.4818
3221.6135 | 373.432
3222.6135 | 373.3328
3223.6135 | 373.2875
3224.6135 | 373.3075
3225.6135 | 373.2698
3226.6135 | 373.3266
3227.6135 | 373.4123
3228.6135 | 373.4416
3229.6135 | 373.4446
3230.6135 | 373.5315
3231.6135 | 373.6164
3232.6135 | 373.7069
3233.6135 | 373.8264
3234.6135 | 373.883
3235.6135 | 373.9161
3236.6135 | 373.8534
3237.6135 | 373.823
3238.6135 | 373.8145
3239.6135 | 373.9094
3240.6135 | 373.8636
3241.6135 | 373.7855
3242.6135 | 373.7698
3243.6135 | 373.6436
3244.6135 | 373.5976
3245.6135 | 373.6606
3246.6135 | 373.7494
3247.6135 | 373.7194
3248.6135 | 373.7287
3249.6135 | 373.6546
3250.6135 | 373.7147
3251.6135 | 373.55
3252.6135 | 373.4909
3253.6135 | 373.4224
3254.6135 | 373.4011
3255.6135 | 373.2954
3256.6135 | 373.2355
3257.6135 | 373.1831
3258.6135 | 373.1145
3259.6135 | 373.1078
3260.6135 | 373.1775
3261.6135 | 373.1291
3262.6135 | 373.0722
3263.6135 | 372.971
3264.6135 | 372.88
3265.6135 | 372.8049
3266.6135 | 372.7915
3267.6135 | 372.8792
3268.6135 | 372.8967
3269.6135 | 372.8798
3270.6135 | 372.8588
3271.6135 | 372.8976
3272.6135 | 373.0281
3273.6135 | 372.8818
3274.6135 | 372.8564
3275.6135 | 372.8919
3276.6135 | 373.0176
3277.6135 | 373.0184
3278.6135 | 372.9484
3279.6135 | 373.0197
3280.6135 | 373.0151
3281.6135 | 372.953
3282.6135 | 372.8716
3283.6135 | 372.8938
3284.6135 | 372.8743
3285.6135 | 372.892
3286.6135 | 372.9171
3287.6135 | 372.9268
3288.6135 | 372.9434
3289.6135 | 372.9815
3290.6135 | 373.016
3291.6135 | 373.0534
3292.6135 | 372.9912
3293.6135 | 372.9784
3294.6135 | 373.1032
3295.6135 | 373.2134
3296.6135 | 373.2257
3297.6135 | 373.2264
3298.6135 | 373.2304
3299.6135 | 373.2649
3300.6135 | 373.3021
3301.6135 | 373.3733
3302.6135 | 373.392
3303.6135 | 373.3667
3304.6135 | 373.3684
3305.6135 | 373.3592
3306.6135 | 373.3602
3307.6135 | 373.4513
3308.6135 | 373.4909
3309.6135 | 373.452
3310.6135 | 373.3754
3311.6135 | 373.3552
3312.6135 | 373.3457
3313.6135 | 373.3868
3314.6135 | 373.3264
3315.6135 | 373.364
3316.6135 | 373.4105
3317.6135 | 373.4273
3318.6135 | 373.4033
3319.6135 | 373.3265
3320.6135 | 373.2808
3321.6135 | 373.305
3322.6135 | 373.3172
3323.6135 | 373.3482
3324.6135 | 373.3957
3325.6135 | 373.4615
3326.6135 | 373.5239
3327.6135 | 373.6226
3328.6135 | 373.5846
3329.6135 | 373.6927
3330.6135 | 373.8483
3331.6135 | 373.8227
3332.6135 | 373.6997
3333.6135 | 373.5326
3334.6135 | 373.5266
3335.6135 | 373.5536
3336.6135 | 373.5631
3337.6135 | 373.5827
3338.6135 | 373.4959
3339.6135 | 373.4167
3340.6135 | 373.4788
3341.6135 | 373.5332
3342.6135 | 373.5752
3343.6135 | 373.4827
3344.6135 | 373.4841
3345.6135 | 373.5774
3346.6135 | 373.5842
3347.6135 | 373.5244
3348.6135 | 373.4536
3349.6135 | 373.4967
3350.6135 | 373.5752
3351.6135 | 373.5489
3352.6135 | 373.6013
3353.6135 | 373.7271
3354.6135 | 373.6512
3355.6135 | 373.5901
3356.6135 | 373.4865
3357.6135 | 373.5587
3358.6135 | 373.6461
3359.6135 | 373.7834
3360.6135 | 373.695
3361.6135 | 373.5711
3362.6135 | 373.5415
3363.6135 | 373.4945
3364.6135 | 373.4515
3365.6135 | 373.5175
3366.6135 | 373.5277
3367.6135 | 373.4669
3368.6135 | 373.4495
3369.6135 | 373.4267
3370.6135 | 373.4839
3371.6135 | 373.5897
3372.6135 | 373.7272
3373.6135 | 373.662
3374.6135 | 373.6458
3375.6135 | 373.5806
3376.6135 | 373.5394
3377.6135 | 373.4828
3378.6135 | 373.5088
3379.6135 | 373.5202
3380.6135 | 373.5958
3381.6135 | 373.7248
3382.6135 | 373.6578
3383.6135 | 373.4922
3384.6135 | 373.348
3385.6135 | 373.3439
3386.6135 | 373.374
3387.6135 | 373.3526
3388.6135 | 373.2968
3389.6135 | 373.1732
3390.6135 | 372.997
3391.6135 | 372.8875
3392.6135 | 372.8419
3393.6135 | 372.8756
3394.6135 | 372.8148
3395.6135 | 372.8443
3396.6135 | 372.8324
3397.6135 | 372.8949
3398.6135 | 372.977
3399.6135 | 373.1297
3400.6135 | 373.2569
3401.6135 | 373.3195
3402.6135 | 373.4107
3403.6135 | 373.5758
3404.6135 | 373.6955
3405.6135 | 373.728
3406.6135 | 373.7273
3407.6135 | 373.7612
3408.6135 | 373.7239
3409.6135 | 373.7159
3410.6135 | 373.6767
3411.6135 | 373.5623
3412.6135 | 373.5636
3413.6135 | 373.5853
3414.6135 | 373.6078
3415.6135 | 373.6315
3416.6135 | 373.6424
3417.6135 | 373.6231
3418.6135 | 373.6425
3419.6135 | 373.6504
3420.6135 | 373.6759
3421.6135 | 373.6483
3422.6135 | 373.6458
3423.6135 | 373.6434
3424.6135 | 373.5834
3425.6135 | 373.5419
3426.6135 | 373.5383
3427.6135 | 373.4982
3428.6135 | 373.4799
3429.6135 | 373.5204
3430.6135 | 373.4655
3431.6135 | 373.5629
3432.6135 | 373.6047
3433.6135 | 373.6182
3434.6135 | 373.633
3435.6135 | 373.5912
3436.6135 | 373.568
3437.6135 | 373.5075
3438.6135 | 373.5774
3439.6135 | 373.5157
3440.6135 | 373.5305
3441.6135 | 373.5281
3442.6135 | 373.5634
3443.6135 | 373.3955
3444.6135 | 373.4238
3445.6135 | 373.406
3446.6135 | 373.2588
3447.6135 | 373.2172
3448.6135 | 373.1713
3449.6135 | 373.0967
3450.6135 | 373.0365
3451.6135 | 373.0821
3452.6135 | 373.0594
3453.6135 | 373.0555
3454.6135 | 373.0306
3455.6135 | 373.091
3456.6135 | 373.0609
3457.6135 | 373.0473
3458.6135 | 373.1044
3459.6135 | 373.1653
3460.6135 | 373.2639
3461.6135 | 373.3369
3462.6135 | 373.3428
3463.6135 | 373.3427
3464.6135 | 373.3808
3465.6135 | 373.5219
3466.6135 | 373.5925
3467.6135 | 373.5865
3468.6135 | 373.6103
3469.6135 | 373.5322
3470.6135 | 373.5388
3471.6135 | 373.4638
3472.6135 | 373.3685
3473.6135 | 373.2835
3474.6135 | 373.1922
3475.6135 | 373.1052
3476.6135 | 373.0668
3477.6135 | 373.0541
3478.6135 | 372.9411
3479.6135 | 372.8881
3480.6135 | 372.908
3481.6135 | 372.9115
3482.6135 | 372.9065
3483.6135 | 372.8833
3484.6135 | 372.958
3485.6135 | 372.9458
3486.6135 | 372.9599
3487.6135 | 372.976
3488.6135 | 372.9192
3489.6135 | 373.015
3490.6135 | 373.0067
3491.6135 | 372.8777
3492.6135 | 372.873
3493.6135 | 372.8125
3494.6135 | 372.8282
3495.6135 | 372.8732
3496.6135 | 372.9161
3497.6135 | 373.0058
3498.6135 | 373.1484
3499.6135 | 373.1468
3500.6135 | 373.2441
3501.6135 | 373.4107
3502.6135 | 373.5337
3503.6135 | 373.5242
3504.6135 | 373.4965
3505.6135 | 373.4255
3506.6135 | 373.318
3507.6135 | 373.3084
3508.6135 | 373.3713
3509.6135 | 373.4399
3510.6135 | 373.4851
3511.6135 | 373.3779
3512.6135 | 373.4047
3513.6135 | 373.4542
3514.6135 | 373.3926
3515.6135 | 373.41
3516.6135 | 373.4158
3517.6135 | 373.4729
3518.6135 | 373.4533
3519.6135 | 373.4373
3520.6135 | 373.3587
3521.6135 | 373.3791
3522.6135 | 373.3279
3523.6135 | 373.331
3524.6135 | 373.2577
3525.6135 | 373.2967
3526.6135 | 373.2597
3527.6135 | 373.1696
3528.6135 | 373.3084
3529.6135 | 373.3979
3530.6135 | 373.4464
3531.6135 | 373.4737
3532.6135 | 373.4072
3533.6135 | 373.3806
3534.6135 | 373.2902
3535.6135 | 373.2299
3536.6135 | 373.2428
3537.6135 | 373.1965
3538.6135 | 373.1204
3539.6135 | 373.2177
3540.6135 | 373.4016
3541.6135 | 373.4578
3542.6135 | 373.4651
3543.6135 | 373.4508
3544.6135 | 373.473
3545.6135 | 373.469
3546.6135 | 373.5288
3547.6135 | 373.6514
3548.6135 | 373.7157
3549.6135 | 373.595
3550.6135 | 373.5711
3551.6135 | 373.5651
3552.6135 | 373.5938
3553.6135 | 373.6279
3554.6135 | 373.5564
3555.6135 | 373.6411
3556.6135 | 373.7023
3557.6135 | 373.5755
3558.6135 | 373.5589
3559.6292 | 373.5819
3560.6135 | 373.5836
3561.6135 | 373.6431
3562.6135 | 373.7152
3563.6135 | 373.9058
3564.6135 | 374.0016
3565.6135 | 373.9927
3566.6135 | 373.9809
3567.6135 | 374.1234
3568.6135 | 374.2323
3569.6135 | 374.1664
3570.6135 | 374.175
3571.6135 | 374.247
3572.6135 | 374.194
3573.6135 | 374.2781
3574.6135 | 374.3272
3575.6135 | 374.33
3576.6135 | 374.3367
3577.6135 | 374.2872
3578.6135 | 374.1633
3579.6135 | 374.0684
3580.6135 | 373.8604
3581.6135 | 373.7815
3582.6135 | 373.6517
3583.6135 | 373.5135
3584.6135 | 373.403
3585.6135 | 373.4101
3586.6135 | 373.399
3587.6135 | 373.2719
3588.6135 | 373.2417
3589.6135 | 373.1713
3590.6135 | 373.2553
3591.6135 | 373.3842
3592.6135 | 373.444
3593.6135 | 373.4003
3594.6135 | 373.3303
3595.6135 | 373.3904
3596.6135 | 373.4685
3597.6135 | 373.4105
3598.6135 | 373.4761
3599.6135 | 373.5726
3600.6135 | 373.6406
3601.6135 | 373.7319
3602.6135 | 373.6724
3603.6135 | 373.7392
3604.6135 | 373.7748
3605.6135 | 373.838
3606.6135 | 373.8335
3607.6135 | 373.7415
3608.6135 | 373.7076
3609.6135 | 373.7598
3610.6135 | 373.8385
3611.6135 | 373.9249
3612.6135 | 373.9906
3613.6135 | 374.0448
3614.6135 | 374.0607
3615.6135 | 374.0187
3616.6135 | 373.8285
3617.6135 | 373.708
3618.6135 | 373.6114
3619.6135 | 373.6549
3620.6135 | 373.6287
3621.6135 | 373.6021
3622.6135 | 373.5991
3623.6135 | 373.6774
3624.6135 | 373.6579
3625.6135 | 373.4963
3626.6135 | 373.5129
3627.6135 | 373.4869
3628.6135 | 373.5809
3629.6135 | 373.6082
3630.6135 | 373.595
3631.6135 | 373.5068
3632.6135 | 373.4259
3633.6135 | 373.4899
3634.6135 | 373.4584
3635.6135 | 373.4507
3636.6135 | 373.4989
3637.6135 | 373.5885
3638.6135 | 373.6018
3639.6135 | 373.5525
3640.6135 | 373.6152
3641.6135 | 373.7174
3642.6135 | 373.8497
3643.6135 | 373.9297
3644.6135 | 373.8874
3645.6135 | 373.9021
3646.6135 | 373.8182
3647.6135 | 373.8502
3648.6135 | 373.8809
3649.6135 | 373.8704
3650.6135 | 373.8045
3651.6135 | 373.8329
3652.6135 | 373.8494
3653.6135 | 373.9323
3654.6135 | 373.8829
3655.6135 | 373.7854
3656.6135 | 373.859
3657.6135 | 374.0042
3658.6135 | 374.1578
3659.6135 | 374.1294
3660.6135 | 374.0106
3661.6135 | 373.8804
3662.6135 | 373.8536
3663.6135 | 373.8349
3664.6135 | 373.752
3665.6135 | 373.6285
3666.6135 | 373.5529
3667.6135 | 373.5664
3668.6135 | 373.6231
3669.6135 | 373.5625
3670.6135 | 373.6385
3671.6135 | 373.7014
3672.6135 | 373.6802
3673.6135 | 373.6062
3674.6135 | 373.5718
3675.6135 | 373.5598
3676.6135 | 373.6644
3677.6135 | 373.7295
3678.6135 | 373.8303
3679.6135 | 373.8625
3680.6135 | 373.872
3681.6135 | 373.8929
3682.6135 | 373.7837
3683.6135 | 373.7352
3684.6135 | 373.6814
3685.6135 | 373.7521
3686.6135 | 373.8104
3687.6135 | 373.707
3688.6135 | 373.6832
3689.6135 | 373.6526
3690.6135 | 373.6657
3691.6135 | 373.6101
3692.6135 | 373.6121
3693.6135 | 373.585
3694.6135 | 373.5527
3695.6135 | 373.5027
3696.6135 | 373.506
3697.6135 | 373.5397
3698.6135 | 373.6207
3699.6135 | 373.6966
3700.6135 | 373.7679
3701.6135 | 373.8052
3702.6135 | 373.74
3703.6135 | 373.8269
3704.6135 | 374.0144
3705.6135 | 374.0677
3706.6135 | 374.0667
3707.6135 | 373.9542
3708.6135 | 373.8089
3709.6135 | 373.8035
3710.6135 | 373.8914
3711.6135 | 374.0163
3712.6135 | 374.1547
3713.6135 | 374.2517
3714.6135 | 374.2908
3715.6135 | 374.2567
3716.6135 | 374.1697
3717.6135 | 374.0849
3718.6135 | 374.0513
3719.6135 | 374.0227
3720.6135 | 373.9277
3721.6135 | 373.7945
3722.6135 | 373.7981
3723.6135 | 373.7852
3724.6135 | 373.8587
3725.6135 | 373.9423
3726.6135 | 373.8858
3727.6135 | 373.8794
3728.6135 | 373.8643
3729.6135 | 373.8182
3730.6135 | 373.6932
3731.6135 | 373.6677
3732.6135 | 373.741
3733.6135 | 373.7092
3734.6135 | 373.7168
3735.6135 | 373.7435
3736.6135 | 373.8357
3737.6135 | 373.9692
3738.6135 | 374.0366
3739.6135 | 374.0081
3740.6135 | 374.085
3741.6135 | 374.1586
3742.6135 | 374.185
3743.6135 | 374.2302
3744.6135 | 374.241
3745.6135 | 374.3249
3746.6135 | 374.3286
3747.6135 | 374.3643
3748.6135 | 374.3399
3749.6135 | 374.2698
3750.6135 | 374.3226
3751.6135 | 374.3171
3752.6135 | 374.2311
3753.6135 | 374.1291
3754.6135 | 373.9962
3755.6135 | 373.959
3756.6135 | 373.9723
3757.6135 | 373.9245
3758.6135 | 373.8277
3759.6135 | 373.8471
3760.6135 | 373.9003
3761.6135 | 373.9471
3762.6135 | 373.9225
3763.6135 | 373.9025
3764.6135 | 373.9421
3765.6135 | 373.9496
3766.6135 | 373.9834
3767.6135 | 374.0048
3768.6135 | 373.9777
3769.6135 | 373.9966
3770.6135 | 373.9595
3771.6135 | 373.867
3772.6135 | 373.8205
3773.6135 | 373.7561
3774.6135 | 373.6645
3775.6135 | 373.6251
3776.6135 | 373.6851
3777.6135 | 373.6584
3778.6135 | 373.7098
3779.6135 | 373.8176
3780.6135 | 373.8206
3781.6135 | 373.846
3782.6135 | 373.8592
3783.6135 | 373.9247
3784.6135 | 373.933
3785.6135 | 373.8957
3786.6135 | 373.7926
3787.6135 | 373.7181
3788.6135 | 373.6665
3789.6135 | 373.7494
3790.6135 | 373.7407
3791.6135 | 373.7048
3792.6135 | 373.6195
3793.6135 | 373.6323
3794.6135 | 373.7096
3795.6135 | 373.6315
3796.6135 | 373.5486
3797.6135 | 373.5836
3798.6135 | 373.5019
3799.6135 | 373.4233
3800.6135 | 373.2861
3801.6135 | 373.2836
3802.6135 | 373.3132
3803.6135 | 373.4139
3804.6135 | 373.4938
3805.6135 | 373.5895
3806.6135 | 373.6729
3807.6135 | 373.6834
3808.6135 | 373.7373
3809.6135 | 373.7152
3810.6135 | 373.6081
3811.6135 | 373.5243
3812.6135 | 373.4487
3813.6135 | 373.4224
3814.6135 | 373.2939
3815.6135 | 373.165
3816.6135 | 373.1236
3817.6135 | 373.1136
3818.6135 | 373.0179
3819.6135 | 372.9923
3820.6135 | 373.0639
3821.6135 | 372.9588
3822.6135 | 372.9044
3823.6135 | 372.895
3824.6135 | 373.0591
3825.6135 | 373.2124
3826.6135 | 373.3207
3827.6135 | 373.3565
3828.6135 | 373.2901
3829.6135 | 373.285
3830.6135 | 373.1264
3831.6135 | 373.0604
3832.6135 | 372.9706
3833.6135 | 373.0437
3834.6135 | 373.0852
3835.6135 | 373.0782
3836.6135 | 373.0318
3837.6135 | 372.9954
3838.6135 | 373.011
3839.6135 | 373.0535
3840.6135 | 373.0524
3841.6135 | 373.1248
3842.6135 | 373.0897
3843.6135 | 372.9828
3844.6135 | 372.8804
3845.6135 | 372.8388
3846.6135 | 372.8238
3847.6135 | 372.8056
3848.6135 | 372.7543
3849.6135 | 372.6939
3850.6135 | 372.7339
3851.6135 | 372.889
3852.6135 | 373.0387
3853.6135 | 373.0963
3854.6135 | 373.1
3855.6135 | 373.1067
3856.6135 | 373.0619
3857.6135 | 373.1159
3858.6135 | 373.1504
3859.6135 | 373.1359
3860.6135 | 372.9853
3861.6135 | 372.928
3862.6135 | 372.9362
3863.6135 | 372.9956
3864.6135 | 373.0053
3865.6135 | 372.9739
3866.6135 | 373.0837
3867.6135 | 373.1847
3868.6135 | 373.1799
3869.6135 | 373.2844
3870.6135 | 373.2169
3871.6135 | 373.1403
3872.6135 | 373.2518
3873.6135 | 373.3924
3874.6135 | 373.505
3875.6135 | 373.4747
3876.6135 | 373.4643
3877.6135 | 373.4998
3878.6135 | 373.5276
3879.6135 | 373.5373
3880.6135 | 373.5541
3881.6135 | 373.6509
3882.6135 | 373.6181
3883.6135 | 373.5496
3884.6135 | 373.5603
3885.6135 | 373.6138
3886.6135 | 373.6414
3887.6135 | 373.6578
3888.6135 | 373.7213
3889.6135 | 373.6899
3890.6135 | 373.6072
3891.6135 | 373.4838
3892.6135 | 373.3823
3893.6135 | 373.3234
3894.6135 | 373.2653
3895.6135 | 373.2805
3896.6135 | 373.2455
3897.6135 | 373.2666
3898.6135 | 373.2107
3899.6135 | 373.2362
3900.6135 | 373.3696
3901.6135 | 373.2419
3902.6135 | 373.2213
3903.6135 | 373.2411
3904.6135 | 373.2751
3905.6135 | 373.3456
3906.6135 | 373.3033
3907.6135 | 373.3784
3908.6135 | 373.3448
3909.6135 | 373.2983
3910.6135 | 373.3643
3911.6135 | 373.4379
3912.6135 | 373.5678
3913.6135 | 373.6156
3914.6135 | 373.6782
3915.6135 | 373.6981
3916.6135 | 373.6358
3917.6135 | 373.6804
3918.6135 | 373.6724
3919.6135 | 373.724
3920.6135 | 373.8201
3921.6135 | 373.9512
3922.6135 | 374.0858
3923.6135 | 374.2155
3924.6135 | 374.3332
3925.6135 | 374.4436
3926.6135 | 374.4511
3927.6135 | 374.4853
3928.6135 | 374.6002
3929.6135 | 374.6249
3930.6135 | 374.5147
3931.6135 | 374.4975
3932.6135 | 374.3691
3933.6135 | 374.3047
3934.6135 | 374.14
3935.6135 | 374.0699
3936.6135 | 373.9645
3937.6135 | 373.933
3938.6135 | 373.9571
3939.6135 | 374.0096
3940.6135 | 373.912
3941.6135 | 373.8113
3942.6135 | 373.7486
3943.6135 | 373.6747
3944.6135 | 373.6146
3945.6135 | 373.5044
3946.6135 | 373.4738
3947.6135 | 373.5656
3948.6135 | 373.5694
3949.6135 | 373.5464
3950.6135 | 373.5611
3951.6135 | 373.4432
3952.6135 | 373.3445
3953.6135 | 373.2754
3954.6135 | 373.2702
3955.6135 | 373.3045
3956.6135 | 373.2322
3957.6135 | 373.2313
3958.6135 | 373.2525
3959.6135 | 373.2424
3960.6135 | 373.2601
3961.6135 | 373.3596
3962.6135 | 373.4307
3963.6135 | 373.4642
3964.6135 | 373.4547
3965.6135 | 373.3577
3966.6135 | 373.2444
3967.6135 | 373.2178
3968.6135 | 373.2685
3969.6135 | 373.3515
3970.6135 | 373.3681
3971.6135 | 373.3575
3972.6135 | 373.3277
3973.6135 | 373.3859
3974.6135 | 373.3273
3975.6135 | 373.2944
3976.6135 | 373.2108
3977.6135 | 373.1923
3978.6135 | 373.1575
3979.6135 | 373.2512
3980.6135 | 373.3014
3981.6135 | 373.3467
3982.6135 | 373.3131
3983.6135 | 373.258
3984.6135 | 373.1276
3985.6135 | 373.0179
3986.6135 | 372.9948
3987.6135 | 372.983
3988.6135 | 372.9449
3989.6135 | 372.9535
3990.6135 | 373.0463
3991.6135 | 373.0465
3992.6135 | 373.0205
3993.6135 | 372.9717
3994.6135 | 372.9558
3995.6135 | 372.9512
3996.6135 | 372.9308
3997.6135 | 372.8504
3998.6135 | 372.9327
3999.6135 | 372.991
4000.6135 | 372.9935
4001.6135 | 372.9191
4002.6135 | 372.9108
4003.6135 | 372.8817
4004.6135 | 372.9402
4005.6135 | 372.9062
4006.6135 | 373.0607
4007.6135 | 373.1686
4008.6135 | 373.0952
4009.6135 | 373.083
4010.6135 | 373.1731
4011.6135 | 373.1497
4012.6135 | 373.1329
4013.6135 | 373.1148
4014.6135 | 373.0194
4015.6135 | 373.0817
4016.6135 | 373.1453
4017.6135 | 373.2343
4018.6135 | 373.3648
4019.6135 | 373.517
4020.6135 | 373.6334
4021.6135 | 373.6523
4022.6135 | 373.7233
4023.6135 | 373.7977
4024.6135 | 373.8208
4025.6135 | 373.8608
4026.6135 | 373.9246
4027.6135 | 373.8812
4028.6135 | 373.8423
4029.6135 | 373.8269
4030.6135 | 373.7856
4031.6135 | 373.7407
4032.6135 | 373.71
4033.6135 | 373.753
4034.6135 | 373.8494
4035.6135 | 373.9161
4036.6135 | 373.7229
4037.6135 | 373.5855
4038.6135 | 373.4544
4039.6135 | 373.3585
4040.6135 | 373.3451
4041.6135 | 373.383
4042.6135 | 373.4016
4043.6135 | 373.3618
4044.6135 | 373.4028
4045.6135 | 373.4959
4046.6135 | 373.5091
4047.6135 | 373.5586
4048.6135 | 373.5594
4049.6135 | 373.5355
4050.6135 | 373.49
4051.6135 | 373.4371
4052.6135 | 373.3535
4053.6135 | 373.3084
4054.6135 | 373.2667
4055.6135 | 373.2056
4056.6135 | 373.2096
4057.6135 | 373.2123
4058.6135 | 373.2512
4059.6135 | 373.2977
4060.6135 | 373.2484
4061.6135 | 373.253
4062.6135 | 373.2661
4063.6135 | 373.3275
4064.6135 | 373.2202
4065.6135 | 373.116
4066.6135 | 373.1806
4067.6135 | 373.2098
4068.6135 | 373.3371
4069.6135 | 373.3235
4070.6135 | 373.2647
4071.6135 | 373.2504
4072.6135 | 373.1316
4073.6135 | 373.1372
4074.6135 | 373.1298
4075.6135 | 373.0896
4076.6135 | 373.1417
4077.6135 | 373.1859
4078.6135 | 373.4417
4079.6135 | 373.4771
4080.6135 | 373.4213
4081.6135 | 373.4677
4082.6135 | 373.5663
4083.6135 | 373.7082
4084.6135 | 373.7477
4085.6135 | 373.7163
4086.6135 | 373.7521
4087.6135 | 373.8709
4088.6135 | 373.9191
4089.6135 | 373.9776
4090.6135 | 373.9676
4091.6135 | 373.9749
4092.6135 | 374.0032
4093.6135 | 373.9875
4094.6135 | 373.9425
4095.6135 | 373.8808
4096.6135 | 373.9739
4097.6135 | 374.1134
4098.6135 | 374.1663
4099.6135 | 374.2257
4100.6135 | 374.3032
4101.6135 | 374.3526
4102.6135 | 374.2636
4103.6135 | 374.2599
4104.6135 | 374.1771
4105.6135 | 374.177
4106.6135 | 374.1501
4107.6135 | 374.0968
4108.6135 | 374.0094
4109.6135 | 374.0127
4110.6135 | 373.9104
4111.6135 | 373.8764
4112.6135 | 373.887
4113.6135 | 373.7941
4114.6135 | 373.7448
4115.6135 | 373.7207
4116.6135 | 373.6629
4117.6135 | 373.6837
4118.6135 | 373.6549
4119.6135 | 373.6379
4120.6135 | 373.6639
4121.6135 | 373.6889
4122.6135 | 373.6866
4123.6135 | 373.6967
4124.6135 | 373.547
4125.6135 | 373.464
4126.6135 | 373.6301
4127.6135 | 373.6602
4128.6135 | 373.5374
4129.6135 | 373.5406
4130.6135 | 373.5332
4131.6135 | 373.5359
4132.6135 | 373.5873
4133.6135 | 373.5985
4134.6135 | 373.4895
4135.6135 | 373.4414
4136.6135 | 373.3628
4137.6135 | 373.3368
4138.6135 | 373.358
4139.6135 | 373.3733
4140.6135 | 373.3045
4141.6135 | 373.1739
4142.6135 | 373.1461
4143.6135 | 373.1489
4144.6135 | 373.0433
4145.6135 | 373.1237
4146.6135 | 373.2039
4147.6135 | 373.1626
4148.6135 | 373.0769
4149.6135 | 373.112
4150.6135 | 373.0647
4151.6135 | 373.0266
4152.6135 | 373.0399
4153.6135 | 373.0637
4154.6135 | 373.0578
4155.6135 | 373.0987
4156.6135 | 373.0239
4157.6135 | 373.1196
4158.6135 | 373.2322
4159.6135 | 373.2474
4160.6135 | 373.3348
4161.6135 | 373.4365
4162.6135 | 373.47
4163.6135 | 373.3849
4164.6135 | 373.2934
4165.6135 | 373.156
4166.6135 | 373.2566
4167.6135 | 373.3401
4168.6135 | 373.2491
4169.6135 | 373.1545
4170.6135 | 373.1495
4171.6135 | 373.1591
4172.6135 | 373.197
4173.6135 | 373.1822
4174.6135 | 373.1831
4175.6135 | 373.1461
4176.6135 | 373.1729
4177.6135 | 373.1634
4178.6135 | 373.1198
4179.6135 | 373.1696
4180.6135 | 373.2341
4181.6135 | 373.2201
4182.6135 | 373.1418
4183.6135 | 373.2186
4184.6135 | 373.274
4185.6135 | 373.2026
4186.6135 | 373.2863
4187.6135 | 373.4102
4188.6135 | 373.5867
4189.6135 | 373.6584
4190.6135 | 373.6744
4191.6135 | 373.7144
4192.6135 | 373.7112
4193.6135 | 373.6318
4194.6135 | 373.5766
4195.6135 | 373.5172
4196.6135 | 373.5189
4197.6135 | 373.5689
4198.6135 | 373.5207
4199.6135 | 373.558
4200.6135 | 373.7131
4201.6135 | 373.8471
4202.6135 | 373.9225
4203.6135 | 373.8416
4204.6135 | 373.7343
4205.6135 | 373.6966
4206.6135 | 373.7416
4207.6135 | 373.9015
4208.6135 | 374.0297
4209.6135 | 374.0903
4210.6135 | 374.0983
4211.6135 | 374.2489
4212.6135 | 374.241
4213.6135 | 374.2571
4214.6135 | 374.1715
4215.6135 | 374.1922
4216.6135 | 374.1488
4217.6135 | 374.1269
4218.6135 | 374.0962
4219.6135 | 374.0564
4220.6135 | 374.0371
4221.6135 | 373.9827
4222.6135 | 374.0336
4223.6135 | 374.0736
4224.6135 | 374.1839
4225.6135 | 374.2671
4226.6135 | 374.3139
4227.6135 | 374.3482
4228.6135 | 374.4175
4229.6135 | 374.3632
4230.6135 | 374.2561
4231.6135 | 374.1119
4232.6135 | 373.9776
4233.6135 | 374.0244
4234.6135 | 374.021
4235.6135 | 373.8792
4236.6135 | 373.8709
4237.6135 | 373.7765
4238.6135 | 373.7257
4239.6135 | 373.7202
4240.6135 | 373.6572
4241.6135 | 373.6075
4242.6135 | 373.6635
4243.6135 | 373.5819
4244.6135 | 373.4385
4245.6135 | 373.4129
4246.6135 | 373.4293
4247.6135 | 373.4745
4248.6135 | 373.4555
4249.6135 | 373.4203
4250.6135 | 373.3209
4251.6135 | 373.2396
4252.6135 | 373.1917
4253.6135 | 373.0815
4254.6135 | 372.9557
4255.6135 | 372.9111
4256.6135 | 372.8645
4257.6135 | 372.8139
4258.6135 | 372.7566
4259.6135 | 372.8226
4260.6135 | 372.9729
4261.6135 | 372.9534
4262.6135 | 373.0134
4263.6135 | 373.0659
4264.6135 | 373.176
4265.6135 | 373.192
4266.6135 | 373.2727
4267.6135 | 373.2342
4268.6135 | 373.185
4269.6135 | 373.1849
4270.6135 | 373.2372
4271.6135 | 373.2163
4272.6135 | 373.2047
4273.6135 | 373.2471
4274.6135 | 373.2756
4275.6135 | 373.26
4276.6135 | 373.2414
4277.6135 | 373.2657
4278.6135 | 373.3558
4279.6135 | 373.4287
4280.6135 | 373.2997
4281.6135 | 373.2139
4282.6135 | 373.1802
4283.6135 | 373.2026
4284.6135 | 373.2413
4285.6135 | 373.2821
4286.6135 | 373.401
4287.6135 | 373.3989
4288.6135 | 373.287
4289.6135 | 373.1722
4290.6135 | 373.1672
4291.6135 | 373.2287
4292.6135 | 373.1935
4293.6135 | 373.2188
4294.6135 | 373.2843
4295.6135 | 373.3939
4296.6135 | 373.302
4297.6135 | 373.3416
4298.6135 | 373.4472
4299.6135 | 373.4898
4300.6135 | 373.5224
4301.6135 | 373.5521
4302.6135 | 373.5971
4303.6135 | 373.6206
4304.6135 | 373.6232
4305.6135 | 373.5486
4306.6135 | 373.3989
4307.6135 | 373.3712
4308.6135 | 373.4009
4309.6135 | 373.5182
4310.6135 | 373.6264
4311.6135 | 373.5624
4312.6135 | 373.4734
4313.6135 | 373.4594
4314.6135 | 373.548
4315.6135 | 373.4918
4316.6135 | 373.3792
4317.6135 | 373.4182
4318.6135 | 373.5465
4319.6135 | 373.4986
4320.6135 | 373.4089
4321.6135 | 373.4231
4322.6135 | 373.4622
4323.6135 | 373.4007
4324.6135 | 373.3704
4325.6135 | 373.3319
4326.6135 | 373.3301
4327.6135 | 373.231
4328.6135 | 373.2499
4329.6135 | 373.2679
4330.6135 | 373.244
4331.6135 | 373.2996
4332.6135 | 373.4187
4333.6135 | 373.3598
4334.6135 | 373.3886
4335.6135 | 373.3741
4336.6135 | 373.3404
4337.6135 | 373.2538
4338.6135 | 373.3133
4339.6135 | 373.3623
4340.6135 | 373.2507
4341.6135 | 373.2119
4342.6135 | 373.1695
4343.6135 | 373.2174
4344.6135 | 373.2667
4345.6135 | 373.3369
4346.6135 | 373.4297
4347.6135 | 373.479
4348.6135 | 373.4625
4349.6135 | 373.3669
4350.6135 | 373.335
4351.6135 | 373.3322
4352.6135 | 373.3098
4353.6135 | 373.3115
4354.6135 | 373.2711
4355.6135 | 373.315
4356.6135 | 373.4638
4357.6135 | 373.5463
4358.6135 | 373.6268
4359.6135 | 373.707
4360.6135 | 373.751
4361.6135 | 373.7061
4362.6135 | 373.6057
4363.6135 | 373.6041
4364.6135 | 373.5439
4365.6135 | 373.582
4366.6135 | 373.6549
4367.6135 | 373.5802
4368.6135 | 373.5168
4369.6135 | 373.5765
4370.6135 | 373.6354
4371.6135 | 373.7048
4372.6135 | 373.7655
4373.6135 | 373.7672
4374.6135 | 373.8471
4375.6135 | 373.9518
4376.6135 | 373.9164
4377.6135 | 373.9889
4378.6135 | 374.0105
4379.6135 | 374.0443
4380.6135 | 373.9702
4381.6135 | 373.8937
4382.6135 | 373.8409
4383.6135 | 373.7881
4384.6135 | 373.8553
4385.6135 | 373.8985
4386.6135 | 373.8946
4387.6135 | 373.893
4388.6135 | 373.8802
4389.6135 | 373.8113
4390.6135 | 373.8048
4391.6135 | 373.9129
4392.6135 | 374.0393
4393.6135 | 373.9711
4394.6135 | 373.9351
4395.6135 | 373.9198
4396.6135 | 373.8682
4397.6135 | 373.8622
4398.6135 | 373.7259
4399.6135 | 373.6411
4400.6135 | 373.7484
4401.6135 | 373.6527
4402.6135 | 373.6047
4403.6135 | 373.6785
4404.6135 | 373.7502
4405.6135 | 373.8212
4406.6135 | 373.7977
4407.6135 | 373.8412
4408.6135 | 373.8275
4409.6135 | 373.8308
4410.6135 | 373.7548
4411.6135 | 373.7124
4412.6135 | 373.6604
4413.6135 | 373.5528
4414.6135 | 373.5537
4415.6135 | 373.5888
4416.6135 | 373.6516
4417.6135 | 373.5692
4418.6135 | 373.5281
4419.6135 | 373.6032
4420.6135 | 373.544
4421.6135 | 373.5238
4422.6135 | 373.419
4423.6135 | 373.3545
4424.6135 | 373.4041
4425.6135 | 373.4557
4426.6135 | 373.439
4427.6135 | 373.3339
4428.6135 | 373.2645
4429.6135 | 373.2138
4430.6135 | 373.3097
4431.6135 | 373.3345
4432.6135 | 373.2516
4433.6135 | 373.1684
4434.6135 | 373.1904
4435.6135 | 373.1086
4436.6135 | 373.1049
4437.6135 | 373.1638
4438.6135 | 373.0822
4439.6135 | 373.0818
4440.6135 | 373.1899
4441.6135 | 373.2895
4442.6135 | 373.2753
4443.6135 | 373.2112
4444.6135 | 373.2058
4445.6135 | 373.1591
4446.6135 | 373.1885
4447.6135 | 373.1243
4448.6135 | 373.1779
4449.6135 | 373.2655
4450.6135 | 373.3907
4451.6135 | 373.4466
4452.6135 | 373.3995
4453.6135 | 373.4247
4454.6135 | 373.5132
4455.6135 | 373.5068
4456.6135 | 373.4954
4457.6135 | 373.4654
4458.6135 | 373.4514
4459.6135 | 373.3938
4460.6135 | 373.301
4461.6135 | 373.237
4462.6135 | 373.2463
4463.6135 | 373.3255
4464.6135 | 373.3395
4465.6135 | 373.3479
4466.6135 | 373.3427
4467.6135 | 373.4434
4468.6135 | 373.4404
4469.6135 | 373.4909
4470.6135 | 373.6119
4471.6135 | 373.5971
4472.6135 | 373.3967
4473.6135 | 373.375
4474.6135 | 373.3289
4475.6135 | 373.3148
4476.6135 | 373.1498
4477.6135 | 373.0067
4478.6135 | 372.844
4479.6135 | 372.7504
4480.6135 | 372.6924
4481.6135 | 372.6437
4482.6135 | 372.5925
4483.6135 | 372.5288
4484.6135 | 372.5003
4485.6135 | 372.5167
4486.6135 | 372.677
4487.6135 | 372.7914
4488.6135 | 372.9155
4489.6135 | 372.9263
4490.6135 | 372.9728
4491.6135 | 372.9974
4492.6135 | 373.118
4493.6135 | 373.3352
4494.6135 | 373.413
4495.6135 | 373.4361
4496.6135 | 373.4693
4497.6135 | 373.3806
4498.6135 | 373.3679
4499.6135 | 373.1834
4500.6135 | 373.1292
4501.6135 | 373.1221
4502.6135 | 373.2608
4503.6135 | 373.4327
4504.6135 | 373.5559
4505.6135 | 373.5357
4506.6135 | 373.497
4507.6135 | 373.502
4508.6135 | 373.5314
4509.6135 | 373.5978
4510.6135 | 373.6759
4511.6135 | 373.684
4512.6135 | 373.664
4513.6135 | 373.6101
4514.6135 | 373.6876
4515.6135 | 373.7696
4516.6135 | 373.7591
4517.6135 | 373.6678
4518.6135 | 373.5017
4519.6135 | 373.4711
4520.6135 | 373.4805
4521.6135 | 373.4812
4522.6135 | 373.4954
4523.6135 | 373.5533
4524.6135 | 373.4736
4525.6135 | 373.3915
4526.6135 | 373.3204
4527.6135 | 373.4183
4528.6135 | 373.5664
4529.6135 | 373.5405
4530.6135 | 373.5
4531.6135 | 373.5062
4532.6135 | 373.5255
4533.6135 | 373.5775
4534.6135 | 373.481
4535.6135 | 373.4113
4536.6135 | 373.4127
4537.6135 | 373.3239
4538.6135 | 373.278
4539.6135 | 373.2868
4540.6135 | 373.2099
4541.6135 | 373.1798
4542.6135 | 373.2066
4543.6135 | 373.0614
4544.6135 | 372.9633
4545.6135 | 372.9819
4546.6135 | 373.0369
4547.6135 | 372.9999
4548.6135 | 372.9815
4549.6135 | 372.8704
4550.6135 | 372.9007
4551.6135 | 372.9656
4552.6135 | 372.9174
4553.6135 | 372.8627
4554.6135 | 372.9744
4555.6135 | 373.0774
4556.6135 | 373.0655
4557.6135 | 373.154
4558.6135 | 373.1899
4559.6135 | 373.2047
4560.6135 | 373.2601
4561.6135 | 373.1585
4562.6135 | 373.1821
4563.6135 | 373.1975
4564.6135 | 373.231
4565.6135 | 373.3678
4566.6135 | 373.4115
4567.6135 | 373.3887
4568.6135 | 373.3761
4569.6135 | 373.2783
4570.6135 | 373.2946
4571.6135 | 373.2768
4572.6135 | 373.2265
4573.6135 | 373.1852
4574.6135 | 373.1292
4575.6135 | 373.1782
4576.6135 | 373.2243
4577.6135 | 373.2842
4578.6135 | 373.3313
4579.6135 | 373.3214
4580.6135 | 373.3035
4581.6135 | 373.3205
4582.6135 | 373.4413
4583.6135 | 373.4413
4584.6135 | 373.441
4585.6135 | 373.4316
4586.6135 | 373.5171
4587.6135 | 373.5975
4588.6135 | 373.578
4589.6135 | 373.5292
4590.6135 | 373.538
4591.6135 | 373.5667
4592.6135 | 373.5613
4593.6135 | 373.5527
4594.6135 | 373.4477
4595.6135 | 373.4185
4596.6135 | 373.2987
4597.6135 | 373.1945
4598.6135 | 373.1364
4599.6135 | 373.1329
4600.6135 | 373.087
4601.6135 | 373.0128
4602.6135 | 373.0936
4603.6135 | 373.2371
4604.6135 | 373.3849
4605.6135 | 373.3022
4606.6135 | 373.3325
4607.6135 | 373.4151
4608.6135 | 373.508
4609.6135 | 373.4589
4610.6135 | 373.4231
4611.6135 | 373.3405
4612.6135 | 373.4846
4613.6135 | 373.5648
4614.6135 | 373.6507
4615.6135 | 373.7206
4616.6135 | 373.6785
4617.6135 | 373.5122
4618.6135 | 373.3982
4619.6135 | 373.3362
4620.6135 | 373.3165
4621.6135 | 373.2694
4622.6135 | 373.1874
4623.6135 | 373.2204
4624.6135 | 373.1822
4625.6135 | 373.1239
4626.6135 | 373.1257
4627.6135 | 373.0893
4628.6135 | 373.1741
4629.6135 | 373.2776
4630.6135 | 373.3266
4631.6135 | 373.2978
4632.6135 | 373.2662
4633.6135 | 373.2753
4634.6135 | 373.3059
4635.6135 | 373.5579
4636.6135 | 373.6848
4637.6135 | 373.6544
4638.6135 | 373.5774
4639.6135 | 373.492
4640.6135 | 373.5433
4641.6135 | 373.5273
4642.6135 | 373.5777
4643.6135 | 373.573
4644.6135 | 373.4878
4645.6135 | 373.4085
4646.6135 | 373.4178
4647.6135 | 373.4509
4648.6135 | 373.4136
4649.6135 | 373.6511
4650.6135 | 373.7695
4651.6135 | 373.8704
4652.6135 | 373.7401
4653.6135 | 373.7088
4654.6135 | 373.7798
4655.6135 | 373.7628
4656.6135 | 373.6959
4657.6135 | 373.6445
4658.6135 | 373.7209
4659.6135 | 373.7972
4660.6135 | 373.847
4661.6135 | 373.7967
4662.6135 | 373.7826
4663.6135 | 373.7165
4664.6135 | 373.6776
4665.6135 | 373.7305
4666.6135 | 373.6712
4667.6135 | 373.5903
4668.6135 | 373.6657
4669.6135 | 373.6702
4670.6135 | 373.6498
4671.6135 | 373.6173
4672.6135 | 373.6538
4673.6135 | 373.6939
4674.6135 | 373.7412
4675.6135 | 373.6864
4676.6135 | 373.6135
4677.6135 | 373.6826
4678.6135 | 373.725
4679.6135 | 373.7536
4680.6135 | 373.7825
4681.6135 | 373.806
4682.6135 | 373.8299
4683.6135 | 373.8765
4684.6135 | 373.913
4685.6135 | 373.9272
4686.6135 | 373.8979
4687.6135 | 373.8039
4688.6135 | 373.8283
4689.6135 | 373.8813
4690.6135 | 373.9876
4691.6135 | 374.0125
4692.6135 | 374.0007
4693.6135 | 373.9377
4694.6135 | 373.9054
4695.6135 | 373.8864
4696.6135 | 373.8888
4697.6135 | 373.8259
4698.6135 | 373.8017
4699.6135 | 373.77
4700.6135 | 373.7319
4701.6135 | 373.6183
4702.6135 | 373.5475
4703.6135 | 373.557
4704.6135 | 373.5998
4705.6135 | 373.5969
4706.6135 | 373.4872
4707.6135 | 373.456
4708.6135 | 373.5255
4709.6135 | 373.5122
4710.6135 | 373.6075
4711.6135 | 373.6604
4712.6135 | 373.7153
4713.6135 | 373.731
4714.6135 | 373.7509
4715.6135 | 373.7685
4716.6135 | 373.8106
4717.6135 | 373.7424
4718.6135 | 373.6789
4719.6135 | 373.5972
4720.6135 | 373.5181
4721.6135 | 373.5541
4722.6135 | 373.5991
4723.6135 | 373.5504
4724.6135 | 373.673
4725.6135 | 373.7463
4726.6135 | 373.6803
4727.6135 | 373.676
4728.6135 | 373.7575
4729.6135 | 373.8564
4730.6135 | 373.9333
4731.6135 | 373.8467
4732.6135 | 373.8933
4733.6135 | 373.9658
4734.6135 | 374.0606
4735.6135 | 374.1855
4736.6135 | 374.1827
4737.6135 | 374.1584
4738.6135 | 374.2516
4739.6135 | 374.2233
4740.6135 | 374.0867
4741.6135 | 374.1075
4742.6135 | 374.0591
4743.6135 | 373.9856
4744.6135 | 373.9048
4745.6135 | 373.9227
4746.6135 | 373.8578
4747.6135 | 373.8807
4748.6135 | 373.8353
4749.6135 | 373.7935
4750.6135 | 373.7238
4751.6135 | 373.7485
4752.6135 | 373.7718
4753.6135 | 373.7715
4754.6135 | 373.7373
4755.6135 | 373.6616
4756.6135 | 373.6633
4757.6135 | 373.6372
4758.6135 | 373.6113
4759.6135 | 373.704
4760.6135 | 373.7154
4761.6135 | 373.7432
4762.6135 | 373.7412
4763.6135 | 373.6537
4764.6135 | 373.6497
4765.6135 | 373.6883
4766.6135 | 373.6837
4767.6135 | 373.686
4768.6135 | 373.4906
4769.6135 | 373.4118
4770.6135 | 373.3436
4771.6135 | 373.3637
4772.6135 | 373.3198
4773.6135 | 373.3779
4774.6135 | 373.4517
4775.6135 | 373.4384
4776.6135 | 373.3775
4777.6135 | 373.3808
4778.6135 | 373.3353
4779.6135 | 373.4619
4780.6135 | 373.4429
4781.6135 | 373.4571
4782.6135 | 373.545
4783.6135 | 373.6681
4784.6135 | 373.7174
4785.6135 | 373.7549
4786.6135 | 373.7389
4787.6135 | 373.635
4788.6135 | 373.6319
4789.6135 | 373.7307
4790.6135 | 373.6926
4791.6135 | 373.7446
4792.6135 | 373.8663
4793.6135 | 373.8449
4794.6292 | 373.7017
4795.6135 | 373.5968
4796.6135 | 373.5155
4797.6135 | 373.4993
4798.6135 | 373.4597
4799.6135 | 373.4357
4800.6135 | 373.4741
4801.6135 | 373.4985
4802.6135 | 373.5707
4803.6135 | 373.5321
4804.6135 | 373.4907
4805.6135 | 373.5881
4806.6135 | 373.5757
4807.6135 | 373.5692
4808.6135 | 373.6567
4809.6135 | 373.7427
4810.6135 | 373.7463
4811.6135 | 373.656
4812.6135 | 373.549
4813.6135 | 373.5148
4814.6135 | 373.5159
4815.6135 | 373.6045
4816.6135 | 373.6254
4817.6135 | 373.7001
4818.6135 | 373.7046
4819.6135 | 373.638
4820.6135 | 373.748
4821.6135 | 373.8082
4822.6135 | 373.7354
4823.6135 | 373.7656
4824.6135 | 373.7649
4825.6135 | 373.7413
4826.6135 | 373.6655
4827.6135 | 373.5591
4828.6135 | 373.5788
4829.6135 | 373.6523
4830.6135 | 373.6649
4831.6135 | 373.5302
4832.6135 | 373.4103
4833.6135 | 373.3125
4834.6135 | 373.2357
4835.6135 | 373.2468
4836.6135 | 373.2961
4837.6135 | 373.2668
4838.6135 | 373.2712
4839.6135 | 373.1207
4840.6135 | 373.1281
4841.6135 | 373.1752
4842.6135 | 373.1985
4843.6135 | 373.2478
4844.6135 | 373.4579
4845.6135 | 373.6418
4846.6135 | 373.6972
4847.6135 | 373.7722
4848.6135 | 373.8296
4849.6135 | 373.8092
4850.6135 | 373.7718
4851.6135 | 373.8446
4852.6135 | 373.8013
4853.6135 | 373.7822
4854.6135 | 373.931
4855.6135 | 373.8833
4856.6135 | 373.8034
4857.6135 | 373.8698
4858.6135 | 373.9396
4859.6135 | 373.8601
4860.6135 | 373.7861
4861.6135 | 373.7967
4862.6135 | 373.8515
4863.6135 | 373.8939
4864.6135 | 373.8832
4865.6135 | 374.0257
4866.6135 | 374.0719
4867.6135 | 374.0758
4868.6135 | 374.0566
4869.6292 | 374.0798
4870.6135 | 374.1413
4871.6135 | 374.2749
4872.6135 | 374.3184
4873.6135 | 374.3531
4874.6135 | 374.417
4875.6135 | 374.5096
4876.6135 | 374.6242
4877.6135 | 374.5994
4878.6135 | 374.4581
4879.6135 | 374.4003
4880.6135 | 374.2965
4881.6135 | 374.2612
4882.6135 | 374.2517
4883.6135 | 374.232
4884.6135 | 374.3349
4885.6135 | 374.4982
4886.6135 | 374.4
4887.6135 | 374.2892
4888.6135 | 374.3314
4889.6135 | 374.3859
4890.6135 | 374.4395
4891.6135 | 374.4622
4892.6135 | 374.3885
4893.6135 | 374.4109
4894.6135 | 374.3967
4895.6135 | 374.3986
4896.6135 | 374.4298
4897.6135 | 374.4296
4898.6135 | 374.3891
4899.6292 | 374.3371
4900.6135 | 374.3223
4901.6135 | 374.1877
4902.6135 | 374.1443
4903.6135 | 374.1414
4904.6135 | 374.1513
4905.6135 | 374.1404
4906.6135 | 374.1295
4907.6135 | 374.1039
4908.6135 | 374.0297
4909.6135 | 373.9463
4910.6135 | 373.8732
4911.6135 | 373.8385
4912.6135 | 373.8076
4913.6135 | 373.7274
4914.6135 | 373.7476
4915.6135 | 373.8234
4916.6135 | 373.809
4917.6135 | 373.6656
4918.6135 | 373.6209
4919.6135 | 373.5993
4920.6135 | 373.4447
4921.6135 | 373.4221
4922.6135 | 373.4279
4923.6135 | 373.4075
4924.6135 | 373.3896
4925.6135 | 373.474
4926.6135 | 373.5594
4927.6135 | 373.5696
4928.6135 | 373.6478
4929.6135 | 373.6135
4930.6135 | 373.5828
4931.6135 | 373.5448
4932.6135 | 373.5656
4933.6135 | 373.5166
4934.6135 | 373.5983
4935.6135 | 373.6247
4936.6135 | 373.6214
4937.6135 | 373.7336
4938.6135 | 373.7836
4939.6135 | 373.7922
4940.6135 | 373.6668
4941.6135 | 373.6214
4942.6135 | 373.6637
4943.6135 | 373.7169
4944.6135 | 373.8608
4945.6135 | 373.9267
4946.6135 | 373.7986
4947.6135 | 373.8155
4948.6135 | 373.8883
4949.6135 | 373.9713
4950.6135 | 374.0334
4951.6135 | 373.9963
4952.6135 | 373.906
4953.6135 | 373.9936
4954.6135 | 373.9735
4955.6135 | 373.8759
4956.6135 | 373.8444
4957.6135 | 373.825
4958.6135 | 373.7991
4959.6135 | 373.9675
4960.6135 | 374.1057
4961.6135 | 374.1516
4962.6135 | 374.0993
4963.6135 | 374.1753
4964.6135 | 374.1688
4965.6135 | 374.1444
4966.6135 | 374.189
4967.6135 | 374.3925
4968.6135 | 374.3795
4969.6135 | 374.4864
4970.6135 | 374.6746
4971.6135 | 374.8015
4972.6135 | 374.8293
4973.6135 | 374.7917
4974.6135 | 374.8259
4975.6135 | 374.863
4976.6135 | 374.8664
4977.6135 | 374.7296
4978.6135 | 374.5998
4979.6135 | 374.4128
4980.6135 | 374.2811
4981.6135 | 374.3214
4982.6135 | 374.3334
4983.6135 | 374.2605
4984.6135 | 374.1357
4985.6135 | 374.1048
4986.6135 | 374.0736
4987.6135 | 374.1063
4988.6135 | 374.0784
4989.6135 | 373.9872
4990.6135 | 373.9745
4991.6135 | 373.9418
4992.6135 | 373.7973
4993.6135 | 373.6728
4994.6135 | 373.6964
4995.6135 | 373.7421
4996.6135 | 373.7391
4997.6135 | 373.6879
4998.6135 | 373.7496
4999.6135 | 373.6862
5000.6135 | 373.7398
5001.6135 | 373.814
5002.6135 | 373.726
5003.6135 | 373.6603
5004.6135 | 373.5943
5005.6135 | 373.5853
5006.6135 | 373.5653
5007.6135 | 373.5193
5008.6135 | 373.5444
5009.6135 | 373.5481
5010.6135 | 373.5127
5011.6135 | 373.5135
5012.6135 | 373.4024
5013.6135 | 373.3074
5014.6135 | 373.3745
5015.6135 | 373.54
5016.6135 | 373.5354
5017.6135 | 373.6546
5018.6135 | 373.7036
5019.6135 | 373.6326
5020.6135 | 373.4832
5021.6135 | 373.5409
5022.6135 | 373.6857
5023.6135 | 373.7399
5024.6135 | 373.8116
5025.6135 | 373.7797
5026.6135 | 373.8426
5027.6135 | 373.7846
5028.6135 | 373.8768
5029.6135 | 373.9005
5030.6135 | 374.0892
5031.6135 | 374.2282
5032.6135 | 374.3182
5033.6135 | 374.3719
5034.6135 | 374.3046
5035.6135 | 374.4129
5036.6135 | 374.4268
5037.6135 | 374.4614
5038.6135 | 374.512
5039.6135 | 374.4901
5040.6135 | 374.4565
5041.6135 | 374.3896
5042.6135 | 374.4165
5043.6135 | 374.3435
5044.6135 | 374.3001
5045.6135 | 374.2309
5046.6135 | 374.1901
5047.6135 | 374.1007
5048.6135 | 374.117
5049.6135 | 374.1314
5050.6135 | 374.1544
5051.6135 | 374.155
5052.6135 | 374.0969
5053.6135 | 374.0517
5054.6135 | 373.9927
5055.6135 | 373.9406
5056.6135 | 373.8052
5057.6135 | 373.7325
5058.6135 | 373.7135
5059.6135 | 373.7542
5060.6135 | 373.7148
5061.6135 | 373.5546
5062.6135 | 373.4272
5063.6135 | 373.4376
5064.6135 | 373.4168
5065.6135 | 373.3393
5066.6135 | 373.2066
5067.6135 | 373.1044
5068.6135 | 373.0856
5069.6135 | 373.1072
5070.6135 | 373.166
5071.6135 | 373.2779
5072.6135 | 373.3748
5073.6135 | 373.3172
5074.6135 | 373.3811
5075.6135 | 373.413
5076.6135 | 373.3666
5077.6135 | 373.2048
5078.6135 | 373.1266
5079.6135 | 373.1345
5080.6135 | 373.0939
5081.6135 | 373.1691
5082.6135 | 373.256
5083.6135 | 373.2805
5084.6135 | 373.3374
5085.6135 | 373.2967
5086.6135 | 373.3902
5087.6135 | 373.4525
5088.6135 | 373.48
5089.6135 | 373.5092
5090.6135 | 373.5586
5091.6135 | 373.5687
5092.6135 | 373.6198
5093.6135 | 373.6106
5094.6135 | 373.6727
5095.6135 | 373.7591
5096.6135 | 373.7155
5097.6135 | 373.7508
5098.6135 | 373.7911
5099.6135 | 373.7784
5100.6135 | 373.7883
5101.6135 | 373.8244
5102.6135 | 373.8292
5103.6135 | 373.7694
5104.6135 | 373.713
5105.6135 | 373.7093
5106.6135 | 373.7751
5107.6135 | 373.8705
5108.6135 | 373.8549
5109.6135 | 373.9536
5110.6135 | 374.0853
5111.6135 | 374.1071
5112.6135 | 374.1126
5113.6135 | 374.0744
5114.6135 | 374.0737
5115.6135 | 374.0096
5116.6135 | 374.0574
5117.6135 | 374.1134
5118.6135 | 374.0154
5119.6135 | 374.0629
5120.6135 | 373.993
5121.6135 | 373.9211
5122.6135 | 373.7966
5123.6135 | 373.8039
5124.6135 | 373.9209
5125.6135 | 373.9982
5126.6135 | 374.0411
5127.6135 | 373.9724
5128.6135 | 373.9437
5129.6135 | 373.9483
5130.6135 | 373.9483
5131.6135 | 373.9289
5132.6135 | 373.8935
5133.6135 | 373.7419
5134.6135 | 373.6867
5135.6135 | 373.7774
5136.6135 | 373.7053
5137.6135 | 373.6972
5138.6135 | 373.766
5139.6292 | 373.7916
5140.6135 | 373.7193
5141.6135 | 373.6963
5142.6135 | 373.7564
5143.6135 | 373.819
5144.6135 | 373.849
5145.6135 | 373.8204
5146.6135 | 373.7486
5147.6135 | 373.8201
5148.6135 | 373.7448
5149.6135 | 373.6439
5150.6135 | 373.6674
5151.6135 | 373.7063
5152.6135 | 373.5816
5153.6135 | 373.544
5154.6135 | 373.4946
5155.6135 | 373.4447
5156.6135 | 373.4724
5157.6135 | 373.4205
5158.6135 | 373.4414
5159.6135 | 373.3209
5160.6135 | 373.4269
5161.6135 | 373.2526
5162.6135 | 373.1482
5163.6135 | 373.0978
5164.6135 | 373.0594
5165.6135 | 372.9487
5166.6135 | 372.9496
5167.6135 | 372.8733
5168.6135 | 372.8214
5169.6135 | 372.7848
5170.6135 | 372.8132
5171.6135 | 372.912
5172.6135 | 372.9762
5173.6135 | 373.0982
5174.6135 | 373.1983
5175.6135 | 373.2287
5176.6135 | 373.2282
5177.6135 | 373.2179
5178.6135 | 373.217
5179.6135 | 373.2533
5180.6135 | 373.3306
5181.6135 | 373.2562
5182.6135 | 373.2653
5183.6135 | 373.319
5184.6135 | 373.333
5185.6135 | 373.4564
5186.6135 | 373.5485
5187.6135 | 373.5774
5188.6135 | 373.5675
5189.6135 | 373.5523
5190.6135 | 373.6134
5191.6135 | 373.7101
5192.6135 | 373.7595
5193.6135 | 373.877
5194.6135 | 373.998
5195.6135 | 374.1652
5196.6135 | 374.2534
5197.6135 | 374.1861
5198.6135 | 374.2539
5199.6135 | 374.2697
5200.6135 | 374.3561
5201.6135 | 374.413
5202.6135 | 374.3864
5203.6135 | 374.4196
5204.6135 | 374.4282
5205.6135 | 374.3713
5206.6135 | 374.2961
5207.6135 | 374.2226
5208.6135 | 374.2146
5209.6135 | 374.139
5210.6135 | 374.083
5211.6135 | 374.0385
5212.6135 | 373.9984
5213.6135 | 374.0517
5214.6135 | 374.057
5215.6135 | 373.996
5216.6135 | 373.9468
5217.6135 | 373.9848
5218.6135 | 373.9953
5219.6135 | 373.9848
5220.6135 | 373.9788
5221.6135 | 373.9687
5222.6135 | 374.0147
5223.6135 | 373.9606
5224.6135 | 373.9959
5225.6135 | 374.0848
5226.6135 | 374.045
5227.6135 | 374.0817
5228.6135 | 374.1253
5229.6135 | 374.2594
5230.6135 | 374.182
5231.6135 | 374.1939
5232.6135 | 374.1965
5233.6135 | 374.1413
5234.6135 | 374.1142
5235.6135 | 374.0284
5236.6135 | 373.9339
5237.6135 | 374.0154
5238.6135 | 374.1435
5239.6135 | 374.1511
5240.6135 | 374.1613
5241.6135 | 374.128
5242.6135 | 374.2158
5243.6135 | 374.275
5244.6135 | 374.2673
5245.6135 | 374.1964
5246.6135 | 374.1748
5247.6135 | 374.0363
5248.6135 | 374.0328
5249.6135 | 374.1031
5250.6135 | 374.0718
5251.6135 | 374.0314
5252.6135 | 374.0022
5253.6135 | 373.9701
5254.6135 | 374.0874
5255.6135 | 374.059
5256.6135 | 374.0819
5257.6135 | 374.0368
5258.6135 | 374.0696
5259.6135 | 373.9263
5260.6135 | 373.8969
5261.6135 | 373.9216
5262.6135 | 373.9961
5263.6135 | 374.1378
5264.6135 | 374.2263
5265.6135 | 374.4123
5266.6135 | 374.4936
5267.6135 | 374.4916
5268.6135 | 374.446
5269.6135 | 374.3592
5270.6135 | 374.2641
5271.6135 | 374.3111
5272.6135 | 374.4238
5273.6135 | 374.5638
5274.6135 | 374.6452
5275.6135 | 374.5761
5276.6135 | 374.3849
5277.6135 | 374.2904
5278.6135 | 374.2367
5279.6135 | 374.2644
5280.6135 | 374.2698
5281.6135 | 374.3141
5282.6135 | 374.3273
5283.6135 | 374.4209
5284.6135 | 374.392
5285.6135 | 374.3668
5286.6135 | 374.2042
5287.6135 | 374.0856
5288.6135 | 374.0977
5289.6135 | 374.0953
5290.6135 | 374.0565
5291.6135 | 374.0419
5292.6135 | 374.0769
5293.6135 | 374.0383
5294.6135 | 373.9542
5295.6135 | 374.0095
5296.6135 | 373.9545
5297.6135 | 373.9846
5298.6135 | 373.9969
5299.6135 | 374.0878
5300.6135 | 374.1131
5301.6135 | 374.2155
5302.6135 | 374.2314
5303.6135 | 374.1432
5304.6135 | 374.1024
5305.6135 | 374.1604
5306.6135 | 374.1176
5307.6135 | 374.1419
5308.6135 | 374.106
5309.6135 | 374.1457
5310.6135 | 374.0693
5311.6135 | 373.9947
5312.6135 | 373.9159
5313.6135 | 373.9316
5314.6135 | 373.8795
5315.6135 | 373.8168
5316.6135 | 373.7895
5317.6135 | 373.7655
5318.6135 | 373.7621
5319.6135 | 373.7895
5320.6135 | 373.9348
5321.6135 | 373.9782
5322.6135 | 374.0665
5323.6135 | 374.0747
5324.6135 | 373.9449
5325.6135 | 373.8118
5326.6135 | 373.7658
5327.6135 | 373.7602
5328.6135 | 373.788
5329.6135 | 373.7977
5330.6135 | 373.7893
5331.6135 | 373.8123
5332.6135 | 373.7469
5333.6135 | 373.7259
5334.6135 | 373.7453
5335.6135 | 373.6066
5336.6135 | 373.583
5337.6135 | 373.6281
5338.6135 | 373.6392
5339.6135 | 373.6932
5340.6292 | 373.6824
5341.6292 | 373.6728
5342.6135 | 373.5911
5343.6135 | 373.6676
5344.6135 | 373.7225
5345.6292 | 373.6774
5346.6292 | 373.7729
5347.6135 | 373.7636
5348.6135 | 373.6846
5349.6135 | 373.647
5350.6292 | 373.7025
5351.6135 | 373.7119
5352.6292 | 373.8083
5353.6292 | 373.8822
5354.6292 | 373.8943
5355.6135 | 373.9454
5356.6135 | 373.9042
5357.6135 | 373.8309
5358.6135 | 373.7283
5359.6135 | 373.6415
5360.6135 | 373.5306
5361.6135 | 373.5821
5362.6135 | 373.5579
5363.6135 | 373.4987
5364.6135 | 373.5939
5365.6135 | 373.6485
5366.6135 | 373.6218
5367.6135 | 373.5425
5368.6135 | 373.6196
5369.6135 | 373.6616
5370.6135 | 373.6792
5371.6135 | 373.6553
5372.6135 | 373.6181
5373.6135 | 373.6234
5374.6135 | 373.708
5375.6135 | 373.7496
5376.6135 | 373.6784
5377.6135 | 373.6162
5378.6135 | 373.6977
5379.6135 | 373.6878
5380.6135 | 373.6442
5381.6135 | 373.5757
5382.6135 | 373.4708
5383.6135 | 373.4896
5384.6135 | 373.5301
5385.6135 | 373.5789
5386.6135 | 373.6243
5387.6135 | 373.688
5388.6135 | 373.7732
5389.6135 | 373.8207
5390.6135 | 373.9111
5391.6135 | 373.822
5392.6135 | 373.7527
5393.6135 | 373.6816
5394.6292 | 373.7283
5395.6135 | 373.7524
5396.6135 | 373.8192
5397.6135 | 373.7481
5398.6135 | 373.554
5399.6135 | 373.4447
5400.6135 | 373.3056
5401.6135 | 373.2725
5402.6135 | 373.1922
5403.6135 | 373.1423
5404.6135 | 373.1259
5405.6135 | 373.1908
5406.6135 | 373.2572
5407.6135 | 373.3004
5408.6135 | 373.3889
5409.6135 | 373.4305
5410.6135 | 373.4387
5411.6135 | 373.3221
5412.6135 | 373.2591
5413.6135 | 373.3694
5414.6135 | 373.4368
5415.6135 | 373.39
5416.6135 | 373.3998
5417.6135 | 373.4844
5418.6135 | 373.4548
5419.6135 | 373.316
5420.6135 | 373.3029
5421.6135 | 373.2545
5422.6135 | 373.2199
5423.6135 | 373.2238
5424.6135 | 373.1293
5425.6135 | 373.1083
5426.6135 | 373.0336
5427.6135 | 373.1649
5428.6135 | 373.2542
5429.6135 | 373.2178
5430.6135 | 373.2758
5431.6135 | 373.3632
5432.6135 | 373.2933
5433.6135 | 373.2887
5434.6135 | 373.2657
5435.6135 | 373.2815
5436.6135 | 373.2957
5437.6135 | 373.3518
5438.6135 | 373.4486
5439.6135 | 373.4903
5440.6135 | 373.599
5441.6135 | 373.7164
5442.6135 | 373.7656
5443.6135 | 373.8595
5444.6135 | 373.9019
5445.6135 | 374.0152
5446.6135 | 374.0407
5447.6135 | 373.9869
5448.6135 | 373.8738
5449.6135 | 373.7741
5450.6135 | 373.6403
5451.6135 | 373.5935
5452.6135 | 373.5116
5453.6135 | 373.4852
5454.6135 | 373.4132
5455.6135 | 373.2788
5456.6135 | 373.2517
5457.6135 | 373.1512
5458.6135 | 373.1765
5459.6135 | 373.2419
5460.6135 | 373.3416
5461.6135 | 373.4005
5462.6135 | 373.4421
5463.6135 | 373.3774
5464.6135 | 373.2432
5465.6135 | 373.1857
5466.6135 | 373.195
5467.6135 | 373.285
5468.6135 | 373.305
5469.6135 | 373.3855
5470.6135 | 373.2324
5471.6135 | 373.308
5472.6135 | 373.2227
5473.6135 | 373.0718
5474.6135 | 373.1528
5475.6135 | 373.2076
5476.6135 | 373.2439
5477.6135 | 373.2453
5478.6135 | 373.3697
5479.6135 | 373.4166
5480.6135 | 373.4426
5481.6135 | 373.4916
5482.6135 | 373.5157
5483.6135 | 373.5025
5484.6135 | 373.4242
5485.6135 | 373.4042
5486.6135 | 373.5436
5487.6135 | 373.5951
5488.6135 | 373.624
5489.6135 | 373.5024
5490.6135 | 373.4109
5491.6135 | 373.4015
5492.6135 | 373.3516
5493.6135 | 373.4014
5494.6135 | 373.4434
5495.6135 | 373.4025
5496.6135 | 373.3376
5497.6135 | 373.3228
5498.6135 | 373.3056
5499.6135 | 373.4074
5500.6135 | 373.5839
5501.6135 | 373.6422
5502.6135 | 373.5435
5503.6135 | 373.5053
5504.6135 | 373.498
5505.6135 | 373.554
5506.6135 | 373.6917
5507.6135 | 373.7119
5508.6135 | 373.8357
5509.6135 | 373.8143
5510.6135 | 373.7625
5511.6135 | 373.7695
5512.6135 | 373.7787
5513.6135 | 373.8459
5514.6135 | 373.7952
5515.6135 | 373.738
5516.6135 | 373.7236
5517.6135 | 373.6593
5518.6135 | 373.6706
5519.6135 | 373.6962
5520.6135 | 373.6447
5521.6135 | 373.5775
5522.6135 | 373.4535
5523.6135 | 373.4976
5524.6135 | 373.5675
5525.6135 | 373.5219
5526.6135 | 373.5745
5527.6135 | 373.5623
5528.6135 | 373.4849
5529.6135 | 373.4263
5530.6135 | 373.4872
5531.6135 | 373.5106
5532.6135 | 373.464
5533.6135 | 373.4774
5534.6135 | 373.4815
5535.6135 | 373.4979
5536.6135 | 373.4352
5537.6135 | 373.448
5538.6135 | 373.4094
5539.6135 | 373.3761
5540.6135 | 373.3595
5541.6135 | 373.4113
5542.6135 | 373.5522
5543.6135 | 373.5639
5544.6135 | 373.6015
5545.6135 | 373.6916
5546.6135 | 373.6732
5547.6135 | 373.7154
5548.6135 | 373.7606
5549.6135 | 373.8021
5550.6135 | 373.9333
5551.6135 | 373.8967
5552.6135 | 373.8968
5553.6135 | 373.975
5554.6135 | 374.009
5555.6135 | 373.8976
5556.6135 | 373.9996
5557.6135 | 374.0042
5558.6135 | 374.0361
5559.6135 | 374.0804
5560.6135 | 374.1032
5561.6135 | 374.1371
5562.6135 | 374.1808
5563.6135 | 374.1805
5564.6135 | 374.2604
5565.6135 | 374.2352
5566.6135 | 374.3386
5567.6135 | 374.2634
5568.6135 | 374.1822
5569.6135 | 374.1827
5570.6135 | 374.1489
5571.6135 | 374.1647
5572.6135 | 373.9466
5573.6135 | 373.8757
5574.6135 | 373.883
5575.6135 | 373.9449
5576.6135 | 374.0167
5577.6135 | 374.0918
5578.6135 | 374.0985
5579.6135 | 374.1273
5580.6135 | 374.169
5581.6135 | 374.2479
5582.6135 | 374.3285
5583.6135 | 374.4221
5584.6135 | 374.4414
5585.6135 | 374.4124
5586.6135 | 374.208
5587.6135 | 374.1488
5588.6135 | 374.1493
5589.6135 | 374.1261
5590.6135 | 374.0524
5591.6135 | 373.9303
5592.6135 | 373.9221
5593.6135 | 373.9863
5594.6135 | 374.0787
5595.6135 | 374.21
5596.6135 | 374.2144
5597.6135 | 374.0925
5598.6135 | 374.0508
5599.6135 | 374.0086
5600.6135 | 373.9848
5601.6135 | 373.9625
5602.6135 | 373.909
5603.6135 | 373.9858
5604.6135 | 373.8795
5605.6135 | 373.9742
5606.6135 | 374.0536
5607.6135 | 374.0969
5608.6135 | 374.1169
5609.6135 | 374.116
5610.6135 | 374.1668
5611.6135 | 374.2348
5612.6135 | 374.2544
5613.6135 | 374.2495
5614.6135 | 374.2102
5615.6135 | 374.1324
5616.6135 | 374.1497
5617.6135 | 374.0846
5618.6135 | 373.9511
5619.6135 | 373.8313
5620.6135 | 373.8254
5621.6135 | 373.8302
5622.6135 | 373.8296
5623.6135 | 373.743
5624.6135 | 373.7376
5625.6135 | 373.6612
5626.6135 | 373.6829
5627.6135 | 373.7477
5628.6135 | 373.6257
5629.6135 | 373.5489
5630.6135 | 373.4387
5631.6135 | 373.3623
5632.6135 | 373.3367
5633.6135 | 373.4089
5634.6135 | 373.4344
5635.6135 | 373.4181
5636.6135 | 373.4135
5637.6135 | 373.5725
5638.6135 | 373.6523
5639.6135 | 373.7377
5640.6135 | 373.8196
5641.6135 | 373.7862
5642.6135 | 373.8098
5643.6135 | 373.8079
5644.6135 | 373.8037
5645.6135 | 373.7616
5646.6135 | 373.8274
5647.6135 | 373.9872
5648.6135 | 374.0253
5649.6135 | 373.9464
5650.6135 | 373.9019
5651.6135 | 373.98
5652.6135 | 373.9947
5653.6135 | 374.0111
5654.6135 | 374.035
5655.6135 | 373.9303
5656.6135 | 373.8296
5657.6135 | 373.7974
5658.6135 | 373.8416
5659.6135 | 373.8267
5660.6135 | 373.7906
5661.6135 | 373.8126
5662.6135 | 373.8036
5663.6135 | 373.754
5664.6135 | 373.6677
5665.6135 | 373.6034
5666.6135 | 373.6334
5667.6135 | 373.5849
5668.6135 | 373.5875
5669.6135 | 373.6193
5670.6135 | 373.6362
5671.6135 | 373.7547
5672.6135 | 373.7898
5673.6135 | 373.8912
5674.6135 | 373.9442
5675.6135 | 373.8451
5676.6135 | 373.7095
5677.6135 | 373.6079
5678.6135 | 373.7104
5679.6135 | 373.7629
5680.6135 | 373.6926
5681.6135 | 373.5908
5682.6135 | 373.4732
5683.6135 | 373.4905
5684.6135 | 373.5595
5685.6135 | 373.611
5686.6135 | 373.7025
5687.6135 | 373.756
5688.6135 | 373.8318
5689.6135 | 373.9136
5690.6135 | 373.966
5691.6135 | 374.0052
5692.6135 | 374.0832
5693.6135 | 374.2495
5694.6135 | 374.3836
5695.6135 | 374.4914
5696.6135 | 374.4696
5697.6135 | 374.3978
5698.6135 | 374.4421
5699.6135 | 374.4733
5700.6135 | 374.3507
5701.6135 | 374.2595
5702.6135 | 374.1322
5703.6135 | 374.0218
5704.6135 | 373.9415
5705.6135 | 373.849
5706.6135 | 373.8279
5707.6135 | 373.7546
5708.6135 | 373.7279
5709.6135 | 373.7726
5710.6135 | 373.7264
5711.6135 | 373.7301
5712.6135 | 373.6996
5713.6135 | 373.7167
5714.6135 | 373.7085
5715.6135 | 373.5966
5716.6135 | 373.6143
5717.6135 | 373.6697
5718.6135 | 373.7142
5719.6135 | 373.7473
5720.6135 | 373.7638
5721.6135 | 373.8212
5722.6135 | 373.8988
5723.6135 | 373.903
5724.6135 | 373.9285
5725.6135 | 373.8961
5726.6135 | 373.8925
5727.6135 | 373.899
5728.6135 | 373.9871
5729.6135 | 374.121
5730.6135 | 374.2148
5731.6135 | 374.2437
5732.6135 | 374.1728
5733.6135 | 374.0585
5734.6135 | 374.0401
5735.6135 | 374.0578
5736.6135 | 374.0171
5737.6135 | 374.0318
5738.6135 | 374.0499
5739.6135 | 374.0888
5740.6135 | 374.1334
5741.6135 | 374.1612
5742.6135 | 374.112
5743.6135 | 374.0678
5744.6135 | 374.0659
5745.6135 | 374.063
5746.6135 | 373.9979
5747.6135 | 374.0748
5748.6135 | 374.1343
5749.6135 | 374.1619
5750.6135 | 374.2211
5751.6135 | 374.2149
5752.6135 | 374.2077
5753.6135 | 374.2959
5754.6135 | 374.3901
5755.6135 | 374.3623
5756.6135 | 374.3917
5757.6135 | 374.387
5758.6135 | 374.3709
5759.6135 | 374.4519
5760.6135 | 374.548
5761.6135 | 374.4751
5762.6135 | 374.4663
5763.6135 | 374.3568
5764.6135 | 374.3805
5765.6135 | 374.4503
5766.6135 | 374.4206
5767.6135 | 374.4016
5768.6135 | 374.4247
5769.6135 | 374.418
5770.6135 | 374.2817
5771.6135 | 374.1995
5772.6135 | 374.1452
5773.6135 | 374.1215
5774.6135 | 373.9912
5775.6135 | 373.8875
5776.6135 | 373.7974
5777.6135 | 373.7416
5778.6135 | 373.6908
5779.6135 | 373.6118
5780.6135 | 373.4918
5781.6135 | 373.5049
5782.6135 | 373.5204
5783.6135 | 373.4642
5784.6135 | 373.4301
5785.6135 | 373.4764
5786.6135 | 373.539
5787.6135 | 373.5587
5788.6135 | 373.5105
5789.6135 | 373.4174
5790.6135 | 373.3476
5791.6135 | 373.365
5792.6135 | 373.3287
5793.6135 | 373.3661
5794.6135 | 373.4143
5795.6135 | 373.3194
5796.6135 | 373.2792
5797.6135 | 373.2265
5798.6135 | 373.1311
5799.6135 | 373.1229
5800.6135 | 373.0786
5801.6135 | 373.0086
5802.6135 | 372.9559
5803.6135 | 372.9611
5804.6135 | 372.9153
5805.6135 | 372.957
5806.6135 | 372.9841
5807.6135 | 372.9841
5808.6135 | 372.9823
5809.6135 | 373.0198
5810.6135 | 372.9631
5811.6135 | 372.9713
5812.6135 | 373.0711
5813.6135 | 373.0219
5814.6135 | 372.9508
5815.6135 | 372.8555
5816.6135 | 372.8523
5817.6135 | 372.8956
5818.6135 | 372.9941
5819.6135 | 373.0669
5820.6135 | 373.072
5821.6135 | 373.0943
5822.6135 | 373.0742
5823.6135 | 373.0503
5824.6135 | 373.0167
5825.6135 | 373.2259
5826.6135 | 373.3611
5827.6135 | 373.3983
5828.6135 | 373.3735
5829.6135 | 373.3923
5830.6135 | 373.3806
5831.6135 | 373.3172
5832.6135 | 373.3536
5833.6135 | 373.4006
5834.6135 | 373.4007
5835.6135 | 373.3618
5836.6135 | 373.4104
5837.6135 | 373.526
5838.6135 | 373.6359
5839.6135 | 373.5992
5840.6135 | 373.6218
5841.6135 | 373.6532
5842.6135 | 373.6685
5843.6135 | 373.7194
5844.6135 | 373.714
5845.6135 | 373.723
5846.6135 | 373.7292
5847.6135 | 373.7585
5848.6135 | 373.7954
5849.6135 | 373.9261
5850.6135 | 374.0464
5851.6135 | 374.094
5852.6135 | 374.0258
5853.6135 | 373.9972
5854.6135 | 374.0173
5855.6135 | 373.9897
5856.6135 | 373.932
5857.6135 | 373.9007
5858.6135 | 373.9713
5859.6135 | 374.0731
5860.6292 | 374.1119
5861.6135 | 374.1793
5862.6135 | 374.3152
5863.6135 | 374.3291
5864.6135 | 374.4071
5865.6135 | 374.5373
5866.6135 | 374.5751
5867.6135 | 374.5921
5868.6135 | 374.505
5869.6135 | 374.4832
5870.6135 | 374.5478
5871.6135 | 374.6063
5872.6135 | 374.5825
5873.6135 | 374.6159
5874.6135 | 374.6551
5875.6135 | 374.7167
5876.6135 | 374.687
5877.6135 | 374.54
5878.6135 | 374.2105
5879.6135 | 374.1313
5880.6135 | 374.2153
5881.6135 | 374.6404
5882.6135 | 375.4486
5883.6135 | 376.623
5884.6135 | 378.2191
5885.6135 | 379.8611
5886.6135 | 381.6314
5887.6135 | 383.4078
5888.6135 | 385.1363
5889.6135 | 386.77
5890.6292 | 388.3795
5891.6135 | 389.7208
5892.6135 | 390.7097
5893.6135 | 391.5901
5894.6135 | 392.515
5895.6135 | 393.2857
5896.6135 | 393.7725
5897.6135 | 394.2386
5898.6135 | 394.5795
5899.6135 | 394.8125
5900.6135 | 394.984
5901.6135 | 395.0984
5902.6135 | 395.0807
5903.6135 | 395.0329
5904.6135 | 394.9714
5905.6135 | 394.756
5906.6135 | 394.4485
5907.6135 | 394.1995
5908.6135 | 393.9766
5909.6135 | 393.6839
5910.6135 | 393.312
5911.6135 | 393.0617
5912.6135 | 392.805
5913.6135 | 392.5565
5914.6135 | 392.2935
5915.6135 | 392.1068
5916.6135 | 391.9434
5917.6135 | 391.5423
5918.6135 | 391.2081
5919.6135 | 391.0426
5920.6135 | 390.8786
5921.6135 | 390.7385
5922.6135 | 390.5806
5923.6135 | 390.346
5924.6135 | 390.1086
5925.6135 | 389.9178
5926.6135 | 389.6832
5927.6135 | 389.475
5928.6135 | 389.3362
5929.6135 | 389.2262
5930.6135 | 389.0883
5931.6135 | 388.9449
5932.6135 | 388.8747
5933.6135 | 388.9157
5934.6135 | 388.854
5935.6135 | 388.7709
5936.6135 | 388.749
5937.6135 | 388.7122
5938.6135 | 388.5949
5939.6135 | 388.5209
5940.6135 | 388.5827
5941.6135 | 388.6692
5942.6135 | 388.7049
5943.6135 | 388.6292
5944.6135 | 388.6536
5945.6135 | 388.6688
5946.6135 | 388.7637
5947.6135 | 388.7457
5948.6135 | 388.7941
5949.6135 | 388.7765
5950.6135 | 388.8123
5951.6135 | 388.8525
5952.6135 | 388.8535
5953.6135 | 388.9042
5954.6135 | 389.0783
5955.6135 | 389.1868
5956.6135 | 389.2674
5957.6135 | 389.4135
5958.6135 | 389.4986
5959.6135 | 389.4883
5960.6135 | 389.4649
5961.6135 | 389.5691
5962.6135 | 389.6144
5963.6135 | 389.6437
5964.6135 | 389.6404
5965.6135 | 389.6399
5966.6135 | 389.7925
5967.6135 | 389.9137
5968.6135 | 389.8548
5969.6135 | 389.7675
5970.6135 | 389.8486
5971.6135 | 389.9317
5972.6135 | 389.92
5973.6135 | 390.0209
5974.6135 | 390.0981
5975.6135 | 390.0314
5976.6135 | 390.0259
5977.6135 | 390.0412
5978.6135 | 390.0543
5979.6135 | 389.9151
5980.6135 | 389.7749
5981.6135 | 389.7826
5982.6135 | 389.7438
5983.6135 | 389.7736
5984.6135 | 389.8643
5985.6135 | 389.8648
5986.6135 | 389.9721
5987.6135 | 389.9632
5988.6135 | 389.8606
5989.6135 | 389.8571
5990.6135 | 389.9724
5991.6135 | 390.1021
5992.6135 | 390.1887
5993.6135 | 390.1862
5994.6292 | 390.195
5995.6135 | 390.0609
5996.6135 | 389.9378
5997.6135 | 389.8637
5998.6135 | 389.7764
5999.6135 | 389.7811
6000.6135 | 389.8218
6001.6135 | 389.8093
6002.6135 | 389.9301
6003.6135 | 389.9923
6004.6135 | 390.0315
6005.6135 | 390.0423
6006.6135 | 390.0848
6007.6135 | 390.0612
6008.6135 | 389.9478
6009.6135 | 389.8691
6010.6135 | 389.805
6011.6135 | 389.7654
6012.6135 | 389.7147
6013.6135 | 389.7202
6014.6135 | 389.7107
6015.6135 | 389.6358
6016.6135 | 389.5803
6017.6135 | 389.5326
6018.6135 | 389.4829
6019.6135 | 389.441
6020.6135 | 389.3217
6021.6135 | 389.2261
6022.6135 | 389.1576
6023.6135 | 388.9719
6024.6135 | 388.9119
6025.6135 | 388.869
6026.6135 | 388.9077
6027.6135 | 389.0204
6028.6135 | 389.061
6029.6135 | 389.0853
6030.6135 | 389.2564
6031.6135 | 389.2849
6032.6135 | 389.3157
6033.6135 | 389.2908
6034.6135 | 389.4042
6035.6135 | 389.5081
6036.6135 | 389.6464
6037.6135 | 389.8343
6038.6135 | 389.8148
6039.6135 | 389.8055
6040.6135 | 389.9016
6041.6135 | 389.9972
6042.6135 | 390.0739
6043.6135 | 390.1806
6044.6135 | 390.0426
6045.6135 | 390.0547
6046.6135 | 390.1621
6047.6135 | 390.1043
6048.6135 | 389.9983
6049.6135 | 389.9335
6050.6135 | 389.827
6051.6135 | 389.798
6052.6135 | 389.6899
6053.6135 | 389.6244
6054.6135 | 389.6422
6055.6135 | 389.6142
6056.6135 | 389.6132
6057.6135 | 389.6938
6058.6135 | 389.6486
6059.6135 | 389.572
6060.6135 | 389.4385
6061.6135 | 389.3466
6062.6135 | 389.2985
6063.6135 | 389.1584
6064.6135 | 389.0976
6065.6135 | 389.1731
6066.6135 | 389.2066
6067.6135 | 389.1824
6068.6135 | 389.074
6069.6135 | 389.0281
6070.6135 | 389.0909
6071.6135 | 389.1511
6072.6135 | 389.1581
6073.6135 | 389.1419
6074.6135 | 389.1644
6075.6135 | 389.332
6076.6135 | 389.4345
6077.6135 | 389.5713
6078.6135 | 389.6846
6079.6135 | 389.6748
6080.6135 | 389.7349
6081.6135 | 389.7456
6082.6135 | 389.8505
6083.6135 | 389.9754
6084.6135 | 389.972
6085.6135 | 389.8856
6086.6135 | 389.9095
6087.6135 | 389.9353
6088.6135 | 389.954
6089.6135 | 389.919
6090.6135 | 389.7913
6091.6135 | 389.7069
6092.6135 | 389.5599
6093.6135 | 389.4486
6094.6135 | 389.4894
6095.6135 | 389.4994
6096.6135 | 389.5259
6097.6135 | 389.4664
6098.6135 | 389.4229
6099.6135 | 389.3443
6100.6135 | 389.2209
6101.6135 | 389.2066
6102.6135 | 389.0973
6103.6135 | 389.0428
6104.6135 | 388.989
6105.6135 | 389.1082
6106.6135 | 389.1344
6107.6135 | 389.2491
6108.6135 | 389.3674
6109.6135 | 389.4499
6110.6135 | 389.4637
6111.6135 | 389.5636
6112.6135 | 389.6145
6113.6135 | 389.6647
6114.6135 | 389.7254
6115.6135 | 389.7629
6116.6135 | 389.7884
6117.6135 | 389.7872
6118.6135 | 389.7297
6119.6135 | 389.6426
6120.6135 | 389.4515
6121.6135 | 389.3258
6122.6135 | 389.3733
6123.6135 | 389.4141
6124.6135 | 389.4581
6125.6135 | 389.4812
6126.6135 | 389.4335
6127.6135 | 389.4258
6128.6135 | 389.4521
6129.6135 | 389.5594
6130.6135 | 389.6215
6131.6135 | 389.671
6132.6135 | 389.6909
6133.6135 | 389.7039
6134.6135 | 389.6627
6135.6135 | 389.742
6136.6135 | 389.6538
6137.6135 | 389.6011
6138.6135 | 389.6557
6139.6135 | 389.6749
6140.6135 | 389.673
6141.6135 | 389.5387
6142.6135 | 389.4497
6143.6135 | 389.4477
6144.6135 | 389.4015
6145.6135 | 389.3564
6146.6135 | 389.2862
6147.6135 | 389.3577
6148.6135 | 389.4286
6149.6135 | 389.4036
6150.6135 | 389.3454
6151.6135 | 389.1931
6152.6135 | 389.0875
6153.6135 | 388.9909
6154.6135 | 388.9297
6155.6135 | 388.8579
6156.6135 | 388.7232
6157.6135 | 388.7449
6158.6135 | 388.841
6159.6135 | 388.8871
6160.6135 | 388.9506
6161.6135 | 389.0332
6162.6135 | 389.0411
6163.6135 | 389.0879
6164.6135 | 389.0379
6165.6135 | 389.0008
6166.6135 | 389.0621
6167.6135 | 389.0931
6168.6135 | 388.9728
6169.6135 | 388.8636
6170.6135 | 388.6787
6171.6135 | 388.5901
6172.6135 | 388.625
6173.6135 | 388.525
6174.6135 | 388.5102
6175.6135 | 388.4917
6176.6135 | 388.4957
6177.6135 | 388.5153
6178.6135 | 388.5153
6179.6135 | 388.5849
6180.6135 | 388.5864
6181.6135 | 388.5069
6182.6135 | 388.6582
6183.6135 | 388.7632
6184.6135 | 388.7474
6185.6135 | 388.7881
6186.6135 | 388.9152
6187.6135 | 388.9891
6188.6135 | 389.1108
6189.6135 | 389.2143
6190.6135 | 389.1659
6191.6135 | 389.0839
6192.6135 | 389.058
6193.6135 | 389.0222
6194.6135 | 388.9693
6195.6135 | 388.9218
6196.6135 | 388.898
6197.6135 | 388.8609
6198.6135 | 388.8698
6199.6135 | 389.0725
6200.6135 | 389.1899
6201.6135 | 389.2752
6202.6135 | 389.3337
6203.6135 | 389.3935
6204.6135 | 389.4769
6205.6135 | 389.4663
6206.6135 | 389.4604
6207.6135 | 389.5308
6208.6135 | 389.5595
6209.6135 | 389.5897
6210.6135 | 389.6668
6211.6135 | 389.6849
6212.6135 | 389.6449
6213.6135 | 389.573
6214.6135 | 389.5635
6215.6135 | 389.4849
6216.6135 | 389.4397
6217.6135 | 389.4686
6218.6135 | 389.5396
6219.6135 | 389.5636
6220.6135 | 389.6281
6221.6135 | 389.633
6222.6135 | 389.7052
6223.6135 | 389.71
6224.6135 | 389.7852
6225.6135 | 389.8211
6226.6135 | 389.8174
6227.6135 | 389.7016
6228.6135 | 389.657
6229.6135 | 389.7284
6230.6135 | 389.8516
6231.6135 | 389.7414
6232.6135 | 389.7687
6233.6135 | 389.753
6234.6135 | 389.8348
6235.6135 | 389.9242
6236.6135 | 389.9638
6237.6135 | 390.0049
6238.6135 | 390.0358
6239.6135 | 389.9394
6240.6135 | 389.8023
6241.6135 | 389.7645
6242.6135 | 389.807
6243.6135 | 389.8205
6244.6135 | 389.6938
6245.6135 | 389.5635
6246.6135 | 389.5561
6247.6135 | 389.4481
6248.6135 | 389.3766
6249.6135 | 389.2428
6250.6135 | 389.3161
6251.6135 | 389.4495
6252.6135 | 389.409
6253.6135 | 389.4198
6254.6135 | 389.3937
6255.6135 | 389.4096
6256.6135 | 389.4525
6257.6135 | 389.4762
6258.6135 | 389.5842
6259.6135 | 389.6362
6260.6135 | 389.7122
6261.6135 | 389.8063
6262.6135 | 389.9117
6263.6135 | 389.9028
6264.6135 | 389.8772
6265.6135 | 389.8786
6266.6135 | 389.9339
6267.6135 | 390.0298
6268.6135 | 389.983
6269.6135 | 389.9217
6270.6135 | 389.8398
6271.6135 | 389.8661
6272.6135 | 389.827
6273.6135 | 389.7833
6274.6135 | 389.6336
6275.6135 | 389.6122
6276.6135 | 389.5251
6277.6135 | 389.6195
6278.6135 | 389.6102
6279.6135 | 389.5969
6280.6135 | 389.7447
6281.6135 | 389.7672
6282.6135 | 389.818
6283.6135 | 389.8073
6284.6135 | 389.9069
6285.6135 | 390.118
6286.6135 | 390.1346
6287.6135 | 390.0314
6288.6135 | 390.0373
6289.6135 | 389.9633
6290.6135 | 389.9261
6291.6135 | 390.0571
6292.6135 | 389.9767
6293.6135 | 390.0062
6294.6135 | 390.1057
6295.6135 | 390.0298
6296.6135 | 389.9315
6297.6135 | 389.9851
6298.6135 | 390.0866
6299.6135 | 390.158
6300.6135 | 389.9698
6301.6135 | 389.8959
6302.6135 | 389.7299
6303.6135 | 389.6301
6304.6135 | 389.4993
6305.6135 | 389.3944
6306.6135 | 389.3633
6307.6135 | 389.2899
6308.6135 | 389.1682
6309.6135 | 389.1845
6310.6135 | 389.2743
6311.6135 | 389.3674
6312.6135 | 389.3479
6313.6135 | 389.379
6314.6135 | 389.4441
6315.6135 | 389.4584
6316.6135 | 389.5733
6317.6135 | 389.629
6318.6135 | 389.6599
6319.6135 | 389.5549
6320.6135 | 389.4018
6321.6135 | 389.3047
6322.6135 | 389.2399
6323.6135 | 389.2548
6324.6135 | 389.1723
6325.6135 | 389.1106
6326.6135 | 389.075
6327.6135 | 388.9986
6328.6135 | 388.9022
6329.6135 | 388.7923
6330.6135 | 388.9263
6331.6135 | 389.0672
6332.6135 | 389.1414
6333.6135 | 389.1642
6334.6135 | 389.0635
6335.6135 | 389.092
6336.6135 | 389.1665
6337.6135 | 389.1698
6338.6135 | 389.2072
6339.6135 | 389.2873
6340.6135 | 389.2622
6341.6135 | 389.2819
6342.6135 | 389.3062
6343.6135 | 389.304
6344.6135 | 389.288
6345.6135 | 389.3284
6346.6135 | 389.4066
6347.6135 | 389.567
6348.6135 | 389.5174
6349.6135 | 389.5671
6350.6135 | 389.7246
6351.6135 | 389.8884
6352.6135 | 390.1083
6353.6135 | 390.2659
6354.6135 | 390.2924
6355.6135 | 390.2821
6356.6135 | 390.2676
6357.6135 | 390.1773
6358.6135 | 390.1857
6359.6135 | 390.1593
6360.6135 | 390.2492
6361.6135 | 390.3372
6362.6135 | 390.3784
6363.6135 | 390.4012
6364.6135 | 390.4557
6365.6135 | 390.5116
6366.6135 | 390.536
6367.6135 | 390.6043
6368.6135 | 390.6468
6369.6135 | 390.6891
6370.6135 | 390.7887
6371.6135 | 390.8326
6372.6135 | 390.875
6373.6135 | 390.8375
6374.6135 | 390.7523
6375.6135 | 390.7372
6376.6135 | 390.8144
6377.6135 | 390.8012
6378.6135 | 390.7884
6379.6135 | 390.8928
6380.6292 | 390.9439
6381.6135 | 391.0208
6382.6135 | 390.8954
6383.6135 | 390.6808
6384.6135 | 390.4555
6385.6135 | 390.3534
6386.6135 | 390.3582
6387.6135 | 390.3335
6388.6135 | 390.3291
6389.6135 | 390.3479
6390.6135 | 390.3645
6391.6135 | 390.2392
6392.6135 | 390.0122
6393.6135 | 390.0117
6394.6135 | 390.1215
6395.6135 | 390.01
6396.6135 | 389.9705
6397.6135 | 390.0103
6398.6135 | 390.0316
6399.6135 | 390.126
6400.6135 | 390.1568
6401.6135 | 390.0637
6402.6135 | 389.9996
6403.6135 | 389.9575
6404.6135 | 390.0018
6405.6135 | 389.9166
6406.6135 | 389.9368
6407.6135 | 389.875
6408.6135 | 389.9569
6409.6135 | 390.0275
6410.6135 | 390.0338
6411.6135 | 389.9453
6412.6135 | 389.8731
6413.6135 | 389.829
6414.6135 | 389.7227
6415.6135 | 389.5827
6416.6135 | 389.4532
6417.6135 | 389.5224
6418.6135 | 389.71
6419.6135 | 389.6729
6420.6135 | 389.63
6421.6135 | 389.6435
6422.6135 | 389.7101
6423.6135 | 389.7714
6424.6135 | 389.732
6425.6135 | 389.6322
6426.6135 | 389.5107
6427.6135 | 389.54
6428.6135 | 389.6065
6429.6135 | 389.5673
6430.6135 | 389.5675
6431.6135 | 389.5918
6432.6135 | 389.7054
6433.6135 | 389.7578
6434.6135 | 389.6661
6435.6135 | 389.6455
6436.6135 | 389.7697
6437.6135 | 389.8317
6438.6135 | 389.7746
6439.6135 | 389.7635
6440.6135 | 389.6972
6441.6135 | 389.6361
6442.6135 | 389.7702
6443.6135 | 389.8534
6444.6135 | 389.9152
6445.6135 | 390.0272
6446.6135 | 389.9455
6447.6135 | 389.9848
6448.6135 | 390.024
6449.6135 | 390.1486
6450.6135 | 390.1836
6451.6135 | 390.2502
6452.6135 | 390.3053
6453.6135 | 390.2563
6454.6135 | 390.1862
6455.6135 | 390.2166
6456.6135 | 390.2245
6457.6135 | 390.1275
6458.6135 | 390.0737
6459.6135 | 390.0549
6460.6135 | 390.0927
6461.6135 | 390.0667
6462.6135 | 390.0182
6463.6135 | 389.9572
6464.6135 | 390.0411
6465.6135 | 390.1031
6466.6135 | 390.138
6467.6135 | 390.1304
6468.6135 | 390.2339
6469.6135 | 390.1566
6470.6135 | 390.1767
6471.6135 | 390.2239
6472.6135 | 390.1106
6473.6135 | 389.9728
6474.6135 | 389.8893
6475.6135 | 389.9468
6476.6135 | 389.9784
6477.6135 | 389.8904
6478.6135 | 389.8047
6479.6135 | 389.733
6480.6135 | 389.9811
6481.6135 | 390.6645
6482.6135 | 391.8448
6483.6135 | 393.2837
6484.6135 | 395.0732
6485.6135 | 396.9535
6486.6135 | 398.7888
6487.6135 | 400.5339
6488.6135 | 402.1202
6489.6135 | 403.5558
6490.6135 | 404.8781
6491.6135 | 405.834
6492.6135 | 406.7281
6493.6135 | 407.5897
6494.6135 | 408.1658
6495.6135 | 408.5571
6496.6135 | 408.9134
6497.6135 | 409.2285
6498.6135 | 409.408
6499.6135 | 409.562
6500.6135 | 409.6348
6501.6135 | 409.5455
6502.6135 | 409.5297
6503.6135 | 409.4586
6504.6135 | 409.3368
6505.6135 | 409.1204
6506.6135 | 408.9079
6507.6135 | 408.7703
6508.6135 | 408.5978
6509.6135 | 408.3955
6510.6135 | 408.2012
6511.6135 | 408.0903
6512.6135 | 407.865
6513.6135 | 407.592
6514.6135 | 407.3153
6515.6135 | 406.9787
6516.6135 | 406.7614
6517.6135 | 406.6302
6518.6135 | 406.434
6519.6135 | 406.3723
6520.6135 | 406.1824
6521.6135 | 405.9413
6522.6135 | 405.7989
6523.6135 | 405.6532
6524.6135 | 405.4084
6525.6135 | 405.1181
6526.6135 | 404.9624
6527.6135 | 404.8878
6528.6135 | 404.772
6529.6135 | 404.5926
6530.6135 | 404.4129
6531.6135 | 404.2066
6532.6135 | 404.0416
6533.6135 | 404.1003
6534.6135 | 404.089
6535.6135 | 404.0157
6536.6135 | 403.9971
6537.6135 | 403.9378
6538.6135 | 404.0262
6539.6135 | 404.0825
6540.6135 | 404.0935
6541.6135 | 404.1064
6542.6135 | 404.0642
6543.6135 | 404.0878
6544.6135 | 404.1467
6545.6135 | 404.2205
6546.6135 | 404.3359
6547.6135 | 404.4058
6548.6135 | 404.4816
6549.6135 | 404.434
6550.6135 | 404.5384
6551.6135 | 404.5368
6552.6135 | 404.5356
6553.6135 | 404.4897
6554.6135 | 404.4278
6555.6135 | 404.4531
6556.6135 | 404.368
6557.6135 | 404.257
6558.6135 | 404.3692
6559.6135 | 404.4127
6560.6135 | 404.5314
6561.6135 | 404.5725
6562.6135 | 404.7082
6563.6135 | 404.7745
6564.6135 | 404.7898
6565.6135 | 404.7243
6566.6135 | 404.7873
6567.6135 | 404.9174
6568.6135 | 405.0524
6569.6135 | 405.1028
6570.6135 | 405.0316
6571.6135 | 405.0905
6572.6135 | 405.065
6573.6135 | 404.9896
6574.6135 | 405.0304
6575.6135 | 405.1108
6576.6135 | 405.2025
6577.6135 | 405.2604
6578.6135 | 405.2952
6579.6135 | 405.3369
6580.6135 | 405.4253
6581.6135 | 405.5125
6582.6135 | 405.5612
6583.6135 | 405.469
6584.6135 | 405.3268
6585.6135 | 405.3319
6586.6135 | 405.4287
6587.6135 | 405.2904
6588.6135 | 405.3123
6589.6135 | 405.4141
6590.6135 | 405.3465
6591.6135 | 405.2208
6592.6135 | 405.1135
6593.6135 | 405.0323
6594.6135 | 404.9848
6595.6135 | 404.9955
6596.6135 | 405.0412
6597.6135 | 405.0189
6598.6135 | 404.8944
6599.6135 | 404.8276
6600.6135 | 404.7594
6601.6135 | 404.8056
6602.6135 | 404.7272
6603.6135 | 404.711
6604.6135 | 404.6724
6605.6135 | 404.5142
6606.6135 | 404.5208
6607.6135 | 404.5415
6608.6135 | 404.569
6609.6135 | 404.6551
6610.6135 | 404.6527
6611.6135 | 404.6399
6612.6135 | 404.807
6613.6135 | 404.831
6614.6135 | 404.8155
6615.6135 | 404.7609
6616.6135 | 404.8456
6617.6135 | 404.8938
6618.6135 | 404.8586
6619.6135 | 404.9383
6620.6135 | 404.9118
6621.6135 | 404.8734
6622.6135 | 404.9382
6623.6135 | 404.8919
6624.6135 | 404.7974
6625.6135 | 404.6986
6626.6135 | 404.7616
6627.6135 | 404.8176
6628.6135 | 404.8601
6629.6135 | 404.8982
6630.6135 | 405.0011
6631.6135 | 405.0222
6632.6135 | 404.8975
6633.6135 | 404.8392
6634.6135 | 404.8011
6635.6135 | 404.7424
6636.6135 | 404.5791
6637.6135 | 404.6315
6638.6135 | 404.6385
6639.6135 | 404.6247
6640.6135 | 404.5114
6641.6135 | 404.3896
6642.6135 | 404.5163
6643.6135 | 404.4578
6644.6135 | 404.505
6645.6135 | 404.5541
6646.6135 | 404.5147
6647.6135 | 404.4693
6648.6135 | 404.4746
6649.6135 | 404.3732
6650.6135 | 404.2427
6651.6135 | 404.2502
6652.6135 | 404.3681
6653.6135 | 404.4312
6654.6135 | 404.3665
6655.6135 | 404.3475
6656.6135 | 404.298
6657.6135 | 404.2308
6658.6135 | 404.2326
6659.6135 | 404.1963
6660.6135 | 404.186
6661.6135 | 404.0755
6662.6135 | 404.1281
6663.6135 | 404.172
6664.6135 | 404.1377
6665.6135 | 404.158
6666.6135 | 404.1558
6667.6135 | 404.2703
6668.6135 | 404.2941
6669.6135 | 404.2919
6670.6135 | 404.3494
6671.6135 | 404.2906
6672.6135 | 404.2861
6673.6135 | 404.4733
6674.6135 | 404.5116
6675.6135 | 404.5501
6676.6135 | 404.5212
6677.6135 | 404.6052
6678.6135 | 404.6674
6679.6135 | 404.5669
6680.6135 | 404.5518
6681.6135 | 404.4095
6682.6135 | 404.2434
6683.6135 | 404.2271
6684.6135 | 404.2014
6685.6135 | 404.1619
6686.6135 | 404.2327
6687.6135 | 404.266
6688.6135 | 404.1606
6689.6135 | 404.0022
6690.6135 | 403.8788
6691.6135 | 403.888
6692.6135 | 403.878
6693.6135 | 403.8674
6694.6135 | 403.971
6695.6135 | 403.9405
6696.6135 | 403.8841
6697.6135 | 403.8443
6698.6135 | 403.8134
6699.6135 | 403.8323
6700.6135 | 403.8195
6701.6135 | 403.9451
6702.6135 | 404.0713
6703.6135 | 404.2183
6704.6135 | 404.1264
6705.6135 | 404.1355
6706.6135 | 404.1167
6707.6135 | 404.0333
6708.6135 | 403.9548
6709.6135 | 403.8675
6710.6135 | 403.79
6711.6135 | 403.7609
6712.6135 | 403.7246
6713.6135 | 403.8255
6714.6135 | 403.994
6715.6135 | 403.9658
6716.6135 | 403.9048
6717.6135 | 403.8805
6718.6135 | 403.7757
6719.6135 | 403.7657
6720.6135 | 403.8658
6721.6135 | 404.0221
6722.6135 | 404.0571
6723.6135 | 404.108
6724.6135 | 404.1419
6725.6135 | 404.0181
6726.6135 | 403.9967
6727.6135 | 404.0199
6728.6135 | 403.9991
6729.6135 | 404.0401
6730.6135 | 404.1422
6731.6135 | 404.3163
6732.6135 | 404.4279
6733.6135 | 404.437
6734.6135 | 404.3489
6735.6135 | 404.3501
6736.6135 | 404.349
6737.6135 | 404.2798
6738.6135 | 404.1493
6739.6135 | 404.063
6740.6292 | 404.1158
6741.6135 | 404.0718
6742.6135 | 403.9823
6743.6135 | 403.981
6744.6135 | 403.9565
6745.6135 | 403.9043
6746.6135 | 404.0073
6747.6135 | 404.0097
6748.6135 | 403.9996
6749.6135 | 403.9567
6750.6135 | 403.867
6751.6135 | 403.8704
6752.6135 | 403.8524
6753.6135 | 403.9022
6754.6135 | 404.0171
6755.6135 | 404.1148
6756.6135 | 404.0624
6757.6135 | 404.0761
6758.6135 | 404.0934
6759.6135 | 404.0184
6760.6135 | 403.9908
6761.6135 | 404.0016
6762.6135 | 404.0914
6763.6135 | 404.0965
6764.6135 | 404.1797
6765.6135 | 404.1142
6766.6135 | 404.2385
6767.6135 | 404.2436
6768.6135 | 404.2749
6769.6135 | 404.2522
6770.6135 | 404.2543
6771.6135 | 404.1664
6772.6135 | 404.151
6773.6135 | 404.1336
6774.6135 | 404.1827
6775.6135 | 404.2512
6776.6135 | 404.2546
6777.6135 | 404.1935
6778.6135 | 404.2039
6779.6135 | 404.2106
6780.6135 | 404.1615
6781.6135 | 404.189
6782.6135 | 404.1935
6783.6135 | 404.2032
6784.6135 | 404.1693
6785.6135 | 404.0831
6786.6135 | 404.0288
6787.6135 | 404.1084
6788.6135 | 404.1879
6789.6135 | 404.1856
6790.6135 | 404.1302
6791.6135 | 403.9982
6792.6135 | 403.9971
6793.6135 | 403.9272
6794.6135 | 403.9947
6795.6135 | 404.1558
6796.6135 | 404.1447
6797.6135 | 404.1454
6798.6135 | 404.2472
6799.6135 | 404.4612
6800.6135 | 404.5999
6801.6135 | 404.7221
6802.6135 | 404.7544
6803.6135 | 404.7374
6804.6135 | 404.6656
6805.6135 | 404.5148
6806.6135 | 404.4388
6807.6135 | 404.2249
6808.6135 | 404.0785
6809.6135 | 403.898
6810.6135 | 403.8268
6811.6135 | 403.7971
6812.6135 | 403.7257
6813.6135 | 403.7091
6814.6135 | 403.6717
6815.6135 | 403.553
6816.6135 | 403.5332
6817.6135 | 403.461
6818.6135 | 403.3707
6819.6135 | 403.32
6820.6135 | 403.2766
6821.6135 | 403.276
6822.6135 | 403.2614
6823.6135 | 403.348
6824.6135 | 403.5104
6825.6135 | 403.5993
6826.6135 | 403.6588
6827.6135 | 403.7275
6828.6135 | 403.719
6829.6135 | 403.7711
6830.6135 | 403.736
6831.6135 | 403.6738
6832.6135 | 403.6895
6833.6135 | 403.8124
6834.6135 | 403.6985
6835.6135 | 403.5748
6836.6135 | 403.6276
6837.6135 | 403.5059
6838.6135 | 403.411
6839.6135 | 403.4883
6840.6135 | 403.4958
6841.6135 | 403.4885
6842.6135 | 403.5
6843.6135 | 403.5728
6844.6135 | 403.5985
6845.6135 | 403.5572
6846.6135 | 403.5621
6847.6135 | 403.547
6848.6135 | 403.4859
6849.6135 | 403.3918
6850.6135 | 403.4954
6851.6135 | 403.5885
6852.6135 | 403.5895
6853.6135 | 403.6423
6854.6135 | 403.5954
6855.6135 | 403.6478
6856.6135 | 403.7442
6857.6135 | 403.8638
6858.6135 | 403.8481
6859.6135 | 403.7209
6860.6135 | 403.5844
6861.6135 | 403.6085
6862.6135 | 403.5875
6863.6135 | 403.4927
6864.6135 | 403.3942
6865.6135 | 403.2897
6866.6135 | 403.2146
6867.6135 | 403.1185
6868.6135 | 403.1046
6869.6135 | 403.1513
6870.6135 | 403.1917
6871.6135 | 403.2246
6872.6135 | 403.3613
6873.6135 | 403.4666
6874.6135 | 403.5923
6875.6135 | 403.5949
6876.6135 | 403.668
6877.6135 | 403.7666
6878.6135 | 403.829
6879.6135 | 403.9342
6880.6135 | 403.9867
6881.6135 | 404.0753
6882.6135 | 404.0475
6883.6135 | 404.0375
6884.6135 | 404.0155
6885.6135 | 404.046
6886.6135 | 403.9439
6887.6135 | 403.9913
6888.6135 | 403.9207
6889.6135 | 403.8807
6890.6135 | 403.8936
6891.6135 | 403.8845
6892.6135 | 403.8955
6893.6135 | 403.8061
6894.6135 | 403.7463
6895.6135 | 403.6627
6896.6135 | 403.6175
6897.6135 | 403.6064
6898.6135 | 403.6132
6899.6135 | 403.4719
6900.6135 | 403.3376
6901.6135 | 403.3374
6902.6135 | 403.4678
6903.6135 | 403.5081
6904.6135 | 403.4803
6905.6135 | 403.5182
6906.6135 | 403.4598
6907.6135 | 403.3281
6908.6135 | 403.2392
6909.6135 | 403.2963
6910.6135 | 403.3852
6911.6135 | 403.3859
6912.6135 | 403.6042
6913.6135 | 403.7706
6914.6135 | 403.7033
6915.6135 | 403.5936
6916.6135 | 403.5678
6917.6135 | 403.6287
6918.6135 | 403.8188
6919.6135 | 404.0422
6920.6135 | 404.1863
6921.6135 | 404.3207
6922.6135 | 404.3255
6923.6135 | 404.2429
6924.6135 | 404.2523
6925.6135 | 404.2556
6926.6135 | 404.4259
6927.6135 | 404.4505
6928.6135 | 404.4513
6929.6135 | 404.287
6930.6135 | 404.1882
6931.6135 | 404.1937
6932.6135 | 404.1926
6933.6135 | 404.1502
6934.6135 | 404.1995
6935.6135 | 404.123
6936.6135 | 404.1036
6937.6135 | 404.1044
6938.6135 | 404.2351
6939.6135 | 404.2653
6940.6135 | 404.3231
6941.6135 | 404.3238
6942.6135 | 404.2363
6943.6135 | 404.2062
6944.6135 | 404.2346
6945.6135 | 404.1604
6946.6135 | 404.2415
6947.6135 | 404.3415
6948.6135 | 404.4568
6949.6135 | 404.5846
6950.6135 | 404.6712
6951.6135 | 404.7835
6952.6135 | 404.7635
6953.6135 | 404.6507
6954.6135 | 404.5264
6955.6135 | 404.4093
6956.6135 | 404.3781
6957.6135 | 404.3762
6958.6135 | 404.2966
6959.6135 | 404.155
6960.6135 | 404.1562
6961.6135 | 404.0958
6962.6135 | 404.0854
6963.6135 | 404.0032
6964.6135 | 403.9212
6965.6135 | 403.9113
6966.6135 | 403.8445
6967.6135 | 403.9898
6968.6135 | 403.9493
6969.6135 | 404.0671
6970.6135 | 404.0375
6971.6135 | 403.9497
6972.6135 | 403.9398
6973.6135 | 404.0171
6974.6135 | 404.0314
6975.6135 | 403.9884
6976.6135 | 404.0801
6977.6135 | 404.1343
6978.6135 | 404.1269
6979.6135 | 404.0884
6980.6135 | 404.0371
6981.6135 | 404.084
6982.6135 | 404.1151
6983.6135 | 404.0867
6984.6135 | 404.0779
6985.6135 | 404.1224
6986.6135 | 404.2276
6987.6135 | 404.3744
6988.6135 | 404.4526
6989.6135 | 404.4576
6990.6135 | 404.4932
6991.6135 | 404.5865
6992.6135 | 404.5916
6993.6135 | 404.7641
6994.6135 | 404.803
6995.6135 | 404.8942
6996.6135 | 404.8477
6997.6135 | 404.8384
6998.6135 | 404.9458
6999.6135 | 404.903
7000.6135 | 404.9943
7001.6135 | 404.904
7002.6135 | 404.7844
7003.6135 | 404.7122
7004.6135 | 404.7151
7005.6135 | 404.7344
7006.6135 | 404.7945
7007.6135 | 404.726
7008.6135 | 404.6885
7009.6135 | 404.7023
7010.6135 | 404.7526
7011.6135 | 404.8613
7012.6135 | 404.7761
7013.6135 | 404.7345
7014.6135 | 404.6042
7015.6135 | 404.4072
7016.6135 | 404.3208
7017.6135 | 404.2148
7018.6135 | 404.259
7019.6135 | 404.234
7020.6135 | 404.2544
7021.6135 | 404.1446
7022.6135 | 404.1051
7023.6135 | 404.115
7024.6135 | 403.9884
7025.6135 | 403.9723
7026.6135 | 403.8477
7027.6135 | 403.8125
7028.6135 | 403.8813
7029.6135 | 403.9885
7030.6135 | 404.0184
7031.6135 | 403.9599
7032.6135 | 403.8958
7033.6135 | 403.7936
7034.6135 | 403.8402
7035.6135 | 403.9281
7036.6135 | 403.9054
7037.6135 | 403.8246
7038.6135 | 403.7744
7039.6135 | 403.8153
7040.6135 | 403.8858
7041.6135 | 403.896
7042.6292 | 403.8752
7043.6135 | 403.8546
7044.6135 | 403.7761
7045.6135 | 403.7303
7046.6135 | 403.7952
7047.6135 | 403.7619
7048.6135 | 403.7598
7049.6135 | 403.781
7050.6135 | 403.8536
7051.6135 | 404.0676
7052.6135 | 404.1886
7053.6135 | 404.233
7054.6135 | 404.2115
7055.6135 | 404.1422
7056.6135 | 404.1092
7057.6135 | 404.0435
7058.6135 | 404.0039
7059.6135 | 404.0078
7060.6135 | 403.9656
7061.6135 | 403.955
7062.6135 | 404.026
7063.6135 | 404.1946
7064.6135 | 404.3847
7065.6135 | 404.3703
7066.6135 | 404.2687
7067.6135 | 404.2441
7068.6135 | 404.07
7069.6135 | 403.972
7070.6135 | 404.0802
7071.6135 | 404.0625
7072.6135 | 403.9876
7073.6135 | 403.9948
7074.6135 | 403.8674
7075.6135 | 403.8084
7076.6135 | 403.8485
7077.6135 | 403.8874
7078.6135 | 403.8764
7079.6135 | 403.7672
7080.6135 | 403.6447
7081.6135 | 403.6447
7082.6135 | 403.7554
7083.6135 | 403.8295
7084.6135 | 403.7767
7085.6135 | 403.7813
7086.6135 | 403.894
7087.6135 | 403.9525
7088.6135 | 403.9574
7089.6135 | 403.9223
7090.6135 | 404.0114
7091.6135 | 404.1563
7092.6135 | 404.2666
7093.6135 | 404.2859
7094.6135 | 404.1822
7095.6135 | 404.2791
7096.6135 | 404.2839
7097.6135 | 404.353
7098.6135 | 404.285
7099.6135 | 404.2072
7100.6135 | 404.3513
7101.6135 | 404.3931
7102.6135 | 404.2637
7103.6135 | 404.1904
7104.6135 | 404.1899
7105.6135 | 404.2781
7106.6135 | 404.2847
7107.6135 | 404.3577
7108.6135 | 404.4275
7109.6135 | 404.5014
7110.6135 | 404.5665
7111.6135 | 404.6264
7112.6135 | 404.7561
7113.6135 | 404.9359
7114.6135 | 404.9582
7115.6135 | 405.0868
7116.6135 | 405.212
7117.6135 | 405.1796
7118.6135 | 405.2362
7119.6135 | 405.1949
7120.6135 | 405.1707
7121.6135 | 405.1378
7122.6135 | 405.0331
7123.6135 | 404.9364
7124.6135 | 404.8536
7125.6135 | 404.7905
7126.6135 | 404.7776
7127.6135 | 404.7031
7128.6135 | 404.611
7129.6135 | 404.5367
7130.6135 | 404.5286
7131.6135 | 404.4896
7132.6135 | 404.5278
7133.6135 | 404.5749
7134.6135 | 404.6536
7135.6135 | 404.6477
7136.6135 | 404.5867
7137.6135 | 404.4478
7138.6135 | 404.3775
7139.6135 | 404.4065
7140.6135 | 404.5104
7141.6135 | 404.5131
7142.6135 | 404.4089
7143.6135 | 404.3065
7144.6135 | 404.2674
7145.6135 | 404.1803
7146.6135 | 404.1567
7147.6135 | 404.1963
7148.6135 | 404.1596
7149.6135 | 404.1856
7150.6135 | 404.1002
7151.6135 | 403.9297
7152.6135 | 403.91
7153.6135 | 403.8587
7154.6135 | 403.8941
7155.6135 | 403.889
7156.6135 | 404.0012
7157.6135 | 404.062
7158.6135 | 404.0519
7159.6135 | 403.9921
7160.6135 | 403.9905
7161.6135 | 404.0225
7162.6135 | 403.9806
7163.6135 | 403.917
7164.6135 | 403.9997
7165.6135 | 404.0052
7166.6135 | 404.0809
7167.6135 | 404.0823
7168.6135 | 403.977
7169.6135 | 403.9484
7170.6135 | 404.0682
7171.6135 | 404.0325
7172.6135 | 404.1735
7173.6135 | 404.2941
7174.6135 | 404.446
7175.6135 | 404.6709
7176.6135 | 404.7308
7177.6135 | 404.7922
7178.6135 | 404.7568
7179.6135 | 404.7763
7180.6135 | 404.8181
7181.6135 | 404.6496
7182.6135 | 404.5258
7183.6135 | 404.5611
7184.6135 | 404.6053
7185.6135 | 404.5812
7186.6135 | 404.6705
7187.6135 | 404.8351
7188.6135 | 404.9154
7189.6135 | 404.9289
7190.6135 | 404.9884
7191.6135 | 405.0451
7192.6135 | 405.1755
7193.6135 | 405.2869
7194.6135 | 405.4188
7195.6135 | 405.3498
7196.6135 | 405.3342
7197.6135 | 405.2057
7198.6135 | 405.1282
7199.6135 | 405.0016
7200.6135 | 404.9358
7201.6135 | 404.9962
7202.6135 | 405.0362
7203.6135 | 405.1245
7204.6135 | 405.0505
7205.6135 | 405.0809
7206.6135 | 405.0974
7207.6135 | 405.0777
7208.6135 | 405.012
7209.6135 | 405.0108
7210.6135 | 405.0046
7211.6135 | 404.9569
7212.6135 | 404.7775
7213.6135 | 404.583
7214.6135 | 404.5773
7215.6135 | 404.5103
7216.6135 | 404.3561
7217.6135 | 404.3536
7218.6135 | 404.3986
7219.6135 | 404.4448
7220.6135 | 404.3994
7221.6135 | 404.313
7222.6135 | 404.2391
7223.6135 | 404.2311
7224.6135 | 404.3468
7225.6135 | 404.3464
7226.6135 | 404.2902
7227.6135 | 404.3425
7228.6135 | 404.2157
7229.6135 | 404.2049
7230.6135 | 404.1642
7231.6135 | 404.1394
7232.6135 | 404.1833
7233.6135 | 404.221
7234.6135 | 404.183
7235.6135 | 404.2848
7236.6135 | 404.3915
7237.6135 | 404.3495
7238.6135 | 404.3331
7239.6135 | 404.3958
7240.6135 | 404.371
7241.6135 | 404.3542
7242.6135 | 404.2803
7243.6135 | 404.3375
7244.6135 | 404.4605
7245.6135 | 404.5433
7246.6135 | 404.7408
7247.6135 | 404.8576
7248.6135 | 404.8785
7249.676 | 404.8035
7250.6292 | 404.809
7251.6135 | 404.841
7252.6135 | 404.8513
7253.6135 | 404.8399
7254.6135 | 404.8476
7255.6292 | 404.948
7256.6135 | 404.9474
7257.6135 | 404.9638
7258.6135 | 404.9256
7259.6292 | 404.8301
7260.6135 | 404.6198
7261.6135 | 404.6805
7262.6135 | 404.6108
7263.6292 | 404.5581
7264.6448 | 404.4741
7265.6135 | 404.5612
7266.6135 | 404.6699
7267.6135 | 404.7873
7268.6135 | 404.8268
7269.6135 | 404.8947
7270.6135 | 405.0053
7271.6135 | 404.9966
7272.6135 | 404.9878
7273.6135 | 404.8502
7274.6135 | 404.6768
7275.6135 | 404.568
7276.6135 | 404.5005
7277.6135 | 404.4832
7278.6135 | 404.5501
7279.6135 | 404.5763
7280.6135 | 404.6361
7281.6135 | 404.7731
7282.6135 | 404.7574
7283.6135 | 404.7881
7284.6135 | 404.7078
7285.6135 | 404.7113
7286.6135 | 404.6975
7287.6135 | 404.5683
7288.6135 | 404.5311
7289.6135 | 404.6144
7290.6135 | 404.7318
7291.6135 | 404.8017
7292.6135 | 404.8623
7293.6135 | 404.8552
7294.6135 | 404.9405
7295.6135 | 404.8624
7296.6135 | 404.8701
7297.6135 | 404.8997
7298.6135 | 404.8831
7299.6135 | 404.8854
7300.6135 | 405.0182
7301.6135 | 405.1342
7302.6135 | 405.1527
7303.6135 | 405.1671
7304.6135 | 405.2879
7305.6135 | 405.3473
7306.6135 | 405.3264
7307.6135 | 405.2442
7308.6135 | 405.2527
7309.6135 | 405.1505
7310.6135 | 405.1494
7311.6135 | 405.1296
7312.6135 | 404.9895
7313.6135 | 404.9627
7314.6135 | 404.9221
7315.6135 | 404.9439
7316.6135 | 404.9702
7317.6135 | 404.9473
7318.6135 | 404.9346
7319.6135 | 404.832
7320.6135 | 404.7356
7321.6135 | 404.5342
7322.6135 | 404.4187
7323.6135 | 404.1521
7324.6135 | 403.9085
7325.6135 | 403.5589
7326.6135 | 403.1808
7327.6135 | 402.7258
7328.6135 | 402.3109
7329.6135 | 401.9466
7330.6135 | 401.5353
7331.6135 | 401.02
7332.6135 | 400.4576
7333.6135 | 400.0423
7334.6135 | 399.4778
7335.6135 | 398.9403
7336.6135 | 398.392
7337.6135 | 397.7259
7338.6135 | 397.1673
7339.6135 | 396.5785
7340.6135 | 395.9397
7341.6135 | 395.444
7342.6135 | 394.9045
7343.6135 | 394.1372
7344.6135 | 393.5681
7345.6135 | 393.0579
7346.6135 | 392.5079
7347.6135 | 391.8978
7348.6135 | 391.2997
7349.6135 | 390.6334
7350.6135 | 389.9704
7351.6135 | 389.3041
7352.6135 | 388.6589
7353.6135 | 388.0307
7354.6135 | 387.3186
7355.6135 | 386.7429
7356.6135 | 386.2921
7357.6135 | 385.7191
7358.6135 | 385.0045
7359.6135 | 384.438
7360.6135 | 383.8482
7361.6135 | 383.2675
7362.6135 | 382.6777
7363.6135 | 382.1086
7364.6135 | 381.4329
7365.6135 | 380.8054
7366.6135 | 380.2266
7367.6135 | 379.6171
7368.6135 | 379.0968
7369.6135 | 378.6721
7370.6135 | 378.2429
7371.6135 | 377.8295
7372.6135 | 377.2366
7373.6135 | 376.6614
7374.6135 | 376.0988
7375.6135 | 375.5791
7376.6135 | 375.1061
7377.6135 | 374.5323
7378.6135 | 373.8747
7379.6135 | 373.3214
7380.6135 | 372.854
7381.6135 | 372.3628
7382.6135 | 371.8683
7383.6135 | 371.364
7384.6135 | 370.8697
7385.6135 | 370.3541
7386.6135 | 369.9355
7387.6135 | 369.3918
7388.6135 | 368.8048
7389.6135 | 368.316
7390.6135 | 367.8063
7391.6135 | 367.1706
7392.6135 | 366.7026
7393.6135 | 366.1193
7394.6135 | 365.5684
7395.6135 | 365.0207
7396.6135 | 364.3749
7397.6135 | 363.8372
7398.6135 | 363.3202
7399.6135 | 362.8897
7400.6135 | 362.3672
7401.6135 | 361.8912
7402.6135 | 361.4043
7403.6135 | 360.8421
7404.6135 | 360.345
7405.6135 | 359.9415
7406.6135 | 359.5177
7407.6135 | 359.0253
7408.6135 | 358.4318
7409.6135 | 357.983
7410.6135 | 357.3542
7411.6135 | 356.7418
7412.6135 | 356.1279
7413.6135 | 355.5474
7414.6135 | 355.0882
7415.6135 | 354.6514
7416.6135 | 354.1829
7417.6135 | 353.6929
7418.6135 | 353.1864
7419.6135 | 352.6997
7420.6135 | 352.1619
7421.6135 | 351.656
7422.6135 | 351.2064
7423.6135 | 350.8246
7424.6135 | 350.3862
7425.6135 | 349.9184
7426.6135 | 349.4018
7427.6135 | 348.8487
7428.6135 | 348.2652
7429.6135 | 347.8165
7430.6135 | 347.3951
7431.6135 | 346.9025
7432.6135 | 346.4373
7433.6135 | 345.9522
7434.6135 | 345.3795
7435.6135 | 344.8383
7436.6135 | 344.3644
7437.6135 | 343.8523
7438.6135 | 343.4505
7439.6135 | 342.9966
7440.6135 | 342.4954
7441.6135 | 341.9756
7442.6135 | 341.5341
7443.6135 | 341.0643
7444.6135 | 340.5321
7445.6135 | 340.0005
7446.6135 | 339.4899
7447.6135 | 338.9693
7448.6135 | 338.4984
7449.6135 | 337.9641
7450.6135 | 337.3853
7451.6135 | 336.8494
7452.6135 | 336.3488
7453.6135 | 335.7695
7454.6135 | 335.2558
7455.6135 | 334.7101
7456.6135 | 334.1527
7457.6135 | 333.6882
7458.6135 | 333.2634
7459.6135 | 332.9076
7460.6135 | 332.6404
7461.6135 | 332.2013
7462.6135 | 331.7934
7463.6135 | 331.3142
7464.6135 | 330.8645
7465.6135 | 330.3672
7466.6135 | 329.9093
7467.6135 | 329.4365
7468.6135 | 328.8526
7469.6135 | 328.3632
7470.6135 | 327.9401
7471.6135 | 327.5431
7472.6135 | 327.0663
7473.6135 | 326.5581
7474.6135 | 326.0974
7475.6135 | 325.5516
7476.6135 | 325.186
7477.6135 | 324.8535
7478.6135 | 324.452
7479.6135 | 324.0451
7480.6135 | 323.6033
7481.6135 | 323.1048
7482.6135 | 322.6416
7483.6135 | 322.2208
7484.6135 | 321.7708
7485.6135 | 321.2947
7486.6135 | 320.86
7487.6135 | 320.6015
7488.6135 | 320.1982
7489.6135 | 319.7263
7490.6135 | 319.1874
7491.6135 | 318.7319
7492.6135 | 318.2676
7493.6135 | 317.8475
7494.6135 | 317.4004
7495.6135 | 316.9001
7496.6135 | 316.5219
7497.6135 | 316.1211
7498.6135 | 315.6983
7499.6135 | 315.1758
7500.6135 | 314.7757
7501.6135 | 314.3506
7502.6135 | 313.9099
7503.6135 | 313.5246
7504.6135 | 313.1128
7505.6135 | 312.6434
7506.6135 | 312.1845
7507.6135 | 311.7653
7508.6135 | 311.3931
7509.6135 | 311.0347
7510.6135 | 310.5715
7511.6135 | 310.1755
7512.6135 | 309.7494
7513.6135 | 309.3311
7514.6135 | 308.9702
7515.6135 | 308.5669
7516.6135 | 308.2007
7517.6135 | 307.7396
7518.6135 | 307.2663
7519.6135 | 306.8883
7520.6135 | 306.4198
7521.6135 | 305.9649
7522.6135 | 305.52
7523.6135 | 305.0958
7524.6135 | 304.7587
7525.6135 | 304.4049
7526.6135 | 304.1211
7527.6135 | 303.8033
7528.6135 | 303.3856
7529.6135 | 303.0007
7530.6135 | 302.6815
7531.6135 | 302.3119
7532.6135 | 301.9313
7533.6135 | 301.5247
7534.6135 | 301.1022
7535.6135 | 300.6104
7536.6135 | 300.2178
7537.6135 | 299.9152
7538.6135 | 299.6056
7539.6135 | 299.2071
7540.6135 | 298.7965
7541.6135 | 298.2802
7542.6135 | 297.7545
7543.6135 | 297.3755
7544.6135 | 296.8816
7545.6135 | 296.4649
7546.6135 | 296.0393
7547.6135 | 295.7322
7548.6135 | 295.3882
7549.6135 | 295.0751
7550.6135 | 294.7393
7551.6135 | 294.435
7552.6135 | 294.0751
7553.6135 | 293.7232
7554.6135 | 293.3383
7555.6135 | 292.975
7556.6135 | 292.5734
7557.6135 | 292.1791
7558.6135 | 291.7911
7559.6135 | 291.4336
7560.6135 | 291.0104
7561.6135 | 290.6114
7562.6135 | 290.1782
7563.6135 | 289.7684
7564.6135 | 289.4142
7565.6135 | 289.089
7566.6135 | 288.761
7567.6135 | 288.4209
7568.6135 | 288.0642
7569.6135 | 287.7379
7570.6135 | 287.3796
7571.6135 | 287.0578
7572.6135 | 286.714
7573.6135 | 286.3054
7574.6135 | 285.9183
7575.6135 | 285.6119
7576.6135 | 285.2799
7577.6135 | 284.9371
7578.6135 | 284.5856
7579.6135 | 284.219
7580.6135 | 283.8872
7581.6135 | 283.5889
7582.6135 | 283.2663
7583.6135 | 282.9143
7584.6135 | 282.5741
7585.6135 | 282.201
7586.6135 | 281.8578
7587.6135 | 281.5203
7588.6135 | 281.2013
7589.6135 | 280.8516
7590.6135 | 280.5003
7591.6135 | 280.1778
7592.6135 | 279.8274
7593.6135 | 279.5185
7594.6135 | 279.2069
7595.6135 | 278.8511
7596.6135 | 278.5039
7597.6135 | 278.1764
7598.6135 | 277.7508
7599.6135 | 277.4587
7600.6135 | 277.1934
7601.6135 | 276.928
7602.6135 | 276.6291
7603.6135 | 276.3271
7604.6135 | 276.0026
7605.6135 | 275.6661
7606.6135 | 275.3134
7607.6135 | 274.9927
7608.6135 | 274.6827
7609.6135 | 274.326
7610.6135 | 273.949
7611.6135 | 273.4684
7612.6135 | 272.9972
7613.6135 | 272.6459
7614.6135 | 272.3568
7615.6135 | 272.0874
7616.6135 | 271.6933
7617.6135 | 271.3678
7618.6135 | 270.9812
7619.6135 | 270.6958
7620.6135 | 270.4147
7621.6135 | 270.1688
7622.6135 | 269.8677
7623.6135 | 269.4922
7624.6135 | 269.0936
7625.6135 | 268.7014
7626.6135 | 268.3754
7627.6135 | 268.0207
7628.6135 | 267.6358
7629.6135 | 267.3176
7630.6135 | 267.0305
7631.6135 | 266.675
7632.6135 | 266.3723
7633.6135 | 266.0467
7634.6135 | 265.7605
7635.6135 | 265.458
7636.6135 | 265.1316
7637.6135 | 264.8298
7638.6135 | 264.5616
7639.6135 | 264.2078
7640.6135 | 263.9078
7641.6135 | 263.6534
7642.6135 | 263.3983
7643.6135 | 263.1124
7644.6135 | 262.7895
7645.6135 | 262.4893
7646.6135 | 262.1634
7647.6135 | 261.8433
7648.6135 | 261.596
7649.6135 | 261.3714
7650.6135 | 261.0661
7651.6135 | 260.7293
7652.6135 | 260.4363
7653.6135 | 260.129
7654.6135 | 259.8889
7655.6135 | 259.5773
7656.6135 | 259.2813
7657.6135 | 258.9627
7658.6135 | 258.5667
7659.6135 | 258.22
7660.6135 | 257.9174
7661.6135 | 257.6245
7662.6135 | 257.3407
7663.6135 | 257.037
7664.6135 | 256.7988
7665.6135 | 256.5073
7666.6135 | 256.2934
7667.6135 | 256.0575
7668.6135 | 255.7647
7669.6135 | 255.5153
7670.6135 | 255.1802
7671.6135 | 254.874
7672.6135 | 254.5365
7673.6135 | 254.2882
7674.6135 | 253.9565
7675.6135 | 253.6133
7676.6135 | 253.304
7677.6135 | 252.9928
7678.6135 | 252.6846
7679.6135 | 252.3616
7680.6135 | 252.0819
7681.6135 | 251.762
7682.6135 | 251.4362
7683.6135 | 251.1381
7684.6135 | 250.8779
7685.6135 | 250.6696
7686.6135 | 250.4165
7687.6135 | 250.1674
7688.6135 | 249.8972
7689.6135 | 249.5597
7690.6135 | 249.2243
7691.6135 | 248.8784
7692.6135 | 248.5494
7693.6135 | 248.2526
7694.6135 | 247.932
7695.6135 | 247.65
7696.6135 | 247.4313
7697.6135 | 247.2319
7698.6135 | 246.9514
7699.6135 | 246.6735
7700.6135 | 246.343
7701.6135 | 246.0715
7702.6135 | 245.7934
7703.6135 | 245.5268
7704.6135 | 245.2775
7705.6135 | 244.9836
7706.6135 | 244.7383
7707.6135 | 244.5115
7708.6135 | 244.1846
7709.6135 | 243.8593
7710.6135 | 243.6302
7711.6135 | 243.4067
7712.6135 | 243.1799
7713.6135 | 242.9134
7714.6135 | 242.6414
7715.6135 | 242.3686
7716.6135 | 242.0583
7717.6135 | 241.6883
7718.6135 | 241.4265
7719.6135 | 241.2082
7720.6135 | 240.9693
7721.6135 | 240.7936
7722.6135 | 240.6636
7723.6135 | 240.4034
7724.6135 | 240.1611
7725.6135 | 239.8484
7726.6135 | 239.5936
7727.6135 | 239.3441
7728.6135 | 239.0821
7729.6135 | 238.7502
7730.6135 | 238.5388
7731.6135 | 238.241
7732.6135 | 237.9151
7733.6135 | 237.6413
7734.6135 | 237.3762
7735.6135 | 237.0701
7736.6135 | 236.8182
7737.6135 | 236.5565
7738.6135 | 236.323
7739.6135 | 236.074
7740.6135 | 235.8039
7741.6135 | 235.5599
7742.6135 | 235.3386
7743.6135 | 235.0899
7744.6135 | 234.8103
7745.6135 | 234.623
7746.6135 | 234.4288
7747.6135 | 234.2
7748.6135 | 233.9038
7749.6135 | 233.5937
7750.6135 | 233.3091
7751.6135 | 232.9957
7752.6135 | 232.7751
7753.6135 | 232.5738
7754.6135 | 232.3312
7755.6135 | 232.0764
7756.6135 | 231.8238
7757.6135 | 231.624
7758.6135 | 231.3475
7759.6135 | 231.1196
7760.6135 | 230.8927
7761.6135 | 230.6893
7762.6135 | 230.4626
7763.6135 | 230.1832
7764.6135 | 229.9339
7765.6135 | 229.653
7766.6135 | 229.3829
7767.6135 | 229.1018
7768.6135 | 228.8518
7769.6135 | 228.6296
7770.6135 | 228.4241
7771.6135 | 228.2155
7772.6135 | 227.9875
7773.6135 | 227.7263
7774.6135 | 227.424
7775.6135 | 227.1785
7776.6135 | 226.9645
7777.6135 | 226.7283
7778.6135 | 226.4843
7779.6135 | 226.2568
7780.6135 | 225.9929
7781.6135 | 225.7267
7782.6135 | 225.4915
7783.6135 | 225.2169
7784.6135 | 224.9511
7785.6135 | 224.7304
7786.6135 | 224.5048
7787.6135 | 224.1676
7788.6135 | 223.8698
7789.6135 | 223.6052
7790.6135 | 223.4044
7791.6135 | 223.2166
7792.6135 | 223.0508
7793.6135 | 222.8807
7794.6135 | 222.6211
7795.6135 | 222.2952
7796.6135 | 222.0056
7797.6135 | 221.7901
7798.6135 | 221.596
7799.6135 | 221.4009
7800.6135 | 221.179
7801.6135 | 220.8999
7802.6135 | 220.6015
7803.6135 | 220.3746
7804.6135 | 220.1263
7805.6135 | 219.9041
7806.6135 | 219.7095
7807.6135 | 219.5005
7808.6135 | 219.3273
7809.6135 | 219.1341
7810.6135 | 218.8918
7811.6135 | 218.6801
7812.6135 | 218.4693
7813.6135 | 218.2767
7814.6135 | 218.0176
7815.6135 | 217.7883
7816.6135 | 217.5455
7817.6135 | 217.3057
7818.6135 | 217.0814
7819.6135 | 216.8245
7820.6135 | 216.611
7821.6135 | 216.4082
7822.6135 | 216.1931
7823.6135 | 215.9762
7824.6135 | 215.7555
7825.6135 | 215.5794
7826.6135 | 215.3566
7827.6135 | 215.113
7828.6135 | 214.913
7829.6135 | 214.6989
7830.6135 | 214.5535
7831.6135 | 214.3149
7832.6135 | 214.1241
7833.6135 | 213.8876
7834.6135 | 213.7447
7835.6135 | 213.5658
7836.6135 | 213.3928
7837.6135 | 213.1796
7838.6135 | 212.9377
7839.6135 | 212.646
7840.6135 | 212.3725
7841.6135 | 212.1621
7842.6135 | 211.9274
7843.6135 | 211.7448
7844.6135 | 211.5654
7845.6135 | 211.3372
7846.6135 | 211.0753
7847.6135 | 210.8474
7848.6135 | 210.5993
7849.6135 | 210.4003
7850.6135 | 210.1916
7851.6135 | 209.9425
7852.6135 | 209.7775
7853.6135 | 209.6482
7854.6135 | 209.4419
7855.6135 | 209.215
7856.6135 | 208.9701
7857.6135 | 208.7897
7858.6135 | 208.6151
7859.6135 | 208.3922
7860.6135 | 208.1954
7861.6135 | 207.9924
7862.6135 | 207.7957
7863.6135 | 207.6172
7864.6135 | 207.3904
7865.6135 | 207.1615
7866.6135 | 206.9884
7867.6135 | 206.7893
7868.6135 | 206.5674
7869.6135 | 206.388
7870.6135 | 206.1837
7871.6135 | 206.0277
7872.6135 | 205.8132
7873.6135 | 205.5159
7874.6135 | 205.3292
7875.6135 | 205.1633
7876.6135 | 205.0051
7877.6135 | 204.8112
7878.6135 | 204.5281
7879.6135 | 204.3131
7880.6135 | 204.124
7881.6135 | 203.8758
7882.6135 | 203.6859
7883.6135 | 203.5075
7884.6135 | 203.2956
7885.6135 | 203.1412
7886.6135 | 202.9045
7887.6135 | 202.6912
7888.6135 | 202.5036
7889.6135 | 202.3184
7890.6135 | 202.0748
7891.6135 | 201.803
7892.6135 | 201.581
7893.6135 | 201.4142
7894.6135 | 201.2283
7895.6135 | 200.99
7896.6135 | 200.7633
7897.6135 | 200.544
7898.6135 | 200.4035
7899.6135 | 200.2592
7900.6135 | 200.0537
7901.6135 | 199.8602
7902.6135 | 199.6667
7903.6135 | 199.4459
7904.6135 | 199.3009
7905.6135 | 199.087
7906.6135 | 198.8914
7907.6135 | 198.7313
7908.6135 | 198.5609
7909.6135 | 198.3836
7910.6135 | 198.1874
7911.6135 | 197.9526
7912.6135 | 197.7664
7913.6135 | 197.5666
7914.6135 | 197.3732
7915.6135 | 197.1903
7916.6135 | 197.0262
7917.6135 | 196.8487
7918.6135 | 196.6667
7919.6135 | 196.4305
7920.6135 | 196.2063
7921.6135 | 196.035
7922.6135 | 195.8593
7923.6135 | 195.6814
7924.6135 | 195.4138
7925.6135 | 195.1415
7926.6135 | 194.9594
7927.6135 | 194.8379
7928.6135 | 194.6499
7929.6135 | 194.4702
7930.6135 | 194.3185
7931.6135 | 194.134
7932.6135 | 193.9363
7933.6135 | 193.7336
7934.6135 | 193.5544
7935.6135 | 193.3937
7936.6135 | 193.1639
7937.6135 | 192.908
7938.6135 | 192.7394
7939.6135 | 192.5804
7940.6135 | 192.4105
7941.6135 | 192.2058
7942.6135 | 191.9971
7943.6135 | 191.8911
7944.6135 | 191.7948
7945.6135 | 191.6231
7946.6135 | 191.3877
7947.6135 | 191.1998
7948.6135 | 190.9979
7949.6135 | 190.8032
7950.6135 | 190.6207
7951.6135 | 190.4447
7952.6135 | 190.31
7953.6135 | 190.1493
7954.6135 | 190.0087
7955.6135 | 189.8705
7956.6135 | 189.7106
7957.6135 | 189.589
7958.6135 | 189.4097
7959.6135 | 189.189
7960.6135 | 188.9628
7961.6135 | 188.7341
7962.6135 | 188.4739
7963.6135 | 188.2654
7964.6135 | 188.0543
7965.6135 | 187.9031
7966.6135 | 187.7482
7967.6135 | 187.5767
7968.6135 | 187.3999
7969.6135 | 187.2424
7970.6135 | 187.0579
7971.6135 | 186.8695
7972.6135 | 186.6901
7973.6135 | 186.5412
7974.6135 | 186.4126
7975.6135 | 186.2822
7976.6135 | 186.127
7977.6135 | 185.9743
7978.6135 | 185.7749
7979.6135 | 185.5909
7980.6135 | 185.4165
7981.6135 | 185.263
7982.6135 | 185.046
7983.6135 | 184.8832
7984.6135 | 184.741
7985.6135 | 184.5664
7986.6135 | 184.4233
7987.6135 | 184.2887
7988.6135 | 184.0425
7989.6135 | 183.8478
7990.6135 | 183.6666
7991.6135 | 183.5173
7992.6135 | 183.3765
7993.6135 | 183.1985
7994.6135 | 183.0552
7995.6135 | 182.8922
7996.6135 | 182.6703
7997.6135 | 182.4882
7998.6135 | 182.3298
7999.6135 | 182.1407
8000.6135 | 181.9957
8001.6135 | 181.8864
8002.6135 | 181.7008
8003.6135 | 181.5396
8004.6135 | 181.3984
8005.6135 | 181.2224
8006.6135 | 181.0467
8007.6135 | 180.8772
8008.6135 | 180.7324
8009.6135 | 180.5379
8010.6135 | 180.4043
8011.6135 | 180.2555
8012.6135 | 180.1368
8013.6135 | 180.0269
8014.6135 | 179.8413
8015.6135 | 179.6537
8016.6135 | 179.4688
8017.6135 | 179.3045
8018.6135 | 179.1558
8019.6135 | 179.0241
8020.6135 | 178.9208
8021.6135 | 178.7548
8022.6135 | 178.6105
8023.6135 | 178.4062
8024.6135 | 178.2367
8025.6135 | 178.0723
8026.6135 | 177.9097
8027.6135 | 177.7643
8028.6135 | 177.6776
8029.6135 | 177.5158
8030.6135 | 177.3009
8031.6135 | 177.0954
8032.6135 | 176.9828
8033.6135 | 176.8038
8034.6135 | 176.6833
8035.6135 | 176.5231
8036.6135 | 176.373
8037.6135 | 176.2052
8038.6135 | 176.0209
8039.6135 | 175.8497
8040.6135 | 175.6666
8041.6135 | 175.5308
8042.6135 | 175.359
8043.6135 | 175.2315
8044.6135 | 175.1328
8045.6135 | 175.0045
8046.6135 | 174.8208
8047.6135 | 174.6587
8048.6135 | 174.5066
8049.6135 | 174.3604
8050.6135 | 174.1777
8051.6135 | 173.9993
8052.6135 | 173.8148
8053.6135 | 173.6181
8054.6135 | 173.4533
8055.6135 | 173.2521
8056.6135 | 173.1261
8057.6135 | 172.9942
8058.6135 | 172.8331
8059.6135 | 172.6942
8060.6135 | 172.542
8061.6135 | 172.3812
8062.6135 | 172.1851
8063.6135 | 172.0564
8064.6135 | 171.9224
8065.6135 | 171.7482
8066.6135 | 171.5544
8067.6135 | 171.429
8068.6135 | 171.2906
8069.6135 | 171.1367
8070.6135 | 170.9995
8071.6135 | 170.8623
8072.6135 | 170.6966
8073.6135 | 170.5677
8074.6135 | 170.4039
8075.6135 | 170.2918
8076.6135 | 170.1272
8077.6135 | 169.9457
8078.6135 | 169.8085
8079.6135 | 169.6492
8080.6135 | 169.5121
8081.6135 | 169.3587
8082.6135 | 169.2136
8083.6135 | 169.0438
8084.6135 | 168.9272
8085.6135 | 168.8093
8086.6135 | 168.6633
8087.6135 | 168.5562
8088.6135 | 168.4303
8089.6135 | 168.2689
8090.6135 | 168.1585
8091.6135 | 168.0339
8092.6135 | 167.8167
8093.6135 | 167.6253
8094.6135 | 167.4429
8095.6135 | 167.275
8096.6135 | 167.1463
8097.6135 | 167.0396
8098.6135 | 166.9332
8099.6135 | 166.824
8100.6135 | 166.7219
8101.6135 | 166.5462
8102.6135 | 166.3774
8103.6135 | 166.2375
8104.6135 | 166.1538
8105.6135 | 166.0932
8106.6135 | 165.9819
8107.6135 | 165.874
8108.6135 | 165.7367
8109.6135 | 165.6315
8110.6135 | 165.4971
8111.6135 | 165.3289
8112.6135 | 165.1782
8113.6135 | 165.0303
8114.6135 | 164.9014
8115.6135 | 164.768
8116.6135 | 164.5862
8117.6135 | 164.4194
8118.6135 | 164.2476
8119.6135 | 164.0497
8120.6135 | 163.9209
8121.6135 | 163.7979
8122.6135 | 163.653
8123.6135 | 163.5058
8124.6135 | 163.3783
8125.6135 | 163.2469
8126.6135 | 163.0535
8127.6135 | 162.8842
8128.6135 | 162.7285
8129.6135 | 162.5915
8130.6135 | 162.463
8131.6135 | 162.3644
8132.6135 | 162.2383
8133.6135 | 162.0998
8134.6135 | 161.9351
8135.6135 | 161.8225
8136.6135 | 161.6966
8137.6135 | 161.5511
8138.6135 | 161.403
8139.6135 | 161.2926
8140.6135 | 161.2197
8141.6135 | 161.1042
8142.6135 | 160.9912
8143.6135 | 160.8535
8144.6135 | 160.7339
8145.6135 | 160.602
8146.6135 | 160.4446
8147.6135 | 160.3015
8148.6135 | 160.1835
8149.6135 | 160.0647
8150.6135 | 159.9815
8151.6135 | 159.8646
8152.6135 | 159.7425
8153.6135 | 159.6099
8154.6135 | 159.4544
8155.6135 | 159.3224
8156.6135 | 159.1652
8157.6135 | 158.9755
8158.6135 | 158.8455
8159.6135 | 158.7355
8160.6135 | 158.5479
8161.6135 | 158.4162
8162.6135 | 158.2858
8163.6135 | 158.147
8164.6135 | 158.0238
8165.6135 | 157.882
8166.6135 | 157.7454
8167.6135 | 157.5866
8168.6135 | 157.4153
8169.6135 | 157.2925
8170.6135 | 157.1859
8171.6135 | 157.0718
8172.6135 | 156.9456
8173.6135 | 156.8181
8174.6135 | 156.7182
8175.6135 | 156.5856
8176.6135 | 156.4703
8177.6135 | 156.3201
8178.6135 | 156.15
8179.6135 | 155.9818
8180.6135 | 155.8414
8181.6135 | 155.7044
8182.6135 | 155.5727
8183.6135 | 155.4472
8184.6135 | 155.3514
8185.6135 | 155.2421
8186.6135 | 155.1126
8187.6135 | 154.9952
8188.6135 | 154.8741
8189.6135 | 154.7958
8190.6135 | 154.6714
8191.6135 | 154.5188
8192.6135 | 154.3823
8193.6135 | 154.2479
8194.6135 | 154.1314
8195.6135 | 153.9566
8196.6135 | 153.79
8197.6135 | 153.6064
8198.6135 | 153.4174
8199.6135 | 153.291
8200.6135 | 153.1714
8201.6135 | 153.0813
8202.6135 | 152.948
8203.6135 | 152.8374
8204.6135 | 152.7537
8205.6135 | 152.6458
8206.6135 | 152.5181
8207.6135 | 152.4158
8208.6135 | 152.3132
8209.6135 | 152.2051
8210.6135 | 152.0837
8211.6135 | 151.9634
8212.6135 | 151.7841
8213.6135 | 151.6203
8214.6135 | 151.4938
8215.6135 | 151.3735
8216.6135 | 151.2994
8217.6135 | 151.218
8218.6135 | 151.1005
8219.6135 | 150.9844
8220.6135 | 150.8581
8221.6135 | 150.7353
8222.6135 | 150.6165
8223.6135 | 150.5087
8224.6135 | 150.3379
8225.6135 | 150.2082
8226.6135 | 150.0785
8227.6135 | 149.9737
8228.6135 | 149.8816
8229.6135 | 149.7922
8230.6135 | 149.6829
8231.6135 | 149.5343
8232.6135 | 149.4476
8233.6135 | 149.3521
8234.6135 | 149.2073
8235.6135 | 149.0747
8236.6135 | 148.916
8237.6135 | 148.783
8238.6135 | 148.6407
8239.6135 | 148.4913
8240.6135 | 148.3778
8241.6135 | 148.2872
8242.6135 | 148.1952
8243.6135 | 148.1065
8244.6135 | 148.0022
8245.6135 | 147.8842
8246.6135 | 147.7334
8247.6135 | 147.6338
8248.6135 | 147.5363
8249.6135 | 147.4362
8250.6135 | 147.3202
8251.6135 | 147.1821
8252.6135 | 147.0826
8253.6135 | 146.9795
8254.6135 | 146.8419
8255.6135 | 146.7114
8256.6135 | 146.6044
8257.6135 | 146.4802
8258.6135 | 146.3517
8259.6135 | 146.2763
8260.6135 | 146.155
8261.6135 | 146.0015
8262.6135 | 145.8589
8263.6135 | 145.7366
8264.6135 | 145.6149
8265.6135 | 145.5086
8266.6135 | 145.4049
8267.6135 | 145.3126
8268.6135 | 145.2207
8269.6135 | 145.0944
8270.6135 | 145.0019
8271.6135 | 144.8961
8272.6135 | 144.8061
8273.6135 | 144.6871
8274.6135 | 144.5586
8275.6135 | 144.4292
8276.6135 | 144.3201
8277.6135 | 144.2257
8278.6135 | 144.1214
8279.6135 | 144.0134
8280.6135 | 143.9138
8281.6135 | 143.7999
8282.6135 | 143.714
8283.6135 | 143.6024
8284.6135 | 143.505
8285.6135 | 143.4043
8286.6135 | 143.2751
8287.6135 | 143.1548
8288.6135 | 143.0438
8289.6135 | 142.9375
8290.6135 | 142.8181
8291.6135 | 142.7213
8292.6135 | 142.5966
8293.6135 | 142.5062
8294.6135 | 142.3842
8295.6135 | 142.2673
8296.6135 | 142.157
8297.6135 | 142.004
8298.6135 | 141.9096
8299.6135 | 141.7925
8300.6135 | 141.6402
8301.6135 | 141.5475
8302.6135 | 141.4806
8303.6135 | 141.4024
8304.6135 | 141.3031
8305.6135 | 141.2128
8306.6135 | 141.1081
8307.6135 | 141.0253
8308.6135 | 140.9735
8309.6135 | 140.9148
8310.6135 | 140.8316
8311.6135 | 140.6989
8312.6135 | 140.5338
8313.6135 | 140.3887
8314.6135 | 140.2866
8315.6135 | 140.1797
8316.6135 | 140.0678
8317.6135 | 139.9505
8318.6135 | 139.8459
8319.6135 | 139.7214
8320.6135 | 139.5881
8321.6135 | 139.4982
8322.6135 | 139.3994
8323.6135 | 139.3167
8324.6135 | 139.204
8325.6135 | 139.1208
8326.6135 | 139.0037
8327.6135 | 138.8668
8328.6135 | 138.7612
8329.6135 | 138.662
8330.6135 | 138.5555
8331.6135 | 138.4453
8332.6135 | 138.362
8333.6135 | 138.2925
8334.6135 | 138.1647
8335.6135 | 138.05
8336.6135 | 137.9322
8337.6135 | 137.8092
8338.6135 | 137.6821
8339.6135 | 137.5771
8340.6135 | 137.4701
8341.6135 | 137.3612
8342.6135 | 137.2608
8343.6135 | 137.1886
8344.6135 | 137.118
8345.6135 | 137.0379
8346.6135 | 136.9413
8347.6135 | 136.8483
8348.6135 | 136.7429
8349.6135 | 136.64
8350.6135 | 136.5083
8351.6135 | 136.3747
8352.6135 | 136.2772
8353.6135 | 136.2056
8354.6135 | 136.1097
8355.6135 | 135.9999
8356.6135 | 135.8765
8357.6135 | 135.7485
8358.6135 | 135.6521
8359.6135 | 135.5542
8360.6135 | 135.457
8361.6135 | 135.3739
8362.6135 | 135.267
8363.6135 | 135.1637
8364.6135 | 135.0806
8365.6135 | 134.9719
8366.6135 | 134.8512
8367.6135 | 134.7349
8368.6135 | 134.6393
8369.6135 | 134.5348
8370.6135 | 134.4397
8371.6135 | 134.3349
8372.6135 | 134.2165
8373.6135 | 134.1111
8374.6135 | 134.0427
8375.6135 | 133.9308
8376.6135 | 133.8137
8377.6135 | 133.6663
8378.6135 | 133.5527
8379.6135 | 133.4577
8380.6135 | 133.3518
8381.6135 | 133.2826
8382.6135 | 133.2233
8383.6135 | 133.1512
8384.6135 | 133.08
8385.6135 | 132.9792
8386.6135 | 132.8817
8387.6135 | 132.7973
8388.6135 | 132.665
8389.6135 | 132.5427
8390.6135 | 132.447
8391.6135 | 132.3522
8392.6135 | 132.2823
8393.6135 | 132.1848
8394.6135 | 132.0801
8395.6448 | 131.9732
8396.6135 | 131.8607
8397.6135 | 131.7663
8398.6135 | 131.68
8399.6135 | 131.5767
8400.6135 | 131.4862
8401.6135 | 131.3782
8402.6135 | 131.2803
8403.6135 | 131.1571
8404.6135 | 131.0777
8405.6135 | 131.0056
8406.6135 | 130.8935
8407.6135 | 130.7822
8408.6135 | 130.6698
8409.6135 | 130.5799
8410.6135 | 130.4751
8411.6135 | 130.3576
8412.6135 | 130.2702
8413.6135 | 130.1678
8414.6135 | 130.0617
8415.6135 | 129.9355
8416.6135 | 129.8084
8417.6135 | 129.7383
8418.6135 | 129.6522
8419.6135 | 129.5697
8420.6135 | 129.5006
8421.6135 | 129.406
8422.6135 | 129.3398
8423.6135 | 129.2438
8424.6135 | 129.1705
8425.6135 | 129.0875
8426.6135 | 128.9766
8427.6135 | 128.8591
8428.6135 | 128.7377
8429.6135 | 128.6679
8430.6135 | 128.6303
8431.6135 | 128.549
8432.6135 | 128.453
8433.6135 | 128.3655
8434.6135 | 128.2974
8435.6135 | 128.2072
8436.6135 | 128.1074
8437.6135 | 127.9836
8438.6135 | 127.9147
8439.6135 | 127.798
8440.6135 | 127.6938
8441.6135 | 127.6099
8442.6135 | 127.5145
8443.6135 | 127.4301
8444.6135 | 127.3706
8445.6135 | 127.2539
8446.6135 | 127.1438
8447.6135 | 127.047
8448.6135 | 126.952
8449.6135 | 126.8437
8450.6135 | 126.7517
8451.6135 | 126.6611
8452.6135 | 126.5637
8453.6135 | 126.487
8454.6135 | 126.3921
8455.6135 | 126.291
8456.6135 | 126.1976
8457.6135 | 126.1221
8458.6135 | 126.0191
8459.6135 | 125.9337
8460.6135 | 125.8665
8461.6135 | 125.7684
8462.6135 | 125.6323
8463.6135 | 125.5549
8464.6135 | 125.4853
8465.6135 | 125.4077
8466.6135 | 125.3498
8467.6135 | 125.2506
8468.6135 | 125.1412
8469.6135 | 125.0654
8470.6135 | 124.9467
8471.6135 | 124.8509
8472.6135 | 124.767
8473.6135 | 124.6675
8474.6135 | 124.5519
8475.6135 | 124.4788
8476.6135 | 124.3938
8477.6135 | 124.3057
8478.6135 | 124.2359
8479.6135 | 124.15
8480.6135 | 124.0565
8481.6135 | 123.9754
8482.6135 | 123.8882
8483.6135 | 123.8168
8484.6135 | 123.7134
8485.6135 | 123.602
8486.6135 | 123.5007
8487.6135 | 123.4145
8488.6135 | 123.3436
8489.6135 | 123.2607
8490.6135 | 123.1692
8491.6135 | 123.0951
8492.6135 | 123.0019
8493.6135 | 122.9042
8494.6135 | 122.8295
8495.6135 | 122.756
8496.6135 | 122.7045
8497.6135 | 122.6349
8498.6135 | 122.545
8499.6135 | 122.4465
8500.6135 | 122.3492
8501.6135 | 122.2516
8502.6135 | 122.1678
8503.6135 | 122.0408
8504.6135 | 121.9533
8505.6135 | 121.8607
8506.6135 | 121.7956
8507.6135 | 121.74
8508.6135 | 121.6912
8509.6135 | 121.6272
8510.6135 | 121.5543
8511.6135 | 121.4717
8512.6135 | 121.3569
8513.6135 | 121.2344
8514.6135 | 121.1336
8515.6135 | 121.0459
8516.6135 | 120.9728
8517.6135 | 120.8847
8518.6135 | 120.788
8519.6135 | 120.7302
8520.6135 | 120.6362
8521.6135 | 120.5277
8522.6135 | 120.4347
8523.6135 | 120.3331
8524.6135 | 120.2513
8525.6135 | 120.196
8526.6135 | 120.1308
8527.6135 | 120.0411
8528.6135 | 119.9596
8529.6135 | 119.8715
8530.6135 | 119.8107
8531.6135 | 119.7662
8532.6135 | 119.6889
8533.6135 | 119.6198
8534.6135 | 119.5097
8535.6135 | 119.3978
8536.6135 | 119.3122
8537.6135 | 119.2101
8538.6135 | 119.1348
8539.6135 | 119.0501
8540.6135 | 118.9286
8541.6135 | 118.8361
8542.6135 | 118.7428
8543.6135 | 118.644
8544.6135 | 118.584
8545.6135 | 118.4881
8546.6135 | 118.4019
8547.6135 | 118.3032
8548.6135 | 118.2258
8549.6135 | 118.1614
8550.6135 | 118.0827
8551.6135 | 117.9919
8552.6135 | 117.8759
8553.6135 | 117.7772
8554.6135 | 117.6687
8555.6135 | 117.6102
8556.6135 | 117.5305
8557.6135 | 117.4469
8558.6135 | 117.3435
8559.6135 | 117.2829
8560.6135 | 117.2247
8561.6135 | 117.1305
8562.6135 | 117.0584
8563.6135 | 117.0024
8564.6135 | 116.9493
8565.6135 | 116.88
8566.6135 | 116.8444
8567.6135 | 116.7573
8568.6135 | 116.6802
8569.6135 | 116.5995
8570.6135 | 116.5416
8571.6135 | 116.4528
8572.6135 | 116.39
8573.6135 | 116.3058
8574.6135 | 116.2106
8575.6135 | 116.104
8576.6135 | 115.9972
8577.6135 | 115.9064
8578.6135 | 115.7994
8579.6135 | 115.743
8580.6135 | 115.682
8581.6135 | 115.605
8582.6135 | 115.5035
8583.6135 | 115.4108
8584.6135 | 115.3066
8585.6135 | 115.2313
8586.6135 | 115.179
8587.6135 | 115.1199
8588.6135 | 115.055
8589.6135 | 114.9864
8590.6135 | 114.8828
8591.6135 | 114.8032
8592.6135 | 114.6774
8593.6135 | 114.6057
8594.6135 | 114.5307
8595.6135 | 114.4826
8596.6135 | 114.4373
8597.6135 | 114.3405
8598.6135 | 114.2573
8599.6135 | 114.2096
8600.6135 | 114.13
8601.6135 | 114.0502
8602.6135 | 113.9999
8603.6135 | 113.9183
8604.6135 | 113.8142
8605.6135 | 113.7245
8606.6135 | 113.6812
8607.6135 | 113.5969
8608.6135 | 113.5249
8609.6135 | 113.4338
8610.6135 | 113.335
8611.6135 | 113.2696
8612.6135 | 113.2095
8613.6135 | 113.1516
8614.6135 | 113.0819
8615.6135 | 112.9967
8616.6135 | 112.9097
8617.6135 | 112.8179
8618.6135 | 112.7384
8619.6135 | 112.6236
8620.6135 | 112.5594
8621.6135 | 112.4695
8622.6135 | 112.3722
8623.6135 | 112.2781
8624.6135 | 112.2129
8625.6135 | 112.1293
8626.6135 | 112.0624
8627.6135 | 111.9717
8628.6135 | 111.8955
8629.6135 | 111.8285
8630.6135 | 111.7589
8631.6135 | 111.7091
8632.6135 | 111.651
8633.6135 | 111.5787
8634.6135 | 111.488
8635.6135 | 111.4018
8636.6135 | 111.348
8637.6135 | 111.3251
8638.6135 | 111.2542
8639.6135 | 111.1649
8640.6135 | 111.0799